## Test Conditions
DESIREE-FIRE Test Number 21 - Circuit Simulator Data Only
Test Date: | 2009-09-28
DCSim DAQ Start Time | 11:44
DCSim Time for Synchronization | 12:27
Heat Source Synchronization | 0:50 | minutes:seconds
Heat Source DAQ Start Time | 11:37
Heat Source Start Time | 12:30
DCSim Offset | 0:46 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 2760 | seconds
Heat Source Offset | 0:53 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 3161 | seconds
Heat Source Stop Time | 12:51
Test Duration | 0:21 | minutes:seconds
| 1245 | seconds
CT500 Turns | 2 |  | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 Turns | 5
Pre-Test Baseline: | Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SWGR Close | Armored, 8c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
SWGR Trip | Armored, 8c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SWGR_CT500 | SWGR-a_CT35_1_PC | SWGR-a_CT35_2_N1 | SWGR-b_CT35_1_PT | SWGR-b_CT35_2_G | SWGR-b_CT35_3_R | SWGR-b_CT35_4_N2 | SWGR-a_VT7_1_C1 | SWGR-a_VTU_1_PC | SWGR-a_VTU_2_N1 | SWGR-b_VT7_1_G | SWGR-b_VT7_2_R | SWGR-b_VT7_3_T | SWGR-b_VT7_4_SP | SWGR-b_VT7_5_SP | SWGR-b_VTU_1_PT | SWGR-b_VTU_2_N2 | {SWGR-C} V(N1) - V(Batt -) | {SWGR-C} V(PC) - V(Batt +) | {SWGR-C} V(C1) - V(Batt +) | {SWGR-T} V(G) - V(Batt -) | {SWGR-T} V(R) - V(Batt +) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-T} V(PT) - V(Batt +) | {SWGR-C} V(C1) - V(N1) | {SWGR-T} V(SP1) - V(Batt -) | {SWGR-T} V(SP2) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PC) - V(Batt -) | {SWGR-T} V(C1) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-C} V(PC) - V(Batt -) | {SWGR-C} V(C1) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-C} V(N1) - V(Batt +) | {SWGR-T} V(N2) - V(Batt +)
-0.625 | 125.1755 | -61.853 | 62.9929 | 0.1329 | 0.014939 | 0.01552 | 0.0077865 | 0.069643 | 0.0010254 | 0.06896 | -61.8851 | 62.8738 | -62.0728 | -61.9537 | 62.7914 | 0.13733 | -0.15564 | 0.13733 | 62.8876 | -62.0499 | -0.21973 | -0.11902 | -0.032044 | -0.10071 | -0.20142 | -0.19684 | -0.10529 | 0.18768 | 61.6974 | 61.9904 | 124.6445 | 124.7269 | -0.032044 | 124.7406 | 61.9904 | -0.19684 | 124.7269 | -0.032044 | 61.9904 | 124.6445 | 124.7406 | -125.0656 | -125.0427
0.375 | 125.1389 | -61.8256 | 62.9929 | 0.15579 | 0.016648 | 0.016588 | 0.0067185 | 0.06943 | -0.0019654 | 0.0696 | -61.8713 | 62.8967 | -62.0361 | -61.9812 | 62.7365 | 0.064087 | -0.16937 | 0.1236 | 62.8693 | -62.0682 | -0.21057 | -0.09613 | -0.045776 | -0.15564 | -0.25635 | -0.24261 | -0.1236 | 0.16479 | 61.6562 | 61.9492 | 124.5621 | 124.7223 | -0.045776 | 124.6948 | 61.8896 | -0.24261 | 124.7223 | -0.045776 | 61.8896 | 124.5621 | 124.6948 | -125.029 | -125.061
1.375 | 125.1114 | -61.8759 | 63.0112 | 0.30838 | 0.011093 | 0.015733 | 0.0024461 | 0.068789 | -0.0019654 | 0.068532 | -61.9629 | 62.8784 | -62.1002 | -62.0316 | 62.7136 | 0.050354 | -0.086975 | 0.10529 | 62.8922 | -62.0544 | -0.2243 | -0.13275 | -0.086975 | -0.15564 | -0.29755 | -0.17853 | -0.11902 | 0.13733 | 61.7889 | 61.9812 | 124.5895 | 124.7543 | -0.086975 | 124.7681 | 61.9263 | -0.17853 | 124.7543 | -0.086975 | 61.9263 | 124.5895 | 124.7681 | -125.1114 | -125.0656
2.375 | 125.1251 | -61.8393 | 62.9837 | 0.11002 | 0.013657 | 0.021501 | 0.0054367 | 0.067934 | -4.2788e-05 | 0.069814 | -61.8988 | 62.851 | -62.0499 | -61.9812 | 62.7228 | 0.050354 | -0.16479 | 0.12817 | 62.8784 | -62.0865 | -0.21057 | -0.13275 | -0.05951 | -0.14191 | -0.26093 | -0.24719 | -0.10529 | 0.15106 | 61.6745 | 61.9675 | 124.5621 | 124.6902 | -0.05951 | 124.7177 | 61.8896 | -0.24719 | 124.6902 | -0.05951 | 61.8896 | 124.5621 | 124.7177 | -125.0336 | -125.0702
3.375 | 125.1709 | -61.8484 | 62.9791 | 0.17868 | 0.013657 | 0.022569 | 0.0062913 | 0.068789 | -0.0028198 | 0.070028 | -61.8896 | 62.8693 | -62.0865 | -61.9629 | 62.7365 | 0.054932 | -0.20142 | 0.13733 | 62.8464 | -62.0682 | -0.23804 | -0.10986 | -0.041198 | -0.11444 | -0.24262 | -0.21973 | -0.13275 | 0.19684 | 61.647 | 61.9858 | 124.585 | 124.7177 | -0.041198 | 124.6948 | 61.9034 | -0.21973 | 124.7177 | -0.041198 | 61.9034 | 124.585 | 124.6948 | -125.0656 | -125.0473
4.375 | 125.0931 | -61.8484 | 62.9883 | 0.23972 | 0.016007 | 0.015092 | 0.0067185 | 0.070498 | -0.0015382 | 0.067891 | -61.94 | 62.9196 | -62.0728 | -62.0361 | 62.5992 | -0.036621 | -0.091553 | 0.045776 | 62.8784 | -62.1094 | -0.2243 | -0.068664 | -0.091552 | -0.18768 | -0.3891 | -0.26093 | -0.10986 | 0.13275 | 61.7569 | 61.8942 | 124.4476 | 124.7681 | -0.091552 | 124.7269 | 61.8118 | -0.26093 | 124.7681 | -0.091552 | 61.8118 | 124.4476 | 124.7269 | -125.061 | -125.0977
5.375 | 125.1114 | -61.8622 | 62.9929 | 0.10239 | 0.013657 | 0.010606 | -0.00033113 | 0.06943 | 0.00038461 | 0.069173 | -61.9263 | 62.8693 | -62.0682 | -62.0316 | 62.7045 | 0.018311 | -0.13733 | 0.10986 | 62.8647 | -62.0773 | -0.20599 | -0.1236 | -0.064087 | -0.16937 | -0.28839 | -0.21515 | -0.12817 | 0.14191 | 61.7249 | 61.972 | 124.5667 | 124.7314 | -0.064087 | 124.7269 | 61.8805 | -0.21515 | 124.7314 | -0.064087 | 61.8805 | 124.5667 | 124.7269 | -125.061 | -125.0702
6.375 | 125.1343 | -61.8484 | 62.97 | 0.16342 | 0.01323 | 0.015306 | 0.0058639 | 0.069643 | 0.00059821 | 0.071523 | -61.8896 | 62.8738 | -62.0544 | -61.972 | 62.7365 | 0.064087 | -0.18768 | 0.13275 | 62.8372 | -62.0819 | -0.20599 | -0.096131 | -0.041198 | -0.1236 | -0.23346 | -0.23346 | -0.13275 | 0.16479 | 61.6608 | 61.9812 | 124.585 | 124.7223 | -0.041198 | 124.6857 | 61.9125 | -0.23346 | 124.7223 | -0.041198 | 61.9125 | 124.585 | 124.6857 | -125.0244 | -125.0519
7.375 | 125.1114 | -61.853 | 62.9929 | 0.071869 | 0.012802 | 0.015947 | 0.00052347 | 0.069857 | 0.00081181 | 0.071309 | -61.9537 | 62.8693 | -62.0682 | -62.027 | 62.6907 | 0.045776 | -0.073242 | 0.10986 | 62.8601 | -62.0499 | -0.21515 | -0.1236 | -0.10071 | -0.17395 | -0.30212 | -0.19684 | -0.13275 | 0.11444 | 61.7798 | 61.9629 | 124.5438 | 124.7223 | -0.10071 | 124.7131 | 61.8988 | -0.19684 | 124.7223 | -0.10071 | 61.8988 | 124.5438 | 124.7131 | -125.061 | -125.0427
8.375 | 125.1343 | -61.8439 | 62.9974 | 0.38467 | 0.013443 | 0.018083 | 0.0088547 | 0.069216 | -0.0011108 | 0.069387 | -61.8805 | 62.9059 | -62.0682 | -61.9949 | 62.7182 | 0.054932 | -0.16479 | 0.11902 | 62.8784 | -62.1048 | -0.2243 | -0.091553 | -0.036621 | -0.15106 | -0.27924 | -0.26093 | -0.11902 | 0.18768 | 61.6791 | 61.9629 | 124.5621 | 124.7498 | -0.036621 | 124.7223 | 61.8988 | -0.26093 | 124.7498 | -0.036621 | 61.8988 | 124.5621 | 124.7223 | -125.0656 | -125.1022
9.375 | 125.0748 | -61.8484 | 62.9929 | 0.041351 | 0.013016 | 0.017229 | 0.0013779 | 0.070711 | -0.0028198 | 0.068105 | -61.9583 | 62.8738 | -62.0911 | -62.0224 | 62.709 | 0.036621 | -0.073242 | 0.11902 | 62.9013 | -62.059 | -0.24261 | -0.11902 | -0.10986 | -0.17395 | -0.28381 | -0.21057 | -0.091553 | 0.13275 | 61.7752 | 61.9675 | 124.5575 | 124.7223 | -0.10986 | 124.7498 | 61.8851 | -0.21057 | 124.7223 | -0.10986 | 61.8851 | 124.5575 | 124.7498 | -125.0839 | -125.0519
10.375 | 125.061 | -61.8759 | 63.0112 | 0.14816 | 0.017075 | 0.021288 | 0.0058639 | 0.071139 | -0.0030334 | 0.071523 | -61.9537 | 62.9608 | -62.0819 | -62.0682 | 62.6495 | -0.045776 | -0.059509 | 0.022888 | 62.8967 | -62.1277 | -0.20599 | -0.050354 | -0.077819 | -0.19226 | -0.36163 | -0.25177 | -0.11444 | 0.12817 | 61.8164 | 61.8988 | 124.5255 | 124.8367 | -0.077819 | 124.7726 | 61.8301 | -0.25177 | 124.8367 | -0.077819 | 61.8301 | 124.5255 | 124.7726 | -125.0931 | -125.1389
11.375 | 125.1617 | -61.821 | 62.9837 | 0.19394 | 0.015366 | 0.017442 | 0.0043687 | 0.070711 | -4.2788e-05 | 0.071309 | -61.8759 | 62.851 | -62.0728 | -61.972 | 62.7457 | 0.068665 | -0.19684 | 0.13275 | 62.8693 | -62.0544 | -0.25177 | -0.13275 | -0.054932 | -0.15106 | -0.23804 | -0.23346 | -0.11444 | 0.19684 | 61.6241 | 61.9537 | 124.5667 | 124.6719 | -0.054932 | 124.6902 | 61.8896 | -0.23346 | 124.6719 | -0.054932 | 61.8896 | 124.5667 | 124.6902 | -125.0565 | -125.0381
12.375 | 125.148 | -61.8073 | 62.9791 | 0.17868 | 0.014725 | 0.01787 | 0.0045823 | 0.070711 | -0.0013244 | 0.071737 | -61.8851 | 62.8738 | -62.0544 | -61.9812 | 62.7457 | 0.059509 | -0.18768 | 0.11902 | 62.8418 | -62.0911 | -0.24719 | -0.10529 | -0.07782 | -0.17395 | -0.23346 | -0.28381 | -0.13733 | 0.16937 | 61.6196 | 61.9263 | 124.5529 | 124.6811 | -0.07782 | 124.649 | 61.8668 | -0.28381 | 124.6811 | -0.07782 | 61.8668 | 124.5529 | 124.649 | -125.0336 | -125.0702
13.375 | 125.1068 | -61.821 | 62.9929 | 0.094757 | 0.013657 | 0.021715 | 0.0024461 | 0.069643 | -4.2788e-05 | 0.071309 | -61.9583 | 62.8647 | -62.0728 | -62.0224 | 62.7045 | 0.027466 | -0.10071 | 0.10529 | 62.8784 | -62.0453 | -0.25177 | -0.12817 | -0.13733 | -0.20142 | -0.28839 | -0.2243 | -0.11444 | 0.11444 | 61.7203 | 61.9263 | 124.5255 | 124.6857 | -0.13733 | 124.6994 | 61.8484 | -0.2243 | 124.6857 | -0.13733 | 61.8484 | 124.5255 | 124.6994 | -125.0656 | -125.0381
14.375 | 125.1434 | -61.8256 | 62.9974 | 0.12527 | 0.013443 | 0.018938 | 0.0037277 | 0.069216 | -0.00046999 | 0.069387 | -61.8942 | 62.8738 | -62.0773 | -61.9766 | 62.7274 | 0.054932 | -0.15564 | 0.12817 | 62.8555 | -62.0865 | -0.25177 | -0.1236 | -0.068664 | -0.15106 | -0.27008 | -0.26093 | -0.14191 | 0.18311 | 61.6699 | 61.9537 | 124.5529 | 124.6994 | -0.068664 | 124.6811 | 61.8805 | -0.26093 | 124.6994 | -0.068664 | 61.8805 | 124.5529 | 124.6811 | -125.0748 | -125.0839
15.3906 | 125.0198 | -61.8484 | 63.0478 | -0.24094 | 0.014298 | 0.016801 | 0.0080003 | 0.067721 | -0.00068359 | 0.070455 | -61.9446 | 62.9929 | -62.0682 | -62.0316 | 62.677 | 0.050354 | 0.15106 | 0.13733 | 62.9562 | -62.1002 | -0.21973 | -0.054932 | -0.09613 | -0.1831 | -0.37079 | -0.25177 | -0.091553 | 0.1236 | 61.9995 | 61.9858 | 124.5255 | 124.8413 | -0.09613 | 124.8047 | 61.8988 | -0.25177 | 124.8413 | -0.09613 | 61.8988 | 124.5255 | 124.8047 | -125.116 | -125.148
16.375 | 125.1114 | -61.8622 | 62.9837 | 0.2092 | 0.015793 | 0.016801 | 0.0047959 | 0.070498 | -0.0017518 | 0.070669 | -61.8851 | 62.9059 | -62.0773 | -61.9675 | 62.7411 | 0.054932 | -0.1831 | 0.13275 | 62.8418 | -62.0499 | -0.21515 | -0.07782 | -0.022888 | -0.10528 | -0.24262 | -0.18768 | -0.14191 | 0.19226 | 61.6791 | 61.9949 | 124.6033 | 124.7681 | -0.022888 | 124.704 | 61.9171 | -0.18768 | 124.7681 | -0.022888 | 61.9171 | 124.6033 | 124.704 | -125.061 | -125.0336
17.375 | 125.0931 | -61.8118 | 63.0112 | -0.19516 | 0.011307 | 0.018724 | 0.0018051 | 0.070498 | -0.0028198 | 0.070669 | -61.8759 | 62.8738 | -62.0636 | -61.9492 | 62.7777 | 0.14648 | 0.018311 | 0.24719 | 62.9013 | -62.0499 | -0.25177 | -0.13733 | -0.064087 | -0.13733 | -0.23346 | -0.23804 | -0.10986 | 0.18768 | 61.8301 | 62.059 | 124.5895 | 124.6857 | -0.064087 | 124.7131 | 61.9583 | -0.23804 | 124.6857 | -0.064087 | 61.9583 | 124.5895 | 124.7131 | -125.0748 | -125.061
18.375 | 125.1205 | -61.8301 | 62.9837 | 0.1329 | 0.013657 | 0.020219 | 0.0037277 | 0.068361 | 0.0010254 | 0.070669 | -61.8896 | 62.8647 | -62.0636 | -61.9766 | 62.7365 | 0.050354 | -0.16479 | 0.14191 | 62.8693 | -62.0453 | -0.23346 | -0.11902 | -0.059509 | -0.14648 | -0.24719 | -0.21515 | -0.11444 | 0.17395 | 61.6653 | 61.972 | 124.5667 | 124.6948 | -0.059509 | 124.6994 | 61.8805 | -0.21515 | 124.6948 | -0.059509 | 61.8805 | 124.5667 | 124.6994 | -125.0473 | -125.029
19.375 | 125.1068 | -61.8484 | 62.97 | 0.14816 | 0.013443 | 0.014452 | 0.0069321 | 0.068148 | 0.00038461 | 0.068746 | -61.8759 | 62.8693 | -62.0224 | -61.9904 | 62.7319 | 0.045776 | -0.16022 | 0.12817 | 62.8555 | -62.0773 | -0.17395 | -0.10071 | -0.027466 | -0.14191 | -0.23804 | -0.22888 | -0.11444 | 0.14648 | 61.6882 | 61.9766 | 124.5804 | 124.7177 | -0.027466 | 124.704 | 61.8942 | -0.22888 | 124.7177 | -0.027466 | 61.8942 | 124.5804 | 124.704 | -124.9924 | -125.0473
20.3906 | 125.0748 | -61.821 | 63.0066 | -0.24857 | 0.013443 | 0.017656 | 0.0045823 | 0.068148 | -0.0023926 | 0.06896 | -61.8805 | 62.9105 | -62.0499 | -61.9629 | 62.764 | 0.13275 | 0.045776 | 0.23804 | 62.9105 | -62.0682 | -0.22888 | -0.096131 | -0.059509 | -0.14191 | -0.24262 | -0.24719 | -0.096131 | 0.16937 | 61.8668 | 62.059 | 124.585 | 124.7314 | -0.059509 | 124.7314 | 61.9537 | -0.24719 | 124.7314 | -0.059509 | 61.9537 | 124.585 | 124.7314 | -125.0565 | -125.0748
21.375 | 125.1022 | -61.8576 | 63.002 | -0.050202 | 0.011734 | 0.015092 | 0.00030967 | 0.068789 | -0.00068359 | 0.068105 | -61.9308 | 62.8876 | -62.0682 | -61.9675 | 62.7228 | 0.09613 | -0.041199 | 0.20142 | 62.883 | -62.0453 | -0.21057 | -0.11444 | -0.073242 | -0.10986 | -0.27924 | -0.18768 | -0.11902 | 0.13733 | 61.8164 | 62.059 | 124.5804 | 124.7452 | -0.073242 | 124.7406 | 61.9537 | -0.18768 | 124.7452 | -0.073242 | 61.9537 | 124.5804 | 124.7406 | -125.0702 | -125.0473
22.375 | 125.148 | -61.7752 | 63.0203 | -0.22568 | 0.012802 | 0.016161 | 0.0022323 | 0.068361 | -0.00089719 | 0.069387 | -61.8896 | 62.8647 | -62.0407 | -61.94 | 62.7823 | 0.14191 | -0.082397 | 0.24261 | 62.8738 | -62.0499 | -0.2655 | -0.15564 | -0.11444 | -0.16479 | -0.23804 | -0.27466 | -0.14648 | 0.15106 | 61.6928 | 62.0178 | 124.5575 | 124.6399 | -0.11444 | 124.649 | 61.9171 | -0.27466 | 124.6399 | -0.11444 | 61.9171 | 124.5575 | 124.649 | -125.061 | -125.0702
23.375 | 125.1022 | -61.8301 | 63.002 | 0.16342 | 0.012162 | 0.01787 | 0.0041549 | 0.066225 | -0.0019654 | 0.070455 | -61.9125 | 62.8555 | -62.0819 | -62.027 | 62.6862 | 0 | -0.10071 | 0.10071 | 62.8464 | -62.059 | -0.25177 | -0.14648 | -0.082398 | -0.19684 | -0.31586 | -0.22888 | -0.15564 | 0.16937 | 61.7294 | 61.9308 | 124.5163 | 124.6857 | -0.082398 | 124.6765 | 61.8301 | -0.22888 | 124.6857 | -0.082398 | 61.8301 | 124.5163 | 124.6765 | -125.0839 | -125.061
24.375 | 125.1297 | -61.8301 | 62.9608 | 0.14053 | 0.014939 | 0.019151 | 0.0065049 | 0.068148 | -4.2788e-05 | 0.068746 | -61.8759 | 62.8967 | -62.0682 | -61.9675 | 62.7319 | 0.050354 | -0.18768 | 0.12817 | 62.851 | -62.0911 | -0.23804 | -0.064086 | -0.045777 | -0.13733 | -0.22888 | -0.26093 | -0.10986 | 0.19226 | 61.6425 | 61.9583 | 124.5621 | 124.7269 | -0.045777 | 124.6811 | 61.8805 | -0.26093 | 124.7269 | -0.045777 | 61.8805 | 124.5621 | 124.6811 | -125.029 | -125.0519
25.3906 | 125.061 | -61.8713 | 63.0157 | -0.088349 | 0.016007 | 0.023424 | 0.010136 | 0.071993 | -0.0011108 | 0.069814 | -61.8805 | 62.9654 | -62.0544 | -61.9949 | 62.6907 | 0.050354 | 0.041199 | 0.12817 | 62.915 | -62.0865 | -0.1831 | -0.050354 | -0.009155 | -0.1236 | -0.32501 | -0.21515 | -0.10071 | 0.17395 | 61.9125 | 61.9995 | 124.5621 | 124.8367 | -0.009155 | 124.7864 | 61.9217 | -0.21515 | 124.8367 | -0.009155 | 61.9217 | 124.5621 | 124.7864 | -125.0702 | -125.1022
26.375 | 125.0977 | -61.8439 | 63.002 | -0.042572 | 0.011734 | 0.01552 | -0.00075833 | 0.06943 | -0.0017518 | 0.070669 | -61.94 | 62.883 | -62.0544 | -62.0178 | 62.7045 | 0.045776 | -0.036621 | 0.12817 | 62.9105 | -62.0407 | -0.21057 | -0.11902 | -0.09613 | -0.17395 | -0.29755 | -0.19684 | -0.091553 | 0.11444 | 61.8073 | 61.972 | 124.5483 | 124.7269 | -0.09613 | 124.7543 | 61.8896 | -0.19684 | 124.7269 | -0.09613 | 61.8896 | 124.5483 | 124.7543 | -125.0565 | -125.0427
27.3906 | 125.0107 | -61.8484 | 63.0341 | -0.050202 | 0.016861 | 0.016588 | 0.0069321 | 0.069643 | -0.00068359 | 0.070669 | -61.8713 | 62.9883 | -62.0682 | -62.0087 | 62.6999 | 0.032043 | 0.032043 | 0.11902 | 62.9013 | -62.1094 | -0.21973 | -0.045777 | -0.022888 | -0.16022 | -0.33417 | -0.26093 | -0.13275 | 0.19684 | 61.8805 | 61.9675 | 124.5483 | 124.8367 | -0.022888 | 124.7498 | 61.8805 | -0.26093 | 124.8367 | -0.022888 | 61.8805 | 124.5483 | 124.7498 | -125.1022 | -125.1434
28.375 | 125.0748 | -61.821 | 62.9837 | 0.27023 | 0.012375 | 0.015733 | -0.00054473 | 0.07242 | -0.0015382 | 0.070241 | -61.972 | 62.8464 | -62.0773 | -62.027 | 62.6907 | 0.027466 | -0.10529 | 0.10071 | 62.8967 | -62.0544 | -0.25635 | -0.13733 | -0.15106 | -0.20599 | -0.29297 | -0.23346 | -0.086975 | 0.10529 | 61.7157 | 61.9217 | 124.5117 | 124.6674 | -0.15106 | 124.7177 | 61.8484 | -0.23346 | 124.6674 | -0.15106 | 61.8484 | 124.5117 | 124.7177 | -125.061 | -125.0381
29.375 | 125.1389 | -61.821 | 63.0112 | -0.080719 | 0.010025 | 0.01317 | 0.00052347 | 0.06708 | -0.0017518 | 0.069387 | -61.9263 | 62.8784 | -62.059 | -61.9583 | 62.7548 | 0.10529 | -0.073242 | 0.18768 | 62.9013 | -62.027 | -0.23804 | -0.13275 | -0.10529 | -0.13733 | -0.25635 | -0.20599 | -0.10986 | 0.13275 | 61.7477 | 62.0087 | 124.5758 | 124.6994 | -0.10529 | 124.7223 | 61.9263 | -0.20599 | 124.6994 | -0.10529 | 61.9263 | 124.5758 | 124.7223 | -125.0702 | -125.0381
30.375 | 125.0061 | -61.8713 | 63.0569 | -0.26382 | 0.012802 | 0.014238 | 0.0071457 | 0.068789 | 0.00081181 | 0.0696 | -61.9766 | 62.9379 | -62.0682 | -62.0407 | 62.6724 | 0.059509 | 0.17853 | 0.13733 | 62.9379 | -62.0728 | -0.19684 | -0.11902 | -0.10529 | -0.16937 | -0.38452 | -0.20142 | -0.11902 | 0.091552 | 62.0499 | 62.0087 | 124.5438 | 124.8093 | -0.10529 | 124.8093 | 61.9308 | -0.20142 | 124.8093 | -0.10529 | 61.9308 | 124.5438 | 124.8093 | -125.1251 | -125.1297
31.375 | 125.0977 | -61.8393 | 63.0249 | 0.18631 | 0.013016 | 0.017656 | 0.0024461 | 0.066652 | -0.0013244 | 0.068319 | -61.9675 | 62.8693 | -62.0636 | -62.0453 | 62.6953 | 0.032043 | -0.091553 | 0.091553 | 62.8738 | -62.059 | -0.22431 | -0.15564 | -0.12817 | -0.20599 | -0.32959 | -0.21973 | -0.15106 | 0.096131 | 61.7477 | 61.9308 | 124.5346 | 124.7086 | -0.12817 | 124.7131 | 61.8713 | -0.21973 | 124.7086 | -0.12817 | 61.8713 | 124.5346 | 124.7131 | -125.0885 | -125.0839
32.375 | 125.0793 | -61.8027 | 63.0157 | -0.27145 | 0.014298 | 0.01317 | 0.0020187 | 0.066652 | -0.0017518 | 0.070455 | -61.8576 | 62.883 | -62.0316 | -61.908 | 62.8006 | 0.17853 | -0.009155 | 0.26093 | 62.8967 | -62.0453 | -0.22888 | -0.13275 | -0.054932 | -0.10529 | -0.21515 | -0.24262 | -0.11902 | 0.17395 | 61.7935 | 62.0636 | 124.6033 | 124.6857 | -0.054932 | 124.6994 | 61.9812 | -0.24262 | 124.6857 | -0.054932 | 61.9812 | 124.6033 | 124.6994 | -125.0473 | -125.061
33.375 | 125.1434 | -61.7981 | 63.0295 | -0.10361 | 0.011093 | 0.011675 | 0.0035141 | 0.068361 | -0.00068359 | 0.067891 | -61.8622 | 62.8693 | -62.0178 | -61.908 | 62.8052 | 0.1831 | -0.086975 | 0.26093 | 62.8876 | -62.027 | -0.21973 | -0.16022 | -0.064087 | -0.10986 | -0.2243 | -0.22888 | -0.14191 | 0.15564 | 61.7111 | 62.059 | 124.6033 | 124.6674 | -0.064087 | 124.6857 | 61.9812 | -0.22888 | 124.6674 | -0.064087 | 61.9812 | 124.6033 | 124.6857 | -125.0473 | -125.0565
34.375 | 125.1251 | -61.8027 | 63.0157 | -0.1799 | 0.012802 | 0.016161 | 0.0018051 | 0.066652 | -0.0015382 | 0.06896 | -61.8988 | 62.8647 | -62.0407 | -61.9675 | 62.7457 | 0.10986 | -0.064087 | 0.21057 | 62.8922 | -62.0316 | -0.23804 | -0.15106 | -0.096131 | -0.16479 | -0.27008 | -0.22888 | -0.1236 | 0.14191 | 61.7386 | 62.0132 | 124.5483 | 124.6674 | -0.096131 | 124.6948 | 61.9125 | -0.22888 | 124.6674 | -0.096131 | 61.9125 | 124.5483 | 124.6948 | -125.0565 | -125.0473
35.375 | 125.1114 | -61.8347 | 63.002 | -0.057831 | 0.012162 | 0.013811 | 0.0028733 | 0.068575 | -0.00068359 | 0.068319 | -61.9446 | 62.8784 | -62.0636 | -62.0178 | 62.7228 | 0.054932 | -0.050354 | 0.13275 | 62.8784 | -62.0728 | -0.22888 | -0.1236 | -0.10986 | -0.18311 | -0.27924 | -0.23804 | -0.1236 | 0.11902 | 61.7844 | 61.9675 | 124.5575 | 124.7131 | -0.10986 | 124.7131 | 61.8896 | -0.23804 | 124.7131 | -0.10986 | 61.8896 | 124.5575 | 124.7131 | -125.0656 | -125.0748
36.375 | 125.0839 | -61.8256 | 63.0157 | -0.07309 | 0.011734 | 0.015306 | 0.0020187 | 0.068575 | -0.0017518 | 0.0696 | -61.9308 | 62.8738 | -62.0544 | -61.9858 | 62.7045 | 0.064087 | -0.073242 | 0.13733 | 62.8784 | -62.0224 | -0.22888 | -0.14191 | -0.10529 | -0.16022 | -0.31128 | -0.19684 | -0.13733 | 0.1236 | 61.7523 | 61.9629 | 124.53 | 124.6994 | -0.10529 | 124.704 | 61.8896 | -0.19684 | 124.6994 | -0.10529 | 61.8896 | 124.53 | 124.704 | -125.0702 | -125.0381
37.375 | 125.0336 | -61.8256 | 63.0569 | -0.23331 | 0.016007 | 0.018083 | 0.0080003 | 0.068361 | -0.0041016 | 0.069173 | -61.8896 | 62.9745 | -62.0728 | -62.0682 | 62.5671 | 0.004578 | 0.12817 | 0.15564 | 62.9242 | -62.0544 | -0.24719 | -0.082398 | -0.064086 | -0.24261 | -0.48981 | -0.22888 | -0.13275 | 0.18311 | 61.9537 | 61.9812 | 124.3927 | 124.8001 | -0.064086 | 124.7498 | 61.8301 | -0.22888 | 124.8001 | -0.064086 | 61.8301 | 124.3927 | 124.7498 | -125.1297 | -125.1114
38.375 | 125.0977 | -61.8301 | 62.9837 | -0.06546 | 0.011521 | 0.014024 | -0.0018265 | 0.068575 | -0.00068359 | 0.068532 | -61.9537 | 62.8647 | -62.0499 | -62.0132 | 62.709 | 0.073242 | -0.045776 | 0.12817 | 62.8967 | -62.0544 | -0.21973 | -0.11902 | -0.1236 | -0.18311 | -0.27466 | -0.2243 | -0.086975 | 0.096131 | 61.7844 | 61.9583 | 124.5392 | 124.6948 | -0.1236 | 124.7269 | 61.9034 | -0.2243 | 124.6948 | -0.1236 | 61.9034 | 124.5392 | 124.7269 | -125.0336 | -125.0381
39.375 | 125.1297 | -61.7889 | 63.0295 | -0.16464 | 0.013443 | 0.018083 | 0.0028733 | 0.067721 | -0.00068359 | 0.0696 | -61.8576 | 62.8601 | -62.0453 | -61.8942 | 62.796 | 0.14648 | -0.054932 | 0.26093 | 62.883 | -62.0316 | -0.25635 | -0.16937 | -0.068665 | -0.10529 | -0.23346 | -0.24262 | -0.14648 | 0.18768 | 61.734 | 62.0499 | 124.585 | 124.649 | -0.068665 | 124.6719 | 61.9354 | -0.24262 | 124.649 | -0.068665 | 61.9354 | 124.585 | 124.6719 | -125.0748 | -125.061
40.375 | 125.1709 | -61.853 | 63.0066 | -0.088349 | 0.010453 | 0.012529 | 0.0043687 | 0.065798 | -0.0013244 | 0.0696 | -61.9034 | 62.8693 | -62.027 | -61.9583 | 62.7502 | 0.10986 | -0.054932 | 0.21515 | 62.8601 | -62.0407 | -0.17395 | -0.13733 | -0.050354 | -0.10529 | -0.25635 | -0.18768 | -0.14648 | 0.1236 | 61.7981 | 62.0682 | 124.6033 | 124.7223 | -0.050354 | 124.7131 | 61.9629 | -0.18768 | 124.7223 | -0.050354 | 61.9629 | 124.6033 | 124.7131 | -125.0336 | -125.0473
41.375 | 125.0977 | -61.8118 | 63.0295 | -0.19516 | 0.012375 | 0.018297 | 0.0018051 | 0.065798 | -0.003247 | 0.070241 | -61.8576 | 62.8555 | -62.0361 | -61.9171 | 62.7686 | 0.16479 | -0.004578 | 0.24719 | 62.8967 | -62.0087 | -0.2243 | -0.17395 | -0.045776 | -0.10528 | -0.26093 | -0.19684 | -0.13275 | 0.17853 | 61.8073 | 62.059 | 124.5804 | 124.6674 | -0.045776 | 124.7086 | 61.9766 | -0.19684 | 124.6674 | -0.045776 | 61.9766 | 124.5804 | 124.7086 | -125.0656 | -125.0381
42.375 | 125.0519 | -61.8484 | 63.0524 | -0.31723 | 0.014084 | 0.019579 | 0.0030869 | 0.069002 | -4.2788e-05 | 0.064687 | -61.8851 | 62.9013 | -62.027 | -61.8851 | 62.764 | 0.10986 | 0.13733 | 0.20142 | 62.9425 | -62.0361 | -0.17853 | -0.15106 | -0.036621 | -0.036621 | -0.28839 | -0.18768 | -0.10986 | 0.14191 | 61.9858 | 62.0499 | 124.6124 | 124.7498 | -0.036621 | 124.791 | 61.9583 | -0.18768 | 124.7498 | -0.036621 | 61.9583 | 124.6124 | 124.791 | -125.0793 | -125.0885
43.375 | 125.1251 | -61.8118 | 63.0203 | -0.15701 | 0.013871 | 0.014024 | 0.00073707 | 0.068575 | 0.00059821 | 0.0696 | -61.8851 | 62.8601 | -62.0316 | -61.972 | 62.7502 | 0.11444 | -0.050354 | 0.21515 | 62.883 | -62.0224 | -0.21973 | -0.16022 | -0.073242 | -0.16022 | -0.27008 | -0.21057 | -0.13733 | 0.14648 | 61.7615 | 62.027 | 124.5621 | 124.6719 | -0.073242 | 124.6948 | 61.9263 | -0.21057 | 124.6719 | -0.073242 | 61.9263 | 124.5621 | 124.6948 | -125.0519 | -125.0427
44.375 | 125.1389 | -61.7889 | 63.0157 | -0.1799 | 0.013016 | 0.015092 | 0.0013779 | 0.067507 | -0.00068359 | 0.071096 | -61.9034 | 62.8967 | -62.0636 | -61.9537 | 62.764 | 0.10986 | -0.064087 | 0.20599 | 62.8967 | -62.0132 | -0.27466 | -0.11902 | -0.11444 | -0.1648 | -0.25177 | -0.22431 | -0.11902 | 0.16022 | 61.7249 | 61.9949 | 124.5529 | 124.6857 | -0.11444 | 124.6857 | 61.8988 | -0.22431 | 124.6857 | -0.11444 | 61.8988 | 124.5529 | 124.6857 | -125.0793 | -125.029
45.375 | 125.0473 | -61.821 | 63.0478 | -0.24094 | 0.012589 | 0.016374 | 0.0026597 | 0.06708 | 0.00059821 | 0.070241 | -61.8942 | 62.9013 | -62.027 | -61.972 | 62.6221 | 0.018311 | 0.21057 | 0.23804 | 62.8922 | -62.0407 | -0.20599 | -0.14648 | -0.073242 | -0.15106 | -0.42572 | -0.21973 | -0.15564 | 0.13275 | 62.0316 | 62.059 | 124.4431 | 124.7223 | -0.073242 | 124.7131 | 61.8393 | -0.21973 | 124.7223 | -0.073242 | 61.8393 | 124.4431 | 124.7131 | -125.0748 | -125.0885
46.375 | 125.1572 | -61.8073 | 63.0249 | -0.11124 | 0.013443 | 0.016374 | 0.0028733 | 0.06708 | 0.00059821 | 0.067891 | -61.8576 | 62.8647 | -62.0636 | -61.9263 | 62.8098 | 0.16937 | -0.082397 | 0.27466 | 62.8738 | -62.0041 | -0.25635 | -0.16022 | -0.050354 | -0.11902 | -0.21515 | -0.19684 | -0.15106 | 0.20599 | 61.7249 | 62.0819 | 124.617 | 124.6719 | -0.050354 | 124.6811 | 61.9766 | -0.19684 | 124.6719 | -0.050354 | 61.9766 | 124.617 | 124.6811 | -125.0885 | -125.029
47.3906 | 125.0107 | -61.8668 | 63.0661 | -0.22568 | 0.014939 | 0.014879 | 0.0050095 | 0.068148 | 0.0014526 | 0.069173 | -61.9125 | 63.002 | -62.0728 | -62.027 | 62.6816 | 0.045776 | 0.13733 | 0.12817 | 62.9379 | -62.0728 | -0.20599 | -0.064087 | -0.045777 | -0.16022 | -0.38452 | -0.20599 | -0.12817 | 0.16022 | 62.0041 | 61.9949 | 124.5483 | 124.8688 | -0.045777 | 124.8047 | 61.9125 | -0.20599 | 124.8688 | -0.045777 | 61.9125 | 124.5483 | 124.8047 | -125.1389 | -125.1389
48.375 | 125.1297 | -61.7935 | 63.0112 | -0.11124 | 0.01088 | 0.01317 | 0.00073707 | 0.070284 | -0.0011108 | 0.0696 | -61.8622 | 62.8784 | -62.059 | -61.94 | 62.764 | 0.14648 | -0.086975 | 0.25177 | 62.9196 | -61.9949 | -0.2655 | -0.13275 | -0.068665 | -0.14648 | -0.24719 | -0.20142 | -0.091552 | 0.19684 | 61.7065 | 62.0453 | 124.5575 | 124.6719 | -0.068665 | 124.7131 | 61.94 | -0.20142 | 124.6719 | -0.068665 | 61.94 | 124.5575 | 124.7131 | -125.0702 | -125.0061
49.375 | 124.9741 | -61.8256 | 63.0569 | -0.29434 | 0.011948 | 0.014665 | 0.0043687 | 0.067721 | -0.003247 | 0.067678 | -61.9583 | 62.9242 | -62.0453 | -62.0178 | 62.677 | 0.054932 | 0.14191 | 0.15106 | 62.9425 | -62.0407 | -0.21973 | -0.13275 | -0.13275 | -0.19226 | -0.37994 | -0.21515 | -0.11444 | 0.086975 | 61.9675 | 61.9766 | 124.5026 | 124.7498 | -0.13275 | 124.7681 | 61.8805 | -0.21515 | 124.7498 | -0.13275 | 61.8805 | 124.5026 | 124.7681 | -125.1022 | -125.0977
50.375 | 125.1205 | -61.8164 | 63.0386 | -0.20279 | 0.013443 | 0.017229 | 0.0022323 | 0.067507 | -0.00068359 | 0.069387 | -61.8393 | 62.8647 | -62.0453 | -61.9125 | 62.8052 | 0.1831 | -0.032043 | 0.28839 | 62.8876 | -62.0132 | -0.22888 | -0.17395 | -0.022888 | -0.096131 | -0.23346 | -0.19684 | -0.15106 | 0.20599 | 61.7844 | 62.1048 | 124.6216 | 124.6811 | -0.022888 | 124.704 | 61.9995 | -0.19684 | 124.6811 | -0.022888 | 61.9995 | 124.6216 | 124.704 | -125.0839 | -125.0519
51.375 | 125.1205 | -61.8164 | 63.0249 | -0.19516 | 0.012589 | 0.012743 | -0.00011753 | 0.069216 | -0.00068359 | 0.068746 | -61.8301 | 62.8693 | -62.0407 | -61.9125 | 62.7914 | 0.16479 | -0.041199 | 0.27466 | 62.8784 | -61.9629 | -0.2243 | -0.15564 | -0.013733 | -0.096131 | -0.23346 | -0.14648 | -0.14648 | 0.21057 | 61.7752 | 62.0911 | 124.6078 | 124.6857 | -0.013733 | 124.6948 | 61.9812 | -0.14648 | 124.6857 | -0.013733 | 61.9812 | 124.6078 | 124.6948 | -125.0656 | -124.9878
52.375 | 125.1389 | -61.8073 | 63.0249 | -0.18753 | 0.010239 | 0.01082 | 0.0026597 | 0.069002 | -0.00046999 | 0.068105 | -61.8439 | 62.8464 | -62.0316 | -61.8988 | 62.7869 | 0.15564 | -0.045776 | 0.27008 | 62.8693 | -62.0178 | -0.2243 | -0.17853 | -0.036621 | -0.091553 | -0.23804 | -0.21057 | -0.15564 | 0.18768 | 61.7615 | 62.0773 | 124.5941 | 124.6536 | -0.036621 | 124.6765 | 61.9629 | -0.21057 | 124.6536 | -0.036621 | 61.9629 | 124.5941 | 124.6765 | -125.0565 | -125.0427
53.375 | 125.1068 | -61.821 | 63.0341 | -0.27145 | 0.011521 | 0.017656 | 0.0030869 | 0.06708 | -0.0017518 | 0.067678 | -61.8576 | 62.8555 | -62.0316 | -61.9263 | 62.7823 | 0.15564 | -0.009155 | 0.27466 | 62.9013 | -62.0316 | -0.21057 | -0.17853 | -0.036621 | -0.10529 | -0.25177 | -0.21057 | -0.13275 | 0.17395 | 61.8118 | 62.0956 | 124.6033 | 124.6765 | -0.036621 | 124.7223 | 61.9766 | -0.21057 | 124.6765 | -0.036621 | 61.9766 | 124.6033 | 124.7223 | -125.0656 | -125.0656
54.375 | 125.1389 | -61.8347 | 63.0249 | -0.24094 | 0.013657 | 0.012529 | 0.0024461 | 0.06708 | -0.0013244 | 0.06896 | -61.8622 | 62.8693 | -62.0407 | -61.908 | 62.7869 | 0.1831 | -0.036621 | 0.27008 | 62.8738 | -62.0224 | -0.20599 | -0.15564 | -0.027466 | -0.073242 | -0.23804 | -0.18768 | -0.15106 | 0.17853 | 61.7981 | 62.1048 | 124.6216 | 124.704 | -0.027466 | 124.7086 | 62.0178 | -0.18768 | 124.704 | -0.027466 | 62.0178 | 124.6216 | 124.7086 | -125.0656 | -125.0473
55.375 | 125.0061 | -61.8484 | 63.0844 | -1.2938 | 0.014084 | 0.014879 | 0.0033005 | 0.067721 | -0.0019654 | 0.069173 | -61.9171 | 62.915 | -62.0361 | -62.0224 | 62.6724 | 0.082397 | 0.11902 | 0.16479 | 62.9333 | -62.0407 | -0.18768 | -0.16937 | -0.068664 | -0.17395 | -0.41199 | -0.19226 | -0.15106 | 0.11902 | 61.9675 | 62.0132 | 124.5209 | 124.7635 | -0.068664 | 124.7818 | 61.9308 | -0.19226 | 124.7635 | -0.068664 | 61.9308 | 124.5209 | 124.7818 | -125.1205 | -125.1251
56.375 | 125.0931 | -61.8118 | 63.0112 | -0.11124 | 0.011948 | 0.014238 | 0.0013779 | 0.066866 | -0.0011108 | 0.070028 | -61.8942 | 62.8693 | -62.059 | -61.9766 | 62.7502 | 0.10986 | -0.064087 | 0.21515 | 62.8784 | -62.0453 | -0.24719 | -0.14191 | -0.082397 | -0.16479 | -0.26093 | -0.23346 | -0.13275 | 0.16479 | 61.7477 | 62.027 | 124.5621 | 124.6811 | -0.082397 | 124.6902 | 61.9217 | -0.23346 | 124.6811 | -0.082397 | 61.9217 | 124.5621 | 124.6902 | -125.0702 | -125.0565
57.375 | 125.0427 | -61.8439 | 63.0112 | -0.20279 | 0.018143 | 0.014665 | 0.0086411 | 0.06943 | -0.0019654 | 0.070241 | -61.8759 | 62.9333 | -62.0682 | -61.9583 | 62.709 | 0.091553 | 0.059509 | 0.15106 | 62.915 | -62.0499 | -0.2243 | -0.077819 | -0.032044 | -0.11444 | -0.30212 | -0.20599 | -0.09613 | 0.19226 | 61.9034 | 61.9949 | 124.5529 | 124.7772 | -0.032044 | 124.7589 | 61.9354 | -0.20599 | 124.7772 | -0.032044 | 61.9354 | 124.5529 | 124.7589 | -125.0793 | -125.061
58.375 | 125.1297 | -61.8164 | 63.0203 | -0.1799 | 0.011093 | 0.015092 | -0.00011753 | 0.070284 | -0.00025639 | 0.069173 | -61.8484 | 62.8738 | -62.0407 | -61.9354 | 62.7869 | 0.16022 | -0.041199 | 0.25177 | 62.8876 | -61.9995 | -0.2243 | -0.14648 | -0.032044 | -0.11902 | -0.23346 | -0.18311 | -0.13275 | 0.19226 | 61.7752 | 62.0682 | 124.6033 | 124.6902 | -0.032044 | 124.704 | 61.9766 | -0.18311 | 124.6902 | -0.032044 | 61.9766 | 124.6033 | 124.704 | -125.061 | -125.0198
59.375 | 125.0931 | -61.821 | 63.0066 | -0.28671 | 0.013016 | 0.012529 | 0.0028733 | 0.068789 | -0.002179 | 0.067464 | -61.8668 | 62.8784 | -62.0316 | -61.9583 | 62.7502 | 0.13733 | 0.068665 | 0.21057 | 62.8784 | -62.0407 | -0.21057 | -0.12817 | -0.045776 | -0.13733 | -0.25635 | -0.21973 | -0.12817 | 0.16479 | 61.8896 | 62.0316 | 124.5712 | 124.6994 | -0.045776 | 124.6994 | 61.9583 | -0.21973 | 124.6994 | -0.045776 | 61.9583 | 124.5712 | 124.6994 | -125.0381 | -125.0473
60.375 | 125.0931 | -61.8256 | 62.9974 | -0.042572 | 0.012162 | 0.014665 | 0.0018051 | 0.06708 | -0.0011108 | 0.06896 | -61.9354 | 62.8876 | -62.059 | -62.0041 | 62.7274 | 0.073242 | -0.045776 | 0.15564 | 62.8784 | -62.027 | -0.23346 | -0.10986 | -0.10986 | -0.17853 | -0.27008 | -0.20142 | -0.11902 | 0.1236 | 61.7798 | 61.9812 | 124.5529 | 124.7131 | -0.10986 | 124.704 | 61.8988 | -0.20142 | 124.7131 | -0.10986 | 61.8988 | 124.5529 | 124.704 | -125.0565 | -125.0244
61.375 | 125.1617 | -61.8118 | 63.0203 | -0.21042 | 0.013871 | 0.011461 | 0.0033005 | 0.067721 | -0.00068359 | 0.070241 | -61.853 | 62.8693 | -62.0361 | -61.9217 | 62.7914 | 0.16479 | -0.018311 | 0.25635 | 62.883 | -61.9995 | -0.2243 | -0.15106 | -0.041198 | -0.10986 | -0.22888 | -0.18768 | -0.13733 | 0.18311 | 61.7935 | 62.0682 | 124.6033 | 124.6811 | -0.041198 | 124.6948 | 61.9766 | -0.18768 | 124.6811 | -0.041198 | 61.9766 | 124.6033 | 124.6948 | -125.0565 | -125.0198
62.375 | 125.1114 | -61.8118 | 63.0203 | -0.20279 | 0.01323 | 0.012102 | 0.0054367 | 0.066225 | -0.0023926 | 0.067678 | -61.8759 | 62.8922 | -62.059 | -61.9308 | 62.764 | 0.14648 | 0.027466 | 0.2243 | 62.9059 | -62.0407 | -0.24719 | -0.12817 | -0.064087 | -0.11902 | -0.25635 | -0.22888 | -0.11444 | 0.18311 | 61.8393 | 62.0361 | 124.5758 | 124.704 | -0.064087 | 124.7177 | 61.9583 | -0.22888 | 124.704 | -0.064087 | 61.9583 | 124.5758 | 124.7177 | -125.0793 | -125.061
63.375 | 125.1343 | -61.7844 | 63.0432 | -0.11887 | 0.013016 | 0.017656 | 0.00030967 | 0.06708 | -0.003247 | 0.069387 | -61.8622 | 62.8601 | -62.027 | -61.9171 | 62.8052 | 0.16022 | -0.064087 | 0.2655 | 62.8967 | -62.0224 | -0.24262 | -0.18311 | -0.07782 | -0.13275 | -0.23804 | -0.23804 | -0.14648 | 0.16479 | 61.7203 | 62.0499 | 124.5895 | 124.6445 | -0.07782 | 124.6811 | 61.9446 | -0.23804 | 124.6445 | -0.07782 | 61.9446 | 124.5895 | 124.6811 | -125.0702 | -125.0656
64.375 | 125.0565 | -61.8439 | 62.9929 | 0.087128 | 0.016007 | 0.016588 | 0.0011643 | 0.068148 | -0.0017518 | 0.069814 | -61.7935 | 62.8464 | -62.059 | -62.0178 | 62.6862 | 0.027466 | -0.10529 | 0.10986 | 62.8555 | -62.0544 | -0.21515 | -0.14648 | 0.050354 | -0.17395 | -0.3067 | -0.21057 | -0.13733 | 0.2655 | 61.7386 | 61.9537 | 124.53 | 124.6902 | 0.050354 | 124.6994 | 61.8713 | -0.21057 | 124.6902 | 0.050354 | 61.8713 | 124.53 | 124.6994 | -125.0519 | -125.0473
65.375 | 125.0748 | -61.8301 | 63.0112 | -0.11124 | 0.013443 | 0.015092 | 0.0020187 | 0.065584 | -4.2788e-05 | 0.068746 | -61.9263 | 62.8647 | -62.0636 | -62.0041 | 62.6999 | 0.059509 | -0.054932 | 0.14191 | 62.8967 | -62.0407 | -0.23346 | -0.14648 | -0.096131 | -0.17395 | -0.31128 | -0.21057 | -0.11444 | 0.13733 | 61.7752 | 61.972 | 124.53 | 124.6948 | -0.096131 | 124.7269 | 61.8896 | -0.21057 | 124.6948 | -0.096131 | 61.8896 | 124.53 | 124.7269 | -125.0748 | -125.0519
66.375 | 125.1022 | -61.8347 | 62.9929 | 0.11765 | 0.012162 | 0.018724 | 0.0050095 | 0.067934 | -0.00025639 | 0.069387 | -61.8713 | 62.8418 | -62.0361 | -61.9492 | 62.7228 | 0.059509 | -0.18768 | 0.16022 | 62.8372 | -62.0407 | -0.20142 | -0.15106 | -0.036621 | -0.11444 | -0.27008 | -0.20599 | -0.15564 | 0.16479 | 61.647 | 61.9949 | 124.5575 | 124.6765 | -0.036621 | 124.6719 | 61.8942 | -0.20599 | 124.6765 | -0.036621 | 61.8942 | 124.5575 | 124.6719 | -125.029 | -125.0336
67.3906 | 125.0885 | -61.8118 | 63.0157 | -0.21042 | 0.01088 | 0.015733 | 0.0037277 | 0.068361 | 0.00017081 | 0.0696 | -61.8576 | 62.9105 | -62.0361 | -61.9354 | 62.7594 | 0.13733 | -0.009155 | 0.25177 | 62.8876 | -62.0178 | -0.2243 | -0.10529 | -0.045776 | -0.1236 | -0.25635 | -0.20599 | -0.12817 | 0.17853 | 61.8027 | 62.0636 | 124.5712 | 124.7223 | -0.045776 | 124.6994 | 61.9492 | -0.20599 | 124.7223 | -0.045776 | 61.9492 | 124.5712 | 124.6994 | -125.0519 | -125.0336
68.375 | 125.0931 | -61.8118 | 62.9745 | 0.1329 | 0.013016 | 0.018938 | 0.0062913 | 0.068361 | -0.0019654 | 0.070241 | -61.8622 | 62.8693 | -62.0407 | -61.9537 | 62.7136 | 0.064087 | -0.20142 | 0.13275 | 62.8281 | -62.0453 | -0.22888 | -0.10529 | -0.050354 | -0.14191 | -0.26093 | -0.23346 | -0.14648 | 0.17853 | 61.6104 | 61.9446 | 124.5255 | 124.6811 | -0.050354 | 124.6399 | 61.8759 | -0.23346 | 124.6811 | -0.050354 | 61.8759 | 124.5255 | 124.6399 | -125.0153 | -125.0198
69.375 | 125.0656 | -61.8347 | 62.9837 | 0.11002 | 0.016434 | 0.016374 | 0.0024461 | 0.06943 | -0.00046999 | 0.068532 | -61.8942 | 62.8647 | -62.0407 | -62.0132 | 62.7869 | 0.18768 | -0.23804 | 0.082397 | 62.8693 | -62.0544 | -0.20599 | -0.11902 | -0.059509 | -0.17853 | -0.19684 | -0.21973 | -0.11444 | 0.14648 | 61.5967 | 61.9171 | 124.6216 | 124.6994 | -0.059509 | 124.704 | 62.0224 | -0.21973 | 124.6994 | -0.059509 | 62.0224 | 124.6216 | 124.704 | -125.0244 | -125.0381
70.375 | 125.0793 | -61.8439 | 62.97 | 0.11002 | 0.015152 | 0.016588 | 0.0045823 | 0.06708 | -0.003247 | 0.069387 | -61.8759 | 62.8555 | -62.0544 | -61.972 | 62.7411 | 0.041199 | -0.15564 | 0.13275 | 62.8464 | -62.0636 | -0.21057 | -0.11444 | -0.032044 | -0.12817 | -0.22888 | -0.21973 | -0.1236 | 0.17853 | 61.6882 | 61.9766 | 124.585 | 124.6994 | -0.032044 | 124.6902 | 61.8851 | -0.21973 | 124.6994 | -0.032044 | 61.8851 | 124.585 | 124.6902 | -125.0244 | -125.0336
71.375 | 125.148 | -61.8347 | 63.0066 | -0.057831 | 0.013871 | 0.015092 | 0.0015915 | 0.068361 | 0.00059821 | 0.068532 | -61.9263 | 62.8647 | -62.0453 | -61.9766 | 62.7182 | 0.091553 | -0.064087 | 0.16022 | 62.8922 | -62.0499 | -0.21057 | -0.14191 | -0.091553 | -0.14191 | -0.28839 | -0.21515 | -0.11444 | 0.11902 | 61.7706 | 61.9949 | 124.5529 | 124.6994 | -0.091553 | 124.7269 | 61.9263 | -0.21515 | 124.6994 | -0.091553 | 61.9263 | 124.5529 | 124.7269 | -125.0519 | -125.0565
72.375 | 125.0839 | -61.8393 | 62.9974 | 0.041351 | 0.011307 | 0.018297 | 0.0037277 | 0.068361 | -0.0013244 | 0.069387 | -61.9217 | 62.8738 | -62.0407 | -62.0132 | 62.6862 | 0.045776 | -0.073242 | 0.12817 | 62.8601 | -62.0956 | -0.20142 | -0.1236 | -0.082398 | -0.17395 | -0.31128 | -0.25635 | -0.13733 | 0.11902 | 61.7661 | 61.9675 | 124.5255 | 124.7131 | -0.082398 | 124.6994 | 61.8851 | -0.25635 | 124.7131 | -0.082398 | 61.8851 | 124.5255 | 124.6994 | -125.0381 | -125.0931
73.375 | 125.1114 | -61.8393 | 62.9791 | 0.19394 | 0.014084 | 0.017015 | 0.0071457 | 0.068361 | -0.00089719 | 0.071096 | -61.8713 | 62.8784 | -62.059 | -61.9629 | 62.7319 | 0.045776 | -0.1831 | 0.11902 | 62.8326 | -62.0682 | -0.21973 | -0.10071 | -0.032044 | -0.1236 | -0.24719 | -0.22888 | -0.14648 | 0.18768 | 61.6562 | 61.9583 | 124.5712 | 124.7177 | -0.032044 | 124.6719 | 61.8851 | -0.22888 | 124.7177 | -0.032044 | 61.8851 | 124.5712 | 124.6719 | -125.0381 | -125.0473
74.375 | 125.0336 | -61.8393 | 62.9883 | 0.16342 | 0.013871 | 0.016374 | 0.0080003 | 0.071993 | -0.00089719 | 0.070882 | -61.94 | 62.9288 | -62.0728 | -62.0224 | 62.645 | -0.027466 | -0.10071 | 0.050354 | 62.8738 | -62.1002 | -0.23346 | -0.059509 | -0.10071 | -0.18311 | -0.34332 | -0.26093 | -0.11444 | 0.13275 | 61.7386 | 61.8896 | 124.4843 | 124.7681 | -0.10071 | 124.7131 | 61.8118 | -0.26093 | 124.7681 | -0.10071 | 61.8118 | 124.4843 | 124.7131 | -125.061 | -125.0885
75.375 | 125.0656 | -61.8256 | 62.9929 | 0.10239 | 0.016434 | 0.017656 | 0.0011643 | 0.06943 | 0.0010254 | 0.0696 | -61.908 | 62.8784 | -62.0499 | -62.0041 | 62.6953 | 0.032043 | -0.091553 | 0.10986 | 62.8784 | -62.0865 | -0.2243 | -0.11444 | -0.082397 | -0.17853 | -0.29755 | -0.26093 | -0.11444 | 0.14191 | 61.734 | 61.9354 | 124.5209 | 124.704 | -0.082397 | 124.704 | 61.8576 | -0.26093 | 124.704 | -0.082397 | 61.8576 | 124.5209 | 124.704 | -125.0427 | -125.0793
76.375 | 125.0153 | -61.8805 | 62.9883 | 0.19394 | 0.014084 | 0.018724 | 0.0069321 | 0.069216 | 0.00059821 | 0.069173 | -61.9263 | 62.9562 | -62.0819 | -62.0087 | 62.6724 | -0.009155 | -0.045776 | 0.17853 | 62.8967 | -62.0544 | -0.20142 | -0.032043 | -0.045777 | -0.12817 | -0.31586 | -0.17395 | -0.091552 | 0.15564 | 61.8347 | 62.059 | 124.5529 | 124.8367 | -0.045777 | 124.7772 | 61.8713 | -0.17395 | 124.8367 | -0.045777 | 61.8713 | 124.5529 | 124.7772 | -125.0702 | -125.0427
77.375 | 125.1205 | -61.8073 | 63.0112 | -0.24094 | 0.013871 | 0.011675 | 0.0015915 | 0.070711 | -0.0028198 | 0.066396 | -61.8576 | 62.9196 | -62.0407 | -61.9034 | 62.7914 | 0.17853 | -0.082397 | 0.2655 | 62.8784 | -62.0178 | -0.23346 | -0.091552 | -0.050354 | -0.09613 | -0.21973 | -0.21057 | -0.13275 | 0.1831 | 61.7249 | 62.0728 | 124.5987 | 124.7269 | -0.050354 | 124.6857 | 61.9858 | -0.21057 | 124.7269 | -0.050354 | 61.9858 | 124.5987 | 124.6857 | -125.0519 | -125.029
78.375 | 125.0153 | -61.8576 | 63.0386 | 0.15579 | 0.012802 | 0.016161 | 0.010136 | 0.068361 | -0.0015382 | 0.072378 | -61.9492 | 62.9608 | -62.1048 | -62.0453 | 62.6312 | -0.032043 | -0.036621 | 0.009155 | 62.8784 | -62.1002 | -0.24719 | -0.07782 | -0.091553 | -0.18768 | -0.40741 | -0.24262 | -0.16022 | 0.15564 | 61.821 | 61.8668 | 124.4888 | 124.8184 | -0.091553 | 124.736 | 61.8256 | -0.24262 | 124.8184 | -0.091553 | 61.8256 | 124.4888 | 124.736 | -125.1434 | -125.1389
79.375 | 125.0977 | -61.8347 | 62.9745 | 0.20157 | 0.014298 | 0.019151 | 0.0056503 | 0.071139 | -0.0015382 | 0.069387 | -61.8439 | 62.8784 | -62.0544 | -61.9629 | 62.7548 | 0.054932 | -0.15564 | 0.13733 | 62.8601 | -62.0728 | -0.21973 | -0.09613 | -0.009155 | -0.12817 | -0.21973 | -0.23804 | -0.11444 | 0.21057 | 61.6791 | 61.972 | 124.5895 | 124.7131 | -0.009155 | 124.6948 | 61.8896 | -0.23804 | 124.7131 | -0.009155 | 61.8896 | 124.5895 | 124.6948 | -125.029 | -125.0473
80.375 | 125.1068 | -61.8439 | 62.9837 | 0.033722 | 0.014725 | 0.019365 | 0.0056503 | 0.071993 | -0.00089719 | 0.068105 | -61.8805 | 62.9105 | -62.059 | -61.9675 | 62.7228 | 0.050354 | -0.17395 | 0.12817 | 62.8555 | -62.0544 | -0.21515 | -0.073243 | -0.036621 | -0.1236 | -0.26093 | -0.21057 | -0.12817 | 0.17853 | 61.6699 | 61.972 | 124.5666 | 124.7543 | -0.036621 | 124.6994 | 61.8942 | -0.21057 | 124.7543 | -0.036621 | 61.8942 | 124.5666 | 124.6994 | -125.0427 | -125.0381
81.375 | 125.1297 | -61.821 | 62.9608 | 0.041351 | 0.013657 | 0.018297 | 0.0075729 | 0.070711 | -0.00025639 | 0.070455 | -61.8805 | 62.9196 | -62.0728 | -61.972 | 62.7228 | 0.059509 | -0.16022 | 0.12817 | 62.8601 | -62.0728 | -0.25177 | -0.041198 | -0.059509 | -0.15106 | -0.23804 | -0.25177 | -0.10071 | 0.19226 | 61.6608 | 61.9492 | 124.5438 | 124.7406 | -0.059509 | 124.6811 | 61.8805 | -0.25177 | 124.7406 | -0.059509 | 61.8805 | 124.5438 | 124.6811 | -125.0336 | -125.0336
82.375 | 125.0977 | -61.8347 | 62.9791 | 0.087128 | 0.014298 | 0.01552 | 0.0013779 | 0.069216 | 0.00017081 | 0.069814 | -61.9217 | 62.8967 | -62.059 | -62.0132 | 62.6816 | 0.032043 | -0.082397 | 0.10986 | 62.8601 | -62.0911 | -0.2243 | -0.082397 | -0.086975 | -0.17853 | -0.29755 | -0.25635 | -0.11902 | 0.13733 | 61.7523 | 61.9446 | 124.5163 | 124.7314 | -0.086975 | 124.6948 | 61.8668 | -0.25635 | 124.7314 | -0.086975 | 61.8668 | 124.5163 | 124.6948 | -125.0381 | -125.0702
83.375 | 125.1114 | -61.8164 | 62.9745 | 0.17868 | 0.014511 | 0.022356 | 0.0054367 | 0.069002 | -0.0013244 | 0.068319 | -61.8713 | 62.8876 | -62.0636 | -61.972 | 62.7365 | 0.059509 | -0.17395 | 0.14648 | 62.851 | -62.0819 | -0.24719 | -0.086975 | -0.054932 | -0.15564 | -0.23804 | -0.2655 | -0.1236 | 0.19226 | 61.6425 | 61.9629 | 124.5529 | 124.704 | -0.054932 | 124.6674 | 61.8759 | -0.2655 | 124.704 | -0.054932 | 61.8759 | 124.5529 | 124.6674 | -125.0381 | -125.0565
84.375 | 125.0336 | -61.8347 | 63.0249 | 0.1329 | 0.01558 | 0.017656 | 0.0071457 | 0.069643 | -0.0019654 | 0.06896 | -61.94 | 62.9745 | -62.1002 | -62.027 | 62.645 | -0.022888 | -0.091553 | 0.050354 | 62.8693 | -62.0911 | -0.2655 | -0.050354 | -0.10529 | -0.19226 | -0.37994 | -0.25635 | -0.15564 | 0.16022 | 61.7432 | 61.8851 | 124.4797 | 124.8093 | -0.10529 | 124.704 | 61.8118 | -0.25635 | 124.8093 | -0.10529 | 61.8118 | 124.4797 | 124.704 | -125.1251 | -125.116
85.375 | 125.1526 | -61.8118 | 62.9562 | 0.18631 | 0.014939 | 0.014452 | 0.0069321 | 0.071566 | -0.0011108 | 0.070028 | -61.853 | 62.915 | -62.0682 | -61.9629 | 62.7274 | 0.064087 | -0.19226 | 0.14191 | 62.8555 | -62.0773 | -0.25635 | -0.041199 | -0.041198 | -0.15106 | -0.22888 | -0.2655 | -0.10071 | 0.21515 | 61.6196 | 61.9537 | 124.5392 | 124.7269 | -0.041198 | 124.6674 | 61.8759 | -0.2655 | 124.7269 | -0.041198 | 61.8759 | 124.5392 | 124.6674 | -125.0244 | -125.0336
86.375 | 125.0061 | -61.853 | 63.0066 | 0.14816 | 0.014298 | 0.014879 | 0.0075729 | 0.070925 | -0.00089719 | 0.070455 | -61.9492 | 62.9883 | -62.1048 | -62.0682 | 62.6221 | -0.045776 | -0.018311 | 0.018311 | 62.915 | -62.1048 | -0.25177 | -0.018311 | -0.096131 | -0.21515 | -0.38452 | -0.25177 | -0.091553 | 0.15564 | 61.8347 | 61.8713 | 124.4751 | 124.8413 | -0.096131 | 124.7681 | 61.8073 | -0.25177 | 124.8413 | -0.096131 | 61.8073 | 124.4751 | 124.7681 | -125.1114 | -125.1114
87.375 | 125.0885 | -61.8484 | 63.0341 | 0.14816 | 0.017075 | 0.01787 | 0.0058639 | 0.074984 | -4.2788e-05 | 0.070241 | -61.9263 | 62.9608 | -62.1048 | -62.0316 | 62.6678 | 0.004578 | -0.10071 | 0.054932 | 62.8876 | -62.0911 | -0.25635 | -0.073243 | -0.07782 | -0.1831 | -0.36621 | -0.24261 | -0.14648 | 0.17853 | 61.7477 | 61.9034 | 124.5163 | 124.8093 | -0.07782 | 124.736 | 61.853 | -0.24261 | 124.8093 | -0.07782 | 61.853 | 124.5163 | 124.736 | -125.1389 | -125.1251
88.375 | 125.1526 | -61.853 | 62.9562 | 0.42282 | 0.016434 | 0.018724 | 0.0043687 | 0.072634 | -0.00068359 | 0.071096 | -61.8713 | 62.9242 | -62.0728 | -61.9949 | 62.709 | 0.054932 | -0.16022 | 0.10986 | 62.8876 | -62.0544 | -0.21973 | -0.032044 | -0.018311 | -0.14191 | -0.24719 | -0.20142 | -0.068665 | 0.20142 | 61.6928 | 61.9629 | 124.5621 | 124.7772 | -0.018311 | 124.7406 | 61.908 | -0.20142 | 124.7772 | -0.018311 | 61.908 | 124.5621 | 124.7406 | -125.029 | -125.0107
89.375 | 125.0381 | -61.8851 | 62.9974 | 0.14053 | 0.014939 | 0.017229 | 0.0065049 | 0.071352 | -0.0019654 | 0.068319 | -61.9492 | 62.97 | -62.0865 | -62.0682 | 62.6404 | -0.045776 | -0.018311 | 0.013733 | 62.9333 | -62.1094 | -0.20142 | -0.027466 | -0.064087 | -0.1831 | -0.35706 | -0.2243 | -0.064087 | 0.13733 | 61.8668 | 61.8988 | 124.5255 | 124.855 | -0.064087 | 124.8184 | 61.8393 | -0.2243 | 124.855 | -0.064087 | 61.8393 | 124.5255 | 124.8184 | -125.0839 | -125.1068
90.375 | 124.9374 | -61.8851 | 63.0249 | 0.018463 | 0.016861 | 0.020219 | 0.0062913 | 0.072634 | -0.0015382 | 0.0696 | -61.9492 | 62.9654 | -62.0956 | -62.0728 | 62.6175 | -0.036621 | 0.045776 | 0.013733 | 62.9379 | -62.1231 | -0.21057 | -0.059509 | -0.064087 | -0.18768 | -0.40741 | -0.23804 | -0.086975 | 0.14648 | 61.9308 | 61.8988 | 124.5026 | 124.8505 | -0.064087 | 124.823 | 61.8485 | -0.23804 | 124.8505 | -0.064087 | 61.8485 | 124.5026 | 124.823 | -125.1205 | -125.148
91.375 | 125.1205 | -61.8484 | 62.9471 | 0.18631 | 0.013016 | 0.017656 | 0.0033005 | 0.073916 | -0.0015382 | 0.070241 | -61.8988 | 62.9517 | -62.0819 | -61.9766 | 62.7136 | 0.059509 | -0.17395 | 0.11902 | 62.9013 | -62.059 | -0.23346 | 0.004577 | -0.050354 | -0.12817 | -0.23346 | -0.21057 | -0.045777 | 0.18311 | 61.6745 | 61.9675 | 124.5621 | 124.8001 | -0.050354 | 124.7498 | 61.908 | -0.21057 | 124.8001 | -0.050354 | 61.908 | 124.5621 | 124.7498 | -125.029 | -125.0061
92.375 | 125.0427 | -61.8668 | 63.002 | 0.10239 | 0.017289 | 0.01851 | 0.0047959 | 0.072848 | -0.00089719 | 0.0696 | -61.94 | 62.9562 | -62.1002 | -62.0636 | 62.6175 | -0.036621 | -0.013733 | 0.013733 | 62.9333 | -62.1414 | -0.23346 | -0.045776 | -0.073242 | -0.19684 | -0.38452 | -0.27466 | -0.068664 | 0.16022 | 61.853 | 61.8805 | 124.4843 | 124.823 | -0.073242 | 124.8001 | 61.8301 | -0.27466 | 124.823 | -0.073242 | 61.8301 | 124.4843 | 124.8001 | -125.1022 | -125.1434
93.375 | 124.942 | -61.8805 | 63.0157 | 0.041351 | 0.015152 | 0.014238 | 0.0088547 | 0.073061 | -0.00046999 | 0.069173 | -61.9263 | 62.9929 | -62.0819 | -62.0911 | 62.6038 | -0.036621 | 0.045776 | 0.027466 | 62.9471 | -62.1185 | -0.20142 | -0.022888 | -0.045777 | -0.21057 | -0.41199 | -0.23804 | -0.068664 | 0.15564 | 61.9263 | 61.908 | 124.4843 | 124.8734 | -0.045777 | 124.8276 | 61.8439 | -0.23804 | 124.8734 | -0.045777 | 61.8439 | 124.4843 | 124.8276 | -125.0977 | -125.1343
94.375 | 124.9832 | -61.8805 | 62.9974 | -0.034943 | 0.017289 | 0.020433 | 0.0073593 | 0.075411 | -4.2788e-05 | 0.069814 | -61.8988 | 62.9791 | -62.059 | -62.0132 | 62.6816 | 0.036621 | 0.041199 | 0.11444 | 62.9517 | -62.1002 | -0.17853 | -0.018311 | -0.018311 | -0.13275 | -0.31586 | -0.21973 | -0.045777 | 0.16022 | 61.9217 | 61.9949 | 124.5621 | 124.8596 | -0.018311 | 124.8322 | 61.9171 | -0.21973 | 124.8596 | -0.018311 | 61.9171 | 124.5621 | 124.8322 | -125.0565 | -125.0977
95.375 | 124.9695 | -61.8713 | 63.0157 | -0.0044251 | 0.017502 | 0.016588 | 0.0067185 | 0.073916 | -0.0011108 | 0.0696 | -61.9766 | 62.9791 | -62.0819 | -62.0956 | 62.59 | -0.064087 | 0.018311 | 0.009155 | 62.9425 | -62.0956 | -0.21057 | -0.036621 | -0.10529 | -0.2243 | -0.42572 | -0.2243 | -0.073242 | 0.10529 | 61.8896 | 61.8805 | 124.4614 | 124.8505 | -0.10529 | 124.8138 | 61.8073 | -0.2243 | 124.8505 | -0.10529 | 61.8073 | 124.4614 | 124.8138 | -125.0977 | -125.1114
96.375 | 124.9695 | -61.8576 | 62.9837 | 0.094757 | 0.015152 | 0.019151 | 0.0050095 | 0.071566 | -0.00089719 | 0.071523 | -61.9675 | 62.9837 | -62.1002 | -62.1002 | 62.6038 | -0.041199 | 0.013733 | 0.004578 | 62.9425 | -62.1048 | -0.24262 | 0 | -0.10986 | -0.24262 | -0.37994 | -0.24719 | -0.041199 | 0.13275 | 61.8713 | 61.8622 | 124.4614 | 124.8413 | -0.10986 | 124.8001 | 61.8164 | -0.24719 | 124.8413 | -0.10986 | 61.8164 | 124.4614 | 124.8001 | -125.0839 | -125.0885
97.375 | 125.0519 | -61.8759 | 62.9929 | 0.12527 | 0.014939 | 0.01552 | 0.0037277 | 0.074129 | -0.0013244 | 0.068746 | -61.9446 | 62.9791 | -62.0819 | -62.0499 | 62.5992 | -0.045776 | -0.018311 | -0.018311 | 62.9196 | -62.1094 | -0.20599 | -0.013733 | -0.068664 | -0.17395 | -0.39368 | -0.23346 | -0.073242 | 0.13733 | 61.8576 | 61.8576 | 124.4751 | 124.855 | -0.068664 | 124.7955 | 61.8301 | -0.23346 | 124.855 | -0.068664 | 61.8301 | 124.4751 | 124.7955 | -125.0748 | -125.1022
98.375 | 125.0565 | -61.8484 | 63.002 | -0.07309 | 0.014511 | 0.022356 | 0.0073593 | 0.073275 | -0.0023926 | 0.068746 | -61.8805 | 62.9791 | -62.027 | -61.9949 | 62.6999 | 0.064087 | 0.018311 | 0.13733 | 62.9288 | -62.0773 | -0.17853 | -0.022888 | -0.032043 | -0.14648 | -0.30212 | -0.22888 | -0.073242 | 0.14648 | 61.8668 | 61.9858 | 124.5483 | 124.8276 | -0.032043 | 124.7772 | 61.9125 | -0.22888 | 124.8276 | -0.032043 | 61.9125 | 124.5483 | 124.7772 | -125.029 | -125.0793
99.375 | 124.9832 | -61.9034 | 62.9929 | 0.11002 | 0.01088 | 0.016161 | 0.0043687 | 0.071566 | 0.0010254 | 0.070669 | -61.9766 | 62.9608 | -62.1048 | -62.0956 | 62.6175 | -0.054932 | 0.018311 | 0 | 62.9608 | -62.1231 | -0.20142 | -0.032044 | -0.073243 | -0.19226 | -0.37537 | -0.21973 | -0.032044 | 0.12817 | 61.9217 | 61.9034 | 124.5209 | 124.8642 | -0.073243 | 124.8642 | 61.8484 | -0.21973 | 124.8642 | -0.073243 | 61.8484 | 124.5209 | 124.8642 | -125.0977 | -125.116
100.375 | 125.0153 | -61.853 | 63.0386 | -0.21042 | 0.017502 | 0.021715 | 0.0035141 | 0.07242 | -0.00068359 | 0.069387 | -62.233 | 62.9562 | -62.0865 | -62.0728 | 62.709 | 0.07782 | 0.14648 | 0.15564 | 62.9883 | -62.059 | -0.23346 | -0.082397 | -0.37994 | -0.21973 | -0.32959 | -0.20599 | -0.050354 | -0.14648 | 61.9995 | 62.0087 | 124.5621 | 124.8093 | -0.37994 | 124.8413 | 61.9308 | -0.20599 | 124.8093 | -0.37994 | 61.9308 | 124.5621 | 124.8413 | -125.1251 | -125.0977
101.375 | 125.0519 | -61.8393 | 63.0295 | -0.29434 | 0.016007 | 0.01851 | 0.0041549 | 0.07007 | 0.00038461 | 0.070241 | -61.908 | 63.0112 | -62.0499 | -61.9949 | 62.7045 | 0.091553 | 0.10986 | 0.17395 | 62.9562 | -62.0728 | -0.21057 | -0.018311 | -0.068665 | -0.15564 | -0.32501 | -0.23346 | -0.073242 | 0.14191 | 61.9492 | 62.0132 | 124.5438 | 124.8505 | -0.068665 | 124.7955 | 61.9308 | -0.23346 | 124.8505 | -0.068665 | 61.9308 | 124.5438 | 124.7955 | -125.0793 | -125.1022
102.375 | 125.0244 | -61.8622 | 63.0203 | -0.17227 | 0.014511 | 0.01787 | 0.0065049 | 0.073488 | -0.0043152 | 0.06896 | -61.8668 | 62.9791 | -62.0499 | -61.9995 | 62.6953 | 0.073242 | 0.045776 | 0.16479 | 62.9425 | -62.0728 | -0.18768 | -0.041199 | -0.004577 | -0.13733 | -0.32501 | -0.21057 | -0.07782 | 0.18311 | 61.908 | 62.027 | 124.5575 | 124.8413 | -0.004577 | 124.8047 | 61.9354 | -0.21057 | 124.8413 | -0.004577 | 61.9354 | 124.5575 | 124.8047 | -125.0702 | -125.0931
103.375 | 125.0427 | -61.8484 | 63.0341 | -0.88181 | 0.014084 | 0.013811 | 0.0050095 | 0.073061 | 0.00059821 | 0.069814 | -61.908 | 63.002 | -62.0636 | -61.9995 | 62.6953 | 0.082397 | 0.07782 | 0.17853 | 62.9791 | -62.0819 | -0.21515 | -0.032044 | -0.059509 | -0.15106 | -0.33875 | -0.23346 | -0.054932 | 0.15564 | 61.9263 | 62.027 | 124.5438 | 124.8505 | -0.059509 | 124.8276 | 61.9308 | -0.23346 | 124.8505 | -0.059509 | 61.9308 | 124.5438 | 124.8276 | -125.0977 | -125.116
104.375 | 125.0977 | -61.853 | 63.0478 | -0.22568 | 0.014939 | 0.019365 | 0.0041549 | 0.073488 | 0.00059821 | 0.067678 | -61.8988 | 63.0112 | -62.1048 | -62.0041 | 62.6862 | -0.17395 | 0.2243 | 0.3067 | 62.97 | -62.0956 | -0.25177 | -0.036622 | -0.045777 | -0.15106 | -0.36163 | -0.24262 | -0.07782 | 0.20599 | 62.0773 | 62.1597 | 124.5392 | 124.8642 | -0.045777 | 124.823 | 61.6791 | -0.24262 | 124.8642 | -0.045777 | 61.6791 | 124.5392 | 124.823 | -125.1526 | -125.1434
105.375 | 125.0153 | -61.8439 | 63.0249 | -0.16464 | 0.014511 | 0.015947 | 0.0033005 | 0.073916 | -0.0011108 | 0.068105 | -61.9171 | 62.97 | -62.0773 | -62.027 | 62.677 | 0.059509 | 0.13733 | 0.15564 | 62.9517 | -62.0728 | -0.23346 | -0.054931 | -0.073242 | -0.18311 | -0.3479 | -0.22888 | -0.073242 | 0.16022 | 61.9812 | 61.9995 | 124.5209 | 124.8138 | -0.073242 | 124.7955 | 61.9034 | -0.22888 | 124.8138 | -0.073242 | 61.9034 | 124.5209 | 124.7955 | -125.1022 | -125.0977
106.375 | 125.0931 | -61.821 | 62.97 | 0.22446 | 0.016648 | 0.01787 | 0.0030869 | 0.071993 | -0.002179 | 0.069173 | -61.8759 | 62.9059 | -62.0865 | -61.8896 | 62.7045 | 0 | -0.10071 | 0.13275 | 62.9105 | -62.0453 | -0.2655 | -0.064087 | -0.054932 | -0.068664 | -0.2655 | -0.2243 | -0.05951 | 0.21057 | 61.7203 | 61.9537 | 124.5255 | 124.7269 | -0.054932 | 124.7314 | 61.821 | -0.2243 | 124.7269 | -0.054932 | 61.821 | 124.5255 | 124.7314 | -125.0565 | -125.0153
107.375 | 125.0336 | -61.8256 | 63.0249 | -0.23331 | 0.015793 | 0.017015 | 0.0033005 | 0.071779 | -0.0019654 | 0.070882 | -61.8851 | 62.9654 | -62.059 | -62.0041 | 62.6862 | 0.091553 | 0.091553 | 0.17853 | 62.9425 | -62.0728 | -0.23346 | -0.059509 | -0.059509 | -0.17853 | -0.33874 | -0.24719 | -0.082397 | 0.17395 | 61.9171 | 62.0041 | 124.5117 | 124.791 | -0.059509 | 124.7681 | 61.9171 | -0.24719 | 124.791 | -0.059509 | 61.9171 | 124.5117 | 124.7681 | -125.0839 | -125.0977
108.375 | 124.9786 | -61.8439 | 63.0524 | -0.28671 | 0.015152 | 0.016801 | 0.0015915 | 0.071139 | 0.00038461 | 0.068746 | -61.9308 | 62.9837 | -62.059 | -62.0361 | 62.6541 | 0.050354 | 0.16937 | 0.14648 | 62.9929 | -62.0819 | -0.21515 | -0.068664 | -0.086975 | -0.19226 | -0.39825 | -0.23804 | -0.059509 | 0.12817 | 62.0132 | 61.9904 | 124.498 | 124.8276 | -0.086975 | 124.8367 | 61.8942 | -0.23804 | 124.8276 | -0.086975 | 61.8942 | 124.498 | 124.8367 | -125.1114 | -125.1343
109.375 | 125.0381 | -61.8484 | 63.0295 | -0.22568 | 0.015152 | 0.01851 | 0.0037277 | 0.070711 | -0.0017518 | 0.06896 | -61.9034 | 62.97 | -62.0453 | -62.027 | 62.6541 | 0.054932 | 0.11902 | 0.14648 | 62.9745 | -62.0544 | -0.19684 | -0.059509 | -0.054931 | -0.17853 | -0.37537 | -0.20599 | -0.054932 | 0.14191 | 61.9675 | 61.9949 | 124.5026 | 124.8184 | -0.054931 | 124.823 | 61.9034 | -0.20599 | 124.8184 | -0.054931 | 61.9034 | 124.5026 | 124.823 | -125.0748 | -125.0839
110.375 | 125.0198 | -61.8668 | 63.0341 | -0.22568 | 0.014939 | 0.012743 | 0.0041549 | 0.070711 | -0.0028198 | 0.069814 | -61.9308 | 62.9837 | -62.0773 | -62.0407 | 62.6587 | 0.045776 | 0.13733 | 0.14648 | 62.9745 | -62.0773 | -0.21057 | -0.050354 | -0.064087 | -0.17395 | -0.37537 | -0.21057 | -0.05951 | 0.14648 | 62.0041 | 62.0132 | 124.5255 | 124.8505 | -0.064087 | 124.8413 | 61.9125 | -0.21057 | 124.8505 | -0.064087 | 61.9125 | 124.5255 | 124.8413 | -125.1114 | -125.1114
111.3906 | 124.9924 | -61.8851 | 63.002 | 0.1329 | 0.01622 | 0.019151 | 0.0058639 | 0.07242 | -0.00068359 | 0.070669 | -61.9629 | 62.9791 | -62.0773 | -62.0865 | 62.6083 | -0.045776 | 0.013733 | -0.004578 | 62.9379 | -62.1094 | -0.19226 | -0.022888 | -0.07782 | -0.20142 | -0.39368 | -0.2243 | -0.064087 | 0.11444 | 61.8988 | 61.8805 | 124.4934 | 124.8642 | -0.07782 | 124.823 | 61.8393 | -0.2243 | 124.8642 | -0.07782 | 61.8393 | 124.4934 | 124.823 | -125.0793 | -125.1114
112.375 | 124.9969 | -61.853 | 63.0478 | -0.2562 | 0.01323 | 0.014238 | 0.0026597 | 0.071993 | -0.0011108 | 0.0696 | -61.9354 | 62.97 | -62.0682 | -62.0499 | 62.6633 | 0.045776 | 0.16022 | 0.13275 | 62.9929 | -62.0728 | -0.21515 | -0.07782 | -0.082398 | -0.19684 | -0.38452 | -0.21973 | -0.054932 | 0.13275 | 62.0132 | 61.9858 | 124.5163 | 124.823 | -0.082398 | 124.8459 | 61.8988 | -0.21973 | 124.823 | -0.082398 | 61.8988 | 124.5163 | 124.8459 | -125.116 | -125.1205
113.375 | 125.0153 | -61.8393 | 63.0295 | -0.21042 | 0.013657 | 0.019792 | 0.0041549 | 0.071566 | -0.0013244 | 0.072378 | -61.9217 | 62.9791 | -62.059 | -62.0132 | 62.6587 | 0.041199 | 0.12817 | 0.15106 | 62.9791 | -62.0544 | -0.21973 | -0.050354 | -0.082398 | -0.17395 | -0.37079 | -0.21515 | -0.050354 | 0.13733 | 61.9675 | 61.9904 | 124.498 | 124.8184 | -0.082398 | 124.8184 | 61.8805 | -0.21515 | 124.8184 | -0.082398 | 61.8805 | 124.498 | 124.8184 | -125.0885 | -125.0839
114.375 | 124.9878 | -61.8484 | 63.0341 | -0.26382 | 0.014084 | 0.011888 | 0.0022323 | 0.071139 | 0.00081181 | 0.067251 | -61.9217 | 62.97 | -62.0636 | -62.0407 | 62.6495 | 0.036621 | 0.14648 | 0.14648 | 62.9745 | -62.0911 | -0.21515 | -0.064087 | -0.073242 | -0.19226 | -0.38452 | -0.24261 | -0.05951 | 0.14191 | 61.9949 | 61.9949 | 124.498 | 124.8184 | -0.073242 | 124.823 | 61.8851 | -0.24261 | 124.8184 | -0.073242 | 61.8851 | 124.498 | 124.823 | -125.0977 | -125.1251
115.375 | 125.0244 | -61.8393 | 63.0295 | -0.088349 | 0.013871 | 0.01787 | 0.0052231 | 0.072634 | -0.0015382 | 0.070669 | -61.8851 | 62.9562 | -62.0544 | -62.0087 | 62.6678 | 0.041199 | 0.009155 | 0.10071 | 62.9471 | -62.0728 | -0.21515 | -0.073242 | -0.045777 | -0.16937 | -0.36163 | -0.23346 | -0.082397 | 0.16937 | 61.8484 | 61.94 | 124.5071 | 124.7955 | -0.045777 | 124.7864 | 61.8805 | -0.23346 | 124.7955 | -0.045777 | 61.8805 | 124.5071 | 124.7864 | -125.0839 | -125.1022
116.3906 | 124.9741 | -61.8713 | 62.9974 | -0.44693 | 0.014939 | 0.017015 | 0.0043687 | 0.074129 | -0.0023926 | 0.070241 | -61.9446 | 62.97 | -62.0865 | -62.0865 | 62.6083 | -0.054932 | 0.018311 | 0.009155 | 62.9608 | -62.1094 | -0.21515 | -0.027466 | -0.073242 | -0.21515 | -0.3891 | -0.23804 | -0.036622 | 0.14191 | 61.8896 | 61.8805 | 124.4797 | 124.8413 | -0.073242 | 124.8322 | 61.8164 | -0.23804 | 124.8413 | -0.073242 | 61.8164 | 124.4797 | 124.8322 | -125.0839 | -125.1068
117.375 | 124.9878 | -61.8347 | 63.0386 | -0.23331 | 0.014298 | 0.012102 | 0.00073707 | 0.071779 | 0.0020934 | 0.069387 | -61.9354 | 62.9791 | -62.0728 | -62.0407 | 62.6633 | 0.045776 | 0.15106 | 0.13733 | 62.9837 | -62.0865 | -0.23804 | -0.059509 | -0.10071 | -0.20599 | -0.37537 | -0.25177 | -0.054931 | 0.13733 | 61.9858 | 61.972 | 124.498 | 124.8138 | -0.10071 | 124.8184 | 61.8805 | -0.25177 | 124.8138 | -0.10071 | 61.8805 | 124.498 | 124.8184 | -125.1114 | -125.1251
118.375 | 125.0107 | -61.8439 | 63.0066 | -0.34775 | 0.014511 | 0.018938 | 0.0013779 | 0.071566 | -0.00089719 | 0.06896 | -61.9217 | 62.9791 | -62.0773 | -62.0316 | 62.645 | 0.041199 | 0.14191 | 0.14191 | 62.9791 | -62.0728 | -0.23346 | -0.027466 | -0.07782 | -0.18768 | -0.36163 | -0.22888 | -0.027466 | 0.15564 | 61.9858 | 61.9858 | 124.4888 | 124.823 | -0.07782 | 124.823 | 61.8851 | -0.22888 | 124.823 | -0.07782 | 61.8851 | 124.4888 | 124.823 | -125.0839 | -125.0793
119.375 | 124.9969 | -61.853 | 63.0295 | -0.81314 | 0.014939 | 0.011675 | 0.0035141 | 0.069643 | -4.2788e-05 | 0.069387 | -61.9629 | 62.9379 | -62.0728 | -62.0453 | 62.6541 | 0.045776 | 0.13733 | 0.15564 | 62.9791 | -62.0682 | -0.21973 | -0.091553 | -0.10986 | -0.19226 | -0.37537 | -0.21515 | -0.050354 | 0.10986 | 61.9904 | 62.0087 | 124.5071 | 124.791 | -0.10986 | 124.8322 | 61.8988 | -0.21515 | 124.791 | -0.10986 | 61.8988 | 124.5071 | 124.8322 | -125.1022 | -125.0977
120.375 | 124.9512 | -61.8668 | 63.0386 | -0.43167 | 0.013016 | 0.009752 | 0.00095067 | 0.070498 | -0.0011108 | 0.06896 | -61.7706 | 62.9654 | -61.9995 | -62.0407 | 62.6862 | 0.064087 | 0.11444 | 0.14648 | 62.9791 | -62.0819 | -0.13275 | -0.073242 | 0.09613 | -0.17395 | -0.35248 | -0.21515 | -0.059509 | 0.22888 | 61.9812 | 62.0132 | 124.5529 | 124.8322 | 0.09613 | 124.8459 | 61.9308 | -0.21515 | 124.8322 | 0.09613 | 61.9308 | 124.5529 | 124.8459 | -125.0381 | -125.1205
121.3906 | 125.0839 | -61.8393 | 62.9562 | 0.05661 | 0.012375 | 0.014024 | 0.0039413 | 0.071779 | -0.0011108 | 0.070669 | -61.8668 | 62.9105 | -62.0316 | -61.972 | 62.7045 | 0.054932 | -0.17853 | 0.13275 | 62.8876 | -62.0773 | -0.19226 | -0.045777 | -0.027466 | -0.13275 | -0.25177 | -0.23804 | -0.068665 | 0.16479 | 61.6608 | 61.972 | 124.5438 | 124.7498 | -0.027466 | 124.7269 | 61.8942 | -0.23804 | 124.7498 | -0.027466 | 61.8942 | 124.5438 | 124.7269 | -124.9878 | -125.0336
122.375 | 124.9054 | -61.8347 | 62.9974 | -0.21042 | 0.015152 | 0.014879 | 0.0039413 | 0.068575 | -4.2788e-05 | 0.070882 | -61.8896 | 62.915 | -62.0316 | -61.9995 | 62.6724 | 0.073242 | 0.13275 | 0.42572 | 62.9883 | -62.0499 | -0.19684 | -0.082398 | -0.054931 | -0.1648 | -0.32501 | -0.21515 | -0.009156 | 0.14191 | 61.9675 | 62.2604 | 124.5071 | 124.7498 | -0.054931 | 124.823 | 61.908 | -0.21515 | 124.7498 | -0.054931 | 61.908 | 124.5071 | 124.823 | -125.029 | -125.0473
123.375 | 124.9741 | -61.8393 | 63.0524 | -0.16464 | 0.013871 | 0.01552 | 0.0024461 | 0.068148 | -0.0026062 | 0.0696 | -61.9308 | 62.97 | -62.0956 | -62.027 | 62.6587 | 0.041199 | 0.15564 | 0.14191 | 62.9791 | -62.0544 | -0.25635 | -0.082397 | -0.091553 | -0.18768 | -0.39368 | -0.21515 | -0.073242 | 0.16479 | 61.9949 | 61.9812 | 124.498 | 124.8093 | -0.091553 | 124.8184 | 61.8805 | -0.21515 | 124.8093 | -0.091553 | 61.8805 | 124.498 | 124.8184 | -125.148 | -125.1068
124.375 | 124.9786 | -61.8347 | 63.0432 | -0.18753 | 0.013871 | 0.013383 | 0.0030869 | 0.069857 | -0.0043152 | 0.069814 | -61.9217 | 62.9288 | -62.0544 | -62.0316 | 62.6633 | 0.050354 | 0.14648 | 0.15106 | 62.9929 | -62.0636 | -0.21973 | -0.11444 | -0.086975 | -0.19684 | -0.37994 | -0.22888 | -0.050354 | 0.13275 | 61.9812 | 61.9858 | 124.498 | 124.7635 | -0.086975 | 124.8276 | 61.8851 | -0.22888 | 124.7635 | -0.086975 | 61.8851 | 124.498 | 124.8276 | -125.0977 | -125.1068
125.375 | 125.0015 | -61.8256 | 63.0661 | -1.1107 | 0.014511 | 0.013811 | 0.0022323 | 0.069002 | -0.0019654 | 0.066823 | -61.9171 | 62.9654 | -62.0316 | -62.0041 | 62.6312 | 0.027466 | 0.14648 | 0.15106 | 62.9608 | -62.0636 | -0.20599 | -0.10071 | -0.091552 | -0.17853 | -0.43488 | -0.23804 | -0.10529 | 0.11444 | 61.972 | 61.9766 | 124.4568 | 124.791 | -0.091552 | 124.7864 | 61.853 | -0.23804 | 124.791 | -0.091552 | 61.853 | 124.4568 | 124.7864 | -125.0977 | -125.1297
126.375 | 124.9695 | -61.8439 | 63.0341 | -0.24857 | 0.014298 | 0.015947 | 0.0030869 | 0.070284 | -0.0019654 | 0.068105 | -61.9034 | 62.9242 | -62.0361 | -61.7981 | 62.6358 | -0.091553 | 0.068665 | 0.1831 | 62.9654 | -62.0728 | -0.19226 | -0.10986 | -0.059509 | 0.045776 | -0.39825 | -0.22888 | -0.068665 | 0.13275 | 61.9125 | 62.027 | 124.4797 | 124.7681 | -0.059509 | 124.8093 | 61.7523 | -0.22888 | 124.7681 | -0.059509 | 61.7523 | 124.4797 | 124.8093 | -125.0702 | -125.1068
127.375 | 125.0336 | -61.8118 | 63.1119 | -0.24094 | 0.012162 | 0.0093246 | 0.00095067 | 0.068575 | -0.0019654 | 0.0696 | -61.8805 | 62.915 | -62.0499 | -61.9949 | 62.6907 | 0.086975 | 0.10529 | 0.16937 | 62.9608 | -62.0224 | -0.23804 | -0.19684 | -0.068664 | -0.1831 | -0.42114 | -0.21057 | -0.15106 | 0.16937 | 61.9171 | 61.9812 | 124.5026 | 124.7269 | -0.068664 | 124.7726 | 61.8988 | -0.21057 | 124.7269 | -0.068664 | 61.8988 | 124.5026 | 124.7726 | -125.1617 | -125.1343
128.375 | 125.029 | -61.8256 | 63.0295 | -0.2562 | 0.012375 | 0.013811 | 0.0024461 | 0.070284 | -0.0028198 | 0.068319 | -61.8713 | 62.9242 | -62.0544 | -61.972 | 62.709 | 0.10986 | 0.073242 | 0.20599 | 62.9562 | -62.0407 | -0.22888 | -0.10529 | -0.045776 | -0.14648 | -0.32043 | -0.21515 | -0.073242 | 0.1831 | 61.8988 | 62.0316 | 124.5346 | 124.7498 | -0.045776 | 124.7818 | 61.9354 | -0.21515 | 124.7498 | -0.045776 | 61.9354 | 124.5346 | 124.7818 | -125.0839 | -125.0702
129.375 | 125.0244 | -61.821 | 63.0157 | -0.23331 | 0.015366 | 0.017229 | 0.0037277 | 0.066866 | -0.00068359 | 0.0696 | -61.8484 | 62.8922 | -62.0453 | -61.9537 | 62.7365 | 0.13275 | 0.054932 | 0.23346 | 62.9288 | -62.0682 | -0.2243 | -0.1236 | -0.027466 | -0.13275 | -0.27924 | -0.24719 | -0.086975 | 0.19684 | 61.8759 | 62.0544 | 124.5575 | 124.7131 | -0.027466 | 124.7498 | 61.9537 | -0.24719 | 124.7131 | -0.027466 | 61.9537 | 124.5575 | 124.7498 | -125.061 | -125.0839
130.375 | 125.0061 | -61.8668 | 63.0432 | -0.24094 | 0.014511 | 0.015947 | 0.0041549 | 0.071779 | -0.00068359 | 0.068105 | -61.9034 | 62.9059 | -62.0361 | -62.0132 | 62.6404 | 0.041199 | 0.14648 | 0.15564 | 62.9517 | -62.0682 | -0.16937 | -0.13733 | -0.036621 | -0.14648 | -0.40283 | -0.20142 | -0.091553 | 0.13275 | 62.0132 | 62.0224 | 124.5071 | 124.7726 | -0.036621 | 124.8184 | 61.908 | -0.20142 | 124.7726 | -0.036621 | 61.908 | 124.5071 | 124.8184 | -125.0793 | -125.1114
131.375 | 125.0107 | -61.853 | 63.0295 | -0.29434 | 0.012589 | 0.018083 | 0.0035141 | 0.068789 | -0.0023926 | 0.068105 | -61.8988 | 62.915 | -62.0361 | -61.972 | 62.6724 | 0.050354 | 0.46692 | -0.013733 | 62.9929 | -62.0453 | -0.18311 | -0.11444 | -0.045777 | -0.11902 | -0.35706 | -0.19226 | -0.036621 | 0.13733 | 62.3199 | 61.8393 | 124.5255 | 124.7681 | -0.045777 | 124.8459 | 61.9034 | -0.19226 | 124.7681 | -0.045777 | 61.9034 | 124.5255 | 124.8459 | -125.0656 | -125.0748
132.375 | 124.9741 | -61.8484 | 63.0341 | -0.27908 | 0.012802 | 0.012956 | 0.0050095 | 0.068148 | -0.00046999 | 0.070882 | -61.8896 | 62.9105 | -62.059 | -62.0041 | 62.6862 | 0.073242 | 0.12817 | 0.16937 | 62.9379 | -62.0728 | -0.21057 | -0.1236 | -0.041198 | -0.15564 | -0.3479 | -0.2243 | -0.096131 | 0.16937 | 61.9766 | 62.0178 | 124.5346 | 124.7589 | -0.041198 | 124.7864 | 61.9217 | -0.2243 | 124.7589 | -0.041198 | 61.9217 | 124.5346 | 124.7864 | -125.0931 | -125.1068
133.375 | 125.0198 | -61.8164 | 63.0249 | -0.2562 | 0.013657 | 0.019579 | 0.0037277 | 0.07007 | -0.00089719 | 0.067678 | -61.8713 | 62.9105 | -62.0544 | -61.9537 | 62.7045 | 0.10986 | 0.091553 | 0.19684 | 62.9471 | -62.0224 | -0.23804 | -0.11444 | -0.054932 | -0.13733 | -0.32043 | -0.20599 | -0.077819 | 0.1831 | 61.908 | 62.0132 | 124.5209 | 124.7269 | -0.054932 | 124.7635 | 61.9263 | -0.20599 | 124.7269 | -0.054932 | 61.9263 | 124.5209 | 124.7635 | -125.0793 | -125.0473
134.375 | 125.0015 | -61.8164 | 63.0295 | -0.21042 | 0.011734 | 0.015306 | 0.0039413 | 0.069002 | -0.0023926 | 0.068746 | -61.8668 | 62.8876 | -62.0407 | -61.9537 | 62.7182 | 0.11902 | 0.068665 | 0.20599 | 62.9517 | -62.0453 | -0.2243 | -0.14191 | -0.050354 | -0.13733 | -0.31128 | -0.22888 | -0.07782 | 0.17395 | 61.8851 | 62.0224 | 124.5346 | 124.704 | -0.050354 | 124.7681 | 61.9354 | -0.22888 | 124.704 | -0.050354 | 61.9354 | 124.5346 | 124.7681 | -125.0702 | -125.0748
135.375 | 125.029 | -61.8256 | 63.0203 | -0.24857 | 0.012162 | 0.014665 | 0.0041549 | 0.07007 | 0.00038461 | 0.068105 | -61.8622 | 62.9013 | -62.0224 | -61.9583 | 62.7319 | 0.11444 | 0.045776 | 0.22888 | 62.9379 | -62.0453 | -0.19684 | -0.11902 | -0.036621 | -0.13275 | -0.28839 | -0.21973 | -0.082398 | 0.16022 | 61.8713 | 62.0544 | 124.5575 | 124.7269 | -0.036621 | 124.7635 | 61.94 | -0.21973 | 124.7269 | -0.036621 | 61.94 | 124.5575 | 124.7635 | -125.0427 | -125.0656
136.375 | 125.0748 | -61.8164 | 63.0066 | -0.24857 | 0.012375 | 0.016588 | 0.0043687 | 0.069857 | -0.0019654 | 0.069173 | -61.8484 | 62.8876 | -62.0087 | -61.9446 | 62.7274 | 0.13275 | 0.041199 | 0.24719 | 62.9333 | -62.027 | -0.19226 | -0.11902 | -0.032044 | -0.12817 | -0.27924 | -0.21057 | -0.073242 | 0.16022 | 61.8576 | 62.0636 | 124.5438 | 124.704 | -0.032044 | 124.7498 | 61.9492 | -0.21057 | 124.704 | -0.032044 | 61.9492 | 124.5438 | 124.7498 | -125.0153 | -125.0336
137.375 | 124.9512 | -61.8576 | 63.0112 | -0.22568 | 0.014084 | 0.012743 | 0.0035141 | 0.068575 | -0.00068359 | 0.068532 | -61.9034 | 62.915 | -62.0544 | -62.0087 | 62.9471 | 0.2243 | -0.14648 | 0.10986 | 62.9654 | -62.0682 | -0.19684 | -0.09613 | -0.045776 | -0.15106 | -0.064086 | -0.21057 | -0.045776 | 0.15106 | 61.7111 | 61.9675 | 124.8047 | 124.7726 | -0.045776 | 124.823 | 62.0819 | -0.21057 | 124.7726 | -0.045776 | 62.0819 | 124.8047 | 124.823 | -125.0656 | -125.0793
138.375 | 124.9466 | -61.8393 | 63.0478 | -0.33249 | 0.011734 | 0.012743 | 0.0035141 | 0.068148 | -0.0013244 | 0.068532 | -61.8896 | 62.915 | -62.0682 | -61.9812 | 62.6953 | 0.073242 | 0.10071 | 0.17853 | 62.9608 | -62.0361 | -0.22888 | -0.13275 | -0.050354 | -0.14191 | -0.35248 | -0.19684 | -0.086976 | 0.17853 | 61.94 | 62.0178 | 124.5346 | 124.7543 | -0.050354 | 124.8001 | 61.9125 | -0.19684 | 124.7543 | -0.050354 | 61.9125 | 124.5346 | 124.8001 | -125.116 | -125.0839
139.375 | 124.9786 | -61.8484 | 63.0386 | -0.28671 | 0.012375 | 0.016374 | 0.0026597 | 0.069643 | -0.0019654 | 0.069814 | -61.8896 | 62.915 | -62.0178 | -61.9858 | 62.6953 | 0.086975 | 0.10529 | 0.17853 | 62.9517 | -62.0361 | -0.16937 | -0.1236 | -0.041198 | -0.13733 | -0.34332 | -0.18768 | -0.086975 | 0.12817 | 61.9537 | 62.027 | 124.5438 | 124.7635 | -0.041198 | 124.8001 | 61.9354 | -0.18768 | 124.7635 | -0.041198 | 61.9354 | 124.5438 | 124.8001 | -125.0565 | -125.0748
140.375 | 125.0153 | -61.8484 | 63.0386 | -0.30197 | 0.014511 | 0.01851 | 0.0045823 | 0.06943 | -0.0011108 | 0.068746 | -61.8759 | 62.9196 | -62.0453 | -61.9629 | 62.6862 | 0.09613 | 0.091553 | 0.19226 | 62.9654 | -62.0316 | -0.19684 | -0.11902 | -0.027466 | -0.11444 | -0.35248 | -0.1831 | -0.073242 | 0.16937 | 61.94 | 62.0407 | 124.5346 | 124.7681 | -0.027466 | 124.8138 | 61.9446 | -0.1831 | 124.7681 | -0.027466 | 61.9446 | 124.5346 | 124.8138 | -125.0839 | -125.0702
141.375 | 124.9969 | -61.8073 | 63.0386 | -0.21042 | 0.012589 | 0.0095382 | 0.0041549 | 0.06943 | -0.0026062 | 0.06896 | -61.8439 | 62.8876 | -62.0407 | -61.9446 | 62.7228 | 0.12817 | 0.064087 | 0.20599 | 62.9333 | -62.0636 | -0.23346 | -0.15106 | -0.036621 | -0.13733 | -0.31586 | -0.25635 | -0.10529 | 0.19684 | 61.8713 | 62.0132 | 124.53 | 124.6948 | -0.036621 | 124.7406 | 61.9354 | -0.25635 | 124.6948 | -0.036621 | 61.9354 | 124.53 | 124.7406 | -125.0793 | -125.1022
142.375 | 125.0565 | -61.8256 | 63.0112 | -0.22568 | 0.011521 | 0.017442 | 0.0043687 | 0.069002 | -0.0030334 | 0.06896 | -61.8393 | 62.8784 | -62.0407 | -61.9308 | 62.7274 | 0.11902 | 0.054932 | 0.23346 | 62.9288 | -62.027 | -0.21515 | -0.13275 | -0.013732 | -0.10529 | -0.28381 | -0.20142 | -0.082397 | 0.20142 | 61.8805 | 62.059 | 124.5529 | 124.704 | -0.013732 | 124.7543 | 61.9446 | -0.20142 | 124.704 | -0.013732 | 61.9446 | 124.5529 | 124.7543 | -125.0519 | -125.0381
143.375 | 125.0702 | -61.8164 | 63.0524 | -0.20279 | 0.011521 | 0.015947 | 0.0035141 | 0.069002 | -0.002179 | 0.071737 | -61.8393 | 62.8967 | -62.0178 | -61.9217 | 62.7457 | 0.15106 | 0.027466 | 0.24261 | 62.9288 | -62.0041 | -0.20142 | -0.15564 | -0.022888 | -0.10529 | -0.3067 | -0.18768 | -0.1236 | 0.17853 | 61.8439 | 62.059 | 124.5621 | 124.7131 | -0.022888 | 124.7452 | 61.9675 | -0.18768 | 124.7131 | -0.022888 | 61.9675 | 124.5621 | 124.7452 | -125.0702 | -125.0565
144.375 | 124.9878 | -61.853 | 63.0524 | -0.32486 | 0.013871 | 0.013597 | 0.0030869 | 0.068148 | -0.00046999 | 0.06896 | -61.8896 | 62.9059 | -62.027 | -61.9812 | 62.6404 | -0.036621 | 0.48981 | 0.16022 | 62.9791 | -62.059 | -0.17395 | -0.14648 | -0.036621 | -0.12817 | -0.41199 | -0.20599 | -0.073242 | 0.13733 | 62.3428 | 62.0132 | 124.4934 | 124.7589 | -0.036621 | 124.8322 | 61.8164 | -0.20599 | 124.7589 | -0.036621 | 61.8164 | 124.4934 | 124.8322 | -125.0793 | -125.1114
145.375 | 124.9832 | -61.8256 | 63.0798 | -0.33249 | 0.012589 | 0.014024 | 0.0060777 | 0.069643 | -0.0026062 | 0.069173 | -61.8942 | 62.9333 | -62.0316 | -62.0041 | 62.677 | 0.068665 | 0.13275 | 0.16937 | 62.9379 | -62.0682 | -0.20599 | -0.14648 | -0.068664 | -0.17853 | -0.40283 | -0.24261 | -0.14191 | 0.13733 | 61.9583 | 61.9949 | 124.5026 | 124.7589 | -0.068664 | 124.7635 | 61.8942 | -0.24261 | 124.7589 | -0.068664 | 61.8942 | 124.5026 | 124.7635 | -125.1114 | -125.148
146.375 | 124.9603 | -61.8301 | 63.0524 | -0.2562 | 0.011521 | 0.013383 | 0.0056503 | 0.068789 | -0.002179 | 0.067891 | -61.8805 | 62.915 | -62.0316 | -61.972 | 62.6953 | 0.10529 | 0.10986 | 0.17395 | 62.9654 | -62.0544 | -0.20142 | -0.13733 | -0.050354 | -0.14191 | -0.35706 | -0.2243 | -0.086975 | 0.15106 | 61.94 | 62.0041 | 124.5255 | 124.7452 | -0.050354 | 124.7955 | 61.9354 | -0.2243 | 124.7452 | -0.050354 | 61.9354 | 124.5255 | 124.7955 | -125.0839 | -125.1068
147.375 | 124.9924 | -61.821 | 63.0432 | -0.31723 | 0.013016 | 0.013597 | 0.0056503 | 0.069216 | -0.0034608 | 0.069814 | -61.8576 | 62.8876 | -62.0316 | -61.9766 | 62.7045 | 0.09613 | 0.10529 | 0.20142 | 62.9425 | -62.0361 | -0.21057 | -0.15564 | -0.036621 | -0.15564 | -0.33875 | -0.21515 | -0.10071 | 0.17395 | 61.9263 | 62.0224 | 124.5255 | 124.7086 | -0.036621 | 124.7635 | 61.9171 | -0.21515 | 124.7086 | -0.036621 | 61.9171 | 124.5255 | 124.7635 | -125.0748 | -125.0793
148.375 | 125.0427 | -61.8301 | 63.0249 | -0.23331 | 0.013443 | 0.014238 | 0.0037277 | 0.067293 | 0.00038461 | 0.070669 | -61.8713 | 62.8922 | -62.0499 | -61.9537 | 62.7182 | 0.1236 | 0.07782 | 0.21057 | 62.9288 | -62.0407 | -0.21973 | -0.13275 | -0.041199 | -0.1236 | -0.3067 | -0.21057 | -0.09613 | 0.17853 | 61.908 | 62.0407 | 124.5483 | 124.7223 | -0.041199 | 124.7589 | 61.9537 | -0.21057 | 124.7223 | -0.041199 | 61.9537 | 124.5483 | 124.7589 | -125.0748 | -125.0656
149.375 | 125.0198 | -61.8118 | 63.0203 | -0.29434 | 0.01323 | 0.013597 | 0.0043687 | 0.067721 | 0.00038461 | 0.070882 | -61.8576 | 62.8693 | -62.0178 | -61.9354 | 62.7228 | 0.12817 | 0.059509 | 0.23346 | 62.9196 | -62.0361 | -0.20599 | -0.15106 | -0.045776 | -0.1236 | -0.29755 | -0.2243 | -0.10071 | 0.16022 | 61.8713 | 62.0453 | 124.5346 | 124.6811 | -0.045776 | 124.7314 | 61.94 | -0.2243 | 124.6811 | -0.045776 | 61.94 | 124.5346 | 124.7314 | -125.0381 | -125.0565
150.375 | 125.0107 | -61.8164 | 63.0157 | -0.27145 | 0.012802 | 0.015947 | 0.0041549 | 0.068789 | -0.0019654 | 0.069387 | -61.8484 | 62.9059 | -62.0316 | -61.9354 | 62.7457 | 0.13275 | 0.050354 | 0.2243 | 62.9105 | -62.0087 | -0.21515 | -0.10986 | -0.032044 | -0.11902 | -0.27008 | -0.19226 | -0.10529 | 0.1831 | 61.8668 | 62.0407 | 124.5621 | 124.7223 | -0.032044 | 124.7269 | 61.9492 | -0.19226 | 124.7223 | -0.032044 | 61.9492 | 124.5621 | 124.7269 | -125.0473 | -125.0244
151.375 | 124.9832 | -61.853 | 63.0386 | -0.34012 | 0.012589 | 0.019151 | 0.00095067 | 0.066866 | 0.0010254 | 0.070241 | -61.9034 | 62.9654 | -62.059 | -62.1002 | 62.6541 | 0.07782 | 0.10529 | 0.15564 | 62.9288 | -62.059 | -0.20599 | -0.073242 | -0.050354 | -0.24719 | -0.38452 | -0.20599 | -0.10986 | 0.15564 | 61.9583 | 62.0087 | 124.5071 | 124.8184 | -0.050354 | 124.7818 | 61.9308 | -0.20599 | 124.8184 | -0.050354 | 61.9308 | 124.5071 | 124.7818 | -125.0977 | -125.0977
152.375 | 124.9832 | -61.8576 | 63.0478 | -0.21805 | 0.011521 | 0.016374 | 0.0035141 | 0.070925 | -0.003247 | 0.068532 | -61.8942 | 62.9288 | -62.0453 | -61.8118 | 62.6862 | -0.091553 | 0.11902 | 0.16022 | 62.9333 | -62.0544 | -0.18768 | -0.11902 | -0.036621 | 0.045776 | -0.36163 | -0.19684 | -0.11444 | 0.15106 | 61.9766 | 62.0178 | 124.5438 | 124.7864 | -0.036621 | 124.791 | 61.7661 | -0.19684 | 124.7864 | -0.036621 | 61.7661 | 124.5438 | 124.791 | -125.0931 | -125.1022
153.375 | 125.0015 | -61.8713 | 63.0249 | -0.24857 | 0.01622 | 0.01317 | 0.0030869 | 0.068789 | -0.0017518 | 0.069387 | -61.9034 | 62.9379 | -62.0499 | -62.0041 | 62.4573 | 0.09613 | 0.39368 | -0.073242 | 62.9654 | -62.0453 | -0.17853 | -0.086975 | -0.032043 | -0.13275 | -0.56763 | -0.17395 | -0.059509 | 0.14648 | 62.265 | 61.7981 | 124.3286 | 124.8093 | -0.032043 | 124.8367 | 61.9675 | -0.17395 | 124.8093 | -0.032043 | 61.9675 | 124.3286 | 124.8367 | -125.0748 | -125.0702
154.375 | 124.9878 | -61.8347 | 63.0386 | -0.3096 | 0.012802 | 0.01317 | 0.0045823 | 0.07007 | -0.0023926 | 0.070455 | -61.8851 | 62.9517 | -62.0453 | -62.0132 | 62.677 | 0.073242 | 0.37537 | 0.39368 | 62.9791 | -62.0224 | -0.21057 | -0.086975 | -0.050354 | -0.17853 | -0.36163 | -0.18768 | -0.059509 | 0.16022 | 62.2101 | 62.2284 | 124.5117 | 124.7864 | -0.050354 | 124.8138 | 61.908 | -0.18768 | 124.7864 | -0.050354 | 61.908 | 124.5117 | 124.8138 | -125.0839 | -125.061
155.375 | 124.8596 | -61.821 | 63.0432 | -0.32486 | 0.011093 | 0.012743 | 0.0015915 | 0.068361 | -0.00089719 | 0.069173 | -61.908 | 62.9379 | -62.0544 | -62.0224 | 62.6358 | 0.064087 | 0.15106 | 0.39368 | 62.9929 | -62.027 | -0.23346 | -0.10529 | -0.086975 | -0.20142 | -0.40741 | -0.20599 | -0.050354 | 0.14648 | 61.972 | 62.2147 | 124.4568 | 124.7589 | -0.086975 | 124.8138 | 61.8851 | -0.20599 | 124.7589 | -0.086975 | 61.8851 | 124.4568 | 124.8138 | -125.0977 | -125.0702
156.375 | 124.9512 | -61.8484 | 63.0432 | -0.28671 | 0.012375 | 0.012102 | 0.0026597 | 0.070284 | 0.00017081 | 0.068532 | -61.9034 | 62.915 | -62.0316 | -62.0087 | 62.6587 | 0.073242 | 0.3479 | 0.39825 | 62.9974 | -62.027 | -0.1831 | -0.12817 | -0.054931 | -0.16022 | -0.38452 | -0.17853 | -0.045776 | 0.12817 | 62.1964 | 62.2467 | 124.5071 | 124.7635 | -0.054931 | 124.8459 | 61.9217 | -0.17853 | 124.7635 | -0.054931 | 61.9217 | 124.5071 | 124.8459 | -125.0748 | -125.0702
157.375 | 125.0107 | -61.8484 | 63.0295 | -0.24857 | 0.013443 | 0.011461 | 0.0026597 | 0.07007 | 0.0010254 | 0.0696 | -61.8942 | 62.9379 | -62.059 | -61.9995 | 62.6862 | 0.11444 | 0.36621 | -0.09613 | 62.9654 | -62.0453 | -0.21057 | -0.091553 | -0.045776 | -0.15106 | -0.34332 | -0.19684 | -0.064087 | 0.16479 | 62.2147 | 61.7523 | 124.5346 | 124.7864 | -0.045776 | 124.8138 | 61.9629 | -0.19684 | 124.7864 | -0.045776 | 61.9629 | 124.5346 | 124.8138 | -125.0885 | -125.0748
158.375 | 124.9466 | -61.853 | 63.0478 | -0.27145 | 0.013016 | 0.016801 | 0.0054367 | 0.069216 | -0.0013244 | 0.066823 | -61.908 | 62.9745 | -62.0544 | -62.0087 | 62.645 | 0.050354 | 0.15564 | 0.14191 | 62.9517 | -62.059 | -0.20142 | -0.073243 | -0.054932 | -0.15564 | -0.40283 | -0.20599 | -0.096131 | 0.14648 | 62.0087 | 61.9949 | 124.498 | 124.8276 | -0.054932 | 124.8047 | 61.9034 | -0.20599 | 124.8276 | -0.054932 | 61.9034 | 124.498 | 124.8047 | -125.1022 | -125.1068
159.375 | 124.9741 | -61.8576 | 63.0432 | -0.27145 | 0.01323 | 0.020219 | 0.0058639 | 0.073702 | -0.0017518 | 0.069387 | -61.9263 | 62.9517 | -62.0682 | -62.0087 | 62.6678 | 0.054932 | 0.15106 | 0.12817 | 62.9425 | -62.0499 | -0.21057 | -0.091553 | -0.068665 | -0.15106 | -0.37537 | -0.19226 | -0.10071 | 0.14191 | 62.0087 | 61.9858 | 124.5255 | 124.8093 | -0.068665 | 124.8001 | 61.9125 | -0.19226 | 124.8093 | -0.068665 | 61.9125 | 124.5255 | 124.8001 | -125.1114 | -125.0931
160.375 | 124.9786 | -61.8347 | 63.0432 | -0.24857 | 0.014511 | 0.017442 | 0.0056503 | 0.069857 | -0.00025639 | 0.069387 | -61.9125 | 62.9562 | -62.0316 | -62.0087 | 62.6633 | 0.068665 | 0.15564 | 0.13733 | 62.9471 | -62.0636 | -0.19684 | -0.086975 | -0.07782 | -0.17395 | -0.37994 | -0.22888 | -0.09613 | 0.11902 | 61.9904 | 61.972 | 124.498 | 124.791 | -0.07782 | 124.7818 | 61.9034 | -0.22888 | 124.791 | -0.07782 | 61.9034 | 124.498 | 124.7818 | -125.0748 | -125.1068
161.375 | 124.9649 | -61.8576 | 63.0341 | -0.26382 | 0.012802 | 0.016801 | 0.0050095 | 0.071566 | -0.00089719 | 0.06896 | -61.908 | 62.9425 | -62.0773 | -62.0178 | 62.6587 | 0.059509 | 0.16022 | 0.12817 | 62.9471 | -62.0636 | -0.21973 | -0.091553 | -0.050354 | -0.16022 | -0.37537 | -0.20599 | -0.086975 | 0.16937 | 62.0178 | 61.9858 | 124.5163 | 124.8001 | -0.050354 | 124.8047 | 61.9171 | -0.20599 | 124.8001 | -0.050354 | 61.9171 | 124.5163 | 124.8047 | -125.1114 | -125.0977
162.375 | 124.9878 | -61.8301 | 63.0524 | -0.24094 | 0.014084 | 0.011034 | 0.0052231 | 0.071779 | -0.0019654 | 0.071523 | -61.9171 | 62.9654 | -62.0636 | -62.0224 | 62.6404 | 0.059509 | 0.14648 | 0.1236 | 62.9562 | -62.0453 | -0.23346 | -0.086975 | -0.086975 | -0.19226 | -0.41199 | -0.21515 | -0.09613 | 0.14649 | 61.9766 | 61.9537 | 124.4705 | 124.7955 | -0.086975 | 124.7864 | 61.8896 | -0.21515 | 124.7955 | -0.086975 | 61.8896 | 124.4705 | 124.7864 | -125.116 | -125.0977
163.375 | 124.9786 | -61.8301 | 63.0478 | -0.2562 | 0.013871 | 0.014452 | 0.0047959 | 0.070925 | -0.0011108 | 0.068319 | -61.9171 | 62.9608 | -62.0361 | -62.0132 | 62.6404 | 0.054932 | 0.13733 | 0.13275 | 62.9654 | -62.0544 | -0.20599 | -0.086976 | -0.086975 | -0.18311 | -0.40741 | -0.2243 | -0.082398 | 0.11902 | 61.9675 | 61.9629 | 124.4705 | 124.791 | -0.086975 | 124.7955 | 61.8851 | -0.2243 | 124.791 | -0.086975 | 61.8851 | 124.4705 | 124.7955 | -125.0839 | -125.1022
164.375 | 124.9329 | -61.8347 | 63.0112 | -0.24857 | 0.013657 | 0.019365 | 0.0035141 | 0.071779 | -0.003247 | 0.0696 | -61.8942 | 62.9791 | -62.0407 | -62.0361 | 62.6495 | 0.068665 | 0.15106 | 0.13733 | 62.9654 | -62.0728 | -0.20599 | -0.032043 | -0.059509 | -0.20142 | -0.36163 | -0.23804 | -0.045776 | 0.14648 | 61.9858 | 61.972 | 124.4843 | 124.8138 | -0.059509 | 124.8001 | 61.9034 | -0.23804 | 124.8138 | -0.059509 | 61.9034 | 124.4843 | 124.8001 | -125.0519 | -125.0839
165.375 | 125.0198 | -61.8347 | 63.0203 | -0.18753 | 0.016434 | 0.013597 | 0.0067185 | 0.070711 | -0.00068359 | 0.069387 | -61.8713 | 62.9791 | -62.0819 | -61.972 | 62.677 | 0.09613 | 0.07782 | 0.17395 | 62.9379 | -62.0728 | -0.24719 | -0.041199 | -0.036621 | -0.13733 | -0.34332 | -0.23804 | -0.082398 | 0.21057 | 61.9125 | 62.0087 | 124.5117 | 124.8138 | -0.036621 | 124.7726 | 61.9308 | -0.23804 | 124.8138 | -0.036621 | 61.9308 | 124.5117 | 124.7726 | -125.1022 | -125.0931
166.375 | 125.0015 | -61.8439 | 63.002 | -0.22568 | 0.014511 | 0.015947 | 0.0056503 | 0.071566 | -0.0026062 | 0.067678 | -61.8759 | 62.9745 | -62.0682 | -61.972 | 62.6999 | 0.09613 | 0.091553 | 0.16937 | 62.915 | -62.0728 | -0.2243 | -0.027466 | -0.032044 | -0.12817 | -0.30212 | -0.22888 | -0.086975 | 0.19226 | 61.9354 | 62.0132 | 124.5438 | 124.8184 | -0.032044 | 124.7589 | 61.94 | -0.22888 | 124.8184 | -0.032044 | 61.94 | 124.5438 | 124.7589 | -125.0702 | -125.0748
167.375 | 125.0244 | -61.8347 | 63.0203 | -0.2562 | 0.014725 | 0.017656 | 0.0041549 | 0.070498 | -0.0011108 | 0.068746 | -61.8576 | 62.9745 | -62.0544 | -61.9858 | 62.6816 | 0.091553 | 0.086975 | 0.20599 | 62.9425 | -62.0544 | -0.21973 | -0.045777 | -0.022888 | -0.15106 | -0.33875 | -0.21973 | -0.07782 | 0.19684 | 61.9217 | 62.0407 | 124.5163 | 124.8093 | -0.022888 | 124.7772 | 61.9263 | -0.21973 | 124.8093 | -0.022888 | 61.9263 | 124.5163 | 124.7772 | -125.0748 | -125.0748
168.375 | 124.9924 | -61.8439 | 63.0341 | -0.2562 | 0.014298 | 0.013811 | 0.0030869 | 0.071779 | -0.00068359 | 0.06896 | -61.9171 | 62.9745 | -62.0499 | -62.027 | 62.6587 | 0.059509 | 0.13733 | 0.14648 | 62.9608 | -62.0453 | -0.20599 | -0.05951 | -0.073242 | -0.18311 | -0.37537 | -0.20142 | -0.073243 | 0.13275 | 61.9812 | 61.9904 | 124.5026 | 124.8184 | -0.073242 | 124.8047 | 61.9034 | -0.20142 | 124.8184 | -0.073242 | 61.9034 | 124.5026 | 124.8047 | -125.0839 | -125.0793
169.375 | 124.9832 | -61.8393 | 62.9883 | -0.17227 | 0.01622 | 0.021074 | 0.0045823 | 0.070711 | -0.0011108 | 0.07195 | -61.8576 | 62.97 | -62.059 | -61.9858 | 62.6953 | 0.10071 | 0.054932 | 0.16479 | 62.9425 | -62.0682 | -0.21973 | -0.01831 | -0.018311 | -0.14648 | -0.29297 | -0.22888 | -0.045776 | 0.20142 | 61.8942 | 62.0041 | 124.5346 | 124.8093 | -0.018311 | 124.7818 | 61.94 | -0.22888 | 124.8093 | -0.018311 | 61.94 | 124.5346 | 124.7818 | -125.0473 | -125.0565
170.375 | 124.9512 | -61.8622 | 62.9974 | -0.21805 | 0.014298 | 0.014879 | 0.0065049 | 0.071566 | -0.00068359 | 0.070028 | -61.853 | 62.9791 | -62.0316 | -61.972 | 62.6862 | 0.086975 | 0.068665 | 0.17853 | 62.9562 | -62.0728 | -0.16937 | -0.018311 | 0.009156 | -0.10986 | -0.31128 | -0.21057 | -0.041199 | 0.17853 | 61.9308 | 62.0407 | 124.5483 | 124.8413 | 0.009156 | 124.8184 | 61.9492 | -0.21057 | 124.8413 | 0.009156 | 61.9492 | 124.5483 | 124.8184 | -125.029 | -125.0702
171.375 | 125.0061 | -61.853 | 63.0203 | -0.22568 | 0.016007 | 0.015947 | 0.0052231 | 0.071993 | -0.0013244 | 0.06896 | -61.853 | 62.9974 | -62.0224 | -61.9675 | 62.6953 | 0.07782 | -0.20599 | 0.073242 | 62.9242 | -62.0911 | -0.16937 | -0.022888 | 0 | -0.11444 | -0.32501 | -0.23804 | -0.096131 | 0.16937 | 61.647 | 61.9263 | 124.5483 | 124.8505 | 0 | 124.7772 | 61.9308 | -0.23804 | 124.8505 | 0 | 61.9308 | 124.5483 | 124.7772 | -125.0427 | -125.1114
172.375 | 124.9878 | -61.8347 | 63.0066 | -0.06546 | 0.01558 | 0.018297 | 0.0058639 | 0.073061 | -0.00046999 | 0.070028 | -61.853 | 63.002 | -62.0407 | -61.9904 | 62.6678 | 0.068665 | 0.027466 | 0.13275 | 62.9288 | -62.0819 | -0.20599 | -0.004578 | -0.01831 | -0.15564 | -0.33874 | -0.24719 | -0.07782 | 0.18768 | 61.8622 | 61.9675 | 124.5026 | 124.8367 | -0.01831 | 124.7635 | 61.9034 | -0.24719 | 124.8367 | -0.01831 | 61.9034 | 124.5026 | 124.7635 | -125.0473 | -125.0885
173.375 | 124.9924 | -61.8347 | 62.9974 | -0.088349 | 0.015366 | 0.020006 | 0.0054367 | 0.075625 | -0.002179 | 0.070455 | -61.853 | 62.9745 | -62.0544 | -62.0041 | 62.6678 | 0.050354 | 0.041199 | 0.13275 | 62.9471 | -62.0911 | -0.21973 | -0.022889 | -0.01831 | -0.16937 | -0.32959 | -0.25635 | -0.050354 | 0.20142 | 61.8759 | 61.9675 | 124.5026 | 124.8093 | -0.01831 | 124.7818 | 61.8851 | -0.25635 | 124.8093 | -0.01831 | 61.8851 | 124.5026 | 124.7818 | -125.0519 | -125.0885
174.375 | 125.0198 | -61.8164 | 63.002 | -0.034943 | 0.015793 | 0.018938 | 0.0062913 | 0.076266 | -0.00089719 | 0.069814 | -61.8622 | 62.9837 | -62.0499 | -62.0041 | 62.6541 | 0.041199 | 0.032043 | 0.11902 | 62.9471 | -62.0636 | -0.23346 | -0.01831 | -0.045777 | -0.18768 | -0.3479 | -0.24719 | -0.054931 | 0.18768 | 61.8484 | 61.9354 | 124.4705 | 124.8001 | -0.045777 | 124.7635 | 61.8576 | -0.24719 | 124.8001 | -0.045777 | 61.8576 | 124.4705 | 124.7635 | -125.0519 | -125.0656
175.375 | 124.9374 | -61.8668 | 62.9837 | 0.010834 | 0.017289 | 0.015306 | 0.0041549 | 0.072848 | -0.0030334 | 0.069814 | -61.9125 | 62.9929 | -62.0636 | -62.0407 | 62.6266 | -0.018311 | 0.041199 | 0.036621 | 62.9517 | -62.0956 | -0.19684 | 0.009155 | -0.045777 | -0.17395 | -0.35706 | -0.22888 | -0.032044 | 0.15106 | 61.908 | 61.9034 | 124.4934 | 124.8596 | -0.045777 | 124.8184 | 61.8484 | -0.22888 | 124.8596 | -0.045777 | 61.8484 | 124.4934 | 124.8184 | -125.0473 | -125.0793
176.375 | 124.9603 | -61.8439 | 62.97 | -0.057831 | 0.01558 | 0.019151 | 0.0056503 | 0.072634 | -0.0011108 | 0.071309 | -61.8805 | 62.9745 | -62.0773 | -62.0224 | 62.6541 | 0.022888 | 0.009155 | 0.10529 | 62.9333 | -62.0773 | -0.23346 | 0.004577 | -0.036621 | -0.17853 | -0.31586 | -0.23346 | -0.036621 | 0.19684 | 61.853 | 61.9492 | 124.498 | 124.8184 | -0.036621 | 124.7772 | 61.8668 | -0.23346 | 124.8184 | -0.036621 | 61.8668 | 124.498 | 124.7772 | -125.0473 | -125.0473
177.375 | 124.9786 | -61.8668 | 62.9974 | -0.06546 | 0.01558 | 0.017442 | 0.0052231 | 0.073061 | -0.0026062 | 0.070241 | -61.8851 | 62.9745 | -62.059 | -62.0361 | 62.6404 | 0.018311 | 0.009155 | 0.073242 | 62.9471 | -62.0819 | -0.19226 | -0.022889 | -0.018311 | -0.16937 | -0.35706 | -0.21515 | -0.050354 | 0.17395 | 61.8759 | 61.94 | 124.5071 | 124.8413 | -0.018311 | 124.8138 | 61.8851 | -0.21515 | 124.8413 | -0.018311 | 61.8851 | 124.5071 | 124.8138 | -125.0565 | -125.0793
178.375 | 124.9878 | -61.8622 | 63.002 | -0.019684 | 0.017716 | 0.015733 | 0.0035141 | 0.073061 | -4.2788e-05 | 0.070669 | -61.8851 | 62.9929 | -62.0636 | -62.0453 | 62.6312 | 0.009155 | 0.032043 | 0.10071 | 62.9333 | -62.1048 | -0.20142 | -0.009155 | -0.022888 | -0.1831 | -0.37079 | -0.24261 | -0.068664 | 0.17853 | 61.8942 | 61.9629 | 124.4934 | 124.855 | -0.022888 | 124.7955 | 61.8713 | -0.24261 | 124.855 | -0.022888 | 61.8713 | 124.4934 | 124.7955 | -125.0656 | -125.1068
179.375 | 124.9603 | -61.8622 | 63.0295 | 0.071869 | 0.01622 | 0.01317 | 0.0013779 | 0.071139 | 0.00081181 | 0.069814 | -61.9537 | 62.9929 | -62.0773 | -62.0361 | 62.7319 | 0.009155 | 0.041199 | 0.064087 | 62.9517 | -62.1048 | -0.21515 | -0.036621 | -0.091552 | -0.17395 | -0.29755 | -0.24261 | -0.07782 | 0.1236 | 61.9034 | 61.9263 | 124.5941 | 124.855 | -0.091552 | 124.8138 | 61.8713 | -0.24261 | 124.855 | -0.091552 | 61.8713 | 124.5941 | 124.8138 | -125.1068 | -125.1343
180.375 | 124.9329 | -61.8484 | 63.0112 | 0.97214 | 0.014298 | 0.01851 | 0.0052231 | 0.073702 | -0.00068359 | 0.069173 | -61.702 | 62.9654 | -62.0728 | -62.0728 | 62.5946 | -0.032043 | 0.013733 | 0.032043 | 62.9562 | -62.1002 | -0.2243 | -0.045776 | 0.14648 | -0.2243 | -0.41657 | -0.25177 | -0.054931 | 0.37079 | 61.8622 | 61.8805 | 124.4431 | 124.8138 | 0.14648 | 124.8047 | 61.8164 | -0.25177 | 124.8138 | 0.14648 | 61.8164 | 124.4431 | 124.8047 | -125.0839 | -125.1114
181.375 | 124.9557 | -61.853 | 63.002 | -0.83603 | 0.014725 | 0.016801 | 0.0041549 | 0.073061 | -0.00068359 | 0.071309 | -61.9492 | 62.9929 | -62.0865 | -62.0773 | 62.6083 | -0.050354 | 0.018311 | 0.018311 | 62.9837 | -62.1094 | -0.23346 | -0.009155 | -0.096131 | -0.22431 | -0.39368 | -0.25635 | -0.01831 | 0.13733 | 61.8713 | 61.8713 | 124.4614 | 124.8459 | -0.096131 | 124.8367 | 61.8027 | -0.25635 | 124.8459 | -0.096131 | 61.8027 | 124.4614 | 124.8367 | -125.0885 | -125.1114
182.375 | 124.9741 | -61.8484 | 63.0157 | 0.11002 | 0.015793 | 0.015092 | 0.0056503 | 0.073916 | 0.00081181 | 0.070241 | -61.9263 | 62.9791 | -62.1002 | -62.0728 | 62.5854 | -0.041199 | 0.027466 | 0.018311 | 62.9379 | -62.1277 | -0.25177 | -0.036621 | -0.07782 | -0.2243 | -0.4303 | -0.27924 | -0.07782 | 0.17395 | 61.8759 | 61.8668 | 124.4339 | 124.8276 | -0.07782 | 124.7864 | 61.8073 | -0.27924 | 124.8276 | -0.07782 | 61.8073 | 124.4339 | 124.7864 | -125.116 | -125.1434
183.375 | 125.0107 | -61.8484 | 62.9608 | 0.14816 | 0.016434 | 0.018083 | 0.0028733 | 0.073488 | -0.0019654 | 0.069173 | -61.9308 | 62.9517 | -62.059 | -62.0773 | 62.6221 | -0.032043 | -0.064087 | 0.036621 | 62.915 | -62.0819 | -0.21057 | -0.009155 | -0.082397 | -0.22888 | -0.33874 | -0.23346 | -0.045776 | 0.12817 | 61.7844 | 61.8851 | 124.4705 | 124.8001 | -0.082397 | 124.7635 | 61.8164 | -0.23346 | 124.8001 | -0.082397 | 61.8164 | 124.4705 | 124.7635 | -125.0198 | -125.0427
184.375 | 124.9832 | -61.8668 | 62.9791 | 0.11765 | 0.013657 | 0.014879 | 0.0054367 | 0.075197 | -0.00068359 | 0.068746 | -61.9446 | 62.9837 | -62.0728 | -62.0773 | 62.5717 | -0.045776 | 0.004578 | -0.009155 | 62.9471 | -62.1323 | -0.20599 | 0.004578 | -0.07782 | -0.21057 | -0.40741 | -0.2655 | -0.032043 | 0.12817 | 61.8713 | 61.8576 | 124.4385 | 124.8505 | -0.07782 | 124.8138 | 61.821 | -0.2655 | 124.8505 | -0.07782 | 61.821 | 124.4385 | 124.8138 | -125.0519 | -125.1114
185.375 | 124.9786 | -61.8576 | 62.9791 | 0.15579 | 0.013443 | 0.01787 | 0.0020187 | 0.071993 | 0.0020934 | 0.071737 | -61.9354 | 62.9745 | -62.0636 | -62.0865 | 62.5717 | -0.073242 | -0.013733 | 0.013733 | 62.9517 | -62.0911 | -0.20599 | -0.004578 | -0.07782 | -0.22888 | -0.40741 | -0.23346 | -0.027466 | 0.12817 | 61.8439 | 61.8713 | 124.4293 | 124.8322 | -0.07782 | 124.8093 | 61.7844 | -0.23346 | 124.8322 | -0.07782 | 61.7844 | 124.4293 | 124.8093 | -125.0427 | -125.0702
186.375 | 125.0381 | -61.8301 | 62.9654 | 0.17105 | 0.012162 | 0.020219 | 0.0022323 | 0.071566 | -0.00025639 | 0.069814 | -61.9308 | 62.9288 | -62.0865 | -62.0224 | 62.6495 | 0 | -0.11902 | 0.068665 | 62.9242 | -62.0819 | -0.25635 | -0.036621 | -0.10071 | -0.19226 | -0.31586 | -0.25177 | -0.041199 | 0.15564 | 61.7111 | 61.8988 | 124.4797 | 124.7589 | -0.10071 | 124.7543 | 61.8301 | -0.25177 | 124.7589 | -0.10071 | 61.8301 | 124.4797 | 124.7543 | -125.0519 | -125.0473
187.375 | 125.0793 | -61.8347 | 62.9608 | 0.15579 | 0.016007 | 0.016801 | 0.0033005 | 0.073275 | -0.00068359 | 0.071096 | -61.8988 | 62.9105 | -62.0682 | -62.0087 | 62.6404 | 0.018311 | -0.14191 | 0.091553 | 62.9196 | -62.0865 | -0.23346 | -0.050354 | -0.064087 | -0.17395 | -0.32043 | -0.25177 | -0.041198 | 0.16937 | 61.6928 | 61.9263 | 124.4751 | 124.7452 | -0.064087 | 124.7543 | 61.853 | -0.25177 | 124.7452 | -0.064087 | 61.853 | 124.4751 | 124.7543 | -125.029 | -125.0473
188.375 | 125.0748 | -61.8118 | 62.9288 | 0.094757 | 0.014084 | 0.014452 | 0.0047959 | 0.071779 | -0.0013244 | 0.071096 | -61.908 | 62.915 | -62.0728 | -61.9995 | 62.677 | 0.027466 | -0.16022 | 0.11902 | 62.8555 | -62.0773 | -0.26093 | -0.013733 | -0.09613 | -0.18768 | -0.25177 | -0.2655 | -0.073242 | 0.1648 | 61.6516 | 61.9308 | 124.4888 | 124.7269 | -0.09613 | 124.6674 | 61.8393 | -0.2655 | 124.7269 | -0.09613 | 61.8393 | 124.4888 | 124.6674 | -125.0015 | -125.0061
189.375 | 125.1801 | -61.8164 | 62.9608 | 0.2092 | 0.016648 | 0.018297 | 0.0052231 | 0.071779 | 0.0016662 | 0.070241 | -61.8896 | 62.9059 | -62.0728 | -61.9629 | 62.7045 | 0.054932 | -0.17395 | -0.10986 | 62.8372 | -62.1277 | -0.25635 | -0.054931 | -0.073242 | -0.14648 | -0.25635 | -0.31128 | -0.1236 | 0.18311 | 61.6425 | 61.7065 | 124.5209 | 124.7223 | -0.073242 | 124.6536 | 61.8713 | -0.31128 | 124.7223 | -0.073242 | 61.8713 | 124.5209 | 124.6536 | -125.0336 | -125.0885
190.375 | 125.0702 | -61.8118 | 62.9288 | 0.16342 | 0.014939 | 0.012529 | 0.00030967 | 0.069002 | -0.00068359 | 0.069387 | -61.8759 | 62.8601 | -62.0407 | -61.9675 | 62.7136 | 0.068665 | -0.16937 | 0.14648 | 62.8876 | -62.0728 | -0.22888 | -0.068665 | -0.064087 | -0.15564 | -0.21515 | -0.26093 | -0.041199 | 0.16479 | 61.6425 | 61.9583 | 124.5255 | 124.6719 | -0.064087 | 124.6994 | 61.8805 | -0.26093 | 124.6719 | -0.064087 | 61.8805 | 124.5255 | 124.6994 | -124.9695 | -125.0015
191.375 | 125.0565 | -61.8027 | 62.9608 | 0.23209 | 0.015366 | 0.014452 | 0.0028733 | 0.067293 | -0.0019654 | 0.069173 | -61.8622 | 62.8922 | -62.0773 | -61.9446 | 62.7502 | 0.082397 | -0.16937 | 0.15106 | 62.8693 | -62.0499 | -0.27466 | -0.068664 | -0.05951 | -0.14191 | -0.21057 | -0.24719 | -0.091552 | 0.21515 | 61.6333 | 61.9537 | 124.5529 | 124.6948 | -0.05951 | 124.6719 | 61.8851 | -0.24719 | 124.6948 | -0.05951 | 61.8851 | 124.5529 | 124.6719 | -125.0381 | -125.0107
192.375 | 125.0793 | -61.8027 | 62.9471 | 0.14816 | 0.014939 | 0.018297 | 0.0018051 | 0.068361 | -0.00025639 | 0.0696 | -61.8713 | 62.8693 | -62.0453 | -61.972 | 62.6953 | 0.064087 | -0.17395 | 0.15106 | 62.8967 | -62.0728 | -0.24262 | -0.07782 | -0.068665 | -0.16937 | -0.25177 | -0.27008 | -0.050354 | 0.17395 | 61.6287 | 61.9537 | 124.498 | 124.6719 | -0.068665 | 124.6994 | 61.8668 | -0.27008 | 124.6719 | -0.068665 | 61.8668 | 124.498 | 124.6994 | -124.9924 | -125.0198
193.375 | 125.061 | -61.8118 | 62.9745 | 0.17105 | 0.014511 | 0.017656 | 0.00052347 | 0.067293 | -0.0019654 | 0.067464 | -61.8805 | 62.8372 | -62.059 | -61.9904 | 62.7045 | 0.045776 | -0.16937 | 0.13733 | 62.8555 | -62.0865 | -0.24719 | -0.13733 | -0.068664 | -0.17853 | -0.27008 | -0.27466 | -0.11902 | 0.17853 | 61.6425 | 61.9492 | 124.5163 | 124.649 | -0.068664 | 124.6674 | 61.8576 | -0.27466 | 124.649 | -0.068664 | 61.8576 | 124.5163 | 124.6674 | -125.0336 | -125.061
194.375 | 125.0473 | -61.8164 | 62.97 | 0.079498 | 0.013443 | 0.013597 | 0.0047959 | 0.068361 | -4.2788e-05 | 0.070028 | -61.8759 | 62.8693 | -62.0453 | -61.9629 | 62.6816 | 0.054932 | -0.16937 | 0.13733 | 62.8784 | -62.0728 | -0.22888 | -0.10071 | -0.05951 | -0.14648 | -0.28839 | -0.25635 | -0.091553 | 0.16937 | 61.647 | 61.9537 | 124.498 | 124.6857 | -0.05951 | 124.6948 | 61.8713 | -0.25635 | 124.6857 | -0.05951 | 61.8713 | 124.498 | 124.6948 | -125.0153 | -125.0427
195.375 | 125.061 | -61.8073 | 62.9517 | 0.11002 | 0.011521 | 0.011888 | 0.0022323 | 0.068575 | -0.002179 | 0.067251 | -61.8668 | 62.8464 | -62.0407 | -61.9675 | 62.6724 | 0.032043 | -0.16937 | 0.14191 | 62.8601 | -62.0499 | -0.23346 | -0.10528 | -0.059509 | -0.16022 | -0.27924 | -0.24262 | -0.091553 | 0.17395 | 61.6379 | 61.9492 | 124.4797 | 124.6536 | -0.059509 | 124.6674 | 61.8393 | -0.24262 | 124.6536 | -0.059509 | 61.8393 | 124.4797 | 124.6674 | -124.9924 | -125.0015
196.375 | 125.061 | -61.8256 | 62.9608 | 0.11765 | 0.012589 | 0.015947 | 0.0035141 | 0.067721 | -0.0015382 | 0.069814 | -61.8759 | 62.8647 | -62.0728 | -61.9583 | 62.677 | 0.054932 | -0.16022 | 0.14191 | 62.8555 | -62.0499 | -0.24719 | -0.09613 | -0.050354 | -0.13275 | -0.28381 | -0.2243 | -0.10528 | 0.19684 | 61.6653 | 61.9675 | 124.5026 | 124.6902 | -0.050354 | 124.6811 | 61.8805 | -0.2243 | 124.6902 | -0.050354 | 61.8805 | 124.5026 | 124.6811 | -125.0336 | -125.0107
197.3906 | 124.9695 | -61.853 | 63.0249 | 0.30838 | 0.015152 | 0.014665 | 0.0062913 | 0.067721 | -0.0028198 | 0.067251 | -61.8988 | 62.9471 | -62.0682 | -62.0132 | 62.6495 | 0.036621 | 0.15564 | 0.14191 | 62.9288 | -62.0682 | -0.21515 | -0.077819 | -0.045777 | -0.16022 | -0.37537 | -0.21515 | -0.09613 | 0.16937 | 62.0087 | 61.9949 | 124.5026 | 124.8001 | -0.045777 | 124.7818 | 61.8896 | -0.21515 | 124.8001 | -0.045777 | 61.8896 | 124.5026 | 124.7818 | -125.0931 | -125.0931
198.375 | 125.0198 | -61.7981 | 62.97 | 0.11002 | 0.013443 | 0.011888 | 0.0013779 | 0.067934 | -0.0011108 | 0.06896 | -61.8622 | 62.8464 | -62.0544 | -61.9675 | 62.6816 | 0.041199 | -0.15564 | 0.12817 | 62.8693 | -62.0361 | -0.25635 | -0.1236 | -0.064087 | -0.16937 | -0.28839 | -0.23804 | -0.10071 | 0.19226 | 61.6425 | 61.9263 | 124.4797 | 124.6445 | -0.064087 | 124.6674 | 61.8393 | -0.23804 | 124.6445 | -0.064087 | 61.8393 | 124.4797 | 124.6674 | -125.0244 | -125.0061
199.375 | 125.0381 | -61.8073 | 62.9883 | 0.094757 | 0.012589 | 0.011888 | -0.0031081 | 0.065584 | 0.00059821 | 0.070669 | -61.9217 | 62.8601 | -62.0453 | -62.0728 | 62.7502 | 0.027466 | -0.10986 | 0.10986 | 62.8967 | -62.0819 | -0.23804 | -0.12817 | -0.11444 | -0.2655 | -0.23804 | -0.27466 | -0.091552 | 0.1236 | 61.6974 | 61.9171 | 124.5575 | 124.6674 | -0.11444 | 124.704 | 61.8347 | -0.27466 | 124.6674 | -0.11444 | 61.8347 | 124.5575 | 124.704 | -125.0336 | -125.0702
200.375 | 124.9878 | -61.7844 | 62.9791 | -0.012055 | 0.011521 | 0.017015 | 0.0045823 | 0.066225 | -0.00025639 | 0.068746 | -61.908 | 62.8372 | -62.059 | -61.9308 | 62.6312 | -0.059509 | -0.073242 | 0.086975 | 62.8693 | -62.0407 | -0.27466 | -0.14191 | -0.1236 | -0.14648 | -0.3479 | -0.25635 | -0.10986 | 0.15106 | 61.7111 | 61.8713 | 124.4156 | 124.6216 | -0.1236 | 124.6536 | 61.7249 | -0.25635 | 124.6216 | -0.1236 | 61.7249 | 124.4156 | 124.6536 | -125.0381 | -125.0198
201.375 | 125.0473 | -61.821 | 62.9883 | 0.041351 | 0.01323 | 0.015306 | -0.0020401 | 0.06708 | 0.001239 | 0.07195 | -61.9125 | 62.8418 | -62.059 | -61.9354 | 62.5946 | -0.050354 | -0.086975 | 0.10529 | 62.8693 | -62.0407 | -0.23804 | -0.14648 | -0.091553 | -0.11444 | -0.39368 | -0.21973 | -0.11902 | 0.14648 | 61.734 | 61.9263 | 124.4156 | 124.6628 | -0.091553 | 124.6902 | 61.7706 | -0.21973 | 124.6628 | -0.091553 | 61.7706 | 124.4156 | 124.6902 | -125.0473 | -125.029
202.3906 | 124.9924 | -61.821 | 63.0157 | -0.23331 | 0.015152 | 0.017656 | 0.0084275 | 0.069002 | -0.0017518 | 0.068319 | -61.8896 | 62.9791 | -62.0499 | -61.9995 | 62.645 | 0.036621 | 0.11444 | 0.12817 | 62.9379 | -62.0682 | -0.22888 | -0.036621 | -0.068664 | -0.17853 | -0.37079 | -0.24719 | -0.07782 | 0.16022 | 61.9354 | 61.9492 | 124.4659 | 124.8001 | -0.068664 | 124.7589 | 61.8576 | -0.24719 | 124.8001 | -0.068664 | 61.8576 | 124.4659 | 124.7589 | -125.0656 | -125.0839
203.375 | 125.0198 | -61.8073 | 62.9837 | -0.11887 | 0.012802 | 0.011888 | 0.0020187 | 0.06943 | -0.0017518 | 0.070455 | -61.9171 | 62.8555 | -62.0544 | -61.9766 | 62.677 | 0.050354 | -0.07782 | 0.15106 | 62.8967 | -62.0316 | -0.24719 | -0.12817 | -0.10986 | -0.16937 | -0.3067 | -0.2243 | -0.086975 | 0.13733 | 61.7294 | 61.9583 | 124.4843 | 124.6628 | -0.10986 | 124.704 | 61.8576 | -0.2243 | 124.6628 | -0.10986 | 61.8576 | 124.4843 | 124.704 | -125.0381 | -125.0153
204.375 | 125.029 | -61.821 | 62.9837 | 0.05661 | 0.012589 | 0.014879 | 0.0041549 | 0.068575 | -0.00068359 | 0.070669 | -61.9949 | 62.8235 | -62.0361 | -62.027 | 62.6816 | 0 | -0.059509 | 0.073242 | 62.8647 | -62.0499 | -0.21515 | -0.16022 | -0.17395 | -0.20599 | -0.30212 | -0.22888 | -0.11902 | 0.041199 | 61.7615 | 61.8942 | 124.5026 | 124.6445 | -0.17395 | 124.6857 | 61.821 | -0.22888 | 124.6445 | -0.17395 | 61.821 | 124.5026 | 124.6857 | -125.0198 | -125.0336
205.375 | 125.029 | -61.7981 | 62.9791 | 0.0032044 | 0.012589 | 0.014452 | 0.0022323 | 0.067934 | -0.00068359 | 0.068746 | -62.0041 | 62.8372 | -62.0407 | -62.0132 | 62.6862 | 0 | -0.068665 | 0.073242 | 62.8647 | -62.0361 | -0.24261 | -0.14191 | -0.20599 | -0.21515 | -0.29297 | -0.23804 | -0.11444 | 0.036621 | 61.7294 | 61.8713 | 124.4843 | 124.6353 | -0.20599 | 124.6628 | 61.7981 | -0.23804 | 124.6353 | -0.20599 | 61.7981 | 124.4843 | 124.6628 | -125.0198 | -125.0153
206.375 | 125.0427 | -61.7935 | 62.9929 | -0.057831 | 0.011307 | 0.013811 | 0.0035141 | 0.066225 | -0.00089719 | 0.069387 | -61.9034 | 62.8647 | -62.0544 | -61.9675 | 62.6953 | 0.064087 | -0.068665 | 0.16022 | 62.8693 | -62.0544 | -0.26093 | -0.12817 | -0.10986 | -0.17395 | -0.29755 | -0.26093 | -0.1236 | 0.15106 | 61.7249 | 61.9537 | 124.4888 | 124.6582 | -0.10986 | 124.6628 | 61.8576 | -0.26093 | 124.6582 | -0.10986 | 61.8576 | 124.4888 | 124.6628 | -125.0473 | -125.0473
207.3906 | 125.0336 | -61.8073 | 63.0066 | -0.14175 | 0.017289 | 0.014452 | 0.0077865 | 0.067293 | 0.0014526 | 0.069173 | -61.8347 | 62.9517 | -62.0544 | -61.94 | 62.6816 | 0.086975 | 0.041199 | -0.07782 | 62.8738 | -62.0911 | -0.24719 | -0.054932 | -0.027466 | -0.13275 | -0.32501 | -0.28381 | -0.13275 | 0.21973 | 61.8484 | 61.7294 | 124.4888 | 124.7589 | -0.027466 | 124.6811 | 61.8942 | -0.28381 | 124.7589 | -0.027466 | 61.8942 | 124.4888 | 124.6811 | -125.061 | -125.0977
208.375 | 125.0198 | -61.7706 | 62.9974 | -0.042572 | 0.0091708 | 0.012743 | 0.0022323 | 0.068361 | -0.0015382 | 0.06896 | -61.9217 | 62.8464 | -62.0636 | -61.9583 | 62.6862 | 0.064087 | -0.07782 | 0.16937 | 62.8738 | -62.0361 | -0.29297 | -0.15106 | -0.15106 | -0.18768 | -0.31128 | -0.2655 | -0.1236 | 0.14191 | 61.6928 | 61.94 | 124.4568 | 124.617 | -0.15106 | 124.6445 | 61.8347 | -0.2655 | 124.617 | -0.15106 | 61.8347 | 124.4568 | 124.6445 | -125.061 | -125.0336
209.375 | 125.0336 | -61.8027 | 62.9974 | -0.019684 | 0.0078892 | 0.016801 | 0.0024461 | 0.064303 | 0.0010254 | 0.069387 | -61.908 | 62.8647 | -62.059 | -61.9583 | 62.7045 | 0.064087 | -0.073242 | 0.17395 | 62.8647 | -62.0316 | -0.25635 | -0.13275 | -0.10529 | -0.15564 | -0.29297 | -0.22888 | -0.13275 | 0.15106 | 61.7294 | 61.9766 | 124.5071 | 124.6674 | -0.10529 | 124.6674 | 61.8668 | -0.22888 | 124.6674 | -0.10529 | 61.8668 | 124.5071 | 124.6674 | -125.0565 | -125.029
210.375 | 125.0565 | -61.8164 | 63.0066 | 0.010834 | 0.013657 | 0.015733 | 0.0013779 | 0.066012 | -0.0015382 | 0.070882 | -61.9125 | 62.8601 | -62.0728 | -61.9583 | 62.7136 | 0.07782 | -0.059509 | 0.14648 | 62.8693 | -62.0361 | -0.25635 | -0.14648 | -0.096131 | -0.14191 | -0.29297 | -0.21973 | -0.13733 | 0.16022 | 61.7569 | 61.9629 | 124.53 | 124.6765 | -0.096131 | 124.6857 | 61.8942 | -0.21973 | 124.6765 | -0.096131 | 61.8942 | 124.53 | 124.6857 | -125.0793 | -125.0427
211.375 | 125.0336 | -61.7981 | 62.9883 | -0.042572 | 0.011307 | 0.011034 | 0.00095067 | 0.067721 | -0.0013244 | 0.06896 | -61.9308 | 62.851 | -62.0499 | -61.9583 | 62.6999 | 0.068665 | -0.059509 | 0.14191 | 62.8693 | -62.059 | -0.25177 | -0.13733 | -0.13275 | -0.16022 | -0.28839 | -0.26093 | -0.11902 | 0.11902 | 61.7386 | 61.94 | 124.498 | 124.649 | -0.13275 | 124.6674 | 61.8668 | -0.26093 | 124.649 | -0.13275 | 61.8668 | 124.498 | 124.6674 | -125.0381 | -125.0473
212.375 | 124.9329 | -61.821 | 63.0112 | -0.012055 | 0.014298 | 0.014665 | 0.01035 | 0.06943 | -0.0023926 | 0.068746 | -61.8759 | 62.8967 | -62.059 | -61.972 | 62.6495 | 0.022888 | 0.013733 | 0.091553 | 62.8876 | -62.0361 | -0.23804 | -0.11444 | -0.054932 | -0.15106 | -0.36163 | -0.21515 | -0.1236 | 0.18311 | 61.8347 | 61.9125 | 124.4705 | 124.7177 | -0.054932 | 124.7086 | 61.8439 | -0.21515 | 124.7177 | -0.054932 | 61.8439 | 124.4705 | 124.7086 | -125.0702 | -125.0473
213.375 | 125.0977 | -61.8027 | 62.9562 | -0.057831 | 0.011734 | 0.014879 | -0.00011753 | 0.06708 | -0.0030334 | 0.0696 | -61.8896 | 62.8418 | -62.0453 | -61.9171 | 62.7228 | 0.10986 | -0.068665 | 0.21973 | 62.883 | -62.027 | -0.24262 | -0.11444 | -0.086975 | -0.11444 | -0.23346 | -0.22431 | -0.073242 | 0.15564 | 61.734 | 62.0224 | 124.5255 | 124.6445 | -0.086975 | 124.6857 | 61.9125 | -0.22431 | 124.6445 | -0.086975 | 61.9125 | 124.5255 | 124.6857 | -125.0015 | -124.9832
214.375 | 125.061 | -61.7889 | 62.9837 | -0.1799 | 0.011734 | 0.011888 | 0.0022323 | 0.066652 | -0.0015382 | 0.068105 | -61.8668 | 62.8326 | -62.0132 | -61.9217 | 62.7365 | 0.11444 | -0.073242 | 0.20142 | 62.8647 | -61.9949 | -0.22431 | -0.15106 | -0.07782 | -0.13275 | -0.24719 | -0.20599 | -0.11902 | 0.14648 | 61.7157 | 61.9904 | 124.5255 | 124.6216 | -0.07782 | 124.6536 | 61.9034 | -0.20599 | 124.6216 | -0.07782 | 61.9034 | 124.5255 | 124.6536 | -124.9969 | -124.9786
215.375 | 125.0565 | -61.7889 | 63.002 | -0.14175 | 0.011093 | 0.01317 | 0.0011643 | 0.06708 | -0.0019654 | 0.070028 | -61.8622 | 62.8464 | -62.0316 | -61.9492 | 62.7228 | 0.11902 | -0.068665 | 0.20142 | 62.883 | -62.0087 | -0.24262 | -0.15564 | -0.073243 | -0.16022 | -0.27924 | -0.21973 | -0.11902 | 0.16937 | 61.7203 | 61.9904 | 124.5117 | 124.6353 | -0.073243 | 124.6719 | 61.908 | -0.21973 | 124.6353 | -0.073243 | 61.908 | 124.5117 | 124.6719 | -125.0336 | -125.0107
216.375 | 125.0885 | -61.7706 | 62.9654 | -0.14938 | 0.013016 | 0.010179 | 0.0022323 | 0.065157 | -0.002179 | 0.0696 | -61.8805 | 62.8601 | -62.059 | -61.94 | 62.7228 | 0.10071 | -0.068665 | 0.20142 | 62.8647 | -61.9858 | -0.28839 | -0.10529 | -0.10986 | -0.16937 | -0.24262 | -0.21515 | -0.10071 | 0.17853 | 61.702 | 61.972 | 124.4934 | 124.6307 | -0.10986 | 124.6353 | 61.8713 | -0.21515 | 124.6307 | -0.10986 | 61.8713 | 124.4934 | 124.6353 | -125.0244 | -124.9512
217.375 | 125.0381 | -61.7798 | 62.9974 | -0.042572 | 0.011093 | 0.011888 | 0.00052347 | 0.065798 | -0.002179 | 0.068532 | -61.8942 | 62.851 | -62.0316 | -61.908 | 62.7182 | 0.1236 | -0.082397 | 0.19684 | 62.851 | -62.0224 | -0.25177 | -0.14648 | -0.11444 | -0.12817 | -0.27924 | -0.24262 | -0.14648 | 0.13733 | 61.6974 | 61.9766 | 124.498 | 124.6307 | -0.11444 | 124.6307 | 61.9034 | -0.24262 | 124.6307 | -0.11444 | 61.9034 | 124.498 | 124.6307 | -125.029 | -125.0198
218.375 | 125.0748 | -61.7935 | 62.9791 | -0.019684 | 0.011521 | 0.015092 | 0.00073707 | 0.066439 | 0.00059821 | 0.069814 | -61.8942 | 62.8418 | -62.0453 | -61.9537 | 62.7045 | 0.086975 | -0.07782 | 0.17853 | 62.8555 | -62.0132 | -0.25177 | -0.13733 | -0.10071 | -0.16022 | -0.27466 | -0.21973 | -0.1236 | 0.15106 | 61.7157 | 61.972 | 124.498 | 124.6353 | -0.10071 | 124.649 | 61.8805 | -0.21973 | 124.6353 | -0.10071 | 61.8805 | 124.498 | 124.649 | -125.0244 | -124.9924
219.375 | 125.0702 | -61.8073 | 62.9883 | -0.012055 | 0.013443 | 0.0095382 | 0.0020187 | 0.064944 | -0.00068359 | 0.0696 | -61.8988 | 62.8464 | -62.0407 | -61.9537 | 62.7045 | 0.064087 | -0.07782 | 0.16022 | 62.8326 | -62.0316 | -0.23346 | -0.14191 | -0.091553 | -0.14648 | -0.28381 | -0.2243 | -0.15564 | 0.14191 | 61.7294 | 61.9675 | 124.5117 | 124.6536 | -0.091553 | 124.6399 | 61.8713 | -0.2243 | 124.6536 | -0.091553 | 61.8713 | 124.5117 | 124.6399 | -125.029 | -125.0198
220.375 | 125.0656 | -61.7798 | 62.97 | -0.088349 | 0.010453 | 0.011247 | 0.0024461 | 0.068361 | -0.0011108 | 0.06661 | -61.8713 | 62.8555 | -62.0682 | -61.9217 | 62.7228 | 0.11444 | -0.07782 | 0.21973 | 62.8601 | -62.0087 | -0.28839 | -0.11444 | -0.091553 | -0.14191 | -0.24719 | -0.22888 | -0.10986 | 0.19684 | 61.702 | 61.9995 | 124.5026 | 124.6353 | -0.091553 | 124.6399 | 61.8942 | -0.22888 | 124.6353 | -0.091553 | 61.8942 | 124.5026 | 124.6399 | -125.0381 | -124.9786
221.375 | 125.0793 | -61.7935 | 62.9837 | -0.088349 | 0.011307 | 0.013597 | -0.00054473 | 0.068148 | -0.0015382 | 0.069173 | -61.8988 | 62.8418 | -62.0544 | -61.9308 | 62.7136 | 0.10529 | -0.082397 | 0.20142 | 62.8647 | -61.9995 | -0.26093 | -0.14191 | -0.10529 | -0.13733 | -0.27008 | -0.20599 | -0.11902 | 0.15564 | 61.7111 | 61.9949 | 124.5071 | 124.6353 | -0.10529 | 124.6582 | 61.8988 | -0.20599 | 124.6353 | -0.10529 | 61.8988 | 124.5071 | 124.6582 | -125.0381 | -124.9832
222.375 | 125.0977 | -61.7889 | 62.9791 | -0.057831 | 0.010239 | 0.0071884 | 0.0028733 | 0.067507 | 0.00081181 | 0.070028 | -61.8942 | 62.8143 | -62.0361 | -61.9308 | 62.6953 | 0.10071 | -0.054932 | 0.20599 | 62.8922 | -61.9904 | -0.24719 | -0.16479 | -0.10529 | -0.14191 | -0.28381 | -0.20142 | -0.086975 | 0.14191 | 61.734 | 61.9949 | 124.4843 | 124.6033 | -0.10529 | 124.6811 | 61.8896 | -0.20142 | 124.6033 | -0.10529 | 61.8896 | 124.4843 | 124.6811 | -125.0153 | -124.9695
223.375 | 125.0336 | -61.7935 | 62.9791 | -0.027313 | 0.011948 | 0.01787 | 0.0022323 | 0.069002 | -0.00046999 | 0.067037 | -61.8942 | 62.8326 | -62.0544 | -61.94 | 62.6999 | 0.07782 | -0.073242 | 0.17853 | 62.883 | -61.9949 | -0.26093 | -0.14648 | -0.10071 | -0.14648 | -0.27924 | -0.20142 | -0.09613 | 0.16022 | 61.7203 | 61.972 | 124.4934 | 124.6262 | -0.10071 | 124.6765 | 61.8713 | -0.20142 | 124.6262 | -0.10071 | 61.8713 | 124.4934 | 124.6765 | -125.0336 | -124.9741
224.375 | 125.0198 | -61.8073 | 62.9883 | 0.033722 | 0.0095982 | 0.011461 | 0.0020187 | 0.068575 | -0.0023926 | 0.067251 | -61.8988 | 62.8555 | -62.0407 | -61.9492 | 62.6999 | 0.064087 | -0.059509 | 0.16479 | 62.8647 | -62.0041 | -0.23346 | -0.13275 | -0.091553 | -0.14191 | -0.28839 | -0.19684 | -0.1236 | 0.14191 | 61.7477 | 61.972 | 124.5071 | 124.6628 | -0.091553 | 124.6719 | 61.8713 | -0.19684 | 124.6628 | -0.091553 | 61.8713 | 124.5071 | 124.6719 | -125.029 | -124.9924
225.375 | 125.0702 | -61.8027 | 62.9883 | -0.012055 | 0.010666 | 0.016161 | 0.0011643 | 0.067293 | -0.00089719 | 0.071523 | -61.908 | 62.8555 | -62.0132 | -61.9629 | 62.7045 | 0.064087 | -0.054932 | 0.15564 | 62.8601 | -62.0178 | -0.21057 | -0.13275 | -0.10529 | -0.16022 | -0.28381 | -0.21515 | -0.12817 | 0.10529 | 61.7477 | 61.9583 | 124.5071 | 124.6582 | -0.10529 | 124.6628 | 61.8668 | -0.21515 | 124.6582 | -0.10529 | 61.8668 | 124.5071 | 124.6628 | -125.0015 | -125.0061
226.375 | 125.0153 | -61.8027 | 62.9883 | -0.0044251 | 0.011734 | 0.014238 | 0.00030967 | 0.066225 | -0.00068359 | 0.068532 | -61.9034 | 62.851 | -62.0453 | -61.9583 | 62.6816 | 0.045776 | -0.068665 | 0.14191 | 62.8601 | -61.9949 | -0.24262 | -0.13733 | -0.10071 | -0.15564 | -0.3067 | -0.19226 | -0.12817 | 0.14191 | 61.734 | 61.9446 | 124.4843 | 124.6536 | -0.10071 | 124.6628 | 61.8484 | -0.19226 | 124.6536 | -0.10071 | 61.8484 | 124.4843 | 124.6628 | -125.0336 | -124.9832
227.375 | 125.0427 | -61.7889 | 62.9929 | -0.088349 | 0.012589 | 0.012315 | 0.0026597 | 0.067934 | -0.00025639 | 0.070669 | -61.8896 | 62.8372 | -62.0544 | -61.908 | 62.7182 | 0.10529 | -0.068665 | 0.21057 | 62.851 | -62.0178 | -0.2655 | -0.15564 | -0.10071 | -0.11902 | -0.27466 | -0.22888 | -0.14191 | 0.16479 | 61.7203 | 61.9995 | 124.5071 | 124.6262 | -0.10071 | 124.6399 | 61.8942 | -0.22888 | 124.6262 | -0.10071 | 61.8942 | 124.5071 | 124.6399 | -125.0473 | -125.0107
228.375 | 125.0519 | -61.7706 | 62.9608 | -0.057831 | 0.011734 | 0.013597 | -0.00054473 | 0.06708 | -0.0023926 | 0.06896 | -61.8805 | 62.8555 | -62.0453 | -61.9446 | 62.6953 | 0.086975 | -0.073242 | 0.17395 | 62.8647 | -61.9949 | -0.27466 | -0.10528 | -0.10986 | -0.17395 | -0.2655 | -0.2243 | -0.09613 | 0.16479 | 61.6974 | 61.9446 | 124.4659 | 124.6262 | -0.10986 | 124.6353 | 61.8576 | -0.2243 | 124.6262 | -0.10986 | 61.8576 | 124.4659 | 124.6353 | -125.0061 | -124.9557
229.375 | 125.0519 | -61.7798 | 62.9837 | 0.026092 | 0.010666 | 0.011034 | 0.0022323 | 0.067721 | -4.2788e-05 | 0.070241 | -61.9034 | 62.8326 | -62.0316 | -61.9583 | 62.6816 | 0.073242 | -0.068665 | 0.17853 | 62.851 | -62.0132 | -0.25177 | -0.15106 | -0.1236 | -0.17853 | -0.30212 | -0.23346 | -0.13275 | 0.12817 | 61.7111 | 61.9583 | 124.4614 | 124.6124 | -0.1236 | 124.6307 | 61.853 | -0.23346 | 124.6124 | -0.1236 | 61.853 | 124.4614 | 124.6307 | -125.0153 | -124.9969
230.375 | 125.061 | -61.7889 | 62.9974 | -0.050202 | 0.012589 | 0.012956 | 0.0022323 | 0.06708 | 0.00059821 | 0.070882 | -61.9034 | 62.8372 | -62.059 | -61.9446 | 62.6816 | 0.07782 | -0.068665 | 0.16937 | 62.8876 | -62.0132 | -0.27008 | -0.16022 | -0.11444 | -0.15564 | -0.31586 | -0.22431 | -0.10986 | 0.15564 | 61.7203 | 61.9583 | 124.4705 | 124.6262 | -0.11444 | 124.6765 | 61.8668 | -0.22431 | 124.6262 | -0.11444 | 61.8668 | 124.4705 | 124.6765 | -125.0565 | -125.0107
231.375 | 125.0519 | -61.7752 | 62.9974 | -0.080719 | 0.011734 | 0.016588 | 0.00073707 | 0.067721 | -0.00068359 | 0.071096 | -61.908 | 62.8738 | -62.0453 | -61.94 | 62.6999 | 0.073242 | -0.073242 | 0.15564 | 62.851 | -62.0224 | -0.27008 | -0.1236 | -0.13275 | -0.16479 | -0.29755 | -0.24719 | -0.14648 | 0.13733 | 61.702 | 61.9308 | 124.4751 | 124.649 | -0.13275 | 124.6262 | 61.8484 | -0.24719 | 124.649 | -0.13275 | 61.8484 | 124.4751 | 124.6262 | -125.0427 | -125.0198
232.375 | 125.0244 | -61.7935 | 62.9654 | -0.050202 | 0.012375 | 0.018724 | -0.00075833 | 0.066225 | -0.00068359 | 0.0696 | -61.9171 | 62.8189 | -62.0544 | -61.9583 | 62.677 | 0.068665 | -0.073242 | 0.15106 | 62.8601 | -62.0041 | -0.26093 | -0.14648 | -0.1236 | -0.16479 | -0.28839 | -0.21057 | -0.10529 | 0.13733 | 61.7203 | 61.9446 | 124.4705 | 124.6124 | -0.1236 | 124.6536 | 61.8622 | -0.21057 | 124.6124 | -0.1236 | 61.8622 | 124.4705 | 124.6536 | -125.0198 | -124.9695
233.375 | 125.0656 | -61.7889 | 62.9791 | -0.042572 | 0.010239 | 0.016161 | 0.00052347 | 0.06708 | -0.00089719 | 0.06896 | -61.8942 | 62.8555 | -62.0361 | -61.9583 | 62.6907 | 0.059509 | -0.068665 | 0.16022 | 62.851 | -62.0087 | -0.24719 | -0.1236 | -0.10529 | -0.16937 | -0.28839 | -0.21973 | -0.12817 | 0.14191 | 61.7203 | 61.9492 | 124.4797 | 124.6445 | -0.10529 | 124.6399 | 61.8484 | -0.21973 | 124.6445 | -0.10529 | 61.8484 | 124.4797 | 124.6399 | -125.0153 | -124.9878
234.375 | 125.0473 | -61.7661 | 62.9837 | -0.042572 | 0.013443 | 0.016161 | -0.00033113 | 0.066866 | -0.00046999 | 0.0696 | -61.8576 | 62.8555 | -62.0453 | -61.9263 | 62.7319 | 0.11444 | -0.10071 | 0.20599 | 62.8418 | -61.9904 | -0.27924 | -0.12817 | -0.091553 | -0.16022 | -0.25177 | -0.2243 | -0.14191 | 0.18768 | 61.6653 | 61.972 | 124.498 | 124.6216 | -0.091553 | 124.6078 | 61.8805 | -0.2243 | 124.6216 | -0.091553 | 61.8805 | 124.498 | 124.6078 | -125.029 | -124.9741
235.375 | 125.0153 | -61.8027 | 62.9608 | -0.034943 | 0.01088 | 0.0084702 | 0.0022323 | 0.06708 | -0.0011108 | 0.070028 | -61.8851 | 62.8372 | -62.027 | -61.9217 | 62.7319 | 0.11902 | -0.073242 | 0.21057 | 62.8555 | -62.0087 | -0.22431 | -0.1236 | -0.082398 | -0.11902 | -0.22888 | -0.20599 | -0.10528 | 0.14191 | 61.7294 | 62.0132 | 124.5346 | 124.6399 | -0.082398 | 124.6582 | 61.9217 | -0.20599 | 124.6399 | -0.082398 | 61.9217 | 124.5346 | 124.6582 | -124.9878 | -124.9695
236.375 | 125.0793 | -61.7844 | 62.9608 | -0.050202 | 0.011307 | 0.016588 | -0.00054473 | 0.066439 | 0.0027344 | 0.068532 | -61.8805 | 62.8326 | -62.0499 | -61.94 | 62.6953 | 0.09613 | -0.054932 | 0.19684 | 62.851 | -61.9995 | -0.2655 | -0.12817 | -0.09613 | -0.15564 | -0.2655 | -0.21515 | -0.10986 | 0.16937 | 61.7294 | 61.9812 | 124.4797 | 124.617 | -0.09613 | 124.6353 | 61.8805 | -0.21515 | 124.617 | -0.09613 | 61.8805 | 124.4797 | 124.6353 | -125.0107 | -124.9603
237.375 | 125.0519 | -61.7935 | 62.9791 | -0.034943 | 0.01323 | 0.014024 | 0.0018051 | 0.066866 | -0.00025639 | 0.071737 | -61.8942 | 62.851 | -62.027 | -61.9537 | 62.709 | 0.07782 | -0.07782 | 0.1831 | 62.851 | -61.9949 | -0.23346 | -0.12817 | -0.10071 | -0.16022 | -0.27008 | -0.20142 | -0.12817 | 0.13275 | 61.7157 | 61.9766 | 124.5026 | 124.6445 | -0.10071 | 124.6445 | 61.8713 | -0.20142 | 124.6445 | -0.10071 | 61.8713 | 124.5026 | 124.6445 | -125.0061 | -124.9741
238.375 | 125.0153 | -61.821 | 62.9791 | 0.018463 | 0.01088 | 0.016588 | 0.0015915 | 0.067721 | -0.00046999 | 0.067891 | -61.6837 | 62.851 | -62.0087 | -61.9858 | 62.6541 | 0.041199 | -0.10071 | 0.1236 | 62.883 | -62.027 | -0.18768 | -0.12817 | 0.13733 | -0.16479 | -0.32501 | -0.20599 | -0.09613 | 0.32501 | 61.7203 | 61.9446 | 124.4751 | 124.6719 | 0.13733 | 124.704 | 61.8622 | -0.20599 | 124.6719 | 0.13733 | 61.8622 | 124.4751 | 124.704 | -124.9878 | -125.0061
239.375 | 125.0519 | -61.8118 | 62.9883 | -0.088349 | 0.011948 | 0.01552 | 0.00030967 | 0.067721 | -0.00046999 | 0.069387 | -61.9125 | 62.8464 | -62.0499 | -61.9492 | 62.6862 | 0.050354 | -0.064087 | 0.17395 | 62.851 | -62.0041 | -0.23804 | -0.14191 | -0.10071 | -0.13733 | -0.30212 | -0.19226 | -0.13733 | 0.13733 | 61.7477 | 61.9858 | 124.498 | 124.6582 | -0.10071 | 124.6628 | 61.8622 | -0.19226 | 124.6582 | -0.10071 | 61.8622 | 124.498 | 124.6628 | -125.0381 | -124.9924
240.375 | 125.0473 | -61.8256 | 62.9974 | -0.034943 | 0.012589 | 0.013597 | 0.0013779 | 0.066225 | 0.00038461 | 0.069387 | -61.9034 | 62.8418 | -62.0407 | -61.9492 | 62.6862 | 0.059509 | -0.064087 | 0.13733 | 62.8647 | -61.9949 | -0.21515 | -0.15564 | -0.077819 | -0.1236 | -0.31128 | -0.16937 | -0.13275 | 0.13733 | 61.7615 | 61.9629 | 124.5117 | 124.6674 | -0.077819 | 124.6902 | 61.8851 | -0.16937 | 124.6674 | -0.077819 | 61.8851 | 124.5117 | 124.6902 | -125.0381 | -124.9924
241.375 | 125.0748 | -61.7844 | 62.9745 | -0.07309 | 0.011734 | 0.010179 | 0.0020187 | 0.066012 | -0.00089719 | 0.067891 | -61.8805 | 62.8464 | -62.027 | -61.9263 | 62.7411 | 0.10986 | -0.073242 | 0.20599 | 62.8555 | -62.0224 | -0.24262 | -0.12817 | -0.09613 | -0.14191 | -0.23346 | -0.23804 | -0.11902 | 0.14648 | 61.7111 | 61.9904 | 124.5255 | 124.6307 | -0.09613 | 124.6399 | 61.8942 | -0.23804 | 124.6307 | -0.09613 | 61.8942 | 124.5255 | 124.6399 | -125.0015 | -124.9969
242.375 | 125.0336 | -61.7752 | 63.0112 | 0.11765 | 0.012162 | 0.014879 | 0.0013779 | 0.067293 | -0.00068359 | 0.070241 | -61.9263 | 62.8464 | -62.0544 | -61.9583 | 62.677 | 0.064087 | -0.073242 | 0.15106 | 62.883 | -61.9995 | -0.27923 | -0.16479 | -0.15106 | -0.1831 | -0.33417 | -0.2243 | -0.12817 | 0.12817 | 61.702 | 61.9263 | 124.4522 | 124.6216 | -0.15106 | 124.6582 | 61.8393 | -0.2243 | 124.6216 | -0.15106 | 61.8393 | 124.4522 | 124.6582 | -125.0656 | -125.0107
243.375 | 125.0336 | -61.8027 | 62.9837 | -0.06546 | 0.011521 | 0.018297 | 0.0024461 | 0.066866 | -0.0015382 | 0.06896 | -61.8942 | 62.8326 | -62.0453 | -61.9537 | 62.6907 | 0.07782 | -0.064087 | 0.17853 | 62.8601 | -62.0132 | -0.24262 | -0.15106 | -0.091553 | -0.15106 | -0.29297 | -0.21057 | -0.1236 | 0.15106 | 61.7386 | 61.9812 | 124.4934 | 124.6353 | -0.091553 | 124.6628 | 61.8805 | -0.21057 | 124.6353 | -0.091553 | 61.8805 | 124.4934 | 124.6628 | -125.029 | -124.9969
244.375 | 125.029 | -61.7889 | 62.97 | -0.095978 | 0.01323 | 0.018297 | 0.0018051 | 0.064944 | -0.00089719 | 0.0696 | -61.9217 | 62.8464 | -62.0224 | -61.9629 | 62.7045 | 0.073242 | -0.059509 | 0.15564 | 62.8281 | -62.0178 | -0.23346 | -0.1236 | -0.13275 | -0.17395 | -0.2655 | -0.22888 | -0.14191 | 0.10071 | 61.7294 | 61.9446 | 124.4934 | 124.6353 | -0.13275 | 124.617 | 61.8622 | -0.22888 | 124.6353 | -0.13275 | 61.8622 | 124.4934 | 124.617 | -124.9924 | -124.9878
245.375 | 125.0519 | -61.7981 | 62.97 | -0.057831 | 0.01323 | 0.01851 | 0.00073707 | 0.066225 | -0.00025639 | 0.0696 | -61.908 | 62.8326 | -62.059 | -61.9583 | 62.6953 | 0.068665 | -0.068665 | 0.16022 | 62.8464 | -62.027 | -0.26093 | -0.13733 | -0.10986 | -0.16022 | -0.27466 | -0.22888 | -0.1236 | 0.15106 | 61.7294 | 61.9583 | 124.4934 | 124.6307 | -0.10986 | 124.6445 | 61.8668 | -0.22888 | 124.6307 | -0.10986 | 61.8668 | 124.4934 | 124.6445 | -125.029 | -124.9969
246.375 | 125.0061 | -61.8164 | 62.9745 | -0.042572 | 0.011093 | 0.014024 | -0.0011855 | 0.065371 | -0.0011108 | 0.070028 | -61.8896 | 62.8372 | -62.0361 | -61.9537 | 62.677 | 0.050354 | -0.064087 | 0.14648 | 62.8418 | -62.0087 | -0.21973 | -0.13733 | -0.073242 | -0.13733 | -0.29755 | -0.19226 | -0.13275 | 0.14648 | 61.7523 | 61.9629 | 124.4934 | 124.6536 | -0.073242 | 124.6582 | 61.8668 | -0.19226 | 124.6536 | -0.073242 | 61.8668 | 124.4934 | 124.6582 | -125.0107 | -124.9832
247.375 | 125.0244 | -61.7935 | 62.9883 | -0.057831 | 0.01323 | 0.013383 | 0.0022323 | 0.067293 | 0.0016662 | 0.06896 | -61.8988 | 62.8326 | -62.0453 | -61.9629 | 62.6724 | 0.045776 | -0.054932 | 0.13733 | 62.8464 | -62.0316 | -0.25177 | -0.15564 | -0.10529 | -0.16937 | -0.31586 | -0.23804 | -0.14191 | 0.14648 | 61.7386 | 61.9308 | 124.4659 | 124.6262 | -0.10529 | 124.6399 | 61.8393 | -0.23804 | 124.6262 | -0.10529 | 61.8393 | 124.4659 | 124.6399 | -125.0336 | -125.0198
248.375 | 125.0565 | -61.7752 | 62.97 | -0.095978 | 0.011307 | 0.014879 | -0.00033113 | 0.067934 | -0.002179 | 0.068319 | -61.8713 | 62.8281 | -62.0453 | -61.9354 | 62.7182 | 0.11444 | -0.068665 | 0.20142 | 62.8464 | -61.9858 | -0.27008 | -0.14191 | -0.09613 | -0.16022 | -0.25177 | -0.21057 | -0.1236 | 0.17395 | 61.7065 | 61.9766 | 124.4934 | 124.6033 | -0.09613 | 124.6216 | 61.8896 | -0.21057 | 124.6033 | -0.09613 | 61.8896 | 124.4934 | 124.6216 | -125.0153 | -124.9557
249.375 | 125.0336 | -61.7661 | 63.0157 | -0.06546 | 0.011307 | 0.012529 | 0.0022323 | 0.067507 | -0.00089719 | 0.070669 | -61.8988 | 62.8418 | -62.0087 | -61.9308 | 62.7228 | 0.10529 | -0.054932 | 0.20142 | 62.883 | -61.9995 | -0.24262 | -0.17395 | -0.13275 | -0.16479 | -0.29297 | -0.23346 | -0.13275 | 0.10986 | 61.7111 | 61.9675 | 124.4888 | 124.6078 | -0.13275 | 124.649 | 61.8713 | -0.23346 | 124.6078 | -0.13275 | 61.8713 | 124.4888 | 124.649 | -125.0244 | -125.0153
250.375 | 125.0702 | -61.7661 | 62.9883 | -0.07309 | 0.013657 | 0.013597 | 0.0035141 | 0.06708 | -0.0017518 | 0.067678 | -61.8805 | 62.8372 | -62.0316 | -61.9308 | 62.6953 | 0.10071 | -0.064087 | 0.19684 | 62.8693 | -62.0087 | -0.2655 | -0.15106 | -0.11444 | -0.16479 | -0.29297 | -0.24262 | -0.11902 | 0.15106 | 61.702 | 61.9629 | 124.4614 | 124.6033 | -0.11444 | 124.6353 | 61.8668 | -0.24262 | 124.6033 | -0.11444 | 61.8668 | 124.4614 | 124.6353 | -125.0198 | -124.9969
251.375 | 125.0473 | -61.7798 | 63.002 | -0.07309 | 0.012375 | 0.016161 | 0.0026597 | 0.065371 | -0.0023926 | 0.06896 | -61.8896 | 62.8189 | -62.0544 | -61.9263 | 62.7045 | 0.091553 | -0.059509 | 0.20599 | 62.8601 | -61.9766 | -0.27466 | -0.18311 | -0.10986 | -0.14649 | -0.29755 | -0.19684 | -0.14191 | 0.16479 | 61.7203 | 61.9858 | 124.4843 | 124.5987 | -0.10986 | 124.6399 | 61.8713 | -0.19684 | 124.5987 | -0.10986 | 61.8713 | 124.4843 | 124.6399 | -125.0565 | -124.9786
252.375 | 125.0381 | -61.7569 | 62.9837 | -0.050202 | 0.011093 | 0.016588 | 0.0018051 | 0.066012 | 0.0014526 | 0.066823 | -61.8805 | 62.8464 | -62.027 | -61.9354 | 62.7136 | 0.086975 | -0.050354 | 0.20599 | 62.8464 | -62.0132 | -0.27008 | -0.13733 | -0.1236 | -0.17853 | -0.27008 | -0.25635 | -0.13733 | 0.14648 | 61.7065 | 61.9629 | 124.4705 | 124.6033 | -0.1236 | 124.6033 | 61.8439 | -0.25635 | 124.6033 | -0.1236 | 61.8439 | 124.4705 | 124.6033 | -125.0107 | -124.9969
253.375 | 125.0702 | -61.7935 | 62.9929 | -0.07309 | 0.010453 | 0.012529 | 0.0015915 | 0.06708 | -4.2788e-05 | 0.070455 | -61.8896 | 62.8555 | -62.0361 | -61.9217 | 62.7182 | 0.10529 | -0.059509 | 0.21057 | 62.8601 | -61.9812 | -0.24262 | -0.13733 | -0.09613 | -0.12817 | -0.27466 | -0.18768 | -0.13275 | 0.14648 | 61.734 | 62.0041 | 124.5117 | 124.649 | -0.09613 | 124.6536 | 61.8988 | -0.18768 | 124.649 | -0.09613 | 61.8988 | 124.5117 | 124.6536 | -125.029 | -124.9741
254.375 | 125.0748 | -61.7981 | 62.9837 | -0.027313 | 0.013871 | 0.01317 | 0.00030967 | 0.068148 | -0.0026062 | 0.0696 | -61.8942 | 62.8281 | -62.0316 | -61.9217 | 62.6953 | 0.10529 | -0.054932 | 0.2243 | 62.883 | -61.9995 | -0.23346 | -0.15564 | -0.09613 | -0.1236 | -0.28839 | -0.20142 | -0.10071 | 0.13733 | 61.7432 | 62.0224 | 124.4934 | 124.6262 | -0.09613 | 124.6811 | 61.9034 | -0.20142 | 124.6262 | -0.09613 | 61.9034 | 124.4934 | 124.6811 | -125.0153 | -124.9832
255.375 | 125.1251 | -61.7798 | 62.9517 | -0.095978 | 0.014084 | 0.012102 | 0.0035141 | 0.06708 | -4.2788e-05 | 0.068532 | -61.8393 | 62.8235 | -62.0316 | -61.8668 | 62.7777 | 0.032043 | 0.31586 | 0.33417 | 62.9105 | -61.9354 | -0.25177 | -0.12817 | -0.059509 | -0.086975 | -0.17395 | -0.15564 | -0.041199 | 0.19226 | 62.0956 | 62.114 | 124.5575 | 124.6033 | -0.059509 | 124.6902 | 61.8118 | -0.15564 | 124.6033 | -0.059509 | 61.8118 | 124.5575 | 124.6902 | -124.9832 | -124.8871
256.375 | 125.0565 | -61.7889 | 62.9608 | -0.16464 | 0.011734 | 0.01317 | 0.00095067 | 0.068148 | -0.00025639 | 0.069387 | -61.8164 | 62.8647 | -62.0041 | -61.8805 | 62.9654 | 0.54016 | -0.20599 | 0 | 62.8876 | -61.9858 | -0.21515 | -0.09613 | -0.027466 | -0.091553 | 0.004578 | -0.19684 | -0.073242 | 0.18768 | 61.5829 | 61.7889 | 124.7543 | 124.6536 | -0.027466 | 124.6765 | 62.3291 | -0.19684 | 124.6536 | -0.027466 | 62.3291 | 124.7543 | 124.6765 | -124.9649 | -124.9466
257.375 | 125.029 | -61.7752 | 62.9517 | -0.13412 | 0.013016 | 0.01082 | 0.0024461 | 0.067507 | -0.002179 | 0.070241 | -61.8256 | 62.8418 | -62.0316 | -62.0132 | 63.0295 | 0.51727 | -0.35248 | 0.068665 | 62.8876 | -61.9949 | -0.25635 | -0.10986 | -0.050354 | -0.23804 | 0.07782 | -0.21973 | -0.064087 | 0.20599 | 61.4227 | 61.8439 | 124.8047 | 124.617 | -0.050354 | 124.6628 | 62.2925 | -0.21973 | 124.617 | -0.050354 | 62.2925 | 124.8047 | 124.6628 | -124.9832 | -124.9466
258.375 | 125.0519 | -61.7798 | 62.9791 | -0.057831 | 0.012162 | 0.011461 | 0.0020187 | 0.068575 | -0.0015382 | 0.07195 | -61.8164 | 62.8464 | -62.0316 | -61.8713 | 62.4847 | 0.41657 | 0.054932 | -0.022888 | 62.9105 | -61.9629 | -0.25177 | -0.13275 | -0.036621 | -0.091553 | -0.49439 | -0.18311 | -0.068665 | 0.21515 | 61.8347 | 61.7569 | 124.2645 | 124.6262 | -0.036621 | 124.6902 | 62.1963 | -0.18311 | 124.6262 | -0.036621 | 62.1963 | 124.2645 | 124.6902 | -125.0107 | -124.942
259.375 | 125.0931 | -61.7981 | 62.9929 | -0.21042 | 0.012162 | 0.013597 | 0.00030967 | 0.067721 | -0.0036744 | 0.068105 | -61.8118 | 62.8647 | -61.9904 | -61.8713 | 62.7548 | 0.16022 | -0.032043 | 0.27008 | 62.8647 | -61.9812 | -0.19226 | -0.12817 | -0.013733 | -0.073242 | -0.23804 | -0.1831 | -0.12817 | 0.17853 | 61.7661 | 62.0682 | 124.5529 | 124.6628 | -0.013733 | 124.6628 | 61.9583 | -0.1831 | 124.6628 | -0.013733 | 61.9583 | 124.5529 | 124.6628 | -124.9832 | -124.9741
260.375 | 125.1572 | -61.7844 | 62.9608 | -0.16464 | 0.011307 | 0.016161 | 0.0022323 | 0.06708 | -0.0017518 | 0.070455 | -61.8164 | 62.8418 | -62.0224 | -61.8713 | 62.4985 | 0.28381 | 0.17395 | 0.059509 | 62.915 | -61.972 | -0.23804 | -0.11902 | -0.032043 | -0.086975 | -0.46234 | -0.18768 | -0.045776 | 0.20599 | 61.9583 | 61.8439 | 124.2828 | 124.6262 | -0.032043 | 124.6994 | 62.0682 | -0.18768 | 124.6262 | -0.032043 | 62.0682 | 124.2828 | 124.6994 | -124.9832 | -124.9329
261.375 | 125.0473 | -61.7798 | 62.9379 | -0.17227 | 0.010025 | 0.016161 | -0.00075833 | 0.066225 | 0.00059821 | 0.069387 | -61.8301 | 62.8555 | -62.0178 | -61.8759 | 62.8006 | 0.5127 | 0 | -0.045776 | 62.9196 | -61.9675 | -0.23804 | -0.082397 | -0.050354 | -0.096131 | -0.13733 | -0.18768 | -0.01831 | 0.18768 | 61.7798 | 61.734 | 124.5804 | 124.6353 | -0.050354 | 124.6994 | 62.2925 | -0.18768 | 124.6353 | -0.050354 | 62.2925 | 124.5804 | 124.6994 | -124.9557 | -124.9054
262.375 | 125.0885 | -61.7889 | 62.9883 | -0.26382 | 0.011734 | 0.012529 | 0.0015915 | 0.07007 | -0.0011108 | 0.069173 | -61.8164 | 62.8418 | -62.0132 | -61.8942 | 62.7502 | 0.16022 | -0.032043 | 0.2655 | 62.8693 | -61.9766 | -0.22431 | -0.14648 | -0.027466 | -0.10529 | -0.23804 | -0.18768 | -0.11902 | 0.19684 | 61.7569 | 62.0544 | 124.5392 | 124.6307 | -0.027466 | 124.6582 | 61.9492 | -0.18768 | 124.6307 | -0.027466 | 61.9492 | 124.5392 | 124.6582 | -125.0015 | -124.9649
263.375 | 125.0748 | -61.7615 | 62.9974 | -0.23331 | 0.011948 | 0.013597 | 0.0033005 | 0.072207 | -0.00089719 | 0.067891 | -61.8073 | 62.8418 | -62.0087 | -61.8713 | 62.7502 | 0.16022 | -0.050354 | 0.28381 | 62.8922 | -61.9675 | -0.24719 | -0.15564 | -0.045776 | -0.10986 | -0.24719 | -0.20599 | -0.10529 | 0.20142 | 61.7111 | 62.0453 | 124.5117 | 124.6033 | -0.045776 | 124.6536 | 61.9217 | -0.20599 | 124.6033 | -0.045776 | 61.9217 | 124.5117 | 124.6536 | -125.0061 | -124.9649
264.375 | 125.0473 | -61.7844 | 63.0112 | -0.17227 | 0.010239 | 0.012102 | 0.0037277 | 0.068148 | -0.0030334 | 0.06896 | -61.821 | 62.8555 | -62.0178 | -61.8713 | 62.764 | 0.16479 | -0.045776 | 0.29755 | 62.851 | -61.9492 | -0.23346 | -0.15564 | -0.036621 | -0.086975 | -0.24719 | -0.16479 | -0.16022 | 0.19684 | 61.7386 | 62.0819 | 124.5483 | 124.6399 | -0.036621 | 124.6353 | 61.9492 | -0.16479 | 124.6399 | -0.036621 | 61.9492 | 124.5483 | 124.6353 | -125.029 | -124.9603
265.375 | 125.0748 | -61.7706 | 63.002 | -0.19516 | 0.01088 | 0.009752 | 0.0024461 | 0.067721 | -0.0034608 | 0.069387 | -61.8347 | 62.851 | -62.0087 | -61.8759 | 62.7686 | 0.17395 | -0.032043 | 0.2655 | 62.8372 | -61.9492 | -0.23804 | -0.15106 | -0.064087 | -0.10529 | -0.23346 | -0.17853 | -0.1648 | 0.17395 | 61.7386 | 62.0361 | 124.5392 | 124.6216 | -0.064087 | 124.6078 | 61.9446 | -0.17853 | 124.6216 | -0.064087 | 61.9446 | 124.5392 | 124.6078 | -125.0107 | -124.9512
266.375 | 125.0153 | -61.8027 | 63.0157 | -0.26382 | 0.011093 | 0.016161 | 0.0028733 | 0.069216 | -0.0013244 | 0.069173 | -61.8301 | 62.8967 | -62.0041 | -61.9354 | 62.7228 | 0.13275 | 0.050354 | 0.23804 | 62.883 | -61.9858 | -0.20142 | -0.11902 | -0.027466 | -0.13275 | -0.29297 | -0.18311 | -0.13275 | 0.17395 | 61.853 | 62.0407 | 124.5255 | 124.6994 | -0.027466 | 124.6857 | 61.9354 | -0.18311 | 124.6994 | -0.027466 | 61.9354 | 124.5255 | 124.6857 | -125.0198 | -125.0015
267.375 | 125.0381 | -61.7935 | 62.9929 | -0.27908 | 0.011948 | 0.017656 | 0.00073707 | 0.069643 | -0.0030334 | 0.0696 | -61.8118 | 62.851 | -61.9904 | -61.8896 | 62.7502 | 0.16937 | -0.032043 | 0.27008 | 62.8738 | -61.972 | -0.19684 | -0.14191 | -0.018311 | -0.09613 | -0.24262 | -0.17853 | -0.11902 | 0.17853 | 61.7615 | 62.0636 | 124.5438 | 124.6445 | -0.018311 | 124.6674 | 61.9629 | -0.17853 | 124.6445 | -0.018311 | 61.9629 | 124.5438 | 124.6674 | -124.9832 | -124.9649
268.375 | 125.0473 | -61.7706 | 62.9974 | -0.34012 | 0.012589 | 0.012529 | 0.0043687 | 0.069002 | -0.0015382 | 0.071737 | -61.8256 | 62.8464 | -62.0178 | -61.8622 | 62.764 | 0.16937 | -0.032043 | 0.26093 | 62.8693 | -61.9995 | -0.24719 | -0.15106 | -0.054932 | -0.091553 | -0.23346 | -0.22888 | -0.12817 | 0.19226 | 61.7386 | 62.0316 | 124.5346 | 124.617 | -0.054932 | 124.6399 | 61.94 | -0.22888 | 124.617 | -0.054932 | 61.94 | 124.5346 | 124.6399 | -125.0153 | -124.9969
269.375 | 125.0198 | -61.7889 | 62.9974 | -0.26382 | 0.012162 | 0.016801 | 0.0037277 | 0.065798 | -0.0019654 | 0.067251 | -61.8484 | 62.8693 | -62.0087 | -61.9125 | 62.7274 | 0.14648 | 0.041199 | 0.24261 | 62.883 | -61.9949 | -0.21973 | -0.12817 | -0.05951 | -0.1236 | -0.27008 | -0.20599 | -0.11444 | 0.16022 | 61.8301 | 62.0316 | 124.5163 | 124.6582 | -0.05951 | 124.6719 | 61.9354 | -0.20599 | 124.6582 | -0.05951 | 61.9354 | 124.5163 | 124.6719 | -125.0061 | -124.9924
270.375 | 124.9924 | -61.7706 | 63.002 | -0.24094 | 0.010239 | 0.016161 | 0.0050095 | 0.066866 | -0.003247 | 0.067678 | -61.8118 | 62.8922 | -62.0041 | -61.9217 | 62.7319 | 0.14648 | 0.036621 | 0.23346 | 62.9059 | -61.9858 | -0.23346 | -0.10986 | -0.041199 | -0.15106 | -0.27008 | -0.21515 | -0.09613 | 0.19226 | 61.8073 | 62.0041 | 124.5026 | 124.6628 | -0.041199 | 124.6765 | 61.9171 | -0.21515 | 124.6628 | -0.041199 | 61.9171 | 124.5026 | 124.6765 | -125.0061 | -124.9878
271.375 | 125.029 | -61.7798 | 63.0203 | -0.27908 | 0.012162 | 0.015947 | 0.0045823 | 0.065798 | -0.0041016 | 0.0696 | -61.8256 | 62.8738 | -62.027 | -61.9171 | 62.7045 | 0.13733 | 0.041199 | 0.23346 | 62.915 | -61.9904 | -0.24719 | -0.14648 | -0.045777 | -0.13733 | -0.31586 | -0.21057 | -0.10529 | 0.20142 | 61.821 | 62.0132 | 124.4843 | 124.6536 | -0.045777 | 124.6948 | 61.9171 | -0.21057 | 124.6536 | -0.045777 | 61.9171 | 124.4843 | 124.6948 | -125.0473 | -125.0107
272.375 | 124.9878 | -61.7798 | 63.0157 | -0.22568 | 0.012375 | 0.012743 | 0.0045823 | 0.070284 | -0.002179 | 0.070028 | -61.8256 | 62.8693 | -62.0224 | -61.908 | 62.7228 | 0.15564 | 0.032043 | 0.25177 | 62.9242 | -61.9904 | -0.24262 | -0.14648 | -0.045777 | -0.12817 | -0.29297 | -0.21057 | -0.091553 | 0.19684 | 61.8118 | 62.0316 | 124.5026 | 124.649 | -0.045777 | 124.704 | 61.9354 | -0.21057 | 124.649 | -0.045777 | 61.9354 | 124.5026 | 124.704 | -125.0381 | -125.0061
273.375 | 124.9237 | -61.8301 | 63.0295 | -0.48508 | 0.014084 | 0.015947 | 0.0018051 | 0.066225 | -0.0028198 | 0.068105 | -61.9034 | 62.9105 | -62.0407 | -62.1277 | 62.5946 | 0.086975 | 0.07782 | 0.15564 | 62.9059 | -62.0224 | -0.21057 | -0.11902 | -0.073242 | -0.29755 | -0.43488 | -0.19226 | -0.1236 | 0.13733 | 61.908 | 61.9858 | 124.4247 | 124.7406 | -0.073242 | 124.736 | 61.9171 | -0.19226 | 124.7406 | -0.073242 | 61.9171 | 124.4247 | 124.736 | -125.0702 | -125.0519
274.375 | 125.0336 | -61.7798 | 62.9974 | -0.31723 | 0.013016 | 0.017229 | 0.0030869 | 0.067934 | -0.0013244 | 0.068746 | -61.8164 | 62.8738 | -62.0178 | -61.908 | 62.6999 | 0.15106 | 0.032043 | 0.25177 | 62.9105 | -62.0132 | -0.23804 | -0.1236 | -0.036621 | -0.12817 | -0.29755 | -0.23346 | -0.086976 | 0.20142 | 61.8118 | 62.0316 | 124.4797 | 124.6536 | -0.036621 | 124.6902 | 61.9308 | -0.23346 | 124.6536 | -0.036621 | 61.9308 | 124.4797 | 124.6902 | -125.0153 | -125.0107
275.375 | 124.942 | -61.8347 | 63.0295 | -0.38589 | 0.012162 | 0.012529 | 0.0052231 | 0.06943 | -0.003247 | 0.072164 | -61.8988 | 62.9333 | -62.0224 | -61.8576 | 62.8372 | 0.073242 | 0.027466 | 0.1831 | 62.9333 | -62.0407 | -0.18768 | -0.09613 | -0.064087 | -0.022888 | -0.19226 | -0.20599 | -0.09613 | 0.1236 | 61.8622 | 62.0178 | 124.6719 | 124.7681 | -0.064087 | 124.7681 | 61.908 | -0.20599 | 124.7681 | -0.064087 | 61.908 | 124.6719 | 124.7681 | -125.0519 | -125.0702
276.375 | 124.91 | -61.8484 | 63.0295 | -0.14175 | 0.011093 | 0.0061204 | 0.0030869 | 0.067507 | -0.002179 | 0.069173 | -61.8622 | 62.9333 | -62.0361 | -62.0041 | 62.8281 | 0.26093 | -0.07782 | 0.082397 | 62.9288 | -62.0316 | -0.18768 | -0.09613 | -0.013733 | -0.15564 | -0.20142 | -0.1831 | -0.10071 | 0.17395 | 61.7706 | 61.9308 | 124.6765 | 124.7818 | -0.013733 | 124.7772 | 62.1094 | -0.1831 | 124.7818 | -0.013733 | 62.1094 | 124.6765 | 124.7772 | -125.0656 | -125.061
277.375 | 124.9557 | -61.8439 | 63.0157 | -0.14175 | 0.011948 | 0.017015 | 0.0058639 | 0.069002 | -0.0023926 | 0.0696 | -61.8713 | 62.9333 | -62.0316 | -61.9949 | 62.6083 | 0.23804 | 0.18768 | -0.064087 | 62.9333 | -62.0132 | -0.18768 | -0.082397 | -0.027466 | -0.15106 | -0.40741 | -0.16937 | -0.082397 | 0.16022 | 62.0316 | 61.7798 | 124.4522 | 124.7772 | -0.027466 | 124.7772 | 62.0819 | -0.16937 | 124.7772 | -0.027466 | 62.0819 | 124.4522 | 124.7772 | -125.0473 | -125.029
278.375 | 125.0473 | -61.7706 | 62.9974 | -0.21042 | 0.012589 | 0.014024 | 0.0028733 | 0.068575 | -0.0036744 | 0.069173 | -61.8347 | 62.8922 | -62.0316 | -61.9125 | 62.7228 | 0.14648 | 0.041199 | 0.24719 | 62.883 | -61.9904 | -0.26093 | -0.10529 | -0.064087 | -0.14191 | -0.27466 | -0.21973 | -0.11444 | 0.19684 | 61.8118 | 62.0178 | 124.4934 | 124.6628 | -0.064087 | 124.6536 | 61.9171 | -0.21973 | 124.6628 | -0.064087 | 61.9171 | 124.4934 | 124.6536 | -125.029 | -124.9878
279.375 | 124.9374 | -61.821 | 63.0203 | -0.27908 | 0.014084 | 0.018083 | 0.0071457 | 0.068575 | -0.0026062 | 0.070455 | -61.9034 | 62.9471 | -62.0544 | -62.0041 | 62.6495 | 0.068665 | 0.13733 | 0.14648 | 62.9242 | -62.0316 | -0.23346 | -0.073242 | -0.082397 | -0.1831 | -0.37079 | -0.21057 | -0.096131 | 0.15106 | 61.9583 | 61.9675 | 124.4705 | 124.7681 | -0.082397 | 124.7452 | 61.8896 | -0.21057 | 124.7681 | -0.082397 | 61.8896 | 124.4705 | 124.7452 | -125.0748 | -125.0519
280.375 | 124.9695 | -61.8256 | 63.0569 | -0.31723 | 0.013443 | 0.012315 | 0.0056503 | 0.071993 | -0.0015382 | 0.070882 | -61.8896 | 62.9196 | -62.0499 | -61.9858 | 62.6495 | 0.068665 | 0.13275 | 0.16022 | 62.9379 | -62.0316 | -0.2243 | -0.13733 | -0.064086 | -0.16022 | -0.40741 | -0.20599 | -0.11902 | 0.16022 | 61.9583 | 61.9858 | 124.4751 | 124.7452 | -0.064086 | 124.7635 | 61.8942 | -0.20599 | 124.7452 | -0.064086 | 61.8942 | 124.4751 | 124.7635 | -125.1068 | -125.0885
281.375 | 124.9466 | -61.8027 | 63.0157 | -0.3096 | 0.011307 | 0.015306 | 0.0060777 | 0.067507 | -0.0023926 | 0.067464 | -61.8851 | 62.9196 | -62.027 | -61.9675 | 62.6541 | 0.068665 | 0.1236 | 0.16937 | 62.9242 | -62.0316 | -0.22431 | -0.09613 | -0.082398 | -0.16479 | -0.36163 | -0.22888 | -0.091553 | 0.14191 | 61.9263 | 61.972 | 124.4568 | 124.7223 | -0.082398 | 124.7269 | 61.8713 | -0.22888 | 124.7223 | -0.082398 | 61.8713 | 124.4568 | 124.7269 | -125.0427 | -125.0473
282.375 | 124.9191 | -61.821 | 63.0249 | -0.38589 | 0.014511 | 0.017442 | 0.0056503 | 0.069216 | -0.0028198 | 0.0696 | -61.8942 | 62.9196 | -62.0544 | -61.9812 | 62.6266 | 0.054932 | 0.14191 | 0.14648 | 62.9471 | -62.0361 | -0.23346 | -0.10528 | -0.073242 | -0.16022 | -0.39825 | -0.21515 | -0.077819 | 0.16022 | 61.9629 | 61.9675 | 124.4476 | 124.7406 | -0.073242 | 124.7681 | 61.8759 | -0.21515 | 124.7406 | -0.073242 | 61.8759 | 124.4476 | 124.7681 | -125.0793 | -125.061
283.375 | 124.9374 | -61.8256 | 63.002 | -0.38589 | 0.014725 | 0.015306 | 0.0045823 | 0.069216 | -0.00025639 | 0.069814 | -61.9217 | 62.915 | -62.0636 | -61.9949 | 62.6495 | 0.059509 | 0.14648 | 0.15106 | 62.9242 | -62.0544 | -0.23804 | -0.086975 | -0.09613 | -0.16937 | -0.35248 | -0.22888 | -0.07782 | 0.14191 | 61.972 | 61.9766 | 124.4751 | 124.7406 | -0.09613 | 124.7498 | 61.8851 | -0.22888 | 124.7406 | -0.09613 | 61.8851 | 124.4751 | 124.7498 | -125.0656 | -125.0565
284.375 | 124.9054 | -61.8164 | 63.0203 | -0.019684 | 0.013016 | 0.018297 | 0.0052231 | 0.069002 | -0.0026062 | 0.069814 | -61.8988 | 62.9288 | -62.0865 | -61.9858 | 62.6404 | 0.068665 | 0.13275 | 0.14648 | 62.9288 | -62.0407 | -0.27008 | -0.091553 | -0.082398 | -0.16937 | -0.37994 | -0.2243 | -0.091553 | 0.18768 | 61.9492 | 61.9629 | 124.4568 | 124.7452 | -0.082398 | 124.7452 | 61.8851 | -0.2243 | 124.7452 | -0.082398 | 61.8851 | 124.4568 | 124.7452 | -125.1068 | -125.061
285.375 | 124.91 | -61.821 | 63.0203 | -0.22568 | 0.01088 | 0.014024 | 0.0041549 | 0.070284 | -0.00025639 | 0.0696 | -61.734 | 62.9791 | -62.0544 | -61.9995 | 62.6587 | 0.059509 | 0.13275 | 0.17395 | 62.9425 | -62.059 | -0.23346 | -0.041199 | 0.086975 | -0.17853 | -0.36163 | -0.23804 | -0.07782 | 0.32043 | 61.9537 | 61.9949 | 124.4797 | 124.8001 | 0.086975 | 124.7635 | 61.8805 | -0.23804 | 124.8001 | 0.086975 | 61.8805 | 124.4797 | 124.7635 | -125.0748 | -125.0793
286.375 | 124.9512 | -61.8439 | 63.0203 | -0.16464 | 0.014084 | 0.015306 | 0.0041549 | 0.067721 | -0.0019654 | 0.0696 | -61.8942 | 62.9517 | -62.0728 | -62.1735 | 62.558 | 0.041199 | 0.09613 | 0.09613 | 62.9333 | -62.0636 | -0.22888 | -0.068665 | -0.050354 | -0.32959 | -0.46234 | -0.21973 | -0.086975 | 0.17853 | 61.94 | 61.94 | 124.4019 | 124.7955 | -0.050354 | 124.7772 | 61.8851 | -0.21973 | 124.7955 | -0.050354 | 61.8851 | 124.4019 | 124.7772 | -125.0931 | -125.0839
287.375 | 124.9054 | -61.8484 | 63.0157 | -0.24094 | 0.013871 | 0.01552 | 0.0056503 | 0.06943 | -0.0015382 | 0.070241 | -61.9034 | 62.9333 | -62.0499 | -62.0178 | 62.8693 | 0.23346 | -0.091553 | 0.11444 | 62.9517 | -62.0407 | -0.20142 | -0.082397 | -0.054931 | -0.16937 | -0.14648 | -0.19226 | -0.064087 | 0.14648 | 61.7569 | 61.9629 | 124.7177 | 124.7818 | -0.054931 | 124.8001 | 62.0819 | -0.19226 | 124.7818 | -0.054931 | 62.0819 | 124.7177 | 124.8001 | -125.0656 | -125.0565
288.375 | 124.8322 | -61.8118 | 63.002 | -0.22568 | 0.013016 | 0.012529 | 0.0054367 | 0.070284 | -0.0013244 | 0.068746 | -61.8668 | 62.9242 | -62.0407 | -61.972 | 62.6587 | 0.073242 | 0.13275 | 0.37994 | 62.9791 | -62.0224 | -0.22888 | -0.07782 | -0.054931 | -0.16022 | -0.34332 | -0.21057 | -0.022888 | 0.17395 | 61.9446 | 62.1918 | 124.4705 | 124.736 | -0.054931 | 124.791 | 61.8851 | -0.21057 | 124.736 | -0.054931 | 61.8851 | 124.4705 | 124.791 | -125.0427 | -125.0244
289.375 | 124.9466 | -61.8164 | 63.0112 | -0.22568 | 0.014511 | 0.018724 | 0.0052231 | 0.069857 | -0.0045288 | 0.070669 | -61.9125 | 62.9379 | -62.0407 | -61.9812 | 62.6404 | 0.041199 | 0.15564 | 0.16022 | 62.9425 | -62.0407 | -0.2243 | -0.073242 | -0.096131 | -0.16479 | -0.37079 | -0.2243 | -0.068664 | 0.12817 | 61.972 | 61.9766 | 124.4568 | 124.7543 | -0.096131 | 124.7589 | 61.8576 | -0.2243 | 124.7543 | -0.096131 | 61.8576 | 124.4568 | 124.7589 | -125.0519 | -125.0519
290.375 | 124.9146 | -61.8256 | 62.9974 | -0.15701 | 0.01558 | 0.011888 | 0.0060777 | 0.068148 | -0.00089719 | 0.067891 | -61.8805 | 62.9242 | -62.0544 | -62.0041 | 62.6175 | 0.064087 | 0.12817 | 0.15106 | 62.9517 | -62.0178 | -0.22888 | -0.073243 | -0.054931 | -0.17853 | -0.37994 | -0.19226 | -0.045777 | 0.17395 | 61.9537 | 61.9766 | 124.4431 | 124.7498 | -0.054931 | 124.7772 | 61.8896 | -0.19226 | 124.7498 | -0.054931 | 61.8896 | 124.4431 | 124.7772 | -125.0519 | -125.0153
291.375 | 124.942 | -61.8118 | 63.0249 | -0.78262 | 0.011521 | 0.011247 | 0.0056503 | 0.067934 | -0.00068359 | 0.069814 | -61.94 | 62.9288 | -62.0544 | -62.0041 | 62.6404 | 0.054932 | 0.16022 | 0.16022 | 62.9471 | -62.027 | -0.24261 | -0.09613 | -0.12817 | -0.19226 | -0.38452 | -0.21515 | -0.077819 | 0.11444 | 61.972 | 61.972 | 124.4522 | 124.7406 | -0.12817 | 124.7589 | 61.8668 | -0.21515 | 124.7406 | -0.12817 | 61.8668 | 124.4522 | 124.7589 | -125.0793 | -125.0519
292.375 | 124.9283 | -61.8256 | 63.0386 | -0.40878 | 0.014084 | 0.014238 | 0.0075729 | 0.069643 | -0.0030334 | 0.069173 | -61.9858 | 62.915 | -62.0361 | -62.0544 | 62.6129 | 0.073242 | 0.13275 | 0.13275 | 62.9379 | -62.0361 | -0.21057 | -0.1236 | -0.16022 | -0.22888 | -0.42572 | -0.21057 | -0.10071 | 0.050354 | 61.9583 | 61.9583 | 124.4385 | 124.7406 | -0.16022 | 124.7635 | 61.8988 | -0.21057 | 124.7406 | -0.16022 | 61.8988 | 124.4385 | 124.7635 | -125.0748 | -125.0748
293.375 | 125.0153 | -61.8164 | 63.002 | -0.14938 | 0.014298 | 0.018938 | 0.0075729 | 0.069857 | -0.0017518 | 0.068746 | -62.0773 | 62.9105 | -62.0544 | -61.9583 | 62.6633 | 0.064087 | 0.054932 | 0.16937 | 62.9059 | -62.0361 | -0.23804 | -0.091553 | -0.26093 | -0.14191 | -0.33875 | -0.21973 | -0.09613 | -0.022889 | 61.8713 | 61.9858 | 124.4797 | 124.7269 | -0.26093 | 124.7223 | 61.8805 | -0.21973 | 124.7269 | -0.26093 | 61.8805 | 124.4797 | 124.7223 | -125.0565 | -125.0381
294.375 | 125.0015 | -61.7981 | 62.9745 | -0.21805 | 0.01323 | 0.015947 | 0.0020187 | 0.069002 | -0.0013244 | 0.069814 | -61.8393 | 62.8922 | -62.0087 | -61.9217 | 62.7274 | 0.14648 | 0.018311 | 0.26093 | 62.8967 | -61.9995 | -0.21057 | -0.082397 | -0.041198 | -0.1236 | -0.24719 | -0.20142 | -0.077819 | 0.16937 | 61.8164 | 62.059 | 124.5255 | 124.6902 | -0.041198 | 124.6948 | 61.9446 | -0.20142 | 124.6902 | -0.041198 | 61.9446 | 124.5255 | 124.6948 | -124.9832 | -124.9741
295.375 | 124.942 | -61.7981 | 63.0249 | -0.27908 | 0.012802 | 0.018724 | 0.0041549 | 0.07007 | 0.00059821 | 0.070028 | -61.8576 | 62.8967 | -61.9995 | -61.9766 | 62.6678 | 0.091553 | 0.10986 | 0.21057 | 62.915 | -62.0316 | -0.20142 | -0.12817 | -0.059509 | -0.17853 | -0.35705 | -0.23346 | -0.10986 | 0.14191 | 61.908 | 62.0087 | 124.4659 | 124.6948 | -0.059509 | 124.7131 | 61.8896 | -0.23346 | 124.6948 | -0.059509 | 61.8896 | 124.4659 | 124.7131 | -125.0244 | -125.0565
296.375 | 124.91 | -61.8256 | 63.0066 | -0.74448 | 0.013016 | 0.015306 | 0.0041549 | 0.069002 | -4.2788e-05 | 0.071523 | -61.9492 | 62.915 | -62.059 | -61.9949 | 62.6312 | 0.054932 | 0.13733 | 0.15564 | 62.9745 | -62.0453 | -0.23346 | -0.091553 | -0.1236 | -0.16937 | -0.37537 | -0.21973 | -0.032044 | 0.10986 | 61.9629 | 61.9812 | 124.4568 | 124.7406 | -0.1236 | 124.8001 | 61.8805 | -0.21973 | 124.7406 | -0.1236 | 61.8805 | 124.4568 | 124.8001 | -125.0656 | -125.0519
297.375 | 124.9191 | -61.7981 | 63.0157 | -0.21042 | 0.010239 | 0.009111 | 0.0069321 | 0.069002 | -0.0036744 | 0.065755 | -61.7294 | 62.9425 | -62.0361 | -61.9766 | 62.6221 | 0.036621 | 0.15106 | 0.16937 | 62.9425 | -62.0499 | -0.23804 | -0.073242 | 0.068665 | -0.17853 | -0.39368 | -0.25177 | -0.073242 | 0.3067 | 61.9492 | 61.9675 | 124.4202 | 124.7406 | 0.068665 | 124.7406 | 61.8347 | -0.25177 | 124.7406 | 0.068665 | 61.8347 | 124.4202 | 124.7406 | -125.0519 | -125.0656
298.3906 | 124.9512 | -61.8118 | 62.9929 | -0.14175 | 0.013871 | 0.016588 | 0.0069321 | 0.070284 | -4.2788e-05 | 0.068319 | -61.908 | 62.9517 | -62.0499 | -62.0361 | 62.5763 | -0.054932 | 0 | 0.013733 | 62.9196 | -62.0819 | -0.23804 | -0.041199 | -0.09613 | -0.2243 | -0.41657 | -0.27008 | -0.073242 | 0.14191 | 61.8118 | 61.8256 | 124.3881 | 124.7635 | -0.09613 | 124.7314 | 61.7569 | -0.27008 | 124.7635 | -0.09613 | 61.7569 | 124.3881 | 124.7314 | -125.0427 | -125.0748
299.375 | 124.91 | -61.8301 | 62.9654 | -0.18753 | 0.014084 | 0.014452 | 0.0026597 | 0.069643 | -0.0015382 | 0.069814 | -61.8668 | 62.9196 | -62.0453 | -62.0087 | 62.5854 | 0.21057 | 0.18768 | -0.059509 | 62.9654 | -62.0453 | -0.21515 | -0.045776 | -0.036621 | -0.17853 | -0.37994 | -0.21515 | 0 | 0.17853 | 62.0178 | 61.7706 | 124.4156 | 124.7498 | -0.036621 | 124.7955 | 62.0407 | -0.21515 | 124.7498 | -0.036621 | 62.0407 | 124.4156 | 124.7955 | -125.0107 | -125.0107
300.375 | 124.8596 | -61.8027 | 62.9974 | -0.24094 | 0.01323 | 0.015306 | 0.0024461 | 0.070284 | -0.003247 | 0.069173 | -61.8988 | 62.9242 | -62.0224 | -61.9904 | 62.6266 | 0.073242 | 0.14648 | 0.37537 | 62.9837 | -62.0316 | -0.21973 | -0.073243 | -0.096131 | -0.18768 | -0.37079 | -0.22888 | -0.013733 | 0.1236 | 61.9492 | 62.178 | 124.4293 | 124.7269 | -0.096131 | 124.7864 | 61.8759 | -0.22888 | 124.7269 | -0.096131 | 61.8759 | 124.4293 | 124.7864 | -125.0198 | -125.029
301.375 | 124.9557 | -61.7889 | 63.0524 | -0.30197 | 0.013443 | 0.012315 | 0.0050095 | 0.069002 | -0.0011108 | 0.06896 | -61.8668 | 62.9059 | -62.0361 | -61.972 | 62.6129 | 0.064087 | 0.13275 | 0.16479 | 62.9379 | -62.0453 | -0.24719 | -0.14648 | -0.07782 | -0.18311 | -0.43945 | -0.25635 | -0.11444 | 0.16937 | 61.9217 | 61.9537 | 124.4019 | 124.6948 | -0.07782 | 124.7269 | 61.853 | -0.25635 | 124.6948 | -0.07782 | 61.853 | 124.4019 | 124.7269 | -125.0885 | -125.0977
302.375 | 124.9374 | -61.8347 | 63.0066 | -0.29434 | 0.012375 | 0.010393 | 0.0020187 | 0.07007 | -0.0026062 | 0.069173 | -61.8759 | 62.9379 | -62.0407 | -62.0041 | 62.6587 | 0.10529 | 0.14191 | 0.16022 | 62.9425 | -62.0316 | -0.20599 | -0.068665 | -0.041199 | -0.16937 | -0.3479 | -0.19684 | -0.064087 | 0.16479 | 61.9766 | 61.9949 | 124.4934 | 124.7726 | -0.041199 | 124.7772 | 61.94 | -0.19684 | 124.7726 | -0.041199 | 61.94 | 124.4934 | 124.7772 | -125.0473 | -125.0381
303.3906 | 124.8871 | -61.8393 | 63.002 | 0.0032044 | 0.01622 | 0.01552 | 0.0082139 | 0.073061 | -0.00068359 | 0.06896 | -61.8484 | 62.9471 | -62.027 | -61.9858 | 62.6221 | 0 | 0.027466 | 0.082397 | 62.9471 | -62.0499 | -0.18768 | -0.054931 | -0.009156 | -0.14648 | -0.37994 | -0.21057 | -0.054931 | 0.17853 | 61.8668 | 61.9217 | 124.4614 | 124.7864 | -0.009156 | 124.7864 | 61.8393 | -0.21057 | 124.7864 | -0.009156 | 61.8393 | 124.4614 | 124.7864 | -125.029 | -125.0519
304.375 | 124.9054 | -61.8118 | 63.002 | -0.1265 | 0.012162 | 0.018297 | 0.0043687 | 0.069857 | -0.00025639 | 0.06896 | -61.9171 | 62.9471 | -62.0773 | -61.9995 | 62.6221 | 0.064087 | 0.14648 | 0.13733 | 62.9745 | -62.0499 | -0.2655 | -0.054931 | -0.10528 | -0.18768 | -0.37994 | -0.23804 | -0.027466 | 0.16022 | 61.9583 | 61.9492 | 124.4339 | 124.7589 | -0.10528 | 124.7864 | 61.8759 | -0.23804 | 124.7589 | -0.10528 | 61.8759 | 124.4339 | 124.7864 | -125.0793 | -125.0519
305.375 | 124.9512 | -61.8164 | 63.0112 | 0.064239 | 0.01323 | 0.013811 | 0.0043687 | 0.068148 | -0.0013244 | 0.070028 | -61.8988 | 62.9196 | -62.0636 | -61.9904 | 62.6312 | 0.059509 | 0.13733 | 0.15106 | 62.97 | -62.0636 | -0.24719 | -0.091552 | -0.082398 | -0.17395 | -0.37994 | -0.24719 | -0.041198 | 0.1648 | 61.9537 | 61.9675 | 124.4476 | 124.736 | -0.082398 | 124.7864 | 61.8759 | -0.24719 | 124.736 | -0.082398 | 61.8759 | 124.4476 | 124.7864 | -125.0748 | -125.0748
306.375 | 124.9466 | -61.8118 | 63.0066 | -0.24094 | 0.010666 | 0.013597 | 0.0054367 | 0.069643 | -0.0017518 | 0.067891 | -61.8484 | 62.9425 | -62.0361 | -61.9904 | 62.5992 | 0.041199 | 0.15564 | 0.15106 | 62.9333 | -62.0499 | -0.2243 | -0.064087 | -0.036621 | -0.17853 | -0.40741 | -0.23804 | -0.073242 | 0.18768 | 61.9675 | 61.9629 | 124.411 | 124.7543 | -0.036621 | 124.7452 | 61.853 | -0.23804 | 124.7543 | -0.036621 | 61.853 | 124.411 | 124.7452 | -125.0427 | -125.0565
307.375 | 124.9283 | -61.8164 | 63.0203 | -0.24094 | 0.013443 | 0.01317 | 0.0054367 | 0.071779 | -0.0019654 | 0.068532 | -62.0087 | 62.9562 | -62.0178 | -62.0407 | 62.59 | 0.064087 | 0.13275 | 0.12817 | 62.9471 | -62.0499 | -0.20142 | -0.064087 | -0.19226 | -0.2243 | -0.4303 | -0.23346 | -0.073242 | 0.009155 | 61.9492 | 61.9446 | 124.4064 | 124.7726 | -0.19226 | 124.7635 | 61.8805 | -0.23346 | 124.7726 | -0.19226 | 61.8805 | 124.4064 | 124.7635 | -125.0381 | -125.0702
308.375 | 124.9512 | -61.8347 | 63.0112 | -0.24857 | 0.013016 | 0.015733 | 0.0011643 | 0.070498 | 0.00081181 | 0.068532 | -61.9125 | 62.9425 | -62.0499 | -62.0544 | 62.6358 | 0.041199 | 0.10529 | 0.16937 | 62.9517 | -62.059 | -0.21515 | -0.068664 | -0.07782 | -0.21973 | -0.37537 | -0.2243 | -0.059509 | 0.13733 | 61.94 | 62.0041 | 124.4705 | 124.7772 | -0.07782 | 124.7864 | 61.8759 | -0.2243 | 124.7772 | -0.07782 | 61.8759 | 124.4705 | 124.7864 | -125.061 | -125.0702
309.375 | 124.9374 | -61.8301 | 62.9929 | -0.33249 | 0.014298 | 0.019579 | 0.0045823 | 0.070284 | -0.00089719 | 0.065328 | -61.8896 | 62.9517 | -62.0361 | -61.9034 | 62.8464 | 0.11444 | -0.013733 | 0.16479 | 62.9471 | -62.1002 | -0.20599 | -0.041199 | -0.059509 | -0.073242 | -0.14648 | -0.27008 | -0.045776 | 0.14648 | 61.8164 | 61.9949 | 124.6765 | 124.7818 | -0.059509 | 124.7772 | 61.9446 | -0.27008 | 124.7818 | -0.059509 | 61.9446 | 124.6765 | 124.7772 | -125.029 | -125.0931
310.375 | 124.9054 | -61.821 | 62.9883 | -0.27145 | 0.013443 | 0.015947 | 0.0067185 | 0.069216 | -0.00068359 | 0.0696 | -61.8988 | 62.9562 | -62.027 | -61.9949 | 62.6312 | 0.050354 | 0.14648 | 0.15106 | 62.9471 | -62.0407 | -0.20599 | -0.032043 | -0.07782 | -0.17395 | -0.35706 | -0.21973 | -0.041198 | 0.12817 | 61.9675 | 61.972 | 124.4522 | 124.7772 | -0.07782 | 124.7681 | 61.8713 | -0.21973 | 124.7772 | -0.07782 | 61.8713 | 124.4522 | 124.7681 | -125.0153 | -125.029
311.375 | 124.9466 | -61.8118 | 63.0432 | -0.26382 | 0.012802 | 0.017442 | 0.0060777 | 0.069857 | -0.0036744 | 0.068532 | -61.9034 | 62.9562 | -62.0407 | -61.9858 | 62.6221 | 0.054932 | 0.13733 | 0.1236 | 62.9562 | -62.0499 | -0.22888 | -0.086975 | -0.091552 | -0.17395 | -0.42114 | -0.23804 | -0.086975 | 0.13733 | 61.9492 | 61.9354 | 124.4339 | 124.7681 | -0.091552 | 124.7681 | 61.8668 | -0.23804 | 124.7681 | -0.091552 | 61.8668 | 124.4339 | 124.7681 | -125.0839 | -125.0931
312.375 | 124.91 | -61.8301 | 62.9929 | -0.06546 | 0.013016 | 0.010179 | 0.0033005 | 0.069002 | -0.0034608 | 0.0696 | -61.8759 | 62.9425 | -62.0544 | -62.0087 | 62.6175 | 0.059509 | 0.15106 | 0.15564 | 62.9562 | -62.0361 | -0.2243 | -0.050354 | -0.045777 | -0.17853 | -0.37537 | -0.20599 | -0.036621 | 0.17853 | 61.9812 | 61.9858 | 124.4476 | 124.7726 | -0.045777 | 124.7864 | 61.8896 | -0.20599 | 124.7726 | -0.045777 | 61.8896 | 124.4476 | 124.7864 | -125.0473 | -125.029
313.375 | 124.9146 | -61.8301 | 62.9883 | -0.44693 | 0.014084 | 0.0099656 | 0.0047959 | 0.069857 | -0.0013244 | 0.068532 | -61.9308 | 62.9288 | -62.059 | -61.9858 | 62.6266 | 0.050354 | 0.15106 | 0.14191 | 62.9425 | -62.059 | -0.22888 | -0.059509 | -0.10071 | -0.15564 | -0.36163 | -0.22888 | -0.045776 | 0.12817 | 61.9812 | 61.972 | 124.4568 | 124.7589 | -0.10071 | 124.7726 | 61.8805 | -0.22888 | 124.7589 | -0.10071 | 61.8805 | 124.4568 | 124.7726 | -125.0473 | -125.0473
314.375 | 124.9557 | -61.8256 | 63.0249 | -0.29434 | 0.012589 | 0.015947 | 0.0043687 | 0.067934 | -0.0013244 | 0.069173 | -61.8118 | 62.9608 | -62.0178 | -62.0178 | 62.645 | 0.059509 | 0.11444 | 0.16479 | 62.915 | -62.0453 | -0.19226 | -0.064087 | 0.013733 | -0.19226 | -0.37994 | -0.21973 | -0.10986 | 0.20599 | 61.94 | 61.9904 | 124.4705 | 124.7864 | 0.013733 | 124.7406 | 61.8851 | -0.21973 | 124.7864 | 0.013733 | 61.8851 | 124.4705 | 124.7406 | -125.0427 | -125.0702
315.375 | 124.942 | -61.8301 | 63.002 | -0.27145 | 0.013016 | 0.009111 | 0.0039413 | 0.069857 | -0.0041016 | 0.069387 | -61.8988 | 62.9379 | -62.0224 | -61.8988 | 62.4847 | -0.082397 | 0.16937 | 0.09613 | 62.9242 | -62.059 | -0.19226 | -0.064087 | -0.068665 | -0.068665 | -0.51727 | -0.22888 | -0.07782 | 0.1236 | 61.9995 | 61.9263 | 124.3149 | 124.7681 | -0.068665 | 124.7543 | 61.7477 | -0.22888 | 124.7681 | -0.068665 | 61.7477 | 124.3149 | 124.7543 | -125.0244 | -125.061
316.375 | 124.9466 | -61.7935 | 63.0707 | -0.2562 | 0.014725 | 0.01082 | 0.0039413 | 0.069857 | 0.00017081 | 0.0696 | -61.8851 | 62.9288 | -62.0041 | -62.0041 | 62.6541 | 0.07782 | 0.1236 | 0.15564 | 62.9242 | -62.059 | -0.21057 | -0.14191 | -0.091553 | -0.21057 | -0.41656 | -0.2655 | -0.14648 | 0.11902 | 61.9171 | 61.9492 | 124.4476 | 124.7223 | -0.091553 | 124.7177 | 61.8713 | -0.2655 | 124.7223 | -0.091553 | 61.8713 | 124.4476 | 124.7177 | -125.0748 | -125.1297
317.375 | 124.9329 | -61.7981 | 63.0066 | -0.17227 | 0.012162 | 0.01317 | 0.0022323 | 0.067293 | -0.00025639 | 0.070241 | -61.8942 | 62.9242 | -62.0453 | -61.9995 | 62.6129 | 0.050354 | 0.14648 | 0.13275 | 62.9471 | -62.0407 | -0.24719 | -0.082398 | -0.09613 | -0.20142 | -0.39368 | -0.24261 | -0.059509 | 0.15106 | 61.9446 | 61.9308 | 124.411 | 124.7223 | -0.09613 | 124.7452 | 61.8484 | -0.24261 | 124.7223 | -0.09613 | 61.8484 | 124.411 | 124.7452 | -125.0519 | -125.0473
318.375 | 124.8871 | -61.821 | 63.0295 | -1.4693 | 0.013443 | 0.017442 | 0.0043687 | 0.067507 | -4.2788e-05 | 0.070028 | -62.0682 | 62.9379 | -62.0544 | -62.027 | 62.6129 | 0.073242 | 0.14191 | 0.14191 | 62.9654 | -62.0544 | -0.23346 | -0.091553 | -0.24719 | -0.20599 | -0.41656 | -0.23346 | -0.064087 | -0.013733 | 61.9629 | 61.9629 | 124.4339 | 124.7589 | -0.24719 | 124.7864 | 61.8942 | -0.23346 | 124.7589 | -0.24719 | 61.8942 | 124.4339 | 124.7864 | -125.0839 | -125.0839
319.375 | 124.9146 | -61.821 | 63.0112 | -0.36301 | 0.013657 | 0.016801 | 0.0056503 | 0.065798 | 0.00038461 | 0.070028 | -61.8896 | 62.915 | -62.0453 | -62.1735 | 62.5626 | 0.032043 | 0.068665 | 0.12817 | 62.915 | -62.0544 | -0.2243 | -0.09613 | -0.068664 | -0.35248 | -0.44861 | -0.23346 | -0.09613 | 0.15564 | 61.8896 | 61.9492 | 124.3835 | 124.736 | -0.068664 | 124.736 | 61.853 | -0.23346 | 124.736 | -0.068664 | 61.853 | 124.3835 | 124.736 | -125.0565 | -125.0656
320.375 | 124.9512 | -61.8164 | 63.0112 | -0.27145 | 0.016434 | 0.014024 | 0.0052231 | 0.069857 | -0.003247 | 0.068319 | -61.9034 | 62.9242 | -62.0407 | -61.9949 | 62.6221 | 0.041199 | 0.15564 | 0.13275 | 62.9608 | -62.0453 | -0.2243 | -0.086975 | -0.086975 | -0.17853 | -0.3891 | -0.22888 | -0.050354 | 0.13733 | 61.972 | 61.9492 | 124.4385 | 124.7406 | -0.086975 | 124.7772 | 61.8576 | -0.22888 | 124.7406 | -0.086975 | 61.8576 | 124.4385 | 124.7772 | -125.0519 | -125.0565
321.375 | 124.91 | -61.8073 | 63.0432 | -0.2562 | 0.013443 | 0.016374 | 0.0013779 | 0.069002 | -0.0028198 | 0.070669 | -61.8805 | 62.9196 | -62.0132 | -61.9675 | 62.6678 | 0.054932 | 0.14648 | 0.21515 | 62.9517 | -62.0361 | -0.20599 | -0.1236 | -0.073242 | -0.16022 | -0.37537 | -0.22888 | -0.091553 | 0.13275 | 61.9537 | 62.0224 | 124.4751 | 124.7269 | -0.073242 | 124.7589 | 61.8622 | -0.22888 | 124.7269 | -0.073242 | 61.8622 | 124.4751 | 124.7589 | -125.0565 | -125.0793
322.375 | 124.9374 | -61.8073 | 63.0066 | -0.27908 | 0.011948 | 0.014452 | 0.0039413 | 0.068575 | -0.0011108 | 0.071309 | -61.8484 | 62.9059 | -62.0087 | -61.9492 | 62.6678 | 0.11444 | 0.086975 | 0.21515 | 62.9471 | -62.0316 | -0.20142 | -0.10071 | -0.041199 | -0.14191 | -0.33874 | -0.2243 | -0.059509 | 0.16022 | 61.8942 | 62.0224 | 124.4751 | 124.7131 | -0.041199 | 124.7543 | 61.9217 | -0.2243 | 124.7131 | -0.041199 | 61.9217 | 124.4751 | 124.7543 | -125.0153 | -125.0381
323.375 | 125.0153 | -61.7981 | 63.0157 | -0.24094 | 0.011948 | 0.017015 | 0.0033005 | 0.06943 | 0.0016662 | 0.0696 | -61.8484 | 62.8922 | -62.0087 | -61.9308 | 62.6907 | 0.13275 | 0.041199 | 0.23346 | 62.9196 | -62.0041 | -0.21057 | -0.1236 | -0.050354 | -0.13275 | -0.32501 | -0.20599 | -0.09613 | 0.16022 | 61.8393 | 62.0316 | 124.4888 | 124.6902 | -0.050354 | 124.7177 | 61.9308 | -0.20599 | 124.6902 | -0.050354 | 61.9308 | 124.4888 | 124.7177 | -125.0244 | -125.0198
324.375 | 124.7955 | -61.821 | 63.0157 | -0.28671 | 0.014725 | 0.018083 | 0.0052231 | 0.068575 | 0.00038461 | 0.068105 | -61.8942 | 62.9333 | -62.0453 | -61.9766 | 62.6312 | 0.064087 | 0.11902 | 0.33417 | 62.9562 | -62.027 | -0.2243 | -0.082397 | -0.073242 | -0.15564 | -0.38452 | -0.20599 | -0.059509 | 0.15106 | 61.94 | 62.1552 | 124.4522 | 124.7543 | -0.073242 | 124.7772 | 61.8851 | -0.20599 | 124.7543 | -0.073242 | 61.8851 | 124.4522 | 124.7772 | -125.061 | -125.0427
325.375 | 124.9557 | -61.7935 | 63.0386 | -0.28671 | 0.012802 | 0.016801 | 0.0030869 | 0.06708 | -0.0017518 | 0.068532 | -61.8622 | 62.9242 | -62.0361 | -61.9766 | 62.645 | 0.068665 | 0.082397 | 0.21515 | 62.9333 | -62.027 | -0.24262 | -0.11444 | -0.068665 | -0.18311 | -0.39368 | -0.23346 | -0.10529 | 0.17395 | 61.8759 | 62.0087 | 124.4385 | 124.7177 | -0.068665 | 124.7269 | 61.8622 | -0.23346 | 124.7177 | -0.068665 | 61.8622 | 124.4385 | 124.7269 | -125.0748 | -125.0656
326.375 | 124.9695 | -61.8073 | 62.9974 | -0.2562 | 0.011521 | 0.015306 | 0.0022323 | 0.066652 | -0.0011108 | 0.0696 | -61.8393 | 62.883 | -62.0316 | -61.9354 | 62.6862 | 0.11902 | 0.073242 | 0.21973 | 62.9105 | -61.9995 | -0.2243 | -0.11444 | -0.032043 | -0.12817 | -0.31128 | -0.19226 | -0.086976 | 0.19226 | 61.8805 | 62.027 | 124.4934 | 124.6902 | -0.032043 | 124.7177 | 61.9263 | -0.19226 | 124.6902 | -0.032043 | 61.9263 | 124.4934 | 124.7177 | -125.029 | -124.9969
327.375 | 124.9695 | -61.7935 | 63.0157 | -0.21805 | 0.012589 | 0.011034 | 0.0015915 | 0.06708 | -0.0017518 | 0.069387 | -61.8118 | 62.8555 | -62.0178 | -61.9034 | 62.7045 | 0.12817 | 0.036621 | 0.25177 | 62.9013 | -62.0178 | -0.2243 | -0.16022 | -0.018311 | -0.10986 | -0.31128 | -0.2243 | -0.11444 | 0.20599 | 61.8301 | 62.0453 | 124.498 | 124.649 | -0.018311 | 124.6948 | 61.9217 | -0.2243 | 124.649 | -0.018311 | 61.9217 | 124.498 | 124.6948 | -125.0336 | -125.0336
328.375 | 125.029 | -61.7798 | 63.0112 | -0.2562 | 0.012162 | 0.014238 | 0.0041549 | 0.066866 | -0.00025639 | 0.067251 | -61.8256 | 62.8647 | -62.0224 | -61.9034 | 62.7136 | 0.15106 | -0.004578 | 0.25177 | 62.9013 | -62.0041 | -0.24262 | -0.14648 | -0.045777 | -0.1236 | -0.29755 | -0.2243 | -0.10986 | 0.19684 | 61.7752 | 62.0316 | 124.4934 | 124.6445 | -0.045777 | 124.6811 | 61.9308 | -0.2243 | 124.6445 | -0.045777 | 61.9308 | 124.4934 | 124.6811 | -125.0336 | -125.0153
329.375 | 125.0519 | -61.7706 | 62.9974 | -0.17227 | 0.01088 | 0.013811 | 0.0035141 | 0.066866 | -0.0015382 | 0.068532 | -61.821 | 62.8372 | -62.0224 | -61.8851 | 62.7045 | 0.15106 | -0.022888 | 0.2655 | 62.8738 | -62.0132 | -0.25177 | -0.16022 | -0.050354 | -0.11444 | -0.29297 | -0.24262 | -0.1236 | 0.20142 | 61.7477 | 62.0361 | 124.4751 | 124.6078 | -0.050354 | 124.6445 | 61.9217 | -0.24262 | 124.6078 | -0.050354 | 61.9217 | 124.4751 | 124.6445 | -125.0198 | -125.0107
330.375 | 125.0427 | -61.7752 | 63.002 | -0.19516 | 0.013443 | 0.011034 | 0.0026597 | 0.067293 | -0.0017518 | 0.070669 | -61.8118 | 62.8738 | -62.0224 | -61.8759 | 62.7319 | 0.15564 | -0.032043 | 0.27466 | 62.8967 | -62.0132 | -0.24719 | -0.12817 | -0.036621 | -0.10071 | -0.27008 | -0.23804 | -0.10529 | 0.21057 | 61.7432 | 62.0499 | 124.5071 | 124.649 | -0.036621 | 124.6719 | 61.9308 | -0.23804 | 124.649 | -0.036621 | 61.9308 | 124.5071 | 124.6719 | -125.0244 | -125.0153
331.375 | 125.0015 | -61.7798 | 63.002 | -0.20279 | 0.01323 | 0.013811 | 0.0071457 | 0.06943 | -0.00046999 | 0.071737 | -61.821 | 62.8967 | -62.0224 | -61.9171 | 62.7182 | 0.14648 | 0.013733 | 0.24719 | 62.8967 | -62.0041 | -0.24262 | -0.10529 | -0.041199 | -0.13733 | -0.28381 | -0.2243 | -0.10529 | 0.20142 | 61.7935 | 62.027 | 124.498 | 124.6765 | -0.041199 | 124.6765 | 61.9263 | -0.2243 | 124.6765 | -0.041199 | 61.9263 | 124.498 | 124.6765 | -125.0244 | -125.0061
332.375 | 125.0153 | -61.7569 | 62.9929 | -0.21042 | 0.010025 | 0.015733 | 0.0039413 | 0.068575 | -0.0013244 | 0.069173 | -61.8118 | 62.851 | -61.9995 | -61.8896 | 62.7182 | 0.15106 | -0.004578 | 0.2655 | 62.8738 | -61.9812 | -0.24262 | -0.14191 | -0.054932 | -0.13275 | -0.27466 | -0.2243 | -0.11902 | 0.18768 | 61.7523 | 62.0224 | 124.4751 | 124.6078 | -0.054932 | 124.6307 | 61.908 | -0.2243 | 124.6078 | -0.054932 | 61.908 | 124.4751 | 124.6307 | -124.9924 | -124.9741
333.375 | 125.0244 | -61.7615 | 63.0112 | -0.23331 | 0.011093 | 0.014665 | 0.0030869 | 0.068148 | -0.0017518 | 0.067891 | -61.8118 | 62.8326 | -62.0132 | -61.8851 | 62.7274 | 0.15106 | -0.022888 | 0.27008 | 62.8647 | -62.0132 | -0.25177 | -0.17853 | -0.050354 | -0.1236 | -0.28381 | -0.25177 | -0.14648 | 0.20142 | 61.7386 | 62.0316 | 124.4888 | 124.5941 | -0.050354 | 124.6262 | 61.9125 | -0.25177 | 124.5941 | -0.050354 | 61.9125 | 124.4888 | 124.6262 | -125.0244 | -125.0244
334.375 | 125.0565 | -61.7569 | 62.9837 | -0.23331 | 0.0098118 | 0.011888 | 0.0024461 | 0.067507 | -0.0034608 | 0.070028 | -61.8256 | 62.8555 | -61.9995 | -61.8668 | 62.7365 | 0.16479 | -0.050354 | 0.27924 | 62.8876 | -61.9904 | -0.24262 | -0.12817 | -0.068665 | -0.10986 | -0.24719 | -0.23346 | -0.096131 | 0.17395 | 61.7065 | 62.0361 | 124.4934 | 124.6124 | -0.068665 | 124.6445 | 61.9217 | -0.23346 | 124.6124 | -0.068665 | 61.9217 | 124.4934 | 124.6445 | -124.9832 | -124.9741
335.375 | 124.9924 | -61.7569 | 62.9883 | -0.27908 | 0.012589 | 0.014452 | 0.0067185 | 0.065371 | -0.0023926 | 0.06896 | -61.821 | 62.8464 | -62.027 | -61.8896 | 62.7136 | 0.13733 | 0.013733 | 0.26093 | 62.8967 | -62.0178 | -0.27008 | -0.14191 | -0.064087 | -0.13275 | -0.27466 | -0.26093 | -0.091552 | 0.20599 | 61.7706 | 62.0178 | 124.4705 | 124.6033 | -0.064087 | 124.6536 | 61.8942 | -0.26093 | 124.6033 | -0.064087 | 61.8942 | 124.4705 | 124.6536 | -125.0153 | -125.0061
336.375 | 125.061 | -61.7706 | 62.97 | -0.15701 | 0.0070346 | 0.0069748 | 0.0037277 | 0.06708 | -0.00068359 | 0.069387 | -61.441 | 62.9059 | -61.9629 | -61.8668 | 62.6907 | 0.10529 | -0.07782 | 0.25177 | 62.8876 | -61.9995 | -0.19226 | -0.064087 | 0.32959 | -0.09613 | -0.27924 | -0.22888 | -0.082398 | 0.52185 | 61.6928 | 62.0224 | 124.4614 | 124.6765 | 0.32959 | 124.6582 | 61.8759 | -0.22888 | 124.6765 | 0.32959 | 61.8759 | 124.4614 | 124.6582 | -124.9329 | -124.9695
337.375 | 125.0519 | -61.7844 | 62.9425 | -0.18753 | 0.010025 | 0.012102 | 0.0033005 | 0.066225 | -0.002179 | 0.068319 | -61.8164 | 62.8464 | -62.0087 | -61.8713 | 62.7136 | 0.50812 | -0.059509 | -0.041199 | 62.9196 | -61.972 | -0.2243 | -0.09613 | -0.032043 | -0.086975 | -0.22888 | -0.18768 | -0.022888 | 0.19226 | 61.7249 | 61.7432 | 124.498 | 124.6307 | -0.032043 | 124.704 | 62.2925 | -0.18768 | 124.6307 | -0.032043 | 62.2925 | 124.498 | 124.704 | -124.9512 | -124.9146
338.375 | 125.0061 | -61.7523 | 62.9929 | -0.2562 | 0.0087436 | 0.015092 | 0.0013779 | 0.067507 | -0.00046999 | 0.068746 | -61.8256 | 62.8281 | -62.027 | -61.8668 | 62.7274 | 0.16479 | -0.054932 | 0.28839 | 62.8601 | -61.9812 | -0.27466 | -0.1648 | -0.073243 | -0.11444 | -0.2655 | -0.22888 | -0.13275 | 0.20142 | 61.6974 | 62.0407 | 124.4797 | 124.5804 | -0.073243 | 124.6124 | 61.9171 | -0.22888 | 124.5804 | -0.073243 | 61.9171 | 124.4797 | 124.6124 | -125.0198 | -124.9741
339.375 | 125.0336 | -61.7615 | 62.9883 | -0.71396 | 0.011307 | 0.012529 | 0.0050095 | 0.066866 | -0.0017518 | 0.069814 | -61.8713 | 62.8006 | -62.0132 | -61.8851 | 62.7411 | 0.15106 | -0.050354 | 0.28381 | 62.8601 | -61.9858 | -0.25177 | -0.18768 | -0.10986 | -0.1236 | -0.24719 | -0.2243 | -0.12817 | 0.14191 | 61.7111 | 62.0453 | 124.5026 | 124.5621 | -0.10986 | 124.6216 | 61.9125 | -0.2243 | 124.5621 | -0.10986 | 61.9125 | 124.5026 | 124.6216 | -125.0015 | -124.9741
340.375 | 125.0931 | -61.7523 | 62.9517 | -0.14175 | 0.010025 | 0.014024 | -0.00011753 | 0.068789 | 0.00081181 | 0.066823 | -61.8164 | 62.8464 | -62.0087 | -61.853 | 62.6587 | 0.045776 | 0 | 0.24261 | 62.8464 | -61.9949 | -0.25635 | -0.10528 | -0.064087 | -0.10071 | -0.29297 | -0.24262 | -0.10528 | 0.19226 | 61.7523 | 61.9949 | 124.411 | 124.5987 | -0.064087 | 124.5987 | 61.7981 | -0.24262 | 124.5987 | -0.064087 | 61.7981 | 124.411 | 124.5987 | -124.9603 | -124.9466
341.375 | 124.9786 | -61.7569 | 62.9654 | -0.057831 | 0.00853 | 0.0082566 | 0.0039413 | 0.067293 | -0.00025639 | 0.067891 | -61.7981 | 62.8418 | -62.0132 | -61.8668 | 62.7365 | 0.16479 | 0.086975 | 0.68665 | 62.9059 | -61.9217 | -0.25635 | -0.1236 | -0.041199 | -0.10986 | -0.22888 | -0.16479 | -0.059509 | 0.21515 | 61.8439 | 62.4435 | 124.4934 | 124.5987 | -0.041199 | 124.6628 | 61.9217 | -0.16479 | 124.5987 | -0.041199 | 61.9217 | 124.4934 | 124.6628 | -124.9786 | -124.8871
342.375 | 125.0198 | -61.7523 | 62.9791 | -0.14175 | 0.011734 | 0.013383 | 0.0028733 | 0.066866 | -0.0030334 | 0.068746 | -61.8439 | 62.8189 | -62.027 | -61.908 | 62.7411 | 0.15564 | -0.10986 | 0.27466 | 62.8738 | -62.0087 | -0.27466 | -0.16022 | -0.091553 | -0.15564 | -0.23804 | -0.25635 | -0.10529 | 0.18311 | 61.6425 | 62.027 | 124.4934 | 124.5712 | -0.091553 | 124.6262 | 61.908 | -0.25635 | 124.5712 | -0.091553 | 61.908 | 124.4934 | 124.6262 | -125.0061 | -124.9878
343.375 | 125.061 | -61.7798 | 62.97 | -0.11124 | 0.011948 | 0.01317 | 0.0039413 | 0.066012 | 0.00017081 | 0.06896 | -61.8484 | 62.8326 | -61.9949 | -61.8851 | 62.709 | 0.1236 | -0.07782 | 0.22888 | 62.8464 | -61.9949 | -0.21515 | -0.13733 | -0.068665 | -0.10529 | -0.26093 | -0.21515 | -0.1236 | 0.14648 | 61.702 | 62.0087 | 124.4888 | 124.6124 | -0.068665 | 124.6262 | 61.9034 | -0.21515 | 124.6124 | -0.068665 | 61.9034 | 124.4888 | 124.6262 | -124.9649 | -124.9649
344.375 | 125.0107 | -61.7844 | 62.97 | -0.16464 | 0.013016 | 0.0065476 | 0.00095067 | 0.070498 | 0.00017081 | 0.067037 | -61.8073 | 62.8418 | -62.0041 | -61.8393 | 62.6724 | 0.054932 | -0.027466 | 0.24261 | 62.8647 | -61.9904 | -0.21973 | -0.12817 | -0.022888 | -0.054931 | -0.29755 | -0.20599 | -0.10529 | 0.19684 | 61.7569 | 62.027 | 124.4568 | 124.6262 | -0.022888 | 124.649 | 61.8393 | -0.20599 | 124.6262 | -0.022888 | 61.8393 | 124.4568 | 124.649 | -124.9741 | -124.9603
345.375 | 125.1022 | -61.7661 | 62.9517 | -0.1265 | 0.011521 | 0.0093246 | 0.0018051 | 0.065157 | -0.0013244 | 0.070028 | -61.8164 | 62.8281 | -62.0178 | -61.8622 | 62.7548 | 0.09613 | 0.39825 | 0.44861 | 62.9196 | -61.9446 | -0.25177 | -0.1236 | -0.050354 | -0.096131 | -0.19684 | -0.17853 | -0.032043 | 0.20142 | 62.1643 | 62.2147 | 124.5209 | 124.5941 | -0.050354 | 124.6857 | 61.8622 | -0.17853 | 124.5941 | -0.050354 | 61.8622 | 124.5209 | 124.6857 | -124.9695 | -124.8962
346.375 | 125.0793 | -61.7386 | 62.9745 | -0.11887 | 0.012375 | 0.012102 | 0.0018051 | 0.067293 | -0.0026062 | 0.069387 | -61.8256 | 62.8418 | -62.0041 | -61.8576 | 62.7319 | 0.17853 | -0.07782 | 0.28381 | 62.8693 | -61.9904 | -0.2655 | -0.13275 | -0.086976 | -0.11902 | -0.24261 | -0.25177 | -0.10529 | 0.17853 | 61.6608 | 62.0224 | 124.4705 | 124.5804 | -0.086976 | 124.6078 | 61.9171 | -0.25177 | 124.5804 | -0.086976 | 61.9171 | 124.4705 | 124.6078 | -124.9786 | -124.9649
347.375 | 125.0427 | -61.7569 | 62.9883 | -0.14175 | 0.011521 | 0.015306 | 0.0022323 | 0.06708 | 0.00059821 | 0.069173 | -61.8301 | 62.8235 | -62.0041 | -61.8896 | 62.6907 | 0.11902 | -0.068665 | 0.26093 | 62.8555 | -61.9675 | -0.24719 | -0.16479 | -0.073242 | -0.13275 | -0.29755 | -0.21057 | -0.13275 | 0.17395 | 61.6882 | 62.0178 | 124.4476 | 124.5804 | -0.073242 | 124.6124 | 61.8759 | -0.21057 | 124.5804 | -0.073242 | 61.8759 | 124.4476 | 124.6124 | -124.9924 | -124.9557
348.375 | 125.0565 | -61.7523 | 62.97 | -0.095978 | 0.011948 | 0.012102 | 0.0033005 | 0.065798 | 0.00059821 | 0.06896 | -61.8622 | 62.8189 | -62.0316 | -61.8942 | 62.7045 | 0.12817 | -0.068665 | 0.22888 | 62.8647 | -62.0041 | -0.27924 | -0.15106 | -0.10986 | -0.14191 | -0.2655 | -0.25177 | -0.10529 | 0.16937 | 61.6837 | 61.9812 | 124.4568 | 124.5712 | -0.10986 | 124.617 | 61.8805 | -0.25177 | 124.5712 | -0.10986 | 61.8805 | 124.4568 | 124.617 | -125.0015 | -124.9741
349.4375 | 124.9924 | -61.7661 | 62.9425 | 0.12527 | 0.012589 | 0.015733 | 0.0024461 | 0.070498 | 0.00081181 | 0.070028 | -61.8668 | 62.8326 | -62.0361 | -61.9492 | 62.6404 | 0.022888 | -0.14648 | 0.10986 | 62.8326 | -62.0316 | -0.27008 | -0.10986 | -0.10071 | -0.18311 | -0.30212 | -0.2655 | -0.10986 | 0.16937 | 61.6196 | 61.8759 | 124.4064 | 124.5987 | -0.10071 | 124.5987 | 61.7889 | -0.2655 | 124.5987 | -0.10071 | 61.7889 | 124.4064 | 124.5987 | -124.9786 | -124.9741
350.375 | 125.0107 | -61.7569 | 62.97 | -0.057831 | 0.012375 | 0.01552 | 0.0030869 | 0.064944 | -0.0011108 | 0.06896 | -61.8576 | 62.851 | -62.0499 | -61.9171 | 62.6999 | 0.10071 | -0.073242 | 0.20142 | 62.8555 | -62.0087 | -0.29297 | -0.11902 | -0.10071 | -0.16022 | -0.27008 | -0.25177 | -0.11444 | 0.19226 | 61.6837 | 61.9583 | 124.4568 | 124.6078 | -0.10071 | 124.6124 | 61.8576 | -0.25177 | 124.6078 | -0.10071 | 61.8576 | 124.4568 | 124.6124 | -125.0198 | -124.9786
351.375 | 125.0015 | -61.7615 | 62.9517 | -0.050202 | 0.012589 | 0.011034 | 0.0026597 | 0.065798 | -0.00068359 | 0.06896 | -61.8805 | 62.8326 | -62.0453 | -61.9217 | 62.677 | 0.086975 | -0.064087 | 0.21515 | 62.851 | -61.972 | -0.28381 | -0.11902 | -0.11902 | -0.16022 | -0.27466 | -0.21057 | -0.10071 | 0.16479 | 61.6974 | 61.9766 | 124.4385 | 124.5941 | -0.11902 | 124.6124 | 61.8484 | -0.21057 | 124.5941 | -0.11902 | 61.8484 | 124.4385 | 124.6124 | -124.9969 | -124.9237
352.375 | 125.0702 | -61.7615 | 62.97 | -0.11887 | 0.010025 | 0.012743 | 0.0018051 | 0.068361 | -4.2788e-05 | 0.067464 | -61.8301 | 62.8281 | -62.0316 | -61.8851 | 62.7274 | 0.13275 | -0.086975 | 0.25635 | 62.8372 | -61.9812 | -0.27008 | -0.14191 | -0.068664 | -0.1236 | -0.24262 | -0.21973 | -0.13275 | 0.20142 | 61.6745 | 62.0178 | 124.4888 | 124.5895 | -0.068664 | 124.5987 | 61.8942 | -0.21973 | 124.5895 | -0.068664 | 61.8942 | 124.4888 | 124.5987 | -125.0015 | -124.9512
353.375 | 125.0473 | -61.7752 | 62.97 | -0.080719 | 0.013871 | 0.017015 | -0.00011753 | 0.067293 | -0.002179 | 0.06896 | -61.8484 | 62.8189 | -62.0178 | -61.8805 | 62.709 | 0.13275 | -0.073242 | 0.21973 | 62.8464 | -61.9904 | -0.24261 | -0.15106 | -0.073242 | -0.10529 | -0.26093 | -0.21515 | -0.1236 | 0.16937 | 61.702 | 61.9949 | 124.4843 | 124.5941 | -0.073242 | 124.6216 | 61.908 | -0.21515 | 124.5941 | -0.073242 | 61.908 | 124.4843 | 124.6216 | -124.9878 | -124.9603
354.375 | 125.0565 | -61.7569 | 62.9425 | -0.11887 | 0.010453 | 0.012956 | -0.0013993 | 0.066866 | -0.0011108 | 0.068105 | -61.8484 | 62.8372 | -62.0178 | -61.8851 | 62.7136 | 0.11902 | -0.068665 | 0.2243 | 62.8326 | -61.9904 | -0.26093 | -0.10529 | -0.091553 | -0.12817 | -0.22888 | -0.23346 | -0.10986 | 0.16937 | 61.6882 | 61.9812 | 124.4705 | 124.5941 | -0.091553 | 124.5895 | 61.8759 | -0.23346 | 124.5941 | -0.091553 | 61.8759 | 124.4705 | 124.5895 | -124.9603 | -124.9329
355.375 | 125.0244 | -61.7981 | 62.9745 | -0.095978 | 0.012375 | 0.012315 | 0.0013779 | 0.065371 | 0.00017081 | 0.068319 | -61.8347 | 62.8235 | -62.0178 | -61.908 | 62.6907 | 0.10529 | -0.073242 | 0.21057 | 62.8418 | -61.9904 | -0.21973 | -0.15106 | -0.036621 | -0.10986 | -0.28381 | -0.19226 | -0.13275 | 0.18311 | 61.7249 | 62.0087 | 124.4888 | 124.6216 | -0.036621 | 124.6399 | 61.9034 | -0.19226 | 124.6216 | -0.036621 | 61.9034 | 124.4888 | 124.6399 | -124.9924 | -124.9649
356.375 | 125.1068 | -61.7615 | 62.9425 | -0.080719 | 0.0093844 | 0.013383 | 0.0026597 | 0.066012 | -0.0017518 | 0.06896 | -61.8118 | 62.8372 | -61.9995 | -61.853 | 62.7274 | -0.041199 | 0.37994 | 0.41657 | 62.915 | -61.9446 | -0.23804 | -0.10529 | -0.050354 | -0.091552 | -0.21515 | -0.18311 | -0.027466 | 0.18768 | 62.1414 | 62.178 | 124.4888 | 124.5987 | -0.050354 | 124.6765 | 61.7203 | -0.18311 | 124.5987 | -0.050354 | 61.7203 | 124.4888 | 124.6765 | -124.942 | -124.8871
357.375 | 125.0565 | -61.8027 | 62.9791 | -0.034943 | 0.013657 | 0.0093246 | 0.00073707 | 0.067507 | -0.0015382 | 0.0696 | -61.8759 | 62.8464 | -62.0178 | -61.9171 | 62.6816 | 0.091553 | -0.068665 | 0.21057 | 62.8738 | -62.0087 | -0.21515 | -0.13275 | -0.073243 | -0.11444 | -0.29755 | -0.20599 | -0.10529 | 0.14191 | 61.734 | 62.0132 | 124.4843 | 124.649 | -0.073243 | 124.6765 | 61.8942 | -0.20599 | 124.649 | -0.073243 | 61.8942 | 124.4843 | 124.6765 | -124.9969 | -124.9878
358.375 | 125.0336 | -61.7569 | 62.9654 | -0.11887 | 0.01088 | 0.011888 | 0.0030869 | 0.064089 | -0.0015382 | 0.06896 | -61.8393 | 62.8143 | -62.0224 | -61.8896 | 62.7228 | 0.12817 | -0.07782 | 0.23804 | 62.8464 | -61.9858 | -0.2655 | -0.15106 | -0.082397 | -0.13275 | -0.24262 | -0.22888 | -0.11902 | 0.18311 | 61.6791 | 61.9949 | 124.4797 | 124.5712 | -0.082397 | 124.6033 | 61.8851 | -0.22888 | 124.5712 | -0.082397 | 61.8851 | 124.4797 | 124.6033 | -124.9878 | -124.9512
359.375 | 125.0565 | -61.7661 | 62.9608 | -0.088349 | 0.011521 | 0.010393 | 0.0030869 | 0.065371 | -0.0030334 | 0.068532 | -61.8439 | 62.8464 | -62.0132 | -61.8851 | 62.6999 | 0.13275 | -0.07782 | 0.21973 | 62.8418 | -61.9812 | -0.24719 | -0.11444 | -0.07782 | -0.11902 | -0.26092 | -0.21515 | -0.11902 | 0.16937 | 61.6882 | 61.9858 | 124.4659 | 124.6124 | -0.07782 | 124.6078 | 61.8988 | -0.21515 | 124.6124 | -0.07782 | 61.8988 | 124.4659 | 124.6078 | -124.9741 | -124.942
360.375 | 125.0519 | -61.7706 | 62.9837 | -0.1265 | 0.011093 | 0.014665 | 0.0024461 | 0.067293 | -0.0017518 | 0.06896 | -61.8439 | 62.8418 | -62.027 | -61.8896 | 62.6953 | 0.13275 | -0.086975 | 0.2243 | 62.8372 | -61.9995 | -0.25635 | -0.14191 | -0.073242 | -0.11902 | -0.28839 | -0.22888 | -0.14649 | 0.18311 | 61.6837 | 61.9949 | 124.4659 | 124.6124 | -0.073242 | 124.6078 | 61.9034 | -0.22888 | 124.6124 | -0.073242 | 61.9034 | 124.4659 | 124.6078 | -125.0107 | -124.9832
361.375 | 125.0381 | -61.7752 | 62.9654 | -0.1265 | 0.011307 | 0.0099656 | 0.0033005 | 0.067934 | -0.002179 | 0.070028 | -61.8439 | 62.8601 | -62.0316 | -61.9034 | 62.6907 | 0.10529 | -0.059509 | 0.21973 | 62.8372 | -61.9812 | -0.25635 | -0.10529 | -0.068664 | -0.12817 | -0.27466 | -0.20599 | -0.12817 | 0.18768 | 61.7157 | 61.9949 | 124.4659 | 124.6353 | -0.068664 | 124.6124 | 61.8805 | -0.20599 | 124.6353 | -0.068664 | 61.8805 | 124.4659 | 124.6124 | -124.9969 | -124.9466
362.375 | 125.0153 | -61.7661 | 62.9654 | -0.1265 | 0.010666 | 0.014665 | 0.0015915 | 0.067293 | 0.0020934 | 0.068746 | -61.853 | 62.8098 | -62.0178 | -61.9034 | 62.6953 | 0.11902 | -0.07782 | 0.20599 | 62.8555 | -61.9858 | -0.25177 | -0.15564 | -0.086975 | -0.13733 | -0.27008 | -0.21973 | -0.10986 | 0.1648 | 61.6882 | 61.972 | 124.4614 | 124.5758 | -0.086975 | 124.6216 | 61.8851 | -0.21973 | 124.5758 | -0.086975 | 61.8851 | 124.4614 | 124.6216 | -124.9832 | -124.9512
363.375 | 125.0244 | -61.7706 | 62.9745 | -0.23331 | 0.011093 | 0.011888 | 0.0024461 | 0.065798 | -0.0011108 | 0.069387 | -61.7935 | 62.8372 | -62.027 | -61.6791 | 62.4161 | -0.027466 | -0.036621 | 0.10529 | 62.8189 | -61.9812 | -0.25635 | -0.13733 | -0.022888 | 0.091553 | -0.55847 | -0.21057 | -0.15564 | 0.23346 | 61.734 | 61.8759 | 124.1867 | 124.6078 | -0.022888 | 124.5895 | 61.7432 | -0.21057 | 124.6078 | -0.022888 | 61.7432 | 124.1867 | 124.5895 | -125.0015 | -124.9557
364.375 | 125.0107 | -61.7798 | 62.9837 | -0.06546 | 0.01088 | 0.010179 | 0.0024461 | 0.06473 | -0.0017518 | 0.068746 | -61.8622 | 62.8326 | -62.0361 | -61.8988 | 62.6862 | 0.091553 | -0.073242 | 0.21515 | 62.8326 | -61.9812 | -0.25635 | -0.15106 | -0.082398 | -0.11902 | -0.29755 | -0.20142 | -0.15106 | 0.17395 | 61.7065 | 61.9949 | 124.4659 | 124.6124 | -0.082398 | 124.6124 | 61.8713 | -0.20142 | 124.6124 | -0.082398 | 61.8713 | 124.4659 | 124.6124 | -125.0198 | -124.9649
365.375 | 125.0931 | -61.7386 | 63.0295 | -0.1799 | 0.011307 | 0.0099656 | 0.0039413 | 0.06473 | -0.0019654 | 0.069387 | -61.8256 | 62.8281 | -62.0224 | -61.8576 | 62.7274 | 0.16022 | -0.073242 | 0.2655 | 62.8555 | -61.9583 | -0.28381 | -0.20142 | -0.086976 | -0.11902 | -0.30212 | -0.21973 | -0.17395 | 0.19684 | 61.6653 | 62.0041 | 124.4659 | 124.5666 | -0.086976 | 124.5941 | 61.8988 | -0.21973 | 124.5666 | -0.086976 | 61.8988 | 124.4659 | 124.5941 | -125.0519 | -124.9878
366.375 | 125.0748 | -61.7661 | 62.9608 | -0.11887 | 0.01088 | 0.0076156 | 0.0018051 | 0.067507 | -0.0043152 | 0.069173 | -61.821 | 62.8326 | -62.0041 | -61.8942 | 62.709 | 0.10071 | -0.045776 | 0.24719 | 62.8464 | -61.9904 | -0.23804 | -0.12817 | -0.054932 | -0.12817 | -0.25177 | -0.2243 | -0.11444 | 0.1831 | 61.7203 | 62.0132 | 124.4751 | 124.5987 | -0.054932 | 124.6124 | 61.8668 | -0.2243 | 124.5987 | -0.054932 | 61.8668 | 124.4751 | 124.6124 | -124.9649 | -124.9512
367.375 | 125.0336 | -61.7706 | 62.9288 | -0.1265 | 0.011948 | 0.011461 | 0.0024461 | 0.06708 | -0.00046999 | 0.068532 | -61.8301 | 62.8098 | -61.9949 | -61.8805 | 62.7228 | 0.13275 | -0.086975 | 0.22888 | 62.8326 | -61.9675 | -0.2243 | -0.11902 | -0.059509 | -0.10986 | -0.20599 | -0.19684 | -0.09613 | 0.16479 | 61.6837 | 61.9995 | 124.4934 | 124.5804 | -0.059509 | 124.6033 | 61.9034 | -0.19684 | 124.5804 | -0.059509 | 61.9034 | 124.4934 | 124.6033 | -124.9237 | -124.8962
368.375 | 125.029 | -61.7661 | 62.9654 | -0.81314 | 0.012802 | 0.014238 | 9.6074e-05 | 0.067293 | -0.0011108 | 0.067037 | -61.9034 | 62.851 | -62.0224 | -61.8484 | 62.7319 | 0.16937 | -0.054932 | 0.28381 | 62.8372 | -61.9766 | -0.25635 | -0.11444 | -0.13733 | -0.082398 | -0.23346 | -0.21057 | -0.12817 | 0.11902 | 61.7111 | 62.0499 | 124.498 | 124.617 | -0.13733 | 124.6033 | 61.9354 | -0.21057 | 124.617 | -0.13733 | 61.9354 | 124.498 | 124.6033 | -124.9878 | -124.942
369.375 | 125.0748 | -61.7752 | 62.9929 | -0.07309 | 0.012802 | 0.012743 | 0.0015915 | 0.067721 | -4.2788e-05 | 0.068746 | -61.8484 | 62.8464 | -62.0407 | -61.8805 | 62.7228 | 0.1236 | -0.07782 | 0.21515 | 62.8281 | -61.9629 | -0.2655 | -0.14648 | -0.073242 | -0.10529 | -0.27008 | -0.18768 | -0.1648 | 0.19226 | 61.6974 | 61.9904 | 124.498 | 124.6216 | -0.073242 | 124.6033 | 61.8988 | -0.18768 | 124.6216 | -0.073242 | 61.8988 | 124.498 | 124.6033 | -125.0336 | -124.9557
370.375 | 125.0198 | -61.7477 | 62.9471 | -0.10361 | 0.011521 | 0.010393 | 0.00095067 | 0.066866 | -0.0011108 | 0.070455 | -61.8393 | 62.8235 | -62.0132 | -61.8896 | 62.709 | 0.10986 | -0.07782 | 0.2243 | 62.8143 | -61.9812 | -0.2655 | -0.1236 | -0.091552 | -0.14191 | -0.23804 | -0.23346 | -0.13275 | 0.17395 | 61.6699 | 61.972 | 124.4568 | 124.5712 | -0.091552 | 124.5621 | 61.8576 | -0.23346 | 124.5712 | -0.091552 | 61.8576 | 124.4568 | 124.5621 | -124.9603 | -124.9283
371.375 | 125.0244 | -61.7844 | 62.97 | -0.1265 | 0.010025 | 0.011675 | 0.0028733 | 0.067721 | -0.00025639 | 0.06896 | -61.8439 | 62.8372 | -62.0087 | -61.908 | 62.6999 | 0.10529 | -0.073242 | 0.23346 | 62.8647 | -61.972 | -0.2243 | -0.13275 | -0.059509 | -0.1236 | -0.27008 | -0.18768 | -0.10529 | 0.1648 | 61.7111 | 62.0178 | 124.4843 | 124.6216 | -0.059509 | 124.649 | 61.8896 | -0.18768 | 124.6216 | -0.059509 | 61.8896 | 124.4843 | 124.649 | -124.9786 | -124.942
372.375 | 125.0839 | -61.7706 | 62.9471 | -0.10361 | 0.01088 | 0.015092 | 0.00095067 | 0.066225 | -0.0030334 | 0.070455 | -61.7981 | 62.8326 | -62.0407 | -61.5646 | 62.558 | -0.082397 | 0.004578 | 0.12817 | 62.8052 | -61.9949 | -0.27008 | -0.11444 | -0.027466 | 0.20599 | -0.3891 | -0.2243 | -0.14191 | 0.24261 | 61.7752 | 61.8988 | 124.3286 | 124.6033 | -0.027466 | 124.5758 | 61.6882 | -0.2243 | 124.6033 | -0.027466 | 61.6882 | 124.3286 | 124.5758 | -124.9878 | -124.942
373.375 | 125.029 | -61.7752 | 62.9837 | -0.23331 | 0.010666 | 0.01082 | 0.0030869 | 0.068575 | -0.0023926 | 0.069173 | -61.8118 | 62.8235 | -61.9995 | -61.853 | 62.7411 | 0.16022 | -0.032043 | 0.27008 | 62.8784 | -61.9766 | -0.2243 | -0.16022 | -0.036621 | -0.077819 | -0.24262 | -0.20142 | -0.10529 | 0.18768 | 61.7432 | 62.0453 | 124.5163 | 124.5987 | -0.036621 | 124.6536 | 61.9354 | -0.20142 | 124.5987 | -0.036621 | 61.9354 | 124.5163 | 124.6536 | -124.9832 | -124.9603
374.375 | 124.9557 | -61.7477 | 62.9929 | -0.16464 | 0.010666 | 0.013383 | 0.0028733 | 0.066439 | -0.0030334 | 0.072591 | -61.821 | 62.8372 | -62.0178 | -61.8484 | 62.7365 | 0.15106 | -0.09613 | 0.2655 | 62.8418 | -61.9904 | -0.27008 | -0.15564 | -0.073242 | -0.10071 | -0.25635 | -0.24261 | -0.15106 | 0.19684 | 61.6516 | 62.0132 | 124.4843 | 124.585 | -0.073242 | 124.5895 | 61.8988 | -0.24261 | 124.585 | -0.073242 | 61.8988 | 124.4843 | 124.5895 | -125.0107 | -124.9832
375.375 | 125.0473 | -61.7569 | 62.97 | -0.088349 | 0.010453 | 0.011034 | 0.0024461 | 0.067293 | -0.0011108 | 0.071096 | -61.8347 | 62.8098 | -62.0132 | -61.8942 | 62.6953 | 0.15106 | -0.073242 | 0.2655 | 62.8281 | -61.9675 | -0.25635 | -0.16022 | -0.07782 | -0.13733 | -0.27466 | -0.21057 | -0.14191 | 0.17853 | 61.6837 | 62.0224 | 124.4522 | 124.5667 | -0.07782 | 124.585 | 61.908 | -0.21057 | 124.5667 | -0.07782 | 61.908 | 124.4522 | 124.585 | -124.9832 | -124.9374
376.375 | 125.029 | -61.7752 | 62.9608 | -0.14175 | 0.01088 | 0.01317 | 0.0020187 | 0.067507 | -0.003247 | 0.068532 | -61.821 | 62.8372 | -62.0453 | -61.8759 | 62.6999 | 0.13275 | -0.086975 | 0.24261 | 62.8464 | -61.9675 | -0.27008 | -0.1236 | -0.045776 | -0.10071 | -0.26092 | -0.19226 | -0.11444 | 0.2243 | 61.6882 | 62.0178 | 124.4751 | 124.6124 | -0.045776 | 124.6216 | 61.908 | -0.19226 | 124.6124 | -0.045776 | 61.908 | 124.4751 | 124.6216 | -125.0061 | -124.9283
377.375 | 125.0244 | -61.7477 | 62.9471 | -0.050202 | 0.010239 | 0.011675 | 9.6074e-05 | 0.065798 | -0.00068359 | 0.068532 | -61.853 | 62.851 | -62.0132 | -61.8988 | 62.6999 | 0.11902 | -0.07782 | 0.23346 | 62.8281 | -61.972 | -0.2655 | -0.096131 | -0.10528 | -0.15106 | -0.24719 | -0.2243 | -0.11902 | 0.16022 | 61.6699 | 61.9812 | 124.4476 | 124.5987 | -0.10528 | 124.5758 | 61.8668 | -0.2243 | 124.5987 | -0.10528 | 61.8668 | 124.4476 | 124.5758 | -124.9603 | -124.9191
378.375 | 125.0473 | -61.7844 | 62.9654 | -0.1265 | 0.011948 | 0.01317 | 0.0018051 | 0.063448 | -4.2788e-05 | 0.068105 | -61.8393 | 62.8372 | -62.0178 | -61.9034 | 62.6907 | 0.11444 | -0.091553 | 0.20142 | 62.8693 | -61.9904 | -0.23346 | -0.12817 | -0.054931 | -0.11902 | -0.27466 | -0.20599 | -0.09613 | 0.17853 | 61.6928 | 61.9858 | 124.4751 | 124.6216 | -0.054931 | 124.6536 | 61.8988 | -0.20599 | 124.6216 | -0.054931 | 61.8988 | 124.4751 | 124.6536 | -124.9832 | -124.9557
379.375 | 125.0519 | -61.7569 | 63.0432 | -0.19516 | 0.012375 | 0.012743 | 0.0013779 | 0.067507 | -0.0023926 | 0.069387 | -61.8256 | 62.8281 | -62.0132 | -61.8713 | 62.7411 | 0.16937 | -0.086975 | 0.27466 | 62.8464 | -61.9675 | -0.25635 | -0.21515 | -0.068665 | -0.11444 | -0.30212 | -0.21057 | -0.19684 | 0.18768 | 61.6699 | 62.0316 | 124.498 | 124.585 | -0.068665 | 124.6033 | 61.9263 | -0.21057 | 124.585 | -0.068665 | 61.9263 | 124.498 | 124.6033 | -125.0565 | -125.0107
380.375 | 125.0519 | -61.7569 | 62.9791 | -0.15701 | 0.011093 | 0.016374 | 0.0018051 | 0.066439 | -0.00068359 | 0.069814 | -61.8347 | 62.8281 | -62.0224 | -61.8759 | 62.7182 | 0.13733 | -0.07782 | 0.24261 | 62.851 | -61.9675 | -0.2655 | -0.15106 | -0.07782 | -0.11902 | -0.26093 | -0.21057 | -0.12817 | 0.18768 | 61.6791 | 61.9995 | 124.4751 | 124.585 | -0.07782 | 124.6078 | 61.8942 | -0.21057 | 124.585 | -0.07782 | 61.8942 | 124.4751 | 124.6078 | -125.0015 | -124.9466
381.375 | 125.0702 | -61.7706 | 62.97 | -0.06546 | 0.012375 | 0.011034 | 0.0013779 | 0.068148 | -0.00068359 | 0.069814 | -61.8576 | 62.8418 | -62.0178 | -61.8988 | 62.7045 | 0.1236 | -0.07782 | 0.22888 | 62.8189 | -61.9904 | -0.24719 | -0.12817 | -0.086975 | -0.12817 | -0.2655 | -0.21973 | -0.15106 | 0.16022 | 61.6928 | 61.9995 | 124.4751 | 124.6124 | -0.086975 | 124.5895 | 61.8942 | -0.21973 | 124.6124 | -0.086975 | 61.8942 | 124.4751 | 124.5895 | -124.9878 | -124.9603
382.375 | 124.9695 | -61.7706 | 62.9654 | -0.050202 | 0.011948 | 0.014024 | 0.0020187 | 0.065584 | -0.0023926 | 0.068319 | -61.8576 | 62.8189 | -62.0178 | -61.8988 | 62.6907 | 0.10529 | -0.073242 | 0.21057 | 62.8281 | -61.9812 | -0.24719 | -0.14648 | -0.086975 | -0.12817 | -0.27466 | -0.21057 | -0.13733 | 0.16022 | 61.6974 | 61.9812 | 124.4614 | 124.5895 | -0.086975 | 124.5987 | 61.8759 | -0.21057 | 124.5895 | -0.086975 | 61.8759 | 124.4614 | 124.5987 | -124.9832 | -124.9466
383.375 | 125.0381 | -61.7706 | 62.9562 | -0.13412 | 0.012589 | 0.009752 | 0.0020187 | 0.065157 | -0.0019654 | 0.069173 | -61.8393 | 62.8281 | -62.0316 | -61.8668 | 62.7228 | 0.15106 | -0.10071 | 0.25635 | 62.8555 | -61.9949 | -0.26093 | -0.12817 | -0.068664 | -0.09613 | -0.23346 | -0.2243 | -0.10071 | 0.19226 | 61.6699 | 62.027 | 124.4934 | 124.5987 | -0.068664 | 124.6262 | 61.9217 | -0.2243 | 124.5987 | -0.068664 | 61.9217 | 124.4934 | 124.6262 | -124.9878 | -124.9512
384.375 | 125.0061 | -61.7569 | 62.9745 | -0.088349 | 0.013657 | 0.014665 | 0.0011643 | 0.066652 | -0.0015382 | 0.06896 | -61.8484 | 62.8464 | -62.0041 | -61.8668 | 62.6862 | 0.1236 | -0.07782 | 0.24261 | 62.8555 | -62.0041 | -0.24719 | -0.12817 | -0.091553 | -0.10986 | -0.28839 | -0.24719 | -0.11902 | 0.15564 | 61.6791 | 61.9995 | 124.4431 | 124.6033 | -0.091553 | 124.6124 | 61.8805 | -0.24719 | 124.6033 | -0.091553 | 61.8805 | 124.4431 | 124.6124 | -124.9786 | -124.9786
385.375 | 124.9649 | -61.7798 | 62.9791 | -0.1265 | 0.012162 | 0.012102 | 0.0024461 | 0.066866 | -0.00068359 | 0.070455 | -61.8851 | 62.8326 | -62.0407 | -61.9537 | 62.6404 | 0.032043 | -0.059509 | 0.14191 | 62.8464 | -61.9766 | -0.26093 | -0.14648 | -0.10529 | -0.17395 | -0.33875 | -0.19684 | -0.13275 | 0.15564 | 61.7203 | 61.9217 | 124.4202 | 124.6124 | -0.10529 | 124.6262 | 61.8118 | -0.19684 | 124.6124 | -0.10529 | 61.8118 | 124.4202 | 124.6262 | -125.0198 | -124.9557
386.375 | 124.9695 | -61.7981 | 62.9517 | -0.050202 | 0.010239 | 0.01552 | 0.0018051 | 0.066012 | -0.0041016 | 0.068319 | -61.8851 | 62.8235 | -62.0407 | -61.9354 | 62.6862 | 0.073242 | -0.068665 | 0.16937 | 62.8235 | -61.9812 | -0.24261 | -0.12817 | -0.086975 | -0.13733 | -0.2655 | -0.1831 | -0.12817 | 0.15564 | 61.7294 | 61.9675 | 124.4843 | 124.6216 | -0.086975 | 124.6216 | 61.8713 | -0.1831 | 124.6216 | -0.086975 | 61.8713 | 124.4843 | 124.6216 | -124.9924 | -124.9329
387.375 | 124.9969 | -61.7889 | 62.9745 | -0.07309 | 0.013443 | 0.014452 | 0.0020187 | 0.067293 | -0.0015382 | 0.066823 | -61.8942 | 62.8326 | -62.0407 | -61.9308 | 62.6633 | 0.059509 | -0.073242 | 0.15564 | 62.8326 | -61.9766 | -0.25177 | -0.14191 | -0.10529 | -0.14191 | -0.31128 | -0.18768 | -0.14191 | 0.14648 | 61.7157 | 61.9446 | 124.4522 | 124.6216 | -0.10529 | 124.6216 | 61.8484 | -0.18768 | 124.6216 | -0.10529 | 61.8484 | 124.4522 | 124.6216 | -125.0153 | -124.9512
388.375 | 124.9969 | -61.7752 | 62.97 | -0.07309 | 0.012375 | 0.012529 | 0.0018051 | 0.064516 | 0.00038461 | 0.069173 | -61.8851 | 62.8189 | -62.0453 | -61.9308 | 62.6633 | 0.032043 | -0.064087 | 0.15564 | 62.8464 | -62.0178 | -0.27008 | -0.15106 | -0.10986 | -0.15564 | -0.3067 | -0.24261 | -0.1236 | 0.16022 | 61.7111 | 61.9308 | 124.4385 | 124.5941 | -0.10986 | 124.6216 | 61.8073 | -0.24261 | 124.5941 | -0.10986 | 61.8073 | 124.4385 | 124.6216 | -125.0153 | -124.9878
389.3906 | 124.9054 | -61.7889 | 63.0341 | -0.24857 | 0.01558 | 0.011888 | 0.0084275 | 0.067507 | -0.00025639 | 0.068105 | -61.8622 | 62.9562 | -62.0499 | -61.9354 | 62.6312 | 0.050354 | 0.10529 | 0.15564 | 62.915 | -62.0132 | -0.26093 | -0.07782 | -0.073243 | -0.14649 | -0.40283 | -0.22431 | -0.11902 | 0.18768 | 61.8942 | 61.9446 | 124.4202 | 124.7452 | -0.073243 | 124.704 | 61.8393 | -0.22431 | 124.7452 | -0.073243 | 61.8393 | 124.4202 | 124.704 | -125.0839 | -125.0473
390.375 | 125.1114 | -61.7752 | 62.97 | 0.087128 | 0.011734 | 0.014238 | 0.0018051 | 0.067293 | -0.00068359 | 0.067678 | -61.8942 | 62.8143 | -62.0224 | -61.9308 | 62.6495 | 0.027466 | -0.091553 | 0.12817 | 62.851 | -61.972 | -0.24719 | -0.15564 | -0.11902 | -0.15564 | -0.32044 | -0.19684 | -0.11902 | 0.12817 | 61.6837 | 61.9034 | 124.4247 | 124.5895 | -0.11902 | 124.6262 | 61.8027 | -0.19684 | 124.5895 | -0.11902 | 61.8027 | 124.4247 | 124.6262 | -124.9924 | -124.942
391.375 | 125.0015 | -61.7752 | 62.9379 | 0.079498 | 0.012375 | 0.014024 | 0.0028733 | 0.066225 | -0.00025639 | 0.071737 | -61.8851 | 62.8235 | -62.0316 | -61.9492 | 62.6495 | 0.041199 | -0.1236 | 0.11444 | 62.8464 | -62.0132 | -0.25635 | -0.11444 | -0.10986 | -0.17395 | -0.28839 | -0.23804 | -0.091552 | 0.14648 | 61.6516 | 61.8896 | 124.4247 | 124.5987 | -0.10986 | 124.6216 | 61.8164 | -0.23804 | 124.5987 | -0.10986 | 61.8164 | 124.4247 | 124.6216 | -124.9695 | -124.9512
392.375 | 124.9741 | -61.7889 | 62.9333 | 0.14816 | 0.013657 | 0.011461 | 0.0035141 | 0.067293 | 0.00017081 | 0.068319 | -61.853 | 62.8189 | -62.0132 | -61.9308 | 62.6541 | 0.050354 | -0.16022 | 0.1236 | 62.8235 | -62.0087 | -0.22431 | -0.11444 | -0.064087 | -0.14191 | -0.27924 | -0.21973 | -0.10986 | 0.16022 | 61.6287 | 61.9125 | 124.4431 | 124.6078 | -0.064087 | 124.6124 | 61.8393 | -0.21973 | 124.6078 | -0.064087 | 61.8393 | 124.4431 | 124.6124 | -124.9466 | -124.942
393.375 | 124.9924 | -61.7798 | 62.9196 | 0.071869 | 0.014084 | 0.012529 | 0.00095067 | 0.067293 | -0.0019654 | 0.071096 | -61.8668 | 62.8281 | -62.027 | -61.9537 | 62.6587 | 0.032043 | -0.091553 | 0.12817 | 62.8235 | -62.0178 | -0.24719 | -0.091553 | -0.086975 | -0.17395 | -0.26093 | -0.23804 | -0.096131 | 0.16022 | 61.6882 | 61.908 | 124.4385 | 124.6078 | -0.086975 | 124.6033 | 61.8118 | -0.23804 | 124.6078 | -0.086975 | 61.8118 | 124.4385 | 124.6033 | -124.9466 | -124.9374
394.3906 | 125.0107 | -61.7569 | 62.97 | -0.23331 | 0.013871 | 0.012529 | 0.0018051 | 0.06473 | -0.0028198 | 0.070241 | -61.8164 | 62.8647 | -62.0178 | -61.8713 | 62.709 | 0.15564 | 0.027466 | 0.25635 | 62.8601 | -61.972 | -0.26093 | -0.10529 | -0.059509 | -0.11444 | -0.26093 | -0.21515 | -0.10986 | 0.20142 | 61.7844 | 62.0132 | 124.4659 | 124.6216 | -0.059509 | 124.617 | 61.9125 | -0.21515 | 124.6216 | -0.059509 | 61.9125 | 124.4659 | 124.617 | -124.9878 | -124.942
395.375 | 125.0107 | -61.7615 | 62.915 | 0.16342 | 0.014084 | 0.015306 | 0.0056503 | 0.068148 | -0.0023926 | 0.071737 | -61.8164 | 62.8647 | -62.027 | -61.9034 | 62.6724 | 0.064087 | -0.18768 | 0.15564 | 62.8235 | -62.0041 | -0.2655 | -0.050354 | -0.054931 | -0.14191 | -0.24262 | -0.24261 | -0.091553 | 0.21057 | 61.5738 | 61.9171 | 124.4339 | 124.6262 | -0.054931 | 124.585 | 61.8256 | -0.24261 | 124.6262 | -0.054931 | 61.8256 | 124.4339 | 124.585 | -124.942 | -124.9191
396.375 | 125.0244 | -61.7935 | 62.9059 | 0.12527 | 0.013871 | 0.016161 | 0.0056503 | 0.069002 | -0.0015382 | 0.070455 | -61.8301 | 62.851 | -62.0132 | -61.908 | 62.6724 | 0.064087 | -0.16022 | 0.15106 | 62.8098 | -62.0361 | -0.21973 | -0.054932 | -0.036621 | -0.11444 | -0.23346 | -0.24262 | -0.096131 | 0.18311 | 61.6333 | 61.9446 | 124.4659 | 124.6445 | -0.036621 | 124.6033 | 61.8576 | -0.24262 | 124.6445 | -0.036621 | 61.8576 | 124.4659 | 124.6033 | -124.9191 | -124.942
397.375 | 125.0107 | -61.7844 | 62.9288 | 0.15579 | 0.012162 | 0.015947 | 0.0037277 | 0.06708 | -0.00025639 | 0.070241 | -61.8256 | 62.8464 | -62.0636 | -61.9125 | 62.677 | 0.073242 | -0.1831 | 0.15564 | 62.8189 | -62.0132 | -0.27924 | -0.082397 | -0.041199 | -0.12817 | -0.25177 | -0.22888 | -0.10986 | 0.23804 | 61.6013 | 61.94 | 124.4614 | 124.6307 | -0.041199 | 124.6033 | 61.8576 | -0.22888 | 124.6307 | -0.041199 | 61.8576 | 124.4614 | 124.6033 | -124.9924 | -124.942
398.375 | 125.0015 | -61.7889 | 62.9196 | 0.15579 | 0.013657 | 0.01082 | 0.0067185 | 0.066866 | -0.002179 | 0.069387 | -61.821 | 62.8143 | -62.0453 | -61.9034 | 62.677 | 0.050354 | -0.18768 | 0.15106 | 62.8006 | -62.027 | -0.25635 | -0.10529 | -0.032044 | -0.11444 | -0.24262 | -0.23804 | -0.11902 | 0.2243 | 61.6013 | 61.94 | 124.4659 | 124.6033 | -0.032044 | 124.5895 | 61.8393 | -0.23804 | 124.6033 | -0.032044 | 61.8393 | 124.4659 | 124.5895 | -124.9649 | -124.9466
399.3906 | 124.9786 | -61.7752 | 62.9974 | -0.27908 | 0.010239 | 0.01317 | 0.0056503 | 0.068361 | -0.0047424 | 0.06896 | -61.8256 | 62.8784 | -62.0132 | -61.9217 | 62.6862 | 0.11444 | 0.073242 | 0.23804 | 62.8555 | -62.0178 | -0.23804 | -0.11902 | -0.050354 | -0.14648 | -0.31128 | -0.24261 | -0.14191 | 0.18768 | 61.8484 | 62.0132 | 124.4614 | 124.6536 | -0.050354 | 124.6307 | 61.8896 | -0.24261 | 124.6536 | -0.050354 | 61.8896 | 124.4614 | 124.6307 | -125.0107 | -125.0153
400.375 | 125.0336 | -61.7661 | 62.9425 | 0.12527 | 0.013657 | 0.012956 | 0.0047959 | 0.06943 | -0.0030334 | 0.071096 | -61.8301 | 62.851 | -62.0178 | -61.9171 | 62.6862 | 0.050354 | -0.16479 | 0.15106 | 62.8189 | -62.0499 | -0.25177 | -0.091553 | -0.064087 | -0.15106 | -0.25635 | -0.28381 | -0.1236 | 0.18768 | 61.6013 | 61.9171 | 124.4522 | 124.617 | -0.064087 | 124.585 | 61.8164 | -0.28381 | 124.617 | -0.064087 | 61.8164 | 124.4522 | 124.585 | -124.9603 | -124.9924
401.375 | 124.9924 | -61.7706 | 62.9379 | 0.14816 | 0.013871 | 0.015947 | 0.0054367 | 0.070925 | -0.00025639 | 0.069387 | -61.8073 | 62.8418 | -62.0407 | -61.9034 | 62.677 | 0.054932 | -0.19684 | 0.14648 | 62.8326 | -62.027 | -0.27008 | -0.09613 | -0.036621 | -0.13275 | -0.26093 | -0.25635 | -0.10529 | 0.23346 | 61.5738 | 61.9171 | 124.4476 | 124.6124 | -0.036621 | 124.6033 | 61.8256 | -0.25635 | 124.6124 | -0.036621 | 61.8256 | 124.4476 | 124.6033 | -124.9786 | -124.9649
402.375 | 125.0153 | -61.7569 | 62.9471 | 0.17105 | 0.014084 | 0.01082 | 0.0071457 | 0.072207 | -0.002179 | 0.071096 | -61.8256 | 62.8418 | -62.0224 | -61.8805 | 62.6678 | 0.068665 | -0.19684 | 0.14648 | 62.8189 | -62.0178 | -0.2655 | -0.10529 | -0.068665 | -0.1236 | -0.27924 | -0.26093 | -0.12817 | 0.19684 | 61.5601 | 61.9034 | 124.4247 | 124.5987 | -0.068665 | 124.5758 | 61.8256 | -0.26093 | 124.5987 | -0.068665 | 61.8256 | 124.4247 | 124.5758 | -124.9695 | -124.9649
403.375 | 124.9878 | -61.7661 | 62.9196 | 0.10239 | 0.011521 | 0.015306 | 0.0043687 | 0.06943 | -0.0013244 | 0.070241 | -61.8256 | 62.8418 | -62.027 | -61.9171 | 62.677 | 0.050354 | -0.16479 | 0.15106 | 62.8143 | -62.0178 | -0.26093 | -0.07782 | -0.05951 | -0.15106 | -0.24262 | -0.25177 | -0.10529 | 0.20142 | 61.6013 | 61.9171 | 124.4431 | 124.6078 | -0.05951 | 124.5804 | 61.8164 | -0.25177 | 124.6078 | -0.05951 | 61.8164 | 124.4431 | 124.5804 | -124.9466 | -124.9374
404.375 | 125.0198 | -61.7752 | 62.9379 | 0.16342 | 0.014511 | 0.015306 | 0.0082139 | 0.068361 | -0.0015382 | 0.067891 | -61.8073 | 62.8601 | -62.0361 | -61.8622 | 62.6541 | 0.082397 | -0.16937 | 0.12817 | 62.8326 | -62.0087 | -0.26093 | -0.07782 | -0.032043 | -0.086975 | -0.28381 | -0.23346 | -0.10529 | 0.22888 | 61.6058 | 61.9034 | 124.4293 | 124.6353 | -0.032043 | 124.6078 | 61.8576 | -0.23346 | 124.6353 | -0.032043 | 61.8576 | 124.4293 | 124.6078 | -124.9741 | -124.9466
405.375 | 124.9878 | -61.8118 | 62.915 | 0.19394 | 0.012802 | 0.020006 | 0.0082139 | 0.070284 | -0.0019654 | 0.068746 | -61.8347 | 62.8693 | -62.0499 | -61.9171 | 62.6358 | 0.041199 | -0.17395 | 0.12817 | 62.8098 | -62.027 | -0.23804 | -0.045776 | -0.022888 | -0.10528 | -0.27924 | -0.21515 | -0.10529 | 0.21515 | 61.6379 | 61.94 | 124.4476 | 124.6811 | -0.022888 | 124.6216 | 61.853 | -0.21515 | 124.6811 | -0.022888 | 61.853 | 124.4476 | 124.6216 | -124.9649 | -124.942
406.375 | 125.0061 | -61.7889 | 62.9333 | 0.2092 | 0.014939 | 0.013597 | 0.0043687 | 0.070925 | -0.00089719 | 0.069387 | -61.8576 | 62.8601 | -62.0316 | -61.9308 | 62.6404 | 0.032043 | -0.1831 | 0.082397 | 62.8464 | -62.027 | -0.24262 | -0.073243 | -0.068665 | -0.14191 | -0.29297 | -0.23804 | -0.086975 | 0.17395 | 61.6058 | 61.8713 | 124.4293 | 124.649 | -0.068665 | 124.6353 | 61.821 | -0.23804 | 124.649 | -0.068665 | 61.821 | 124.4293 | 124.6353 | -124.9649 | -124.9603
407.375 | 124.9786 | -61.7752 | 62.9105 | 0.27023 | 0.01323 | 0.01787 | 0.0052231 | 0.07007 | -0.0017518 | 0.068746 | -61.7981 | 62.8693 | -62.0132 | -61.94 | 62.6633 | 0.050354 | -0.18768 | 0.14191 | 62.8418 | -62.0132 | -0.23804 | -0.041198 | -0.022888 | -0.16479 | -0.24719 | -0.23804 | -0.068664 | 0.21515 | 61.5875 | 61.9171 | 124.4385 | 124.6445 | -0.022888 | 124.617 | 61.8256 | -0.23804 | 124.6445 | -0.022888 | 61.8256 | 124.4385 | 124.617 | -124.9237 | -124.9237
408.375 | 125.029 | -61.7798 | 62.9059 | 0.1329 | 0.013016 | 0.014879 | 0.0035141 | 0.070498 | -0.0026062 | 0.069814 | -61.7523 | 62.8647 | -62.0544 | -61.8713 | 62.6907 | 0.041199 | -0.16937 | 0.16479 | 62.851 | -61.9995 | -0.27466 | -0.041199 | 0.027466 | -0.091553 | -0.21515 | -0.21973 | -0.054932 | 0.30212 | 61.6104 | 61.9446 | 124.4705 | 124.6445 | 0.027466 | 124.6307 | 61.821 | -0.21973 | 124.6445 | 0.027466 | 61.821 | 124.4705 | 124.6307 | -124.9603 | -124.9054
409.375 | 125.0244 | -61.7615 | 62.9333 | 0.14053 | 0.013657 | 0.016588 | 0.0071457 | 0.069002 | -0.0019654 | 0.072805 | -61.821 | 62.851 | -62.0224 | -62.0132 | 62.4435 | -0.013733 | -0.018311 | 0.14648 | 62.851 | -62.0087 | -0.26093 | -0.082398 | -0.059509 | -0.25177 | -0.48981 | -0.24719 | -0.082398 | 0.20142 | 61.7432 | 61.908 | 124.205 | 124.6124 | -0.059509 | 124.6124 | 61.7477 | -0.24719 | 124.6124 | -0.059509 | 61.7477 | 124.205 | 124.6124 | -124.9557 | -124.942
410.375 | 124.9466 | -61.8073 | 62.9379 | 0.14053 | 0.014939 | 0.019365 | 0.0088547 | 0.07007 | -0.0023926 | 0.069387 | -61.908 | 62.915 | -62.0773 | -61.9949 | 62.59 | -0.032043 | -0.054932 | 0.045776 | 62.8464 | -62.0453 | -0.27008 | -0.022888 | -0.10071 | -0.18768 | -0.3479 | -0.23804 | -0.091552 | 0.16937 | 61.7523 | 61.853 | 124.3973 | 124.7223 | -0.10071 | 124.6536 | 61.7752 | -0.23804 | 124.7223 | -0.10071 | 61.7752 | 124.3973 | 124.6536 | -125.0153 | -124.9832
411.375 | 125.0015 | -61.7706 | 62.8967 | 0.10239 | 0.013016 | 0.019792 | 0.0056503 | 0.070925 | -0.00025639 | 0.070455 | -61.8118 | 62.8372 | -62.0316 | -61.908 | 62.6724 | 0.059509 | -0.21057 | 0.14191 | 62.8372 | -62.0087 | -0.26093 | -0.05951 | -0.041199 | -0.13733 | -0.22431 | -0.23804 | -0.05951 | 0.21973 | 61.5601 | 61.9125 | 124.4431 | 124.6078 | -0.041199 | 124.6078 | 61.8301 | -0.23804 | 124.6078 | -0.041199 | 61.8301 | 124.4431 | 124.6078 | -124.9283 | -124.9054
412.375 | 125.0336 | -61.7935 | 62.915 | 0.17105 | 0.01323 | 0.012315 | 0.0075729 | 0.070498 | -0.0047424 | 0.0696 | -61.8622 | 62.8693 | -62.0499 | -61.9354 | 62.6358 | 0.027466 | -0.1236 | 0.07782 | 62.8372 | -62.0132 | -0.25635 | -0.045776 | -0.068665 | -0.14191 | -0.27924 | -0.21973 | -0.07782 | 0.18768 | 61.6699 | 61.8713 | 124.4293 | 124.6628 | -0.068665 | 124.6307 | 61.821 | -0.21973 | 124.6628 | -0.068665 | 61.821 | 124.4293 | 124.6307 | -124.9649 | -124.9283
413.375 | 124.9832 | -61.7752 | 62.915 | 0.15579 | 0.014511 | 0.016374 | 0.0073593 | 0.070925 | -0.0028198 | 0.070455 | -61.8576 | 62.8647 | -62.0453 | -61.9492 | 62.6221 | 0.027466 | -0.14191 | 0.11902 | 62.851 | -62.0041 | -0.27008 | -0.050354 | -0.082397 | -0.17395 | -0.29297 | -0.22888 | -0.064087 | 0.18768 | 61.6333 | 61.8942 | 124.3973 | 124.6399 | -0.082397 | 124.6262 | 61.8027 | -0.22888 | 124.6399 | -0.082397 | 61.8027 | 124.3973 | 124.6262 | -124.9603 | -124.9191
414.375 | 125.0015 | -61.7615 | 62.9196 | -0.65292 | 0.014511 | 0.019151 | 0.0075729 | 0.070498 | -0.00025639 | 0.06896 | -61.8347 | 62.8738 | -62.0041 | -61.9217 | 62.6587 | 0.054932 | -0.1831 | 0.16022 | 62.8281 | -62.0224 | -0.24261 | -0.045777 | -0.073242 | -0.16022 | -0.26093 | -0.26093 | -0.091553 | 0.16937 | 61.5784 | 61.9217 | 124.4202 | 124.6353 | -0.073242 | 124.5895 | 61.8164 | -0.26093 | 124.6353 | -0.073242 | 61.8164 | 124.4202 | 124.5895 | -124.9237 | -124.942
415.375 | 125.0198 | -61.7798 | 62.9288 | -1.5837 | 0.011948 | 0.01552 | 0.0050095 | 0.069643 | -0.0026062 | 0.070882 | -61.7935 | 62.8738 | -62.0132 | -61.9125 | 62.6541 | 0.059509 | -0.18768 | 0.16022 | 62.8464 | -62.0132 | -0.23346 | -0.054932 | -0.013733 | -0.13275 | -0.27466 | -0.23346 | -0.082397 | 0.21973 | 61.5921 | 61.94 | 124.4339 | 124.6536 | -0.013733 | 124.6262 | 61.8393 | -0.23346 | 124.6536 | -0.013733 | 61.8393 | 124.4339 | 124.6262 | -124.942 | -124.942
416.375 | 125.0061 | -61.7935 | 62.915 | 0.50674 | 0.014084 | 0.015947 | 0.0035141 | 0.068148 | -0.003247 | 0.070028 | -61.7844 | 62.8601 | -62.0087 | -61.908 | 62.6678 | 0.064087 | -0.17853 | 0.15564 | 62.8326 | -62.027 | -0.21515 | -0.054932 | 0.009155 | -0.11444 | -0.24719 | -0.23346 | -0.082397 | 0.2243 | 61.615 | 61.9492 | 124.4614 | 124.6536 | 0.009155 | 124.6262 | 61.8576 | -0.23346 | 124.6536 | 0.009155 | 61.8576 | 124.4614 | 124.6262 | -124.9237 | -124.942
417.375 | 125.0107 | -61.7569 | 62.9059 | -0.042572 | 0.01558 | 0.018297 | 0.0065049 | 0.07007 | -0.0051696 | 0.0696 | -61.8118 | 62.8555 | -62.0132 | -61.9263 | 62.6862 | 0.068665 | -0.20142 | 0.16479 | 62.8326 | -62.0499 | -0.25635 | -0.050354 | -0.054932 | -0.16937 | -0.21973 | -0.29297 | -0.073242 | 0.20142 | 61.5555 | 61.9217 | 124.4431 | 124.6124 | -0.054932 | 124.5895 | 61.8256 | -0.29297 | 124.6124 | -0.054932 | 61.8256 | 124.4431 | 124.5895 | -124.9191 | -124.9557
418.375 | 124.9969 | -61.7798 | 62.9242 | 0.12527 | 0.012375 | 0.018083 | 0.0050095 | 0.069216 | -0.0019654 | 0.069814 | -61.8164 | 62.8372 | -62.0361 | -61.9263 | 62.6724 | 0.073242 | -0.16937 | 0.14191 | 62.851 | -62.0224 | -0.25635 | -0.086975 | -0.036621 | -0.14649 | -0.25177 | -0.24262 | -0.073242 | 0.21973 | 61.6104 | 61.9217 | 124.4522 | 124.617 | -0.036621 | 124.6307 | 61.853 | -0.24262 | 124.617 | -0.036621 | 61.853 | 124.4522 | 124.6307 | -124.9603 | -124.9466
419.375 | 125.0336 | -61.7569 | 62.9105 | 0.026092 | 0.012375 | 0.01851 | 0.0056503 | 0.069216 | -0.003247 | 0.068746 | -61.821 | 62.8326 | -62.0132 | -61.9217 | 62.677 | 0.064087 | -0.19226 | 0.16022 | 62.8052 | -62.0178 | -0.25635 | -0.077819 | -0.064087 | -0.16479 | -0.23346 | -0.26093 | -0.10528 | 0.19226 | 61.5646 | 61.9171 | 124.4339 | 124.5895 | -0.064087 | 124.5621 | 61.821 | -0.26093 | 124.5895 | -0.064087 | 61.821 | 124.4339 | 124.5621 | -124.9237 | -124.9283
420.375 | 124.9649 | -61.7661 | 62.9333 | 0.071869 | 0.015152 | 0.015306 | 0.0054367 | 0.068575 | -0.0023926 | 0.068532 | -61.8164 | 62.8372 | -62.0087 | -61.9125 | 62.677 | 0.064087 | -0.18768 | 0.15106 | 62.851 | -62.0316 | -0.24262 | -0.096131 | -0.050354 | -0.14648 | -0.25635 | -0.2655 | -0.082398 | 0.19226 | 61.5784 | 61.9171 | 124.4431 | 124.6033 | -0.050354 | 124.617 | 61.8301 | -0.2655 | 124.6033 | -0.050354 | 61.8301 | 124.4431 | 124.617 | -124.942 | -124.9649
421.375 | 124.9969 | -61.7981 | 62.9288 | 0.11765 | 0.012375 | 0.014238 | 0.0035141 | 0.067293 | -0.0017518 | 0.06896 | -61.8439 | 62.8464 | -62.0178 | -61.94 | 62.6266 | 0.050354 | -0.15564 | 0.13733 | 62.851 | -62.0087 | -0.21973 | -0.082397 | -0.045776 | -0.14191 | -0.30212 | -0.21057 | -0.07782 | 0.17395 | 61.6425 | 61.9354 | 124.4247 | 124.6445 | -0.045776 | 124.649 | 61.8484 | -0.21057 | 124.6445 | -0.045776 | 61.8484 | 124.4247 | 124.649 | -124.9466 | -124.9374
422.375 | 124.9878 | -61.7844 | 62.9425 | 0.10239 | 0.012589 | 0.018297 | 0.0052231 | 0.067721 | -0.0015382 | 0.070669 | -61.8439 | 62.8326 | -62.0453 | -61.9537 | 62.6312 | 0.036621 | -0.13733 | 0.12817 | 62.8281 | -62.0041 | -0.26093 | -0.10986 | -0.059509 | -0.16937 | -0.31128 | -0.21973 | -0.11444 | 0.20142 | 61.647 | 61.9125 | 124.4156 | 124.617 | -0.059509 | 124.6124 | 61.821 | -0.21973 | 124.617 | -0.059509 | 61.821 | 124.4156 | 124.6124 | -124.9878 | -124.9466
423.375 | 124.9512 | -61.7752 | 62.9562 | 0.1329 | 0.013443 | 0.012956 | 0.0035141 | 0.066012 | 0.00017081 | 0.06896 | -61.8759 | 62.8326 | -62.027 | -61.9492 | 62.6129 | 0.032043 | -0.1236 | 0.11902 | 62.8464 | -62.0316 | -0.25177 | -0.1236 | -0.10071 | -0.17395 | -0.34332 | -0.25635 | -0.10986 | 0.15106 | 61.6516 | 61.8942 | 124.3881 | 124.6078 | -0.10071 | 124.6216 | 61.8073 | -0.25635 | 124.6078 | -0.10071 | 61.8073 | 124.3881 | 124.6216 | -124.9832 | -124.9878
424.375 | 124.9649 | -61.7752 | 62.9379 | 0.079498 | 0.012802 | 0.014238 | 0.0060777 | 0.066225 | -0.00068359 | 0.06896 | -61.8576 | 62.8372 | -62.0178 | -61.9629 | 62.6083 | 0.027466 | -0.11902 | 0.11444 | 62.8326 | -62.0224 | -0.24261 | -0.10071 | -0.082397 | -0.18768 | -0.32959 | -0.24719 | -0.10529 | 0.16022 | 61.6562 | 61.8896 | 124.3835 | 124.6124 | -0.082397 | 124.6078 | 61.8027 | -0.24719 | 124.6124 | -0.082397 | 61.8027 | 124.3835 | 124.6078 | -124.9557 | -124.9603
425.375 | 124.9741 | -61.7935 | 62.9608 | 0.15579 | 0.011093 | 0.01317 | 0.0024461 | 0.066225 | -0.00025639 | 0.0696 | -61.8988 | 62.8281 | -62.0316 | -61.9492 | 62.6678 | 0.050354 | -0.07782 | 0.14648 | 62.8647 | -61.9949 | -0.23804 | -0.13275 | -0.10529 | -0.15564 | -0.29297 | -0.20142 | -0.09613 | 0.13275 | 61.7157 | 61.94 | 124.4614 | 124.6216 | -0.10529 | 124.6582 | 61.8439 | -0.20142 | 124.6216 | -0.10529 | 61.8439 | 124.4614 | 124.6582 | -124.9924 | -124.9557
426.375 | 124.9832 | -61.7844 | 62.9608 | 0.064239 | 0.012375 | 0.013383 | 0.0035141 | 0.066866 | -0.0026062 | 0.068105 | -61.8713 | 62.8052 | -62.0132 | -61.9675 | 62.6221 | 0.018311 | -0.091553 | 0.11444 | 62.8326 | -62.027 | -0.22888 | -0.15564 | -0.086975 | -0.1831 | -0.33874 | -0.24262 | -0.12817 | 0.14191 | 61.6928 | 61.8988 | 124.4064 | 124.5895 | -0.086975 | 124.617 | 61.8027 | -0.24262 | 124.5895 | -0.086975 | 61.8027 | 124.4064 | 124.617 | -124.9741 | -124.9878
427.375 | 124.9649 | -61.7844 | 62.9517 | 0.079498 | 0.013871 | 0.017442 | 0.0039413 | 0.066225 | -0.0028198 | 0.071523 | -61.8851 | 62.8098 | -62.027 | -61.972 | 62.6266 | 0.027466 | -0.10071 | 0.1236 | 62.851 | -62.0132 | -0.24262 | -0.14191 | -0.10071 | -0.18768 | -0.32501 | -0.22888 | -0.10071 | 0.14191 | 61.6837 | 61.908 | 124.411 | 124.5941 | -0.10071 | 124.6353 | 61.8118 | -0.22888 | 124.5941 | -0.10071 | 61.8118 | 124.411 | 124.6353 | -124.9786 | -124.9649
428.375 | 124.9695 | -61.7935 | 62.9562 | -0.0044251 | 0.010453 | 0.008043 | 0.0054367 | 0.066225 | -0.002179 | 0.068105 | -61.8805 | 62.8281 | -62.0132 | -61.9492 | 62.6404 | 0.050354 | -0.064087 | 0.16479 | 62.8464 | -62.0041 | -0.21973 | -0.12817 | -0.086975 | -0.15564 | -0.31586 | -0.21057 | -0.10986 | 0.13275 | 61.7294 | 61.9583 | 124.4339 | 124.6216 | -0.086975 | 124.6399 | 61.8439 | -0.21057 | 124.6216 | -0.086975 | 61.8439 | 124.4339 | 124.6399 | -124.9695 | -124.9603
429.375 | 124.9603 | -61.7844 | 62.9562 | -0.019684 | 0.0093844 | 0.013597 | 0.0030869 | 0.065798 | -0.0026062 | 0.070455 | -61.8851 | 62.8372 | -62.0316 | -61.94 | 62.6404 | 0.041199 | -0.059509 | 0.16022 | 62.8372 | -62.0041 | -0.24719 | -0.11902 | -0.10071 | -0.15564 | -0.31586 | -0.21973 | -0.11902 | 0.14648 | 61.7249 | 61.9446 | 124.4247 | 124.6216 | -0.10071 | 124.6216 | 61.8256 | -0.21973 | 124.6216 | -0.10071 | 61.8256 | 124.4247 | 124.6216 | -124.9878 | -124.9603
430.375 | 124.9969 | -61.7752 | 62.9517 | 0.033722 | 0.012162 | 0.014238 | 0.0026597 | 0.066225 | -0.0011108 | 0.0696 | -61.8759 | 62.8326 | -62.0407 | -61.9308 | 62.6404 | 0.050354 | -0.07782 | 0.16479 | 62.8464 | -62.0132 | -0.2655 | -0.11902 | -0.10071 | -0.15564 | -0.31128 | -0.23804 | -0.10528 | 0.16479 | 61.6974 | 61.94 | 124.4156 | 124.6078 | -0.10071 | 124.6216 | 61.8256 | -0.23804 | 124.6078 | -0.10071 | 61.8256 | 124.4156 | 124.6216 | -124.9924 | -124.9649
431.375 | 125.0198 | -61.7477 | 62.9471 | -0.050202 | 0.011521 | 0.016374 | 0.0037277 | 0.066652 | -0.0017518 | 0.06896 | -61.8301 | 62.8189 | -62.0041 | -61.8805 | 62.6862 | 0.11902 | -0.07782 | 0.2243 | 62.8464 | -62.0132 | -0.25635 | -0.12817 | -0.082397 | -0.13275 | -0.26093 | -0.2655 | -0.10071 | 0.17395 | 61.6699 | 61.972 | 124.4339 | 124.5667 | -0.082397 | 124.5941 | 61.8668 | -0.2655 | 124.5667 | -0.082397 | 61.8668 | 124.4339 | 124.5941 | -124.9512 | -124.9603
432.375 | 124.9924 | -61.7661 | 62.9608 | -0.095978 | 0.014511 | 0.0099656 | 0.0018051 | 0.067721 | 0.00017081 | 0.070241 | -61.821 | 62.8281 | -61.9949 | -61.8759 | 62.6907 | 0.1236 | -0.068665 | 0.24261 | 62.851 | -61.9904 | -0.22888 | -0.13275 | -0.054932 | -0.10986 | -0.27008 | -0.2243 | -0.10986 | 0.17395 | 61.6974 | 62.0087 | 124.4568 | 124.5941 | -0.054932 | 124.617 | 61.8896 | -0.2243 | 124.5941 | -0.054932 | 61.8896 | 124.4568 | 124.617 | -124.9557 | -124.9512
433.375 | 124.9695 | -61.7752 | 62.9425 | 0.010834 | 0.012589 | 0.011675 | 0.0028733 | 0.064944 | -4.2788e-05 | 0.06661 | -61.8713 | 62.8189 | -62.0041 | -61.9217 | 62.645 | 0.054932 | -0.064087 | 0.16022 | 62.8098 | -61.9995 | -0.22888 | -0.1236 | -0.09613 | -0.14648 | -0.29755 | -0.2243 | -0.13275 | 0.13275 | 61.7111 | 61.9354 | 124.4202 | 124.5941 | -0.09613 | 124.585 | 61.8301 | -0.2243 | 124.5941 | -0.09613 | 61.8301 | 124.4202 | 124.585 | -124.9466 | -124.942
434.375 | 124.9832 | -61.7477 | 62.9562 | -0.019684 | 0.012802 | 0.012956 | 0.0022323 | 0.066225 | -0.0011108 | 0.069814 | -61.8576 | 62.8464 | -62.0132 | -61.9263 | 62.6678 | 0.07782 | -0.068665 | 0.17853 | 62.8464 | -62.0224 | -0.2655 | -0.10986 | -0.10986 | -0.17853 | -0.28839 | -0.27466 | -0.10986 | 0.15564 | 61.6791 | 61.9263 | 124.4156 | 124.5941 | -0.10986 | 124.5941 | 61.8256 | -0.27466 | 124.5941 | -0.10986 | 61.8256 | 124.4156 | 124.5941 | -124.9695 | -124.9786
435.375 | 124.9969 | -61.7432 | 62.9608 | -0.13412 | 0.011307 | 0.011034 | 0.0018051 | 0.064944 | -0.00046999 | 0.067037 | -61.8256 | 62.8326 | -62.0041 | -61.8668 | 62.7136 | 0.14191 | -0.091553 | 0.25177 | 62.851 | -61.9812 | -0.26093 | -0.12817 | -0.082398 | -0.1236 | -0.24719 | -0.23804 | -0.10986 | 0.17853 | 61.6516 | 61.9949 | 124.4568 | 124.5758 | -0.082398 | 124.5941 | 61.8851 | -0.23804 | 124.5758 | -0.082398 | 61.8851 | 124.4568 | 124.5941 | -124.9649 | -124.942
436.375 | 125.029 | -61.734 | 62.97 | -0.14175 | 0.012802 | 0.014024 | 0.0035141 | 0.066012 | -0.00025639 | 0.067464 | -61.8118 | 62.8326 | -62.0041 | -61.8622 | 62.7136 | 0.16022 | -0.09613 | 0.2655 | 62.8098 | -61.9675 | -0.27008 | -0.13733 | -0.07782 | -0.12817 | -0.25635 | -0.23346 | -0.16022 | 0.19226 | 61.6379 | 61.9995 | 124.4476 | 124.5667 | -0.07782 | 124.5438 | 61.8942 | -0.23346 | 124.5667 | -0.07782 | 61.8942 | 124.4476 | 124.5438 | -124.9741 | -124.9374
437.375 | 125.0565 | -61.7294 | 62.9654 | -0.1265 | 0.011521 | 0.014879 | 0.0020187 | 0.065157 | -0.0015382 | 0.067464 | -61.8164 | 62.8143 | -62.0178 | -61.8393 | 62.7045 | 0.14648 | -0.086975 | 0.27466 | 62.8601 | -61.9492 | -0.28839 | -0.15106 | -0.086975 | -0.10986 | -0.26093 | -0.21973 | -0.10529 | 0.20142 | 61.6425 | 62.0041 | 124.4339 | 124.5438 | -0.086975 | 124.5895 | 61.8759 | -0.21973 | 124.5438 | -0.086975 | 61.8759 | 124.4339 | 124.5895 | -124.9832 | -124.9146
438.375 | 125.116 | -61.7386 | 63.0249 | -0.15701 | 0.010025 | 0.015947 | 0.0026597 | 0.066012 | -0.00046999 | 0.067464 | -61.8256 | 62.8555 | -61.9995 | -61.8301 | 62.7228 | 0.15564 | -0.09613 | 0.28381 | 62.8281 | -61.9629 | -0.26093 | -0.16937 | -0.086976 | -0.091553 | -0.30212 | -0.22431 | -0.19684 | 0.17395 | 61.6425 | 62.0224 | 124.4614 | 124.5941 | -0.086976 | 124.5666 | 61.8942 | -0.22431 | 124.5941 | -0.086976 | 61.8942 | 124.4614 | 124.5666 | -125.0244 | -124.9878
439.375 | 124.9969 | -61.7523 | 62.9654 | -0.2562 | 0.010666 | 0.0071884 | 0.0037277 | 0.066439 | -0.0011108 | 0.069387 | -61.7935 | 62.8372 | -61.9949 | -61.853 | 62.7274 | 0.13733 | -0.045776 | 0.2655 | 62.8601 | -61.9629 | -0.24262 | -0.12817 | -0.041199 | -0.10071 | -0.23804 | -0.21057 | -0.10529 | 0.20142 | 61.7065 | 62.0178 | 124.4797 | 124.5895 | -0.041199 | 124.6124 | 61.8896 | -0.21057 | 124.5895 | -0.041199 | 61.8896 | 124.4797 | 124.6124 | -124.9603 | -124.9283
440.375 | 124.9786 | -61.7615 | 62.9379 | -0.13412 | 0.0095982 | 0.016801 | 0.0039413 | 0.068148 | -0.0023926 | 0.067464 | -61.7935 | 62.8235 | -62.0041 | -61.9492 | 63.0112 | 0.45776 | -0.3067 | 0.054932 | 62.8738 | -61.9904 | -0.24261 | -0.11444 | -0.032043 | -0.18768 | 0.073242 | -0.22888 | -0.064087 | 0.21057 | 61.4548 | 61.8164 | 124.7726 | 124.585 | -0.032043 | 124.6353 | 62.2192 | -0.22888 | 124.585 | -0.032043 | 62.2192 | 124.7726 | 124.6353 | -124.942 | -124.9283
441.375 | 125.0153 | -61.7889 | 62.9608 | -0.14938 | 0.011948 | 0.016588 | 0.0013779 | 0.065584 | -0.0047424 | 0.068105 | -61.7889 | 62.8281 | -61.9949 | -61.821 | 62.3932 | 0.013733 | -0.082397 | 0.13275 | 62.851 | -61.9675 | -0.20599 | -0.13275 | 0 | -0.032044 | -0.56763 | -0.17853 | -0.10986 | 0.20599 | 61.7065 | 61.9217 | 124.1821 | 124.617 | 0 | 124.6399 | 61.8027 | -0.17853 | 124.617 | 0 | 61.8027 | 124.1821 | 124.6399 | -124.9557 | -124.9283
442.375 | 125.0015 | -61.7569 | 62.9745 | -0.24094 | 0.011521 | 0.010179 | 0.0043687 | 0.06708 | -0.0019654 | 0.068746 | -61.8073 | 62.8418 | -62.0224 | -61.8622 | 62.6953 | 0.15106 | -0.018311 | 0.27008 | 62.8555 | -61.972 | -0.2655 | -0.13275 | -0.050354 | -0.10529 | -0.27924 | -0.21515 | -0.11902 | 0.21515 | 61.7386 | 62.027 | 124.4522 | 124.5987 | -0.050354 | 124.6124 | 61.908 | -0.21515 | 124.5987 | -0.050354 | 61.908 | 124.4522 | 124.6124 | -124.9969 | -124.9466
443.375 | 125.0061 | -61.7615 | 62.9745 | -0.24094 | 0.010453 | 0.013383 | 0.0037277 | 0.068789 | -0.0017518 | 0.068105 | -61.8073 | 62.8464 | -62.0178 | -61.853 | 62.7045 | 0.15106 | -0.013733 | 0.25177 | 62.8693 | -61.972 | -0.25635 | -0.12817 | -0.045776 | -0.091552 | -0.27008 | -0.21057 | -0.10529 | 0.21057 | 61.7477 | 62.0132 | 124.4659 | 124.6078 | -0.045776 | 124.6307 | 61.9125 | -0.21057 | 124.6078 | -0.045776 | 61.9125 | 124.4659 | 124.6307 | -124.9924 | -124.9466
444.375 | 124.9557 | -61.7615 | 62.9929 | -0.21042 | 0.012375 | 0.015306 | 0.0060777 | 0.066012 | -0.0013244 | 0.066823 | -61.7981 | 62.8693 | -61.9995 | -61.853 | 62.7136 | 0.15106 | -0.018311 | 0.25177 | 62.8738 | -61.9858 | -0.23804 | -0.1236 | -0.036621 | -0.091552 | -0.27924 | -0.2243 | -0.11902 | 0.20142 | 61.7432 | 62.0132 | 124.4751 | 124.6307 | -0.036621 | 124.6353 | 61.9125 | -0.2243 | 124.6307 | -0.036621 | 61.9125 | 124.4751 | 124.6353 | -124.9924 | -124.9786
445.375 | 124.9603 | -61.7615 | 62.9654 | -0.21042 | 0.014511 | 0.011888 | 0.0037277 | 0.066866 | -0.0026062 | 0.068105 | -61.8073 | 62.8601 | -62.0087 | -61.8622 | 62.6999 | 0.14648 | 0 | 0.24719 | 62.8647 | -61.9583 | -0.24719 | -0.10529 | -0.045776 | -0.10071 | -0.2655 | -0.19684 | -0.10071 | 0.20142 | 61.7615 | 62.0087 | 124.4614 | 124.6216 | -0.045776 | 124.6262 | 61.908 | -0.19684 | 124.6216 | -0.045776 | 61.908 | 124.4614 | 124.6262 | -124.9741 | -124.9237
446.375 | 124.8871 | -61.7935 | 62.9929 | -0.22568 | 0.012375 | 0.014452 | 0.0039413 | 0.06708 | -0.003247 | 0.068319 | -61.8484 | 62.8876 | -62.0316 | -61.94 | 62.6266 | 0.064087 | 0.11902 | 0.16937 | 62.883 | -61.9949 | -0.23804 | -0.10529 | -0.054932 | -0.14648 | -0.36621 | -0.20142 | -0.10986 | 0.1831 | 61.9125 | 61.9629 | 124.4202 | 124.6811 | -0.054932 | 124.6765 | 61.8576 | -0.20142 | 124.6811 | -0.054932 | 61.8576 | 124.4202 | 124.6765 | -125.0244 | -124.9878
447.375 | 124.9466 | -61.7661 | 63.0066 | -0.24094 | 0.011307 | 0.014024 | 0.0030869 | 0.06708 | -0.0017518 | 0.068746 | -61.8073 | 62.8372 | -61.9858 | -61.8713 | 62.7045 | 0.16022 | 0.013733 | 0.25635 | 62.8738 | -61.9537 | -0.21973 | -0.16937 | -0.041199 | -0.10529 | -0.30212 | -0.18768 | -0.13275 | 0.17853 | 61.7798 | 62.0224 | 124.4705 | 124.6033 | -0.041199 | 124.6399 | 61.9263 | -0.18768 | 124.6033 | -0.041199 | 61.9263 | 124.4705 | 124.6399 | -124.9924 | -124.9603
448.375 | 125.0427 | -61.7935 | 63.0341 | -0.27145 | 0.012375 | 0.010179 | 0.0069321 | 0.065584 | -0.00025639 | 0.068532 | -61.8622 | 62.8876 | -62.0224 | -61.9629 | 62.6129 | 0.073242 | 0.12817 | 0.15564 | 62.9196 | -61.9995 | -0.22888 | -0.14648 | -0.068665 | -0.16937 | -0.42114 | -0.20599 | -0.11444 | 0.16022 | 61.9217 | 61.9492 | 124.4064 | 124.6811 | -0.068665 | 124.7131 | 61.8668 | -0.20599 | 124.6811 | -0.068665 | 61.8668 | 124.4064 | 124.7131 | -125.0565 | -125.0336
449.375 | 125.0565 | -61.7752 | 63.0295 | -0.32486 | 0.011734 | 0.0095382 | 0.0045823 | 0.069002 | -0.0030334 | 0.069173 | -61.8668 | 62.9059 | -62.0224 | -61.9537 | 62.6358 | 0.082397 | 0.13275 | 0.17395 | 62.9333 | -61.9995 | -0.24719 | -0.1236 | -0.091552 | -0.17853 | -0.39368 | -0.2243 | -0.09613 | 0.15564 | 61.908 | 61.9492 | 124.411 | 124.6811 | -0.091552 | 124.7086 | 61.8576 | -0.2243 | 124.6811 | -0.091552 | 61.8576 | 124.411 | 124.7086 | -125.0519 | -125.029
450.375 | 124.9374 | -61.7615 | 63.0569 | -0.24857 | 0.012375 | 0.011888 | 0.0045823 | 0.067293 | -0.002179 | 0.070028 | -61.8576 | 62.8967 | -62.0178 | -61.9629 | 62.645 | 0.073242 | 0.13275 | 0.16022 | 62.9059 | -62.0132 | -0.25635 | -0.16022 | -0.09613 | -0.20142 | -0.41199 | -0.25177 | -0.15106 | 0.16022 | 61.8942 | 61.9217 | 124.4064 | 124.6582 | -0.09613 | 124.6674 | 61.8347 | -0.25177 | 124.6582 | -0.09613 | 61.8347 | 124.4064 | 124.6674 | -125.0748 | -125.0702
451.375 | 124.9146 | -61.7706 | 63.0478 | -0.31723 | 0.012162 | 0.017656 | 0.0056503 | 0.068361 | -0.00046999 | 0.068746 | -61.8576 | 62.8922 | -61.9904 | -61.9537 | 62.6358 | 0.064087 | 0.1236 | 0.14191 | 62.9196 | -61.9995 | -0.21973 | -0.15564 | -0.086975 | -0.18311 | -0.41199 | -0.22888 | -0.12817 | 0.13275 | 61.8942 | 61.9125 | 124.4064 | 124.6628 | -0.086975 | 124.6902 | 61.8347 | -0.22888 | 124.6628 | -0.086975 | 61.8347 | 124.4064 | 124.6902 | -125.0381 | -125.0473
452.375 | 124.9603 | -61.7798 | 63.0203 | -0.29434 | 0.013016 | 0.012956 | 0.0065049 | 0.068361 | -0.00068359 | 0.069387 | -61.8622 | 62.9013 | -62.0087 | -61.9629 | 62.6358 | 0.07782 | 0.12817 | 0.17395 | 62.9242 | -62.0224 | -0.22888 | -0.11902 | -0.082398 | -0.18311 | -0.38452 | -0.24262 | -0.096131 | 0.14648 | 61.908 | 61.9537 | 124.4156 | 124.6811 | -0.082398 | 124.704 | 61.8576 | -0.24262 | 124.6811 | -0.082398 | 61.8576 | 124.4156 | 124.704 | -125.029 | -125.0427
453.375 | 124.9191 | -61.8027 | 63.0478 | -0.26382 | 0.013016 | 0.011675 | 0.0060777 | 0.066225 | -0.0028198 | 0.067037 | -61.8622 | 62.9013 | -62.0041 | -61.9492 | 62.6312 | 0.07782 | 0.12817 | 0.17395 | 62.9105 | -61.9995 | -0.20142 | -0.14648 | -0.05951 | -0.14648 | -0.41656 | -0.19684 | -0.13733 | 0.14191 | 61.9308 | 61.9766 | 124.4339 | 124.704 | -0.05951 | 124.7131 | 61.8805 | -0.19684 | 124.704 | -0.05951 | 61.8805 | 124.4339 | 124.7131 | -125.0519 | -125.0473
454.375 | 124.8688 | -61.8118 | 63.0157 | -0.32486 | 0.01323 | 0.010393 | 0.0039413 | 0.067293 | -0.0026062 | 0.067251 | -61.8713 | 62.9288 | -61.9858 | -61.9125 | 62.677 | 0.10529 | 0.10529 | 0.18768 | 62.9379 | -62.0132 | -0.17395 | -0.086975 | -0.059509 | -0.10071 | -0.33874 | -0.20142 | -0.07782 | 0.11444 | 61.9171 | 61.9995 | 124.4888 | 124.7406 | -0.059509 | 124.7498 | 61.9171 | -0.20142 | 124.7406 | -0.059509 | 61.9171 | 124.4888 | 124.7498 | -125.0015 | -125.029
455.375 | 124.8779 | -61.8118 | 62.9883 | -0.21042 | 0.01323 | 0.013597 | 0.0052231 | 0.069216 | -0.0041016 | 0.068746 | -61.8851 | 62.9471 | -62.0361 | -61.9675 | 62.6083 | 0.068665 | 0.14648 | 0.15106 | 62.9242 | -62.0132 | -0.2243 | -0.041198 | -0.073242 | -0.15564 | -0.37994 | -0.20142 | -0.064087 | 0.15106 | 61.9583 | 61.9629 | 124.4202 | 124.7589 | -0.073242 | 124.736 | 61.8805 | -0.20142 | 124.7589 | -0.073242 | 61.8805 | 124.4202 | 124.736 | -125.0244 | -125.0015
456.375 | 124.8779 | -61.7889 | 63.0066 | -0.39352 | 0.013657 | 0.017229 | 0.0080003 | 0.068148 | -0.00025639 | 0.068319 | -61.8713 | 62.9288 | -62.0316 | -61.9858 | 62.6221 | 0.059509 | 0.14191 | 0.16022 | 62.9333 | -62.0178 | -0.24262 | -0.07782 | -0.082398 | -0.19684 | -0.38452 | -0.22888 | -0.073242 | 0.16022 | 61.9308 | 61.9492 | 124.411 | 124.7177 | -0.082398 | 124.7223 | 61.8484 | -0.22888 | 124.7177 | -0.082398 | 61.8484 | 124.411 | 124.7223 | -125.0381 | -125.0244
457.375 | 124.8734 | -61.7981 | 62.9929 | -0.36301 | 0.013657 | 0.013383 | 0.0084275 | 0.068789 | -0.0019654 | 0.067251 | -61.8988 | 62.9196 | -62.0407 | -61.9858 | 62.6083 | 0.064087 | 0.14648 | 0.15564 | 62.9517 | -62.0224 | -0.24261 | -0.073242 | -0.10071 | -0.18768 | -0.38452 | -0.2243 | -0.041199 | 0.14191 | 61.9446 | 61.9537 | 124.4064 | 124.7177 | -0.10071 | 124.7498 | 61.8622 | -0.2243 | 124.7177 | -0.10071 | 61.8622 | 124.4064 | 124.7498 | -125.0336 | -125.0153
458.375 | 124.8917 | -61.7935 | 62.9929 | -0.57663 | 0.01323 | 0.012956 | 0.0058639 | 0.070284 | -0.0013244 | 0.068105 | -61.9171 | 62.9013 | -62.027 | -61.972 | 62.6083 | 0.064087 | 0.13733 | 0.15106 | 62.915 | -62.0132 | -0.23346 | -0.091553 | -0.1236 | -0.17853 | -0.38452 | -0.21973 | -0.07782 | 0.10986 | 61.9308 | 61.9446 | 124.4019 | 124.6948 | -0.1236 | 124.7086 | 61.8576 | -0.21973 | 124.6948 | -0.1236 | 61.8576 | 124.4019 | 124.7086 | -125.0198 | -125.0061
459.375 | 124.8642 | -61.8027 | 62.9974 | -0.24857 | 0.01323 | 0.014452 | 0.0090683 | 0.069857 | -0.00068359 | 0.068746 | -61.8576 | 62.9562 | -62.0453 | -61.9583 | 62.6221 | 0.064087 | 0.13275 | 0.14191 | 62.9333 | -62.027 | -0.24262 | -0.041199 | -0.054932 | -0.15564 | -0.37537 | -0.22431 | -0.064087 | 0.18768 | 61.9354 | 61.9446 | 124.4247 | 124.7589 | -0.054932 | 124.736 | 61.8668 | -0.22431 | 124.7589 | -0.054932 | 61.8668 | 124.4247 | 124.736 | -125.0427 | -125.0244
460.375 | 124.8917 | -61.7935 | 63.002 | -0.22568 | 0.014511 | 0.012529 | 0.0056503 | 0.070711 | -0.0015382 | 0.068319 | -61.8622 | 62.9333 | -62.0499 | -61.9583 | 62.6038 | 0.059509 | 0.13733 | 0.15564 | 62.9196 | -62.0316 | -0.25635 | -0.068664 | -0.068665 | -0.16479 | -0.39825 | -0.23804 | -0.082397 | 0.18768 | 61.9308 | 61.9492 | 124.3973 | 124.7269 | -0.068665 | 124.7131 | 61.853 | -0.23804 | 124.7269 | -0.068665 | 61.853 | 124.3973 | 124.7131 | -125.0519 | -125.0336
461.375 | 124.9054 | -61.8073 | 62.9791 | -0.22568 | 0.012589 | 0.017442 | 0.0033005 | 0.069643 | -0.0017518 | 0.069387 | -61.8713 | 62.915 | -62.027 | -61.972 | 62.7182 | 0.28381 | 0.004578 | 0.018311 | 62.915 | -62.027 | -0.21973 | -0.064087 | -0.064087 | -0.16479 | -0.26093 | -0.21973 | -0.064087 | 0.15564 | 61.8118 | 61.8256 | 124.5255 | 124.7223 | -0.064087 | 124.7223 | 62.0911 | -0.21973 | 124.7223 | -0.064087 | 62.0911 | 124.5255 | 124.7223 | -125.0061 | -125.0061
462.375 | 124.8505 | -61.7981 | 63.0066 | -0.27145 | 0.012802 | 0.011675 | 0.0039413 | 0.068361 | -0.0015382 | 0.068105 | -61.8759 | 62.9517 | -62.0316 | -61.9812 | 62.6129 | 0.068665 | 0.15106 | 0.15564 | 62.9059 | -62.0361 | -0.23346 | -0.054932 | -0.07782 | -0.1831 | -0.39368 | -0.23804 | -0.10071 | 0.15564 | 61.9492 | 61.9537 | 124.411 | 124.7498 | -0.07782 | 124.704 | 61.8668 | -0.23804 | 124.7498 | -0.07782 | 61.8668 | 124.411 | 124.704 | -125.0381 | -125.0427
463.375 | 124.8642 | -61.7889 | 62.9974 | -0.14175 | 0.014298 | 0.011888 | 0.0050095 | 0.069002 | -0.0045288 | 0.069173 | -61.8576 | 62.9242 | -62.0361 | -61.9812 | 62.6129 | 0.07782 | 0.14648 | 0.14191 | 62.9242 | -62.027 | -0.24719 | -0.073243 | -0.068665 | -0.19226 | -0.38452 | -0.23804 | -0.073243 | 0.17853 | 61.9354 | 61.9308 | 124.4019 | 124.7131 | -0.068665 | 124.7131 | 61.8668 | -0.23804 | 124.7131 | -0.068665 | 61.8668 | 124.4019 | 124.7131 | -125.0336 | -125.0244
464.375 | 124.9283 | -61.8027 | 62.9883 | -0.21805 | 0.014084 | 0.010606 | 0.0041549 | 0.070284 | -0.0041016 | 0.067251 | -61.8622 | 62.9562 | -62.027 | -61.9675 | 62.6129 | 0.064087 | 0.13275 | 0.14648 | 62.9105 | -62.0132 | -0.22431 | -0.032043 | -0.05951 | -0.16479 | -0.37537 | -0.21057 | -0.07782 | 0.16479 | 61.9354 | 61.9492 | 124.4156 | 124.7589 | -0.05951 | 124.7131 | 61.8668 | -0.21057 | 124.7589 | -0.05951 | 61.8668 | 124.4156 | 124.7131 | -125.0153 | -125.0015
465.375 | 124.8825 | -61.7935 | 62.9974 | -0.22568 | 0.011948 | 0.011247 | 0.0058639 | 0.070711 | -0.002179 | 0.069173 | -61.8713 | 62.9379 | -62.0132 | -62.0224 | 62.6221 | 0.10529 | 0.10529 | 0.17395 | 62.9379 | -62.0224 | -0.21973 | -0.05951 | -0.07782 | -0.22888 | -0.37537 | -0.22888 | -0.05951 | 0.14191 | 61.8988 | 61.9675 | 124.4156 | 124.7314 | -0.07782 | 124.7314 | 61.8988 | -0.22888 | 124.7314 | -0.07782 | 61.8988 | 124.4156 | 124.7314 | -125.0107 | -125.0198
466.375 | 124.855 | -61.7981 | 63.0112 | -0.35538 | 0.013871 | 0.011034 | 0.0035141 | 0.069002 | -0.0036744 | 0.071096 | -61.8622 | 62.9105 | -62.0178 | -61.7752 | 62.6541 | -0.041199 | 0.10529 | 0.16937 | 62.9333 | -62.0316 | -0.21973 | -0.10071 | -0.064087 | 0.022888 | -0.35706 | -0.23346 | -0.077819 | 0.15564 | 61.9034 | 61.9675 | 124.4522 | 124.7086 | -0.064087 | 124.7314 | 61.7569 | -0.23346 | 124.7086 | -0.064087 | 61.7569 | 124.4522 | 124.7314 | -125.029 | -125.0427
467.375 | 124.8962 | -61.7752 | 63.0066 | -0.22568 | 0.011521 | 0.013811 | 0.0054367 | 0.071566 | -0.0043152 | 0.070882 | -61.8622 | 62.9196 | -62.0041 | -61.9492 | 62.6083 | 0.073242 | 0.13733 | 0.16937 | 62.9517 | -62.0361 | -0.22888 | -0.086975 | -0.086975 | -0.17395 | -0.39825 | -0.26093 | -0.054932 | 0.14191 | 61.9125 | 61.9446 | 124.3835 | 124.6948 | -0.086975 | 124.7269 | 61.8484 | -0.26093 | 124.6948 | -0.086975 | 61.8484 | 124.3835 | 124.7269 | -125.0107 | -125.0427
468.375 | 124.8871 | -61.7844 | 62.9929 | -0.28671 | 0.013016 | 0.014452 | 0.0041549 | 0.069643 | -0.0015382 | 0.06896 | -61.853 | 62.8922 | -61.9995 | -61.9583 | 62.6404 | 0.10529 | 0.13275 | 0.16937 | 62.9242 | -61.9904 | -0.21515 | -0.10071 | -0.068664 | -0.17395 | -0.35248 | -0.20599 | -0.068665 | 0.14649 | 61.9171 | 61.9537 | 124.4247 | 124.6765 | -0.068664 | 124.7086 | 61.8896 | -0.20599 | 124.6765 | -0.068664 | 61.8896 | 124.4247 | 124.7086 | -124.9924 | -124.9832
469.375 | 124.9008 | -61.7935 | 63.0112 | 0.026092 | 0.012375 | 0.008043 | 0.0062913 | 0.069643 | -4.2788e-05 | 0.06896 | -61.8622 | 62.9242 | -62.0407 | -61.972 | 62.5992 | 0.068665 | 0.14648 | 0.16479 | 62.915 | -62.027 | -0.24719 | -0.086975 | -0.068665 | -0.17853 | -0.41199 | -0.23346 | -0.09613 | 0.17853 | 61.94 | 61.9583 | 124.3927 | 124.7177 | -0.068665 | 124.7086 | 61.8622 | -0.23346 | 124.7177 | -0.068665 | 61.8622 | 124.3927 | 124.7086 | -125.0519 | -125.0381
470.375 | 124.9054 | -61.7889 | 63.0066 | -0.1799 | 0.010453 | 0.011034 | 0.0054367 | 0.068361 | -0.0017518 | 0.068319 | -61.7065 | 62.9471 | -62.027 | -61.9583 | 62.6038 | 0.045776 | 0.16479 | 0.16479 | 62.9471 | -62.0316 | -0.23804 | -0.059509 | 0.082397 | -0.16937 | -0.40283 | -0.24262 | -0.059509 | 0.32043 | 61.9537 | 61.9537 | 124.3927 | 124.736 | 0.082397 | 124.736 | 61.8347 | -0.24262 | 124.736 | 0.082397 | 61.8347 | 124.3927 | 124.736 | -125.0336 | -125.0381
471.375 | 124.8413 | -61.8027 | 62.9883 | -0.46982 | 0.014084 | 0.015733 | 0.0045823 | 0.069002 | -0.0023926 | 0.066182 | -61.8805 | 62.9288 | -62.0316 | -61.821 | 62.7594 | 0.045776 | 0.064087 | 0.16937 | 62.9288 | -62.0316 | -0.22888 | -0.059509 | -0.07782 | -0.018311 | -0.22888 | -0.22888 | -0.059509 | 0.15106 | 61.8668 | 61.972 | 124.5621 | 124.7314 | -0.07782 | 124.7314 | 61.8484 | -0.22888 | 124.7314 | -0.07782 | 61.8484 | 124.5621 | 124.7314 | -125.0198 | -125.0198
472.375 | 124.8825 | -61.7569 | 63.0478 | -0.3096 | 0.011093 | 0.012956 | 0.0018051 | 0.069002 | -0.0026062 | 0.066823 | -61.8576 | 62.915 | -62.0178 | -61.9812 | 62.6083 | 0.07782 | 0.13275 | 0.17395 | 62.9333 | -62.0132 | -0.26093 | -0.13275 | -0.10071 | -0.2243 | -0.43945 | -0.25635 | -0.11444 | 0.16022 | 61.8896 | 61.9308 | 124.3652 | 124.6719 | -0.10071 | 124.6902 | 61.8347 | -0.25635 | 124.6719 | -0.10071 | 61.8347 | 124.3652 | 124.6902 | -125.0656 | -125.061
473.375 | 124.8962 | -61.7615 | 63.0157 | -0.36301 | 0.011948 | 0.018938 | 0.0047959 | 0.069643 | -0.0026062 | 0.070669 | -61.8393 | 62.8922 | -62.0087 | -61.9446 | 62.6221 | 0.091553 | 0.068665 | 0.19684 | 62.9196 | -61.9949 | -0.24719 | -0.1236 | -0.077819 | -0.18311 | -0.39368 | -0.23346 | -0.09613 | 0.16937 | 61.8301 | 61.9583 | 124.3835 | 124.6536 | -0.077819 | 124.6811 | 61.853 | -0.23346 | 124.6536 | -0.077819 | 61.853 | 124.3835 | 124.6811 | -125.0244 | -125.0107
474.375 | 124.8596 | -61.7981 | 63.0295 | -0.67581 | 0.01558 | 0.014879 | 0.0077865 | 0.068361 | -0.0019654 | 0.06896 | -61.9125 | 62.915 | -62.0407 | -61.9583 | 62.6038 | 0.050354 | 0.1236 | 0.16479 | 62.9288 | -62.0361 | -0.24261 | -0.11444 | -0.11444 | -0.16022 | -0.42572 | -0.23804 | -0.10071 | 0.12817 | 61.9217 | 61.9629 | 124.4019 | 124.7131 | -0.11444 | 124.7269 | 61.8484 | -0.23804 | 124.7131 | -0.11444 | 61.8484 | 124.4019 | 124.7269 | -125.0702 | -125.0656
475.375 | 124.9191 | -61.7569 | 62.9837 | -0.24094 | 0.012589 | 0.013383 | 0.0033005 | 0.066866 | -0.00046999 | 0.068319 | -61.821 | 62.8693 | -62.0087 | -61.9125 | 62.6678 | 0.14191 | 0.059509 | 0.23804 | 62.9105 | -61.9949 | -0.25177 | -0.11444 | -0.064087 | -0.15564 | -0.31586 | -0.23804 | -0.073243 | 0.18768 | 61.8164 | 61.9949 | 124.4247 | 124.6262 | -0.064087 | 124.6674 | 61.8988 | -0.23804 | 124.6262 | -0.064087 | 61.8988 | 124.4247 | 124.6674 | -124.9924 | -124.9786
476.375 | 124.9054 | -61.8118 | 62.9883 | -0.30197 | 0.013016 | 0.013811 | 0.0030869 | 0.066652 | -0.0013244 | 0.069814 | -61.8805 | 62.9105 | -62.0224 | -61.8073 | 62.7365 | 0 | 0.068665 | 0.1831 | 62.8967 | -62.0316 | -0.21057 | -0.07782 | -0.068664 | 0.004578 | -0.25177 | -0.21973 | -0.091552 | 0.14191 | 61.8805 | 61.9949 | 124.5483 | 124.7223 | -0.068664 | 124.7086 | 61.8118 | -0.21973 | 124.7223 | -0.068664 | 61.8118 | 124.5483 | 124.7086 | -125.0107 | -125.0198
477.375 | 124.9329 | -61.7752 | 63.0203 | -0.22568 | 0.011307 | 0.01317 | 0.0041549 | 0.07007 | -0.0023926 | 0.069387 | -61.8484 | 62.9013 | -62.0453 | -61.9583 | 62.6083 | 0.068665 | 0.1236 | 0.16479 | 62.9333 | -62.0041 | -0.27008 | -0.11902 | -0.073242 | -0.1831 | -0.41199 | -0.22888 | -0.086975 | 0.19684 | 61.8988 | 61.94 | 124.3835 | 124.6765 | -0.073242 | 124.7086 | 61.8439 | -0.22888 | 124.6765 | -0.073242 | 61.8439 | 124.3835 | 124.7086 | -125.0656 | -125.0244
478.375 | 124.8596 | -61.7752 | 63.002 | -0.26382 | 0.012589 | 0.012529 | 0.0039413 | 0.069002 | -0.0023926 | 0.068319 | -61.8393 | 62.8922 | -62.0132 | -61.94 | 62.6266 | 0.10071 | 0.064087 | 0.17853 | 62.9059 | -61.9904 | -0.23804 | -0.10986 | -0.064086 | -0.16479 | -0.37537 | -0.21515 | -0.09613 | 0.17395 | 61.8393 | 61.9537 | 124.4019 | 124.6674 | -0.064086 | 124.6811 | 61.8759 | -0.21515 | 124.6674 | -0.064086 | 61.8759 | 124.4019 | 124.6811 | -125.0153 | -124.9924
479.375 | 124.9146 | -61.7661 | 62.9883 | -0.31723 | 0.011948 | 0.015947 | 0.0039413 | 0.069002 | -0.0017518 | 0.069173 | -61.821 | 62.8693 | -61.9904 | -61.9171 | 62.6541 | 0.12817 | 0.07782 | 0.21057 | 62.9196 | -62.0087 | -0.2243 | -0.11902 | -0.054932 | -0.15106 | -0.33417 | -0.24262 | -0.068664 | 0.16937 | 61.8439 | 61.9766 | 124.4202 | 124.6353 | -0.054932 | 124.6857 | 61.8942 | -0.24262 | 124.6353 | -0.054932 | 61.8942 | 124.4202 | 124.6857 | -124.9786 | -124.9969
480.3906 | 124.9329 | -61.8027 | 62.9608 | 0.14816 | 0.015793 | 0.014024 | 0.010136 | 0.069857 | -0.00089719 | 0.069814 | -61.8805 | 62.9288 | -62.0682 | -61.9766 | 62.5671 | -0.022888 | -0.059509 | 0.036621 | 62.8876 | -62.0728 | -0.2655 | -0.032043 | -0.07782 | -0.17395 | -0.39368 | -0.27008 | -0.073242 | 0.18768 | 61.7432 | 61.8393 | 124.3698 | 124.7314 | -0.07782 | 124.6902 | 61.7798 | -0.27008 | 124.7314 | -0.07782 | 61.7798 | 124.3698 | 124.6902 | -125.029 | -125.0336
481.375 | 124.9512 | -61.7706 | 62.9745 | -0.20279 | 0.012162 | 0.015092 | 0.0022323 | 0.069002 | -0.00068359 | 0.0696 | -61.7981 | 62.8647 | -61.9812 | -61.8851 | 62.6816 | 0.14191 | 0.027466 | 0.25635 | 62.8967 | -61.972 | -0.21057 | -0.10986 | -0.027466 | -0.11444 | -0.29297 | -0.20142 | -0.077819 | 0.1831 | 61.7981 | 62.027 | 124.4522 | 124.6353 | -0.027466 | 124.6674 | 61.9125 | -0.20142 | 124.6353 | -0.027466 | 61.9125 | 124.4522 | 124.6674 | -124.9557 | -124.9466
482.375 | 124.9054 | -61.8073 | 62.9929 | -0.27908 | 0.013443 | 0.017015 | 0.0054367 | 0.068575 | -4.2788e-05 | 0.069387 | -61.8393 | 62.9333 | -62.0132 | -61.9446 | 62.6404 | 0.09613 | 0.1236 | 0.17395 | 62.9517 | -62.0178 | -0.20599 | -0.059509 | -0.032043 | -0.13733 | -0.35248 | -0.21057 | -0.041199 | 0.17395 | 61.9308 | 61.9812 | 124.4476 | 124.7406 | -0.032043 | 124.7589 | 61.9034 | -0.21057 | 124.7406 | -0.032043 | 61.9034 | 124.4476 | 124.7589 | -125.0061 | -125.0107
483.375 | 124.8642 | -61.7752 | 62.9974 | -0.32486 | 0.013871 | 0.012956 | 0.0052231 | 0.06943 | -0.0013244 | 0.067037 | -61.8301 | 62.8647 | -62.0041 | -61.9308 | 62.6312 | 0.09613 | 0.10071 | 0.18768 | 62.9288 | -61.9949 | -0.22888 | -0.13275 | -0.054931 | -0.15564 | -0.36621 | -0.21973 | -0.068665 | 0.17395 | 61.8759 | 61.9629 | 124.4064 | 124.6399 | -0.054931 | 124.704 | 61.8713 | -0.21973 | 124.6399 | -0.054931 | 61.8713 | 124.4064 | 124.704 | -125.0015 | -124.9924
484.375 | 124.8688 | -61.7844 | 62.9929 | -0.24857 | 0.01088 | 0.012743 | 0.0067185 | 0.069002 | 0.00038461 | 0.070455 | -61.853 | 62.97 | -61.9949 | -61.9904 | 62.6266 | 0.082397 | 0.091553 | 0.16022 | 62.9196 | -62.0178 | -0.21057 | -0.022888 | -0.068664 | -0.20599 | -0.36621 | -0.23346 | -0.073242 | 0.14191 | 61.8759 | 61.9446 | 124.411 | 124.7543 | -0.068664 | 124.704 | 61.8668 | -0.23346 | 124.7543 | -0.068664 | 61.8668 | 124.411 | 124.704 | -124.9878 | -125.0107
485.375 | 124.9008 | -61.7798 | 62.9974 | -0.06546 | 0.013657 | 0.011675 | 0.0097091 | 0.068789 | -0.0017518 | 0.066823 | -61.7981 | 62.9105 | -62.0316 | -61.9125 | 62.645 | 0.10529 | 0.036621 | 0.1831 | 62.9013 | -62.0178 | -0.25177 | -0.086976 | -0.018311 | -0.13275 | -0.35248 | -0.23804 | -0.096131 | 0.23346 | 61.8164 | 61.9629 | 124.4247 | 124.6902 | -0.018311 | 124.6811 | 61.8851 | -0.23804 | 124.6902 | -0.018311 | 61.8851 | 124.4247 | 124.6811 | -125.029 | -125.0153
486.375 | 124.9603 | -61.7523 | 62.9837 | -0.24857 | 0.013871 | 0.015733 | 0.0037277 | 0.069216 | -0.0028198 | 0.067464 | -61.7935 | 62.8372 | -61.9949 | -61.8759 | 62.6862 | 0.17395 | 0.009155 | 0.26093 | 62.8876 | -61.9675 | -0.24262 | -0.14649 | -0.041199 | -0.1236 | -0.29755 | -0.21515 | -0.096131 | 0.20142 | 61.7615 | 62.0132 | 124.4385 | 124.5895 | -0.041199 | 124.6399 | 61.9263 | -0.21515 | 124.5895 | -0.041199 | 61.9263 | 124.4385 | 124.6399 | -124.9786 | -124.9512
487.375 | 124.8734 | -61.7889 | 62.9837 | -0.30197 | 0.013657 | 0.012956 | 0.0056503 | 0.067721 | -0.0011108 | 0.068532 | -61.8393 | 62.8876 | -62.0041 | -61.94 | 62.6358 | 0.10986 | 0.10529 | 0.17395 | 62.8922 | -62.0132 | -0.21515 | -0.096131 | -0.050354 | -0.15106 | -0.3479 | -0.22431 | -0.091553 | 0.16479 | 61.8942 | 61.9629 | 124.4247 | 124.6765 | -0.050354 | 124.6811 | 61.8988 | -0.22431 | 124.6765 | -0.050354 | 61.8988 | 124.4247 | 124.6811 | -124.9878 | -124.9969
488.375 | 125.0015 | -61.7569 | 62.97 | -0.2562 | 0.013871 | 0.012529 | 0.0022323 | 0.067721 | -0.002179 | 0.070455 | -61.7889 | 62.8418 | -61.9675 | -61.8622 | 62.7045 | 0.1831 | -0.027466 | 0.27924 | 62.8876 | -61.9995 | -0.21057 | -0.12817 | -0.032043 | -0.10529 | -0.2655 | -0.24262 | -0.082398 | 0.17853 | 61.7294 | 62.0361 | 124.4614 | 124.5987 | -0.032043 | 124.6445 | 61.94 | -0.24262 | 124.5987 | -0.032043 | 61.94 | 124.4614 | 124.6445 | -124.9374 | -124.9695
489.375 | 125.0107 | -61.7615 | 62.9562 | -0.24094 | 0.010666 | 0.013383 | 0.0037277 | 0.068361 | -0.00046999 | 0.068532 | -61.7935 | 62.8464 | -62.0132 | -61.853 | 62.7045 | 0.1831 | -0.036621 | 0.27924 | 62.8738 | -61.9949 | -0.25177 | -0.10986 | -0.032043 | -0.091552 | -0.25177 | -0.23346 | -0.082398 | 0.21973 | 61.7249 | 62.0407 | 124.4659 | 124.6078 | -0.032043 | 124.6353 | 61.9446 | -0.23346 | 124.6078 | -0.032043 | 61.9446 | 124.4659 | 124.6353 | -124.9695 | -124.9512
490.3906 | 124.8459 | -61.8393 | 62.9745 | 0.43045 | 0.013657 | 0.015947 | 0.0094955 | 0.069643 | -0.0015382 | 0.071096 | -61.8393 | 62.915 | -62.0728 | -62.0178 | 62.558 | -0.027466 | -0.013733 | 0.013733 | 62.8922 | -62.0316 | -0.23346 | -0.059509 | 0 | -0.17853 | -0.41656 | -0.19226 | -0.082397 | 0.23346 | 61.8256 | 61.853 | 124.3973 | 124.7543 | 0 | 124.7314 | 61.8118 | -0.19226 | 124.7543 | 0 | 61.8118 | 124.3973 | 124.7314 | -125.0473 | -125.0061
491.375 | 124.9603 | -61.7569 | 62.9654 | -0.23331 | 0.011307 | 0.014024 | 0.0011643 | 0.070925 | -0.003247 | 0.069173 | -61.7889 | 62.8601 | -62.0041 | -61.8759 | 62.6862 | 0.14648 | 0.009155 | 0.25635 | 62.9105 | -61.972 | -0.24719 | -0.10529 | -0.032043 | -0.11902 | -0.27924 | -0.21515 | -0.054932 | 0.21515 | 61.7661 | 62.0132 | 124.4431 | 124.617 | -0.032043 | 124.6674 | 61.9034 | -0.21515 | 124.617 | -0.032043 | 61.9034 | 124.4431 | 124.6674 | -124.9695 | -124.9374
492.375 | 124.8367 | -61.7752 | 62.9791 | -0.21805 | 0.012375 | 0.011675 | 0.0056503 | 0.067721 | -0.0026062 | 0.069814 | -61.8301 | 62.8876 | -62.0178 | -61.94 | 62.6312 | 0.09613 | 0.11902 | 0.18768 | 62.9013 | -62.0087 | -0.24261 | -0.091553 | -0.054931 | -0.16479 | -0.3479 | -0.23346 | -0.07782 | 0.18768 | 61.8942 | 61.9629 | 124.4064 | 124.6628 | -0.054931 | 124.6765 | 61.8713 | -0.23346 | 124.6628 | -0.054931 | 61.8713 | 124.4064 | 124.6765 | -124.9969 | -124.9878
493.375 | 124.9557 | -61.7523 | 62.97 | -0.27908 | 0.014298 | 0.009752 | 0.0050095 | 0.068148 | -0.0036744 | 0.0696 | -61.7844 | 62.8326 | -62.0041 | -61.8622 | 62.7045 | 0.17395 | -0.036621 | 0.27008 | 62.8738 | -61.9812 | -0.25177 | -0.13733 | -0.032044 | -0.10986 | -0.2655 | -0.22888 | -0.096131 | 0.21973 | 61.7157 | 62.0224 | 124.4568 | 124.585 | -0.032044 | 124.6262 | 61.9263 | -0.22888 | 124.585 | -0.032044 | 61.9263 | 124.4568 | 124.6262 | -124.9741 | -124.9512
494.375 | 124.9603 | -61.7798 | 62.9654 | -0.3096 | 0.012375 | 0.013383 | 0.0050095 | 0.066439 | -0.0013244 | 0.068105 | -61.8073 | 62.8601 | -61.9995 | -61.8896 | 62.6724 | 0.14648 | 0.032043 | 0.23804 | 62.8784 | -61.972 | -0.21973 | -0.10529 | -0.027466 | -0.10986 | -0.29297 | -0.19226 | -0.086975 | 0.19226 | 61.8118 | 62.0178 | 124.4522 | 124.6399 | -0.027466 | 124.6582 | 61.9263 | -0.19226 | 124.6399 | -0.027466 | 61.9263 | 124.4522 | 124.6582 | -124.9649 | -124.9374
495.375 | 125.0061 | -61.7203 | 62.9608 | -0.24094 | 0.011734 | 0.014665 | 0.0045823 | 0.068361 | -0.0011108 | 0.066823 | -61.7889 | 62.8418 | -61.9766 | -61.8484 | 62.7045 | 0.18768 | -0.050354 | 0.27924 | 62.8922 | -61.9675 | -0.25635 | -0.11902 | -0.068664 | -0.12817 | -0.25635 | -0.24719 | -0.068664 | 0.18768 | 61.6699 | 61.9995 | 124.4247 | 124.5621 | -0.068664 | 124.6124 | 61.908 | -0.24719 | 124.5621 | -0.068664 | 61.908 | 124.4247 | 124.6124 | -124.9374 | -124.9283
496.375 | 124.9741 | -61.7157 | 62.9379 | -0.21042 | 0.0098118 | 0.019792 | 0.0037277 | 0.068789 | -0.0015382 | 0.068319 | -61.821 | 62.8326 | -62.0041 | -61.8301 | 62.7274 | 0.18768 | -0.059509 | 0.28381 | 62.883 | -61.9537 | -0.28839 | -0.10529 | -0.10529 | -0.11444 | -0.21057 | -0.23804 | -0.054931 | 0.1831 | 61.6562 | 61.9995 | 124.4431 | 124.5483 | -0.10529 | 124.5987 | 61.9034 | -0.23804 | 124.5483 | -0.10529 | 61.9034 | 124.4431 | 124.5987 | -124.942 | -124.8917
497.375 | 124.9832 | -61.7386 | 62.9745 | -0.27908 | 0.011307 | 0.014024 | 0.0052231 | 0.068361 | -0.0026062 | 0.069387 | -61.7981 | 62.8326 | -61.972 | -61.8668 | 62.6862 | 0.17853 | -0.036621 | 0.25635 | 62.883 | -61.9629 | -0.23346 | -0.14191 | -0.05951 | -0.12817 | -0.28839 | -0.22431 | -0.091552 | 0.17395 | 61.702 | 61.9949 | 124.4247 | 124.5712 | -0.05951 | 124.6216 | 61.9171 | -0.22431 | 124.5712 | -0.05951 | 61.9171 | 124.4247 | 124.6216 | -124.9466 | -124.9374
498.375 | 124.9603 | -61.7523 | 62.9837 | -0.23331 | 0.0095982 | 0.01552 | 0.0037277 | 0.066866 | -0.0026062 | 0.068746 | -61.7844 | 62.8189 | -61.9858 | -61.8393 | 62.7136 | 0.1831 | -0.032043 | 0.25635 | 62.8738 | -61.9583 | -0.23346 | -0.1648 | -0.032044 | -0.086975 | -0.27008 | -0.20599 | -0.10986 | 0.20142 | 61.7203 | 62.0087 | 124.4659 | 124.5712 | -0.032044 | 124.6262 | 61.9354 | -0.20599 | 124.5712 | -0.032044 | 61.9354 | 124.4659 | 124.6262 | -124.9695 | -124.942
499.375 | 124.9924 | -61.7294 | 62.9654 | -0.24857 | 0.010666 | 0.01317 | 0.0043687 | 0.066012 | -0.003247 | 0.06896 | -61.7935 | 62.8235 | -61.9858 | -61.8347 | 62.7045 | 0.19684 | -0.054932 | 0.27466 | 62.8601 | -61.9583 | -0.25635 | -0.14191 | -0.064087 | -0.10529 | -0.26093 | -0.22888 | -0.10529 | 0.19226 | 61.6745 | 62.0041 | 124.4339 | 124.5529 | -0.064087 | 124.5895 | 61.9263 | -0.22888 | 124.5529 | -0.064087 | 61.9263 | 124.4339 | 124.5895 | -124.9512 | -124.9237
500.375 | 125.0107 | -61.7432 | 62.9471 | 2.91 | 0.011093 | 0.0088974 | 0.0033005 | 0.068361 | -0.0019654 | 0.06896 | -61.6974 | 62.8098 | -61.9995 | -61.8576 | 62.6953 | 0.19226 | -0.082397 | 0.27924 | 62.851 | -61.972 | -0.25635 | -0.13733 | 0.045776 | -0.11444 | -0.25177 | -0.22888 | -0.096131 | 0.30212 | 61.6608 | 62.0224 | 124.4385 | 124.5529 | 0.045776 | 124.5941 | 61.9354 | -0.22888 | 124.5529 | 0.045776 | 61.9354 | 124.4385 | 124.5941 | -124.9466 | -124.9191
501.375 | 124.9741 | -61.7569 | 62.9608 | -0.22568 | 0.011307 | 0.0086838 | 0.0069321 | 0.066012 | -0.0043152 | 0.067037 | -61.7615 | 62.8235 | -62.0132 | -61.853 | 62.7136 | 0.1831 | -0.045776 | 0.26093 | 62.8922 | -61.9766 | -0.25635 | -0.13733 | -0.004578 | -0.09613 | -0.24719 | -0.21973 | -0.068664 | 0.25177 | 61.7111 | 62.0178 | 124.4705 | 124.5804 | -0.004578 | 124.649 | 61.94 | -0.21973 | 124.5804 | -0.004578 | 61.94 | 124.4705 | 124.649 | -124.9741 | -124.9374
502.375 | 124.9832 | -61.7432 | 62.9471 | -0.14175 | 0.010453 | 0.014665 | 0.0039413 | 0.067934 | -0.0019654 | 0.069387 | -61.8073 | 62.8281 | -62.0453 | -61.8484 | 62.6999 | 0.16479 | -0.091553 | 0.27466 | 62.8601 | -61.9492 | -0.30212 | -0.11902 | -0.064087 | -0.10529 | -0.24719 | -0.20599 | -0.086976 | 0.23804 | 61.6516 | 62.0178 | 124.4431 | 124.5712 | -0.064087 | 124.6033 | 61.908 | -0.20599 | 124.5712 | -0.064087 | 61.908 | 124.4431 | 124.6033 | -124.9924 | -124.8962
503.375 | 124.9741 | -61.7661 | 62.9471 | -0.088349 | 0.010025 | 0.012102 | 0.0039413 | 0.067934 | -0.00068359 | 0.070455 | -61.8073 | 62.8143 | -62.0087 | -61.8668 | 62.6862 | 0.15106 | -0.10986 | 0.21973 | 62.851 | -61.9812 | -0.24262 | -0.13275 | -0.041199 | -0.10071 | -0.26093 | -0.21515 | -0.096131 | 0.20142 | 61.6562 | 61.9858 | 124.4522 | 124.5804 | -0.041199 | 124.617 | 61.9171 | -0.21515 | 124.5804 | -0.041199 | 61.9171 | 124.4522 | 124.617 | -124.9557 | -124.9283
504.375 | 125.0015 | -61.7432 | 62.9562 | -0.16464 | 0.0095982 | 0.011461 | 0.0024461 | 0.060885 | -0.0013244 | 0.070028 | -61.7889 | 62.796 | -61.9904 | -62.0956 | 62.5534 | 0.20142 | -0.24719 | 0.18768 | 62.8235 | -61.972 | -0.24719 | -0.16022 | -0.045776 | -0.35248 | -0.40283 | -0.22888 | -0.13275 | 0.20142 | 61.496 | 61.9308 | 124.2966 | 124.5392 | -0.045776 | 124.5667 | 61.9446 | -0.22888 | 124.5392 | -0.045776 | 61.9446 | 124.2966 | 124.5667 | -124.9466 | -124.9283
505.375 | 125.1572 | -61.7111 | 63.0157 | -0.1265 | 0.013016 | 0.008043 | 0.0050095 | 0.064944 | -0.0028198 | 0.069814 | -61.7844 | 62.8006 | -61.9904 | -61.8393 | 62.7319 | 0.18768 | -0.10986 | 0.25177 | 62.8464 | -61.9446 | -0.27923 | -0.21515 | -0.073242 | -0.12817 | -0.28381 | -0.23346 | -0.16937 | 0.20599 | 61.6013 | 61.9629 | 124.4431 | 124.5117 | -0.073242 | 124.5575 | 61.8988 | -0.23346 | 124.5117 | -0.073242 | 61.8988 | 124.4431 | 124.5575 | -125.0061 | -124.9603
506.375 | 124.9969 | -61.7432 | 62.9471 | -0.14175 | 0.012375 | 0.016161 | 0.0011643 | 0.067934 | -0.0041016 | 0.069173 | -61.8118 | 62.8006 | -61.9904 | -61.853 | 62.6953 | 0.16937 | -0.10529 | 0.22888 | 62.8647 | -61.9675 | -0.24719 | -0.14648 | -0.068665 | -0.10986 | -0.25177 | -0.2243 | -0.082398 | 0.17853 | 61.6379 | 61.972 | 124.4385 | 124.5438 | -0.068665 | 124.6078 | 61.9125 | -0.2243 | 124.5438 | -0.068665 | 61.9125 | 124.4385 | 124.6078 | -124.9374 | -124.9146
507.375 | 124.9924 | -61.734 | 62.9242 | -0.06546 | 0.0098118 | 0.015947 | 0.0035141 | 0.065157 | -0.0013244 | 0.069387 | -61.8256 | 62.8052 | -62.027 | -61.8668 | 62.6862 | 0.15564 | -0.10529 | 0.20142 | 62.8555 | -61.9537 | -0.29297 | -0.11902 | -0.091553 | -0.13275 | -0.23804 | -0.21973 | -0.068664 | 0.20142 | 61.6287 | 61.9354 | 124.4202 | 124.5392 | -0.091553 | 124.5895 | 61.8896 | -0.21973 | 124.5392 | -0.091553 | 61.8896 | 124.4202 | 124.5895 | -124.9512 | -124.8779
508.375 | 124.9969 | -61.7294 | 62.9562 | -0.1265 | 0.011521 | 0.012102 | -0.00011753 | 0.067721 | 0.0014526 | 0.06661 | -61.7798 | 62.8235 | -61.9812 | -61.8118 | 62.677 | 0.068665 | -0.041199 | 0.23804 | 62.8372 | -61.9629 | -0.25177 | -0.13275 | -0.050354 | -0.082398 | -0.27924 | -0.23346 | -0.11902 | 0.20142 | 61.6882 | 61.9675 | 124.4064 | 124.5529 | -0.050354 | 124.5666 | 61.7981 | -0.23346 | 124.5529 | -0.050354 | 61.7981 | 124.4064 | 124.5666 | -124.9374 | -124.9191
509.375 | 124.9786 | -61.7706 | 62.9517 | -0.07309 | 0.01088 | 0.011034 | 0.0037277 | 0.064516 | -0.00068359 | 0.068105 | -61.8439 | 62.8143 | -62.027 | -61.8851 | 62.677 | 0.14648 | -0.10071 | 0.17853 | 62.8418 | -61.9766 | -0.25635 | -0.13733 | -0.073242 | -0.11444 | -0.27466 | -0.20599 | -0.10986 | 0.18311 | 61.6699 | 61.9492 | 124.4476 | 124.585 | -0.073242 | 124.6124 | 61.9171 | -0.20599 | 124.585 | -0.073242 | 61.9171 | 124.4476 | 124.6124 | -124.9786 | -124.9283
510.375 | 124.9786 | -61.7386 | 62.97 | -0.057831 | 0.010239 | 0.012529 | 0.0035141 | 0.066225 | -0.00068359 | 0.06896 | -61.8439 | 62.8235 | -62.0224 | -61.8942 | 62.6724 | 0.14648 | -0.10529 | 0.18768 | 62.8464 | -61.9812 | -0.28381 | -0.14648 | -0.10529 | -0.15564 | -0.29755 | -0.24262 | -0.1236 | 0.17853 | 61.6333 | 61.9263 | 124.411 | 124.5621 | -0.10529 | 124.585 | 61.8851 | -0.24262 | 124.5621 | -0.10529 | 61.8851 | 124.411 | 124.585 | -124.9924 | -124.9512
511.375 | 124.9969 | -61.734 | 62.9471 | -0.14175 | 0.01323 | 0.011675 | 0.0033005 | 0.067934 | -0.0034608 | 0.070455 | -61.8027 | 62.8143 | -61.9766 | -61.8347 | 62.7045 | 0.15106 | -0.10529 | 0.24261 | 62.851 | -61.9675 | -0.24262 | -0.13275 | -0.068664 | -0.10071 | -0.24262 | -0.23346 | -0.096131 | 0.17395 | 61.6287 | 61.9766 | 124.4385 | 124.5483 | -0.068664 | 124.585 | 61.8851 | -0.23346 | 124.5483 | -0.068664 | 61.8851 | 124.4385 | 124.585 | -124.9237 | -124.9146
512.375 | 124.9649 | -61.7477 | 62.9517 | -0.050202 | 0.013657 | 0.011888 | 0.0028733 | 0.066652 | -0.0013244 | 0.070241 | -61.8347 | 62.8235 | -62.0087 | -61.9034 | 62.6633 | 0.10986 | -0.091553 | 0.15564 | 62.8693 | -61.9675 | -0.26093 | -0.12817 | -0.086975 | -0.15564 | -0.28839 | -0.21973 | -0.082397 | 0.17395 | 61.6562 | 61.9034 | 124.411 | 124.5712 | -0.086975 | 124.617 | 61.8576 | -0.21973 | 124.5712 | -0.086975 | 61.8576 | 124.411 | 124.617 | -124.9603 | -124.9191
513.375 | 124.9695 | -61.7477 | 62.9379 | -0.019684 | 0.012162 | 0.0095382 | 0.0018051 | 0.065584 | -0.0015382 | 0.070669 | -61.8484 | 62.8143 | -62.0316 | -61.908 | 62.645 | 0.10529 | -0.10529 | 0.14648 | 62.8738 | -61.9904 | -0.28381 | -0.1236 | -0.10071 | -0.16022 | -0.29297 | -0.24261 | -0.064087 | 0.1831 | 61.6425 | 61.8942 | 124.3927 | 124.5621 | -0.10071 | 124.6216 | 61.853 | -0.24261 | 124.5621 | -0.10071 | 61.853 | 124.3927 | 124.6216 | -124.9695 | -124.9283
514.375 | 124.942 | -61.734 | 62.9517 | 0.018463 | 0.010025 | 0.012102 | 0.0045823 | 0.064944 | -0.0028198 | 0.067891 | -61.8576 | 62.8235 | -62.0178 | -61.9125 | 62.6404 | 0.10529 | -0.10529 | 0.13275 | 62.8372 | -61.972 | -0.28381 | -0.12817 | -0.1236 | -0.17853 | -0.31128 | -0.23804 | -0.11444 | 0.16022 | 61.6287 | 61.8668 | 124.3744 | 124.5575 | -0.1236 | 124.5712 | 61.8393 | -0.23804 | 124.5575 | -0.1236 | 61.8393 | 124.3744 | 124.5712 | -124.9695 | -124.9237
515.375 | 125.0153 | -61.7661 | 62.9608 | -0.088349 | 0.010453 | 0.011461 | 0.0026597 | 0.06473 | -0.00025639 | 0.070241 | -61.8347 | 62.8098 | -61.9904 | -61.8713 | 62.6816 | 0.15106 | -0.10529 | 0.17853 | 62.8235 | -61.9812 | -0.2243 | -0.15106 | -0.068665 | -0.10529 | -0.27923 | -0.21515 | -0.13733 | 0.15564 | 61.6608 | 61.9446 | 124.4476 | 124.5758 | -0.068665 | 124.5895 | 61.9171 | -0.21515 | 124.5758 | -0.068665 | 61.9171 | 124.4476 | 124.5895 | -124.9512 | -124.942
516.375 | 124.9741 | -61.7569 | 62.9562 | -0.019684 | 0.013443 | 0.013383 | 0.0022323 | 0.068789 | -0.0013244 | 0.069387 | -61.8805 | 62.8464 | -62.0087 | -61.908 | 62.6358 | 0.09613 | -0.09613 | 0.13733 | 62.851 | -61.9583 | -0.25177 | -0.10986 | -0.1236 | -0.15106 | -0.32043 | -0.20142 | -0.10529 | 0.12817 | 61.6608 | 61.8942 | 124.3927 | 124.6033 | -0.1236 | 124.6078 | 61.853 | -0.20142 | 124.6033 | -0.1236 | 61.853 | 124.3927 | 124.6078 | -124.9649 | -124.9146
517.375 | 124.9695 | -61.734 | 62.9517 | -0.13412 | 0.012162 | 0.01317 | 0.0039413 | 0.065798 | 0.00081181 | 0.070028 | -61.821 | 62.8235 | -62.0041 | -61.8713 | 62.677 | 0.14648 | -0.13275 | 0.1831 | 62.8372 | -61.9629 | -0.27008 | -0.12817 | -0.086975 | -0.13733 | -0.27466 | -0.22888 | -0.11444 | 0.1831 | 61.6013 | 61.9171 | 124.411 | 124.5575 | -0.086975 | 124.5712 | 61.8805 | -0.22888 | 124.5575 | -0.086975 | 61.8805 | 124.411 | 124.5712 | -124.9557 | -124.9146
518.375 | 124.9512 | -61.7523 | 62.97 | -0.088349 | 0.012589 | 0.012102 | 0.0028733 | 0.063875 | -0.0023926 | 0.070028 | -61.8301 | 62.8464 | -62.0087 | -61.8851 | 62.677 | 0.14191 | -0.11902 | 0.16479 | 62.8326 | -61.9446 | -0.25635 | -0.1236 | -0.07782 | -0.13275 | -0.29297 | -0.19226 | -0.13733 | 0.17853 | 61.6333 | 61.9171 | 124.4293 | 124.5987 | -0.07782 | 124.585 | 61.8942 | -0.19226 | 124.5987 | -0.07782 | 61.8942 | 124.4293 | 124.585 | -124.9786 | -124.9146
519.375 | 125.0198 | -61.7432 | 62.9471 | -0.10361 | 0.010666 | 0.015733 | 0.0015915 | 0.066652 | -0.0015382 | 0.0696 | -61.8439 | 62.8281 | -62.0178 | -61.8668 | 62.6907 | 0.15564 | -0.11444 | 0.15564 | 62.8281 | -61.9675 | -0.27466 | -0.11902 | -0.10071 | -0.1236 | -0.25635 | -0.2243 | -0.11902 | 0.17395 | 61.6287 | 61.8988 | 124.4339 | 124.5712 | -0.10071 | 124.5712 | 61.8988 | -0.2243 | 124.5712 | -0.10071 | 61.8988 | 124.4339 | 124.5712 | -124.9649 | -124.9146
520.375 | 124.8688 | -61.7294 | 62.9333 | -0.13412 | 0.010239 | 0.01317 | 0.0022323 | 0.064303 | -0.00068359 | 0.068319 | -61.8073 | 62.8189 | -61.972 | -61.8393 | 62.7228 | 0.21515 | -0.11444 | 0.60883 | 62.8967 | -61.9125 | -0.24262 | -0.11444 | -0.07782 | -0.10986 | -0.21057 | -0.18311 | -0.036621 | 0.16479 | 61.615 | 62.3383 | 124.4522 | 124.5483 | -0.07782 | 124.6262 | 61.9446 | -0.18311 | 124.5483 | -0.07782 | 61.9446 | 124.4522 | 124.6262 | -124.9054 | -124.8459
521.375 | 125.1526 | -61.6928 | 63.0112 | -0.10361 | 0.01088 | 0.012529 | 0.0020187 | 0.064944 | -0.0026062 | 0.068319 | -61.8027 | 62.8555 | -61.9904 | -61.8301 | 62.7136 | 0.19226 | -0.12817 | 0.23804 | 62.8418 | -61.9537 | -0.29755 | -0.15564 | -0.10986 | -0.13733 | -0.29755 | -0.26093 | -0.16937 | 0.18768 | 61.5646 | 61.9308 | 124.4064 | 124.5483 | -0.10986 | 124.5346 | 61.8851 | -0.26093 | 124.5483 | -0.10986 | 61.8851 | 124.4064 | 124.5346 | -125.0015 | -124.9649
522.375 | 124.9741 | -61.7249 | 62.9608 | -0.35538 | 0.012375 | 0.0086838 | 0.0047959 | 0.066012 | -0.0028198 | 0.067891 | -61.7889 | 62.8281 | -61.9629 | -61.8393 | 62.7045 | 0.20142 | -0.10071 | 0.23804 | 62.8601 | -61.9537 | -0.23804 | -0.13275 | -0.064086 | -0.11444 | -0.25635 | -0.22888 | -0.10071 | 0.17395 | 61.6241 | 61.9629 | 124.4293 | 124.5529 | -0.064086 | 124.585 | 61.9263 | -0.22888 | 124.5529 | -0.064086 | 61.9263 | 124.4293 | 124.585 | -124.9237 | -124.9145
523.375 | 125.0061 | -61.734 | 62.9471 | -0.1265 | 0.010666 | 0.016374 | 0.0056503 | 0.06708 | 0.00059821 | 0.068746 | -61.8027 | 62.8235 | -61.9904 | -61.8439 | 62.6953 | 0.17395 | -0.11902 | 0.20142 | 62.8006 | -61.9537 | -0.25635 | -0.1236 | -0.068664 | -0.10986 | -0.25177 | -0.21973 | -0.14648 | 0.18768 | 61.615 | 61.9354 | 124.4293 | 124.5575 | -0.068664 | 124.5346 | 61.908 | -0.21973 | 124.5575 | -0.068664 | 61.908 | 124.4293 | 124.5346 | -124.9374 | -124.9008
524.375 | 125.0015 | -61.7432 | 62.9562 | 0.22446 | 0.012162 | 0.014665 | 0.0024461 | 0.067507 | 0.00017081 | 0.067891 | -61.7935 | 62.8098 | -61.9995 | -61.821 | 62.6953 | 0.21057 | -0.082397 | 0.24719 | 62.8281 | -61.9812 | -0.25635 | -0.14648 | -0.050354 | -0.07782 | -0.26093 | -0.23804 | -0.12817 | 0.20599 | 61.6608 | 61.9904 | 124.4385 | 124.5529 | -0.050354 | 124.5712 | 61.9537 | -0.23804 | 124.5529 | -0.050354 | 61.9537 | 124.4385 | 124.5712 | -124.9557 | -124.9374
525.375 | 124.9512 | -61.7477 | 62.9608 | 2.7727 | 0.012589 | 0.01082 | 0.0011643 | 0.067934 | -0.0019654 | 0.069173 | -61.7294 | 62.8235 | -61.9904 | -61.8484 | 62.7182 | 0.19684 | -0.10986 | 0.23346 | 62.8464 | -61.9446 | -0.24261 | -0.13733 | 0.018311 | -0.10071 | -0.24261 | -0.19684 | -0.11444 | 0.26093 | 61.6379 | 61.9812 | 124.4659 | 124.5712 | 0.018311 | 124.5941 | 61.9446 | -0.19684 | 124.5712 | 0.018311 | 61.9446 | 124.4659 | 124.5941 | -124.9512 | -124.9054
526.375 | 124.9832 | -61.7249 | 62.9654 | -3.4377 | 0.00853 | 0.011675 | 0.0062913 | 0.065157 | -0.0041016 | 0.068105 | -61.5463 | 62.8967 | -61.9537 | -61.8484 | 62.6862 | 0.19226 | -0.1236 | 0.22888 | 62.8326 | -61.9354 | -0.22888 | -0.068664 | 0.17853 | -0.1236 | -0.27924 | -0.21057 | -0.13275 | 0.40741 | 61.6013 | 61.9537 | 124.411 | 124.6216 | 0.17853 | 124.5575 | 61.9171 | -0.21057 | 124.6216 | 0.17853 | 61.9171 | 124.411 | 124.5575 | -124.9191 | -124.9008
527.375 | 124.9969 | -61.7477 | 62.9288 | -0.22568 | 0.010453 | 0.012102 | 0.0011643 | 0.068575 | -0.002179 | 0.068105 | -61.4319 | 62.8876 | -61.9583 | -61.7935 | 62.6953 | 0.17395 | -0.12817 | 0.21515 | 62.8601 | -61.9354 | -0.21057 | -0.041199 | 0.31586 | -0.045776 | -0.23346 | -0.18768 | -0.068665 | 0.52643 | 61.6196 | 61.9629 | 124.4431 | 124.6353 | 0.31586 | 124.6078 | 61.9217 | -0.18768 | 124.6353 | 0.31586 | 61.9217 | 124.4431 | 124.6078 | -124.8871 | -124.8642
528.375 | 125.0244 | -61.7111 | 62.97 | -0.16464 | 0.01088 | 0.01082 | 0.0013779 | 0.06473 | -0.00046999 | 0.070241 | -61.7844 | 62.8555 | -61.9537 | -61.8759 | 62.7548 | 0.21515 | -0.15106 | 0.20142 | 62.8235 | -61.9446 | -0.24261 | -0.11444 | -0.073242 | -0.16479 | -0.21515 | -0.23346 | -0.14648 | 0.16937 | 61.5601 | 61.9125 | 124.4659 | 124.5667 | -0.073242 | 124.5346 | 61.9263 | -0.23346 | 124.5667 | -0.073242 | 61.9263 | 124.4659 | 124.5346 | -124.9237 | -124.9146
529.375 | 124.9374 | -61.7477 | 62.9608 | -0.24094 | 0.010025 | 0.012102 | 0.0052231 | 0.068575 | -0.0011108 | 0.068105 | -61.8027 | 62.8418 | -61.9766 | -61.8301 | 62.7045 | 0.19684 | -0.082397 | 0.19684 | 62.8372 | -61.9675 | -0.22888 | -0.11902 | -0.054931 | -0.082397 | -0.25635 | -0.21973 | -0.1236 | 0.17395 | 61.6653 | 61.9446 | 124.4522 | 124.5895 | -0.054931 | 124.585 | 61.9446 | -0.21973 | 124.5895 | -0.054931 | 61.9446 | 124.4522 | 124.585 | -124.9374 | -124.9283
530.375 | 124.9969 | -61.7386 | 62.9608 | -0.14938 | 0.010239 | 0.012102 | 0.0039413 | 0.068148 | -0.00046999 | 0.067891 | -61.7615 | 62.8235 | -61.9812 | -61.8118 | 62.6907 | 0.10529 | -0.073242 | 0.1831 | 62.8418 | -61.9492 | -0.24262 | -0.13733 | -0.022889 | -0.073243 | -0.27008 | -0.21057 | -0.11902 | 0.21973 | 61.6653 | 61.9217 | 124.4293 | 124.5621 | -0.022889 | 124.5804 | 61.8439 | -0.21057 | 124.5621 | -0.022889 | 61.8439 | 124.4293 | 124.5804 | -124.942 | -124.91
531.375 | 124.9924 | -61.7111 | 62.9791 | -0.24857 | 0.011734 | 0.012529 | 0.0056503 | 0.06708 | -0.0013244 | 0.068532 | -61.7798 | 62.8326 | -61.9904 | -61.8347 | 62.6999 | 0.1831 | -0.082397 | 0.20599 | 62.8784 | -61.9263 | -0.27923 | -0.14648 | -0.068664 | -0.1236 | -0.27924 | -0.21515 | -0.10071 | 0.21057 | 61.6287 | 61.9171 | 124.411 | 124.5438 | -0.068664 | 124.5895 | 61.8942 | -0.21515 | 124.5438 | -0.068664 | 61.8942 | 124.411 | 124.5895 | -124.9695 | -124.9054
532.375 | 124.9374 | -61.734 | 62.9654 | -0.24094 | 0.011734 | 0.015092 | 0.0030869 | 0.067507 | -0.003247 | 0.069173 | -61.7752 | 62.8189 | -61.9949 | -61.8301 | 62.7136 | 0.19684 | -0.091553 | 0.20599 | 62.8601 | -61.9629 | -0.26093 | -0.14648 | -0.041199 | -0.09613 | -0.25177 | -0.22888 | -0.10529 | 0.21973 | 61.6425 | 61.94 | 124.4476 | 124.5529 | -0.041199 | 124.5941 | 61.9308 | -0.22888 | 124.5529 | -0.041199 | 61.9308 | 124.4476 | 124.5941 | -124.9603 | -124.9283
533.375 | 124.9557 | -61.7249 | 62.9471 | -0.27145 | 0.011093 | 0.01317 | 0.0041549 | 0.066652 | -0.0019654 | 0.070669 | -61.7798 | 62.8601 | -61.9766 | -61.8439 | 62.7045 | 0.19684 | -0.086975 | 0.20142 | 62.8372 | -61.9629 | -0.25177 | -0.086976 | -0.054931 | -0.11902 | -0.24262 | -0.23804 | -0.10986 | 0.19684 | 61.6379 | 61.9263 | 124.4293 | 124.585 | -0.054931 | 124.5621 | 61.9217 | -0.23804 | 124.585 | -0.054931 | 61.9217 | 124.4293 | 124.5621 | -124.9237 | -124.91
534.375 | 124.9878 | -61.7386 | 62.9562 | -0.21042 | 0.011093 | 0.013811 | 0.0033005 | 0.064303 | -0.0017518 | 0.068319 | -61.7798 | 62.8418 | -61.9675 | -61.8347 | 62.7182 | 0.18768 | -0.091553 | 0.19684 | 62.851 | -61.9354 | -0.22888 | -0.11444 | -0.041199 | -0.096131 | -0.23804 | -0.19684 | -0.10529 | 0.18768 | 61.647 | 61.9354 | 124.4568 | 124.5804 | -0.041199 | 124.5895 | 61.9263 | -0.19684 | 124.5804 | -0.041199 | 61.9263 | 124.4568 | 124.5895 | -124.9237 | -124.8917
535.375 | 124.9008 | -61.7661 | 62.9929 | -0.27145 | 0.014298 | 0.014665 | 0.0058639 | 0.068789 | -0.00025639 | 0.0696 | -61.8027 | 62.8784 | -62.0041 | -61.8805 | 62.6678 | 0.16022 | 0.009155 | 0.15106 | 62.8738 | -61.9858 | -0.23804 | -0.11444 | -0.036621 | -0.11444 | -0.32501 | -0.21973 | -0.11902 | 0.20142 | 61.7752 | 61.9171 | 124.4339 | 124.6445 | -0.036621 | 124.6399 | 61.9263 | -0.21973 | 124.6445 | -0.036621 | 61.9263 | 124.4339 | 124.6399 | -124.9969 | -124.9786
536.375 | 124.9237 | -61.7752 | 62.9883 | -0.27145 | 0.011734 | 0.011461 | 0.0056503 | 0.067721 | -0.0045288 | 0.068319 | -61.821 | 62.8784 | -61.972 | -61.8759 | 62.6633 | 0.16937 | -0.009155 | 0.14648 | 62.8693 | -61.9629 | -0.19684 | -0.10986 | -0.045776 | -0.10071 | -0.32501 | -0.18768 | -0.11902 | 0.15106 | 61.7661 | 61.9217 | 124.4385 | 124.6536 | -0.045776 | 124.6445 | 61.9446 | -0.18768 | 124.6536 | -0.045776 | 61.9446 | 124.4385 | 124.6445 | -124.9603 | -124.9512
537.375 | 124.9741 | -61.7386 | 62.9654 | -0.27145 | 0.0095982 | 0.010606 | 0.0035141 | 0.067507 | -0.0026062 | 0.069814 | -61.7935 | 62.8555 | -61.9858 | -61.8256 | 62.6999 | 0.19684 | -0.10986 | 0.20142 | 62.8555 | -61.9766 | -0.24719 | -0.10986 | -0.054932 | -0.086976 | -0.2655 | -0.23804 | -0.10986 | 0.19226 | 61.6287 | 61.94 | 124.4385 | 124.5941 | -0.054932 | 124.5941 | 61.9354 | -0.23804 | 124.5941 | -0.054932 | 61.9354 | 124.4385 | 124.5941 | -124.9512 | -124.942
538.375 | 124.9237 | -61.7661 | 62.9837 | -0.27145 | 0.010453 | 0.014024 | 0.0052231 | 0.065798 | -0.0041016 | 0.068319 | -61.7889 | 62.8555 | -62.0041 | -61.8713 | 62.6816 | 0.16479 | -0.027466 | 0.14648 | 62.8784 | -61.9766 | -0.23804 | -0.12817 | -0.022888 | -0.10529 | -0.30212 | -0.21057 | -0.10529 | 0.21515 | 61.7386 | 61.9125 | 124.4476 | 124.6216 | -0.022888 | 124.6445 | 61.9308 | -0.21057 | 124.6216 | -0.022888 | 61.9308 | 124.4476 | 124.6445 | -124.9878 | -124.9603
539.375 | 124.9374 | -61.7477 | 62.9562 | -0.17227 | 0.013443 | 0.012529 | 0.0047959 | 0.06943 | -0.003247 | 0.06896 | -61.7981 | 62.8418 | -61.9949 | -61.8622 | 62.6862 | 0.17853 | -0.050354 | 0.16022 | 62.8555 | -61.9629 | -0.24719 | -0.11444 | -0.050354 | -0.11444 | -0.27008 | -0.21515 | -0.10071 | 0.19684 | 61.6974 | 61.908 | 124.4339 | 124.5895 | -0.050354 | 124.6033 | 61.9263 | -0.21515 | 124.5895 | -0.050354 | 61.9263 | 124.4339 | 124.6033 | -124.9512 | -124.9191
540.375 | 124.9374 | -61.7477 | 62.9791 | -0.24094 | 0.0089572 | 0.015092 | 0.0043687 | 0.066652 | -0.0030334 | 0.068105 | -61.7889 | 62.851 | -61.9949 | -61.8439 | 62.677 | 0.17395 | -0.064087 | 0.16937 | 62.851 | -61.9583 | -0.24719 | -0.12817 | -0.041198 | -0.09613 | -0.30212 | -0.21057 | -0.12817 | 0.20599 | 61.6837 | 61.9171 | 124.4247 | 124.5987 | -0.041198 | 124.5987 | 61.9217 | -0.21057 | 124.5987 | -0.041198 | 61.9217 | 124.4247 | 124.5987 | -124.9741 | -124.9374
541.375 | 124.9374 | -61.7203 | 62.9745 | -0.23331 | 0.012802 | 0.011675 | 0.0054367 | 0.06708 | -0.0028198 | 0.0696 | -61.7798 | 62.8326 | -61.9858 | -61.853 | 62.6953 | 0.19226 | -0.082397 | 0.16479 | 62.883 | -61.9583 | -0.2655 | -0.14191 | -0.059509 | -0.13275 | -0.27924 | -0.23804 | -0.091552 | 0.20599 | 61.6379 | 61.8851 | 124.4156 | 124.5529 | -0.059509 | 124.6033 | 61.9125 | -0.23804 | 124.5529 | -0.059509 | 61.9125 | 124.4156 | 124.6033 | -124.9603 | -124.9329
542.375 | 124.9649 | -61.7249 | 62.97 | -0.24857 | 0.010666 | 0.014238 | 0.0056503 | 0.067721 | -0.0013244 | 0.068105 | -61.7844 | 62.8464 | -61.972 | -61.8393 | 62.6999 | 0.18768 | -0.091553 | 0.18768 | 62.8693 | -61.9629 | -0.24719 | -0.1236 | -0.059509 | -0.11444 | -0.27008 | -0.23804 | -0.10071 | 0.18768 | 61.6333 | 61.9125 | 124.4247 | 124.5712 | -0.059509 | 124.5941 | 61.9125 | -0.23804 | 124.5712 | -0.059509 | 61.9125 | 124.4247 | 124.5941 | -124.942 | -124.9329
543.375 | 124.9878 | -61.7294 | 62.9608 | -0.22568 | 0.012802 | 0.014238 | 0.0037277 | 0.066866 | -0.0036744 | 0.067891 | -61.7798 | 62.8464 | -61.972 | -61.8439 | 62.7136 | 0.19226 | -0.10986 | 0.17395 | 62.8876 | -61.9675 | -0.24262 | -0.11444 | -0.050354 | -0.11444 | -0.24719 | -0.23804 | -0.073242 | 0.19226 | 61.6196 | 61.9034 | 124.4431 | 124.5758 | -0.050354 | 124.617 | 61.9217 | -0.23804 | 124.5758 | -0.050354 | 61.9217 | 124.4431 | 124.617 | -124.9329 | -124.9283
544.375 | 124.9512 | -61.7386 | 62.9425 | -0.21805 | 0.013657 | 0.014238 | 0.0056503 | 0.066652 | -0.003247 | 0.069814 | -61.7752 | 62.8555 | -62.0041 | -61.8256 | 62.7045 | 0.1831 | -0.10986 | 0.17853 | 62.851 | -61.9583 | -0.2655 | -0.086975 | -0.036622 | -0.086976 | -0.23804 | -0.21973 | -0.091553 | 0.22888 | 61.6287 | 61.9171 | 124.4431 | 124.5941 | -0.036622 | 124.5895 | 61.9217 | -0.21973 | 124.5941 | -0.036622 | 61.9217 | 124.4431 | 124.5895 | -124.9466 | -124.9008
545.375 | 124.942 | -61.7569 | 62.97 | -0.28671 | 0.010453 | 0.014238 | 0.0033005 | 0.06708 | -0.003247 | 0.068532 | -61.8027 | 62.8647 | -61.9812 | -61.8622 | 62.6633 | 0.16479 | -0.041199 | 0.13733 | 62.8601 | -61.9675 | -0.2243 | -0.10529 | -0.045776 | -0.10529 | -0.3067 | -0.21057 | -0.10986 | 0.17853 | 61.7157 | 61.8942 | 124.4202 | 124.6216 | -0.045776 | 124.617 | 61.9217 | -0.21057 | 124.6216 | -0.045776 | 61.9217 | 124.4202 | 124.617 | -124.9512 | -124.9374
546.375 | 124.91 | -61.7523 | 62.9883 | -0.24857 | 0.011093 | 0.016161 | 0.0037277 | 0.065798 | -0.0019654 | 0.067037 | -61.7752 | 62.8555 | -61.9766 | -61.8622 | 62.6862 | 0.17853 | -0.054932 | 0.14648 | 62.8693 | -61.9537 | -0.22431 | -0.13275 | -0.022889 | -0.10986 | -0.30212 | -0.20142 | -0.11902 | 0.20142 | 61.6974 | 61.8988 | 124.4385 | 124.6078 | -0.022889 | 124.6216 | 61.9308 | -0.20142 | 124.6078 | -0.022889 | 61.9308 | 124.4385 | 124.6216 | -124.9649 | -124.942
547.375 | 124.9374 | -61.7615 | 62.9654 | -0.21805 | 0.011734 | 0.011034 | 0.0056503 | 0.065584 | -0.0023926 | 0.070669 | -61.7935 | 62.8464 | -61.9812 | -61.8439 | 62.6816 | 0.17853 | -0.068665 | 0.15564 | 62.851 | -61.9537 | -0.21973 | -0.11902 | -0.032043 | -0.082397 | -0.28381 | -0.19226 | -0.11444 | 0.18768 | 61.6928 | 61.9171 | 124.4431 | 124.6078 | -0.032043 | 124.6124 | 61.94 | -0.19226 | 124.6078 | -0.032043 | 61.94 | 124.4431 | 124.6124 | -124.9466 | -124.9191
548.375 | 124.942 | -61.7523 | 62.9883 | -0.21805 | 0.011948 | 0.0099656 | 0.0060777 | 0.067934 | -0.003247 | 0.068746 | -61.7935 | 62.8601 | -61.9812 | -61.8439 | 62.6953 | 0.18768 | -0.09613 | 0.14648 | 62.8647 | -61.94 | -0.22888 | -0.12817 | -0.041199 | -0.091553 | -0.29297 | -0.18768 | -0.1236 | 0.18768 | 61.6562 | 61.8988 | 124.4476 | 124.6124 | -0.041199 | 124.617 | 61.94 | -0.18768 | 124.6124 | -0.041199 | 61.94 | 124.4476 | 124.617 | -124.9695 | -124.9283
549.375 | 124.8459 | -61.7615 | 62.9883 | -0.26382 | 0.011521 | 0.012102 | 0.0058639 | 0.066439 | -0.0026062 | 0.067464 | -61.8027 | 62.8876 | -62.0132 | -61.8942 | 62.6129 | 0.14191 | 0.027466 | 0.073242 | 62.8922 | -61.972 | -0.25177 | -0.10071 | -0.041198 | -0.13275 | -0.37537 | -0.21057 | -0.09613 | 0.21057 | 61.7889 | 61.8347 | 124.3744 | 124.649 | -0.041198 | 124.6536 | 61.9034 | -0.21057 | 124.649 | -0.041198 | 61.9034 | 124.3744 | 124.6536 | -125.0015 | -124.9603
550.375 | 124.9512 | -61.7249 | 62.9471 | -0.21805 | 0.012375 | 0.014665 | 0.0050095 | 0.065798 | -0.0019654 | 0.067251 | -61.7706 | 62.8922 | -61.9629 | -61.8393 | 62.6816 | 0.17395 | -0.09613 | 0.15106 | 62.8784 | -61.9492 | -0.23804 | -0.054932 | -0.045776 | -0.11444 | -0.2655 | -0.2243 | -0.068665 | 0.19226 | 61.6287 | 61.8759 | 124.4064 | 124.617 | -0.045776 | 124.6033 | 61.8988 | -0.2243 | 124.617 | -0.045776 | 61.8988 | 124.4064 | 124.6033 | -124.91 | -124.8962
551.375 | 124.9741 | -61.734 | 62.9562 | -0.21805 | 0.012162 | 0.011675 | 0.0047959 | 0.067293 | -0.0026062 | 0.069814 | -61.7752 | 62.8326 | -61.9949 | -61.8301 | 62.709 | 0.17853 | -0.10529 | 0.16022 | 62.8647 | -61.9629 | -0.26093 | -0.1236 | -0.041199 | -0.09613 | -0.24719 | -0.22888 | -0.091553 | 0.21973 | 61.6287 | 61.8942 | 124.4431 | 124.5667 | -0.041199 | 124.5987 | 61.9125 | -0.22888 | 124.5667 | -0.041199 | 61.9125 | 124.4431 | 124.5987 | -124.9512 | -124.9191
552.375 | 124.9191 | -61.7249 | 62.97 | -0.24857 | 0.011307 | 0.015733 | 0.0056503 | 0.066225 | -0.0015382 | 0.06896 | -61.8027 | 62.8738 | -62.0178 | -61.8759 | 62.6541 | 0.14648 | -0.013733 | 0.09613 | 62.8876 | -61.9904 | -0.29297 | -0.096131 | -0.077819 | -0.15106 | -0.31586 | -0.2655 | -0.082398 | 0.21515 | 61.7111 | 61.821 | 124.379 | 124.5987 | -0.077819 | 124.6124 | 61.8713 | -0.2655 | 124.5987 | -0.077819 | 61.8713 | 124.379 | 124.6124 | -124.9878 | -124.9603
553.375 | 124.9054 | -61.7203 | 62.9974 | -0.26382 | 0.011948 | 0.012956 | 0.0058639 | 0.068575 | -0.00068359 | 0.069173 | -61.7981 | 62.8647 | -61.9858 | -61.8576 | 62.677 | 0.16479 | -0.032043 | 0.11444 | 62.8967 | -61.9537 | -0.2655 | -0.13275 | -0.07782 | -0.13733 | -0.32043 | -0.23346 | -0.10071 | 0.18768 | 61.6882 | 61.8347 | 124.3973 | 124.585 | -0.07782 | 124.617 | 61.8851 | -0.23346 | 124.585 | -0.07782 | 61.8851 | 124.3973 | 124.617 | -124.9832 | -124.9512
554.375 | 124.9283 | -61.7249 | 62.9929 | -0.21805 | 0.011948 | 0.01317 | 0.0047959 | 0.069643 | -0.0026062 | 0.070669 | -61.7844 | 62.8647 | -61.9858 | -61.8576 | 62.677 | 0.17395 | -0.054932 | 0.11902 | 62.8555 | -61.9583 | -0.26093 | -0.12817 | -0.059509 | -0.13275 | -0.31586 | -0.23346 | -0.13733 | 0.20142 | 61.6699 | 61.8439 | 124.4019 | 124.5895 | -0.059509 | 124.5804 | 61.8988 | -0.23346 | 124.5895 | -0.059509 | 61.8988 | 124.4019 | 124.5804 | -124.9786 | -124.9512
555.375 | 124.9512 | -61.7615 | 62.9837 | -0.19516 | 0.011093 | 0.012956 | 0.0054367 | 0.067507 | -0.0023926 | 0.070241 | -61.7706 | 62.8738 | -61.9766 | -61.8668 | 62.709 | 0.1831 | -0.091553 | 0.11902 | 62.8738 | -61.9583 | -0.21515 | -0.10986 | -0.009155 | -0.10529 | -0.27466 | -0.19684 | -0.10986 | 0.20599 | 61.6699 | 61.8805 | 124.4705 | 124.6353 | -0.009155 | 124.6353 | 61.9446 | -0.19684 | 124.6353 | -0.009155 | 61.9446 | 124.4705 | 124.6353 | -124.9603 | -124.942
556.375 | 124.8459 | -61.7615 | 62.9974 | -0.27908 | 0.011734 | 0.012315 | 0.0077865 | 0.066652 | -0.002179 | 0.067891 | -61.8073 | 62.8784 | -61.9904 | -61.9217 | 62.6266 | 0.11902 | -0.009155 | 0.032043 | 62.8967 | -61.972 | -0.22888 | -0.11902 | -0.045776 | -0.16022 | -0.37079 | -0.21057 | -0.10071 | 0.1831 | 61.7523 | 61.7935 | 124.3881 | 124.6399 | -0.045776 | 124.6582 | 61.8805 | -0.21057 | 124.6399 | -0.045776 | 61.8805 | 124.3881 | 124.6582 | -124.9878 | -124.9695
557.375 | 124.9603 | -61.7294 | 62.9425 | -0.30197 | 0.012162 | 0.011247 | 0.0045823 | 0.067507 | -0.0047424 | 0.069387 | -61.7752 | 62.8464 | -61.9904 | -61.8393 | 62.6953 | 0.18768 | -0.11444 | 0.1236 | 62.8555 | -61.972 | -0.26093 | -0.09613 | -0.045777 | -0.10986 | -0.24719 | -0.24262 | -0.086975 | 0.21515 | 61.615 | 61.853 | 124.4247 | 124.5758 | -0.045777 | 124.585 | 61.9171 | -0.24262 | 124.5758 | -0.045777 | 61.9171 | 124.4247 | 124.585 | -124.9329 | -124.9146
558.375 | 125.0015 | -61.7294 | 62.9791 | -0.24857 | 0.011948 | 0.01317 | 0.0050095 | 0.068789 | -0.0015382 | 0.06896 | -61.7889 | 62.8601 | -61.9675 | -61.8256 | 62.7182 | 0.1831 | -0.13733 | 0.12817 | 62.8647 | -61.972 | -0.23804 | -0.11902 | -0.059509 | -0.096131 | -0.26093 | -0.24262 | -0.11444 | 0.17853 | 61.5921 | 61.8576 | 124.4476 | 124.5895 | -0.059509 | 124.5941 | 61.9125 | -0.24262 | 124.5895 | -0.059509 | 61.9125 | 124.4476 | 124.5941 | -124.9466 | -124.9512
559.375 | 124.91 | -61.7294 | 62.9837 | -0.24857 | 0.011521 | 0.015306 | 0.0056503 | 0.066225 | -0.0019654 | 0.068105 | -61.7798 | 62.8647 | -61.9858 | -61.8484 | 62.677 | 0.16937 | -0.07782 | 0.10529 | 62.8922 | -61.9629 | -0.25635 | -0.11902 | -0.050354 | -0.11902 | -0.3067 | -0.23346 | -0.091553 | 0.20599 | 61.6516 | 61.8347 | 124.4064 | 124.5941 | -0.050354 | 124.6216 | 61.8988 | -0.23346 | 124.5941 | -0.050354 | 61.8988 | 124.4064 | 124.6216 | -124.9695 | -124.9466
560.375 | 124.9741 | -61.7203 | 62.9837 | -0.24857 | 0.012162 | 0.0084702 | 0.0052231 | 0.06708 | -0.0023926 | 0.070241 | -61.7661 | 62.8418 | -61.972 | -61.8439 | 62.6953 | 0.1831 | -0.091553 | 0.10986 | 62.8693 | -61.9446 | -0.25177 | -0.14191 | -0.045776 | -0.1236 | -0.28839 | -0.2243 | -0.11444 | 0.20599 | 61.6287 | 61.8301 | 124.4156 | 124.5621 | -0.045776 | 124.5895 | 61.9034 | -0.2243 | 124.5621 | -0.045776 | 61.9034 | 124.4156 | 124.5895 | -124.9557 | -124.9283
561.375 | 124.9786 | -61.702 | 62.9745 | -0.21805 | 0.011093 | 0.011461 | 0.0033005 | 0.067293 | -0.0015382 | 0.067464 | -61.7615 | 62.8326 | -61.9904 | -61.8393 | 62.7045 | 0.19226 | -0.11902 | 0.10986 | 62.883 | -61.9446 | -0.28839 | -0.14191 | -0.05951 | -0.13733 | -0.27008 | -0.24262 | -0.091552 | 0.22888 | 61.5829 | 61.8118 | 124.4064 | 124.5346 | -0.05951 | 124.585 | 61.8942 | -0.24262 | 124.5346 | -0.05951 | 61.8942 | 124.4064 | 124.585 | -124.9649 | -124.9191
562.375 | 124.9603 | -61.7157 | 62.9837 | -0.20279 | 0.011948 | 0.012102 | 0.0037277 | 0.066652 | -0.0017518 | 0.068105 | -61.7706 | 62.8601 | -61.9858 | -61.821 | 62.7136 | 0.19684 | -0.12817 | 0.11902 | 62.8647 | -61.9492 | -0.27008 | -0.1236 | -0.054932 | -0.10529 | -0.27008 | -0.23346 | -0.11902 | 0.21515 | 61.5875 | 61.8347 | 124.4293 | 124.5758 | -0.054932 | 124.5804 | 61.9125 | -0.23346 | 124.5758 | -0.054932 | 61.9125 | 124.4293 | 124.5804 | -124.9695 | -124.9329
563.375 | 124.9741 | -61.7111 | 62.9791 | -0.2562 | 0.012802 | 0.01317 | 0.0041549 | 0.066652 | -0.003247 | 0.069387 | -61.7935 | 62.8555 | -61.9949 | -61.8439 | 62.6907 | 0.16479 | -0.073242 | 0.086975 | 62.8876 | -61.9766 | -0.28381 | -0.1236 | -0.082397 | -0.13275 | -0.28839 | -0.2655 | -0.091553 | 0.20142 | 61.6379 | 61.7981 | 124.4019 | 124.5667 | -0.082397 | 124.5987 | 61.8759 | -0.2655 | 124.5667 | -0.082397 | 61.8759 | 124.4019 | 124.5987 | -124.9741 | -124.9557
564.375 | 124.9786 | -61.6882 | 62.97 | 0.9874 | 0.013657 | 0.012743 | 0.0022323 | 0.066866 | -0.0015382 | 0.070241 | -61.7935 | 62.8235 | -62.0178 | -61.8301 | 62.7045 | 0.20599 | -0.14648 | 0.11902 | 62.8693 | -61.9537 | -0.32959 | -0.14648 | -0.10529 | -0.14191 | -0.2655 | -0.2655 | -0.10071 | 0.2243 | 61.5417 | 61.8073 | 124.3927 | 124.5117 | -0.10529 | 124.5575 | 61.8942 | -0.2655 | 124.5117 | -0.10529 | 61.8942 | 124.3927 | 124.5575 | -124.9878 | -124.9237
565.375 | 124.9741 | -61.7294 | 62.9517 | -0.13412 | 0.014298 | 0.012956 | 0.0030869 | 0.064944 | -0.00068359 | 0.06661 | -61.7569 | 62.8693 | -61.9675 | -61.5555 | 62.4847 | -0.045776 | -0.082397 | -0.032043 | 62.8235 | -61.94 | -0.23804 | -0.082397 | -0.027466 | 0.17395 | -0.46692 | -0.21057 | -0.12817 | 0.21057 | 61.647 | 61.6974 | 124.2142 | 124.5987 | -0.027466 | 124.5529 | 61.6837 | -0.21057 | 124.5987 | -0.027466 | 61.6837 | 124.2142 | 124.5529 | -124.9191 | -124.8917
566.375 | 124.9374 | -61.7294 | 62.9929 | -0.24857 | 0.011093 | 0.011888 | 0.0050095 | 0.066439 | -0.0015382 | 0.068105 | -61.7752 | 62.8601 | -61.972 | -61.8484 | 62.6633 | 0.17395 | -0.054932 | 0.068665 | 62.8876 | -61.972 | -0.24262 | -0.13275 | -0.045777 | -0.11902 | -0.32959 | -0.24262 | -0.10529 | 0.19684 | 61.6745 | 61.7981 | 124.3927 | 124.5895 | -0.045777 | 124.617 | 61.9034 | -0.24262 | 124.5895 | -0.045777 | 61.9034 | 124.3927 | 124.617 | -124.9649 | -124.9649
567.375 | 124.9969 | -61.6974 | 62.97 | -0.11124 | 0.0089572 | 0.011675 | 0.0030869 | 0.066225 | -0.0015382 | 0.068532 | -61.7935 | 62.8372 | -61.9766 | -61.821 | 62.7182 | 0.19226 | -0.16479 | 0.10071 | 62.8647 | -61.9583 | -0.27924 | -0.13275 | -0.09613 | -0.1236 | -0.25177 | -0.26093 | -0.10529 | 0.18311 | 61.5326 | 61.7981 | 124.4156 | 124.5346 | -0.09613 | 124.5621 | 61.8896 | -0.26093 | 124.5346 | -0.09613 | 61.8896 | 124.4156 | 124.5621 | -124.9466 | -124.9283
568.375 | 124.9466 | -61.7157 | 62.9745 | -0.1799 | 0.011948 | 0.0086838 | 0.0062913 | 0.066225 | -0.0015382 | 0.069173 | -61.7615 | 62.8693 | -61.94 | -61.8576 | 62.764 | 0.18768 | -0.1831 | 0.082397 | 62.8647 | -61.9492 | -0.2243 | -0.10529 | -0.045777 | -0.14191 | -0.21057 | -0.23346 | -0.10986 | 0.17853 | 61.5326 | 61.7981 | 124.4797 | 124.585 | -0.045777 | 124.5804 | 61.9034 | -0.23346 | 124.585 | -0.045777 | 61.9034 | 124.4797 | 124.5804 | -124.9145 | -124.9237
569.375 | 124.9695 | -61.7249 | 62.9654 | -0.21805 | 0.0091708 | 0.01082 | 0.0056503 | 0.066439 | -0.002179 | 0.068746 | -61.7523 | 62.851 | -61.9812 | -61.8164 | 62.709 | 0.19226 | -0.12817 | 0.073242 | 62.8647 | -61.9217 | -0.25635 | -0.11444 | -0.027465 | -0.091552 | -0.25635 | -0.19684 | -0.10071 | 0.22888 | 61.5967 | 61.7981 | 124.4339 | 124.5758 | -0.027465 | 124.5895 | 61.9171 | -0.19684 | 124.5758 | -0.027465 | 61.9171 | 124.4339 | 124.5895 | -124.9466 | -124.8871
570.375 | 124.9878 | -61.734 | 62.9929 | -0.26382 | 0.011734 | 0.011247 | 0.0043687 | 0.068575 | -0.0017518 | 0.071096 | -61.7706 | 62.8418 | -61.9675 | -61.821 | 62.7045 | 0.19684 | -0.14648 | 0.10071 | 62.851 | -61.9446 | -0.23346 | -0.15106 | -0.036621 | -0.086975 | -0.28839 | -0.21057 | -0.14191 | 0.19684 | 61.5875 | 61.8347 | 124.4385 | 124.5758 | -0.036621 | 124.585 | 61.9308 | -0.21057 | 124.5758 | -0.036621 | 61.9308 | 124.4385 | 124.585 | -124.9603 | -124.9374
571.3906 | 124.8184 | -61.7569 | 62.9745 | 0.079498 | 0.017716 | 0.016374 | 0.0080003 | 0.066652 | -0.0023926 | 0.069814 | -61.8164 | 62.9288 | -61.9904 | -61.9217 | 62.5671 | 0.022888 | -0.082397 | -0.1236 | 62.9013 | -62.0132 | -0.23346 | -0.045776 | -0.059509 | -0.16479 | -0.40741 | -0.25635 | -0.073242 | 0.17395 | 61.6745 | 61.6333 | 124.324 | 124.6857 | -0.059509 | 124.6582 | 61.7798 | -0.25635 | 124.6857 | -0.059509 | 61.7798 | 124.324 | 124.6582 | -124.9649 | -124.9878
572.375 | 124.9786 | -61.734 | 62.9333 | -0.24857 | 0.012589 | 0.0095382 | 0.0041549 | 0.069002 | -0.0017518 | 0.068532 | -61.9812 | 62.8464 | -61.972 | -61.9308 | 62.6678 | 0.2243 | -0.18768 | 0.064087 | 62.8876 | -61.9125 | -0.23804 | -0.086975 | -0.24719 | -0.19684 | -0.2655 | -0.17853 | -0.045777 | -0.009155 | 61.5463 | 61.7981 | 124.4019 | 124.5804 | -0.24719 | 124.6216 | 61.9583 | -0.17853 | 124.5804 | -0.24719 | 61.9583 | 124.4019 | 124.6216 | -124.9054 | -124.8459
573.375 | 125.0519 | -61.7203 | 62.9471 | -0.11887 | 0.011093 | 0.011888 | 0.00052347 | 0.066439 | -0.0041016 | 0.06896 | -61.7752 | 62.8326 | -61.9995 | -61.8027 | 62.7182 | 0.07782 | 0.2243 | 0.10529 | 62.9242 | -61.8896 | -0.27924 | -0.11444 | -0.054932 | -0.082397 | -0.22888 | -0.16937 | -0.022889 | 0.2243 | 61.9446 | 61.8256 | 124.4385 | 124.5529 | -0.054932 | 124.6445 | 61.7981 | -0.16937 | 124.5529 | -0.054932 | 61.7981 | 124.4385 | 124.6445 | -124.9466 | -124.8367
574.375 | 124.9832 | -61.7157 | 62.9654 | -0.10361 | 0.011948 | 0.014879 | 0.0018051 | 0.063662 | -0.0019654 | 0.069814 | -61.7798 | 62.8372 | -61.9949 | -61.8118 | 62.7365 | 0.1831 | -0.20599 | 0.059509 | 62.8647 | -61.94 | -0.27924 | -0.12817 | -0.064087 | -0.096131 | -0.22888 | -0.2243 | -0.10071 | 0.21515 | 61.5097 | 61.7752 | 124.4522 | 124.5529 | -0.064087 | 124.5804 | 61.8988 | -0.2243 | 124.5529 | -0.064087 | 61.8988 | 124.4522 | 124.5804 | -124.9603 | -124.9054
575.375 | 124.9741 | -61.7157 | 62.9608 | -0.14938 | 0.012375 | 0.013597 | 0.0018051 | 0.064303 | -0.0017518 | 0.069173 | -61.7889 | 62.8418 | -61.9858 | -61.853 | 62.6999 | 0.16479 | -0.1831 | 0.032043 | 62.8738 | -61.9354 | -0.27008 | -0.11902 | -0.073242 | -0.13733 | -0.26092 | -0.21973 | -0.086975 | 0.19684 | 61.5326 | 61.7477 | 124.4156 | 124.5575 | -0.073242 | 124.5895 | 61.8805 | -0.21973 | 124.5575 | -0.073242 | 61.8805 | 124.4156 | 124.5895 | -124.9466 | -124.8962
576.3906 | 124.8917 | -61.7661 | 62.9471 | 0.16342 | 0.013657 | 0.017015 | 0.0092819 | 0.06708 | -0.00068359 | 0.070241 | -61.8164 | 62.9013 | -62.0224 | -61.8988 | 62.6083 | 0.036621 | -0.23346 | -0.16479 | 62.8601 | -62.0361 | -0.25635 | -0.045777 | -0.050354 | -0.13275 | -0.33875 | -0.27008 | -0.086976 | 0.20599 | 61.5326 | 61.6013 | 124.3744 | 124.6674 | -0.050354 | 124.6262 | 61.8027 | -0.27008 | 124.6674 | -0.050354 | 61.8027 | 124.3744 | 124.6262 | -124.9695 | -124.9832
577.4062 | 124.8688 | -61.7569 | 62.9837 | -0.24094 | 0.013657 | 0.012743 | 0.0069321 | 0.067934 | -0.00068359 | 0.068319 | -61.8301 | 62.9288 | -62.0132 | -61.8988 | 62.6266 | 0.10071 | 0 | -0.07782 | 62.9242 | -61.94 | -0.25635 | -0.054932 | -0.073242 | -0.14191 | -0.35706 | -0.1831 | -0.05951 | 0.18311 | 61.7569 | 61.6791 | 124.3835 | 124.6857 | -0.073242 | 124.6811 | 61.8576 | -0.1831 | 124.6857 | -0.073242 | 61.8576 | 124.3835 | 124.6811 | -124.9969 | -124.9237
578.3906 | 124.9054 | -61.7157 | 62.9333 | 0.094757 | 0.012375 | 0.012743 | 0.0033005 | 0.068361 | 0.00038461 | 0.0696 | -61.7889 | 62.8372 | -61.9995 | -61.8896 | 62.6495 | 0.09613 | -0.28839 | -0.082397 | 62.8098 | -61.9766 | -0.28381 | -0.096131 | -0.073242 | -0.17395 | -0.28381 | -0.26093 | -0.1236 | 0.21057 | 61.4273 | 61.6333 | 124.3652 | 124.5529 | -0.073242 | 124.5255 | 61.8118 | -0.26093 | 124.5529 | -0.073242 | 61.8118 | 124.3652 | 124.5255 | -124.9329 | -124.91
579.4062 | 124.8138 | -61.7615 | 62.9929 | 0.0032044 | 0.01622 | 0.019579 | 0.010136 | 0.071139 | -0.0036744 | 0.068319 | -61.8256 | 62.9562 | -61.9904 | -61.9446 | 62.5854 | 0.036621 | -0.11444 | -0.20142 | 62.9333 | -62.0087 | -0.22888 | -0.036621 | -0.064087 | -0.18311 | -0.40741 | -0.24719 | -0.059509 | 0.16479 | 61.647 | 61.5601 | 124.3469 | 124.7177 | -0.064087 | 124.6948 | 61.7981 | -0.24719 | 124.7177 | -0.064087 | 61.7981 | 124.3469 | 124.6948 | -124.9832 | -125.0015
580.4219 | 124.8505 | -61.7523 | 62.9791 | -0.0044251 | 0.016434 | 0.019365 | 0.0077865 | 0.071352 | -0.003247 | 0.070669 | -61.7981 | 62.9105 | -62.0041 | -61.908 | 62.59 | 0.073242 | -0.11902 | -0.13275 | 62.9333 | -61.9583 | -0.25177 | -0.068665 | -0.045777 | -0.15564 | -0.3891 | -0.20599 | -0.045776 | 0.20599 | 61.6333 | 61.6196 | 124.3423 | 124.6628 | -0.045777 | 124.6857 | 61.8256 | -0.20599 | 124.6628 | -0.045777 | 61.8256 | 124.3423 | 124.6857 | -124.9832 | -124.9374
581.3906 | 124.8688 | -61.7661 | 62.9425 | -0.012055 | 0.014511 | 0.017229 | 0.0077865 | 0.071993 | -0.003888 | 0.068746 | -61.7889 | 62.9517 | -61.9812 | -61.9171 | 62.5946 | 0.045776 | -0.11902 | -0.16937 | 62.9242 | -61.9904 | -0.21515 | 0.009155 | -0.022888 | -0.15106 | -0.3479 | -0.2243 | -0.018311 | 0.19226 | 61.647 | 61.5967 | 124.3607 | 124.7177 | -0.022888 | 124.6902 | 61.8118 | -0.2243 | 124.7177 | -0.022888 | 61.8118 | 124.3607 | 124.6902 | -124.9237 | -124.9329
582.375 | 124.9695 | -61.7203 | 62.9562 | -0.042572 | 0.011093 | 0.012743 | -0.0026809 | 0.067934 | -0.002179 | 0.071523 | -61.821 | 62.8693 | -61.9904 | -61.8622 | 62.6862 | 0.16937 | -0.19226 | -0.045776 | 62.8693 | -61.9446 | -0.27008 | -0.086975 | -0.10071 | -0.14191 | -0.27008 | -0.2243 | -0.086975 | 0.16937 | 61.528 | 61.6745 | 124.4064 | 124.5895 | -0.10071 | 124.5895 | 61.8896 | -0.2243 | 124.5895 | -0.10071 | 61.8896 | 124.4064 | 124.5895 | -124.9466 | -124.9008
583.375 | 124.8779 | -61.734 | 62.97 | -0.1265 | 0.01558 | 0.013383 | 0.0088547 | 0.070284 | -0.0030334 | 0.069387 | -61.7889 | 62.9471 | -61.9949 | -61.8896 | 62.6221 | 0.13275 | -0.073242 | -0.086975 | 62.915 | -61.9995 | -0.26093 | -0.022888 | -0.054931 | -0.15564 | -0.3479 | -0.2655 | -0.054932 | 0.20599 | 61.6608 | 61.647 | 124.3561 | 124.6811 | -0.054931 | 124.649 | 61.8668 | -0.2655 | 124.6811 | -0.054931 | 61.8668 | 124.3561 | 124.649 | -124.9649 | -124.9695
584.375 | 124.9237 | -61.734 | 62.9379 | -0.06546 | 0.011093 | 0.014238 | -0.0024673 | 0.068361 | -0.0023926 | 0.068319 | -61.8301 | 62.8601 | -62.0041 | -61.9034 | 62.6678 | 0.15106 | -0.20142 | -0.082397 | 62.8922 | -61.94 | -0.27008 | -0.07782 | -0.09613 | -0.16937 | -0.27008 | -0.20599 | -0.045776 | 0.17395 | 61.5326 | 61.6516 | 124.4019 | 124.5941 | -0.09613 | 124.6262 | 61.8851 | -0.20599 | 124.5941 | -0.09613 | 61.8851 | 124.4019 | 124.6262 | -124.942 | -124.8779
585.375 | 124.9557 | -61.7477 | 62.9425 | 0.087128 | 0.01088 | 0.012956 | 0.0020187 | 0.062166 | -0.0053834 | 0.071523 | -61.8347 | 62.8326 | -61.9766 | -61.9858 | 62.645 | 0.16022 | -0.29755 | -0.1236 | 62.8647 | -61.972 | -0.22888 | -0.10986 | -0.086975 | -0.23804 | -0.29755 | -0.2243 | -0.07782 | 0.14191 | 61.4502 | 61.6241 | 124.3927 | 124.5804 | -0.086975 | 124.6124 | 61.908 | -0.2243 | 124.5804 | -0.086975 | 61.908 | 124.3927 | 124.6124 | -124.9191 | -124.9146
586.375 | 124.9008 | -61.7249 | 62.97 | -0.012055 | 0.012162 | 0.0093246 | 0.0015915 | 0.065584 | -0.0028198 | 0.069387 | -61.8164 | 62.851 | -61.9766 | -61.908 | 62.6358 | 0.10986 | -0.18768 | -0.10986 | 62.8738 | -61.9171 | -0.25177 | -0.11902 | -0.091552 | -0.1831 | -0.33417 | -0.19226 | -0.096131 | 0.16022 | 61.5372 | 61.615 | 124.3607 | 124.5758 | -0.091552 | 124.5987 | 61.8347 | -0.19226 | 124.5758 | -0.091552 | 61.8347 | 124.3607 | 124.5987 | -124.9466 | -124.8871
587.375 | 124.9466 | -61.7203 | 62.9654 | -0.080719 | 0.0098118 | 0.014452 | 0.0024461 | 0.06708 | -0.0034608 | 0.069173 | -61.821 | 62.8281 | -61.9812 | -61.9034 | 62.6358 | 0.091553 | -0.19684 | -0.12817 | 62.9059 | -61.9446 | -0.26093 | -0.13733 | -0.10071 | -0.18311 | -0.32959 | -0.2243 | -0.059509 | 0.16022 | 61.5234 | 61.5921 | 124.3561 | 124.5483 | -0.10071 | 124.6262 | 61.8118 | -0.2243 | 124.5483 | -0.10071 | 61.8118 | 124.3561 | 124.6262 | -124.9466 | -124.91
588.375 | 124.91 | -61.7294 | 62.9471 | -0.080719 | 0.011307 | 0.015092 | 0.0043687 | 0.067721 | -0.002179 | 0.070669 | -61.8439 | 62.8372 | -61.9949 | -61.8942 | 62.6221 | 0.09613 | -0.1831 | -0.14648 | 62.915 | -61.9583 | -0.2655 | -0.10986 | -0.11444 | -0.1648 | -0.32501 | -0.22888 | -0.032044 | 0.15106 | 61.5463 | 61.5829 | 124.3515 | 124.5666 | -0.11444 | 124.6445 | 61.8256 | -0.22888 | 124.5666 | -0.11444 | 61.8256 | 124.3515 | 124.6445 | -124.942 | -124.9054
589.375 | 124.9557 | -61.7203 | 62.9654 | -0.034943 | 0.011307 | 0.013597 | 0.0043687 | 0.065584 | -0.0053834 | 0.068319 | -61.8118 | 62.8326 | -61.9904 | -61.8851 | 62.645 | 0.1236 | -0.19226 | -0.11444 | 62.8784 | -61.9217 | -0.27008 | -0.13275 | -0.091553 | -0.1648 | -0.32043 | -0.20142 | -0.086975 | 0.17853 | 61.528 | 61.6058 | 124.3652 | 124.5529 | -0.091553 | 124.5987 | 61.8439 | -0.20142 | 124.5529 | -0.091553 | 61.8439 | 124.3652 | 124.5987 | -124.9557 | -124.8871
590.375 | 124.9557 | -61.7203 | 62.9791 | -0.080719 | 0.011521 | 0.010179 | 0.0039413 | 0.066225 | -0.0047424 | 0.068319 | -61.8073 | 62.8464 | -61.9766 | -61.8713 | 62.6495 | 0.11902 | -0.19226 | -0.15106 | 62.9288 | -61.9308 | -0.25635 | -0.13275 | -0.086975 | -0.15106 | -0.32959 | -0.21057 | -0.050354 | 0.16937 | 61.528 | 61.5692 | 124.3698 | 124.5667 | -0.086975 | 124.649 | 61.8393 | -0.21057 | 124.5667 | -0.086975 | 61.8393 | 124.3698 | 124.649 | -124.9557 | -124.91
591.375 | 124.9557 | -61.7065 | 62.9745 | -0.13412 | 0.0093844 | 0.012102 | 0.0039413 | 0.065371 | -0.003247 | 0.06896 | -61.7752 | 62.8693 | -61.9904 | -61.8439 | 62.6724 | 0.16022 | -0.21515 | -0.086975 | 62.8738 | -61.9446 | -0.28381 | -0.10529 | -0.068665 | -0.13733 | -0.30212 | -0.23804 | -0.10071 | 0.21515 | 61.4914 | 61.6196 | 124.379 | 124.5758 | -0.068665 | 124.5804 | 61.8668 | -0.23804 | 124.5758 | -0.068665 | 61.8668 | 124.379 | 124.5804 | -124.9649 | -124.9191
592.375 | 124.9329 | -61.702 | 62.9745 | 0.026092 | 0.010666 | 0.012102 | 0.0024461 | 0.065798 | -0.0017518 | 0.070455 | -61.821 | 62.8235 | -61.9904 | -61.8988 | 62.6312 | 0.086975 | -0.19226 | -0.15564 | 62.883 | -61.9537 | -0.28839 | -0.15106 | -0.11902 | -0.19684 | -0.34332 | -0.25177 | -0.091552 | 0.16937 | 61.5097 | 61.5463 | 124.3332 | 124.5255 | -0.11902 | 124.585 | 61.7889 | -0.25177 | 124.5255 | -0.11902 | 61.7889 | 124.3332 | 124.585 | -124.9649 | -124.9283
593.375 | 124.9329 | -61.7203 | 62.9791 | 0.19394 | 0.0095982 | 0.010179 | 0.0030869 | 0.065798 | -0.00046999 | 0.070028 | -61.8164 | 62.8143 | -61.9995 | -61.8805 | 62.6358 | 0.10071 | -0.21515 | -0.17395 | 62.8738 | -61.9446 | -0.27924 | -0.16479 | -0.09613 | -0.16022 | -0.34332 | -0.2243 | -0.10529 | 0.18311 | 61.5051 | 61.5463 | 124.3561 | 124.5346 | -0.09613 | 124.5941 | 61.821 | -0.2243 | 124.5346 | -0.09613 | 61.821 | 124.3561 | 124.5941 | -124.9786 | -124.9237
594.375 | 124.9237 | -61.702 | 62.9745 | -0.034943 | 0.012162 | 0.011888 | 0.0030869 | 0.066439 | -0.0015382 | 0.068746 | -61.7889 | 62.8555 | -61.9583 | -61.8347 | 62.6495 | 0.10986 | -0.22888 | -0.15106 | 62.8967 | -61.94 | -0.25635 | -0.11902 | -0.086975 | -0.13275 | -0.32501 | -0.23804 | -0.077819 | 0.16937 | 61.4731 | 61.5509 | 124.3515 | 124.5575 | -0.086975 | 124.5987 | 61.8118 | -0.23804 | 124.5575 | -0.086975 | 61.8118 | 124.3515 | 124.5987 | -124.9329 | -124.9145
595.375 | 124.9329 | -61.6974 | 62.9883 | -0.06546 | 0.011307 | 0.011675 | 0.0039413 | 0.065798 | -0.002179 | 0.069387 | -61.8027 | 62.851 | -61.9812 | -61.8622 | 62.6541 | 0.1236 | -0.22888 | -0.15564 | 62.8922 | -61.9446 | -0.28381 | -0.13733 | -0.10529 | -0.1648 | -0.33417 | -0.24719 | -0.09613 | 0.17853 | 61.4685 | 61.5417 | 124.3515 | 124.5483 | -0.10529 | 124.5895 | 61.821 | -0.24719 | 124.5483 | -0.10529 | 61.821 | 124.3515 | 124.5895 | -124.9695 | -124.9329
596.375 | 124.9741 | -61.6882 | 62.97 | -0.027313 | 0.011734 | 0.01787 | 0.0018051 | 0.068575 | -0.0026062 | 0.06896 | -61.8118 | 62.8281 | -61.9675 | -61.8622 | 62.6633 | 0.11444 | -0.21515 | -0.18768 | 62.8876 | -61.94 | -0.27924 | -0.14191 | -0.1236 | -0.17395 | -0.3067 | -0.25177 | -0.082398 | 0.15564 | 61.4731 | 61.5005 | 124.3515 | 124.5163 | -0.1236 | 124.5758 | 61.8027 | -0.25177 | 124.5163 | -0.1236 | 61.8027 | 124.3515 | 124.5758 | -124.9374 | -124.91
597.375 | 124.9008 | -61.6974 | 62.97 | 0.0032044 | 0.011307 | 0.014879 | 0.00095067 | 0.067293 | -0.0011108 | 0.06896 | -61.8073 | 62.8281 | -61.9766 | -61.8484 | 62.645 | 0.10986 | -0.21515 | -0.18768 | 62.9196 | -61.9308 | -0.27924 | -0.14191 | -0.10986 | -0.15106 | -0.32501 | -0.23346 | -0.050354 | 0.16937 | 61.4822 | 61.5097 | 124.3423 | 124.5255 | -0.10986 | 124.617 | 61.8073 | -0.23346 | 124.5255 | -0.10986 | 61.8073 | 124.3423 | 124.617 | -124.9466 | -124.9008
598.375 | 125.0061 | -61.6974 | 62.9608 | -0.080719 | 0.010453 | 0.0067612 | 0.0033005 | 0.068361 | -0.0015382 | 0.070241 | -61.7569 | 62.8281 | -61.9446 | -61.8164 | 62.6953 | 0.16937 | -0.23346 | -0.12817 | 62.915 | -61.8988 | -0.24719 | -0.13275 | -0.059509 | -0.11902 | -0.2655 | -0.20142 | -0.045776 | 0.18768 | 61.4639 | 61.5692 | 124.3927 | 124.5255 | -0.059509 | 124.6124 | 61.8668 | -0.20142 | 124.5255 | -0.059509 | 61.8668 | 124.3927 | 124.6124 | -124.9054 | -124.8596
599.375 | 124.942 | -61.6882 | 62.9745 | -0.057831 | 0.0087436 | 0.017015 | 0.0024461 | 0.066652 | -0.0023926 | 0.068746 | -61.8027 | 62.8326 | -61.9858 | -61.8576 | 62.6678 | 0.10986 | -0.23346 | -0.21057 | 62.8647 | -61.9537 | -0.29755 | -0.14191 | -0.11444 | -0.16937 | -0.3067 | -0.2655 | -0.10986 | 0.18311 | 61.4548 | 61.4777 | 124.3561 | 124.5209 | -0.11444 | 124.5529 | 61.7981 | -0.2655 | 124.5209 | -0.11444 | 61.7981 | 124.3561 | 124.5529 | -124.9603 | -124.9283
600.375 | 124.9008 | -61.7249 | 62.9791 | -0.027313 | 0.011307 | 0.011034 | 0.0033005 | 0.067934 | -0.0015382 | 0.06661 | -61.8164 | 62.8281 | -61.9812 | -61.8759 | 62.6541 | 0.1236 | -0.22888 | -0.21973 | 62.8738 | -61.94 | -0.25635 | -0.15106 | -0.091552 | -0.15106 | -0.32501 | -0.21515 | -0.10529 | 0.16479 | 61.496 | 61.5051 | 124.379 | 124.5529 | -0.091552 | 124.5987 | 61.8484 | -0.21515 | 124.5529 | -0.091552 | 61.8484 | 124.379 | 124.5987 | -124.9603 | -124.9191
601.375 | 124.9878 | -61.6837 | 62.9608 | -0.057831 | 0.0091708 | 0.014238 | 0.0022323 | 0.068361 | -4.2788e-05 | 0.069173 | -61.7661 | 62.851 | -61.9354 | -61.8027 | 62.6953 | 0.16479 | -0.23346 | -0.15564 | 62.915 | -61.9125 | -0.25177 | -0.10986 | -0.082397 | -0.11902 | -0.2655 | -0.22888 | -0.045776 | 0.16937 | 61.4502 | 61.528 | 124.379 | 124.5346 | -0.082397 | 124.5987 | 61.8484 | -0.22888 | 124.5346 | -0.082397 | 61.8484 | 124.379 | 124.5987 | -124.8962 | -124.8734
602.375 | 124.9603 | -61.6882 | 62.9654 | -0.080719 | 0.012375 | 0.012529 | 0.0011643 | 0.066652 | -0.0023926 | 0.067251 | -61.7615 | 62.8464 | -61.9217 | -61.8027 | 62.6907 | 0.16937 | -0.25635 | -0.16479 | 62.883 | -61.8942 | -0.23346 | -0.11902 | -0.073243 | -0.11444 | -0.27466 | -0.20599 | -0.082397 | 0.16022 | 61.4319 | 61.5234 | 124.379 | 124.5346 | -0.073243 | 124.5712 | 61.8576 | -0.20599 | 124.5346 | -0.073243 | 61.8576 | 124.379 | 124.5712 | -124.8871 | -124.8596
603.375 | 124.9557 | -61.6837 | 62.9425 | -0.07309 | 0.01088 | 0.011675 | 0.0024461 | 0.066225 | -0.0013244 | 0.068532 | -61.7523 | 62.8281 | -61.9446 | -61.8073 | 62.6862 | 0.16479 | -0.24261 | -0.1831 | 62.8876 | -61.8896 | -0.26093 | -0.11444 | -0.068664 | -0.1236 | -0.25635 | -0.20599 | -0.054932 | 0.19226 | 61.441 | 61.5006 | 124.3698 | 124.5117 | -0.068664 | 124.5712 | 61.8484 | -0.20599 | 124.5117 | -0.068664 | 61.8484 | 124.3698 | 124.5712 | -124.8871 | -124.8322
604.375 | 124.9786 | -61.6928 | 62.9654 | -0.088349 | 0.011307 | 0.011461 | 0.0024461 | 0.066225 | -0.002179 | 0.06896 | -61.7477 | 62.851 | -61.94 | -61.8027 | 62.7045 | 0.17395 | -0.25635 | -0.18768 | 62.8738 | -61.9125 | -0.24719 | -0.11444 | -0.054932 | -0.10986 | -0.26093 | -0.21973 | -0.091553 | 0.19226 | 61.4365 | 61.5051 | 124.3973 | 124.5438 | -0.054932 | 124.5667 | 61.8668 | -0.21973 | 124.5438 | -0.054932 | 61.8668 | 124.3973 | 124.5667 | -124.9054 | -124.8779
605.375 | 124.9832 | -61.6928 | 62.9837 | -0.96573 | 0.012375 | 0.01317 | 0.0054367 | 0.068361 | -0.003247 | 0.069387 | -61.8347 | 62.8098 | -61.9492 | -61.7615 | 62.7365 | 0.21973 | -0.20599 | -0.15106 | 62.915 | -61.8988 | -0.25635 | -0.17395 | -0.14191 | -0.068665 | -0.24719 | -0.20599 | -0.068665 | 0.11444 | 61.4868 | 61.5417 | 124.4293 | 124.5026 | -0.14191 | 124.6078 | 61.9125 | -0.20599 | 124.5026 | -0.14191 | 61.9125 | 124.4293 | 124.6078 | -124.9329 | -124.8825
606.375 | 124.9512 | -61.702 | 62.9745 | -0.095978 | 0.0089572 | 0.016161 | 0.0026597 | 0.067507 | -0.0028198 | 0.069173 | -61.7386 | 62.8555 | -61.9629 | -61.7889 | 62.7136 | 0.16937 | -0.24719 | -0.1831 | 62.8693 | -61.9125 | -0.26093 | -0.11902 | -0.036621 | -0.086975 | -0.26093 | -0.21057 | -0.10529 | 0.22431 | 61.4548 | 61.5189 | 124.4156 | 124.5575 | -0.036621 | 124.5712 | 61.8713 | -0.21057 | 124.5575 | -0.036621 | 61.8713 | 124.4156 | 124.5712 | -124.9374 | -124.8871
607.375 | 124.9832 | -61.6653 | 62.9974 | 0.14816 | 0.010666 | 0.0065476 | 0.0030869 | 0.065584 | -0.00089719 | 0.068319 | -61.7111 | 62.851 | -61.9583 | -61.7752 | 62.7182 | 0.20599 | -0.2243 | -0.16937 | 62.8738 | -61.9217 | -0.29297 | -0.14648 | -0.045777 | -0.10986 | -0.27924 | -0.25635 | -0.1236 | 0.24719 | 61.441 | 61.496 | 124.3835 | 124.5163 | -0.045777 | 124.5392 | 61.8713 | -0.25635 | 124.5163 | -0.045777 | 61.8713 | 124.3835 | 124.5392 | -124.9557 | -124.9191
608.375 | 124.9695 | -61.6608 | 63.0066 | 0.11765 | 0.012375 | 0.0093246 | 0.0035141 | 0.065584 | -0.0034608 | 0.067891 | -61.6974 | 62.8601 | -61.9583 | -61.7798 | 62.7319 | 0.21057 | -0.23804 | -0.16937 | 62.8738 | -61.908 | -0.29755 | -0.14648 | -0.036621 | -0.11902 | -0.27466 | -0.24719 | -0.13275 | 0.26093 | 61.4227 | 61.4914 | 124.3927 | 124.5209 | -0.036621 | 124.5346 | 61.8713 | -0.24719 | 124.5209 | -0.036621 | 61.8713 | 124.3927 | 124.5346 | -124.9649 | -124.9146
609.375 | 124.942 | -61.6608 | 62.9883 | -0.22568 | 0.011948 | 0.015733 | 0.0037277 | 0.065371 | -0.0030334 | 0.06896 | -61.7111 | 62.8418 | -61.9492 | -61.7661 | 62.7182 | 0.21973 | -0.23346 | -0.18768 | 62.9013 | -61.9034 | -0.28839 | -0.14648 | -0.050354 | -0.10529 | -0.27008 | -0.24261 | -0.086975 | 0.23804 | 61.4273 | 61.4731 | 124.379 | 124.5026 | -0.050354 | 124.5621 | 61.8805 | -0.24261 | 124.5026 | -0.050354 | 61.8805 | 124.379 | 124.5621 | -124.9374 | -124.8917
610.375 | 124.9878 | -61.6608 | 62.9837 | -0.28671 | 0.010025 | 0.010179 | 0.0028733 | 0.066439 | -0.003247 | 0.069387 | -61.7157 | 62.8738 | -61.9537 | -61.7661 | 62.7228 | 0.21973 | -0.2243 | -0.19226 | 62.9013 | -61.8896 | -0.29297 | -0.10986 | -0.054931 | -0.10529 | -0.26093 | -0.22888 | -0.082398 | 0.23804 | 61.4365 | 61.4685 | 124.3835 | 124.5346 | -0.054931 | 124.5621 | 61.8805 | -0.22888 | 124.5346 | -0.054931 | 61.8805 | 124.3835 | 124.5621 | -124.9374 | -124.8734
611.375 | 124.8962 | -61.6974 | 62.9974 | -0.24857 | 0.01088 | 0.013811 | 0.0030869 | 0.066866 | -0.002179 | 0.06896 | -61.7432 | 62.8647 | -61.9537 | -61.8027 | 62.6862 | 0.19226 | -0.15106 | -0.22888 | 62.9333 | -61.908 | -0.25635 | -0.13275 | -0.045776 | -0.10529 | -0.31128 | -0.21057 | -0.064087 | 0.21057 | 61.5463 | 61.4685 | 124.3835 | 124.5621 | -0.045776 | 124.6307 | 61.8896 | -0.21057 | 124.5621 | -0.045776 | 61.8896 | 124.3835 | 124.6307 | -124.9512 | -124.9054
612.375 | 124.9054 | -61.6699 | 63.0112 | -0.23331 | 0.010453 | 0.01317 | 0.0052231 | 0.067507 | -0.00068359 | 0.069173 | -61.7294 | 62.8876 | -61.9446 | -61.7844 | 62.677 | 0.1831 | -0.16937 | -0.24719 | 62.883 | -61.9217 | -0.27466 | -0.1236 | -0.059509 | -0.11444 | -0.33417 | -0.25177 | -0.12817 | 0.21515 | 61.5005 | 61.4227 | 124.3469 | 124.5575 | -0.059509 | 124.5529 | 61.853 | -0.25177 | 124.5575 | -0.059509 | 61.853 | 124.3469 | 124.5529 | -124.9557 | -124.9329
613.375 | 124.9512 | -61.6745 | 62.9883 | -0.10361 | 0.012375 | 0.0084702 | 0.0037277 | 0.068575 | -0.0015382 | 0.070241 | -61.7065 | 62.8784 | -61.94 | -61.7889 | 62.7319 | 0.21057 | -0.23804 | -0.20142 | 62.9105 | -61.8942 | -0.2655 | -0.10986 | -0.032043 | -0.11444 | -0.25635 | -0.21973 | -0.07782 | 0.23346 | 61.4365 | 61.4731 | 124.4064 | 124.5529 | -0.032043 | 124.585 | 61.8851 | -0.21973 | 124.5529 | -0.032043 | 61.8851 | 124.4064 | 124.585 | -124.9283 | -124.8825
614.375 | 124.9146 | -61.6974 | 63.0157 | -0.20279 | 0.012162 | 0.012529 | 0.0054367 | 0.06708 | -0.00046999 | 0.068319 | -61.734 | 62.8693 | -61.94 | -61.8027 | 62.6816 | 0.18768 | -0.15106 | -0.25177 | 62.8967 | -61.9217 | -0.24261 | -0.14648 | -0.036621 | -0.10529 | -0.33417 | -0.2243 | -0.11902 | 0.20599 | 61.5463 | 61.4456 | 124.379 | 124.5667 | -0.036621 | 124.5941 | 61.8851 | -0.2243 | 124.5667 | -0.036621 | 61.8851 | 124.379 | 124.5941 | -124.9557 | -124.9374
615.4375 | 124.8825 | -61.702 | 63.0524 | -0.21042 | 0.012375 | 0.013383 | 0.0082139 | 0.065798 | -0.0030334 | 0.069387 | -61.7889 | 62.915 | -61.9858 | -61.8576 | 62.6175 | 0.1236 | -0.10071 | -0.3479 | 62.9242 | -61.9308 | -0.28381 | -0.13733 | -0.086975 | -0.15564 | -0.43487 | -0.22888 | -0.12817 | 0.19684 | 61.6013 | 61.3541 | 124.3195 | 124.617 | -0.086975 | 124.6262 | 61.8256 | -0.22888 | 124.617 | -0.086975 | 61.8256 | 124.3195 | 124.6262 | -125.0381 | -124.9832
616.3906 | 124.91 | -61.7065 | 62.9379 | 0.14053 | 0.012162 | 0.012102 | 0.0047959 | 0.067721 | 0.00017081 | 0.069173 | -61.7569 | 62.8967 | -61.972 | -61.8484 | 62.6633 | 0.10529 | -0.36163 | -0.38452 | 62.8372 | -61.9629 | -0.2655 | -0.041198 | -0.050354 | -0.14191 | -0.27466 | -0.25635 | -0.10071 | 0.21515 | 61.3449 | 61.322 | 124.3698 | 124.6033 | -0.050354 | 124.5438 | 61.8118 | -0.25635 | 124.6033 | -0.050354 | 61.8118 | 124.3698 | 124.5438 | -124.91 | -124.9008
617.4219 | 124.91 | -61.7157 | 62.9791 | 0.16342 | 0.013016 | 0.01317 | 0.0050095 | 0.067293 | -0.0026062 | 0.06896 | -61.7706 | 62.8784 | -61.9446 | -61.8622 | 62.6312 | 0.09613 | -0.31586 | -0.41657 | 62.8784 | -61.972 | -0.22888 | -0.10071 | -0.054932 | -0.14648 | -0.3479 | -0.25635 | -0.10071 | 0.17395 | 61.3998 | 61.2991 | 124.3469 | 124.5941 | -0.054932 | 124.5941 | 61.8118 | -0.25635 | 124.5941 | -0.054932 | 61.8118 | 124.3469 | 124.5941 | -124.9237 | -124.9512
618.375 | 124.8459 | -61.7294 | 63.0341 | -0.29434 | 0.012162 | 0.011888 | 0.0071457 | 0.067507 | -0.0043152 | 0.069173 | -61.7752 | 62.9242 | -61.9308 | -61.8347 | 62.6907 | 0.16479 | -0.10529 | -0.37537 | 62.9059 | -61.9675 | -0.20142 | -0.10986 | -0.045777 | -0.10529 | -0.34332 | -0.23804 | -0.12817 | 0.15564 | 61.6241 | 61.3541 | 124.4202 | 124.6536 | -0.045777 | 124.6353 | 61.8942 | -0.23804 | 124.6536 | -0.045777 | 61.8942 | 124.4202 | 124.6353 | -124.9649 | -125.0015
619.3906 | 124.8276 | -61.7477 | 63.002 | 0.033722 | 0.015366 | 0.013383 | 0.010564 | 0.069857 | -0.0030334 | 0.068319 | -61.7889 | 62.9745 | -61.9583 | -61.8851 | 62.5854 | 0.068665 | -0.16937 | -0.46234 | 62.9059 | -61.9904 | -0.21057 | -0.027466 | -0.041198 | -0.13733 | -0.41657 | -0.24261 | -0.09613 | 0.16937 | 61.5784 | 61.2854 | 124.3332 | 124.7223 | -0.041198 | 124.6536 | 61.8164 | -0.24261 | 124.7223 | -0.041198 | 61.8164 | 124.3332 | 124.6536 | -124.9603 | -124.9924
620.375 | 124.8138 | -61.7157 | 63.0341 | -0.26382 | 0.013871 | 0.018083 | 0.0043687 | 0.068575 | -0.0028198 | 0.070455 | -61.7981 | 62.9379 | -61.94 | -61.8759 | 62.6266 | 0.1236 | -0.050354 | -0.32501 | 62.9425 | -61.9263 | -0.2243 | -0.096131 | -0.082398 | -0.16022 | -0.40741 | -0.21057 | -0.091553 | 0.14191 | 61.6653 | 61.3907 | 124.3423 | 124.6536 | -0.082398 | 124.6582 | 61.8393 | -0.21057 | 124.6536 | -0.082398 | 61.8393 | 124.3423 | 124.6582 | -124.9741 | -124.9603
621.375 | 124.8596 | -61.7294 | 63.0112 | 0.018463 | 0.013871 | 0.017229 | 0.010136 | 0.071993 | -0.0023926 | 0.067037 | -61.7477 | 62.9608 | -61.9812 | -61.8668 | 62.6175 | 0.14191 | -0.19226 | -0.41657 | 62.9379 | -61.9492 | -0.25177 | -0.050354 | -0.018311 | -0.13733 | -0.39368 | -0.21973 | -0.073242 | 0.23346 | 61.5372 | 61.3129 | 124.3469 | 124.6902 | -0.018311 | 124.6674 | 61.8713 | -0.21973 | 124.6902 | -0.018311 | 61.8713 | 124.3469 | 124.6674 | -124.9924 | -124.9603
622.375 | 124.8871 | -61.7157 | 63.0112 | -0.27908 | 0.010666 | 0.01317 | 0.0022323 | 0.069857 | -0.0015382 | 0.069814 | -61.7615 | 62.9242 | -61.9675 | -61.8439 | 62.6495 | 0.19226 | -0.11444 | -0.35706 | 62.9333 | -61.9034 | -0.25177 | -0.086975 | -0.045777 | -0.12817 | -0.36163 | -0.18768 | -0.077819 | 0.20599 | 61.6013 | 61.3586 | 124.3652 | 124.6399 | -0.045777 | 124.649 | 61.908 | -0.18768 | 124.6399 | -0.045777 | 61.908 | 124.3652 | 124.649 | -124.9786 | -124.9146
623.375 | 124.8505 | -61.6974 | 62.9837 | -0.30197 | 0.013443 | 0.0099656 | 0.0022323 | 0.07007 | -0.004956 | 0.068319 | -61.7477 | 62.883 | -61.9629 | -61.8393 | 62.645 | 0.19226 | -0.1236 | -0.35706 | 62.9242 | -61.908 | -0.2655 | -0.10071 | -0.050354 | -0.14191 | -0.33875 | -0.21057 | -0.05951 | 0.21515 | 61.5738 | 61.3403 | 124.3423 | 124.5804 | -0.050354 | 124.6216 | 61.8896 | -0.21057 | 124.5804 | -0.050354 | 61.8896 | 124.3423 | 124.6216 | -124.9466 | -124.8917
624.3906 | 124.8001 | -61.734 | 62.9974 | 0.1329 | 0.013657 | 0.015306 | 0.010777 | 0.069857 | 0.00017081 | 0.068532 | -61.8118 | 62.9745 | -61.9766 | -61.9537 | 62.5488 | 0.041199 | -0.19684 | -0.58136 | 62.915 | -62.027 | -0.24262 | -0.022889 | -0.07782 | -0.21973 | -0.44861 | -0.29297 | -0.082398 | 0.16479 | 61.5372 | 61.1526 | 124.2828 | 124.7086 | -0.07782 | 124.649 | 61.7752 | -0.29297 | 124.7086 | -0.07782 | 61.7752 | 124.2828 | 124.649 | -124.9741 | -125.0244
625.3906 | 124.8413 | -61.7249 | 62.9974 | -0.050202 | 0.013443 | 0.01317 | 0.0086411 | 0.071993 | -0.0011108 | 0.06896 | -61.7386 | 62.9608 | -61.9858 | -61.8851 | 62.6221 | 0.14191 | -0.19684 | -0.45776 | 62.9379 | -61.9904 | -0.26093 | -0.036622 | -0.013732 | -0.16022 | -0.37537 | -0.2655 | -0.05951 | 0.24719 | 61.528 | 61.2671 | 124.3469 | 124.6857 | -0.013732 | 124.6628 | 61.8668 | -0.2655 | 124.6857 | -0.013732 | 61.8668 | 124.3469 | 124.6628 | -124.9832 | -124.9878
626.375 | 124.9237 | -61.7111 | 62.9745 | -0.20279 | 0.0091708 | 0.012743 | 0.0013779 | 0.070284 | -0.003247 | 0.067891 | -61.7477 | 62.8922 | -61.9583 | -61.8118 | 62.677 | 0.25635 | -0.18768 | -0.33875 | 62.9105 | -61.9034 | -0.24719 | -0.082397 | -0.036621 | -0.10071 | -0.29755 | -0.19226 | -0.064087 | 0.21057 | 61.5234 | 61.3724 | 124.3881 | 124.6033 | -0.036621 | 124.6216 | 61.9675 | -0.19226 | 124.6033 | -0.036621 | 61.9675 | 124.3881 | 124.6216 | -124.9329 | -124.8779
627.375 | 124.9329 | -61.6791 | 62.9654 | -0.23331 | 0.010025 | 0.011461 | 0.0028733 | 0.068148 | -0.0030334 | 0.067464 | -61.734 | 62.8738 | -61.9629 | -61.8393 | 62.6724 | 0.2655 | -0.23346 | -0.35706 | 62.9333 | -61.9171 | -0.28381 | -0.091553 | -0.054932 | -0.16022 | -0.29297 | -0.23804 | -0.032043 | 0.22888 | 61.4456 | 61.322 | 124.3515 | 124.5529 | -0.054932 | 124.6124 | 61.9446 | -0.23804 | 124.5529 | -0.054932 | 61.9446 | 124.3515 | 124.6124 | -124.9283 | -124.8825
628.3906 | 124.7314 | -61.7752 | 62.9471 | 0.010834 | 0.015366 | 0.017656 | 0.010991 | 0.067507 | -0.0013244 | 0.070455 | -61.8027 | 62.9745 | -61.9812 | -61.94 | 62.5488 | 0.07782 | -0.17853 | -0.58594 | 62.9242 | -62.0316 | -0.20599 | 0.027465 | -0.027465 | -0.16479 | -0.39825 | -0.25635 | -0.022889 | 0.17853 | 61.5967 | 61.1893 | 124.324 | 124.7498 | -0.027465 | 124.6994 | 61.853 | -0.25635 | 124.7498 | -0.027465 | 61.853 | 124.324 | 124.6994 | -124.9283 | -124.9786
629.375 | 124.8825 | -61.6882 | 62.9883 | -0.28671 | 0.01323 | 0.014452 | 0.0037277 | 0.068575 | -0.0036744 | 0.070028 | -61.7569 | 62.8738 | -61.9675 | -61.8439 | 62.6495 | 0.25177 | -0.17853 | -0.39368 | 62.9196 | -61.9217 | -0.27924 | -0.11444 | -0.068665 | -0.15564 | -0.33875 | -0.23346 | -0.068664 | 0.21057 | 61.5097 | 61.2946 | 124.3378 | 124.5621 | -0.068665 | 124.6078 | 61.94 | -0.23346 | 124.5621 | -0.068665 | 61.94 | 124.3378 | 124.6078 | -124.9557 | -124.91
630.375 | 124.9191 | -61.7111 | 62.9837 | -0.21805 | 0.012589 | 0.017229 | 0.0024461 | 0.068148 | -0.00046999 | 0.069814 | -61.7386 | 62.883 | -61.972 | -61.8393 | 62.6633 | 0.29755 | -0.20599 | -0.3891 | 62.9242 | -61.9217 | -0.26093 | -0.10071 | -0.027465 | -0.12817 | -0.32044 | -0.21057 | -0.05951 | 0.23346 | 61.5051 | 61.322 | 124.3744 | 124.5941 | -0.027465 | 124.6353 | 62.0087 | -0.21057 | 124.5941 | -0.027465 | 62.0087 | 124.3744 | 124.6353 | -124.9557 | -124.9054
631.375 | 124.7314 | -61.7203 | 62.9791 | -0.24857 | 0.014298 | 0.013597 | 0.01035 | 0.069002 | -0.003247 | 0.067464 | -61.7386 | 62.9562 | -61.9766 | -61.8759 | 62.5763 | 0.23346 | -0.16937 | -0.47607 | 62.9013 | -62.0132 | -0.25635 | -0.022888 | -0.01831 | -0.15564 | -0.40283 | -0.29297 | -0.07782 | 0.23804 | 61.5509 | 61.2442 | 124.2966 | 124.6765 | -0.01831 | 124.6216 | 61.9537 | -0.29297 | 124.6765 | -0.01831 | 61.9537 | 124.2966 | 124.6216 | -124.9557 | -124.9924
632.375 | 124.8505 | -61.6928 | 62.9883 | -0.27145 | 0.012589 | 0.01787 | 0.0035141 | 0.069643 | -0.0017518 | 0.069814 | -61.7661 | 62.8922 | -61.9675 | -61.853 | 62.6129 | 0.30212 | -0.14648 | -0.42114 | 62.9379 | -61.94 | -0.27466 | -0.09613 | -0.073242 | -0.16022 | -0.37537 | -0.24719 | -0.050354 | 0.20142 | 61.5463 | 61.2717 | 124.3057 | 124.585 | -0.073242 | 124.6307 | 61.9949 | -0.24719 | 124.585 | -0.073242 | 61.9949 | 124.3057 | 124.6307 | -124.9557 | -124.9283
633.375 | 124.9191 | -61.7065 | 63.002 | -0.26382 | 0.012589 | 0.013811 | 0.0033005 | 0.066652 | -0.0023926 | 0.069173 | -61.7477 | 62.851 | -61.9675 | -61.8576 | 62.6175 | 0.3479 | -0.19684 | -0.4303 | 62.9105 | -61.9446 | -0.26092 | -0.15106 | -0.041199 | -0.15106 | -0.38452 | -0.23804 | -0.091553 | 0.21973 | 61.5097 | 61.2762 | 124.324 | 124.5575 | -0.041199 | 124.617 | 62.0544 | -0.23804 | 124.5575 | -0.041199 | 62.0544 | 124.324 | 124.617 | -124.9695 | -124.9466
634.375 | 124.9557 | -61.6882 | 62.9471 | 1.0408 | 0.010453 | 0.011247 | 0.0020187 | 0.067293 | -0.0015382 | 0.06896 | -61.7294 | 62.8464 | -61.9995 | -61.8347 | 62.6678 | 0.43488 | -0.28839 | -0.37994 | 62.8876 | -61.9263 | -0.31128 | -0.10071 | -0.041199 | -0.14648 | -0.27924 | -0.23804 | -0.05951 | 0.27008 | 61.3998 | 61.3083 | 124.3561 | 124.5346 | -0.041199 | 124.5758 | 62.1231 | -0.23804 | 124.5346 | -0.041199 | 62.1231 | 124.3561 | 124.5758 | -124.9466 | -124.8734
635.375 | 124.9512 | -61.702 | 62.9837 | -0.23331 | 0.010666 | 0.016374 | 0.0039413 | 0.06708 | -0.0026062 | 0.068319 | -61.7569 | 62.8464 | -61.9492 | -61.8347 | 62.6358 | 0.44861 | -0.26093 | -0.39368 | 62.8738 | -61.9629 | -0.24719 | -0.13733 | -0.054932 | -0.13275 | -0.3479 | -0.26093 | -0.10986 | 0.19226 | 61.441 | 61.3083 | 124.3378 | 124.5483 | -0.054932 | 124.5758 | 62.1506 | -0.26093 | 124.5483 | -0.054932 | 62.1506 | 124.3378 | 124.5758 | -124.9329 | -124.9466
636.375 | 124.9146 | -61.7294 | 62.9837 | -0.2562 | 0.011948 | 0.014452 | 0.0056503 | 0.065157 | -0.0017518 | 0.069173 | -61.7706 | 62.8601 | -62.0132 | -61.8484 | 62.5946 | 0.46234 | -0.20142 | -0.4303 | 62.8876 | -61.9629 | -0.28381 | -0.1236 | -0.041199 | -0.11902 | -0.3891 | -0.23346 | -0.096131 | 0.24262 | 61.528 | 61.2991 | 124.324 | 124.5895 | -0.041199 | 124.617 | 62.1918 | -0.23346 | 124.5895 | -0.041199 | 62.1918 | 124.324 | 124.617 | -124.9969 | -124.9466
637.375 | 124.9786 | -61.6974 | 62.9333 | 0.39993 | 0.011093 | 0.012743 | 0.0060777 | 0.067934 | -0.004956 | 0.0696 | -61.7477 | 62.8281 | -62.0041 | -61.8256 | 62.6358 | 0.54932 | -0.31586 | -0.41199 | 62.8647 | -61.9492 | -0.3067 | -0.10529 | -0.050354 | -0.12817 | -0.29755 | -0.25177 | -0.068665 | 0.25635 | 61.3815 | 61.2854 | 124.3332 | 124.5255 | -0.050354 | 124.5621 | 62.2467 | -0.25177 | 124.5255 | -0.050354 | 62.2467 | 124.3332 | 124.5621 | -124.9374 | -124.8825
638.375 | 124.9374 | -61.7157 | 62.9379 | -0.16464 | 0.011948 | 0.012529 | 0.0065049 | 0.066439 | -0.0026062 | 0.0696 | -61.7569 | 62.8052 | -61.9904 | -61.9446 | 62.5442 | 0.62256 | -0.36163 | -0.4303 | 62.8464 | -61.9675 | -0.27466 | -0.13275 | -0.041199 | -0.22888 | -0.39368 | -0.25177 | -0.091552 | 0.23346 | 61.3541 | 61.2854 | 124.2599 | 124.5209 | -0.041199 | 124.5621 | 62.3383 | -0.25177 | 124.5209 | -0.041199 | 62.3383 | 124.2599 | 124.5621 | -124.9283 | -124.9054
639.375 | 124.8413 | -61.7798 | 62.9929 | -0.21805 | 0.015793 | 0.01082 | 0.0099229 | 0.066866 | -0.0026062 | 0.068105 | -61.8393 | 62.9013 | -62.027 | -61.9308 | 62.4893 | 0.56763 | -0.13733 | -0.55389 | 62.9013 | -62.0361 | -0.24719 | -0.091553 | -0.059509 | -0.15106 | -0.50354 | -0.25635 | -0.091553 | 0.18768 | 61.6425 | 61.2259 | 124.2691 | 124.6811 | -0.059509 | 124.6811 | 62.3474 | -0.25635 | 124.6811 | -0.059509 | 62.3474 | 124.2691 | 124.6811 | -125.0198 | -125.029
640.375 | 124.942 | -61.7249 | 62.9425 | -0.14938 | 0.013016 | 0.012529 | 0.0035141 | 0.066225 | -0.0011108 | 0.068746 | -61.7798 | 62.7731 | -62.0087 | -61.8347 | 62.5946 | 0.76446 | -0.31128 | -0.42572 | 62.8464 | -61.9629 | -0.28381 | -0.16937 | -0.054931 | -0.10986 | -0.3479 | -0.23804 | -0.09613 | 0.22888 | 61.4136 | 61.2991 | 124.3195 | 124.498 | -0.054931 | 124.5712 | 62.4893 | -0.23804 | 124.498 | -0.054931 | 62.4893 | 124.3195 | 124.5712 | -124.9512 | -124.9054
641.4062 | 124.9054 | -61.7752 | 62.8922 | 0.048981 | 0.012162 | 0.016374 | 0.0039413 | 0.06943 | -0.0011108 | 0.067678 | -61.8484 | 62.8143 | -62.0361 | -61.9537 | 62.4802 | 0.7782 | -0.3479 | -0.5722 | 62.8143 | -62.0316 | -0.26093 | -0.07782 | -0.073242 | -0.17853 | -0.41199 | -0.25635 | -0.07782 | 0.18768 | 61.4273 | 61.203 | 124.2554 | 124.5895 | -0.073242 | 124.5895 | 62.5534 | -0.25635 | 124.5895 | -0.073242 | 62.5534 | 124.2554 | 124.5895 | -124.9283 | -124.9237
642.375 | 124.9603 | -61.7798 | 62.883 | -0.13412 | 0.0098118 | 0.012315 | 0.0026597 | 0.06473 | -0.0013244 | 0.068105 | -61.8347 | 62.7731 | -62.0132 | -61.8942 | 62.5214 | 0.97046 | -0.3479 | -0.48981 | 62.8418 | -61.9766 | -0.23346 | -0.10986 | -0.054932 | -0.11444 | -0.36163 | -0.19684 | -0.041199 | 0.17853 | 61.4319 | 61.29 | 124.3011 | 124.5529 | -0.054932 | 124.6216 | 62.7502 | -0.19684 | 124.5529 | -0.054932 | 62.7502 | 124.3011 | 124.6216 | -124.8962 | -124.8596
643.375 | 124.9741 | -61.7477 | 62.9242 | -0.1265 | 0.010025 | 0.01082 | 0.0030869 | 0.064944 | -4.2788e-05 | 0.068746 | -61.8164 | 62.7777 | -62.0361 | -61.8759 | 62.5534 | 1.1719 | -0.36621 | -0.43945 | 62.8143 | -61.9858 | -0.28839 | -0.14648 | -0.068664 | -0.12817 | -0.37079 | -0.23804 | -0.10986 | 0.21973 | 61.3815 | 61.3083 | 124.3011 | 124.5255 | -0.068664 | 124.5621 | 62.9196 | -0.23804 | 124.5255 | -0.068664 | 62.9196 | 124.3011 | 124.5621 | -124.9603 | -124.91
644.375 | 124.9466 | -61.7569 | 62.8876 | -0.57663 | 0.013871 | 0.01082 | 0.0054367 | 0.066866 | -0.0017518 | 0.067037 | -61.8301 | 62.7731 | -62.027 | -61.8484 | 62.5351 | 1.3458 | -0.34332 | -0.4303 | 62.8098 | -61.9995 | -0.27008 | -0.11444 | -0.073242 | -0.091553 | -0.35248 | -0.24262 | -0.07782 | 0.19684 | 61.4136 | 61.3266 | 124.292 | 124.53 | -0.073242 | 124.5667 | 63.1027 | -0.24262 | 124.53 | -0.073242 | 63.1027 | 124.292 | 124.5667 | -124.9146 | -124.8871
645.375 | 124.9741 | -61.7661 | 62.9059 | -2.7815 | 0.011948 | 0.017229 | 0.0045823 | 0.06473 | -0.00089719 | 0.069814 | -62.0316 | 62.7686 | -62.0361 | -61.8942 | 62.5259 | 1.5335 | -0.32959 | -0.42572 | 62.7823 | -62.0041 | -0.27008 | -0.13733 | -0.2655 | -0.12817 | -0.37994 | -0.23804 | -0.1236 | 0.004578 | 61.4365 | 61.3403 | 124.292 | 124.5346 | -0.2655 | 124.5483 | 63.2996 | -0.23804 | 124.5346 | -0.2655 | 63.2996 | 124.292 | 124.5483 | -124.942 | -124.91
646.4375 | 124.7864 | -61.8164 | 62.9013 | 0.010834 | 0.016434 | 0.015306 | 0.012273 | 0.067934 | -0.0013244 | 0.070028 | -61.8988 | 62.8738 | -62.1048 | -62.0132 | 62.3199 | 1.5839 | -0.26093 | -0.66376 | 62.8006 | -62.0865 | -0.28839 | -0.027466 | -0.082398 | -0.19684 | -0.58136 | -0.27008 | -0.10071 | 0.20599 | 61.5555 | 61.1526 | 124.1364 | 124.6902 | -0.082398 | 124.617 | 63.4003 | -0.27008 | 124.6902 | -0.082398 | 63.4003 | 124.1364 | 124.617 | -125.0061 | -124.9878
647.375 | 125.0702 | -61.7615 | 62.8693 | -0.11887 | 0.011948 | 0.010393 | 0.00095067 | 0.066866 | -4.2788e-05 | 0.069387 | -61.8347 | 62.7411 | -62.0682 | -61.8942 | 62.5076 | 2.0325 | -0.3891 | -0.39368 | 62.7731 | -61.9904 | -0.3067 | -0.12817 | -0.073242 | -0.13275 | -0.36163 | -0.22888 | -0.096131 | 0.23346 | 61.3724 | 61.3678 | 124.2691 | 124.5026 | -0.073242 | 124.5346 | 63.7939 | -0.22888 | 124.5026 | -0.073242 | 63.7939 | 124.2691 | 124.5346 | -124.9374 | -124.8596
648.375 | 124.9557 | -61.7981 | 62.8464 | -0.10361 | 0.010025 | 0.011888 | 0.00073707 | 0.065584 | -0.0023926 | 0.0696 | -61.8713 | 62.7182 | -62.059 | -61.9308 | 62.4435 | 2.3163 | -0.3891 | -0.40741 | 62.7548 | -62.0224 | -0.26093 | -0.12817 | -0.073242 | -0.13275 | -0.40283 | -0.2243 | -0.091553 | 0.18768 | 61.409 | 61.3907 | 124.2416 | 124.5163 | -0.073242 | 124.5529 | 64.1144 | -0.2243 | 124.5163 | -0.073242 | 64.1144 | 124.2416 | 124.5529 | -124.9054 | -124.8688
649.375 | 124.9649 | -61.8164 | 62.8464 | -0.11124 | 0.010666 | 0.012529 | 0.0054367 | 0.067293 | -0.0036744 | 0.068746 | -61.8851 | 62.7228 | -62.0773 | -61.9446 | 62.4207 | 2.623 | -0.39825 | -0.41657 | 62.7319 | -62.0361 | -0.26093 | -0.1236 | -0.068665 | -0.12817 | -0.42572 | -0.21973 | -0.11444 | 0.19226 | 61.4182 | 61.3998 | 124.2371 | 124.5392 | -0.068665 | 124.5483 | 64.4394 | -0.21973 | 124.5392 | -0.068665 | 64.4394 | 124.2371 | 124.5483 | -124.9237 | -124.8825
650.375 | 124.9466 | -61.8164 | 62.8372 | -0.17227 | 0.012802 | 0.011461 | -0.0011855 | 0.066866 | 0.00081181 | 0.071309 | -61.8576 | 62.7136 | -62.0728 | -61.94 | 62.4252 | 2.8748 | -0.36621 | -0.36621 | 62.7228 | -62.0407 | -0.25635 | -0.1236 | -0.041199 | -0.1236 | -0.41199 | -0.2243 | -0.11444 | 0.21515 | 61.4502 | 61.4502 | 124.2416 | 124.53 | -0.041199 | 124.5392 | 64.6912 | -0.2243 | 124.53 | -0.041199 | 64.6912 | 124.2416 | 124.5392 | -124.91 | -124.8779
651.375 | 124.8596 | -61.8439 | 62.796 | -0.19516 | 0.011734 | 0.012743 | 0.0026597 | 0.065584 | -0.0011108 | 0.070241 | -61.8622 | 62.6724 | -62.0728 | -61.9263 | 62.4115 | 3.3737 | -0.41199 | 0.1236 | 62.7594 | -62.0453 | -0.22888 | -0.1236 | -0.018311 | -0.082398 | -0.38452 | -0.20142 | -0.036622 | 0.21057 | 61.4319 | 61.9675 | 124.2554 | 124.5163 | -0.018311 | 124.6033 | 65.2176 | -0.20142 | 124.5163 | -0.018311 | 65.2176 | 124.2554 | 124.6033 | -124.8688 | -124.8413
652.375 | 124.9329 | -61.8393 | 62.8006 | -0.14938 | 0.010453 | 0.015306 | 0.0043687 | 0.066439 | -0.00046999 | 0.069173 | -61.8942 | 62.6953 | -62.1277 | -61.9446 | 62.3795 | 3.7674 | -0.4303 | -0.30212 | 62.7274 | -62.0636 | -0.28839 | -0.10529 | -0.054932 | -0.10529 | -0.42114 | -0.22431 | -0.073242 | 0.23346 | 61.409 | 61.5372 | 124.2188 | 124.5346 | -0.054932 | 124.5667 | 65.6067 | -0.22431 | 124.5346 | -0.054932 | 65.6067 | 124.2188 | 124.5667 | -124.9283 | -124.8642
653.375 | 124.9649 | -61.8347 | 62.8006 | -0.14175 | 0.010453 | 0.010179 | 0.0022323 | 0.065584 | -0.0015382 | 0.070028 | -61.9125 | 62.6678 | -62.1506 | -61.9537 | 62.3199 | 4.1931 | -0.43488 | -0.27466 | 62.7045 | -62.0728 | -0.31586 | -0.13275 | -0.07782 | -0.11902 | -0.48065 | -0.23804 | -0.09613 | 0.23804 | 61.3998 | 61.5601 | 124.1547 | 124.5026 | -0.07782 | 124.5392 | 66.0278 | -0.23804 | 124.5026 | -0.07782 | 66.0278 | 124.1547 | 124.5392 | -124.9512 | -124.8734
654.375 | 124.9283 | -61.8851 | 62.7731 | -0.0044251 | 0.01323 | 0.013597 | 0.0024461 | 0.065798 | -0.0017518 | 0.0696 | -61.9675 | 62.6587 | -62.1552 | -62.0316 | 62.233 | 4.6234 | -0.42572 | -0.32501 | 62.7045 | -62.1277 | -0.27008 | -0.11444 | -0.082397 | -0.14648 | -0.54016 | -0.24261 | -0.068664 | 0.18768 | 61.4594 | 61.5601 | 124.118 | 124.5438 | -0.082397 | 124.5895 | 66.5085 | -0.24261 | 124.5438 | -0.082397 | 66.5085 | 124.118 | 124.5895 | -124.9283 | -124.9008
655.375 | 124.9512 | -61.8759 | 62.7686 | -0.080719 | 0.01088 | 0.0082566 | 0.0020187 | 0.06708 | -0.0011108 | 0.070241 | -61.9537 | 62.6541 | -62.1552 | -61.9949 | 62.2238 | 5.2368 | -0.43488 | -0.24261 | 62.6724 | -62.1185 | -0.27923 | -0.11444 | -0.077819 | -0.11902 | -0.54474 | -0.24261 | -0.096131 | 0.20142 | 61.441 | 61.6333 | 124.0997 | 124.53 | -0.077819 | 124.5483 | 67.1127 | -0.24261 | 124.53 | -0.077819 | 67.1127 | 124.0997 | 124.5483 | -124.9237 | -124.8871
656.375 | 124.9466 | -61.8988 | 62.7823 | -0.088349 | 0.011307 | 0.0099656 | -0.00054473 | 0.066012 | -0.00046999 | 0.06896 | -61.972 | 62.6175 | -62.1735 | -62.0316 | 62.1872 | 5.7999 | -0.45776 | -0.2243 | 62.6541 | -62.1277 | -0.27466 | -0.16479 | -0.073242 | -0.13275 | -0.59509 | -0.22888 | -0.12817 | 0.20142 | 61.441 | 61.6745 | 124.086 | 124.5163 | -0.073242 | 124.5529 | 67.6987 | -0.22888 | 124.5163 | -0.073242 | 67.6987 | 124.086 | 124.5529 | -124.9557 | -124.91
657.375 | 124.9557 | -61.9171 | 62.7365 | -0.095978 | 0.011734 | 0.012743 | 0.0041549 | 0.064944 | -0.0011108 | 0.068532 | -61.9812 | 62.6266 | -62.1826 | -62.027 | 62.1552 | 6.3675 | -0.48065 | -0.21515 | 62.6862 | -62.1414 | -0.2655 | -0.10986 | -0.064087 | -0.10986 | -0.58136 | -0.2243 | -0.050354 | 0.20142 | 61.4365 | 61.702 | 124.0723 | 124.5438 | -0.064087 | 124.6033 | 68.2846 | -0.2243 | 124.5438 | -0.064087 | 68.2846 | 124.0723 | 124.6033 | -124.9191 | -124.8779
658.375 | 124.942 | -61.8988 | 62.7136 | -0.080719 | 0.011948 | 0.012743 | 0.0041549 | 0.063235 | -0.00025639 | 0.070028 | -61.9812 | 62.6083 | -62.1964 | -62.0361 | 62.1231 | 6.9077 | -0.48523 | -0.2243 | 62.6312 | -62.1414 | -0.29755 | -0.10529 | -0.082397 | -0.13733 | -0.59051 | -0.24261 | -0.082397 | 0.21515 | 61.4136 | 61.6745 | 124.0219 | 124.5071 | -0.082397 | 124.53 | 68.8065 | -0.24261 | 124.5071 | -0.082397 | 68.8065 | 124.0219 | 124.53 | -124.91 | -124.855
659.375 | 124.9374 | -61.908 | 62.7228 | -0.17227 | 0.010239 | 0.010179 | 0.0018051 | 0.065798 | 0.00017081 | 0.068105 | -61.6425 | 62.6633 | -62.1368 | -62.0087 | 62.0956 | 7.4615 | -0.54016 | -0.20599 | 62.5992 | -62.1643 | -0.22888 | -0.059509 | 0.2655 | -0.10071 | -0.62714 | -0.25635 | -0.1236 | 0.49438 | 61.3678 | 61.702 | 124.0036 | 124.5712 | 0.2655 | 124.5071 | 69.3695 | -0.25635 | 124.5712 | 0.2655 | 69.3695 | 124.0036 | 124.5071 | -124.8596 | -124.8871
660.375 | 124.9374 | -61.9446 | 62.709 | -0.19516 | 0.011734 | 0.012529 | 0.0056503 | 0.067721 | -0.0013244 | 0.069814 | -61.972 | 62.5763 | -62.2009 | -62.1368 | 61.9537 | 7.814 | -0.5722 | -0.17853 | 62.5992 | -62.1735 | -0.25635 | -0.13275 | -0.027466 | -0.19226 | -0.75531 | -0.22888 | -0.10986 | 0.22888 | 61.3724 | 61.7661 | 123.8983 | 124.5209 | -0.027466 | 124.5438 | 69.7586 | -0.22888 | 124.5209 | -0.027466 | 69.7586 | 123.8983 | 124.5438 | -124.91 | -124.8825
661.375 | 124.9695 | -61.9858 | 62.7045 | -0.16464 | 0.0070346 | 0.010393 | 0.0022323 | 0.065157 | -0.0030334 | 0.068319 | -62.0224 | 62.5717 | -62.2101 | -62.0865 | 61.9492 | 8.1665 | -0.59509 | -0.24719 | 62.6083 | -62.2009 | -0.2243 | -0.13275 | -0.036621 | -0.10071 | -0.75531 | -0.21515 | -0.096131 | 0.18768 | 61.3907 | 61.7386 | 123.9349 | 124.5575 | -0.036621 | 124.5941 | 70.1523 | -0.21515 | 124.5575 | -0.036621 | 70.1523 | 123.9349 | 124.5941 | -124.9146 | -124.9054
662.375 | 124.9466 | -61.9629 | 62.6816 | -0.14175 | 0.011734 | 0.012743 | -0.0018265 | 0.065157 | -0.0013244 | 0.069814 | -61.9904 | 62.5763 | -62.2375 | -62.1689 | 61.9812 | 8.6929 | -0.77362 | -0.21973 | 62.5717 | -62.1826 | -0.27466 | -0.10529 | -0.027465 | -0.20599 | -0.70038 | -0.21973 | -0.10986 | 0.24719 | 61.1893 | 61.7432 | 123.9441 | 124.5392 | -0.027465 | 124.5346 | 70.6558 | -0.21973 | 124.5392 | -0.027465 | 70.6558 | 123.9441 | 124.5346 | -124.9191 | -124.8642
663.375 | 124.9741 | -61.9583 | 62.6724 | -0.17227 | 0.011734 | 0.012743 | 0.0020187 | 0.068575 | -0.0028198 | 0.068532 | -61.9858 | 62.5442 | -62.233 | -62.114 | 61.5875 | 8.9996 | -0.81482 | -0.48065 | 62.5488 | -62.2147 | -0.27466 | -0.12817 | -0.027466 | -0.15564 | -1.0849 | -0.25635 | -0.1236 | 0.24719 | 61.1435 | 61.4777 | 123.5458 | 124.5026 | -0.027466 | 124.5071 | 70.9579 | -0.25635 | 124.5026 | -0.027466 | 70.9579 | 123.5458 | 124.5071 | -124.9054 | -124.8871
664.375 | 124.9512 | -61.9675 | 62.7045 | -0.1799 | 0.013443 | 0.012315 | 0.0022323 | 0.066866 | -0.0015382 | 0.065328 | -61.9812 | 62.558 | -62.2284 | -61.6562 | 62.1048 | 9.4803 | -0.92468 | -0.40283 | 62.5854 | -62.1826 | -0.26093 | -0.14648 | -0.013733 | 0.31128 | -0.59967 | -0.21515 | -0.11902 | 0.24719 | 61.0428 | 61.5646 | 124.0723 | 124.5255 | -0.013733 | 124.5529 | 71.4478 | -0.21515 | 124.5255 | -0.013733 | 71.4478 | 124.0723 | 124.5529 | -124.9329 | -124.8871
665.375 | 124.9237 | -61.9446 | 62.6724 | -0.24857 | 0.010453 | 0.01317 | 0.0020187 | 0.066225 | -0.0017518 | 0.067251 | -61.9904 | 62.5671 | -62.2375 | -62.0453 | 61.8942 | 10.3317 | -1.0529 | -0.88348 | 62.6266 | -62.1735 | -0.29297 | -0.10529 | -0.045776 | -0.10071 | -0.7782 | -0.22888 | -0.045776 | 0.24719 | 60.8917 | 61.0611 | 123.8388 | 124.5117 | -0.045776 | 124.5712 | 72.2763 | -0.22888 | 124.5117 | -0.045776 | 72.2763 | 123.8388 | 124.5712 | -124.91 | -124.8459
666.375 | 124.9283 | -61.94 | 62.7274 | -0.18753 | 0.010025 | 0.013383 | 0.0056503 | 0.065371 | -0.0017518 | 0.068746 | -61.9629 | 62.5992 | -62.2101 | -62.0499 | 61.6699 | 10.3775 | -1.0437 | -0.75073 | 62.5992 | -62.1597 | -0.27008 | -0.12817 | -0.022889 | -0.10986 | -1.0574 | -0.21973 | -0.12817 | 0.24719 | 60.8963 | 61.1893 | 123.6099 | 124.5392 | -0.022889 | 124.5392 | 72.3175 | -0.21973 | 124.5392 | -0.022889 | 72.3175 | 123.6099 | 124.5392 | -124.9374 | -124.8871
667.375 | 124.9329 | -61.9034 | 62.7274 | -0.27908 | 0.010666 | 0.011675 | 0.0035141 | 0.066012 | -0.00068359 | 0.067891 | -61.9263 | 62.6083 | -62.1826 | -62.0178 | 61.6287 | 10.7895 | -1.1765 | -0.93384 | 62.6221 | -62.1414 | -0.27924 | -0.11902 | -0.022889 | -0.11444 | -1.0986 | -0.23804 | -0.10529 | 0.25635 | 60.7269 | 60.9695 | 123.5321 | 124.5117 | -0.022889 | 124.5255 | 72.6929 | -0.23804 | 124.5117 | -0.022889 | 72.6929 | 123.5321 | 124.5255 | -124.91 | -124.8688
668.375 | 124.942 | -61.9034 | 62.764 | -0.057831 | 0.012802 | 0.013383 | 0.0026597 | 0.064516 | -0.002179 | 0.0696 | -61.9354 | 62.6404 | -62.1735 | -62.0453 | 61.5189 | 11.0413 | -1.2634 | -1.1581 | 62.6633 | -62.1414 | -0.27008 | -0.1236 | -0.032044 | -0.14191 | -1.2451 | -0.23804 | -0.10071 | 0.23804 | 60.64 | 60.7452 | 123.4222 | 124.5438 | -0.032044 | 124.5667 | 72.9446 | -0.23804 | 124.5438 | -0.032044 | 72.9446 | 123.4222 | 124.5667 | -124.9374 | -124.9054
669.375 | 124.9283 | -61.7386 | 62.9013 | -0.24094 | 0.01088 | 0.012743 | 0.0033005 | 0.06708 | -0.0017518 | 0.069173 | -61.7523 | 62.796 | -62.0132 | -61.8301 | 61.6562 | 11.2152 | -1.1765 | -1.0712 | 62.8006 | -61.9583 | -0.27466 | -0.10528 | -0.013733 | -0.091553 | -1.2451 | -0.21973 | -0.10071 | 0.26093 | 60.5621 | 60.6674 | 123.3948 | 124.5346 | -0.013733 | 124.5392 | 72.9538 | -0.21973 | 124.5346 | -0.013733 | 72.9538 | 123.3948 | 124.5392 | -124.9146 | -124.8596
670.375 | 124.9374 | -61.7203 | 62.9242 | -0.24094 | 0.013657 | 0.0093246 | 0.0071457 | 0.06708 | -0.0013244 | 0.070455 | -61.7523 | 62.8006 | -61.9995 | -61.8622 | 61.5051 | 11.1328 | -1.2497 | -1.3229 | 62.8052 | -61.9949 | -0.27924 | -0.1236 | -0.032043 | -0.14191 | -1.4191 | -0.27466 | -0.11902 | 0.24719 | 60.4706 | 60.3973 | 123.2254 | 124.5209 | -0.032043 | 124.5255 | 72.8531 | -0.27466 | 124.5209 | -0.032043 | 72.8531 | 123.2254 | 124.5255 | -124.9237 | -124.9191
671.375 | 124.942 | -61.6608 | 62.9974 | -0.16464 | 0.0091708 | 0.013383 | 0.0056503 | 0.067721 | -0.00046999 | 0.068319 | -61.3403 | 62.9471 | -61.9171 | -61.7615 | 61.5372 | 10.4279 | -1.3092 | -1.3641 | 62.8784 | -61.8759 | -0.25635 | -0.050354 | 0.32044 | -0.10071 | -1.4603 | -0.21515 | -0.11902 | 0.57678 | 60.3516 | 60.2966 | 123.1979 | 124.6078 | 0.32044 | 124.5392 | 72.0886 | -0.21515 | 124.6078 | 0.32044 | 72.0886 | 123.1979 | 124.5392 | -124.9146 | -124.8734
672.375 | 124.9054 | -61.6287 | 63.0341 | -0.24094 | 0.011307 | 0.012315 | 0.0043687 | 0.064944 | -0.0026062 | 0.069173 | -61.5875 | 62.9242 | -61.8942 | -61.7249 | 61.4502 | 10.4599 | -1.3321 | -1.5518 | 62.9379 | -61.8256 | -0.2655 | -0.10986 | 0.041199 | -0.096131 | -1.5839 | -0.19684 | -0.096131 | 0.3067 | 60.2966 | 60.0769 | 123.0789 | 124.5529 | 0.041199 | 124.5667 | 72.0886 | -0.19684 | 124.5529 | 0.041199 | 72.0886 | 123.0789 | 124.5667 | -124.9283 | -124.8596
673.375 | 124.9146 | -61.5005 | 63.1531 | -0.23331 | 0.010666 | 0.012529 | 0.0041549 | 0.066439 | -0.0017518 | 0.067891 | -61.4777 | 63.0203 | -61.7752 | -61.615 | 61.3861 | 10.5057 | -1.4236 | -1.8173 | 63.0249 | -61.7523 | -0.27466 | -0.13275 | 0.022888 | -0.11444 | -1.767 | -0.25177 | -0.12817 | 0.29755 | 60.0769 | 59.6832 | 122.8867 | 124.5209 | 0.022888 | 124.5255 | 72.0062 | -0.25177 | 124.5209 | 0.022888 | 72.0062 | 122.8867 | 124.5255 | -124.9283 | -124.9054
674.375 | 124.9649 | -61.4182 | 63.2263 | -0.27908 | 0.010239 | 0.013597 | 0.0052231 | 0.066225 | -0.0017518 | 0.070669 | -61.3953 | 63.1119 | -61.6745 | -61.5005 | 61.322 | 10.4507 | -1.5152 | -2.0554 | 63.1119 | -61.6379 | -0.25635 | -0.11444 | 0.022888 | -0.082397 | -1.9043 | -0.21973 | -0.11444 | 0.27924 | 59.903 | 59.3628 | 122.7402 | 124.53 | 0.022888 | 124.53 | 71.8689 | -0.21973 | 124.53 | 0.022888 | 71.8689 | 122.7402 | 124.53 | -124.9008 | -124.8642
675.375 | 124.9695 | -61.377 | 63.2721 | -0.13412 | 0.012375 | 0.011888 | 0.00095067 | 0.065157 | -0.0017518 | 0.070241 | -61.3449 | 63.176 | -61.6333 | -61.4914 | 61.1252 | 10.2127 | -1.6479 | -2.3163 | 63.1622 | -61.5784 | -0.25635 | -0.096131 | 0.032043 | -0.11444 | -2.1469 | -0.20142 | -0.10986 | 0.28839 | 59.729 | 59.0607 | 122.5021 | 124.5529 | 0.032043 | 124.5392 | 71.5897 | -0.20142 | 124.5529 | 0.032043 | 71.5897 | 122.5021 | 124.5392 | -124.9054 | -124.8505
676.375 | 124.8962 | -61.3312 | 63.3408 | -0.50034 | 0.012375 | 0.012102 | 0.0028733 | 0.065371 | -0.00089719 | 0.067891 | -61.3083 | 63.1989 | -61.5967 | -61.4136 | 60.9924 | 9.4437 | -1.6434 | -2.4902 | 63.2401 | -61.5417 | -0.2655 | -0.14191 | 0.022888 | -0.082397 | -2.3483 | -0.21057 | -0.10071 | 0.28839 | 59.6878 | 58.8409 | 122.3236 | 124.53 | 0.022888 | 124.5712 | 70.7748 | -0.21057 | 124.53 | 0.022888 | 70.7748 | 122.3236 | 124.5712 | -124.9374 | -124.8825
677.375 | 124.9741 | -61.3861 | 63.2767 | -0.21042 | 0.0053256 | 0.011675 | 0.00095067 | 0.065157 | 0.00081181 | 0.069173 | -61.0245 | 63.1805 | -61.6516 | -61.4594 | 60.6125 | 8.963 | -1.7166 | -2.71 | 63.1393 | -61.6104 | -0.2655 | -0.09613 | 0.36163 | -0.073243 | -2.6642 | -0.22431 | -0.13733 | 0.62714 | 59.6695 | 58.6761 | 121.9986 | 124.5667 | 0.36163 | 124.5255 | 70.3491 | -0.22431 | 124.5667 | 0.36163 | 70.3491 | 121.9986 | 124.5255 | -124.9283 | -124.8871
678.375 | 124.8505 | -61.4044 | 63.3041 | -0.24857 | 0.01558 | 0.012956 | 0.0071457 | 0.066652 | 0.00038461 | 0.068746 | -61.3495 | 63.2538 | -61.6562 | -61.5829 | 60.2234 | 8.5831 | -1.6251 | -3.0212 | 63.208 | -61.6791 | -0.25177 | -0.050354 | 0.054932 | -0.17853 | -3.0807 | -0.27466 | -0.09613 | 0.3067 | 59.7794 | 58.3832 | 121.6278 | 124.6582 | 0.054932 | 124.6124 | 69.9875 | -0.27466 | 124.6582 | 0.054932 | 69.9875 | 121.6278 | 124.6124 | -124.9603 | -124.9832
679.375 | 124.9191 | -62.1735 | 62.5031 | -0.088349 | 0.01088 | 0.016801 | 0.0015915 | 0.066439 | 0.00017081 | 0.069387 | -62.0865 | 62.4023 | -62.4161 | -62.2925 | 59.024 | 6.7154 | -1.8036 | -3.067 | 62.4115 | -62.3749 | -0.24262 | -0.10071 | 0.086975 | -0.11902 | -3.479 | -0.20142 | -0.091553 | 0.32959 | 60.3699 | 59.1064 | 121.1975 | 124.5758 | 0.086975 | 124.585 | 68.8889 | -0.20142 | 124.5758 | 0.086975 | 68.8889 | 121.1975 | 124.585 | -124.9191 | -124.8779
680.375 | 125.1709 | -62.3657 | 62.2925 | -0.14938 | 0.010025 | 0.016161 | 0.0024461 | 0.066012 | 0.0018798 | 0.071309 | -62.2696 | 62.1368 | -62.6495 | -62.4802 | 58.429 | 5.8685 | -1.7075 | -2.8976 | 62.1735 | -62.5809 | -0.28381 | -0.15564 | 0.096131 | -0.11444 | -3.8635 | -0.21515 | -0.11902 | 0.37994 | 60.6583 | 59.4681 | 120.7947 | 124.5026 | 0.096131 | 124.5392 | 68.2343 | -0.21515 | 124.5026 | 0.096131 | 68.2343 | 120.7947 | 124.5392 | -124.942 | -124.8734
681.375 | 124.9329 | -62.1094 | 62.5488 | -0.23331 | 0.011521 | 0.015733 | 0.0030869 | 0.065584 | -0.00089719 | 0.069814 | -61.9125 | 62.4527 | -62.3428 | -62.1643 | 58.5251 | 5.5115 | -1.7487 | -3.0808 | 62.439 | -62.3108 | -0.23346 | -0.09613 | 0.19684 | -0.054932 | -4.0237 | -0.20142 | -0.10986 | 0.4303 | 60.3607 | 59.0286 | 120.6345 | 124.5621 | 0.19684 | 124.5483 | 67.6209 | -0.20142 | 124.5621 | 0.19684 | 67.6209 | 120.6345 | 124.5483 | -124.8917 | -124.8596
682.375 | 124.9374 | -61.9125 | 62.7365 | -0.095978 | 0.010239 | 0.010179 | 0.0030869 | 0.064089 | 0.00017081 | 0.0696 | -61.7065 | 62.6541 | -62.1414 | -62.0087 | 58.2138 | 5.0583 | -1.8265 | -3.2684 | 62.6587 | -62.1323 | -0.22888 | -0.082397 | 0.20599 | -0.09613 | -4.5227 | -0.21973 | -0.07782 | 0.43487 | 60.0861 | 58.6441 | 120.1263 | 124.5667 | 0.20599 | 124.5712 | 66.9708 | -0.21973 | 124.5667 | 0.20599 | 66.9708 | 120.1263 | 124.5712 | -124.8779 | -124.8688
683.3906 | 124.855 | -61.7065 | 62.9517 | -0.14938 | 0.015152 | 0.014665 | 0.010136 | 0.06708 | 0.001239 | 0.071523 | -61.4456 | 62.9745 | -61.9354 | -61.8118 | 57.9941 | 4.6509 | -1.8677 | -3.5843 | 62.9059 | -61.9537 | -0.22888 | 0.022888 | 0.26093 | -0.10529 | -4.9576 | -0.24719 | -0.045776 | 0.48981 | 59.8389 | 58.1223 | 119.7006 | 124.6811 | 0.26093 | 124.6124 | 66.3574 | -0.24719 | 124.6811 | 0.26093 | 66.3574 | 119.7006 | 124.6124 | -124.8871 | -124.9054
684.375 | 124.8917 | -61.6837 | 62.9608 | -0.11887 | 0.013016 | 0.014665 | 0.0013779 | 0.067293 | 0.00038461 | 0.070455 | -62.5809 | 62.114 | -62.8738 | -61.4456 | 57.9163 | 4.5685 | -2.0233 | -4.1153 | 62.9745 | -61.8668 | -1.1902 | -0.84686 | -0.89722 | 0.23804 | -5.0446 | -0.1831 | 0.013733 | 0.29297 | 59.6603 | 57.5684 | 119.5999 | 123.7976 | -0.89722 | 124.6582 | 66.2521 | -0.1831 | 123.7976 | -0.89722 | 66.2521 | 119.5999 | 124.6582 | -125.8347 | -124.8276
685.375 | 124.9329 | -60.7956 | 63.8351 | -0.14938 | 0.012162 | 0.007402 | 0.0015915 | 0.06473 | -0.0019654 | 0.07195 | -60.553 | 63.7253 | -61.0931 | -60.8597 | 57.5684 | 4.1382 | -1.9913 | -4.2526 | 63.7299 | -61.0291 | -0.29755 | -0.10986 | 0.24261 | -0.064087 | -6.2668 | -0.23346 | -0.10529 | 0.54016 | 58.8043 | 56.543 | 118.364 | 124.5209 | 0.24261 | 124.5255 | 64.9338 | -0.23346 | 124.5209 | 0.24261 | 64.9338 | 118.364 | 124.5255 | -124.9283 | -124.8642
686.375 | 125.0977 | -60.2646 | 64.357 | -0.14938 | 0.012589 | 0.014452 | 0.0020187 | 0.065584 | -0.00089719 | 0.071737 | -59.9579 | 64.238 | -60.5484 | -60.4065 | 57.8247 | 4.0649 | -2.0737 | -4.2847 | 64.2471 | -60.5118 | -0.28381 | -0.11902 | 0.3067 | -0.14191 | -6.5323 | -0.24719 | -0.10986 | 0.59051 | 58.1909 | 55.9799 | 118.0893 | 124.5026 | 0.3067 | 124.5117 | 64.3295 | -0.24719 | 124.5026 | 0.3067 | 64.3295 | 118.0893 | 124.5117 | -124.9054 | -124.8688
687.375 | 124.9191 | -59.8114 | 64.8514 | -0.27908 | 0.012589 | 0.011461 | 0.0013779 | 0.066439 | 0.00081181 | 0.069814 | -59.4498 | 64.7186 | -60.0861 | -59.9167 | 57.8293 | 3.6209 | -1.886 | -4.3396 | 64.7095 | -60.0403 | -0.27466 | -0.13275 | 0.36163 | -0.10529 | -7.0221 | -0.22888 | -0.14191 | 0.63629 | 57.9254 | 55.4718 | 117.6407 | 124.53 | 0.36163 | 124.5209 | 63.4323 | -0.22888 | 124.53 | 0.36163 | 63.4323 | 117.6407 | 124.5209 | -124.9374 | -124.8917
688.3906 | 124.7864 | -59.4727 | 65.2817 | -0.21042 | 0.01323 | 0.018724 | 0.011632 | 0.06708 | 0.00059821 | 0.070241 | -58.9874 | 65.181 | -59.6649 | -60.0082 | 57.3441 | 3.3783 | -1.6891 | -4.4449 | 65.0253 | -59.7885 | -0.19226 | -0.10071 | 0.48523 | -0.53558 | -7.9376 | -0.31586 | -0.25635 | 0.67749 | 57.7835 | 55.0278 | 116.8167 | 124.6536 | 0.48523 | 124.498 | 62.851 | -0.31586 | 124.6536 | 0.48523 | 62.851 | 116.8167 | 124.498 | -124.9466 | -125.0702
689.375 | 124.8871 | -83.2169 | 41.391 | -0.050202 | 0.0093844 | 0.014238 | 0.0052231 | 0.069216 | 0.010638 | 0.073018 | -82.4661 | 41.3681 | -83.4961 | -83.3038 | 18.2877 | -3.2639 | -2.6733 | -6.8573 | 41.3818 | -83.4183 | -0.27924 | -0.022888 | 0.75073 | -0.086975 | -23.1033 | -0.20142 | -0.009155 | 1.03 | 80.5435 | 76.3596 | 101.5045 | 124.585 | 0.75073 | 124.5987 | 79.953 | -0.20142 | 124.585 | 0.75073 | 79.953 | 101.5045 | 124.5987 | -124.8871 | -124.8093
690.375 | 124.9741 | -82.5943 | 42.0456 | -0.24094 | 0.011307 | 0.01552 | 0.00095067 | 0.068148 | 0.0099976 | 0.072591 | -81.9534 | 41.7297 | -83.0383 | -82.6721 | 17.894 | -3.2455 | -2.6871 | -6.6696 | 41.9403 | -82.8094 | -0.44403 | -0.31586 | 0.64087 | -0.07782 | -24.1516 | -0.21515 | -0.10528 | 1.0849 | 79.9072 | 75.9247 | 100.4883 | 124.324 | 0.64087 | 124.5346 | 79.3488 | -0.21515 | 124.324 | 0.64087 | 79.3488 | 100.4883 | 124.5346 | -125.0839 | -124.855
691.375 | 124.9283 | -83.139 | 41.4505 | -0.15701 | 0.013871 | 0.012315 | 0.0018051 | 0.067507 | 0.010852 | 0.073446 | -82.2235 | 41.3956 | -83.4229 | -83.2077 | 15.6784 | -3.6987 | -2.5955 | -6.5414 | 41.4047 | -83.3771 | -0.28381 | -0.054931 | 0.91553 | -0.068665 | -25.7721 | -0.23804 | -0.045776 | 1.1993 | 80.5435 | 76.5976 | 98.8174 | 124.5346 | 0.91553 | 124.5438 | 79.4403 | -0.23804 | 124.5346 | 0.91553 | 79.4403 | 98.8174 | 124.5438 | -124.8734 | -124.8276
692.4375 | 124.8276 | -81.4453 | 43.2587 | -0.042572 | 0.01558 | 0.018724 | 0.010777 | 0.068361 | 0.011066 | 0.074087 | -80.4428 | 43.2037 | -81.7291 | -81.5643 | 17.1387 | -3.6713 | -2.3621 | -6.3812 | 43.1717 | -81.7154 | -0.28381 | -0.054932 | 1.0025 | -0.11902 | -26.12 | -0.27008 | -0.086975 | 1.2863 | 79.0833 | 75.0641 | 98.584 | 124.649 | 1.0025 | 124.617 | 77.774 | -0.27008 | 124.649 | 1.0025 | 77.774 | 98.584 | 124.617 | -124.9878 | -124.9741
693.3906 | 124.8642 | -76.03 | 48.6969 | -0.16464 | 0.011734 | 0.017442 | 0.0094955 | 0.069002 | 0.010425 | 0.073232 | -74.9634 | 48.6053 | -76.2634 | -76.0712 | 24.7604 | -2.5497 | -2.179 | -5.8182 | 48.642 | -76.2131 | -0.23346 | -0.091552 | 1.0666 | -0.041199 | -23.9365 | -0.18311 | -0.054931 | 1.3 | 73.851 | 70.2118 | 100.7904 | 124.6353 | 1.0666 | 124.6719 | 73.4802 | -0.18311 | 124.6353 | 1.0666 | 73.4802 | 100.7904 | 124.6719 | -124.9603 | -124.91
694.375 | 124.7772 | -76.6525 | 47.9736 | -0.13412 | 0.012589 | 0.012956 | -0.00075833 | 0.071352 | 0.011493 | 0.074941 | -75.5402 | 47.8592 | -76.9226 | -76.7761 | 22.1603 | -2.7054 | -2.092 | -5.397 | 47.8729 | -76.8814 | -0.27008 | -0.11444 | 1.1124 | -0.1236 | -25.8133 | -0.22888 | -0.10071 | 1.3824 | 74.5605 | 71.2555 | 98.8129 | 124.5117 | 1.1124 | 124.5255 | 73.9471 | -0.22888 | 124.5117 | 1.1124 | 73.9471 | 98.8129 | 124.5255 | -124.8962 | -124.855
695.375 | 124.9466 | -76.5152 | 48.111 | -0.088349 | 0.011093 | 0.014452 | 0.0011643 | 0.067934 | 0.012775 | 0.075155 | -75.2609 | 48.0103 | -76.7899 | -76.6296 | 20.6589 | -2.98 | -2.005 | -5.2872 | 48.0194 | -76.767 | -0.27466 | -0.10071 | 1.2543 | -0.11444 | -27.4521 | -0.25177 | -0.091553 | 1.5289 | 74.5102 | 71.228 | 97.1741 | 124.5255 | 1.2543 | 124.5346 | 73.5352 | -0.25177 | 124.5255 | 1.2543 | 73.5352 | 97.1741 | 124.5346 | -124.9008 | -124.8779
696.4375 | 124.6399 | -79.4632 | 45.2408 | -0.027313 | 0.013016 | 0.01552 | 0.012059 | 0.071139 | 0.01427 | 0.073873 | -78.0441 | 45.1996 | -79.7058 | -79.6738 | 13.4125 | -4.1016 | -1.9409 | -5.8502 | 45.163 | -79.7379 | -0.24262 | -0.041199 | 1.4191 | -0.21057 | -31.8283 | -0.27466 | -0.07782 | 1.6617 | 77.5223 | 73.613 | 92.8757 | 124.6628 | 1.4191 | 124.6262 | 75.3616 | -0.27466 | 124.6628 | 1.4191 | 75.3616 | 92.8757 | 124.6262 | -124.9466 | -124.9786
697.375 | 124.9237 | -75.3387 | 49.3103 | -0.06546 | 0.0095982 | 0.02086 | 0.00095067 | 0.066225 | 0.012561 | 0.07665 | -73.938 | 49.1821 | -75.6363 | -75.4807 | 18.8004 | -3.3005 | -1.9501 | -5.4428 | 49.2325 | -75.5768 | -0.29755 | -0.12817 | 1.4008 | -0.14191 | -30.5099 | -0.23804 | -0.07782 | 1.6983 | 73.3887 | 69.8959 | 94.1391 | 124.5209 | 1.4008 | 124.5712 | 72.0383 | -0.23804 | 124.5209 | 1.4008 | 72.0383 | 94.1391 | 124.5712 | -124.9466 | -124.8871
698.375 | 124.91 | -80.7587 | 43.8812 | -0.057831 | 0.011307 | 0.016374 | 0.0015915 | 0.066866 | 0.01897 | 0.078145 | -79.1016 | 43.7576 | -81.0516 | -80.8777 | 6.7749 | -4.8614 | -2.0828 | -5.9601 | 43.7942 | -80.9921 | -0.29297 | -0.1236 | 1.6571 | -0.11902 | -37.1063 | -0.23346 | -0.086976 | 1.9501 | 78.6758 | 74.7986 | 87.5336 | 124.5163 | 1.6571 | 124.5529 | 75.8972 | -0.23346 | 124.5163 | 1.6571 | 75.8972 | 87.5336 | 124.5529 | -124.9329 | -124.8734
699.375 | 124.9008 | -80.0262 | 44.6411 | 0.0032044 | 0.010666 | 0.01851 | 0.0035141 | 0.064944 | 0.017047 | 0.077077 | -78.1998 | 44.5404 | -80.2689 | -80.1544 | 5.6168 | -5.0629 | -2.0279 | -5.9418 | 44.5862 | -80.2505 | -0.24262 | -0.10071 | 1.8265 | -0.12817 | -39.0244 | -0.2243 | -0.054931 | 2.0691 | 77.9984 | 74.0845 | 85.643 | 124.5667 | 1.8265 | 124.6124 | 74.9634 | -0.2243 | 124.5667 | 1.8265 | 74.9634 | 85.643 | 124.6124 | -124.91 | -124.8917
700.375 | 124.9054 | -72.4457 | 52.2263 | 0.14053 | 0.010666 | 0.021501 | 0.0052231 | 0.067721 | 0.019183 | 0.079 | -70.6238 | 52.121 | -72.6517 | -72.583 | 17.395 | -3.5751 | -1.8219 | -5.2734 | 52.1072 | -72.6654 | -0.20599 | -0.10528 | 1.8219 | -0.13733 | -34.8312 | -0.21973 | -0.11902 | 2.0279 | 70.6238 | 67.1722 | 89.8407 | 124.5667 | 1.8219 | 124.5529 | 68.8705 | -0.21973 | 124.5667 | 1.8219 | 68.8705 | 89.8407 | 124.5529 | -124.8779 | -124.8917
701.375 | 124.8688 | -79.1061 | 45.5521 | 0.10239 | 0.011734 | 0.01851 | 0.0024461 | 0.066439 | 0.022815 | 0.079427 | -77.2064 | 45.4056 | -79.4403 | -79.2343 | 2.6138 | -5.5298 | -2.005 | -5.8411 | 45.4788 | -79.3213 | -0.33417 | -0.14648 | 1.8997 | -0.12817 | -42.9382 | -0.21515 | -0.073242 | 2.2339 | 77.1011 | 73.2651 | 81.72 | 124.5117 | 1.8997 | 124.585 | 73.5764 | -0.21515 | 124.5117 | 1.8997 | 73.5764 | 81.72 | 124.585 | -124.9924 | -124.8734
702.375 | 124.9191 | -78.5065 | 46.1426 | 0.10239 | 0.014298 | 0.024706 | 0.0065049 | 0.066439 | 0.024524 | 0.079854 | -76.3229 | 45.9457 | -78.8635 | -78.6163 | 1.1536 | -5.6992 | -2.0233 | -5.7953 | 46.0419 | -78.7308 | -0.35706 | -0.19684 | 2.1835 | -0.10986 | -44.989 | -0.2243 | -0.10071 | 2.5406 | 76.4832 | 72.7112 | 79.66 | 124.4522 | 2.1835 | 124.5483 | 72.8073 | -0.2243 | 124.4522 | 2.1835 | 72.8073 | 79.66 | 124.5483 | -125.0061 | -124.8734
703.375 | 124.8779 | -77.0782 | 47.525 | 0.11765 | 0.015152 | 0.022142 | 0.0052231 | 0.069643 | 0.022174 | 0.079641 | -74.6567 | 47.4243 | -77.3483 | -77.1835 | 0.65918 | -5.7678 | -1.9821 | -5.7129 | 47.4472 | -77.33 | -0.27008 | -0.10071 | 2.4216 | -0.10529 | -46.8658 | -0.25177 | -0.077819 | 2.6917 | 75.0961 | 71.3654 | 77.7374 | 124.5026 | 2.4216 | 124.5255 | 71.3104 | -0.25177 | 124.5026 | 2.4216 | 71.3104 | 77.7374 | 124.5255 | -124.8734 | -124.855
704.375 | 124.9283 | -75.3662 | 49.2371 | 0.041351 | 0.012162 | 0.025346 | 0.0047959 | 0.066439 | 0.023029 | 0.079854 | -72.8943 | 49.1089 | -75.705 | -75.5539 | 0.76904 | -5.6625 | -1.8356 | -5.6396 | 49.1409 | -75.65 | -0.33874 | -0.12817 | 2.4719 | -0.18768 | -48.468 | -0.28381 | -0.096131 | 2.8107 | 73.5306 | 69.7266 | 76.1353 | 124.4751 | 2.4719 | 124.5071 | 69.7037 | -0.28381 | 124.4751 | 2.4719 | 69.7037 | 76.1353 | 124.5071 | -124.942 | -124.8871
705.375 | 124.9008 | -74.5239 | 50.0977 | 0.12527 | 0.013016 | 0.02791 | 0.0065049 | 0.069002 | 0.024097 | 0.081991 | -71.7453 | 49.9924 | -74.7894 | -74.6338 | 0.35248 | -5.4703 | -1.7258 | -5.4153 | 50.0061 | -74.7665 | -0.2655 | -0.10529 | 2.7786 | -0.10986 | -49.7452 | -0.24262 | -0.091552 | 3.0441 | 72.7982 | 69.1086 | 74.8764 | 124.5163 | 2.7786 | 124.53 | 69.0537 | -0.24262 | 124.5163 | 2.7786 | 69.0537 | 74.8764 | 124.53 | -124.8871 | -124.8642
706.375 | 124.9008 | -73.1232 | 51.4755 | 0.15579 | 0.014939 | 0.02556 | 0.0077865 | 0.067293 | 0.026233 | 0.081777 | -70.134 | 51.3886 | -73.3887 | -73.2422 | 0.24719 | -5.365 | -1.6617 | -5.2872 | 51.4069 | -73.3887 | -0.2655 | -0.086975 | 2.9892 | -0.11902 | -51.2283 | -0.2655 | -0.068665 | 3.2547 | 71.4615 | 67.836 | 73.3704 | 124.5117 | 2.9892 | 124.53 | 67.7582 | -0.2655 | 124.5117 | 2.9892 | 67.7582 | 73.3704 | 124.53 | -124.8642 | -124.8642
707.375 | 124.9557 | -71.6858 | 52.9449 | 0.18631 | 0.011093 | 0.024919 | 0.0058639 | 0.067507 | 0.025165 | 0.0837 | -68.5135 | 52.8122 | -71.9284 | -71.7865 | 0.37994 | -5.2551 | -1.6251 | -5.1498 | 52.8488 | -71.9284 | -0.24262 | -0.13275 | 3.1723 | -0.10071 | -52.565 | -0.24262 | -0.09613 | 3.4149 | 70.0607 | 66.5359 | 72.0657 | 124.498 | 3.1723 | 124.5346 | 66.4307 | -0.24262 | 124.498 | 3.1723 | 66.4307 | 72.0657 | 124.5346 | -124.8734 | -124.8734
708.375 | 124.9237 | -70.5002 | 54.1077 | 0.10239 | 0.013016 | 0.023851 | 0.0050095 | 0.068361 | 0.027515 | 0.084127 | -67.2318 | 54.0161 | -70.7886 | -70.6238 | 0.26093 | -5.2689 | -1.5381 | -5.0537 | 54.0436 | -70.7565 | -0.28839 | -0.091553 | 3.2684 | -0.1236 | -53.8467 | -0.25635 | -0.064087 | 3.5568 | 68.9621 | 65.4465 | 70.7611 | 124.5163 | 3.2684 | 124.5438 | 65.2313 | -0.25635 | 124.5163 | 3.2684 | 65.2313 | 70.7611 | 124.5438 | -124.8962 | -124.8642
709.375 | 124.8871 | -69.1956 | 55.426 | 0.14816 | 0.013443 | 0.025346 | 0.0065049 | 0.067934 | 0.02901 | 0.083486 | -65.7578 | 55.3207 | -69.4794 | -69.31 | 0.19684 | -5.2139 | -1.4877 | -4.921 | 55.3482 | -69.429 | -0.28381 | -0.10529 | 3.4378 | -0.11444 | -55.2292 | -0.23346 | -0.077819 | 3.7216 | 67.7078 | 64.2746 | 69.3924 | 124.5163 | 3.4378 | 124.5438 | 63.9816 | -0.23346 | 124.5163 | 3.4378 | 63.9816 | 69.3924 | 124.5438 | -124.9054 | -124.855
710.375 | 124.9146 | -68.042 | 56.5567 | 0.14816 | 0.011307 | 0.028123 | 0.0071457 | 0.068789 | 0.025806 | 0.084554 | -64.4989 | 56.4697 | -68.3395 | -68.1885 | 0.16479 | -5.246 | -1.474 | -4.8843 | 56.4743 | -68.3212 | -0.29755 | -0.086975 | 3.5431 | -0.14649 | -56.3919 | -0.27924 | -0.082398 | 3.8406 | 66.568 | 63.1577 | 68.2068 | 124.5117 | 3.5431 | 124.5163 | 62.796 | -0.27924 | 124.5117 | 3.5431 | 62.796 | 68.2068 | 124.5163 | -124.8962 | -124.8779
711.375 | 124.91 | -66.8198 | 57.7835 | 0.1329 | 0.013016 | 0.029192 | 0.0058639 | 0.069643 | 0.028583 | 0.085195 | -63.1805 | 57.6782 | -67.0944 | -66.9434 | 0.16937 | -5.2826 | -1.4191 | -4.834 | 57.692 | -67.0944 | -0.27466 | -0.10528 | 3.6392 | -0.1236 | -57.6141 | -0.27466 | -0.091552 | 3.9139 | 65.4007 | 61.9858 | 66.9891 | 124.498 | 3.6392 | 124.5117 | 61.5372 | -0.27466 | 124.498 | 3.6392 | 61.5372 | 66.9891 | 124.5117 | -124.8779 | -124.8779
712.375 | 124.8871 | -65.7211 | 58.8684 | 0.11002 | 0.014725 | 0.03261 | 0.0080003 | 0.067721 | 0.02901 | 0.084127 | -61.9904 | 58.786 | -66.0233 | -65.8585 | 0.16937 | -5.3101 | -1.4374 | -4.8111 | 58.786 | -65.9729 | -0.30212 | -0.082397 | 3.7308 | -0.13733 | -58.699 | -0.25177 | -0.082397 | 4.0329 | 64.2838 | 60.91 | 65.8905 | 124.5071 | 3.7308 | 124.5071 | 60.4111 | -0.25177 | 124.5071 | 3.7308 | 60.4111 | 65.8905 | 124.5071 | -124.8917 | -124.8413
713.375 | 124.9146 | -64.476 | 60.1501 | 0.14053 | 0.012375 | 0.02791 | 0.0080003 | 0.067934 | 0.029437 | 0.085836 | -60.6354 | 60.0586 | -64.7186 | -64.5767 | 0.17395 | -5.3009 | -1.4282 | -4.8294 | 60.0632 | -64.7232 | -0.24262 | -0.091552 | 3.8406 | -0.10071 | -59.9762 | -0.24719 | -0.086975 | 4.0833 | 63.0478 | 59.6466 | 64.65 | 124.5346 | 3.8406 | 124.5392 | 59.1751 | -0.24719 | 124.5346 | 3.8406 | 59.1751 | 64.65 | 124.5392 | -124.8688 | -124.8734
714.375 | 124.91 | -63.0798 | 61.5463 | 0.12527 | 0.011734 | 0.028551 | 0.0043687 | 0.06708 | 0.031787 | 0.085622 | -59.166 | 61.4365 | -63.3499 | -63.2263 | 0.16022 | -5.3101 | -1.3779 | -4.7104 | 61.4594 | -63.3545 | -0.27008 | -0.10986 | 3.9139 | -0.14648 | -61.3861 | -0.27466 | -0.086975 | 4.184 | 61.702 | 58.3694 | 63.2401 | 124.5163 | 3.9139 | 124.5392 | 57.7698 | -0.27466 | 124.5163 | 3.9139 | 57.7698 | 63.2401 | 124.5392 | -124.8962 | -124.9008
715.375 | 124.8734 | -61.7752 | 62.8235 | 0.1329 | 0.014725 | 0.032182 | 0.0028733 | 0.067721 | 0.03136 | 0.086904 | -57.692 | 62.7457 | -62.0636 | -61.908 | 0.16937 | -5.3558 | -1.4008 | -4.6463 | 62.7365 | -62.0407 | -0.28839 | -0.077819 | 4.0833 | -0.13275 | -62.6541 | -0.2655 | -0.086975 | 4.3716 | 60.3745 | 57.1289 | 61.9446 | 124.5209 | 4.0833 | 124.5117 | 56.4194 | -0.2655 | 124.5209 | 4.0833 | 56.4194 | 61.9446 | 124.5117 | -124.8871 | -124.8642
716.375 | 124.8962 | -60.6216 | 63.9862 | 0.20157 | 0.013871 | 0.032182 | 0.0067185 | 0.068148 | 0.030719 | 0.088399 | -56.5155 | 63.9267 | -60.9283 | -60.8276 | 0.13275 | -5.3375 | -1.355 | -4.6555 | 63.9084 | -60.8963 | -0.3067 | -0.059509 | 4.1061 | -0.20599 | -63.8535 | -0.27466 | -0.07782 | 4.4128 | 59.2667 | 55.9662 | 60.7544 | 124.5483 | 4.1061 | 124.53 | 55.2841 | -0.27466 | 124.5483 | 4.1061 | 55.2841 | 60.7544 | 124.53 | -124.9146 | -124.8825
717.375 | 124.9008 | -59.6558 | 64.9796 | 0.12527 | 0.014511 | 0.031755 | 0.0062913 | 0.068361 | 0.033069 | 0.088186 | -55.4031 | 64.9475 | -59.9533 | -59.8206 | 0.1236 | -5.3604 | -1.3138 | -4.5822 | 64.9017 | -59.9304 | -0.29755 | -0.032043 | 4.2526 | -0.16479 | -64.856 | -0.27466 | -0.07782 | 4.5502 | 58.342 | 55.0735 | 59.7794 | 124.6033 | 4.2526 | 124.5575 | 54.2953 | -0.27466 | 124.6033 | 4.2526 | 54.2953 | 59.7794 | 124.5575 | -124.9329 | -124.91
718.375 | 124.9191 | -58.6258 | 65.9821 | 0.048981 | 0.012375 | 0.035387 | 0.0084275 | 0.071352 | 0.032428 | 0.088186 | -54.1992 | 65.9592 | -58.8547 | -58.7997 | -0.13275 | -5.484 | -1.1078 | -4.3579 | 65.9088 | -58.8821 | -0.22888 | -0.022889 | 4.4266 | -0.17395 | -66.1148 | -0.25635 | -0.073243 | 4.6555 | 57.518 | 54.2679 | 58.493 | 124.585 | 4.4266 | 124.5346 | 53.1418 | -0.25635 | 124.585 | 4.4266 | 53.1418 | 58.493 | 124.5346 | -124.8367 | -124.8642
719.375 | 124.9191 | -57.637 | 66.9708 | 0.23209 | 0.014298 | 0.034532 | 0.0077865 | 0.069643 | 0.032855 | 0.090108 | -53.1601 | 66.9159 | -57.9254 | -57.7927 | 0.15106 | -5.2322 | -1.3 | -4.2572 | 66.8838 | -57.9025 | -0.28839 | -0.054931 | 4.4769 | -0.15564 | -66.8198 | -0.2655 | -0.086975 | 4.7653 | 56.337 | 53.3798 | 57.7881 | 124.5529 | 4.4769 | 124.5209 | 52.4048 | -0.2655 | 124.5529 | 4.4769 | 52.4048 | 57.7881 | 124.5209 | -124.8962 | -124.8734
720.375 | 124.9008 | -56.7444 | 67.8864 | 0.23972 | 0.014084 | 0.032182 | 0.0071457 | 0.070925 | 0.03371 | 0.087545 | -52.2354 | 67.8268 | -57.0419 | -56.9138 | 0.13733 | -5.0354 | -1.1902 | -4.1565 | 67.8131 | -57.0007 | -0.29755 | -0.05951 | 4.509 | -0.16937 | -67.749 | -0.25635 | -0.073243 | 4.8065 | 55.5542 | 52.5879 | 56.8817 | 124.5712 | 4.509 | 124.5575 | 51.709 | -0.25635 | 124.5712 | 4.509 | 51.709 | 56.8817 | 124.5575 | -124.9283 | -124.8871
721.375 | 124.8413 | -55.7785 | 68.866 | 0.14053 | 0.014725 | 0.036455 | 0.0097091 | 0.070711 | 0.034991 | 0.088827 | -51.2009 | 68.8705 | -56.0211 | -55.9708 | 0.073242 | -4.953 | -1.1078 | -4.0924 | 68.8065 | -56.0394 | -0.24262 | 0.004577 | 4.5776 | -0.19226 | -68.7927 | -0.26093 | -0.059509 | 4.8203 | 54.6707 | 51.6861 | 55.8517 | 124.649 | 4.5776 | 124.585 | 50.8255 | -0.26093 | 124.649 | 4.5776 | 50.8255 | 55.8517 | 124.585 | -124.8871 | -124.9054
722.375 | 125.0015 | -54.8264 | 69.8318 | 0.05661 | 0.013657 | 0.032182 | 0.0062913 | 0.070284 | 0.037555 | 0.088827 | -50.0565 | 69.7815 | -55.0507 | -54.9179 | 0.14191 | -4.7928 | -1.1627 | -4.0924 | 69.7586 | -55.0735 | -0.2243 | -0.050354 | 4.7699 | -0.091553 | -69.6899 | -0.24719 | -0.073242 | 4.9942 | 53.6636 | 50.7339 | 54.9683 | 124.6078 | 4.7699 | 124.585 | 50.0336 | -0.24719 | 124.6078 | 4.7699 | 50.0336 | 54.9683 | 124.585 | -124.8825 | -124.9054
723.375 | 124.8459 | -53.6819 | 70.9579 | 0.1329 | 0.013443 | 0.030901 | 0.0071457 | 0.06943 | 0.039905 | 0.092885 | -48.9532 | 70.9534 | -53.9474 | -53.9291 | 0.036621 | -4.8477 | -1.0071 | -4.0192 | 70.8847 | -53.9566 | -0.2655 | -0.004578 | 4.7287 | -0.24719 | -70.9213 | -0.27466 | -0.073242 | 4.9942 | 52.6749 | 49.6628 | 53.7186 | 124.6353 | 4.7287 | 124.5667 | 48.8342 | -0.27466 | 124.6353 | 4.7287 | 48.8342 | 53.7186 | 124.5667 | -124.9054 | -124.9146
724.375 | 124.8001 | -52.7573 | 71.9238 | 0.079498 | 0.017929 | 0.031969 | 0.0084275 | 0.069002 | 0.037769 | 0.091604 | -48.1522 | 71.933 | -52.9999 | -52.977 | 0.009155 | -4.7653 | -0.97504 | -3.9139 | 71.8735 | -53.0045 | -0.24262 | 0.009155 | 4.6051 | -0.21973 | -71.9147 | -0.24719 | -0.050354 | 4.8477 | 51.7822 | 48.8434 | 52.7664 | 124.6902 | 4.6051 | 124.6307 | 47.9919 | -0.24719 | 124.6902 | 4.6051 | 47.9919 | 52.7664 | 124.6307 | -124.9237 | -124.9283
725.375 | 124.8413 | -51.8326 | 72.7936 | 0.18631 | 0.014725 | 0.034319 | 0.0062913 | 0.070284 | 0.0367 | 0.090536 | -46.9986 | 72.7707 | -52.0798 | -52.034 | 0.068665 | -4.6555 | -0.99792 | -3.7445 | 72.7524 | -52.0981 | -0.24719 | -0.022888 | 4.834 | -0.20142 | -72.7249 | -0.2655 | -0.041199 | 5.0812 | 50.8347 | 48.0881 | 51.9012 | 124.6033 | 4.834 | 124.585 | 47.1771 | -0.2655 | 124.6033 | 4.834 | 47.1771 | 51.9012 | 124.585 | -124.8734 | -124.8917
726.375 | 124.855 | -50.8759 | 73.7457 | 0.12527 | 0.016648 | 0.039659 | 0.0069321 | 0.06943 | 0.0367 | 0.093526 | -45.9412 | 73.7503 | -51.178 | -51.1093 | 0.036621 | -4.5868 | -0.94299 | -3.6209 | 73.6862 | -51.1368 | -0.30213 | 0.004577 | 4.9347 | -0.23346 | -73.7091 | -0.26093 | -0.05951 | 5.2368 | 49.9329 | 47.2549 | 50.9125 | 124.6262 | 4.9347 | 124.5621 | 46.2891 | -0.26093 | 124.6262 | 4.9347 | 46.2891 | 50.9125 | 124.5621 | -124.9237 | -124.8825
727.375 | 124.8184 | -50.1389 | 74.5193 | 0.1329 | 0.016434 | 0.039659 | 0.0073593 | 0.069857 | 0.036914 | 0.093953 | -45.1767 | 74.5056 | -50.4364 | -50.3723 | 0.045776 | -4.4403 | -0.90637 | -3.5431 | 74.4553 | -50.4044 | -0.29755 | -0.013733 | 4.9622 | -0.23346 | -74.4736 | -0.2655 | -0.064087 | 5.2597 | 49.2325 | 46.5958 | 50.1846 | 124.6445 | 4.9622 | 124.5941 | 45.6985 | -0.2655 | 124.6445 | 4.9622 | 45.6985 | 50.1846 | 124.5941 | -124.9557 | -124.9237
728.375 | 124.7726 | -49.4888 | 75.1923 | 0.16342 | 0.015366 | 0.036241 | 0.0054367 | 0.070925 | 0.03905 | 0.091817 | -44.339 | 75.1694 | -49.7543 | -49.7177 | 0.036621 | -4.2572 | -0.84686 | -3.511 | 75.1282 | -49.7772 | -0.2655 | -0.022888 | 5.1498 | -0.22888 | -75.1556 | -0.28839 | -0.064087 | 5.4153 | 48.642 | 45.9778 | 49.5255 | 124.6582 | 5.1498 | 124.617 | 45.2316 | -0.28839 | 124.6582 | 5.1498 | 45.2316 | 49.5255 | 124.617 | -124.9466 | -124.9695
729.375 | 124.8871 | -48.3673 | 76.268 | 0.18631 | 0.012375 | 0.039873 | 0.0071457 | 0.071139 | 0.039905 | 0.095449 | -43.19 | 76.2634 | -48.6374 | -48.5641 | 0.064087 | -4.0512 | -0.90637 | -3.3188 | 76.2177 | -48.6328 | -0.27008 | -0.004577 | 5.1773 | -0.19684 | -76.2039 | -0.2655 | -0.050354 | 5.4474 | 47.4609 | 45.0485 | 48.4314 | 124.6307 | 5.1773 | 124.585 | 44.3161 | -0.2655 | 124.6307 | 5.1773 | 44.3161 | 48.4314 | 124.585 | -124.9054 | -124.9008
730.375 | 124.8138 | -47.3373 | 77.3666 | 0.12527 | 0.015366 | 0.031755 | 0.0084275 | 0.071566 | 0.040546 | 0.093313 | -42.1234 | 77.3438 | -47.58 | -47.5754 | 0.022888 | -4.0466 | -0.75989 | -3.2684 | 77.3209 | -47.5571 | -0.24262 | -0.022888 | 5.2139 | -0.23804 | -77.3438 | -0.21973 | -0.045776 | 5.4565 | 46.5775 | 44.0689 | 47.3602 | 124.6811 | 5.2139 | 124.6582 | 43.2907 | -0.21973 | 124.6811 | 5.2139 | 43.2907 | 47.3602 | 124.6582 | -124.9466 | -124.9237
731.375 | 124.7726 | -46.3486 | 78.3325 | 0.094757 | 0.013657 | 0.033891 | 0.0069321 | 0.071139 | 0.039264 | 0.095662 | -41.1301 | 78.3188 | -46.6187 | -46.5958 | 0 | -3.9734 | -0.737 | -3.1631 | 78.2959 | -46.6049 | -0.27008 | -0.013733 | 5.2185 | -0.24719 | -78.3325 | -0.25635 | -0.036622 | 5.4886 | 45.6116 | 43.1854 | 46.3486 | 124.6674 | 5.2185 | 124.6445 | 42.3752 | -0.25635 | 124.6674 | 5.2185 | 42.3752 | 46.3486 | 124.6445 | -124.9512 | -124.9374
732.375 | 124.8367 | -45.3827 | 79.2709 | 0.14816 | 0.013871 | 0.037737 | 0.0067185 | 0.071779 | 0.03905 | 0.094808 | -40.1917 | 79.2892 | -45.639 | -45.6253 | 0.022888 | -3.8544 | -0.76446 | -3.0258 | 79.2297 | -45.6711 | -0.25635 | 0.018311 | 5.191 | -0.24262 | -79.248 | -0.28839 | -0.041199 | 5.4474 | 44.6182 | 42.3569 | 45.4056 | 124.6719 | 5.191 | 124.6124 | 41.5283 | -0.28839 | 124.6719 | 5.191 | 41.5283 | 45.4056 | 124.6124 | -124.91 | -124.942
733.375 | 124.8367 | -44.4763 | 80.1682 | 0.14053 | 0.015152 | 0.038591 | 0.0056503 | 0.071993 | 0.0414 | 0.095876 | -39.1937 | 80.1727 | -44.7464 | -44.7281 | 0.022888 | -3.7445 | -0.72327 | -2.948 | 80.1682 | -44.7235 | -0.27008 | 0.004577 | 5.2826 | -0.25177 | -80.1453 | -0.24719 | 0 | 5.5527 | 43.7531 | 41.5283 | 44.4992 | 124.649 | 5.2826 | 124.6445 | 40.7318 | -0.24719 | 124.649 | 5.2826 | 40.7318 | 44.4992 | 124.6445 | -124.9146 | -124.8917
734.375 | 124.7955 | -42.1051 | 82.5897 | 0.079498 | 0.014298 | 0.037737 | 0.0073593 | 0.071139 | 0.04375 | 0.095022 | -35.6094 | 82.5851 | -42.334 | -42.3523 | 0.009155 | -3.5614 | -0.65918 | -2.8152 | 82.5485 | -42.3523 | -0.22888 | -0.004578 | 6.4957 | -0.24719 | -82.5806 | -0.24719 | -0.041199 | 6.7245 | 41.4459 | 39.2899 | 42.1143 | 124.6902 | 6.4957 | 124.6536 | 38.5437 | -0.24719 | 124.6902 | 6.4957 | 38.5437 | 42.1143 | 124.6536 | -124.9237 | -124.942
735.375 | 124.7726 | -42.9245 | 81.7703 | 0.15579 | 0.016648 | 0.036028 | 0.0065049 | 0.070711 | 0.044818 | 0.096944 | -37.6419 | 81.7749 | -43.1808 | -43.1671 | 0.004578 | -3.5751 | -0.65918 | -2.8061 | 81.72 | -43.1808 | -0.25635 | 0.004577 | 5.2826 | -0.24261 | -81.7657 | -0.25635 | -0.050354 | 5.5389 | 42.2653 | 40.1184 | 42.9291 | 124.6994 | 5.2826 | 124.6445 | 39.3494 | -0.25635 | 124.6994 | 5.2826 | 39.3494 | 42.9291 | 124.6445 | -124.9512 | -124.9512
736.375 | 124.8596 | -42.2058 | 82.4478 | 0.16342 | 0.015152 | 0.039018 | 0.0058639 | 0.069857 | 0.042895 | 0.094167 | -36.8591 | 82.4203 | -42.4713 | -42.4255 | 0.054932 | -3.36 | -0.67291 | -2.5818 | 82.4112 | -42.453 | -0.2655 | -0.027466 | 5.3467 | -0.21973 | -82.3929 | -0.24719 | -0.036621 | 5.6122 | 41.5329 | 39.624 | 42.2607 | 124.6262 | 5.3467 | 124.617 | 38.8458 | -0.24719 | 124.6262 | 5.3467 | 38.8458 | 42.2607 | 124.617 | -124.9191 | -124.9008
737.375 | 124.7955 | -41.7297 | 82.9742 | 0.12527 | 0.014725 | 0.040941 | 0.0075729 | 0.071566 | 0.042682 | 0.095662 | -36.3327 | 82.9788 | -41.9632 | -41.9769 | -0.004578 | -3.3737 | -0.55389 | -2.6276 | 82.9285 | -41.9815 | -0.23346 | 0.004578 | 5.397 | -0.24719 | -82.9788 | -0.25177 | -0.045776 | 5.6305 | 41.1758 | 39.1022 | 41.7252 | 124.7086 | 5.397 | 124.6582 | 38.356 | -0.25177 | 124.7086 | 5.397 | 38.356 | 41.7252 | 124.6582 | -124.9374 | -124.9557
738.375 | 124.7772 | -41.098 | 83.5968 | 0.1329 | 0.016434 | 0.037096 | 0.0054367 | 0.071779 | 0.043536 | 0.097371 | -35.6873 | 83.6151 | -41.3361 | -41.3406 | -0.018311 | -3.2959 | -0.53101 | -2.5635 | 83.5602 | -41.3406 | -0.23804 | 0.01831 | 5.4108 | -0.24262 | -83.6151 | -0.24262 | -0.036621 | 5.6488 | 40.567 | 38.5345 | 41.0797 | 124.7131 | 5.4108 | 124.6582 | 37.8021 | -0.24262 | 124.7131 | 5.4108 | 37.8021 | 41.0797 | 124.6582 | -124.9329 | -124.9374
739.375 | 124.8367 | -40.3839 | 84.2743 | 0.11002 | 0.013016 | 0.037309 | 0.0062913 | 0.07242 | 0.044177 | 0.096731 | -34.9274 | 84.2743 | -40.6357 | -40.6128 | 0.027466 | -3.2227 | -0.6134 | -2.4445 | 84.2239 | -40.6128 | -0.25177 | 0 | 5.4565 | -0.22888 | -84.2468 | -0.22888 | -0.050354 | 5.7083 | 39.7705 | 37.9395 | 40.4114 | 124.6582 | 5.4565 | 124.6078 | 37.1613 | -0.22888 | 124.6582 | 5.4565 | 37.1613 | 40.4114 | 124.6078 | -124.91 | -124.8871
740.375 | 124.8184 | -39.6149 | 85.0433 | 0.1329 | 0.01558 | 0.038164 | 0.0062913 | 0.070711 | 0.042468 | 0.097585 | -34.1537 | 85.0479 | -39.8849 | -39.8849 | 0.032043 | -3.1311 | -0.59052 | -2.3758 | 84.9792 | -39.8895 | -0.27008 | 0.004578 | 5.4611 | -0.27008 | -85.0113 | -0.27466 | -0.064087 | 5.7312 | 39.0244 | 37.2391 | 39.6469 | 124.6628 | 5.4611 | 124.5941 | 36.4838 | -0.27466 | 124.6628 | 5.4611 | 36.4838 | 39.6469 | 124.5941 | -124.9283 | -124.9329
741.375 | 124.8276 | -38.9877 | 85.6384 | 0.17868 | 0.015152 | 0.036241 | 0.0047959 | 0.070711 | 0.045032 | 0.098012 | -33.577 | 85.6613 | -39.2578 | -39.2212 | 0.022888 | -3.0441 | -0.56763 | -2.3254 | 85.611 | -39.2578 | -0.27008 | 0.022888 | 5.4108 | -0.23346 | -85.6155 | -0.27008 | -0.027466 | 5.6808 | 38.4201 | 36.6623 | 39.0106 | 124.649 | 5.4108 | 124.5987 | 35.9436 | -0.27008 | 124.649 | 5.4108 | 35.9436 | 39.0106 | 124.5987 | -124.8962 | -124.8962
742.375 | 124.8917 | -38.2828 | 86.3113 | 0.17868 | 0.012802 | 0.036241 | 0.0060777 | 0.070498 | 0.046954 | 0.10015 | -32.7301 | 86.3022 | -38.5437 | -38.7222 | 0.009155 | -2.6917 | -0.65918 | -2.2751 | 86.2701 | -38.5483 | -0.26093 | -0.009155 | 5.5527 | -0.43945 | -86.3022 | -0.2655 | -0.041198 | 5.8136 | 37.6236 | 36.0077 | 38.2919 | 124.585 | 5.5527 | 124.5529 | 35.5911 | -0.2655 | 124.585 | 5.5527 | 35.5911 | 38.2919 | 124.5529 | -124.855 | -124.8596
743.375 | 124.8596 | -37.4817 | 87.1262 | 0.094757 | 0.012802 | 0.041154 | 0.0050095 | 0.071779 | 0.046527 | 0.10143 | -31.8558 | 87.1124 | -37.738 | -37.9257 | -0.10529 | -2.7237 | -0.5722 | -2.2751 | 87.0529 | -37.7289 | -0.25635 | -0.013733 | 5.6259 | -0.44403 | -87.2314 | -0.24719 | -0.073243 | 5.8823 | 36.9095 | 35.2066 | 37.3764 | 124.5941 | 5.6259 | 124.5346 | 34.758 | -0.24719 | 124.5941 | 5.6259 | 34.758 | 37.3764 | 124.5346 | -124.8642 | -124.855
744.375 | 124.8367 | -36.8362 | 87.8265 | 0.16342 | 0.013016 | 0.036028 | 0.0067185 | 0.070925 | 0.046527 | 0.099935 | -31.3293 | 87.8174 | -37.1063 | -37.1017 | 0.022888 | -2.742 | -0.54932 | -2.2797 | 87.7487 | -37.1017 | -0.27008 | -0.009155 | 5.5069 | -0.2655 | -87.8037 | -0.2655 | -0.07782 | 5.777 | 36.2869 | 34.5566 | 36.8591 | 124.6536 | 5.5069 | 124.585 | 34.0942 | -0.2655 | 124.6536 | 5.5069 | 34.0942 | 36.8591 | 124.585 | -124.9329 | -124.9283
745.375 | 124.8322 | -36.0443 | 88.5818 | 0.20157 | 0.015366 | 0.041582 | 0.0067185 | 0.070284 | 0.044177 | 0.098012 | -30.5008 | 88.5361 | -36.3464 | -36.3007 | 0.032043 | -2.6779 | -0.54016 | -2.2934 | 88.5544 | -36.3007 | -0.30212 | -0.045776 | 5.5435 | -0.25635 | -88.5498 | -0.25635 | -0.027466 | 5.8456 | 35.5042 | 33.7509 | 36.0764 | 124.5804 | 5.5435 | 124.5987 | 33.3664 | -0.25635 | 124.5804 | 5.5435 | 33.3664 | 36.0764 | 124.5987 | -124.9283 | -124.8825
746.375 | 124.9008 | -35.2798 | 89.3372 | 0.43808 | 0.012162 | 0.040727 | 0.0069321 | 0.070284 | 0.045245 | 0.099721 | -29.718 | 89.3188 | -35.5316 | -35.3943 | -0.082397 | -2.7054 | -0.48065 | -2.0874 | 89.2639 | -35.5225 | -0.25177 | -0.01831 | 5.5618 | -0.11444 | -89.4196 | -0.24262 | -0.073242 | 5.8136 | 34.7992 | 33.1924 | 35.1974 | 124.5987 | 5.5618 | 124.5438 | 32.5745 | -0.24262 | 124.5987 | 5.5618 | 32.5745 | 35.1974 | 124.5438 | -124.8688 | -124.8596
747.375 | 124.9237 | -34.2361 | 90.4312 | 0.27786 | 0.012162 | 0.038591 | 0.0062913 | 0.070498 | 0.048022 | 0.098226 | -28.6102 | 90.358 | -34.5108 | -34.4421 | 0.086975 | -2.4307 | -0.75531 | -2.4261 | 90.271 | -34.5428 | -0.27466 | -0.073242 | 5.6259 | -0.20599 | -90.3442 | -0.3067 | -0.16022 | 5.9006 | 33.4808 | 31.81 | 34.3231 | 124.5941 | 5.6259 | 124.5071 | 31.8054 | -0.3067 | 124.5941 | 5.6259 | 31.8054 | 34.3231 | 124.5071 | -124.942 | -124.9741
748.375 | 124.8047 | -33.4076 | 91.1728 | 0.094757 | 0.01323 | 0.039873 | 0.0065049 | 0.071566 | 0.049091 | 0.10164 | -27.7176 | 91.246 | -33.6182 | -33.5632 | 0.10986 | -2.4078 | -0.58594 | -2.0416 | 91.1957 | -33.609 | -0.21057 | 0.073242 | 5.69 | -0.15564 | -91.0629 | -0.20142 | 0.022888 | 5.9006 | 32.8217 | 31.366 | 33.5175 | 124.6536 | 5.69 | 124.6033 | 30.9998 | -0.20142 | 124.6536 | 5.69 | 30.9998 | 33.5175 | 124.6033 | -124.791 | -124.7818
749.375 | 124.8825 | -32.103 | 92.5278 | 0.11765 | 0.013016 | 0.037737 | 0.0037277 | 0.069643 | 0.048877 | 0.10186 | -26.6144 | 92.4454 | -32.3868 | -32.2952 | 0.091553 | -2.3209 | -0.57678 | -1.9547 | 92.4591 | -32.3547 | -0.28381 | -0.082397 | 5.4886 | -0.19226 | -92.4362 | -0.25177 | -0.068665 | 5.7724 | 31.5262 | 30.1483 | 32.1945 | 124.5483 | 5.4886 | 124.5621 | 29.7821 | -0.25177 | 124.5483 | 5.4886 | 29.7821 | 32.1945 | 124.5621 | -124.9146 | -124.8825
750.375 | 124.8917 | -31.2973 | 93.3243 | 0.12527 | 0.014298 | 0.038591 | 0.0067185 | 0.067507 | 0.049091 | 0.10207 | -25.8224 | 93.2831 | -31.5445 | -31.4713 | 0.086975 | -2.2751 | -0.6134 | -2.4307 | 93.2556 | -31.5445 | -0.24719 | -0.041199 | 5.4749 | -0.17395 | -93.2373 | -0.24719 | -0.068665 | 5.722 | 30.6839 | 28.8666 | 31.3843 | 124.5804 | 5.4749 | 124.5529 | 29.0222 | -0.24719 | 124.5804 | 5.4749 | 29.0222 | 31.3843 | 124.5529 | -124.8688 | -124.8688
751.375 | 124.8825 | -30.3772 | 94.2352 | 0.2092 | 0.013443 | 0.040086 | 0.0060777 | 0.068361 | 0.051013 | 0.10335 | -25.0397 | 94.1803 | -30.6976 | -30.5832 | 0.082397 | -2.2247 | -0.66376 | -3.3966 | 94.1483 | -30.6473 | -0.32043 | -0.054931 | 5.3375 | -0.20599 | -94.1528 | -0.27008 | -0.086975 | 5.658 | 29.7134 | 26.9806 | 30.4596 | 124.5575 | 5.3375 | 124.5255 | 28.1525 | -0.27008 | 124.5575 | 5.3375 | 28.1525 | 30.4596 | 124.5255 | -124.9329 | -124.8825
752.375 | 124.8779 | -29.892 | 94.7205 | 0.16342 | 0.014939 | 0.038377 | 0.0065049 | 0.069857 | 0.04845 | 0.10271 | -24.4675 | 94.6793 | -30.1666 | -30.0842 | 0.073242 | -2.2018 | -0.59509 | -2.9434 | 94.6838 | -30.1529 | -0.27466 | -0.041199 | 5.4245 | -0.19226 | -94.6472 | -0.26093 | -0.036621 | 5.6992 | 29.2969 | 26.9485 | 29.9652 | 124.5712 | 5.4245 | 124.5758 | 27.6901 | -0.26093 | 124.5712 | 5.4245 | 27.6901 | 29.9652 | 124.5758 | -124.8871 | -124.8734
753.375 | 124.9008 | -28.5461 | 96.0846 | 0.018463 | 0.013016 | 0.042863 | 0.0035141 | 0.068361 | 0.051654 | 0.10463 | -23.1171 | 95.9244 | -28.8895 | -28.7201 | 0.10071 | -2.0691 | -0.66834 | -3.3142 | 96.0022 | -28.775 | -0.34332 | -0.16022 | 5.4291 | -0.17395 | -95.9839 | -0.22888 | -0.082398 | 5.7724 | 27.8778 | 25.2319 | 28.6469 | 124.4705 | 5.4291 | 124.5483 | 26.4771 | -0.22888 | 124.4705 | 5.4291 | 26.4771 | 28.6469 | 124.5483 | -124.9741 | -124.8596
754.375 | 124.8871 | -27.6901 | 96.904 | 0.033722 | 0.012375 | 0.045 | 0.0067185 | 0.068361 | 0.050372 | 0.10463 | -21.9498 | 96.8582 | -27.9556 | -27.919 | 0.10071 | -1.9958 | -0.67291 | -3.5889 | 96.8674 | -27.9648 | -0.2655 | -0.045777 | 5.7404 | -0.22888 | -96.8033 | -0.27466 | -0.036621 | 6.0059 | 27.0172 | 24.1013 | 27.7908 | 124.5483 | 5.7404 | 124.5575 | 25.6943 | -0.27466 | 124.5483 | 5.7404 | 25.6943 | 27.7908 | 124.5575 | -124.8596 | -124.8688
755.375 | 124.8642 | -26.1246 | 98.5382 | 0.2626 | 0.013657 | 0.041368 | 0.0075729 | 0.069002 | 0.052509 | 0.10186 | -20.2744 | 98.5199 | -26.3123 | -26.2985 | 0.091553 | -1.886 | -0.737 | -4.4449 | 98.4283 | -26.3535 | -0.18768 | -0.018311 | 5.8502 | -0.17395 | -98.4467 | -0.22888 | -0.10986 | 6.0379 | 25.3876 | 21.6797 | 26.2161 | 124.6445 | 5.8502 | 124.5529 | 24.2386 | -0.22888 | 124.6445 | 5.8502 | 24.2386 | 26.2161 | 124.5529 | -124.8505 | -124.8917
756.375 | 124.8642 | -23.2132 | 101.4404 | 0.14053 | 0.013016 | 0.041368 | 0.0052231 | 0.070711 | 0.05144 | 0.10656 | -17.9535 | 101.413 | -23.41 | -23.6115 | 0.082397 | -1.6708 | -0.59967 | -3.2776 | 101.2665 | -23.5245 | -0.19684 | -0.027466 | 5.2597 | -0.39825 | -101.358 | -0.31128 | -0.17395 | 5.4565 | 22.6135 | 19.9356 | 23.2956 | 124.6262 | 5.2597 | 124.4797 | 21.5424 | -0.31128 | 124.6262 | 5.2597 | 21.5424 | 23.2956 | 124.4797 | -124.8505 | -124.9649
757.375 | 124.8734 | -9.9792 | 114.7659 | 0.14816 | 0.014511 | 0.029405 | 0.0041549 | 0.068789 | 0.061908 | 0.13454 | -7.9697 | 114.4913 | -10.3867 | -9.8557 | 0.09613 | -0.6958 | -0.3891 | -1.2817 | 114.592 | -10.1898 | -0.40741 | -0.27466 | 2.0096 | 0.1236 | -114.6698 | -0.21057 | -0.17395 | 2.417 | 9.5901 | 8.6975 | 10.0754 | 124.4705 | 2.0096 | 124.5712 | 9.2834 | -0.21057 | 124.4705 | 2.0096 | 9.2834 | 10.0754 | 124.5712 | -125.1526 | -124.9557
758.375 | 124.8596 | -6.3446 | 118.364 | -1.2938 | 0.01323 | 0.022569 | 0.0082139 | 0.06943 | 0.060413 | 0.14245 | -4.8614 | 118.2129 | -6.6879 | -6.2164 | 0.082397 | -0.44861 | -0.34332 | -0.70953 | 118.2999 | -6.5598 | -0.34332 | -0.15106 | 1.4832 | 0.12817 | -118.2816 | -0.21515 | -0.064087 | 1.8265 | 6.0013 | 5.6351 | 6.427 | 124.5575 | 1.4832 | 124.6445 | 5.896 | -0.21515 | 124.5575 | 1.4832 | 5.896 | 6.427 | 124.6445 | -125.0519 | -124.9237
759.375 | 124.8642 | -5.1498 | 119.6045 | 0.10239 | 0.012802 | 0.019365 | 0.0069321 | 0.067934 | 0.063831 | 0.14138 | -4.1336 | 119.3619 | -5.5298 | -5.0995 | 0.07782 | -0.3479 | -0.33875 | -0.53558 | 119.4534 | -5.397 | -0.37994 | -0.24261 | 1.0162 | 0.050354 | -119.5267 | -0.24719 | -0.15106 | 1.3962 | 4.8111 | 4.6143 | 5.2277 | 124.5117 | 1.0162 | 124.6033 | 4.8019 | -0.24719 | 124.5117 | 1.0162 | 4.8019 | 5.2277 | 124.6033 | -125.1343 | -125.0015
760.375 | 124.8276 | -4.9622 | 119.8013 | 0.12527 | 0.013657 | 0.016588 | 0.0050095 | 0.066652 | 0.064044 | 0.14309 | -3.7216 | 118.9178 | -5.8365 | -4.9393 | 0.086975 | -0.28839 | -0.24261 | -0.48065 | 119.5908 | -5.1956 | -0.87433 | -0.88348 | 1.2405 | 0.022888 | -119.7144 | -0.23346 | -0.21057 | 2.1149 | 4.7195 | 4.4815 | 5.0491 | 123.88 | 1.2405 | 124.5529 | 4.6738 | -0.23346 | 123.88 | 1.2405 | 4.6738 | 5.0491 | 124.5529 | -125.6378 | -124.9969
761.375 | 124.8688 | -6.0287 | 118.7393 | 0.14053 | 0.015152 | 0.02086 | 0.0077865 | 0.067934 | 0.062122 | 0.14095 | -4.5502 | 118.5883 | -6.2805 | -5.9143 | 0.10071 | -0.30212 | -0.31586 | -0.54016 | 118.5608 | -6.2714 | -0.25177 | -0.15106 | 1.4786 | 0.11444 | -118.6386 | -0.24261 | -0.17853 | 1.7303 | 5.7129 | 5.4886 | 6.1295 | 124.617 | 1.4786 | 124.5895 | 5.7266 | -0.24261 | 124.617 | 1.4786 | 5.7266 | 6.1295 | 124.5895 | -125.0198 | -125.0107
762.375 | 124.8642 | -9.3887 | 115.274 | 0.19394 | 0.014298 | 0.025774 | 0.0094955 | 0.069643 | 0.062335 | 0.13476 | -6.4362 | 115.4022 | -9.4986 | -9.2011 | 0.091553 | -0.013733 | -0.36621 | -0.83771 | 115.3015 | -9.5627 | -0.10986 | 0.12817 | 2.9526 | 0.18768 | -115.1825 | -0.17395 | 0.027466 | 3.0624 | 9.0225 | 8.551 | 9.4803 | 124.791 | 2.9526 | 124.6902 | 9.375 | -0.17395 | 124.791 | 2.9526 | 9.375 | 9.4803 | 124.6902 | -124.7726 | -124.8367
763.375 | 124.8596 | -5.7312 | 118.927 | 0.087128 | 0.013871 | 0.021715 | 0.0056503 | 0.067293 | 0.062549 | 0.14159 | -4.3304 | 118.8354 | -6.0745 | -5.6259 | 0.10071 | 0.004578 | -0.26093 | -0.27924 | 118.8995 | -5.9418 | -0.34332 | -0.091553 | 1.4008 | 0.10529 | -118.8263 | -0.21057 | -0.027466 | 1.7441 | 5.4703 | 5.452 | 5.8319 | 124.5666 | 1.4008 | 124.6307 | 5.7358 | -0.21057 | 124.5666 | 1.4008 | 5.7358 | 5.8319 | 124.6307 | -125.0015 | -124.8688
764.375 | 124.8459 | -5.2826 | 119.4122 | 0.11765 | 0.012589 | 0.019579 | 0.0054367 | 0.065584 | 0.064044 | 0.14223 | -3.8132 | 119.3665 | -5.5801 | -5.1224 | 0.14191 | 0.036621 | -0.25177 | -0.21973 | 119.3207 | -5.5069 | -0.29755 | -0.045776 | 1.4694 | 0.16022 | -119.2703 | -0.2243 | -0.091552 | 1.767 | 5.0308 | 5.0629 | 5.4245 | 124.649 | 1.4694 | 124.6033 | 5.3192 | -0.2243 | 124.649 | 1.4694 | 5.3192 | 5.4245 | 124.6033 | -124.9924 | -124.9191
765.375 | 124.855 | -4.509 | 120.2087 | 0.30838 | 0.014298 | 0.018297 | 0.0080003 | 0.067507 | 0.063403 | 0.14202 | -2.8152 | 120.0485 | -4.834 | -4.4037 | 0.10071 | 0.068665 | -0.29297 | -0.27924 | 120.1263 | -4.715 | -0.32501 | -0.16022 | 1.6937 | 0.10529 | -120.108 | -0.20599 | -0.082397 | 2.0187 | 4.216 | 4.2297 | 4.6097 | 124.5575 | 1.6937 | 124.6353 | 4.5776 | -0.20599 | 124.5575 | 1.6937 | 4.5776 | 4.6097 | 124.6353 | -125.0427 | -124.9237
766.375 | 124.8596 | -4.4128 | 120.2637 | -0.2562 | 0.012589 | 0.021715 | 0.0067185 | 0.068789 | 0.063831 | 0.14416 | -2.5085 | 120.2728 | -4.6829 | -4.2801 | 0.091553 | -0.18768 | -0.27466 | -0.25177 | 120.2271 | -4.6371 | -0.27008 | 0.009155 | 1.9043 | 0.13275 | -120.1721 | -0.2243 | -0.036621 | 2.1744 | 4.1382 | 4.1611 | 4.5044 | 124.6857 | 1.9043 | 124.6399 | 4.2252 | -0.2243 | 124.6857 | 1.9043 | 4.2252 | 4.5044 | 124.6399 | -124.9466 | -124.9008
767.375 | 124.8734 | -4.5227 | 120.195 | 0.11002 | 0.013871 | 0.021074 | 0.0073593 | 0.067934 | 0.064044 | 0.14095 | -2.6825 | 120.0897 | -4.8157 | -4.3625 | 0.091553 | 0.07782 | -0.26093 | -0.25177 | 120.1218 | -4.7333 | -0.29297 | -0.10529 | 1.8402 | 0.16022 | -120.1035 | -0.21057 | -0.073242 | 2.1332 | 4.2618 | 4.2709 | 4.6143 | 124.6124 | 1.8402 | 124.6445 | 4.6005 | -0.21057 | 124.6124 | 1.8402 | 4.6005 | 4.6143 | 124.6445 | -125.0107 | -124.9283
768.375 | 124.8825 | -4.2343 | 120.433 | 0.14053 | 0.012802 | 0.022783 | 0.0056503 | 0.068361 | 0.064258 | 0.14159 | -2.124 | 120.4102 | -4.4769 | -4.1107 | 0.10529 | 0.073242 | -0.24261 | -0.20599 | 120.3918 | -4.4724 | -0.24261 | -0.022888 | 2.1103 | 0.1236 | -120.3278 | -0.23804 | -0.041198 | 2.3529 | 3.9917 | 4.0283 | 4.3396 | 124.6445 | 2.1103 | 124.6262 | 4.3076 | -0.23804 | 124.6445 | 2.1103 | 4.3076 | 4.3396 | 124.6262 | -124.91 | -124.9054
769.375 | 124.8962 | -4.2114 | 120.5063 | -0.042572 | 0.012589 | 0.026842 | 0.0033005 | 0.066439 | 0.063831 | 0.13967 | -1.5564 | 120.433 | -4.454 | -4.0466 | 0.10986 | 0.07782 | -0.18768 | -0.15564 | 120.433 | -4.4174 | -0.24261 | -0.073243 | 2.655 | 0.1648 | -120.3964 | -0.20599 | -0.073243 | 2.8976 | 4.0237 | 4.0558 | 4.3213 | 124.6445 | 2.655 | 124.6445 | 4.2892 | -0.20599 | 124.6445 | 2.655 | 4.2892 | 4.3213 | 124.6445 | -124.9603 | -124.9237
770.375 | 124.8276 | -4.7379 | 119.9753 | 0.094757 | 0.01323 | 0.023851 | 0.0054367 | 0.067293 | 0.064044 | 0.13967 | -1.0391 | 119.8975 | -5.0354 | -4.5364 | 0.082397 | 0.073242 | -0.22888 | -0.24261 | 119.8883 | -4.9255 | -0.29755 | -0.07782 | 3.6987 | 0.20142 | -119.8929 | -0.18768 | -0.086975 | 3.9963 | 4.509 | 4.4952 | 4.8203 | 124.6353 | 3.6987 | 124.6262 | 4.8111 | -0.18768 | 124.6353 | 3.6987 | 4.8111 | 4.8203 | 124.6262 | -125.0107 | -124.9008
771.375 | 124.8688 | -4.1931 | 120.5017 | 0.14816 | 0.013871 | 0.022356 | 0.0073593 | 0.066225 | 0.064899 | 0.1401 | -0.51727 | 120.433 | -4.4083 | -4.0878 | 0.10071 | 0.07782 | -0.21057 | -0.18768 | 120.4239 | -4.4174 | -0.21515 | -0.068665 | 3.6758 | 0.10528 | -120.401 | -0.2243 | -0.07782 | 3.891 | 3.9825 | 4.0054 | 4.2938 | 124.6262 | 3.6758 | 124.617 | 4.2709 | -0.2243 | 124.6262 | 3.6758 | 4.2709 | 4.2938 | 124.617 | -124.91 | -124.9191
772.375 | 124.855 | -4.2526 | 120.4788 | 0.064239 | 0.014725 | 0.028764 | 0.011204 | 0.066652 | 0.062762 | 0.13839 | -0.26093 | 120.5109 | -4.3808 | -4.0649 | 0.059509 | 0.07782 | -0.26093 | -0.18768 | 120.3644 | -4.4128 | -0.12817 | 0.032043 | 3.9917 | 0.18768 | -120.4193 | -0.16022 | -0.11444 | 4.1199 | 3.9917 | 4.0649 | 4.3121 | 124.7635 | 3.9917 | 124.617 | 4.3304 | -0.16022 | 124.7635 | 3.9917 | 4.3304 | 4.3121 | 124.617 | -124.8596 | -124.8917
773.375 | 124.8413 | -5.0995 | 119.5679 | 0.11002 | 0.013016 | 0.029192 | 0.0099229 | 0.068575 | 0.065112 | 0.13411 | -0.21973 | 119.5953 | -5.3284 | -4.953 | 0.086975 | 0.068665 | -0.2243 | -0.22888 | 119.5404 | -5.3055 | -0.22888 | 0.027466 | 4.8798 | 0.14648 | -119.4809 | -0.20599 | -0.027466 | 5.1086 | 4.8752 | 4.8706 | 5.1865 | 124.6948 | 4.8798 | 124.6399 | 5.1682 | -0.20599 | 124.6948 | 4.8798 | 5.1682 | 5.1865 | 124.6399 | -124.8962 | -124.8734
774.3906 | 124.8413 | -4.1336 | 120.5658 | -0.13412 | 0.016007 | 0.022783 | 0.0035141 | 0.065157 | 0.064258 | 0.13796 | -0.20599 | 120.5383 | -4.3533 | -4.0192 | 0.40741 | 0.27466 | -0.52643 | -0.073242 | 120.488 | -4.3442 | -0.21973 | -0.027466 | 3.9276 | 0.11444 | -120.1584 | -0.21057 | -0.07782 | 4.1473 | 3.6072 | 4.0604 | 4.541 | 124.6719 | 3.9276 | 124.6216 | 4.4083 | -0.21057 | 124.6719 | 3.9276 | 4.4083 | 4.541 | 124.6216 | -124.9191 | -124.91
775.375 | 124.8779 | -4.1245 | 120.607 | 0.14816 | 0.015793 | 0.028123 | 0.0082139 | 0.068789 | 0.064044 | 0.14074 | -0.28839 | 120.4651 | -4.3991 | -4.01 | 0.073242 | 0.086975 | -0.16479 | -0.09613 | 120.5063 | -4.3579 | -0.27466 | -0.14191 | 3.8361 | 0.11444 | -120.5338 | -0.23346 | -0.10071 | 4.1107 | 3.9597 | 4.0283 | 4.1977 | 124.5895 | 3.8361 | 124.6307 | 4.2114 | -0.23346 | 124.5895 | 3.8361 | 4.2114 | 4.1977 | 124.6307 | -125.0061 | -124.9649
776.375 | 124.942 | -4.6143 | 120.0989 | 0.27786 | 0.017075 | 0.024706 | 0.0084275 | 0.068575 | 0.063831 | 0.13796 | -0.18768 | 120.1447 | -4.7974 | -4.422 | 0.09613 | 0.10071 | -0.15106 | -0.37537 | 120.0027 | -4.7607 | -0.1831 | 0.045776 | 4.4266 | 0.19226 | -120.0027 | -0.14648 | -0.09613 | 4.6097 | 4.4632 | 4.2389 | 4.7104 | 124.7589 | 4.4266 | 124.617 | 4.715 | -0.14648 | 124.7589 | 4.4266 | 4.715 | 4.7104 | 124.617 | -124.8962 | -124.8596
777.375 | 124.8505 | -5.1819 | 119.5084 | 0.094757 | 0.01558 | 0.030473 | 0.0069321 | 0.069216 | 0.063617 | 0.13689 | -0.29297 | 119.4855 | -5.4016 | -5.0491 | 0.10071 | 0.091553 | -0.16022 | -0.10071 | 119.458 | -5.3879 | -0.21973 | -0.022888 | 4.8889 | 0.13275 | -119.4077 | -0.20599 | -0.050354 | 5.1086 | 5.0217 | 5.0812 | 5.2826 | 124.6674 | 4.8889 | 124.6399 | 5.2734 | -0.20599 | 124.6674 | 4.8889 | 5.2734 | 5.2826 | 124.6399 | -124.91 | -124.8962
778.375 | 124.8734 | -5.4245 | 119.2474 | 0.14053 | 0.014725 | 0.031328 | 0.011845 | 0.07007 | 0.064899 | 0.1354 | -0.25635 | 119.2795 | -5.603 | -5.2597 | 0.054932 | 0.082397 | -0.10071 | -0.1236 | 119.2017 | -5.6396 | -0.17853 | 0.032043 | 5.1682 | 0.16479 | -119.1925 | -0.21515 | -0.045777 | 5.3467 | 5.3238 | 5.3009 | 5.4794 | 124.704 | 5.1682 | 124.6262 | 5.5069 | -0.21515 | 124.704 | 5.1682 | 5.5069 | 5.4794 | 124.6262 | -124.8505 | -124.8871
779.375 | 124.8505 | -5.6992 | 119.0186 | 0.10239 | 0.013871 | 0.027696 | 0.0043687 | 0.068789 | 0.063617 | 0.13476 | -0.25635 | 118.9728 | -5.9235 | -5.6213 | 0.082397 | 0.086975 | -0.027466 | -0.068665 | 118.8995 | -5.896 | -0.2243 | -0.045777 | 5.4428 | 0.07782 | -118.9362 | -0.19684 | -0.11902 | 5.6671 | 5.6717 | 5.6305 | 5.7816 | 124.6719 | 5.4428 | 124.5987 | 5.7861 | -0.19684 | 124.6719 | 5.4428 | 5.7861 | 5.7816 | 124.5987 | -124.942 | -124.9146
780.375 | 124.8642 | -5.6534 | 119.0735 | 0.14053 | 0.017502 | 0.031541 | 0.0127 | 0.067721 | 0.064258 | 0.13518 | -0.2243 | 119.0964 | -5.8777 | -5.5801 | 0.064087 | 0.068665 | 0.004578 | -0.018311 | 118.9545 | -5.8731 | -0.2243 | 0.022889 | 5.4291 | 0.073242 | -119.0094 | -0.21973 | -0.11902 | 5.6534 | 5.658 | 5.6351 | 5.7175 | 124.7498 | 5.4291 | 124.6078 | 5.722 | -0.21973 | 124.7498 | 5.4291 | 5.722 | 5.7175 | 124.6078 | -124.9512 | -124.9466
781.375 | 124.8047 | -5.7999 | 118.9041 | 0.17105 | 0.015152 | 0.034105 | 0.012913 | 0.068789 | 0.063403 | 0.1354 | -0.26093 | 118.9728 | -6.0013 | -5.7037 | 0.027466 | 0.027466 | 0.12817 | -0.022888 | 118.8583 | -5.9738 | -0.20142 | 0.068664 | 5.5389 | 0.096131 | -118.8766 | -0.17395 | -0.045777 | 5.7404 | 5.928 | 5.777 | 5.8273 | 124.7726 | 5.5389 | 124.6582 | 5.8273 | -0.17395 | 124.7726 | 5.5389 | 5.8273 | 5.8273 | 124.6582 | -124.9054 | -124.8779
782.375 | 124.8047 | -5.5939 | 119.1696 | 0.14053 | 0.019211 | 0.031541 | 0.012486 | 0.068575 | 0.063403 | 0.13689 | -0.26093 | 119.1879 | -5.8228 | -5.5344 | 0.018311 | 0.013733 | 0.23804 | 0.032043 | 119.0964 | -5.7861 | -0.22888 | 0.01831 | 5.3329 | 0.059509 | -119.1513 | -0.19226 | -0.073242 | 5.5618 | 5.8319 | 5.6259 | 5.6122 | 124.7818 | 5.3329 | 124.6902 | 5.6076 | -0.19226 | 124.7818 | 5.3329 | 5.6076 | 5.6122 | 124.6902 | -124.9924 | -124.9558
783.375 | 124.7269 | -5.3558 | 119.4122 | 0.16342 | 0.016434 | 0.03325 | 0.012059 | 0.071566 | 0.061908 | 0.13604 | -0.22888 | 119.3939 | -5.6442 | -5.2963 | 0.004578 | 0.013733 | 0.36621 | 0.13275 | 119.3665 | -5.5664 | -0.28839 | -0.01831 | 5.127 | 0.059509 | -119.4077 | -0.21057 | -0.045776 | 5.4153 | 5.722 | 5.4886 | 5.3604 | 124.7498 | 5.127 | 124.7223 | 5.3696 | -0.21057 | 124.7498 | 5.127 | 5.3696 | 5.3604 | 124.7223 | -125.0565 | -124.9786
784.375 | 124.7314 | -5.6122 | 119.1467 | -1.866 | 0.014725 | 0.036028 | 0.011632 | 0.068789 | 0.064044 | 0.13497 | -0.35248 | 119.2245 | -5.7678 | -5.5573 | 0.018311 | 0.050354 | 0.51727 | 0.3067 | 119.133 | -5.8044 | -0.15564 | 0.077819 | 5.2597 | 0.054932 | -119.1284 | -0.19226 | -0.013733 | 5.4153 | 6.1295 | 5.9189 | 5.6305 | 124.8367 | 5.2597 | 124.7452 | 5.6625 | -0.19226 | 124.8367 | 5.2597 | 5.6625 | 5.6305 | 124.7452 | -124.9146 | -124.9512
785.375 | 124.7543 | -5.6808 | 119.1101 | 0.87296 | 0.019852 | 0.032182 | 0.016331 | 0.069002 | 0.060413 | 0.13796 | -0.27008 | 119.0964 | -5.9143 | -5.6259 | -0.013733 | 0.027466 | 0.51727 | 0.32501 | 119.046 | -5.8914 | -0.23346 | -0.013732 | 5.4108 | 0.054931 | -119.1238 | -0.21057 | -0.064086 | 5.6442 | 6.1981 | 6.0059 | 5.6671 | 124.7772 | 5.4108 | 124.7269 | 5.7083 | -0.21057 | 124.7772 | 5.4108 | 5.7083 | 5.6671 | 124.7269 | -125.0244 | -125.0015
786.375 | 124.7223 | -5.7678 | 118.959 | 0.033722 | 0.021561 | 0.031328 | 0.016545 | 0.071566 | 0.062122 | 0.13903 | -0.30212 | 119.0826 | -5.9875 | -5.9052 | -0.13733 | 0.16022 | 0.54932 | 0.41657 | 118.9957 | -5.9601 | -0.21973 | 0.1236 | 5.4657 | -0.13733 | -119.0964 | -0.19226 | 0.036622 | 5.6854 | 6.3171 | 6.1844 | 5.6305 | 124.8505 | 5.4657 | 124.7635 | 5.928 | -0.19226 | 124.8505 | 5.4657 | 5.928 | 5.6305 | 124.7635 | -124.9466 | -124.9191
787.375 | 124.6902 | -5.4977 | 119.2474 | 0.2092 | 0.020707 | 0.037523 | 0.016759 | 0.073702 | 0.06554 | 0.13839 | -0.34332 | 119.1971 | -5.7816 | -5.4886 | 0 | 0.009155 | 0.63171 | 0.54016 | 119.252 | -5.7083 | -0.28381 | -0.050354 | 5.1544 | 0.009156 | -119.2474 | -0.21057 | 0.004577 | 5.4382 | 6.1295 | 6.0379 | 5.4977 | 124.6948 | 5.1544 | 124.7498 | 5.5069 | -0.21057 | 124.6948 | 5.1544 | 5.5069 | 5.4977 | 124.7498 | -125.029 | -124.9558
788.375 | 124.7131 | -5.6946 | 119.0643 | -0.16464 | 0.019425 | 0.036028 | 0.0174 | 0.071993 | 0.062976 | 0.13967 | -2.3483 | 119.0414 | -5.983 | -5.658 | -0.018311 | 0.027466 | 0.7782 | 0.68207 | 119.0094 | -5.9006 | -0.28839 | -0.022888 | 3.3463 | 0.036621 | -119.0826 | -0.20599 | -0.054932 | 3.6346 | 6.4728 | 6.3766 | 5.6763 | 124.736 | 3.3463 | 124.704 | 5.722 | -0.20599 | 124.736 | 3.3463 | 5.722 | 5.6763 | 124.704 | -125.0473 | -124.9649
789.375 | 124.7498 | -5.2094 | 119.5953 | 0.11765 | 0.021347 | 0.042863 | 0.0174 | 0.071779 | 0.062335 | 0.13903 | -1.68 | 119.4717 | -5.5893 | -5.1956 | 0.17395 | -0.1236 | 1.1307 | 1.1948 | 119.4992 | -5.4474 | -0.37994 | -0.1236 | 3.5294 | 0.013733 | -119.4214 | -0.23804 | -0.09613 | 3.9093 | 6.34 | 6.4041 | 5.3833 | 124.6811 | 3.5294 | 124.7086 | 5.0858 | -0.23804 | 124.6811 | 3.5294 | 5.0858 | 5.3833 | 124.7086 | -125.1846 | -125.0427
790.375 | 124.7406 | -5.4153 | 119.3573 | 0.2092 | 0.020707 | 0.047136 | 0.019109 | 0.070284 | 0.062976 | 0.1339 | -2.5681 | 119.4992 | -5.5344 | -5.3284 | -0.027466 | 0.07782 | 1.0208 | 1.03 | 119.2978 | -5.5939 | -0.11902 | 0.14191 | 2.8473 | 0.086975 | -119.3848 | -0.17853 | -0.059509 | 2.9663 | 6.4362 | 6.4453 | 5.3879 | 124.9146 | 2.8473 | 124.7131 | 5.4932 | -0.17853 | 124.9146 | 2.8473 | 5.4932 | 5.3879 | 124.7131 | -124.8917 | -124.9512
791.375 | 124.7177 | -4.8111 | 119.9295 | 0.11002 | 0.020493 | 0.05739 | 0.020177 | 0.071139 | 0.065753 | 0.13219 | -1.9592 | 120.0623 | -4.9759 | -4.7195 | -0.027466 | 0.059509 | 1.1765 | 1.2451 | 119.9615 | -5.0079 | -0.16479 | 0.13275 | 2.8519 | 0.091553 | -119.957 | -0.19684 | 0.032044 | 3.0167 | 5.9875 | 6.0562 | 4.7836 | 124.8734 | 2.8519 | 124.7726 | 4.8706 | -0.19684 | 124.8734 | 2.8519 | 4.8706 | 4.7836 | 124.7726 | -124.9054 | -124.9374
792.375 | 124.7314 | -5.5481 | 119.1742 | -0.012055 | 0.024552 | 0.04735 | 0.022313 | 0.073275 | 0.062122 | 0.14159 | -1.5884 | 119.1879 | -5.8319 | -5.4703 | 0.004578 | 0.050354 | 1.2817 | 1.2222 | 119.1742 | -5.7449 | -0.28381 | 0.013733 | 3.9597 | 0.07782 | -119.1696 | -0.19684 | 0 | 4.2435 | 6.8298 | 6.7703 | 5.5527 | 124.736 | 3.9597 | 124.7223 | 5.5984 | -0.19684 | 124.736 | 3.9597 | 5.5984 | 5.5527 | 124.7223 | -125.0061 | -124.9191
793.375 | 124.7681 | -5.7495 | 118.9911 | 0.033722 | 0.024979 | 0.0403 | 0.02274 | 0.071779 | 0.062762 | 0.14181 | -1.268 | 119.133 | -5.8777 | -5.5939 | 0.027466 | 0.036621 | 1.3184 | 1.3916 | 118.9819 | -5.9372 | -0.12817 | 0.14191 | 4.4815 | 0.15564 | -118.9636 | -0.18768 | -0.009155 | 4.6097 | 7.0679 | 7.1411 | 5.777 | 124.8825 | 4.4815 | 124.7314 | 5.7861 | -0.18768 | 124.8825 | 4.4815 | 5.7861 | 5.777 | 124.7314 | -124.8688 | -124.9283
794.375 | 124.7086 | -4.834 | 119.9112 | 0.018463 | 0.025193 | 0.061235 | 0.024663 | 0.073061 | 0.062549 | 0.13347 | -1.3229 | 119.9753 | -5.0354 | -4.8157 | -0.004578 | 0.004578 | 1.5289 | 1.2634 | 119.9066 | -5.0217 | -0.20142 | 0.064087 | 3.511 | 0.01831 | -119.9158 | -0.18768 | -0.004578 | 3.7125 | 6.3629 | 6.0974 | 4.8294 | 124.8093 | 3.511 | 124.7406 | 4.8386 | -0.18768 | 124.8093 | 3.511 | 4.8386 | 4.8294 | 124.7406 | -124.9466 | -124.9329
795.375 | 124.7131 | -5.0308 | 119.7556 | -0.0044251 | 0.02797 | 0.062944 | 0.02509 | 0.071139 | 0.064685 | 0.13155 | -1.1856 | 119.8242 | -5.2414 | -4.9438 | 0.004578 | 0.009155 | 1.6113 | 1.2863 | 119.6869 | -5.2231 | -0.21057 | 0.068665 | 3.8452 | 0.086975 | -119.751 | -0.19226 | -0.068664 | 4.0558 | 6.6422 | 6.3171 | 5.0354 | 124.855 | 3.8452 | 124.7177 | 5.04 | -0.19226 | 124.855 | 3.8452 | 5.04 | 5.0354 | 124.7177 | -124.9969 | -124.9786
796.375 | 124.7452 | -5.2917 | 119.4489 | -0.019684 | 0.028611 | 0.059312 | 0.024449 | 0.071139 | 0.063617 | 0.13689 | -1.8906 | 119.5862 | -5.4382 | -5.191 | 0.027466 | 0.027466 | 1.6983 | 1.1902 | 119.4717 | -5.484 | -0.14648 | 0.13733 | 3.4012 | 0.10071 | -119.4214 | -0.19226 | 0.022888 | 3.5477 | 6.9901 | 6.4819 | 5.3192 | 124.8779 | 3.4012 | 124.7635 | 5.3192 | -0.19226 | 124.8779 | 3.4012 | 5.3192 | 5.3192 | 124.7635 | -124.8871 | -124.9329
797.375 | 124.7589 | -5.2414 | 119.4946 | 0.010834 | 0.029038 | 0.06209 | 0.026799 | 0.071993 | 0.063403 | 0.13967 | -1.1261 | 119.5633 | -5.4291 | -5.1224 | 0.032043 | 0.032043 | 1.6937 | 1.0941 | 119.5129 | -5.4153 | -0.18768 | 0.068664 | 4.1153 | 0.11902 | -119.4626 | -0.17395 | 0.01831 | 4.303 | 6.9351 | 6.3354 | 5.2734 | 124.8047 | 4.1153 | 124.7543 | 5.2734 | -0.17395 | 124.8047 | 4.1153 | 5.2734 | 5.2734 | 124.7543 | -124.9237 | -124.91
798.375 | 124.7314 | -6.2393 | 118.483 | 0.041351 | 0.032883 | 0.05504 | 0.026799 | 0.073702 | 0.064044 | 0.14202 | -1.7715 | 118.7119 | -6.308 | -6.1111 | -0.004578 | -0.013733 | 1.9455 | 1.9958 | 118.4738 | -6.4087 | -0.068664 | 0.22888 | 4.4678 | 0.12817 | -118.4875 | -0.16937 | -0.009155 | 4.5364 | 8.1848 | 8.2352 | 6.2347 | 124.9512 | 4.4678 | 124.7131 | 6.2256 | -0.16937 | 124.9512 | 4.4678 | 6.2256 | 6.2347 | 124.7131 | -124.791 | -124.8917
799.375 | 124.7726 | -6.8115 | 117.8879 | -0.11124 | 0.03331 | 0.039659 | 0.027867 | 0.07007 | 0.061694 | 0.15783 | -1.8814 | 117.9291 | -7.077 | -6.7337 | 0.064087 | 0.064087 | 1.973 | 2.1103 | 117.9337 | -7.0038 | -0.2655 | 0.041199 | 4.9301 | 0.077819 | -117.8238 | -0.19226 | 0.045777 | 5.1956 | 8.7845 | 8.9218 | 6.8756 | 124.7406 | 4.9301 | 124.7452 | 6.8756 | -0.19226 | 124.7406 | 4.9301 | 6.8756 | 6.8756 | 124.7452 | -124.9649 | -124.8917
800.375 | 124.7635 | -6.7383 | 118.0206 | -0.1799 | 0.030747 | 0.043504 | 0.027653 | 0.070925 | 0.064899 | 0.15825 | -1.6937 | 118.1442 | -6.8619 | -6.6193 | 0.032043 | 0.041199 | 1.9638 | 2.3346 | 117.9657 | -6.9168 | -0.1236 | 0.1236 | 5.0446 | 0.11902 | -117.9886 | -0.17853 | -0.054932 | 5.1682 | 8.7021 | 9.0729 | 6.7703 | 124.8825 | 5.0446 | 124.704 | 6.7795 | -0.17853 | 124.8825 | 5.0446 | 6.7795 | 6.7703 | 124.704 | -124.8825 | -124.9374
801.375 | 124.7498 | -6.4545 | 118.2312 | -0.07309 | 0.033951 | 0.046495 | 0.030431 | 0.073702 | 0.063831 | 0.15462 | -1.4328 | 118.3731 | -6.6376 | -6.3583 | 0.013733 | 0.027466 | 2.0004 | 2.3895 | 118.2678 | -6.6467 | -0.1831 | 0.14191 | 5.0217 | 0.096131 | -118.2175 | -0.19226 | 0.036621 | 5.2048 | 8.4549 | 8.844 | 6.4682 | 124.8276 | 5.0217 | 124.7223 | 6.4819 | -0.19226 | 124.8276 | 5.0217 | 6.4819 | 6.4682 | 124.7223 | -124.8688 | -124.8779
802.375 | 124.7589 | -6.2256 | 118.483 | -0.080719 | 0.033524 | 0.046495 | 0.02979 | 0.07007 | 0.06319 | 0.15505 | -0.89264 | 118.5287 | -6.4499 | -6.1661 | 0.032043 | 0.050354 | 2.0828 | 2.4536 | 118.4509 | -6.459 | -0.2243 | 0.045777 | 5.3329 | 0.059509 | -118.4509 | -0.23346 | -0.032043 | 5.5573 | 8.3084 | 8.6792 | 6.2576 | 124.7543 | 5.3329 | 124.6765 | 6.2759 | -0.23346 | 124.7543 | 5.3329 | 6.2759 | 6.2576 | 124.6765 | -124.9329 | -124.942
803.375 | 124.7406 | -6.0242 | 118.689 | -0.13412 | 0.034806 | 0.050554 | 0.028722 | 0.074343 | 0.063617 | 0.1559 | -0.8194 | 118.7943 | -6.2164 | -5.9143 | 0.027466 | 0.059509 | 2.0874 | 2.4033 | 118.7119 | -6.1935 | -0.19226 | 0.10529 | 5.2048 | 0.10986 | -118.6615 | -0.16937 | 0.022888 | 5.397 | 8.1116 | 8.4274 | 6.0516 | 124.8184 | 5.2048 | 124.736 | 6.0837 | -0.16937 | 124.8184 | 5.2048 | 6.0837 | 6.0516 | 124.736 | -124.9054 | -124.8825
804.375 | 124.7726 | -5.7495 | 118.9774 | -0.3096 | 0.036087 | 0.048204 | 0.027013 | 0.071993 | 0.064258 | 0.15612 | -0.2243 | 118.9819 | -6.015 | -5.6488 | 0.068665 | 0.054932 | 2.1332 | 2.2156 | 118.9819 | -5.9509 | -0.2655 | 0.004578 | 5.5252 | 0.10071 | -118.9087 | -0.20142 | 0.004578 | 5.7907 | 7.8827 | 7.9651 | 5.8182 | 124.7314 | 5.5252 | 124.7314 | 5.8044 | -0.20142 | 124.7314 | 5.5252 | 5.8044 | 5.8182 | 124.7314 | -124.9924 | -124.9283
805.375 | 124.7543 | -6.4087 | 118.3136 | -0.15701 | 0.038224 | 0.043932 | 0.029149 | 0.071352 | 0.063403 | 0.16295 | -0.2655 | 118.3502 | -6.6193 | -6.34 | 0.045776 | 0.068665 | 1.8951 | 2.0874 | 118.3228 | -6.6193 | -0.21057 | 0.036621 | 6.1432 | 0.068664 | -118.2678 | -0.21057 | 0.009155 | 6.3538 | 8.3038 | 8.4961 | 6.4545 | 124.7589 | 6.1432 | 124.7314 | 6.4774 | -0.21057 | 124.7589 | 6.1432 | 6.4774 | 6.4545 | 124.7314 | -124.9329 | -124.9329
806.375 | 124.6399 | -6.134 | 118.6523 | -0.21042 | 0.037369 | 0.042223 | 0.029576 | 0.072634 | 0.062549 | 0.16488 | -0.22888 | 118.5654 | -6.4316 | -6.134 | 0.082397 | 0.059509 | 1.9318 | 1.0254 | 118.5654 | -6.4499 | -0.29755 | -0.086975 | 5.9052 | 0 | -118.5699 | -0.31586 | -0.086975 | 6.2027 | 8.0658 | 7.1594 | 6.2164 | 124.6994 | 5.9052 | 124.6994 | 6.1935 | -0.31586 | 124.6994 | 5.9052 | 6.1935 | 6.2164 | 124.6994 | -125.0839 | -125.1022
807.375 | 124.7864 | -5.8182 | 118.8995 | -0.2562 | 0.03566 | 0.039232 | 0.027867 | 0.072634 | 0.063831 | 0.17086 | -1.4145 | 118.9545 | -6.0242 | -5.6992 | 0.09613 | 0.054932 | 2.0142 | 0.80566 | 118.927 | -5.9967 | -0.20599 | 0.054932 | 4.4037 | 0.11902 | -118.8034 | -0.17853 | 0.027466 | 4.6097 | 7.8323 | 6.6238 | 5.9143 | 124.7726 | 4.4037 | 124.7452 | 5.8731 | -0.17853 | 124.7726 | 4.4037 | 5.8731 | 5.9143 | 124.7452 | -124.9237 | -124.8962
808.375 | 124.7726 | -5.6992 | 119.0048 | -0.13412 | 0.037583 | 0.036882 | 0.030431 | 0.07477 | 0.068317 | 0.1715 | -1.3 | 119.0735 | -5.928 | -5.5069 | 0.16022 | 0.050354 | 2.124 | 0.63171 | 119.0231 | -5.7999 | -0.22888 | 0.068664 | 4.3991 | 0.19226 | -118.8446 | -0.10071 | 0.01831 | 4.628 | 7.8232 | 6.3309 | 5.8594 | 124.7726 | 4.3991 | 124.7223 | 5.7495 | -0.10071 | 124.7726 | 4.3991 | 5.7495 | 5.8594 | 124.7223 | -124.9329 | -124.8047
809.375 | 124.7543 | -5.4382 | 119.2795 | -0.2562 | 0.036087 | 0.039018 | 0.031285 | 0.070925 | 0.064044 | 0.17299 | -0.96588 | 119.3436 | -5.6488 | -5.3375 | 0.059509 | 0.33417 | 2.0554 | 0.83771 | 119.3161 | -5.6259 | -0.21057 | 0.064087 | 4.4724 | 0.10071 | -119.22 | -0.18768 | 0.036621 | 4.6829 | 7.4936 | 6.2759 | 5.4977 | 124.7818 | 4.4724 | 124.7543 | 5.7724 | -0.18768 | 124.7818 | 4.4724 | 5.7724 | 5.4977 | 124.7543 | -124.9283 | -124.9054
810.375 | 124.7498 | -5.3284 | 119.426 | -0.17227 | 0.03801 | 0.034959 | 0.031071 | 0.071139 | 0.061694 | 0.17342 | -0.85602 | 119.4626 | -5.5023 | -5.2231 | 0.032043 | 0.21515 | 2.1515 | 0.71411 | 119.4214 | -5.5115 | -0.17395 | 0.036621 | 4.4724 | 0.10529 | -119.3939 | -0.18311 | -0.004577 | 4.6463 | 7.4799 | 6.0425 | 5.3604 | 124.791 | 4.4724 | 124.7498 | 5.5435 | -0.18311 | 124.791 | 4.4724 | 5.5435 | 5.3604 | 124.7498 | -124.9283 | -124.9374
811.375 | 124.7635 | -5.1727 | 119.5679 | -0.24094 | 0.039078 | 0.041795 | 0.031071 | 0.071779 | 0.06319 | 0.1715 | -0.21057 | 119.6136 | -5.3741 | -5.0812 | 0.009155 | 0.14191 | 2.1835 | 0.67291 | 119.5953 | -5.3513 | -0.20142 | 0.045776 | 4.9622 | 0.091552 | -119.5587 | -0.17853 | 0.027466 | 5.1636 | 7.3563 | 5.8456 | 5.1819 | 124.7864 | 4.9622 | 124.7681 | 5.3146 | -0.17853 | 124.7864 | 4.9622 | 5.3146 | 5.1819 | 124.7681 | -124.942 | -124.9191
812.375 | 124.7635 | -5.1178 | 119.6136 | -0.24857 | 0.040573 | 0.036241 | 0.032353 | 0.07007 | 0.064258 | 0.17385 | -0.16022 | 119.6594 | -5.3604 | -4.9896 | 0.009155 | 0.1831 | 2.1149 | 0.70496 | 119.6045 | -5.3009 | -0.24262 | 0.045777 | 4.9576 | 0.12817 | -119.6045 | -0.18311 | -0.009155 | 5.2002 | 7.2327 | 5.8228 | 5.127 | 124.7772 | 4.9576 | 124.7223 | 5.3009 | -0.18311 | 124.7772 | 4.9576 | 5.3009 | 5.127 | 124.7223 | -124.9741 | -124.9146
813.375 | 124.6719 | -5.1682 | 119.6136 | -0.26382 | 0.038864 | 0.041368 | 0.029149 | 0.070925 | 0.065753 | 0.1747 | -0.21515 | 119.6136 | -5.4153 | -5.0903 | 0 | 0.20142 | 2.2064 | 0.6958 | 119.6091 | -5.3741 | -0.24719 | 0 | 4.953 | 0.07782 | -119.6136 | -0.20599 | -0.004577 | 5.2002 | 7.3746 | 5.864 | 5.1682 | 124.7818 | 4.953 | 124.7772 | 5.3696 | -0.20599 | 124.7818 | 4.953 | 5.3696 | 5.1682 | 124.7772 | -125.029 | -124.9878
814.375 | 124.7086 | -4.8248 | 119.9478 | -0.2562 | 0.038651 | 0.037309 | 0.028722 | 0.069643 | 0.066608 | 0.17663 | -0.1831 | 119.957 | -5.0308 | -4.7699 | -0.004578 | 0.11444 | 2.2659 | 0.70496 | 119.9478 | -5.0262 | -0.20599 | 0.009155 | 4.6417 | 0.054932 | -119.9524 | -0.20142 | 0 | 4.8477 | 7.0908 | 5.5298 | 4.8203 | 124.7818 | 4.6417 | 124.7726 | 4.9393 | -0.20142 | 124.7818 | 4.6417 | 4.9393 | 4.8203 | 124.7726 | -124.9786 | -124.9741
815.375 | 124.7223 | -4.8523 | 119.9249 | -0.24094 | 0.040787 | 0.0356 | 0.030858 | 0.071566 | 0.066394 | 0.17577 | -0.16937 | 119.9203 | -5.0354 | -4.7562 | 0.004578 | 0.064087 | 2.2018 | 0.49896 | 119.9295 | -5.0262 | -0.18311 | -0.004578 | 4.6829 | 0.09613 | -119.9203 | -0.17395 | 0.004577 | 4.866 | 7.0541 | 5.3513 | 4.8569 | 124.7726 | 4.6829 | 124.7818 | 4.9164 | -0.17395 | 124.7726 | 4.6829 | 4.9164 | 4.8569 | 124.7818 | -124.9603 | -124.9512
816.375 | 124.6857 | -5.2551 | 119.4946 | -0.22568 | 0.039719 | 0.036455 | 0.029362 | 0.071993 | 0.062549 | 0.17727 | -0.2243 | 119.4809 | -5.4703 | -5.1727 | -0.009155 | 0.036621 | 2.1835 | 0.72784 | 119.4809 | -5.4337 | -0.21515 | -0.013733 | 5.0308 | 0.082398 | -119.5038 | -0.17853 | -0.013733 | 5.246 | 7.4387 | 5.983 | 5.246 | 124.736 | 5.0308 | 124.736 | 5.2917 | -0.17853 | 124.736 | 5.0308 | 5.2917 | 5.246 | 124.736 | -124.9649 | -124.9283
817.375 | 124.7086 | -5.072 | 119.7006 | -0.30197 | 0.03801 | 0.034105 | 0.030644 | 0.069643 | 0.064685 | 0.17449 | -0.2243 | 119.7006 | -5.2689 | -5.0034 | -0.013733 | 0.032043 | 2.0828 | 0.55847 | 119.6777 | -5.2689 | -0.19684 | 0 | 4.8477 | 0.068664 | -119.7144 | -0.19684 | -0.022889 | 5.0446 | 7.1548 | 5.6305 | 5.0583 | 124.7726 | 4.8477 | 124.7498 | 5.1041 | -0.19684 | 124.7726 | 4.8477 | 5.1041 | 5.0583 | 124.7498 | -124.9695 | -124.9695
818.375 | 124.7269 | -6.0562 | 118.7027 | -0.38589 | 0.037155 | 0.042009 | 0.031712 | 0.068789 | 0.06319 | 0.17299 | -0.29297 | 118.6523 | -6.2851 | -6.0059 | 0 | 0.036621 | 2.1194 | 0.64087 | 118.6661 | -6.2759 | -0.22888 | -0.050354 | 5.7632 | 0.050354 | -118.7027 | -0.21973 | -0.036621 | 5.9921 | 8.1757 | 6.6971 | 6.0562 | 124.7086 | 5.7632 | 124.7223 | 6.0928 | -0.21973 | 124.7086 | 5.7632 | 6.0928 | 6.0562 | 124.7223 | -124.9878 | -124.9786
819.375 | 124.7131 | -5.928 | 118.8263 | -0.23331 | 0.039719 | 0.043504 | 0.031712 | 0.069002 | 0.063403 | 0.17086 | -0.33417 | 118.8309 | -6.1203 | -5.8594 | -0.004578 | 0.036621 | 2.0462 | 0.62714 | 118.8126 | -6.0974 | -0.19226 | 0.004578 | 5.5939 | 0.068665 | -118.8309 | -0.16937 | -0.013733 | 5.7861 | 7.9742 | 6.5552 | 5.9235 | 124.7589 | 5.5939 | 124.7406 | 5.9647 | -0.16937 | 124.7589 | 5.5939 | 5.9647 | 5.9235 | 124.7406 | -124.9466 | -124.9237
820.375 | 124.5941 | -5.8548 | 118.8766 | -0.10361 | 0.038651 | 0.039873 | 0.028935 | 0.067934 | 0.062976 | 0.17235 | -0.29755 | 118.8629 | -6.102 | -5.8228 | 0.013733 | 0.14648 | 2.037 | 2.4582 | 118.8721 | -6.0654 | -0.24719 | -0.013733 | 5.5573 | 0.032043 | -118.8629 | -0.21057 | -0.004578 | 5.8044 | 7.8918 | 8.313 | 5.8685 | 124.7177 | 5.5573 | 124.7269 | 6.0013 | -0.21057 | 124.7177 | 5.5573 | 6.0013 | 5.8685 | 124.7269 | -124.9786 | -124.942
821.375 | 124.7131 | -5.8365 | 118.9362 | -0.2562 | 0.038437 | 0.036668 | 0.030003 | 0.069857 | 0.064899 | 0.17342 | -0.28839 | 118.8995 | -6.0287 | -5.7678 | -0.009155 | 0.1236 | 1.2131 | 2.3529 | 118.8629 | -6.0471 | -0.19226 | -0.036621 | 5.5481 | 0.068665 | -118.9453 | -0.21057 | -0.073242 | 5.7404 | 7.0496 | 8.1894 | 5.8273 | 124.736 | 5.5481 | 124.6994 | 5.9601 | -0.21057 | 124.736 | 5.5481 | 5.9601 | 5.8273 | 124.6994 | -124.9649 | -124.9832
822.375 | 124.7131 | -5.6808 | 119.0781 | -0.27145 | 0.037583 | 0.038164 | 0.029576 | 0.066439 | 0.063403 | 0.17385 | -0.13733 | 119.1742 | -5.8182 | -5.5618 | 0.009155 | 0.091553 | 1.1627 | 2.417 | 119.0735 | -5.8456 | -0.13733 | 0.09613 | 5.5435 | 0.11902 | -119.0689 | -0.16479 | -0.004578 | 5.6808 | 6.8436 | 8.0978 | 5.69 | 124.855 | 5.5435 | 124.7543 | 5.7724 | -0.16479 | 124.855 | 5.5435 | 5.7724 | 5.69 | 124.7543 | -124.8962 | -124.9237
823.375 | 124.6857 | -5.5984 | 119.1467 | -0.34012 | 0.039078 | 0.039873 | 0.029362 | 0.06708 | 0.064471 | 0.17321 | -0.36621 | 119.1055 | -5.8273 | -5.5344 | -0.018311 | 0.082397 | 1.2497 | 2.4445 | 119.1788 | -5.777 | -0.22888 | -0.041199 | 5.2322 | 0.064087 | -119.165 | -0.17853 | 0.032043 | 5.4611 | 6.8481 | 8.0429 | 5.5801 | 124.704 | 5.2322 | 124.7772 | 5.6808 | -0.17853 | 124.704 | 5.2322 | 5.6808 | 5.5801 | 124.7772 | -124.9741 | -124.9237
824.375 | 124.7223 | -5.6305 | 119.101 | -0.2562 | 0.038437 | 0.033464 | 0.030431 | 0.067934 | 0.064899 | 0.17321 | -0.3479 | 119.0964 | -5.8136 | -5.5481 | 0.018311 | 0.050354 | 2.1423 | 2.4811 | 119.0872 | -5.8411 | -0.18311 | -0.004577 | 5.2826 | 0.082397 | -119.0826 | -0.21057 | -0.013733 | 5.4657 | 7.7728 | 8.1116 | 5.6488 | 124.7269 | 5.2826 | 124.7177 | 5.6808 | -0.21057 | 124.7269 | 5.2826 | 5.6808 | 5.6488 | 124.7177 | -124.9146 | -124.942
825.375 | 124.6857 | -5.5206 | 119.252 | -0.23331 | 0.039505 | 0.038164 | 0.034062 | 0.068789 | 0.065753 | 0.17385 | -0.50812 | 119.2337 | -5.7037 | -5.4428 | -0.022888 | 0.059509 | 0.86975 | 2.3529 | 119.2062 | -5.7129 | -0.18311 | -0.01831 | 5.0125 | 0.07782 | -119.2749 | -0.19226 | -0.045776 | 5.1956 | 6.3904 | 7.8735 | 5.4977 | 124.7543 | 5.0125 | 124.7269 | 5.5801 | -0.19226 | 124.7543 | 5.0125 | 5.5801 | 5.4977 | 124.7269 | -124.9557 | -124.9649
826.375 | 124.6674 | -5.3192 | 119.4214 | -0.28671 | 0.038864 | 0.037096 | 0.030003 | 0.065798 | 0.063403 | 0.17898 | -1.7761 | 119.3665 | -5.5527 | -5.2826 | -0.004578 | 0.032043 | 0.75073 | 2.7054 | 119.4077 | -5.5206 | -0.23346 | -0.054932 | 3.5431 | 0.036621 | -119.426 | -0.20142 | -0.013733 | 3.7766 | 6.0699 | 8.0246 | 5.3146 | 124.6857 | 3.5431 | 124.7269 | 5.3513 | -0.20142 | 124.6857 | 3.5431 | 5.3513 | 5.3146 | 124.7269 | -124.9741 | -124.942
827.375 | 124.7772 | -5.2872 | 119.4077 | -0.24094 | 0.036728 | 0.036028 | 0.031285 | 0.067721 | 0.063403 | 0.17577 | -1.5427 | 119.3436 | -5.5069 | -5.1544 | 0.10529 | 0.14191 | 0.34332 | 2.4628 | 119.3573 | -5.4932 | -0.21973 | -0.064087 | 3.7445 | 0.13275 | -119.3024 | -0.20599 | -0.050354 | 3.9642 | 5.6305 | 7.7499 | 5.3925 | 124.6307 | 3.7445 | 124.6445 | 5.4291 | -0.20599 | 124.6307 | 3.7445 | 5.4291 | 5.3925 | 124.6445 | -124.9146 | -124.9008
828.375 | 124.7772 | -5.2872 | 119.3893 | -0.19516 | 0.038651 | 0.0356 | 0.030644 | 0.06708 | 0.06554 | 0.17748 | -1.7624 | 119.339 | -5.5161 | -5.1682 | 0.11902 | 0.14191 | 0.36163 | 2.3438 | 119.3161 | -5.5069 | -0.22888 | -0.050354 | 3.5248 | 0.11902 | -119.2703 | -0.21973 | -0.073242 | 3.7537 | 5.6488 | 7.6309 | 5.4062 | 124.6262 | 3.5248 | 124.6033 | 5.4291 | -0.21973 | 124.6262 | 3.5248 | 5.4291 | 5.4062 | 124.6033 | -124.9054 | -124.8962
829.375 | 124.7726 | -5.2277 | 119.4763 | -0.27145 | 0.036515 | 0.033678 | 0.030431 | 0.066439 | 0.064899 | 0.1794 | -1.7624 | 119.4122 | -5.4382 | -5.0766 | 0.068665 | 0.09613 | 0.37994 | 2.3529 | 119.4031 | -5.4108 | -0.21057 | -0.064087 | 3.4653 | 0.15106 | -119.4077 | -0.18311 | -0.073242 | 3.6758 | 5.6076 | 7.5806 | 5.2963 | 124.6399 | 3.4653 | 124.6307 | 5.3238 | -0.18311 | 124.6399 | 3.4653 | 5.3238 | 5.2963 | 124.6307 | -124.9146 | -124.8871
830.375 | 124.7955 | -5.191 | 119.4901 | -0.2562 | 0.038651 | 0.034319 | 0.02979 | 0.065798 | 0.064044 | 0.1762 | -1.7258 | 119.4489 | -5.3787 | -5.0262 | 0.09613 | 0.09613 | 0.23804 | 2.5131 | 119.4443 | -5.397 | -0.18768 | -0.041198 | 3.4653 | 0.16479 | -119.3939 | -0.20599 | -0.045776 | 3.653 | 5.4291 | 7.7042 | 5.2872 | 124.6399 | 3.4653 | 124.6353 | 5.2872 | -0.20599 | 124.6399 | 3.4653 | 5.2872 | 5.2872 | 124.6353 | -124.8688 | -124.8871
831.375 | 124.7818 | -5.1132 | 119.5541 | -0.24094 | 0.037369 | 0.032182 | 0.030431 | 0.065584 | 0.063403 | 0.17556 | -1.6205 | 119.4992 | -5.3421 | -4.9759 | 0.10986 | 0.13275 | 0.34332 | 2.4582 | 119.4901 | -5.3192 | -0.22888 | -0.054931 | 3.4927 | 0.13733 | -119.4443 | -0.20599 | -0.064087 | 3.7216 | 5.4565 | 7.5714 | 5.2231 | 124.6124 | 3.4927 | 124.6033 | 5.246 | -0.20599 | 124.6124 | 3.4927 | 5.246 | 5.2231 | 124.6033 | -124.8962 | -124.8734
832.375 | 124.7177 | -5.3787 | 119.3298 | -0.24094 | 0.036515 | 0.035814 | 0.033421 | 0.066866 | 0.064471 | 0.17769 | -1.8219 | 119.2886 | -5.5664 | -5.2185 | 0.073242 | 0.068665 | 1.7166 | 2.3483 | 119.2703 | -5.5527 | -0.18768 | -0.041199 | 3.5568 | 0.16022 | -119.2566 | -0.17395 | -0.059509 | 3.7445 | 7.0953 | 7.7271 | 5.452 | 124.6674 | 3.5568 | 124.649 | 5.4474 | -0.17395 | 124.6674 | 3.5568 | 5.4474 | 5.452 | 124.649 | -124.8962 | -124.8825
833.375 | 124.7772 | -5.1956 | 119.4901 | -0.26382 | 0.036728 | 0.03325 | 0.031926 | 0.06708 | 0.064471 | 0.17727 | -1.6846 | 119.4397 | -5.4062 | -5.0537 | 0.09613 | 0.07782 | 0.15106 | 2.1194 | 119.4443 | -5.4016 | -0.21057 | -0.050354 | 3.511 | 0.14191 | -119.3939 | -0.20599 | -0.045776 | 3.7216 | 5.3467 | 7.3151 | 5.2917 | 124.6353 | 3.511 | 124.6399 | 5.2734 | -0.20599 | 124.6353 | 3.511 | 5.2734 | 5.2917 | 124.6399 | -124.8962 | -124.8917
834.375 | 124.8322 | -5.1453 | 119.4992 | -0.034943 | 0.040573 | 0.032823 | 0.031285 | 0.06473 | 0.064899 | 0.17791 | -1.8082 | 119.4443 | -5.397 | -4.985 | 0.14191 | 0.11902 | 0.091553 | 2.2018 | 119.4534 | -5.3375 | -0.25177 | -0.054932 | 3.3371 | 0.16022 | -119.3573 | -0.19226 | -0.045777 | 3.5889 | 5.2368 | 7.3471 | 5.2872 | 124.5895 | 3.3371 | 124.5987 | 5.2643 | -0.19226 | 124.5895 | 3.3371 | 5.2643 | 5.2872 | 124.5987 | -124.8962 | -124.8367
835.375 | 124.8184 | -5.1682 | 119.5129 | -0.17227 | 0.036942 | 0.034746 | 0.029149 | 0.059603 | 0.062335 | 0.17898 | -1.593 | 119.4489 | -5.3787 | -5.1361 | -0.13733 | 0.10986 | 0 | 1.6342 | 119.4077 | -5.3558 | -0.21057 | -0.064086 | 3.5751 | 0.032044 | -119.6503 | -0.18768 | -0.10529 | 3.7857 | 5.1682 | 6.8024 | 5.0308 | 124.617 | 3.5751 | 124.5758 | 5.278 | -0.18768 | 124.617 | 3.5751 | 5.278 | 5.0308 | 124.5758 | -124.8917 | -124.8688
836.375 | 124.8093 | -5.159 | 119.5267 | -0.34012 | 0.035874 | 0.034746 | 0.031499 | 0.066439 | 0.062122 | 0.18026 | -1.6067 | 119.458 | -5.3787 | -4.9622 | 0.12817 | 0.11444 | 0.1831 | 2.2247 | 119.4443 | -5.3146 | -0.21973 | -0.068664 | 3.5522 | 0.19684 | -119.3985 | -0.15564 | -0.082397 | 3.772 | 5.3421 | 7.3837 | 5.2872 | 124.617 | 3.5522 | 124.6033 | 5.2734 | -0.15564 | 124.617 | 3.5522 | 5.2734 | 5.2872 | 124.6033 | -124.9054 | -124.8413
837.375 | 124.8459 | -5.1682 | 119.4992 | -0.55374 | 0.036728 | 0.0356 | 0.030858 | 0.065157 | 0.064899 | 0.17812 | -1.5335 | 119.3893 | -5.4062 | -5.0171 | 0.11902 | 0.14191 | 0.36163 | 1.8082 | 119.3893 | -5.3604 | -0.23804 | -0.10986 | 3.6346 | 0.15106 | -119.3802 | -0.19226 | -0.10986 | 3.8727 | 5.5298 | 6.9763 | 5.2872 | 124.5575 | 3.6346 | 124.5575 | 5.3101 | -0.19226 | 124.5575 | 3.6346 | 5.3101 | 5.2872 | 124.5575 | -124.9054 | -124.8596
838.375 | 124.8047 | -5.0995 | 119.5679 | -0.18753 | 0.036942 | 0.031969 | 0.031926 | 0.066012 | 0.064899 | 0.17833 | -1.2268 | 119.4443 | -5.3375 | -4.9301 | 0.14191 | 0.11444 | 0.12817 | 2.1057 | 119.4626 | -5.3055 | -0.23804 | -0.1236 | 3.8727 | 0.16937 | -119.426 | -0.20599 | -0.10529 | 4.1107 | 5.2277 | 7.2052 | 5.2414 | 124.5438 | 3.8727 | 124.5621 | 5.2139 | -0.20599 | 124.5438 | 3.8727 | 5.2139 | 5.2414 | 124.5621 | -124.9054 | -124.8734
839.375 | 124.7772 | -5.1224 | 119.5679 | -0.21805 | 0.037583 | 0.030901 | 0.033635 | 0.066012 | 0.064044 | 0.1809 | -1.2543 | 119.4489 | -5.3284 | -4.9301 | 0.11444 | 0.11444 | 0.12817 | 2.298 | 119.4672 | -5.3238 | -0.20599 | -0.11902 | 3.8681 | 0.19226 | -119.4534 | -0.20142 | -0.10071 | 4.0741 | 5.2505 | 7.4203 | 5.2368 | 124.5712 | 3.8681 | 124.5895 | 5.2368 | -0.20142 | 124.5712 | 3.8681 | 5.2368 | 5.2368 | 124.5895 | -124.8962 | -124.8917
840.375 | 124.8047 | -5.0354 | 119.6182 | -0.23331 | 0.03566 | 0.039018 | 0.03214 | 0.065157 | 0.06319 | 0.18026 | -1.1581 | 119.545 | -5.246 | -4.866 | 0.11902 | 0.13275 | 0.12817 | 2.3117 | 119.545 | -5.2277 | -0.21057 | -0.073242 | 3.8773 | 0.16937 | -119.4992 | -0.19226 | -0.073242 | 4.0878 | 5.1636 | 7.3471 | 5.1544 | 124.5804 | 3.8773 | 124.5804 | 5.1682 | -0.19226 | 124.5804 | 3.8773 | 5.1682 | 5.1544 | 124.5804 | -124.8642 | -124.8459
841.375 | 124.8276 | -5.1682 | 119.5129 | -0.095978 | 0.036301 | 0.030473 | 0.030858 | 0.062594 | 0.064258 | 0.17876 | -1.2863 | 119.4168 | -5.3741 | -5.0079 | 0.11902 | 0.13275 | 0.16479 | 2.1194 | 119.4214 | -5.3513 | -0.20599 | -0.09613 | 3.8818 | 0.16022 | -119.3939 | -0.18311 | -0.091552 | 4.0878 | 5.3329 | 7.2876 | 5.2872 | 124.585 | 3.8818 | 124.5895 | 5.3009 | -0.18311 | 124.585 | 3.8818 | 5.3009 | 5.2872 | 124.5895 | -124.8871 | -124.8642
842.375 | 124.791 | -5.7037 | 118.9407 | -0.06546 | 0.03801 | 0.034319 | 0.031071 | 0.064516 | 0.063403 | 0.17919 | -1.5244 | 118.8904 | -5.9418 | -5.5801 | 0.10071 | 0.10986 | 0.082397 | 2.6779 | 118.8446 | -5.9006 | -0.23804 | -0.050354 | 4.1794 | 0.1236 | -118.84 | -0.19684 | -0.096131 | 4.4174 | 5.7861 | 8.3817 | 5.8044 | 124.5941 | 4.1794 | 124.5483 | 5.8136 | -0.19684 | 124.5941 | 4.1794 | 5.8136 | 5.8044 | 124.5483 | -124.8825 | -124.8413
843.375 | 124.8322 | -5.484 | 119.1605 | -0.11887 | 0.036728 | 0.036668 | 0.03278 | 0.065798 | 0.062762 | 0.17727 | -1.4603 | 119.0826 | -5.7129 | -5.3192 | 0.1236 | 0.1236 | 0.045776 | 2.7054 | 119.0964 | -5.6717 | -0.22888 | -0.077819 | 4.0237 | 0.1648 | -119.0369 | -0.18768 | -0.064086 | 4.2526 | 5.5298 | 8.1894 | 5.6076 | 124.5667 | 4.0237 | 124.5804 | 5.6076 | -0.18768 | 124.5667 | 4.0237 | 5.6076 | 5.6076 | 124.5804 | -124.8734 | -124.8322
844.375 | 124.8276 | -5.5801 | 119.0689 | -0.11124 | 0.036087 | 0.033891 | 0.03278 | 0.066652 | 0.065753 | 0.17898 | -1.6022 | 119.0002 | -5.7816 | -5.4291 | 0.1236 | 0.12817 | 0.068665 | 2.7054 | 119.0002 | -5.7495 | -0.20142 | -0.068665 | 3.978 | 0.15106 | -118.9453 | -0.16937 | -0.068665 | 4.1794 | 5.6488 | 8.2855 | 5.7037 | 124.5804 | 3.978 | 124.5804 | 5.7083 | -0.16937 | 124.5804 | 3.978 | 5.7083 | 5.7037 | 124.5804 | -124.8505 | -124.8184
845.375 | 124.7818 | -5.6763 | 118.9911 | -0.019684 | 0.036301 | 0.040941 | 0.033849 | 0.065798 | 0.062549 | 0.17684 | -1.7395 | 118.9041 | -5.9143 | -5.5389 | 0.11444 | 0.11444 | 0.091553 | 2.4628 | 118.9041 | -5.864 | -0.23804 | -0.086975 | 3.9368 | 0.13733 | -118.8766 | -0.18768 | -0.086975 | 4.1748 | 5.7678 | 8.139 | 5.7907 | 124.5804 | 3.9368 | 124.5804 | 5.7907 | -0.18768 | 124.5804 | 3.9368 | 5.7907 | 5.7907 | 124.5804 | -124.9054 | -124.855
846.375 | 124.8138 | -5.7266 | 118.9316 | -0.1265 | 0.037155 | 0.037096 | 0.032994 | 0.066012 | 0.065112 | 0.17791 | -1.3962 | 118.8629 | -5.9463 | -5.5435 | 0.1236 | 0.1236 | 0.75073 | 2.8702 | 118.8538 | -5.9097 | -0.21973 | -0.068665 | 4.3304 | 0.18311 | -118.808 | -0.1831 | -0.07782 | 4.5502 | 6.4774 | 8.5968 | 5.8502 | 124.5895 | 4.3304 | 124.5804 | 5.8502 | -0.1831 | 124.5895 | 4.3304 | 5.8502 | 5.8502 | 124.5804 | -124.8779 | -124.8413
847.375 | 124.7726 | -5.9006 | 118.7714 | -0.11124 | 0.035874 | 0.038805 | 0.033208 | 0.067293 | 0.06319 | 0.17876 | -1.4877 | 118.6569 | -6.1295 | -5.7404 | 0.10529 | 0.13275 | 0.46692 | 2.8748 | 118.6523 | -6.0699 | -0.22888 | -0.11444 | 4.4128 | 0.16022 | -118.6661 | -0.16937 | -0.11902 | 4.6417 | 6.3675 | 8.7753 | 6.0059 | 124.5575 | 4.4128 | 124.5529 | 6.0333 | -0.16937 | 124.5575 | 4.4128 | 6.0333 | 6.0059 | 124.5529 | -124.9008 | -124.8413
848.375 | 124.7635 | -5.2139 | 119.4534 | 0.14053 | 0.039078 | 0.037523 | 0.034062 | 0.06708 | 0.064258 | 0.17791 | -1.181 | 119.3756 | -5.4199 | -5.0949 | 0.064087 | 0.068665 | 0.16022 | 2.8473 | 119.3985 | -5.3787 | -0.20599 | -0.07782 | 4.0329 | 0.11902 | -119.3893 | -0.16479 | -0.054931 | 4.2389 | 5.3741 | 8.0612 | 5.278 | 124.5895 | 4.0329 | 124.6124 | 5.2826 | -0.16479 | 124.5895 | 4.0329 | 5.2826 | 5.278 | 124.6124 | -124.8734 | -124.8322
849.375 | 124.7681 | -5.2643 | 119.3893 | -0.012055 | 0.039719 | 0.036455 | 0.035557 | 0.067507 | 0.066608 | 0.17983 | -0.97961 | 119.3298 | -5.4749 | -5.1544 | 0.073242 | 0.091553 | 0.21057 | 2.8748 | 119.3161 | -5.4611 | -0.21057 | -0.059509 | 4.2847 | 0.10986 | -119.3161 | -0.19684 | -0.073242 | 4.4952 | 5.4749 | 8.139 | 5.3375 | 124.5941 | 4.2847 | 124.5804 | 5.3558 | -0.19684 | 124.5941 | 4.2847 | 5.3558 | 5.3375 | 124.5804 | -124.8642 | -124.8505
850.375 | 124.7543 | -5.0217 | 119.6411 | -0.16464 | 0.038864 | 0.036668 | 0.034917 | 0.064944 | 0.064258 | 0.18026 | -0.87891 | 119.5679 | -5.2551 | -4.8752 | 0.10071 | 0.1236 | 0.10986 | 2.9709 | 119.5496 | -5.2048 | -0.23346 | -0.073242 | 4.1428 | 0.14648 | -119.5404 | -0.18311 | -0.091552 | 4.3762 | 5.1315 | 7.9926 | 5.1224 | 124.5895 | 4.1428 | 124.5712 | 5.1453 | -0.18311 | 124.5895 | 4.1428 | 5.1453 | 5.1224 | 124.5712 | -124.8962 | -124.8459
851.375 | 124.7864 | -5.0674 | 119.6411 | 0.17105 | 0.039505 | 0.040727 | 0.035771 | 0.066225 | 0.064258 | 0.1809 | -0.95673 | 119.5084 | -5.3055 | -4.9438 | 0.059509 | 0.068665 | 0.11444 | 2.8427 | 119.5312 | -5.2277 | -0.23804 | -0.13275 | 4.1107 | 0.1236 | -119.5816 | -0.16022 | -0.10986 | 4.3488 | 5.1819 | 7.9102 | 5.127 | 124.5758 | 4.1107 | 124.5987 | 5.1361 | -0.16022 | 124.5758 | 4.1107 | 5.1361 | 5.127 | 124.5987 | -124.9466 | -124.8688
852.375 | 124.7772 | -5.0812 | 119.5999 | -0.012055 | 0.037369 | 0.038164 | 0.03513 | 0.065371 | 0.065112 | 0.18239 | -0.79651 | 119.5633 | -5.2368 | -5.0766 | -0.009155 | 0.068665 | -0.059509 | 2.9663 | 119.4946 | -5.1727 | -0.15564 | -0.036622 | 4.2847 | 0.004578 | -119.6091 | -0.091552 | -0.10529 | 4.4403 | 5.0217 | 8.0475 | 5.072 | 124.6445 | 4.2847 | 124.5758 | 5.1498 | -0.091552 | 124.6445 | 4.2847 | 5.1498 | 5.072 | 124.5758 | -124.8367 | -124.7726
853.375 | 124.7406 | -6.6971 | 117.9749 | -0.07309 | 0.039933 | 0.045 | 0.034276 | 0.066012 | 0.064044 | 0.17428 | -1.4374 | 117.9108 | -6.871 | -6.5781 | 0.064087 | 0.086975 | 0.14648 | 2.774 | 117.8833 | -6.8619 | -0.17395 | -0.064087 | 5.2597 | 0.11902 | -117.9108 | -0.16479 | -0.091553 | 5.4337 | 6.8436 | 9.4711 | 6.7612 | 124.6079 | 5.2597 | 124.5804 | 6.7841 | -0.16479 | 124.6079 | 5.2597 | 6.7841 | 6.7612 | 124.5804 | -124.8459 | -124.8367
854.375 | 124.7223 | -6.395 | 118.2587 | -0.13412 | 0.041642 | 0.042863 | 0.033849 | 0.066866 | 0.062549 | 0.17748 | -1.1902 | 118.1854 | -6.6101 | -6.2714 | 0.009155 | 0.004578 | 0.27466 | 2.774 | 118.1442 | -6.5689 | -0.21515 | -0.073242 | 5.2048 | 0.1236 | -118.2495 | -0.17395 | -0.11444 | 5.4199 | 6.6696 | 9.169 | 6.4041 | 124.5804 | 5.2048 | 124.5392 | 6.3995 | -0.17395 | 124.5804 | 5.2048 | 6.3995 | 6.4041 | 124.5392 | -124.8688 | -124.8276
855.3906 | 124.6902 | -6.4316 | 118.2632 | -0.20279 | 0.041001 | 0.043504 | 0.040257 | 0.06708 | 0.062549 | 0.17855 | -1.5335 | 118.2724 | -6.6742 | -6.3446 | 0.004578 | -0.013733 | 0.36621 | 2.8061 | 118.19 | -6.6284 | -0.24261 | 0.009155 | 4.8981 | 0.086976 | -118.2587 | -0.19684 | -0.073243 | 5.1407 | 6.7978 | 9.2377 | 6.4362 | 124.704 | 4.8981 | 124.6216 | 6.4178 | -0.19684 | 124.704 | 4.8981 | 6.4178 | 6.4362 | 124.6216 | -124.9374 | -124.8917
856.375 | 124.7498 | -6.0104 | 118.6111 | 0.064239 | 0.039505 | 0.043718 | 0.037053 | 0.068789 | 0.063617 | 0.18068 | -1.1948 | 118.5928 | -6.2393 | -5.928 | 0.054932 | 0.09613 | 0.045776 | 2.9022 | 118.5425 | -6.189 | -0.22888 | -0.018311 | 4.8157 | 0.082397 | -118.5562 | -0.17853 | -0.068665 | 5.0446 | 6.0562 | 8.9127 | 6.0654 | 124.6033 | 4.8157 | 124.5529 | 6.1066 | -0.17853 | 124.6033 | 4.8157 | 6.1066 | 6.0654 | 124.5529 | -124.8505 | -124.8001
857.375 | 124.7406 | -6.0562 | 118.634 | 0.087128 | 0.03801 | 0.043932 | 0.037694 | 0.066866 | 0.064685 | 0.18047 | -1.2222 | 118.6249 | -6.1798 | -5.9189 | 0.10529 | 0.11902 | 0.036621 | 2.9709 | 118.5287 | -6.2485 | -0.1236 | -0.009155 | 4.834 | 0.13733 | -118.5287 | -0.19226 | -0.10529 | 4.9576 | 6.0928 | 9.0271 | 6.1615 | 124.6811 | 4.834 | 124.585 | 6.1752 | -0.19226 | 124.6811 | 4.834 | 6.1752 | 6.1615 | 124.585 | -124.8138 | -124.8825
858.375 | 124.8047 | -5.9235 | 118.6798 | 0.11002 | 0.042496 | 0.041368 | 0.040684 | 0.067934 | 0.063831 | 0.17962 | -1.0345 | 118.6478 | -6.1615 | -5.7953 | 0.10071 | 0.1236 | 0.018311 | 2.9984 | 118.6157 | -6.1066 | -0.23804 | -0.032044 | 4.8889 | 0.12817 | -118.5791 | -0.18311 | -0.064087 | 5.127 | 5.9418 | 8.9218 | 6.0242 | 124.5712 | 4.8889 | 124.5392 | 6.0471 | -0.18311 | 124.5712 | 4.8889 | 6.0471 | 6.0242 | 124.5392 | -124.8413 | -124.7864
859.375 | 124.8047 | -6.2256 | 118.4189 | 0.18631 | 0.041428 | 0.044145 | 0.041112 | 0.068361 | 0.064899 | 0.17812 | -0.98419 | 118.3548 | -6.4682 | -6.102 | 0.12817 | 0.1236 | 0 | 3.0853 | 118.3319 | -6.4041 | -0.24261 | -0.064087 | 5.2414 | 0.1236 | -118.2907 | -0.17853 | -0.086975 | 5.484 | 6.2256 | 9.3109 | 6.3538 | 124.5804 | 5.2414 | 124.5575 | 6.3492 | -0.17853 | 124.5804 | 5.2414 | 6.3492 | 6.3538 | 124.5575 | -124.8871 | -124.823
860.375 | 124.7406 | -6.134 | 118.5059 | -0.2562 | 0.041642 | 0.042436 | 0.039403 | 0.066866 | 0.061908 | 0.18068 | -0.79193 | 118.5333 | -6.2759 | -6.015 | 0.14191 | 0.091553 | 0.13733 | 3.1906 | 118.4692 | -6.3171 | -0.14191 | 0.027466 | 5.3421 | 0.11902 | -118.364 | -0.18311 | -0.036621 | 5.484 | 6.2714 | 9.3246 | 6.2759 | 124.6674 | 5.3421 | 124.6033 | 6.2256 | -0.18311 | 124.6674 | 5.3421 | 6.2256 | 6.2759 | 124.6033 | -124.7818 | -124.823
861.375 | 124.791 | -6.0287 | 118.602 | 0.14053 | 0.040146 | 0.042436 | 0.042821 | 0.067721 | 0.06319 | 0.18239 | -0.79193 | 118.6249 | -6.221 | -5.8731 | 0.16937 | 0.13275 | 0.036621 | 3.273 | 118.5242 | -6.1981 | -0.19226 | 0.022888 | 5.2368 | 0.15564 | -118.4326 | -0.16937 | -0.07782 | 5.4291 | 6.0654 | 9.3018 | 6.1981 | 124.6536 | 5.2368 | 124.5529 | 6.1615 | -0.16937 | 124.6536 | 5.2368 | 6.1615 | 6.1981 | 124.5529 | -124.823 | -124.8001
862.375 | 124.7772 | -5.5435 | 119.046 | 0.19394 | 0.042282 | 0.044572 | 0.042821 | 0.066652 | 0.062335 | 0.18175 | -0.67749 | 119.133 | -5.7037 | -5.4291 | 0.77362 | 0.1236 | 0.013733 | 3.3554 | 119.0369 | -5.7266 | -0.16022 | 0.086975 | 4.866 | 0.11444 | -118.2724 | -0.18311 | -0.009156 | 5.0262 | 5.5573 | 8.8989 | 6.3171 | 124.6765 | 4.866 | 124.5804 | 5.6671 | -0.18311 | 124.6765 | 4.866 | 5.6671 | 6.3171 | 124.5804 | -124.7498 | -124.7726
863.375 | 124.7772 | -5.4245 | 119.2154 | 0.36179 | 0.040787 | 0.043932 | 0.041753 | 0.066866 | 0.064471 | 0.18368 | -0.67291 | 119.1879 | -5.6534 | -5.2734 | 0.83313 | 0.12817 | 0 | 3.4012 | 119.1055 | -5.6305 | -0.22888 | -0.027466 | 4.7516 | 0.15106 | -118.3823 | -0.20599 | -0.10986 | 4.9805 | 5.4245 | 8.8257 | 6.2576 | 124.6124 | 4.7516 | 124.53 | 5.5527 | -0.20599 | 124.6124 | 4.7516 | 5.5527 | 6.2576 | 124.53 | -124.8688 | -124.8459
864.375 | 124.7772 | -6.0379 | 118.5471 | 0.37704 | 0.042923 | 0.040086 | 0.039616 | 0.068575 | 0.060199 | 0.17876 | -0.95673 | 118.5333 | -6.3309 | -5.9326 | 3.9825 | 0.11902 | 0.036621 | 3.3463 | 118.4921 | -6.2164 | -0.29297 | -0.013733 | 5.0812 | 0.10529 | -114.5645 | -0.17853 | -0.054932 | 5.3741 | 6.0745 | 9.3842 | 10.0204 | 124.5712 | 5.0812 | 124.53 | 6.1569 | -0.17853 | 124.5712 | 5.0812 | 6.1569 | 10.0204 | 124.53 | -124.8779 | -124.7635
865.3906 | 124.7864 | -5.6351 | 118.9728 | 0.033722 | 0.042282 | 0.041154 | 0.039189 | 0.067721 | 0.061908 | 0.1809 | -0.83313 | 119.0323 | -5.777 | -5.4749 | 2.9434 | 0.14191 | 0.1236 | 3.4836 | 118.9545 | -5.8182 | -0.14191 | 0.05951 | 4.8019 | 0.16022 | -116.0294 | -0.18311 | -0.01831 | 4.9438 | 5.7587 | 9.1187 | 8.5785 | 124.6674 | 4.8019 | 124.5895 | 5.777 | -0.18311 | 124.6674 | 4.8019 | 5.777 | 8.5785 | 124.5895 | -124.7498 | -124.791
866.375 | 124.7864 | -5.1498 | 119.4397 | 0.087128 | 0.045487 | 0.042863 | 0.042607 | 0.069216 | 0.063617 | 0.18474 | -0.85144 | 119.4763 | -5.3925 | -4.9393 | 2.8885 | 0.1236 | -0.3479 | 3.2547 | 119.339 | -5.3421 | -0.24261 | 0.036621 | 4.2984 | 0.21057 | -116.5512 | -0.19226 | -0.10071 | 4.541 | 4.8019 | 8.4045 | 8.0383 | 124.6262 | 4.2984 | 124.4888 | 5.2734 | -0.19226 | 124.6262 | 4.2984 | 5.2734 | 8.0383 | 124.4888 | -124.8322 | -124.7818
867.375 | 124.8001 | -4.8065 | 119.8196 | 0.12527 | 0.044205 | 0.036241 | 0.043462 | 0.06943 | 0.06319 | 0.18752 | -0.97504 | 119.8105 | -5.0034 | -4.6234 | 2.9938 | 0.13275 | -0.032043 | 3.5065 | 119.7556 | -4.9622 | -0.19684 | -0.009155 | 3.8315 | 0.18311 | -116.8259 | -0.15564 | -0.064087 | 4.0283 | 4.7745 | 8.313 | 7.8003 | 124.617 | 3.8315 | 124.5621 | 4.9393 | -0.15564 | 124.617 | 3.8315 | 4.9393 | 7.8003 | 124.5621 | -124.823 | -124.7818
868.375 | 124.7543 | -4.66 | 119.9661 | 0.10239 | 0.042282 | 0.03795 | 0.043034 | 0.065798 | 0.063617 | 0.19137 | -0.85144 | 119.9295 | -4.9026 | -4.5136 | 2.5589 | 0.14191 | 0.022888 | 3.5294 | 119.8791 | -4.8386 | -0.24262 | -0.036621 | 3.8086 | 0.14648 | -117.4072 | -0.17853 | -0.086975 | 4.0512 | 4.6829 | 8.1894 | 7.2189 | 124.5895 | 3.8086 | 124.5392 | 4.8019 | -0.17853 | 124.5895 | 3.8086 | 4.8019 | 7.2189 | 124.5392 | -124.8688 | -124.8047
869.375 | 124.7589 | -4.7058 | 119.9753 | 0.21683 | 0.043991 | 0.039659 | 0.045171 | 0.069857 | 0.063403 | 0.18624 | -0.89722 | 120.0119 | -4.9118 | -4.6051 | 2.5543 | 0.068665 | 0.11902 | 3.4561 | 119.8654 | -4.8981 | -0.20599 | 0.036621 | 3.8086 | 0.10071 | -117.421 | -0.19226 | -0.10986 | 4.0146 | 4.8248 | 8.1619 | 7.2601 | 124.7177 | 3.8086 | 124.5712 | 4.7745 | -0.19226 | 124.7177 | 3.8086 | 4.7745 | 7.2601 | 124.5712 | -124.8871 | -124.8734
870.375 | 124.7314 | -4.4907 | 120.1584 | 1.1247 | 0.043778 | 0.036241 | 0.039189 | 0.068148 | 0.064044 | 0.19008 | -0.89722 | 120.108 | -4.7104 | -4.3671 | 1.2039 | 0.082397 | 0.23346 | 3.5339 | 120.0577 | -4.6783 | -0.21973 | -0.050354 | 3.5934 | 0.1236 | -118.9545 | -0.18768 | -0.10071 | 3.8132 | 4.7241 | 8.0246 | 5.6946 | 124.5987 | 3.5934 | 124.5483 | 4.5731 | -0.18768 | 124.5987 | 3.5934 | 4.5731 | 5.6946 | 124.5483 | -124.8688 | -124.8367
871.375 | 124.7589 | -3.9642 | 120.6665 | 0.24734 | 0.044846 | 0.041154 | 0.04688 | 0.067721 | 0.065112 | 0.19201 | -0.62256 | 120.7352 | -4.1336 | -3.7354 | 0.84686 | 0.11902 | 1.0712 | 3.5751 | 120.5429 | -4.1245 | -0.16937 | 0.068664 | 3.3417 | 0.22888 | -119.8196 | -0.16022 | -0.1236 | 3.511 | 5.0354 | 7.5394 | 4.8111 | 124.6994 | 3.3417 | 124.5071 | 4.0833 | -0.16022 | 124.6994 | 3.3417 | 4.0833 | 4.8111 | 124.5071 | -124.8001 | -124.791
872.375 | 124.7818 | -4.1428 | 120.4651 | 0.20157 | 0.045487 | 0.037096 | 0.045171 | 0.070284 | 0.06618 | 0.19286 | -0.68207 | 120.5383 | -4.3304 | -3.9642 | 0.66376 | 0.15106 | 1.4557 | 3.6575 | 120.3918 | -4.3213 | -0.18768 | 0.073242 | 3.4607 | 0.17853 | -119.8013 | -0.17853 | -0.073242 | 3.6484 | 5.5984 | 7.8003 | 4.8065 | 124.6811 | 3.4607 | 124.5346 | 4.2938 | -0.17853 | 124.6811 | 3.4607 | 4.2938 | 4.8065 | 124.5346 | -124.7955 | -124.7864
873.375 | 124.7406 | -4.0649 | 120.5566 | 0.14053 | 0.047409 | 0.034319 | 0.045384 | 0.069002 | 0.064471 | 0.19521 | -0.5722 | 120.5887 | -4.3167 | -3.9139 | 0.6546 | 0.10071 | 2.5909 | 3.6667 | 120.5154 | -4.2526 | -0.25177 | 0.032043 | 3.4927 | 0.15106 | -119.902 | -0.18768 | -0.041199 | 3.7445 | 6.6559 | 7.7316 | 4.7195 | 124.6536 | 3.4927 | 124.5804 | 4.1656 | -0.18768 | 124.6536 | 3.4927 | 4.1656 | 4.7195 | 124.5804 | -124.8734 | -124.8093
874.375 | 124.7772 | -4.0604 | 120.5521 | -1.1259 | 0.045273 | 0.039873 | 0.043675 | 0.068575 | 0.063831 | 0.19393 | -0.58594 | 120.5612 | -4.2892 | -3.8773 | 0.57678 | 0.17395 | 2.5864 | 3.717 | 120.4971 | -4.2389 | -0.22888 | 0.009155 | 3.4744 | 0.18311 | -119.9753 | -0.17853 | -0.054932 | 3.7033 | 6.6467 | 7.7774 | 4.6371 | 124.6216 | 3.4744 | 124.5575 | 4.2343 | -0.17853 | 124.6216 | 3.4744 | 4.2343 | 4.6371 | 124.5575 | -124.8413 | -124.791
875.375 | 124.7177 | -4.0558 | 120.6436 | 0.16342 | 0.044205 | 0.040941 | 0.048802 | 0.069002 | 0.065112 | 0.1935 | -0.60883 | 120.6619 | -4.2618 | -3.9551 | 0.52643 | 0.19684 | 2.6962 | 3.6026 | 120.5566 | -4.2389 | -0.20599 | 0.01831 | 3.447 | 0.10071 | -120.1172 | -0.18311 | -0.086975 | 3.653 | 6.752 | 7.6584 | 4.5822 | 124.7177 | 3.447 | 124.6124 | 4.2526 | -0.18311 | 124.7177 | 3.447 | 4.2526 | 4.5822 | 124.6124 | -124.9054 | -124.8825
876.375 | 124.6811 | -4.0421 | 120.6162 | 0.11002 | 0.046769 | 0.039018 | 0.046452 | 0.067934 | 0.06554 | 0.19115 | -0.56763 | 120.6757 | -4.2618 | -3.9505 | 0.40283 | 0.17853 | 2.6871 | 3.6209 | 120.5795 | -4.2343 | -0.21973 | 0.059509 | 3.4744 | 0.091553 | -120.2133 | -0.19226 | -0.036621 | 3.6942 | 6.7291 | 7.663 | 4.4449 | 124.7177 | 3.4744 | 124.6216 | 4.2206 | -0.19226 | 124.7177 | 3.4744 | 4.2206 | 4.4449 | 124.6216 | -124.8779 | -124.8505
877.375 | 124.8047 | -3.8361 | 120.7993 | 0.20157 | 0.046769 | 0.045427 | 0.046025 | 0.069002 | 0.064899 | 0.1935 | -0.6958 | 120.8496 | -4.0512 | -3.7033 | 0.43945 | 1.9958 | 2.6001 | 3.6713 | 120.7352 | -4.0329 | -0.21515 | 0.050354 | 3.1403 | 0.13275 | -120.3598 | -0.19684 | -0.064087 | 3.3554 | 6.4362 | 7.5073 | 4.2755 | 124.6857 | 3.1403 | 124.5712 | 5.8319 | -0.19684 | 124.6857 | 3.1403 | 5.8319 | 4.2755 | 124.5712 | -124.8505 | -124.8322
878.375 | 124.736 | -3.9505 | 120.6848 | 0.17105 | 0.0457 | 0.037523 | 0.047093 | 0.06943 | 0.06319 | 0.19585 | -0.76904 | 120.7764 | -4.1382 | -3.804 | 0.36163 | 0.1831 | 2.6047 | 3.7399 | 120.6528 | -4.1245 | -0.18768 | 0.091553 | 3.1815 | 0.14648 | -120.3232 | -0.17395 | -0.032043 | 3.3691 | 6.5552 | 7.6904 | 4.3121 | 124.7269 | 3.1815 | 124.6033 | 4.1336 | -0.17395 | 124.7269 | 3.1815 | 4.1336 | 4.3121 | 124.6033 | -124.823 | -124.8093
879.375 | 124.7086 | -4.1931 | 120.4285 | 0.21683 | 0.047196 | 0.043077 | 0.046666 | 0.069857 | 0.064258 | 0.19072 | -0.89722 | 120.488 | -4.4403 | -4.0146 | 0.32044 | 0.20599 | 2.6733 | 3.6163 | 120.4468 | -4.3808 | -0.24719 | 0.059509 | 3.2959 | 0.17853 | -120.108 | -0.18768 | 0.01831 | 3.5431 | 6.8665 | 7.8094 | 4.5135 | 124.6811 | 3.2959 | 124.6399 | 4.3991 | -0.18768 | 124.6811 | 3.2959 | 4.3991 | 4.5135 | 124.6399 | -124.8688 | -124.8093
880.375 | 125.1022 | -4.2892 | 120.2316 | 0.1329 | 0.048264 | 0.042863 | 0.046666 | 0.070925 | 0.063617 | 0.19243 | -0.92468 | 120.4651 | -4.4724 | -4.0878 | 0.35706 | 0.33875 | 2.5818 | 3.7354 | 120.3506 | -4.422 | -0.1831 | 0.23346 | 3.3646 | 0.20142 | -119.8746 | -0.13275 | 0.11902 | 3.5477 | 6.871 | 8.0246 | 4.6463 | 124.7543 | 3.3646 | 124.6399 | 4.628 | -0.13275 | 124.7543 | 3.3646 | 4.628 | 4.6463 | 124.6399 | -124.704 | -124.6536
881.375 | 124.7635 | -3.8132 | 120.8313 | 0.15579 | 0.049332 | 0.040727 | 0.045811 | 0.069002 | 0.067035 | 0.195 | -0.70038 | 120.8954 | -4.0375 | -3.6896 | 0.30212 | 3.154 | 2.6093 | 3.7216 | 120.7489 | -4.0009 | -0.2243 | 0.064087 | 3.1128 | 0.1236 | -120.5292 | -0.18768 | -0.082398 | 3.3371 | 6.4224 | 7.5348 | 4.1153 | 124.7086 | 3.1128 | 124.5621 | 6.9672 | -0.18768 | 124.7086 | 3.1128 | 6.9672 | 4.1153 | 124.5621 | -124.8688 | -124.8322
882.375 | 124.6445 | -4.2572 | 120.4651 | 0.10239 | 0.050186 | 0.043504 | 0.045811 | 0.071139 | 0.066608 | 0.19521 | -0.94299 | 120.4834 | -4.4724 | -4.1245 | 0.20599 | 3.1586 | 2.7832 | 3.6255 | 120.4147 | -4.422 | -0.21515 | 0.01831 | 3.3142 | 0.13275 | -120.2591 | -0.16479 | -0.050354 | 3.5294 | 7.0404 | 7.8827 | 4.4632 | 124.7406 | 3.3142 | 124.6719 | 7.4158 | -0.16479 | 124.7406 | 3.3142 | 7.4158 | 4.4632 | 124.6719 | -124.9374 | -124.8871
883.375 | 124.6765 | -4.4861 | 120.3278 | 0.81955 | 0.04805 | 0.045 | 0.046666 | 0.06943 | 0.064471 | 0.19051 | -0.97046 | 120.4147 | -4.5364 | -4.5364 | 0.18768 | 3.1769 | 2.7191 | 3.6255 | 120.1721 | -4.7058 | -0.050354 | 0.086975 | 3.5156 | -0.050354 | -120.1401 | -0.21973 | -0.15564 | 3.566 | 7.2052 | 8.1116 | 4.6738 | 124.9008 | 3.5156 | 124.6582 | 7.663 | -0.21973 | 124.9008 | 3.5156 | 7.663 | 4.6738 | 124.6582 | -124.8642 | -125.0336
884.375 | 124.649 | -3.8818 | 120.845 | 0.11002 | 0.048264 | 0.043718 | 0.048588 | 0.070925 | 0.062976 | 0.19329 | -0.70038 | 120.9045 | -4.0695 | -3.7949 | 0.16937 | 3.2639 | 2.7786 | 3.7262 | 120.8176 | -4.0283 | -0.18768 | 0.059509 | 3.1815 | 0.086975 | -120.6757 | -0.14648 | -0.027466 | 3.3691 | 6.6605 | 7.608 | 4.0512 | 124.7864 | 3.1815 | 124.6994 | 7.1457 | -0.14648 | 124.7864 | 3.1815 | 7.1457 | 4.0512 | 124.6994 | -124.9146 | -124.8734
885.375 | 124.6353 | -4.8203 | 119.8517 | 0.40756 | 0.04805 | 0.05269 | 0.048802 | 0.071352 | 0.062335 | 0.18773 | -1.2405 | 119.8837 | -5.0995 | -4.7928 | 0.14648 | 3.1677 | 2.774 | 3.6346 | 119.8425 | -5.0171 | -0.27924 | 0.032043 | 3.5797 | 0.027465 | -119.7052 | -0.19684 | -0.009156 | 3.8589 | 7.5943 | 8.4549 | 4.9667 | 124.704 | 3.5797 | 124.6628 | 7.988 | -0.19684 | 124.704 | 3.5797 | 7.988 | 4.9667 | 124.6628 | -124.9512 | -124.8688
886.375 | 124.6582 | -4.335 | 120.3964 | 0.0032044 | 0.048478 | 0.047777 | 0.04688 | 0.074557 | 0.066394 | 0.19201 | -0.95215 | 120.4102 | -4.5731 | -4.0329 | 0.21973 | 3.0991 | 2.8748 | 3.6804 | 120.3094 | -4.5136 | -0.23804 | 0.013733 | 3.3829 | 0.30212 | -120.1767 | -0.17853 | -0.086975 | 3.6209 | 7.2098 | 8.0154 | 4.5547 | 124.7452 | 3.3829 | 124.6445 | 7.4341 | -0.17853 | 124.7452 | 3.3829 | 7.4341 | 4.5547 | 124.6445 | -124.9695 | -124.91
887.375 | 124.6719 | -4.0787 | 120.6162 | 0.24734 | 0.051255 | 0.05034 | 0.047093 | 0.06943 | 0.06554 | 0.19072 | -0.8194 | 120.6757 | -4.303 | -3.9871 | 0.16022 | 3.2547 | 2.829 | 3.7216 | 120.6116 | -4.2343 | -0.2243 | 0.059509 | 3.2593 | 0.091552 | -120.4559 | -0.15564 | -0.004578 | 3.4836 | 6.9077 | 7.8003 | 4.2389 | 124.7543 | 3.2593 | 124.6902 | 7.3334 | -0.15564 | 124.7543 | 3.2593 | 7.3334 | 4.2389 | 124.6902 | -124.9191 | -124.8505
888.3906 | 124.7406 | -4.9576 | 119.8746 | -0.0044251 | 0.046555 | 0.038805 | 0.03983 | 0.068575 | 0.062549 | 0.19094 | -1.1765 | 119.7876 | -5.0903 | -4.9072 | 0.2243 | 3.2547 | 2.7603 | 3.7537 | 119.5908 | -5.191 | -0.13275 | -0.086975 | 3.7811 | 0.050354 | -119.6503 | -0.23346 | -0.28381 | 3.9139 | 7.7179 | 8.7112 | 5.1819 | 124.7452 | 3.7811 | 124.5483 | 8.2123 | -0.23346 | 124.7452 | 3.7811 | 8.2123 | 5.1819 | 124.5483 | -124.9649 | -125.0656
889.375 | 124.6353 | -4.6967 | 120.0073 | 0.010834 | 0.0504 | 0.050127 | 0.051366 | 0.070498 | 0.063831 | 0.18752 | -1.0117 | 120.108 | -4.8569 | -4.541 | 0.14191 | 2.4948 | 2.8473 | 3.7674 | 119.9341 | -4.866 | -0.16022 | 0.10071 | 3.685 | 0.15564 | -119.8654 | -0.16937 | -0.073242 | 3.8452 | 7.5439 | 8.4641 | 4.8386 | 124.8047 | 3.685 | 124.6307 | 7.1915 | -0.16937 | 124.8047 | 3.685 | 7.1915 | 4.8386 | 124.6307 | -124.8642 | -124.8734
890.375 | 124.6719 | -4.4495 | 120.2499 | -0.057831 | 0.048264 | 0.05269 | 0.050725 | 0.070284 | 0.06554 | 0.18859 | -0.20142 | 120.2682 | -4.66 | -4.2847 | 0.1831 | 3.241 | 2.861 | 3.8315 | 120.2271 | -4.6097 | -0.21057 | 0.018311 | 4.248 | 0.16479 | -120.0668 | -0.16022 | -0.022888 | 4.4586 | 7.3105 | 8.2809 | 4.6326 | 124.7177 | 4.248 | 124.6765 | 7.6904 | -0.16022 | 124.7177 | 4.248 | 7.6904 | 4.6326 | 124.6765 | -124.91 | -124.8596
891.375 | 124.6307 | -3.8452 | 120.8679 | 0.094757 | 0.049973 | 0.049699 | 0.050297 | 0.068789 | 0.065112 | 0.1888 | -0.11902 | 120.8176 | -4.1473 | -3.9413 | -0.032043 | 3.2043 | 2.9846 | 3.7903 | 120.7947 | -4.0558 | -0.30212 | -0.050354 | 3.7262 | -0.09613 | -120.9 | -0.21057 | -0.073242 | 4.0283 | 6.8298 | 7.6355 | 3.8132 | 124.6628 | 3.7262 | 124.6399 | 7.0496 | -0.21057 | 124.6628 | 3.7262 | 7.0496 | 3.8132 | 124.6399 | -125.0153 | -124.9237
892.375 | 124.6399 | -4.1153 | 120.5429 | -0.027313 | 0.051468 | 0.045427 | 0.046666 | 0.068575 | 0.063617 | 0.19329 | -0.091553 | 120.6024 | -4.3442 | -4.0283 | 0.19226 | 3.2776 | 2.504 | 3.8864 | 120.5475 | -4.2984 | -0.22888 | 0.059509 | 4.0237 | 0.086975 | -120.3506 | -0.18311 | 0.004577 | 4.2526 | 6.6193 | 8.0017 | 4.3076 | 124.7177 | 4.0237 | 124.6628 | 7.3929 | -0.18311 | 124.7177 | 4.0237 | 7.3929 | 4.3076 | 124.6628 | -124.8871 | -124.8413
893.3906 | 124.7452 | -3.6163 | 121.0327 | -0.10361 | 0.048264 | 0.040727 | 0.039616 | 0.06943 | 0.062976 | 0.19799 | -0.036621 | 120.9686 | -3.8315 | -3.447 | 0.31128 | 3.4698 | 1.5427 | 4.0604 | 120.9641 | -3.7949 | -0.21515 | -0.064087 | 3.5797 | 0.16937 | -120.7214 | -0.17853 | -0.068665 | 3.7949 | 5.159 | 7.6767 | 3.9276 | 124.585 | 3.5797 | 124.5804 | 7.0862 | -0.17853 | 124.585 | 3.5797 | 7.0862 | 3.9276 | 124.5804 | -124.8642 | -124.8276
894.375 | 124.6536 | -3.6758 | 120.9824 | -0.042572 | 0.051468 | 0.04799 | 0.051152 | 0.071352 | 0.065112 | 0.19863 | -0.013733 | 121.138 | -3.7903 | -3.4882 | 0.46692 | 3.3554 | 1.3367 | 3.9551 | 120.9961 | -3.8132 | -0.11444 | 0.15564 | 3.6621 | 0.18768 | -120.5154 | -0.13733 | 0.013733 | 3.7765 | 5.0125 | 7.6309 | 4.1428 | 124.8138 | 3.6621 | 124.6719 | 7.0312 | -0.13733 | 124.8138 | 3.6621 | 7.0312 | 4.1428 | 124.6719 | -124.7726 | -124.7955
895.375 | 124.6628 | -3.5477 | 121.1197 | -0.06546 | 0.053391 | 0.045427 | 0.048161 | 0.068789 | 0.064685 | 0.19671 | 0 | 121.1838 | -3.7491 | -3.4058 | 0.34332 | 3.5065 | 1.149 | 4.0283 | 121.138 | -3.7308 | -0.20142 | 0.064087 | 3.5477 | 0.14191 | -120.7764 | -0.18311 | 0.01831 | 3.7491 | 4.6967 | 7.576 | 3.891 | 124.7314 | 3.5477 | 124.6857 | 7.0541 | -0.18311 | 124.7314 | 3.5477 | 7.0541 | 3.891 | 124.6857 | -124.8688 | -124.8505
896.375 | 124.5438 | -3.0396 | 121.701 | -0.21042 | 0.052323 | 0.042436 | 0.049229 | 0.069002 | 0.067676 | 0.19713 | 0.054932 | 121.6644 | -3.2776 | -2.9297 | 0.48523 | 3.5843 | 0.90637 | 4.0649 | 121.582 | -3.3142 | -0.23804 | -0.036621 | 3.0945 | 0.10986 | -121.2158 | -0.27466 | -0.11902 | 3.3325 | 3.9459 | 7.1045 | 3.5248 | 124.704 | 3.0945 | 124.6216 | 6.6238 | -0.27466 | 124.704 | 3.0945 | 6.6238 | 3.5248 | 124.6216 | -124.9786 | -125.0153
897.375 | 124.704 | -3.6484 | 121.0007 | -0.20279 | 0.053391 | 0.051836 | 0.048802 | 0.071993 | 0.064258 | 0.19457 | -0.018311 | 121.0739 | -3.8681 | -3.4882 | 0.59052 | 3.5522 | 0.75989 | 3.9688 | 120.9915 | -3.8361 | -0.21973 | 0.073243 | 3.6301 | 0.16022 | -120.4102 | -0.18768 | -0.009155 | 3.8498 | 4.4083 | 7.6172 | 4.2389 | 124.7223 | 3.6301 | 124.6399 | 7.2006 | -0.18768 | 124.7223 | 3.6301 | 7.2006 | 4.2389 | 124.6399 | -124.8688 | -124.8367
898.3906 | 124.6719 | -3.3508 | 121.3669 | -0.18753 | 0.052964 | 0.044786 | 0.047093 | 0.071779 | 0.064258 | 0.20183 | -0.004578 | 121.4172 | -3.5477 | -3.1952 | 0.5722 | 3.5294 | 0.83313 | 4.0421 | 121.3531 | -3.5156 | -0.19684 | 0.050354 | 3.3463 | 0.15564 | -120.7947 | -0.16479 | -0.013733 | 3.5431 | 4.184 | 7.3929 | 3.923 | 124.7681 | 3.3463 | 124.704 | 6.8802 | -0.16479 | 124.7681 | 3.3463 | 6.8802 | 3.923 | 124.704 | -124.9146 | -124.8825
899.375 | 124.6536 | -3.5019 | 121.1792 | -0.027313 | 0.051895 | 0.046709 | 0.050297 | 0.071139 | 0.063831 | 0.20141 | 0 | 121.2662 | -3.6987 | -3.3371 | 0.69122 | 3.4744 | 0.69122 | 4.0009 | 121.1884 | -3.6942 | -0.19684 | 0.086975 | 3.5019 | 0.16479 | -120.488 | -0.19226 | 0.009155 | 3.6987 | 4.1931 | 7.5027 | 4.1931 | 124.7681 | 3.5019 | 124.6902 | 6.9763 | -0.19226 | 124.7681 | 3.5019 | 6.9763 | 4.1931 | 124.6902 | -124.8779 | -124.8734
900.375 | 124.6078 | -3.1723 | 121.4996 | 0.087128 | 0.054459 | 0.041582 | 0.048161 | 0.072848 | 0.062762 | 0.20611 | -0.050354 | 121.5317 | -3.3875 | -3.0899 | 0.63171 | 3.2318 | 1.0391 | 3.9597 | 121.5088 | -3.3554 | -0.21515 | 0.032043 | 3.1219 | 0.082397 | -120.8679 | -0.18311 | 0.009155 | 3.3371 | 4.2114 | 7.132 | 3.804 | 124.704 | 3.1219 | 124.6811 | 6.4041 | -0.18311 | 124.704 | 3.1219 | 6.4041 | 3.804 | 124.6811 | -124.8871 | -124.855
901.375 | 124.6307 | -2.9663 | 121.756 | -0.019684 | 0.053818 | 0.039232 | 0.050084 | 0.071139 | 0.065112 | 0.20867 | 0.059509 | 121.8338 | -3.1128 | -2.8244 | 0.63629 | 2.8564 | 0.64545 | 3.9642 | 121.756 | -3.1036 | -0.14648 | 0.07782 | 3.0258 | 0.14191 | -121.1197 | -0.13733 | 0 | 3.1723 | 3.6118 | 6.9305 | 3.6026 | 124.8001 | 3.0258 | 124.7223 | 5.8228 | -0.13733 | 124.8001 | 3.0258 | 5.8228 | 3.6026 | 124.7223 | -124.8688 | -124.8596
902.375 | 124.6674 | -3.1723 | 121.4951 | -0.034943 | 0.053818 | 0.042009 | 0.049443 | 0.073488 | 0.065753 | 0.20461 | 0.082397 | 121.5775 | -3.3646 | -3.0029 | 0.45776 | 2.6505 | 0.54932 | 3.9963 | 121.5042 | -3.3371 | -0.19226 | 0.082398 | 3.2547 | 0.16937 | -121.0373 | -0.16479 | 0.009155 | 3.447 | 3.7216 | 7.1686 | 3.6301 | 124.7498 | 3.2547 | 124.6765 | 5.8228 | -0.16479 | 124.7498 | 3.2547 | 5.8228 | 3.6301 | 124.6765 | -124.8596 | -124.8322
903.3906 | 124.6811 | -3.035 | 121.669 | -0.22568 | 0.051895 | 0.042436 | 0.047948 | 0.071993 | 0.06618 | 0.20739 | 0.013733 | 121.7148 | -3.2364 | -2.9068 | 0.45776 | 2.3438 | 1.0025 | 4.0604 | 121.6644 | -3.2227 | -0.20142 | 0.045777 | 3.0487 | 0.12817 | -121.2112 | -0.18768 | -0.004577 | 3.2501 | 4.0375 | 7.0953 | 3.4927 | 124.7498 | 3.0487 | 124.6994 | 5.3787 | -0.18768 | 124.7498 | 3.0487 | 5.3787 | 3.4927 | 124.6994 | -124.9054 | -124.8917
904.375 | 124.6445 | -3.1631 | 121.4951 | -0.042572 | 0.055527 | 0.043077 | 0.050297 | 0.071566 | 0.064044 | 0.20141 | 0.07782 | 121.5683 | -3.3646 | -3.0121 | 0.48065 | 2.9068 | 1.0941 | 4.0924 | 121.5134 | -3.3463 | -0.20142 | 0.073242 | 3.241 | 0.15106 | -121.0144 | -0.1831 | 0.018311 | 3.4424 | 4.2572 | 7.2556 | 3.6438 | 124.7314 | 3.241 | 124.6765 | 6.0699 | -0.1831 | 124.7314 | 3.241 | 6.0699 | 3.6438 | 124.6765 | -124.8596 | -124.8413
905.375 | 124.6078 | -3.0624 | 121.6644 | -0.19516 | 0.053818 | 0.039018 | 0.047948 | 0.069857 | 0.065753 | 0.20632 | 0.018311 | 121.6644 | -3.2913 | -2.9388 | 0.44861 | 2.7557 | 0.5722 | 4.0787 | 121.6461 | -3.241 | -0.22888 | 0 | 3.0808 | 0.1236 | -121.2158 | -0.17853 | -0.018311 | 3.3096 | 3.6346 | 7.1411 | 3.511 | 124.7269 | 3.0808 | 124.7086 | 5.8182 | -0.17853 | 124.7269 | 3.0808 | 5.8182 | 3.511 | 124.7086 | -124.9557 | -124.9054
906.375 | 124.6536 | -3.2364 | 121.3852 | -0.11887 | 0.053818 | 0.044572 | 0.052434 | 0.071352 | 0.063617 | 0.20546 | 0.045776 | 121.4081 | -3.511 | -2.9755 | 0.59052 | 2.6733 | 0.63629 | 4.0604 | 121.3898 | -3.3554 | -0.27466 | 0.022888 | 3.2822 | 0.26092 | -120.7947 | -0.11902 | 0.004578 | 3.5568 | 3.8727 | 7.2968 | 3.8269 | 124.6445 | 3.2822 | 124.6262 | 5.9097 | -0.11902 | 124.6445 | 3.2822 | 5.9097 | 3.8269 | 124.6262 | -124.8962 | -124.7406
907.375 | 124.6811 | -3.2913 | 121.4035 | -0.21042 | 0.056382 | 0.043932 | 0.050297 | 0.069643 | 0.064471 | 0.20269 | 0 | 121.4447 | -3.479 | -3.1815 | 0.5722 | 3.6713 | 0.5127 | 4.097 | 121.3943 | -3.4698 | -0.18768 | 0.041199 | 3.2913 | 0.10986 | -120.8313 | -0.17853 | -0.009155 | 3.479 | 3.804 | 7.3883 | 3.8635 | 124.736 | 3.2913 | 124.6857 | 6.9626 | -0.17853 | 124.736 | 3.2913 | 6.9626 | 3.8635 | 124.6857 | -124.8825 | -124.8734
908.3906 | 124.6582 | -3.186 | 121.5088 | -0.21805 | 0.054245 | 0.036455 | 0.050297 | 0.072207 | 0.06554 | 0.20611 | 0.045776 | 121.5546 | -3.4058 | -3.0029 | 0.56763 | 3.7582 | 0.25177 | 4.1245 | 121.4676 | -3.3875 | -0.21973 | 0.045776 | 3.2318 | 0.1831 | -120.9412 | -0.20142 | -0.041199 | 3.4515 | 3.4378 | 7.3105 | 3.7537 | 124.7406 | 3.2318 | 124.6536 | 6.9443 | -0.20142 | 124.7406 | 3.2318 | 6.9443 | 3.7537 | 124.6536 | -124.9146 | -124.8962
909.375 | 124.6948 | -3.2639 | 121.4127 | -0.17227 | 0.056382 | 0.042223 | 0.05222 | 0.071993 | 0.064044 | 0.2029 | 0.054932 | 121.4584 | -3.4653 | -3.1082 | 0.69122 | 3.7079 | 0.25635 | 4.1107 | 121.4127 | -3.4241 | -0.20142 | 0.045776 | 3.3188 | 0.15564 | -120.7214 | -0.16022 | 0 | 3.5202 | 3.5202 | 7.3746 | 3.9551 | 124.7223 | 3.3188 | 124.6765 | 6.9717 | -0.16022 | 124.7223 | 3.3188 | 6.9717 | 3.9551 | 124.6765 | -124.8779 | -124.8367
910.375 | 124.6033 | -3.3005 | 121.344 | -0.24094 | 0.053177 | 0.041154 | 0.047948 | 0.069002 | 0.066608 | 0.20397 | -0.018311 | 121.3531 | -3.5431 | -3.0121 | 0.63171 | 3.5019 | 0.15106 | 4.0878 | 121.376 | -3.4744 | -0.24261 | 0.009155 | 3.2822 | 0.28839 | -120.7123 | -0.17395 | 0.032044 | 3.5248 | 3.4515 | 7.3883 | 3.9322 | 124.6536 | 3.2822 | 124.6765 | 6.8024 | -0.17395 | 124.6536 | 3.2822 | 6.8024 | 3.9322 | 124.6765 | -124.8871 | -124.8184
911.375 | 124.7177 | -3.4515 | 121.2112 | -0.21805 | 0.053177 | 0.044572 | 0.045598 | 0.070284 | 0.064258 | 0.20141 | 0.045776 | 121.1563 | -3.6255 | -3.2867 | 0.66376 | 3.1723 | 0.13733 | 4.0924 | 121.17 | -3.6255 | -0.17395 | -0.054932 | 3.4973 | 0.1648 | -120.5475 | -0.17395 | -0.041199 | 3.6713 | 3.5889 | 7.5439 | 4.1153 | 124.6078 | 3.4973 | 124.6216 | 6.6238 | -0.17395 | 124.6078 | 3.4973 | 6.6238 | 4.1153 | 124.6216 | -124.8367 | -124.8367
912.375 | 124.6857 | -3.4744 | 121.1792 | -0.2562 | 0.054032 | 0.052049 | 0.054784 | 0.069857 | 0.06554 | 0.20397 | 0.032043 | 121.2341 | -3.7033 | -3.3188 | 1.0437 | 2.3117 | 0.28839 | 0.48981 | 121.1655 | -3.6438 | -0.22888 | 0.054932 | 3.5065 | 0.15564 | -120.1355 | -0.16937 | -0.013733 | 3.7354 | 3.7628 | 3.9642 | 4.5181 | 124.7086 | 3.5065 | 124.6399 | 5.7861 | -0.16937 | 124.7086 | 3.5065 | 5.7861 | 4.5181 | 124.6399 | -124.8825 | -124.823
913.3906 | 124.7314 | -3.4744 | 121.138 | -0.088349 | 0.054245 | 0.044145 | 0.047093 | 0.06708 | 0.067035 | 0.20354 | 0.032043 | 121.0922 | -3.685 | -3.3279 | 1.5289 | 2.504 | 0.21515 | 0.55847 | 121.1334 | -3.6484 | -0.21057 | -0.045776 | 3.5065 | 0.14648 | -119.6091 | -0.17395 | -0.004577 | 3.717 | 3.6896 | 4.0329 | 5.0034 | 124.5666 | 3.5065 | 124.6078 | 5.9784 | -0.17395 | 124.5666 | 3.5065 | 5.9784 | 5.0034 | 124.6078 | -124.823 | -124.7864
914.375 | 124.5941 | -3.5156 | 121.1655 | -0.2562 | 0.054886 | 0.043718 | 0.048802 | 0.06943 | 0.064044 | 0.20504 | 0.054932 | 121.2067 | -3.7125 | -3.3691 | 2.2751 | 2.5955 | 0.53558 | 0.54474 | 121.1609 | -3.6758 | -0.19684 | 0.041199 | 3.5706 | 0.14648 | -118.8904 | -0.16022 | -0.004577 | 3.7674 | 4.0512 | 4.0604 | 5.7907 | 124.7223 | 3.5706 | 124.6765 | 6.1111 | -0.16022 | 124.7223 | 3.5706 | 6.1111 | 5.7907 | 124.6765 | -124.8779 | -124.8413
915.375 | 124.6857 | -3.5019 | 121.1105 | -0.27145 | 0.052323 | 0.044145 | 0.049443 | 0.065798 | 0.063403 | 0.20632 | 0.14648 | 121.1014 | -3.7262 | -3.3188 | 2.3712 | 1.7624 | 0.2655 | 0.54932 | 121.1014 | -3.6896 | -0.2243 | -0.009156 | 3.6484 | 0.1831 | -118.7393 | -0.18768 | -0.009156 | 3.8727 | 3.7674 | 4.0512 | 5.8731 | 124.6033 | 3.6484 | 124.6033 | 5.2643 | -0.18768 | 124.6033 | 3.6484 | 5.2643 | 5.8731 | 124.6033 | -124.8367 | -124.8001
916.375 | 124.6262 | -3.7903 | 120.8725 | -0.050202 | 0.060868 | 0.045427 | 0.057133 | 0.069216 | 0.063403 | 0.20141 | -0.036621 | 120.9045 | -3.9963 | -3.6346 | 2.2842 | 1.3367 | 0.27008 | 0.42572 | 120.8542 | -3.9734 | -0.20599 | 0.032043 | 3.7537 | 0.15564 | -118.5883 | -0.18311 | -0.018311 | 3.9597 | 4.0604 | 4.216 | 6.0745 | 124.6948 | 3.7537 | 124.6445 | 5.127 | -0.18311 | 124.6948 | 3.7537 | 5.127 | 6.0745 | 124.6445 | -124.8688 | -124.8459
917.375 | 124.5209 | -3.6621 | 121.0098 | -0.22568 | 0.056168 | 0.042863 | 0.052647 | 0.066866 | 0.063403 | 0.20589 | -0.032043 | 120.9686 | -3.9093 | -3.598 | 2.6321 | 1.1124 | 0.35248 | 0.54016 | 121.0419 | -3.8498 | -0.24719 | -0.041199 | 3.6301 | 0.064087 | -118.3777 | -0.18768 | 0.032043 | 3.8773 | 4.0146 | 4.2023 | 6.2942 | 124.6307 | 3.6301 | 124.704 | 4.7745 | -0.18768 | 124.6307 | 3.6301 | 4.7745 | 6.2942 | 124.704 | -124.9191 | -124.8596
918.3906 | 124.6399 | -3.7125 | 120.9641 | -0.21042 | 0.058518 | 0.039659 | 0.056706 | 0.071139 | 0.063617 | 0.21123 | 0.064087 | 121.0144 | -3.9185 | -3.5477 | 3.0304 | 1.0803 | 0.36621 | 0.54932 | 120.9137 | -3.891 | -0.20599 | 0.050354 | 3.7766 | 0.1648 | -117.9337 | -0.17853 | -0.050354 | 3.9825 | 4.0787 | 4.2618 | 6.7429 | 124.7269 | 3.7766 | 124.6262 | 4.7928 | -0.17853 | 124.7269 | 3.7766 | 4.7928 | 6.7429 | 124.6262 | -124.8825 | -124.855
919.375 | 124.6445 | -3.8361 | 120.7306 | -0.012055 | 0.053177 | 0.034319 | 0.048802 | 0.066866 | 0.063617 | 0.21337 | -0.073242 | 120.726 | -4.0375 | -3.6484 | 4.2252 | 1.062 | 0.25177 | 0.68665 | 120.7352 | -4.01 | -0.20142 | -0.004578 | 3.7628 | 0.18768 | -116.5054 | -0.17395 | 0.004577 | 3.9642 | 4.0878 | 4.5227 | 8.0612 | 124.5621 | 3.7628 | 124.5712 | 4.8981 | -0.17395 | 124.5621 | 3.7628 | 4.8981 | 8.0612 | 124.5712 | -124.7681 | -124.7406
920.375 | 124.5987 | -3.6896 | 120.9915 | -0.27145 | 0.054032 | 0.036882 | 0.053715 | 0.066866 | 0.062976 | 0.21486 | 0.032043 | 120.9869 | -3.8818 | -3.5385 | 3.8727 | 0.76904 | 0.53558 | 0.63629 | 120.9641 | -3.8589 | -0.19226 | -0.004578 | 3.7216 | 0.15106 | -117.1188 | -0.16937 | -0.027466 | 3.9139 | 4.2252 | 4.3259 | 7.5623 | 124.6765 | 3.7216 | 124.6536 | 4.4586 | -0.16937 | 124.6765 | 3.7216 | 4.4586 | 7.5623 | 124.6536 | -124.8734 | -124.8505
921.375 | 124.7086 | -3.6118 | 120.9869 | -0.14938 | 0.054245 | 0.036455 | 0.050725 | 0.06708 | 0.061267 | 0.21721 | 0.07782 | 120.8954 | -3.8589 | -3.4653 | 3.9825 | 0.92926 | 0.35706 | 0.70496 | 120.932 | -3.7994 | -0.24719 | -0.091552 | 3.6896 | 0.14648 | -117.0044 | -0.18768 | -0.054931 | 3.9368 | 3.9688 | 4.3167 | 7.5943 | 124.5071 | 3.6896 | 124.5438 | 4.541 | -0.18768 | 124.5071 | 3.6896 | 4.541 | 7.5943 | 124.5438 | -124.8459 | -124.7864
922.375 | 124.8047 | -3.3966 | 121.2204 | -0.10361 | 0.056382 | 0.039446 | 0.052434 | 0.066012 | 0.065326 | 0.21273 | 0.19226 | 121.1655 | -3.6072 | -3.186 | 3.9322 | 0.91553 | 0.40283 | 0.81482 | 121.1792 | -3.5751 | -0.21057 | -0.054932 | 3.5889 | 0.21057 | -117.2882 | -0.17853 | -0.041199 | 3.7994 | 3.7994 | 4.2114 | 7.3288 | 124.5621 | 3.5889 | 124.5758 | 4.3121 | -0.17853 | 124.5621 | 3.5889 | 4.3121 | 7.3288 | 124.5758 | -124.8276 | -124.7955
923.3906 | 124.6216 | -3.5339 | 121.1609 | -0.19516 | 0.058518 | 0.035814 | 0.060765 | 0.066012 | 0.062122 | 0.2185 | 0.24719 | 121.1746 | -3.7262 | -3.36 | 3.7125 | 0.72784 | 1.3046 | 1.4145 | 121.0876 | -3.7262 | -0.19226 | 0.013733 | 3.7811 | 0.17395 | -117.4484 | -0.19226 | -0.073243 | 3.9734 | 4.8386 | 4.9484 | 7.2464 | 124.7086 | 3.7811 | 124.6216 | 4.2618 | -0.19226 | 124.7086 | 3.7811 | 4.2618 | 7.2464 | 124.6216 | -124.8871 | -124.8871
924.375 | 124.6857 | -3.1815 | 121.4355 | -0.23331 | 0.056382 | 0.039446 | 0.055211 | 0.066439 | 0.063617 | 0.21251 | 0.48065 | 121.344 | -3.447 | -3.0029 | 3.7582 | 0.88348 | 3.9185 | 4.1153 | 121.3943 | -3.3783 | -0.2655 | -0.091553 | 3.6621 | 0.17853 | -117.6773 | -0.19684 | -0.041199 | 3.9276 | 7.0999 | 7.2968 | 6.9397 | 124.5255 | 3.6621 | 124.5758 | 4.0649 | -0.19684 | 124.5255 | 3.6621 | 4.0649 | 6.9397 | 124.5758 | -124.8825 | -124.8138
925.375 | 124.8779 | -3.3142 | 121.2891 | -0.11124 | 0.056382 | 0.030901 | 0.055424 | 0.065798 | 0.061908 | 0.21807 | 0.43945 | 121.2204 | -3.5431 | -3.0762 | 3.6987 | 0.87891 | 1.5839 | 1.9821 | 121.2845 | -3.4561 | -0.22888 | -0.068664 | 3.7537 | 0.23804 | -117.5903 | -0.14191 | -0.004577 | 3.9825 | 4.8981 | 5.2963 | 7.0129 | 124.5346 | 3.7537 | 124.5987 | 4.1931 | -0.14191 | 124.5346 | 3.7537 | 4.1931 | 7.0129 | 124.5987 | -124.8322 | -124.7452
926.375 | 124.7589 | -3.3188 | 121.2524 | -0.11887 | 0.054245 | 0.033678 | 0.054997 | 0.068361 | 0.062335 | 0.22213 | 0.50812 | 121.2387 | -3.511 | -3.1311 | 3.6621 | 0.87891 | 0.90179 | 1.2909 | 121.2204 | -3.511 | -0.19226 | -0.013733 | 3.8269 | 0.18768 | -117.5903 | -0.19226 | -0.032043 | 4.0192 | 4.2206 | 4.6097 | 6.9809 | 124.5575 | 3.8269 | 124.5392 | 4.1977 | -0.19226 | 124.5575 | 3.8269 | 4.1977 | 6.9809 | 124.5392 | -124.7635 | -124.7635
927.375 | 124.6902 | -2.9892 | 121.6599 | -0.027313 | 0.058091 | 0.038377 | 0.05457 | 0.065157 | 0.065112 | 0.22255 | 0.61798 | 121.5454 | -3.186 | -2.8519 | 3.4424 | 0.81024 | 0.51727 | 0.76446 | 121.5546 | -3.1723 | -0.19684 | -0.11444 | 3.6072 | 0.13733 | -118.2175 | -0.18311 | -0.10529 | 3.804 | 3.5065 | 3.7537 | 6.4316 | 124.5346 | 3.6072 | 124.5438 | 3.7994 | -0.18311 | 124.5346 | 3.6072 | 3.7994 | 6.4316 | 124.5438 | -124.8459 | -124.8322
928.3906 | 124.6216 | -3.1128 | 121.5775 | 0.12527 | 0.063217 | 0.044572 | 0.063328 | 0.067293 | 0.06319 | 0.21978 | 0.56305 | 121.582 | -3.2913 | -2.9892 | 3.2501 | 0.65002 | 0.25177 | 0.34332 | 121.5088 | -3.3051 | -0.17853 | 0.004577 | 3.6758 | 0.1236 | -118.3273 | -0.19226 | -0.068665 | 3.8544 | 3.3646 | 3.4561 | 6.3629 | 124.6948 | 3.6758 | 124.6216 | 3.7628 | -0.19226 | 124.6948 | 3.6758 | 3.7628 | 6.3629 | 124.6216 | -124.8688 | -124.8825
929.375 | 124.7131 | -2.9434 | 121.6736 | -0.21805 | 0.059159 | 0.03261 | 0.056493 | 0.067293 | 0.065326 | 0.22341 | 0.70953 | 121.5958 | -3.1677 | -2.7191 | 3.0075 | 0.7782 | 0.16022 | 0.50812 | 121.6095 | -3.1082 | -0.2243 | -0.07782 | 3.653 | 0.2243 | -118.6661 | -0.16479 | -0.064087 | 3.8773 | 3.1036 | 3.4515 | 5.9509 | 124.5392 | 3.653 | 124.5529 | 3.7216 | -0.16479 | 124.5392 | 3.653 | 3.7216 | 5.9509 | 124.5529 | -124.8413 | -124.7818
930.375 | 124.704 | -3.1403 | 121.4081 | -0.15701 | 0.058518 | 0.036668 | 0.057347 | 0.064089 | 0.065753 | 0.22512 | 0.6546 | 121.4264 | -3.3279 | -2.9343 | 2.8381 | 0.75989 | 0.091553 | 0.50354 | 121.4035 | -3.3188 | -0.18768 | 0.018311 | 3.7949 | 0.20599 | -118.5699 | -0.17853 | -0.004578 | 3.9825 | 3.2318 | 3.6438 | 5.9784 | 124.5667 | 3.7949 | 124.5438 | 3.9001 | -0.17853 | 124.5667 | 3.7949 | 3.9001 | 5.9784 | 124.5438 | -124.736 | -124.7269
931.375 | 124.6811 | -3.0762 | 121.5454 | -0.3096 | 0.060654 | 0.034319 | 0.057774 | 0.067293 | 0.064685 | 0.22661 | 0.57678 | 121.4218 | -3.3188 | -2.9297 | 2.2247 | 0.66376 | 0.16479 | 0.42572 | 121.4722 | -3.2455 | -0.24261 | -0.1236 | 3.653 | 0.14649 | -119.3207 | -0.16937 | -0.073242 | 3.8956 | 3.241 | 3.5019 | 5.3009 | 124.498 | 3.653 | 124.5483 | 3.7399 | -0.16937 | 124.498 | 3.653 | 3.7399 | 5.3009 | 124.5483 | -124.8642 | -124.791
932.375 | 124.7269 | -3.1586 | 121.4264 | -0.96573 | 0.0598 | 0.039018 | 0.05927 | 0.06708 | 0.064685 | 0.22597 | 0.59967 | 121.3486 | -3.3737 | -2.9343 | 2.2202 | 0.74616 | 0.15106 | 0.50812 | 121.3669 | -3.3417 | -0.21515 | -0.07782 | 3.7582 | 0.2243 | -119.2062 | -0.18311 | -0.05951 | 3.9734 | 3.3096 | 3.6667 | 5.3787 | 124.5071 | 3.7582 | 124.5255 | 3.9047 | -0.18311 | 124.5071 | 3.7582 | 3.9047 | 5.3787 | 124.5255 | -124.8001 | -124.7681
933.4531 | 124.6857 | -3.1357 | 121.4813 | -0.27145 | 0.060868 | 0.039873 | 0.058629 | 0.066012 | 0.065753 | 0.22512 | 1.6525 | 121.4401 | -3.3325 | -2.9526 | 1.8448 | 0.6546 | 0.21057 | 0.49896 | 121.4081 | -3.3279 | -0.19684 | -0.041198 | 4.7882 | 0.1831 | -119.6365 | -0.19226 | -0.073242 | 4.985 | 3.3463 | 3.6346 | 4.9805 | 124.5758 | 4.7882 | 124.5438 | 3.7903 | -0.19226 | 124.5758 | 4.7882 | 3.7903 | 4.9805 | 124.5438 | -124.8138 | -124.8093
934.375 | 124.704 | -3.1265 | 121.5088 | -0.080719 | 0.0598 | 0.041154 | 0.059483 | 0.064516 | 0.062976 | 0.22469 | 1.593 | 121.4172 | -3.3463 | -2.9343 | 1.6937 | 0.68665 | 0.32044 | 0.66834 | 121.431 | -3.2822 | -0.21973 | -0.091553 | 4.7195 | 0.19226 | -119.8151 | -0.15564 | -0.07782 | 4.9393 | 3.447 | 3.7949 | 4.8203 | 124.5438 | 4.7195 | 124.5575 | 3.8132 | -0.15564 | 124.5438 | 4.7195 | 3.8132 | 4.8203 | 124.5575 | -124.855 | -124.791
935.375 | 124.6811 | -3.035 | 121.582 | -0.019684 | 0.061081 | 0.040941 | 0.05927 | 0.064303 | 0.068103 | 0.22255 | 1.5152 | 121.5134 | -3.2867 | -2.9114 | 1.561 | 0.62714 | 0.32501 | 0.59509 | 121.5042 | -3.2272 | -0.25177 | -0.068664 | 4.5502 | 0.1236 | -120.0211 | -0.19226 | -0.07782 | 4.8019 | 3.36 | 3.6301 | 4.5959 | 124.5483 | 4.5502 | 124.5392 | 3.6621 | -0.19226 | 124.5483 | 4.5502 | 3.6621 | 4.5959 | 124.5392 | -124.8688 | -124.8093
936.375 | 124.7086 | -3.2181 | 121.376 | -0.22568 | 0.061722 | 0.042863 | 0.062047 | 0.06473 | 0.064044 | 0.22255 | 1.6113 | 121.312 | -3.447 | -3.0258 | 1.561 | 0.64545 | 0.25635 | 0.62714 | 121.3074 | -3.4103 | -0.22888 | -0.064087 | 4.8294 | 0.19226 | -119.8151 | -0.19226 | -0.068665 | 5.0583 | 3.4744 | 3.8452 | 4.7791 | 124.53 | 4.8294 | 124.5255 | 3.8635 | -0.19226 | 124.53 | 4.8294 | 3.8635 | 4.7791 | 124.5255 | -124.823 | -124.7864
937.375 | 124.7269 | -3.2089 | 121.3989 | -0.13412 | 0.060654 | 0.043718 | 0.059483 | 0.065798 | 0.064899 | 0.2249 | 1.6754 | 121.3257 | -3.392 | -2.9663 | 1.4603 | 0.60883 | 0.16022 | 0.5722 | 121.2891 | -3.392 | -0.18311 | -0.073242 | 4.8843 | 0.24261 | -119.9387 | -0.18311 | -0.10986 | 5.0674 | 3.3691 | 3.7811 | 4.6692 | 124.5346 | 4.8843 | 124.498 | 3.8177 | -0.18311 | 124.5346 | 4.8843 | 3.8177 | 4.6692 | 124.498 | -124.791 | -124.791
938.3906 | 124.6399 | -3.1952 | 121.4584 | -0.19516 | 0.063431 | 0.042009 | 0.06931 | 0.066866 | 0.064258 | 0.22747 | 1.5839 | 121.4401 | -3.447 | -3.035 | 1.2589 | 0.48065 | 0.21515 | 0.33417 | 121.4081 | -3.3966 | -0.25177 | -0.01831 | 4.7791 | 0.16022 | -120.1996 | -0.20142 | -0.050354 | 5.0308 | 3.4103 | 3.5294 | 4.454 | 124.6353 | 4.7791 | 124.6033 | 3.6758 | -0.20142 | 124.6353 | 4.7791 | 3.6758 | 4.454 | 124.6033 | -124.9054 | -124.855
939.375 | 124.6902 | -3.0258 | 121.5866 | -0.10361 | 0.062363 | 0.041368 | 0.05927 | 0.067293 | 0.06618 | 0.23131 | 1.7075 | 121.5271 | -3.2272 | -2.8564 | 1.2634 | 0.5722 | 0.12817 | 0.42114 | 121.5317 | -3.2181 | -0.20142 | -0.059509 | 4.7333 | 0.16937 | -120.3232 | -0.19226 | -0.054932 | 4.9347 | 3.154 | 3.447 | 4.2892 | 124.5529 | 4.7333 | 124.5575 | 3.598 | -0.19226 | 124.5529 | 4.7333 | 3.598 | 4.2892 | 124.5575 | -124.8138 | -124.8047
940.375 | 124.7131 | -2.9114 | 121.6782 | -0.29434 | 0.065354 | 0.03795 | 0.061192 | 0.06473 | 0.063831 | 0.22982 | 1.8723 | 121.6461 | -3.1174 | -2.7008 | 1.2268 | 0.55847 | 0.11902 | 0.44861 | 121.6003 | -3.0853 | -0.20599 | -0.032044 | 4.7836 | 0.21057 | -120.4514 | -0.17395 | -0.07782 | 4.9896 | 3.0304 | 3.36 | 4.1382 | 124.5575 | 4.7836 | 124.5117 | 3.4698 | -0.17395 | 124.5575 | 4.7836 | 3.4698 | 4.1382 | 124.5117 | -124.7955 | -124.7635
941.375 | 124.704 | -2.8107 | 121.8063 | -0.22568 | 0.065567 | 0.039659 | 0.06226 | 0.067293 | 0.064685 | 0.22533 | 1.9547 | 121.756 | -2.9755 | -2.5452 | 1.4832 | 0.65918 | -0.17395 | 0.54016 | 121.6919 | -2.9846 | -0.1648 | -0.050354 | 4.7653 | 0.2655 | -120.3232 | -0.17395 | -0.11444 | 4.9301 | 2.6367 | 3.3508 | 4.2938 | 124.5667 | 4.7653 | 124.5026 | 3.4698 | -0.17395 | 124.5667 | 4.7653 | 3.4698 | 4.2938 | 124.5026 | -124.7818 | -124.791
942.3906 | 124.5621 | -2.7328 | 121.9254 | -0.17227 | 0.065995 | 0.041795 | 0.066319 | 0.065371 | 0.064685 | 0.2279 | 1.9089 | 121.9208 | -2.9251 | -2.6276 | 1.3138 | 0.59967 | 0.068665 | 0.27008 | 121.8704 | -2.8748 | -0.19226 | -0.004578 | 4.6417 | 0.10529 | -120.6116 | -0.14191 | -0.054932 | 4.834 | 2.8015 | 3.0029 | 4.0466 | 124.6536 | 4.6417 | 124.6033 | 3.3325 | -0.14191 | 124.6536 | 4.6417 | 3.3325 | 4.0466 | 124.6033 | -124.8505 | -124.8001
943.375 | 124.6445 | -2.8107 | 121.8475 | -0.19516 | 0.067276 | 0.045213 | 0.069524 | 0.067507 | 0.065112 | 0.22619 | 1.9226 | 121.8887 | -2.98 | -2.6367 | 3.717 | 0.41657 | 0.19684 | 0.29297 | 121.7834 | -2.9617 | -0.16937 | 0.041199 | 4.7333 | 0.17395 | -118.1305 | -0.15106 | -0.064087 | 4.9026 | 3.0075 | 3.1036 | 6.5277 | 124.6994 | 4.7333 | 124.5941 | 3.2272 | -0.15106 | 124.6994 | 4.7333 | 3.2272 | 6.5277 | 124.5941 | -124.8276 | -124.8093
944.375 | 124.7589 | -2.6825 | 121.9162 | 0.087128 | 0.066849 | 0.038805 | 0.062047 | 0.067934 | 0.06319 | 0.23067 | 1.886 | 121.8201 | -2.9251 | -2.4765 | 3.8635 | 0.58136 | 0.036621 | 0.4303 | 121.8338 | -2.8427 | -0.24262 | -0.096131 | 4.5685 | 0.20599 | -118.0527 | -0.16022 | -0.082398 | 4.8111 | 2.7191 | 3.1128 | 6.546 | 124.5026 | 4.5685 | 124.5163 | 3.2639 | -0.16022 | 124.5026 | 4.5685 | 3.2639 | 6.546 | 124.5163 | -124.8413 | -124.7589
945.375 | 124.6811 | -2.6871 | 121.8887 | -0.11124 | 0.064926 | 0.03795 | 0.060979 | 0.063875 | 0.065326 | 0.23281 | 1.973 | 121.8567 | -2.9434 | -2.5085 | 4.0878 | 0.58136 | 0.032043 | 0.39368 | 121.8109 | -2.8885 | -0.25635 | -0.032044 | 4.66 | 0.17853 | -117.8009 | -0.20142 | -0.07782 | 4.9164 | 2.7191 | 3.0807 | 6.7749 | 124.5438 | 4.66 | 124.498 | 3.2684 | -0.20142 | 124.5438 | 4.66 | 3.2684 | 6.7749 | 124.498 | -124.8322 | -124.7772
946.3906 | 124.6307 | -2.6733 | 121.9528 | -0.24094 | 0.070908 | 0.041154 | 0.069951 | 0.066652 | 0.06084 | 0.23559 | 1.9089 | 122.0169 | -2.8976 | -2.5131 | 4.3716 | 0.47607 | 0.14191 | 0.30212 | 121.907 | -2.8656 | -0.2243 | 0.064087 | 4.5822 | 0.16022 | -117.5812 | -0.19226 | -0.045777 | 4.8065 | 2.8152 | 2.9755 | 7.045 | 124.6902 | 4.5822 | 124.5804 | 3.1494 | -0.19226 | 124.6902 | 4.5822 | 3.1494 | 7.045 | 124.5804 | -124.8505 | -124.8184
947.375 | 124.6719 | -2.536 | 122.0673 | 0.3389 | 0.066635 | 0.039232 | 0.062901 | 0.066012 | 0.062335 | 0.2311 | 1.8906 | 121.9757 | -2.7512 | -2.3895 | 4.2801 | 0.50354 | 0.10986 | 0.37537 | 122.0032 | -2.6962 | -0.21515 | -0.091553 | 4.4266 | 0.14648 | -117.7872 | -0.16022 | -0.064087 | 4.6417 | 2.6459 | 2.9114 | 6.8161 | 124.5117 | 4.4266 | 124.5392 | 3.0396 | -0.16022 | 124.5117 | 4.4266 | 3.0396 | 6.8161 | 124.5392 | -124.8184 | -124.7635
948.3906 | 124.617 | -2.5818 | 122.0764 | -0.23331 | 0.068131 | 0.043077 | 0.073369 | 0.06943 | 0.06554 | 0.23644 | 1.9089 | 122.0718 | -2.8244 | -2.4078 | 4.2892 | 0.39368 | 0.17853 | 0.27924 | 122.0215 | -2.7603 | -0.24262 | -0.004578 | 4.4907 | 0.17395 | -117.7872 | -0.17853 | -0.054932 | 4.7333 | 2.7603 | 2.861 | 6.871 | 124.6536 | 4.4907 | 124.6033 | 2.9755 | -0.17853 | 124.6536 | 4.4907 | 2.9755 | 6.871 | 124.6033 | -124.9008 | -124.8367
949.375 | 124.6674 | -2.4948 | 122.0673 | -0.06546 | 0.066635 | 0.038805 | 0.062901 | 0.066652 | 0.065967 | 0.23665 | 1.9226 | 122.049 | -2.7054 | -2.3117 | 4.1931 | 0.54474 | 0.013733 | 0.37079 | 122.0261 | -2.6733 | -0.21057 | -0.018311 | 4.4174 | 0.1831 | -117.8741 | -0.17853 | -0.041199 | 4.628 | 2.5085 | 2.8656 | 6.6879 | 124.5438 | 4.4174 | 124.5209 | 3.0396 | -0.17853 | 124.5438 | 4.4174 | 3.0396 | 6.6879 | 124.5209 | -124.7726 | -124.7406
950.375 | 124.5895 | -2.5543 | 122.0993 | -0.2562 | 0.071335 | 0.037737 | 0.069096 | 0.06708 | 0.063403 | 0.23644 | 1.8723 | 122.1039 | -2.7695 | -2.4078 | 3.772 | 0.45319 | 0.19226 | 0.24261 | 122.0444 | -2.7145 | -0.21515 | 0.004578 | 4.4266 | 0.14648 | -118.3273 | -0.16022 | -0.054931 | 4.6417 | 2.7466 | 2.7969 | 6.3263 | 124.6582 | 4.4266 | 124.5987 | 3.0075 | -0.16022 | 124.6582 | 4.4266 | 3.0075 | 6.3263 | 124.5987 | -124.8688 | -124.8138
951.375 | 124.5712 | -2.5269 | 122.1313 | -0.64529 | 0.06984 | 0.039446 | 0.067174 | 0.067721 | 0.062122 | 0.23516 | 1.8494 | 122.1405 | -2.7054 | -2.3758 | 3.923 | 3.9871 | 0.19684 | 0.24719 | 122.0764 | -2.7054 | -0.17853 | 0.009155 | 4.3762 | 0.15106 | -118.2083 | -0.17853 | -0.054932 | 4.5547 | 2.7237 | 2.774 | 6.4499 | 124.6674 | 4.3762 | 124.6033 | 6.514 | -0.17853 | 124.6674 | 4.3762 | 6.514 | 6.4499 | 124.6033 | -124.8367 | -124.8367
952.375 | 124.6353 | -2.417 | 122.2046 | -0.095978 | 0.071762 | 0.04799 | 0.063756 | 0.066866 | 0.061694 | 0.23153 | 2.0416 | 122.1497 | -2.6184 | -2.2568 | 3.8132 | 4.4495 | 0.027466 | 0.34332 | 122.1176 | -2.5864 | -0.20142 | -0.054932 | 4.4586 | 0.16022 | -118.3914 | -0.16937 | -0.086975 | 4.66 | 2.4445 | 2.7603 | 6.2302 | 124.5666 | 4.4586 | 124.5346 | 6.8665 | -0.16937 | 124.5666 | 4.4586 | 6.8665 | 6.2302 | 124.5346 | -124.823 | -124.791
953.3906 | 124.6811 | -2.449 | 122.1451 | -0.27908 | 0.069626 | 0.045641 | 0.067174 | 0.064944 | 0.061267 | 0.23836 | 2.124 | 122.1085 | -2.6459 | -2.2202 | 3.7537 | 4.4403 | 0.022888 | 0.38452 | 122.0673 | -2.6093 | -0.19684 | -0.036622 | 4.5731 | 0.22888 | -118.3914 | -0.16022 | -0.07782 | 4.7699 | 2.4719 | 2.8336 | 6.2027 | 124.5575 | 4.5731 | 124.5163 | 6.8893 | -0.16022 | 124.5575 | 4.5731 | 6.8893 | 6.2027 | 124.5163 | -124.791 | -124.7543
954.375 | 124.6582 | -2.417 | 122.1725 | 0.14816 | 0.071549 | 0.039873 | 0.068242 | 0.064944 | 0.063617 | 0.24029 | 2.1378 | 122.168 | -2.5955 | -2.2339 | 3.7216 | 2.7512 | 0.022888 | 0.31586 | 122.1176 | -2.5726 | -0.17853 | -0.004577 | 4.5547 | 0.1831 | -118.4509 | -0.15564 | -0.054931 | 4.7333 | 2.4399 | 2.7328 | 6.1386 | 124.585 | 4.5547 | 124.5346 | 5.1682 | -0.15564 | 124.585 | 4.5547 | 5.1682 | 6.1386 | 124.5346 | -124.7681 | -124.7452
955.375 | 124.6262 | -2.4307 | 122.1313 | 0.094757 | 0.075394 | 0.03795 | 0.065892 | 0.067721 | 0.064899 | 0.24264 | 2.1744 | 122.1039 | -2.6459 | -2.2705 | 3.7857 | 2.5314 | 0.018311 | 0.34332 | 122.0673 | -2.6138 | -0.21515 | -0.027466 | 4.6051 | 0.16022 | -118.3456 | -0.18311 | -0.064087 | 4.8203 | 2.449 | 2.774 | 6.2164 | 124.5346 | 4.6051 | 124.498 | 4.9622 | -0.18311 | 124.5346 | 4.6051 | 4.9622 | 6.2164 | 124.498 | -124.7772 | -124.7452
956.3906 | 124.6262 | -2.4948 | 122.1085 | -0.79788 | 0.075821 | 0.045427 | 0.07166 | 0.066652 | 0.064044 | 0.24285 | 2.2247 | 122.2 | -2.6184 | -2.3163 | 3.8818 | 2.0966 | 0.10986 | 0.30212 | 122.0535 | -2.7145 | -0.1236 | 0.091553 | 4.7195 | 0.17853 | -118.2266 | -0.21973 | -0.054931 | 4.8431 | 2.6047 | 2.7969 | 6.3766 | 124.6948 | 4.7195 | 124.5483 | 4.5914 | -0.21973 | 124.6948 | 4.7195 | 4.5914 | 6.3766 | 124.5483 | -124.7269 | -124.823
957.375 | 124.6582 | -2.5085 | 122.081 | 0.018463 | 0.073899 | 0.038805 | 0.063542 | 0.068361 | 0.062762 | 0.24499 | 2.0874 | 122.0123 | -2.7466 | -2.3575 | 4.3625 | 1.8585 | 0.073242 | 0.34332 | 122.0306 | -2.6779 | -0.23804 | -0.068665 | 4.5959 | 0.15106 | -117.7185 | -0.16937 | -0.050354 | 4.834 | 2.5818 | 2.8519 | 6.871 | 124.5209 | 4.5959 | 124.5392 | 4.3671 | -0.16937 | 124.5209 | 4.5959 | 4.3671 | 6.871 | 124.5392 | -124.8276 | -124.7589
958.3906 | 124.585 | -2.4765 | 122.1634 | -0.10361 | 0.07753 | 0.042009 | 0.074223 | 0.06943 | 0.062976 | 0.24242 | 2.1332 | 122.2229 | -2.6733 | -2.2934 | 3.9551 | 2.3529 | 0.18768 | 0.37079 | 122.0947 | -2.6505 | -0.19684 | 0.059509 | 4.6097 | 0.1831 | -118.2083 | -0.17395 | -0.068664 | 4.8065 | 2.6642 | 2.8473 | 6.4316 | 124.6994 | 4.6097 | 124.5712 | 4.8294 | -0.17395 | 124.6994 | 4.6097 | 4.8294 | 6.4316 | 124.5712 | -124.8367 | -124.8138
959.375 | 124.6719 | -2.4719 | 122.0627 | 0.27023 | 0.075608 | 0.039232 | 0.068455 | 0.068789 | 0.064471 | 0.2452 | 2.2476 | 122.0764 | -2.6917 | -2.2659 | 4.0375 | 2.1927 | 0.61798 | 0.96588 | 122.0627 | -2.6413 | -0.21973 | 0.013733 | 4.7195 | 0.20599 | -118.0252 | -0.16937 | 0 | 4.9393 | 3.0899 | 3.4378 | 6.5094 | 124.5483 | 4.7195 | 124.5346 | 4.6646 | -0.16937 | 124.5483 | 4.7195 | 4.6646 | 6.5094 | 124.5346 | -124.7543 | -124.704
960.375 | 124.6445 | -2.4765 | 122.1039 | -0.1265 | 0.073258 | 0.033464 | 0.070378 | 0.068361 | 0.064899 | 0.25139 | 2.3712 | 122.0123 | -2.7054 | -2.3346 | 4.1382 | 1.8494 | 5.9509 | 6.1523 | 122.0673 | -2.6505 | -0.22888 | -0.091553 | 4.8477 | 0.14191 | -117.9657 | -0.17395 | -0.036621 | 5.0766 | 8.4274 | 8.6288 | 6.6147 | 124.4888 | 4.8477 | 124.5438 | 4.3259 | -0.17395 | 124.4888 | 4.8477 | 4.3259 | 6.6147 | 124.5438 | -124.8093 | -124.7543
961.3906 | 124.8093 | -12.9135 | 111.4563 | 2.704 | 0.073685 | 0.10353 | 1.0806 | 0.066866 | 0.046527 | 1.415 | -3.3646 | 111.1679 | -13.6093 | -13.3209 | 21.7712 | 2.6596 | 3.9734 | 2.449 | 111.319 | -13.0646 | -0.6958 | -0.28839 | 9.5489 | -0.40741 | -89.6851 | -0.15106 | -0.13733 | 10.2448 | 16.8869 | 15.3625 | 34.6848 | 124.0814 | 9.5489 | 124.2325 | 15.5731 | -0.15106 | 124.0814 | 9.5489 | 15.5731 | 34.6848 | 124.2325 | -125.0656 | -124.5209
962.375 | 123.9532 | -19.4595 | 104.425 | 0.11002 | 0.072617 | 0.14113 | 6.9381 | 0.065584 | 0.042468 | 7.0132 | -3.7765 | 104.0634 | -19.9402 | -16.7358 | 18.4753 | -5.0766 | 10.2631 | 0.37537 | 102.9327 | -18.3426 | -0.48065 | -0.36163 | 15.683 | 2.7237 | -85.9497 | 1.1169 | -1.4923 | 16.1636 | 29.7226 | 19.8349 | 37.9349 | 123.523 | 15.683 | 122.3923 | 14.3829 | 1.1169 | 123.523 | 15.683 | 14.3829 | 37.9349 | 122.3923 | -124.3652 | -122.7676
963.3906 | 124.2645 | -123.848 | 0.23346 | -0.24857 | 0.01088 | 0.011888 | 0.029149 | 0.002352 | -0.0019654 | 0.015981 | 0.022888 | 0.18768 | -0.22888 | 0.10071 | 0.10986 | 0.13275 | -0.050354 | 0.27008 | 0.25177 | -0.21515 | 123.6191 | -0.045776 | 123.8708 | 123.9487 | -0.1236 | 123.6328 | 0.018311 | 0.25177 | 123.7976 | 124.118 | 123.9578 | 124.0356 | 123.8708 | 124.0997 | 123.9807 | 123.6328 | 124.0356 | 123.8708 | 123.9807 | 123.9578 | 124.0997 | -0.46234 | -0.44861
964.4375 | 124.3652 | -124.0036 | 0.21057 | 0.16342 | 0.015152 | 0.018938 | 0.038975 | -0.00021158 | 0.0016662 | 0.014058 | -0.1236 | 0.16022 | -0.24261 | 0.064087 | 0.10529 | 0.14191 | -0.15106 | 0.24719 | 0.2243 | -0.17853 | 123.761 | -0.050354 | 123.88 | 124.0677 | -0.10529 | 123.8251 | 0.013733 | 0.11902 | 123.8525 | 124.2508 | 124.1089 | 124.1638 | 123.88 | 124.2279 | 124.1455 | 123.8251 | 124.1638 | 123.88 | 124.1455 | 124.1089 | 124.2279 | -0.45319 | -0.3891
965.375 | 124.411 | -124.0036 | 0.22888 | 0.17868 | 0.013657 | 0.014879 | 0.035985 | 0.0021384 | 0.0016662 | 0.014913 | 0.050354 | 0.15564 | -0.21973 | 0.11444 | 0.10071 | 0.13733 | -0.13275 | 0.23346 | 0.25177 | -0.1831 | 123.7839 | -0.073242 | 124.054 | 124.118 | -0.12817 | 123.8205 | 0.022888 | 0.27008 | 123.8709 | 124.2371 | 124.1043 | 124.1592 | 124.054 | 124.2554 | 124.1409 | 123.8205 | 124.1592 | 124.054 | 124.1409 | 124.1043 | 124.2554 | -0.44861 | -0.41199
966.375 | 124.4019 | -124.0723 | 0.23804 | 0.010834 | 0.010666 | 0.012529 | 0.032994 | -0.0017068 | 0.0016662 | 0.015127 | -0.027466 | 0.15106 | -0.22888 | 0.059509 | 0.068665 | 0.073242 | -0.013733 | 0.1831 | 0.24719 | -0.21057 | 123.8434 | -0.086975 | 124.0448 | 124.1318 | -0.16937 | 123.8617 | 0.009155 | 0.20142 | 124.0585 | 124.2554 | 124.1409 | 124.2233 | 124.0448 | 124.3195 | 124.1455 | 123.8617 | 124.2233 | 124.0448 | 124.1455 | 124.1409 | 124.3195 | -0.46692 | -0.44861
967.375 | 124.4568 | -124.1043 | 0.17395 | 0.16342 | 0.010666 | 0.016374 | 0.040684 | 0.0019248 | -0.002179 | 0.013631 | 0.082397 | 0.18768 | -0.23346 | 0.10986 | 0.082397 | 0.12817 | -0.48065 | 0.004578 | 0.21515 | -0.19684 | 123.8709 | 0.013733 | 124.1867 | 124.2142 | -0.091553 | 123.9075 | 0.041199 | 0.31586 | 123.6237 | 124.1089 | 124.1867 | 124.292 | 124.1867 | 124.3195 | 124.2325 | 123.9075 | 124.292 | 124.1867 | 124.2325 | 124.1867 | 124.3195 | -0.40741 | -0.37079
968.3906 | 124.4385 | -124.1043 | 0.23346 | -0.24857 | 0.010239 | 0.013383 | 0.037266 | -0.00042518 | -0.00046999 | 0.013418 | 0.032043 | 0.17395 | -0.23804 | 0.11444 | 0.09613 | 0.09613 | -0.032043 | 0.25177 | 0.25177 | -0.21057 | 123.8663 | -0.059509 | 124.1364 | 124.2188 | -0.13733 | 123.8937 | 0.018311 | 0.27008 | 124.0723 | 124.3561 | 124.2004 | 124.2783 | 124.1364 | 124.3561 | 124.2004 | 123.8937 | 124.2783 | 124.1364 | 124.2004 | 124.2004 | 124.3561 | -0.4715 | -0.44403
969.375 | 124.4843 | -124.0997 | 0.20599 | 0.25497 | 0.012375 | 0.016374 | 0.038548 | 0.00042942 | -0.0023926 | 0.016195 | -0.091553 | 0.14648 | -0.25635 | 0.091553 | 0.11444 | 0.13275 | -0.14191 | 0.23346 | 0.21515 | -0.19226 | 123.8434 | -0.05951 | 124.0082 | 124.1913 | -0.091553 | 123.9075 | 0.009155 | 0.1648 | 123.9578 | 124.3332 | 124.2142 | 124.2462 | 124.0082 | 124.3149 | 124.2325 | 123.9075 | 124.2462 | 124.0082 | 124.2325 | 124.2142 | 124.3149 | -0.46234 | -0.39826
970.375 | 124.4385 | -124.1089 | 0.20599 | 0.064239 | 0.0095982 | 0.014238 | 0.036626 | -0.0012796 | -0.00089719 | 0.016408 | -0.27466 | 0.16479 | -0.24261 | 0.041199 | 0.045776 | 0.036621 | -0.059509 | 0.16022 | 0.20599 | -0.20599 | 123.8663 | -0.041199 | 123.8342 | 124.1501 | -0.16022 | 123.9029 | 0 | -0.032043 | 124.0494 | 124.2691 | 124.1547 | 124.2737 | 123.8342 | 124.3149 | 124.1455 | 123.9029 | 124.2737 | 123.8342 | 124.1455 | 124.1547 | 124.3149 | -0.44861 | -0.41199
971.375 | 124.498 | -124.0997 | 0.21973 | 0.21683 | 0.01323 | 0.015947 | 0.041325 | 0.00021582 | -0.00068359 | 0.012563 | 0.059509 | 0.16937 | -0.24261 | 0.10529 | 0.10071 | 0.11444 | -0.13733 | 0.21973 | 0.22888 | -0.19684 | 123.8571 | -0.050354 | 124.1592 | 124.205 | -0.11902 | 123.9029 | 0.009155 | 0.30212 | 123.9624 | 124.3195 | 124.2004 | 124.2691 | 124.1592 | 124.3286 | 124.2142 | 123.9029 | 124.2691 | 124.1592 | 124.2142 | 124.2004 | 124.3286 | -0.46234 | -0.41657
972.375 | 124.4705 | -124.0997 | 0.21057 | 0.12527 | 0.010666 | 0.011461 | 0.037907 | -0.0019206 | -0.0019654 | 0.015981 | 0.032043 | 0.1831 | -0.22888 | 0.10071 | 0.10071 | 0.09613 | -0.09613 | 0.20599 | 0.24261 | -0.19684 | 123.8708 | -0.027466 | 124.1318 | 124.2004 | -0.10986 | 123.9029 | 0.032044 | 0.26093 | 124.0036 | 124.3057 | 124.2004 | 124.2828 | 124.1318 | 124.3423 | 124.1959 | 123.9029 | 124.2828 | 124.1318 | 124.1959 | 124.2004 | 124.3423 | -0.43945 | -0.40741
973.4531 | 124.4568 | -124.1089 | 0.20599 | -0.012055 | 0.0098118 | 0.017229 | 0.036839 | -0.0021342 | -0.00046999 | 0.014699 | 0 | 0.16937 | -0.24261 | 0.050354 | 0.045776 | 0.059509 | -0.064087 | 0.18768 | 0.24261 | -0.20142 | 123.8663 | -0.036621 | 124.1089 | 124.1592 | -0.16022 | 123.9075 | 0.036621 | 0.24261 | 124.0448 | 124.2966 | 124.1547 | 124.2783 | 124.1089 | 124.3515 | 124.1684 | 123.9075 | 124.2783 | 124.1089 | 124.1684 | 124.1547 | 124.3515 | -0.44861 | -0.40741
974.375 | 124.4568 | -124.1135 | 0.22888 | 0.16342 | 0.011948 | 0.011675 | 0.036626 | -0.0014932 | -0.0019654 | 0.015981 | -0.009155 | 0.18768 | -0.21973 | 0.050354 | 0.059509 | 0.082397 | -0.07782 | 0.16022 | 0.24261 | -0.21973 | 123.8937 | -0.041199 | 124.1043 | 124.1638 | -0.16937 | 123.8937 | 0.013733 | 0.21057 | 124.0356 | 124.2737 | 124.173 | 124.3011 | 124.1043 | 124.3561 | 124.1959 | 123.8937 | 124.3011 | 124.1043 | 124.1959 | 124.173 | 124.3561 | -0.44861 | -0.44861
975.375 | 124.4522 | -124.1638 | 0.21057 | 0.18631 | 0.01323 | 0.017015 | 0.041325 | 0.00042942 | -0.00068359 | 0.013418 | -0.027466 | 0.18768 | -0.26093 | 0.022888 | 0.004578 | 0.041199 | -0.064087 | 0.12817 | 0.21515 | -0.24719 | 123.9029 | -0.022888 | 124.1364 | 124.1867 | -0.20599 | 123.9166 | 0.004578 | 0.23346 | 124.0997 | 124.292 | 124.1684 | 124.3515 | 124.1364 | 124.379 | 124.205 | 123.9166 | 124.3515 | 124.1364 | 124.205 | 124.1684 | 124.379 | -0.4715 | -0.45776
976.375 | 124.5163 | -124.1272 | 0.19226 | 0.62881 | 0.013871 | 0.015306 | 0.03748 | 0.00021582 | -0.00089719 | 0.014486 | 0.091553 | 0.11444 | -0.26093 | 0.091553 | 0.10071 | 0.1236 | -0.13733 | 0.21973 | 0.22888 | -0.20599 | 123.8663 | -0.07782 | 124.2188 | 124.2188 | -0.091553 | 123.9212 | 0.036621 | 0.35248 | 123.9899 | 124.3469 | 124.2279 | 124.2416 | 124.2188 | 124.3561 | 124.2508 | 123.9212 | 124.2416 | 124.2188 | 124.2508 | 124.2279 | 124.3561 | -0.45319 | -0.39826
977.375 | 124.5071 | -124.1364 | 0.20599 | 0.20157 | 0.011948 | 0.015306 | 0.03983 | 0.0029928 | -0.003247 | 0.014486 | 0.027466 | 0.18768 | -0.25177 | 0.073242 | 0.064087 | 0.091553 | -0.11902 | 0.19684 | 0.2243 | -0.21515 | 123.8846 | -0.018311 | 124.1638 | 124.2096 | -0.14191 | 123.9212 | 0.01831 | 0.27924 | 124.0173 | 124.3332 | 124.2004 | 124.324 | 124.1638 | 124.3607 | 124.2279 | 123.9212 | 124.324 | 124.1638 | 124.2279 | 124.2004 | 124.3607 | -0.45776 | -0.42114
978.3906 | 124.4614 | -124.1547 | 0.23804 | -0.29434 | 0.010453 | 0.013811 | 0.036839 | -0.001066 | -0.0019654 | 0.015767 | 0.018311 | 0.15564 | -0.24261 | 0.091553 | 0.07782 | 0.082397 | -0.004578 | 0.20599 | 0.24261 | -0.21973 | 123.912 | -0.082397 | 124.173 | 124.2462 | -0.16022 | 123.9349 | 0.004578 | 0.26093 | 124.1501 | 124.3607 | 124.2325 | 124.3103 | 124.173 | 124.3973 | 124.2371 | 123.9349 | 124.3103 | 124.173 | 124.2371 | 124.2325 | 124.3973 | -0.48065 | -0.45776
979.375 | 124.4064 | -124.1913 | 0.24261 | 0.70511 | 0.013016 | 0.018297 | 0.045171 | 0.00064302 | -0.0019654 | 0.014913 | -0.018311 | 0.21973 | -0.25177 | -0.018311 | -0.041199 | -0.004578 | 0.004578 | 0.064087 | 0.2655 | -0.26093 | 123.9395 | -0.022888 | 124.173 | 124.173 | -0.28381 | 123.9304 | 0.022888 | 0.23346 | 124.1959 | 124.2554 | 124.1501 | 124.411 | 124.173 | 124.4568 | 124.1867 | 123.9304 | 124.411 | 124.173 | 124.1867 | 124.1501 | 124.4568 | -0.49438 | -0.50354
980.375 | 124.5071 | -124.1638 | 0.19684 | 0.17868 | 0.011734 | 0.013811 | 0.039616 | 0.002352 | -0.0028198 | 0.017263 | 0.036621 | 0.16479 | -0.25177 | 0.091553 | 0.091553 | 0.10071 | -0.13275 | 0.20142 | 0.2243 | -0.20142 | 123.912 | -0.032043 | 124.2004 | 124.2554 | -0.10529 | 123.9624 | 0.027466 | 0.28839 | 124.0311 | 124.3652 | 124.2554 | 124.3286 | 124.2004 | 124.3881 | 124.2645 | 123.9624 | 124.3286 | 124.2004 | 124.2645 | 124.2554 | 124.3881 | -0.44861 | -0.39825
981.375 | 124.4385 | -124.1776 | 0.21515 | 0.11765 | 0.013443 | 0.017015 | 0.042393 | 0.0014974 | -4.2788e-05 | 0.016408 | -0.032043 | 0.19226 | -0.27008 | -0.013733 | -0.013733 | 0 | 0.004578 | 0.086975 | 0.24261 | -0.25177 | 123.9075 | -0.022888 | 124.1455 | 124.1638 | -0.22888 | 123.9258 | 0.027466 | 0.23804 | 124.1821 | 124.2645 | 124.1638 | 124.3698 | 124.1455 | 124.4202 | 124.1776 | 123.9258 | 124.3698 | 124.1455 | 124.1776 | 124.1638 | 124.4202 | -0.48523 | -0.46692
982.375 | 124.5117 | -124.1638 | 0.21515 | 0.087128 | 0.013657 | 0.011888 | 0.034703 | 0.00042942 | -0.0026062 | 0.015127 | 0.004578 | 0.15564 | -0.23804 | 0.041199 | 0.054932 | 0.073242 | -0.07782 | 0.18768 | 0.21515 | -0.20599 | 123.9258 | -0.059509 | 124.1684 | 124.205 | -0.16022 | 123.9578 | 0 | 0.24261 | 124.086 | 124.3515 | 124.2188 | 124.3195 | 124.1684 | 124.379 | 124.2371 | 123.9578 | 124.3195 | 124.1684 | 124.2371 | 124.2188 | 124.379 | -0.45319 | -0.42114
983.3906 | 124.6033 | -124.2828 | 0.18768 | -0.027313 | 0.011521 | 0.011034 | 0.037053 | -0.00021158 | 0.0010254 | 0.015767 | 0.009155 | 0.15106 | -0.23804 | 0.013733 | 0.054932 | 0.068665 | -0.045776 | 0.16937 | 0.22888 | -0.27466 | 124.0448 | -0.036621 | 124.292 | 124.2966 | -0.13275 | 124.0082 | 0.041199 | 0.24719 | 124.2371 | 124.4522 | 124.3378 | 124.4339 | 124.292 | 124.5117 | 124.3515 | 124.0082 | 124.4339 | 124.292 | 124.3515 | 124.3378 | 124.5117 | -0.42572 | -0.46234
984.375 | 124.5209 | -124.173 | 0.20142 | 0.15579 | 0.015366 | 0.017656 | 0.041966 | -0.0017068 | 0.00081181 | 0.01534 | 0.041199 | 0.17395 | -0.23804 | 0.059509 | 0.091553 | 0.10071 | -0.16937 | 0.21057 | 0.20142 | -0.21973 | 123.9349 | -0.027466 | 124.2142 | 124.2325 | -0.10986 | 123.9532 | 0 | 0.27924 | 124.0036 | 124.3835 | 124.2645 | 124.3469 | 124.2142 | 124.3744 | 124.2737 | 123.9532 | 124.3469 | 124.2142 | 124.2737 | 124.2645 | 124.3744 | -0.43945 | -0.42114
985.375 | 124.4431 | -124.2142 | 0.21973 | 0.14053 | 0.013443 | 0.018083 | 0.042607 | 0.00085662 | -0.0017518 | 0.015767 | -0.004578 | 0.19226 | -0.26093 | -0.013733 | -0.018311 | -0.009155 | 0 | 0.082397 | 0.26093 | -0.25177 | 123.9532 | -0.027466 | 124.2096 | 124.2004 | -0.23804 | 123.9624 | 0.041198 | 0.25635 | 124.2142 | 124.2966 | 124.1959 | 124.4064 | 124.2096 | 124.4751 | 124.205 | 123.9624 | 124.4064 | 124.2096 | 124.205 | 124.1959 | 124.4751 | -0.48065 | -0.4715
986.375 | 124.498 | -124.1821 | 0.20599 | -0.019684 | 0.011521 | 0.015306 | 0.035771 | 0.0019248 | -0.0015382 | 0.014272 | -0.004578 | 0.15564 | -0.24719 | 0.032043 | 0.059509 | 0.091553 | -0.050354 | 0.17853 | 0.23346 | -0.21973 | 123.9349 | -0.050354 | 124.1776 | 124.2142 | -0.14649 | 123.9624 | 0.027465 | 0.24261 | 124.1318 | 124.3607 | 124.2416 | 124.3378 | 124.1776 | 124.4156 | 124.2737 | 123.9624 | 124.3378 | 124.1776 | 124.2737 | 124.2416 | 124.4156 | -0.45319 | -0.42572
987.375 | 124.4339 | -124.2233 | 0.21515 | 0.05661 | 0.016648 | 0.011461 | 0.042607 | 0.00064302 | -0.0026062 | 0.014272 | -0.009155 | 0.20599 | -0.26093 | -0.022888 | -0.027466 | -0.032043 | 0.041199 | 0.064087 | 0.23804 | -0.25635 | 123.9624 | -0.009155 | 124.2142 | 124.2004 | -0.24261 | 123.967 | 0.022888 | 0.25177 | 124.2645 | 124.2874 | 124.1959 | 124.4293 | 124.2142 | 124.4614 | 124.1913 | 123.967 | 124.4293 | 124.2142 | 124.1913 | 124.1959 | 124.4614 | -0.47607 | -0.4715
988.3906 | 124.5163 | -124.1913 | 0.17395 | -0.1799 | 0.011521 | 0.015733 | 0.036412 | -0.0017068 | -0.0017518 | 0.015767 | 0.068665 | 0.15106 | -0.21973 | 0.11902 | 0.12817 | 0.13733 | -0.091553 | 0.27008 | 0.21515 | -0.21515 | 123.9716 | -0.022888 | 124.2599 | 124.3103 | -0.045776 | 123.9761 | 0.041199 | 0.28839 | 124.0997 | 124.4614 | 124.3195 | 124.3423 | 124.2599 | 124.4064 | 124.3286 | 123.9761 | 124.3423 | 124.2599 | 124.3286 | 124.3195 | 124.4064 | -0.39368 | -0.3891
989.375 | 124.4522 | -124.2416 | 0.22888 | 0.11002 | 0.014298 | 0.018297 | 0.042607 | 0.00021582 | -0.00089719 | 0.012349 | -0.004578 | 0.19684 | -0.26093 | -0.004578 | -0.022888 | 0.004578 | 0.004578 | 0.086975 | 0.23346 | -0.24261 | 123.9807 | -0.032044 | 124.2371 | 124.2371 | -0.25177 | 123.999 | 0.004577 | 0.25635 | 124.2462 | 124.3286 | 124.2188 | 124.4385 | 124.2371 | 124.4751 | 124.2462 | 123.999 | 124.4385 | 124.2371 | 124.2462 | 124.2188 | 124.4751 | -0.48981 | -0.4715
990.375 | 124.5346 | -124.1959 | 0.21057 | 0.1329 | 0.010239 | 0.015092 | 0.041539 | 0.0021384 | -0.0026062 | 0.013845 | 0.064087 | 0.13275 | -0.2243 | 0.07782 | 0.07782 | 0.11444 | -0.1236 | 0.21515 | 0.20142 | -0.21057 | 123.9716 | -0.07782 | 124.2599 | 124.2737 | -0.13275 | 123.9853 | -0.009155 | 0.28839 | 124.0723 | 124.411 | 124.2737 | 124.3286 | 124.2599 | 124.3973 | 124.3103 | 123.9853 | 124.3286 | 124.2599 | 124.3103 | 124.2737 | 124.3973 | -0.43488 | -0.42114
991.375 | 124.6216 | -124.2188 | 0.14191 | 0.15579 | 0.012802 | 0.018297 | 0.03983 | 0.00064302 | -0.0015382 | 0.017476 | 0.073242 | 0.13275 | -0.23804 | 0.086975 | 0.10071 | 0.1236 | -0.21973 | -0.13275 | 0.1831 | -0.21515 | 123.9807 | -0.009156 | 124.292 | 124.3057 | -0.041199 | 124.0036 | 0.041198 | 0.31128 | 123.999 | 124.086 | 124.3195 | 124.3515 | 124.292 | 124.4019 | 124.3423 | 124.0036 | 124.3515 | 124.292 | 124.3423 | 124.3195 | 124.4019 | -0.37994 | -0.35706
992.375 | 124.4888 | -124.2325 | 0.21515 | 0.17105 | 0.015366 | 0.016588 | 0.042393 | -0.00085238 | -0.00025639 | 0.016195 | 0.009155 | 0.18768 | -0.27466 | 0.004578 | 0.018311 | 0.022888 | -0.054932 | 0.1236 | 0.21057 | -0.25635 | 123.9578 | -0.027466 | 124.2416 | 124.2371 | -0.19684 | 123.9761 | -0.004578 | 0.28381 | 124.1776 | 124.3561 | 124.2508 | 124.4202 | 124.2416 | 124.4431 | 124.2554 | 123.9761 | 124.4202 | 124.2416 | 124.2554 | 124.2508 | 124.4431 | -0.48981 | -0.4715
993.375 | 124.4659 | -124.205 | 0.21515 | 0.17105 | 0.014084 | 0.014665 | 0.041112 | 0.0025656 | 0.00059821 | 0.015127 | -0.004578 | 0.1831 | -0.26093 | -0.004578 | 0.009155 | 0.013733 | -0.018311 | 0.11444 | 0.23804 | -0.23346 | 123.9441 | -0.032044 | 124.2004 | 124.2004 | -0.20599 | 123.9716 | 0.022888 | 0.25635 | 124.1867 | 124.3195 | 124.2142 | 124.3881 | 124.2004 | 124.4431 | 124.2188 | 123.9716 | 124.3881 | 124.2004 | 124.2188 | 124.2142 | 124.4431 | -0.47607 | -0.44861
994.375 | 124.5438 | -124.1867 | 0.20599 | 0.20157 | 0.014084 | 0.014665 | 0.039403 | 0.0014974 | -0.0019654 | 0.01299 | 0.041199 | 0.16022 | -0.25635 | 0.059509 | 0.050354 | 0.07782 | -0.10986 | 0.20142 | 0.21515 | -0.21515 | 123.9304 | -0.045777 | 124.2279 | 124.2462 | -0.15564 | 123.9716 | 0.009155 | 0.29755 | 124.0768 | 124.3881 | 124.2371 | 124.3469 | 124.2279 | 124.4019 | 124.2645 | 123.9716 | 124.3469 | 124.2279 | 124.2645 | 124.2371 | 124.4019 | -0.46234 | -0.42114
995.375 | 124.411 | -124.2416 | 0.24261 | 0.11002 | 0.01323 | 0.021928 | 0.043248 | 0.0014974 | -0.0026062 | 0.015554 | -0.027466 | 0.20142 | -0.27008 | -0.17395 | -0.15564 | 0.041199 | 0.086975 | -0.018311 | 0.2655 | -0.24261 | 123.9716 | -0.041199 | 124.2142 | 124.0677 | -0.39826 | 123.999 | 0.022888 | 0.24262 | 124.3286 | 124.2233 | 124.086 | 124.4431 | 124.2142 | 124.5071 | 124.2828 | 123.999 | 124.4431 | 124.2142 | 124.2828 | 124.086 | 124.5071 | -0.5127 | -0.48523
996.375 | 124.5163 | -124.1821 | 0.20599 | 0.16342 | 0.012375 | 0.012743 | 0.039616 | 0.0027792 | -0.00068359 | 0.018117 | 0.004578 | 0.17395 | -0.25177 | 0.032043 | 0.045776 | 0.054932 | -0.10071 | 0.16937 | 0.21057 | -0.21515 | 123.9304 | -0.032044 | 124.1867 | 124.2142 | -0.16022 | 123.967 | 0.004577 | 0.25635 | 124.0814 | 124.3515 | 124.2279 | 124.3561 | 124.1867 | 124.3927 | 124.2371 | 123.967 | 124.3561 | 124.1867 | 124.2371 | 124.2279 | 124.3927 | -0.45776 | -0.42114
997.375 | 124.4019 | -124.2508 | 0.2243 | 0.048981 | 0.016648 | 0.017229 | 0.041325 | 0.001711 | -0.0026062 | 0.016622 | -0.054932 | 0.17853 | -0.28381 | -0.045776 | -0.054932 | -0.032043 | 0.050354 | 0.045776 | 0.23804 | -0.2655 | 123.967 | -0.045776 | 124.1959 | 124.205 | -0.27924 | 123.9853 | 0.013733 | 0.22888 | 124.3011 | 124.2966 | 124.1959 | 124.4293 | 124.1959 | 124.4888 | 124.2188 | 123.9853 | 124.4293 | 124.1959 | 124.2188 | 124.1959 | 124.4888 | -0.50812 | -0.48981
998.375 | 124.5621 | -124.1913 | 0.18768 | 0.14816 | 0.013871 | 0.018297 | 0.036412 | 0.0032064 | -0.0023926 | 0.015981 | 0.022888 | 0.13275 | -0.24719 | 0.073242 | 0.082397 | 0.10986 | -0.14191 | 0.21057 | 0.21057 | -0.20599 | 123.9441 | -0.054932 | 124.2142 | 124.2645 | -0.10529 | 123.9853 | 0.022888 | 0.27008 | 124.0494 | 124.4019 | 124.2737 | 124.324 | 124.2142 | 124.4019 | 124.3011 | 123.9853 | 124.324 | 124.2142 | 124.3011 | 124.2737 | 124.4019 | -0.43488 | -0.39368
999.375 | 124.5438 | -124.2462 | 0.17395 | 0.018463 | 0.011948 | 0.016374 | 0.038762 | 0.0021384 | -0.0013244 | 0.014699 | 0.059509 | 0.17395 | -0.25635 | 0.07782 | 0.082397 | 0.11444 | -0.13275 | 0.20599 | 0.21057 | -0.21057 | 123.9899 | 0 | 124.3057 | 124.324 | -0.091553 | 124.0356 | 0.036621 | 0.31586 | 124.1135 | 124.4522 | 124.3286 | 124.4202 | 124.3057 | 124.4568 | 124.3607 | 124.0356 | 124.4202 | 124.3057 | 124.3607 | 124.3286 | 124.4568 | -0.4303 | -0.38452
1000.375 | 124.4476 | -124.2508 | 0.2243 | -0.48508 | 0.014725 | 0.016801 | 0.041966 | 0.0019248 | -0.0015382 | 0.017263 | -0.073242 | 0.19684 | -0.24719 | -0.027466 | -0.041199 | -0.013733 | 0.018311 | 0.073242 | 0.24719 | -0.25635 | 124.0036 | -0.027466 | 124.1776 | 124.2233 | -0.2655 | 123.9944 | 0.022888 | 0.17395 | 124.2691 | 124.324 | 124.2096 | 124.4476 | 124.1776 | 124.498 | 124.2371 | 123.9944 | 124.4476 | 124.1776 | 124.2371 | 124.2096 | 124.498 | -0.4715 | -0.48065
1001.375 | 124.4339 | -124.2462 | 0.21973 | -1.0115 | 0.013443 | 0.020647 | 0.043462 | 0.005129 | -0.0015382 | 0.016408 | -0.054932 | 0.21057 | -0.25635 | -0.036621 | -0.032043 | -0.004578 | 0.013733 | 0.073242 | 0.24719 | -0.23346 | 123.9899 | -0.009156 | 124.1913 | 124.2096 | -0.25177 | 124.0128 | 0.027465 | 0.20142 | 124.2599 | 124.3195 | 124.2142 | 124.4568 | 124.1913 | 124.4934 | 124.2416 | 124.0128 | 124.4568 | 124.1913 | 124.2416 | 124.2142 | 124.4934 | -0.47608 | -0.45319
1002.375 | 124.5529 | -124.2004 | 0.20142 | 0.24734 | 0.013443 | 0.019792 | 0.038335 | 0.00085662 | -0.0023926 | 0.01534 | 0.050354 | 0.13733 | -0.25177 | 0.073242 | 0.10529 | 0.1236 | -0.13733 | 0.21973 | 0.21973 | -0.21973 | 123.9487 | -0.064087 | 124.2508 | 124.2737 | -0.09613 | 123.9807 | 0.018311 | 0.30212 | 124.0631 | 124.4202 | 124.3057 | 124.3378 | 124.2508 | 124.4202 | 124.324 | 123.9807 | 124.3378 | 124.2508 | 124.324 | 124.3057 | 124.4202 | -0.45319 | -0.42114
1003.375 | 124.585 | -124.1959 | 0.21515 | 0.15579 | 0.011521 | 0.015947 | 0.040684 | 0.004061 | -0.00068359 | 0.014058 | 0.018311 | 0.17395 | -0.26093 | 0.064087 | 0.086975 | 0.11444 | -0.12817 | 0.19684 | 0.21515 | -0.21515 | 123.9349 | -0.041199 | 124.2142 | 124.2599 | -0.12817 | 123.9807 | 0 | 0.27924 | 124.0677 | 124.3927 | 124.2828 | 124.3698 | 124.2142 | 124.411 | 124.3103 | 123.9807 | 124.3698 | 124.2142 | 124.3103 | 124.2828 | 124.411 | -0.47607 | -0.4303
1004.375 | 124.4568 | -124.2371 | 0.21515 | 0.15579 | 0.013443 | 0.012102 | 0.041539 | 0.0032064 | -4.2788e-05 | 0.017476 | -0.018311 | 0.18768 | -0.27924 | -0.009155 | -0.032043 | 0 | -0.018311 | 0.086975 | 0.23804 | -0.24719 | 123.9578 | -0.027466 | 124.2188 | 124.2279 | -0.24719 | 123.9899 | 0.022888 | 0.26092 | 124.2188 | 124.324 | 124.205 | 124.4247 | 124.2188 | 124.4751 | 124.2371 | 123.9899 | 124.4247 | 124.2188 | 124.2371 | 124.205 | 124.4751 | -0.49438 | -0.46234
1005.375 | 124.4888 | -124.2416 | 0.21057 | 0.11002 | 0.012589 | 0.014665 | 0.042607 | 0.0027792 | -0.00068359 | 0.01534 | -0.022888 | 0.1831 | -0.27008 | -0.027466 | -0.009155 | 0.013733 | -0.004578 | 0.091553 | 0.23804 | -0.24261 | 123.9716 | -0.027466 | 124.2188 | 124.2142 | -0.21973 | 123.999 | 0.027466 | 0.24719 | 124.2371 | 124.3332 | 124.2325 | 124.4247 | 124.2188 | 124.4797 | 124.2554 | 123.999 | 124.4247 | 124.2188 | 124.2554 | 124.2325 | 124.4797 | -0.48065 | -0.45319
1006.375 | 124.5346 | -124.2004 | 0.21515 | 0.12527 | 0.011521 | 0.011675 | 0.035344 | 0.00085662 | -0.0013244 | 0.016622 | 0.059509 | 0.14648 | -0.21515 | 0.059509 | 0.07782 | 0.12817 | -0.10986 | 0.21973 | 0.20599 | -0.21057 | 123.9853 | -0.068665 | 124.2599 | 124.2599 | -0.13733 | 123.9899 | -0.009155 | 0.27466 | 124.0906 | 124.4202 | 124.2783 | 124.3469 | 124.2599 | 124.4064 | 124.3286 | 123.9899 | 124.3469 | 124.2599 | 124.3286 | 124.2783 | 124.4064 | -0.4303 | -0.42572
1007.375 | 124.4843 | -124.2096 | 0.21057 | 0.20157 | 0.014939 | 0.014879 | 0.040471 | 0.00342 | -0.0017518 | 0.015981 | -0.009155 | 0.19226 | -0.27008 | -0.027466 | -0.036621 | 0.004578 | 0 | 0.091553 | 0.24261 | -0.26093 | 123.9395 | -0.01831 | 124.2004 | 124.1821 | -0.24719 | 123.9487 | 0.032044 | 0.26093 | 124.2096 | 124.3011 | 124.173 | 124.4019 | 124.2004 | 124.4522 | 124.2142 | 123.9487 | 124.4019 | 124.2004 | 124.2142 | 124.173 | 124.4522 | -0.48065 | -0.4715
1008.375 | 124.5529 | -124.205 | 0.1831 | 0.20157 | 0.012589 | 0.016801 | 0.040044 | 0.002352 | -0.00089719 | 0.016408 | 0.045776 | 0.16022 | -0.24719 | 0.036621 | 0.050354 | 0.073242 | -0.09613 | 0.19226 | 0.21057 | -0.21973 | 123.9578 | -0.022888 | 124.2508 | 124.2416 | -0.13275 | 123.9853 | 0.027466 | 0.29297 | 124.1089 | 124.3973 | 124.2554 | 124.3652 | 124.2508 | 124.4156 | 124.2783 | 123.9853 | 124.3652 | 124.2508 | 124.2783 | 124.2554 | 124.4156 | -0.4303 | -0.40283
1009.375 | 124.4888 | -124.2371 | 0.21973 | 0.1329 | 0.015793 | 0.016801 | 0.040044 | 0.0032064 | -4.2788e-05 | 0.016195 | 0 | 0.21973 | -0.27924 | -0.009155 | 0 | 0.004578 | 0.027466 | 0.10071 | 0.24261 | -0.23346 | 123.9578 | 0 | 124.2371 | 124.2279 | -0.21973 | 124.0036 | 0.022888 | 0.27924 | 124.2645 | 124.3378 | 124.2371 | 124.4568 | 124.2371 | 124.4797 | 124.2416 | 124.0036 | 124.4568 | 124.2371 | 124.2416 | 124.2371 | 124.4797 | -0.49896 | -0.45319
1010.375 | 124.5438 | -124.2096 | 0.21973 | 0.2092 | 0.013016 | 0.014238 | 0.039616 | 0.0036336 | -0.00046999 | 0.015127 | 0.018311 | 0.1831 | -0.25635 | 0.045776 | 0.045776 | 0.082397 | -0.082397 | 0.16022 | 0.23346 | -0.21515 | 123.9532 | -0.036622 | 124.2279 | 124.2554 | -0.17395 | 123.9944 | 0.013732 | 0.27466 | 124.1272 | 124.3698 | 124.2554 | 124.3927 | 124.2279 | 124.4431 | 124.292 | 123.9944 | 124.3927 | 124.2279 | 124.292 | 124.2554 | 124.4431 | -0.47608 | -0.43488
1011.375 | 124.6033 | -124.205 | 0.17853 | 0.11002 | 0.01323 | 0.016374 | 0.039616 | 0.00342 | 0.00059821 | 0.016195 | 0.10071 | 0.16022 | -0.2243 | 0.086975 | 0.10529 | 0.1236 | -0.12817 | 0.2243 | 0.21057 | -0.19226 | 123.9807 | -0.018311 | 124.3057 | 124.292 | -0.073242 | 124.0128 | 0.032043 | 0.32501 | 124.0768 | 124.4293 | 124.3103 | 124.3652 | 124.3057 | 124.4156 | 124.3286 | 124.0128 | 124.3652 | 124.3057 | 124.3286 | 124.3103 | 124.4156 | -0.40283 | -0.37079
1012.375 | 124.53 | -124.2142 | 0.2243 | 0.17105 | 0.013871 | 0.016374 | 0.037907 | 0.0014974 | 0.00017081 | 0.016622 | 0.036621 | 0.18768 | -0.25177 | 0.036621 | 0.027466 | 0.045776 | -0.054932 | 0.13733 | 0.2243 | -0.21057 | 123.9624 | -0.036621 | 124.2508 | 124.2508 | -0.19684 | 124.0036 | 0 | 0.28839 | 124.1592 | 124.3515 | 124.2416 | 124.4019 | 124.2508 | 124.4385 | 124.2599 | 124.0036 | 124.4019 | 124.2508 | 124.2599 | 124.2416 | 124.4385 | -0.47607 | -0.43488
1013.375 | 124.5346 | -124.1913 | 0.19226 | 0.071869 | 0.012162 | 0.01317 | 0.033849 | 0.00085662 | 0.0018798 | 0.015554 | 0.050354 | 0.16022 | -0.21515 | 0.068665 | 0.082397 | 0.10071 | -0.082397 | 0.19684 | 0.23804 | -0.19684 | 123.9761 | -0.032044 | 124.2416 | 124.2599 | -0.10986 | 123.9944 | 0.045776 | 0.2655 | 124.1089 | 124.3881 | 124.2737 | 124.3515 | 124.2416 | 124.4293 | 124.292 | 123.9944 | 124.3515 | 124.2416 | 124.292 | 124.2737 | 124.4293 | -0.40741 | -0.3891
1014.375 | 124.4888 | -124.2462 | 0.21515 | -0.24857 | 0.014939 | 0.014238 | 0.040257 | -0.00042518 | -0.0011108 | 0.015981 | -0.013733 | 0.20142 | -0.24719 | 0.009155 | 0.004578 | 0.022888 | -0.022888 | 0.11444 | 0.2243 | -0.23804 | 123.999 | -0.013733 | 124.2325 | 124.2554 | -0.21057 | 124.0082 | 0.009155 | 0.23346 | 124.2233 | 124.3607 | 124.2508 | 124.4476 | 124.2325 | 124.4705 | 124.2691 | 124.0082 | 124.4476 | 124.2325 | 124.2691 | 124.2508 | 124.4705 | -0.46234 | -0.45319
1015.375 | 124.585 | -124.2004 | 0.17853 | 0.14816 | 0.012375 | 0.018938 | 0.039403 | 0.001711 | -0.0019654 | 0.01534 | 0.09613 | 0.13733 | -0.22888 | 0.086975 | 0.07782 | 0.11444 | -0.13733 | 0.21057 | 0.20599 | -0.22888 | 123.9716 | -0.041199 | 124.2966 | 124.2874 | -0.10071 | 123.9716 | 0.027466 | 0.32501 | 124.0631 | 124.411 | 124.2783 | 124.3378 | 124.2966 | 124.4064 | 124.3149 | 123.9716 | 124.3378 | 124.2966 | 124.3149 | 124.2783 | 124.4064 | -0.40741 | -0.40741
1016.375 | 124.4888 | -124.2508 | 0.21973 | 0.11002 | 0.015152 | 0.016161 | 0.041966 | 0.0064108 | -0.0013244 | 0.014913 | -0.009155 | 0.17853 | -0.25635 | 0.10986 | 0.12817 | 0.004578 | 0.054932 | 0.16479 | 0.26093 | -0.21515 | 123.9944 | -0.041199 | 124.2416 | 124.3607 | -0.091553 | 124.0356 | 0.041198 | 0.24719 | 124.3057 | 124.4156 | 124.379 | 124.4293 | 124.2416 | 124.5117 | 124.2554 | 124.0356 | 124.4293 | 124.2416 | 124.2554 | 124.379 | 124.5117 | -0.47608 | -0.43488
1017.375 | 124.4064 | -124.2096 | 0.21515 | 0.11002 | 0.014298 | 0.014665 | 0.041325 | 0.0038474 | -0.00068359 | 0.014486 | 0 | 0.17395 | -0.26093 | -0.013733 | -0.022888 | -0.018311 | 0.013733 | 0.07782 | 0.25177 | -0.25177 | 123.9487 | -0.041199 | 124.2096 | 124.1959 | -0.23804 | 123.9578 | 0.036621 | 0.26093 | 124.2233 | 124.2874 | 124.1867 | 124.3835 | 124.2096 | 124.4614 | 124.1913 | 123.9578 | 124.3835 | 124.2096 | 124.1913 | 124.1867 | 124.4614 | -0.47607 | -0.46692
1018.375 | 124.5438 | -124.2096 | 0.19684 | 0.11765 | 0.010025 | 0.016801 | 0.036839 | 0.001711 | -0.0019654 | 0.016622 | 0.059509 | 0.12817 | -0.22888 | 0.054932 | 0.082397 | 0.091553 | -0.09613 | 0.19226 | 0.22888 | -0.21515 | 123.9807 | -0.068664 | 124.2691 | 124.2645 | -0.11444 | 123.9944 | 0.032044 | 0.28839 | 124.1135 | 124.4019 | 124.292 | 124.3378 | 124.2691 | 124.4385 | 124.3011 | 123.9944 | 124.3378 | 124.2691 | 124.3011 | 124.292 | 124.4385 | -0.42572 | -0.41199
1019.375 | 124.5895 | -124.2279 | 0.1831 | 0.094757 | 0.012802 | 0.018297 | 0.040471 | 0.0019248 | -0.0023926 | 0.015981 | 0.045776 | 0.15564 | -0.25635 | 0.050354 | 0.059509 | 0.064087 | -0.091553 | 0.16937 | 0.19226 | -0.22888 | 123.9716 | -0.027465 | 124.2737 | 124.2783 | -0.1236 | 123.999 | 0.009156 | 0.30212 | 124.1364 | 124.3973 | 124.2874 | 124.3835 | 124.2737 | 124.4202 | 124.292 | 123.999 | 124.3835 | 124.2737 | 124.292 | 124.2874 | 124.4202 | -0.43945 | -0.41199
1020.375 | 124.5346 | -124.2508 | 0.19684 | 0.15579 | 0.015152 | 0.012743 | 0.040257 | 0.0012838 | -0.00068359 | 0.013845 | 0.004578 | 0.16479 | -0.25635 | 0.013733 | 0.022888 | 0.050354 | -0.068665 | 0.15106 | 0.20599 | -0.21973 | 123.9944 | -0.032043 | 124.2554 | 124.2645 | -0.17395 | 124.0311 | 0.009156 | 0.26093 | 124.1821 | 124.4019 | 124.2737 | 124.4156 | 124.2554 | 124.4568 | 124.3011 | 124.0311 | 124.4156 | 124.2554 | 124.3011 | 124.2737 | 124.4568 | -0.45319 | -0.41657
1021.375 | 124.4614 | -124.2691 | 0.21057 | -0.0044251 | 0.013657 | 0.014665 | 0.042821 | 0.00042942 | -0.0017518 | 0.012349 | -0.004578 | 0.17853 | -0.27008 | -0.022888 | -0.027466 | -0.022888 | 0.045776 | 0.082397 | 0.24261 | -0.27924 | 123.999 | -0.032043 | 124.2645 | 124.2462 | -0.23804 | 123.9899 | 0.032044 | 0.2655 | 124.3149 | 124.3515 | 124.2416 | 124.4476 | 124.2645 | 124.5117 | 124.2462 | 123.9899 | 124.4476 | 124.2645 | 124.2462 | 124.2416 | 124.5117 | -0.48065 | -0.48981
1022.375 | 124.4659 | -124.2599 | 0.20599 | -0.095978 | 0.013871 | 0.018083 | 0.040898 | 0.0029928 | -0.0023926 | 0.01534 | -0.022888 | 0.17853 | -0.25635 | -0.013733 | -0.032043 | 0 | 0 | 0.10529 | 0.23804 | -0.24719 | 124.0036 | -0.027466 | 124.2371 | 124.2462 | -0.23804 | 124.0128 | 0.032043 | 0.23346 | 124.2599 | 124.3652 | 124.2279 | 124.4385 | 124.2371 | 124.498 | 124.2599 | 124.0128 | 124.4385 | 124.2371 | 124.2599 | 124.2279 | 124.498 | -0.46234 | -0.45319
1023.375 | 124.5987 | -124.2188 | 0.18768 | 0.087128 | 0.013016 | 0.014665 | 0.036839 | 0.0029928 | -0.0019654 | 0.016622 | 0.073242 | 0.13733 | -0.23346 | 0.073242 | 0.082397 | 0.1236 | -0.13733 | 0.21973 | 0.20599 | -0.21515 | 123.9853 | -0.050354 | 124.292 | 124.292 | -0.10529 | 124.0036 | 0.018311 | 0.3067 | 124.0814 | 124.4385 | 124.3011 | 124.3561 | 124.292 | 124.4247 | 124.3423 | 124.0036 | 124.3561 | 124.292 | 124.3423 | 124.3011 | 124.4247 | -0.42114 | -0.40283
1024.375 | 124.4614 | -124.2737 | 0.23346 | 0.14816 | 0.013657 | 0.014879 | 0.041112 | 0.0036336 | -0.00046999 | 0.014272 | -0.004578 | 0.1831 | -0.25177 | -0.027466 | -0.022888 | 0.068665 | -0.30212 | 0.064087 | 0.23804 | -0.22888 | 124.0219 | -0.050354 | 124.2691 | 124.2462 | -0.25635 | 124.0448 | 0.004578 | 0.24719 | 123.9716 | 124.3378 | 124.2508 | 124.4568 | 124.2691 | 124.5117 | 124.3423 | 124.0448 | 124.4568 | 124.2691 | 124.3423 | 124.2508 | 124.5117 | -0.48523 | -0.46234
1025.375 | 124.4888 | -124.2645 | 0.21515 | 0.048981 | 0.01323 | 0.012102 | 0.04218 | 0.0021384 | -0.0028198 | 0.015981 | -0.018311 | 0.19684 | -0.2655 | -0.036621 | -0.045776 | -0.009155 | 0.032043 | 0.07782 | 0.24261 | -0.2655 | 123.999 | -0.018311 | 124.2462 | 124.2279 | -0.26093 | 123.999 | 0.027466 | 0.24719 | 124.2966 | 124.3423 | 124.2188 | 124.4614 | 124.2462 | 124.5071 | 124.2554 | 123.999 | 124.4614 | 124.2462 | 124.2554 | 124.2188 | 124.5071 | -0.48065 | -0.48065
1026.375 | 124.5255 | -124.2233 | 0.20142 | 0.16342 | 0.015152 | 0.016801 | 0.040684 | 0.0032064 | -0.00089719 | 0.015767 | 0.004578 | 0.16022 | -0.2655 | 0 | 0.009155 | 0.032043 | -0.059509 | 0.1236 | 0.21973 | -0.24719 | 123.9578 | -0.041199 | 124.2279 | 124.2233 | -0.19226 | 123.9761 | 0.018311 | 0.27008 | 124.1638 | 124.3469 | 124.2325 | 124.3835 | 124.2279 | 124.4431 | 124.2554 | 123.9761 | 124.3835 | 124.2279 | 124.2554 | 124.2325 | 124.4431 | -0.46692 | -0.44861
1027.375 | 124.4568 | -124.3011 | 0.24719 | 0.10239 | 0.014511 | 0.010393 | 0.039403 | 0.0012838 | -0.00089719 | 0.017049 | 0.004578 | 0.1831 | -0.27008 | -0.045776 | 0.15564 | -0.013733 | -0.045776 | 0.37537 | 0.25635 | -0.23804 | 124.0311 | -0.064087 | 124.3057 | 124.2554 | -0.091552 | 124.0631 | 0.009156 | 0.27466 | 124.2554 | 124.6765 | 124.4568 | 124.4843 | 124.3057 | 124.5575 | 124.2874 | 124.0631 | 124.4843 | 124.3057 | 124.2874 | 124.4568 | 124.5575 | -0.51727 | -0.48523
1028.375 | 124.4888 | -124.2828 | 0.20142 | -0.0044251 | 0.014725 | 0.01552 | 0.040684 | 0.0049154 | -0.002179 | 0.01534 | 0.013733 | 0.17395 | -0.27008 | -0.009155 | -0.022888 | -0.013733 | 0.032043 | 0.091553 | 0.22888 | -0.27466 | 124.0128 | -0.027466 | 124.2966 | 124.2737 | -0.2243 | 124.0082 | 0.027466 | 0.28381 | 124.3149 | 124.3744 | 124.2599 | 124.4568 | 124.2966 | 124.5117 | 124.2691 | 124.0082 | 124.4568 | 124.2966 | 124.2691 | 124.2599 | 124.5117 | -0.4715 | -0.47607
1029.375 | 124.4843 | -124.2645 | 0.20599 | -0.012055 | 0.014725 | 0.016801 | 0.038121 | 0.0047018 | -0.0015382 | 0.017049 | 0.036621 | 0.17395 | -0.24719 | -0.004578 | -0.032043 | 0.009155 | 0.032043 | 0.11444 | 0.2243 | -0.26093 | 124.0173 | -0.032044 | 124.3011 | 124.2599 | -0.23804 | 124.0036 | 0.01831 | 0.28381 | 124.2966 | 124.379 | 124.2325 | 124.4385 | 124.3011 | 124.4888 | 124.2737 | 124.0036 | 124.4385 | 124.3011 | 124.2737 | 124.2325 | 124.4888 | -0.45319 | -0.46692
1030.375 | 124.5117 | -124.292 | 0.20142 | 0.1329 | 0.01558 | 0.015092 | 0.038335 | 0.00342 | -4.2788e-05 | 0.016195 | 0 | 0.19226 | -0.26093 | -0.013733 | -0.004578 | 0.009155 | -0.004578 | 0.10071 | 0.2655 | -0.25635 | 124.0311 | -0.009155 | 124.292 | 124.2783 | -0.20599 | 124.0356 | 0.064087 | 0.26093 | 124.2874 | 124.3927 | 124.2874 | 124.4843 | 124.292 | 124.5575 | 124.3011 | 124.0356 | 124.4843 | 124.292 | 124.3011 | 124.2874 | 124.5575 | -0.46234 | -0.45776
1031.375 | 124.4476 | -124.2828 | 0.23346 | 0.026092 | 0.017502 | 0.017656 | 0.038975 | 0.0029928 | -0.0026062 | 0.01534 | -0.018311 | 0.19684 | -0.27008 | -0.045776 | -0.032043 | -0.009155 | 0.032043 | 0.064087 | 0.25177 | -0.26093 | 124.0128 | -0.036621 | 124.2645 | 124.2371 | -0.2655 | 124.0219 | 0.018311 | 0.25177 | 124.3149 | 124.3469 | 124.2508 | 124.4797 | 124.2645 | 124.5346 | 124.2737 | 124.0219 | 124.4797 | 124.2645 | 124.2737 | 124.2508 | 124.5346 | -0.50354 | -0.49438
1032.375 | 124.4614 | -124.2874 | 0.23804 | -0.0044251 | 0.013016 | 0.018297 | 0.038762 | 0.0042746 | -0.0011108 | 0.01534 | -0.004578 | 0.1831 | -0.27466 | -0.045776 | -0.041199 | -0.022888 | 0.045776 | 0.073242 | 0.23346 | -0.24719 | 124.0128 | -0.054932 | 124.2828 | 124.2416 | -0.27924 | 124.0402 | -0.004578 | 0.27008 | 124.3332 | 124.3607 | 124.2462 | 124.4705 | 124.2828 | 124.5209 | 124.2645 | 124.0402 | 124.4705 | 124.2828 | 124.2645 | 124.2462 | 124.5209 | -0.5127 | -0.48523
1033.375 | 124.5026 | -124.2874 | 0.20599 | -0.027313 | 0.021988 | 0.019151 | 0.032353 | 0.0049154 | 0.0010254 | 0.015767 | 0.050354 | 0.19684 | -0.22888 | 0.013733 | 0.018311 | 0.032043 | 0.013733 | 0.1236 | 0.23346 | -0.24719 | 124.0585 | -0.009156 | 124.3378 | 124.3011 | -0.18768 | 124.0402 | 0.027465 | 0.27924 | 124.3011 | 124.411 | 124.3057 | 124.4843 | 124.3378 | 124.5209 | 124.3195 | 124.0402 | 124.4843 | 124.3378 | 124.3195 | 124.3057 | 124.5209 | -0.43488 | -0.45319
1034.375 | 124.4797 | -124.2828 | 0.2243 | 0.11002 | 0.022843 | 0.016374 | 0.030003 | 0.005129 | -0.00046999 | 0.013631 | -0.022888 | 0.16937 | -0.27466 | -0.045776 | -0.013733 | -0.018311 | 0.027466 | 0.054932 | 0.23804 | -0.24719 | 124.0082 | -0.054931 | 124.2599 | 124.2371 | -0.23804 | 124.0356 | 0.013733 | 0.25177 | 124.3103 | 124.3378 | 124.2691 | 124.4522 | 124.2599 | 124.5209 | 124.2645 | 124.0356 | 124.4522 | 124.2599 | 124.2645 | 124.2691 | 124.5209 | -0.49896 | -0.4715
1035.375 | 124.4888 | -124.2645 | 0.2243 | -0.042572 | 0.024765 | 0.019579 | 0.029362 | 0.0047018 | -0.0019654 | 0.015767 | 0.036621 | 0.17395 | -0.25635 | -0.032043 | 0 | 0 | 0.018311 | 0.09613 | 0.21973 | -0.25635 | 124.0082 | -0.050354 | 124.3011 | 124.2325 | -0.2243 | 124.0082 | -0.004577 | 0.29297 | 124.2828 | 124.3607 | 124.2645 | 124.4385 | 124.3011 | 124.4843 | 124.2645 | 124.0082 | 124.4385 | 124.3011 | 124.2645 | 124.2645 | 124.4843 | -0.48065 | -0.48065
1036.375 | 124.5026 | -124.292 | 0.19684 | -0.088349 | 0.023911 | 0.016588 | 0.028935 | 0.0042746 | -0.0011108 | 0.015767 | 0.041199 | 0.18768 | -0.27008 | 0.004578 | 0.009155 | 0.013733 | 0.004578 | 0.10529 | 0.24261 | -0.2655 | 124.0219 | -0.009155 | 124.3332 | 124.2966 | -0.18768 | 124.0265 | 0.045777 | 0.31128 | 124.2966 | 124.3973 | 124.3011 | 124.4797 | 124.3332 | 124.5346 | 124.3057 | 124.0265 | 124.4797 | 124.3332 | 124.3057 | 124.3011 | 124.5346 | -0.46692 | -0.46234
1037.3906 | 124.5941 | -124.2462 | 0.16479 | 0.19394 | 0.021561 | 0.012529 | 0.022313 | 0.0044882 | -0.00025639 | 0.016836 | 0.073242 | 0.13733 | -0.2243 | 0.027466 | 0.045776 | 0.15564 | -0.16937 | 0.20142 | 0.16022 | -0.24719 | 124.0219 | -0.027466 | 124.3195 | 124.2737 | -0.11902 | 123.999 | -0.004578 | 0.29755 | 124.0768 | 124.4476 | 124.292 | 124.3835 | 124.3195 | 124.4064 | 124.4019 | 123.999 | 124.3835 | 124.3195 | 124.4019 | 124.292 | 124.4064 | -0.3891 | -0.41199
1038.375 | 124.4751 | -124.2966 | 0.2243 | 0.094757 | 0.025193 | 0.016374 | 0.027867 | 0.0014974 | -0.00046999 | 0.014913 | -0.027466 | 0.18768 | -0.27008 | -0.041199 | -0.022888 | -0.004578 | 0.013733 | 0.059509 | 0.23804 | -0.26093 | 124.0265 | -0.036621 | 124.2691 | 124.2554 | -0.24719 | 124.0356 | 0.013733 | 0.24262 | 124.3103 | 124.3561 | 124.2737 | 124.4843 | 124.2691 | 124.5346 | 124.292 | 124.0356 | 124.4843 | 124.2691 | 124.292 | 124.2737 | 124.5346 | -0.49439 | -0.48523
1039.375 | 124.5117 | -124.2783 | 0.21515 | -0.18753 | 0.025833 | 0.01317 | 0.028294 | 0.002352 | -0.0017518 | 0.014058 | 0.041199 | 0.19226 | -0.24719 | 0.036621 | 0.027466 | 0.032043 | 0.022888 | 0.17395 | 0.23346 | -0.24261 | 124.0311 | -0.022888 | 124.3195 | 124.3149 | -0.18768 | 124.0356 | 0.01831 | 0.28839 | 124.3011 | 124.4522 | 124.3057 | 124.4705 | 124.3195 | 124.5117 | 124.3103 | 124.0356 | 124.4705 | 124.3195 | 124.3103 | 124.3057 | 124.5117 | -0.46234 | -0.45776
1040.375 | 124.5026 | -124.2783 | 0.22888 | -0.080719 | 0.027115 | 0.022356 | 0.027867 | 0.0019248 | -0.0013244 | 0.015981 | 0.17853 | 0.20142 | -0.21057 | 0.045776 | 0.045776 | 0.041199 | 0.018311 | 0.14648 | 0.2655 | -0.20142 | 124.0677 | -0.027466 | 124.4568 | 124.324 | -0.18311 | 124.0768 | 0.036621 | 0.3891 | 124.2966 | 124.4247 | 124.324 | 124.4797 | 124.4568 | 124.5438 | 124.3195 | 124.0768 | 124.4797 | 124.4568 | 124.3195 | 124.324 | 124.5438 | -0.43945 | -0.4303
1041.375 | 124.5209 | -124.2783 | 0.19684 | -0.18753 | 0.027756 | 0.011888 | 0.02509 | 0.0038474 | 0.00059821 | 0.015127 | 0.036621 | 0.16479 | -0.26093 | 0.041199 | 0.050354 | 0.036621 | 0.018311 | 0.17395 | 0.22888 | -0.23804 | 124.0173 | -0.032043 | 124.3149 | 124.3195 | -0.14648 | 124.0402 | 0.032044 | 0.29755 | 124.2966 | 124.4522 | 124.3286 | 124.4431 | 124.3149 | 124.5071 | 124.3149 | 124.0402 | 124.4431 | 124.3149 | 124.3149 | 124.3286 | 124.5071 | -0.45776 | -0.43488
1042.3906 | 124.5438 | -124.2462 | 0.18768 | 0.094757 | 0.024338 | 0.014879 | 0.018895 | 0.00085662 | -0.00068359 | 0.016408 | 0.036621 | 0.12817 | -0.2243 | 0.036621 | 0.050354 | 0.10071 | -0.073242 | 0.1831 | 0.21057 | -0.20599 | 124.0219 | -0.059509 | 124.2828 | 124.2828 | -0.13733 | 124.0402 | 0.022888 | 0.26093 | 124.173 | 124.4293 | 124.2966 | 124.3744 | 124.2828 | 124.4568 | 124.3469 | 124.0402 | 124.3744 | 124.2828 | 124.3469 | 124.2966 | 124.4568 | -0.41199 | -0.39368
1043.375 | 124.498 | -124.2828 | 0.19226 | -0.057831 | 0.029679 | 0.016801 | 0.025731 | 0.0012838 | -0.00089719 | 0.015127 | 0.045776 | 0.16479 | -0.25635 | -0.004578 | -0.032043 | 0 | 0.027466 | 0.11902 | 0.21515 | -0.27008 | 124.0265 | -0.027466 | 124.3286 | 124.2783 | -0.2243 | 124.0128 | 0.022888 | 0.30212 | 124.3103 | 124.4019 | 124.2508 | 124.4476 | 124.3286 | 124.498 | 124.2828 | 124.0128 | 124.4476 | 124.3286 | 124.2828 | 124.2508 | 124.498 | -0.44861 | -0.46234
1044.375 | 124.4568 | -124.3057 | 0.2243 | 0.05661 | 0.030747 | 0.017015 | 0.024663 | 0.0014974 | -0.0028198 | 0.015554 | -0.032043 | 0.16479 | -0.2655 | -0.036621 | -0.045776 | -0.032043 | 0.064087 | 0.059509 | 0.2243 | -0.27466 | 124.0402 | -0.059509 | 124.2737 | 124.2691 | -0.27008 | 124.0311 | 0 | 0.23346 | 124.3698 | 124.3652 | 124.2599 | 124.4705 | 124.2737 | 124.53 | 124.2737 | 124.0311 | 124.4705 | 124.2737 | 124.2737 | 124.2599 | 124.53 | -0.48981 | -0.49896
1045.375 | 124.4888 | -124.3057 | 0.21057 | -0.06546 | 0.033524 | 0.016161 | 0.024449 | 0.0036336 | -0.00068359 | 0.016622 | 0.045776 | 0.17853 | -0.24719 | -0.004578 | -0.004578 | 0.004578 | 0.004578 | 0.10529 | 0.24719 | -0.25177 | 124.0585 | -0.032043 | 124.3515 | 124.3011 | -0.21515 | 124.054 | 0.036621 | 0.29297 | 124.3103 | 124.411 | 124.3011 | 124.4843 | 124.3515 | 124.5529 | 124.3103 | 124.054 | 124.4843 | 124.3515 | 124.3103 | 124.3011 | 124.5529 | -0.45776 | -0.46234
1046.375 | 124.5346 | -124.2966 | 0.19226 | 0.14053 | 0.028824 | 0.019579 | 0.021886 | 0.0032064 | -0.002179 | 0.016836 | 0.004578 | 0.16937 | -0.25635 | -0.004578 | 0.004578 | 0.022888 | -0.032043 | 0.11444 | 0.21973 | -0.25177 | 124.0402 | -0.022888 | 124.3011 | 124.292 | -0.18768 | 124.0448 | 0.027466 | 0.26093 | 124.2645 | 124.411 | 124.3011 | 124.4659 | 124.3011 | 124.5163 | 124.3195 | 124.0448 | 124.4659 | 124.3011 | 124.3195 | 124.3011 | 124.5163 | -0.44861 | -0.44403
1047.3906 | 124.5666 | -124.2371 | 0.20142 | 0.064239 | 0.02797 | 0.013811 | 0.016545 | 0.00042942 | -0.0015382 | 0.014913 | 0.050354 | 0.13275 | -0.23804 | 0.032043 | 0.068665 | 0.09613 | -0.07782 | 0.20599 | 0.21973 | -0.20142 | 123.999 | -0.068665 | 124.2874 | 124.2691 | -0.13275 | 124.0356 | 0.018311 | 0.28839 | 124.1592 | 124.4431 | 124.3057 | 124.3698 | 124.2874 | 124.4568 | 124.3332 | 124.0356 | 124.3698 | 124.2874 | 124.3332 | 124.3057 | 124.4568 | -0.43945 | -0.40283
1048.3906 | 124.6078 | -124.2462 | 0.17395 | 1.1247 | 0.03032 | 0.012743 | 0.018681 | 0.0027792 | 0.00017081 | 0.014272 | 0.1831 | 0.10071 | -0.22888 | 0.086975 | 0.07782 | 0.10529 | -0.15106 | 0.22888 | 0.17395 | -0.21057 | 124.0173 | -0.073242 | 124.4293 | 124.3332 | -0.09613 | 124.0356 | 0 | 0.41199 | 124.0952 | 124.4751 | 124.324 | 124.3469 | 124.4293 | 124.4202 | 124.3515 | 124.0356 | 124.3469 | 124.4293 | 124.3515 | 124.324 | 124.4202 | -0.40283 | -0.38452
1049.375 | 124.5621 | -124.2279 | 0.25635 | -0.057831 | 0.029892 | 0.02086 | 0.026585 | -0.00021158 | 0.00017081 | 0.016408 | 0.045776 | 0.17853 | -0.22888 | 0.036621 | 0.018311 | 0.018311 | 0 | 0.20142 | 0.25177 | -0.22888 | 123.999 | -0.07782 | 124.2737 | 124.2645 | -0.23804 | 123.999 | -0.004578 | 0.27466 | 124.2279 | 124.4293 | 124.2462 | 124.4064 | 124.2737 | 124.4797 | 124.2462 | 123.999 | 124.4064 | 124.2737 | 124.2462 | 124.2462 | 124.4797 | -0.48523 | -0.48523
1050.375 | 124.4843 | -124.3011 | 0.21515 | 0.16342 | 0.033524 | 0.018297 | 0.022526 | 0.0061972 | -0.0013244 | 0.013845 | -0.013733 | 0.17395 | -0.26093 | 0.086975 | 0.14648 | 0 | 0.082397 | 0.16479 | 0.24261 | -0.25177 | 124.0402 | -0.041199 | 124.2874 | 124.3881 | -0.068665 | 124.0494 | 0.027466 | 0.24719 | 124.3835 | 124.4659 | 124.4476 | 124.4751 | 124.2874 | 124.5438 | 124.3011 | 124.0494 | 124.4751 | 124.2874 | 124.3011 | 124.4476 | 124.5438 | -0.47607 | -0.46692
1051.375 | 124.5346 | -124.2828 | 0.18768 | -0.095978 | 0.032029 | 0.015733 | 0.02274 | 0.00342 | -0.0017518 | 0.014058 | 0.045776 | 0.16937 | -0.24719 | -0.018311 | -0.009155 | -0.018311 | 0.022888 | 0.11902 | 0.23346 | -0.27466 | 124.0356 | -0.01831 | 124.3286 | 124.2645 | -0.19684 | 124.0082 | 0.045776 | 0.29297 | 124.3057 | 124.4019 | 124.2737 | 124.4522 | 124.3286 | 124.5163 | 124.2645 | 124.0082 | 124.4522 | 124.3286 | 124.2645 | 124.2737 | 124.5163 | -0.43488 | -0.46234
1052.4531 | 124.5621 | -124.2783 | 0.20599 | 0.071869 | 0.029679 | 0.014238 | 0.013341 | 0.0032064 | -0.0030334 | 0.016836 | 0.018311 | 0.12817 | -0.21515 | 0.013733 | 0.022888 | 0.068665 | -0.050354 | 0.17395 | 0.20599 | -0.20599 | 124.0631 | -0.07782 | 124.2966 | 124.292 | -0.18311 | 124.0723 | 0 | 0.23346 | 124.2279 | 124.4522 | 124.3011 | 124.4064 | 124.2966 | 124.4843 | 124.3469 | 124.0723 | 124.4064 | 124.2966 | 124.3469 | 124.3011 | 124.4843 | -0.42114 | -0.41199
1053.375 | 124.6216 | -124.2554 | 0.1831 | 0.10239 | 0.030533 | 0.018297 | 0.018468 | 0.0010702 | -0.00046999 | 0.014486 | 0.091553 | 0.12817 | -0.21973 | 0.073242 | 0.073242 | 0.11444 | -0.13733 | 0.2243 | 0.20142 | -0.21057 | 124.0356 | -0.054931 | 124.3469 | 124.3286 | -0.10986 | 124.0448 | 0.018311 | 0.31128 | 124.118 | 124.4797 | 124.3286 | 124.3835 | 124.3469 | 124.4568 | 124.3698 | 124.0448 | 124.3835 | 124.3469 | 124.3698 | 124.3286 | 124.4568 | -0.40283 | -0.39368
1054.375 | 124.5026 | -124.3286 | 0.20599 | 0.37704 | 0.030106 | 0.012529 | 0.020177 | 0.0014974 | -0.00046999 | 0.014058 | 0.036621 | 0.18768 | -0.24719 | -0.041199 | -0.032043 | -0.018311 | 0.009155 | 0.09613 | 0.24261 | -0.27008 | 124.0814 | -0.018311 | 124.3652 | 124.2874 | -0.23804 | 124.0585 | 0.036621 | 0.28381 | 124.3378 | 124.4247 | 124.2966 | 124.5163 | 124.3652 | 124.5712 | 124.3103 | 124.0585 | 124.5163 | 124.3652 | 124.3103 | 124.2966 | 124.5712 | -0.45319 | -0.47608
1055.375 | 124.4888 | -124.3103 | 0.19684 | -0.034943 | 0.033097 | 0.017229 | 0.021245 | 0.0032064 | -0.0011108 | 0.014272 | 0.013733 | 0.16937 | -0.25635 | -0.018311 | -0.041199 | -0.027466 | 0.027466 | 0.10071 | 0.22888 | -0.26093 | 124.054 | -0.027465 | 124.324 | 124.292 | -0.23804 | 124.0494 | 0.032044 | 0.27008 | 124.3378 | 124.411 | 124.2691 | 124.4797 | 124.324 | 124.5392 | 124.2828 | 124.0494 | 124.4797 | 124.324 | 124.2828 | 124.2691 | 124.5392 | -0.45319 | -0.45776
1056.375 | 124.4614 | -124.2966 | 0.19684 | -0.012055 | 0.037155 | 0.018938 | 0.019322 | 0.0042746 | 0.0010254 | 0.014272 | 0.018311 | 0.18768 | -0.26093 | -0.022888 | -0.022888 | -0.018311 | 0.032043 | 0.086975 | 0.23346 | -0.25635 | 124.0356 | -0.009155 | 124.3149 | 124.2737 | -0.21973 | 124.0402 | 0.036621 | 0.27924 | 124.3286 | 124.3835 | 124.2737 | 124.4843 | 124.3149 | 124.53 | 124.2783 | 124.0402 | 124.4843 | 124.3149 | 124.2783 | 124.2737 | 124.53 | -0.45776 | -0.45319
1057.375 | 124.6445 | -124.2599 | 0.19226 | -0.14938 | 0.032456 | 0.015733 | 0.012273 | 0.0014974 | 0.0018798 | 0.016195 | 0.07782 | 0.16479 | -0.20142 | 0.09613 | 0.10529 | 0.14191 | -0.09613 | 0.28381 | 0.20599 | -0.21515 | 124.0585 | -0.027466 | 124.3378 | 124.3561 | -0.086975 | 124.0448 | 0.013733 | 0.27924 | 124.1638 | 124.5438 | 124.3652 | 124.4247 | 124.3378 | 124.4659 | 124.4019 | 124.0448 | 124.4247 | 124.3378 | 124.4019 | 124.3652 | 124.4659 | -0.39368 | -0.40741
1058.375 | 124.5941 | -124.2371 | 0.19226 | 0.23209 | 0.033951 | 0.017015 | 0.01804 | 0.00064302 | 0.00017081 | 0.013845 | 0.050354 | 0.15106 | -0.23804 | 0.086975 | 0.073242 | 0.11902 | -0.13275 | 0.21973 | 0.21057 | -0.2243 | 123.999 | -0.041199 | 124.2874 | 124.324 | -0.11902 | 124.0128 | 0.01831 | 0.28839 | 124.1043 | 124.4568 | 124.3103 | 124.3881 | 124.2874 | 124.4476 | 124.3561 | 124.0128 | 124.3881 | 124.2874 | 124.3561 | 124.3103 | 124.4476 | -0.4303 | -0.41656
1059.375 | 124.6124 | -124.2004 | 0.20142 | 0.064239 | 0.034165 | 0.016801 | 0.017186 | 0.00064302 | 0.0018798 | 0.014699 | 0.054932 | 0.091553 | -0.24719 | 0.068665 | 0.068665 | 0.1236 | -0.1236 | 0.21973 | 0.20142 | -0.21973 | 123.9532 | -0.10986 | 124.2554 | 124.2691 | -0.13275 | 123.9807 | 0 | 0.30212 | 124.0768 | 124.4202 | 124.2691 | 124.292 | 124.2554 | 124.4019 | 124.324 | 123.9807 | 124.292 | 124.2554 | 124.324 | 124.2691 | 124.4019 | -0.44861 | -0.42114
1060.375 | 124.585 | -124.2691 | 0.1831 | 0.15579 | 0.030533 | 0.021501 | 0.018468 | 0.0025656 | -0.0013244 | 0.014272 | 0.032043 | 0.16479 | -0.25635 | 0.036621 | 0.018311 | 0.054932 | -0.07782 | 0.15106 | 0.21973 | -0.24719 | 124.0128 | -0.01831 | 124.3011 | 124.3057 | -0.16479 | 124.0219 | 0.036622 | 0.28839 | 124.1913 | 124.4202 | 124.2874 | 124.4339 | 124.3011 | 124.4888 | 124.324 | 124.0219 | 124.4339 | 124.3011 | 124.324 | 124.2874 | 124.4888 | -0.43945 | -0.4303
1061.375 | 124.585 | -124.2416 | 0.19226 | 0.2092 | 0.033738 | 0.013383 | 0.018895 | 0.002352 | -0.0019654 | 0.016195 | 0.022888 | 0.15564 | -0.24261 | 0.050354 | 0.050354 | 0.068665 | -0.10071 | 0.19684 | 0.19226 | -0.22888 | 123.999 | -0.036621 | 124.2645 | 124.292 | -0.14191 | 124.0128 | 0 | 0.2655 | 124.1409 | 124.4385 | 124.292 | 124.3973 | 124.2645 | 124.4339 | 124.3103 | 124.0128 | 124.3973 | 124.2645 | 124.3103 | 124.292 | 124.4339 | -0.43488 | -0.42114
1062.375 | 124.617 | -124.2371 | 0.1831 | 0.17105 | 0.034806 | 0.017656 | 0.018468 | 0.0029928 | 0.00038461 | 0.015554 | 0.027466 | 0.15564 | -0.25177 | 0.073242 | 0.050354 | 0.09613 | -0.09613 | 0.21515 | 0.22888 | -0.21515 | 123.9853 | -0.027465 | 124.2645 | 124.3103 | -0.13275 | 124.0219 | 0.045777 | 0.27924 | 124.1409 | 124.4522 | 124.2874 | 124.3927 | 124.2645 | 124.4659 | 124.3332 | 124.0219 | 124.3927 | 124.2645 | 124.3332 | 124.2874 | 124.4659 | -0.43488 | -0.39825
1063.375 | 124.5392 | -124.292 | 0.20599 | 0.14053 | 0.035019 | 0.017229 | 0.0174 | 0.0014974 | 0.00081181 | 0.015981 | -0.004578 | 0.17395 | -0.25635 | 0.004578 | -0.004578 | 0.018311 | -0.027466 | 0.1236 | 0.23804 | -0.24719 | 124.0356 | -0.032044 | 124.2874 | 124.2966 | -0.21057 | 124.0448 | 0.032043 | 0.25177 | 124.2645 | 124.4156 | 124.2874 | 124.4659 | 124.2874 | 124.53 | 124.3103 | 124.0448 | 124.4659 | 124.2874 | 124.3103 | 124.2874 | 124.53 | -0.46234 | -0.45319
1064.375 | 124.6124 | -124.2325 | 0.19684 | 0.3389 | 0.034165 | 0.014879 | 0.018681 | -0.00085238 | -0.0013244 | 0.014486 | 0.07782 | 0.12817 | -0.22888 | 0.091553 | 0.073242 | 0.10986 | -0.13733 | 0.22888 | 0.21057 | -0.18768 | 124.0036 | -0.068664 | 124.3103 | 124.324 | -0.1236 | 124.0448 | 0.013733 | 0.3067 | 124.0952 | 124.4614 | 124.3057 | 124.3607 | 124.3103 | 124.4431 | 124.3423 | 124.0448 | 124.3607 | 124.3103 | 124.3423 | 124.3057 | 124.4431 | -0.42572 | -0.38452
1065.375 | 124.5941 | -124.2462 | 0.17395 | 0.11002 | 0.035446 | 0.01552 | 0.015904 | -0.00042518 | 0.00038461 | 0.014699 | 0.073242 | 0.14648 | -0.22888 | 0.07782 | 0.068665 | 0.11902 | -0.11902 | 0.23804 | 0.21057 | -0.20599 | 124.0173 | -0.027466 | 124.3195 | 124.324 | -0.10528 | 124.0402 | 0.036621 | 0.30212 | 124.1272 | 124.4843 | 124.3149 | 124.3927 | 124.3195 | 124.4568 | 124.3652 | 124.0402 | 124.3927 | 124.3195 | 124.3652 | 124.3149 | 124.4568 | -0.40283 | -0.37994
1066.375 | 124.5666 | -124.2325 | 0.19684 | 0.15579 | 0.031815 | 0.01082 | 0.01505 | -0.0017068 | -0.00068359 | 0.016408 | 0.041199 | 0.13275 | -0.21515 | 0.050354 | 0.041199 | 0.086975 | -0.059509 | 0.19226 | 0.21057 | -0.20599 | 124.0173 | -0.064087 | 124.2737 | 124.2828 | -0.15564 | 124.0265 | 0.013733 | 0.25635 | 124.173 | 124.4247 | 124.2737 | 124.3652 | 124.2737 | 124.4431 | 124.3195 | 124.0265 | 124.3652 | 124.2737 | 124.3195 | 124.2737 | 124.4431 | -0.41199 | -0.40283
1067.375 | 124.5804 | -124.3011 | 0.14648 | 0.033722 | 0.030106 | 0.014665 | 0.017827 | -0.0019206 | -0.002179 | 0.014486 | 0.013733 | 0.14191 | -0.2243 | 0.009155 | -0.10071 | 0.045776 | -0.24719 | 0.2243 | 0.16022 | -0.20142 | 124.0768 | -0.004577 | 124.3149 | 124.3103 | -0.24719 | 124.0997 | 0.013733 | 0.23804 | 124.054 | 124.5255 | 124.2004 | 124.4431 | 124.3149 | 124.4614 | 124.3469 | 124.0997 | 124.4431 | 124.3149 | 124.3469 | 124.2004 | 124.4614 | -0.37079 | -0.3479
1068.375 | 124.5117 | -124.2828 | 0.23804 | -0.18753 | 0.03032 | 0.0076156 | 0.0174 | 0.00042942 | -0.0013244 | 0.015981 | 0.009155 | 0.16479 | -0.24719 | 0.004578 | 0.018311 | 0.036621 | 0.064087 | 0.14191 | 0.26093 | -0.23346 | 124.0356 | -0.073242 | 124.292 | 124.2874 | -0.21973 | 124.0494 | 0.022888 | 0.25635 | 124.3469 | 124.4247 | 124.3011 | 124.4476 | 124.292 | 124.5438 | 124.3195 | 124.0494 | 124.4476 | 124.292 | 124.3195 | 124.3011 | 124.5438 | -0.48523 | -0.4715
1069.375 | 124.5941 | -124.2554 | 0.14648 | 0.12527 | 0.033524 | 0.012956 | 0.020177 | -0.00085238 | -0.0030334 | 0.014272 | 0.091553 | 0.1236 | -0.23346 | 0.09613 | 0.07782 | 0.16479 | -0.50354 | 0.07782 | 0.17395 | -0.21515 | 124.0219 | -0.022888 | 124.3469 | 124.3515 | -0.068664 | 124.0402 | 0.027466 | 0.32501 | 123.7518 | 124.3332 | 124.3332 | 124.379 | 124.3469 | 124.4293 | 124.4202 | 124.0402 | 124.379 | 124.3469 | 124.4202 | 124.3332 | 124.4293 | -0.37994 | -0.36163
1070.375 | 124.5758 | -124.2416 | 0.19684 | 0.12527 | 0.03096 | 0.014665 | 0.017186 | -0.0014932 | -0.002179 | 0.016195 | 0.059509 | 0.1236 | -0.22888 | 0.09613 | 0.059509 | 0.11444 | -0.1236 | 0.2243 | 0.19684 | -0.2243 | 124.0128 | -0.073242 | 124.3011 | 124.3378 | -0.13733 | 124.0173 | 0 | 0.28839 | 124.118 | 124.4659 | 124.3011 | 124.3652 | 124.3011 | 124.4385 | 124.3561 | 124.0173 | 124.3652 | 124.3011 | 124.3561 | 124.3011 | 124.4385 | -0.42572 | -0.42114
1071.375 | 124.585 | -124.2233 | 0.21515 | 0.10239 | 0.033524 | 0.018938 | 0.0174 | -0.001066 | -0.0011108 | 0.017476 | 0.064087 | 0.11902 | -0.21057 | 0.091553 | 0.068665 | 0.11444 | -0.10529 | 0.2243 | 0.19684 | -0.20142 | 124.0128 | -0.09613 | 124.2874 | 124.3149 | -0.14648 | 124.0219 | -0.018311 | 0.27466 | 124.118 | 124.4476 | 124.292 | 124.3423 | 124.2874 | 124.4202 | 124.3378 | 124.0219 | 124.3423 | 124.2874 | 124.3378 | 124.292 | 124.4202 | -0.42572 | -0.41657
1072.375 | 124.6078 | -124.2508 | 0.20142 | 0.087128 | 0.032029 | 0.018297 | 0.013982 | -0.0019206 | 0.001239 | 0.013845 | 0.064087 | 0.13733 | -0.20599 | 0.07782 | 0.082397 | 0.10986 | -0.11444 | 0.2243 | 0.20142 | -0.19684 | 124.0448 | -0.064087 | 124.3149 | 124.3286 | -0.11902 | 124.054 | 0 | 0.27008 | 124.1364 | 124.4751 | 124.3332 | 124.3881 | 124.3149 | 124.4522 | 124.3607 | 124.054 | 124.3881 | 124.3149 | 124.3607 | 124.3332 | 124.4522 | -0.40741 | -0.39825
1073.375 | 124.6033 | -124.2691 | 0.20142 | 0.70511 | 0.034165 | 0.011034 | 0.013768 | -0.0014932 | -0.0013244 | 0.015554 | 0.013733 | 0.09613 | -0.26093 | 0.041199 | 0.045776 | 0.086975 | -0.036621 | 0.20142 | 0.20142 | -0.21057 | 124.0082 | -0.10529 | 124.2828 | 124.3103 | -0.15564 | 124.0585 | 0 | 0.27466 | 124.2325 | 124.4705 | 124.3149 | 124.3652 | 124.2828 | 124.4705 | 124.3561 | 124.0585 | 124.3652 | 124.2828 | 124.3561 | 124.3149 | 124.4705 | -0.46234 | -0.41199
1074.375 | 124.6078 | -124.2783 | 0.22888 | -0.31723 | 0.033738 | 0.014665 | 0.01505 | -0.0023478 | -0.00068359 | 0.012136 | -0.036621 | 0.073242 | -0.23804 | 0.050354 | 0.032043 | 0.068665 | -0.050354 | 0.20142 | 0.21057 | -0.22888 | 124.0402 | -0.15564 | 124.2416 | 124.3286 | -0.19684 | 124.0494 | -0.018311 | 0.20142 | 124.2279 | 124.4797 | 124.3103 | 124.3515 | 124.2416 | 124.4888 | 124.3469 | 124.0494 | 124.3515 | 124.2416 | 124.3469 | 124.3103 | 124.4888 | -0.46692 | -0.45776
1075.375 | 124.6124 | -124.2371 | 0.20599 | -0.050202 | 0.032669 | 0.0082566 | 0.014836 | -0.0029886 | 0.0010254 | 0.014272 | 0.041199 | 0.14191 | -0.21973 | 0.086975 | 0.10529 | 0.1236 | -0.07782 | 0.26093 | 0.22888 | -0.21973 | 124.0173 | -0.064087 | 124.2783 | 124.324 | -0.10071 | 124.0173 | 0.022888 | 0.26093 | 124.1592 | 124.498 | 124.3423 | 124.379 | 124.2783 | 124.4659 | 124.3607 | 124.0173 | 124.379 | 124.2783 | 124.3607 | 124.3423 | 124.4659 | -0.42572 | -0.42572
1076.4531 | 124.5438 | -124.324 | 0.21973 | -0.18753 | 0.034592 | 0.017656 | 0.022526 | -0.00042518 | -0.0030334 | 0.013204 | 0 | 0.1831 | -0.26093 | 0.022888 | -0.018311 | -0.004578 | 0.054932 | 0.16022 | 0.23346 | -0.25177 | 124.0631 | -0.036622 | 124.324 | 124.3469 | -0.23804 | 124.0723 | 0.013732 | 0.26093 | 124.379 | 124.4843 | 124.3057 | 124.5071 | 124.324 | 124.5575 | 124.3195 | 124.0723 | 124.5071 | 124.324 | 124.3195 | 124.3057 | 124.5575 | -0.48065 | -0.4715
1077.375 | 124.5987 | -124.2462 | 0.19226 | 0.11002 | 0.03331 | 0.015092 | 0.016545 | -0.0012796 | -4.2788e-05 | 0.015554 | 0.064087 | 0.11902 | -0.2243 | 0.10071 | 0.07782 | 0.11444 | -0.11444 | 0.21515 | 0.20142 | -0.20142 | 124.0219 | -0.073242 | 124.3103 | 124.3469 | -0.11444 | 124.0448 | 0.009155 | 0.28839 | 124.1318 | 124.4614 | 124.324 | 124.3652 | 124.3103 | 124.4476 | 124.3607 | 124.0448 | 124.3652 | 124.3103 | 124.3607 | 124.324 | 124.4476 | -0.41656 | -0.39368
1078.375 | 124.6216 | -124.2416 | 0.19226 | -0.19516 | 0.033097 | 0.012102 | 0.017827 | -0.00021158 | -0.0030334 | 0.01534 | 0.073242 | 0.12817 | -0.2243 | 0.10986 | 0.10071 | 0.10529 | -0.064087 | 0.27008 | 0.20142 | -0.21515 | 124.0173 | -0.064087 | 124.3149 | 124.3515 | -0.091553 | 124.0265 | 0.009155 | 0.29755 | 124.1776 | 124.5117 | 124.3423 | 124.3698 | 124.3149 | 124.4431 | 124.3469 | 124.0265 | 124.3698 | 124.3149 | 124.3469 | 124.3423 | 124.4431 | -0.41656 | -0.40741
1079.375 | 124.5712 | -124.2645 | 0.19226 | 0.11002 | 0.034592 | 0.014879 | 0.014836 | 0.00042942 | 0.00038461 | 0.014913 | -0.004578 | 0.13275 | -0.21057 | 0.045776 | 0.050354 | 0.082397 | -0.050354 | 0.20142 | 0.20142 | -0.20142 | 124.054 | -0.05951 | 124.2599 | 124.3103 | -0.14191 | 124.0631 | 0.009155 | 0.20599 | 124.2142 | 124.4659 | 124.3149 | 124.3973 | 124.2599 | 124.4659 | 124.3469 | 124.0631 | 124.3973 | 124.2599 | 124.3469 | 124.3149 | 124.4659 | -0.40283 | -0.39368
1080.375 | 124.5666 | -124.2966 | 0.19684 | 0.12527 | 0.034165 | 0.015306 | 0.013554 | -0.0012796 | 0.001239 | 0.016195 | 0.009155 | 0.14648 | -0.21515 | 0.041199 | 0.050354 | 0.07782 | -0.068665 | 0.21515 | 0.19226 | -0.20142 | 124.0814 | -0.050354 | 124.3057 | 124.3378 | -0.14648 | 124.0952 | -0.004577 | 0.2243 | 124.2279 | 124.5117 | 124.3469 | 124.4431 | 124.3057 | 124.4888 | 124.3744 | 124.0952 | 124.4431 | 124.3057 | 124.3744 | 124.3469 | 124.4888 | -0.41199 | -0.39825
1081.4531 | 124.585 | -124.2554 | 0.21057 | -0.18753 | 0.033524 | 0.016161 | 0.013341 | -0.0014932 | -0.0013244 | 0.014272 | 0.068665 | 0.14191 | -0.2243 | 0.11902 | 0.09613 | 0.11444 | -0.036621 | 0.2655 | 0.20599 | -0.22888 | 124.0311 | -0.068664 | 124.324 | 124.3744 | -0.11444 | 124.0265 | -0.004577 | 0.29297 | 124.2188 | 124.5209 | 124.3515 | 124.3973 | 124.324 | 124.4614 | 124.3698 | 124.0265 | 124.3973 | 124.324 | 124.3698 | 124.3515 | 124.4614 | -0.43488 | -0.43945
1082.375 | 124.6262 | -124.2645 | 0.19684 | -0.16464 | 0.031815 | 0.009752 | 0.016118 | -0.001066 | -0.00089719 | 0.014699 | 0.041199 | 0.11902 | -0.2243 | 0.09613 | 0.09613 | 0.10986 | -0.068665 | 0.27466 | 0.19226 | -0.20142 | 124.0402 | -0.077819 | 124.3057 | 124.3607 | -0.10071 | 124.0631 | -0.004577 | 0.2655 | 124.1959 | 124.5392 | 124.3607 | 124.3835 | 124.3057 | 124.4568 | 124.3744 | 124.0631 | 124.3835 | 124.3057 | 124.3744 | 124.3607 | 124.4568 | -0.42114 | -0.39825
1083.375 | 124.5209 | -124.3057 | 0.23346 | -0.53848 | 0.034378 | 0.010606 | 0.017186 | -0.0021342 | -0.0028198 | 0.014058 | -0.032043 | 0.19684 | -0.25177 | 0.018311 | -0.009155 | 0.004578 | 0.09613 | 0.14648 | 0.23804 | -0.2655 | 124.054 | -0.036621 | 124.2737 | 124.324 | -0.24261 | 124.0402 | 0.004578 | 0.21973 | 124.4019 | 124.4522 | 124.2966 | 124.5026 | 124.2737 | 124.5438 | 124.3103 | 124.0402 | 124.5026 | 124.2737 | 124.3103 | 124.2966 | 124.5438 | -0.48523 | -0.49896
1084.375 | 124.585 | -124.2828 | 0.20599 | 0.49911 | 0.036728 | 0.014879 | 0.0127 | -0.0032022 | -0.0026062 | 0.01534 | 0.022888 | 0.082397 | -0.24719 | 0.022888 | 0.036621 | 0.082397 | -0.054932 | 0.19684 | 0.19226 | -0.21973 | 124.0356 | -0.1236 | 124.3057 | 124.3057 | -0.16937 | 124.0631 | -0.013733 | 0.27008 | 124.2279 | 124.4797 | 124.3195 | 124.3652 | 124.3057 | 124.4751 | 124.3652 | 124.0631 | 124.3652 | 124.3057 | 124.3652 | 124.3195 | 124.4751 | -0.45319 | -0.42572
1085.375 | 124.5666 | -124.3011 | 0.20599 | -0.042572 | 0.033738 | 0.015092 | 0.012913 | -0.0025614 | 0.0010254 | 0.014913 | -0.004578 | 0.10986 | -0.23804 | 0.022888 | 0.036621 | 0.073242 | -0.045776 | 0.21057 | 0.17853 | -0.2243 | 124.0631 | -0.096131 | 124.2966 | 124.324 | -0.16937 | 124.0768 | -0.027466 | 0.23346 | 124.2554 | 124.5117 | 124.3378 | 124.411 | 124.2966 | 124.4797 | 124.3744 | 124.0768 | 124.411 | 124.2966 | 124.3744 | 124.3378 | 124.4797 | -0.44403 | -0.4303
1086.375 | 124.6445 | -124.2508 | 0.17853 | -0.1265 | 0.033738 | 0.011461 | 0.011418 | -0.0012796 | -0.0011108 | 0.014699 | 0.050354 | 0.14191 | -0.21973 | 0.13275 | 0.11444 | 0.14648 | -0.10529 | 0.29297 | 0.19684 | -0.20599 | 124.0311 | -0.036621 | 124.3011 | 124.3835 | -0.064087 | 124.0448 | 0.01831 | 0.27008 | 124.1455 | 124.5438 | 124.3652 | 124.3927 | 124.3011 | 124.4476 | 124.3973 | 124.0448 | 124.3927 | 124.3011 | 124.3973 | 124.3652 | 124.4476 | -0.39826 | -0.38452
1087.375 | 124.5758 | -124.3011 | 0.15564 | 0.048981 | 0.032883 | 0.011675 | 0.0067185 | -0.0049112 | -0.00068359 | 0.015127 | 0.004578 | 0.11902 | -0.23346 | 0.032043 | 0.068665 | 0.050354 | -0.041199 | 0.16479 | 0.15106 | -0.21515 | 124.0677 | -0.036621 | 124.3057 | 124.3332 | -0.086975 | 124.086 | -0.004578 | 0.23804 | 124.2599 | 124.4659 | 124.3698 | 124.4202 | 124.3057 | 124.4522 | 124.3515 | 124.086 | 124.4202 | 124.3057 | 124.3515 | 124.3698 | 124.4522 | -0.3891 | -0.37079
1088.375 | 124.5483 | -124.2966 | 0.21057 | -0.23331 | 0.03566 | 0.017229 | 0.021458 | -0.0025614 | -0.0023926 | 0.014913 | 0.022888 | 0.14648 | -0.27924 | 0.073242 | 0.018311 | 0.036621 | 0.009155 | 0.17853 | 0.21057 | -0.25177 | 124.0173 | -0.064087 | 124.3195 | 124.3698 | -0.19226 | 124.0448 | 0 | 0.30212 | 124.3057 | 124.4751 | 124.3149 | 124.4431 | 124.3195 | 124.5071 | 124.3332 | 124.0448 | 124.4431 | 124.3195 | 124.3332 | 124.3149 | 124.5071 | -0.48981 | -0.46234
1089.375 | 124.6033 | -124.2691 | 0.19226 | -0.042572 | 0.031601 | 0.013811 | 0.012486 | -0.001066 | -0.0015382 | 0.015127 | 0.018311 | 0.14191 | -0.2243 | 0.064087 | 0.068665 | 0.086975 | -0.059509 | 0.23346 | 0.21973 | -0.2243 | 124.0448 | -0.050354 | 124.2874 | 124.3332 | -0.1236 | 124.0448 | 0.027466 | 0.24261 | 124.2096 | 124.5026 | 124.3378 | 124.411 | 124.2874 | 124.4888 | 124.3561 | 124.0448 | 124.411 | 124.2874 | 124.3561 | 124.3378 | 124.4888 | -0.41656 | -0.41656
1090.375 | 124.5804 | -124.2828 | 0.21515 | 0.026092 | 0.032242 | 0.0082566 | 0.015263 | -0.0014932 | -4.2788e-05 | 0.014486 | 0.004578 | 0.11902 | -0.24719 | 0.050354 | 0.050354 | 0.10071 | -0.050354 | 0.22888 | 0.21057 | -0.21057 | 124.0356 | -0.09613 | 124.2874 | 124.3332 | -0.16479 | 124.0723 | -0.004578 | 0.25177 | 124.2325 | 124.5117 | 124.3332 | 124.4019 | 124.2874 | 124.4934 | 124.3835 | 124.0723 | 124.4019 | 124.2874 | 124.3835 | 124.3332 | 124.4934 | -0.46234 | -0.42572
1091.375 | 124.6307 | -124.2599 | 0.20599 | -0.088349 | 0.03096 | 0.013597 | 0.013341 | -0.002775 | 0.00017081 | 0.014699 | 0.054932 | 0.14191 | -0.22888 | 0.10986 | 0.10071 | 0.11902 | -0.07782 | 0.27466 | 0.20142 | -0.20599 | 124.0311 | -0.064087 | 124.3149 | 124.3698 | -0.10529 | 124.054 | -0.004578 | 0.28381 | 124.1821 | 124.5346 | 124.3607 | 124.4019 | 124.3149 | 124.4614 | 124.379 | 124.054 | 124.4019 | 124.3149 | 124.379 | 124.3607 | 124.4614 | -0.43488 | -0.41199
1092.375 | 124.5895 | -124.2691 | 0.19684 | -0.057831 | 0.033951 | 0.014879 | 0.011845 | -0.0014932 | -0.0011108 | 0.016195 | -0.004578 | 0.09613 | -0.23346 | 0.059509 | 0.054932 | 0.068665 | -0.050354 | 0.20142 | 0.20599 | -0.21515 | 124.0356 | -0.10071 | 124.2645 | 124.3286 | -0.14191 | 124.054 | 0.009156 | 0.22888 | 124.2188 | 124.4705 | 124.324 | 124.3652 | 124.2645 | 124.4751 | 124.3378 | 124.054 | 124.3652 | 124.2645 | 124.3378 | 124.324 | 124.4751 | -0.4303 | -0.41199
1093.375 | 124.5987 | -124.2737 | 0.20142 | -0.06546 | 0.032883 | 0.011461 | 0.013554 | -0.0021342 | -0.0023926 | 0.013631 | 0.073242 | 0.10529 | -0.21973 | 0.10986 | 0.10986 | 0.12817 | -0.064087 | 0.28381 | 0.19226 | -0.20142 | 124.054 | -0.09613 | 124.3469 | 124.3835 | -0.091553 | 124.0723 | -0.009155 | 0.29297 | 124.2096 | 124.5575 | 124.3835 | 124.379 | 124.3469 | 124.4659 | 124.4019 | 124.0723 | 124.379 | 124.3469 | 124.4019 | 124.3835 | 124.4659 | -0.42114 | -0.40283
1094.375 | 124.649 | -124.2691 | 0.20142 | -0.06546 | 0.031815 | 0.012102 | 0.014195 | -0.0042704 | -0.0023926 | 0.01534 | 0.022888 | 0.13275 | -0.2243 | 0.086975 | 0.091553 | 0.11444 | -0.07782 | 0.25177 | 0.21057 | -0.21057 | 124.0448 | -0.068665 | 124.292 | 124.3561 | -0.10986 | 124.0585 | 0.009155 | 0.24719 | 124.1913 | 124.5209 | 124.3607 | 124.4019 | 124.292 | 124.4797 | 124.3835 | 124.0585 | 124.4019 | 124.292 | 124.3835 | 124.3607 | 124.4797 | -0.42572 | -0.41199
1095.375 | 124.6445 | -124.2783 | 0.21515 | -0.11124 | 0.031388 | 0.012743 | 0.012913 | -0.0040568 | -0.002179 | 0.014699 | 0.050354 | 0.14191 | -0.21057 | 0.12817 | 0.086975 | 0.11444 | -0.064087 | 0.27924 | 0.21057 | -0.19226 | 124.0677 | -0.073242 | 124.3286 | 124.4064 | -0.12817 | 124.086 | -0.004578 | 0.26093 | 124.2142 | 124.5575 | 124.3652 | 124.4202 | 124.3286 | 124.4888 | 124.3927 | 124.086 | 124.4202 | 124.3286 | 124.3927 | 124.3652 | 124.4888 | -0.42572 | -0.40741
1096.375 | 124.6124 | -124.2737 | 0.21515 | -0.080719 | 0.03096 | 0.0076156 | 0.012913 | -0.0023478 | -0.00025639 | 0.014699 | 0 | 0.14191 | -0.2243 | 0.068665 | 0.050354 | 0.082397 | -0.059509 | 0.23346 | 0.21057 | -0.21057 | 124.0494 | -0.073242 | 124.2737 | 124.3423 | -0.16479 | 124.0631 | -0.004578 | 0.2243 | 124.2142 | 124.5071 | 124.324 | 124.4156 | 124.2737 | 124.4843 | 124.3561 | 124.0631 | 124.4156 | 124.2737 | 124.3561 | 124.324 | 124.4843 | -0.43945 | -0.42572
1097.4375 | 124.6262 | -124.2828 | 0.21973 | 0.14816 | 0.034165 | 0.013383 | 0.019322 | 2.222e-06 | -4.2788e-05 | 0.014272 | 0.082397 | 0.10529 | -0.21057 | 0.11444 | 0.07782 | 0.10986 | -0.1236 | 0.24261 | 0.19226 | -0.20142 | 124.0723 | -0.11444 | 124.3652 | 124.3973 | -0.14191 | 124.0814 | -0.027466 | 0.29297 | 124.1592 | 124.5255 | 124.3607 | 124.3881 | 124.3652 | 124.4751 | 124.3927 | 124.0814 | 124.3881 | 124.3652 | 124.3927 | 124.3607 | 124.4751 | -0.4303 | -0.42114
1098.375 | 124.6536 | -124.2783 | 0.19226 | -0.1265 | 0.03032 | 0.01317 | 0.015263 | -0.0017068 | -0.0011108 | 0.014913 | 0.068665 | 0.10986 | -0.21973 | 0.11444 | 0.09613 | 0.1236 | -0.073242 | 0.27924 | 0.21057 | -0.21057 | 124.0585 | -0.082398 | 124.3469 | 124.3927 | -0.096131 | 124.0677 | 0.01831 | 0.28839 | 124.205 | 124.5575 | 124.3744 | 124.3881 | 124.3469 | 124.4888 | 124.4019 | 124.0677 | 124.3881 | 124.3469 | 124.4019 | 124.3744 | 124.4888 | -0.41199 | -0.40283
1099.375 | 124.6033 | -124.2508 | 0.20142 | -0.057831 | 0.029679 | 0.012529 | 0.013341 | -0.0034158 | -4.2788e-05 | 0.017049 | 0.022888 | 0.14648 | -0.2243 | 0.10529 | 0.09613 | 0.10529 | -0.064087 | 0.24261 | 0.20599 | -0.20142 | 124.0265 | -0.054932 | 124.2737 | 124.3561 | -0.10529 | 124.0494 | 0.004578 | 0.24719 | 124.1867 | 124.4934 | 124.3469 | 124.3973 | 124.2737 | 124.4568 | 124.3561 | 124.0494 | 124.3973 | 124.2737 | 124.3561 | 124.3469 | 124.4568 | -0.42572 | -0.40283
1100.375 | 124.6078 | -124.3103 | 0.14648 | -0.027313 | 0.032242 | 0.013597 | 0.015263 | -0.001066 | 0.0016662 | 0.014699 | 0.013733 | 0.12817 | -0.21515 | -0.14191 | 0.032043 | 0.036621 | -0.13275 | 0.20142 | 0.16022 | -0.21057 | 124.0952 | -0.01831 | 124.324 | 124.1684 | -0.11444 | 124.0997 | 0.013733 | 0.22888 | 124.1776 | 124.5117 | 124.3423 | 124.4385 | 124.324 | 124.4705 | 124.3469 | 124.0997 | 124.4385 | 124.324 | 124.3469 | 124.3423 | 124.4705 | -0.36163 | -0.35706
1101.375 | 124.5941 | -124.3973 | 0.16937 | 0.11002 | 0.031174 | 0.0086838 | 0.014836 | -0.002775 | -0.00025639 | 0.014272 | 0.009155 | 0.13733 | -0.21973 | 0.041199 | 0.050354 | 0.07782 | -0.059509 | 0.21515 | 0.22888 | -0.23804 | 124.1776 | -0.032044 | 124.4064 | 124.4385 | -0.11902 | 124.1592 | 0.059509 | 0.22888 | 124.3378 | 124.6124 | 124.4476 | 124.5346 | 124.4064 | 124.6262 | 124.4751 | 124.1592 | 124.5346 | 124.4064 | 124.4751 | 124.4476 | 124.6262 | -0.3891 | -0.40741
1102.375 | 124.585 | -124.2783 | 0.20599 | -0.10361 | 0.032456 | 0.017442 | 0.014622 | -0.0042704 | 0.00059821 | 0.014913 | 0.009155 | 0.11902 | -0.23804 | 0.054932 | 0.050354 | 0.082397 | -0.059509 | 0.21057 | 0.21057 | -0.20599 | 124.0402 | -0.086975 | 124.2874 | 124.3332 | -0.15564 | 124.0723 | 0.004577 | 0.24719 | 124.2188 | 124.4888 | 124.3286 | 124.3973 | 124.2874 | 124.4888 | 124.3607 | 124.0723 | 124.3973 | 124.2874 | 124.3607 | 124.3286 | 124.4888 | -0.44403 | -0.41199
1103.375 | 124.6307 | -124.2645 | 0.20142 | -0.15701 | 0.028824 | 0.011247 | 0.015904 | -0.004484 | -0.0011108 | 0.016408 | 0.032043 | 0.15106 | -0.21973 | 0.09613 | 0.091553 | 0.12817 | -0.073242 | 0.24261 | 0.18768 | -0.21057 | 124.0448 | -0.050354 | 124.2966 | 124.3607 | -0.10986 | 124.054 | -0.013733 | 0.25177 | 124.1913 | 124.5071 | 124.3561 | 124.4156 | 124.2966 | 124.4522 | 124.3927 | 124.054 | 124.4156 | 124.2966 | 124.3927 | 124.3561 | 124.4522 | -0.42114 | -0.41199
1104.375 | 124.6033 | -124.2783 | 0.1831 | -1.5913 | 0.034806 | 0.012743 | 0.014622 | -0.0042704 | 0.00017081 | 0.014913 | -0.054932 | 0.091553 | -0.24261 | 0.050354 | 0.022888 | 0.064087 | -0.032043 | 0.20599 | 0.16937 | -0.20599 | 124.0356 | -0.091552 | 124.2233 | 124.3286 | -0.16022 | 124.0723 | -0.013732 | 0.18768 | 124.2462 | 124.4843 | 124.3011 | 124.3698 | 124.2233 | 124.4476 | 124.3423 | 124.0723 | 124.3698 | 124.2233 | 124.3423 | 124.3011 | 124.4476 | -0.42572 | -0.3891
1105.375 | 124.6033 | -124.2737 | 0.15106 | -0.034943 | 0.029892 | 0.013383 | 0.011418 | 0.00064302 | -0.0013244 | 0.015127 | -0.004578 | 0.12817 | -0.23804 | 0.032043 | -0.022888 | 0.059509 | -0.091553 | 0.17395 | 0.15106 | -0.23346 | 124.0356 | -0.022888 | 124.2691 | 124.3057 | -0.17395 | 124.0402 | 0 | 0.23346 | 124.1821 | 124.4476 | 124.2508 | 124.4019 | 124.2691 | 124.4247 | 124.3332 | 124.0402 | 124.4019 | 124.2691 | 124.3332 | 124.2508 | 124.4247 | -0.3891 | -0.38452
1106.375 | 124.6353 | -124.2645 | 0.17395 | -0.24857 | 0.029465 | 0.0071884 | 0.016118 | -0.0021342 | -4.2788e-05 | 0.013845 | -0.054932 | 0.11902 | -0.22888 | 0.091553 | 0.15106 | 0.13275 | -0.091553 | 0.28839 | 0.20142 | -0.21973 | 124.0356 | -0.054931 | 124.2096 | 124.3561 | -0.022888 | 124.0448 | 0.027466 | 0.17395 | 124.173 | 124.5529 | 124.4156 | 124.3835 | 124.2096 | 124.4659 | 124.3973 | 124.0448 | 124.3835 | 124.2096 | 124.3973 | 124.4156 | 124.4659 | -0.40283 | -0.39368
1107.375 | 124.6445 | -124.2554 | 0.19226 | -0.06546 | 0.03032 | 0.013597 | 0.014195 | -0.0023478 | -4.2788e-05 | 0.015767 | 0.041199 | 0.13733 | -0.21973 | 0.12817 | 0.10986 | 0.13275 | -0.073242 | 0.27008 | 0.18768 | -0.17853 | 124.0356 | -0.054932 | 124.2966 | 124.3835 | -0.082398 | 124.0768 | -0.004578 | 0.26093 | 124.1821 | 124.5255 | 124.3652 | 124.3927 | 124.2966 | 124.4431 | 124.3881 | 124.0768 | 124.3927 | 124.2966 | 124.3881 | 124.3652 | 124.4431 | -0.41199 | -0.37079
1108.375 | 124.6399 | -124.2554 | 0.1831 | -0.012055 | 0.029038 | 0.017442 | 0.016545 | -0.0032022 | -0.0019654 | 0.01769 | 0.050354 | 0.13275 | -0.21973 | 0.10529 | 0.09613 | 0.1236 | -0.064087 | 0.2655 | 0.19684 | -0.18768 | 124.0356 | -0.050354 | 124.3057 | 124.3607 | -0.086975 | 124.0677 | 0.013733 | 0.27008 | 124.1913 | 124.5209 | 124.3515 | 124.3881 | 124.3057 | 124.4522 | 124.379 | 124.0677 | 124.3881 | 124.3057 | 124.379 | 124.3515 | 124.4522 | -0.40283 | -0.37079
1109.375 | 124.6536 | -124.2828 | 0.19226 | 0.23209 | 0.029892 | 0.013811 | 0.018254 | -0.0040568 | -0.0030334 | 0.015127 | 0 | 0.10986 | -0.23346 | 0.054932 | 0.059509 | 0.07782 | -0.054932 | 0.20142 | 0.20599 | -0.20599 | 124.0494 | -0.082398 | 124.2828 | 124.3378 | -0.13275 | 124.0768 | 0.013733 | 0.23346 | 124.2279 | 124.4843 | 124.3423 | 124.3927 | 124.2828 | 124.4888 | 124.3607 | 124.0768 | 124.3927 | 124.2828 | 124.3607 | 124.3423 | 124.4888 | -0.42572 | -0.39826
1110.375 | 124.6033 | -124.2966 | 0.19226 | -0.29434 | 0.029251 | 0.01552 | 0.016545 | -0.0019206 | -0.0013244 | 0.01299 | -0.032043 | 0.07782 | -0.24261 | 0.045776 | 0.050354 | 0.068665 | -0.050354 | 0.1831 | 0.19684 | -0.19684 | 124.054 | -0.11444 | 124.2645 | 124.3423 | -0.14191 | 124.0997 | 0.004577 | 0.21057 | 124.2462 | 124.4797 | 124.3469 | 124.3744 | 124.2645 | 124.4934 | 124.3652 | 124.0997 | 124.3744 | 124.2645 | 124.3652 | 124.3469 | 124.4934 | -0.43488 | -0.3891
1111.375 | 124.5941 | -124.3011 | 0.19684 | 0.12527 | 0.025833 | 0.012529 | 0.019963 | -0.00063878 | -0.00046999 | 0.016622 | 0.022888 | 0.14191 | -0.1831 | 0.054932 | 0.054932 | 0.059509 | -0.07782 | 0.19684 | 0.20599 | -0.19684 | 124.118 | -0.054931 | 124.324 | 124.3561 | -0.14191 | 124.1043 | 0.009156 | 0.20599 | 124.2233 | 124.498 | 124.3561 | 124.4431 | 124.324 | 124.5071 | 124.3607 | 124.1043 | 124.4431 | 124.324 | 124.3607 | 124.3561 | 124.5071 | -0.37994 | -0.39368
1112.375 | 124.5941 | -124.2966 | 0.18768 | 0.041351 | 0.02562 | 0.013597 | 0.016545 | -0.00021158 | -0.00089719 | 0.014913 | -0.25635 | 0.1236 | -0.24719 | 0.064087 | 0.022888 | 0.050354 | -0.07782 | 0.16937 | 0.15106 | -0.19226 | 124.0494 | -0.064087 | 124.0402 | 124.3607 | -0.16479 | 124.1043 | -0.036621 | -0.009156 | 124.2188 | 124.4659 | 124.3195 | 124.4202 | 124.0402 | 124.4476 | 124.3469 | 124.1043 | 124.4202 | 124.0402 | 124.3469 | 124.3195 | 124.4476 | -0.43488 | -0.37994
1113.375 | 124.6216 | -124.3011 | 0.14191 | 0.0032044 | 0.026261 | 0.011888 | 0.02039 | -0.0042704 | -0.00025639 | 0.016622 | 0.009155 | 0.14648 | -0.21973 | -0.045776 | 0.068665 | 0.073242 | -0.068665 | 0.19684 | 0.15106 | -0.21515 | 124.0814 | 0.004577 | 124.3103 | 124.2554 | -0.073242 | 124.086 | 0.009155 | 0.22888 | 124.2325 | 124.498 | 124.3698 | 124.4476 | 124.3103 | 124.4522 | 124.3744 | 124.086 | 124.4476 | 124.3103 | 124.3744 | 124.3698 | 124.4522 | -0.36163 | -0.35706
1114.375 | 124.6124 | -124.3057 | 0.13275 | -0.06546 | 0.026474 | 0.01317 | 0.020177 | -0.0021342 | 0.00038461 | 0.015981 | 0.004578 | 0.13275 | -0.2243 | -0.14648 | 0.022888 | 0.036621 | -0.086975 | 0.18768 | 0.13733 | -0.20142 | 124.0814 | 0 | 124.3103 | 124.1592 | -0.10986 | 124.1043 | 0.004578 | 0.22888 | 124.2188 | 124.4934 | 124.3286 | 124.4385 | 124.3103 | 124.4431 | 124.3423 | 124.1043 | 124.4385 | 124.3103 | 124.3423 | 124.3286 | 124.4431 | -0.35706 | -0.33417
1115.375 | 124.6262 | -124.2691 | 0.21515 | 0.033722 | 0.026688 | 0.01082 | 0.019963 | -0.0019206 | -0.00089719 | 0.014699 | 0.004578 | 0.14191 | -0.19684 | 0.073242 | 0.073242 | 0.09613 | -0.054932 | 0.21515 | 0.21057 | -0.20142 | 124.0723 | -0.073242 | 124.2737 | 124.3423 | -0.14191 | 124.0677 | -0.004578 | 0.20142 | 124.2142 | 124.4843 | 124.3423 | 124.411 | 124.2737 | 124.4797 | 124.3652 | 124.0677 | 124.411 | 124.2737 | 124.3652 | 124.3423 | 124.4797 | -0.41199 | -0.41657
1116.4375 | 124.6033 | -124.3011 | 0.17853 | 0.14816 | 0.027329 | 0.012529 | 0.028294 | -0.00085238 | 0.00059821 | 0.014699 | 0.018311 | 0.16022 | -0.23804 | 0.045776 | 0.027466 | 0.050354 | -0.059509 | 0.13733 | 0.20599 | -0.20142 | 124.0631 | -0.018311 | 124.3195 | 124.3469 | -0.15106 | 124.0997 | 0.027466 | 0.25635 | 124.2416 | 124.4385 | 124.3286 | 124.4614 | 124.3195 | 124.5071 | 124.3515 | 124.0997 | 124.4614 | 124.3195 | 124.3515 | 124.3286 | 124.5071 | -0.41656 | -0.37994
1117.375 | 124.6078 | -124.2783 | 0.20142 | -0.06546 | 0.026902 | 0.017015 | 0.019749 | 0.00042942 | -0.0013244 | 0.015554 | -0.018311 | 0.1236 | -0.21973 | 0.059509 | 0.064087 | 0.07782 | -0.041199 | 0.21515 | 0.20142 | -0.20142 | 124.0585 | -0.07782 | 124.2599 | 124.3378 | -0.13733 | 124.0768 | 0 | 0.20142 | 124.2371 | 124.4934 | 124.3423 | 124.4019 | 124.2599 | 124.4797 | 124.3561 | 124.0768 | 124.4019 | 124.2599 | 124.3561 | 124.3423 | 124.4797 | -0.42114 | -0.40283
1118.4375 | 124.585 | -124.2874 | 0.18768 | 0.11765 | 0.02562 | 0.01082 | 0.022313 | -0.0023478 | 0.00059821 | 0.015127 | 0.054932 | 0.12817 | -0.20142 | 0.082397 | 0.07782 | 0.09613 | -0.082397 | 0.19226 | 0.20599 | -0.19684 | 124.086 | -0.059509 | 124.3423 | 124.3698 | -0.10986 | 124.0906 | 0.018311 | 0.25635 | 124.205 | 124.4797 | 124.3652 | 124.4156 | 124.3423 | 124.4934 | 124.3835 | 124.0906 | 124.4156 | 124.3423 | 124.3835 | 124.3652 | 124.4934 | -0.3891 | -0.38452
1119.375 | 124.5941 | -124.292 | 0.17853 | -0.16464 | 0.023056 | 0.011461 | 0.021886 | -0.00085238 | -0.0019654 | 0.015554 | 0 | 0.11902 | -0.21973 | 0.050354 | 0.054932 | 0.07782 | -0.050354 | 0.20599 | 0.21515 | -0.1831 | 124.0723 | -0.059509 | 124.292 | 124.3423 | -0.1236 | 124.1089 | 0.036621 | 0.21973 | 124.2416 | 124.498 | 124.3469 | 124.411 | 124.292 | 124.5071 | 124.3698 | 124.1089 | 124.411 | 124.292 | 124.3698 | 124.3469 | 124.5071 | -0.39826 | -0.36163
1120.375 | 124.6719 | -124.2554 | 0.16937 | -0.23331 | 0.022629 | 0.014879 | 0.021672 | -0.0038432 | -0.00089719 | 0.017049 | 0.054932 | 0.1236 | -0.19226 | 0.14191 | 0.1236 | 0.15564 | -0.11444 | 0.29755 | 0.20142 | -0.19226 | 124.0631 | -0.045777 | 124.3103 | 124.3973 | -0.045777 | 124.0631 | 0.032043 | 0.24719 | 124.1409 | 124.5529 | 124.379 | 124.379 | 124.3103 | 124.4568 | 124.411 | 124.0631 | 124.379 | 124.3103 | 124.411 | 124.379 | 124.4568 | -0.36163 | -0.36163
1121.375 | 124.5758 | -124.2737 | 0.19226 | -0.569 | 0.026688 | 0.012956 | 0.02039 | -0.00063878 | -0.00025639 | 0.015767 | -0.054932 | 0.054932 | -0.23346 | 0.041199 | 0.050354 | 0.07782 | -0.045776 | 0.18768 | 0.19226 | -0.21515 | 124.0402 | -0.13733 | 124.2188 | 124.3149 | -0.14191 | 124.0585 | 0 | 0.17853 | 124.2279 | 124.4614 | 124.324 | 124.3286 | 124.2188 | 124.4659 | 124.3515 | 124.0585 | 124.3286 | 124.2188 | 124.3515 | 124.324 | 124.4659 | -0.42572 | -0.40741
1122.375 | 124.6262 | -124.2645 | 0.19684 | -0.07309 | 0.022202 | 0.013597 | 0.022526 | -0.002775 | 0.00059821 | 0.016195 | 0.027466 | 0.13733 | -0.21057 | 0.086975 | 0.091553 | 0.11444 | -0.064087 | 0.23346 | 0.20142 | -0.19226 | 124.054 | -0.059509 | 124.292 | 124.3515 | -0.10529 | 124.0723 | 0.004578 | 0.23804 | 124.2004 | 124.498 | 124.3561 | 124.4019 | 124.292 | 124.4659 | 124.379 | 124.0723 | 124.4019 | 124.292 | 124.379 | 124.3561 | 124.4659 | -0.40741 | -0.3891
1123.4375 | 124.5346 | -124.3011 | 0.20142 | 0.12527 | 0.026902 | 0.015733 | 0.028081 | -0.0025614 | -0.0017518 | 0.01534 | 0.009155 | 0.16479 | -0.26093 | 0.022888 | -0.013733 | 0.004578 | -0.009155 | 0.10986 | 0.2243 | -0.21973 | 124.0402 | -0.036621 | 124.3103 | 124.324 | -0.21515 | 124.0814 | 0.022888 | 0.27008 | 124.292 | 124.411 | 124.2874 | 124.4659 | 124.3103 | 124.5255 | 124.3057 | 124.0814 | 124.4659 | 124.3103 | 124.3057 | 124.2874 | 124.5255 | -0.46234 | -0.42114
1124.375 | 124.5895 | -124.2737 | 0.16022 | -0.057831 | 0.024338 | 0.0082566 | 0.020817 | -0.00085238 | -0.00025639 | 0.014058 | -0.23804 | 0.11444 | -0.23346 | 0.036621 | 0.059509 | 0.032043 | -0.054932 | 0.18768 | 0.15106 | -0.20142 | 124.0402 | -0.045776 | 124.0356 | 124.3103 | -0.10071 | 124.0723 | -0.009155 | -0.004578 | 124.2188 | 124.4614 | 124.3332 | 124.3881 | 124.0356 | 124.4247 | 124.3057 | 124.0723 | 124.3881 | 124.0356 | 124.3057 | 124.3332 | 124.4247 | -0.39368 | -0.36163
1125.4375 | 124.5071 | -124.3378 | 0.19684 | -0.019684 | 0.02797 | 0.016588 | 0.031712 | 0.0021384 | -0.00068359 | 0.013631 | 0.027466 | 0.15564 | -0.25177 | 0.004578 | -0.018311 | -0.004578 | 0.027466 | 0.10071 | 0.20142 | -0.24261 | 124.086 | -0.041198 | 124.3652 | 124.3423 | -0.21515 | 124.0952 | 0.004578 | 0.27924 | 124.3652 | 124.4385 | 124.3195 | 124.4934 | 124.3652 | 124.5392 | 124.3332 | 124.0952 | 124.4934 | 124.3652 | 124.3332 | 124.3195 | 124.5392 | -0.44861 | -0.43945
1126.375 | 124.617 | -124.2966 | 0.19684 | -0.050202 | 0.024765 | 0.010179 | 0.022526 | -0.00085238 | -0.0011108 | 0.015981 | -0.013733 | 0.14191 | -0.21515 | 0.068665 | 0.07782 | 0.10071 | -0.068665 | 0.22888 | 0.20142 | -0.1831 | 124.0814 | -0.054931 | 124.2828 | 124.3652 | -0.11902 | 124.1135 | 0.004578 | 0.20142 | 124.2279 | 124.5255 | 124.3744 | 124.4385 | 124.2828 | 124.498 | 124.3973 | 124.1135 | 124.4385 | 124.2828 | 124.3973 | 124.3744 | 124.498 | -0.41199 | -0.37994
1127.375 | 124.6216 | -124.292 | 0.19226 | -0.06546 | 0.024338 | 0.011034 | 0.023167 | -0.0012796 | -0.0030334 | 0.014913 | 0.004578 | 0.14648 | -0.23346 | 0.073242 | 0.073242 | 0.09613 | -0.050354 | 0.22888 | 0.20142 | -0.19226 | 124.0585 | -0.045777 | 124.2966 | 124.3652 | -0.11902 | 124.0997 | 0.009155 | 0.23804 | 124.2416 | 124.5209 | 124.3652 | 124.4385 | 124.2966 | 124.4934 | 124.3881 | 124.0997 | 124.4385 | 124.2966 | 124.3881 | 124.3652 | 124.4934 | -0.42572 | -0.38452
1128.375 | 124.6307 | -124.2828 | 0.18768 | -0.012055 | 0.021347 | 0.011034 | 0.024449 | -0.0021342 | -0.0013244 | 0.015554 | 0.013733 | 0.11902 | -0.21057 | 0.059509 | 0.059509 | 0.086975 | -0.045776 | 0.21057 | 0.19684 | -0.19684 | 124.0723 | -0.068664 | 124.2966 | 124.3423 | -0.12817 | 124.086 | 0.009155 | 0.2243 | 124.2371 | 124.4934 | 124.3423 | 124.4019 | 124.2966 | 124.4797 | 124.3698 | 124.086 | 124.4019 | 124.2966 | 124.3698 | 124.3423 | 124.4797 | -0.39825 | -0.38452
1129.375 | 124.649 | -124.2691 | 0.18768 | -0.080719 | 0.022629 | 0.01552 | 0.024876 | -0.0042704 | 0.0010254 | 0.013631 | 0.054932 | 0.14191 | -0.19684 | 0.10986 | 0.10071 | 0.13275 | -0.082397 | 0.27466 | 0.20599 | -0.1831 | 124.0723 | -0.045776 | 124.324 | 124.379 | -0.086975 | 124.086 | 0.018311 | 0.25177 | 124.1867 | 124.5438 | 124.3698 | 124.411 | 124.324 | 124.4751 | 124.4019 | 124.086 | 124.411 | 124.324 | 124.4019 | 124.3698 | 124.4751 | -0.38452 | -0.37079
1130.375 | 124.6582 | -124.2828 | 0.19226 | -0.080719 | 0.022202 | 0.011675 | 0.023381 | -0.0017068 | -0.0017518 | 0.016195 | 0.041199 | 0.12817 | -0.21057 | 0.091553 | 0.11444 | 0.1236 | -0.082397 | 0.27008 | 0.20142 | -0.17395 | 124.0723 | -0.064087 | 124.324 | 124.3744 | -0.07782 | 124.1089 | 0.009155 | 0.25177 | 124.2004 | 124.5529 | 124.3973 | 124.411 | 124.324 | 124.4843 | 124.4064 | 124.1089 | 124.411 | 124.324 | 124.4064 | 124.3973 | 124.4843 | -0.40283 | -0.36621
1131.375 | 124.5987 | -124.2645 | 0.18768 | 0.0032044 | 0.021775 | 0.014665 | 0.023808 | -0.00085238 | 0.00017081 | 0.015554 | 0.018311 | 0.10071 | -0.23804 | 0.050354 | 0.045776 | 0.07782 | -0.041199 | 0.20599 | 0.21057 | -0.20142 | 124.0265 | -0.086975 | 124.2828 | 124.3149 | -0.14191 | 124.0631 | 0.022888 | 0.25635 | 124.2233 | 124.4705 | 124.3103 | 124.3652 | 124.2828 | 124.4751 | 124.3423 | 124.0631 | 124.3652 | 124.2828 | 124.3423 | 124.3103 | 124.4751 | -0.42572 | -0.3891
1132.375 | 124.585 | -124.3057 | 0.20599 | -0.18753 | 0.026047 | 0.011247 | 0.022954 | -0.002775 | -0.0019654 | 0.014486 | -0.022888 | 0.091553 | -0.24261 | 0.041199 | 0.059509 | 0.073242 | -0.050354 | 0.19684 | 0.20142 | -0.19226 | 124.0631 | -0.11444 | 124.2828 | 124.3469 | -0.14649 | 124.1135 | -0.004578 | 0.21973 | 124.2554 | 124.5026 | 124.3652 | 124.3973 | 124.2828 | 124.5071 | 124.379 | 124.1135 | 124.3973 | 124.2828 | 124.379 | 124.3652 | 124.5071 | -0.44861 | -0.39826
1133.4375 | 124.617 | -124.2783 | 0.19684 | 0.10239 | 0.023484 | 0.018083 | 0.028722 | -0.0012796 | -0.00025639 | 0.014913 | 0.064087 | 0.1236 | -0.21515 | 0.091553 | 0.082397 | 0.10986 | -0.10071 | 0.22888 | 0.17853 | -0.17395 | 124.0631 | -0.073242 | 124.3423 | 124.3698 | -0.11444 | 124.1043 | -0.01831 | 0.27924 | 124.1776 | 124.5071 | 124.3607 | 124.4019 | 124.3423 | 124.4568 | 124.3881 | 124.1043 | 124.4019 | 124.3423 | 124.3881 | 124.3607 | 124.4568 | -0.41199 | -0.37079
1134.375 | 124.6628 | -124.2828 | 0.20142 | -0.095978 | 0.021347 | 0.014879 | 0.024235 | -0.0017068 | -0.00068359 | 0.015767 | 0.013733 | 0.14648 | -0.23804 | 0.07782 | 0.07782 | 0.10071 | -0.050354 | 0.24719 | 0.21057 | -0.17853 | 124.0448 | -0.054932 | 124.2966 | 124.3607 | -0.1236 | 124.1043 | 0.009155 | 0.25177 | 124.2325 | 124.53 | 124.3607 | 124.4293 | 124.2966 | 124.4934 | 124.3835 | 124.1043 | 124.4293 | 124.2966 | 124.3835 | 124.3607 | 124.4934 | -0.43945 | -0.37994
1135.375 | 124.6353 | -124.2783 | 0.19684 | 0.010834 | 0.021988 | 0.010393 | 0.026158 | -0.0023478 | -0.00068359 | 0.013631 | 0.018311 | 0.12817 | -0.22888 | 0.073242 | 0.054932 | 0.091553 | -0.064087 | 0.2243 | 0.19226 | -0.20142 | 124.0494 | -0.068664 | 124.2966 | 124.3515 | -0.14191 | 124.0768 | -0.004577 | 0.24719 | 124.2142 | 124.5026 | 124.3332 | 124.4064 | 124.2966 | 124.4705 | 124.3698 | 124.0768 | 124.4064 | 124.2966 | 124.3698 | 124.3332 | 124.4705 | -0.42572 | -0.39825
1136.375 | 124.6399 | -124.2737 | 0.16937 | -0.16464 | 0.020707 | 0.011888 | 0.024663 | -0.0021342 | -0.00046999 | 0.016195 | 0.086975 | 0.1236 | -0.20599 | 0.2655 | 0.2243 | 0.091553 | -0.15564 | 0.38452 | 0.20599 | -0.20599 | 124.0677 | -0.045777 | 124.3607 | 124.5392 | 0.054931 | 124.0677 | 0.036621 | 0.29297 | 124.118 | 124.6582 | 124.498 | 124.3973 | 124.3607 | 124.4797 | 124.3652 | 124.0677 | 124.3973 | 124.3607 | 124.3652 | 124.498 | 124.4797 | -0.37537 | -0.37537
1137.375 | 124.649 | -124.2691 | 0.19684 | -0.21042 | 0.020279 | 0.012102 | 0.024235 | -0.001066 | -0.002179 | 0.01534 | 0.041199 | 0.14191 | -0.21515 | 0.10071 | 0.091553 | 0.12817 | -0.059509 | 0.25635 | 0.21973 | -0.19226 | 124.054 | -0.054931 | 124.3103 | 124.3698 | -0.10529 | 124.0768 | 0.022889 | 0.25635 | 124.2096 | 124.5255 | 124.3607 | 124.411 | 124.3103 | 124.4888 | 124.3973 | 124.0768 | 124.411 | 124.3103 | 124.3973 | 124.3607 | 124.4888 | -0.41199 | -0.3891
1138.3906 | 124.5666 | -124.3378 | 0.21973 | -0.27908 | 0.02562 | 0.017229 | 0.033208 | -0.00063878 | -0.0019654 | 0.012777 | 0.018311 | 0.16022 | -0.25177 | 0.045776 | 0.018311 | 0.022888 | 0.036621 | 0.17395 | 0.21057 | -0.23804 | 124.086 | -0.05951 | 124.3561 | 124.3835 | -0.20142 | 124.0997 | -0.009156 | 0.27008 | 124.3744 | 124.5117 | 124.3561 | 124.498 | 124.3561 | 124.5483 | 124.3607 | 124.0997 | 124.498 | 124.3561 | 124.3607 | 124.3561 | 124.5483 | -0.4715 | -0.45776
1139.375 | 124.5941 | -124.2966 | 0.19684 | -1.9804 | 0.026261 | 0.011034 | 0.021031 | -0.00085238 | -0.00068359 | 0.014486 | -0.086975 | 0.091553 | -0.25177 | 0.022888 | 0.013733 | 0.064087 | -0.041199 | 0.19684 | 0.16937 | -0.19684 | 124.0448 | -0.10529 | 124.2096 | 124.3195 | -0.18311 | 124.0997 | -0.027465 | 0.16479 | 124.2554 | 124.4934 | 124.3103 | 124.3881 | 124.2096 | 124.4659 | 124.3607 | 124.0997 | 124.3881 | 124.2096 | 124.3607 | 124.3103 | 124.4659 | -0.44861 | -0.39368
1140.375 | 124.617 | -124.2737 | 0.19684 | -0.034943 | 0.021561 | 0.011247 | 0.023167 | -0.0012796 | -0.0028198 | 0.015981 | 0.004578 | 0.13275 | -0.21057 | 0.064087 | 0.068665 | 0.091553 | -0.045776 | 0.22888 | 0.19684 | -0.20599 | 124.0631 | -0.064087 | 124.2783 | 124.3378 | -0.12817 | 124.0677 | 0 | 0.21515 | 124.2279 | 124.5026 | 124.3423 | 124.4064 | 124.2783 | 124.4705 | 124.3652 | 124.0677 | 124.4064 | 124.2783 | 124.3652 | 124.3423 | 124.4705 | -0.40741 | -0.40283
1141.375 | 124.6353 | -124.2828 | 0.19684 | -0.034943 | 0.020493 | 0.017442 | 0.027226 | -0.002775 | -4.2788e-05 | 0.014699 | 0 | 0.14191 | -0.22888 | 0.050354 | 0.064087 | 0.091553 | -0.054932 | 0.21973 | 0.21057 | -0.18768 | 124.054 | -0.054931 | 124.2828 | 124.3332 | -0.13275 | 124.0952 | 0.013733 | 0.22888 | 124.2279 | 124.5026 | 124.3469 | 124.4247 | 124.2828 | 124.4934 | 124.3744 | 124.0952 | 124.4247 | 124.2828 | 124.3744 | 124.3469 | 124.4934 | -0.42572 | -0.38452
1142.375 | 124.617 | -124.2508 | 0.18768 | -0.14175 | 0.020493 | 0.01082 | 0.02274 | -0.0019206 | -0.0030334 | 0.013631 | 0.041199 | 0.13275 | -0.23804 | 0.10071 | 0.086975 | 0.12817 | -0.068665 | 0.26093 | 0.21057 | -0.16937 | 124.0128 | -0.054932 | 124.292 | 124.3515 | -0.10071 | 124.0814 | 0.022888 | 0.27924 | 124.1821 | 124.5117 | 124.3378 | 124.3835 | 124.292 | 124.4614 | 124.379 | 124.0814 | 124.3835 | 124.292 | 124.379 | 124.3378 | 124.4614 | -0.42572 | -0.35706
1143.375 | 124.5575 | -124.3378 | 0.20142 | -0.21042 | 0.024124 | 0.012315 | 0.033208 | 0.0010702 | -0.0041016 | 0.013631 | -0.009155 | 0.16022 | -0.2655 | 0.022888 | 0.004578 | 0.004578 | 0.073242 | 0.16022 | 0.21515 | -0.2243 | 124.0723 | -0.041199 | 124.3286 | 124.3607 | -0.19684 | 124.1135 | 0.013733 | 0.25635 | 124.411 | 124.498 | 124.3423 | 124.498 | 124.3286 | 124.5529 | 124.3423 | 124.1135 | 124.498 | 124.3286 | 124.3423 | 124.3423 | 124.5529 | -0.46692 | -0.42572
1144.375 | 124.6307 | -124.2966 | 0.19684 | -0.080719 | 0.02092 | 0.018083 | 0.025944 | -0.0025614 | -0.0015382 | 0.015554 | 0.027466 | 0.13733 | -0.2243 | 0.068665 | 0.07782 | 0.10071 | -0.050354 | 0.23804 | 0.21515 | -0.20142 | 124.0723 | -0.059509 | 124.324 | 124.3652 | -0.11902 | 124.0952 | 0.018311 | 0.25177 | 124.2462 | 124.5346 | 124.3744 | 124.4339 | 124.324 | 124.5117 | 124.3973 | 124.0952 | 124.4339 | 124.324 | 124.3973 | 124.3744 | 124.5117 | -0.42114 | -0.39825
1145.375 | 124.6033 | -124.3286 | 0.16022 | 0.041351 | 0.020066 | 0.013597 | 0.026585 | -0.00063878 | -4.2788e-05 | 0.013845 | 0.009155 | 0.13733 | -0.22888 | -0.009155 | 0.009155 | 0.086975 | -0.073242 | 0.19226 | 0.15106 | -0.21057 | 124.0997 | -0.022888 | 124.3378 | 124.3195 | -0.15106 | 124.118 | -0.009155 | 0.23804 | 124.2554 | 124.5209 | 124.3378 | 124.4659 | 124.3378 | 124.4797 | 124.4156 | 124.118 | 124.4659 | 124.3378 | 124.4156 | 124.3378 | 124.4797 | -0.3891 | -0.37079
1146.375 | 124.5483 | -124.3469 | 0.11902 | 0.041351 | 0.018784 | 0.0088974 | 0.026799 | -0.0014932 | 0.0014526 | 0.01534 | 0.009155 | 0.13275 | -0.20599 | 0.064087 | -0.17853 | -0.004578 | -0.29297 | 0.07782 | 0.16022 | -0.21515 | 124.1409 | 0.013732 | 124.3561 | 124.411 | -0.29755 | 124.1318 | 0.041198 | 0.21515 | 124.054 | 124.4247 | 124.1684 | 124.4797 | 124.3561 | 124.5071 | 124.3423 | 124.1318 | 124.4797 | 124.3561 | 124.3423 | 124.1684 | 124.5071 | -0.32501 | -0.33417
1147.375 | 124.6124 | -124.3011 | 0.18768 | -0.050202 | 0.020707 | 0.009111 | 0.027013 | -0.0032022 | -0.00089719 | 0.015554 | 0.013733 | 0.1236 | -0.23804 | 0.050354 | 0.064087 | 0.068665 | -0.054932 | 0.19684 | 0.20142 | -0.19684 | 124.0631 | -0.064087 | 124.3149 | 124.3515 | -0.1236 | 124.1043 | 0.013733 | 0.25177 | 124.2462 | 124.498 | 124.3652 | 124.4247 | 124.3149 | 124.5026 | 124.3698 | 124.1043 | 124.4247 | 124.3149 | 124.3698 | 124.3652 | 124.5026 | -0.42572 | -0.38452
1148.3906 | 124.5804 | -124.3332 | 0.19684 | -0.24094 | 0.021988 | 0.015306 | 0.032994 | -0.00021158 | -0.0026062 | 0.013204 | 0.009155 | 0.15564 | -0.25635 | 0.022888 | 0.013733 | 0.018311 | 0.045776 | 0.15564 | 0.19684 | -0.23346 | 124.0768 | -0.041198 | 124.3423 | 124.3561 | -0.18311 | 124.0997 | 0 | 0.2655 | 124.379 | 124.4888 | 124.3469 | 124.4888 | 124.3423 | 124.53 | 124.3515 | 124.0997 | 124.4888 | 124.3423 | 124.3515 | 124.3469 | 124.53 | -0.45319 | -0.4303
1149.375 | 124.5987 | -124.2828 | 0.19684 | 1.2773 | 0.024552 | 0.014452 | 0.024876 | -0.0012796 | -4.2788e-05 | 0.014272 | 0.013733 | 0.059509 | -0.24719 | 0.027466 | 0.059509 | 0.068665 | -0.045776 | 0.1831 | 0.17853 | -0.20599 | 124.0356 | -0.13733 | 124.2966 | 124.3103 | -0.13733 | 124.0768 | -0.01831 | 0.26093 | 124.2371 | 124.4659 | 124.3423 | 124.3423 | 124.2966 | 124.4614 | 124.3515 | 124.0768 | 124.3423 | 124.2966 | 124.3515 | 124.3423 | 124.4614 | -0.44403 | -0.40283
1150.375 | 124.5987 | -124.2966 | 0.19684 | 0.018463 | 0.020279 | 0.016161 | 0.026585 | -0.0019206 | -0.00089719 | 0.014486 | 0 | 0.13275 | -0.21515 | 0.050354 | 0.064087 | 0.091553 | -0.045776 | 0.21057 | 0.21057 | -0.19226 | 124.0814 | -0.064087 | 124.2966 | 124.3469 | -0.13275 | 124.1043 | 0.013733 | 0.21515 | 124.2508 | 124.5071 | 124.3607 | 124.4293 | 124.2966 | 124.5071 | 124.3881 | 124.1043 | 124.4293 | 124.2966 | 124.3881 | 124.3607 | 124.5071 | -0.41199 | -0.3891
1151.375 | 124.6033 | -124.3011 | 0.19226 | -0.07309 | 0.018357 | 0.016374 | 0.025304 | -0.001066 | 0.00038461 | 0.014913 | -0.009155 | 0.10986 | -0.21973 | 0.050354 | 0.054932 | 0.059509 | -0.036621 | 0.20599 | 0.19684 | -0.19226 | 124.0814 | -0.082398 | 124.292 | 124.3515 | -0.13733 | 124.1089 | 0.004577 | 0.21057 | 124.2645 | 124.5071 | 124.3561 | 124.411 | 124.292 | 124.498 | 124.3607 | 124.1089 | 124.411 | 124.292 | 124.3607 | 124.3561 | 124.498 | -0.41199 | -0.38452
1152.375 | 124.5941 | -124.2737 | 0.19684 | 0.1329 | 0.021134 | 0.017015 | 0.027226 | -0.001066 | -4.2788e-05 | 0.015554 | 0.036621 | 0.11444 | -0.21973 | 0.07782 | 0.064087 | 0.07782 | -0.073242 | 0.21515 | 0.19226 | -0.19684 | 124.054 | -0.082397 | 124.3103 | 124.3515 | -0.13275 | 124.0768 | -0.004577 | 0.25635 | 124.2004 | 124.4888 | 124.3378 | 124.3881 | 124.3103 | 124.4659 | 124.3515 | 124.0768 | 124.3881 | 124.3103 | 124.3515 | 124.3378 | 124.4659 | -0.41657 | -0.39368
1153.375 | 124.649 | -124.2737 | 0.17853 | 0.49149 | 0.018143 | 0.009752 | 0.027653 | -0.0025614 | -0.00068359 | 0.014913 | 0.091553 | 0.10071 | -0.21515 | 0.10529 | 0.13275 | 0.13275 | -0.07782 | 0.28381 | 0.17853 | -0.20142 | 124.0585 | -0.07782 | 124.3652 | 124.379 | -0.045777 | 124.0723 | 0 | 0.3067 | 124.1959 | 124.5575 | 124.4064 | 124.3744 | 124.3652 | 124.4522 | 124.4064 | 124.0723 | 124.3744 | 124.3652 | 124.4064 | 124.4064 | 124.4522 | -0.39368 | -0.37994
1154.4375 | 124.5209 | -124.3561 | 0.20142 | 0.11765 | 0.023056 | 0.018297 | 0.036198 | 0.0010702 | 0.00017081 | 0.014272 | 0.009155 | 0.17853 | -0.25635 | -0.018311 | -0.045776 | -0.018311 | 0.013733 | 0.086975 | 0.21057 | -0.23804 | 124.0997 | -0.022888 | 124.3652 | 124.3378 | -0.24719 | 124.118 | 0.009155 | 0.2655 | 124.3698 | 124.4431 | 124.3103 | 124.5346 | 124.3652 | 124.5666 | 124.3378 | 124.118 | 124.5346 | 124.3652 | 124.3378 | 124.3103 | 124.5666 | -0.45776 | -0.43945
1155.375 | 124.5987 | -124.3057 | 0.1831 | 0.10239 | 0.017929 | 0.012529 | 0.030644 | -0.0014932 | 0.00038461 | 0.015127 | 0.036621 | 0.1236 | -0.2243 | 0.064087 | 0.068665 | 0.091553 | -0.068665 | 0.19226 | 0.1831 | -0.19226 | 124.0814 | -0.059509 | 124.3423 | 124.3698 | -0.11444 | 124.1135 | 0 | 0.26093 | 124.2371 | 124.498 | 124.3744 | 124.4293 | 124.3423 | 124.4888 | 124.3973 | 124.1135 | 124.4293 | 124.3423 | 124.3973 | 124.3744 | 124.4888 | -0.40741 | -0.37537
1156.375 | 124.5987 | -124.2691 | 0.1831 | 0.094757 | 0.017289 | 0.013383 | 0.031926 | -0.0012796 | -0.0030334 | 0.016836 | 0.054932 | 0.11444 | -0.21515 | 0.086975 | 0.068665 | 0.10529 | -0.086975 | 0.21515 | 0.20599 | -0.21515 | 124.054 | -0.068664 | 124.324 | 124.3561 | -0.11444 | 124.054 | 0.022889 | 0.27008 | 124.1821 | 124.4843 | 124.3378 | 124.3835 | 124.324 | 124.4751 | 124.3744 | 124.054 | 124.3835 | 124.324 | 124.3744 | 124.3378 | 124.4751 | -0.39825 | -0.39825
1157.375 | 124.5941 | -124.3103 | 0.16479 | 0.10239 | 0.015366 | 0.010393 | 0.031926 | -0.0014932 | -0.00025639 | 0.01534 | -0.37537 | 0.1236 | -0.25177 | 0.045776 | 0.041199 | 0.032043 | -0.068665 | 0.17395 | 0.15564 | -0.21057 | 124.0585 | -0.041199 | 123.9349 | 124.3561 | -0.1236 | 124.0997 | -0.009155 | -0.1236 | 124.2416 | 124.4843 | 124.3515 | 124.4339 | 123.9349 | 124.4659 | 124.3423 | 124.0997 | 124.4339 | 123.9349 | 124.3423 | 124.3515 | 124.4659 | -0.41656 | -0.37537
1158.4375 | 124.617 | -124.292 | 0.20142 | 0.018463 | 0.013443 | 0.01082 | 0.033635 | -0.0025614 | 0.00017081 | 0.01299 | 0.027466 | 0.12817 | -0.22888 | 0.050354 | 0.054932 | 0.07782 | -0.032043 | 0.20142 | 0.21057 | -0.21973 | 124.0631 | -0.073242 | 124.3195 | 124.3423 | -0.14648 | 124.0723 | 0.009155 | 0.25635 | 124.2599 | 124.4934 | 124.3469 | 124.4202 | 124.3195 | 124.5026 | 124.3698 | 124.0723 | 124.4202 | 124.3195 | 124.3698 | 124.3469 | 124.5026 | -0.4303 | -0.42114
1159.375 | 124.6445 | -124.2691 | 0.19226 | 0.17105 | 0.011093 | 0.01552 | 0.039403 | -0.0025614 | -0.00089719 | 0.015767 | 0.073242 | 0.12817 | -0.21057 | 0.10071 | 0.10529 | 0.1236 | -0.13275 | 0.23346 | 0.17853 | -0.17853 | 124.0585 | -0.064087 | 124.3423 | 124.3698 | -0.086975 | 124.0906 | -0.013733 | 0.28381 | 124.1364 | 124.5026 | 124.3744 | 124.3973 | 124.3423 | 124.4476 | 124.3927 | 124.0906 | 124.3973 | 124.3423 | 124.3927 | 124.3744 | 124.4476 | -0.40283 | -0.37079
1160.375 | 124.6445 | -124.2828 | 0.16937 | 0.14816 | 0.011307 | 0.015733 | 0.039616 | -0.0017068 | -0.0028198 | 0.014699 | 0.07782 | 0.1236 | -0.21057 | 0.10071 | 0.073242 | 0.1236 | -0.14191 | 0.22888 | 0.18768 | -0.20142 | 124.0723 | -0.045777 | 124.3607 | 124.3835 | -0.096131 | 124.0814 | 0.01831 | 0.28839 | 124.1409 | 124.5117 | 124.3561 | 124.4064 | 124.3607 | 124.4705 | 124.4064 | 124.0814 | 124.4064 | 124.3607 | 124.4064 | 124.3561 | 124.4705 | -0.37994 | -0.37079
1161.375 | 124.5987 | -124.292 | 0.17853 | 0.094757 | 0.014511 | 0.01317 | 0.038335 | -0.0021342 | -0.0013244 | 0.016195 | 0.064087 | 0.11444 | -0.21057 | 0.10071 | 0.07782 | 0.10986 | -0.10071 | 0.23804 | 0.18768 | -0.19684 | 124.0814 | -0.064087 | 124.3561 | 124.3927 | -0.10071 | 124.0952 | 0.009155 | 0.27466 | 124.1913 | 124.53 | 124.3698 | 124.4064 | 124.3561 | 124.4797 | 124.4019 | 124.0952 | 124.4064 | 124.3561 | 124.4019 | 124.3698 | 124.4797 | -0.3891 | -0.37537
1162.375 | 124.6124 | -124.2645 | 0.19226 | 0.15579 | 0.0087436 | 0.011461 | 0.04453 | -0.0025614 | -0.00025639 | 0.012777 | 0.073242 | 0.11444 | -0.20142 | 0.09613 | 0.10071 | 0.12817 | -0.1236 | 0.23346 | 0.19684 | -0.20599 | 124.0631 | -0.07782 | 124.3378 | 124.3607 | -0.091553 | 124.0585 | 0.004577 | 0.27466 | 124.1409 | 124.498 | 124.3652 | 124.379 | 124.3378 | 124.4614 | 124.3927 | 124.0585 | 124.379 | 124.3378 | 124.3927 | 124.3652 | 124.4614 | -0.39368 | -0.39826
1163.375 | 124.6216 | -124.2645 | 0.18768 | 0.094757 | 0.0089572 | 0.012743 | 0.03983 | -0.0025614 | 0.001239 | 0.015767 | 0.041199 | 0.1236 | -0.21515 | 0.059509 | 0.059509 | 0.07782 | -0.064087 | 0.20142 | 0.20599 | -0.20599 | 124.0494 | -0.064087 | 124.3057 | 124.324 | -0.12817 | 124.0585 | 0.018311 | 0.25635 | 124.2004 | 124.4659 | 124.324 | 124.3881 | 124.3057 | 124.4705 | 124.3423 | 124.0585 | 124.3881 | 124.3057 | 124.3423 | 124.324 | 124.4705 | -0.40283 | -0.39368
1164.375 | 124.5758 | -124.292 | 0.19684 | 0.071869 | 0.0078892 | 0.011461 | 0.040471 | -0.001066 | -0.0030334 | 0.014913 | 0.054932 | 0.1236 | -0.20599 | 0.07782 | 0.073242 | 0.10986 | -0.091553 | 0.20599 | 0.20599 | -0.19226 | 124.086 | -0.073242 | 124.3469 | 124.3698 | -0.1236 | 124.0997 | 0.009156 | 0.26093 | 124.2004 | 124.498 | 124.3652 | 124.4156 | 124.3469 | 124.498 | 124.4019 | 124.0997 | 124.4156 | 124.3469 | 124.4019 | 124.3652 | 124.498 | -0.40283 | -0.3891
1165.375 | 124.617 | -124.2828 | 0.19226 | 0.094757 | 0.0083164 | 0.018297 | 0.040471 | -0.0029886 | -0.0015382 | 0.017049 | 0.073242 | 0.12817 | -0.22888 | 0.09613 | 0.10071 | 0.10986 | -0.11444 | 0.23346 | 0.20142 | -0.19684 | 124.054 | -0.064087 | 124.3561 | 124.379 | -0.091553 | 124.086 | 0.009155 | 0.30212 | 124.1684 | 124.5163 | 124.3835 | 124.411 | 124.3561 | 124.4843 | 124.3927 | 124.086 | 124.411 | 124.3561 | 124.3927 | 124.3835 | 124.4843 | -0.42114 | -0.3891
1166.375 | 124.6445 | -124.3195 | 0.17853 | -0.4393 | 0.0081028 | 0.015306 | 0.04218 | 0.00042942 | -0.00046999 | 0.015767 | 0.050354 | 0.068665 | -0.24719 | 0.086975 | 0.086975 | 0.13275 | -0.13733 | 0.21973 | 0.16937 | -0.19684 | 124.0723 | -0.10986 | 124.3698 | 124.4064 | -0.091553 | 124.1226 | -0.009155 | 0.29755 | 124.1821 | 124.5392 | 124.4064 | 124.3881 | 124.3698 | 124.4888 | 124.4522 | 124.1226 | 124.3881 | 124.3698 | 124.4522 | 124.4064 | 124.4888 | -0.42572 | -0.37537
1167.375 | 124.6536 | -124.324 | 0.14648 | 0.11765 | 0.010453 | 0.021501 | 0.045384 | 0.0025656 | -0.0015382 | 0.014913 | 0.086975 | 0.11902 | -0.21057 | 0.21057 | 0.09613 | 0.073242 | -0.082397 | 0.2243 | 0.15106 | -0.21515 | 124.1135 | -0.027465 | 124.411 | 124.5346 | -0.050354 | 124.1089 | 0.004578 | 0.29755 | 124.2416 | 124.5483 | 124.4202 | 124.4431 | 124.411 | 124.4751 | 124.3973 | 124.1089 | 124.4431 | 124.411 | 124.3973 | 124.4202 | 124.4751 | -0.35706 | -0.36163
1168.375 | 124.6765 | -124.2874 | 0.17395 | 0.21683 | 0.012802 | 0.01787 | 0.039403 | -0.00063878 | -0.00089719 | 0.014699 | 0.086975 | 0.10529 | -0.21515 | 0.10071 | 0.073242 | 0.11902 | -0.12817 | 0.2243 | 0.20599 | -0.20599 | 124.0723 | -0.068664 | 124.3744 | 124.3881 | -0.10071 | 124.0814 | 0.032044 | 0.30212 | 124.1592 | 124.5117 | 124.3607 | 124.3927 | 124.3744 | 124.4934 | 124.4064 | 124.0814 | 124.3927 | 124.3744 | 124.4064 | 124.3607 | 124.4934 | -0.3891 | -0.37994
1169.375 | 124.6536 | -124.2599 | 0.14648 | 0.033722 | 0.013443 | 0.015733 | 0.040898 | -0.0012796 | -0.002179 | 0.015767 | 0.068665 | 0.086975 | -0.24261 | 0.091553 | 0.073242 | 0.11444 | -0.15106 | 0.22888 | 0.17853 | -0.20142 | 124.0173 | -0.059509 | 124.3286 | 124.3515 | -0.073242 | 124.0585 | 0.032044 | 0.31128 | 124.1089 | 124.4888 | 124.3332 | 124.3469 | 124.3286 | 124.4385 | 124.3744 | 124.0585 | 124.3469 | 124.3286 | 124.3744 | 124.3332 | 124.4385 | -0.3891 | -0.3479
1170.375 | 124.649 | -124.2828 | 0.16022 | 0.094757 | 0.013657 | 0.014665 | 0.038121 | 2.222e-06 | -0.0023926 | 0.015554 | 0.064087 | 0.11902 | -0.20599 | 0.086975 | 0.082397 | 0.1236 | -0.11902 | 0.23346 | 0.19684 | -0.19684 | 124.0768 | -0.041198 | 124.3469 | 124.3698 | -0.07782 | 124.086 | 0.036621 | 0.27008 | 124.1638 | 124.5163 | 124.3652 | 124.4019 | 124.3469 | 124.4797 | 124.4064 | 124.086 | 124.4019 | 124.3469 | 124.4064 | 124.3652 | 124.4797 | -0.36621 | -0.35706
1171.375 | 124.6399 | -124.3011 | 0.16479 | 0.12527 | 0.013443 | 0.014024 | 0.039403 | 0.0012838 | -0.0028198 | 0.016622 | 0.07782 | 0.12817 | -0.21057 | 0.086975 | 0.086975 | 0.11902 | -0.1236 | 0.23346 | 0.1831 | -0.21057 | 124.0906 | -0.036621 | 124.379 | 124.3881 | -0.07782 | 124.0906 | 0.01831 | 0.28839 | 124.1776 | 124.5346 | 124.3881 | 124.4293 | 124.379 | 124.4843 | 124.4202 | 124.0906 | 124.4293 | 124.379 | 124.4202 | 124.3881 | 124.4843 | -0.37537 | -0.37537
1172.375 | 124.649 | -124.292 | 0.17395 | -0.042572 | 0.012589 | 0.015306 | 0.039189 | 0.00021582 | -0.0028198 | 0.013845 | 0.073242 | 0.10529 | -0.20599 | 0.11444 | 0.086975 | 0.11444 | -0.13733 | 0.22888 | 0.17853 | -0.20142 | 124.086 | -0.068664 | 124.3652 | 124.4064 | -0.086975 | 124.0906 | 0.004578 | 0.27924 | 124.1547 | 124.5209 | 124.379 | 124.3973 | 124.3652 | 124.4705 | 124.4064 | 124.0906 | 124.3973 | 124.3652 | 124.4064 | 124.379 | 124.4705 | -0.37994 | -0.37537
1173.375 | 124.6078 | -124.3011 | 0.1831 | 0.16342 | 0.013016 | 0.017442 | 0.043462 | -0.00021158 | -0.0011108 | 0.014058 | 0.027466 | 0.15106 | -0.23804 | 0.050354 | 0.041199 | 0.073242 | -0.10986 | 0.1831 | 0.19226 | -0.2243 | 124.0631 | -0.032043 | 124.3286 | 124.3515 | -0.14191 | 124.0768 | 0.009156 | 0.2655 | 124.1913 | 124.4843 | 124.3423 | 124.4522 | 124.3286 | 124.4934 | 124.3744 | 124.0768 | 124.4522 | 124.3286 | 124.3744 | 124.3423 | 124.4934 | -0.42114 | -0.40741
1174.375 | 124.5895 | -124.3332 | 0.12817 | 0.018463 | 0.012375 | 0.013383 | 0.041753 | -0.00063878 | -0.0023926 | 0.015127 | 0.073242 | 0.13733 | -0.21515 | 0.09613 | 0.091553 | -0.009155 | -0.44861 | 0.31586 | 0.16022 | -0.2243 | 124.118 | 0.009155 | 124.4064 | 124.4293 | -0.036621 | 124.1089 | 0.032043 | 0.28839 | 123.8846 | 124.649 | 124.4247 | 124.4705 | 124.4064 | 124.4934 | 124.324 | 124.1089 | 124.4705 | 124.4064 | 124.324 | 124.4247 | 124.4934 | -0.34332 | -0.35248
1175.375 | 124.649 | -124.2783 | 0.17853 | 0.18631 | 0.013443 | 0.0093246 | 0.041539 | 0.0027792 | -4.2788e-05 | 0.01534 | 0.050354 | 0.11902 | -0.21057 | 0.045776 | 0.022888 | 0.11444 | -0.09613 | 0.19226 | 0.19226 | -0.20599 | 124.0677 | -0.059509 | 124.3286 | 124.324 | -0.15564 | 124.0723 | 0.013733 | 0.26093 | 124.1821 | 124.4705 | 124.3011 | 124.3973 | 124.3286 | 124.4705 | 124.3927 | 124.0723 | 124.3973 | 124.3286 | 124.3927 | 124.3011 | 124.4705 | -0.3891 | -0.38452
1176.375 | 124.6399 | -124.3057 | 0.19226 | 0.19394 | 0.011948 | 0.019792 | 0.042607 | 0.00064302 | -0.00046999 | 0.014058 | 0.032043 | 0.14191 | -0.23346 | 0.041199 | 0.050354 | 0.068665 | -0.073242 | 0.1831 | 0.19684 | -0.21515 | 124.0723 | -0.050354 | 124.3378 | 124.3469 | -0.14191 | 124.0906 | 0.004577 | 0.2655 | 124.2325 | 124.4888 | 124.3561 | 124.4476 | 124.3378 | 124.5026 | 124.3744 | 124.0906 | 124.4476 | 124.3378 | 124.3744 | 124.3561 | 124.5026 | -0.42572 | -0.40741
1177.375 | 124.7223 | -124.3469 | 0.13275 | 0.19394 | 0.012802 | 0.020219 | 0.041539 | 0.0012838 | -0.0015382 | 0.015767 | 0.082397 | 0.13733 | -0.21973 | 0.07782 | 0.086975 | 0.11444 | -0.11444 | 0.064087 | 0.16937 | -0.2243 | 124.1272 | 0.004578 | 124.4293 | 124.4247 | -0.045776 | 124.1226 | 0.036622 | 0.30212 | 124.2325 | 124.411 | 124.4339 | 124.4843 | 124.4293 | 124.5163 | 124.4614 | 124.1226 | 124.4843 | 124.4293 | 124.4614 | 124.4339 | 124.5163 | -0.35248 | -0.35706
1178.375 | 124.649 | -124.2874 | 0.1831 | 0.11765 | 0.00853 | 0.015947 | 0.041539 | -0.0012796 | -0.0028198 | 0.017904 | 0.045776 | 0.13275 | -0.21973 | 0.07782 | 0.059509 | 0.10529 | -0.10529 | 0.21515 | 0.19226 | -0.21515 | 124.0677 | -0.050354 | 124.3332 | 124.3652 | -0.1236 | 124.0723 | 0.009156 | 0.2655 | 124.1821 | 124.5026 | 124.3469 | 124.4202 | 124.3332 | 124.4797 | 124.3927 | 124.0723 | 124.4202 | 124.3332 | 124.3927 | 124.3469 | 124.4797 | -0.40283 | -0.39825
1179.375 | 124.6262 | -124.292 | 0.1831 | 0.2092 | 0.00853 | 0.015733 | 0.043675 | 0.0012838 | -0.0013244 | 0.014913 | 0.022888 | 0.16022 | -0.23804 | 0.022888 | 0.032043 | 0.068665 | -0.073242 | 0.15564 | 0.20142 | -0.22888 | 124.054 | -0.022888 | 124.3149 | 124.3149 | -0.15106 | 124.0631 | 0.018311 | 0.26093 | 124.2188 | 124.4476 | 124.324 | 124.4522 | 124.3149 | 124.4934 | 124.3607 | 124.0631 | 124.4522 | 124.3149 | 124.3607 | 124.324 | 124.4934 | -0.42114 | -0.41199
1180.375 | 124.5255 | -124.3332 | 0.20142 | 0.47623 | 0.010025 | 0.015947 | 0.045171 | 0.0012838 | -0.0015382 | 0.015554 | -0.009155 | 0.19226 | -0.23346 | -0.032043 | -0.032043 | 0.004578 | 0.036621 | 0.082397 | 0.24261 | -0.24719 | 124.0997 | -0.009155 | 124.324 | 124.3011 | -0.23346 | 124.086 | 0.041199 | 0.2243 | 124.3698 | 124.4156 | 124.3011 | 124.5255 | 124.324 | 124.5758 | 124.3378 | 124.086 | 124.5255 | 124.324 | 124.3378 | 124.3011 | 124.5758 | -0.43488 | -0.44861
1181.375 | 124.5483 | -124.3286 | 0.19684 | 0.1329 | 0.010453 | 0.011888 | 0.04752 | 0.0036336 | -0.00068359 | 0.01534 | -0.009155 | 0.16937 | -0.23804 | -0.027466 | -0.009155 | 0.022888 | -0.004578 | 0.10529 | 0.21057 | -0.23804 | 124.0906 | -0.027465 | 124.3195 | 124.3011 | -0.20599 | 124.0906 | 0.013733 | 0.22888 | 124.324 | 124.4339 | 124.3195 | 124.498 | 124.3195 | 124.5392 | 124.3515 | 124.0906 | 124.498 | 124.3195 | 124.3515 | 124.3195 | 124.5392 | -0.43488 | -0.43488
1182.375 | 124.5575 | -124.3561 | 0.18768 | 0.2092 | 0.00853 | 0.01552 | 0.048588 | 0.0027792 | -0.0019654 | 0.01534 | 0 | 0.17853 | -0.25635 | -0.027466 | -0.022888 | -0.013733 | 0.032043 | 0.10529 | 0.23346 | -0.23346 | 124.0997 | -0.009155 | 124.3561 | 124.3286 | -0.21057 | 124.1226 | 0.045776 | 0.25635 | 124.3881 | 124.4614 | 124.3332 | 124.5346 | 124.3561 | 124.5895 | 124.3423 | 124.1226 | 124.5346 | 124.3561 | 124.3423 | 124.3332 | 124.5895 | -0.44403 | -0.42114
1183.375 | 124.5483 | -124.3515 | 0.21515 | 0.86533 | 0.0066074 | 0.015092 | 0.048588 | 0.0025656 | 0.00059821 | 0.015127 | 0.022888 | 0.17395 | -0.23346 | -0.036621 | -0.022888 | 0 | 0.032043 | 0.086975 | 0.2243 | -0.26093 | 124.118 | -0.041199 | 124.3744 | 124.3149 | -0.23804 | 124.0906 | 0.009155 | 0.25635 | 124.3835 | 124.4385 | 124.3286 | 124.5255 | 124.3744 | 124.5758 | 124.3515 | 124.0906 | 124.5255 | 124.3744 | 124.3515 | 124.3286 | 124.5758 | -0.44861 | -0.47607
1184.375 | 124.5392 | -124.3286 | 0.19684 | 0.14816 | 0.0087436 | 0.014238 | 0.047734 | 0.0029928 | 0.00038461 | 0.017049 | -0.004578 | 0.16479 | -0.22888 | -0.036621 | -0.022888 | -0.018311 | 0.018311 | 0.091553 | 0.2243 | -0.25177 | 124.0997 | -0.032043 | 124.324 | 124.292 | -0.21973 | 124.0768 | 0.027466 | 0.2243 | 124.3469 | 124.4202 | 124.3057 | 124.4934 | 124.324 | 124.5529 | 124.3103 | 124.0768 | 124.4934 | 124.324 | 124.3103 | 124.3057 | 124.5529 | -0.42572 | -0.44861
1185.375 | 124.5621 | -124.3332 | 0.20142 | 0.11002 | 0.0087436 | 0.014452 | 0.046452 | 0.001711 | -0.0017518 | 0.014486 | -0.004578 | 0.16022 | -0.23804 | -0.032043 | -0.036621 | -0.009155 | 0.036621 | 0.082397 | 0.23804 | -0.23804 | 124.0952 | -0.041199 | 124.3286 | 124.3011 | -0.23804 | 124.0952 | 0.036621 | 0.23346 | 124.3698 | 124.4156 | 124.2966 | 124.4934 | 124.3286 | 124.5712 | 124.324 | 124.0952 | 124.4934 | 124.3286 | 124.324 | 124.2966 | 124.5712 | -0.43945 | -0.43945
1186.375 | 124.5071 | -124.3561 | 0.20142 | 2.8719 | 0.0081028 | 0.013597 | 0.046666 | 0.00342 | -0.00068359 | 0.014699 | -0.09613 | 0.18768 | -0.20599 | -0.022888 | -0.022888 | -0.013733 | 0.054932 | 0.07782 | 0.22888 | -0.25635 | 124.1501 | -0.013733 | 124.2599 | 124.3332 | -0.2243 | 124.0997 | 0.027466 | 0.10986 | 124.411 | 124.4339 | 124.3332 | 124.5438 | 124.2599 | 124.585 | 124.3423 | 124.0997 | 124.5438 | 124.2599 | 124.3423 | 124.3332 | 124.585 | -0.40741 | -0.45776
1187.375 | 124.5438 | -124.3607 | 0.20599 | 0.071869 | 0.0089572 | 0.013811 | 0.047093 | 0.001711 | -0.00025639 | 0.013631 | 0.022888 | 0.16479 | -0.25177 | -0.013733 | 0 | -0.009155 | 0.036621 | 0.10529 | 0.21973 | -0.26093 | 124.1089 | -0.041199 | 124.3835 | 124.3469 | -0.20599 | 124.0997 | 0.013733 | 0.27466 | 124.3973 | 124.4659 | 124.3607 | 124.5255 | 124.3835 | 124.5804 | 124.3515 | 124.0997 | 124.5255 | 124.3835 | 124.3515 | 124.3607 | 124.5804 | -0.45776 | -0.46692
1188.375 | 124.5392 | -124.3423 | 0.21057 | 0.041351 | 0.0098118 | 0.014024 | 0.045811 | 0.004061 | -0.0011108 | 0.015554 | 0 | 0.17395 | -0.25635 | -0.032043 | -0.032043 | -0.018311 | 0.068665 | 0.09613 | 0.2243 | -0.25635 | 124.086 | -0.036621 | 124.3423 | 124.3103 | -0.24261 | 124.086 | 0.013733 | 0.25635 | 124.411 | 124.4385 | 124.3103 | 124.5163 | 124.3423 | 124.5667 | 124.324 | 124.086 | 124.5163 | 124.3423 | 124.324 | 124.3103 | 124.5667 | -0.46692 | -0.46692
1189.375 | 124.5392 | -124.4064 | 0.19684 | -0.050202 | 0.0087436 | 0.017656 | 0.047093 | 0.004061 | -0.00068359 | 0.017476 | 0.022888 | 0.17395 | -0.23804 | -0.018311 | -0.036621 | -0.022888 | 0.041199 | 0.09613 | 0.2243 | -0.26093 | 124.1684 | -0.022888 | 124.4293 | 124.3881 | -0.23346 | 124.1455 | 0.027466 | 0.26093 | 124.4476 | 124.5026 | 124.3698 | 124.5804 | 124.4293 | 124.6307 | 124.3835 | 124.1455 | 124.5804 | 124.4293 | 124.3835 | 124.3698 | 124.6307 | -0.43488 | -0.45776
1190.375 | 124.5438 | -124.3423 | 0.20142 | -0.034943 | 0.0089572 | 0.018083 | 0.045811 | 0.004061 | -0.0026062 | 0.014699 | 0.036621 | 0.16022 | -0.23804 | 0 | 0 | 0.013733 | 0.022888 | 0.13733 | 0.21057 | -0.23804 | 124.1043 | -0.041199 | 124.379 | 124.3423 | -0.20142 | 124.1043 | 0.009155 | 0.27466 | 124.3652 | 124.4797 | 124.3423 | 124.5026 | 124.379 | 124.5529 | 124.3561 | 124.1043 | 124.5026 | 124.379 | 124.3561 | 124.3423 | 124.5529 | -0.43945 | -0.43945
1191.4375 | 124.6628 | -124.324 | 0.20599 | -0.21042 | 0.0061802 | 0.011247 | 0.037907 | 0.001711 | -0.0023926 | 0.015554 | 0.068665 | 0.13275 | -0.20142 | 0.07782 | 0.09613 | 0.11902 | -0.045776 | 0.28381 | 0.21515 | -0.21057 | 124.1226 | -0.073243 | 124.3927 | 124.4019 | -0.10986 | 124.1135 | 0.009155 | 0.27008 | 124.2783 | 124.6078 | 124.4202 | 124.4568 | 124.3927 | 124.5392 | 124.4431 | 124.1135 | 124.4568 | 124.3927 | 124.4431 | 124.4202 | 124.5392 | -0.40741 | -0.41657
1192.375 | 124.5392 | -124.3881 | 0.19684 | -0.019684 | 0.00853 | 0.013811 | 0.047093 | 0.001711 | -0.0015382 | 0.015767 | 0.027466 | 0.17395 | -0.24719 | -0.018311 | -0.041199 | 0 | 0.032043 | 0.11902 | 0.21973 | -0.24261 | 124.1409 | -0.022888 | 124.4156 | 124.3698 | -0.23804 | 124.1455 | 0.022889 | 0.27466 | 124.4202 | 124.5071 | 124.3469 | 124.5621 | 124.4156 | 124.6078 | 124.3881 | 124.1455 | 124.5621 | 124.4156 | 124.3881 | 124.3469 | 124.6078 | -0.44403 | -0.43945
1193.4375 | 124.6536 | -124.3057 | 0.19684 | -0.21805 | 0.0031894 | 0.0067612 | 0.039189 | 0.0019248 | -0.0011108 | 0.017263 | 0.10071 | 0.11902 | -0.2243 | 0.07782 | 0.13275 | 0.11444 | -0.068665 | 0.28381 | 0.17853 | -0.21057 | 124.0814 | -0.077819 | 124.4064 | 124.3835 | -0.064087 | 124.0952 | -0.01831 | 0.32501 | 124.2371 | 124.5895 | 124.4385 | 124.4247 | 124.4064 | 124.4843 | 124.4202 | 124.0952 | 124.4247 | 124.4064 | 124.4202 | 124.4385 | 124.4843 | -0.42114 | -0.40741
1194.375 | 124.6216 | -124.292 | 0.28381 | -0.095978 | 0.0076756 | 0.018724 | 0.04987 | 0.002352 | 0.0010254 | 0.014058 | 0.036621 | 0.17395 | -0.22888 | 0.032043 | 0.25177 | 0.23346 | 0.22888 | 0.32501 | 0.27008 | -0.14191 | 124.0631 | -0.10986 | 124.3286 | 124.324 | -0.032043 | 124.1501 | -0.013732 | 0.2655 | 124.5209 | 124.617 | 124.5438 | 124.4659 | 124.3286 | 124.5621 | 124.5255 | 124.1501 | 124.4659 | 124.3286 | 124.5255 | 124.5438 | 124.5621 | -0.5127 | -0.42572
1195.4375 | 124.6353 | -124.292 | 0.19684 | -0.034943 | 0.0063938 | 0.013597 | 0.037266 | 0.0014974 | 0.0018798 | 0.016408 | 0.022888 | 0.15564 | -0.2243 | 0.059509 | 0.073242 | 0.10986 | -0.036621 | 0.23346 | 0.19684 | -0.1831 | 124.0677 | -0.041198 | 124.3149 | 124.3515 | -0.1236 | 124.1089 | 0 | 0.24719 | 124.2554 | 124.5255 | 124.3652 | 124.4476 | 124.3149 | 124.4888 | 124.4019 | 124.1089 | 124.4476 | 124.3149 | 124.4019 | 124.3652 | 124.4888 | -0.42114 | -0.37994
1196.375 | 124.5987 | -124.3469 | 0.21973 | -0.13412 | 0.0081028 | 0.017442 | 0.051366 | 0.0014974 | -0.0034608 | 0.014913 | 0.25177 | 0.1831 | -0.16937 | 0.064087 | 0.059509 | 0.041199 | 0.027466 | 0.19226 | 0.25177 | -0.17395 | 124.1776 | -0.036622 | 124.5987 | 124.411 | -0.16022 | 124.173 | 0.032043 | 0.42114 | 124.3744 | 124.5392 | 124.4064 | 124.53 | 124.5987 | 124.5987 | 124.3881 | 124.173 | 124.53 | 124.5987 | 124.3881 | 124.4064 | 124.5987 | -0.3891 | -0.39368
1197.375 | 124.6445 | -124.2828 | 0.25635 | -0.095978 | 0.0055392 | 0.015733 | 0.050511 | 0.0021384 | -0.0013244 | 0.015767 | 0.073242 | 0.16937 | -0.23346 | 0.045776 | 0.027466 | 0.050354 | 0.013733 | 0.25177 | 0.24261 | -0.19226 | 124.0494 | -0.086975 | 124.3561 | 124.3286 | -0.22888 | 124.0906 | -0.013733 | 0.3067 | 124.2966 | 124.5346 | 124.3103 | 124.4522 | 124.3561 | 124.5255 | 124.3332 | 124.0906 | 124.4522 | 124.3561 | 124.3332 | 124.3103 | 124.5255 | -0.48981 | -0.44861
1198.4375 | 124.585 | -124.379 | 0.20599 | -0.21042 | 0.00853 | 0.020006 | 0.043675 | 0.0029928 | -0.0015382 | 0.014486 | 0.013733 | 0.17853 | -0.24261 | -0.004578 | 0.013733 | 0.022888 | 0.041199 | 0.15564 | 0.21515 | -0.25635 | 124.1364 | -0.027466 | 124.3927 | 124.3744 | -0.19226 | 124.1226 | 0.009155 | 0.25635 | 124.4202 | 124.5346 | 124.3927 | 124.5575 | 124.3927 | 124.5941 | 124.4019 | 124.1226 | 124.5575 | 124.3927 | 124.4019 | 124.3927 | 124.5941 | -0.44861 | -0.46234
1199.375 | 124.585 | -124.3332 | 0.20142 | 0.68985 | 0.0055392 | 0.018083 | 0.045171 | 0.005129 | -0.003247 | 0.014699 | 0.13275 | 0.22888 | -0.13733 | 0.036621 | 0.045776 | 0.041199 | 0.009155 | 0.17853 | 0.24719 | -0.18768 | 124.1959 | 0.027466 | 124.4659 | 124.3698 | -0.15564 | 124.1455 | 0.045776 | 0.27008 | 124.3423 | 124.5117 | 124.379 | 124.5621 | 124.4659 | 124.5804 | 124.3744 | 124.1455 | 124.5621 | 124.4659 | 124.3744 | 124.379 | 124.5804 | -0.33875 | -0.3891
1200.375 | 124.585 | -124.3286 | 0.24719 | -0.14175 | 0.0083164 | 0.01552 | 0.04688 | 0.0042746 | 0.00017081 | 0.014272 | 0.059509 | 0.15564 | -0.25177 | 0.10071 | 0.004578 | 0.045776 | 0.036621 | 0.18768 | 0.2655 | -0.10986 | 124.0768 | -0.091552 | 124.3881 | 124.4293 | -0.24261 | 124.2188 | 0.018311 | 0.31128 | 124.3652 | 124.5163 | 124.3332 | 124.4843 | 124.3881 | 124.5941 | 124.3744 | 124.2188 | 124.4843 | 124.3881 | 124.3744 | 124.3332 | 124.5941 | -0.49896 | -0.35706
1201.375 | 124.6078 | -124.3607 | 0.18768 | -0.20279 | 0.0083164 | 0.013597 | 0.046025 | 0.0014974 | -0.00068359 | 0.015127 | 0.013733 | 0.17853 | -0.24719 | 0.022888 | 0.009155 | 0.018311 | 0.050354 | 0.15564 | 0.23346 | -0.23804 | 124.1135 | -0.009155 | 124.3744 | 124.3835 | -0.17853 | 124.1226 | 0.045776 | 0.26093 | 124.411 | 124.5163 | 124.3698 | 124.5392 | 124.3744 | 124.5941 | 124.379 | 124.1226 | 124.5392 | 124.3744 | 124.379 | 124.3698 | 124.5941 | -0.43488 | -0.42572
1202.4375 | 124.6811 | -124.3057 | 0.1831 | -0.095978 | 0.004044 | 0.017442 | 0.038121 | 0.0025656 | -0.0023926 | 0.016195 | 0.07782 | 0.15106 | -0.18768 | 0.11444 | 0.12817 | 0.14648 | -0.09613 | 0.29755 | 0.19226 | -0.20142 | 124.118 | -0.032043 | 124.3835 | 124.4202 | -0.054931 | 124.1043 | 0.009156 | 0.2655 | 124.2096 | 124.6033 | 124.4339 | 124.4568 | 124.3835 | 124.498 | 124.4522 | 124.1043 | 124.4568 | 124.3835 | 124.4522 | 124.4339 | 124.498 | -0.37079 | -0.38452
1203.375 | 124.5895 | -124.3195 | 0.20599 | -0.23331 | 0.0093844 | 0.013811 | 0.044743 | 0.0014974 | -0.003247 | 0.014699 | 0.064087 | 0.16022 | -0.24261 | 0.036621 | 0.022888 | 0.027466 | 0.027466 | 0.1831 | 0.22888 | -0.25177 | 124.0768 | -0.045777 | 124.3835 | 124.3561 | -0.18311 | 124.0677 | 0.022888 | 0.3067 | 124.3469 | 124.5026 | 124.3423 | 124.4797 | 124.3835 | 124.5483 | 124.3469 | 124.0677 | 124.4797 | 124.3835 | 124.3469 | 124.3423 | 124.5483 | -0.44861 | -0.45776
1204.4531 | 124.5666 | -124.3378 | 0.20142 | -0.07309 | 0.0074618 | 0.01552 | 0.048161 | 0.0047018 | -4.2788e-05 | 0.014058 | 0.068665 | 0.16022 | -0.22888 | 0.018311 | 0.018311 | 0.022888 | 0.013733 | 0.15564 | 0.21973 | -0.26093 | 124.1089 | -0.041199 | 124.4064 | 124.3561 | -0.18311 | 124.0768 | 0.018311 | 0.29755 | 124.3515 | 124.4934 | 124.3561 | 124.498 | 124.4064 | 124.5575 | 124.3607 | 124.0768 | 124.498 | 124.4064 | 124.3607 | 124.3561 | 124.5575 | -0.4303 | -0.46234
1205.375 | 124.5758 | -124.3515 | 0.20599 | -0.40878 | 0.0089572 | 0.021288 | 0.046025 | 0.0042746 | -4.2788e-05 | 0.012563 | 0.064087 | 0.21515 | -0.12817 | 0.041199 | 0.022888 | 0.045776 | 0.022888 | 0.16937 | 0.21515 | -0.25635 | 124.2233 | 0.009155 | 124.4156 | 124.3927 | -0.18311 | 124.0952 | 0.009155 | 0.19226 | 124.3744 | 124.5209 | 124.3744 | 124.5666 | 124.4156 | 124.5666 | 124.3973 | 124.0952 | 124.5666 | 124.4156 | 124.3973 | 124.3744 | 124.5666 | -0.33417 | -0.46234
1206.375 | 124.5987 | -124.3286 | 0.19684 | -0.79025 | 0.0057528 | 0.016801 | 0.045811 | 0.0032064 | -0.0011108 | 0.01299 | 0.022888 | 0.22888 | -0.11902 | 0.054932 | 0.036621 | 0.045776 | 0.009155 | 0.17853 | 0.24719 | -0.21973 | 124.2096 | 0.032044 | 124.3515 | 124.3835 | -0.16022 | 124.1089 | 0.050354 | 0.14191 | 124.3378 | 124.5071 | 124.3652 | 124.5575 | 124.3515 | 124.5758 | 124.3744 | 124.1089 | 124.5575 | 124.3515 | 124.3744 | 124.3652 | 124.5758 | -0.31586 | -0.41657
1207.375 | 124.5712 | -124.3561 | 0.21515 | -0.22568 | 0.0095982 | 0.012956 | 0.047307 | 0.004061 | -0.002179 | 0.011709 | 0.036621 | 0.16479 | -0.24719 | 0.018311 | 0.018311 | 0.054932 | 0.032043 | 0.17395 | 0.22888 | -0.23346 | 124.1089 | -0.050354 | 124.3927 | 124.3744 | -0.19684 | 124.1226 | 0.013733 | 0.28381 | 124.3881 | 124.53 | 124.3744 | 124.5209 | 124.3927 | 124.585 | 124.411 | 124.1226 | 124.5209 | 124.3927 | 124.411 | 124.3744 | 124.585 | -0.46234 | -0.44861
1208.375 | 124.5895 | -124.3607 | 0.18768 | -0.22568 | 0.0083164 | 0.012102 | 0.045598 | 0.0042746 | -0.00089719 | 0.015767 | 0.022888 | 0.17395 | -0.23804 | 0.027466 | 0.027466 | 0.036621 | 0.032043 | 0.1831 | 0.23346 | -0.25635 | 124.1226 | -0.013733 | 124.3835 | 124.3881 | -0.16022 | 124.1043 | 0.045776 | 0.26093 | 124.3927 | 124.5438 | 124.3881 | 124.5346 | 124.3835 | 124.5941 | 124.3973 | 124.1043 | 124.5346 | 124.3835 | 124.3973 | 124.3881 | 124.5941 | -0.42572 | -0.44403
1209.375 | 124.5666 | -124.3423 | 0.21515 | -0.14175 | 0.0095982 | 0.016588 | 0.046239 | 0.002352 | -0.0026062 | 0.017049 | 0.21973 | 0.20142 | -0.18768 | 0.045776 | 0.059509 | 0.036621 | 0.027466 | 0.18768 | 0.27924 | -0.18768 | 124.1547 | -0.013733 | 124.5621 | 124.3881 | -0.15564 | 124.1547 | 0.064087 | 0.40741 | 124.3698 | 124.53 | 124.4019 | 124.5438 | 124.5621 | 124.6216 | 124.379 | 124.1547 | 124.5438 | 124.5621 | 124.379 | 124.4019 | 124.6216 | -0.40283 | -0.40283
1210.375 | 124.5483 | -124.3652 | 0.19684 | -0.080719 | 0.0089572 | 0.016588 | 0.046666 | 0.0044882 | -0.0019654 | 0.014058 | 0.041199 | 0.17853 | -0.22888 | 0.022888 | 0.004578 | 0.009155 | 0.018311 | 0.13733 | 0.2243 | -0.25635 | 124.1364 | -0.01831 | 124.4064 | 124.3881 | -0.19226 | 124.1089 | 0.027466 | 0.27008 | 124.3835 | 124.5026 | 124.3698 | 124.5438 | 124.4064 | 124.5895 | 124.3744 | 124.1089 | 124.5438 | 124.4064 | 124.3744 | 124.3698 | 124.5895 | -0.42572 | -0.45319
1211.375 | 124.5987 | -124.3561 | 0.20599 | -0.088349 | 0.0059666 | 0.017656 | 0.044957 | 0.00342 | -0.002179 | 0.013845 | 0.036621 | 0.1831 | -0.21973 | 0.073242 | 0.032043 | 0.086975 | 0.027466 | 0.20599 | 0.27008 | -0.16022 | 124.1364 | -0.022889 | 124.3927 | 124.4293 | -0.17395 | 124.1959 | 0.064087 | 0.25635 | 124.3835 | 124.5621 | 124.3881 | 124.5392 | 124.3927 | 124.6262 | 124.4431 | 124.1959 | 124.5392 | 124.3927 | 124.4431 | 124.3881 | 124.6262 | -0.42572 | -0.36621
1212.375 | 124.5529 | -124.3652 | 0.20599 | -0.027313 | 0.00853 | 0.017442 | 0.046239 | 0.00577 | -0.0017518 | 0.01534 | 0.050354 | 0.17395 | -0.25177 | 0.013733 | 0.013733 | 0.032043 | 0.022888 | 0.14191 | 0.2243 | -0.24719 | 124.1135 | -0.032044 | 124.4156 | 124.379 | -0.19226 | 124.118 | 0.01831 | 0.30212 | 124.3881 | 124.5071 | 124.379 | 124.5392 | 124.4156 | 124.5895 | 124.3973 | 124.118 | 124.5392 | 124.4156 | 124.3973 | 124.379 | 124.5895 | -0.45776 | -0.45319
1213.375 | 124.5758 | -124.3561 | 0.20599 | -0.095978 | 0.0083164 | 0.015092 | 0.043889 | 0.0044882 | -0.0019654 | 0.016836 | 0.045776 | 0.17395 | -0.23804 | -0.009155 | 0.004578 | 0.032043 | 0.013733 | 0.14191 | 0.23804 | -0.24719 | 124.118 | -0.032044 | 124.4019 | 124.3469 | -0.20142 | 124.1089 | 0.032043 | 0.28381 | 124.3698 | 124.498 | 124.3607 | 124.53 | 124.4019 | 124.5941 | 124.3881 | 124.1089 | 124.53 | 124.4019 | 124.3881 | 124.3607 | 124.5941 | -0.44403 | -0.45319
1214.375 | 124.5758 | -124.3423 | 0.24261 | -0.13412 | 0.010025 | 0.015306 | 0.046666 | 0.0029928 | 0.00059821 | 0.013845 | 0.045776 | 0.16937 | -0.28381 | 0.064087 | 0.10986 | 0.054932 | 0.059509 | 0.19684 | 0.27466 | -0.14648 | 124.0585 | -0.073242 | 124.3881 | 124.4064 | -0.13275 | 124.1959 | 0.032043 | 0.32959 | 124.4019 | 124.5392 | 124.4522 | 124.5117 | 124.3881 | 124.617 | 124.3973 | 124.1959 | 124.5117 | 124.3881 | 124.3973 | 124.4522 | 124.617 | -0.52643 | -0.3891
1215.375 | 124.6124 | -124.3652 | 0.25177 | -0.11887 | 0.0083164 | 0.016588 | 0.044957 | 0.0010702 | -0.00046999 | 0.014272 | 0.054932 | 0.17853 | -0.27466 | 0.068665 | 0.091553 | 0.032043 | 0.059509 | 0.18768 | 0.28381 | -0.15564 | 124.0906 | -0.073242 | 124.4202 | 124.4339 | -0.16022 | 124.2096 | 0.032043 | 0.32959 | 124.4247 | 124.5529 | 124.4568 | 124.5438 | 124.4202 | 124.649 | 124.3973 | 124.2096 | 124.5438 | 124.4202 | 124.3973 | 124.4568 | 124.649 | -0.52643 | -0.40741
1216.4375 | 124.5483 | -124.3652 | 0.21515 | -0.23331 | 0.0089572 | 0.011034 | 0.041753 | 0.002352 | 0.00059821 | 0.016622 | -0.004578 | 0.17395 | -0.25177 | -0.013733 | -0.018311 | 0 | 0.09613 | 0.14191 | 0.2243 | -0.22888 | 124.1135 | -0.041199 | 124.3607 | 124.3515 | -0.23346 | 124.1364 | 0.009155 | 0.24719 | 124.4614 | 124.5071 | 124.3469 | 124.5392 | 124.3607 | 124.5895 | 124.3652 | 124.1364 | 124.5392 | 124.3607 | 124.3652 | 124.3469 | 124.5895 | -0.46692 | -0.44403
1217.375 | 124.5941 | -124.3607 | 0.20142 | -0.13412 | 0.00853 | 0.01552 | 0.044957 | 0.005129 | -0.0011108 | 0.016408 | 0.050354 | 0.15564 | -0.23804 | 0.013733 | 0.009155 | 0.018311 | 0.013733 | 0.14191 | 0.2243 | -0.23346 | 124.1226 | -0.045776 | 124.411 | 124.3744 | -0.19226 | 124.1272 | 0.022888 | 0.28839 | 124.3744 | 124.5026 | 124.3698 | 124.5163 | 124.411 | 124.585 | 124.379 | 124.1272 | 124.5163 | 124.411 | 124.379 | 124.3698 | 124.585 | -0.43945 | -0.43488
1218.375 | 124.5621 | -124.3607 | 0.1831 | -0.06546 | 0.01088 | 0.011888 | 0.043889 | 0.0025656 | -0.00089719 | 0.017904 | 0.059509 | 0.17853 | -0.23804 | 0 | 0 | 0.013733 | 0.004578 | 0.15564 | 0.21057 | -0.24261 | 124.1226 | -0.004577 | 124.4202 | 124.3607 | -0.1831 | 124.118 | 0.027466 | 0.29755 | 124.3652 | 124.5163 | 124.3607 | 124.5392 | 124.4202 | 124.5712 | 124.3744 | 124.118 | 124.5392 | 124.4202 | 124.3744 | 124.3607 | 124.5712 | -0.42114 | -0.42572
1219.4375 | 124.5666 | -124.3652 | 0.19684 | -0.20279 | 0.0078892 | 0.017656 | 0.041112 | 0.00342 | 0.00038461 | 0.013418 | -0.013733 | 0.17395 | -0.23346 | -0.018311 | 0 | -0.004578 | 0.07782 | 0.15564 | 0.25635 | -0.2655 | 124.1318 | -0.022888 | 124.3515 | 124.3469 | -0.19684 | 124.0997 | 0.05951 | 0.21973 | 124.4431 | 124.5209 | 124.3652 | 124.5392 | 124.3515 | 124.6216 | 124.3607 | 124.0997 | 124.5392 | 124.3515 | 124.3607 | 124.3652 | 124.6216 | -0.4303 | -0.46234
1220.375 | 124.5209 | -124.3515 | 0.20142 | -0.019684 | 0.0098118 | 0.018083 | 0.046239 | 0.0029928 | -0.0011108 | 0.014058 | 0.013733 | 0.16479 | -0.24719 | -0.036621 | -0.041199 | -0.013733 | 0.050354 | 0.10529 | 0.22888 | -0.2655 | 124.1043 | -0.036621 | 124.3652 | 124.3149 | -0.24262 | 124.086 | 0.027466 | 0.26093 | 124.4019 | 124.4568 | 124.3103 | 124.5163 | 124.3652 | 124.5804 | 124.3378 | 124.086 | 124.5163 | 124.3652 | 124.3378 | 124.3103 | 124.5804 | -0.44861 | -0.46692
1221.375 | 124.5895 | -124.3423 | 0.21515 | -0.1265 | 0.010025 | 0.015092 | 0.043462 | 0.0042746 | -0.0043152 | 0.017904 | 0.054932 | 0.16022 | -0.23804 | 0.004578 | 0.004578 | 0.032043 | 0.013733 | 0.15564 | 0.2243 | -0.24719 | 124.1043 | -0.054932 | 124.3973 | 124.3469 | -0.21057 | 124.0952 | 0.009155 | 0.29297 | 124.3561 | 124.498 | 124.3469 | 124.5026 | 124.3973 | 124.5667 | 124.3744 | 124.0952 | 124.5026 | 124.3973 | 124.3744 | 124.3469 | 124.5667 | -0.45319 | -0.46234
1222.375 | 124.5666 | -124.3652 | 0.19684 | -0.10361 | 0.00853 | 0.018938 | 0.043248 | 0.0038474 | 0.0010254 | 0.014486 | 0.059509 | 0.16022 | -0.25635 | 0 | 0.004578 | 0.013733 | 0 | 0.14648 | 0.21973 | -0.25177 | 124.1089 | -0.036621 | 124.4247 | 124.3652 | -0.19226 | 124.1135 | 0.022889 | 0.31586 | 124.3652 | 124.5117 | 124.3698 | 124.5255 | 124.4247 | 124.585 | 124.379 | 124.1135 | 124.5255 | 124.4247 | 124.379 | 124.3698 | 124.585 | -0.45319 | -0.44861
1223.375 | 124.53 | -124.4019 | 0.16937 | -0.027313 | 0.0091708 | 0.018297 | 0.04453 | 0.00342 | -0.00089719 | 0.015127 | 0.013733 | 0.17395 | -0.23804 | -0.027466 | -0.036621 | -0.027466 | 0.027466 | 0.091553 | 0.24261 | -0.25177 | 124.1638 | 0.004577 | 124.4156 | 124.3744 | -0.20599 | 124.1501 | 0.073242 | 0.25177 | 124.4293 | 124.4934 | 124.3652 | 124.5758 | 124.4156 | 124.6445 | 124.3744 | 124.1501 | 124.5758 | 124.4156 | 124.3744 | 124.3652 | 124.6445 | -0.40741 | -0.42114
1224.375 | 124.5575 | -124.3835 | 0.18768 | -0.057831 | 0.0087436 | 0.011247 | 0.043034 | 0.0042746 | -0.0011108 | 0.015981 | 0.018311 | 0.17853 | -0.24261 | -0.036621 | -0.036621 | -0.018311 | 0.032043 | 0.10071 | 0.2243 | -0.2655 | 124.1409 | -0.009155 | 124.4019 | 124.3469 | -0.2243 | 124.118 | 0.036621 | 0.26093 | 124.4156 | 124.4843 | 124.3469 | 124.5621 | 124.4019 | 124.6078 | 124.3652 | 124.118 | 124.5621 | 124.4019 | 124.3652 | 124.3469 | 124.6078 | -0.4303 | -0.45319
1225.375 | 124.53 | -124.3698 | 0.1831 | -0.027313 | 0.011307 | 0.014665 | 0.042607 | 0.0049154 | -0.00046999 | 0.014486 | 0.013733 | 0.17395 | -0.23804 | -0.032043 | -0.032043 | -0.022888 | 0.018311 | 0.09613 | 0.2243 | -0.2655 | 124.1318 | -0.009155 | 124.3835 | 124.3378 | -0.21515 | 124.1043 | 0.041199 | 0.25177 | 124.3881 | 124.4659 | 124.3378 | 124.5438 | 124.3835 | 124.5941 | 124.3469 | 124.1043 | 124.5438 | 124.3835 | 124.3469 | 124.3378 | 124.5941 | -0.42114 | -0.44861
1226.375 | 124.53 | -124.3835 | 0.21515 | 0.064239 | 0.0093844 | 0.019365 | 0.044316 | 0.0047018 | 0.0052978 | 0.016836 | -0.022888 | 0.16937 | -0.24719 | -0.10071 | 0.16022 | 0.14191 | -0.059509 | 0.21057 | 0.23346 | -0.23346 | 124.1364 | -0.045776 | 124.3607 | 124.2828 | -0.054932 | 124.1501 | 0.01831 | 0.2243 | 124.324 | 124.5941 | 124.5438 | 124.5529 | 124.3607 | 124.617 | 124.5255 | 124.1501 | 124.5529 | 124.3607 | 124.5255 | 124.5438 | 124.617 | -0.46234 | -0.44861
1227.375 | 124.4797 | -124.3332 | 0.23346 | 0.10239 | 0.010453 | 0.018724 | 0.043889 | 0.0053426 | -0.0015382 | 0.014699 | -0.009155 | 0.16022 | -0.23346 | -0.054932 | -0.032043 | 0.16937 | -0.26093 | 0.1236 | 0.22888 | -0.21515 | 124.0997 | -0.073242 | 124.324 | 124.2783 | -0.2655 | 124.118 | -0.004577 | 0.2243 | 124.0723 | 124.4568 | 124.3011 | 124.4934 | 124.324 | 124.5621 | 124.5026 | 124.118 | 124.4934 | 124.324 | 124.5026 | 124.3011 | 124.5621 | -0.46692 | -0.44861
1228.375 | 124.5438 | -124.3561 | 0.18768 | -0.027313 | 0.0098118 | 0.01787 | 0.042393 | 0.0032064 | 0.00038461 | 0.015554 | 0.045776 | 0.16022 | -0.2243 | -0.013733 | -0.018311 | 0 | 0.009155 | 0.12817 | 0.23346 | -0.25177 | 124.1318 | -0.027466 | 124.4019 | 124.3423 | -0.20599 | 124.1043 | 0.045776 | 0.27008 | 124.3652 | 124.4843 | 124.3378 | 124.5163 | 124.4019 | 124.5895 | 124.3561 | 124.1043 | 124.5163 | 124.4019 | 124.3561 | 124.3378 | 124.5895 | -0.41199 | -0.43945
1229.375 | 124.5712 | -124.3652 | 0.17395 | 0.033722 | 0.0081028 | 0.016374 | 0.042607 | 0.004061 | -0.00046999 | 0.016836 | 0.041199 | 0.15564 | -0.23804 | 0.013733 | -0.013733 | 0 | 0.009155 | 0.1236 | 0.24719 | -0.24719 | 124.1272 | -0.01831 | 124.4064 | 124.379 | -0.18768 | 124.118 | 0.073242 | 0.27924 | 124.3744 | 124.4888 | 124.3515 | 124.5209 | 124.4064 | 124.6124 | 124.3652 | 124.118 | 124.5209 | 124.4064 | 124.3652 | 124.3515 | 124.6124 | -0.41199 | -0.42114
1230.375 | 124.5346 | -124.3561 | 0.21057 | 0.010834 | 0.011734 | 0.014452 | 0.044102 | 0.0036336 | -0.0013244 | 0.016622 | 0.009155 | 0.16937 | -0.2655 | -0.041199 | -0.032043 | -0.018311 | 0.022888 | 0.086975 | 0.21057 | -0.25177 | 124.0906 | -0.041198 | 124.3652 | 124.3149 | -0.24261 | 124.1043 | 0 | 0.27466 | 124.379 | 124.4431 | 124.324 | 124.5255 | 124.3652 | 124.5666 | 124.3378 | 124.1043 | 124.5255 | 124.3652 | 124.3378 | 124.324 | 124.5666 | -0.47607 | -0.46234
1231.375 | 124.5575 | -124.379 | 0.19684 | 0.026092 | 0.012375 | 0.010179 | 0.040684 | 0.0038474 | -4.2788e-05 | 0.012349 | 0.009155 | 0.15106 | -0.24261 | -0.054932 | -0.041199 | -0.022888 | 0.059509 | 0.10529 | 0.21057 | -0.2655 | 124.1364 | -0.045776 | 124.3881 | 124.324 | -0.23804 | 124.1135 | 0.013733 | 0.25177 | 124.4385 | 124.4843 | 124.3378 | 124.53 | 124.3881 | 124.5895 | 124.3561 | 124.1135 | 124.53 | 124.3881 | 124.3561 | 124.3378 | 124.5895 | -0.43945 | -0.46234
1232.375 | 124.5392 | -124.3744 | 0.19684 | 0.010834 | 0.010025 | 0.014024 | 0.043462 | 0.0059836 | -0.0026062 | 0.015767 | 0.018311 | 0.17853 | -0.24719 | -0.036621 | -0.027466 | -0.013733 | 0.032043 | 0.10071 | 0.21973 | -0.26093 | 124.1272 | -0.01831 | 124.3927 | 124.3378 | -0.2243 | 124.1135 | 0.022889 | 0.2655 | 124.4064 | 124.4751 | 124.3469 | 124.5529 | 124.3927 | 124.5941 | 124.3607 | 124.1135 | 124.5529 | 124.3927 | 124.3607 | 124.3469 | 124.5941 | -0.44403 | -0.45776
1233.375 | 124.5666 | -124.3973 | 0.21973 | 0.087128 | 0.011948 | 0.019151 | 0.041753 | 0.0036336 | -0.00025639 | 0.020467 | -0.022888 | 0.17395 | -0.24261 | -0.12817 | -0.2243 | -0.07782 | 0.23346 | 0.018311 | 0.24719 | -0.22888 | 124.1547 | -0.045777 | 124.3744 | 124.2691 | -0.44403 | 124.1684 | 0.027465 | 0.21973 | 124.6307 | 124.4156 | 124.173 | 124.5712 | 124.3744 | 124.6445 | 124.3195 | 124.1684 | 124.5712 | 124.3744 | 124.3195 | 124.173 | 124.6445 | -0.46234 | -0.44861
1234.375 | 124.4247 | -124.3423 | 0.21973 | -0.034943 | 0.01323 | 0.018297 | 0.039616 | 0.002352 | 0.0018798 | 0.013845 | -0.013733 | 0.17853 | -0.24719 | -0.050354 | -0.045776 | -0.027466 | 0.054932 | 0.068665 | 0.23804 | -0.23804 | 124.0952 | -0.041199 | 124.3286 | 124.292 | -0.2655 | 124.1043 | 0.01831 | 0.23346 | 124.3973 | 124.411 | 124.2966 | 124.5209 | 124.3286 | 124.5804 | 124.3149 | 124.1043 | 124.5209 | 124.3286 | 124.3149 | 124.2966 | 124.5804 | -0.46692 | -0.45776
1235.4375 | 124.6262 | -124.3744 | 0.20142 | -0.20279 | 0.011948 | 0.015092 | 0.041966 | 0.0025656 | -0.00089719 | 0.014058 | 0.059509 | 0.16937 | -0.25177 | 0.027466 | 0.036621 | 0.022888 | 0.018311 | 0.1831 | 0.21515 | -0.24719 | 124.1226 | -0.032043 | 124.4339 | 124.4019 | -0.1648 | 124.1272 | 0.013733 | 0.31128 | 124.3927 | 124.5575 | 124.411 | 124.5438 | 124.4339 | 124.5895 | 124.3973 | 124.1272 | 124.5438 | 124.4339 | 124.3973 | 124.411 | 124.5895 | -0.45319 | -0.44861
1236.375 | 124.5621 | -124.3469 | 0.20142 | -0.07309 | 0.012375 | 0.017015 | 0.043889 | 0.0025656 | 0.00059821 | 0.014699 | 0.050354 | 0.16937 | -0.2243 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | 0.15564 | 0.23346 | -0.2243 | 124.1226 | -0.032043 | 124.3973 | 124.3652 | -0.18311 | 124.1226 | 0.032043 | 0.27466 | 124.3652 | 124.5026 | 124.3652 | 124.5163 | 124.3973 | 124.5804 | 124.3652 | 124.1226 | 124.5163 | 124.3973 | 124.3652 | 124.3652 | 124.5804 | -0.42572 | -0.42572
1237.375 | 124.5529 | -124.3881 | 0.20142 | 0.0032044 | 0.012802 | 0.017229 | 0.041325 | 0.0038474 | -0.002179 | 0.015127 | 0.022888 | 0.15106 | -0.24261 | -0.036621 | -0.036621 | -0.041199 | 0.032043 | 0.11444 | 0.21973 | -0.24719 | 124.1455 | -0.050354 | 124.411 | 124.3515 | -0.23804 | 124.1409 | 0.018311 | 0.2655 | 124.4202 | 124.5026 | 124.3515 | 124.5392 | 124.411 | 124.6078 | 124.3469 | 124.1409 | 124.5392 | 124.411 | 124.3469 | 124.3515 | 124.6078 | -0.44403 | -0.44861
1238.375 | 124.5666 | -124.3927 | 0.19226 | -0.0044251 | 0.012375 | 0.014452 | 0.041753 | 0.0044882 | -0.0013244 | 0.014913 | 0.045776 | 0.16022 | -0.24261 | -0.027466 | -0.009155 | 0.004578 | 0.036621 | 0.10986 | 0.23346 | -0.26093 | 124.1501 | -0.032044 | 124.4385 | 124.3652 | -0.20142 | 124.1318 | 0.041198 | 0.28839 | 124.4293 | 124.5026 | 124.3835 | 124.5529 | 124.4385 | 124.6262 | 124.3973 | 124.1318 | 124.5529 | 124.4385 | 124.3973 | 124.3835 | 124.6262 | -0.43488 | -0.45319
1239.3906 | 124.6445 | -124.3561 | 0.10986 | -0.0044251 | 0.0083164 | 0.015306 | 0.032353 | 0.0012838 | -0.0011108 | 0.011281 | 0.009155 | 0.11444 | -0.21973 | -0.11444 | 0.054932 | -0.018311 | -0.013733 | 0.13733 | 0.15564 | -0.2243 | 124.1364 | 0.004578 | 124.3652 | 124.2416 | -0.054931 | 124.1318 | 0.045777 | 0.22888 | 124.3423 | 124.4934 | 124.411 | 124.4705 | 124.3652 | 124.5117 | 124.3378 | 124.1318 | 124.4705 | 124.3652 | 124.3378 | 124.411 | 124.5117 | -0.32959 | -0.33417
1240.375 | 124.5438 | -124.3698 | 0.17853 | -0.012055 | 0.013657 | 0.014452 | 0.042607 | 0.00085662 | -0.0017518 | 0.015767 | 0.022888 | 0.17395 | -0.24719 | -0.036621 | -0.041199 | -0.022888 | 0.036621 | 0.10986 | 0.20142 | -0.26093 | 124.1226 | -0.004578 | 124.3927 | 124.3332 | -0.21973 | 124.1089 | 0.022888 | 0.27008 | 124.4064 | 124.4797 | 124.3286 | 124.5438 | 124.3927 | 124.5712 | 124.3469 | 124.1089 | 124.5438 | 124.3927 | 124.3469 | 124.3286 | 124.5712 | -0.42572 | -0.43945
1241.4375 | 124.585 | -124.3698 | 0.17853 | -0.088349 | 0.011734 | 0.014452 | 0.043248 | 0.001711 | -0.0023926 | 0.013845 | 0.059509 | 0.16479 | -0.23804 | 0.009155 | 0.022888 | 0.022888 | 0.009155 | 0.16479 | 0.2243 | -0.24261 | 124.1318 | -0.013733 | 124.4293 | 124.379 | -0.15564 | 124.1272 | 0.045776 | 0.29755 | 124.379 | 124.5346 | 124.3927 | 124.5346 | 124.4293 | 124.5941 | 124.3927 | 124.1272 | 124.5346 | 124.4293 | 124.3927 | 124.3927 | 124.5941 | -0.41656 | -0.42114
1242.375 | 124.5895 | -124.3286 | 0.19684 | -0.16464 | 0.010025 | 0.012743 | 0.041539 | 0.0036336 | -0.0023926 | 0.013631 | 0.050354 | 0.21057 | -0.12817 | 0.050354 | 0.009155 | 0.059509 | -0.004578 | 0.17395 | 0.25177 | -0.19684 | 124.2004 | 0.013733 | 124.379 | 124.379 | -0.18768 | 124.1318 | 0.054932 | 0.17853 | 124.324 | 124.5026 | 124.3378 | 124.5392 | 124.379 | 124.5804 | 124.3881 | 124.1318 | 124.5392 | 124.379 | 124.3881 | 124.3378 | 124.5804 | -0.32501 | -0.39368
1243.375 | 124.6353 | -124.2874 | 0.2655 | -0.32486 | 0.010239 | 0.019365 | 0.04218 | 0.0042746 | -0.0013244 | 0.015767 | 0.054932 | 0.15564 | -0.25635 | 0.032043 | 0.022888 | 0.036621 | 0.022888 | 0.23346 | 0.24261 | -0.21515 | 124.0311 | -0.10986 | 124.3423 | 124.3195 | -0.24261 | 124.0723 | -0.022888 | 0.31128 | 124.3103 | 124.5209 | 124.3103 | 124.4431 | 124.3423 | 124.53 | 124.324 | 124.0723 | 124.4431 | 124.3423 | 124.324 | 124.3103 | 124.53 | -0.52185 | -0.48065
1244.3906 | 124.7086 | -124.3744 | 0.11902 | 0.14816 | 0.0091708 | 0.01317 | 0.038548 | 0.00577 | -0.00025639 | 0.017049 | 0.086975 | 0.11444 | -0.21057 | 0.064087 | -0.041199 | -0.10986 | -0.1831 | 0.42114 | 0.14648 | -0.22888 | 124.1638 | -0.004578 | 124.4614 | 124.4385 | -0.16022 | 124.1455 | 0.027465 | 0.29755 | 124.1913 | 124.7955 | 124.3332 | 124.4888 | 124.4614 | 124.5209 | 124.2645 | 124.1455 | 124.4888 | 124.4614 | 124.2645 | 124.3332 | 124.5209 | -0.32959 | -0.3479
1245.375 | 124.585 | -124.3332 | 0.25177 | -0.14938 | 0.011307 | 0.01082 | 0.043034 | 0.0014974 | -0.0023926 | 0.013418 | 0.050354 | 0.17395 | -0.23346 | 0.032043 | 0.21973 | 0.082397 | 0.27008 | 0.1831 | 0.25635 | -0.13275 | 124.0997 | -0.07782 | 124.3835 | 124.3652 | -0.032043 | 124.2004 | 0.004578 | 0.28381 | 124.6033 | 124.5163 | 124.5529 | 124.5071 | 124.3835 | 124.5895 | 124.4156 | 124.2004 | 124.5071 | 124.3835 | 124.4156 | 124.5529 | 124.5895 | -0.48523 | -0.38452

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2 | Armor
-0.5583 | 23.1037 | 22.0268 | 22.1908 | 22.318
0.4417 | 23.1045 | 22.022 | 22.1867 | 22.3231
1.4417 | 23.1058 | 22.03 | 22.1926 | 22.3174
2.4417 | 23.1015 | 22.0251 | 22.1913 | 22.3194
3.4417 | 23.1354 | 22.0208 | 22.1943 | 22.3233
4.4417 | 23.5818 | 22.0258 | 22.1882 | 22.3189
5.4417 | 24.8273 | 22.0325 | 22.1896 | 22.3185
6.4417 | 26.8667 | 22.0317 | 22.1921 | 22.3191
7.4417 | 29.5624 | 22.0263 | 22.1953 | 22.3203
8.4417 | 32.7977 | 22.0301 | 22.1942 | 22.3294
9.4417 | 36.4934 | 22.028 | 22.1873 | 22.3303
10.4417 | 40.504 | 22.0221 | 22.1941 | 22.3407
11.4417 | 44.8556 | 22.0209 | 22.1928 | 22.3528
12.4417 | 49.4541 | 22.0165 | 22.1902 | 22.37
13.4417 | 54.2212 | 22.0371 | 22.1947 | 22.3903
14.4417 | 59.1911 | 22.0296 | 22.1891 | 22.4124
15.4417 | 64.3005 | 22.0285 | 22.1878 | 22.4476
16.4417 | 69.5151 | 22.0325 | 22.1894 | 22.4812
17.4417 | 74.8723 | 22.0329 | 22.1946 | 22.5304
18.4417 | 80.3694 | 22.0309 | 22.1921 | 22.5797
19.4417 | 85.971 | 22.0347 | 22.1902 | 22.6437
20.4417 | 91.5687 | 22.0398 | 22.1877 | 22.7046
21.4417 | 97.2693 | 22.031 | 22.1908 | 22.7913
22.4417 | 103.0462 | 22.0361 | 22.1937 | 22.8781
23.4417 | 108.8808 | 22.039 | 22.1909 | 22.9775
24.4417 | 114.7875 | 22.0456 | 22.204 | 23.0831
25.4417 | 120.7099 | 22.0492 | 22.193 | 23.1988
26.4417 | 126.6581 | 22.0434 | 22.1968 | 23.3339
27.4417 | 132.6255 | 22.0469 | 22.1962 | 23.4547
28.4417 | 138.5319 | 22.0454 | 22.1964 | 23.598
29.4417 | 144.5147 | 22.0459 | 22.2026 | 23.7535
30.4417 | 150.4972 | 22.0495 | 22.2052 | 23.9278
31.4417 | 156.4136 | 22.0533 | 22.2079 | 24.1125
32.4417 | 162.3653 | 22.0524 | 22.2086 | 24.3114
33.4417 | 168.2258 | 22.067 | 22.2173 | 24.5187
34.4417 | 174.1287 | 22.0633 | 22.2098 | 24.7457
35.4417 | 180.1523 | 22.0698 | 22.218 | 24.9898
36.4417 | 186.0422 | 22.076 | 22.2284 | 25.2474
37.4417 | 191.9379 | 22.0768 | 22.2254 | 25.5221
38.4417 | 197.7698 | 22.0724 | 22.2319 | 25.8103
39.4417 | 203.6082 | 22.0753 | 22.2384 | 26.1206
40.4417 | 209.4105 | 22.0905 | 22.2389 | 26.4463
41.4417 | 215.3003 | 22.0884 | 22.2498 | 26.7924
42.4417 | 221.2191 | 22.0919 | 22.2571 | 27.1497
43.4417 | 226.9551 | 22.0965 | 22.2669 | 27.5345
44.4417 | 232.7301 | 22.1048 | 22.2695 | 27.9391
45.4417 | 238.4126 | 22.1071 | 22.2856 | 28.3674
46.4417 | 244.2033 | 22.1177 | 22.2874 | 28.7982
47.4417 | 250.0008 | 22.1226 | 22.2946 | 29.258
48.4417 | 255.7175 | 22.1335 | 22.3108 | 29.7308
49.4417 | 261.5047 | 22.1369 | 22.3218 | 30.2195
50.4417 | 267.1966 | 22.1407 | 22.3329 | 30.7339
51.4417 | 272.8863 | 22.1584 | 22.3465 | 31.2572
52.4417 | 278.5051 | 22.1665 | 22.3694 | 31.8101
53.4417 | 283.9695 | 22.1761 | 22.3837 | 32.3756
54.4417 | 289.3782 | 22.18 | 22.4004 | 32.9666
55.4417 | 294.8399 | 22.1939 | 22.4174 | 33.561
56.4417 | 300.2722 | 22.216 | 22.4435 | 34.1811
57.4417 | 305.6011 | 22.2285 | 22.4619 | 34.8084
58.4417 | 310.8196 | 22.2366 | 22.4901 | 35.4651
59.4417 | 316.2564 | 22.2482 | 22.5117 | 36.134
60.4417 | 321.6942 | 22.2631 | 22.5301 | 36.83
61.4417 | 327.0977 | 22.2833 | 22.5595 | 37.5437
62.4417 | 332.3509 | 22.3002 | 22.5824 | 38.2892
63.4417 | 337.726 | 22.3153 | 22.6119 | 39.0417
64.4417 | 343.056 | 22.3397 | 22.6519 | 39.8212
65.4417 | 348.1099 | 22.3616 | 22.6795 | 40.6068
66.4417 | 353.2108 | 22.3868 | 22.7191 | 41.4175
67.4417 | 358.3135 | 22.4062 | 22.7509 | 42.2514
68.4417 | 363.4159 | 22.425 | 22.7924 | 43.0948
69.4417 | 368.4406 | 22.4372 | 22.8313 | 43.9686
70.4417 | 373.353 | 22.4721 | 22.8752 | 44.8567
71.4417 | 378.3492 | 22.5026 | 22.9143 | 45.7775
72.4417 | 383.1913 | 22.5371 | 22.9643 | 46.7252
73.4417 | 388.2249 | 22.5574 | 23.0031 | 47.7222
74.4417 | 393.2186 | 22.5924 | 23.0523 | 48.7344
75.4417 | 398.0913 | 22.6308 | 23.0983 | 49.8007
76.4417 | 402.8522 | 22.6643 | 23.1565 | 50.9176
77.4417 | 407.7836 | 22.7068 | 23.2095 | 52.0874
78.4417 | 412.6209 | 22.7471 | 23.272 | 53.3016
79.4417 | 417.4262 | 22.7767 | 23.33 | 54.5644
80.4417 | 422.1357 | 22.8326 | 23.3972 | 55.8548
81.4417 | 426.8336 | 22.8656 | 23.4652 | 57.1987
82.4417 | 431.554 | 22.9117 | 23.5347 | 58.5679
83.4417 | 436.1637 | 22.9546 | 23.6067 | 59.9835
84.4417 | 440.8165 | 22.9995 | 23.6873 | 61.413
85.4417 | 445.3011 | 23.0423 | 23.7618 | 62.8825
86.4417 | 449.6846 | 23.1018 | 23.8475 | 64.3804
87.4417 | 454.2789 | 23.1482 | 23.934 | 65.919
88.4417 | 458.745 | 23.2126 | 24.0202 | 67.4835
89.4417 | 463.2823 | 23.2602 | 24.111 | 69.0587
90.4417 | 467.7058 | 23.3293 | 24.2049 | 70.66
91.4417 | 472.2133 | 23.3967 | 24.2966 | 72.283
92.4417 | 476.3572 | 23.4589 | 24.3973 | 73.937
93.4417 | 480.1731 | 23.5239 | 24.505 | 75.6177
94.4417 | 483.4116 | 23.5892 | 24.6067 | 77.356
95.4417 | 486.5989 | 23.661 | 24.7164 | 79.1351
96.4417 | 489.44 | 23.7273 | 24.8321 | 80.9358
97.4417 | 492.2876 | 23.8112 | 24.9412 | 82.7528
99.051 | 496.4394 | 23.9517 | 25.1383 | 85.6776
99.6135 | 497.6974 | 23.9938 | 25.2042 | 86.7313
100.4417 | 499.6803 | 24.0643 | 25.3119 | 88.3505
101.4417 | 502.0422 | 24.1494 | 25.4459 | 90.3321
102.4417 | 504.5084 | 24.2554 | 25.5803 | 92.4701
103.4417 | 507.1248 | 24.3408 | 25.7239 | 94.8392
104.4417 | 509.4541 | 24.4463 | 25.8628 | 97.3099
105.4417 | 511.5158 | 24.5476 | 26.0136 | 99.8715
106.4417 | 513.201 | 24.6597 | 26.1645 | 102.4689
107.4417 | 515.1622 | 24.7545 | 26.3097 | 105.1445
108.4417 | 516.8386 | 24.8618 | 26.4765 | 107.8702
109.4417 | 518.3044 | 24.9899 | 26.6368 | 110.6037
110.4417 | 519.5916 | 25.1032 | 26.8062 | 113.2326
111.4417 | 520.5349 | 25.2322 | 26.977 | 115.9349
112.4417 | 521.1635 | 25.3548 | 27.1532 | 119.045
113.4417 | 521.7924 | 25.485 | 27.3379 | 122.5413
114.4417 | 522.2828 | 25.6123 | 27.5223 | 126.1812
115.4417 | 522.6905 | 25.7571 | 27.7102 | 129.8653
116.4417 | 522.9811 | 25.8835 | 27.9064 | 133.8262
117.4417 | 523.3569 | 26.0317 | 28.1045 | 138.2558
118.4417 | 523.6785 | 26.1872 | 28.2964 | 142.1569
119.4417 | 523.6699 | 26.3355 | 28.5035 | 145.3938
120.4417 | 523.5675 | 26.4855 | 28.7128 | 148.2404
121.4417 | 523.4081 | 26.643 | 28.9246 | 151.0977
122.4417 | 523.446 | 26.8057 | 29.1388 | 154.2622
123.4417 | 523.5281 | 26.9634 | 29.3581 | 157.4773
124.4417 | 523.8648 | 27.1398 | 29.5787 | 160.803
125.4417 | 524.0534 | 27.3133 | 29.8001 | 164.1705
126.4417 | 524.3833 | 27.4873 | 30.0236 | 167.6709
127.4417 | 524.5521 | 27.6731 | 30.2573 | 171.3574
128.4417 | 524.9379 | 27.8656 | 30.4973 | 175.3323
129.4417 | 525.0618 | 28.0506 | 30.7249 | 179.4116
130.4417 | 525.2248 | 28.2495 | 30.9619 | 183.4983
131.4417 | 525.3989 | 28.4412 | 31.212 | 187.6122
132.4417 | 525.576 | 28.6458 | 31.4532 | 191.7642
133.4417 | 526.0617 | 28.8399 | 31.7034 | 195.8569
134.4417 | 526.4318 | 29.0503 | 31.9595 | 200.1192
135.4417 | 526.7233 | 29.2571 | 32.2148 | 204.4228
136.4417 | 526.9657 | 29.462 | 32.4757 | 208.7591
137.4417 | 526.9582 | 29.6812 | 32.7262 | 213.1408
138.4417 | 526.8751 | 29.9074 | 32.9899 | 217.4342
139.4417 | 526.9696 | 30.1196 | 33.2576 | 221.8191
140.4417 | 526.9887 | 30.3514 | 33.5256 | 225.9918
141.4417 | 527.3871 | 30.5717 | 33.7965 | 230.0453
142.4417 | 527.6018 | 30.8005 | 34.0789 | 233.8691
143.4417 | 527.7918 | 31.042 | 34.3671 | 237.5274
144.4417 | 527.9698 | 31.2833 | 34.6425 | 241.0877
145.4417 | 527.9058 | 31.5176 | 34.9415 | 244.6504
146.4417 | 527.9785 | 31.762 | 35.2279 | 248.1903
147.4417 | 527.9782 | 32.0119 | 35.5165 | 251.2424
148.4417 | 528.054 | 32.2713 | 35.8116 | 254.3205
149.4417 | 528.1416 | 32.5192 | 36.1146 | 257.3449
150.4417 | 528.2848 | 32.7808 | 36.4206 | 260.4084
151.4417 | 528.2723 | 33.0556 | 36.7326 | 263.458
152.4417 | 528.121 | 33.3175 | 37.043 | 266.3834
153.4417 | 528.1042 | 33.5897 | 37.364 | 269.1472
154.4417 | 528.061 | 33.8699 | 37.6982 | 271.8823
155.4417 | 528.1488 | 34.1486 | 38.0259 | 274.3223
156.4417 | 528.4035 | 34.4377 | 38.3575 | 276.8511
157.4417 | 528.7441 | 34.7361 | 38.6932 | 279.261
158.4417 | 528.7683 | 35.0198 | 39.0326 | 281.6308
159.4417 | 528.6688 | 35.3145 | 39.3857 | 283.8084
160.4417 | 528.7005 | 35.6161 | 39.7341 | 285.4184
161.4417 | 528.659 | 35.9142 | 40.0957 | 286.9524
162.4417 | 528.7379 | 36.2217 | 40.4389 | 288.5062
163.4417 | 528.8476 | 36.5379 | 40.8036 | 290.1824
164.4417 | 529.099 | 36.8524 | 41.1674 | 291.6478
165.4417 | 529.3792 | 37.1642 | 41.5388 | 292.9236
166.4417 | 529.2455 | 37.4987 | 41.928 | 294.3016
167.4417 | 529.0826 | 37.8305 | 42.3089 | 295.9711
168.4417 | 528.6855 | 38.1641 | 42.6993 | 297.9326
169.4417 | 528.6414 | 38.4947 | 43.0887 | 299.4985
170.4417 | 528.9119 | 38.8475 | 43.4761 | 301.0753
171.4417 | 528.8444 | 39.1898 | 43.8791 | 302.1586
172.4417 | 528.9297 | 39.545 | 44.2788 | 303.4796
173.4417 | 528.921 | 39.897 | 44.6928 | 304.8896
174.4417 | 528.7546 | 40.2628 | 45.1051 | 306.6408
175.4417 | 528.6925 | 40.6282 | 45.5258 | 308.1858
176.4417 | 528.6475 | 40.9906 | 45.9522 | 309.6948
177.4417 | 528.5904 | 41.3733 | 46.3835 | 310.6065
178.4417 | 528.5412 | 41.7549 | 46.8227 | 311.6971
179.4417 | 528.4429 | 42.1416 | 47.2829 | 312.7873
180.4417 | 528.4193 | 42.5205 | 47.7444 | 314.1297
181.4417 | 528.5584 | 42.9227 | 48.1998 | 315.4485
182.4417 | 528.6731 | 43.3222 | 48.6522 | 317.0699
183.4417 | 528.6352 | 43.7274 | 49.1145 | 318.114
184.4417 | 528.5616 | 44.1388 | 49.5714 | 319.0001
185.4417 | 528.7145 | 44.5422 | 50.0432 | 319.3763
186.4417 | 528.629 | 44.9561 | 50.5074 | 320.203
187.4417 | 528.7512 | 45.376 | 50.9769 | 320.6708
188.4417 | 528.8139 | 45.7973 | 51.4422 | 321.4166
189.4417 | 528.9098 | 46.2323 | 51.9047 | 322.2832
190.4417 | 528.9006 | 46.6611 | 52.378 | 323.1551
191.4417 | 528.7962 | 47.1 | 52.8487 | 324.1075
192.4417 | 528.8866 | 47.5414 | 53.3403 | 325.2729
193.4417 | 528.9796 | 47.9848 | 53.8148 | 325.4683
194.4417 | 529.179 | 48.4342 | 54.3029 | 326.0482
195.4417 | 529.2183 | 48.8735 | 54.7756 | 327.1801
196.4417 | 529.4644 | 49.3378 | 55.2692 | 328.4598
197.4417 | 529.6766 | 49.7989 | 55.7637 | 328.923
198.4417 | 529.665 | 50.2644 | 56.2749 | 329.4106
199.4417 | 529.5801 | 50.7292 | 56.7913 | 329.6156
200.4417 | 529.2455 | 51.2035 | 57.2933 | 330.1079
201.4417 | 529.4203 | 51.6744 | 57.8107 | 330.7188
202.4417 | 529.4757 | 52.1629 | 58.3218 | 331.0418
203.4417 | 529.5611 | 52.6375 | 58.8305 | 331.8324
204.4417 | 529.5785 | 53.122 | 59.3577 | 332.8636
205.4417 | 529.6274 | 53.6158 | 59.8991 | 333.5358
206.4417 | 529.7728 | 54.1101 | 60.4471 | 334.3037
207.4417 | 529.7593 | 54.6127 | 61.013 | 335.0391
208.4417 | 529.6718 | 55.1119 | 61.5337 | 336.2384
209.4417 | 529.8593 | 55.621 | 62.0694 | 337.4328
210.4417 | 530.0724 | 56.1304 | 62.6107 | 337.6617
211.4417 | 529.9899 | 56.6439 | 63.1633 | 337.5693
212.4417 | 530.0219 | 57.1621 | 63.7169 | 338.2369
213.4417 | 530.1475 | 57.6777 | 64.2881 | 339.4997
214.4417 | 530.2725 | 58.1913 | 64.8374 | 340.3953
215.4417 | 530.3052 | 58.7157 | 65.3971 | 341.5317
216.4417 | 530.3018 | 59.2283 | 65.9726 | 342.6538
217.4417 | 530.2446 | 59.7463 | 66.5431 | 342.8379
218.4417 | 530.4039 | 60.2772 | 67.0931 | 344.3022
219.4417 | 530.4533 | 60.7983 | 67.6594 | 345.0568
220.4417 | 530.1448 | 61.3192 | 68.2174 | 345.0255
221.4417 | 529.9573 | 61.8373 | 68.7694 | 346.4423
222.4417 | 529.7877 | 62.3647 | 69.3264 | 347.0378
223.4417 | 529.6743 | 62.8974 | 69.8927 | 347.6134
224.4417 | 529.512 | 63.4308 | 70.4682 | 348.7997
225.4417 | 529.5993 | 63.9549 | 71.016 | 350.1996
226.4417 | 529.3751 | 64.4933 | 71.5635 | 350.9772
227.4417 | 529.1772 | 65.0126 | 72.1204 | 352.0045
228.4417 | 529.3442 | 65.5425 | 72.6626 | 353.2472
229.4417 | 529.4358 | 66.0984 | 73.2111 | 355.0932
230.4417 | 529.289 | 66.6211 | 73.7578 | 356.0307
231.4417 | 529.1685 | 67.1564 | 74.3099 | 358.1381
232.4417 | 528.9806 | 67.6899 | 74.842 | 359.298
233.4417 | 528.7598 | 68.2304 | 75.3962 | 361.5734
234.4417 | 528.4314 | 68.7566 | 75.9331 | 363.635
235.4417 | 528.3445 | 69.2986 | 76.4841 | 365.9225
236.4417 | 528.4478 | 69.8327 | 77.035 | 368.0784
237.4417 | 528.4413 | 70.3729 | 77.5836 | 369.5479
238.4417 | 528.2643 | 70.9134 | 78.1198 | 371.1767
239.4417 | 528.063 | 71.4508 | 78.6345 | 372.6333
240.4417 | 528.1881 | 71.9919 | 79.1594 | 373.8547
241.4417 | 528.3706 | 72.5218 | 79.697 | 375.1419
242.4417 | 528.3375 | 73.0666 | 80.2413 | 377.0784
243.4417 | 528.358 | 73.6004 | 80.7886 | 378.8761
244.4417 | 528.1176 | 74.1478 | 81.3103 | 379.9946
245.4417 | 528.0517 | 74.691 | 81.851 | 380.5697
246.4417 | 527.9325 | 75.2433 | 82.351 | 382.2887
247.4417 | 527.8753 | 75.8009 | 82.885 | 383.0649
248.4417 | 528.0339 | 76.3546 | 83.3836 | 384.1539
249.4417 | 528.1884 | 76.8866 | 83.9133 | 385.1396
250.4417 | 528.2695 | 77.4561 | 84.4334 | 386.6548
251.4417 | 528.3904 | 78.007 | 84.9906 | 387.4892
252.4417 | 528.5975 | 78.561 | 85.5345 | 388.2668
253.4417 | 528.7118 | 79.1225 | 86.111 | 388.5971
254.4417 | 528.7645 | 79.6793 | 86.6171 | 389.9821
255.4417 | 528.7536 | 80.2283 | 87.1425 | 390.9647
256.4417 | 528.7857 | 80.7835 | 87.6023 | 390.8193
257.4417 | 528.6648 | 81.3386 | 88.0777 | 391.2927
258.4417 | 528.483 | 81.8938 | 88.6896 | 392.1885
259.4417 | 528.4408 | 82.4594 | 89.2378 | 393.2739
260.4417 | 528.4527 | 83.0122 | 89.7619 | 394.5766
261.4417 | 528.0703 | 83.5709 | 90.3502 | 395.0343
262.4417 | 527.983 | 84.1198 | 90.9272 | 395.6818
263.4417 | 528.1775 | 84.6749 | 91.4754 | 396.2699
264.4417 | 528.0659 | 85.2344 | 92.0103 | 396.8189
265.4417 | 528.015 | 85.787 | 92.5811 | 397.1771
266.4417 | 528.1177 | 86.3212 | 93.1322 | 398.1843
267.4417 | 528.119 | 86.8619 | 93.6605 | 398.0056
268.4417 | 528.1805 | 87.4042 | 94.0922 | 398.9314
269.4417 | 528.3328 | 87.941 | 94.5657 | 399.8183
270.4417 | 528.4082 | 88.453 | 95.0488 | 399.8547
271.4417 | 528.4804 | 88.9812 | 95.5232 | 399.8361
272.4417 | 528.4224 | 89.4933 | 95.9971 | 399.5114
273.4417 | 528.3928 | 90.0086 | 96.4735 | 399.7606
274.4417 | 528.2289 | 90.5135 | 96.978 | 399.6483
275.4417 | 528.2528 | 91.0251 | 97.496 | 400.9236
276.4417 | 527.7923 | 91.5543 | 98.0301 | 400.5986
277.4417 | 528.0087 | 92.0535 | 98.5692 | 400.9863
278.4417 | 527.8095 | 92.5717 | 99.1554 | 401.9299
279.4417 | 528.094 | 93.0981 | 99.8723 | 400.732
280.4417 | 528.1975 | 93.6284 | 100.4129 | 400.509
281.4417 | 528.2776 | 94.1787 | 100.9326 | 401.3401
282.4417 | 528.4166 | 94.7129 | 101.4546 | 401.2218
283.4417 | 528.6353 | 95.2694 | 102.0004 | 401.4475
284.4417 | 528.8201 | 95.827 | 102.5563 | 402.318
285.4417 | 528.9026 | 96.3845 | 103.1364 | 403.4761
286.4417 | 528.8283 | 96.9537 | 103.6947 | 403.7707
287.4417 | 528.8024 | 97.517 | 104.2747 | 404.3331
288.4417 | 528.8042 | 98.0744 | 104.8242 | 404.6391
289.4417 | 528.8012 | 98.6519 | 105.3955 | 404.5455
290.4417 | 528.9498 | 99.2323 | 105.9595 | 403.5952
291.4417 | 528.9047 | 99.7967 | 106.5185 | 403.8313
292.4417 | 528.8026 | 100.3611 | 107.0955 | 403.185
293.4417 | 528.7376 | 100.9252 | 107.66 | 403.0776
294.4417 | 528.6752 | 101.4784 | 108.2619 | 402.7993
295.4417 | 528.7439 | 102.0127 | 108.8474 | 402.8548
296.4417 | 528.7085 | 102.5704 | 109.4808 | 402.1027
297.4417 | 528.6463 | 103.1095 | 110.0556 | 401.4262
298.4417 | 528.7403 | 103.6689 | 110.6767 | 400.6318
299.4417 | 528.9226 | 104.1942 | 111.2795 | 399.9748
300.4417 | 529.1738 | 104.7187 | 111.8629 | 399.3413
301.4417 | 529.1889 | 105.2303 | 112.4818 | 398.385
302.4417 | 529.1869 | 105.7683 | 112.9317 | 398.0075
303.4417 | 529.2999 | 106.3055 | 113.678 | 398.3707
304.4417 | 529.5893 | 106.8244 | 114.7606 | 399.6944
305.4417 | 529.6647 | 107.3475 | 115.3209 | 399.814
306.4417 | 529.7764 | 107.8568 | 116.1593 | 399.8562
307.4417 | 529.8668 | 108.3763 | 116.7595 | 399.0942
308.4417 | 529.5795 | 108.8734 | 118.2501 | 398.2937
309.4417 | 529.5269 | 109.391 | 119.068 | 397.6841
310.4417 | 529.4798 | 109.9044 | 119.6883 | 397.9512
311.4417 | 529.3408 | 110.4191 | 120.1766 | 397.0126
312.4417 | 529.1145 | 110.9505 | 122.0081 | 396.874
313.4417 | 529.1343 | 111.476 | 122.537 | 396.5363
314.4417 | 529.0547 | 112.0386 | 123.3007 | 396.8931
315.4417 | 529.0268 | 112.607 | 123.8156 | 397.0329
316.4417 | 528.9411 | 113.1948 | 124.4672 | 396.4929
317.4417 | 528.803 | 113.7821 | 125.1162 | 395.9219
318.4417 | 528.7403 | 114.4141 | 125.624 | 395.5868
319.4417 | 528.7657 | 115.0991 | 126.4598 | 395.2874
320.4417 | 528.4963 | 115.8121 | 126.8359 | 394.2388
321.4417 | 528.5542 | 116.5559 | 127.6665 | 393.9406
322.4417 | 528.6301 | 117.3307 | 128.1931 | 393.8194
323.4417 | 528.5876 | 118.1056 | 129.1038 | 393.5116
324.4417 | 528.5637 | 118.92 | 129.6821 | 393.6159
325.4417 | 528.4956 | 119.7261 | 130.2876 | 393.6336
326.4417 | 528.3305 | 120.5318 | 130.6007 | 393.2806
327.4417 | 528.2145 | 121.3328 | 131.0548 | 393.3223
328.4417 | 527.9993 | 122.1384 | 131.6762 | 393.3002
329.4417 | 527.8224 | 122.9309 | 132.2683 | 393.8848
330.4417 | 527.8782 | 123.709 | 132.9084 | 394.9432
331.4417 | 527.9608 | 124.4806 | 133.5734 | 395.2337
332.4417 | 527.9567 | 125.2576 | 134.2654 | 394.6643
333.4417 | 528.0118 | 126.0102 | 134.9726 | 394.4925
334.4417 | 528.151 | 126.7645 | 135.623 | 395.0845
335.4417 | 528.1446 | 127.5187 | 136.2711 | 395.8817
336.4417 | 528.0618 | 128.2634 | 136.9279 | 395.7331
337.4417 | 528.1283 | 128.9998 | 137.6237 | 395.7486
338.4417 | 528.4626 | 129.7225 | 138.3287 | 396.0154
339.4417 | 528.5219 | 130.4524 | 139.0357 | 396.345
340.4417 | 528.553 | 131.1645 | 139.7002 | 396.5418
341.4417 | 528.6211 | 131.8792 | 140.4036 | 396.4874
342.4417 | 528.6219 | 132.5948 | 141.1271 | 395.5387
343.4417 | 528.6109 | 133.297 | 141.8569 | 395.1821
344.4417 | 528.6014 | 133.9928 | 142.5837 | 395.0152
345.4417 | 528.5509 | 134.6838 | 143.3215 | 394.4215
346.4417 | 528.6211 | 135.375 | 144.0311 | 394.8742
347.4417 | 528.5628 | 136.0657 | 144.7589 | 394.7861
348.4417 | 528.5332 | 136.7439 | 145.4579 | 395.0464
349.4417 | 528.5335 | 137.4285 | 146.162 | 394.3827
350.4417 | 528.4381 | 138.1133 | 146.8611 | 394.0444
351.4417 | 528.2014 | 138.7989 | 147.5818 | 395.085
352.4417 | 528.1129 | 139.47 | 148.2653 | 395.7525
353.4417 | 528.1328 | 140.1455 | 148.946 | 395.3529
354.4417 | 528.1343 | 140.7933 | 149.6346 | 396.3012
355.4417 | 527.8856 | 141.4596 | 150.3247 | 395.9871
356.4417 | 527.6783 | 142.1111 | 151.0168 | 396.2074
357.4417 | 527.7218 | 142.7558 | 151.6992 | 396.3702
358.4417 | 527.5434 | 143.3929 | 152.382 | 396.089
359.4417 | 527.632 | 144.0203 | 153.1051 | 395.336
360.4417 | 527.7102 | 144.6355 | 153.801 | 395.9187
361.4417 | 527.8055 | 145.2614 | 154.5036 | 395.4161
362.4885 | 527.8732 | 145.8943 | 155.2528 | 395.5966
363.4417 | 527.8772 | 146.4815 | 155.9477 | 395.3704
364.4417 | 528.0275 | 147.0966 | 156.6216 | 395.3486
365.4417 | 527.858 | 147.6988 | 157.2993 | 395.4961
366.4417 | 527.7613 | 148.3 | 157.9917 | 394.9564
367.4417 | 527.745 | 148.9097 | 158.7729 | 395.1763
368.4417 | 527.8707 | 149.5015 | 159.3699 | 395.278
369.4417 | 527.9517 | 150.0984 | 160.0017 | 394.7703
370.4417 | 527.9648 | 150.7113 | 160.7077 | 394.9354
371.4417 | 527.8683 | 151.3135 | 161.3698 | 395.0183
372.4417 | 527.938 | 151.9285 | 162.0103 | 394.9899
373.4417 | 527.922 | 152.5375 | 162.6637 | 394.8633
374.4417 | 528.1108 | 153.142 | 163.3074 | 396.0235
375.4417 | 528.374 | 153.7627 | 163.9714 | 396.4266
376.4417 | 528.317 | 154.3849 | 164.6809 | 395.9934
377.4417 | 528.2115 | 155.0015 | 165.4223 | 395.4399
378.4417 | 528.1301 | 155.6406 | 166.1945 | 395.7451
379.4417 | 527.9042 | 156.2998 | 166.9156 | 396.8865
380.4417 | 527.7832 | 156.9649 | 167.6845 | 396.9858
381.4417 | 527.7763 | 157.6276 | 168.4698 | 396.5953
382.4417 | 527.6238 | 158.3014 | 169.1491 | 396.8571
383.4417 | 527.4096 | 158.9821 | 169.9153 | 397.287
384.4417 | 527.5056 | 159.6671 | 170.6515 | 397.9844
385.4417 | 527.5581 | 160.3491 | 171.3902 | 397.5414
386.4417 | 527.4797 | 161.052 | 172.1272 | 398.6098
387.4417 | 527.3576 | 161.7665 | 172.1539 | 399.1794
388.4417 | 527.292 | 162.4878 | 172.6728 | 398.5754
389.4417 | 527.3646 | 163.2043 | 173.2717 | 398.3295
390.4417 | 527.4742 | 163.9257 | 173.9557 | 398.2884
391.4417 | 527.3222 | 164.6739 | 174.6775 | 398.5067
392.4417 | 527.197 | 165.4455 | 175.3787 | 398.4154
393.4417 | 527.1609 | 166.2203 | 176.0041 | 398.8209
394.4417 | 527.1902 | 166.9907 | 176.5831 | 399.0391
395.4417 | 527.1193 | 167.7665 | 177.2862 | 400.1922
396.4417 | 526.8758 | 168.5476 | 178.293 | 399.6973
397.4417 | 526.9054 | 169.3244 | 179.2049 | 399.8964
398.4417 | 526.8818 | 170.0987 | 180.2694 | 399.7504
399.4417 | 526.8875 | 170.8523 | 181.0667 | 399.2339
400.4417 | 526.9097 | 171.6005 | 181.8291 | 399.6577
401.4417 | 526.8571 | 172.3833 | 182.8274 | 399.9075
402.4417 | 526.8223 | 173.1191 | 183.8463 | 400.2438
403.4417 | 526.8442 | 173.8733 | 184.5895 | 399.7205
404.4417 | 526.7701 | 174.6182 | 185.3291 | 400.0019
405.4417 | 526.9111 | 175.3603 | 186.0777 | 400.4064
406.4417 | 526.8108 | 176.1005 | 186.8385 | 400.803
407.4417 | 526.8083 | 176.8372 | 187.6042 | 400.4784
408.4417 | 526.9976 | 177.571 | 188.3223 | 400.3808
409.4417 | 526.9925 | 178.2888 | 189.0322 | 399.9033
410.4417 | 527.1244 | 179.0022 | 189.7311 | 400.0533
411.4417 | 527.1928 | 179.7305 | 190.4275 | 399.8803
412.4417 | 527.3182 | 180.4449 | 191.1578 | 399.6547
413.4417 | 527.5538 | 181.1567 | 191.895 | 399.3212
414.4417 | 527.6655 | 181.8749 | 192.6163 | 399.9064
415.4417 | 527.6051 | 182.5764 | 193.3347 | 400.4134
416.4417 | 527.469 | 183.2735 | 194.0419 | 400.1009
417.4417 | 527.418 | 183.9744 | 194.7471 | 399.6359
418.4417 | 527.4266 | 184.6568 | 195.4283 | 399.3303
419.4417 | 527.4253 | 185.3664 | 196.058 | 399.1497
420.4417 | 527.5535 | 186.045 | 196.7033 | 399.3375
421.4417 | 527.6015 | 186.7338 | 197.3633 | 399.8758
422.4417 | 527.6035 | 187.413 | 198.0017 | 399.7889
423.4417 | 527.712 | 188.1028 | 198.5613 | 399.702
424.4417 | 527.7254 | 188.776 | 199.1677 | 400.3038
425.4417 | 527.8432 | 189.4514 | 199.8448 | 400.4071
426.4417 | 527.7662 | 190.1364 | 200.5424 | 401.4613
427.4417 | 527.4301 | 190.8092 | 201.228 | 401.9056
428.4417 | 527.5387 | 191.4743 | 201.9146 | 401.344
429.4417 | 527.6392 | 192.1414 | 202.5993 | 401.1942
430.4417 | 527.3218 | 192.7961 | 203.2834 | 401.1344
431.4417 | 527.3944 | 193.4503 | 203.9632 | 401.4583
432.4417 | 527.4011 | 194.0987 | 204.6451 | 402.1669
433.4417 | 527.3861 | 194.7389 | 205.3253 | 402.3472
434.4417 | 527.3419 | 195.382 | 205.991 | 401.9092
435.4417 | 527.3405 | 196.0228 | 206.6747 | 401.4696
436.4417 | 527.2957 | 196.6559 | 207.3465 | 401.8329
437.4417 | 527.1699 | 197.2613 | 208.0139 | 402.2395
438.4417 | 527.0679 | 197.8864 | 208.6845 | 401.9697
439.4417 | 527.1748 | 198.4954 | 209.3514 | 402.3317
440.4417 | 527.4094 | 199.0854 | 210.0109 | 402.1569
441.4417 | 527.4654 | 199.6849 | 210.6892 | 402.6937
442.4417 | 527.3179 | 200.2863 | 211.349 | 402.5624
443.4417 | 527.2652 | 200.8772 | 212.0099 | 402.4816
444.4417 | 527.3067 | 201.4775 | 212.6743 | 402.8975
445.4417 | 527.3967 | 202.0581 | 213.3332 | 402.2936
446.4417 | 527.4551 | 202.6462 | 213.9876 | 403.1252
447.4417 | 527.2332 | 203.2124 | 214.6453 | 404.2468
448.4417 | 527.1934 | 203.7972 | 215.2902 | 404.2046
449.4417 | 527.2427 | 204.3635 | 215.9334 | 405.066
450.4417 | 527.2883 | 204.9302 | 216.5803 | 404.9889
451.4417 | 527.1431 | 205.4947 | 217.2342 | 405.2987
452.4417 | 526.9471 | 206.0743 | 217.8796 | 405.6053
453.4417 | 526.9982 | 206.6618 | 218.5244 | 405.0189
454.4417 | 527.0821 | 207.2418 | 219.1716 | 405.1904
455.4417 | 527.0029 | 207.8389 | 219.8159 | 404.7575
456.4417 | 527.0041 | 208.442 | 220.456 | 404.9233
457.4417 | 526.9506 | 209.0626 | 221.0901 | 404.8018
458.4417 | 526.9876 | 209.6846 | 221.7199 | 405.7521
459.4417 | 526.8233 | 210.3243 | 222.3563 | 406.6247
460.4417 | 526.814 | 210.9397 | 222.9829 | 405.7136
461.4417 | 526.8002 | 211.5645 | 223.6104 | 405.2078
462.4417 | 526.8352 | 212.1926 | 224.2351 | 405.7133
463.4417 | 526.9622 | 212.8001 | 224.8613 | 405.3463
464.4417 | 527.0591 | 213.4206 | 225.4997 | 406.2182
465.4417 | 526.9421 | 214.0552 | 226.1163 | 407.2871
466.4417 | 526.7092 | 214.6911 | 226.7261 | 407.3081
467.4417 | 526.5988 | 215.3132 | 227.343 | 407.4119
468.4417 | 526.6206 | 215.939 | 227.9613 | 407.4954
469.4417 | 526.6683 | 216.5739 | 228.5689 | 407.4503
470.4417 | 526.751 | 217.2054 | 229.1662 | 407.2516
471.4417 | 526.8447 | 217.8327 | 229.7911 | 406.9431
472.4417 | 526.8902 | 218.4722 | 230.4041 | 407.1843
473.4417 | 527.0079 | 219.1141 | 231.02 | 408.4769
474.4417 | 526.8763 | 219.7516 | 231.6299 | 408.5633
475.4417 | 526.9161 | 220.3898 | 232.2321 | 409.0942
476.4417 | 526.9747 | 221.0486 | 232.8297 | 408.6512
477.4417 | 526.9047 | 221.6873 | 233.4409 | 408.5177
478.4417 | 526.9572 | 222.3391 | 234.0213 | 408.2923
479.4417 | 527.1298 | 222.9791 | 234.6189 | 408.8159
480.4417 | 527.0655 | 223.6155 | 235.2413 | 409.0968
481.4417 | 527.0963 | 224.2382 | 235.925 | 409.0747
482.4417 | 527.1998 | 224.8708 | 236.564 | 408.8884
483.4417 | 527.2642 | 225.5197 | 237.1729 | 408.7542
484.4417 | 527.1637 | 226.1602 | 237.7884 | 409.1995
485.4417 | 527.1468 | 226.7944 | 238.4495 | 409.543
486.4417 | 527.2597 | 227.4303 | 239.0753 | 409.6825
487.4417 | 527.2398 | 228.057 | 239.7094 | 410.3483
488.4417 | 527.1498 | 228.6883 | 240.3692 | 410.3336
489.4417 | 527.1041 | 229.3227 | 240.9228 | 410.5041
490.4417 | 527.1036 | 229.9612 | 241.4761 | 410.3556
491.4417 | 527.074 | 230.5891 | 241.9959 | 410.6506
492.4417 | 527.1951 | 231.2184 | 242.6768 | 410.2896
493.4417 | 527.1166 | 231.8537 | 243.0008 | 410.7251
494.4417 | 526.9696 | 232.545 | 243.5213 | 411.0656
495.4417 | 526.803 | 233.1591 | 244.0613 | 410.9292
496.4417 | 526.8995 | 233.7734 | 244.644 | 410.0244
497.4417 | 526.8349 | 234.389 | 245.2146 | 410.1011
498.4417 | 526.9023 | 234.9929 | 245.7689 | 409.6626
499.4417 | 526.8167 | 235.6124 | 246.327 | 410.2824
500.4417 | 526.7302 | 236.25 | 246.8711 | 409.8675
501.4417 | 526.804 | 236.8693 | 247.4253 | 410.0592
502.4417 | 527.0972 | 237.4931 | 247.9626 | 410.4952
503.4417 | 527.2638 | 238.1367 | 248.5112 | 410.7356
504.4417 | 527.2974 | 238.7405 | 249.0739 | 411.4055
505.4417 | 527.1209 | 239.355 | 249.611 | 411.6789
506.4417 | 526.9582 | 239.9674 | 250.2541 | 411.6634
507.4417 | 526.9701 | 240.6071 | 250.8025 | 411.9619
508.4417 | 526.9067 | 241.243 | 251.3415 | 411.1861
509.4417 | 526.8153 | 241.8696 | 251.8353 | 412.501
510.4417 | 526.9028 | 242.4797 | 252.3555 | 413.8475
511.4417 | 526.7322 | 243.1054 | 252.8893 | 414.0392
512.4417 | 526.5639 | 243.6273 | 253.4285 | 414.5891
513.4417 | 526.7322 | 244.0999 | 253.988 | 415.5109
514.4417 | 526.8686 | 244.6676 | 254.5372 | 415.4838
515.4417 | 526.9956 | 245.2761 | 255.0882 | 415.3243
516.4417 | 526.9096 | 245.9003 | 255.6192 | 415.3261
517.4417 | 526.7346 | 246.5384 | 256.1724 | 415.2905
518.4417 | 526.7318 | 247.1483 | 256.715 | 414.3227
519.4417 | 526.8951 | 247.7753 | 257.2663 | 414.1683
520.4417 | 526.879 | 248.3844 | 257.8772 | 413.4699
521.4417 | 526.7504 | 249.0069 | 258.4208 | 413.2461
522.4417 | 526.6683 | 249.47 | 258.9625 | 412.5419
523.4417 | 526.7691 | 249.9969 | 259.5541 | 412.0839
524.4417 | 526.9249 | 250.5624 | 260.0881 | 411.9864
525.4417 | 527.0135 | 251.1165 | 260.618 | 411.4393
526.4417 | 527.2423 | 251.6904 | 261.1532 | 411.2638
527.4417 | 527.1894 | 252.2627 | 261.6917 | 411.6053
528.4417 | 527.1217 | 252.8238 | 262.2247 | 411.6571
529.4417 | 527.1676 | 253.4052 | 262.7525 | 412.8648
530.4417 | 527.2813 | 254.0219 | 263.2707 | 413.577
531.4417 | 527.4043 | 254.6083 | 263.834 | 413.9975
532.4417 | 527.2512 | 255.1883 | 264.3552 | 413.7885
533.4417 | 527.2128 | 255.7693 | 264.8582 | 414.4179
534.4417 | 527.0126 | 256.3283 | 265.3866 | 414.1277
535.4417 | 527.1651 | 256.9011 | 265.9186 | 413.89
536.4417 | 527.1155 | 257.4583 | 266.4399 | 414.5555
537.4417 | 526.9303 | 258.0235 | 267.0847 | 415.1241
538.4417 | 526.5124 | 258.6185 | 267.5821 | 416.5174
539.4417 | 526.1768 | 259.1763 | 268.1589 | 416.6303
540.4417 | 526.2585 | 259.7447 | 268.6308 | 416.7332
541.4417 | 526.3676 | 260.3395 | 269.2397 | 415.8024
542.4573 | 526.3231 | 260.8928 | 269.8572 | 415.567
543.4417 | 526.3632 | 261.4258 | 270.335 | 416.3159
544.4417 | 526.1858 | 261.9589 | 270.8299 | 416.2667
545.4417 | 526.1573 | 262.5006 | 271.3243 | 416.0883
546.4417 | 526.2489 | 263.0135 | 271.7457 | 417.2749
547.4417 | 526.2548 | 263.5924 | 272.5306 | 416.9537
548.4417 | 526.2665 | 264.1352 | 272.9872 | 417.9952
549.4417 | 526.4002 | 264.682 | 273.3172 | 417.8144
550.4417 | 526.4958 | 265.2361 | 273.7247 | 417.9211
551.4417 | 526.5998 | 265.7971 | 274.2051 | 418.7244
552.4417 | 526.6218 | 266.3386 | 274.6319 | 418.9606
553.4417 | 526.6475 | 266.8862 | 275.0772 | 418.1953
554.4417 | 526.7938 | 267.3098 | 275.6292 | 419.0126
555.4417 | 526.8334 | 267.7367 | 276.0263 | 418.5403
556.4417 | 526.7629 | 268.2032 | 276.4964 | 418.1647
557.4417 | 526.6879 | 268.6556 | 277.044 | 418.2716
558.4417 | 526.769 | 269.1245 | 277.4037 | 417.9763
559.4417 | 526.7307 | 269.6252 | 278.2935 | 417.5629
560.4417 | 526.9121 | 270.0936 | 278.7964 | 417.8234
561.4417 | 527.0016 | 270.5846 | 279.2016 | 418.3519
562.4417 | 527.026 | 271.0568 | 279.6792 | 419.4418
563.4417 | 526.9561 | 271.6524 | 280.0998 | 419.2549
564.4417 | 526.8815 | 272.1805 | 280.5081 | 419.3455
565.4417 | 526.8722 | 272.7089 | 280.9488 | 418.4746
566.4417 | 526.8709 | 273.2145 | 281.3716 | 418.8055
567.4417 | 526.8951 | 273.6628 | 281.7358 | 419.2204
568.4417 | 527.0734 | 274.2318 | 282.1469 | 418.4597
569.4417 | 526.9694 | 274.7547 | 282.5553 | 418.9154
570.4417 | 526.9248 | 275.2201 | 283.1161 | 419.7789
571.4417 | 526.9485 | 275.7178 | 283.5498 | 419.7049
572.4417 | 526.9162 | 276.2808 | 284.0235 | 419.0107
573.4417 | 526.9161 | 276.7445 | 284.4382 | 418.9125
574.4417 | 527.1211 | 277.2968 | 284.9282 | 418.9863
575.4417 | 527.242 | 277.816 | 285.4748 | 420.1554
576.4417 | 527.1431 | 278.3221 | 285.8024 | 421.329
577.4417 | 527.173 | 278.791 | 286.3186 | 421.7573
578.4417 | 526.9098 | 279.2436 | 286.6849 | 422.0161
579.4417 | 526.4303 | 279.7909 | 287.1914 | 422.6206
580.4417 | 526.2529 | 280.2626 | 287.7291 | 423.0114
581.4417 | 526.3951 | 280.7765 | 288.4306 | 423.6205
582.4417 | 526.6235 | 281.2757 | 289.0598 | 423.2675
583.4417 | 526.6856 | 281.8343 | 289.5739 | 423.6077
584.4417 | 526.6496 | 282.4518 | 289.8803 | 423.4156
585.4417 | 526.5674 | 282.948 | 290.4626 | 423.8782
586.4417 | 526.5378 | 283.4245 | 290.8189 | 424.391
587.4417 | 526.5612 | 283.952 | 291.3712 | 424.3138
588.4417 | 526.5555 | 284.4331 | 291.7792 | 423.8506
589.4417 | 526.3391 | 284.9042 | 292.2676 | 424.3723
590.4417 | 526.0872 | 285.3851 | 292.6262 | 426.1685
591.4573 | 526.0092 | 285.8818 | 292.9773 | 426.7154
592.4417 | 526.0021 | 286.3022 | 293.3137 | 426.4678
593.4417 | 526.1039 | 286.8588 | 293.6499 | 427.5029
594.4417 | 526.2719 | 287.362 | 294.0496 | 427.3123
595.4417 | 526.2149 | 287.8754 | 294.7192 | 427.3113
596.4417 | 526.2875 | 288.2738 | 294.9402 | 426.2002
597.4417 | 526.3324 | 288.7931 | 295.4886 | 426.0615
598.4417 | 526.3638 | 289.2843 | 295.9253 | 426.208
599.4417 | 526.3092 | 289.8161 | 296.6481 | 426.4419
600.4417 | 526.5489 | 290.3357 | 296.8771 | 426.8381
601.4417 | 526.6193 | 290.8107 | 297.2714 | 426.0433
602.4417 | 526.4649 | 291.2545 | 297.8195 | 425.6691
603.4417 | 526.5192 | 291.6854 | 298.2069 | 425.749
604.4417 | 526.6505 | 292.0288 | 298.673 | 427.0425
605.4417 | 526.6516 | 292.5649 | 299.169 | 426.7047
606.4417 | 526.7323 | 293.0356 | 299.5912 | 426.0565
607.4417 | 526.8954 | 293.4713 | 300.5314 | 425.988
608.4417 | 526.9069 | 293.9172 | 300.7379 | 425.56
609.4417 | 526.9388 | 294.3941 | 301.0761 | 425.0347
610.4417 | 526.9364 | 294.9376 | 301.4106 | 425.3748
611.4417 | 526.9713 | 295.309 | 301.8016 | 425.8156
612.4417 | 527.0236 | 295.8129 | 302.2854 | 426.6177
613.4417 | 526.9973 | 296.2916 | 302.5535 | 426.9126
614.4417 | 526.9016 | 296.7728 | 302.8242 | 427.496
615.4417 | 526.8065 | 297.1356 | 303.234 | 427.2887
616.4417 | 526.7466 | 297.6085 | 303.2076 | 427.2737
617.4417 | 526.6414 | 298.066 | 303.3426 | 427.8204
618.4417 | 526.7891 | 298.4863 | 303.9744 | 428.3407
619.4417 | 526.8373 | 298.9267 | 304.4602 | 429.2811
620.4417 | 526.7399 | 299.4061 | 304.4112 | 428.8974
621.4573 | 526.8146 | 299.8592 | 304.6682 | 429.105
622.4417 | 526.6736 | 300.3181 | 305.7173 | 430.1412
623.4417 | 526.4402 | 300.7256 | 305.2225 | 429.8658
624.4417 | 526.4232 | 301.2485 | 306.2082 | 430.978
625.4417 | 526.5824 | 301.6861 | 306.3567 | 429.8037
626.4417 | 526.6103 | 301.99 | 306.7724 | 429.3838
627.4417 | 526.4948 | 302.4406 | 307.1645 | 429.0488
628.4417 | 526.492 | 302.8709 | 307.4307 | 428.7535
629.4417 | 526.5778 | 303.3933 | 307.9474 | 428.6443
630.4417 | 526.5351 | 303.7562 | 308.0294 | 429.2875
631.4417 | 526.6864 | 304.272 | 308.3181 | 429.4143
632.4417 | 526.7102 | 304.6825 | 308.9086 | 429.7579
633.4417 | 526.7579 | 305.1717 | 309.8756 | 430.9893
634.4417 | 526.7365 | 305.6126 | 310.2207 | 430.7354
635.4417 | 526.7283 | 306.1172 | 309.9841 | 430.8144
636.4417 | 526.7773 | 306.4761 | 309.6163 | 430.751
637.4417 | 526.8874 | 306.8686 | 310.0115 | 431.3461
638.4417 | 526.8491 | 307.2488 | 310.3089 | 431.7825
639.4417 | 526.8354 | 307.699 | 310.6863 | 432.0224
640.4417 | 527.0338 | 307.9243 | 310.8575 | 432.8488
641.4417 | 527.1724 | 308.4925 | 311.1756 | 432.1583
642.4417 | 527.2278 | 308.9845 | 311.5937 | 432.0823
643.4417 | 527.3547 | 309.2778 | 311.8093 | 431.5885
644.4417 | 527.402 | 309.7841 | 312.1448 | 431.6348
645.4417 | 527.3752 | 310.1967 | 312.5759 | 431.8959
646.4417 | 527.0819 | 310.6526 | 313.0222 | 432.4005
647.4417 | 526.7178 | 310.7955 | 313.0766 | 431.4185
648.4417 | 526.5914 | 311.2813 | 313.3185 | 431.0713
649.4417 | 526.8013 | 311.6288 | 313.5866 | 431.753
650.4417 | 526.7894 | 312.0885 | 313.884 | 431.4333
651.4417 | 526.6364 | 312.4595 | 314.2707 | 431.2397
652.4417 | 526.8707 | 312.9957 | 314.5778 | 430.7977
653.4417 | 526.9947 | 313.3765 | 314.8721 | 430.7033
654.4417 | 526.9664 | 313.8343 | 315.2221 | 431.0897
655.4417 | 526.7737 | 314.2789 | 315.5561 | 431.4793
656.4417 | 526.7604 | 314.8083 | 316.0527 | 431.1423
657.4417 | 526.7424 | 315.2923 | 316.5545 | 430.488
658.4417 | 526.7407 | 315.7778 | 316.7788 | 431.0206
659.4417 | 526.7288 | 316.2425 | 316.9723 | 429.9292
660.4417 | 526.6671 | 316.7256 | 317.3704 | 430.4086
661.4417 | 526.7598 | 317.2173 | 318.2385 | 430.1834
662.4417 | 526.9917 | 317.7202 | 319.943 | 430.1297
663.4417 | 527.0663 | 318.2317 | 320.8456 | 429.842
664.4417 | 527.0018 | 318.6363 | 321.4387 | 430.4191
665.4417 | 526.9929 | 318.9809 | 321.8518 | 430.294
666.4417 | 526.9371 | 319.3169 | 322.3432 | 430.0917
667.4417 | 526.7284 | 319.7042 | 322.8967 | 430.0972
668.4417 | 526.6922 | 320.1268 | 323.3644 | 430.7805
669.4417 | 526.7763 | 320.5937 | 323.6995 | 430.658
670.4417 | 526.719 | 320.8226 | 324.1487 | 430.6118
671.4417 | 526.6725 | 321.3386 | 324.7794 | 431.3222
672.4417 | 526.7495 | 321.7122 | 326.2345 | 430.5973
673.4417 | 526.7457 | 322.123 | 326.3336 | 430.5788
674.4417 | 526.777 | 322.4876 | 326.4537 | 430.5134
675.4417 | 526.808 | 322.9654 | 326.7984 | 429.963
676.4417 | 526.921 | 323.3654 | 326.7817 | 430.6455
677.4417 | 527.0233 | 323.7963 | 326.5935 | 431.0168
678.4417 | 527.0327 | 324.0096 | 326.4863 | 430.7088
679.4417 | 527.0266 | 324.5555 | 326.6786 | 432.0347
680.4417 | 527.0059 | 324.9805 | 326.9848 | 431.5565
681.4417 | 526.9487 | 325.4481 | 327.1009 | 431.9026
682.4417 | 526.9181 | 325.8276 | 327.2495 | 431.0754
683.4417 | 527.0498 | 326.2862 | 327.4321 | 430.7236
684.4417 | 527.1653 | 326.6968 | 327.513 | 430.376
685.4417 | 527.1743 | 327.082 | 327.5885 | 431.0177
686.4417 | 527.4185 | 327.5782 | 327.407 | 430.6199
687.4417 | 527.6513 | 327.9907 | 327.404 | 431.2956
688.4417 | 527.6341 | 328.3915 | 327.5155 | 432.3386
689.4417 | 527.6382 | 328.67 | 327.5743 | 432.4028
690.4417 | 527.5639 | 329.2876 | 327.7319 | 433.0997
691.4417 | 527.5655 | 329.7804 | 327.9562 | 432.8362
692.4417 | 527.5224 | 330.2327 | 328.1245 | 433.227
693.4417 | 527.4454 | 330.6136 | 328.3231 | 433.3894
694.4417 | 527.0712 | 331.1487 | 328.4806 | 433.0049
695.4417 | 526.9687 | 331.5668 | 328.7008 | 434.0349
696.4417 | 526.807 | 332.0214 | 328.9307 | 434.0579
697.4417 | 526.7433 | 332.4111 | 329.2576 | 434.0127
698.4417 | 526.9063 | 332.8014 | 329.358 | 434.9188
699.4417 | 526.9177 | 333.2253 | 329.6501 | 434.701
700.4417 | 527.047 | 333.4678 | 329.8184 | 434.8086
701.4417 | 527.3656 | 334.0484 | 330.0155 | 435.8525
702.4417 | 527.4667 | 334.4549 | 330.2973 | 435.0371
703.4417 | 527.3599 | 334.8526 | 330.5537 | 435.2938
704.4417 | 527.3653 | 335.3595 | 330.7842 | 435.3571
705.4417 | 527.3619 | 335.7619 | 331.0124 | 435.9329
706.4417 | 527.5121 | 335.9707 | 331.2478 | 436.08
707.4417 | 527.4946 | 336.1972 | 331.4729 | 436.3929
708.4417 | 527.4202 | 336.8162 | 331.8199 | 437.8189
709.4417 | 527.3323 | 337.1582 | 332.1382 | 437.6529
710.4417 | 527.2647 | 337.3304 | 332.3805 | 437.5512
711.4417 | 527.2457 | 337.887 | 332.8024 | 438.3556
712.4417 | 527.2738 | 338.5182 | 333.1428 | 439.8911
713.4417 | 527.3604 | 338.8987 | 333.4574 | 439.7384
714.4417 | 527.4752 | 339.9735 | 333.8957 | 438.9279
715.4417 | 527.4881 | 340.3662 | 334.2943 | 439.1782
716.4417 | 527.5097 | 340.8602 | 334.8359 | 439.5891
717.4417 | 527.5714 | 341.1378 | 335.2632 | 440.8108
718.4417 | 527.4592 | 341.3935 | 335.7293 | 442.4094
719.4417 | 527.5357 | 342.111 | 336.1614 | 441.5766
720.4417 | 527.6271 | 342.7931 | 336.4015 | 441.4868
721.4417 | 527.5779 | 343.1818 | 336.7266 | 441.8785
722.4417 | 527.5293 | 343.8195 | 337.2999 | 442.1819
723.4417 | 527.5095 | 344.0544 | 337.7021 | 442.8755
724.4417 | 527.5576 | 344.7738 | 338.021 | 442.995
725.4417 | 527.2692 | 345.0643 | 338.3748 | 443.4284
726.4417 | 527.2119 | 345.5843 | 338.7668 | 444.9505
727.4417 | 527.2535 | 346.0011 | 339.0614 | 446.2925
728.4417 | 527.3877 | 346.5975 | 339.4635 | 446.0044
729.4417 | 527.4019 | 346.9929 | 339.7377 | 447.0215
730.4417 | 527.131 | 347.5342 | 340.1262 | 447.2998
731.4417 | 526.9047 | 348.0535 | 340.5374 | 448.0718
732.4417 | 526.9218 | 348.2328 | 341.1961 | 448.8232
733.4417 | 527.2138 | 348.916 | 342.0765 | 448.186
734.4417 | 527.2538 | 349.379 | 342.6233 | 447.7702
735.4417 | 527.3164 | 349.8297 | 343.1998 | 447.0741
736.4417 | 527.2536 | 350.3843 | 343.9733 | 448.0849
737.4417 | 527.0477 | 350.329 | 345.0811 | 448.0045
738.4417 | 526.9845 | 350.7081 | 345.5004 | 447.6994
739.4417 | 527.0634 | 351.299 | 346.0845 | 447.6976
740.4417 | 526.9148 | 351.7088 | 346.7199 | 447.5677
741.4573 | 527.0775 | 352.1519 | 347.8193 | 448.2373
742.4417 | 527.0643 | 352.4952 | 348.0971 | 448.6943
743.4417 | 527.1385 | 353.0098 | 348.8811 | 449.622
744.4417 | 527.1125 | 353.4086 | 361.6313 | 450.2867
745.4417 | 527.2448 | 353.8271 | 363.0333 | 450.0539
746.4417 | 527.2849 | 354.463 | 363.6356 | 449.2946
747.4417 | 527.3038 | 354.5841 | 364.0728 | 449.9352
748.4417 | 527.4432 | 354.9899 | 364.6919 | 449.7595
749.4417 | 527.4201 | 355.3242 | 365.4904 | 450.1656
750.4417 | 527.2764 | 355.8701 | 366.3733 | 450.9158
751.4417 | 527.3506 | 356.2985 | 366.9254 | 450.6216
752.4417 | 527.3293 | 356.6754 | 367.2306 | 450.7017
753.4417 | 527.2095 | 357.0644 | 367.7072 | 450.8445
754.4417 | 527.2146 | 357.9681 | 368.3101 | 451.2658
755.4417 | 527.2424 | 358.6726 | 369.1372 | 452.1903
756.4417 | 527.1568 | 359.1418 | 369.6518 | 452.1558
757.4417 | 527.1815 | 359.3551 | 370.1654 | 451.537
758.4417 | 527.2693 | 359.7537 | 370.823 | 450.8384
759.4417 | 527.1798 | 360.2331 | 371.3788 | 451.1764
760.4417 | 527.023 | 360.7509 | 372.1546 | 451.2983
761.4417 | 526.9179 | 361.2381 | 372.866 | 452.1705
762.4417 | 526.8911 | 361.5557 | 373.2921 | 452.066
763.4417 | 526.8572 | 361.9234 | 373.6966 | 451.2509
764.4417 | 526.7295 | 362.5567 | 374.575 | 450.7208
765.4417 | 527.0247 | 363.0065 | 374.5607 | 449.793
766.4417 | 527.0702 | 363.4876 | 374.9394 | 450.2119
767.4417 | 527.1091 | 363.9951 | 375.3754 | 450.1111
768.4417 | 527.0863 | 364.5668 | 375.7427 | 450.3111
769.4417 | 527.1604 | 364.7303 | 375.5192 | 450.3572
770.4417 | 527.0504 | 365.7023 | 376.8534 | 450.3017
771.4417 | 526.9807 | 366.3439 | 376.7688 | 450.2532
772.4417 | 527.0059 | 366.8002 | 377.463 | 450.4758
773.4417 | 526.8811 | 367.2555 | 379.0004 | 451.2194
774.4417 | 526.66 | 367.8825 | 379.2992 | 450.3947
775.4417 | 526.8828 | 368.5915 | 380.3476 | 450.9597
776.4417 | 526.8998 | 369.2155 | 381.727 | 451.6441
777.4417 | 526.7991 | 369.5502 | 382.0312 | 452.5432
778.4417 | 526.77 | 370.1079 | 382.6232 | 453.0993
779.4417 | 526.9429 | 370.945 | 383.2265 | 453.914
780.4417 | 526.9244 | 371.7047 | 383.9681 | 453.4726
781.4417 | 526.9024 | 372.5443 | 384.2845 | 454.1305
782.4417 | 526.8317 | 373.3335 | 385.1956 | 453.3084
783.4417 | 526.4291 | 374.351 | 385.4505 | 452.6102
784.4417 | 526.3539 | 375.0294 | 385.9303 | 451.6539
785.4417 | 526.3573 | 375.7816 | 385.7605 | 451.4032
786.4417 | 526.3452 | 376.4279 | 386.9716 | 451.2435
787.4417 | 526.4692 | 377.8117 | 387.3747 | 451.9316
788.4417 | 526.4424 | 379.7904 | 388.0475 | 451.2822
789.4417 | 526.4259 | 380.3916 | 388.2673 | 451.0551
790.4417 | 526.4729 | 381.8191 | 388.195 | 450.7978
791.4417 | 526.516 | 383.2277 | 388.565 | 450.9044
792.4417 | 526.4749 | 384.2935 | 389.1006 | 452.1301
793.4417 | 526.6234 | 383.7821 | 390.2098 | 452.6579
794.4417 | 526.7515 | 386.8628 | 389.2958 | 453.3127
795.4417 | 526.9809 | 389.2697 | 388.5625 | 453.4946
796.4417 | 527.0316 | 390.6454 | 388.9785 | 454.1991
797.4417 | 526.94 | 393.1303 | 387.9694 | 454.0404
798.4417 | 526.9168 | 396.1514 | 386.2072 | 454.0587
799.4417 | 526.6644 | 398.3157 | 385.5269 | 453.5077
800.4417 | 526.6698 | 399.9721 | 384.0341 | 453.8533
801.4573 | 526.9442 | 402.7425 | 384.4457 | 454.5557
802.4417 | 526.6804 | 407.6901 | 380.148 | 454.3135
803.4417 | 526.6463 | 414.6588 | 375.2539 | 453.7583
804.4417 | 526.7715 | 418.6316 | 373.2623 | 454.5523
805.4417 | 526.8046 | 419.2629 | 373.1759 | 455.6685
806.4417 | 526.5403 | 422.4115 | 371.6839 | 456.444
807.4417 | 526.2941 | 427.6551 | 368.5323 | 456.6908
808.4417 | 526.3847 | 428.7836 | 370.3643 | 456.7108
809.4417 | 526.5181 | 430.3861 | 369.5146 | 456.2241
810.4417 | 526.4942 | 428.8682 | 377.0801 | 455.5292
811.4417 | 526.6342 | 429.0576 | 376.4902 | 454.5492
812.4417 | 526.6244 | 428.6934 | 379.3548 | 454.894
813.4417 | 526.5545 | 427.3693 | 381.6964 | 454.177
814.4417 | 526.3469 | 427.1484 | 382.2539 | 453.5391
815.4417 | 526.498 | 428.4007 | 378.5458 | 454.4774
816.4417 | 526.6367 | 428.6738 | 376.3634 | 454.3672
817.4417 | 526.501 | 430.1149 | 382.9882 | 454.4479
818.4417 | 526.5699 | 430.8689 | 383.3332 | 454.0393
819.4417 | 526.4559 | 432.8772 | 388.064 | 453.4224
820.4417 | 526.14 | 433.8409 | 387.1519 | 453.1326
821.4417 | 526.322 | 434.5864 | 388.0317 | 452.1041
822.4417 | 526.6209 | 438.8905 | 385.8411 | 450.8624
823.4417 | 526.9083 | 438.9809 | 386.9075 | 451.2879
824.4417 | 527.1351 | 439.7579 | 387.7454 | 451.5294
825.4417 | 526.9471 | 440.8651 | 388.277 | 452.091
826.4417 | 526.7888 | 440.1626 | 389.6421 | 451.5184
827.4417 | 526.895 | 440.8119 | 391.8244 | 451.4752
828.4417 | 527.1049 | 441.8434 | 393.8544 | 450.4391
829.4417 | 527.0433 | 441.9732 | 391.8733 | 450.4555
830.4417 | 527.0615 | 443.1925 | 393.0231 | 450.3305
831.4417 | 526.8239 | 442.9728 | 386.8615 | 450.6959
832.4417 | 526.7549 | 444.6003 | 390.8213 | 450.8
833.4417 | 526.7543 | 444.6121 | 389.8174 | 450.5446
834.4417 | 526.717 | 445.9048 | 389.8851 | 451.3455
835.4417 | 526.6136 | 445.7158 | 382.5595 | 450.7183
836.4417 | 526.3779 | 440.8689 | 323.5779 | 451.4532
837.4417 | 526.3578 | 441.1194 | 319.7208 | 452.103
838.4417 | 526.5742 | 440.0165 | 307.9508 | 451.5137
839.4417 | 526.5699 | 441.8765 | 318.8669 | 453.1193
840.4417 | 526.2905 | 440.8838 | 307.0514 | 453.1842
841.4417 | 526.5133 | 443.4255 | 321.7172 | 452.4626
842.4417 | 526.6938 | 442.0371 | 304.8588 | 451.5806
843.4417 | 526.7246 | 443.5553 | 314.1766 | 452.0928
844.4417 | 526.7185 | 443.2672 | 306.8066 | 452.6408
845.4417 | 526.891 | 443.7377 | 303.1685 | 452.5626
846.4417 | 527.0615 | 436.8477 | 316.9242 | 451.6096
847.4417 | 527.0226 | 434.5519 | 296.901 | 450.9025
848.4417 | 526.972 | 434.1907 | 291.8657 | 450.8743
849.4417 | 526.9447 | 437.0025 | 301.5919 | 451.8752
850.4417 | 526.9478 | 440.5866 | 286.9561 | 452.5414
851.4417 | 526.8714 | 443.4071 | 310.2248 | 452.3911
852.4417 | 526.7747 | 444.3052 | 336.6724 | 452.6421
853.4417 | 526.6045 | 445.5372 | 360.597 | 453.0593
854.4417 | 526.6304 | 446.6751 | 395.9474 | 453.1711
855.4417 | 526.6397 | 443.4609 | 322.6875 | 452.3609
856.4417 | 526.7444 | 445.3212 | 329.5321 | 451.2841
857.4417 | 526.7153 | 444.6667 | 310.7182 | 452.1364
858.4417 | 526.558 | 444.8395 | 302.9323 | 451.2099
859.4417 | 526.4121 | 444.9813 | 313.2644 | 451.0894
860.4417 | 526.3576 | 440.9714 | 268.3422 | 450.978
861.4573 | 526.3062 | 445.0999 | 307.9596 | 450.8333
862.4417 | 526.2623 | 444.835 | 308.2864 | 449.9474
863.4417 | 526.3336 | 445.5121 | 311.1646 | 450.6847
864.4417 | 526.3019 | 445.8538 | 309.604 | 450.2235
865.4417 | 526.2149 | 445.6974 | 305.0487 | 449.8292
866.4417 | 526.2285 | 445.6252 | 302.7367 | 449.4823
867.4417 | 526.1652 | 444.7549 | 291.2307 | 449.5581
868.4417 | 526.0389 | 446.0657 | 301.4651 | 449.9985
869.4417 | 525.8616 | 445.5612 | 293.1824 | 451.39
870.4417 | 526.095 | 445.3873 | 289.8312 | 451.0371
871.4417 | 526.1103 | 445.7596 | 291.1446 | 450.2267
872.4417 | 526.173 | 448.0971 | 311.9412 | 450.2681
873.4417 | 526.0407 | 448.5069 | 309.0549 | 449.9914
874.4417 | 525.9992 | 447.5356 | 294.9659 | 450.1713
875.4417 | 526.0148 | 449.4809 | 314.7877 | 449.968
876.4417 | 526.1467 | 449.7334 | 315.2218 | 449.8673
877.4417 | 526.2001 | 450.0515 | 316.1374 | 450.5879
878.4417 | 526.1909 | 450.4502 | 317.3055 | 450.6701
879.4417 | 526.3909 | 450.6471 | 318.3416 | 449.7994
880.4417 | 526.7963 | 450.7309 | 318.7697 | 450.6055
881.4417 | 526.8731 | 451.125 | 320.514 | 451.0983
882.4417 | 526.8311 | 451.302 | 321.1394 | 451.1147
883.4417 | 526.8686 | 451.4477 | 322.5708 | 451.2672
884.4417 | 526.899 | 451.668 | 325.5521 | 450.2071
885.4417 | 526.8837 | 451.8331 | 326.7663 | 450.0591
886.4417 | 527.1756 | 451.8995 | 329.0169 | 449.7844
887.4417 | 527.2202 | 451.9221 | 329.9794 | 450.3043
888.4417 | 527.5901 | 452.0092 | 330.6246 | 450.8855
889.4417 | 527.6502 | 452.1856 | 331.5497 | 452.0424
890.4417 | 527.8307 | 452.2184 | 331.7897 | 451.9129
891.4573 | 528.1282 | 452.1088 | 330.9331 | 451.3731
892.4417 | 528.1927 | 452.3648 | 334.612 | 451.5346
893.4417 | 528.1154 | 452.2924 | 334.4462 | 450.6054
894.4417 | 528.1056 | 452.3562 | 335.5196 | 449.5036
895.4417 | 528.2797 | 452.505 | 338.0304 | 450.4136
896.4417 | 528.3723 | 452.4982 | 341.1792 | 450.4966
897.4417 | 528.136 | 452.8903 | 346.5035 | 450.1226
898.4417 | 527.8894 | 453.1334 | 353.6257 | 449.6573
899.4417 | 527.766 | 455.8009 | 411.1425 | 450.4359
900.4417 | 527.6379 | 455.6092 | 412.0028 | 449.5605
901.4417 | 527.6277 | 440.9085 | 428.3773 | 450.2571
902.4417 | 527.5431 | 441.024 | 427.7317 | 450.969
903.4417 | 527.5142 | 441.1216 | 427.9457 | 450.5392
904.4417 | 527.5999 | 441.1811 | 428.143 | 452.6347
905.4417 | 527.9395 | 440.8644 | 428.3511 | 463.5011
906.4417 | 528.1199 | 440.9654 | 428.4221 | 480.2997
907.4417 | 528.1162 | 441.1504 | 428.7973 | 493.564
908.4417 | 528.0742 | 455.7369 | 413.6489 | 507.6086
909.4417 | 528.1221 | 439.7394 | 426.7322 | 520.1551
910.4417 | 528.1033 | 438.0902 | 429.1154 | 531.8517
911.4417 | 528.1266 | 437.9349 | 429.558 | 532.1014
912.4417 | 528.1247 | 436.1764 | 429.6015 | 535.0825
913.4417 | 528.0318 | 436.4091 | 429.7565 | 536.8467
914.4417 | 527.8211 | 436.6654 | 429.9988 | 541.2815
915.4417 | 527.5868 | 436.9372 | 430.5187 | 545.6979
916.4417 | 527.4376 | 437.2365 | 430.6622 | 550.4376
917.4417 | 527.4255 | 437.5839 | 430.7809 | 548.7298
918.4417 | 527.4093 | 441.0657 | 431.416 | 549.7056
919.4417 | 527.2411 | 442.3053 | 431.8187 | 551.1956
920.4417 | 526.9857 | 442.5163 | 431.7645 | 553.2481
921.4573 | 526.8704 | 442.3149 | 431.782 | 552.6351
922.4417 | 526.6136 | 443.1113 | 432.124 | 553.8555
923.4417 | 526.4348 | 443.6216 | 432.4123 | 554.6613
924.4417 | 526.3444 | 444.7002 | 432.8129 | 553.067
925.4417 | 526.4478 | 444.8773 | 433.225 | 552.4848
926.4417 | 526.3389 | 444.935 | 433.4411 | 552.862
927.4417 | 526.1533 | 445.2235 | 433.8482 | 553.4202
928.4417 | 525.783 | 443.5734 | 434.3171 | 552.7973
929.4417 | 525.5376 | 444.6261 | 434.9141 | 552.3662
930.4417 | 525.6146 | 444.5669 | 435.3641 | 550.4599
931.4417 | 525.5984 | 444.5142 | 436.2453 | 550.4452
932.4417 | 525.7327 | 444.9446 | 436.6814 | 549.9563
933.4417 | 526.0789 | 445.1013 | 437.4024 | 552.2454
934.4417 | 526.1976 | 445.3497 | 437.6236 | 552.3166
935.4417 | 526.3585 | 445.677 | 437.9894 | 550.099
936.4417 | 526.5876 | 445.9229 | 438.2777 | 552.5564
937.4417 | 526.5218 | 446.0722 | 438.553 | 550.8763
938.4417 | 526.6772 | 446.4449 | 439.0827 | 549.9046
939.4417 | 526.7838 | 446.6 | 439.2615 | 546.1135
940.4417 | 526.8102 | 447.0077 | 439.3604 | 543.8224
941.4417 | 526.7437 | 447.164 | 439.8447 | 541.3619
942.4417 | 526.8153 | 447.4023 | 439.749 | 539.6102
943.4417 | 526.9004 | 447.7332 | 440.0019 | 539.1084
944.4417 | 526.9809 | 447.7323 | 440.1143 | 541.0518
945.4417 | 526.9547 | 448.1443 | 440.2216 | 540.025
946.4417 | 526.9066 | 448.4299 | 440.337 | 540.3191
947.4417 | 527.0253 | 448.5382 | 440.2649 | 539.9331
948.4417 | 527.1446 | 448.6441 | 440.2738 | 538.6538
949.4417 | 527.1846 | 449.292 | 440.2988 | 536.6959
950.4417 | 527.3484 | 450.485 | 440.5151 | 534.519
951.4417 | 527.5643 | 450.5832 | 440.8801 | 533.253
952.4417 | 527.6565 | 450.8179 | 441.0986 | 533.1991
953.4417 | 527.7487 | 450.8536 | 441.3556 | 531.6375
954.4417 | 527.5928 | 450.768 | 441.722 | 532.327
955.4417 | 527.7942 | 451.2372 | 442.1389 | 532.1207
956.4417 | 527.8871 | 451.3158 | 442.3809 | 531.0883
957.4417 | 527.9644 | 451.5566 | 442.927 | 530.5346
958.4417 | 528.1631 | 451.7732 | 443.375 | 530.1841
959.4417 | 528.0537 | 452.0427 | 443.8942 | 530.0267
960.4417 | 528.0549 | 452.0963 | 370.4461 | 528.1327
961.4417 | 528.1073 | 452.336 | 371.8923 | 526.6465
962.5042 | 527.996 | 452.4334 | 441.7621 | 525.7275
963.4417 | 527.976 | 453.3662 | 373.9748 | 532.8318
964.4417 | 528.1805 | 453.4804 | 373.1252 | 532.1068
965.4417 | 528.4234 | 453.8859 | 373.8554 | 533.0411
966.4417 | 528.9304 | 454.4032 | 374.7088 | 531.8887
967.4417 | 529.2286 | 454.7209 | 446.6192 | 531.5574
968.4417 | 529.3714 | 455.0769 | 447.4622 | 533.6376
969.4417 | 529.5553 | 455.8039 | 378.1418 | 538.5138
970.4417 | 529.6584 | 456.3358 | 377.3288 | 539.4424
971.4417 | 529.7017 | 456.9984 | 378.1206 | 539.7785
972.4417 | 529.6582 | 457.4333 | 379.7505 | 538.8055
973.4417 | 529.8853 | 457.8619 | 373.3733 | 537.8605
974.4417 | 529.9142 | 458.2997 | 386.0833 | 538.1119
975.4417 | 529.8 | 458.5471 | 376.4087 | 538.1488
976.4417 | 529.7637 | 458.7878 | 385.2649 | 538.6321
977.4417 | 529.6906 | 458.8509 | 378.5832 | 540.1465
978.4417 | 529.4678 | 459.7642 | 377.0341 | 540.977
979.4417 | 529.2222 | 460.5736 | 377.9213 | 542.2252
980.4417 | 528.9325 | 461.3779 | 378.5995 | 541.0788
981.4417 | 528.6177 | 461.8067 | 377.8779 | 539.5992
982.4417 | 528.4268 | 462.2833 | 374.5447 | 538.7779
983.4417 | 528.0828 | 462.5458 | 376.5546 | 539.8055
984.4417 | 527.6036 | 462.5699 | 377.2942 | 540.2917
985.4417 | 527.2555 | 462.5585 | 377.1773 | 544.234
986.4417 | 527.0432 | 462.9636 | 381.0846 | 544.2593
987.4417 | 526.9605 | 463.4275 | 381.5807 | 549.0731
988.4417 | 526.8047 | 463.9341 | 382.5205 | 553.9092
989.4417 | 526.5067 | 464.6667 | 383.0075 | 553.525
990.4417 | 526.2762 | 465.3402 | 383.1971 | 552.7544
991.4417 | 526.3338 | 465.9925 | 383.3559 | 552.217
992.4417 | 526.2015 | 466.4735 | 383.6242 | 553.3017
993.4417 | 526.0328 | 467.2582 | 384.2237 | 554.0301
994.4417 | 525.9282 | 467.9905 | 384.4243 | 555.3238
995.4417 | 525.8589 | 468.7996 | 385.1339 | 556.2916
996.4417 | 525.7478 | 469.6217 | 385.3075 | 557.1865
997.4417 | 525.6718 | 470.26 | 385.3591 | 556.1985
998.4417 | 525.6966 | 470.9914 | 385.9607 | 554.9259
999.4417 | 525.5892 | 471.8808 | 385.7547 | 556.2735
1000.4417 | 525.393 | 472.297 | 386.1937 | 555.1753
1001.4417 | 525.1561 | 472.9098 | 385.4685 | 553.7746
1002.4417 | 524.9484 | 473.5373 | 387.4115 | 551.9889
1003.4417 | 524.8615 | 474.1288 | 388.0581 | 552.8025
1004.4417 | 524.7065 | 474.3348 | 388.3535 | 554.9929
1005.4417 | 524.7791 | 474.6393 | 388.6511 | 553.2869
1006.4417 | 524.9484 | 475.117 | 388.7179 | 551.2915
1007.4417 | 525.2107 | 475.3837 | 389.341 | 551.6428
1008.4417 | 525.2758 | 475.3731 | 389.914 | 551.4282
1009.4417 | 525.4041 | 475.7515 | 390.3014 | 550.7404
1010.4417 | 525.4972 | 475.9229 | 390.3176 | 550.2409
1011.4417 | 525.4649 | 476.1498 | 390.5803 | 550.6485
1012.4417 | 525.7465 | 476.6727 | 395.5609 | 567.4696
1013.4417 | 526.8135 | 477.2712 | 401.1685 | 588.7173
1014.4417 | 527.5601 | 477.8104 | 462.9896 | 600.3287
1015.4417 | 528.0301 | 478.4649 | 454.451 | 605.8981
1016.4417 | 527.9242 | 478.7134 | 457.8449 | 603.7593
1017.4417 | 527.7978 | 479.4626 | 456.9422 | 602.8411
1018.4417 | 527.5946 | 479.9105 | 457.6213 | 601.0422
1019.4417 | 527.1187 | 480.2915 | 450.3429 | 599.2078
1020.4417 | 526.6548 | 481.1385 | 455.9847 | 599.4017
1021.4417 | 526.0801 | 481.4481 | 457.1717 | 598.336
1022.4417 | 525.5811 | 482.0707 | 457.2133 | 598.1017
1023.4417 | 525.1112 | 483.0374 | 457.4993 | 599.467
1024.4417 | 524.4853 | 483.6551 | 456.8524 | 596.0918
1025.4417 | 523.8406 | 484.2295 | 475.5859 | 594.2125
1026.4417 | 523.1597 | 484.9998 | 477.7212 | 593.6214
1027.4417 | 522.527 | 485.5886 | 462.4768 | 590.2407
1028.4417 | 521.9163 | 486.0048 | 465.5174 | 589.0546
1029.4417 | 521.5167 | 486.2472 | 466.6651 | 584.041
1030.4417 | 521.1571 | 486.63 | 466.0199 | 580.3399
1031.4417 | 520.8533 | 487.2939 | 467.1719 | 577.8198
1032.4417 | 520.6155 | 487.7386 | 467.651 | 576.2128
1033.4417 | 520.33 | 487.9277 | 466.7534 | 573.6412
1034.4417 | 520.0611 | 488.4575 | 468.1461 | 572.1911
1035.4417 | 519.822 | 488.8319 | 469.3739 | 571.1305
1036.4417 | 519.6675 | 489.3273 | 412.2424 | 570.1781
1037.4417 | 519.3997 | 489.5611 | 412.5383 | 569.5448
1038.4417 | 519.2565 | 491.1114 | 413.3044 | 567.8356
1039.4417 | 519.0962 | 490.2289 | 413.8009 | 566.2667
1040.4417 | 518.9272 | 491.4583 | 413.9143 | 565.3148
1041.4417 | 518.5552 | 492.0834 | 414.1393 | 565.405
1042.4417 | 518.4616 | 492.7818 | 414.3444 | 566.038
1043.4417 | 518.2555 | 494.7356 | 414.7563 | 564.1274
1044.4417 | 518.0707 | 496.1437 | 415.3897 | 566.1631
1045.4417 | 518.021 | 495.0588 | 415.376 | 564.7585
1046.4417 | 517.8123 | 496.2777 | 415.9716 | 564.4001
1047.4417 | 517.6209 | 496.4444 | 416.4604 | 562.3561
1048.4417 | 517.413 | 497.446 | 417.3146 | 564.106
1049.4417 | 517.2202 | 497.9104 | 417.7933 | 562.5076
1050.4417 | 517.0114 | 498.5917 | 418.2573 | 562.0731
1051.4417 | 516.6786 | 499.0314 | 418.3203 | 562.2414
1052.4417 | 516.351 | 499.2916 | 418.6413 | 561.5471
1053.4417 | 516.0536 | 500.0192 | 419.3479 | 562.2873
1054.4417 | 515.7919 | 500.5922 | 419.8592 | 567.7065
1055.4417 | 515.3505 | 501.1125 | 420.436 | 566.9854
1056.4417 | 514.7479 | 501.6075 | 421.0313 | 568.9081
1057.4417 | 514.2823 | 502.1247 | 421.1978 | 568.4562
1058.4417 | 513.8639 | 502.1881 | 422.0346 | 568.0852
1059.4417 | 513.5686 | 502.7434 | 421.9059 | 568.3595
1060.4417 | 513.2452 | 502.9449 | 422.4821 | 569.3862
1061.4417 | 512.9747 | 500.2773 | 422.4128 | 568.2317
1062.4417 | 512.6874 | 499.4407 | 423.071 | 567.8301
1063.4417 | 512.3291 | 499.726 | 423.4568 | 566.8214
1064.4417 | 512.1459 | 499.9453 | 424.1229 | 566.3913
1065.4417 | 511.8898 | 495.6519 | 424.8829 | 568.2328
1066.4417 | 511.778 | 495.3752 | 424.4044 | 567.2455
1067.4417 | 511.6625 | 496.4202 | 424.7593 | 568.0657
1068.4417 | 511.3656 | 496.302 | 424.6776 | 568.0347
1069.4417 | 510.9768 | 496.8796 | 424.9633 | 566.9085
1070.4417 | 510.8236 | 496.9685 | 425.6873 | 568.1371
1071.4417 | 510.5374 | 499.3861 | 425.4743 | 569.3714
1072.4417 | 510.3024 | 509.4595 | 425.5289 | 570.2153
1073.4417 | 510.086 | 504.024 | 426.1066 | 570.5884
1074.4417 | 509.956 | 509.1569 | 426.2508 | 570.3378
1075.4417 | 509.9509 | 511.6679 | 426.6142 | 570.0585
1076.4417 | 509.8699 | 511.1892 | 427.0624 | 570.2335
1077.4417 | 509.7057 | 507.6145 | 427.7278 | 568.8859
1078.4417 | 509.6137 | 507.4942 | 428.2674 | 569.5697
1079.4417 | 509.3545 | 505.6323 | 428.865 | 569.2234
1080.4417 | 509.0606 | 505.3775 | 428.9609 | 566.432
1081.4417 | 508.751 | 505.189 | 429.4799 | 566.3102
1082.4417 | 508.6718 | 503.3814 | 430.5947 | 566.6709
1083.4417 | 508.6828 | 505.2592 | 431.6075 | 566.6172
1084.4417 | 508.4152 | 506.7578 | 431.9899 | 564.4877
1085.4417 | 508.1792 | 507.7133 | 432.7477 | 564.0073
1086.4417 | 508.09 | 508.3059 | 433.743 | 562.143
1087.4417 | 507.8963 | 510.7447 | 434.2972 | 561.7082
1088.4417 | 507.7007 | 509.7425 | 434.8647 | 561.5516
1089.4417 | 507.482 | 511.2742 | 435.6441 | 560.9817
1090.4417 | 507.4214 | 516.8183 | 436.4246 | 560.1619
1091.4417 | 507.3665 | 517.47 | 437.2557 | 558.9808
1092.4417 | 507.1308 | 516.623 | 438.2005 | 558.7712
1093.4417 | 506.9974 | 514.3473 | 438.2488 | 556.4216
1094.4417 | 506.8496 | 520.3162 | 439.1532 | 554.3026
1095.4417 | 506.824 | 510.8131 | 439.8347 | 553.6209
1096.4417 | 506.8179 | 508.1449 | 440.6612 | 552.4156
1097.4417 | 506.8559 | 509.9803 | 441.1312 | 551.2317
1098.4417 | 506.9751 | 509.6496 | 441.9913 | 549.4365
1099.4417 | 507.0738 | 510.4314 | 442.3879 | 546.9394
1100.4417 | 507.0206 | 509.7503 | 443.1187 | 548.6958
1101.4417 | 506.9968 | 509.8867 | 443.4538 | 546.857
1102.4417 | 506.9147 | 515.9305 | 444.0132 | 544.3341
1103.4417 | 506.7707 | 512.2865 | 444.8365 | 543.5451
1104.4417 | 506.6501 | 512.9052 | 444.8977 | 544.3912
1105.4417 | 506.4813 | 523.8865 | 445.6691 | 544.9717
1106.4573 | 506.5611 | 522.7729 | 446.2263 | 543.3173
1107.4417 | 506.6672 | 523.8993 | 446.8296 | 543.2319
1108.4417 | 506.5636 | 517.7611 | 447.4347 | 542.0895
1109.4417 | 506.4827 | 518.8084 | 447.683 | 542.9836
1110.4417 | 506.5822 | 516.6805 | 448.0037 | 541.9064
1111.4417 | 506.7396 | 515.3438 | 448.4126 | 541.0877
1112.4417 | 506.6515 | 516.234 | 448.6466 | 541.2056
1113.4417 | 506.4424 | 521.4463 | 449.0952 | 541.7463
1114.4417 | 506.3042 | 521.0867 | 449.3213 | 539.7156
1115.4417 | 506.0689 | 520.2834 | 449.8513 | 538.7528
1116.4417 | 506.117 | 515.7704 | 450.4299 | 538.356
1117.4417 | 506.202 | 514.8813 | 450.7588 | 538.3306
1118.4417 | 506.1895 | 513.0631 | 451.2703 | 536.2656
1119.4417 | 506.1883 | 516.4364 | 451.8959 | 537.5755
1120.4417 | 506.2187 | 514.5753 | 452.3037 | 534.9281
1121.4417 | 506.252 | 513.548 | 452.8793 | 533.8308
1122.4417 | 506.4835 | 514.276 | 453.3452 | 531.3017
1123.4417 | 506.3515 | 512.7897 | 453.4588 | 530.81
1124.4417 | 506.3127 | 512.1548 | 453.7932 | 530.0615
1125.4417 | 506.3149 | 511.7183 | 454.1168 | 529.7165
1126.4417 | 506.3366 | 511.2939 | 454.5345 | 529.7338
1127.4417 | 506.3256 | 511.787 | 454.9659 | 529.1783
1128.4417 | 506.3166 | 514.5822 | 455.3009 | 528.1162
1129.4417 | 506.1979 | 513.4278 | 455.2986 | 529.5927
1130.4417 | 505.9593 | 507.8426 | 455.8092 | 529.9122
1131.4417 | 506.2322 | 508.1972 | 456.2048 | 530.3808
1132.4417 | 506.4646 | 506.6643 | 456.5585 | 531.1726
1133.4417 | 506.5272 | 505.6965 | 457.0293 | 531.6136
1134.4417 | 506.5364 | 504.9364 | 457.3924 | 532.36
1135.4417 | 506.3663 | 503.8915 | 457.1995 | 529.0223
1136.4417 | 506.4989 | 502.8369 | 457.4885 | 527.928
1137.4417 | 506.5333 | 507.0946 | 458.0745 | 526.0008
1138.4417 | 506.6909 | 504.6416 | 458.1584 | 525.3452
1139.4417 | 506.5796 | 507.3195 | 458.4046 | 525.4065
1140.4417 | 506.6164 | 504.3121 | 458.1457 | 523.2945
1141.4417 | 506.6682 | 500.7447 | 458.8909 | 522.3776
1142.4417 | 506.8542 | 499.0303 | 459.0772 | 522.1716
1143.4417 | 506.8161 | 498.5801 | 459.6959 | 521.0838
1144.4417 | 507.0015 | 498.6333 | 459.9795 | 520.9142
1145.4417 | 507.2968 | 498.7624 | 460.1818 | 519.4208
1146.4417 | 507.5113 | 497.0885 | 460.4692 | 519.1734
1147.4417 | 507.617 | 497.8353 | 460.5614 | 517.6636
1148.4417 | 507.7824 | 496.1871 | 460.9669 | 515.1166
1149.4417 | 507.9569 | 499.885 | 460.9217 | 516.0416
1150.4417 | 508.2159 | 500.0526 | 461.6297 | 515.4543
1151.4417 | 508.3959 | 497.6242 | 461.5399 | 513.3858
1152.4417 | 508.6579 | 493.3154 | 461.7079 | 511.491
1153.4417 | 508.9627 | 496.2825 | 461.9428 | 510.9456
1154.4417 | 509.2878 | 499.953 | 461.7281 | 509.3176
1155.4417 | 509.5835 | 492.165 | 462.6454 | 509.0876
1156.4417 | 509.9792 | 502.8328 | 461.8482 | 508.0995
1157.4417 | 510.5107 | 498.776 | 462.5491 | 508.2134
1158.4417 | 510.9784 | 497.4184 | 462.355 | 505.4022
1159.4417 | 511.6009 | 495.3706 | 462.7305 | 503.7877
1160.4417 | 512.2953 | 496.6636 | 462.2292 | 502.6118
1161.4417 | 513.11 | 491.7662 | 462.519 | 501.7591
1162.4417 | 513.8244 | 490.8896 | 462.4989 | 499.9526
1163.4417 | 514.5925 | 491.2206 | 462.8113 | 499.8327
1164.4417 | 515.3065 | 490.1078 | 462.7069 | 499.4198
1165.4417 | 516.1463 | 491.2045 | 462.6231 | 498.8363
1166.4573 | 516.7509 | 488.4386 | 462.8712 | 497.5079
1167.4417 | 517.1275 | 487.5324 | 463.1227 | 495.3483
1168.4417 | 517.6916 | 487.1158 | 463.2409 | 494.5675
1169.4417 | 518.0418 | 487.4442 | 463.1042 | 493.9078
1170.4417 | 518.348 | 485.2855 | 463.1697 | 494.5034
1171.4417 | 518.5569 | 486.0201 | 463.0624 | 494.5331
1172.4417 | 518.7827 | 485.5055 | 463.0272 | 494.2514
1173.4417 | 518.9402 | 487.9839 | 462.9135 | 492.6081
1174.4417 | 519.0534 | 484.6121 | 462.9222 | 490.9514
1175.4417 | 519.223 | 485.8473 | 462.7368 | 491.4326
1176.4417 | 519.2508 | 484.6945 | 462.3914 | 490.834
1177.4417 | 519.3059 | 489.2623 | 462.3556 | 490.6147
1178.4417 | 519.3477 | 485.3982 | 462.2723 | 489.9867
1179.4417 | 519.348 | 484.1723 | 461.9364 | 489.7726
1180.4417 | 519.3996 | 484.2544 | 461.7996 | 487.6126
1181.4417 | 519.6492 | 483.6426 | 461.7225 | 487.1831
1182.4417 | 519.7083 | 482.1323 | 461.6295 | 487.581
1183.4417 | 519.8982 | 481.1209 | 461.6758 | 487.6605
1184.4417 | 520.2216 | 481.2633 | 461.4748 | 486.9859
1185.4417 | 520.3358 | 480.3376 | 461.2374 | 486.6785
1186.4417 | 520.5093 | 479.6264 | 461.1317 | 485.8866
1187.4417 | 520.5226 | 479.1073 | 460.7186 | 484.4253
1188.4417 | 520.5241 | 480.6895 | 460.8666 | 483.3495
1189.4417 | 520.6772 | 479.9577 | 461.2705 | 483.3858
1190.4417 | 520.6175 | 478.4597 | 460.6241 | 481.5914
1191.4417 | 520.4999 | 479.3851 | 460.485 | 481.4587
1192.4417 | 520.5148 | 478.4526 | 460.5131 | 482.007
1193.4417 | 520.4839 | 480.2602 | 460.3776 | 482.055
1194.4417 | 520.1958 | 479.5964 | 459.7745 | 480.3425
1195.4417 | 520.1701 | 479.0603 | 459.6455 | 480.8382
1196.4417 | 520.161 | 479.182 | 459.5753 | 479.7458
1197.4417 | 519.9616 | 479.2293 | 459.3961 | 478.7357
1198.4417 | 520.044 | 477.9074 | 459.2874 | 477.7547
1199.4417 | 520.0031 | 479.0939 | 459.2672 | 477.6384
1200.4417 | 519.6006 | 477.315 | 458.7606 | 477.9143
1201.4417 | 519.5186 | 477.9745 | 458.4193 | 477.7742
1202.4417 | 519.4726 | 478.302 | 458.7642 | 477.0212
1203.4417 | 519.5119 | 478.5554 | 458.265 | 475.0841
1204.4417 | 519.2502 | 477.3011 | 457.966 | 475.0549
1205.4417 | 518.9105 | 479.8043 | 457.7762 | 474.3898
1206.4417 | 518.6459 | 475.9412 | 457.6315 | 475.4882
1207.4417 | 518.335 | 475.2395 | 457.7101 | 474.5384
1208.4417 | 518.1158 | 479.1001 | 457.4052 | 474.1906
1209.4417 | 517.9605 | 474.1729 | 456.8818 | 474.0824
1210.4417 | 517.884 | 476.5406 | 456.4102 | 473.0001
1211.4417 | 517.6191 | 474.6365 | 456.2012 | 472.5209
1212.4417 | 517.3309 | 478.1283 | 455.5089 | 470.6795
1213.4417 | 517.2136 | 478.131 | 456.2054 | 469.9689
1214.4417 | 517.2567 | 479.0016 | 455.9645 | 469.7096
1215.4417 | 517.4287 | 478.5874 | 456.6548 | 469.9514
1216.4417 | 517.5048 | 474.9625 | 456.5533 | 469.6758
1217.4417 | 517.2181 | 477.2803 | 456.3689 | 468.6305
1218.4417 | 516.9331 | 473.7648 | 455.9637 | 468.8304
1219.4417 | 516.6999 | 473.3659 | 455.4868 | 468.5888
1220.4417 | 516.6233 | 473.0781 | 455.0779 | 468.0589
1221.4417 | 516.5984 | 471.9857 | 454.3618 | 467.583
1222.4417 | 516.8069 | 471.6289 | 453.5669 | 467.2706
1223.4417 | 517.0637 | 471.0296 | 453.2528 | 466.6171
1224.4417 | 517.2268 | 470.6723 | 453.109 | 466.3549
1225.4417 | 517.3268 | 471.1861 | 452.9447 | 465.782
1226.4417 | 517.4249 | 469.9921 | 452.873 | 465.5304
1227.4417 | 517.5485 | 466.8009 | 452.8714 | 464.3911
1228.4417 | 517.6742 | 465.3579 | 452.8585 | 465.418
1229.4417 | 517.8888 | 465.7198 | 452.6193 | 465.112
1230.4417 | 517.6532 | 464.9084 | 452.3908 | 465.5913
1231.4417 | 517.6144 | 464.5005 | 452.257 | 465.1038
1232.4417 | 517.7376 | 464.6301 | 452.072 | 465.1024
1233.4417 | 517.8972 | 464.9518 | 452.9739 | 464.294
1234.4417 | 517.9355 | 463.3527 | 452.0747 | 464.6214
1235.4417 | 517.9855 | 464.0874 | 452.0592 | 463.8604
1236.4417 | 518.115 | 463.2816 | 451.3495 | 462.1586
1237.4417 | 518.1271 | 462.647 | 451.3381 | 461.0169
1238.4417 | 518.0958 | 463.0724 | 451.4838 | 461.5591
1239.4417 | 518.1405 | 461.6677 | 450.8723 | 461.668
1240.4417 | 518.1644 | 461.2288 | 450.6466 | 462.2053
1241.4417 | 518.3871 | 461.7531 | 450.7377 | 462.7621
1242.4417 | 518.6194 | 460.5472 | 450.2053 | 461.7693
1243.4417 | 518.7379 | 460.6035 | 450.2255 | 460.8106
1244.4417 | 518.9813 | 460.4328 | 449.8755 | 460.7965
1245.4417 | 519.1714 | 460.7253 | 450.0298 | 460.4786