## Test Conditions
DESIREE-FIRE Test Number 22 - Circuit Simulator Data Only
Test Date: | 2009-08-13
DCSim DAQ Start Time | 12:44
DCSim Time for Synchronization | 14:24
Heat Source Synchronization | 1:38 | minutes:seconds
Heat Source DAQ Start Time | 14:22
Fire Time | 14:25
Offset | 1:41 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 6060 | seconds
Heat Source Offset | 0:03 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 188 | seconds
Heat Source Stop Time | 14:38
Test Duration | 0:13 | minutes:seconds
| 785 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
MOV 1 | Armored, 8c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. Channel 5 represents the temp under the armor. | TC11 in the Temperature Data File
MOV 2 | Armored, 8c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. Channel 5 represents the temp under the armor. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | MOV-1_CT500 | MOV-1a_CT35_1_P | MOV-1a_CT35_2_N | MOV-1b_CT35_1_G | MOV-1b_CT35_2_R | MOV-1b_CT35_3_YO | MOV-1b_CT35_4_YC | MOV-2_CT500 | MOV-2a_CT35_1_P | MOV-2a_CT35_2_N | MOV-2b_CT35_1_G | MOV-2b_CT35_2_R | MOV-2b_CT35_3_YO | 2b_CT35_4_YC1 | MOV-1a_VT7_1_SP | MOV-1a_VTU_1_P | MOV-1a_VTU_2_N | MOV-1b_VT7_1_G | MOV-1b_VT7_2_R | MOV-1b_VT7_3_YO1 | MOV-1b_VT7_4_YC1 | MOV-2a_VT7_1_SP | MOV-2a_VTU_1_P | MOV-2a_VTU_2_N | MOV-2b_VT7_1_G | MOV-2b_VT7_2_R | 2b_VT7_3_YO1 | MOV-2b_VT7_4_YC1 | {MOV1} V(N) - V(Batt -) | {MOV1} V(P) - V(Batt +) | {MOV1} V(G) - V(Batt +) | {MOV1} V(R) - V(Batt -) | {MOV1} V(YC1) - V(Batt -) | {MOV1} V(YO1) - V(Batt -) | {MOV1} V(YC1) - V(N) | {MOV1} V(YO1) - V(N) | {MOV2} V(N) - V(Batt -) | {MOV2} V(P) - V(Batt +) | {MOV2} V(G) - V(Batt +) | {MOV2} V(R) - V(Batt -) | {MOV2} V(YC1) - V(Batt -) | {MOV2} V(YO1) - V(Batt -) | {MOV2} V(YC1) - V(N) | {MOV2} V(YO1) - V(N) | {MOV-1} V(R) - V(N) | {MOV-1} V(G) - V(N) | {MOV-2} V(R) - V(N) | {MOV-2} V(G) - V(N) | {MOV-1} V(P) - V(N) | {MOV-2} V(P) - V(N) | {MOV-1} V(P) - V(Batt -) | {MOV-2} V(P) - V(Batt -) | {MOV-1} V(N) - V(Batt +) | {MOV-2} V(N) - V(Batt +) | {MOV-1} V(G) - V(Batt -) | {MOV2} V(G) - V(Batt-) | {MOV1} V(SP) - V(Batt -) | {MOV2} V(SP) - V(Batt -)
-0.67188 | 123.3078 | -59.9854 | 63.0249 | -0.052872 | 0.0013523 | 0.06549 | 0.070541 | -0.0015615 | -0.0013929 | -0.0012071 | -0.036377 | 0.00116 | 0.064497 | 0.072788 | -0.0023626 | 0.0027751 | -0.0024887 | 0.018311 | 63.0112 | -60.1547 | 63.002 | -59.8938 | -60.2646 | 0.013733 | 0.045776 | 62.9791 | -60.0403 | 63.0844 | -60.0403 | -60.1593 | -59.9579 | -0.16937 | -0.013733 | -0.022888 | 0.091553 | 59.9991 | -0.27923 | 60.1685 | -0.10986 | -0.054931 | -0.045776 | 0.05951 | -0.054931 | 0.027466 | -0.17395 | 0.082397 | -0.11902 | 0.26093 | 123.1567 | 0 | 123.1247 | 123.1659 | 123.0194 | 122.9965 | 122.9645 | -123.1796 | -123.0652 | 122.9874 | 123.0698 | 60.0037 | 60.0311
0.32812 | 123.2117 | -60.0449 | 63.0341 | -0.052872 | 0.0022067 | 0.06549 | 0.070113 | -6.6126e-05 | 0.00074348 | -0.0022751 | -0.069946 | 0.00030543 | 0.065992 | 0.062107 | -0.00043997 | 0.0012797 | -0.00099325 | -0.022888 | 62.9929 | -60.1959 | 62.9883 | -59.9213 | -60.3058 | -0.036621 | -0.054932 | 62.97 | -60.054 | 63.0157 | -60.0906 | -60.2097 | -60.0082 | -0.15106 | -0.041199 | -0.045777 | 0.1236 | 60.0082 | -0.26093 | 60.1593 | -0.10986 | -0.009155 | -0.064087 | -0.018311 | -0.045776 | 0.036621 | -0.1648 | 0.045776 | -0.15564 | 0.27466 | 123.1842 | -0.036621 | 123.0698 | 123.1888 | 123.024 | 123.0377 | 123.0148 | -123.23 | -123.0881 | 123.0331 | 123.0606 | 60.022 | 59.9899
1.3281 | 123.2483 | -60.0677 | 62.9974 | -0.045242 | 0.0019931 | 0.065704 | 0.072036 | 0.0022837 | 0.0022387 | 0.00028833 | -0.039429 | 0.0015872 | 0.065352 | 0.058689 | 0.00020083 | 0.0036295 | 7.4746e-05 | -0.07782 | 63.0066 | -60.1959 | 62.9196 | -60.0128 | -60.379 | -0.11902 | -0.1831 | 62.9288 | -60.0677 | 62.9929 | -60.141 | -60.2325 | -60.0311 | -0.12817 | 0.009155 | -0.07782 | 0.054932 | 59.9487 | -0.31128 | 60.0769 | -0.1831 | 0 | -0.068665 | -0.004578 | -0.073242 | 0.036621 | -0.16479 | 0.036621 | -0.16479 | 0.18311 | 123.1155 | -0.073242 | 123.0606 | 123.2025 | 122.9965 | 123.0743 | 122.9965 | -123.1934 | -123.0652 | 122.9874 | 123.0606 | 59.9899 | 59.8846
2.3281 | 123.3261 | -60.0311 | 62.9745 | -0.098648 | 0.00028412 | 0.06485 | 0.069045 | -0.0034841 | 0.00095708 | -0.00035247 | 0.0093995 | 0.00073263 | 0.062147 | 0.063388 | -0.002149 | 0.0021341 | -0.0037705 | -0.027466 | 62.9105 | -60.1547 | 63.0386 | -59.8526 | -60.2417 | -0.022888 | -0.032043 | 62.9059 | -60.0632 | 63.1027 | -60.022 | -60.1089 | -59.9213 | -0.1236 | -0.064087 | 0.064087 | 0.17853 | 60.0082 | -0.21057 | 60.1318 | -0.086975 | -0.032043 | -0.068664 | 0.12817 | 0.009155 | 0.10986 | -0.07782 | 0.14191 | -0.045777 | 0.30212 | 123.1934 | 0.041198 | 123.1659 | 123.0652 | 122.9691 | 122.9416 | 122.937 | -123.1293 | -123.0377 | 123.0698 | 123.1338 | 60.0037 | 59.9991
3.3281 | 123.2391 | -60.0082 | 63.0341 | -0.014725 | 0.0013523 | 0.063995 | 0.0699 | -0.0030569 | -0.0013929 | 0.0017837 | -0.021118 | 0.0013736 | 0.065565 | 0.059757 | -0.0030036 | 0.0021341 | -0.00099325 | -0.009155 | 63.0203 | -60.1685 | 62.9791 | -59.9625 | -60.2646 | 0.009155 | 0 | 63.0341 | -60.0449 | 63.089 | -60.2051 | -60.1089 | -59.8938 | -0.16022 | -0.013733 | -0.054932 | 0.045777 | 60.0174 | -0.25635 | 60.1776 | -0.09613 | -0.036621 | 0 | 0.054931 | -0.19684 | 0.11444 | -0.10071 | 0.15106 | -0.064087 | 0.20599 | 123.1476 | -0.16022 | 123.1338 | 123.1888 | 123.0789 | 123.0286 | 123.0423 | -123.2025 | -123.0789 | 122.9874 | 123.0972 | 59.9991 | 60.0082
4.3281 | 123.2803 | -60.0311 | 63.0432 | -0.029984 | 0.0022067 | 0.065918 | 0.071822 | -6.6126e-05 | -0.0020337 | -0.0024887 | -0.027222 | 9.1834e-05 | 0.064711 | 0.066165 | -0.0023626 | 0.00085247 | -0.00099325 | 0.022888 | 62.9974 | -60.1913 | 63.0157 | -59.903 | -60.2509 | 0.027466 | 0.059509 | 62.9654 | -60.0174 | 63.0615 | -60.0403 | -60.141 | -59.9533 | -0.16022 | -0.045776 | -0.027466 | 0.12817 | 60.0586 | -0.21973 | 60.2188 | -0.059509 | 0.013733 | -0.07782 | 0.01831 | -0.009155 | 0.07782 | -0.10986 | 0.064087 | -0.1236 | 0.28839 | 123.2071 | -0.022888 | 123.0789 | 123.1888 | 122.9828 | 123.0286 | 122.9965 | -123.2346 | -123.0606 | 123.0469 | 123.0927 | 60.054 | 60.0906
5.3281 | 123.1934 | -60.054 | 63.0203 | -0.091019 | 0.00049772 | 0.064209 | 0.070968 | 0.0035653 | 0.00095708 | -0.0035569 | -0.039429 | 0.002228 | 0.067274 | 0.065311 | -0.00086737 | 0.0014933 | 0.0019973 | -0.027466 | 62.9929 | -60.1868 | 62.9608 | -59.9533 | -60.3149 | -0.050354 | -0.068665 | 62.9562 | -60.054 | 63.0249 | -60.1044 | -60.1959 | -60.0174 | -0.13275 | -0.027466 | -0.05951 | 0.10071 | 60.0037 | -0.26093 | 60.1364 | -0.12817 | 0 | -0.064087 | 0.004577 | -0.050354 | 0.036621 | -0.14191 | 0.036621 | -0.14191 | 0.23346 | 123.1476 | -0.050354 | 123.0789 | 123.1796 | 123.0103 | 123.0469 | 123.0103 | -123.2071 | -123.0743 | 123.0148 | 123.0789 | 60.0266 | 59.9854
6.3281 | 123.1842 | -60.0403 | 63.0203 | -0.10628 | 0.0013523 | 0.064422 | 0.07289 | -0.00027993 | 0.0011707 | 0.0022109 | -0.033325 | 0.00073263 | 0.064711 | 0.06232 | -0.0019354 | 0.00042507 | 0.0015701 | -0.059509 | 63.0112 | -60.1959 | 62.9288 | -60.0266 | -60.3653 | -0.11444 | -0.18768 | 62.97 | -60.0677 | 62.97 | -60.1776 | -60.2646 | -60.0494 | -0.15564 | -0.009156 | -0.091553 | 0.013733 | 59.9258 | -0.32501 | 60.0815 | -0.16937 | -0.027466 | -0.050354 | -0.050354 | -0.13733 | -0.009155 | -0.2243 | 0.018311 | -0.19684 | 0.16937 | 123.1247 | -0.10986 | 123.0377 | 123.2071 | 123.0377 | 123.0515 | 123.0103 | -123.2162 | -123.0881 | 122.9691 | 123.0103 | 59.9808 | 59.8526
7.3281 | 123.2391 | -60.0449 | 63.0112 | -0.12917 | 0.0026339 | 0.065277 | 0.069686 | -0.0022025 | -0.00011112 | -0.0044113 | -0.042481 | 0.0013736 | 0.063002 | 0.063175 | -0.0012946 | 0.0012797 | 0.00050195 | -0.07782 | 63.002 | -60.1913 | 62.915 | -60.0174 | -60.379 | -0.12817 | -0.16479 | 62.9562 | -60.0815 | 63.0112 | -60.1364 | -60.2371 | -60.0174 | -0.14648 | -0.009155 | -0.09613 | 0.027466 | 59.9167 | -0.33417 | 60.0632 | -0.18768 | -0.036621 | -0.054931 | 0 | -0.091553 | 0.027466 | -0.19226 | 0.064087 | -0.15564 | 0.17395 | 123.1064 | -0.054932 | 123.0927 | 123.1934 | 123.0377 | 123.0469 | 123.0011 | -123.2025 | -123.0927 | 122.9599 | 123.056 | 59.967 | 59.8801
8.3281 | 123.2529 | -60.0632 | 63.0386 | -0.06813 | -0.00035668 | 0.064636 | 0.070968 | -0.0022025 | 0.00031608 | 0.0013565 | -0.054688 | 0.00073263 | 0.06642 | 0.059116 | -0.00279 | 0.0025613 | -0.00099325 | -0.009155 | 62.9791 | -60.1776 | 62.97 | -59.9304 | -60.3149 | -0.036621 | -0.054932 | 62.9837 | -60.0449 | 63.0341 | -60.0952 | -60.2051 | -60.0311 | -0.11444 | -0.059509 | -0.068664 | 0.13275 | 60.0266 | -0.25177 | 60.141 | -0.13733 | 0.01831 | -0.054931 | -0.004577 | -0.032044 | 0.032043 | -0.14191 | 0.013733 | -0.16022 | 0.24719 | 123.1476 | -0.050354 | 123.0789 | 123.1567 | 123.0286 | 123.0423 | 123.0469 | -123.2162 | -123.0835 | 123.0331 | 123.0972 | 60.054 | 60.0082
9.3281 | 123.2483 | -60.022 | 63.0249 | -0.06813 | 0.00092492 | 0.06485 | 0.071609 | 0.0029245 | -0.00032472 | 0.00092933 | -0.018066 | 0.0013736 | 0.065138 | 0.060825 | -0.0025764 | 0.00063867 | -0.0029159 | 0.004578 | 63.0249 | -60.1776 | 63.0112 | -59.9075 | -60.2646 | 0.041199 | 0.054932 | 62.9837 | -60.0403 | 63.0661 | -60.0449 | -60.1547 | -59.9487 | -0.15564 | 0 | -0.013733 | 0.11444 | 60.0632 | -0.24261 | 60.2188 | -0.086975 | -0.01831 | -0.041198 | 0.041199 | -0.022888 | 0.073243 | -0.13275 | 0.091553 | -0.11444 | 0.27008 | 123.1888 | -0.004578 | 123.1064 | 123.2025 | 123.024 | 123.0469 | 123.0057 | -123.2025 | -123.0652 | 123.0331 | 123.0881 | 60.0266 | 60.0769
10.3281 | 123.2208 | -60.022 | 63.0341 | -0.10628 | 0.0015659 | 0.066986 | 0.072463 | -6.6126e-05 | 0.00052988 | -0.0012071 | -0.030273 | 0.00094643 | 0.064497 | 0.063388 | -0.00086737 | 0.0017069 | -0.00077965 | -0.050354 | 62.9929 | -60.1913 | 62.9288 | -59.9945 | -60.3516 | -0.10529 | -0.13275 | 62.9471 | -60.054 | 62.9929 | -60.1456 | -60.2463 | -60.0266 | -0.16937 | -0.041199 | -0.10529 | 0.027466 | 59.9167 | -0.32959 | 60.0861 | -0.16022 | -0.032043 | -0.086975 | -0.041199 | -0.1236 | -0.004577 | -0.2243 | 0.027466 | -0.19226 | 0.19684 | 123.1201 | -0.091553 | 123.0469 | 123.1842 | 123.0011 | 123.0148 | 122.9691 | -123.2254 | -123.0881 | 122.9507 | 123.0148 | 59.9716 | 59.8892
11.3281 | 123.2712 | -60.0174 | 63.0478 | -0.06813 | 0.0026339 | 0.063354 | 0.072677 | 0.0033517 | -0.0016065 | -0.00099327 | -0.0089111 | 0.00094643 | 0.064283 | 0.06467 | -0.001081 | 0.0023477 | 0.00028835 | 0 | 63.0386 | -60.1547 | 63.0066 | -59.8389 | -60.2509 | 0.032043 | 0.041199 | 62.9974 | -60.0128 | 63.0798 | -60.054 | -60.1501 | -59.9396 | -0.13733 | -0.009156 | -0.041199 | 0.17853 | 60.0494 | -0.23346 | 60.1868 | -0.09613 | 0.004578 | -0.050354 | 0.032043 | -0.036621 | 0.07782 | -0.13275 | 0.073242 | -0.13733 | 0.31586 | 123.1613 | -0.041199 | 123.0927 | 123.1934 | 123.0103 | 123.056 | 123.0148 | -123.2025 | -123.0606 | 123.024 | 123.0972 | 60.0174 | 60.0586
12.3281 | 123.3398 | -59.9716 | 63.0157 | -0.060501 | 0.00028412 | 0.065277 | 0.070541 | -0.0030569 | 0.00052988 | -0.0022751 | 0.064331 | 9.1834e-05 | 0.065138 | 0.050785 | 0.00020083 | -0.00042933 | 0.0013565 | 0.036621 | 62.9608 | -60.1227 | 63.0661 | -59.8114 | -60.1593 | 0.10986 | 0.13733 | 62.9288 | -59.9991 | 63.1256 | -59.9579 | -60.0494 | -59.8892 | -0.15106 | -0.054932 | 0.050354 | 0.16022 | 60.0815 | -0.18768 | 60.2325 | -0.036621 | -0.027465 | -0.086975 | 0.10986 | 0.013733 | 0.082398 | -0.077819 | 0.10986 | -0.050354 | 0.31128 | 123.1888 | 0.041198 | 123.1247 | 123.0835 | 122.9279 | 122.9324 | 122.9004 | -123.1384 | -123.0148 | 123.0377 | 123.0972 | 60.0082 | 60.1089
13.3281 | 123.2483 | -60.0311 | 63.0661 | -0.10628 | 0.00092492 | 0.063995 | 0.071181 | 0.00014747 | -0.0039563 | -0.0018479 | -0.048584 | 0.002228 | 0.065779 | 0.067234 | -0.004499 | 0.00085247 | -0.0029159 | -0.07782 | 62.9745 | -60.2005 | 62.9379 | -59.9854 | -60.3699 | -0.068665 | -0.1236 | 62.9379 | -60.0723 | 63.002 | -60.1501 | -60.2509 | -60.0174 | -0.16937 | -0.091553 | -0.12817 | 0.045776 | 59.9625 | -0.33874 | 60.1318 | -0.16937 | -0.041199 | -0.12817 | -0.064087 | -0.11902 | 0.013733 | -0.21973 | 0.054932 | -0.17853 | 0.21515 | 123.1384 | -0.077819 | 123.0743 | 123.175 | 123.0103 | 123.0057 | 122.9691 | -123.2666 | -123.1384 | 122.9691 | 123.0331 | 59.9533 | 59.9075
14.3281 | 123.2208 | -60.0403 | 63.0112 | -0.098648 | 0.00049772 | 0.064636 | 0.073531 | 0.0033517 | 0.00010248 | 0.0024245 | -0.048584 | 0.0026552 | 0.065779 | 0.062961 | -0.0015082 | 0.0017069 | 0.00050195 | -0.086975 | 62.9745 | -60.2051 | 62.9013 | -60.0311 | -60.3745 | -0.10986 | -0.16479 | 62.9608 | -60.0906 | 62.9929 | -60.1501 | -60.26 | -60.0266 | -0.16479 | -0.036621 | -0.10986 | 0.009155 | 59.9304 | -0.33417 | 60.0952 | -0.16937 | -0.050354 | -0.050354 | -0.01831 | -0.10986 | 0.013733 | -0.21973 | 0.064087 | -0.16937 | 0.17395 | 123.1064 | -0.059509 | 123.0835 | 123.1796 | 123.0515 | 123.0148 | 123.0011 | -123.2162 | -123.1018 | 122.9416 | 123.0331 | 59.9533 | 59.8755
15.3281 | 123.2529 | -60.0403 | 63.0112 | -0.06813 | 0.0015659 | 0.065918 | 0.072677 | 0.0027109 | -0.00075192 | 0.0037063 | -0.039429 | -0.00033537 | 0.064924 | 0.061252 | -0.00279 | 0.00042507 | -0.0020615 | 0.013733 | 62.9929 | -60.1593 | 63.002 | -59.8846 | -60.26 | 0.027466 | 0.041199 | 62.9608 | -60.0174 | 63.0707 | -60.0403 | -60.1456 | -59.9396 | -0.11902 | -0.01831 | -0.009155 | 0.15564 | 60.0677 | -0.21973 | 60.1868 | -0.10071 | 0.022888 | -0.050354 | 0.05951 | 0 | 0.10071 | -0.10529 | 0.07782 | -0.12817 | 0.27466 | 123.1613 | -0.022888 | 123.0881 | 123.1522 | 122.9782 | 123.0331 | 123.0011 | -123.1705 | -123.0286 | 123.0423 | 123.111 | 60.054 | 60.0815
16.3281 | 123.2254 | -60.0174 | 63.0295 | -0.037613 | 0.00049772 | 0.065277 | 0.071822 | 0.0035653 | -0.0028881 | 0.00092933 | -0.066895 | 0.00094643 | 0.064711 | 0.065097 | -0.00086737 | 0.0014933 | 0.0019973 | -0.045776 | 63.002 | -60.2005 | 62.9379 | -59.9487 | -60.3195 | -0.07782 | -0.1236 | 62.9837 | -60.0677 | 63.0112 | -60.1227 | -60.26 | -59.9991 | -0.1831 | -0.027466 | -0.091553 | 0.068665 | 59.9396 | -0.30212 | 60.1227 | -0.11902 | -0.050354 | -0.045776 | -0.018311 | -0.10529 | 0.018311 | -0.24262 | 0.068665 | -0.19226 | 0.25177 | 123.1384 | -0.054932 | 123.0789 | 123.2025 | 123.0515 | 123.0194 | 123.0011 | -123.23 | -123.0972 | 122.9553 | 123.0286 | 59.9716 | 59.8938
17.3281 | 123.2162 | -60.054 | 63.0157 | -0.10628 | 0.0015659 | 0.064422 | 0.073104 | -0.0013479 | 0.0011707 | -0.0014207 | -0.057739 | 0.00051903 | 0.063215 | 0.064029 | -0.0015082 | 0.0014933 | 0.00028835 | -0.059509 | 63.002 | -60.1639 | 62.9333 | -59.9762 | -60.3058 | -0.073242 | -0.10071 | 62.9837 | -60.0815 | 63.0157 | -60.1318 | -60.2463 | -60.0082 | -0.10986 | -0.013733 | -0.082397 | 0.07782 | 59.9808 | -0.25177 | 60.0906 | -0.14191 | -0.027466 | -0.032043 | 0 | -0.07782 | 0.045776 | -0.19226 | 0.073242 | -0.16479 | 0.18768 | 123.0972 | -0.050354 | 123.0972 | 123.1659 | 123.0652 | 123.056 | 123.0377 | -123.1796 | -123.0972 | 122.9874 | 123.0698 | 59.9945 | 59.9533
18.3281 | 123.2025 | -60.0174 | 63.0112 | -0.022354 | 0.00028412 | 0.064636 | 0.071181 | 0.0022837 | 0.0018115 | -0.0014207 | -0.039429 | 0.0026552 | 0.064711 | 0.060825 | -0.0019354 | 0.0012797 | -0.0027023 | -0.050354 | 62.9837 | -60.1822 | 62.9379 | -59.9808 | -60.2783 | -0.082397 | -0.11902 | 62.9608 | -60.0586 | 63.0112 | -60.1501 | -60.26 | -60.0174 | -0.16479 | -0.027465 | -0.073242 | 0.036621 | 59.935 | -0.26093 | 60.0998 | -0.09613 | -0.041199 | -0.050354 | 0 | -0.13275 | 0 | -0.24262 | 0.041199 | -0.20142 | 0.20142 | 123.1201 | -0.091552 | 123.0698 | 123.1659 | 123.0194 | 123.0011 | 122.9782 | -123.1934 | -123.0698 | 122.9553 | 123.0286 | 59.967 | 59.8984
19.3281 | 123.262 | -60.0403 | 63.0157 | -0.06813 | 0.00071132 | 0.064209 | 0.07289 | 0.0016427 | 0.00010248 | -0.00056607 | -0.033325 | 0.00116 | 0.06407 | 0.066165 | -0.0040716 | 0.00063867 | 0.0054153 | 0 | 63.0112 | -60.1639 | 62.9929 | -59.9121 | -60.2783 | -0.004578 | 0 | 62.9791 | -60.0449 | 63.0478 | -60.0906 | -60.1913 | -59.967 | -0.1236 | -0.004578 | -0.022888 | 0.12817 | 60.0357 | -0.23804 | 60.1593 | -0.11444 | -0.004578 | -0.036621 | 0.032044 | -0.050354 | 0.073242 | -0.15106 | 0.07782 | -0.14648 | 0.25177 | 123.1567 | -0.045776 | 123.0927 | 123.175 | 123.024 | 123.0515 | 123.0194 | -123.1796 | -123.0606 | 123.0331 | 123.0881 | 60.0403 | 60.0403
20.3281 | 123.2025 | -60.0494 | 63.002 | -0.07576 | 0.00028412 | 0.065063 | 0.072036 | 0.0014291 | 0.00052988 | 0.00050193 | -0.030273 | 0.00030543 | 0.065138 | 0.063816 | -1.2774e-05 | 0.00085247 | -0.00035245 | -0.091553 | 62.9837 | -60.2097 | 62.8922 | -60.0494 | -60.3928 | -0.10986 | -0.15106 | 62.9562 | -60.0723 | 62.9883 | -60.1456 | -60.2509 | -60.0174 | -0.16022 | -0.01831 | -0.10986 | 0 | 59.9396 | -0.34332 | 60.0998 | -0.1831 | -0.022889 | -0.045776 | -0.013733 | -0.096131 | 0.032043 | -0.20142 | 0.054932 | -0.17853 | 0.16022 | 123.1018 | -0.073242 | 123.0606 | 123.1934 | 123.0286 | 123.0331 | 123.0057 | -123.2117 | -123.0743 | 122.9416 | 123.0377 | 59.9579 | 59.8984
21.3281 | 123.2025 | -60.054 | 63.0249 | -0.06813 | 0.0026339 | 0.06485 | 0.070754 | 0.0022837 | 0.00052988 | -0.00099327 | -0.042481 | 0.003937 | 0.063429 | 0.063816 | 0.0010552 | 0.0021341 | -0.00035245 | -0.091553 | 62.9745 | -60.2051 | 62.883 | -60.0586 | -60.3928 | -0.11444 | -0.16022 | 62.9562 | -60.0998 | 62.9929 | -60.1456 | -60.2463 | -60.0174 | -0.15106 | -0.050354 | -0.14191 | -0.004578 | 59.9396 | -0.33875 | 60.0906 | -0.18768 | -0.045776 | -0.068664 | -0.032043 | -0.091553 | 0.036621 | -0.19226 | 0.082397 | -0.14648 | 0.14648 | 123.0881 | -0.045777 | 123.0927 | 123.1796 | 123.056 | 123.0286 | 123.0103 | -123.23 | -123.1247 | 122.937 | 123.0469 | 59.9625 | 59.8938
22.3281 | 123.3215 | -60.0037 | 62.97 | -0.06813 | 0.0024203 | 0.065277 | 0.07225 | 0.0014291 | -0.00011112 | 0.0019973 | -0.0058593 | 9.1834e-05 | 0.06407 | 0.05933 | -0.0025764 | 0.0027751 | 0.0026383 | -0.091553 | 62.9562 | -60.1959 | 62.9791 | -59.935 | -60.3745 | -0.068665 | -0.082397 | 62.915 | -60.0632 | 63.0707 | -60.0311 | -60.1318 | -59.8892 | -0.19226 | -0.013733 | 0.009155 | 0.068664 | 59.935 | -0.37079 | 60.1273 | -0.17853 | -0.059509 | -0.054932 | 0.10071 | -0.027466 | 0.11444 | -0.12817 | 0.17395 | -0.068665 | 0.26093 | 123.175 | 0.032043 | 123.1338 | 123.1522 | 122.9782 | 122.9599 | 122.9187 | -123.1659 | -123.0331 | 122.9828 | 123.0743 | 59.9121 | 59.9213
23.3281 | 123.2849 | -60.0174 | 63.0203 | -0.052872 | 7.0518e-05 | 0.06485 | 0.071822 | 0.0014291 | -0.0026745 | -0.00056607 | -0.021118 | -0.00054897 | 0.066847 | 0.065311 | -0.00065377 | -2.13e-06 | -0.0048387 | 0.009155 | 63.0157 | -60.1776 | 62.9974 | -59.8984 | -60.26 | 0.013733 | 0.054932 | 63.0066 | -60.0632 | 63.0798 | -60.054 | -60.1456 | -59.9396 | -0.16022 | -0.004578 | -0.022888 | 0.11902 | 60.0311 | -0.24262 | 60.1913 | -0.082398 | -0.045776 | -0.013733 | 0.059509 | -0.036621 | 0.07782 | -0.12817 | 0.1236 | -0.082398 | 0.27924 | 123.175 | 0.009155 | 123.143 | 123.1934 | 123.0698 | 123.0331 | 123.024 | -123.1979 | -123.0835 | 123.0148 | 123.0972 | 60.0266 | 60.0723
24.3281 | 123.23 | -60.0449 | 63.0295 | -0.060501 | 0.0013523 | 0.064636 | 0.072036 | -0.0030569 | -0.00032472 | -0.0020615 | -0.051636 | 0.00051903 | 0.064924 | 0.064456 | -0.0042854 | 0.0021341 | 0.0015701 | -0.041199 | 63.0112 | -60.1868 | 62.9288 | -59.9716 | -60.3333 | -0.050354 | -0.1236 | 62.9471 | -60.0815 | 63.0249 | -60.1181 | -60.2371 | -60.0082 | -0.14191 | -0.018311 | -0.10071 | 0.073242 | 59.9945 | -0.28839 | 60.1364 | -0.14648 | -0.036621 | -0.082397 | -0.004578 | -0.073242 | 0.036621 | -0.19226 | 0.073242 | -0.15564 | 0.21515 | 123.1155 | -0.036621 | 123.1064 | 123.1979 | 123.0286 | 123.056 | 122.9919 | -123.2162 | -123.111 | 122.9736 | 123.0698 | 60.0037 | 59.9213
25.3281 | 123.2437 | -60.0174 | 63.0249 | -0.07576 | -0.00035668 | 0.066345 | 0.074599 | 0.0022837 | -0.0013929 | 0.0026383 | -0.030273 | 0.00030543 | 0.062788 | 0.061252 | -0.0019354 | 0.00063867 | 0.0026383 | 0.004578 | 63.0157 | -60.1547 | 62.9974 | -59.903 | -60.26 | 0.009155 | 0.013733 | 62.9562 | -60.054 | 63.0524 | -60.0632 | -60.1776 | -59.967 | -0.13733 | -0.009155 | -0.027465 | 0.11444 | 60.0266 | -0.24262 | 60.1639 | -0.10529 | -0.036621 | -0.068664 | 0.027466 | -0.045776 | 0.050354 | -0.16022 | 0.086975 | -0.1236 | 0.25177 | 123.1522 | -0.009155 | 123.1064 | 123.1705 | 123.0103 | 123.0331 | 122.9736 | -123.1796 | -123.0789 | 123.0148 | 123.0698 | 60.022 | 60.0311
26.3281 | 123.2895 | -60.0174 | 62.9517 | -0.083389 | -0.0012113 | 0.066131 | 0.071822 | 0.0018565 | -0.00053832 | -0.00035247 | -0.02417 | 0.00094643 | 0.063856 | 0.058261 | -0.003858 | 0.00042507 | 0.0015701 | -0.09613 | 62.9837 | -60.2005 | 62.9517 | -59.9762 | -60.3333 | -0.09613 | -0.032043 | 62.9425 | -60.0769 | 63.0661 | -60.0494 | -60.1639 | -59.9442 | -0.1831 | 0.032044 | 0 | 0.041199 | 59.9213 | -0.31586 | 60.1044 | -0.13275 | -0.059509 | -0.009155 | 0.11444 | -0.032043 | 0.073242 | -0.14648 | 0.13275 | -0.086975 | 0.2243 | 123.1522 | 0.027466 | 123.143 | 123.1842 | 123.0194 | 123.0011 | 122.9599 | -123.1522 | -123.0286 | 122.9691 | 123.0835 | 59.9213 | 59.9854
27.3281 | 123.23 | -60.054 | 63.0249 | 0.023422 | 0.00071132 | 0.065063 | 0.072463 | -0.0022025 | 0.00010248 | 0.0017837 | -0.030273 | 0.00116 | 0.065565 | 0.064884 | -0.0023626 | 0.0017069 | 0.00092935 | -0.018311 | 63.0157 | -60.1639 | 62.9883 | -59.935 | -60.3012 | -0.054932 | -0.041199 | 62.97 | -60.054 | 63.0341 | -60.1227 | -60.2142 | -59.9854 | -0.10986 | -0.009155 | -0.036621 | 0.11902 | 59.9991 | -0.24719 | 60.1089 | -0.13733 | 0 | -0.054931 | 0.009156 | -0.068665 | 0.068664 | -0.16022 | 0.068664 | -0.16022 | 0.22888 | 123.1522 | -0.068665 | 123.0881 | 123.1796 | 123.024 | 123.0698 | 123.024 | -123.1888 | -123.0789 | 123.0423 | 123.0881 | 60.0357 | 60.0128
28.3281 | 123.2162 | -60.0586 | 63.0249 | -0.060501 | 0.0015659 | 0.064209 | 0.068832 | 0.0048471 | -0.00011112 | -0.00013887 | -0.02417 | 0.00030543 | 0.063643 | 0.060398 | -0.0023626 | 0.0019205 | 0.00028835 | -0.10071 | 62.9883 | -60.1639 | 62.8922 | -60.0311 | -60.3745 | -0.1236 | -0.17853 | 62.9517 | -60.0906 | 63.002 | -60.1501 | -60.2554 | -60.0174 | -0.10529 | -0.036621 | -0.13275 | 0.027466 | 59.935 | -0.31586 | 60.0403 | -0.21057 | -0.032043 | -0.073242 | -0.022888 | -0.091552 | 0.041199 | -0.19684 | 0.073242 | -0.16479 | 0.13275 | 123.056 | -0.059509 | 123.0927 | 123.1522 | 123.0423 | 123.0469 | 123.0103 | -123.1888 | -123.1155 | 122.9507 | 123.0606 | 59.9579 | 59.8801
29.3281 | 123.2208 | -60.0266 | 62.9974 | -0.060501 | 7.0518e-05 | 0.065277 | 0.071609 | 0.0014291 | 0.00095708 | -0.00013887 | -0.042481 | 0.0018008 | 0.065779 | 0.063602 | -0.0019354 | 0.0019205 | -0.0029159 | -0.018311 | 62.9883 | -60.1868 | 63.002 | -59.9213 | -60.2875 | -0.018311 | -0.032043 | 62.9745 | -60.0357 | 63.0386 | -60.0815 | -60.1868 | -59.9762 | -0.16022 | -0.009156 | 0.004577 | 0.10529 | 60.0082 | -0.26093 | 60.1685 | -0.10071 | -0.009156 | -0.022889 | 0.041198 | -0.054932 | 0.050354 | -0.16022 | 0.05951 | -0.15106 | 0.2655 | 123.1888 | -0.045776 | 123.0743 | 123.175 | 123.0103 | 123.0148 | 123.0011 | -123.1842 | -123.0331 | 123.0286 | 123.0652 | 60.0082 | 59.9945
30.3281 | 123.2117 | -60.0357 | 62.9929 | -0.098648 | 0.0024203 | 0.064636 | 0.069259 | -0.0017751 | 0.0015979 | 0.00071573 | -0.039429 | 0.0013736 | 0.064283 | 0.061466 | -1.2774e-05 | 0.0029887 | 0.00071555 | -0.07782 | 63.002 | -60.1913 | 62.8967 | -60.054 | -60.3836 | -0.12817 | -0.16479 | 62.9517 | -60.0677 | 62.9837 | -60.141 | -60.2554 | -60.0128 | -0.15564 | 0.009155 | -0.09613 | -0.01831 | 59.9075 | -0.3479 | 60.0632 | -0.19226 | -0.032043 | -0.041199 | -0.009155 | -0.10529 | 0.022889 | -0.21973 | 0.054932 | -0.18768 | 0.13733 | 123.0881 | -0.073242 | 123.0515 | 123.1934 | 123.0194 | 123.0377 | 122.9874 | -123.1842 | -123.0606 | 122.9324 | 123.0194 | 59.9579 | 59.8709
31.3281 | 123.262 | -60.0311 | 63.0432 | -0.037613 | -0.00057028 | 0.063354 | 0.070968 | -0.00049353 | -0.0013929 | -0.0024887 | 0.0063477 | 0.0015872 | 0.065352 | 0.065311 | -0.0019354 | 0.00021147 | 0.0013565 | 0.013733 | 63.0066 | -60.1639 | 62.9929 | -59.8938 | -60.2554 | 0.022888 | 0.041199 | 62.9745 | -60.0357 | 63.0798 | -60.0494 | -60.1501 | -59.9396 | -0.13275 | -0.036621 | -0.050354 | 0.13733 | 60.054 | -0.2243 | 60.1868 | -0.091553 | -0.004578 | -0.068665 | 0.036621 | -0.01831 | 0.091553 | -0.11902 | 0.096131 | -0.11444 | 0.27008 | 123.1567 | -0.013732 | 123.1155 | 123.1705 | 123.0103 | 123.0377 | 123.0057 | -123.2071 | -123.0789 | 123.024 | 123.111 | 60.0449 | 60.0723
32.3438 | 123.2391 | -60.0082 | 63.0386 | -0.045242 | 0.00049772 | 0.063354 | 0.071395 | 0.00057467 | 0.00010248 | 0.0013565 | -0.021118 | 0.00094643 | 0.063643 | 0.063175 | -0.00065377 | 0.0042703 | -0.00013885 | 0 | 63.0112 | -60.1501 | 62.9974 | -59.9121 | -60.2554 | 0 | 0.009155 | 62.9517 | -60.0449 | 63.0432 | -60.0586 | -60.1685 | -59.9625 | -0.14191 | -0.027466 | -0.041198 | 0.096131 | 60.0082 | -0.24719 | 60.1501 | -0.10529 | -0.036621 | -0.086975 | 0.004578 | -0.050354 | 0.045777 | -0.16022 | 0.082398 | -0.1236 | 0.23804 | 123.1476 | -0.013733 | 123.0881 | 123.1613 | 122.9965 | 123.0194 | 122.9599 | -123.1888 | -123.0835 | 123.0057 | 123.0515 | 60.0082 | 60.0174
33.3281 | 123.2346 | -60.0266 | 63.0112 | -0.098648 | 0.0015659 | 0.064636 | 0.071609 | 0.00057467 | -0.00032472 | 0.00092933 | -0.02417 | 0.0013736 | 0.063856 | 0.06702 | -0.0030036 | 0.0023477 | -0.0024887 | -0.004578 | 63.002 | -60.1639 | 62.97 | -59.9213 | -60.2921 | -0.013733 | -0.009155 | 62.9745 | -60.054 | 63.0386 | -60.0906 | -60.1822 | -59.9625 | -0.13733 | -0.009155 | -0.041198 | 0.10529 | 60.0128 | -0.2655 | 60.1501 | -0.12817 | -0.027466 | -0.036621 | 0.027466 | -0.064087 | 0.064087 | -0.15564 | 0.091553 | -0.12817 | 0.24261 | 123.1338 | -0.036621 | 123.0927 | 123.1659 | 123.0286 | 123.0286 | 123.0011 | -123.175 | -123.0652 | 122.9965 | 123.0652 | 60.022 | 60.0174
34.3281 | 123.2025 | -60.0449 | 63.0203 | -0.083389 | 0.0022067 | 0.063995 | 0.070541 | 0.0012155 | 0.00031608 | 0.0017837 | -0.02417 | 0.0015872 | 0.064497 | 0.060825 | -0.00065377 | 0.0023477 | 0.0030655 | -0.086975 | 63.0112 | -60.1868 | 62.8922 | -60.0403 | -60.3882 | -0.1236 | -0.16479 | 62.9883 | -60.0906 | 62.9883 | -60.1364 | -60.2554 | -60.0128 | -0.14191 | -0.009156 | -0.12817 | 0.004578 | 59.9213 | -0.34332 | 60.0632 | -0.20142 | -0.045776 | -0.032044 | -0.032044 | -0.091553 | 0.032044 | -0.21057 | 0.07782 | -0.16479 | 0.14648 | 123.0789 | -0.045777 | 123.0789 | 123.1979 | 123.0789 | 123.056 | 123.0331 | -123.2071 | -123.111 | 122.937 | 123.0331 | 59.9579 | 59.8801
35.3281 | 123.23 | -60.0082 | 63.0203 | -0.052872 | 0.00092492 | 0.063354 | 0.070113 | -0.00070713 | -0.00053832 | -0.0012071 | -0.027222 | 9.1834e-05 | 0.063215 | 0.062534 | -0.00065377 | -2.13e-06 | 0.0011429 | 0.013733 | 63.0066 | -60.1639 | 63.0066 | -59.8984 | -60.2554 | 0 | 0.018311 | 62.9608 | -60.0449 | 63.0707 | -60.054 | -60.1685 | -59.9487 | -0.15564 | -0.013733 | -0.013733 | 0.10986 | 60.0082 | -0.24719 | 60.1639 | -0.091553 | -0.036621 | -0.05951 | 0.050354 | -0.045776 | 0.05951 | -0.16022 | 0.096131 | -0.1236 | 0.2655 | 123.1705 | -0.009155 | 123.1155 | 123.1705 | 123.0057 | 123.0148 | 122.9691 | -123.1842 | -123.0652 | 123.0148 | 123.0789 | 60.022 | 60.0266
36.3281 | 123.2208 | -60.0632 | 63.002 | -0.052872 | 0.0011385 | 0.06549 | 0.070754 | -0.0030569 | -0.00075192 | 0.00092933 | -0.039429 | 0.00073263 | 0.066206 | 0.066379 | -0.0034308 | 0.0025613 | 0.00092935 | -0.036621 | 62.9974 | -60.1913 | 62.9242 | -59.9854 | -60.3378 | -0.091553 | -0.14648 | 62.9837 | -60.054 | 62.9929 | -60.1273 | -60.2509 | -60.0311 | -0.12817 | -0.004577 | -0.07782 | 0.077819 | 59.9716 | -0.27466 | 60.0998 | -0.14648 | 0.009155 | -0.01831 | -0.009155 | -0.064087 | 0.032043 | -0.18768 | 0.022888 | -0.19684 | 0.20599 | 123.1155 | -0.073242 | 123.0469 | 123.1888 | 123.0377 | 123.0606 | 123.0469 | -123.1934 | -123.056 | 122.9874 | 123.056 | 60.0266 | 59.9167
37.3281 | 123.2895 | -59.9945 | 63.0295 | -0.045242 | 0.0019931 | 0.063995 | 0.073531 | 0.0022837 | 0.00010248 | -0.0033433 | -0.048584 | -0.0014036 | 0.064924 | 0.058689 | -0.001081 | 0.00085247 | -0.00013885 | -0.009155 | 63.0569 | -60.1364 | 62.97 | -59.9396 | -60.2509 | 0.022888 | 0.009155 | 62.9745 | -60.0586 | 63.0661 | -60.0266 | -60.1547 | -59.9487 | -0.14191 | 0.027466 | -0.059509 | 0.054932 | 60.0174 | -0.25635 | 60.1593 | -0.11444 | -0.064087 | -0.054932 | 0.036621 | -0.032043 | 0.045777 | -0.16022 | 0.10986 | -0.09613 | 0.19684 | 123.1064 | 0.032044 | 123.1247 | 123.1934 | 123.0331 | 123.0515 | 122.9691 | -123.1659 | -123.0881 | 122.9645 | 123.0606 | 59.9854 | 60.0037
38.3281 | 123.23 | -60.0449 | 62.97 | -0.060501 | 0.0011385 | 0.063141 | 0.071609 | 0.00057467 | -0.0024609 | 0.00050193 | -0.027222 | 0.00094643 | 0.064283 | 0.06467 | -0.00022637 | 0.0012797 | -0.0012071 | -0.091553 | 62.9974 | -60.2005 | 62.9105 | -60.0082 | -60.3607 | -0.1236 | -0.16479 | 62.9608 | -60.0677 | 63.002 | -60.1456 | -60.2325 | -60.0037 | -0.15564 | 0.027466 | -0.05951 | 0.036621 | 59.9213 | -0.31586 | 60.0769 | -0.16022 | -0.022888 | -0.009156 | 0.032043 | -0.10071 | 0.041199 | -0.18768 | 0.064087 | -0.16479 | 0.19226 | 123.111 | -0.07782 | 123.0698 | 123.1979 | 123.0286 | 123.0423 | 123.0057 | -123.1705 | -123.0377 | 122.9553 | 123.0469 | 59.9533 | 59.8801
39.3281 | 123.2574 | -60.0266 | 63.0157 | -0.083389 | 0.00092492 | 0.064422 | 0.070113 | -0.0047659 | 0.00074348 | -0.00013887 | -0.02417 | 0.00094643 | 0.063643 | 0.061679 | 0.00041443 | 0.0027751 | -0.0014207 | 0.004578 | 63.002 | -60.1776 | 62.9929 | -59.903 | -60.2737 | 0.013733 | 0.036621 | 62.9654 | -60.022 | 63.0753 | -60.0494 | -60.1501 | -59.9442 | -0.15106 | -0.013733 | -0.022888 | 0.1236 | 60.0403 | -0.24719 | 60.1913 | -0.096131 | 0.004577 | -0.050354 | 0.059509 | -0.022888 | 0.082397 | -0.1236 | 0.07782 | -0.12817 | 0.27466 | 123.1705 | -0.027465 | 123.0972 | 123.1796 | 122.9874 | 123.0286 | 122.9919 | -123.1934 | -123.0377 | 123.0194 | 123.1018 | 60.0311 | 60.0632
40.3281 | 123.2162 | -60.0449 | 63.0112 | -0.091019 | 0.00028412 | 0.063781 | 0.071822 | 0.0016427 | 0.00010248 | 7.4734e-05 | -0.018066 | 0.00116 | 0.062788 | 0.060184 | -0.002149 | 0.0023477 | -0.00077965 | -0.086975 | 63.0203 | -60.1959 | 62.9379 | -59.9854 | -60.379 | -0.09613 | -0.1236 | 62.97 | -60.0861 | 62.9974 | -60.1456 | -60.2417 | -60.0128 | -0.15106 | 0.009156 | -0.073242 | 0.059509 | 59.9487 | -0.33417 | 60.0998 | -0.1831 | -0.041199 | -0.041198 | -0.013732 | -0.10071 | 0.032044 | -0.19684 | 0.073243 | -0.15564 | 0.21057 | 123.1338 | -0.059509 | 123.0835 | 123.2162 | 123.056 | 123.0652 | 123.0148 | -123.2071 | -123.0972 | 122.9828 | 123.0423 | 59.9579 | 59.9213
41.3281 | 123.2483 | -60.0403 | 63.0341 | -0.022354 | 0.00028412 | 0.064422 | 0.073745 | -0.00027993 | -0.00075192 | -0.0016343 | -0.0058593 | 0.00030543 | 0.065138 | 0.06232 | -0.0017218 | 0.0012797 | -0.0027023 | 0.032043 | 63.0112 | -60.1456 | 63.0157 | -59.8984 | -60.26 | 0.022888 | 0.045776 | 62.9471 | -60.0311 | 63.0569 | -60.0449 | -60.141 | -59.9487 | -0.10529 | -0.022889 | -0.018311 | 0.14191 | 60.0632 | -0.21973 | 60.1685 | -0.11444 | 0.009155 | -0.086975 | 0.022888 | -0.004578 | 0.091553 | -0.10071 | 0.082398 | -0.10986 | 0.24719 | 123.1613 | -0.013733 | 123.0881 | 123.1567 | 122.9782 | 123.0515 | 122.9874 | -123.1796 | -123.0652 | 123.056 | 123.0972 | 60.0723 | 60.0861
42.3281 | 123.1979 | -60.0494 | 63.0295 | -0.091019 | 0.0017795 | 0.066986 | 0.072677 | 0.0035653 | 0.00031608 | 0.0013565 | -0.051636 | 9.1834e-05 | 0.065352 | 0.067447 | -0.002149 | -0.00021573 | -0.00035245 | -0.032043 | 63.0066 | -60.2097 | 62.9562 | -59.9442 | -60.3104 | -0.045776 | -0.068665 | 62.9791 | -60.0769 | 63.0157 | -60.1044 | -60.2051 | -60.0082 | -0.16022 | -0.022888 | -0.073242 | 0.10529 | 60.0037 | -0.26093 | 60.1639 | -0.10071 | -0.027466 | -0.050354 | -0.013733 | -0.054932 | 0.041198 | -0.15564 | 0.068664 | -0.12817 | 0.2655 | 123.1659 | -0.027466 | 123.0927 | 123.2162 | 123.056 | 123.056 | 123.0286 | -123.2391 | -123.1064 | 123.0057 | 123.0652 | 60.0174 | 59.9808
43.3281 | 123.2346 | -60.0266 | 63.0203 | -0.014725 | -0.0012113 | 0.06549 | 0.071822 | 0.0022837 | -0.00011112 | 7.4734e-05 | -0.0089111 | 0.00073263 | 0.063002 | 0.062747 | -0.00043997 | 0.0021341 | 0.0013565 | 0.004578 | 63.0112 | -60.1593 | 62.9974 | -59.8984 | -60.2554 | 0.036621 | 0.032043 | 62.9837 | -60.0403 | 63.0707 | -60.0494 | -60.1547 | -59.935 | -0.13275 | -0.009156 | -0.022888 | 0.12817 | 60.0632 | -0.22888 | 60.1959 | -0.09613 | -0.013733 | -0.036621 | 0.050354 | -0.022888 | 0.091552 | -0.12817 | 0.10529 | -0.11444 | 0.26093 | 123.1567 | -0.009155 | 123.111 | 123.1705 | 123.024 | 123.0377 | 123.0103 | -123.1796 | -123.0606 | 123.024 | 123.0972 | 60.0311 | 60.0586
44.3281 | 123.2666 | -59.9945 | 63.0157 | -0.07576 | -0.00014308 | 0.064422 | 0.072036 | 0.00036107 | -0.00053832 | 7.4734e-05 | -0.021118 | 0.00094643 | 0.065352 | 0.063602 | -0.0017218 | 0.0017069 | -0.0014207 | 0.018311 | 63.0203 | -60.1639 | 62.9837 | -59.8984 | -60.2417 | 0.009155 | 0.045776 | 62.97 | -60.0266 | 63.0707 | -60.0311 | -60.1547 | -59.9442 | -0.16937 | 0.004578 | -0.032043 | 0.096131 | 60.0037 | -0.24719 | 60.173 | -0.07782 | -0.032043 | -0.045776 | 0.054932 | -0.036621 | 0.050354 | -0.16022 | 0.082397 | -0.12817 | 0.2655 | 123.1476 | -0.004578 | 123.0972 | 123.1842 | 122.9965 | 123.0148 | 122.9645 | -123.1796 | -123.0423 | 122.9782 | 123.0652 | 60.0128 | 60.0403
45.3281 | 123.2162 | -60.0037 | 63.0432 | -0.022354 | -0.00057028 | 0.063781 | 0.070541 | -0.0019889 | -0.00032472 | -0.0014207 | 0.0093995 | 0.00116 | 0.063215 | 0.057193 | -0.0012946 | 0.0012797 | -0.00035245 | -0.013733 | 63.0569 | -60.1501 | 62.9379 | -59.9442 | -60.2875 | 0.013733 | 0.004578 | 62.97 | -60.0403 | 63.0203 | -60.0906 | -60.173 | -59.9762 | -0.14648 | 0.013733 | -0.10529 | 0.059509 | 60.0174 | -0.28381 | 60.1639 | -0.13733 | -0.036621 | -0.073242 | -0.022888 | -0.086975 | 0.027466 | -0.16937 | 0.064087 | -0.13275 | 0.20599 | 123.0881 | -0.050354 | 123.0606 | 123.2071 | 123.0103 | 123.0606 | 122.9736 | -123.1934 | -123.0835 | 122.9416 | 123.024 | 59.9899 | 60.0082
46.3281 | 123.2071 | -60.0128 | 63.0112 | -0.060501 | 0.0024203 | 0.06549 | 0.07289 | 0.0014291 | -0.0022473 | 7.4734e-05 | -0.033325 | 0.0020144 | 0.063002 | 0.062107 | -0.002149 | 0.0034159 | 0.0026383 | -0.036621 | 62.9929 | -60.1959 | 62.97 | -59.9396 | -60.3058 | -0.054932 | -0.041199 | 62.9608 | -60.0494 | 63.0386 | -60.1089 | -60.2325 | -59.9625 | -0.18311 | -0.01831 | -0.041198 | 0.073242 | 59.9579 | -0.29297 | 60.141 | -0.10986 | -0.036621 | -0.050354 | 0.027466 | -0.096131 | 0.050354 | -0.21973 | 0.086975 | -0.18311 | 0.25635 | 123.1659 | -0.05951 | 123.0881 | 123.1888 | 123.0103 | 123.0057 | 122.9736 | -123.2071 | -123.0606 | 122.9828 | 123.0515 | 59.9762 | 59.9716
47.3281 | 123.2666 | -60.022 | 63.0203 | 0.00053424 | 0.0019931 | 0.064636 | 0.072463 | -0.00027993 | 0.00095708 | 0.00092933 | -0.0058593 | 0.0013736 | 0.066847 | 0.057621 | -0.002149 | 0.0017069 | 0.00092935 | 0.004578 | 63.0157 | -60.1639 | 62.9196 | -60.0586 | -60.1868 | 0.041199 | 0.045776 | 62.9974 | -60.0266 | 63.0569 | -60.0494 | -60.1364 | -59.9442 | -0.14191 | -0.004578 | -0.10071 | -0.036621 | 60.0632 | -0.16479 | 60.2051 | -0.022889 | -0.004577 | -0.022888 | 0.036621 | -0.027465 | 0.07782 | -0.11444 | 0.082397 | -0.10986 | 0.10529 | 123.0835 | -0.022888 | 123.0835 | 123.1796 | 123.024 | 123.0377 | 123.0194 | -123.1842 | -123.0469 | 122.9416 | 123.0789 | 60.0266 | 60.0677
48.3281 | 123.2208 | -60.0082 | 63.0249 | -0.091019 | 0.00049772 | 0.065063 | 0.071395 | 0.0029245 | 0.0013843 | -0.0024887 | -0.048584 | 0.0013736 | 0.06642 | 0.062747 | -0.0025764 | 0.0025613 | -0.0012071 | 0.004578 | 62.9929 | -60.1822 | 62.9929 | -59.9121 | -60.2783 | -0.009155 | 0.022888 | 62.97 | -60.0403 | 63.0524 | -60.0632 | -60.1776 | -59.9716 | -0.17395 | -0.032043 | -0.032043 | 0.096131 | 59.9991 | -0.27008 | 60.173 | -0.09613 | -0.032043 | -0.054931 | 0.027466 | -0.054931 | 0.036621 | -0.16937 | 0.068664 | -0.13733 | 0.27008 | 123.175 | -0.022888 | 123.0927 | 123.175 | 123.0103 | 123.0011 | 122.9782 | -123.2071 | -123.0652 | 123.0011 | 123.0606 | 60.0128 | 60.0311
49.3281 | 123.2208 | -60.0128 | 63.0615 | -0.06813 | -0.00035668 | 0.063568 | 0.070541 | 0.00057467 | -0.0016065 | -0.0048385 | 0.0093995 | 0.00094643 | 0.065138 | 0.064884 | -0.0023626 | 0.0034159 | 0.0013565 | -0.004578 | 63.0341 | -60.1456 | 62.9517 | -59.9579 | -60.2692 | 0 | 0 | 62.9791 | -60.0677 | 63.0341 | -60.0677 | -60.173 | -59.967 | -0.13275 | -0.027465 | -0.10986 | 0.054931 | 60.0128 | -0.25635 | 60.1456 | -0.1236 | -0.054932 | -0.082397 | -0.027465 | -0.054932 | 0.045776 | -0.16022 | 0.10071 | -0.10529 | 0.18768 | 123.0972 | 0 | 123.1018 | 123.1796 | 123.0469 | 123.0469 | 122.9919 | -123.2071 | -123.1293 | 122.9645 | 123.0469 | 60.0082 | 60.0128
50.3281 | 123.2895 | -60.0357 | 63.0249 | -0.07576 | 0.0022067 | 0.063995 | 0.071181 | 0.00036107 | -0.0011791 | -0.00056607 | -0.045532 | 0.00073263 | 0.067061 | 0.058048 | -0.0015082 | 0.0021341 | -0.0022751 | -0.004578 | 63.0157 | -60.173 | 63.0066 | -59.903 | -60.2554 | 0.009155 | 0.036621 | 62.9654 | -60.0403 | 63.0615 | -60.0449 | -60.1501 | -59.9442 | -0.13733 | -0.009155 | -0.01831 | 0.13275 | 60.0449 | -0.21973 | 60.1822 | -0.082397 | -0.004577 | -0.059509 | 0.036621 | -0.009155 | 0.091553 | -0.11444 | 0.09613 | -0.10986 | 0.27008 | 123.1796 | -0.004578 | 123.1018 | 123.1888 | 123.0057 | 123.0515 | 123.0011 | -123.1979 | -123.0652 | 123.0423 | 123.0972 | 60.0311 | 60.0723
51.3281 | 123.2208 | -60.022 | 63.0615 | -0.029984 | 0.0013523 | 0.065918 | 0.0699 | 0.0018565 | -0.0045971 | -0.00035247 | 0.024658 | 0.00073263 | 0.065779 | 0.058048 | -0.0012946 | 0.00042507 | 0.0013565 | 0.004578 | 63.0157 | -60.1273 | 62.9883 | -59.935 | -60.26 | 0.036621 | 0.022888 | 63.0066 | -60.0311 | 63.0386 | -60.0723 | -60.1593 | -59.9808 | -0.10528 | -0.045776 | -0.073242 | 0.086975 | 60.0586 | -0.23804 | 60.1639 | -0.13275 | -0.009155 | -0.054931 | -0.022888 | -0.050354 | 0.041199 | -0.13733 | 0.050354 | -0.12817 | 0.19226 | 123.1155 | -0.041199 | 123.0698 | 123.143 | 123.0377 | 123.0377 | 123.0286 | -123.1888 | -123.0927 | 123.0103 | 123.0606 | 60.0266 | 60.0449
52.3281 | 123.1888 | -60.0266 | 63.0386 | -0.029984 | 0.00049772 | 0.063995 | 0.070541 | -0.0011343 | -0.00032472 | -0.00099327 | -0.0089111 | -0.00054897 | 0.065779 | 0.062961 | 0.00041443 | 0.0014933 | -0.0012071 | -0.004578 | 63.0249 | -60.1593 | 62.9517 | -59.935 | -60.2692 | 0.009155 | 0.009155 | 62.9974 | -60.0128 | 63.0386 | -60.0403 | -60.1318 | -60.0174 | -0.13275 | -0.013733 | -0.086975 | 0.091552 | 60.0357 | -0.24262 | 60.1685 | -0.10986 | 0.013733 | -0.041198 | 0 | -0.013733 | 0.009155 | -0.10529 | -0.004578 | -0.11902 | 0.2243 | 123.111 | -0.027466 | 123.0515 | 123.1842 | 123.0103 | 123.0515 | 123.024 | -123.1979 | -123.0515 | 122.9782 | 123.0652 | 60.022 | 60.0357
53.3281 | 123.23 | -60.022 | 63.0569 | -0.0070953 | 0.00028412 | 0.062072 | 0.072036 | -0.0015615 | 0.00074348 | -0.0041977 | -0.02417 | 0.002869 | 0.06642 | 0.065525 | -0.001081 | 0.00021147 | -0.0016343 | -0.018311 | 63.0432 | -60.1639 | 62.9608 | -59.9625 | -60.2829 | 0 | 0.009155 | 62.9929 | -60.0357 | 63.0386 | -60.0586 | -60.173 | -59.9579 | -0.14191 | -0.013733 | -0.096131 | 0.05951 | 60.022 | -0.26093 | 60.1639 | -0.11902 | -0.013733 | -0.064087 | -0.018311 | -0.036621 | 0.064087 | -0.15106 | 0.07782 | -0.13733 | 0.20142 | 123.1247 | -0.022888 | 123.0743 | 123.2071 | 123.0286 | 123.0652 | 123.0148 | -123.2208 | -123.0927 | 122.9828 | 123.0606 | 60.0037 | 60.0311
54.3281 | 123.2666 | -60.0128 | 63.0157 | -0.0070953 | 0.00028412 | 0.063568 | 0.070541 | 0.0027109 | -0.0013929 | -0.00077967 | -0.048584 | 0.0035098 | 0.065138 | 0.06937 | -1.2774e-05 | 0.0025613 | 0.0011429 | 0.022888 | 62.9974 | -60.1868 | 63.002 | -59.9121 | -60.2646 | 0.013733 | 0.050354 | 62.9654 | -60.0494 | 63.0707 | -60.0449 | -60.1593 | -59.9533 | -0.17395 | -0.01831 | -0.013733 | 0.10071 | 60.0266 | -0.25177 | 60.2005 | -0.077819 | -0.036621 | -0.050354 | 0.054932 | -0.032044 | 0.059509 | -0.14648 | 0.09613 | -0.10986 | 0.27466 | 123.1888 | 0.004577 | 123.1201 | 123.1842 | 123.0148 | 123.0103 | 122.9782 | -123.2025 | -123.0652 | 123.0148 | 123.0835 | 60.0357 | 60.0632
55.3281 | 123.2025 | -60.0266 | 63.0661 | -0.037613 | -0.00035668 | 0.063141 | 0.070754 | -0.0015615 | -0.0011791 | -0.00077967 | -0.0028075 | 0.00116 | 0.066206 | 0.05933 | -0.0015082 | 0.0012797 | 0.00050195 | -0.013733 | 63.0432 | -60.1685 | 62.9471 | -59.9487 | -60.2783 | 0.027466 | 0.013733 | 63.0157 | -60.0311 | 63.002 | -60.0769 | -60.173 | -59.9808 | -0.14191 | -0.022888 | -0.11902 | 0.07782 | 60.054 | -0.25177 | 60.1959 | -0.10986 | -0.004578 | -0.050354 | -0.064087 | -0.050354 | 0.045776 | -0.14648 | 0.050354 | -0.14191 | 0.21973 | 123.1155 | -0.045776 | 123.0331 | 123.2117 | 123.0469 | 123.0698 | 123.0423 | -123.2346 | -123.0972 | 122.9736 | 123.0286 | 60.0128 | 60.0403
56.3281 | 123.2529 | -60.022 | 63.0478 | -0.07576 | 0.0019931 | 0.065704 | 0.073531 | -0.00070713 | -0.0028881 | -0.0039841 | -0.030273 | -0.00012177 | 0.064924 | 0.060184 | -0.0019354 | 0.0038431 | -0.0012071 | 0.082397 | 63.0157 | -60.1639 | 63.0066 | -59.903 | -60.2554 | 0.036621 | 0.041199 | 62.9791 | -60.0449 | 63.0798 | -60.0449 | -60.1501 | -59.935 | -0.14191 | -0.032044 | -0.041199 | 0.11902 | 60.0586 | -0.23346 | 60.2005 | -0.091553 | -0.022888 | -0.068665 | 0.032043 | -0.022888 | 0.086975 | -0.12817 | 0.10986 | -0.10529 | 0.26093 | 123.1705 | 0 | 123.1247 | 123.1796 | 123.024 | 123.0377 | 123.0011 | -123.2117 | -123.0927 | 123.0286 | 123.1018 | 60.1044 | 60.0632
57.3281 | 123.1934 | -60.0082 | 63.0798 | -0.083389 | 0.00092492 | 0.063781 | 0.07289 | 0.0012155 | 0.00095708 | 0.0013565 | 0.00024405 | -0.00076257 | 0.067274 | 0.064029 | -0.0019354 | -2.13e-06 | -0.00056605 | -0.013733 | 63.0157 | -60.1685 | 62.9562 | -59.9258 | -60.2692 | 0.022888 | 0.018311 | 62.9883 | -60.0357 | 63.0157 | -60.0815 | -60.1776 | -59.9716 | -0.16022 | -0.064087 | -0.1236 | 0.082398 | 60.0311 | -0.26093 | 60.1913 | -0.10071 | -0.027466 | -0.091553 | -0.064087 | -0.073242 | 0.036621 | -0.16937 | 0.064087 | -0.14191 | 0.24261 | 123.1247 | -0.045776 | 123.0515 | 123.1842 | 123.024 | 123.024 | 122.9965 | -123.2483 | -123.1155 | 122.9645 | 123.024 | 59.9945 | 60.0266
58.3281 | 123.1705 | -59.9854 | 63.0707 | -0.045242 | -0.00057028 | 0.064209 | 0.073531 | 0.0018565 | -0.0037427 | 0.0017837 | 0.012451 | 0.0013736 | 0.064497 | 0.06232 | -0.0015082 | 0.00085247 | -0.00077965 | -0.022888 | 63.0112 | -60.1547 | 62.9425 | -59.9487 | -60.2921 | 0.004578 | 0.004578 | 62.9974 | -60.054 | 63.0249 | -60.0677 | -60.1685 | -59.9716 | -0.16937 | -0.05951 | -0.12817 | 0.036622 | 59.9899 | -0.3067 | 60.1593 | -0.13733 | -0.068664 | -0.073242 | -0.045777 | -0.082397 | 0.013733 | -0.1831 | 0.082397 | -0.11444 | 0.20599 | 123.0972 | -0.013733 | 123.0789 | 123.1659 | 123.0515 | 122.9965 | 122.9828 | -123.2254 | -123.1247 | 122.9279 | 123.0103 | 59.9625 | 59.9899
59.3281 | 123.23 | -60.0128 | 63.0569 | -0.045242 | 0.0015659 | 0.063354 | 0.072463 | 0.0012155 | -0.0018201 | -0.0018479 | 0.018555 | -0.002258 | 0.067274 | 0.058902 | -0.001081 | 0.00042507 | -0.00077965 | 0.036621 | 63.0157 | -60.1593 | 62.9929 | -59.903 | -60.2509 | 0.022888 | 0.022888 | 62.9974 | -60.0311 | 63.0386 | -60.0632 | -60.1593 | -59.9854 | -0.14648 | -0.041199 | -0.064087 | 0.10986 | 60.0357 | -0.23804 | 60.1822 | -0.091552 | -0.018311 | -0.059509 | -0.018311 | -0.050354 | 0.027465 | -0.14648 | 0.045776 | -0.12817 | 0.25635 | 123.1522 | -0.032043 | 123.0698 | 123.175 | 123.0286 | 123.0286 | 123.0103 | -123.2162 | -123.0881 | 123.0057 | 123.0515 | 60.0494 | 60.0357
60.3281 | 123.2574 | -60.0403 | 63.0295 | -0.060501 | 0.00028412 | 0.065704 | 0.07225 | 0.00036107 | -0.0026745 | -0.0014207 | -0.036377 | 0.00051903 | 0.06407 | 0.061252 | -0.001081 | 0.0027751 | -0.0033433 | 0.027466 | 63.0249 | -60.1593 | 63.0112 | -59.8892 | -60.26 | 0.013733 | 0.045776 | 62.9608 | -60.0449 | 63.0615 | -60.0311 | -60.1547 | -59.9442 | -0.11902 | -0.004578 | -0.018311 | 0.15106 | 60.054 | -0.21973 | 60.173 | -0.10071 | -0.004578 | -0.068665 | 0.032043 | 0.009155 | 0.09613 | -0.11444 | 0.10071 | -0.10986 | 0.27008 | 123.1705 | 0.013733 | 123.1064 | 123.1842 | 123.0057 | 123.0652 | 123.0011 | -123.1888 | -123.0743 | 123.0515 | 123.1018 | 60.0677 | 60.0861
61.3281 | 123.2208 | -60.0037 | 63.0707 | -0.091019 | 0.0011385 | 0.064209 | 0.072036 | 0.0050607 | -0.0013929 | -0.0033433 | -0.0028075 | 9.1834e-05 | 0.065992 | 0.063175 | -0.00022637 | 0.00063867 | -0.00099325 | -0.022888 | 63.0478 | -60.1593 | 62.9608 | -59.935 | -60.2646 | 0.027466 | 0.009155 | 62.9929 | -60.0357 | 63.0203 | -60.0632 | -60.1685 | -59.9808 | -0.15564 | -0.022888 | -0.10986 | 0.068664 | 60.0311 | -0.26093 | 60.1868 | -0.10529 | -0.032044 | -0.07782 | -0.050354 | -0.059509 | 0.022888 | -0.16479 | 0.054932 | -0.13275 | 0.2243 | 123.1201 | -0.027465 | 123.056 | 123.2071 | 123.0286 | 123.0515 | 122.9965 | -123.23 | -123.1064 | 122.9645 | 123.024 | 59.9808 | 60.0128
62.3281 | 123.2666 | -60.022 | 63.0432 | 0.015793 | 0.00071132 | 0.0625 | 0.070968 | 0.0016427 | 0.0015979 | -0.0022751 | -0.02417 | 9.1834e-05 | 0.064924 | 0.064029 | -0.0019354 | 0.00042507 | 0.00071555 | 0.022888 | 63.0341 | -60.1639 | 62.9791 | -59.8984 | -60.2509 | 0.036621 | 0.041199 | 62.9929 | -60.0403 | 63.0569 | -60.0449 | -60.1456 | -59.9258 | -0.14191 | -0.009155 | -0.064087 | 0.1236 | 60.0586 | -0.22888 | 60.2005 | -0.086975 | -0.01831 | -0.050354 | 0.013733 | -0.022888 | 0.096131 | -0.1236 | 0.11444 | -0.10529 | 0.2655 | 123.143 | -0.004578 | 123.0972 | 123.1979 | 123.0331 | 123.056 | 123.0148 | -123.2071 | -123.0835 | 123.0011 | 123.0789 | 60.0449 | 60.0632
63.3281 | 123.1934 | -60.0174 | 63.0524 | -0.029984 | 0.0011385 | 0.065277 | 0.072036 | 0.00036107 | 0.00052988 | -0.0014207 | 0.033813 | 0.00116 | 0.065779 | 0.054843 | -0.0015082 | 0.0032023 | -0.00056605 | -0.004578 | 63.0341 | -60.141 | 62.9654 | -59.9442 | -60.2692 | 0.036621 | 0.018311 | 62.9837 | -60.022 | 63.0066 | -60.0723 | -60.1822 | -59.9808 | -0.1236 | -0.01831 | -0.086975 | 0.073242 | 60.054 | -0.25177 | 60.1776 | -0.12817 | -0.004578 | -0.068664 | -0.045776 | -0.054932 | 0.036621 | -0.16479 | 0.041199 | -0.16022 | 0.19684 | 123.1064 | -0.050354 | 123.0286 | 123.175 | 123.0057 | 123.0515 | 123.0011 | -123.1934 | -123.0743 | 122.9828 | 123.024 | 60.0128 | 60.0357
64.3281 | 123.2574 | -60.0037 | 63.0386 | -0.037613 | 0.00049772 | 0.065277 | 0.070113 | 0.0039927 | 0.0015979 | -0.0027023 | -0.011963 | 0.0018008 | 0.065565 | 0.063602 | -0.0034308 | 0.0021341 | -0.0044113 | 0.004578 | 63.0157 | -60.1639 | 62.9974 | -59.9487 | -60.4156 | -0.009155 | 0.036621 | 62.9791 | -60.0311 | 63.0707 | -60.0586 | -60.1364 | -59.9442 | -0.16022 | -0.022888 | -0.041198 | 0.054932 | 59.9945 | -0.41199 | 60.1547 | -0.25177 | -0.027466 | -0.059509 | 0.032044 | -0.054932 | 0.059509 | -0.13275 | 0.086975 | -0.10529 | 0.21515 | 123.1613 | -0.027466 | 123.1018 | 123.1796 | 123.0103 | 123.0194 | 122.9828 | -123.2025 | -123.0698 | 123.0011 | 123.0743 | 60.0082 | 60.0403
65.3281 | 123.2941 | -59.9899 | 63.0249 | -0.045242 | -0.00035668 | 0.066131 | 0.073959 | 0.0024973 | -0.0016065 | 0.0011429 | 0.024658 | -0.00097617 | 0.063429 | 0.062961 | -0.00279 | 0.00085247 | 7.4746e-05 | 0.064087 | 62.9974 | -60.141 | 63.0432 | -59.8434 | -60.1913 | 0.091553 | 0.10529 | 62.9745 | -60.0082 | 63.1256 | -59.9899 | -60.1273 | -59.9121 | -0.15106 | -0.027465 | 0.018311 | 0.14648 | 60.0815 | -0.20142 | 60.2325 | -0.050354 | -0.018311 | -0.050354 | 0.10071 | 0 | 0.07782 | -0.13733 | 0.096131 | -0.11902 | 0.29755 | 123.1842 | 0.018311 | 123.1338 | 123.1384 | 122.9828 | 122.9874 | 122.9645 | -123.1659 | -123.0331 | 123.0331 | 123.1155 | 60.054 | 60.0952
66.3281 | 123.2117 | -60.0128 | 63.0844 | -0.045242 | 7.0518e-05 | 0.065063 | 0.073531 | 0.0029245 | -0.0028881 | -0.00099327 | -0.018066 | 0.00116 | 0.062361 | 0.067874 | -0.0030036 | -0.00021573 | -0.0012071 | -0.018311 | 63.0203 | -60.1639 | 62.9608 | -59.9487 | -60.2737 | 0.022888 | 0.013733 | 63.002 | -60.0494 | 63.0295 | -60.0815 | -60.1639 | -59.967 | -0.15106 | -0.064087 | -0.1236 | 0.064087 | 60.0357 | -0.26093 | 60.1868 | -0.10986 | -0.036621 | -0.082398 | -0.054932 | -0.068665 | 0.045776 | -0.15106 | 0.082397 | -0.11444 | 0.21515 | 123.1247 | -0.032044 | 123.0789 | 123.1842 | 123.0515 | 123.0331 | 123.0148 | -123.2483 | -123.1338 | 122.9736 | 123.0423 | 59.9945 | 60.0266
67.3438 | 123.1979 | -60.0494 | 63.0203 | -0.052872 | 0.00071132 | 0.065918 | 0.073959 | 0.0031381 | -0.0013929 | 0.0032791 | -0.036377 | 0.0043642 | 0.065992 | 0.060825 | -0.0023626 | 0.00085247 | -0.0046249 | -0.09613 | 62.9883 | -60.2188 | 62.8922 | -60.0449 | -60.3836 | -0.11444 | -0.15564 | 62.97 | -60.0723 | 62.9883 | -60.1456 | -60.2463 | -60.0128 | -0.16937 | -0.032044 | -0.12817 | 0.004577 | 59.935 | -0.33417 | 60.1044 | -0.16479 | -0.022889 | -0.050354 | -0.032044 | -0.096131 | 0.036621 | -0.19684 | 0.05951 | -0.17395 | 0.17395 | 123.111 | -0.073242 | 123.0606 | 123.2071 | 123.0423 | 123.0377 | 123.0194 | -123.2391 | -123.0927 | 122.9416 | 123.0377 | 59.9533 | 59.8938
68.3281 | 123.2758 | -60.0037 | 63.0295 | -0.0070953 | 0.0030613 | 0.064636 | 0.072677 | 0.00057467 | 0.0015979 | -0.0041977 | -0.042481 | -0.00097617 | 0.067701 | 0.05997 | -0.00086737 | 0.00021147 | -0.0024887 | 0.032043 | 63.0112 | -60.1501 | 62.9974 | -59.8938 | -60.2509 | 0.013733 | 0.059509 | 62.9791 | -60.0266 | 63.0753 | -60.0403 | -60.1273 | -59.9396 | -0.14648 | -0.018311 | -0.032043 | 0.10986 | 60.0174 | -0.24719 | 60.1639 | -0.10071 | -0.022888 | -0.050354 | 0.045776 | -0.036621 | 0.064087 | -0.1236 | 0.086975 | -0.10071 | 0.25635 | 123.1476 | -0.013733 | 123.1018 | 123.1613 | 123.0057 | 123.0148 | 122.9828 | -123.1796 | -123.056 | 123.0011 | 123.0789 | 60.0357 | 60.0632
69.3281 | 123.2162 | -59.9945 | 63.0432 | -0.022354 | 0.0022067 | 0.064209 | 0.074599 | 0.00036107 | -0.0016065 | -0.0012071 | -0.0028075 | 0.00073263 | 0.066633 | 0.06467 | -0.0017218 | -0.00064293 | 0.0015701 | -0.022888 | 63.0569 | -60.1547 | 62.9562 | -59.9579 | -60.2737 | 0.018311 | 0 | 62.9974 | -60.0311 | 63.0249 | -60.0815 | -60.1547 | -59.967 | -0.16022 | 0.013733 | -0.086975 | 0.036621 | 60.0128 | -0.27924 | 60.173 | -0.11902 | -0.036621 | -0.045776 | -0.018311 | -0.086975 | 0.027466 | -0.16022 | 0.064087 | -0.1236 | 0.19684 | 123.111 | -0.050354 | 123.056 | 123.2117 | 123.0286 | 123.0515 | 122.9919 | -123.1979 | -123.0743 | 122.9507 | 123.0194 | 59.9716 | 59.9945
70.3281 | 123.2666 | -59.9945 | 63.0112 | -0.06813 | 0.0013523 | 0.06549 | 0.073318 | 0.00078827 | -0.0022473 | -0.00077967 | -0.036377 | 0.00116 | 0.065352 | 0.061679 | -0.002149 | 0.0010661 | 0.00092935 | 0.013733 | 62.9974 | -60.1639 | 63.0066 | -59.8938 | -60.2554 | 0.022888 | 0.054932 | 62.97 | -60.0494 | 63.0661 | -60.0357 | -60.1273 | -59.9304 | -0.16937 | -0.013732 | -0.004577 | 0.10071 | 60.0174 | -0.26093 | 60.1868 | -0.091553 | -0.054931 | -0.041198 | 0.054932 | -0.041199 | 0.064087 | -0.13275 | 0.11902 | -0.07782 | 0.27008 | 123.1705 | 0.013732 | 123.1155 | 123.1613 | 123.0194 | 122.9919 | 122.9645 | -123.175 | -123.0606 | 123.0011 | 123.0606 | 60.0082 | 60.0494
71.3281 | 123.23 | -60.0037 | 63.0478 | -0.029984 | 0.00049772 | 0.063781 | 0.070754 | 0.0014291 | 0.0013843 | -0.00099327 | -0.015015 | 0.00073263 | 0.063643 | 0.05933 | -0.00086737 | -0.00042933 | -0.00013885 | -0.004578 | 63.0432 | -60.1364 | 62.9517 | -59.9396 | -60.2875 | 0.022888 | 0.004578 | 62.9883 | -60.0449 | 63.0432 | -60.0723 | -60.173 | -59.9808 | -0.13275 | -0.004578 | -0.096131 | 0.064087 | 60.0266 | -0.28381 | 60.1593 | -0.15106 | -0.041199 | -0.05951 | -0.004578 | -0.068665 | 0.022888 | -0.16937 | 0.064087 | -0.12817 | 0.19684 | 123.0881 | -0.027466 | 123.0881 | 123.1796 | 123.0331 | 123.0469 | 122.9919 | -123.1842 | -123.0927 | 122.9553 | 123.0469 | 59.9991 | 60.0082
72.3438 | 123.3261 | -60.0311 | 62.9837 | -0.060501 | 0.0019931 | 0.065063 | 0.070541 | -0.0013479 | -0.00032472 | -0.00077967 | -0.021118 | -0.00076257 | 0.062575 | 0.062961 | -0.0012946 | 0.0029887 | 0.00028835 | -0.013733 | 62.9379 | -60.1364 | 63.0249 | -59.8618 | -60.2371 | -0.027466 | -0.027466 | 62.9059 | -60.0494 | 63.1119 | -60.0037 | -60.0861 | -59.8846 | -0.10529 | -0.045777 | 0.041198 | 0.16937 | 60.0037 | -0.20599 | 60.1089 | -0.10071 | -0.01831 | -0.07782 | 0.12817 | 0.027466 | 0.14648 | -0.054932 | 0.16479 | -0.036622 | 0.27466 | 123.1613 | 0.045776 | 123.1613 | 123.0743 | 122.9553 | 122.9691 | 122.937 | -123.1201 | -123.0331 | 123.056 | 123.143 | 60.0174 | 60.0037
73.3281 | 123.2529 | -60.0266 | 63.0478 | -0.07576 | 0.0013523 | 0.064422 | 0.074813 | 0.00014747 | -0.0016065 | -0.00013887 | -0.02417 | 0.002869 | 0.065352 | 0.067874 | -0.001081 | 0.0029887 | -0.00035245 | -0.009155 | 63.0295 | -60.1501 | 62.97 | -59.9533 | -60.2554 | 0.004578 | 0.018311 | 62.9883 | -60.0449 | 63.0478 | -60.0128 | -60.1318 | -59.9304 | -0.1236 | -0.018311 | -0.07782 | 0.073242 | 60.0311 | -0.22888 | 60.1547 | -0.10529 | -0.018311 | -0.05951 | 0 | 0.013733 | 0.09613 | -0.10529 | 0.11444 | -0.086975 | 0.19684 | 123.1201 | 0.032044 | 123.0927 | 123.1796 | 123.0331 | 123.056 | 123.0148 | -123.1979 | -123.0927 | 122.9965 | 123.0743 | 60.0174 | 60.0449
74.3281 | 123.1705 | -60.0357 | 63.0341 | -0.091019 | 0.0019931 | 0.064422 | 0.07225 | -0.00027993 | 0.00031608 | 7.4734e-05 | -0.057739 | 0.00030543 | 0.062788 | 0.064029 | -0.0032172 | 0.0023477 | -0.00099325 | -0.041199 | 62.97 | -60.1913 | 62.9562 | -59.9625 | -60.3607 | -0.091553 | -0.068665 | 62.97 | -60.054 | 63.0157 | -60.1181 | -60.2188 | -59.9945 | -0.15564 | -0.064087 | -0.07782 | 0.073243 | 59.9442 | -0.32501 | 60.0998 | -0.16937 | -0.01831 | -0.064087 | -0.018311 | -0.082397 | 0.041199 | -0.18311 | 0.059509 | -0.1648 | 0.22888 | 123.1476 | -0.064087 | 123.0698 | 123.1613 | 123.024 | 123.0057 | 123.0057 | -123.2254 | -123.0881 | 122.9919 | 123.0515 | 59.9945 | 59.967
75.3281 | 123.2437 | -60.0082 | 63.0478 | -0.022354 | 0.0011385 | 0.065063 | 0.072036 | -0.00092073 | -0.0026745 | -0.00056607 | -0.027222 | 0.00030543 | 0.065138 | 0.061893 | -0.001081 | 0.0019205 | -0.00099325 | 0.004578 | 63.0341 | -60.173 | 62.9608 | -59.935 | -60.2875 | 0.018311 | 0.004578 | 62.9883 | -60.0403 | 63.1027 | -60.0494 | -60.1318 | -59.9167 | -0.16479 | -0.013733 | -0.086976 | 0.073242 | 60.0266 | -0.27924 | 60.1913 | -0.11444 | -0.032043 | -0.05951 | 0.054931 | -0.041198 | 0.091553 | -0.1236 | 0.1236 | -0.091553 | 0.23804 | 123.1338 | -0.009155 | 123.143 | 123.2071 | 123.0286 | 123.0423 | 122.9965 | -123.2208 | -123.0881 | 122.9691 | 123.111 | 60.0128 | 60.0128
76.3281 | 123.2483 | -60.0174 | 63.0432 | -0.06813 | 0.0015659 | 0.063568 | 0.07289 | 0.0024973 | 0.0020251 | 0.0015701 | -0.051636 | 9.1834e-05 | 0.062147 | 0.060184 | -0.00279 | 0.0012797 | 7.4746e-05 | -0.004578 | 62.9883 | -60.1639 | 62.9974 | -59.9075 | -60.26 | 0.004578 | 0.009155 | 62.9517 | -60.0311 | 63.0524 | -60.0632 | -60.1593 | -59.9533 | -0.14648 | -0.054932 | -0.045776 | 0.10986 | 60.022 | -0.24262 | 60.1685 | -0.096131 | -0.013733 | -0.091553 | 0.009155 | -0.045776 | 0.064087 | -0.14191 | 0.07782 | -0.12817 | 0.25635 | 123.1613 | -0.032043 | 123.0835 | 123.1522 | 122.9828 | 123.0057 | 122.9691 | -123.2071 | -123.0743 | 123.0148 | 123.0698 | 60.0128 | 60.0266
77.3438 | 123.3307 | -59.9945 | 62.9837 | -0.11391 | 0.0022067 | 0.064636 | 0.072036 | 0.0022837 | 0.0020251 | 0.0011429 | -0.015015 | -0.00097617 | 0.06407 | 0.068302 | -0.0030036 | 0.0019205 | -0.00077965 | -0.050354 | 62.9425 | -60.1822 | 63.0112 | -59.8709 | -60.2371 | -0.045776 | -0.045776 | 62.8738 | -60.0449 | 63.1027 | -60.0128 | -60.1089 | -59.8801 | -0.18768 | -0.041199 | 0.027465 | 0.1236 | 59.9487 | -0.24262 | 60.1364 | -0.054932 | -0.050354 | -0.10986 | 0.11902 | -0.01831 | 0.11444 | -0.11444 | 0.16479 | -0.064087 | 0.31128 | 123.1934 | 0.032044 | 123.1476 | 123.1247 | 122.9187 | 122.937 | 122.8683 | -123.1659 | -123.0286 | 123.0057 | 123.0972 | 59.9442 | 59.9487
78.3281 | 123.262 | -60.0266 | 63.002 | -0.060501 | 0.0026339 | 0.065704 | 0.071609 | 0.00078827 | 0.0013843 | 0.00028833 | -0.030273 | 0.0020144 | 0.063215 | 0.05933 | -0.0017218 | 0.0021341 | -0.0014207 | -0.004578 | 62.9929 | -60.1593 | 62.9883 | -59.8984 | -60.2554 | -0.009155 | 0.027466 | 62.9837 | -60.0403 | 63.0478 | -60.0494 | -60.1685 | -59.9487 | -0.13275 | -0.009155 | -0.013733 | 0.12817 | 60.0174 | -0.22888 | 60.1501 | -0.09613 | -0.013733 | -0.01831 | 0.045777 | -0.022888 | 0.07782 | -0.14191 | 0.091553 | -0.12817 | 0.26093 | 123.1476 | -0.009155 | 123.0881 | 123.1522 | 123.024 | 123.0194 | 123.0103 | -123.1613 | -123.0423 | 123.0148 | 123.0743 | 60.022 | 60.054
79.3281 | 123.1796 | -60.0357 | 63.0478 | -0.014725 | -0.00014308 | 0.065277 | 0.071395 | -0.00070713 | 0.00031608 | 0.00028833 | -0.0028075 | 0.0020144 | 0.064711 | 0.056125 | -0.001081 | -2.13e-06 | 0.0030655 | -0.009155 | 63.0569 | -60.1318 | 62.9379 | -59.9442 | -60.2737 | 0.018311 | 0.013733 | 63.002 | -60.0449 | 63.0066 | -60.0677 | -60.1685 | -59.967 | -0.09613 | 0.009155 | -0.10986 | 0.091553 | 60.054 | -0.23804 | 60.1501 | -0.14191 | -0.009155 | -0.045777 | -0.041199 | -0.032043 | 0.068665 | -0.13275 | 0.07782 | -0.1236 | 0.18768 | 123.0698 | -0.022888 | 123.0515 | 123.1888 | 123.0469 | 123.0927 | 123.0377 | -123.1796 | -123.0927 | 122.9736 | 123.0423 | 60.0266 | 60.0494
80.3281 | 123.2483 | -60.0266 | 63.0203 | -0.060501 | 0.0015659 | 0.06549 | 0.072677 | 0.0035653 | -0.0026745 | 0.0017837 | -0.048584 | 0.0015872 | 0.062788 | 0.061679 | -0.0047126 | 0.0021341 | -0.0033433 | -0.004578 | 63.0112 | -60.1913 | 63.002 | -59.8984 | -60.2371 | 0.004578 | 0.045776 | 62.9837 | -60.0082 | 63.0753 | -60.0403 | -60.1639 | -59.9258 | -0.16479 | -0.009156 | -0.018311 | 0.12817 | 60.0311 | -0.21057 | 60.1959 | -0.045777 | 0.01831 | -0.036621 | 0.054931 | -0.013733 | 0.10071 | -0.13733 | 0.082398 | -0.15564 | 0.29297 | 123.1934 | -0.032043 | 123.0835 | 123.2025 | 122.9919 | 123.0377 | 123.0103 | -123.2117 | -123.0286 | 123.0286 | 123.1018 | 60.022 | 60.0723
81.3281 | 123.2346 | -60.0037 | 63.0295 | -0.12917 | 0.0019931 | 0.064209 | 0.073104 | 0.00057467 | 0.00031608 | 0.00028833 | -0.030273 | 0.0013736 | 0.063856 | 0.066593 | -0.0017218 | 0.00042507 | -0.0012071 | 0.045776 | 63.0386 | -60.1547 | 62.9883 | -59.903 | -60.26 | 0.013733 | 0.041199 | 62.9929 | -60.0311 | 63.0707 | -60.0357 | -60.1456 | -59.9442 | -0.15106 | 0.009155 | -0.041199 | 0.10071 | 60.0174 | -0.25635 | 60.1685 | -0.10529 | -0.027466 | -0.036621 | 0.041199 | -0.032044 | 0.059509 | -0.14191 | 0.086975 | -0.11444 | 0.25177 | 123.143 | -0.004578 | 123.1018 | 123.1934 | 123.024 | 123.0423 | 122.9965 | -123.1842 | -123.0606 | 122.9919 | 123.0743 | 60.0494 | 60.0449
82.3438 | 123.3124 | -59.9991 | 62.9654 | -0.1368 | 0.00071132 | 0.063995 | 0.072036 | -0.0026297 | -0.00011112 | -0.0027023 | 0.012451 | 0.00073263 | 0.063643 | 0.064456 | -0.0030036 | 0.0027751 | -0.00013885 | -0.041199 | 62.9288 | -60.1639 | 63.0295 | -59.8663 | -60.2509 | -0.045776 | -0.027466 | 62.8967 | -60.0449 | 63.0981 | -59.9854 | -60.0952 | -59.8892 | -0.16479 | -0.036621 | 0.064087 | 0.13275 | 59.9533 | -0.25177 | 60.1181 | -0.086975 | -0.045777 | -0.068664 | 0.13275 | 0.013732 | 0.10986 | -0.096131 | 0.15564 | -0.050354 | 0.29755 | 123.1934 | 0.059509 | 123.143 | 123.0927 | 122.9416 | 122.9279 | 122.8958 | -123.1293 | -123.0103 | 123.0286 | 123.0972 | 59.9579 | 59.9716
83.3281 | 123.2529 | -60.0174 | 63.0112 | -0.07576 | 0.0013523 | 0.064636 | 0.07225 | 0.0033517 | -0.00053832 | -0.00077967 | -0.039429 | 0.00094643 | 0.065138 | 0.065311 | -0.0012946 | 0.00085247 | 0.00092935 | 0.16022 | 62.9929 | -60.173 | 63.0524 | -59.9304 | -60.2417 | 0.036621 | 0.022888 | 62.9974 | -60.0357 | 63.0615 | -60.0266 | -60.1639 | -59.9442 | -0.15564 | -0.01831 | 0.041199 | 0.086975 | 60.054 | -0.2243 | 60.2097 | -0.068664 | -0.018311 | -0.013732 | 0.050354 | -0.009155 | 0.073242 | -0.14648 | 0.091553 | -0.12817 | 0.24262 | 123.2254 | 0.009156 | 123.0972 | 123.1659 | 123.0331 | 123.0103 | 123.0148 | -123.1842 | -123.0469 | 123.0698 | 123.0789 | 60.1776 | 60.0403
84.3281 | 123.23 | -60.0174 | 63.0249 | -0.07576 | 0.0028475 | 0.064636 | 0.071395 | 0.0014291 | -0.00011112 | 0.00028833 | -0.048584 | 0.00051903 | 0.063643 | 0.067874 | -0.002149 | 0.0019205 | 0.00092935 | 0.004578 | 63.0066 | -60.1639 | 63.002 | -59.9121 | -60.2509 | 0.009155 | 0.004578 | 62.9608 | -60.0128 | 63.0386 | -60.0677 | -60.173 | -59.9396 | -0.14648 | -0.01831 | -0.022888 | 0.10529 | 60.0266 | -0.23346 | 60.173 | -0.086975 | 0.004578 | -0.064087 | 0.013733 | -0.050354 | 0.07782 | -0.15564 | 0.073242 | -0.16022 | 0.25177 | 123.1659 | -0.054932 | 123.0515 | 123.1705 | 122.9736 | 123.024 | 122.9782 | -123.1888 | -123.0377 | 123.0194 | 123.056 | 60.022 | 60.022
85.3281 | 123.1979 | -60.0174 | 63.0524 | -0.022354 | -0.00078408 | 0.062927 | 0.070541 | -0.0013479 | -0.00053832 | -0.0020615 | 0.0093995 | 0.00030543 | 0.065779 | 0.060184 | -0.0030036 | 0.0021341 | -0.00056605 | -0.022888 | 63.0341 | -60.1593 | 62.9517 | -59.9304 | -60.2829 | 0.022888 | 0.009155 | 62.9929 | -60.0403 | 63.0112 | -60.0632 | -60.173 | -59.967 | -0.14191 | -0.01831 | -0.10071 | 0.086975 | 60.0403 | -0.2655 | 60.1822 | -0.1236 | -0.022888 | -0.059509 | -0.041199 | -0.045776 | 0.050354 | -0.15564 | 0.073242 | -0.13275 | 0.22888 | 123.111 | -0.022888 | 123.0515 | 123.1934 | 123.0331 | 123.0515 | 123.0103 | -123.2117 | -123.0927 | 122.9691 | 123.0286 | 59.9945 | 60.0266
86.3281 | 123.2346 | -59.9808 | 63.0341 | -0.060501 | -0.00035668 | 0.064209 | 0.073318 | -0.00049353 | -0.00075192 | -0.0016343 | -0.039429 | 0.0024416 | 0.068129 | 0.066806 | -0.0017218 | 0.0034159 | -0.0052659 | 0.009155 | 63.002 | -60.1822 | 62.9837 | -59.903 | -60.2509 | 0.032043 | 0.054932 | 62.9837 | -60.0403 | 63.0569 | -60.0357 | -60.141 | -59.935 | -0.20142 | -0.032044 | -0.050354 | 0.07782 | 60.0128 | -0.27008 | 60.2142 | -0.068664 | -0.059509 | -0.050354 | 0.022888 | -0.054932 | 0.045776 | -0.16022 | 0.10529 | -0.10071 | 0.27924 | 123.1659 | 0.004577 | 123.0972 | 123.1842 | 123.024 | 122.9828 | 122.9645 | -123.2162 | -123.0743 | 122.9645 | 123.0377 | 59.9899 | 60.0357
87.3438 | 123.2117 | -60.0449 | 63.0249 | -0.052872 | 0.0017795 | 0.063568 | 0.072677 | 0.00078827 | -0.00075192 | 7.4734e-05 | -0.060791 | 0.0018008 | 0.065565 | 0.06467 | -0.00086737 | 0.0017069 | 0.0011429 | -0.10071 | 62.9883 | -60.1822 | 62.9059 | -60.0174 | -60.3653 | -0.12817 | -0.16022 | 62.9608 | -60.0815 | 63.002 | -60.141 | -60.2417 | -60.0037 | -0.13733 | -0.036621 | -0.11902 | 0.027466 | 59.9167 | -0.32043 | 60.054 | -0.18311 | -0.036621 | -0.064087 | -0.022888 | -0.09613 | 0.041199 | -0.19684 | 0.07782 | -0.16022 | 0.16479 | 123.0881 | -0.059509 | 123.0835 | 123.1705 | 123.0423 | 123.0331 | 123.0057 | -123.2071 | -123.1064 | 122.9507 | 123.0469 | 59.9442 | 59.8846
88.3281 | 123.2254 | -60.0449 | 63.0249 | -0.06813 | 0.0011385 | 0.065277 | 0.073104 | 0.0027109 | -0.00075192 | -0.00013887 | -0.079102 | 0.00116 | 0.065565 | 0.064243 | -0.0032172 | 0.0019205 | -0.0012071 | -0.050354 | 62.9791 | -60.1822 | 62.8235 | -60.3653 | -60.1593 | 0.091553 | -0.009155 | 62.9929 | -60.0311 | 62.9929 | -60.1135 | -60.2142 | -59.9991 | -0.13733 | -0.045776 | -0.20142 | -0.32043 | 60.1364 | -0.11444 | 60.2737 | 0.022888 | 0.013733 | -0.032043 | -0.032043 | -0.068664 | 0.045777 | -0.16937 | 0.032044 | -0.1831 | -0.18311 | 123.0057 | -0.082397 | 123.024 | 123.1613 | 123.024 | 123.024 | 123.0377 | -123.2071 | -123.056 | 122.8683 | 123.0377 | 59.9945 | 60.0357
89.3281 | 123.262 | -60.0082 | 63.0432 | -0.029984 | 0.00092492 | 0.061432 | 0.073531 | -0.0030569 | -0.0018201 | -0.0027023 | -0.021118 | 0.00094643 | 0.065138 | 0.057407 | -0.00279 | 0.00042507 | 0.00050195 | 0 | 63.0341 | -60.1547 | 62.9562 | -59.935 | -60.2692 | 0.027466 | 0 | 62.9837 | -60.0311 | 63.0569 | -60.0357 | -60.1456 | -59.9442 | -0.14648 | -0.009155 | -0.086975 | 0.073242 | 60.0357 | -0.26093 | 60.1822 | -0.11444 | -0.022888 | -0.059509 | 0.013733 | -0.027466 | 0.064087 | -0.13733 | 0.086975 | -0.11444 | 0.21973 | 123.111 | -0.004578 | 123.0881 | 123.1888 | 123.0148 | 123.0423 | 122.9919 | -123.1979 | -123.0743 | 122.9645 | 123.0652 | 60.0082 | 60.0082
90.3281 | 123.1888 | -60.0449 | 62.9883 | -0.083389 | 0.0017795 | 0.063568 | 0.073745 | 0.0016427 | -0.00075192 | 0.00092933 | -0.069946 | 0.00094643 | 0.064711 | 0.063388 | -0.00043997 | 0.0038431 | -0.00035245 | -0.073242 | 62.9929 | -60.2051 | 62.5488 | -60.3104 | -59.9442 | -0.045776 | -0.09613 | 63.0066 | -60.054 | 62.9929 | -60.1364 | -60.228 | -60.0128 | -0.16022 | 0.004578 | -0.43945 | -0.2655 | 59.9991 | 0.10071 | 60.1593 | 0.26093 | -0.009155 | 0.018311 | 0.004578 | -0.091553 | 0.032044 | -0.18311 | 0.041199 | -0.17395 | -0.10529 | 122.7539 | -0.082398 | 123.0469 | 123.1979 | 123.0606 | 123.0377 | 123.0515 | -123.1934 | -123.0423 | 122.5937 | 123.0377 | 59.9716 | 59.9487
91.3281 | 123.23 | -59.9945 | 63.0478 | -0.052872 | 0.0019931 | 0.063568 | 0.073745 | -0.0022025 | 0.00095708 | -0.0016343 | -0.0058593 | 0.00116 | 0.065138 | 0.057407 | -0.0019354 | 0.0032023 | 0.0015701 | 0 | 63.0295 | -60.1547 | 62.9425 | -59.9487 | -60.2646 | 0.022888 | -0.009155 | 62.9791 | -60.054 | 63.0249 | -60.0632 | -60.1639 | -59.9716 | -0.16022 | -0.018311 | -0.10529 | 0.045777 | 60.0174 | -0.27008 | 60.1776 | -0.10986 | -0.059509 | -0.068665 | -0.022889 | -0.068664 | 0.022888 | -0.16937 | 0.082397 | -0.10986 | 0.20599 | 123.0972 | -0.009155 | 123.0789 | 123.1842 | 123.0331 | 123.024 | 122.9736 | -123.2025 | -123.1018 | 122.937 | 123.0194 | 59.9945 | 59.9854
92.3281 | 123.2254 | -59.9991 | 63.0203 | -0.052872 | -0.0012113 | 0.064636 | 0.072036 | 0.0035653 | -0.00053832 | -0.0037705 | 0.030762 | 0.0015872 | 0.063856 | 0.063816 | -0.0032172 | 0.00085247 | -0.0012071 | 0.032043 | 62.9837 | -60.1685 | 62.9883 | -59.8984 | -60.2829 | -0.10071 | 0.009155 | 62.9791 | -60.022 | 63.0844 | -60.0266 | -60.173 | -59.9121 | -0.16937 | -0.036621 | -0.032044 | 0.10071 | 59.8984 | -0.28381 | 60.0677 | -0.11444 | -0.022889 | -0.041199 | 0.064087 | -0.027466 | 0.086975 | -0.17395 | 0.10986 | -0.15106 | 0.27008 | 123.1567 | -0.004577 | 123.1064 | 123.1522 | 123.0011 | 122.9828 | 122.9782 | -123.1888 | -123.0423 | 122.9874 | 123.0835 | 60.0311 | 60.0082
93.3281 | 123.2071 | -59.9854 | 63.0386 | -0.10628 | 0.0032749 | 0.062713 | 0.071395 | 0.00078827 | 0.00031608 | 0.00071573 | 0.02771 | 0.0018008 | 0.06407 | 0.06467 | -0.00043997 | 0.0014933 | 0.0019973 | 0.027466 | 63.0066 | -60.1456 | 63.0066 | -59.8984 | -60.2142 | 0.064087 | 0.054932 | 62.9929 | -60.0174 | 63.0295 | -60.0586 | -60.141 | -59.9533 | -0.16022 | -0.032043 | -0.032043 | 0.086976 | 60.0494 | -0.22888 | 60.2097 | -0.068664 | -0.032043 | -0.045776 | -0.009155 | -0.073242 | 0.032044 | -0.15564 | 0.064087 | -0.1236 | 0.24719 | 123.1522 | -0.041199 | 123.0469 | 123.1522 | 123.0103 | 122.9919 | 122.9782 | -123.1842 | -123.056 | 122.9919 | 123.0148 | 60.0128 | 60.0403
94.3281 | 123.2529 | -60.0174 | 63.0295 | -0.083389 | -0.0012113 | 0.064209 | 0.07524 | 0.0010019 | -0.0011791 | 7.4734e-05 | -0.036377 | 0.00094643 | 0.063643 | 0.058689 | -0.0025764 | 0.0023477 | 0.00092935 | 0.022888 | 63.0478 | -60.1685 | 62.9837 | -59.903 | -60.2417 | 0.009155 | 0.036621 | 62.9654 | -60.0494 | 63.0432 | -60.0174 | -60.1318 | -59.9304 | -0.15106 | 0.018311 | -0.045776 | 0.11444 | 60.0266 | -0.2243 | 60.1776 | -0.073242 | -0.032043 | -0.064087 | 0.013733 | 0 | 0.086975 | -0.11444 | 0.11902 | -0.082398 | 0.2655 | 123.1522 | 0.032043 | 123.0927 | 123.2162 | 123.0148 | 123.0652 | 122.9828 | -123.1979 | -123.0789 | 123.0011 | 123.0606 | 60.0403 | 60.054
95.3281 | 123.1979 | -60.0037 | 63.0386 | -0.11391 | -0.0012113 | 0.062072 | 0.07289 | -0.0041251 | -0.0011791 | -0.0018479 | -0.0089111 | 0.0037234 | 0.065992 | 0.058048 | -0.0036444 | 0.0023477 | -0.0018479 | -0.022888 | 63.0203 | -60.1593 | 62.9425 | -59.9396 | -60.2783 | 0.022888 | 0.004578 | 62.9883 | -60.0403 | 63.0295 | -60.0632 | -60.1501 | -59.9487 | -0.15564 | -0.01831 | -0.09613 | 0.064087 | 60.0266 | -0.27466 | 60.1822 | -0.11902 | -0.036621 | -0.050354 | -0.009155 | -0.059509 | 0.054932 | -0.14648 | 0.091553 | -0.10986 | 0.21973 | 123.1018 | -0.022888 | 123.0698 | 123.1796 | 123.0286 | 123.024 | 122.9919 | -123.1979 | -123.0789 | 122.9462 | 123.0331 | 59.9808 | 60.0082
96.3281 | 123.2346 | -60.022 | 63.0569 | -0.029984 | 0.0026339 | 0.066772 | 0.071181 | -0.0013479 | -0.00096552 | 0.0022109 | -0.054688 | 0.0015872 | 0.06642 | 0.061038 | -0.0015082 | 0.0032023 | -0.0012071 | 0.018311 | 62.9791 | -60.1822 | 63.0066 | -59.9121 | -60.2463 | 0.009155 | 0.045776 | 62.9837 | -60.022 | 63.1668 | -60.1868 | -60.2051 | -59.9075 | -0.16022 | -0.07782 | -0.050354 | 0.10986 | 60.0311 | -0.2243 | 60.1913 | -0.064087 | 0 | -0.073242 | 0.10986 | -0.16479 | 0.11444 | -0.1831 | 0.11444 | -0.1831 | 0.27008 | 123.1888 | -0.16479 | 123.1888 | 123.1613 | 123.0057 | 123.0011 | 123.0057 | -123.2391 | -123.0789 | 123.0286 | 123.1888 | 60.0403 | 60.0677
97.3281 | 123.1979 | -60.0082 | 63.0569 | -0.091019 | 0.00092492 | 0.063354 | 0.072463 | -0.00070713 | -0.0020337 | -0.00099327 | -0.021118 | 0.0024416 | 0.062788 | 0.065525 | -0.0017218 | 0.0025613 | 0.0032791 | -0.004578 | 63.0478 | -60.1639 | 62.8601 | -60.0769 | -60.3149 | 0.022888 | 0.004578 | 62.9883 | -60.0586 | 63.0066 | -60.0906 | -60.1593 | -59.9533 | -0.15564 | -0.009155 | -0.19684 | -0.068664 | 60.0311 | -0.3067 | 60.1868 | -0.15106 | -0.050354 | -0.068665 | -0.050354 | -0.082397 | 0.054932 | -0.15106 | 0.10529 | -0.10071 | 0.086975 | 123.024 | -0.032043 | 123.0652 | 123.2117 | 123.0469 | 123.056 | 122.9965 | -123.2208 | -123.1155 | 122.8683 | 123.0148 | 60.0037 | 60.0128
98.3281 | 123.2483 | -59.9991 | 63.0203 | -0.052872 | 0.0013523 | 0.06549 | 0.072677 | 0.0037791 | -0.0018201 | 0.0017837 | -0.033325 | 0.00051903 | 0.065779 | 0.059543 | -0.0019354 | 0.0029887 | -0.0012071 | 0.018311 | 63.0386 | -60.1593 | 62.9837 | -59.9167 | -60.2554 | 0.032043 | 0.050354 | 62.9745 | -60.0266 | 63.0524 | -60.0311 | -60.1318 | -59.9258 | -0.16022 | 0.01831 | -0.036621 | 0.082397 | 60.0311 | -0.25635 | 60.1913 | -0.09613 | -0.027466 | -0.045777 | 0.032043 | -0.032044 | 0.073242 | -0.13275 | 0.10071 | -0.10529 | 0.24261 | 123.143 | -0.004578 | 123.0789 | 123.1979 | 123.0011 | 123.0377 | 122.9736 | -123.1796 | -123.0469 | 122.9828 | 123.0515 | 60.0174 | 60.0494
99.3281 | 123.2391 | -60.0037 | 63.0295 | -0.037613 | 0.0013523 | 0.063568 | 0.072036 | 0.00078827 | -0.0013929 | 0.0011429 | 0.024658 | 9.1834e-05 | 0.064283 | 0.061893 | -0.0034308 | 0.00063867 | -0.0022751 | 0.064087 | 63.002 | -60.1227 | 63.0432 | -59.8434 | -60.1868 | 0.07782 | 0.10071 | 62.9608 | -60.0174 | 63.0707 | -60.0128 | -60.1135 | -59.9258 | -0.11902 | -0.027466 | 0.013733 | 0.16022 | 60.0815 | -0.18311 | 60.2005 | -0.064087 | -0.013733 | -0.068665 | 0.041199 | -0.009155 | 0.07782 | -0.10986 | 0.091553 | -0.09613 | 0.27924 | 123.1659 | 0.004578 | 123.0881 | 123.1247 | 122.9782 | 123.0057 | 122.9645 | -123.1522 | -123.0469 | 123.0469 | 123.0743 | 60.0677 | 60.1044
100.3281 | 123.2483 | -60.022 | 63.0569 | -0.12154 | 0.00028412 | 0.063568 | 0.07289 | 0.0014291 | -0.0016065 | 0.0011429 | -0.0089111 | 0.00073263 | 0.063429 | 0.064029 | -0.003858 | -0.0012839 | -0.0012071 | -0.013733 | 63.0157 | -60.1547 | 62.9379 | -59.9396 | -60.2829 | 0.004578 | -0.009155 | 62.9837 | -60.0357 | 63.0249 | -60.0723 | -60.173 | -59.9808 | -0.13275 | -0.041199 | -0.11902 | 0.082398 | 60.0266 | -0.26093 | 60.1593 | -0.12817 | -0.013733 | -0.073242 | -0.032044 | -0.050354 | 0.041199 | -0.15106 | 0.054932 | -0.13733 | 0.21515 | 123.0927 | -0.036621 | 123.0606 | 123.1705 | 123.0194 | 123.0377 | 123.0057 | -123.2117 | -123.0927 | 122.9599 | 123.0469 | 60.0082 | 60.0128
101.3281 | 123.2346 | -60.0311 | 63.0707 | -0.045242 | 0.0024203 | 0.063141 | 0.074172 | 0.00014747 | -0.0020337 | -0.0029159 | -0.0058593 | 0.0015872 | 0.065138 | 0.06232 | -0.0017218 | 0.0025613 | 0.0013565 | -0.013733 | 63.0295 | -60.1456 | 62.97 | -59.9762 | -60.3012 | 0 | 0.027466 | 63.0112 | -60.0311 | 63.0157 | -60.0723 | -60.1685 | -59.9625 | -0.11444 | -0.041199 | -0.10071 | 0.054932 | 60.0311 | -0.27008 | 60.1456 | -0.15564 | 0 | -0.05951 | -0.054932 | -0.041199 | 0.068665 | -0.13733 | 0.068665 | -0.13733 | 0.16937 | 123.1155 | -0.041199 | 123.0469 | 123.175 | 123.0423 | 123.0606 | 123.0423 | -123.2162 | -123.1018 | 123.0011 | 123.0469 | 60.0174 | 60.0586
102.3281 | 123.2346 | -59.9991 | 63.0386 | 0.00053424 | 0.0011385 | 0.065704 | 0.074813 | 0.0033517 | 0.00010248 | -0.00035247 | -0.030273 | 0.0032962 | 0.065565 | 0.059116 | -0.0030036 | 0.0021341 | -0.0018479 | 0.032043 | 63.0249 | -60.1593 | 62.9837 | -59.8984 | -60.2325 | 0.045776 | 0.054932 | 62.9974 | -60.0311 | 63.0569 | -60.0403 | -60.1456 | -59.9258 | -0.16022 | -0.013733 | -0.054931 | 0.10071 | 60.0449 | -0.23346 | 60.2051 | -0.073242 | -0.032044 | -0.041198 | 0.018311 | -0.041199 | 0.073242 | -0.14648 | 0.10529 | -0.11444 | 0.26093 | 123.143 | -0.009155 | 123.0881 | 123.1842 | 123.0286 | 123.024 | 122.9965 | -123.1979 | -123.0698 | 122.9828 | 123.056 | 60.0311 | 60.054
103.3281 | 123.1979 | -60.0266 | 63.0112 | -0.037613 | 0.0017795 | 0.066131 | 0.073745 | 0.00078827 | 0.00074348 | -0.0022751 | 0.0032959 | 0.00116 | 0.062361 | 0.057834 | -0.00022637 | 0.0012797 | 0.0017837 | -0.022888 | 63.0432 | -60.141 | 62.9517 | -59.935 | -60.2783 | 0.018311 | 0.022888 | 62.9929 | -60.0311 | 63.0295 | -60.1089 | -60.1501 | -59.9258 | -0.11444 | 0.032044 | -0.059509 | 0.091552 | 60.0449 | -0.25177 | 60.1593 | -0.13733 | -0.004578 | -0.01831 | 0.018311 | -0.082398 | 0.10071 | -0.1236 | 0.10529 | -0.11902 | 0.20599 | 123.0927 | -0.07782 | 123.0606 | 123.1842 | 123.024 | 123.0698 | 123.0194 | -123.1522 | -123.0423 | 122.9782 | 123.056 | 60.0037 | 60.0494
104.3281 | 123.2162 | -60.0082 | 63.0203 | -0.045242 | 0.0028475 | 0.065277 | 0.071609 | -0.00027993 | -0.00075192 | 0.00071573 | -0.051636 | 9.1834e-05 | 0.065565 | 0.061679 | -0.00279 | 0.0023477 | -0.0039841 | 0.018311 | 63.0066 | -60.1776 | 62.9929 | -59.8938 | -60.26 | 0.009155 | 0.032043 | 62.9791 | -60.0449 | 63.0615 | -59.9899 | -60.1273 | -59.8801 | -0.16937 | -0.013733 | -0.027466 | 0.11444 | 60.0174 | -0.25177 | 60.1868 | -0.082398 | -0.036621 | -0.041199 | 0.041198 | 0.018311 | 0.12817 | -0.11902 | 0.16479 | -0.082397 | 0.28381 | 123.1705 | 0.054932 | 123.1064 | 123.1842 | 123.024 | 123.0148 | 122.9874 | -123.1979 | -123.0652 | 123.0011 | 123.0698 | 60.0266 | 60.0403
105.3281 | 123.1888 | -60.0174 | 63.0432 | -0.029984 | 0.0019931 | 0.06485 | 0.073318 | -6.6126e-05 | 0.0020251 | -0.00077967 | 0.024658 | 0.0020144 | 0.066206 | 0.062961 | -0.0036444 | 0.00085247 | 0.00092935 | 0.018311 | 63.0157 | -60.1364 | 62.9654 | -59.8846 | -60.2463 | 0.027466 | 0.027466 | 62.9745 | -60.0266 | 63.0203 | -60.0677 | -60.1501 | -59.9716 | -0.11902 | -0.027466 | -0.07782 | 0.13275 | 60.0449 | -0.22888 | 60.1639 | -0.10986 | -0.009155 | -0.068665 | -0.022888 | -0.050354 | 0.045776 | -0.13275 | 0.054931 | -0.1236 | 0.25177 | 123.1018 | -0.041199 | 123.0469 | 123.1522 | 123.0011 | 123.0331 | 122.9919 | -123.1796 | -123.0698 | 122.9828 | 123.0377 | 60.0357 | 60.0449
106.3281 | 123.2254 | -60.0082 | 63.0432 | -0.029984 | -0.00078408 | 0.063354 | 0.073318 | -0.0011343 | -0.0026745 | 0.00050193 | -0.0028075 | 9.1834e-05 | 0.063856 | 0.06232 | -0.0032172 | 0.00021147 | -0.0024887 | 0 | 63.0661 | -60.1501 | 62.9013 | -59.9579 | -60.2646 | 0.013733 | 0.013733 | 63.002 | -60.022 | 63.0157 | -60.0723 | -60.1868 | -59.9762 | -0.14191 | 0.022888 | -0.14191 | 0.050354 | 60.022 | -0.25635 | 60.1639 | -0.11444 | -0.013733 | -0.041199 | -0.027466 | -0.064087 | 0.032044 | -0.17853 | 0.045777 | -0.16479 | 0.19226 | 123.0515 | -0.050354 | 123.0377 | 123.2162 | 123.024 | 123.0743 | 123.0103 | -123.1934 | -123.0652 | 122.9095 | 123.024 | 60.0082 | 60.022
107.3281 | 123.2941 | -59.9991 | 63.0203 | -0.10628 | -0.00014308 | 0.065063 | 0.071609 | 0.00057467 | -0.00096552 | -0.0024887 | 0.030762 | 0.00094643 | 0.06407 | 0.058689 | -0.001081 | -0.00064293 | 0.0011429 | 0.045776 | 62.9929 | -60.1273 | 63.0615 | -59.7977 | -60.1547 | 0.10529 | 0.14191 | 62.9654 | -60.0082 | 63.1119 | -59.967 | -60.0586 | -59.8755 | -0.12817 | -0.027466 | 0.041198 | 0.20142 | 60.1044 | -0.15564 | 60.2325 | -0.027466 | -0.009156 | -0.054932 | 0.091552 | 0.032043 | 0.1236 | -0.05951 | 0.13275 | -0.050354 | 0.32959 | 123.1888 | 0.041199 | 123.1201 | 123.1201 | 122.9736 | 122.9919 | 122.9645 | -123.1476 | -123.0286 | 123.0606 | 123.111 | 60.0449 | 60.141
108.3281 | 123.262 | -59.9808 | 63.0569 | -0.045242 | 0.0026339 | 0.064636 | 0.072463 | -0.0019889 | -0.0031017 | 0.0030655 | -0.054688 | 0.0018008 | 0.063215 | 0.062747 | -0.0023626 | 0.0023477 | 0.00092935 | 0.004578 | 63.0249 | -60.1639 | 62.9974 | -59.9167 | -60.2417 | 0.027466 | 0.050354 | 62.9837 | -60.0311 | 63.0661 | -60.0266 | -60.1364 | -59.9396 | -0.18311 | -0.032044 | -0.059509 | 0.064087 | 60.0082 | -0.26093 | 60.1913 | -0.07782 | -0.050354 | -0.073242 | 0.009155 | -0.045776 | 0.041199 | -0.15564 | 0.091553 | -0.10529 | 0.24719 | 123.1613 | 0.004578 | 123.0972 | 123.1888 | 123.0148 | 123.0057 | 122.9645 | -123.2208 | -123.0881 | 122.9782 | 123.0469 | 59.9854 | 60.0311
109.3281 | 123.1934 | -60.0037 | 63.0478 | -0.0070953 | 0.00028412 | 0.063568 | 0.07225 | 0.0010019 | 0.00052988 | -0.00013887 | 0.0032959 | 0.0026552 | 0.065992 | 0.06467 | -0.0023626 | -0.00021573 | 0.00028835 | -0.009155 | 63.0341 | -60.1456 | 62.9654 | -59.935 | -60.2646 | 0.027466 | 0.018311 | 63.0341 | -60.0037 | 63.0157 | -60.1044 | -60.1181 | -59.935 | -0.14191 | -0.013733 | -0.082398 | 0.068664 | 60.0311 | -0.26093 | 60.173 | -0.11902 | 0 | -0.013733 | -0.032044 | -0.10071 | 0.068664 | -0.11444 | 0.068664 | -0.11444 | 0.21057 | 123.111 | -0.10071 | 123.0194 | 123.1796 | 123.0377 | 123.0377 | 123.0377 | -123.1934 | -123.0515 | 122.9691 | 123.0194 | 59.9945 | 60.022
110.3281 | 123.2162 | -60.0174 | 63.0341 | -0.014725 | 0.0015659 | 0.062927 | 0.07289 | 0.0010019 | -0.0011791 | 0.0024245 | -0.015015 | 0.0015872 | 0.06407 | 0.058689 | -0.0042854 | 0.0021341 | 0.00092935 | 0.009155 | 63.0249 | -60.1685 | 62.9974 | -59.935 | -60.2509 | 0.009155 | 0.027466 | 62.9974 | -60.0449 | 63.0753 | -60.0357 | -60.1273 | -59.9304 | -0.15106 | -0.009156 | -0.036621 | 0.082397 | 60.0266 | -0.23346 | 60.1776 | -0.082397 | -0.027466 | -0.036621 | 0.041198 | -0.018311 | 0.086975 | -0.10986 | 0.11444 | -0.082397 | 0.23346 | 123.1659 | 0.009155 | 123.1201 | 123.1934 | 123.0423 | 123.0423 | 123.0148 | -123.2025 | -123.0789 | 123.0148 | 123.0927 | 60.0266 | 60.0449
111.3281 | 123.1888 | -60.0403 | 63.0295 | -0.07576 | 0.0013523 | 0.06485 | 0.07289 | -0.0015615 | -0.00053832 | -0.00035247 | 0.0063477 | 0.002228 | 0.062361 | 0.057407 | -0.0019354 | 0.0019205 | 7.4746e-05 | 0.004578 | 63.0157 | -60.1456 | 62.9608 | -59.9121 | -60.2692 | 0.036621 | 0.027466 | 62.9883 | -60.0403 | 63.1531 | -60.0037 | -60.434 | -60.1227 | -0.10529 | -0.013733 | -0.068665 | 0.12817 | 60.0769 | -0.22888 | 60.1822 | -0.1236 | 0 | -0.041199 | 0.1236 | 0.036621 | -0.082398 | -0.39368 | -0.082398 | -0.39368 | 0.23346 | 123.1064 | 0.036621 | 123.1934 | 123.1613 | 123.0286 | 123.056 | 123.0286 | -123.175 | -123.0698 | 123.0011 | 123.1934 | 60.0449 | 60.0677
112.3281 | 123.2574 | -60.0037 | 63.0157 | -0.06813 | 0.0034885 | 0.062286 | 0.072677 | 0.00078827 | -0.0020337 | -0.00077967 | -0.085205 | 0.00094643 | 0.063856 | 0.061038 | -0.0025764 | 0.0017069 | 0.0013565 | 0.013733 | 63.0341 | -60.1639 | 62.9883 | -59.8938 | -60.2509 | 0.013733 | 0.045776 | 62.9837 | -60.0266 | 63.0753 | -59.9899 | -60.0998 | -59.8846 | -0.16022 | 0.018311 | -0.027466 | 0.10986 | 60.0174 | -0.24719 | 60.1776 | -0.086975 | -0.022888 | -0.032043 | 0.059509 | 0.013733 | 0.11902 | -0.09613 | 0.14191 | -0.073242 | 0.27008 | 123.1522 | 0.036621 | 123.1018 | 123.1979 | 123.0103 | 123.0377 | 122.9874 | -123.1796 | -123.0423 | 122.9919 | 123.0789 | 60.0174 | 60.0494
113.3281 | 123.2758 | -60.0037 | 63.0432 | -0.029984 | 0.0013523 | 0.06485 | 0.072463 | -0.0013479 | 0.0011707 | 0.0015701 | 0.0093995 | -0.00076257 | 0.064283 | 0.061893 | -0.0030036 | -2.13e-06 | -0.0029159 | 0.054932 | 62.9745 | -60.1273 | 63.0478 | -59.8206 | -60.1639 | 0.10071 | 0.13733 | 62.9471 | -60.0037 | 63.1073 | -59.9716 | -60.054 | -59.8755 | -0.1236 | -0.068665 | 0.004578 | 0.1831 | 60.1044 | -0.16022 | 60.228 | -0.036621 | 0 | -0.09613 | 0.064087 | 0.032043 | 0.12817 | -0.050354 | 0.12817 | -0.050354 | 0.3067 | 123.175 | 0.032043 | 123.111 | 123.1018 | 122.9507 | 122.9782 | 122.9507 | -123.1705 | -123.0469 | 123.0515 | 123.111 | 60.0586 | 60.141
114.3281 | 123.2117 | -60.0037 | 63.0478 | 0.015793 | 0.00028412 | 0.063781 | 0.07225 | 0.00057467 | -0.00011112 | -0.0033433 | -0.015015 | 0.00051903 | 0.064497 | 0.060184 | -0.0012946 | -0.00064293 | 7.4746e-05 | -0.036621 | 62.9974 | -60.1685 | 62.9471 | -59.9442 | -60.2783 | 0.027466 | 0.013733 | 62.9791 | -60.0357 | 63.0249 | -60.0723 | -60.1639 | -59.9762 | -0.16479 | -0.050354 | -0.10071 | 0.059509 | 60.0311 | -0.27466 | 60.1959 | -0.10986 | -0.032044 | -0.068665 | -0.022889 | -0.068665 | 0.027466 | -0.16022 | 0.05951 | -0.12817 | 0.2243 | 123.1155 | -0.036621 | 123.0606 | 123.1659 | 123.0148 | 123.0011 | 122.9828 | -123.2162 | -123.0835 | 122.9507 | 123.0286 | 59.967 | 60.0174
115.3281 | 123.2071 | -60.0174 | 63.0432 | -0.1368 | 0.0026339 | 0.063781 | 0.073745 | 0.0018565 | -0.0011791 | -0.00035247 | -0.021118 | 0.0026552 | 0.065992 | 0.065311 | -0.0032172 | 0.0027751 | 0.0013565 | -0.004578 | 63.0249 | -60.173 | 62.9517 | -59.9304 | -60.2966 | 0.018311 | 0.018311 | 62.9883 | -60.0174 | 63.0295 | -60.0723 | -60.1501 | -59.9487 | -0.15564 | -0.018311 | -0.091553 | 0.086975 | 60.0357 | -0.27924 | 60.1913 | -0.1236 | 0 | -0.054932 | -0.013733 | -0.054932 | 0.068665 | -0.13275 | 0.068665 | -0.13275 | 0.24262 | 123.1247 | -0.054932 | 123.0469 | 123.1979 | 123.0057 | 123.0423 | 123.0057 | -123.2162 | -123.0606 | 122.9691 | 123.0469 | 60.0128 | 60.0357
116.3281 | 123.262 | -60.0128 | 63.0341 | -0.037613 | 0.0019931 | 0.06485 | 0.075454 | 0.0016427 | 0.0015979 | -0.0022751 | -0.051636 | -0.00097617 | 0.065565 | 0.062747 | -0.00279 | 0.00085247 | -0.0035569 | 0.018311 | 63.002 | -60.173 | 63.002 | -59.8938 | -60.2509 | 0.022888 | 0.059509 | 62.9929 | -60.0266 | 63.0615 | -60.0174 | -60.2783 | -60.0769 | -0.16022 | -0.032044 | -0.032044 | 0.11902 | 60.0357 | -0.23804 | 60.1959 | -0.077819 | -0.013733 | -0.041199 | 0.027465 | -0.004578 | -0.064087 | -0.2655 | -0.050354 | -0.25177 | 0.27924 | 123.175 | 0.009155 | 123.0881 | 123.175 | 123.0194 | 123.0148 | 123.0057 | -123.2071 | -123.0606 | 123.0148 | 123.0743 | 60.0311 | 60.0723
117.3281 | 123.2071 | -60.0128 | 63.0569 | -0.022354 | -0.0027067 | 0.06485 | 0.07289 | -0.0011343 | 0.00031608 | -0.0041977 | 0.00024405 | 0.00116 | 0.064497 | 0.064884 | -0.0017218 | 0.0025613 | 0.0030655 | 0.17395 | 63.0707 | -60.1227 | 62.9425 | -59.9304 | -60.2783 | 0.009155 | 0 | 62.9745 | -60.0403 | 63.0203 | -60.054 | -60.1776 | -59.9442 | -0.10986 | 0.013733 | -0.11444 | 0.082397 | 60.022 | -0.2655 | 60.1318 | -0.15564 | -0.027466 | -0.082398 | -0.036621 | -0.041199 | 0.068664 | -0.1648 | 0.09613 | -0.13733 | 0.19226 | 123.0652 | -0.013733 | 123.0606 | 123.1934 | 123.0148 | 123.0835 | 122.9874 | -123.1796 | -123.0972 | 122.9553 | 123.0331 | 60.1868 | 60.0128
118.3281 | 123.2483 | -60.0174 | 63.0112 | -0.098648 | 0.00028412 | 0.064209 | 0.074813 | -0.00027993 | -0.0016065 | -0.0018479 | -0.036377 | 0.00116 | 0.062788 | 0.066806 | -0.0023626 | 0.0027751 | -0.00013885 | 0.013733 | 63.0066 | -60.173 | 62.9791 | -59.9167 | -60.2463 | 0.013733 | 0.045776 | 62.9837 | -60.0311 | 63.0661 | -60.0357 | -60.1318 | -59.9258 | -0.15564 | -0.004577 | -0.032043 | 0.10071 | 60.0311 | -0.22888 | 60.1868 | -0.073242 | -0.013733 | -0.027465 | 0.054932 | -0.018311 | 0.091553 | -0.11444 | 0.10529 | -0.10071 | 0.25635 | 123.1522 | -0.004578 | 123.0972 | 123.1796 | 123.0148 | 123.024 | 123.0011 | -123.1842 | -123.0423 | 122.9965 | 123.0835 | 60.0311 | 60.0632
119.3281 | 123.1934 | -60.0311 | 63.0249 | -0.0070953 | 0.00049772 | 0.064422 | 0.073959 | 0.0024973 | 0.00052988 | -0.0035569 | 0.0032959 | -0.00054897 | 0.063429 | 0.058261 | -0.0012946 | -0.00042933 | -0.00056605 | -0.022888 | 63.0203 | -60.1456 | 62.97 | -59.967 | -60.3058 | 0.022888 | -0.004578 | 63.0066 | -60.0128 | 63.0249 | -60.0769 | -60.1547 | -59.9808 | -0.11444 | -0.004577 | -0.054931 | 0.064087 | 60.054 | -0.27466 | 60.1685 | -0.16022 | 0.018311 | -0.01831 | 0 | -0.045776 | 0.050354 | -0.1236 | 0.032043 | -0.14191 | 0.17853 | 123.1155 | -0.064087 | 123.0377 | 123.1659 | 123.0194 | 123.0515 | 123.0377 | -123.1705 | -123.0377 | 123.0011 | 123.056 | 60.0082 | 60.0266
120.3281 | 123.2483 | -60.022 | 63.0615 | -0.07576 | 0.00071132 | 0.067199 | 0.072463 | 0.00057467 | -0.0011791 | -0.00099327 | -0.021118 | 0.00030543 | 0.064711 | 0.062107 | -0.00065377 | 0.0044839 | 0.00028835 | -0.027466 | 63.0341 | -60.1685 | 62.9471 | -59.9442 | -60.2783 | 0.018311 | -0.004578 | 63.0112 | -60.0494 | 63.0386 | -60.054 | -60.1685 | -59.9487 | -0.14648 | -0.027465 | -0.11444 | 0.07782 | 60.0403 | -0.25635 | 60.1868 | -0.10986 | -0.027465 | -0.050354 | -0.022888 | -0.032043 | 0.073243 | -0.14648 | 0.10071 | -0.11902 | 0.2243 | 123.1155 | -0.004578 | 123.0881 | 123.2025 | 123.0606 | 123.056 | 123.0331 | -123.23 | -123.111 | 122.9691 | 123.0606 | 59.9945 | 60.0174
121.3281 | 123.2483 | -59.9991 | 63.0569 | -0.098648 | 0.0011385 | 0.065704 | 0.070968 | -0.0019889 | 0.0024525 | 0.00028833 | 0.0093995 | -0.00119 | 0.063643 | 0.05698 | -0.002149 | 0.0017069 | -0.0022751 | 0.045776 | 62.9974 | -60.1364 | 63.0112 | -59.8572 | -60.1913 | 0.068665 | 0.07782 | 62.9745 | -60.022 | 63.0341 | -60.022 | -60.1227 | -59.9533 | -0.13733 | -0.059509 | -0.045777 | 0.14191 | 60.0677 | -0.19226 | 60.2051 | -0.054931 | -0.022889 | -0.082398 | -0.022888 | -0.022889 | 0.045776 | -0.1236 | 0.068665 | -0.10071 | 0.27924 | 123.1476 | 0 | 123.056 | 123.1339 | 122.9965 | 122.9965 | 122.9736 | -123.1934 | -123.0789 | 123.0103 | 123.0331 | 60.0449 | 60.0769
122.3281 | 123.2117 | -60.0174 | 63.0478 | -0.098648 | -0.00099768 | 0.06549 | 0.073318 | 0.0010019 | 0.00074348 | 0.00092933 | -0.069946 | 0.00094643 | 0.067274 | 0.065525 | -0.0030036 | -2.13e-06 | 0.0013565 | 0 | 63.0066 | -60.173 | 62.9654 | -59.9258 | -60.2966 | -0.036621 | -0.045776 | 62.97 | -60.0266 | 63.0249 | -60.0861 | -60.1868 | -59.9716 | -0.15564 | -0.041199 | -0.082398 | 0.091553 | 59.9808 | -0.27924 | 60.1364 | -0.1236 | -0.009155 | -0.07782 | -0.022889 | -0.068665 | 0.045776 | -0.16937 | 0.054931 | -0.16022 | 0.24719 | 123.1384 | -0.05951 | 123.0515 | 123.1796 | 122.9965 | 123.024 | 122.9874 | -123.2208 | -123.0743 | 122.9828 | 123.0423 | 60.0174 | 59.9716
123.3281 | 123.2071 | -59.9899 | 63.0432 | 0.0081632 | 0.0019931 | 0.063568 | 0.073531 | 0.0033517 | -0.0011791 | -0.0029159 | -0.018066 | 0.0013736 | 0.063429 | 0.05997 | -0.00043997 | 0.0027751 | -0.0012071 | -0.004578 | 63.0386 | -60.173 | 62.9242 | -59.9396 | -60.2692 | 0.013733 | 0 | 62.9929 | -60.0586 | 63.0203 | -60.0586 | -60.1685 | -59.9533 | -0.18311 | -0.004578 | -0.11902 | 0.050354 | 60.0037 | -0.27924 | 60.1868 | -0.09613 | -0.068665 | -0.050354 | -0.022888 | -0.068665 | 0.036621 | -0.17853 | 0.10529 | -0.10986 | 0.23346 | 123.0972 | 0 | 123.0789 | 123.2117 | 123.0515 | 123.0286 | 122.9828 | -123.2162 | -123.1018 | 122.9141 | 123.0103 | 59.9854 | 59.9899
124.3281 | 123.2254 | -60.0082 | 62.9974 | -0.060501 | 0.0022067 | 0.063568 | 0.075027 | 0.0020701 | -0.00032472 | -0.00056607 | -0.051636 | 0.0013736 | 0.064924 | 0.063175 | -0.0032172 | 0.00085247 | 0.0017837 | -0.018311 | 62.9974 | -60.1822 | 63.0203 | -59.8755 | -60.26 | 0.009155 | 0.041199 | 62.9929 | -60.0128 | 63.0661 | -60.0357 | -60.1456 | -59.9167 | -0.17395 | 0 | 0.022888 | 0.13275 | 60.0174 | -0.25177 | 60.1913 | -0.07782 | -0.004577 | -0.004578 | 0.068664 | -0.027466 | 0.091553 | -0.13733 | 0.09613 | -0.13275 | 0.3067 | 123.2025 | -0.022889 | 123.0789 | 123.1796 | 123.0057 | 123.0057 | 123.0011 | -123.1796 | -123.0103 | 123.0286 | 123.0743 | 59.9899 | 60.0494
125.3281 | 123.1979 | -60.022 | 63.0569 | -0.029984 | 0.0015659 | 0.061859 | 0.071395 | 0.00036107 | 0.00074348 | -0.0041977 | -0.018066 | -0.00033537 | 0.063429 | 0.064456 | -0.002149 | 0.0014933 | -0.0016343 | -0.022888 | 63.0295 | -60.173 | 62.9425 | -59.9442 | -60.2921 | 0.022888 | -0.009155 | 63.0203 | -60.0357 | 63.0203 | -60.0449 | -60.1639 | -59.9487 | -0.15106 | -0.027466 | -0.11444 | 0.07782 | 60.0449 | -0.27008 | 60.1959 | -0.11902 | -0.013733 | -0.036621 | -0.036621 | -0.022888 | 0.073243 | -0.14191 | 0.086976 | -0.12817 | 0.22888 | 123.1155 | -0.009155 | 123.056 | 123.2025 | 123.056 | 123.0515 | 123.0423 | -123.23 | -123.0927 | 122.9645 | 123.0423 | 59.9991 | 60.0128
126.3281 | 123.2712 | -60.0128 | 63.0478 | -0.20546 | 0.0019931 | 0.063781 | 0.073531 | 0.00036107 | -0.00053832 | -0.00035247 | -0.033325 | 0.002228 | 0.066206 | 0.068515 | -0.0012946 | 0.0049113 | 0.0026383 | 0.082397 | 63.0112 | -60.1913 | 63.0066 | -59.8618 | -60.2463 | 0.018311 | 0.032043 | 62.9608 | -60.0266 | 63.0707 | -60.0403 | -60.1273 | -59.903 | -0.17853 | -0.036622 | -0.041199 | 0.15106 | 60.0311 | -0.23346 | 60.2097 | -0.054932 | -0.013733 | -0.086976 | 0.022888 | -0.027466 | 0.10986 | -0.11444 | 0.1236 | -0.10071 | 0.32959 | 123.1979 | -0.013733 | 123.0972 | 123.2025 | 122.9874 | 123.024 | 122.9736 | -123.2391 | -123.0743 | 123.0194 | 123.0835 | 60.0952 | 60.0449
127.3281 | 123.1842 | -60.0174 | 63.0524 | -0.06813 | 0.00071132 | 0.063141 | 0.07289 | 0.0022837 | 0.00074348 | -0.00035247 | 0.0032959 | 0.00116 | 0.065565 | 0.057193 | -0.00279 | -2.13e-06 | -0.0020615 | -0.022888 | 63.0249 | -60.1547 | 63.0249 | -60.1089 | -60.4019 | 0.032043 | 0.018311 | 63.002 | -60.0357 | 63.0066 | -60.0723 | -60.1456 | -59.9487 | -0.13733 | -0.027466 | -0.027466 | -0.091553 | 60.0494 | -0.38452 | 60.1868 | -0.24719 | -0.018311 | -0.050354 | -0.045776 | -0.054932 | 0.068665 | -0.12817 | 0.086976 | -0.10986 | 0.045776 | 123.1796 | -0.036621 | 123.0423 | 123.1796 | 123.0377 | 123.0423 | 123.0194 | -123.2071 | -123.0881 | 123.0423 | 123.024 | 59.9945 | 60.0357
128.3281 | 123.2483 | -59.9899 | 63.0157 | -0.28175 | 0.0024203 | 0.0625 | 0.074813 | 0.0033517 | 0.00010248 | -0.00099327 | -0.042481 | 0.0013736 | 0.065352 | 0.066379 | -0.0023626 | 0.0032023 | -0.0027023 | 0.09613 | 62.9974 | -60.1685 | 62.9929 | -59.8709 | -60.26 | 0.032043 | 0.032043 | 62.9837 | -60.0266 | 63.0661 | -60.0357 | -60.1273 | -59.9213 | -0.17853 | -0.01831 | -0.022888 | 0.11902 | 60.022 | -0.27008 | 60.2005 | -0.091553 | -0.036621 | -0.032043 | 0.050354 | -0.045777 | 0.068664 | -0.13733 | 0.10529 | -0.10071 | 0.29755 | 123.1613 | -0.009156 | 123.0927 | 123.1659 | 123.0103 | 122.9874 | 122.9736 | -123.1842 | -123.0423 | 122.9828 | 123.056 | 60.0861 | 60.022
129.3281 | 123.2391 | -59.9991 | 63.0157 | -0.06813 | 0.00092492 | 0.06485 | 0.07289 | -0.00070713 | -0.00096552 | -0.00077967 | -0.030273 | 0.00073263 | 0.065992 | 0.063175 | -0.0034308 | 0.0017069 | 0.0019973 | 0.004578 | 63.0112 | -60.1593 | 62.9791 | -59.903 | -60.2463 | 0.027466 | 0.036621 | 62.9929 | -60.0266 | 63.0524 | -60.022 | -60.1501 | -59.9258 | -0.16022 | -0.004578 | -0.036621 | 0.09613 | 60.0266 | -0.24719 | 60.1868 | -0.086975 | -0.027466 | -0.022888 | 0.036621 | -0.022889 | 0.073242 | -0.15106 | 0.10071 | -0.1236 | 0.25635 | 123.1384 | 0.004577 | 123.0789 | 123.1705 | 123.0194 | 123.0103 | 122.9919 | -123.175 | -123.0423 | 122.9782 | 123.0515 | 60.0037 | 60.0357
130.3281 | 123.175 | -60.0449 | 63.0066 | -0.022354 | 0.0019931 | 0.063141 | 0.07524 | 0.0033517 | 0.0028797 | 0.0024245 | -0.042481 | 0.002228 | 0.067488 | 0.06232 | -0.0012946 | 0.0017069 | 0.0062697 | -0.082397 | 62.9745 | -60.2005 | 62.9013 | -59.9854 | -60.3561 | -0.11444 | -0.14191 | 62.9654 | -60.0952 | 63.0386 | -60.5713 | -60.1547 | -59.8114 | -0.15564 | -0.032044 | -0.10529 | 0.059509 | 59.9304 | -0.31128 | 60.0861 | -0.15564 | -0.050354 | -0.041199 | 0.032043 | -0.52643 | 0.23346 | -0.10986 | 0.28381 | -0.059509 | 0.21515 | 123.1018 | -0.47607 | 123.1338 | 123.175 | 123.0606 | 123.0194 | 123.0103 | -123.2071 | -123.1018 | 122.9462 | 123.0835 | 59.9625 | 59.903
131.3281 | 123.2208 | -60.0082 | 62.9883 | -0.022354 | 0.00028412 | 0.065063 | 0.075027 | -0.0026297 | -0.0026745 | -0.0016343 | -0.027222 | 0.0015872 | 0.067061 | 0.06467 | -0.002149 | 0.0010661 | 0.0017837 | 0.018311 | 63.0066 | -60.1776 | 62.9745 | -59.9121 | -60.2463 | 0.009155 | 0.054932 | 62.9837 | -60.0311 | 63.0615 | -60.0266 | -60.1593 | -59.9304 | -0.16937 | 0.018311 | -0.013733 | 0.096131 | 60.0174 | -0.23804 | 60.1868 | -0.068665 | -0.022888 | -0.004577 | 0.073242 | -0.01831 | 0.07782 | -0.15106 | 0.10071 | -0.12817 | 0.2655 | 123.1522 | 0.004578 | 123.0927 | 123.1842 | 123.0148 | 123.0148 | 122.9919 | -123.1659 | -123.0194 | 122.9828 | 123.0698 | 60.0266 | 60.0632
132.3281 | 123.2025 | -60.022 | 63.002 | -0.06813 | 0.0024203 | 0.066345 | 0.076095 | 0.0044199 | -0.00075192 | -0.00035247 | -0.045532 | 0.00030543 | 0.064924 | 0.061252 | -0.0023626 | 0.0025613 | -0.0024887 | -0.032043 | 63.002 | -60.1776 | 62.9471 | -59.935 | -60.3058 | -0.050354 | -0.064087 | 62.9562 | -60.0494 | 63.0066 | -60.0906 | -60.1959 | -59.9808 | -0.15564 | 0 | -0.054931 | 0.086975 | 59.9716 | -0.28381 | 60.1273 | -0.12817 | -0.027465 | -0.045776 | 0.004578 | -0.068664 | 0.041199 | -0.17395 | 0.068664 | -0.14648 | 0.24261 | 123.1247 | -0.041199 | 123.056 | 123.1796 | 123.0057 | 123.024 | 122.9782 | -123.1796 | -123.0515 | 122.9691 | 123.0286 | 59.9899 | 59.9579
133.3281 | 123.2437 | -59.9991 | 63.0432 | -0.07576 | 0.0013523 | 0.063995 | 0.073531 | 0.0010019 | 0.00031608 | 0.0032791 | -0.033325 | 0.0020144 | 0.064283 | 0.067661 | -0.002149 | -0.0012839 | 0.0060561 | 0.018311 | 63.0112 | -60.1501 | 62.9791 | -59.9075 | -60.2463 | 0.022888 | 0.050354 | 62.9837 | -60.0403 | 63.0386 | -60.0266 | -60.0769 | -59.8663 | -0.15106 | -0.032044 | -0.064087 | 0.091552 | 60.022 | -0.24719 | 60.173 | -0.096131 | -0.041199 | -0.059509 | -0.004578 | -0.027466 | 0.13275 | -0.07782 | 0.17395 | -0.036621 | 0.24261 | 123.1293 | 0.013733 | 123.0789 | 123.1613 | 123.024 | 123.0103 | 122.9828 | -123.1934 | -123.0835 | 122.9782 | 123.0377 | 60.0174 | 60.0494
134.3281 | 123.1934 | -60.0174 | 62.9974 | -0.12154 | 7.0518e-05 | 0.06485 | 0.074172 | 0.0010019 | 0.00010248 | 0.0019973 | -0.039429 | 0.0015872 | 0.065138 | 0.057621 | -0.002149 | 0.0025613 | 0.0015701 | 0.013733 | 62.9929 | -60.1456 | 62.9883 | -59.9075 | -60.2463 | -0.022888 | 0 | 62.9883 | -60.0494 | 63.0524 | -60.0632 | -60.173 | -59.9167 | -0.12817 | -0.004578 | -0.009156 | 0.10986 | 59.9945 | -0.22888 | 60.1227 | -0.10071 | -0.032043 | -0.009156 | 0.054931 | -0.045776 | 0.10071 | -0.15564 | 0.13275 | -0.1236 | 0.23804 | 123.1338 | -0.013733 | 123.1018 | 123.1384 | 123.0377 | 123.0103 | 123.0057 | -123.143 | -123.0469 | 123.0057 | 123.0698 | 60.0311 | 60.0174
135.3281 | 123.23 | -60.0266 | 63.0157 | -0.060501 | 0.0028475 | 0.067413 | 0.075881 | 0.00036107 | 0.0015979 | -0.00077967 | -0.030273 | 9.1834e-05 | 0.063429 | 0.065952 | -0.00086737 | 0.0023477 | -0.0020615 | 0.009155 | 62.9883 | -60.1868 | 62.9608 | -59.903 | -60.2783 | -0.022888 | -0.004578 | 62.9608 | -60.0311 | 63.0249 | -60.0586 | -60.1685 | -59.9442 | -0.16022 | -0.027466 | -0.054932 | 0.1236 | 60.0037 | -0.25177 | 60.1639 | -0.091552 | -0.004578 | -0.054932 | 0.009155 | -0.032044 | 0.082397 | -0.14191 | 0.086975 | -0.13733 | 0.28381 | 123.1476 | -0.027466 | 123.056 | 123.175 | 122.9919 | 123.0148 | 122.9874 | -123.2025 | -123.0469 | 122.9874 | 123.0515 | 60.0357 | 60.022
136.3281 | 123.2483 | -60.0311 | 62.9929 | -0.052872 | 0.0011385 | 0.063141 | 0.07225 | -0.0013479 | 0.00052988 | 0.00092933 | -0.021118 | 0.00073263 | 0.064924 | 0.06232 | -0.0019354 | 0.0019205 | 0.0011429 | -0.10529 | 62.9837 | -60.1959 | 62.9013 | -59.967 | -60.3333 | -0.11902 | -0.12817 | 62.9196 | -60.0815 | 63.0341 | -60.0861 | -60.1913 | -59.9533 | -0.16479 | -0.009155 | -0.091553 | 0.064087 | 59.9121 | -0.30212 | 60.0769 | -0.13733 | -0.050354 | -0.073242 | 0.041199 | -0.054932 | 0.07782 | -0.16022 | 0.12817 | -0.10986 | 0.22888 | 123.0972 | -0.004578 | 123.1155 | 123.1796 | 123.0011 | 123.0148 | 122.9507 | -123.1888 | -123.0743 | 122.9324 | 123.0652 | 59.9258 | 59.903
137.3281 | 123.2071 | -60.0128 | 62.9883 | -0.0070953 | 0.0019931 | 0.065063 | 0.075881 | 0.0018565 | 0.0018115 | 0.0032791 | -0.030273 | 9.1834e-05 | 0.063429 | 0.066593 | -0.002149 | 0.0017069 | 0.0019973 | -0.022888 | 62.9974 | -60.1822 | 62.9471 | -59.9213 | -60.2783 | -0.027466 | -0.045776 | 62.9745 | -60.0586 | 63.0112 | -60.0906 | -60.1822 | -59.9487 | -0.16937 | 0.009156 | -0.041198 | 0.091552 | 59.9854 | -0.2655 | 60.1547 | -0.09613 | -0.045777 | -0.013733 | 0.022888 | -0.07782 | 0.064087 | -0.16937 | 0.10986 | -0.1236 | 0.26093 | 123.1293 | -0.032043 | 123.0698 | 123.1796 | 123.0331 | 123.0103 | 122.9874 | -123.1705 | -123.0469 | 122.9599 | 123.024 | 59.9899 | 59.967
138.3281 | 123.2391 | -60.022 | 62.9562 | -0.098648 | 0.0011385 | 0.062927 | 0.074386 | 0.0022837 | 0.00095708 | 0.0022109 | -0.0028075 | 9.1834e-05 | 0.064924 | 0.062107 | -0.0036444 | 0.00042507 | -0.0012071 | -0.09613 | 62.9654 | -60.1868 | 62.9059 | -59.9533 | -60.3333 | -0.10071 | -0.1236 | 62.9242 | -60.0723 | 63.0661 | -60.0586 | -60.1456 | -59.9304 | -0.16479 | 0.009155 | -0.050354 | 0.068665 | 59.9213 | -0.31128 | 60.0861 | -0.14648 | -0.050354 | -0.032044 | 0.10986 | -0.036621 | 0.091553 | -0.1236 | 0.14191 | -0.073242 | 0.23346 | 123.0927 | 0.013733 | 123.1384 | 123.1522 | 122.9965 | 122.9874 | 122.9462 | -123.143 | -123.0286 | 122.9279 | 123.0881 | 59.9258 | 59.8984
139.3281 | 123.2071 | -60.022 | 63.002 | -0.083389 | 0.0026339 | 0.06549 | 0.073531 | 0.00036107 | -0.00011112 | -0.0027023 | -0.039429 | 0.00073263 | 0.065565 | 0.060184 | -0.00279 | 0.0034159 | -0.0027023 | -0.036621 | 62.9929 | -60.173 | 62.9608 | -59.9396 | -60.3058 | -0.068665 | -0.082397 | 62.9837 | -60.0357 | 63.0066 | -60.0952 | -60.2097 | -59.9625 | -0.15106 | -0.009155 | -0.041199 | 0.082398 | 59.9533 | -0.28381 | 60.1044 | -0.13275 | -0.013733 | -0.01831 | 0.004578 | -0.073242 | 0.05951 | -0.18768 | 0.073243 | -0.17395 | 0.23346 | 123.1338 | -0.059509 | 123.0423 | 123.1659 | 123.0194 | 123.0148 | 123.0057 | -123.175 | -123.0377 | 122.9828 | 123.0286 | 59.9854 | 59.9396
140.3281 | 123.2208 | -60.0403 | 62.9837 | -0.06813 | 7.0518e-05 | 0.065277 | 0.073531 | -0.00070713 | -0.00075192 | -0.0020615 | -0.039429 | 0.00116 | 0.064283 | 0.065311 | -0.0023626 | 0.0012797 | -0.0012071 | -0.09613 | 62.9883 | -60.2097 | 62.8876 | -59.9945 | -60.3607 | -0.10071 | -0.16022 | 62.9379 | -60.0677 | 63.002 | -60.1044 | -60.228 | -59.9716 | -0.16937 | 0.004577 | -0.096131 | 0.045776 | 59.9396 | -0.32043 | 60.1089 | -0.15106 | -0.027466 | -0.045777 | 0.01831 | -0.064087 | 0.068664 | -0.18768 | 0.09613 | -0.16022 | 0.21515 | 123.0972 | -0.036621 | 123.0698 | 123.1979 | 123.0057 | 123.0286 | 122.9782 | -123.1934 | -123.0515 | 122.9279 | 123.0423 | 59.9442 | 59.8801
141.3281 | 123.2437 | -60.054 | 63.0112 | -0.098648 | 0.0024203 | 0.066131 | 0.075027 | -0.00070713 | 0.00095708 | -0.00035247 | -0.033325 | 9.1834e-05 | 0.065138 | 0.062747 | -0.0025764 | 0.0014933 | -0.00077965 | -0.004578 | 62.9837 | -60.1913 | 62.9837 | -59.903 | -60.2692 | -0.013733 | -0.009155 | 62.9883 | -60.0449 | 63.0386 | -60.0632 | -60.1913 | -59.935 | -0.13733 | -0.027465 | -0.027465 | 0.15106 | 60.0403 | -0.21515 | 60.1776 | -0.07782 | 0.009155 | -0.022888 | 0.027466 | -0.009155 | 0.11902 | -0.13733 | 0.10986 | -0.14648 | 0.28839 | 123.175 | -0.01831 | 123.0835 | 123.175 | 123.0331 | 123.0377 | 123.0423 | -123.2025 | -123.056 | 123.0377 | 123.0927 | 60.0494 | 60.0449
142.3281 | 123.23 | -60.0449 | 62.9929 | -0.091019 | 7.0518e-05 | 0.065277 | 0.075881 | -0.00049353 | 0.00010248 | -0.0016343 | -0.042481 | 0.00073263 | 0.064497 | 0.059116 | -0.0030036 | 0.00063867 | -0.0029159 | -0.10071 | 62.9837 | -60.2005 | 62.883 | -59.9808 | -60.3378 | -0.12817 | -0.15564 | 62.9471 | -60.0357 | 63.0066 | -60.0998 | -60.1913 | -59.967 | -0.15564 | -0.009155 | -0.10986 | 0.064087 | 59.9167 | -0.29297 | 60.0723 | -0.13733 | 0.009155 | -0.045776 | 0.013733 | -0.054931 | 0.07782 | -0.14648 | 0.068665 | -0.15564 | 0.21973 | 123.0835 | -0.064086 | 123.0423 | 123.1842 | 122.9828 | 123.0286 | 122.9919 | -123.1934 | -123.0286 | 122.9279 | 123.0515 | 59.9442 | 59.8892
143.3281 | 123.1979 | -60.0494 | 62.9929 | -0.045242 | 7.0518e-05 | 0.063781 | 0.07289 | 0.0027109 | 0.0013843 | -0.00077967 | -0.042481 | 0.00116 | 0.063643 | 0.060611 | -0.002149 | 0.0036295 | 0.0032791 | -0.11902 | 62.97 | -60.2142 | 63.0981 | -59.9442 | -60.3745 | -0.054932 | -0.13275 | 62.9654 | -60.0403 | 62.9929 | -60.1456 | -60.2371 | -59.9854 | -0.16479 | -0.022888 | 0.10529 | 0.10529 | 59.9945 | -0.32501 | 60.1593 | -0.16022 | 0.009155 | -0.027466 | 0 | -0.096131 | 0.064086 | -0.18768 | 0.054931 | -0.19684 | 0.27008 | 123.3124 | -0.10529 | 123.0331 | 123.1842 | 123.0057 | 123.0194 | 123.0148 | -123.2071 | -123.0331 | 123.1476 | 123.0423 | 59.9304 | 59.9167
144.3281 | 123.317 | -59.9991 | 62.9517 | -0.06813 | 0.0019931 | 0.06549 | 0.074172 | 0.0016427 | -0.0011791 | 7.4734e-05 | 0.0032959 | 0.0018008 | 0.063429 | 0.058048 | -0.0012946 | 0.0025613 | -0.0014207 | -0.064087 | 62.9562 | -60.1685 | 62.9929 | -59.8846 | -60.2692 | -0.059509 | -0.064087 | 62.9333 | -60.0632 | 63.0981 | -60.0082 | -60.1181 | -59.8755 | -0.16937 | 0.004578 | 0.041199 | 0.11444 | 59.9396 | -0.27008 | 60.1089 | -0.10071 | -0.064087 | -0.01831 | 0.14649 | -0.009156 | 0.1236 | -0.11902 | 0.18768 | -0.054932 | 0.28381 | 123.1613 | 0.054931 | 123.1613 | 123.1247 | 122.9965 | 122.9553 | 122.9324 | -123.1201 | -123.0148 | 122.9919 | 123.0972 | 59.935 | 59.935
145.3281 | 123.1567 | -60.054 | 62.9974 | -0.06813 | 0.0041293 | 0.065918 | 0.074599 | -0.0022025 | -0.0037427 | 0.00028833 | -0.033325 | 0.00030543 | 0.066633 | 0.065525 | -0.0025764 | 0.0036295 | 0.0024245 | -0.35248 | 62.9196 | -60.2371 | 62.8876 | -60.0037 | -60.3287 | -0.11902 | -0.16937 | 62.9379 | -60.0677 | 62.9883 | -60.1181 | -60.2417 | -59.9854 | -0.18311 | -0.07782 | -0.10986 | 0.050354 | 59.935 | -0.27466 | 60.1181 | -0.091552 | -0.013733 | -0.05951 | -0.009156 | -0.064087 | 0.068664 | -0.18768 | 0.082397 | -0.17395 | 0.23346 | 123.1247 | -0.050354 | 123.056 | 123.1567 | 123.0057 | 122.9736 | 122.9919 | -123.2346 | -123.0652 | 122.9416 | 123.0423 | 59.7015 | 59.8846
146.3281 | 123.3353 | -59.9854 | 62.9745 | -0.12154 | 0.0017795 | 0.065277 | 0.073104 | 0.0014291 | -0.00075192 | -0.0014207 | 0.015503 | 0.00073263 | 0.06407 | 0.060398 | -0.0019354 | 0.0036295 | 0.0011429 | -0.032043 | 62.9608 | -60.1639 | 63.0203 | -59.8663 | -60.2463 | -0.018311 | -0.027466 | 62.9059 | -60.0403 | 63.0981 | -59.9945 | -60.0769 | -59.8755 | -0.17853 | -0.013733 | 0.045777 | 0.11902 | 59.967 | -0.26093 | 60.1456 | -0.082398 | -0.054931 | -0.068664 | 0.1236 | -0.009155 | 0.10986 | -0.091552 | 0.1648 | -0.036621 | 0.29755 | 123.1842 | 0.045776 | 123.1384 | 123.1247 | 122.9462 | 122.9462 | 122.8912 | -123.1384 | -123.0148 | 123.0057 | 123.0835 | 59.9533 | 59.9579
147.3281 | 123.1934 | -60.0449 | 63.0112 | -0.060501 | 0.0017795 | 0.065918 | 0.076095 | 0.0012155 | 0.00010248 | -0.0016343 | -0.069946 | 0.00073263 | 0.065352 | 0.062961 | -0.0025764 | 0.0014933 | -0.0018479 | -0.07782 | 62.9837 | -60.1868 | 62.9059 | -59.9945 | -60.3561 | -0.10529 | -0.16022 | 62.9654 | -60.0815 | 62.9837 | -60.141 | -60.2646 | -60.0082 | -0.14191 | -0.027465 | -0.10529 | 0.050354 | 59.9396 | -0.31128 | 60.0815 | -0.16937 | -0.036621 | -0.045776 | -0.027465 | -0.09613 | 0.036621 | -0.21973 | 0.073242 | -0.1831 | 0.19226 | 123.0927 | -0.059509 | 123.0652 | 123.1705 | 123.0469 | 123.0286 | 123.0103 | -123.1979 | -123.0927 | 122.9507 | 123.0286 | 59.967 | 59.8846
148.3281 | 123.2529 | -60.0174 | 62.9608 | -0.083389 | -0.00057028 | 0.064636 | 0.074172 | -0.0015615 | 0.0013843 | -0.00035247 | -0.030273 | -0.00054897 | 0.064497 | 0.062747 | -0.0030036 | 0.0025613 | 0.0039199 | -0.10529 | 62.9791 | -60.2051 | 62.9288 | -59.9579 | -60.3287 | -0.10986 | -0.14191 | 62.9471 | -60.0677 | 63.0478 | -60.0632 | -60.1685 | -59.9396 | -0.18768 | 0.018311 | -0.032043 | 0.059509 | 59.9075 | -0.31128 | 60.0952 | -0.1236 | -0.050354 | -0.013732 | 0.086976 | -0.045776 | 0.07782 | -0.15106 | 0.12817 | -0.10071 | 0.24719 | 123.1338 | 0.004578 | 123.1155 | 123.1842 | 123.0148 | 122.9965 | 122.9645 | -123.1659 | -123.0286 | 122.9462 | 123.0652 | 59.9121 | 59.8755
149.3281 | 123.2712 | -60.0311 | 62.9379 | -0.12154 | -0.00035668 | 0.065704 | 0.073531 | -0.00070713 | -0.0016065 | -0.0016343 | -0.011963 | 0.0020144 | 0.064711 | 0.063388 | -0.0023626 | 0.00063867 | -0.00035245 | -0.10986 | 62.9791 | -60.228 | 62.9288 | -59.9579 | -60.3241 | -0.10986 | -0.14191 | 62.9517 | -60.0723 | 63.0524 | -60.0723 | -60.1547 | -59.9258 | -0.19684 | 0.041199 | -0.009155 | 0.073242 | 59.9213 | -0.29297 | 60.1181 | -0.096131 | -0.041199 | 0.013733 | 0.11444 | -0.041199 | 0.10529 | -0.1236 | 0.14648 | -0.082397 | 0.27008 | 123.1567 | 0 | 123.1247 | 123.2071 | 123.024 | 123.0103 | 122.9828 | -123.1659 | -123.0103 | 122.9599 | 123.0835 | 59.9213 | 59.8892
150.3281 | 123.262 | -60.0082 | 62.9562 | -0.060501 | 0.0013523 | 0.063781 | 0.071822 | -0.00070713 | -0.00075192 | -0.0012071 | 0.015503 | -0.0016172 | 0.063215 | 0.061466 | -0.0019354 | 0.0014933 | 0.0043471 | -0.054932 | 62.9425 | -60.1456 | 62.9929 | -59.8709 | -60.2692 | -0.036621 | -0.054932 | 62.9333 | -60.022 | 63.0707 | -60.0266 | -60.1318 | -59.9167 | -0.13733 | -0.013733 | 0.036621 | 0.13733 | 59.9716 | -0.26093 | 60.1089 | -0.1236 | -0.013733 | -0.022888 | 0.11444 | -0.01831 | 0.091553 | -0.1236 | 0.10529 | -0.10986 | 0.27466 | 123.1384 | -0.004577 | 123.0927 | 123.0881 | 122.9553 | 122.9507 | 122.9416 | -123.1018 | -122.9782 | 123.0011 | 123.0789 | 59.9533 | 59.9533
151.3281 | 123.2803 | -60.022 | 62.97 | -0.098648 | 0.00049772 | 0.061645 | 0.075454 | -0.00027993 | -0.00032472 | 0.0024245 | -0.021118 | 0.0013736 | 0.063856 | 0.05997 | -0.0025764 | 0.0019205 | 0.00050195 | -0.07782 | 62.9654 | -60.2371 | 62.9379 | -59.9625 | -60.3149 | -0.09613 | -0.13733 | 62.9517 | -60.0586 | 63.0661 | -60.0494 | -60.1547 | -59.9258 | -0.21515 | -0.004578 | -0.032044 | 0.05951 | 59.9258 | -0.29297 | 60.141 | -0.077819 | -0.036621 | -0.018311 | 0.09613 | -0.027465 | 0.096131 | -0.13275 | 0.13275 | -0.09613 | 0.27466 | 123.175 | 0.009156 | 123.1247 | 123.2025 | 123.0103 | 122.9874 | 122.9736 | -123.2071 | -123.0286 | 122.9599 | 123.0881 | 59.9442 | 59.8846
152.3281 | 123.3078 | -60.0128 | 62.9517 | -0.091019 | 0.0013523 | 0.06485 | 0.074386 | 0.00078827 | 0.00074348 | -0.0035569 | -0.0028075 | 0.00073263 | 0.063429 | 0.055698 | -0.0015082 | 0.0017069 | 0.0015701 | -0.027466 | 62.9333 | -60.1501 | 63.0112 | -59.8618 | -60.2325 | -0.036621 | -0.041199 | 62.9333 | -60.0357 | 63.121 | -60.0037 | -60.0906 | -59.8938 | -0.13733 | -0.01831 | 0.059509 | 0.15106 | 59.9762 | -0.21973 | 60.1135 | -0.082398 | -0.022889 | -0.01831 | 0.16937 | 0.009155 | 0.11902 | -0.07782 | 0.14191 | -0.054931 | 0.28839 | 123.1613 | 0.032044 | 123.1567 | 123.0835 | 122.9691 | 122.9462 | 122.9462 | -123.1018 | -122.9874 | 123.024 | 123.1338 | 59.9854 | 59.9716
153.3281 | 123.2758 | -60.0403 | 62.9517 | -0.12154 | 0.00028412 | 0.06485 | 0.073745 | 0.00078827 | -0.0033155 | -0.00013887 | -0.045532 | 0.0015872 | 0.063643 | 0.06232 | -0.0030036 | 0.0014933 | 0.00092935 | -0.10529 | 62.9791 | -60.1868 | 62.9333 | -59.9533 | -60.3287 | -0.091553 | -0.11902 | 62.9471 | -60.0677 | 63.0707 | -60.0449 | -60.1501 | -59.9075 | -0.14648 | 0.027466 | -0.01831 | 0.086975 | 59.9487 | -0.28839 | 60.0952 | -0.14191 | -0.027466 | -0.004577 | 0.11902 | -0.004578 | 0.13275 | -0.10986 | 0.16022 | -0.082397 | 0.23346 | 123.1201 | 0.022888 | 123.1384 | 123.1659 | 123.0148 | 123.0194 | 122.9874 | -123.1384 | -123.0194 | 122.9736 | 123.111 | 59.935 | 59.9213
154.3281 | 123.2666 | -60.0357 | 62.9791 | -0.07576 | -0.00078408 | 0.064636 | 0.076949 | -0.00092073 | -0.0020337 | -0.0037705 | -0.0028075 | -0.00012177 | 0.064283 | 0.060398 | -0.0047126 | 0.0010661 | 0.00092935 | -0.054932 | 62.9562 | -60.1685 | 62.9791 | -59.8801 | -60.2646 | -0.036621 | -0.064087 | 62.9288 | -60.0403 | 63.0615 | -60.054 | -60.1318 | -59.9167 | -0.13275 | -0.022888 | 0 | 0.15564 | 59.9991 | -0.22888 | 60.1318 | -0.09613 | -0.004577 | -0.050354 | 0.082397 | -0.01831 | 0.11902 | -0.09613 | 0.1236 | -0.091553 | 0.28839 | 123.1476 | -0.013733 | 123.1018 | 123.1247 | 122.9691 | 122.9919 | 122.9645 | -123.1476 | -123.0194 | 123.0148 | 123.0972 | 59.9808 | 59.9716
155.3281 | 123.2025 | -60.0403 | 63.0112 | -0.091019 | 0.0019931 | 0.065277 | 0.076522 | -0.00092073 | 0.0013843 | -0.00056607 | -0.063843 | -0.0014036 | 0.064497 | 0.063175 | -0.0012946 | 0.0029887 | -0.00056605 | -0.09613 | 62.9791 | -60.2097 | 62.9013 | -60.0082 | -60.3561 | -0.11444 | -0.17395 | 62.97 | -60.054 | 63.002 | -60.1273 | -60.2234 | -59.9854 | -0.16937 | -0.032043 | -0.10986 | 0.032043 | 59.9258 | -0.31586 | 60.0952 | -0.14648 | -0.013733 | -0.041198 | -0.009155 | -0.086975 | 0.054931 | -0.18311 | 0.068664 | -0.16937 | 0.20142 | 123.111 | -0.073242 | 123.056 | 123.1888 | 123.024 | 123.0194 | 123.0103 | -123.2208 | -123.0652 | 122.9416 | 123.0423 | 59.9442 | 59.8663
156.3281 | 123.3078 | -59.9899 | 62.9608 | -0.10628 | 0.00092492 | 0.066131 | 0.074813 | 0.0033517 | -0.00032472 | 0.00092933 | -0.0058593 | 0.00073263 | 0.065138 | 0.066593 | -0.0040716 | 0.00085247 | -0.0012071 | -0.045776 | 62.9517 | -60.1639 | 63.0203 | -59.848 | -60.2417 | -0.036621 | -0.022888 | 62.9242 | -60.0311 | 63.1027 | -60.0037 | -60.0998 | -59.8709 | -0.17395 | -0.009155 | 0.05951 | 0.14191 | 59.9533 | -0.25177 | 60.1273 | -0.07782 | -0.041199 | -0.036621 | 0.14191 | -0.013733 | 0.11902 | -0.10986 | 0.16022 | -0.068664 | 0.31586 | 123.1842 | 0.027466 | 123.1338 | 123.1155 | 122.9553 | 122.9416 | 122.9141 | -123.1247 | -122.9919 | 123.0103 | 123.0927 | 59.9442 | 59.967
157.3281 | 123.2986 | -60.0082 | 62.9425 | -0.091019 | 0.00049772 | 0.063781 | 0.073745 | -0.00049353 | 0.0028797 | -0.00099327 | -0.039429 | -0.00119 | 0.060866 | 0.062747 | -0.0030036 | 0.0010661 | 0.0013565 | -0.027466 | 62.97 | -60.1776 | 63.0157 | -59.8618 | -60.2234 | -0.022888 | -0.032043 | 62.9196 | -60.0357 | 63.0981 | -59.9991 | -60.0723 | -59.8801 | -0.16937 | 0.027466 | 0.073242 | 0.14648 | 59.9854 | -0.21515 | 60.1547 | -0.045777 | -0.027466 | -0.022888 | 0.15564 | 0.009156 | 0.12817 | -0.064087 | 0.15564 | -0.036621 | 0.31586 | 123.1934 | 0.036622 | 123.1339 | 123.1476 | 122.9553 | 122.9782 | 122.9279 | -123.1201 | -122.9782 | 123.024 | 123.1064 | 59.9808 | 59.9762
158.3281 | 123.2666 | -60.0266 | 62.9608 | -0.12917 | 0.0022067 | 0.066559 | 0.074386 | 0.0020701 | -0.00011112 | -0.00013887 | 0.0063477 | 0.0030826 | 0.06172 | 0.068515 | -0.0017218 | 0.0012797 | -0.00077965 | -0.064087 | 62.9608 | -60.1639 | 62.9974 | -59.8663 | -60.2554 | -0.022888 | -0.041199 | 62.915 | -60.054 | 63.0844 | -60.0357 | -60.1181 | -59.9167 | -0.13733 | 0 | 0.036622 | 0.16022 | 60.0037 | -0.22888 | 60.141 | -0.091553 | -0.027466 | -0.045776 | 0.1236 | -0.009156 | 0.10986 | -0.091553 | 0.13733 | -0.064087 | 0.29755 | 123.1613 | 0.01831 | 123.1384 | 123.1247 | 122.9691 | 122.9874 | 122.9416 | -123.1247 | -123.0148 | 123.024 | 123.111 | 59.9625 | 59.9854
159.3281 | 123.3765 | -60.0037 | 62.9654 | -0.083389 | 7.0518e-05 | 0.06485 | 0.072463 | -0.00070713 | 0.00074348 | 0.00028833 | -0.027222 | 0.0013736 | 0.064711 | 0.069156 | -0.0025764 | 0.0025613 | -0.0012071 | -0.050354 | 62.9608 | -60.1822 | 62.9929 | -59.903 | -60.2554 | -0.027466 | -0.050354 | 62.9059 | -60.054 | 63.121 | -59.9487 | -60.3333 | -60.0403 | -0.17853 | -0.004578 | 0.027466 | 0.10071 | 59.9762 | -0.25177 | 60.1547 | -0.073242 | -0.050354 | -0.059509 | 0.15564 | 0.054932 | -0.036621 | -0.32959 | 0.013733 | -0.27924 | 0.27924 | 123.175 | 0.10529 | 123.175 | 123.143 | 122.9599 | 122.9645 | 122.9095 | -123.1476 | -123.0194 | 122.9965 | 123.1247 | 59.9533 | 59.9533
160.3281 | 123.2803 | -59.9945 | 62.9837 | -0.12917 | 0.0037021 | 0.064422 | 0.073745 | -0.00049353 | -0.00096552 | 0.0015701 | -0.039429 | 0.0020144 | 0.063215 | 0.060398 | -0.001081 | -0.00021573 | 0.0015701 | -0.050354 | 62.9379 | -60.1639 | 63.0112 | -59.8343 | -60.2417 | -0.036621 | -0.032043 | 62.915 | -60.0449 | 63.0844 | -60.0311 | -60.0952 | -59.903 | -0.16937 | -0.045777 | 0.027465 | 0.16022 | 59.9579 | -0.24719 | 60.1273 | -0.07782 | -0.050354 | -0.068665 | 0.10071 | -0.036621 | 0.091553 | -0.10071 | 0.14191 | -0.050354 | 0.32959 | 123.175 | 0.013733 | 123.1293 | 123.1018 | 122.9599 | 122.9324 | 122.9095 | -123.1476 | -123.0286 | 123.0057 | 123.0789 | 59.9442 | 59.9625
161.3281 | 123.2483 | -60.0174 | 62.9974 | -0.10628 | 0.00028412 | 0.06485 | 0.075881 | 0.00036107 | 0.00010248 | -0.0018479 | -0.07605 | 0.0015872 | 0.064711 | 0.064456 | -0.0036444 | 0.0025613 | 0.00050195 | -0.10071 | 62.9745 | -60.1959 | 62.915 | -59.9899 | -60.347 | -0.11902 | -0.14648 | 62.9883 | -60.0723 | 63.0112 | -60.1181 | -60.2097 | -59.9716 | -0.17853 | -0.022889 | -0.082398 | 0.027466 | 59.8984 | -0.32959 | 60.0769 | -0.15106 | -0.054932 | -0.009156 | 0.013732 | -0.10071 | 0.045776 | -0.19226 | 0.10071 | -0.13733 | 0.20599 | 123.111 | -0.045776 | 123.0835 | 123.1705 | 123.0606 | 122.9919 | 123.0057 | -123.1934 | -123.0698 | 122.9324 | 123.0286 | 59.9167 | 59.8709
162.3281 | 123.2941 | -60.0037 | 62.9379 | -0.060501 | 0.0026339 | 0.065277 | 0.073745 | 0.0016427 | 0.0013843 | 0.0017837 | -0.039429 | -0.00054897 | 0.063215 | 0.060611 | -0.0032172 | 0.0010661 | 0.0028519 | -0.032043 | 62.9425 | -60.1776 | 63.0112 | -59.8526 | -60.2463 | -0.018311 | -0.013733 | 62.9425 | -60.0357 | 63.1073 | -59.9899 | -60.0906 | -59.8846 | -0.17395 | 0.004578 | 0.073242 | 0.15106 | 59.9854 | -0.24262 | 60.1593 | -0.068665 | -0.032044 | 0.004578 | 0.16937 | 0.013733 | 0.11902 | -0.086975 | 0.15106 | -0.054931 | 0.32501 | 123.1888 | 0.045777 | 123.143 | 123.1201 | 122.9782 | 122.9462 | 122.9462 | -123.1155 | -122.9736 | 123.0148 | 123.111 | 59.9716 | 59.9899
163.3438 | 123.3032 | -60.0037 | 63.0066 | -0.037613 | 7.0518e-05 | 0.064422 | 0.074386 | -0.0019889 | -0.0018201 | -0.0052659 | -0.045532 | 0.0013736 | 0.06407 | 0.060825 | -0.0034308 | 0.00063867 | -0.00035245 | 0.045776 | 63.002 | -60.1318 | 63.2401 | -60.1181 | -60.2005 | 0.1236 | 0.13733 | 62.9242 | -60.0357 | 63.1531 | -59.9167 | -60.0128 | -59.8343 | -0.12817 | -0.004578 | 0.23346 | -0.11444 | 60.1273 | -0.19684 | 60.2554 | -0.068664 | -0.032044 | -0.082398 | 0.14648 | 0.086975 | 0.16937 | -0.009155 | 0.20142 | 0.022889 | 0.013733 | 123.3719 | 0.11902 | 123.1888 | 123.1338 | 122.9599 | 123.0057 | 122.9279 | -123.1384 | -123.0423 | 123.2437 | 123.1567 | 60.0494 | 60.141
164.3281 | 123.3032 | -59.9991 | 62.9837 | -0.15968 | 0.0034885 | 0.065918 | 0.073531 | -0.00049353 | 0.0015979 | 0.00028833 | -0.027222 | -0.00076257 | 0.063429 | 0.057407 | -0.0019354 | 0.0021341 | -0.0022751 | -0.036621 | 62.9242 | -60.173 | 63.0157 | -59.8526 | -60.2371 | -0.022888 | -0.041199 | 62.9059 | -60.0449 | 63.0798 | -60.022 | -60.1044 | -59.8892 | -0.17395 | -0.05951 | 0.032043 | 0.14648 | 59.9762 | -0.23804 | 60.1501 | -0.064087 | -0.045777 | -0.07782 | 0.09613 | -0.022889 | 0.10986 | -0.10529 | 0.15564 | -0.059509 | 0.32043 | 123.1888 | 0.022888 | 123.1247 | 123.0972 | 122.9507 | 122.9233 | 122.905 | -123.1567 | -123.0286 | 123.0148 | 123.0789 | 59.9625 | 59.9579
165.3281 | 123.2712 | -60.0082 | 62.9837 | -0.12917 | 0.00071132 | 0.06485 | 0.077163 | 0.0031381 | 0.0015979 | 0.00092933 | -0.07605 | 0.0013736 | 0.062575 | 0.070011 | -0.0030036 | 0.00042507 | 0.0032791 | -0.082397 | 62.9562 | -60.1868 | 62.9608 | -59.9304 | -60.2921 | -0.07782 | -0.086975 | 62.9471 | -60.0586 | 63.0936 | -59.9899 | -60.1501 | -59.903 | -0.17853 | -0.027466 | -0.022889 | 0.07782 | 59.9304 | -0.28381 | 60.1089 | -0.10529 | -0.050354 | -0.036621 | 0.10986 | 0.018311 | 0.10529 | -0.14191 | 0.15564 | -0.091552 | 0.25635 | 123.1476 | 0.068665 | 123.1522 | 123.143 | 123.0057 | 122.9645 | 122.9553 | -123.1705 | -123.0423 | 122.9691 | 123.1018 | 59.9258 | 59.9213
166.3281 | 123.2712 | -60.0082 | 62.9654 | -0.11391 | 0.00049772 | 0.063781 | 0.076949 | -0.00049353 | 0.0013843 | -0.0018479 | -0.033325 | 0.00030543 | 0.063643 | 0.058689 | -0.0034308 | 0.00085247 | -0.00013885 | -0.041199 | 62.9379 | -60.1593 | 62.9974 | -59.8709 | -60.26 | -0.045776 | -0.050354 | 62.9196 | -60.0494 | 63.0661 | -60.0174 | -60.1181 | -59.903 | -0.15106 | -0.027466 | 0.032044 | 0.13733 | 59.9625 | -0.25177 | 60.1135 | -0.10071 | -0.041198 | -0.045776 | 0.10071 | -0.009155 | 0.10529 | -0.10986 | 0.14648 | -0.068665 | 0.28839 | 123.1567 | 0.032043 | 123.1155 | 123.0972 | 122.9691 | 122.9462 | 122.9279 | -123.1247 | -123.0148 | 123.0057 | 123.0743 | 59.967 | 59.9579
167.3281 | 123.2712 | -60.0311 | 62.97 | -0.037613 | 0.00071132 | 0.063354 | 0.074172 | -0.00027993 | -0.0022473 | -0.00099327 | -0.07605 | 0.0018008 | 0.062788 | 0.064243 | -0.00279 | 0.0027751 | 0.00028835 | -0.10071 | 62.9929 | -60.2005 | 62.9196 | -59.9762 | -60.3287 | -0.11444 | -0.15106 | 62.9517 | -60.0815 | 63.0569 | -60.0861 | -60.1868 | -59.935 | -0.16937 | 0.022888 | -0.050354 | 0.054932 | 59.9167 | -0.29755 | 60.0861 | -0.12817 | -0.050354 | -0.018311 | 0.086975 | -0.054932 | 0.09613 | -0.15564 | 0.14648 | -0.10529 | 0.2243 | 123.1201 | -0.004578 | 123.1384 | 123.1934 | 123.0331 | 123.024 | 122.9828 | -123.1705 | -123.0515 | 122.9507 | 123.0881 | 59.9304 | 59.8801
168.3438 | 123.1842 | -60.0082 | 63.0249 | -0.06813 | 0.0022067 | 0.066131 | 0.074813 | -0.0015615 | -0.0016065 | 7.4734e-05 | -0.0089111 | 0.00030543 | 0.062575 | 0.061038 | -0.0019354 | 0.00063867 | 0.0024245 | 0.045776 | 63.0066 | -60.1318 | 63.0295 | -59.8526 | -60.1868 | 0.091553 | 0.091553 | 62.9837 | -60.0082 | 63.0569 | -59.9991 | -60.1181 | -59.9121 | -0.1236 | -0.01831 | 0.004578 | 0.15564 | 60.0998 | -0.17853 | 60.2234 | -0.054932 | 0 | -0.041198 | 0.032044 | 0.009156 | 0.096131 | -0.10986 | 0.096131 | -0.10986 | 0.27924 | 123.1613 | 0.009156 | 123.0652 | 123.1384 | 122.9919 | 123.0148 | 122.9919 | -123.1567 | -123.0331 | 123.0377 | 123.0652 | 60.054 | 60.0998
169.3281 | 123.1934 | -60.0403 | 63.0249 | -0.091019 | 7.0518e-05 | 0.066131 | 0.076308 | 0.00036107 | -0.0035291 | -0.0012071 | -0.07605 | 0.00030543 | 0.063856 | 0.05933 | -0.0015082 | 0.0076883 | 0.0015701 | -0.068665 | 63.002 | -60.1913 | 62.883 | -60.0128 | -60.3607 | -0.1236 | -0.18768 | 62.97 | -60.0723 | 62.7823 | -59.816 | -60.1913 | -59.9808 | -0.15106 | -0.022888 | -0.14191 | 0.027466 | 59.9167 | -0.32043 | 60.0677 | -0.16937 | -0.032044 | -0.054931 | -0.24261 | 0.2243 | 0.059509 | -0.15106 | 0.091553 | -0.11902 | 0.17853 | 123.0743 | 0.25635 | 122.8546 | 123.1934 | 123.0423 | 123.0423 | 123.0103 | -123.2162 | -123.0972 | 122.9233 | 122.8226 | 59.9716 | 59.8526
170.3281 | 123.2941 | -60.0174 | 62.9517 | -0.1368 | -0.00057028 | 0.066131 | 0.074386 | -0.00049353 | 0.00031608 | -0.0014207 | -0.0089111 | 0.00073263 | 0.064283 | 0.065952 | -0.00279 | 0.0010661 | -0.0012071 | -0.041199 | 62.9379 | -60.1593 | 63.0112 | -59.8343 | -60.2325 | -0.022888 | -0.022888 | 62.915 | -60.0174 | 63.1165 | -59.9854 | -60.1044 | -59.8846 | -0.14191 | -0.013733 | 0.059509 | 0.1831 | 59.9945 | -0.21515 | 60.1364 | -0.073242 | 0 | -0.036621 | 0.1648 | 0.032043 | 0.13275 | -0.086975 | 0.13275 | -0.086975 | 0.32501 | 123.1705 | 0.032043 | 123.1338 | 123.0972 | 122.9324 | 122.9553 | 122.9324 | -123.111 | -122.9691 | 123.0286 | 123.1338 | 59.9762 | 59.9945
171.3281 | 123.2071 | -60.0128 | 62.9791 | -0.091019 | 0.0011385 | 0.063354 | 0.07524 | 0.00078827 | -0.00011112 | 0.00028833 | -0.079102 | 0.00116 | 0.065779 | 0.065738 | -0.0019354 | 0.0021341 | 0.0015701 | -0.10071 | 62.9837 | -60.1868 | 62.9105 | -59.9762 | -60.3378 | -0.12817 | -0.14648 | 62.9562 | -60.0861 | 63.0386 | -60.0769 | -60.1639 | -59.9396 | -0.17395 | 0.004578 | -0.068665 | 0.036621 | 59.8846 | -0.32501 | 60.0586 | -0.15106 | -0.073243 | -0.022888 | 0.059509 | -0.064087 | 0.073242 | -0.15106 | 0.14649 | -0.077819 | 0.21057 | 123.0972 | 0.009156 | 123.1247 | 123.1705 | 123.0423 | 122.9965 | 122.9691 | -123.1659 | -123.0652 | 122.9233 | 123.0515 | 59.9121 | 59.8663
172.3281 | 123.3261 | -59.9899 | 62.9333 | -0.11391 | 0.0011385 | 0.065704 | 0.073531 | -0.0011343 | 0.0028797 | 0.00028833 | -0.045532 | 9.1834e-05 | 0.063856 | 0.065738 | -0.0042854 | 0.0042703 | -0.0050523 | -0.027466 | 62.9288 | -60.1776 | 63.0844 | -59.697 | -60.1868 | -0.036621 | -0.045776 | 62.9333 | -60.0174 | 63.1165 | -59.9808 | -60.1044 | -59.8709 | -0.18768 | -0.004578 | 0.15106 | 0.29297 | 59.9533 | -0.19684 | 60.141 | -0.009156 | -0.027466 | 0 | 0.18311 | 0.009155 | 0.11902 | -0.11444 | 0.14648 | -0.086975 | 0.48065 | 123.262 | 0.036621 | 123.1338 | 123.1064 | 122.9507 | 122.9187 | 122.9233 | -123.111 | -122.9507 | 123.0743 | 123.1064 | 59.9625 | 59.9442
173.3281 | 123.3398 | -59.9808 | 62.9654 | -0.029984 | 0.00049772 | 0.063781 | 0.073745 | -0.0045523 | -0.0022473 | -0.0024887 | 0.024658 | 0.00094643 | 0.06407 | 0.06232 | -0.003858 | 0.00085247 | -0.00077965 | 0.004578 | 62.9929 | -60.1227 | 63.0249 | -59.8251 | -60.1685 | 0.07782 | 0.07782 | 62.9333 | -60.0037 | 63.1393 | -59.9579 | -60.0266 | -59.8251 | -0.14191 | 0.027466 | 0.059509 | 0.15564 | 60.0586 | -0.18768 | 60.2005 | -0.045776 | -0.022888 | -0.032043 | 0.17395 | 0.022888 | 0.15564 | -0.045776 | 0.17853 | -0.022888 | 0.29755 | 123.1476 | 0.045776 | 123.143 | 123.1155 | 122.937 | 122.9736 | 122.9141 | -123.0881 | -122.9691 | 123.0057 | 123.1201 | 59.9854 | 60.0586
174.3281 | 123.317 | -60.0174 | 62.9608 | -0.07576 | 0.00049772 | 0.065063 | 0.073959 | 0.00036107 | 0.00031608 | 0.00028833 | -0.02417 | 9.1834e-05 | 0.064497 | 0.063602 | -0.0042854 | 0.0017069 | -0.00013885 | -0.041199 | 62.9425 | -60.141 | 63.0386 | -59.8343 | -60.228 | -0.022888 | -0.032043 | 62.9288 | -60.0357 | 63.1073 | -60.0037 | -60.0861 | -59.8801 | -0.1236 | -0.01831 | 0.07782 | 0.1831 | 59.9945 | -0.21057 | 60.1181 | -0.086975 | -0.018311 | -0.032043 | 0.14649 | 0.013733 | 0.13733 | -0.068665 | 0.15564 | -0.050354 | 0.3067 | 123.1796 | 0.032044 | 123.143 | 123.0835 | 122.9645 | 122.9599 | 122.9462 | -123.1018 | -122.9965 | 123.056 | 123.1247 | 59.9762 | 59.9854
175.3281 | 123.1476 | -60.0403 | 63.0066 | -0.083389 | 0.0015659 | 0.067413 | 0.078231 | 0.0029245 | 0.00052988 | -0.00099327 | -0.09436 | 0.0015872 | 0.063643 | 0.069583 | -0.0030036 | 0.00063867 | -0.0016343 | -0.059509 | 62.9791 | -60.1913 | 62.9105 | -59.9762 | -60.3287 | -0.091553 | -0.14648 | 62.9883 | -60.0494 | 62.9791 | -60.1227 | -60.2417 | -59.9899 | -0.15106 | -0.027466 | -0.096131 | 0.064087 | 59.9487 | -0.28839 | 60.0998 | -0.13733 | -0.009155 | -0.018311 | -0.027466 | -0.082398 | 0.050354 | -0.20142 | 0.059509 | -0.19226 | 0.21515 | 123.1018 | -0.073243 | 123.0286 | 123.1705 | 123.0377 | 123.0194 | 123.0286 | -123.1979 | -123.056 | 122.9507 | 123.0194 | 59.9808 | 59.8938
176.3281 | 123.2529 | -60.022 | 62.9837 | -0.06813 | 0.0013523 | 0.063781 | 0.074386 | 0.00078827 | -0.0024609 | 0.00028833 | -0.057739 | 0.0024416 | 0.063643 | 0.062534 | -0.00086737 | 0.0042703 | -0.0012071 | -0.10071 | 62.9974 | -60.2005 | 62.8922 | -59.9945 | -60.3424 | -0.10986 | -0.15564 | 62.9471 | -60.0586 | 63.0112 | -60.0906 | -60.2051 | -59.9625 | -0.17853 | 0.013733 | -0.091553 | 0.027466 | 59.9121 | -0.32043 | 60.0906 | -0.14191 | -0.036621 | -0.036621 | 0.027465 | -0.068664 | 0.05951 | -0.1831 | 0.096131 | -0.14648 | 0.20599 | 123.0927 | -0.032043 | 123.0698 | 123.1979 | 123.0057 | 123.0194 | 122.9691 | -123.1842 | -123.0423 | 122.9141 | 123.0331 | 59.9213 | 59.8663
177.3281 | 123.2162 | -60.0449 | 62.9837 | -0.022354 | 0.0022067 | 0.064209 | 0.076736 | 0.0029245 | 0.00052988 | -0.0018479 | -0.082153 | 0.0032962 | 0.063215 | 0.062747 | -0.0015082 | 0.0036295 | -0.0054795 | -0.10529 | 62.9883 | -60.2097 | 62.9013 | -59.9945 | -60.3561 | -0.11902 | -0.16479 | 62.9654 | -60.054 | 63.0157 | -60.1135 | -60.2188 | -59.9625 | -0.1648 | 0.004577 | -0.082398 | 0.050354 | 59.9258 | -0.31128 | 60.0906 | -0.14648 | -0.009155 | -0.018311 | 0.032043 | -0.068664 | 0.082398 | -0.17395 | 0.091553 | -0.1648 | 0.21515 | 123.111 | -0.059509 | 123.0698 | 123.1979 | 123.0194 | 123.0331 | 123.0103 | -123.1934 | -123.0377 | 122.9462 | 123.0606 | 59.9396 | 59.8801
178.3438 | 123.3215 | -59.9762 | 62.9791 | -0.12154 | 0.00028412 | 0.063141 | 0.074172 | -0.0036977 | -0.00075192 | 0.00028833 | 0.033813 | 0.00051903 | 0.065992 | 0.06232 | -0.0042854 | 0.00021147 | -0.0022751 | 0.009155 | 63.002 | -60.1227 | 63.0386 | -59.8114 | -60.1776 | 0.073242 | 0.091553 | 62.9379 | -60.0128 | 63.1577 | -59.9258 | -60.0082 | -59.8389 | -0.14648 | 0.022888 | 0.059509 | 0.1648 | 60.0494 | -0.20142 | 60.1959 | -0.054931 | -0.036621 | -0.041199 | 0.17853 | 0.050354 | 0.13733 | -0.032044 | 0.17395 | 0.004577 | 0.31128 | 123.1613 | 0.086975 | 123.1705 | 123.1247 | 122.9507 | 122.9782 | 122.9141 | -123.1018 | -122.9919 | 123.0148 | 123.1338 | 59.9854 | 60.0677
179.3281 | 123.2162 | -60.022 | 63.0203 | -0.07576 | -0.0024929 | 0.066345 | 0.074172 | -0.0011343 | -0.0026745 | -0.00077967 | -0.069946 | 0.00051903 | 0.063643 | 0.063602 | -0.0032172 | 0.0036295 | 0.0034927 | -0.32959 | 62.8967 | -60.2371 | 62.8967 | -59.967 | -60.347 | -0.12817 | -0.15564 | 62.9791 | -60.0677 | 63.0157 | -60.1318 | -60.2234 | -59.9533 | -0.21515 | -0.1236 | -0.1236 | 0.054932 | 59.8938 | -0.32501 | 60.1089 | -0.10986 | -0.045776 | -0.041199 | -0.004578 | -0.10986 | 0.068665 | -0.20142 | 0.11444 | -0.15564 | 0.27008 | 123.1339 | -0.064087 | 123.0835 | 123.1339 | 123.0469 | 122.9187 | 123.0011 | -123.2574 | -123.0881 | 122.9187 | 123.0377 | 59.6924 | 59.8663
180.3281 | 123.2895 | -59.9899 | 62.9608 | -0.12154 | 7.0518e-05 | 0.063354 | 0.073745 | -0.0026297 | -0.0013929 | 0.00050193 | -0.054688 | 0.00073263 | 0.06407 | 0.063175 | -0.00279 | 0.0014933 | 0.0013565 | -0.091553 | 62.9562 | -60.2097 | 62.9791 | -59.8938 | -60.2554 | -0.041199 | -0.09613 | 62.9288 | -60.0449 | 63.1119 | -60.022 | -60.1044 | -59.8709 | -0.21973 | -0.004577 | 0.018311 | 0.09613 | 59.9487 | -0.2655 | 60.1685 | -0.045776 | -0.054932 | -0.032043 | 0.15106 | -0.032044 | 0.11902 | -0.11444 | 0.17395 | -0.059509 | 0.31586 | 123.1888 | 0.022888 | 123.1567 | 123.1659 | 122.9736 | 122.9462 | 122.9187 | -123.1705 | -123.0057 | 122.9691 | 123.1018 | 59.8984 | 59.8938
181.3281 | 123.1842 | -60.0266 | 63.0066 | -0.060501 | 0.0024203 | 0.065063 | 0.076095 | -0.00027993 | 0.00031608 | 0.0015701 | -0.09436 | 0.0047916 | 0.064711 | 0.059543 | -0.003858 | 0.0032023 | -0.00013885 | -0.09613 | 62.9791 | -60.2142 | 62.883 | -60.0357 | -60.3973 | -0.12817 | -0.47607 | 62.8784 | -60.1044 | 63.0112 | -60.1273 | -60.2188 | -59.9899 | -0.18768 | -0.027466 | -0.1236 | -0.009156 | 59.8984 | -0.37079 | 60.0861 | -0.18311 | -0.07782 | -0.12817 | 0.004577 | -0.10071 | 0.036621 | -0.19226 | 0.11444 | -0.11444 | 0.17853 | 123.0972 | -0.022888 | 123.1155 | 123.1934 | 122.9828 | 123.0057 | 122.905 | -123.2208 | -123.111 | 122.9095 | 123.0377 | 59.9304 | 59.5505
182.3281 | 123.2071 | -60.0357 | 62.9974 | -0.12917 | 0.00028412 | 0.062713 | 0.074599 | 0.0012155 | 0.0013843 | 0.0017837 | -0.069946 | 0.00116 | 0.064497 | 0.058048 | -0.0017218 | 0.00063867 | -0.0031297 | -0.10071 | 63.0066 | -60.2188 | 62.9059 | -60.0037 | -60.3424 | -0.10986 | -0.17395 | 62.9562 | -60.0815 | 63.0066 | -60.1089 | -60.2051 | -59.967 | -0.18311 | 0.009155 | -0.091553 | 0.032044 | 59.9258 | -0.3067 | 60.1089 | -0.1236 | -0.045776 | -0.041199 | 0.009155 | -0.073242 | 0.068665 | -0.16937 | 0.11444 | -0.1236 | 0.21515 | 123.1247 | -0.027466 | 123.0881 | 123.2254 | 123.0377 | 123.0423 | 122.9919 | -123.2162 | -123.0789 | 122.9416 | 123.0423 | 59.935 | 59.8618
183.3438 | 123.2803 | -60.0128 | 62.9562 | -0.098648 | 0.00028412 | 0.065277 | 0.073959 | -0.0011343 | -0.00096552 | -0.00077967 | 0.018555 | -0.00054897 | 0.064711 | 0.063602 | -0.0015082 | 0.0010661 | -0.00077965 | -0.068665 | 62.9562 | -60.1822 | 62.9974 | -59.8618 | -60.2737 | -0.032043 | -0.064087 | 62.915 | -60.0494 | 63.0615 | -60.0266 | -60.1273 | -59.8984 | -0.16937 | 0 | 0.041199 | 0.15106 | 59.9808 | -0.26093 | 60.1501 | -0.091553 | -0.036621 | -0.041199 | 0.10529 | -0.013733 | 0.11444 | -0.11444 | 0.15106 | -0.07782 | 0.32043 | 123.1796 | 0.022888 | 123.111 | 123.1384 | 122.9645 | 122.9691 | 122.9279 | -123.1384 | -123.0057 | 123.0103 | 123.0743 | 59.9442 | 59.9487
184.3281 | 123.3902 | -60.0266 | 62.9562 | -0.11391 | 0.00092492 | 0.063781 | 0.076095 | 0.0014291 | 0.00095708 | 0.00092933 | -0.033325 | 0.00051903 | 0.063643 | 0.064243 | -0.0042854 | 0.0040567 | -0.0018479 | -0.054932 | 62.9745 | -60.173 | 63.0066 | -59.8618 | -60.2509 | -0.032043 | -0.045776 | 62.9288 | -60.0082 | 63.1027 | -60.0082 | -60.379 | -59.9579 | -0.14648 | 0.01831 | 0.050354 | 0.16479 | 59.9945 | -0.2243 | 60.141 | -0.077819 | 0.01831 | -0.027466 | 0.14648 | 0.01831 | 0.068664 | -0.35248 | 0.050354 | -0.37079 | 0.31128 | 123.1796 | 0 | 123.111 | 123.1476 | 122.937 | 123.0011 | 122.9553 | -123.1293 | -122.9645 | 123.0331 | 123.1293 | 59.9716 | 59.9808
185.3281 | 123.2071 | -60.0449 | 62.9883 | -0.045242 | 0.0019931 | 0.065063 | 0.075454 | -0.0024161 | 0.0015979 | -0.00013887 | -0.057739 | 0.0037234 | 0.065138 | 0.060184 | -0.002149 | 0.0032023 | 0.0013565 | -0.10529 | 62.9883 | -60.2188 | 62.8693 | -59.903 | -60.3378 | -0.10986 | -0.17853 | 62.9745 | -60.0632 | 63.002 | -60.1181 | -60.2463 | -59.9808 | -0.17395 | 0 | -0.11902 | 0.14191 | 59.935 | -0.29297 | 60.1089 | -0.11902 | -0.01831 | -0.013733 | 0.013733 | -0.073242 | 0.064087 | -0.20142 | 0.082397 | -0.18311 | 0.31586 | 123.0881 | -0.054932 | 123.0652 | 123.2071 | 123.0377 | 123.0331 | 123.0194 | -123.2071 | -123.0515 | 122.9141 | 123.0469 | 59.9396 | 59.8663
186.3281 | 123.3215 | -59.9991 | 62.9517 | -0.07576 | -0.00099768 | 0.065918 | 0.075667 | 0.00036107 | -0.00032472 | -0.00099327 | -0.054688 | 0.00030543 | 0.064497 | 0.062961 | -0.0025764 | 0.0029887 | -0.0029159 | -0.086975 | 62.97 | -60.1913 | 62.9745 | -59.903 | -60.2692 | -0.054932 | -0.082397 | 62.9105 | -60.0494 | 63.0981 | -60.0128 | -60.1089 | -59.8755 | -0.19226 | 0.018311 | 0.022888 | 0.09613 | 59.9442 | -0.27008 | 60.1364 | -0.07782 | -0.050354 | -0.041199 | 0.14649 | -0.013733 | 0.1236 | -0.10986 | 0.17395 | -0.05951 | 0.28839 | 123.1659 | 0.036621 | 123.1476 | 123.1613 | 122.9599 | 122.9691 | 122.9095 | -123.143 | -123.0011 | 122.9736 | 123.0972 | 59.9121 | 59.9167
187.3281 | 123.2025 | -60.0403 | 63.002 | -0.083389 | 0.0019931 | 0.063354 | 0.075667 | 0.0024973 | -0.00053832 | 0.0028519 | -0.2561 | 0.0015872 | 0.061934 | 0.061038 | -0.0019354 | 0.0010661 | 0.0013565 | -0.091553 | 63.002 | -60.2234 | 62.8693 | -60.0174 | -60.3745 | -0.12817 | 0.054932 | 62.9562 | -60.0403 | 63.002 | -60.1135 | -60.26 | -59.9716 | -0.18311 | 0 | -0.13275 | 0.022888 | 59.9121 | -0.33417 | 60.0952 | -0.15106 | 0 | -0.045776 | 0 | -0.073242 | 0.068664 | -0.21973 | 0.068664 | -0.21973 | 0.20599 | 123.0927 | -0.073242 | 123.0423 | 123.2254 | 122.9965 | 123.0423 | 122.9965 | -123.2254 | -123.0423 | 122.9095 | 123.0423 | 59.9487 | 60.0952
188.3281 | 123.2986 | -59.9854 | 62.9471 | -0.12917 | 0.0054111 | 0.06485 | 0.072463 | 0.00014747 | 0.00010248 | -0.00056607 | -0.027222 | 9.1834e-05 | 0.065138 | 0.064029 | -0.0012946 | 0.0014933 | -0.00099325 | -0.082397 | 62.9745 | -60.1959 | 62.9517 | -59.9258 | -60.3058 | -0.07782 | -0.10529 | 62.9288 | -60.054 | 63.089 | -60.0494 | -60.1044 | -59.8618 | -0.21057 | 0.027465 | 0.004577 | 0.05951 | 59.9075 | -0.32043 | 60.1181 | -0.10986 | -0.068664 | -0.018311 | 0.14191 | -0.064086 | 0.1236 | -0.11902 | 0.19226 | -0.050354 | 0.27008 | 123.1476 | 0.004578 | 123.143 | 123.1705 | 122.9828 | 122.9599 | 122.9141 | -123.143 | -123.0011 | 122.937 | 123.0743 | 59.903 | 59.8801
189.3281 | 123.2025 | -60.0357 | 63.002 | -0.083389 | 0.0017795 | 0.065918 | 0.076095 | 0.0059153 | 0.0026661 | -0.0016343 | -0.063843 | 0.0018008 | 0.064283 | 0.067447 | -0.0040716 | 0.0025613 | -0.0018479 | -0.041199 | 62.9745 | -60.1913 | 62.9333 | -59.9396 | -60.3104 | -0.064087 | -0.082397 | 62.9562 | -60.0815 | 63.0112 | -60.1044 | -60.2051 | -59.967 | -0.15564 | -0.027466 | -0.068664 | 0.096131 | 59.9716 | -0.27466 | 60.1273 | -0.11902 | -0.045776 | -0.045776 | 0.009155 | -0.068664 | 0.068665 | -0.16937 | 0.11444 | -0.1236 | 0.25177 | 123.1247 | -0.022888 | 123.0927 | 123.1659 | 123.0377 | 123.0103 | 122.9919 | -123.1934 | -123.0835 | 122.9691 | 123.0469 | 59.9945 | 59.9533
190.3281 | 123.2162 | -60.022 | 62.9745 | -0.07576 | 0.0017795 | 0.064209 | 0.074386 | 0.0035653 | 0.0015979 | -0.0012071 | -0.048584 | 0.00030543 | 0.065138 | 0.056339 | -0.0025764 | 0.0025613 | -0.0012071 | -0.091553 | 63.0112 | -60.2005 | 62.9059 | -59.9899 | -60.3516 | -0.11902 | -0.1831 | 62.9471 | -60.0449 | 63.0066 | -60.1273 | -60.2051 | -59.967 | -0.17853 | 0.036621 | -0.068664 | 0.032044 | 59.903 | -0.32959 | 60.0815 | -0.15106 | -0.022888 | -0.027465 | 0.032044 | -0.10528 | 0.054932 | -0.1831 | 0.07782 | -0.16022 | 0.21057 | 123.1064 | -0.082397 | 123.0515 | 123.2117 | 122.9919 | 123.0331 | 122.9691 | -123.175 | -123.0194 | 122.9279 | 123.0286 | 59.9304 | 59.8389
191.3281 | 123.2254 | -60.0449 | 62.9929 | -0.11391 | 0.0019931 | 0.065277 | 0.076308 | 0.0014291 | -0.00053832 | 0.00050193 | -0.051636 | 0.0030826 | 0.063429 | 0.064243 | -0.0030036 | 0.0021341 | 0.0022109 | -0.091553 | 63.002 | -60.1913 | 62.883 | -59.9899 | -60.3424 | -0.11444 | -0.17853 | 62.9745 | -60.0403 | 63.0066 | -60.1181 | -60.228 | -59.9625 | -0.14648 | 0.009155 | -0.10986 | 0.054932 | 59.9304 | -0.29755 | 60.0769 | -0.15106 | 0.004578 | -0.018311 | 0.013733 | -0.073242 | 0.082398 | -0.18311 | 0.07782 | -0.18768 | 0.20142 | 123.0743 | -0.07782 | 123.0469 | 123.1934 | 123.0148 | 123.0469 | 123.0194 | -123.1842 | -123.0331 | 122.9279 | 123.0515 | 59.9533 | 59.8663
192.3281 | 123.3032 | -59.9854 | 62.9883 | -0.10628 | 0.00071132 | 0.066559 | 0.074813 | 0.0027109 | -0.00053832 | -0.0027023 | -0.042481 | -0.00076257 | 0.063643 | 0.064884 | -0.0040716 | 0.0014933 | 0.00071555 | -0.064087 | 62.9562 | -60.1593 | 62.9883 | -59.8572 | -60.2463 | -0.022888 | -0.045776 | 62.8876 | -60.0494 | 63.1897 | -60.0449 | -60.0403 | -59.8572 | -0.17395 | -0.032043 | 0 | 0.12817 | 59.9625 | -0.26093 | 60.1364 | -0.086975 | -0.064086 | -0.10071 | 0.20142 | -0.059509 | 0.12817 | -0.054931 | 0.19226 | 0.009155 | 0.30212 | 123.1476 | 0.004577 | 123.2391 | 123.1155 | 122.937 | 122.9416 | 122.8729 | -123.1476 | -123.0377 | 122.9736 | 123.175 | 59.9213 | 59.9396
193.3281 | 123.1979 | -60.0357 | 62.9883 | 0.1226 | -0.00057028 | 0.066559 | 0.075454 | 0.0014291 | -0.0018201 | -0.00013887 | -0.051636 | 0.00051903 | 0.063002 | 0.066165 | -1.2774e-05 | -0.00021573 | -0.00056605 | -0.15564 | 62.9837 | -60.2097 | 62.883 | -59.9991 | -60.3516 | -0.10529 | -0.16022 | 62.9608 | -60.0586 | 63.0066 | -60.1227 | -60.228 | -59.967 | -0.17395 | -0.004577 | -0.10529 | 0.036622 | 59.9304 | -0.31586 | 60.1044 | -0.14191 | -0.022888 | -0.027466 | 0.018311 | -0.086975 | 0.068665 | -0.19226 | 0.091553 | -0.16937 | 0.21057 | 123.0927 | -0.064087 | 123.0652 | 123.1934 | 123.0194 | 123.0194 | 122.9965 | -123.1979 | -123.0469 | 122.9187 | 123.0423 | 59.8801 | 59.8755
194.3281 | 123.2437 | -60.0449 | 62.9196 | -0.083389 | 0.00092492 | 0.06485 | 0.074813 | 0.0012155 | -0.00032472 | 0.00092933 | -0.030273 | -0.00033537 | 0.067061 | 0.063175 | -0.0025764 | 0.0029887 | -0.00077965 | -0.036621 | 62.9517 | -60.1822 | 62.9883 | -59.8572 | -60.2509 | -0.041199 | -0.041199 | 62.9013 | -60.0403 | 63.1027 | -60.0037 | -60.0769 | -59.8892 | -0.13733 | 0.032043 | 0.068664 | 0.18768 | 60.0037 | -0.20599 | 60.141 | -0.068664 | 0.004578 | -0.018311 | 0.1831 | 0.041199 | 0.15564 | -0.032043 | 0.15106 | -0.036621 | 0.32501 | 123.1705 | 0.036621 | 123.143 | 123.1338 | 122.9416 | 122.9965 | 122.9462 | -123.1018 | -122.9599 | 123.0331 | 123.1476 | 60.0082 | 60.0037
195.3281 | 123.1934 | -60.0357 | 63.0112 | -0.11391 | 0.0013523 | 0.06485 | 0.073959 | -0.0011343 | 0.0041613 | 7.4734e-05 | -0.048584 | 0.002228 | 0.063856 | 0.060398 | -0.0032172 | 0.0040567 | -0.0022751 | -0.091553 | 62.9791 | -60.2325 | 62.8647 | -59.8846 | -60.3241 | -0.13275 | -0.17395 | 62.97 | -60.0723 | 62.9974 | -60.1318 | -60.2234 | -59.9625 | -0.19684 | -0.032043 | -0.14648 | 0.15106 | 59.903 | -0.28839 | 60.0998 | -0.091553 | -0.036621 | -0.041198 | -0.013732 | -0.09613 | 0.073243 | -0.18768 | 0.10986 | -0.15106 | 0.3479 | 123.0972 | -0.059509 | 123.0698 | 123.2117 | 123.0423 | 123.0148 | 123.0057 | -123.2437 | -123.0835 | 122.9004 | 123.0331 | 59.9442 | 59.8618
196.3281 | 123.262 | -60.0082 | 62.9608 | -0.091019 | 0.0013523 | 0.06549 | 0.076308 | 0.0022837 | -0.0013929 | -0.00056607 | -0.02417 | 0.002228 | 0.065138 | 0.058261 | -0.001081 | 0.0025613 | 7.4746e-05 | -0.10529 | 62.9974 | -60.2005 | 62.9013 | -59.9762 | -60.3378 | -0.11444 | -0.15564 | 62.9562 | -60.0815 | 63.0249 | -60.0906 | -60.1822 | -59.9258 | -0.19226 | 0.036622 | -0.059509 | 0.032044 | 59.8938 | -0.32959 | 60.0861 | -0.13733 | -0.073242 | -0.004577 | 0.064087 | -0.082397 | 0.082398 | -0.17395 | 0.15564 | -0.10071 | 0.2243 | 123.1018 | -0.009155 | 123.1064 | 123.1979 | 123.0377 | 123.0057 | 122.9645 | -123.1613 | -123.0423 | 122.9095 | 123.0331 | 59.903 | 59.8526
197.3281 | 123.2117 | -60.0311 | 62.9883 | -0.060501 | -0.00014308 | 0.063141 | 0.075667 | -0.0022025 | -0.0013929 | -0.00056607 | -0.051636 | 0.0024416 | 0.064283 | 0.064884 | -0.00279 | 0.0010661 | 0.00050195 | -0.10529 | 62.9883 | -60.1959 | 62.8876 | -59.9808 | -60.3516 | -0.10529 | -0.15564 | 62.9562 | -60.0769 | 63.0112 | -60.0861 | -60.2051 | -59.9533 | -0.16479 | 0 | -0.10071 | 0.050354 | 59.9258 | -0.32043 | 60.0906 | -0.15564 | -0.045776 | -0.032043 | 0.022888 | -0.054932 | 0.07782 | -0.17395 | 0.1236 | -0.12817 | 0.21515 | 123.0835 | -0.009156 | 123.0881 | 123.1842 | 123.0331 | 123.0194 | 122.9874 | -123.1842 | -123.0652 | 122.9187 | 123.0423 | 59.9258 | 59.8755
198.3281 | 123.262 | -59.9762 | 62.9288 | -0.07576 | 0.00092492 | 0.065918 | 0.074813 | 0.00036107 | -0.0013929 | -0.0027023 | 0.015503 | 0.0018008 | 0.063215 | 0.058689 | -0.0040716 | 0.0019205 | 0.0015701 | -0.045776 | 62.9333 | -60.1593 | 62.9974 | -59.848 | -60.2325 | -0.013733 | -0.013733 | 62.9013 | -60.0266 | 63.0844 | -60.0037 | -60.0998 | -59.8755 | -0.18311 | 0.004578 | 0.068665 | 0.12817 | 59.9625 | -0.25635 | 60.1456 | -0.073242 | -0.050354 | -0.027466 | 0.15564 | -0.027466 | 0.10071 | -0.1236 | 0.15106 | -0.073242 | 0.31128 | 123.1567 | 0.022888 | 123.111 | 123.0927 | 122.9279 | 122.9095 | 122.8775 | -123.0881 | -122.9553 | 122.9736 | 123.0606 | 59.9304 | 59.9625
199.3281 | 123.1979 | -60.0311 | 63.002 | -0.06813 | 0.00092492 | 0.065063 | 0.07524 | -0.00049353 | -0.00011112 | 0.00092933 | -0.060791 | 0.0015872 | 0.06407 | 0.068943 | -0.0025764 | 0.0023477 | -0.00035245 | -0.10529 | 62.9929 | -60.1868 | 62.883 | -59.9991 | -60.3333 | -0.11444 | -0.15106 | 62.9562 | -60.0586 | 63.002 | -60.1089 | -60.2097 | -59.967 | -0.15564 | -0.009155 | -0.11902 | 0.032044 | 59.9167 | -0.30212 | 60.0723 | -0.14648 | -0.027466 | -0.045776 | 0 | -0.07782 | 0.064087 | -0.17853 | 0.091553 | -0.15106 | 0.18768 | 123.0698 | -0.050354 | 123.0606 | 123.1796 | 123.0148 | 123.024 | 122.9874 | -123.1888 | -123.0606 | 122.9141 | 123.0331 | 59.9258 | 59.8801
200.3281 | 123.2986 | -59.9945 | 62.9745 | -0.060501 | 0.0022067 | 0.06485 | 0.075881 | 0.0035653 | -0.00011112 | 7.4734e-05 | -0.045532 | 0.0032962 | 0.063643 | 0.068302 | -0.00279 | 0.00042507 | -0.0022751 | -0.041199 | 62.9471 | -60.1776 | 63.0112 | -59.8709 | -60.228 | -0.027466 | -0.23346 | 62.8922 | -60.0494 | 63.1165 | -59.9808 | -60.0769 | -59.8206 | -0.18311 | -0.027465 | 0.036621 | 0.1236 | 59.967 | -0.23346 | 60.1501 | -0.050354 | -0.054931 | -0.082397 | 0.14191 | 0.013733 | 0.17395 | -0.082397 | 0.22888 | -0.027466 | 0.3067 | 123.1888 | 0.068664 | 123.1659 | 123.1247 | 122.9416 | 122.9416 | 122.8867 | -123.1522 | -123.024 | 123.0057 | 123.111 | 59.9533 | 59.761
201.3281 | 123.1934 | -60.0311 | 62.9929 | 0.015793 | 0.0019931 | 0.062927 | 0.075881 | 0.0010019 | 0.00074348 | 7.4734e-05 | -0.045532 | -0.00054897 | 0.063856 | 0.064029 | -0.0040716 | 0.0040567 | 0.0015701 | -0.10529 | 62.9745 | -60.1822 | 62.8876 | -60.0128 | -60.3516 | -0.10986 | -0.16022 | 62.9517 | -60.0449 | 63.002 | -60.1044 | -60.2325 | -59.9716 | -0.15106 | -0.018311 | -0.10529 | 0.018311 | 59.9213 | -0.32043 | 60.0723 | -0.16937 | -0.013733 | -0.041199 | 0.009155 | -0.073242 | 0.059509 | -0.20142 | 0.073242 | -0.18768 | 0.16937 | 123.0698 | -0.059509 | 123.0469 | 123.1567 | 122.9965 | 123.0057 | 122.9828 | -123.175 | -123.0377 | 122.9187 | 123.0331 | 59.9258 | 59.8709
202.3281 | 123.3948 | -59.9991 | 62.9517 | -0.083389 | 0.0011385 | 0.063781 | 0.073318 | -0.0039115 | -0.0013929 | 0.00071573 | -0.015015 | 0.00094643 | 0.065779 | 0.062961 | -0.0019354 | 0.0021341 | -0.0014207 | -0.064087 | 62.9471 | -60.1776 | 62.9883 | -59.8846 | -60.2554 | -0.050354 | -0.059509 | 62.9059 | -60.0449 | 63.2172 | -60.1501 | -60.2783 | -59.8114 | -0.17853 | -0.004577 | 0.036621 | 0.11444 | 59.9487 | -0.25635 | 60.1273 | -0.07782 | -0.045777 | -0.045776 | 0.2655 | -0.15106 | 0.18768 | -0.27924 | 0.23346 | -0.23346 | 0.29297 | 123.1659 | -0.10529 | 123.262 | 123.1247 | 122.9507 | 122.9462 | 122.905 | -123.1293 | -122.9965 | 122.9874 | 123.2162 | 59.935 | 59.9396
203.3281 | 123.175 | -60.0449 | 63.0112 | -0.11391 | 0.0013523 | 0.064209 | 0.075454 | -0.00027993 | -0.0024609 | 0.0015701 | -0.063843 | -0.0016172 | 0.064924 | 0.063602 | -0.0053534 | 0.0010661 | 0.0015701 | -0.07782 | 62.9837 | -60.1959 | 62.9196 | -59.9716 | -60.3378 | -0.07782 | -0.15564 | 62.9929 | -60.0494 | 62.9837 | -60.1273 | -60.228 | -59.9533 | -0.15106 | -0.027465 | -0.091552 | 0.073242 | 59.967 | -0.29297 | 60.1181 | -0.14191 | -0.004577 | -0.01831 | -0.027465 | -0.082397 | 0.091553 | -0.18311 | 0.09613 | -0.17853 | 0.2243 | 123.1155 | -0.07782 | 123.0331 | 123.1796 | 123.0423 | 123.0286 | 123.0377 | -123.2071 | -123.0606 | 122.9645 | 123.0286 | 59.967 | 59.8892
204.3281 | 123.3124 | -59.9945 | 62.9745 | -0.22072 | -0.00035668 | 0.063354 | 0.07524 | 0.0016427 | -0.0018201 | 0.00050193 | -0.0089111 | -0.00054897 | 0.063002 | 0.061679 | -0.0019354 | 0.0040567 | -0.0016343 | 0.10529 | 62.9745 | -60.1547 | 63.0203 | -59.8251 | -60.2463 | -0.045776 | -0.036621 | 62.9242 | -60.022 | 63.1165 | -59.9854 | -60.0998 | -59.8709 | -0.16022 | 0 | 0.045777 | 0.16937 | 59.9487 | -0.25177 | 60.1089 | -0.091553 | -0.027466 | -0.050354 | 0.14191 | 0.009155 | 0.1236 | -0.10529 | 0.15106 | -0.077819 | 0.32959 | 123.175 | 0.036621 | 123.1384 | 123.1293 | 122.9462 | 122.9691 | 122.9187 | -123.1293 | -122.9965 | 123.0148 | 123.111 | 60.0998 | 59.9579
205.3281 | 123.2391 | -60.0494 | 62.9883 | -0.098648 | -0.00035668 | 0.064636 | 0.076522 | -0.00070713 | -0.0020337 | -0.00013887 | -0.066895 | 0.0020144 | 0.066206 | 0.060611 | -0.0047126 | 0.0023477 | -0.0016343 | -0.09613 | 62.9883 | -60.1822 | 62.8967 | -59.9808 | -60.3424 | -0.10986 | -0.14648 | 62.9654 | -60.0586 | 63.0249 | -60.0861 | -60.1959 | -59.9533 | -0.13275 | 0 | -0.091552 | 0.068664 | 59.9396 | -0.29297 | 60.0723 | -0.16022 | -0.009156 | -0.022888 | 0.036621 | -0.036622 | 0.09613 | -0.14648 | 0.10529 | -0.13733 | 0.20142 | 123.0789 | -0.027466 | 123.0835 | 123.1705 | 123.024 | 123.0377 | 123.0148 | -123.1705 | -123.0469 | 122.9462 | 123.0743 | 59.9533 | 59.903
206.3281 | 123.2986 | -59.9808 | 62.9425 | -0.15968 | 0.00092492 | 0.064636 | 0.074599 | -0.0019889 | 0.0013843 | -0.0020615 | -0.02417 | -0.00097617 | 0.064497 | 0.056552 | -0.004499 | 0.0021341 | -0.0014207 | -0.036621 | 62.9288 | -60.1685 | 62.8143 | -59.8984 | -59.9121 | 0.009155 | -0.032043 | 62.915 | -60.0311 | 63.1027 | -59.9899 | -60.1089 | -59.8709 | -0.18768 | -0.013733 | -0.12817 | 0.082398 | 59.9899 | 0.068665 | 60.1776 | 0.25635 | -0.050354 | -0.027466 | 0.16022 | -0.009155 | 0.10986 | -0.12817 | 0.16022 | -0.07782 | 0.27008 | 122.9828 | 0.041199 | 123.1338 | 123.0972 | 122.9462 | 122.9095 | 122.8958 | -123.111 | -122.9736 | 122.7951 | 123.0835 | 59.9442 | 59.9487
207.3281 | 123.2025 | -60.0449 | 62.97 | -0.037613 | 0.0011385 | 0.064209 | 0.076308 | 0.0012155 | -0.0037427 | -0.0014207 | -0.054688 | 9.1834e-05 | 0.067701 | 0.063388 | -0.001081 | 0.0027751 | -0.00013885 | -0.091553 | 63.002 | -60.1959 | 62.8876 | -59.9991 | -60.3561 | -0.11902 | -0.15564 | 62.9517 | -60.054 | 63.0203 | -60.1227 | -60.2325 | -59.9762 | -0.15106 | 0.032043 | -0.082398 | 0.045777 | 59.9258 | -0.31128 | 60.0769 | -0.16022 | -0.009155 | -0.018311 | 0.050354 | -0.07782 | 0.068665 | -0.18768 | 0.07782 | -0.17853 | 0.19684 | 123.0835 | -0.068665 | 123.0743 | 123.1979 | 123.0057 | 123.0469 | 122.9965 | -123.1659 | -123.024 | 122.9324 | 123.0652 | 59.9533 | 59.8892
208.3281 | 123.3124 | -59.9945 | 62.9608 | -0.06813 | 0.0019931 | 0.065277 | 0.073959 | -0.00049353 | 0.00010248 | -0.00035247 | -0.02417 | 0.00094643 | 0.065138 | 0.067234 | -0.0040716 | -0.00085653 | -0.00077965 | -0.059509 | 62.9608 | -60.1685 | 63.002 | -59.8663 | -60.228 | -0.032043 | -0.054932 | 62.9105 | -60.0449 | 63.1851 | -60.0632 | -60.0403 | -59.848 | -0.17395 | 0 | 0.041199 | 0.12817 | 59.9625 | -0.23346 | 60.1364 | -0.059509 | -0.050354 | -0.050354 | 0.22431 | -0.068664 | 0.14648 | -0.045776 | 0.19684 | 0.004578 | 0.30212 | 123.1705 | -0.01831 | 123.23 | 123.1293 | 122.9553 | 122.9553 | 122.905 | -123.1293 | -123.0057 | 122.9965 | 123.1796 | 59.935 | 59.9396
209.3281 | 123.1888 | -60.0494 | 62.9791 | -0.19783 | 0.00071132 | 0.063141 | 0.075454 | 0.0024973 | -0.0013929 | -0.0018479 | -0.063843 | -0.00097617 | 0.064283 | 0.064884 | -0.00279 | 0.0051249 | -0.0035569 | 0.10529 | 62.9837 | -60.2051 | 62.9105 | -59.9854 | -60.3561 | -0.1236 | -0.17395 | 62.9562 | -60.0677 | 63.0112 | -60.1089 | -60.2325 | -59.9716 | -0.15564 | 0.004578 | -0.068665 | 0.064086 | 59.9258 | -0.3067 | 60.0815 | -0.15106 | -0.018311 | -0.022888 | 0.032043 | -0.05951 | 0.077819 | -0.18311 | 0.09613 | -0.16479 | 0.21973 | 123.1155 | -0.041199 | 123.0789 | 123.1888 | 123.024 | 123.0331 | 123.0057 | -123.1842 | -123.0469 | 122.9599 | 123.0606 | 60.1547 | 59.8755
210.3281 | 123.2208 | -60.0266 | 62.9837 | -0.06813 | 0.0011385 | 0.064422 | 0.07524 | 0.0037791 | -0.00053832 | -0.00035247 | -0.045532 | 0.00051903 | 0.064283 | 0.065311 | -0.0019354 | 0.0034159 | -0.0037705 | -0.10071 | 62.9883 | -60.1913 | 62.9013 | -59.9762 | -60.3424 | -0.11444 | -0.15564 | 62.9562 | -60.0449 | 63.0386 | -60.0815 | -60.1639 | -59.9442 | -0.16479 | 0.004577 | -0.082398 | 0.050354 | 59.9121 | -0.31586 | 60.0769 | -0.15106 | -0.018311 | -0.027466 | 0.054931 | -0.054932 | 0.082397 | -0.13733 | 0.10071 | -0.11902 | 0.21515 | 123.0927 | -0.036621 | 123.0835 | 123.1796 | 123.0011 | 123.0148 | 122.9828 | -123.175 | -123.0286 | 122.9279 | 123.0652 | 59.9258 | 59.8709
211.3281 | 123.2254 | -60.0357 | 62.9654 | -0.10628 | -0.0012113 | 0.065063 | 0.076308 | -0.00027993 | -0.0013929 | -0.00013887 | -0.027222 | 0.002869 | 0.065565 | 0.063175 | -0.0032172 | 0.0040567 | -0.00056605 | -0.086975 | 62.9791 | -60.2234 | 62.8967 | -59.9762 | -60.3607 | -0.10986 | -0.15564 | 62.9333 | -60.0861 | 63.0112 | -60.1044 | -60.1913 | -59.9533 | -0.18768 | 0.013733 | -0.068664 | 0.05951 | 59.9258 | -0.32501 | 60.1135 | -0.13733 | -0.050354 | -0.032043 | 0.045776 | -0.068664 | 0.082398 | -0.15564 | 0.13275 | -0.10528 | 0.24719 | 123.1201 | -0.01831 | 123.0972 | 123.2025 | 123.0194 | 123.0148 | 122.9691 | -123.1888 | -123.0515 | 122.9324 | 123.0469 | 59.9487 | 59.8801
212.3281 | 123.2712 | -60.0037 | 62.9562 | -0.12154 | 0.00049772 | 0.064422 | 0.074813 | -0.0024161 | -0.0011791 | -0.0022751 | 0.015503 | 0.00051903 | 0.062788 | 0.055484 | -0.0025764 | 0.00021147 | -0.0018479 | -0.041199 | 62.9288 | -60.1456 | 62.9929 | -59.8434 | -60.228 | -0.027466 | -0.041199 | 62.9059 | -60.0632 | 63.0981 | -60.0128 | -60.0906 | -59.8572 | -0.14191 | -0.027466 | 0.036621 | 0.16022 | 59.9762 | -0.2243 | 60.1181 | -0.082397 | -0.059509 | -0.050354 | 0.14191 | -0.009155 | 0.14648 | -0.086975 | 0.20599 | -0.027466 | 0.30212 | 123.1384 | 0.050354 | 123.1613 | 123.0743 | 122.9691 | 122.9324 | 122.9095 | -123.1018 | -123.0194 | 122.9965 | 123.1018 | 59.9625 | 59.9625
213.3281 | 123.175 | -60.0174 | 63.002 | -0.06813 | 0.00092492 | 0.064422 | 0.075881 | 0.0010019 | -0.00032472 | -0.00099327 | -0.069946 | 0.0013736 | 0.064711 | 0.063175 | -0.0023626 | 0.0012797 | -0.00035245 | -0.09613 | 62.97 | -60.2234 | 62.8967 | -59.9945 | -60.3424 | -0.11902 | -0.15106 | 62.9608 | -60.0815 | 63.002 | -60.1135 | -60.2188 | -59.967 | -0.20599 | -0.032043 | -0.10529 | 0.022888 | 59.8984 | -0.32501 | 60.1044 | -0.11902 | -0.064087 | -0.041199 | 0 | -0.09613 | 0.050354 | -0.20142 | 0.11444 | -0.13733 | 0.22888 | 123.1201 | -0.032043 | 123.0835 | 123.1934 | 123.0423 | 122.9874 | 122.9782 | -123.2254 | -123.0835 | 122.9141 | 123.0194 | 59.9213 | 59.8663
214.3281 | 123.349 | -59.9808 | 62.9654 | -0.15205 | 0.00049772 | 0.06485 | 0.075027 | 0.00078827 | -0.00075192 | -0.0014207 | -0.042481 | -0.00012177 | 0.063002 | 0.06702 | -0.0032172 | 0.00021147 | -0.0035569 | -0.059509 | 62.9654 | -60.1685 | 62.9883 | -59.8618 | -60.2371 | -0.032043 | -0.041199 | 62.9196 | -60.054 | 63.2126 | -60.054 | -60.054 | -59.8434 | -0.18768 | 0 | 0.022888 | 0.11902 | 59.9487 | -0.25635 | 60.1364 | -0.068665 | -0.073242 | -0.045776 | 0.24719 | -0.073242 | 0.13733 | -0.073242 | 0.21057 | 0 | 0.3067 | 123.1567 | 0 | 123.2666 | 123.1338 | 122.9736 | 122.9462 | 122.9004 | -123.1338 | -123.0194 | 122.9691 | 123.1934 | 59.9213 | 59.9396
215.3281 | 123.2025 | -60.0403 | 63.0157 | -0.045242 | -0.00014308 | 0.062072 | 0.076522 | 0.0048471 | 0.00031608 | -0.00077967 | -0.057739 | 0.0020144 | 0.063856 | 0.066379 | -0.0032172 | 0.00085247 | -0.0035569 | 0.059509 | 63.002 | -60.1776 | 62.915 | -60.0082 | -60.3882 | -0.10071 | -0.16937 | 62.97 | -60.0723 | 63.002 | -60.1318 | -60.2234 | -59.9854 | -0.13733 | -0.013733 | -0.10071 | 0.032043 | 59.9396 | -0.3479 | 60.0769 | -0.21057 | -0.032044 | -0.045776 | -0.013733 | -0.091553 | 0.054931 | -0.18311 | 0.086975 | -0.15106 | 0.16937 | 123.0927 | -0.059509 | 123.0743 | 123.1796 | 123.0423 | 123.0423 | 123.0103 | -123.1934 | -123.0881 | 122.9553 | 123.0423 | 60.0998 | 59.8709
216.3281 | 123.3307 | -59.9808 | 62.9517 | -0.098648 | 0.0022067 | 0.063354 | 0.075027 | 0.0018565 | 0.00074348 | -0.00099327 | -0.011963 | 0.00094643 | 0.064497 | 0.064456 | -0.004499 | 0.0032023 | -0.0041977 | -0.068665 | 62.97 | -60.1959 | 62.9791 | -59.8526 | -60.2875 | -0.07782 | -0.054932 | 62.8922 | -60.0311 | 63.089 | -60.0174 | -60.1089 | -59.8618 | -0.21515 | 0.018311 | 0.027466 | 0.12817 | 59.903 | -0.3067 | 60.1181 | -0.091553 | -0.050354 | -0.059509 | 0.13733 | -0.036621 | 0.11902 | -0.12817 | 0.16937 | -0.07782 | 0.34332 | 123.175 | 0.013733 | 123.1201 | 123.1659 | 122.9233 | 122.9507 | 122.8729 | -123.1476 | -122.9828 | 122.9599 | 123.0698 | 59.9121 | 59.9258
217.3281 | 123.1705 | -60.0266 | 63.002 | -0.07576 | 0.0019931 | 0.064422 | 0.078231 | -0.0015615 | -0.00096552 | -0.00056607 | -0.057739 | 0.00094643 | 0.065138 | 0.065525 | -0.0034308 | 0.00085247 | -0.0012071 | -0.050354 | 63.0203 | -60.1959 | 62.9333 | -59.967 | -60.3333 | -0.086975 | -0.1236 | 62.9517 | -60.0586 | 63.002 | -60.141 | -60.2234 | -59.967 | -0.16937 | 0.018311 | -0.068664 | 0.059509 | 59.9396 | -0.3067 | 60.1089 | -0.13733 | -0.032044 | -0.050354 | 0 | -0.11444 | 0.059509 | -0.19684 | 0.091553 | -0.16479 | 0.22888 | 123.1293 | -0.082397 | 123.0606 | 123.2162 | 123.0103 | 123.0469 | 122.9782 | -123.1979 | -123.0606 | 122.9599 | 123.0286 | 59.9762 | 59.903
218.3281 | 123.2849 | -60.0082 | 62.9608 | -0.06813 | -0.0016385 | 0.06549 | 0.07524 | -6.6126e-05 | 0.0015979 | 0.00028833 | -0.027222 | 0.00073263 | 0.064711 | 0.058902 | -0.00279 | 0.0034159 | 0.0011429 | -0.091553 | 62.9883 | -60.1868 | 62.9608 | -59.9167 | -60.2692 | -0.07782 | -0.073242 | 62.9013 | -60.0494 | 63.0981 | -60.0128 | -60.1089 | -59.8572 | -0.17853 | 0.027466 | 0 | 0.091553 | 59.9304 | -0.26093 | 60.1089 | -0.082397 | -0.041198 | -0.059509 | 0.13733 | -0.004577 | 0.15106 | -0.10071 | 0.19226 | -0.05951 | 0.27008 | 123.1476 | 0.036621 | 123.1476 | 123.175 | 122.9507 | 122.9965 | 122.9095 | -123.1476 | -123.0103 | 122.9691 | 123.1064 | 59.9167 | 59.935
219.3281 | 123.2025 | -60.0266 | 63.0066 | -0.083389 | -0.00078408 | 0.065063 | 0.075881 | 0.0018565 | 0.0013843 | -0.0018479 | -0.051636 | 0.0020144 | 0.06407 | 0.063816 | -0.0017218 | 0.00063867 | 0.0019973 | -0.11444 | 62.9654 | -60.1822 | 62.8922 | -59.9899 | -60.3378 | -0.10986 | -0.16479 | 62.9379 | -60.0632 | 63.0203 | -60.1044 | -60.2097 | -59.9533 | -0.15564 | -0.041199 | -0.11444 | 0.036621 | 59.9167 | -0.31128 | 60.0723 | -0.15564 | -0.036621 | -0.068665 | 0.013733 | -0.07782 | 0.073242 | -0.18311 | 0.10986 | -0.14649 | 0.19226 | 123.0743 | -0.041199 | 123.0835 | 123.1476 | 123.0011 | 122.9919 | 122.9645 | -123.1888 | -123.0698 | 122.9187 | 123.0469 | 59.9121 | 59.8618
220.3281 | 123.3078 | -60.0082 | 62.9471 | -0.1368 | 0.0011385 | 0.065704 | 0.07524 | 0.0024973 | -0.0024609 | -0.0014207 | 0.0063477 | -0.00033537 | 0.065565 | 0.062961 | -0.00043997 | 0.0019205 | -0.00099325 | -0.036621 | 62.9333 | -60.1456 | 63.002 | -59.8389 | -60.2325 | -0.004578 | -0.022888 | 62.9379 | -60.0311 | 63.0936 | -59.9991 | -60.0815 | -59.8618 | -0.13733 | -0.013733 | 0.054931 | 0.16937 | 60.0037 | -0.2243 | 60.141 | -0.086975 | -0.022888 | -0.009156 | 0.14648 | 0.009156 | 0.14648 | -0.073242 | 0.16937 | -0.050354 | 0.3067 | 123.1476 | 0.032044 | 123.1247 | 123.0789 | 122.9691 | 122.9416 | 122.9462 | -123.0927 | -122.9782 | 123.0103 | 123.1018 | 59.9716 | 59.9854
221.3281 | 123.1934 | -60.0449 | 62.9929 | -0.11391 | -0.00035668 | 0.063781 | 0.076095 | 0.0010019 | -0.0031017 | -0.0033433 | -0.085205 | 0.00116 | 0.065779 | 0.062747 | -0.0017218 | 0.00063867 | -0.0022751 | -0.041199 | 63.0112 | -60.1913 | 62.8967 | -59.9945 | -60.3561 | -0.10071 | -0.16937 | 62.9654 | -60.0906 | 63.002 | -60.1273 | -60.2142 | -59.9533 | -0.14648 | 0.01831 | -0.09613 | 0.050354 | 59.9442 | -0.31128 | 60.0906 | -0.1648 | -0.045776 | -0.027466 | 0.009155 | -0.082397 | 0.091553 | -0.16937 | 0.13733 | -0.1236 | 0.19684 | 123.0881 | -0.036621 | 123.0927 | 123.2025 | 123.056 | 123.056 | 123.0103 | -123.1842 | -123.0835 | 122.9416 | 123.0469 | 60.0037 | 59.8755
222.3281 | 123.262 | -60.0449 | 62.9517 | -0.06813 | 0.00028412 | 0.063995 | 0.076095 | 0.0012155 | -0.00075192 | -0.0035569 | -0.02417 | -0.00119 | 0.063002 | 0.066806 | -0.0017218 | 0.0034159 | 0.00050195 | -0.064087 | 62.9837 | -60.1776 | 62.9883 | -59.8663 | -60.2463 | -0.036621 | -0.059509 | 62.9379 | -60.0403 | 63.1027 | -59.9899 | -60.0266 | -59.9442 | -0.13275 | 0.032044 | 0.036621 | 0.17853 | 60.0082 | -0.20142 | 60.141 | -0.068665 | 0.004578 | -0.013733 | 0.15106 | 0.054932 | 0.10071 | 0.018311 | 0.09613 | 0.013733 | 0.31128 | 123.1659 | 0.050354 | 123.143 | 123.1613 | 122.9782 | 123.0286 | 122.9828 | -123.1293 | -122.9919 | 123.0331 | 123.1476 | 59.9808 | 59.9854
223.3281 | 123.1567 | -60.0357 | 63.0203 | -0.07576 | 0.0024203 | 0.0625 | 0.076949 | 0.0014291 | 0.0015979 | -0.00013887 | -0.060791 | 0.0020144 | 0.063856 | 0.068515 | -0.001081 | 0.0012797 | -0.0020615 | -0.054932 | 63.0157 | -60.2005 | 62.915 | -59.9762 | -60.3287 | -0.091553 | -0.14191 | 62.9791 | -60.054 | 63.0066 | -60.1227 | -60.2463 | -59.9762 | -0.16479 | -0.004578 | -0.10529 | 0.05951 | 59.9442 | -0.29297 | 60.1089 | -0.12817 | -0.01831 | -0.041199 | -0.013733 | -0.086975 | 0.05951 | -0.21057 | 0.07782 | -0.19226 | 0.2243 | 123.1155 | -0.068665 | 123.0606 | 123.2162 | 123.0331 | 123.0515 | 123.0148 | -123.2208 | -123.0743 | 122.9507 | 123.0423 | 59.9808 | 59.8938
224.3281 | 123.1934 | -60.0357 | 62.9608 | -0.07576 | 0.00092492 | 0.063781 | 0.075667 | 0.00057467 | -0.0013929 | 0.0013565 | -0.054688 | -0.00033537 | 0.061293 | 0.05933 | -0.0047126 | 0.0032023 | -0.00035245 | -0.086975 | 62.9883 | -60.1913 | 62.9013 | -59.9899 | -60.3333 | -0.11902 | -0.16479 | 62.97 | -60.0677 | 63.0203 | -60.1227 | -60.2188 | -59.9533 | -0.15564 | 0.027466 | -0.059509 | 0.045777 | 59.9167 | -0.29755 | 60.0723 | -0.14191 | -0.032043 | 0.009156 | 0.05951 | -0.086975 | 0.082398 | -0.18311 | 0.11444 | -0.15106 | 0.20142 | 123.0927 | -0.054932 | 123.0881 | 123.1796 | 123.0377 | 123.024 | 123.0057 | -123.1522 | -123.0286 | 122.937 | 123.056 | 59.9487 | 59.8709
225.3281 | 123.1705 | -60.0082 | 63.0112 | 0.00053424 | 0.00049772 | 0.064636 | 0.078658 | 0.0014291 | -0.00032472 | -0.0024887 | -0.054688 | 0.0013736 | 0.064497 | 0.072788 | -0.0034308 | 0.00085247 | 0.0022109 | -0.1236 | 63.002 | -60.2142 | 62.8784 | -59.9991 | -60.3287 | -0.10986 | -0.17395 | 62.9654 | -60.0677 | 62.9929 | -60.1089 | -60.228 | -59.9625 | -0.20599 | -0.009155 | -0.13275 | 0.009156 | 59.8984 | -0.32043 | 60.1044 | -0.11444 | -0.059509 | -0.045776 | -0.01831 | -0.10071 | 0.045777 | -0.21973 | 0.10529 | -0.16022 | 0.21515 | 123.0927 | -0.041199 | 123.0606 | 123.2162 | 123.0331 | 123.0103 | 122.9736 | -123.2254 | -123.0789 | 122.8867 | 123.0011 | 59.8846 | 59.8343
226.3281 | 123.3627 | -60.022 | 62.9288 | -0.06813 | 0.0011385 | 0.065704 | 0.07524 | -0.0041251 | 0.0011707 | 0.00071573 | -0.021118 | 0.0018008 | 0.063429 | 0.061252 | -0.0057806 | -0.00021573 | -0.0035569 | -0.054932 | 62.9562 | -60.173 | 62.9745 | -59.8618 | -60.2646 | -0.027466 | -0.068665 | 62.8967 | -60.0266 | 63.0936 | -59.9991 | -60.0906 | -59.8343 | -0.15106 | 0.027466 | 0.045776 | 0.16022 | 59.9945 | -0.24261 | 60.1456 | -0.091552 | -0.004577 | -0.032043 | 0.16479 | 0.022889 | 0.18768 | -0.068664 | 0.19226 | -0.064087 | 0.31128 | 123.1476 | 0.027466 | 123.1201 | 123.1293 | 122.9233 | 122.9782 | 122.9187 | -123.1018 | -122.9553 | 122.9965 | 123.1155 | 59.967 | 59.9533
227.3281 | 123.1888 | -60.0815 | 62.9974 | -0.060501 | 0.0015659 | 0.065918 | 0.077804 | -0.00049353 | 0.00010248 | 0.00050193 | 0.11621 | 0.00030543 | 0.063215 | 0.064243 | -0.0030036 | 0.0021341 | -0.00077965 | -0.11444 | 63.002 | -60.2234 | 62.8555 | -59.9075 | -60.8139 | -0.2655 | -0.27466 | 62.9654 | -60.0677 | 62.9929 | -60.1364 | -60.2234 | -59.935 | -0.14191 | 0.004577 | -0.14191 | 0.17395 | 59.816 | -0.73242 | 59.9579 | -0.59052 | 0.013733 | -0.032044 | -0.004578 | -0.054932 | 0.14648 | -0.14191 | 0.13275 | -0.15564 | 0.31586 | 123.0789 | -0.068665 | 123.0606 | 123.2254 | 123.0331 | 123.0835 | 123.0469 | -123.2208 | -123.0652 | 122.937 | 123.0743 | 59.967 | 59.8068
228.3281 | 123.2849 | -60.0174 | 62.9608 | -0.098648 | 0.00049772 | 0.064422 | 0.076736 | -0.0015615 | -0.0011791 | -0.0027023 | -0.02417 | 0.002228 | 0.063002 | 0.063816 | -0.00279 | 0.0032023 | -0.0024887 | -0.11444 | 62.9791 | -60.1685 | 62.9471 | -59.9442 | -60.2966 | -0.086975 | -0.09613 | 62.9562 | -60.0632 | 63.0615 | -60.022 | -60.1318 | -59.8709 | -0.15106 | 0.018311 | -0.013732 | 0.073242 | 59.9304 | -0.27924 | 60.0815 | -0.12817 | -0.045776 | -0.004577 | 0.10071 | -0.004578 | 0.14648 | -0.11444 | 0.19226 | -0.068665 | 0.2243 | 123.1155 | 0.041198 | 123.1247 | 123.1476 | 123.0194 | 122.9965 | 122.9736 | -123.1293 | -123.024 | 122.9645 | 123.0789 | 59.903 | 59.9213
229.3281 | 123.1705 | -60.0403 | 62.9791 | -0.06813 | 0.0026339 | 0.064422 | 0.076095 | -0.00027993 | -0.0016065 | 0.0017837 | -0.063843 | 0.0015872 | 0.063429 | 0.066379 | -0.0019354 | 0.0042703 | 0.00071555 | -0.068665 | 62.9929 | -60.1959 | 62.8922 | -60.0082 | -60.3333 | -0.10529 | -0.16937 | 62.9837 | -60.0494 | 62.9745 | -60.1456 | -60.2554 | -59.9854 | -0.15564 | 0.013733 | -0.086975 | 0.032043 | 59.935 | -0.29297 | 60.0906 | -0.13733 | -0.009155 | 0.004578 | -0.004578 | -0.10529 | 0.054931 | -0.21515 | 0.064086 | -0.20599 | 0.18768 | 123.0881 | -0.096131 | 123.024 | 123.1888 | 123.0331 | 123.0331 | 123.024 | -123.175 | -123.0286 | 122.9324 | 123.0148 | 59.9716 | 59.8709
230.3281 | 123.1934 | -60.0357 | 62.9974 | -0.091019 | 0.0026339 | 0.064422 | 0.080154 | 0.0065561 | 0.00074348 | -0.0012071 | 0.021606 | -0.00012177 | 0.067274 | 0.065311 | -0.00279 | 0.0029887 | 0.0026383 | -0.10986 | 62.9974 | -60.1959 | 63.0112 | -59.7473 | -60.4843 | -0.10071 | -0.20142 | 62.9883 | -60.0677 | 62.9791 | -60.1318 | -60.2234 | -59.9716 | -0.16022 | 0 | 0.013732 | 0.28839 | 59.935 | -0.44861 | 60.0952 | -0.28839 | -0.032043 | -0.009156 | -0.018311 | -0.09613 | 0.064087 | -0.18768 | 0.09613 | -0.15564 | 0.44861 | 123.2071 | -0.064087 | 123.0469 | 123.1934 | 123.056 | 123.0331 | 123.024 | -123.1934 | -123.0652 | 123.0469 | 123.0148 | 59.9258 | 59.8343
231.3281 | 123.1705 | -60.0082 | 63.0341 | -0.037613 | 0.0011385 | 0.065277 | 0.076736 | -6.6126e-05 | -0.00096552 | 0.00071573 | -0.072998 | 0.0015872 | 0.065565 | 0.061679 | -0.00279 | 0.0042703 | -0.0027023 | -0.059509 | 62.9974 | -60.1913 | 62.9059 | -59.9396 | -60.3104 | -0.064087 | -0.09613 | 62.9562 | -60.054 | 62.9974 | -60.1089 | -60.2188 | -59.9716 | -0.1831 | -0.036621 | -0.12817 | 0.068665 | 59.9442 | -0.30212 | 60.1273 | -0.11902 | -0.045776 | -0.07782 | -0.036621 | -0.10071 | 0.036621 | -0.21057 | 0.082397 | -0.1648 | 0.25177 | 123.0972 | -0.054932 | 123.0515 | 123.1888 | 123.0103 | 123.0057 | 122.9645 | -123.2254 | -123.0881 | 122.9141 | 123.0057 | 59.9487 | 59.9121
232.3281 | 123.2758 | -60.0082 | 62.97 | -0.091019 | 0.0019931 | 0.063995 | 0.075881 | 0.0031381 | 0.0013843 | -0.0027023 | -0.033325 | -0.00054897 | 0.063002 | 0.065738 | -0.0030036 | 0.0025613 | 0.0024245 | -0.10071 | 62.9974 | -60.1822 | 62.9059 | -59.9487 | -60.3195 | -0.09613 | -0.13733 | 62.9288 | -60.0586 | 63.0569 | -60.0311 | -60.141 | -59.8892 | -0.17395 | 0.027466 | -0.064087 | 0.05951 | 59.9121 | -0.31128 | 60.0861 | -0.13733 | -0.050354 | -0.041199 | 0.086975 | -0.022888 | 0.11902 | -0.13275 | 0.16937 | -0.082397 | 0.23346 | 123.0881 | 0.027466 | 123.1155 | 123.1796 | 122.9874 | 123.0057 | 122.937 | -123.1522 | -123.0286 | 122.9141 | 123.0652 | 59.9075 | 59.8709
233.3281 | 123.143 | -60.0357 | 63.0157 | -0.037613 | -0.00014308 | 0.063781 | 0.07524 | -0.0026297 | 0.0011707 | 0.00092933 | -0.072998 | -0.00012177 | 0.063429 | 0.05698 | -0.0030036 | 0.0032023 | 0.0024245 | -0.073242 | 62.9883 | -60.1959 | 62.8876 | -59.9716 | -60.3241 | -0.10071 | -0.14648 | 62.9517 | -60.022 | 62.9791 | -60.1227 | -60.2325 | -59.9762 | -0.16022 | -0.027466 | -0.12817 | 0.064087 | 59.935 | -0.28839 | 60.0952 | -0.12817 | 0.013733 | -0.064087 | -0.036621 | -0.086975 | 0.05951 | -0.19684 | 0.045777 | -0.21057 | 0.2243 | 123.0835 | -0.10071 | 123.0011 | 123.1842 | 122.9736 | 123.024 | 122.9874 | -123.2117 | -123.0377 | 122.9233 | 123.0148 | 59.9625 | 59.8892
234.3281 | 123.2574 | -60.0311 | 62.9791 | -0.1368 | 0.00071132 | 0.064209 | 0.077163 | 0.0014291 | -0.00075192 | 0.00028833 | -0.018066 | 0.002869 | 0.06407 | 0.05933 | -0.0019354 | 0.0021341 | -0.0020615 | -0.10529 | 62.9608 | -60.2142 | 62.8922 | -59.9808 | -60.3424 | -0.1236 | -0.14648 | 62.9608 | -60.0723 | 63.0249 | -60.0998 | -60.1959 | -59.9304 | -0.1831 | -0.018311 | -0.086975 | 0.050354 | 59.9075 | -0.31128 | 60.0906 | -0.12817 | -0.041199 | -0.018311 | 0.045776 | -0.068664 | 0.10071 | -0.16479 | 0.14191 | -0.1236 | 0.23346 | 123.1064 | -0.027465 | 123.0972 | 123.175 | 123.0331 | 122.9919 | 122.9919 | -123.1934 | -123.0515 | 122.9233 | 123.056 | 59.9258 | 59.8846
235.3281 | 123.1705 | -60.0174 | 63.0066 | -0.037613 | 0.0019931 | 0.065704 | 0.076095 | -6.6126e-05 | 0.00095708 | 7.4734e-05 | -0.048584 | 0.00094643 | 0.063856 | 0.062961 | -0.0032172 | 0.00063867 | -0.0035569 | -0.045776 | 62.9837 | -60.1776 | 62.9242 | -59.9487 | -60.3058 | -0.068665 | -0.10071 | 62.9929 | -60.0357 | 62.9883 | -60.1044 | -60.2188 | -59.9625 | -0.16022 | -0.022888 | -0.082398 | 0.068665 | 59.9487 | -0.28839 | 60.1089 | -0.12817 | -0.018311 | -0.013733 | -0.018311 | -0.086975 | 0.054932 | -0.20142 | 0.073243 | -0.18311 | 0.22888 | 123.1018 | -0.068664 | 123.024 | 123.1613 | 123.0286 | 123.0011 | 123.0103 | -123.1842 | -123.0423 | 122.9416 | 123.0057 | 59.9716 | 59.9167
236.3281 | 123.1888 | -60.0174 | 62.9791 | -0.1368 | 0.0017795 | 0.065063 | 0.075454 | 0.0024973 | -0.00032472 | -0.0020615 | -0.039429 | 0.0015872 | 0.066206 | 0.058902 | -0.0023626 | 0.0012797 | -0.00056605 | -0.091553 | 62.9929 | -60.1959 | 62.8876 | -59.9854 | -60.3424 | -0.11444 | -0.16022 | 62.9471 | -60.0723 | 63.002 | -60.1181 | -60.2097 | -59.9579 | -0.17853 | 0.013733 | -0.091553 | 0.032043 | 59.903 | -0.32501 | 60.0815 | -0.14648 | -0.054932 | -0.032043 | 0.022888 | -0.10071 | 0.059509 | -0.19226 | 0.11444 | -0.13733 | 0.21057 | 123.0835 | -0.045776 | 123.0743 | 123.1888 | 123.0194 | 123.0103 | 122.9645 | -123.175 | -123.0515 | 122.905 | 123.0194 | 59.9258 | 59.8572
237.3281 | 123.2117 | -59.9899 | 63.0066 | -0.07576 | 0.0013523 | 0.063781 | 0.076736 | 0.00078827 | 0.00010248 | -0.00056607 | -0.033325 | 0.00030543 | 0.066633 | 0.06702 | -0.0030036 | 0.0025613 | 0.00071555 | -0.009155 | 63.0112 | -60.1776 | 62.9791 | -59.8709 | -60.2692 | 0.018311 | 0.032043 | 62.9745 | -60.0266 | 63.0524 | -60.0403 | -60.1227 | -59.8892 | -0.18768 | 0.004577 | -0.027466 | 0.11902 | 60.0082 | -0.27924 | 60.1959 | -0.091553 | -0.036621 | -0.032044 | 0.045776 | -0.050354 | 0.10071 | -0.13275 | 0.13733 | -0.096131 | 0.3067 | 123.1567 | -0.013733 | 123.0789 | 123.1888 | 123.0011 | 123.0011 | 122.9645 | -123.1842 | -123.0331 | 122.9691 | 123.0423 | 59.9808 | 60.022
238.3281 | 123.1842 | -60.0449 | 62.9608 | -0.0070953 | 0.0022067 | 0.063995 | 0.079513 | -0.0015615 | 0.00074348 | -0.00056607 | -0.060791 | 0.00073263 | 0.065352 | 0.059757 | -0.0012946 | 0.0025613 | 0.0028519 | -0.073242 | 63.0157 | -60.2005 | 62.8784 | -59.9945 | -60.347 | -0.12817 | -0.16022 | 62.9654 | -60.0632 | 63.002 | -60.1273 | -60.2325 | -59.9625 | -0.15564 | 0.054932 | -0.082397 | 0.050354 | 59.9167 | -0.30212 | 60.0723 | -0.14648 | -0.01831 | 0.004578 | 0.041199 | -0.082397 | 0.082398 | -0.18768 | 0.10071 | -0.16937 | 0.20599 | 123.0789 | -0.064087 | 123.0652 | 123.2162 | 123.0286 | 123.0606 | 123.0103 | -123.1613 | -123.024 | 122.9233 | 123.0469 | 59.9716 | 59.8846
239.3281 | 123.1842 | -60.0311 | 63.0203 | -0.045242 | 0.0022067 | 0.063781 | 0.076522 | 0.0027109 | -0.0026745 | 0.00092933 | -0.045532 | -0.00033537 | 0.064924 | 0.063602 | -0.0030036 | 0.0036295 | -0.0020615 | -0.064087 | 62.9974 | -60.1822 | 62.8922 | -59.9854 | -60.3333 | -0.086975 | -0.16937 | 62.97 | -60.0357 | 62.9654 | -60.1456 | -60.2417 | -59.9854 | -0.15106 | -0.022888 | -0.12817 | 0.045776 | 59.9442 | -0.30212 | 60.0952 | -0.15106 | -0.004578 | -0.050354 | -0.054932 | -0.11444 | 0.045776 | -0.21057 | 0.050354 | -0.20599 | 0.19684 | 123.0743 | -0.10986 | 123.0011 | 123.1796 | 123.0057 | 123.0286 | 123.0011 | -123.2025 | -123.056 | 122.9233 | 122.9965 | 59.967 | 59.8618
240.3281 | 123.2162 | -60.0311 | 62.9745 | -0.091019 | 7.0518e-05 | 0.064636 | 0.075667 | 0.0027109 | 0.00031608 | 0.0011429 | -0.02417 | -0.00119 | 0.065352 | 0.062534 | -0.00065377 | 0.0029887 | -0.00056605 | -0.10986 | 62.9791 | -60.2142 | 62.8784 | -59.9625 | -60.3333 | -0.1236 | -0.14648 | 62.9471 | -60.0449 | 63.0295 | -60.0723 | -60.173 | -59.9213 | -0.1831 | 0.004578 | -0.09613 | 0.068665 | 59.9075 | -0.30212 | 60.0906 | -0.11902 | -0.013733 | -0.027465 | 0.054932 | -0.041199 | 0.10986 | -0.14191 | 0.1236 | -0.12817 | 0.25177 | 123.0927 | -0.027466 | 123.0743 | 123.1934 | 122.9919 | 123.0103 | 122.9782 | -123.1888 | -123.0194 | 122.9095 | 123.0606 | 59.9213 | 59.8846
241.3281 | 123.1796 | -60.0128 | 63.0203 | -0.029984 | 0.0011385 | 0.064209 | 0.076308 | 0.0020701 | -0.00053832 | 0.0015701 | -0.051636 | 0.00073263 | 0.066206 | 0.060825 | -0.0042854 | 0.0010661 | 0.0013565 | -0.050354 | 62.9837 | -60.1868 | 62.9059 | -59.9762 | -60.3287 | -0.091553 | -0.12817 | 62.9791 | -60.0128 | 62.9837 | -60.1364 | -60.228 | -59.9625 | -0.17395 | -0.036621 | -0.11444 | 0.036621 | 59.9213 | -0.31586 | 60.0952 | -0.14191 | 0 | -0.041199 | -0.036621 | -0.1236 | 0.050354 | -0.21515 | 0.050354 | -0.21515 | 0.21057 | 123.0927 | -0.1236 | 122.9965 | 123.1705 | 122.9919 | 122.9965 | 122.9919 | -123.2071 | -123.0331 | 122.9187 | 122.9965 | 59.9625 | 59.8846
242.3281 | 123.1979 | -60.0082 | 62.97 | -0.10628 | 0.00071132 | 0.065918 | 0.076522 | 0.0016427 | -0.00032472 | -0.0012071 | -0.015015 | 0.0020144 | 0.062788 | 0.057407 | -0.0036444 | 0.0025613 | -0.0041977 | -0.091553 | 62.97 | -60.2005 | 62.8876 | -59.9716 | -60.3424 | -0.11902 | -0.15106 | 62.9517 | -60.0769 | 63.002 | -60.0815 | -60.1913 | -59.9258 | -0.19226 | 0 | -0.082398 | 0.036621 | 59.8892 | -0.33417 | 60.0815 | -0.14191 | -0.068664 | -0.018311 | 0.032043 | -0.073242 | 0.082398 | -0.1831 | 0.15106 | -0.11444 | 0.22888 | 123.0881 | -0.004578 | 123.0789 | 123.1705 | 123.0286 | 122.9782 | 122.9599 | -123.1705 | -123.0469 | 122.8958 | 123.0103 | 59.9167 | 59.8572
243.3281 | 123.1522 | -60.022 | 63.002 | -0.07576 | 0.0028475 | 0.066345 | 0.077376 | 0.00036107 | -0.00032472 | -0.00077967 | -0.048584 | 9.1834e-05 | 0.063856 | 0.066165 | -0.0023626 | 0.0025613 | 0.0045609 | -0.054932 | 63.0066 | -60.2051 | 62.915 | -59.9442 | -60.3012 | -0.086975 | -0.10986 | 62.9654 | -60.054 | 62.9929 | -60.1135 | -60.1913 | -59.9716 | -0.1831 | 0.004578 | -0.086975 | 0.07782 | 59.935 | -0.27923 | 60.1181 | -0.09613 | -0.032043 | -0.036621 | -0.009155 | -0.091552 | 0.050354 | -0.16937 | 0.082397 | -0.13733 | 0.26093 | 123.1201 | -0.059509 | 123.0469 | 123.2117 | 123.0194 | 123.0286 | 122.9874 | -123.2071 | -123.056 | 122.937 | 123.0148 | 59.967 | 59.9121
244.3281 | 123.1659 | -60.0266 | 63.002 | -0.045242 | 0.0019931 | 0.063781 | 0.077376 | 0.00036107 | -0.0031017 | -0.0033433 | -0.085205 | -0.00012177 | 0.065138 | 0.06467 | -0.0032172 | 0.00063867 | 0.0049881 | -0.10529 | 63.0066 | -60.1822 | 62.8693 | -60.0174 | -60.3699 | -0.34332 | 0.032043 | 62.9654 | -60.0494 | 62.9929 | -60.1364 | -60.2417 | -59.9579 | -0.15564 | 0.004578 | -0.13275 | 0.009155 | 59.6832 | -0.34332 | 59.8389 | -0.18768 | -0.022888 | -0.036621 | -0.009155 | -0.10986 | 0.068664 | -0.21515 | 0.091552 | -0.19226 | 0.16479 | 123.0515 | -0.086976 | 123.0423 | 123.1888 | 123.0148 | 123.0331 | 122.9919 | -123.1842 | -123.0515 | 122.8958 | 123.0194 | 59.9213 | 60.0586
245.3281 | 123.1934 | -60.0311 | 63.0295 | -0.06813 | 7.0518e-05 | 0.064636 | 0.076736 | 0.00057467 | 0.00031608 | -0.00099327 | -0.036377 | -0.00012177 | 0.062788 | 0.063602 | -0.00279 | 0.0021341 | 7.4746e-05 | -0.054932 | 62.9929 | -60.1959 | 62.915 | -59.9442 | -60.3058 | -0.059509 | -0.10986 | 62.9791 | -60.0403 | 62.9929 | -60.0906 | -60.2097 | -59.9442 | -0.16479 | -0.036621 | -0.11444 | 0.086975 | 59.9716 | -0.27466 | 60.1364 | -0.10986 | -0.009155 | -0.050354 | -0.036621 | -0.059509 | 0.086975 | -0.17853 | 0.09613 | -0.16937 | 0.25177 | 123.111 | -0.050354 | 123.0331 | 123.1888 | 123.0194 | 123.024 | 123.0103 | -123.2254 | -123.0698 | 122.9462 | 123.024 | 59.9762 | 59.9213
246.3281 | 123.2986 | -60.0037 | 62.9883 | -0.091019 | -0.00057028 | 0.063781 | 0.074386 | 0.0010019 | -0.0016065 | -0.0012071 | -0.011963 | 0.00116 | 0.065138 | 0.05997 | -0.0023626 | 0.00085247 | -0.00099325 | -0.09613 | 62.9654 | -60.1822 | 62.9333 | -59.9258 | -60.2966 | -0.07782 | -0.10071 | 62.9105 | -60.0586 | 63.0661 | -60.0174 | -60.1227 | -59.8801 | -0.17853 | -0.022888 | -0.054931 | 0.07782 | 59.9258 | -0.29297 | 60.1044 | -0.11444 | -0.054932 | -0.07782 | 0.07782 | -0.013733 | 0.1236 | -0.11902 | 0.17853 | -0.064087 | 0.25635 | 123.1155 | 0.041199 | 123.1247 | 123.1476 | 122.9691 | 122.9691 | 122.9141 | -123.1705 | -123.0469 | 122.937 | 123.0698 | 59.9075 | 59.903
247.3281 | 123.23 | -60.0082 | 63.0112 | -0.06813 | -0.00035668 | 0.063995 | 0.075027 | -0.0015615 | -0.0018201 | 0.0013565 | -0.033325 | 0.00051903 | 0.065779 | 0.061252 | -1.2774e-05 | 0.0027751 | -0.0035569 | -0.10071 | 63.0066 | -60.173 | 62.8693 | -60.0128 | -60.3653 | -0.11902 | -0.19684 | 62.9562 | -60.0723 | 63.0661 | -59.967 | -60.2737 | -59.9625 | -0.16479 | -0.004577 | -0.14191 | -0.004577 | 59.8892 | -0.35706 | 60.054 | -0.19226 | -0.064087 | -0.054931 | 0.054932 | 0.041199 | 0.045777 | -0.2655 | 0.10986 | -0.20142 | 0.16022 | 123.0423 | 0.10529 | 123.1384 | 123.1796 | 123.0286 | 123.0148 | 122.9645 | -123.1842 | -123.0835 | 122.8775 | 123.0743 | 59.9075 | 59.8114
248.3281 | 123.3215 | -60.0082 | 62.9654 | -0.029984 | 0.00092492 | 0.06549 | 0.076949 | -0.00070713 | -0.00032472 | -0.00056607 | 0.012451 | -0.00054897 | 0.065352 | 0.061038 | -0.0036444 | 0.0012797 | -0.0054795 | -0.050354 | 62.9425 | -60.1593 | 62.9883 | -59.8618 | -60.2371 | -0.036621 | -0.23804 | 62.8876 | -60.0861 | 63.1073 | -60.0082 | -60.1044 | -59.8206 | -0.15106 | -0.022888 | 0.022888 | 0.14648 | 59.9716 | -0.22888 | 60.1227 | -0.07782 | -0.07782 | -0.07782 | 0.14191 | 0 | 0.18768 | -0.09613 | 0.2655 | -0.01831 | 0.29755 | 123.1476 | 0.07782 | 123.1934 | 123.1018 | 122.9736 | 122.9507 | 122.8958 | -123.1247 | -123.0515 | 122.9965 | 123.1155 | 59.9579 | 59.7702
249.3281 | 123.3078 | -60.0632 | 63.0432 | -0.07576 | 0.00071132 | 0.063995 | 0.078231 | 0.00057467 | -0.00032472 | 0.00028833 | -0.030273 | 0.0015872 | 0.064711 | 0.06467 | -0.0053534 | 0.0029887 | -0.00013885 | -0.068665 | 63.002 | -60.1822 | 62.8784 | -59.9945 | -60.3607 | -0.10986 | -0.18768 | 63.002 | -60.0632 | 62.9517 | -60.1776 | -60.5896 | -60.2325 | -0.11902 | -0.041199 | -0.16479 | 0.068664 | 59.9533 | -0.29755 | 60.0723 | -0.17853 | 0 | -0.041199 | -0.091553 | -0.11444 | -0.16937 | -0.52643 | -0.16937 | -0.52643 | 0.18768 | 123.0606 | -0.11444 | 123.0148 | 123.1842 | 123.0652 | 123.0652 | 123.0652 | -123.2254 | -123.1064 | 122.9416 | 123.0148 | 59.9945 | 59.8755
250.3281 | 123.2758 | -60.0082 | 62.97 | -0.091019 | 0.00092492 | 0.065277 | 0.076522 | -0.00049353 | -0.0018201 | 7.4734e-05 | -0.0058593 | 0.0018008 | 0.06407 | 0.065525 | -0.003858 | 0.0012797 | 0.0047745 | -0.11444 | 62.9883 | -60.2005 | 62.9059 | -59.935 | -60.3241 | -0.10529 | -0.11902 | 62.9471 | -60.0815 | 63.0569 | -60.0494 | -60.1273 | -59.8984 | -0.19226 | 0.01831 | -0.064087 | 0.073242 | 59.903 | -0.31586 | 60.0952 | -0.1236 | -0.073242 | -0.022888 | 0.086975 | -0.041198 | 0.10986 | -0.11902 | 0.18311 | -0.045776 | 0.2655 | 123.1064 | 0.032044 | 123.1384 | 123.1888 | 123.0286 | 122.9965 | 122.9553 | -123.1705 | -123.0515 | 122.9141 | 123.0652 | 59.8938 | 59.8892
251.3281 | 123.1796 | -60.0128 | 63.002 | -0.037613 | 0.00028412 | 0.066131 | 0.075667 | -6.6126e-05 | 0.00031608 | -0.0024887 | -0.036377 | 0.0018008 | 0.067274 | 0.065525 | -0.0032172 | 0.0029887 | -0.00056605 | -0.032043 | 63.002 | -60.1868 | 62.9333 | -59.903 | -60.2966 | -0.045776 | -0.050354 | 62.9745 | -60.0494 | 63.0295 | -60.0815 | -60.1913 | -59.9396 | -0.17395 | 0 | -0.068664 | 0.10986 | 59.967 | -0.28381 | 60.141 | -0.10986 | -0.036621 | -0.027466 | 0.027466 | -0.068665 | 0.073242 | -0.17853 | 0.10986 | -0.14191 | 0.28381 | 123.1201 | -0.032044 | 123.0789 | 123.1888 | 123.024 | 123.0148 | 122.9874 | -123.1888 | -123.0515 | 122.9462 | 123.0423 | 59.9808 | 59.9625
252.3281 | 123.2254 | -60.0082 | 62.9883 | -0.045242 | -0.00035668 | 0.063141 | 0.076095 | 0.00036107 | -0.00032472 | 0.0011429 | -0.021118 | 0.0015872 | 0.065138 | 0.061038 | -0.0025764 | 0.0014933 | -0.00035245 | -0.10529 | 62.9929 | -60.2005 | 62.8922 | -59.9579 | -60.3241 | -0.10071 | -0.14648 | 62.9333 | -60.0769 | 63.0249 | -60.0586 | -60.1685 | -59.9258 | -0.19226 | 0.004578 | -0.09613 | 0.050354 | 59.9075 | -0.31586 | 60.0998 | -0.1236 | -0.068664 | -0.054931 | 0.036621 | -0.050354 | 0.082398 | -0.16022 | 0.15106 | -0.091553 | 0.24261 | 123.0927 | 0.01831 | 123.1018 | 123.1934 | 123.0103 | 123.0011 | 122.9416 | -123.1888 | -123.0652 | 122.9004 | 123.0331 | 59.903 | 59.8618
253.3281 | 123.2117 | -60.0266 | 63.0112 | -0.07576 | 7.0518e-05 | 0.064209 | 0.077376 | 0.0014291 | -0.0037427 | -0.0022751 | -0.045532 | 0.00073263 | 0.064497 | 0.066593 | -0.0030036 | 0.0023477 | 0.0011429 | -0.10529 | 62.9974 | -60.2188 | 62.9105 | -59.8938 | -60.3836 | -0.10986 | -0.18768 | 62.9654 | -60.0723 | 63.002 | -60.1364 | -60.2325 | -59.9533 | -0.19226 | -0.013732 | -0.10071 | 0.13275 | 59.9167 | -0.35706 | 60.1089 | -0.16479 | -0.045777 | -0.045776 | -0.009155 | -0.10986 | 0.073242 | -0.20599 | 0.11902 | -0.16022 | 0.32501 | 123.1293 | -0.064087 | 123.0743 | 123.2162 | 123.0377 | 123.024 | 122.9919 | -123.23 | -123.0835 | 122.937 | 123.0286 | 59.9213 | 59.8389
254.3438 | 123.2803 | -59.9625 | 63.0203 | -0.07576 | 0.0026339 | 0.064209 | 0.075667 | -0.0043387 | 0.0022387 | -0.0014207 | 0.064331 | 0.00094643 | 0.063429 | 0.061038 | -0.00279 | 0.0014933 | 0.0019973 | 0.045776 | 63.002 | -60.1181 | 63.0478 | -59.7931 | -60.1501 | 0.10986 | 0.10986 | 62.9608 | -59.9945 | 63.1073 | -59.9487 | -60.0311 | -59.8343 | -0.15564 | -0.018311 | 0.027466 | 0.16937 | 60.0723 | -0.18768 | 60.228 | -0.032043 | -0.032044 | -0.05951 | 0.086975 | 0.013733 | 0.12817 | -0.068665 | 0.16022 | -0.036621 | 0.32501 | 123.1659 | 0.045777 | 123.1018 | 123.1201 | 122.9553 | 122.9645 | 122.9233 | -123.1384 | -123.0148 | 123.0103 | 123.0698 | 60.0082 | 60.0723
255.3281 | 123.1842 | -60.0266 | 63.0157 | -0.045242 | 0.00092492 | 0.065063 | 0.078658 | -0.0026297 | -0.0022473 | 7.4734e-05 | 0.0063477 | 0.0026552 | 0.06407 | 0.062961 | -0.0047126 | 0.00063867 | -0.00099325 | -0.10986 | 62.9883 | -60.2142 | 62.8647 | -60.141 | -60.7361 | -0.045776 | -0.1831 | 62.9608 | -60.0815 | 62.9745 | -60.1227 | -60.2234 | -59.9579 | -0.18768 | -0.027466 | -0.15106 | -0.11444 | 59.9808 | -0.70953 | 60.1685 | -0.52185 | -0.054932 | -0.054932 | -0.041199 | -0.096131 | 0.068664 | -0.19684 | 0.1236 | -0.14191 | 0.073242 | 123.0789 | -0.041199 | 123.056 | 123.2025 | 123.0423 | 123.0148 | 122.9874 | -123.23 | -123.0972 | 122.8912 | 123.0011 | 59.9167 | 59.8434
256.3281 | 123.3124 | -59.9808 | 62.9471 | -0.1368 | 0.0013523 | 0.065063 | 0.076736 | 0.0010019 | -0.00053832 | 0.00050193 | -0.018066 | 0.00116 | 0.064283 | 0.055271 | -0.003858 | 0.0010661 | -0.0029159 | -0.036621 | 62.9196 | -60.1868 | 62.8098 | -59.9625 | -59.8984 | 0.013733 | 0 | 62.9288 | -60.0357 | 63.1027 | -59.9854 | -60.0906 | -59.8572 | -0.20599 | -0.027466 | -0.13733 | 0.018311 | 59.9945 | 0.082398 | 60.2005 | 0.28839 | -0.054932 | -0.018311 | 0.15564 | -0.004578 | 0.1236 | -0.10986 | 0.17853 | -0.054931 | 0.22431 | 122.9965 | 0.050354 | 123.1384 | 123.1064 | 122.9645 | 122.9004 | 122.9095 | -123.1339 | -122.9828 | 122.7905 | 123.0835 | 59.9442 | 59.9808
257.3281 | 123.2025 | -60.0357 | 63.0249 | -0.083389 | 0.0015659 | 0.06485 | 0.078658 | 0.0014291 | 0.00010248 | 7.4734e-05 | -0.057739 | 0.0018008 | 0.062575 | 0.059757 | -0.0032172 | 0.0074747 | -0.00099325 | -0.10986 | 63.002 | -60.1959 | 62.8693 | -60.0037 | -60.3607 | -0.11902 | -0.17853 | 62.9654 | -60.0677 | 62.7594 | -59.8572 | -60.0861 | -59.9213 | -0.16022 | -0.022888 | -0.15564 | 0.032044 | 59.9167 | -0.32501 | 60.0769 | -0.16479 | -0.032043 | -0.059509 | -0.2655 | 0.17853 | 0.11444 | -0.050354 | 0.14648 | -0.018311 | 0.19226 | 123.0652 | 0.21057 | 122.8271 | 123.1979 | 123.0331 | 123.0377 | 123.0011 | -123.2208 | -123.0927 | 122.905 | 122.7951 | 59.9258 | 59.8572
258.3281 | 123.175 | -60.0266 | 62.9929 | -0.11391 | 0.00092492 | 0.066559 | 0.078231 | -0.0026297 | 0.00074348 | 0.00092933 | -0.045532 | 0.00116 | 0.064924 | 0.069583 | -0.0036444 | 0.0014933 | -0.00056605 | -0.064087 | 63.0066 | -60.1913 | 62.8738 | -59.9945 | -60.3424 | -0.11902 | -0.15564 | 62.9562 | -60.0815 | 62.9974 | -60.1273 | -60.2097 | -59.9533 | -0.16479 | 0.013733 | -0.11902 | 0.032043 | 59.9075 | -0.31586 | 60.0723 | -0.15106 | -0.054932 | -0.036621 | 0.004578 | -0.10071 | 0.073242 | -0.18311 | 0.12817 | -0.12817 | 0.19684 | 123.0652 | -0.045776 | 123.0789 | 123.1979 | 123.0377 | 123.0331 | 122.9828 | -123.1842 | -123.0743 | 122.9004 | 123.024 | 59.9625 | 59.8709
259.3438 | 123.2758 | -59.9854 | 62.9929 | -0.06813 | 0.00092492 | 0.062286 | 0.077163 | -0.0032705 | -0.0020337 | -0.0014207 | 0.070435 | -0.0014036 | 0.06407 | 0.057621 | -0.0025764 | 0.00085247 | 0.00092935 | -0.004578 | 62.9791 | -60.141 | 63.0066 | -59.8297 | -60.173 | 0.068665 | 0.068665 | 62.9471 | -60.0174 | 63.1256 | -59.9579 | -60.0037 | -59.816 | -0.15564 | -0.013733 | 0.013733 | 0.15564 | 60.054 | -0.18768 | 60.2097 | -0.032044 | -0.032043 | -0.045776 | 0.13275 | 0.027466 | 0.16937 | -0.01831 | 0.20142 | 0.013733 | 0.31128 | 123.1476 | 0.059509 | 123.143 | 123.1201 | 122.9645 | 122.9645 | 122.9324 | -123.1338 | -123.0103 | 122.9919 | 123.111 | 59.9808 | 60.054
260.3281 | 123.2712 | -59.9991 | 62.97 | -0.052872 | 0.0049839 | 0.064422 | 0.075881 | -0.00092073 | -0.00011112 | 0.0011429 | -0.011963 | 0.0013736 | 0.063856 | 0.065097 | -0.005567 | 0.0029887 | -0.00099325 | -0.10071 | 62.9105 | -60.1868 | 63.002 | -59.8206 | -60.2234 | -0.032043 | -0.018311 | 62.9379 | -60.0174 | 63.1027 | -59.9991 | -60.0815 | -59.8663 | -0.18768 | -0.05951 | 0.032043 | 0.17853 | 59.967 | -0.2243 | 60.1547 | -0.036621 | -0.018311 | -0.032044 | 0.13275 | 0 | 0.13275 | -0.082398 | 0.15106 | -0.064087 | 0.36621 | 123.1888 | 0.018311 | 123.1201 | 123.0972 | 122.9553 | 122.9095 | 122.937 | -123.1567 | -122.9874 | 123.0011 | 123.1018 | 59.8984 | 59.9808
261.3281 | 123.1705 | -60.0449 | 63.0066 | -0.037613 | 0.00049772 | 0.065063 | 0.078658 | 0.00078827 | -0.0013929 | 0.0019973 | -0.079102 | -0.0016172 | 0.064924 | 0.067234 | -0.006208 | 0.0025613 | -0.0022751 | -0.086975 | 62.9974 | -60.228 | 62.8738 | -60.0311 | -60.3607 | -0.11444 | -0.4715 | 62.915 | -60.0952 | 63.0157 | -60.1547 | -60.2005 | -59.9625 | -0.18311 | -0.009155 | -0.13275 | 0.013733 | 59.9304 | -0.31586 | 60.1135 | -0.13275 | -0.050354 | -0.091553 | 0.009155 | -0.10986 | 0.082398 | -0.15564 | 0.13275 | -0.10528 | 0.19684 | 123.1018 | -0.059509 | 123.111 | 123.2254 | 123.0103 | 123.0423 | 122.9599 | -123.2346 | -123.1018 | 122.9187 | 123.0606 | 59.9579 | 59.5734
262.3281 | 123.2986 | -60.0311 | 62.9425 | -0.07576 | -0.00057028 | 0.062286 | 0.078872 | -0.0017751 | 0.00074348 | -0.0016343 | -0.057739 | -0.00097617 | 0.064497 | 0.066379 | -0.0023626 | 0.0023477 | -0.00099325 | -0.11444 | 62.9837 | -60.1959 | 62.9288 | -59.9442 | -60.3012 | -0.07782 | -0.10986 | 62.9425 | -60.0586 | 63.0661 | -60.0311 | -60.1044 | -59.8801 | -0.16479 | 0.041199 | -0.013733 | 0.086975 | 59.9533 | -0.27008 | 60.1181 | -0.10529 | -0.027466 | 0 | 0.1236 | 0 | 0.15106 | -0.073242 | 0.17853 | -0.045776 | 0.25177 | 123.1247 | 0.027466 | 123.1247 | 123.1796 | 123.0011 | 123.0148 | 122.9736 | -123.1384 | -123.0011 | 122.9599 | 123.0972 | 59.9167 | 59.9213
263.3281 | 123.1842 | -60.0174 | 63.0066 | -0.12154 | -0.00078408 | 0.064209 | 0.078445 | -0.0026297 | -0.0018201 | 0.00092933 | -0.060791 | 9.1834e-05 | 0.064711 | 0.065097 | -0.0036444 | 0.0025613 | 0.0015701 | -0.064087 | 63.0066 | -60.173 | 62.8922 | -59.9991 | -60.3516 | -0.10071 | -0.15106 | 62.9974 | -60.0449 | 62.9791 | -60.1364 | -60.2509 | -59.9762 | -0.15564 | 0 | -0.11444 | 0.018311 | 59.9167 | -0.33417 | 60.0723 | -0.17853 | -0.027466 | -0.009155 | -0.027466 | -0.11902 | 0.041199 | -0.23346 | 0.068665 | -0.20599 | 0.17395 | 123.0652 | -0.091553 | 123.024 | 123.1796 | 123.0423 | 123.024 | 123.0148 | -123.1796 | -123.0515 | 122.9095 | 122.9965 | 59.9533 | 59.8663
264.3438 | 123.3307 | -59.9945 | 63.002 | -0.037613 | 0.00092492 | 0.062927 | 0.072677 | -0.0017751 | -0.00032472 | -0.0035569 | 0.036865 | -0.00033537 | 0.063429 | 0.063602 | -0.0025764 | 0.00021147 | 0.0032791 | -0.009155 | 62.9974 | -60.1273 | 63.0066 | -59.8251 | -60.1776 | 0.068665 | 0.064087 | 62.9333 | -60.0128 | 63.1027 | -59.935 | -60.0266 | -59.8297 | -0.13275 | -0.004577 | 0.004578 | 0.16937 | 60.0632 | -0.18311 | 60.1959 | -0.050354 | -0.01831 | -0.068664 | 0.10071 | 0.059509 | 0.16479 | -0.032043 | 0.1831 | -0.013733 | 0.30212 | 123.1338 | 0.077819 | 123.1155 | 123.1247 | 122.9462 | 122.9919 | 122.9279 | -123.1293 | -123.0148 | 123.0011 | 123.0972 | 59.9854 | 60.0586
265.3281 | 123.1522 | -60.0403 | 63.0157 | -0.091019 | 0.00071132 | 0.06549 | 0.078231 | 0.0035653 | 0.00010248 | 0.0017837 | -0.079102 | 0.002228 | 0.062788 | 0.062107 | -0.0032172 | 0.0038431 | 0.0030655 | -0.059509 | 62.97 | -60.1868 | 62.9379 | -59.9442 | -60.3149 | -0.068665 | -0.091553 | 62.9791 | -60.0586 | 62.9974 | -60.1089 | -60.2142 | -59.935 | -0.14648 | -0.045776 | -0.07782 | 0.09613 | 59.9716 | -0.27466 | 60.1181 | -0.12817 | -0.018311 | -0.036621 | -0.01831 | -0.068665 | 0.10529 | -0.17395 | 0.1236 | -0.15564 | 0.24262 | 123.1247 | -0.050354 | 123.056 | 123.1567 | 123.0377 | 123.0103 | 123.0194 | -123.2025 | -123.0743 | 122.9782 | 123.0377 | 59.9808 | 59.9487
266.3281 | 123.3078 | -59.9625 | 62.9791 | -0.10628 | 0.0015659 | 0.06485 | 0.078658 | 0.0014291 | 0.00095708 | 0.0011429 | -0.021118 | 0.0015872 | 0.064924 | 0.060825 | -0.0034308 | 0.0019205 | -0.0012071 | -0.018311 | 62.9608 | -60.1822 | 63.002 | -59.8663 | -60.2325 | -0.041199 | -0.045776 | 62.915 | -60.0357 | 63.0661 | -59.9304 | -60.1227 | -59.8709 | -0.21973 | -0.018311 | 0.022888 | 0.09613 | 59.9213 | -0.27008 | 60.141 | -0.050354 | -0.073243 | -0.064087 | 0.086975 | 0.032043 | 0.091552 | -0.16022 | 0.16479 | -0.086975 | 0.31586 | 123.1842 | 0.10529 | 123.1018 | 123.143 | 122.9507 | 122.9233 | 122.8775 | -123.1613 | -123.0148 | 122.9645 | 123.0286 | 59.9442 | 59.9167
267.3281 | 123.1567 | -60.0449 | 62.9929 | -0.091019 | 0.0015659 | 0.063568 | 0.076308 | 0.0010019 | -0.00011112 | -0.0014207 | -0.079102 | -0.0014036 | 0.065138 | 0.064456 | -0.0034308 | 0.0044839 | 0.00028835 | -0.07782 | 62.9929 | -60.2142 | 62.9013 | -59.9854 | -60.3241 | -0.11444 | -0.15564 | 62.9745 | -60.0632 | 62.9883 | -60.1318 | -60.2509 | -59.9716 | -0.16937 | 0 | -0.091553 | 0.059509 | 59.9304 | -0.27924 | 60.0998 | -0.10986 | -0.01831 | -0.018311 | -0.004578 | -0.086975 | 0.073242 | -0.20599 | 0.091552 | -0.18768 | 0.22888 | 123.1155 | -0.068665 | 123.0515 | 123.2071 | 123.0377 | 123.0377 | 123.0194 | -123.2071 | -123.056 | 122.9462 | 123.0331 | 59.967 | 59.8892
268.3281 | 123.2254 | -60.0037 | 62.9837 | -0.060501 | 7.0518e-05 | 0.061859 | 0.076095 | -6.6126e-05 | 0.0011707 | -0.0012071 | -0.048584 | 0.0015872 | 0.065352 | 0.064884 | -0.0030036 | 0.0032023 | 0.0017837 | -0.082397 | 62.9837 | -60.2234 | 62.883 | -59.9945 | -60.3333 | -0.10986 | -0.14648 | 62.9608 | -60.0677 | 63.0203 | -60.0906 | -60.1868 | -59.935 | -0.21973 | 0 | -0.10071 | 0.009155 | 59.8938 | -0.32959 | 60.1135 | -0.10986 | -0.064087 | -0.022889 | 0.036621 | -0.086975 | 0.068664 | -0.18311 | 0.13275 | -0.11902 | 0.22888 | 123.1064 | -0.022888 | 123.0881 | 123.2071 | 123.0286 | 122.9874 | 122.9645 | -123.2071 | -123.0515 | 122.8867 | 123.024 | 59.9213 | 59.8572
269.3438 | 123.2483 | -59.9579 | 62.97 | -0.060501 | -0.0029203 | 0.063781 | 0.074599 | -0.0049795 | -0.0011791 | -0.00035247 | 0.052124 | -0.00012177 | 0.063643 | 0.05997 | -0.0030036 | 0.00042507 | -0.0016343 | -0.073242 | 62.9608 | -60.141 | 63.0615 | -60.0494 | -60.1593 | -0.018311 | -0.086975 | 62.9105 | -60.0311 | 63.0432 | -60.0403 | -60.1181 | -59.8801 | -0.1831 | -0.009156 | 0.091552 | -0.091552 | 59.9396 | -0.20142 | 60.1227 | -0.018311 | -0.073242 | -0.05951 | 0.073242 | -0.082397 | 0.07782 | -0.16022 | 0.15106 | -0.086975 | 0.091553 | 123.2025 | -0.009155 | 123.0743 | 123.1018 | 122.9416 | 122.9187 | 122.8683 | -123.111 | -123.0011 | 123.0194 | 123.0011 | 59.8846 | 59.8709
270.3281 | 123.175 | -60.0174 | 63.0066 | -0.35042 | 0.0013523 | 0.061645 | 0.078231 | 0.0012155 | -0.0020337 | -0.00013887 | -0.069946 | 0.00094643 | 0.064924 | 0.05698 | -0.0036444 | 0.0038431 | 0.0017837 | 0.1236 | 62.9883 | -60.2142 | 62.9196 | -59.9625 | -60.3882 | -0.11444 | -0.14648 | 62.9562 | -60.0723 | 62.9974 | -60.1181 | -60.2188 | -59.9579 | -0.19684 | -0.018311 | -0.086975 | 0.054932 | 59.903 | -0.37079 | 60.0998 | -0.17395 | -0.054932 | -0.050354 | -0.009155 | -0.10071 | 0.059509 | -0.20142 | 0.11444 | -0.14648 | 0.25177 | 123.1338 | -0.045776 | 123.0698 | 123.2025 | 123.0286 | 123.0057 | 122.9736 | -123.2208 | -123.0789 | 122.937 | 123.0148 | 60.141 | 59.8709
271.3281 | 123.2162 | -60.0082 | 63.0112 | -0.098648 | 0.0011385 | 0.065277 | 0.076736 | -0.0011343 | -0.00075192 | -0.00077967 | -0.048584 | -0.00097617 | 0.063429 | 0.063175 | -0.0025764 | 0.00042507 | -0.0027023 | 0.018311 | 63.002 | -60.1822 | 62.97 | -59.8755 | -60.2371 | 0.027466 | 0.041199 | 63.002 | -60.0082 | 63.1119 | -60.0494 | -60.0723 | -59.8618 | -0.17395 | -0.009155 | -0.041198 | 0.13275 | 60.0357 | -0.22888 | 60.2097 | -0.054932 | 0 | -0.009155 | 0.10071 | -0.041198 | 0.14648 | -0.064087 | 0.14648 | -0.064087 | 0.3067 | 123.1522 | -0.041198 | 123.1201 | 123.1842 | 123.0103 | 123.0103 | 123.0103 | -123.1934 | -123.0194 | 122.9782 | 123.1201 | 60.0266 | 60.0494
272.3281 | 123.1476 | -60.0266 | 63.0249 | -0.091019 | 0.00049772 | 0.066772 | 0.078445 | 0.00014747 | -0.0013929 | -0.0033433 | -0.069946 | -0.00054897 | 0.064497 | 0.065311 | -0.0023626 | 0.0098245 | -0.00035245 | -0.07782 | 63.002 | -60.2188 | 62.8693 | -59.9991 | -60.3653 | -0.1236 | -0.17853 | 62.97 | -60.0632 | 62.8143 | -60.1685 | -59.9487 | -59.8297 | -0.19226 | -0.022888 | -0.15564 | 0.027466 | 59.903 | -0.33875 | 60.0952 | -0.14648 | -0.036621 | -0.054931 | -0.21057 | -0.14191 | 0.19684 | 0.07782 | 0.23346 | 0.11444 | 0.21973 | 123.0881 | -0.10529 | 122.8775 | 123.2208 | 123.0331 | 123.0286 | 122.9965 | -123.2437 | -123.0881 | 122.8958 | 122.8409 | 59.9487 | 59.848
273.3281 | 123.2071 | -60.0494 | 63.002 | -0.060501 | 0.0017795 | 0.06485 | 0.077163 | -0.0013479 | -0.00096552 | 0.00028833 | -0.063843 | 0.00094643 | 0.065779 | 0.063816 | -0.0034308 | 0.0034159 | -0.00013885 | 0 | 63.0203 | -60.1639 | 62.9425 | -59.903 | -60.2875 | -0.022888 | -0.036621 | 62.9791 | -60.0266 | 63.0157 | -60.0677 | -60.1822 | -59.935 | -0.11444 | 0.018311 | -0.059509 | 0.14648 | 60.0266 | -0.23804 | 60.141 | -0.1236 | 0.022888 | -0.022888 | 0.013733 | -0.018311 | 0.11444 | -0.13275 | 0.091552 | -0.15564 | 0.26093 | 123.1064 | -0.041199 | 123.0423 | 123.1842 | 123.0057 | 123.0698 | 123.0286 | -123.1659 | -123.0286 | 122.9919 | 123.0652 | 60.0494 | 60.0128
274.3281 | 123.2849 | -59.9854 | 62.9425 | -0.098648 | 0.00028412 | 0.064636 | 0.078231 | -0.00049353 | -0.00053832 | -0.0018479 | -0.027222 | 0.0020144 | 0.065565 | 0.058689 | -0.0032172 | 0.0027751 | 0.00071555 | -0.091553 | 62.97 | -60.1959 | 62.9425 | -59.8938 | -60.2875 | -0.054932 | -0.07782 | 62.9105 | -60.0449 | 63.0844 | -60.0174 | -60.1089 | -59.8526 | -0.21057 | 0.027466 | 0 | 0.091553 | 59.9304 | -0.30212 | 60.141 | -0.091553 | -0.059509 | -0.032044 | 0.14191 | -0.032043 | 0.13275 | -0.1236 | 0.19226 | -0.064087 | 0.30212 | 123.1384 | 0.027466 | 123.1293 | 123.1659 | 122.9553 | 122.9553 | 122.8958 | -123.1384 | -122.9874 | 122.9279 | 123.0698 | 59.8938 | 59.9075
275.3281 | 123.2117 | -59.9945 | 63.002 | -0.052872 | 7.0518e-05 | 0.063141 | 0.077376 | 0.0016427 | -0.0011791 | -0.0035569 | -0.07605 | 0.00073263 | 0.064924 | 0.061252 | -0.0030036 | 0.0017069 | -0.0027023 | -0.013733 | 63.0112 | -60.1868 | 62.9745 | -59.8618 | -60.2737 | 0.009155 | 0.013733 | 62.9837 | -60.0311 | 63.0615 | -60.0266 | -60.1181 | -59.9213 | -0.19226 | 0.009155 | -0.027466 | 0.13275 | 60.0037 | -0.27924 | 60.1959 | -0.086975 | -0.036621 | -0.01831 | 0.059509 | -0.032043 | 0.073242 | -0.1236 | 0.10986 | -0.086975 | 0.32501 | 123.1613 | 0.004578 | 123.0927 | 123.1979 | 123.0148 | 123.0057 | 122.9782 | -123.1888 | -123.0331 | 122.9691 | 123.056 | 59.9808 | 60.0082
276.3281 | 123.1705 | -60.022 | 62.9883 | -0.091019 | 0.0011385 | 0.0625 | 0.076736 | 0.0024973 | 0.0011707 | 0.00028833 | -0.057739 | 0.00116 | 0.063002 | 0.067234 | -0.004499 | 0.0040567 | -0.0018479 | -0.059509 | 62.9929 | -60.1959 | 62.8922 | -59.967 | -60.3287 | -0.086975 | -0.14648 | 62.9791 | -60.0723 | 62.9791 | -60.1227 | -60.2417 | -59.9808 | -0.17395 | 0.004578 | -0.09613 | 0.054932 | 59.935 | -0.3067 | 60.1089 | -0.13275 | -0.050354 | -0.009155 | -0.009155 | -0.10071 | 0.041199 | -0.21973 | 0.091553 | -0.16937 | 0.22888 | 123.0881 | -0.050354 | 123.0515 | 123.1888 | 123.0515 | 123.0148 | 123.0011 | -123.1842 | -123.0606 | 122.9141 | 123.0011 | 59.9625 | 59.8755
277.3281 | 123.1934 | -59.967 | 63.0112 | -0.052872 | 0.0019931 | 0.065704 | 0.077804 | 0.0020701 | -0.00011112 | -0.0022751 | -0.048584 | 0.00030543 | 0.065352 | 0.062747 | -0.0017218 | 0.0019205 | 0.00092935 | 0.004578 | 63.0066 | -60.173 | 62.9562 | -59.8709 | -60.228 | 0.022888 | 0.045776 | 62.9791 | -60.0586 | 63.1256 | -60.0449 | -60.1456 | -59.8343 | -0.20599 | -0.004577 | -0.054931 | 0.09613 | 59.9899 | -0.26093 | 60.1959 | -0.054931 | -0.091553 | -0.032043 | 0.11444 | -0.07782 | 0.13275 | -0.17853 | 0.2243 | -0.086975 | 0.30212 | 123.1293 | 0.013733 | 123.1842 | 123.1796 | 123.0377 | 122.9736 | 122.9462 | -123.1842 | -123.0698 | 122.9233 | 123.0927 | 59.9716 | 60.0128
278.3281 | 123.23 | -60.0266 | 63.0386 | -0.098648 | 0.00049772 | 0.066559 | 0.076949 | 0.00057467 | 0.00010248 | -0.0012071 | -0.063843 | 0.0013736 | 0.064497 | 0.057621 | -0.0019354 | 0.0027751 | -0.0012071 | -0.032043 | 62.9929 | -60.1776 | 62.915 | -59.9258 | -60.3058 | -0.045776 | -0.07782 | 62.97 | -60.0494 | 62.9974 | -60.0861 | -60.1868 | -59.9442 | -0.15106 | -0.045776 | -0.1236 | 0.10071 | 59.9808 | -0.27924 | 60.1318 | -0.12817 | -0.022888 | -0.068664 | -0.041198 | -0.05951 | 0.082397 | -0.16022 | 0.10529 | -0.13733 | 0.25177 | 123.0927 | -0.036622 | 123.0469 | 123.1705 | 123.0194 | 123.0194 | 122.9965 | -123.2162 | -123.0881 | 122.9416 | 123.024 | 59.9945 | 59.9487
279.3281 | 123.2712 | -59.967 | 63.0203 | -0.037613 | 0.0015659 | 0.065277 | 0.076949 | 0.00036107 | -0.0028881 | 0.0011429 | -0.030273 | -0.00097617 | 0.062575 | 0.05933 | -0.0030036 | 0.0017069 | -0.00013885 | -0.004578 | 63.0203 | -60.1456 | 62.9471 | -59.8892 | -60.2325 | 0.022888 | 0.027466 | 62.97 | -60.022 | 63.0569 | -60.0174 | -60.1181 | -59.8938 | -0.17853 | 0 | -0.073242 | 0.07782 | 59.9899 | -0.2655 | 60.1685 | -0.086975 | -0.054932 | -0.050354 | 0.036621 | -0.050354 | 0.073242 | -0.15106 | 0.12817 | -0.09613 | 0.25635 | 123.0927 | 0.004578 | 123.0789 | 123.1659 | 122.9919 | 122.9874 | 122.937 | -123.1659 | -123.0423 | 122.9141 | 123.024 | 59.9625 | 59.9945
280.3281 | 123.175 | -60.022 | 63.0478 | -0.045242 | -0.00099768 | 0.064209 | 0.078231 | 0.00014747 | -0.00075192 | -0.0024887 | -0.033325 | -0.00012177 | 0.06407 | 0.066806 | -0.0030036 | 0.0019205 | 0.0011429 | -0.050354 | 62.9929 | -60.1776 | 62.9059 | -59.9579 | -60.3149 | -0.091553 | -0.10529 | 62.9883 | -60.054 | 62.9929 | -60.1044 | -60.1959 | -59.9533 | -0.15564 | -0.054932 | -0.14191 | 0.064087 | 59.9304 | -0.29297 | 60.0861 | -0.13733 | -0.032043 | -0.05951 | -0.054932 | -0.082397 | 0.068665 | -0.17395 | 0.10071 | -0.14191 | 0.21973 | 123.0835 | -0.050354 | 123.0469 | 123.1705 | 123.0423 | 123.0148 | 123.0103 | -123.2254 | -123.1018 | 122.9279 | 123.0148 | 59.9716 | 59.9167
281.3281 | 123.2346 | -59.9716 | 63.0112 | -0.0070953 | 0.0013523 | 0.06485 | 0.076736 | -6.6126e-05 | -0.0024609 | 0.0026383 | -0.030273 | -0.00076257 | 0.064283 | 0.063175 | -0.0023626 | 0.00063867 | -0.00035245 | 0.013733 | 63.0432 | -60.1501 | 62.9562 | -59.8663 | -60.2234 | 0.032043 | 0.064087 | 62.9837 | -60.0449 | 63.0478 | -60.0174 | -60.1318 | -59.903 | -0.17853 | 0.032044 | -0.054931 | 0.10529 | 60.0037 | -0.25177 | 60.1822 | -0.073243 | -0.073242 | -0.027465 | 0.036622 | -0.045776 | 0.068665 | -0.16022 | 0.14191 | -0.086975 | 0.28381 | 123.1064 | 0.027466 | 123.0927 | 123.1934 | 123.0286 | 123.0148 | 122.9553 | -123.1613 | -123.056 | 122.9279 | 123.0194 | 59.9854 | 60.0357
282.3281 | 123.1934 | -60.0082 | 63.002 | -0.060501 | 0.00028412 | 0.064636 | 0.07759 | -0.0013479 | 0.00031608 | 0.0039199 | -0.021118 | 0.00073263 | 0.065565 | 0.059116 | -1.2774e-05 | 0.0014933 | 0.0030655 | -0.091553 | 62.9883 | -60.1913 | 62.8693 | -59.9991 | -60.3561 | -0.11902 | -0.12817 | 62.9562 | -60.0906 | 62.9471 | -60.0311 | -60.2188 | -59.9899 | -0.1831 | -0.013733 | -0.13275 | 0.009156 | 59.8892 | -0.3479 | 60.0723 | -0.1648 | -0.082397 | -0.045776 | -0.054931 | -0.022888 | 0.018311 | -0.21057 | 0.10071 | -0.12817 | 0.19226 | 123.0606 | 0.059509 | 123.0377 | 123.1796 | 123.0469 | 122.9965 | 122.9645 | -123.1934 | -123.0927 | 122.8775 | 122.9553 | 59.9167 | 59.8801
283.3281 | 123.1934 | -59.9854 | 63.0478 | -0.06813 | 0.0028475 | 0.063781 | 0.077376 | -0.0030569 | 0.0013843 | -0.0018479 | 0.00024405 | -0.00033537 | 0.066847 | 0.060825 | -0.003858 | 0.0032023 | -0.00099325 | -0.009155 | 63.0386 | -60.1685 | 62.9425 | -59.9167 | -60.2463 | 0.018311 | 0.013733 | 62.97 | -60.0266 | 63.0295 | -60.0174 | -60.1273 | -59.8892 | -0.1831 | -0.009156 | -0.10529 | 0.068665 | 60.0037 | -0.26093 | 60.1868 | -0.07782 | -0.041198 | -0.07782 | -0.018311 | -0.032043 | 0.096131 | -0.14191 | 0.13733 | -0.10071 | 0.25177 | 123.111 | 0.009155 | 123.056 | 123.2071 | 122.9965 | 123.024 | 122.9553 | -123.2162 | -123.0743 | 122.9279 | 123.0148 | 59.9762 | 59.9991
284.3281 | 123.2483 | -59.9945 | 63.0249 | -0.037613 | 0.0015659 | 0.066345 | 0.076949 | -0.0017751 | -0.00075192 | -0.00035247 | -0.042481 | 0.002228 | 0.063429 | 0.059116 | -0.0042854 | 0.0023477 | -0.00099325 | 0.004578 | 63.0295 | -60.1868 | 62.9608 | -59.8755 | -60.2463 | 0.004578 | -0.004578 | 62.9837 | -60.0266 | 63.0981 | -60.0906 | -60.2005 | -59.9762 | -0.19226 | 0.004578 | -0.064087 | 0.11902 | 59.9991 | -0.25177 | 60.1913 | -0.059509 | -0.032043 | -0.041198 | 0.073243 | -0.09613 | 0.018311 | -0.20599 | 0.050354 | -0.17395 | 0.31128 | 123.1476 | -0.064087 | 123.1247 | 123.2162 | 123.0103 | 123.024 | 122.9782 | -123.2117 | -123.0515 | 122.9553 | 123.0927 | 59.9991 | 59.9899
285.3281 | 123.2117 | -60.0082 | 63.0478 | 0.00053424 | 7.0518e-05 | 0.063781 | 0.077163 | -0.0011343 | -0.00075192 | -0.0012071 | 0.012451 | 0.00073263 | 0.065138 | 0.057621 | -0.00279 | 0.0010661 | 0.0019973 | -0.013733 | 63.0615 | -60.1868 | 62.9242 | -59.9167 | -60.26 | 0.036621 | 0.018311 | 62.9929 | -60.0037 | 63.0066 | -60.0494 | -60.1364 | -59.9258 | -0.17853 | 0.013732 | -0.1236 | 0.091553 | 60.0449 | -0.25177 | 60.2234 | -0.073242 | 0.004578 | -0.054932 | -0.041199 | -0.041198 | 0.082398 | -0.12817 | 0.07782 | -0.13275 | 0.27008 | 123.111 | -0.045776 | 123.0103 | 123.2483 | 122.9965 | 123.0698 | 123.0011 | -123.2346 | -123.0515 | 122.9324 | 123.0148 | 59.9945 | 60.0266
286.3281 | 123.2071 | -59.9808 | 63.0203 | -0.029984 | -0.00035668 | 0.066986 | 0.078231 | -0.0017751 | -0.0018201 | -0.0046249 | -0.018066 | 0.0018008 | 0.064711 | 0.065311 | -0.0047126 | 0.0036295 | -0.00013885 | -0.018311 | 63.0112 | -60.1639 | 62.9425 | -59.9121 | -60.2417 | 0.022888 | 0.032043 | 62.9837 | -60.0174 | 63.0432 | -60.0357 | -60.1364 | -59.8938 | -0.18311 | -0.009156 | -0.07782 | 0.068665 | 60.0037 | -0.26093 | 60.1868 | -0.07782 | -0.036621 | -0.036621 | 0.022888 | -0.054932 | 0.086975 | -0.15564 | 0.1236 | -0.11902 | 0.25177 | 123.1064 | -0.018311 | 123.0606 | 123.175 | 123.0011 | 122.9919 | 122.9645 | -123.1842 | -123.0377 | 122.9233 | 123.024 | 59.9625 | 60.0128
287.3281 | 123.23 | -60.0037 | 63.0249 | -0.060501 | 0.00028412 | 0.063568 | 0.076949 | 0.0018565 | -0.00053832 | -0.0024887 | -0.0028075 | 0.0020144 | 0.065992 | 0.071079 | -0.0023626 | 0.0032023 | -0.00056605 | -0.004578 | 63.0112 | -60.1501 | 63.0112 | -59.935 | -60.379 | 0.018311 | 0.022888 | 62.9837 | -60.0128 | 63.0249 | -60.0357 | -60.1135 | -59.8846 | -0.14648 | -0.013733 | -0.013733 | 0.068664 | 60.022 | -0.37537 | 60.1685 | -0.22888 | -0.009155 | -0.041198 | 0 | -0.032044 | 0.11902 | -0.10986 | 0.12817 | -0.10071 | 0.21515 | 123.1613 | -0.022889 | 123.0377 | 123.1613 | 122.9965 | 123.0148 | 122.9874 | -123.175 | -123.0377 | 123.0148 | 123.0286 | 59.9991 | 60.0266
288.3281 | 123.1659 | -60.022 | 63.0203 | -0.014725 | 0.00092492 | 0.06549 | 0.078658 | -0.00070713 | -0.00096552 | -0.00013887 | -0.063843 | 9.1834e-05 | 0.063429 | 0.062534 | -0.0032172 | 0.0029887 | 0.0028519 | -0.032043 | 63.002 | -60.1776 | 62.9242 | -59.9304 | -60.3012 | -0.073242 | -0.027466 | 62.9608 | -60.0403 | 63.0112 | -60.1044 | -60.1959 | -59.9396 | -0.15564 | -0.018311 | -0.096131 | 0.091553 | 59.9487 | -0.27923 | 60.1044 | -0.1236 | -0.01831 | -0.05951 | -0.009156 | -0.082397 | 0.082398 | -0.17395 | 0.10071 | -0.15564 | 0.24719 | 123.1018 | -0.064087 | 123.0515 | 123.1796 | 123.0011 | 123.024 | 122.9828 | -123.1979 | -123.0606 | 122.9462 | 123.0331 | 59.9899 | 59.9945
289.3281 | 123.2025 | -59.9854 | 63.0295 | -0.052872 | 0.00049772 | 0.064209 | 0.07759 | 0.0016427 | 0.0015979 | -0.00013887 | 0.00024405 | 0.0015872 | 0.064283 | 0.061252 | -0.003858 | 0.0010661 | 0.00071555 | -0.022888 | 63.0432 | -60.141 | 62.9059 | -59.935 | -60.2692 | 0.022888 | 0.013733 | 63.0203 | -60.022 | 63.0203 | -60.0357 | -60.1547 | -59.9121 | -0.15564 | 0.013733 | -0.1236 | 0.050354 | 60.0082 | -0.28381 | 60.1639 | -0.12817 | -0.036621 | -0.009155 | -0.009155 | -0.050354 | 0.073243 | -0.16937 | 0.10986 | -0.13275 | 0.20599 | 123.0469 | -0.013733 | 123.0423 | 123.1842 | 123.0423 | 123.0286 | 123.0057 | -123.1705 | -123.0515 | 122.8912 | 123.0057 | 59.9625 | 59.9991
290.3281 | 123.1567 | -60.0266 | 63.0112 | -0.098648 | -0.00014308 | 0.065918 | 0.077804 | -0.0013479 | -0.00053832 | 0.00050193 | -0.042481 | 0.0020144 | 0.063429 | 0.063816 | -0.00279 | 0.0023477 | -0.0016343 | -0.10529 | 63.002 | -60.1868 | 62.9059 | -59.9487 | -60.3241 | -0.082397 | -0.10529 | 62.9791 | -60.0677 | 62.9745 | -60.1181 | -60.2371 | -59.9442 | -0.16022 | -0.009155 | -0.10529 | 0.07782 | 59.9442 | -0.29755 | 60.1044 | -0.13733 | -0.041199 | -0.032043 | -0.036621 | -0.091553 | 0.082397 | -0.21057 | 0.1236 | -0.16937 | 0.23804 | 123.0927 | -0.050354 | 123.0423 | 123.1888 | 123.0469 | 123.0286 | 123.0057 | -123.1979 | -123.0789 | 122.9324 | 123.0011 | 59.9213 | 59.9213
291.3281 | 123.2162 | -60.0128 | 63.0569 | -0.07576 | 0.00092492 | 0.062072 | 0.078231 | -0.00049353 | 0.0015979 | -0.0044113 | 0.00024405 | 0.00094643 | 0.064497 | 0.055057 | -0.0019354 | 0.00085247 | 0.0034927 | -0.013733 | 63.0432 | -60.1685 | 62.9105 | -59.9533 | -60.2646 | 0.022888 | 0 | 63.0066 | -60.0494 | 62.9974 | -60.0403 | -60.1547 | -59.9121 | -0.15564 | -0.013733 | -0.14649 | 0.059509 | 60.0357 | -0.25177 | 60.1913 | -0.09613 | -0.036621 | -0.050354 | -0.059509 | -0.027466 | 0.10071 | -0.14191 | 0.13733 | -0.10529 | 0.21515 | 123.0789 | 0.009155 | 123.0469 | 123.2117 | 123.056 | 123.056 | 123.0194 | -123.2254 | -123.1064 | 122.9233 | 123.0103 | 59.9991 | 60.0128
292.3281 | 123.2071 | -60.0082 | 63.0478 | -0.052872 | 0.0017795 | 0.065277 | 0.077163 | -0.0026297 | -0.0011791 | 0.0022109 | -0.021118 | 0.002228 | 0.063643 | 0.064884 | -0.0019354 | 0.0034159 | -0.0012071 | -0.027466 | 63.0432 | -60.1501 | 62.915 | -59.9304 | -60.2646 | 0.013733 | 0.009155 | 63.0112 | -60.022 | 63.0341 | -60.0311 | -60.1364 | -59.9167 | -0.14191 | -0.004578 | -0.13275 | 0.07782 | 60.022 | -0.25635 | 60.1639 | -0.11444 | -0.013733 | -0.036622 | -0.013733 | -0.022888 | 0.091553 | -0.12817 | 0.10529 | -0.11444 | 0.21973 | 123.0652 | -0.009155 | 123.056 | 123.1934 | 123.0331 | 123.0515 | 123.0194 | -123.1979 | -123.0698 | 122.9233 | 123.0423 | 59.9808 | 60.0174
293.3281 | 123.1979 | -60.0174 | 63.0569 | -0.11391 | 0.0024203 | 0.061645 | 0.078445 | -0.0049795 | -0.0026745 | -0.0012071 | 0.02771 | 0.00030543 | 0.065138 | 0.064884 | -0.0034308 | 0.0023477 | -0.00013885 | -0.027466 | 63.0386 | -60.141 | 62.9242 | -59.9213 | -60.2554 | 0.022888 | 0.013733 | 63.0249 | -60.0128 | 63.0157 | -60.0586 | -60.1456 | -59.9167 | -0.1236 | -0.018311 | -0.13275 | 0.09613 | 60.0403 | -0.23804 | 60.1639 | -0.11444 | 0.004578 | -0.032044 | -0.041199 | -0.041199 | 0.10071 | -0.12817 | 0.09613 | -0.13275 | 0.21973 | 123.0652 | -0.045777 | 123.0286 | 123.1796 | 123.0377 | 123.056 | 123.0423 | -123.1979 | -123.0698 | 122.9416 | 123.0331 | 59.9899 | 60.0311
294.3281 | 123.2346 | -60.0082 | 63.0203 | -0.07576 | 0.0030613 | 0.063354 | 0.078231 | -0.0015615 | -0.0011791 | -0.0014207 | -0.036377 | 0.0024416 | 0.065779 | 0.067661 | -0.0025764 | 0.0017069 | -0.0020615 | 0.013733 | 63.0157 | -60.173 | 62.9745 | -59.8846 | -60.2417 | 0.004578 | 0.036621 | 62.9883 | -60.0311 | 63.0524 | -60.022 | -60.1318 | -59.8938 | -0.16479 | -0.004578 | -0.045777 | 0.1236 | 60.0128 | -0.23346 | 60.1776 | -0.068664 | -0.022888 | -0.032044 | 0.032043 | -0.013733 | 0.11444 | -0.1236 | 0.13733 | -0.10071 | 0.28839 | 123.1476 | 0.009155 | 123.0835 | 123.1888 | 123.0194 | 123.024 | 122.9965 | -123.1934 | -123.0515 | 122.9828 | 123.0606 | 60.022 | 60.0449
295.3281 | 123.1842 | -60.022 | 63.0707 | -0.029984 | 0.0011385 | 0.063568 | 0.077163 | 0.0039927 | -0.0020337 | -0.0014207 | 0.018555 | 0.0020144 | 0.064497 | 0.062747 | -0.0030036 | 0.0019205 | 0.0011429 | -0.009155 | 63.0478 | -60.1501 | 62.9242 | -59.935 | -60.2692 | 0.013733 | 0.004578 | 62.9837 | -60.022 | 63.0203 | -60.0494 | -60.1593 | -59.9258 | -0.12817 | -0.022888 | -0.14648 | 0.086975 | 60.0357 | -0.24719 | 60.1639 | -0.11902 | 0 | -0.086975 | -0.050354 | -0.027465 | 0.096131 | -0.13733 | 0.096131 | -0.13733 | 0.21515 | 123.0743 | -0.027465 | 123.0423 | 123.1979 | 123.0057 | 123.0698 | 123.0057 | -123.2208 | -123.0927 | 122.9462 | 123.0423 | 60.0128 | 60.0266
296.3281 | 123.23 | -60.0037 | 63.0341 | -0.029984 | -0.00014308 | 0.065063 | 0.07759 | -6.6126e-05 | -0.0024609 | 0.00028833 | -0.030273 | 9.1834e-05 | 0.062788 | 0.055698 | -0.0034308 | 0.0012797 | 0.0028519 | 0 | 63.0157 | -60.1776 | 62.9654 | -59.8801 | -60.2509 | 0.022888 | 0.041199 | 62.97 | -60.0403 | 63.0661 | -60.0174 | -60.1273 | -59.8938 | -0.17395 | -0.018311 | -0.068665 | 0.1236 | 60.0266 | -0.24719 | 60.2005 | -0.073242 | -0.036621 | -0.064087 | 0.032043 | -0.013733 | 0.10986 | -0.1236 | 0.14648 | -0.086975 | 0.29755 | 123.143 | 0.022888 | 123.1064 | 123.1934 | 123.0103 | 123.0194 | 122.9736 | -123.2117 | -123.0743 | 122.9691 | 123.0698 | 60.0037 | 60.0449
297.3281 | 123.1979 | -59.9945 | 63.0478 | -0.06813 | 0.00049772 | 0.064636 | 0.078445 | -0.0030569 | 0.0018115 | -0.0018479 | 0.015503 | 0.00116 | 0.064924 | 0.062961 | -0.00065377 | -0.00042933 | -0.0018479 | -0.004578 | 63.0615 | -60.1547 | 62.9059 | -59.9487 | -60.26 | 0.022888 | 0.004578 | 63.0112 | -60.022 | 63.0157 | -60.054 | -60.1639 | -59.9258 | -0.16022 | 0.013732 | -0.14191 | 0.045777 | 60.0174 | -0.2655 | 60.1776 | -0.10529 | -0.027466 | -0.036622 | -0.032044 | -0.059509 | 0.068665 | -0.16937 | 0.096131 | -0.14191 | 0.20599 | 123.0606 | -0.032043 | 123.0377 | 123.2162 | 123.0331 | 123.056 | 123.0057 | -123.2025 | -123.0698 | 122.9004 | 123.0103 | 59.9899 | 59.9991
298.3281 | 123.1934 | -59.9899 | 63.0341 | -0.045242 | 0.0028475 | 0.063781 | 0.078658 | 0.0020701 | -0.0011791 | -0.0027023 | -0.02417 | 0.00051903 | 0.063215 | 0.066806 | -0.0036444 | 0.0012797 | 7.4746e-05 | 0.018311 | 63.0524 | -60.1639 | 62.9654 | -59.8984 | -60.2417 | 0.027466 | 0.045776 | 62.9974 | -60.0082 | 63.0478 | -60.0174 | -60.1273 | -59.8984 | -0.17395 | 0.01831 | -0.068665 | 0.091553 | 60.0174 | -0.25177 | 60.1913 | -0.07782 | -0.018311 | -0.036621 | 0.013733 | -0.027466 | 0.091553 | -0.13733 | 0.10986 | -0.11902 | 0.2655 | 123.1293 | -0.009155 | 123.056 | 123.2162 | 123.0057 | 123.0423 | 122.9874 | -123.1979 | -123.0423 | 122.9553 | 123.0377 | 60.0082 | 60.0357
299.3281 | 123.1842 | -60.0082 | 63.0615 | -0.037613 | 0.0019931 | 0.063568 | 0.076736 | -0.0022025 | -0.0024609 | -0.00013887 | 0.021606 | -0.00012177 | 0.065779 | 0.063175 | -0.0059942 | 0.0027751 | 0.0026383 | 0.041199 | 63.0249 | -60.141 | 62.9883 | -59.8434 | -60.1913 | 0.091553 | 0.14191 | 62.9974 | -59.9854 | 63.0157 | -60.0082 | -60.1318 | -59.8892 | -0.13275 | -0.036621 | -0.073242 | 0.16479 | 60.0998 | -0.1831 | 60.2325 | -0.050354 | 0.022888 | -0.064086 | -0.045776 | 0 | 0.11902 | -0.1236 | 0.096131 | -0.14648 | 0.29755 | 123.1293 | -0.022888 | 123.0011 | 123.1659 | 122.9828 | 123.0331 | 123.0057 | -123.2025 | -123.0469 | 122.9965 | 123.024 | 60.0494 | 60.1501
300.3281 | 123.2529 | -60.0037 | 63.0249 | 0.015793 | 0.0013523 | 0.063354 | 0.076949 | 0.0029245 | -0.00011112 | -0.0012071 | -0.027222 | 0.0013736 | 0.065138 | 0.064884 | -0.0032172 | 0.0023477 | -0.0027023 | 0.004578 | 63.0295 | -60.1822 | 62.9288 | -59.903 | -60.2875 | 0.009155 | 0.004578 | 62.97 | -60.0357 | 63.0432 | -60.022 | -60.1227 | -59.8984 | -0.17853 | 0.004578 | -0.09613 | 0.10071 | 60.0128 | -0.28381 | 60.1913 | -0.10529 | -0.032044 | -0.054931 | 0.018311 | -0.018311 | 0.10529 | -0.11902 | 0.13733 | -0.086975 | 0.27924 | 123.111 | 0.013733 | 123.0789 | 123.2117 | 123.0057 | 123.0331 | 122.9736 | -123.2071 | -123.0606 | 122.9324 | 123.0469 | 60.0082 | 60.0082
301.3281 | 123.1979 | -59.9808 | 63.0661 | -0.037613 | 0.0011385 | 0.064422 | 0.078445 | 0.0020701 | 0.00031608 | -0.0027023 | -0.0058593 | 0.00030543 | 0.065779 | 0.053775 | -0.0040716 | 0.0010661 | -0.0012071 | -0.009155 | 63.0569 | -60.1501 | 62.915 | -59.9396 | -60.2646 | 0.018311 | 0.009155 | 63.0066 | -60.0357 | 62.9974 | -60.0632 | -60.173 | -59.9167 | -0.16937 | -0.009155 | -0.15106 | 0.041199 | 59.9991 | -0.28381 | 60.1685 | -0.11444 | -0.054932 | -0.059509 | -0.068664 | -0.082397 | 0.064087 | -0.19226 | 0.11902 | -0.13733 | 0.21057 | 123.0652 | -0.027465 | 123.0331 | 123.2071 | 123.0423 | 123.0377 | 122.9874 | -123.2162 | -123.1018 | 122.8958 | 122.9782 | 59.9716 | 59.9899
302.3281 | 123.2254 | -60.0037 | 63.0295 | -0.06813 | 0.00071132 | 0.063354 | 0.078872 | 0.0044199 | -0.00075192 | -0.00099327 | -0.027222 | 0.0013736 | 0.061293 | 0.060825 | -0.0023626 | 0.0044839 | 0.0030655 | 0.013733 | 63.0112 | -60.1868 | 62.9517 | -59.8846 | -60.26 | -0.009155 | 0.022888 | 62.9791 | -60.0357 | 63.0341 | -60.0403 | -60.1364 | -59.8892 | -0.18311 | -0.018311 | -0.07782 | 0.11902 | 59.9945 | -0.25635 | 60.1776 | -0.073242 | -0.032044 | -0.050354 | 0.004578 | -0.036621 | 0.11444 | -0.13275 | 0.14648 | -0.10071 | 0.30212 | 123.1384 | -0.004577 | 123.0698 | 123.1979 | 123.0148 | 123.0148 | 122.9828 | -123.2162 | -123.0652 | 122.9553 | 123.0377 | 60.0174 | 60.0266
303.3281 | 123.2025 | -60.0128 | 63.0478 | -0.07576 | 0.0015659 | 0.062927 | 0.07524 | -0.0013479 | -0.00096552 | 0.00071573 | 0.024658 | 0.00094643 | 0.063429 | 0.061893 | -0.0025764 | 0.00085247 | 0.00092935 | -0.018311 | 63.0386 | -60.1547 | 62.9196 | -59.9258 | -60.2692 | 0.018311 | 0.022888 | 63.0157 | -60.0311 | 63.0157 | -60.054 | -60.141 | -59.935 | -0.14191 | -0.009156 | -0.12817 | 0.086975 | 60.0311 | -0.25635 | 60.173 | -0.11444 | -0.018311 | -0.032044 | -0.032044 | -0.041199 | 0.077819 | -0.12817 | 0.09613 | -0.10986 | 0.22888 | 123.0743 | -0.022888 | 123.0469 | 123.1934 | 123.0469 | 123.0515 | 123.0286 | -123.2025 | -123.0789 | 122.9324 | 123.0286 | 59.9945 | 60.0357
304.3281 | 123.23 | -59.9945 | 63.0249 | -0.045242 | 0.0011385 | 0.065277 | 0.076736 | -0.0013479 | -0.0045971 | -0.0018479 | -0.011963 | 0.00073263 | 0.064711 | 0.066806 | -0.0042854 | 0.00042507 | 0.0026383 | -0.027466 | 63.0157 | -60.1822 | 62.9425 | -59.9304 | -60.2417 | 0.018311 | 0.022888 | 62.9883 | -60.022 | 63.0569 | -60.0311 | -60.1364 | -59.8892 | -0.18768 | -0.009155 | -0.082397 | 0.064087 | 60.0128 | -0.24719 | 60.2005 | -0.059509 | -0.027466 | -0.036621 | 0.032044 | -0.036621 | 0.10529 | -0.14191 | 0.13275 | -0.11444 | 0.25177 | 123.1247 | -0.009155 | 123.0789 | 123.1979 | 123.0103 | 123.0103 | 122.9828 | -123.2071 | -123.0469 | 122.937 | 123.0515 | 59.967 | 60.0174
305.3281 | 123.1796 | -60.0082 | 63.0432 | -0.091019 | 0.0013523 | 0.061645 | 0.076095 | -0.0019889 | 0.00010248 | -0.00099327 | 0.015503 | 0.00073263 | 0.065992 | 0.055912 | -0.002149 | 0.0032023 | -0.00056605 | 0.022888 | 63.0341 | -60.0998 | 62.9608 | -59.8801 | -60.2234 | 0.050354 | 0.054932 | 63.002 | -60.0128 | 63.0112 | -60.0266 | -60.1364 | -59.9258 | -0.091552 | -0.009155 | -0.082398 | 0.12817 | 60.0586 | -0.21515 | 60.1501 | -0.1236 | -0.004577 | -0.041199 | -0.032044 | -0.01831 | 0.082398 | -0.12817 | 0.086975 | -0.1236 | 0.21973 | 123.0606 | -0.013733 | 123.024 | 123.1338 | 123.0148 | 123.0423 | 123.0103 | -123.143 | -123.056 | 122.9691 | 123.0194 | 60.0311 | 60.0632
306.3281 | 123.175 | -60.0082 | 63.0661 | -0.060501 | -0.00014308 | 0.065063 | 0.079085 | 0.0033517 | -0.00053832 | -0.0020615 | 0.015503 | 0.00073263 | 0.06642 | 0.057834 | -0.004499 | 0.0023477 | -0.0018479 | -0.022888 | 63.0569 | -60.1593 | 62.9105 | -59.9167 | -60.2554 | 0.027466 | 0.004578 | 63.0112 | -60.022 | 63.0157 | -60.0586 | -60.1501 | -59.9304 | -0.15106 | -0.009155 | -0.15564 | 0.091553 | 60.0357 | -0.24719 | 60.1868 | -0.09613 | -0.013733 | -0.054932 | -0.050354 | -0.050354 | 0.07782 | -0.14191 | 0.091553 | -0.12817 | 0.24261 | 123.0698 | -0.036621 | 123.0377 | 123.2162 | 123.0331 | 123.0652 | 123.0194 | -123.2254 | -123.0881 | 122.9187 | 123.024 | 59.9854 | 60.0128
307.3281 | 123.2254 | -59.967 | 63.0432 | -0.060501 | 0.0045565 | 0.063995 | 0.078017 | -0.0011343 | 0.0018115 | -0.0018479 | 0.024658 | 0.00030543 | 0.063856 | 0.061679 | -0.0036444 | 0.0014933 | -0.0014207 | 0.050354 | 63.002 | -60.1273 | 63.002 | -59.8251 | -60.1913 | 0.10071 | 0.10986 | 62.9608 | -59.9991 | 63.0569 | -59.9991 | -60.0906 | -59.8892 | -0.16022 | -0.041199 | -0.041199 | 0.14191 | 60.0677 | -0.2243 | 60.228 | -0.064087 | -0.032043 | -0.082398 | 0.013733 | -0.032043 | 0.07782 | -0.1236 | 0.10986 | -0.091553 | 0.30212 | 123.1293 | 0 | 123.056 | 123.1293 | 122.9599 | 122.9691 | 122.9279 | -123.1705 | -123.0423 | 122.9691 | 123.024 | 60.0174 | 60.0769
308.3281 | 123.1979 | -59.9991 | 63.0295 | -0.052872 | -0.0016385 | 0.063995 | 0.078445 | -0.00049353 | -0.0043835 | -0.00099327 | -0.036377 | 0.00116 | 0.064497 | 0.057193 | -0.003858 | 0.0014933 | -0.0031297 | -0.018311 | 63.0157 | -60.1913 | 62.9333 | -59.9304 | -60.2371 | 0 | 0.013733 | 63.0203 | -60.0174 | 63.0386 | -60.0357 | -60.1089 | -59.8846 | -0.19226 | -0.013733 | -0.09613 | 0.068664 | 59.9991 | -0.23804 | 60.1913 | -0.045777 | -0.018311 | -0.009155 | 0.009155 | -0.036622 | 0.11444 | -0.10986 | 0.13275 | -0.091553 | 0.26093 | 123.1247 | -0.018311 | 123.056 | 123.2071 | 123.0377 | 123.0148 | 123.0194 | -123.2208 | -123.0469 | 122.9324 | 123.0377 | 59.9808 | 60.0128
309.3281 | 123.1659 | -60.0128 | 63.0661 | -0.037613 | -0.00099768 | 0.065277 | 0.076308 | -0.0058341 | -0.0013929 | -0.00013887 | 0.024658 | 0.00051903 | 0.063429 | 0.063602 | -0.003858 | 0.00085247 | -0.0014207 | 0.041199 | 63.0157 | -60.1227 | 62.9654 | -59.8526 | -60.2097 | 0.073242 | 0.073242 | 62.9883 | -60.0082 | 63.0386 | -60.0403 | -60.1364 | -59.9258 | -0.10986 | -0.050354 | -0.10071 | 0.16022 | 60.0861 | -0.19684 | 60.1959 | -0.086975 | 0.004577 | -0.07782 | -0.027466 | -0.027466 | 0.086975 | -0.1236 | 0.082398 | -0.12817 | 0.27008 | 123.0881 | -0.032043 | 123.0469 | 123.1384 | 122.9965 | 123.0286 | 123.0011 | -123.1888 | -123.0743 | 122.9782 | 123.0515 | 60.054 | 60.0861
310.3281 | 123.175 | -60.0174 | 63.0341 | -0.037613 | 0.0028475 | 0.064209 | 0.077163 | 0.00014747 | -0.00032472 | 0.0013565 | -0.011963 | 0.0020144 | 0.064711 | 0.058048 | -0.0017218 | 0.00021147 | -0.0041977 | -0.004578 | 63.0661 | -60.1593 | 62.9059 | -59.9716 | -60.2554 | 0.018311 | -0.009155 | 62.9837 | -60.0311 | 63.0112 | -60.0357 | -60.1593 | -59.8938 | -0.14191 | 0.032043 | -0.12817 | 0.045776 | 60.0357 | -0.23804 | 60.1776 | -0.09613 | -0.013733 | -0.050354 | -0.022889 | -0.018311 | 0.1236 | -0.14191 | 0.13733 | -0.12817 | 0.18768 | 123.0652 | -0.004578 | 123.0423 | 123.2254 | 123.0148 | 123.0835 | 123.0011 | -123.1934 | -123.0652 | 122.9233 | 123.0286 | 60.0128 | 60.0082
311.3281 | 123.2437 | -59.9442 | 63.0157 | -0.10628 | 0.0034885 | 0.0625 | 0.07759 | 0.0024973 | 0.00031608 | -0.0014207 | 0.042969 | -0.00033537 | 0.064924 | 0.061466 | -0.0042854 | 0.00063867 | -0.0033433 | 0.054932 | 62.9837 | -60.1318 | 63.0341 | -59.816 | -60.1685 | 0.09613 | 0.12817 | 62.97 | -59.9991 | 63.0936 | -59.967 | -60.0494 | -59.848 | -0.18768 | -0.032043 | 0.018311 | 0.12817 | 60.0403 | -0.2243 | 60.228 | -0.036621 | -0.054931 | -0.045776 | 0.07782 | -0.022888 | 0.096131 | -0.10529 | 0.15106 | -0.050354 | 0.31586 | 123.1659 | 0.032043 | 123.0927 | 123.1155 | 122.9691 | 122.9279 | 122.9141 | -123.1476 | -123.0148 | 122.9782 | 123.0377 | 59.9991 | 60.0723
312.3281 | 123.1979 | -59.9854 | 63.0341 | -0.060501 | -0.0022793 | 0.063141 | 0.080367 | -0.0019889 | -0.0022473 | -0.0012071 | -0.039429 | 0.0015872 | 0.06407 | 0.057193 | -0.003858 | 0.0017069 | 0.0013565 | -0.009155 | 63.0203 | -60.1868 | 62.9379 | -59.935 | -60.2509 | 0.013733 | 0.013733 | 63.0157 | -60.022 | 63.0249 | -60.0266 | -60.1364 | -59.9121 | -0.20142 | -0.013733 | -0.096131 | 0.050354 | 59.9991 | -0.2655 | 60.2005 | -0.064086 | -0.036621 | -0.018311 | -0.009156 | -0.041198 | 0.073243 | -0.15106 | 0.10986 | -0.11444 | 0.25177 | 123.1247 | -0.004577 | 123.0469 | 123.2071 | 123.0377 | 123.0057 | 123.0011 | -123.2208 | -123.056 | 122.9233 | 123.0103 | 59.9762 | 59.9991
313.3281 | 123.3582 | -59.967 | 63.002 | -0.045242 | 0.0022067 | 0.066345 | 0.076949 | -0.0028433 | -0.00053832 | 0.00028833 | 0.052124 | -0.0018308 | 0.063856 | 0.062961 | -0.0025764 | 0.00063867 | -0.0016343 | 0.036621 | 62.9929 | -60.141 | 63.0295 | -59.7702 | -60.1547 | 0.10071 | 0.1236 | 62.9608 | -59.9991 | 63.1348 | -59.8892 | -59.9716 | -59.7885 | -0.17395 | -0.009155 | 0.027466 | 0.19684 | 60.0677 | -0.18768 | 60.2417 | -0.013733 | -0.032043 | -0.041199 | 0.13275 | 0.07782 | 0.17853 | -0.004578 | 0.21057 | 0.027465 | 0.37079 | 123.1705 | 0.10986 | 123.1338 | 123.1338 | 122.9599 | 122.9599 | 122.9279 | -123.143 | -123.0011 | 122.9965 | 123.1018 | 60.0037 | 60.0906
314.3281 | 123.1522 | -59.9854 | 63.0478 | -0.06813 | 0.0013523 | 0.064422 | 0.077804 | -0.00070713 | -0.0035291 | -0.0012071 | -0.030273 | 9.1834e-05 | 0.065565 | 0.061466 | -0.0030036 | 0.0012797 | 7.4746e-05 | -0.064087 | 63.0386 | -60.141 | 62.8876 | -59.9808 | -60.228 | 0 | 0.018311 | 63.0249 | -60.0357 | 63.002 | -60.0632 | -60.1639 | -59.9258 | -0.15564 | -0.009156 | -0.16022 | 0.004578 | 59.9854 | -0.24261 | 60.141 | -0.086975 | -0.050354 | -0.022889 | -0.045777 | -0.077819 | 0.05951 | -0.17853 | 0.10986 | -0.12817 | 0.16022 | 123.0286 | -0.027465 | 123.0377 | 123.1796 | 123.0606 | 123.024 | 123.0103 | -123.1888 | -123.0835 | 122.8729 | 122.9874 | 59.9213 | 60.0037
315.3281 | 123.2758 | -59.9808 | 63.0249 | -0.1368 | 0.0017795 | 0.064422 | 0.076308 | -0.00027993 | -0.00075192 | -0.00056607 | 0.021606 | 0.00051903 | 0.066633 | 0.058475 | -0.0034308 | 0.00021147 | -0.0035569 | 0.050354 | 62.9883 | -60.1364 | 63.0386 | -59.7977 | -60.1318 | 0.10986 | 0.13275 | 62.9562 | -59.9991 | 63.1165 | -59.9442 | -60.022 | -59.8297 | -0.15564 | -0.036621 | 0.013733 | 0.18311 | 60.0906 | -0.15106 | 60.2463 | 0.004578 | -0.01831 | -0.068664 | 0.091553 | 0.036621 | 0.15106 | -0.041199 | 0.16937 | -0.022889 | 0.33875 | 123.175 | 0.054931 | 123.1155 | 123.1247 | 122.9553 | 122.9691 | 122.937 | -123.1613 | -123.024 | 123.0194 | 123.0972 | 60.0311 | 60.1135
316.3281 | 123.111 | -59.9854 | 63.0249 | -0.052872 | 0.00049772 | 0.06549 | 0.078445 | 0.00014747 | 0.00095708 | -0.0020615 | -0.0028075 | 0.00030543 | 0.065565 | 0.060825 | -0.0057806 | 0.0021341 | 7.4746e-05 | 0 | 63.0295 | -60.1547 | 62.9425 | -59.9167 | -60.2509 | 0.041199 | 0.022888 | 63.0112 | -60.0494 | 62.9562 | -59.8663 | -60.0082 | -59.9762 | -0.16937 | 0.004578 | -0.082397 | 0.068665 | 60.0266 | -0.2655 | 60.1959 | -0.09613 | -0.064086 | -0.013733 | -0.068664 | 0.11902 | 0.009156 | -0.022888 | 0.073242 | 0.041198 | 0.23804 | 123.0972 | 0.18311 | 123.0057 | 123.1842 | 123.0606 | 123.0148 | 122.9965 | -123.1796 | -123.0743 | 122.9279 | 122.9416 | 59.9854 | 60.0082
317.3281 | 123.3032 | -59.9625 | 62.9837 | -0.07576 | 0.0013523 | 0.064422 | 0.075027 | -0.00070713 | -0.00032472 | -0.0027023 | -0.051636 | -0.00054897 | 0.063215 | 0.060825 | -0.0042854 | 0.0010661 | -0.0029159 | 0.054932 | 62.9883 | -60.1364 | 63.2309 | -60.1227 | -60.2371 | 0.14648 | 0.16479 | 62.9288 | -60.0128 | 63.1348 | -59.9121 | -59.9991 | -59.8114 | -0.17395 | 0.004577 | 0.24719 | -0.16022 | 60.1089 | -0.27466 | 60.2829 | -0.10071 | -0.050354 | -0.054932 | 0.15106 | 0.050354 | 0.15106 | -0.036621 | 0.20142 | 0.013733 | 0.013733 | 123.3673 | 0.10071 | 123.1476 | 123.1247 | 122.9416 | 122.9507 | 122.8912 | -123.1201 | -122.9965 | 123.1934 | 123.0972 | 60.0174 | 60.1273
318.3281 | 123.2208 | -59.9899 | 63.0386 | -0.052872 | 7.0518e-05 | 0.063995 | 0.078231 | -6.6126e-05 | -0.0013929 | 0.0024245 | 0.015503 | -0.00097617 | 0.064283 | 0.062534 | -0.0034308 | 0.0017069 | 0.00028835 | 0.045776 | 62.9974 | -60.1089 | 63.002 | -59.8343 | -60.1913 | 0.086975 | 0.09613 | 62.9929 | -60.022 | 63.0432 | -60.0128 | -60.1227 | -59.8984 | -0.11902 | -0.041198 | -0.036621 | 0.15564 | 60.0769 | -0.20142 | 60.1959 | -0.082397 | -0.032044 | -0.045776 | 0.004578 | -0.022888 | 0.091553 | -0.13275 | 0.1236 | -0.10071 | 0.27466 | 123.111 | 0.009156 | 123.0652 | 123.1064 | 123.0148 | 122.9874 | 122.9828 | -123.1476 | -123.0606 | 122.9919 | 123.0331 | 60.0357 | 60.0861
319.3281 | 123.2986 | -59.967 | 62.9745 | -0.052872 | 0.0026339 | 0.06485 | 0.078231 | -0.00049353 | -0.0016065 | -0.00056607 | 0.030762 | 0.002228 | 0.06407 | 0.056339 | -0.0023626 | -0.00042933 | 0.00050195 | -0.018311 | 62.9974 | -60.141 | 62.97 | -59.8663 | -60.2097 | 0.022888 | 0.018311 | 62.97 | -60.0266 | 63.089 | -59.9716 | -60.0586 | -59.8297 | -0.17395 | 0.022889 | -0.004577 | 0.10071 | 59.9899 | -0.24262 | 60.1639 | -0.068665 | -0.059509 | -0.004577 | 0.11444 | -0.004578 | 0.13733 | -0.091553 | 0.19684 | -0.032044 | 0.27466 | 123.111 | 0.054931 | 123.1155 | 123.1384 | 122.9965 | 122.9645 | 122.937 | -123.1155 | -123.0011 | 122.937 | 123.056 | 59.9487 | 59.9854
320.3281 | 123.2849 | -59.967 | 63.0112 | 0.00053424 | 0.00092492 | 0.064209 | 0.077804 | 0.0016427 | -0.0018201 | -0.0016343 | 0.0093995 | 0.0018008 | 0.065138 | 0.061466 | -0.00086737 | 0.0012797 | -0.0022751 | 0.050354 | 62.9745 | -60.1089 | 63.0615 | -59.8022 | -60.1593 | 0.09613 | 0.13275 | 62.9883 | -60.0082 | 63.1119 | -59.9487 | -60.0449 | -59.8251 | -0.14191 | -0.036621 | 0.050354 | 0.1648 | 60.0632 | -0.19226 | 60.2051 | -0.050354 | -0.041199 | -0.022888 | 0.10071 | 0.018311 | 0.14191 | -0.07782 | 0.18311 | -0.036621 | 0.3067 | 123.1705 | 0.05951 | 123.1201 | 123.0835 | 122.9965 | 122.9416 | 122.9553 | -123.1201 | -123.0194 | 123.0286 | 123.0789 | 60.0174 | 60.0998
321.3281 | 123.2758 | -59.9808 | 63.002 | -0.045242 | 0.0026339 | 0.063781 | 0.076308 | -0.0019889 | -0.0016065 | -0.00035247 | 0.0032959 | 0.00073263 | 0.063643 | 0.065097 | -0.0025764 | -2.13e-06 | -0.0024887 | 0.032043 | 62.9929 | -60.1501 | 63.0615 | -59.7656 | -60.1318 | 0.11444 | 0 | 62.9608 | -59.9625 | 63.1256 | -60.0082 | -60.0037 | -59.7885 | -0.16937 | -0.009155 | 0.059509 | 0.21515 | 60.0952 | -0.15106 | 60.2646 | 0.01831 | 0.018311 | -0.041199 | 0.1236 | -0.027466 | 0.19226 | -0.022888 | 0.17395 | -0.041199 | 0.38452 | 123.2117 | -0.045777 | 123.0881 | 123.143 | 122.9233 | 122.9736 | 122.9416 | -123.1522 | -122.9645 | 123.0423 | 123.1064 | 60.0128 | 59.9808
322.3281 | 123.1613 | -60.0082 | 63.0478 | -0.06813 | 0.0030613 | 0.062927 | 0.077376 | -0.0013479 | -0.0013929 | -0.0020615 | -0.015015 | 9.1834e-05 | 0.065138 | 0.063816 | -0.0047126 | 0.00021147 | -0.00035245 | 0.004578 | 63.0157 | -60.1593 | 62.9379 | -59.9213 | -60.2554 | 0.041199 | 0.027466 | 63.0157 | -60.0266 | 63.0432 | -60.2097 | -60.173 | -59.8938 | -0.15106 | -0.032044 | -0.10986 | 0.086975 | 60.0494 | -0.24719 | 60.2005 | -0.09613 | -0.01831 | -0.032044 | -0.004578 | -0.20142 | 0.11444 | -0.16479 | 0.13275 | -0.14648 | 0.23804 | 123.0972 | -0.18311 | 123.0698 | 123.175 | 123.0423 | 123.024 | 123.024 | -123.2071 | -123.0743 | 122.9462 | 123.0515 | 60.0128 | 60.0357
323.3281 | 123.3307 | -59.9808 | 62.9837 | -0.060501 | 0.0011385 | 0.06015 | 0.076949 | -0.0011343 | -0.0013929 | -0.00056607 | -0.0028075 | 0.0018008 | 0.063002 | 0.058902 | -0.0036444 | -2.13e-06 | -0.00056605 | 0.004578 | 62.97 | -60.1639 | 63.0066 | -59.8251 | -60.1913 | 0.068665 | 0.07782 | 62.9471 | -60.022 | 63.1348 | -59.9396 | -60.0128 | -59.8022 | -0.18311 | -0.013733 | 0.022888 | 0.15564 | 60.0494 | -0.21057 | 60.2325 | -0.027466 | -0.041199 | -0.036621 | 0.15106 | 0.041199 | 0.17853 | -0.032043 | 0.21973 | 0.009156 | 0.33875 | 123.1705 | 0.082398 | 123.1567 | 123.1338 | 122.9691 | 122.9507 | 122.9279 | -123.1476 | -123.0057 | 122.9874 | 123.1155 | 59.9854 | 60.0586
324.3281 | 123.2712 | -59.9854 | 63.0112 | -0.045242 | 0.0019931 | 0.0625 | 0.07759 | 0.0027109 | -0.0013929 | 0.0024245 | -0.0058593 | 0.00051903 | 0.062575 | 0.062107 | -0.0025764 | 0.0021341 | -0.0031297 | 0.036621 | 62.9929 | -60.1547 | 63.0524 | -59.7885 | -60.1501 | 0.10986 | 0.11902 | 62.9562 | -59.9945 | 63.121 | -59.9304 | -60.0174 | -59.8343 | -0.16937 | -0.01831 | 0.041199 | 0.19684 | 60.0952 | -0.16479 | 60.2646 | 0.004578 | -0.009155 | -0.054931 | 0.10986 | 0.054932 | 0.15106 | -0.032043 | 0.16022 | -0.022888 | 0.36621 | 123.2071 | 0.064087 | 123.1155 | 123.1476 | 122.9507 | 122.9782 | 122.9416 | -123.1659 | -123.0057 | 123.0377 | 123.1064 | 60.022 | 60.1044
325.3281 | 123.2986 | -59.9625 | 63.0066 | -0.07576 | 0.0017795 | 0.064422 | 0.076095 | 0.0033517 | 0.00074348 | -0.00056607 | 0.012451 | 0.0024416 | 0.064283 | 0.059543 | -0.0047126 | 0.0014933 | 0.0024245 | -0.032043 | 62.97 | -60.1547 | 62.9837 | -59.8618 | -60.1959 | 0.018311 | 0.027466 | 62.9471 | -60.0266 | 63.089 | -59.9579 | -60.0403 | -59.8297 | -0.19226 | -0.036621 | -0.022888 | 0.10071 | 59.9808 | -0.23346 | 60.173 | -0.041199 | -0.064087 | -0.059509 | 0.082397 | 0.004577 | 0.13275 | -0.07782 | 0.19684 | -0.013733 | 0.29297 | 123.1384 | 0.068664 | 123.1155 | 123.1247 | 122.9736 | 122.9324 | 122.9095 | -123.1613 | -123.0331 | 122.9462 | 123.0515 | 59.9304 | 59.9899
326.3281 | 123.2849 | -59.967 | 62.9929 | -0.098648 | -0.00014308 | 0.06485 | 0.076736 | 0.0035653 | -0.00032472 | -0.0016343 | -0.021118 | 0.00094643 | 0.061934 | 0.063388 | -0.0040716 | 0.0027751 | -0.0018479 | 0.050354 | 62.9745 | -60.1227 | 63.0203 | -59.8984 | -60.1318 | 0.11444 | 0.15106 | 62.9471 | -60.022 | 63.1302 | -59.9213 | -60.0128 | -59.816 | -0.15564 | -0.018311 | 0.027466 | 0.068665 | 60.0815 | -0.16479 | 60.2371 | -0.009155 | -0.054932 | -0.045776 | 0.13733 | 0.045776 | 0.15106 | -0.045776 | 0.20599 | 0.009156 | 0.22431 | 123.143 | 0.10071 | 123.1522 | 123.0972 | 122.9691 | 122.9416 | 122.9141 | -123.1155 | -123.0148 | 122.9874 | 123.0972 | 60.0174 | 60.1181
327.3281 | 123.2895 | -59.9899 | 63.0112 | -0.052872 | 0.0019931 | 0.062286 | 0.078872 | 0.00057467 | -0.00075192 | -0.0029159 | -0.0089111 | -0.0016172 | 0.06407 | 0.062961 | -0.0030036 | -0.00021573 | -0.0016343 | -0.050354 | 62.9929 | -60.173 | 62.9837 | -59.8755 | -60.2325 | 0.009155 | -0.018311 | 62.9517 | -60.0174 | 63.0936 | -59.9854 | -60.0632 | -59.8526 | -0.18311 | -0.01831 | -0.027465 | 0.11444 | 59.9991 | -0.24262 | 60.1822 | -0.059509 | -0.027466 | -0.059509 | 0.082398 | 0.004577 | 0.13733 | -0.073242 | 0.16479 | -0.045776 | 0.29755 | 123.1567 | 0.032043 | 123.111 | 123.1659 | 122.9691 | 122.9828 | 122.9416 | -123.1842 | -123.0286 | 122.9736 | 123.0835 | 59.9396 | 59.9716
328.3281 | 123.2941 | -59.9716 | 62.9471 | -0.07576 | 0.0013523 | 0.064209 | 0.078445 | -0.0011343 | -0.0022473 | -0.0018479 | -0.02417 | 0.0015872 | 0.063215 | 0.059757 | -0.010908 | -0.0012839 | -0.0024887 | 0.018311 | 62.97 | -60.1364 | 63.0569 | -59.7565 | -60.1273 | 0.11902 | 0.13733 | 62.9837 | -59.9991 | 63.3087 | -60.2737 | -60.0082 | -59.7519 | -0.1648 | 0.022888 | 0.10986 | 0.21515 | 60.0906 | -0.15564 | 60.2554 | 0.009156 | -0.027465 | 0.036621 | 0.36163 | -0.30212 | 0.21973 | -0.036621 | 0.24719 | -0.009156 | 0.37994 | 123.1934 | -0.27466 | 123.3078 | 123.1064 | 122.9828 | 122.9416 | 122.9553 | -123.0835 | -122.9462 | 123.0286 | 123.2803 | 59.9899 | 60.1089
329.3281 | 123.3032 | -59.9808 | 62.9837 | -0.060501 | 0.0017795 | 0.064636 | 0.077804 | -0.00070713 | -0.00075192 | -0.00035247 | -0.0058593 | 0.00073263 | 0.064711 | 0.058689 | -0.0040716 | 0.0029887 | -0.00056605 | -0.022888 | 62.9654 | -60.1685 | 62.9929 | -59.8663 | -60.2188 | 0.032043 | 0.004578 | 62.9745 | -60.022 | 63.1027 | -59.9625 | -60.0494 | -59.8389 | -0.18768 | -0.018311 | 0.009155 | 0.11444 | 60.0128 | -0.23804 | 60.2005 | -0.050354 | -0.041199 | -0.009156 | 0.11902 | 0.018311 | 0.14191 | -0.068664 | 0.18311 | -0.027465 | 0.30212 | 123.1613 | 0.05951 | 123.1247 | 123.1338 | 122.9965 | 122.9462 | 122.9553 | -123.1522 | -123.0057 | 122.9736 | 123.0835 | 59.9579 | 59.9854
330.3281 | 123.2437 | -59.9945 | 63.0249 | -0.12154 | 0.0030613 | 0.063141 | 0.076095 | -6.6126e-05 | -0.00032472 | 7.4734e-05 | -0.0058593 | 0.00094643 | 0.065138 | 0.065311 | -0.0040716 | 0.0021341 | -0.0016343 | 0.059509 | 62.9654 | -60.141 | 63.0341 | -59.8022 | -60.1501 | 0.10986 | 0.13733 | 62.9929 | -60.0082 | 63.0981 | -59.9579 | -60.054 | -59.8297 | -0.14648 | -0.059509 | 0.009156 | 0.19226 | 60.1044 | -0.15564 | 60.2509 | -0.009155 | -0.013733 | -0.032043 | 0.073243 | 0.036621 | 0.16479 | -0.059509 | 0.17853 | -0.045776 | 0.33875 | 123.175 | 0.050354 | 123.1064 | 123.1064 | 123.0011 | 122.9599 | 122.9874 | -123.1659 | -123.0331 | 123.0286 | 123.0927 | 60.054 | 60.1318
331.3281 | 123.2529 | -59.9762 | 62.9745 | -0.029984 | 0.00049772 | 0.063995 | 0.078445 | 0.00078827 | -0.00075192 | -0.0046249 | -0.027222 | 0.00030543 | 0.065565 | 0.061679 | -0.0059942 | -2.13e-06 | -0.0016343 | -0.036621 | 62.9929 | -60.141 | 62.9883 | -59.8984 | -60.2142 | -0.009155 | -0.022888 | 62.9654 | -60.0494 | 63.089 | -59.9899 | -60.0861 | -59.8618 | -0.16479 | 0.018311 | 0.013733 | 0.07782 | 59.967 | -0.23804 | 60.1318 | -0.073242 | -0.073242 | -0.009155 | 0.11444 | -0.013733 | 0.11444 | -0.10986 | 0.18768 | -0.036622 | 0.24262 | 123.1293 | 0.059509 | 123.1384 | 123.1338 | 123.0148 | 122.9691 | 122.9416 | -123.1155 | -123.024 | 122.9645 | 123.0652 | 59.9396 | 59.9533
332.3281 | 123.2437 | -59.9762 | 62.9883 | -0.045242 | 0.00028412 | 0.064422 | 0.079513 | 0.0010019 | 0.0030933 | -0.0016343 | -0.0058593 | -0.00033537 | 0.063002 | 0.063175 | -0.004499 | 0.0023477 | 0.0017837 | 0.022888 | 62.97 | -60.1456 | 63.0524 | -59.7656 | -60.1501 | 0.09613 | 0.16022 | 62.9517 | -59.9899 | 62.9379 | -59.5276 | -59.8618 | -59.8892 | -0.16937 | -0.01831 | 0.064087 | 0.21057 | 60.0723 | -0.17395 | 60.2417 | -0.004577 | -0.013733 | -0.036621 | -0.050354 | 0.44861 | 0.086975 | 0.11444 | 0.10071 | 0.12817 | 0.37994 | 123.1979 | 0.46234 | 122.9279 | 123.1155 | 122.9416 | 122.9462 | 122.9279 | -123.1338 | -122.9782 | 123.0286 | 122.9141 | 59.9991 | 60.1364
333.3281 | 123.262 | -59.9854 | 62.9791 | -0.091019 | 0.00071132 | 0.061645 | 0.079085 | 0.0048471 | 0.0011707 | 0.0011429 | -0.030273 | 0.0020144 | 0.063643 | 0.061252 | -0.0036444 | 0.0012797 | 7.4746e-05 | -0.045776 | 62.9654 | -60.1868 | 62.97 | -59.8618 | -60.2692 | -0.022888 | -0.059509 | 62.9288 | -60.0311 | 63.0524 | -60.0266 | -60.1181 | -59.8755 | -0.20142 | -0.013733 | -0.009155 | 0.1236 | 59.9625 | -0.28381 | 60.1639 | -0.082397 | -0.045776 | -0.050354 | 0.073242 | -0.041198 | 0.10986 | -0.13275 | 0.15564 | -0.086975 | 0.32501 | 123.1567 | 0.004578 | 123.0835 | 123.1522 | 122.9599 | 122.9507 | 122.9141 | -123.1659 | -123.0103 | 122.9553 | 123.0377 | 59.9396 | 59.9258
334.3281 | 123.3032 | -59.967 | 62.97 | -0.083389 | 0.00028412 | 0.063781 | 0.077163 | 0.0010019 | 0.00010248 | 0.0011429 | -0.015015 | 0.0015872 | 0.063643 | 0.05698 | -0.003858 | 0.0010661 | -0.0027023 | -0.004578 | 62.9883 | -60.1501 | 63.0203 | -59.816 | -60.173 | 0.082397 | 0.091553 | 62.9425 | -60.0082 | 63.121 | -59.935 | -60.0082 | -59.816 | -0.1831 | 0.01831 | 0.050354 | 0.15106 | 60.0494 | -0.20599 | 60.2325 | -0.022889 | -0.041199 | -0.027466 | 0.15106 | 0.032043 | 0.15106 | -0.041199 | 0.19226 | 0 | 0.33417 | 123.1705 | 0.073242 | 123.1293 | 123.1384 | 122.9507 | 122.9553 | 122.9095 | -123.1201 | -122.9782 | 122.9874 | 123.0881 | 59.9625 | 60.0586
335.3281 | 123.3032 | -59.9945 | 62.9929 | -0.06813 | 0.0019931 | 0.062927 | 0.078231 | -0.0011343 | -0.0018201 | -0.0035569 | -0.0058593 | 0.00116 | 0.067701 | 0.060184 | -0.0036444 | 0.0038431 | -0.00077965 | 0.036621 | 62.9745 | -60.1593 | 63.0615 | -59.7702 | -60.141 | 0.10986 | 0.17395 | 62.9608 | -59.9991 | 62.9745 | -59.848 | -60.0357 | -59.8755 | -0.16479 | -0.018311 | 0.068664 | 0.2243 | 60.1044 | -0.14648 | 60.2692 | 0.018311 | -0.004577 | -0.032044 | -0.018311 | 0.14648 | 0.11902 | -0.041199 | 0.1236 | -0.036622 | 0.3891 | 123.2208 | 0.15106 | 122.9736 | 123.1338 | 122.9599 | 122.9691 | 122.9553 | -123.1522 | -122.9919 | 123.056 | 122.9691 | 60.0311 | 60.1685
336.3281 | 123.2895 | -59.9625 | 63.002 | -0.10628 | 0.0015659 | 0.065063 | 0.077804 | -0.00070713 | 0.00095708 | -0.00099327 | -0.011963 | 0.00116 | 0.063643 | 0.059543 | -0.0025764 | 0.0017069 | 0.0011429 | 0.013733 | 62.9654 | -60.141 | 63.0661 | -59.7839 | -60.1501 | 0.11444 | 0.15106 | 62.9745 | -59.9945 | 63.1302 | -59.9258 | -60.0128 | -59.7931 | -0.17853 | -0.036621 | 0.064087 | 0.17853 | 60.0769 | -0.18768 | 60.2554 | -0.009155 | -0.032044 | -0.027466 | 0.12817 | 0.036621 | 0.16937 | -0.050354 | 0.20142 | -0.01831 | 0.35706 | 123.2071 | 0.068665 | 123.1247 | 123.1064 | 122.9691 | 122.9279 | 122.937 | -123.143 | -122.9965 | 123.0286 | 123.0927 | 59.9762 | 60.1135
337.3281 | 123.2254 | -59.9716 | 62.9883 | -0.091019 | 0.0013523 | 0.061859 | 0.078872 | -0.00049353 | -0.0011791 | -0.00056607 | -0.0028075 | -0.00054897 | 0.063856 | 0.065097 | -0.0036444 | 0.00042507 | 7.4746e-05 | -0.068665 | 62.9837 | -60.1685 | 62.9745 | -59.8892 | -60.2463 | -0.018311 | -0.064087 | 62.9562 | -60.0586 | 63.0386 | -60.0266 | -60.0723 | -59.848 | -0.19684 | -0.004577 | -0.013733 | 0.082398 | 59.9533 | -0.27466 | 60.1501 | -0.07782 | -0.086975 | -0.032043 | 0.050354 | -0.054931 | 0.1236 | -0.10071 | 0.21057 | -0.013733 | 0.27924 | 123.143 | 0.032044 | 123.0972 | 123.1522 | 123.0148 | 122.9553 | 122.9279 | -123.1567 | -123.0469 | 122.9462 | 123.0103 | 59.903 | 59.9075
338.3281 | 123.3078 | -59.9899 | 62.9883 | -0.07576 | -0.00078408 | 0.06485 | 0.077376 | -0.00092073 | 0.00010248 | -0.00077967 | -0.0058593 | -0.00012177 | 0.062147 | 0.058475 | -0.0053534 | 0.0010661 | -0.0024887 | 0.041199 | 62.9974 | -60.1181 | 63.0844 | -59.7382 | -60.1273 | 0.11444 | 0.46692 | 63.0157 | -59.9396 | 63.0981 | -59.8709 | -60.0266 | -59.8068 | -0.12817 | 0.009156 | 0.096131 | 0.25177 | 60.1044 | -0.13733 | 60.2325 | -0.009155 | 0.050354 | 0.027466 | 0.10986 | 0.11902 | 0.1831 | -0.036621 | 0.13275 | -0.086975 | 0.37994 | 123.2025 | 0.068664 | 123.0377 | 123.1155 | 122.9553 | 122.9874 | 123.0057 | -123.1064 | -122.9279 | 123.0743 | 123.0881 | 60.0311 | 60.4568
339.3281 | 123.2758 | -59.9808 | 62.9974 | -0.10628 | -0.00057028 | 0.063568 | 0.07759 | -6.6126e-05 | -0.00032472 | -0.00013887 | -0.045532 | 0.002869 | 0.062788 | 0.060825 | -0.0023626 | 0.0027751 | -0.0046249 | -0.064087 | 62.9517 | -60.1776 | 62.97 | -59.8801 | -60.2692 | -0.032043 | -0.082397 | 62.9425 | -60.0586 | 63.0707 | -60.0128 | -60.0998 | -59.8709 | -0.19684 | -0.045777 | -0.027466 | 0.10071 | 59.9487 | -0.28839 | 60.1456 | -0.091553 | -0.07782 | -0.054932 | 0.073242 | -0.032043 | 0.10986 | -0.11902 | 0.18768 | -0.041198 | 0.29755 | 123.1476 | 0.045777 | 123.1293 | 123.1293 | 123.0011 | 122.9324 | 122.9233 | -123.175 | -123.056 | 122.9507 | 123.0515 | 59.9167 | 59.8984
340.3438 | 123.1934 | -60.0128 | 63.0249 | -0.052872 | 0.0034885 | 0.064209 | 0.07994 | 0.0033517 | -0.00011112 | 0.0041335 | -0.10657 | 0.0015872 | 0.061934 | 0.06702 | -0.0019354 | 0.0023477 | 0.00092935 | -0.013733 | 62.9837 | -60.1959 | 62.97 | -59.8846 | -60.2463 | 0 | 0.004578 | 62.97 | -60.0403 | 63.0478 | -60.0449 | -60.1501 | -59.8801 | -0.18311 | -0.041198 | -0.054931 | 0.12817 | 60.0128 | -0.23346 | 60.1959 | -0.050354 | -0.027466 | -0.054931 | 0.022889 | -0.032044 | 0.13275 | -0.13733 | 0.16022 | -0.10986 | 0.31128 | 123.1659 | -0.004578 | 123.0881 | 123.1796 | 123.0103 | 122.9965 | 122.9828 | -123.2208 | -123.0652 | 122.9828 | 123.0606 | 59.9991 | 60.0174
341.3281 | 123.262 | -59.9899 | 62.9745 | -0.07576 | 0.0013523 | 0.06549 | 0.07759 | 0.00078827 | -0.00053832 | -0.00077967 | -0.030273 | 9.1834e-05 | 0.064283 | 0.059543 | -0.0036444 | 0.0027751 | -0.0020615 | -0.045776 | 62.9562 | -60.1639 | 62.9837 | -59.8434 | -60.2371 | -0.022888 | -0.041199 | 62.9379 | -60.0266 | 63.0798 | -60.0174 | -60.1044 | -59.8663 | -0.17395 | -0.01831 | 0.009156 | 0.14648 | 59.967 | -0.24719 | 60.141 | -0.073243 | -0.036621 | -0.036621 | 0.10529 | -0.027466 | 0.1236 | -0.11444 | 0.16022 | -0.07782 | 0.32043 | 123.1476 | 0.009155 | 123.1064 | 123.1201 | 122.9645 | 122.9462 | 122.9279 | -123.1384 | -123.0011 | 122.9736 | 123.0698 | 59.9442 | 59.9487
342.3281 | 123.2803 | -59.9854 | 62.9745 | -0.083389 | 0.0011385 | 0.062713 | 0.079299 | -0.00092073 | -0.0020337 | 0.00092933 | -0.0058593 | 0.0020144 | 0.064711 | 0.061893 | -0.0025764 | 0.0034159 | 0.0026383 | -0.022888 | 62.9791 | -60.1547 | 62.9974 | -59.8389 | -60.2005 | 0.050354 | 0.032043 | 62.9471 | -60.0174 | 63.1165 | -59.967 | -60.022 | -59.8114 | -0.16937 | 0.004578 | 0.022889 | 0.14648 | 60.0357 | -0.21515 | 60.2051 | -0.045776 | -0.032043 | -0.027465 | 0.14191 | 0.018311 | 0.17395 | -0.036621 | 0.20599 | -0.004578 | 0.31586 | 123.1522 | 0.050354 | 123.1338 | 123.1338 | 122.9645 | 122.9645 | 122.9324 | -123.1293 | -122.9919 | 122.9828 | 123.1018 | 59.9625 | 60.0174
343.3281 | 123.2529 | -59.9716 | 62.97 | -0.091019 | 0.0011385 | 0.063568 | 0.076308 | -0.0017751 | -0.00032472 | 0.00092933 | -0.027222 | -0.00054897 | 0.063643 | 0.061252 | -0.0042854 | 0.0010661 | 0.00071555 | -0.059509 | 62.9425 | -60.1868 | 62.97 | -59.8709 | -60.2554 | -0.045776 | -0.068665 | 62.9425 | -60.0403 | 63.0707 | -60.0174 | -60.0998 | -59.8663 | -0.21515 | -0.027466 | 0 | 0.10071 | 59.9258 | -0.28381 | 60.141 | -0.068664 | -0.068664 | -0.027466 | 0.10071 | -0.045776 | 0.10529 | -0.12817 | 0.17395 | -0.059509 | 0.31586 | 123.1567 | 0.022888 | 123.111 | 123.1293 | 122.9828 | 122.9141 | 122.9141 | -123.1567 | -123.0103 | 122.9416 | 123.0423 | 59.9121 | 59.903
344.3281 | 123.3078 | -59.9716 | 62.9745 | 0.031052 | -0.0014249 | 0.065063 | 0.079726 | 0.0010019 | -0.0013929 | -0.0024887 | -0.042481 | 0.0013736 | 0.064711 | 0.058689 | -0.0032172 | 0.00042507 | -0.0031297 | -0.022888 | 62.9929 | -60.1593 | 62.9791 | -59.8663 | -60.2097 | 0.009155 | -0.018311 | 62.9425 | -59.9991 | 63.0844 | -59.967 | -60.0632 | -59.8572 | -0.18768 | 0.018311 | 0.004578 | 0.10529 | 59.9808 | -0.23804 | 60.1685 | -0.050354 | -0.027465 | -0.032043 | 0.10986 | 0.004578 | 0.11444 | -0.091552 | 0.14191 | -0.064087 | 0.29297 | 123.1384 | 0.032043 | 123.0835 | 123.1522 | 122.9416 | 122.9645 | 122.9141 | -123.1338 | -122.9736 | 122.9507 | 123.056 | 59.9487 | 59.9533
345.3438 | 123.1659 | -59.9899 | 63.0478 | -0.014725 | 0.0022067 | 0.063354 | 0.078231 | -0.0036977 | 0.00010248 | -0.0031297 | -0.069946 | -0.00054897 | 0.062147 | 0.060611 | -0.0042854 | 0.0029887 | 0.0032791 | -0.018311 | 63.0157 | -60.1593 | 62.9288 | -59.9213 | -60.2554 | 0.027466 | 0.009155 | 63.0157 | -60.022 | 63.0295 | -60.0266 | -60.1501 | -59.9213 | -0.16937 | -0.032044 | -0.11902 | 0.068664 | 60.0174 | -0.2655 | 60.1868 | -0.09613 | -0.032044 | -0.032044 | -0.018311 | -0.036621 | 0.068664 | -0.16022 | 0.10071 | -0.12817 | 0.23804 | 123.0881 | -0.004577 | 123.0515 | 123.175 | 123.0377 | 123.0057 | 123.0057 | -123.2071 | -123.0698 | 122.9187 | 123.0194 | 59.9716 | 59.9991
346.3281 | 123.262 | -59.9716 | 62.9883 | -0.060501 | 0.0022067 | 0.062713 | 0.078231 | -0.00092073 | 0.0022387 | -0.00056607 | -0.011963 | 9.1834e-05 | 0.066206 | 0.06232 | -0.004499 | 0.0027751 | -0.0086839 | -0.054932 | 62.9654 | -60.173 | 62.9562 | -59.8755 | -60.2509 | -0.013733 | -0.059509 | 62.9837 | -60.0357 | 63.0569 | -59.9304 | -60.0449 | -59.7977 | -0.20142 | -0.022888 | -0.032043 | 0.096131 | 59.9579 | -0.27923 | 60.1593 | -0.077819 | -0.064087 | -0.004577 | 0.068665 | 0.041199 | 0.17395 | -0.073242 | 0.23804 | -0.009155 | 0.29755 | 123.1293 | 0.10529 | 123.0927 | 123.1384 | 123.0194 | 122.937 | 122.9553 | -123.1613 | -123.024 | 122.9279 | 123.0286 | 59.9167 | 59.9121
347.3281 | 123.2803 | -59.9854 | 62.97 | -0.098648 | 0.0030613 | 0.063781 | 0.078017 | 0.00078827 | -0.0013929 | -0.00077967 | -0.072998 | -0.00076257 | 0.064711 | 0.068515 | -0.006208 | 0.0027751 | -0.00056605 | -0.032043 | 62.9425 | -60.1913 | 63.002 | -59.8572 | -60.2188 | -0.036621 | -0.032043 | 62.9333 | -60.0311 | 63.1119 | -59.9716 | -60.0677 | -59.8251 | -0.20599 | -0.027466 | 0.032043 | 0.12817 | 59.9487 | -0.23346 | 60.1547 | -0.027466 | -0.045776 | -0.036621 | 0.14191 | 0.013733 | 0.16022 | -0.082397 | 0.20599 | -0.036621 | 0.33417 | 123.1934 | 0.059509 | 123.143 | 123.1338 | 122.9645 | 122.9279 | 122.9187 | -123.1613 | -123.0011 | 122.9874 | 123.0972 | 59.9533 | 59.9533
348.3281 | 123.2574 | -59.9808 | 62.9745 | -0.07576 | 0.0022067 | 0.063781 | 0.080794 | 0.0020701 | -0.0018201 | -0.00013887 | -0.0089111 | 0.00094643 | 0.063429 | 0.065097 | -0.00279 | 0.0017069 | 0.00071555 | -0.073242 | 62.9929 | -60.1501 | 62.9562 | -59.8709 | -60.2417 | -0.013733 | -0.073242 | 62.97 | -60.0403 | 63.0707 | -60.0082 | -60.1089 | -59.8618 | -0.16937 | 0.018311 | -0.01831 | 0.10986 | 59.967 | -0.26093 | 60.1364 | -0.091553 | -0.059509 | -0.004577 | 0.096131 | -0.027466 | 0.11902 | -0.12817 | 0.17853 | -0.068665 | 0.27923 | 123.1064 | 0.032043 | 123.111 | 123.143 | 123.0103 | 122.9736 | 122.9507 | -123.1247 | -123.0148 | 122.937 | 123.0515 | 59.9075 | 59.9075
349.3281 | 123.2574 | -60.0037 | 62.9425 | -0.060501 | 0.00049772 | 0.063781 | 0.076308 | -0.00092073 | -0.0011791 | -0.00099327 | -0.039429 | -0.00097617 | 0.064711 | 0.061893 | -0.0042854 | 0.00085247 | 0.0028519 | -0.045776 | 62.9471 | -60.1547 | 62.9929 | -59.8434 | -60.2325 | -0.013733 | -0.036621 | 62.9471 | -60.0311 | 63.089 | -60.0037 | -60.0815 | -59.8663 | -0.15106 | 0.004578 | 0.050354 | 0.16022 | 59.9899 | -0.22888 | 60.141 | -0.07782 | -0.027466 | 0.004578 | 0.14648 | 0 | 0.13733 | -0.07782 | 0.1648 | -0.050354 | 0.31128 | 123.1476 | 0.027466 | 123.1201 | 123.1018 | 122.9782 | 122.9507 | 122.9507 | -123.0972 | -122.9736 | 122.9965 | 123.0927 | 59.9579 | 59.967
350.3438 | 123.1796 | -60.0037 | 63.0203 | -0.060501 | 0.00071132 | 0.063354 | 0.079299 | -0.0039115 | -0.00032472 | 7.4734e-05 | -0.069946 | 0.0041506 | 0.060866 | 0.067447 | -0.0034308 | 0.0036295 | -0.0014207 | -0.013733 | 63.0478 | -60.173 | 62.9288 | -59.9396 | -60.2646 | 0.009155 | 0.16479 | 63.0203 | -59.9899 | 63.0157 | -60.0266 | -60.141 | -59.9121 | -0.16937 | 0.027466 | -0.091553 | 0.064087 | 60.0128 | -0.26093 | 60.1822 | -0.091552 | 0.013733 | 0 | -0.004578 | -0.022888 | 0.091553 | -0.13733 | 0.07782 | -0.15106 | 0.23346 | 123.1018 | -0.036621 | 123.0057 | 123.2208 | 123.0103 | 123.0515 | 123.024 | -123.1934 | -123.0103 | 122.9324 | 123.0194 | 59.9899 | 60.1685
351.3281 | 123.2941 | -59.9945 | 62.9654 | -0.15968 | 0.0041293 | 0.061859 | 0.076736 | -0.00027993 | 0.00010248 | -0.0014207 | -0.10962 | 0.0018008 | 0.060652 | 0.057621 | -0.0034308 | 0.0014933 | -0.0027023 | -0.045776 | 62.9517 | -60.1639 | 63.002 | -59.8389 | -60.2325 | -0.022888 | 0.032043 | 62.9196 | -60.0311 | 63.1073 | -59.9808 | -60.0586 | -59.8343 | -0.16937 | -0.013733 | 0.036621 | 0.15564 | 59.9716 | -0.23804 | 60.141 | -0.068665 | -0.036621 | -0.045776 | 0.14191 | 0.013733 | 0.16022 | -0.064087 | 0.19684 | -0.027466 | 0.32501 | 123.1659 | 0.050354 | 123.1384 | 123.1155 | 122.9507 | 122.9462 | 122.9141 | -123.1293 | -122.9965 | 122.9965 | 123.1018 | 59.9487 | 60.0266
352.3281 | 123.2529 | -59.9899 | 62.9929 | -0.11391 | 0.0017795 | 0.06485 | 0.077163 | 0.0018565 | 0.0011707 | -0.0029159 | -0.0058593 | -0.00054897 | 0.063643 | 0.05463 | -0.0012946 | 0.0034159 | 0.00071555 | -0.07782 | 62.9837 | -60.1501 | 62.9471 | -59.8846 | -60.2463 | -0.032043 | -0.064087 | 62.9517 | -60.054 | 63.0524 | -59.9991 | -60.0815 | -59.8572 | -0.16022 | -0.009155 | -0.045776 | 0.10528 | 59.9579 | -0.25635 | 60.1181 | -0.096131 | -0.064087 | -0.041199 | 0.059509 | -0.009155 | 0.13275 | -0.091553 | 0.19684 | -0.027466 | 0.2655 | 123.0972 | 0.054932 | 123.1064 | 123.1338 | 123.0057 | 122.9736 | 122.9416 | -123.143 | -123.0469 | 122.937 | 123.0423 | 59.9121 | 59.9258
353.3281 | 123.2986 | -59.9854 | 62.9517 | -0.16731 | 0.0019931 | 0.06549 | 0.079299 | -0.0013479 | -0.00096552 | 7.4734e-05 | -0.069946 | 0.002228 | 0.063429 | 0.060184 | -0.0068488 | 0.0023477 | -0.0014207 | -0.041199 | 62.9242 | -60.1868 | 63.0112 | -59.8297 | -60.2371 | -0.036621 | -0.036621 | 62.9242 | -60.0357 | 63.0981 | -59.9762 | -60.0723 | -59.8206 | -0.20142 | -0.027466 | 0.059509 | 0.15564 | 59.9487 | -0.25177 | 60.1501 | -0.050354 | -0.050354 | -0.027466 | 0.14649 | 0.009156 | 0.16479 | -0.086975 | 0.21515 | -0.036621 | 0.35706 | 123.1979 | 0.05951 | 123.1339 | 123.111 | 122.9599 | 122.9095 | 122.9095 | -123.1384 | -122.9874 | 122.9965 | 123.0835 | 59.9442 | 59.9487
354.3281 | 123.2529 | -59.9945 | 62.9745 | -0.1368 | 0.0028475 | 0.066345 | 0.077163 | 0.0024973 | -0.00096552 | 0.00071573 | -0.030273 | -0.00012177 | 0.063429 | 0.061038 | -0.003858 | 0.0014933 | -0.0020615 | -0.041199 | 62.9654 | -60.1639 | 63.0753 | -59.816 | -60.1959 | 0 | -0.027466 | 62.9608 | -60.0311 | 63.0981 | -60.0082 | -60.1044 | -59.8618 | -0.16937 | -0.009155 | 0.10071 | 0.17853 | 59.9945 | -0.20142 | 60.1639 | -0.032044 | -0.036621 | -0.013733 | 0.1236 | -0.013733 | 0.13275 | -0.10986 | 0.16937 | -0.073242 | 0.3479 | 123.2391 | 0.022888 | 123.1293 | 123.1293 | 122.9919 | 122.9599 | 122.9553 | -123.1384 | -123.0057 | 123.0698 | 123.0927 | 59.9533 | 59.967
355.3281 | 123.1888 | -59.9945 | 63.0386 | -0.083389 | 0.0015659 | 0.062713 | 0.078445 | 0.0024973 | -0.0031017 | -0.0024887 | -0.027222 | 0.0018008 | 0.064497 | 0.058689 | -0.0051398 | 0.0010661 | 0.0011429 | 0.004578 | 63.0341 | -60.141 | 62.9379 | -59.8801 | -60.2051 | 0.050354 | 0.036621 | 63.0112 | -60.0357 | 63.0341 | -60.0311 | -60.141 | -59.9121 | -0.14648 | -0.004577 | -0.10071 | 0.11444 | 60.0449 | -0.21057 | 60.1913 | -0.064087 | -0.041199 | -0.027466 | -0.004577 | -0.036621 | 0.082398 | -0.14648 | 0.1236 | -0.10529 | 0.26093 | 123.0789 | 0.004578 | 123.0698 | 123.175 | 123.0469 | 123.0286 | 123.0057 | -123.1796 | -123.0743 | 122.9324 | 123.0286 | 59.9991 | 60.0311
356.3281 | 123.2941 | -59.9808 | 62.9791 | -0.10628 | 0.00049772 | 0.063781 | 0.078872 | 0.00057467 | -0.0013929 | -0.00099327 | 0.12537 | 0.00116 | 0.065992 | 0.066806 | -0.002149 | 0.0010661 | -0.0037705 | -0.036621 | 62.9837 | -60.1318 | 62.9837 | -59.8572 | -60.2051 | 0.022888 | -0.045776 | 62.9425 | -60.022 | 63.1027 | -59.9808 | -60.0266 | -59.8022 | -0.15106 | 0.004578 | 0.004578 | 0.1236 | 60.0037 | -0.2243 | 60.1547 | -0.073242 | -0.041199 | -0.036621 | 0.1236 | 0 | 0.17853 | -0.045776 | 0.21973 | -0.004577 | 0.27466 | 123.1155 | 0.041199 | 123.1247 | 123.1155 | 122.9645 | 122.9645 | 122.9233 | -123.111 | -123.0011 | 122.9645 | 123.0835 | 59.9442 | 59.935
357.3281 | 123.3398 | -59.9945 | 62.9333 | -0.083389 | -0.00035668 | 0.063781 | 0.080794 | 0.0031381 | -0.0020337 | -0.00013887 | -0.045532 | 0.00030543 | 0.063215 | 0.066165 | -0.0049262 | 0.0019205 | 0.00071555 | -0.041199 | 62.9608 | -60.1776 | 62.9883 | -59.8343 | -60.2325 | -0.004578 | -0.027466 | 62.9333 | -60.0174 | 63.1119 | -59.9808 | -60.0998 | -59.8389 | -0.18311 | 0.027465 | 0.054931 | 0.16022 | 59.9899 | -0.23804 | 60.173 | -0.054932 | -0.022888 | 0 | 0.17853 | 0.013733 | 0.15564 | -0.10529 | 0.17853 | -0.082397 | 0.34332 | 123.1659 | 0.036621 | 123.1293 | 123.1384 | 122.9507 | 122.9553 | 122.9279 | -123.111 | -122.9507 | 122.9828 | 123.1064 | 59.9533 | 59.967
358.3281 | 123.262 | -59.9899 | 62.9745 | -0.07576 | 0.00071132 | 0.063568 | 0.076522 | -0.0054067 | -0.00011112 | 0.00092933 | -0.042481 | 0.00051903 | 0.063856 | 0.062747 | -0.004499 | 0.0036295 | 0.00092935 | -0.07782 | 62.9837 | -60.1639 | 62.9471 | -59.8846 | -60.2417 | -0.032043 | -0.064087 | 62.9379 | -60.0449 | 63.0615 | -60.0174 | -60.0952 | -59.8618 | -0.17395 | 0.009156 | -0.027465 | 0.10528 | 59.9579 | -0.25177 | 60.1318 | -0.07782 | -0.054932 | -0.036621 | 0.086975 | -0.027466 | 0.12817 | -0.10529 | 0.18311 | -0.050354 | 0.27923 | 123.111 | 0.027466 | 123.1064 | 123.1476 | 122.9828 | 122.9736 | 122.9279 | -123.1384 | -123.0194 | 122.937 | 123.0515 | 59.9121 | 59.9258
359.3281 | 123.3124 | -59.9808 | 62.97 | -0.06813 | 0.00028412 | 0.063354 | 0.079726 | 0.0035653 | -0.0011791 | 0.00092933 | -0.048584 | 0.00051903 | 0.062361 | 0.069583 | -0.0036444 | 0.0046977 | -0.0012071 | -0.027466 | 62.9562 | -60.1822 | 63.0066 | -59.8297 | -60.2234 | -0.032043 | -0.032043 | 62.9288 | -60.022 | 63.1256 | -59.9808 | -60.0769 | -59.8206 | -0.20142 | -0.013733 | 0.036621 | 0.15106 | 59.9487 | -0.24262 | 60.1501 | -0.041199 | -0.041199 | -0.041199 | 0.15564 | 0 | 0.16022 | -0.09613 | 0.20142 | -0.054931 | 0.35248 | 123.1888 | 0.041199 | 123.1476 | 123.1384 | 122.9507 | 122.937 | 122.9095 | -123.1522 | -122.9919 | 122.9874 | 123.1064 | 59.9533 | 59.9487
360.3281 | 123.2483 | -59.9945 | 62.9883 | -0.045242 | 0.0013523 | 0.06485 | 0.079085 | -0.00070713 | -0.00096552 | 0.0015701 | -0.0028075 | -0.00012177 | 0.063429 | 0.063175 | -0.0034308 | 0.0032023 | -0.0024887 | -0.054932 | 63.0066 | -60.1685 | 62.9608 | -59.8846 | -60.228 | -0.004578 | -0.045776 | 62.9517 | -60.0266 | 63.0661 | -60.0082 | -60.0769 | -59.8572 | -0.17395 | 0.018311 | -0.027466 | 0.10986 | 59.9899 | -0.23346 | 60.1639 | -0.059509 | -0.032043 | -0.036621 | 0.07782 | -0.013733 | 0.13733 | -0.082397 | 0.16937 | -0.050354 | 0.28381 | 123.1293 | 0.01831 | 123.0927 | 123.175 | 122.9782 | 123.0011 | 122.9462 | -123.1567 | -123.0148 | 122.9553 | 123.0606 | 59.9396 | 59.9487
361.3281 | 123.2483 | -59.9854 | 62.9745 | 0.0081632 | 0.0022067 | 0.063995 | 0.079513 | 0.0010019 | 0.0015979 | 0.0019973 | -0.07605 | 0.0026552 | 0.062147 | 0.064029 | -0.00279 | 0.0044839 | -0.0012071 | -0.11444 | 62.9654 | -60.1959 | 62.9288 | -59.9304 | -60.2921 | -0.082397 | -0.10529 | 62.9425 | -60.0494 | 63.0798 | -60.0311 | -60.1135 | -59.8709 | -0.21057 | -0.009155 | -0.045776 | 0.054932 | 59.903 | -0.3067 | 60.1135 | -0.09613 | -0.064086 | -0.032043 | 0.10529 | -0.045776 | 0.11444 | -0.12817 | 0.17853 | -0.064087 | 0.2655 | 123.1247 | 0.01831 | 123.1293 | 123.1613 | 122.9919 | 122.9507 | 122.9279 | -123.1705 | -123.024 | 122.9141 | 123.0652 | 59.8709 | 59.8801
362.3281 | 123.2437 | -59.9899 | 62.9883 | -0.083389 | 0.0015659 | 0.063568 | 0.076522 | -0.00049353 | -0.0031017 | -0.0029159 | -0.02417 | 0.00051903 | 0.061293 | 0.05997 | -0.0053534 | 0.00085247 | -0.00035245 | -0.064087 | 62.97 | -60.1593 | 62.9517 | -59.8709 | -60.2463 | -0.013733 | -0.082397 | 62.9562 | -60.0311 | 63.0707 | -60.0082 | -60.1044 | -59.8618 | -0.16937 | -0.01831 | -0.036621 | 0.11902 | 59.9762 | -0.25635 | 60.1456 | -0.086975 | -0.041199 | -0.032043 | 0.082398 | -0.018311 | 0.12817 | -0.11444 | 0.16937 | -0.073242 | 0.28839 | 123.111 | 0.022888 | 123.1018 | 123.1293 | 122.9874 | 122.9599 | 122.9462 | -123.1476 | -123.0194 | 122.9416 | 123.0606 | 59.9258 | 59.9075
363.3281 | 123.2071 | -60.0082 | 62.9425 | -0.091019 | 0.0030613 | 0.063354 | 0.081008 | 0.0020701 | -0.0011791 | 0.00050193 | -0.045532 | 0.0020144 | 0.063429 | 0.061038 | -0.0034308 | 0.0027751 | -0.0020615 | -0.032043 | 62.9471 | -60.1685 | 63.002 | -59.8297 | -60.2234 | -0.018311 | -0.032043 | 62.9425 | -60.054 | 63.0981 | -59.9808 | -60.1501 | -59.9075 | -0.16022 | 0.004578 | 0.059509 | 0.17853 | 59.9899 | -0.21515 | 60.1501 | -0.054932 | -0.045776 | 0 | 0.15564 | 0.027466 | 0.10071 | -0.14191 | 0.14648 | -0.09613 | 0.33874 | 123.1705 | 0.073242 | 123.1522 | 123.1155 | 122.9965 | 122.9553 | 122.9507 | -123.111 | -122.9965 | 123.0103 | 123.1064 | 59.9762 | 59.9762
364.3281 | 123.2529 | -59.9625 | 62.9837 | -0.045242 | 0.00092492 | 0.064422 | 0.077804 | -0.0015615 | 0.00031608 | -0.0016343 | -0.021118 | -0.00012177 | 0.062788 | 0.063175 | -0.0049262 | 0.00063867 | -0.0018479 | -0.054932 | 62.9974 | -60.1593 | 62.9654 | -59.8938 | -60.2234 | 0.009155 | -0.027466 | 62.9608 | -60.0266 | 63.1943 | -60.0906 | -59.9762 | -59.8068 | -0.19684 | 0.013733 | -0.018311 | 0.068664 | 59.9716 | -0.26093 | 60.1685 | -0.064087 | -0.064087 | -0.022889 | 0.21057 | -0.12817 | 0.15564 | -0.013733 | 0.21973 | 0.050354 | 0.2655 | 123.1247 | -0.064087 | 123.2208 | 123.1567 | 122.9874 | 122.9599 | 122.9233 | -123.143 | -123.0103 | 122.9279 | 123.1567 | 59.9075 | 59.935
365.3281 | 123.3124 | -60.0082 | 62.9471 | -0.14442 | 0.00049772 | 0.067627 | 0.07994 | 0.0016427 | -0.0013929 | 0.0011429 | -0.048584 | 0.0018008 | 0.062575 | 0.064029 | -0.0042854 | 0.0017069 | 0.00050195 | -0.036621 | 62.9379 | -60.1593 | 63.002 | -59.8251 | -60.2325 | -0.041199 | -0.027466 | 62.9379 | -60.0311 | 63.089 | -59.9945 | -60.0677 | -59.8206 | -0.15106 | -0.009156 | 0.054931 | 0.18311 | 59.967 | -0.2243 | 60.1181 | -0.073242 | -0.022888 | -0.009156 | 0.14191 | 0.013733 | 0.18768 | -0.059509 | 0.21057 | -0.036621 | 0.33417 | 123.1613 | 0.036621 | 123.1201 | 123.0972 | 122.9691 | 122.9462 | 122.9462 | -123.1064 | -122.9782 | 123.0103 | 123.0972 | 59.9716 | 59.9808
366.3281 | 123.23 | -59.9808 | 62.9929 | -0.052872 | 0.0011385 | 0.063995 | 0.078872 | -0.0019889 | -0.00053832 | 0.00071573 | -0.018066 | -0.0016172 | 0.061934 | 0.064029 | -0.004499 | 0.0014933 | -0.0037705 | -0.064087 | 62.9562 | -60.1868 | 62.9562 | -59.8938 | -60.2646 | -0.050354 | -0.07782 | 62.9242 | -60.0494 | 63.0707 | -60.0128 | -60.0952 | -59.8801 | -0.20599 | -0.036621 | -0.036621 | 0.086975 | 59.9304 | -0.28381 | 60.1364 | -0.077819 | -0.068664 | -0.068665 | 0.07782 | -0.032043 | 0.10071 | -0.11444 | 0.16937 | -0.045777 | 0.29297 | 123.143 | 0.036621 | 123.1201 | 123.143 | 122.9736 | 122.937 | 122.905 | -123.1796 | -123.0423 | 122.937 | 123.0515 | 59.9167 | 59.903
367.3281 | 123.2666 | -59.9716 | 62.9471 | -0.029984 | 0.0011385 | 0.063995 | 0.077804 | 0.0018565 | -0.0016065 | -0.0024887 | -0.060791 | 0.002228 | 0.063429 | 0.057834 | -0.0049262 | 0.0034159 | 0.0026383 | -0.041199 | 62.9333 | -60.1685 | 63.0066 | -59.8297 | -60.2371 | -0.045776 | -0.027466 | 62.9242 | -60.0311 | 63.0981 | -59.967 | -60.0769 | -59.8206 | -0.19684 | -0.013733 | 0.059509 | 0.14191 | 59.9258 | -0.2655 | 60.1227 | -0.068665 | -0.059509 | -0.022889 | 0.15106 | 0.004578 | 0.15106 | -0.10529 | 0.21057 | -0.045776 | 0.33874 | 123.175 | 0.064087 | 123.1293 | 123.1018 | 122.9553 | 122.905 | 122.8958 | -123.1155 | -122.9782 | 122.9782 | 123.0698 | 59.9304 | 59.9442
368.3281 | 123.262 | -59.9945 | 62.9425 | -0.11391 | 0.0026339 | 0.064422 | 0.078017 | -0.00070713 | -0.0011791 | -0.00035247 | -0.0028075 | 0.00116 | 0.065138 | 0.058261 | -0.0049262 | 0.0019205 | 0.00050195 | -0.050354 | 62.9837 | -60.173 | 62.9562 | -59.8755 | -60.26 | -0.032043 | -0.064087 | 62.9242 | -60.0311 | 63.0478 | -60.0128 | -60.1044 | -59.8801 | -0.17853 | 0.041199 | 0.013733 | 0.11902 | 59.9625 | -0.2655 | 60.141 | -0.086975 | -0.036621 | -0.018311 | 0.10529 | -0.01831 | 0.11444 | -0.10986 | 0.15106 | -0.073242 | 0.29755 | 123.1293 | 0.018311 | 123.0789 | 123.1567 | 122.9553 | 122.9782 | 122.9187 | -123.1155 | -122.9736 | 122.9507 | 123.0423 | 59.9442 | 59.9304
369.3281 | 123.2849 | -59.9945 | 62.97 | -0.083389 | 0.0024203 | 0.064422 | 0.078231 | -0.0013479 | -0.00032472 | 0.00071573 | -0.072998 | -0.00033537 | 0.064924 | 0.062534 | -0.0036444 | 0.0025613 | -0.0041977 | -0.041199 | 62.9562 | -60.1593 | 62.9791 | -59.8572 | -60.2417 | -0.027466 | -0.045776 | 62.9288 | -60.0357 | 63.1302 | -59.9762 | -60.0723 | -59.8114 | -0.16479 | -0.013733 | 0.009155 | 0.13733 | 59.967 | -0.24719 | 60.1318 | -0.082397 | -0.041199 | -0.041199 | 0.16022 | 0.018311 | 0.18311 | -0.07782 | 0.22431 | -0.036621 | 0.30212 | 123.1384 | 0.05951 | 123.1659 | 123.1155 | 122.9645 | 122.9507 | 122.9233 | -123.1293 | -123.0057 | 122.9736 | 123.1247 | 59.9533 | 59.9487
370.3281 | 123.2803 | -59.9625 | 62.9745 | -0.060501 | -0.00099768 | 0.063781 | 0.077376 | 0.0014291 | 0.00074348 | -0.0022751 | -0.021118 | -0.00012177 | 0.062575 | 0.057621 | -0.0019354 | -0.00064293 | 7.4746e-05 | -0.032043 | 63.002 | -60.1639 | 63.0112 | -59.7748 | -60.2509 | 0.013733 | -0.041199 | 62.9517 | -60.0403 | 63.0753 | -59.9808 | -60.0906 | -59.8618 | -0.20142 | 0.027466 | 0.036621 | 0.18768 | 59.9762 | -0.28839 | 60.1776 | -0.086975 | -0.07782 | -0.022888 | 0.10071 | -0.018311 | 0.10071 | -0.12817 | 0.17853 | -0.050354 | 0.3891 | 123.175 | 0.059509 | 123.1155 | 123.1659 | 122.9919 | 122.9645 | 122.9141 | -123.1384 | -123.0148 | 122.9736 | 123.0377 | 59.9304 | 59.9213
371.3281 | 123.2986 | -59.9716 | 62.9379 | -0.12917 | 0.0028475 | 0.062927 | 0.078872 | 0.0010019 | -0.00096552 | 0.00050193 | -0.039429 | 0.00030543 | 0.063429 | 0.066593 | -0.0051398 | 0.0021341 | -0.0022751 | -0.027466 | 62.9333 | -60.1822 | 62.9883 | -59.8389 | -60.2188 | -0.032043 | -0.013733 | 62.9105 | -60.0266 | 63.208 | -59.9991 | -60.0128 | -59.7931 | -0.21057 | -0.004577 | 0.050354 | 0.13275 | 59.9396 | -0.24719 | 60.1501 | -0.036621 | -0.054931 | -0.027466 | 0.27008 | -0.027465 | 0.17853 | -0.041198 | 0.23346 | 0.013733 | 0.34332 | 123.1705 | 0.027466 | 123.2346 | 123.1155 | 122.937 | 122.905 | 122.8821 | -123.1201 | -122.9645 | 122.9599 | 123.1796 | 59.9442 | 59.9579
372.3281 | 123.2346 | -59.9716 | 62.97 | -0.06813 | -0.00057028 | 0.0625 | 0.079085 | -0.00092073 | -0.0011791 | -0.0012071 | -0.02417 | 0.00094643 | 0.062147 | 0.064029 | -0.0025764 | 0.0019205 | 0.0011429 | -0.059509 | 62.9837 | -60.173 | 62.9333 | -59.9121 | -60.228 | -0.022888 | -0.064087 | 62.9425 | -60.0494 | 63.0615 | -60.0128 | -60.0861 | -59.8663 | -0.20142 | 0.013733 | -0.036621 | 0.05951 | 59.9487 | -0.25635 | 60.1501 | -0.054931 | -0.077819 | -0.027466 | 0.091552 | -0.041198 | 0.10529 | -0.11444 | 0.18311 | -0.036622 | 0.26093 | 123.1064 | 0.036621 | 123.111 | 123.1567 | 122.9919 | 122.9553 | 122.9141 | -123.143 | -123.0194 | 122.905 | 123.0331 | 59.9121 | 59.9075
373.3281 | 123.1842 | -60.0174 | 62.9196 | -0.091019 | 0.0028475 | 0.065063 | 0.078445 | -0.0034841 | 0.00095708 | -0.0012071 | -0.045532 | 0.00094643 | 0.064283 | 0.061893 | -0.0051398 | 0.0029887 | 0.00071555 | -0.036621 | 62.97 | -60.1776 | 62.9883 | -59.8434 | -60.2142 | -0.022888 | -0.027466 | 62.9196 | -60.0357 | 63.1119 | -59.9716 | -60.0769 | -59.8297 | -0.16022 | 0.050354 | 0.068664 | 0.17395 | 59.9945 | -0.19684 | 60.1547 | -0.036621 | -0.018311 | 0 | 0.19226 | 0.045776 | 0.18768 | -0.059509 | 0.20599 | -0.041198 | 0.33417 | 123.1659 | 0.064087 | 123.1476 | 123.1476 | 122.9553 | 122.9874 | 122.937 | -123.0972 | -122.9553 | 123.0057 | 123.1293 | 59.9808 | 59.9899
374.3281 | 123.262 | -59.967 | 62.9745 | -0.12917 | 0.0011385 | 0.062713 | 0.079299 | 0.0033517 | -0.00053832 | -0.00013887 | -0.021118 | 0.00116 | 0.064497 | 0.063388 | -0.00279 | 0.0025613 | 0.00028835 | -0.059509 | 62.9562 | -60.173 | 62.9562 | -59.8709 | -60.2554 | -0.018311 | -0.082397 | 62.9425 | -60.0311 | 63.0661 | -60.0174 | -60.1044 | -59.8526 | -0.20599 | -0.01831 | -0.01831 | 0.09613 | 59.9487 | -0.28839 | 60.1547 | -0.082397 | -0.064087 | -0.032043 | 0.091553 | -0.050354 | 0.11444 | -0.13733 | 0.17853 | -0.073242 | 0.30212 | 123.1293 | 0.013733 | 123.0972 | 123.1293 | 122.9736 | 122.9233 | 122.9095 | -123.1476 | -123.0057 | 122.9233 | 123.0331 | 59.9075 | 59.8846
375.3281 | 123.3032 | -59.9899 | 62.9654 | -0.060501 | 0.0024203 | 0.063354 | 0.076522 | -0.00070713 | -0.0016065 | -0.0037705 | -0.063843 | -0.00033537 | 0.060866 | 0.063175 | -0.0051398 | 0.0042703 | 0.00028835 | -0.036621 | 62.9517 | -60.1776 | 62.9883 | -59.8618 | -60.2325 | -0.032043 | -0.045776 | 62.9379 | -60.0037 | 63.1027 | -59.9808 | -60.0815 | -59.8206 | -0.18768 | -0.013733 | 0.022888 | 0.12817 | 59.9579 | -0.24262 | 60.1456 | -0.054932 | -0.013733 | -0.027466 | 0.13733 | 0.009155 | 0.16937 | -0.091553 | 0.1831 | -0.07782 | 0.31586 | 123.1659 | 0.022888 | 123.1064 | 123.1293 | 122.9416 | 122.9416 | 122.9279 | -123.143 | -122.9691 | 122.9782 | 123.0927 | 59.9533 | 59.9442
376.3281 | 123.2346 | -60.0174 | 62.97 | -0.11391 | -0.00035668 | 0.062286 | 0.078231 | -0.0011343 | -0.00053832 | 0.0011429 | -0.033325 | -0.00012177 | 0.062788 | 0.065311 | -0.0019354 | 0.0021341 | 0.00071555 | -0.059509 | 62.97 | -60.1776 | 62.9654 | -59.8618 | -60.2554 | -0.032043 | -0.068665 | 62.9379 | -60.0266 | 63.0707 | -59.9991 | -60.1044 | -59.8801 | -0.16022 | 0 | -0.004578 | 0.15564 | 59.9854 | -0.23804 | 60.1456 | -0.07782 | -0.009155 | -0.032044 | 0.10071 | 0.018311 | 0.13733 | -0.086975 | 0.14648 | -0.07782 | 0.31586 | 123.143 | 0.027466 | 123.0972 | 123.1476 | 122.9645 | 122.9874 | 122.9553 | -123.1476 | -122.9965 | 122.9828 | 123.0881 | 59.9579 | 59.9487
377.3281 | 123.2712 | -59.9945 | 62.9654 | -0.14442 | 0.0026339 | 0.063995 | 0.078231 | -0.0015615 | 0.00095708 | -0.0039841 | -0.039429 | 9.1834e-05 | 0.064497 | 0.056552 | -0.0049262 | 0.0017069 | -0.0037705 | -0.050354 | 62.915 | -60.173 | 63.1393 | -59.7107 | -60.2783 | 0.009155 | -0.036621 | 62.9333 | -60.0357 | 63.1256 | -59.9808 | -60.0906 | -59.8297 | -0.17853 | -0.050354 | 0.17395 | 0.28381 | 60.0037 | -0.28381 | 60.1822 | -0.10529 | -0.041199 | -0.032043 | 0.16022 | 0.013733 | 0.16479 | -0.09613 | 0.20599 | -0.054931 | 0.46234 | 123.3124 | 0.054932 | 123.1613 | 123.0881 | 122.9691 | 122.9095 | 122.9279 | -123.1384 | -123.0011 | 123.1338 | 123.1201 | 59.9442 | 59.9579
378.3281 | 123.2666 | -59.9808 | 62.9837 | -0.052872 | 0.0032749 | 0.061432 | 0.079299 | 0.00014747 | -0.0011791 | -0.0027023 | -0.02417 | 0.00116 | 0.065565 | 0.066593 | -0.0023626 | 0.00021147 | -0.00056605 | -0.050354 | 62.9883 | -60.173 | 62.9379 | -59.8572 | -60.2692 | -0.009155 | -0.022888 | 62.97 | -60.0311 | 63.0798 | -59.9945 | -60.054 | -59.8434 | -0.19226 | 0.004577 | -0.045777 | 0.1236 | 59.9716 | -0.28839 | 60.1639 | -0.09613 | -0.050354 | -0.013733 | 0.09613 | -0.013733 | 0.13733 | -0.073242 | 0.18768 | -0.022888 | 0.31586 | 123.111 | 0.036621 | 123.111 | 123.1613 | 123.0011 | 122.9691 | 122.9507 | -123.1567 | -123.0148 | 122.9187 | 123.0606 | 59.9304 | 59.9579
379.3281 | 123.2712 | -59.9899 | 62.9517 | -0.12154 | 0.0015659 | 0.063995 | 0.078658 | -0.0041251 | 0.00095708 | -0.0039841 | -0.054688 | 0.00051903 | 0.06642 | 0.068088 | -0.0049262 | 0.0023477 | -0.0052659 | -0.032043 | 62.9288 | -60.1685 | 63.002 | -59.8343 | -60.2325 | -0.032043 | -0.25635 | 62.8647 | -60.0861 | 63.1531 | -59.9854 | -60.0632 | -59.7931 | -0.17853 | -0.022888 | 0.050354 | 0.15564 | 59.9579 | -0.24262 | 60.1364 | -0.064087 | -0.096131 | -0.086975 | 0.20142 | 0.004577 | 0.19684 | -0.073242 | 0.29297 | 0.022889 | 0.33417 | 123.1705 | 0.10071 | 123.2391 | 123.0972 | 122.9507 | 122.9187 | 122.8546 | -123.1201 | -123.0377 | 122.9919 | 123.143 | 59.9579 | 59.7336
380.3281 | 123.2529 | -59.9762 | 63.0112 | -0.11391 | -0.0012113 | 0.06485 | 0.079726 | -0.0015615 | -0.00032472 | -0.00077967 | -0.02417 | 0.00116 | 0.062788 | 0.059116 | -0.0023626 | 0.0019205 | -0.0012071 | -0.064087 | 62.9791 | -60.1822 | 62.97 | -59.8663 | -60.2554 | -0.022888 | -0.07782 | 62.9379 | -60.0174 | 63.0753 | -60.0128 | -60.1181 | -59.848 | -0.20599 | -0.032043 | -0.041198 | 0.10986 | 59.9533 | -0.27924 | 60.1593 | -0.073242 | -0.041199 | -0.073242 | 0.064087 | -0.036621 | 0.12817 | -0.14191 | 0.16937 | -0.10071 | 0.31586 | 123.1522 | 0.004578 | 123.0927 | 123.1613 | 122.9553 | 122.9553 | 122.9141 | -123.1934 | -123.0286 | 122.9462 | 123.0515 | 59.9121 | 59.8984
381.3281 | 123.2574 | -59.9991 | 62.9745 | -0.083389 | 0.0041293 | 0.064209 | 0.082076 | 0.00078827 | -0.00011112 | -0.0014207 | -0.082153 | -0.00054897 | 0.06407 | 0.067874 | -0.00279 | 0.0029887 | -0.0029159 | -0.09613 | 62.9929 | -60.1959 | 62.9196 | -59.9396 | -60.2921 | -0.086975 | -0.10071 | 62.9471 | -60.0494 | 63.0798 | -60.0037 | -60.1089 | -59.8572 | -0.19684 | 0.018311 | -0.054931 | 0.059509 | 59.9121 | -0.29297 | 60.1089 | -0.09613 | -0.050354 | -0.027465 | 0.10529 | -0.004578 | 0.14191 | -0.10986 | 0.19226 | -0.05951 | 0.25635 | 123.1155 | 0.045776 | 123.1293 | 123.1888 | 122.9965 | 122.9919 | 122.9462 | -123.1705 | -123.024 | 122.9187 | 123.0789 | 59.903 | 59.8984
382.3281 | 123.2254 | -60.0037 | 62.9562 | -0.052872 | 0.0011385 | 0.064636 | 0.078658 | -0.00027993 | -0.0013929 | -0.00077967 | -0.027222 | -0.00054897 | 0.062788 | 0.061038 | -0.0030036 | 0.0032023 | -0.0024887 | -0.027466 | 62.9745 | -60.1868 | 62.9608 | -59.8572 | -60.2463 | -0.032043 | -0.036621 | 62.9471 | -60.0357 | 63.0753 | -60.0082 | -60.1089 | -59.8572 | -0.18311 | 0.01831 | 0.004577 | 0.14648 | 59.9716 | -0.24262 | 60.1547 | -0.059509 | -0.032044 | -0.009155 | 0.11902 | -0.004578 | 0.14648 | -0.10529 | 0.17853 | -0.073242 | 0.32959 | 123.1476 | 0.027466 | 123.111 | 123.1613 | 122.9828 | 122.9782 | 122.9507 | -123.143 | -122.9919 | 122.9645 | 123.0789 | 59.9762 | 59.967
383.3281 | 123.2666 | -59.9579 | 62.9608 | -0.098648 | -0.00014308 | 0.063995 | 0.079085 | 0.00078827 | -0.0022473 | 0.00092933 | -0.066895 | 0.00030543 | 0.063429 | 0.064456 | -0.004499 | 0.0032023 | -0.0022751 | -0.054932 | 62.9517 | -60.1547 | 62.9837 | -59.8389 | -60.141 | -0.027466 | -0.027466 | 62.9517 | -60.0266 | 63.1119 | -59.967 | -60.0723 | -59.8206 | -0.19684 | -0.009155 | 0.022889 | 0.11902 | 59.9304 | -0.1831 | 60.1273 | 0.013733 | -0.068664 | -0.009155 | 0.15106 | -0.009155 | 0.13733 | -0.11444 | 0.20599 | -0.045777 | 0.31586 | 123.1384 | 0.059509 | 123.1384 | 123.1064 | 122.9782 | 122.9095 | 122.9095 | -123.1155 | -122.9874 | 122.9416 | 123.0698 | 59.903 | 59.9304
384.3281 | 123.2666 | -59.9945 | 62.9929 | -0.06813 | 0.0013523 | 0.062072 | 0.080154 | -0.0013479 | 0.00052988 | -0.00077967 | -0.011963 | 0.00073263 | 0.063002 | 0.06467 | -0.002149 | 0.0012797 | -0.00013885 | -0.07782 | 62.9883 | -60.1685 | 62.9745 | -59.8801 | -60.2875 | -0.032043 | -0.032043 | 62.9517 | -60.0494 | 63.0707 | -59.9945 | -60.0769 | -59.8434 | -0.17395 | -0.004578 | -0.018311 | 0.11444 | 59.9625 | -0.29297 | 60.1364 | -0.11902 | -0.054931 | -0.041199 | 0.07782 | 0 | 0.15106 | -0.082397 | 0.20599 | -0.027466 | 0.28839 | 123.143 | 0.054931 | 123.1201 | 123.1567 | 123.0011 | 122.9828 | 122.9462 | -123.1613 | -123.0423 | 122.9691 | 123.0652 | 59.9167 | 59.9625
385.3281 | 123.2986 | -59.9762 | 62.9745 | -0.098648 | 0.0022067 | 0.063568 | 0.079085 | 0.0018565 | -0.00011112 | -0.0018479 | -0.079102 | 0.0013736 | 0.063643 | 0.065097 | -0.0042854 | 0.0012797 | -0.00077965 | -0.041199 | 62.9288 | -60.1776 | 62.9974 | -59.8526 | -60.2142 | -0.032043 | -0.19684 | 62.8967 | -60.0906 | 63.1393 | -59.9762 | -60.0769 | -59.8022 | -0.20142 | -0.045776 | 0.022889 | 0.1236 | 59.9442 | -0.23804 | 60.1456 | -0.036621 | -0.11444 | -0.077819 | 0.16479 | 0 | 0.17395 | -0.10071 | 0.28839 | 0.013733 | 0.32501 | 123.175 | 0.11444 | 123.23 | 123.1064 | 122.9874 | 122.905 | 122.8729 | -123.1522 | -123.0652 | 122.9736 | 123.1155 | 59.935 | 59.7794
386.3281 | 123.2346 | -60.0037 | 62.9883 | -0.083389 | 7.0518e-05 | 0.063141 | 0.079085 | -0.0013479 | -0.00011112 | -0.0029159 | 0.052124 | 0.00094643 | 0.064497 | 0.059116 | -0.0049262 | 0.0027751 | -0.00077965 | -0.059509 | 62.9883 | -60.1639 | 62.9471 | -59.8984 | -60.2509 | -0.018311 | -0.13733 | 62.9517 | -60.0037 | 63.0615 | -60.0357 | -60.0677 | -59.8389 | -0.16022 | 0 | -0.041198 | 0.10529 | 59.9854 | -0.24719 | 60.1456 | -0.086975 | 0 | -0.036621 | 0.073242 | -0.032044 | 0.16479 | -0.064087 | 0.16479 | -0.064087 | 0.2655 | 123.111 | -0.032044 | 123.0652 | 123.1522 | 122.9553 | 122.9919 | 122.9553 | -123.1522 | -122.9919 | 122.9507 | 123.0652 | 59.9442 | 59.8663
387.3281 | 123.3719 | -60.0128 | 62.9425 | -0.1368 | -0.00014308 | 0.066131 | 0.07994 | 0.0029245 | -0.0022473 | 0.00028833 | -0.036377 | -0.00012177 | 0.065779 | 0.065311 | -0.0040716 | 0.0027751 | 0.00050195 | -0.054932 | 62.9425 | -60.2142 | 62.9883 | -59.848 | -60.2325 | -0.050354 | -0.032043 | 62.9196 | -60.0266 | 63.1119 | -59.9396 | -60.3516 | -59.9716 | -0.20142 | 0 | 0.045776 | 0.16479 | 59.9625 | -0.21973 | 60.1639 | -0.018311 | -0.013733 | -0.022888 | 0.16937 | 0.073242 | 0.041198 | -0.33875 | 0.054931 | -0.32501 | 0.36621 | 123.2025 | 0.086975 | 123.1384 | 123.1567 | 122.9462 | 122.9553 | 122.9324 | -123.1567 | -122.9691 | 123.0011 | 123.1247 | 59.9579 | 59.9808
388.3281 | 123.2391 | -59.9808 | 62.97 | -0.11391 | 0.0034885 | 0.063781 | 0.080154 | -0.0017751 | -0.0013929 | -0.00099327 | -0.039429 | -0.00012177 | 0.065352 | 0.065952 | -0.00279 | 0.0034159 | 0.0019973 | -0.068665 | 62.9379 | -60.1822 | 62.9608 | -59.8572 | -60.2371 | -0.018311 | -0.041199 | 62.9471 | -60.0403 | 63.0707 | -60.0128 | -60.0952 | -59.8572 | -0.20142 | -0.032044 | -0.009156 | 0.1236 | 59.9625 | -0.25635 | 60.1639 | -0.054932 | -0.059509 | -0.022888 | 0.10071 | -0.032043 | 0.1236 | -0.11444 | 0.18311 | -0.054932 | 0.32501 | 123.143 | 0.027466 | 123.111 | 123.1201 | 122.9874 | 122.9187 | 122.9279 | -123.1522 | -123.0103 | 122.9416 | 123.0515 | 59.9121 | 59.9396
389.3281 | 123.2849 | -59.9991 | 62.9425 | -0.07576 | 0.00092492 | 0.064209 | 0.080794 | 0.0022837 | 0.0015979 | -0.0016343 | -0.048584 | 0.00073263 | 0.061934 | 0.066593 | -0.00279 | 0.0029887 | 7.4746e-05 | -0.073242 | 62.9608 | -60.2005 | 62.97 | -59.8709 | -60.2463 | -0.054932 | -0.068665 | 62.9379 | -60.0403 | 63.1027 | -59.9945 | -60.0952 | -59.8297 | -0.20142 | 0.01831 | 0.027466 | 0.12817 | 59.9442 | -0.24719 | 60.1456 | -0.045777 | -0.041199 | -0.004578 | 0.16022 | 0.004577 | 0.16937 | -0.096131 | 0.21057 | -0.054932 | 0.32959 | 123.1705 | 0.045776 | 123.143 | 123.1613 | 122.9782 | 122.9599 | 122.937 | -123.143 | -122.9828 | 122.9691 | 123.1018 | 59.9258 | 59.9304
390.3281 | 123.2849 | -60.0037 | 62.9654 | -0.16731 | 0.0024203 | 0.061859 | 0.081008 | -0.00070713 | 0.0015979 | -0.0020615 | -0.039429 | 0.00030543 | 0.064924 | 0.061252 | -0.0025764 | 0.0040567 | -0.0016343 | -0.036621 | 62.9791 | -60.1456 | 62.9837 | -59.8434 | -60.2325 | -0.027466 | -0.027466 | 62.9242 | -60.0128 | 63.0844 | -60.0082 | -60.0723 | -59.848 | -0.14191 | 0.013733 | 0.018311 | 0.16022 | 59.9762 | -0.22888 | 60.1181 | -0.086975 | -0.009155 | -0.041199 | 0.11902 | -0.004578 | 0.15564 | -0.068665 | 0.16479 | -0.05951 | 0.30212 | 123.1293 | 0.004577 | 123.0972 | 123.1247 | 122.937 | 122.9828 | 122.9279 | -123.111 | -122.9782 | 122.9874 | 123.0881 | 59.967 | 59.9762
391.3281 | 123.3124 | -59.9762 | 62.9517 | -0.098648 | 0.0022067 | 0.064422 | 0.080367 | 0.0018565 | -0.0018201 | 0.0013565 | -0.066895 | -0.00119 | 0.063429 | 0.064029 | -0.0030036 | 0.0019205 | -0.0037705 | -0.054932 | 62.9333 | -60.1868 | 62.9974 | -59.8251 | -60.2371 | -0.16479 | 0.1236 | 62.915 | -60.022 | 63.1302 | -59.9716 | -60.0723 | -59.8022 | -0.21057 | -0.01831 | 0.045777 | 0.15106 | 59.8114 | -0.26093 | 60.022 | -0.050354 | -0.045777 | -0.036621 | 0.17853 | 0.004577 | 0.17395 | -0.096131 | 0.21973 | -0.050354 | 0.36163 | 123.1842 | 0.050354 | 123.1522 | 123.1201 | 122.937 | 122.9095 | 122.8912 | -123.1384 | -122.9736 | 122.9736 | 123.1064 | 59.9213 | 60.0998
392.3281 | 123.2391 | -59.9945 | 62.9654 | -0.083389 | 0.00071132 | 0.064422 | 0.080581 | 0.0022837 | -0.00053832 | -0.00077967 | -0.021118 | 0.00073263 | 0.063215 | 0.068302 | -0.0040716 | 0.0021341 | -0.0039841 | -0.064087 | 62.9379 | -60.1685 | 62.97 | -59.8572 | -60.2463 | -0.036621 | -0.068665 | 62.9425 | -60.0311 | 63.0615 | -60.022 | -60.0906 | -59.8618 | -0.17395 | -0.027466 | 0.004578 | 0.13733 | 59.9579 | -0.25177 | 60.1318 | -0.07782 | -0.036621 | -0.022888 | 0.09613 | -0.027466 | 0.13275 | -0.09613 | 0.16937 | -0.059509 | 0.31128 | 123.1384 | 0.009155 | 123.0927 | 123.1064 | 122.9736 | 122.9324 | 122.937 | -123.1338 | -122.9965 | 122.9645 | 123.056 | 59.9304 | 59.9258
393.3281 | 123.2758 | -59.9899 | 62.9745 | -0.091019 | 0.0032749 | 0.065063 | 0.078872 | -0.0028433 | 0.00095708 | -0.0024887 | -0.063843 | -0.00033537 | 0.062361 | 0.062747 | -0.0040716 | 0.0021341 | -0.0022751 | -0.027466 | 62.9791 | -60.173 | 62.9929 | -59.8572 | -60.228 | -0.045776 | -0.050354 | 62.9333 | -60.0403 | 62.9929 | -59.7702 | -59.935 | -59.7885 | -0.18311 | 0.004578 | 0.018311 | 0.13275 | 59.9442 | -0.23804 | 60.1273 | -0.054931 | -0.050354 | -0.041198 | 0.018311 | 0.21973 | 0.20142 | 0.054931 | 0.25177 | 0.10529 | 0.31586 | 123.1659 | 0.27008 | 123.0331 | 123.1522 | 122.9736 | 122.9691 | 122.9233 | -123.1476 | -123.0148 | 122.9828 | 122.9828 | 59.9625 | 59.9396
394.3281 | 123.2529 | -59.9762 | 62.9791 | -0.10628 | -0.00035668 | 0.063141 | 0.078231 | -0.00049353 | -0.0016065 | 0.00028833 | -0.030273 | -0.0014036 | 0.065138 | 0.061466 | -0.003858 | 0.00021147 | 7.4746e-05 | -0.059509 | 62.9883 | -60.1639 | 62.9517 | -59.8709 | -60.2325 | 0.004578 | -0.022888 | 62.9425 | -60.022 | 63.089 | -59.9808 | -60.0494 | -59.8251 | -0.18768 | 0.009155 | -0.027466 | 0.10529 | 59.9808 | -0.25635 | 60.1685 | -0.068665 | -0.045777 | -0.036621 | 0.10986 | -0.004578 | 0.15106 | -0.073242 | 0.19684 | -0.027465 | 0.29297 | 123.1155 | 0.041199 | 123.111 | 123.1522 | 122.9645 | 122.9645 | 122.9187 | -123.143 | -123.0011 | 122.9279 | 123.0652 | 59.9167 | 59.9533
395.3281 | 123.2483 | -59.9945 | 62.9791 | -0.052872 | 0.00028412 | 0.062286 | 0.078872 | 0.0016427 | 0.00010248 | 0.00050193 | -0.088257 | 0.0013736 | 0.063429 | 0.063602 | -0.0036444 | 0.0023477 | -0.0020615 | -0.10529 | 62.9929 | -60.1959 | 62.9013 | -59.9487 | -60.3104 | -0.10071 | -0.12817 | 62.9608 | -60.0723 | 63.0615 | -60.0494 | -60.1364 | -59.8984 | -0.20142 | 0.013733 | -0.07782 | 0.045777 | 59.8938 | -0.31586 | 60.0952 | -0.11444 | -0.07782 | -0.018311 | 0.082397 | -0.054931 | 0.096131 | -0.14191 | 0.17395 | -0.064087 | 0.24719 | 123.0972 | 0.022889 | 123.1338 | 123.1888 | 123.0331 | 122.9874 | 122.9553 | -123.175 | -123.0515 | 122.8958 | 123.056 | 59.8892 | 59.8663
396.3281 | 123.2391 | -59.9945 | 62.9379 | -0.1902 | 0.0017795 | 0.064636 | 0.079299 | 0.0010019 | -0.0035291 | -0.0024887 | -0.039429 | 0.00073263 | 0.065352 | 0.060398 | -0.0040716 | 0.0027751 | -0.0046249 | 0.091553 | 62.9562 | -60.1822 | 63.0157 | -59.8206 | -60.2463 | -0.045776 | -0.022888 | 62.915 | -60.0037 | 63.1119 | -59.9899 | -60.0769 | -59.8251 | -0.18768 | 0.018311 | 0.07782 | 0.17395 | 59.9487 | -0.25177 | 60.1364 | -0.064087 | -0.009155 | -0.022888 | 0.17395 | 0.004578 | 0.16937 | -0.082397 | 0.17853 | -0.073242 | 0.36163 | 123.1979 | 0.013733 | 123.1155 | 123.1384 | 122.9187 | 122.9507 | 122.9095 | -123.1201 | -122.9416 | 123.0103 | 123.1064 | 60.0861 | 59.9716
397.3281 | 123.2758 | -60.0174 | 62.9654 | -0.10628 | 0.00092492 | 0.065918 | 0.079513 | -0.0017751 | 0.00031608 | -0.00013887 | -0.048584 | 0.00073263 | 0.065565 | 0.06467 | -0.0057806 | 0.0029887 | -0.0046249 | -0.15106 | 62.915 | -60.2005 | 62.9745 | -59.8068 | -60.228 | -0.032043 | -0.041199 | 62.9288 | -60.0128 | 63.0936 | -59.9716 | -60.0677 | -59.8434 | -0.1831 | -0.050354 | 0.009155 | 0.21057 | 59.9854 | -0.21057 | 60.1685 | -0.027466 | 0.004578 | -0.036621 | 0.12817 | 0.045776 | 0.17395 | -0.050354 | 0.16937 | -0.054932 | 0.39368 | 123.175 | 0.041198 | 123.1064 | 123.1155 | 122.9416 | 122.9324 | 122.9462 | -123.1659 | -122.9782 | 122.9919 | 123.111 | 59.8663 | 59.9762
398.3281 | 123.2483 | -59.9991 | 63.002 | -0.014725 | 0.0015659 | 0.063141 | 0.079726 | -0.0026297 | 0.0013843 | -0.00056607 | -0.0028075 | -0.00076257 | 0.063215 | 0.064456 | -0.0036444 | 0.0025613 | 0.0015701 | -0.07782 | 62.9837 | -60.173 | 62.9379 | -59.8755 | -60.2325 | -0.013733 | -0.050354 | 62.9517 | -60.022 | 63.0844 | -59.9899 | -60.0861 | -59.8389 | -0.17395 | -0.01831 | -0.064087 | 0.1236 | 59.9854 | -0.23346 | 60.1593 | -0.059509 | -0.022889 | -0.050354 | 0.082398 | 0.009155 | 0.16022 | -0.086976 | 0.18311 | -0.064087 | 0.29755 | 123.111 | 0.032044 | 123.1064 | 123.1567 | 122.9736 | 122.9828 | 122.9507 | -123.175 | -123.024 | 122.937 | 123.0835 | 59.9213 | 59.9487
399.3281 | 123.2895 | -59.9899 | 62.9517 | -0.06813 | 0.0017795 | 0.066559 | 0.078658 | 0.0031381 | 0.0015979 | 0.00092933 | -0.0089111 | 0.00116 | 0.062147 | 0.064456 | -0.0051398 | 0.0051249 | 0.0024245 | -0.032043 | 62.9471 | -60.1685 | 63.0707 | -59.6512 | -60.2463 | -0.032043 | -0.054932 | 62.9242 | -60.022 | 63.1165 | -59.9579 | -60.0815 | -59.816 | -0.17853 | -0.004577 | 0.11902 | 0.33874 | 59.9579 | -0.25635 | 60.1364 | -0.07782 | -0.032044 | -0.027466 | 0.1648 | 0.032043 | 0.17395 | -0.091553 | 0.20599 | -0.059509 | 0.51727 | 123.2391 | 0.064087 | 123.1384 | 123.1155 | 122.9462 | 122.937 | 122.9141 | -123.1201 | -122.9736 | 123.0606 | 123.1064 | 59.9579 | 59.935
400.3281 | 123.2712 | -60.0082 | 62.9883 | -0.06813 | -0.00099768 | 0.06485 | 0.079513 | 0.00036107 | -0.0013929 | -0.0020615 | -0.0089111 | -0.00076257 | 0.064497 | 0.063388 | -0.0030036 | 0.00063867 | -0.0031297 | -0.082397 | 62.9974 | -60.1456 | 62.9562 | -59.8938 | -60.2554 | -0.018311 | -0.041199 | 62.9562 | -60.0082 | 63.0569 | -59.9991 | -60.054 | -59.8572 | -0.13733 | 0.009156 | -0.032043 | 0.11444 | 59.9899 | -0.24719 | 60.1273 | -0.10986 | 0 | -0.032043 | 0.068665 | 0.009156 | 0.15106 | -0.045776 | 0.15106 | -0.045776 | 0.25177 | 123.1018 | 0.009156 | 123.0652 | 123.143 | 122.9645 | 123.0057 | 122.9645 | -123.1338 | -122.9965 | 122.9645 | 123.0652 | 59.9258 | 59.967
401.3281 | 123.3032 | -59.9716 | 62.9471 | -0.098648 | 0.0011385 | 0.064209 | 0.07994 | 0.00057467 | 0.00010248 | -0.00013887 | -0.15234 | 0.0024416 | 0.062575 | 0.064029 | -0.0036444 | 0.0021341 | -0.0027023 | -0.032043 | 62.9425 | -60.1868 | 62.9929 | -59.8343 | -60.2097 | -0.036621 | 0.15564 | 62.915 | -60.022 | 63.1073 | -59.9487 | -60.0769 | -59.8068 | -0.21515 | -0.004578 | 0.045776 | 0.13733 | 59.935 | -0.23804 | 60.1501 | -0.022888 | -0.050354 | -0.032044 | 0.16022 | 0.022889 | 0.16479 | -0.10529 | 0.21515 | -0.054931 | 0.35248 | 123.1796 | 0.073243 | 123.1293 | 123.1293 | 122.937 | 122.9141 | 122.8867 | -123.1339 | -122.9691 | 122.9645 | 123.0789 | 59.9396 | 60.1273
402.3281 | 123.2437 | -59.9625 | 62.9608 | -0.098648 | 0.0028475 | 0.06549 | 0.078445 | -0.0026297 | -0.00096552 | 0.0017837 | -0.0058593 | 0.0013736 | 0.063002 | 0.06467 | -0.0036444 | 0.0019205 | 0.00050195 | -0.064087 | 62.9837 | -60.1364 | 63.0707 | -59.8297 | -60.3058 | -0.004578 | -0.068665 | 62.9425 | -60.0357 | 63.0478 | -60.0082 | -60.1089 | -59.8572 | -0.17395 | 0.022889 | 0.10986 | 0.13275 | 59.9579 | -0.34332 | 60.1318 | -0.16937 | -0.073243 | -0.01831 | 0.086976 | -0.045777 | 0.10529 | -0.14648 | 0.17853 | -0.073242 | 0.3067 | 123.2071 | 0.027466 | 123.0835 | 123.1201 | 122.9782 | 122.9462 | 122.905 | -123.0972 | -122.9965 | 123.0331 | 123.0103 | 59.8984 | 59.8938
403.3281 | 123.2666 | -59.967 | 62.97 | -0.06813 | -0.00035668 | 0.067199 | 0.079726 | -0.00027993 | -0.0020337 | -0.00056607 | -0.060791 | 0.00094643 | 0.064283 | 0.063388 | -0.0042854 | 0.00063867 | 7.4746e-05 | -0.041199 | 62.9379 | -60.173 | 62.9745 | -59.8434 | -60.2371 | -0.036621 | -0.032043 | 62.915 | -60.0494 | 63.1943 | -60.0311 | -60.0266 | -59.8022 | -0.20599 | -0.032044 | 0.004577 | 0.1236 | 59.9304 | -0.27008 | 60.1364 | -0.064087 | -0.082397 | -0.054932 | 0.2243 | -0.064087 | 0.1648 | -0.059509 | 0.24719 | 0.022888 | 0.32959 | 123.1476 | 0.01831 | 123.2437 | 123.111 | 122.9645 | 122.905 | 122.8821 | -123.143 | -123.0194 | 122.9416 | 123.1613 | 59.9258 | 59.935
404.3281 | 123.2849 | -59.9854 | 62.9745 | -0.1368 | 0.0037021 | 0.063141 | 0.081435 | -0.0017751 | -0.0016065 | -0.00013887 | -0.030273 | 0.00073263 | 0.063002 | 0.06467 | -0.0036444 | 0.0017069 | 0.0024245 | -0.064087 | 62.9562 | -60.1501 | 62.9562 | -59.8663 | -60.2554 | -0.041199 | -0.059509 | 62.9471 | -60.0311 | 63.0615 | -60.0311 | -60.1089 | -59.8572 | -0.16479 | -0.01831 | -0.01831 | 0.11902 | 59.9442 | -0.27008 | 60.1089 | -0.10529 | -0.045776 | -0.027465 | 0.086975 | -0.045776 | 0.12817 | -0.1236 | 0.17395 | -0.07782 | 0.28381 | 123.1064 | 0 | 123.0927 | 123.1064 | 122.9782 | 122.9416 | 122.9324 | -123.1247 | -123.0057 | 122.9416 | 123.0469 | 59.9213 | 59.9258
405.3281 | 123.2941 | -59.9899 | 62.97 | -0.10628 | 0.00092492 | 0.063354 | 0.080794 | 0.0031381 | 0.00074348 | -0.00035247 | -0.039429 | -0.00012177 | 0.063643 | 0.055912 | -0.0030036 | 0.0019205 | -0.00077965 | -0.032043 | 62.9608 | -60.173 | 62.9974 | -59.8206 | -60.228 | -0.022888 | -0.027466 | 62.9333 | -60.0403 | 63.1119 | -59.967 | -60.0677 | -59.8434 | -0.18311 | -0.009156 | 0.027466 | 0.16937 | 59.967 | -0.23804 | 60.1501 | -0.054931 | -0.050354 | -0.036621 | 0.14191 | 0.022888 | 0.14648 | -0.07782 | 0.19684 | -0.027466 | 0.35248 | 123.1705 | 0.073242 | 123.1522 | 123.1338 | 122.9736 | 122.9507 | 122.9233 | -123.143 | -123.0103 | 122.9874 | 123.1018 | 59.9579 | 59.9625
406.3281 | 123.2483 | -59.9762 | 62.9837 | -0.083389 | 0.0011385 | 0.063995 | 0.078872 | 0.00014747 | -0.0018201 | 0.0022109 | -0.021118 | 0.00094643 | 0.065138 | 0.055698 | -0.0074896 | 0.00021147 | 0.00071555 | -0.064087 | 62.97 | -60.1639 | 62.9471 | -59.8938 | -60.2371 | -0.032043 | -0.086975 | 62.9379 | -60.0266 | 63.1485 | -60.0906 | -60.0266 | -59.848 | -0.18768 | -0.013733 | -0.036621 | 0.082397 | 59.9442 | -0.26093 | 60.1318 | -0.073243 | -0.050354 | -0.045777 | 0.16479 | -0.11444 | 0.12817 | -0.050354 | 0.17853 | 0 | 0.27008 | 123.111 | -0.064087 | 123.175 | 123.1338 | 122.9645 | 122.9462 | 122.9141 | -123.1476 | -123.0103 | 122.9233 | 123.1247 | 59.9121 | 59.8892
407.3281 | 123.2712 | -59.9808 | 62.9471 | 0.023422 | 0.0011385 | 0.066559 | 0.080794 | 0.0035653 | -0.00032472 | -0.00077967 | -0.045532 | 0.00094643 | 0.063215 | 0.068088 | -0.0017218 | 0.0032023 | -0.0016343 | -0.022888 | 62.9517 | -60.1593 | 62.9974 | -59.8709 | -60.2097 | -0.027466 | -0.032043 | 62.9333 | -60.0357 | 63.0981 | -59.9808 | -60.0861 | -59.8343 | -0.17853 | 0.004577 | 0.050354 | 0.10986 | 59.9533 | -0.22888 | 60.1318 | -0.050354 | -0.054932 | -0.013733 | 0.15106 | 0 | 0.14648 | -0.10529 | 0.20142 | -0.050354 | 0.28839 | 123.1567 | 0.054932 | 123.1339 | 123.111 | 122.9691 | 122.9324 | 122.9141 | -123.1064 | -122.9828 | 122.9782 | 123.0789 | 59.9579 | 59.9487
408.3281 | 123.3032 | -59.9579 | 62.9608 | -0.083389 | 0.00071132 | 0.064422 | 0.080581 | 0.0037791 | 0.0013843 | -0.0029159 | -0.0089111 | 9.1834e-05 | 0.063002 | 0.060398 | -0.0057806 | -2.13e-06 | 7.4746e-05 | -0.009155 | 62.9929 | -60.1318 | 63.0249 | -59.7977 | -60.1685 | 0.07782 | 0.068665 | 62.9425 | -59.9991 | 63.1302 | -59.9396 | -60.0082 | -59.7885 | -0.17395 | 0.032044 | 0.064087 | 0.16022 | 60.0357 | -0.21057 | 60.2097 | -0.036621 | -0.041198 | -0.01831 | 0.16937 | 0.018311 | 0.16937 | -0.050354 | 0.21057 | -0.009156 | 0.33417 | 123.1567 | 0.059509 | 123.1293 | 123.1247 | 122.9416 | 122.9507 | 122.9004 | -123.0927 | -122.9599 | 122.9828 | 123.0881 | 59.9487 | 60.0266
409.3281 | 123.2941 | -59.9808 | 62.9654 | -0.10628 | 0.00092492 | 0.065704 | 0.081222 | -0.0013479 | -0.0033155 | 0.00028833 | -0.072998 | 0.00073263 | 0.063215 | 0.070652 | -0.0053534 | 0.0038431 | -0.0031297 | -0.082397 | 62.9517 | -60.2005 | 62.9608 | -59.8938 | -60.2325 | -0.032043 | -0.064087 | 62.9471 | -60.0311 | 63.1165 | -59.967 | -60.0906 | -59.8068 | -0.21973 | -0.013733 | -0.004578 | 0.086975 | 59.9487 | -0.25177 | 60.1685 | -0.032044 | -0.050354 | -0.01831 | 0.15106 | 0.013733 | 0.17395 | -0.10986 | 0.2243 | -0.059509 | 0.3067 | 123.1613 | 0.064087 | 123.1476 | 123.1522 | 122.9782 | 122.9324 | 122.9279 | -123.1659 | -122.9965 | 122.9416 | 123.0972 | 59.8984 | 59.9167
410.3281 | 123.262 | -59.9899 | 63.0066 | -0.10628 | 0.0022067 | 0.065277 | 0.077376 | -0.0013479 | 0.00052988 | 0.00050193 | -0.0028075 | 0.002228 | 0.064497 | 0.063175 | -0.004499 | 0.0019205 | 0.0015701 | -0.050354 | 62.9974 | -60.1685 | 62.9425 | -59.8709 | -60.2417 | 0.004578 | -0.032043 | 62.97 | -60.0311 | 63.0707 | -59.967 | -60.0723 | -59.8114 | -0.17853 | -0.009155 | -0.064087 | 0.11902 | 59.9945 | -0.25177 | 60.173 | -0.073242 | -0.041199 | -0.036621 | 0.064087 | 0.022888 | 0.17853 | -0.082398 | 0.21973 | -0.041199 | 0.29755 | 123.111 | 0.064087 | 123.1018 | 123.1659 | 123.0011 | 122.9874 | 122.9599 | -123.175 | -123.0377 | 122.9324 | 123.0606 | 59.9396 | 59.9579
411.3281 | 123.2758 | -60.0128 | 62.9745 | -0.098648 | 0.0015659 | 0.064209 | 0.07994 | 0.00036107 | -0.0011791 | 7.4734e-05 | -0.027222 | -0.00054897 | 0.061293 | 0.062747 | -0.0051398 | 0.0029887 | -0.00077965 | -0.054932 | 62.9654 | -60.1639 | 62.97 | -59.8343 | -60.2234 | -0.032043 | -0.027466 | 62.9333 | -60.0403 | 63.0798 | -59.9991 | -60.0815 | -59.8389 | -0.15106 | -0.009155 | -0.004577 | 0.17853 | 59.9808 | -0.21057 | 60.1318 | -0.05951 | -0.027466 | -0.041198 | 0.10529 | 0.013733 | 0.17395 | -0.068665 | 0.20142 | -0.041199 | 0.32959 | 123.1338 | 0.041199 | 123.1201 | 123.1293 | 122.9736 | 122.9782 | 122.9462 | -123.1384 | -123.0148 | 122.9828 | 123.0927 | 59.9579 | 59.9854
412.3281 | 123.23 | -59.9854 | 62.9654 | 0.04631 | 0.0022067 | 0.062713 | 0.081649 | -0.00049353 | -0.0024609 | -0.0035569 | -0.033325 | -0.00097617 | 0.063856 | 0.069156 | -0.00279 | 0.0012797 | 0.0015701 | -0.09613 | 63.0066 | -60.1868 | 62.9517 | -59.8984 | -60.228 | -0.022888 | -0.059509 | 62.9517 | -60.0266 | 63.0615 | -59.9945 | -60.0815 | -59.8572 | -0.20142 | 0.041199 | -0.013733 | 0.086976 | 59.9625 | -0.24261 | 60.1639 | -0.041198 | -0.041198 | -0.013733 | 0.09613 | -0.009155 | 0.12817 | -0.09613 | 0.16937 | -0.054932 | 0.28839 | 123.1384 | 0.032043 | 123.0881 | 123.1934 | 122.9782 | 122.9919 | 122.937 | -123.1522 | -122.9919 | 122.937 | 123.0469 | 59.8892 | 59.9258
413.3281 | 123.2574 | -59.9716 | 62.9562 | -0.1368 | 0.0017795 | 0.065063 | 0.080367 | 0.00014747 | 0.00052988 | -0.0012071 | -0.069946 | -0.00033537 | 0.063215 | 0.067447 | -0.0034308 | 0.00063867 | 0.0022109 | -0.041199 | 62.9425 | -60.1547 | 62.9883 | -59.8343 | -60.2234 | -0.018311 | -0.032043 | 62.9288 | -60.0266 | 63.0753 | -60.0082 | -60.0952 | -59.8389 | -0.18311 | -0.013733 | 0.032043 | 0.13733 | 59.9533 | -0.25177 | 60.1364 | -0.068665 | -0.054931 | -0.027466 | 0.11902 | -0.036621 | 0.13275 | -0.1236 | 0.18768 | -0.068665 | 0.32043 | 123.143 | 0.01831 | 123.1018 | 123.0972 | 122.9553 | 122.9141 | 122.9004 | -123.111 | -122.9828 | 122.9599 | 123.0469 | 59.9304 | 59.9396
414.3281 | 123.2529 | -59.9716 | 62.9883 | -0.052872 | 0.0013523 | 0.063141 | 0.07994 | 0.0016427 | 0.00010248 | -0.00099327 | -0.0089111 | 0.0018008 | 0.063643 | 0.066593 | -0.0025764 | 0.0021341 | 0.00050195 | -0.086975 | 62.9929 | -60.1273 | 62.9654 | -59.8938 | -60.2509 | -0.036621 | -0.045776 | 62.9517 | -60.0266 | 63.0661 | -60.0037 | -60.0632 | -59.848 | -0.15564 | 0.004578 | -0.022888 | 0.07782 | 59.935 | -0.27923 | 60.0906 | -0.1236 | -0.054931 | -0.036621 | 0.07782 | -0.032043 | 0.1236 | -0.091552 | 0.17853 | -0.036621 | 0.23346 | 123.0927 | 0.022888 | 123.0927 | 123.1201 | 122.9782 | 122.9645 | 122.9233 | -123.1155 | -123.0148 | 122.937 | 123.0377 | 59.8846 | 59.9258
415.3281 | 123.2574 | -59.9945 | 62.9471 | -0.10628 | 0.0022067 | 0.065063 | 0.078658 | 0.0022837 | -0.0031017 | -0.0012071 | -0.027222 | 0.00051903 | 0.063215 | 0.063175 | -0.004499 | 0.0021341 | -0.0016343 | -0.054932 | 62.9471 | -60.1685 | 62.9974 | -59.816 | -60.2234 | -0.018311 | -0.027466 | 62.9562 | -60.0357 | 63.1027 | -59.9991 | -60.0769 | -59.8251 | -0.17395 | 0 | 0.050354 | 0.17853 | 59.9762 | -0.22888 | 60.1501 | -0.054932 | -0.041199 | 0.009155 | 0.15564 | -0.004577 | 0.16937 | -0.082397 | 0.21057 | -0.041198 | 0.35248 | 123.1659 | 0.036622 | 123.1384 | 123.1155 | 122.9919 | 122.9416 | 122.9507 | -123.1155 | -122.9828 | 122.9919 | 123.0972 | 59.9396 | 59.967
416.3281 | 123.3398 | -59.967 | 63.0295 | -0.037613 | -0.00078408 | 0.064422 | 0.080794 | 0.0022837 | 0.0011707 | -0.0031297 | 0.00024405 | 9.1834e-05 | 0.062147 | 0.058689 | -0.0032172 | 0.0029887 | -0.0033433 | 0.009155 | 62.9837 | -60.1227 | 63.0386 | -59.7748 | -60.1318 | 0.091553 | 0.14191 | 62.9791 | -59.9716 | 63.1485 | -59.8618 | -59.9899 | -59.7748 | -0.15564 | -0.045776 | 0.009155 | 0.19226 | 60.0586 | -0.16479 | 60.2142 | -0.009155 | -0.004578 | -0.050354 | 0.11902 | 0.10529 | 0.19226 | -0.022888 | 0.19684 | -0.01831 | 0.3479 | 123.1613 | 0.10986 | 123.1201 | 123.1064 | 122.9507 | 122.9507 | 122.9462 | -123.1522 | -123.0011 | 123.0057 | 123.1155 | 59.9762 | 60.1089
417.3281 | 123.2391 | -59.9945 | 62.9654 | -0.1368 | 0.0026339 | 0.063995 | 0.080154 | 0.0037791 | -0.00096552 | -0.0037705 | -0.051636 | -0.0014036 | 0.064283 | 0.06232 | -0.0034308 | 0.00085247 | 7.4746e-05 | -0.050354 | 62.915 | -60.173 | 62.9974 | -59.816 | -60.2234 | -0.036621 | -0.032043 | 62.9379 | -60.0266 | 63.0798 | -59.9899 | -60.0815 | -59.8343 | -0.17853 | -0.050354 | 0.032044 | 0.17853 | 59.9579 | -0.22888 | 60.1364 | -0.050354 | -0.032043 | -0.027466 | 0.11444 | 0.004578 | 0.16022 | -0.086975 | 0.19226 | -0.054932 | 0.35706 | 123.1705 | 0.036621 | 123.1064 | 123.0881 | 122.9645 | 122.9095 | 122.9324 | -123.1384 | -122.9919 | 122.9919 | 123.0743 | 59.9442 | 59.9625
418.3281 | 123.2666 | -59.9625 | 62.9883 | 0.10735 | 0.00071132 | 0.065277 | 0.080581 | -0.00027993 | -0.0037427 | 0.00050193 | -0.027222 | -0.0014036 | 0.065138 | 0.061893 | -0.0032172 | 0.00063867 | -0.0041977 | -0.16937 | 62.9745 | -60.141 | 63.002 | -59.7977 | -60.0906 | 0.09613 | 0.1236 | 62.97 | -59.9991 | 63.1302 | -59.903 | -60.0128 | -59.7885 | -0.17853 | -0.013733 | 0.013733 | 0.16479 | 60.0586 | -0.12817 | 60.2371 | 0.050354 | -0.036621 | -0.01831 | 0.14191 | 0.059509 | 0.17395 | -0.050354 | 0.21057 | -0.013733 | 0.34332 | 123.143 | 0.09613 | 123.1293 | 123.1155 | 122.9691 | 122.937 | 122.9324 | -123.1293 | -122.9874 | 122.9645 | 123.0927 | 59.7931 | 60.0861
419.3281 | 123.2391 | -59.9716 | 62.9837 | -0.06813 | 0.0013523 | 0.062072 | 0.078872 | -0.0011343 | -0.0033155 | -0.0018479 | -0.057739 | 0.00073263 | 0.065352 | 0.064029 | -0.0042854 | 0.0012797 | 0.00092935 | -0.064087 | 62.9608 | -60.141 | 62.9562 | -59.8892 | -60.2417 | -0.045776 | -0.07782 | 62.9608 | -60.0311 | 63.0707 | -60.0082 | -60.0815 | -59.848 | -0.16937 | -0.022889 | -0.027466 | 0.082398 | 59.9258 | -0.27008 | 60.0952 | -0.10071 | -0.059509 | -0.022889 | 0.086975 | -0.036621 | 0.1236 | -0.10986 | 0.18311 | -0.050354 | 0.25177 | 123.0972 | 0.022888 | 123.1018 | 123.1018 | 122.9919 | 122.9324 | 122.9324 | -123.1247 | -123.0148 | 122.9279 | 123.0423 | 59.9075 | 59.8938
420.3281 | 123.317 | -59.9533 | 62.9745 | -0.083389 | -0.00035668 | 0.063995 | 0.08229 | -0.0022025 | -0.00032472 | -0.0016343 | -0.0089111 | 0.00073263 | 0.063429 | 0.062534 | -0.0036444 | 0.0027751 | -0.0050523 | 0.022888 | 62.9654 | -60.1501 | 63.0524 | -59.7473 | -60.1181 | 0.091553 | 0.14648 | 62.9562 | -59.9945 | 63.1622 | -59.8938 | -59.9808 | -59.7656 | -0.19684 | -0.009155 | 0.07782 | 0.20599 | 60.0449 | -0.16479 | 60.2417 | 0.032043 | -0.041199 | -0.01831 | 0.18768 | 0.059509 | 0.18768 | -0.027466 | 0.22888 | 0.013733 | 0.40283 | 123.2025 | 0.10071 | 123.1567 | 123.1155 | 122.9507 | 122.9187 | 122.9095 | -123.1247 | -122.9691 | 123.0057 | 123.1155 | 59.9762 | 60.0998
421.3281 | 123.2346 | -59.9716 | 62.9883 | -0.083389 | -0.00014308 | 0.063781 | 0.081222 | 0.0014291 | -0.0013929 | 0.00071573 | -0.021118 | 0.00030543 | 0.063643 | 0.061466 | -0.0047126 | 0.0025613 | -0.0022751 | -0.059509 | 62.9654 | -60.1822 | 62.9562 | -59.8846 | -60.2371 | -0.050354 | -0.054932 | 62.9471 | -60.0266 | 63.0707 | -59.9991 | -60.0952 | -59.8572 | -0.21057 | -0.022888 | -0.032043 | 0.086975 | 59.9213 | -0.2655 | 60.1318 | -0.054932 | -0.054931 | -0.041198 | 0.082398 | -0.027465 | 0.11444 | -0.1236 | 0.16937 | -0.068665 | 0.29755 | 123.1384 | 0.027466 | 123.0972 | 123.1476 | 122.9736 | 122.937 | 122.9187 | -123.1705 | -123.0148 | 122.9279 | 123.0423 | 59.9121 | 59.9167
422.3281 | 123.262 | -59.9487 | 62.9974 | -0.06813 | 0.00071132 | 0.063354 | 0.078017 | -0.00049353 | 0.00074348 | -0.0039841 | -0.021118 | -0.00012177 | 0.061293 | 0.065738 | -0.002149 | -2.13e-06 | -0.0020615 | 0.004578 | 62.9837 | -60.1227 | 63.0432 | -59.7565 | -60.1318 | 0.11444 | 0.13733 | 62.9745 | -59.9716 | 63.1485 | -59.9075 | -59.9716 | -59.7794 | -0.17395 | -0.013733 | 0.045776 | 0.19226 | 60.0632 | -0.18311 | 60.2371 | -0.009155 | -0.022889 | -0.022889 | 0.15106 | 0.041198 | 0.16937 | -0.022889 | 0.19226 | 0 | 0.36621 | 123.1659 | 0.064087 | 123.1201 | 123.1064 | 122.9462 | 122.9324 | 122.9233 | -123.1201 | -122.9691 | 122.9919 | 123.0972 | 59.9533 | 60.0861
423.3281 | 123.2712 | -59.9762 | 62.9471 | -0.060501 | 0.0019931 | 0.064636 | 0.080581 | 0.00057467 | -0.0022473 | -0.00099327 | -0.060791 | 0.00116 | 0.06172 | 0.061466 | -0.0042854 | 0.0019205 | -0.00099325 | -0.036621 | 62.9562 | -60.1593 | 63.0066 | -59.8251 | -60.2463 | -0.022888 | -0.027466 | 62.9517 | -60.0266 | 63.089 | -59.9991 | -60.0861 | -59.8434 | -0.18311 | 0.009155 | 0.059509 | 0.15106 | 59.9533 | -0.27008 | 60.1364 | -0.086975 | -0.050354 | 0.004577 | 0.14191 | -0.022888 | 0.13275 | -0.10986 | 0.1831 | -0.05951 | 0.33417 | 123.1659 | 0.027466 | 123.1155 | 123.1155 | 122.9782 | 122.9324 | 122.9279 | -123.1064 | -122.9736 | 122.9828 | 123.0652 | 59.9396 | 59.9487
424.3281 | 123.3124 | -59.9762 | 62.9929 | -0.11391 | 0.0032749 | 0.062072 | 0.079726 | -0.00027993 | -0.00032472 | -0.0012071 | -0.0028075 | 0.0015872 | 0.066847 | 0.063602 | -0.0051398 | 0.0023477 | -0.0035569 | 0.013733 | 62.9929 | -60.1318 | 63.0615 | -59.761 | -60.1318 | 0.09613 | 0.14191 | 62.9471 | -59.9945 | 63.1531 | -59.8846 | -59.9991 | -59.7702 | -0.15564 | 0 | 0.068664 | 0.21515 | 60.0723 | -0.15564 | 60.228 | 0 | -0.018311 | -0.045776 | 0.16022 | 0.091552 | 0.20599 | -0.022888 | 0.2243 | -0.004577 | 0.37079 | 123.1934 | 0.10986 | 123.1476 | 123.1247 | 122.9416 | 122.9691 | 122.9233 | -123.1247 | -122.9874 | 123.0377 | 123.1293 | 59.9899 | 60.1181
425.3281 | 123.262 | -59.9762 | 63.002 | -0.06813 | 0.00092492 | 0.062072 | 0.080154 | 0.00014747 | 0.00052988 | -0.00056607 | -0.0028075 | -0.00076257 | 0.065138 | 0.064029 | -0.004499 | 0.0014933 | 7.4746e-05 | -0.064087 | 62.9791 | -60.1913 | 62.883 | -59.8526 | -60.2051 | -0.036621 | -0.064087 | 62.9654 | -60.0082 | 63.0753 | -59.9808 | -60.0952 | -59.8343 | -0.21515 | -0.022888 | -0.11902 | 0.1236 | 59.9396 | -0.22888 | 60.1547 | -0.013733 | -0.032044 | -0.036621 | 0.073242 | -0.004578 | 0.14191 | -0.11902 | 0.17395 | -0.086975 | 0.33874 | 123.0743 | 0.027466 | 123.0835 | 123.1705 | 122.9736 | 122.9553 | 122.9416 | -123.1934 | -123.0103 | 122.8592 | 123.0515 | 59.9121 | 59.9121
426.3438 | 123.1567 | -59.9945 | 63.0157 | -0.045242 | 0.0013523 | 0.063995 | 0.084426 | 0.0024973 | -0.00053832 | 0.00028833 | -0.10962 | 0.002228 | 0.06407 | 0.069797 | -0.0047126 | 0.0034159 | 0.0013565 | -0.004578 | 62.9745 | -60.1776 | 62.9608 | -59.8892 | -60.2509 | -0.027466 | -0.018311 | 62.9974 | -60.0403 | 63.0432 | -60.0677 | -60.173 | -59.8938 | -0.18311 | -0.041199 | -0.054932 | 0.10529 | 59.967 | -0.25635 | 60.1501 | -0.073242 | -0.045776 | -0.01831 | 0.027466 | -0.073242 | 0.10071 | -0.17853 | 0.14648 | -0.13275 | 0.28839 | 123.1384 | -0.027466 | 123.0835 | 123.1522 | 123.0377 | 122.9691 | 122.9919 | -123.1934 | -123.056 | 122.9553 | 123.0377 | 59.9899 | 59.9762
427.3281 | 123.2391 | -59.9945 | 62.9745 | -0.060501 | -0.0012113 | 0.064209 | 0.080154 | 0.0010019 | -0.00032472 | -0.0012071 | -0.027222 | 0.0013736 | 0.061293 | 0.060825 | -0.0030036 | -0.0012839 | 0.0028519 | -0.07782 | 62.9745 | -60.1593 | 63.0569 | -59.9075 | -60.2142 | -0.009155 | -0.064087 | 62.97 | -60.0311 | 63.0478 | -59.9854 | -60.1089 | -59.8526 | -0.16479 | 0 | 0.082398 | 0.086975 | 59.9854 | -0.21973 | 60.1501 | -0.054931 | -0.036621 | -0.004577 | 0.073243 | 0.009155 | 0.14191 | -0.11444 | 0.17853 | -0.07782 | 0.25177 | 123.2162 | 0.045776 | 123.0789 | 123.1338 | 123.0011 | 122.9691 | 122.9645 | -123.1338 | -123.0057 | 123.0515 | 123.0423 | 59.9167 | 59.9304
428.3281 | 123.2208 | -59.9716 | 63.0386 | -0.045242 | 0.00028412 | 0.063781 | 0.080581 | 0.0014291 | -0.00011112 | -0.0018479 | -0.027222 | -0.00076257 | 0.063429 | 0.063388 | -0.0040716 | 0.0027751 | -0.0024887 | 0.027466 | 63.0112 | -60.1547 | 63.0341 | -59.8068 | -60.173 | 0.09613 | 0.10986 | 62.9974 | -60.0174 | 63.089 | -59.9625 | -60.0632 | -59.848 | -0.18311 | -0.027466 | -0.004577 | 0.16479 | 60.0677 | -0.20142 | 60.2509 | -0.018311 | -0.045776 | -0.041198 | 0.050354 | 0.009156 | 0.1236 | -0.091552 | 0.16937 | -0.045776 | 0.3479 | 123.1888 | 0.054932 | 123.1064 | 123.1659 | 123.0148 | 122.9828 | 122.9691 | -123.1934 | -123.056 | 123.0057 | 123.0606 | 59.9991 | 60.0815
429.3281 | 123.262 | -60.0082 | 62.9791 | -0.06813 | 0.0013523 | 0.063995 | 0.078017 | -6.6126e-05 | 0.0011707 | -0.0016343 | 0.0093995 | 0.00094643 | 0.064497 | 0.058689 | -0.0047126 | 0.0017069 | -0.0012071 | -0.059509 | 62.9837 | -60.1593 | 62.9471 | -59.8709 | -60.2463 | -0.009155 | -0.059509 | 62.9608 | -60.0128 | 63.0661 | -60.0082 | -60.0449 | -59.8389 | -0.15106 | 0.004578 | -0.032043 | 0.13733 | 59.9991 | -0.23804 | 60.1501 | -0.086975 | -0.004577 | -0.018311 | 0.086975 | 0 | 0.16937 | -0.036621 | 0.17395 | -0.032044 | 0.28839 | 123.1064 | 0.004577 | 123.0789 | 123.143 | 122.9736 | 122.9919 | 122.9691 | -123.1384 | -122.9919 | 122.9553 | 123.0743 | 59.9487 | 59.9487
430.3281 | 123.3215 | -59.9487 | 63.0112 | -0.091019 | 0.0015659 | 0.064636 | 0.078658 | -6.6126e-05 | -0.0026745 | -0.00099327 | -0.011963 | -0.00054897 | 0.062575 | 0.06467 | -0.0057806 | 0.0023477 | -0.00099325 | 0.009155 | 62.9974 | -60.1456 | 63.0295 | -59.7702 | -60.1456 | 0.07782 | 0.13275 | 62.9517 | -60.0037 | 63.1577 | -59.8846 | -59.9808 | -59.7656 | -0.19684 | -0.013732 | 0.018311 | 0.17853 | 60.0266 | -0.19684 | 60.2234 | 0 | -0.054932 | -0.059509 | 0.14648 | 0.064086 | 0.1831 | -0.032044 | 0.23804 | 0.022888 | 0.37537 | 123.175 | 0.11902 | 123.1613 | 123.143 | 122.9553 | 122.9462 | 122.9004 | -123.1567 | -123.0148 | 122.9782 | 123.1064 | 59.9579 | 60.0815
431.3438 | 123.1705 | -59.9808 | 63.0295 | 0.0081632 | -0.0012113 | 0.061432 | 0.081008 | 0.0016427 | -0.0022473 | -0.0035569 | -0.063843 | 0.002228 | 0.062361 | 0.060611 | -0.0042854 | 0.0025613 | -0.0016343 | 0 | 63.0707 | -60.1456 | 62.8693 | -59.9258 | -60.228 | 0 | 0 | 63.0203 | -60.0128 | 63.0341 | -60.0357 | -60.1456 | -59.8801 | -0.1648 | 0.041199 | -0.16022 | 0.054932 | 59.9808 | -0.24719 | 60.1456 | -0.082397 | -0.032043 | -0.009155 | 0.004578 | -0.054932 | 0.10071 | -0.1648 | 0.13275 | -0.13275 | 0.21973 | 123.0148 | -0.022889 | 123.0469 | 123.2162 | 123.0331 | 123.0515 | 123.0011 | -123.175 | -123.0423 | 122.85 | 123.0148 | 59.9808 | 59.9808
432.3281 | 123.2895 | -59.9808 | 63.0066 | -0.098648 | 0.0011385 | 0.063568 | 0.080367 | 0.0029245 | -0.00032472 | 0.00050193 | -0.045532 | -0.00076257 | 0.062788 | 0.058261 | -0.0034308 | 0.0014933 | 7.4746e-05 | 0.059509 | 63.0066 | -60.1181 | 63.0386 | -59.7473 | -60.1135 | 0.082397 | 0.30212 | 63.0203 | -59.9899 | 63.1668 | -59.9396 | -59.9762 | -59.7656 | -0.13733 | 0 | 0.032043 | 0.23346 | 60.0632 | -0.13275 | 60.2005 | 0.004578 | -0.009155 | 0.013733 | 0.16022 | 0.041199 | 0.21515 | 0.004578 | 0.2243 | 0.013733 | 0.37079 | 123.1567 | 0.050354 | 123.1567 | 123.1247 | 123.0103 | 122.9874 | 123.0011 | -123.1247 | -122.9965 | 123.0194 | 123.1476 | 60.0403 | 60.2829
433.3281 | 123.2391 | -59.967 | 63.0112 | -0.06813 | 0.0017795 | 0.063568 | 0.081008 | -0.0011343 | 0.00074348 | 0.0015701 | -0.018066 | -0.00097617 | 0.063856 | 0.061252 | -0.0040716 | 0.0019205 | -0.0018479 | -0.054932 | 62.9929 | -60.1685 | 62.97 | -59.8755 | -60.2463 | 0.004578 | -0.027466 | 62.9471 | -60.022 | 63.0936 | -59.9808 | -60.0449 | -59.8251 | -0.20142 | -0.01831 | -0.041198 | 0.091553 | 59.9716 | -0.27924 | 60.173 | -0.07782 | -0.054932 | -0.064086 | 0.082398 | -0.013733 | 0.14191 | -0.07782 | 0.19684 | -0.022888 | 0.29297 | 123.1384 | 0.041199 | 123.1155 | 123.1613 | 122.9691 | 122.9599 | 122.9141 | -123.1796 | -123.0331 | 122.937 | 123.0606 | 59.9121 | 59.9396
434.3281 | 123.2025 | -60.0037 | 63.0249 | -0.07576 | -0.0012113 | 0.064209 | 0.080367 | 0.0018565 | 0.00031608 | 0.00050193 | -0.039429 | 0.00051903 | 0.065352 | 0.062107 | -0.0025764 | 0.0012797 | 0.00071555 | 0.022888 | 63.0203 | -60.1547 | 62.9883 | -59.848 | -60.1868 | 0.064087 | 0.036621 | 63.0341 | -60.0266 | 63.0432 | -60.0266 | -60.1044 | -59.8801 | -0.15106 | -0.004577 | -0.036621 | 0.15564 | 60.0677 | -0.18311 | 60.2188 | -0.032044 | -0.022888 | 0.009156 | 0.018311 | -0.022888 | 0.1236 | -0.10071 | 0.14648 | -0.07782 | 0.3067 | 123.143 | 0 | 123.0698 | 123.175 | 123.0606 | 123.024 | 123.0377 | -123.1796 | -123.0515 | 122.9919 | 123.0469 | 60.0266 | 60.0403
435.3281 | 123.2758 | -59.9808 | 62.9974 | -0.12917 | 0.0011385 | 0.063995 | 0.080367 | -0.0024161 | -0.00032472 | -0.0014207 | -0.021118 | 0.0018008 | 0.063856 | 0.057621 | -0.0036444 | 0.00063867 | 0.00050195 | -0.022888 | 63.0066 | -60.1364 | 62.9517 | -59.8846 | -60.2097 | -0.009155 | -0.045776 | 62.9791 | -60.0403 | 63.0798 | -59.967 | -60.0723 | -59.8434 | -0.15564 | 0.009155 | -0.045777 | 0.09613 | 59.9716 | -0.22888 | 60.1273 | -0.073242 | -0.059509 | -0.018311 | 0.082397 | 0.013733 | 0.13733 | -0.091553 | 0.19684 | -0.032044 | 0.25177 | 123.0881 | 0.073242 | 123.1201 | 123.143 | 123.0194 | 122.9874 | 122.9599 | -123.1339 | -123.0377 | 122.9324 | 123.0606 | 59.9579 | 59.935
436.3281 | 123.2346 | -59.9716 | 63.0386 | -0.045242 | 0.00071132 | 0.062072 | 0.08229 | -0.0026297 | 0.00010248 | -0.0016343 | -0.060791 | 0.00073263 | 0.06407 | 0.064456 | -0.0032172 | 0.0036295 | -0.00056605 | -0.004578 | 63.0341 | -60.1685 | 62.9654 | -59.8938 | -60.2234 | -0.004578 | 0.013733 | 63.0112 | -60.0128 | 63.0569 | -60.0037 | -60.1089 | -59.8801 | -0.19684 | -0.004577 | -0.073242 | 0.07782 | 59.967 | -0.25177 | 60.1639 | -0.054932 | -0.041198 | -0.027466 | 0.018311 | -0.032043 | 0.091553 | -0.13733 | 0.13275 | -0.096131 | 0.27466 | 123.1338 | 0.009155 | 123.0698 | 123.2025 | 123.024 | 123.0057 | 122.9828 | -123.2071 | -123.0515 | 122.937 | 123.0286 | 59.967 | 59.9854
437.3281 | 123.2574 | -59.9854 | 62.9791 | -0.091019 | 0.0013523 | 0.065277 | 0.080367 | -0.0022025 | 0.00031608 | -0.0024887 | -0.021118 | -0.00097617 | 0.066847 | 0.068088 | -0.004499 | 0.0025613 | 0.00028835 | -0.07782 | 62.9837 | -60.1456 | 62.9517 | -59.8801 | -60.228 | -0.045776 | -0.068665 | 62.9517 | -60.054 | 63.0753 | -60.0037 | -60.0861 | -59.8343 | -0.16022 | 0.004578 | -0.027466 | 0.10529 | 59.9396 | -0.24261 | 60.0998 | -0.082397 | -0.068664 | -0.027466 | 0.09613 | -0.01831 | 0.15106 | -0.10071 | 0.21973 | -0.032044 | 0.2655 | 123.0972 | 0.050354 | 123.1293 | 123.1293 | 123.0057 | 122.9691 | 122.937 | -123.1247 | -123.0331 | 122.937 | 123.0606 | 59.9075 | 59.9167
438.3281 | 123.2254 | -59.9487 | 63.0157 | -0.06813 | 0.0028475 | 0.065277 | 0.079513 | -0.0015615 | 0.00031608 | -0.0018479 | -0.018066 | -0.00012177 | 0.064283 | 0.062107 | -0.0032172 | 0.0014933 | -0.0031297 | 0.022888 | 62.9974 | -60.1273 | 63.0249 | -59.7977 | -60.1547 | 0.082397 | 0.07782 | 62.9974 | -59.9716 | 63.0753 | -59.9762 | -60.0723 | -59.8389 | -0.17853 | -0.01831 | 0.009155 | 0.15106 | 60.0311 | -0.20599 | 60.2097 | -0.027466 | -0.022889 | -0.01831 | 0.059509 | -0.027466 | 0.10986 | -0.1236 | 0.13275 | -0.10071 | 0.32959 | 123.1522 | -0.004577 | 123.0469 | 123.1247 | 122.9691 | 122.9462 | 122.9462 | -123.143 | -122.9874 | 122.9736 | 123.024 | 59.9716 | 60.0266
439.3281 | 123.2758 | -59.9625 | 63.002 | -0.06813 | 0.0015659 | 0.061645 | 0.07994 | -0.0022025 | -0.00096552 | -0.0027023 | -0.0028075 | -0.00012177 | 0.063429 | 0.056339 | -0.0049262 | 0.0025613 | 0.0013565 | -0.041199 | 63.0112 | -60.1547 | 62.97 | -59.8389 | -60.1868 | 0.022888 | 0.009155 | 62.9745 | -59.9808 | 63.1165 | -59.9258 | -60.0357 | -59.7977 | -0.19226 | 0.009155 | -0.032043 | 0.1236 | 59.9854 | -0.22431 | 60.1776 | -0.032044 | -0.018311 | -0.027466 | 0.11444 | 0.036621 | 0.16479 | -0.073243 | 0.18311 | -0.054932 | 0.31586 | 123.1247 | 0.054932 | 123.0972 | 123.1659 | 122.9553 | 122.9736 | 122.937 | -123.1567 | -122.9828 | 122.9324 | 123.0789 | 59.9213 | 59.9716
440.3281 | 123.2986 | -59.9487 | 63.002 | -0.091019 | 7.0518e-05 | 0.064422 | 0.081008 | -0.0015615 | -0.0011791 | 0.00050193 | 0.0093995 | 0.0032962 | 0.065138 | 0.064884 | -0.0053534 | 0.0019205 | 0.0011429 | 0.013733 | 62.9929 | -60.1273 | 62.9745 | -59.4086 | -60.0037 | -0.10986 | 0.07782 | 62.9745 | -59.9899 | 63.1393 | -59.9167 | -60.0082 | -59.7794 | -0.17853 | -0.009155 | -0.027466 | 0.54016 | 59.8389 | -0.054932 | 60.0174 | 0.1236 | -0.041199 | -0.027466 | 0.13733 | 0.032043 | 0.16937 | -0.05951 | 0.21057 | -0.018311 | 0.71869 | 123.1018 | 0.073242 | 123.1293 | 123.1201 | 122.9645 | 122.9416 | 122.9233 | -123.1293 | -122.9919 | 122.9233 | 123.0881 | 59.9625 | 60.0266
441.3438 | 123.2071 | -59.9808 | 63.0386 | -0.052872 | 0.0028475 | 0.062713 | 0.084426 | 0.0014291 | -0.0022473 | -0.0012071 | -0.091309 | 0.0015872 | 0.064497 | 0.062107 | -0.0049262 | 0.0014933 | -0.0031297 | 0.004578 | 63.0386 | -60.1547 | 62.9608 | -59.8663 | -60.2142 | 0 | 0.032043 | 63.0157 | -60.022 | 63.0707 | -59.9808 | -60.0998 | -59.8389 | -0.17395 | 0 | -0.07782 | 0.11444 | 59.9808 | -0.23346 | 60.1547 | -0.059509 | -0.041199 | -0.022888 | 0.032044 | 0 | 0.14191 | -0.11902 | 0.18311 | -0.077819 | 0.28839 | 123.1155 | 0.041199 | 123.0927 | 123.1934 | 123.0377 | 123.0194 | 122.9965 | -123.1934 | -123.0606 | 122.9416 | 123.0515 | 59.9854 | 60.0128
442.3281 | 123.317 | -59.9533 | 63.0066 | -0.045242 | 0.00092492 | 0.062072 | 0.078445 | -0.00070713 | -0.0016065 | 0.00092933 | 0.018555 | 0.00051903 | 0.064283 | 0.05698 | -0.002149 | 0.0040567 | 0.0041335 | 0.027466 | 63.0112 | -60.0998 | 63.0661 | -59.7336 | -60.0998 | 0.086975 | 0.1236 | 62.9791 | -59.9854 | 63.0157 | -59.7931 | -60.1044 | -59.8618 | -0.14648 | 0.004577 | 0.059509 | 0.21973 | 60.0403 | -0.14648 | 60.1868 | 0 | -0.032044 | -0.027466 | 0.009155 | 0.16022 | 0.091553 | -0.15106 | 0.1236 | -0.11902 | 0.36621 | 123.1659 | 0.19226 | 123.0011 | 123.111 | 122.9645 | 122.9645 | 122.9324 | -123.1064 | -122.9919 | 123.0194 | 122.9691 | 59.9808 | 60.0769
443.3281 | 123.2437 | -59.9625 | 63.0157 | -0.07576 | 0.00071132 | 0.063141 | 0.080794 | 0.0059153 | -0.00075192 | -0.0022751 | 0.00024405 | 0.0013736 | 0.063856 | 0.060611 | -0.00279 | -2.13e-06 | -0.00013885 | -0.086975 | 62.97 | -60.1593 | 62.9608 | -59.8663 | -60.2417 | -0.036621 | -0.09613 | 62.9333 | -60.0494 | 63.0661 | -60.0037 | -60.0815 | -59.8343 | -0.19684 | -0.045776 | -0.054932 | 0.09613 | 59.9258 | -0.27924 | 60.1227 | -0.082397 | -0.086975 | -0.082397 | 0.050354 | -0.041199 | 0.12817 | -0.11902 | 0.21515 | -0.032044 | 0.29297 | 123.1201 | 0.045776 | 123.1155 | 123.1293 | 122.9828 | 122.9324 | 122.8958 | -123.175 | -123.0652 | 122.9233 | 123.0286 | 59.8755 | 59.8663
444.3281 | 123.3078 | -59.9442 | 63.0249 | -0.037613 | 0.00049772 | 0.065704 | 0.078872 | 0.0020701 | -0.0011791 | 0.00092933 | 0.0063477 | -0.00012177 | 0.06172 | 0.062747 | -0.0030036 | 0.00042507 | -0.0037705 | -0.009155 | 62.9883 | -60.1456 | 63.0524 | -59.7382 | -60.1044 | 0.091553 | 0.14191 | 62.9379 | -60.0082 | 63.1393 | -59.8892 | -59.9808 | -59.7794 | -0.20142 | -0.036621 | 0.027466 | 0.20599 | 60.0357 | -0.16022 | 60.2371 | 0.041199 | -0.064087 | -0.086975 | 0.11444 | 0.054932 | 0.16479 | -0.036621 | 0.22888 | 0.027466 | 0.40741 | 123.1979 | 0.11902 | 123.1476 | 123.1338 | 122.9462 | 122.9324 | 122.8821 | -123.1705 | -123.0331 | 122.9965 | 123.0835 | 59.935 | 60.0861
445.3281 | 123.3032 | -59.9579 | 63.0341 | -0.091019 | 0.00071132 | 0.063995 | 0.081222 | 0.0012155 | -0.0020337 | 7.4734e-05 | 0.0063477 | -0.00033537 | 0.064497 | 0.066593 | -0.0034308 | 0.0027751 | 7.4746e-05 | -0.050354 | 62.9608 | -60.1456 | 62.9929 | -59.8297 | -60.1685 | 0.027466 | 0.018311 | 62.9517 | -60.0037 | 63.1027 | -59.9396 | -60.0082 | -59.7839 | -0.18768 | -0.073243 | -0.041199 | 0.12817 | 59.9854 | -0.21057 | 60.173 | -0.022888 | -0.045776 | -0.082398 | 0.068664 | 0.018311 | 0.17395 | -0.050354 | 0.21973 | -0.004578 | 0.31586 | 123.1384 | 0.064087 | 123.1064 | 123.1064 | 122.9553 | 122.9187 | 122.9095 | -123.1796 | -123.0377 | 122.9507 | 123.0606 | 59.9075 | 59.9762
446.3281 | 123.2437 | -59.9487 | 63.0524 | -0.045242 | 0.0028475 | 0.062713 | 0.080581 | 0.00014747 | -0.00032472 | -0.0018479 | -0.011963 | 0.00094643 | 0.06407 | 0.059116 | -0.0053534 | 0.0012797 | -0.00077965 | 0.027466 | 63.0249 | -60.1227 | 63.0249 | -59.7794 | -60.1456 | 0.086975 | 0.09613 | 62.9974 | -59.9808 | 63.0936 | -59.9533 | -60.0357 | -59.816 | -0.17395 | -0.027466 | -0.027466 | 0.16937 | 60.0357 | -0.19684 | 60.2097 | -0.022888 | -0.032044 | -0.054931 | 0.041199 | -0.004578 | 0.13275 | -0.086976 | 0.16479 | -0.054932 | 0.34332 | 123.1476 | 0.027466 | 123.0743 | 123.1476 | 122.9782 | 122.9736 | 122.9462 | -123.175 | -123.0331 | 122.9736 | 123.0423 | 59.9762 | 60.0449
447.3281 | 123.2895 | -59.9442 | 62.9837 | -0.1368 | 0.0024203 | 0.063354 | 0.079513 | -0.00070713 | 0.0022387 | -0.0029159 | -0.011963 | 0.0020144 | 0.065992 | 0.055698 | -0.0053534 | 0.0014933 | 0.0034927 | -0.07782 | 62.9974 | -60.1593 | 62.9791 | -59.848 | -60.2051 | -0.027466 | -0.041199 | 62.97 | -60.022 | 63.1027 | -59.9533 | -60.0449 | -59.8251 | -0.21515 | 0.013733 | -0.004578 | 0.096131 | 59.9167 | -0.26093 | 60.1318 | -0.045776 | -0.07782 | -0.013733 | 0.11902 | -0.009155 | 0.11902 | -0.10071 | 0.19684 | -0.022888 | 0.31128 | 123.1384 | 0.068665 | 123.1247 | 123.1567 | 122.9919 | 122.9416 | 122.9141 | -123.143 | -123.0057 | 122.9233 | 123.0469 | 59.8663 | 59.903
448.3281 | 123.3307 | -59.9304 | 62.9883 | -0.07576 | -0.0014249 | 0.062286 | 0.082503 | -0.00070713 | -0.00011112 | -0.0022751 | -0.0028075 | 0.00116 | 0.063643 | 0.057834 | -0.004499 | 0.0017069 | 0.00050195 | 0.004578 | 63.0066 | -60.1181 | 63.0753 | -59.7107 | -60.0906 | 0.082397 | 0.11444 | 62.9745 | -59.9716 | 63.2629 | -59.7015 | -60.2783 | -59.9213 | -0.18768 | 0.018311 | 0.086975 | 0.21973 | 60.0128 | -0.16022 | 60.2005 | 0.027466 | -0.041199 | -0.013733 | 0.27466 | 0.22888 | 0.009155 | -0.3479 | 0.050354 | -0.3067 | 0.40741 | 123.1934 | 0.27008 | 123.2346 | 123.1247 | 122.9462 | 122.937 | 122.905 | -123.1064 | -122.9599 | 123.0057 | 123.1934 | 59.935 | 60.0449
449.3281 | 123.2666 | -59.9579 | 63.0157 | -0.07576 | 0.0015659 | 0.063354 | 0.080367 | -0.0026297 | -0.00011112 | 0.00092933 | -0.0058593 | -0.00097617 | 0.063215 | 0.06467 | -0.0030036 | 0.0019205 | -0.0018479 | -0.12817 | 62.9837 | -60.1593 | 62.9654 | -59.8434 | -60.2463 | -0.032043 | -0.050354 | 62.9745 | -59.9945 | 63.0844 | -59.9625 | -60.054 | -59.8206 | -0.20142 | -0.032043 | -0.050354 | 0.11444 | 59.9258 | -0.28839 | 60.1273 | -0.086975 | -0.036621 | -0.041199 | 0.068665 | -0.004577 | 0.13733 | -0.09613 | 0.17395 | -0.059509 | 0.31586 | 123.1247 | 0.032044 | 123.0789 | 123.143 | 122.9691 | 122.9416 | 122.9324 | -123.175 | -123.0103 | 122.9233 | 123.0423 | 59.8297 | 59.9075
450.3281 | 123.3078 | -59.9304 | 63.0341 | -0.06813 | 0.0024203 | 0.063781 | 0.080581 | -6.6126e-05 | -0.0018201 | 0.0017837 | 0.0063477 | 9.1834e-05 | 0.060866 | 0.05997 | -0.0047126 | 0.00021147 | -0.00056605 | -0.009155 | 63.0249 | -60.1318 | 63.0615 | -59.7473 | -60.1044 | 0.091553 | 0.1236 | 62.9883 | -59.9625 | 63.1668 | -59.8755 | -59.9487 | -59.7427 | -0.20142 | -0.009156 | 0.027465 | 0.18311 | 60.022 | -0.17395 | 60.2234 | 0.027466 | -0.032043 | -0.045777 | 0.13275 | 0.054932 | 0.18768 | -0.01831 | 0.21973 | 0.013733 | 0.38452 | 123.1934 | 0.086975 | 123.1293 | 123.1567 | 122.9507 | 122.9553 | 122.9187 | -123.1659 | -122.9965 | 122.9919 | 123.0972 | 59.9213 | 60.054
451.3281 | 123.2391 | -59.9579 | 63.0157 | -0.12917 | 0.0034885 | 0.063995 | 0.081222 | 0.0010019 | -0.00032472 | 0.00050193 | -0.02417 | 0.00094643 | 0.063215 | 0.061466 | -0.0019354 | 0.0010661 | -0.0027023 | -0.09613 | 62.9654 | -60.1501 | 62.97 | -59.8663 | -60.2234 | -0.032043 | -0.11902 | 62.9791 | -59.9899 | 63.0798 | -59.9762 | -60.1089 | -59.8297 | -0.19226 | -0.050354 | -0.045776 | 0.091553 | 59.9258 | -0.2655 | 60.1181 | -0.073243 | -0.032043 | -0.036621 | 0.064087 | -0.01831 | 0.12817 | -0.15106 | 0.16022 | -0.11902 | 0.28381 | 123.1201 | 0.013733 | 123.0698 | 123.1155 | 122.9691 | 122.9233 | 122.937 | -123.1659 | -123.0057 | 122.9279 | 123.0377 | 59.8618 | 59.8389
452.3281 | 123.2803 | -59.9396 | 63.0203 | -0.037613 | 0.00071132 | 0.062286 | 0.079513 | -0.0011343 | -0.00075192 | -0.0012071 | -0.015015 | 9.1834e-05 | 0.063856 | 0.061466 | -0.0034308 | 0.0012797 | -0.0018479 | -0.018311 | 62.9837 | -60.1364 | 63.0295 | -59.7839 | -60.1227 | 0.059509 | 0.09613 | 62.9837 | -60.0082 | 63.1577 | -59.8755 | -59.9762 | -59.7565 | -0.19684 | -0.036621 | 0.009155 | 0.15564 | 59.9991 | -0.18311 | 60.1959 | 0.013733 | -0.068665 | -0.036621 | 0.13733 | 0.064087 | 0.1831 | -0.036621 | 0.25177 | 0.032044 | 0.35248 | 123.1659 | 0.13275 | 123.1659 | 123.1201 | 122.9919 | 122.9233 | 122.9233 | -123.1567 | -123.0286 | 122.9691 | 123.0972 | 59.9213 | 60.0357
453.3281 | 123.2437 | -59.967 | 62.9974 | -0.098648 | -0.00014308 | 0.065063 | 0.079513 | -0.0032705 | 0.0015979 | 0.0015701 | -0.015015 | 0.002228 | 0.062788 | 0.064456 | -0.003858 | 0.0014933 | -0.0024887 | -0.086975 | 62.9929 | -60.1044 | 62.9883 | -59.8434 | -60.2188 | -0.013733 | -0.045776 | 62.9883 | -60.0037 | 63.089 | -59.9533 | -60.0357 | -59.8068 | -0.13733 | -0.004578 | -0.009156 | 0.1236 | 59.9533 | -0.25177 | 60.0906 | -0.11444 | -0.036621 | -0.009156 | 0.091552 | 0.013733 | 0.16022 | -0.068665 | 0.19684 | -0.032044 | 0.26093 | 123.0927 | 0.050354 | 123.0927 | 123.0972 | 122.9919 | 122.9599 | 122.9553 | -123.1018 | -123.0011 | 122.9553 | 123.056 | 59.8801 | 59.9213
454.3281 | 123.2666 | -59.9304 | 63.0432 | -0.12154 | 0.0013523 | 0.062927 | 0.08229 | -0.0019889 | -0.0022473 | -0.00056607 | -0.048584 | 0.00116 | 0.064283 | 0.06467 | -0.0049262 | 0.0029887 | -0.0029159 | 0 | 62.9974 | -60.1227 | 63.0569 | -59.7656 | -60.1227 | 0.064087 | 0.10529 | 62.9791 | -59.9716 | 63.1348 | -59.8846 | -59.9945 | -59.7931 | -0.19226 | -0.045776 | 0.013733 | 0.16479 | 59.9945 | -0.19226 | 60.1868 | 0 | -0.041199 | -0.064087 | 0.091553 | 0.045776 | 0.13733 | -0.064087 | 0.17853 | -0.022888 | 0.35706 | 123.1796 | 0.086975 | 123.1064 | 123.1201 | 122.9507 | 122.9279 | 122.9095 | -123.1659 | -123.0148 | 122.9874 | 123.0652 | 59.9304 | 60.0357
455.3281 | 123.2437 | -59.9442 | 63.0203 | -0.11391 | 0.0015659 | 0.063141 | 0.081008 | 0.0012155 | 0.00095708 | -0.0012071 | -0.033325 | 0.00051903 | 0.065779 | 0.058475 | -0.0059942 | 0.0019205 | -0.0020615 | -0.091553 | 62.9883 | -60.1181 | 63.002 | -59.8801 | -60.2142 | -0.045776 | -0.064087 | 62.9791 | -59.9991 | 63.1027 | -59.9625 | -60.054 | -59.8068 | -0.17395 | -0.032044 | -0.018311 | 0.064087 | 59.8984 | -0.27008 | 60.0723 | -0.09613 | -0.054931 | -0.041199 | 0.082397 | -0.01831 | 0.13733 | -0.10986 | 0.19226 | -0.054932 | 0.23804 | 123.1201 | 0.036621 | 123.1018 | 123.1064 | 122.9782 | 122.9324 | 122.9233 | -123.1384 | -123.0194 | 122.9462 | 123.0469 | 59.8526 | 59.8801
456.3281 | 123.2712 | -59.9396 | 63.0157 | -0.10628 | 0.0017795 | 0.065063 | 0.078445 | -0.0032705 | -0.0035291 | 0.00071573 | -0.030273 | -0.00097617 | 0.064283 | 0.066165 | -0.003858 | -0.00042933 | 0.00028835 | 0.004578 | 63.0432 | -60.0998 | 62.9745 | -59.761 | -60.0861 | 0.050354 | 0.1236 | 62.9974 | -59.9899 | 63.1485 | -59.8755 | -59.967 | -59.7656 | -0.16022 | 0.027466 | -0.041199 | 0.17853 | 59.9899 | -0.14649 | 60.1501 | 0.013732 | -0.050354 | -0.01831 | 0.13275 | 0.064087 | 0.17395 | -0.027466 | 0.2243 | 0.022888 | 0.33875 | 123.0743 | 0.11444 | 123.1384 | 123.143 | 122.9874 | 122.9828 | 122.937 | -123.1155 | -123.0057 | 122.9141 | 123.0881 | 59.9442 | 60.0632
457.3281 | 123.2254 | -59.9442 | 62.9974 | -0.083389 | 0.00049772 | 0.064209 | 0.081649 | 0.00036107 | -0.00032472 | -0.00035247 | -0.018066 | 0.0013736 | 0.064924 | 0.063175 | -0.003858 | 0.00063867 | 7.4746e-05 | -0.091553 | 62.9654 | -60.1318 | 62.9883 | -59.8343 | -60.2234 | -0.068665 | -0.082397 | 62.9608 | -60.0357 | 63.0936 | -59.9762 | -60.0677 | -59.8251 | -0.18768 | -0.032044 | -0.009156 | 0.10986 | 59.8755 | -0.27924 | 60.0632 | -0.091553 | -0.091553 | -0.036622 | 0.09613 | -0.032043 | 0.11902 | -0.1236 | 0.21057 | -0.032043 | 0.29755 | 123.1201 | 0.05951 | 123.1293 | 123.0972 | 122.9965 | 122.9095 | 122.905 | -123.1293 | -123.0331 | 122.9324 | 123.0377 | 59.8526 | 59.8618
458.3281 | 123.2758 | -59.9075 | 63.0203 | -0.052872 | 0.0017795 | 0.063781 | 0.082503 | -0.0026297 | -0.0011791 | -0.0012071 | 0.18945 | -0.00033537 | 0.066847 | 0.064029 | -0.0049262 | 0.0021341 | -0.0048387 | 0.018311 | 63.0386 | -60.0906 | 63.0661 | -59.729 | -60.0952 | 0.082397 | -0.14191 | 63.0249 | -59.9716 | 63.1622 | -59.9121 | -59.9258 | -59.7473 | -0.1831 | 0.01831 | 0.045776 | 0.17853 | 59.9899 | -0.18768 | 60.173 | -0.004578 | -0.064087 | 0.004577 | 0.14191 | -0.004577 | 0.16022 | -0.01831 | 0.2243 | 0.045777 | 0.36163 | 123.1567 | 0.05951 | 123.1338 | 123.1293 | 122.9965 | 122.9462 | 122.9324 | -123.111 | -122.9919 | 122.9736 | 123.0698 | 59.9258 | 59.7656
459.3281 | 123.3032 | -59.9213 | 63.0249 | -0.037613 | 7.0518e-05 | 0.063781 | 0.082076 | 0.0014291 | -0.00053832 | -0.0022751 | -0.030273 | 0.00030543 | 0.062575 | 0.065311 | -0.0042854 | 0.0029887 | -0.0033433 | -0.041199 | 63.0066 | -60.1181 | 63.0295 | -59.7702 | -60.1227 | 0.027466 | 0.036621 | 62.9745 | -59.9945 | 63.1577 | -59.8846 | -59.9762 | -59.761 | -0.19684 | -0.01831 | 0.004578 | 0.15106 | 59.9487 | -0.20142 | 60.1456 | -0.004578 | -0.073242 | -0.050354 | 0.13275 | 0.036621 | 0.16022 | -0.054931 | 0.23346 | 0.018311 | 0.3479 | 123.1476 | 0.10986 | 123.1522 | 123.1247 | 122.9691 | 122.9279 | 122.8958 | -123.143 | -123.0194 | 122.9507 | 123.0789 | 59.8801 | 59.9579
460.3906 | 123.2895 | -59.9579 | 63.0112 | 0.023422 | 0.0019931 | 0.065063 | 0.080367 | 0.0016427 | -0.0018201 | -0.0012071 | -0.030273 | -0.00012177 | 0.064283 | 0.058475 | -0.003858 | 0.00042507 | -0.0033433 | -0.10986 | 62.9837 | -60.1364 | 63.0249 | -59.8068 | -60.173 | -0.064087 | -0.050354 | 62.9608 | -59.9899 | 63.1531 | -59.9487 | -60.0494 | -59.7885 | -0.17853 | -0.027465 | 0.013733 | 0.15106 | 59.8938 | -0.21515 | 60.0723 | -0.036621 | -0.032043 | -0.050354 | 0.14191 | 0.009156 | 0.16937 | -0.091552 | 0.20142 | -0.059509 | 0.32959 | 123.1613 | 0.041199 | 123.143 | 123.1201 | 122.9507 | 122.9416 | 122.9187 | -123.1476 | -123.0011 | 122.9828 | 123.111 | 59.848 | 59.9075
461.3281 | 123.2529 | -59.9487 | 63.0295 | -0.060501 | 7.0518e-05 | 0.062927 | 0.081863 | -0.0026297 | -0.0041699 | -0.00013887 | -0.021118 | 9.1834e-05 | 0.064711 | 0.059757 | -0.0049262 | 0.0021341 | -0.0014207 | -0.10071 | 63.0203 | -60.1089 | 63.0112 | -59.9442 | -60.1089 | -0.073242 | -0.091553 | 62.9929 | -59.9899 | 63.1073 | -59.9579 | -60.0723 | -59.8114 | -0.16022 | -0.009155 | -0.018311 | 0.004577 | 59.8755 | -0.16022 | 60.0357 | 0 | -0.041199 | -0.036621 | 0.07782 | -0.009156 | 0.13733 | -0.1236 | 0.17853 | -0.082398 | 0.16479 | 123.1201 | 0.032043 | 123.0972 | 123.1293 | 122.9828 | 122.9691 | 122.9416 | -123.1384 | -123.0194 | 122.9599 | 123.056 | 59.848 | 59.8572
462.3281 | 123.262 | -59.9121 | 63.0295 | -0.037613 | 0.00028412 | 0.064636 | 0.080581 | 0.0031381 | -0.0026745 | -0.00099327 | -0.082153 | -0.0031126 | 0.06172 | 0.063175 | -0.00279 | 0.00042507 | -0.0024887 | -0.004578 | 63.0524 | -60.1044 | 63.0432 | -60.022 | -60.0037 | 0.073242 | 0.13733 | 62.9929 | -59.9579 | 63.176 | -59.8801 | -59.967 | -59.7519 | -0.19226 | 0.022888 | 0.013733 | -0.10986 | 59.9854 | -0.091553 | 60.1776 | 0.10071 | -0.045777 | -0.036621 | 0.14648 | 0.032043 | 0.16022 | -0.054932 | 0.20599 | -0.009155 | 0.082397 | 123.1476 | 0.07782 | 123.1338 | 123.1567 | 122.9507 | 122.9645 | 122.905 | -123.1338 | -122.9874 | 122.9553 | 123.0881 | 59.9075 | 60.0494
463.3281 | 123.2071 | -59.9304 | 63.0249 | -0.10628 | 0.0022067 | 0.063354 | 0.081863 | 0.00057467 | -0.0013929 | -0.00056607 | -0.027222 | 0.00116 | 0.062147 | 0.058475 | -0.0030036 | 0.00021147 | -0.0033433 | -0.10071 | 63.0066 | -60.1547 | 62.9883 | -59.8389 | -60.1913 | -0.064087 | -0.091553 | 63.002 | -60.0128 | 63.2034 | -60.0632 | -59.9533 | -59.7885 | -0.2243 | -0.01831 | -0.036621 | 0.091553 | 59.8663 | -0.26093 | 60.0906 | -0.036621 | -0.082397 | -0.022888 | 0.17853 | -0.13275 | 0.14191 | -0.022888 | 0.2243 | 0.059509 | 0.31586 | 123.143 | -0.050354 | 123.2162 | 123.1613 | 123.0148 | 122.937 | 122.9324 | -123.1796 | -123.0377 | 122.9187 | 123.1338 | 59.8297 | 59.8389
464.3281 | 123.2895 | -59.9213 | 63.0341 | -0.07576 | -0.00035668 | 0.063141 | 0.081435 | -0.0022025 | -0.00075192 | -0.0031297 | -0.011963 | -0.00033537 | 0.065352 | 0.059757 | -0.0032172 | -0.00042933 | 0.00028835 | -0.10986 | 63.0524 | -60.1318 | 63.002 | -59.8343 | -60.1959 | -0.050354 | -0.041199 | 62.9974 | -59.9808 | 63.1119 | -59.9167 | -60.0357 | -59.7702 | -0.21057 | 0.01831 | -0.032044 | 0.086975 | 59.8709 | -0.27466 | 60.0815 | -0.064087 | -0.059509 | -0.036621 | 0.077819 | 0.004578 | 0.15106 | -0.11444 | 0.21057 | -0.054932 | 0.29755 | 123.1338 | 0.064087 | 123.0927 | 123.1842 | 122.9782 | 122.9736 | 122.9187 | -123.1659 | -123.0148 | 122.9233 | 123.0331 | 59.8114 | 59.8801
465.3281 | 123.2574 | -59.9533 | 63.0066 | -0.083389 | 0.0019931 | 0.0625 | 0.082076 | 0.0012155 | -0.0020337 | 0.00092933 | -0.02417 | -0.00097617 | 0.064283 | 0.060184 | -0.003858 | 0.0032023 | -0.00099325 | -0.1236 | 63.002 | -60.1273 | 62.9929 | -59.8389 | -60.2051 | -0.091553 | -0.07782 | 62.9883 | -59.9854 | 63.0936 | -59.9625 | -60.0357 | -59.7931 | -0.17395 | -0.004578 | -0.013733 | 0.11444 | 59.8618 | -0.25177 | 60.0357 | -0.07782 | -0.032044 | -0.018311 | 0.086975 | -0.009155 | 0.16022 | -0.082398 | 0.19226 | -0.050354 | 0.28839 | 123.1201 | 0.022889 | 123.0789 | 123.1293 | 122.9736 | 122.9553 | 122.9416 | -123.1338 | -122.9919 | 122.9462 | 123.0469 | 59.8297 | 59.8755
466.3906 | 123.2941 | -59.9487 | 62.9883 | -0.083389 | 0.00049772 | 0.063781 | 0.083785 | 0.00014747 | -0.0016065 | -0.00099327 | -0.10046 | -0.00054897 | 0.064283 | 0.060398 | -0.0042854 | 0.0040567 | -0.0012071 | -0.1236 | 63.0203 | -60.1639 | 63.002 | -59.816 | -60.1822 | -0.1236 | -0.09613 | 62.97 | -59.9808 | 63.1577 | -59.9396 | -60.022 | -59.761 | -0.21515 | 0.032044 | 0.013733 | 0.13275 | 59.8251 | -0.23346 | 60.0403 | -0.018311 | -0.032044 | -0.01831 | 0.16937 | 0.009155 | 0.18768 | -0.073243 | 0.21973 | -0.041199 | 0.3479 | 123.1659 | 0.041199 | 123.1384 | 123.1842 | 122.9507 | 122.9691 | 122.9187 | -123.1522 | -122.9691 | 122.9507 | 123.1064 | 59.8251 | 59.8526
467.3281 | 123.2162 | -59.935 | 63.0203 | -0.083389 | 0.0030613 | 0.063995 | 0.079726 | -0.0022025 | -0.0013929 | 0.0024245 | -0.018066 | 0.002228 | 0.063429 | 0.058048 | -0.0059942 | 0.0027751 | 0.0026383 | -0.14191 | 63.0341 | -60.1181 | 62.9883 | -59.8297 | -60.1822 | -0.07782 | 0.022888 | 63.002 | -59.9487 | 63.1256 | -59.9625 | -60.0266 | -59.7702 | -0.1831 | 0.013733 | -0.032044 | 0.10529 | 59.8572 | -0.24719 | 60.0403 | -0.064087 | -0.013732 | -0.018311 | 0.10529 | -0.027465 | 0.16479 | -0.091552 | 0.17853 | -0.07782 | 0.28839 | 123.1064 | -0.013733 | 123.0743 | 123.1522 | 122.9507 | 122.9691 | 122.937 | -123.1384 | -122.9691 | 122.9233 | 123.0606 | 59.7931 | 59.9579
468.3281 | 123.2895 | -59.8846 | 63.0295 | -0.037613 | -0.00078408 | 0.062713 | 0.081649 | 0.0012155 | -0.0013929 | -0.0020615 | -0.018066 | 0.0013736 | 0.064283 | 0.064029 | -0.003858 | 0.0036295 | -0.00099325 | -0.054932 | 63.0569 | -60.0998 | 63.0569 | -59.7427 | -60.1089 | 0.013733 | 0.073242 | 63.0066 | -59.9625 | 63.1851 | -59.8572 | -59.9533 | -59.7107 | -0.21515 | 0.027466 | 0.027466 | 0.14191 | 59.8984 | -0.2243 | 60.1135 | -0.009156 | -0.077819 | -0.022888 | 0.15564 | 0.027466 | 0.17395 | -0.068664 | 0.25177 | 0.009155 | 0.35706 | 123.1567 | 0.10529 | 123.1476 | 123.1567 | 122.9691 | 122.9416 | 122.8912 | -123.1293 | -122.9919 | 122.9416 | 123.0698 | 59.8297 | 59.9579
469.3281 | 123.2208 | -59.935 | 63.0157 | -0.098648 | -0.00035668 | 0.061859 | 0.081649 | 0.0014291 | -0.0033155 | -0.00099327 | -0.027222 | -0.00012177 | 0.06407 | 0.067234 | -0.0051398 | 0.0027751 | -0.00056605 | -0.14191 | 63.0341 | -60.0906 | 63.002 | -59.8114 | -60.1776 | -0.07782 | -0.10529 | 63.0066 | -59.9808 | 63.1119 | -59.9533 | -60.0357 | -59.7885 | -0.15564 | 0.018311 | -0.013733 | 0.1236 | 59.8572 | -0.24261 | 60.0128 | -0.086975 | -0.045776 | -0.009155 | 0.09613 | -0.01831 | 0.14648 | -0.10071 | 0.19226 | -0.054932 | 0.27924 | 123.0927 | 0.027466 | 123.0927 | 123.1247 | 122.9874 | 122.9691 | 122.9416 | -123.1064 | -122.9965 | 122.937 | 123.0469 | 59.7931 | 59.8297
470.3281 | 123.317 | -59.8938 | 63.0753 | -0.07576 | 0.0011385 | 0.063995 | 0.078872 | 0.00057467 | 0.0013843 | -0.0016343 | 0.00024405 | 0.0013736 | 0.063002 | 0.059543 | -0.0049262 | 0.0025613 | -0.0012071 | -0.045776 | 63.0432 | -60.0723 | 63.0936 | -59.697 | -60.0632 | 0.032043 | 0.10986 | 62.9974 | -59.935 | 63.2172 | -59.816 | -59.935 | -59.7107 | -0.17853 | -0.032043 | 0.018311 | 0.19684 | 59.9258 | -0.16937 | 60.1044 | 0.009156 | -0.041199 | -0.077819 | 0.14191 | 0.07782 | 0.18311 | -0.041199 | 0.22431 | 0 | 0.37537 | 123.1659 | 0.11902 | 123.1522 | 123.1155 | 122.9324 | 122.937 | 122.8912 | -123.1476 | -123.0103 | 122.9874 | 123.111 | 59.848 | 60.0037
471.3281 | 123.2712 | -59.9442 | 63.0295 | -0.17494 | 0.0026339 | 0.063354 | 0.081863 | -6.6126e-05 | -0.00096552 | -0.0022751 | -0.048584 | 0.00094643 | 0.066206 | 0.060611 | -0.004499 | 0.0036295 | -0.0018479 | -0.10071 | 63.0295 | -60.1089 | 63.0432 | -59.7565 | -60.1501 | -0.07782 | -0.059509 | 63.002 | -59.9762 | 63.1622 | -59.9167 | -60.0037 | -59.7656 | -0.16479 | 0 | 0.013733 | 0.18768 | 59.8663 | -0.20599 | 60.0311 | -0.041198 | -0.032043 | -0.027466 | 0.13275 | 0.027466 | 0.17853 | -0.059509 | 0.21057 | -0.027466 | 0.35248 | 123.1522 | 0.059509 | 123.1384 | 123.1384 | 122.9782 | 122.9736 | 122.9462 | -123.1384 | -123.0057 | 122.9874 | 123.1064 | 59.8434 | 59.8846
472.3281 | 123.2574 | -59.9258 | 63.0295 | -0.10628 | 0.0022067 | 0.06549 | 0.07994 | 0.00036107 | -0.00075192 | -0.00099327 | -0.018066 | 0.00094643 | 0.062147 | 0.065311 | -0.0040716 | 0.0021341 | 0.0019973 | -0.12817 | 63.0478 | -60.0815 | 63.0249 | -59.7931 | -60.173 | -0.059509 | -0.073242 | 62.9974 | -59.9533 | 63.1531 | -59.9075 | -59.9899 | -59.7702 | -0.15564 | 0.018311 | -0.004578 | 0.13275 | 59.8663 | -0.24719 | 60.022 | -0.091553 | -0.027466 | -0.032043 | 0.1236 | 0.01831 | 0.15564 | -0.064087 | 0.1831 | -0.036621 | 0.28839 | 123.1064 | 0.045776 | 123.1064 | 123.1293 | 122.9507 | 122.9736 | 122.9233 | -123.111 | -122.9828 | 122.9507 | 123.0789 | 59.7977 | 59.8526
473.3281 | 123.2391 | -59.8846 | 63.0249 | -0.12154 | -0.00014308 | 0.064422 | 0.080154 | -0.0013479 | -0.0013929 | -0.00099327 | -0.036377 | -0.00054897 | 0.062788 | 0.062107 | -0.003858 | 0.0036295 | 0.0013565 | -0.14648 | 63.0432 | -60.0952 | 63.0066 | -59.7931 | -60.1639 | -0.09613 | -0.13275 | 63.0432 | -59.9762 | 63.1256 | -59.9304 | -60.0311 | -59.7794 | -0.21057 | 0.018311 | -0.01831 | 0.091553 | 59.7885 | -0.27923 | 59.9991 | -0.068664 | -0.091552 | 0.018311 | 0.10071 | -0.045776 | 0.10529 | -0.14648 | 0.19684 | -0.054932 | 0.30212 | 123.1018 | 0.045776 | 123.1018 | 123.1384 | 123.0194 | 122.9279 | 122.9279 | -123.1201 | -123.0011 | 122.8912 | 123.0103 | 59.7382 | 59.7519
474.3281 | 123.2849 | -59.9121 | 63.0341 | -0.10628 | 0.0024203 | 0.062927 | 0.081222 | 0.0027109 | -0.0011791 | -0.00056607 | -0.030273 | -0.0014036 | 0.061506 | 0.062961 | -0.0059942 | 0.0017069 | -0.00013885 | -0.1236 | 63.0524 | -60.1044 | 63.0341 | -59.7702 | -60.0998 | -0.036621 | -0.036621 | 63.0249 | -59.9579 | 63.1668 | -59.8526 | -59.9762 | -59.7336 | -0.19226 | 0.01831 | 0 | 0.14191 | 59.8755 | -0.18768 | 60.0677 | 0.004578 | -0.045777 | -0.009156 | 0.13275 | 0.059509 | 0.17853 | -0.064087 | 0.2243 | -0.01831 | 0.33417 | 123.1384 | 0.10529 | 123.1247 | 123.1567 | 122.9828 | 122.9645 | 122.937 | -123.1384 | -122.9919 | 122.9462 | 123.0789 | 59.7885 | 59.8755
475.3281 | 123.2574 | -59.8938 | 63.0478 | -0.12154 | 0.0019931 | 0.06485 | 0.081435 | -0.00027993 | -0.00053832 | 0.0011429 | -0.051636 | 0.00030543 | 0.063856 | 0.065738 | -0.0023626 | 0.0010661 | -0.0020615 | -0.13733 | 63.0341 | -60.0952 | 63.0295 | -59.761 | -60.1639 | -0.082397 | -0.09613 | 63.0295 | -59.935 | 63.1485 | -59.9213 | -60.0266 | -59.7839 | -0.20142 | -0.013733 | -0.018311 | 0.13275 | 59.8114 | -0.27008 | 60.0128 | -0.068664 | -0.041199 | -0.018311 | 0.10071 | -0.027466 | 0.10986 | -0.13275 | 0.15106 | -0.091552 | 0.33417 | 123.1247 | 0.013733 | 123.0835 | 123.1293 | 122.9645 | 122.9279 | 122.9233 | -123.143 | -122.9828 | 122.9233 | 123.0423 | 59.7565 | 59.7977
476.3281 | 123.2346 | -59.935 | 63.0432 | -0.06813 | -0.00078408 | 0.063995 | 0.081863 | -0.00027993 | 0.00010248 | -0.0018479 | -0.0058593 | 0.00030543 | 0.06172 | 0.060611 | -0.0042854 | 0.0021341 | -0.0024887 | -0.068665 | 63.0661 | -60.0677 | 63.0203 | -59.8022 | -60.1776 | -0.082397 | -0.091553 | 63.0341 | -59.9213 | 63.1531 | -59.8892 | -59.9808 | -59.7702 | -0.13275 | 0.022888 | -0.022888 | 0.13275 | 59.8526 | -0.24261 | 59.9854 | -0.10986 | 0.013733 | -0.009155 | 0.10986 | 0.045777 | 0.16479 | -0.045776 | 0.15106 | -0.059509 | 0.2655 | 123.0881 | 0.032044 | 123.0743 | 123.1338 | 122.9553 | 123.0011 | 122.9691 | -123.111 | -122.9645 | 122.9553 | 123.0881 | 59.8663 | 59.8434
477.3281 | 123.2803 | -59.8801 | 63.0341 | -0.06813 | -0.00035668 | 0.064636 | 0.082076 | 0.0012155 | -0.0028881 | -0.0018479 | -0.051636 | -0.002258 | 0.061506 | 0.058902 | -0.0036444 | 0.0027751 | -0.0039841 | -0.14191 | 63.0249 | -60.0815 | 63.0707 | -59.7427 | -60.1318 | -0.086975 | -0.07782 | 63.0157 | -59.9258 | 63.1805 | -59.8892 | -59.9899 | -59.729 | -0.20142 | -0.009156 | 0.036621 | 0.13733 | 59.7931 | -0.25177 | 59.9945 | -0.050354 | -0.045776 | -0.018311 | 0.14648 | -0.009155 | 0.15106 | -0.10986 | 0.19684 | -0.064087 | 0.33875 | 123.1522 | 0.036621 | 123.1064 | 123.1064 | 122.9416 | 122.905 | 122.8958 | -123.1155 | -122.9599 | 122.9507 | 123.0606 | 59.7382 | 59.8022
478.3281 | 123.2437 | -59.8984 | 63.0432 | -0.098648 | 0.0011385 | 0.064422 | 0.081435 | 0.00014747 | -0.0031017 | -0.00035247 | -0.042481 | 0.0015872 | 0.062361 | 0.063175 | -0.004499 | 0.0019205 | -0.0031297 | -0.14648 | 63.0432 | -60.0861 | 63.0478 | -59.7519 | -60.1501 | -0.07782 | -0.09613 | 63.0203 | -59.9487 | 63.1668 | -59.9167 | -59.9991 | -59.7519 | -0.18768 | 0 | 0.004578 | 0.14648 | 59.8206 | -0.25177 | 60.0082 | -0.064086 | -0.050354 | -0.022888 | 0.1236 | -0.018311 | 0.14648 | -0.10071 | 0.19684 | -0.050354 | 0.33417 | 123.1339 | 0.032043 | 123.1155 | 123.1293 | 122.9691 | 122.9416 | 122.9187 | -123.1293 | -122.9919 | 122.9462 | 123.0652 | 59.7519 | 59.8022
479.3281 | 123.2895 | -59.9075 | 63.0524 | -0.11391 | 0.0017795 | 0.063568 | 0.081863 | 0.0010019 | 0.0011707 | -0.0014207 | -0.11267 | 0.002869 | 0.061934 | 0.06232 | -0.006208 | 0.0021341 | 0.0026383 | -0.15106 | 63.0615 | -60.0861 | 63.089 | -59.7427 | -60.1273 | -0.091553 | -0.24261 | 62.97 | -59.9487 | 63.1897 | -59.8389 | -59.967 | -59.7015 | -0.17853 | 0.009155 | 0.036621 | 0.1648 | 59.816 | -0.21973 | 59.9945 | -0.041198 | -0.041198 | -0.082397 | 0.13733 | 0.068665 | 0.20599 | -0.059509 | 0.24719 | -0.018311 | 0.34332 | 123.175 | 0.10986 | 123.1384 | 123.1476 | 122.9187 | 122.9691 | 122.8775 | -123.1384 | -123.0011 | 122.9965 | 123.0972 | 59.7565 | 59.6649
480.3281 | 123.2529 | -59.8801 | 63.0798 | -0.1368 | 0.0013523 | 0.062286 | 0.082076 | 0.00078827 | 0.00052988 | -0.0018479 | -0.027222 | 0.0015872 | 0.06172 | 0.057834 | -0.0032172 | 0.0012797 | 0.00028835 | -0.18768 | 63.0753 | -60.0586 | 63.0341 | -59.7702 | -60.1273 | -0.10529 | -0.14191 | 63.0478 | -59.9258 | 63.1577 | -59.9167 | -60.0357 | -59.7885 | -0.17853 | -0.004578 | -0.045776 | 0.10986 | 59.7748 | -0.24719 | 59.9533 | -0.068664 | -0.045776 | -0.032043 | 0.07782 | -0.036621 | 0.091553 | -0.15564 | 0.13733 | -0.10986 | 0.28839 | 123.0927 | 0.009155 | 123.0835 | 123.1338 | 122.9736 | 122.9553 | 122.9279 | -123.1384 | -123.0057 | 122.9141 | 123.0377 | 59.6924 | 59.7382
481.3281 | 123.2712 | -59.903 | 63.0661 | -0.11391 | 0.0030613 | 0.062927 | 0.082503 | -0.0011343 | -0.0024609 | 0.00092933 | -0.051636 | -0.00012177 | 0.062361 | 0.067874 | -0.0070624 | 0.0010661 | 0.00050195 | -0.16022 | 63.0478 | -60.0952 | 63.0615 | -59.7198 | -60.0403 | -0.10071 | -0.10986 | 63.0295 | -59.9167 | 63.2263 | -59.848 | -59.9533 | -59.7061 | -0.19226 | -0.01831 | -0.004578 | 0.1831 | 59.8022 | -0.13733 | 59.9945 | 0.054932 | -0.013733 | -0.036621 | 0.16022 | 0.054932 | 0.19684 | -0.050354 | 0.21057 | -0.036621 | 0.37537 | 123.1567 | 0.068665 | 123.143 | 123.143 | 122.9462 | 122.9507 | 122.9324 | -123.1613 | -122.9828 | 122.9645 | 123.1293 | 59.7427 | 59.7931
482.3281 | 123.2574 | -59.8663 | 63.0798 | -0.12154 | 0.0013523 | 0.065918 | 0.07994 | 0.0010019 | -0.00075192 | -0.0012071 | -0.030273 | 0.0018008 | 0.063643 | 0.061252 | -0.0042854 | 0.0014933 | 0.00050195 | -0.19684 | 63.0569 | -60.054 | 63.0432 | -59.761 | -60.1501 | -0.11444 | -0.14648 | 63.0432 | -59.9396 | 63.1622 | -59.8892 | -59.9762 | -59.7427 | -0.18768 | -0.022888 | -0.036621 | 0.10529 | 59.7519 | -0.28381 | 59.9396 | -0.09613 | -0.073242 | -0.036621 | 0.082397 | -0.022888 | 0.1236 | -0.10986 | 0.19684 | -0.036621 | 0.29297 | 123.0972 | 0.050354 | 123.1018 | 123.111 | 122.9828 | 122.9233 | 122.9095 | -123.1338 | -123.0194 | 122.9095 | 123.0286 | 59.6695 | 59.7198
483.3281 | 123.3856 | -59.8663 | 63.0295 | -0.11391 | 0.00049772 | 0.063568 | 0.080581 | 0.0010019 | -0.00075192 | 0.0011429 | -0.07605 | -0.00097617 | 0.062788 | 0.066593 | -0.0064216 | 0.0014933 | -0.0020615 | -0.18768 | 63.0432 | -60.0677 | 63.0844 | -59.7336 | -60.1089 | -0.11444 | -0.13733 | 63.0478 | -59.9167 | 63.1989 | -59.848 | -59.967 | -59.6786 | -0.20142 | 0.013733 | 0.054932 | 0.13275 | 59.7519 | -0.24262 | 59.9533 | -0.041199 | -0.050354 | 0.018311 | 0.16937 | 0.018311 | 0.18768 | -0.10071 | 0.23804 | -0.050354 | 0.33417 | 123.1522 | 0.068665 | 123.1155 | 123.111 | 122.9645 | 122.9095 | 122.9141 | -123.0972 | -122.9462 | 122.9507 | 123.0652 | 59.6786 | 59.729
484.3281 | 123.262 | -59.8984 | 63.0661 | -0.14442 | 0.0011385 | 0.065277 | 0.081649 | -0.00027993 | -0.0022473 | 0.0011429 | -0.048584 | -0.00033537 | 0.064283 | 0.060611 | -0.0025764 | 0.00063867 | 7.4746e-05 | -0.18768 | 63.0661 | -60.0632 | 63.0936 | -59.7061 | -60.1227 | -0.10071 | -0.11444 | 63.0569 | -59.9121 | 63.1943 | -59.8755 | -59.9716 | -59.729 | -0.16479 | 0 | 0.027466 | 0.19226 | 59.7977 | -0.22431 | 59.9625 | -0.05951 | -0.013733 | -0.009155 | 0.12817 | 0.022888 | 0.16937 | -0.073243 | 0.1831 | -0.05951 | 0.35705 | 123.1567 | 0.036621 | 123.1064 | 123.1293 | 122.9691 | 122.9645 | 122.9553 | -123.1293 | -122.9782 | 122.9919 | 123.0927 | 59.7107 | 59.7839
485.3281 | 123.2254 | -59.8984 | 63.1119 | -0.098648 | 0.00092492 | 0.065704 | 0.082076 | -0.00070713 | -0.00096552 | -0.00077967 | -0.097412 | 0.0015872 | 0.064283 | 0.067661 | -0.00279 | 0.0027751 | -0.00013885 | -0.24719 | 63.1302 | -60.0815 | 62.9974 | -59.8206 | -60.2188 | -0.19684 | -0.25635 | 63.0981 | -59.9442 | 63.1439 | -59.9442 | -60.0586 | -59.7839 | -0.18311 | 0.018311 | -0.11444 | 0.077819 | 59.7015 | -0.32044 | 59.8846 | -0.13733 | -0.045777 | -0.013732 | 0.032044 | -0.045777 | 0.11444 | -0.16022 | 0.16022 | -0.11444 | 0.26093 | 123.0789 | 0 | 123.0881 | 123.2117 | 123.0423 | 123.0286 | 122.9965 | -123.1934 | -123.056 | 122.8958 | 123.0423 | 59.6512 | 59.642
486.3281 | 123.2666 | -59.8526 | 63.0844 | -0.098648 | 0.0017795 | 0.064209 | 0.082076 | 0.00014747 | 0.00052988 | -0.0014207 | -0.039429 | 0.0018008 | 0.062788 | 0.058689 | -0.0047126 | 0.0010661 | 0.00071555 | -0.21057 | 63.0844 | -59.9991 | 63.1027 | -59.6741 | -60.0815 | -0.10529 | -0.14648 | 63.0524 | -59.9167 | 63.2172 | -59.8343 | -59.9487 | -59.7061 | -0.14648 | 0 | 0.01831 | 0.17853 | 59.7473 | -0.22888 | 59.8938 | -0.082398 | -0.064087 | -0.032044 | 0.13275 | 0.01831 | 0.14648 | -0.09613 | 0.21057 | -0.032043 | 0.32501 | 123.1018 | 0.082397 | 123.1338 | 123.0835 | 122.9691 | 122.937 | 122.905 | -123.0835 | -123.0011 | 122.9553 | 123.0698 | 59.642 | 59.7061
487.3281 | 123.3032 | -59.8434 | 63.0798 | -0.12154 | 0.00071132 | 0.063354 | 0.082931 | 0.00036107 | 0.00095708 | -0.0014207 | -0.057739 | 0.0015872 | 0.064497 | 0.068515 | -0.002149 | 0.0034159 | -0.00056605 | -0.21973 | 63.0981 | -60.0403 | 63.0936 | -59.7198 | -60.0861 | -0.12817 | -0.16937 | 63.0753 | -59.9075 | 63.2401 | -59.8297 | -59.935 | -59.6741 | -0.19684 | 0.018311 | 0.013733 | 0.1236 | 59.7153 | -0.24262 | 59.9121 | -0.045777 | -0.064087 | -0.004578 | 0.16022 | 0.013733 | 0.16937 | -0.091553 | 0.23346 | -0.027466 | 0.32043 | 123.1338 | 0.07782 | 123.1476 | 123.1384 | 122.9828 | 122.9416 | 122.9187 | -123.1201 | -122.9874 | 122.937 | 123.0835 | 59.6237 | 59.6741
488.3281 | 123.2346 | -59.8618 | 63.1165 | -0.098648 | 0.00071132 | 0.066559 | 0.081008 | -0.00027993 | -0.0020337 | 0.00028833 | -0.018066 | 0.0015872 | 0.064283 | 0.056552 | -0.0036444 | 0.0040567 | -0.00013885 | -0.23804 | 63.1256 | -60.022 | 63.0707 | -59.7153 | -60.0632 | -0.10529 | -0.17395 | 63.0936 | -59.8938 | 63.208 | -59.816 | -59.9442 | -59.6878 | -0.16022 | 0.009155 | -0.045776 | 0.14648 | 59.7565 | -0.20142 | 59.9167 | -0.041198 | -0.032044 | -0.022888 | 0.091553 | 0.045776 | 0.17395 | -0.082398 | 0.20599 | -0.050354 | 0.3067 | 123.0927 | 0.07782 | 123.1018 | 123.1476 | 122.9874 | 122.9874 | 122.9553 | -123.1384 | -123.0103 | 122.9324 | 123.0698 | 59.6237 | 59.6878
489.3281 | 123.2712 | -59.8618 | 63.1165 | -0.052872 | 0.00092492 | 0.063781 | 0.083358 | -0.0022025 | 0.00031608 | -0.0031297 | -0.057739 | -0.00012177 | 0.064283 | 0.069797 | -0.0057806 | 0.0023477 | -0.0097519 | -0.25635 | 63.1256 | -60.0632 | 63.0798 | -59.7153 | -60.1227 | -0.16479 | -0.18768 | 63.0707 | -59.8984 | 63.2401 | -59.8114 | -59.935 | -59.6558 | -0.20142 | 0.009155 | -0.036621 | 0.14648 | 59.697 | -0.26093 | 59.8984 | -0.05951 | -0.036621 | -0.045776 | 0.1236 | 0.050354 | 0.20599 | -0.073243 | 0.24261 | -0.036622 | 0.3479 | 123.143 | 0.086975 | 123.1384 | 123.1888 | 122.9691 | 122.9874 | 122.9324 | -123.1796 | -123.0148 | 122.9416 | 123.1018 | 59.6054 | 59.6741
490.3281 | 123.2712 | -59.8297 | 63.121 | -0.12154 | 0.0011385 | 0.063781 | 0.08229 | 0.0031381 | -0.0028881 | -0.00099327 | -0.033325 | 0.00116 | 0.064283 | 0.068729 | -0.0036444 | 0.0029887 | -0.00099325 | -0.23346 | 63.1073 | -60.0037 | 63.121 | -59.6466 | -60.054 | -0.12817 | -0.16479 | 63.0936 | -59.8846 | 63.2492 | -59.8251 | -59.9304 | -59.6695 | -0.17395 | -0.013733 | 0 | 0.18311 | 59.7015 | -0.2243 | 59.8755 | -0.050354 | -0.054932 | -0.027466 | 0.12817 | 0.004578 | 0.16022 | -0.10071 | 0.21515 | -0.045776 | 0.35706 | 123.1247 | 0.05951 | 123.1339 | 123.111 | 122.9782 | 122.937 | 122.9233 | -123.1247 | -123.0057 | 122.9507 | 123.0789 | 59.5963 | 59.6649
491.3281 | 123.2529 | -59.8434 | 63.1073 | -0.083389 | 0.0019931 | 0.060577 | 0.081222 | 0.00057467 | 0.00031608 | -0.00077967 | -0.10046 | 0.00073263 | 0.06407 | 0.060611 | -0.004499 | 0.0051249 | -0.0044113 | -0.30212 | 63.1531 | -60.0494 | 63.0569 | -59.7656 | -60.1593 | -0.18768 | -0.27466 | 63.1302 | -59.9121 | 63.2172 | -59.848 | -59.9762 | -59.7015 | -0.20599 | 0.045776 | -0.050354 | 0.07782 | 59.6558 | -0.31586 | 59.8618 | -0.10986 | -0.068664 | 0.022888 | 0.10986 | -0.004577 | 0.14191 | -0.13275 | 0.21057 | -0.064087 | 0.28381 | 123.1064 | 0.064087 | 123.1293 | 123.2025 | 123.0423 | 122.9965 | 122.9736 | -123.1567 | -123.0194 | 122.9004 | 123.0606 | 59.5413 | 59.5688
492.3281 | 123.2803 | -59.8022 | 63.1165 | -0.15968 | 0.00092492 | 0.06485 | 0.081435 | -0.0011343 | -0.00011112 | -0.0016343 | -0.030273 | 9.1834e-05 | 0.064283 | 0.062961 | -0.0030036 | 0.0017069 | 0.00028835 | -0.25177 | 63.1165 | -60.0311 | 63.208 | -59.6054 | -60.0677 | -0.10071 | -0.17853 | 63.0569 | -59.8663 | 63.2767 | -59.7839 | -59.8846 | -59.6512 | -0.22888 | 0 | 0.091553 | 0.19684 | 59.7015 | -0.2655 | 59.9304 | -0.036621 | -0.064087 | -0.059509 | 0.16022 | 0.01831 | 0.15106 | -0.082398 | 0.21515 | -0.018311 | 0.42572 | 123.2391 | 0.082397 | 123.143 | 123.1476 | 122.9233 | 122.9187 | 122.8592 | -123.1476 | -122.9828 | 123.0103 | 123.0789 | 59.5505 | 59.6237
493.3281 | 123.1934 | -59.8526 | 63.1393 | -0.11391 | 0.0028475 | 0.065277 | 0.082076 | -0.00070713 | -0.0013929 | -0.0031297 | -0.066895 | 0.003937 | 0.065352 | 0.068515 | -0.0040716 | 0.0034159 | -0.0018479 | -0.32959 | 63.1714 | -60.0266 | 63.0341 | -59.761 | -60.1593 | -0.21973 | -0.30212 | 63.1577 | -59.8938 | 63.1943 | -59.8709 | -59.9899 | -59.7061 | -0.17395 | 0.032044 | -0.10528 | 0.091553 | 59.6329 | -0.3067 | 59.8068 | -0.13275 | -0.041199 | 0.018311 | 0.054932 | -0.018311 | 0.14648 | -0.13733 | 0.18768 | -0.09613 | 0.2655 | 123.0606 | 0.022888 | 123.0881 | 123.1979 | 123.0515 | 123.024 | 123.0103 | -123.1659 | -123.0331 | 122.8867 | 123.0469 | 59.523 | 59.5505
494.3281 | 123.2437 | -59.7977 | 63.089 | -0.11391 | 0.0011385 | 0.063568 | 0.08229 | -0.0015615 | -0.0022473 | 0.00050193 | -0.027222 | 0.002228 | 0.065779 | 0.064243 | -0.003858 | 0.0012797 | -0.0014207 | -0.27008 | 63.1439 | -60.0037 | 63.1531 | -59.6237 | -60.0311 | -0.1236 | -0.21515 | 63.1073 | -59.8572 | 63.2812 | -59.7656 | -59.8801 | -59.642 | -0.20599 | 0.054932 | 0.064087 | 0.17395 | 59.6741 | -0.23346 | 59.8801 | -0.027466 | -0.05951 | 0.018311 | 0.19226 | 0.032043 | 0.15564 | -0.082398 | 0.21515 | -0.022888 | 0.37994 | 123.1567 | 0.091553 | 123.1384 | 123.1476 | 122.9645 | 122.9416 | 122.905 | -123.0927 | -122.9462 | 122.9507 | 123.0789 | 59.5276 | 59.5825
495.3281 | 123.2437 | -59.8114 | 63.1577 | -0.037613 | 0.0024203 | 0.065918 | 0.085708 | -0.00027993 | -0.00096552 | -0.00035247 | -0.085205 | 0.00030543 | 0.061293 | 0.062961 | -0.0051398 | 0.0021341 | 0.0026383 | -0.34332 | 63.1805 | -60.022 | 63.0753 | -59.7336 | -60.1181 | -0.20599 | -0.31128 | 63.1485 | -59.8755 | 63.2446 | -59.8114 | -59.9304 | -59.6832 | -0.21057 | 0.022888 | -0.082398 | 0.077819 | 59.6054 | -0.3067 | 59.816 | -0.09613 | -0.064087 | -0.009155 | 0.086975 | 0 | 0.12817 | -0.11902 | 0.19226 | -0.054932 | 0.28839 | 123.0972 | 0.064087 | 123.1201 | 123.2025 | 123.024 | 122.9919 | 122.9599 | -123.1796 | -123.0331 | 122.8867 | 123.056 | 59.4681 | 59.5001
496.3281 | 123.2895 | -59.7931 | 63.1485 | -0.11391 | 0.00092492 | 0.06784 | 0.082076 | 0.0012155 | -0.0011791 | -0.0024887 | -0.033325 | 0.002228 | 0.06407 | 0.065738 | -0.0040716 | 0.0023477 | -0.0014207 | -0.49439 | 63.0844 | -60.0037 | 63.1943 | -59.6283 | -59.9991 | -0.11444 | -0.22888 | 63.1302 | -59.8343 | 63.3087 | -59.7382 | -59.8618 | -59.642 | -0.21057 | -0.064087 | 0.045776 | 0.16479 | 59.6786 | -0.20599 | 59.8892 | 0.004578 | -0.041199 | -0.018311 | 0.16022 | 0.054932 | 0.15106 | -0.068664 | 0.19226 | -0.027465 | 0.37537 | 123.1979 | 0.096131 | 123.143 | 123.0881 | 122.9645 | 122.8775 | 122.9233 | -123.1522 | -122.9828 | 122.9874 | 123.1018 | 59.2987 | 59.5642
497.3281 | 123.1934 | -59.8068 | 63.1714 | -0.1368 | -0.00099768 | 0.0625 | 0.080794 | -0.0015615 | -0.0016065 | 0.0045609 | -0.063843 | 0.00073263 | 0.06172 | 0.065311 | -0.0034308 | 0.0044839 | 0.00092935 | -0.35706 | 63.2217 | -59.9762 | 63.0615 | -59.7427 | -60.1181 | -0.2243 | -0.35248 | 63.1805 | -59.848 | 63.2034 | -59.8297 | -59.9808 | -59.6786 | -0.16937 | 0.050354 | -0.10986 | 0.064087 | 59.5825 | -0.31128 | 59.7519 | -0.14191 | -0.041198 | 0.009155 | 0.032043 | -0.022888 | 0.12817 | -0.17395 | 0.16937 | -0.13275 | 0.23346 | 123.0377 | 0.01831 | 123.0515 | 123.1979 | 123.0286 | 123.0286 | 122.9874 | -123.1476 | -123.0194 | 122.8683 | 123.0103 | 59.4498 | 59.4543
498.3281 | 123.3078 | -59.7519 | 63.176 | -0.15205 | 0.0017795 | 0.06485 | 0.082076 | -0.0022025 | -0.00053832 | 0.0030655 | -0.045532 | -0.00012177 | 0.063215 | 0.06232 | -0.003858 | 0.0014933 | -0.0054795 | -0.31586 | 63.1805 | -59.9579 | 63.1805 | -59.5917 | -59.9854 | -0.13275 | -0.2655 | 63.1165 | -59.8114 | 63.3957 | -59.6695 | -59.8434 | -59.5871 | -0.20599 | 0.004578 | 0.004578 | 0.16022 | 59.6191 | -0.23346 | 59.8251 | -0.027466 | -0.059509 | -0.059509 | 0.21973 | 0.082397 | 0.16479 | -0.091553 | 0.2243 | -0.032044 | 0.36621 | 123.1384 | 0.14191 | 123.2071 | 123.1384 | 122.9279 | 122.9324 | 122.8683 | -123.1338 | -122.9874 | 122.9324 | 123.1476 | 59.436 | 59.4864
499.3281 | 123.175 | -59.816 | 63.2126 | -0.06813 | 0.0030613 | 0.063995 | 0.083144 | -0.0054067 | -0.00032472 | -0.0014207 | -0.057739 | 0.0015872 | 0.067061 | 0.061252 | -0.0047126 | 0.0036295 | -0.0022751 | -0.3891 | 63.2126 | -59.967 | 63.0341 | -59.6512 | -60.022 | -0.25177 | -0.42114 | 63.2217 | -59.8251 | 63.2217 | -59.8434 | -59.9716 | -59.6924 | -0.15106 | 0 | -0.17853 | 0.16479 | 59.5642 | -0.20599 | 59.7153 | -0.054932 | -0.009155 | 0.009156 | 0.009156 | -0.027466 | 0.1236 | -0.15564 | 0.13275 | -0.14648 | 0.31586 | 123.0011 | -0.018311 | 123.0469 | 123.1796 | 123.0469 | 123.0286 | 123.0377 | -123.1796 | -123.0377 | 122.85 | 123.0377 | 59.4269 | 59.3948
500.3281 | 123.2529 | -59.729 | 63.2034 | -0.07576 | 0.0026339 | 0.065063 | 0.081863 | 0.00078827 | -0.0011791 | -0.00056607 | -0.036377 | 0.0015872 | 0.062361 | 0.062961 | -0.0049262 | 0.00063867 | -0.00077965 | -0.37994 | 63.1989 | -59.9442 | 63.1805 | -59.61 | -60.0037 | -0.15564 | -0.32501 | 63.1714 | -59.816 | 63.327 | -59.7153 | -59.8526 | -59.5642 | -0.21515 | -0.004577 | -0.022888 | 0.11902 | 59.5734 | -0.27466 | 59.7885 | -0.059509 | -0.086975 | -0.032043 | 0.1236 | 0.013733 | 0.1648 | -0.1236 | 0.25177 | -0.036621 | 0.33417 | 123.1247 | 0.10071 | 123.143 | 123.143 | 122.9874 | 122.9279 | 122.9004 | -123.1476 | -123.0194 | 122.9095 | 123.056 | 59.3491 | 59.404
501.3281 | 123.1613 | -59.7427 | 63.2217 | -0.052872 | -0.00035668 | 0.063354 | 0.082503 | 0.0039927 | 0.0013843 | 0.0013565 | -0.066895 | 0.002228 | 0.063643 | 0.067447 | -0.0034308 | 0.0051249 | -0.0033433 | -0.39825 | 63.2721 | -59.9716 | 63.1119 | -59.6924 | -60.0861 | -0.23804 | -0.41657 | 63.2492 | -59.8206 | 63.2629 | -59.7977 | -59.9304 | -59.6466 | -0.22888 | 0.050354 | -0.10986 | 0.050354 | 59.5047 | -0.34332 | 59.7336 | -0.11444 | -0.07782 | 0.027466 | 0.041198 | -0.054931 | 0.096131 | -0.18768 | 0.17395 | -0.10986 | 0.27924 | 123.0835 | 0.022889 | 123.0835 | 123.2437 | 123.0698 | 123.0148 | 122.9919 | -123.1934 | -123.0423 | 122.8546 | 123.0057 | 59.3445 | 59.3262
502.3281 | 123.2208 | -59.7473 | 63.1897 | -0.091019 | 0.00071132 | 0.064209 | 0.082076 | -0.00092073 | 0.0022387 | -0.0016343 | -0.027222 | -0.00054897 | 0.064711 | 0.066806 | -0.004499 | 0.0025613 | -0.0014207 | -0.39368 | 63.2446 | -59.9258 | 63.2355 | -59.5551 | -59.9533 | -0.14648 | -0.32501 | 63.2034 | -59.7885 | 63.3545 | -59.6786 | -59.7885 | -59.6191 | -0.17853 | 0.054932 | 0.045777 | 0.19226 | 59.6008 | -0.20599 | 59.7794 | -0.027466 | -0.041199 | 0.013733 | 0.16479 | 0.068664 | 0.12817 | -0.041199 | 0.16937 | 0 | 0.37079 | 123.1613 | 0.10986 | 123.143 | 123.1705 | 122.9919 | 122.9919 | 122.9507 | -123.1155 | -122.9782 | 122.9828 | 123.1018 | 59.3536 | 59.4223
503.3281 | 123.1338 | -59.7336 | 63.2904 | -0.098648 | 0.00028412 | 0.063354 | 0.082931 | -0.00049353 | -0.0018201 | -0.00013887 | 0.033813 | 0.00116 | 0.066847 | 0.062747 | -0.00279 | 0.0023477 | -0.0037705 | -0.45776 | 63.2629 | -59.9396 | 63.1348 | -59.729 | -60.4568 | -0.21057 | -0.52643 | 63.2721 | -59.7565 | 63.2767 | -59.7794 | -59.9121 | -59.6237 | -0.20599 | -0.027466 | -0.15564 | 0.004578 | 59.523 | -0.72327 | 59.729 | -0.51727 | -0.022888 | -0.01831 | -0.013733 | -0.045776 | 0.10986 | -0.17853 | 0.13275 | -0.15564 | 0.21057 | 123.0743 | -0.022888 | 123.0331 | 123.2025 | 123.0286 | 122.9965 | 123.0057 | -123.23 | -123.0469 | 122.8683 | 123.0103 | 59.2758 | 59.2072
504.3281 | 123.2758 | -59.6558 | 63.2584 | -0.1368 | 0.00049772 | 0.0625 | 0.08464 | 0.0027109 | -0.0011791 | 0.0024245 | -0.039429 | 0.00116 | 0.065352 | 0.060825 | -0.004499 | 0.0038431 | -0.00077965 | -0.45319 | 63.2721 | -59.9075 | 63.208 | -59.5779 | -59.9716 | -0.20599 | -0.39825 | 63.2629 | -59.7519 | 63.3591 | -59.6924 | -59.7656 | -59.5093 | -0.25177 | 0.013733 | -0.050354 | 0.07782 | 59.4498 | -0.31586 | 59.7015 | -0.064087 | -0.09613 | 0.004577 | 0.10071 | -0.036621 | 0.14649 | -0.10986 | 0.24262 | -0.013733 | 0.32959 | 123.1155 | 0.059509 | 123.111 | 123.1796 | 123.0148 | 122.9279 | 122.9187 | -123.1659 | -123.0103 | 122.8638 | 123.0148 | 59.2026 | 59.2575
505.3281 | 123.175 | -59.6924 | 63.3316 | -0.052872 | 7.0518e-05 | 0.0625 | 0.084212 | -0.0032705 | -0.0028881 | -0.0018479 | -0.07605 | 0.0018008 | 0.065352 | 0.063816 | -0.0030036 | 0.0034159 | 0.0024245 | -0.41199 | 63.3133 | -59.8572 | 63.2355 | -59.5596 | -59.9579 | -0.17853 | -0.40283 | 63.2904 | -59.7336 | 63.327 | -59.7061 | -59.8434 | -59.5871 | -0.16479 | -0.018311 | -0.09613 | 0.13275 | 59.5139 | -0.2655 | 59.6786 | -0.10071 | -0.041199 | -0.041199 | -0.004578 | -0.013733 | 0.10529 | -0.15106 | 0.14648 | -0.10986 | 0.29755 | 123.0927 | 0.027466 | 123.0606 | 123.1705 | 123.024 | 123.0057 | 122.9828 | -123.1888 | -123.0652 | 122.9279 | 123.0194 | 59.2804 | 59.2896
506.3281 | 123.2025 | -59.6786 | 63.3224 | -0.022354 | 0.0017795 | 0.063568 | 0.08229 | 0.0042063 | -0.0013929 | -0.0020615 | -0.051636 | 0.0024416 | 0.065779 | 0.061466 | -0.0036444 | 0.0021341 | -0.0020615 | -0.48981 | 63.3545 | -59.8572 | 63.208 | -59.5734 | -59.9854 | -0.2243 | -0.49896 | 63.3087 | -59.7015 | 63.3728 | -59.6832 | -59.8114 | -59.5367 | -0.17853 | 0.032043 | -0.11444 | 0.10529 | 59.4543 | -0.3067 | 59.6329 | -0.12817 | -0.022888 | -0.013733 | 0.050354 | -0.004578 | 0.14191 | -0.13275 | 0.16479 | -0.10986 | 0.28381 | 123.0652 | 0.01831 | 123.0743 | 123.2117 | 123.0103 | 123.0331 | 122.9874 | -123.1796 | -123.024 | 122.8867 | 123.0515 | 59.1888 | 59.1797
507.3281 | 123.1384 | -59.642 | 63.3682 | -0.06813 | 0.0037021 | 0.061859 | 0.083785 | -0.00049353 | -0.00096552 | 0.00050193 | -0.033325 | 0.0032962 | 0.063856 | 0.062534 | -0.0070624 | 0.00085247 | -0.0027023 | -0.52185 | 63.3499 | -59.8434 | 63.1897 | -59.6146 | -59.9899 | -0.2243 | -0.54474 | 63.3224 | -59.6878 | 63.3591 | -59.7198 | -59.7015 | -59.5139 | -0.20142 | -0.01831 | -0.17853 | 0.027466 | 59.4177 | -0.3479 | 59.6191 | -0.14648 | -0.045776 | -0.045776 | -0.009155 | -0.07782 | 0.12817 | -0.059509 | 0.17395 | -0.013733 | 0.22888 | 123.0331 | -0.032044 | 123.0469 | 123.1934 | 123.0103 | 122.9919 | 122.9645 | -123.2117 | -123.056 | 122.8317 | 123.0011 | 59.1202 | 59.0973
508.3281 | 123.3582 | -59.6054 | 63.3408 | -0.098648 | 0.0011385 | 0.066131 | 0.080154 | 0.0027109 | 0.00074348 | 0.00092933 | -0.0028075 | 0.0030826 | 0.065352 | 0.064456 | -0.003858 | 0.0029887 | 0.0022109 | -0.46234 | 63.3316 | -59.8068 | 63.3316 | -59.4269 | -59.848 | -0.14648 | -0.42572 | 63.2996 | -59.6466 | 63.5696 | -59.7153 | -59.8251 | -59.3903 | -0.20142 | -0.009155 | -0.009155 | 0.17853 | 59.4589 | -0.24261 | 59.6603 | -0.041198 | -0.041198 | -0.041198 | 0.22888 | -0.10986 | 0.21515 | -0.21973 | 0.25635 | -0.17853 | 0.37994 | 123.1384 | -0.068665 | 123.2162 | 123.1384 | 122.9462 | 122.937 | 122.905 | -123.1476 | -122.9874 | 122.937 | 123.175 | 59.1431 | 59.1797
509.3281 | 123.1338 | -59.5963 | 63.414 | -0.12154 | 0.00049772 | 0.065277 | 0.081435 | 0.0024973 | -0.00075192 | -0.0046249 | -0.057739 | -0.00033537 | 0.063429 | 0.061038 | -0.0030036 | 0.0032023 | -0.0014207 | -0.50812 | 63.4186 | -59.7839 | 63.2812 | -59.5001 | -59.8846 | -0.21973 | -0.53101 | 63.3774 | -59.642 | 63.3865 | -59.6375 | -59.7794 | -59.491 | -0.18768 | 0.004578 | -0.13275 | 0.09613 | 59.3765 | -0.28839 | 59.5642 | -0.10071 | -0.045777 | -0.036621 | -0.027465 | -0.041199 | 0.10529 | -0.18311 | 0.15106 | -0.13733 | 0.28381 | 123.0652 | 0.004578 | 123.0286 | 123.2025 | 123.0194 | 123.0148 | 122.9736 | -123.1979 | -123.056 | 122.8775 | 122.9828 | 59.0881 | 59.0652
510.3281 | 123.1979 | -59.5871 | 63.4323 | -0.12154 | 0.0019931 | 0.064636 | 0.08229 | 0.0022837 | 0.00052988 | -0.00077967 | -0.042481 | 0.0024416 | 0.06407 | 0.067661 | -0.0025764 | 0.0023477 | 0.0011429 | -0.5722 | 63.4598 | -59.7336 | 63.2996 | -59.4818 | -59.8984 | -0.21973 | -0.56763 | 63.4369 | -59.6237 | 63.446 | -59.5825 | -59.7336 | -59.4543 | -0.14648 | 0.027466 | -0.13275 | 0.10529 | 59.3674 | -0.31128 | 59.5139 | -0.16479 | -0.036621 | 0.004578 | 0.013733 | 0.004577 | 0.13275 | -0.14648 | 0.16937 | -0.10986 | 0.25177 | 123.0331 | 0.041198 | 123.0698 | 123.1934 | 123.0606 | 123.0469 | 123.024 | -123.1659 | -123.056 | 122.8867 | 123.0331 | 59.0149 | 59.0195
511.3281 | 123.1705 | -59.5184 | 63.5101 | -0.060501 | 0.00028412 | 0.062927 | 0.083358 | 0.00057467 | -0.00096552 | -0.0014207 | -0.033325 | 0.002228 | 0.064924 | 0.065738 | -0.0049262 | 0.0021341 | 0.00071555 | -0.51727 | 63.4964 | -59.7015 | 63.3957 | -59.3765 | -59.7931 | -0.16022 | -0.49896 | 63.4598 | -59.5642 | 63.4735 | -59.5001 | -59.6924 | -59.4269 | -0.1831 | -0.013733 | -0.11444 | 0.14191 | 59.3582 | -0.27466 | 59.5413 | -0.091553 | -0.045776 | -0.050354 | -0.036621 | 0.018311 | 0.091553 | -0.17395 | 0.13733 | -0.12817 | 0.32501 | 123.0972 | 0.064087 | 123.0377 | 123.1979 | 123.024 | 123.0148 | 122.9782 | -123.2117 | -123.0743 | 122.9141 | 122.9919 | 59.0012 | 59.0195
512.3281 | 123.1522 | -59.4955 | 63.5193 | -0.06813 | 0.00049772 | 0.065918 | 0.083144 | 0.0042063 | 0.0026661 | -0.0014207 | -0.26526 | 0.00116 | 0.061934 | 0.061038 | -0.0064216 | 0.0029887 | 0.0011429 | -0.59967 | 63.5101 | -59.6832 | 63.3408 | -59.404 | -59.8206 | -0.23346 | -0.42572 | 63.4918 | -59.5413 | 63.4918 | -59.4772 | -59.7153 | -59.4131 | -0.18768 | -0.009155 | -0.17853 | 0.091552 | 59.2621 | -0.32501 | 59.4498 | -0.13733 | -0.045777 | -0.027466 | -0.027466 | 0.01831 | 0.082397 | -0.21973 | 0.12817 | -0.17395 | 0.27924 | 123.024 | 0.064087 | 123.0331 | 123.1934 | 123.0331 | 123.0057 | 122.9874 | -123.2025 | -123.0606 | 122.8363 | 122.9874 | 58.8959 | 59.0698
513.3281 | 123.175 | -59.4406 | 63.5788 | -0.12917 | 0.0026339 | 0.063781 | 0.081435 | 0.0010019 | -0.00075192 | -0.00077967 | -0.033325 | 0.00073263 | 0.065992 | 0.065952 | -0.0032172 | 0.0029887 | 0.0028519 | -0.53558 | 63.5925 | -59.6008 | 63.5193 | -59.2529 | -59.6878 | -0.13275 | -0.4715 | 63.5559 | -59.491 | 63.6017 | -59.3719 | -59.5596 | -59.2804 | -0.16022 | 0.013733 | -0.059509 | 0.18768 | 59.3079 | -0.24719 | 59.4681 | -0.086975 | -0.050354 | -0.022888 | 0.022889 | 0.068665 | 0.16022 | -0.11902 | 0.21057 | -0.068664 | 0.3479 | 123.1201 | 0.11902 | 123.0927 | 123.1934 | 123.0469 | 123.0331 | 122.9965 | -123.1796 | -123.0698 | 122.9599 | 123.0423 | 58.905 | 58.9691
514.3281 | 123.1705 | -59.4131 | 63.6154 | -0.091019 | 0.0013523 | 0.064209 | 0.08229 | 0.0010019 | -0.0016065 | -0.00035247 | -0.033325 | 0.0024416 | 0.063002 | 0.05997 | -0.0042854 | 0.0027751 | 0.0015701 | -0.59052 | 63.6337 | -59.5734 | 63.4644 | -59.2758 | -59.7015 | -0.23804 | -0.65002 | 63.5834 | -59.4543 | 63.5788 | -59.4086 | -59.61 | -59.3262 | -0.16022 | 0.018311 | -0.15106 | 0.13733 | 59.1751 | -0.28839 | 59.3353 | -0.12817 | -0.041199 | -0.032043 | -0.036621 | 0.004578 | 0.086975 | -0.19684 | 0.12817 | -0.15564 | 0.29755 | 123.0377 | 0.045777 | 123.0331 | 123.2071 | 123.0377 | 123.0469 | 122.9965 | -123.1888 | -123.0698 | 122.8775 | 122.9919 | 58.8226 | 58.7631
515.3281 | 123.2071 | -59.317 | 63.6841 | -0.014725 | 0.0030613 | 0.063354 | 0.081863 | -0.00070713 | -0.00075192 | -0.0022751 | -0.011963 | 0.0018008 | 0.063643 | 0.063175 | -0.0023626 | 0.0023477 | -0.0020615 | -0.57678 | 63.7207 | -59.5093 | 63.5925 | -59.1385 | -59.5825 | -0.12817 | -0.53101 | 63.6566 | -59.3582 | 63.707 | -59.2575 | -59.4589 | -59.2026 | -0.19226 | 0.036621 | -0.091553 | 0.17853 | 59.1888 | -0.2655 | 59.3811 | -0.073243 | -0.041198 | -0.027466 | 0.022888 | 0.05951 | 0.11444 | -0.14191 | 0.15564 | -0.10071 | 0.37079 | 123.1018 | 0.10071 | 123.0652 | 123.23 | 123.0148 | 123.0377 | 122.9736 | -123.1934 | -123.0423 | 122.9095 | 123.024 | 58.7402 | 58.786
516.3281 | 123.175 | -59.2987 | 63.7436 | -0.052872 | -0.00057028 | 0.063141 | 0.081863 | 0.0037791 | -0.00075192 | 0.0017837 | -0.02417 | 0.0013736 | 0.063429 | 0.061466 | -0.0040716 | 0.0023477 | 0.0034927 | -0.65002 | 63.7619 | -59.4498 | 63.5834 | -59.1568 | -59.5917 | -0.22888 | -0.68665 | 63.7024 | -59.3308 | 63.7299 | -59.23 | -59.4543 | -59.1705 | -0.15106 | 0.018311 | -0.16022 | 0.14191 | 59.0698 | -0.29297 | 59.2209 | -0.14191 | -0.032044 | -0.041198 | -0.013733 | 0.068664 | 0.12817 | -0.15564 | 0.16022 | -0.1236 | 0.29297 | 123.0331 | 0.10071 | 123.0606 | 123.2117 | 123.0331 | 123.0606 | 123.0011 | -123.1934 | -123.0743 | 122.8821 | 123.0286 | 58.6487 | 58.6121
517.3281 | 123.2437 | -59.198 | 63.7756 | -0.06813 | 0.0013523 | 0.065277 | 0.082717 | 0.00014747 | 0.0022387 | -0.0014207 | -0.048584 | -0.00012177 | 0.063002 | 0.059116 | -0.0034308 | 0.0038431 | 0.0028519 | -0.67749 | 63.8077 | -59.404 | 63.6841 | -59.0286 | -59.4818 | -0.22888 | -0.68207 | 63.7665 | -59.2575 | 63.8489 | -59.079 | -59.3079 | -59.0469 | -0.20599 | 0.032043 | -0.091553 | 0.16937 | 58.9691 | -0.28381 | 59.1751 | -0.07782 | -0.059509 | -0.009156 | 0.073242 | 0.11902 | 0.15106 | -0.10986 | 0.21057 | -0.050354 | 0.37537 | 123.0881 | 0.17853 | 123.1064 | 123.2117 | 123.024 | 123.0057 | 122.9645 | -123.1796 | -123.0331 | 122.8821 | 123.0469 | 58.5205 | 58.5159
518.3281 | 123.1567 | -59.1385 | 63.8901 | -0.07576 | 0.0019931 | 0.062927 | 0.082503 | 0.00078827 | -0.0026745 | -0.0014207 | 0.11621 | 0.0037234 | 0.065779 | 0.068302 | -0.0049262 | 0.0012797 | -0.00077965 | -0.70038 | 63.8992 | -59.317 | 63.7482 | -58.9188 | -59.9167 | -0.35248 | -0.83313 | 63.8718 | -59.1751 | 63.858 | -59.0332 | -59.3124 | -59.0195 | -0.17853 | 0.009155 | -0.14191 | 0.21973 | 58.786 | -0.7782 | 58.9645 | -0.59967 | -0.036621 | -0.018311 | -0.032044 | 0.10529 | 0.11902 | -0.17395 | 0.15564 | -0.13733 | 0.39825 | 123.0652 | 0.14191 | 123.0331 | 123.2162 | 123.0469 | 123.0377 | 123.0103 | -123.2071 | -123.0652 | 122.8867 | 122.9965 | 58.4381 | 58.3054
519.3281 | 123.2208 | -59.0012 | 64.0274 | -0.045242 | 0.00049772 | 0.062072 | 0.081008 | -0.0026297 | -0.0031017 | 7.4734e-05 | -0.021118 | 0.0030826 | 0.063643 | 0.058902 | -0.0057806 | 0.0023477 | 0.0024245 | -0.6134 | 64.064 | -59.166 | 63.9084 | -58.7997 | -59.2575 | -0.10986 | -0.60883 | 64.0045 | -59.0332 | 64.0366 | -58.8318 | -59.1339 | -58.8638 | -0.16479 | 0.036621 | -0.11902 | 0.20142 | 58.8913 | -0.25635 | 59.0561 | -0.091552 | -0.032043 | -0.022888 | 0.009155 | 0.16937 | 0.13733 | -0.13275 | 0.16937 | -0.10071 | 0.36621 | 123.0743 | 0.20142 | 123.0698 | 123.23 | 123.0377 | 123.0652 | 123.0057 | -123.1934 | -123.0606 | 122.9095 | 123.0377 | 58.3878 | 58.3923
520.3281 | 123.1476 | -58.9142 | 64.1098 | -0.098648 | 0.0019931 | 0.06485 | 0.083785 | 0.00078827 | -0.0018201 | 0.0045609 | -0.045532 | 0.00051903 | 0.064924 | 0.063816 | -0.0059942 | 0.0051249 | -0.0027023 | -0.70038 | 64.1327 | -59.111 | 63.9496 | -58.7585 | -59.2392 | -0.21973 | -0.78278 | 64.0915 | -58.9691 | 64.0594 | -58.8135 | -59.1202 | -58.8409 | -0.19684 | 0.022888 | -0.16022 | 0.15564 | 58.6945 | -0.32501 | 58.8913 | -0.12817 | -0.054931 | -0.01831 | -0.050354 | 0.10071 | 0.073243 | -0.20599 | 0.12817 | -0.15106 | 0.35248 | 123.0606 | 0.15564 | 123.0286 | 123.2437 | 123.0606 | 123.0469 | 123.0057 | -123.2208 | -123.0789 | 122.8638 | 122.9736 | 58.2138 | 58.1314
521.3281 | 123.2208 | -58.7631 | 64.2426 | -0.037613 | 0.0019931 | 0.062072 | 0.081863 | 0.0010019 | -0.0011791 | -0.0031297 | -0.057739 | -0.00054897 | 0.064283 | 0.066379 | -0.0051398 | 0.0023477 | 0.0026383 | -0.62714 | 64.2426 | -58.9462 | 64.1602 | -58.4793 | -59.0195 | -0.14191 | -0.62256 | 64.1922 | -58.8089 | 64.2746 | -58.5434 | -58.9142 | -58.6578 | -0.1831 | 0 | -0.082398 | 0.28381 | 58.6212 | -0.25635 | 58.8043 | -0.073242 | -0.045776 | -0.050354 | 0.032043 | 0.21973 | 0.10529 | -0.15106 | 0.15106 | -0.10529 | 0.46692 | 123.1064 | 0.2655 | 123.0835 | 123.1888 | 123.0011 | 123.0057 | 122.9553 | -123.1888 | -123.0515 | 122.9233 | 123.0377 | 58.136 | 58.1406
522.3438 | 123.2162 | -58.5938 | 64.3433 | -0.037613 | 0.00071132 | 0.062927 | 0.079726 | 0.0010019 | -0.00032472 | -0.0022751 | 0.076538 | -0.00054897 | 0.064283 | 0.060611 | -0.004499 | 0.00042507 | 0.00071555 | -0.63171 | 64.3524 | -58.7631 | 64.3662 | -58.2321 | -58.7402 | 0 | -0.50812 | 64.3204 | -58.6304 | 64.2609 | -57.93 | -58.5571 | -58.5159 | -0.16937 | 0.009155 | 0.022888 | 0.36163 | 58.5938 | -0.14648 | 58.7631 | 0.022889 | -0.036621 | -0.022888 | -0.082398 | 0.66376 | 0.07782 | 0.036621 | 0.11444 | 0.073242 | 0.53101 | 123.1293 | 0.70038 | 122.8912 | 123.1155 | 122.9507 | 122.9462 | 122.9141 | -123.1064 | -122.9736 | 122.9599 | 122.8546 | 57.962 | 58.0856
523.3281 | 123.2391 | -58.4976 | 64.5355 | -0.029984 | 0.0028475 | 0.06485 | 0.083144 | 0.0059153 | -0.00032472 | -0.0037705 | -0.033325 | 0.0020144 | 0.066206 | 0.066165 | -0.0064216 | 0.0025613 | -0.00056605 | -0.65002 | 64.5401 | -58.6487 | 64.4485 | -58.1818 | -58.7128 | -0.12817 | -0.63171 | 64.5126 | -58.5114 | 64.5676 | -58.1909 | -58.5938 | -58.3466 | -0.15106 | 0.004578 | -0.086975 | 0.31586 | 58.3694 | -0.21515 | 58.5205 | -0.064087 | -0.013733 | -0.022888 | 0.032044 | 0.3067 | 0.15106 | -0.09613 | 0.16479 | -0.082397 | 0.46692 | 123.0972 | 0.32043 | 123.0789 | 123.1888 | 123.024 | 123.0377 | 123.0103 | -123.1842 | -123.0469 | 122.9462 | 123.0652 | 57.8476 | 57.8659
524.3281 | 123.1979 | -58.3328 | 64.7141 | -0.083389 | 0.0037021 | 0.065277 | 0.081222 | 0.0035653 | 0.00095708 | 0.00028833 | -0.045532 | 0.002228 | 0.064711 | 0.068302 | -0.003858 | 0.0040567 | -0.0012071 | -0.71869 | 64.682 | -58.5159 | 64.5859 | -58.0536 | -58.6166 | -0.18768 | -0.74616 | 64.6729 | -58.3786 | 64.6729 | -58.0811 | -58.5022 | -58.2321 | -0.1831 | -0.032043 | -0.12817 | 0.27924 | 58.1451 | -0.28381 | 58.3282 | -0.10071 | -0.045776 | -0.041198 | -0.041198 | 0.25177 | 0.10071 | -0.16937 | 0.14648 | -0.1236 | 0.46234 | 123.1018 | 0.29755 | 123.0515 | 123.1979 | 123.0515 | 123.0148 | 123.0057 | -123.23 | -123.0927 | 122.9187 | 123.0057 | 57.6141 | 57.5867
525.3281 | 123.2254 | -58.136 | 64.856 | -0.052872 | 0.0015659 | 0.062286 | 0.084212 | 0.0016427 | -0.0041699 | 0.0026383 | -0.02417 | 0.002228 | 0.066206 | 0.056339 | -0.00279 | 0.0019205 | -0.00056605 | -0.6958 | 64.8972 | -58.3008 | 64.769 | -57.8018 | -58.3649 | -0.10529 | -0.65002 | 64.8605 | -58.1818 | 64.9017 | -57.7835 | -58.2321 | -57.9895 | -0.16479 | 0.041199 | -0.086975 | 0.33417 | 58.0307 | -0.22888 | 58.1955 | -0.064087 | -0.045777 | 0.004578 | 0.045776 | 0.35248 | 0.14648 | -0.096131 | 0.19226 | -0.050354 | 0.49896 | 123.0698 | 0.39825 | 123.0835 | 123.1979 | 123.0423 | 123.0331 | 122.9965 | -123.1567 | -123.0377 | 122.905 | 123.0377 | 57.4402 | 57.486
526.3281 | 123.143 | -57.9849 | 65.0482 | -0.045242 | 0.0013523 | 0.06485 | 0.081863 | 0.00014747 | -0.0033155 | -0.00035247 | -0.042481 | 0.0041506 | 0.063856 | 0.065097 | -0.0047126 | 0.0040567 | -0.0014207 | -0.76446 | 65.0528 | -58.1497 | 64.9063 | -57.6645 | -58.2687 | -0.2243 | -0.83313 | 65.0391 | -57.9895 | 64.9979 | -57.6782 | -58.1726 | -57.8842 | -0.16479 | 0.004577 | -0.14191 | 0.32043 | 57.7606 | -0.28381 | 57.9254 | -0.11902 | -0.004578 | -0.009156 | -0.050354 | 0.3067 | 0.10071 | -0.18768 | 0.10529 | -0.1831 | 0.48523 | 123.056 | 0.31128 | 122.9874 | 123.2025 | 123.0286 | 123.0377 | 123.024 | -123.1979 | -123.0377 | 122.8912 | 122.9828 | 57.2205 | 57.1518
527.3438 | 123.23 | -57.7652 | 65.2496 | -0.10628 | 0.00028412 | 0.064422 | 0.082076 | 0.0046335 | -0.00075192 | 0.00071573 | -0.021118 | 0.0020144 | 0.065138 | 0.062534 | -0.00279 | 0.0021341 | -0.0020615 | -0.80109 | 65.2313 | -57.9437 | 65.1123 | -57.4265 | -58.0582 | -0.23804 | -0.8194 | 65.213 | -57.8247 | 65.2542 | -57.3669 | -57.9025 | -57.6279 | -0.17853 | -0.018311 | -0.13733 | 0.33874 | 57.5272 | -0.29297 | 57.7057 | -0.11444 | -0.059509 | -0.036621 | 0.004577 | 0.39825 | 0.13733 | -0.13733 | 0.19684 | -0.07782 | 0.51727 | 123.056 | 0.45776 | 123.0789 | 123.175 | 123.0377 | 122.9965 | 122.9782 | -123.1934 | -123.0743 | 122.8775 | 123.0194 | 56.9641 | 56.9458
528.3281 | 123.143 | -57.55 | 65.4602 | -0.14442 | 0.0032749 | 0.063568 | 0.083144 | 0.0031381 | 0.0028797 | -0.0029159 | -0.19202 | 0.00094643 | 0.063856 | 0.062534 | -0.0040716 | 0.0034159 | 0.0019973 | -0.81482 | 65.4648 | -57.7744 | 65.2817 | -57.2433 | -57.8842 | -0.23346 | -0.6134 | 65.3961 | -57.605 | 65.4282 | -57.1426 | -57.7744 | -57.4814 | -0.2243 | 0.004578 | -0.17853 | 0.3067 | 57.3166 | -0.33417 | 57.5409 | -0.10986 | -0.054931 | -0.064087 | -0.032043 | 0.40741 | 0.068665 | -0.2243 | 0.1236 | -0.16937 | 0.53101 | 123.056 | 0.46234 | 123.0331 | 123.2391 | 123.0011 | 123.0148 | 122.9462 | -123.2346 | -123.0652 | 122.8317 | 122.9782 | 56.7352 | 56.9366
529.3281 | 123.2483 | -57.3303 | 65.657 | -0.098648 | 0.00092492 | 0.06485 | 0.082717 | 0.0031381 | 0.00010248 | 0.00050193 | -0.027222 | 0.00073263 | 0.061293 | 0.073856 | -0.0034308 | 0.0010661 | 0.0026383 | -0.71869 | 65.6891 | -57.4997 | 65.5975 | -56.8954 | -57.5821 | -0.13733 | -0.68207 | 65.657 | -57.3532 | 65.7074 | -56.8542 | -57.5409 | -57.3257 | -0.16937 | 0.032044 | -0.059509 | 0.43488 | 57.193 | -0.25177 | 57.3624 | -0.082397 | -0.022888 | 0 | 0.050354 | 0.47607 | 0.004577 | -0.21057 | 0.027465 | -0.18768 | 0.60425 | 123.0972 | 0.49896 | 123.0606 | 123.1888 | 123.0103 | 123.0194 | 122.9874 | -123.1567 | -123.0103 | 122.9279 | 123.0377 | 56.6116 | 56.6483
530.3281 | 123.1842 | -57.1518 | 65.8859 | -0.07576 | -0.00057028 | 0.065277 | 0.082931 | 0.00036107 | 0.00074348 | 0.0015701 | -0.036377 | 0.0026552 | 0.064924 | 0.063816 | -0.0059942 | 0.0025613 | 0.0013565 | -0.75989 | 65.8813 | -57.3166 | 65.7623 | -56.7078 | -57.4173 | -0.2243 | -0.81482 | 65.8768 | -57.1518 | 65.8585 | -56.6528 | -57.3074 | -57.0465 | -0.16479 | -0.004577 | -0.1236 | 0.44403 | 56.9275 | -0.2655 | 57.0923 | -0.10071 | 0 | -0.009155 | -0.027466 | 0.49896 | 0.10529 | -0.15564 | 0.10529 | -0.15564 | 0.60883 | 123.0789 | 0.49896 | 123.0103 | 123.1979 | 123.0286 | 123.0331 | 123.0286 | -123.2025 | -123.0377 | 122.9141 | 123.0103 | 56.3919 | 56.337
531.3281 | 123.2071 | -56.781 | 66.2247 | 0.00053424 | 0.0011385 | 0.062927 | 0.084853 | 0.0018565 | -0.00053832 | -0.0014207 | -0.030273 | -0.0018308 | 0.065138 | 0.063175 | -0.0047126 | 0.0040567 | 0.0015701 | -0.72784 | 66.2384 | -56.9733 | 66.1514 | -56.2958 | -57.0374 | -0.15564 | -0.69122 | 66.1789 | -56.813 | 66.243 | -56.1768 | -56.8909 | -56.662 | -0.19226 | 0.013733 | -0.073242 | 0.48523 | 56.6254 | -0.25635 | 56.8176 | -0.064087 | -0.032043 | -0.045776 | 0.018311 | 0.60425 | 0.11902 | -0.10986 | 0.15106 | -0.07782 | 0.67749 | 123.1247 | 0.63629 | 123.056 | 123.2117 | 122.9919 | 123.0194 | 122.9599 | -123.1979 | -123.0377 | 122.9324 | 123.024 | 56.0532 | 56.0898
532.3438 | 123.2117 | -56.4651 | 66.5222 | -0.091019 | 0.00049772 | 0.063568 | 0.082503 | -0.00049353 | -0.0013929 | -0.0024887 | -0.036377 | -0.00054897 | 0.064924 | 0.06232 | -0.003858 | 0.0034159 | -0.00056605 | -0.76904 | 66.4993 | -56.6345 | 66.4444 | -55.9341 | -56.6116 | -0.14648 | -0.75073 | 66.4764 | -56.5292 | 66.5405 | -55.7968 | -56.543 | -56.337 | -0.16937 | -0.022888 | -0.07782 | 0.53101 | 56.3187 | -0.14648 | 56.488 | 0.022888 | -0.064087 | -0.045777 | 0.01831 | 0.66833 | 0.12817 | -0.07782 | 0.19226 | -0.013733 | 0.70038 | 123.0789 | 0.73242 | 123.0698 | 123.1338 | 123.0057 | 122.9645 | 122.9416 | -123.1567 | -123.0515 | 122.9095 | 123.0057 | 55.6961 | 55.7144
533.3281 | 123.1888 | -56.0211 | 67.0074 | -0.0070953 | 0.00092492 | 0.064209 | 0.08229 | -0.00070713 | -0.0016065 | -0.0041977 | -0.02417 | 0.00116 | 0.064924 | 0.065952 | -0.0057806 | 0.0021341 | -0.00077965 | -0.75989 | 66.9983 | -56.2134 | 66.8701 | -55.4855 | -56.2637 | -0.1831 | -0.75531 | 66.9891 | -56.0577 | 66.98 | -55.2658 | -56.1447 | -55.9113 | -0.19226 | -0.009155 | -0.13733 | 0.53558 | 55.838 | -0.24262 | 56.0303 | -0.050354 | -0.036621 | -0.01831 | -0.027466 | 0.75531 | 0.10986 | -0.1236 | 0.14648 | -0.086975 | 0.72784 | 123.0835 | 0.79193 | 123.0377 | 123.2117 | 123.0469 | 123.0194 | 123.0103 | -123.2208 | -123.0652 | 122.8912 | 123.0011 | 55.2612 | 55.2658
534.3281 | 123.1705 | -55.5542 | 67.4698 | -0.060501 | 0.0015659 | 0.061645 | 0.084853 | 0.0048471 | -0.00032472 | -0.00056607 | -0.057739 | -0.00076257 | 0.064283 | 0.06467 | -0.004499 | 0.0025613 | 0.00028835 | -0.75989 | 67.4881 | -55.7144 | 67.3325 | -54.9316 | -55.806 | -0.22888 | -0.76904 | 67.4377 | -55.5862 | 67.4561 | -54.6661 | -55.7098 | -55.4672 | -0.16022 | 0.01831 | -0.13733 | 0.62256 | 55.3253 | -0.25177 | 55.4855 | -0.091552 | -0.032044 | -0.032044 | -0.013733 | 0.88806 | 0.086975 | -0.15564 | 0.11902 | -0.1236 | 0.78278 | 123.0469 | 0.92011 | 123.0423 | 123.2025 | 123.024 | 123.0423 | 122.9919 | -123.1842 | -123.056 | 122.8867 | 123.0103 | 54.7943 | 54.7852
535.3281 | 123.1934 | -54.9683 | 68.0557 | -0.060501 | 0.0028475 | 0.065063 | 0.085494 | 0.0037791 | -0.0037427 | -0.0016343 | -0.036377 | 0.00116 | 0.063429 | 0.062107 | -0.0042854 | 0.0036295 | -0.0037705 | -0.72784 | 68.0649 | -55.1422 | 67.9871 | -54.2999 | -55.1926 | -0.16479 | -0.67749 | 68.0191 | -55.0095 | 68.0786 | -53.9383 | -55.0781 | -54.8584 | -0.17395 | 0.009155 | -0.068664 | 0.66834 | 54.8035 | -0.2243 | 54.9774 | -0.050354 | -0.041198 | -0.036621 | 0.022888 | 1.03 | 0.10986 | -0.10986 | 0.15106 | -0.068665 | 0.84229 | 123.1293 | 1.0712 | 123.0881 | 123.2071 | 123.0286 | 123.0331 | 122.9874 | -123.1979 | -123.0652 | 122.9553 | 123.0469 | 54.2404 | 54.2908
536.3281 | 123.1888 | -54.3365 | 68.6874 | -0.48775 | 0.0011385 | 0.061004 | 0.082503 | 0.00014747 | -0.00053832 | -0.0031297 | -0.045532 | 0.0015872 | 0.063856 | 0.06232 | -0.0034308 | 0.0040567 | -0.00056605 | -0.78278 | 68.6737 | -54.538 | 68.5089 | -53.6224 | -54.6524 | -0.28839 | -0.83313 | 68.6691 | -54.3869 | 68.66 | -53.1967 | -54.4968 | -54.245 | -0.20142 | -0.013733 | -0.17853 | 0.71411 | 54.0482 | -0.31586 | 54.2496 | -0.11444 | -0.050354 | -0.018311 | -0.027466 | 1.1398 | 0.091553 | -0.16022 | 0.14191 | -0.10986 | 0.91553 | 123.0469 | 1.1902 | 123.0469 | 123.2117 | 123.056 | 123.0103 | 123.0057 | -123.2254 | -123.0743 | 122.8455 | 122.9965 | 53.5538 | 53.5034
537.3281 | 123.2758 | -53.5675 | 69.4016 | -0.11391 | 7.0518e-05 | 0.0625 | 0.081008 | -0.0047659 | 0.00010248 | -0.0014207 | 0.02771 | 0.00073263 | 0.063643 | 0.060825 | -0.0032172 | 0.0027751 | 0.00028835 | -0.76446 | 69.4702 | -53.6728 | 69.3878 | -52.6703 | -53.7186 | -0.19226 | -0.70496 | 69.4565 | -53.5446 | 69.4611 | -52.1942 | -53.6636 | -53.4348 | -0.10529 | 0.068665 | -0.013733 | 0.89722 | 53.3752 | -0.15106 | 53.4805 | -0.045776 | 0.022888 | 0.054932 | 0.05951 | 1.3733 | 0.13275 | -0.09613 | 0.10986 | -0.11902 | 1.0025 | 123.0606 | 1.3504 | 123.0057 | 123.143 | 123.0011 | 123.0377 | 123.024 | -123.0743 | -122.9462 | 122.9553 | 123.0286 | 52.803 | 52.8625
538.3281 | 123.1338 | -52.9953 | 70.0562 | -0.083389 | 0.0013523 | 0.062713 | 0.082076 | 0.0029245 | -0.00032472 | -0.0012071 | -0.057739 | -0.00012177 | 0.064711 | 0.064243 | -0.0049262 | 0.0023477 | -0.0035569 | -0.78735 | 70.0378 | -53.1555 | 69.8776 | -52.1301 | -53.2837 | -0.27924 | -0.82398 | 70.0195 | -53.0411 | 69.9875 | -51.5854 | -53.1876 | -52.9175 | -0.16022 | -0.01831 | -0.17853 | 0.86517 | 52.7161 | -0.28839 | 52.8763 | -0.12817 | -0.045777 | -0.036621 | -0.068664 | 1.4099 | 0.07782 | -0.19226 | 0.1236 | -0.14648 | 1.0254 | 123.0331 | 1.4557 | 123.0286 | 123.1934 | 123.0606 | 123.0331 | 123.0148 | -123.2117 | -123.0972 | 122.8729 | 122.9828 | 52.2079 | 52.1713
539.3281 | 123.1796 | -52.2171 | 70.7657 | -0.10628 | 0.0011385 | 0.064209 | 0.081649 | 0.0016427 | 0.00010248 | -0.0039841 | -0.039429 | 0.0024416 | 0.065138 | 0.065952 | -0.0051398 | 0.0032023 | -0.0041977 | -0.737 | 70.7932 | -52.4048 | 70.697 | -51.178 | -52.4506 | -0.20142 | -0.76446 | 70.784 | -52.272 | 70.816 | -50.5417 | -52.327 | -52.121 | -0.18768 | 0.027466 | -0.068665 | 1.0391 | 52.0157 | -0.23346 | 52.2034 | -0.045777 | -0.054932 | 0.018311 | 0.050354 | 1.6754 | 0.09613 | -0.10986 | 0.15106 | -0.054931 | 1.2268 | 123.1018 | 1.7303 | 123.0881 | 123.1979 | 123.056 | 123.0103 | 123.0011 | -123.1705 | -123.0377 | 122.9141 | 123.0331 | 51.4801 | 51.4526
540.3281 | 123.175 | -51.4389 | 71.5668 | -0.060501 | 0.0015659 | 0.06485 | 0.083144 | -0.0019889 | 0.00074348 | -0.0014207 | -0.051636 | 0.0037234 | 0.065992 | 0.065097 | -0.0023626 | 0.0032023 | -0.0012071 | -0.74158 | 71.6171 | -51.5671 | 71.4844 | -50.3174 | -51.6769 | -0.23804 | -0.70496 | 71.5759 | -51.4801 | 71.5668 | -49.6307 | -51.5854 | -51.3474 | -0.12817 | 0.050354 | -0.082397 | 1.1215 | 51.2009 | -0.23804 | 51.329 | -0.10986 | -0.041199 | 0.009156 | 0 | 1.8082 | 0.091553 | -0.14648 | 0.13275 | -0.10529 | 1.2497 | 123.0515 | 1.8494 | 123.0469 | 123.1842 | 123.056 | 123.056 | 123.0148 | -123.1338 | -123.0469 | 122.9233 | 123.0057 | 50.6973 | 50.7339
541.3281 | 123.2437 | -50.9674 | 72.0657 | -0.07576 | 0.0022067 | 0.063781 | 0.083999 | -0.0019889 | -0.0037427 | 0.00071573 | -0.042481 | -0.00076257 | 0.065565 | 0.06467 | 0.00020083 | 0.0042703 | 0.0017837 | -0.76446 | 72.0612 | -51.1185 | 71.9559 | -49.704 | -51.1688 | -0.21973 | -0.67749 | 72.0245 | -50.9903 | 72.0016 | -49.0677 | -51.1093 | -50.8804 | -0.15106 | -0.004578 | -0.10986 | 1.2634 | 50.7477 | -0.20142 | 50.8987 | -0.050354 | -0.022888 | -0.041199 | -0.064087 | 1.8997 | 0.086975 | -0.14191 | 0.10986 | -0.11902 | 1.4145 | 123.0743 | 1.9226 | 122.9919 | 123.1796 | 123.0148 | 123.0286 | 122.9919 | -123.1842 | -123.056 | 122.9233 | 122.9691 | 50.2029 | 50.2899
542.3281 | 123.1293 | -50.2853 | 72.7707 | -0.10628 | 0.00092492 | 0.065277 | 0.083144 | 0.0037791 | -0.0016065 | 0.0015701 | -0.066895 | 0.0015872 | 0.067701 | 0.054416 | -0.0034308 | 0.0032023 | 0.0028519 | -0.83313 | 72.7707 | -50.4822 | 72.551 | -49.1226 | -50.6058 | -0.29297 | -0.81024 | 72.7066 | -50.3586 | 72.6013 | -48.2162 | -50.473 | -50.2396 | -0.19684 | 0 | -0.21973 | 1.1627 | 49.9924 | -0.32043 | 50.1892 | -0.1236 | -0.073243 | -0.064087 | -0.16937 | 2.0691 | 0.045776 | -0.18768 | 0.11902 | -0.11444 | 1.3596 | 123.0331 | 2.1423 | 122.9599 | 123.2529 | 123.0652 | 123.056 | 122.9919 | -123.2529 | -123.1293 | 122.8363 | 122.8867 | 49.4522 | 49.4751
543.3281 | 123.1888 | -49.4843 | 73.5352 | -0.037613 | 0.0026339 | 0.064636 | 0.080367 | 0.0037791 | -0.0026745 | 0.00071573 | -0.042481 | 0.00051903 | 0.066206 | 0.064884 | -0.0040716 | 0.0038431 | 0.00028835 | -0.74616 | 73.5764 | -49.6262 | 73.4344 | -47.9324 | -49.7223 | -0.21973 | -0.69122 | 73.494 | -49.5209 | 73.5397 | -47.2366 | -49.6262 | -49.379 | -0.14191 | 0.041199 | -0.10071 | 1.5518 | 49.2645 | -0.23804 | 49.4064 | -0.09613 | -0.036621 | -0.041198 | 0.004578 | 2.2476 | 0.10529 | -0.14191 | 0.14191 | -0.10529 | 1.6937 | 123.0606 | 2.2842 | 123.0606 | 123.2025 | 123.0148 | 123.0606 | 122.9782 | -123.1613 | -123.056 | 122.9187 | 123.024 | 48.7381 | 48.793
544.3281 | 123.175 | -49.7269 | 73.2834 | -0.07576 | 0.00071132 | 0.064209 | 0.083144 | 0.0010019 | -0.0035291 | 7.4734e-05 | -0.021118 | 0.0018008 | 0.066206 | 0.066165 | -0.0049262 | 0.0040567 | -0.0031297 | -0.82855 | 73.3154 | -49.91 | 73.1003 | -48.1293 | -50.0336 | -0.27924 | -0.8194 | 73.2605 | -49.7864 | 73.2697 | -47.8043 | -49.8825 | -49.6445 | -0.1831 | 0.032044 | -0.1831 | 1.5976 | 49.4476 | -0.3067 | 49.6307 | -0.1236 | -0.059509 | -0.022888 | -0.013733 | 1.9226 | 0.082398 | -0.15564 | 0.14191 | -0.09613 | 1.7807 | 123.0103 | 1.9821 | 123.056 | 123.2254 | 123.0469 | 123.0423 | 122.9874 | -123.1934 | -123.0698 | 122.8271 | 122.9965 | 48.8983 | 48.9075
545.3281 | 123.1934 | -47.2778 | 75.7828 | -0.091019 | 0.00049772 | 0.065063 | 0.083999 | 0.00057467 | 0.00074348 | 0.00092933 | -0.036377 | 0.0013736 | 0.067061 | 0.063602 | -0.004499 | 0.0012797 | 0.0026383 | -0.79651 | 75.7095 | -47.4884 | 75.6042 | -45.5658 | -47.5159 | -0.17853 | -0.68207 | 75.6866 | -47.3373 | 75.7645 | -44.7739 | -47.3923 | -47.1451 | -0.21057 | -0.073242 | -0.17853 | 1.712 | 47.0993 | -0.23804 | 47.3099 | -0.027466 | -0.059509 | -0.09613 | -0.018311 | 2.504 | 0.13275 | -0.11444 | 0.19226 | -0.054932 | 1.9226 | 123.0927 | 2.5635 | 123.1018 | 123.1979 | 123.024 | 122.9874 | 122.9645 | -123.2712 | -123.1201 | 122.8821 | 123.0423 | 46.4813 | 46.5958
546.3281 | 123.1155 | -46.2204 | 76.8082 | -0.060501 | 0.00071132 | 0.06549 | 0.08229 | 0.00014747 | -0.00032472 | -0.0018479 | -0.027222 | 0.00051903 | 0.067488 | 0.059757 | -0.0034308 | 0.0042703 | -0.0027023 | -0.87433 | 76.8082 | -46.3852 | 76.6388 | -44.1422 | -46.4355 | -0.27008 | -0.85602 | 76.7853 | -46.2891 | 76.7487 | -43.5974 | -46.3852 | -46.1655 | -0.16479 | 0 | -0.16937 | 2.0782 | 45.9503 | -0.21515 | 46.1151 | -0.050354 | -0.068664 | -0.022889 | -0.05951 | 2.623 | 0.054932 | -0.16479 | 0.1236 | -0.096131 | 2.243 | 123.024 | 2.6917 | 123.0377 | 123.1934 | 123.0743 | 123.0286 | 123.0057 | -123.1934 | -123.0972 | 122.8592 | 122.9691 | 45.3461 | 45.3644
547.3281 | 123.1842 | -46.4493 | 76.5747 | -0.07576 | 0.0045565 | 0.066345 | 0.082717 | 0.00057467 | 0.0013843 | -0.0014207 | -0.030273 | 0.00051903 | 0.063856 | 0.059116 | -0.0047126 | 0.0032023 | -0.0052659 | -0.8606 | 76.7715 | -46.431 | 76.7258 | -43.7347 | -46.3989 | -0.16937 | -0.74616 | 76.6754 | -46.3669 | 76.6068 | -43.4189 | -46.5134 | -46.3165 | 0.018311 | 0.19684 | 0.15106 | 2.7145 | 46.2799 | 0.050354 | 46.2616 | 0.032043 | 0.082398 | 0.10071 | 0.032043 | 3.0304 | 0.13275 | -0.064087 | 0.050354 | -0.14649 | 2.6962 | 123.1567 | 2.948 | 122.9736 | 123.2025 | 123.0423 | 123.2208 | 123.1247 | -123.0057 | -122.9416 | 123.175 | 123.056 | 45.5887 | 45.7031
548.3281 | 123.0469 | -31.4804 | 91.6718 | -0.045242 | 0.0037021 | 0.068268 | 0.083785 | 0.0012155 | -0.00096552 | 0.0013565 | -0.045532 | 0.0018008 | 0.066633 | 0.06702 | -0.0036444 | 0.0038431 | -0.0037705 | -0.737 | 91.5436 | -31.6681 | 91.1819 | -22.1741 | -31.8375 | 0.064087 | -0.64087 | 91.4474 | -31.6269 | 91.4566 | -29.4434 | -31.7139 | -31.4484 | -0.18768 | -0.12817 | -0.48981 | 9.3063 | 31.5445 | -0.35705 | 31.7322 | -0.16937 | -0.14648 | -0.2243 | -0.21515 | 2.037 | 0.032044 | -0.23346 | 0.17853 | -0.086975 | 9.494 | 122.85 | 2.1835 | 123.0835 | 123.2117 | 123.0743 | 123.024 | 122.9279 | -123.3398 | -123.2986 | 122.6624 | 122.937 | 30.7434 | 30.8395
549.3281 | 122.9233 | -22.1924 | 100.914 | -0.060501 | 0.00049772 | 0.068908 | 0.081008 | -0.00027993 | -0.0024609 | 0.00050193 | -0.048584 | 0.0015872 | 0.063856 | 0.060184 | -0.0023626 | 0.0023477 | 0.0013565 | -0.49896 | 100.8911 | -22.316 | 100.6577 | -6.2714 | -22.3663 | 0.35706 | -0.42114 | 100.8636 | -22.2244 | 100.8316 | -20.6406 | -22.3572 | -22.2153 | -0.1236 | -0.022888 | -0.25635 | 15.921 | 22.5494 | -0.17395 | 22.673 | -0.050354 | -0.032043 | -0.050354 | -0.082397 | 1.5518 | -0.022888 | -0.1648 | 0.009155 | -0.13275 | 16.0446 | 122.9736 | 1.5839 | 123.056 | 123.2071 | 123.0881 | 123.0835 | 123.056 | -123.23 | -123.1384 | 122.85 | 123.024 | 21.6934 | 21.7712
550.3281 | 123.143 | -25.4654 | 97.5769 | -0.098648 | 0.0011385 | 0.070404 | 0.084212 | -0.0026297 | 0.0015979 | -0.00099327 | -0.079102 | 0.0020144 | 0.066847 | 0.058689 | -0.0032172 | 0.0038431 | -0.0024887 | -0.59509 | 97.6456 | -25.6256 | 97.3434 | -11.9659 | -25.4929 | 0.44861 | -0.46692 | 97.5998 | -25.5203 | 97.522 | -23.5886 | -25.6943 | -25.4929 | -0.16022 | 0.068665 | -0.23346 | 13.4995 | 25.914 | -0.027466 | 26.0742 | 0.13275 | -0.054932 | 0.022888 | -0.054931 | 1.8768 | -0.027466 | -0.22888 | 0.027466 | -0.17395 | 13.6597 | 122.9691 | 1.9318 | 123.0423 | 123.2712 | 123.1201 | 123.111 | 123.0652 | -123.2025 | -123.0972 | 122.8088 | 122.9874 | 24.8703 | 24.9985
551.3281 | 123.175 | -24.2889 | 98.7991 | -0.12917 | 0.0028475 | 0.071472 | 0.085494 | -0.00092073 | 0.00074348 | 7.4734e-05 | -0.030273 | 0.0024416 | 0.067061 | 0.068515 | -0.0059942 | 0.0038431 | -0.0024887 | -0.52185 | 98.7854 | -24.4354 | 98.5931 | -8.6838 | -24.5636 | 0.33875 | -0.49439 | 98.7396 | -24.3851 | 98.7122 | -22.348 | -24.4766 | -24.321 | -0.14648 | -0.013733 | -0.20599 | 15.6052 | 24.6277 | -0.27466 | 24.7742 | -0.12817 | -0.096131 | -0.059509 | -0.086975 | 1.9409 | -0.032044 | -0.18768 | 0.064087 | -0.091553 | 15.7516 | 123.0286 | 2.037 | 123.0972 | 123.2208 | 123.1247 | 123.0743 | 123.0286 | -123.2346 | -123.1842 | 122.8821 | 123.0011 | 23.7671 | 23.7946
552.3281 | 123.1613 | -23.9365 | 99.1196 | -0.060501 | 0.00092492 | 0.073395 | 0.085067 | 0.0022837 | 0.00031608 | 0.00092933 | -0.021118 | 0.0013736 | 0.066633 | 0.060398 | -0.0049262 | 0.0012797 | 0.0026383 | -0.58594 | 99.147 | -24.1058 | 98.8815 | -7.3059 | -24.2477 | 0.34332 | -0.56305 | 99.0875 | -24.0234 | 99.0509 | -21.9589 | -24.1333 | -24.0143 | -0.16937 | 0.027466 | -0.23804 | 16.6306 | 24.2798 | -0.31128 | 24.4492 | -0.14191 | -0.086975 | -0.032044 | -0.068665 | 1.9775 | -0.07782 | -0.19684 | 0.009155 | -0.10986 | 16.7999 | 122.9874 | 2.0645 | 123.0743 | 123.2529 | 123.111 | 123.0835 | 123.024 | -123.2254 | -123.143 | 122.818 | 122.9874 | 23.3505 | 23.3734
553.3281 | 123.1567 | -23.0621 | 100.0122 | -0.052872 | 0.0022067 | 0.072967 | 0.084426 | -6.6126e-05 | 0.0013843 | -0.0035569 | -0.030273 | 0.00073263 | 0.067061 | 0.063816 | -0.0042854 | 0.0023477 | -0.0024887 | -0.53101 | 99.9298 | -23.259 | 99.7833 | -6.9626 | -22.9385 | 0.38452 | -0.4715 | 99.939 | -23.1491 | 99.9939 | -21.0526 | -23.2132 | -23.1354 | -0.19684 | -0.082397 | -0.22888 | 16.0995 | 23.4467 | 0.1236 | 23.6435 | 0.32043 | -0.086975 | -0.073242 | -0.018311 | 2.0096 | -0.073242 | -0.15106 | 0.013733 | -0.064087 | 16.2964 | 123.0423 | 2.0966 | 123.143 | 123.1888 | 123.0881 | 122.9919 | 123.0011 | -123.2712 | -123.1613 | 122.8455 | 123.056 | 22.5311 | 22.5906
554.3281 | 123.0743 | -23.1445 | 99.9298 | -0.052872 | 0.0024203 | 0.071686 | 0.084853 | 0.0027109 | 0.00052988 | -0.0020615 | -0.02417 | 0.0018008 | 0.067061 | 0.064456 | -0.0053534 | 0.0042703 | 0.0013565 | -0.61798 | 99.9756 | -23.2681 | 99.6689 | -9.2377 | -23.4695 | 0.2655 | -0.63171 | 99.9298 | -23.204 | 99.7833 | -21.254 | -23.0896 | -23.0759 | -0.1236 | 0.045776 | -0.26093 | 13.9069 | 23.41 | -0.32501 | 23.5336 | -0.20142 | -0.05951 | 0 | -0.14648 | 1.8906 | 0.068664 | 0.054931 | 0.12817 | 0.11444 | 14.0305 | 122.937 | 1.9501 | 122.9874 | 123.2437 | 123.1339 | 123.1201 | 123.0743 | -123.1979 | -123.1339 | 122.8134 | 122.9279 | 22.5266 | 22.5128
555.3281 | 123.1705 | -23.1995 | 99.8474 | -0.014725 | 0.0019931 | 0.07254 | 0.082931 | 0.0033517 | 0.0028797 | -0.00099327 | -0.030273 | 0.0030826 | 0.065779 | 0.065738 | -0.0040716 | 0.0057657 | -0.00099325 | -0.52185 | 99.9527 | -23.2727 | 99.6506 | -8.5098 | -23.0988 | 0.37537 | -0.54474 | 99.8611 | -23.2498 | 99.8108 | -21.1029 | -23.3871 | -23.2773 | -0.073242 | 0.10529 | -0.19684 | 14.6896 | 23.5748 | 0.10071 | 23.6481 | 0.17395 | -0.050354 | 0.013733 | -0.036621 | 2.0966 | -0.07782 | -0.18768 | -0.027466 | -0.13733 | 14.7629 | 122.9233 | 2.1469 | 123.0606 | 123.2254 | 123.111 | 123.1522 | 123.0606 | -123.1201 | -123.0972 | 122.85 | 123.0103 | 22.6776 | 22.6547
556.3281 | 123.262 | -25.0671 | 97.9248 | -0.052872 | -0.00099768 | 0.070831 | 0.084426 | 0.0018565 | 0.0041613 | -0.0027023 | -0.027222 | 0.0015872 | 0.06642 | 0.060398 | -0.005567 | 0.0014933 | -0.0037705 | -0.70496 | 97.9294 | -25.2914 | 97.7692 | -9.1415 | -25.2914 | 0.31586 | -0.63629 | 97.9156 | -25.1358 | 97.9523 | -22.5266 | -25.2136 | -25.0214 | -0.2243 | 0.004577 | -0.15564 | 15.9256 | 25.383 | -0.2243 | 25.6073 | 0 | -0.068664 | -0.009156 | 0.027466 | 2.5406 | 0.045777 | -0.14648 | 0.11444 | -0.07782 | 16.1499 | 123.0606 | 2.6093 | 123.0881 | 123.2208 | 123.0515 | 122.9965 | 122.9828 | -123.2162 | -123.0606 | 122.8363 | 123.0194 | 24.3622 | 24.4308
557.3281 | 123.1613 | -24.7559 | 98.3185 | -0.07576 | 0.0034885 | 0.072967 | 0.086776 | 0.0037791 | 0.00031608 | -0.00056607 | -0.018066 | 0.00116 | 0.067488 | 0.061893 | -0.0047126 | 0.0038431 | 0.0030655 | -0.737 | 98.3047 | -24.8932 | 98.1079 | -8.931 | -24.9069 | 0.34332 | -0.66376 | 98.259 | -24.8199 | 98.2452 | -22.0871 | -24.9435 | -24.7604 | -0.13733 | -0.013732 | -0.21057 | 15.8249 | 25.0992 | -0.15106 | 25.2365 | -0.013733 | -0.064087 | -0.059509 | -0.073242 | 2.6688 | -0.004578 | -0.18768 | 0.059509 | -0.1236 | 15.9622 | 123.0011 | 2.7328 | 123.0652 | 123.1979 | 123.0789 | 123.0606 | 123.0148 | -123.2117 | -123.1384 | 122.8638 | 123.0011 | 24.0189 | 24.0921
558.3281 | 123.143 | -26.239 | 96.8536 | -0.060501 | 0.0017795 | 0.072326 | 0.086135 | 0.0027109 | 0.00074348 | -0.0014207 | 0.018555 | 0.0018008 | 0.067274 | 0.065311 | -0.00279 | 0.0027751 | 0.0019973 | -0.8606 | 96.8903 | -26.3535 | 96.524 | -10.3226 | -26.3672 | 0.21973 | -0.8194 | 96.8445 | -26.2756 | 96.7621 | -23.4283 | -26.4038 | -26.1246 | -0.11444 | 0.036621 | -0.32959 | 15.9164 | 26.4587 | -0.12817 | 26.5732 | -0.013732 | -0.036621 | -0.009156 | -0.091553 | 2.8107 | 0.11444 | -0.16479 | 0.15106 | -0.12817 | 16.0309 | 122.8775 | 2.8473 | 123.0377 | 123.2437 | 123.1201 | 123.1293 | 123.0835 | -123.2071 | -123.1293 | 122.7631 | 123.0011 | 25.3784 | 25.4196
559.3281 | 123.1476 | -27.4704 | 95.5444 | -0.052872 | 0.0030613 | 0.069977 | 0.083572 | 0.00078827 | 0.0011707 | -0.0016343 | -0.02417 | 0.00073263 | 0.065992 | 0.070224 | -0.0040716 | 0.0029887 | -0.00077965 | -0.85144 | 95.6085 | -27.6169 | 95.3568 | -14.328 | -27.4292 | 0.29297 | -0.78735 | 95.5124 | -27.5711 | 95.4071 | -24.353 | -27.6443 | -27.4246 | -0.14648 | 0.064087 | -0.18768 | 13.1424 | 27.7634 | 0.041199 | 27.9099 | 0.18768 | -0.10071 | -0.032044 | -0.13733 | 3.1174 | 0.045776 | -0.17395 | 0.14648 | -0.073242 | 13.2889 | 122.9736 | 3.2181 | 122.9782 | 123.2254 | 123.0835 | 123.0789 | 122.9828 | -123.1613 | -123.1155 | 122.8271 | 122.8775 | 26.619 | 26.683
560.3281 | 123.1888 | -28.2349 | 94.7205 | -0.083389 | 0.00092492 | 0.071045 | 0.085494 | -0.00049353 | 0.00052988 | 0.0015701 | -0.018066 | 0.0018008 | 0.067701 | 0.062534 | -0.0047126 | 0.0025613 | 0.00071555 | -0.78735 | 95.5399 | -27.7084 | 95.1782 | -12.6251 | -27.6169 | 0.38452 | -0.93842 | 95.2881 | -27.8549 | 94.9631 | -25.1175 | -28.2623 | -28.0975 | 0.52643 | 0.8194 | 0.45776 | 15.6097 | 28.6194 | 0.61798 | 28.093 | 0.091553 | 0.37994 | 0.56763 | 0.24262 | 3.1174 | 0.13733 | -0.027466 | -0.24262 | -0.40741 | 15.0833 | 122.8867 | 2.7374 | 122.818 | 123.2483 | 123.143 | 123.7747 | 123.5229 | -122.4289 | -122.5754 | 123.4131 | 123.1979 | 27.4475 | 27.2964
561.3281 | 123.2666 | -70.4544 | 52.446 | -0.25887 | 0.00028412 | 0.069122 | 0.083144 | -0.0015615 | 0.00095708 | -0.0020615 | -0.045532 | 0.0020144 | 0.070906 | 0.080692 | -0.0036444 | 0.0025613 | -0.00056605 | -2.0142 | 52.5513 | -70.6558 | 52.4323 | -63.2721 | -70.3674 | -0.84686 | -2.1835 | 52.4506 | -70.5688 | 52.5055 | -61.6058 | -70.3766 | -69.7952 | -0.20142 | 0.10529 | -0.013733 | 7.1823 | 69.6075 | 0.086975 | 69.809 | 0.28839 | -0.11444 | 0.004578 | 0.059509 | 8.8486 | 0.65918 | 0.07782 | 0.77362 | 0.19226 | 7.3837 | 123.0881 | 8.963 | 123.0743 | 123.2071 | 123.0194 | 123.0057 | 122.905 | -123.1018 | -123.0148 | 122.8867 | 122.9599 | 68.4402 | 68.2709
562.3281 | 123.1018 | -38.8184 | 84.2377 | -0.10628 | 0.0015659 | 0.066986 | 0.084853 | 0.00014747 | 0.0015979 | 0.00028833 | -0.042481 | 0.0024416 | 0.066633 | 0.067661 | -0.005567 | 0.0025613 | -0.0012071 | -1.3504 | 84.2651 | -38.9465 | 84.082 | -34.7946 | -38.9008 | -0.12817 | -1.4511 | 84.2468 | -38.8138 | 84.1599 | -33.8928 | -38.8962 | -38.5437 | -0.12817 | 0.027466 | -0.15564 | 4.0237 | 38.6902 | -0.082398 | 38.8184 | 0.045776 | 0.004577 | 0.009155 | -0.07782 | 4.9255 | 0.27466 | -0.07782 | 0.27008 | -0.082397 | 4.1519 | 123.0286 | 4.921 | 122.9736 | 123.2117 | 123.0606 | 123.0835 | 123.0652 | -123.1842 | -123.0515 | 122.9004 | 122.9782 | 37.468 | 37.3672
563.3281 | 123.1476 | -39.1296 | 83.9264 | -0.12917 | 7.0518e-05 | 0.068481 | 0.086135 | 0.00057467 | -0.00075192 | 0.00071573 | -0.066895 | 0.002228 | 0.068342 | 0.069797 | -0.0025764 | 0.0012797 | 0.0045609 | -1.3733 | 83.9447 | -39.2258 | 83.8028 | -34.5245 | -39.1754 | -0.17395 | -1.3229 | 83.9127 | -39.1388 | 83.8715 | -34.2133 | -39.2029 | -38.7589 | -0.09613 | 0.01831 | -0.1236 | 4.6051 | 38.9557 | -0.045776 | 39.0518 | 0.050354 | -0.009155 | -0.013733 | -0.054932 | 4.9164 | 0.37079 | -0.073242 | 0.37994 | -0.064087 | 4.7012 | 123.0286 | 4.9255 | 123.0103 | 123.1705 | 123.0515 | 123.0743 | 123.0423 | -123.1522 | -123.0652 | 122.9324 | 123.0011 | 37.7563 | 37.8067
564.3281 | 123.1522 | -40.4709 | 82.6035 | -0.07576 | 0.00049772 | 0.067627 | 0.08464 | 0.0069833 | 0.0037341 | -0.0022751 | 0.030762 | 0.00073263 | 0.067701 | 0.072361 | -0.0023626 | 0.0059793 | 0.00092935 | -1.6067 | 82.6813 | -40.5762 | 82.5943 | -35.3256 | -40.6677 | -0.17853 | -1.4786 | 82.608 | -40.48 | 82.5714 | -35.0922 | -40.4846 | -40.2466 | -0.10529 | 0.077819 | -0.009156 | 5.1453 | 40.2924 | -0.19684 | 40.3976 | -0.091553 | -0.009156 | 0.004577 | -0.032044 | 5.3787 | 0.2243 | -0.013733 | 0.23346 | -0.004577 | 5.2505 | 123.1705 | 5.3879 | 123.0515 | 123.2574 | 123.0881 | 123.1522 | 123.0789 | -123.1796 | -123.0835 | 123.0652 | 123.0423 | 38.8641 | 38.9923
565.3281 | 123.1796 | -43.9774 | 79.0558 | -0.052872 | 0.00092492 | 0.068908 | 0.085921 | 0.0035653 | 0.0015979 | 0.00071573 | -0.042481 | 0.0018008 | 0.067488 | 0.070865 | -0.0074896 | 0.0010661 | 0.0022109 | -1.799 | 79.129 | -44.0826 | 78.9734 | -37.999 | -43.7805 | -0.31586 | -1.5427 | 79.0009 | -44.0231 | 79.0375 | -37.9532 | -43.9865 | -43.6523 | -0.10529 | 0.073242 | -0.082397 | 5.9784 | 43.6615 | 0.19684 | 43.7668 | 0.30212 | -0.045776 | -0.054932 | -0.01831 | 6.0242 | 0.32501 | -0.009155 | 0.37079 | 0.036621 | 6.0837 | 123.056 | 6.0699 | 123.0606 | 123.2117 | 123.024 | 123.1064 | 122.9782 | -123.1384 | -123.0789 | 122.9507 | 123.0148 | 42.1783 | 42.4347
566.3281 | 123.1247 | -34.9686 | 88.1149 | -0.083389 | 0.00092492 | 0.066772 | 0.085494 | 0.0012155 | 0.0022387 | -0.00099327 | -0.021118 | 0.002869 | 0.067915 | 0.070011 | -0.0059942 | 0.0044839 | 0.00092935 | -1.561 | 88.0966 | -35.1425 | 87.822 | -29.7729 | -34.877 | -0.16937 | -1.3184 | 88.0875 | -35.0006 | 87.9868 | -29.7455 | -35.0281 | -34.7946 | -0.17395 | -0.01831 | -0.29297 | 5.1956 | 34.7992 | 0.091553 | 34.9731 | 0.2655 | -0.032043 | -0.027466 | -0.12817 | 5.2231 | 0.17395 | -0.059509 | 0.20599 | -0.027466 | 5.3696 | 122.9645 | 5.2551 | 122.9874 | 123.2391 | 123.0881 | 123.0652 | 123.056 | -123.2574 | -123.1155 | 122.7905 | 122.9553 | 33.4076 | 33.6502
567.3281 | 123.1796 | -35.701 | 87.3322 | -0.052872 | 0.0017795 | 0.067627 | 0.087417 | 0.0022837 | 0.00052988 | -0.0022751 | -0.039429 | -0.00033537 | 0.065565 | 0.067661 | -0.0066352 | 0.0034159 | 0.00028835 | -1.6434 | 87.3734 | -35.82 | 87.1994 | -30.7022 | -35.8749 | -0.1831 | -1.2726 | 87.3047 | -35.7468 | 87.3184 | -31.0455 | -35.733 | -35.4767 | -0.11902 | 0.041199 | -0.13275 | 4.9988 | 35.5179 | -0.17395 | 35.6369 | -0.054932 | -0.045776 | -0.027466 | -0.013733 | 4.6555 | 0.2243 | -0.032043 | 0.27008 | 0.013733 | 5.1178 | 123.0194 | 4.7012 | 123.0652 | 123.1934 | 123.0515 | 123.0743 | 123.0057 | -123.1522 | -123.0789 | 122.9004 | 123.0194 | 34.0576 | 34.4284
568.3281 | 123.1155 | -35.2661 | 87.822 | -0.045242 | 0.0032749 | 0.065918 | 0.086776 | 0.0010019 | 0.0011707 | -0.0024887 | -0.036377 | -0.00097617 | 0.068129 | 0.075138 | -0.0064216 | 0.0046977 | 0.0024245 | -1.7578 | 87.8082 | -35.4263 | 87.5519 | -29.5807 | -35.3714 | -0.14191 | -1.4008 | 87.7899 | -35.2982 | 87.7258 | -30.6656 | -35.2753 | -35.0006 | -0.16022 | -0.013732 | -0.27008 | 5.6854 | 35.1242 | -0.10529 | 35.2844 | 0.054932 | -0.032044 | -0.032043 | -0.09613 | 4.6005 | 0.2655 | -0.009156 | 0.29755 | 0.022888 | 5.8456 | 122.9782 | 4.6326 | 123.024 | 123.2346 | 123.0881 | 123.0743 | 123.056 | -123.2483 | -123.1201 | 122.818 | 122.9919 | 33.5083 | 33.8654
569.3281 | 123.1338 | -34.4925 | 88.5727 | -0.052872 | 0.0030613 | 0.068908 | 0.086562 | 0.00036107 | 0.00074348 | -0.00077967 | -0.018066 | 0.0032962 | 0.06642 | 0.060184 | -0.003858 | 0.0061929 | -0.0018479 | -1.7761 | 88.5635 | -34.6207 | 88.3987 | -28.4592 | -34.4696 | -0.13733 | -1.3184 | 88.504 | -34.5383 | 88.4995 | -29.8737 | -34.4833 | -34.3185 | -0.12817 | -0.009155 | -0.17395 | 6.0333 | 34.3552 | 0.022889 | 34.4833 | 0.15106 | -0.045776 | -0.068665 | -0.073242 | 4.6188 | 0.17395 | 0.009156 | 0.21973 | 0.054932 | 6.1615 | 123.0194 | 4.6646 | 123.0377 | 123.1842 | 123.0423 | 123.056 | 122.9965 | -123.1934 | -123.111 | 122.8912 | 122.9919 | 32.7164 | 33.1741
570.3281 | 123.1934 | -34.4009 | 88.623 | -0.10628 | 0.0019931 | 0.068481 | 0.085921 | 0.0031381 | 0.00052988 | -0.00013887 | -0.02417 | 9.1834e-05 | 0.067061 | 0.061893 | -0.003858 | 0.0032023 | 0.0013565 | -1.8036 | 88.623 | -34.5886 | 88.4125 | -28.1113 | -34.552 | -0.1236 | -1.3641 | 88.5681 | -34.4788 | 88.6047 | -29.6494 | -34.3826 | -34.1721 | -0.18768 | 0 | -0.21057 | 6.2897 | 34.2773 | -0.15106 | 34.465 | 0.036621 | -0.07782 | -0.054932 | -0.018311 | 4.7516 | 0.22888 | 0.018311 | 0.3067 | 0.096131 | 6.4774 | 123.0011 | 4.8294 | 123.0835 | 123.2117 | 123.0469 | 123.024 | 122.9691 | -123.2117 | -123.1018 | 122.8134 | 123.0057 | 32.5974 | 33.0368
571.3281 | 123.1888 | -34.1858 | 88.8519 | -0.11391 | 0.0028475 | 0.067413 | 0.087203 | 0.00014747 | 0.0011707 | -0.00099327 | -0.036377 | 0.0020144 | 0.067274 | 0.061679 | -0.0032172 | 0.0027751 | -0.00056605 | -1.7029 | 88.884 | -34.3323 | 88.7375 | -27.594 | -33.8379 | 0.022888 | -1.3229 | 88.9023 | -34.1537 | 88.8657 | -29.3106 | -34.1309 | -33.9249 | -0.14648 | 0.032043 | -0.11444 | 6.5918 | 34.2087 | 0.3479 | 34.3552 | 0.49438 | 0.032043 | 0.050354 | 0.013733 | 4.8752 | 0.26093 | 0.054932 | 0.22888 | 0.022889 | 6.7383 | 123.0698 | 4.8431 | 123.0194 | 123.2162 | 123.056 | 123.0698 | 123.0881 | -123.1842 | -123.0057 | 122.9233 | 123.0515 | 32.4829 | 32.8629
572.3281 | 123.2941 | -34.2545 | 88.8428 | -0.083389 | 0.0013523 | 0.068054 | 0.085281 | -6.6126e-05 | 0.0024525 | -0.0027023 | -0.033325 | 0.0020144 | 0.068556 | 0.064456 | -0.0047126 | 0.0044839 | 0.0047745 | -1.712 | 88.7787 | -34.4421 | 88.4857 | -27.6855 | -34.3689 | -0.07782 | -1.5015 | 88.7146 | -34.3735 | 88.6826 | -28.9581 | -34.5108 | -34.1583 | -0.18768 | -0.064086 | -0.35705 | 6.5689 | 34.1766 | -0.11444 | 34.3643 | 0.073243 | -0.11902 | -0.12817 | -0.16022 | 5.2963 | 0.096131 | -0.25635 | 0.21515 | -0.13733 | 6.7566 | 122.9279 | 5.4153 | 123.056 | 123.2208 | 123.0881 | 123.0331 | 122.9691 | -123.2849 | -123.2162 | 122.7402 | 122.937 | 32.5424 | 32.753
573.3281 | 123.2071 | -35.1288 | 87.8586 | -0.06813 | 0.0015659 | 0.066986 | 0.086135 | 0.0010019 | 0.0013843 | 0.0011429 | -0.027222 | 0.0020144 | 0.067488 | 0.070224 | -0.0040716 | 0.0079019 | 0.0043471 | -1.7303 | 87.8906 | -35.3073 | 87.7029 | -28.2806 | -34.8083 | -0.013733 | -1.4374 | 87.8723 | -35.1883 | 87.8723 | -29.7318 | -35.0693 | -34.8495 | -0.17853 | 0.032043 | -0.15564 | 6.8481 | 35.1151 | 0.32043 | 35.2936 | 0.49896 | -0.059509 | 0.013732 | 0.013732 | 5.397 | 0.27924 | 0.059509 | 0.33875 | 0.11902 | 7.0267 | 123.0103 | 5.4565 | 123.0606 | 123.1979 | 123.0606 | 123.0194 | 123.0011 | -123.1659 | -123.0469 | 122.8317 | 123.0011 | 33.3984 | 33.6914
574.3281 | 123.1476 | -34.5016 | 88.5269 | -0.037613 | 0.0017795 | 0.068695 | 0.088698 | -0.0019889 | 0.0020251 | 0.0015701 | -0.033325 | 0.0032962 | 0.068129 | 0.06937 | -0.0030036 | 0.0051249 | 0.0017837 | -1.7349 | 88.6597 | -34.584 | 88.3987 | -27.1637 | -34.6115 | -0.42114 | -1.593 | 88.5864 | -34.4879 | 88.5086 | -29.0955 | -34.3918 | -34.1766 | -0.082397 | 0.13275 | -0.12817 | 7.338 | 34.0805 | -0.10986 | 34.1629 | -0.027466 | 0.013733 | 0.059509 | -0.018311 | 5.4062 | 0.32501 | 0.10986 | 0.31128 | 0.09613 | 7.4203 | 122.9828 | 5.3925 | 122.9965 | 123.2437 | 123.0743 | 123.1613 | 123.0881 | -123.111 | -123.0148 | 122.9004 | 123.0103 | 32.7667 | 32.9086
575.3281 | 123.1979 | -33.8882 | 89.1312 | -0.07576 | 0.00071132 | 0.069336 | 0.08763 | -0.00092073 | 0.0020251 | -0.0044113 | -0.018066 | 0.00116 | 0.067061 | 0.068515 | -0.0049262 | 0.0066203 | 0.0043471 | -1.6251 | 89.1037 | -34.1354 | 88.9435 | -26.6327 | -33.7189 | -0.49439 | -1.3687 | 89.0945 | -33.9661 | 89.1174 | -28.3768 | -33.7555 | -33.5541 | -0.24719 | -0.027466 | -0.18768 | 7.2556 | 33.3939 | 0.16937 | 33.6411 | 0.41657 | -0.077819 | -0.036622 | -0.013733 | 5.5115 | 0.33417 | 0.13275 | 0.41199 | 0.21057 | 7.5027 | 123.0789 | 5.5893 | 123.0835 | 123.2391 | 123.0606 | 122.9919 | 122.9828 | -123.2666 | -123.0972 | 122.8317 | 123.0057 | 32.2632 | 32.5195
576.3281 | 123.1567 | -34.0897 | 89.003 | -0.11391 | 0.0030613 | 0.06784 | 0.08699 | 0.0022837 | 0.0013843 | -0.0018479 | -0.039429 | -0.00054897 | 0.067488 | 0.071506 | -0.00279 | 0.0042703 | 0.0034927 | -1.6617 | 88.9847 | -34.2499 | 88.7741 | -26.1795 | -33.9844 | -0.49439 | -1.4923 | 88.9893 | -34.1217 | 88.8977 | -28.4546 | -33.9981 | -33.8242 | -0.16022 | -0.018311 | -0.22888 | 7.9102 | 33.5953 | 0.10529 | 33.7555 | 0.2655 | -0.032043 | -0.013733 | -0.10529 | 5.6351 | 0.2655 | 0.091553 | 0.29755 | 0.1236 | 8.0704 | 123.024 | 5.6671 | 123.0194 | 123.2346 | 123.111 | 123.0743 | 123.0789 | -123.2529 | -123.1247 | 122.8638 | 122.9874 | 32.428 | 32.5974
577.3281 | 123.2117 | -34.14 | 88.8748 | -0.060501 | -0.00035668 | 0.068268 | 0.086135 | 0.00078827 | 0.0022387 | 0.0015701 | -0.036377 | 0.00116 | 0.068129 | 0.073856 | -0.0074896 | 0.0059793 | 0.0013565 | -1.6571 | 88.8657 | -34.3506 | 88.6917 | -26.7059 | -33.6685 | -0.78278 | -1.4191 | 88.8611 | -34.2133 | 88.8794 | -28.2303 | -33.9523 | -33.815 | -0.21057 | -0.009155 | -0.18311 | 7.4341 | 33.3572 | 0.4715 | 33.5678 | 0.68207 | -0.073242 | -0.013733 | 0.004578 | 5.9097 | 0.32501 | 0.18768 | 0.39825 | 0.26093 | 7.6447 | 123.0423 | 5.983 | 123.0927 | 123.2162 | 123.0743 | 123.0057 | 123.0011 | -123.2254 | -123.0881 | 122.8317 | 123.0194 | 32.4829 | 32.7209
578.3281 | 123.1567 | -34.1949 | 88.8519 | -0.060501 | 0.0017795 | 0.068481 | 0.087203 | 0.0016427 | 0.0026661 | -0.0035569 | -0.051636 | 0.0037234 | 0.067488 | 0.067447 | -0.0030036 | 0.0038431 | 0.0049881 | -1.7029 | 88.8428 | -34.3643 | 88.6505 | -26.7838 | -34.1446 | -0.70038 | -1.5152 | 88.8062 | -34.2728 | 88.8016 | -28.2578 | -33.8654 | -33.8928 | -0.16937 | -0.009156 | -0.20142 | 7.4112 | 33.4946 | 0.050354 | 33.6639 | 0.21973 | -0.07782 | -0.045777 | -0.050354 | 5.9372 | 0.30212 | 0.32959 | 0.37994 | 0.40741 | 7.5806 | 123.0148 | 6.015 | 123.0743 | 123.2071 | 123.0789 | 123.0377 | 123.0011 | -123.2162 | -123.1247 | 122.8455 | 122.9965 | 32.4921 | 32.6797
579.3281 | 123.2071 | -42.1097 | 80.8868 | -0.060501 | 0.0013523 | 0.069549 | 0.088271 | 0.0031381 | 0.0033069 | 0.00071573 | -0.0028075 | 0.0024416 | 0.071119 | 0.086887 | -0.0023626 | 0.0046977 | 0.0015701 | -2.1606 | 81.3171 | -41.9678 | 80.7404 | -32.8537 | -41.6016 | -1.8906 | -1.9958 | 80.9235 | -42.1417 | 80.8136 | -34.552 | -41.7343 | -41.5924 | 0.14191 | 0.4303 | -0.14648 | 9.256 | 40.2191 | 0.50812 | 40.0772 | 0.36621 | -0.032044 | 0.036621 | -0.073242 | 7.5577 | 0.51727 | 0.37537 | 0.54932 | 0.40741 | 9.1141 | 122.7081 | 7.5897 | 122.9553 | 123.2849 | 123.0652 | 123.4268 | 123.0331 | -122.8546 | -123.0286 | 122.85 | 122.9233 | 39.949 | 40.1138
580.3281 | 123.2346 | -40.6082 | 82.3608 | -0.1368 | 0.0024203 | 0.070831 | 0.086776 | -0.0043387 | 0.0026661 | 7.4734e-05 | -0.033325 | 0.002228 | 0.071119 | 0.085605 | -0.0051398 | 0.0061929 | 0.0062697 | -2.1194 | 82.5027 | -40.686 | 82.5394 | -30.2902 | -40.3152 | -2.0966 | -1.7487 | 82.4661 | -40.5624 | 82.3883 | -33.1375 | -39.9124 | -39.8529 | -0.07782 | 0.14191 | 0.17853 | 10.318 | 38.5117 | 0.29297 | 38.5895 | 0.37079 | 0.045776 | 0.10529 | 0.027466 | 7.4707 | 0.75531 | 0.6958 | 0.70953 | 0.65002 | 10.3958 | 123.2254 | 7.4249 | 122.9507 | 123.1888 | 123.0286 | 123.111 | 123.0743 | -123.0469 | -122.9233 | 123.1476 | 122.9965 | 38.4888 | 38.8596
581.3281 | 123.0972 | -33.8837 | 89.2593 | -0.045242 | 0.0019931 | 0.070617 | 0.08699 | 0.00057467 | 0.0024525 | -0.0020615 | 0.033813 | 0.0020144 | 0.069624 | 0.065525 | -0.0036444 | 0.0046977 | 0.0052017 | -1.8814 | 89.2136 | -34.0027 | 88.9755 | -25.6302 | -33.6639 | -1.7624 | -1.6113 | 89.1998 | -33.8837 | 89.1815 | -27.4567 | -33.49 | -33.3435 | -0.11902 | -0.045776 | -0.28381 | 8.2535 | 32.1213 | 0.21973 | 32.2403 | 0.33875 | 0 | -0.059509 | -0.077819 | 6.427 | 0.54016 | 0.39368 | 0.54016 | 0.39368 | 8.3725 | 122.9782 | 6.427 | 123.0652 | 123.2162 | 123.0835 | 123.0972 | 123.0835 | -123.262 | -123.143 | 122.8592 | 123.0652 | 32.0023 | 32.2723
582.3281 | 123.1476 | -33.8242 | 89.2181 | -0.052872 | 0.0011385 | 0.071899 | 0.088698 | 0.00014747 | 0.0013843 | 0.00092933 | -0.036377 | 0.0020144 | 0.067915 | 0.067234 | -0.0049262 | 0.0061929 | -0.00035245 | -1.9226 | 89.241 | -33.9798 | 89.0717 | -25.589 | -33.5495 | -1.9363 | -1.6525 | 89.1953 | -33.8791 | 89.2227 | -27.269 | -33.49 | -33.2108 | -0.15564 | 0.022888 | -0.14648 | 8.2352 | 31.8878 | 0.27466 | 32.0435 | 0.4303 | -0.054931 | -0.022889 | 0.004577 | 6.5552 | 0.6134 | 0.33417 | 0.66833 | 0.3891 | 8.3908 | 123.0515 | 6.6101 | 123.1018 | 123.2208 | 123.0743 | 123.0652 | 123.0194 | -123.1979 | -123.0972 | 122.8958 | 123.0469 | 31.9016 | 32.1716
583.3281 | 123.1476 | -33.3069 | 89.7537 | -0.06813 | -0.00014308 | 0.069122 | 0.086776 | 0.0061289 | 0.00074348 | -0.0020615 | -0.018066 | 0.002869 | 0.068342 | 0.080905 | -0.0049262 | 0.0055521 | 0.0039199 | -1.9775 | 89.7629 | -33.4717 | 89.5386 | -25.3372 | -32.9681 | -1.2817 | -1.7029 | 89.7354 | -33.3298 | 89.6851 | -26.7654 | -32.9361 | -32.9224 | -0.16479 | 0.009155 | -0.21515 | 7.9697 | 32.0251 | 0.33875 | 32.1899 | 0.50354 | -0.022888 | -0.01831 | -0.068664 | 6.5414 | 0.38452 | 0.37079 | 0.40741 | 0.39368 | 8.1345 | 123.0103 | 6.5643 | 123.0148 | 123.2346 | 123.0652 | 123.0698 | 123.0423 | -123.2254 | -123.0835 | 122.8455 | 122.9919 | 31.3293 | 31.604
584.3281 | 123.1522 | -33.8013 | 89.2593 | -0.029984 | 0.00049772 | 0.07019 | 0.089767 | -0.00070713 | 0.0045887 | -0.0044113 | -0.018066 | 0.00116 | 0.069197 | 0.071506 | -0.003858 | 0.0064065 | 0.0056289 | -1.9775 | 89.2822 | -33.934 | 89.0854 | -25.4471 | -33.4534 | -0.91553 | -1.6434 | 89.2548 | -33.8058 | 89.1861 | -27.0401 | -33.3527 | -33.0505 | -0.13275 | 0.022889 | -0.17395 | 8.3542 | 32.8857 | 0.3479 | 33.0185 | 0.48065 | -0.004577 | -0.004577 | -0.073242 | 6.7612 | 0.75073 | 0.44861 | 0.75531 | 0.45319 | 8.4869 | 123.0194 | 6.7657 | 122.9919 | 123.2162 | 123.0606 | 123.0835 | 123.056 | -123.1934 | -123.0652 | 122.8867 | 122.9874 | 31.8237 | 32.1579
585.3281 | 123.1842 | -113.855 | 9.1232 | -0.11391 | 7.0518e-05 | 0.12808 | 0.085494 | 0.00036107 | 0.68071 | 0.0026383 | -0.28662 | 0.0024416 | 0.082228 | 0.86789 | -0.0051398 | 0.018369 | 0.014388 | -2.8519 | 9.2011 | -113.9694 | 8.9172 | -13.7329 | -5.6122 | -0.86517 | -5.3421 | 9.0546 | -113.9465 | 8.844 | -87.8815 | -111.7401 | -111.1588 | -0.11444 | 0.07782 | -0.20599 | 100.1221 | 112.9898 | 108.2428 | 113.1042 | 108.3572 | -0.091553 | -0.068665 | -0.27924 | 25.9735 | 2.6962 | 2.1149 | 2.7878 | 2.2064 | 100.2365 | 122.8867 | 26.0651 | 122.7905 | 123.1705 | 123.0011 | 123.056 | 122.9095 | -123.0927 | -123.0698 | 122.7722 | 122.699 | 111.0031 | 108.5129
586.3281 | 123.1659 | -116.7389 | 6.189 | -0.022354 | 0.0030613 | 0.13 | 0.083999 | 0.0033517 | 0.70463 | 0.0015701 | -0.62842 | 0.0015872 | 0.082228 | 1.5981 | -0.0053534 | 0.014738 | 0.71614 | -3.0258 | 6.2073 | -116.8991 | 5.9921 | -9.1187 | -4.4495 | -0.53101 | -5.4565 | 6.0699 | -116.716 | 5.8868 | -87.8448 | -114.3265 | -4.1016 | -0.16022 | 0.01831 | -0.19684 | 107.6202 | 116.2079 | 112.2894 | 116.3681 | 112.4496 | 0.022889 | -0.11902 | -0.30212 | 28.894 | 112.6373 | 2.4124 | 112.6144 | 2.3895 | 107.7805 | 122.8912 | 28.8712 | 122.6028 | 123.1064 | 122.7859 | 122.9462 | 122.8088 | -123.0881 | -122.905 | 122.731 | 122.6257 | 113.7131 | 111.2823
587.3281 | 123.1018 | -116.4322 | 6.514 | -0.083389 | 0.0043429 | 0.13086 | 0.084212 | 0.0024973 | 0.60295 | -0.00056607 | -0.67419 | 0.0013736 | 0.087141 | 1.9268 | -0.0032172 | 0.47339 | 0.66936 | -3.1723 | 6.4224 | -116.5649 | 6.2393 | -9.0958 | -3.9276 | -0.62256 | -3.6484 | 6.221 | -116.4276 | 5.6259 | -80.3558 | -29.6402 | -4.1656 | -0.13275 | -0.091553 | -0.27466 | 107.3364 | 115.8096 | 112.5046 | 115.9424 | 112.6373 | 0.004578 | -0.29297 | -0.88806 | 36.0764 | 112.2665 | 86.792 | 112.262 | 86.7874 | 107.4692 | 122.8043 | 36.0718 | 122.0535 | 122.9874 | 122.6486 | 122.8546 | 122.6532 | -123.0789 | -122.9416 | 122.6715 | 122.0581 | 113.2599 | 112.7838
588.3281 | 123.2712 | 8.8531 | 146.8964 | 0.64903 | 0.027414 | 0.052887 | 0.086349 | 0.035182 | 0.05244 | 0.047499 | -0.31714 | 0.017609 | 0.014296 | 0.016605 | 0.25698 | 0.0083293 | 0.032118 | 0.10071 | 149.9954 | 8.2397 | 122.2504 | 0.10071 | 0.10529 | 0.10071 | 0.09613 | 148.0133 | 8.2397 | 0.10071 | 117.7002 | 0.091553 | 0.10529 | -0.6134 | 3.0991 | -24.646 | -8.7524 | -8.7524 | -8.7479 | -8.139 | -8.1345 | -0.6134 | 1.1169 | -146.7957 | 108.847 | -8.7479 | -8.7616 | -8.1345 | -8.1482 | -8.139 | 114.0106 | 109.4604 | -8.139 | 141.7557 | 139.7736 | 141.1423 | 139.1602 | -138.6566 | -138.6566 | 113.3972 | -8.7524 | -8.7524 | -8.757
589.3281 | 123.0835 | -118.0344 | 4.8798 | -0.029984 | 0.0039157 | 0.13769 | 0.085067 | 0.00014747 | 0.49763 | -0.0022751 | -0.63147 | -0.0018308 | 0.086714 | 1.7399 | -0.0040716 | 0.47958 | 0.57878 | -3.2364 | 4.9347 | -118.1808 | 4.7012 | -8.8303 | -2.948 | -0.75531 | -3.3966 | 4.6326 | -118.0527 | 4.2023 | -87.6892 | -14.9414 | -3.1174 | -0.14648 | 0.054931 | -0.17853 | 109.2041 | 117.2791 | 115.0864 | 117.4255 | 115.2328 | -0.01831 | -0.24719 | -0.67749 | 30.3452 | 114.917 | 103.093 | 114.9353 | 103.1113 | 109.3506 | 122.8821 | 30.3635 | 122.2549 | 123.1155 | 122.6852 | 122.9691 | 122.6669 | -123.0606 | -122.9324 | 122.7356 | 122.2366 | 114.798 | 114.6378
590.3281 | 123.0972 | -116.8762 | 6.0104 | -0.07576 | 0.0081881 | 0.12616 | 0.070541 | -0.011175 | 0.52305 | -0.015306 | -0.92139 | -0.016357 | 0.082869 | 1.7717 | -0.020307 | 0.43066 | 0.062453 | -3.598 | 5.4382 | -117.2928 | 5.5664 | -5.9509 | 0.091553 | 0.10071 | -3.2135 | 5.2231 | -117.0914 | 0.09613 | -57.2479 | 0.22888 | 0.09613 | -0.41657 | -0.5722 | -0.44403 | 110.9253 | 116.9769 | 116.9678 | 117.3935 | 117.3843 | -0.21515 | -0.78735 | -5.9143 | 59.6283 | 116.9724 | 117.1051 | 117.1875 | 117.3203 | 111.3419 | 122.8592 | 59.8434 | 117.1875 | 122.731 | 122.3145 | 122.3145 | 122.0993 | -123.3032 | -123.1018 | 122.4426 | 116.9724 | 113.2782 | 113.6627
591.3281 | 123.0743 | -114.8941 | 8.0521 | -0.052872 | 0.0022067 | 0.1347 | 0.08464 | 0.0037791 | 0.56663 | -0.0012071 | -0.67114 | 0.00030543 | 0.086928 | 1.9245 | -0.0036444 | 0.54025 | 0.64073 | -3.1906 | 7.9239 | -115.0955 | 7.8232 | -8.7616 | -4.0695 | -0.58136 | -3.4515 | 7.5348 | -114.8849 | 7.1411 | -83.1116 | -12.9501 | -3.3646 | -0.20142 | -0.12817 | -0.22888 | 106.1325 | 114.3127 | 110.8246 | 114.5142 | 111.026 | 0.009155 | -0.51727 | -0.91095 | 31.7825 | 111.5295 | 101.944 | 111.5204 | 101.9348 | 106.3339 | 122.9187 | 31.7734 | 122.0261 | 123.0194 | 122.4197 | 122.818 | 122.4289 | -123.1476 | -122.937 | 122.7173 | 122.0352 | 111.7035 | 111.4426
592.3281 | 123.1476 | 8.6517 | 149.9954 | -1.2202 | 0.080179 | 0.06784 | 0.1404 | 0.053767 | 0.2447 | 0.099196 | -0.31714 | 0.092804 | 0.0128 | 0.054416 | 0.15529 | 0.05319 | 0.050063 | 3.3051 | 149.9954 | 7.37 | 149.9954 | 6.6238 | 0.10529 | 0.09613 | 1.6571 | 149.9954 | 7.2693 | 0.086975 | 149.9954 | 0.55389 | 0.082397 | -1.2817 | 0 | 0 | -2.0279 | -8.5556 | -8.5464 | -7.2739 | -7.2647 | -1.3824 | 0 | -149.9084 | 141.3437 | -8.5693 | -8.0978 | -7.1869 | -6.7154 | -0.74615 | 142.6254 | 142.7261 | -7.1823 | 142.6254 | 142.7261 | 141.3437 | 141.3437 | -142.6254 | -142.7261 | 141.3437 | -8.5648 | -5.3467 | -6.9946
593.3281 | 123.0606 | -120.1263 | 2.861 | -0.11391 | 0.0028475 | 0.12637 | 0.059859 | -0.0071157 | 0.21159 | -0.011247 | -0.45142 | 0.017395 | 0.014082 | 0.92493 | 0.17494 | 0.11877 | 0.032118 | 0.091553 | 0.045776 | -120.4514 | 2.4124 | 0.09613 | 0.09613 | 0.09613 | 0.09613 | 0.068665 | -120.2591 | 0.10529 | -84.7824 | 0.09613 | 0.09613 | -0.32501 | -2.8152 | -0.44861 | 120.2225 | 120.2225 | 120.2225 | 120.5475 | 120.5475 | -0.13275 | -2.7924 | -2.7557 | 35.3439 | 120.2225 | 120.2225 | 120.3552 | 120.3552 | 120.5475 | 122.8638 | 35.4767 | 120.3644 | 120.4971 | 120.3278 | 120.1721 | 120.195 | -123.3124 | -123.1201 | 122.5388 | 120.2316 | 120.2179 | 120.2225
594.3281 | 123.0194 | -117.6773 | 5.1178 | -0.083389 | 0.0024203 | 0.13492 | 0.083144 | 0.0010019 | 0.60679 | 0.00050193 | -0.82373 | -0.0048216 | 0.11748 | 2.0834 | -0.0036444 | 0.5473 | 0.66017 | -3.5339 | 5.0766 | -117.8101 | 4.9438 | -9.7458 | 0.15564 | 0.091553 | -3.8589 | 4.747 | -117.6682 | 1.1307 | -17.2897 | -11.1511 | 0.086975 | -0.13275 | -0.041199 | -0.17395 | 107.9315 | 117.7689 | 117.8329 | 117.9016 | 117.9657 | 0.009155 | -0.37079 | -3.9871 | 100.3876 | 117.7643 | 106.5262 | 117.7551 | 106.517 | 108.0643 | 122.7539 | 100.3784 | 118.7988 | 122.8867 | 122.4152 | 122.7539 | 122.4243 | -122.9279 | -122.7859 | 122.6212 | 118.808 | 114.1434 | 113.8184
595.3281 | 115.9103 | -74.881 | 66.8564 | 89.768 | 4.3507 | 3.8101 | 0.46019 | 0.25415 | 0.57026 | 0.2483 | 12.6254 | 0.56683 | 0.34114 | 1.9465 | 1.1892 | 1.1414 | 0.11586 | 51.6541 | 105.4916 | -93.3014 | 81.5689 | 41.8396 | 23.9227 | 1.6159 | -5.8044 | 74.9176 | -78.7582 | 6.4499 | 52.0523 | 1.8219 | 6.2439 | -18.4204 | 38.6353 | 14.7125 | 116.7206 | 76.4969 | 98.8037 | 94.9173 | 117.2241 | -3.8773 | 8.0612 | -60.4065 | 126.9333 | 81.1249 | 76.7029 | 85.0021 | 80.5801 | 135.141 | 174.8703 | 130.8105 | 85.2081 | 198.793 | 153.6758 | 180.3726 | 149.7986 | -160.1578 | -145.6146 | 156.4499 | 81.3309 | 126.535 | 69.0765
596.3281 | 123.0881 | -114.9673 | 7.782 | -0.052872 | 0.0024203 | 0.13257 | 0.083358 | 0.0012155 | 0.68925 | 7.4734e-05 | -0.40869 | -0.002258 | 0.13478 | 0.0054966 | 0.99697 | 0.097837 | -0.0029159 | -3.4607 | 7.8506 | -115.1596 | 7.4066 | -8.931 | -3.6804 | 0.12817 | -3.4698 | 7.4387 | -115.0543 | -0.25635 | 7.4203 | -2.8381 | 0.10529 | -0.19226 | 0.068665 | -0.37537 | 106.0364 | 115.0955 | 111.2869 | 115.2878 | 111.4792 | -0.086975 | -0.34332 | -8.0383 | 122.3877 | 115.0726 | 112.1292 | 115.1596 | 112.2162 | 106.2286 | 122.5662 | 122.4747 | 114.798 | 123.0103 | 122.493 | 122.818 | 122.406 | -122.9416 | -122.8363 | 122.374 | 114.711 | 111.5067 | 111.4975
597.3281 | 123.024 | -116.4368 | 6.3629 | -0.060501 | 0.0024203 | 0.1362 | 0.083785 | 0.0016427 | 0.69566 | -0.00013887 | -0.31104 | -0.00097617 | 0.13777 | -0.00027138 | 1.0128 | 0.098905 | 0.0019973 | -3.4607 | 6.3675 | -116.5695 | 6.1478 | -7.9742 | -3.8223 | -0.76446 | -3.5797 | 6.2622 | -116.4139 | -0.23804 | 6.1295 | -2.742 | -0.28839 | -0.13275 | 0.004578 | -0.21515 | 108.4625 | 115.6723 | 112.6144 | 115.8051 | 112.7472 | 0.022889 | -0.10071 | -6.601 | 122.5662 | 116.1484 | 113.6948 | 116.1255 | 113.6719 | 108.5953 | 122.7173 | 122.5433 | 116.1758 | 122.937 | 122.6761 | 122.8043 | 122.699 | -122.9324 | -122.7768 | 122.5845 | 116.1987 | 112.9761 | 112.8571
598.3281 | 123.0515 | -116.9357 | 5.8868 | -0.029984 | 0.0019931 | 0.13235 | 0.067336 | -0.010107 | 0.68647 | -0.015306 | -0.32629 | 0.018036 | 0.12089 | -0.0011258 | 0.99376 | 0.1004 | -0.013383 | -3.4836 | 5.8731 | -117.0822 | 5.5435 | -8.2169 | 0.17395 | 0.09613 | -3.7582 | 5.7999 | -116.7068 | -0.21057 | 5.6992 | -2.9114 | 0.10986 | -0.14648 | -0.013733 | -0.34332 | 108.7189 | 117.0319 | 117.1097 | 117.1783 | 117.2562 | 0.22888 | -0.086975 | -6.0974 | 122.6349 | 117.0456 | 114.0244 | 116.8167 | 113.7955 | 108.8654 | 122.6257 | 122.406 | 116.4963 | 122.9553 | 122.5067 | 122.8088 | 122.7356 | -122.9691 | -122.5937 | 122.4792 | 116.7252 | 113.4521 | 113.1775
599.3281 | 123.0011 | -117.1646 | 5.722 | -0.098648 | 0.0037021 | 0.13705 | 0.083999 | 0.0029245 | 0.69801 | -0.00056607 | -0.34766 | -0.002899 | 0.13435 | -0.00091218 | 1.0173 | 0.098478 | 0.0011429 | -3.5568 | 5.6717 | -117.2424 | 5.5252 | -7.5577 | -3.4287 | -0.59967 | -3.8635 | 5.6259 | -117.0364 | -0.23804 | 5.484 | -2.6093 | -0.07782 | -0.07782 | -0.050354 | -0.19684 | 109.6069 | 116.5649 | 113.736 | 116.6428 | 113.8138 | 0.12817 | -0.09613 | -5.9601 | 122.6486 | 117.0868 | 114.5554 | 116.9586 | 114.4272 | 109.6848 | 122.7676 | 122.5204 | 116.7984 | 122.9141 | 122.6624 | 122.8363 | 122.7905 | -122.9645 | -122.7585 | 122.6898 | 116.9266 | 113.6078 | 113.3011
600.3281 | 122.9691 | -117.627 | 5.2185 | -0.037613 | 0.0047701 | 0.13791 | 0.08464 | 0.00057467 | 0.69993 | -0.0016343 | -0.52771 | -0.0024716 | 0.13692 | 0.0040012 | 1.0194 | 0.1004 | 0.00050195 | -3.7308 | 5.2551 | -117.7414 | 4.985 | -7.7042 | -3.6392 | -0.78278 | -4.0787 | 5.1636 | -117.5766 | -0.25635 | 4.9896 | -2.8976 | -0.25177 | -0.11444 | 0.036621 | -0.23346 | 109.9228 | 116.8442 | 113.9877 | 116.9586 | 114.1022 | 0.050354 | -0.054932 | -5.4749 | 122.6166 | 117.3752 | 114.7293 | 117.3248 | 114.679 | 110.0372 | 122.7264 | 122.5662 | 117.3203 | 122.9965 | 122.7402 | 122.8821 | 122.7905 | -122.9599 | -122.7951 | 122.612 | 117.3706 | 113.8962 | 113.5483
601.3281 | 122.9965 | -115.9607 | 6.871 | -0.052872 | 0.0030613 | 0.13919 | 0.083572 | 0.00078827 | 0.68605 | 0.0017837 | -0.32019 | -0.002258 | 0.13371 | 0.0025058 | 1.0047 | 0.096128 | -0.0022751 | -3.7308 | 6.8527 | -116.0156 | 6.7566 | -7.4295 | -3.1494 | -0.42114 | -4.0329 | 6.8024 | -115.9058 | -0.20142 | 6.7474 | -3.1769 | 0.07782 | -0.054932 | -0.018311 | -0.11444 | 108.5312 | 115.5396 | 112.8113 | 115.5945 | 112.8662 | 0.054931 | -0.068665 | -7.0724 | 122.7081 | 116.0385 | 112.7838 | 115.9836 | 112.7289 | 108.5861 | 122.7722 | 122.6532 | 115.7043 | 122.8683 | 122.7081 | 122.8134 | 122.7631 | -122.8867 | -122.7768 | 122.7173 | 115.7593 | 112.2299 | 111.9278
602.3281 | 122.937 | -117.1371 | 5.7175 | 0.023422 | 0.0037021 | 0.13235 | 0.083999 | 0.0057017 | 0.69374 | 0.0013565 | -0.44836 | -0.00054897 | 0.13692 | 0.0072054 | 1.0149 | 0.097196 | 0.0013565 | -3.7903 | 5.7587 | -117.1738 | 5.4337 | -7.489 | -3.2867 | -0.69122 | -4.3762 | 5.6442 | -117.1188 | -0.25177 | 5.4703 | -3.3188 | -0.07782 | -0.036621 | 0.041199 | -0.28381 | 109.6481 | 116.4459 | 113.8504 | 116.4825 | 113.887 | 0.018311 | -0.073242 | -5.9692 | 122.6074 | 117.0593 | 113.8184 | 117.041 | 113.8 | 109.6848 | 122.6074 | 122.5891 | 116.8671 | 122.9324 | 122.7631 | 122.8958 | 122.7814 | -122.8912 | -122.8363 | 122.5708 | 116.8854 | 113.3469 | 112.7609
603.3281 | 123.0148 | -117.5812 | 5.2139 | -0.083389 | 0.0022067 | 0.13898 | 0.082931 | 0.0042063 | 0.69566 | 0.0013565 | -0.31104 | -0.0020444 | 0.13692 | -0.003903 | 1.0173 | 0.099546 | -0.0046249 | -3.9963 | 5.191 | -117.6727 | 5.0858 | -7.4112 | -2.98 | -0.36163 | -4.3213 | 5.1224 | -117.5583 | -0.16022 | 5.0903 | -3.2272 | 0.09613 | -0.091552 | -0.022888 | -0.12817 | 110.17 | 117.2195 | 114.6011 | 117.3111 | 114.6927 | 0.022888 | -0.091553 | -5.3741 | 122.6715 | 117.6773 | 114.3539 | 117.6544 | 114.3311 | 110.2615 | 122.7585 | 122.6486 | 117.3981 | 122.8638 | 122.6807 | 122.7722 | 122.7036 | -122.8867 | -122.7722 | 122.6669 | 117.421 | 113.5849 | 113.2599
604.3281 | 122.9599 | -117.7002 | 5.1407 | -0.037613 | 0.0017795 | 0.13898 | 0.086135 | 0.0033517 | 0.69224 | -0.00035247 | -0.54602 | -0.0069578 | 0.13606 | -0.0017666 | 1.0168 | 0.09741 | 0.0028519 | -4.129 | 5.1224 | -117.8421 | 4.9026 | -7.5806 | -3.2593 | -0.68665 | -4.5593 | 5.072 | -117.691 | -0.27008 | 4.9072 | -3.4332 | -0.004578 | -0.14191 | -0.018311 | -0.23804 | 110.1196 | 117.0135 | 114.4409 | 117.1555 | 114.5828 | 0.009155 | -0.068665 | -5.4108 | 122.6074 | 117.6956 | 114.267 | 117.6865 | 114.2578 | 110.2615 | 122.7448 | 122.5983 | 117.421 | 122.9645 | 122.7631 | 122.8226 | 122.7722 | -122.9828 | -122.8317 | 122.6028 | 117.4301 | 113.5712 | 113.1409
605.3281 | 122.8958 | -117.8741 | 4.9759 | -0.0070953 | 0.0024203 | 0.14069 | 0.085708 | 0.0014291 | 0.69395 | 0.0015701 | -0.36291 | -0.00119 | 0.13969 | -0.0041166 | 1.0183 | 0.096555 | 0.0026383 | -4.1977 | 4.921 | -118.0069 | 4.6875 | -7.576 | -2.8748 | -0.53101 | -4.5868 | 4.8889 | -117.8192 | -0.48523 | 4.6646 | -3.3646 | 0.045776 | -0.13275 | -0.054932 | -0.28839 | 110.2982 | 117.3431 | 114.9994 | 117.4759 | 115.1321 | 0.054932 | -0.086975 | -5.4611 | 122.5388 | 117.9199 | 114.5096 | 117.865 | 114.4547 | 110.4309 | 122.6944 | 122.4838 | 117.334 | 122.9279 | 122.7081 | 122.7951 | 122.7631 | -122.9828 | -122.7951 | 122.5616 | 117.3889 | 113.6765 | 113.2874
606.3281 | 122.9279 | -117.746 | 5.0537 | -0.098648 | 0.0047701 | 0.14047 | 0.086562 | -0.00027993 | 0.6916 | -0.0014207 | -0.66504 | -0.01593 | 0.1335 | 0.0020786 | 1.013 | 0.093137 | 0.0034927 | -4.248 | 5.0491 | -117.8787 | 4.8431 | -7.4615 | -2.7328 | -0.64087 | -4.6555 | 4.9667 | -117.778 | -0.48065 | 4.8614 | -4.4266 | 0.064087 | -0.13275 | -0.004578 | -0.21057 | 110.2844 | 117.1051 | 115.0131 | 117.2379 | 115.1459 | -0.032043 | -0.086975 | -5.5344 | 122.6074 | 117.8101 | 113.3194 | 117.8421 | 113.3514 | 110.4172 | 122.7219 | 122.6395 | 117.2974 | 122.9279 | 122.7448 | 122.7951 | 122.7127 | -122.9324 | -122.8317 | 122.5891 | 117.2653 | 113.4979 | 113.0905
607.3281 | 122.8455 | -117.6407 | 5.1865 | -0.052872 | 0.0024203 | 0.14133 | 0.086349 | 0.0010019 | 0.6869 | 0.0015701 | -0.35071 | -0.002258 | 0.14012 | 0.002933 | 1.0164 | 0.098264 | 7.4746e-05 | -4.2664 | 5.1224 | -117.7689 | 4.8935 | -7.4249 | -2.8244 | -0.45776 | -4.7928 | 5.0446 | -117.6544 | -0.44403 | 4.9026 | -4.422 | 0.009155 | -0.12817 | -0.064087 | -0.29297 | 110.2158 | 117.1829 | 114.8163 | 117.3111 | 114.9445 | -0.013733 | -0.14191 | -5.6305 | 122.5433 | 117.6498 | 113.2187 | 117.6636 | 113.2324 | 110.3439 | 122.6624 | 122.5571 | 117.2104 | 122.8912 | 122.699 | 122.7631 | 122.6852 | -122.9553 | -122.8409 | 122.5342 | 117.1967 | 113.3743 | 112.8479
608.3438 | 122.9874 | -117.7002 | 5.0262 | -0.06813 | 0.0019931 | 0.14325 | 0.086135 | 0.0010019 | 0.68968 | -0.00099327 | -0.41785 | -0.0016172 | 0.13905 | 0.0020786 | 1.0121 | 0.097837 | 0.0011429 | -4.5959 | 5.0308 | -117.8604 | 4.8431 | -9.0134 | -2.6917 | -0.54474 | -4.7562 | 4.9393 | -117.7185 | -0.33875 | 4.8935 | -6.1157 | 0.13275 | -0.16022 | 0.004578 | -0.18311 | 108.6868 | 117.1555 | 115.0085 | 117.3157 | 115.1688 | -0.018311 | -0.086975 | -5.365 | 122.5937 | 117.8329 | 111.5845 | 117.8513 | 111.6028 | 108.847 | 122.7036 | 122.612 | 117.3798 | 122.8912 | 122.6578 | 122.731 | 122.6395 | -122.8867 | -122.7448 | 122.5433 | 117.3614 | 113.1042 | 112.944
609.3281 | 122.9599 | -118.0756 | 4.7058 | -0.037613 | 0.0030613 | 0.14304 | 0.083144 | 0.00078827 | 0.68989 | -0.0012071 | -0.36291 | -0.002258 | 0.13862 | -0.00091218 | 1.0175 | 0.097624 | -0.0018479 | -4.6967 | 4.6738 | -118.1992 | 4.5685 | -8.2306 | -2.504 | -0.4303 | -4.715 | 4.5776 | -118.0389 | -0.37537 | 4.5639 | -5.8594 | 0.10529 | -0.1236 | -0.032044 | -0.13733 | 109.845 | 117.6453 | 115.5716 | 117.7689 | 115.6952 | 0.036622 | -0.12817 | -5.0812 | 122.6395 | 118.1808 | 112.2162 | 118.1442 | 112.1796 | 109.9686 | 122.7676 | 122.6028 | 117.6636 | 122.8729 | 122.6166 | 122.7493 | 122.6532 | -122.905 | -122.7448 | 122.644 | 117.7002 | 113.3789 | 113.3606
610.3281 | 122.9095 | -118.158 | 4.6555 | -0.022354 | 0.0032749 | 0.14432 | 0.083785 | 0.0031381 | 0.68968 | 0.0019973 | -0.50024 | -0.0026852 | 0.14183 | 0.0050692 | 1.0192 | 0.096555 | -0.00077965 | -4.9072 | 4.6417 | -118.2953 | 4.4128 | -8.2031 | -2.5726 | -0.50812 | -4.9759 | 4.5914 | -118.1625 | -0.41657 | 4.422 | -5.603 | 0.032043 | -0.13733 | -0.013733 | -0.24261 | 109.9548 | 117.6498 | 115.5853 | 117.7872 | 115.7227 | -0.004578 | -0.064087 | -5.072 | 122.58 | 118.19 | 112.5549 | 118.1946 | 112.5595 | 110.0922 | 122.7081 | 122.5845 | 117.746 | 122.937 | 122.7539 | 122.7997 | 122.7493 | -122.9507 | -122.818 | 122.5708 | 117.7414 | 113.2507 | 113.1821
611.3281 | 122.818 | -118.2907 | 4.5044 | -0.045242 | 0.0019931 | 0.14581 | 0.083785 | 0.0033517 | 0.68882 | -0.00013887 | -0.39038 | -0.00076257 | 0.14226 | 0.0010104 | 1.0228 | 0.097624 | 0.0022109 | -4.8889 | 4.3716 | -118.5791 | 4.1107 | -8.0154 | -2.4902 | -0.5127 | -4.8477 | 4.2892 | -118.3777 | -0.37079 | 4.4724 | -4.9667 | 0.068665 | -0.28839 | -0.13275 | -0.39368 | 110.2753 | 117.778 | 115.8005 | 118.0664 | 116.0889 | -0.086976 | -0.21515 | -4.8752 | 122.7631 | 118.3594 | 113.324 | 118.4464 | 113.4109 | 110.5637 | 122.6898 | 122.85 | 118.0069 | 122.9507 | 122.6669 | 122.6624 | 122.58 | -123.0835 | -122.8821 | 122.4014 | 117.9199 | 113.4018 | 113.443
612.3281 | 122.905 | -118.5333 | 4.248 | -0.083389 | 0.0041293 | 0.14603 | 0.08464 | 0.0014291 | 0.68669 | 0.0019973 | -0.55212 | -0.0065304 | 0.14247 | 0.0069918 | 1.0209 | 0.098905 | -0.00013885 | -4.866 | 4.2526 | -118.6798 | 4.0192 | -7.7774 | -2.4628 | -0.50354 | -4.9347 | 4.1702 | -118.515 | -0.32959 | 4.0512 | -4.921 | 0.064087 | -0.14648 | 0.004578 | -0.22888 | 110.7559 | 118.0298 | 116.0706 | 118.1763 | 116.217 | 0.01831 | -0.07782 | -4.5776 | 122.5845 | 118.5974 | 113.6124 | 118.5791 | 113.5941 | 110.9024 | 122.699 | 122.5662 | 118.1854 | 122.9324 | 122.6852 | 122.7859 | 122.7036 | -122.9279 | -122.7631 | 122.5525 | 118.2037 | 113.6673 | 113.5986
613.3438 | 122.9324 | -118.4601 | 4.2892 | -0.23598 | -0.0080471 | 0.13898 | 0.085708 | -0.0081839 | 0.67131 | -0.0080429 | -0.74438 | -0.018921 | 0.23027 | 0.009128 | 1.0769 | 0.094419 | 0.0024245 | -4.921 | 4.3945 | -118.4372 | 4.1245 | -7.6584 | -2.4673 | -0.48523 | -4.9347 | 4.3716 | -118.1808 | -0.27924 | 4.0146 | -4.8798 | 0.018311 | 0.022888 | 0.10528 | -0.1648 | 110.8017 | 117.9749 | 115.9927 | 117.952 | 115.9698 | 0.27924 | 0.082397 | -4.5685 | 122.4747 | 118.4784 | 113.5803 | 118.1992 | 113.3011 | 110.7788 | 122.5616 | 122.1954 | 117.9016 | 122.8317 | 122.5525 | 122.8546 | 122.8317 | -122.7264 | -122.4701 | 122.5845 | 118.1808 | 113.5391 | 113.5254
614.3281 | 122.9324 | -118.4921 | 4.2755 | -0.022354 | 0.0026339 | 0.14944 | 0.08699 | -6.6126e-05 | 0.68562 | -0.00013887 | -0.427 | 0.00030543 | 0.15251 | 0.0061374 | 1.0382 | 0.095701 | 0.0015701 | -5.1132 | 4.2664 | -118.6523 | 4.0192 | -7.5851 | -2.504 | -0.48523 | -5.0491 | 4.2023 | -118.5059 | -0.29297 | 4.0466 | -4.8889 | 0.041199 | -0.16022 | -0.009156 | -0.25635 | 110.907 | 118.0069 | 115.9882 | 118.1671 | 116.1484 | -0.013733 | -0.073242 | -4.5685 | 122.5388 | 118.5333 | 113.6032 | 118.5471 | 113.6169 | 111.0672 | 122.6715 | 122.5525 | 118.2129 | 122.9187 | 122.7081 | 122.7585 | 122.6944 | -122.9279 | -122.7814 | 122.5113 | 118.1992 | 113.3789 | 113.443
615.3281 | 122.9279 | -118.7668 | 3.9688 | -0.060501 | 0.0034885 | 0.15094 | 0.084426 | -0.0013479 | 0.68541 | -0.0020615 | -0.36902 | -0.0035398 | 0.1523 | -0.0036892 | 1.0427 | 0.098478 | 0.0028519 | -5.159 | 3.9597 | -118.8858 | 3.8177 | -7.0175 | -2.3666 | -0.36621 | -4.985 | 3.8681 | -118.7622 | -0.2243 | 3.7994 | -4.7012 | 0.082397 | -0.11902 | -0.009155 | -0.15106 | 111.7493 | 118.4006 | 116.4001 | 118.5196 | 116.5192 | 0.004578 | -0.10071 | -4.1931 | 122.5662 | 118.8492 | 114.0656 | 118.8446 | 114.061 | 111.8683 | 122.7036 | 122.5616 | 118.5379 | 122.8455 | 122.6303 | 122.7264 | 122.6349 | -122.8546 | -122.731 | 122.5845 | 118.5425 | 113.6078 | 113.7817
616.3281 | 122.905 | -118.9178 | 3.8589 | -0.083389 | 0.0011385 | 0.1503 | 0.086135 | 0.0012155 | 0.68476 | -0.00056607 | -0.40564 | -0.00119 | 0.16276 | -0.00048498 | 1.0489 | 0.099119 | -0.00013885 | -5.0858 | 3.9001 | -118.9957 | 3.6026 | -6.7612 | -2.4719 | -0.43945 | -5.1407 | 3.7811 | -118.8995 | -0.30212 | 3.6072 | -4.7699 | 0.032043 | -0.07782 | 0.041198 | -0.25635 | 112.1567 | 118.4784 | 116.4459 | 118.5562 | 116.5237 | 0.018311 | -0.07782 | -4.1611 | 122.525 | 118.9499 | 114.1479 | 118.9316 | 114.1296 | 112.2345 | 122.5983 | 122.5067 | 118.5974 | 122.8958 | 122.6807 | 122.818 | 122.699 | -122.8546 | -122.7585 | 122.5204 | 118.6157 | 113.8321 | 113.7772
617.3281 | 122.9507 | -119.4763 | 3.2501 | -0.07576 | 0.0022067 | 0.15457 | 0.083358 | 0.0042063 | 0.68583 | 0.0019973 | -0.36597 | -0.00097617 | 0.15379 | -0.0011258 | 1.0576 | 0.098264 | 0.0011429 | -5.2734 | 3.2135 | -119.5862 | 3.1128 | -5.6625 | -2.3621 | -0.31128 | -4.9942 | 3.154 | -119.4901 | -0.16937 | 3.1265 | -4.541 | 0.10529 | -0.10986 | -0.036621 | -0.13733 | 113.8138 | 119.165 | 117.1143 | 119.2749 | 117.2241 | -0.013733 | -0.09613 | -3.4195 | 122.6028 | 119.5816 | 114.9353 | 119.5953 | 114.949 | 113.9236 | 122.699 | 122.6166 | 119.3207 | 122.7997 | 122.644 | 122.6898 | 122.6303 | -122.8363 | -122.7402 | 122.5891 | 119.3069 | 114.2029 | 114.4821
618.3438 | 122.8867 | -120.5841 | 2.1149 | -0.014725 | 0.0034885 | 0.15863 | 0.091689 | 0.033473 | 0.67515 | 0.047499 | -0.31714 | 0.017609 | 0.15977 | -0.0079618 | 1.0784 | 0.098692 | -0.015306 | -5.5847 | 2.1194 | -120.1767 | 1.4969 | -7.1228 | 0.17395 | 0.09613 | -5.2414 | 1.7715 | -120.0348 | -0.29297 | 1.767 | -4.8981 | -0.22888 | 0.40741 | 0.004578 | -0.61798 | 113.4613 | 120.6802 | 120.7581 | 120.2728 | 120.3506 | 0.54932 | -0.34332 | -2.4078 | 122.3511 | 120.3552 | 115.686 | 119.8059 | 115.1367 | 113.0539 | 121.6736 | 121.8018 | 119.7418 | 122.2961 | 121.8063 | 122.7036 | 122.3557 | -122.2916 | -122.1497 | 122.081 | 120.2911 | 114.9994 | 115.3427
619.3281 | 122.9782 | -120.1355 | 2.5223 | -0.083389 | 0.0024203 | 0.16077 | 0.084853 | -0.0032705 | 0.68562 | -0.00099327 | -0.32324 | -0.0014036 | 0.15892 | -0.0017666 | 1.0777 | 0.10147 | 0.0019973 | -5.3146 | 2.4902 | -120.1538 | 2.3438 | -6.0883 | -2.3849 | -0.62256 | -5.2689 | 2.3483 | -119.7372 | -0.19684 | 2.3438 | -5.072 | -0.073242 | -0.018311 | -0.032044 | -0.17853 | 114.0472 | 119.5129 | 117.7505 | 119.5312 | 117.7689 | 0.39825 | -0.17395 | -2.7191 | 122.4792 | 120.0623 | 115.0635 | 119.664 | 114.6652 | 114.0656 | 122.4976 | 122.081 | 119.5404 | 122.644 | 122.0856 | 122.6257 | 122.4838 | -122.6761 | -122.2595 | 122.4792 | 119.9387 | 114.8209 | 114.8666
620.3281 | 122.8912 | -120.8588 | 1.9043 | 0.038681 | 0.0017795 | 0.15991 | 0.086562 | -0.0015615 | 0.6916 | 0.0011429 | -0.43005 | 0.00030543 | 0.16383 | 0.001865 | 1.0839 | 0.10147 | 0.0015701 | -5.4611 | 1.886 | -120.9824 | 1.6754 | -6.4041 | -2.8015 | -0.56763 | -5.484 | 1.8265 | -120.3781 | -0.25635 | 1.6251 | -5.4337 | -0.32501 | -0.1236 | -0.018311 | -0.22888 | 114.4547 | 120.2911 | 118.0573 | 120.4147 | 118.1808 | 0.48065 | -0.07782 | -2.1606 | 122.4838 | 120.5338 | 115.4251 | 120.0531 | 114.9445 | 114.5782 | 122.6578 | 122.0032 | 120.1218 | 122.8683 | 122.2046 | 122.7448 | 122.6852 | -122.8867 | -122.2824 | 122.5342 | 120.6024 | 115.3976 | 115.3748
621.3281 | 122.9599 | -121.0785 | 1.6205 | -0.06813 | 0.0037021 | 0.18362 | 0.082931 | -0.00092073 | 0.68989 | 0.00050193 | -0.32019 | -0.0016172 | 0.16255 | -0.0013394 | 1.0905 | 0.10019 | 0.0026383 | -5.4108 | 1.5976 | -121.2021 | 1.4877 | -5.809 | -2.2705 | -0.53558 | -5.4611 | 1.4923 | -120.7947 | -0.16479 | 1.4786 | -5.2826 | 0.073242 | -0.1236 | -0.022888 | -0.13275 | 115.2695 | 120.5429 | 118.808 | 120.6665 | 118.9316 | 0.28381 | -0.12817 | -1.7853 | 122.5571 | 121.1517 | 115.7959 | 120.8679 | 115.5121 | 115.3931 | 122.6898 | 122.2733 | 120.6299 | 122.7997 | 122.287 | 122.6761 | 122.5708 | -122.8226 | -122.4152 | 122.5662 | 120.9137 | 115.6677 | 115.6174
622.3281 | 122.85 | -121.2341 | 1.561 | -0.052872 | 0.0019931 | 0.18512 | 0.083785 | 0.0027109 | 0.68711 | 0.0015701 | -0.35986 | 0.00051903 | 0.16746 | 0.0040012 | 1.0944 | 0.099333 | -0.0024887 | -5.5801 | 1.5106 | -121.376 | 1.2314 | -6.3126 | -2.4811 | -0.85602 | -5.7266 | 1.4465 | -120.8633 | -0.2655 | 1.2589 | -5.2963 | -0.20142 | -0.14191 | -0.050354 | -0.32959 | 114.9216 | 120.3781 | 118.7531 | 120.52 | 118.895 | 0.37079 | -0.11444 | -1.8265 | 122.493 | 121.0327 | 115.9378 | 120.6619 | 115.567 | 115.0635 | 122.6074 | 122.1222 | 120.5978 | 122.8867 | 122.3099 | 122.7448 | 122.6807 | -122.937 | -122.4243 | 122.4655 | 120.9686 | 115.654 | 115.5075
623.3281 | 123.0881 | -118.2266 | 4.3533 | -0.37331 | -0.00014308 | 0.016357 | 0.2895 | -0.0011343 | 0.0013843 | -0.0018479 | -0.045532 | -0.0033262 | 0.16148 | 0.00015602 | 0.024127 | 0.09741 | 0.00071555 | -0.11444 | 4.3213 | -0.1236 | 4.2618 | 0.091553 | 0.050354 | -0.018311 | -5.2094 | -2.3941 | -118.4052 | -0.19226 | -2.2934 | -3.9093 | 0.018311 | 118.103 | -0.032044 | -0.091553 | 118.3182 | 118.2083 | 118.277 | 0.10528 | 0.17395 | -0.17853 | -6.7474 | -4.5456 | 115.9332 | 118.2449 | 114.3173 | 118.4235 | 114.4958 | 0.21515 | 4.3854 | 116.1118 | 118.2129 | 4.4449 | 116.011 | 122.5479 | 115.8325 | -4.4769 | -122.7585 | 122.4884 | 118.0344 | 118.1122 | 113.0173
624.3281 | 122.9507 | -119.2566 | 3.4836 | -0.38094 | 0.00092492 | 0.015716 | 0.29378 | -0.0022025 | -0.0018201 | -0.0022751 | 0.070435 | 0.00051903 | 0.16084 | 0.001224 | 0.023913 | 0.09741 | 0.0039199 | -0.1236 | 3.447 | -0.13275 | 3.2593 | -0.009155 | -0.26093 | -0.27008 | -5.4977 | -1.0986 | -119.2978 | -0.2655 | -1.2634 | -4.6783 | -0.28381 | 119.1238 | -0.036622 | -0.22431 | 119.2474 | 118.9865 | 118.9957 | -0.13733 | -0.12817 | -0.041199 | -4.5822 | -3.7491 | 117.9932 | 118.9728 | 114.5782 | 119.014 | 114.6194 | 0.1236 | 3.392 | 118.0344 | 119.0323 | 3.5797 | 118.1992 | 122.7036 | 118.158 | -3.6163 | -122.7814 | 122.5159 | 118.9911 | 119.133 | 113.7588
625.3281 | 123.0423 | -119.7052 | 3.0029 | -0.35042 | 0.0024203 | 0.013366 | 0.29549 | -0.0034841 | -0.00032472 | 0.0024245 | 0.07959 | -0.0054624 | 0.16084 | -0.0028348 | 0.021777 | 0.096555 | 0.0049881 | -0.14191 | 2.9755 | -0.13733 | 2.8793 | 0.10986 | -0.018311 | -0.068665 | -5.5573 | -1.4145 | -119.7647 | -0.16022 | -1.4282 | -4.7333 | 0 | 119.5679 | -0.027466 | -0.1236 | 119.8151 | 119.6365 | 119.6869 | 0.068664 | 0.11902 | -0.059509 | -4.4174 | -3.1631 | 118.277 | 119.7052 | 114.9719 | 119.7647 | 115.0314 | 0.24719 | 3.0167 | 118.3365 | 119.6045 | 3.1128 | 118.3502 | 122.6807 | 118.2907 | -3.1403 | -122.7676 | 122.5845 | 119.545 | 119.5633 | 114.1479
626.3281 | 122.9553 | -120.1584 | 2.7191 | -0.41145 | 0.00049772 | 0.012726 | 0.2989 | -0.0013479 | -0.0011791 | -0.00035247 | 0.052124 | -0.0020444 | 0.16426 | -0.0036892 | 0.023058 | 0.09741 | 0.0028519 | -0.12817 | 2.655 | -0.15564 | 2.3849 | -0.036621 | -0.20599 | -0.32044 | -5.7266 | -1.6296 | -120.1355 | -0.2655 | -1.8173 | -5.1636 | -0.27008 | 120.0027 | -0.064087 | -0.33417 | 120.1218 | 119.838 | 119.9524 | -0.1648 | -0.050354 | 0.022888 | -4.3488 | -2.9846 | 118.3411 | 119.8883 | 114.9948 | 119.8654 | 114.9719 | 0.11902 | 2.5406 | 118.3182 | 119.87 | 2.8107 | 118.5059 | 122.8134 | 118.5287 | -2.8748 | -122.8546 | 122.5433 | 119.8929 | 120.0302 | 114.4318
627.3281 | 123.0606 | -120.5338 | 2.2797 | -0.40382 | -0.00014308 | 0.012298 | 0.29976 | -0.0024161 | 0.00010248 | -0.0022751 | -0.12183 | -0.002899 | 0.16597 | -0.00048498 | 0.023486 | 0.098264 | 0.0013565 | -0.059509 | 2.2522 | -0.13275 | 2.1286 | 0.07782 | 0.29755 | -0.018311 | -5.6076 | -1.4465 | -120.4697 | -0.15564 | -1.4145 | -5.0446 | 0.10986 | 120.401 | -0.027466 | -0.15106 | 120.6116 | 120.5154 | 120.8313 | 0.11444 | 0.4303 | 0.064086 | -3.7262 | -2.4353 | 119.1193 | 120.6436 | 115.4892 | 120.5795 | 115.4251 | 0.21057 | 2.2614 | 119.0552 | 120.314 | 2.3849 | 119.0231 | 122.7859 | 119.0872 | -2.4124 | -122.7493 | 122.6624 | 120.3781 | 120.4742 | 114.9261
628.3281 | 122.9599 | -121.1105 | 1.7761 | -0.38857 | -0.00035668 | 0.012512 | 0.30275 | 0.0012155 | 0.0018115 | -0.0016343 | 0.052124 | -0.0026852 | 0.17131 | 0.0014376 | 0.023272 | 0.097624 | 0.00050195 | -0.082397 | 1.7166 | -0.12817 | 1.5472 | 0.018311 | -0.041199 | -0.16937 | -6.0471 | -1.4008 | -121.0648 | -0.26093 | -1.5839 | -5.1773 | -0.086975 | 120.9824 | -0.059509 | -0.22888 | 121.1288 | 120.9412 | 121.0693 | -0.041199 | 0.086975 | 0.045777 | -3.1769 | -2.037 | 119.5267 | 121.0236 | 115.9332 | 120.9778 | 115.8875 | 0.14649 | 1.6754 | 119.4809 | 120.8038 | 1.8448 | 119.664 | 122.8271 | 119.7098 | -1.9043 | -122.8409 | 122.6578 | 120.8496 | 121.0281 | 115.0635
629.3281 | 123.056 | -121.3989 | 1.4236 | -0.40382 | 0.00049772 | 0.011871 | 0.30424 | 0.00036107 | 0.0024525 | -0.0020615 | 0.067383 | -0.003967 | 0.1696 | -0.0013394 | 0.023272 | 0.098051 | 7.4746e-05 | -0.086975 | 1.3779 | -0.13733 | 1.2497 | 0.07782 | -0.009155 | 0.009155 | -6.1935 | -1.3046 | -121.344 | -0.15106 | -1.3321 | -6.6284 | 0.13733 | 121.2616 | -0.045776 | -0.17395 | 121.4767 | 121.4081 | 121.3898 | 0.14648 | 0.12817 | 0.054932 | -2.7283 | -1.5747 | 120.0668 | 121.5363 | 114.7705 | 121.4813 | 114.7156 | 0.21515 | 1.387 | 120.0119 | 121.1929 | 1.5152 | 120.0394 | 122.7768 | 120.0943 | -1.561 | -122.7676 | 122.6486 | 121.2479 | 121.312 | 115.2054
630.3281 | 122.9919 | -121.5958 | 1.2955 | -0.37331 | 0.0011385 | 0.011657 | 0.30531 | 0.0027109 | 0.00074348 | 0.00050193 | 0.058227 | -0.002258 | 0.17195 | 0.001865 | 0.021777 | 0.098264 | 0.00028835 | -0.07782 | 1.181 | -0.13275 | 1.0757 | 0.059509 | -0.013733 | -0.045776 | -6.427 | -1.3687 | -121.5271 | -0.22888 | -1.4603 | -7.0038 | 0.045776 | 121.463 | -0.11444 | -0.21973 | 121.6553 | 121.55 | 121.582 | 0.086975 | 0.11902 | 0.068664 | -2.6642 | -1.5244 | 120.1355 | 121.6415 | 114.592 | 121.5729 | 114.5233 | 0.19226 | 1.2085 | 120.0668 | 121.2982 | 1.3138 | 120.1584 | 122.7768 | 120.2271 | -1.4282 | -122.8226 | 122.6715 | 121.3669 | 121.5179 | 115.1688
631.3281 | 123.0652 | -121.6919 | 1.1261 | -0.42671 | 0.0030613 | 0.0090939 | 0.30788 | 0.0024973 | 0.0020251 | -0.0012071 | 0.061279 | -0.0046078 | 0.17387 | 0.00079682 | 0.020709 | 0.096769 | 0.0037063 | 0.018311 | 1.0529 | -0.14191 | 0.94757 | 0.13733 | -0.036621 | -0.004578 | -6.5552 | -1.6067 | -121.6827 | -0.14648 | -1.6067 | -7.576 | 0.11444 | 121.55 | -0.073243 | -0.17853 | 121.8292 | 121.6873 | 121.6553 | 0.13733 | 0.10529 | 0.009156 | -2.7328 | -1.2726 | 120.0851 | 121.8063 | 114.1159 | 121.7972 | 114.1068 | 0.27924 | 1.0895 | 120.076 | 121.5363 | 1.1948 | 120.076 | 122.7448 | 120.0851 | -1.268 | -122.8088 | 122.6395 | 121.5454 | 121.7102 | 115.1367
632.3281 | 122.937 | -120.6711 | 2.0142 | -0.55641 | 0.0043429 | 0.014435 | 0.44459 | 0.0020701 | 0.0011707 | -0.0016343 | 0.061279 | -0.0014036 | 0.31294 | 0.0010104 | 0.023272 | 0.10061 | 0.0034927 | -0.13275 | 1.6251 | -0.10986 | 1.5564 | 0 | -0.37537 | -0.39368 | -6.5231 | -1.4786 | -120.9274 | -0.28381 | -1.5381 | -4.0558 | -0.34332 | 120.5612 | -0.3891 | -0.45776 | 120.6711 | 120.2774 | 120.2957 | -0.28381 | -0.2655 | -0.25635 | -3.4927 | -2.298 | 119.133 | 120.3278 | 116.6153 | 120.5841 | 116.8716 | 0.10986 | 1.6663 | 119.3893 | 120.6436 | 1.7349 | 119.4489 | 122.2961 | 119.1925 | -2.124 | -122.9416 | 122.2275 | 120.3873 | 120.5383 | 114.1479
633.3281 | 122.9874 | -61.2305 | 60.6445 | -0.045242 | -0.0022793 | 0.015075 | 0.035293 | 0.0024973 | 0.0020251 | -0.00099327 | 0.11011 | -0.0024716 | 0.0025464 | 0.00058322 | 0.023272 | 0.0044839 | 0.0058425 | -0.082397 | 0.1236 | -0.1236 | -0.16479 | 0.2243 | -0.16479 | -0.44861 | -0.082397 | 0.082397 | 0.20142 | 0.059509 | 0.13733 | 0.032043 | 0.013733 | 61.1069 | -60.5209 | -60.8093 | 61.4548 | 60.7819 | 61.0657 | -0.32501 | -0.041199 | 61.4319 | -60.5621 | -60.585 | 61.3678 | 61.2442 | 61.2625 | -0.18768 | -0.16937 | 0.3479 | -0.041199 | -0.064087 | -0.14191 | 0.24719 | -0.11902 | 61.3541 | 61.3129 | -60.7681 | -60.4431 | 61.0657 | 61.29 | 61.1481 | 61.1481
634.3281 | 122.2504 | -60.91 | 61.0977 | -0.022354 | -0.00057028 | 0.011017 | 0.038283 | 0.0010019 | -0.00053832 | -0.0018479 | 0.042969 | -0.0048216 | 0.0070326 | -5.7584e-05 | 0.022418 | 0.0021341 | 0.0011429 | -0.10986 | 0.14191 | -0.14648 | -0.07782 | -0.054932 | -0.31586 | -0.47607 | -0.13275 | 0.17853 | 0.20142 | -0.064087 | 0.009155 | -0.23804 | -0.3067 | 60.7636 | -60.9558 | -61.1755 | 60.8551 | 60.434 | 60.5942 | -0.32959 | -0.16937 | 61.1115 | -60.9192 | -61.1618 | 60.9192 | 60.6033 | 60.672 | -0.50812 | -0.43945 | 0.091552 | 0.068664 | -0.19226 | -0.2655 | 0.28839 | -0.022888 | 61.0519 | 61.0886 | -61.2442 | -60.8963 | 60.8322 | 60.8459 | 60.8002 | 60.7773
635.3281 | 122.6624 | -61.2717 | 61.2534 | -0.052872 | 7.0518e-05 | 0.01358 | 0.037002 | -0.0034841 | -0.00011112 | -0.00099327 | 0.10095 | -0.0016172 | 0.0072462 | -0.0036892 | 0.023486 | 0.0029887 | 0.00071555 | -0.073242 | 0.11444 | -0.13275 | 0.036621 | 0.1236 | 0.004578 | -0.12817 | -0.009155 | 0.13733 | -0.059509 | 0.1236 | 0.07782 | 0.068665 | 0.086975 | 61.1389 | -61.1389 | -61.2167 | 61.3953 | 61.1435 | 61.2762 | 0.004577 | 0.13733 | 61.2122 | -61.116 | -61.1298 | 61.3495 | 61.3586 | 61.3403 | 0.14648 | 0.12817 | 0.25635 | 0.16937 | 0.13733 | 0.1831 | 0.24719 | 0.19684 | 61.3861 | 61.409 | -61.3861 | -61.3129 | 61.3083 | 61.3953 | 61.1984 | 61.2625
636.3281 | 122.3831 | -60.9146 | 61.4639 | -0.060501 | -0.00035668 | 0.012298 | 0.03807 | -0.0017751 | -0.0028881 | -0.0022751 | 0.058227 | -0.0024716 | 0.0070326 | -0.0019804 | 0.022204 | 0.0023477 | 0.0056289 | -0.09613 | 0.12817 | -0.14191 | -0.041199 | 0.041199 | -0.13733 | -0.31586 | -0.10071 | 0.16937 | -0.10529 | -0.041199 | 0.050354 | -0.064087 | -0.16479 | 60.7727 | -61.3358 | -61.5051 | 60.9558 | 60.5988 | 60.7773 | -0.17395 | 0.004578 | 60.8093 | -61.2946 | -61.5051 | 60.965 | 60.7498 | 60.8505 | -0.059509 | 0.041199 | 0.18311 | 0.10071 | 0.15564 | 0.064087 | 0.27008 | 0.27466 | 61.0428 | 61.084 | -61.6058 | -61.5692 | 60.8734 | 60.8734 | 60.8185 | 60.8139
637.3281 | 122.438 | -61.1526 | 61.4685 | -0.07576 | -0.00057028 | 0.012298 | 0.038497 | 0.00078827 | 0.00074348 | -0.0016343 | 0.0979 | -0.0016172 | 0.0072462 | -0.0013394 | 0.021563 | 0.0044839 | 0.0011429 | -0.064087 | 0.14191 | -0.11902 | 0.032043 | 0.10986 | 0.022888 | -0.073242 | 0.032043 | 0.16022 | -0.10529 | 0.054932 | 0.15106 | 0.086975 | 0.1236 | 61.0336 | -61.3266 | -61.4365 | 61.2625 | 61.0794 | 61.1755 | 0.045777 | 0.14191 | 61.0474 | -61.3083 | -61.4136 | 61.3037 | 61.2762 | 61.2396 | 0.22888 | 0.19226 | 0.22888 | 0.15106 | 0.25635 | 0.16022 | 0.26093 | 0.2655 | 61.2946 | 61.3129 | -61.5875 | -61.5738 | 61.1847 | 61.2076 | 61.0886 | 61.1847
638.3281 | 122.1359 | -60.8597 | 61.4822 | -0.16731 | -0.00078408 | 0.013366 | 0.038497 | -0.0026297 | 0.00074348 | -0.00056607 | 0.055176 | -0.0037534 | 0.0083142 | 0.001224 | 0.022204 | 0.0046977 | 0.0011429 | -0.07782 | 0.14191 | -0.1236 | -0.013733 | 0.086975 | -0.009155 | -0.21057 | -0.059509 | 0.16022 | -0.14191 | -0.004578 | 0.082397 | 0.022888 | -0.032043 | 60.7361 | -61.3403 | -61.496 | 60.9467 | 60.6491 | 60.8505 | -0.086975 | 0.11444 | 60.7178 | -61.322 | -61.4868 | 60.9421 | 60.8276 | 60.8826 | 0.10986 | 0.16479 | 0.21057 | 0.10986 | 0.2243 | 0.13733 | 0.2655 | 0.30212 | 61.0016 | 61.0199 | -61.6058 | -61.6241 | 60.8459 | 60.8551 | 60.7819 | 60.8002
639.3281 | 122.6212 | -61.0794 | 61.4502 | -0.06813 | -0.00078408 | 0.012512 | 0.038711 | -0.0036977 | 0.0024525 | 0.00050193 | 0.10095 | -0.0020444 | 0.0059644 | -0.0058256 | 0.023272 | 0.0027751 | -0.00035245 | -0.082397 | 0.14191 | -0.1236 | -0.082397 | 0.20599 | -0.032043 | -0.13733 | -0.032043 | 0.13733 | -0.11444 | 0.050354 | 0.16479 | 0.091553 | 0.1236 | 60.9558 | -61.3083 | -61.5326 | 61.2854 | 60.9421 | 61.0474 | -0.013733 | 0.091553 | 60.965 | -61.3129 | -61.3998 | 61.2442 | 61.203 | 61.171 | 0.23804 | 0.20599 | 0.32959 | 0.041199 | 0.27924 | 0.16479 | 0.2655 | 0.25177 | 61.2213 | 61.2167 | -61.5738 | -61.5646 | 60.997 | 61.1298 | 60.997 | 61.0474
640.3281 | 122.5113 | -60.7178 | 61.4914 | -0.22835 | -0.00014308 | 0.012726 | 0.039565 | -6.6126e-05 | 0.00031608 | -0.0024887 | 0.042969 | -0.00119 | 0.0063916 | -5.7584e-05 | 0.023913 | 0.0023477 | -0.00035245 | -0.10529 | 0.14191 | -0.16022 | -0.054932 | 0.022888 | -0.068665 | -0.28381 | -0.11902 | 0.1831 | -0.14648 | -0.073242 | 0.050354 | -0.045776 | -0.07782 | 60.5576 | -61.3495 | -61.5463 | 60.7407 | 60.434 | 60.6491 | -0.1236 | 0.091552 | 60.5713 | -61.3083 | -61.5646 | 60.7681 | 60.64 | 60.672 | 0.068664 | 0.10071 | 0.1831 | 0.10528 | 0.19684 | 0.073242 | 0.30212 | 0.32959 | 60.8597 | 60.9009 | -61.6516 | -61.6379 | 60.6628 | 60.6445 | 60.6125 | 60.5988
641.3281 | 122.6944 | -61.1847 | 61.4456 | -0.029984 | -0.0012113 | 0.013794 | 0.038283 | -0.00070713 | 0.00074348 | -0.00013887 | 0.058227 | -0.002258 | 0.0057508 | -0.0077482 | 0.021349 | 0.0053385 | 0.0022109 | -0.068665 | 0.13275 | -0.12817 | 0.032043 | 0.13733 | 0.045776 | -0.009155 | 0.009155 | 0.13733 | -0.10986 | -0.068665 | 0.28839 | 0.027466 | 0.064087 | 61.0565 | -61.3129 | -61.4136 | 61.322 | 61.1755 | 61.2305 | 0.11902 | 0.17395 | 61.0748 | -61.3083 | -61.5143 | 61.4731 | 61.2488 | 61.2122 | 0.17395 | 0.13733 | 0.2655 | 0.16022 | 0.39825 | 0.041198 | 0.26093 | 0.24719 | 61.3174 | 61.322 | -61.5738 | -61.5555 | 61.2167 | 61.116 | 61.116 | 61.1938
642.3281 | 122.2321 | -60.8459 | 61.4685 | -0.21309 | -0.0018521 | 0.013794 | 0.040633 | -0.0036977 | -0.00032472 | -0.00035247 | 0.052124 | -0.0035398 | 0.0048962 | 0.0014376 | 0.022845 | 0.0040567 | 0.0028519 | -0.082397 | 0.13275 | -0.13275 | -0.018311 | 0.054932 | -0.022888 | -0.11902 | -0.068665 | 0.15564 | -0.1236 | -0.032043 | 0.064087 | -0.013733 | 0.027466 | 60.7132 | -61.3358 | -61.4868 | 60.9009 | 60.7269 | 60.8231 | 0.013732 | 0.10986 | 60.7224 | -61.3129 | -61.5005 | 60.91 | 60.8734 | 60.8322 | 0.15106 | 0.10986 | 0.18768 | 0.11444 | 0.18768 | 0.091553 | 0.2655 | 0.27924 | 60.9787 | 61.0016 | -61.6013 | -61.5921 | 60.8276 | 60.8139 | 60.7636 | 60.7773
643.3281 | 122.9645 | -61.322 | 61.496 | -0.091019 | -0.0018521 | 0.012085 | 0.038497 | -0.0024161 | 0.0011707 | -0.0012071 | 0.070435 | -0.0041806 | 0.0063916 | -0.00048498 | 0.023272 | 0.0034159 | -0.0035569 | -0.11444 | 0.11902 | -0.14648 | -0.018311 | 0.073242 | -0.027466 | -0.07782 | -0.054932 | 0.16479 | -0.10529 | 0.041199 | 0.15106 | 0.064087 | 0.11902 | 61.1755 | -61.377 | -61.5143 | 61.3953 | 61.2442 | 61.2946 | 0.068664 | 0.11902 | 61.2167 | -61.3312 | -61.4548 | 61.4731 | 61.441 | 61.3861 | 0.22431 | 0.16937 | 0.21973 | 0.12817 | 0.25635 | 0.14649 | 0.2655 | 0.27008 | 61.441 | 61.4868 | -61.6425 | -61.6013 | 61.3037 | 61.3632 | 61.2076 | 61.2671
644.3281 | 122.4701 | -60.9467 | 61.4594 | -0.07576 | -0.0016385 | 0.012512 | 0.040633 | -0.00049353 | -0.00075192 | -0.0039841 | 0.058227 | -0.002258 | 0.0059644 | -0.0034756 | 0.020709 | 0.0044839 | 0.0043471 | -0.073242 | 0.13275 | -0.10986 | 0.013733 | 0.10071 | 0.004578 | -0.054932 | -0.041199 | 0.16479 | -0.13275 | 0.009155 | 0.11444 | 0.036621 | 0.09613 | 60.8368 | -61.3266 | -61.4456 | 61.0474 | 60.8917 | 60.9512 | 0.054931 | 0.11444 | 60.8139 | -61.2946 | -61.4502 | 61.0611 | 61.0428 | 60.9833 | 0.22888 | 0.16937 | 0.21057 | 0.1236 | 0.24719 | 0.14191 | 0.24261 | 0.29755 | 61.0794 | 61.1114 | -61.5692 | -61.5921 | 60.9604 | 60.9558 | 60.8734 | 60.9055
645.3281 | 122.9553 | -61.3037 | 61.4639 | -0.037613 | -0.0016385 | 0.011657 | 0.037215 | -0.00049353 | 0.00095708 | 0.0013565 | 0.064331 | -0.0016172 | 0.0057508 | -0.002194 | 0.024127 | 0.0029887 | -0.00077965 | -0.09613 | 0.12817 | -0.1236 | 0 | 0.091553 | 0.009155 | -0.036621 | -0.004578 | 0.15106 | -0.09613 | 0.064087 | 0.16937 | 0.091553 | 0.13275 | 61.1801 | -61.3358 | -61.4639 | 61.3953 | 61.2671 | 61.3129 | 0.086975 | 0.13275 | 61.2076 | -61.3129 | -61.3998 | 61.4731 | 61.4365 | 61.3953 | 0.22888 | 0.18768 | 0.21515 | 0.1236 | 0.2655 | 0.16022 | 0.25177 | 0.24719 | 61.4319 | 61.4548 | -61.5875 | -61.5601 | 61.3037 | 61.3678 | 61.2076 | 61.2991
646.3281 | 122.7081 | -61.0931 | 61.4594 | -0.12154 | 7.0518e-05 | 0.01123 | 0.037643 | 0.0022837 | 0.0013843 | -0.0022751 | 0.02771 | -0.0041806 | 0.00511 | -0.0090298 | 0.023486 | 0.0012797 | -0.0029159 | -0.064087 | 0.10529 | -0.12817 | 0.027466 | 0.11444 | 0.009155 | -0.050354 | -0.013733 | 0.14191 | -0.10529 | 0.054932 | 0.15564 | 0.059509 | 0.11444 | 60.965 | -61.3541 | -61.4319 | 61.2076 | 61.0428 | 61.1023 | 0.07782 | 0.13733 | 60.9879 | -61.3174 | -61.4044 | 61.2488 | 61.2076 | 61.1526 | 0.21973 | 0.16479 | 0.24262 | 0.15564 | 0.26093 | 0.16022 | 0.23346 | 0.24719 | 61.1984 | 61.235 | -61.5875 | -61.5646 | 61.1206 | 61.1481 | 61.0291 | 61.0794
647.3281 | 122.9736 | -61.3129 | 61.496 | 0.00053424 | -0.00057028 | 0.012726 | 0.038497 | -0.0045523 | 0.00031608 | -0.0022751 | 0.067383 | -0.002899 | 0.0066052 | -0.003262 | 0.022204 | 0.0040567 | -0.00013885 | -0.082397 | 0.13733 | -0.11444 | 0.022888 | 0.12817 | 0.032043 | -0.036621 | 0.004578 | 0.16937 | -0.068665 | 0.054932 | 0.1831 | 0.10071 | 0.13275 | 61.1984 | -61.3586 | -61.4731 | 61.441 | 61.2762 | 61.3449 | 0.07782 | 0.14648 | 61.2442 | -61.3266 | -61.441 | 61.496 | 61.4456 | 61.4136 | 0.20142 | 0.16937 | 0.24262 | 0.13733 | 0.25177 | 0.1236 | 0.25177 | 0.23804 | 61.4502 | 61.4822 | -61.6104 | -61.5646 | 61.3358 | 61.3678 | 61.2305 | 61.3174
648.3281 | 122.85 | -61.2625 | 61.4822 | -0.022354 | -0.0020657 | 0.014007 | 0.039779 | -0.00070713 | -0.0024609 | -0.0020615 | 0.12842 | -0.00119 | 0.006178 | 0.00058322 | 0.022631 | 0.0025613 | 0.0022109 | -0.07782 | 0.11902 | -0.12817 | 0.013733 | 0.13733 | 0.022888 | 0 | -0.1831 | 0.1236 | -0.11444 | 0.041199 | 0.11902 | 0.086975 | 0.1236 | 61.1343 | -61.3632 | -61.4685 | 61.3998 | 61.2625 | 61.2854 | 0.12817 | 0.15106 | 61.1481 | -61.3586 | -61.441 | 61.3815 | 61.3861 | 61.3495 | 0.23804 | 0.20142 | 0.2655 | 0.14191 | 0.23346 | 0.15564 | 0.24719 | 0.23804 | 61.3815 | 61.3861 | -61.6104 | -61.5967 | 61.2762 | 61.3037 | 61.1847 | 61.0794
649.3281 | 123.0972 | -61.3495 | 61.4777 | -0.10628 | -0.0012113 | 0.012298 | 0.037643 | 0.00036107 | -0.00096552 | 0.00050193 | 0.04602 | -0.003967 | 0.006819 | -0.00048498 | 0.022631 | -0.00064293 | 0.0030655 | -0.12817 | 0.054932 | -0.13275 | -0.068665 | 0.036621 | -0.059509 | -0.10529 | -0.09613 | 0.16479 | -0.10529 | 0 | 0.10071 | 0.027466 | 0.09613 | 61.2167 | -61.4227 | -61.5463 | 61.3861 | 61.2442 | 61.29 | 0.027465 | 0.073242 | 61.2442 | -61.3129 | -61.4777 | 61.4502 | 61.4456 | 61.377 | 0.20142 | 0.13275 | 0.16937 | 0.064086 | 0.20599 | 0.10529 | 0.18768 | 0.27008 | 61.4044 | 61.5143 | -61.6104 | -61.5829 | 61.2808 | 61.3495 | 61.2213 | 61.2534
650.3281 | 123.0423 | -61.3129 | 61.441 | -0.045242 | -0.0020657 | 0.011871 | 0.040206 | -0.00027993 | -0.00032472 | -0.0018479 | 0.058227 | -0.003967 | 0.0040418 | -0.0056118 | 0.021349 | 0.0025613 | 0.0062697 | -0.086975 | 0.12817 | -0.10986 | 0.032043 | 0.13733 | 0.009155 | -0.022888 | 0.013733 | 0.13733 | -0.082397 | 0.073242 | 0.17395 | 0.11902 | 0.15106 | 61.203 | -61.3129 | -61.409 | 61.4502 | 61.29 | 61.322 | 0.086975 | 0.11902 | 61.2305 | -61.3037 | -61.3678 | 61.4868 | 61.4639 | 61.4319 | 0.23346 | 0.20142 | 0.24719 | 0.14191 | 0.25635 | 0.15564 | 0.23804 | 0.21973 | 61.441 | 61.4502 | -61.5509 | -61.5234 | 61.3449 | 61.3861 | 61.2259 | 61.3266
651.3281 | 123.0972 | -61.322 | 61.4548 | -0.06813 | -0.0018521 | 0.015075 | 0.038711 | 0.00078827 | -0.0011791 | -0.00056607 | 0.033813 | -0.002258 | 0.006178 | -0.002194 | 0.022418 | 0.0012797 | -0.00056605 | -0.13733 | 0.11444 | -0.10529 | -0.041199 | 0.064087 | -0.073242 | -0.10986 | -0.09613 | 0.16022 | -0.10529 | -0.059509 | 0.073242 | -0.027466 | 0.036621 | 61.2167 | -61.3403 | -61.496 | 61.3861 | 61.2122 | 61.2488 | -0.004577 | 0.032044 | 61.2167 | -61.2946 | -61.5143 | 61.3953 | 61.3586 | 61.2946 | 0.14191 | 0.07782 | 0.16937 | 0.064087 | 0.17853 | 0.045777 | 0.21973 | 0.2655 | 61.4365 | 61.4822 | -61.5601 | -61.5601 | 61.2808 | 61.2625 | 61.1847 | 61.2259
652.3281 | 123.0148 | -61.2991 | 61.4822 | -0.029984 | 0.00028412 | 0.010376 | 0.039565 | 0.0012155 | 0.0011707 | -0.0014207 | 0.055176 | -0.0037534 | 0.0089552 | -0.0026212 | 0.022631 | 0.0040567 | -0.00013885 | -0.10071 | 0.14191 | -0.11444 | 0.022888 | 0.13733 | 0.032043 | -0.018311 | 0.009155 | 0.15106 | -0.09613 | 0.041199 | 0.14191 | 0.15106 | 0.18768 | 61.1847 | -61.3403 | -61.4594 | 61.4365 | 61.2808 | 61.3312 | 0.09613 | 0.14648 | 61.203 | -61.3312 | -61.441 | 61.441 | 61.4868 | 61.4502 | 0.28381 | 0.24719 | 0.25177 | 0.13733 | 0.23804 | 0.13733 | 0.25635 | 0.24719 | 61.441 | 61.4502 | -61.5967 | -61.5784 | 61.322 | 61.3403 | 61.1984 | 61.3083
653.3281 | 123.0743 | -61.3541 | 61.4868 | -0.037613 | -0.00078408 | 0.01123 | 0.037643 | 0.0014291 | -0.00053832 | -0.0031297 | -0.045532 | -0.0024716 | 0.0070326 | -0.0028348 | 0.021136 | 0.0029887 | 0.0058425 | -0.14191 | 0.13733 | -0.13275 | -0.064087 | 0.050354 | -0.14191 | -0.2655 | -0.11444 | 0.09613 | -0.073242 | -0.009155 | 0.073242 | 0.018311 | 0.082397 | 61.2213 | -61.3495 | -61.5509 | 61.4044 | 61.0886 | 61.2122 | -0.13275 | -0.009156 | 61.2808 | -61.3907 | -61.496 | 61.4273 | 61.4365 | 61.3724 | 0.15564 | 0.091553 | 0.18311 | 0.068664 | 0.14648 | 0.064087 | 0.27008 | 0.16937 | 61.4914 | 61.4502 | -61.6196 | -61.5601 | 61.29 | 61.3449 | 61.2122 | 61.2396
654.3281 | 123.1522 | -61.3403 | 61.4777 | -0.045242 | 0.00071132 | 0.011017 | 0.039138 | 0.00036107 | -0.00032472 | 0.00050193 | 0.042969 | -0.0043942 | 0.0053236 | -5.7584e-05 | 0.01964 | 0.0032023 | 0.0041335 | -0.10986 | 0.1236 | -0.11444 | 0 | 0.11902 | 0 | -0.045776 | -0.018311 | 0.16022 | -0.064087 | 0.045776 | 0.14648 | 0.10529 | 0.13275 | 61.2259 | -61.3541 | -61.4777 | 61.4594 | 61.2946 | 61.3403 | 0.068665 | 0.11444 | 61.2762 | -61.3174 | -61.4319 | 61.4868 | 61.4731 | 61.4456 | 0.19684 | 0.16937 | 0.23346 | 0.11444 | 0.21057 | 0.10986 | 0.23804 | 0.2243 | 61.4639 | 61.5005 | -61.5921 | -61.5417 | 61.3403 | 61.3861 | 61.2305 | 61.322
655.3281 | 123.0835 | -61.3541 | 61.4685 | -0.083389 | -0.00099768 | 0.01358 | 0.039352 | -0.00092073 | 0.00095708 | 0.0011429 | -0.0058593 | -0.0031126 | 0.007887 | -0.0036892 | 0.022418 | 0.0046977 | 0.0022109 | -0.13733 | 0.14191 | -0.11902 | -0.036621 | 0.059509 | -0.068665 | -0.086975 | -0.10529 | 0.14648 | -0.10986 | 0.004578 | 0.082397 | 0.018311 | 0.073242 | 61.235 | -61.3266 | -61.5051 | 61.4136 | 61.2671 | 61.2854 | 0.032044 | 0.050354 | 61.2442 | -61.322 | -61.4639 | 61.4365 | 61.4273 | 61.3724 | 0.18311 | 0.12817 | 0.17853 | 0.082398 | 0.19226 | 0.11444 | 0.26093 | 0.25635 | 61.496 | 61.5005 | -61.5875 | -61.5784 | 61.3174 | 61.3586 | 61.2167 | 61.2488
656.3281 | 123.1476 | -61.3403 | 61.4639 | -0.037613 | -0.00014308 | 0.012726 | 0.037856 | 0.0010019 | 0.00031608 | -0.0020615 | 0.030762 | -0.0016172 | 0.0066052 | 0.0057102 | 0.021777 | 0.0023477 | 0.0017837 | -0.13733 | 0.13275 | -0.1236 | -0.022888 | 0.073242 | -0.027466 | -0.068665 | -0.07782 | 0.14648 | -0.10071 | 0.041199 | 0.12817 | 0.068665 | 0.11902 | 61.2167 | -61.3312 | -61.4868 | 61.4136 | 61.2717 | 61.3129 | 0.054931 | 0.09613 | 61.2396 | -61.3174 | -61.4227 | 61.4685 | 61.4594 | 61.409 | 0.21973 | 0.16937 | 0.19684 | 0.10071 | 0.22888 | 0.14191 | 0.25635 | 0.24719 | 61.4731 | 61.4868 | -61.5875 | -61.5646 | 61.3174 | 61.3815 | 61.203 | 61.2625
657.3281 | 123.1064 | -61.3586 | 61.4639 | -0.06813 | -0.0024929 | 0.01358 | 0.03807 | -0.00049353 | -0.00032472 | -0.0020615 | 0.012451 | -0.0031126 | 0.0055372 | -0.0028348 | 0.022418 | 0.0017069 | -0.00035245 | -0.1236 | 0.10529 | -0.12817 | 0.004578 | 0.10529 | -0.041199 | -0.068665 | -0.054932 | 0.15106 | -0.10986 | 0.050354 | 0.09613 | 0.018311 | 0.086975 | 61.2305 | -61.3586 | -61.4594 | 61.4639 | 61.29 | 61.3174 | 0.059509 | 0.086975 | 61.2488 | -61.3129 | -61.4136 | 61.4548 | 61.4456 | 61.377 | 0.19684 | 0.12817 | 0.23346 | 0.13275 | 0.20599 | 0.16022 | 0.23346 | 0.26093 | 61.4639 | 61.5097 | -61.5921 | -61.5738 | 61.3632 | 61.409 | 61.235 | 61.3037
658.3281 | 123.1247 | -61.3541 | 61.4777 | -0.014725 | -0.0024929 | 0.012726 | 0.039992 | -0.0015615 | -0.0013929 | -0.0016343 | 0.02771 | -0.0035398 | 0.004469 | 0.0042148 | 0.022845 | 0.0027751 | 0.0047745 | -0.25177 | 0.068665 | -0.12817 | -0.054932 | 0.013733 | -0.068665 | -0.086975 | -0.12817 | 0.14191 | -0.11444 | 0.013733 | 0.10071 | 0.054932 | 0.10071 | 61.2259 | -61.409 | -61.5326 | 61.3678 | 61.2671 | 61.2854 | 0.041199 | 0.059509 | 61.2396 | -61.3358 | -61.4639 | 61.4548 | 61.4548 | 61.409 | 0.21515 | 0.16937 | 0.14191 | 0.073242 | 0.21515 | 0.12817 | 0.19684 | 0.25635 | 61.4227 | 61.496 | -61.6058 | -61.5921 | 61.2991 | 61.3678 | 61.1023 | 61.2259
659.3281 | 123.1064 | -61.3586 | 61.4731 | -0.060501 | 0.0013523 | 0.01358 | 0.039565 | -0.0017751 | 0.00010248 | -0.0037705 | -0.048584 | -0.0018308 | 0.0055372 | -0.0036892 | 0.021136 | 0.0032023 | -0.0033433 | -0.1236 | 0.11902 | -0.11444 | -0.009155 | 0.064087 | -0.064087 | -0.073242 | -0.07782 | 0.16022 | -0.086975 | 0.004578 | 0.086975 | 0.022888 | 0.073242 | 61.2442 | -61.3541 | -61.4822 | 61.4227 | 61.2854 | 61.2946 | 0.041199 | 0.050354 | 61.2717 | -61.3129 | -61.4685 | 61.4456 | 61.4319 | 61.3815 | 0.16022 | 0.10986 | 0.17853 | 0.10529 | 0.17395 | 0.091553 | 0.23346 | 0.24719 | 61.4777 | 61.5189 | -61.5875 | -61.5601 | 61.3495 | 61.3632 | 61.235 | 61.2808
660.3281 | 123.143 | -61.3037 | 61.4594 | -0.052872 | -0.0012113 | 0.010376 | 0.03807 | -0.00049353 | 0.00095708 | -0.0027023 | 0.0093995 | -0.0020444 | 0.0048962 | -0.0041166 | 0.022204 | 0.0029887 | -0.00099325 | -0.12817 | 0.13733 | -0.1236 | 0.013733 | 0.10986 | 0.004578 | 0 | -0.004578 | 0.16937 | -0.082397 | 0.07782 | 0.13733 | 0.10071 | 0.14191 | 61.1801 | -61.322 | -61.4456 | 61.4136 | 61.3037 | 61.3083 | 0.1236 | 0.12817 | 61.2213 | -61.29 | -61.3815 | 61.441 | 61.4456 | 61.4044 | 0.2243 | 0.18311 | 0.23346 | 0.13733 | 0.21973 | 0.16022 | 0.26093 | 0.25177 | 61.441 | 61.4731 | -61.5829 | -61.5417 | 61.3174 | 61.3815 | 61.1755 | 61.2991
661.3281 | 123.1247 | -61.3449 | 61.4639 | -0.037613 | -0.00014308 | 0.012939 | 0.039138 | 0.0029245 | 0.00052988 | -0.0016343 | -0.0058593 | -0.0035398 | 0.0070326 | -0.002194 | 0.022204 | 0.0038431 | 0.0011429 | -0.11902 | 0.10986 | -0.10529 | 0.004578 | 0.10529 | -0.041199 | -0.022888 | -0.036621 | 0.15106 | -0.11902 | 0.045776 | 0.09613 | 0.036621 | 0.09613 | 61.2396 | -61.3541 | -61.4594 | 61.4502 | 61.322 | 61.3037 | 0.082398 | 0.064087 | 61.2259 | -61.3129 | -61.4182 | 61.441 | 61.441 | 61.3815 | 0.21515 | 0.15564 | 0.21057 | 0.10986 | 0.21515 | 0.16479 | 0.21515 | 0.27008 | 61.4548 | 61.496 | -61.5692 | -61.5829 | 61.3495 | 61.3907 | 61.2259 | 61.3083
662.3281 | 123.1155 | -61.3724 | 61.4822 | -0.091019 | -0.0020657 | 0.012512 | 0.039138 | 0.00014747 | -0.0013929 | -0.0029159 | -0.0089111 | -0.002258 | 0.0055372 | -0.0013394 | 0.021777 | 0.0012797 | 0.0017837 | -0.14648 | 0.1236 | -0.11444 | -0.041199 | 0.045776 | -0.054932 | -0.018311 | -0.15564 | 0.10071 | -0.10529 | -0.032043 | 0.064087 | 0.004578 | 0.086975 | 61.2579 | -61.3586 | -61.5234 | 61.4182 | 61.3541 | 61.3174 | 0.09613 | 0.059509 | 61.2671 | -61.3815 | -61.5143 | 61.4365 | 61.4594 | 61.377 | 0.19226 | 0.10986 | 0.16022 | 0.073242 | 0.16937 | 0.073243 | 0.23804 | 0.20599 | 61.496 | 61.4731 | -61.5967 | -61.5875 | 61.3312 | 61.3403 | 61.2259 | 61.2167
663.3281 | 123.1705 | -61.3541 | 61.4594 | -0.098648 | -0.00014308 | 0.018921 | 0.04042 | 0.0029245 | 0.00095708 | -0.0027023 | -0.036377 | -0.0041806 | 0.0057508 | 0.0031466 | 0.022631 | 0.0042703 | -0.00056605 | -0.29755 | 0.10529 | -0.11444 | 0.018311 | 0.082397 | -0.041199 | 0.022888 | -0.032043 | 0.11902 | -0.10986 | 0.059509 | 0.14191 | 0.054932 | 0.11902 | 61.2396 | -61.3541 | -61.441 | 61.4365 | 61.377 | 61.3129 | 0.13733 | 0.073242 | 61.2442 | -61.3403 | -61.3998 | 61.496 | 61.4731 | 61.409 | 0.22888 | 0.16479 | 0.19684 | 0.13275 | 0.25177 | 0.16937 | 0.21973 | 0.22888 | 61.4594 | 61.4731 | -61.5738 | -61.5692 | 61.3724 | 61.4136 | 61.0565 | 61.322
664.3281 | 123.1247 | -61.3678 | 61.5051 | -0.14442 | 0.0024203 | 0.011444 | 0.039138 | -0.0028433 | 0.00095708 | -0.0033433 | -0.015015 | -0.0016172 | 0.006819 | 0.0031466 | 0.021136 | 0.0027751 | 0.00071555 | -0.15106 | 0.13275 | -0.10986 | -0.027466 | 0.07782 | -0.059509 | -0.041199 | -0.086975 | 0.16022 | -0.082397 | 0.018311 | 0.086975 | 0.018311 | 0.07782 | 61.2579 | -61.3724 | -61.5326 | 61.4456 | 61.3266 | 61.3083 | 0.068664 | 0.050354 | 61.2854 | -61.3449 | -61.4868 | 61.4548 | 61.4456 | 61.3861 | 0.16022 | 0.10071 | 0.18768 | 0.082397 | 0.16937 | 0.10071 | 0.24261 | 0.24261 | 61.5005 | 61.528 | -61.615 | -61.5875 | 61.3403 | 61.3861 | 61.2167 | 61.2808
665.3281 | 123.1659 | -61.3678 | 61.496 | -0.16731 | -0.00014308 | 0.012939 | 0.038924 | -0.0015615 | 0.00031608 | 0.00028833 | -0.051636 | -0.00076257 | 0.0076734 | -0.001553 | 0.02199 | 0.0042703 | 0.00050195 | -0.15564 | 0.1236 | -0.13733 | -0.018311 | 0.064087 | -0.027466 | -0.027466 | -0.059509 | 0.13733 | -0.11902 | 0.064087 | 0.12817 | 0.045776 | 0.15106 | 61.2305 | -61.3724 | -61.5143 | 61.4319 | 61.3403 | 61.3403 | 0.10986 | 0.10986 | 61.2488 | -61.3586 | -61.4319 | 61.496 | 61.5189 | 61.4136 | 0.27008 | 0.16479 | 0.20142 | 0.11902 | 0.24719 | 0.18311 | 0.26093 | 0.25635 | 61.4914 | 61.5051 | -61.6333 | -61.615 | 61.3495 | 61.4319 | 61.2122 | 61.3083
666.3281 | 123.1155 | -61.3678 | 61.4639 | -0.12917 | 0.00092492 | 0.014221 | 0.038711 | -0.0026297 | -0.00011112 | -0.0020615 | -0.011963 | -0.0020444 | 0.0063916 | -5.7584e-05 | 0.022631 | 0.0029887 | 0.00092935 | -0.16937 | 0.12817 | -0.11902 | -0.018311 | 0.059509 | -0.045776 | -0.027466 | -0.11902 | 0.16937 | -0.10529 | 0.022888 | 0.10986 | 0.027466 | 0.082397 | 61.2488 | -61.3358 | -61.4822 | 61.4273 | 61.3403 | 61.322 | 0.091553 | 0.073243 | 61.2625 | -61.2946 | -61.441 | 61.4777 | 61.4502 | 61.3953 | 0.18768 | 0.13275 | 0.17853 | 0.10071 | 0.21515 | 0.12817 | 0.24719 | 0.27466 | 61.496 | 61.5372 | -61.5829 | -61.5692 | 61.3495 | 61.3907 | 61.1984 | 61.2488
667.3281 | 123.1796 | -61.3632 | 61.4777 | -0.091019 | 0.00092492 | 0.013153 | 0.040633 | -0.00049353 | 0.00052988 | -0.0014207 | -0.085205 | -0.0026852 | 0.0046826 | 0.0057102 | 0.02199 | 0.0053385 | 0.00050195 | -0.14191 | 0.10986 | -0.15106 | -0.009155 | 0.086975 | -0.032043 | -0.082397 | -0.059509 | 0.13275 | -0.12817 | 0.068665 | 0.13733 | 0.045776 | 0.12817 | 61.2122 | -61.3678 | -61.4868 | 61.4502 | 61.2808 | 61.3312 | 0.068665 | 0.11902 | 61.235 | -61.3449 | -61.409 | 61.5005 | 61.4914 | 61.409 | 0.25635 | 0.17395 | 0.23804 | 0.14191 | 0.2655 | 0.19684 | 0.26093 | 0.26093 | 61.4731 | 61.496 | -61.6287 | -61.6058 | 61.3541 | 61.4319 | 61.2213 | 61.3037
668.3281 | 123.1201 | -61.3632 | 61.4502 | -0.091019 | -0.00099768 | 0.01123 | 0.04042 | -0.0011343 | 0.00095708 | 0.0017837 | -0.039429 | -0.0014036 | 0.0066052 | 0.00058322 | 0.021777 | 0.0032023 | 7.4746e-05 | -0.14191 | 0.11902 | -0.10529 | 0.009155 | 0.11902 | -0.022888 | 0 | -0.050354 | 0.12817 | -0.11902 | 0.050354 | 0.12817 | 0.059509 | 0.11444 | 61.2579 | -61.3312 | -61.441 | 61.4822 | 61.3632 | 61.3403 | 0.10529 | 0.082398 | 61.2442 | -61.322 | -61.3998 | 61.4914 | 61.4777 | 61.4227 | 0.23346 | 0.17853 | 0.22431 | 0.11444 | 0.24719 | 0.16937 | 0.22431 | 0.24719 | 61.4822 | 61.4914 | -61.5555 | -61.5692 | 61.3724 | 61.4136 | 61.2213 | 61.3129
669.3281 | 123.0377 | -61.3861 | 61.3586 | -0.15968 | 0.00049772 | 0.013366 | 0.027389 | 0.00036107 | -0.0013929 | 0.00071573 | -0.097412 | 0.0018008 | 0.006819 | 0.0052828 | 0.021563 | 0.0053385 | 0.00028835 | -0.20599 | 0.13275 | -0.17395 | -0.10071 | -0.009155 | -0.1236 | -0.10986 | -0.15564 | 0.16479 | -0.14648 | 0.004578 | 0.036621 | -0.022888 | 0.082397 | 61.2122 | -61.2259 | -61.4594 | 61.377 | 61.2762 | 61.2625 | 0.064087 | 0.050354 | 61.2396 | -61.1938 | -61.3541 | 61.4227 | 61.4685 | 61.3632 | 0.22888 | 0.1236 | 0.16479 | 0.073242 | 0.18311 | 0.15106 | 0.3067 | 0.31128 | 61.5189 | 61.5509 | -61.5326 | -61.5051 | 61.2854 | 61.3907 | 61.1801 | 61.2305
670.3281 | 123.1659 | -61.3632 | 61.4639 | -0.1368 | 0.00049772 | 0.015289 | 0.037215 | -0.0017751 | 0.0020251 | -0.0031297 | 0.0032959 | 9.1834e-05 | 0.0040418 | 0.0031466 | 0.021777 | 0.0029887 | -0.00035245 | -0.1236 | 0.10529 | -0.11902 | 0.018311 | -0.11902 | -0.22888 | 0.050354 | -0.068665 | 0.073242 | -0.11902 | 0.068665 | 0.15106 | 0.041199 | 0.11902 | 61.2442 | -61.3586 | -61.4456 | 61.2442 | 61.4136 | 61.1343 | 0.16937 | -0.10986 | 61.2442 | -61.3907 | -61.3953 | 61.5143 | 61.4822 | 61.4044 | 0.23804 | 0.16022 | 0 | 0.13733 | 0.27008 | 0.18768 | 0.22431 | 0.19226 | 61.4685 | 61.4365 | -61.5829 | -61.5829 | 61.3815 | 61.4319 | 61.2396 | 61.2946
671.3281 | 122.8226 | -61.3815 | 61.3724 | -0.30464 | 0.0022067 | 0.013366 | 0.013076 | -0.0041251 | 0.00074348 | -0.0046249 | -0.085205 | -0.0024716 | 0.0048962 | 0.0031466 | 0.022631 | 0.0042703 | 0.0015701 | -0.15564 | 0.15564 | -0.13733 | -0.14648 | -0.022888 | -0.15564 | -0.16022 | -0.21515 | 0.17853 | -0.14648 | -0.041199 | -0.004578 | -0.07782 | 0.032043 | 61.2442 | -61.2167 | -61.5189 | 61.3586 | 61.2213 | 61.2259 | -0.022888 | -0.018311 | 61.235 | -61.1938 | -61.4136 | 61.377 | 61.4136 | 61.3037 | 0.17853 | 0.068664 | 0.11444 | -0.009155 | 0.14191 | 0.10529 | 0.29297 | 0.32501 | 61.5372 | 61.5601 | -61.5097 | -61.5189 | 61.235 | 61.3403 | 61.2259 | 61.1664
672.3281 | 123.1567 | -61.3541 | 61.3998 | -0.091019 | 0.00028412 | 0.013366 | 0.038711 | -0.0034841 | 0.0028797 | -0.0012071 | -0.042481 | -0.0020444 | 0.0066052 | 0.0033602 | 0.023486 | 0.0040567 | 0.0019973 | -0.18768 | 0.14191 | -0.16022 | -0.041199 | 0.050354 | -0.073242 | -0.068665 | -0.091553 | 0.12817 | -0.12817 | 0.054932 | 0.1236 | 0.041199 | 0.12817 | 61.1938 | -61.2579 | -61.441 | 61.4044 | 61.2854 | 61.2808 | 0.091552 | 0.086975 | 61.2259 | -61.2717 | -61.3449 | 61.4777 | 61.4822 | 61.3953 | 0.25635 | 0.16937 | 0.21057 | 0.11902 | 0.25177 | 0.18311 | 0.30212 | 0.25635 | 61.496 | 61.4822 | -61.5601 | -61.528 | 61.3129 | 61.409 | 61.1664 | 61.2625
673.3281 | 122.85 | -61.3907 | 61.2488 | -0.098648 | 0.0013523 | 0.01593 | 0.020125 | 0.00078827 | 0.00052988 | -0.0063339 | -0.054688 | 9.1834e-05 | 0.007887 | 0.001224 | 0.022204 | 0.0021341 | 0.00071555 | -0.19684 | 0.13275 | -0.15106 | -0.14648 | -0.009155 | -0.14191 | -0.13733 | -0.21515 | 0.16937 | -0.13275 | -0.064087 | 0.004578 | -0.068665 | 0.018311 | 61.2396 | -61.116 | -61.3953 | 61.3815 | 61.2534 | 61.2488 | 0.013733 | 0.009155 | 61.2579 | -61.0794 | -61.3129 | 61.3953 | 61.409 | 61.322 | 0.15106 | 0.064086 | 0.14191 | 0.004578 | 0.13733 | 0.068664 | 0.28381 | 0.30212 | 61.5234 | 61.5601 | -61.3998 | -61.3815 | 61.2442 | 61.3266 | 61.1938 | 61.1755
674.3281 | 123.1659 | -61.377 | 61.4273 | 0.00053424 | 0.0013523 | 0.012726 | 0.037856 | 0.0033517 | 0.00095708 | -0.00035247 | -0.02417 | -0.0020444 | 0.0066052 | -0.0013394 | 0.021136 | 0.0046977 | 0.0017837 | -0.17395 | 0.13733 | -0.13733 | -0.045776 | 0.064087 | -0.054932 | -0.027466 | -0.10529 | 0.14191 | -0.11902 | 0.073242 | 0.1236 | 0.027466 | 0.11444 | 61.2396 | -61.29 | -61.4731 | 61.441 | 61.3495 | 61.322 | 0.10986 | 0.082397 | 61.2579 | -61.2854 | -61.3541 | 61.5005 | 61.4914 | 61.4044 | 0.23346 | 0.14649 | 0.20142 | 0.091553 | 0.24261 | 0.19226 | 0.27466 | 0.26093 | 61.5143 | 61.5189 | -61.5646 | -61.5463 | 61.3312 | 61.4502 | 61.203 | 61.2717
675.3281 | 122.7356 | -61.4136 | 61.2671 | -0.12917 | -0.00035668 | 0.0088803 | 0.0036765 | -0.0064749 | -0.0026745 | -0.01082 | -0.079102 | -0.0033262 | 0.00276 | -0.0090298 | 0.017291 | -0.0044881 | -0.0037705 | -0.23346 | 0.10986 | -0.15106 | -0.13733 | -0.082397 | -0.17853 | -0.11444 | -0.25635 | 0.16022 | -0.14648 | -0.059509 | -0.009155 | -0.10071 | 0.022888 | 61.2625 | -61.1572 | -61.4044 | 61.3312 | 61.2991 | 61.235 | 0.036621 | -0.027466 | 61.2671 | -61.1069 | -61.3266 | 61.4044 | 61.4365 | 61.3129 | 0.16937 | 0.045776 | 0.068665 | 0.013733 | 0.13733 | 0.086975 | 0.26093 | 0.3067 | 61.5234 | 61.5738 | -61.4182 | -61.4136 | 61.2762 | 61.3541 | 61.1801 | 61.1572
676.3281 | 123.1201 | -61.3815 | 61.4914 | -0.060501 | 0.00049772 | 0.013153 | 0.033157 | -6.6126e-05 | 0.0015979 | 0.00028833 | -0.060791 | -0.00076257 | 0.00511 | 0.00015602 | 0.021563 | 0.0044839 | 0.0017837 | -0.20599 | 0.15106 | -0.16022 | -0.11902 | -0.004578 | -0.13275 | -0.082397 | -0.18768 | 0.16937 | -0.14191 | -0.013733 | 0.050354 | -0.022888 | 0.045776 | 61.2213 | -61.3403 | -61.6104 | 61.377 | 61.2991 | 61.2488 | 0.07782 | 0.027466 | 61.2396 | -61.322 | -61.5051 | 61.4319 | 61.4273 | 61.3586 | 0.18768 | 0.11902 | 0.15564 | 0.041198 | 0.19226 | 0.12817 | 0.31128 | 0.31128 | 61.5326 | 61.5509 | -61.6516 | -61.6333 | 61.2625 | 61.3678 | 61.1755 | 61.1938
677.3281 | 122.612 | -61.2991 | 61.1801 | -0.07576 | -0.0018521 | 0.0073849 | 0.0094443 | -0.0054067 | -0.0060925 | -0.013597 | -0.048584 | -0.0048216 | -0.0019396 | -0.0077482 | 0.0012688 | 0.0083293 | -0.01552 | -0.20599 | 0.16937 | -0.054932 | -0.064087 | 0.041199 | -0.073242 | -0.032043 | -0.14191 | 0.16022 | -0.1236 | -0.018311 | 0.064087 | -0.027466 | 0.045776 | 61.2442 | -61.0107 | -61.2442 | 61.3403 | 61.2671 | 61.2259 | 0.022889 | -0.01831 | 61.1755 | -61.0199 | -61.1984 | 61.3632 | 61.3449 | 61.2717 | 0.16937 | 0.09613 | 0.096131 | -0.009155 | 0.18768 | 0.10528 | 0.22431 | 0.28381 | 61.4685 | 61.4594 | -61.235 | -61.3037 | 61.235 | 61.2808 | 61.0931 | 61.1572
678.3281 | 122.9782 | -61.3998 | 61.5234 | -0.36568 | 0.00071132 | 0.0097347 | 0.027389 | 0.0020701 | -0.00096552 | -0.0020615 | -0.060791 | -0.00097617 | 0.0081006 | 0.00015602 | 0.023058 | 0.0038431 | 0.0022109 | -0.027466 | 0.16479 | -0.11444 | -0.14191 | -0.032043 | -0.16937 | -0.086975 | -0.23346 | 0.17853 | -0.15106 | -0.059509 | 0.004578 | -0.07782 | 0.022888 | 61.2854 | -61.3586 | -61.6653 | 61.3678 | 61.3129 | 61.2305 | 0.027466 | -0.054932 | 61.2488 | -61.3449 | -61.5829 | 61.4044 | 61.4227 | 61.322 | 0.17395 | 0.073242 | 0.082398 | -0.027466 | 0.15564 | 0.091553 | 0.27924 | 0.32959 | 61.5646 | 61.5784 | -61.6379 | -61.6745 | 61.2579 | 61.3403 | 61.3724 | 61.1664
679.3281 | 122.7356 | -61.4227 | 61.4639 | -0.06813 | -0.0020657 | 0.0086667 | 0.0036765 | -0.0058341 | -0.0045971 | -0.012743 | -0.054688 | -0.00033537 | 0.0055372 | 0.00036962 | 0.015368 | -0.0091879 | -0.0084701 | -0.2243 | 0.10071 | -0.16022 | -0.13275 | -0.036621 | -0.13733 | -0.09613 | -0.23804 | 0.18768 | -0.11444 | -0.064087 | -0.009155 | -0.10071 | 0.004578 | 61.2625 | -61.3632 | -61.5967 | 61.3861 | 61.3266 | 61.2854 | 0.064087 | 0.022888 | 61.3083 | -61.2762 | -61.528 | 61.4136 | 61.4273 | 61.322 | 0.11902 | 0.013733 | 0.1236 | 0.027466 | 0.10529 | 0.050354 | 0.26093 | 0.30212 | 61.5234 | 61.6104 | -61.6241 | -61.5784 | 61.29 | 61.3586 | 61.1984 | 61.1847
680.3281 | 123.1796 | -61.3724 | 61.4731 | -0.022354 | 0.00071132 | 0.011657 | 0.040633 | -0.0017751 | -0.0024609 | 0.0011429 | -0.011963 | -0.0031126 | 0.007887 | 0.0057102 | 0.02199 | 0.0025613 | 0.0022109 | -0.1831 | 0.11444 | -0.16479 | -0.073242 | 0.022888 | -0.086975 | -0.050354 | -0.13275 | 0.13275 | -0.11444 | 0.027466 | 0.10071 | -0.004578 | 0.1236 | 61.2076 | -61.3586 | -61.5463 | 61.3953 | 61.322 | 61.2854 | 0.11444 | 0.07782 | 61.2579 | -61.3403 | -61.4456 | 61.4731 | 61.496 | 61.3678 | 0.23804 | 0.10986 | 0.18768 | 0.091553 | 0.21515 | 0.14191 | 0.27924 | 0.24719 | 61.4868 | 61.5051 | -61.6379 | -61.5875 | 61.2991 | 61.3998 | 61.1893 | 61.2396
681.3281 | 122.7264 | -61.3998 | 61.3541 | -0.091019 | 0.00028412 | 0.0050351 | 0.00068573 | -0.0047659 | -0.0039563 | -0.010393 | -0.048584 | 9.1834e-05 | 0.0014784 | -0.011166 | 0.013445 | -0.012606 | -0.014238 | -0.21515 | 0.13733 | -0.15106 | -0.091553 | 0.004578 | -0.10529 | -0.073242 | -0.17395 | 0.15564 | -0.11444 | -0.045776 | 0.013733 | -0.086975 | 0.018311 | 61.2488 | -61.2167 | -61.4456 | 61.4044 | 61.3266 | 61.2946 | 0.07782 | 0.045776 | 61.2854 | -61.1984 | -61.3998 | 61.4136 | 61.4182 | 61.3129 | 0.13275 | 0.027466 | 0.15564 | 0.059509 | 0.12817 | 0.068665 | 0.28839 | 0.27008 | 61.5372 | 61.5555 | -61.5051 | -61.4685 | 61.3083 | 61.3541 | 61.1847 | 61.2259
682.3281 | 122.9736 | -61.4044 | 61.5372 | -0.060501 | 0.00092492 | 0.013366 | 0.023971 | 0.0014291 | 0.0028797 | -0.00099327 | 0.15283 | -0.0037534 | 0.007887 | 0.0031466 | 0.021563 | 0.0025613 | 0.0032791 | -0.21973 | 0.15106 | -0.1831 | -0.13733 | 0.10529 | -0.44861 | -0.050354 | -0.31586 | 0.17853 | -0.10071 | -0.059509 | -0.018311 | -0.10071 | 0.027466 | 61.2213 | -61.3861 | -61.6745 | 61.5097 | 61.3541 | 60.9558 | 0.13275 | -0.2655 | 61.3037 | -61.3586 | -61.5967 | 61.3861 | 61.4319 | 61.3037 | 0.12817 | 0 | 0.28839 | 0.045776 | 0.082397 | 0.041199 | 0.33417 | 0.27924 | 61.5555 | 61.5829 | -61.7203 | -61.6379 | 61.2671 | 61.3449 | 61.1847 | 61.0886
683.3281 | 122.7631 | -61.4136 | 61.4639 | -0.052872 | -0.0014249 | 0.0067441 | 0.0092307 | -0.00027993 | -0.0022473 | -0.0088975 | -0.018066 | 9.1834e-05 | 0.003401 | -0.0060392 | 0.016436 | -0.013033 | -0.012102 | -0.14191 | 0.20142 | -0.018311 | -0.082397 | 0.041199 | -0.059509 | -0.027466 | -0.13275 | 0.15106 | -0.11902 | -0.013733 | 0.054932 | -0.036621 | 0.050354 | 61.3953 | -61.2625 | -61.5463 | 61.4548 | 61.3861 | 61.3541 | -0.009155 | -0.041198 | 61.2946 | -61.3129 | -61.4777 | 61.4685 | 61.4639 | 61.377 | 0.16937 | 0.082398 | 0.05951 | -0.064086 | 0.17395 | 0.10529 | 0.21973 | 0.27008 | 61.615 | 61.5646 | -61.4822 | -61.5829 | 61.3312 | 61.3998 | 61.2717 | 61.2808
684.3281 | 123.1613 | -61.3861 | 61.5097 | -0.045242 | 0.00028412 | 0.013366 | 0.041701 | -6.6126e-05 | -0.00096552 | -0.0022751 | -0.011963 | -0.0026852 | 0.006178 | 0.0022922 | 0.02199 | 0.0029887 | 0.0034927 | -0.1831 | 0.14648 | -0.16479 | -0.10986 | 0.009155 | -0.10529 | -0.054932 | -0.15106 | 0.15564 | -0.13275 | 0.004578 | 0.07782 | -0.009155 | 0.09613 | 61.2213 | -61.3632 | -61.6196 | 61.3953 | 61.3312 | 61.2808 | 0.10986 | 0.059509 | 61.2534 | -61.3541 | -61.5051 | 61.4639 | 61.4822 | 61.377 | 0.22888 | 0.1236 | 0.17395 | 0.054932 | 0.21057 | 0.13733 | 0.31128 | 0.28839 | 61.5326 | 61.5417 | -61.6745 | -61.6425 | 61.2762 | 61.3907 | 61.203 | 61.235
685.3281 | 122.8088 | -61.3861 | 61.5601 | -0.045242 | 0.0011385 | 0.011657 | 0.014144 | -0.0013479 | -0.00096552 | -0.0052659 | 0.058227 | -0.00119 | 0.0066052 | -0.0013394 | 0.020709 | -0.0087607 | -0.010393 | -0.15564 | 0.14191 | -0.13733 | -0.064087 | 0.027466 | 0.045776 | 0.12817 | -0.14191 | 0.23346 | 0.041199 | 0.013733 | 0.073242 | -0.027466 | 0.064087 | 61.2488 | -61.4182 | -61.6241 | 61.4136 | 61.5143 | 61.4319 | 0.2655 | 0.18311 | 61.4273 | -61.3266 | -61.5463 | 61.4594 | 61.4502 | 61.3586 | 0.022888 | -0.068665 | 0.16479 | 0.073242 | 0.032043 | -0.027466 | 0.27924 | 0.19226 | 61.528 | 61.6196 | -61.6974 | -61.5189 | 61.322 | 61.3998 | 61.2305 | 61.2442
686.3281 | 122.8638 | -61.3998 | 61.5372 | -0.029984 | -0.0016385 | 0.0084531 | 0.017776 | -0.0073293 | -0.00096552 | -0.0069749 | -0.051636 | -0.0020444 | 0.003401 | -0.0024076 | 0.021563 | -0.00042933 | -0.0050523 | -0.19226 | 0.13733 | -0.15106 | -0.13733 | -0.036621 | -0.14648 | -0.09613 | -0.23346 | 0.17395 | -0.11902 | -0.07782 | 0 | -0.10529 | 0.018311 | 61.2488 | -61.3998 | -61.6745 | 61.3632 | 61.3037 | 61.2534 | 0.054932 | 0.004578 | 61.2808 | -61.3632 | -61.615 | 61.3998 | 61.4182 | 61.2946 | 0.13733 | 0.013733 | 0.11444 | 0.013733 | 0.11902 | 0.041199 | 0.28839 | 0.29297 | 61.5372 | 61.5738 | -61.6882 | -61.6562 | 61.2625 | 61.322 | 61.2076 | 61.1664
687.3281 | 122.8271 | -61.3907 | 61.5372 | -0.060501 | 0.0032749 | 0.0084531 | 0.020339 | -0.0056203 | 0.00031608 | -0.0067613 | -0.02417 | -0.00097617 | 0.0059644 | -0.0011258 | 0.018572 | -0.0079061 | -0.0065475 | -0.13275 | 0.19226 | -0.050354 | -0.059509 | 0.036621 | -0.068665 | -0.032043 | -0.11902 | 0.16479 | -0.13275 | -0.004578 | 0.050354 | -0.036621 | 0.050354 | 61.3403 | -61.3449 | -61.5967 | 61.4273 | 61.3586 | 61.322 | 0.018311 | -0.018311 | 61.2579 | -61.3724 | -61.5417 | 61.441 | 61.441 | 61.3541 | 0.18311 | 0.09613 | 0.086975 | -0.009155 | 0.18311 | 0.12817 | 0.24261 | 0.29755 | 61.5829 | 61.5555 | -61.5875 | -61.6699 | 61.3312 | 61.3861 | 61.2579 | 61.2717
688.3281 | 123.1018 | -61.4273 | 61.5555 | -0.11391 | 0.00049772 | 0.012939 | 0.039779 | -0.0017751 | -0.00011112 | -0.00099327 | -0.0089111 | -0.0018308 | 0.004469 | 0.0027194 | 0.022204 | 0.0042703 | 0.00028835 | -0.18768 | 0.14648 | -0.13733 | -0.13733 | -0.041199 | -0.14191 | -0.07782 | -0.20599 | 0.16937 | -0.14191 | -0.059509 | -0.009155 | -0.082397 | 0.027466 | 61.29 | -61.409 | -61.6928 | 61.3861 | 61.3495 | 61.2854 | 0.059509 | -0.004578 | 61.2854 | -61.3861 | -61.615 | 61.4182 | 61.4548 | 61.3449 | 0.16937 | 0.05951 | 0.09613 | 0 | 0.13275 | 0.082398 | 0.28381 | 0.31128 | 61.5738 | 61.5967 | -61.6928 | -61.6974 | 61.29 | 61.3678 | 61.2396 | 61.2213
689.3281 | 122.8363 | -61.3907 | 61.5555 | -0.0070953 | 0.0019931 | 0.0082393 | 0.021621 | 0.0033517 | -0.0031017 | -0.0024887 | 0.015503 | 9.1834e-05 | 0.0066052 | -0.0024076 | 0.020922 | -0.0034201 | -0.0059067 | -0.16022 | 0.11444 | -0.14191 | -0.086975 | 0.12817 | -0.022888 | 0.050354 | -0.07782 | 0.22888 | 0.050354 | 0 | 0.073242 | -0.022888 | 0.073242 | 61.2488 | -61.441 | -61.6425 | 61.5189 | 61.441 | 61.3678 | 0.19226 | 0.11902 | 61.441 | -61.3266 | -61.5555 | 61.4639 | 61.4639 | 61.3678 | 0.022888 | -0.073242 | 0.27008 | 0.054932 | 0.022888 | -0.050354 | 0.25635 | 0.17853 | 61.5051 | 61.6196 | -61.6974 | -61.5051 | 61.3037 | 61.3907 | 61.2305 | 61.3129
690.3281 | 122.8638 | -61.4136 | 61.5555 | -0.083389 | 0.0019931 | 0.0093075 | 0.021407 | -0.00092073 | -0.00075192 | -0.0039841 | -0.018066 | -0.00012177 | 0.0074598 | 0.0050692 | 0.023913 | 0.0044839 | 0.00028835 | -0.19226 | 0.11902 | -0.12817 | -0.14191 | -0.050354 | -0.14191 | -0.10071 | -0.2243 | 0.15564 | -0.14648 | -0.073242 | -0.004578 | -0.11444 | 0.018311 | 61.2854 | -61.4365 | -61.6974 | 61.3632 | 61.3129 | 61.2717 | 0.027466 | -0.013733 | 61.2671 | -61.3998 | -61.6287 | 61.409 | 61.4319 | 61.2991 | 0.16479 | 0.032043 | 0.07782 | -0.013733 | 0.14191 | 0.073242 | 0.24719 | 0.30212 | 61.5326 | 61.5692 | -61.6837 | -61.702 | 61.2717 | 61.3403 | 61.2213 | 61.1893
691.3281 | 122.8912 | -61.409 | 61.5555 | 0.00053424 | 0.0026339 | 0.012939 | 0.039992 | 0.0012155 | -0.0013929 | -0.00077967 | 0.0093995 | -0.0024716 | 0.0057508 | 0.002933 | 0.023058 | 0.0038431 | 0.0026383 | -0.17395 | 0.14191 | -0.17853 | -0.1236 | -0.027466 | -0.091553 | -0.059509 | -0.21515 | 0.16479 | -0.14191 | -0.050354 | 0.050354 | -0.041199 | 0.050354 | 61.2305 | -61.4136 | -61.6791 | 61.3815 | 61.3495 | 61.3174 | 0.11902 | 0.086975 | 61.2671 | -61.3907 | -61.6058 | 61.4594 | 61.4594 | 61.3678 | 0.19226 | 0.10071 | 0.15106 | 0.054932 | 0.19226 | 0.091553 | 0.32044 | 0.3067 | 61.5509 | 61.5738 | -61.734 | -61.6974 | 61.2854 | 61.3586 | 61.235 | 61.1938
692.3281 | 122.8363 | -61.4044 | 61.5692 | -0.06813 | 0.0015659 | 0.0086667 | 0.021621 | -0.0077567 | -0.0041699 | -0.0020615 | -0.0028075 | 0.00051903 | 0.0029736 | 0.0067782 | 0.023058 | 0.00021147 | 0.00028835 | -0.17395 | 0.14648 | -0.15106 | -0.10529 | -0.009155 | -0.11444 | -0.1236 | -0.18768 | 0.17395 | -0.11444 | -0.054932 | 0 | -0.09613 | 0.013733 | 61.2534 | -61.4227 | -61.6745 | 61.3953 | 61.2808 | 61.29 | 0.027466 | 0.036621 | 61.29 | -61.3953 | -61.6241 | 61.4044 | 61.4182 | 61.3083 | 0.12817 | 0.018311 | 0.14191 | 0.045776 | 0.11444 | 0.059509 | 0.29755 | 0.28839 | 61.5509 | 61.5784 | -61.7203 | -61.6837 | 61.2991 | 61.3495 | 61.2305 | 61.2167
693.3281 | 122.8271 | -61.3907 | 61.5189 | -0.014725 | 0.0015659 | 0.0095211 | 0.025252 | 0.0014291 | -0.0016065 | -0.0044113 | -0.027222 | -0.0018308 | 0.0038282 | 0.0027194 | 0.024127 | 0.0012797 | -0.0067613 | -0.14191 | 0.13733 | -0.15564 | -0.032043 | 0.20142 | -0.091553 | -0.082397 | -0.086975 | 0.24261 | 0.004578 | -0.018311 | 0.073242 | -0.022888 | 0.059509 | 61.235 | -61.3815 | -61.5509 | 61.5921 | 61.3083 | 61.2991 | 0.073243 | 0.064087 | 61.3953 | -61.2762 | -61.5372 | 61.4639 | 61.4502 | 61.3678 | 0.054931 | -0.027466 | 0.35706 | 0.1236 | 0.068664 | -0.022889 | 0.29297 | 0.23804 | 61.528 | 61.6333 | -61.6745 | -61.5143 | 61.3586 | 61.3724 | 61.2488 | 61.3037
694.3281 | 123.0927 | -61.4182 | 61.5601 | -0.045242 | 0.0028475 | 0.014007 | 0.040633 | 0.0031381 | 0.00095708 | -0.0048385 | 0.052124 | -0.0037534 | 0.007887 | 0.0059238 | 0.02199 | 0.0027751 | 0.00071555 | -0.19684 | 0.14648 | -0.17395 | -0.059509 | 0.16937 | -0.29297 | -0.10529 | -0.24261 | 0.19226 | -0.12817 | -0.054932 | -0.009155 | -0.10529 | 0.018311 | 61.2442 | -61.4136 | -61.6196 | 61.5875 | 61.3129 | 61.1252 | 0.068664 | -0.11902 | 61.29 | -61.3678 | -61.615 | 61.409 | 61.4365 | 61.3129 | 0.14649 | 0.022888 | 0.34332 | 0.11444 | 0.11902 | 0.073242 | 0.32043 | 0.32044 | 61.5646 | 61.6104 | -61.734 | -61.6882 | 61.3586 | 61.3632 | 61.2213 | 61.1755
695.3281 | 122.8592 | -61.3998 | 61.5555 | -0.07576 | -0.00099768 | 0.011871 | 0.033157 | 0.0044199 | -0.0013929 | -0.0039841 | 0.0032959 | -0.0024716 | 0.0063916 | 0.0067782 | 0.02199 | 0.0038431 | 0.00028835 | -0.13733 | 0.12817 | -0.13275 | -0.068665 | 0.041199 | -0.064087 | -0.11444 | -0.11902 | 0.16479 | -0.10986 | 0.082397 | 0.073242 | 0 | 0.11902 | 61.2671 | -61.4273 | -61.6241 | 61.441 | 61.2854 | 61.3358 | 0.01831 | 0.068664 | 61.29 | -61.3907 | -61.4731 | 61.4731 | 61.5189 | 61.3998 | 0.22888 | 0.10986 | 0.17395 | 0.064086 | 0.18311 | 0.19226 | 0.26093 | 0.27466 | 61.528 | 61.5646 | -61.6882 | -61.6653 | 61.3312 | 61.4822 | 61.2625 | 61.2808
696.3281 | 122.8729 | -61.4273 | 61.5738 | -0.052872 | 7.0518e-05 | 0.0097347 | 0.030379 | -0.0054067 | -0.0022473 | -0.0016343 | -0.027222 | -0.00054897 | 0.0055372 | 0.0069918 | 0.022631 | 0.0036295 | 0.00050195 | -0.18768 | 0.14191 | -0.14648 | -0.13275 | -0.032043 | -0.14191 | -0.17853 | -0.20142 | 0.16479 | -0.13733 | -0.082397 | 0 | -0.10529 | 0.004578 | 61.2808 | -61.4319 | -61.7065 | 61.3953 | 61.2488 | 61.2854 | -0.032044 | 0.004577 | 61.29 | -61.409 | -61.6562 | 61.4273 | 61.4319 | 61.322 | 0.14191 | 0.032043 | 0.11444 | 0.013733 | 0.13733 | 0.054932 | 0.28839 | 0.30212 | 61.5692 | 61.5921 | -61.7203 | -61.7111 | 61.2946 | 61.3449 | 61.2396 | 61.2259
697.3281 | 122.8683 | -61.3861 | 61.5646 | -0.022354 | 0.0015659 | 0.012726 | 0.040633 | 0.00078827 | -0.0016065 | -0.0029159 | 0.0032959 | -0.00012177 | 0.0070326 | 0.0072054 | 0.022845 | 0.0049113 | -0.0016343 | -0.16022 | 0.11902 | -0.17395 | -0.073242 | 0.041199 | -0.073242 | -0.10071 | -0.10071 | 0.16479 | -0.11444 | -0.022888 | 0.064087 | -0.036621 | 0.059509 | 61.2122 | -61.4456 | -61.6379 | 61.4273 | 61.2854 | 61.3129 | 0.073242 | 0.10071 | 61.2717 | -61.3998 | -61.5875 | 61.4502 | 61.4456 | 61.3495 | 0.17395 | 0.07782 | 0.21515 | 0.10071 | 0.17853 | 0.091553 | 0.29297 | 0.27924 | 61.5051 | 61.5509 | -61.7386 | -61.6791 | 61.3129 | 61.3632 | 61.2259 | 61.2854
698.3281 | 122.8455 | -61.3907 | 61.5509 | -0.029984 | 0.00071132 | 0.01123 | 0.033157 | -0.0036977 | -0.00075192 | -0.00099327 | -0.015015 | -0.0020444 | 0.0070326 | 0.0037876 | 0.023272 | 0.0038431 | 0.0028519 | 0.054932 | 0.16479 | -0.11444 | -0.036621 | 0.045776 | -0.032043 | -0.036621 | -0.11902 | 0.1831 | -0.045776 | -0.018311 | 0.064087 | -0.041199 | 0.064087 | 61.2762 | -61.3861 | -61.5875 | 61.4365 | 61.3541 | 61.3586 | 0.07782 | 0.082398 | 61.3449 | -61.3678 | -61.5692 | 61.4548 | 61.4548 | 61.3495 | 0.10986 | 0.004577 | 0.16022 | 0.07782 | 0.10986 | 0.027465 | 0.27924 | 0.22888 | 61.5555 | 61.5738 | -61.6653 | -61.5967 | 61.3541 | 61.3724 | 61.4456 | 61.2717
699.3438 | 123.2391 | -61.3541 | 61.528 | -0.06813 | 0.0028475 | 0.015289 | 0.041061 | 0.0010019 | 0.00074348 | -0.0016343 | 0.042969 | -0.00097617 | 0.0057508 | -0.004971 | 0.020495 | 0.0034159 | 0.00050195 | -0.13275 | 0.082397 | -0.1236 | -0.032043 | 0.10529 | -0.018311 | -0.013733 | -0.004578 | 0.1236 | -0.10529 | 0.059509 | 0.13733 | 0.045776 | 0.1236 | 61.2305 | -61.4456 | -61.5601 | 61.4594 | 61.3403 | 61.3358 | 0.10986 | 0.10528 | 61.2488 | -61.4044 | -61.4685 | 61.4914 | 61.4777 | 61.3998 | 0.22888 | 0.15106 | 0.22888 | 0.091553 | 0.24262 | 0.16479 | 0.20599 | 0.22888 | 61.4365 | 61.4777 | -61.6516 | -61.6333 | 61.322 | 61.4136 | 61.2213 | 61.3495
700.3281 | 122.9965 | -61.4227 | 61.5784 | -0.083389 | -0.0014249 | 0.012726 | 0.026748 | -0.0022025 | 0.00010248 | -0.0024887 | -0.045532 | -0.002258 | 0.0057508 | 0.0025058 | 0.020068 | 0.0032023 | -0.00056605 | -0.18768 | 0.13275 | -0.15564 | -0.14191 | -0.068665 | -0.15106 | -0.14191 | -0.23346 | 0.16479 | -0.13275 | -0.086975 | -0.027466 | -0.12817 | 0.004578 | 61.2671 | -61.4456 | -61.7203 | 61.3541 | 61.2808 | 61.2717 | 0.013733 | 0.004578 | 61.29 | -61.4136 | -61.6653 | 61.3953 | 61.4273 | 61.2946 | 0.13733 | 0.004577 | 0.086975 | 0.013733 | 0.10529 | 0.045776 | 0.28839 | 0.29755 | 61.5555 | 61.5875 | -61.734 | -61.7111 | 61.2808 | 61.3358 | 61.235 | 61.1893
701.3281 | 122.9279 | -61.4044 | 61.5646 | -0.037613 | 0.0026339 | 0.012939 | 0.035506 | 0.0012155 | -0.00053832 | -0.0018479 | -0.015015 | -0.0033262 | 0.0063916 | 0.002933 | 0.022631 | 0.0046977 | 0.0034927 | -0.13733 | 0.14648 | -0.13733 | -0.068665 | 0.036621 | -0.064087 | -0.073242 | 0.15564 | 0.1831 | -0.036621 | 0.022888 | 0.091553 | -0.027466 | 0.07782 | 61.2671 | -61.4182 | -61.6333 | 61.441 | 61.3312 | 61.3403 | 0.064087 | 0.073242 | 61.3678 | -61.3815 | -61.5417 | 61.496 | 61.4822 | 61.377 | 0.11444 | 0.009155 | 0.17395 | 0.068664 | 0.12817 | 0.059509 | 0.28381 | 0.21973 | 61.5509 | 61.5875 | -61.702 | -61.6013 | 61.3358 | 61.4273 | 61.2671 | 61.5601
702.3281 | 122.9462 | -61.4182 | 61.5555 | -0.091019 | 0.0022067 | 0.013153 | 0.033157 | -0.0024161 | 0.0011707 | -0.0016343 | -0.018066 | -0.0020444 | 0.0057508 | 0.0022922 | 0.02199 | 0.0034159 | 0.0030655 | -0.18768 | 0.11444 | -0.15564 | -0.12817 | -0.036621 | -0.14191 | -0.15106 | -0.21515 | 0.14191 | -0.11902 | -0.064087 | -0.022888 | -0.10529 | 0.036621 | 61.2625 | -61.441 | -61.6837 | 61.3815 | 61.2671 | 61.2762 | 0.004578 | 0.013733 | 61.2991 | -61.4136 | -61.6196 | 61.3953 | 61.4548 | 61.3129 | 0.15564 | 0.013733 | 0.11902 | 0.027466 | 0.096131 | 0.054932 | 0.27008 | 0.26093 | 61.5326 | 61.5601 | -61.7111 | -61.6745 | 61.29 | 61.3541 | 61.2305 | 61.203
703.3281 | 122.905 | -61.4044 | 61.5601 | -0.06813 | 0.00049772 | 0.012512 | 0.039138 | 0.00036107 | -0.0033155 | -0.0016343 | -0.0028075 | -0.002258 | 0.0055372 | 0.00015602 | 0.022204 | 0.0076883 | 0.0028519 | -0.16022 | 0.1236 | -0.14191 | -0.064087 | 0.027466 | -0.059509 | -0.07782 | -0.10986 | 0.14648 | -0.1236 | 0.1236 | 0.15106 | 0.032043 | 0.064087 | 61.2625 | -61.4365 | -61.6241 | 61.4319 | 61.3266 | 61.3449 | 0.064087 | 0.082398 | 61.2808 | -61.4136 | -61.4365 | 61.5555 | 61.4685 | 61.4365 | 0.18768 | 0.15564 | 0.16937 | 0.07782 | 0.27466 | 0.24719 | 0.2655 | 0.27008 | 61.528 | 61.5509 | -61.702 | -61.6837 | 61.3403 | 61.528 | 61.2442 | 61.2946
704.3438 | 123.2666 | -61.3632 | 61.5646 | -0.06813 | -0.00035668 | 0.01123 | 0.040206 | -0.0017751 | -0.00053832 | 0.00050193 | 0.07959 | -0.0026852 | 0.00511 | -0.0071072 | 0.02199 | 0.0021341 | 0.0015701 | -0.10986 | 0.14191 | -0.10529 | -0.009155 | 0.16022 | 0.027466 | 0.041199 | -0.013733 | 0.14191 | -0.07782 | 0.050354 | 0.16022 | 0.068665 | 0.12817 | 61.2579 | -61.4227 | -61.5738 | 61.5234 | 61.4044 | 61.3907 | 0.14649 | 0.13275 | 61.2854 | -61.4227 | -61.5143 | 61.5234 | 61.4914 | 61.4319 | 0.20599 | 0.14649 | 0.2655 | 0.096131 | 0.23804 | 0.12817 | 0.24719 | 0.21973 | 61.5051 | 61.5051 | -61.6699 | -61.6425 | 61.3541 | 61.4136 | 61.2534 | 61.3495
705.3281 | 123.0011 | -61.4273 | 61.5463 | 0.0081632 | 0.00028412 | 0.014221 | 0.031875 | -0.010107 | 0.0011707 | -0.0035569 | -0.018066 | -0.00119 | 0.0059644 | 0.00079682 | 0.022418 | 0.0038431 | 0.0015701 | -0.14191 | 0.13275 | -0.16479 | -0.082397 | 0.050354 | -0.068665 | -0.073242 | -0.11444 | 0.16479 | -0.10071 | -0.009155 | 0.068665 | -0.045776 | 0.07782 | 61.2625 | -61.4136 | -61.6287 | 61.4777 | 61.3541 | 61.3586 | 0.091553 | 0.09613 | 61.3266 | -61.3815 | -61.5555 | 61.496 | 61.5051 | 61.3815 | 0.17853 | 0.054932 | 0.21515 | 0.082398 | 0.16937 | 0.091553 | 0.29755 | 0.2655 | 61.5601 | 61.5921 | -61.7111 | -61.647 | 61.3449 | 61.4182 | 61.2854 | 61.3129
706.3281 | 123.0377 | -61.4182 | 61.5738 | -0.060501 | 0.0015659 | 0.012939 | 0.030166 | -0.0098929 | -0.0024609 | -0.0069749 | -0.045532 | -0.00076257 | 0.00511 | -0.0017666 | 0.022418 | 0.0044839 | -0.0020615 | -0.17853 | 0.14191 | -0.14648 | -0.10529 | -0.009155 | -0.13733 | -0.13733 | -0.18768 | 0.16937 | -0.13733 | -0.073242 | 0 | -0.11444 | 0.018311 | 61.2717 | -61.4319 | -61.6791 | 61.409 | 61.2808 | 61.2808 | 0.009155 | 0.009155 | 61.2808 | -61.4044 | -61.647 | 61.4182 | 61.4365 | 61.3037 | 0.15564 | 0.022888 | 0.13733 | 0.041198 | 0.13733 | 0.064087 | 0.28839 | 0.3067 | 61.5601 | 61.5875 | -61.7203 | -61.7111 | 61.3129 | 61.3449 | 61.2396 | 61.2305
707.3281 | 122.9691 | -61.4182 | 61.5555 | -0.06813 | 0.0013523 | 0.01123 | 0.034438 | 0.00014747 | 0.0011707 | -0.0044113 | 0.00024405 | -0.0026852 | 0.0042554 | 0.0031466 | 0.020709 | 0.0023477 | -0.0022751 | -0.12817 | 0.19684 | -0.009155 | -0.068665 | 0.041199 | -0.064087 | -0.064087 | -0.11902 | 0.16022 | -0.11902 | -0.032043 | 0.064087 | -0.064087 | 0.041199 | 61.409 | -61.3586 | -61.6241 | 61.4594 | 61.3541 | 61.3541 | -0.054932 | -0.054932 | 61.2991 | -61.3953 | -61.5875 | 61.4822 | 61.4594 | 61.3541 | 0.16022 | 0.054932 | 0.050354 | -0.05951 | 0.18311 | 0.086976 | 0.20599 | 0.27924 | 61.615 | 61.5784 | -61.5646 | -61.6745 | 61.3495 | 61.3861 | 61.29 | 61.2991
708.3281 | 123.0743 | -61.4273 | 61.5829 | -0.07576 | 0.0032749 | 0.013153 | 0.041274 | -0.00049353 | 0.00031608 | 0.00050193 | -0.045532 | -0.0037534 | 0.006178 | -0.00048498 | 0.023486 | 0.0021341 | 0.0049881 | -0.19684 | 0.12817 | -0.16937 | -0.15564 | -0.086975 | -0.16022 | -0.15106 | -0.22888 | 0.17853 | -0.14648 | -0.091553 | 0.09613 | 0.054932 | 0.07782 | 61.2579 | -61.4548 | -61.7386 | 61.3403 | 61.2762 | 61.2671 | 0.018311 | 0.009156 | 61.2808 | -61.4044 | -61.6745 | 61.5234 | 61.5051 | 61.4822 | 0.2243 | 0.20142 | 0.082398 | 0.013733 | 0.24261 | 0.054931 | 0.29755 | 0.32501 | 61.5555 | 61.6058 | -61.7523 | -61.7294 | 61.2717 | 61.3358 | 61.2305 | 61.1984
709.3281 | 123.2712 | -61.3861 | 61.528 | -0.0070953 | 0.0017795 | 0.014007 | 0.041701 | 0.0020701 | -0.00096552 | -0.0014207 | 0.02771 | -0.003967 | 0.0066052 | -0.0026212 | 0.023058 | 0.0042703 | 0.0037063 | -0.16479 | 0.1236 | -0.15564 | -0.086975 | 0.022888 | -0.091553 | -0.022888 | -0.10986 | 0.13733 | -0.11902 | 0.027466 | 0.10986 | -0.018311 | 0.12817 | 61.2305 | -61.4044 | -61.615 | 61.409 | 61.3632 | 61.2946 | 0.13275 | 0.064087 | 61.2671 | -61.3907 | -61.5005 | 61.496 | 61.5143 | 61.3678 | 0.24719 | 0.10071 | 0.17853 | 0.068665 | 0.22888 | 0.14649 | 0.27924 | 0.25635 | 61.5097 | 61.5234 | -61.6837 | -61.647 | 61.2991 | 61.4136 | 61.2213 | 61.2762
710.3281 | 123.0835 | -61.4273 | 61.5921 | -0.06813 | -0.00035668 | 0.015075 | 0.040206 | -0.0017751 | 0.0028797 | -0.0020615 | -0.045532 | -0.0035398 | 0.0070326 | 0.0010104 | 0.020922 | 0.0089701 | 0.0028519 | -0.20599 | 0.13275 | -0.16022 | -0.15106 | -0.073242 | -0.17853 | -0.13733 | -0.21057 | 0.16479 | -0.14648 | -0.1236 | 0.14191 | 0.013733 | 0.054932 | 61.2671 | -61.4594 | -61.7432 | 61.3541 | 61.29 | 61.2488 | 0.022888 | -0.018311 | 61.2808 | -61.4273 | -61.7157 | 61.5692 | 61.4822 | 61.441 | 0.20142 | 0.16022 | 0.086975 | 0.009155 | 0.28839 | 0.022888 | 0.29297 | 0.31128 | 61.5601 | 61.5921 | -61.7523 | -61.7386 | 61.2762 | 61.3037 | 61.2213 | 61.2167
711.3281 | 122.8958 | -61.4044 | 61.5692 | 0.00053424 | -0.00014308 | 0.014435 | 0.034652 | 0.0014291 | 0.00031608 | -0.00077967 | -0.011963 | -0.0035398 | 0.0063916 | 0.0016512 | 0.022204 | 0.0040567 | 0.00050195 | -0.054932 | 0.18768 | 0.004578 | -0.091553 | 0.027466 | -0.073242 | -0.050354 | -0.1236 | 0.16479 | -0.11902 | -0.027466 | 0.059509 | -0.054932 | 0.054932 | 61.409 | -61.3815 | -61.6608 | 61.4319 | 61.3541 | 61.3312 | -0.054932 | -0.07782 | 61.2854 | -61.4044 | -61.5967 | 61.4639 | 61.4594 | 61.3495 | 0.17395 | 0.064087 | 0.022888 | -0.096131 | 0.17853 | 0.091553 | 0.1831 | 0.28381 | 61.5921 | 61.5692 | -61.5646 | -61.6882 | 61.3129 | 61.377 | 61.3495 | 61.2808
712.3281 | 123.0652 | -61.4182 | 61.5692 | -0.098648 | 0.00049772 | 0.013153 | 0.039992 | 0.0018565 | -0.00053832 | -0.00013887 | -0.018066 | -0.00119 | 0.0046826 | 0.0010104 | 0.02199 | 0.00042507 | 0.0056289 | -0.16479 | 0.14648 | -0.16022 | -0.15106 | -0.086975 | -0.18768 | -0.13275 | -0.21515 | 0.14648 | -0.14648 | -0.073242 | -0.059509 | 0.11902 | 0.1236 | 61.2579 | -61.4227 | -61.7203 | 61.3312 | 61.2854 | 61.2305 | 0.027466 | -0.027466 | 61.2717 | -61.4227 | -61.6425 | 61.3586 | 61.5417 | 61.5372 | 0.27008 | 0.2655 | 0.073242 | 0.009155 | 0.086975 | 0.073242 | 0.3067 | 0.29297 | 61.5646 | 61.5646 | -61.7294 | -61.7157 | 61.2671 | 61.3449 | 61.2534 | 61.203
713.3281 | 122.9187 | -61.3998 | 61.5784 | -0.091019 | 0.00049772 | 0.01358 | 0.039138 | -0.00049353 | -0.00011112 | -0.0012071 | -0.015015 | -0.0026852 | 0.0057508 | 0.0025058 | 0.022418 | 0.0032023 | -0.00013885 | -0.068665 | 0.20599 | -0.009155 | -0.07782 | 0.036621 | -0.068665 | -0.054932 | -0.12817 | 0.16479 | -0.12817 | -0.032043 | 0.050354 | -0.068665 | 0.045776 | 61.3907 | -61.3724 | -61.6562 | 61.4365 | 61.3449 | 61.3312 | -0.045777 | -0.05951 | 61.2717 | -61.4136 | -61.6104 | 61.4502 | 61.4456 | 61.3312 | 0.17395 | 0.059509 | 0.045776 | -0.068665 | 0.17853 | 0.096131 | 0.21515 | 0.29297 | 61.6058 | 61.5646 | -61.5875 | -61.7065 | 61.322 | 61.3678 | 61.3312 | 61.2717
714.3281 | 123.262 | -61.3861 | 61.5234 | -0.10628 | -0.00078408 | 0.015503 | 0.038711 | 0.0020701 | -0.00032472 | -0.00077967 | -0.036377 | -0.002899 | 0.0036146 | -0.00027138 | 0.023058 | 0.0032023 | 0.0034927 | -0.07782 | 0.091553 | -0.10986 | -0.018311 | 0.10071 | -0.032043 | 0.009155 | -0.013733 | 0.082397 | -0.1236 | 0.036621 | 0.14648 | 0.032043 | 0.12817 | 61.2762 | -61.4319 | -61.5417 | 61.4868 | 61.3953 | 61.3541 | 0.11902 | 0.07782 | 61.2625 | -61.441 | -61.4868 | 61.5326 | 61.5143 | 61.4182 | 0.25177 | 0.15564 | 0.21057 | 0.091552 | 0.27008 | 0.16022 | 0.20142 | 0.20599 | 61.4777 | 61.4685 | -61.6333 | -61.647 | 61.3678 | 61.4227 | 61.3083 | 61.3724
715.3281 | 122.9874 | -61.4182 | 61.5967 | -0.0070953 | 0.0011385 | 0.014862 | 0.030807 | -0.0015615 | 0.00031608 | -0.00056607 | -0.066895 | -0.00097617 | 0.0085278 | 0.0035738 | 0.020281 | 0.00042507 | 0.0013565 | -0.12817 | 0.13733 | -0.14191 | -0.1236 | -0.018311 | -0.15106 | -0.091553 | -0.17395 | 0.14191 | -0.13733 | -0.07782 | 0.004578 | -0.10071 | 0.004578 | 61.2762 | -61.4594 | -61.7203 | 61.3998 | 61.3266 | 61.2671 | 0.050354 | -0.009155 | 61.2808 | -61.4548 | -61.6745 | 61.4227 | 61.4227 | 61.3174 | 0.14191 | 0.036621 | 0.1236 | 0.018311 | 0.14191 | 0.059509 | 0.27924 | 0.27924 | 61.5555 | 61.5601 | -61.7386 | -61.734 | 61.2946 | 61.3403 | 61.29 | 61.2442
716.3281 | 123.1796 | -61.4136 | 61.5417 | -0.098648 | 0.0032749 | 0.013366 | 0.040206 | -6.6126e-05 | -0.00075192 | -0.0022751 | -0.0089111 | -0.0018308 | 0.0038282 | 0.0048556 | 0.021349 | 0.0049113 | 0.0037063 | -0.13275 | 0.14191 | -0.17395 | -0.12817 | -0.036621 | -0.14648 | -0.07782 | -0.1831 | 0.16022 | -0.13275 | -0.050354 | 0.013733 | -0.086975 | 0.036621 | 61.2396 | -61.3998 | -61.6699 | 61.377 | 61.3358 | 61.2671 | 0.09613 | 0.027466 | 61.2808 | -61.3815 | -61.5921 | 61.4273 | 61.4502 | 61.3266 | 0.16937 | 0.045776 | 0.13733 | 0.045776 | 0.14648 | 0.082397 | 0.31586 | 0.29297 | 61.5555 | 61.5738 | -61.7157 | -61.6745 | 61.2854 | 61.3632 | 61.2808 | 61.2305
717.3281 | 123.0423 | -61.4365 | 61.5692 | -0.060501 | 0.0015659 | 0.014007 | 0.036147 | 0.0018565 | -0.0011791 | -0.00056607 | -0.060791 | -0.00076257 | 0.0091688 | 0.006351 | 0.021563 | 0.0021341 | -0.0020615 | -0.14191 | 0.12817 | -0.13733 | -0.12817 | -0.036621 | -0.15106 | -0.10529 | -0.21973 | 0.16022 | -0.13733 | -0.07782 | -0.004578 | -0.10529 | 0.018311 | 61.2991 | -61.441 | -61.6974 | 61.3998 | 61.3312 | 61.2854 | 0.032043 | -0.013733 | 61.2991 | -61.409 | -61.647 | 61.4319 | 61.4548 | 61.3312 | 0.15564 | 0.032043 | 0.10071 | 0.009155 | 0.13275 | 0.059509 | 0.2655 | 0.29755 | 61.5646 | 61.5967 | -61.7065 | -61.7065 | 61.3083 | 61.3586 | 61.2946 | 61.2167
718.3281 | 123.175 | -61.4319 | 61.5509 | -0.091019 | -0.00057028 | 0.011871 | 0.040847 | 0.0052743 | -0.0016065 | -0.00077967 | -0.021118 | 9.1834e-05 | 0.004469 | -0.00091218 | 0.023058 | 0.0040567 | 0.0019973 | -0.16022 | 0.13733 | -0.16937 | -0.14648 | -0.036621 | -0.15106 | -0.068665 | -0.17395 | 0.15564 | -0.14191 | -0.032043 | 0.036621 | -0.059509 | 0.045776 | 61.2625 | -61.4136 | -61.6974 | 61.3953 | 61.3632 | 61.2808 | 0.10071 | 0.018311 | 61.29 | -61.3953 | -61.5829 | 61.4685 | 61.4777 | 61.3724 | 0.18768 | 0.082398 | 0.13275 | 0.022889 | 0.17853 | 0.10986 | 0.3067 | 0.29755 | 61.5692 | 61.5875 | -61.7203 | -61.6928 | 61.2854 | 61.3998 | 61.2717 | 61.2579
719.3281 | 123.0194 | -61.4456 | 61.5875 | -0.098648 | -0.00014308 | 0.013794 | 0.037002 | -0.0015615 | 0.00031608 | 7.4734e-05 | -0.048584 | -0.002899 | 0.0076734 | 0.0025058 | 0.020922 | 0.0040567 | -0.00056605 | -0.16022 | 0.12817 | -0.16479 | -0.12817 | -0.041199 | -0.14191 | -0.086975 | -0.2243 | 0.17853 | -0.1236 | -0.086975 | -0.013733 | -0.10986 | 0.013733 | 61.2808 | -61.4594 | -61.7157 | 61.4044 | 61.3586 | 61.3037 | 0.07782 | 0.022888 | 61.322 | -61.409 | -61.6745 | 61.4319 | 61.4594 | 61.3358 | 0.13733 | 0.013733 | 0.1236 | 0.036621 | 0.10986 | 0.036621 | 0.29297 | 0.30212 | 61.5738 | 61.6241 | -61.7523 | -61.7111 | 61.3174 | 61.3586 | 61.2854 | 61.2213
720.3281 | 123.1888 | -61.4456 | 61.5555 | -0.07576 | 0.0019931 | 0.014648 | 0.041488 | 0.0039927 | -0.00096552 | -0.00099327 | -0.036377 | -0.0035398 | 0.0089552 | -0.00091218 | 0.022418 | 0.0025613 | 0.0028519 | -0.16937 | 0.15564 | -0.15106 | -0.13275 | -0.027466 | -0.14191 | -0.082397 | -0.1831 | 0.16937 | -0.15106 | -0.036621 | 0.036621 | -0.068665 | 0.059509 | 61.2946 | -61.3998 | -61.6882 | 61.4182 | 61.3632 | 61.3037 | 0.068665 | 0.009155 | 61.2946 | -61.3861 | -61.5921 | 61.4822 | 61.5051 | 61.377 | 0.21057 | 0.082397 | 0.1236 | 0.018311 | 0.18768 | 0.11444 | 0.3067 | 0.32044 | 61.6013 | 61.615 | -61.7065 | -61.7065 | 61.3129 | 61.409 | 61.2762 | 61.2625
721.3281 | 123.1613 | -61.4273 | 61.5601 | -0.098648 | -0.00078408 | 0.014007 | 0.041061 | 0.0031381 | 0.0011707 | 0.0011429 | -0.033325 | -0.0035398 | 0.00511 | 0.00036962 | 0.020281 | 0.0055521 | 0.00071555 | -0.17395 | 0.14191 | -0.16937 | -0.16022 | -0.068665 | -0.12817 | -0.2243 | -0.10986 | 0.18768 | -0.09613 | -0.054932 | -0.027466 | -0.09613 | 0.036621 | 61.2579 | -61.4182 | -61.7203 | 61.3586 | 61.203 | 61.2991 | -0.054931 | 0.041199 | 61.3312 | -61.3724 | -61.615 | 61.3998 | 61.4639 | 61.3312 | 0.13275 | 0 | 0.10071 | 0.009156 | 0.068664 | 0.041198 | 0.31128 | 0.28381 | 61.5692 | 61.615 | -61.7294 | -61.6562 | 61.2671 | 61.3724 | 61.2534 | 61.3174
722.3281 | 123.2529 | -61.3907 | 61.528 | -0.06813 | 0.0017795 | 0.013794 | 0.037856 | 0.0010019 | 0.00052988 | -0.00013887 | 0.00024405 | -0.0024716 | 0.0063916 | 0.0035738 | 0.021349 | 0.0040567 | 0.0043471 | -0.13275 | 0.12817 | -0.16022 | -0.068665 | 0.054932 | -0.059509 | -0.022888 | -0.082397 | 0.14191 | -0.11444 | 0.032043 | 0.14648 | 0.018311 | 0.11902 | 61.2305 | -61.3998 | -61.5967 | 61.4456 | 61.3678 | 61.3312 | 0.13733 | 0.10071 | 61.2762 | -61.3861 | -61.496 | 61.5372 | 61.5097 | 61.409 | 0.23346 | 0.13275 | 0.21515 | 0.091552 | 0.26093 | 0.14648 | 0.28839 | 0.25635 | 61.5189 | 61.5326 | -61.6882 | -61.6425 | 61.322 | 61.4227 | 61.2579 | 61.3083
723.3281 | 123.1201 | -61.4365 | 61.5784 | -0.14442 | 0.0019931 | 0.01358 | 0.041274 | 0.00057467 | -0.0013929 | -0.0037705 | -0.057739 | -0.0043942 | 0.0074598 | 0.009769 | 0.021136 | 0.0029887 | -0.00035245 | -0.16022 | 0.15106 | -0.16479 | -0.15564 | -0.064087 | -0.16937 | -0.09613 | -0.32501 | 0.16479 | -0.1236 | -0.064087 | -0.045776 | -0.073242 | 0.032043 | 61.2717 | -61.4273 | -61.734 | 61.3724 | 61.3403 | 61.2671 | 0.068665 | -0.004578 | 61.3129 | -61.4136 | -61.6425 | 61.3907 | 61.4685 | 61.3632 | 0.15564 | 0.050354 | 0.10071 | 0.009155 | 0.07782 | 0.059509 | 0.31586 | 0.28839 | 61.5875 | 61.6013 | -61.7432 | -61.702 | 61.2808 | 61.3724 | 61.2762 | 61.1114
724.3281 | 123.2574 | -61.3907 | 61.528 | -0.091019 | 0.0019931 | 0.012085 | 0.040633 | -0.0015615 | 0.00095708 | -0.0014207 | 0.0063477 | -0.0026852 | 0.006819 | 0.0052828 | 0.02199 | 0.0036295 | -0.00077965 | -0.13275 | 0.12817 | -0.16022 | -0.091553 | 0.022888 | -0.09613 | -0.036621 | -0.11444 | 0.11902 | -0.10529 | 0.032043 | 0.1236 | 0.022888 | 0.12817 | 61.2305 | -61.3998 | -61.6196 | 61.4136 | 61.3541 | 61.2946 | 0.1236 | 0.064087 | 61.2854 | -61.409 | -61.496 | 61.5143 | 61.5189 | 61.4136 | 0.23346 | 0.12817 | 0.1831 | 0.068664 | 0.22888 | 0.13733 | 0.28839 | 0.22431 | 61.5189 | 61.5097 | -61.6882 | -61.6333 | 61.2991 | 61.4227 | 61.2579 | 61.2762
725.3281 | 123.1476 | -61.4594 | 61.5921 | -0.052872 | 0.0034885 | 0.012085 | 0.040847 | 0.00014747 | -0.00011112 | -0.0046249 | -0.048584 | -0.0020444 | 0.0063916 | 0.0016512 | 0.022204 | 0.011533 | 0.0054153 | -0.13733 | 0.13275 | -0.17395 | -0.16022 | -0.07782 | -0.1831 | -0.10529 | -0.22888 | 0.17395 | -0.16022 | -0.12817 | 0.19226 | 0.013733 | 0.050354 | 61.2854 | -61.4594 | -61.7523 | 61.3815 | 61.3541 | 61.2762 | 0.068664 | -0.009155 | 61.2991 | -61.4182 | -61.7203 | 61.6516 | 61.5097 | 61.4731 | 0.21057 | 0.17395 | 0.09613 | 0.013733 | 0.35248 | 0.032043 | 0.3067 | 0.33417 | 61.5921 | 61.6333 | -61.7661 | -61.7523 | 61.2991 | 61.3312 | 61.322 | 61.2305
726.3281 | 123.2483 | -61.3998 | 61.5463 | -0.10628 | 0.00049772 | 0.014435 | 0.040847 | 0.0012155 | -0.00011112 | -0.0022751 | 0.00024405 | -0.00076257 | 0.0042554 | 0.0037876 | 0.02199 | 0.0027751 | 0.0019973 | -0.1236 | 0.12817 | -0.16479 | -0.09613 | -0.004578 | -0.10986 | -0.041199 | -0.1236 | 0.15106 | -0.12817 | 0.018311 | 0.10071 | -0.009155 | 0.086975 | 61.235 | -61.4182 | -61.6425 | 61.3953 | 61.3586 | 61.29 | 0.1236 | 0.054932 | 61.2717 | -61.3953 | -61.528 | 61.5005 | 61.4868 | 61.3907 | 0.21515 | 0.11902 | 0.16022 | 0.068665 | 0.22888 | 0.14649 | 0.29297 | 0.27924 | 61.528 | 61.5509 | -61.7111 | -61.6745 | 61.3037 | 61.4182 | 61.2762 | 61.2762
727.3281 | 123.1613 | -61.4182 | 61.5463 | 0.15312 | 0.00049772 | 0.014007 | 0.043197 | -0.0011343 | -0.00096552 | -0.00056607 | -0.033325 | 0.00094643 | 0.0059644 | 0.001224 | 0.022204 | 0.0042703 | 0.0037063 | -0.22888 | 0.14648 | -0.15106 | -0.15564 | -0.059509 | -0.13275 | -0.09613 | -0.20142 | 0.15564 | -0.13733 | -0.059509 | 0 | -0.082397 | 0.027466 | 61.2671 | -61.3998 | -61.702 | 61.3586 | 61.322 | 61.2854 | 0.054932 | 0.018311 | 61.2808 | -61.3907 | -61.6058 | 61.4182 | 61.4456 | 61.3358 | 0.16479 | 0.054932 | 0.091553 | -0.004578 | 0.13733 | 0.07782 | 0.29755 | 0.29297 | 61.5646 | 61.5738 | -61.6974 | -61.6837 | 61.2625 | 61.3586 | 61.1893 | 61.2167
728.3281 | 123.262 | -61.3724 | 61.5509 | -0.12154 | 0.0013523 | 0.012726 | 0.039352 | -0.00070713 | -0.00011112 | -0.0022751 | 0.033813 | -0.0052488 | 0.0059644 | 0.0020786 | 0.022204 | 0.0021341 | 0.0032791 | -0.045776 | 0.050354 | -0.13733 | -0.013733 | 0.11444 | -0.032043 | 0.013733 | -0.050354 | 0.1236 | -0.10986 | 0.054932 | 0.13275 | 0.036621 | 0.10986 | 61.235 | -61.5005 | -61.5646 | 61.4868 | 61.3861 | 61.3403 | 0.15106 | 0.10529 | 61.2625 | -61.4273 | -61.496 | 61.5051 | 61.4822 | 61.409 | 0.21973 | 0.14648 | 0.25177 | 0.1236 | 0.24261 | 0.16479 | 0.18768 | 0.23346 | 61.4227 | 61.496 | -61.6882 | -61.6608 | 61.3586 | 61.4273 | 61.3266 | 61.322
729.3281 | 123.1705 | -61.4594 | 61.5555 | -0.052872 | 0.0028475 | 0.012512 | 0.041274 | 0.0074107 | -0.00053832 | 0.0015701 | 0.0032959 | -0.00054897 | 0.006819 | -0.002194 | 0.020068 | 0.0049113 | 0.0017837 | -0.13733 | 0.11902 | -0.15106 | -0.11444 | 0.20142 | -0.24719 | -0.10529 | -0.2655 | 0.1831 | -0.1236 | -0.07782 | -0.004578 | -0.09613 | 0.036621 | 61.3083 | -61.4365 | -61.6699 | 61.6608 | 61.3541 | 61.2122 | 0.045776 | -0.09613 | 61.3358 | -61.3724 | -61.6333 | 61.4548 | 61.496 | 61.3632 | 0.16022 | 0.027466 | 0.35248 | 0.036621 | 0.11902 | 0.045776 | 0.27008 | 0.3067 | 61.5784 | 61.6425 | -61.7065 | -61.6791 | 61.3449 | 61.3815 | 61.322 | 61.1938
730.3281 | 123.262 | -61.3815 | 61.5463 | -0.083389 | 7.0518e-05 | 0.012939 | 0.040847 | 0.0010019 | 0.00010248 | 0.00028833 | -0.033325 | -0.002899 | 0.0072462 | 0.00058322 | 0.020922 | 0.0042703 | 0.0017837 | -0.10529 | 0.10529 | -0.14191 | -0.045776 | 0.064087 | -0.059509 | 0.009155 | -0.09613 | 0.14648 | -0.11902 | 0.054932 | 0.1236 | 0.032043 | 0.12817 | 61.2396 | -61.441 | -61.5921 | 61.4456 | 61.3907 | 61.322 | 0.15106 | 0.082398 | 61.2625 | -61.3998 | -61.4914 | 61.5051 | 61.5097 | 61.4136 | 0.24719 | 0.15106 | 0.20599 | 0.096131 | 0.24261 | 0.17395 | 0.24719 | 0.2655 | 61.4868 | 61.528 | -61.6882 | -61.6653 | 61.3358 | 61.4365 | 61.2762 | 61.2854
731.3281 | 123.1934 | -61.4319 | 61.5738 | -0.07576 | 0.0019931 | 0.013153 | 0.04341 | -6.6126e-05 | 0.00052988 | 0.00028833 | -0.027222 | -0.0024716 | 0.0072462 | 0.006351 | 0.02199 | 0.0046977 | 0.0013565 | -0.13733 | 0.13275 | -0.16479 | -0.15106 | -0.068665 | -0.15564 | -0.09613 | -0.086975 | 0.17853 | -0.13275 | -0.032043 | 0.013733 | -0.10986 | 0.027466 | 61.2671 | -61.441 | -61.7249 | 61.3632 | 61.3358 | 61.2762 | 0.068665 | 0.009155 | 61.2991 | -61.3953 | -61.6058 | 61.4456 | 61.4594 | 61.322 | 0.16022 | 0.022888 | 0.09613 | 0.013733 | 0.14648 | 0.10071 | 0.29755 | 0.31128 | 61.5646 | 61.6104 | -61.7386 | -61.7065 | 61.2808 | 61.3998 | 61.2946 | 61.3449
732.3281 | 123.2712 | -61.3998 | 61.528 | -0.07576 | 0.0024203 | 0.011871 | 0.041915 | 0.0035653 | -0.00075192 | -0.0020615 | -0.0028075 | 0.0020144 | 0.0066052 | 0.0050692 | 0.021349 | 0.0014933 | 0.0024245 | -0.045776 | 0.10986 | -0.10071 | -0.027466 | 0.10071 | -0.036621 | 0.032043 | -0.27924 | 0.10529 | -0.10986 | 0.068665 | 0.11444 | 0.050354 | 0.12817 | 61.2991 | -61.4182 | -61.5555 | 61.5005 | 61.4319 | 61.3632 | 0.13275 | 0.064087 | 61.29 | -61.4227 | -61.4594 | 61.5143 | 61.528 | 61.4502 | 0.23804 | 0.16022 | 0.20142 | 0.073242 | 0.2243 | 0.17853 | 0.21057 | 0.21515 | 61.5097 | 61.5051 | -61.6287 | -61.6379 | 61.3724 | 61.4685 | 61.3541 | 61.1206
733.3281 | 123.2849 | -61.4685 | 61.5417 | -0.083389 | 0.0013523 | 0.013153 | 0.037856 | 0.0020701 | -0.0020337 | -0.00077967 | -0.045532 | -0.00012177 | 0.0074598 | 0.00058322 | 0.019854 | 0.0057657 | 0.00028835 | -0.13733 | 0.14648 | -0.15564 | -0.13733 | -0.086975 | -0.17853 | -0.10529 | -0.24719 | 0.17395 | -0.1236 | -0.059509 | -0.009155 | -0.091553 | 0.027466 | 61.3129 | -61.3953 | -61.6791 | 61.3815 | 61.3632 | 61.29 | 0.050354 | -0.022888 | 61.3449 | -61.3678 | -61.6013 | 61.4594 | 61.496 | 61.377 | 0.15106 | 0.032043 | 0.068665 | 0.018311 | 0.11444 | 0.064087 | 0.30212 | 0.29755 | 61.615 | 61.6425 | -61.6974 | -61.6653 | 61.3312 | 61.409 | 61.3312 | 61.2213
734.3281 | 123.2117 | -61.4365 | 61.5463 | -0.045242 | 0.00028412 | 0.014648 | 0.040847 | 0.0029245 | 0.00052988 | -0.00056607 | -0.036377 | -0.00097617 | 0.0063916 | -0.001553 | 0.022418 | 0.0051249 | 0.0043471 | -0.1236 | 0.13275 | -0.17395 | -0.1236 | -0.027466 | -0.12817 | -0.064087 | -0.16022 | 0.15564 | -0.13275 | 0.004578 | 0.059509 | -0.027466 | 0.07782 | 61.2625 | -61.4136 | -61.6699 | 61.409 | 61.3724 | 61.3083 | 0.10986 | 0.045776 | 61.3037 | -61.3907 | -61.5417 | 61.496 | 61.5143 | 61.409 | 0.21057 | 0.10529 | 0.14648 | 0.050354 | 0.19226 | 0.13733 | 0.3067 | 0.28839 | 61.5692 | 61.5921 | -61.7203 | -61.6791 | 61.3129 | 61.441 | 61.3129 | 61.2762
735.3281 | 123.1705 | -61.4456 | 61.5829 | -0.07576 | 0.0017795 | 0.012298 | 0.044906 | 0.0022837 | -0.00053832 | -0.0018479 | -0.069946 | -0.0026852 | 0.00511 | 0.0048556 | 0.020495 | 0.0038431 | -0.0018479 | -0.13275 | 0.14191 | -0.18768 | -0.022888 | -0.10986 | -0.1236 | -0.013733 | -0.18768 | 0.17853 | -0.13733 | -0.054932 | -0.009155 | -0.10071 | 0.027466 | 61.2579 | -61.441 | -61.6058 | 61.3358 | 61.4319 | 61.322 | 0.17395 | 0.064087 | 61.3083 | -61.4044 | -61.6379 | 61.4365 | 61.4731 | 61.3449 | 0.16479 | 0.036621 | 0.07782 | 0.16479 | 0.12817 | 0.082397 | 0.32959 | 0.31586 | 61.5875 | 61.6241 | -61.7706 | -61.7203 | 61.4227 | 61.3907 | 61.3129 | 61.2579
736.3281 | 123.2941 | -61.377 | 61.5601 | -0.10628 | 0.0011385 | 0.014007 | 0.039352 | 0.00078827 | -0.0016065 | -0.00099327 | 0.021606 | -0.005676 | 0.004469 | 0.0044284 | 0.021349 | 0.0023477 | 0.0030655 | -0.059509 | 0.10071 | -0.10986 | 0.032043 | 0.041199 | -0.004578 | 0.032043 | -0.022888 | 0.086975 | -0.10529 | 0.050354 | 0.14191 | 0.036621 | 0.1236 | 61.2671 | -61.4594 | -61.528 | 61.4182 | 61.409 | 61.3724 | 0.14191 | 0.10529 | 61.2717 | -61.4731 | -61.5097 | 61.5189 | 61.5005 | 61.4136 | 0.22888 | 0.14191 | 0.15106 | 0.14191 | 0.24719 | 0.15564 | 0.21057 | 0.19226 | 61.4777 | 61.4639 | -61.6699 | -61.6653 | 61.409 | 61.4273 | 61.3174 | 61.3541
737.3281 | 123.1384 | -61.4548 | 61.6058 | -0.07576 | 0.0017795 | 0.012298 | 0.042983 | 0.0035653 | -0.00096552 | -0.0018479 | -0.045532 | -0.00012177 | 0.0048962 | 0.0050692 | 0.01964 | 0.0032023 | 0.0030655 | -0.13275 | 0.13275 | -0.16022 | -0.16022 | -0.082397 | -0.16479 | -0.09613 | -0.19684 | 0.19226 | -0.16479 | -0.10986 | -0.004578 | -0.041199 | 0.032043 | 61.2946 | -61.4731 | -61.7661 | 61.3724 | 61.3586 | 61.29 | 0.064087 | -0.004578 | 61.29 | -61.4136 | -61.7157 | 61.4502 | 61.4868 | 61.4136 | 0.19684 | 0.1236 | 0.07782 | 0 | 0.16022 | 0.054932 | 0.29297 | 0.35706 | 61.5875 | 61.647 | -61.7661 | -61.7706 | 61.2946 | 61.3449 | 61.322 | 61.2579
738.3281 | 123.2849 | -61.3815 | 61.5326 | -0.083389 | 0.00049772 | 0.012939 | 0.039565 | -0.00027993 | 0.0024525 | -0.0061203 | -0.011963 | -0.0048216 | 0.0025464 | 0.0048556 | 0.024554 | 0.0046977 | 0.0058425 | -0.050354 | 0.10529 | -0.13275 | -0.004578 | 0.10529 | -0.027466 | 0.018311 | -0.2243 | 0.09613 | -0.10071 | 0.054932 | 0.13275 | 0.036621 | 0.13733 | 61.2488 | -61.4273 | -61.5372 | 61.4868 | 61.3998 | 61.3541 | 0.15106 | 0.10529 | 61.2808 | -61.4365 | -61.4777 | 61.5143 | 61.5189 | 61.4182 | 0.23804 | 0.13733 | 0.23804 | 0.12817 | 0.23346 | 0.15564 | 0.23804 | 0.19684 | 61.4868 | 61.4777 | -61.6653 | -61.6333 | 61.377 | 61.4365 | 61.3312 | 61.1572
739.3281 | 123.1155 | -61.4456 | 61.5143 | -0.060501 | 0.00028412 | 0.012298 | 0.041701 | 0.0022837 | 0.0011707 | 0.00050193 | -0.054688 | -0.00119 | 0.0053236 | 0.0057102 | 0.022631 | 0.0036295 | 0.0047745 | -0.15564 | 0.13733 | -0.16479 | -0.14191 | -0.064087 | -0.17853 | -0.10986 | -0.24261 | 0.16937 | -0.15106 | -0.059509 | -0.004578 | -0.10529 | 0.068665 | 61.2808 | -61.377 | -61.6562 | 61.3815 | 61.3358 | 61.2671 | 0.054932 | -0.013733 | 61.2946 | -61.3449 | -61.5738 | 61.441 | 61.5143 | 61.3403 | 0.21973 | 0.045776 | 0.10071 | 0.022888 | 0.14648 | 0.091553 | 0.30212 | 0.32044 | 61.5829 | 61.615 | -61.6791 | -61.6653 | 61.3037 | 61.3861 | 61.29 | 61.203
740.3281 | 123.2529 | -61.4044 | 61.5417 | -0.098648 | -0.00099768 | 0.01358 | 0.041488 | -0.00027993 | 0.00074348 | 0.0024245 | -0.018066 | -0.0016172 | 0.006178 | -0.0030484 | 0.020922 | 0.0038431 | 0.0013565 | -0.1236 | 0.14191 | -0.15564 | -0.10071 | 0.009155 | -0.10529 | -0.050354 | -0.14191 | 0.15564 | -0.14191 | 0.009155 | 0.091553 | -0.018311 | 0.082397 | 61.2488 | -61.3998 | -61.6425 | 61.4136 | 61.3541 | 61.2991 | 0.10529 | 0.050354 | 61.2625 | -61.3861 | -61.5326 | 61.496 | 61.4868 | 61.3861 | 0.2243 | 0.1236 | 0.16479 | 0.054932 | 0.23346 | 0.15106 | 0.29755 | 0.29755 | 61.5463 | 61.5601 | -61.6974 | -61.6837 | 61.3037 | 61.4136 | 61.2808 | 61.2625
741.3281 | 123.175 | -61.4594 | 61.5463 | -0.06813 | 0.00028412 | 0.015716 | 0.042129 | 0.0044199 | -0.0011791 | 0.00050193 | -0.039429 | -0.0026852 | 0.006178 | -0.001553 | 0.023058 | 0.0034159 | -0.00035245 | -0.21057 | 0.13275 | -0.13733 | -0.14191 | -0.10529 | -0.10529 | -0.07782 | -0.19684 | 0.15564 | -0.13275 | -0.054932 | 0.004578 | -0.09613 | 0.032043 | 61.322 | -61.4136 | -61.6882 | 61.3541 | 61.3815 | 61.3541 | 0.059509 | 0.032043 | 61.3266 | -61.3907 | -61.6013 | 61.4639 | 61.4914 | 61.3632 | 0.16479 | 0.036621 | 0.032043 | -0.004578 | 0.13733 | 0.077819 | 0.27008 | 0.28839 | 61.5921 | 61.615 | -61.6837 | -61.6791 | 61.3174 | 61.4044 | 61.2488 | 61.2625
742.3281 | 123.2895 | -61.3998 | 61.5189 | 0.069199 | 0.0028475 | 0.014221 | 0.039138 | 0.0035653 | -0.00096552 | -0.0027023 | 0.018555 | -0.003967 | 0.0070326 | -0.0013394 | 0.022204 | 0.0040567 | -0.00035245 | -0.10071 | 0.07782 | -0.11444 | -0.022888 | 0.10071 | -0.013733 | 0.022888 | -0.041199 | 0.11444 | -0.10529 | 0.041199 | 0.13275 | 0.036621 | 0.12817 | 61.2854 | -61.441 | -61.5417 | 61.5005 | 61.4227 | 61.3861 | 0.13733 | 0.10071 | 61.2946 | -61.4044 | -61.4777 | 61.5326 | 61.528 | 61.4365 | 0.23346 | 0.14191 | 0.21515 | 0.091553 | 0.23804 | 0.14649 | 0.19226 | 0.21973 | 61.4777 | 61.5143 | -61.6333 | -61.6241 | 61.377 | 61.441 | 61.2991 | 61.3586
743.3281 | 123.1705 | -61.4456 | 61.5921 | -0.052872 | 0.0017795 | 0.012085 | 0.041701 | -0.0011343 | 0.0022387 | -0.0029159 | -0.027222 | -0.00054897 | 0.0063916 | 0.004642 | 0.021136 | 0.0042703 | 0.0015701 | -0.12817 | 0.12817 | -0.1831 | -0.17853 | 0.21973 | -0.19226 | -0.09613 | -0.23346 | 0.16479 | -0.10986 | -0.045776 | 0 | -0.09613 | 0.022888 | 61.2625 | -61.4639 | -61.7706 | 61.6653 | 61.3495 | 61.2534 | 0.086975 | -0.009156 | 61.3358 | -61.4273 | -61.6379 | 61.4456 | 61.4685 | 61.3495 | 0.13275 | 0.013733 | 0.40283 | 0.004577 | 0.10986 | 0.064087 | 0.31128 | 0.27466 | 61.5738 | 61.6104 | -61.7752 | -61.702 | 61.2671 | 61.3998 | 61.3174 | 61.2122
744.3281 | 123.2849 | -61.409 | 61.5417 | -0.083389 | 0.0015659 | 0.014435 | 0.041915 | 0.0014291 | -0.0020337 | -0.0063339 | -0.018066 | -0.002258 | 0.004469 | 0.001224 | 0.021136 | 0.0023477 | 0.0043471 | -0.082397 | 0.11902 | -0.12817 | -0.041199 | 0.07782 | -0.07782 | 0.022888 | -0.082397 | 0.13275 | -0.11902 | 0.050354 | 0.11902 | 0.036621 | 0.14191 | 61.2808 | -61.4227 | -61.5829 | 61.4868 | 61.4319 | 61.3312 | 0.15106 | 0.050354 | 61.29 | -61.409 | -61.4914 | 61.528 | 61.5509 | 61.4456 | 0.26093 | 0.15564 | 0.20599 | 0.086975 | 0.23804 | 0.16937 | 0.24719 | 0.25177 | 61.528 | 61.5417 | -61.6699 | -61.6608 | 61.3678 | 61.4594 | 61.3266 | 61.3266
745.3281 | 123.1842 | -61.4365 | 61.5738 | -0.045242 | -0.00014308 | 0.013366 | 0.039779 | -0.0015615 | -0.00096552 | -0.0024887 | -0.10352 | -0.002258 | 0.0091688 | 0.00036962 | 0.020281 | 0.0057657 | -0.00077965 | -0.15106 | 0.13733 | -0.16022 | -0.14191 | -0.054932 | -0.091553 | -0.21973 | -0.09613 | 0.17395 | -0.09613 | -0.041199 | -0.018311 | -0.10986 | 0.013733 | 61.2762 | -61.4365 | -61.7157 | 61.3815 | 61.2167 | 61.3449 | -0.05951 | 0.068664 | 61.3403 | -61.3998 | -61.615 | 61.4182 | 61.4502 | 61.3266 | 0.10986 | -0.013733 | 0.10528 | 0.01831 | 0.077819 | 0.054931 | 0.29755 | 0.27008 | 61.5738 | 61.6104 | -61.734 | -61.6699 | 61.2946 | 61.3953 | 61.2854 | 61.3403
746.3281 | 123.3032 | -61.4136 | 61.5417 | -0.10628 | 0.00028412 | 0.01358 | 0.038497 | 0.0020701 | -0.0013929 | -0.0024887 | 0.012451 | -0.0016172 | 0.006178 | 0.0033602 | 0.020922 | 0.0019205 | 0.0041335 | -0.054932 | 0.09613 | -0.12817 | -0.18768 | 0.10529 | 0.12817 | -0.050354 | -0.064087 | 0.10071 | -0.12817 | 0.073242 | 0.12817 | 0.045776 | 0.13733 | 61.2854 | -61.4456 | -61.7294 | 61.5189 | 61.3632 | 61.5417 | 0.07782 | 0.25635 | 61.2854 | -61.441 | -61.4685 | 61.5417 | 61.5509 | 61.4593 | 0.2655 | 0.17395 | 0.23346 | -0.059509 | 0.25635 | 0.20142 | 0.2243 | 0.22888 | 61.5097 | 61.5143 | -61.6699 | -61.6699 | 61.2259 | 61.4868 | 61.3586 | 61.3495
747.3281 | 123.1979 | -61.441 | 61.5509 | -0.10628 | 0.0011385 | 0.014862 | 0.041701 | -0.00049353 | -0.0022473 | 0.0011429 | -0.033325 | -0.0018308 | 0.0055372 | -5.7584e-05 | 0.020281 | 0.0044839 | -0.0048387 | -0.1236 | 0.14191 | -0.15564 | -0.1236 | -0.036621 | -0.15106 | -0.07782 | -0.17853 | 0.16937 | -0.14648 | -0.032043 | 0.018311 | -0.086975 | 0.045776 | 61.2854 | -61.409 | -61.6745 | 61.4044 | 61.3632 | 61.29 | 0.07782 | 0.004578 | 61.2946 | -61.3815 | -61.5829 | 61.4594 | 61.4868 | 61.3541 | 0.19226 | 0.059509 | 0.11902 | 0.032044 | 0.16479 | 0.11444 | 0.29755 | 0.31586 | 61.5829 | 61.6104 | -61.7065 | -61.6974 | 61.3174 | 61.409 | 61.3174 | 61.2625
748.3281 | 123.3032 | -61.4227 | 61.5509 | -0.098648 | 0.00092492 | 0.01358 | 0.04042 | -0.0011343 | -0.0026745 | -0.0018479 | -0.10657 | -0.0026852 | 0.0057508 | -0.0013394 | 0.021563 | 0.0044839 | -0.00035245 | -0.041199 | 0.1236 | -0.12817 | -0.027466 | 0.09613 | -0.022888 | 0.013733 | 0.068665 | 0.10529 | -0.10986 | 0.054932 | 0.16479 | 0.036621 | 0.1236 | 61.2946 | -61.4273 | -61.5784 | 61.5189 | 61.4365 | 61.3998 | 0.14191 | 0.10529 | 61.3129 | -61.4456 | -61.496 | 61.5875 | 61.5463 | 61.4593 | 0.23346 | 0.14648 | 0.2243 | 0.10071 | 0.27466 | 0.16479 | 0.25177 | 0.21515 | 61.5463 | 61.528 | -61.6791 | -61.6608 | 61.3953 | 61.4777 | 61.3815 | 61.4914
749.3281 | 123.1796 | -61.4365 | 61.5784 | -0.052872 | 0.00028412 | 0.011871 | 0.042129 | 0.00057467 | 0.00095708 | -0.0012071 | -0.045532 | -0.0024716 | 0.0063916 | 0.0052828 | 0.021349 | 0.0057657 | 0.0043471 | -0.14648 | 0.14191 | -0.13733 | -0.1236 | -0.027466 | -0.15106 | -0.086975 | -0.16937 | 0.16937 | -0.15106 | -0.045776 | 0.009155 | -0.091553 | 0.027466 | 61.2991 | -61.4365 | -61.702 | 61.409 | 61.3495 | 61.2854 | 0.050354 | -0.013733 | 61.2854 | -61.409 | -61.6241 | 61.4456 | 61.4639 | 61.3449 | 0.17853 | 0.059509 | 0.10986 | 0.013733 | 0.16022 | 0.10529 | 0.27924 | 0.32044 | 61.5784 | 61.6058 | -61.7157 | -61.7294 | 61.3129 | 61.3907 | 61.29 | 61.2671
750.3281 | 123.3124 | -61.4136 | 61.5417 | -0.07576 | -0.00014308 | 0.012512 | 0.041915 | 0.0027109 | -0.0020337 | -0.00056607 | -0.021118 | -0.0026852 | 0.0063916 | 0.0048556 | 0.01964 | 0.0019205 | 0.00071555 | -0.041199 | 0.10986 | -0.10529 | -0.013733 | 0.086975 | -0.027466 | 0.009155 | -0.041199 | 0.13733 | -0.10986 | 0.10986 | 0.059509 | 0.054932 | 0.13275 | 61.3083 | -61.4319 | -61.5555 | 61.5005 | 61.4227 | 61.3861 | 0.11444 | 0.07782 | 61.3037 | -61.4044 | -61.4319 | 61.4731 | 61.5463 | 61.4685 | 0.24261 | 0.16479 | 0.19226 | 0.091553 | 0.16937 | 0.21973 | 0.21515 | 0.24719 | 61.5234 | 61.5509 | -61.647 | -61.6516 | 61.3998 | 61.5234 | 61.3724 | 61.3724
751.3281 | 123.1888 | -61.4502 | 61.5829 | 0.15312 | -0.00057028 | 0.012726 | 0.041061 | 0.0024973 | -0.00075192 | -0.0044113 | -0.063843 | -0.0016172 | 0.0072462 | 0.0059238 | 0.021777 | 0.0055521 | 0.0013565 | -0.18768 | 0.16022 | -0.13275 | -0.13733 | -0.073242 | -0.14648 | -0.091553 | -0.19226 | 0.15564 | -0.14648 | -0.050354 | 0.013733 | -0.091553 | 0.032043 | 61.3174 | -61.4227 | -61.7203 | 61.377 | 61.3586 | 61.3037 | 0.041198 | -0.013733 | 61.3037 | -61.4273 | -61.6333 | 61.4639 | 61.4822 | 61.3586 | 0.17853 | 0.054931 | 0.059509 | -0.004578 | 0.16022 | 0.09613 | 0.29297 | 0.30212 | 61.6104 | 61.6058 | -61.7157 | -61.7294 | 61.3129 | 61.3998 | 61.2625 | 61.2579
752.3281 | 123.3124 | -61.4182 | 61.5784 | -0.06813 | 0.0015659 | 0.01358 | 0.039779 | -0.0011343 | 0.00010248 | -0.0018479 | 0.049072 | -0.00119 | 0.006178 | -0.0028348 | 0.021136 | 0.0014933 | -0.0033433 | -0.073242 | 0.09613 | -0.09613 | -0.004578 | 0.10071 | 0.009155 | 0.041199 | -0.054932 | 0.14191 | -0.09613 | 0.050354 | 0.17395 | 0.07782 | 0.13275 | 61.322 | -61.4822 | -61.5829 | 61.5189 | 61.4594 | 61.4273 | 0.13733 | 0.10528 | 61.322 | -61.4365 | -61.528 | 61.5921 | 61.5509 | 61.496 | 0.22888 | 0.17395 | 0.19684 | 0.091552 | 0.27008 | 0.14648 | 0.19226 | 0.23804 | 61.5143 | 61.5601 | -61.6745 | -61.6745 | 61.4136 | 61.4685 | 61.3449 | 61.3632
753.3281 | 123.1796 | -61.4502 | 61.615 | -0.029984 | 0.0013523 | 0.012085 | 0.042983 | 0.0022837 | 0.00010248 | -0.0012071 | -0.066895 | -0.002899 | 0.0055372 | 0.0042148 | 0.02199 | 0.0040567 | -0.00056605 | -0.11902 | 0.11444 | -0.17853 | 0.018311 | 0.091553 | -0.29297 | -0.022888 | -0.20599 | 0.17853 | -0.12817 | -0.050354 | 0 | -0.082397 | 0.013733 | 61.2717 | -61.5005 | -61.5967 | 61.5417 | 61.4273 | 61.1572 | 0.15564 | -0.11444 | 61.322 | -61.4365 | -61.6653 | 61.4502 | 61.4639 | 61.3678 | 0.14191 | 0.045777 | 0.27008 | 0.19684 | 0.12817 | 0.07782 | 0.29297 | 0.3067 | 61.5646 | 61.6287 | -61.7935 | -61.7432 | 61.4685 | 61.3998 | 61.3312 | 61.2442
754.3281 | 123.2895 | -61.4136 | 61.5601 | -0.060501 | 0.0015659 | 0.012085 | 0.04277 | 0.0014291 | -0.00075192 | -0.0033433 | -0.02417 | -0.003967 | 0.0070326 | 0.00058322 | 0.022631 | 0.0038431 | 0.0011429 | -0.086975 | 0.12817 | -0.15564 | -0.050354 | 0.054932 | -0.054932 | -0.004578 | -0.054932 | 0.12817 | -0.086975 | 0.045776 | 0.12817 | 0.027466 | 0.12817 | 61.2579 | -61.4319 | -61.6104 | 61.4685 | 61.409 | 61.3586 | 0.15106 | 0.10071 | 61.3266 | -61.4319 | -61.5143 | 61.5417 | 61.5417 | 61.441 | 0.21515 | 0.11444 | 0.21057 | 0.10529 | 0.21515 | 0.13275 | 0.28381 | 0.21515 | 61.5417 | 61.5417 | -61.7157 | -61.647 | 61.3632 | 61.4593 | 61.3266 | 61.3586
755.3281 | 123.2162 | -61.4639 | 61.5829 | -0.10628 | -0.00035668 | 0.014221 | 0.044051 | 0.0018565 | -0.00075192 | -0.0033433 | -0.042481 | -0.00033537 | 0.0059644 | 0.002933 | 0.021563 | 0.0040567 | 0.0052017 | -0.12817 | 0.13275 | -0.16479 | -0.12817 | -0.050354 | -0.14648 | -0.091553 | -0.18768 | 0.15564 | -0.13733 | -0.032043 | 0.013733 | -0.054932 | 0.059509 | 61.2991 | -61.4502 | -61.7111 | 61.4136 | 61.3724 | 61.3174 | 0.073242 | 0.018311 | 61.3266 | -61.4273 | -61.615 | 61.4777 | 61.5234 | 61.409 | 0.19684 | 0.082397 | 0.11444 | 0.036621 | 0.15106 | 0.10529 | 0.29755 | 0.29297 | 61.5967 | 61.6196 | -61.7477 | -61.7203 | 61.3358 | 61.4319 | 61.3358 | 61.2762
756.3281 | 123.3078 | -61.4319 | 61.5417 | -0.083389 | -0.00014308 | 0.013794 | 0.040847 | -0.00049353 | -0.00096552 | -0.0033433 | -0.011963 | -0.0031126 | 0.0040418 | -0.001553 | 0.018572 | 0.0032023 | 0.0056289 | -0.045776 | 0.086975 | -0.11444 | 0.004578 | 0.091553 | -0.027466 | 0.027466 | -0.032043 | 0.11902 | -0.10986 | 0.018311 | 0.15564 | 0.045776 | 0.11444 | 61.3174 | -61.4548 | -61.5372 | 61.5234 | 61.4594 | 61.4044 | 0.14191 | 0.086975 | 61.322 | -61.4227 | -61.5234 | 61.5875 | 61.5463 | 61.4777 | 0.2243 | 0.15564 | 0.20599 | 0.11902 | 0.2655 | 0.12817 | 0.20142 | 0.22888 | 61.5189 | 61.5509 | -61.6562 | -61.6516 | 61.4365 | 61.4502 | 61.3861 | 61.3998
757.3438 | 123.2574 | -61.4319 | 61.5692 | -0.098648 | 0.0015659 | 0.010162 | 0.039779 | -0.00092073 | 0.00010248 | -0.0024887 | 0.018555 | -0.0018308 | 0.0040418 | 0.0020786 | 0.022418 | 0.0038431 | 0.0024245 | -0.091553 | 0.11902 | -0.09613 | -0.059509 | 0.050354 | -0.050354 | -0.013733 | -0.2243 | 0.11902 | -0.13733 | -0.041199 | 0.064087 | -0.018311 | 0.059509 | 61.3358 | -61.4502 | -61.6287 | 61.4822 | 61.4182 | 61.3815 | 0.082397 | 0.045776 | 61.2946 | -61.4502 | -61.6104 | 61.496 | 61.4914 | 61.4136 | 0.19684 | 0.11902 | 0.14648 | 0.036621 | 0.20142 | 0.09613 | 0.21515 | 0.25635 | 61.5509 | 61.5509 | -61.6653 | -61.7065 | 61.3724 | 61.3907 | 61.3403 | 61.2076
758.3281 | 123.317 | -61.4044 | 61.5646 | -0.083389 | 0.00028412 | 0.012939 | 0.04277 | 0.0020701 | 0.0018115 | -0.0012071 | -0.011963 | -0.0018308 | 0.0046826 | 0.0048556 | 0.020922 | 0.0046977 | 0.0026383 | -0.068665 | 0.09613 | -0.13275 | -0.018311 | 0.086975 | -0.036621 | 0.032043 | -0.045776 | 0.1236 | -0.10529 | 0.054932 | 0.13275 | 0.022888 | 0.13733 | 61.2717 | -61.4685 | -61.5829 | 61.4914 | 61.4365 | 61.3678 | 0.16479 | 0.09613 | 61.2991 | -61.441 | -61.5097 | 61.5372 | 61.5417 | 61.4273 | 0.24262 | 0.12817 | 0.21973 | 0.11444 | 0.23804 | 0.16022 | 0.22888 | 0.22888 | 61.5005 | 61.528 | -61.6974 | -61.6699 | 61.3861 | 61.4594 | 61.3358 | 61.3586
759.3281 | 123.1934 | -61.4685 | 61.5875 | -0.06813 | 0.0022067 | 0.013153 | 0.042129 | -0.0019889 | 0.00074348 | -0.0016343 | -0.082153 | -0.002899 | 0.0046826 | 0.0089144 | 0.022631 | 0.0040567 | 0.0039199 | -0.14648 | 0.14191 | -0.16937 | 0.009155 | -0.15106 | -0.21057 | 0.18768 | -0.17395 | 0.17853 | -0.10986 | -0.064087 | 0.004578 | -0.10529 | 0.013733 | 61.2991 | -61.4456 | -61.5784 | 61.3174 | 61.6562 | 61.2579 | 0.35706 | -0.041198 | 61.3586 | -61.409 | -61.6516 | 61.4731 | 61.4822 | 61.3632 | 0.1236 | 0.004577 | 0.018311 | 0.17853 | 0.11444 | 0.045776 | 0.31128 | 0.28839 | 61.6104 | 61.647 | -61.7569 | -61.6974 | 61.4777 | 61.4044 | 61.322 | 61.2946
760.3281 | 123.2986 | -61.3998 | 61.5692 | -0.091019 | 0.0022067 | 0.012085 | 0.042556 | 0.0029245 | 0.0020251 | -0.0018479 | -0.051636 | -0.0016172 | 0.0042554 | -0.0026212 | 0.02199 | 0.0027751 | 0.0024245 | -0.11902 | 0.1236 | -0.14648 | -0.086975 | 0.022888 | -0.10529 | -0.013733 | -0.086975 | 0.12817 | -0.11444 | 0.041199 | 0.1236 | 0 | 0.12817 | 61.2534 | -61.4456 | -61.6562 | 61.4227 | 61.3861 | 61.2946 | 0.13275 | 0.041198 | 61.2854 | -61.441 | -61.528 | 61.5234 | 61.528 | 61.3998 | 0.24262 | 0.11444 | 0.16937 | 0.059509 | 0.23804 | 0.15564 | 0.27008 | 0.24262 | 61.5234 | 61.528 | -61.7157 | -61.6837 | 61.3129 | 61.441 | 61.2808 | 61.3129
761.3281 | 123.2117 | -61.4502 | 61.6104 | -0.083389 | 7.0518e-05 | 0.011444 | 0.042129 | 0.0029245 | -0.0020337 | -0.00099327 | -0.048584 | -0.00033537 | 0.0074598 | 0.0061374 | 0.023913 | 0.0044839 | -0.00077965 | -0.10071 | 0.15564 | -0.14648 | -0.13733 | -0.045776 | -0.13733 | -0.07782 | -0.19684 | 0.16479 | -0.13733 | -0.050354 | 0.018311 | -0.091553 | 0.036621 | 61.3037 | -61.4548 | -61.7477 | 61.4044 | 61.3724 | 61.3129 | 0.068664 | 0.009155 | 61.3129 | -61.4456 | -61.6608 | 61.4685 | 61.4868 | 61.3586 | 0.17395 | 0.045776 | 0.10071 | 0.009155 | 0.15564 | 0.086975 | 0.30212 | 0.30212 | 61.6058 | 61.615 | -61.7569 | -61.7477 | 61.3129 | 61.3998 | 61.3495 | 61.2534
762.3438 | 123.1842 | -61.4319 | 61.6241 | -0.045242 | 0.00028412 | 0.012298 | 0.039565 | -0.0011343 | -0.0011791 | -0.0056931 | 0.0093995 | -0.00097617 | 0.0055372 | 0.0010104 | 0.023913 | 0.0027751 | 0.0022109 | -0.07782 | 0.14648 | -0.12817 | -0.064087 | 0.036621 | -0.054932 | -0.036621 | -0.16022 | 0.16937 | -0.11902 | -0.068665 | 0.045776 | -0.050354 | 0.022888 | 61.3037 | -61.4777 | -61.6882 | 61.4685 | 61.3953 | 61.377 | 0.091553 | 0.073242 | 61.3129 | -61.4548 | -61.6928 | 61.4777 | 61.4548 | 61.3815 | 0.14191 | 0.068665 | 0.1648 | 0.064087 | 0.16479 | 0.050354 | 0.27466 | 0.28839 | 61.5784 | 61.6013 | -61.7523 | -61.7432 | 61.3678 | 61.3632 | 61.3541 | 61.2717
763.3281 | 123.2574 | -61.441 | 61.5921 | -0.060501 | 7.0518e-05 | 0.013153 | 0.041061 | 0.00014747 | 0.00052988 | -0.0022751 | -0.027222 | -0.0014036 | 0.006178 | 0.0057102 | 0.02199 | 0.0049113 | 0.0037063 | -0.12817 | 0.12817 | -0.15106 | -0.1236 | -0.036621 | -0.13733 | -0.068665 | -0.16937 | 0.16479 | -0.13733 | -0.018311 | 0.041199 | -0.045776 | 0.064087 | 61.29 | -61.4639 | -61.7157 | 61.4044 | 61.3724 | 61.3037 | 0.082397 | 0.013733 | 61.3037 | -61.4273 | -61.6104 | 61.4822 | 61.5051 | 61.3953 | 0.20142 | 0.091553 | 0.11444 | 0.027466 | 0.17853 | 0.11902 | 0.27924 | 0.30212 | 61.5692 | 61.6058 | -61.7432 | -61.7294 | 61.3174 | 61.4227 | 61.3129 | 61.2717
764.3281 | 123.3032 | -61.3998 | 61.5646 | -0.060501 | -0.00014308 | 0.012298 | 0.042556 | -0.0028433 | -0.00096552 | -0.0016343 | -0.060791 | -0.002258 | 0.00511 | -0.0034756 | 0.02199 | 0.0057657 | 0.00028835 | -0.10071 | 0.13275 | -0.14191 | -0.082397 | 0.022888 | -0.091553 | -0.027466 | -0.086975 | 0.12817 | -0.10986 | 0.041199 | 0.10986 | 0.045776 | 0.12817 | 61.2579 | -61.4319 | -61.647 | 61.4227 | 61.3724 | 61.3083 | 0.11444 | 0.050354 | 61.29 | -61.4365 | -61.5234 | 61.5097 | 61.528 | 61.4456 | 0.23804 | 0.15564 | 0.16479 | 0.05951 | 0.21973 | 0.15106 | 0.27466 | 0.23804 | 61.5326 | 61.528 | -61.7065 | -61.6745 | 61.3174 | 61.441 | 61.2991 | 61.3129
765.3281 | 123.2574 | -61.5005 | 61.5921 | -0.07576 | 0.0039157 | 0.011444 | 0.041274 | 0.0016427 | 0.00095708 | 0.0011429 | -0.063843 | -0.00097617 | 0.0081006 | 0.0057102 | 0.020709 | 0.0036295 | -0.00035245 | -0.14191 | 0.13275 | -0.15564 | -0.16479 | -0.073242 | -0.16479 | -0.10529 | -0.23346 | 0.16937 | -0.12817 | -0.059509 | 0.1236 | -0.27924 | -0.027466 | 61.3449 | -61.4594 | -61.7569 | 61.4273 | 61.3953 | 61.3358 | 0.050354 | -0.009155 | 61.3724 | -61.4227 | -61.6516 | 61.6241 | 61.4731 | 61.2213 | 0.10071 | -0.15106 | 0.082398 | -0.009155 | 0.25177 | 0.068665 | 0.28839 | 0.29755 | 61.6333 | 61.6699 | -61.7477 | -61.7203 | 61.3358 | 61.441 | 61.3586 | 61.2671
766.3281 | 123.2803 | -61.4456 | 61.5875 | -0.029984 | 0.00028412 | 0.01358 | 0.039779 | 0.0035653 | -0.00096552 | 0.0030655 | -0.054688 | -0.0037534 | 0.0072462 | 0.0010104 | 0.023486 | 0.0057657 | 0.00028835 | -0.11444 | 0.11902 | -0.16022 | -0.10986 | -0.009155 | -0.13275 | -0.064087 | -0.14191 | 0.13733 | -0.13275 | 0 | 0.068665 | -0.022888 | 0.082397 | 61.2854 | -61.4685 | -61.6974 | 61.4365 | 61.3815 | 61.3129 | 0.09613 | 0.027466 | 61.3129 | -61.4502 | -61.5875 | 61.5143 | 61.528 | 61.4227 | 0.21515 | 0.10986 | 0.15106 | 0.050354 | 0.20142 | 0.13275 | 0.27924 | 0.27008 | 61.5646 | 61.5829 | -61.7477 | -61.7203 | 61.3358 | 61.4456 | 61.3312 | 61.3037
767.3438 | 123.2391 | -61.4136 | 61.5967 | -0.022354 | 7.0518e-05 | 0.012512 | 0.04277 | 0.0029245 | -0.0016065 | 0.00071573 | -0.057739 | -0.0016172 | 0.0048962 | -0.0096708 | 0.023486 | -0.0017111 | -0.0016343 | 0.036621 | 0.13275 | -0.11902 | -0.032043 | 0.054932 | -0.050354 | -0.009155 | -0.064087 | 0.1831 | -0.054932 | -0.009155 | 0.059509 | -0.032043 | 0.068665 | 61.2946 | -61.4639 | -61.6287 | 61.4685 | 61.4044 | 61.3632 | 0.10986 | 0.068665 | 61.3586 | -61.4136 | -61.6058 | 61.4731 | 61.4822 | 61.3815 | 0.1236 | 0.022889 | 0.17395 | 0.086976 | 0.11444 | 0.045777 | 0.25177 | 0.23804 | 61.5463 | 61.5967 | -61.7157 | -61.6516 | 61.3815 | 61.4044 | 61.4502 | 61.3495
768.3281 | 123.317 | -61.409 | 61.5784 | -0.07576 | 0.0013523 | 0.012085 | 0.041488 | 0.0016427 | -0.0011791 | -0.00013887 | -0.033325 | -0.0033262 | 0.006819 | 0.0050692 | 0.020709 | 0.0038431 | 0.0030655 | -0.091553 | 0.11902 | -0.14648 | -0.068665 | 0.041199 | -0.086975 | -0.022888 | -0.091553 | 0.12817 | -0.11444 | 0.050354 | 0.11444 | 0.027466 | 0.1236 | 61.2625 | -61.4594 | -61.647 | 61.4502 | 61.3861 | 61.322 | 0.1236 | 0.059509 | 61.2946 | -61.4502 | -61.528 | 61.5234 | 61.5326 | 61.4365 | 0.23804 | 0.14191 | 0.18768 | 0.077819 | 0.22888 | 0.16479 | 0.2655 | 0.24262 | 61.528 | 61.5372 | -61.7249 | -61.6928 | 61.3403 | 61.4594 | 61.3174 | 61.3174
769.3281 | 123.2208 | -61.4502 | 61.5784 | -0.06813 | 0.00071132 | 0.010803 | 0.042342 | 0.0020701 | -0.0033155 | -0.0018479 | -0.045532 | -0.0026852 | 0.0055372 | 0.0042148 | 0.021563 | 0.0036295 | -0.00077965 | -0.10071 | 0.14191 | -0.14648 | -0.14191 | -0.036621 | -0.13733 | -0.082397 | -0.18768 | 0.14648 | -0.14648 | -0.050354 | 0.027466 | -0.086975 | 0.054932 | 61.3037 | -61.4365 | -61.7203 | 61.4136 | 61.3678 | 61.3129 | 0.064087 | 0.009155 | 61.3037 | -61.4319 | -61.6287 | 61.4777 | 61.5051 | 61.3632 | 0.20142 | 0.059509 | 0.10986 | 0.004577 | 0.17395 | 0.09613 | 0.28839 | 0.29297 | 61.5921 | 61.5967 | -61.7249 | -61.7249 | 61.3083 | 61.3998 | 61.3495 | 61.2625
770.3281 | 123.3215 | -61.4456 | 61.5417 | -0.12917 | 0.0017795 | 0.01358 | 0.041061 | 0.00036107 | -0.0041699 | -0.0022751 | 0.015503 | -0.0026852 | 0.004469 | 0.0010104 | 0.022204 | 0.0027751 | 0.00050195 | -0.022888 | 0.086975 | -0.12817 | -0.013733 | 0.11444 | -0.032043 | 0.036621 | -0.032043 | 0.14191 | -0.082397 | 0.050354 | 0.12817 | 0.054932 | 0.13275 | 61.3174 | -61.4548 | -61.5555 | 61.5601 | 61.4822 | 61.4136 | 0.1648 | 0.096131 | 61.3632 | -61.3998 | -61.4914 | 61.5738 | 61.5784 | 61.5006 | 0.21515 | 0.13733 | 0.24262 | 0.11444 | 0.21057 | 0.13275 | 0.21515 | 0.2243 | 61.5326 | 61.5875 | -61.6699 | -61.6241 | 61.4319 | 61.496 | 61.4227 | 61.4136
771.3281 | 123.2574 | -61.4319 | 61.5921 | -0.091019 | 0.00071132 | 0.010589 | 0.043624 | 0.0018565 | -0.00075192 | -0.0024887 | -0.054688 | -0.0026852 | 0.0081006 | 0.0020786 | 0.022418 | 0.0036295 | 0.0011429 | -0.091553 | 0.13733 | -0.15106 | -0.11902 | -0.013733 | -0.11902 | -0.054932 | -0.15106 | 0.14191 | -0.11444 | 0 | 0.064087 | -0.041199 | 0.068665 | 61.2808 | -61.4548 | -61.7111 | 61.4182 | 61.377 | 61.3129 | 0.09613 | 0.032043 | 61.3174 | -61.4502 | -61.5921 | 61.496 | 61.5006 | 61.3907 | 0.18311 | 0.073242 | 0.13733 | 0.032043 | 0.17853 | 0.11444 | 0.28839 | 0.25635 | 61.5692 | 61.5738 | -61.7432 | -61.7065 | 61.3129 | 61.4319 | 61.3403 | 61.2808
772.3594 | 123.3307 | -61.4182 | 61.5509 | -0.1368 | 0.0013523 | 0.014221 | 0.039992 | 0.00078827 | 0.00052988 | -0.0018479 | 0.0032959 | -0.0016172 | 0.0087416 | -0.0024076 | 0.021136 | 0.0029887 | 0.0022109 | -0.022888 | 0.059509 | -0.11902 | -0.004578 | 0.10986 | -0.032043 | 0.027466 | -0.036621 | 0.11444 | -0.10529 | 0.050354 | 0.13733 | 0.036621 | 0.1236 | 61.2991 | -61.4914 | -61.5555 | 61.528 | 61.4456 | 61.3861 | 0.14649 | 0.086976 | 61.3129 | -61.4365 | -61.5005 | 61.5555 | 61.5417 | 61.4548 | 0.22888 | 0.14191 | 0.22888 | 0.11444 | 0.24262 | 0.15564 | 0.17853 | 0.21973 | 61.4777 | 61.5326 | -61.6699 | -61.6562 | 61.4136 | 61.4685 | 61.3953 | 61.3815
773.3281 | 123.2758 | -61.4273 | 61.5784 | -0.06813 | 0.0017795 | 0.013153 | 0.040206 | -6.6126e-05 | 0.00074348 | -0.00013887 | 0.14673 | -0.0016172 | 0.0057508 | -0.0017666 | 0.01964 | 0.0019205 | 0.0058425 | -0.045776 | 0.11444 | -0.10986 | -0.07782 | 0.027466 | -0.059509 | -0.013733 | -0.18768 | 0.086975 | -0.10986 | -0.013733 | 0.068665 | 0.013733 | 0.07782 | 61.3174 | -61.4639 | -61.6562 | 61.4548 | 61.4136 | 61.3678 | 0.09613 | 0.050354 | 61.3174 | -61.4914 | -61.5921 | 61.496 | 61.5051 | 61.441 | 0.18768 | 0.1236 | 0.13733 | 0.032043 | 0.17853 | 0.09613 | 0.2243 | 0.19684 | 61.5417 | 61.5143 | -61.6882 | -61.6882 | 61.3495 | 61.4136 | 61.3815 | 61.2396
774.3438 | 123.2666 | -61.4319 | 61.5921 | -0.037613 | 0.00092492 | 0.012939 | 0.039138 | -0.0024161 | -0.0013929 | -0.0046249 | 0.042969 | -0.0026852 | 0.0063916 | -0.0024076 | 0.021777 | 0.0012797 | -0.00056605 | -0.032043 | 0.12817 | -0.10529 | -0.32044 | -0.036621 | -0.22888 | -0.073242 | -0.15106 | 0.068665 | -0.086975 | -0.013733 | 0.086975 | 0.004578 | 0.07782 | 61.3266 | -61.4639 | -61.9125 | 61.3953 | 61.3586 | 61.203 | 0.032044 | -0.1236 | 61.3449 | -61.5234 | -61.6058 | 61.5189 | 61.5097 | 61.4365 | 0.16479 | 0.091553 | 0.068665 | -0.21515 | 0.17395 | 0.073242 | 0.23346 | 0.15564 | 61.5601 | 61.5006 | -61.6974 | -61.6791 | 61.1114 | 61.4182 | 61.3998 | 61.2808
775.3438 | 123.3353 | -61.409 | 61.5784 | -0.11391 | 0.0022067 | 0.012512 | 0.04277 | 0.00036107 | -0.00075192 | -0.0024887 | 0.00024405 | -0.002258 | 0.004469 | 0.001224 | 0.020922 | 0.0040567 | -0.0035569 | -0.004578 | 0.091553 | -0.13733 | -0.009155 | 0.10071 | -0.032043 | 0.032043 | -0.018311 | 0.14191 | -0.09613 | 0.045776 | 0.12817 | 0.041199 | 0.11902 | 61.2717 | -61.4868 | -61.5875 | 61.5097 | 61.441 | 61.377 | 0.16937 | 0.10529 | 61.3129 | -61.4365 | -61.5326 | 61.5372 | 61.528 | 61.4502 | 0.21515 | 0.13733 | 0.23804 | 0.12817 | 0.2243 | 0.14191 | 0.22888 | 0.23804 | 61.5005 | 61.5509 | -61.7157 | -61.6745 | 61.3998 | 61.4548 | 61.4044 | 61.3907
776.3281 | 123.3261 | -61.4182 | 61.5784 | -0.014725 | 0.00028412 | 0.012939 | 0.041488 | 0.0042063 | -0.0011791 | -0.0029159 | -0.011963 | -0.002899 | 0.0042554 | 0.0042148 | 0.022204 | 0.0038431 | -0.0018479 | -0.054932 | 0.054932 | -0.13275 | -0.004578 | 0.09613 | -0.032043 | 0.041199 | -0.022888 | 0.11902 | -0.10529 | 0.064087 | 0.14648 | 0.045776 | 0.12817 | 61.2854 | -61.5234 | -61.5829 | 61.5143 | 61.4594 | 61.3861 | 0.17395 | 0.10071 | 61.3129 | -61.4594 | -61.5143 | 61.5646 | 61.5463 | 61.4639 | 0.23346 | 0.15106 | 0.22888 | 0.12817 | 0.25177 | 0.16937 | 0.18768 | 0.22431 | 61.4731 | 61.5372 | -61.7111 | -61.6837 | 61.4136 | 61.4822 | 61.3632 | 61.3953
777.3438 | 123.1979 | -61.4777 | 61.5967 | -0.11391 | 0.0019931 | 0.01358 | 0.039352 | 0.0018565 | -0.00075192 | 0.00071573 | -0.091309 | -0.0026852 | 0.003401 | 0.0020786 | 0.021349 | 0.00021147 | -0.0044113 | -0.068665 | 0.13275 | -0.15106 | -0.11444 | -0.086975 | -0.17395 | -0.07782 | -0.23346 | 0.16022 | -0.13733 | -0.07782 | -0.032043 | -0.1236 | 0 | 61.3266 | -61.4639 | -61.7111 | 61.3907 | 61.3998 | 61.3037 | 0.073242 | -0.022888 | 61.3403 | -61.4365 | -61.6745 | 61.4456 | 61.4777 | 61.3541 | 0.13733 | 0.013733 | 0.064087 | 0.036621 | 0.10529 | 0.059509 | 0.28381 | 0.29755 | 61.6104 | 61.6379 | -61.7477 | -61.734 | 61.3632 | 61.3998 | 61.409 | 61.2442
778.3281 | 123.2986 | -61.4136 | 61.5646 | -0.07576 | -0.00057028 | 0.011871 | 0.042983 | 0.0029245 | -0.0031017 | -0.0039841 | -0.018066 | -0.0020444 | 0.0055372 | 0.001224 | 0.021777 | 0.0049113 | 0.00071555 | -0.045776 | 0.11902 | -0.14648 | -0.064087 | 0.045776 | -0.086975 | -0.013733 | -0.086975 | 0.13733 | -0.10529 | 0.050354 | 0.11444 | 0.027466 | 0.13275 | 61.2671 | -61.4456 | -61.6287 | 61.4593 | 61.3998 | 61.3266 | 0.13275 | 0.059509 | 61.3083 | -61.4273 | -61.5143 | 61.528 | 61.5463 | 61.441 | 0.23804 | 0.13275 | 0.19226 | 0.082397 | 0.21973 | 0.15564 | 0.2655 | 0.24262 | 61.5326 | 61.5509 | -61.7111 | -61.6699 | 61.3495 | 61.4639 | 61.3678 | 61.3266
779.3281 | 123.2483 | -61.4685 | 61.6058 | -0.091019 | -0.00035668 | 0.013794 | 0.040847 | 0.00078827 | -0.00032472 | -0.0029159 | -0.054688 | -0.0014036 | 0.004469 | 0.0020786 | 0.021777 | 0.0051249 | 0.0034927 | -0.086975 | 0.15564 | -0.15564 | -0.13733 | -0.036621 | -0.14648 | -0.068665 | -0.18768 | 0.15106 | -0.15564 | -0.032043 | 0.027466 | -0.07782 | 0.036621 | 61.3129 | -61.4502 | -61.7432 | 61.4319 | 61.3998 | 61.322 | 0.086975 | 0.009156 | 61.3129 | -61.4548 | -61.6379 | 61.496 | 61.5051 | 61.3907 | 0.19226 | 0.07782 | 0.11902 | 0.018311 | 0.18311 | 0.1236 | 0.31128 | 0.3067 | 61.6241 | 61.6196 | -61.7615 | -61.7615 | 61.3312 | 61.4365 | 61.3815 | 61.2808
780.3281 | 123.2162 | -61.4136 | 61.5875 | -0.06813 | 0.0011385 | 0.011871 | 0.04042 | -0.00027993 | -0.0020337 | -0.0022751 | 0.04602 | -0.0016172 | 0.0072462 | -0.0017666 | 0.021777 | 0.0025613 | 0.00028835 | -0.050354 | 0.12817 | -0.11902 | -0.068665 | 0.050354 | -0.054932 | 0.009155 | -0.1236 | 0.14191 | -0.10529 | 0 | -0.027466 | -0.082397 | 0.032043 | 61.2946 | -61.4594 | -61.6562 | 61.4639 | 61.4227 | 61.3586 | 0.12817 | 0.064087 | 61.3083 | -61.4456 | -61.5875 | 61.3861 | 61.4456 | 61.3312 | 0.13733 | 0.022889 | 0.16937 | 0.050354 | 0.07782 | 0.10529 | 0.24719 | 0.24719 | 61.5417 | 61.5555 | -61.7065 | -61.6928 | 61.3449 | 61.4136 | 61.3632 | 61.29
781.3281 | 123.3215 | -61.4136 | 61.5555 | -0.12154 | -0.00035668 | 0.012085 | 0.042983 | 0.0016427 | -0.00011112 | 0.00050193 | -0.030273 | -0.0014036 | 0.0046826 | 0.0020786 | 0.020495 | 0.0029887 | 0.0019973 | -0.004578 | 0.086975 | -0.12817 | -0.009155 | 0.082397 | -0.018311 | 0.022888 | -0.050354 | 0.1236 | -0.10071 | 0.073242 | 0.12817 | -0.25635 | -0.059509 | 61.2854 | -61.4685 | -61.5646 | 61.496 | 61.4365 | 61.3953 | 0.15106 | 0.10986 | 61.3129 | -61.4319 | -61.4822 | 61.5417 | 61.3541 | 61.1572 | 0.041199 | -0.15564 | 0.21057 | 0.11902 | 0.22888 | 0.17395 | 0.21515 | 0.2243 | 61.5005 | 61.5372 | -61.6837 | -61.6562 | 61.4044 | 61.4868 | 61.409 | 61.3632
782.3438 | 123.3032 | -61.4365 | 61.5738 | -0.06813 | 0.00071132 | 0.013366 | 0.039352 | -0.0032705 | -0.0011791 | -0.0035569 | -0.0089111 | -0.0035398 | 0.006819 | 0.00079682 | 0.021563 | 0.0032023 | 0.00050195 | -0.018311 | 0.09613 | -0.10529 | -0.027466 | 0.10529 | -0.022888 | 0.036621 | -0.054932 | 0.15106 | -0.10071 | 0.022888 | 0.10529 | 0.009155 | 0.091553 | 61.3312 | -61.4777 | -61.6013 | 61.5417 | 61.4731 | 61.4136 | 0.14191 | 0.082398 | 61.3358 | -61.4227 | -61.5509 | 61.5417 | 61.528 | 61.4456 | 0.19226 | 0.10986 | 0.21057 | 0.07782 | 0.20599 | 0.1236 | 0.20142 | 0.25177 | 61.5326 | 61.5875 | -61.6791 | -61.6745 | 61.409 | 61.4594 | 61.4182 | 61.3815
783.3281 | 123.262 | -61.4365 | 61.6013 | -0.07576 | 0.0032749 | 0.014007 | 0.041061 | 0.0035653 | 0.00031608 | -0.0022751 | -0.07605 | -0.0018308 | 0.0063916 | 0.0035738 | 0.021349 | 0.0042703 | 0.0011429 | -0.07782 | 0.12817 | -0.16479 | -0.10986 | -0.027466 | -0.13733 | -0.07782 | -0.16022 | 0.15564 | -0.14191 | -0.009155 | 0.041199 | -0.045776 | 0.050354 | 61.2717 | -61.4731 | -61.7111 | 61.409 | 61.3586 | 61.2991 | 0.086975 | 0.027466 | 61.2946 | -61.4456 | -61.6104 | 61.4777 | 61.4868 | 61.3907 | 0.19226 | 0.096131 | 0.13733 | 0.054932 | 0.18311 | 0.13275 | 0.29297 | 0.29755 | 61.5646 | 61.5921 | -61.7661 | -61.7432 | 61.3266 | 61.4273 | 61.3586 | 61.2762
784.3438 | 123.3078 | -61.4502 | 61.5784 | -0.14442 | 0.00092492 | 0.015075 | 0.041274 | -6.6126e-05 | -0.00096552 | -0.0012071 | -0.018066 | -0.0031126 | 0.0070326 | -5.7584e-05 | 0.021563 | 0.0042703 | 7.4746e-05 | 0.004578 | 0.10529 | -0.10529 | -0.009155 | 0.11444 | -0.036621 | 0.027466 | -0.041199 | 0.14191 | -0.091553 | 0.045776 | 0.11902 | 0.027466 | 0.09613 | 61.3449 | -61.4731 | -61.5875 | 61.5646 | 61.4777 | 61.4136 | 0.13275 | 0.068665 | 61.3586 | -61.4365 | -61.5326 | 61.5692 | 61.5463 | 61.4777 | 0.18768 | 0.11902 | 0.21973 | 0.096131 | 0.21057 | 0.13733 | 0.21057 | 0.23346 | 61.5555 | 61.5921 | -61.6837 | -61.6699 | 61.441 | 61.496 | 61.4548 | 61.409
785.3438 | 123.2071 | -61.4502 | 61.6287 | -0.052872 | 0.00049772 | 0.012298 | 0.044692 | -0.0034841 | -0.0016065 | -0.0027023 | -0.018066 | -0.0020444 | 0.0046826 | 0.004642 | 0.020922 | 0.0019205 | 0.0034927 | -0.082397 | 0.15564 | -0.15564 | -0.11902 | -0.018311 | -0.09613 | -0.045776 | -0.19684 | 0.16479 | -0.13275 | -0.041199 | 0.009155 | -0.059509 | 0.032043 | 61.2946 | -61.4731 | -61.7477 | 61.4319 | 61.4044 | 61.3541 | 0.10986 | 0.05951 | 61.3174 | -61.4639 | -61.6699 | 61.4594 | 61.4822 | 61.3907 | 0.16479 | 0.073242 | 0.13733 | 0.036621 | 0.14191 | 0.091552 | 0.31128 | 0.29755 | 61.6058 | 61.615 | -61.7844 | -61.7615 | 61.3312 | 61.409 | 61.3678 | 61.2534

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2 | Beneath Armor
-0.3083 | 22.3835 | 22.3719 | 22.5208 | 22.6583
0.6917 | 22.3821 | 22.3706 | 22.5266 | 22.656
1.6917 | 22.3783 | 22.3636 | 22.5256 | 22.6595
2.6917 | 22.437 | 22.3565 | 22.5147 | 22.659
3.6917 | 22.9409 | 22.3648 | 22.5201 | 22.6597
4.6917 | 24.2385 | 22.3532 | 22.5184 | 22.6575
5.6917 | 26.289 | 22.3686 | 22.5229 | 22.6549
6.6917 | 29.0209 | 22.3708 | 22.5252 | 22.6619
7.6917 | 32.2747 | 22.3617 | 22.5236 | 22.6608
8.6917 | 35.9432 | 22.3726 | 22.5336 | 22.6613
9.6917 | 39.9877 | 22.3839 | 22.5427 | 22.6541
10.6917 | 44.3094 | 22.3808 | 22.552 | 22.6634
11.7073 | 48.9305 | 22.3967 | 22.5664 | 22.6589
12.6917 | 53.5974 | 22.3979 | 22.5956 | 22.662
13.6917 | 58.5087 | 22.4157 | 22.6165 | 22.658
14.6917 | 63.5588 | 22.4453 | 22.6418 | 22.6634
15.6917 | 68.7296 | 22.446 | 22.6815 | 22.6582
16.6917 | 74.004 | 22.4755 | 22.7265 | 22.665
17.6917 | 79.4317 | 22.5081 | 22.7642 | 22.663
18.6917 | 84.8914 | 22.5476 | 22.8296 | 22.6614
19.6917 | 90.503 | 22.5723 | 22.8936 | 22.6598
20.6917 | 96.2248 | 22.6165 | 22.9678 | 22.667
21.6917 | 101.9884 | 22.6773 | 23.0417 | 22.6691
22.6917 | 107.8143 | 22.7258 | 23.1327 | 22.6688
23.6917 | 113.6287 | 22.7797 | 23.2384 | 22.6742
24.6917 | 119.5414 | 22.8368 | 23.3414 | 22.6771
25.6917 | 125.5211 | 22.9175 | 23.4601 | 22.6785
26.6917 | 131.4667 | 23.0077 | 23.5958 | 22.6807
27.6917 | 137.4633 | 23.0894 | 23.7387 | 22.6864
28.6917 | 143.4399 | 23.1801 | 23.8982 | 22.6834
29.6917 | 149.3507 | 23.2807 | 24.0657 | 22.6929
30.6917 | 155.3123 | 23.4122 | 24.2554 | 22.6969
31.6917 | 161.3021 | 23.5432 | 24.4447 | 22.7032
32.6917 | 167.2672 | 23.6668 | 24.6514 | 22.7038
33.6917 | 173.1771 | 23.8142 | 24.88 | 22.71
34.6917 | 179.1335 | 23.9732 | 25.1121 | 22.7139
35.6917 | 185.182 | 24.1403 | 25.3613 | 22.7136
36.6917 | 191.0443 | 24.3148 | 25.6303 | 22.7278
37.6917 | 196.8893 | 24.4846 | 25.9056 | 22.7347
38.6917 | 202.793 | 24.6891 | 26.2029 | 22.7455
39.6917 | 208.5275 | 24.9029 | 26.5169 | 22.7469
40.6917 | 214.4489 | 25.1147 | 26.8395 | 22.7639
41.6917 | 220.2146 | 25.3564 | 27.1822 | 22.7707
42.6917 | 226.1464 | 25.5923 | 27.5283 | 22.7902
43.6917 | 232.0758 | 25.8467 | 27.8985 | 22.8041
44.6917 | 237.7981 | 26.1187 | 28.2889 | 22.8048
45.6917 | 243.6494 | 26.3937 | 28.6949 | 22.8234
46.6917 | 249.4238 | 26.7027 | 29.1198 | 22.8269
47.6917 | 255.0933 | 27.0301 | 29.5669 | 22.8433
48.6917 | 260.8962 | 27.3387 | 30.0315 | 22.868
49.6917 | 266.6021 | 27.6747 | 30.5091 | 22.8849
50.6917 | 272.2351 | 28.0239 | 31.0139 | 22.9029
51.6917 | 277.7743 | 28.407 | 31.527 | 22.9206
52.6917 | 283.3438 | 28.7853 | 32.0729 | 22.9408
53.6917 | 288.9099 | 29.1922 | 32.6351 | 22.9557
54.6917 | 294.4446 | 29.6117 | 33.2118 | 22.9752
55.6917 | 300.1317 | 30.0605 | 33.8128 | 22.9946
56.6917 | 305.7531 | 30.516 | 34.4304 | 23.013
57.6917 | 311.2845 | 31.0016 | 35.0676 | 23.0513
58.6917 | 316.6432 | 31.4885 | 35.7249 | 23.0673
59.6917 | 321.8524 | 31.9936 | 36.4061 | 23.0953
60.6917 | 327.0773 | 32.5517 | 37.1188 | 23.1258
61.6917 | 332.4195 | 33.0999 | 37.8508 | 23.1553
62.6917 | 337.8284 | 33.6839 | 38.6028 | 23.1822
63.6917 | 343.1195 | 34.3161 | 39.3849 | 23.216
64.6917 | 348.4236 | 34.974 | 40.1878 | 23.2527
65.6917 | 353.8198 | 35.6891 | 41.017 | 23.2943
66.6917 | 358.8478 | 36.4366 | 41.8717 | 23.3274
67.6917 | 363.9779 | 37.2172 | 42.7389 | 23.3597
68.6917 | 369.0512 | 38.0355 | 43.6321 | 23.4031
69.6917 | 374.0756 | 38.8839 | 44.5448 | 23.4426
70.6917 | 379.2557 | 39.7601 | 45.4875 | 23.4908
71.6917 | 384.4336 | 40.6824 | 46.4616 | 23.5477
72.6917 | 389.3968 | 41.6613 | 47.4636 | 23.5822
73.6917 | 394.4964 | 42.6269 | 48.5032 | 23.636
74.6917 | 399.6145 | 43.6141 | 49.572 | 23.6891
75.6917 | 404.629 | 44.7441 | 50.675 | 23.7448
76.6917 | 409.5526 | 46.706 | 51.8341 | 23.7918
77.6917 | 414.4653 | 48.3018 | 53.0211 | 23.8499
78.6917 | 419.318 | 48.7799 | 54.2592 | 23.9055
79.6917 | 424.0099 | 50.0361 | 55.509 | 23.968
80.6917 | 428.6456 | 54.0384 | 56.7614 | 24.0287
81.6917 | 432.6922 | 55.7273 | 58.0938 | 24.0987
82.6917 | 436.3217 | 57.7371 | 59.4462 | 24.1763
83.6917 | 439.6135 | 59.842 | 60.8532 | 24.2459
84.6917 | 442.5606 | 61.6826 | 62.3182 | 24.3137
85.6917 | 445.4135 | 63.5147 | 63.786 | 24.3906
86.6917 | 448.2434 | 65.2199 | 65.3795 | 24.4791
87.6917 | 451.0419 | 67.0069 | 66.9408 | 24.5651
88.6917 | 453.8645 | 68.8134 | 68.4993 | 24.644
89.6917 | 456.404 | 70.6331 | 70.0974 | 24.7445
90.6917 | 458.6907 | 72.4516 | 71.7096 | 24.8243
91.6917 | 460.7103 | 74.3719 | 73.346 | 24.9177
92.6917 | 462.5411 | 76.4301 | 74.9875 | 25.0198
93.6917 | 464.402 | 78.4317 | 76.6548 | 25.1128
94.6917 | 465.9983 | 80.4392 | 78.3351 | 25.2224
95.6917 | 467.2369 | 82.479 | 80.0451 | 25.3288
96.6917 | 468.2959 | 84.5511 | 81.7551 | 25.4392
97.6917 | 469.1726 | 86.6149 | 83.4816 | 25.5552
98.6917 | 469.7981 | 88.6715 | 85.2158 | 25.6671
99.6917 | 470.3026 | 90.7444 | 86.9691 | 25.7867
100.6917 | 470.5488 | 92.7878 | 88.7379 | 25.9076
101.6917 | 470.7853 | 94.8236 | 90.5191 | 26.0407
102.6917 | 471.0466 | 96.8138 | 92.3068 | 26.1623
103.6917 | 470.9915 | 98.8253 | 94.0934 | 26.2989
104.6917 | 470.8725 | 100.8024 | 95.8929 | 26.4352
105.6917 | 470.6593 | 102.7633 | 97.6961 | 26.5724
106.6917 | 470.6803 | 104.7198 | 99.5147 | 26.715
107.6917 | 470.6053 | 106.6536 | 101.3148 | 26.8538
108.6917 | 470.6101 | 108.5913 | 103.1301 | 27.0138
109.6917 | 470.6295 | 110.5122 | 104.9198 | 27.1578
110.6917 | 470.5627 | 112.437 | 106.7144 | 27.3095
111.6917 | 470.5142 | 114.3451 | 108.5301 | 27.4656
112.6917 | 470.4603 | 116.2276 | 110.333 | 27.6328
113.6917 | 470.4061 | 118.1168 | 112.1494 | 27.7856
114.6917 | 470.467 | 119.9858 | 113.9682 | 27.9504
115.6917 | 470.5491 | 121.8234 | 115.7905 | 28.125
116.6917 | 470.7411 | 123.6395 | 117.6539 | 28.2928
117.6917 | 470.8272 | 125.4402 | 119.5015 | 28.4651
118.6917 | 470.9625 | 127.2131 | 121.35 | 28.6499
119.6917 | 471.0318 | 129.0091 | 123.1619 | 28.828
120.6917 | 471.1804 | 130.8063 | 124.9537 | 29.0108
121.6917 | 471.3012 | 132.6062 | 126.8281 | 29.1961
122.6917 | 471.3729 | 134.3967 | 128.7797 | 29.3918
123.6917 | 471.5017 | 136.1239 | 130.8707 | 29.5736
124.6917 | 471.5998 | 139.8523 | 133.2421 | 29.765
125.6917 | 471.9307 | 144.6116 | 135.7248 | 29.9617
126.6917 | 472.3007 | 150.0278 | 138.2694 | 30.1609
127.6917 | 472.5873 | 153.4707 | 140.7061 | 30.3596
128.6917 | 472.7831 | 156.5169 | 143.0931 | 30.5671
129.6917 | 472.9766 | 159.2044 | 145.6216 | 30.7633
130.6917 | 473.0355 | 162.1956 | 148.2921 | 30.9779
131.6917 | 473.1153 | 165.784 | 151.0447 | 31.1827
132.6917 | 473.1993 | 169.4026 | 153.9485 | 31.3916
133.6917 | 473.3618 | 172.4866 | 157.0217 | 31.5987
134.6917 | 473.4357 | 175.2741 | 160.1965 | 31.8117
135.6917 | 473.6262 | 178.5653 | 163.4024 | 32.0267
136.6917 | 473.8903 | 181.4101 | 166.5952 | 32.2434
137.6917 | 474.1572 | 183.3838 | 169.7377 | 32.4631
138.6917 | 474.0785 | 185.9731 | 172.8628 | 32.7037
139.6917 | 474.1741 | 188.6091 | 176.0683 | 32.9252
140.6917 | 474.3522 | 191.4757 | 179.3269 | 33.1531
141.6917 | 474.4456 | 193.9567 | 182.5432 | 33.3866
142.6917 | 474.5012 | 196.057 | 185.8387 | 33.6144
143.6917 | 474.6851 | 197.7182 | 189.0585 | 33.8387
144.6917 | 474.7717 | 199.9618 | 192.4624 | 34.0828
145.6917 | 474.7693 | 203.1984 | 196.024 | 34.3132
146.6917 | 474.6913 | 205.9002 | 199.679 | 34.5497
147.6917 | 474.7107 | 208.0216 | 203.0472 | 34.7953
148.6917 | 474.6163 | 210.1366 | 206.7268 | 35.0367
149.6917 | 474.5894 | 212.503 | 210.3939 | 35.2829
150.6917 | 474.6023 | 215.1114 | 214.1703 | 35.5248
151.6917 | 474.7647 | 217.3211 | 217.4866 | 35.7683
152.6917 | 474.7347 | 218.8517 | 220.4469 | 36.024
153.6917 | 474.7436 | 221.0518 | 224.304 | 36.2783
154.6917 | 474.9049 | 223.8505 | 226.7949 | 36.5306
155.6917 | 475.1351 | 226.4531 | 230.7988 | 36.7863
156.6917 | 475.227 | 228.0733 | 233.0679 | 37.0502
157.6917 | 475.257 | 230.5601 | 235.4362 | 37.3064
158.6917 | 475.392 | 233.4597 | 238.6803 | 37.5705
159.6917 | 475.4279 | 236.693 | 241.8304 | 37.8328
160.6917 | 475.4214 | 239.7453 | 245.0023 | 38.0883
161.6917 | 475.5056 | 243.0872 | 247.8725 | 38.3657
162.6917 | 475.6398 | 244.337 | 249.0608 | 38.6304
163.6917 | 475.7572 | 247.0143 | 251.5536 | 38.9082
164.6917 | 475.754 | 249.553 | 254.0951 | 39.183
165.6917 | 475.6988 | 251.4435 | 257.0328 | 39.4606
166.6917 | 475.7237 | 254.2177 | 259.2485 | 39.7376
167.6917 | 475.4854 | 257.0692 | 260.8731 | 40.0241
168.6917 | 475.632 | 259.6221 | 262.7025 | 40.3
169.6917 | 475.8593 | 261.2932 | 264.3428 | 40.5852
170.6917 | 475.9472 | 263.5079 | 266.5051 | 40.8795
171.6917 | 475.958 | 265.6572 | 268.4368 | 41.1608
172.6917 | 476.0675 | 267.2001 | 269.7847 | 41.454
173.6917 | 476.0212 | 269.7554 | 271.9734 | 41.7554
174.6917 | 475.986 | 272.0204 | 273.7269 | 42.0499
175.6917 | 476.0102 | 275.4166 | 276.3324 | 42.363
176.6917 | 476.0319 | 277.7889 | 278.8038 | 42.6795
177.6917 | 476.1221 | 279.6664 | 280.6654 | 42.9801
178.6917 | 476.0766 | 281.4567 | 281.9254 | 43.2841
179.6917 | 476.0097 | 283.8892 | 283.3001 | 43.6036
180.6917 | 475.8496 | 285.6792 | 285.7808 | 43.9155
181.6917 | 475.9422 | 285.947 | 286.7659 | 44.2383
182.6917 | 475.9868 | 286.8069 | 288.4726 | 44.5499
183.6917 | 475.9013 | 290.1742 | 291.3527 | 44.8744
184.6917 | 475.7746 | 291.6103 | 292.8473 | 45.1931
185.6917 | 475.7474 | 293.1508 | 294.5127 | 45.5224
186.6917 | 475.711 | 294.2607 | 295.7145 | 45.8428
187.6917 | 475.6073 | 296.6101 | 297.8272 | 46.1741
188.6917 | 475.5283 | 300.0721 | 301.6403 | 46.517
189.6917 | 475.502 | 302.1339 | 303.7629 | 46.8542
190.6917 | 475.4492 | 303.1643 | 305.6021 | 47.1977
191.6917 | 475.2418 | 304.157 | 306.5717 | 47.5384
192.6917 | 475.1055 | 305.3956 | 308.307 | 47.882
193.6917 | 475.1486 | 305.9686 | 309.523 | 48.2391
194.6917 | 475.0715 | 307.2581 | 311.346 | 48.5884
195.6917 | 474.9199 | 309.2773 | 312.9905 | 48.9467
196.6917 | 474.8981 | 311.2411 | 314.2355 | 49.3033
197.6917 | 474.8333 | 313.2033 | 315.2081 | 49.6666
198.6917 | 474.8055 | 314.99 | 317.001 | 50.031
199.6917 | 474.839 | 315.7694 | 317.948 | 50.4062
200.6917 | 474.8041 | 315.5971 | 318.6075 | 50.7773
201.6917 | 474.7637 | 316.675 | 320.0856 | 51.1533
202.6917 | 474.7318 | 318.0332 | 321.8265 | 51.5338
203.6917 | 474.8094 | 319.6457 | 323.576 | 51.9261
204.6917 | 474.7039 | 321.5248 | 324.2019 | 52.3203
205.6917 | 474.6593 | 323.0879 | 324.7964 | 52.7143
206.6917 | 474.5902 | 323.8669 | 325.7 | 53.1075
207.6917 | 474.571 | 324.1605 | 325.3898 | 53.5121
208.6917 | 474.6347 | 323.837 | 325.0913 | 53.9114
209.6917 | 474.6122 | 324.599 | 326.3 | 54.3253
210.6917 | 474.5853 | 325.7241 | 326.9586 | 54.7372
211.6917 | 474.687 | 326.2092 | 328.2169 | 55.1547
212.6917 | 474.8642 | 327.6911 | 329.893 | 55.584
213.6917 | 474.9482 | 327.4877 | 330.8192 | 56.0097
214.6917 | 475.0256 | 328.4777 | 330.6844 | 56.4393
215.6917 | 474.9654 | 328.8382 | 331.3729 | 56.8766
216.6917 | 475.0018 | 329.2401 | 331.8621 | 57.3188
217.6917 | 475.0426 | 329.4684 | 332.6106 | 57.7521
218.6917 | 475.03 | 330.5519 | 333.9059 | 58.1973
219.6917 | 475.0492 | 333.0575 | 336.0057 | 58.6427
220.6917 | 475.0022 | 334.4928 | 336.7652 | 59.089
221.6917 | 474.8465 | 335.3059 | 337.7826 | 59.5327
222.6917 | 474.7804 | 336.2122 | 340.2839 | 59.9849
223.6917 | 474.7721 | 337.171 | 341.2615 | 60.4351
224.6917 | 474.8244 | 337.7948 | 341.1023 | 60.8894
225.6917 | 474.8306 | 338.7908 | 342.1071 | 61.3582
226.6917 | 474.7841 | 339.9956 | 342.6058 | 61.8132
227.6917 | 474.7148 | 341.1861 | 343.4348 | 62.2654
228.6917 | 474.7182 | 342.8581 | 344.5103 | 62.7294
229.6917 | 474.6644 | 343.2446 | 344.7466 | 63.1858
230.6917 | 474.7307 | 343.9522 | 345.3591 | 63.6477
231.6917 | 474.837 | 344.3202 | 345.2136 | 64.1005
232.6917 | 474.8443 | 344.8807 | 345.8153 | 64.5623
233.6917 | 474.837 | 345.7432 | 347.5038 | 65.0273
234.6917 | 474.7598 | 346.8783 | 348.6761 | 65.4856
235.6917 | 474.6546 | 347.7535 | 348.637 | 65.9462
236.6917 | 474.5254 | 347.4513 | 348.8553 | 66.4043
237.6917 | 474.5719 | 348.5685 | 350.4514 | 66.8564
238.6917 | 474.6159 | 350.4675 | 351.5901 | 67.3163
239.6917 | 474.6501 | 351.0786 | 352.2485 | 67.7786
240.6917 | 474.6591 | 353.2006 | 353.9676 | 68.2396
241.6917 | 474.7163 | 355.0988 | 355.1434 | 68.6964
242.6917 | 474.8543 | 355.5109 | 353.9863 | 69.1565
243.6917 | 474.8422 | 356.6174 | 355.4702 | 69.6115
244.6917 | 474.8139 | 358.6353 | 355.8061 | 70.0663
245.6917 | 474.9126 | 359.03 | 356.0836 | 70.5354
246.6917 | 474.9139 | 360.0496 | 356.5372 | 70.9968
247.6917 | 474.9842 | 361.8047 | 357.6529 | 71.4441
248.6917 | 475.0388 | 363.1668 | 358.3665 | 71.9049
249.6917 | 475.0306 | 362.3956 | 358.086 | 72.3712
250.6917 | 475.0692 | 362.6747 | 358.8373 | 72.832
251.6917 | 475.0934 | 365.4983 | 359.1489 | 73.2963
252.6917 | 475.1821 | 366.9099 | 358.5141 | 73.751
253.6917 | 475.3769 | 366.4388 | 359.5749 | 74.2144
254.6917 | 475.3256 | 368.509 | 362.0742 | 74.6746
255.6917 | 475.2054 | 371.7025 | 363.2396 | 75.1453
256.6917 | 475.2638 | 371.9644 | 362.7985 | 75.6024
257.6917 | 475.2916 | 372.4032 | 361.7882 | 76.0674
258.6917 | 475.3022 | 372.9705 | 362.1821 | 76.5466
259.6917 | 475.3469 | 375.6985 | 363.089 | 77.008
260.6917 | 475.3599 | 374.9154 | 362.102 | 77.4751
261.6917 | 475.2653 | 375.7078 | 362.3562 | 77.9391
262.6917 | 475.2804 | 377.3633 | 363.4226 | 78.4054
263.6917 | 475.3526 | 376.4081 | 364.3065 | 78.8653
264.6917 | 475.3172 | 377.4875 | 365.6211 | 79.3223
265.6917 | 475.385 | 379.1134 | 365.049 | 79.781
266.6917 | 475.4893 | 381.9491 | 367.6158 | 80.2478
267.6917 | 475.4414 | 383.9044 | 368.6945 | 80.7005
268.6917 | 475.4455 | 385.1551 | 368.4144 | 81.1551
269.6917 | 475.4813 | 388.2528 | 367.647 | 81.6047
270.6917 | 475.3912 | 389.1086 | 365.6861 | 82.0505
271.6917 | 475.3009 | 389.0834 | 365.4054 | 82.5041
272.6917 | 475.1429 | 389.2532 | 365.7412 | 82.9465
273.6917 | 475.1266 | 388.8007 | 365.049 | 83.3979
274.6917 | 475.1268 | 387.9623 | 365.0011 | 83.8473
275.6917 | 475.1342 | 389.2283 | 364.7564 | 84.2905
276.6917 | 475.2538 | 390.0161 | 364.3879 | 84.7333
277.6917 | 475.294 | 388.9456 | 365.9425 | 85.1657
278.6917 | 475.2702 | 387.7735 | 366.3999 | 85.6016
279.6917 | 475.4824 | 420.8668 | 391.5016 | 86.0184
280.6917 | 476.376 | 446.0866 | 433.8857 | 86.4645
281.6917 | 477.2958 | 492.3731 | 473.794 | 86.8952
282.6917 | 478.0815 | 519.698 | 503.9606 | 87.3128
283.6917 | 478.7883 | 526.6986 | 525.4745 | 87.722
284.6917 | 479.4279 | 537.7741 | 553.4478 | 88.1279
285.6917 | 480.0461 | 554.0995 | 567.9324 | 88.5252
286.6917 | 480.7992 | 565.38 | 573.1644 | 88.9509
287.6917 | 481.461 | 569.5284 | 565.7077 | 89.3857
288.6917 | 481.2135 | 560.1491 | 555.1017 | 89.8445
289.6917 | 480.8863 | 551.8542 | 549.3029 | 90.2925
290.6917 | 481.0297 | 547.9914 | 551.7447 | 90.745
291.6917 | 480.8825 | 539.8515 | 548.0792 | 91.1719
292.6917 | 480.2894 | 529.7611 | 553.9571 | 91.5911
293.6917 | 479.6341 | 522.2886 | 548.106 | 92.0064
294.6917 | 478.9157 | 514.6269 | 542.4512 | 92.4087
295.6917 | 478.2439 | 508.818 | 538.8296 | 92.8082
296.6917 | 477.5401 | 503.4696 | 533.1661 | 93.2152
297.6917 | 476.7783 | 498.9266 | 528.8735 | 93.6333
298.6917 | 476.0271 | 494.352 | 524.2017 | 94.045
299.6917 | 475.2953 | 490.5416 | 522.4033 | 94.457
300.6917 | 474.6108 | 486.4046 | 518.3505 | 94.8697
301.6917 | 473.8807 | 483.2078 | 514.9006 | 95.2853
302.6917 | 473.1549 | 479.2413 | 510.2855 | 95.6959
303.6917 | 472.4088 | 476.4915 | 506.2814 | 96.0957
304.6917 | 471.7476 | 473.868 | 503.1509 | 96.524
305.6917 | 471.0035 | 471.7933 | 500.3595 | 96.9482
306.6917 | 470.3146 | 469.0968 | 496.5185 | 97.3904
307.6917 | 469.5152 | 467.0112 | 493.1243 | 97.826
308.6917 | 468.6946 | 464.7166 | 489.4109 | 98.261
309.6917 | 467.9074 | 462.5657 | 485.4425 | 98.6947
310.6917 | 467.2341 | 460.7325 | 481.9445 | 99.1525
311.6917 | 466.5391 | 459.3888 | 478.0286 | 99.5946
312.6917 | 465.9749 | 457.4528 | 474.2883 | 100.044
313.6917 | 465.4975 | 455.4279 | 470.2895 | 100.4902
314.6917 | 465.1291 | 454.0972 | 466.9079 | 100.9531
315.6917 | 464.7517 | 452.4452 | 463.497 | 101.4024
316.6917 | 464.4095 | 451.262 | 461.5948 | 101.8653
317.6917 | 464.2072 | 448.8576 | 458.3031 | 102.3387
318.6917 | 464.0479 | 447.5535 | 454.6452 | 102.8119
319.6917 | 463.9164 | 445.9228 | 451.5853 | 103.2895
320.6917 | 463.7557 | 445.5777 | 448.4652 | 103.7897
321.6917 | 463.6853 | 445.1552 | 445.3832 | 104.2761
322.6917 | 463.7796 | 443.0907 | 442.3886 | 104.7697
323.6917 | 463.9074 | 440.0681 | 439.2642 | 105.2434
324.6917 | 464.0803 | 438.1895 | 436.826 | 105.724
325.6917 | 464.2952 | 436.9714 | 434.8331 | 106.1945
326.6917 | 464.475 | 436.7618 | 432.8105 | 106.6704
327.6917 | 464.6658 | 435.7986 | 431.0007 | 107.1347
328.6917 | 465.0028 | 436.1292 | 428.7495 | 107.5995
329.6917 | 465.1782 | 434.1462 | 427.9188 | 108.0601
330.6917 | 465.3435 | 432.3449 | 426.0336 | 108.5347
331.6917 | 465.5475 | 430.2207 | 424.2537 | 108.997
332.6917 | 465.641 | 428.2288 | 422.3144 | 109.4604
333.6917 | 465.7832 | 426.4089 | 420.8014 | 109.9184
334.6917 | 465.982 | 425.2681 | 419.3895 | 110.3904
335.6917 | 466.1795 | 424.3521 | 418.4924 | 110.8758
336.6917 | 466.3368 | 423.2883 | 416.5164 | 111.3579
337.6917 | 466.4811 | 422.3757 | 416.289 | 111.8653
338.6917 | 466.5284 | 423.6448 | 415.247 | 112.3709
339.6917 | 466.5932 | 424.6865 | 414.6997 | 112.8798
340.6917 | 466.8278 | 432.8748 | 427.7716 | 113.3346
341.6917 | 468.0808 | 454.2907 | 439.8042 | 113.8279
342.6917 | 469.2699 | 465.9549 | 442.2621 | 114.3573
343.6917 | 469.629 | 473.1046 | 446.8034 | 114.9981
344.6917 | 469.7773 | 486.8389 | 452.876 | 115.7626
345.6917 | 469.9456 | 513.6561 | 460.5922 | 116.607
346.6917 | 470.1316 | 527.7981 | 469.5816 | 117.5852
347.6917 | 470.2576 | 546.7442 | 479.6371 | 118.6063
348.6917 | 470.5473 | 567.8454 | 491.2179 | 119.7133
349.6917 | 470.8237 | 589.6189 | 500.9623 | 120.8912
350.6917 | 471.0116 | 607.1081 | 510.124 | 121.7579
351.6917 | 471.0239 | 621.7929 | 519.9853 | 122.5731
352.6917 | 470.9001 | 641.1552 | 531.4897 | 123.575
353.6917 | 471.0576 | 652.5504 | 540.7678 | 124.5188
354.6917 | 471.3838 | 654.2591 | 548.2733 | 125.4287
355.6917 | 471.236 | 658.7524 | 554.8387 | 126.6179
356.6917 | 470.9587 | 677.5232 | 560.8005 | 127.6469
357.6917 | 470.4657 | 685.321 | 565.7216 | 128.592
358.6917 | 470.0525 | 688.2283 | 571.8243 | 129.8726
359.6917 | 469.5219 | 672.5804 | 574.8669 | 131.0368
360.6917 | 469.1093 | 668.5827 | 577.454 | 132.2027
361.6917 | 468.7443 | 660.5616 | 580.4554 | 133.4922
362.6917 | 468.5214 | 647.4477 | 581.0825 | 134.6114
363.6917 | 468.0769 | 656.3282 | 583.6684 | 136.0358
364.6917 | 467.5975 | 644.7401 | 583.9973 | 137.8252
365.6917 | 467.1035 | 641.4846 | 583.6738 | 139.8142
366.6917 | 466.6296 | 634.7273 | 584.5741 | 142.3816
367.6917 | 466.0975 | 625.8794 | 584.0056 | 144.5466
368.6917 | 465.5664 | 620.9249 | 583.4311 | 146.4995
369.6917 | 464.9324 | 611.5883 | 582.2185 | 149.5001
370.6917 | 464.4286 | 603.8052 | 579.9526 | 151.6506
371.6917 | 463.9417 | 606.4902 | 578.5399 | 154.4225
372.6917 | 463.4542 | 599.8185 | 576.1171 | 157.2441
373.6917 | 462.9069 | 593.1731 | 572.3788 | 160.1689
374.6917 | 462.495 | 585.5928 | 569.4702 | 162.6108
375.6917 | 462.0962 | 582.8887 | 566.8689 | 164.8568
376.6917 | 461.682 | 582.106 | 566.1134 | 165.9632
377.6917 | 461.3672 | 582.1789 | 563.9502 | 169.8054
378.6917 | 460.9992 | 581.8629 | 560.7219 | 173.168
379.6917 | 460.6401 | 583.0993 | 558.4979 | 175.9997
380.6917 | 460.3701 | 579.3855 | 555.2547 | 178.8095
381.6917 | 460.1387 | 574.3158 | 551.5636 | 182.1741
382.6917 | 460.0265 | 567.2572 | 549.4989 | 185.1257
383.6917 | 459.8942 | 561.7378 | 546.7268 | 188.079
384.6917 | 459.8887 | 559.0916 | 543.5856 | 191.778
385.6917 | 459.7329 | 553.3905 | 540.2106 | 195.6767
386.6917 | 459.5631 | 545.4905 | 534.8141 | 197.7837
387.6917 | 459.5046 | 545.0783 | 533.5511 | 200.0383
388.6917 | 459.4228 | 543.0114 | 530.7456 | 201.8208
389.6917 | 459.4204 | 538.1551 | 527.8229 | 204.0463
390.6917 | 459.4815 | 535.2308 | 523.796 | 205.6
391.6917 | 459.5191 | 532.527 | 520.6834 | 208.208
392.6917 | 459.5381 | 534.9483 | 518.4769 | 211.3054
393.6917 | 459.6176 | 532.6911 | 517.4548 | 212.1233
394.6917 | 459.7134 | 534.1619 | 515.3922 | 214.1222
395.6917 | 459.8394 | 536.3373 | 516.8164 | 215.8149
396.6917 | 459.9659 | 531.2407 | 512.5889 | 217.8411
397.6917 | 460.048 | 526.3067 | 508.7151 | 219.6964
398.6917 | 460.2027 | 523.8473 | 505.9613 | 222.1239
399.6917 | 460.2939 | 519.5724 | 502.8157 | 224.7712
400.6917 | 460.4347 | 516.3515 | 499.4685 | 227.0908
401.6917 | 460.6121 | 513.4829 | 498.5752 | 229.6156
402.6917 | 460.6797 | 510.7762 | 495.3978 | 232.3866
403.6917 | 460.7525 | 511.8758 | 494.5804 | 234.7839
404.6917 | 460.8508 | 513.7279 | 494.7977 | 237.2823
405.6917 | 460.9548 | 513.9967 | 492.897 | 239.4953
406.6917 | 461.0884 | 513.7466 | 490.0838 | 242.8161
407.6917 | 461.1773 | 514.3833 | 487.0933 | 245.9813
408.6917 | 461.3479 | 511.6986 | 486.0267 | 249.1976
409.6917 | 461.5056 | 514.2453 | 486.4337 | 251.0009
410.6917 | 461.6177 | 511.8069 | 484.7604 | 253.397
411.6917 | 461.7922 | 511.8982 | 482.8362 | 253.8252
412.6917 | 462.0765 | 512.7229 | 482.4574 | 255.4579
413.6917 | 462.2857 | 513.0494 | 480.4695 | 254.63
414.6917 | 462.3196 | 513.6009 | 479.1786 | 254.0208
415.6917 | 462.4708 | 513.8054 | 477.7268 | 252.0739
416.6917 | 462.552 | 512.7294 | 476.0825 | 252.9052
417.6917 | 462.6897 | 512.4049 | 472.9865 | 254.4339
418.6917 | 462.9493 | 510.0819 | 470.6077 | 254.7541
419.6917 | 463.08 | 507.8227 | 467.9155 | 254.0408
420.6917 | 463.1845 | 504.6237 | 467.3766 | 253.6292
421.6917 | 463.2925 | 504.3463 | 464.5553 | 255.4689
422.6917 | 463.4369 | 502.9264 | 462.8647 | 256.1598
423.6917 | 463.4745 | 500.557 | 460.4192 | 255.781
424.6917 | 463.3818 | 500.8404 | 459.086 | 257.5508
425.6917 | 463.4083 | 498.5414 | 456.4369 | 257.4959
426.6917 | 463.4365 | 499.2549 | 455.9413 | 258.5532
427.6917 | 463.4476 | 499.6521 | 454.2239 | 259.4766
428.6917 | 463.4218 | 499.7067 | 451.5721 | 259.8954
429.6917 | 463.5072 | 497.898 | 448.5459 | 260.6409
430.6917 | 463.5816 | 498.8817 | 448.2513 | 262.0697
431.6917 | 463.59 | 498.2838 | 448.5195 | 263.0636
432.6917 | 463.7198 | 498.2968 | 448.8171 | 264.087
433.6917 | 463.7973 | 496.3133 | 446.5458 | 264.8754
434.6917 | 463.8828 | 493.715 | 443.6112 | 265.2765
435.6917 | 463.8363 | 494.1651 | 444.8753 | 265.8721
436.6917 | 463.9235 | 493.5447 | 443.541 | 266.5762
437.6917 | 463.991 | 490.9776 | 442.1572 | 267.3163
438.6917 | 464.1408 | 488.7766 | 440.7905 | 267.3773
439.6917 | 464.1853 | 489.0153 | 441.1119 | 268.4995
440.6917 | 464.2525 | 486.8661 | 439.8606 | 268.4281
441.6917 | 464.3498 | 486.136 | 439.1567 | 268.7863
442.6917 | 464.3914 | 484.032 | 438.9508 | 268.8253
443.6917 | 464.3679 | 483.2578 | 438.6792 | 268.6447
444.6917 | 464.2881 | 482.0525 | 437.806 | 268.611
445.6917 | 464.3562 | 480.5069 | 437.5186 | 268.5743
446.6917 | 464.4185 | 480.4907 | 436.1997 | 268.6324
447.6917 | 464.4063 | 476.3376 | 434.4435 | 268.4353
448.6917 | 464.4253 | 477.3923 | 433.5646 | 268.1905
449.6917 | 464.5256 | 477.8855 | 433.4145 | 267.9381
450.6917 | 464.4936 | 477.2148 | 432.9993 | 267.9189
451.6917 | 464.4459 | 478.0707 | 432.4752 | 267.8322
452.6917 | 464.4347 | 478.2452 | 432.3918 | 267.7547
453.6917 | 464.4832 | 478.2638 | 430.8627 | 267.6243
454.6917 | 464.372 | 477.7162 | 429.3664 | 267.3426
455.6917 | 464.382 | 473.1964 | 427.1319 | 266.8547
456.6917 | 464.3306 | 473.3579 | 428.2206 | 266.8282
457.6917 | 464.2748 | 473.0019 | 429.3205 | 266.8366
458.6917 | 464.2728 | 472.4206 | 427.5237 | 267.4208
459.6917 | 464.2516 | 472.7143 | 428.271 | 267.7333
460.6917 | 464.1534 | 473.2053 | 428.7627 | 268.07
461.6917 | 464.1788 | 471.979 | 428.8596 | 268.2742
462.6917 | 464.1742 | 471.0842 | 428.6162 | 268.8199
463.6917 | 464.2472 | 470.7158 | 430.0323 | 268.9397
464.6917 | 464.2349 | 469.1705 | 428.1856 | 269.4541
465.6917 | 464.1962 | 469.8919 | 427.7484 | 269.9102
466.6917 | 464.3285 | 469.1472 | 428.1735 | 270.2292
467.6917 | 464.3669 | 467.3113 | 425.2259 | 270.5718
468.6917 | 464.3754 | 465.0033 | 424.8656 | 271.0563
469.6917 | 464.3373 | 464.3247 | 423.5741 | 271.5013
470.6917 | 464.2952 | 462.6492 | 421.9584 | 271.8888
471.6917 | 464.2391 | 463.0476 | 421.5014 | 272.3755
472.6917 | 464.1668 | 462.1099 | 419.8483 | 272.8129
473.6917 | 464.2333 | 462.0878 | 418.715 | 273.8764
474.6917 | 464.329 | 460.256 | 418.5813 | 274.3208
475.6917 | 464.3329 | 459.5769 | 417.6646 | 274.8703
476.6917 | 464.4278 | 459.0285 | 418.6542 | 275.3323
477.6917 | 464.4737 | 459.38 | 417.6228 | 276.0001
478.6917 | 464.5877 | 459.782 | 416.9675 | 276.6431
479.6917 | 464.5829 | 459.5554 | 417.6972 | 277.1806
480.6917 | 464.615 | 460.0951 | 417.4894 | 277.7174
481.6917 | 464.5425 | 459.6025 | 416.5203 | 278.3061
482.6917 | 464.5084 | 459.6472 | 416.5809 | 278.8994
483.6917 | 464.4523 | 459.0117 | 414.6806 | 279.3312
484.6917 | 464.4042 | 459.8651 | 414.9945 | 279.7498
485.6917 | 464.3211 | 459.6526 | 415.6148 | 280.2725
486.6917 | 464.3903 | 458.1706 | 414.5936 | 280.7082
487.6917 | 464.4614 | 457.8157 | 415.4431 | 281.0864
488.6917 | 464.5348 | 457.6768 | 417.1731 | 281.5952
489.6917 | 464.5598 | 456.0482 | 416.5673 | 282.0897
490.6917 | 464.4757 | 456.0014 | 417.1327 | 282.5769
491.6917 | 464.4005 | 455.7326 | 415.9245 | 282.991
492.6917 | 464.374 | 455.8469 | 417.9394 | 283.5026
493.6917 | 464.39 | 454.1435 | 417.4174 | 283.8
494.6917 | 464.271 | 453.5971 | 416.9212 | 284.2199
495.6917 | 464.2103 | 453.208 | 416.4784 | 284.9586
496.6917 | 464.2075 | 452.1033 | 416.3218 | 285.04
497.6917 | 464.19 | 451.5098 | 414.5657 | 285.1256
498.6917 | 464.2709 | 448.6337 | 413.8768 | 285.257
499.6917 | 464.2813 | 447.5597 | 413.5851 | 285.3055
500.6917 | 464.3306 | 445.5828 | 413.5099 | 285.208
501.6917 | 464.3193 | 443.923 | 412.4726 | 285.0576
502.6917 | 464.2363 | 443.6106 | 413.7846 | 284.9381
503.6917 | 464.1728 | 445.0645 | 413.784 | 284.8317
504.6917 | 464.1539 | 444.2243 | 413.0725 | 284.7255
505.6917 | 464.0864 | 444.2747 | 413.5344 | 284.7226
506.6917 | 464.1581 | 444.5174 | 412.8524 | 284.8719
507.6917 | 464.2449 | 443.1488 | 411.8917 | 285.1548
508.6917 | 464.3268 | 444.1007 | 412.3501 | 285.5868
509.6917 | 464.3878 | 443.5468 | 411.3347 | 286.2019
510.6917 | 464.5534 | 441.9989 | 410.8581 | 286.8566
511.6917 | 464.5757 | 441.2871 | 411.5445 | 287.5521
512.6917 | 464.6011 | 440.4482 | 410.7122 | 288.2761
513.6917 | 464.6269 | 441.127 | 410.4981 | 288.8093
514.6917 | 464.7328 | 438.677 | 408.5035 | 289.5442
515.6917 | 464.7579 | 439.8178 | 409.0419 | 290.3821
516.6917 | 464.7452 | 438.422 | 407.8301 | 291.1762
517.6917 | 464.8025 | 439.7217 | 409.082 | 292.042
518.6917 | 464.8265 | 439.6839 | 408.8901 | 292.8545
519.6917 | 464.8094 | 438.9162 | 407.8262 | 293.6273
520.6917 | 464.811 | 438.0963 | 408.2385 | 294.4693
521.6917 | 464.9214 | 438.4841 | 408.0867 | 295.2697
522.6917 | 465.0506 | 437.3756 | 408.95 | 296.0398
523.6917 | 465.0937 | 436.85 | 407.837 | 296.8046
524.6917 | 465.214 | 436.0278 | 407.6946 | 297.4881
525.6917 | 465.2521 | 437.6022 | 407.9755 | 298.1185
526.6917 | 465.1784 | 438.2777 | 408.7263 | 298.721
527.6917 | 465.2245 | 438.9195 | 409.2953 | 299.4002
528.6917 | 465.233 | 437.5791 | 409.0267 | 300.0759
529.6917 | 465.2991 | 436.5874 | 407.3241 | 300.2809
530.6917 | 465.3665 | 437.6405 | 407.6156 | 300.7986
531.6917 | 465.3996 | 437.1452 | 406.8234 | 301.4355
532.6917 | 465.4528 | 437.4459 | 406.07 | 302.0485
533.6917 | 465.5012 | 436.8449 | 405.4403 | 302.7242
534.6917 | 465.4676 | 435.2598 | 404.7778 | 303.3291
535.6917 | 465.496 | 436.1753 | 405.4475 | 303.8872
536.6917 | 465.4494 | 435.9523 | 404.5423 | 304.4632
537.6917 | 465.5098 | 438.0059 | 405.9836 | 305.068
538.6917 | 465.6544 | 438.6941 | 405.755 | 305.6942
539.6917 | 465.7408 | 438.8067 | 406.242 | 306.329
540.6917 | 465.696 | 439.2037 | 405.521 | 307.0047
541.6917 | 465.6562 | 439.3799 | 406.7828 | 307.7106
542.6917 | 465.589 | 439.5553 | 406.683 | 308.388
543.6917 | 465.5945 | 439.5011 | 408.1209 | 309.0368
544.6917 | 465.7204 | 441.9155 | 408.8241 | 309.7718
545.6917 | 465.898 | 442.223 | 408.2198 | 310.4999
546.6917 | 465.844 | 442.336 | 407.9692 | 311.1653
547.6917 | 465.7579 | 443.2201 | 411.0407 | 311.8233
548.6917 | 465.7519 | 443.8793 | 410.0398 | 312.4799
549.6917 | 465.6721 | 444.1362 | 409.558 | 313.1861
550.6917 | 465.6394 | 444.5618 | 409.4584 | 313.9312
551.6917 | 465.6428 | 442.9324 | 409.1724 | 314.6775
552.6917 | 465.6834 | 440.9781 | 408.7551 | 315.3726
553.6917 | 465.596 | 441.458 | 409.3339 | 316.1162
554.6917 | 465.6158 | 442.168 | 408.8318 | 316.8212
555.6917 | 465.5897 | 443.1777 | 409.5414 | 317.5244
556.6917 | 465.492 | 443.7646 | 409.5498 | 318.2256
557.6917 | 465.4747 | 444.4218 | 411.8571 | 318.9535
558.6917 | 465.3801 | 442.7038 | 409.8167 | 319.6097
559.6917 | 465.4106 | 441.8248 | 408.121 | 320.3891
560.6917 | 465.3947 | 441.7952 | 407.4449 | 321.1766
561.6917 | 465.2901 | 442.2106 | 406.392 | 321.945
562.6917 | 465.1908 | 443.4858 | 407.2176 | 322.6554
563.6917 | 465.1266 | 445.8344 | 408.8133 | 323.3553
564.6917 | 464.9605 | 444.8172 | 408.2504 | 323.9345
565.6917 | 464.8543 | 443.7489 | 407.6002 | 324.6178
566.6917 | 464.8567 | 444.6201 | 407.9928 | 325.3015
567.6917 | 464.9566 | 444.3384 | 407.166 | 325.8101
568.6917 | 464.985 | 442.9037 | 405.8121 | 326.4811
569.6917 | 464.825 | 443.0467 | 405.9603 | 327.792
570.6917 | 464.8522 | 442.343 | 403.9341 | 328.9102
571.6917 | 464.866 | 442.949 | 405.6167 | 330.0693
572.6917 | 464.7861 | 441.7664 | 404.5926 | 331.0118
573.6917 | 464.8599 | 441.8727 | 404.0131 | 331.8221
574.6917 | 464.9853 | 441.6401 | 404.1823 | 332.5437
575.6917 | 465.0103 | 440.5748 | 404.4219 | 333.2369
576.6917 | 465.0169 | 438.4714 | 403.7278 | 333.9048
577.6917 | 465.1342 | 437.9937 | 404.0828 | 334.5766
578.6917 | 465.1585 | 439.2572 | 404.8727 | 335.2672
579.6917 | 465.1237 | 437.8874 | 403.8256 | 335.8837
580.6917 | 465.1722 | 434.7735 | 403.6458 | 336.4978
581.6917 | 465.1397 | 434.2808 | 403.8793 | 337.0516
582.6917 | 465.0972 | 431.2839 | 401.8178 | 337.559
583.6917 | 465.1969 | 430.6472 | 401.6855 | 338.1474
584.6917 | 465.2961 | 428.6312 | 400.3185 | 338.6125
585.6917 | 465.3938 | 427.8074 | 399.889 | 339.0808
586.6917 | 465.4591 | 427.9663 | 399.2546 | 339.5047
587.6917 | 465.5404 | 426.0478 | 398.342 | 339.9992
588.6917 | 465.4939 | 425.6265 | 399.237 | 340.4199
589.6917 | 465.4601 | 426.2562 | 398.0979 | 340.802
590.6917 | 465.5401 | 426.2987 | 398.5547 | 341.3139
591.6917 | 465.5896 | 427.4325 | 399.4106 | 341.8566
592.6917 | 465.6994 | 427.7439 | 398.9047 | 342.4798
593.6917 | 465.7006 | 425.9429 | 399.4853 | 343.1307
594.6917 | 465.6909 | 426.1203 | 398.8671 | 343.761
595.6917 | 465.6803 | 426.0207 | 400.4438 | 344.4246
596.6917 | 465.6772 | 425.7237 | 399.4928 | 345.0504
597.6917 | 465.7663 | 425.9167 | 399.424 | 345.7006
598.6917 | 465.9107 | 425.6728 | 400.5569 | 346.3177
599.6917 | 465.9517 | 424.5768 | 399.0419 | 346.9005
600.6917 | 465.9289 | 424.1434 | 398.9701 | 347.4827
601.6917 | 466.013 | 424.2064 | 397.4419 | 348.0893
602.6917 | 465.8914 | 423.3803 | 397.3554 | 348.6387
603.6917 | 465.9488 | 423.0501 | 397.4744 | 349.1912
604.6917 | 465.9688 | 421.1512 | 397.6945 | 349.733
605.6917 | 465.8005 | 421.4097 | 397.4254 | 350.3667
606.6917 | 465.6024 | 421.8233 | 397.3666 | 350.9697
607.6917 | 465.5978 | 421.9618 | 397.6869 | 351.4982
608.6917 | 465.6286 | 421.3842 | 398.314 | 351.9656
609.6917 | 465.6368 | 419.9787 | 397.588 | 352.6644
610.6917 | 465.7606 | 419.2152 | 395.7282 | 353.2323
611.6917 | 465.7714 | 419.1434 | 397.2306 | 353.785
612.6917 | 465.861 | 418.872 | 397.2311 | 354.2145
613.6917 | 465.8388 | 417.6646 | 396.059 | 354.729
614.6917 | 465.8169 | 416.7954 | 396.5801 | 355.2149
615.6917 | 465.7404 | 417.0121 | 397.9116 | 355.639
616.6917 | 465.713 | 418.1872 | 399.2185 | 356.0957
617.6917 | 465.7545 | 416.6519 | 398.0093 | 356.7436
618.6917 | 465.8651 | 417.2761 | 399.1787 | 357.2484
619.6917 | 466.0299 | 415.4397 | 398.3088 | 357.7695
620.6917 | 466.0457 | 415.9814 | 397.5068 | 358.1032
621.6917 | 466.1335 | 415.984 | 398.2882 | 358.449
622.6917 | 466.1157 | 416.6191 | 397.5435 | 358.9976
623.6917 | 466.1004 | 415.47 | 395.6545 | 359.651
624.6917 | 466.1563 | 416.3402 | 393.3618 | 360.3417
625.6917 | 466.1259 | 415.5267 | 390.667 | 361.1284
626.6917 | 466.1441 | 417.1117 | 388.6142 | 361.207
627.6917 | 466.0155 | 417.0758 | 387.6136 | 361.4317
628.6917 | 466.025 | 418.0326 | 385.2693 | 361.7561
629.6917 | 466.0682 | 418.4608 | 382.874 | 362.1009
630.6917 | 466.0348 | 418.9105 | 382.2971 | 362.6996
631.6917 | 466.093 | 416.528 | 381.5525 | 363.3088
632.6917 | 466.1037 | 417.0448 | 381.7804 | 363.9142
633.6917 | 466.1303 | 417.5957 | 381.2345 | 364.5024
634.6917 | 466.0852 | 418.0599 | 383.113 | 364.7828
635.6917 | 466.0593 | 417.1758 | 383.5955 | 364.9987
636.6917 | 466.0503 | 417.0367 | 384.422 | 365.2018
637.6917 | 466.0612 | 417.5238 | 383.8908 | 365.6755
638.6917 | 466.1726 | 417.3149 | 385.9105 | 365.6005
639.6917 | 466.1825 | 417.2484 | 386.198 | 365.7946
640.6917 | 466.2687 | 417.8997 | 386.2608 | 366.0454
641.6917 | 466.3115 | 416.7828 | 386.6591 | 366.0465
642.6917 | 466.3554 | 416.0785 | 386.3064 | 366.0514
643.6917 | 466.2934 | 417.5877 | 386.8882 | 366.272
644.6917 | 466.3393 | 417.3309 | 386.7721 | 366.0495
645.6917 | 466.3502 | 416.2825 | 386.5377 | 367.0343
646.6917 | 466.333 | 416.9454 | 387.2675 | 367.3374
647.6917 | 466.375 | 416.9449 | 387.1677 | 367.5656
648.6917 | 466.3913 | 417.492 | 387.561 | 367.7522
649.6917 | 466.4961 | 417.81 | 387.8734 | 367.9949
650.6917 | 466.5442 | 417.8248 | 387.3026 | 366.9041
651.6917 | 466.489 | 417.4156 | 387.6138 | 367.1129
652.6917 | 466.4226 | 418.1532 | 389.486 | 367.0819
653.6917 | 466.5394 | 419.044 | 387.7429 | 368.2809
654.6917 | 466.5428 | 419.846 | 387.8451 | 369.1193
655.6917 | 466.5951 | 419.7426 | 387.5157 | 369.6729
656.6917 | 466.72 | 420.7829 | 387.4702 | 369.8578
657.6917 | 466.8553 | 421.8165 | 386.4579 | 370.394
658.6917 | 466.86 | 423.0032 | 388.8321 | 370.6269
659.6917 | 466.9155 | 424.1242 | 388.1418 | 370.5346
660.6917 | 466.985 | 424.5408 | 389.9326 | 370.8999
661.6917 | 467.0388 | 425.9111 | 391.4092 | 370.988
662.6917 | 467.0548 | 426.807 | 391.8541 | 371.6856
663.6917 | 467.04 | 426.9096 | 391.809 | 371.8408
664.6917 | 467.0267 | 427.6258 | 390.2365 | 370.8381
665.6917 | 467.0065 | 428.1038 | 390.948 | 380.1351
666.6917 | 466.9432 | 428.1014 | 391.9515 | 381.3558
667.6917 | 466.9032 | 428.8487 | 391.7567 | 371.4864
668.6917 | 466.8499 | 428.8883 | 392.453 | 370.7451
669.6917 | 466.9423 | 429.329 | 391.9644 | 372.1063
670.6917 | 467.1329 | 429.1273 | 392.2644 | 371.8168
671.6917 | 467.1631 | 428.2679 | 394.3962 | 374.1218
672.6917 | 466.9128 | 428.4494 | 392.9159 | 374.1349
673.6917 | 466.7521 | 427.6767 | 394.4377 | 376.0639
674.6917 | 466.7258 | 427.8083 | 393.3614 | 378.474
675.6917 | 466.7955 | 427.5062 | 392.6675 | 380.3892
676.6917 | 466.8179 | 427.0383 | 391.4019 | 381.3269
677.6917 | 466.8636 | 427.103 | 391.0486 | 382.8292
678.6917 | 466.8325 | 426.2793 | 390.6426 | 383.4026
679.6917 | 466.8304 | 426.4114 | 389.1886 | 384.4695
680.6917 | 466.7729 | 426.1544 | 389.5209 | 384.2147
681.6917 | 466.72 | 425.6057 | 389.2053 | 384.0728
682.6917 | 466.5502 | 425.1404 | 389.0253 | 384.1598
683.6917 | 466.4883 | 425.2264 | 387.7649 | 384.2305
684.6917 | 466.6184 | 424.9114 | 386.6622 | 384.2598
685.6917 | 466.5695 | 424.8815 | 386.0641 | 385.273
686.6917 | 466.4492 | 425.2618 | 385.6686 | 385.8985
687.6917 | 466.467 | 425.2669 | 384.376 | 386.7424
688.6917 | 466.5197 | 425.2462 | 383.8134 | 387.1452
689.6917 | 466.5703 | 426.0967 | 383.8569 | 387.8737
690.6917 | 466.664 | 426.7811 | 383.5569 | 388.0297
691.6917 | 466.6984 | 426.3165 | 383.9469 | 388.7145
692.6917 | 466.6479 | 426.6952 | 384.4113 | 391.4015
693.6917 | 466.5426 | 425.9968 | 384.9344 | 390.6903
694.6917 | 466.4301 | 425.2452 | 385.6505 | 390.6133
695.6917 | 466.309 | 425.327 | 386.7194 | 390.9276
696.6917 | 466.3738 | 425.2807 | 386.7546 | 394.0617
697.6917 | 466.4861 | 422.5235 | 385.514 | 394.9835
698.6917 | 466.4912 | 418.7691 | 385.8179 | 395.7584
699.6917 | 466.5199 | 415.2659 | 386.1974 | 395.3256
700.6917 | 466.6257 | 415.3134 | 386.6553 | 395.1161
701.6917 | 466.7108 | 414.0383 | 388.1419 | 395.928
702.6917 | 466.7632 | 415.3721 | 388.6973 | 396.5534
703.6917 | 466.7787 | 417.444 | 389.8644 | 396.9478
704.6917 | 466.8043 | 417.6162 | 391.1702 | 397.5479
705.6917 | 466.7394 | 417.6433 | 392.0032 | 398.3496
706.6917 | 466.7314 | 418.0378 | 392.1234 | 398.5915
707.6917 | 466.879 | 417.7729 | 393.9376 | 398.065
708.6917 | 466.958 | 415.6131 | 394.4684 | 398.5789
709.6917 | 466.9764 | 411.9254 | 394.5897 | 398.7106
710.6917 | 467.0513 | 408.1313 | 396.0009 | 398.5257
711.6917 | 467.1834 | 405.3579 | 396.6886 | 399.4936
712.6917 | 467.1237 | 402.4181 | 397.6188 | 397.8292
713.6917 | 467.0126 | 399.5337 | 398.4496 | 397.9997
714.6917 | 467.0287 | 398.2073 | 398.3541 | 398.0696
715.6917 | 467.0228 | 395.8412 | 398.9766 | 398.5923
716.6917 | 467.0635 | 394.0694 | 397.7992 | 399.1503
717.6917 | 466.947 | 393.3963 | 398.2473 | 399.9197
718.6917 | 466.9324 | 391.7171 | 399.163 | 400.1151
719.6917 | 467.0429 | 391.335 | 398.6247 | 399.7699
720.6917 | 467.0504 | 390.686 | 396.8882 | 399.8427
721.6917 | 467.0284 | 389.0674 | 396.6993 | 400.1272
722.6917 | 467.0497 | 388.4432 | 398.3089 | 400.4367
723.6917 | 466.954 | 388.281 | 399.2776 | 400.6309
724.6917 | 466.9427 | 388.1259 | 397.764 | 400.8469
725.6917 | 466.9909 | 387.5585 | 396.0429 | 400.8781
726.6917 | 466.9168 | 387.5729 | 395.6154 | 400.809
727.6917 | 466.8646 | 388.7618 | 396.745 | 400.7909
728.6917 | 466.9002 | 389.2581 | 396.1642 | 401.0054
729.6917 | 466.9081 | 390.3386 | 397.4191 | 399.2438
730.6917 | 466.9808 | 391.6452 | 396.8031 | 399.1845
731.6917 | 467.0299 | 391.8469 | 398.6281 | 399.6507
732.6917 | 466.9409 | 393.086 | 398.1261 | 399.9275
733.6917 | 466.9853 | 392.8804 | 397.8322 | 400.8977
734.6917 | 467.0197 | 392.8525 | 397.9397 | 400.2415
735.6917 | 466.9964 | 394.6872 | 399.0524 | 400.4556
736.6917 | 466.9472 | 396.6029 | 398.3995 | 400.4978
737.6917 | 467.0078 | 397.8557 | 400.5546 | 400.7825
738.6917 | 467.0447 | 397.8892 | 399.4921 | 400.832
739.6917 | 467.0138 | 398.4322 | 399.2686 | 400.5168
740.6917 | 466.9457 | 398.9485 | 397.881 | 400.3614
741.6917 | 466.8835 | 399.8654 | 396.5926 | 400.3068
742.6917 | 466.8371 | 401.2565 | 396.6237 | 400.758
743.6917 | 466.6877 | 403.9114 | 397.9185 | 400.0904
744.6917 | 466.6466 | 401.5499 | 397.5787 | 400.3516
745.6917 | 466.6078 | 400.4692 | 396.3604 | 400.4888
746.6917 | 466.5788 | 399.9315 | 394.5852 | 403.586
747.6917 | 466.5645 | 401.4937 | 395.4442 | 403.5474
748.6917 | 466.6279 | 403.4462 | 395.5887 | 403.8403
749.6917 | 466.6683 | 404.2729 | 394.2547 | 404.0597
750.6917 | 466.7562 | 404.9347 | 396.6356 | 403.8771
751.6917 | 466.6245 | 406.9862 | 396.6649 | 404.2993
752.6917 | 466.4252 | 405.9631 | 396.7742 | 404.4455
753.6917 | 466.3109 | 404.7741 | 395.7686 | 404.6698
754.6917 | 466.1371 | 405.5831 | 394.6351 | 404.8694
755.6917 | 466.1225 | 404.6089 | 394.3404 | 404.9313
756.6917 | 466.2263 | 402.8407 | 394.0552 | 405.1897
757.6917 | 466.3139 | 402.3029 | 393.6341 | 405.2272
758.6917 | 466.3886 | 401.774 | 393.9756 | 405.2865
759.6917 | 466.3921 | 401.8919 | 392.3113 | 405.0691
760.6917 | 466.3691 | 402.0229 | 392.9887 | 405.1327
761.6917 | 466.2893 | 403.3017 | 391.3025 | 405.1342
762.6917 | 466.2975 | 403.0513 | 392.4186 | 405.2176
763.6917 | 466.3636 | 404.8204 | 394.5288 | 405.4337
764.6917 | 466.4088 | 405.1662 | 395.503 | 405.22
765.6917 | 466.5389 | 404.9535 | 392.9646 | 405.3085
766.6917 | 466.6241 | 406.7272 | 393.6521 | 405.401
767.6917 | 466.6745 | 407.2126 | 391.5421 | 405.5357
768.6917 | 466.7574 | 407.0437 | 390.8131 | 404.8512
769.6917 | 466.8184 | 409.0617 | 392.7429 | 407.1718
770.6917 | 466.8586 | 409.8724 | 392.251 | 407.848
771.6917 | 466.8931 | 408.6497 | 391.6575 | 408.4035
772.6917 | 466.9426 | 409.0836 | 393.5239 | 408.7192
773.6917 | 467.0086 | 409.6941 | 395.4972 | 408.6429
774.6917 | 467.034 | 410.9244 | 396.0018 | 408.6117
775.6917 | 467.0081 | 411.602 | 396.2174 | 408.7902
776.6917 | 467.0465 | 413.3279 | 397.3059 | 408.737
777.6917 | 467.079 | 414.6706 | 398.2242 | 408.9893
778.6917 | 467.1193 | 414.1902 | 397.6679 | 408.7127
779.6917 | 467.1469 | 413.2681 | 396.5486 | 408.8954
780.6917 | 467.1526 | 412.7173 | 397.4949 | 408.8715
781.6917 | 467.1488 | 413.7881 | 396.7148 | 409.1574
782.6917 | 467.2284 | 415.1241 | 397.0843 | 409.2456
783.6917 | 467.2302 | 417.1823 | 397.5462 | 409.2497
784.6917 | 467.2606 | 418.4805 | 395.9032 | 409.1661
785.6917 | 467.2186 | 419.3911 | 396.573 | 409.4707