## Test Conditions
DESIREE-FIRE Test Number 24 - Circuit Simulator Data Only
Test Date: | 2009-07-29
DCSim DAQ Start Time | 9:11
DCSim Time for Synchronization | 9:11
Heat Source Synchronization | 0:00 | minutes:seconds
Heat Source DAQ Start Time | 9:11
Heat Source Start Time | 9:24
DCSim Offset | 0:13 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 796 | seconds
Heat Source Offset | 0:13 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 772 | seconds
Heat Source Stop Time | 10:06
Test Duration | 0:42 | minutes:seconds
| 2504 | seconds
CT500 Turns | 2 |  | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 Turns | 5
Pre-Test Baseline: | Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SWGR Close | EPR/CPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
SWGR Trip | EPR/CPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SWGR_CT500 | SWGR-a_CT35_1_PC | SWGR-a_CT35_2_N1 | SWGR-b_CT35_1_PT | SWGR-b_CT35_2_G | SWGR-b_CT35_3_R | SWGR-b_CT35_4_N2 | SWGR-a_VT7_1_C1 | SWGR-a_VTU_1_PC | SWGR-a_VTU_2_N1 | SWGR-b_VT7_1_G | SWGR-b_VT7_2_R | SWGR-b_VT7_3_T | SWGR-b_VT7_4_SP | SWGR-b_VT7_5_SP | SWGR-b_VTU_1_PT | SWGR-b_VTU_2_N2 | {SWGR-C} V(N1) - V(Batt -) | {SWGR-C} V(PC) - V(Batt +) | {SWGR-C} V(C1) - V(Batt +) | {SWGR-T} V(G) - V(Batt -) | {SWGR-T} V(R) - V(Batt +) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-T} V(PT) - V(Batt +) | {SWGR-C} V(C1) - V(N1) | {SWGR-T} V(SP1) - V(Batt -) | {SWGR-T} V(SP2) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PC) - V(Batt -) | {SWGR-T} V(C1) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-C} V(PC) - V(Batt -) | {SWGR-C} V(C1) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-C} V(N1) - V(Batt +) | {SWGR-T} V(N2) - V(Batt +)
-0.67188 | 123.0515 | -60.9009 | 61.9629 | 0.23239 | 0.02136 | 0.015729 | 0.0027472 | 0.066734 | -0.0017111 | 0.069677 | -61.0382 | 61.8668 | -60.8826 | -61.1481 | 61.7294 | -0.013733 | 0.041199 | -0.10986 | 61.8484 | -61.0382 | 0.018311 | -0.096131 | -0.13733 | -0.24719 | -0.23346 | -0.13733 | -0.11444 | -0.15564 | 60.9421 | 60.791 | 122.6303 | 122.7676 | -0.13733 | 122.7493 | 60.8871 | -0.13733 | 122.7676 | -0.13733 | 60.8871 | 122.6303 | 122.7493 | -122.8455 | -123.0011
0.32812 | 123.0011 | -60.8917 | 61.9904 | 0.17899 | 0.022215 | 0.015088 | 0.003388 | 0.069297 | -0.00064309 | 0.070318 | -61.0428 | 61.8668 | -60.8917 | -61.1298 | 61.7249 | -0.018311 | 0.032043 | -0.11444 | 61.8347 | -61.0245 | 0 | -0.1236 | -0.15106 | -0.23804 | -0.2655 | -0.13275 | -0.15564 | -0.15106 | 60.9238 | 60.7773 | 122.6166 | 122.7585 | -0.15106 | 122.7264 | 60.8734 | -0.13275 | 122.7585 | -0.15106 | 60.8734 | 122.6166 | 122.7264 | -122.8821 | -123.0148
1.3281 | 123.0331 | -60.91 | 61.9858 | 0.2095 | 0.020719 | 0.020215 | 0.00232 | 0.066734 | -0.0021383 | 0.070105 | -61.0519 | 61.8713 | -60.8688 | -61.1435 | 61.734 | -0.004578 | 0.041199 | -0.10529 | 61.8164 | -61.0382 | 0.041199 | -0.11444 | -0.14191 | -0.23346 | -0.25177 | -0.12817 | -0.16937 | -0.18311 | 60.9512 | 60.8047 | 122.644 | 122.7814 | -0.14191 | 122.7264 | 60.9055 | -0.12817 | 122.7814 | -0.14191 | 60.9055 | 122.644 | 122.7264 | -122.8546 | -123.024
2.3281 | 123.0377 | -60.9146 | 61.972 | 0.17136 | 0.019224 | 0.020429 | 0.0025336 | 0.065025 | 0.00021151 | 0.070532 | -61.0474 | 61.9034 | -60.8917 | -61.1389 | 61.7249 | -0.004578 | 0.050354 | -0.09613 | 61.8118 | -61.0519 | 0.022888 | -0.068665 | -0.13275 | -0.2243 | -0.24719 | -0.13733 | -0.16022 | -0.15564 | 60.965 | 60.8185 | 122.6395 | 122.818 | -0.13275 | 122.7264 | 60.91 | -0.13733 | 122.818 | -0.13275 | 60.91 | 122.6395 | 122.7264 | -122.8638 | -123.024
3.3281 | 123.0286 | -60.8826 | 61.972 | 0.056915 | 0.021574 | 0.020642 | 0.0018928 | 0.069938 | -0.0012839 | 0.071814 | -60.9879 | 61.8851 | -60.8826 | -61.0931 | 61.7661 | 0.022888 | 0.045776 | -0.018311 | 61.8439 | -61.0245 | 0 | -0.086975 | -0.10529 | -0.21057 | -0.20599 | -0.14191 | -0.12817 | -0.10529 | 60.9283 | 60.8643 | 122.6486 | 122.7676 | -0.10529 | 122.7264 | 60.9055 | -0.14191 | 122.7676 | -0.10529 | 60.9055 | 122.6486 | 122.7264 | -122.8546 | -122.9965
4.3281 | 123.0423 | -60.9192 | 61.972 | 0.14847 | 0.022428 | 0.019361 | 0.0048834 | 0.06652 | -0.0010703 | 0.072027 | -61.0336 | 61.8713 | -60.8871 | -61.1435 | 61.7203 | -0.022888 | 0.064087 | -0.11444 | 61.8439 | -61.0153 | 0.032043 | -0.10071 | -0.11444 | -0.2243 | -0.25177 | -0.096131 | -0.12817 | -0.14648 | 60.9833 | 60.8047 | 122.6395 | 122.7905 | -0.11444 | 122.7631 | 60.8963 | -0.096131 | 122.7905 | -0.11444 | 60.8963 | 122.6395 | 122.7631 | -122.8592 | -122.9874
5.3281 | 123.0011 | -60.91 | 61.9766 | 0.079804 | 0.020506 | 0.018506 | 0.0025336 | 0.069297 | -0.0014975 | 0.070105 | -61.0199 | 61.8988 | -60.8871 | -61.1343 | 61.7477 | -0.013733 | 0.07782 | -0.091553 | 61.8439 | -61.0565 | 0.022888 | -0.07782 | -0.10986 | -0.2243 | -0.22888 | -0.14648 | -0.13275 | -0.13275 | 60.9879 | 60.8185 | 122.6578 | 122.8088 | -0.10986 | 122.7539 | 60.8963 | -0.14648 | 122.8088 | -0.10986 | 60.8963 | 122.6578 | 122.7539 | -122.8638 | -123.0331
6.3281 | 123.056 | -60.9146 | 61.9766 | 0.1561 | 0.022428 | 0.018079 | 0.003388 | 0.06652 | -0.00064309 | 0.072455 | -61.0336 | 61.8942 | -60.8734 | -61.171 | 61.734 | -0.027466 | 0.050354 | -0.11444 | 61.8484 | -61.0199 | 0.041199 | -0.082398 | -0.11902 | -0.25635 | -0.24262 | -0.10529 | -0.12817 | -0.16022 | 60.965 | 60.8002 | 122.6486 | 122.8088 | -0.11902 | 122.7631 | 60.8871 | -0.10529 | 122.8088 | -0.11902 | 60.8871 | 122.6486 | 122.7631 | -122.85 | -122.9965
7.3281 | 123.0148 | -60.8963 | 61.9629 | 0.064545 | 0.020719 | 0.01637 | 0.0027472 | 0.066734 | -0.0025657 | 0.070105 | -60.9924 | 61.908 | -60.8551 | -61.116 | 61.7294 | 0.018311 | 0.050354 | -0.059509 | 61.8576 | -61.0199 | 0.041198 | -0.054932 | -0.096131 | -0.21973 | -0.23346 | -0.1236 | -0.10529 | -0.13733 | 60.9467 | 60.8368 | 122.6257 | 122.8043 | -0.096131 | 122.7539 | 60.9146 | -0.1236 | 122.8043 | -0.096131 | 60.9146 | 122.6257 | 122.7539 | -122.818 | -122.9828
8.3281 | 123.0011 | -60.8963 | 61.9675 | 0.10269 | 0.022001 | 0.016584 | 0.0018928 | 0.066947 | -0.0027793 | 0.070105 | -61.0336 | 61.8805 | -60.8688 | -61.1481 | 61.734 | -0.041199 | 0.059509 | -0.09613 | 61.8576 | -61.0199 | 0.027466 | -0.086975 | -0.13733 | -0.25177 | -0.23346 | -0.1236 | -0.10986 | -0.1648 | 60.9558 | 60.8002 | 122.6303 | 122.7768 | -0.13733 | 122.7539 | 60.8551 | -0.1236 | 122.7768 | -0.13733 | 60.8551 | 122.6303 | 122.7539 | -122.8363 | -122.9874
9.3281 | 123.0331 | -60.8917 | 61.9858 | 0.056915 | 0.022215 | 0.020002 | 0.00232 | 0.067161 | -0.0017111 | 0.070532 | -60.9833 | 61.8805 | -60.8597 | -61.0748 | 61.7752 | 0.050354 | 0.054932 | -0.022888 | 61.8393 | -61.0336 | 0.032044 | -0.10529 | -0.091552 | -0.1831 | -0.21057 | -0.14191 | -0.14648 | -0.1236 | 60.9467 | 60.8688 | 122.6669 | 122.7722 | -0.091552 | 122.731 | 60.9421 | -0.14191 | 122.7722 | -0.091552 | 60.9421 | 122.6669 | 122.731 | -122.8455 | -123.0194
10.3281 | 123.0652 | -60.8826 | 61.972 | -0.019379 | 0.022215 | 0.017224 | 0.0029608 | 0.06652 | -0.0017111 | 0.070532 | -60.9787 | 61.8942 | -60.8643 | -61.0611 | 61.8027 | 0.064087 | 0.054932 | 0.004578 | 61.8576 | -61.0474 | 0.01831 | -0.07782 | -0.096131 | -0.17853 | -0.16937 | -0.16479 | -0.11444 | -0.11444 | 60.9375 | 60.8871 | 122.6852 | 122.7768 | -0.096131 | 122.7402 | 60.9467 | -0.16479 | 122.7768 | -0.096131 | 60.9467 | 122.6852 | 122.7402 | -122.8363 | -123.0194
11.3281 | 123.056 | -60.9009 | 61.9629 | 0.056915 | 0.021574 | 0.020002 | 0.00232 | 0.067375 | -0.0027793 | 0.071814 | -61.0016 | 61.8805 | -60.8734 | -61.0931 | 61.7661 | 0.022888 | 0.082397 | -0.041199 | 61.8484 | -61.0336 | 0.027466 | -0.082398 | -0.10071 | -0.19226 | -0.19684 | -0.13275 | -0.11444 | -0.12817 | 60.9833 | 60.8597 | 122.6669 | 122.7814 | -0.10071 | 122.7493 | 60.9238 | -0.13275 | 122.7814 | -0.10071 | 60.9238 | 122.6669 | 122.7493 | -122.8363 | -122.9965
12.3281 | 123.0469 | -60.9055 | 61.9766 | 0.041657 | 0.022001 | 0.017438 | 0.0038154 | 0.069084 | -0.0017111 | 0.070318 | -60.9787 | 61.8942 | -60.878 | -61.0886 | 61.7706 | 0.050354 | 0.045776 | -0.013733 | 61.8256 | -60.9924 | 0.027466 | -0.082398 | -0.073242 | -0.18311 | -0.20599 | -0.086975 | -0.15106 | -0.10071 | 60.9512 | 60.8917 | 122.6761 | 122.7997 | -0.073242 | 122.731 | 60.9558 | -0.086975 | 122.7997 | -0.073242 | 60.9558 | 122.6761 | 122.731 | -122.8546 | -122.9691
13.3281 | 123.0331 | -60.8963 | 61.9629 | 0.25528 | 0.022001 | 0.014875 | 0.0029608 | 0.067588 | -0.0023519 | 0.070532 | -60.9695 | 61.8851 | -60.8688 | -61.1252 | 61.7615 | 0.013733 | 0.068665 | -0.050354 | 61.8851 | -61.0199 | 0.027466 | -0.07782 | -0.073242 | -0.22888 | -0.20142 | -0.1236 | -0.07782 | -0.10071 | 60.965 | 60.8459 | 122.6578 | 122.7814 | -0.073242 | 122.7814 | 60.91 | -0.1236 | 122.7814 | -0.073242 | 60.91 | 122.6578 | 122.7814 | -122.8317 | -122.9828
14.3281 | 123.056 | -60.9192 | 61.9629 | -0.019379 | 0.022856 | 0.017438 | 0.00232 | 0.067588 | -0.0023519 | 0.070746 | -60.997 | 61.8668 | -60.8826 | -61.1023 | 61.7798 | 0.041199 | 0.064087 | -0.004578 | 61.8301 | -61.0428 | 0.036621 | -0.096131 | -0.07782 | -0.18311 | -0.18311 | -0.1236 | -0.13275 | -0.11444 | 60.9833 | 60.9146 | 122.699 | 122.7859 | -0.07782 | 122.7493 | 60.9604 | -0.1236 | 122.7859 | -0.07782 | 60.9604 | 122.699 | 122.7493 | -122.8455 | -123.0057
15.3281 | 123.0423 | -60.9009 | 61.9766 | 0.011139 | 0.019438 | 0.017224 | 0.004029 | 0.066947 | -0.0029929 | 0.070532 | -60.965 | 61.8622 | -60.8917 | -61.0977 | 61.7935 | 0.032043 | 0.064087 | -0.032043 | 61.853 | -61.0062 | 0.009155 | -0.11444 | -0.064087 | -0.19684 | -0.18311 | -0.10529 | -0.1236 | -0.073242 | 60.965 | 60.8688 | 122.6944 | 122.7631 | -0.064087 | 122.7539 | 60.9329 | -0.10529 | 122.7631 | -0.064087 | 60.9329 | 122.6944 | 122.7539 | -122.8683 | -122.9828
16.3281 | 123.0789 | -60.8826 | 61.9583 | -0.049896 | 0.019651 | 0.021283 | 0.0012518 | 0.066947 | -0.0012839 | 0.069891 | -60.9558 | 61.908 | -60.8505 | -61.0519 | 61.8164 | 0.10986 | 0.07782 | 0.064087 | 61.8576 | -61.0199 | 0.032043 | -0.050354 | -0.073243 | -0.16937 | -0.14191 | -0.13733 | -0.10071 | -0.10529 | 60.9604 | 60.9467 | 122.699 | 122.7905 | -0.073243 | 122.7402 | 60.9924 | -0.13733 | 122.7905 | -0.073243 | 60.9924 | 122.699 | 122.7402 | -122.8088 | -122.9782
17.3281 | 123.0927 | -60.8826 | 61.9812 | -0.11093 | 0.020506 | 0.015088 | 0.0018928 | 0.068656 | -0.0012839 | 0.070105 | -60.9558 | 61.8988 | -60.8688 | -61.0565 | 61.8164 | 0.10071 | 0.086975 | 0.050354 | 61.8713 | -61.0062 | 0.013733 | -0.082397 | -0.073243 | -0.17395 | -0.16479 | -0.1236 | -0.10986 | -0.086976 | 60.9695 | 60.9329 | 122.699 | 122.7814 | -0.073243 | 122.7539 | 60.9833 | -0.1236 | 122.7814 | -0.073243 | 60.9833 | 122.699 | 122.7539 | -122.85 | -122.9874
18.3281 | 123.0515 | -60.8734 | 61.9675 | -0.027008 | 0.020933 | 0.018506 | 0.00061099 | 0.067588 | -0.0025657 | 0.070746 | -60.9558 | 61.8713 | -60.8597 | -61.0519 | 61.8164 | 0.091553 | 0.041199 | 0.045776 | 61.8713 | -61.0107 | 0.013733 | -0.09613 | -0.082398 | -0.17853 | -0.15106 | -0.13733 | -0.09613 | -0.096131 | 60.9146 | 60.9192 | 122.6898 | 122.7448 | -0.082398 | 122.7448 | 60.965 | -0.13733 | 122.7448 | -0.082398 | 60.965 | 122.6898 | 122.7448 | -122.8271 | -122.9782
19.3281 | 123.0743 | -60.878 | 61.9766 | -0.057526 | 0.02136 | 0.019361 | 0.0014654 | 0.068015 | -2.092e-06 | 0.069464 | -60.965 | 61.8805 | -60.8597 | -61.0474 | 61.8073 | 0.10529 | 0.064087 | 0.054932 | 61.8576 | -61.0107 | 0.018311 | -0.096131 | -0.086975 | -0.16937 | -0.16937 | -0.13275 | -0.11902 | -0.10529 | 60.9421 | 60.9329 | 122.6852 | 122.7585 | -0.086975 | 122.7356 | 60.9833 | -0.13275 | 122.7585 | -0.086975 | 60.9833 | 122.6852 | 122.7356 | -122.8363 | -122.9874
20.3281 | 123.0469 | -60.8917 | 61.9675 | -0.019379 | 0.019438 | 0.017224 | 0.00039739 | 0.068656 | -0.0012839 | 0.070746 | -60.9512 | 61.8896 | -60.8734 | -61.0657 | 61.7889 | 0.068665 | 0.036621 | 0.004578 | 61.8668 | -61.0016 | 0.018311 | -0.07782 | -0.059509 | -0.17395 | -0.17853 | -0.10986 | -0.10071 | -0.07782 | 60.9283 | 60.8963 | 122.6807 | 122.7814 | -0.059509 | 122.7585 | 60.9604 | -0.10986 | 122.7814 | -0.059509 | 60.9604 | 122.6807 | 122.7585 | -122.8409 | -122.9691
21.3281 | 123.1018 | -60.8871 | 61.9629 | -0.042267 | 0.019224 | 0.02107 | 0.00061099 | 0.06887 | -0.00085669 | 0.068609 | -60.9512 | 61.8805 | -60.8643 | -61.0245 | 61.8118 | 0.091553 | 0.041199 | 0.036621 | 61.8851 | -61.0107 | 0.022888 | -0.082398 | -0.064087 | -0.13733 | -0.15106 | -0.1236 | -0.07782 | -0.086975 | 60.9283 | 60.9238 | 122.699 | 122.7676 | -0.064087 | 122.7722 | 60.9787 | -0.1236 | 122.7676 | -0.064087 | 60.9787 | 122.699 | 122.7722 | -122.8271 | -122.9736
22.3281 | 123.0789 | -60.8734 | 61.9858 | -0.042267 | 0.020292 | 0.015943 | 0.00232 | 0.07122 | -0.0034201 | 0.070318 | -60.9467 | 61.8713 | -60.878 | -61.0474 | 61.8073 | 0.09613 | 0.064087 | 0.050354 | 61.8988 | -61.0291 | -0.004578 | -0.11444 | -0.073242 | -0.17395 | -0.17853 | -0.15564 | -0.086975 | -0.068664 | 60.9375 | 60.9238 | 122.6807 | 122.7448 | -0.073242 | 122.7722 | 60.9695 | -0.15564 | 122.7448 | -0.073242 | 60.9695 | 122.6807 | 122.7722 | -122.8638 | -123.0148
23.3281 | 123.0606 | -60.8734 | 62.0087 | -0.13382 | 0.020719 | 0.015088 | -0.0013116 | 0.066093 | -0.0012839 | 0.06925 | -60.9924 | 61.8988 | -60.8597 | -61.0886 | 61.7981 | 0.082397 | 0.054932 | 0.11444 | 61.908 | -61.0153 | 0.013733 | -0.10986 | -0.11902 | -0.21515 | -0.21057 | -0.14191 | -0.10071 | -0.13275 | 60.9283 | 60.9879 | 122.6715 | 122.7722 | -0.11902 | 122.7814 | 60.9558 | -0.14191 | 122.7722 | -0.11902 | 60.9558 | 122.6715 | 122.7814 | -122.8683 | -123.024
24.3281 | 123.0377 | -60.878 | 61.9858 | -0.14908 | 0.020719 | 0.017652 | 0.0012518 | 0.067588 | -0.0017111 | 0.069891 | -60.9924 | 61.9034 | -60.8917 | -61.084 | 61.7889 | 0.07782 | 0.15564 | 0.009155 | 61.8942 | -61.0016 | -0.013733 | -0.082398 | -0.11444 | -0.20599 | -0.19684 | -0.1236 | -0.091553 | -0.10071 | 61.0336 | 60.8871 | 122.6669 | 122.7814 | -0.11444 | 122.7722 | 60.9558 | -0.1236 | 122.7814 | -0.11444 | 60.9558 | 122.6669 | 122.7722 | -122.8775 | -122.9874
25.3281 | 123.0515 | -60.8688 | 61.972 | -0.16434 | 0.021787 | 0.017224 | -0.0025934 | 0.065452 | -2.092e-06 | 0.069464 | -60.9375 | 61.8942 | -60.8734 | -61.0657 | 61.8301 | 0.10071 | 0.09613 | 0.050354 | 61.8988 | -60.9879 | -0.004578 | -0.07782 | -0.068665 | -0.19684 | -0.14191 | -0.11902 | -0.073242 | -0.064087 | 60.965 | 60.9192 | 122.699 | 122.7631 | -0.068665 | 122.7676 | 60.9695 | -0.11902 | 122.7631 | -0.068665 | 60.9695 | 122.699 | 122.7676 | -122.8455 | -122.9599
26.3281 | 123.0331 | -60.8734 | 61.9904 | -0.088043 | 0.022001 | 0.01872 | 0.003388 | 0.065879 | 0.0025613 | 0.070318 | -60.9787 | 61.8851 | -60.8688 | -61.0657 | 61.8256 | 0.13733 | 0.10986 | 0.054932 | 61.8759 | -61.0062 | 0.004578 | -0.10528 | -0.10529 | -0.19226 | -0.16479 | -0.13275 | -0.11444 | -0.10986 | 60.9833 | 60.9283 | 122.699 | 122.7585 | -0.10529 | 122.7493 | 61.0107 | -0.13275 | 122.7585 | -0.10529 | 61.0107 | 122.699 | 122.7493 | -122.8592 | -122.9965
27.3281 | 123.0652 | -60.9009 | 61.9949 | -0.042267 | 0.020719 | 0.016797 | 0.0018928 | 0.066093 | -0.0025657 | 0.069464 | -60.9512 | 61.9034 | -60.8551 | -61.0474 | 61.8073 | 0.09613 | 0.082397 | 0.068665 | 61.8988 | -61.0062 | 0.045776 | -0.091553 | -0.050354 | -0.14648 | -0.18768 | -0.10529 | -0.09613 | -0.09613 | 60.9833 | 60.9695 | 122.7081 | 122.8043 | -0.050354 | 122.7997 | 60.997 | -0.10529 | 122.8043 | -0.050354 | 60.997 | 122.7081 | 122.7997 | -122.85 | -123.0011
28.3281 | 123.0606 | -60.8871 | 61.9675 | -0.13382 | 0.020078 | 0.015088 | 0.0021064 | 0.065452 | -0.0040609 | 0.0716 | -60.9512 | 61.8942 | -60.8871 | -61.0428 | 61.8164 | 0.10529 | 0.091553 | 0.045776 | 61.8988 | -61.0199 | 0 | -0.073242 | -0.064087 | -0.15564 | -0.15106 | -0.13275 | -0.068664 | -0.064087 | 60.9787 | 60.9329 | 122.7036 | 122.7814 | -0.064087 | 122.7859 | 60.9924 | -0.13275 | 122.7814 | -0.064087 | 60.9924 | 122.7036 | 122.7859 | -122.8546 | -122.9874
29.3281 | 123.0606 | -60.8688 | 61.972 | -0.12619 | 0.019224 | 0.017865 | 0.0010382 | 0.066947 | -0.0012839 | 0.069037 | -60.9467 | 61.8805 | -60.8551 | -61.0611 | 61.821 | 0.11444 | 0.09613 | 0.045776 | 61.8622 | -61.0107 | 0.013732 | -0.091553 | -0.07782 | -0.19226 | -0.15106 | -0.14191 | -0.10986 | -0.091552 | 60.965 | 60.9146 | 122.6898 | 122.7493 | -0.07782 | 122.731 | 60.9833 | -0.14191 | 122.7493 | -0.07782 | 60.9833 | 122.6898 | 122.731 | -122.8271 | -122.9828
30.3281 | 123.0469 | -60.8917 | 61.9812 | -0.17197 | 0.022428 | 0.015729 | 0.00061099 | 0.066093 | -0.0025657 | 0.070105 | -61.0107 | 61.8896 | -60.8826 | -61.1069 | 61.7661 | 0.091553 | 0.14191 | 0.018311 | 61.8896 | -61.0062 | 0.009156 | -0.091553 | -0.11902 | -0.21515 | -0.21515 | -0.11444 | -0.091553 | -0.12817 | 61.0336 | 60.91 | 122.6578 | 122.7814 | -0.11902 | 122.7814 | 60.9833 | -0.11444 | 122.7814 | -0.11902 | 60.9833 | 122.6578 | 122.7814 | -122.8638 | -122.9874
31.3281 | 123.0011 | -60.8734 | 61.9858 | -0.15671 | 0.02136 | 0.016797 | -0.00088441 | 0.065666 | -0.00021569 | 0.068396 | -61.0016 | 61.8942 | -60.8734 | -61.0886 | 61.7935 | 0.054932 | 0.17395 | 0.018311 | 61.8942 | -60.997 | 0 | -0.091553 | -0.12817 | -0.21515 | -0.19226 | -0.1236 | -0.091553 | -0.12817 | 61.0474 | 60.8917 | 122.6669 | 122.7676 | -0.12817 | 122.7676 | 60.9283 | -0.1236 | 122.7676 | -0.12817 | 60.9283 | 122.6669 | 122.7676 | -122.8592 | -122.9828
32.3281 | 123.0469 | -60.878 | 61.9858 | -0.18723 | 0.019651 | 0.018506 | -2.9814e-05 | 0.067375 | -0.0025657 | 0.067969 | -60.9695 | 61.8805 | -60.878 | -60.9924 | 61.7844 | 0.082397 | 0.17853 | 0.032043 | 61.9034 | -60.9695 | 0 | -0.10529 | -0.091552 | -0.11444 | -0.20142 | -0.091552 | -0.082398 | -0.091552 | 61.0565 | 60.91 | 122.6624 | 122.7585 | -0.091552 | 122.7814 | 60.9604 | -0.091552 | 122.7585 | -0.091552 | 60.9604 | 122.6624 | 122.7814 | -122.8638 | -122.9553
33.3281 | 123.0652 | -60.8688 | 61.9858 | -0.17197 | 0.019224 | 0.018506 | 0.0021064 | 0.06652 | -0.0012839 | 0.071814 | -60.9879 | 61.8759 | -60.8459 | -61.0748 | 61.7386 | -0.050354 | 0.23346 | 0.082397 | 61.8851 | -61.0062 | 0.022888 | -0.10986 | -0.11902 | -0.20599 | -0.24719 | -0.13733 | -0.10071 | -0.14191 | 61.1023 | 60.9512 | 122.6074 | 122.7448 | -0.11902 | 122.7539 | 60.8185 | -0.13733 | 122.7448 | -0.11902 | 60.8185 | 122.6074 | 122.7539 | -122.8317 | -122.9919
34.3281 | 123.056 | -60.8826 | 61.9858 | -0.034637 | 0.017088 | 0.015943 | 0.0012518 | 0.067802 | -0.0025657 | 0.06925 | -60.9421 | 61.8851 | -60.8505 | -61.0611 | 61.821 | 0.10529 | 0.064087 | 0.050354 | 61.8759 | -61.0245 | 0.032043 | -0.10071 | -0.05951 | -0.17853 | -0.16479 | -0.14191 | -0.10986 | -0.091553 | 60.9467 | 60.9329 | 122.7036 | 122.7676 | -0.05951 | 122.7585 | 60.9879 | -0.14191 | 122.7676 | -0.05951 | 60.9879 | 122.7036 | 122.7585 | -122.8363 | -123.0103
35.3281 | 123.0515 | -60.8917 | 61.972 | -0.14145 | 0.02371 | 0.016156 | 0.0014654 | 0.066093 | -0.0012839 | 0.070959 | -60.9558 | 61.8851 | -60.8414 | -61.0565 | 61.8073 | 0.10529 | 0.068665 | 0.045776 | 61.8668 | -61.0016 | 0.050354 | -0.086975 | -0.064087 | -0.16479 | -0.16479 | -0.10986 | -0.10529 | -0.11444 | 60.9604 | 60.9375 | 122.699 | 122.7768 | -0.064087 | 122.7585 | 60.997 | -0.10986 | 122.7768 | -0.064087 | 60.997 | 122.699 | 122.7585 | -122.8134 | -122.9736
36.3281 | 123.0331 | -60.878 | 61.9858 | -0.11856 | 0.02136 | 0.016797 | 0.0014654 | 0.066093 | -0.0014975 | 0.071814 | -60.9512 | 61.8851 | -60.8688 | -61.0336 | 61.8118 | 0.10529 | 0.091553 | 0.050354 | 61.8668 | -61.0291 | 0.009156 | -0.10071 | -0.073242 | -0.15564 | -0.17395 | -0.15106 | -0.11902 | -0.082398 | 60.9695 | 60.9283 | 122.6898 | 122.7631 | -0.073242 | 122.7448 | 60.9833 | -0.15106 | 122.7631 | -0.073242 | 60.9833 | 122.6898 | 122.7448 | -122.8546 | -123.0148
37.3281 | 123.0698 | -60.8734 | 61.9858 | -0.16434 | 0.019865 | 0.016797 | -0.00067081 | 0.065452 | -0.00085669 | 0.069464 | -61.0016 | 61.9125 | -60.8826 | -61.084 | 61.7844 | 0.07782 | 0.16937 | 0.022888 | 61.8805 | -61.0016 | -0.009155 | -0.073242 | -0.12817 | -0.21057 | -0.20142 | -0.12817 | -0.10529 | -0.11902 | 61.0428 | 60.8963 | 122.6578 | 122.7859 | -0.12817 | 122.7539 | 60.9512 | -0.12817 | 122.7859 | -0.12817 | 60.9512 | 122.6578 | 122.7539 | -122.8683 | -122.9874
38.3281 | 123.0515 | -60.8597 | 62.0178 | -0.13382 | 0.020292 | 0.015729 | -0.00024361 | 0.065666 | -0.0014975 | 0.069464 | -60.9833 | 61.9171 | -60.8826 | -61.0977 | 61.8073 | 0.064087 | 0.16022 | 0.032043 | 61.8942 | -61.0016 | -0.022888 | -0.10071 | -0.1236 | -0.23804 | -0.21057 | -0.14191 | -0.1236 | -0.10071 | 61.0199 | 60.8917 | 122.6669 | 122.7768 | -0.1236 | 122.7539 | 60.9238 | -0.14191 | 122.7768 | -0.1236 | 60.9238 | 122.6669 | 122.7539 | -122.9004 | -123.0194
39.3281 | 123.0743 | -60.8871 | 61.9904 | -0.26352 | 0.020719 | 0.012738 | 0.0027472 | 0.067161 | -0.0010703 | 0.071173 | -60.9558 | 61.8576 | -60.8734 | -61.0519 | 61.8073 | 0.10529 | 0.091553 | 0.059509 | 61.8851 | -60.997 | 0.013733 | -0.13275 | -0.068665 | -0.16479 | -0.1831 | -0.10986 | -0.10528 | -0.082398 | 60.9787 | 60.9467 | 122.6944 | 122.7448 | -0.068665 | 122.7722 | 60.9924 | -0.10986 | 122.7448 | -0.068665 | 60.9924 | 122.6944 | 122.7722 | -122.8638 | -122.9874
40.3281 | 123.0743 | -60.8871 | 61.9766 | -0.33218 | 0.019651 | 0.017224 | 0.0036018 | 0.068443 | -0.0014975 | 0.067328 | -60.9924 | 61.8942 | -60.878 | -61.0565 | 61.8027 | 0.10529 | 0.10071 | 0.036621 | 61.8988 | -60.997 | 0.009155 | -0.082398 | -0.10529 | -0.16937 | -0.17395 | -0.10986 | -0.07782 | -0.11444 | 60.9879 | 60.9238 | 122.6898 | 122.7814 | -0.10529 | 122.7859 | 60.9924 | -0.10986 | 122.7814 | -0.10529 | 60.9924 | 122.6898 | 122.7859 | -122.8546 | -122.9736
41.3281 | 123.056 | -60.8826 | 61.9766 | -0.080414 | 0.022001 | 0.019788 | 0.005097 | 0.065666 | 0.00085231 | 0.06925 | -60.9512 | 61.9125 | -60.8505 | -61.0382 | 61.8256 | 0.091553 | 0.064087 | 0.036621 | 61.8759 | -60.997 | 0.032043 | -0.064087 | -0.068665 | -0.15564 | -0.15106 | -0.11444 | -0.10071 | -0.10071 | 60.9467 | 60.9192 | 122.7081 | 122.7951 | -0.068665 | 122.7585 | 60.9741 | -0.11444 | 122.7951 | -0.068665 | 60.9741 | 122.7081 | 122.7585 | -122.8271 | -122.9736
42.3281 | 123.0972 | -60.8597 | 61.9537 | -0.049896 | 0.020719 | 0.017652 | 0.0021064 | 0.067375 | -0.0017111 | 0.069037 | -60.9421 | 61.8759 | -60.8597 | -61.0474 | 61.8118 | 0.091553 | 0.054932 | 0.059509 | 61.8713 | -60.997 | 0 | -0.077819 | -0.082398 | -0.18768 | -0.14191 | -0.13733 | -0.082397 | -0.082398 | 60.9146 | 60.9192 | 122.6715 | 122.7356 | -0.082398 | 122.731 | 60.9512 | -0.13733 | 122.7356 | -0.082398 | 60.9512 | 122.6715 | 122.731 | -122.8134 | -122.9507
43.3281 | 123.0698 | -60.8871 | 61.9904 | -0.080414 | 0.023069 | 0.017224 | 0.00082459 | 0.065452 | -0.0025657 | 0.070105 | -60.9421 | 61.8896 | -60.8917 | -61.0519 | 61.8347 | 0.091553 | 0.064087 | 0.041199 | 61.8622 | -61.0245 | -0.004578 | -0.10071 | -0.054932 | -0.16479 | -0.15564 | -0.13733 | -0.12817 | -0.050354 | 60.9512 | 60.9283 | 122.7219 | 122.7768 | -0.054932 | 122.7493 | 60.9787 | -0.13733 | 122.7768 | -0.054932 | 60.9787 | 122.7219 | 122.7493 | -122.8821 | -123.0148
44.3281 | 123.0789 | -60.8459 | 61.9858 | -0.17197 | 0.019651 | 0.018933 | 0.0025336 | 0.066734 | -0.0040609 | 0.070318 | -60.9741 | 61.8713 | -60.8597 | -61.0703 | 61.8301 | 0.11444 | 0.10071 | 0.045776 | 61.8851 | -61.0062 | -0.013733 | -0.11444 | -0.12817 | -0.2243 | -0.15564 | -0.16022 | -0.10071 | -0.11444 | 60.9467 | 60.8917 | 122.6761 | 122.7173 | -0.12817 | 122.731 | 60.9604 | -0.16022 | 122.7173 | -0.12817 | 60.9604 | 122.6761 | 122.731 | -122.8455 | -122.9919
45.3281 | 123.0423 | -60.8643 | 62.0132 | -0.14908 | 0.020933 | 0.015515 | -0.00024361 | 0.066947 | 0.00085231 | 0.069891 | -60.9924 | 61.8988 | -60.8963 | -61.0382 | 61.6379 | -0.027466 | 0.23804 | 0.018311 | 61.8942 | -60.9833 | -0.032043 | -0.11444 | -0.12817 | -0.17395 | -0.37537 | -0.11902 | -0.11902 | -0.096131 | 61.1023 | 60.8826 | 122.5021 | 122.7631 | -0.12817 | 122.7585 | 60.8368 | -0.11902 | 122.7631 | -0.12817 | 60.8368 | 122.5021 | 122.7585 | -122.9095 | -122.9965
46.3281 | 123.0835 | -60.8597 | 61.9629 | -0.095673 | 0.020078 | 0.015515 | 0.0038154 | 0.067375 | -0.00021569 | 0.070105 | -60.9558 | 61.908 | -60.878 | -61.0519 | 61.8027 | 0.10529 | 0.068665 | 0.064087 | 61.8805 | -61.0016 | -0.018311 | -0.054932 | -0.096131 | -0.19226 | -0.16022 | -0.14191 | -0.082398 | -0.07782 | 60.9283 | 60.9238 | 122.6624 | 122.7676 | -0.096131 | 122.7402 | 60.965 | -0.14191 | 122.7676 | -0.096131 | 60.965 | 122.6624 | 122.7402 | -122.8409 | -122.9645
47.3281 | 123.0469 | -60.8917 | 61.9904 | -0.1033 | 0.022215 | 0.01637 | 0.0046698 | 0.067375 | 0.00021151 | 0.070959 | -60.9467 | 61.8805 | -60.878 | -61.0611 | 61.8164 | 0.091553 | 0.082397 | 0.059509 | 61.8713 | -60.997 | 0.013733 | -0.10986 | -0.054931 | -0.16937 | -0.17395 | -0.10528 | -0.11902 | -0.068664 | 60.9741 | 60.9512 | 122.7081 | 122.7722 | -0.054931 | 122.7631 | 60.9833 | -0.10528 | 122.7722 | -0.054931 | 60.9833 | 122.7081 | 122.7631 | -122.8683 | -122.9874
48.3281 | 123.0423 | -60.8688 | 61.9858 | -0.042267 | 0.022001 | 0.015515 | 0.0010382 | 0.065666 | -2.092e-06 | 0.068609 | -60.9421 | 61.8713 | -60.8551 | -61.0657 | 61.8164 | 0.086975 | 0.036621 | 0.027466 | 61.8576 | -61.0382 | 0.013732 | -0.11444 | -0.073243 | -0.19684 | -0.16937 | -0.16937 | -0.12817 | -0.086975 | 60.9055 | 60.8963 | 122.6852 | 122.7402 | -0.073243 | 122.7264 | 60.9558 | -0.16937 | 122.7402 | -0.073243 | 60.9558 | 122.6852 | 122.7264 | -122.8409 | -123.024
49.3281 | 123.056 | -60.8917 | 61.9629 | -0.080414 | 0.019651 | 0.016797 | 0.0031744 | 0.067161 | -0.0019247 | 0.070959 | -60.9512 | 61.8668 | -60.8597 | -61.0703 | 61.7981 | 0.10071 | 0.045776 | 0.041199 | 61.8805 | -61.0107 | 0.032044 | -0.096131 | -0.059509 | -0.17853 | -0.16479 | -0.11902 | -0.082398 | -0.091553 | 60.9375 | 60.9329 | 122.6898 | 122.7585 | -0.059509 | 122.7722 | 60.9924 | -0.11902 | 122.7585 | -0.059509 | 60.9924 | 122.6898 | 122.7722 | -122.8226 | -122.9736
50.3281 | 123.0606 | -60.8734 | 61.972 | -0.072784 | 0.020506 | 0.017438 | 0.0010382 | 0.066734 | -0.0029929 | 0.071814 | -60.9741 | 61.908 | -60.8734 | -61.0474 | 61.8164 | 0.10529 | 0.045776 | 0.045776 | 61.8896 | -60.997 | 0 | -0.064087 | -0.10071 | -0.17395 | -0.15564 | -0.1236 | -0.082398 | -0.10071 | 60.9192 | 60.9192 | 122.6898 | 122.7814 | -0.10071 | 122.7631 | 60.9787 | -0.1236 | 122.7814 | -0.10071 | 60.9787 | 122.6898 | 122.7631 | -122.8455 | -122.9691
51.3281 | 123.0652 | -60.8734 | 61.9766 | 0.20187 | 0.019438 | 0.014875 | 0.0018928 | 0.068015 | -0.0021383 | 0.069677 | -60.8963 | 61.8896 | -60.8734 | -61.0611 | 61.821 | 0.11444 | 0.10986 | 0.064087 | 61.8713 | -61.0062 | 0 | -0.086976 | -0.022888 | -0.18768 | -0.15564 | -0.13275 | -0.10529 | -0.022888 | 60.9833 | 60.9375 | 122.6944 | 122.7631 | -0.022888 | 122.7448 | 60.9879 | -0.13275 | 122.7631 | -0.022888 | 60.9879 | 122.6944 | 122.7448 | -122.85 | -122.9828
52.3281 | 123.056 | -60.8734 | 62.0041 | -0.16434 | 0.019438 | 0.019361 | 0.00018379 | 0.067375 | -0.00085669 | 0.071173 | -60.997 | 61.8851 | -60.878 | -61.0886 | 61.8027 | 0.10986 | 0.10986 | 0.045776 | 61.8668 | -61.0016 | -0.004578 | -0.11902 | -0.1236 | -0.21515 | -0.20142 | -0.12817 | -0.13733 | -0.11902 | 60.9833 | 60.9192 | 122.6761 | 122.7585 | -0.1236 | 122.7402 | 60.9833 | -0.12817 | 122.7585 | -0.1236 | 60.9833 | 122.6761 | 122.7402 | -122.8821 | -123.0057
53.3281 | 123.0927 | -60.878 | 61.94 | -0.034637 | 0.019438 | 0.014234 | 0.0014654 | 0.064811 | -0.0021383 | 0.070532 | -60.9421 | 61.8896 | -60.8643 | -61.0428 | 61.8256 | 0.09613 | 0.054932 | 0.050354 | 61.8942 | -60.9879 | 0.013733 | -0.050354 | -0.064087 | -0.16479 | -0.11444 | -0.10986 | -0.045776 | -0.07782 | 60.9329 | 60.9283 | 122.7036 | 122.7676 | -0.064087 | 122.7722 | 60.9741 | -0.10986 | 122.7676 | -0.064087 | 60.9741 | 122.7036 | 122.7722 | -122.8043 | -122.9279
54.3281 | 123.0652 | -60.8963 | 61.972 | -0.065155 | 0.022428 | 0.017865 | 0.0014654 | 0.06887 | -0.0010703 | 0.06925 | -60.9512 | 61.8851 | -60.8688 | -61.0428 | 61.8164 | 0.086975 | 0.064087 | 0.059509 | 61.8759 | -61.0153 | 0.027466 | -0.086975 | -0.054932 | -0.14648 | -0.15564 | -0.11902 | -0.09613 | -0.082398 | 60.9604 | 60.9558 | 122.7127 | 122.7814 | -0.054932 | 122.7722 | 60.9833 | -0.11902 | 122.7814 | -0.054932 | 60.9833 | 122.7127 | 122.7722 | -122.8409 | -122.9874
55.3281 | 123.0652 | -60.8917 | 62.0041 | -0.049896 | 0.021147 | 0.016156 | 0.0021064 | 0.066734 | -0.0012839 | 0.068396 | -60.9467 | 61.8668 | -60.878 | -61.0611 | 61.8164 | 0.09613 | 0.045776 | 0.036621 | 61.8576 | -61.0382 | 0.013733 | -0.13733 | -0.054931 | -0.16937 | -0.18768 | -0.14648 | -0.14648 | -0.068664 | 60.9375 | 60.9283 | 122.7081 | 122.7585 | -0.054931 | 122.7493 | 60.9879 | -0.14648 | 122.7585 | -0.054931 | 60.9879 | 122.7081 | 122.7493 | -122.8821 | -123.0423
56.3281 | 123.0652 | -60.8734 | 61.9446 | 0.011139 | 0.021787 | 0.015943 | 0.0044562 | 0.066306 | -0.0012839 | 0.0716 | -60.9421 | 61.8851 | -60.8871 | -61.0565 | 61.8256 | 0.086975 | 0.050354 | 0.027466 | 61.8759 | -61.0062 | -0.013733 | -0.059509 | -0.068665 | -0.18311 | -0.11902 | -0.13275 | -0.068664 | -0.054932 | 60.9238 | 60.9009 | 122.699 | 122.7585 | -0.068665 | 122.7493 | 60.9604 | -0.13275 | 122.7585 | -0.068665 | 60.9604 | 122.699 | 122.7493 | -122.8317 | -122.9507
57.3281 | 123.0972 | -60.9009 | 61.9583 | -0.065155 | 0.020292 | 0.019147 | 0.0031744 | 0.069297 | -0.0012839 | 0.0716 | -60.9604 | 61.8805 | -60.878 | -61.0519 | 61.8118 | 0.086975 | 0.054932 | 0.045776 | 61.8805 | -61.0199 | 0.022888 | -0.07782 | -0.059509 | -0.15106 | -0.14648 | -0.11902 | -0.07782 | -0.082397 | 60.9558 | 60.9467 | 122.7127 | 122.7814 | -0.059509 | 122.7814 | 60.9879 | -0.11902 | 122.7814 | -0.059509 | 60.9879 | 122.7127 | 122.7814 | -122.8363 | -122.9782
58.3281 | 123.0698 | -60.8688 | 62.0041 | -0.13382 | 0.023069 | 0.017438 | 0.0016792 | 0.065666 | -0.0014975 | 0.069037 | -61.1069 | 61.8622 | -60.8871 | -61.0703 | 61.8439 | 0.10986 | 0.10986 | 0.054932 | 61.8942 | -60.997 | -0.018311 | -0.14191 | -0.23804 | -0.20142 | -0.16022 | -0.12817 | -0.10986 | -0.21973 | 60.9787 | 60.9238 | 122.7127 | 122.731 | -0.23804 | 122.7631 | 60.9787 | -0.12817 | 122.731 | -0.23804 | 60.9787 | 122.7127 | 122.7631 | -122.8912 | -123.0011
59.3281 | 123.0652 | -60.8917 | 62.0132 | -0.16434 | 0.020933 | 0.019147 | 0.0029608 | 0.06652 | 0.00085231 | 0.06925 | -61.0107 | 61.908 | -60.8734 | -61.1023 | 61.8988 | 0.10986 | 0.17395 | 0.091553 | 61.908 | -61.0153 | 0.018311 | -0.10529 | -0.11902 | -0.21057 | -0.11444 | -0.1236 | -0.10529 | -0.13733 | 61.0657 | 60.9833 | 122.7905 | 122.7997 | -0.11902 | 122.7997 | 61.0016 | -0.1236 | 122.7997 | -0.11902 | 61.0016 | 122.7905 | 122.7997 | -122.8867 | -123.0286
60.3281 | 123.0652 | -60.878 | 61.9904 | -0.1033 | 0.020933 | 0.014661 | 0.0016792 | 0.066093 | -0.0029929 | 0.068823 | -60.9512 | 61.8988 | -60.878 | -61.0565 | 61.821 | 0.10529 | 0.064087 | 0.059509 | 61.8942 | -61.0153 | 0 | -0.091552 | -0.073242 | -0.17853 | -0.16937 | -0.13733 | -0.09613 | -0.073242 | 60.9421 | 60.9375 | 122.699 | 122.7768 | -0.073242 | 122.7722 | 60.9833 | -0.13733 | 122.7768 | -0.073242 | 60.9833 | 122.699 | 122.7722 | -122.8683 | -123.0057
61.3281 | 123.0789 | -60.878 | 61.9858 | -0.11093 | 0.018583 | 0.018079 | 0.0025336 | 0.066734 | -0.0025657 | 0.070532 | -60.9512 | 61.8942 | -60.8551 | -61.0611 | 61.8164 | 0.09613 | 0.09613 | 0.054932 | 61.8759 | -60.9924 | 0.022888 | -0.091553 | -0.073242 | -0.1831 | -0.16937 | -0.11444 | -0.10986 | -0.09613 | 60.9741 | 60.9329 | 122.6944 | 122.7722 | -0.073242 | 122.7539 | 60.9741 | -0.11444 | 122.7722 | -0.073242 | 60.9741 | 122.6944 | 122.7539 | -122.8409 | -122.9782
62.3281 | 123.0652 | -60.8826 | 61.9675 | -0.019379 | 0.022001 | 0.017652 | 0.0027472 | 0.068443 | -0.00085669 | 0.068823 | -60.9467 | 61.8668 | -60.8688 | -61.0565 | 61.821 | 0.09613 | 0.054932 | 0.041199 | 61.8759 | -61.0245 | 0.013733 | -0.10071 | -0.064087 | -0.17395 | -0.14648 | -0.14191 | -0.091552 | -0.07782 | 60.9375 | 60.9238 | 122.7036 | 122.7493 | -0.064087 | 122.7585 | 60.9787 | -0.14191 | 122.7493 | -0.064087 | 60.9787 | 122.7036 | 122.7585 | -122.8363 | -122.9919
63.3281 | 123.0698 | -60.91 | 61.9583 | -0.057526 | 0.020292 | 0.016156 | 0.0025336 | 0.068015 | -0.0032065 | 0.068823 | -60.9558 | 61.8988 | -60.8871 | -61.0474 | 61.8027 | 0.09613 | 0.068665 | 0.064087 | 61.8759 | -61.0291 | 0.022888 | -0.059509 | -0.045777 | -0.13733 | -0.15564 | -0.11902 | -0.082397 | -0.068665 | 60.9787 | 60.9741 | 122.7127 | 122.8088 | -0.045777 | 122.7859 | 61.0062 | -0.11902 | 122.8088 | -0.045777 | 61.0062 | 122.7127 | 122.7859 | -122.8455 | -122.9874
64.3281 | 123.056 | -60.878 | 61.972 | -0.088043 | 0.022001 | 0.016156 | 0.0021064 | 0.064811 | -0.00085669 | 0.070532 | -60.9558 | 61.8988 | -60.8917 | -61.0474 | 61.8256 | 0.10071 | 0.07782 | 0.054932 | 61.8805 | -61.0153 | -0.013733 | -0.073242 | -0.07782 | -0.16937 | -0.14648 | -0.13733 | -0.091553 | -0.064087 | 60.9558 | 60.9329 | 122.7036 | 122.7768 | -0.07782 | 122.7585 | 60.9787 | -0.13733 | 122.7768 | -0.07782 | 60.9787 | 122.7036 | 122.7585 | -122.8638 | -122.9874
65.3281 | 123.0698 | -60.8688 | 61.9995 | -0.11856 | 0.019438 | 0.020429 | -0.001098 | 0.065452 | -2.092e-06 | 0.070959 | -60.9924 | 61.9034 | -60.9055 | -61.1114 | 61.7935 | 0.091553 | 0.16479 | 0.036621 | 61.8851 | -61.0245 | -0.036622 | -0.096131 | -0.1236 | -0.24262 | -0.20599 | -0.15564 | -0.11444 | -0.086975 | 61.0336 | 60.9055 | 122.6624 | 122.7722 | -0.1236 | 122.7539 | 60.9604 | -0.15564 | 122.7722 | -0.1236 | 60.9604 | 122.6624 | 122.7539 | -122.905 | -123.024
66.3281 | 123.0194 | -60.8734 | 62.0041 | -0.1796 | 0.021147 | 0.013593 | 0.00018379 | 0.066306 | -2.092e-06 | 0.072241 | -60.997 | 61.908 | -60.878 | -61.1069 | 61.7844 | 0.082397 | 0.16022 | 0.027466 | 61.908 | -61.0245 | -0.004578 | -0.09613 | -0.1236 | -0.23346 | -0.21973 | -0.15106 | -0.09613 | -0.11902 | 61.0336 | 60.9009 | 122.6578 | 122.7814 | -0.1236 | 122.7814 | 60.9558 | -0.15106 | 122.7814 | -0.1236 | 60.9558 | 122.6578 | 122.7814 | -122.8821 | -123.0286
67.3281 | 123.0698 | -60.8688 | 62.0132 | -0.14145 | 0.018156 | 0.014661 | 0.0029608 | 0.064811 | 0.00063871 | 0.069464 | -60.9924 | 61.8805 | -60.878 | -60.997 | 61.8439 | 0.059509 | 0.15564 | 0.036621 | 61.9034 | -61.0153 | -0.009156 | -0.13275 | -0.1236 | -0.12817 | -0.16937 | -0.14649 | -0.10986 | -0.11444 | 61.0245 | 60.9055 | 122.7127 | 122.7493 | -0.1236 | 122.7722 | 60.9283 | -0.14649 | 122.7493 | -0.1236 | 60.9283 | 122.7127 | 122.7722 | -122.8912 | -123.0286
68.3281 | 123.0103 | -60.878 | 61.9583 | -0.15671 | 0.02136 | 0.015302 | 0.0010382 | 0.067375 | -0.0014975 | 0.069037 | -61.0062 | 61.8759 | -60.8963 | -61.0886 | 61.7844 | 0.10071 | 0.14191 | 0.036621 | 61.9034 | -60.9741 | -0.01831 | -0.082397 | -0.12817 | -0.21057 | -0.17395 | -0.09613 | -0.054932 | -0.10986 | 61.0199 | 60.9146 | 122.6624 | 122.7539 | -0.12817 | 122.7814 | 60.9787 | -0.09613 | 122.7539 | -0.12817 | 60.9787 | 122.6624 | 122.7814 | -122.8546 | -122.9324
69.3281 | 123.0515 | -60.8414 | 61.9537 | -0.065155 | 0.019865 | 0.022565 | 0.0010382 | 0.06652 | -0.0057699 | 0.070105 | -60.9558 | 61.8759 | -60.8505 | -61.0519 | 61.8027 | 0.091553 | 0.068665 | 0.059509 | 61.8622 | -61.0062 | -0.009155 | -0.077819 | -0.11444 | -0.21057 | -0.15106 | -0.1648 | -0.091552 | -0.10529 | 60.91 | 60.9009 | 122.644 | 122.7173 | -0.11444 | 122.7036 | 60.9329 | -0.1648 | 122.7173 | -0.11444 | 60.9329 | 122.644 | 122.7036 | -122.8043 | -122.9599
70.3281 | 123.1064 | -60.8643 | 61.9904 | 0.0035097 | 0.019438 | 0.012097 | 0.0016792 | 0.067588 | -0.0012839 | 0.069891 | -60.9421 | 61.8851 | -60.8688 | -61.0703 | 61.821 | 0.10986 | 0.091553 | 0.059509 | 61.8851 | -61.0062 | -0.004577 | -0.10528 | -0.07782 | -0.20599 | -0.16937 | -0.14191 | -0.10528 | -0.073243 | 60.9558 | 60.9238 | 122.6852 | 122.7493 | -0.07782 | 122.7493 | 60.9741 | -0.14191 | 122.7493 | -0.07782 | 60.9741 | 122.6852 | 122.7493 | -122.8592 | -122.9965
71.3281 | 123.0331 | -60.8826 | 61.9675 | -0.14908 | 0.020506 | 0.016797 | 0.0031744 | 0.066306 | -0.00042929 | 0.067541 | -60.9283 | 61.8896 | -60.91 | -61.0657 | 61.8073 | 0.10529 | 0.11444 | 0.045776 | 61.8668 | -61.0291 | -0.027466 | -0.07782 | -0.045777 | -0.18311 | -0.16022 | -0.14648 | -0.10071 | -0.018311 | 60.997 | 60.9283 | 122.6898 | 122.7722 | -0.045777 | 122.7493 | 60.9879 | -0.14648 | 122.7722 | -0.045777 | 60.9879 | 122.6898 | 122.7493 | -122.8775 | -122.9965
72.3438 | 123.1522 | -60.878 | 61.908 | 0.2858 | 0.022001 | 0.015302 | -0.0021662 | 0.066093 | -0.0023519 | 0.0716 | -60.9375 | 61.8027 | -60.878 | -61.0199 | 61.8439 | 0.082397 | -0.15564 | 0.036621 | 61.7981 | -60.9879 | 0 | -0.10529 | -0.059509 | -0.14191 | -0.064087 | -0.10986 | -0.10986 | -0.059509 | 60.7224 | 60.9146 | 122.7219 | 122.6807 | -0.059509 | 122.6761 | 60.9604 | -0.10986 | 122.6807 | -0.059509 | 60.9604 | 122.7219 | 122.6761 | -122.7859 | -122.8958
73.3281 | 123.0972 | -60.8826 | 62.0087 | -0.14145 | 0.019651 | 0.01402 | 0.0016792 | 0.063957 | -0.0032065 | 0.06925 | -60.9741 | 61.8896 | -60.8826 | -61.0565 | 61.7981 | 0.09613 | 0.13733 | -0.12817 | 61.8576 | -61.0245 | 0 | -0.11902 | -0.091553 | -0.17395 | -0.21057 | -0.14191 | -0.15106 | -0.091553 | 61.0199 | 60.7544 | 122.6807 | 122.7722 | -0.091553 | 122.7402 | 60.9787 | -0.14191 | 122.7722 | -0.091553 | 60.9787 | 122.6807 | 122.7402 | -122.8912 | -123.0331
74.3281 | 123.024 | -60.8826 | 61.9904 | -0.14145 | 0.02136 | 0.014447 | 0.0021064 | 0.064811 | -0.0025657 | 0.070532 | -60.997 | 61.8851 | -60.8734 | -61.0886 | 61.8027 | 0.07782 | 0.14648 | 0.036621 | 61.8896 | -60.9879 | 0.009155 | -0.10528 | -0.11444 | -0.20599 | -0.18768 | -0.10529 | -0.10071 | -0.1236 | 61.0291 | 60.9192 | 122.6852 | 122.7676 | -0.11444 | 122.7722 | 60.9604 | -0.10529 | 122.7676 | -0.11444 | 60.9604 | 122.6852 | 122.7722 | -122.8638 | -122.9782
75.3281 | 123.0469 | -60.9009 | 61.9812 | -0.088043 | 0.020078 | 0.013806 | 0.0029608 | 0.067802 | -0.0014975 | 0.068823 | -60.9924 | 61.8896 | -60.8917 | -61.084 | 61.7798 | 0.07782 | 0.13733 | 0.045776 | 61.9034 | -60.997 | 0.009155 | -0.091553 | -0.091553 | -0.1831 | -0.20142 | -0.09613 | -0.07782 | -0.10071 | 61.0382 | 60.9467 | 122.6807 | 122.7905 | -0.091553 | 122.8043 | 60.9787 | -0.09613 | 122.7905 | -0.091553 | 60.9787 | 122.6807 | 122.8043 | -122.8729 | -122.9782
76.3281 | 123.0515 | -60.8917 | 61.9812 | -0.088043 | 0.019865 | 0.013806 | 0.004029 | 0.067588 | -0.0021383 | 0.070105 | -60.9512 | 61.8851 | -60.8597 | -61.0291 | 61.8118 | 0.082397 | 0.086975 | 0.059509 | 61.8851 | -61.0153 | 0.032044 | -0.09613 | -0.059509 | -0.13733 | -0.16937 | -0.1236 | -0.09613 | -0.091553 | 60.9787 | 60.9512 | 122.7036 | 122.7768 | -0.059509 | 122.7768 | 60.9741 | -0.1236 | 122.7768 | -0.059509 | 60.9741 | 122.7036 | 122.7768 | -122.8409 | -122.9965
77.3438 | 123.1247 | -60.8871 | 61.9308 | 0.22476 | 0.020719 | 0.018079 | 0.00018379 | 0.064811 | -0.0010703 | 0.06925 | -60.9421 | 61.7752 | -60.8826 | -61.0382 | 61.853 | 0.073242 | -0.14648 | 0.018311 | 61.8164 | -60.9787 | 0.004578 | -0.15564 | -0.054932 | -0.15106 | -0.07782 | -0.091553 | -0.11444 | -0.05951 | 60.7407 | 60.9055 | 122.7402 | 122.6624 | -0.054932 | 122.7036 | 60.9604 | -0.091553 | 122.6624 | -0.054932 | 60.9604 | 122.7402 | 122.7036 | -122.8134 | -122.9095
78.3281 | 123.0652 | -60.8643 | 61.9766 | -0.1033 | 0.020719 | 0.017224 | 0.00232 | 0.068015 | -0.0012839 | 0.069464 | -60.9512 | 61.8851 | -60.8688 | -61.0519 | 61.8164 | 0.091553 | 0.09613 | 0.041199 | 61.8759 | -61.0107 | -0.004577 | -0.091553 | -0.086975 | -0.18768 | -0.16022 | -0.14648 | -0.10071 | -0.082398 | 60.9604 | 60.9055 | 122.6807 | 122.7493 | -0.086975 | 122.7402 | 60.9558 | -0.14648 | 122.7493 | -0.086975 | 60.9558 | 122.6807 | 122.7402 | -122.8455 | -122.9874
79.3281 | 122.8821 | -60.9283 | 61.9766 | -0.14145 | 0.01837 | 0.014234 | 0.0036018 | 0.065666 | -0.0019247 | 0.069677 | -61.0016 | 61.9217 | -60.8871 | -61.084 | 61.7706 | 0.082397 | 0.14648 | 0.041199 | 61.8896 | -61.0062 | 0.041199 | -0.054932 | -0.073242 | -0.15564 | -0.20599 | -0.07782 | -0.086976 | -0.11444 | 61.0748 | 60.9695 | 122.699 | 122.85 | -0.073242 | 122.818 | 61.0107 | -0.07782 | 122.85 | -0.073242 | 61.0107 | 122.699 | 122.818 | -122.8638 | -122.9828
80.3281 | 123.0469 | -60.9055 | 61.9537 | -0.15671 | 0.020933 | 0.013593 | 0.0016792 | 0.066947 | -0.0029929 | 0.071814 | -60.997 | 61.908 | -60.878 | -61.0977 | 61.7844 | 0.082397 | 0.15564 | 0.041199 | 61.8805 | -61.0016 | 0.027466 | -0.045776 | -0.091552 | -0.19226 | -0.16937 | -0.09613 | -0.073242 | -0.11902 | 61.0611 | 60.9467 | 122.6898 | 122.8134 | -0.091552 | 122.7859 | 60.9879 | -0.09613 | 122.8134 | -0.091552 | 60.9879 | 122.6898 | 122.7859 | -122.8317 | -122.9553
81.3281 | 123.0927 | -60.8826 | 61.9858 | -0.14908 | 0.021574 | 0.018293 | 0.0016792 | 0.065238 | -0.0027793 | 0.070532 | -60.965 | 61.8851 | -60.8871 | -61.0657 | 61.8073 | 0.10529 | 0.10071 | 0.064087 | 61.8759 | -61.0291 | -0.004578 | -0.10071 | -0.082398 | -0.18311 | -0.17853 | -0.14648 | -0.10986 | -0.07782 | 60.9833 | 60.9467 | 122.6898 | 122.7676 | -0.082398 | 122.7585 | 60.9879 | -0.14648 | 122.7676 | -0.082398 | 60.9879 | 122.6898 | 122.7585 | -122.8729 | -123.0148
82.3438 | 123.1476 | -60.8643 | 61.9125 | 0.23239 | 0.019651 | 0.017652 | -0.00024361 | 0.066734 | -0.00042929 | 0.069464 | -60.9512 | 61.7844 | -60.878 | -61.0382 | 61.8439 | 0.086975 | -0.16479 | 0.041199 | 61.8164 | -60.9787 | -0.013733 | -0.12817 | -0.086975 | -0.17395 | -0.068665 | -0.11444 | -0.096131 | -0.073242 | 60.6995 | 60.9055 | 122.7081 | 122.6486 | -0.086975 | 122.6807 | 60.9512 | -0.11444 | 122.6486 | -0.086975 | 60.9512 | 122.7081 | 122.6807 | -122.7905 | -122.8912
83.3281 | 123.0789 | -60.8734 | 61.9537 | -0.049896 | 0.019438 | 0.014661 | 0.0046698 | 0.065666 | 0.00021151 | 0.071814 | -60.9604 | 61.8896 | -60.8734 | -61.0428 | 61.8118 | 0.091553 | 0.054932 | 0.045776 | 61.8393 | -61.0428 | 0 | -0.064087 | -0.086975 | -0.16937 | -0.14191 | -0.16937 | -0.11444 | -0.086975 | 60.9283 | 60.9192 | 122.6852 | 122.7631 | -0.086975 | 122.7127 | 60.965 | -0.16937 | 122.7631 | -0.086975 | 60.965 | 122.6852 | 122.7127 | -122.8271 | -122.9965
84.3281 | 123.0789 | -60.8597 | 61.972 | -0.027008 | 0.021147 | 0.01637 | 0.003388 | 0.06887 | -0.00085669 | 0.069891 | -60.9421 | 61.8805 | -60.878 | -61.0474 | 61.8073 | 0.086975 | 0.045776 | 0.041199 | 61.8713 | -61.0199 | -0.018311 | -0.091553 | -0.082398 | -0.18768 | -0.16479 | -0.16022 | -0.10071 | -0.064087 | 60.9055 | 60.9009 | 122.6669 | 122.7402 | -0.082398 | 122.731 | 60.9467 | -0.16022 | 122.7402 | -0.082398 | 60.9467 | 122.6669 | 122.731 | -122.85 | -122.9919
85.3281 | 123.056 | -60.8597 | 61.972 | -0.072784 | 0.020078 | 0.018506 | 0.0059516 | 0.067802 | -0.0027793 | 0.070318 | -60.9467 | 61.8988 | -60.8917 | -61.0428 | 61.8301 | 0.09613 | 0.054932 | 0.045776 | 61.8988 | -61.0199 | -0.032044 | -0.073242 | -0.086975 | -0.18311 | -0.14191 | -0.16022 | -0.073242 | -0.054931 | 60.9146 | 60.9055 | 122.6898 | 122.7585 | -0.086975 | 122.7585 | 60.9558 | -0.16022 | 122.7585 | -0.086975 | 60.9558 | 122.6898 | 122.7585 | -122.8638 | -122.9919
86.3281 | 123.0652 | -60.878 | 61.972 | -0.22537 | 0.019651 | 0.01872 | 0.0031744 | 0.066093 | -0.0040609 | 0.071173 | -61.0016 | 61.9125 | -60.8826 | -61.0336 | 61.7889 | 0.10529 | 0.11902 | 0.059509 | 61.8896 | -61.0199 | -0.004577 | -0.059509 | -0.1236 | -0.15564 | -0.18311 | -0.14191 | -0.082398 | -0.11902 | 60.997 | 60.9375 | 122.6669 | 122.7905 | -0.1236 | 122.7676 | 60.9833 | -0.14191 | 122.7905 | -0.1236 | 60.9833 | 122.6669 | 122.7676 | -122.8546 | -122.9919
87.3438 | 123.0103 | -60.9146 | 61.9354 | 0.13321 | 0.020506 | 0.016156 | 0.0027472 | 0.065238 | -0.0027793 | 0.068823 | -61.0382 | 61.853 | -60.9192 | -61.1435 | 61.734 | -0.032043 | 0.041199 | -0.10071 | 61.8576 | -61.0428 | -0.004577 | -0.082398 | -0.1236 | -0.22888 | -0.20142 | -0.12817 | -0.07782 | -0.11902 | 60.9558 | 60.8139 | 122.6486 | 122.7676 | -0.1236 | 122.7722 | 60.8826 | -0.12817 | 122.7676 | -0.1236 | 60.8826 | 122.6486 | 122.7722 | -122.8546 | -122.9782
88.3281 | 123.056 | -60.8917 | 61.972 | -0.1033 | 0.019224 | 0.015088 | 0.0016792 | 0.065879 | -0.0027793 | 0.069464 | -60.9467 | 61.8668 | -60.8688 | -61.0611 | 61.8301 | 0.09613 | 0.07782 | 0.064087 | 61.8576 | -60.997 | 0.022889 | -0.10529 | -0.054931 | -0.16937 | -0.14191 | -0.10528 | -0.11444 | -0.07782 | 60.9695 | 60.9558 | 122.7219 | 122.7585 | -0.054931 | 122.7493 | 60.9879 | -0.10528 | 122.7585 | -0.054931 | 60.9879 | 122.7219 | 122.7493 | -122.8409 | -122.9691
89.3281 | 123.0698 | -60.878 | 61.9675 | 0.0035097 | 0.020078 | 0.014875 | 0.0044562 | 0.06652 | -0.0021383 | 0.070318 | -60.9421 | 61.8942 | -60.9055 | -61.0657 | 61.8164 | 0.10071 | 0.036621 | 0.041199 | 61.8576 | -61.0107 | -0.027466 | -0.073242 | -0.064087 | -0.18768 | -0.15106 | -0.13275 | -0.10986 | -0.036621 | 60.9146 | 60.9192 | 122.6944 | 122.7722 | -0.064087 | 122.7356 | 60.9787 | -0.13275 | 122.7722 | -0.064087 | 60.9787 | 122.6944 | 122.7356 | -122.8729 | -122.9782
90.3281 | 123.0606 | -60.8688 | 61.9812 | -0.065155 | 0.019438 | 0.014234 | 0.0012518 | 0.066093 | -0.0010703 | 0.069464 | -60.9375 | 61.8988 | -60.8871 | -61.0519 | 61.821 | 0.10071 | 0.041199 | 0.041199 | 61.8759 | -61.0016 | -0.018311 | -0.082397 | -0.068665 | -0.18311 | -0.16022 | -0.13275 | -0.10529 | -0.050354 | 60.91 | 60.91 | 122.6898 | 122.7676 | -0.068665 | 122.7448 | 60.9695 | -0.13275 | 122.7676 | -0.068665 | 60.9695 | 122.6898 | 122.7448 | -122.8683 | -122.9828
91.3281 | 123.1064 | -60.8643 | 61.9766 | -0.027008 | 0.019438 | 0.017652 | 0.0044562 | 0.06652 | -0.00085669 | 0.072455 | -60.9512 | 61.8759 | -60.8871 | -61.0474 | 61.8256 | 0.10986 | 0.064087 | 0.032043 | 61.8851 | -61.0107 | -0.022888 | -0.10071 | -0.086975 | -0.1831 | -0.15106 | -0.14648 | -0.091553 | -0.064087 | 60.9283 | 60.8963 | 122.6898 | 122.7402 | -0.086975 | 122.7493 | 60.9741 | -0.14648 | 122.7402 | -0.086975 | 60.9741 | 122.6898 | 122.7493 | -122.8638 | -122.9874
92.3281 | 123.111 | -60.8688 | 61.972 | -0.69839 | 0.020933 | 0.015302 | 0.0031744 | 0.067161 | -0.0010703 | 0.069037 | -60.997 | 61.908 | -60.8688 | -61.0382 | 61.8256 | 0.10071 | 0.073242 | 0.059509 | 61.8805 | -61.0016 | 0 | -0.064087 | -0.12817 | -0.16937 | -0.14648 | -0.13275 | -0.091553 | -0.12817 | 60.9421 | 60.9283 | 122.6944 | 122.7768 | -0.12817 | 122.7493 | 60.9695 | -0.13275 | 122.7768 | -0.12817 | 60.9695 | 122.6944 | 122.7493 | -122.8409 | -122.9736
93.3281 | 123.0743 | -60.8734 | 62.0087 | -0.11093 | 0.019865 | 0.014875 | -0.00024361 | 0.067588 | -0.0044883 | 0.06925 | -61.0062 | 61.8942 | -60.8871 | -61.0886 | 61.7798 | 0.082397 | 0.15106 | 0.050354 | 61.8988 | -60.9879 | -0.013733 | -0.11444 | -0.13275 | -0.21515 | -0.22888 | -0.11444 | -0.10986 | -0.11902 | 61.0245 | 60.9238 | 122.6532 | 122.7676 | -0.13275 | 122.7722 | 60.9558 | -0.11444 | 122.7676 | -0.13275 | 60.9558 | 122.6532 | 122.7722 | -122.8958 | -122.9965
94.3281 | 123.0423 | -60.8688 | 62.0178 | -0.16434 | 0.022215 | 0.016156 | 0.00018379 | 0.065238 | -0.0019247 | 0.06925 | -60.997 | 61.9354 | -60.8871 | -61.0886 | 61.7889 | 0.07782 | 0.15106 | 0.027466 | 61.8988 | -61.0291 | -0.018311 | -0.082397 | -0.12817 | -0.21973 | -0.22888 | -0.16022 | -0.11902 | -0.10986 | 61.0199 | 60.8963 | 122.6578 | 122.8043 | -0.12817 | 122.7676 | 60.9467 | -0.16022 | 122.8043 | -0.12817 | 60.9467 | 122.6578 | 122.7676 | -122.905 | -123.0469
95.3281 | 123.0515 | -60.8688 | 61.9812 | -0.14908 | 0.019651 | 0.017011 | 0.00232 | 0.068015 | -0.0023519 | 0.070105 | -60.9604 | 61.8759 | -60.8871 | -61.0382 | 61.821 | 0.10071 | 0.09613 | 0.064087 | 61.8942 | -61.0107 | -0.018311 | -0.10529 | -0.091553 | -0.16937 | -0.16022 | -0.14191 | -0.086975 | -0.073242 | 60.965 | 60.9329 | 122.6898 | 122.7448 | -0.091553 | 122.7631 | 60.9695 | -0.14191 | 122.7448 | -0.091553 | 60.9695 | 122.6898 | 122.7631 | -122.8683 | -122.9919
96.3281 | 123.0972 | -60.8826 | 61.9904 | 1.8575 | 0.022001 | 0.013593 | 0.0046698 | 0.067161 | -0.0012839 | 0.069037 | -60.7407 | 61.8851 | -60.8826 | -61.0428 | 61.8347 | 0.12817 | 0.073242 | 0.07782 | 61.8896 | -61.0062 | 0 | -0.10528 | 0.14191 | -0.16022 | -0.15564 | -0.1236 | -0.10071 | 0.14191 | 60.9558 | 60.9604 | 122.7173 | 122.7676 | 0.14191 | 122.7722 | 61.0107 | -0.1236 | 122.7676 | 0.14191 | 61.0107 | 122.7173 | 122.7722 | -122.8729 | -122.9965
97.3281 | 123.1018 | -60.8688 | 61.9858 | -0.1033 | 0.019651 | 0.017652 | 0.0042426 | 0.066947 | 0.0019205 | 0.071386 | -60.9604 | 61.8942 | -60.8734 | -61.1755 | 62.027 | 0.20599 | 0.059509 | 0.13275 | 61.8942 | -61.0382 | -0.004578 | -0.091553 | -0.091553 | -0.3067 | 0.041199 | -0.16937 | -0.091553 | -0.086975 | 60.9283 | 61.0016 | 122.8958 | 122.7631 | -0.091553 | 122.7631 | 61.0748 | -0.16937 | 122.7631 | -0.091553 | 61.0748 | 122.8958 | 122.7631 | -122.8592 | -123.024
98.3281 | 123.0698 | -60.8643 | 62.0132 | -0.16434 | 0.020078 | 0.015302 | 0.00082459 | 0.067375 | -0.0027793 | 0.070532 | -60.9924 | 61.908 | -60.8963 | -61.0886 | 61.7798 | 0.068665 | 0.16479 | 0.036621 | 61.8851 | -60.9924 | -0.032043 | -0.10529 | -0.12817 | -0.2243 | -0.23346 | -0.12817 | -0.12817 | -0.096131 | 61.0291 | 60.9009 | 122.644 | 122.7722 | -0.12817 | 122.7493 | 60.9329 | -0.12817 | 122.7722 | -0.12817 | 60.9329 | 122.644 | 122.7493 | -122.9095 | -123.0057
99.3281 | 123.0743 | -60.8826 | 61.9949 | -0.072784 | 0.021147 | 0.018933 | 0.00232 | 0.064811 | -0.0023519 | 0.070105 | -60.9558 | 61.9125 | -60.8963 | -61.0474 | 61.8301 | 0.09613 | 0.086975 | 0.054932 | 61.8622 | -61.0382 | -0.013733 | -0.082397 | -0.073243 | -0.16479 | -0.16479 | -0.15564 | -0.13275 | -0.05951 | 60.9695 | 60.9375 | 122.7127 | 122.7951 | -0.073243 | 122.7448 | 60.9787 | -0.15564 | 122.7951 | -0.073243 | 60.9787 | 122.7127 | 122.7448 | -122.8912 | -123.0331
100.3281 | 123.0469 | -60.8871 | 62.0041 | -0.19485 | 0.01837 | 0.020429 | -0.00024361 | 0.06652 | -0.0040609 | 0.070105 | -60.9879 | 61.8988 | -60.8826 | -61.0931 | 61.7798 | 0.086975 | 0.15564 | 0.032043 | 61.8851 | -61.0016 | 0.004578 | -0.10529 | -0.10071 | -0.20599 | -0.2243 | -0.11444 | -0.11902 | -0.10529 | 61.0428 | 60.9192 | 122.6669 | 122.7859 | -0.10071 | 122.7722 | 60.9741 | -0.11444 | 122.7859 | -0.10071 | 60.9741 | 122.6669 | 122.7722 | -122.8867 | -123.0057
101.3281 | 123.0423 | -60.878 | 61.9858 | -0.11093 | 0.020292 | 0.017438 | 0.0010382 | 0.066093 | -2.092e-06 | 0.06925 | -60.997 | 61.9034 | -60.8963 | -61.0657 | 61.7935 | 0.082397 | 0.10986 | 0.054932 | 61.8942 | -61.0107 | -0.01831 | -0.082398 | -0.11902 | -0.18768 | -0.19226 | -0.13275 | -0.091553 | -0.10071 | 60.9879 | 60.9329 | 122.6715 | 122.7814 | -0.11902 | 122.7722 | 60.9604 | -0.13275 | 122.7814 | -0.11902 | 60.9604 | 122.6715 | 122.7722 | -122.8821 | -122.9965
102.3281 | 123.0698 | -60.8826 | 61.9812 | -0.16434 | 0.020078 | 0.017224 | -0.00024361 | 0.065452 | -0.0010703 | 0.070105 | -60.9879 | 61.8851 | -60.8734 | -61.0748 | 61.8027 | 0.09613 | 0.13275 | 0.045776 | 61.8805 | -60.997 | 0.009155 | -0.09613 | -0.10529 | -0.19226 | -0.17853 | -0.11444 | -0.10071 | -0.11444 | 61.0153 | 60.9283 | 122.6852 | 122.7676 | -0.10529 | 122.7631 | 60.9787 | -0.11444 | 122.7676 | -0.10529 | 60.9787 | 122.6852 | 122.7631 | -122.8546 | -122.9782
103.3281 | 123.0789 | -60.8826 | 61.9812 | -0.1033 | 0.021574 | 0.016156 | 0.0010382 | 0.066093 | -0.00042929 | 0.070532 | -60.9375 | 61.9125 | -60.8826 | -61.0611 | 61.821 | 0.10071 | 0.073242 | 0.073242 | 61.8713 | -61.0153 | 0 | -0.068664 | -0.054932 | -0.17853 | -0.16022 | -0.13275 | -0.10986 | -0.054932 | 60.9558 | 60.9558 | 122.7036 | 122.7951 | -0.054932 | 122.7539 | 60.9833 | -0.13275 | 122.7951 | -0.054932 | 60.9833 | 122.7036 | 122.7539 | -122.8638 | -122.9965
104.3281 | 123.0652 | -60.8643 | 61.9949 | -0.12619 | 0.017729 | 0.017865 | 0.0021064 | 0.068229 | -0.0034201 | 0.070532 | -60.9741 | 61.9171 | -60.8917 | -61.0474 | 61.8027 | 0.09613 | 0.091553 | 0.059509 | 61.8851 | -60.9787 | -0.027466 | -0.07782 | -0.10986 | -0.1831 | -0.19226 | -0.11444 | -0.10986 | -0.082397 | 60.9558 | 60.9238 | 122.6669 | 122.7814 | -0.10986 | 122.7493 | 60.9604 | -0.11444 | 122.7814 | -0.10986 | 60.9604 | 122.6669 | 122.7493 | -122.8867 | -122.9736
105.3281 | 123.0652 | -60.878 | 61.9904 | -0.16434 | 0.020933 | 0.018079 | 0.0036018 | 0.065452 | -0.00085669 | 0.068396 | -60.9741 | 61.9034 | -60.8871 | -61.0703 | 61.8027 | 0.07782 | 0.11902 | 0.064087 | 61.8759 | -60.9879 | -0.009155 | -0.086975 | -0.09613 | -0.19226 | -0.18768 | -0.10986 | -0.11444 | -0.086975 | 60.997 | 60.9421 | 122.6807 | 122.7814 | -0.09613 | 122.7539 | 60.9558 | -0.10986 | 122.7814 | -0.09613 | 60.9558 | 122.6807 | 122.7539 | -122.8775 | -122.9782
106.3281 | 123.0331 | -60.8826 | 62.027 | -0.088043 | 0.017729 | 0.014661 | 0.003388 | 0.065025 | -0.0027793 | 0.072027 | -60.9833 | 61.8896 | -60.8734 | -61.0931 | 61.7844 | 0.073242 | 0.14648 | 0.050354 | 61.8988 | -60.9879 | 0.009155 | -0.13733 | -0.10071 | -0.21057 | -0.24262 | -0.10529 | -0.12817 | -0.10986 | 61.0291 | 60.9329 | 122.6669 | 122.7722 | -0.10071 | 122.7814 | 60.9558 | -0.10529 | 122.7722 | -0.10071 | 60.9558 | 122.6669 | 122.7814 | -122.9004 | -123.0148
107.3281 | 123.0103 | -60.8826 | 61.9949 | -0.20248 | 0.020506 | 0.017438 | -2.9814e-05 | 0.064384 | -0.0027793 | 0.070318 | -61.1389 | 61.8988 | -60.8734 | -61.1572 | 61.7523 | 0.10986 | 0.16479 | 0.013733 | 61.8896 | -61.0245 | 0.009155 | -0.09613 | -0.25635 | -0.27466 | -0.24262 | -0.14191 | -0.10529 | -0.2655 | 61.0474 | 60.8963 | 122.6349 | 122.7814 | -0.25635 | 122.7722 | 60.9924 | -0.14191 | 122.7814 | -0.25635 | 60.9924 | 122.6349 | 122.7722 | -122.8683 | -123.0194
108.3281 | 123.0377 | -60.9055 | 61.9995 | -0.15671 | 0.020506 | 0.012952 | 0.0016792 | 0.06417 | -0.0021383 | 0.067755 | -61.0199 | 61.8988 | -60.878 | -61.1023 | 61.7844 | 0.073242 | 0.16479 | 0.036621 | 61.8896 | -60.997 | 0.027466 | -0.10071 | -0.11444 | -0.19684 | -0.21515 | -0.091552 | -0.10986 | -0.14191 | 61.0703 | 60.9421 | 122.6898 | 122.8043 | -0.11444 | 122.7951 | 60.9787 | -0.091552 | 122.8043 | -0.11444 | 60.9787 | 122.6898 | 122.7951 | -122.8775 | -122.9965
109.3281 | 123.024 | -60.8734 | 61.9858 | -0.11093 | 0.018797 | 0.012525 | -0.00045721 | 0.062889 | -0.0019247 | 0.071173 | -61.0199 | 61.8805 | -60.8963 | -61.0886 | 61.7798 | 0.059509 | 0.16022 | 0.041199 | 61.8896 | -60.9924 | -0.022888 | -0.10529 | -0.14648 | -0.21515 | -0.20599 | -0.11902 | -0.096131 | -0.1236 | 61.0336 | 60.9146 | 122.6532 | 122.7539 | -0.14648 | 122.7631 | 60.9329 | -0.11902 | 122.7539 | -0.14648 | 60.9329 | 122.6532 | 122.7631 | -122.8821 | -122.9782
110.3281 | 123.0515 | -60.8688 | 62.0087 | -0.14908 | 0.020292 | 0.019788 | 0.0014654 | 0.065666 | -0.0044883 | 0.070746 | -60.9924 | 61.8668 | -60.8734 | -61.0977 | 61.7752 | 0.064087 | 0.15564 | 0.032043 | 61.9263 | -61.0107 | -0.004578 | -0.14191 | -0.1236 | -0.22888 | -0.23346 | -0.14191 | -0.082397 | -0.11902 | 61.0245 | 60.9009 | 122.644 | 122.7356 | -0.1236 | 122.7951 | 60.9329 | -0.14191 | 122.7356 | -0.1236 | 60.9329 | 122.644 | 122.7951 | -122.8821 | -123.0194
111.3281 | 123.0377 | -60.878 | 61.9995 | -0.13382 | 0.018583 | 0.016797 | 0.00082459 | 0.065238 | -0.0025657 | 0.070532 | -60.9879 | 61.8896 | -60.8917 | -61.1069 | 61.7661 | 0.073242 | 0.16022 | 0.041199 | 61.8896 | -61.0107 | -0.013733 | -0.10986 | -0.10986 | -0.22888 | -0.23346 | -0.13275 | -0.10986 | -0.09613 | 61.0382 | 60.9192 | 122.644 | 122.7676 | -0.10986 | 122.7676 | 60.9512 | -0.13275 | 122.7676 | -0.10986 | 60.9512 | 122.644 | 122.7676 | -122.8912 | -123.0103
112.3281 | 123.0103 | -60.8871 | 62.0041 | 0.018768 | 0.017515 | 0.011029 | 0.00018379 | 0.064811 | -0.0027793 | 0.069891 | -61.0016 | 61.853 | -60.8871 | -61.0886 | 61.7615 | 0.07782 | 0.16479 | 0.041199 | 61.8988 | -60.9924 | 0 | -0.15106 | -0.11444 | -0.20142 | -0.24261 | -0.10529 | -0.10529 | -0.11444 | 61.0519 | 60.9283 | 122.6486 | 122.7402 | -0.11444 | 122.7859 | 60.965 | -0.10529 | 122.7402 | -0.11444 | 60.965 | 122.6486 | 122.7859 | -122.8912 | -122.9965
113.3281 | 123.0698 | -60.8459 | 61.972 | -0.1796 | 0.019224 | 0.015088 | -0.00088441 | 0.063102 | -0.0017111 | 0.071173 | -60.9375 | 61.8347 | -60.8459 | -61.0382 | 61.8484 | 0.13733 | 0.091553 | 0.10986 | 61.8622 | -60.965 | 0 | -0.13733 | -0.091553 | -0.19226 | -0.1236 | -0.11902 | -0.10986 | -0.091553 | 60.9375 | 60.9558 | 122.6944 | 122.6807 | -0.091553 | 122.7081 | 60.9833 | -0.11902 | 122.6807 | -0.091553 | 60.9833 | 122.6944 | 122.7081 | -122.818 | -122.937
114.3281 | 123.1201 | -60.8368 | 61.9766 | -0.14908 | 0.013883 | 0.012952 | -0.0013116 | 0.065025 | -0.0038473 | 0.068609 | -60.9146 | 61.8073 | -60.8551 | -61.0016 | 61.8668 | 0.16022 | 0.059509 | 0.15564 | 61.8622 | -60.9604 | -0.018311 | -0.16937 | -0.07782 | -0.16479 | -0.10986 | -0.1236 | -0.11444 | -0.059509 | 60.8963 | 60.9924 | 122.7036 | 122.644 | -0.07782 | 122.699 | 60.997 | -0.1236 | 122.644 | -0.07782 | 60.997 | 122.7036 | 122.699 | -122.8317 | -122.937
115.3281 | 123.0286 | -60.8826 | 62.0178 | -0.20248 | 0.019651 | 0.018933 | -2.9814e-05 | 0.063102 | -0.0027793 | 0.06925 | -60.8734 | 61.8484 | -60.878 | -61.0153 | 61.8256 | 0.20599 | 0.15106 | 0.07782 | 61.8713 | -60.9604 | 0.004577 | -0.16937 | 0.009155 | -0.13275 | -0.19226 | -0.07782 | -0.14648 | 0.004578 | 61.0336 | 60.9604 | 122.7081 | 122.731 | 0.009155 | 122.7539 | 61.0886 | -0.07782 | 122.731 | 0.009155 | 61.0886 | 122.7081 | 122.7539 | -122.8958 | -122.9782
116.3281 | 123.0972 | -60.8231 | 61.9812 | -0.20248 | 0.01901 | 0.013593 | 0.00061099 | 0.062889 | -0.0029929 | 0.070105 | -60.91 | 61.7981 | -60.8643 | -61.0062 | 61.8805 | 0.15106 | 0.1236 | 0.16937 | 61.8805 | -60.9741 | -0.041199 | -0.1831 | -0.086975 | -0.18311 | -0.10071 | -0.15106 | -0.10071 | -0.045776 | 60.9467 | 60.9924 | 122.7036 | 122.6212 | -0.086975 | 122.7036 | 60.9741 | -0.15106 | 122.6212 | -0.086975 | 60.9741 | 122.7036 | 122.7036 | -122.8455 | -122.9553
117.3281 | 123.0194 | -60.8871 | 61.9812 | -0.15671 | 0.017088 | 0.015088 | 0.00039739 | 0.064384 | -0.0061973 | 0.070318 | -60.9787 | 61.8576 | -60.878 | -60.9421 | 61.5875 | -0.10071 | 0.19226 | 0.032043 | 61.8942 | -60.9741 | 0.009155 | -0.1236 | -0.091553 | -0.054932 | -0.39368 | -0.086975 | -0.086975 | -0.10071 | 61.0794 | 60.9192 | 122.4747 | 122.7448 | -0.091553 | 122.7814 | 60.7864 | -0.086975 | 122.7448 | -0.091553 | 60.7864 | 122.4747 | 122.7814 | -122.8592 | -122.9553
118.3281 | 122.9553 | -60.8826 | 62.0636 | -0.21011 | 0.01901 | 0.018293 | 0.00061099 | 0.06417 | -0.0027793 | 0.071173 | -60.9695 | 61.8256 | -60.8505 | -61.0565 | 61.821 | 0.11902 | 0.15106 | 0.059509 | 61.9034 | -60.965 | 0.032043 | -0.23804 | -0.086975 | -0.17395 | -0.24262 | -0.082398 | -0.16022 | -0.11902 | 61.0336 | 60.9421 | 122.7036 | 122.7081 | -0.086975 | 122.7859 | 61.0016 | -0.082398 | 122.7081 | -0.086975 | 61.0016 | 122.7036 | 122.7859 | -122.9141 | -123.0286
119.3281 | 123.0743 | -60.8734 | 62.0132 | -0.19485 | 0.017729 | 0.013379 | -2.9814e-05 | 0.063316 | -0.0032065 | 0.068609 | -60.9467 | 61.8393 | -60.8551 | -61.0336 | 61.8027 | 0.12817 | 0.12817 | 0.082397 | 61.8484 | -60.9695 | 0.01831 | -0.17395 | -0.073242 | -0.16022 | -0.21057 | -0.09613 | -0.16479 | -0.091552 | 61.0016 | 60.9558 | 122.6761 | 122.7127 | -0.073242 | 122.7219 | 61.0016 | -0.09613 | 122.7127 | -0.073242 | 61.0016 | 122.6761 | 122.7219 | -122.8683 | -122.9828
120.3281 | 123.0743 | -60.8505 | 61.9904 | -0.1796 | 0.017515 | 0.01167 | 0.00232 | 0.063743 | -0.0023519 | 0.070318 | -60.9329 | 61.8118 | -60.8551 | -61.0153 | 61.8347 | 0.14191 | 0.082397 | 0.11902 | 61.8668 | -60.965 | -0.004578 | -0.17853 | -0.082397 | -0.1648 | -0.15564 | -0.11444 | -0.1236 | -0.077819 | 60.9329 | 60.9695 | 122.6852 | 122.6624 | -0.082397 | 122.7173 | 60.9924 | -0.11444 | 122.6624 | -0.082397 | 60.9924 | 122.6852 | 122.7173 | -122.8455 | -122.9553
121.3281 | 123.1384 | -60.8459 | 61.9812 | -0.14908 | 0.019865 | 0.015515 | 0.0010382 | 0.063316 | -0.0049155 | 0.069677 | -60.9238 | 61.7752 | -60.8505 | -60.9833 | 61.8988 | 0.1831 | -0.032043 | 0.16022 | 61.821 | -60.9558 | -0.004578 | -0.20599 | -0.07782 | -0.13733 | -0.082397 | -0.10986 | -0.16022 | -0.073242 | 60.8139 | 61.0062 | 122.7448 | 122.6212 | -0.07782 | 122.6669 | 61.0291 | -0.10986 | 122.6212 | -0.07782 | 61.0291 | 122.7448 | 122.6669 | -122.8317 | -122.937
122.3281 | 123.1018 | -60.8368 | 62.0178 | -0.16434 | 0.017515 | 0.013166 | -0.00024361 | 0.061607 | -0.0032065 | 0.070746 | -60.9238 | 61.8073 | -60.8551 | -60.9924 | 61.8622 | 0.15564 | 0.027466 | 0.15564 | 61.8256 | -60.965 | -0.018311 | -0.21057 | -0.086975 | -0.15564 | -0.15564 | -0.12817 | -0.19226 | -0.068664 | 60.8643 | 60.9924 | 122.699 | 122.644 | -0.086975 | 122.6624 | 60.9924 | -0.12817 | 122.644 | -0.086975 | 60.9924 | 122.699 | 122.6624 | -122.8729 | -122.9828
123.3281 | 123.1201 | -60.8322 | 61.9675 | -0.14145 | 0.016661 | 0.017438 | 0.00232 | 0.062034 | -0.0021383 | 0.068823 | -60.9283 | 61.7706 | -60.8505 | -60.9833 | 61.8668 | 0.16479 | 0.027466 | 0.14648 | 61.8393 | -60.9421 | -0.018311 | -0.19684 | -0.096131 | -0.15106 | -0.10071 | -0.10986 | -0.12817 | -0.07782 | 60.8597 | 60.9787 | 122.699 | 122.6028 | -0.096131 | 122.6715 | 60.997 | -0.10986 | 122.6028 | -0.096131 | 60.997 | 122.699 | 122.6715 | -122.818 | -122.9095
124.3281 | 123.0469 | -60.8551 | 61.9995 | -0.21011 | 0.017088 | 0.019147 | 0.00232 | 0.06182 | -0.0032065 | 0.068823 | -60.9467 | 61.8027 | -60.878 | -61.0245 | 61.8256 | 0.11902 | 0.11444 | 0.091553 | 61.8896 | -60.9879 | -0.022888 | -0.19684 | -0.091552 | -0.16937 | -0.17395 | -0.13275 | -0.10986 | -0.068664 | 60.9695 | 60.9467 | 122.6807 | 122.6578 | -0.091552 | 122.7448 | 60.9741 | -0.13275 | 122.6578 | -0.091552 | 60.9741 | 122.6807 | 122.7448 | -122.8775 | -122.9874
125.3281 | 123.2025 | -60.8414 | 61.9995 | -0.1796 | 0.019865 | 0.016584 | 0.0031744 | 0.06182 | -0.0025657 | 0.071386 | -60.9512 | 61.821 | -60.8688 | -60.8826 | 62.1872 | 0.21515 | 0.10071 | 0.16937 | 61.8622 | -60.965 | -0.027465 | -0.17853 | -0.10986 | -0.041198 | 0.18768 | -0.1236 | -0.13733 | -0.082398 | 60.9421 | 61.0107 | 123.0286 | 122.6624 | -0.10986 | 122.7036 | 61.0565 | -0.1236 | 122.6624 | -0.10986 | 61.0565 | 123.0286 | 122.7036 | -122.8683 | -122.9645
126.3281 | 123.2712 | -60.8459 | 61.9949 | -0.15671 | 0.020506 | 0.015729 | 0.003388 | 0.063957 | -0.0034201 | 0.069037 | -60.9375 | 61.8118 | -60.8551 | -60.8871 | 62.1414 | 0.20142 | 0.10986 | 0.20142 | 61.8301 | -60.9879 | -0.009156 | -0.1831 | -0.091553 | -0.041199 | 0.14648 | -0.14191 | -0.16479 | -0.082397 | 60.9558 | 61.0474 | 122.9874 | 122.6578 | -0.091553 | 122.6761 | 61.0474 | -0.14191 | 122.6578 | -0.091553 | 61.0474 | 122.9874 | 122.6761 | -122.85 | -122.9828
127.3281 | 123.1293 | -60.8551 | 61.9904 | -0.17197 | 0.016447 | 0.012097 | 0.0038154 | 0.063102 | -0.0064109 | 0.070959 | -60.9329 | 61.7844 | -60.8688 | -60.9329 | 62.1185 | 0.2243 | 0.082397 | 0.16479 | 61.8484 | -60.9375 | -0.013732 | -0.20599 | -0.077819 | -0.077819 | 0.12817 | -0.082397 | -0.14191 | -0.064087 | 60.9375 | 61.0199 | 122.9736 | 122.6395 | -0.077819 | 122.7036 | 61.0794 | -0.082397 | 122.6395 | -0.077819 | 61.0794 | 122.9736 | 122.7036 | -122.8592 | -122.9279
128.3281 | 123.143 | -60.8231 | 61.9766 | -0.034637 | 0.015592 | 0.010816 | 0.0012518 | 0.063529 | -0.0021383 | 0.070105 | -60.9055 | 61.7981 | -60.8368 | -60.9741 | 61.9263 | 0.20142 | -0.009155 | 0.16937 | 61.8073 | -60.9512 | -0.013733 | -0.17853 | -0.082398 | -0.15106 | -0.050354 | -0.12817 | -0.16937 | -0.068665 | 60.8139 | 60.9924 | 122.7493 | 122.6212 | -0.082398 | 122.6303 | 61.0245 | -0.12817 | 122.6212 | -0.082398 | 61.0245 | 122.7493 | 122.6303 | -122.8134 | -122.9279
129.3281 | 123.2025 | -60.8231 | 61.9675 | -0.1796 | 0.019438 | 0.012097 | 0.0029608 | 0.061393 | -0.0044883 | 0.070532 | -60.8871 | 61.8118 | -60.8597 | -60.9558 | 61.9583 | 0.19226 | 0.041199 | 0.15106 | 61.8256 | -60.9467 | -0.036621 | -0.15564 | -0.064087 | -0.13275 | -0.009155 | -0.1236 | -0.14191 | -0.027466 | 60.8643 | 60.9741 | 122.7814 | 122.6349 | -0.064087 | 122.6486 | 61.0153 | -0.1236 | 122.6349 | -0.064087 | 61.0153 | 122.7814 | 122.6486 | -122.8271 | -122.9141
130.3281 | 123.2025 | -60.8368 | 61.9675 | -0.11856 | 0.017515 | 0.0099612 | 0.004029 | 0.060966 | -0.0044883 | 0.067755 | -60.878 | 61.7889 | -60.8688 | -60.9604 | 61.9263 | 0.1831 | 0 | 0.15564 | 61.8073 | -60.9558 | -0.032043 | -0.17853 | -0.041199 | -0.1236 | -0.041198 | -0.11902 | -0.16022 | -0.009156 | 60.8368 | 60.9924 | 122.7631 | 122.6257 | -0.041199 | 122.644 | 61.0199 | -0.11902 | 122.6257 | -0.041199 | 61.0199 | 122.7631 | 122.644 | -122.8363 | -122.9233
131.3281 | 123.0469 | -60.8597 | 61.9949 | -0.18723 | 0.015592 | 0.015302 | 0.003388 | 0.062248 | -0.0027793 | 0.06925 | -60.9467 | 61.8301 | -60.8643 | -61.0291 | 61.8439 | 0.12817 | 0.11902 | 0.10529 | 61.8622 | -60.9512 | -0.004578 | -0.16479 | -0.086975 | -0.16937 | -0.15106 | -0.091553 | -0.13275 | -0.082397 | 60.9787 | 60.965 | 122.7036 | 122.6898 | -0.086975 | 122.7219 | 60.9879 | -0.091553 | 122.6898 | -0.086975 | 60.9879 | 122.7036 | 122.7219 | -122.8592 | -122.9462
132.3281 | 123.0789 | -60.8459 | 61.9812 | -0.16434 | 0.016874 | 0.016156 | 0.00232 | 0.062461 | -0.0034201 | 0.068609 | -60.9329 | 61.8118 | -60.8597 | -61.0016 | 61.8439 | 0.15564 | 0.073242 | 0.12817 | 61.853 | -60.9695 | -0.013733 | -0.16937 | -0.086975 | -0.15564 | -0.13733 | -0.1236 | -0.12817 | -0.073242 | 60.9192 | 60.9741 | 122.6898 | 122.6578 | -0.086975 | 122.699 | 61.0016 | -0.1236 | 122.6578 | -0.086975 | 61.0016 | 122.6898 | 122.699 | -122.8409 | -122.9507
133.3281 | 123.0972 | -60.8414 | 61.9904 | -0.19485 | 0.017301 | 0.018506 | 0.0027472 | 0.060325 | -0.00085669 | 0.070746 | -60.9238 | 61.8164 | -60.8688 | -60.997 | 61.8622 | 0.16022 | 0.068665 | 0.13733 | 61.8256 | -60.9558 | -0.027465 | -0.17395 | -0.082397 | -0.15564 | -0.12817 | -0.11444 | -0.16479 | -0.054932 | 60.91 | 60.9787 | 122.7036 | 122.6578 | -0.082397 | 122.6669 | 61.0016 | -0.11444 | 122.6578 | -0.082397 | 61.0016 | 122.7036 | 122.6669 | -122.8592 | -122.9462
134.3281 | 123.1476 | -60.8322 | 61.9766 | -0.1033 | 0.018583 | 0.018079 | -2.9814e-05 | 0.060966 | -0.0044883 | 0.069037 | -60.9055 | 61.7706 | -60.8414 | -60.9512 | 61.9034 | 0.17395 | -0.018311 | 0.16022 | 61.8484 | -60.9467 | -0.009156 | -0.20599 | -0.073243 | -0.11902 | -0.073243 | -0.11444 | -0.12817 | -0.064087 | 60.8139 | 60.9924 | 122.7356 | 122.6028 | -0.073243 | 122.6807 | 61.0062 | -0.11444 | 122.6028 | -0.073243 | 61.0062 | 122.7356 | 122.6807 | -122.818 | -122.9233
135.3281 | 123.1476 | -60.8276 | 61.9583 | -0.40848 | 0.017729 | 0.015088 | 0.00061099 | 0.062461 | -0.0025657 | 0.068396 | -60.91 | 61.7889 | -60.8643 | -60.9695 | 61.8942 | 0.19226 | -0.027466 | 0.17395 | 61.8347 | -60.9558 | -0.036621 | -0.16937 | -0.082397 | -0.14191 | -0.064087 | -0.12817 | -0.1236 | -0.045776 | 60.8002 | 61.0016 | 122.7219 | 122.6166 | -0.082397 | 122.6624 | 61.0199 | -0.12817 | 122.6166 | -0.082397 | 61.0199 | 122.7219 | 122.6624 | -122.8226 | -122.9141
136.3281 | 123.1247 | -60.8185 | 61.972 | -0.1796 | 0.018583 | 0.013166 | 0.0010382 | 0.063957 | -0.0057699 | 0.067969 | -60.9146 | 61.8073 | -60.8368 | -60.9695 | 61.8851 | 0.16937 | 0.027466 | 0.13733 | 61.8301 | -60.9512 | -0.018311 | -0.16479 | -0.096131 | -0.15106 | -0.086975 | -0.13275 | -0.14191 | -0.07782 | 60.8459 | 60.9558 | 122.7036 | 122.6257 | -0.096131 | 122.6486 | 60.9879 | -0.13275 | 122.6257 | -0.096131 | 60.9879 | 122.7036 | 122.6486 | -122.8088 | -122.9233
137.3281 | 123.0286 | -60.8643 | 61.9995 | -0.1796 | 0.018797 | 0.016797 | 0.003388 | 0.063102 | -0.0049155 | 0.06925 | -60.9467 | 61.821 | -60.8597 | -61.0428 | 61.7981 | 0.11902 | 0.13275 | 0.09613 | 61.8896 | -60.9467 | 0.004578 | -0.17853 | -0.082397 | -0.17853 | -0.20142 | -0.082397 | -0.10986 | -0.086975 | 60.997 | 60.9604 | 122.6624 | 122.6852 | -0.082397 | 122.7539 | 60.9833 | -0.082397 | 122.6852 | -0.082397 | 60.9833 | 122.6624 | 122.7539 | -122.8592 | -122.9462
138.3281 | 123.0377 | -60.8597 | 61.9995 | -0.19485 | 0.01901 | 0.015729 | 0.0027472 | 0.062034 | -0.0053427 | 0.070746 | -60.9604 | 61.8347 | -60.8414 | -61.0199 | 61.7981 | 0.11902 | 0.13275 | 0.068665 | 61.8896 | -60.9375 | 0.01831 | -0.1648 | -0.10071 | -0.16022 | -0.20142 | -0.07782 | -0.10986 | -0.11902 | 60.9924 | 60.9283 | 122.6578 | 122.6944 | -0.10071 | 122.7493 | 60.9787 | -0.07782 | 122.6944 | -0.10071 | 60.9787 | 122.6578 | 122.7493 | -122.8409 | -122.937
139.3281 | 123.0469 | -60.8551 | 62.027 | -0.20248 | 0.019224 | 0.014447 | 0.0027472 | 0.063316 | -0.0040609 | 0.072241 | -60.9467 | 61.8164 | -60.878 | -61.0107 | 61.821 | 0.11902 | 0.10986 | 0.086975 | 61.8942 | -60.9604 | -0.022888 | -0.21057 | -0.091552 | -0.15564 | -0.20599 | -0.10529 | -0.13275 | -0.068664 | 60.965 | 60.9421 | 122.6761 | 122.6715 | -0.091552 | 122.7493 | 60.9741 | -0.10529 | 122.6715 | -0.091552 | 60.9741 | 122.6761 | 122.7493 | -122.905 | -122.9874
140.3281 | 123.024 | -60.8551 | 61.9766 | -0.21011 | 0.017515 | 0.012525 | 0.0031744 | 0.064598 | -0.0025657 | 0.068609 | -60.9375 | 61.8301 | -60.8688 | -61.0199 | 61.8393 | 0.11444 | 0.14191 | 0.082397 | 61.8622 | -60.9695 | -0.013732 | -0.14648 | -0.082397 | -0.16479 | -0.13733 | -0.11444 | -0.11444 | -0.068665 | 60.997 | 60.9375 | 122.6944 | 122.6852 | -0.082397 | 122.7173 | 60.9695 | -0.11444 | 122.6852 | -0.082397 | 60.9695 | 122.6944 | 122.7173 | -122.8455 | -122.9462
141.3281 | 123.1293 | -60.8322 | 61.9675 | -0.13382 | 0.018156 | 0.011457 | 0.0021064 | 0.063529 | -0.0036337 | 0.06925 | -60.9009 | 61.7844 | -60.9009 | -60.9695 | 61.8988 | 0.1831 | 0.009155 | 0.16937 | 61.8301 | -60.9329 | -0.068665 | -0.1831 | -0.068665 | -0.13733 | -0.068664 | -0.10071 | -0.13733 | 0 | 60.8414 | 61.0016 | 122.731 | 122.6166 | -0.068665 | 122.6624 | 61.0153 | -0.10071 | 122.6166 | -0.068665 | 61.0153 | 122.731 | 122.6624 | -122.8683 | -122.9004
142.3281 | 123.1384 | -60.8459 | 61.9858 | -0.17197 | 0.020078 | 0.011884 | 0.00061099 | 0.062889 | -0.0057699 | 0.069037 | -60.9238 | 61.7981 | -60.8688 | -60.9787 | 61.8851 | 0.17853 | 0.022888 | 0.16479 | 61.8164 | -60.9283 | -0.022888 | -0.18768 | -0.07782 | -0.13275 | -0.10071 | -0.082398 | -0.16937 | -0.054932 | 60.8688 | 61.0107 | 122.731 | 122.644 | -0.07782 | 122.6624 | 61.0245 | -0.082398 | 122.644 | -0.07782 | 61.0245 | 122.731 | 122.6624 | -122.8546 | -122.9141
143.3281 | 123.056 | -60.8826 | 61.9949 | -0.19485 | 0.016661 | 0.01167 | 0.00061099 | 0.063316 | -0.0057699 | 0.069677 | -60.9421 | 61.7981 | -60.8688 | -61.0062 | 61.8393 | 0.13733 | 0.09613 | 0.10071 | 61.8439 | -60.9695 | 0.013733 | -0.19684 | -0.05951 | -0.1236 | -0.15564 | -0.086975 | -0.15106 | -0.073243 | 60.9787 | 60.9833 | 122.7219 | 122.6807 | -0.05951 | 122.7264 | 61.0199 | -0.086975 | 122.6807 | -0.05951 | 61.0199 | 122.7219 | 122.7264 | -122.8638 | -122.9645
144.3281 | 123.0835 | -60.8597 | 61.9904 | -0.17197 | 0.018797 | 0.016797 | 0.0014654 | 0.06182 | -0.0025657 | 0.068823 | -60.9283 | 61.8118 | -60.8551 | -61.0062 | 61.8576 | 0.13275 | 0.09613 | 0.11444 | 61.8256 | -60.965 | 0.004577 | -0.17853 | -0.068665 | -0.14649 | -0.13275 | -0.10529 | -0.16479 | -0.073242 | 60.9558 | 60.9741 | 122.7173 | 122.6715 | -0.068665 | 122.6852 | 60.9924 | -0.10529 | 122.6715 | -0.068665 | 60.9924 | 122.7173 | 122.6852 | -122.8455 | -122.9553
145.3281 | 123.0194 | -60.8826 | 61.9812 | -0.1796 | 0.017088 | 0.014447 | 0.0021064 | 0.063743 | -0.0036337 | 0.071173 | -60.9833 | 61.8713 | -60.8826 | -61.2259 | 61.5875 | 0.004578 | 0.21057 | -0.022888 | 61.8805 | -60.9833 | 0 | -0.10986 | -0.10071 | -0.34332 | -0.39368 | -0.10071 | -0.10071 | -0.10071 | 61.0931 | 60.8597 | 122.4701 | 122.7539 | -0.10071 | 122.7631 | 60.8871 | -0.10071 | 122.7539 | -0.10071 | 60.8871 | 122.4701 | 122.7631 | -122.8638 | -122.9645
146.3281 | 123.0515 | -60.8917 | 62.0087 | -0.21011 | 0.020933 | 0.015943 | 0.003388 | 0.062675 | -0.0032065 | 0.070105 | -60.997 | 61.8759 | -60.8826 | -61.0931 | 61.6699 | 0.11444 | 0.4303 | -0.15106 | 61.8576 | -60.9695 | 0.009156 | -0.13275 | -0.10528 | -0.20142 | -0.33875 | -0.077819 | -0.15106 | -0.11444 | 61.322 | 60.7407 | 122.5616 | 122.7676 | -0.10528 | 122.7493 | 61.0062 | -0.077819 | 122.7676 | -0.10528 | 61.0062 | 122.5616 | 122.7493 | -122.8912 | -122.9782
147.3281 | 123.0652 | -60.8414 | 62.0087 | -0.14908 | 0.019224 | 0.019788 | 0.0036018 | 0.065879 | -0.0023519 | 0.071386 | -60.965 | 61.8576 | -60.8963 | -61.0657 | 61.8027 | 0.086975 | 0.14191 | 0.036621 | 61.8713 | -60.965 | -0.054931 | -0.15106 | -0.1236 | -0.2243 | -0.20599 | -0.1236 | -0.13733 | -0.068665 | 60.9833 | 60.878 | 122.644 | 122.699 | -0.1236 | 122.7127 | 60.9283 | -0.1236 | 122.699 | -0.1236 | 60.9283 | 122.644 | 122.7127 | -122.905 | -122.9736
148.3281 | 123.111 | -60.8322 | 61.9904 | -0.15671 | 0.016233 | 0.017865 | -0.00045721 | 0.062461 | -0.0038473 | 0.068396 | -60.9375 | 61.7935 | -60.8643 | -61.0016 | 61.8713 | 0.1831 | 0.045776 | 0.14191 | 61.8393 | -60.9512 | -0.032044 | -0.19684 | -0.10529 | -0.16937 | -0.11902 | -0.11902 | -0.15106 | -0.073242 | 60.878 | 60.9741 | 122.7036 | 122.6257 | -0.10529 | 122.6715 | 61.0153 | -0.11902 | 122.6257 | -0.10529 | 61.0153 | 122.7036 | 122.6715 | -122.8546 | -122.9416
149.3281 | 123.0927 | -60.8505 | 61.9675 | -0.16434 | 0.016661 | 0.015729 | -0.00045721 | 0.063316 | -0.0019247 | 0.0716 | -60.91 | 61.8347 | -60.8414 | -60.9741 | 61.8896 | 0.16022 | 0.027466 | 0.16022 | 61.8576 | -60.9421 | 0.009155 | -0.13275 | -0.059509 | -0.1236 | -0.07782 | -0.091553 | -0.10986 | -0.068664 | 60.878 | 61.0107 | 122.7402 | 122.6852 | -0.059509 | 122.7081 | 61.0107 | -0.091553 | 122.6852 | -0.059509 | 61.0107 | 122.7402 | 122.7081 | -122.8088 | -122.9095
150.3281 | 123.0515 | -60.8459 | 62.0087 | -0.1796 | 0.016874 | 0.013379 | 0.0036018 | 0.060539 | -0.0032065 | 0.070959 | -60.9421 | 61.8347 | -60.8688 | -61.0336 | 61.8347 | 0.13275 | 0.13733 | 0.07782 | 61.8805 | -60.9467 | -0.022888 | -0.17395 | -0.096131 | -0.18768 | -0.17395 | -0.10071 | -0.12817 | -0.073243 | 60.9833 | 60.9238 | 122.6807 | 122.6807 | -0.096131 | 122.7264 | 60.9787 | -0.10071 | 122.6807 | -0.096131 | 60.9787 | 122.6807 | 122.7264 | -122.8775 | -122.9553
151.3281 | 123.056 | -60.8505 | 61.9766 | -0.21011 | 0.018583 | 0.013806 | 0.0025336 | 0.063743 | -0.0029929 | 0.067328 | -60.9467 | 61.8301 | -60.8597 | -61.0245 | 61.8668 | 0.13733 | 0.10071 | 0.12817 | 61.8484 | -60.9421 | -0.009155 | -0.14648 | -0.09613 | -0.17395 | -0.10986 | -0.091553 | -0.12817 | -0.086975 | 60.9512 | 60.9787 | 122.7173 | 122.6807 | -0.09613 | 122.699 | 60.9879 | -0.091553 | 122.6807 | -0.09613 | 60.9879 | 122.7173 | 122.699 | -122.8363 | -122.9187
152.3281 | 122.9782 | -60.8917 | 62.0087 | -0.17197 | 0.01837 | 0.015943 | 0.0038154 | 0.062034 | 0.0014933 | 0.070318 | -61.0016 | 61.8668 | -60.8963 | -61.0291 | 62.0911 | 0.19684 | -0.07782 | 0.027466 | 61.8576 | -60.9924 | -0.004577 | -0.14191 | -0.10986 | -0.13733 | 0.082397 | -0.10071 | -0.15106 | -0.10529 | 60.8139 | 60.9192 | 122.9828 | 122.7585 | -0.10986 | 122.7493 | 61.0886 | -0.10071 | 122.7585 | -0.10986 | 61.0886 | 122.9828 | 122.7493 | -122.905 | -123.0011
153.3281 | 122.9233 | -60.8734 | 62.0316 | -0.1796 | 0.019651 | 0.014875 | -2.9814e-05 | 0.063102 | -0.0010703 | 0.069037 | -60.9833 | 61.8713 | -60.8688 | -61.0611 | 61.7981 | 0.082397 | 0.15564 | 0.068665 | 61.8988 | -60.9924 | 0.004578 | -0.16022 | -0.10986 | -0.18768 | -0.23346 | -0.11902 | -0.13275 | -0.11444 | 61.0291 | 60.9421 | 122.6715 | 122.7448 | -0.10986 | 122.7722 | 60.9558 | -0.11902 | 122.7448 | -0.10986 | 60.9558 | 122.6715 | 122.7722 | -122.9004 | -123.024
154.3281 | 123.0469 | -60.8917 | 61.9949 | -0.17197 | 0.018583 | 0.012738 | 0.0029608 | 0.060966 | -0.0047019 | 0.069891 | -60.9604 | 61.8256 | -60.8643 | -61.0382 | 61.8164 | 0.10986 | 0.13733 | 0.09613 | 61.8576 | -60.9558 | 0.027466 | -0.16937 | -0.068664 | -0.14648 | -0.17853 | -0.064087 | -0.13733 | -0.09613 | 61.0291 | 60.9879 | 122.7081 | 122.7173 | -0.068664 | 122.7493 | 61.0016 | -0.064087 | 122.7173 | -0.068664 | 61.0016 | 122.7081 | 122.7493 | -122.8592 | -122.9507
155.3281 | 123.1476 | -60.8322 | 61.9904 | -0.14908 | 0.018156 | 0.015943 | 0.0012518 | 0.064384 | -0.0025657 | 0.069464 | -60.9192 | 61.7844 | -60.8505 | -60.9787 | 61.9034 | 0.17853 | -0.004578 | 0.16937 | 61.8439 | -60.9329 | -0.018311 | -0.20599 | -0.086975 | -0.14648 | -0.086975 | -0.10071 | -0.14648 | -0.068664 | 60.8276 | 61.0016 | 122.7356 | 122.6166 | -0.086975 | 122.6761 | 61.0107 | -0.10071 | 122.6166 | -0.086975 | 61.0107 | 122.7356 | 122.6761 | -122.8409 | -122.9233
156.3281 | 123.1384 | -60.8368 | 61.9766 | -0.16434 | 0.017729 | 0.014661 | 0.0018928 | 0.062034 | -0.0038473 | 0.070318 | -60.91 | 61.7752 | -60.8643 | -60.9604 | 61.908 | 0.19226 | -0.022888 | 0.17395 | 61.8347 | -60.9283 | -0.027466 | -0.20142 | -0.073242 | -0.1236 | -0.068665 | -0.091553 | -0.14191 | -0.045776 | 60.8139 | 61.0107 | 122.7448 | 122.612 | -0.073242 | 122.6715 | 61.0291 | -0.091553 | 122.612 | -0.073242 | 61.0291 | 122.7448 | 122.6715 | -122.8409 | -122.905
157.3281 | 123.1201 | -60.8551 | 61.9812 | -0.16434 | 0.018156 | 0.012738 | 0.0025336 | 0.063102 | -0.0044883 | 0.070746 | -60.91 | 61.8073 | -60.8551 | -60.9833 | 61.8713 | 0.16479 | 0.041199 | 0.16022 | 61.8622 | -60.9055 | 0 | -0.17395 | -0.054931 | -0.12817 | -0.10986 | -0.050354 | -0.11902 | -0.054931 | 60.8963 | 61.0153 | 122.7264 | 122.6624 | -0.054931 | 122.7173 | 61.0199 | -0.050354 | 122.6624 | -0.054931 | 61.0199 | 122.7264 | 122.7173 | -122.8363 | -122.8867
158.3281 | 123.1247 | -60.8276 | 61.972 | -0.13382 | 0.017942 | 0.013806 | 0.0014654 | 0.063957 | -0.0027793 | 0.069677 | -60.9009 | 61.7981 | -60.878 | -60.9467 | 61.8988 | 0.17853 | 0.009155 | 0.16479 | 61.8301 | -60.9329 | -0.050354 | -0.17395 | -0.073242 | -0.11902 | -0.073242 | -0.10528 | -0.14191 | -0.022888 | 60.8368 | 60.9924 | 122.7264 | 122.6257 | -0.073242 | 122.6578 | 61.0062 | -0.10528 | 122.6257 | -0.073242 | 61.0062 | 122.7264 | 122.6578 | -122.85 | -122.905
159.3281 | 123.0881 | -60.8459 | 61.9858 | -0.20248 | 0.016874 | 0.014447 | 0.003388 | 0.063743 | -0.0036337 | 0.067969 | -60.9146 | 61.7981 | -60.8505 | -61.0016 | 61.8576 | 0.14648 | 0.07782 | 0.11902 | 61.853 | -60.965 | -0.004578 | -0.18768 | -0.068665 | -0.15564 | -0.12817 | -0.11902 | -0.13275 | -0.064087 | 60.9238 | 60.965 | 122.7036 | 122.644 | -0.068665 | 122.699 | 60.9924 | -0.11902 | 122.644 | -0.068665 | 60.9924 | 122.7036 | 122.699 | -122.8363 | -122.9507
160.3281 | 123.1018 | -60.8414 | 61.9766 | -0.15671 | 0.017301 | 0.010175 | 0.00061099 | 0.063529 | -0.0044883 | 0.068823 | -60.9146 | 61.8027 | -60.8917 | -60.9879 | 61.8851 | 0.1831 | 0.050354 | 0.16479 | 61.8393 | -60.9238 | -0.050354 | -0.17395 | -0.073242 | -0.14648 | -0.091553 | -0.082397 | -0.13733 | -0.022888 | 60.8917 | 61.0062 | 122.7264 | 122.644 | -0.073242 | 122.6807 | 61.0245 | -0.082397 | 122.644 | -0.073242 | 61.0245 | 122.7264 | 122.6807 | -122.8683 | -122.9004
161.3281 | 123.1247 | -60.8414 | 61.9995 | -0.15671 | 0.017301 | 0.011029 | 0.0014654 | 0.064384 | -0.0034201 | 0.070746 | -60.9055 | 61.7569 | -60.8643 | -60.9695 | 61.8851 | 0.16937 | 0.009155 | 0.16479 | 61.8484 | -60.9146 | -0.022888 | -0.24262 | -0.064087 | -0.12817 | -0.11444 | -0.073242 | -0.15106 | -0.041199 | 60.8505 | 61.0062 | 122.7264 | 122.5983 | -0.064087 | 122.6898 | 61.0107 | -0.073242 | 122.5983 | -0.064087 | 61.0107 | 122.7264 | 122.6898 | -122.8638 | -122.9141
162.3281 | 123.0698 | -60.8322 | 61.94 | -0.088043 | 0.018797 | 0.015729 | -0.00067081 | 0.063529 | -0.0036337 | 0.070532 | -60.8917 | 61.7615 | -60.8551 | -60.9741 | 61.9171 | 0.20142 | -0.054932 | 0.31586 | 61.8347 | -60.9192 | -0.022889 | -0.17853 | -0.05951 | -0.14191 | -0.022888 | -0.086975 | -0.10529 | -0.036621 | 60.7773 | 61.1481 | 122.7493 | 122.5937 | -0.05951 | 122.6669 | 61.0336 | -0.086975 | 122.5937 | -0.05951 | 61.0336 | 122.7493 | 122.6669 | -122.7951 | -122.8592
163.3281 | 123.175 | -60.8231 | 61.9492 | -0.027008 | 0.018156 | 0.014661 | 0.00061099 | 0.061607 | -0.0023519 | 0.070746 | -60.9238 | 61.7844 | -60.8734 | -60.9695 | 61.8851 | 0.18768 | -0.036621 | 0.15564 | 61.8484 | -60.9283 | -0.050354 | -0.16479 | -0.10071 | -0.14648 | -0.064087 | -0.10529 | -0.10071 | -0.050354 | 60.7864 | 60.9787 | 122.7081 | 122.6074 | -0.10071 | 122.6715 | 61.0107 | -0.10529 | 122.6074 | -0.10071 | 61.0107 | 122.7081 | 122.6715 | -122.8226 | -122.8775
164.3281 | 123.1522 | -60.8368 | 61.9675 | -0.088043 | 0.017729 | 0.0099612 | 0.0010382 | 0.063316 | -0.0040609 | 0.070318 | -60.5026 | 61.8576 | -60.8276 | -60.9192 | 61.8301 | 0.13733 | -0.009155 | 0.15106 | 61.821 | -60.91 | 0.009155 | -0.10986 | 0.33417 | -0.082397 | -0.13733 | -0.073242 | -0.14648 | 0.32501 | 60.8276 | 60.9879 | 122.6669 | 122.6944 | 0.33417 | 122.6578 | 60.9741 | -0.073242 | 122.6944 | 0.33417 | 60.9741 | 122.6669 | 122.6578 | -122.7951 | -122.8775
165.3281 | 123.1338 | -60.8459 | 61.9446 | -0.14145 | 0.018156 | 0.013806 | 0.003388 | 0.062248 | -0.0042747 | 0.071814 | -60.91 | 61.7798 | -60.8505 | -60.9512 | 61.908 | 0.53558 | -0.14191 | -0.14191 | 61.8118 | -60.965 | -0.004578 | -0.1648 | -0.064087 | -0.10529 | -0.036621 | -0.11902 | -0.13275 | -0.059509 | 60.704 | 60.704 | 122.7539 | 122.6257 | -0.064087 | 122.6578 | 61.3815 | -0.11902 | 122.6257 | -0.064087 | 61.3815 | 122.7539 | 122.6578 | -122.7951 | -122.9095
166.3281 | 123.1384 | -60.8459 | 61.9629 | -0.080414 | 0.018797 | 0.015302 | 0.0021064 | 0.062675 | -0.0025657 | 0.070959 | -60.8826 | 61.7981 | -60.8414 | -60.9467 | 61.8942 | 0.18768 | -0.027466 | 0.17395 | 61.8164 | -60.9009 | 0.004577 | -0.16479 | -0.036621 | -0.10071 | -0.068665 | -0.054932 | -0.14648 | -0.041198 | 60.8185 | 61.0199 | 122.7402 | 122.644 | -0.036621 | 122.6624 | 61.0336 | -0.054932 | 122.644 | -0.036621 | 61.0336 | 122.7402 | 122.6624 | -122.8043 | -122.8638
167.3281 | 123.1247 | -60.8231 | 61.9858 | 0.43839 | 0.01837 | 0.017865 | 0.0036018 | 0.060325 | -0.0051291 | 0.070532 | -60.878 | 61.7798 | -60.8734 | -60.9558 | 61.9034 | 0.1831 | -0.018311 | 0.17853 | 61.8347 | -60.9192 | -0.050354 | -0.20599 | -0.054932 | -0.13275 | -0.082398 | -0.09613 | -0.15106 | -0.004578 | 60.8047 | 61.0016 | 122.7264 | 122.6028 | -0.054932 | 122.6578 | 61.0062 | -0.09613 | 122.6028 | -0.054932 | 61.0062 | 122.7264 | 122.6578 | -122.8592 | -122.905
168.3281 | 123.1522 | -60.8505 | 61.972 | -0.13382 | 0.021574 | 0.014661 | 0.0021064 | 0.063957 | -0.0032065 | 0.067969 | -61.1618 | 61.7752 | -60.8826 | -60.9421 | 61.8988 | 0.16937 | -0.013733 | 0.16479 | 61.8027 | -60.9192 | -0.032043 | -0.19684 | -0.31128 | -0.091553 | -0.073242 | -0.068664 | -0.16937 | -0.27924 | 60.8368 | 61.0153 | 122.7493 | 122.6257 | -0.31128 | 122.6532 | 61.0199 | -0.068664 | 122.6257 | -0.31128 | 61.0199 | 122.7493 | 122.6532 | -122.8546 | -122.8912
169.3281 | 123.143 | -60.8231 | 61.9812 | -0.042267 | 0.016874 | 0.014661 | -2.9814e-05 | 0.063743 | -0.0025657 | 0.06925 | -60.965 | 61.7844 | -60.8643 | -60.9924 | 61.8622 | 0.14191 | -0.036621 | 0.11902 | 61.8164 | -60.9375 | -0.041199 | -0.19684 | -0.14191 | -0.16937 | -0.11902 | -0.11444 | -0.16479 | -0.10071 | 60.7864 | 60.9421 | 122.6852 | 122.6074 | -0.14191 | 122.6395 | 60.965 | -0.11444 | 122.6074 | -0.14191 | 60.965 | 122.6852 | 122.6395 | -122.8455 | -122.9187
170.3281 | 123.1522 | -60.8185 | 61.9583 | 0.011139 | 0.018156 | 0.015088 | 0.0029608 | 0.060111 | -0.0027793 | 0.072027 | -60.9421 | 61.7752 | -60.8643 | -61.0062 | 61.853 | 0.13275 | -0.050354 | 0.11444 | 61.7844 | -60.9558 | -0.045777 | -0.1831 | -0.1236 | -0.18768 | -0.10529 | -0.13733 | -0.17395 | -0.07782 | 60.7681 | 60.9329 | 122.6715 | 122.5937 | -0.1236 | 122.6028 | 60.9512 | -0.13733 | 122.5937 | -0.1236 | 60.9512 | 122.6715 | 122.6028 | -122.8226 | -122.9141
171.3281 | 123.1934 | -60.8231 | 61.9583 | -0.065155 | 0.017942 | 0.016156 | 0.0031744 | 0.06182 | -0.0053427 | 0.06925 | -60.9192 | 61.7615 | -60.8688 | -60.965 | 61.8942 | 0.1831 | -0.064087 | 0.16937 | 61.8118 | -60.9009 | -0.045776 | -0.19684 | -0.09613 | -0.14191 | -0.064087 | -0.07782 | -0.14648 | -0.050354 | 60.759 | 60.9924 | 122.7173 | 122.5845 | -0.09613 | 122.6349 | 61.0062 | -0.07782 | 122.5845 | -0.09613 | 61.0062 | 122.7173 | 122.6349 | -122.8271 | -122.8592
172.3281 | 123.1338 | -60.8459 | 61.9766 | -0.11093 | 0.018156 | 0.013379 | 0.00061099 | 0.062034 | -0.0025657 | 0.069891 | -60.91 | 61.7844 | -60.8597 | -60.9741 | 61.8896 | 0.17395 | -0.032043 | 0.15564 | 61.8301 | -60.9055 | -0.013733 | -0.19226 | -0.064087 | -0.12817 | -0.086976 | -0.05951 | -0.14648 | -0.050354 | 60.8139 | 61.0016 | 122.7356 | 122.6303 | -0.064087 | 122.6761 | 61.0199 | -0.05951 | 122.6303 | -0.064087 | 61.0199 | 122.7356 | 122.6761 | -122.8363 | -122.8821
173.3438 | 123.0286 | -60.878 | 61.9904 | 0.056915 | 0.020719 | 0.015515 | 0.010438 | 0.066306 | -0.0042747 | 0.069037 | -60.9604 | 61.8759 | -60.8597 | -61.0565 | 61.7615 | 0.013733 | 0.045776 | -0.036621 | 61.8668 | -61.0291 | 0.018311 | -0.11444 | -0.082397 | -0.17853 | -0.22888 | -0.15106 | -0.1236 | -0.10071 | 60.9238 | 60.8414 | 122.6395 | 122.7539 | -0.082397 | 122.7448 | 60.8917 | -0.15106 | 122.7539 | -0.082397 | 60.8917 | 122.6395 | 122.7448 | -122.85 | -123.0194
174.3281 | 123.1247 | -60.8368 | 61.9629 | -0.13382 | 0.014738 | 0.015943 | 0.003388 | 0.064384 | -0.0012839 | 0.069464 | -60.8917 | 61.7752 | -60.8551 | -60.9192 | 61.8118 | 0.073242 | 0.004578 | 0.10529 | 61.8118 | -60.9421 | -0.018311 | -0.18768 | -0.054932 | -0.082397 | -0.15106 | -0.10529 | -0.15106 | -0.036621 | 60.8414 | 60.9421 | 122.6486 | 122.612 | -0.054932 | 122.6486 | 60.91 | -0.10529 | 122.612 | -0.054932 | 60.91 | 122.6486 | 122.6486 | -122.818 | -122.905
175.3281 | 123.1888 | -60.8139 | 61.9446 | 0.0035097 | 0.02136 | 0.010388 | -0.00045721 | 0.06182 | -0.0047019 | 0.071173 | -60.9238 | 61.7661 | -60.8505 | -60.9375 | 61.9125 | 0.082397 | 0.41657 | 0.07782 | 61.8759 | -60.9329 | -0.036621 | -0.17853 | -0.10986 | -0.1236 | -0.032043 | -0.11902 | -0.068664 | -0.073242 | 61.2305 | 60.8917 | 122.7264 | 122.58 | -0.10986 | 122.6898 | 60.8963 | -0.11902 | 122.58 | -0.10986 | 60.8963 | 122.7264 | 122.6898 | -122.7951 | -122.8775
176.3281 | 123.1338 | -60.8551 | 61.9583 | 0.018768 | 0.017301 | 0.015943 | 0.00232 | 0.061607 | -0.0047019 | 0.071814 | -60.9741 | 61.8118 | -60.91 | -61.0153 | 61.8439 | 0.10071 | -0.027466 | 0.086975 | 61.8027 | -60.9604 | -0.054931 | -0.14648 | -0.11902 | -0.16022 | -0.11444 | -0.10529 | -0.15564 | -0.064087 | 60.8276 | 60.9421 | 122.699 | 122.6669 | -0.11902 | 122.6578 | 60.9558 | -0.10529 | 122.6669 | -0.11902 | 60.9558 | 122.699 | 122.6578 | -122.8683 | -122.9187
177.3281 | 123.1155 | -60.8276 | 61.9675 | 0.011139 | 0.015165 | 0.012097 | 0.00061099 | 0.061607 | -0.0012839 | 0.071386 | -60.9741 | 61.7889 | -60.8871 | -61.0336 | 61.8347 | 0.10529 | -0.036621 | 0.073242 | 61.7981 | -60.965 | -0.059509 | -0.17853 | -0.14648 | -0.20599 | -0.13275 | -0.13733 | -0.16937 | -0.086975 | 60.791 | 60.9009 | 122.6624 | 122.6166 | -0.14648 | 122.6257 | 60.9329 | -0.13733 | 122.6166 | -0.14648 | 60.9329 | 122.6624 | 122.6257 | -122.8546 | -122.9324
178.3438 | 123.0515 | -60.8826 | 62.0178 | -0.14908 | 0.019651 | 0.015729 | 0.0063788 | 0.061607 | -0.0036337 | 0.069464 | -60.9695 | 61.908 | -60.8871 | -61.0611 | 61.7935 | 0.091553 | 0.14648 | 0.032043 | 61.8759 | -61.0153 | -0.004578 | -0.10986 | -0.086975 | -0.17853 | -0.2243 | -0.13275 | -0.14191 | -0.082397 | 61.0291 | 60.9146 | 122.6761 | 122.7905 | -0.086975 | 122.7585 | 60.9741 | -0.13275 | 122.7905 | -0.086975 | 60.9741 | 122.6761 | 122.7585 | -122.905 | -123.0331
179.3281 | 123.143 | -60.8185 | 61.9537 | -0.11856 | 0.018156 | 0.013593 | 0.00039739 | 0.060966 | -0.0055563 | 0.063055 | -60.9055 | 61.7706 | -60.8734 | -60.5438 | 62.1094 | -0.064087 | 0.004578 | 0.15106 | 61.8347 | -60.9329 | -0.054932 | -0.18311 | -0.086976 | 0.27466 | 0.15564 | -0.11444 | -0.11902 | -0.032044 | 60.8231 | 60.9695 | 122.9279 | 122.5891 | -0.086976 | 122.6532 | 60.7544 | -0.11444 | 122.5891 | -0.086976 | 60.7544 | 122.9279 | 122.6532 | -122.8271 | -122.8867
180.3281 | 123.0698 | -60.8231 | 62.0361 | -0.14908 | 0.017301 | 0.014234 | 0.00232 | 0.064384 | -0.0023519 | 0.068182 | -60.9329 | 61.7844 | -60.8734 | -60.9787 | 61.8896 | 0.17853 | -0.059509 | 0.15106 | 61.8073 | -60.9192 | -0.050354 | -0.25177 | -0.10986 | -0.15564 | -0.14648 | -0.09613 | -0.22888 | -0.059509 | 60.7636 | 60.9741 | 122.7127 | 122.6074 | -0.10986 | 122.6303 | 61.0016 | -0.09613 | 122.6074 | -0.10986 | 61.0016 | 122.7127 | 122.6303 | -122.9095 | -122.9553
181.3281 | 123.1476 | -60.8414 | 61.9492 | -0.019379 | 0.015592 | 0.010602 | 0.0021064 | 0.06118 | -0.0021383 | 0.071173 | -60.9329 | 61.7752 | -60.8643 | -60.9879 | 61.8896 | 0.15106 | -0.032043 | 0.14648 | 61.8256 | -60.9283 | -0.022888 | -0.17395 | -0.091552 | -0.14648 | -0.05951 | -0.086975 | -0.1236 | -0.068664 | 60.8093 | 60.9879 | 122.731 | 122.6166 | -0.091552 | 122.6669 | 60.9924 | -0.086975 | 122.6166 | -0.091552 | 60.9924 | 122.731 | 122.6669 | -122.8134 | -122.8775
182.3281 | 123.1247 | -60.8414 | 61.9583 | -0.057526 | 0.01837 | 0.014447 | 0.0031744 | 0.06118 | -0.0034201 | 0.069677 | -60.9512 | 61.7889 | -60.8734 | -60.9833 | 61.8576 | 0.16479 | -0.050354 | 0.12817 | 61.821 | -60.9467 | -0.032043 | -0.16937 | -0.10986 | -0.14191 | -0.10071 | -0.10529 | -0.13733 | -0.07782 | 60.791 | 60.9695 | 122.699 | 122.6303 | -0.10986 | 122.6624 | 61.0062 | -0.10529 | 122.6303 | -0.10986 | 61.0062 | 122.699 | 122.6624 | -122.8317 | -122.905
183.3438 | 123.0515 | -60.878 | 61.9858 | 0.049286 | 0.023496 | 0.015729 | 0.0093696 | 0.063102 | -0.0047019 | 0.071173 | -60.9467 | 61.8484 | -60.878 | -61.0382 | 61.7752 | 0.050354 | 0.050354 | -0.018311 | 61.8027 | -61.0153 | 0 | -0.13733 | -0.068664 | -0.16022 | -0.21057 | -0.13733 | -0.18311 | -0.068664 | 60.9283 | 60.8597 | 122.6532 | 122.7264 | -0.068664 | 122.6807 | 60.9283 | -0.13733 | 122.7264 | -0.068664 | 60.9283 | 122.6532 | 122.6807 | -122.8638 | -123.0011
184.3281 | 123.1567 | -60.8597 | 61.9583 | 0.018768 | 0.01837 | 0.017652 | -2.9814e-05 | 0.059684 | -0.0010703 | 0.06925 | -60.965 | 61.7889 | -60.8826 | -61.0336 | 61.8393 | 0.11902 | -0.045776 | 0.073242 | 61.7844 | -60.9558 | -0.022888 | -0.16937 | -0.10529 | -0.17395 | -0.11902 | -0.096131 | -0.17395 | -0.082398 | 60.8139 | 60.9329 | 122.699 | 122.6486 | -0.10529 | 122.644 | 60.9787 | -0.096131 | 122.6486 | -0.10529 | 60.9787 | 122.699 | 122.644 | -122.8409 | -122.9141
185.3281 | 123.1338 | -60.8459 | 61.9446 | 0.064545 | 0.018797 | 0.014447 | 0.0025336 | 0.062248 | -0.0036337 | 0.072668 | -60.9833 | 61.7935 | -60.9009 | -61.0245 | 61.8393 | 0.09613 | -0.036621 | 0.073242 | 61.8027 | -60.9879 | -0.054932 | -0.15106 | -0.13733 | -0.17853 | -0.10529 | -0.14191 | -0.14191 | -0.082397 | 60.8093 | 60.9192 | 122.6852 | 122.6395 | -0.13733 | 122.6486 | 60.9421 | -0.14191 | 122.6395 | -0.13733 | 60.9421 | 122.6852 | 122.6486 | -122.8455 | -122.9324
186.3281 | 123.1293 | -60.8551 | 61.9537 | 0.072174 | 0.01602 | 0.015302 | 0.0027472 | 0.064598 | -0.0027793 | 0.070105 | -60.9833 | 61.7935 | -60.91 | -61.0474 | 61.8118 | 0.07782 | -0.027466 | 0.059509 | 61.8118 | -60.9467 | -0.054931 | -0.16022 | -0.12817 | -0.19226 | -0.14191 | -0.091552 | -0.14191 | -0.073242 | 60.8276 | 60.9146 | 122.6669 | 122.6486 | -0.12817 | 122.6669 | 60.9329 | -0.091552 | 122.6486 | -0.12817 | 60.9329 | 122.6669 | 122.6669 | -122.8638 | -122.9004
187.3281 | 123.1064 | -60.8643 | 61.9583 | 0.0035097 | 0.019651 | 0.011243 | -0.0013116 | 0.061607 | -0.0036337 | 0.070105 | -60.9375 | 61.7752 | -60.9009 | -61.0016 | 61.8576 | 0.13733 | -0.054932 | 0.09613 | 61.7981 | -60.9421 | -0.036621 | -0.1831 | -0.073242 | -0.13733 | -0.10071 | -0.07782 | -0.16022 | -0.036621 | 60.8093 | 60.9604 | 122.7219 | 122.6395 | -0.073242 | 122.6624 | 61.0016 | -0.07782 | 122.6395 | -0.073242 | 61.0016 | 122.7219 | 122.6624 | -122.8592 | -122.9004
188.3438 | 123.0331 | -60.8505 | 61.9995 | -0.16434 | 0.021574 | 0.014875 | 0.0089422 | 0.063957 | -0.0017111 | 0.068609 | -60.9604 | 61.8896 | -60.8917 | -61.0245 | 61.7981 | 0.091553 | 0.10071 | 0.050354 | 61.8622 | -60.9604 | -0.041199 | -0.10986 | -0.10986 | -0.17395 | -0.20142 | -0.10986 | -0.13733 | -0.068664 | 60.9512 | 60.9009 | 122.6486 | 122.7402 | -0.10986 | 122.7127 | 60.9421 | -0.10986 | 122.7402 | -0.10986 | 60.9421 | 122.6486 | 122.7127 | -122.8912 | -122.9599
189.3281 | 123.143 | -60.8276 | 61.9492 | 0.087433 | 0.017942 | 0.014875 | -0.00024361 | 0.06182 | -0.0036337 | 0.068396 | -60.9879 | 61.8118 | -60.8917 | -61.0291 | 61.8347 | 0.10529 | -0.032043 | 0.068665 | 61.8118 | -60.9467 | -0.064087 | -0.13733 | -0.16022 | -0.20142 | -0.11444 | -0.11902 | -0.13733 | -0.09613 | 60.7956 | 60.8963 | 122.6624 | 122.6395 | -0.16022 | 122.6395 | 60.9329 | -0.11902 | 122.6395 | -0.16022 | 60.9329 | 122.6624 | 122.6395 | -122.8409 | -122.8958
190.3281 | 123.0743 | -60.8551 | 61.9675 | 0.072174 | 0.017515 | 0.013166 | -2.9814e-05 | 0.060966 | -0.0034201 | 0.072027 | -60.9879 | 61.7661 | -60.8826 | -61.1481 | 61.8713 | 0.091553 | -0.059509 | 0.009155 | 61.8027 | -60.9558 | -0.027465 | -0.20142 | -0.13275 | -0.29297 | -0.09613 | -0.10071 | -0.16479 | -0.10529 | 60.7956 | 60.8643 | 122.7264 | 122.6212 | -0.13275 | 122.6578 | 60.9467 | -0.10071 | 122.6212 | -0.13275 | 60.9467 | 122.7264 | 122.6578 | -122.85 | -122.9233
191.3281 | 123.111 | -60.8551 | 61.9354 | 0.17899 | 0.018156 | 0.0080386 | 0.0014654 | 0.062461 | -0.0029929 | 0.070746 | -60.9833 | 61.7477 | -60.8826 | -61.0565 | 61.8027 | -0.036621 | 0.28839 | 0.07782 | 61.8347 | -60.9238 | -0.027465 | -0.18768 | -0.12817 | -0.20142 | -0.13275 | -0.068664 | -0.10071 | -0.10071 | 61.1435 | 60.9329 | 122.6578 | 122.6028 | -0.12817 | 122.6898 | 60.8185 | -0.068664 | 122.6028 | -0.12817 | 60.8185 | 122.6578 | 122.6898 | -122.818 | -122.8592
192.3281 | 123.143 | -60.8368 | 61.9675 | 0.026398 | 0.01837 | 0.012525 | 0.0016792 | 0.060111 | -0.0029929 | 0.068609 | -60.9833 | 61.7569 | -60.8688 | -61.0611 | 61.821 | 0.073242 | -0.032043 | 0.036621 | 61.7935 | -60.9512 | -0.032043 | -0.21057 | -0.14648 | -0.2243 | -0.14648 | -0.11444 | -0.17395 | -0.11444 | 60.8047 | 60.8734 | 122.6578 | 122.5937 | -0.14648 | 122.6303 | 60.91 | -0.11444 | 122.5937 | -0.14648 | 60.91 | 122.6578 | 122.6303 | -122.8363 | -122.9187
193.3438 | 123.0469 | -60.8459 | 61.9904 | -0.11856 | 0.019651 | 0.014875 | 0.0076606 | 0.06417 | -0.0061973 | 0.070105 | -60.965 | 61.8484 | -60.8826 | -61.0107 | 61.8118 | 0.091553 | 0.10071 | 0.054932 | 61.8347 | -60.9558 | -0.036621 | -0.14191 | -0.11902 | -0.16479 | -0.17853 | -0.10986 | -0.15564 | -0.082398 | 60.9467 | 60.9009 | 122.6578 | 122.6944 | -0.11902 | 122.6807 | 60.9375 | -0.10986 | 122.6944 | -0.11902 | 60.9375 | 122.6578 | 122.6807 | -122.8729 | -122.9462
194.3281 | 123.1155 | -60.8505 | 61.9263 | 0.16373 | 0.018156 | 0.011884 | 0.00082459 | 0.062461 | -0.0025657 | 0.069891 | -61.0519 | 61.7844 | -60.8871 | -61.0565 | 61.7844 | 0.073242 | -0.041199 | 0.036621 | 61.821 | -60.9512 | -0.036621 | -0.14191 | -0.20142 | -0.20599 | -0.14191 | -0.10071 | -0.10529 | -0.16479 | 60.8093 | 60.8871 | 122.6349 | 122.6349 | -0.20142 | 122.6715 | 60.9238 | -0.10071 | 122.6349 | -0.20142 | 60.9238 | 122.6349 | 122.6715 | -122.8134 | -122.8775
195.3281 | 123.0927 | -60.8276 | 61.9675 | 0.049286 | 0.017942 | 0.011457 | 0.00039739 | 0.059471 | -0.0040609 | 0.068182 | -60.965 | 61.7752 | -60.8688 | -61.0291 | 61.8347 | 0.10529 | -0.045776 | 0.082397 | 61.8027 | -60.9467 | -0.041198 | -0.19226 | -0.13733 | -0.20142 | -0.13275 | -0.11902 | -0.16479 | -0.096131 | 60.7819 | 60.91 | 122.6624 | 122.6028 | -0.13733 | 122.6303 | 60.9329 | -0.11902 | 122.6028 | -0.13733 | 60.9329 | 122.6624 | 122.6303 | -122.8363 | -122.9141
196.3281 | 123.1155 | -60.8505 | 61.9583 | 0.026398 | 0.017088 | 0.014447 | 0.0038154 | 0.062889 | -0.0042747 | 0.071386 | -60.9787 | 61.7752 | -60.8826 | -61.0382 | 61.821 | 0.10529 | -0.032043 | 0.059509 | 61.7844 | -60.9604 | -0.032043 | -0.1831 | -0.12817 | -0.18768 | -0.13733 | -0.10986 | -0.17395 | -0.096131 | 60.8185 | 60.91 | 122.6715 | 122.6257 | -0.12817 | 122.6349 | 60.9558 | -0.10986 | 122.6257 | -0.12817 | 60.9558 | 122.6715 | 122.6349 | -122.8409 | -122.9187
197.3281 | 123.0743 | -60.8688 | 61.9629 | 0.095062 | 0.01837 | 0.014447 | 0.0010382 | 0.062889 | -0.0027793 | 0.070318 | -60.9787 | 61.7706 | -60.878 | -61.0565 | 62.0407 | 0.29297 | -0.29755 | 0.068665 | 61.7889 | -60.965 | -0.009156 | -0.19226 | -0.10986 | -0.18768 | 0.077819 | -0.096131 | -0.17395 | -0.10071 | 60.5713 | 60.9375 | 122.9095 | 122.6395 | -0.10986 | 122.6578 | 61.1618 | -0.096131 | 122.6395 | -0.10986 | 61.1618 | 122.9095 | 122.6578 | -122.8409 | -122.9279
198.3281 | 123.143 | -60.8505 | 61.9904 | 0.095062 | 0.01901 | 0.012097 | 0.0036018 | 0.059684 | -0.0047019 | 0.069464 | -60.9924 | 61.7661 | -60.8917 | -61.0382 | 61.8301 | 0.073242 | -0.032043 | 0.059509 | 61.821 | -60.9512 | -0.041199 | -0.2243 | -0.14191 | -0.18768 | -0.16022 | -0.10071 | -0.16937 | -0.10071 | 60.8185 | 60.91 | 122.6807 | 122.6166 | -0.14191 | 122.6715 | 60.9238 | -0.10071 | 122.6166 | -0.14191 | 60.9238 | 122.6807 | 122.6715 | -122.8821 | -122.9416
199.3281 | 123.111 | -60.8643 | 61.9537 | 0.079804 | 0.018797 | 0.01402 | 0.00232 | 0.060966 | -0.0032065 | 0.069464 | -60.965 | 61.7523 | -60.878 | -61.0474 | 61.8073 | 0.073242 | -0.022888 | 0.059509 | 61.8164 | -60.9329 | -0.013733 | -0.20142 | -0.10071 | -0.1831 | -0.14648 | -0.068664 | -0.13733 | -0.086975 | 60.8414 | 60.9238 | 122.6715 | 122.6166 | -0.10071 | 122.6807 | 60.9375 | -0.068664 | 122.6166 | -0.10071 | 60.9375 | 122.6715 | 122.6807 | -122.8317 | -122.8867
200.3281 | 123.1338 | -60.8322 | 61.9812 | -0.049896 | 0.01602 | 0.013593 | 0.0031744 | 0.061393 | -0.0038473 | 0.070959 | -60.9467 | 61.7523 | -60.8871 | -61.0062 | 61.8439 | 0.1236 | -0.041199 | 0.11444 | 61.8073 | -60.9283 | -0.054932 | -0.22888 | -0.11444 | -0.17395 | -0.13733 | -0.096131 | -0.17395 | -0.059509 | 60.791 | 60.9467 | 122.6761 | 122.5845 | -0.11444 | 122.6395 | 60.9558 | -0.096131 | 122.5845 | -0.11444 | 60.9558 | 122.6761 | 122.6395 | -122.8683 | -122.9095
201.3281 | 123.111 | -60.8505 | 61.9858 | -0.011749 | 0.016447 | 0.012097 | 0.004029 | 0.06118 | -0.0032065 | 0.070105 | -60.9604 | 61.7569 | -60.8826 | -61.0016 | 61.8484 | 0.11902 | -0.059509 | 0.10071 | 61.7981 | -60.9512 | -0.032043 | -0.22888 | -0.10986 | -0.15106 | -0.13733 | -0.10071 | -0.18768 | -0.07782 | 60.791 | 60.9512 | 122.699 | 122.6074 | -0.10986 | 122.6486 | 60.9695 | -0.10071 | 122.6074 | -0.10986 | 60.9695 | 122.699 | 122.6486 | -122.8683 | -122.937
202.3281 | 123.1247 | -60.8414 | 61.9583 | 0.018768 | 0.018156 | 0.012525 | 0.0038154 | 0.060325 | -0.0029929 | 0.070105 | -60.9421 | 61.7752 | -60.8734 | -61.0107 | 61.853 | 0.11902 | -0.045776 | 0.10071 | 61.8118 | -60.9741 | -0.032043 | -0.1831 | -0.10071 | -0.16937 | -0.10529 | -0.13275 | -0.14648 | -0.068665 | 60.7956 | 60.9421 | 122.6944 | 122.6166 | -0.10071 | 122.6532 | 60.9604 | -0.13275 | 122.6166 | -0.10071 | 60.9604 | 122.6944 | 122.6532 | -122.8317 | -122.9324
203.3281 | 123.1659 | -60.8643 | 61.9812 | 0.011139 | 0.016874 | 0.014234 | 0.00232 | 0.058402 | -0.0047019 | 0.070532 | -60.965 | 61.7981 | -60.8734 | -61.0153 | 61.8622 | 0.11444 | -0.050354 | 0.091553 | 61.821 | -60.9283 | -0.009155 | -0.1831 | -0.10071 | -0.15106 | -0.11902 | -0.064087 | -0.16022 | -0.091553 | 60.8139 | 60.9558 | 122.7264 | 122.6624 | -0.10071 | 122.6852 | 60.9787 | -0.064087 | 122.6624 | -0.10071 | 60.9787 | 122.7264 | 122.6852 | -122.8546 | -122.9095
204.3281 | 123.0743 | -60.8597 | 61.9354 | 0.14847 | 0.017729 | 0.015729 | 0.0036018 | 0.060111 | -0.0032065 | 0.070318 | -60.9558 | 61.7569 | -60.8963 | -61.0519 | 61.8256 | 0.050354 | -0.086975 | 0.018311 | 61.8164 | -60.9695 | -0.036621 | -0.17853 | -0.096131 | -0.19226 | -0.10986 | -0.10986 | -0.11902 | -0.05951 | 60.7727 | 60.878 | 122.6852 | 122.6166 | -0.096131 | 122.6761 | 60.91 | -0.10986 | 122.6166 | -0.096131 | 60.91 | 122.6852 | 122.6761 | -122.8317 | -122.905
205.3281 | 123.0789 | -60.8459 | 61.9492 | -0.74417 | 0.017942 | 0.011884 | 0.0038154 | 0.062461 | -0.0038473 | 0.067755 | -61.0657 | 61.7523 | -60.9055 | -61.0519 | 61.8027 | 0.045776 | -0.036621 | 0.036621 | 61.8027 | -60.9375 | -0.05951 | -0.19684 | -0.21973 | -0.20599 | -0.14648 | -0.091553 | -0.14648 | -0.16022 | 60.8093 | 60.8826 | 122.6486 | 122.5983 | -0.21973 | 122.6486 | 60.8917 | -0.091553 | 122.5983 | -0.21973 | 60.8917 | 122.6486 | 122.6486 | -122.8546 | -122.8867
206.3281 | 123.1384 | -60.8276 | 61.9537 | -0.011749 | 0.017729 | 0.012311 | 0.0031744 | 0.059471 | -0.0029929 | 0.071386 | -60.965 | 61.7935 | -60.878 | -60.997 | 61.8347 | 0.091553 | -0.045776 | 0.082397 | 61.8118 | -60.9558 | -0.050354 | -0.16022 | -0.13733 | -0.16937 | -0.11902 | -0.12817 | -0.14191 | -0.086975 | 60.7819 | 60.91 | 122.6624 | 122.6212 | -0.13733 | 122.6395 | 60.9192 | -0.12817 | 122.6212 | -0.13733 | 60.9192 | 122.6624 | 122.6395 | -122.8317 | -122.9095
207.3281 | 123.1384 | -60.8231 | 61.9583 | -0.011749 | 0.019865 | 0.0097476 | 0.005097 | 0.060539 | -0.0044883 | 0.068823 | -60.9283 | 61.7752 | -60.8963 | -60.9695 | 61.8988 | 0.15106 | -0.068665 | 0.15564 | 61.7889 | -60.9375 | -0.073242 | -0.1831 | -0.10529 | -0.14648 | -0.059509 | -0.11444 | -0.16937 | -0.032044 | 60.7544 | 60.9787 | 122.7219 | 122.5983 | -0.10529 | 122.612 | 60.9741 | -0.11444 | 122.5983 | -0.10529 | 60.9741 | 122.7219 | 122.612 | -122.8546 | -122.8958
208.3281 | 123.143 | -60.8414 | 61.9308 | -0.0041198 | 0.016874 | 0.013379 | 0.005097 | 0.061607 | -0.0042747 | 0.069037 | -60.9421 | 61.7889 | -60.8597 | -60.9695 | 61.8576 | 0.15106 | -0.059509 | 0.13733 | 61.821 | -60.9421 | -0.01831 | -0.14191 | -0.10071 | -0.12817 | -0.073242 | -0.10071 | -0.10986 | -0.082398 | 60.7819 | 60.9787 | 122.699 | 122.6303 | -0.10071 | 122.6624 | 60.9924 | -0.10071 | 122.6303 | -0.10071 | 60.9924 | 122.699 | 122.6624 | -122.7905 | -122.8729
209.3281 | 123.1476 | -60.8505 | 61.9629 | -0.019379 | 0.017942 | 0.015088 | 0.00232 | 0.060966 | -0.0049155 | 0.069037 | -60.9467 | 61.7615 | -60.8734 | -60.9879 | 61.8668 | 0.14191 | -0.027466 | 0.13275 | 61.7981 | -60.9283 | -0.022888 | -0.20142 | -0.09613 | -0.13733 | -0.096131 | -0.07782 | -0.16479 | -0.073242 | 60.8231 | 60.9833 | 122.7173 | 122.612 | -0.09613 | 122.6486 | 60.9924 | -0.07782 | 122.612 | -0.09613 | 60.9924 | 122.7173 | 122.6486 | -122.8363 | -122.8912
210.3281 | 123.1384 | -60.8459 | 61.94 | -0.027008 | 0.017301 | 0.015515 | 0.0036018 | 0.062675 | -0.0047019 | 0.069464 | -60.9421 | 61.7752 | -60.8597 | -60.997 | 61.8484 | 0.1236 | -0.041199 | 0.1236 | 61.821 | -60.9329 | -0.013733 | -0.16479 | -0.096131 | -0.15106 | -0.091552 | -0.086975 | -0.11902 | -0.082398 | 60.8047 | 60.9695 | 122.6944 | 122.6212 | -0.096131 | 122.6669 | 60.9695 | -0.086975 | 122.6212 | -0.096131 | 60.9695 | 122.6944 | 122.6669 | -122.7997 | -122.8729
211.3281 | 123.0835 | -60.8551 | 61.9446 | 0.12558 | 0.019438 | 0.0093204 | 0.0044562 | 0.060325 | -0.0036337 | 0.069677 | -60.997 | 61.7661 | -60.8963 | -61.0565 | 61.8118 | 0.064087 | -0.032043 | 0.032043 | 61.8164 | -60.9558 | -0.041198 | -0.17853 | -0.14191 | -0.20142 | -0.13275 | -0.10071 | -0.12817 | -0.10071 | 60.8231 | 60.8871 | 122.6669 | 122.6212 | -0.14191 | 122.6715 | 60.9192 | -0.10071 | 122.6212 | -0.14191 | 60.9192 | 122.6669 | 122.6715 | -122.8409 | -122.9004
212.3281 | 123.1338 | -60.8643 | 61.9812 | 0.049286 | 0.017301 | 0.014447 | 0.0029608 | 0.062675 | -0.0042747 | 0.069891 | -60.9467 | 61.7661 | -60.8917 | -61.0062 | 61.853 | 0.11902 | -0.050354 | 0.07782 | 61.8118 | -60.9238 | -0.027466 | -0.21515 | -0.082397 | -0.14191 | -0.12817 | -0.059509 | -0.16937 | -0.054931 | 60.8139 | 60.9421 | 122.7173 | 122.6303 | -0.082397 | 122.6761 | 60.9833 | -0.059509 | 122.6303 | -0.082397 | 60.9833 | 122.7173 | 122.6761 | -122.8729 | -122.905
213.3281 | 123.1293 | -60.8368 | 61.9629 | 0.056915 | 0.017088 | 0.012525 | 0.0025336 | 0.062034 | -0.0023519 | 0.072027 | -60.9512 | 61.7752 | -60.8917 | -61.0107 | 61.8484 | 0.10986 | -0.045776 | 0.091553 | 61.8164 | -60.9467 | -0.054932 | -0.18768 | -0.11444 | -0.17395 | -0.11444 | -0.10986 | -0.14648 | -0.059509 | 60.791 | 60.9283 | 122.6852 | 122.612 | -0.11444 | 122.6532 | 60.9467 | -0.10986 | 122.612 | -0.11444 | 60.9467 | 122.6852 | 122.6532 | -122.8546 | -122.9095
214.3281 | 123.1293 | -60.8597 | 61.9675 | 0.0035097 | 0.018156 | 0.015515 | 0.00232 | 0.062889 | -0.0038473 | 0.073095 | -60.965 | 61.7844 | -60.8871 | -61.0291 | 61.8347 | 0.086975 | -0.045776 | 0.059509 | 61.7889 | -60.9375 | -0.027466 | -0.1831 | -0.10529 | -0.16937 | -0.13275 | -0.07782 | -0.17853 | -0.07782 | 60.8139 | 60.9192 | 122.6944 | 122.644 | -0.10529 | 122.6486 | 60.9467 | -0.07782 | 122.644 | -0.10529 | 60.9467 | 122.6944 | 122.6486 | -122.8546 | -122.905
215.3281 | 123.1476 | -60.8459 | 61.9446 | -0.011749 | 0.018156 | 0.013806 | 0.0046698 | 0.059684 | -0.0044883 | 0.070532 | -60.9421 | 61.7798 | -60.8688 | -60.9879 | 61.8484 | 0.14191 | -0.059509 | 0.13733 | 61.7844 | -60.9421 | -0.022888 | -0.1648 | -0.096131 | -0.14191 | -0.09613 | -0.096131 | -0.16022 | -0.073243 | 60.7864 | 60.9833 | 122.6944 | 122.6257 | -0.096131 | 122.6303 | 60.9879 | -0.096131 | 122.6257 | -0.096131 | 60.9879 | 122.6944 | 122.6303 | -122.8134 | -122.8867
216.3281 | 123.1338 | -60.8459 | 61.9858 | 0.011139 | 0.016447 | 0.010175 | 0.0036018 | 0.062461 | -0.0036337 | 0.069891 | -60.9421 | 61.7661 | -60.8734 | -60.9879 | 61.8576 | 0.14648 | -0.054932 | 0.10529 | 61.8073 | -60.9375 | -0.027466 | -0.21973 | -0.096131 | -0.14191 | -0.12817 | -0.091553 | -0.17853 | -0.068665 | 60.791 | 60.9512 | 122.7036 | 122.612 | -0.096131 | 122.6532 | 60.9924 | -0.091553 | 122.612 | -0.096131 | 60.9924 | 122.7036 | 122.6532 | -122.8592 | -122.9233
217.3281 | 123.0835 | -60.8643 | 61.9675 | 0.0035097 | 0.017515 | 0.013166 | 0.00232 | 0.062461 | -0.0044883 | 0.070959 | -60.997 | 61.7889 | -60.8963 | -61.0474 | 61.821 | 0.059509 | -0.032043 | 0.054932 | 61.7981 | -60.9329 | -0.032043 | -0.17853 | -0.13275 | -0.1831 | -0.14648 | -0.068664 | -0.16937 | -0.10071 | 60.8322 | 60.9192 | 122.6852 | 122.6532 | -0.13275 | 122.6624 | 60.9238 | -0.068664 | 122.6532 | -0.13275 | 60.9238 | 122.6852 | 122.6624 | -122.8638 | -122.9004
218.3281 | 123.1064 | -60.8505 | 61.9537 | 0.21713 | 0.01837 | 0.010175 | 0.0046698 | 0.061393 | -0.0017111 | 0.06925 | -60.9787 | 61.7661 | -60.878 | -61.0382 | 61.8164 | 0.054932 | -0.036621 | 0.041199 | 61.8393 | -60.9421 | -0.027466 | -0.18768 | -0.12817 | -0.18768 | -0.13733 | -0.091553 | -0.11444 | -0.10071 | 60.8139 | 60.8917 | 122.6669 | 122.6166 | -0.12817 | 122.6898 | 60.9055 | -0.091553 | 122.6166 | -0.12817 | 60.9055 | 122.6669 | 122.6898 | -122.8317 | -122.8958
219.3281 | 123.1155 | -60.8368 | 61.9766 | 0.0035097 | 0.014952 | 0.015515 | 0.003388 | 0.06118 | -0.0025657 | 0.070959 | -60.9604 | 61.7844 | -60.8734 | -61.0199 | 61.8576 | 0.12817 | -0.045776 | 0.091553 | 61.7935 | -60.9421 | -0.036621 | -0.19226 | -0.1236 | -0.1831 | -0.11902 | -0.10529 | -0.18311 | -0.086975 | 60.791 | 60.9283 | 122.6944 | 122.6212 | -0.1236 | 122.6303 | 60.965 | -0.10529 | 122.6212 | -0.1236 | 60.965 | 122.6944 | 122.6303 | -122.85 | -122.9187
220.3281 | 123.143 | -60.8322 | 61.9858 | 0.011139 | 0.01901 | 0.01402 | 0.003388 | 0.063102 | -0.0029929 | 0.067969 | -60.9695 | 61.8073 | -60.878 | -61.0245 | 61.8484 | 0.11444 | -0.050354 | 0.082397 | 61.8256 | -60.9238 | -0.045777 | -0.17853 | -0.13733 | -0.19226 | -0.13733 | -0.091553 | -0.16022 | -0.091552 | 60.7819 | 60.9146 | 122.6807 | 122.6395 | -0.13733 | 122.6578 | 60.9467 | -0.091553 | 122.6395 | -0.13733 | 60.9467 | 122.6807 | 122.6578 | -122.8638 | -122.9095
221.3281 | 123.1476 | -60.8322 | 61.9904 | -0.042267 | 0.016661 | 0.012097 | 0.0031744 | 0.061393 | -0.0044883 | 0.068823 | -60.9283 | 61.7752 | -60.8826 | -60.9787 | 61.8988 | 0.16479 | -0.059509 | 0.14648 | 61.7889 | -60.9192 | -0.050354 | -0.21515 | -0.096131 | -0.14648 | -0.091552 | -0.086975 | -0.20142 | -0.045777 | 60.7727 | 60.9787 | 122.731 | 122.6074 | -0.096131 | 122.6212 | 60.997 | -0.086975 | 122.6074 | -0.096131 | 60.997 | 122.731 | 122.6212 | -122.8729 | -122.9095
222.3281 | 123.175 | -60.8459 | 61.9583 | -0.072784 | 0.020933 | 0.011029 | 0.0038154 | 0.060325 | -0.0044883 | 0.072027 | -60.9329 | 61.7889 | -60.9055 | -60.9558 | 61.8668 | 0.17395 | -0.073242 | 0.13733 | 61.8073 | -60.9421 | -0.05951 | -0.16937 | -0.086975 | -0.10986 | -0.091553 | -0.096131 | -0.15106 | -0.027465 | 60.7727 | 60.9833 | 122.7127 | 122.6349 | -0.086975 | 122.6532 | 61.0199 | -0.096131 | 122.6349 | -0.086975 | 61.0199 | 122.7127 | 122.6532 | -122.8638 | -122.9004
223.3281 | 123.175 | -60.8185 | 61.9629 | -0.011749 | 0.01602 | 0.01167 | 0.00232 | 0.060539 | -0.0040609 | 0.0716 | -60.9238 | 61.7935 | -60.8597 | -60.9695 | 61.8805 | 0.16937 | -0.068665 | 0.13275 | 61.8164 | -60.9329 | -0.041199 | -0.16937 | -0.10529 | -0.15106 | -0.082398 | -0.11444 | -0.14648 | -0.064087 | 60.7498 | 60.9512 | 122.699 | 122.612 | -0.10529 | 122.6349 | 60.9879 | -0.11444 | 122.612 | -0.10529 | 60.9879 | 122.699 | 122.6349 | -122.8226 | -122.8958
224.3281 | 123.1201 | -60.8551 | 61.9675 | 0.087433 | 0.018156 | 0.016797 | 0.0048834 | 0.061393 | -0.0047019 | 0.070105 | -60.9833 | 61.8118 | -60.9009 | -61.0291 | 61.8439 | 0.09613 | -0.054932 | 0.059509 | 61.8073 | -60.9512 | -0.045776 | -0.15564 | -0.12817 | -0.17395 | -0.1236 | -0.09613 | -0.16022 | -0.082397 | 60.8002 | 60.9146 | 122.699 | 122.6669 | -0.12817 | 122.6624 | 60.9512 | -0.09613 | 122.6669 | -0.12817 | 60.9512 | 122.699 | 122.6624 | -122.8683 | -122.9187
225.3281 | 123.1018 | -60.8597 | 61.972 | 0.034027 | 0.016661 | 0.012738 | 0.0048834 | 0.061393 | -0.0034201 | 0.068823 | -60.9879 | 61.7752 | -60.8826 | -61.0336 | 61.821 | 0.073242 | -0.032043 | 0.068665 | 61.8027 | -60.9558 | -0.022888 | -0.19684 | -0.12817 | -0.17395 | -0.15106 | -0.096131 | -0.16937 | -0.10529 | 60.8276 | 60.9283 | 122.6807 | 122.6349 | -0.12817 | 122.6624 | 60.9329 | -0.096131 | 122.6349 | -0.12817 | 60.9329 | 122.6807 | 122.6624 | -122.8546 | -122.9279
226.3281 | 123.1338 | -60.8551 | 61.9766 | 0.0035097 | 0.017301 | 0.010602 | 0.0031744 | 0.059898 | -0.0055563 | 0.070746 | -60.9329 | 61.7981 | -60.8826 | -60.9833 | 61.8622 | 0.14648 | -0.059509 | 0.11444 | 61.7752 | -60.9512 | -0.027465 | -0.17853 | -0.077819 | -0.12817 | -0.11444 | -0.09613 | -0.20142 | -0.050354 | 60.7956 | 60.9695 | 122.7173 | 122.6532 | -0.077819 | 122.6303 | 61.0016 | -0.09613 | 122.6532 | -0.077819 | 61.0016 | 122.7173 | 122.6303 | -122.8592 | -122.9279
227.3281 | 123.1522 | -60.8322 | 61.9629 | -0.0041198 | 0.020292 | 0.01167 | 0.0038154 | 0.061393 | -0.0053427 | 0.070532 | -60.9467 | 61.7935 | -60.878 | -60.9879 | 61.8713 | 0.14191 | -0.064087 | 0.11902 | 61.821 | -60.9512 | -0.045777 | -0.16937 | -0.11444 | -0.15564 | -0.091553 | -0.11902 | -0.14191 | -0.068664 | 60.7681 | 60.9512 | 122.7036 | 122.6257 | -0.11444 | 122.6532 | 60.9741 | -0.11902 | 122.6257 | -0.11444 | 60.9741 | 122.7036 | 122.6532 | -122.8409 | -122.9141
228.3281 | 123.1384 | -60.8276 | 61.9629 | -0.13382 | 0.017301 | 0.015088 | 0.00232 | 0.059471 | -0.0042747 | 0.072027 | -60.8917 | 61.7935 | -60.8734 | -61.29 | 61.8301 | 0.22888 | -0.21057 | 0.14191 | 61.7752 | -60.9695 | -0.045776 | -0.16937 | -0.064087 | -0.46234 | -0.13275 | -0.14191 | -0.18768 | -0.018311 | 60.6171 | 60.9695 | 122.6578 | 122.6212 | -0.064087 | 122.6028 | 61.0565 | -0.14191 | 122.6212 | -0.064087 | 61.0565 | 122.6578 | 122.6028 | -122.8363 | -122.9324
229.3281 | 123.1155 | -60.8459 | 61.9675 | -0.095673 | 0.016661 | 0.01167 | 0.0021064 | 0.060111 | -0.0023519 | 0.071386 | -60.9055 | 61.7798 | -60.8734 | -60.9421 | 62.1552 | 0.54932 | -0.27924 | -0.12817 | 61.8073 | -60.9375 | -0.027466 | -0.18768 | -0.05951 | -0.096131 | 0.18768 | -0.091553 | -0.16022 | -0.032044 | 60.5667 | 60.7178 | 123.0011 | 122.6257 | -0.05951 | 122.6532 | 61.3953 | -0.091553 | 122.6257 | -0.05951 | 61.3953 | 123.0011 | 122.6532 | -122.8409 | -122.905
230.3281 | 123.3124 | -60.8185 | 62.0087 | -0.11856 | 0.016874 | 0.014447 | 0.0036018 | 0.061393 | -0.0029929 | 0.067969 | -60.9009 | 61.8073 | -60.8871 | -60.9375 | 61.908 | 0.1831 | -0.059509 | 0.17395 | 61.7935 | -60.9375 | -0.068665 | -0.20142 | -0.082398 | -0.11902 | -0.10071 | -0.11902 | -0.21515 | -0.013733 | 60.759 | 60.9924 | 122.7264 | 122.6257 | -0.082398 | 122.612 | 61.0016 | -0.11902 | 122.6257 | -0.082398 | 61.0016 | 122.7264 | 122.612 | -122.8958 | -122.9462
231.3281 | 123.1201 | -60.8459 | 61.9766 | 0.0035097 | 0.018156 | 0.012311 | 0.0014654 | 0.06118 | -0.0025657 | 0.070318 | -60.9741 | 61.7981 | -60.8871 | -61.0062 | 61.8393 | 0.12817 | -0.045776 | 0.10071 | 61.821 | -60.9421 | -0.041199 | -0.17853 | -0.12817 | -0.16022 | -0.13733 | -0.096131 | -0.15564 | -0.086975 | 60.8002 | 60.9467 | 122.6852 | 122.644 | -0.12817 | 122.6669 | 60.9741 | -0.096131 | 122.644 | -0.12817 | 60.9741 | 122.6852 | 122.6669 | -122.8638 | -122.9187
232.3438 | 123.1522 | -60.8368 | 61.9675 | -0.049896 | 0.017088 | 0.013593 | 0.005738 | 0.061393 | -0.0049155 | 0.070318 | -60.8871 | 61.7844 | -60.8734 | -60.9512 | 61.8988 | 0.17395 | -0.045776 | 0.17395 | 61.8347 | -60.91 | -0.036621 | -0.1831 | -0.050354 | -0.11444 | -0.068664 | -0.073242 | -0.13275 | -0.013733 | 60.791 | 61.0107 | 122.7356 | 122.6212 | -0.050354 | 122.6715 | 61.0107 | -0.073242 | 122.6212 | -0.050354 | 61.0107 | 122.7356 | 122.6715 | -122.8409 | -122.8775
233.3281 | 123.143 | -60.8139 | 61.9629 | -0.057526 | 0.016233 | 0.012738 | 0.0029608 | 0.061607 | -0.0038473 | 0.069037 | -60.9192 | 61.7889 | -60.8917 | -60.9604 | 61.8942 | 0.17395 | -0.073242 | 0.15564 | 61.821 | -60.9055 | -0.07782 | -0.17395 | -0.10529 | -0.14648 | -0.068665 | -0.091553 | -0.14191 | -0.027465 | 60.7407 | 60.9695 | 122.7081 | 122.6028 | -0.10529 | 122.6349 | 60.9879 | -0.091553 | 122.6028 | -0.10529 | 60.9879 | 122.7081 | 122.6349 | -122.8546 | -122.8683
234.3281 | 123.1384 | -60.8139 | 61.9812 | 0.5452 | 0.017515 | 0.0082522 | 0.0016792 | 0.059898 | -0.0042747 | 0.06925 | -60.8871 | 61.7798 | -60.878 | -60.9695 | 61.8988 | 0.19684 | -0.041199 | 0.16022 | 61.8256 | -60.9192 | -0.064087 | -0.20142 | -0.073242 | -0.15564 | -0.082397 | -0.10529 | -0.15564 | -0.009155 | 60.7727 | 60.9741 | 122.7127 | 122.5937 | -0.073242 | 122.6395 | 61.0107 | -0.10529 | 122.5937 | -0.073242 | 61.0107 | 122.7127 | 122.6395 | -122.8592 | -122.9004
235.3281 | 123.143 | -60.8231 | 61.9812 | 3.3376 | 0.014738 | 0.013806 | 0.0055244 | 0.062461 | -0.0023519 | 0.070318 | -60.8551 | 61.7752 | -60.8871 | -60.9421 | 61.8942 | 0.19226 | -0.059509 | 0.15564 | 61.821 | -60.9192 | -0.064087 | -0.20599 | -0.032044 | -0.11902 | -0.086975 | -0.09613 | -0.16022 | 0.032043 | 60.7636 | 60.9787 | 122.7173 | 122.5983 | -0.032044 | 122.644 | 61.0153 | -0.09613 | 122.5983 | -0.032044 | 61.0153 | 122.7173 | 122.644 | -122.8683 | -122.9004
236.3281 | 123.1613 | -60.8139 | 61.9629 | -0.14908 | 0.019224 | 0.0073978 | 0.0018928 | 0.060539 | -0.0051291 | 0.070746 | -60.498 | 61.853 | -60.8414 | -60.9329 | 61.8393 | 0.12817 | -0.022888 | 0.15106 | 61.7935 | -60.9192 | -0.027466 | -0.10986 | 0.31586 | -0.11902 | -0.1236 | -0.10529 | -0.16937 | 0.34332 | 60.791 | 60.965 | 122.6532 | 122.6669 | 0.31586 | 122.6074 | 60.9421 | -0.10529 | 122.6669 | 0.31586 | 60.9421 | 122.6532 | 122.6074 | -122.8043 | -122.8821
237.3281 | 123.1293 | -60.8322 | 61.9629 | -0.065155 | 0.016874 | 0.0084658 | 0.0072332 | 0.062889 | -0.0032065 | 0.06925 | -60.8963 | 61.7981 | -60.8414 | -61.0336 | 61.8073 | 0.2243 | -0.11902 | 0.11902 | 61.8027 | -60.9375 | -0.009156 | -0.16479 | -0.064087 | -0.20142 | -0.15564 | -0.10529 | -0.16022 | -0.054931 | 60.7132 | 60.9512 | 122.6395 | 122.6303 | -0.064087 | 122.6349 | 61.0565 | -0.10529 | 122.6303 | -0.064087 | 61.0565 | 122.6395 | 122.6349 | -122.8043 | -122.9004
238.3281 | 123.0423 | -60.8551 | 62.0087 | -0.14145 | 0.018156 | 0.013593 | 0.0025336 | 0.062248 | -0.0057699 | 0.0716 | -61.0016 | 61.8393 | -60.8963 | -61.0565 | 61.5784 | 0.09613 | 0.42114 | -0.14648 | 61.8988 | -60.9695 | -0.041198 | -0.16937 | -0.14648 | -0.20142 | -0.4303 | -0.11444 | -0.10986 | -0.10529 | 61.2762 | 60.7086 | 122.4335 | 122.6944 | -0.14648 | 122.7539 | 60.9512 | -0.11444 | 122.6944 | -0.14648 | 60.9512 | 122.4335 | 122.7539 | -122.905 | -122.9782
239.3281 | 123.1567 | -60.8597 | 61.9492 | 0.018768 | 0.017729 | 0.01167 | 0.0027472 | 0.06182 | -0.0034201 | 0.068823 | -60.9467 | 61.7798 | -60.8963 | -61.0062 | 61.8576 | 0.13275 | -0.073242 | 0.09613 | 61.7935 | -60.9329 | -0.036621 | -0.16937 | -0.086975 | -0.14649 | -0.091553 | -0.073242 | -0.15564 | -0.050354 | 60.7864 | 60.9558 | 122.7173 | 122.6395 | -0.086975 | 122.6532 | 60.9924 | -0.073242 | 122.6395 | -0.086975 | 60.9924 | 122.7173 | 122.6532 | -122.8455 | -122.8821
240.3281 | 123.143 | -60.8139 | 61.9904 | -0.11093 | 0.016661 | 0.009534 | 0.0036018 | 0.062248 | -0.0032065 | 0.070532 | -60.9146 | 61.7981 | -60.8688 | -60.9558 | 61.908 | 0.1831 | -0.032043 | 0.16479 | 61.8164 | -60.9238 | -0.054931 | -0.19226 | -0.10071 | -0.14191 | -0.082397 | -0.10986 | -0.17395 | -0.045777 | 60.7819 | 60.9787 | 122.7219 | 122.612 | -0.10071 | 122.6303 | 60.997 | -0.10986 | 122.612 | -0.10071 | 60.997 | 122.7219 | 122.6303 | -122.8592 | -122.9141
241.3281 | 123.1796 | -60.8185 | 61.9492 | -0.11856 | 0.01837 | 0.016156 | 0.0012518 | 0.059471 | -0.0027793 | 0.069891 | -60.9238 | 61.7706 | -60.8734 | -60.9695 | 61.8896 | 0.17853 | -0.082397 | 0.14191 | 61.7981 | -60.9329 | -0.054932 | -0.17853 | -0.10529 | -0.15106 | -0.05951 | -0.11444 | -0.15106 | -0.050354 | 60.7361 | 60.9604 | 122.7081 | 122.5891 | -0.10529 | 122.6166 | 60.997 | -0.11444 | 122.5891 | -0.10529 | 60.997 | 122.7081 | 122.6166 | -122.8226 | -122.8821
242.3281 | 123.1567 | -60.8231 | 61.9537 | -0.4924 | 0.018583 | 0.013806 | 0.0036018 | 0.06118 | -0.0040609 | 0.06925 | -60.9512 | 61.7844 | -60.9146 | -60.9695 | 61.9263 | 0.18768 | -0.054932 | 0.16479 | 61.821 | -60.9558 | -0.091553 | -0.16937 | -0.12817 | -0.14648 | -0.027465 | -0.13275 | -0.13275 | -0.036621 | 60.7681 | 60.9879 | 122.7493 | 122.6074 | -0.12817 | 122.644 | 61.0107 | -0.13275 | 122.6074 | -0.12817 | 61.0107 | 122.7493 | 122.644 | -122.8683 | -122.9095
243.3281 | 123.1613 | -60.8368 | 61.9766 | 2.5441 | 0.016874 | 0.01167 | 0.0046698 | 0.062675 | -0.0047019 | 0.070532 | -60.8276 | 61.7752 | -60.8917 | -60.9558 | 61.8942 | 0.1831 | -0.068665 | 0.16479 | 61.8164 | -60.9146 | -0.054932 | -0.20142 | 0.009155 | -0.11902 | -0.082398 | -0.07782 | -0.16022 | 0.064087 | 60.7681 | 61.0016 | 122.731 | 122.612 | 0.009155 | 122.6532 | 61.0199 | -0.07782 | 122.612 | 0.009155 | 61.0199 | 122.731 | 122.6532 | -122.8683 | -122.8912
244.3281 | 123.1613 | -60.8093 | 61.9766 | -0.14145 | 0.017729 | 0.0086796 | 0.00082459 | 0.062248 | -0.0023519 | 0.070105 | -60.5438 | 61.8576 | -60.8459 | -60.9146 | 61.8759 | 0.1236 | -0.050354 | 0.15564 | 61.821 | -60.9329 | -0.036621 | -0.11902 | 0.2655 | -0.10529 | -0.10071 | -0.1236 | -0.15564 | 0.30212 | 60.759 | 60.965 | 122.6852 | 122.6669 | 0.2655 | 122.6303 | 60.9329 | -0.1236 | 122.6669 | 0.2655 | 60.9329 | 122.6852 | 122.6303 | -122.8226 | -122.9095
245.3281 | 123.1247 | -60.8414 | 61.972 | -0.027008 | 0.016447 | 0.0091068 | 0.003388 | 0.060966 | -0.0051291 | 0.069464 | -60.9375 | 61.7981 | -60.878 | -61.0107 | 61.8668 | 0.15564 | -0.068665 | 0.09613 | 61.8118 | -60.9329 | -0.036621 | -0.17395 | -0.09613 | -0.16937 | -0.10529 | -0.091552 | -0.16022 | -0.059509 | 60.7727 | 60.9375 | 122.7081 | 122.6395 | -0.09613 | 122.6532 | 60.997 | -0.091552 | 122.6395 | -0.09613 | 60.997 | 122.7081 | 122.6532 | -122.85 | -122.905
246.3281 | 123.1659 | -60.8459 | 61.9446 | 0.011139 | 0.017515 | 0.015515 | 0.0031744 | 0.061393 | -0.0029929 | 0.069891 | -60.9558 | 61.7798 | -60.9055 | -61.0016 | 61.8393 | 0.13733 | -0.064087 | 0.091553 | 61.7981 | -60.9283 | -0.05951 | -0.1648 | -0.10986 | -0.15564 | -0.10529 | -0.082398 | -0.14648 | -0.050354 | 60.7819 | 60.9375 | 122.6852 | 122.6257 | -0.10986 | 122.644 | 60.9833 | -0.082398 | 122.6257 | -0.10986 | 60.9833 | 122.6852 | 122.644 | -122.85 | -122.8729
247.3281 | 123.0972 | -60.8368 | 61.9446 | -0.080414 | 0.014097 | 0.012525 | 0.0018928 | 0.060966 | -0.0053427 | 0.070959 | -60.91 | 61.7615 | -60.8917 | -61.0062 | 62.2971 | 0.54474 | -0.4715 | -0.032043 | 61.821 | -60.9329 | -0.054932 | -0.18311 | -0.073242 | -0.16937 | 0.35248 | -0.09613 | -0.1236 | -0.01831 | 60.3653 | 60.8047 | 123.1338 | 122.5983 | -0.073242 | 122.6578 | 61.3815 | -0.09613 | 122.5983 | -0.073242 | 61.3815 | 123.1338 | 122.6578 | -122.8363 | -122.8775
248.3281 | 123.175 | -60.8459 | 61.9217 | -0.15671 | 0.017088 | 0.014661 | 0.0027472 | 0.060325 | -0.0025657 | 0.071386 | -60.9146 | 61.7752 | -60.8917 | -60.965 | 61.908 | 0.082397 | 0.43488 | 0.032043 | 61.8668 | -60.9009 | -0.045777 | -0.14648 | -0.068665 | -0.11902 | -0.013733 | -0.054932 | -0.054932 | -0.022888 | 61.2808 | 60.878 | 122.7539 | 122.6212 | -0.068665 | 122.7127 | 60.9283 | -0.054932 | 122.6212 | -0.068665 | 60.9283 | 122.7539 | 122.7127 | -122.8134 | -122.8226
249.3438 | 123.0469 | -60.8597 | 61.9904 | -0.21774 | 0.020078 | 0.01167 | 0.0046698 | 0.060325 | -0.0051291 | 0.06925 | -60.9329 | 61.8164 | -60.8551 | -61.0016 | 61.853 | 0.14648 | 0.045776 | 0.09613 | 61.8256 | -60.9512 | 0.004577 | -0.17395 | -0.073242 | -0.14191 | -0.13733 | -0.091553 | -0.16479 | -0.077819 | 60.9055 | 60.9558 | 122.7127 | 122.6761 | -0.073242 | 122.6852 | 61.0062 | -0.091553 | 122.6761 | -0.073242 | 61.0062 | 122.7127 | 122.6852 | -122.8455 | -122.9416
250.3281 | 123.1201 | -60.8276 | 61.9583 | -0.13382 | 0.015379 | 0.010816 | 0.003388 | 0.059898 | -0.0032065 | 0.070532 | -60.9238 | 61.7844 | -60.8643 | -60.965 | 61.8942 | 0.18768 | -0.050354 | 0.14191 | 61.8073 | -60.9375 | -0.036621 | -0.17395 | -0.09613 | -0.13733 | -0.064087 | -0.10986 | -0.15106 | -0.059509 | 60.7773 | 60.9695 | 122.7219 | 122.612 | -0.09613 | 122.6349 | 61.0153 | -0.10986 | 122.612 | -0.09613 | 61.0153 | 122.7219 | 122.6349 | -122.8226 | -122.8958
251.3281 | 123.143 | -60.8047 | 61.9583 | -0.11093 | 0.017729 | 0.013166 | 0.0042426 | 0.061393 | -0.0040609 | 0.067755 | -60.9238 | 61.8027 | -60.8688 | -60.9512 | 61.8942 | 0.16937 | -0.045776 | 0.14191 | 61.8301 | -60.9558 | -0.064086 | -0.15564 | -0.11902 | -0.14648 | -0.064087 | -0.15106 | -0.12817 | -0.054932 | 60.759 | 60.9467 | 122.699 | 122.6074 | -0.11902 | 122.6349 | 60.9741 | -0.15106 | 122.6074 | -0.11902 | 60.9741 | 122.699 | 122.6349 | -122.8271 | -122.9141
252.3438 | 123.0789 | -60.8871 | 62.0087 | -0.13382 | 0.021147 | 0.012097 | 0.006806 | 0.06182 | -0.0034201 | 0.06925 | -60.9238 | 61.8851 | -60.8963 | -61.0062 | 61.8164 | 0.11444 | 0.064087 | 0.022888 | 61.8622 | -60.9924 | -0.009155 | -0.1236 | -0.036621 | -0.11902 | -0.19226 | -0.10529 | -0.14648 | -0.027466 | 60.9512 | 60.91 | 122.7036 | 122.7722 | -0.036621 | 122.7493 | 61.0016 | -0.10529 | 122.7722 | -0.036621 | 61.0016 | 122.7036 | 122.7493 | -122.905 | -123.0011
253.3281 | 122.9919 | -60.8093 | 61.9675 | -0.088043 | 0.01837 | 0.014661 | -0.00024361 | 0.062675 | -0.0014975 | 0.069891 | -60.9146 | 61.7844 | -60.8871 | -60.9467 | 61.9125 | 0.21057 | -0.082397 | 0.53101 | 61.8484 | -60.8917 | -0.07782 | -0.1831 | -0.10529 | -0.13733 | -0.054931 | -0.082398 | -0.11902 | -0.027466 | 60.7269 | 61.3403 | 122.7219 | 122.5937 | -0.10529 | 122.6578 | 61.0199 | -0.082398 | 122.5937 | -0.10529 | 61.0199 | 122.7219 | 122.6578 | -122.8546 | -122.8592
254.3281 | 123.1338 | -60.8414 | 61.9766 | -0.14908 | 0.016874 | 0.016156 | 0.0016792 | 0.06182 | -0.0064109 | 0.067969 | -60.9238 | 61.7981 | -60.8688 | -60.9604 | 61.8805 | 0.19226 | -0.064087 | 0.14648 | 61.8439 | -60.9146 | -0.027465 | -0.17853 | -0.082397 | -0.11902 | -0.096131 | -0.073242 | -0.13275 | -0.054932 | 60.7773 | 60.9879 | 122.7219 | 122.6395 | -0.082397 | 122.6852 | 61.0336 | -0.073242 | 122.6395 | -0.082397 | 61.0336 | 122.7219 | 122.6852 | -122.8455 | -122.8912
255.3281 | 123.0606 | -60.8368 | 62.0132 | -0.20248 | 0.016233 | 0.0097476 | 0.0029608 | 0.060752 | -0.0029929 | 0.069677 | -60.9329 | 61.8301 | -60.878 | -61.0153 | 61.8576 | 0.14191 | 0.050354 | 0.091553 | 61.8393 | -60.9467 | -0.041199 | -0.18311 | -0.09613 | -0.17853 | -0.15564 | -0.10986 | -0.17395 | -0.054931 | 60.8871 | 60.9283 | 122.6944 | 122.6669 | -0.09613 | 122.6761 | 60.9787 | -0.10986 | 122.6669 | -0.09613 | 60.9787 | 122.6944 | 122.6761 | -122.8912 | -122.9599
256.3281 | 123.0652 | -60.8459 | 62.0132 | -0.19485 | 0.017515 | 0.01167 | 0.004029 | 0.063102 | -0.0038473 | 0.067328 | -60.9375 | 61.8347 | -60.8917 | -61.0245 | 61.8484 | 0.13275 | 0.041199 | 0.082397 | 61.853 | -60.9421 | -0.045777 | -0.17853 | -0.091553 | -0.17853 | -0.16479 | -0.096131 | -0.16022 | -0.045776 | 60.8871 | 60.9283 | 122.6944 | 122.6807 | -0.091553 | 122.699 | 60.9787 | -0.096131 | 122.6807 | -0.091553 | 60.9787 | 122.6944 | 122.699 | -122.905 | -122.9553
257.3281 | 123.0652 | -60.8231 | 61.9995 | -0.1796 | 0.017301 | 0.012311 | 0.0031744 | 0.060325 | -0.0057699 | 0.06925 | -60.9283 | 61.8439 | -60.9055 | -60.997 | 61.8484 | 0.14648 | 0.036621 | 0.10071 | 61.8301 | -60.9512 | -0.082398 | -0.15564 | -0.10529 | -0.17395 | -0.15106 | -0.12817 | -0.16937 | -0.022888 | 60.8597 | 60.9238 | 122.6715 | 122.6669 | -0.10529 | 122.6532 | 60.9695 | -0.12817 | 122.6669 | -0.10529 | 60.9695 | 122.6715 | 122.6532 | -122.905 | -122.9507
258.3281 | 123.0286 | -60.8597 | 61.9995 | -0.16434 | 0.020506 | 0.015088 | 0.0027472 | 0.063102 | -0.0055563 | 0.070959 | -60.9375 | 61.8256 | -60.8917 | -61.0153 | 61.8393 | 0.15564 | 0.045776 | 0.07782 | 61.8622 | -60.9558 | -0.032044 | -0.17395 | -0.07782 | -0.15564 | -0.16022 | -0.096131 | -0.13733 | -0.045776 | 60.9055 | 60.9375 | 122.699 | 122.6852 | -0.07782 | 122.7219 | 61.0153 | -0.096131 | 122.6852 | -0.07782 | 61.0153 | 122.699 | 122.7219 | -122.8912 | -122.9553
259.3281 | 123.1064 | -60.8322 | 61.9949 | -0.1796 | 0.016661 | 0.014875 | 0.00232 | 0.062889 | -0.0051291 | 0.067969 | -60.9055 | 61.821 | -60.8734 | -60.965 | 61.8988 | 0.20599 | -0.045776 | 0.14191 | 61.8393 | -60.9467 | -0.041199 | -0.17395 | -0.073243 | -0.13275 | -0.09613 | -0.11444 | -0.15564 | -0.032044 | 60.7864 | 60.9741 | 122.731 | 122.6532 | -0.073243 | 122.6715 | 61.0382 | -0.11444 | 122.6532 | -0.073243 | 61.0382 | 122.731 | 122.6715 | -122.8683 | -122.9416
260.3281 | 123.143 | -60.8597 | 61.94 | -0.088043 | 0.016233 | 0.007825 | 0.00232 | 0.060325 | -0.0040609 | 0.070959 | -60.9055 | 61.8118 | -60.8459 | -60.6125 | 62.2742 | 0.20599 | -0.32501 | 0.16937 | 61.7981 | -60.9604 | 0.013733 | -0.12817 | -0.045777 | 0.24719 | 0.33417 | -0.10071 | -0.14191 | -0.05951 | 60.5347 | 61.0291 | 123.1338 | 122.6715 | -0.045777 | 122.6578 | 61.0657 | -0.10071 | 122.6715 | -0.045777 | 61.0657 | 123.1338 | 122.6578 | -122.7859 | -122.9004
261.3281 | 123.0652 | -60.8551 | 61.9904 | -0.19485 | 0.017942 | 0.010602 | 0.0036018 | 0.062034 | -0.0044883 | 0.070746 | -60.9467 | 61.8118 | -60.8688 | -61.0062 | 61.821 | 0.15564 | 0.059509 | 0.059509 | 61.8805 | -60.9558 | -0.013732 | -0.17853 | -0.091552 | -0.15106 | -0.16937 | -0.10071 | -0.10986 | -0.07782 | 60.9146 | 60.9146 | 122.6761 | 122.6669 | -0.091552 | 122.7356 | 61.0107 | -0.10071 | 122.6669 | -0.091552 | 61.0107 | 122.6761 | 122.7356 | -122.8592 | -122.9462
262.3281 | 123.0469 | -60.8551 | 62.0041 | -0.18723 | 0.019224 | 0.017865 | 0.0036018 | 0.06118 | -0.0068381 | 0.069464 | -60.9375 | 61.853 | -60.8826 | -61.0016 | 61.8347 | 0.13275 | 0.059509 | 0.054932 | 61.8805 | -60.9512 | -0.027465 | -0.15106 | -0.082397 | -0.14648 | -0.16937 | -0.09613 | -0.1236 | -0.054932 | 60.9146 | 60.91 | 122.6898 | 122.7081 | -0.082397 | 122.7356 | 60.9879 | -0.09613 | 122.7081 | -0.082397 | 60.9879 | 122.6898 | 122.7356 | -122.8867 | -122.9553
263.3281 | 123.0469 | -60.8871 | 61.9904 | -0.21011 | 0.017942 | 0.010602 | 0.004029 | 0.060966 | -0.0038473 | 0.072027 | -60.7452 | 61.9125 | -60.8826 | -61.0565 | 61.7935 | 0.068665 | 0.12817 | 0.022888 | 61.8988 | -60.9879 | 0.004578 | -0.077819 | 0.14191 | -0.16937 | -0.19684 | -0.10071 | -0.091552 | 0.13733 | 61.0153 | 60.91 | 122.6807 | 122.7997 | 0.14191 | 122.7859 | 60.9558 | -0.10071 | 122.7997 | 0.14191 | 60.9558 | 122.6807 | 122.7859 | -122.8729 | -122.9782
264.3281 | 123.0194 | -60.8826 | 62.0224 | -1.9344 | 0.017088 | 0.015302 | 0.0059516 | 0.063743 | -0.0029929 | 0.069677 | -61.0886 | 61.9125 | -60.9009 | -61.084 | 61.7523 | 0.091553 | 0.10071 | 0.009155 | 61.9034 | -60.9741 | -0.018311 | -0.10986 | -0.20599 | -0.20142 | -0.27008 | -0.091553 | -0.11902 | -0.18768 | 60.9833 | 60.8917 | 122.6349 | 122.7951 | -0.20599 | 122.7859 | 60.9741 | -0.091553 | 122.7951 | -0.20599 | 60.9741 | 122.6349 | 122.7859 | -122.9233 | -122.9965
265.3281 | 123.0103 | -60.878 | 62.0041 | -1.4995 | 0.017515 | 0.010388 | 0.0055244 | 0.063529 | -0.0025657 | 0.069677 | -61.1664 | 61.8713 | -60.9238 | -61.0931 | 61.7661 | 0.10071 | 0.11444 | -0.009155 | 61.8942 | -60.9879 | -0.045776 | -0.13275 | -0.28839 | -0.21515 | -0.23804 | -0.10986 | -0.10986 | -0.24262 | 60.9924 | 60.8688 | 122.644 | 122.7493 | -0.28839 | 122.7722 | 60.9787 | -0.10986 | 122.7493 | -0.28839 | 60.9787 | 122.644 | 122.7722 | -122.9279 | -122.9919
266.3281 | 123.0652 | -60.8551 | 62.0132 | -0.20248 | 0.017942 | 0.01402 | 0.0031744 | 0.062889 | -0.0034201 | 0.070959 | -60.9421 | 61.8439 | -60.8826 | -61.0474 | 61.8256 | 0.12817 | 0.064087 | 0.036621 | 61.853 | -60.9558 | -0.027465 | -0.16937 | -0.086975 | -0.19226 | -0.18768 | -0.10071 | -0.16022 | -0.05951 | 60.9192 | 60.8917 | 122.6807 | 122.699 | -0.086975 | 122.7081 | 60.9833 | -0.10071 | 122.699 | -0.086975 | 60.9833 | 122.6807 | 122.7081 | -122.8958 | -122.9691
267.3281 | 123.0789 | -60.8734 | 62.0224 | -0.21011 | 0.019865 | 0.016797 | 0.0036018 | 0.062248 | -0.0017111 | 0.070532 | -60.9512 | 61.8393 | -60.8734 | -61.0153 | 61.821 | 0.13733 | 0.068665 | 0.032043 | 61.8896 | -60.965 | 0 | -0.18311 | -0.07782 | -0.14191 | -0.20142 | -0.091553 | -0.13275 | -0.07782 | 60.9421 | 60.9055 | 122.6944 | 122.7127 | -0.07782 | 122.7631 | 61.0107 | -0.091553 | 122.7127 | -0.07782 | 61.0107 | 122.6944 | 122.7631 | -122.8958 | -122.9874
268.3281 | 123.0011 | -60.8688 | 62.0132 | -0.1033 | 0.017515 | 0.013593 | 0.004029 | 0.063529 | -0.0049155 | 0.070318 | -60.9833 | 61.8805 | -60.9421 | -61.0657 | 61.7798 | 0.091553 | 0.091553 | -0.018311 | 61.8988 | -60.9741 | -0.073243 | -0.13275 | -0.11444 | -0.19684 | -0.23346 | -0.10529 | -0.11444 | -0.041198 | 60.9604 | 60.8505 | 122.6486 | 122.7493 | -0.11444 | 122.7676 | 60.9604 | -0.10529 | 122.7493 | -0.11444 | 60.9604 | 122.6486 | 122.7676 | -122.9553 | -122.9874
269.3438 | 123.1522 | -60.8551 | 61.9263 | 0.25528 | 0.018797 | 0.013379 | 0.0025336 | 0.066306 | -0.0044883 | 0.069037 | -60.9238 | 61.7889 | -60.9055 | -60.8505 | 61.9858 | 0.13275 | -0.21057 | 0.036621 | 61.821 | -60.9741 | -0.050354 | -0.13733 | -0.068664 | 0.004578 | 0.059509 | -0.11902 | -0.10529 | -0.01831 | 60.6445 | 60.8917 | 122.8409 | 122.644 | -0.068664 | 122.6761 | 60.9879 | -0.11902 | 122.644 | -0.068664 | 60.9879 | 122.8409 | 122.6761 | -122.8317 | -122.9004
270.3281 | 123.0286 | -60.8734 | 62.0224 | -0.14908 | 0.020078 | 0.010816 | 0.004029 | 0.06417 | -0.0027793 | 0.071173 | -60.9924 | 61.8988 | -60.9009 | -61.0748 | 61.7798 | 0.10529 | 0.082397 | -0.004578 | 61.8759 | -61.0062 | -0.027466 | -0.1236 | -0.11902 | -0.20142 | -0.24262 | -0.13275 | -0.14648 | -0.091553 | 60.9558 | 60.8688 | 122.6532 | 122.7722 | -0.11902 | 122.7493 | 60.9787 | -0.13275 | 122.7722 | -0.11902 | 60.9787 | 122.6532 | 122.7493 | -122.9233 | -123.0286
271.3281 | 123.0377 | -60.8826 | 62.0224 | -0.12619 | 0.020078 | 0.01167 | 0.0038154 | 0.06417 | -0.0032065 | 0.070959 | -60.9924 | 61.9492 | -60.8963 | -61.0748 | 61.7798 | 0.10986 | 0.086975 | -0.009155 | 61.8759 | -61.0153 | -0.013733 | -0.073242 | -0.10986 | -0.19226 | -0.24262 | -0.13275 | -0.14648 | -0.096131 | 60.9695 | 60.8734 | 122.6624 | 122.8317 | -0.10986 | 122.7585 | 60.9924 | -0.13275 | 122.8317 | -0.10986 | 60.9924 | 122.6624 | 122.7585 | -122.9187 | -123.0377
272.3281 | 123.0469 | -60.8597 | 62.0224 | -0.12619 | 0.019224 | 0.013806 | 0.0031744 | 0.065025 | -0.0042747 | 0.069891 | -60.9833 | 61.9034 | -60.8917 | -61.0703 | 61.7981 | 0.091553 | 0.073242 | -0.018311 | 61.8805 | -60.9833 | -0.032044 | -0.11902 | -0.1236 | -0.21057 | -0.2243 | -0.1236 | -0.14191 | -0.091552 | 60.9329 | 60.8414 | 122.6578 | 122.7631 | -0.1236 | 122.7402 | 60.9512 | -0.1236 | 122.7631 | -0.1236 | 60.9512 | 122.6578 | 122.7402 | -122.9141 | -123.0057
273.3281 | 123.0331 | -60.8688 | 61.9995 | 0.5452 | 0.020292 | 0.014875 | 0.0027472 | 0.063957 | 0.00021151 | 0.072241 | -60.9741 | 61.9125 | -60.9009 | -61.0931 | 61.7889 | 0.10529 | 0.10986 | -0.027466 | 61.8896 | -61.0016 | -0.032044 | -0.086975 | -0.10529 | -0.22431 | -0.21057 | -0.13275 | -0.10986 | -0.073242 | 60.9787 | 60.8414 | 122.6578 | 122.7814 | -0.10529 | 122.7585 | 60.9741 | -0.13275 | 122.7814 | -0.10529 | 60.9741 | 122.6578 | 122.7585 | -122.9004 | -123.0011
274.3438 | 123.0927 | -60.878 | 61.9446 | 0.23239 | 0.019865 | 0.015729 | 0.0055244 | 0.065879 | -0.0042747 | 0.070532 | -60.9741 | 61.8668 | -60.9329 | -61.0657 | 61.8027 | 0.054932 | -0.17853 | -0.091553 | 61.853 | -60.9833 | -0.054931 | -0.07782 | -0.09613 | -0.18768 | -0.14191 | -0.10528 | -0.091553 | -0.041199 | 60.6995 | 60.7864 | 122.6807 | 122.7448 | -0.09613 | 122.731 | 60.9329 | -0.10528 | 122.7448 | -0.09613 | 60.9329 | 122.6807 | 122.731 | -122.8775 | -122.9279
275.3281 | 123.0652 | -60.878 | 62.0041 | -0.16434 | 0.019438 | 0.018079 | 0.0036018 | 0.062034 | -0.0019247 | 0.069037 | -60.9741 | 61.9125 | -60.8963 | -61.0794 | 61.7935 | 0.11444 | 0.059509 | -0.022888 | 61.8805 | -61.0016 | -0.01831 | -0.091552 | -0.09613 | -0.20142 | -0.21057 | -0.1236 | -0.1236 | -0.07782 | 60.9375 | 60.8551 | 122.6715 | 122.7905 | -0.09613 | 122.7585 | 60.9924 | -0.1236 | 122.7905 | -0.09613 | 60.9924 | 122.6715 | 122.7585 | -122.9004 | -123.0057
276.3281 | 122.8912 | -60.8871 | 61.972 | -0.12619 | 0.021147 | 0.017865 | 0.005738 | 0.066947 | -0.00064309 | 0.070959 | -60.9283 | 61.9034 | -60.9329 | -61.0382 | 61.8118 | 0.1236 | -0.018311 | 0 | 61.8988 | -61.0199 | -0.045776 | -0.068665 | -0.041199 | -0.15106 | -0.16022 | -0.13275 | -0.073242 | 0.004577 | 60.8688 | 60.8871 | 122.699 | 122.7905 | -0.041199 | 122.7859 | 61.0107 | -0.13275 | 122.7905 | -0.041199 | 61.0107 | 122.699 | 122.7859 | -122.905 | -122.9919
277.3281 | 123.1522 | -60.9055 | 61.9949 | -0.14908 | 0.017729 | 0.019574 | 0.0046698 | 0.064384 | -0.0023519 | 0.070959 | -60.9421 | 61.8942 | -60.9055 | -61.0428 | 61.8393 | 0.1236 | -0.018311 | -0.068665 | 61.8576 | -61.0062 | 0 | -0.10071 | -0.036621 | -0.13733 | -0.15564 | -0.10071 | -0.13733 | -0.036621 | 60.8871 | 60.8368 | 122.7448 | 122.7997 | -0.036621 | 122.7631 | 61.0291 | -0.10071 | 122.7997 | -0.036621 | 61.0291 | 122.7448 | 122.7631 | -122.9004 | -123.0011
278.3281 | 123.1659 | -60.8688 | 61.9995 | -0.12619 | 0.022215 | 0.01637 | 0.004029 | 0.065666 | -0.0032065 | 0.068182 | -60.9558 | 61.94 | -60.9192 | -61.0336 | 61.821 | 0.13275 | -0.018311 | -0.21515 | 61.8576 | -61.0062 | -0.050354 | -0.05951 | -0.086976 | -0.1648 | -0.17853 | -0.13733 | -0.14191 | -0.036622 | 60.8505 | 60.6537 | 122.6898 | 122.8088 | -0.086976 | 122.7264 | 61.0016 | -0.13733 | 122.8088 | -0.086976 | 61.0016 | 122.6898 | 122.7264 | -122.9187 | -123.0057
279.3438 | 123.1338 | -60.8734 | 61.94 | 1.6515 | 0.017942 | 0.015943 | -2.9814e-05 | 0.067802 | -0.00085669 | 0.071386 | -60.8002 | 61.8256 | -60.9055 | -60.997 | 61.8805 | 0.11902 | -0.2655 | -0.032043 | 61.8118 | -60.9741 | -0.032044 | -0.11444 | 0.073242 | -0.1236 | -0.059509 | -0.10071 | -0.12817 | 0.10529 | 60.6079 | 60.8414 | 122.7539 | 122.699 | 0.073242 | 122.6852 | 60.9924 | -0.10071 | 122.699 | 0.073242 | 60.9924 | 122.7539 | 122.6852 | -122.8455 | -122.9141
280.3281 | 123.0469 | -60.8505 | 62.0041 | -0.15671 | 0.01901 | 0.015088 | 0.0027472 | 0.065025 | -0.0027793 | 0.06925 | -60.9695 | 61.9537 | -60.9009 | -61.0748 | 61.7935 | 0.11444 | 0.054932 | -0.018311 | 61.8896 | -61.0107 | -0.050354 | -0.050354 | -0.11902 | -0.2243 | -0.21057 | -0.16022 | -0.11444 | -0.068664 | 60.9055 | 60.8322 | 122.644 | 122.8043 | -0.11902 | 122.7402 | 60.965 | -0.16022 | 122.8043 | -0.11902 | 60.965 | 122.644 | 122.7402 | -122.905 | -123.0148
281.3281 | 123.143 | -60.8871 | 61.9904 | -0.095673 | 0.019438 | 0.013593 | 0.007447 | 0.066306 | -0.0049155 | 0.068823 | -60.9512 | 61.9217 | -60.9009 | -61.0428 | 61.8027 | 0.12817 | -0.018311 | -0.091553 | 61.8622 | -61.0062 | -0.013733 | -0.068664 | -0.064087 | -0.15564 | -0.18768 | -0.11902 | -0.12817 | -0.050354 | 60.8688 | 60.7956 | 122.6898 | 122.8088 | -0.064087 | 122.7493 | 61.0153 | -0.11902 | 122.8088 | -0.064087 | 61.0153 | 122.6898 | 122.7493 | -122.8912 | -122.9965
282.3281 | 123.1018 | -60.8963 | 62.0041 | -0.13382 | 0.018583 | 0.011884 | 0.003388 | 0.066306 | -0.0044883 | 0.069677 | -60.9375 | 61.94 | -60.8826 | -61.0336 | 61.8073 | 0.13275 | -0.013733 | -0.013733 | 61.9034 | -61.0107 | 0.013733 | -0.064087 | -0.041199 | -0.13733 | -0.19684 | -0.11444 | -0.10071 | -0.054932 | 60.8826 | 60.8826 | 122.7036 | 122.8363 | -0.041199 | 122.7997 | 61.0291 | -0.11444 | 122.8363 | -0.041199 | 61.0291 | 122.7036 | 122.7997 | -122.8867 | -123.0148
283.3281 | 123.056 | -60.8688 | 61.9858 | 0.026398 | 0.018156 | 0.017224 | 0.0046698 | 0.065025 | -0.0019247 | 0.072027 | -60.9467 | 61.9125 | -60.9055 | -61.0657 | 61.7935 | 0.10986 | -0.059509 | -0.054932 | 61.8896 | -61.0291 | -0.036622 | -0.073242 | -0.07782 | -0.19684 | -0.19226 | -0.16022 | -0.096131 | -0.041198 | 60.8093 | 60.8139 | 122.6624 | 122.7814 | -0.07782 | 122.7585 | 60.9787 | -0.16022 | 122.7814 | -0.07782 | 60.9787 | 122.6624 | 122.7585 | -122.8912 | -123.0148
284.3438 | 123.1613 | -60.8643 | 61.9217 | 0.21713 | 0.020506 | 0.014875 | -2.9814e-05 | 0.066734 | -0.0029929 | 0.070105 | -60.9512 | 61.8164 | -60.9146 | -61.0519 | 61.853 | 0.11444 | -0.2655 | -0.045776 | 61.8164 | -60.9924 | -0.050354 | -0.10529 | -0.086975 | -0.18768 | -0.068665 | -0.12817 | -0.10529 | -0.036621 | 60.5988 | 60.8185 | 122.7173 | 122.6807 | -0.086975 | 122.6807 | 60.9787 | -0.12817 | 122.6807 | -0.086975 | 60.9787 | 122.7173 | 122.6807 | -122.8363 | -122.9141
285.3281 | 123.0469 | -60.8643 | 61.972 | -0.065155 | 0.020078 | 0.014875 | 0.0046698 | 0.062889 | -0.0034201 | 0.068609 | -60.9467 | 61.94 | -60.8963 | -61.0428 | 61.8164 | 0.1236 | -0.073242 | -0.045776 | 61.8622 | -61.0474 | -0.032043 | -0.032044 | -0.082397 | -0.17853 | -0.15564 | -0.1831 | -0.10986 | -0.050354 | 60.791 | 60.8185 | 122.6807 | 122.8043 | -0.082397 | 122.7264 | 60.9879 | -0.1831 | 122.8043 | -0.082397 | 60.9879 | 122.6807 | 122.7264 | -122.8683 | -123.0194
286.3281 | 123.0698 | -60.878 | 61.9812 | 0.041657 | 0.018156 | 0.015729 | 0.0055244 | 0.065879 | -0.0017111 | 0.070105 | -60.9238 | 61.9308 | -60.9055 | -61.0382 | 61.8073 | 0.13275 | -0.068665 | -0.050354 | 61.8759 | -61.0428 | -0.027466 | -0.050354 | -0.045776 | -0.16022 | -0.17395 | -0.16479 | -0.10529 | -0.01831 | 60.8093 | 60.8276 | 122.6852 | 122.8088 | -0.045776 | 122.7539 | 61.0107 | -0.16479 | 122.8088 | -0.045776 | 61.0107 | 122.6852 | 122.7539 | -122.8867 | -123.024
287.3281 | 123.0927 | -60.8826 | 61.9812 | -0.14145 | 0.018156 | 0.015515 | 0.0038154 | 0.064598 | -0.0034201 | 0.070318 | -60.965 | 61.9171 | -60.9055 | -61.0474 | 61.8073 | 0.15106 | -0.022888 | -0.009155 | 61.8713 | -61.0245 | -0.022889 | -0.064087 | -0.082398 | -0.16479 | -0.17395 | -0.14191 | -0.10986 | -0.059509 | 60.8597 | 60.8734 | 122.6898 | 122.7997 | -0.082398 | 122.7539 | 61.0336 | -0.14191 | 122.7997 | -0.082398 | 61.0336 | 122.6898 | 122.7539 | -122.8867 | -123.0057
288.3281 | 123.0606 | -60.878 | 61.9904 | -0.14908 | 0.020078 | 0.018506 | 0.0053106 | 0.066093 | -0.0027793 | 0.069891 | -60.9695 | 61.9308 | -60.8963 | -61.0519 | 61.8164 | 0.16022 | -0.013733 | -0.032043 | 61.9034 | -61.0199 | -0.01831 | -0.059509 | -0.091552 | -0.17395 | -0.17395 | -0.14191 | -0.086975 | -0.073242 | 60.8643 | 60.8459 | 122.6944 | 122.8088 | -0.091552 | 122.7814 | 61.0382 | -0.14191 | 122.8088 | -0.091552 | 61.0382 | 122.6944 | 122.7814 | -122.8867 | -123.0103
289.3281 | 123.0515 | -60.8643 | 61.9858 | -0.065155 | 0.01901 | 0.017224 | 0.003388 | 0.065879 | -0.0019247 | 0.070105 | -60.8459 | 61.8988 | -60.9192 | -61.0291 | 61.7981 | 0.14648 | -0.054932 | -0.022888 | 61.8851 | -61.0245 | -0.054931 | -0.086975 | 0.018311 | -0.16479 | -0.18768 | -0.16022 | -0.10071 | 0.073242 | 60.8093 | 60.8414 | 122.6624 | 122.7631 | 0.018311 | 122.7493 | 61.0107 | -0.16022 | 122.7631 | 0.018311 | 61.0107 | 122.6624 | 122.7493 | -122.905 | -123.0103
290.3281 | 123.056 | -60.8551 | 61.9537 | -0.027008 | 0.020933 | 0.01637 | 0.0029608 | 0.066093 | -0.0012839 | 0.070746 | -60.9375 | 61.9263 | -60.9009 | -61.0657 | 61.8073 | 0.10986 | -0.082397 | -0.091553 | 61.8713 | -61.0199 | -0.045776 | -0.027465 | -0.082397 | -0.21057 | -0.14648 | -0.16479 | -0.082397 | -0.036621 | 60.7727 | 60.7636 | 122.6624 | 122.7814 | -0.082397 | 122.7264 | 60.965 | -0.16479 | 122.7814 | -0.082397 | 60.965 | 122.6624 | 122.7264 | -122.8546 | -122.9736
291.3438 | 123.0194 | -60.8734 | 61.9995 | -0.17197 | 0.019651 | 0.0091068 | 0.00082459 | 0.064598 | -0.0027793 | 0.069677 | -60.9879 | 61.9034 | -60.91 | -61.0931 | 61.7661 | 0.12817 | 0.036621 | -0.064087 | 61.8988 | -61.0153 | -0.036621 | -0.096131 | -0.11444 | -0.21973 | -0.23346 | -0.14191 | -0.10071 | -0.07782 | 60.91 | 60.8093 | 122.6395 | 122.7768 | -0.11444 | 122.7722 | 61.0016 | -0.14191 | 122.7768 | -0.11444 | 61.0016 | 122.6395 | 122.7722 | -122.9095 | -123.0148
292.3281 | 123.056 | -60.8826 | 61.9949 | -0.0041198 | 0.018156 | 0.014234 | 0.0055244 | 0.066734 | -0.0042747 | 0.069677 | -60.9283 | 61.908 | -60.9009 | -61.0382 | 61.8027 | 0.14191 | -0.09613 | -0.059509 | 61.8896 | -61.0336 | -0.018311 | -0.086975 | -0.045777 | -0.15564 | -0.19226 | -0.15106 | -0.10529 | -0.027466 | 60.7864 | 60.8231 | 122.6852 | 122.7905 | -0.045777 | 122.7722 | 61.0245 | -0.15106 | 122.7905 | -0.045777 | 61.0245 | 122.6852 | 122.7722 | -122.8958 | -123.0286
293.3281 | 123.0606 | -60.8597 | 61.9766 | -0.73654 | 0.021787 | 0.017865 | 0.0044562 | 0.067375 | -0.0038473 | 0.070532 | -60.9329 | 61.9354 | -60.8734 | -61.0474 | 61.8164 | 0.14648 | -0.09613 | -0.059509 | 61.8713 | -61.0291 | -0.013733 | -0.041199 | -0.073242 | -0.18768 | -0.16022 | -0.16937 | -0.10529 | -0.059509 | 60.7635 | 60.8002 | 122.6761 | 122.7951 | -0.073242 | 122.731 | 61.0062 | -0.16937 | 122.7951 | -0.073242 | 61.0062 | 122.6761 | 122.731 | -122.85 | -123.0057
294.3438 | 123.0011 | -60.8826 | 61.9766 | 0.095062 | 0.020933 | 0.018933 | 0.0063788 | 0.067802 | -0.0025657 | 0.071814 | -61.0016 | 61.908 | -60.9283 | -61.1252 | 61.7294 | 0.041199 | -0.07782 | -0.19226 | 61.9125 | -61.0382 | -0.045777 | -0.068665 | -0.11902 | -0.24262 | -0.24719 | -0.15564 | -0.064087 | -0.073242 | 60.8047 | 60.6903 | 122.612 | 122.7905 | -0.11902 | 122.7951 | 60.9238 | -0.15564 | 122.7905 | -0.11902 | 60.9238 | 122.612 | 122.7951 | -122.905 | -123.0148
295.3281 | 123.0789 | -60.8414 | 62.0132 | -0.019379 | 0.022215 | 0.017224 | 0.0055244 | 0.067375 | -0.0025657 | 0.072027 | -60.9421 | 61.9308 | -60.9055 | -61.1572 | 61.9858 | 0.29755 | -0.07782 | 0.022888 | 61.8988 | -61.0474 | -0.064087 | -0.082398 | -0.10071 | -0.31586 | -0.027466 | -0.20599 | -0.11444 | -0.036621 | 60.7635 | 60.8643 | 122.8271 | 122.7722 | -0.10071 | 122.7402 | 61.1389 | -0.20599 | 122.7722 | -0.10071 | 61.1389 | 122.8271 | 122.7402 | -122.9187 | -123.0606
296.3281 | 123.0469 | -60.8643 | 62.0132 | -0.088043 | 0.02136 | 0.012525 | 0.0044562 | 0.067161 | -0.0029929 | 0.069677 | -60.9375 | 61.9354 | -60.9009 | -61.0428 | 61.8256 | 0.17395 | -0.39368 | -0.16022 | 61.853 | -61.0428 | -0.036621 | -0.07782 | -0.073242 | -0.17853 | -0.18768 | -0.17853 | -0.16022 | -0.036621 | 60.4706 | 60.704 | 122.6898 | 122.7997 | -0.073242 | 122.7173 | 61.0382 | -0.17853 | 122.7997 | -0.073242 | 61.0382 | 122.6898 | 122.7173 | -122.9141 | -123.056
297.3281 | 123.0606 | -60.878 | 61.9675 | -0.011749 | 0.020078 | 0.012952 | 0.0046698 | 0.067161 | -0.00085669 | 0.069464 | -60.9421 | 61.9354 | -60.8917 | -61.0428 | 61.8027 | 0.16022 | -0.10986 | -0.086975 | 61.8942 | -61.0474 | -0.013733 | -0.032043 | -0.064087 | -0.16479 | -0.16479 | -0.16937 | -0.073242 | -0.050354 | 60.7681 | 60.791 | 122.6807 | 122.8134 | -0.064087 | 122.7722 | 61.0382 | -0.16937 | 122.8134 | -0.064087 | 61.0382 | 122.6807 | 122.7722 | -122.8592 | -123.0148
298.3281 | 123.0743 | -60.8551 | 61.9629 | 0.44601 | 0.020078 | 0.015729 | 0.0036018 | 0.067161 | -0.0017111 | 0.072027 | -60.9329 | 61.94 | -60.9283 | -61.0291 | 61.8073 | 0.16022 | -0.091553 | -0.091553 | 61.8805 | -61.0382 | -0.073242 | -0.022889 | -0.077819 | -0.17395 | -0.15564 | -0.1831 | -0.082398 | -0.004577 | 60.7636 | 60.7636 | 122.6624 | 122.7951 | -0.077819 | 122.7356 | 61.0153 | -0.1831 | 122.7951 | -0.077819 | 61.0153 | 122.6624 | 122.7356 | -122.8912 | -123.0011
299.3438 | 123.0148 | -60.9055 | 61.9766 | 0.087433 | 0.017515 | 0.019574 | 0.0053106 | 0.068229 | -0.0032065 | 0.070959 | -60.9924 | 61.9171 | -60.9238 | -61.116 | 61.7477 | 0.073242 | -0.091553 | -0.18768 | 61.9034 | -61.0382 | -0.01831 | -0.05951 | -0.086975 | -0.21057 | -0.22888 | -0.13275 | -0.073243 | -0.068665 | 60.8139 | 60.7178 | 122.6532 | 122.8226 | -0.086975 | 122.8088 | 60.9787 | -0.13275 | 122.8226 | -0.086975 | 60.9787 | 122.6532 | 122.8088 | -122.9004 | -123.0148
300.3281 | 123.0331 | -60.8826 | 62.0087 | -0.080414 | 0.020292 | 0.014447 | 0.00232 | 0.066306 | -0.0012839 | 0.070532 | -60.9558 | 61.9263 | -60.9238 | -61.0519 | 61.8942 | 0.12817 | -0.13733 | 0.068665 | 61.8622 | -61.0428 | -0.041199 | -0.082397 | -0.073243 | -0.16937 | -0.11444 | -0.16022 | -0.14648 | -0.032044 | 60.7452 | 60.9512 | 122.7768 | 122.8088 | -0.073243 | 122.7448 | 61.0107 | -0.16022 | 122.8088 | -0.073243 | 61.0107 | 122.7768 | 122.7448 | -122.9324 | -123.0515
301.3281 | 123.0286 | -60.8688 | 61.9949 | -0.14908 | 0.019651 | 0.014661 | 0.0025336 | 0.066093 | -0.00085669 | 0.070746 | -60.9879 | 61.9354 | -60.9009 | -61.0931 | 61.7661 | 0.15106 | 0 | -0.10529 | 61.9217 | -61.0245 | -0.032044 | -0.059509 | -0.11902 | -0.22431 | -0.22888 | -0.15564 | -0.073242 | -0.086975 | 60.8688 | 60.7635 | 122.6349 | 122.8043 | -0.11902 | 122.7905 | 61.0199 | -0.15564 | 122.8043 | -0.11902 | 61.0199 | 122.6349 | 122.7905 | -122.8958 | -123.0194
302.3281 | 123.0652 | -60.8688 | 62.0041 | -0.11856 | 0.018797 | 0.013593 | 0.0031744 | 0.067161 | -0.0034201 | 0.06925 | -60.965 | 61.9217 | -60.8917 | -61.0611 | 61.8027 | 0.19684 | -0.054932 | -0.082397 | 61.9217 | -61.0153 | -0.022889 | -0.082397 | -0.096131 | -0.19226 | -0.20142 | -0.14649 | -0.082397 | -0.073242 | 60.8139 | 60.7864 | 122.6715 | 122.7905 | -0.096131 | 122.7905 | 61.0657 | -0.14649 | 122.7905 | -0.096131 | 61.0657 | 122.6715 | 122.7905 | -122.8958 | -123.0194
303.3281 | 123.0515 | -60.8734 | 61.9904 | -0.15671 | 0.020506 | 0.01402 | 0.0014654 | 0.066306 | -0.0034201 | 0.070746 | -60.9833 | 61.94 | -60.8963 | -61.0474 | 61.8073 | 0.16937 | -0.036621 | -0.091553 | 61.9034 | -60.997 | -0.022888 | -0.050354 | -0.10986 | -0.17395 | -0.1831 | -0.1236 | -0.086975 | -0.086975 | 60.8368 | 60.7819 | 122.6807 | 122.8134 | -0.10986 | 122.7768 | 61.0428 | -0.1236 | 122.8134 | -0.10986 | 61.0428 | 122.6807 | 122.7768 | -122.8867 | -122.9874
304.3438 | 123.0377 | -60.9146 | 61.9766 | 0.22476 | 0.020078 | 0.015515 | 0.003388 | 0.06652 | -0.0014975 | 0.072241 | -61.0245 | 61.9263 | -60.9146 | -61.1343 | 61.7157 | 0.082397 | -0.17395 | -0.23346 | 61.8805 | -61.0336 | 0 | -0.050354 | -0.10986 | -0.21973 | -0.26093 | -0.11902 | -0.096131 | -0.10986 | 60.7407 | 60.6812 | 122.6303 | 122.8409 | -0.10986 | 122.7951 | 60.997 | -0.11902 | 122.8409 | -0.10986 | 60.997 | 122.6303 | 122.7951 | -122.8912 | -123.0103
305.3281 | 123.0103 | -60.9009 | 61.9858 | 0.079804 | 0.020292 | 0.014447 | 0.0029608 | 0.067161 | -0.00085669 | 0.0716 | -60.9879 | 61.9217 | -60.9055 | -61.1206 | 61.7477 | 0.091553 | -0.11902 | -0.21973 | 61.8942 | -61.0474 | -0.004578 | -0.064087 | -0.086975 | -0.21973 | -0.23804 | -0.14648 | -0.091553 | -0.082397 | 60.7819 | 60.6812 | 122.6486 | 122.8226 | -0.086975 | 122.7951 | 60.9924 | -0.14648 | 122.8226 | -0.086975 | 60.9924 | 122.6486 | 122.7951 | -122.8912 | -123.0331
306.3281 | 123.056 | -60.8551 | 61.9766 | -0.16434 | 0.020506 | 0.016797 | 0.0014654 | 0.063743 | -0.0040609 | 0.069464 | -60.9604 | 61.9263 | -60.9009 | -61.0703 | 61.7935 | 0.18768 | -0.054932 | -0.10986 | 61.9034 | -61.0336 | -0.045776 | -0.050354 | -0.10529 | -0.21515 | -0.18311 | -0.17853 | -0.073243 | -0.059509 | 60.8002 | 60.7452 | 122.6486 | 122.7814 | -0.10529 | 122.7585 | 61.0428 | -0.17853 | 122.7814 | -0.10529 | 61.0428 | 122.6486 | 122.7585 | -122.8775 | -123.0103
307.3281 | 123.0835 | -60.8734 | 61.9904 | -0.17197 | 0.021147 | 0.015302 | 0.00232 | 0.065025 | -0.0025657 | 0.070959 | -60.9879 | 61.9263 | -60.9238 | -61.0748 | 61.7981 | 0.1831 | -0.050354 | -0.10529 | 61.9171 | -61.0062 | -0.050354 | -0.064086 | -0.11444 | -0.20142 | -0.19226 | -0.13275 | -0.073242 | -0.064087 | 60.8231 | 60.7681 | 122.6715 | 122.7997 | -0.11444 | 122.7905 | 61.0565 | -0.13275 | 122.7997 | -0.11444 | 61.0565 | 122.6715 | 122.7905 | -122.9141 | -122.9965
308.3281 | 123.0377 | -60.8871 | 62.0041 | 1.1479 | 0.021574 | 0.012738 | -0.0013116 | 0.063316 | -0.0040609 | 0.0716 | -61.0748 | 61.9171 | -60.9009 | -61.1069 | 61.7935 | 0.20142 | -0.018311 | -0.13733 | 61.9263 | -61.0062 | -0.013733 | -0.086975 | -0.18768 | -0.21973 | -0.21057 | -0.11902 | -0.077819 | -0.17395 | 60.8688 | 60.7498 | 122.6807 | 122.8043 | -0.18768 | 122.8134 | 61.0886 | -0.11902 | 122.8043 | -0.18768 | 61.0886 | 122.6807 | 122.8134 | -122.905 | -123.0103
309.3438 | 123.024 | -60.8871 | 61.9583 | 0.20187 | 0.019651 | 0.014447 | 0.003388 | 0.064598 | -0.0027793 | 0.071173 | -61.0107 | 61.8851 | -60.9283 | -61.1206 | 61.7386 | 0.086975 | -0.23346 | -0.25635 | 61.8668 | -61.0107 | -0.041199 | -0.073242 | -0.1236 | -0.23346 | -0.21973 | -0.1236 | -0.091553 | -0.082397 | 60.6537 | 60.6308 | 122.6257 | 122.7722 | -0.1236 | 122.7539 | 60.9741 | -0.1236 | 122.7722 | -0.1236 | 60.9741 | 122.6257 | 122.7539 | -122.8867 | -122.9691
310.3281 | 123.0011 | -60.8551 | 62.0178 | -0.18723 | 0.018583 | 0.014661 | 0.0027472 | 0.062889 | -0.0014975 | 0.070746 | -61.0245 | 61.9308 | -60.9192 | -61.1023 | 61.7798 | 0.18768 | -0.036621 | -0.15106 | 61.8942 | -61.0336 | -0.064086 | -0.086975 | -0.16937 | -0.24719 | -0.23804 | -0.17853 | -0.1236 | -0.10529 | 60.8185 | 60.704 | 122.6349 | 122.7859 | -0.16937 | 122.7493 | 61.0428 | -0.17853 | 122.7859 | -0.16937 | 61.0428 | 122.6349 | 122.7493 | -122.937 | -123.0515
311.3281 | 123.056 | -60.8643 | 62.0224 | -0.14145 | 0.02136 | 0.013379 | 0.0042426 | 0.063957 | -0.0038473 | 0.070532 | -60.9833 | 61.9217 | -60.91 | -61.0703 | 61.7661 | 0.19684 | -0.050354 | -0.15106 | 61.9217 | -61.0153 | -0.045776 | -0.10071 | -0.11902 | -0.20599 | -0.25635 | -0.15106 | -0.10071 | -0.073242 | 60.8139 | 60.7132 | 122.6303 | 122.7859 | -0.11902 | 122.7859 | 61.0611 | -0.15106 | 122.7859 | -0.11902 | 61.0611 | 122.6303 | 122.7859 | -122.9324 | -123.0377
312.3281 | 123.0057 | -60.8734 | 62.0224 | -0.19485 | 0.020292 | 0.0093204 | 0.00232 | 0.064384 | -0.0017111 | 0.070959 | -60.9924 | 61.908 | -60.9238 | -61.084 | 61.7706 | 0.19684 | -0.054932 | -0.16937 | 61.9354 | -61.0107 | -0.050354 | -0.11444 | -0.11902 | -0.21057 | -0.25177 | -0.13733 | -0.086975 | -0.068665 | 60.8185 | 60.704 | 122.644 | 122.7814 | -0.11902 | 122.8088 | 61.0703 | -0.13733 | 122.7814 | -0.11902 | 61.0703 | 122.644 | 122.8088 | -122.9462 | -123.0331
313.3281 | 123.0469 | -60.8643 | 61.9995 | -0.14145 | 0.020933 | 0.012097 | 0.004029 | 0.064598 | -0.0027793 | 0.070105 | -60.997 | 61.9171 | -60.9055 | -61.0703 | 61.7844 | 0.18768 | -0.045776 | -0.16937 | 61.9308 | -61.0107 | -0.041199 | -0.082398 | -0.13275 | -0.20599 | -0.21515 | -0.14648 | -0.068665 | -0.091552 | 60.8185 | 60.6949 | 122.6486 | 122.7814 | -0.13275 | 122.7951 | 61.0519 | -0.14648 | 122.7814 | -0.13275 | 61.0519 | 122.6486 | 122.7951 | -122.905 | -123.0103
314.3438 | 123.1064 | -60.8597 | 61.9583 | 0.22476 | 0.022428 | 0.015729 | 0.003388 | 0.066093 | -0.0029929 | 0.070746 | -60.9879 | 61.8713 | -60.9192 | -61.0794 | 61.7661 | 0.14191 | -0.31128 | -0.25177 | 61.8713 | -61.0336 | -0.059509 | -0.086975 | -0.12817 | -0.21973 | -0.19226 | -0.17395 | -0.086975 | -0.068665 | 60.5484 | 60.6079 | 122.6257 | 122.731 | -0.12817 | 122.731 | 61.0016 | -0.17395 | 122.731 | -0.12817 | 61.0016 | 122.6257 | 122.731 | -122.8775 | -122.9919
315.3281 | 123.0515 | -60.8505 | 61.9904 | -0.1796 | 0.01901 | 0.010816 | 0.0010382 | 0.062248 | -0.0014975 | 0.071386 | -60.9329 | 61.8759 | -60.9192 | -61.0199 | 61.8347 | 0.25635 | -0.13733 | -0.10529 | 61.8713 | -60.9924 | -0.068664 | -0.11444 | -0.082397 | -0.16937 | -0.15564 | -0.14191 | -0.11902 | -0.013733 | 60.7132 | 60.7452 | 122.6852 | 122.7264 | -0.082397 | 122.7219 | 61.1069 | -0.14191 | 122.7264 | -0.082397 | 61.1069 | 122.6852 | 122.7219 | -122.9095 | -122.9828
316.3281 | 122.9599 | -60.8643 | 61.9949 | -0.14145 | 0.019865 | 0.011029 | 0.0014654 | 0.062461 | -0.0036337 | 0.069037 | -60.9695 | 61.8896 | -60.9009 | -61.084 | 61.7798 | 0.22888 | 0.009155 | 0.073242 | 61.972 | -60.9741 | -0.036621 | -0.10529 | -0.10529 | -0.21973 | -0.21515 | -0.10986 | -0.022888 | -0.068664 | 60.8734 | 60.9375 | 122.644 | 122.7539 | -0.10529 | 122.8363 | 61.0931 | -0.10986 | 122.7539 | -0.10529 | 61.0931 | 122.644 | 122.8363 | -122.8958 | -122.9691
317.3438 | 123.024 | -60.8643 | 62.0087 | -0.11093 | 0.020292 | 0.01402 | 0.007447 | 0.065025 | -0.0032065 | 0.070318 | -60.9329 | 61.9354 | -60.8917 | -61.0107 | 61.8027 | 0.22888 | -0.26093 | -0.43488 | 61.8713 | -61.0245 | -0.027466 | -0.073242 | -0.068664 | -0.14648 | -0.20599 | -0.16022 | -0.13733 | -0.041198 | 60.6033 | 60.4294 | 122.6669 | 122.7997 | -0.068664 | 122.7356 | 61.0931 | -0.16022 | 122.7997 | -0.068664 | 61.0931 | 122.6669 | 122.7356 | -122.9004 | -123.0331
318.3281 | 122.9965 | -60.8734 | 62.0041 | 0.37735 | 0.020292 | 0.013379 | 0.0021064 | 0.064811 | -0.0027793 | 0.069464 | -60.9695 | 61.9034 | -60.9238 | -61.1023 | 61.7615 | 0.21515 | -0.073242 | -0.19226 | 61.9308 | -60.997 | -0.050354 | -0.10071 | -0.09613 | -0.22888 | -0.24261 | -0.1236 | -0.073242 | -0.045776 | 60.8002 | 60.6812 | 122.6349 | 122.7768 | -0.09613 | 122.8043 | 61.0886 | -0.1236 | 122.7768 | -0.09613 | 61.0886 | 122.6349 | 122.8043 | -122.9279 | -123.0011
319.3438 | 123.0881 | -60.8459 | 61.9583 | 0.18662 | 0.016447 | 0.0097476 | -0.001098 | 0.063529 | -0.0012839 | 0.071386 | -60.9604 | 61.7935 | -60.9146 | -61.0565 | 61.8164 | 0.20599 | -0.35248 | -0.22888 | 61.8256 | -60.9924 | -0.068665 | -0.16479 | -0.11444 | -0.21057 | -0.14191 | -0.14648 | -0.13275 | -0.045776 | 60.4935 | 60.6171 | 122.6624 | 122.6395 | -0.11444 | 122.6715 | 61.0519 | -0.14648 | 122.6395 | -0.11444 | 61.0519 | 122.6624 | 122.6715 | -122.8729 | -122.9507
320.3281 | 123.0194 | -60.8688 | 62.0316 | -0.17197 | 0.01602 | 0.013166 | 0.0048834 | 0.062461 | -0.0029929 | 0.069891 | -61.084 | 61.9171 | -60.8734 | -61.1298 | 61.7798 | 0.25177 | -0.11902 | -0.21057 | 61.8851 | -61.0291 | -0.004578 | -0.11444 | -0.21515 | -0.26093 | -0.25177 | -0.16022 | -0.14648 | -0.21057 | 60.7498 | 60.6583 | 122.6486 | 122.7859 | -0.21515 | 122.7539 | 61.1206 | -0.16022 | 122.7859 | -0.21515 | 61.1206 | 122.6486 | 122.7539 | -122.905 | -123.0606
321.3438 | 123.0606 | -60.8871 | 61.9675 | 0.23239 | 0.020933 | 0.011884 | 0.0038154 | 0.064384 | -0.0042747 | 0.069037 | -60.9924 | 61.908 | -60.9283 | -61.0931 | 61.7477 | 0.13733 | -0.32501 | -0.32044 | 61.8668 | -61.0382 | -0.041199 | -0.059509 | -0.10529 | -0.20599 | -0.21973 | -0.15106 | -0.10071 | -0.064087 | 60.5621 | 60.5667 | 122.6349 | 122.7951 | -0.10529 | 122.7539 | 61.0245 | -0.15106 | 122.7951 | -0.10529 | 61.0245 | 122.6349 | 122.7539 | -122.8958 | -123.0057
322.3281 | 123.0698 | -60.8322 | 62.027 | -0.1796 | 0.017301 | 0.012952 | -2.9814e-05 | 0.06118 | -0.0032065 | 0.069891 | -60.9375 | 61.8668 | -60.8826 | -61.0107 | 61.853 | 0.3067 | -0.20599 | -0.13733 | 61.8713 | -60.9833 | -0.050354 | -0.16022 | -0.10529 | -0.17853 | -0.17395 | -0.15106 | -0.15564 | -0.054932 | 60.6262 | 60.6949 | 122.6852 | 122.699 | -0.10529 | 122.7036 | 61.1389 | -0.15106 | 122.699 | -0.10529 | 61.1389 | 122.6852 | 122.7036 | -122.9095 | -123.0103
323.3281 | 123.0423 | -60.8826 | 62.0178 | -0.19485 | 0.01837 | 0.014234 | 0.005738 | 0.063957 | -0.0038473 | 0.069464 | -60.9924 | 61.908 | -60.91 | -61.0703 | 61.7706 | 0.2243 | -0.10529 | -0.23804 | 61.8988 | -60.997 | -0.027466 | -0.10986 | -0.10986 | -0.18768 | -0.24719 | -0.11444 | -0.11902 | -0.082398 | 60.7773 | 60.6445 | 122.6532 | 122.7905 | -0.10986 | 122.7814 | 61.1069 | -0.11444 | 122.7905 | -0.10986 | 61.1069 | 122.6532 | 122.7814 | -122.9279 | -123.0148
324.3438 | 123.0423 | -60.8688 | 61.9904 | 0.17899 | 0.020506 | 0.014875 | 0.0046698 | 0.065025 | -0.0025657 | 0.069464 | -61.0199 | 61.9125 | -60.9512 | -61.1069 | 61.7294 | 0.14191 | -0.30212 | -0.36163 | 61.8668 | -61.0245 | -0.082398 | -0.077819 | -0.15106 | -0.23804 | -0.26093 | -0.15564 | -0.1236 | -0.068664 | 60.5667 | 60.5072 | 122.5983 | 122.7814 | -0.15106 | 122.7356 | 61.0107 | -0.15564 | 122.7814 | -0.15106 | 61.0107 | 122.5983 | 122.7356 | -122.9416 | -123.0148
325.3438 | 123.0743 | -60.8734 | 62.0041 | -0.14145 | 0.020078 | 0.012738 | 0.0036018 | 0.064384 | -0.0034201 | 0.070105 | -60.9558 | 61.9492 | -60.9146 | -61.0565 | 61.8118 | 0.25635 | -0.15106 | -0.24719 | 61.908 | -61.0107 | -0.041199 | -0.054931 | -0.082398 | -0.18311 | -0.19226 | -0.13733 | -0.09613 | -0.041199 | 60.7224 | 60.6262 | 122.6852 | 122.8226 | -0.082398 | 122.7814 | 61.1298 | -0.13733 | 122.8226 | -0.082398 | 61.1298 | 122.6852 | 122.7814 | -122.9187 | -123.0148
326.3438 | 123.0698 | -60.8688 | 62.0316 | 0.12558 | 0.019438 | 0.014875 | 0.0055244 | 0.064384 | -0.0019247 | 0.070318 | -61.0016 | 61.8988 | -60.91 | -61.1343 | 61.702 | 0.13733 | -0.52185 | -0.76446 | 61.8301 | -61.0794 | -0.041199 | -0.13275 | -0.13275 | -0.2655 | -0.32959 | -0.21057 | -0.20142 | -0.091553 | 60.347 | 60.1044 | 122.5708 | 122.7676 | -0.13275 | 122.699 | 61.0062 | -0.21057 | 122.7676 | -0.13275 | 61.0062 | 122.5708 | 122.699 | -122.9416 | -123.111
327.3438 | 123.0652 | -60.8688 | 61.9949 | -0.11856 | 0.019651 | 0.013593 | 0.0029608 | 0.066306 | -0.0027793 | 0.0716 | -60.9421 | 61.9217 | -60.8871 | -61.0291 | 61.821 | 0.27924 | -0.24261 | -0.23346 | 61.8896 | -61.0107 | -0.018311 | -0.073242 | -0.073243 | -0.16022 | -0.17395 | -0.14191 | -0.10529 | -0.054932 | 60.6262 | 60.6354 | 122.6898 | 122.7905 | -0.073243 | 122.7585 | 61.1481 | -0.14191 | 122.7905 | -0.073243 | 61.1481 | 122.6898 | 122.7585 | -122.8821 | -123.0057
328.3438 | 123.0011 | -60.8734 | 61.9858 | 0.087433 | 0.020292 | 0.013593 | 0.005738 | 0.064811 | -0.0017111 | 0.069464 | -61.0062 | 61.9354 | -60.9146 | -61.1389 | 61.7111 | 0.1831 | -0.27008 | -0.39825 | 61.9034 | -61.0657 | -0.041199 | -0.050354 | -0.13275 | -0.2655 | -0.27466 | -0.19226 | -0.082398 | -0.091553 | 60.6033 | 60.4752 | 122.5845 | 122.8088 | -0.13275 | 122.7768 | 61.0565 | -0.19226 | 122.8088 | -0.13275 | 61.0565 | 122.5845 | 122.7768 | -122.9004 | -123.0515
329.3594 | 123.0789 | -60.8459 | 61.9766 | -0.11093 | 0.021574 | 0.012738 | 0.0055244 | 0.065666 | -0.0023519 | 0.06925 | -60.9421 | 61.9446 | -60.8963 | -61.0245 | 61.8073 | 0.27466 | -0.29297 | -0.28381 | 61.8988 | -61.0474 | -0.050354 | -0.032044 | -0.096131 | -0.17853 | -0.16937 | -0.20142 | -0.07782 | -0.045777 | 60.553 | 60.5621 | 122.6532 | 122.7905 | -0.096131 | 122.7448 | 61.1206 | -0.20142 | 122.7905 | -0.096131 | 61.1206 | 122.6532 | 122.7448 | -122.8729 | -123.024
330.3438 | 122.9691 | -60.8963 | 61.9629 | 0.12558 | 0.018797 | 0.015088 | 0.0044562 | 0.065666 | -0.0040609 | 0.069464 | -60.9924 | 61.94 | -60.9238 | -61.1252 | 61.734 | 0.16937 | -0.27924 | -0.40283 | 61.8896 | -61.0428 | -0.027466 | -0.022889 | -0.096131 | -0.22888 | -0.22888 | -0.14648 | -0.073243 | -0.068665 | 60.6171 | 60.4935 | 122.6303 | 122.8363 | -0.096131 | 122.7859 | 61.0657 | -0.14648 | 122.8363 | -0.096131 | 61.0657 | 122.6303 | 122.7859 | -122.8867 | -123.0057
331.3438 | 123.0103 | -60.8826 | 61.9949 | 0.072174 | 0.020933 | 0.014234 | 0.004029 | 0.066093 | -0.0032065 | 0.070746 | -60.9879 | 61.972 | -60.9238 | -61.1114 | 61.7523 | 0.21515 | -0.31128 | -0.39825 | 61.8851 | -61.0703 | -0.041199 | -0.022888 | -0.10529 | -0.22888 | -0.24262 | -0.18768 | -0.10986 | -0.064087 | 60.5713 | 60.4843 | 122.6349 | 122.8546 | -0.10529 | 122.7676 | 61.0977 | -0.18768 | 122.8546 | -0.10529 | 61.0977 | 122.6349 | 122.7676 | -122.9187 | -123.0652
332.3438 | 123.1476 | -60.8276 | 61.9583 | 0.91141 | 0.017088 | 0.01402 | -0.0017388 | 0.063529 | -0.0019247 | 0.0716 | -60.8826 | 61.853 | -60.8917 | -61.0153 | 61.8393 | 0.29297 | -0.5127 | -0.29297 | 61.8073 | -61.0107 | -0.064087 | -0.10529 | -0.054931 | -0.18768 | -0.11902 | -0.1831 | -0.15106 | 0.009156 | 60.3149 | 60.5347 | 122.6669 | 122.6807 | -0.054931 | 122.6349 | 61.1206 | -0.1831 | 122.6807 | -0.054931 | 61.1206 | 122.6669 | 122.6349 | -122.85 | -122.9691
333.3438 | 123.0331 | -60.8688 | 61.9446 | 0.2095 | 0.020933 | 0.01402 | 0.004029 | 0.062675 | -0.0019247 | 0.069891 | -61.0153 | 61.9354 | -60.9421 | -61.1252 | 61.7294 | 0.18768 | -0.36621 | -0.42572 | 61.853 | -61.0703 | -0.073243 | -0.009155 | -0.14649 | -0.25635 | -0.21515 | -0.20142 | -0.091553 | -0.073242 | 60.5026 | 60.4431 | 122.5983 | 122.8043 | -0.14649 | 122.7219 | 61.0565 | -0.20142 | 122.8043 | -0.14649 | 61.0565 | 122.5983 | 122.7219 | -122.8867 | -123.0148
334.3594 | 123.024 | -60.878 | 62.0132 | 0.13321 | 0.019224 | 0.015088 | 0.0059516 | 0.063529 | -0.0027793 | 0.071814 | -60.9833 | 61.9354 | -60.9055 | -61.0977 | 61.7432 | 0.21973 | -0.3067 | -0.40283 | 61.8759 | -61.0474 | -0.027466 | -0.07782 | -0.10528 | -0.21973 | -0.27008 | -0.16937 | -0.13733 | -0.077819 | 60.5713 | 60.4752 | 122.6212 | 122.8134 | -0.10528 | 122.7539 | 61.0977 | -0.16937 | 122.8134 | -0.10528 | 61.0977 | 122.6212 | 122.7539 | -122.9187 | -123.0606
335.3594 | 123.0286 | -60.8826 | 62.0087 | 0.16373 | 0.02371 | 0.016156 | 0.0025336 | 0.062034 | -0.0029929 | 0.071386 | -61.0107 | 61.9308 | -60.9283 | -61.1343 | 61.7432 | 0.20142 | -0.3891 | -0.46234 | 61.8576 | -61.0565 | -0.045777 | -0.07782 | -0.12817 | -0.25177 | -0.2655 | -0.17395 | -0.15106 | -0.082397 | 60.4935 | 60.4202 | 122.6257 | 122.8134 | -0.12817 | 122.7402 | 61.084 | -0.17395 | 122.8134 | -0.12817 | 61.084 | 122.6257 | 122.7402 | -122.937 | -123.0652
336.3438 | 123.024 | -60.8414 | 61.9904 | 0.3392 | 0.019438 | 0.015088 | 0.0044562 | 0.063529 | -0.0027793 | 0.071386 | -61.0107 | 61.9308 | -60.9375 | -61.1389 | 61.7432 | 0.21515 | -0.37079 | -0.44861 | 61.8439 | -61.0428 | -0.09613 | -0.059509 | -0.16937 | -0.29755 | -0.24719 | -0.20142 | -0.14648 | -0.073242 | 60.4706 | 60.3928 | 122.5845 | 122.7722 | -0.16937 | 122.6852 | 61.0565 | -0.20142 | 122.7722 | -0.16937 | 61.0565 | 122.5845 | 122.6852 | -122.9279 | -123.0331
337.3438 | 122.9919 | -60.8826 | 61.9995 | 0.13321 | 0.020506 | 0.014661 | 0.0044562 | 0.066306 | -0.0038473 | 0.072882 | -60.997 | 61.94 | -60.9146 | -61.116 | 61.7386 | 0.25177 | -0.36621 | -0.45319 | 61.8622 | -61.0519 | -0.032044 | -0.05951 | -0.11444 | -0.23346 | -0.26093 | -0.16937 | -0.13733 | -0.082397 | 60.5164 | 60.4294 | 122.6212 | 122.8226 | -0.11444 | 122.7448 | 61.1343 | -0.16937 | 122.8226 | -0.11444 | 61.1343 | 122.6212 | 122.7448 | -122.9141 | -123.0515
338.3438 | 123.1613 | -60.8093 | 61.9675 | -0.042267 | 0.014952 | 0.010816 | -0.0030206 | 0.064384 | -0.0023519 | 0.072027 | -60.9604 | 61.8439 | -60.9009 | -61.0016 | 61.8576 | 0.38452 | -0.43945 | -0.28839 | 61.8713 | -60.965 | -0.091553 | -0.1236 | -0.15106 | -0.19226 | -0.10986 | -0.15564 | -0.09613 | -0.059509 | 60.3699 | 60.5209 | 122.6669 | 122.6532 | -0.15106 | 122.6807 | 61.1938 | -0.15564 | 122.6532 | -0.15106 | 61.1938 | 122.6669 | 122.6807 | -122.8683 | -122.9324
339.3438 | 123.111 | -60.8414 | 61.9675 | 0.24002 | 0.017088 | 0.01637 | 0.0018928 | 0.064811 | -0.0017111 | 0.0716 | -60.9695 | 61.8759 | -60.9009 | -61.0611 | 61.7889 | 0.28839 | -0.55389 | -0.42572 | 61.8347 | -60.9924 | -0.059509 | -0.091552 | -0.12817 | -0.21973 | -0.17853 | -0.15106 | -0.13275 | -0.068664 | 60.2875 | 60.4156 | 122.6303 | 122.7173 | -0.12817 | 122.6761 | 61.1298 | -0.15106 | 122.7173 | -0.12817 | 61.1298 | 122.6303 | 122.6761 | -122.8683 | -122.9599
340.3438 | 123.1567 | -60.8505 | 61.9675 | 0.18662 | 0.017088 | 0.012525 | -0.001098 | 0.06118 | -0.0049155 | 0.071173 | -60.9283 | 61.8393 | -60.9055 | -61.0245 | 61.8484 | 0.33417 | -0.59967 | -0.37537 | 61.8347 | -61.0199 | -0.054932 | -0.12817 | -0.07782 | -0.17395 | -0.11902 | -0.16937 | -0.13275 | -0.022888 | 60.2509 | 60.4752 | 122.699 | 122.6898 | -0.07782 | 122.6852 | 61.1847 | -0.16937 | 122.6898 | -0.07782 | 61.1847 | 122.699 | 122.6852 | -122.8729 | -122.9874
341.3438 | 123.1018 | -60.8276 | 61.9766 | 0.21713 | 0.01901 | 0.015943 | 0.0031744 | 0.062248 | -0.0027793 | 0.071386 | -60.9146 | 61.8439 | -60.8688 | -61.2305 | 61.9492 | 0.49896 | -0.63629 | -0.41199 | 61.8393 | -60.965 | -0.041198 | -0.13275 | -0.086975 | -0.40283 | -0.027466 | -0.13733 | -0.13733 | -0.045777 | 60.1913 | 60.4156 | 122.7768 | 122.6715 | -0.086975 | 122.6669 | 61.3266 | -0.13733 | 122.6715 | -0.086975 | 61.3266 | 122.7768 | 122.6669 | -122.8455 | -122.9416
342.3438 | 123.1247 | -60.8459 | 61.9583 | 0.20187 | 0.016447 | 0.012738 | 0.0029608 | 0.062675 | -0.0019247 | 0.070318 | -60.9192 | 61.8576 | -60.9009 | -61.0016 | 61.8576 | 0.36621 | -0.63171 | -0.39368 | 61.8118 | -60.9879 | -0.054932 | -0.10071 | -0.073242 | -0.15564 | -0.10071 | -0.14191 | -0.14648 | -0.01831 | 60.2142 | 60.4523 | 122.7036 | 122.7036 | -0.073242 | 122.6578 | 61.2122 | -0.14191 | 122.7036 | -0.073242 | 61.2122 | 122.7036 | 122.6578 | -122.8592 | -122.9462
343.3438 | 123.0469 | -60.8597 | 62.0132 | 0.026398 | 0.020933 | 0.012525 | 0.0070196 | 0.063957 | -0.0036337 | 0.071814 | -60.9467 | 61.908 | -60.91 | -61.0519 | 61.7798 | 0.34332 | -0.44861 | -0.45776 | 61.8668 | -61.0336 | -0.050354 | -0.10529 | -0.086975 | -0.19226 | -0.23346 | -0.17395 | -0.14648 | -0.036621 | 60.4111 | 60.4019 | 122.6395 | 122.7676 | -0.086975 | 122.7264 | 61.203 | -0.17395 | 122.7676 | -0.086975 | 61.203 | 122.6395 | 122.7264 | -122.9233 | -123.0469
344.3594 | 123.0927 | -60.8231 | 61.9446 | 0.25528 | 0.017088 | 0.015729 | 0.005097 | 0.064811 | -0.0025657 | 0.070746 | -60.9238 | 61.8668 | -60.8688 | -61.0245 | 61.821 | 0.37537 | -1.0071 | -0.31586 | 61.7844 | -61.0291 | -0.045776 | -0.07782 | -0.10071 | -0.20142 | -0.1236 | -0.20599 | -0.16022 | -0.054932 | 59.816 | 60.5072 | 122.644 | 122.6898 | -0.10071 | 122.6074 | 61.1984 | -0.20599 | 122.6898 | -0.10071 | 61.1984 | 122.644 | 122.6074 | -122.8134 | -122.9736
345.3438 | 123.0423 | -60.8871 | 61.9904 | 0.20187 | 0.020719 | 0.011457 | 0.0061652 | 0.063743 | -0.0019247 | 0.071386 | -60.997 | 61.9263 | -60.9238 | -61.0977 | 61.7386 | 0.27466 | -0.54016 | -0.54932 | 61.8805 | -61.0107 | -0.036621 | -0.064086 | -0.10986 | -0.21057 | -0.25177 | -0.1236 | -0.10986 | -0.073242 | 60.347 | 60.3378 | 122.6257 | 122.8134 | -0.10986 | 122.7676 | 61.1618 | -0.1236 | 122.8134 | -0.10986 | 61.1618 | 122.6257 | 122.7676 | -122.9141 | -123.0011
346.3438 | 123.1567 | -60.8459 | 61.9354 | 1.5065 | 0.020078 | 0.014661 | 0.0025336 | 0.063743 | -0.0027793 | 0.072668 | -60.7224 | 61.8439 | -60.878 | -60.9924 | 61.8576 | 0.35706 | -0.70496 | -0.44403 | 61.8256 | -60.9879 | -0.032044 | -0.091553 | 0.1236 | -0.14648 | -0.07782 | -0.14191 | -0.10986 | 0.15564 | 60.141 | 60.4019 | 122.7036 | 122.6898 | 0.1236 | 122.6715 | 61.203 | -0.14191 | 122.6898 | 0.1236 | 61.203 | 122.7036 | 122.6715 | -122.8134 | -122.9233
347.3438 | 123.1384 | -60.8414 | 61.9675 | 0.27817 | 0.019651 | 0.014661 | 0.0016792 | 0.062461 | -0.0019247 | 0.070318 | -60.9283 | 61.8439 | -60.9009 | -60.9787 | 61.8988 | 0.39368 | -0.737 | -0.44403 | 61.8347 | -61.0016 | -0.059509 | -0.1236 | -0.086975 | -0.13733 | -0.068664 | -0.16022 | -0.13275 | -0.027466 | 60.1044 | 60.3973 | 122.7402 | 122.6852 | -0.086975 | 122.6761 | 61.235 | -0.16022 | 122.6852 | -0.086975 | 61.235 | 122.7402 | 122.6761 | -122.8683 | -122.9691
348.3438 | 123.0881 | -60.8368 | 61.9904 | 0.75882 | 0.019438 | 0.013593 | -0.0019524 | 0.061607 | -0.0017111 | 0.071173 | -60.9604 | 61.8484 | -60.8826 | -61.0886 | 61.7935 | 0.37994 | -0.59052 | -0.49439 | 61.8393 | -60.9879 | -0.045776 | -0.14191 | -0.1236 | -0.25177 | -0.19684 | -0.15106 | -0.15106 | -0.07782 | 60.2463 | 60.3424 | 122.6303 | 122.6852 | -0.1236 | 122.6761 | 61.2167 | -0.15106 | 122.6852 | -0.1236 | 61.2167 | 122.6303 | 122.6761 | -122.8729 | -122.9782
349.3438 | 122.8592 | -60.8826 | 61.9125 | 0.10269 | 0.019865 | 0.017224 | 0.006806 | 0.062248 | -0.0010703 | 0.069464 | -60.997 | 61.9263 | -60.9238 | -61.116 | 61.7249 | 0.29297 | -0.52185 | -0.62256 | 61.8759 | -61.0565 | -0.041199 | 0.013733 | -0.11444 | -0.23346 | -0.18768 | -0.17395 | -0.036621 | -0.073242 | 60.3607 | 60.26 | 122.6074 | 122.8088 | -0.11444 | 122.7585 | 61.1755 | -0.17395 | 122.8088 | -0.11444 | 61.1755 | 122.6074 | 122.7585 | -122.8363 | -122.9691
350.3438 | 123.0698 | -60.8276 | 62.0224 | -0.11093 | 0.019438 | 0.015729 | 0.0059516 | 0.063529 | -0.0047019 | 0.06925 | -60.9329 | 61.9492 | -60.8963 | -61.0062 | 61.8164 | 0.4303 | -0.50812 | -0.48981 | 61.8896 | -60.9924 | -0.068664 | -0.073242 | -0.10528 | -0.17853 | -0.20599 | -0.16479 | -0.13275 | -0.036621 | 60.3195 | 60.3378 | 122.644 | 122.7768 | -0.10528 | 122.7173 | 61.2579 | -0.16479 | 122.7768 | -0.10528 | 61.2579 | 122.644 | 122.7173 | -122.9187 | -123.0148
351.3438 | 123.1018 | -60.8414 | 61.9675 | 0.072174 | 0.017729 | 0.015943 | -0.0019524 | 0.063316 | -0.0032065 | 0.069464 | -60.9695 | 61.8164 | -60.9238 | -60.965 | 61.5875 | 0.36163 | -0.67291 | -0.62256 | 61.8393 | -60.9467 | -0.082397 | -0.15106 | -0.12817 | -0.1236 | -0.37994 | -0.10529 | -0.12817 | -0.045776 | 60.1685 | 60.2188 | 122.4289 | 122.6578 | -0.12817 | 122.6807 | 61.203 | -0.10529 | 122.6578 | -0.12817 | 61.203 | 122.4289 | 122.6807 | -122.8912 | -122.9141
352.3438 | 123.1247 | -60.8139 | 61.9904 | -0.088043 | 0.016874 | 0.014447 | 0.0048834 | 0.060752 | -0.0044883 | 0.069464 | -60.8917 | 61.8347 | -60.8597 | -61.0428 | 61.853 | 0.58594 | -0.737 | -0.42572 | 61.8713 | -60.9375 | -0.045776 | -0.15564 | -0.07782 | -0.22888 | -0.13733 | -0.1236 | -0.11902 | -0.032044 | 60.0769 | 60.3882 | 122.6669 | 122.6486 | -0.07782 | 122.6852 | 61.3998 | -0.1236 | 122.6486 | -0.07782 | 61.3998 | 122.6669 | 122.6852 | -122.85 | -122.9279
353.3438 | 123.1384 | -60.8093 | 61.9583 | -0.034637 | 0.016874 | 0.015515 | 0.00082459 | 0.057548 | -0.0027793 | 0.070746 | -60.8871 | 61.8484 | -60.8505 | -61.2579 | 61.8713 | 0.60425 | -0.80109 | -0.40741 | 61.8668 | -60.9375 | -0.041199 | -0.10986 | -0.07782 | -0.44861 | -0.086975 | -0.12817 | -0.091553 | -0.036621 | 60.0082 | 60.4019 | 122.6807 | 122.6578 | -0.07782 | 122.6761 | 61.4136 | -0.12817 | 122.6578 | -0.07782 | 61.4136 | 122.6807 | 122.6761 | -122.8088 | -122.8958
354.3438 | 123.1247 | -60.8368 | 61.972 | 0.17899 | 0.016874 | 0.011457 | 0.0027472 | 0.062889 | -0.0025657 | 0.06925 | -60.9146 | 61.8027 | -60.9192 | -61.0016 | 61.8256 | 0.43488 | -0.79193 | -0.56763 | 61.8347 | -60.9695 | -0.082397 | -0.16937 | -0.07782 | -0.16479 | -0.14648 | -0.13275 | -0.13733 | 0.004577 | 60.0449 | 60.2692 | 122.6624 | 122.6395 | -0.07782 | 122.6715 | 61.2717 | -0.13275 | 122.6395 | -0.07782 | 61.2717 | 122.6624 | 122.6715 | -122.8912 | -122.9416
355.3438 | 123.0377 | -60.878 | 62.027 | 0.064545 | 0.020292 | 0.015515 | 0.0093696 | 0.064384 | -0.0053427 | 0.067969 | -60.9375 | 61.9263 | -60.8917 | -61.0748 | 61.734 | 0.3891 | -0.6134 | -0.65918 | 61.8942 | -61.0382 | -0.013733 | -0.10071 | -0.059509 | -0.19684 | -0.29297 | -0.16022 | -0.13275 | -0.045776 | 60.2646 | 60.2188 | 122.612 | 122.8043 | -0.059509 | 122.7722 | 61.2671 | -0.16022 | 122.8043 | -0.059509 | 61.2671 | 122.612 | 122.7722 | -122.9187 | -123.0652
356.3438 | 123.0194 | -60.8643 | 62.0178 | -0.26352 | 0.016661 | 0.015515 | 0.003388 | 0.060966 | -0.00085669 | 0.070105 | -60.9741 | 61.9125 | -60.8917 | -60.8368 | 61.6516 | 0.29297 | -0.50812 | -0.57678 | 61.908 | -61.0153 | -0.027466 | -0.10529 | -0.10986 | 0.027466 | -0.36621 | -0.15106 | -0.10986 | -0.082397 | 60.3561 | 60.2875 | 122.5159 | 122.7768 | -0.10986 | 122.7722 | 61.1572 | -0.15106 | 122.7768 | -0.10986 | 61.1572 | 122.5159 | 122.7722 | -122.9095 | -123.0331
357.3438 | 122.9828 | -60.878 | 62.027 | -0.18723 | 0.020506 | 0.010816 | 0.004029 | 0.061393 | -0.0029929 | 0.071386 | -60.9695 | 61.9171 | -60.8826 | -61.0291 | 62.027 | 0.63629 | -0.80566 | -0.62714 | 61.9263 | -60.9787 | -0.004577 | -0.10986 | -0.091552 | -0.15106 | 0 | -0.10071 | -0.10071 | -0.086975 | 60.0723 | 60.2509 | 122.905 | 122.7951 | -0.091552 | 122.8043 | 61.5143 | -0.10071 | 122.7951 | -0.091552 | 61.5143 | 122.905 | 122.8043 | -122.9095 | -123.0057
358.3438 | 123.056 | -60.8459 | 62.0178 | 0.0035097 | 0.018583 | 0.019147 | 0.0080878 | 0.065238 | -0.0023519 | 0.070105 | -60.9009 | 61.94 | -60.8826 | -61.0016 | 61.8073 | 0.48981 | -0.70038 | -0.63171 | 61.908 | -60.9924 | -0.036621 | -0.07782 | -0.054932 | -0.15564 | -0.21057 | -0.14648 | -0.10986 | -0.018311 | 60.1456 | 60.2142 | 122.6532 | 122.7859 | -0.054932 | 122.7539 | 61.3358 | -0.14648 | 122.7859 | -0.054932 | 61.3358 | 122.6532 | 122.7539 | -122.9004 | -123.0103
359.3438 | 123.1201 | -60.8368 | 61.94 | 0.17136 | 0.018156 | 0.016584 | 0.0018928 | 0.063529 | -0.0021383 | 0.070532 | -60.9283 | 61.8301 | -60.91 | -60.9924 | 61.8484 | 0.48523 | -0.88348 | -0.63171 | 61.8347 | -60.9695 | -0.073242 | -0.10986 | -0.091553 | -0.15564 | -0.091552 | -0.13275 | -0.10529 | -0.018311 | 59.9533 | 60.2051 | 122.6852 | 122.6669 | -0.091553 | 122.6715 | 61.322 | -0.13275 | 122.6669 | -0.091553 | 61.322 | 122.6852 | 122.6715 | -122.85 | -122.9095
360.3438 | 123.1018 | -60.8505 | 61.9583 | 0.24765 | 0.01901 | 0.015515 | 0.005738 | 0.064384 | -0.0032065 | 0.071814 | -60.965 | 61.908 | -60.9055 | -61.0474 | 61.7889 | 0.43488 | -0.85144 | -0.72784 | 61.8668 | -61.0245 | -0.054932 | -0.050354 | -0.11444 | -0.19684 | -0.16937 | -0.17395 | -0.091553 | -0.059509 | 59.9991 | 60.1227 | 122.6395 | 122.7585 | -0.11444 | 122.7173 | 61.2854 | -0.17395 | 122.7585 | -0.11444 | 61.2854 | 122.6395 | 122.7173 | -122.8638 | -122.9828
361.3438 | 123.024 | -60.8643 | 61.9995 | 0.17136 | 0.019651 | 0.012738 | 0.0038154 | 0.062461 | -0.0040609 | 0.070959 | -60.9924 | 61.9537 | -60.9283 | -61.1206 | 61.7386 | 0.41199 | -0.75073 | -0.79193 | 61.8759 | -61.0245 | -0.064087 | -0.045777 | -0.12817 | -0.25635 | -0.26093 | -0.16022 | -0.1236 | -0.064087 | 60.1135 | 60.0723 | 122.6028 | 122.818 | -0.12817 | 122.7402 | 61.2762 | -0.16022 | 122.818 | -0.12817 | 61.2762 | 122.6028 | 122.7402 | -122.9279 | -123.024
362.3438 | 123.0423 | -60.878 | 61.9949 | 0.22476 | 0.019438 | 0.015302 | 0.0044562 | 0.063743 | -0.0014975 | 0.0716 | -61.0107 | 61.9446 | -60.9283 | -61.1206 | 61.7477 | 0.41199 | -0.76446 | -0.8194 | 61.8759 | -61.0428 | -0.050354 | -0.050354 | -0.13275 | -0.24261 | -0.24719 | -0.16479 | -0.11902 | -0.082397 | 60.1135 | 60.0586 | 122.6257 | 122.8226 | -0.13275 | 122.7539 | 61.29 | -0.16479 | 122.8226 | -0.13275 | 61.29 | 122.6257 | 122.7539 | -122.9233 | -123.0377
363.3438 | 123.0881 | -60.8368 | 61.9675 | 0.24765 | 0.020078 | 0.015088 | 0.0044562 | 0.062675 | -0.0029929 | 0.069891 | -60.9741 | 61.9263 | -60.9375 | -61.0794 | 61.7615 | 0.48523 | -0.86975 | -0.80109 | 61.8393 | -61.0107 | -0.10071 | -0.041198 | -0.13733 | -0.24262 | -0.20599 | -0.17395 | -0.12817 | -0.036621 | 59.967 | 60.0357 | 122.5983 | 122.7631 | -0.13733 | 122.6761 | 61.322 | -0.17395 | 122.7631 | -0.13733 | 61.322 | 122.5983 | 122.6761 | -122.905 | -122.9782
364.3438 | 123.0698 | -60.8276 | 61.9949 | 0.095062 | 0.019438 | 0.011884 | -0.0030206 | 0.060111 | -0.0019247 | 0.071173 | -60.9879 | 61.8713 | -60.9146 | -61.0199 | 61.8118 | 0.43488 | -0.84228 | -0.7782 | 61.853 | -60.9833 | -0.086975 | -0.1236 | -0.16022 | -0.19226 | -0.1831 | -0.15564 | -0.14191 | -0.073242 | 59.9854 | 60.0494 | 122.6395 | 122.699 | -0.16022 | 122.6807 | 61.2625 | -0.15564 | 122.699 | -0.16022 | 61.2625 | 122.6395 | 122.6807 | -122.9095 | -122.9782
365.3438 | 123.0881 | -60.8551 | 62.0224 | 0.81223 | 0.021147 | 0.0099612 | 0.0070196 | 0.060752 | -0.0040609 | 0.069464 | -60.8093 | 61.9812 | -60.8643 | -61.0062 | 61.8393 | 0.57678 | -0.82398 | -0.737 | 61.8896 | -61.0016 | -0.009155 | -0.041199 | 0.045777 | -0.15106 | -0.18311 | -0.14648 | -0.13275 | 0.054932 | 60.0311 | 60.1181 | 122.6944 | 122.8363 | 0.045777 | 122.7448 | 61.4319 | -0.14648 | 122.8363 | 0.045777 | 61.4319 | 122.6944 | 122.7448 | -122.8867 | -123.024
366.3438 | 123.1155 | -60.8322 | 61.9583 | 0.17136 | 0.020506 | 0.018506 | 0.00061099 | 0.062889 | -0.0017111 | 0.073095 | -60.9238 | 61.8439 | -60.8963 | -61.0199 | 61.8118 | 0.55847 | -0.98877 | -0.7782 | 61.8393 | -60.9512 | -0.064087 | -0.11444 | -0.091553 | -0.18768 | -0.14648 | -0.11902 | -0.11902 | -0.027466 | 59.8434 | 60.054 | 122.644 | 122.6761 | -0.091553 | 122.6715 | 61.3907 | -0.11902 | 122.6761 | -0.091553 | 61.3907 | 122.644 | 122.6715 | -122.8546 | -122.9095
367.3438 | 123.0194 | -60.8734 | 62.0178 | 0.072174 | 0.018797 | 0.013379 | 0.005738 | 0.063529 | -0.0010703 | 0.070318 | -60.9741 | 61.9583 | -60.8917 | -61.0886 | 61.7432 | 0.48981 | -0.83771 | -0.88806 | 61.908 | -60.997 | -0.018311 | -0.059509 | -0.10071 | -0.21515 | -0.27466 | -0.1236 | -0.10986 | -0.082397 | 60.0357 | 59.9854 | 122.6166 | 122.8317 | -0.10071 | 122.7814 | 61.3632 | -0.1236 | 122.8317 | -0.10071 | 61.3632 | 122.6166 | 122.7814 | -122.9095 | -123.0148
368.3438 | 123.1476 | -60.8459 | 61.9766 | 0.23239 | 0.020292 | 0.01402 | 0.0044562 | 0.065238 | -0.0012839 | 0.070959 | -60.9146 | 61.8759 | -60.8963 | -61.0107 | 61.8256 | 0.58136 | -1.0666 | -0.81024 | 61.8301 | -60.9924 | -0.050354 | -0.10071 | -0.068665 | -0.16479 | -0.15106 | -0.14648 | -0.14648 | -0.018311 | 59.7794 | 60.0357 | 122.6715 | 122.7219 | -0.068665 | 122.6761 | 61.4273 | -0.14648 | 122.7219 | -0.068665 | 61.4273 | 122.6715 | 122.6761 | -122.8729 | -122.9691
369.3438 | 123.1018 | -60.7956 | 61.9675 | 0.18662 | 0.015592 | 0.013166 | 0.00232 | 0.060966 | -0.0027793 | 0.071386 | -60.9238 | 61.8576 | -60.8963 | -61.0062 | 61.8393 | 0.60883 | -1.0574 | -0.83313 | 61.8347 | -60.9695 | -0.10071 | -0.10986 | -0.12817 | -0.21057 | -0.12817 | -0.17395 | -0.13275 | -0.027466 | 59.7382 | 59.9625 | 122.6349 | 122.6532 | -0.12817 | 122.6303 | 61.4044 | -0.17395 | 122.6532 | -0.12817 | 61.4044 | 122.6349 | 122.6303 | -122.8638 | -122.937
370.3438 | 123.024 | -60.8597 | 61.972 | 0.21713 | 0.019651 | 0.017438 | 0.0072332 | 0.063957 | -0.0023519 | 0.071173 | -60.9833 | 61.9125 | -60.9055 | -61.084 | 61.7523 | 0.53101 | -0.98877 | -0.95673 | 61.9125 | -61.0199 | -0.045777 | -0.059509 | -0.1236 | -0.2243 | -0.21973 | -0.16022 | -0.059509 | -0.077819 | 59.8709 | 59.903 | 122.612 | 122.7722 | -0.1236 | 122.7722 | 61.3907 | -0.16022 | 122.7722 | -0.1236 | 61.3907 | 122.612 | 122.7722 | -122.8775 | -122.9919
371.3438 | 123.0194 | -60.8688 | 62.0224 | 0.018768 | 0.021147 | 0.014234 | 0.0078742 | 0.063529 | -0.0034201 | 0.070318 | -60.9604 | 61.9583 | -60.9009 | -61.0748 | 61.7477 | 0.55389 | -0.92468 | -0.95673 | 61.8851 | -61.0062 | -0.032044 | -0.064087 | -0.091553 | -0.20599 | -0.27466 | -0.13733 | -0.13733 | -0.059509 | 59.9442 | 59.9121 | 122.6166 | 122.8271 | -0.091553 | 122.7539 | 61.4227 | -0.13733 | 122.8271 | -0.091553 | 61.4227 | 122.6166 | 122.7539 | -122.9233 | -123.0286
372.3438 | 123.1338 | -60.8231 | 61.9812 | 0.20187 | 0.018156 | 0.016156 | 0.0027472 | 0.066947 | -0.00064309 | 0.069677 | -60.9329 | 61.8896 | -60.8871 | -61.0153 | 61.8164 | 0.61798 | -1.1627 | -0.9201 | 61.8393 | -60.965 | -0.064087 | -0.091553 | -0.10986 | -0.19226 | -0.16479 | -0.14191 | -0.14191 | -0.045776 | 59.6603 | 59.903 | 122.6395 | 122.7127 | -0.10986 | 122.6624 | 61.441 | -0.14191 | 122.7127 | -0.10986 | 61.441 | 122.6395 | 122.6624 | -122.8683 | -122.9462
373.3438 | 123.1201 | -60.8231 | 61.9583 | 0.19424 | 0.017942 | 0.01637 | 0.00061099 | 0.064384 | -0.0014975 | 0.070318 | -60.9192 | 61.8622 | -60.8917 | -61.0016 | 61.8484 | 0.66834 | -1.1627 | -0.90179 | 61.8484 | -60.9833 | -0.068665 | -0.09613 | -0.09613 | -0.17853 | -0.10986 | -0.16022 | -0.10986 | -0.027465 | 59.6603 | 59.9213 | 122.6715 | 122.6852 | -0.09613 | 122.6715 | 61.4914 | -0.16022 | 122.6852 | -0.09613 | 61.4914 | 122.6715 | 122.6715 | -122.85 | -122.9416
374.3438 | 123.143 | -60.7956 | 61.9858 | -0.11093 | 0.018583 | 0.01167 | 0.00082459 | 0.060325 | -0.0032065 | 0.069037 | -60.8688 | 61.8347 | -60.8505 | -60.9238 | 61.908 | 0.78735 | -0.67749 | -0.48981 | 61.9812 | -60.878 | -0.054932 | -0.15106 | -0.073242 | -0.12817 | -0.07782 | -0.082398 | -0.004578 | -0.01831 | 60.1181 | 60.3058 | 122.7036 | 122.6303 | -0.073242 | 122.7768 | 61.5829 | -0.082398 | 122.6303 | -0.073242 | 61.5829 | 122.7036 | 122.7768 | -122.8363 | -122.8638
375.3438 | 123.0194 | -60.8734 | 61.9995 | 0.14084 | 0.017729 | 0.015729 | 0.008515 | 0.061607 | -0.0038473 | 0.070746 | -61.3815 | 61.8988 | -60.9192 | -61.1252 | 61.7889 | 0.64087 | -1.0529 | -1.0803 | 61.94 | -61.0107 | -0.045776 | -0.10071 | -0.50812 | -0.25177 | -0.21057 | -0.13733 | -0.05951 | -0.46234 | 59.8206 | 59.7931 | 122.6624 | 122.7722 | -0.50812 | 122.8134 | 61.5143 | -0.13733 | 122.7722 | -0.50812 | 61.5143 | 122.6624 | 122.8134 | -122.9187 | -123.0103
376.3438 | 123.1201 | -60.8368 | 61.9629 | 0.21713 | 0.020078 | 0.017224 | 0.005738 | 0.065025 | -0.0047019 | 0.069464 | -60.9375 | 61.8805 | -60.8871 | -61.0107 | 61.821 | 0.67749 | -1.2497 | -1.0254 | 61.8668 | -60.9741 | -0.050354 | -0.082398 | -0.10071 | -0.17395 | -0.14191 | -0.13733 | -0.096131 | -0.050354 | 59.5871 | 59.8114 | 122.6578 | 122.7173 | -0.10071 | 122.7036 | 61.5143 | -0.13733 | 122.7173 | -0.10071 | 61.5143 | 122.6578 | 122.7036 | -122.85 | -122.937
377.3438 | 123.1293 | -60.8002 | 61.9675 | -0.233 | 0.017729 | 0.012952 | 0.0021064 | 0.062034 | -0.0040609 | 0.070532 | -60.9146 | 61.8576 | -60.8688 | -60.9787 | 61.8439 | 0.73242 | -1.2817 | -0.98419 | 61.8347 | -60.9879 | -0.068664 | -0.10986 | -0.11444 | -0.17853 | -0.1236 | -0.18768 | -0.13275 | -0.045777 | 59.5184 | 59.816 | 122.644 | 122.6578 | -0.11444 | 122.6349 | 61.5326 | -0.18768 | 122.6578 | -0.11444 | 61.5326 | 122.644 | 122.6349 | -122.8363 | -122.9553
378.3438 | 123.1613 | -60.8139 | 61.9675 | 0.24002 | 0.017088 | 0.014875 | 0.005738 | 0.06417 | -0.0023519 | 0.071386 | -60.9421 | 61.8713 | -60.8871 | -61.0107 | 61.8027 | 0.71869 | -1.2772 | -1.0941 | 61.8393 | -60.9924 | -0.073242 | -0.09613 | -0.12817 | -0.19684 | -0.16479 | -0.17853 | -0.12817 | -0.054932 | 59.5367 | 59.7198 | 122.6166 | 122.6852 | -0.12817 | 122.6532 | 61.5326 | -0.17853 | 122.6852 | -0.12817 | 61.5326 | 122.6166 | 122.6532 | -122.8546 | -122.9599
379.3438 | 123.0927 | -60.8276 | 61.9858 | 0.14084 | 0.016447 | 0.013379 | -0.0013116 | 0.06118 | -0.0021383 | 0.072668 | -60.9695 | 61.8393 | -60.8826 | -61.0336 | 61.8118 | 0.73242 | -1.2497 | -1.062 | 61.853 | -60.965 | -0.054931 | -0.14648 | -0.14191 | -0.20599 | -0.17395 | -0.13733 | -0.13275 | -0.086975 | 59.5779 | 59.7656 | 122.6395 | 122.6669 | -0.14191 | 122.6807 | 61.5601 | -0.13733 | 122.6669 | -0.14191 | 61.5601 | 122.6395 | 122.6807 | -122.8683 | -122.9507
380.3438 | 122.9782 | -60.7819 | 62.0087 | -0.14145 | 0.018156 | 0.011243 | 0.0014654 | 0.059898 | -0.0019247 | 0.070318 | -60.878 | 61.8484 | -60.8505 | -60.9329 | 61.9171 | 0.87891 | -1.2543 | -0.67749 | 61.9171 | -60.9238 | -0.068665 | -0.16022 | -0.096131 | -0.15106 | -0.091553 | -0.14191 | -0.091553 | -0.027466 | 59.5276 | 60.1044 | 122.699 | 122.6303 | -0.096131 | 122.699 | 61.6608 | -0.14191 | 122.6303 | -0.096131 | 61.6608 | 122.699 | 122.699 | -122.8592 | -122.9324
381.3438 | 123.1476 | -60.8002 | 61.972 | 0.2858 | 0.018156 | 0.016156 | 0.003388 | 0.06118 | -0.0044883 | 0.069037 | -60.9009 | 61.8713 | -60.8322 | -60.9879 | 61.8484 | 0.79193 | -1.3962 | -1.1078 | 61.8301 | -60.9741 | -0.032043 | -0.10071 | -0.10071 | -0.18768 | -0.1236 | -0.17395 | -0.14191 | -0.068665 | 59.404 | 59.6924 | 122.6486 | 122.6715 | -0.10071 | 122.6303 | 61.5921 | -0.17395 | 122.6715 | -0.10071 | 61.5921 | 122.6486 | 122.6303 | -122.8043 | -122.9462
382.3438 | 123.1247 | -60.8093 | 62.0041 | 0.018768 | 0.01837 | 0.01402 | -0.00024361 | 0.060966 | -0.0025657 | 0.070746 | -60.9238 | 61.8622 | -60.8826 | -60.9833 | 61.8622 | 0.8606 | -1.3092 | -1.0849 | 61.8622 | -60.9558 | -0.073242 | -0.14191 | -0.11444 | -0.17395 | -0.14191 | -0.14648 | -0.14191 | -0.041199 | 59.5001 | 59.7244 | 122.6715 | 122.6715 | -0.11444 | 122.6715 | 61.6699 | -0.14648 | 122.6715 | -0.11444 | 61.6699 | 122.6715 | 122.6715 | -122.8867 | -122.9599
383.3438 | 123.0286 | -60.8459 | 62.0041 | 0.22476 | 0.021574 | 0.012525 | 0.0078742 | 0.063529 | -0.0019247 | 0.069677 | -60.9604 | 61.9308 | -60.9009 | -61.0794 | 61.7477 | 0.72784 | -1.2909 | -1.2817 | 61.8942 | -61.0062 | -0.054932 | -0.073242 | -0.11444 | -0.23346 | -0.25635 | -0.16022 | -0.10986 | -0.059509 | 59.5551 | 59.5642 | 122.5937 | 122.7768 | -0.11444 | 122.7402 | 61.5738 | -0.16022 | 122.7768 | -0.11444 | 61.5738 | 122.5937 | 122.7402 | -122.905 | -123.0103
384.3438 | 123.1338 | -60.8185 | 62.0087 | 0.049286 | 0.017942 | 0.014447 | 0.0010382 | 0.059898 | -0.0019247 | 0.071814 | -60.9375 | 61.8668 | -60.8459 | -60.997 | 61.853 | 0.87891 | -1.3733 | -1.1444 | 61.8759 | -60.9421 | -0.027466 | -0.14191 | -0.11902 | -0.17853 | -0.15564 | -0.1236 | -0.13275 | -0.091553 | 59.4452 | 59.6741 | 122.6715 | 122.6852 | -0.11902 | 122.6944 | 61.6974 | -0.1236 | 122.6852 | -0.11902 | 61.6974 | 122.6715 | 122.6944 | -122.8546 | -122.9507
385.3438 | 123.1567 | -60.7636 | 62.0224 | 0.71304 | 0.018797 | 0.012738 | 0.0025336 | 0.060111 | -0.0038473 | 0.070746 | -60.8459 | 61.8484 | -60.8688 | -60.9192 | 61.8988 | 0.96588 | -1.3916 | -1.0849 | 61.8576 | -60.9192 | -0.10528 | -0.17395 | -0.082397 | -0.15564 | -0.1236 | -0.15564 | -0.16479 | 0.022888 | 59.3719 | 59.6787 | 122.6624 | 122.612 | -0.082397 | 122.6212 | 61.7294 | -0.15564 | 122.612 | -0.082397 | 61.7294 | 122.6624 | 122.6212 | -122.8912 | -122.9416
386.3438 | 123.143 | -60.8368 | 61.9766 | 0.22476 | 0.017729 | 0.012311 | 0.0042426 | 0.062889 | -0.0021383 | 0.071173 | -60.8734 | 61.8301 | -60.8597 | -60.9604 | 61.8439 | 0.87891 | -1.5472 | -1.2314 | 61.8439 | -60.9512 | -0.022888 | -0.14648 | -0.036621 | -0.1236 | -0.13275 | -0.11444 | -0.13275 | -0.013733 | 59.2896 | 59.6054 | 122.6807 | 122.6669 | -0.036621 | 122.6807 | 61.7157 | -0.11444 | 122.6669 | -0.036621 | 61.7157 | 122.6807 | 122.6807 | -122.8363 | -122.9279
387.3438 | 123.0194 | -60.7956 | 61.9858 | 0.064545 | 0.016233 | 0.012097 | 0.0014654 | 0.061607 | -0.0051291 | 0.071173 | -60.9375 | 61.8347 | -60.8826 | -61.0199 | 61.8256 | 0.85602 | -1.4786 | -1.1307 | 61.8896 | -60.9467 | -0.086975 | -0.15106 | -0.14191 | -0.2243 | -0.16022 | -0.15106 | -0.096131 | -0.054932 | 59.317 | 59.6649 | 122.6212 | 122.6303 | -0.14191 | 122.6852 | 61.6516 | -0.15106 | 122.6303 | -0.14191 | 61.6516 | 122.6212 | 122.6852 | -122.8683 | -122.9324
388.3438 | 123.1293 | -60.8093 | 62.0041 | 0.19424 | 0.014738 | 0.013379 | 0.0025336 | 0.06118 | -0.0047019 | 0.070532 | -60.8871 | 61.8393 | -60.8551 | -60.9924 | 61.8393 | 0.91095 | -1.593 | -1.3 | 61.853 | -60.9604 | -0.045777 | -0.16479 | -0.07782 | -0.18311 | -0.16479 | -0.15106 | -0.15106 | -0.032043 | 59.2163 | 59.5093 | 122.6486 | 122.6486 | -0.07782 | 122.6624 | 61.7203 | -0.15106 | 122.6486 | -0.07782 | 61.7203 | 122.6486 | 122.6624 | -122.8592 | -122.9645
389.3438 | 123.111 | -60.7864 | 62.0316 | -0.19485 | 0.017942 | 0.013379 | 0.0021064 | 0.059471 | -0.0029929 | 0.069464 | -60.8826 | 61.8851 | -60.8505 | -60.9421 | 61.8622 | 1.0117 | -1.4374 | -1.2451 | 61.908 | -60.9283 | -0.064087 | -0.14648 | -0.09613 | -0.15564 | -0.16937 | -0.14191 | -0.1236 | -0.032043 | 59.3491 | 59.5413 | 122.6486 | 122.6715 | -0.09613 | 122.6944 | 61.7981 | -0.14191 | 122.6715 | -0.09613 | 61.7981 | 122.6486 | 122.6944 | -122.8821 | -122.9599
390.3438 | 123.1247 | -60.8322 | 62.0132 | -0.095673 | 0.020933 | 0.015088 | 0.0070196 | 0.063743 | -0.0061973 | 0.068609 | -60.8734 | 61.9583 | -60.8643 | -60.9787 | 61.8164 | 0.97504 | -1.4786 | -1.3321 | 61.9354 | -60.9833 | -0.032044 | -0.054932 | -0.041199 | -0.14648 | -0.19684 | -0.15106 | -0.07782 | -0.009155 | 59.3536 | 59.5001 | 122.6486 | 122.7905 | -0.041199 | 122.7676 | 61.8073 | -0.15106 | 122.7905 | -0.041199 | 61.8073 | 122.6486 | 122.7676 | -122.8775 | -122.9965
391.3438 | 123.0286 | -60.8643 | 62.0224 | 0.049286 | 0.019651 | 0.015088 | 0.0080878 | 0.063743 | -0.0027793 | 0.070532 | -60.9375 | 61.9629 | -60.8871 | -61.0474 | 61.7477 | 0.89722 | -1.5198 | -1.4969 | 61.8988 | -61.0062 | -0.022888 | -0.059509 | -0.073242 | -0.1831 | -0.27466 | -0.14191 | -0.1236 | -0.050354 | 59.3445 | 59.3674 | 122.612 | 122.8271 | -0.073242 | 122.7631 | 61.7615 | -0.14191 | 122.8271 | -0.073242 | 61.7615 | 122.612 | 122.7631 | -122.9095 | -123.0286
392.3438 | 123.1522 | -60.7956 | 61.9812 | 0.079804 | 0.016447 | 0.011029 | 0.0038154 | 0.065025 | -0.0025657 | 0.072241 | -60.7452 | 61.8805 | -60.8917 | -60.9421 | 61.8484 | 0.97961 | -1.7624 | -1.4145 | 61.8484 | -60.9467 | -0.096131 | -0.10071 | 0.050354 | -0.14649 | -0.13275 | -0.15106 | -0.13275 | 0.14649 | 59.0332 | 59.3811 | 122.644 | 122.6761 | 0.050354 | 122.644 | 61.7752 | -0.15106 | 122.6761 | 0.050354 | 61.7752 | 122.644 | 122.644 | -122.8729 | -122.9279
393.3438 | 123.0423 | -60.8368 | 61.9812 | 0.24002 | 0.01901 | 0.015943 | 0.0059516 | 0.063529 | -0.00085669 | 0.070532 | -60.9512 | 61.9446 | -60.9009 | -61.0382 | 61.7844 | 0.95215 | -1.6937 | -1.5335 | 61.8942 | -60.9833 | -0.064087 | -0.036621 | -0.11444 | -0.20142 | -0.19684 | -0.14648 | -0.086975 | -0.050354 | 59.1431 | 59.3033 | 122.6212 | 122.7814 | -0.11444 | 122.731 | 61.7889 | -0.14648 | 122.7814 | -0.11444 | 61.7889 | 122.6212 | 122.731 | -122.8821 | -122.9645
394.3438 | 123.0515 | -60.791 | 62.0407 | -0.19485 | 0.01901 | 0.014661 | 0.0021064 | 0.06182 | -0.0034201 | 0.069677 | -60.9146 | 61.94 | -60.878 | -60.9924 | 61.8301 | 1.0849 | -1.5427 | -1.4236 | 61.9308 | -60.9604 | -0.086975 | -0.10071 | -0.1236 | -0.20142 | -0.21057 | -0.16937 | -0.10986 | -0.036621 | 59.2484 | 59.3674 | 122.6212 | 122.731 | -0.1236 | 122.7219 | 61.8759 | -0.16937 | 122.731 | -0.1236 | 61.8759 | 122.6212 | 122.7219 | -122.9187 | -123.0011
395.3438 | 123.0743 | -60.8093 | 61.9812 | 0.88852 | 0.020933 | 0.013806 | 0.00039739 | 0.060325 | -0.0027793 | 0.072668 | -60.9467 | 61.8576 | -60.8826 | -61.0291 | 61.8256 | 1.0666 | -1.7303 | -1.5152 | 61.8942 | -60.9329 | -0.073242 | -0.1236 | -0.13733 | -0.21973 | -0.15564 | -0.1236 | -0.086975 | -0.064087 | 59.079 | 59.2941 | 122.6349 | 122.6669 | -0.13733 | 122.7036 | 61.8759 | -0.1236 | 122.6669 | -0.13733 | 61.8759 | 122.6349 | 122.7036 | -122.8638 | -122.9141
396.3438 | 123.0835 | -60.8459 | 61.9537 | 0.3392 | 0.019224 | 0.017438 | 0.0061652 | 0.064384 | -0.0034201 | 0.071173 | -60.8871 | 61.8851 | -60.8826 | -60.9741 | 61.8393 | 1.0986 | -1.9043 | -1.5518 | 61.821 | -60.965 | -0.036621 | -0.068664 | -0.041199 | -0.12817 | -0.11444 | -0.11902 | -0.13275 | -0.004578 | 58.9417 | 59.2941 | 122.6852 | 122.731 | -0.041199 | 122.6669 | 61.9446 | -0.11902 | 122.731 | -0.041199 | 61.9446 | 122.6852 | 122.6669 | -122.8363 | -122.9187
397.3438 | 123.1338 | -60.7956 | 61.9858 | 0.47653 | 0.018797 | 0.014875 | 0.0029608 | 0.063529 | -0.0019247 | 0.071386 | -60.8597 | 61.8713 | -60.8459 | -60.9833 | 61.8484 | 1.1261 | -1.9501 | -1.5701 | 61.853 | -60.9558 | -0.050354 | -0.11444 | -0.064087 | -0.18768 | -0.13733 | -0.16022 | -0.13275 | -0.013733 | 58.8455 | 59.2255 | 122.644 | 122.6669 | -0.064087 | 122.6486 | 61.9217 | -0.16022 | 122.6669 | -0.064087 | 61.9217 | 122.644 | 122.6486 | -122.8317 | -122.9416
398.3438 | 123.0698 | -60.8093 | 62.0544 | -0.12619 | 0.022001 | 0.010388 | 0.009156 | 0.062461 | -0.0040609 | 0.070318 | -60.8871 | 61.9675 | -60.8414 | -60.9741 | 61.8347 | 1.1719 | -1.7578 | -1.5747 | 61.9171 | -60.9787 | -0.032044 | -0.086975 | -0.07782 | -0.16479 | -0.21973 | -0.16937 | -0.13733 | -0.045776 | 59.0515 | 59.2346 | 122.644 | 122.7768 | -0.07782 | 122.7264 | 61.9812 | -0.16937 | 122.7768 | -0.07782 | 61.9812 | 122.644 | 122.7264 | -122.8958 | -123.0331
399.3438 | 123.1018 | -60.8047 | 61.9858 | 0.20187 | 0.016447 | 0.014875 | 0.0018928 | 0.062461 | -0.0044883 | 0.072455 | -60.9009 | 61.8439 | -60.9009 | -60.9879 | 61.8301 | 1.1673 | -1.9958 | -1.6205 | 61.8484 | -60.9421 | -0.09613 | -0.14191 | -0.09613 | -0.1831 | -0.15564 | -0.13733 | -0.13733 | 0 | 58.8089 | 59.1843 | 122.6349 | 122.6486 | -0.09613 | 122.6532 | 61.972 | -0.13733 | 122.6486 | -0.09613 | 61.972 | 122.6349 | 122.6532 | -122.8867 | -122.9279
400.3438 | 123.0515 | -60.8231 | 62.0544 | -0.065155 | 0.018797 | 0.0091068 | 0.0076606 | 0.063743 | -0.0034201 | 0.071173 | -60.8688 | 61.9766 | -60.8643 | -60.965 | 61.821 | 1.2039 | -1.8814 | -1.6663 | 61.908 | -60.9833 | -0.041199 | -0.077819 | -0.045776 | -0.14191 | -0.23346 | -0.16022 | -0.14648 | -0.004577 | 58.9417 | 59.1568 | 122.644 | 122.7997 | -0.045776 | 122.731 | 62.027 | -0.16022 | 122.7997 | -0.045776 | 62.027 | 122.644 | 122.731 | -122.9187 | -123.0377
401.3438 | 123.0103 | -60.8643 | 62.0316 | 0.56046 | 0.018156 | 0.015729 | 0.0059516 | 0.062889 | -0.00042929 | 0.070746 | -60.9146 | 61.9812 | -60.8688 | -61.0794 | 61.7386 | 1.1124 | -1.8997 | -1.8173 | 61.9034 | -60.997 | -0.004577 | -0.050354 | -0.050354 | -0.21515 | -0.29297 | -0.13275 | -0.12817 | -0.045777 | 58.9645 | 59.0469 | 122.6028 | 122.8455 | -0.050354 | 122.7676 | 61.9766 | -0.13275 | 122.8455 | -0.050354 | 61.9766 | 122.6028 | 122.7676 | -122.9004 | -123.0286
402.3438 | 123.0057 | -60.8414 | 62.0361 | 0.10269 | 0.02136 | 0.013806 | 0.0089422 | 0.060325 | -0.0025657 | 0.071173 | -60.9833 | 61.9949 | -60.8871 | -61.116 | 61.7935 | 1.2497 | -2.005 | -1.7807 | 61.908 | -60.9787 | -0.045776 | -0.041199 | -0.14191 | -0.27466 | -0.24262 | -0.13733 | -0.12817 | -0.09613 | 58.8364 | 59.0607 | 122.6349 | 122.8363 | -0.14191 | 122.7493 | 62.0911 | -0.13733 | 122.8363 | -0.14191 | 62.0911 | 122.6349 | 122.7493 | -122.9233 | -123.0148
403.3438 | 123.0469 | -60.8139 | 61.9858 | 0.24002 | 0.019224 | 0.013806 | 0.0031744 | 0.065452 | -0.0051291 | 0.072241 | -60.9421 | 61.94 | -60.8963 | -61.0291 | 61.7752 | 1.1948 | -2.0966 | -1.8448 | 61.908 | -60.9695 | -0.082397 | -0.045777 | -0.12817 | -0.21515 | -0.21057 | -0.15564 | -0.07782 | -0.045777 | 58.7173 | 58.9691 | 122.5891 | 122.7539 | -0.12817 | 122.7219 | 62.0087 | -0.15564 | 122.7539 | -0.12817 | 62.0087 | 122.5891 | 122.7219 | -122.8821 | -122.9553
404.3438 | 123.0652 | -60.8368 | 62.0041 | 0.2095 | 0.018156 | 0.015302 | 0.0046698 | 0.064598 | -0.0023519 | 0.068609 | -60.9512 | 61.9629 | -60.9009 | -61.0886 | 61.7523 | 1.1993 | -2.0874 | -1.8951 | 61.9217 | -60.9879 | -0.064087 | -0.041198 | -0.11444 | -0.25177 | -0.25177 | -0.15106 | -0.082397 | -0.050354 | 58.7494 | 58.9417 | 122.5891 | 122.7997 | -0.11444 | 122.7585 | 62.0361 | -0.15106 | 122.7997 | -0.11444 | 62.0361 | 122.5891 | 122.7585 | -122.905 | -122.9919
405.3438 | 123.0103 | -60.8322 | 62.0636 | 0.17136 | 0.020506 | 0.016584 | 0.005738 | 0.06417 | -0.0010703 | 0.070532 | -60.9604 | 61.9949 | -60.9009 | -61.0931 | 61.7706 | 1.1673 | -2.449 | -1.6296 | 61.908 | -60.9833 | -0.068665 | -0.068665 | -0.12817 | -0.26093 | -0.29297 | -0.15106 | -0.15564 | -0.059509 | 58.3832 | 59.2026 | 122.6028 | 122.8271 | -0.12817 | 122.7402 | 61.9995 | -0.15106 | 122.8271 | -0.12817 | 61.9995 | 122.6028 | 122.7402 | -122.9645 | -123.0469
406.3438 | 123.0835 | -60.8368 | 62.0407 | -1.6673 | 0.022642 | 0.015088 | 0.0038154 | 0.06652 | -0.0036337 | 0.071173 | -60.9329 | 61.9995 | -60.8688 | -60.9741 | 61.8439 | 1.3641 | -2.1378 | -1.8173 | 61.9446 | -60.9558 | -0.032043 | -0.041198 | -0.09613 | -0.13733 | -0.19684 | -0.11902 | -0.09613 | -0.064087 | 58.699 | 59.0195 | 122.6807 | 122.8363 | -0.09613 | 122.7814 | 62.2009 | -0.11902 | 122.8363 | -0.09613 | 62.2009 | 122.6807 | 122.7814 | -122.9095 | -122.9965
407.3438 | 123.0057 | -60.8185 | 62.0544 | 0.018768 | 0.020506 | 0.015729 | 0.0078742 | 0.065879 | -0.0021383 | 0.069677 | -60.9283 | 61.9812 | -60.8734 | -61.0519 | 61.7569 | 1.2955 | -2.1423 | -1.9684 | 61.94 | -61.0107 | -0.054932 | -0.073242 | -0.10986 | -0.23346 | -0.29755 | -0.19226 | -0.11444 | -0.054932 | 58.6761 | 58.8501 | 122.5754 | 122.7997 | -0.10986 | 122.7585 | 62.114 | -0.19226 | 122.7997 | -0.10986 | 62.114 | 122.5754 | 122.7585 | -122.9279 | -123.0652
408.3438 | 123.111 | -60.8002 | 61.9583 | 0.22476 | 0.018583 | 0.013166 | -0.0017388 | 0.067375 | -0.0023519 | 0.071386 | -60.8597 | 61.8805 | -60.9009 | -60.9421 | 61.9217 | 1.4099 | -2.4353 | -1.8906 | 61.9034 | -60.91 | -0.10071 | -0.07782 | -0.059509 | -0.14191 | -0.036621 | -0.10986 | -0.054932 | 0.041199 | 58.3649 | 58.9096 | 122.7219 | 122.6807 | -0.059509 | 122.7036 | 62.2101 | -0.10986 | 122.6807 | -0.059509 | 62.2101 | 122.7219 | 122.7036 | -122.8592 | -122.8683
409.3438 | 123.111 | -60.8002 | 62.0178 | 0.17899 | 0.017088 | 0.013379 | -0.0013116 | 0.062461 | -0.0027793 | 0.070959 | -60.91 | 61.8622 | -60.8734 | -61.0199 | 61.8301 | 1.4099 | -2.4124 | -1.9547 | 61.8759 | -60.9375 | -0.073242 | -0.15564 | -0.10986 | -0.21973 | -0.18768 | -0.13733 | -0.14191 | -0.036621 | 58.3878 | 58.8455 | 122.6303 | 122.6624 | -0.10986 | 122.6761 | 62.2101 | -0.13733 | 122.6624 | -0.10986 | 62.2101 | 122.6303 | 122.6761 | -122.8912 | -122.9553
410.3438 | 123.0835 | -60.8185 | 61.9949 | 0.16373 | 0.020292 | 0.01402 | 0.0016792 | 0.062461 | -0.0027793 | 0.070746 | -60.8826 | 61.8622 | -60.8643 | -60.9833 | 61.8164 | 1.442 | -2.4765 | -1.9821 | 61.8805 | -60.9283 | -0.045777 | -0.13275 | -0.064087 | -0.16479 | -0.17853 | -0.10986 | -0.11444 | -0.01831 | 58.342 | 58.8364 | 122.6349 | 122.6807 | -0.064087 | 122.699 | 62.2604 | -0.10986 | 122.6807 | -0.064087 | 62.2604 | 122.6349 | 122.699 | -122.8592 | -122.9233
411.3438 | 123.0286 | -60.8231 | 62.059 | -0.15671 | 0.01901 | 0.016584 | 0.0046698 | 0.063316 | -0.0042747 | 0.069037 | -60.9055 | 61.972 | -60.8505 | -61.0016 | 61.7889 | 1.4832 | -2.2385 | -2.0142 | 61.9858 | -60.9467 | -0.027466 | -0.086975 | -0.082398 | -0.17853 | -0.27008 | -0.1236 | -0.073242 | -0.054932 | 58.5846 | 58.8089 | 122.612 | 122.7951 | -0.082398 | 122.8088 | 62.3062 | -0.1236 | 122.7951 | -0.082398 | 62.3062 | 122.612 | 122.8088 | -122.9095 | -123.0057
412.3438 | 123.0652 | -60.8414 | 62.059 | 0.13321 | 0.017729 | 0.010816 | 0.0046698 | 0.064598 | -0.0025657 | 0.070532 | -60.9558 | 61.9995 | -60.8871 | -61.0886 | 61.7249 | 1.3779 | -2.7145 | -2.5452 | 61.8805 | -61.0291 | -0.045776 | -0.059509 | -0.11444 | -0.24719 | -0.33417 | -0.18768 | -0.17853 | -0.068665 | 58.1268 | 58.2962 | 122.5662 | 122.8409 | -0.11444 | 122.7219 | 62.2192 | -0.18768 | 122.8409 | -0.11444 | 62.2192 | 122.5662 | 122.7219 | -122.9462 | -123.0881
413.3438 | 123.0698 | -60.8139 | 62.0499 | 0.37735 | 0.019224 | 0.011029 | 0.0063788 | 0.063529 | -0.0012839 | 0.070318 | -60.8551 | 62.0041 | -60.8643 | -60.9695 | 61.8118 | 1.5335 | -2.4399 | -2.0782 | 61.9308 | -60.9879 | -0.050354 | -0.045777 | -0.041199 | -0.15564 | -0.23804 | -0.17395 | -0.11902 | 0.009155 | 58.374 | 58.7357 | 122.6257 | 122.818 | -0.041199 | 122.7448 | 62.3474 | -0.17395 | 122.818 | -0.041199 | 62.3474 | 122.6257 | 122.7448 | -122.9141 | -123.0377
414.3438 | 123.0835 | -60.8276 | 62.0087 | 0.19424 | 0.017729 | 0.012311 | 0.0031744 | 0.064598 | -0.0012839 | 0.070959 | -60.9512 | 61.9766 | -60.8963 | -61.0565 | 61.7569 | 1.4603 | -2.5543 | -2.2293 | 61.9125 | -60.9787 | -0.068664 | -0.032043 | -0.1236 | -0.22888 | -0.25177 | -0.15106 | -0.09613 | -0.054932 | 58.2733 | 58.5983 | 122.5845 | 122.8043 | -0.1236 | 122.7402 | 62.2879 | -0.15106 | 122.8043 | -0.1236 | 62.2879 | 122.5845 | 122.7402 | -122.905 | -122.9874
415.3438 | 123.0194 | -60.8688 | 62.0544 | 0.072174 | 0.022642 | 0.012525 | 0.0063788 | 0.063316 | -0.0025657 | 0.070746 | -60.9329 | 61.9766 | -60.8597 | -61.0657 | 61.7523 | 1.4877 | -2.5223 | -2.2797 | 61.94 | -60.9833 | 0.009155 | -0.077819 | -0.064087 | -0.19684 | -0.30212 | -0.11444 | -0.11444 | -0.073242 | 58.3466 | 58.5892 | 122.6212 | 122.8455 | -0.064087 | 122.8088 | 62.3566 | -0.11444 | 122.8455 | -0.064087 | 62.3566 | 122.6212 | 122.8088 | -122.9141 | -123.0377
416.3438 | 123.1018 | -60.8276 | 62.027 | 0.23239 | 0.019651 | 0.014447 | 0.0016792 | 0.065879 | -0.00085669 | 0.070959 | -60.91 | 61.94 | -60.8734 | -61.0107 | 61.8118 | 1.5518 | -2.7237 | -2.2247 | 61.908 | -60.965 | -0.045776 | -0.086976 | -0.082397 | -0.1831 | -0.21515 | -0.13733 | -0.11902 | -0.036621 | 58.1039 | 58.6029 | 122.6395 | 122.7676 | -0.082397 | 122.7356 | 62.3795 | -0.13733 | 122.7676 | -0.082397 | 62.3795 | 122.6395 | 122.7356 | -122.9004 | -122.9919
417.3438 | 123.0698 | -60.8139 | 62.0682 | -0.095673 | 0.020292 | 0.015088 | 0.0044562 | 0.064598 | -0.0034201 | 0.071173 | -60.878 | 62.0041 | -60.8551 | -60.9741 | 61.821 | 1.6205 | -2.5909 | -2.211 | 61.9308 | -60.965 | -0.041199 | -0.064087 | -0.064087 | -0.16022 | -0.24719 | -0.15106 | -0.13733 | -0.022888 | 58.223 | 58.6029 | 122.6349 | 122.818 | -0.064087 | 122.7448 | 62.4344 | -0.15106 | 122.818 | -0.064087 | 62.4344 | 122.6349 | 122.7448 | -122.9233 | -123.0331
418.3438 | 123.1522 | -60.7819 | 61.9858 | 0.20187 | 0.018797 | 0.013593 | 0.0016792 | 0.064811 | -0.0044883 | 0.069464 | -60.8688 | 61.9217 | -60.878 | -60.9329 | 61.6608 | 1.3962 | -2.6321 | -2.2018 | 61.8851 | -60.9283 | -0.096131 | -0.064087 | -0.086975 | -0.15106 | -0.32501 | -0.14648 | -0.10071 | 0.009156 | 58.1497 | 58.58 | 122.4426 | 122.7036 | -0.086975 | 122.6669 | 62.178 | -0.14648 | 122.7036 | -0.086975 | 62.178 | 122.4426 | 122.6669 | -122.8638 | -122.9141
419.3438 | 123.111 | -60.7956 | 61.9629 | 0.27054 | 0.020078 | 0.012738 | 0.0038154 | 0.065025 | -0.0027793 | 0.069464 | -60.878 | 61.9125 | -60.8414 | -60.9695 | 61.8301 | 1.6479 | -2.9068 | -2.3071 | 61.908 | -60.9375 | -0.045777 | -0.050354 | -0.082398 | -0.17395 | -0.13275 | -0.14191 | -0.054932 | -0.036621 | 57.8888 | 58.4885 | 122.6257 | 122.7081 | -0.082398 | 122.7036 | 62.4435 | -0.14191 | 122.7081 | -0.082398 | 62.4435 | 122.6257 | 122.7036 | -122.8043 | -122.9004
420.3438 | 123.0331 | -60.8139 | 62.0682 | -0.0041198 | 0.020078 | 0.014447 | 0.006806 | 0.065238 | -0.0036337 | 0.071386 | -60.8734 | 61.9995 | -60.8505 | -61.0062 | 61.7935 | 1.6251 | -2.774 | -2.3941 | 61.9446 | -60.9833 | -0.036621 | -0.068664 | -0.059509 | -0.19226 | -0.27466 | -0.16937 | -0.1236 | -0.022888 | 58.0399 | 58.4198 | 122.6074 | 122.8134 | -0.059509 | 122.7585 | 62.439 | -0.16937 | 122.8134 | -0.059509 | 62.439 | 122.6074 | 122.7585 | -122.9187 | -123.0515
421.3438 | 123.0377 | -60.8047 | 62.059 | -0.034637 | 0.017088 | 0.014447 | 0.0061652 | 0.065666 | -0.0025657 | 0.071173 | -60.8688 | 62.0041 | -60.8597 | -61.1984 | 61.6516 | 1.7441 | -2.8656 | -2.3804 | 61.94 | -60.9879 | -0.054931 | -0.054932 | -0.064086 | -0.39368 | -0.40741 | -0.1831 | -0.11902 | -0.009155 | 57.9391 | 58.4244 | 122.4564 | 122.8088 | -0.064086 | 122.7448 | 62.5488 | -0.1831 | 122.8088 | -0.064086 | 62.5488 | 122.4564 | 122.7448 | -122.9187 | -123.0469
422.3438 | 123.056 | -60.8368 | 62.0224 | 0.1561 | 0.020292 | 0.013166 | 0.0048834 | 0.068015 | 0.0027749 | 0.067541 | -60.9741 | 62.0041 | -60.8688 | -60.9558 | 62.0956 | 1.6434 | -2.8473 | -2.449 | 61.94 | -61.0062 | -0.032043 | -0.018311 | -0.13733 | -0.11902 | 0.073242 | -0.16937 | -0.082398 | -0.10529 | 57.9895 | 58.3878 | 122.9324 | 122.8409 | -0.13733 | 122.7768 | 62.4802 | -0.16937 | 122.8409 | -0.13733 | 62.4802 | 122.9324 | 122.7768 | -122.8912 | -123.0286
423.3438 | 123.0423 | -60.8047 | 62.0636 | 0.13321 | 0.021787 | 0.0097476 | 0.0053106 | 0.065025 | -0.0027793 | 0.071386 | -60.9604 | 62.0041 | -60.8826 | -61.0794 | 61.7249 | 1.5976 | -3.2181 | -2.9709 | 61.8713 | -61.0382 | -0.077819 | -0.05951 | -0.15564 | -0.27466 | -0.33875 | -0.23346 | -0.19226 | -0.07782 | 57.5867 | 57.8339 | 122.5296 | 122.8088 | -0.15564 | 122.6761 | 62.4023 | -0.23346 | 122.8088 | -0.15564 | 62.4023 | 122.5296 | 122.6761 | -122.9462 | -123.1018
424.3438 | 123.0194 | -60.8276 | 62.0224 | 0.18662 | 0.01837 | 0.01637 | 0.0059516 | 0.063743 | -0.0010703 | 0.071173 | -60.9512 | 61.9904 | -60.9192 | -61.0794 | 61.734 | 1.6022 | -2.9938 | -2.6459 | 61.9263 | -60.9924 | -0.091552 | -0.032044 | -0.1236 | -0.25177 | -0.28839 | -0.16479 | -0.09613 | -0.032044 | 57.8339 | 58.1818 | 122.5616 | 122.818 | -0.1236 | 122.7539 | 62.4298 | -0.16479 | 122.818 | -0.1236 | 62.4298 | 122.5616 | 122.7539 | -122.9416 | -123.0148
425.3438 | 123.024 | -60.8231 | 62.0224 | 0.37735 | 0.020292 | 0.013166 | 0.0038154 | 0.065452 | -0.0025657 | 0.070105 | -60.9421 | 61.9904 | -60.9055 | -61.0519 | 61.7294 | 1.6251 | -3.0396 | -2.6825 | 61.9766 | -60.965 | -0.082398 | -0.032044 | -0.11902 | -0.22888 | -0.29297 | -0.14191 | -0.045776 | -0.036621 | 57.7835 | 58.1406 | 122.5525 | 122.8134 | -0.11902 | 122.7997 | 62.4481 | -0.14191 | 122.8134 | -0.11902 | 62.4481 | 122.5525 | 122.7997 | -122.9279 | -122.9874
426.3438 | 123.0515 | -60.791 | 62.0636 | -0.13382 | 0.018797 | 0.015729 | 0.0042426 | 0.064598 | -0.0014975 | 0.0716 | -60.8917 | 62.0087 | -60.8643 | -60.9833 | 61.7981 | 1.7395 | -3.0304 | -2.5589 | 61.9537 | -60.9695 | -0.073242 | -0.054932 | -0.10071 | -0.19226 | -0.2655 | -0.17853 | -0.10986 | -0.027466 | 57.7606 | 58.2321 | 122.5891 | 122.7997 | -0.10071 | 122.7448 | 62.5305 | -0.17853 | 122.7997 | -0.10071 | 62.5305 | 122.5891 | 122.7448 | -122.9279 | -123.0331
427.3438 | 122.9736 | -60.8093 | 62.0728 | -0.21011 | 0.018156 | 0.012738 | 0.0010382 | 0.063316 | -0.0014975 | 0.070959 | -60.91 | 62.0132 | -60.8643 | -61.0291 | 61.9629 | 1.9867 | -3.241 | -2.742 | 61.9904 | -60.9558 | -0.054932 | -0.059509 | -0.10071 | -0.21973 | -0.10986 | -0.14648 | -0.082398 | -0.045776 | 57.5684 | 58.0673 | 122.7722 | 122.8226 | -0.10071 | 122.7997 | 62.796 | -0.14648 | 122.8226 | -0.10071 | 62.796 | 122.7722 | 122.7997 | -122.937 | -123.0286
428.3438 | 123.0652 | -60.791 | 62.0453 | -0.027008 | 0.020078 | 0.013379 | 0.0072332 | 0.067375 | -0.0032065 | 0.070746 | -60.8643 | 61.9949 | -60.8459 | -60.9879 | 61.7889 | 1.7349 | -3.1769 | -2.7283 | 61.9629 | -60.9421 | -0.054931 | -0.050354 | -0.073242 | -0.19684 | -0.25635 | -0.15106 | -0.082397 | -0.018311 | 57.6141 | 58.0627 | 122.58 | 122.7859 | -0.073242 | 122.7539 | 62.5259 | -0.15106 | 122.7859 | -0.073242 | 62.5259 | 122.58 | 122.7539 | -122.8912 | -122.9874
429.3438 | 123.0286 | -60.8093 | 62.0544 | 0.079804 | 0.020506 | 0.017011 | 0.0048834 | 0.065666 | -0.0032065 | 0.072027 | -60.91 | 61.9904 | -60.8597 | -61.0382 | 61.7432 | 1.7075 | -3.2181 | -2.8336 | 61.9766 | -60.9695 | -0.050354 | -0.064087 | -0.10071 | -0.22888 | -0.31128 | -0.16022 | -0.077819 | -0.050354 | 57.5912 | 57.9758 | 122.5525 | 122.7997 | -0.10071 | 122.7859 | 62.5168 | -0.16022 | 122.7997 | -0.10071 | 62.5168 | 122.5525 | 122.7859 | -122.9141 | -123.024
430.3438 | 122.9736 | -60.8276 | 62.0453 | 0.034027 | 0.018797 | 0.014875 | 0.006806 | 0.067161 | -0.0055563 | 0.069037 | -60.8963 | 61.9995 | -60.8505 | -61.0474 | 61.7432 | 1.7303 | -3.273 | -2.8702 | 61.9537 | -60.9833 | -0.022888 | -0.045776 | -0.068664 | -0.21973 | -0.30212 | -0.15564 | -0.091553 | -0.045776 | 57.5546 | 57.9575 | 122.5708 | 122.8271 | -0.068664 | 122.7814 | 62.558 | -0.15564 | 122.8271 | -0.068664 | 62.558 | 122.5708 | 122.7814 | -122.8958 | -123.0286
431.3438 | 122.9965 | -60.8002 | 62.0728 | 0.087433 | 0.020292 | 0.011029 | 0.0059516 | 0.066306 | -0.0027793 | 0.073095 | -60.8917 | 62.0132 | -60.8551 | -61.0245 | 61.7523 | 1.7395 | -3.3051 | -2.916 | 61.9766 | -60.9787 | -0.054932 | -0.059509 | -0.091553 | -0.2243 | -0.32044 | -0.17853 | -0.09613 | -0.036621 | 57.4951 | 57.8842 | 122.5525 | 122.8134 | -0.091553 | 122.7768 | 62.5397 | -0.17853 | 122.8134 | -0.091553 | 62.5397 | 122.5525 | 122.7768 | -122.9279 | -123.0515
432.3438 | 123.0927 | -60.8139 | 62.0453 | -0.019379 | 0.020078 | 0.015088 | 0.0027472 | 0.066734 | -0.0017111 | 0.070105 | -60.8643 | 62.0087 | -60.8505 | -60.9833 | 61.821 | 1.8265 | -3.3463 | -2.861 | 61.9675 | -60.9421 | -0.036621 | -0.036621 | -0.050354 | -0.16937 | -0.2243 | -0.12817 | -0.07782 | -0.013733 | 57.4677 | 57.9529 | 122.6349 | 122.8226 | -0.050354 | 122.7814 | 62.6404 | -0.12817 | 122.8226 | -0.050354 | 62.6404 | 122.6349 | 122.7814 | -122.8958 | -122.9874
433.3438 | 123.0377 | -60.7819 | 62.1002 | -0.14908 | 0.018156 | 0.013379 | 0.00061099 | 0.066306 | -0.0029929 | 0.069464 | -60.9055 | 62.0316 | -60.8643 | -61.0062 | 61.7935 | 1.8219 | -3.3188 | -2.9388 | 61.9995 | -60.9558 | -0.082398 | -0.068665 | -0.1236 | -0.22431 | -0.3067 | -0.17395 | -0.10071 | -0.041199 | 57.4631 | 57.843 | 122.5754 | 122.8134 | -0.1236 | 122.7814 | 62.6038 | -0.17395 | 122.8134 | -0.1236 | 62.6038 | 122.5754 | 122.7814 | -122.9645 | -123.056
434.3438 | 123.0377 | -60.8093 | 62.1048 | 0.57571 | 0.018797 | 0.011243 | 0.0018928 | 0.065666 | -0.0010703 | 0.070959 | -60.878 | 61.9949 | -60.8505 | -61.0107 | 61.7615 | 1.8219 | -3.3554 | -2.9846 | 62.0087 | -60.9375 | -0.041199 | -0.10986 | -0.068665 | -0.20142 | -0.34332 | -0.12817 | -0.09613 | -0.027466 | 57.4539 | 57.8247 | 122.5708 | 122.8043 | -0.068665 | 122.818 | 62.6312 | -0.12817 | 122.8043 | -0.068665 | 62.6312 | 122.5708 | 122.818 | -122.9553 | -123.0423
435.3281 | 123.0789 | -60.7819 | 62.0956 | -0.19485 | 0.017088 | 0.012738 | -0.00024361 | 0.06118 | -0.0034201 | 0.069037 | -60.8459 | 61.9537 | -60.8231 | -60.9558 | 61.8301 | 1.8951 | -3.4607 | -2.9617 | 61.972 | -60.9238 | -0.041199 | -0.14191 | -0.064087 | -0.17395 | -0.2655 | -0.14191 | -0.1236 | -0.022888 | 57.3212 | 57.8201 | 122.612 | 122.7356 | -0.064087 | 122.7539 | 62.677 | -0.14191 | 122.7356 | -0.064087 | 62.677 | 122.612 | 122.7539 | -122.9187 | -123.0194
436.3438 | 123.0652 | -60.7819 | 62.0499 | -0.15671 | 0.020292 | 0.014875 | 0.003388 | 0.064384 | -0.0025657 | 0.070318 | -60.8688 | 62.0316 | -60.8505 | -60.9558 | 61.7981 | 1.8631 | -3.5248 | -3.0716 | 61.9995 | -60.9329 | -0.068665 | -0.018311 | -0.086975 | -0.17395 | -0.25177 | -0.15106 | -0.050354 | -0.01831 | 57.2571 | 57.7103 | 122.58 | 122.8134 | -0.086975 | 122.7814 | 62.645 | -0.15106 | 122.8134 | -0.086975 | 62.645 | 122.58 | 122.7814 | -122.9004 | -122.9828
437.3438 | 123.0789 | -60.791 | 62.0819 | -0.088043 | 0.019651 | 0.015515 | 0.0072332 | 0.063743 | -0.0038473 | 0.069464 | -61.0931 | 61.9583 | -60.878 | -60.9467 | 61.8164 | 1.886 | -3.6346 | -3.1082 | 61.9766 | -60.9512 | -0.086975 | -0.1236 | -0.30212 | -0.15564 | -0.2655 | -0.16022 | -0.10529 | -0.21515 | 57.1564 | 57.6828 | 122.6074 | 122.7493 | -0.30212 | 122.7676 | 62.677 | -0.16022 | 122.7493 | -0.30212 | 62.677 | 122.6074 | 122.7676 | -122.9599 | -123.0331
438.3438 | 123.0515 | -60.7864 | 62.0865 | -0.12619 | 0.019651 | 0.013166 | 0.0029608 | 0.063316 | -0.00064309 | 0.070959 | -60.8734 | 61.972 | -60.8459 | -60.9833 | 61.8073 | 1.8814 | -3.6301 | -3.1586 | 62.0178 | -60.965 | -0.059509 | -0.11444 | -0.086975 | -0.19684 | -0.27924 | -0.17853 | -0.068665 | -0.027466 | 57.1564 | 57.6279 | 122.5937 | 122.7585 | -0.086975 | 122.8043 | 62.6678 | -0.17853 | 122.7585 | -0.086975 | 62.6678 | 122.5937 | 122.8043 | -122.9324 | -123.0515
439.3438 | 123.0652 | -60.7819 | 62.0865 | 0.026398 | 0.020719 | 0.013593 | 0.0046698 | 0.065452 | -0.0036337 | 0.06925 | -60.8459 | 61.9904 | -60.8505 | -60.9741 | 61.7798 | 1.8631 | -3.7354 | -3.2364 | 61.9949 | -60.9512 | -0.068665 | -0.096131 | -0.064087 | -0.19226 | -0.3067 | -0.16937 | -0.091553 | 0.004578 | 57.0465 | 57.5455 | 122.5616 | 122.7722 | -0.064087 | 122.7768 | 62.645 | -0.16937 | 122.7722 | -0.064087 | 62.645 | 122.5616 | 122.7768 | -122.937 | -123.0377
440.3281 | 123.0789 | -60.7636 | 62.0453 | -0.14908 | 0.019438 | 0.012738 | -2.9814e-05 | 0.06118 | -0.0014975 | 0.068182 | -60.8368 | 61.9354 | -60.8185 | -60.9192 | 61.8668 | 1.9821 | -3.7628 | -3.1631 | 61.9812 | -60.9146 | -0.054931 | -0.10986 | -0.073242 | -0.15564 | -0.17853 | -0.15106 | -0.064087 | -0.018311 | 57.0007 | 57.6004 | 122.6303 | 122.699 | -0.073242 | 122.7448 | 62.7457 | -0.15106 | 122.699 | -0.073242 | 62.7457 | 122.6303 | 122.7448 | -122.8638 | -122.9599
441.3438 | 123.0698 | -60.7956 | 62.1094 | -0.1796 | 0.019224 | 0.01402 | 0.0046698 | 0.065666 | -0.0025657 | 0.067114 | -60.878 | 62.0087 | -60.8368 | -60.9879 | 61.7798 | 1.9043 | -3.772 | -3.3142 | 62.0224 | -60.9421 | -0.041199 | -0.10071 | -0.082398 | -0.19226 | -0.32959 | -0.14649 | -0.086975 | -0.041199 | 57.0236 | 57.4814 | 122.5754 | 122.8043 | -0.082398 | 122.818 | 62.6999 | -0.14649 | 122.8043 | -0.082398 | 62.6999 | 122.5754 | 122.818 | -122.9462 | -123.0515
442.3438 | 123.056 | -60.7819 | 62.0819 | 0.026398 | 0.019224 | 0.010816 | 0.0065924 | 0.065238 | -0.0038473 | 0.070746 | -60.8322 | 62.0041 | -60.8551 | -60.9604 | 61.7935 | 1.9272 | -3.9093 | -3.3646 | 61.9949 | -60.965 | -0.073243 | -0.07782 | -0.050354 | -0.17853 | -0.28839 | -0.18311 | -0.086975 | 0.022889 | 56.8726 | 57.4173 | 122.5754 | 122.7859 | -0.050354 | 122.7768 | 62.709 | -0.18311 | 122.7859 | -0.050354 | 62.709 | 122.5754 | 122.7768 | -122.937 | -123.0469
443.3438 | 122.8729 | -60.8368 | 62.0407 | 0.095062 | 0.018583 | 0.012097 | 0.0042426 | 0.064384 | -0.00042929 | 0.070746 | -60.9146 | 61.9949 | -60.8597 | -61.0428 | 61.6974 | 1.8356 | -3.923 | -3.5568 | 61.9812 | -60.9787 | -0.022888 | -0.045776 | -0.07782 | -0.20599 | -0.34332 | -0.14191 | -0.059509 | -0.054932 | 56.9138 | 57.28 | 122.5342 | 122.8317 | -0.07782 | 122.818 | 62.6724 | -0.14191 | 122.8317 | -0.07782 | 62.6724 | 122.5342 | 122.818 | -122.9004 | -123.0194
444.3438 | 123.024 | -60.8139 | 62.0773 | 0.14847 | 0.019865 | 0.01402 | 0.0038154 | 0.065025 | -0.0012839 | 0.072668 | -60.9238 | 61.9904 | -60.8688 | -61.0474 | 61.734 | 1.8494 | -4.0466 | -3.6255 | 61.9766 | -60.9695 | -0.054931 | -0.086976 | -0.10986 | -0.23346 | -0.34332 | -0.15564 | -0.10071 | -0.054932 | 56.7673 | 57.1884 | 122.5479 | 122.8043 | -0.10986 | 122.7905 | 62.6633 | -0.15564 | 122.8043 | -0.10986 | 62.6633 | 122.5479 | 122.7905 | -122.9462 | -123.0469
445.3438 | 123.0331 | -60.7727 | 62.0544 | 0.056915 | 0.017515 | 0.011457 | 0.0061652 | 0.064811 | -0.0032065 | 0.072455 | -60.8688 | 62.0316 | -60.8505 | -60.9787 | 61.7752 | 1.9501 | -4.0649 | -3.5934 | 61.9675 | -60.9604 | -0.07782 | -0.022888 | -0.09613 | -0.20599 | -0.27923 | -0.18768 | -0.086975 | -0.01831 | 56.7078 | 57.1793 | 122.5479 | 122.8043 | -0.09613 | 122.7402 | 62.7228 | -0.18768 | 122.8043 | -0.09613 | 62.7228 | 122.5479 | 122.7402 | -122.905 | -123.0148
446.3438 | 123.024 | -60.8139 | 62.059 | -0.3093 | 0.020719 | 0.012311 | 0.003388 | 0.064598 | -0.0038473 | 0.070105 | -60.9329 | 62.027 | -60.8505 | -61.0703 | 61.7249 | 1.8814 | -4.1382 | -3.7262 | 61.9904 | -60.9741 | -0.036621 | -0.032043 | -0.11902 | -0.25635 | -0.33417 | -0.16022 | -0.068665 | -0.082397 | 56.6757 | 57.0877 | 122.5388 | 122.8409 | -0.11902 | 122.8043 | 62.6953 | -0.16022 | 122.8409 | -0.11902 | 62.6953 | 122.5388 | 122.8043 | -122.9095 | -123.0331
447.3438 | 123.0377 | -60.7864 | 62.0819 | 0.026398 | 0.016874 | 0.012311 | 0.0059516 | 0.064598 | -0.0027793 | 0.070959 | -60.8368 | 62.0087 | -60.8368 | -60.965 | 61.7889 | 1.9821 | -4.1977 | -3.6804 | 61.9766 | -60.9558 | -0.050354 | -0.073242 | -0.050354 | -0.17853 | -0.29297 | -0.16937 | -0.10529 | 0 | 56.5887 | 57.106 | 122.5754 | 122.7951 | -0.050354 | 122.7631 | 62.7686 | -0.16937 | 122.7951 | -0.050354 | 62.7686 | 122.5754 | 122.7631 | -122.9187 | -123.0377
448.3438 | 123.0377 | -60.7681 | 62.1094 | -0.1796 | 0.017942 | 0.013166 | 0.0018928 | 0.064384 | -0.0014975 | 0.070105 | -60.8963 | 62.0132 | -60.8322 | -61.0153 | 61.7752 | 2.0233 | -4.0924 | -3.6987 | 62.027 | -60.9238 | -0.064087 | -0.09613 | -0.12817 | -0.24719 | -0.33417 | -0.15564 | -0.082397 | -0.064087 | 56.6757 | 57.0694 | 122.5433 | 122.7814 | -0.12817 | 122.7951 | 62.7914 | -0.15564 | 122.7814 | -0.12817 | 62.7914 | 122.5433 | 122.7951 | -122.9416 | -123.0331
449.3438 | 123.0469 | -60.8093 | 62.0728 | 0.11795 | 0.020933 | 0.012738 | 0.0046698 | 0.067161 | -0.00021569 | 0.072455 | -60.9192 | 62.0132 | -60.878 | -61.0931 | 62.1094 | 2.1423 | -4.3213 | -3.7262 | 62.0087 | -60.9741 | -0.068665 | -0.059509 | -0.10986 | -0.28381 | 0.036621 | -0.16479 | -0.064087 | -0.041198 | 56.488 | 57.0831 | 122.9187 | 122.8226 | -0.10986 | 122.818 | 62.9517 | -0.16479 | 122.8226 | -0.10986 | 62.9517 | 122.9187 | 122.818 | -122.9507 | -123.0469
450.3438 | 122.9965 | -60.7956 | 62.0956 | 0.14847 | 0.021147 | 0.013379 | 0.0048834 | 0.065879 | -0.0038473 | 0.06925 | -60.91 | 62.0453 | -60.8688 | -61.0748 | 61.9858 | 1.7258 | -4.4769 | -3.5614 | 61.9858 | -60.9558 | -0.073242 | -0.050354 | -0.11444 | -0.27924 | -0.10986 | -0.16022 | -0.10986 | -0.041199 | 56.3187 | 57.2342 | 122.7814 | 122.8409 | -0.11444 | 122.7814 | 62.5214 | -0.16022 | 122.8409 | -0.11444 | 62.5214 | 122.7814 | 122.7814 | -122.9645 | -123.0515
451.3438 | 123.0011 | -60.8093 | 62.0544 | 0.041657 | 0.020506 | 0.010388 | 0.0065924 | 0.066093 | -0.00085669 | 0.070318 | -60.8551 | 62.027 | -60.8734 | -60.9924 | 61.7432 | 2.0416 | -4.39 | -3.923 | 62.0087 | -60.9558 | -0.064087 | -0.027465 | -0.045777 | -0.18311 | -0.31128 | -0.14648 | -0.045776 | 0.01831 | 56.4194 | 56.8863 | 122.5525 | 122.8363 | -0.045777 | 122.818 | 62.851 | -0.14648 | 122.8363 | -0.045777 | 62.851 | 122.5525 | 122.818 | -122.9279 | -123.0103
452.3438 | 123.0743 | -60.7864 | 62.0911 | -0.35507 | 0.017301 | 0.015302 | 0.0048834 | 0.065238 | -0.0014975 | 0.070105 | -60.8322 | 62.059 | -60.8231 | -60.9467 | 61.8073 | 2.1103 | -4.4769 | -3.9185 | 62.0361 | -60.9283 | -0.036621 | -0.032043 | -0.045776 | -0.16022 | -0.28381 | -0.14191 | -0.054931 | -0.009155 | 56.3095 | 56.868 | 122.5937 | 122.8455 | -0.045776 | 122.8226 | 62.8967 | -0.14191 | 122.8455 | -0.045776 | 62.8967 | 122.5937 | 122.8226 | -122.9141 | -123.0194
453.3438 | 123.0789 | -60.7727 | 62.0636 | 1.9795 | 0.01901 | 0.012738 | 0.004029 | 0.065025 | -0.0027793 | 0.069891 | -60.6583 | 62.027 | -60.8505 | -60.9283 | 61.8164 | 2.1423 | -4.5044 | -3.9825 | 62.0087 | -60.9375 | -0.07782 | -0.036621 | 0.11444 | -0.15564 | -0.24719 | -0.16479 | -0.054932 | 0.19226 | 56.2683 | 56.7902 | 122.5891 | 122.7997 | 0.11444 | 122.7814 | 62.915 | -0.16479 | 122.7997 | 0.11444 | 62.915 | 122.5891 | 122.7814 | -122.9141 | -123.0011
454.3438 | 123.1476 | -60.7498 | 62.0316 | 0.16373 | 0.017942 | 0.010602 | -0.0017388 | 0.065238 | -0.0047019 | 0.070746 | -60.8459 | 61.9537 | -60.8414 | -60.9421 | 61.8347 | 2.1744 | -4.7791 | -4.0283 | 61.9446 | -60.8871 | -0.091553 | -0.07782 | -0.09613 | -0.19226 | -0.19684 | -0.13733 | -0.086975 | -0.004577 | 55.9708 | 56.7215 | 122.5845 | 122.7036 | -0.09613 | 122.6944 | 62.9242 | -0.13733 | 122.7036 | -0.09613 | 62.9242 | 122.5845 | 122.6944 | -122.8729 | -122.9187
455.3438 | 123.0011 | -60.7681 | 62.1094 | -0.19485 | 0.01837 | 0.0080386 | 0.0016792 | 0.062248 | -0.00064309 | 0.070318 | -60.878 | 62.0544 | -60.8597 | -61.0062 | 61.7569 | 2.1606 | -4.5456 | -4.1382 | 62.0499 | -60.9421 | -0.091553 | -0.054932 | -0.10986 | -0.23804 | -0.35248 | -0.17395 | -0.059509 | -0.018311 | 56.2225 | 56.6299 | 122.525 | 122.8226 | -0.10986 | 122.818 | 62.9288 | -0.17395 | 122.8226 | -0.10986 | 62.9288 | 122.525 | 122.818 | -122.9691 | -123.0515
456.3438 | 123.0606 | -60.759 | 62.1185 | -0.027008 | 0.017515 | 0.014234 | 0.006806 | 0.063316 | -0.0027793 | 0.068823 | -60.8322 | 62.059 | -60.8322 | -60.9375 | 61.7981 | 2.1973 | -4.7699 | -4.4632 | 61.9629 | -60.9604 | -0.073242 | -0.059509 | -0.073242 | -0.17853 | -0.32043 | -0.20142 | -0.15564 | 0 | 55.9891 | 56.2958 | 122.5571 | 122.818 | -0.073242 | 122.7219 | 62.9562 | -0.20142 | 122.818 | -0.073242 | 62.9562 | 122.5571 | 122.7219 | -122.9507 | -123.0789
457.3438 | 123.0606 | -60.7819 | 62.0773 | -0.065155 | 0.019865 | 0.017011 | 0.004029 | 0.063529 | -0.0032065 | 0.071814 | -60.8139 | 62.0316 | -60.8459 | -60.9375 | 61.8164 | 2.2156 | -4.7791 | -4.2572 | 62.0224 | -60.9558 | -0.064087 | -0.045777 | -0.032044 | -0.15564 | -0.26093 | -0.17395 | -0.054932 | 0.032043 | 56.0028 | 56.5247 | 122.5983 | 122.8134 | -0.032044 | 122.8043 | 62.9974 | -0.17395 | 122.8134 | -0.032044 | 62.9974 | 122.5983 | 122.8043 | -122.9233 | -123.0331
458.3438 | 123.056 | -60.7727 | 62.0773 | 0.049286 | 0.019224 | 0.010175 | 0.0046698 | 0.065452 | -0.0044883 | 0.070532 | -60.7956 | 62.0178 | -60.8231 | -60.9512 | 61.7889 | 2.211 | -4.9026 | -4.3442 | 62.0224 | -60.9604 | -0.050354 | -0.05951 | -0.022888 | -0.17853 | -0.28839 | -0.18768 | -0.054932 | 0.027466 | 55.8701 | 56.4285 | 122.5616 | 122.7905 | -0.022888 | 122.7951 | 62.9837 | -0.18768 | 122.7905 | -0.022888 | 62.9837 | 122.5616 | 122.7951 | -122.9004 | -123.0377
459.3438 | 123.0698 | -60.7773 | 62.0544 | 0.24002 | 0.020078 | 0.010388 | 0.0010382 | 0.06652 | -0.00021569 | 0.071173 | -60.8826 | 62.0178 | -60.8551 | -61.0016 | 61.7523 | 2.1835 | -5.0537 | -4.4952 | 61.9904 | -60.9512 | -0.07782 | -0.036621 | -0.10529 | -0.2243 | -0.30212 | -0.17395 | -0.064087 | -0.027465 | 55.7236 | 56.282 | 122.5296 | 122.7951 | -0.10529 | 122.7676 | 62.9608 | -0.17395 | 122.7951 | -0.10529 | 62.9608 | 122.5296 | 122.7676 | -122.9095 | -123.0057
460.3438 | 123.0377 | -60.759 | 62.1048 | -0.11856 | 0.01901 | 0.013379 | 0.0046698 | 0.063102 | -0.0017111 | 0.070532 | -60.8368 | 62.0728 | -60.8185 | -60.9467 | 61.8027 | 2.2568 | -4.9988 | -4.4861 | 62.0132 | -60.9375 | -0.059509 | -0.032043 | -0.07782 | -0.18768 | -0.30212 | -0.17853 | -0.091552 | -0.018311 | 55.7602 | 56.2729 | 122.5616 | 122.8317 | -0.07782 | 122.7722 | 63.0157 | -0.17853 | 122.8317 | -0.07782 | 63.0157 | 122.5616 | 122.7722 | -122.9233 | -123.0423
461.3438 | 123.0469 | -60.7452 | 62.1002 | -0.14908 | 0.022428 | 0.0091068 | 0.0038154 | 0.064384 | -0.0036337 | 0.071386 | -60.8368 | 62.0728 | -60.8276 | -60.9421 | 61.7981 | 2.2842 | -5.0491 | -4.5868 | 62.027 | -60.9283 | -0.082398 | -0.027466 | -0.091553 | -0.19684 | -0.30212 | -0.18311 | -0.073242 | -0.009155 | 55.6961 | 56.1584 | 122.5433 | 122.818 | -0.091553 | 122.7722 | 63.0295 | -0.18311 | 122.818 | -0.091553 | 63.0295 | 122.5433 | 122.7722 | -122.9279 | -123.0286
462.3438 | 123.056 | -60.7407 | 62.1002 | -0.14908 | 0.018583 | 0.010388 | 0.003388 | 0.065452 | -0.0023519 | 0.070959 | -60.8459 | 62.0773 | -60.8231 | -60.9421 | 61.7935 | 2.3026 | -5.0949 | -4.6463 | 62.0453 | -60.9192 | -0.082397 | -0.022888 | -0.10529 | -0.20142 | -0.3067 | -0.17853 | -0.054932 | -0.022888 | 55.6458 | 56.0944 | 122.5342 | 122.818 | -0.10529 | 122.7859 | 63.0432 | -0.17853 | 122.818 | -0.10529 | 63.0432 | 122.5342 | 122.7859 | -122.9233 | -123.0194
463.3438 | 123.0194 | -60.7636 | 62.1002 | 0.079804 | 0.020078 | 0.015088 | 0.0059516 | 0.065452 | -0.0010703 | 0.070105 | -60.8597 | 62.027 | -60.8459 | -60.9879 | 61.7386 | 2.2476 | -5.2643 | -4.8614 | 62.027 | -60.9558 | -0.082397 | -0.073242 | -0.09613 | -0.2243 | -0.36163 | -0.19226 | -0.073242 | -0.013733 | 55.4993 | 55.9021 | 122.5021 | 122.7905 | -0.09613 | 122.7905 | 63.0112 | -0.19226 | 122.7905 | -0.09613 | 63.0112 | 122.5021 | 122.7905 | -122.9462 | -123.056
464.3438 | 123.0331 | -60.7819 | 62.0499 | 0.11795 | 0.01837 | 0.018506 | 0.0031744 | 0.063957 | -0.0034201 | 0.072882 | -60.9009 | 62.0087 | -60.8597 | -61.0291 | 61.7111 | 2.2614 | -5.4062 | -4.9896 | 61.9812 | -60.9467 | -0.07782 | -0.041199 | -0.11902 | -0.24719 | -0.33875 | -0.16479 | -0.068665 | -0.041199 | 55.3757 | 55.7922 | 122.493 | 122.7905 | -0.11902 | 122.7631 | 63.0432 | -0.16479 | 122.7905 | -0.11902 | 63.0432 | 122.493 | 122.7631 | -122.9095 | -122.9965
465.3438 | 123.0835 | -60.7544 | 62.0819 | -0.11093 | 0.019438 | 0.01167 | 0.0055244 | 0.066734 | -0.0034201 | 0.071814 | -60.8002 | 62.0773 | -60.8459 | -60.9192 | 61.7844 | 2.3895 | -5.4428 | -4.9438 | 62.0087 | -60.9192 | -0.091552 | -0.004577 | -0.045776 | -0.16479 | -0.29755 | -0.16479 | -0.073242 | 0.045776 | 55.3116 | 55.8105 | 122.5388 | 122.8317 | -0.045776 | 122.7631 | 63.1439 | -0.16479 | 122.8317 | -0.045776 | 63.1439 | 122.5388 | 122.7631 | -122.9279 | -123.0011
466.3438 | 123.0377 | -60.7498 | 62.0956 | -1.7741 | 0.020078 | 0.015302 | 0.0065924 | 0.062889 | -0.0025657 | 0.073309 | -60.8459 | 62.0407 | -60.8185 | -60.9146 | 61.7935 | 2.4216 | -5.5527 | -5.0308 | 62.0407 | -60.9055 | -0.068664 | -0.054932 | -0.09613 | -0.16479 | -0.30212 | -0.15564 | -0.054932 | -0.027466 | 55.1971 | 55.719 | 122.5433 | 122.7905 | -0.09613 | 122.7905 | 63.1714 | -0.15564 | 122.7905 | -0.09613 | 63.1714 | 122.5433 | 122.7905 | -122.9141 | -123.0011
467.3438 | 123.0194 | -60.7681 | 62.1002 | 0.049286 | 0.019224 | 0.017865 | 0.0044562 | 0.065025 | -0.0044883 | 0.069464 | -60.8139 | 62.0453 | -60.8276 | -60.9512 | 61.7569 | 2.3804 | -5.6259 | -5.1682 | 62.0224 | -60.9375 | -0.05951 | -0.054932 | -0.045777 | -0.18311 | -0.34332 | -0.16937 | -0.07782 | 0.013733 | 55.1422 | 55.6 | 122.525 | 122.8134 | -0.045777 | 122.7905 | 63.1485 | -0.16937 | 122.8134 | -0.045777 | 63.1485 | 122.525 | 122.7905 | -122.9279 | -123.0377
468.3438 | 123.0194 | -60.759 | 62.1414 | -0.14145 | 0.017729 | 0.010175 | 0.00061099 | 0.062461 | -0.0025657 | 0.069677 | -60.8597 | 62.0728 | -60.8276 | -60.9787 | 61.7523 | 2.4307 | -5.5893 | -5.2551 | 62.0407 | -60.9009 | -0.068665 | -0.068664 | -0.10071 | -0.21973 | -0.3891 | -0.14191 | -0.10071 | -0.032043 | 55.1697 | 55.5038 | 122.5113 | 122.8317 | -0.10071 | 122.7997 | 63.1897 | -0.14191 | 122.8317 | -0.10071 | 63.1897 | 122.5113 | 122.7997 | -122.9691 | -123.0423
469.3438 | 123.0057 | -60.7681 | 62.0865 | 0.041657 | 0.020933 | 0.014661 | 0.0053106 | 0.065452 | -0.0051291 | 0.070318 | -60.8414 | 62.059 | -60.8231 | -60.9879 | 61.7386 | 2.4399 | -5.777 | -5.3925 | 62.0499 | -60.9238 | -0.054932 | -0.027466 | -0.073243 | -0.21973 | -0.3479 | -0.15564 | -0.036621 | -0.018311 | 54.9911 | 55.3757 | 122.5067 | 122.8271 | -0.073243 | 122.818 | 63.208 | -0.15564 | 122.8271 | -0.073243 | 63.208 | 122.5067 | 122.818 | -122.9095 | -123.0103
470.3438 | 123.0469 | -60.7727 | 62.0773 | 0.25528 | 0.017729 | 0.015729 | 0.00232 | 0.065238 | -2.092e-06 | 0.070105 | -60.8459 | 62.0361 | -60.8505 | -60.9833 | 61.7386 | 2.4719 | -5.9509 | -5.5069 | 61.9949 | -60.9146 | -0.07782 | -0.041199 | -0.073242 | -0.21057 | -0.33875 | -0.14191 | -0.082398 | 0.004578 | 54.8218 | 55.2658 | 122.5113 | 122.8088 | -0.073242 | 122.7676 | 63.2446 | -0.14191 | 122.8088 | -0.073242 | 63.2446 | 122.5113 | 122.7676 | -122.9279 | -122.9919
471.3438 | 123.056 | -60.7544 | 62.1185 | 0.11032 | 0.020078 | 0.012097 | 0.0048834 | 0.062889 | -0.0038473 | 0.069891 | -60.7864 | 62.0544 | -60.8047 | -60.9283 | 61.7889 | 2.5681 | -5.9784 | -5.5252 | 61.9904 | -60.9512 | -0.050354 | -0.064087 | -0.032043 | -0.17395 | -0.32959 | -0.19684 | -0.12817 | 0.018311 | 54.776 | 55.2292 | 122.5433 | 122.8088 | -0.032043 | 122.7448 | 63.3224 | -0.19684 | 122.8088 | -0.032043 | 63.3224 | 122.5433 | 122.7448 | -122.9233 | -123.0698
472.3438 | 123.0011 | -60.7727 | 62.0956 | 0.29343 | 0.020933 | 0.017011 | 0.0046698 | 0.066093 | -0.0034201 | 0.070959 | -60.8414 | 62.059 | -60.8368 | -61.0336 | 61.6928 | 2.4857 | -6.0425 | -5.7358 | 62.0087 | -60.9329 | -0.064087 | -0.036621 | -0.068665 | -0.26093 | -0.40283 | -0.16022 | -0.086975 | -0.004578 | 54.7302 | 55.0369 | 122.4655 | 122.8317 | -0.068665 | 122.7814 | 63.2584 | -0.16022 | 122.8317 | -0.068665 | 63.2584 | 122.4655 | 122.7814 | -122.9324 | -123.0286
473.3438 | 123.056 | -60.7361 | 62.1094 | -0.13382 | 0.020506 | 0.011884 | 0.0036018 | 0.063957 | -0.0034201 | 0.069891 | -60.8185 | 62.0453 | -60.7864 | -60.9283 | 61.7752 | 2.6184 | -6.0287 | -5.7175 | 62.0178 | -60.9283 | -0.050354 | -0.064087 | -0.082397 | -0.19226 | -0.33417 | -0.19226 | -0.091553 | -0.032043 | 54.7073 | 55.0186 | 122.5113 | 122.7814 | -0.082397 | 122.7539 | 63.3545 | -0.19226 | 122.7814 | -0.082397 | 63.3545 | 122.5113 | 122.7539 | -122.8958 | -123.0377
474.3438 | 123.1064 | -60.759 | 62.0544 | 0.26291 | 0.019651 | 0.012738 | 0.0029608 | 0.063102 | -0.00064309 | 0.070532 | -60.8276 | 61.9904 | -60.8322 | -60.9558 | 61.7798 | 2.5955 | -6.3538 | -5.8502 | 61.9995 | -60.8871 | -0.073242 | -0.064087 | -0.068665 | -0.19684 | -0.27466 | -0.12817 | -0.054931 | 0.004577 | 54.4052 | 54.9088 | 122.5388 | 122.7493 | -0.068665 | 122.7585 | 63.3545 | -0.12817 | 122.7493 | -0.068665 | 63.3545 | 122.5388 | 122.7585 | -122.8867 | -122.9416
475.3438 | 123.0698 | -60.7498 | 62.0865 | -0.1033 | 0.019651 | 0.015943 | 0.0027472 | 0.063743 | -0.00085669 | 0.070746 | -60.8047 | 62.0636 | -60.7773 | -60.9146 | 61.7844 | 2.6779 | -6.2164 | -5.864 | 62.0087 | -60.9283 | -0.027466 | -0.022888 | -0.054932 | -0.16479 | -0.30212 | -0.17853 | -0.07782 | -0.027466 | 54.5334 | 54.8859 | 122.5342 | 122.8134 | -0.054932 | 122.7585 | 63.4277 | -0.17853 | 122.8134 | -0.054932 | 63.4277 | 122.5342 | 122.7585 | -122.8638 | -123.0148
476.3438 | 123.1293 | -60.6949 | 62.1094 | 0.48416 | 0.019865 | 0.012525 | -0.003875 | 0.063102 | -0.0055563 | 0.070532 | -60.7681 | 61.9446 | -60.7864 | -60.8688 | 61.8713 | 2.8152 | -6.3904 | -5.8319 | 61.9812 | -60.8551 | -0.091553 | -0.16479 | -0.073242 | -0.17395 | -0.23804 | -0.16022 | -0.12817 | 0.018311 | 54.3045 | 54.863 | 122.5662 | 122.6395 | -0.073242 | 122.6761 | 63.5101 | -0.16022 | 122.6395 | -0.073242 | 63.5101 | 122.5662 | 122.6761 | -122.8958 | -122.9645
477.3438 | 123.0286 | -60.759 | 62.146 | -0.1796 | 0.01901 | 0.011243 | 0.004029 | 0.06417 | -0.00064309 | 0.070105 | -60.8322 | 62.0682 | -60.7956 | -60.9741 | 61.7523 | 2.7283 | -6.2805 | -6.0699 | 62.059 | -60.91 | -0.036621 | -0.07782 | -0.073242 | -0.21515 | -0.39368 | -0.15106 | -0.086975 | -0.036621 | 54.4785 | 54.689 | 122.5113 | 122.8271 | -0.073242 | 122.818 | 63.4872 | -0.15106 | 122.8271 | -0.073242 | 63.4872 | 122.5113 | 122.818 | -122.9416 | -123.056
478.3438 | 122.9874 | -60.7544 | 62.0728 | 0.14084 | 0.020292 | 0.013806 | 0.0063788 | 0.065879 | -0.0027793 | 0.071814 | -60.8368 | 62.0407 | -60.8093 | -61.0016 | 61.6882 | 2.6825 | -6.4407 | -6.2531 | 62.0499 | -60.9329 | -0.054931 | -0.032044 | -0.082397 | -0.24719 | -0.38452 | -0.17853 | -0.022888 | -0.027466 | 54.3137 | 54.5013 | 122.4426 | 122.7951 | -0.082397 | 122.8043 | 63.4369 | -0.17853 | 122.7951 | -0.082397 | 63.4369 | 122.4426 | 122.8043 | -122.8821 | -123.0057
479.3438 | 123.056 | -60.7498 | 62.0773 | 0.20187 | 0.020078 | 0.014447 | 0.0029608 | 0.065879 | -0.0032065 | 0.067114 | -60.8597 | 62.0087 | -60.8185 | -60.9833 | 61.7157 | 2.6871 | -6.6055 | -6.3538 | 62.027 | -60.9009 | -0.068664 | -0.068665 | -0.10986 | -0.23346 | -0.36163 | -0.15106 | -0.050354 | -0.041199 | 54.1443 | 54.3961 | 122.4655 | 122.7585 | -0.10986 | 122.7768 | 63.4369 | -0.15106 | 122.7585 | -0.10986 | 63.4369 | 122.4655 | 122.7768 | -122.8958 | -122.9782
480.3438 | 123.1476 | -60.7224 | 62.0773 | 0.24765 | 0.01837 | 0.010388 | 0.0018928 | 0.065666 | -0.0023519 | 0.070318 | -60.8002 | 61.9995 | -60.8185 | -60.9329 | 61.7889 | 2.7786 | -6.7657 | -6.3583 | 62.0041 | -60.8963 | -0.09613 | -0.07782 | -0.07782 | -0.21057 | -0.28839 | -0.17395 | -0.073243 | 0.01831 | 53.9566 | 54.364 | 122.5113 | 122.7219 | -0.07782 | 122.7264 | 63.501 | -0.17395 | 122.7219 | -0.07782 | 63.501 | 122.5113 | 122.7264 | -122.8958 | -122.9736
481.3438 | 123.1155 | -60.704 | 62.0682 | 0.2095 | 0.016233 | 0.013806 | -0.00045721 | 0.062889 | -0.0014975 | 0.070746 | -60.7819 | 61.94 | -60.8047 | -60.9055 | 61.7889 | 2.8656 | -6.9351 | -6.4133 | 61.9675 | -60.8871 | -0.10071 | -0.12817 | -0.077819 | -0.20142 | -0.27924 | -0.18311 | -0.10071 | 0.022889 | 53.7689 | 54.2908 | 122.493 | 122.644 | -0.077819 | 122.6715 | 63.5696 | -0.18311 | 122.644 | -0.077819 | 63.5696 | 122.493 | 122.6715 | -122.8729 | -122.9553
482.3438 | 123.0515 | -60.7315 | 62.1002 | -0.11093 | 0.020292 | 0.015943 | 0.005738 | 0.062034 | -0.0027793 | 0.070532 | -60.7681 | 62.059 | -60.8093 | -60.9146 | 61.7844 | 2.9114 | -6.7657 | -6.5048 | 62.0316 | -60.8963 | -0.07782 | -0.041199 | -0.036621 | -0.18311 | -0.31586 | -0.16479 | -0.068665 | 0.041199 | 53.9658 | 54.2267 | 122.5159 | 122.7905 | -0.036621 | 122.7631 | 63.6429 | -0.16479 | 122.7905 | -0.036621 | 63.6429 | 122.5159 | 122.7631 | -122.9095 | -122.9965
483.3438 | 123.0515 | -60.7315 | 62.1506 | -0.13382 | 0.01837 | 0.010388 | 0.0038154 | 0.064811 | -0.0021383 | 0.070532 | -60.7681 | 62.0773 | -60.7727 | -60.8963 | 61.7752 | 2.8564 | -6.8848 | -6.6055 | 62.0728 | -60.91 | -0.041199 | -0.073242 | -0.036621 | -0.16479 | -0.37537 | -0.17853 | -0.07782 | 0.004578 | 53.8467 | 54.126 | 122.5067 | 122.8088 | -0.036621 | 122.8043 | 63.588 | -0.17853 | 122.8088 | -0.036621 | 63.588 | 122.5067 | 122.8043 | -122.9233 | -123.0606
484.3438 | 123.175 | -60.7407 | 62.0956 | 0.24002 | 0.019438 | 0.010602 | 0.0016792 | 0.065879 | -0.0014975 | 0.070959 | -60.791 | 61.9675 | -60.8368 | -60.8917 | 61.7935 | 2.9297 | -7.1548 | -6.7291 | 61.9812 | -60.8963 | -0.09613 | -0.12817 | -0.050354 | -0.15106 | -0.30212 | -0.15564 | -0.11444 | 0.045776 | 53.5858 | 54.0115 | 122.5342 | 122.7081 | -0.050354 | 122.7219 | 63.6703 | -0.15564 | 122.7081 | -0.050354 | 63.6703 | 122.5342 | 122.7219 | -122.9324 | -122.9919
485.3438 | 123.0743 | -60.7315 | 62.114 | -0.11856 | 0.019865 | 0.014447 | 0.007447 | 0.062889 | -0.0019247 | 0.069037 | -60.8047 | 62.1002 | -60.8047 | -60.9192 | 61.7661 | 2.9709 | -6.9809 | -6.7703 | 62.0316 | -60.8963 | -0.073243 | -0.013733 | -0.073243 | -0.18768 | -0.3479 | -0.16479 | -0.082398 | 0 | 53.7506 | 53.9612 | 122.4976 | 122.8317 | -0.073243 | 122.7631 | 63.7024 | -0.16479 | 122.8317 | -0.073243 | 63.7024 | 122.4976 | 122.7631 | -122.9187 | -123.0103
486.3438 | 123.2208 | -60.704 | 62.1277 | 0.11795 | 0.015806 | 0.0086796 | -0.0023798 | 0.062675 | -0.0032065 | 0.071814 | -60.8322 | 61.9537 | -60.8047 | -60.9604 | 61.7844 | 2.9617 | -7.251 | -6.8619 | 62.0041 | -60.8688 | -0.10071 | -0.17395 | -0.12817 | -0.25635 | -0.34332 | -0.16479 | -0.1236 | -0.027465 | 53.4531 | 53.8422 | 122.4884 | 122.6578 | -0.12817 | 122.7081 | 63.6658 | -0.16479 | 122.6578 | -0.12817 | 63.6658 | 122.4884 | 122.7081 | -122.9324 | -122.9965
487.3438 | 123.0331 | -60.7544 | 62.146 | 0.034027 | 0.020078 | 0.012525 | 0.0072332 | 0.065238 | -0.0066245 | 0.070105 | -60.7727 | 62.0728 | -60.7636 | -60.91 | 61.7432 | 2.9938 | -7.251 | -6.9992 | 62.0544 | -60.8734 | -0.009155 | -0.073242 | -0.01831 | -0.15564 | -0.40283 | -0.11902 | -0.091553 | -0.009155 | 53.5034 | 53.7552 | 122.4976 | 122.8271 | -0.01831 | 122.8088 | 63.7482 | -0.11902 | 122.8271 | -0.01831 | 63.7482 | 122.4976 | 122.8088 | -122.9095 | -123.0194
488.3438 | 123.0423 | -60.7361 | 62.1323 | 0.10269 | 0.021574 | 0.017224 | 0.0076606 | 0.064598 | -0.0027793 | 0.070105 | -60.7864 | 62.0499 | -60.8002 | -60.9512 | 61.7157 | 3.0258 | -7.2372 | -7.1274 | 62.0453 | -60.9055 | -0.064087 | -0.082397 | -0.050354 | -0.21515 | -0.41656 | -0.16937 | -0.086975 | 0.013733 | 53.4988 | 53.6087 | 122.4518 | 122.7859 | -0.050354 | 122.7814 | 63.7619 | -0.16937 | 122.7859 | -0.050354 | 63.7619 | 122.4518 | 122.7814 | -122.9324 | -123.0377
489.3438 | 123.0469 | -60.7636 | 62.114 | 0.20187 | 0.01837 | 0.012738 | 0.0048834 | 0.066734 | 0.00021151 | 0.073095 | -60.8368 | 62.0499 | -60.8002 | -60.997 | 61.6837 | 3.0075 | -7.4341 | -7.283 | 62.0453 | -60.9055 | -0.036621 | -0.064087 | -0.073242 | -0.23346 | -0.4303 | -0.14191 | -0.068665 | -0.036621 | 53.3295 | 53.4805 | 122.4472 | 122.8134 | -0.073242 | 122.8088 | 63.7711 | -0.14191 | 122.8134 | -0.073242 | 63.7711 | 122.4472 | 122.8088 | -122.9141 | -123.0194
490.3438 | 123.0606 | -60.7178 | 62.1368 | -0.080414 | 0.017301 | 0.011884 | 0.0044562 | 0.064384 | -0.0034201 | 0.070746 | -60.7681 | 62.0819 | -60.7956 | -60.8917 | 61.7752 | 3.1494 | -7.4753 | -7.2098 | 62.0544 | -60.8871 | -0.07782 | -0.054932 | -0.050354 | -0.17395 | -0.36163 | -0.16937 | -0.082398 | 0.027466 | 53.2425 | 53.508 | 122.493 | 122.7997 | -0.050354 | 122.7722 | 63.8672 | -0.16937 | 122.7997 | -0.050354 | 63.8672 | 122.493 | 122.7722 | -122.9324 | -123.024
491.3438 | 123.1293 | -60.704 | 62.0773 | 0.19424 | 0.015165 | 0.01167 | -0.0019524 | 0.065452 | -0.0014975 | 0.072668 | -60.7498 | 61.9492 | -60.8002 | -60.8871 | 61.7981 | 3.1952 | -7.7683 | -7.3013 | 62.0132 | -60.8459 | -0.09613 | -0.12817 | -0.045776 | -0.18311 | -0.27924 | -0.14191 | -0.064087 | 0.050354 | 52.9358 | 53.4027 | 122.5021 | 122.6532 | -0.045776 | 122.7173 | 63.8992 | -0.14191 | 122.6532 | -0.045776 | 63.8992 | 122.5021 | 122.7173 | -122.8775 | -122.9233
492.3438 | 123.2117 | -60.7681 | 62.0636 | 0.072174 | 0.019865 | 0.012097 | 0.007447 | 0.064384 | -0.0023519 | 0.069891 | -60.8231 | 62.0682 | -60.8093 | -60.9833 | 61.6653 | 3.1174 | -7.6126 | -7.5439 | 62.0773 | -60.9146 | -0.041199 | 0.004577 | -0.054932 | -0.21515 | -0.39826 | -0.14648 | 0.013733 | -0.013733 | 53.1555 | 53.2242 | 122.4335 | 122.8363 | -0.054932 | 122.8455 | 63.8855 | -0.14648 | 122.8363 | -0.054932 | 63.8855 | 122.4335 | 122.8455 | -122.8729 | -122.9782
493.3438 | 123.0423 | -60.7178 | 62.1048 | 0.087433 | 0.020719 | 0.014875 | 0.0065924 | 0.065666 | -0.0029929 | 0.070105 | -60.7498 | 62.0956 | -60.759 | -60.8826 | 61.7386 | 3.2913 | -7.695 | -7.4524 | 62.0499 | -60.8871 | -0.041199 | -0.009155 | -0.032044 | -0.16479 | -0.36621 | -0.16937 | -0.054931 | 0.009155 | 53.0228 | 53.2654 | 122.4564 | 122.8134 | -0.032044 | 122.7676 | 64.0091 | -0.16937 | 122.8134 | -0.032044 | 64.0091 | 122.4564 | 122.7676 | -122.8638 | -122.9919
494.3438 | 123.0789 | -60.7407 | 62.114 | 0.20187 | 0.01901 | 0.011243 | 0.0016792 | 0.065666 | -0.0034201 | 0.0716 | -60.8322 | 62.0407 | -60.8322 | -60.965 | 61.6928 | 3.2318 | -7.8506 | -7.6584 | 61.9949 | -60.8917 | -0.091552 | -0.073243 | -0.091552 | -0.2243 | -0.42114 | -0.15106 | -0.11902 | 0 | 52.89 | 53.0823 | 122.4335 | 122.7814 | -0.091552 | 122.7356 | 63.9725 | -0.15106 | 122.7814 | -0.091552 | 63.9725 | 122.4335 | 122.7356 | -122.9462 | -123.0057
495.3438 | 123.0972 | -60.7315 | 62.146 | 1.2776 | 0.015592 | 0.010816 | 0.007447 | 0.062461 | -0.0044883 | 0.0716 | -60.553 | 62.1048 | -60.7819 | -60.8917 | 61.7844 | 3.2867 | -7.8735 | -7.5943 | 62.0544 | -60.9009 | -0.050354 | -0.041199 | 0.17853 | -0.16022 | -0.36163 | -0.16937 | -0.091553 | 0.22888 | 52.858 | 53.1372 | 122.5159 | 122.8363 | 0.17853 | 122.7859 | 64.0182 | -0.16937 | 122.8363 | 0.17853 | 64.0182 | 122.5159 | 122.7859 | -122.9279 | -123.0469
496.3438 | 123.0652 | -60.7224 | 62.1277 | -0.057526 | 0.019865 | 0.015729 | 0.0036018 | 0.063743 | -0.0040609 | 0.0716 | -60.965 | 62.0636 | -60.8185 | -60.8826 | 61.7752 | 3.3463 | -7.9285 | -7.7042 | 62.0728 | -60.8826 | -0.09613 | -0.064087 | -0.24261 | -0.16022 | -0.35248 | -0.16022 | -0.054932 | -0.14648 | 52.7939 | 53.0182 | 122.4976 | 122.786 | -0.24261 | 122.7951 | 64.0686 | -0.16022 | 122.786 | -0.24261 | 64.0686 | 122.4976 | 122.7951 | -122.9462 | -123.0103
497.3438 | 123.0469 | -60.7224 | 62.1689 | -0.14908 | 0.01901 | 0.0091068 | 0.0025336 | 0.065238 | -0.0032065 | 0.071173 | -60.7864 | 62.1094 | -60.7819 | -60.9055 | 61.7569 | 3.3463 | -7.9834 | -7.8644 | 62.0911 | -60.878 | -0.059509 | -0.059509 | -0.064087 | -0.18311 | -0.41199 | -0.15564 | -0.07782 | -0.004578 | 52.739 | 52.858 | 122.4792 | 122.8317 | -0.064087 | 122.8134 | 64.0686 | -0.15564 | 122.8317 | -0.064087 | 64.0686 | 122.4792 | 122.8134 | -122.9507 | -123.0469
498.3438 | 123.0286 | -60.7269 | 62.1643 | 0.095062 | 0.018797 | 0.0097476 | 0.0061652 | 0.063529 | -0.0027793 | 0.070959 | -60.7956 | 62.1048 | -60.7819 | -60.9604 | 61.6928 | 3.2593 | -8.1573 | -8.0521 | 62.059 | -60.91 | -0.054931 | -0.05951 | -0.068664 | -0.23346 | -0.4715 | -0.18311 | -0.10529 | -0.013733 | 52.5696 | 52.6749 | 122.4197 | 122.8317 | -0.068664 | 122.7859 | 63.9862 | -0.18311 | 122.8317 | -0.068664 | 63.9862 | 122.4197 | 122.7859 | -122.9462 | -123.0743
499.3438 | 123.0835 | -60.7315 | 62.0819 | 0.2095 | 0.020078 | 0.014234 | 0.0031744 | 0.065879 | -0.0017111 | 0.0716 | -60.791 | 62.0636 | -60.7956 | -60.9192 | 61.7386 | 3.3875 | -8.3725 | -8.0521 | 62.0041 | -60.9146 | -0.064087 | -0.01831 | -0.05951 | -0.18768 | -0.34332 | -0.18311 | -0.07782 | 0.004577 | 52.359 | 52.6794 | 122.4701 | 122.7951 | -0.05951 | 122.7356 | 64.119 | -0.18311 | 122.7951 | -0.05951 | 64.119 | 122.4701 | 122.7356 | -122.8775 | -122.9965
500.3438 | 123.0423 | -60.7224 | 62.1506 | 0.072174 | 0.020078 | 0.011029 | 0.005097 | 0.063957 | -0.0032065 | 0.070532 | -60.8047 | 62.1002 | -60.8139 | -60.9512 | 61.6928 | 3.3554 | -8.2901 | -8.1665 | 62.0453 | -60.9146 | -0.091553 | -0.050354 | -0.082398 | -0.22888 | -0.45776 | -0.19226 | -0.10529 | 0.009155 | 52.4323 | 52.5558 | 122.4152 | 122.8226 | -0.082398 | 122.7676 | 64.0778 | -0.19226 | 122.8226 | -0.082398 | 64.0778 | 122.4152 | 122.7676 | -122.9645 | -123.0652
501.3438 | 123.0789 | -60.7361 | 62.1643 | -0.13382 | 0.018156 | 0.0084658 | 0.003388 | 0.063316 | -0.0034201 | 0.071173 | -60.7773 | 62.1231 | -60.8002 | -60.9283 | 61.7294 | 3.4195 | -8.3084 | -8.2077 | 62.0773 | -60.8963 | -0.064087 | -0.041199 | -0.041199 | -0.19226 | -0.43488 | -0.16022 | -0.086975 | 0.022888 | 52.4277 | 52.5284 | 122.4655 | 122.8592 | -0.041199 | 122.8134 | 64.1556 | -0.16022 | 122.8592 | -0.041199 | 64.1556 | 122.4655 | 122.8134 | -122.9645 | -123.0606
502.3438 | 123.0606 | -60.704 | 62.1323 | -0.095673 | 0.020506 | 0.012097 | 0.004029 | 0.064384 | -0.0023519 | 0.068823 | -60.7544 | 62.1048 | -60.7636 | -60.8826 | 61.7569 | 3.4882 | -8.5007 | -8.2397 | 62.0773 | -60.8734 | -0.059509 | -0.027466 | -0.050354 | -0.17853 | -0.37537 | -0.16937 | -0.054931 | 0.009155 | 52.2034 | 52.4643 | 122.4609 | 122.8088 | -0.050354 | 122.7814 | 64.1922 | -0.16937 | 122.8088 | -0.050354 | 64.1922 | 122.4609 | 122.7814 | -122.8958 | -123.0057
503.3438 | 123.0698 | -60.6857 | 62.1735 | -0.19485 | 0.020506 | 0.013593 | 0.0053106 | 0.06417 | -0.0034201 | 0.070532 | -60.7498 | 62.0865 | -60.7681 | -60.8643 | 61.7294 | 3.5248 | -8.638 | -8.3817 | 62.0865 | -60.8688 | -0.082397 | -0.086975 | -0.064087 | -0.17853 | -0.44403 | -0.1831 | -0.086975 | 0.01831 | 52.0477 | 52.3041 | 122.4152 | 122.7722 | -0.064087 | 122.7722 | 64.2105 | -0.1831 | 122.7722 | -0.064087 | 64.2105 | 122.4152 | 122.7722 | -122.9416 | -123.0423
504.3438 | 123.1613 | -60.7132 | 62.114 | 0.2095 | 0.016874 | 0.010175 | -0.0015252 | 0.063529 | -0.0023519 | 0.071386 | -60.7452 | 62.027 | -60.7727 | -60.8688 | 61.7477 | 3.6026 | -8.8806 | -8.4137 | 62.0041 | -60.9009 | -0.059509 | -0.086975 | -0.032043 | -0.15564 | -0.36621 | -0.18768 | -0.10986 | 0.027466 | 51.8326 | 52.2995 | 122.4609 | 122.7402 | -0.032043 | 122.7173 | 64.3158 | -0.18768 | 122.7402 | -0.032043 | 64.3158 | 122.4609 | 122.7173 | -122.8867 | -123.0148
505.3438 | 123.0331 | -60.7178 | 62.1323 | 0.24002 | 0.019651 | 0.013379 | 0.0063788 | 0.06182 | -0.0012839 | 0.068609 | -60.8139 | 62.0911 | -60.8093 | -60.9879 | 61.6562 | 3.5065 | -8.7662 | -8.6151 | 62.0499 | -60.9009 | -0.091553 | -0.041199 | -0.096131 | -0.27008 | -0.47607 | -0.18311 | -0.082397 | -0.004578 | 51.9516 | 52.1027 | 122.374 | 122.8088 | -0.096131 | 122.7676 | 64.2242 | -0.18311 | 122.8088 | -0.096131 | 64.2242 | 122.374 | 122.7676 | -122.9416 | -123.0331
506.3438 | 123.0011 | -60.7361 | 62.1094 | 0.16373 | 0.020506 | 0.012097 | 0.0061652 | 0.064384 | -0.0017111 | 0.071386 | -60.8047 | 62.114 | -60.7956 | -60.9924 | 61.6287 | 3.5202 | -8.7662 | -8.6975 | 62.059 | -60.9192 | -0.059509 | 0.004578 | -0.068665 | -0.25635 | -0.48065 | -0.18311 | -0.050354 | -0.009156 | 51.9699 | 52.0386 | 122.3648 | 122.85 | -0.068665 | 122.7951 | 64.2563 | -0.18311 | 122.85 | -0.068665 | 64.2563 | 122.3648 | 122.7951 | -122.905 | -123.0286
507.3438 | 123.1018 | -60.7636 | 62.0865 | 0.11795 | 0.019651 | 0.013593 | 0.0063788 | 0.065452 | -0.0017111 | 0.072027 | -60.8047 | 62.1094 | -60.7956 | -60.9879 | 61.6287 | 3.5156 | -8.9081 | -8.8028 | 62.0682 | -60.8963 | -0.032043 | 0.022888 | -0.041199 | -0.2243 | -0.45776 | -0.13275 | -0.018311 | -0.009156 | 51.8555 | 51.9608 | 122.3923 | 122.8729 | -0.041199 | 122.8317 | 64.2792 | -0.13275 | 122.8729 | -0.041199 | 64.2792 | 122.3923 | 122.8317 | -122.8821 | -122.9828
508.3438 | 123.0469 | -60.7315 | 62.1414 | 0.22476 | 0.019865 | 0.01637 | 0.005097 | 0.065238 | -0.0032065 | 0.069677 | -60.8047 | 62.0956 | -60.8185 | -60.9833 | 61.647 | 3.5706 | -9.0271 | -8.9172 | 62.0682 | -60.9009 | -0.086975 | -0.045776 | -0.073243 | -0.25177 | -0.49438 | -0.16937 | -0.073242 | 0.013732 | 51.7044 | 51.8143 | 122.3785 | 122.8271 | -0.073243 | 122.7997 | 64.3021 | -0.16937 | 122.8271 | -0.073243 | 64.3021 | 122.3785 | 122.7997 | -122.9599 | -123.0423
509.3438 | 123.111 | -60.6903 | 62.0956 | 0.20187 | 0.019651 | 0.014234 | 0.00018379 | 0.062675 | -0.0019247 | 0.069464 | -60.7407 | 62.0087 | -60.759 | -60.8688 | 61.7432 | 3.7628 | -9.256 | -8.8165 | 62.0316 | -60.8597 | -0.068664 | -0.086975 | -0.050354 | -0.17853 | -0.35248 | -0.16937 | -0.064087 | 0.01831 | 51.4343 | 51.8738 | 122.4335 | 122.699 | -0.050354 | 122.7219 | 64.4531 | -0.16937 | 122.699 | -0.050354 | 64.4531 | 122.4335 | 122.7219 | -122.8546 | -122.9553
510.3438 | 123.0103 | -60.7269 | 62.1506 | 0.056915 | 0.021147 | 0.014661 | 0.0061652 | 0.065238 | -0.0014975 | 0.071814 | -60.7498 | 62.1231 | -60.7819 | -60.9283 | 61.6699 | 3.6942 | -9.1919 | -9.0271 | 62.0773 | -60.9009 | -0.054931 | -0.027466 | -0.022888 | -0.20142 | -0.48065 | -0.17395 | -0.073242 | 0.032043 | 51.535 | 51.6998 | 122.3969 | 122.85 | -0.022888 | 122.8043 | 64.4211 | -0.17395 | 122.85 | -0.022888 | 64.4211 | 122.3969 | 122.8043 | -122.9324 | -123.0515
511.3438 | 123.0148 | -60.7178 | 62.1323 | 0.079804 | 0.018797 | 0.018506 | 0.006806 | 0.065025 | -0.0019247 | 0.071173 | -60.7681 | 62.1185 | -60.791 | -60.9238 | 61.6745 | 3.7033 | -9.1873 | -9.0683 | 62.0728 | -60.8917 | -0.073243 | -0.013733 | -0.050354 | -0.20599 | -0.45776 | -0.17395 | -0.059509 | 0.022889 | 51.5305 | 51.6495 | 122.3923 | 122.8363 | -0.050354 | 122.7905 | 64.4211 | -0.17395 | 122.8363 | -0.050354 | 64.4211 | 122.3923 | 122.7905 | -122.9233 | -123.024
512.3438 | 123.0423 | -60.7407 | 62.1323 | 0.18662 | 0.020506 | 0.0097476 | 0.0031744 | 0.065025 | -0.0023519 | 0.071814 | -60.8047 | 62.1048 | -60.8139 | -60.9787 | 61.6287 | 3.7399 | -9.3201 | -9.1919 | 62.0728 | -60.9009 | -0.073242 | -0.027466 | -0.064087 | -0.23804 | -0.50354 | -0.16022 | -0.059509 | 0.009155 | 51.4206 | 51.5488 | 122.3694 | 122.8455 | -0.064087 | 122.8134 | 64.4806 | -0.16022 | 122.8455 | -0.064087 | 64.4806 | 122.3694 | 122.8134 | -122.9462 | -123.0331
513.3438 | 123.111 | -60.6766 | 62.1094 | 0.24002 | 0.01837 | 0.01167 | 0.003388 | 0.06182 | -0.0017111 | 0.072882 | -60.878 | 62.0041 | -60.7773 | -60.8597 | 61.7111 | 3.8498 | -9.5673 | -9.1827 | 62.0087 | -60.8734 | -0.10071 | -0.10529 | -0.20142 | -0.1831 | -0.39825 | -0.19684 | -0.10071 | -0.10071 | 51.1093 | 51.4938 | 122.3877 | 122.6807 | -0.20142 | 122.6852 | 64.5264 | -0.19684 | 122.6807 | -0.20142 | 64.5264 | 122.3877 | 122.6852 | -122.8867 | -122.9828
514.3438 | 123.1155 | -60.6995 | 62.1231 | 0.20187 | 0.01901 | 0.014447 | 0.0036018 | 0.062889 | -0.00085669 | 0.070959 | -60.7544 | 62.0636 | -60.7773 | -60.9055 | 61.6974 | 3.8177 | -9.6313 | -9.3018 | 62.0178 | -60.8734 | -0.07782 | -0.059509 | -0.054932 | -0.20599 | -0.42572 | -0.17395 | -0.10529 | 0.022888 | 51.0681 | 51.3977 | 122.3969 | 122.7631 | -0.054932 | 122.7173 | 64.5172 | -0.17395 | 122.7631 | -0.054932 | 64.5172 | 122.3969 | 122.7173 | -122.9004 | -122.9965
515.3438 | 123.024 | -60.704 | 62.1368 | 0.13321 | 0.020292 | 0.016584 | 0.00232 | 0.063529 | -0.0010703 | 0.070746 | -60.8276 | 62.114 | -60.791 | -60.8734 | 61.6882 | 3.7491 | -9.4757 | -9.494 | 62.0911 | -60.91 | -0.086975 | -0.022888 | -0.1236 | -0.16937 | -0.44861 | -0.20599 | -0.045777 | -0.036621 | 51.2283 | 51.21 | 122.3923 | 122.818 | -0.1236 | 122.7951 | 64.4531 | -0.20599 | 122.818 | -0.1236 | 64.4531 | 122.3923 | 122.7951 | -122.9279 | -123.0469
516.3438 | 123.1338 | -60.6903 | 62.114 | -0.027008 | 0.018156 | 0.015088 | -0.00045721 | 0.063102 | -0.0017111 | 0.070746 | -60.672 | 62.0682 | -60.7544 | -60.8505 | 61.7569 | 3.9459 | -9.8557 | -9.4482 | 61.9995 | -60.8734 | -0.064087 | -0.045777 | 0.018311 | -0.16022 | -0.35706 | -0.1831 | -0.11444 | 0.082398 | 50.8347 | 51.2421 | 122.4472 | 122.7585 | 0.018311 | 122.6898 | 64.6362 | -0.1831 | 122.7585 | 0.018311 | 64.6362 | 122.4472 | 122.6898 | -122.8683 | -122.9874
517.3438 | 123.0743 | -60.704 | 62.1689 | -0.034637 | 0.018156 | 0.011457 | 0.0059516 | 0.064598 | -0.0027793 | 0.069891 | -60.704 | 62.1414 | -60.7361 | -60.7224 | 61.7752 | 3.9093 | -9.581 | -9.5261 | 62.0819 | -60.8551 | -0.032043 | -0.027466 | 0 | -0.01831 | -0.39368 | -0.15106 | -0.086975 | 0.032043 | 51.123 | 51.178 | 122.4792 | 122.8455 | 0 | 122.7859 | 64.6133 | -0.15106 | 122.8455 | 0 | 64.6133 | 122.4792 | 122.7859 | -122.905 | -123.024
518.3438 | 123.0194 | -60.7178 | 62.1643 | 0.034027 | 0.020933 | 0.01637 | 0.0055244 | 0.06417 | -0.0025657 | 0.071386 | -60.7864 | 62.1002 | -60.7773 | -60.9375 | 61.615 | 3.9093 | -9.7778 | -9.7321 | 62.0682 | -60.8963 | -0.05951 | -0.064087 | -0.068665 | -0.21973 | -0.54932 | -0.17853 | -0.096131 | -0.009155 | 50.9399 | 50.9857 | 122.3328 | 122.818 | -0.068665 | 122.7859 | 64.6271 | -0.17853 | 122.818 | -0.068665 | 64.6271 | 122.3328 | 122.7859 | -122.9416 | -123.0606
519.3281 | 123.1018 | -60.6949 | 62.1002 | 0.24765 | 0.019224 | 0.013806 | 0.003388 | 0.063743 | -0.00042929 | 0.06925 | -60.7544 | 62.0865 | -60.7864 | -60.8871 | 61.6653 | 4.01 | -10.0067 | -9.7733 | 62.0407 | -60.8871 | -0.091553 | -0.013733 | -0.05951 | -0.19226 | -0.43488 | -0.19226 | -0.05951 | 0.032043 | 50.6882 | 50.9216 | 122.3602 | 122.7814 | -0.05951 | 122.7356 | 64.7049 | -0.19226 | 122.7814 | -0.05951 | 64.7049 | 122.3602 | 122.7356 | -122.8867 | -122.9874
520.3438 | 123.1384 | -60.6674 | 62.1323 | 0.23239 | 0.019651 | 0.015515 | 0.0031744 | 0.063316 | -0.0014975 | 0.070532 | -60.7315 | 62.0865 | -60.7498 | -60.8688 | 61.7157 | 4.0878 | -10.144 | -9.8602 | 62.0224 | -60.8551 | -0.082398 | -0.045776 | -0.064087 | -0.20142 | -0.41656 | -0.18768 | -0.10986 | 0.018311 | 50.5234 | 50.8072 | 122.3831 | 122.7539 | -0.064087 | 122.6898 | 64.7552 | -0.18768 | 122.7539 | -0.064087 | 64.7552 | 122.3831 | 122.6898 | -122.8821 | -122.9874
521.3438 | 123.1522 | -60.672 | 62.1231 | 0.25528 | 0.019224 | 0.014447 | 0.0038154 | 0.064384 | -0.00064309 | 0.070532 | -60.6903 | 62.0407 | -60.7498 | -60.8551 | 61.7294 | 4.1702 | -10.2722 | -9.9014 | 62.0178 | -60.8643 | -0.07782 | -0.082398 | -0.018311 | -0.18311 | -0.39368 | -0.19226 | -0.10529 | 0.059509 | 50.3998 | 50.7706 | 122.4014 | 122.7127 | -0.018311 | 122.6898 | 64.8422 | -0.19226 | 122.7127 | -0.018311 | 64.8422 | 122.4014 | 122.6898 | -122.8729 | -122.9874
522.3438 | 123.0423 | -60.6949 | 62.1368 | 0.22476 | 0.022428 | 0.0093204 | 0.005097 | 0.06182 | -0.0010703 | 0.070532 | -60.7681 | 62.1185 | -60.7773 | -60.9283 | 61.6196 | 4.0787 | -10.1669 | -10.1074 | 62.059 | -60.878 | -0.082398 | -0.018311 | -0.073242 | -0.23346 | -0.51727 | -0.18311 | -0.07782 | 0.009156 | 50.528 | 50.5875 | 122.3145 | 122.8134 | -0.073242 | 122.7539 | 64.7736 | -0.18311 | 122.8134 | -0.073242 | 64.7736 | 122.3145 | 122.7539 | -122.9141 | -123.0148
523.3438 | 123.0698 | -60.7086 | 62.1414 | 0.22476 | 0.020506 | 0.014661 | 0.004029 | 0.063743 | -0.0019247 | 0.072241 | -60.759 | 62.1231 | -60.7956 | -60.9283 | 61.615 | 4.0924 | -10.2264 | -10.1624 | 62.0544 | -60.9192 | -0.086975 | -0.01831 | -0.050354 | -0.21973 | -0.52643 | -0.21057 | -0.086975 | 0.036621 | 50.4822 | 50.5463 | 122.3236 | 122.8317 | -0.050354 | 122.7631 | 64.801 | -0.21057 | 122.8317 | -0.050354 | 64.801 | 122.3236 | 122.7631 | -122.937 | -123.0606
524.3438 | 123.0286 | -60.6766 | 62.1323 | 0.1561 | 0.020292 | 0.011457 | -0.00045721 | 0.062248 | -0.00064309 | 0.072241 | -60.7407 | 62.0773 | -60.7636 | -60.8917 | 61.6562 | 4.1702 | -10.3043 | -10.1028 | 62.0499 | -60.8414 | -0.086975 | -0.054931 | -0.064087 | -0.21515 | -0.47607 | -0.16479 | -0.082397 | 0.022888 | 50.3723 | 50.5737 | 122.3328 | 122.7539 | -0.064087 | 122.7264 | 64.8468 | -0.16479 | 122.7539 | -0.064087 | 64.8468 | 122.3328 | 122.7264 | -122.8958 | -122.9736
525.3438 | 123.1522 | -60.672 | 62.1231 | -0.057526 | 0.020078 | 0.013806 | 0.004029 | 0.065025 | -0.0027793 | 0.073736 | -60.6995 | 62.0636 | -60.7315 | -60.8276 | 61.7111 | 4.2618 | -10.5331 | -10.231 | 62.0178 | -60.8643 | -0.059509 | -0.059509 | -0.027466 | -0.15564 | -0.41199 | -0.19226 | -0.10529 | 0.032043 | 50.1389 | 50.441 | 122.3831 | 122.7356 | -0.027466 | 122.6898 | 64.9338 | -0.19226 | 122.7356 | -0.027466 | 64.9338 | 122.3831 | 122.6898 | -122.8546 | -122.9874
526.3281 | 123.1064 | -60.6766 | 62.146 | 0.92667 | 0.017729 | 0.006116 | 0.0016792 | 0.062034 | -0.0021383 | 0.070746 | -60.7224 | 62.0819 | -60.7407 | -60.8917 | 61.6608 | 4.2847 | -10.4691 | -10.3363 | 62.0407 | -60.8414 | -0.064087 | -0.064087 | -0.045776 | -0.21515 | -0.48523 | -0.16479 | -0.10529 | 0.018311 | 50.2075 | 50.3403 | 122.3373 | 122.7585 | -0.045776 | 122.7173 | 64.9612 | -0.16479 | 122.7585 | -0.045776 | 64.9612 | 122.3373 | 122.7173 | -122.8867 | -122.9874
527.3438 | 123.1338 | -60.672 | 62.114 | 0.37735 | 0.01837 | 0.012525 | 0.006806 | 0.062675 | -0.00064309 | 0.068823 | -60.6537 | 62.0636 | -60.7452 | -60.8322 | 61.6882 | 4.3625 | -10.643 | -10.3821 | 62.0178 | -60.8459 | -0.073242 | -0.050354 | 0.01831 | -0.16022 | -0.42572 | -0.17395 | -0.096131 | 0.091552 | 50.029 | 50.2899 | 122.3602 | 122.7356 | 0.01831 | 122.6898 | 65.0345 | -0.17395 | 122.7356 | 0.01831 | 65.0345 | 122.3602 | 122.6898 | -122.8592 | -122.9599
528.3281 | 123.1476 | -60.6354 | 62.1506 | -0.12619 | 0.017515 | 0.014875 | 0.0016792 | 0.06118 | -0.0051291 | 0.069677 | -60.64 | 62.1002 | -60.7269 | -60.7773 | 61.7523 | 4.4495 | -10.6155 | -10.405 | 62.0499 | -60.8093 | -0.091553 | -0.050354 | -0.004578 | -0.14191 | -0.39825 | -0.17395 | -0.10071 | 0.086975 | 50.0198 | 50.2304 | 122.3877 | 122.7356 | -0.004578 | 122.6852 | 65.0848 | -0.17395 | 122.7356 | -0.004578 | 65.0848 | 122.3877 | 122.6852 | -122.8775 | -122.9599
529.3438 | 123.2162 | -60.6628 | 62.1414 | -0.13382 | 0.018156 | 0.010388 | 0.0021064 | 0.060325 | -0.0010703 | 0.068396 | -60.6308 | 62.059 | -60.7086 | -60.7544 | 61.7569 | 4.3762 | -10.1028 | -10.3867 | 62.1048 | -60.8185 | -0.045776 | -0.082397 | 0.032044 | -0.091553 | -0.38452 | -0.15564 | -0.036621 | 0.07782 | 50.56 | 50.2762 | 122.4197 | 122.7219 | 0.032044 | 122.7676 | 65.0391 | -0.15564 | 122.7219 | 0.032044 | 65.0391 | 122.4197 | 122.7676 | -122.85 | -122.9599
530.3281 | 123.1613 | -60.6445 | 62.1735 | -0.057526 | 0.017088 | 0.012525 | 0.003388 | 0.060325 | -0.0021383 | 0.069677 | -60.64 | 62.0819 | -60.6949 | -60.7773 | 61.7477 | 4.4952 | -10.7803 | -10.5331 | 62.0911 | -60.8231 | -0.050354 | -0.091553 | 0.004577 | -0.13275 | -0.42572 | -0.17853 | -0.082398 | 0.054931 | 49.8642 | 50.1114 | 122.3923 | 122.7264 | 0.004577 | 122.7356 | 65.1398 | -0.17853 | 122.7264 | 0.004577 | 65.1398 | 122.3923 | 122.7356 | -122.8683 | -122.9965
531.3281 | 123.0789 | -60.6537 | 62.1643 | 1.2852 | 0.018797 | 0.011884 | 0.00232 | 0.059684 | -0.00085669 | 0.069464 | -60.6628 | 62.0819 | -60.7498 | -60.878 | 61.6425 | 4.4128 | -10.8627 | -10.7574 | 62.0316 | -60.8459 | -0.09613 | -0.082398 | -0.009155 | -0.2243 | -0.52185 | -0.19226 | -0.13275 | 0.086975 | 49.791 | 49.8962 | 122.2961 | 122.7356 | -0.009155 | 122.6852 | 65.0665 | -0.19226 | 122.7356 | -0.009155 | 65.0665 | 122.2961 | 122.6852 | -122.9141 | -123.0103
532.3438 | 123.1293 | -60.6674 | 62.1735 | 0.18662 | 0.017942 | 0.01167 | 0.0036018 | 0.059471 | -0.0025657 | 0.071173 | -60.6857 | 62.059 | -60.7315 | -60.8688 | 61.6379 | 4.4907 | -10.9406 | -10.8353 | 62.0132 | -60.8414 | -0.064087 | -0.11444 | -0.018311 | -0.20142 | -0.53558 | -0.17395 | -0.16022 | 0.045776 | 49.7269 | 49.8322 | 122.3053 | 122.7264 | -0.018311 | 122.6807 | 65.1581 | -0.17395 | 122.7264 | -0.018311 | 65.1581 | 122.3053 | 122.6807 | -122.905 | -123.0148
533.3438 | 123.1293 | -60.6766 | 62.1277 | 0.16373 | 0.01837 | 0.012738 | 0.0059516 | 0.060539 | -0.0038473 | 0.072027 | -60.6583 | 62.0636 | -60.7361 | -60.8093 | 61.6653 | 4.5685 | -11.0733 | -10.8673 | 62.0087 | -60.8322 | -0.059509 | -0.064087 | 0.018311 | -0.13275 | -0.46234 | -0.15564 | -0.11902 | 0.07782 | 49.6033 | 49.8093 | 122.3419 | 122.7402 | 0.018311 | 122.6852 | 65.2451 | -0.15564 | 122.7402 | 0.018311 | 65.2451 | 122.3419 | 122.6852 | -122.8638 | -122.9599
534.3281 | 123.1659 | -60.6583 | 62.1735 | 0.049286 | 0.018156 | 0.012097 | 0.004029 | 0.060111 | -0.00064309 | 0.070532 | -60.704 | 62.0865 | -60.7361 | -60.8368 | 61.6745 | 4.5959 | -11.0504 | -10.9314 | 62.0544 | -60.8368 | -0.07782 | -0.086975 | -0.045777 | -0.17853 | -0.49896 | -0.17853 | -0.11902 | 0.032043 | 49.6078 | 49.7269 | 122.3328 | 122.7448 | -0.045777 | 122.7127 | 65.2542 | -0.17853 | 122.7448 | -0.045777 | 65.2542 | 122.3328 | 122.7127 | -122.9095 | -123.0103
535.3281 | 123.143 | -60.6628 | 62.146 | 0.2095 | 0.018583 | 0.013806 | 0.0063788 | 0.062889 | -0.0029929 | 0.071814 | -60.6537 | 62.0361 | -60.7224 | -60.8139 | 61.6653 | 4.6143 | -11.2381 | -11.0458 | 62.0316 | -60.8231 | -0.059509 | -0.10986 | 0.009155 | -0.15106 | -0.48065 | -0.16022 | -0.11444 | 0.068664 | 49.4247 | 49.617 | 122.3282 | 122.699 | 0.009155 | 122.6944 | 65.2771 | -0.16022 | 122.699 | 0.009155 | 65.2771 | 122.3282 | 122.6944 | -122.8683 | -122.9691
536.3281 | 123.0881 | -60.6812 | 62.1506 | 0.19424 | 0.020078 | 0.012525 | 0.0016792 | 0.061607 | -0.0017111 | 0.070318 | -60.6812 | 62.0682 | -60.7269 | -60.8459 | 61.6516 | 4.66 | -11.2152 | -11.1282 | 62.0407 | -60.8459 | -0.045777 | -0.082398 | 0 | -0.1648 | -0.49896 | -0.1648 | -0.10986 | 0.045777 | 49.4659 | 49.5529 | 122.3328 | 122.7493 | 0 | 122.7219 | 65.3412 | -0.1648 | 122.7493 | 0 | 65.3412 | 122.3328 | 122.7219 | -122.8775 | -122.9965
537.3281 | 123.1338 | -60.6766 | 62.1597 | 0.026398 | 0.017515 | 0.013593 | 0.0014654 | 0.05883 | -0.0021383 | 0.070318 | -60.6995 | 62.0819 | -60.704 | -60.8459 | 61.6562 | 4.7562 | -11.1923 | -11.1557 | 62.0361 | -60.8414 | -0.027466 | -0.07782 | -0.022888 | -0.16937 | -0.50354 | -0.16479 | -0.1236 | 0.004578 | 49.4843 | 49.5209 | 122.3328 | 122.7585 | -0.022888 | 122.7127 | 65.4327 | -0.16479 | 122.7585 | -0.022888 | 65.4327 | 122.3328 | 122.7127 | -122.8638 | -123.0011
538.3281 | 123.143 | -60.6583 | 62.1368 | 0.24002 | 0.018797 | 0.015943 | 0.0053106 | 0.063529 | -0.0021383 | 0.070532 | -60.6491 | 62.0544 | -60.7269 | -60.8047 | 61.6653 | 4.7653 | -11.3617 | -11.2244 | 62.0544 | -60.8368 | -0.068665 | -0.082398 | 0.009155 | -0.14648 | -0.4715 | -0.17853 | -0.082398 | 0.07782 | 49.2966 | 49.4339 | 122.3236 | 122.7127 | 0.009155 | 122.7127 | 65.4236 | -0.17853 | 122.7127 | 0.009155 | 65.4236 | 122.3236 | 122.7127 | -122.8638 | -122.9736
539.3281 | 123.1338 | -60.6995 | 62.2147 | 0.11032 | 0.019438 | 0.015943 | 0.0093696 | 0.063743 | -0.0034201 | 0.070318 | -60.7224 | 62.1552 | -60.7773 | -60.9055 | 61.5326 | 4.7104 | -11.1603 | -11.879 | 62.0316 | -60.91 | -0.07782 | -0.05951 | -0.022888 | -0.20599 | -0.68207 | -0.21057 | -0.18311 | 0.054932 | 49.5392 | 48.8205 | 122.2321 | 122.8546 | -0.022888 | 122.731 | 65.4099 | -0.21057 | 122.8546 | -0.022888 | 65.4099 | 122.2321 | 122.731 | -122.9919 | -123.1247
540.3281 | 123.1476 | -60.64 | 62.1826 | 0.026398 | 0.01837 | 0.010175 | 0.00039739 | 0.062248 | -0.0025657 | 0.069891 | -60.64 | 62.1048 | -60.7132 | -60.7956 | 61.6791 | 4.9713 | -11.3068 | -11.2244 | 62.0407 | -60.8002 | -0.073242 | -0.07782 | 0 | -0.15564 | -0.50354 | -0.16022 | -0.14191 | 0.073242 | 49.3332 | 49.4156 | 122.319 | 122.7448 | 0 | 122.6807 | 65.6113 | -0.16022 | 122.7448 | 0 | 65.6113 | 122.319 | 122.6807 | -122.8958 | -122.9828
541.3281 | 123.1338 | -60.6537 | 62.1277 | 0.23239 | 0.019438 | 0.014234 | 0.0076606 | 0.063316 | -0.0010703 | 0.069677 | -60.6628 | 62.0728 | -60.7681 | -60.8322 | 61.6379 | 4.9164 | -11.4441 | -11.3754 | 62.0407 | -60.8093 | -0.11444 | -0.054932 | -0.009155 | -0.17853 | -0.48981 | -0.15564 | -0.086976 | 0.10529 | 49.2096 | 49.2783 | 122.2916 | 122.7264 | -0.009155 | 122.6944 | 65.5701 | -0.15564 | 122.7264 | -0.009155 | 65.5701 | 122.2916 | 122.6944 | -122.8958 | -122.937
542.3281 | 123.0148 | -60.6949 | 62.1872 | 0.095062 | 0.019224 | 0.013379 | 0.0083014 | 0.063743 | -0.0019247 | 0.071173 | -60.7178 | 62.1597 | -60.7544 | -60.9055 | 61.5372 | 4.8157 | -11.3434 | -11.5677 | 62.1094 | -60.8917 | -0.05951 | -0.027466 | -0.022888 | -0.21057 | -0.65002 | -0.19684 | -0.07782 | 0.036622 | 49.3515 | 49.1272 | 122.2321 | 122.8546 | -0.022888 | 122.8043 | 65.5106 | -0.19684 | 122.8546 | -0.022888 | 65.5106 | 122.2321 | 122.8043 | -122.9416 | -123.0789
543.3281 | 123.1201 | -60.6903 | 62.1323 | 0.25528 | 0.019865 | 0.013593 | 0.0038154 | 0.064811 | -0.0023519 | 0.071814 | -60.6903 | 62.1368 | -60.759 | -60.8505 | 61.6241 | 4.9622 | -11.5677 | -11.5036 | 62.0132 | -60.8505 | -0.068664 | 0.004578 | 0 | -0.16022 | -0.50812 | -0.16022 | -0.11902 | 0.068664 | 49.1226 | 49.1867 | 122.3145 | 122.8271 | 0 | 122.7036 | 65.6525 | -0.16022 | 122.8271 | 0 | 65.6525 | 122.3145 | 122.7036 | -122.8912 | -122.9828
544.3281 | 123.1659 | -60.6491 | 62.1323 | 0.7283 | 0.019651 | 0.012952 | 0.0029608 | 0.062675 | -0.00085669 | 0.070532 | -60.6216 | 62.1002 | -60.7178 | -60.8276 | 61.647 | 5.0766 | -11.618 | -11.554 | 62.0041 | -60.8231 | -0.068664 | -0.032043 | 0.027466 | -0.17853 | -0.48523 | -0.17395 | -0.12817 | 0.09613 | 49.0311 | 49.0952 | 122.2961 | 122.7493 | 0.027466 | 122.6532 | 65.7257 | -0.17395 | 122.7493 | 0.027466 | 65.7257 | 122.2961 | 122.6532 | -122.85 | -122.9553
545.3281 | 123.0927 | -60.6537 | 62.146 | 0.16373 | 0.01901 | 0.012097 | 0.0025336 | 0.063529 | -0.0023519 | 0.070105 | -60.6628 | 62.0956 | -60.7452 | -60.8276 | 61.6196 | 5.0812 | -11.6409 | -11.5997 | 62.0316 | -60.8093 | -0.091552 | -0.050354 | -0.009155 | -0.17395 | -0.52643 | -0.15564 | -0.11444 | 0.082397 | 49.0128 | 49.054 | 122.2733 | 122.7493 | -0.009155 | 122.6852 | 65.7349 | -0.15564 | 122.7493 | -0.009155 | 65.7349 | 122.2733 | 122.6852 | -122.8912 | -122.9553
546.3281 | 123.0011 | -60.6674 | 62.1964 | 0.16373 | 0.020506 | 0.015302 | 0.0093696 | 0.064598 | -0.0034201 | 0.069677 | -60.704 | 62.1597 | -60.7544 | -60.9055 | 61.5326 | 5.0262 | -11.4944 | -11.8011 | 62.0773 | -60.8643 | -0.086976 | -0.036621 | -0.036622 | -0.23804 | -0.66376 | -0.19684 | -0.11902 | 0.050354 | 49.173 | 48.8663 | 122.2 | 122.8271 | -0.036622 | 122.7448 | 65.6937 | -0.19684 | 122.8271 | -0.036622 | 65.6937 | 122.2 | 122.7448 | -122.9507 | -123.0606
547.3281 | 123.0194 | -60.6903 | 62.178 | -1.2248 | 0.019651 | 0.013593 | 0.006806 | 0.065025 | -0.0017111 | 0.072241 | -60.7773 | 62.1643 | -60.7636 | -60.9238 | 61.5097 | 5.0491 | -11.5723 | -11.879 | 62.1094 | -60.8826 | -0.073242 | -0.013733 | -0.086975 | -0.23346 | -0.66834 | -0.19226 | -0.068665 | -0.013733 | 49.118 | 48.8113 | 122.2 | 122.8546 | -0.086975 | 122.7997 | 65.7394 | -0.19226 | 122.8546 | -0.086975 | 65.7394 | 122.2 | 122.7997 | -122.9416 | -123.0606
548.3281 | 123.0469 | -60.7086 | 62.178 | 0.62149 | 0.021787 | 0.011243 | 0.0070196 | 0.063957 | -0.0023519 | 0.070746 | -60.6766 | 62.1597 | -60.7452 | -60.9283 | 61.496 | 5.1544 | -11.5952 | -11.8973 | 62.0956 | -60.8734 | -0.036621 | -0.018311 | 0.032043 | -0.21973 | -0.68207 | -0.16479 | -0.082398 | 0.068664 | 49.1135 | 48.8113 | 122.2046 | 122.8683 | 0.032043 | 122.8043 | 65.863 | -0.16479 | 122.8683 | 0.032043 | 65.863 | 122.2046 | 122.8043 | -122.9233 | -123.0515
549.3281 | 123.1384 | -60.6628 | 62.1277 | 0.5452 | 0.019224 | 0.014234 | 0.003388 | 0.062675 | -0.0021383 | 0.071173 | -60.6033 | 62.114 | -60.7361 | -60.8231 | 61.615 | 5.3467 | -11.8103 | -11.8011 | 62.0316 | -60.8414 | -0.073242 | -0.013733 | 0.059509 | -0.16022 | -0.5127 | -0.17853 | -0.096131 | 0.13275 | 48.8525 | 48.8617 | 122.2778 | 122.7768 | 0.059509 | 122.6944 | 66.0095 | -0.17853 | 122.7768 | 0.059509 | 66.0095 | 122.2778 | 122.6944 | -122.8638 | -122.9691
550.3281 | 123.0927 | -60.6491 | 62.1689 | 0.13321 | 0.018797 | 0.011243 | 0.00018379 | 0.062889 | -0.0017111 | 0.073095 | -60.7178 | 62.0911 | -60.7224 | -60.8734 | 61.5921 | 5.3421 | -11.7462 | -11.8652 | 62.0407 | -60.8414 | -0.073242 | -0.07782 | -0.068664 | -0.2243 | -0.57678 | -0.19226 | -0.12817 | 0.004578 | 48.9029 | 48.7839 | 122.2412 | 122.7402 | -0.068664 | 122.6898 | 65.9912 | -0.19226 | 122.7402 | -0.068664 | 65.9912 | 122.2412 | 122.6898 | -122.8912 | -123.0103
551.3438 | 123.0148 | -60.6628 | 62.2238 | -0.20248 | 0.019438 | 0.010388 | 0.005097 | 0.06118 | -0.0055563 | 0.069464 | -60.6537 | 62.1643 | -60.7178 | -60.8643 | 61.5509 | 5.3375 | -11.5723 | -11.8652 | 62.1368 | -60.8276 | -0.054931 | -0.059509 | 0.009155 | -0.20142 | -0.67291 | -0.1648 | -0.086975 | 0.064086 | 49.0906 | 48.7976 | 122.2137 | 122.8271 | 0.009155 | 122.7997 | 66.0004 | -0.1648 | 122.8271 | 0.009155 | 66.0004 | 122.2137 | 122.7997 | -122.9416 | -123.0515
552.7031 | 122.9736 | -60.6079 | 62.1643 | -0.080414 | 0.014952 | 0.011029 | 0.00018379 | 0.063957 | -0.0042747 | 0.070959 | -60.6033 | 62.0453 | -60.7132 | -60.7544 | 61.6608 | 5.5389 | -11.8103 | -11.4166 | 62.1231 | -60.7178 | -0.10529 | -0.11902 | 0.004577 | -0.14649 | -0.50354 | -0.10986 | -0.041199 | 0.10986 | 48.7976 | 49.1913 | 122.2687 | 122.6532 | 0.004577 | 122.731 | 66.1469 | -0.10986 | 122.6532 | 0.004577 | 66.1469 | 122.2687 | 122.731 | -122.8775 | -122.8821
553.3906 | 123.1384 | -60.6033 | 62.2009 | 0.011139 | 0.016233 | 0.009534 | 0.003388 | 0.060111 | -0.0059835 | 0.070746 | -60.5988 | 62.0499 | -60.704 | -60.759 | 61.6333 | 5.5161 | -11.8195 | -11.8469 | 62.0773 | -60.7681 | -0.10071 | -0.15106 | 0.004578 | -0.15564 | -0.56763 | -0.16479 | -0.1236 | 0.10529 | 48.7839 | 48.7564 | 122.2366 | 122.6532 | 0.004578 | 122.6807 | 66.1194 | -0.16479 | 122.6532 | 0.004578 | 66.1194 | 122.2366 | 122.6807 | -122.905 | -122.9691
554.3281 | 123.1201 | -60.6583 | 62.1552 | 0.2095 | 0.017301 | 0.01402 | 0.0061652 | 0.060325 | -0.0042747 | 0.070746 | -60.672 | 62.0865 | -60.7727 | -60.8551 | 61.5372 | 5.4291 | -11.9385 | -12.0255 | 62.0361 | -60.8643 | -0.11444 | -0.068664 | -0.013733 | -0.19684 | -0.61798 | -0.20599 | -0.11902 | 0.10071 | 48.7198 | 48.6328 | 122.1954 | 122.7448 | -0.013733 | 122.6944 | 66.0873 | -0.20599 | 122.7448 | -0.013733 | 66.0873 | 122.1954 | 122.6944 | -122.9279 | -123.0194
555.3281 | 123.1293 | -60.6674 | 62.146 | 0.25528 | 0.018583 | 0.013806 | 0.0059516 | 0.063316 | -0.0038473 | 0.072027 | -60.6628 | 62.1002 | -60.759 | -60.8459 | 61.5601 | 5.4703 | -11.9659 | -12.0438 | 62.0316 | -60.8414 | -0.091553 | -0.045776 | 0.004577 | -0.17853 | -0.58594 | -0.17395 | -0.11444 | 0.09613 | 48.7015 | 48.6237 | 122.2275 | 122.7676 | 0.004577 | 122.699 | 66.1377 | -0.17395 | 122.7676 | 0.004577 | 66.1377 | 122.2275 | 122.699 | -122.905 | -122.9874
556.3281 | 123.1201 | -60.64 | 62.1552 | 0.22476 | 0.017515 | 0.01402 | 0.0072332 | 0.062034 | -0.0027793 | 0.071814 | -60.6537 | 62.0911 | -60.7544 | -60.8414 | 61.5555 | 5.5252 | -11.9934 | -11.9888 | 62.0361 | -60.8276 | -0.11444 | -0.064087 | -0.013733 | -0.20142 | -0.59967 | -0.18768 | -0.11902 | 0.10071 | 48.6465 | 48.6511 | 122.1954 | 122.731 | -0.013733 | 122.6761 | 66.1652 | -0.18768 | 122.731 | -0.013733 | 66.1652 | 122.1954 | 122.6761 | -122.9095 | -122.9828
557.3438 | 123.1064 | -60.6216 | 62.1872 | -0.17197 | 0.015806 | 0.010602 | 0.0036018 | 0.059898 | -0.0023519 | 0.070532 | -60.6125 | 62.0728 | -60.7224 | -60.7773 | 61.615 | 5.6534 | -11.8057 | -11.9156 | 62.0636 | -60.7956 | -0.10071 | -0.11444 | 0.009155 | -0.15564 | -0.57221 | -0.17395 | -0.1236 | 0.10986 | 48.8159 | 48.7061 | 122.2366 | 122.6944 | 0.009155 | 122.6852 | 66.275 | -0.17395 | 122.6944 | 0.009155 | 66.275 | 122.2366 | 122.6852 | -122.9095 | -122.9828
558.3281 | 123.0286 | -60.6491 | 62.1689 | 0.26291 | 0.020078 | 0.012952 | 0.0063788 | 0.062675 | -0.0029929 | 0.0716 | -60.6857 | 62.114 | -60.759 | -60.8963 | 61.4685 | 5.5664 | -11.9431 | -12.1765 | 62.0544 | -60.8368 | -0.10986 | -0.054931 | -0.036621 | -0.24719 | -0.70038 | -0.18768 | -0.11444 | 0.073242 | 48.7061 | 48.4726 | 122.1176 | 122.7631 | -0.036621 | 122.7036 | 66.2155 | -0.18768 | 122.7631 | -0.036621 | 66.2155 | 122.1176 | 122.7036 | -122.9279 | -123.0057
559.3281 | 123.1522 | -60.64 | 62.1826 | 0.22476 | 0.01837 | 0.012525 | 0.0072332 | 0.062461 | -0.0032065 | 0.072668 | -60.6125 | 62.0819 | -60.7407 | -60.8093 | 61.5509 | 5.7678 | -12.3871 | -12.1674 | 61.9949 | -60.8368 | -0.10071 | -0.10071 | 0.027466 | -0.16937 | -0.63171 | -0.19684 | -0.18768 | 0.12817 | 48.2529 | 48.4726 | 122.1909 | 122.7219 | 0.027466 | 122.6349 | 66.4078 | -0.19684 | 122.7219 | 0.027466 | 66.4078 | 122.1909 | 122.6349 | -122.9233 | -123.0194
560.3281 | 123.1247 | -60.6216 | 62.1368 | 0.23239 | 0.01837 | 0.011029 | 0.0042426 | 0.063316 | -0.0029929 | 0.071814 | -60.6125 | 62.0682 | -60.7269 | -61.0336 | 61.6699 | 5.8685 | -12.1078 | -12.0987 | 62.0728 | -60.7864 | -0.10529 | -0.068665 | 0.009155 | -0.41199 | -0.46692 | -0.16479 | -0.064087 | 0.11444 | 48.5138 | 48.5229 | 122.2916 | 122.6898 | 0.009155 | 122.6944 | 66.4902 | -0.16479 | 122.6898 | 0.009155 | 66.4902 | 122.2916 | 122.6944 | -122.8638 | -122.9233
561.3281 | 123.1247 | -60.64 | 62.1231 | 0.19424 | 0.018797 | 0.012097 | 0.0038154 | 0.06182 | -0.0040609 | 0.070746 | -60.6216 | 62.059 | -60.7269 | -60.8139 | 61.5555 | 5.777 | -12.0209 | -12.0666 | 62.0361 | -60.8093 | -0.086975 | -0.064087 | 0.018311 | -0.17395 | -0.56763 | -0.16937 | -0.086975 | 0.10529 | 48.6191 | 48.5733 | 122.1954 | 122.699 | 0.018311 | 122.6761 | 66.4169 | -0.16937 | 122.699 | 0.018311 | 66.4169 | 122.1954 | 122.6761 | -122.85 | -122.9324
562.3438 | 123.2574 | -60.6079 | 62.2559 | -0.1033 | 0.016447 | 0.01167 | 0.00082459 | 0.059684 | -0.0038473 | 0.072882 | -60.5988 | 62.0316 | -60.7269 | -60.759 | 61.5967 | 5.9555 | -11.8881 | -11.9064 | 62.0682 | -60.7727 | -0.11902 | -0.2243 | 0.009155 | -0.15106 | -0.65918 | -0.1648 | -0.18768 | 0.12817 | 48.7198 | 48.7015 | 122.2046 | 122.6395 | 0.009155 | 122.6761 | 66.5634 | -0.1648 | 122.6395 | 0.009155 | 66.5634 | 122.2046 | 122.6761 | -122.9828 | -123.0286
563.3281 | 123.1201 | -60.6445 | 62.1735 | 0.1561 | 0.017088 | 0.013379 | 0.0044562 | 0.062461 | -0.0029929 | 0.070318 | -60.6125 | 62.0361 | -60.7452 | -60.8276 | 61.5234 | 5.9097 | -11.9339 | -12.085 | 62.0499 | -60.8047 | -0.10071 | -0.13733 | 0.032043 | -0.18311 | -0.65002 | -0.16022 | -0.1236 | 0.13275 | 48.7106 | 48.5596 | 122.168 | 122.6807 | 0.032043 | 122.6944 | 66.5543 | -0.16022 | 122.6807 | 0.032043 | 66.5543 | 122.168 | 122.6944 | -122.9187 | -122.9782
564.3281 | 123.1293 | -60.6171 | 62.146 | 0.63675 | 0.016447 | 0.011884 | 0.0055244 | 0.062675 | -0.0042747 | 0.071814 | -60.5804 | 62.027 | -60.7178 | -60.791 | 61.5326 | 5.9006 | -11.9614 | -12.0483 | 62.0682 | -60.791 | -0.10071 | -0.11902 | 0.036621 | -0.17395 | -0.6134 | -0.17395 | -0.07782 | 0.13733 | 48.6557 | 48.5687 | 122.1497 | 122.644 | 0.036621 | 122.6852 | 66.5176 | -0.17395 | 122.644 | 0.036621 | 66.5176 | 122.1497 | 122.6852 | -122.8638 | -122.937
565.3281 | 123.143 | -60.6308 | 62.1597 | 0.29343 | 0.017729 | 0.012097 | 0.0053106 | 0.062034 | -0.0044883 | 0.0716 | -60.6262 | 62.0224 | -60.7132 | -60.8047 | 61.5005 | 6.0608 | -11.824 | -11.9705 | 62.0544 | -60.7727 | -0.082398 | -0.13733 | 0.004577 | -0.17395 | -0.65918 | -0.14191 | -0.10529 | 0.086975 | 48.8068 | 48.6603 | 122.1313 | 122.6532 | 0.004577 | 122.6852 | 66.6916 | -0.14191 | 122.6532 | 0.004577 | 66.6916 | 122.1313 | 122.6852 | -122.8729 | -122.9324
566.3281 | 123.1293 | -60.6445 | 62.178 | 0.14084 | 0.017515 | 0.010816 | 0.004029 | 0.063102 | -0.0059835 | 0.072882 | -60.6354 | 62.0224 | -60.7407 | -60.8322 | 61.4822 | 6.102 | -11.705 | -11.9339 | 62.0361 | -60.8047 | -0.096131 | -0.15564 | 0.009155 | -0.18768 | -0.6958 | -0.16022 | -0.14191 | 0.10529 | 48.9395 | 48.7106 | 122.1268 | 122.6669 | 0.009155 | 122.6807 | 66.7465 | -0.16022 | 122.6669 | 0.009155 | 66.7465 | 122.1268 | 122.6807 | -122.9187 | -122.9828
567.3281 | 123.0789 | -60.6537 | 62.178 | 0.22476 | 0.018583 | 0.017652 | 0.004029 | 0.058616 | -0.0042747 | 0.071814 | -60.6491 | 62.0453 | -60.7361 | -60.8688 | 61.4685 | 6.1203 | -11.6592 | -11.8927 | 62.0316 | -60.8093 | -0.082397 | -0.13275 | 0.004578 | -0.21515 | -0.70953 | -0.15564 | -0.14649 | 0.086975 | 48.9944 | 48.761 | 122.1222 | 122.699 | 0.004578 | 122.6852 | 66.774 | -0.15564 | 122.699 | 0.004578 | 66.774 | 122.1222 | 122.6852 | -122.9141 | -122.9874
568.3281 | 123.0789 | -60.6674 | 62.1735 | -0.27115 | 0.015165 | 0.010388 | 0.00232 | 0.060539 | -0.0059835 | 0.071173 | -60.7544 | 62.0132 | -60.7224 | -60.8734 | 61.4365 | 6.2027 | -11.5311 | -11.8195 | 62.0682 | -60.791 | -0.054932 | -0.16022 | -0.086976 | -0.20599 | -0.737 | -0.1236 | -0.10529 | -0.032044 | 49.1364 | 48.848 | 122.1039 | 122.6807 | -0.086976 | 122.7356 | 66.8701 | -0.1236 | 122.6807 | -0.086976 | 66.8701 | 122.1039 | 122.7356 | -122.8958 | -122.9645
569.3281 | 123.0927 | -60.6354 | 62.1689 | 0.11032 | 0.017088 | 0.014661 | 0.0038154 | 0.059898 | -0.0038473 | 0.068823 | -60.6857 | 62.027 | -60.7544 | -60.8551 | 61.4594 | 6.2302 | -11.5448 | -11.7966 | 62.0544 | -60.8047 | -0.11902 | -0.14191 | -0.050354 | -0.21973 | -0.70953 | -0.16937 | -0.11444 | 0.068665 | 49.0906 | 48.8388 | 122.0947 | 122.6624 | -0.050354 | 122.6898 | 66.8655 | -0.16937 | 122.6624 | -0.050354 | 66.8655 | 122.0947 | 122.6898 | -122.9233 | -122.9736
570.3281 | 123.1064 | -60.6445 | 62.178 | 0.011139 | 0.01602 | 0.011884 | 0.0021064 | 0.061393 | -0.0032065 | 0.071173 | -60.6537 | 62.0041 | -60.7407 | -60.8459 | 61.4456 | 6.308 | -11.4853 | -11.705 | 62.0728 | -60.8002 | -0.096131 | -0.17395 | -0.009156 | -0.20142 | -0.73242 | -0.15564 | -0.10529 | 0.086975 | 49.1592 | 48.9395 | 122.0901 | 122.6486 | -0.009156 | 122.7173 | 66.9525 | -0.15564 | 122.6486 | -0.009156 | 66.9525 | 122.0901 | 122.7173 | -122.9187 | -122.9782
571.3281 | 123.0148 | -60.6308 | 62.1689 | 0.16373 | 0.016447 | 0.0097476 | 0.0046698 | 0.060539 | -0.0034201 | 0.06925 | -60.6628 | 62.0041 | -60.7498 | -60.8643 | 61.4365 | 6.3766 | -11.4487 | -11.4624 | 62.0728 | -60.7819 | -0.11902 | -0.16479 | -0.032044 | -0.23346 | -0.73242 | -0.15106 | -0.09613 | 0.086975 | 49.1821 | 49.1684 | 122.0673 | 122.6349 | -0.032044 | 122.7036 | 67.0074 | -0.15106 | 122.6349 | -0.032044 | 67.0074 | 122.0673 | 122.7036 | -122.9187 | -122.9507
572.3281 | 123.1247 | -60.6537 | 62.1643 | 0.064545 | 0.015806 | 0.011243 | 0.0044562 | 0.060325 | -0.0047019 | 0.069891 | -60.672 | 62.0041 | -60.7361 | -60.672 | 61.647 | 6.395 | -11.3663 | -11.5768 | 62.0636 | -60.7864 | -0.082397 | -0.16022 | -0.01831 | -0.01831 | -0.51727 | -0.13275 | -0.10071 | 0.064087 | 49.2874 | 49.0768 | 122.3007 | 122.6578 | -0.01831 | 122.7173 | 67.0486 | -0.13275 | 122.6578 | -0.01831 | 67.0486 | 122.3007 | 122.7173 | -122.9004 | -122.9507
573.3281 | 123.1018 | -60.6537 | 62.1597 | 0.034027 | 0.018583 | 0.010816 | 0.0029608 | 0.061607 | -0.0025657 | 0.069677 | -60.6491 | 62.0224 | -60.7636 | -60.8414 | 61.4319 | 6.5918 | -11.2473 | -11.4761 | 62.0636 | -60.7864 | -0.10986 | -0.13733 | 0.004578 | -0.18768 | -0.72784 | -0.13275 | -0.09613 | 0.11444 | 49.4064 | 49.1776 | 122.0856 | 122.6761 | 0.004578 | 122.7173 | 67.2455 | -0.13275 | 122.6761 | 0.004578 | 67.2455 | 122.0856 | 122.7173 | -122.9233 | -122.9462
574.3281 | 123.1659 | -60.6262 | 62.1597 | 0.011139 | 0.017301 | 0.0097476 | 0.0046698 | 0.059898 | -0.0053427 | 0.0716 | -60.6033 | 61.9949 | -60.7224 | -60.7727 | 61.4914 | 6.665 | -11.2061 | -11.2106 | 62.0544 | -60.791 | -0.09613 | -0.16479 | 0.022888 | -0.14648 | -0.66833 | -0.16479 | -0.10529 | 0.11902 | 49.4202 | 49.4156 | 122.1176 | 122.6212 | 0.022888 | 122.6807 | 67.2913 | -0.16479 | 122.6212 | 0.022888 | 67.2913 | 122.1176 | 122.6807 | -122.8821 | -122.9507
575.3281 | 123.143 | -60.6125 | 62.1597 | -0.15671 | 0.015592 | 0.012311 | 0.005097 | 0.060325 | -0.0023519 | 0.070532 | -60.6125 | 61.9858 | -60.7636 | -60.759 | 61.5051 | 6.72 | -11.1649 | -11.1191 | 62.0316 | -60.7636 | -0.15106 | -0.17395 | 0 | -0.14648 | -0.6546 | -0.15106 | -0.12817 | 0.15106 | 49.4476 | 49.4934 | 122.1176 | 122.5983 | 0 | 122.644 | 67.3325 | -0.15106 | 122.5983 | 0 | 67.3325 | 122.1176 | 122.644 | -122.9233 | -122.9233
576.3281 | 123.1659 | -60.64 | 62.1597 | -0.080414 | 0.014524 | 0.0080386 | 0.0065924 | 0.058402 | -0.0049155 | 0.0716 | -60.5896 | 61.9904 | -60.704 | -60.7727 | 61.5051 | 6.8024 | -11.0504 | -10.9909 | 62.0773 | -60.7727 | -0.064087 | -0.16937 | 0.050354 | -0.13275 | -0.6546 | -0.13275 | -0.082397 | 0.11444 | 49.5895 | 49.649 | 122.1451 | 122.6303 | 0.050354 | 122.7173 | 67.4423 | -0.13275 | 122.6303 | 0.050354 | 67.4423 | 122.1451 | 122.7173 | -122.8638 | -122.9324
577.3281 | 123.1567 | -60.6262 | 62.1552 | -0.095673 | 0.015379 | 0.012952 | 0.0048834 | 0.060966 | -0.0053427 | 0.072027 | -60.585 | 61.9949 | -60.7178 | -60.7681 | 61.5051 | 6.8619 | -11.0092 | -10.9039 | 62.0499 | -60.7681 | -0.091552 | -0.16022 | 0.041199 | -0.14191 | -0.65002 | -0.14191 | -0.10528 | 0.13275 | 49.617 | 49.7223 | 122.1313 | 122.6212 | 0.041199 | 122.6761 | 67.4881 | -0.14191 | 122.6212 | 0.041199 | 67.4881 | 122.1313 | 122.6761 | -122.8729 | -122.9233
578.3281 | 123.0652 | -60.6674 | 62.146 | 0.049286 | 0.017942 | 0.011243 | 0.0042426 | 0.057762 | -0.0055563 | 0.069891 | -60.6857 | 61.9949 | -60.7773 | -60.8688 | 61.3998 | 6.8115 | -10.881 | -10.936 | 62.0407 | -60.7819 | -0.10986 | -0.15106 | -0.018311 | -0.20142 | -0.74615 | -0.11444 | -0.10529 | 0.091553 | 49.7864 | 49.7314 | 122.0673 | 122.6624 | -0.018311 | 122.7081 | 67.4789 | -0.11444 | 122.6624 | -0.018311 | 67.4789 | 122.0673 | 122.7081 | -122.9233 | -122.9279
579.3281 | 123.1293 | -60.6583 | 62.1826 | -0.0041198 | 0.018156 | 0.012525 | 0.0065924 | 0.061393 | -0.0029929 | 0.071386 | -60.6262 | 61.9858 | -60.7452 | -60.8231 | 61.4365 | 6.8985 | -10.8307 | -10.7758 | 62.0316 | -60.7864 | -0.086975 | -0.19684 | 0.032043 | -0.16479 | -0.74616 | -0.12817 | -0.15106 | 0.11902 | 49.8276 | 49.8825 | 122.0947 | 122.644 | 0.032043 | 122.6898 | 67.5568 | -0.12817 | 122.644 | 0.032043 | 67.5568 | 122.0947 | 122.6898 | -122.9279 | -122.9691
580.3281 | 123.0286 | -60.6125 | 62.1368 | -0.049896 | 0.01602 | 0.01167 | 0.005738 | 0.060539 | -0.0055563 | 0.071386 | -60.5759 | 61.9904 | -60.7315 | -60.7544 | 61.4914 | 7.0129 | -10.8215 | -10.4416 | 62.059 | -60.7636 | -0.11902 | -0.14648 | 0.036621 | -0.14191 | -0.64545 | -0.15106 | -0.07782 | 0.15564 | 49.791 | 50.1709 | 122.1039 | 122.6028 | 0.036621 | 122.6715 | 67.6254 | -0.15106 | 122.6028 | 0.036621 | 67.6254 | 122.1039 | 122.6715 | -122.8683 | -122.9004
581.3281 | 123.143 | -60.6445 | 62.1689 | -0.15671 | 0.016661 | 0.01167 | 0.0046698 | 0.059471 | -0.0051291 | 0.070746 | -60.5988 | 62.0041 | -60.7132 | -60.7773 | 61.4639 | 7.1045 | -10.643 | -10.5011 | 62.0224 | -60.7819 | -0.068665 | -0.16479 | 0.045776 | -0.13275 | -0.70496 | -0.13733 | -0.14648 | 0.11444 | 50.0015 | 50.1434 | 122.1085 | 122.6486 | 0.045776 | 122.6669 | 67.749 | -0.13733 | 122.6486 | 0.045776 | 67.749 | 122.1085 | 122.6669 | -122.8821 | -122.9507
582.3281 | 123.1613 | -60.672 | 62.1643 | -0.12619 | 0.016233 | 0.0099612 | 0.0055244 | 0.058189 | -0.0038473 | 0.071386 | -60.585 | 61.9904 | -60.7224 | -60.7727 | 61.4639 | 7.2464 | -10.4599 | -10.318 | 62.0132 | -60.8093 | -0.050354 | -0.17395 | 0.086975 | -0.10071 | -0.70038 | -0.13733 | -0.15106 | 0.13733 | 50.2121 | 50.354 | 122.1359 | 122.6624 | 0.086975 | 122.6852 | 67.9184 | -0.13733 | 122.6624 | 0.086975 | 67.9184 | 122.1359 | 122.6852 | -122.8867 | -122.9736
583.3281 | 123.143 | -60.6491 | 62.146 | -0.16434 | 0.01837 | 0.012097 | 0.0065924 | 0.060325 | -0.0057699 | 0.0716 | -60.5988 | 62.0132 | -60.7498 | -60.7864 | 61.4319 | 7.2876 | -10.405 | -10.1807 | 62.0224 | -60.7727 | -0.10071 | -0.13275 | 0.050354 | -0.13733 | -0.71411 | -0.1236 | -0.1236 | 0.15106 | 50.2441 | 50.4684 | 122.081 | 122.6624 | 0.050354 | 122.6715 | 67.9367 | -0.1236 | 122.6624 | 0.050354 | 67.9367 | 122.081 | 122.6715 | -122.8958 | -122.9187
584.3281 | 123.1201 | -60.6674 | 62.1323 | -0.13382 | 0.015592 | 0.010602 | 0.007447 | 0.056266 | -0.0038473 | 0.069677 | -60.5942 | 62.027 | -60.7315 | -60.7956 | 61.4548 | 7.3746 | -10.318 | -10.0891 | 62.027 | -60.8231 | -0.064087 | -0.10529 | 0.073242 | -0.12817 | -0.67749 | -0.15564 | -0.10529 | 0.13733 | 50.3494 | 50.5783 | 122.1222 | 122.6944 | 0.073242 | 122.6944 | 68.042 | -0.15564 | 122.6944 | 0.073242 | 68.042 | 122.1222 | 122.6944 | -122.8638 | -122.9553
585.3281 | 123.2758 | -60.6079 | 62.146 | -0.088043 | 0.016447 | 0.012525 | 0.0044562 | 0.059471 | -0.0029929 | 0.069464 | -60.5988 | 61.9858 | -60.7269 | -60.7864 | 61.441 | 7.4432 | -10.2493 | -9.9426 | 62.0224 | -60.791 | -0.11902 | -0.16022 | 0.009155 | -0.17853 | -0.70496 | -0.18311 | -0.1236 | 0.12817 | 50.3586 | 50.6653 | 122.0489 | 122.5937 | 0.009155 | 122.6303 | 68.0511 | -0.18311 | 122.5937 | 0.009155 | 68.0511 | 122.0489 | 122.6303 | -122.8729 | -122.937
586.3281 | 123.1293 | -60.6354 | 62.1231 | -0.080414 | 0.017088 | 0.013379 | 0.0042426 | 0.059471 | -0.0029929 | 0.070959 | -60.5942 | 61.9904 | -60.7498 | -60.7727 | 61.4365 | 7.4707 | -10.199 | -9.9152 | 62.0316 | -60.7864 | -0.11444 | -0.13275 | 0.041199 | -0.13733 | -0.68665 | -0.15106 | -0.091553 | 0.15564 | 50.4364 | 50.7202 | 122.0718 | 122.6257 | 0.041199 | 122.6669 | 68.1061 | -0.15106 | 122.6257 | 0.041199 | 68.1061 | 122.0718 | 122.6669 | -122.8729 | -122.9095
587.3281 | 123.1384 | -60.6537 | 62.114 | -0.13382 | 0.015165 | 0.013379 | 0.0046698 | 0.059257 | -0.0072653 | 0.071814 | -60.5942 | 61.9949 | -60.7636 | -60.8002 | 61.4227 | 7.4982 | -10.0937 | -9.7412 | 62.0316 | -60.791 | -0.10986 | -0.11902 | 0.05951 | -0.14648 | -0.69122 | -0.13733 | -0.082398 | 0.16937 | 50.56 | 50.9125 | 122.0764 | 122.6486 | 0.05951 | 122.6852 | 68.1519 | -0.13733 | 122.6486 | 0.05951 | 68.1519 | 122.0764 | 122.6852 | -122.8775 | -122.905
588.3281 | 123.0652 | -60.6628 | 62.1735 | -0.21774 | 0.016874 | 0.012311 | 0.0053106 | 0.061607 | -0.0064109 | 0.070746 | -60.6125 | 62.0361 | -60.7544 | -60.8322 | 61.3632 | 7.4707 | -9.9884 | -9.7366 | 62.0636 | -60.8139 | -0.091553 | -0.13733 | 0.050354 | -0.16937 | -0.81024 | -0.15106 | -0.10986 | 0.14191 | 50.6744 | 50.9262 | 122.0261 | 122.699 | 0.050354 | 122.7264 | 68.1335 | -0.15106 | 122.699 | 0.050354 | 68.1335 | 122.0261 | 122.7264 | -122.9279 | -122.9874
589.3281 | 123.0881 | -60.6766 | 62.146 | -0.20248 | 0.018156 | 0.011029 | 0.0044562 | 0.059043 | -0.0040609 | 0.071814 | -60.5988 | 62.027 | -60.7498 | -60.8551 | 61.377 | 7.5165 | -9.8831 | -9.5856 | 62.0728 | -60.8185 | -0.073242 | -0.11902 | 0.07782 | -0.17853 | -0.76904 | -0.14191 | -0.073242 | 0.15106 | 50.7935 | 51.091 | 122.0535 | 122.7036 | 0.07782 | 122.7493 | 68.1931 | -0.14191 | 122.7036 | 0.07782 | 68.1931 | 122.0535 | 122.7493 | -122.8958 | -122.9645
590.3281 | 123.0698 | -60.6812 | 62.1552 | -0.20248 | 0.017301 | 0.011457 | 0.0059516 | 0.060752 | -0.0055563 | 0.070532 | -60.6171 | 62.0224 | -60.7681 | -60.8414 | 61.3632 | 7.489 | -9.8602 | -9.494 | 62.0453 | -60.8139 | -0.086975 | -0.13275 | 0.064087 | -0.16022 | -0.79193 | -0.13275 | -0.10986 | 0.15106 | 50.8209 | 51.1871 | 122.0444 | 122.7036 | 0.064087 | 122.7264 | 68.1702 | -0.13275 | 122.7036 | 0.064087 | 68.1702 | 122.0444 | 122.7264 | -122.9233 | -122.9691
591.3281 | 123.0881 | -60.6766 | 62.1597 | -0.19485 | 0.017301 | 0.012311 | 0.005097 | 0.061393 | -0.0029929 | 0.069891 | -60.6216 | 62.027 | -60.7544 | -60.8414 | 61.3678 | 7.5119 | -9.7687 | -9.3567 | 62.0499 | -60.8002 | -0.07782 | -0.13275 | 0.054932 | -0.16479 | -0.79193 | -0.1236 | -0.10986 | 0.13275 | 50.9079 | 51.3199 | 122.0444 | 122.7036 | 0.054932 | 122.7264 | 68.1885 | -0.1236 | 122.7036 | 0.054932 | 68.1885 | 122.0444 | 122.7264 | -122.9141 | -122.9599
592.3281 | 123.1293 | -60.6491 | 62.1368 | -0.439 | 0.017088 | 0.011457 | 0.004029 | 0.059471 | -0.0049155 | 0.070959 | -60.5804 | 61.9949 | -60.7544 | -60.8093 | 61.3998 | 7.5668 | -9.7824 | -9.1873 | 62.027 | -60.7864 | -0.10529 | -0.14191 | 0.068665 | -0.16022 | -0.737 | -0.13733 | -0.10986 | 0.17395 | 50.8667 | 51.4618 | 122.049 | 122.644 | 0.068665 | 122.6761 | 68.2159 | -0.13733 | 122.644 | 0.068665 | 68.2159 | 122.049 | 122.6761 | -122.8912 | -122.9233
593.3281 | 123.0881 | -60.6537 | 62.1506 | -0.1796 | 0.016874 | 0.010388 | 0.0070196 | 0.059684 | -0.0061973 | 0.069677 | -60.6171 | 62.0178 | -60.7773 | -60.8231 | 61.3632 | 7.5256 | -9.6359 | -9.1095 | 62.059 | -60.8322 | -0.1236 | -0.13275 | 0.036622 | -0.16937 | -0.78735 | -0.17853 | -0.091553 | 0.16022 | 51.0178 | 51.5442 | 122.0169 | 122.6715 | 0.036622 | 122.7127 | 68.1793 | -0.17853 | 122.6715 | 0.036622 | 68.1793 | 122.0169 | 122.7127 | -122.9279 | -122.9828
594.3281 | 123.0972 | -60.6995 | 62.1506 | -0.15671 | 0.014952 | 0.012097 | 0.0063788 | 0.06182 | -0.0042747 | 0.068609 | -60.6079 | 62.0178 | -60.7452 | -60.8368 | 61.3586 | 7.5348 | -9.5444 | -9.0088 | 62.0407 | -60.8093 | -0.045776 | -0.13275 | 0.091553 | -0.13733 | -0.79193 | -0.10986 | -0.10986 | 0.13733 | 51.1551 | 51.6907 | 122.0581 | 122.7173 | 0.091553 | 122.7402 | 68.2343 | -0.10986 | 122.7173 | 0.091553 | 68.2343 | 122.0581 | 122.7402 | -122.8958 | -122.9599
595.3281 | 123.0057 | -60.7178 | 62.1689 | -0.1796 | 0.018583 | 0.012525 | 0.0053106 | 0.059684 | -0.0044883 | 0.070746 | -60.6674 | 62.0636 | -60.791 | -60.9146 | 61.29 | 7.5394 | -9.3292 | -8.9493 | 62.0773 | -60.8322 | -0.073243 | -0.10528 | 0.050354 | -0.19684 | -0.87891 | -0.11444 | -0.091552 | 0.1236 | 51.3885 | 51.7685 | 122.0078 | 122.7814 | 0.050354 | 122.7951 | 68.2571 | -0.11444 | 122.7814 | 0.050354 | 68.2571 | 122.0078 | 122.7951 | -122.9599 | -123.0011
596.3281 | 123.0331 | -60.704 | 62.1552 | -0.20248 | 0.017729 | 0.010602 | 0.0063788 | 0.060752 | -0.0034201 | 0.070746 | -60.6537 | 62.0544 | -60.7956 | -60.9009 | 61.2946 | 7.5439 | -9.2697 | -8.8303 | 62.059 | -60.8688 | -0.091552 | -0.10071 | 0.050354 | -0.19684 | -0.86059 | -0.16479 | -0.09613 | 0.14191 | 51.4343 | 51.8738 | 121.9986 | 122.7585 | 0.050354 | 122.7631 | 68.248 | -0.16479 | 122.7585 | 0.050354 | 68.248 | 121.9986 | 122.7631 | -122.9507 | -123.024
597.3281 | 123.0286 | -60.6995 | 62.1597 | -0.24826 | 0.01602 | 0.012738 | 0.0055244 | 0.061393 | -0.0025657 | 0.071814 | -60.6537 | 62.0453 | -60.759 | -60.9009 | 61.2717 | 7.5485 | -9.1507 | -8.7296 | 62.0316 | -60.8597 | -0.059509 | -0.11444 | 0.045776 | -0.20142 | -0.88806 | -0.16022 | -0.12817 | 0.10529 | 51.5488 | 51.9699 | 121.9711 | 122.7448 | 0.045776 | 122.731 | 68.248 | -0.16022 | 122.7448 | 0.045776 | 68.248 | 121.9711 | 122.731 | -122.9187 | -123.0194
598.3281 | 123.0469 | -60.7132 | 62.1643 | -0.18723 | 0.017942 | 0.011243 | 0.0065924 | 0.05883 | -0.0047019 | 0.072668 | -60.6308 | 62.0453 | -60.7864 | -60.8826 | 61.29 | 7.2144 | -9.4208 | -8.7433 | 62.0407 | -60.8414 | -0.073242 | -0.11902 | 0.082398 | -0.16937 | -0.87433 | -0.12817 | -0.1236 | 0.15564 | 51.2924 | 51.9699 | 122.0032 | 122.7585 | 0.082398 | 122.7539 | 67.9276 | -0.12817 | 122.7585 | 0.082398 | 67.9276 | 122.0032 | 122.7539 | -122.9507 | -123.0057
599.3281 | 123.1384 | -60.6491 | 62.1323 | -0.16434 | 0.016233 | 0.012525 | 0.0036018 | 0.060539 | -0.0047019 | 0.072027 | -60.5988 | 62.0178 | -60.7544 | -60.8139 | 61.3678 | 7.2235 | -9.5352 | -8.5464 | 62.0499 | -60.8139 | -0.10529 | -0.11444 | 0.050354 | -0.16479 | -0.76447 | -0.16479 | -0.082397 | 0.15564 | 51.1139 | 52.1027 | 122.0169 | 122.6669 | 0.050354 | 122.699 | 67.8726 | -0.16479 | 122.6669 | 0.050354 | 67.8726 | 122.0169 | 122.699 | -122.8867 | -122.9462
600.3281 | 123.0469 | -60.6628 | 62.146 | -0.18723 | 0.018583 | 0.010816 | 0.0055244 | 0.059257 | -0.0036337 | 0.070318 | -60.6033 | 62.0132 | -60.7681 | -60.8643 | 61.3266 | 7.132 | -9.407 | -8.5052 | 62.0682 | -60.8322 | -0.10529 | -0.13275 | 0.059509 | -0.20142 | -0.8194 | -0.16937 | -0.07782 | 0.16479 | 51.2558 | 52.1576 | 121.9894 | 122.6761 | 0.059509 | 122.731 | 67.7948 | -0.16937 | 122.6761 | 0.059509 | 67.7948 | 121.9894 | 122.731 | -122.9141 | -122.9782
601.3281 | 123.0927 | -60.672 | 62.1597 | -0.21011 | 0.016447 | 0.01402 | 0.007447 | 0.063102 | -0.0044883 | 0.068609 | -60.6125 | 62.0499 | -60.7727 | -60.8505 | 61.3037 | 7.1091 | -9.4391 | -8.4183 | 62.0316 | -60.8231 | -0.10071 | -0.10986 | 0.059509 | -0.17853 | -0.85602 | -0.15106 | -0.12817 | 0.16022 | 51.2329 | 52.2537 | 121.9757 | 122.7219 | 0.059509 | 122.7036 | 67.7811 | -0.15106 | 122.7219 | 0.059509 | 67.7811 | 121.9757 | 122.7036 | -122.9324 | -122.9828
602.3281 | 122.9828 | -60.7407 | 62.1552 | -0.233 | 0.017515 | 0.015943 | 0.0080878 | 0.059471 | -0.0034201 | 0.068609 | -60.672 | 62.0682 | -60.7819 | -60.9055 | 61.4914 | 7.1365 | -9.6863 | -8.5236 | 62.0773 | -60.8505 | -0.041198 | -0.086975 | 0.068665 | -0.16479 | -0.66376 | -0.10986 | -0.077819 | 0.10986 | 51.0544 | 52.2171 | 122.2321 | 122.8088 | 0.068665 | 122.818 | 67.8772 | -0.10986 | 122.8088 | 0.068665 | 67.8772 | 122.2321 | 122.818 | -122.937 | -123.0057
603.3281 | 122.9187 | -60.6995 | 62.178 | -0.14145 | 0.01837 | 0.0076114 | 0.006806 | 0.059898 | -0.0057699 | 0.069037 | -60.6674 | 62.0544 | -60.7819 | -60.91 | 61.2396 | 6.9489 | -9.4208 | -8.2397 | 62.114 | -60.8276 | -0.082397 | -0.1236 | 0.032044 | -0.21057 | -0.93842 | -0.12817 | -0.064087 | 0.11444 | 51.2787 | 52.4597 | 121.9391 | 122.7539 | 0.032044 | 122.8134 | 67.6483 | -0.12817 | 122.7539 | 0.032044 | 67.6483 | 121.9391 | 122.8134 | -122.9599 | -123.0057
604.3281 | 123.0148 | -60.704 | 62.1964 | -0.21011 | 0.017942 | 0.010175 | 0.0053106 | 0.058616 | -0.0042747 | 0.071814 | -60.6583 | 62.0819 | -60.7773 | -60.91 | 61.2579 | 6.8893 | -9.3658 | -8.4961 | 62.059 | -60.8597 | -0.073242 | -0.11444 | 0.045777 | -0.20599 | -0.93841 | -0.15564 | -0.13733 | 0.11902 | 51.3382 | 52.2079 | 121.962 | 122.7859 | 0.045777 | 122.7631 | 67.5934 | -0.15564 | 122.7859 | 0.045777 | 67.5934 | 121.962 | 122.7631 | -122.9736 | -123.056
605.3281 | 123.0469 | -60.7224 | 62.1597 | -0.20248 | 0.016233 | 0.0088932 | 0.005738 | 0.060111 | -0.0027793 | 0.073523 | -60.64 | 62.1002 | -60.7727 | -60.8917 | 61.2534 | 6.8527 | -9.3384 | -8.4961 | 62.0819 | -60.8414 | -0.050354 | -0.059509 | 0.082397 | -0.16937 | -0.90637 | -0.11902 | -0.07782 | 0.13275 | 51.384 | 52.2263 | 121.9757 | 122.8226 | 0.082397 | 122.8043 | 67.5751 | -0.11902 | 122.8226 | 0.082397 | 67.5751 | 121.9757 | 122.8043 | -122.9324 | -123.0011
606.3281 | 123.1338 | -60.6583 | 62.1552 | -0.21011 | 0.016233 | 0.011457 | 0.0036018 | 0.059257 | -0.0034201 | 0.072241 | -60.5804 | 62.0499 | -60.7544 | -60.8093 | 61.322 | 6.7245 | -9.6771 | -8.9584 | 62.0361 | -60.8368 | -0.096131 | -0.10528 | 0.07782 | -0.15106 | -0.83313 | -0.17853 | -0.11902 | 0.17395 | 50.9811 | 51.6998 | 121.9803 | 122.7081 | 0.07782 | 122.6944 | 67.3828 | -0.17853 | 122.7081 | 0.07782 | 67.3828 | 121.9803 | 122.6944 | -122.9095 | -122.9919
607.3281 | 123.111 | -60.64 | 62.1414 | -0.13382 | 0.018156 | 0.013593 | 0.0048834 | 0.060539 | -0.0044883 | 0.071173 | -60.5713 | 62.0407 | -60.7361 | -60.791 | 61.3358 | 6.5689 | -9.8282 | -9.1736 | 62.0544 | -60.8047 | -0.09613 | -0.10071 | 0.068665 | -0.15106 | -0.80566 | -0.16479 | -0.086975 | 0.16479 | 50.8118 | 51.4664 | 121.9757 | 122.6807 | 0.068665 | 122.6944 | 67.2089 | -0.16479 | 122.6807 | 0.068665 | 67.2089 | 121.9757 | 122.6944 | -122.8775 | -122.9462
608.3281 | 123.0331 | -60.6583 | 62.2009 | -0.21011 | 0.018156 | 0.011243 | 0.0036018 | 0.063743 | -0.0034201 | 0.073309 | -60.6033 | 62.0636 | -60.7452 | -60.8505 | 61.2671 | 6.427 | -9.8053 | -9.4299 | 62.114 | -60.8185 | -0.086975 | -0.13733 | 0.054931 | -0.19226 | -0.93384 | -0.16022 | -0.086975 | 0.14191 | 50.853 | 51.2283 | 121.9254 | 122.7219 | 0.054931 | 122.7722 | 67.0853 | -0.16022 | 122.7219 | 0.054931 | 67.0853 | 121.9254 | 122.7722 | -122.9462 | -123.0194
609.3281 | 122.9965 | -60.672 | 62.2055 | -1.5376 | 0.019865 | 0.012952 | 0.0076606 | 0.062034 | -0.0036337 | 0.070959 | -60.8368 | 62.1231 | -60.7636 | -60.9192 | 61.2213 | 6.308 | -9.8969 | -9.613 | 62.0956 | -60.8414 | -0.091553 | -0.082397 | -0.1648 | -0.24719 | -0.98419 | -0.16937 | -0.10986 | -0.073242 | 50.7751 | 51.059 | 121.8933 | 122.7951 | -0.1648 | 122.7676 | 66.98 | -0.16937 | 122.7951 | -0.1648 | 66.98 | 121.8933 | 122.7676 | -122.9691 | -123.0469
610.3281 | 123.0469 | -60.6766 | 62.2101 | -0.21774 | 0.01837 | 0.007825 | 0.0072332 | 0.059257 | -0.0034201 | 0.072027 | -60.466 | 62.1826 | -60.7269 | -60.8826 | 61.2625 | 6.189 | -10.025 | -9.7046 | 62.1002 | -60.8597 | -0.050354 | -0.027466 | 0.21057 | -0.20599 | -0.94757 | -0.1831 | -0.10986 | 0.26093 | 50.6516 | 50.972 | 121.9391 | 122.8592 | 0.21057 | 122.7768 | 66.8655 | -0.1831 | 122.8592 | 0.21057 | 66.8655 | 121.9391 | 122.7768 | -122.937 | -123.0698
611.3281 | 122.9965 | -60.6537 | 62.2238 | -0.15671 | 0.017088 | 0.010602 | 0.0055244 | 0.063957 | -0.0017111 | 0.071386 | -60.6491 | 62.1323 | -60.759 | -60.8459 | 61.2167 | 6.0333 | -10.2127 | -9.7549 | 62.1368 | -60.8185 | -0.10529 | -0.091553 | 0.004578 | -0.19226 | -1.0071 | -0.16479 | -0.086975 | 0.10986 | 50.441 | 50.8987 | 121.8704 | 122.7859 | 0.004578 | 122.7905 | 66.687 | -0.16479 | 122.7859 | 0.004578 | 66.687 | 121.8704 | 122.7905 | -122.9828 | -123.0423
612.3281 | 123.0286 | -60.6628 | 62.2101 | -0.19485 | 0.01837 | 0.0080386 | 0.0044562 | 0.062889 | -0.0051291 | 0.070959 | -60.6262 | 62.114 | -60.7498 | -60.9467 | 61.0153 | 5.8823 | -10.405 | -9.906 | 62.114 | -60.8185 | -0.086975 | -0.09613 | 0.036621 | -0.28381 | -1.1948 | -0.15564 | -0.09613 | 0.1236 | 50.2579 | 50.7568 | 121.6782 | 122.7768 | 0.036621 | 122.7768 | 66.5451 | -0.15564 | 122.7768 | 0.036621 | 66.5451 | 121.6782 | 122.7768 | -122.9599 | -123.0286
613.3281 | 123.0743 | -60.6445 | 62.2009 | -0.20248 | 0.018583 | 0.010175 | 0.0038154 | 0.06118 | -0.0017111 | 0.072241 | -60.5576 | 62.0728 | -60.7224 | -60.8185 | 61.2854 | 5.9647 | -10.7941 | -9.8969 | 62.0773 | -60.8093 | -0.07782 | -0.12817 | 0.086975 | -0.17395 | -0.91553 | -0.16479 | -0.1236 | 0.1648 | 49.8505 | 50.7477 | 121.9299 | 122.7173 | 0.086975 | 122.7219 | 66.6092 | -0.16479 | 122.7173 | 0.086975 | 66.6092 | 121.9299 | 122.7219 | -122.9233 | -123.0103
614.3281 | 123.0469 | -60.6262 | 62.233 | -0.095673 | 0.018797 | 0.013806 | 0.0044562 | 0.060966 | -0.0023519 | 0.069464 | -60.5804 | 62.1277 | -60.7224 | -60.8688 | 61.2305 | 5.809 | -10.8719 | -10.0845 | 62.1597 | -60.791 | -0.09613 | -0.10529 | 0.045777 | -0.24261 | -1.0025 | -0.16479 | -0.073242 | 0.14191 | 49.7543 | 50.5417 | 121.8567 | 122.7539 | 0.045777 | 122.7859 | 66.4352 | -0.16479 | 122.7539 | 0.045777 | 66.4352 | 121.8567 | 122.7859 | -122.9553 | -123.024
615.3281 | 122.9965 | -60.6537 | 62.2513 | -0.22537 | 0.018583 | 0.012097 | 0.0044562 | 0.060966 | -0.0027793 | 0.073523 | -60.6079 | 62.1185 | -60.7269 | -60.8368 | 61.2167 | 5.6946 | -11.0001 | -10.1624 | 62.1506 | -60.7864 | -0.073242 | -0.13275 | 0.045777 | -0.18311 | -1.0345 | -0.13275 | -0.10071 | 0.11902 | 49.6536 | 50.4913 | 121.8704 | 122.7722 | 0.045777 | 122.8043 | 66.3483 | -0.13275 | 122.7722 | 0.045777 | 66.3483 | 121.8704 | 122.8043 | -122.9782 | -123.0377
616.3281 | 123.0331 | -60.6537 | 62.2375 | -0.21011 | 0.017515 | 0.012097 | 0.0072332 | 0.062461 | -0.0040609 | 0.071814 | -60.6216 | 62.1643 | -60.7544 | -60.878 | 61.1847 | 5.5664 | -11.1191 | -10.2768 | 62.1368 | -60.8002 | -0.10071 | -0.073242 | 0.032044 | -0.2243 | -1.0529 | -0.14648 | -0.10071 | 0.13275 | 49.5346 | 50.3769 | 121.8384 | 122.818 | 0.032044 | 122.7905 | 66.2201 | -0.14648 | 122.818 | 0.032044 | 66.2201 | 121.8384 | 122.7905 | -122.9919 | -123.0377
617.3281 | 123.0194 | -60.64 | 62.2421 | -0.19485 | 0.018797 | 0.011029 | 0.0076606 | 0.062248 | -0.0014975 | 0.072882 | -60.5942 | 62.1597 | -60.7452 | -60.878 | 61.203 | 5.5206 | -11.2793 | -10.4233 | 62.1597 | -60.8002 | -0.10528 | -0.082397 | 0.045777 | -0.23804 | -1.0391 | -0.16022 | -0.082397 | 0.15106 | 49.3607 | 50.2167 | 121.843 | 122.7997 | 0.045777 | 122.7997 | 66.1606 | -0.16022 | 122.7997 | 0.045777 | 66.1606 | 121.843 | 122.7997 | -122.9874 | -123.0423
618.3281 | 123.0148 | -60.6537 | 62.2513 | 1.2013 | 0.018156 | 0.012097 | 0.0031744 | 0.062248 | -0.0036337 | 0.072668 | -60.585 | 62.1506 | -60.7452 | -60.8597 | 61.2076 | 5.397 | -11.38 | -10.5423 | 62.1323 | -60.8276 | -0.091552 | -0.10071 | 0.068665 | -0.20599 | -1.0437 | -0.17395 | -0.11902 | 0.16022 | 49.2737 | 50.1114 | 121.8613 | 122.8043 | 0.068665 | 122.7859 | 66.0507 | -0.17395 | 122.8043 | 0.068665 | 66.0507 | 121.8613 | 122.7859 | -122.9965 | -123.0789
619.3281 | 123.0057 | -60.6445 | 62.2375 | -0.15671 | 0.017729 | 0.0086796 | 0.003388 | 0.060752 | -0.0021383 | 0.073523 | -60.379 | 62.1964 | -60.6766 | -60.8276 | 61.2305 | 5.0079 | -11.4258 | -10.5881 | 62.1368 | -60.8139 | -0.032044 | -0.041199 | 0.2655 | -0.18311 | -1.0071 | -0.16937 | -0.10071 | 0.29755 | 49.2188 | 50.0565 | 121.875 | 122.8409 | 0.2655 | 122.7814 | 65.6525 | -0.16937 | 122.8409 | 0.2655 | 65.6525 | 121.875 | 122.7814 | -122.9141 | -123.0515
620.3281 | 123.0652 | -60.6171 | 62.2055 | -0.18723 | 0.019224 | 0.011884 | 0.0031744 | 0.06118 | -0.0034201 | 0.072455 | -60.5347 | 62.1094 | -60.6995 | -60.7819 | 61.2625 | 4.7882 | -11.5906 | -10.6064 | 62.1094 | -60.7727 | -0.082398 | -0.09613 | 0.082397 | -0.1648 | -0.94299 | -0.15564 | -0.09613 | 0.16479 | 49.0265 | 50.0107 | 121.8796 | 122.7264 | 0.082397 | 122.7264 | 65.4053 | -0.15564 | 122.7264 | 0.082397 | 65.4053 | 121.8796 | 122.7264 | -122.905 | -122.9782
621.3281 | 123.0515 | -60.6216 | 62.2696 | -0.21774 | 0.019438 | 0.0093204 | 0.0055244 | 0.059471 | -0.0017111 | 0.071173 | -60.5988 | 62.1826 | -60.6949 | -60.8368 | 61.0336 | 4.4495 | -11.4075 | -11.0825 | 62.2101 | -60.7819 | -0.073242 | -0.086975 | 0.022888 | -0.21515 | -1.236 | -0.16022 | -0.059509 | 0.09613 | 49.2142 | 49.5392 | 121.6553 | 122.8043 | 0.022888 | 122.8317 | 65.0711 | -0.16022 | 122.8043 | 0.022888 | 65.0711 | 121.6553 | 122.8317 | -122.9645 | -123.0515
622.3281 | 123.0927 | -60.6171 | 62.2742 | -0.16434 | 0.016447 | 0.007825 | 0.0065924 | 0.059257 | -0.0019247 | 0.070959 | -60.5804 | 62.178 | -60.7224 | -60.8322 | 61.1618 | 4.8157 | -11.6867 | -10.7895 | 62.1735 | -60.7681 | -0.10529 | -0.09613 | 0.036621 | -0.21515 | -1.1124 | -0.15106 | -0.10071 | 0.14191 | 48.9304 | 49.8276 | 121.7789 | 122.7951 | 0.036621 | 122.7905 | 65.4327 | -0.15106 | 122.7951 | 0.036621 | 65.4327 | 121.7789 | 122.7905 | -122.9965 | -123.0423
623.3281 | 123.0286 | -60.6079 | 62.2284 | -0.13382 | 0.019865 | 0.010175 | 0.008515 | 0.062461 | -0.00064309 | 0.070746 | -60.5804 | 62.1964 | -60.6857 | -60.8505 | 61.1526 | 4.7424 | -11.8057 | -10.9085 | 62.1552 | -60.8139 | -0.07782 | -0.032044 | 0.027466 | -0.24262 | -1.0757 | -0.20599 | -0.073243 | 0.10529 | 48.8022 | 49.6994 | 121.7606 | 122.8043 | 0.027466 | 122.7631 | 65.3503 | -0.20599 | 122.8043 | 0.027466 | 65.3503 | 121.7606 | 122.7631 | -122.9141 | -123.0423
624.3281 | 123.0286 | -60.6125 | 62.2604 | -0.27878 | 0.018583 | 0.011884 | 0.0065924 | 0.060966 | -0.0032065 | 0.071173 | -60.6171 | 62.1918 | -60.7086 | -60.8414 | 61.1298 | 4.6463 | -11.9339 | -11.0275 | 62.1597 | -60.7956 | -0.09613 | -0.068665 | -0.004577 | -0.22888 | -1.1307 | -0.1831 | -0.10071 | 0.091553 | 48.6786 | 49.585 | 121.7422 | 122.8043 | -0.004577 | 122.7722 | 65.2588 | -0.1831 | 122.8043 | -0.004577 | 65.2588 | 121.7422 | 122.7722 | -122.9691 | -123.056
625.3281 | 123.0057 | -60.6262 | 62.2696 | -0.25589 | 0.01901 | 0.007825 | 0.0063788 | 0.06118 | -0.0027793 | 0.071386 | -60.6079 | 62.1826 | -60.7269 | -60.8505 | 61.1069 | 4.5685 | -12.0346 | -11.1099 | 62.1552 | -60.8002 | -0.10071 | -0.086975 | 0.018311 | -0.2243 | -1.1627 | -0.17395 | -0.11444 | 0.11902 | 48.5916 | 49.5163 | 121.7331 | 122.8088 | 0.018311 | 122.7814 | 65.1947 | -0.17395 | 122.8088 | 0.018311 | 65.1947 | 121.7331 | 122.7814 | -122.9965 | -123.0698
626.3281 | 123.024 | -60.6171 | 62.2696 | 0.83511 | 0.019224 | 0.013806 | 0.0053106 | 0.06118 | -0.0038473 | 0.0716 | -60.5301 | 62.1872 | -60.7086 | -60.8231 | 61.0977 | 4.422 | -12.1582 | -11.2747 | 62.1872 | -60.7864 | -0.091553 | -0.082397 | 0.086975 | -0.20599 | -1.1719 | -0.16937 | -0.082397 | 0.17853 | 48.4589 | 49.3423 | 121.7148 | 122.8043 | 0.086975 | 122.8043 | 65.0391 | -0.16937 | 122.8043 | 0.086975 | 65.0391 | 121.7148 | 122.8043 | -122.9782 | -123.056
627.3281 | 123.024 | -60.5988 | 62.2696 | -0.19485 | 0.021787 | 0.010816 | 0.003388 | 0.062461 | -0.0025657 | 0.070318 | -60.5209 | 62.1597 | -60.6674 | -60.8047 | 61.1298 | 4.3213 | -12.3505 | -11.3342 | 62.1735 | -60.759 | -0.068664 | -0.10986 | 0.07782 | -0.20599 | -1.1398 | -0.16022 | -0.09613 | 0.14648 | 48.2483 | 49.2645 | 121.7285 | 122.7585 | 0.07782 | 122.7722 | 64.92 | -0.16022 | 122.7585 | 0.07782 | 64.92 | 121.7285 | 122.7722 | -122.937 | -123.0286
628.3281 | 123.0698 | -60.5896 | 62.2696 | -0.18723 | 0.019438 | 0.011457 | 0.0042426 | 0.061393 | -0.0044883 | 0.070746 | -60.5164 | 62.1368 | -60.6857 | -60.7819 | 61.1343 | 4.1885 | -12.4878 | -11.467 | 62.1826 | -60.6995 | -0.09613 | -0.13275 | 0.073243 | -0.19226 | -1.1353 | -0.10986 | -0.086975 | 0.16937 | 48.1018 | 49.1226 | 121.7239 | 122.7264 | 0.073243 | 122.7722 | 64.7781 | -0.10986 | 122.7264 | 0.073243 | 64.7781 | 121.7239 | 122.7722 | -122.9553 | -122.9691
629.3281 | 122.9828 | -60.6079 | 62.3154 | -0.17197 | 0.01901 | 0.011029 | 0.008515 | 0.061607 | -0.0025657 | 0.069891 | -60.5438 | 62.2009 | -60.672 | -60.8231 | 61.0107 | 3.9093 | -12.5748 | -11.7004 | 62.1872 | -60.7773 | -0.064087 | -0.11444 | 0.064087 | -0.21515 | -1.3046 | -0.16937 | -0.12817 | 0.12817 | 48.0331 | 48.9075 | 121.6187 | 122.8088 | 0.064087 | 122.7951 | 64.5172 | -0.16937 | 122.8088 | 0.064087 | 64.5172 | 121.6187 | 122.7951 | -122.9874 | -123.0927
630.3281 | 123.0331 | -60.5896 | 62.2925 | -0.11093 | 0.019865 | 0.01402 | 0.0072332 | 0.061393 | -0.0042747 | 0.072027 | -60.5301 | 62.2467 | -60.6903 | -60.8231 | 61.0794 | 3.804 | -12.7487 | -11.792 | 62.2147 | -60.7498 | -0.10071 | -0.045776 | 0.05951 | -0.23346 | -1.2131 | -0.16022 | -0.077819 | 0.16022 | 47.8409 | 48.7976 | 121.669 | 122.8363 | 0.05951 | 122.8043 | 64.3936 | -0.16022 | 122.8363 | 0.05951 | 64.3936 | 121.669 | 122.8043 | -122.9828 | -123.0423
631.3281 | 123.0469 | -60.5942 | 62.2971 | -0.17197 | 0.019438 | 0.0099612 | 0.008515 | 0.061607 | -0.0057699 | 0.073095 | -60.5392 | 62.2192 | -60.6903 | -60.8002 | 61.0428 | 3.6621 | -12.8906 | -11.9751 | 62.2147 | -60.7498 | -0.096131 | -0.07782 | 0.054931 | -0.20599 | -1.2543 | -0.15564 | -0.082397 | 0.15106 | 47.7036 | 48.6191 | 121.637 | 122.8134 | 0.054931 | 122.8088 | 64.2563 | -0.15564 | 122.8134 | 0.054931 | 64.2563 | 121.637 | 122.8088 | -122.9874 | -123.0469
632.3281 | 123.0377 | -60.585 | 62.2925 | -0.11856 | 0.019865 | 0.012738 | 0.0070196 | 0.063316 | -0.0038473 | 0.0716 | -60.5301 | 62.2375 | -60.6583 | -60.8093 | 61.0519 | 3.4973 | -13.0646 | -12.1765 | 62.2192 | -60.7452 | -0.073242 | -0.054931 | 0.054932 | -0.2243 | -1.2405 | -0.16022 | -0.073242 | 0.12817 | 47.5204 | 48.4085 | 121.637 | 122.8226 | 0.054932 | 122.8043 | 64.0823 | -0.16022 | 122.8226 | 0.054932 | 64.0823 | 121.637 | 122.8043 | -122.9507 | -123.0377
633.3281 | 123.0286 | -60.5942 | 62.2925 | -0.17197 | 0.019438 | 0.009534 | 0.0031744 | 0.059471 | -0.0057699 | 0.072027 | -60.5392 | 62.2421 | -60.6766 | -60.8963 | 60.8322 | 3.241 | -13.1653 | -12.4191 | 62.2375 | -60.7727 | -0.082398 | -0.050354 | 0.054931 | -0.30212 | -1.4603 | -0.17853 | -0.054931 | 0.13733 | 47.4289 | 48.175 | 121.4264 | 122.8363 | 0.054931 | 122.8317 | 63.8351 | -0.17853 | 122.8363 | 0.054931 | 63.8351 | 121.4264 | 122.8317 | -122.9691 | -123.0652
634.3281 | 122.9874 | -60.5759 | 62.3154 | -0.13382 | 0.018583 | 0.011029 | 0.0044562 | 0.057762 | -0.0032065 | 0.074164 | -60.5255 | 62.2284 | -60.6628 | -60.9879 | 60.91 | 3.1586 | -13.4308 | -12.5565 | 62.2238 | -60.7498 | -0.086975 | -0.086975 | 0.050354 | -0.41199 | -1.4053 | -0.17395 | -0.091553 | 0.13733 | 47.1451 | 48.0194 | 121.4859 | 122.8043 | 0.050354 | 122.7997 | 63.7344 | -0.17395 | 122.8043 | 0.050354 | 63.7344 | 121.4859 | 122.7997 | -122.9782 | -123.0652
635.3281 | 123.0286 | -60.5438 | 62.2925 | -0.1796 | 0.021574 | 0.010175 | 0.007447 | 0.063316 | -0.0034201 | 0.07395 | -60.5026 | 62.2604 | -60.6491 | -60.791 | 61.0336 | 2.9617 | -13.5773 | -12.6846 | 62.2238 | -60.7269 | -0.10529 | -0.032043 | 0.041198 | -0.24719 | -1.2588 | -0.18311 | -0.068664 | 0.14648 | 46.9666 | 47.8592 | 121.5775 | 122.8043 | 0.041198 | 122.7676 | 63.5056 | -0.18311 | 122.8043 | 0.041198 | 63.5056 | 121.5775 | 122.7676 | -122.9416 | -123.0194
636.3281 | 123.0194 | -60.5713 | 62.3062 | -0.1033 | 0.019224 | 0.012525 | 0.0072332 | 0.062675 | -0.0036337 | 0.072027 | -60.498 | 62.265 | -60.6491 | -60.7681 | 61.0016 | 2.8336 | -13.7375 | -12.822 | 62.2559 | -60.7178 | -0.07782 | -0.041198 | 0.073242 | -0.19684 | -1.3046 | -0.14648 | -0.050354 | 0.15106 | 46.8338 | 47.7493 | 121.5729 | 122.8363 | 0.073242 | 122.8271 | 63.4048 | -0.14648 | 122.8363 | 0.073242 | 63.4048 | 121.5729 | 122.8271 | -122.9553 | -123.024
637.3281 | 123.024 | -60.5484 | 62.3337 | -0.14908 | 0.018583 | 0.013166 | 0.004029 | 0.062889 | -0.0042747 | 0.072455 | -60.5164 | 62.265 | -60.6491 | -60.791 | 60.997 | 2.6276 | -13.8519 | -12.9639 | 62.2604 | -60.7224 | -0.10071 | -0.068664 | 0.032044 | -0.24262 | -1.3367 | -0.17395 | -0.073242 | 0.13275 | 46.6965 | 47.5845 | 121.5454 | 122.8134 | 0.032044 | 122.8088 | 63.176 | -0.17395 | 122.8134 | 0.032044 | 63.176 | 121.5454 | 122.8088 | -122.9828 | -123.056
638.3281 | 123.0743 | -60.553 | 62.3245 | -0.12619 | 0.019224 | 0.01167 | 0.0065924 | 0.063957 | -0.0049155 | 0.072668 | -60.4523 | 62.2696 | -60.6125 | -60.7269 | 61.0199 | 2.4353 | -14.09 | -13.1012 | 62.2375 | -60.7361 | -0.059509 | -0.054932 | 0.10071 | -0.17395 | -1.3046 | -0.1831 | -0.086975 | 0.16022 | 46.463 | 47.4518 | 121.5729 | 122.8226 | 0.10071 | 122.7905 | 62.9883 | -0.1831 | 122.8226 | 0.10071 | 62.9883 | 121.5729 | 122.7905 | -122.937 | -123.0606
639.3281 | 123.0606 | -60.5438 | 62.3016 | -0.11093 | 0.018156 | 0.015302 | 0.0087286 | 0.063957 | -0.0042747 | 0.070746 | -60.4431 | 62.2787 | -60.6445 | -60.7086 | 61.0107 | 2.2385 | -14.2914 | -13.3026 | 62.2467 | -60.7132 | -0.10071 | -0.022888 | 0.10071 | -0.16479 | -1.2909 | -0.16937 | -0.054932 | 0.20142 | 46.2524 | 47.2412 | 121.5546 | 122.8226 | 0.10071 | 122.7905 | 62.7823 | -0.16937 | 122.8226 | 0.10071 | 62.7823 | 121.5546 | 122.7905 | -122.9462 | -123.0148
640.3281 | 123.0148 | -60.553 | 62.3291 | -0.13382 | 0.020078 | 0.0091068 | 0.0046698 | 0.062889 | -0.0051291 | 0.071386 | -60.4752 | 62.3154 | -60.6125 | -60.7636 | 60.9695 | 1.9867 | -14.4104 | -13.5178 | 62.2742 | -60.7224 | -0.059509 | -0.013733 | 0.07782 | -0.21057 | -1.3596 | -0.16937 | -0.054932 | 0.13733 | 46.1426 | 47.0352 | 121.5225 | 122.8683 | 0.07782 | 122.8271 | 62.5397 | -0.16937 | 122.8683 | 0.07782 | 62.5397 | 121.5225 | 122.8271 | -122.9416 | -123.0515
641.3281 | 123.024 | -60.5209 | 62.352 | -0.18723 | 0.021574 | 0.015302 | 0.0044562 | 0.063316 | -0.0019247 | 0.071386 | -60.466 | 62.3108 | -60.6216 | -60.759 | 60.9604 | 1.767 | -14.6484 | -13.7833 | 62.3108 | -60.6903 | -0.10071 | -0.041199 | 0.054932 | -0.23804 | -1.3916 | -0.16937 | -0.041199 | 0.15564 | 45.8725 | 46.7377 | 121.4813 | 122.8317 | 0.054932 | 122.8317 | 62.2879 | -0.16937 | 122.8317 | 0.054932 | 62.2879 | 121.4813 | 122.8317 | -122.9736 | -123.0423
642.3281 | 123.0835 | -60.5255 | 62.352 | -0.088043 | 0.019224 | 0.0099612 | 0.006806 | 0.062248 | -0.0044883 | 0.071386 | -60.4156 | 62.3154 | -60.6125 | -60.7086 | 60.9787 | 1.6251 | -14.8911 | -13.9618 | 62.265 | -60.7178 | -0.086975 | -0.036621 | 0.10986 | -0.18311 | -1.3733 | -0.19226 | -0.086975 | 0.19684 | 45.6345 | 46.5637 | 121.5042 | 122.8409 | 0.10986 | 122.7905 | 62.1506 | -0.19226 | 122.8409 | 0.10986 | 62.1506 | 121.5042 | 122.7905 | -122.9645 | -123.0698
643.3438 | 123.0927 | -60.5301 | 62.3291 | 0.2095 | 0.020292 | 0.011457 | 0.0038154 | 0.065879 | -0.0029929 | 0.072668 | -60.4614 | 62.2696 | -60.6125 | -60.759 | 60.9192 | 1.3962 | -15.1886 | -14.2456 | 62.2101 | -60.7086 | -0.082398 | -0.05951 | 0.068664 | -0.22888 | -1.4099 | -0.17853 | -0.11902 | 0.15106 | 45.3415 | 46.2845 | 121.4493 | 122.7997 | 0.068664 | 122.7402 | 61.9263 | -0.17853 | 122.7997 | 0.068664 | 61.9263 | 121.4493 | 122.7402 | -122.9416 | -123.0377
644.3281 | 123.0423 | -60.4889 | 62.3199 | -0.11093 | 0.02136 | 0.012525 | 0.007447 | 0.063743 | -0.0036337 | 0.071386 | -60.3699 | 62.3428 | -60.5988 | -60.6949 | 60.9467 | 1.236 | -15.3625 | -14.4745 | 62.2559 | -60.7132 | -0.10986 | 0.022888 | 0.11902 | -0.20599 | -1.3733 | -0.2243 | -0.064087 | 0.22888 | 45.1263 | 46.0144 | 121.4355 | 122.8317 | 0.11902 | 122.7448 | 61.7249 | -0.2243 | 122.8317 | 0.11902 | 61.7249 | 121.4355 | 122.7448 | -122.9187 | -123.0331
645.3281 | 123.0652 | -60.5072 | 62.352 | -0.28641 | 0.020933 | 0.014875 | 0.0072332 | 0.063529 | -0.0017111 | 0.069891 | -60.3653 | 62.3291 | -60.5804 | -60.6949 | 60.9512 | 1.0757 | -15.5594 | -14.6896 | 62.2833 | -60.6857 | -0.073242 | -0.022888 | 0.14191 | -0.18768 | -1.4008 | -0.17853 | -0.068665 | 0.21515 | 44.9478 | 45.8176 | 121.4584 | 122.8363 | 0.14191 | 122.7905 | 61.5829 | -0.17853 | 122.8363 | 0.14191 | 61.5829 | 121.4584 | 122.7905 | -122.9324 | -123.0377
646.3281 | 123.0606 | -60.498 | 62.3428 | -0.16434 | 0.021147 | 0.01167 | 0.0065924 | 0.064811 | -0.0034201 | 0.072027 | -60.3516 | 62.3383 | -60.5804 | -60.672 | 60.9283 | 0.83771 | -15.8112 | -14.9963 | 62.3154 | -60.6857 | -0.082397 | -0.004577 | 0.14648 | -0.17395 | -1.4145 | -0.18768 | -0.027465 | 0.22888 | 44.6869 | 45.5017 | 121.4264 | 122.8363 | 0.14648 | 122.8134 | 61.3358 | -0.18768 | 122.8363 | 0.14648 | 61.3358 | 121.4264 | 122.8134 | -122.9233 | -123.0286
647.3281 | 123.0377 | -60.4752 | 62.3886 | -0.13382 | 0.020719 | 0.014661 | 0.0046698 | 0.064811 | -0.00064309 | 0.072241 | -60.3836 | 62.3474 | -60.585 | -60.6674 | 60.91 | 0.60883 | -15.9988 | -15.271 | 62.3154 | -60.6628 | -0.10986 | -0.041199 | 0.091553 | -0.19226 | -1.4786 | -0.18768 | -0.073242 | 0.20142 | 44.4763 | 45.2042 | 121.3852 | 122.8226 | 0.091553 | 122.7905 | 61.084 | -0.18768 | 122.8226 | 0.091553 | 61.084 | 121.3852 | 122.7905 | -122.9736 | -123.0515
648.3438 | 123.0698 | -60.4706 | 62.3703 | 0.27054 | 0.017515 | 0.015515 | 0.0042426 | 0.065879 | -0.00064309 | 0.07395 | -60.4156 | 62.2971 | -60.6033 | -60.7269 | 60.8368 | 0.32959 | -16.3513 | -15.6647 | 62.3016 | -60.6491 | -0.13275 | -0.073242 | 0.054932 | -0.25635 | -1.5335 | -0.17853 | -0.068664 | 0.18768 | 44.1193 | 44.8059 | 121.3074 | 122.7676 | 0.054932 | 122.7722 | 60.8002 | -0.17853 | 122.7676 | 0.054932 | 60.8002 | 121.3074 | 122.7722 | -122.9736 | -123.0194
649.3281 | 123.0927 | -60.466 | 62.384 | 1.6896 | 0.01901 | 0.0097476 | 0.0055244 | 0.06417 | -0.0034201 | 0.071814 | -60.1913 | 62.352 | -60.5392 | -60.6445 | 60.9238 | 0.20599 | -16.5756 | -15.8295 | 62.3154 | -60.6583 | -0.073243 | -0.032043 | 0.27466 | -0.17853 | -1.4603 | -0.19226 | -0.068664 | 0.3479 | 43.8904 | 44.6365 | 121.3898 | 122.818 | 0.27466 | 122.7814 | 60.672 | -0.19226 | 122.818 | 0.27466 | 60.672 | 121.3898 | 122.7814 | -122.9233 | -123.0423
650.3281 | 123.0331 | -60.4752 | 62.4023 | 0.018768 | 0.020292 | 0.015943 | 0.008515 | 0.065879 | -0.0040609 | 0.072241 | -60.3424 | 62.3611 | -60.5484 | -60.6949 | 60.8322 | -0.036621 | -16.7953 | -16.1682 | 62.2879 | -60.6583 | -0.073242 | -0.041199 | 0.13275 | -0.21973 | -1.5701 | -0.18311 | -0.11444 | 0.20599 | 43.6798 | 44.3069 | 121.3074 | 122.8363 | 0.13275 | 122.7631 | 60.4385 | -0.18311 | 122.8363 | 0.13275 | 60.4385 | 121.3074 | 122.7631 | -122.9507 | -123.0606
651.3281 | 123.0194 | -60.4706 | 62.3932 | 0.011139 | 0.023283 | 0.012097 | 0.0076606 | 0.063743 | -0.0023519 | 0.069464 | -60.3424 | 62.384 | -60.5347 | -60.6628 | 60.8231 | -0.23804 | -17.0746 | -16.4703 | 62.3199 | -60.6445 | -0.064087 | -0.009155 | 0.12817 | -0.19226 | -1.5701 | -0.17395 | -0.073242 | 0.19226 | 43.396 | 44.0002 | 121.2936 | 122.8546 | 0.12817 | 122.7905 | 60.2325 | -0.17395 | 122.8546 | 0.12817 | 60.2325 | 121.2936 | 122.7905 | -122.9279 | -123.0377
652.3281 | 123.0652 | -60.4477 | 62.4252 | 0.011139 | 0.020506 | 0.016156 | 0.0059516 | 0.063743 | -0.0014975 | 0.072882 | -60.3241 | 62.384 | -60.5484 | -60.6308 | 60.8093 | -0.44861 | -17.3355 | -16.7313 | 62.3245 | -60.6674 | -0.10071 | -0.041199 | 0.1236 | -0.1831 | -1.6159 | -0.21973 | -0.10071 | 0.2243 | 43.1122 | 43.7164 | 121.257 | 122.8317 | 0.1236 | 122.7722 | 59.9991 | -0.21973 | 122.8317 | 0.1236 | 59.9991 | 121.257 | 122.7722 | -122.9736 | -123.0927
653.3438 | 123.1522 | -60.4156 | 62.3291 | 0.20187 | 0.016447 | 0.0086796 | 0.00061099 | 0.063102 | -0.0025657 | 0.076086 | -60.3333 | 62.2833 | -60.5438 | -60.6262 | 60.8505 | -0.64087 | -17.7841 | -17.0105 | 62.2925 | -60.6033 | -0.12817 | -0.045777 | 0.082397 | -0.21057 | -1.4786 | -0.18768 | -0.036622 | 0.21057 | 42.6315 | 43.4052 | 121.2662 | 122.699 | 0.082397 | 122.7081 | 59.7748 | -0.18768 | 122.699 | 0.082397 | 59.7748 | 121.2662 | 122.7081 | -122.8729 | -122.9324
654.3281 | 123.0606 | -60.4385 | 62.4207 | -0.034637 | 0.020506 | 0.010816 | 0.007447 | 0.064598 | -0.0019247 | 0.0716 | -60.2966 | 62.4023 | -60.5072 | -60.6033 | 60.8002 | -0.8606 | -17.8986 | -17.3264 | 62.3749 | -60.6079 | -0.068664 | -0.01831 | 0.14191 | -0.16479 | -1.6205 | -0.16937 | -0.045776 | 0.21057 | 42.54 | 43.1122 | 121.2387 | 122.8409 | 0.14191 | 122.8134 | 59.5779 | -0.16937 | 122.8409 | 0.14191 | 59.5779 | 121.2387 | 122.8134 | -122.9279 | -123.0286
655.3281 | 123.0606 | -60.4202 | 62.4481 | -0.072784 | 0.021147 | 0.014447 | 0.0070196 | 0.063102 | -0.00042929 | 0.070746 | -60.2966 | 62.4207 | -60.4889 | -60.585 | 60.8002 | -1.0712 | -18.1915 | -17.6468 | 62.3566 | -60.6125 | -0.068665 | -0.027466 | 0.1236 | -0.1648 | -1.6479 | -0.19226 | -0.091553 | 0.19226 | 42.2287 | 42.7734 | 121.2204 | 122.8409 | 0.1236 | 122.7768 | 59.3491 | -0.19226 | 122.8409 | 0.1236 | 59.3491 | 121.2204 | 122.7768 | -122.937 | -123.0606
656.3281 | 123.0698 | -60.4111 | 62.4481 | -0.14908 | 0.020933 | 0.012097 | 0.0083014 | 0.065238 | -0.0023519 | 0.072668 | -60.3058 | 62.4481 | -60.5026 | -60.5621 | 60.7636 | -1.2726 | -18.4662 | -17.9214 | 62.3978 | -60.6079 | -0.091553 | 0 | 0.10529 | -0.15106 | -1.6846 | -0.19684 | -0.050354 | 0.19684 | 41.9449 | 42.4896 | 121.1746 | 122.8592 | 0.10529 | 122.8088 | 59.1385 | -0.19684 | 122.8592 | 0.10529 | 59.1385 | 121.1746 | 122.8088 | -122.9507 | -123.056
657.3281 | 123.0423 | -60.3973 | 62.4344 | 0.011139 | 0.018797 | 0.015729 | 0.0072332 | 0.064384 | -0.0025657 | 0.072241 | -60.2921 | 62.4207 | -60.4889 | -60.5988 | 60.6995 | -1.4557 | -18.718 | -18.1961 | 62.384 | -60.6216 | -0.091553 | -0.013733 | 0.10529 | -0.20142 | -1.7349 | -0.2243 | -0.050354 | 0.19684 | 41.6794 | 42.2012 | 121.0968 | 122.818 | 0.10529 | 122.7814 | 58.9417 | -0.2243 | 122.818 | 0.10529 | 58.9417 | 121.0968 | 122.7814 | -122.9233 | -123.056
658.3438 | 123.0743 | -60.3882 | 62.4161 | 0.1561 | 0.017515 | 0.012525 | -0.0032342 | 0.063102 | -0.0034201 | 0.0716 | -60.3378 | 62.3245 | -60.4752 | -60.6262 | 60.704 | -1.6159 | -19.1025 | -18.4937 | 62.3657 | -60.5484 | -0.086975 | -0.091553 | 0.050354 | -0.23804 | -1.712 | -0.16022 | -0.050354 | 0.13733 | 41.2857 | 41.8945 | 121.0922 | 122.7127 | 0.050354 | 122.7539 | 58.7723 | -0.16022 | 122.7127 | 0.050354 | 58.7723 | 121.0922 | 122.7539 | -122.8912 | -122.9645
659.3281 | 123.0515 | -60.4019 | 62.4527 | -0.0041198 | 0.02136 | 0.015088 | 0.0076606 | 0.06182 | -0.0025657 | 0.070746 | -60.2554 | 62.4481 | -60.4431 | -60.5713 | 60.672 | -1.8036 | -19.313 | -18.7775 | 62.4023 | -60.5713 | -0.041198 | -0.004578 | 0.14648 | -0.16937 | -1.7807 | -0.16937 | -0.050354 | 0.18768 | 41.0889 | 41.6245 | 121.0739 | 122.85 | 0.14648 | 122.8043 | 58.5983 | -0.16937 | 122.85 | 0.14648 | 58.5983 | 121.0739 | 122.8043 | -122.8958 | -123.024
660.3281 | 123.056 | -60.3745 | 62.4527 | 0.056915 | 0.020506 | 0.011884 | 0.0083014 | 0.065452 | -0.0021383 | 0.072668 | -60.2463 | 62.4527 | -60.4752 | -60.5576 | 60.6674 | -1.918 | -19.5465 | -19.0155 | 62.4115 | -60.5759 | -0.10071 | 0 | 0.12817 | -0.1831 | -1.7853 | -0.20142 | -0.041199 | 0.22888 | 40.8279 | 41.3589 | 121.0419 | 122.8271 | 0.12817 | 122.7859 | 58.4564 | -0.20142 | 122.8271 | 0.12817 | 58.4564 | 121.0419 | 122.7859 | -122.9279 | -123.0286
661.3281 | 123.0743 | -60.3561 | 62.4802 | -0.14908 | 0.02136 | 0.015302 | 0.006806 | 0.063957 | -0.0042747 | 0.070746 | -60.2554 | 62.4939 | -60.4385 | -60.5347 | 60.6445 | -2.1103 | -19.7296 | -19.2352 | 62.4298 | -60.5576 | -0.082398 | 0.013732 | 0.10071 | -0.17853 | -1.8356 | -0.20142 | -0.050354 | 0.18311 | 40.6265 | 41.1209 | 121.0007 | 122.85 | 0.10071 | 122.786 | 58.2458 | -0.20142 | 122.85 | 0.10071 | 58.2458 | 121.0007 | 122.786 | -122.9187 | -123.0377
662.3281 | 123.0652 | -60.3516 | 62.4939 | -0.088043 | 0.020719 | 0.015515 | 0.0053106 | 0.066306 | -0.0014975 | 0.072882 | -60.2463 | 62.4619 | -60.4294 | -60.5438 | 60.6216 | -2.2522 | -19.9585 | -19.487 | 62.4252 | -60.5484 | -0.07782 | -0.032043 | 0.10529 | -0.19226 | -1.8723 | -0.19684 | -0.068664 | 0.1831 | 40.3931 | 40.8646 | 120.9732 | 122.8134 | 0.10529 | 122.7768 | 58.0994 | -0.19684 | 122.8134 | 0.10529 | 58.0994 | 120.9732 | 122.7768 | -122.9233 | -123.0423
663.3438 | 123.0103 | -60.3836 | 62.4619 | 0.22476 | 0.019224 | 0.017011 | 0.0055244 | 0.064811 | -0.0014975 | 0.072882 | -60.2783 | 62.4573 | -60.4614 | -60.6125 | 60.5255 | -2.4445 | -20.2744 | -19.7662 | 62.4298 | -60.5576 | -0.07782 | -0.004578 | 0.10529 | -0.22888 | -1.9363 | -0.17395 | -0.032043 | 0.18311 | 40.1093 | 40.6174 | 120.9091 | 122.8409 | 0.10529 | 122.8134 | 57.9391 | -0.17395 | 122.8409 | 0.10529 | 57.9391 | 120.9091 | 122.8134 | -122.9233 | -123.0194
664.3281 | 123.0331 | -60.3333 | 62.4847 | -0.0041198 | 0.020933 | 0.015088 | 0.0087286 | 0.065452 | -0.0019247 | 0.073309 | -60.2097 | 62.4756 | -60.4523 | -60.5392 | 60.5347 | -2.5955 | -20.4758 | -20.0363 | 62.4435 | -60.5484 | -0.11902 | -0.009155 | 0.1236 | -0.20599 | -1.9501 | -0.21515 | -0.041199 | 0.24262 | 39.8575 | 40.2969 | 120.8679 | 122.8088 | 0.1236 | 122.7768 | 57.7377 | -0.21515 | 122.8088 | 0.1236 | 57.7377 | 120.8679 | 122.7768 | -122.937 | -123.0331
665.3281 | 123.056 | -60.3333 | 62.5305 | -0.14908 | 0.020506 | 0.013379 | 0.0046698 | 0.066734 | -0.0032065 | 0.073095 | -60.1822 | 62.5031 | -60.4248 | -60.7727 | 60.4111 | -2.5909 | -20.8282 | -20.2652 | 62.4847 | -60.5118 | -0.091553 | -0.027466 | 0.15106 | -0.43945 | -2.1194 | -0.17853 | -0.045777 | 0.24262 | 39.505 | 40.0681 | 120.7443 | 122.8363 | 0.15106 | 122.818 | 57.7423 | -0.17853 | 122.8363 | 0.15106 | 57.7423 | 120.7443 | 122.818 | -122.9553 | -123.0423
666.3281 | 123.0606 | -60.3195 | 62.5305 | 0.011139 | 0.021147 | 0.01167 | 0.0076606 | 0.066306 | -0.0021383 | 0.070746 | -60.1685 | 62.5031 | -60.4019 | -60.5301 | 60.5026 | -2.9022 | -21.0571 | -20.6314 | 62.4893 | -60.5209 | -0.082398 | -0.027466 | 0.15106 | -0.21057 | -2.0279 | -0.20142 | -0.041199 | 0.23346 | 39.2624 | 39.6881 | 120.8221 | 122.8226 | 0.15106 | 122.8088 | 57.4173 | -0.20142 | 122.8226 | 0.15106 | 57.4173 | 120.8221 | 122.8088 | -122.9324 | -123.0515
667.3281 | 122.9965 | -60.3424 | 62.5031 | 0.21713 | 0.021147 | 0.011884 | 0.0087286 | 0.064811 | -0.0014975 | 0.073095 | -60.2234 | 62.5214 | -60.4156 | -60.585 | 60.3882 | -3.1128 | -21.3226 | -21.0388 | 62.4664 | -60.5438 | -0.073242 | 0.01831 | 0.11902 | -0.24262 | -2.1149 | -0.20142 | -0.036621 | 0.19226 | 39.0198 | 39.3036 | 120.7306 | 122.8638 | 0.11902 | 122.8088 | 57.2296 | -0.20142 | 122.8638 | 0.11902 | 57.2296 | 120.7306 | 122.8088 | -122.9187 | -123.0469
668.3281 | 123.0606 | -60.3104 | 62.5168 | -0.027008 | 0.02136 | 0.012952 | 0.0080878 | 0.065666 | -0.0012839 | 0.072668 | -60.1273 | 62.5397 | -60.3882 | -60.5118 | 60.4294 | -3.1906 | -21.5744 | -21.1716 | 62.4847 | -60.5164 | -0.07782 | 0.022888 | 0.18311 | -0.20142 | -2.0874 | -0.20599 | -0.032044 | 0.26093 | 38.736 | 39.1388 | 120.7397 | 122.85 | 0.18311 | 122.7951 | 57.1198 | -0.20599 | 122.85 | 0.18311 | 57.1198 | 120.7397 | 122.7951 | -122.905 | -123.0331
669.3281 | 123.0377 | -60.3012 | 62.5671 | -0.12619 | 0.023283 | 0.016797 | 0.0072332 | 0.063743 | -0.00085669 | 0.074164 | -60.1547 | 62.5717 | -60.4019 | -60.5072 | 60.4019 | -3.3371 | -21.8124 | -21.4096 | 62.5076 | -60.4935 | -0.10071 | 0.004577 | 0.14648 | -0.20599 | -2.1652 | -0.19226 | -0.05951 | 0.24719 | 38.4888 | 38.8916 | 120.7031 | 122.8729 | 0.14648 | 122.8088 | 56.9641 | -0.19226 | 122.8729 | 0.14648 | 56.9641 | 120.7031 | 122.8088 | -122.9691 | -123.0606
670.3281 | 123.0515 | -60.3058 | 62.5397 | 1.0716 | 0.021147 | 0.01402 | 0.0061652 | 0.066306 | -0.0023519 | 0.073309 | -60.1089 | 62.5214 | -60.379 | -60.4706 | 60.3928 | -3.479 | -22.1649 | -21.6888 | 62.5168 | -60.4935 | -0.073242 | -0.018311 | 0.19684 | -0.1648 | -2.1469 | -0.18768 | -0.022888 | 0.27008 | 38.1409 | 38.6169 | 120.6985 | 122.8271 | 0.19684 | 122.8226 | 56.8268 | -0.18768 | 122.8271 | 0.19684 | 56.8268 | 120.6985 | 122.8226 | -122.9187 | -123.0331
671.3281 | 123.0423 | -60.2783 | 62.5671 | -0.0041198 | 0.01901 | 0.015302 | 0.0061652 | 0.065879 | -0.0019247 | 0.074591 | -60.1364 | 62.5671 | -60.4019 | -60.4889 | 60.3058 | -3.653 | -22.3526 | -21.9635 | 62.5076 | -60.4935 | -0.1236 | 0 | 0.14191 | -0.21057 | -2.2614 | -0.21515 | -0.05951 | 0.2655 | 37.9257 | 38.3148 | 120.5841 | 122.8455 | 0.14191 | 122.7859 | 56.6254 | -0.21515 | 122.8455 | 0.14191 | 56.6254 | 120.5841 | 122.7859 | -122.9691 | -123.0606
672.3281 | 123.0286 | -60.2783 | 62.5671 | -0.0041198 | 0.021787 | 0.015088 | 0.0061652 | 0.065879 | -0.0038473 | 0.073523 | -60.0952 | 62.558 | -60.379 | -60.4797 | 60.2646 | -3.7903 | -22.5632 | -22.1375 | 62.5305 | -60.4889 | -0.10071 | -0.009156 | 0.1831 | -0.20142 | -2.3026 | -0.21057 | -0.036621 | 0.28381 | 37.7151 | 38.1409 | 120.5429 | 122.8363 | 0.1831 | 122.8088 | 56.488 | -0.21057 | 122.8363 | 0.1831 | 56.488 | 120.5429 | 122.8088 | -122.9462 | -123.056
673.3281 | 123.0698 | -60.2783 | 62.5809 | -0.011749 | 0.021574 | 0.011884 | 0.0059516 | 0.065025 | -0.0029929 | 0.0716 | -60.1181 | 62.5763 | -60.3607 | -60.466 | 60.228 | -3.891 | -22.8149 | -22.3663 | 62.5259 | -60.4614 | -0.082398 | -0.004578 | 0.16022 | -0.18768 | -2.3529 | -0.18311 | -0.054932 | 0.24262 | 37.4634 | 37.912 | 120.5063 | 122.8546 | 0.16022 | 122.8043 | 56.3873 | -0.18311 | 122.8546 | 0.16022 | 56.3873 | 120.5063 | 122.8043 | -122.9416 | -123.0423
674.3281 | 123.056 | -60.2325 | 62.6038 | -0.042267 | 0.020719 | 0.01637 | 0.0065924 | 0.066093 | -0.0023519 | 0.071814 | -60.0769 | 62.5992 | -60.3287 | -60.4568 | 60.2051 | -3.9871 | -23.053 | -22.5632 | 62.5122 | -60.4568 | -0.09613 | -0.004578 | 0.15564 | -0.2243 | -2.3987 | -0.2243 | -0.091553 | 0.25177 | 37.1796 | 37.6694 | 120.4376 | 122.8317 | 0.15564 | 122.7448 | 56.2454 | -0.2243 | 122.8317 | 0.15564 | 56.2454 | 120.4376 | 122.7448 | -122.9324 | -123.0606
675.3281 | 123.0469 | -60.2509 | 62.5946 | -0.14908 | 0.021574 | 0.010602 | 0.0065924 | 0.065452 | -0.0023519 | 0.07395 | -60.0998 | 62.5717 | -60.3561 | -60.4523 | 60.1501 | -4.0649 | -23.259 | -22.8012 | 62.5442 | -60.4477 | -0.10529 | -0.022888 | 0.15106 | -0.20142 | -2.4445 | -0.19684 | -0.050354 | 0.25635 | 36.9919 | 37.4496 | 120.401 | 122.8226 | 0.15106 | 122.7951 | 56.1859 | -0.19684 | 122.8226 | 0.15106 | 56.1859 | 120.401 | 122.7951 | -122.9507 | -123.0423
676.3281 | 123.0377 | -60.26 | 62.6175 | -0.17197 | 0.020292 | 0.012097 | 0.005097 | 0.064811 | -0.0014975 | 0.075232 | -60.1089 | 62.5946 | -60.3424 | -60.4614 | 60.0723 | -4.1565 | -23.4421 | -22.9614 | 62.5809 | -60.4614 | -0.082397 | -0.022889 | 0.15106 | -0.20142 | -2.5452 | -0.20142 | -0.036621 | 0.23346 | 36.8179 | 37.2986 | 120.3323 | 122.8546 | 0.15106 | 122.8409 | 56.1035 | -0.20142 | 122.8546 | 0.15106 | 56.1035 | 120.3323 | 122.8409 | -122.9599 | -123.0789
677.3281 | 123.0515 | -60.2463 | 62.5763 | -0.15671 | 0.021787 | 0.011457 | 0.007447 | 0.064811 | -0.0021383 | 0.071173 | -60.0632 | 62.5992 | -60.3287 | -60.4385 | 60.0311 | -4.1977 | -23.671 | -23.1583 | 62.5671 | -60.434 | -0.082397 | 0.022888 | 0.18311 | -0.19226 | -2.5452 | -0.18768 | -0.009155 | 0.2655 | 36.5753 | 37.088 | 120.2774 | 122.8455 | 0.18311 | 122.8134 | 56.0486 | -0.18768 | 122.8455 | 0.18311 | 56.0486 | 120.2774 | 122.8134 | -122.905 | -123.0103
678.3281 | 123.056 | -60.2325 | 62.59 | 0.049286 | 0.017515 | 0.01167 | 0.0076606 | 0.064811 | -0.0012839 | 0.0763 | -60.0266 | 62.6038 | -60.3149 | -60.4065 | 59.9625 | -4.2252 | -23.8724 | -23.3231 | 62.5626 | -60.4202 | -0.082397 | 0.013733 | 0.20599 | -0.17395 | -2.6276 | -0.18768 | -0.027466 | 0.28839 | 36.3602 | 36.9095 | 120.195 | 122.8363 | 0.20599 | 122.7951 | 56.0074 | -0.18768 | 122.8363 | 0.20599 | 56.0074 | 120.195 | 122.7951 | -122.905 | -123.0103
679.3281 | 123.0515 | -60.2554 | 62.6312 | -1.2019 | 0.020933 | 0.011243 | 0.0059516 | 0.062675 | -0.0029929 | 0.071814 | -60.0769 | 62.6358 | -60.3241 | -60.4111 | 59.9304 | -4.2709 | -24.028 | -23.4741 | 62.5626 | -60.4156 | -0.068665 | 0.004577 | 0.17853 | -0.15564 | -2.7008 | -0.16022 | -0.068665 | 0.24719 | 36.2274 | 36.7813 | 120.1859 | 122.8912 | 0.17853 | 122.818 | 55.9845 | -0.16022 | 122.8912 | 0.17853 | 55.9845 | 120.1859 | 122.818 | -122.9553 | -123.0469
680.3281 | 123.0835 | -60.2417 | 62.6083 | 0.0035097 | 0.021574 | 0.014447 | 0.0097968 | 0.063316 | -0.0021383 | 0.075659 | -60.0311 | 62.6266 | -60.3287 | -60.4568 | 59.935 | -4.2664 | -24.1562 | -23.6023 | 62.5717 | -60.434 | -0.086975 | 0.018311 | 0.21057 | -0.21515 | -2.6733 | -0.19226 | -0.036621 | 0.29755 | 36.0855 | 36.6394 | 120.1767 | 122.8683 | 0.21057 | 122.8134 | 55.9753 | -0.19226 | 122.8683 | 0.21057 | 55.9753 | 120.1767 | 122.8134 | -122.937 | -123.0423
681.3281 | 123.0789 | -60.2234 | 62.6633 | -0.027008 | 0.019438 | 0.012952 | 0.0065924 | 0.065238 | 0.00042511 | 0.074377 | -60.0266 | 62.6358 | -60.3012 | -60.4111 | 59.7748 | -4.3259 | -24.6277 | -23.7259 | 62.5671 | -60.4065 | -0.077819 | -0.027466 | 0.19684 | -0.18768 | -2.8885 | -0.18311 | -0.09613 | 0.27466 | 35.5957 | 36.4975 | 119.9982 | 122.8592 | 0.19684 | 122.7905 | 55.8975 | -0.18311 | 122.8592 | 0.19684 | 55.8975 | 119.9982 | 122.7905 | -122.9645 | -123.0698
682.3281 | 123.056 | -60.1776 | 62.6678 | -0.11856 | 0.020078 | 0.0091068 | 0.0044562 | 0.06118 | -0.0019247 | 0.072027 | -60.054 | 62.6083 | -60.2737 | -60.4477 | 59.6924 | -4.3945 | -24.4995 | -24.0005 | 62.6404 | -60.3973 | -0.096131 | -0.05951 | 0.1236 | -0.27008 | -2.9755 | -0.21973 | -0.027466 | 0.21973 | 35.6781 | 36.1771 | 119.87 | 122.7859 | 0.1236 | 122.818 | 55.7831 | -0.21973 | 122.7859 | 0.1236 | 55.7831 | 119.87 | 122.818 | -122.9416 | -123.0652
683.3281 | 123.0194 | -60.2005 | 62.6633 | -0.15671 | 0.019865 | 0.016584 | 0.0059516 | 0.062675 | -0.0034201 | 0.072241 | -60.0723 | 62.6404 | -60.2875 | -60.4294 | 59.61 | -4.3854 | -24.5728 | -24.0738 | 62.6175 | -60.4111 | -0.086976 | -0.022888 | 0.12817 | -0.22888 | -3.0533 | -0.21057 | -0.045776 | 0.21515 | 35.6277 | 36.1267 | 119.8105 | 122.8409 | 0.12817 | 122.818 | 55.8151 | -0.21057 | 122.8409 | 0.12817 | 55.8151 | 119.8105 | 122.818 | -122.9507 | -123.0743
684.3281 | 123.0469 | -60.1913 | 62.6541 | -0.11856 | 0.019224 | 0.011884 | 0.0072332 | 0.065666 | -0.00085669 | 0.07395 | -60.0174 | 62.6541 | -60.3149 | -60.4156 | 59.5642 | -4.3671 | -24.7879 | -24.1791 | 62.6266 | -60.379 | -0.1236 | 0 | 0.17395 | -0.2243 | -3.0899 | -0.18768 | -0.027466 | 0.29755 | 35.4034 | 36.0123 | 119.7556 | 122.8455 | 0.17395 | 122.818 | 55.8243 | -0.18768 | 122.8455 | 0.17395 | 55.8243 | 119.7556 | 122.818 | -122.9691 | -123.0331
685.3281 | 123.0789 | -60.1959 | 62.6587 | -0.065155 | 0.020933 | 0.017011 | 0.006806 | 0.067161 | -0.0012839 | 0.075232 | -59.9899 | 62.645 | -60.2966 | -60.3745 | 59.4727 | -4.3945 | -25.0214 | -24.4949 | 62.59 | -60.4156 | -0.10071 | -0.013733 | 0.20599 | -0.17853 | -3.186 | -0.21973 | -0.068664 | 0.3067 | 35.1746 | 35.701 | 119.6686 | 122.8409 | 0.20599 | 122.7859 | 55.8014 | -0.21973 | 122.8409 | 0.20599 | 55.8014 | 119.6686 | 122.7859 | -122.9553 | -123.0743
686.3281 | 123.056 | -60.1685 | 62.6541 | -0.088043 | 0.019865 | 0.011884 | 0.006806 | 0.063957 | -0.0017111 | 0.073095 | -59.9854 | 62.645 | -60.2509 | -60.3745 | 59.3903 | -4.335 | -24.9802 | -24.2661 | 62.6266 | -60.3973 | -0.082397 | -0.009156 | 0.1831 | -0.20599 | -3.2639 | -0.22888 | -0.027466 | 0.2655 | 35.1883 | 35.9024 | 119.5587 | 122.8134 | 0.1831 | 122.7951 | 55.8334 | -0.22888 | 122.8134 | 0.1831 | 55.8334 | 119.5587 | 122.7951 | -122.905 | -123.0515
687.3281 | 123.0423 | -60.1868 | 62.677 | -0.12619 | 0.021574 | 0.013806 | 0.0044562 | 0.062675 | 0.0014933 | 0.075018 | -59.9899 | 62.6633 | -60.2829 | -60.3882 | 59.2987 | -4.303 | -25.0854 | -24.3301 | 62.6221 | -60.3836 | -0.09613 | -0.013733 | 0.19684 | -0.20142 | -3.3783 | -0.19684 | -0.054932 | 0.29297 | 35.1013 | 35.8566 | 119.4855 | 122.85 | 0.19684 | 122.8088 | 55.8838 | -0.19684 | 122.85 | 0.19684 | 55.8838 | 119.4855 | 122.8088 | -122.9599 | -123.0606
688.3281 | 123.0743 | -60.1913 | 62.6816 | -0.1796 | 0.020078 | 0.013166 | 0.0070196 | 0.065025 | -0.0029929 | 0.073736 | -60.0082 | 62.6587 | -60.2966 | -60.379 | 59.2117 | -4.2984 | -25.1633 | -24.4171 | 62.6038 | -60.3745 | -0.10529 | -0.022889 | 0.1831 | -0.18768 | -3.4698 | -0.18311 | -0.07782 | 0.28839 | 35.0281 | 35.7742 | 119.4031 | 122.85 | 0.1831 | 122.7951 | 55.8929 | -0.18311 | 122.85 | 0.1831 | 55.8929 | 119.4031 | 122.7951 | -122.9782 | -123.056
689.3281 | 122.9965 | -60.1822 | 62.7045 | -0.12619 | 0.022428 | 0.014447 | 0.00232 | 0.063529 | -0.0021383 | 0.072241 | -60.022 | 62.6495 | -60.2646 | -60.434 | 59.0836 | -4.2664 | -25.1587 | -24.4629 | 62.6816 | -60.3516 | -0.082397 | -0.054932 | 0.16022 | -0.25177 | -3.6209 | -0.16937 | -0.022888 | 0.24261 | 35.0235 | 35.7193 | 119.2657 | 122.8317 | 0.16022 | 122.8638 | 55.9158 | -0.16937 | 122.8317 | 0.16022 | 55.9158 | 119.2657 | 122.8638 | -122.9691 | -123.056
690.3281 | 123.0331 | -60.173 | 62.6999 | -0.16434 | 0.021147 | 0.009534 | 0.0031744 | 0.063743 | -0.00085669 | 0.073309 | -60.0128 | 62.6312 | -60.2921 | -60.4111 | 59.0195 | -4.2206 | -25.1907 | -24.4812 | 62.6541 | -60.379 | -0.11902 | -0.068664 | 0.16022 | -0.23804 | -3.6804 | -0.20599 | -0.045776 | 0.27924 | 34.9823 | 35.6918 | 119.1925 | 122.8043 | 0.16022 | 122.8271 | 55.9525 | -0.20599 | 122.8043 | 0.16022 | 55.9525 | 119.1925 | 122.8271 | -122.9919 | -123.0789
691.3281 | 123.0194 | -60.1868 | 62.7136 | -0.14145 | 0.021787 | 0.006757 | 0.005738 | 0.066093 | -0.0021383 | 0.073523 | -60.0082 | 62.6495 | -60.2646 | -60.3928 | 58.9142 | -4.2297 | -25.3418 | -24.5728 | 62.677 | -60.3561 | -0.077819 | -0.064087 | 0.17853 | -0.20599 | -3.7994 | -0.16937 | -0.036621 | 0.25635 | 34.845 | 35.614 | 119.101 | 122.8363 | 0.17853 | 122.8638 | 55.957 | -0.16937 | 122.8363 | 0.17853 | 55.957 | 119.101 | 122.8638 | -122.9782 | -123.0698
692.3281 | 123.0835 | -60.1547 | 62.6724 | -0.14145 | 0.019438 | 0.01167 | 0.007447 | 0.065666 | -0.0010703 | 0.074377 | -59.9533 | 62.6587 | -60.2325 | -60.3607 | 58.8547 | -4.184 | -25.4196 | -24.5041 | 62.6495 | -60.3516 | -0.07782 | -0.013733 | 0.20142 | -0.20599 | -3.8177 | -0.19684 | -0.022888 | 0.27924 | 34.7351 | 35.6506 | 119.0094 | 122.8134 | 0.20142 | 122.8043 | 55.9708 | -0.19684 | 122.8134 | 0.20142 | 55.9708 | 119.0094 | 122.8043 | -122.905 | -123.024
693.3281 | 123.0515 | -60.1547 | 62.709 | -0.12619 | 0.019438 | 0.015302 | 0.006806 | 0.063743 | 0.0010659 | 0.074164 | -59.9533 | 62.6816 | -60.2692 | -60.3653 | 58.7402 | -3.9688 | -25.2365 | -24.353 | 62.645 | -60.3699 | -0.11444 | -0.027465 | 0.20142 | -0.21057 | -3.9688 | -0.21515 | -0.064087 | 0.31586 | 34.9182 | 35.8017 | 118.895 | 122.8363 | 0.20142 | 122.7997 | 56.1859 | -0.21515 | 122.8363 | 0.20142 | 56.1859 | 118.895 | 122.7997 | -122.9782 | -123.0789
694.3281 | 123.0423 | -60.1364 | 62.6907 | -0.14908 | 0.017088 | 0.012738 | 0.007447 | 0.063102 | -0.0012839 | 0.074164 | -59.9625 | 62.6495 | -60.2417 | -60.3699 | 58.6807 | -3.7033 | -25.0992 | -24.2111 | 62.6404 | -60.3653 | -0.10528 | -0.041199 | 0.17395 | -0.23346 | -4.01 | -0.22888 | -0.050354 | 0.27924 | 35.0372 | 35.9253 | 118.8171 | 122.7859 | 0.17395 | 122.7768 | 56.4331 | -0.22888 | 122.7859 | 0.17395 | 56.4331 | 118.8171 | 122.7768 | -122.9324 | -123.056
695.3281 | 123.0423 | -60.1639 | 62.7045 | -0.14145 | 0.020292 | 0.01167 | 0.0072332 | 0.06417 | -0.0027793 | 0.07395 | -59.9808 | 62.6587 | -60.2692 | -60.3745 | 58.58 | -3.5843 | -24.7696 | -23.7213 | 62.6587 | -60.3607 | -0.10529 | -0.045777 | 0.18311 | -0.21057 | -4.1245 | -0.19684 | -0.045777 | 0.28839 | 35.3943 | 36.4426 | 118.7439 | 122.8226 | 0.18311 | 122.8226 | 56.5796 | -0.19684 | 122.8226 | 0.18311 | 56.5796 | 118.7439 | 122.8226 | -122.9736 | -123.0652
696.3281 | 123.0331 | -60.1685 | 62.6816 | -0.19485 | 0.01837 | 0.0073978 | 0.0053106 | 0.063957 | -0.0012839 | 0.075232 | -59.9991 | 62.6404 | -60.2737 | -60.4156 | 58.461 | -3.4882 | -24.4904 | -23.3871 | 62.6587 | -60.379 | -0.10529 | -0.041199 | 0.16937 | -0.24719 | -4.2206 | -0.21057 | -0.022889 | 0.27466 | 35.6781 | 36.7813 | 118.6295 | 122.8088 | 0.16937 | 122.8271 | 56.6803 | -0.21057 | 122.8088 | 0.16937 | 56.6803 | 118.6295 | 122.8271 | -122.9553 | -123.0606
697.3281 | 123.0103 | -60.173 | 62.677 | -0.11856 | 0.017515 | 0.014234 | 0.006806 | 0.063102 | -2.092e-06 | 0.073523 | -60.0037 | 62.6175 | -60.3058 | -60.4065 | 58.3694 | -3.4149 | -24.2935 | -23.085 | 62.6587 | -60.3653 | -0.13275 | -0.059509 | 0.16937 | -0.23346 | -4.3076 | -0.19226 | -0.018311 | 0.30212 | 35.8795 | 37.088 | 118.5425 | 122.7905 | 0.16937 | 122.8317 | 56.7581 | -0.19226 | 122.7905 | 0.16937 | 56.7581 | 118.5425 | 122.8317 | -122.9828 | -123.0423
698.3281 | 123.0469 | -60.1913 | 62.6907 | -0.16434 | 0.018583 | 0.011457 | 0.0072332 | 0.062034 | -0.00042929 | 0.074377 | -59.9808 | 62.645 | -60.2692 | -60.3973 | 58.2779 | -3.3554 | -24.1837 | -22.9202 | 62.6358 | -60.379 | -0.07782 | -0.045777 | 0.21057 | -0.20599 | -4.4128 | -0.18768 | -0.054932 | 0.28839 | 36.0077 | 37.2711 | 118.4692 | 122.8363 | 0.21057 | 122.8271 | 56.8359 | -0.18768 | 122.8363 | 0.21057 | 56.8359 | 118.4692 | 122.8271 | -122.9599 | -123.0698
699.3281 | 123.0743 | -60.1822 | 62.6953 | -0.12619 | 0.020292 | 0.01637 | 0.0063788 | 0.065238 | -0.0023519 | 0.075659 | -59.9442 | 62.6678 | -60.2829 | -60.3745 | 58.2047 | -3.2822 | -24.1013 | -22.7509 | 62.6175 | -60.3699 | -0.10071 | -0.027465 | 0.23804 | -0.19226 | -4.4907 | -0.18768 | -0.077819 | 0.33875 | 36.0809 | 37.4313 | 118.3868 | 122.85 | 0.23804 | 122.7997 | 56.9 | -0.18768 | 122.85 | 0.23804 | 56.9 | 118.3868 | 122.7997 | -122.9782 | -123.0652
700.3281 | 123.1018 | -60.1776 | 62.6633 | -0.16434 | 0.020078 | 0.010175 | 0.0061652 | 0.063957 | -0.0012839 | 0.072882 | -59.9533 | 62.6724 | -60.26 | -60.3699 | 58.1268 | -3.241 | -23.9456 | -22.5723 | 62.6358 | -60.3561 | -0.082398 | 0.009155 | 0.2243 | -0.19226 | -4.5364 | -0.17853 | -0.027466 | 0.3067 | 36.232 | 37.6053 | 118.3044 | 122.85 | 0.2243 | 122.8134 | 56.9366 | -0.17853 | 122.85 | 0.2243 | 56.9366 | 118.3044 | 122.8134 | -122.9233 | -123.0194
701.3281 | 123.0606 | -60.173 | 62.6953 | -0.13382 | 0.020933 | 0.014447 | 0.0070196 | 0.064384 | -0.0034201 | 0.074164 | -59.9442 | 62.6541 | -60.2737 | -60.3836 | 58.0215 | -3.2593 | -23.8495 | -22.4533 | 62.6312 | -60.3378 | -0.10071 | -0.041198 | 0.22888 | -0.21057 | -4.6738 | -0.16479 | -0.064086 | 0.32959 | 36.3235 | 37.7197 | 118.1946 | 122.8271 | 0.22888 | 122.8043 | 56.9138 | -0.16479 | 122.8271 | 0.22888 | 56.9138 | 118.1946 | 122.8043 | -122.9691 | -123.0331
702.3281 | 123.0377 | -60.1776 | 62.6633 | -0.14145 | 0.023069 | 0.011884 | 0.0048834 | 0.065025 | -0.0019247 | 0.073309 | -59.935 | 62.6495 | -60.2783 | -60.3745 | 57.9208 | -3.2684 | -23.7167 | -22.3022 | 62.645 | -60.3699 | -0.10071 | -0.013733 | 0.24261 | -0.19684 | -4.7424 | -0.19226 | -0.018311 | 0.34332 | 36.4609 | 37.8754 | 118.0984 | 122.8271 | 0.24261 | 122.8226 | 56.9092 | -0.19226 | 122.8271 | 0.24261 | 56.9092 | 118.0984 | 122.8226 | -122.9416 | -123.0331
703.3281 | 123.024 | -60.2005 | 62.6907 | -0.16434 | 0.020719 | 0.013166 | 0.0038154 | 0.06417 | -0.00021569 | 0.074164 | -59.9808 | 62.6587 | -60.2692 | -60.4156 | 57.7881 | -3.2776 | -23.5062 | -22.1649 | 62.6495 | -60.3516 | -0.068665 | -0.032044 | 0.21973 | -0.21515 | -4.9026 | -0.15106 | -0.041199 | 0.28839 | 36.6943 | 38.0356 | 117.9886 | 122.8592 | 0.21973 | 122.85 | 56.9229 | -0.15106 | 122.8592 | 0.21973 | 56.9229 | 117.9886 | 122.85 | -122.9599 | -123.0423
704.3281 | 123.0377 | -60.173 | 62.6999 | -0.19485 | 0.021787 | 0.012311 | 0.0053106 | 0.063743 | -0.0010703 | 0.074804 | -59.9625 | 62.6404 | -60.2646 | -60.4019 | 57.6782 | -3.4103 | -23.4558 | -22.1191 | 62.6724 | -60.3561 | -0.091552 | -0.059509 | 0.21057 | -0.22888 | -5.0217 | -0.18311 | -0.027466 | 0.30212 | 36.7172 | 38.0539 | 117.8513 | 122.8134 | 0.21057 | 122.8455 | 56.7627 | -0.18311 | 122.8134 | 0.21057 | 56.7627 | 117.8513 | 122.8455 | -122.9645 | -123.056
705.3281 | 123.056 | -60.1959 | 62.6862 | -0.18723 | 0.019224 | 0.0065432 | 0.0063788 | 0.062034 | -0.0021383 | 0.073736 | -59.9487 | 62.6633 | -60.2737 | -60.3882 | 57.5912 | -3.4882 | -23.378 | -21.9864 | 62.677 | -60.3424 | -0.07782 | -0.022888 | 0.24719 | -0.19226 | -5.0949 | -0.14648 | -0.009155 | 0.32501 | 36.8179 | 38.2095 | 117.7872 | 122.8592 | 0.24719 | 122.8729 | 56.7078 | -0.14648 | 122.8592 | 0.24719 | 56.7078 | 117.7872 | 122.8729 | -122.9599 | -123.0286
706.3281 | 123.0606 | -60.1776 | 62.6953 | -0.072784 | 0.020933 | 0.014661 | 0.008515 | 0.062675 | -0.0014975 | 0.0763 | -59.9121 | 62.6724 | -60.2646 | -60.3607 | 57.5272 | -3.4836 | -23.2452 | -21.7804 | 62.6358 | -60.3516 | -0.086975 | -0.022888 | 0.2655 | -0.18311 | -5.1682 | -0.17395 | -0.059509 | 0.35248 | 36.9324 | 38.3972 | 117.7048 | 122.85 | 0.2655 | 122.8134 | 56.694 | -0.17395 | 122.85 | 0.2655 | 56.694 | 117.7048 | 122.8134 | -122.9599 | -123.0469
707.3281 | 123.024 | -60.1364 | 62.6678 | -0.14145 | 0.019438 | 0.012097 | 0.01001 | 0.063529 | 0.00085231 | 0.073523 | -59.9075 | 62.6633 | -60.2554 | -60.3607 | 57.4127 | -3.5477 | -23.053 | -21.6339 | 62.645 | -60.3561 | -0.11902 | -0.004578 | 0.22888 | -0.2243 | -5.2551 | -0.21973 | -0.022889 | 0.3479 | 37.0834 | 38.5025 | 117.5491 | 122.7997 | 0.22888 | 122.7814 | 56.5887 | -0.21973 | 122.7997 | 0.22888 | 56.5887 | 117.5491 | 122.7814 | -122.9233 | -123.024
708.3281 | 123.0423 | -60.1776 | 62.6907 | -0.13382 | 0.020292 | 0.011884 | 0.0070196 | 0.063529 | -0.00021569 | 0.076086 | -59.9167 | 62.6816 | -60.26 | -60.347 | 57.3212 | -3.566 | -22.8882 | -21.4828 | 62.6633 | -60.3745 | -0.082398 | -0.009155 | 0.26093 | -0.16937 | -5.3696 | -0.19684 | -0.027466 | 0.34332 | 37.2894 | 38.6948 | 117.4988 | 122.8592 | 0.26093 | 122.8409 | 56.6116 | -0.19684 | 122.8592 | 0.26093 | 56.6116 | 117.4988 | 122.8409 | -122.9507 | -123.0652
709.3281 | 123.0881 | -60.1639 | 62.6862 | -0.14908 | 0.019224 | 0.015088 | 0.0059516 | 0.064384 | -0.00085669 | 0.077154 | -59.9213 | 62.6999 | -60.2737 | -60.3516 | 57.2159 | -3.7308 | -22.8516 | -21.5332 | 62.6678 | -60.3424 | -0.10986 | 0.013733 | 0.24261 | -0.18768 | -5.4703 | -0.17853 | -0.01831 | 0.35248 | 37.3123 | 38.6307 | 117.3798 | 122.8638 | 0.24261 | 122.8317 | 56.4331 | -0.17853 | 122.8638 | 0.24261 | 56.4331 | 117.3798 | 122.8317 | -122.9599 | -123.0286
710.3281 | 122.9919 | -60.1822 | 62.7274 | -0.18723 | 0.019651 | 0.013806 | 0.0063788 | 0.063316 | -0.0012839 | 0.072668 | -59.9442 | 62.677 | -60.2509 | -60.3928 | 57.0923 | -3.8223 | -22.641 | -21.4142 | 62.6678 | -60.347 | -0.068664 | -0.050354 | 0.23804 | -0.21057 | -5.6351 | -0.16479 | -0.059509 | 0.3067 | 37.5412 | 38.768 | 117.2745 | 122.8592 | 0.23804 | 122.85 | 56.3599 | -0.16479 | 122.8592 | 0.23804 | 56.3599 | 117.2745 | 122.85 | -122.9782 | -123.0743
711.3281 | 123.0469 | -60.173 | 62.7182 | -0.14145 | 0.02136 | 0.017652 | 0.0072332 | 0.063957 | -0.0021383 | 0.072455 | -59.9121 | 62.677 | -60.26 | -60.3607 | 57.0099 | -3.9001 | -22.5632 | -21.3318 | 62.6678 | -60.347 | -0.086975 | -0.041199 | 0.26093 | -0.18768 | -5.7083 | -0.17395 | -0.050354 | 0.3479 | 37.6099 | 38.8412 | 117.1829 | 122.85 | 0.26093 | 122.8409 | 56.2729 | -0.17395 | 122.85 | 0.26093 | 56.2729 | 117.1829 | 122.8409 | -122.9782 | -123.0652
712.3281 | 123.0606 | -60.1501 | 62.7045 | -0.12619 | 0.020506 | 0.014661 | 0.0080878 | 0.063316 | -0.00042929 | 0.073309 | -59.8663 | 62.6633 | -60.2646 | -60.3378 | 56.9366 | -3.8635 | -22.4579 | -21.1716 | 62.6541 | -60.3424 | -0.11444 | -0.041199 | 0.28381 | -0.18768 | -5.7678 | -0.19226 | -0.050354 | 0.39825 | 37.6923 | 38.9786 | 117.0868 | 122.8134 | 0.28381 | 122.8043 | 56.2866 | -0.19226 | 122.8134 | 0.28381 | 56.2866 | 117.0868 | 122.8043 | -122.9691 | -123.0469
713.3281 | 123.0835 | -60.1456 | 62.7136 | -0.1033 | 0.021147 | 0.012952 | 0.008515 | 0.065452 | 0.00063871 | 0.075873 | -59.8801 | 62.6678 | -60.2783 | -60.3516 | 56.8405 | -3.8406 | -22.197 | -20.9381 | 62.6495 | -60.3561 | -0.13275 | -0.045776 | 0.2655 | -0.20599 | -5.8731 | -0.21057 | -0.064087 | 0.39825 | 37.9486 | 39.2075 | 116.9861 | 122.8134 | 0.2655 | 122.7951 | 56.3049 | -0.21057 | 122.8134 | 0.2655 | 56.3049 | 116.9861 | 122.7951 | -122.9919 | -123.0698
714.3281 | 123.0469 | -60.1547 | 62.6816 | -0.15671 | 0.022215 | 0.017011 | 0.006806 | 0.066306 | -0.0012839 | 0.074377 | -59.8984 | 62.6816 | -60.2646 | -60.3561 | 56.7261 | -3.9276 | -22.1054 | -20.8969 | 62.6953 | -60.3607 | -0.10986 | 0 | 0.25635 | -0.20142 | -5.9555 | -0.20599 | 0.013732 | 0.36621 | 38.0493 | 39.2578 | 116.8808 | 122.8363 | 0.25635 | 122.85 | 56.2271 | -0.20599 | 122.8363 | 0.25635 | 56.2271 | 116.8808 | 122.85 | -122.9462 | -123.0423
715.3281 | 123.024 | -60.1593 | 62.709 | -0.16434 | 0.018797 | 0.012097 | 0.006806 | 0.065452 | -0.00085669 | 0.076086 | -59.8892 | 62.6587 | -60.2463 | -60.3882 | 56.6208 | -3.9963 | -21.8582 | -20.6772 | 62.6678 | -60.3424 | -0.086975 | -0.050354 | 0.27008 | -0.22888 | -6.0883 | -0.18311 | -0.041198 | 0.35706 | 38.3011 | 39.4821 | 116.7801 | 122.818 | 0.27008 | 122.8271 | 56.163 | -0.18311 | 122.818 | 0.27008 | 56.163 | 116.7801 | 122.8271 | -122.9553 | -123.0515
716.3281 | 123.0148 | -60.1456 | 62.7182 | -0.14145 | 0.017942 | 0.01167 | 0.0065924 | 0.062461 | -0.0010703 | 0.077368 | -59.903 | 62.6678 | -60.26 | -60.4019 | 56.5475 | -3.8956 | -21.5836 | -20.4437 | 62.6862 | -60.3378 | -0.11444 | -0.050354 | 0.24262 | -0.25635 | -6.1707 | -0.19226 | -0.032044 | 0.35706 | 38.562 | 39.7018 | 116.6931 | 122.8134 | 0.24262 | 122.8317 | 56.25 | -0.19226 | 122.8134 | 0.24262 | 56.25 | 116.6931 | 122.8317 | -122.9782 | -123.056
717.3281 | 122.9416 | -60.1547 | 62.7182 | -0.14908 | 0.019651 | 0.013593 | 0.00232 | 0.062675 | 0.00021151 | 0.074377 | -59.8892 | 62.6678 | -60.2509 | -60.3928 | 56.4468 | -3.9871 | -21.4462 | -20.1553 | 62.709 | -60.3149 | -0.09613 | -0.050354 | 0.2655 | -0.23804 | -6.2714 | -0.16022 | -0.009156 | 0.36163 | 38.7085 | 39.9994 | 116.6016 | 122.8226 | 0.2655 | 122.8638 | 56.1676 | -0.16022 | 122.8226 | 0.2655 | 56.1676 | 116.6016 | 122.8638 | -122.9691 | -123.0331
718.3281 | 123.0286 | -60.1501 | 62.7228 | 0.0035097 | 0.019865 | 0.012097 | 0.0065924 | 0.062461 | -0.0014975 | 0.075445 | -59.8846 | 62.6587 | -60.2737 | -60.4065 | 56.3873 | -4.1199 | -21.405 | -20.2789 | 62.6633 | -60.3287 | -0.1236 | -0.064087 | 0.2655 | -0.25635 | -6.3354 | -0.17853 | -0.059509 | 0.3891 | 38.7451 | 39.8712 | 116.5375 | 122.8088 | 0.2655 | 122.8134 | 56.0303 | -0.17853 | 122.8088 | 0.2655 | 56.0303 | 116.5375 | 122.8134 | -122.9965 | -123.0515
719.3281 | 123.0103 | -60.1501 | 62.7274 | -0.21774 | 0.01901 | 0.012097 | 0.0031744 | 0.061393 | -0.0025657 | 0.074377 | -59.8389 | 62.6862 | -60.228 | -60.4065 | 56.3049 | -4.2526 | -21.4233 | -20.2698 | 62.6953 | -60.3424 | -0.07782 | -0.041199 | 0.31128 | -0.25635 | -6.4224 | -0.19226 | -0.032044 | 0.3891 | 38.7268 | 39.8804 | 116.4551 | 122.8363 | 0.31128 | 122.8455 | 55.8975 | -0.19226 | 122.8363 | 0.31128 | 55.8975 | 116.4551 | 122.8455 | -122.9553 | -123.0698
720.3281 | 122.9919 | -60.173 | 62.7319 | -0.20248 | 0.019224 | 0.01167 | 0.0083014 | 0.061607 | -0.00042929 | 0.074804 | -59.8892 | 62.6633 | -60.2509 | -60.379 | 56.2134 | -4.1656 | -21.1624 | -20.0958 | 62.6816 | -60.3424 | -0.077819 | -0.068665 | 0.28381 | -0.20599 | -6.5186 | -0.16937 | -0.050354 | 0.36163 | 39.0106 | 40.0772 | 116.3864 | 122.8363 | 0.28381 | 122.8546 | 56.0074 | -0.16937 | 122.8363 | 0.28381 | 56.0074 | 116.3864 | 122.8546 | -122.9828 | -123.0743
721.3281 | 123.0194 | -60.1639 | 62.7274 | -0.0041198 | 0.019438 | 0.015302 | 0.0055244 | 0.062889 | -0.00042929 | 0.076513 | -59.8251 | 62.6587 | -60.26 | -60.3973 | 56.1127 | -4.1519 | -21.0297 | -19.9677 | 62.6907 | -60.3104 | -0.096131 | -0.068665 | 0.33875 | -0.23346 | -6.6147 | -0.14648 | -0.036621 | 0.43488 | 39.1342 | 40.1962 | 116.2766 | 122.8226 | 0.33875 | 122.8546 | 56.012 | -0.14648 | 122.8226 | 0.33875 | 56.012 | 116.2766 | 122.8546 | -122.9874 | -123.0377
722.3281 | 123.0286 | -60.1639 | 62.709 | -0.20248 | 0.016661 | 0.012952 | 0.0036018 | 0.063957 | -2.092e-06 | 0.074591 | -59.8663 | 62.645 | -60.2417 | -60.3699 | 56.0715 | -4.1245 | -20.7642 | -19.6747 | 62.6724 | -60.3516 | -0.07782 | -0.064087 | 0.29755 | -0.20599 | -6.6376 | -0.18768 | -0.036621 | 0.37537 | 39.3997 | 40.4892 | 116.2354 | 122.8088 | 0.29755 | 122.8363 | 56.0394 | -0.18768 | 122.8088 | 0.29755 | 56.0394 | 116.2354 | 122.8363 | -122.9507 | -123.0606
723.3281 | 123.111 | -60.1273 | 62.764 | -0.095673 | 0.016447 | 0.015729 | 0.0042426 | 0.060325 | 0.00063871 | 0.0763 | -59.8709 | 62.6495 | -60.2234 | -60.3928 | 55.9845 | -4.0604 | -20.6497 | -19.5648 | 62.6724 | -60.3287 | -0.096131 | -0.11444 | 0.25635 | -0.2655 | -6.7795 | -0.20142 | -0.091553 | 0.35248 | 39.4775 | 40.5624 | 116.1118 | 122.7768 | 0.25635 | 122.7997 | 56.0669 | -0.20142 | 122.7768 | 0.25635 | 56.0669 | 116.1118 | 122.7997 | -122.9874 | -123.0927
724.3281 | 123.111 | -60.0906 | 62.6953 | -0.14145 | 0.019438 | 0.014234 | 0.003388 | 0.062034 | -0.0019247 | 0.076941 | -59.7794 | 62.5854 | -60.2234 | -60.2737 | 56.0165 | -3.9368 | -20.4895 | -19.249 | 62.6862 | -60.2692 | -0.13275 | -0.10986 | 0.31128 | -0.18311 | -6.6788 | -0.17853 | -0.009155 | 0.44403 | 39.6011 | 40.8417 | 116.1072 | 122.6761 | 0.31128 | 122.7768 | 56.1539 | -0.17853 | 122.6761 | 0.31128 | 56.1539 | 116.1072 | 122.7768 | -122.9187 | -122.9645
725.3281 | 123.0377 | -60.1318 | 62.7136 | -0.21011 | 0.019651 | 0.0099612 | 0.0059516 | 0.062461 | 0.0025613 | 0.073309 | -59.7931 | 62.5992 | -60.2417 | -60.3241 | 55.9341 | -3.8177 | -20.2423 | -19.162 | 62.6404 | -60.3058 | -0.10986 | -0.11444 | 0.33875 | -0.19226 | -6.7795 | -0.17395 | -0.073242 | 0.44861 | 39.8895 | 40.9698 | 116.066 | 122.731 | 0.33875 | 122.7722 | 56.3141 | -0.17395 | 122.731 | 0.33875 | 56.3141 | 116.066 | 122.7722 | -122.9553 | -123.0194
726.3281 | 123.1064 | -60.1364 | 62.7274 | -0.20248 | 0.018797 | 0.012525 | 0.0042426 | 0.062461 | 0.0010659 | 0.075018 | -59.7794 | 62.5946 | -60.2509 | -60.2921 | 55.9067 | -3.7537 | -20.1874 | -19.0109 | 62.6404 | -60.2783 | -0.11444 | -0.13275 | 0.35706 | -0.15564 | -6.8207 | -0.14191 | -0.086975 | 0.4715 | 39.949 | 41.1255 | 116.0431 | 122.731 | 0.35706 | 122.7768 | 56.3828 | -0.14191 | 122.731 | 0.35706 | 56.3828 | 116.0431 | 122.7768 | -122.9782 | -123.0057
727.3281 | 123.024 | -60.1456 | 62.7274 | -0.14908 | 0.019865 | 0.0097476 | 0.007447 | 0.059257 | -0.00042929 | 0.076086 | -59.8068 | 62.6129 | -60.2371 | -60.3699 | 55.7831 | -3.5751 | -19.7433 | -18.7958 | 62.6495 | -60.3058 | -0.091553 | -0.11444 | 0.33875 | -0.2243 | -6.9443 | -0.16022 | -0.07782 | 0.4303 | 40.4022 | 41.3498 | 115.9287 | 122.7585 | 0.33875 | 122.7951 | 56.5704 | -0.16022 | 122.7585 | 0.33875 | 56.5704 | 115.9287 | 122.7951 | -122.9645 | -123.0331
728.3281 | 123.0469 | -60.1456 | 62.709 | -0.22537 | 0.017088 | 0.010388 | 0.0061652 | 0.059257 | -0.0012839 | 0.073736 | -59.7931 | 62.5854 | -60.2234 | -60.3287 | 55.7236 | -3.4973 | -19.5602 | -18.5349 | 62.6541 | -60.3012 | -0.07782 | -0.1236 | 0.35248 | -0.1831 | -6.9855 | -0.15564 | -0.054931 | 0.4303 | 40.5853 | 41.6107 | 115.8691 | 122.731 | 0.35248 | 122.7997 | 56.6483 | -0.15564 | 122.731 | 0.35248 | 56.6483 | 115.8691 | 122.7997 | -122.9324 | -123.0103
729.3281 | 123.0652 | -60.1181 | 62.7228 | -0.20248 | 0.019865 | 0.014234 | 0.006806 | 0.062461 | -0.0014975 | 0.076513 | -59.7748 | 62.5671 | -60.2417 | -60.3149 | 55.6915 | -3.4287 | -19.4824 | -18.425 | 62.6633 | -60.3195 | -0.1236 | -0.15564 | 0.34332 | -0.19684 | -7.0312 | -0.20142 | -0.059509 | 0.46692 | 40.6357 | 41.6931 | 115.8096 | 122.6852 | 0.34332 | 122.7814 | 56.6895 | -0.20142 | 122.6852 | 0.34332 | 56.6895 | 115.8096 | 122.7814 | -122.9645 | -123.0423
730.3281 | 123.1293 | -60.1364 | 62.6907 | -0.19485 | 0.016874 | 0.012738 | 0.0070196 | 0.062034 | -0.0034201 | 0.074804 | -59.7427 | 62.5671 | -60.2325 | -60.2783 | 55.6824 | -3.5156 | -19.4046 | -18.2922 | 62.645 | -60.2692 | -0.09613 | -0.1236 | 0.39368 | -0.14191 | -7.0084 | -0.13275 | -0.045777 | 0.48981 | 40.7318 | 41.8442 | 115.8188 | 122.7036 | 0.39368 | 122.7814 | 56.6208 | -0.13275 | 122.7036 | 0.39368 | 56.6208 | 115.8188 | 122.7814 | -122.9233 | -122.9599
731.3281 | 123.1979 | -60.1456 | 62.645 | -0.11093 | 0.018156 | 0.010816 | 0.0031744 | 0.060966 | -0.00085669 | 0.076727 | -59.7107 | 62.5259 | -60.2325 | -60.26 | 55.6778 | -3.6484 | -18.9835 | -18.4708 | 62.6724 | -60.26 | -0.086975 | -0.11902 | 0.43488 | -0.11444 | -6.9672 | -0.11444 | 0.027466 | 0.52185 | 41.1621 | 41.6748 | 115.8234 | 122.6715 | 0.43488 | 122.818 | 56.4972 | -0.11444 | 122.6715 | 0.43488 | 56.4972 | 115.8234 | 122.818 | -122.8775 | -122.905
732.3281 | 123.1338 | -60.1318 | 62.677 | -0.042267 | 0.01837 | 0.0080386 | 0.003388 | 0.059471 | -0.0010703 | 0.077368 | -59.7107 | 62.5671 | -60.2463 | -60.2921 | 55.6183 | -3.6987 | -19.281 | -18.0542 | 62.5717 | -60.2875 | -0.11444 | -0.10986 | 0.42114 | -0.16022 | -7.0587 | -0.15564 | -0.10529 | 0.53558 | 40.8508 | 42.0776 | 115.7501 | 122.699 | 0.42114 | 122.7036 | 56.4331 | -0.15564 | 122.699 | 0.42114 | 56.4331 | 115.7501 | 122.7036 | -122.9233 | -122.9645
733.3281 | 123.0881 | -60.1227 | 62.6907 | -0.17197 | 0.018156 | 0.0071842 | 0.0089422 | 0.059257 | -0.0017111 | 0.076727 | -59.7107 | 62.5488 | -60.2463 | -60.2966 | 55.5771 | -3.9001 | -19.2352 | -18.0542 | 62.6221 | -60.2737 | -0.1236 | -0.14191 | 0.41199 | -0.17395 | -7.1136 | -0.15106 | -0.068665 | 0.53558 | 40.8875 | 42.0685 | 115.6998 | 122.6715 | 0.41199 | 122.7448 | 56.2225 | -0.15106 | 122.6715 | 0.41199 | 56.2225 | 115.6998 | 122.7448 | -122.937 | -122.9645
734.3281 | 123.1384 | -60.0906 | 62.6724 | -0.16434 | 0.017515 | 0.0069706 | 0.0048834 | 0.060966 | -0.0019247 | 0.075018 | -59.6924 | 62.5442 | -60.2188 | -60.2463 | 55.5496 | -3.9734 | -19.2856 | -18.0862 | 62.6404 | -60.26 | -0.12817 | -0.12817 | 0.39825 | -0.15564 | -7.1228 | -0.16937 | -0.032043 | 0.52643 | 40.8051 | 42.0044 | 115.6403 | 122.6349 | 0.39825 | 122.731 | 56.1172 | -0.16937 | 122.6349 | 0.39825 | 56.1172 | 115.6403 | 122.731 | -122.8912 | -122.9324
735.3281 | 123.111 | -60.0952 | 62.7136 | -0.19485 | 0.018583 | 0.0099612 | 0.007447 | 0.061393 | -0.00085669 | 0.075873 | -59.6695 | 62.5626 | -60.2005 | -60.26 | 55.5084 | -4.1519 | -19.3359 | -18.0725 | 62.6083 | -60.2554 | -0.10528 | -0.15106 | 0.42572 | -0.16479 | -7.2052 | -0.16022 | -0.10529 | 0.53101 | 40.7593 | 42.0227 | 115.6036 | 122.6578 | 0.42572 | 122.7036 | 55.9433 | -0.16022 | 122.6578 | 0.42572 | 55.9433 | 115.6036 | 122.7036 | -122.9141 | -122.9691
736.3281 | 123.1155 | -60.1135 | 62.6907 | 3.2994 | 0.018156 | 0.010388 | 0.0061652 | 0.060111 | -0.0017111 | 0.075659 | -59.6054 | 62.5854 | -60.2188 | -60.2371 | 55.481 | -4.216 | -19.4092 | -18.0725 | 62.645 | -60.2509 | -0.10529 | -0.10529 | 0.50812 | -0.1236 | -7.2098 | -0.13733 | -0.045777 | 0.6134 | 40.7043 | 42.041 | 115.5945 | 122.699 | 0.50812 | 122.7585 | 55.8975 | -0.13733 | 122.699 | 0.50812 | 55.8975 | 115.5945 | 122.7585 | -122.9095 | -122.9416
737.3281 | 123.1247 | -60.1135 | 62.677 | -0.11856 | 0.018583 | 0.0093204 | 0.0042426 | 0.060966 | -0.00042929 | 0.075873 | -59.6466 | 62.5717 | -60.2325 | -60.2371 | 55.3528 | -4.1336 | -19.5007 | -18.6127 | 62.6541 | -60.2554 | -0.11902 | -0.10529 | 0.46692 | -0.1236 | -7.3242 | -0.14191 | -0.022888 | 0.58594 | 40.6128 | 41.5009 | 115.4663 | 122.6852 | 0.46692 | 122.7676 | 55.9799 | -0.14191 | 122.6852 | 0.46692 | 55.9799 | 115.4663 | 122.7676 | -122.9095 | -122.9324
738.3281 | 123.1064 | -60.1227 | 62.6907 | 0.0035097 | 0.01837 | 0.012738 | 0.0053106 | 0.060325 | -0.0014975 | 0.074377 | -59.7061 | 62.5671 | -60.228 | -60.2966 | 55.3619 | -4.5593 | -19.4687 | -18.1503 | 62.6038 | -60.2829 | -0.10529 | -0.1236 | 0.41656 | -0.17395 | -7.3288 | -0.16022 | -0.086975 | 0.52185 | 40.654 | 41.9724 | 115.4846 | 122.6898 | 0.41656 | 122.7264 | 55.5634 | -0.16022 | 122.6898 | 0.41656 | 55.5634 | 115.4846 | 122.7264 | -122.9187 | -122.9736
739.3438 | 123.0103 | -60.1456 | 62.7686 | -0.82047 | 0.020506 | 0.01167 | 0.011719 | 0.06182 | -0.00042929 | 0.077154 | -59.7656 | 62.677 | -60.2188 | -60.3424 | 55.2612 | -4.7745 | -19.3268 | -18.2831 | 62.6633 | -60.2966 | -0.073242 | -0.091553 | 0.37994 | -0.19684 | -7.5073 | -0.15106 | -0.10529 | 0.45319 | 40.8188 | 41.8625 | 115.4068 | 122.8226 | 0.37994 | 122.8088 | 55.3711 | -0.15106 | 122.8226 | 0.37994 | 55.3711 | 115.4068 | 122.8088 | -122.9874 | -123.0652
740.3281 | 123.3261 | -60.0677 | 62.7594 | -0.057526 | 0.018583 | 0.0093204 | 0.0059516 | 0.058402 | -0.00021569 | 0.075232 | -59.61 | 62.5671 | -60.1868 | -60.228 | 55.3528 | -4.8019 | -19.606 | -18.2144 | 62.6129 | -60.2509 | -0.11902 | -0.19226 | 0.45776 | -0.16022 | -7.4066 | -0.1831 | -0.14648 | 0.57678 | 40.4617 | 41.8533 | 115.4205 | 122.6349 | 0.45776 | 122.6807 | 55.2658 | -0.1831 | 122.6349 | 0.45776 | 55.2658 | 115.4205 | 122.6807 | -122.9462 | -123.0103
741.3281 | 123.1659 | -60.0906 | 62.6999 | -0.027008 | 0.019651 | 0.0088932 | 0.006806 | 0.059471 | -0.00042929 | 0.075232 | -59.6283 | 62.5671 | -60.2051 | -60.2509 | 55.3482 | -5.0125 | -19.5969 | -18.2373 | 62.6175 | -60.2371 | -0.11444 | -0.13275 | 0.46234 | -0.16022 | -7.3517 | -0.14648 | -0.082397 | 0.57678 | 40.4938 | 41.8533 | 115.4388 | 122.6578 | 0.46234 | 122.7081 | 55.0781 | -0.14648 | 122.6578 | 0.46234 | 55.0781 | 115.4388 | 122.7081 | -122.905 | -122.937
742.3281 | 123.143 | -60.0952 | 62.677 | 0.0035097 | 0.019438 | 0.0088932 | 0.005738 | 0.060111 | 0.0014933 | 0.078222 | -59.6283 | 62.5717 | -60.2097 | -60.2783 | 55.3253 | -5.2643 | -19.6609 | -18.338 | 62.6175 | -60.2371 | -0.11444 | -0.10529 | 0.46692 | -0.1831 | -7.3517 | -0.14191 | -0.059509 | 0.58136 | 40.4343 | 41.7572 | 115.4205 | 122.6669 | 0.46692 | 122.7127 | 54.8309 | -0.14191 | 122.6669 | 0.46692 | 54.8309 | 115.4205 | 122.7127 | -122.8867 | -122.9141
743.3281 | 123.1247 | -60.1089 | 62.6999 | 0.049286 | 0.017729 | 0.012097 | 0.0063788 | 0.05883 | -0.0010703 | 0.076941 | -59.6375 | 62.5809 | -60.2234 | -60.3104 | 55.2933 | -5.5252 | -19.7571 | -18.425 | 62.6083 | -60.26 | -0.11444 | -0.11902 | 0.4715 | -0.20142 | -7.4066 | -0.15106 | -0.091553 | 0.58594 | 40.3519 | 41.684 | 115.4022 | 122.6898 | 0.4715 | 122.7173 | 54.5837 | -0.15106 | 122.6898 | 0.4715 | 54.5837 | 115.4022 | 122.7173 | -122.9233 | -122.9599
744.3438 | 123.0377 | -60.1227 | 62.7548 | -0.78995 | 0.022642 | 0.016156 | 0.012787 | 0.063743 | -0.0025657 | 0.075445 | -59.5688 | 62.6907 | -60.2005 | -60.2646 | 55.2887 | -5.8136 | -19.7433 | -18.457 | 62.6541 | -60.3104 | -0.077819 | -0.064087 | 0.55389 | -0.14191 | -7.4661 | -0.18768 | -0.10071 | 0.63171 | 40.3793 | 41.6656 | 115.4114 | 122.8134 | 0.55389 | 122.7768 | 54.3091 | -0.18768 | 122.8134 | 0.55389 | 54.3091 | 115.4114 | 122.7768 | -122.9553 | -123.0652
745.3281 | 123.0606 | -60.1364 | 62.7045 | 0.17136 | 0.017729 | 0.014447 | 0.0053106 | 0.061393 | -0.0010703 | 0.076941 | -59.61 | 62.5442 | -60.2142 | -60.3333 | 55.3116 | -6.0699 | -19.8898 | -18.5074 | 62.6175 | -60.2371 | -0.077819 | -0.16022 | 0.52643 | -0.19684 | -7.3929 | -0.10071 | -0.086975 | 0.60425 | 40.2466 | 41.629 | 115.448 | 122.6807 | 0.52643 | 122.7539 | 54.0665 | -0.10071 | 122.6807 | 0.52643 | 54.0665 | 115.448 | 122.7539 | -122.9187 | -122.9416
746.3281 | 122.9828 | -60.1776 | 62.6587 | 0.1561 | 0.019224 | 0.011884 | 0.005738 | 0.06118 | -0.00042929 | 0.075232 | -59.6786 | 62.5122 | -60.3012 | -60.3928 | 55.3116 | -4.0512 | -17.3767 | -16.0446 | 62.558 | -60.3195 | -0.1236 | -0.14648 | 0.49896 | -0.21515 | -7.3471 | -0.14191 | -0.10071 | 0.62256 | 42.8009 | 44.133 | 115.4892 | 122.6898 | 0.49896 | 122.7356 | 56.1264 | -0.14191 | 122.6898 | 0.49896 | 56.1264 | 115.4892 | 122.7356 | -122.9599 | -122.9782
747.3281 | 123.1064 | -60.2005 | 62.6587 | 0.72067 | 0.019865 | 0.0097476 | 0.0070196 | 0.058189 | 0.00063871 | 0.076727 | -59.6375 | 62.5076 | -60.2737 | -60.3836 | 55.2612 | -3.7903 | -16.9647 | -15.7242 | 62.5397 | -60.347 | -0.073243 | -0.15106 | 0.56305 | -0.18311 | -7.3975 | -0.14648 | -0.11902 | 0.63629 | 43.2358 | 44.4763 | 115.4617 | 122.7081 | 0.56305 | 122.7402 | 56.4102 | -0.14648 | 122.7081 | 0.56305 | 56.4102 | 115.4617 | 122.7402 | -122.9324 | -123.0057
748.3281 | 123.0835 | -60.2142 | 62.6358 | 0.11795 | 0.018156 | 0.0091068 | 0.0065924 | 0.058402 | -0.00042929 | 0.078222 | -59.6603 | 62.5031 | -60.3058 | -60.1593 | 55.2887 | -3.7811 | -16.5894 | -15.5411 | 62.5031 | -60.3561 | -0.091553 | -0.13275 | 0.55389 | 0.054931 | -7.3471 | -0.14191 | -0.13275 | 0.64545 | 43.6249 | 44.6732 | 115.5029 | 122.7173 | 0.55389 | 122.7173 | 56.4331 | -0.14191 | 122.7173 | 0.55389 | 56.4331 | 115.5029 | 122.7173 | -122.9416 | -122.9919
749.3438 | 122.9874 | -60.2097 | 62.6862 | -0.14145 | 0.021574 | 0.01402 | 0.011292 | 0.057975 | -0.0025657 | 0.076727 | -59.6512 | 62.6038 | -60.2966 | -60.4019 | 55.2017 | -3.3279 | -16.3101 | -15.5136 | 62.6038 | -60.3745 | -0.086975 | -0.082397 | 0.55847 | -0.19226 | -7.4844 | -0.16479 | -0.082397 | 0.64545 | 43.8995 | 44.696 | 115.4114 | 122.8134 | 0.55847 | 122.8134 | 56.8817 | -0.16479 | 122.8134 | 0.55847 | 56.8817 | 115.4114 | 122.8134 | -122.9828 | -123.0606
750.3281 | 123.0789 | -60.1913 | 62.6083 | 0.19424 | 0.019865 | 0.0073978 | 0.007447 | 0.060111 | -0.0021383 | 0.077368 | -59.6054 | 62.4756 | -60.3012 | -60.3973 | 55.1559 | -3.4241 | -16.2781 | -15.1291 | 62.5214 | -60.3378 | -0.10986 | -0.13275 | 0.58594 | -0.20599 | -7.4524 | -0.14648 | -0.086975 | 0.6958 | 43.9133 | 45.0623 | 115.3473 | 122.6669 | 0.58594 | 122.7127 | 56.7673 | -0.14648 | 122.6669 | 0.58594 | 56.7673 | 115.3473 | 122.7127 | -122.9095 | -122.9462
751.3281 | 123.1476 | -60.2005 | 62.6083 | -1.1104 | 0.020719 | 0.013379 | 0.011719 | 0.060752 | -0.0010703 | 0.0763 | -59.6283 | 62.5122 | -60.3058 | -60.3745 | 55.1285 | -3.3829 | -16.1636 | -14.9872 | 62.4756 | -60.3745 | -0.10529 | -0.09613 | 0.5722 | -0.17395 | -7.4799 | -0.17395 | -0.13275 | 0.67749 | 44.0369 | 45.2133 | 115.329 | 122.7127 | 0.5722 | 122.6761 | 56.8176 | -0.17395 | 122.7127 | 0.5722 | 56.8176 | 115.329 | 122.6761 | -122.9141 | -122.9828
752.3281 | 123.1659 | -60.1959 | 62.5809 | 0.18662 | 0.020933 | 0.01637 | 0.011292 | 0.060539 | -0.00042929 | 0.076727 | -59.5688 | 62.4939 | -60.347 | -60.3653 | 55.1056 | -3.2639 | -16.1591 | -15.0787 | 62.4344 | -60.4294 | -0.15106 | -0.086976 | 0.62714 | -0.16937 | -7.4753 | -0.23346 | -0.14648 | 0.7782 | 44.0369 | 45.1172 | 115.3015 | 122.6898 | 0.62714 | 122.6303 | 56.9321 | -0.23346 | 122.6898 | 0.62714 | 56.9321 | 115.3015 | 122.6303 | -122.9279 | -123.0103
753.3281 | 123.1384 | -60.2188 | 62.5717 | -0.072784 | 0.022642 | 0.017011 | 0.010224 | 0.062034 | -0.0010703 | 0.078222 | -59.5917 | 62.4893 | -60.3149 | -60.3699 | 55.1147 | -3.1952 | -15.8066 | -14.6118 | 62.4893 | -60.379 | -0.09613 | -0.082397 | 0.62714 | -0.15106 | -7.457 | -0.16022 | -0.082397 | 0.72327 | 44.4122 | 45.607 | 115.3336 | 122.7081 | 0.62714 | 122.7081 | 57.0236 | -0.16022 | 122.7081 | 0.62714 | 57.0236 | 115.3336 | 122.7081 | -122.8867 | -122.9507
754.3438 | 123.0835 | -60.2188 | 62.6129 | -0.13382 | 0.019438 | 0.012311 | 0.0063788 | 0.057334 | -0.0021383 | 0.077368 | -59.5505 | 62.4985 | -60.2966 | -60.3653 | 55.1102 | -3.1357 | -15.5777 | -14.5065 | 62.5168 | -60.3607 | -0.07782 | -0.11444 | 0.66833 | -0.14648 | -7.5027 | -0.14191 | -0.09613 | 0.74615 | 44.6411 | 45.7123 | 115.329 | 122.7173 | 0.66833 | 122.7356 | 57.0831 | -0.14191 | 122.7173 | 0.66833 | 57.0831 | 115.329 | 122.7356 | -122.9095 | -122.9736
755.3281 | 123.1293 | -60.2325 | 62.558 | 0.11795 | 0.019651 | 0.014875 | 0.011079 | 0.059898 | 0.00021151 | 0.077582 | -59.5779 | 62.4756 | -60.3058 | -60.3836 | 55.0644 | -3.1998 | -15.7059 | -14.534 | 62.4481 | -60.4111 | -0.073242 | -0.082397 | 0.6546 | -0.15106 | -7.4936 | -0.17853 | -0.10986 | 0.72784 | 44.5267 | 45.6985 | 115.2969 | 122.7081 | 0.6546 | 122.6807 | 57.0328 | -0.17853 | 122.7081 | 0.6546 | 57.0328 | 115.2969 | 122.6807 | -122.8638 | -122.9691
756.3281 | 123.1247 | -60.228 | 62.558 | 0.24002 | 0.02136 | 0.013166 | 0.01001 | 0.059471 | -0.0012839 | 0.077582 | -59.5551 | 62.4985 | -60.3333 | -60.3973 | 55.101 | -3.1906 | -15.6418 | -14.4562 | 62.4344 | -60.4065 | -0.10529 | -0.059509 | 0.67291 | -0.16937 | -7.457 | -0.17853 | -0.1236 | 0.7782 | 44.5862 | 45.7718 | 115.329 | 122.7264 | 0.67291 | 122.6624 | 57.0374 | -0.17853 | 122.7264 | 0.67291 | 57.0374 | 115.329 | 122.6624 | -122.8912 | -122.9645
757.3281 | 123.111 | -60.2509 | 62.5671 | 0.18662 | 0.021147 | 0.013379 | 0.012147 | 0.061607 | -0.0014975 | 0.081 | -59.5505 | 62.5076 | -60.3516 | -60.4156 | 54.982 | -3.1082 | -15.4449 | -14.36 | 62.4573 | -60.4111 | -0.10071 | -0.05951 | 0.70038 | -0.1648 | -7.5851 | -0.16022 | -0.10986 | 0.80109 | 44.8059 | 45.8908 | 115.2328 | 122.7585 | 0.70038 | 122.7081 | 57.1426 | -0.16022 | 122.7585 | 0.70038 | 57.1426 | 115.2328 | 122.7081 | -122.9187 | -122.9782
758.3438 | 123.0377 | -60.1868 | 62.6495 | -0.20248 | 0.016874 | 0.012525 | 0.0070196 | 0.059257 | -0.00042929 | 0.077582 | -59.5184 | 62.4847 | -60.3195 | -60.3699 | 55.0323 | -2.9892 | -15.2618 | -14.1541 | 62.4893 | -60.3836 | -0.13275 | -0.16479 | 0.66833 | -0.1831 | -7.6172 | -0.19684 | -0.16022 | 0.80109 | 44.9249 | 46.0327 | 115.2191 | 122.6715 | 0.66833 | 122.6761 | 57.1976 | -0.19684 | 122.6715 | 0.66833 | 57.1976 | 115.2191 | 122.6761 | -122.9691 | -123.0331
759.3281 | 122.9965 | -60.2875 | 62.5671 | 0.29343 | 0.023069 | 0.014661 | 0.013642 | 0.059684 | -2.092e-06 | 0.079077 | -59.6146 | 62.5442 | -60.3928 | -60.5255 | 54.8538 | -3.0029 | -14.9963 | -14.2181 | 62.471 | -60.498 | -0.10529 | -0.022889 | 0.67291 | -0.23804 | -7.7133 | -0.21057 | -0.096131 | 0.7782 | 45.2911 | 46.0693 | 115.1413 | 122.8317 | 0.67291 | 122.7585 | 57.2845 | -0.21057 | 122.8317 | 0.67291 | 57.2845 | 115.1413 | 122.7585 | -122.9599 | -123.0652
760.3281 | 123.0606 | -60.2875 | 62.558 | 0.22476 | 0.020933 | 0.014234 | 0.012574 | 0.06182 | 0.00021151 | 0.077582 | -59.61 | 62.5397 | -60.3836 | -60.5209 | 54.8447 | -2.9938 | -14.9139 | -14.1449 | 62.5031 | -60.4706 | -0.09613 | -0.01831 | 0.67749 | -0.23346 | -7.7133 | -0.18311 | -0.054931 | 0.77362 | 45.3735 | 46.1426 | 115.1321 | 122.8271 | 0.67749 | 122.7905 | 57.2937 | -0.18311 | 122.8271 | 0.67749 | 57.2937 | 115.1321 | 122.7905 | -122.9416 | -123.0286
761.3281 | 123.0652 | -60.2509 | 62.5214 | 0.23239 | 0.023283 | 0.014875 | 0.010651 | 0.062248 | -0.00064309 | 0.079077 | -59.5779 | 62.5122 | -60.3928 | -60.4752 | 54.8492 | -3.1082 | -14.9918 | -14.09 | 62.4573 | -60.4568 | -0.14191 | -0.009155 | 0.67291 | -0.22431 | -7.6721 | -0.20599 | -0.064087 | 0.81482 | 45.2591 | 46.1609 | 115.1001 | 122.7631 | 0.67291 | 122.7081 | 57.1426 | -0.20599 | 122.7631 | 0.67291 | 57.1426 | 115.1001 | 122.7081 | -122.9141 | -122.9782
762.3281 | 123.0377 | -60.2783 | 62.5671 | 0.2095 | 0.023924 | 0.015515 | 0.010865 | 0.063102 | 0.00021151 | 0.079077 | -59.6008 | 62.5397 | -60.4111 | -60.498 | 54.8126 | -3.241 | -14.9414 | -14.1724 | 62.4527 | -60.4752 | -0.13275 | -0.027466 | 0.67749 | -0.21973 | -7.7545 | -0.19684 | -0.11444 | 0.81024 | 45.3369 | 46.106 | 115.0909 | 122.818 | 0.67749 | 122.731 | 57.0374 | -0.19684 | 122.818 | 0.67749 | 57.0374 | 115.0909 | 122.731 | -122.9782 | -123.0423
763.3281 | 123.0286 | -60.3012 | 62.5442 | 0.20187 | 0.022428 | 0.011884 | 0.013428 | 0.062461 | 0.0012795 | 0.078009 | -59.5871 | 62.5351 | -60.4019 | -60.5347 | 54.7623 | -3.2867 | -14.8819 | -14.209 | 62.4664 | -60.4889 | -0.10071 | -0.009155 | 0.71411 | -0.23346 | -7.782 | -0.18768 | -0.077819 | 0.81482 | 45.4193 | 46.0922 | 115.0635 | 122.8363 | 0.71411 | 122.7676 | 57.0145 | -0.18768 | 122.8363 | 0.71411 | 57.0145 | 115.0635 | 122.7676 | -122.9462 | -123.0331
764.3281 | 123.0377 | -60.2966 | 62.5488 | 0.1561 | 0.021147 | 0.01402 | 0.011506 | 0.063102 | 0.00042511 | 0.080145 | -59.5825 | 62.5305 | -60.4248 | -60.5392 | 54.7485 | -3.1769 | -14.6393 | -14.0488 | 62.4756 | -60.5026 | -0.12817 | -0.01831 | 0.71411 | -0.24262 | -7.8003 | -0.20599 | -0.073242 | 0.84228 | 45.6573 | 46.2479 | 115.0452 | 122.8271 | 0.71411 | 122.7722 | 57.1198 | -0.20599 | 122.8271 | 0.71411 | 57.1198 | 115.0452 | 122.7722 | -122.9736 | -123.0515
765.3281 | 122.9874 | -60.2921 | 62.5671 | 0.11795 | 0.024137 | 0.013166 | 0.0095832 | 0.065879 | -0.00021569 | 0.076086 | -59.5825 | 62.5671 | -60.4111 | -60.5667 | 54.7623 | -3.1769 | -14.5065 | -13.9893 | 62.4664 | -60.5164 | -0.11902 | 0 | 0.70953 | -0.27466 | -7.8049 | -0.2243 | -0.10071 | 0.82855 | 45.7855 | 46.3028 | 115.0543 | 122.8592 | 0.70953 | 122.7585 | 57.1152 | -0.2243 | 122.8592 | 0.70953 | 57.1152 | 115.0543 | 122.7585 | -122.9782 | -123.0835
766.3281 | 123.0011 | -60.3012 | 62.5488 | 0.079804 | 0.022856 | 0.012738 | 0.011719 | 0.062034 | 0.0014933 | 0.078436 | -59.5688 | 62.5351 | -60.4248 | -60.5301 | 54.7531 | -3.1448 | -14.4424 | -13.9618 | 62.4756 | -60.5072 | -0.1236 | -0.013733 | 0.73242 | -0.22888 | -7.7957 | -0.20599 | -0.073242 | 0.85602 | 45.8588 | 46.3394 | 115.0543 | 122.8363 | 0.73242 | 122.7768 | 57.1564 | -0.20599 | 122.8363 | 0.73242 | 57.1564 | 115.0543 | 122.7768 | -122.9736 | -123.056
767.3281 | 122.9736 | -60.2966 | 62.5442 | 0.14847 | 0.021787 | 0.016156 | 0.011292 | 0.06417 | 0.0038431 | 0.085699 | -59.5688 | 62.5717 | -60.4294 | -60.9741 | 54.5471 | -2.9984 | -14.4836 | -14.003 | 62.5031 | -60.5072 | -0.13275 | 0.027466 | 0.72784 | -0.67749 | -7.9971 | -0.21057 | -0.041198 | 0.86059 | 45.813 | 46.2936 | 114.8438 | 122.8683 | 0.72784 | 122.7997 | 57.2983 | -0.21057 | 122.8683 | 0.72784 | 57.2983 | 114.8438 | 122.7997 | -122.9736 | -123.0515
768.3281 | 123.0194 | -60.3012 | 62.5442 | 0.17136 | 0.024137 | 0.016584 | 0.0095832 | 0.062889 | 0.00042511 | 0.081854 | -59.5688 | 62.5626 | -60.4111 | -60.5667 | 54.6982 | -3.2639 | -14.3921 | -13.9938 | 62.4847 | -60.4889 | -0.10986 | 0.018311 | 0.73242 | -0.2655 | -7.8461 | -0.18768 | -0.059509 | 0.84228 | 45.9091 | 46.3074 | 114.9994 | 122.8638 | 0.73242 | 122.7859 | 57.0374 | -0.18768 | 122.8638 | 0.73242 | 57.0374 | 114.9994 | 122.7859 | -122.9553 | -123.0331
769.3281 | 122.9919 | -60.3104 | 62.5946 | -0.96542 | 0.022642 | 0.017652 | 0.0089422 | 0.064598 | 0.0019205 | 0.079718 | -59.5734 | 62.5763 | -60.3928 | -60.5621 | 54.689 | -3.3371 | -14.36 | -14.0717 | 62.4847 | -60.5072 | -0.082397 | -0.01831 | 0.737 | -0.25177 | -7.9056 | -0.19684 | -0.10986 | 0.8194 | 45.9503 | 46.2387 | 114.9994 | 122.8867 | 0.737 | 122.7951 | 56.9733 | -0.19684 | 122.8867 | 0.737 | 56.9733 | 114.9994 | 122.7951 | -122.9874 | -123.1018
770.3281 | 123.0057 | -60.2783 | 62.5763 | 0.11795 | 0.024565 | 0.011243 | 0.011292 | 0.062675 | 0.00042511 | 0.080786 | -59.5139 | 62.5763 | -60.4019 | -60.5164 | 54.6799 | -3.3646 | -14.2548 | -14.0167 | 62.5076 | -60.5072 | -0.1236 | 0 | 0.76447 | -0.23804 | -7.8964 | -0.22888 | -0.068665 | 0.88806 | 46.0236 | 46.2616 | 114.9582 | 122.8546 | 0.76447 | 122.7859 | 56.9138 | -0.22888 | 122.8546 | 0.76447 | 56.9138 | 114.9582 | 122.7859 | -122.9782 | -123.0835
771.3281 | 123.0469 | -60.3287 | 62.5717 | 0.10269 | 0.022428 | 0.017011 | 0.011079 | 0.070152 | 0.0025613 | 0.077368 | -59.5734 | 62.5626 | -60.4065 | -60.3882 | 54.9866 | -3.2959 | -14.0717 | -13.8199 | 62.5214 | -60.5072 | -0.07782 | -0.009155 | 0.75531 | -0.05951 | -7.5851 | -0.17853 | -0.050354 | 0.83313 | 46.257 | 46.5088 | 115.3152 | 122.8912 | 0.75531 | 122.85 | 57.0328 | -0.17853 | 122.8912 | 0.75531 | 57.0328 | 115.3152 | 122.85 | -122.9782 | -123.0789
772.3281 | 123.0286 | -60.2966 | 62.5671 | 0.0035097 | 0.023069 | 0.018933 | 0.011719 | 0.063529 | 0.0036295 | 0.081213 | -59.523 | 62.5809 | -60.3973 | -60.5118 | 54.657 | -3.3096 | -13.9801 | -13.8199 | 62.4756 | -60.5026 | -0.10071 | 0.013733 | 0.77362 | -0.21515 | -7.9102 | -0.20599 | -0.091553 | 0.87433 | 46.3165 | 46.4767 | 114.9536 | 122.8775 | 0.77362 | 122.7722 | 56.987 | -0.20599 | 122.8775 | 0.77362 | 56.987 | 114.9536 | 122.7722 | -122.9645 | -123.0698
773.3281 | 123.0515 | -60.2921 | 62.5671 | 0.011139 | 0.024992 | 0.017224 | 0.011719 | 0.062889 | 0.0032021 | 0.082068 | -59.5047 | 62.5809 | -60.3928 | -60.5209 | 54.6341 | -3.2272 | -13.8382 | -13.71 | 62.4893 | -60.5164 | -0.10071 | 0.013733 | 0.78735 | -0.22888 | -7.933 | -0.2243 | -0.07782 | 0.88806 | 46.4539 | 46.582 | 114.9261 | 122.8729 | 0.78735 | 122.7814 | 57.0648 | -0.2243 | 122.8729 | 0.78735 | 57.0648 | 114.9261 | 122.7814 | -122.9599 | -123.0835
774.3281 | 122.9874 | -60.2966 | 62.5992 | 0.087433 | 0.025205 | 0.015515 | 0.010865 | 0.062461 | -0.0014975 | 0.080786 | -59.5322 | 62.5488 | -60.4111 | -60.5347 | 54.5609 | -3.2043 | -13.5681 | -13.5452 | 62.5031 | -60.5255 | -0.11444 | -0.050354 | 0.76447 | -0.23804 | -8.0383 | -0.22888 | -0.09613 | 0.87891 | 46.7285 | 46.7514 | 114.8575 | 122.8455 | 0.76447 | 122.7997 | 57.0923 | -0.22888 | 122.8455 | 0.76447 | 57.0923 | 114.8575 | 122.7997 | -123.0103 | -123.1247
775.3281 | 123.0148 | -60.3241 | 62.5534 | -0.35507 | 0.020506 | 0.016584 | 0.010438 | 0.063957 | 0.00085231 | 0.079931 | -59.4086 | 62.5626 | -60.379 | -60.5804 | 54.5013 | -3.2181 | -13.559 | -13.4857 | 62.4893 | -60.4935 | -0.054931 | 0.009155 | 0.91553 | -0.25635 | -8.0521 | -0.16937 | -0.064087 | 0.97046 | 46.7651 | 46.8384 | 114.8254 | 122.8867 | 0.91553 | 122.8134 | 57.106 | -0.16937 | 122.8867 | 0.91553 | 57.106 | 114.8254 | 122.8134 | -122.9324 | -123.0469
776.3281 | 123.0286 | -60.2875 | 62.5534 | 0.18662 | 0.019438 | 0.019574 | 0.0087286 | 0.060111 | 0.0021341 | 0.080572 | -59.5779 | 62.5763 | -60.4111 | -60.585 | 54.5837 | -3.1952 | -13.5498 | -13.4628 | 62.5214 | -60.5072 | -0.1236 | 0.022888 | 0.70953 | -0.29755 | -7.9697 | -0.21973 | -0.032044 | 0.83313 | 46.7377 | 46.8246 | 114.8712 | 122.8638 | 0.70953 | 122.8088 | 57.0923 | -0.21973 | 122.8638 | 0.70953 | 57.0923 | 114.8712 | 122.8088 | -122.9645 | -123.0606
777.3281 | 123.0652 | -60.3058 | 62.5854 | 0.17136 | 0.024137 | 0.019147 | 0.010224 | 0.063957 | -0.00042929 | 0.080572 | -59.5505 | 62.5946 | -60.4202 | -60.5301 | 54.1763 | -3.6026 | -13.0234 | -13.1927 | 62.4802 | -60.4889 | -0.11444 | 0.009155 | 0.75531 | -0.2243 | -8.4091 | -0.18311 | -0.10528 | 0.86975 | 47.2824 | 47.113 | 114.4821 | 122.9004 | 0.75531 | 122.7859 | 56.7032 | -0.18311 | 122.9004 | 0.75531 | 56.7032 | 114.4821 | 122.7859 | -123.0057 | -123.0743
778.3281 | 122.8317 | -60.3378 | 62.5397 | 0.17899 | 0.022001 | 0.014447 | 0.010438 | 0.063102 | 0.0014933 | 0.079291 | -59.5505 | 62.5488 | -60.4019 | -60.5667 | 54.364 | -3.241 | -13.3484 | -13.4262 | 62.4893 | -60.5301 | -0.064087 | 0.009155 | 0.78735 | -0.22888 | -8.1757 | -0.19226 | -0.050354 | 0.85144 | 46.9894 | 46.9116 | 114.7018 | 122.8867 | 0.78735 | 122.8271 | 57.0969 | -0.19226 | 122.8867 | 0.78735 | 57.0969 | 114.7018 | 122.8271 | -122.9416 | -123.0698
779.3281 | 123.0286 | -60.2921 | 62.5442 | 0.064545 | 0.020506 | 0.015302 | 0.012574 | 0.064384 | 0.0010659 | 0.081427 | -59.5001 | 62.5442 | -60.4111 | -60.5072 | 54.4189 | -3.0624 | -13.2065 | -13.2019 | 62.5351 | -60.5026 | -0.11902 | 0 | 0.79193 | -0.21515 | -8.1253 | -0.21057 | -0.009155 | 0.91095 | 47.0856 | 47.0901 | 114.711 | 122.8363 | 0.79193 | 122.8271 | 57.2296 | -0.21057 | 122.8363 | 0.79193 | 57.2296 | 114.711 | 122.8271 | -122.9553 | -123.0469
780.3281 | 123.0606 | -60.2692 | 62.5763 | -0.042267 | 0.020933 | 0.013806 | 0.0087286 | 0.064598 | -0.0012839 | 0.082495 | -59.523 | 62.5534 | -60.3882 | -60.4706 | 54.4693 | -3.1311 | -13.1424 | -13.1378 | 62.5168 | -60.4568 | -0.11902 | -0.022888 | 0.74616 | -0.20142 | -8.107 | -0.18768 | -0.059509 | 0.86517 | 47.1268 | 47.1313 | 114.7385 | 122.8226 | 0.74616 | 122.7859 | 57.1381 | -0.18768 | 122.8226 | 0.74616 | 57.1381 | 114.7385 | 122.7859 | -122.9645 | -123.0331
781.3281 | 122.9919 | -60.3149 | 62.5626 | 0.087433 | 0.024137 | 0.014447 | 0.010651 | 0.063743 | 0.0012795 | 0.081854 | -59.5093 | 62.5626 | -60.3836 | -60.5484 | 54.3182 | -3.2181 | -12.9822 | -13.1516 | 62.5168 | -60.5118 | -0.068665 | 0 | 0.80566 | -0.23346 | -8.2443 | -0.19684 | -0.045776 | 0.87433 | 47.3328 | 47.1634 | 114.6332 | 122.8775 | 0.80566 | 122.8317 | 57.0969 | -0.19684 | 122.8775 | 0.80566 | 57.0969 | 114.6332 | 122.8317 | -122.9462 | -123.0743
782.3281 | 122.9965 | -60.3195 | 62.5626 | 0.12558 | 0.024351 | 0.016797 | 0.0063788 | 0.063102 | 0.0014933 | 0.079077 | -59.5505 | 62.558 | -60.4294 | -60.4843 | 54.3274 | -3.2318 | -12.7533 | -12.973 | 62.5214 | -60.5072 | -0.10986 | -0.004578 | 0.76904 | -0.16479 | -8.2352 | -0.18768 | -0.041199 | 0.87891 | 47.5662 | 47.3465 | 114.6469 | 122.8775 | 0.76904 | 122.8409 | 57.0877 | -0.18768 | 122.8775 | 0.76904 | 57.0877 | 114.6469 | 122.8409 | -122.9919 | -123.0698
783.3281 | 123.0057 | -60.3058 | 62.5717 | 0.041657 | 0.022856 | 0.012952 | 0.011506 | 0.065238 | 0.0029885 | 0.088476 | -59.5551 | 62.5671 | -60.4019 | -60.9741 | 53.9017 | -3.0441 | -12.6205 | -12.9272 | 62.5168 | -60.5164 | -0.096131 | -0.004577 | 0.75073 | -0.66833 | -8.67 | -0.21057 | -0.054931 | 0.84686 | 47.6852 | 47.3785 | 114.2075 | 122.8729 | 0.75073 | 122.8226 | 57.2617 | -0.21057 | 122.8729 | 0.75073 | 57.2617 | 114.2075 | 122.8226 | -122.9736 | -123.0881
784.3281 | 122.818 | -60.3333 | 62.4985 | 0.17899 | 0.02371 | 0.015729 | 0.011079 | 0.063957 | 0.0027749 | 0.083349 | -59.5139 | 62.5534 | -60.4248 | -60.5667 | 54.2084 | -3.1952 | -12.6434 | -12.854 | 62.5168 | -60.5164 | -0.091553 | 0.054932 | 0.8194 | -0.23346 | -8.2901 | -0.1831 | 0.018311 | 0.91095 | 47.6898 | 47.4792 | 114.5416 | 122.8867 | 0.8194 | 122.85 | 57.1381 | -0.1831 | 122.8867 | 0.8194 | 57.1381 | 114.5416 | 122.85 | -122.9233 | -123.0148
785.3281 | 122.9828 | -60.347 | 62.5259 | 0.10269 | 0.023924 | 0.018293 | 0.011292 | 0.062889 | 0.00085231 | 0.082281 | -59.3719 | 62.5122 | -60.466 | -60.6079 | 54.1443 | -3.2318 | -12.6022 | -12.8586 | 62.4573 | -60.5804 | -0.11902 | -0.013733 | 0.97504 | -0.26093 | -8.3817 | -0.23346 | -0.068665 | 1.0941 | 47.7448 | 47.4884 | 114.4913 | 122.8592 | 0.97504 | 122.8043 | 57.1152 | -0.23346 | 122.8592 | 0.97504 | 57.1152 | 114.4913 | 122.8043 | -122.9919 | -123.1064
786.3281 | 123.0331 | -60.3287 | 62.5351 | 0.026398 | 0.023069 | 0.015943 | 0.011719 | 0.067161 | -0.00085669 | 0.08164 | -59.3124 | 62.5168 | -60.4294 | -60.5255 | 54.1534 | -3.1952 | -12.6343 | -12.8265 | 62.4664 | -60.553 | -0.10071 | -0.01831 | 1.0162 | -0.19684 | -8.3817 | -0.22431 | -0.068664 | 1.1169 | 47.6944 | 47.5021 | 114.4821 | 122.8455 | 1.0162 | 122.7951 | 57.1335 | -0.22431 | 122.8455 | 1.0162 | 57.1335 | 114.4821 | 122.7951 | -122.9645 | -123.0881
787.3281 | 122.9965 | -60.347 | 62.5122 | 0.011139 | 0.024137 | 0.019147 | 0.012574 | 0.062675 | -0.00042929 | 0.082068 | -59.2529 | 62.5305 | -60.4385 | -60.5392 | 54.126 | -3.2227 | -12.561 | -12.8082 | 62.4847 | -60.5255 | -0.091553 | 0.018311 | 1.0941 | -0.19226 | -8.3862 | -0.17853 | -0.027466 | 1.1856 | 47.7859 | 47.5388 | 114.473 | 122.8775 | 1.0941 | 122.8317 | 57.1243 | -0.17853 | 122.8775 | 1.0941 | 57.1243 | 114.473 | 122.8317 | -122.9507 | -123.0377
788.3281 | 123.0103 | -60.3516 | 62.5305 | 0.087433 | 0.023283 | 0.018933 | 0.013642 | 0.06417 | 0.00085231 | 0.080572 | -59.2667 | 62.5305 | -60.4523 | -60.5621 | 54.1214 | -3.3417 | -12.5748 | -12.9272 | 62.4893 | -60.5392 | -0.10071 | 0 | 1.0849 | -0.21057 | -8.4091 | -0.18768 | -0.041199 | 1.1856 | 47.7768 | 47.4243 | 114.473 | 122.8821 | 1.0849 | 122.8409 | 57.0099 | -0.18768 | 122.8821 | 1.0849 | 57.0099 | 114.473 | 122.8409 | -122.9828 | -123.0698
789.3281 | 123.1293 | -60.3653 | 62.5259 | 0.095062 | 0.02606 | 0.019361 | 0.011933 | 0.06417 | 0.0010659 | 0.080145 | -59.2987 | 62.5626 | -60.4706 | -60.6308 | 54.0161 | -3.3875 | -12.561 | -13.2248 | 62.4435 | -60.5759 | -0.10529 | 0.036621 | 1.0666 | -0.2655 | -8.5098 | -0.21057 | -0.082398 | 1.1719 | 47.8043 | 47.1405 | 114.3814 | 122.9279 | 1.0666 | 122.8088 | 56.9778 | -0.21057 | 122.9279 | 1.0666 | 56.9778 | 114.3814 | 122.8088 | -122.9965 | -123.1018
790.3281 | 123.0011 | -60.347 | 62.5076 | 0.095062 | 0.025419 | 0.015943 | 0.013215 | 0.063529 | 0.0019205 | 0.081427 | -59.2712 | 62.5259 | -60.4385 | -60.6125 | 54.039 | -3.2822 | -12.4191 | -12.8998 | 62.4847 | -60.5484 | -0.091553 | 0.018311 | 1.0757 | -0.2655 | -8.4686 | -0.20142 | -0.022888 | 1.1673 | 47.9279 | 47.4472 | 114.386 | 122.8729 | 1.0757 | 122.8317 | 57.0648 | -0.20142 | 122.8729 | 1.0757 | 57.0648 | 114.386 | 122.8317 | -122.9462 | -123.056
791.3281 | 122.9782 | -60.3333 | 62.5214 | 0.14847 | 0.024137 | 0.013166 | 0.011719 | 0.065452 | 0.0019205 | 0.079931 | -59.2209 | 62.5214 | -60.4385 | -60.6033 | 53.9932 | -3.1998 | -12.3322 | -12.8265 | 62.4527 | -60.5713 | -0.10529 | 0 | 1.1124 | -0.27008 | -8.5281 | -0.23804 | -0.068664 | 1.2177 | 48.0011 | 47.5067 | 114.3265 | 122.8546 | 1.1124 | 122.7859 | 57.1335 | -0.23804 | 122.8546 | 1.1124 | 57.1335 | 114.3265 | 122.7859 | -122.9599 | -123.0927
792.3281 | 123.0148 | -60.3287 | 62.5488 | 0.11032 | 0.02371 | 0.015515 | 0.011933 | 0.063957 | -0.00021569 | 0.08164 | -59.2163 | 62.5214 | -60.4568 | -60.5804 | 53.9886 | -3.2043 | -12.2772 | -12.767 | 62.4481 | -60.5667 | -0.12817 | -0.027466 | 1.1124 | -0.25177 | -8.5602 | -0.23804 | -0.10071 | 1.2405 | 48.0515 | 47.5616 | 114.3173 | 122.85 | 1.1124 | 122.7768 | 57.1243 | -0.23804 | 122.85 | 1.1124 | 57.1243 | 114.3173 | 122.7768 | -123.0057 | -123.1155
793.3281 | 123.0698 | -60.3241 | 62.5259 | 0.18662 | 0.02371 | 0.017011 | 0.013215 | 0.064811 | 0.00042511 | 0.080359 | -59.1431 | 62.5305 | -60.4431 | -60.5209 | 54.0024 | -3.1311 | -12.2177 | -12.5565 | 62.471 | -60.5621 | -0.11902 | 0.004578 | 1.181 | -0.19684 | -8.5236 | -0.23804 | -0.054932 | 1.3 | 48.1064 | 47.7676 | 114.3265 | 122.8546 | 1.181 | 122.7951 | 57.193 | -0.23804 | 122.8546 | 1.181 | 57.193 | 114.3265 | 122.7951 | -122.9691 | -123.0881
794.3281 | 123.0194 | -60.3424 | 62.5076 | 0.018768 | 0.025205 | 0.015088 | 0.014496 | 0.062889 | -0.00042929 | 0.083136 | -59.1476 | 62.4939 | -60.4385 | -60.5576 | 53.9612 | -3.0533 | -12.0392 | -12.442 | 62.4573 | -60.5713 | -0.096131 | -0.013733 | 1.1948 | -0.21515 | -8.5464 | -0.22888 | -0.050354 | 1.2909 | 48.3032 | 47.9004 | 114.3036 | 122.8363 | 1.1948 | 122.7997 | 57.2891 | -0.22888 | 122.8363 | 1.1948 | 57.2891 | 114.3036 | 122.7997 | -122.9462 | -123.0789
795.3281 | 123.0423 | -60.3333 | 62.4985 | -0.034637 | 0.025846 | 0.019147 | 0.011506 | 0.063102 | 0.0027749 | 0.082068 | -59.1019 | 62.4939 | -60.4385 | -60.5347 | 53.9154 | -3.1036 | -12.0117 | -12.4558 | 62.4664 | -60.5621 | -0.10529 | -0.004578 | 1.2314 | -0.20142 | -8.5831 | -0.22888 | -0.032043 | 1.3367 | 48.3215 | 47.8775 | 114.2487 | 122.8271 | 1.2314 | 122.7997 | 57.2296 | -0.22888 | 122.8271 | 1.2314 | 57.2296 | 114.2487 | 122.7997 | -122.937 | -123.0606
796.3281 | 123.0103 | -60.347 | 62.5168 | 0.011139 | 0.024565 | 0.016797 | 0.015351 | 0.062461 | -0.00021569 | 0.082495 | -59.111 | 62.5031 | -60.4385 | -60.5667 | 53.8879 | -3.1769 | -11.9888 | -12.4878 | 62.4802 | -60.5759 | -0.091553 | -0.013733 | 1.236 | -0.21973 | -8.6288 | -0.22888 | -0.036621 | 1.3275 | 48.3582 | 47.8592 | 114.2349 | 122.85 | 1.236 | 122.8271 | 57.1701 | -0.22888 | 122.85 | 1.236 | 57.1701 | 114.2349 | 122.8271 | -122.9553 | -123.0927
797.3281 | 123.024 | -60.3424 | 62.5305 | 0.0035097 | 0.025846 | 0.018506 | 0.013642 | 0.063316 | 0.0025613 | 0.082495 | -59.0652 | 62.5351 | -60.4385 | -60.5438 | 53.8742 | -3.1128 | -11.8378 | -12.3184 | 62.4619 | -60.5804 | -0.096131 | 0.004577 | 1.2772 | -0.20142 | -8.6563 | -0.23804 | -0.068665 | 1.3733 | 48.5046 | 48.024 | 114.2166 | 122.8775 | 1.2772 | 122.8043 | 57.2296 | -0.23804 | 122.8775 | 1.2772 | 57.2296 | 114.2166 | 122.8043 | -122.9691 | -123.111
798.3281 | 123.0423 | -60.347 | 62.5351 | 0.011139 | 0.024565 | 0.016156 | 0.012147 | 0.06417 | -0.0010703 | 0.083349 | -59.0515 | 62.5305 | -60.4431 | -60.5392 | 53.8696 | -3.1082 | -11.8011 | -12.2452 | 62.4527 | -60.5667 | -0.09613 | -0.004577 | 1.2955 | -0.19226 | -8.6655 | -0.21973 | -0.082397 | 1.3916 | 48.5458 | 48.1018 | 114.2166 | 122.8775 | 1.2955 | 122.7997 | 57.2388 | -0.21973 | 122.8775 | 1.2955 | 57.2388 | 114.2166 | 122.7997 | -122.9782 | -123.1018
799.3281 | 123.056 | -60.3287 | 62.5076 | -1.2019 | 0.024778 | 0.017865 | 0.01236 | 0.064811 | -0.00042929 | 0.083349 | -59.0652 | 62.5076 | -60.4523 | -60.5026 | 53.8605 | -2.948 | -11.5906 | -12.0255 | 62.4664 | -60.5576 | -0.1236 | 0 | 1.2634 | -0.17395 | -8.6472 | -0.22888 | -0.041198 | 1.387 | 48.7381 | 48.3032 | 114.1891 | 122.8363 | 1.2634 | 122.7951 | 57.3807 | -0.22888 | 122.8363 | 1.2634 | 57.3807 | 114.1891 | 122.7951 | -122.9599 | -123.0652
800.3281 | 123.0515 | -60.3378 | 62.5214 | -0.14908 | 0.025633 | 0.016156 | 0.013856 | 0.064384 | 0.0019205 | 0.082708 | -59.0195 | 62.5305 | -60.4568 | -60.5438 | 53.8101 | -2.861 | -11.3754 | -11.8561 | 62.4847 | -60.5438 | -0.11902 | 0.009156 | 1.3184 | -0.20599 | -8.7112 | -0.20599 | -0.036621 | 1.4374 | 48.9624 | 48.4818 | 114.1479 | 122.8683 | 1.3184 | 122.8226 | 57.4768 | -0.20599 | 122.8683 | 1.3184 | 57.4768 | 114.1479 | 122.8226 | -122.9782 | -123.0652
801.3281 | 123.024 | -60.3378 | 62.5214 | -0.17197 | 0.023069 | 0.015729 | 0.011506 | 0.063316 | 0.0021341 | 0.083563 | -59.0286 | 62.5351 | -60.4568 | -60.5667 | 53.7506 | -2.8793 | -11.293 | -11.8835 | 62.4664 | -60.5484 | -0.11902 | 0.013733 | 1.3092 | -0.22888 | -8.7708 | -0.21057 | -0.054931 | 1.4282 | 49.0448 | 48.4543 | 114.0884 | 122.8729 | 1.3092 | 122.8043 | 57.4585 | -0.21057 | 122.8729 | 1.3092 | 57.4585 | 114.0884 | 122.8043 | -122.9782 | -123.0698
802.3281 | 123.0377 | -60.3378 | 62.5305 | -0.14908 | 0.024351 | 0.019361 | 0.011506 | 0.063529 | 0.0019205 | 0.081427 | -58.9828 | 62.5168 | -60.466 | -60.5301 | 53.7781 | -2.8107 | -11.293 | -11.8378 | 62.5076 | -60.5072 | -0.12817 | -0.013733 | 1.355 | -0.19226 | -8.7524 | -0.16937 | -0.022889 | 1.4832 | 49.0448 | 48.5001 | 114.1159 | 122.8546 | 1.355 | 122.8455 | 57.5272 | -0.16937 | 122.8546 | 1.355 | 57.5272 | 114.1159 | 122.8455 | -122.9965 | -123.0377
803.3281 | 123.0148 | -60.3195 | 62.4893 | -0.14908 | 0.023283 | 0.018293 | 0.011719 | 0.064384 | -0.00021569 | 0.083136 | -58.9325 | 62.5031 | -60.4614 | -60.5255 | 53.7643 | -2.861 | -11.2656 | -11.7783 | 62.4985 | -60.5301 | -0.14191 | 0.013733 | 1.387 | -0.20599 | -8.725 | -0.21057 | 0.009155 | 1.5289 | 49.054 | 48.5413 | 114.0839 | 122.8226 | 1.387 | 122.818 | 57.4585 | -0.21057 | 122.8226 | 1.387 | 57.4585 | 114.0839 | 122.818 | -122.9507 | -123.0194
804.3281 | 123.0469 | -60.3424 | 62.5122 | -0.13382 | 0.024351 | 0.016797 | 0.014496 | 0.063529 | -0.00042929 | 0.082495 | -58.8867 | 62.5031 | -60.4706 | -60.5255 | 53.7643 | -2.7054 | -11.0825 | -11.5768 | 62.471 | -60.5667 | -0.12817 | -0.009155 | 1.4557 | -0.18311 | -8.7479 | -0.2243 | -0.041199 | 1.5839 | 49.2599 | 48.7656 | 114.1068 | 122.8455 | 1.4557 | 122.8134 | 57.637 | -0.2243 | 122.8455 | 1.4557 | 57.637 | 114.1068 | 122.8134 | -122.9828 | -123.0789
805.3281 | 123.0423 | -60.3333 | 62.5259 | -0.14145 | 0.02371 | 0.015943 | 0.012787 | 0.063102 | 0.00021151 | 0.079504 | -58.9096 | 62.5122 | -60.4294 | -60.5484 | 53.7277 | -2.7374 | -11.0504 | -11.5814 | 62.4756 | -60.5438 | -0.09613 | -0.013733 | 1.4236 | -0.21515 | -8.7982 | -0.21057 | -0.050354 | 1.5198 | 49.2828 | 48.7518 | 114.061 | 122.8455 | 1.4236 | 122.8088 | 57.5958 | -0.21057 | 122.8455 | 1.4236 | 57.5958 | 114.061 | 122.8088 | -122.9553 | -123.0698
806.3281 | 123.0423 | -60.347 | 62.5305 | -0.1796 | 0.026274 | 0.018079 | 0.010224 | 0.062248 | 0.0032021 | 0.080786 | -58.9142 | 62.5076 | -60.466 | -60.5576 | 53.6774 | -2.774 | -11.0001 | -11.5768 | 62.5076 | -60.5164 | -0.11902 | -0.022889 | 1.4328 | -0.21057 | -8.8531 | -0.16937 | -0.022889 | 1.5518 | 49.3469 | 48.7701 | 114.0244 | 122.8546 | 1.4328 | 122.8546 | 57.5729 | -0.16937 | 122.8546 | 1.4328 | 57.5729 | 114.0244 | 122.8546 | -122.9965 | -123.0469
807.3281 | 123.0469 | -60.3653 | 62.5122 | -0.16434 | 0.022215 | 0.017011 | 0.0095832 | 0.061393 | 0.0023477 | 0.084204 | -58.9005 | 62.4939 | -60.4523 | -60.5759 | 53.6591 | -2.7924 | -10.5515 | -11.5768 | 62.5397 | -60.5118 | -0.086976 | -0.018311 | 1.4648 | -0.21057 | -8.8531 | -0.14648 | 0.027466 | 1.5518 | 49.8138 | 48.7885 | 114.0244 | 122.8592 | 1.4648 | 122.905 | 57.5729 | -0.14648 | 122.8592 | 1.4648 | 57.5729 | 114.0244 | 122.905 | -122.9645 | -123.024
808.3281 | 123.0194 | -60.3241 | 62.558 | -0.19485 | 0.024565 | 0.017224 | 0.011079 | 0.060325 | 0.00063871 | 0.080359 | -58.8638 | 62.4481 | -60.4248 | -60.5438 | 53.6499 | -2.6596 | -10.8765 | -11.3892 | 62.5031 | -60.4935 | -0.10071 | -0.10986 | 1.4603 | -0.21973 | -8.9081 | -0.16937 | -0.054931 | 1.561 | 49.4476 | 48.9349 | 113.974 | 122.7722 | 1.4603 | 122.8271 | 57.6645 | -0.16937 | 122.7722 | 1.4603 | 57.6645 | 113.974 | 122.8271 | -122.9828 | -123.0515
809.3281 | 123.0011 | -60.3378 | 62.5442 | -0.14145 | 0.025205 | 0.013593 | 0.010865 | 0.062675 | 0.0021341 | 0.081854 | -58.8181 | 62.471 | -60.4385 | -60.5621 | 53.595 | -2.6459 | -10.7986 | -11.348 | 62.4847 | -60.5255 | -0.10071 | -0.073242 | 1.5198 | -0.2243 | -8.9493 | -0.18768 | -0.059509 | 1.6205 | 49.5392 | 48.9899 | 113.9328 | 122.8088 | 1.5198 | 122.8226 | 57.692 | -0.18768 | 122.8088 | 1.5198 | 57.692 | 113.9328 | 122.8226 | -122.9828 | -123.0698
810.3281 | 123.0469 | -60.3424 | 62.558 | -0.19485 | 0.023496 | 0.017224 | 0.010224 | 0.063102 | 0.0014933 | 0.08164 | -58.8364 | 62.4527 | -60.4568 | -60.5713 | 53.6087 | -2.4857 | -10.6018 | -11.1374 | 62.4985 | -60.5164 | -0.11444 | -0.10529 | 1.506 | -0.22888 | -8.9493 | -0.17395 | -0.059509 | 1.6205 | 49.7406 | 49.205 | 113.9511 | 122.7951 | 1.506 | 122.8409 | 57.8568 | -0.17395 | 122.7951 | 1.506 | 57.8568 | 113.9511 | 122.8409 | -123.0148 | -123.0743
811.3281 | 123.0789 | -60.3195 | 62.5076 | -0.072784 | 0.023283 | 0.017011 | 0.01471 | 0.062675 | -0.0012839 | 0.081854 | -58.992 | 62.4298 | -60.4523 | -60.5026 | 53.595 | -2.4628 | -10.6979 | -11.0779 | 62.4847 | -60.5118 | -0.13275 | -0.077819 | 1.3275 | -0.18311 | -8.9127 | -0.19226 | -0.022888 | 1.4603 | 49.6216 | 49.2416 | 113.9145 | 122.7493 | 1.3275 | 122.8043 | 57.8567 | -0.19226 | 122.7493 | 1.3275 | 57.8567 | 113.9145 | 122.8043 | -122.9599 | -123.0194
812.3281 | 122.9874 | -60.347 | 62.5168 | -0.18723 | 0.023069 | 0.01637 | 0.010438 | 0.062461 | 0.0012795 | 0.083136 | -58.7769 | 62.4664 | -60.4523 | -60.5713 | 53.714 | -2.1103 | -10.7254 | -11.1374 | 62.4985 | -60.5072 | -0.10529 | -0.050354 | 1.5701 | -0.2243 | -8.8028 | -0.16022 | -0.018311 | 1.6754 | 49.6216 | 49.2096 | 114.061 | 122.8134 | 1.5701 | 122.8455 | 58.2367 | -0.16022 | 122.8134 | 1.5701 | 58.2367 | 114.061 | 122.8455 | -122.9691 | -123.024
813.3281 | 123.0011 | -60.3287 | 62.5397 | -0.21011 | 0.024778 | 0.013379 | 0.0097968 | 0.063316 | -0.0010703 | 0.081427 | -58.7448 | 62.4069 | -60.4385 | -60.5621 | 53.5492 | -2.1835 | -10.4004 | -10.8856 | 62.4939 | -60.498 | -0.10986 | -0.13275 | 1.5839 | -0.23346 | -8.9905 | -0.16937 | -0.045777 | 1.6937 | 49.9283 | 49.4431 | 113.8779 | 122.7356 | 1.5839 | 122.8226 | 58.1451 | -0.16937 | 122.7356 | 1.5839 | 58.1451 | 113.8779 | 122.8226 | -122.9782 | -123.0377
814.3281 | 123.0927 | -60.3149 | 62.5168 | -0.18723 | 0.023069 | 0.016584 | 0.0080878 | 0.061607 | -0.00042929 | 0.080359 | -58.699 | 62.3932 | -60.4248 | -60.4614 | 53.627 | -1.9638 | -10.4462 | -10.7437 | 62.4435 | -60.4843 | -0.10986 | -0.1236 | 1.6159 | -0.14649 | -8.8898 | -0.16937 | -0.073243 | 1.7258 | 49.8688 | 49.5712 | 113.942 | 122.7081 | 1.6159 | 122.7585 | 58.3511 | -0.16937 | 122.7081 | 1.6159 | 58.3511 | 113.942 | 122.7585 | -122.9416 | -123.0011
815.3281 | 123.056 | -60.3287 | 62.4939 | -0.17197 | 0.023069 | 0.014447 | 0.01001 | 0.062034 | -2.092e-06 | 0.082281 | -58.6395 | 62.3978 | -60.4568 | -60.4889 | 53.5675 | -1.9684 | -10.3867 | -10.7758 | 62.4756 | -60.4797 | -0.12817 | -0.09613 | 1.6891 | -0.16022 | -8.9264 | -0.15106 | -0.01831 | 1.8173 | 49.942 | 49.5529 | 113.8962 | 122.7264 | 1.6891 | 122.8043 | 58.3603 | -0.15106 | 122.7264 | 1.6891 | 58.3603 | 113.8962 | 122.8043 | -122.9507 | -122.9736
816.3281 | 123.0011 | -60.3195 | 62.5397 | -0.20248 | 0.024137 | 0.017865 | 0.013001 | 0.062889 | 0.00042511 | 0.081854 | -58.6945 | 62.4298 | -60.434 | -60.5713 | 53.4622 | -1.8951 | -10.2219 | -10.8124 | 62.4985 | -60.5118 | -0.11444 | -0.10986 | 1.6251 | -0.25177 | -9.0775 | -0.19226 | -0.041199 | 1.7395 | 50.0977 | 49.5071 | 113.7817 | 122.7493 | 1.6251 | 122.818 | 58.4244 | -0.19226 | 122.7493 | 1.6251 | 58.4244 | 113.7817 | 122.818 | -122.9736 | -123.0515
817.3281 | 123.024 | -60.3699 | 62.5351 | -0.18723 | 0.021147 | 0.018079 | 0.011719 | 0.060752 | 0.0014933 | 0.083136 | -58.6349 | 62.4344 | -60.4065 | -60.5438 | 53.476 | -1.799 | -10.1624 | -10.7346 | 62.4893 | -60.4935 | -0.036621 | -0.10071 | 1.7349 | -0.17395 | -9.0591 | -0.1236 | -0.045776 | 1.7715 | 50.2075 | 49.6353 | 113.8458 | 122.8043 | 1.7349 | 122.8592 | 58.5709 | -0.1236 | 122.8043 | 1.7349 | 58.5709 | 113.8458 | 122.8592 | -122.9416 | -123.0286
818.3438 | 123.024 | -60.3424 | 62.5214 | -0.14145 | 0.026487 | 0.01872 | 0.015778 | 0.062034 | -0.0012839 | 0.083563 | -58.6807 | 62.471 | -60.4568 | -60.5621 | 53.4531 | -1.7212 | -10.08 | -10.643 | 62.4939 | -60.5209 | -0.11444 | -0.050354 | 1.6617 | -0.21973 | -9.0683 | -0.17853 | -0.027466 | 1.7761 | 50.2625 | 49.6994 | 113.7955 | 122.8134 | 1.6617 | 122.8363 | 58.6212 | -0.17853 | 122.8134 | 1.6617 | 58.6212 | 113.7955 | 122.8363 | -122.9782 | -123.0423
819.3281 | 123.0515 | -60.3149 | 62.5122 | -0.18723 | 0.023069 | 0.020856 | 0.011079 | 0.060752 | 0.00085231 | 0.083563 | -58.5892 | 62.4298 | -60.4294 | -60.4889 | 53.4851 | -1.5747 | -10.1166 | -10.556 | 62.4573 | -60.4797 | -0.11444 | -0.082397 | 1.7258 | -0.17395 | -9.0271 | -0.1648 | -0.054932 | 1.8402 | 50.1984 | 49.7589 | 113.8 | 122.7448 | 1.7258 | 122.7722 | 58.7402 | -0.1648 | 122.7448 | 1.7258 | 58.7402 | 113.8 | 122.7722 | -122.9416 | -122.9919
820.3281 | 123.0881 | -60.3058 | 62.5305 | -0.18723 | 0.022642 | 0.01402 | 0.011506 | 0.060966 | -0.00042929 | 0.081213 | -58.5526 | 62.3978 | -60.4065 | -60.4935 | 53.4988 | -1.4694 | -10.0845 | -10.4507 | 62.4481 | -60.4706 | -0.10071 | -0.13275 | 1.7532 | -0.18768 | -9.0317 | -0.1648 | -0.082398 | 1.8539 | 50.2213 | 49.855 | 113.8046 | 122.7036 | 1.7532 | 122.7539 | 58.8364 | -0.1648 | 122.7036 | 1.7532 | 58.8364 | 113.8046 | 122.7539 | -122.937 | -123.0011
821.3281 | 123.1338 | -60.3149 | 62.4802 | 2.7119 | 0.02371 | 0.017652 | 0.008515 | 0.06182 | -0.00021569 | 0.082922 | -58.4198 | 62.3749 | -60.4523 | -60.466 | 53.508 | -1.3046 | -10.1028 | -10.3409 | 62.439 | -60.4614 | -0.13733 | -0.10529 | 1.8951 | -0.15106 | -8.9722 | -0.14649 | -0.041199 | 2.0325 | 50.2121 | 49.9741 | 113.8229 | 122.6898 | 1.8951 | 122.7539 | 59.0103 | -0.14649 | 122.6898 | 1.8951 | 59.0103 | 113.8229 | 122.7539 | -122.9324 | -122.9416
822.3281 | 123.1018 | -60.3012 | 62.5305 | -0.16434 | 0.023924 | 0.016156 | 0.013001 | 0.06118 | -0.0012839 | 0.083777 | -58.4564 | 62.3795 | -60.3973 | -60.4614 | 53.4943 | -1.268 | -9.9976 | -10.2859 | 62.4298 | -60.4752 | -0.096131 | -0.15106 | 1.8448 | -0.16022 | -9.0363 | -0.17395 | -0.10071 | 1.9409 | 50.3036 | 50.0153 | 113.7955 | 122.6807 | 1.8448 | 122.731 | 59.0332 | -0.17395 | 122.6807 | 1.8448 | 59.0332 | 113.7955 | 122.731 | -122.9279 | -123.0057
823.3281 | 122.9919 | -60.3516 | 62.5214 | -0.1796 | 0.024565 | 0.016584 | 0.013215 | 0.061393 | -0.00042929 | 0.082068 | -58.5068 | 62.4344 | -60.4477 | -60.5255 | 53.389 | -1.2039 | -9.874 | -10.4095 | 62.4527 | -60.4752 | -0.096131 | -0.086975 | 1.8448 | -0.17395 | -9.1324 | -0.1236 | -0.068664 | 1.9409 | 50.4776 | 49.942 | 113.7405 | 122.7859 | 1.8448 | 122.8043 | 59.1476 | -0.1236 | 122.7859 | 1.8448 | 59.1476 | 113.7405 | 122.8043 | -122.9691 | -122.9965
824.3281 | 123.0377 | -60.3195 | 62.5259 | -0.19485 | 0.023924 | 0.015729 | 0.01236 | 0.060325 | -0.00042929 | 0.081427 | -58.4839 | 62.4207 | -60.4385 | -60.5209 | 53.4256 | -1.0666 | -9.8511 | -10.3546 | 62.4756 | -60.4797 | -0.11902 | -0.10529 | 1.8356 | -0.20142 | -9.1003 | -0.16022 | -0.050354 | 1.9547 | 50.4684 | 49.9649 | 113.7451 | 122.7402 | 1.8356 | 122.7951 | 59.2529 | -0.16022 | 122.7402 | 1.8356 | 59.2529 | 113.7451 | 122.7951 | -122.9645 | -123.0057
825.3281 | 123.0469 | -60.3561 | 62.5122 | -0.21774 | 0.026487 | 0.020002 | 0.011719 | 0.059898 | 0.00042511 | 0.082708 | -58.4427 | 62.4207 | -60.4385 | -60.5072 | 53.4164 | -0.84686 | -9.7641 | -10.2448 | 62.4527 | -60.4935 | -0.082398 | -0.091553 | 1.9135 | -0.15106 | -9.0958 | -0.13733 | -0.059509 | 1.9959 | 50.592 | 50.1114 | 113.7726 | 122.7768 | 1.9135 | 122.8088 | 59.5093 | -0.13733 | 122.7768 | 1.9135 | 59.5093 | 113.7726 | 122.8088 | -122.9507 | -123.0057
826.3281 | 123.0515 | -60.3195 | 62.5214 | -0.21011 | 0.023924 | 0.016797 | 0.013428 | 0.060966 | 0.00021151 | 0.081427 | -58.4106 | 62.3703 | -60.4248 | -60.5164 | 53.421 | -0.67291 | -9.7458 | -10.1807 | 62.4573 | -60.5026 | -0.10529 | -0.15106 | 1.9089 | -0.19684 | -9.1003 | -0.18311 | -0.064087 | 2.0142 | 50.5737 | 50.1389 | 113.7405 | 122.6898 | 1.9089 | 122.7768 | 59.6466 | -0.18311 | 122.6898 | 1.9089 | 59.6466 | 113.7405 | 122.7768 | -122.9462 | -123.024
827.3281 | 123.1201 | -60.3333 | 62.4847 | -0.14145 | 0.024351 | 0.017224 | 0.0078742 | 0.058402 | 0.0019205 | 0.081 | -58.3969 | 62.3886 | -60.4156 | -60.4614 | 53.4622 | -0.4715 | -9.7916 | -10.0571 | 62.4161 | -60.4752 | -0.082397 | -0.09613 | 1.9363 | -0.12817 | -9.0225 | -0.14191 | -0.068664 | 2.0187 | 50.5417 | 50.2762 | 113.7955 | 122.7219 | 1.9363 | 122.7493 | 59.8618 | -0.14191 | 122.7219 | 1.9363 | 59.8618 | 113.7955 | 122.7493 | -122.9004 | -122.9599
828.3281 | 123.0881 | -60.3333 | 62.4802 | -0.21774 | 0.024137 | 0.01872 | 0.011719 | 0.060325 | -0.00021569 | 0.082068 | -58.3511 | 62.3703 | -60.4248 | -60.4568 | 53.4576 | -0.19684 | -9.6542 | -9.938 | 62.4344 | -60.4706 | -0.091553 | -0.10986 | 1.9821 | -0.1236 | -9.0225 | -0.13733 | -0.045777 | 2.0737 | 50.679 | 50.3952 | 113.7909 | 122.7036 | 1.9821 | 122.7676 | 60.1364 | -0.13733 | 122.7036 | 1.9821 | 60.1364 | 113.7909 | 122.7676 | -122.905 | -122.9507
829.3281 | 123.0927 | -60.3378 | 62.4985 | -0.17197 | 0.024992 | 0.02107 | 0.011506 | 0.059898 | -0.0014975 | 0.081 | -58.3649 | 62.3611 | -60.4431 | -60.4843 | 53.4256 | -0.027466 | -9.4208 | -9.8053 | 62.4619 | -60.4889 | -0.10529 | -0.13733 | 1.973 | -0.14648 | -9.0729 | -0.15106 | -0.036621 | 2.0782 | 50.9171 | 50.5325 | 113.7634 | 122.699 | 1.973 | 122.7997 | 60.3104 | -0.15106 | 122.699 | 1.973 | 60.3104 | 113.7634 | 122.7997 | -122.9416 | -122.9874
830.3438 | 123.1155 | -60.3378 | 62.4527 | 0.24002 | 0.025633 | 0.022138 | 0.014924 | 0.06182 | 0.0010659 | 0.080572 | -58.3832 | 62.3886 | -60.466 | -60.5255 | 53.3661 | 0.009155 | -9.6542 | -9.993 | 62.4023 | -60.5209 | -0.12817 | -0.064087 | 1.9547 | -0.18768 | -9.0866 | -0.18311 | -0.050354 | 2.0828 | 50.6836 | 50.3448 | 113.7039 | 122.7264 | 1.9547 | 122.7402 | 60.347 | -0.18311 | 122.7264 | 1.9547 | 60.347 | 113.7039 | 122.7402 | -122.9187 | -122.9736
831.3281 | 123.0103 | -60.3516 | 62.5397 | -0.21011 | 0.026487 | 0.014447 | 0.014283 | 0.059684 | 0.00042511 | 0.08164 | -58.3603 | 62.4344 | -60.4477 | -60.5667 | 53.3615 | 0.12817 | -9.3613 | -9.9426 | 62.4298 | -60.5118 | -0.096131 | -0.10529 | 1.9913 | -0.21515 | -9.1782 | -0.16022 | -0.10986 | 2.0874 | 50.9903 | 50.4089 | 113.7131 | 122.7859 | 1.9913 | 122.7814 | 60.4797 | -0.16022 | 122.7859 | 1.9913 | 60.4797 | 113.7131 | 122.7814 | -122.9874 | -123.0515
832.3281 | 123.0331 | -60.3607 | 62.5214 | -0.21774 | 0.02606 | 0.016584 | 0.011933 | 0.060325 | 0.0010659 | 0.082068 | -58.3923 | 62.439 | -60.4523 | -60.5667 | 53.3432 | 0.33417 | -9.2011 | -9.7916 | 62.4481 | -60.5255 | -0.091553 | -0.082397 | 1.9684 | -0.20599 | -9.1782 | -0.16479 | -0.073242 | 2.0599 | 51.1597 | 50.5692 | 113.7039 | 122.7997 | 1.9684 | 122.8088 | 60.6949 | -0.16479 | 122.7997 | 1.9684 | 60.6949 | 113.7039 | 122.8088 | -122.9736 | -123.0469
833.3281 | 123.0103 | -60.3561 | 62.5076 | -0.22537 | 0.025419 | 0.022992 | 0.013001 | 0.061393 | -0.0014975 | 0.08399 | -58.3328 | 62.4298 | -60.4568 | -60.5621 | 53.3524 | 0.48065 | -9.1736 | -9.8145 | 62.4802 | -60.5301 | -0.10071 | -0.077819 | 2.0233 | -0.20599 | -9.1553 | -0.17395 | -0.027465 | 2.124 | 51.1826 | 50.5417 | 113.7085 | 122.786 | 2.0233 | 122.8363 | 60.8368 | -0.17395 | 122.786 | 2.0233 | 60.8368 | 113.7085 | 122.8363 | -122.9645 | -123.0377
834.3281 | 123.1155 | -60.3149 | 62.4664 | -0.14908 | 0.025846 | 0.020856 | 0.010865 | 0.060966 | 0.00085231 | 0.082708 | -58.2367 | 62.3795 | -60.4385 | -60.4797 | 53.4256 | 0.75989 | -9.2056 | -9.6039 | 62.4161 | -60.4935 | -0.1236 | -0.086975 | 2.0782 | -0.1648 | -9.0408 | -0.17853 | -0.050354 | 2.2018 | 51.1093 | 50.7111 | 113.7405 | 122.6944 | 2.0782 | 122.731 | 61.0748 | -0.17853 | 122.6944 | 2.0782 | 61.0748 | 113.7405 | 122.731 | -122.905 | -122.9599
835.3438 | 123.024 | -60.3836 | 62.4985 | -0.12619 | 0.027128 | 0.023847 | 0.017701 | 0.063102 | -2.092e-06 | 0.08164 | -58.2687 | 62.4298 | -60.4523 | -60.5164 | 53.3661 | 0.96588 | -9.0271 | -9.5718 | 62.439 | -60.5301 | -0.068665 | -0.068664 | 2.1149 | -0.13275 | -9.1324 | -0.14648 | -0.059509 | 2.1835 | 51.3565 | 50.8118 | 113.7497 | 122.8134 | 2.1149 | 122.8226 | 61.3495 | -0.14648 | 122.8134 | 2.1149 | 61.3495 | 113.7497 | 122.8226 | -122.9507 | -123.0286
836.3281 | 123.056 | -60.347 | 62.4985 | -0.24063 | 0.024137 | 0.018293 | 0.011719 | 0.060325 | -0.00021569 | 0.082495 | -58.2275 | 62.3932 | -60.4843 | -60.5209 | 53.3936 | 1.181 | -8.9218 | -9.462 | 62.4298 | -60.4889 | -0.13733 | -0.10529 | 2.1194 | -0.17395 | -9.1049 | -0.14191 | -0.068664 | 2.2568 | 51.4252 | 50.885 | 113.7405 | 122.7402 | 2.1194 | 122.7768 | 61.528 | -0.14191 | 122.7402 | 2.1194 | 61.528 | 113.7405 | 122.7768 | -122.9828 | -122.9874
837.3281 | 123.0377 | -60.3836 | 62.4939 | -0.17197 | 0.026487 | 0.019361 | 0.012147 | 0.060966 | 0.00042511 | 0.081854 | -58.287 | 62.4207 | -60.498 | -60.585 | 53.3386 | 1.2543 | -8.4366 | -9.494 | 62.471 | -60.5118 | -0.11444 | -0.073242 | 2.0966 | -0.20142 | -9.1553 | -0.12817 | -0.022888 | 2.211 | 51.947 | 50.8896 | 113.7222 | 122.8043 | 2.0966 | 122.8546 | 61.6379 | -0.12817 | 122.8043 | 2.0966 | 61.6379 | 113.7222 | 122.8546 | -122.9919 | -123.0057
838.3281 | 123.0148 | -60.3745 | 62.5076 | -0.3093 | 0.025419 | 0.018506 | 0.01236 | 0.060752 | -0.00042929 | 0.082495 | -58.2687 | 62.4252 | -60.4889 | -60.5804 | 53.3386 | 1.5427 | -8.7112 | -9.3109 | 62.4298 | -60.5576 | -0.11444 | -0.082397 | 2.1057 | -0.20599 | -9.169 | -0.1831 | -0.077819 | 2.2202 | 51.6632 | 51.0635 | 113.7131 | 122.7997 | 2.1057 | 122.8043 | 61.9171 | -0.1831 | 122.7997 | 2.1057 | 61.9171 | 113.7131 | 122.8043 | -122.9965 | -123.0652
839.3281 | 123.0515 | -60.3699 | 62.5305 | -0.19485 | 0.025419 | 0.013379 | 0.010651 | 0.060111 | -0.00085669 | 0.082922 | -58.1955 | 62.3978 | -60.4843 | -60.5713 | 53.3386 | 1.7487 | -8.6884 | -9.256 | 62.4435 | -60.5392 | -0.11444 | -0.13275 | 2.1744 | -0.20142 | -9.1919 | -0.16937 | -0.086976 | 2.2888 | 51.6815 | 51.1139 | 113.7085 | 122.7676 | 2.1744 | 122.8134 | 62.1185 | -0.16937 | 122.7676 | 2.1744 | 62.1185 | 113.7085 | 122.8134 | -123.0148 | -123.0698
840.3438 | 123.0469 | -60.3882 | 62.4802 | 0.034027 | 0.028837 | 0.020215 | 0.018342 | 0.064811 | 0.00063871 | 0.082708 | -58.1635 | 62.439 | -60.4752 | -60.5988 | 53.3386 | 1.8951 | -8.757 | -9.3201 | 62.4344 | -60.5713 | -0.086975 | -0.041199 | 2.2247 | -0.21057 | -9.1415 | -0.1831 | -0.045777 | 2.3117 | 51.6312 | 51.0681 | 113.7268 | 122.8271 | 2.2247 | 122.8226 | 62.2833 | -0.1831 | 122.8271 | 2.2247 | 62.2833 | 113.7268 | 122.8226 | -122.9553 | -123.0515
841.3281 | 123.2895 | -60.3104 | 62.4573 | -0.13382 | 0.023496 | 0.013593 | 0.0072332 | 0.062034 | 0.0010659 | 0.08164 | -58.1223 | 62.3383 | -60.466 | -60.4797 | 53.4714 | 2.243 | -8.7753 | -9.0134 | 62.352 | -60.4935 | -0.15564 | -0.11902 | 2.1881 | -0.16937 | -8.9859 | -0.1831 | -0.10529 | 2.3438 | 51.535 | 51.297 | 113.7817 | 122.6486 | 2.1881 | 122.6624 | 62.5534 | -0.1831 | 122.6486 | 2.1881 | 62.5534 | 113.7817 | 122.6624 | -122.9233 | -122.9507
842.3281 | 123.111 | -60.3378 | 62.4527 | -0.38559 | 0.025846 | 0.020215 | 0.008515 | 0.06118 | -0.0010703 | 0.083136 | -58.1131 | 62.3566 | -60.4706 | -60.4935 | 53.476 | 2.4628 | -8.5922 | -8.9127 | 62.3474 | -60.5255 | -0.13275 | -0.096131 | 2.2247 | -0.15564 | -8.9767 | -0.18768 | -0.10529 | 2.3575 | 51.7456 | 51.4252 | 113.8138 | 122.6944 | 2.2247 | 122.6852 | 62.8006 | -0.18768 | 122.6944 | 2.2247 | 62.8006 | 113.8138 | 122.6852 | -122.9233 | -122.9782
843.3281 | 123.0972 | -60.3607 | 62.4619 | -0.17197 | 0.027342 | 0.01872 | 0.012147 | 0.059898 | -0.0025657 | 0.083563 | -58.0673 | 62.3611 | -60.4614 | -60.5118 | 53.4485 | 2.623 | -8.4961 | -8.8989 | 62.4115 | -60.5118 | -0.10071 | -0.10071 | 2.2934 | -0.15106 | -9.0134 | -0.15106 | -0.050354 | 2.3941 | 51.8646 | 51.4618 | 113.8092 | 122.7219 | 2.2934 | 122.7722 | 62.9837 | -0.15106 | 122.7219 | 2.2934 | 62.9837 | 113.8092 | 122.7722 | -122.9233 | -122.9736
844.3281 | 123.0286 | -60.3745 | 62.4664 | -0.19485 | 0.026487 | 0.022565 | 0.013856 | 0.060111 | 0.00042511 | 0.081427 | -58.0811 | 62.384 | -60.4797 | -60.5576 | 53.4027 | 2.8061 | -8.2901 | -8.8348 | 62.4207 | -60.5301 | -0.10529 | -0.082398 | 2.2934 | -0.1831 | -9.0637 | -0.15564 | -0.045777 | 2.3987 | 52.0844 | 51.5396 | 113.7772 | 122.7585 | 2.2934 | 122.7951 | 63.1805 | -0.15564 | 122.7585 | 2.2934 | 63.1805 | 113.7772 | 122.7951 | -122.9462 | -122.9965
845.3438 | 123.0103 | -60.4065 | 62.4664 | -0.011749 | 0.028837 | 0.022351 | 0.018128 | 0.06417 | -0.00064309 | 0.082922 | -58.0627 | 62.4252 | -60.4797 | -60.5667 | 53.3752 | 2.9709 | -8.2764 | -8.7616 | 62.3978 | -60.5438 | -0.073242 | -0.041199 | 2.3438 | -0.16022 | -9.0912 | -0.13733 | -0.068665 | 2.417 | 52.1301 | 51.6449 | 113.7817 | 122.8317 | 2.3438 | 122.8043 | 63.3774 | -0.13733 | 122.8317 | 2.3438 | 63.3774 | 113.7817 | 122.8043 | -122.9462 | -123.0103
846.3281 | 123.0606 | -60.3561 | 62.439 | -0.20248 | 0.026274 | 0.019147 | 0.0097968 | 0.063743 | 0.00021151 | 0.082281 | -58.0673 | 62.3703 | -60.4752 | -60.5255 | 53.4897 | 3.3279 | -8.1207 | -8.5007 | 62.3886 | -60.5347 | -0.11902 | -0.068665 | 2.2888 | -0.16937 | -8.9493 | -0.17853 | -0.050354 | 2.4078 | 52.2354 | 51.8555 | 113.8458 | 122.7264 | 2.2888 | 122.7448 | 63.6841 | -0.17853 | 122.7264 | 2.2888 | 63.6841 | 113.8458 | 122.7448 | -122.9141 | -122.9736
847.3281 | 123.1247 | -60.3699 | 62.439 | -0.22537 | 0.025205 | 0.020429 | 0.010438 | 0.06118 | -0.0012839 | 0.083136 | -58.049 | 62.3291 | -60.5026 | -60.5072 | 53.4851 | 3.4195 | -8.1757 | -8.5144 | 62.3932 | -60.5118 | -0.13275 | -0.10986 | 2.3209 | -0.13733 | -8.9539 | -0.14191 | -0.045777 | 2.4536 | 52.1942 | 51.8555 | 113.855 | 122.699 | 2.3209 | 122.7631 | 63.7894 | -0.14191 | 122.699 | 2.3209 | 63.7894 | 113.855 | 122.7631 | -122.9416 | -122.9507
848.3281 | 123.0148 | -60.3973 | 62.4847 | -0.14908 | 0.02606 | 0.017652 | 0.01706 | 0.060966 | -0.00064309 | 0.083563 | -58.0811 | 62.4115 | -60.5026 | -60.6033 | 53.3981 | 3.5843 | -7.869 | -8.4778 | 62.4207 | -60.5759 | -0.10529 | -0.073242 | 2.3163 | -0.20599 | -9.0866 | -0.17853 | -0.064087 | 2.4216 | 52.5284 | 51.9196 | 113.7955 | 122.8088 | 2.3163 | 122.818 | 63.9816 | -0.17853 | 122.8088 | 2.3163 | 63.9816 | 113.7955 | 122.818 | -122.9874 | -123.0606
849.3281 | 123.0927 | -60.379 | 62.4207 | -0.049896 | 0.025419 | 0.01637 | 0.01001 | 0.062248 | 0.0021341 | 0.08399 | -57.9803 | 62.3016 | -60.4706 | -60.4889 | 53.508 | 4.2206 | -8.1619 | -8.6929 | 62.3932 | -60.5347 | -0.091553 | -0.11902 | 2.3987 | -0.10986 | -8.9127 | -0.15564 | -0.027466 | 2.4902 | 52.2171 | 51.6861 | 113.887 | 122.6807 | 2.3987 | 122.7722 | 64.5996 | -0.15564 | 122.6807 | 2.3987 | 64.5996 | 113.887 | 122.7722 | -122.8912 | -122.9553
850.3281 | 123.1201 | -60.3699 | 62.4481 | -0.20248 | 0.024992 | 0.020856 | 0.010865 | 0.060111 | -0.0014975 | 0.084204 | -57.9529 | 62.2925 | -60.4843 | -60.5209 | 53.5629 | 4.0833 | -7.8369 | -8.1482 | 62.3566 | -60.4935 | -0.11444 | -0.15564 | 2.417 | -0.15106 | -8.8852 | -0.1236 | -0.091553 | 2.5314 | 52.533 | 52.2217 | 113.9328 | 122.6624 | 2.417 | 122.7264 | 64.4531 | -0.1236 | 122.6624 | 2.417 | 64.4531 | 113.9328 | 122.7264 | -122.9324 | -122.9416
851.3281 | 123.1201 | -60.3973 | 62.4527 | -0.19485 | 0.02371 | 0.017011 | 0.011079 | 0.060539 | -0.00064309 | 0.081854 | -57.9391 | 62.3154 | -60.4706 | -60.5347 | 53.5263 | 4.2572 | -7.7728 | -8.1894 | 62.3978 | -60.5301 | -0.073242 | -0.13733 | 2.4582 | -0.13733 | -8.9264 | -0.13275 | -0.054932 | 2.5314 | 52.6245 | 52.2079 | 113.9236 | 122.7127 | 2.4582 | 122.7951 | 64.6545 | -0.13275 | 122.7127 | 2.4582 | 64.6545 | 113.9236 | 122.7951 | -122.9233 | -122.9828
852.3281 | 123.0835 | -60.3699 | 62.4435 | -0.16434 | 0.022642 | 0.018079 | 0.012147 | 0.059471 | -0.0017111 | 0.081854 | -58.0032 | 62.3062 | -60.4889 | -60.5392 | 53.5492 | 4.5364 | -7.6721 | -8.0612 | 62.3703 | -60.5347 | -0.11902 | -0.13733 | 2.3666 | -0.16937 | -8.8943 | -0.1648 | -0.073242 | 2.4857 | 52.6978 | 52.3087 | 113.9191 | 122.6761 | 2.3666 | 122.7402 | 64.9063 | -0.1648 | 122.6761 | 2.3666 | 64.9063 | 113.9191 | 122.7402 | -122.9324 | -122.9782
853.3281 | 123.0927 | -60.3607 | 62.4298 | -0.14145 | 0.024778 | 0.017224 | 0.01471 | 0.060539 | 0.0017069 | 0.083349 | -57.9483 | 62.3245 | -60.498 | -60.5347 | 53.5675 | 4.7287 | -7.5943 | -7.9605 | 62.3474 | -60.5164 | -0.13733 | -0.10529 | 2.4124 | -0.17395 | -8.8623 | -0.15564 | -0.082398 | 2.5497 | 52.7664 | 52.4002 | 113.9282 | 122.6852 | 2.4124 | 122.7081 | 65.0894 | -0.15564 | 122.6852 | 2.4124 | 65.0894 | 113.9282 | 122.7081 | -122.9279 | -122.9462
854.3281 | 123.1064 | -60.3745 | 62.4298 | -0.15671 | 0.02606 | 0.01872 | 0.012574 | 0.061393 | -0.0014975 | 0.083136 | -57.9391 | 62.2971 | -60.4935 | -60.5209 | 53.5812 | 4.953 | -7.5211 | -7.8461 | 62.3474 | -60.5301 | -0.11902 | -0.13275 | 2.4353 | -0.14648 | -8.8486 | -0.15564 | -0.082398 | 2.5543 | 52.8534 | 52.5284 | 113.9557 | 122.6715 | 2.4353 | 122.7219 | 65.3275 | -0.15564 | 122.6715 | 2.4353 | 65.3275 | 113.9557 | 122.7219 | -122.9233 | -122.9599
855.3281 | 123.111 | -60.3882 | 62.384 | -0.049896 | 0.024351 | 0.01637 | 0.011719 | 0.059043 | 0.0010659 | 0.08399 | -57.8934 | 62.2833 | -60.4935 | -60.5026 | 54.0024 | 5.5023 | -7.9422 | -7.901 | 62.3611 | -60.5347 | -0.10528 | -0.10071 | 2.4948 | -0.11444 | -8.3817 | -0.14648 | -0.022888 | 2.6001 | 52.446 | 52.4872 | 114.3906 | 122.6715 | 2.4948 | 122.7493 | 65.8905 | -0.14648 | 122.6715 | 2.4948 | 65.8905 | 114.3906 | 122.7493 | -122.8775 | -122.9187
856.3281 | 123.3719 | -60.3378 | 62.4664 | -0.080414 | 0.025633 | 0.013379 | 0.013642 | 0.062675 | -0.0025657 | 0.082708 | -57.9025 | 62.2925 | -60.5072 | -60.5164 | 53.6133 | 5.3238 | -7.4524 | -7.7271 | 62.3474 | -60.5392 | -0.16937 | -0.17395 | 2.4353 | -0.17853 | -8.8531 | -0.20142 | -0.11902 | 2.6047 | 52.8854 | 52.6108 | 113.9511 | 122.6303 | 2.4353 | 122.6852 | 65.6616 | -0.20142 | 122.6303 | 2.4353 | 65.6616 | 113.9511 | 122.6852 | -122.9736 | -123.0057
857.3281 | 123.1201 | -60.379 | 62.4069 | 0.049286 | 0.025419 | 0.018293 | 0.013642 | 0.05883 | -0.0019247 | 0.082068 | -57.8705 | 62.2787 | -60.498 | -60.5118 | 53.6453 | 5.5069 | -7.3242 | -7.5943 | 62.3474 | -60.5301 | -0.11902 | -0.12817 | 2.5085 | -0.13275 | -8.7616 | -0.15106 | -0.059509 | 2.6276 | 53.0548 | 52.7847 | 114.0244 | 122.6578 | 2.5085 | 122.7264 | 65.8859 | -0.15106 | 122.6578 | 2.5085 | 65.8859 | 114.0244 | 122.7264 | -122.905 | -122.937
858.3281 | 123.1018 | -60.3836 | 62.4298 | -0.21011 | 0.024351 | 0.016156 | 0.015565 | 0.059471 | -0.0021383 | 0.08164 | -57.9071 | 62.2879 | -60.5026 | -60.5392 | 53.6224 | 5.6717 | -7.2189 | -7.5668 | 62.3749 | -60.5576 | -0.11902 | -0.14191 | 2.4765 | -0.15564 | -8.8074 | -0.17395 | -0.054932 | 2.5955 | 53.1647 | 52.8168 | 114.006 | 122.6715 | 2.4765 | 122.7585 | 66.0553 | -0.17395 | 122.6715 | 2.4765 | 66.0553 | 114.006 | 122.7585 | -122.9324 | -122.9874
859.3281 | 123.1338 | -60.3928 | 62.4161 | -0.17197 | 0.026487 | 0.017865 | 0.013428 | 0.060539 | 0.00021151 | 0.082495 | -57.8567 | 62.2971 | -60.5209 | -60.5438 | 53.6362 | 5.7587 | -7.2418 | -7.576 | 62.3795 | -60.5301 | -0.12817 | -0.11902 | 2.536 | -0.15106 | -8.7799 | -0.13733 | -0.036621 | 2.6642 | 53.1509 | 52.8168 | 114.0289 | 122.6898 | 2.536 | 122.7722 | 66.1514 | -0.13733 | 122.6898 | 2.536 | 66.1514 | 114.0289 | 122.7722 | -122.937 | -122.9462
860.3281 | 123.1018 | -60.379 | 62.4252 | -0.14908 | 0.024778 | 0.018506 | 0.014283 | 0.060111 | -0.0017111 | 0.083136 | -57.8339 | 62.2925 | -60.5118 | -60.5209 | 53.6362 | 5.9692 | -7.1411 | -7.4936 | 62.3474 | -60.5438 | -0.13275 | -0.13275 | 2.5452 | -0.14191 | -8.7891 | -0.1648 | -0.07782 | 2.6779 | 53.2379 | 52.8854 | 114.0152 | 122.6715 | 2.5452 | 122.7264 | 66.3483 | -0.1648 | 122.6715 | 2.5452 | 66.3483 | 114.0152 | 122.7264 | -122.937 | -122.9691
861.3281 | 123.111 | -60.3928 | 62.4023 | -0.14145 | 0.025205 | 0.014661 | 0.014283 | 0.058402 | -2.092e-06 | 0.082922 | -57.8201 | 62.2879 | -60.5118 | -60.5438 | 53.6957 | 6.2302 | -7.0267 | -7.3837 | 62.3062 | -60.553 | -0.11902 | -0.11444 | 2.5726 | -0.15106 | -8.7067 | -0.16022 | -0.096131 | 2.6917 | 53.3661 | 53.009 | 114.0884 | 122.6807 | 2.5726 | 122.699 | 66.6229 | -0.16022 | 122.6807 | 2.5726 | 66.6229 | 114.0884 | 122.699 | -122.9141 | -122.9553
862.3281 | 123.0057 | -60.3882 | 62.4435 | -0.057526 | 0.024992 | 0.023633 | 0.012787 | 0.059471 | 0.0025613 | 0.085058 | -57.8201 | 62.2742 | -60.498 | -60.5209 | 53.7094 | 6.4545 | -6.9717 | -7.2418 | 62.3016 | -60.5484 | -0.10986 | -0.16937 | 2.5681 | -0.13275 | -8.7341 | -0.16022 | -0.14191 | 2.6779 | 53.4164 | 53.1464 | 114.0976 | 122.6624 | 2.5681 | 122.6898 | 66.8427 | -0.16022 | 122.6624 | 2.5681 | 66.8427 | 114.0976 | 122.6898 | -122.9416 | -122.9919
863.3281 | 123.1567 | -60.4065 | 62.384 | -0.13382 | 0.025419 | 0.020642 | 0.013856 | 0.058189 | 0.0017069 | 0.083136 | -57.8247 | 62.2604 | -60.5164 | -60.5484 | 53.7048 | 6.5918 | -6.8527 | -7.132 | 62.3062 | -60.5759 | -0.10986 | -0.1236 | 2.5818 | -0.14191 | -8.6792 | -0.16937 | -0.07782 | 2.6917 | 53.5538 | 53.2745 | 114.1113 | 122.6669 | 2.5818 | 122.7127 | 66.9983 | -0.16937 | 122.6669 | 2.5818 | 66.9983 | 114.1113 | 122.7127 | -122.9004 | -122.9599
864.3281 | 123.1018 | -60.3653 | 62.4161 | 0.064545 | 0.025633 | 0.023206 | 0.015565 | 0.060539 | -0.00064309 | 0.085272 | -57.8064 | 62.2559 | -60.5438 | -60.5392 | 53.7094 | 6.7108 | -6.8848 | -7.251 | 62.3245 | -60.5392 | -0.17853 | -0.16022 | 2.5589 | -0.17395 | -8.7067 | -0.17395 | -0.091553 | 2.7374 | 53.4805 | 53.1143 | 114.0747 | 122.6212 | 2.5589 | 122.6898 | 67.0761 | -0.17395 | 122.6212 | 2.5589 | 67.0761 | 114.0747 | 122.6898 | -122.9599 | -122.9553
865.3281 | 123.111 | -60.3836 | 62.4207 | -0.14145 | 0.024992 | 0.019361 | 0.015778 | 0.059898 | -0.0017111 | 0.083777 | -57.7744 | 62.2879 | -60.5164 | -60.5347 | 53.7277 | 6.8298 | -6.7474 | -7.2006 | 62.352 | -60.5621 | -0.13275 | -0.13275 | 2.6093 | -0.15106 | -8.6929 | -0.17853 | -0.068664 | 2.742 | 53.6362 | 53.183 | 114.1113 | 122.6715 | 2.6093 | 122.7356 | 67.2134 | -0.17853 | 122.6715 | 2.6093 | 67.2134 | 114.1113 | 122.7356 | -122.937 | -122.9828
866.3281 | 123.1201 | -60.3973 | 62.384 | -0.17197 | 0.026701 | 0.01872 | 0.011719 | 0.059257 | 0.00085231 | 0.084845 | -57.7423 | 62.2833 | -60.5209 | -60.6674 | 54.1214 | 7.3563 | -7.1823 | -7.3105 | 62.2971 | -60.5576 | -0.1236 | -0.10071 | 2.655 | -0.27008 | -8.2626 | -0.16022 | -0.086975 | 2.7786 | 53.215 | 53.0869 | 114.5187 | 122.6807 | 2.655 | 122.6944 | 67.7536 | -0.16022 | 122.6807 | 2.655 | 67.7536 | 114.5187 | 122.6944 | -122.905 | -122.9416
867.3281 | 123.1247 | -60.3973 | 62.3932 | -0.11093 | 0.024778 | 0.018293 | 0.012787 | 0.059684 | -0.0017111 | 0.082068 | -57.7194 | 62.2925 | -60.5118 | -60.5438 | 53.7323 | 7.2052 | -6.601 | -6.9077 | 62.3154 | -60.553 | -0.11444 | -0.10071 | 2.6779 | -0.14648 | -8.6609 | -0.15564 | -0.077819 | 2.7924 | 53.7964 | 53.4897 | 114.1296 | 122.6898 | 2.6779 | 122.7127 | 67.6025 | -0.15564 | 122.6898 | 2.6779 | 67.6025 | 114.1296 | 122.7127 | -122.905 | -122.9462
868.3281 | 123.1064 | -60.3928 | 62.4115 | 0.94193 | 0.026487 | 0.021711 | 0.013428 | 0.059043 | 0.00021151 | 0.083563 | -57.7057 | 62.2604 | -60.5392 | -60.5438 | 53.7369 | 7.402 | -6.427 | -6.752 | 62.3062 | -60.5576 | -0.14648 | -0.15106 | 2.6871 | -0.15106 | -8.6746 | -0.16479 | -0.10529 | 2.8336 | 53.9658 | 53.6407 | 114.1296 | 122.6532 | 2.6871 | 122.699 | 67.7948 | -0.16479 | 122.6532 | 2.6871 | 67.7948 | 114.1296 | 122.699 | -122.9507 | -122.9691
869.3281 | 123.1384 | -60.4019 | 62.3886 | -0.065155 | 0.027342 | 0.013806 | 0.014283 | 0.05883 | -0.00042929 | 0.083563 | -57.7469 | 62.2467 | -60.5255 | -60.5621 | 53.7231 | 7.4432 | -6.5048 | -6.8481 | 62.3108 | -60.5392 | -0.1236 | -0.14191 | 2.655 | -0.16022 | -8.6655 | -0.13733 | -0.07782 | 2.7786 | 53.8971 | 53.5538 | 114.1251 | 122.6486 | 2.655 | 122.7127 | 67.8452 | -0.13733 | 122.6486 | 2.655 | 67.8452 | 114.1251 | 122.7127 | -122.9141 | -122.9279
870.3281 | 123.1155 | -60.4202 | 62.3749 | -0.065155 | 0.025633 | 0.022565 | 0.012574 | 0.060966 | -0.0025657 | 0.082922 | -57.7606 | 62.2742 | -60.5347 | -60.5804 | 53.7506 | 7.5943 | -6.3217 | -6.7245 | 62.2971 | -60.5621 | -0.11444 | -0.10071 | 2.6596 | -0.16022 | -8.6243 | -0.14191 | -0.07782 | 2.774 | 54.0985 | 53.6957 | 114.1708 | 122.6944 | 2.6596 | 122.7173 | 68.0145 | -0.14191 | 122.6944 | 2.6596 | 68.0145 | 114.1708 | 122.7173 | -122.9095 | -122.937
871.3281 | 123.1338 | -60.4019 | 62.384 | -0.049896 | 0.026274 | 0.016797 | 0.013001 | 0.058189 | -0.0017111 | 0.083349 | -57.7606 | 62.2421 | -60.5301 | -60.5484 | 53.8055 | 7.7591 | -6.2714 | -6.6055 | 62.3062 | -60.5621 | -0.12817 | -0.14191 | 2.6413 | -0.14648 | -8.5785 | -0.16022 | -0.07782 | 2.7695 | 54.1306 | 53.7964 | 114.2075 | 122.644 | 2.6413 | 122.7081 | 68.161 | -0.16022 | 122.644 | 2.6413 | 68.161 | 114.2075 | 122.7081 | -122.9141 | -122.9462
872.3281 | 123.1384 | -60.4294 | 62.3657 | -0.1033 | 0.027128 | 0.018506 | 0.0070196 | 0.058402 | -0.00021569 | 0.084204 | -57.7194 | 62.2559 | -60.5484 | -60.7361 | 53.8651 | 8.0063 | -6.2027 | -6.395 | 62.2742 | -60.5896 | -0.11902 | -0.10986 | 2.71 | -0.3067 | -8.5007 | -0.16022 | -0.091553 | 2.829 | 54.2267 | 54.0344 | 114.2944 | 122.6852 | 2.71 | 122.7036 | 68.4357 | -0.16022 | 122.6852 | 2.71 | 68.4357 | 114.2944 | 122.7036 | -122.9141 | -122.9553
873.3281 | 123.1476 | -60.4202 | 62.3611 | -0.1033 | 0.027342 | 0.017865 | 0.013215 | 0.058189 | 0.00063871 | 0.081854 | -57.6553 | 62.2559 | -60.5576 | -60.5392 | 53.8284 | 8.0887 | -6.0791 | -6.4133 | 62.2742 | -60.5759 | -0.13733 | -0.10529 | 2.7649 | -0.11902 | -8.5327 | -0.15564 | -0.086975 | 2.9022 | 54.3411 | 54.007 | 114.2487 | 122.6761 | 2.7649 | 122.6944 | 68.5089 | -0.15564 | 122.6761 | 2.7649 | 68.5089 | 114.2487 | 122.6944 | -122.9187 | -122.937
874.3281 | 123.1293 | -60.4248 | 62.384 | -0.049896 | 0.024565 | 0.021924 | 0.012787 | 0.057975 | -0.0019247 | 0.085272 | -57.6965 | 62.2375 | -60.553 | -60.5621 | 53.7827 | 8.0246 | -6.0837 | -6.4407 | 62.3108 | -60.585 | -0.12817 | -0.14648 | 2.7283 | -0.13733 | -8.6014 | -0.16022 | -0.073242 | 2.8564 | 54.3411 | 53.9841 | 114.2075 | 122.6624 | 2.7283 | 122.7356 | 68.4494 | -0.16022 | 122.6624 | 2.7283 | 68.4494 | 114.2075 | 122.7356 | -122.937 | -122.9691
875.3281 | 123.1384 | -60.4202 | 62.4023 | -0.057526 | 0.025419 | 0.016584 | 0.012787 | 0.058402 | 0.0010659 | 0.086126 | -57.6828 | 62.2467 | -60.5255 | -60.585 | 53.7781 | 8.0978 | -6.0562 | -6.4316 | 62.2879 | -60.5804 | -0.10529 | -0.15564 | 2.7374 | -0.1648 | -8.6243 | -0.16022 | -0.11444 | 2.8427 | 54.364 | 53.9886 | 114.1983 | 122.6669 | 2.7374 | 122.7081 | 68.5181 | -0.16022 | 122.6669 | 2.7374 | 68.5181 | 114.1983 | 122.7081 | -122.9279 | -122.9828
876.3281 | 123.111 | -60.4477 | 62.3749 | 1.7812 | 0.027769 | 0.019147 | 0.014924 | 0.05883 | -2.092e-06 | 0.082281 | -57.6736 | 62.2421 | -60.5484 | -60.6583 | 53.7415 | 8.1711 | -5.9052 | -6.4362 | 62.2604 | -60.6079 | -0.10071 | -0.13275 | 2.774 | -0.21057 | -8.6334 | -0.16022 | -0.11444 | 2.8748 | 54.5425 | 54.0115 | 114.1891 | 122.6898 | 2.774 | 122.7081 | 68.6188 | -0.16022 | 122.6898 | 2.774 | 68.6188 | 114.1891 | 122.7081 | -122.9233 | -122.9828
877.3281 | 123.0286 | -60.4523 | 62.3611 | 0.14084 | 0.026914 | 0.019788 | 0.014924 | 0.059898 | 0.0019205 | 0.085058 | -57.7377 | 62.2513 | -60.5667 | -60.6674 | 53.8559 | 8.5876 | -6.1707 | -6.4545 | 62.2604 | -60.5804 | -0.11444 | -0.10986 | 2.7145 | -0.21515 | -8.5052 | -0.12817 | -0.10071 | 2.829 | 54.2816 | 53.9978 | 114.3082 | 122.7036 | 2.7145 | 122.7127 | 69.0399 | -0.12817 | 122.7036 | 2.7145 | 69.0399 | 114.3082 | 122.7127 | -122.9279 | -122.9416
878.3438 | 123.1613 | -60.3973 | 62.439 | -0.042267 | 0.026487 | 0.017438 | 0.014496 | 0.055839 | 0.0019205 | 0.082281 | -57.6553 | 62.2696 | -60.5392 | -60.5576 | 53.8467 | 8.519 | -5.9143 | -6.2805 | 62.2696 | -60.5621 | -0.14191 | -0.16937 | 2.742 | -0.16022 | -8.5922 | -0.16479 | -0.16937 | 2.8839 | 54.483 | 54.1168 | 114.2441 | 122.6669 | 2.742 | 122.6669 | 68.9163 | -0.16479 | 122.6669 | 2.742 | 68.9163 | 114.2441 | 122.6669 | -122.9782 | -123.0011
879.3281 | 123.1155 | -60.4248 | 62.3932 | 0.018768 | 0.024778 | 0.017652 | 0.013001 | 0.059898 | 0.00021151 | 0.08399 | -57.7286 | 62.2604 | -60.5621 | -60.6079 | 53.8055 | 8.4641 | -5.7861 | -6.2942 | 62.2833 | -60.585 | -0.13733 | -0.13275 | 2.6962 | -0.1831 | -8.5876 | -0.16022 | -0.10986 | 2.8336 | 54.6387 | 54.1306 | 114.2303 | 122.6852 | 2.6962 | 122.7081 | 68.8889 | -0.16022 | 122.6852 | 2.6962 | 68.8889 | 114.2303 | 122.7081 | -122.9553 | -122.9782
880.3281 | 123.0743 | -60.434 | 62.3978 | 0.018768 | 0.027128 | 0.017224 | 0.013001 | 0.057548 | -0.0010703 | 0.083777 | -57.7332 | 62.2421 | -60.5484 | -60.6308 | 53.7872 | 8.519 | -5.8502 | -6.3675 | 62.2833 | -60.5896 | -0.11444 | -0.15564 | 2.7008 | -0.19684 | -8.6105 | -0.15564 | -0.11444 | 2.8152 | 54.5837 | 54.0665 | 114.2212 | 122.6761 | 2.7008 | 122.7173 | 68.9529 | -0.15564 | 122.6761 | 2.7008 | 68.9529 | 114.2212 | 122.7173 | -122.9462 | -122.9874
881.3281 | 123.0789 | -60.434 | 62.384 | 0.56046 | 0.02606 | 0.017438 | 0.013642 | 0.056907 | -0.0012839 | 0.082495 | -57.6416 | 62.2559 | -60.5576 | -60.6445 | 53.7827 | 8.6746 | -5.7404 | -6.2531 | 62.265 | -60.5713 | -0.1236 | -0.12817 | 2.7924 | -0.21057 | -8.6014 | -0.13733 | -0.11902 | 2.916 | 54.6936 | 54.1809 | 114.2166 | 122.6898 | 2.7924 | 122.699 | 69.1086 | -0.13733 | 122.6898 | 2.7924 | 69.1086 | 114.2166 | 122.699 | -122.9416 | -122.9553
882.3281 | 123.0835 | -60.4294 | 62.3703 | 0.10269 | 0.026487 | 0.017224 | 0.012787 | 0.054557 | -0.00085669 | 0.085272 | -57.6874 | 62.2421 | -60.5667 | -60.7956 | 53.7506 | 8.7891 | -5.8548 | -6.2576 | 62.2467 | -60.5942 | -0.13733 | -0.12817 | 2.742 | -0.36621 | -8.6197 | -0.1648 | -0.1236 | 2.8793 | 54.5746 | 54.1718 | 114.18 | 122.6715 | 2.742 | 122.6761 | 69.2184 | -0.1648 | 122.6715 | 2.742 | 69.2184 | 114.18 | 122.6761 | -122.937 | -122.9645
883.3281 | 123.0789 | -60.4248 | 62.3383 | 0.17899 | 0.030119 | 0.016156 | 0.015137 | 0.06118 | 0.00063871 | 0.082281 | -57.6279 | 62.2192 | -60.5759 | -60.6171 | 53.8147 | 8.8486 | -5.7999 | -6.2256 | 62.2513 | -60.585 | -0.15106 | -0.11902 | 2.7969 | -0.19226 | -8.5236 | -0.16022 | -0.086975 | 2.948 | 54.6249 | 54.1992 | 114.2395 | 122.644 | 2.7969 | 122.6761 | 69.2734 | -0.16022 | 122.644 | 2.7969 | 69.2734 | 114.2395 | 122.6761 | -122.9141 | -122.9233
884.3281 | 123.0743 | -60.4248 | 62.3383 | 0.17899 | 0.026701 | 0.020642 | 0.01471 | 0.058189 | 0.00063871 | 0.083563 | -57.6828 | 62.2467 | -60.585 | -60.6308 | 53.8147 | 8.9081 | -5.658 | -6.1523 | 62.2467 | -60.6125 | -0.16022 | -0.091553 | 2.742 | -0.20599 | -8.5236 | -0.18768 | -0.091553 | 2.9022 | 54.7668 | 54.2725 | 114.2395 | 122.6715 | 2.742 | 122.6715 | 69.3329 | -0.18768 | 122.6715 | 2.742 | 69.3329 | 114.2395 | 122.6715 | -122.9233 | -122.9507
885.3281 | 122.9828 | -60.4248 | 62.352 | 0.11032 | 0.027769 | 0.019147 | 0.013428 | 0.058402 | 0.0010659 | 0.084631 | -57.7103 | 62.2467 | -60.5576 | -60.6491 | 53.8055 | 8.931 | -5.5801 | -5.9967 | 62.2833 | -60.5713 | -0.13275 | -0.10529 | 2.7145 | -0.2243 | -8.5464 | -0.14648 | -0.068665 | 2.8473 | 54.8447 | 54.4281 | 114.2303 | 122.6715 | 2.7145 | 122.7081 | 69.3558 | -0.14648 | 122.6715 | 2.7145 | 69.3558 | 114.2303 | 122.7081 | -122.9095 | -122.9233
886.3281 | 123.111 | -60.434 | 62.3383 | 0.17899 | 0.025205 | 0.020215 | 0.013428 | 0.059257 | -0.00064309 | 0.08164 | -57.6736 | 62.2696 | -60.5484 | -60.6583 | 53.8101 | 9.0225 | -5.571 | -6.1157 | 62.2421 | -60.6079 | -0.11444 | -0.068665 | 2.7603 | -0.2243 | -8.5281 | -0.17395 | -0.096131 | 2.8748 | 54.863 | 54.3182 | 114.2441 | 122.7036 | 2.7603 | 122.6761 | 69.4565 | -0.17395 | 122.7036 | 2.7603 | 69.4565 | 114.2441 | 122.6761 | -122.8867 | -122.9462
887.3281 | 123.0881 | -60.4477 | 62.352 | 0.20187 | 0.027342 | 0.018079 | 0.015778 | 0.058616 | -0.0019247 | 0.085699 | -57.6279 | 62.2421 | -60.553 | -60.6445 | 53.8422 | 9.1873 | -5.571 | -6.1752 | 62.233 | -60.6216 | -0.10529 | -0.10986 | 2.8198 | -0.19684 | -8.5098 | -0.17395 | -0.11902 | 2.9251 | 54.8767 | 54.2725 | 114.2899 | 122.6898 | 2.8198 | 122.6807 | 69.635 | -0.17395 | 122.6898 | 2.8198 | 69.635 | 114.2899 | 122.6807 | -122.905 | -122.9736
888.3281 | 123.1247 | -60.4523 | 62.3428 | 0.19424 | 0.026914 | 0.019788 | 0.014924 | 0.058189 | -2.092e-06 | 0.084417 | -57.6187 | 62.2375 | -60.585 | -60.6079 | 53.8559 | 9.2422 | -5.5847 | -6.0745 | 62.1964 | -60.6171 | -0.13275 | -0.10529 | 2.8336 | -0.15564 | -8.4869 | -0.16479 | -0.14648 | 2.9663 | 54.8676 | 54.3777 | 114.3082 | 122.6898 | 2.8336 | 122.6486 | 69.6945 | -0.16479 | 122.6898 | 2.8336 | 69.6945 | 114.3082 | 122.6486 | -122.9279 | -122.9599
889.3281 | 123.1201 | -60.4385 | 62.3428 | 0.19424 | 0.028196 | 0.021497 | 0.016419 | 0.05883 | 0.00085231 | 0.085058 | -57.5638 | 62.2787 | -60.585 | -60.5942 | 53.8696 | 9.3475 | -5.5069 | -6.0562 | 62.2147 | -60.6354 | -0.14648 | -0.064086 | 2.8748 | -0.15564 | -8.4732 | -0.19684 | -0.12817 | 3.0212 | 54.9316 | 54.3823 | 114.3082 | 122.7173 | 2.8748 | 122.6532 | 69.7861 | -0.19684 | 122.7173 | 2.8748 | 69.7861 | 114.3082 | 122.6532 | -122.9279 | -122.9782
890.3281 | 123.1384 | -60.4294 | 62.3337 | 0.16373 | 0.032041 | 0.014875 | 0.016419 | 0.059257 | 0.0014933 | 0.083563 | -57.5867 | 62.2742 | -60.5759 | -60.6171 | 53.8696 | 9.3338 | -5.5573 | -6.1203 | 62.2513 | -60.6125 | -0.14649 | -0.059509 | 2.8427 | -0.18768 | -8.464 | -0.18311 | -0.082397 | 2.9892 | 54.8721 | 54.3091 | 114.299 | 122.7036 | 2.8427 | 122.6807 | 69.7632 | -0.18311 | 122.7036 | 2.8427 | 69.7632 | 114.299 | 122.6807 | -122.9095 | -122.9462
891.3281 | 123.0835 | -60.4568 | 62.352 | 0.20187 | 0.030973 | 0.023419 | 0.017914 | 0.063529 | -0.00042929 | 0.08399 | -57.605 | 62.3199 | -60.5804 | -60.6537 | 53.8422 | 9.3384 | -5.5756 | -6.1798 | 62.2513 | -60.6583 | -0.1236 | -0.032044 | 2.8519 | -0.19684 | -8.5098 | -0.20142 | -0.10071 | 2.9755 | 54.8813 | 54.277 | 114.299 | 122.7768 | 2.8519 | 122.7081 | 69.7952 | -0.20142 | 122.7768 | 2.8519 | 69.7952 | 114.299 | 122.7081 | -122.9324 | -123.0103
892.3281 | 123.0972 | -60.4523 | 62.3199 | 0.20187 | 0.024351 | 0.020002 | 0.01471 | 0.060966 | 0.00042511 | 0.083777 | -57.5638 | 62.2696 | -60.5667 | -60.6125 | 53.8879 | 9.375 | -5.6442 | -6.1249 | 62.2238 | -60.6262 | -0.11444 | -0.050354 | 2.8885 | -0.16022 | -8.432 | -0.17395 | -0.09613 | 3.0029 | 54.808 | 54.3274 | 114.3402 | 122.7219 | 2.8885 | 122.6761 | 69.8273 | -0.17395 | 122.7219 | 2.8885 | 69.8273 | 114.3402 | 122.6761 | -122.8867 | -122.9462
893.3281 | 123.0927 | -60.4431 | 62.3474 | 0.034027 | 0.031401 | 0.021711 | 0.014283 | 0.059043 | 0.00021151 | 0.08399 | -57.5638 | 62.2879 | -60.5667 | -60.6033 | 53.9108 | 9.5489 | -5.5893 | -6.1478 | 62.2238 | -60.64 | -0.1236 | -0.059509 | 2.8793 | -0.16022 | -8.4366 | -0.19684 | -0.1236 | 3.0029 | 54.8538 | 54.2953 | 114.3539 | 122.731 | 2.8793 | 122.6669 | 69.9921 | -0.19684 | 122.731 | 2.8793 | 69.9921 | 114.3539 | 122.6669 | -122.9141 | -122.9874
894.3281 | 123.1064 | -60.4111 | 62.3428 | 0.2095 | 0.031401 | 0.024915 | 0.016846 | 0.062461 | 0.0010659 | 0.082068 | -57.605 | 62.2604 | -60.6079 | -60.5804 | 53.8605 | 9.5764 | -5.4657 | -6.015 | 62.265 | -60.6262 | -0.19684 | -0.082397 | 2.8061 | -0.16937 | -8.4824 | -0.21515 | -0.077819 | 3.0029 | 54.9454 | 54.3961 | 114.2715 | 122.6715 | 2.8061 | 122.6761 | 69.9875 | -0.21515 | 122.6715 | 2.8061 | 69.9875 | 114.2715 | 122.6761 | -122.9507 | -122.9691
895.3281 | 123.0606 | -60.466 | 62.3154 | 0.2858 | 0.029692 | 0.021711 | 0.016205 | 0.059471 | -0.00021569 | 0.08399 | -57.5409 | 62.2971 | -60.5759 | -60.6262 | 53.9062 | 9.6359 | -5.4291 | -5.9647 | 62.2604 | -60.6445 | -0.10986 | -0.018311 | 2.9251 | -0.16022 | -8.4091 | -0.17853 | -0.054932 | 3.035 | 55.0369 | 54.5013 | 114.3723 | 122.7631 | 2.9251 | 122.7264 | 70.1019 | -0.17853 | 122.7631 | 2.9251 | 70.1019 | 114.3723 | 122.7264 | -122.8912 | -122.9599
896.3281 | 123.1064 | -60.4523 | 62.3383 | 0.19424 | 0.033323 | 0.020856 | 0.015992 | 0.061607 | 0.00021151 | 0.084204 | -57.5867 | 62.3016 | -60.585 | -60.6354 | 53.8925 | 9.6176 | -5.4199 | -5.9784 | 62.2147 | -60.6537 | -0.13275 | -0.036621 | 2.8656 | -0.1831 | -8.4457 | -0.20142 | -0.1236 | 2.9984 | 55.0323 | 54.4739 | 114.3448 | 122.7539 | 2.8656 | 122.6669 | 70.0699 | -0.20142 | 122.7539 | 2.8656 | 70.0699 | 114.3448 | 122.6669 | -122.9233 | -122.9919
897.3281 | 123.0148 | -60.4843 | 62.3611 | 0.1561 | 0.029264 | 0.023419 | 0.019196 | 0.060325 | 0.0021341 | 0.084204 | -57.6233 | 62.352 | -60.5988 | -60.704 | 53.8284 | 9.5352 | -5.3284 | -6.0699 | 62.2787 | -60.6766 | -0.11444 | -0.009155 | 2.861 | -0.21973 | -8.5327 | -0.19226 | -0.082397 | 2.9755 | 55.1559 | 54.4144 | 114.3127 | 122.8363 | 2.861 | 122.7631 | 70.0195 | -0.19226 | 122.8363 | 2.861 | 70.0195 | 114.3127 | 122.7631 | -122.9599 | -123.0377
898.3281 | 122.9828 | -60.4889 | 62.3703 | -0.29404 | 0.030546 | 0.022565 | 0.018983 | 0.062248 | 0.0012795 | 0.085058 | -57.5455 | 62.3795 | -60.5988 | -60.7086 | 53.8376 | 9.5764 | -5.3421 | -6.1432 | 62.2879 | -60.6766 | -0.10986 | 0.009156 | 2.9434 | -0.21973 | -8.5327 | -0.18768 | -0.082397 | 3.0533 | 55.1468 | 54.3457 | 114.3265 | 122.8683 | 2.9434 | 122.7768 | 70.0653 | -0.18768 | 122.8683 | 2.9434 | 70.0653 | 114.3265 | 122.7768 | -122.9691 | -123.0469
899.3281 | 123.0148 | -60.4706 | 62.3795 | 0.17899 | 0.030332 | 0.021924 | 0.018128 | 0.06182 | 0.00042511 | 0.081854 | -57.5821 | 62.3749 | -60.5942 | -60.7086 | 53.8284 | 9.5444 | -5.3787 | -6.1798 | 62.2604 | -60.6812 | -0.1236 | -0.004578 | 2.8885 | -0.23804 | -8.551 | -0.21057 | -0.11902 | 3.0121 | 55.0919 | 54.2908 | 114.299 | 122.8455 | 2.8885 | 122.731 | 70.015 | -0.21057 | 122.8455 | 2.8885 | 70.015 | 114.299 | 122.731 | -122.9736 | -123.0606
900.3281 | 123.056 | -60.466 | 62.3657 | 0.24002 | 0.027769 | 0.02107 | 0.01471 | 0.064598 | 0.0023477 | 0.083777 | -57.5409 | 62.3611 | -60.5759 | -60.6903 | 53.8513 | 9.6863 | -5.4016 | -6.1249 | 62.3062 | -60.6628 | -0.10986 | -0.004578 | 2.9251 | -0.22431 | -8.5144 | -0.19684 | -0.05951 | 3.035 | 55.0644 | 54.3411 | 114.3173 | 122.8271 | 2.9251 | 122.7722 | 70.1523 | -0.19684 | 122.8271 | 2.9251 | 70.1523 | 114.3173 | 122.7722 | -122.9416 | -123.0286
901.3281 | 123.024 | -60.4752 | 62.3703 | 0.16373 | 0.03076 | 0.02107 | 0.016419 | 0.062675 | -2.092e-06 | 0.083563 | -57.5592 | 62.3703 | -60.6079 | -60.7224 | 53.8513 | 9.7321 | -5.2917 | -6.0883 | 62.2971 | -60.672 | -0.13275 | 0 | 2.916 | -0.24719 | -8.519 | -0.19684 | -0.073242 | 3.0487 | 55.1834 | 54.3869 | 114.3265 | 122.8455 | 2.916 | 122.7722 | 70.2072 | -0.19684 | 122.8455 | 2.916 | 70.2072 | 114.3265 | 122.7722 | -122.9782 | -123.0423
902.3281 | 123.0515 | -60.4614 | 62.3703 | 0.17899 | 0.030546 | 0.019147 | 0.016205 | 0.065025 | -2.092e-06 | 0.083349 | -57.5684 | 62.3932 | -60.5804 | -60.7132 | 53.833 | 9.8099 | -5.246 | -6.1523 | 62.2925 | -60.6812 | -0.11902 | 0.022888 | 2.8931 | -0.25177 | -8.5373 | -0.21973 | -0.07782 | 3.0121 | 55.2155 | 54.3091 | 114.2944 | 122.8546 | 2.8931 | 122.7539 | 70.2713 | -0.21973 | 122.8546 | 2.8931 | 70.2713 | 114.2944 | 122.7539 | -122.9507 | -123.0515
903.3281 | 123.0103 | -60.466 | 62.3657 | 2.3076 | 0.029478 | 0.019574 | 0.015992 | 0.062461 | -2.092e-06 | 0.083777 | -57.2342 | 62.4023 | -60.5759 | -60.704 | 53.8239 | 9.787 | -5.191 | -6.0928 | 62.3199 | -60.6903 | -0.10986 | 0.036621 | 3.2318 | -0.23804 | -8.5419 | -0.22431 | -0.045777 | 3.3417 | 55.275 | 54.3732 | 114.2899 | 122.8683 | 3.2318 | 122.7859 | 70.253 | -0.22431 | 122.8683 | 3.2318 | 70.253 | 114.2899 | 122.7859 | -122.9416 | -123.056
904.3281 | 122.9965 | -60.4752 | 62.3978 | 0.072174 | 0.031401 | 0.021924 | 0.015778 | 0.062034 | 0.0021341 | 0.084845 | -57.5043 | 62.4115 | -60.5804 | -60.6628 | 53.8834 | 9.874 | -5.2551 | -6.1615 | 62.3108 | -60.6766 | -0.10529 | 0.013733 | 2.9709 | -0.18768 | -8.5144 | -0.20142 | -0.086975 | 3.0762 | 55.22 | 54.3137 | 114.3585 | 122.8867 | 2.9709 | 122.7859 | 70.3491 | -0.20142 | 122.8867 | 2.9709 | 70.3491 | 114.3585 | 122.7859 | -122.9782 | -123.0743
905.3281 | 122.9828 | -60.466 | 62.4069 | 0.16373 | 0.028837 | 0.025556 | 0.018342 | 0.062248 | 0.00042511 | 0.084417 | -57.4997 | 62.3978 | -60.5988 | -60.7132 | 53.8742 | 9.8923 | -5.2277 | -6.2622 | 62.3428 | -60.6674 | -0.13275 | -0.009155 | 2.9663 | -0.24719 | -8.5327 | -0.20142 | -0.064087 | 3.0991 | 55.2383 | 54.2038 | 114.3402 | 122.8638 | 2.9663 | 122.8088 | 70.3583 | -0.20142 | 122.8638 | 2.9663 | 70.3583 | 114.3402 | 122.8088 | -123.0057 | -123.0743
906.3281 | 123.0103 | -60.4614 | 62.3795 | 0.1561 | 0.031401 | 0.026197 | 0.015778 | 0.06887 | 0.0014933 | 0.084845 | -57.5043 | 62.3932 | -60.5804 | -60.5484 | 54.1946 | 9.906 | -5.2185 | -6.2073 | 62.352 | -60.6583 | -0.11902 | 0.013732 | 2.9572 | -0.086975 | -8.1848 | -0.19684 | -0.027466 | 3.0762 | 55.2429 | 54.2542 | 114.6561 | 122.8546 | 2.9572 | 122.8134 | 70.3674 | -0.19684 | 122.8546 | 2.9572 | 70.3674 | 114.6561 | 122.8134 | -122.9599 | -123.0377
907.3281 | 122.9645 | -60.4614 | 62.4115 | 0.095062 | 0.031401 | 0.023419 | 0.016419 | 0.063743 | 0.00085231 | 0.083563 | -57.5043 | 62.3886 | -60.5759 | -60.7315 | 53.8559 | 9.8145 | -5.3787 | -6.395 | 62.352 | -60.6537 | -0.11444 | -0.022888 | 2.9572 | -0.27008 | -8.5556 | -0.19226 | -0.059509 | 3.0716 | 55.0827 | 54.0665 | 114.3173 | 122.85 | 2.9572 | 122.8134 | 70.2759 | -0.19226 | 122.85 | 2.9572 | 70.2759 | 114.3173 | 122.8134 | -122.9874 | -123.0652
908.3281 | 122.9782 | -60.4706 | 62.3795 | 0.11032 | 0.029051 | 0.021497 | 0.015992 | 0.062675 | 0.0021341 | 0.084845 | -57.4402 | 62.4207 | -60.5621 | -60.6903 | 53.9062 | 9.9335 | -5.3375 | -6.3675 | 62.352 | -60.6628 | -0.091553 | 0.041198 | 3.0304 | -0.21973 | -8.4732 | -0.19226 | -0.027466 | 3.1219 | 55.1331 | 54.1031 | 114.3768 | 122.8912 | 3.0304 | 122.8226 | 70.4041 | -0.19226 | 122.8912 | 3.0304 | 70.4041 | 114.3768 | 122.8226 | -122.9416 | -123.0423
909.3281 | 123.0057 | -60.4431 | 62.4115 | 0.041657 | 0.030973 | 0.02107 | 0.015565 | 0.062461 | 0.0019205 | 0.085058 | -57.4539 | 62.4207 | -60.5667 | -60.6766 | 53.9383 | 9.9564 | -5.3146 | -6.2622 | 62.3337 | -60.6766 | -0.1236 | 0.009155 | 2.9892 | -0.23346 | -8.4732 | -0.23346 | -0.07782 | 3.1128 | 55.1285 | 54.1809 | 114.3814 | 122.8638 | 2.9892 | 122.7768 | 70.3995 | -0.23346 | 122.8638 | 2.9892 | 70.3995 | 114.3814 | 122.7768 | -122.9782 | -123.0881
910.3281 | 123.0652 | -60.4477 | 62.384 | -0.034637 | 0.028623 | 0.024488 | 0.016419 | 0.063102 | 0.0023477 | 0.085913 | -57.4265 | 62.4207 | -60.5621 | -60.6628 | 53.9566 | 10.0662 | -5.3009 | -6.2347 | 62.3566 | -60.6537 | -0.11444 | 0.036621 | 3.0212 | -0.21515 | -8.4274 | -0.20599 | -0.027466 | 3.1357 | 55.1468 | 54.213 | 114.4043 | 122.8683 | 3.0212 | 122.8043 | 70.5139 | -0.20599 | 122.8683 | 3.0212 | 70.5139 | 114.4043 | 122.8043 | -122.9462 | -123.0377
911.3281 | 123.056 | -60.4523 | 62.3932 | -0.095673 | 0.031401 | 0.023206 | 0.013215 | 0.063957 | -0.00042929 | 0.08164 | -57.3761 | 62.4023 | -60.5438 | -60.6262 | 53.9795 | 10.0754 | -5.3009 | -6.221 | 62.3566 | -60.6491 | -0.091552 | 0.009156 | 3.0762 | -0.17395 | -8.4137 | -0.19684 | -0.036621 | 3.1677 | 55.1514 | 54.2313 | 114.4318 | 122.8546 | 3.0762 | 122.8088 | 70.5276 | -0.19684 | 122.8546 | 3.0762 | 70.5276 | 114.4318 | 122.8088 | -122.937 | -123.0423
912.3281 | 123.0423 | -60.4523 | 62.3932 | -0.042267 | 0.03076 | 0.022138 | 0.013642 | 0.062248 | 0.00042511 | 0.083777 | -57.5867 | 62.3611 | -60.5621 | -60.6125 | 54.007 | 9.9976 | -5.4108 | -6.3766 | 62.3703 | -60.6354 | -0.10986 | -0.032043 | 2.8656 | -0.16022 | -8.3862 | -0.1831 | -0.022888 | 2.9755 | 55.0415 | 54.0756 | 114.4592 | 122.8134 | 2.8656 | 122.8226 | 70.4498 | -0.1831 | 122.8134 | 2.8656 | 70.4498 | 114.4592 | 122.8226 | -122.9553 | -123.0286
913.3281 | 123.0377 | -60.466 | 62.4115 | -0.0041198 | 0.030332 | 0.023633 | 0.016205 | 0.063957 | 0.00042511 | 0.083563 | -57.3761 | 62.4115 | -60.5484 | -60.6262 | 53.9886 | 10.1166 | -5.3284 | -6.3263 | 62.3566 | -60.64 | -0.082398 | 0 | 3.0899 | -0.16022 | -8.4229 | -0.17395 | -0.054932 | 3.1723 | 55.1376 | 54.1397 | 114.4547 | 122.8775 | 3.0899 | 122.8226 | 70.5826 | -0.17395 | 122.8775 | 3.0899 | 70.5826 | 114.4547 | 122.8226 | -122.9599 | -123.0515
914.3281 | 123.0881 | -60.4385 | 62.4069 | -1.7589 | 0.029692 | 0.022992 | 0.013428 | 0.064811 | 0.0010659 | 0.083136 | -57.4127 | 62.4023 | -60.5484 | -60.5988 | 53.9841 | 10.112 | -5.4474 | -6.4316 | 62.3795 | -60.6354 | -0.10986 | -0.004577 | 3.0258 | -0.16022 | -8.4229 | -0.19684 | -0.027465 | 3.1357 | 54.9912 | 54.007 | 114.4226 | 122.8409 | 3.0258 | 122.818 | 70.5505 | -0.19684 | 122.8409 | 3.0258 | 70.5505 | 114.4226 | 122.818 | -122.9553 | -123.0423
915.3281 | 123.0377 | -60.4111 | 62.4023 | -0.027008 | 0.030332 | 0.020002 | 0.014924 | 0.063529 | -0.0014975 | 0.082495 | -57.3303 | 62.3978 | -60.5484 | -60.6033 | 53.9795 | 10.0204 | -5.6168 | -6.3904 | 62.3749 | -60.6171 | -0.13733 | -0.004578 | 3.0807 | -0.19226 | -8.4229 | -0.20599 | -0.027466 | 3.2181 | 54.7943 | 54.0207 | 114.3906 | 122.8088 | 3.0807 | 122.7859 | 70.4315 | -0.20599 | 122.8088 | 3.0807 | 70.4315 | 114.3906 | 122.7859 | -122.9507 | -123.0194
916.3281 | 123.056 | -60.4065 | 62.3978 | -0.1033 | 0.029478 | 0.023633 | 0.015992 | 0.065666 | -0.00021569 | 0.084845 | -57.3349 | 62.4207 | -60.5621 | -60.6216 | 54.0161 | 10.1166 | -5.5435 | -6.5552 | 62.4161 | -60.64 | -0.15564 | 0.022888 | 3.0716 | -0.21515 | -8.3817 | -0.23346 | 0.018311 | 3.2272 | 54.863 | 53.8513 | 114.4226 | 122.8271 | 3.0716 | 122.8226 | 70.5231 | -0.23346 | 122.8271 | 3.0716 | 70.5231 | 114.4226 | 122.8226 | -122.9599 | -123.0377
917.3281 | 123.0515 | -60.4202 | 62.3978 | -0.13382 | 0.029478 | 0.019788 | 0.012787 | 0.063529 | 0.00063871 | 0.084845 | -57.3532 | 62.4435 | -60.5347 | -60.64 | 54.007 | 10.1486 | -5.4977 | -6.5277 | 62.3932 | -60.6125 | -0.11444 | 0.045776 | 3.067 | -0.21973 | -8.3908 | -0.19226 | -0.004578 | 3.1815 | 54.9225 | 53.8925 | 114.4272 | 122.8638 | 3.067 | 122.8134 | 70.5688 | -0.19226 | 122.8638 | 3.067 | 70.5688 | 114.4272 | 122.8134 | -122.9324 | -123.0103
918.3281 | 123.0194 | -60.4385 | 62.4298 | -0.29404 | 0.031828 | 0.021924 | 0.011933 | 0.062034 | 0.00042511 | 0.082708 | -57.3944 | 62.4023 | -60.5484 | -60.6857 | 54.0024 | 10.1395 | -5.4428 | -6.4865 | 62.4161 | -60.6262 | -0.10986 | -0.027466 | 3.0441 | -0.24719 | -8.4274 | -0.18768 | -0.013733 | 3.154 | 54.9957 | 53.952 | 114.4409 | 122.8409 | 3.0441 | 122.8546 | 70.578 | -0.18768 | 122.8409 | 3.0441 | 70.578 | 114.4409 | 122.8546 | -122.9782 | -123.056
919.3281 | 123.0011 | -60.4202 | 62.4344 | -0.14908 | 0.032041 | 0.019574 | 0.013856 | 0.061607 | -0.00064309 | 0.085486 | -57.3669 | 62.4161 | -60.5576 | -60.6583 | 54.007 | 10.1074 | -5.4749 | -6.5277 | 62.4115 | -60.6216 | -0.13733 | -0.01831 | 3.0533 | -0.23804 | -8.4274 | -0.20142 | -0.022888 | 3.1906 | 54.9454 | 53.8925 | 114.4272 | 122.8363 | 3.0533 | 122.8317 | 70.5276 | -0.20142 | 122.8363 | 3.0533 | 70.5276 | 114.4272 | 122.8317 | -122.9919 | -123.056
920.3281 | 123.0652 | -60.4294 | 62.4069 | -0.12619 | 0.02841 | 0.023419 | 0.015137 | 0.060752 | -0.00042929 | 0.083777 | -57.3715 | 62.4023 | -60.5301 | -60.6171 | 54.0207 | 10.1669 | -5.5069 | -6.5414 | 62.4161 | -60.6216 | -0.10071 | -0.004577 | 3.0579 | -0.18768 | -8.3862 | -0.19226 | 0.009156 | 3.1586 | 54.9225 | 53.8879 | 114.4501 | 122.8317 | 3.0579 | 122.8455 | 70.5963 | -0.19226 | 122.8317 | 3.0579 | 70.5963 | 114.4501 | 122.8455 | -122.937 | -123.0286
921.3438 | 123.1064 | -60.3973 | 62.3474 | 0.18662 | 0.028623 | 0.021497 | 0.010865 | 0.063316 | -0.0010703 | 0.082708 | -57.3257 | 62.2879 | -60.5484 | -60.6079 | 54.0756 | 10.1944 | -5.7632 | -6.5048 | 62.3245 | -60.5988 | -0.15106 | -0.059509 | 3.0716 | -0.21057 | -8.2718 | -0.20142 | -0.022888 | 3.2227 | 54.6341 | 53.8925 | 114.473 | 122.6852 | 3.0716 | 122.7219 | 70.5917 | -0.20142 | 122.6852 | 3.0716 | 70.5917 | 114.473 | 122.7219 | -122.8958 | -122.9462
922.3281 | 123.0057 | -60.4065 | 62.439 | -0.16434 | 0.028837 | 0.023633 | 0.01471 | 0.060539 | 0.00063871 | 0.082708 | -57.3761 | 62.4161 | -60.553 | -60.6445 | 53.9978 | 10.0983 | -5.6488 | -6.7245 | 62.4252 | -60.6125 | -0.14648 | -0.022888 | 3.0304 | -0.23804 | -8.4412 | -0.20599 | -0.013733 | 3.1769 | 54.7577 | 53.6819 | 114.4043 | 122.8226 | 3.0304 | 122.8317 | 70.5048 | -0.20599 | 122.8226 | 3.0304 | 70.5048 | 114.4043 | 122.8317 | -122.9919 | -123.0515
923.3281 | 122.9874 | -60.4111 | 62.4619 | -0.16434 | 0.029692 | 0.01872 | 0.012574 | 0.06182 | -0.0021383 | 0.082922 | -57.3532 | 62.384 | -60.5392 | -60.6445 | 54.0253 | 10.1532 | -5.5847 | -6.6788 | 62.4344 | -60.6171 | -0.12817 | -0.07782 | 3.0579 | -0.23346 | -8.4366 | -0.20599 | -0.027466 | 3.186 | 54.8264 | 53.7323 | 114.4363 | 122.7951 | 3.0579 | 122.8455 | 70.5643 | -0.20599 | 122.7951 | 3.0579 | 70.5643 | 114.4363 | 122.8455 | -123.0011 | -123.0789
924.3281 | 123.0148 | -60.4065 | 62.4664 | -0.22537 | 0.026914 | 0.023419 | 0.011719 | 0.06182 | -0.00085669 | 0.083136 | -57.3029 | 62.3886 | -60.5209 | -60.6354 | 54.0436 | 10.1761 | -5.6305 | -6.6559 | 62.4161 | -60.585 | -0.11444 | -0.07782 | 3.1036 | -0.22888 | -8.4229 | -0.17853 | -0.050354 | 3.2181 | 54.776 | 53.7506 | 114.4501 | 122.7951 | 3.1036 | 122.8226 | 70.5826 | -0.17853 | 122.7951 | 3.1036 | 70.5826 | 114.4501 | 122.8226 | -122.9874 | -123.0515
925.3281 | 123.0148 | -60.4202 | 62.4664 | -0.233 | 0.027769 | 0.022351 | 0.011719 | 0.062034 | 0.0010659 | 0.084417 | -57.3074 | 62.384 | -60.5164 | -60.5896 | 54.039 | 10.112 | -5.7495 | -6.7245 | 62.4207 | -60.5988 | -0.09613 | -0.082398 | 3.1128 | -0.16937 | -8.4274 | -0.17853 | -0.045777 | 3.2089 | 54.6707 | 53.6957 | 114.4592 | 122.8043 | 3.1128 | 122.8409 | 70.5322 | -0.17853 | 122.8043 | 3.1128 | 70.5322 | 114.4592 | 122.8409 | -122.9828 | -123.0652
926.3438 | 123.0881 | -60.4202 | 62.4344 | -0.69077 | 0.031828 | 0.021924 | 0.01706 | 0.061607 | 0.0012795 | 0.084417 | -57.2571 | 62.4298 | -60.5026 | -60.5667 | 54.0573 | 10.1486 | -5.896 | -6.8436 | 62.4252 | -60.5988 | -0.082398 | -0.004577 | 3.1631 | -0.14648 | -8.3771 | -0.17853 | -0.009155 | 3.2455 | 54.5242 | 53.5767 | 114.4775 | 122.85 | 3.1631 | 122.8455 | 70.5688 | -0.17853 | 122.85 | 3.1631 | 70.5688 | 114.4775 | 122.8455 | -122.937 | -123.0331
927.3281 | 123.0057 | -60.3973 | 62.4847 | -0.17197 | 0.029051 | 0.022351 | 0.013428 | 0.062461 | 0.0012795 | 0.082708 | -57.312 | 62.4161 | -60.5392 | -60.6171 | 54.0298 | 10.1166 | -5.777 | -6.9031 | 62.4252 | -60.6125 | -0.14191 | -0.068664 | 3.0853 | -0.21973 | -8.4549 | -0.21515 | -0.059509 | 3.2272 | 54.6204 | 53.4943 | 114.4272 | 122.8134 | 3.0853 | 122.8226 | 70.5139 | -0.21515 | 122.8134 | 3.0853 | 70.5139 | 114.4272 | 122.8226 | -123.024 | -123.0972
928.3281 | 123.0194 | -60.3928 | 62.4619 | -0.21774 | 0.027555 | 0.020002 | 0.012574 | 0.060752 | -0.00064309 | 0.084631 | -57.3029 | 62.4298 | -60.5301 | -60.6445 | 54.0527 | 10.0754 | -5.8914 | -7.1136 | 62.4252 | -60.6216 | -0.13733 | -0.032043 | 3.0899 | -0.25177 | -8.4091 | -0.22888 | -0.036621 | 3.2272 | 54.5013 | 53.2791 | 114.4455 | 122.8226 | 3.0899 | 122.818 | 70.4681 | -0.22888 | 122.8226 | 3.0899 | 70.4681 | 114.4455 | 122.818 | -122.9919 | -123.0835
929.3281 | 123.0011 | -60.4019 | 62.4481 | 0.65964 | 0.029692 | 0.021711 | 0.013215 | 0.060966 | -2.092e-06 | 0.082495 | -57.2113 | 62.4161 | -60.5072 | -60.6125 | 54.0436 | 10.0983 | -5.9372 | -7.164 | 62.4619 | -60.5804 | -0.10529 | -0.032043 | 3.1906 | -0.21057 | -8.4045 | -0.17853 | 0.013733 | 3.2959 | 54.4647 | 53.2379 | 114.4455 | 122.818 | 3.1906 | 122.8638 | 70.5002 | -0.17853 | 122.818 | 3.1906 | 70.5002 | 114.4455 | 122.8638 | -122.9553 | -123.0286
930.3281 | 123.0011 | -60.4111 | 62.4573 | -0.19485 | 0.030546 | 0.018933 | 0.014283 | 0.063529 | -0.00042929 | 0.08399 | -57.3212 | 62.4252 | -60.5209 | -60.5942 | 53.9703 | 9.993 | -5.9647 | -7.2556 | 62.4435 | -60.5942 | -0.10986 | -0.032043 | 3.0899 | -0.18311 | -8.4869 | -0.18311 | -0.013733 | 3.1998 | 54.4464 | 53.1555 | 114.3814 | 122.8363 | 3.0899 | 122.8546 | 70.4041 | -0.18311 | 122.8363 | 3.0899 | 70.4041 | 114.3814 | 122.8546 | -122.9782 | -123.0515
931.3438 | 122.9965 | -60.3973 | 62.471 | 0.026398 | 0.032896 | 0.024915 | 0.016419 | 0.062675 | 0.00021151 | 0.085058 | -57.2662 | 62.4069 | -60.498 | -60.5988 | 54.0436 | 10.0204 | -6.1157 | -7.1686 | 62.4252 | -60.5988 | -0.10071 | -0.064087 | 3.1311 | -0.20142 | -8.4274 | -0.20142 | -0.045776 | 3.2318 | 54.2816 | 53.2288 | 114.4409 | 122.8043 | 3.1311 | 122.8226 | 70.4178 | -0.20142 | 122.8043 | 3.1311 | 70.4178 | 114.4409 | 122.8226 | -122.9691 | -123.0698
932.3281 | 123.0789 | -60.3928 | 62.4573 | -0.18723 | 0.027342 | 0.019147 | 0.011719 | 0.060752 | 0.00021151 | 0.082922 | -57.2433 | 62.3749 | -60.498 | -60.5301 | 54.1489 | 10.1349 | -6.1798 | -7.0084 | 62.3795 | -60.553 | -0.10529 | -0.082397 | 3.1494 | -0.13733 | -8.3084 | -0.16022 | -0.077819 | 3.2547 | 54.213 | 53.3844 | 114.5416 | 122.7676 | 3.1494 | 122.7722 | 70.5276 | -0.16022 | 122.7676 | 3.1494 | 70.5276 | 114.5416 | 122.7722 | -122.9553 | -123.0103
933.3281 | 123.024 | -60.3836 | 62.4527 | -0.21011 | 0.029051 | 0.018293 | 0.014283 | 0.061607 | -2.092e-06 | 0.084417 | -57.2983 | 62.3978 | -60.5164 | -60.6033 | 54.1031 | 10.1028 | -6.0425 | -7.1503 | 62.4298 | -60.5713 | -0.13275 | -0.054932 | 3.0853 | -0.21973 | -8.3496 | -0.18768 | -0.022888 | 3.2181 | 54.3411 | 53.2333 | 114.4867 | 122.7814 | 3.0853 | 122.8134 | 70.4865 | -0.18768 | 122.7814 | 3.0853 | 70.4865 | 114.4867 | 122.8134 | -122.9691 | -123.024
934.3281 | 122.9828 | -60.3745 | 62.4756 | -0.1796 | 0.027769 | 0.021924 | 0.014496 | 0.05883 | -0.0010703 | 0.083563 | -57.4173 | 62.4161 | -60.4752 | -60.6812 | 54.0665 | 10.0433 | -6.2485 | -7.3929 | 62.4573 | -60.5759 | -0.10071 | -0.059509 | 2.9572 | -0.3067 | -8.4091 | -0.20142 | -0.018311 | 3.0579 | 54.126 | 52.9816 | 114.4409 | 122.7905 | 2.9572 | 122.8317 | 70.4178 | -0.20142 | 122.7905 | 2.9572 | 70.4178 | 114.4409 | 122.8317 | -122.9507 | -123.0515
935.3281 | 123.0103 | -60.3928 | 62.4664 | -0.21011 | 0.030546 | 0.019574 | 0.014496 | 0.059471 | -0.00021569 | 0.08164 | -57.28 | 62.4207 | -60.498 | -60.4523 | 54.3228 | 9.9792 | -6.4087 | -7.3196 | 62.4664 | -60.5576 | -0.10529 | -0.045777 | 3.1128 | -0.05951 | -8.1436 | -0.16479 | 0 | 3.2181 | 53.9841 | 53.0731 | 114.7156 | 122.8134 | 3.1128 | 122.8592 | 70.372 | -0.16479 | 122.8134 | 3.1128 | 70.372 | 114.7156 | 122.8592 | -122.9645 | -123.024
936.3438 | 122.9919 | -60.4019 | 62.4481 | 0.072174 | 0.03076 | 0.022565 | 0.015992 | 0.062889 | -0.0017111 | 0.083777 | -57.2708 | 62.4435 | -60.5209 | -60.64 | 54.0344 | 9.8419 | -6.4911 | -7.5302 | 62.4527 | -60.6079 | -0.11902 | -0.004578 | 3.1311 | -0.23804 | -8.4137 | -0.20599 | 0.004578 | 3.2501 | 53.9108 | 52.8717 | 114.4363 | 122.8455 | 3.1311 | 122.8546 | 70.2438 | -0.20599 | 122.8455 | 3.1311 | 70.2438 | 114.4363 | 122.8546 | -122.9691 | -123.056
937.3281 | 122.9965 | -60.379 | 62.4893 | -0.22537 | 0.026701 | 0.020002 | 0.010651 | 0.060111 | -0.00064309 | 0.084845 | -57.2937 | 62.4252 | -60.5072 | -60.5942 | 54.1122 | 9.9976 | -6.3995 | -7.4295 | 62.4527 | -60.5713 | -0.12817 | -0.064087 | 3.0853 | -0.21515 | -8.3771 | -0.19226 | -0.036621 | 3.2135 | 53.9795 | 52.9495 | 114.4913 | 122.8043 | 3.0853 | 122.8317 | 70.3766 | -0.19226 | 122.8043 | 3.0853 | 70.3766 | 114.4913 | 122.8317 | -122.9965 | -123.0606
938.3281 | 123.0972 | -60.347 | 62.4619 | -0.14908 | 0.02841 | 0.01872 | 0.009156 | 0.060539 | 0.0017069 | 0.083349 | -57.2342 | 62.384 | -60.4797 | -60.4935 | 54.1855 | 10.025 | -6.6193 | -7.3929 | 62.4161 | -60.5392 | -0.13275 | -0.07782 | 3.1128 | -0.14648 | -8.2764 | -0.19226 | -0.045776 | 3.2455 | 53.7277 | 52.9541 | 114.5325 | 122.731 | 3.1128 | 122.7631 | 70.372 | -0.19226 | 122.731 | 3.1128 | 70.372 | 114.5325 | 122.7631 | -122.9416 | -123.0011
939.3281 | 123.1018 | -60.3287 | 62.4344 | -0.13382 | 0.028837 | 0.017865 | 0.012787 | 0.060111 | 0.0014933 | 0.08399 | -57.2205 | 62.352 | -60.4568 | -60.5026 | 54.1992 | 10.0616 | -6.7154 | -7.4707 | 62.4115 | -60.5392 | -0.12817 | -0.082397 | 3.1082 | -0.17395 | -8.2352 | -0.21057 | -0.022888 | 3.2364 | 53.6133 | 52.858 | 114.5279 | 122.6807 | 3.1082 | 122.7402 | 70.3903 | -0.21057 | 122.6807 | 3.1082 | 70.3903 | 114.5279 | 122.7402 | -122.8912 | -122.9736
940.3281 | 123.0972 | -60.347 | 62.4481 | -0.18723 | 0.024778 | 0.023847 | 0.011506 | 0.060752 | -0.00042929 | 0.080572 | -57.2433 | 62.3795 | -60.4797 | -60.5301 | 54.1855 | 10.0616 | -6.5552 | -7.4295 | 62.4069 | -60.5209 | -0.13275 | -0.068664 | 3.1036 | -0.18311 | -8.2626 | -0.17395 | -0.041199 | 3.2364 | 53.7918 | 52.9175 | 114.5325 | 122.7264 | 3.1036 | 122.7539 | 70.4086 | -0.17395 | 122.7264 | 3.1036 | 70.4086 | 114.5325 | 122.7539 | -122.9279 | -122.9691
941.3281 | 122.9965 | -60.3882 | 62.4893 | -0.21011 | 0.027769 | 0.019361 | 0.013215 | 0.060752 | 0.00042511 | 0.084845 | -57.28 | 62.4023 | -60.4797 | -60.5667 | 54.1626 | 10.0571 | -6.5048 | -7.4432 | 62.4573 | -60.5301 | -0.091552 | -0.086975 | 3.1082 | -0.17853 | -8.3267 | -0.14191 | -0.032044 | 3.1998 | 53.8834 | 52.9449 | 114.5508 | 122.7905 | 3.1082 | 122.8455 | 70.4453 | -0.14191 | 122.7905 | 3.1082 | 70.4453 | 114.5508 | 122.8455 | -122.9691 | -123.0194
942.3281 | 123.0972 | -60.347 | 62.4664 | -0.13382 | 0.025633 | 0.023633 | 0.013642 | 0.059898 | -0.00042929 | 0.081 | -57.2296 | 62.352 | -60.466 | -60.4843 | 54.2175 | 10.1303 | -6.6833 | -7.4936 | 62.3703 | -60.498 | -0.11902 | -0.11444 | 3.1174 | -0.13733 | -8.2489 | -0.15106 | -0.096131 | 3.2364 | 53.6636 | 52.8534 | 114.5645 | 122.699 | 3.1174 | 122.7173 | 70.4773 | -0.15106 | 122.699 | 3.1174 | 70.4773 | 114.5645 | 122.7173 | -122.9324 | -122.9645
943.3281 | 123.111 | -60.3561 | 62.4619 | -0.18723 | 0.027342 | 0.021497 | 0.014069 | 0.059898 | -0.0023519 | 0.079718 | -57.2159 | 62.3657 | -60.4477 | -60.4935 | 54.2038 | 10.1074 | -6.6925 | -7.5211 | 62.4069 | -60.5347 | -0.091553 | -0.09613 | 3.1403 | -0.13733 | -8.2581 | -0.17853 | -0.054932 | 3.2318 | 53.6636 | 52.8351 | 114.5599 | 122.7219 | 3.1403 | 122.7631 | 70.4636 | -0.17853 | 122.7219 | 3.1403 | 70.4636 | 114.5599 | 122.7631 | -122.9095 | -122.9965
944.3281 | 123.0972 | -60.3378 | 62.4802 | -0.14908 | 0.025846 | 0.017011 | 0.011719 | 0.058189 | 0.00021151 | 0.08399 | -57.2617 | 62.3611 | -60.4523 | -60.5026 | 54.2221 | 10.1303 | -6.7978 | -7.5577 | 62.4069 | -60.498 | -0.11444 | -0.11902 | 3.0762 | -0.1648 | -8.2581 | -0.16022 | -0.073243 | 3.1906 | 53.54 | 52.7802 | 114.5599 | 122.699 | 3.0762 | 122.7448 | 70.4681 | -0.16022 | 122.699 | 3.0762 | 70.4681 | 114.5599 | 122.7448 | -122.9324 | -122.9782
945.3281 | 123.1201 | -60.3104 | 62.4893 | -0.13382 | 0.027555 | 0.016584 | 0.012787 | 0.060325 | -0.0012839 | 0.083136 | -57.2159 | 62.352 | -60.4706 | -60.4752 | 54.2221 | 10.1624 | -6.871 | -7.5897 | 62.4069 | -60.5118 | -0.16022 | -0.13733 | 3.0945 | -0.16479 | -8.2672 | -0.20142 | -0.082398 | 3.2547 | 53.4393 | 52.7206 | 114.5325 | 122.6624 | 3.0945 | 122.7173 | 70.4727 | -0.20142 | 122.6624 | 3.0945 | 70.4727 | 114.5325 | 122.7173 | -122.9599 | -123.0011
946.3281 | 123.1338 | -60.3287 | 62.4756 | -0.088043 | 0.026914 | 0.014661 | 0.01236 | 0.05883 | -0.00085669 | 0.082495 | -57.2067 | 62.3474 | -60.4477 | -60.4935 | 54.2267 | 10.1349 | -6.8985 | -7.6813 | 62.4252 | -60.4843 | -0.11902 | -0.12817 | 3.1219 | -0.16479 | -8.2489 | -0.15564 | -0.050354 | 3.241 | 53.4302 | 52.6474 | 114.5554 | 122.6761 | 3.1219 | 122.7539 | 70.4636 | -0.15564 | 122.6761 | 3.1219 | 70.4636 | 114.5554 | 122.7539 | -122.9233 | -122.9599
947.3281 | 123.1338 | -60.3195 | 62.4619 | -0.019379 | 0.027555 | 0.019361 | 0.013428 | 0.057334 | -0.00085669 | 0.083777 | -57.3257 | 62.3657 | -60.466 | -60.5255 | 54.1809 | 10.1578 | -6.926 | -7.7728 | 62.384 | -60.4935 | -0.14648 | -0.09613 | 2.9938 | -0.20599 | -8.2809 | -0.17395 | -0.07782 | 3.1403 | 53.3936 | 52.5467 | 114.5004 | 122.6852 | 2.9938 | 122.7036 | 70.4773 | -0.17395 | 122.6852 | 2.9938 | 70.4773 | 114.5004 | 122.7036 | -122.9279 | -122.9553
948.3281 | 123.1201 | -60.3012 | 62.4573 | 0.37735 | 0.029051 | 0.019788 | 0.015137 | 0.058189 | -0.0012839 | 0.082708 | -57.2067 | 62.3474 | -60.466 | -60.434 | 54.2542 | 10.1532 | -6.9992 | -7.782 | 62.4023 | -60.4797 | -0.16479 | -0.10986 | 3.0945 | -0.13275 | -8.2031 | -0.17853 | -0.054931 | 3.2593 | 53.302 | 52.5192 | 114.5554 | 122.6486 | 3.0945 | 122.7036 | 70.4544 | -0.17853 | 122.6486 | 3.0945 | 70.4544 | 114.5554 | 122.7036 | -122.9233 | -122.937
949.3281 | 123.143 | -60.3149 | 62.471 | -0.080414 | 0.026914 | 0.024701 | 0.016846 | 0.058189 | -0.0036337 | 0.082281 | -57.3303 | 62.3611 | -60.4111 | -60.5438 | 54.2633 | 10.2676 | -7.0999 | -7.8461 | 62.4115 | -60.4935 | -0.096131 | -0.10986 | 2.9846 | -0.22888 | -8.2077 | -0.17853 | -0.059509 | 3.0807 | 53.215 | 52.4689 | 114.5782 | 122.6761 | 2.9846 | 122.7264 | 70.5826 | -0.17853 | 122.6761 | 2.9846 | 70.5826 | 114.5782 | 122.7264 | -122.8821 | -122.9645
950.3281 | 123.2208 | -60.2829 | 62.4619 | -0.072784 | 0.026914 | 0.017224 | 0.012787 | 0.057334 | -0.0017111 | 0.081854 | -57.2113 | 62.3428 | -60.4477 | -60.4385 | 54.2679 | 10.2264 | -7.0862 | -7.8781 | 62.384 | -60.4706 | -0.16479 | -0.11902 | 3.0716 | -0.15564 | -8.194 | -0.18768 | -0.07782 | 3.2364 | 53.1967 | 52.4048 | 114.5508 | 122.6257 | 3.0716 | 122.6669 | 70.5093 | -0.18768 | 122.6257 | 3.0716 | 70.5093 | 114.5508 | 122.6669 | -122.9095 | -122.9324
951.3281 | 123.0972 | -60.3195 | 62.4893 | 0.0035097 | 0.024137 | 0.017224 | 0.013642 | 0.057975 | 0.00021151 | 0.082708 | -57.2342 | 62.352 | -60.4431 | -60.4706 | 54.2633 | 10.1624 | -7.1274 | -7.8964 | 62.4207 | -60.498 | -0.1236 | -0.13733 | 3.0853 | -0.15106 | -8.226 | -0.17853 | -0.068665 | 3.2089 | 53.1921 | 52.4231 | 114.5828 | 122.6715 | 3.0853 | 122.7402 | 70.4819 | -0.17853 | 122.6715 | 3.0853 | 70.4819 | 114.5828 | 122.7402 | -122.9324 | -122.9874
952.3281 | 123.0927 | -60.3333 | 62.4573 | 0.011139 | 0.025633 | 0.021924 | 0.013856 | 0.056907 | -0.0012839 | 0.082281 | -57.3212 | 62.3703 | -60.4614 | -60.5209 | 54.1946 | 10.0845 | -7.1777 | -7.9971 | 62.3932 | -60.4935 | -0.12817 | -0.086975 | 3.0121 | -0.18768 | -8.2626 | -0.16022 | -0.064087 | 3.1403 | 53.1555 | 52.3361 | 114.5279 | 122.7036 | 3.0121 | 122.7264 | 70.4178 | -0.16022 | 122.7036 | 3.0121 | 70.4178 | 114.5279 | 122.7264 | -122.9187 | -122.9507
953.3281 | 123.0835 | -60.3333 | 62.4619 | 0.83511 | 0.025633 | 0.020429 | 0.014496 | 0.057334 | -0.00021569 | 0.084417 | -57.3715 | 62.352 | -60.4752 | -60.5392 | 54.1672 | 10.0754 | -7.2235 | -8.0521 | 62.4023 | -60.5164 | -0.14191 | -0.10986 | 2.9617 | -0.20599 | -8.2947 | -0.1831 | -0.059509 | 3.1036 | 53.1097 | 52.2812 | 114.5004 | 122.6852 | 2.9617 | 122.7356 | 70.4086 | -0.1831 | 122.6852 | 2.9617 | 70.4086 | 114.5004 | 122.7356 | -122.937 | -122.9782
954.3281 | 123.1018 | -60.3241 | 62.4893 | 0.018768 | 0.029905 | 0.020002 | 0.011079 | 0.055839 | -0.00021569 | 0.081854 | -57.3578 | 62.3703 | -60.4706 | -60.5026 | 54.1946 | 9.9838 | -7.402 | -8.2809 | 62.4115 | -60.4706 | -0.14648 | -0.11902 | 2.9663 | -0.17853 | -8.2947 | -0.14648 | -0.07782 | 3.1128 | 52.9221 | 52.0432 | 114.5187 | 122.6944 | 2.9663 | 122.7356 | 70.3079 | -0.14648 | 122.6944 | 2.9663 | 70.3079 | 114.5187 | 122.7356 | -122.9599 | -122.9599
955.3281 | 123.0972 | -60.2966 | 62.4847 | -0.019379 | 0.026487 | 0.019147 | 0.014069 | 0.056907 | -0.0014975 | 0.085058 | -57.2708 | 62.3886 | -60.4523 | -60.4843 | 54.2084 | 10.0479 | -7.4341 | -8.1985 | 62.384 | -60.4797 | -0.15564 | -0.09613 | 3.0258 | -0.18768 | -8.2764 | -0.18311 | -0.10071 | 3.1815 | 52.8625 | 52.0981 | 114.505 | 122.6852 | 3.0258 | 122.6807 | 70.3445 | -0.18311 | 122.6852 | 3.0258 | 70.3445 | 114.505 | 122.6807 | -122.937 | -122.9645
956.3281 | 123.0743 | -60.3241 | 62.4802 | -0.011749 | 0.026274 | 0.019788 | 0.013001 | 0.060111 | -0.00042929 | 0.081854 | -57.3441 | 62.352 | -60.4523 | -60.498 | 54.2084 | 10.0388 | -7.3608 | -8.1757 | 62.4207 | -60.5118 | -0.12817 | -0.12817 | 2.98 | -0.17395 | -8.2718 | -0.18768 | -0.05951 | 3.1082 | 52.9633 | 52.1484 | 114.5325 | 122.6761 | 2.98 | 122.7448 | 70.3629 | -0.18768 | 122.6761 | 2.98 | 70.3629 | 114.5325 | 122.7448 | -122.9324 | -122.9919
957.3281 | 123.0927 | -60.3149 | 62.5031 | 0.0035097 | 0.027555 | 0.02107 | 0.013215 | 0.058189 | -0.0019247 | 0.08164 | -57.3532 | 62.3749 | -60.4477 | -60.5255 | 54.1763 | 9.9884 | -7.4753 | -8.3588 | 62.4207 | -60.4752 | -0.13275 | -0.12817 | 2.9617 | -0.21057 | -8.3267 | -0.16022 | -0.082398 | 3.0945 | 52.8397 | 51.9562 | 114.4913 | 122.6898 | 2.9617 | 122.7356 | 70.3033 | -0.16022 | 122.6898 | 2.9617 | 70.3033 | 114.4913 | 122.7356 | -122.9507 | -122.9782
958.3281 | 123.0698 | -60.3012 | 62.4847 | 0.041657 | 0.026701 | 0.021924 | 0.014924 | 0.059471 | -0.0010703 | 0.080786 | -57.0969 | 62.3932 | -60.4111 | -60.553 | 54.1946 | 10.0113 | -7.5027 | -8.4 | 62.3657 | -60.4889 | -0.10986 | -0.091553 | 3.2043 | -0.25177 | -8.2901 | -0.18768 | -0.11902 | 3.3142 | 52.7985 | 51.9012 | 114.4958 | 122.6944 | 3.2043 | 122.6669 | 70.3125 | -0.18768 | 122.6944 | 3.2043 | 70.3125 | 114.4958 | 122.6669 | -122.8958 | -122.9736
959.3281 | 123.0698 | -60.3241 | 62.4893 | 0.24002 | 0.026914 | 0.018079 | 0.015351 | 0.058189 | 0.0029885 | 0.084417 | -57.3257 | 62.3291 | -60.4248 | -60.5026 | 54.2084 | 10.0616 | -7.5806 | -8.2901 | 62.3886 | -60.4935 | -0.10071 | -0.16022 | 2.9984 | -0.17853 | -8.2809 | -0.16937 | -0.10071 | 3.0991 | 52.7435 | 52.034 | 114.5325 | 122.6532 | 2.9984 | 122.7127 | 70.3857 | -0.16937 | 122.6532 | 2.9984 | 70.3857 | 114.5325 | 122.7127 | -122.9141 | -122.9828
960.3281 | 123.1018 | -60.3058 | 62.4756 | 0.2095 | 0.026274 | 0.016156 | 0.016205 | 0.057975 | -0.0017111 | 0.082281 | -57.3441 | 62.3611 | -60.4431 | -60.4752 | 54.245 | 10.0571 | -7.6218 | -8.3038 | 62.3932 | -60.4843 | -0.13733 | -0.11444 | 2.9617 | -0.16937 | -8.2306 | -0.17853 | -0.082398 | 3.0991 | 52.684 | 52.002 | 114.5508 | 122.6669 | 2.9617 | 122.699 | 70.3629 | -0.17853 | 122.6669 | 2.9617 | 70.3629 | 114.5508 | 122.699 | -122.9187 | -122.9599
961.3281 | 123.0835 | -60.3104 | 62.4893 | 0.11795 | 0.026914 | 0.019361 | 0.012574 | 0.057975 | 0.00021151 | 0.082281 | -57.3807 | 62.3657 | -60.4294 | -60.5164 | 54.1992 | 9.9838 | -7.6309 | -8.2352 | 62.4207 | -60.4431 | -0.11902 | -0.1236 | 2.9297 | -0.20599 | -8.2901 | -0.13275 | -0.068665 | 3.0487 | 52.6794 | 52.0752 | 114.5096 | 122.6761 | 2.9297 | 122.731 | 70.2942 | -0.13275 | 122.6761 | 2.9297 | 70.2942 | 114.5096 | 122.731 | -122.9187 | -122.9324
962.3281 | 123.0652 | -60.2921 | 62.4847 | 0.17899 | 0.026274 | 0.022992 | 0.013001 | 0.058189 | -0.0021383 | 0.084204 | -57.3303 | 62.3703 | -60.4385 | -60.5072 | 54.2221 | 10.0067 | -7.7728 | -8.638 | 62.3886 | -60.4797 | -0.14648 | -0.11444 | 2.9617 | -0.21515 | -8.2626 | -0.18768 | -0.09613 | 3.1082 | 52.5192 | 51.6541 | 114.5142 | 122.6624 | 2.9617 | 122.6807 | 70.2988 | -0.18768 | 122.6624 | 2.9617 | 70.2988 | 114.5142 | 122.6807 | -122.9233 | -122.9645
963.3281 | 123.0972 | -60.2966 | 62.4847 | 0.1561 | 0.027128 | 0.020856 | 0.01471 | 0.058189 | 0.00021151 | 0.082495 | -57.3395 | 62.3886 | -60.4248 | -60.4935 | 54.2221 | 9.9747 | -7.869 | -8.6884 | 62.3795 | -60.498 | -0.12817 | -0.09613 | 2.9572 | -0.19684 | -8.2626 | -0.20142 | -0.10529 | 3.0853 | 52.4277 | 51.6083 | 114.5187 | 122.6852 | 2.9572 | 122.6761 | 70.2713 | -0.20142 | 122.6852 | 2.9572 | 70.2713 | 114.5187 | 122.6761 | -122.9095 | -122.9828
964.3281 | 123.0972 | -60.2921 | 62.4619 | 0.22476 | 0.027983 | 0.023419 | 0.015778 | 0.058616 | -0.00085669 | 0.082281 | -57.3212 | 62.3886 | -60.4385 | -60.466 | 54.2358 | 10.0021 | -7.9559 | -8.725 | 62.3703 | -60.5072 | -0.14648 | -0.073242 | 2.9709 | -0.17395 | -8.226 | -0.21515 | -0.091553 | 3.1174 | 52.3361 | 51.5671 | 114.5279 | 122.6807 | 2.9709 | 122.6624 | 70.2942 | -0.21515 | 122.6807 | 2.9709 | 70.2942 | 114.5279 | 122.6624 | -122.9004 | -122.9691
965.3281 | 123.111 | -60.2875 | 62.4847 | 0.2095 | 0.028196 | 0.018506 | 0.017701 | 0.059257 | 0.00042511 | 0.082068 | -57.3212 | 62.4207 | -60.4111 | -60.4568 | 54.245 | 9.9792 | -8.0521 | -8.8074 | 62.3703 | -60.5164 | -0.1236 | -0.064087 | 2.9663 | -0.16937 | -8.2397 | -0.22888 | -0.11444 | 3.0899 | 52.2354 | 51.4801 | 114.5325 | 122.7081 | 2.9663 | 122.6578 | 70.2667 | -0.22888 | 122.7081 | 2.9663 | 70.2667 | 114.5325 | 122.6578 | -122.8958 | -123.0011
966.3281 | 123.0927 | -60.3012 | 62.5031 | 0.23239 | 0.03076 | 0.023419 | 0.017701 | 0.059471 | -0.00085669 | 0.084417 | -57.3807 | 62.4573 | -60.4385 | -60.5026 | 54.2358 | 9.9792 | -8.0978 | -8.8943 | 62.384 | -60.498 | -0.13733 | -0.045777 | 2.9205 | -0.20142 | -8.2672 | -0.19684 | -0.11902 | 3.0579 | 52.2034 | 51.4069 | 114.537 | 122.7585 | 2.9205 | 122.6852 | 70.2805 | -0.19684 | 122.7585 | 2.9205 | 70.2805 | 114.537 | 122.6852 | -122.9416 | -123.0011
967.3281 | 123.0331 | -60.3287 | 62.5122 | 0.2095 | 0.030332 | 0.027906 | 0.018342 | 0.061393 | 0.00021151 | 0.082708 | -57.431 | 62.4802 | -60.4752 | -60.5255 | 54.2038 | 9.9243 | -8.0017 | -8.8303 | 62.4527 | -60.5118 | -0.14648 | -0.032043 | 2.8976 | -0.19684 | -8.3084 | -0.18311 | -0.059509 | 3.0441 | 52.327 | 51.4984 | 114.5325 | 122.8088 | 2.8976 | 122.7814 | 70.253 | -0.18311 | 122.8088 | 2.8976 | 70.253 | 114.5325 | 122.7814 | -122.9874 | -123.024
968.3281 | 123.111 | -60.3104 | 62.471 | 0.24765 | 0.030119 | 0.021711 | 0.018555 | 0.060966 | 0.0012795 | 0.083136 | -57.3715 | 62.4847 | -60.4248 | -60.4752 | 54.2542 | 9.993 | -8.1665 | -8.9584 | 62.3795 | -60.4843 | -0.11444 | 0.013733 | 2.9388 | -0.16479 | -8.2169 | -0.17395 | -0.091552 | 3.0533 | 52.1439 | 51.3519 | 114.5645 | 122.7951 | 2.9388 | 122.6898 | 70.3033 | -0.17395 | 122.7951 | 2.9388 | 70.3033 | 114.5645 | 122.6898 | -122.8958 | -122.9553
969.3281 | 123.1201 | -60.2646 | 62.4756 | 0.24765 | 0.02841 | 0.019147 | 0.017274 | 0.060325 | -0.00021569 | 0.083349 | -57.3257 | 62.4619 | -60.4156 | -60.466 | 54.2221 | 9.8373 | -8.1528 | -8.6838 | 62.3657 | -60.5026 | -0.15106 | -0.013733 | 2.9388 | -0.20142 | -8.2535 | -0.23804 | -0.10986 | 3.0899 | 52.1118 | 51.5808 | 114.4867 | 122.7264 | 2.9388 | 122.6303 | 70.1019 | -0.23804 | 122.7264 | 2.9388 | 70.1019 | 114.4867 | 122.6303 | -122.8912 | -122.9782
970.3281 | 123.1064 | -60.2737 | 62.4939 | 0.21713 | 0.027983 | 0.022138 | 0.015137 | 0.060539 | -0.00064309 | 0.083777 | -57.3532 | 62.4847 | -60.4385 | -60.4752 | 54.2358 | 9.9518 | -8.3405 | -9.0775 | 62.3749 | -60.5209 | -0.16479 | -0.009155 | 2.9205 | -0.20142 | -8.2581 | -0.24719 | -0.11902 | 3.0853 | 51.9333 | 51.1963 | 114.5096 | 122.7585 | 2.9205 | 122.6486 | 70.2255 | -0.24719 | 122.7585 | 2.9205 | 70.2255 | 114.5096 | 122.6486 | -122.9324 | -123.0148
971.3281 | 123.0698 | -60.2966 | 62.5168 | 0.24002 | 0.030973 | 0.024701 | 0.014496 | 0.061393 | 0.0012795 | 0.083563 | -57.4402 | 62.5076 | -60.4523 | -60.498 | 54.2175 | 9.8282 | -8.3725 | -9.2239 | 62.4207 | -60.5026 | -0.15564 | -0.009156 | 2.8564 | -0.20142 | -8.2993 | -0.20599 | -0.096131 | 3.0121 | 51.9241 | 51.0727 | 114.5142 | 122.8043 | 2.8564 | 122.7173 | 70.1248 | -0.20599 | 122.8043 | 2.8564 | 70.1248 | 114.5142 | 122.7173 | -122.9691 | -123.0194
972.3281 | 123.0606 | -60.3104 | 62.5259 | 0.22476 | 0.031401 | 0.020856 | 0.017487 | 0.062675 | 0.00085231 | 0.082922 | -57.399 | 62.5305 | -60.4431 | -60.5209 | 54.1901 | 9.7733 | -8.3954 | -9.3246 | 62.4344 | -60.5209 | -0.13275 | 0.004578 | 2.9114 | -0.21057 | -8.3359 | -0.21057 | -0.091553 | 3.0441 | 51.915 | 50.9857 | 114.5004 | 122.8409 | 2.9114 | 122.7448 | 70.0836 | -0.21057 | 122.8409 | 2.9114 | 70.0836 | 114.5004 | 122.7448 | -122.9691 | -123.0469
973.3281 | 122.9919 | -60.3058 | 62.5397 | 0.19424 | 0.03076 | 0.026837 | 0.018983 | 0.062675 | 0.0034159 | 0.083563 | -57.4631 | 62.5626 | -60.4523 | -60.5988 | 54.5563 | 9.8373 | -8.5007 | -9.3201 | 62.4756 | -60.5026 | -0.14649 | 0.022888 | 2.8427 | -0.29297 | -7.9834 | -0.19684 | -0.064087 | 2.9892 | 51.8051 | 50.9857 | 114.8621 | 122.8683 | 2.8427 | 122.7814 | 70.1431 | -0.19684 | 122.8683 | 2.8427 | 70.1431 | 114.8621 | 122.7814 | -122.9919 | -123.0423
974.3281 | 122.9691 | -60.3287 | 62.5214 | 0.11795 | 0.030546 | 0.023633 | 0.017274 | 0.059684 | -0.0010703 | 0.082922 | -57.4448 | 62.5488 | -60.4294 | -60.5667 | 54.1718 | 9.7321 | -8.4229 | -9.3842 | 62.4573 | -60.5164 | -0.10071 | 0.027466 | 2.8839 | -0.23804 | -8.3496 | -0.18768 | -0.064087 | 2.9846 | 51.9058 | 50.9445 | 114.5004 | 122.8775 | 2.8839 | 122.7859 | 70.0607 | -0.18768 | 122.8775 | 2.8839 | 70.0607 | 114.5004 | 122.7859 | -122.9507 | -123.0377
975.3281 | 122.9874 | -60.3333 | 62.5351 | -1.1409 | 0.029264 | 0.023633 | 0.013428 | 0.063316 | 0.00085231 | 0.082708 | -57.5363 | 62.5717 | -60.4385 | -60.5484 | 54.1809 | 9.7504 | -8.5327 | -9.5398 | 62.4985 | -60.5164 | -0.10529 | 0.036621 | 2.7969 | -0.21515 | -8.3542 | -0.1831 | -0.036621 | 2.9022 | 51.8005 | 50.7935 | 114.5142 | 122.905 | 2.7969 | 122.8317 | 70.0836 | -0.1831 | 122.905 | 2.7969 | 70.0836 | 114.5142 | 122.8317 | -122.9736 | -123.0515
976.3281 | 122.9874 | -60.3104 | 62.5534 | 0.18662 | 0.030119 | 0.021283 | 0.013642 | 0.062461 | 0.0023477 | 0.084417 | -57.4677 | 62.5351 | -60.4385 | -60.553 | 54.2038 | 9.7504 | -8.6334 | -9.5352 | 62.4527 | -60.5209 | -0.12817 | -0.018311 | 2.8427 | -0.24262 | -8.3496 | -0.21057 | -0.10071 | 2.9709 | 51.6769 | 50.7751 | 114.5142 | 122.8455 | 2.8427 | 122.7631 | 70.0607 | -0.21057 | 122.8455 | 2.8427 | 70.0607 | 114.5142 | 122.7631 | -122.9919 | -123.0743
977.3281 | 122.9828 | -60.3241 | 62.558 | 0.21713 | 0.029478 | 0.020856 | 0.015351 | 0.062675 | 0.0021341 | 0.082708 | -57.4905 | 62.5442 | -60.4385 | -60.5576 | 54.1763 | 9.7595 | -8.6472 | -9.5535 | 62.4802 | -60.5164 | -0.11444 | -0.013733 | 2.8336 | -0.23346 | -8.3817 | -0.19226 | -0.077819 | 2.948 | 51.6769 | 50.7706 | 114.5004 | 122.8683 | 2.8336 | 122.8043 | 70.0836 | -0.19226 | 122.8683 | 2.8336 | 70.0836 | 114.5004 | 122.8043 | -122.9965 | -123.0743
978.3281 | 123.0194 | -60.3012 | 62.5671 | 1.888 | 0.028196 | 0.023206 | 0.016633 | 0.06182 | 0.00021151 | 0.082922 | -57.3624 | 62.5946 | -60.4111 | -60.5621 | 54.1855 | 9.7137 | -8.7158 | -9.5444 | 62.4756 | -60.5164 | -0.10986 | 0.027465 | 2.9388 | -0.26093 | -8.3817 | -0.21515 | -0.091553 | 3.0487 | 51.5854 | 50.7568 | 114.4867 | 122.8958 | 2.9388 | 122.7768 | 70.015 | -0.21515 | 122.8958 | 2.9388 | 70.015 | 114.4867 | 122.7768 | -122.9782 | -123.0835
979.3281 | 123.0286 | -60.2783 | 62.558 | 0.2095 | 0.031828 | 0.027478 | 0.017487 | 0.065666 | 0.0029885 | 0.083349 | -57.4585 | 62.59 | -60.4111 | -60.3653 | 54.4922 | 9.6954 | -8.6517 | -9.4666 | 62.5076 | -60.4935 | -0.13275 | 0.032044 | 2.8198 | -0.086975 | -8.0658 | -0.21515 | -0.050354 | 2.9526 | 51.6266 | 50.8118 | 114.7705 | 122.8683 | 2.8198 | 122.7859 | 69.9738 | -0.21515 | 122.8683 | 2.8198 | 69.9738 | 114.7705 | 122.7859 | -122.9691 | -123.0515
980.3281 | 123.0057 | -60.2554 | 62.5809 | -0.0041198 | 0.029692 | 0.023206 | 0.016846 | 0.063957 | -0.0014975 | 0.083136 | -57.4219 | 62.5717 | -60.3836 | -60.498 | 54.2221 | 9.6817 | -8.844 | -9.6313 | 62.5076 | -60.498 | -0.12817 | -0.009156 | 2.8336 | -0.24262 | -8.3588 | -0.24262 | -0.073243 | 2.9617 | 51.4114 | 50.6241 | 114.4775 | 122.8271 | 2.8336 | 122.7631 | 69.9371 | -0.24262 | 122.8271 | 2.8336 | 69.9371 | 114.4775 | 122.7631 | -122.9645 | -123.0789
981.3281 | 122.9874 | -60.2783 | 62.5763 | 0.011139 | 0.029905 | 0.026624 | 0.014924 | 0.062889 | 0.00042511 | 0.08164 | -57.4081 | 62.5854 | -60.3928 | -60.4752 | 54.2496 | 9.7046 | -8.931 | -9.6954 | 62.5031 | -60.5118 | -0.11444 | 0.009155 | 2.8702 | -0.19684 | -8.3267 | -0.23346 | -0.073242 | 2.9846 | 51.3474 | 50.5829 | 114.5279 | 122.8638 | 2.8702 | 122.7814 | 69.9829 | -0.23346 | 122.8638 | 2.8702 | 69.9829 | 114.5279 | 122.7814 | -122.9691 | -123.0881
982.3281 | 123.0331 | -60.2737 | 62.5854 | 0.14847 | 0.030332 | 0.022565 | 0.015565 | 0.067588 | -2.092e-06 | 0.082068 | -57.5089 | 62.5717 | -60.3928 | -60.2188 | 54.2862 | 9.5581 | -8.8303 | -9.819 | 62.5214 | -60.4843 | -0.11902 | -0.013733 | 2.7649 | 0.054932 | -8.2993 | -0.21057 | -0.064087 | 2.8839 | 51.4435 | 50.4547 | 114.5599 | 122.8455 | 2.7649 | 122.7951 | 69.8318 | -0.21057 | 122.8455 | 2.7649 | 69.8318 | 114.5599 | 122.7951 | -122.9782 | -123.0698
983.3281 | 122.9462 | -60.3104 | 62.4985 | 0.095062 | 0.030546 | 0.020002 | 0.017914 | 0.063102 | 0.0014933 | 0.083349 | -57.4722 | 62.5946 | -60.4019 | -60.5438 | 54.1718 | 9.5444 | -9.0958 | -10.0113 | 62.4893 | -60.5164 | -0.091553 | 0.09613 | 2.8381 | -0.23346 | -8.3267 | -0.20599 | -0.009155 | 2.9297 | 51.2146 | 50.2991 | 114.4821 | 122.905 | 2.8381 | 122.7997 | 69.8547 | -0.20599 | 122.905 | 2.8381 | 69.8547 | 114.4821 | 122.7997 | -122.9004 | -123.0148
984.3281 | 122.9782 | -60.2554 | 62.5946 | 0.041657 | 0.031614 | 0.022565 | 0.01941 | 0.062461 | -2.092e-06 | 0.080786 | -57.4448 | 62.59 | -60.4156 | -60.5301 | 54.2221 | 9.6085 | -9.082 | -9.9472 | 62.5397 | -60.4797 | -0.16022 | -0.004577 | 2.8107 | -0.27466 | -8.3725 | -0.2243 | -0.054931 | 2.9709 | 51.1734 | 50.3082 | 114.4775 | 122.8455 | 2.8107 | 122.7951 | 69.8639 | -0.2243 | 122.8455 | 2.8107 | 69.8639 | 114.4775 | 122.7951 | -123.0103 | -123.0743
985.3281 | 123.0103 | -60.2921 | 62.5992 | 0.072174 | 0.030546 | 0.024488 | 0.014924 | 0.06182 | -0.00085669 | 0.084204 | -57.4356 | 62.5946 | -60.379 | -60.5164 | 54.213 | 9.5947 | -9.1461 | -10.0113 | 62.5122 | -60.4843 | -0.086975 | -0.004578 | 2.8564 | -0.2243 | -8.3862 | -0.19226 | -0.086975 | 2.9434 | 51.1459 | 50.2808 | 114.505 | 122.8867 | 2.8564 | 122.8043 | 69.8868 | -0.19226 | 122.8867 | 2.8564 | 69.8868 | 114.505 | 122.8043 | -122.9782 | -123.0835
986.3281 | 123.0194 | -60.2921 | 62.59 | 0.087433 | 0.029264 | 0.023633 | 0.017274 | 0.061393 | 0.0025613 | 0.084631 | -57.4036 | 62.5854 | -60.3973 | -60.5026 | 54.2175 | 9.5947 | -9.2743 | -10.1807 | 62.5442 | -60.5026 | -0.10529 | -0.004578 | 2.8885 | -0.21057 | -8.3725 | -0.21057 | -0.045777 | 2.9938 | 51.0178 | 50.1114 | 114.5096 | 122.8775 | 2.8885 | 122.8363 | 69.8868 | -0.21057 | 122.8775 | 2.8885 | 69.8868 | 114.5096 | 122.8363 | -122.9874 | -123.0927
987.3281 | 123.0515 | -60.2417 | 62.5626 | 0.43076 | 0.030546 | 0.028546 | 0.014496 | 0.063102 | 0.0012795 | 0.082068 | -57.3761 | 62.59 | -60.3516 | -60.4431 | 54.2999 | 9.6222 | -9.3704 | -10.1349 | 62.558 | -60.4843 | -0.10986 | 0.027466 | 2.8656 | -0.20142 | -8.2626 | -0.24262 | -0.004578 | 2.9755 | 50.8713 | 50.1068 | 114.5416 | 122.8317 | 2.8656 | 122.7997 | 69.8639 | -0.24262 | 122.8317 | 2.8656 | 69.8639 | 114.5416 | 122.7997 | -122.9141 | -123.0469
988.3281 | 123.0469 | -60.2371 | 62.6129 | 0.018768 | 0.029478 | 0.023419 | 0.014924 | 0.065238 | 0.0014933 | 0.083777 | -57.4081 | 62.6312 | -60.3607 | -60.4706 | 54.2725 | 9.494 | -9.5352 | -10.3455 | 62.5488 | -60.4431 | -0.1236 | 0.018311 | 2.829 | -0.23346 | -8.3405 | -0.20599 | -0.064087 | 2.9526 | 50.7019 | 49.8917 | 114.5096 | 122.8683 | 2.829 | 122.7859 | 69.7311 | -0.20599 | 122.8683 | 2.829 | 69.7311 | 114.5096 | 122.7859 | -122.9736 | -123.056
989.3281 | 122.9965 | -60.2783 | 62.5763 | 0.056915 | 0.030546 | 0.020856 | 0.015351 | 0.064811 | 0.0019205 | 0.083349 | -57.4356 | 62.6038 | -60.3699 | -60.4797 | 54.245 | 9.5169 | -9.5078 | -10.3821 | 62.5717 | -60.4385 | -0.091553 | 0.027466 | 2.8427 | -0.20142 | -8.3313 | -0.16022 | -0.004578 | 2.9343 | 50.7706 | 49.8962 | 114.5233 | 122.8821 | 2.8427 | 122.85 | 69.7952 | -0.16022 | 122.8821 | 2.8427 | 69.7952 | 114.5233 | 122.85 | -122.9462 | -123.0148
990.3281 | 123.0103 | -60.2554 | 62.59 | 0.079804 | 0.029264 | 0.018933 | 0.015778 | 0.062461 | 0.00021151 | 0.08399 | -57.4356 | 62.5992 | -60.3653 | -60.4843 | 54.2496 | 9.5261 | -9.5398 | -10.3088 | 62.558 | -60.466 | -0.10986 | 0.009155 | 2.8198 | -0.22888 | -8.3405 | -0.21057 | -0.032044 | 2.9297 | 50.7156 | 49.9466 | 114.505 | 122.8546 | 2.8198 | 122.8134 | 69.7815 | -0.21057 | 122.8546 | 2.8198 | 69.7815 | 114.505 | 122.8134 | -122.9553 | -123.056
991.3281 | 122.9736 | -60.2417 | 62.5992 | 0.011139 | 0.030332 | 0.021924 | 0.01706 | 0.06182 | -2.092e-06 | 0.083777 | -57.4173 | 62.6221 | -60.3699 | -60.4568 | 54.2725 | 9.4803 | -9.5901 | -10.3867 | 62.5351 | -60.4797 | -0.12817 | 0.022888 | 2.8244 | -0.21515 | -8.3267 | -0.23804 | -0.064087 | 2.9526 | 50.6516 | 49.855 | 114.5142 | 122.8638 | 2.8244 | 122.7768 | 69.722 | -0.23804 | 122.8638 | 2.8244 | 69.722 | 114.5142 | 122.7768 | -122.9691 | -123.0789
992.3281 | 123.0331 | -60.2554 | 62.5809 | 0.049286 | 0.031614 | 0.021924 | 0.014283 | 0.063957 | -2.092e-06 | 0.082708 | -57.4265 | 62.6358 | -60.3836 | -60.4477 | 54.3045 | 9.4803 | -9.7275 | -10.4095 | 62.5351 | -60.4477 | -0.12817 | 0.054931 | 2.829 | -0.19226 | -8.2764 | -0.19226 | -0.045777 | 2.9572 | 50.528 | 49.8459 | 114.5599 | 122.8912 | 2.829 | 122.7905 | 69.7357 | -0.19226 | 122.8912 | 2.829 | 69.7357 | 114.5599 | 122.7905 | -122.9645 | -123.0286
993.3281 | 123.0377 | -60.2325 | 62.5946 | -0.011749 | 0.029478 | 0.021283 | 0.013642 | 0.063316 | -0.00085669 | 0.082068 | -57.4265 | 62.6221 | -60.3745 | -60.4294 | 54.3182 | 9.4437 | -9.7595 | -10.4095 | 62.5534 | -60.4706 | -0.14191 | 0.027466 | 2.8061 | -0.19684 | -8.2764 | -0.23804 | -0.041198 | 2.948 | 50.473 | 49.823 | 114.5508 | 122.8546 | 2.8061 | 122.7859 | 69.6762 | -0.23804 | 122.8546 | 2.8061 | 69.6762 | 114.5508 | 122.7859 | -122.9691 | -123.0652
994.3281 | 123.0377 | -60.2371 | 62.5992 | -0.14908 | 0.028623 | 0.023419 | 0.01471 | 0.063743 | -0.00064309 | 0.082281 | -57.4402 | 62.6358 | -60.3653 | -60.4294 | 54.3091 | 9.4254 | -9.7275 | -10.5148 | 62.5946 | -60.466 | -0.12817 | 0.036621 | 2.7969 | -0.19226 | -8.2901 | -0.22888 | -0.004578 | 2.9251 | 50.5096 | 49.7223 | 114.5462 | 122.8729 | 2.7969 | 122.8317 | 69.6625 | -0.22888 | 122.8729 | 2.7969 | 69.6625 | 114.5462 | 122.8317 | -122.9645 | -123.0652
995.3281 | 123.0377 | -60.2371 | 62.6266 | -0.042267 | 0.02841 | 0.024274 | 0.015137 | 0.068229 | 0.00021151 | 0.081 | -57.4173 | 62.6175 | -60.3745 | -60.347 | 54.2404 | 9.3658 | -9.938 | -10.5789 | 62.5946 | -60.4477 | -0.13733 | -0.009155 | 2.8198 | -0.10986 | -8.3862 | -0.21057 | -0.032044 | 2.9572 | 50.2991 | 49.6582 | 114.4775 | 122.8546 | 2.8198 | 122.8317 | 69.603 | -0.21057 | 122.8546 | 2.8198 | 69.603 | 114.4775 | 122.8317 | -123.0011 | -123.0743
996.3281 | 123.056 | -60.228 | 62.6038 | -0.065155 | 0.028196 | 0.020856 | 0.015137 | 0.062675 | 0.00063871 | 0.084631 | -57.4493 | 62.6083 | -60.3699 | -60.434 | 54.3045 | 9.375 | -9.9701 | -10.5972 | 62.5534 | -60.4523 | -0.14191 | 0.004577 | 2.7786 | -0.20599 | -8.2993 | -0.22431 | -0.050354 | 2.9205 | 50.2579 | 49.6307 | 114.5325 | 122.8363 | 2.7786 | 122.7814 | 69.603 | -0.22431 | 122.8363 | 2.7786 | 69.603 | 114.5325 | 122.7814 | -122.9736 | -123.056
997.3281 | 123.0377 | -60.2051 | 62.5992 | -0.1033 | 0.031187 | 0.023419 | 0.01471 | 0.062889 | -0.00085669 | 0.082922 | -57.4265 | 62.6312 | -60.3653 | -60.4111 | 54.3274 | 9.288 | -10.0342 | -10.5606 | 62.5992 | -60.434 | -0.16022 | 0.032044 | 2.7786 | -0.20599 | -8.2718 | -0.22888 | 0 | 2.9388 | 50.1709 | 49.6445 | 114.5325 | 122.8363 | 2.7786 | 122.8043 | 69.4931 | -0.22888 | 122.8363 | 2.7786 | 69.4931 | 114.5325 | 122.8043 | -122.9645 | -123.0331
998.3281 | 123.0377 | -60.2325 | 62.6083 | -0.38559 | 0.027769 | 0.020002 | 0.017487 | 0.064811 | 0.00063871 | 0.083777 | -57.431 | 62.6221 | -60.3607 | -60.3836 | 54.3503 | 9.2972 | -10.0388 | -10.7162 | 62.5992 | -60.434 | -0.12817 | 0.013733 | 2.8015 | -0.15106 | -8.2581 | -0.20142 | -0.009155 | 2.9297 | 50.1938 | 49.5163 | 114.5828 | 122.8546 | 2.8015 | 122.8317 | 69.5297 | -0.20142 | 122.8546 | 2.8015 | 69.5297 | 114.5828 | 122.8317 | -122.9691 | -123.0423
999.3281 | 123.0606 | -60.2371 | 62.6175 | -0.072784 | 0.03076 | 0.026197 | 0.017274 | 0.065238 | -0.0032065 | 0.082708 | -57.4539 | 62.6175 | -60.3424 | -60.4568 | 54.3228 | 9.4025 | -10.0937 | -10.6567 | 62.5854 | -60.4614 | -0.10529 | 0 | 2.7832 | -0.21973 | -8.2947 | -0.2243 | -0.032044 | 2.8885 | 50.1434 | 49.5804 | 114.5599 | 122.8546 | 2.7832 | 122.8226 | 69.6396 | -0.2243 | 122.8546 | 2.7832 | 69.6396 | 114.5599 | 122.8226 | -122.9599 | -123.0789
1000.3281 | 123.0377 | -60.2234 | 62.6358 | -0.034637 | 0.032469 | 0.020002 | 0.016633 | 0.065238 | 0.0023477 | 0.083563 | -57.4219 | 62.6358 | -60.3424 | -60.4111 | 54.3549 | 9.2606 | -10.3226 | -11.0825 | 62.5534 | -60.4752 | -0.11902 | 0 | 2.8015 | -0.18768 | -8.2809 | -0.25177 | -0.082397 | 2.9205 | 49.9008 | 49.1409 | 114.5782 | 122.8592 | 2.8015 | 122.7768 | 69.4839 | -0.25177 | 122.8592 | 2.8015 | 69.4839 | 114.5782 | 122.7768 | -122.9782 | -123.111
1001.3281 | 123.0286 | -60.228 | 62.6175 | -0.15671 | 0.027342 | 0.020856 | 0.014069 | 0.063743 | -0.0012839 | 0.084204 | -57.4493 | 62.6358 | -60.3195 | -60.4431 | 54.3228 | 9.1232 | -10.1852 | -10.8765 | 62.6266 | -60.4294 | -0.091553 | 0.01831 | 2.7786 | -0.21515 | -8.2947 | -0.20142 | 0.009155 | 2.8702 | 50.0427 | 49.3515 | 114.5508 | 122.8638 | 2.7786 | 122.8546 | 69.3512 | -0.20142 | 122.8638 | 2.7786 | 69.3512 | 114.5508 | 122.8546 | -122.937 | -123.0469
1002.3281 | 123.0103 | -60.1959 | 62.6404 | -0.16434 | 0.029051 | 0.020856 | 0.012574 | 0.062889 | 0.00021151 | 0.083563 | -57.5043 | 62.6312 | -60.3378 | -60.4614 | 54.3137 | 9.1141 | -10.2448 | -10.8902 | 62.6221 | -60.4156 | -0.14191 | -0.009155 | 2.6917 | -0.2655 | -8.3267 | -0.21973 | -0.018311 | 2.8336 | 49.9512 | 49.3057 | 114.5096 | 122.8271 | 2.6917 | 122.818 | 69.31 | -0.21973 | 122.8271 | 2.6917 | 69.31 | 114.5096 | 122.818 | -122.9782 | -123.056
1003.3281 | 123.0377 | -60.1913 | 62.6358 | -0.034637 | 0.027983 | 0.019788 | 0.017701 | 0.062461 | -0.0017111 | 0.082281 | -57.6553 | 62.5992 | -60.3516 | -60.3699 | 54.3823 | 9.2148 | -10.3455 | -10.9543 | 62.5992 | -60.4294 | -0.16022 | -0.036621 | 2.536 | -0.17853 | -8.2535 | -0.23804 | -0.036621 | 2.6962 | 49.8459 | 49.2371 | 114.5737 | 122.7905 | 2.536 | 122.7905 | 69.4061 | -0.23804 | 122.7905 | 2.536 | 69.4061 | 114.5737 | 122.7905 | -122.9874 | -123.0652
1004.3281 | 123.0286 | -60.1822 | 62.6358 | -0.11093 | 0.030119 | 0.026197 | 0.015565 | 0.062675 | 0.0019205 | 0.083563 | -57.4539 | 62.6404 | -60.3149 | -60.6445 | 54.2542 | 9.3201 | -10.4828 | -10.9726 | 62.6129 | -60.4294 | -0.13275 | 0.004578 | 2.7283 | -0.46234 | -8.3817 | -0.24719 | -0.022888 | 2.861 | 49.6994 | 49.2096 | 114.4363 | 122.8226 | 2.7283 | 122.7951 | 69.5023 | -0.24719 | 122.8226 | 2.7283 | 69.5023 | 114.4363 | 122.7951 | -122.9507 | -123.0652
1005.3281 | 122.9279 | -60.2188 | 62.6266 | -0.19485 | 0.029478 | 0.023419 | 0.014069 | 0.063529 | -0.00042929 | 0.082281 | -57.4448 | 62.6175 | -60.3287 | -60.3882 | 54.3961 | 9.2285 | -10.4462 | -11.0596 | 62.6221 | -60.4294 | -0.10986 | -0.009155 | 2.774 | -0.16937 | -8.2306 | -0.21057 | -0.004578 | 2.8839 | 49.7726 | 49.1592 | 114.6149 | 122.8363 | 2.774 | 122.8409 | 69.4473 | -0.21057 | 122.8363 | 2.774 | 69.4473 | 114.6149 | 122.8409 | -122.9553 | -123.056
1006.3281 | 123.0286 | -60.2142 | 62.6312 | -0.13382 | 0.029264 | 0.02107 | 0.013856 | 0.062889 | -0.0010703 | 0.080786 | -57.4768 | 62.6724 | -60.3058 | -60.3882 | 54.3961 | 9.1507 | -10.556 | -11.1145 | 62.6175 | -60.4202 | -0.091553 | 0.041198 | 2.7374 | -0.17395 | -8.2352 | -0.20599 | -0.013733 | 2.829 | 49.6582 | 49.0997 | 114.6103 | 122.8867 | 2.7374 | 122.8317 | 69.3649 | -0.20599 | 122.8867 | 2.7374 | 69.3649 | 114.6103 | 122.8317 | -122.937 | -123.0515
1007.3281 | 123.0698 | -60.1913 | 62.6633 | -0.11856 | 0.030332 | 0.020642 | 0.015565 | 0.064384 | 0.00063871 | 0.082495 | -57.4265 | 62.6495 | -60.3195 | -60.3928 | 54.4006 | 9.137 | -10.5972 | -11.1511 | 62.6495 | -60.4111 | -0.12817 | -0.013733 | 2.7649 | -0.20142 | -8.2626 | -0.21973 | -0.013733 | 2.8931 | 49.5941 | 49.0402 | 114.592 | 122.8409 | 2.7649 | 122.8409 | 69.3283 | -0.21973 | 122.8409 | 2.7649 | 69.3283 | 114.592 | 122.8409 | -122.9828 | -123.0743
1008.3281 | 122.9919 | -60.2097 | 62.6358 | -0.1796 | 0.027769 | 0.019361 | 0.014069 | 0.061607 | 0.0021341 | 0.085058 | -57.4768 | 62.6312 | -60.3241 | -60.434 | 54.3549 | 9.1461 | -10.5057 | -11.1832 | 62.6266 | -60.4111 | -0.11444 | -0.004577 | 2.7328 | -0.2243 | -8.2809 | -0.20142 | -0.009155 | 2.8473 | 49.704 | 49.0265 | 114.5645 | 122.8409 | 2.7328 | 122.8363 | 69.3558 | -0.20142 | 122.8409 | 2.7328 | 69.3558 | 114.5645 | 122.8363 | -122.9599 | -123.0469
1009.3281 | 123.0331 | -60.2051 | 62.6495 | -0.14145 | 0.030119 | 0.022138 | 0.01471 | 0.064384 | 0.00042511 | 0.08164 | -57.4539 | 62.6495 | -60.3287 | -60.4019 | 54.3915 | 9.1644 | -10.5972 | -11.2427 | 62.6312 | -60.3836 | -0.1236 | 0 | 2.7512 | -0.19684 | -8.2581 | -0.17853 | -0.01831 | 2.8748 | 49.6078 | 48.9624 | 114.5966 | 122.8546 | 2.7512 | 122.8363 | 69.3695 | -0.17853 | 122.8546 | 2.7512 | 69.3695 | 114.5966 | 122.8363 | -122.9782 | -123.0331
1010.3281 | 123.0515 | -60.2005 | 62.5992 | -0.065155 | 0.030546 | 0.022779 | 0.014924 | 0.063529 | 0.00042511 | 0.080359 | -57.431 | 62.6404 | -60.3104 | -60.3836 | 54.3961 | 9.1049 | -10.7849 | -11.2976 | 62.6358 | -60.3973 | -0.10986 | 0.041199 | 2.7695 | -0.18311 | -8.2031 | -0.19684 | 0.036621 | 2.8793 | 49.4156 | 48.9029 | 114.5966 | 122.8409 | 2.7695 | 122.8363 | 69.3054 | -0.19684 | 122.8409 | 2.7695 | 69.3054 | 114.5966 | 122.8363 | -122.9095 | -122.9965
1011.3281 | 123.0331 | -60.1822 | 62.6495 | -0.11093 | 0.027342 | 0.021924 | 0.014283 | 0.064384 | 0.0019205 | 0.082922 | -57.4677 | 62.6404 | -60.3378 | -60.379 | 54.4189 | 9.0958 | -10.8353 | -11.3297 | 62.6541 | -60.4019 | -0.15564 | -0.009155 | 2.7145 | -0.19684 | -8.2306 | -0.21973 | 0.004578 | 2.8702 | 49.3469 | 48.8525 | 114.6011 | 122.8226 | 2.7145 | 122.8363 | 69.278 | -0.21973 | 122.8226 | 2.7145 | 69.278 | 114.6011 | 122.8363 | -122.9874 | -123.0515
1012.3281 | 123.0423 | -60.173 | 62.6862 | -0.13382 | 0.027769 | 0.020429 | 0.014496 | 0.061393 | 0.00063871 | 0.083563 | -57.4631 | 62.6862 | -60.3241 | -60.3745 | 54.3915 | 9.0134 | -10.8307 | -11.4761 | 62.6495 | -60.3973 | -0.15106 | 0 | 2.71 | -0.20142 | -8.2947 | -0.2243 | -0.036621 | 2.861 | 49.3423 | 48.6969 | 114.5645 | 122.8592 | 2.71 | 122.8226 | 69.1864 | -0.2243 | 122.8592 | 2.71 | 69.1864 | 114.5645 | 122.8226 | -123.0103 | -123.0835
1013.3281 | 123.0652 | -60.1822 | 62.6862 | -0.14908 | 0.03076 | 0.017652 | 0.013642 | 0.059898 | -0.0023519 | 0.08399 | -57.4722 | 62.6816 | -60.2921 | -60.3882 | 54.3961 | 8.9951 | -10.9772 | -11.5952 | 62.6587 | -60.3928 | -0.10986 | -0.004577 | 2.71 | -0.20599 | -8.2901 | -0.21057 | -0.027466 | 2.8198 | 49.205 | 48.587 | 114.5782 | 122.8638 | 2.71 | 122.8409 | 69.1772 | -0.21057 | 122.8638 | 2.71 | 69.1772 | 114.5782 | 122.8409 | -122.9782 | -123.0789
1014.3281 | 123.0286 | -60.1822 | 62.6724 | -0.16434 | 0.028623 | 0.019574 | 0.013428 | 0.060752 | -0.00042929 | 0.081213 | -57.4677 | 62.677 | -60.3149 | -60.4111 | 54.3869 | 9.0408 | -10.9314 | -11.5814 | 62.6541 | -60.3836 | -0.13275 | 0.004578 | 2.7145 | -0.22888 | -8.2855 | -0.20142 | -0.01831 | 2.8473 | 49.2508 | 48.6008 | 114.5691 | 122.8592 | 2.7145 | 122.8363 | 69.223 | -0.20142 | 122.8592 | 2.7145 | 69.223 | 114.5691 | 122.8363 | -122.9874 | -123.056
1015.3281 | 123.0194 | -60.1776 | 62.6907 | -0.21011 | 0.028196 | 0.015515 | 0.010865 | 0.060325 | -2.092e-06 | 0.082068 | -57.431 | 62.6953 | -60.2829 | -60.4202 | 54.4144 | 8.9447 | -11.0001 | -11.5997 | 62.6587 | -60.3973 | -0.10529 | 0.004577 | 2.7466 | -0.24261 | -8.2764 | -0.21973 | -0.032044 | 2.8519 | 49.1776 | 48.5779 | 114.592 | 122.8729 | 2.7466 | 122.8363 | 69.1223 | -0.21973 | 122.8729 | 2.7466 | 69.1223 | 114.592 | 122.8363 | -122.9736 | -123.0881
1016.3281 | 122.9874 | -60.1913 | 62.7136 | -0.1796 | 0.026487 | 0.018079 | 0.012574 | 0.062889 | 0.0010659 | 0.08399 | -57.5363 | 62.6724 | -60.3058 | -60.4202 | 54.3777 | 8.9218 | -11.0687 | -11.7416 | 62.6862 | -60.3653 | -0.11444 | -0.041199 | 2.655 | -0.22888 | -8.3359 | -0.17395 | -0.027466 | 2.7695 | 49.1226 | 48.4497 | 114.5691 | 122.8638 | 2.655 | 122.8775 | 69.1132 | -0.17395 | 122.8638 | 2.655 | 69.1132 | 114.5691 | 122.8775 | -123.0194 | -123.0789
1017.3438 | 122.9965 | -60.2051 | 62.6633 | 0.19424 | 0.029692 | 0.020002 | 0.015992 | 0.061607 | 0.00021151 | 0.083349 | -57.5363 | 62.6495 | -60.2966 | -60.4568 | 54.3411 | 8.8943 | -11.1282 | -11.824 | 62.6358 | -60.3928 | -0.091553 | -0.013733 | 2.6688 | -0.25177 | -8.3221 | -0.18768 | -0.027466 | 2.7603 | 49.0768 | 48.381 | 114.5462 | 122.8546 | 2.6688 | 122.8409 | 69.0994 | -0.18768 | 122.8546 | 2.6688 | 69.0994 | 114.5462 | 122.8409 | -122.9599 | -123.056
1018.3281 | 123.0103 | -60.1639 | 62.7136 | -0.18723 | 0.028196 | 0.019147 | 0.01471 | 0.059898 | 0.00021151 | 0.082495 | -57.5134 | 62.6633 | -60.3058 | -60.3928 | 54.3869 | 8.9722 | -11.0825 | -11.7142 | 62.6587 | -60.3699 | -0.14191 | -0.050354 | 2.6505 | -0.22888 | -8.3267 | -0.20599 | -0.054932 | 2.7924 | 49.0814 | 48.4497 | 114.5508 | 122.8271 | 2.6505 | 122.8226 | 69.136 | -0.20599 | 122.8271 | 2.6505 | 69.136 | 114.5508 | 122.8226 | -123.0194 | -123.0835
1019.3281 | 123.0148 | -60.1913 | 62.7045 | -0.18723 | 0.025419 | 0.020002 | 0.012147 | 0.062248 | -2.092e-06 | 0.083136 | -57.5226 | 62.6678 | -60.2966 | -60.3882 | 54.3777 | 8.9218 | -11.1374 | -11.8011 | 62.677 | -60.3745 | -0.10529 | -0.036621 | 2.6688 | -0.19684 | -8.3267 | -0.18311 | -0.027466 | 2.774 | 49.054 | 48.3902 | 114.5691 | 122.8592 | 2.6688 | 122.8683 | 69.1132 | -0.18311 | 122.8592 | 2.6688 | 69.1132 | 114.5691 | 122.8683 | -123.0011 | -123.0789
1020.3281 | 122.9782 | -60.1685 | 62.6816 | -0.14908 | 0.026274 | 0.019574 | 0.010865 | 0.06182 | -0.0010703 | 0.083136 | -57.4905 | 62.677 | -60.2692 | -60.3973 | 54.3869 | 8.876 | -11.2976 | -11.911 | 62.6862 | -60.3699 | -0.10071 | -0.004578 | 2.6779 | -0.22888 | -8.2947 | -0.20142 | 0.004577 | 2.7786 | 48.8708 | 48.2574 | 114.5554 | 122.8455 | 2.6779 | 122.8546 | 69.0445 | -0.20142 | 122.8455 | 2.6779 | 69.0445 | 114.5554 | 122.8546 | -122.9507 | -123.0515
1021.3281 | 123.0423 | -60.1227 | 62.6907 | -0.21011 | 0.024992 | 0.01872 | 0.012574 | 0.060752 | -0.00021569 | 0.082708 | -57.4768 | 62.6221 | -60.2646 | -60.3333 | 54.4647 | 8.9081 | -11.3846 | -11.9202 | 62.6862 | -60.3149 | -0.14191 | -0.068665 | 2.6459 | -0.21057 | -8.226 | -0.19226 | -0.004578 | 2.7878 | 48.7381 | 48.2025 | 114.5874 | 122.7448 | 2.6459 | 122.8088 | 69.0308 | -0.19226 | 122.7448 | 2.6459 | 69.0308 | 114.5874 | 122.8088 | -122.9553 | -123.0057
1022.3438 | 122.9965 | -60.173 | 62.6862 | 0.11032 | 0.028196 | 0.019361 | 0.015778 | 0.063957 | -0.00064309 | 0.081854 | -57.4768 | 62.6724 | -60.3104 | -60.4156 | 54.3869 | 8.8348 | -11.3754 | -11.9888 | 62.6862 | -60.3699 | -0.13733 | -0.013733 | 2.6962 | -0.24261 | -8.2993 | -0.19684 | 0 | 2.8336 | 48.7976 | 48.1842 | 114.5599 | 122.8455 | 2.6962 | 122.8592 | 69.0079 | -0.19684 | 122.8455 | 2.6962 | 69.0079 | 114.5599 | 122.8592 | -122.9965 | -123.056
1023.3281 | 123.0057 | -60.1501 | 62.6999 | -0.17197 | 0.02606 | 0.017652 | 0.013001 | 0.059043 | -0.00085669 | 0.082068 | -57.4905 | 62.6358 | -60.2692 | -60.3699 | 54.4647 | 8.9264 | -11.3434 | -11.9705 | 62.6633 | -60.3241 | -0.11902 | -0.064087 | 2.6596 | -0.21973 | -8.2352 | -0.17395 | -0.036621 | 2.7786 | 48.8068 | 48.1796 | 114.6149 | 122.7859 | 2.6596 | 122.8134 | 69.0765 | -0.17395 | 122.7859 | 2.6596 | 69.0765 | 114.6149 | 122.8134 | -122.9691 | -123.024
1024.3281 | 123.0057 | -60.141 | 62.7274 | -0.20248 | 0.026487 | 0.014234 | 0.014924 | 0.062461 | -0.0021383 | 0.083777 | -57.5409 | 62.6541 | -60.2692 | -60.3378 | 54.3686 | 8.725 | -11.4899 | -12.1262 | 62.6907 | -60.347 | -0.12817 | -0.073242 | 2.6001 | -0.19684 | -8.3588 | -0.20599 | -0.036621 | 2.7283 | 48.6511 | 48.0148 | 114.5096 | 122.7951 | 2.6001 | 122.8317 | 68.866 | -0.20599 | 122.7951 | 2.6001 | 68.866 | 114.5096 | 122.8317 | -122.9965 | -123.0743
1025.3281 | 123.0789 | -60.1227 | 62.7686 | -0.32455 | 0.027342 | 0.01872 | 0.012147 | 0.060325 | -0.0032065 | 0.083136 | -57.5363 | 62.6541 | -60.2646 | -60.3653 | 54.4418 | 8.7021 | -11.673 | -12.2452 | 62.7045 | -60.347 | -0.14191 | -0.11444 | 2.5864 | -0.24261 | -8.3267 | -0.2243 | -0.064087 | 2.7283 | 48.4497 | 47.8775 | 114.5645 | 122.7768 | 2.5864 | 122.8271 | 68.8248 | -0.2243 | 122.7768 | 2.5864 | 68.8248 | 114.5645 | 122.8271 | -123.0331 | -123.1155
1026.3281 | 123.0057 | -60.141 | 62.7182 | -0.20248 | 0.024137 | 0.016797 | 0.011506 | 0.062034 | -0.0012839 | 0.082281 | -57.4631 | 62.6358 | -60.2646 | -60.3516 | 54.4785 | 8.7524 | -11.586 | -12.0117 | 62.6953 | -60.3241 | -0.1236 | -0.082398 | 2.6779 | -0.21057 | -8.2397 | -0.18311 | -0.022889 | 2.8015 | 48.555 | 48.1293 | 114.6194 | 122.7768 | 2.6779 | 122.8363 | 68.8934 | -0.18311 | 122.7768 | 2.6779 | 68.8934 | 114.6194 | 122.8363 | -122.9828 | -123.0423
1027.3438 | 122.9874 | -60.1639 | 62.6862 | 0.11795 | 0.029478 | 0.019788 | 0.018128 | 0.063316 | -0.0019247 | 0.082708 | -57.518 | 62.6907 | -60.2646 | -60.4065 | 54.3823 | 8.6334 | -11.7004 | -12.1994 | 62.677 | -60.3653 | -0.10071 | 0.004578 | 2.6459 | -0.24262 | -8.3038 | -0.20142 | -0.009155 | 2.7466 | 48.4634 | 47.9645 | 114.5462 | 122.8546 | 2.6459 | 122.8409 | 68.7973 | -0.20142 | 122.8546 | 2.6459 | 68.7973 | 114.5462 | 122.8409 | -122.9507 | -123.0515
1028.3281 | 123.1705 | -60.0952 | 62.6633 | -0.072784 | 0.026914 | 0.017438 | 0.0083014 | 0.059257 | 0.0025613 | 0.082281 | -57.4814 | 62.5946 | -60.2554 | -60.2692 | 54.5792 | 8.7753 | -11.8973 | -12.0758 | 62.6175 | -60.2783 | -0.16022 | -0.068665 | 2.6138 | -0.17395 | -8.0841 | -0.1831 | -0.045776 | 2.774 | 48.1979 | 48.0194 | 114.6744 | 122.6898 | 2.6138 | 122.7127 | 68.8705 | -0.1831 | 122.6898 | 2.6138 | 68.8705 | 114.6744 | 122.7127 | -122.9187 | -122.9416
1029.3281 | 123.1522 | -60.0906 | 62.6953 | -0.1033 | 0.026274 | 0.018506 | 0.01001 | 0.059257 | -0.00064309 | 0.081854 | -57.1106 | 62.645 | -60.1913 | -60.2188 | 54.57 | 8.67 | -11.8423 | -12.0163 | 62.6312 | -60.2646 | -0.10071 | -0.050354 | 2.98 | -0.12817 | -8.1253 | -0.17395 | -0.064086 | 3.0807 | 48.2483 | 48.0743 | 114.6606 | 122.7356 | 2.98 | 122.7219 | 68.7607 | -0.17395 | 122.7356 | 2.98 | 68.7607 | 114.6606 | 122.7219 | -122.8867 | -122.9599
1030.3281 | 123.0881 | -60.0815 | 62.709 | -0.11856 | 0.026274 | 0.020002 | 0.012147 | 0.059257 | -0.0017111 | 0.083136 | -57.431 | 62.5946 | -60.2325 | -60.2325 | 54.5471 | 8.6197 | -12.0392 | -12.204 | 62.6495 | -60.2646 | -0.15106 | -0.11444 | 2.6505 | -0.15106 | -8.1619 | -0.1831 | -0.059509 | 2.8015 | 48.0423 | 47.8775 | 114.6286 | 122.6761 | 2.6505 | 122.731 | 68.7012 | -0.1831 | 122.6761 | 2.6505 | 68.7012 | 114.6286 | 122.731 | -122.9416 | -122.9736
1031.3281 | 123.0743 | -60.1044 | 62.709 | -0.20248 | 0.026274 | 0.017652 | 0.015137 | 0.059471 | 0.00042511 | 0.082708 | -57.4539 | 62.6083 | -60.2234 | -60.2829 | 54.5334 | 8.6426 | -11.8286 | -12.1811 | 62.6678 | -60.2692 | -0.11902 | -0.10071 | 2.6505 | -0.17853 | -8.1757 | -0.16479 | -0.041198 | 2.7695 | 48.2758 | 47.9233 | 114.6378 | 122.7127 | 2.6505 | 122.7722 | 68.7469 | -0.16479 | 122.7127 | 2.6505 | 68.7469 | 114.6378 | 122.7722 | -122.9324 | -122.9782
1032.3281 | 123.0652 | -60.0815 | 62.7274 | -0.11856 | 0.026274 | 0.017652 | 0.012574 | 0.059043 | -0.00021569 | 0.081427 | -57.4631 | 62.5809 | -60.2234 | -60.2554 | 54.5654 | 8.67 | -11.9843 | -12.1628 | 62.645 | -60.2646 | -0.14191 | -0.14648 | 2.6184 | -0.17395 | -8.1619 | -0.1831 | -0.082398 | 2.7603 | 48.0972 | 47.9187 | 114.6469 | 122.6624 | 2.6184 | 122.7264 | 68.7515 | -0.1831 | 122.6624 | 2.6184 | 68.7515 | 114.6469 | 122.7264 | -122.9507 | -122.9919
1033.3281 | 123.111 | -60.0769 | 62.7182 | -0.18723 | 0.023069 | 0.018933 | 0.015137 | 0.060539 | -0.00021569 | 0.081854 | -57.4631 | 62.5717 | -60.2234 | -60.2463 | 54.57 | 8.6243 | -12.0666 | -12.2314 | 62.6724 | -60.2692 | -0.14648 | -0.14648 | 2.6138 | -0.16937 | -8.1482 | -0.19226 | -0.045777 | 2.7603 | 48.0103 | 47.8455 | 114.6469 | 122.6486 | 2.6138 | 122.7493 | 68.7012 | -0.19226 | 122.6486 | 2.6138 | 68.7012 | 114.6469 | 122.7493 | -122.9416 | -122.9874
1034.3281 | 123.1201 | -60.0906 | 62.7274 | 1.1021 | 0.025205 | 0.018079 | 0.013856 | 0.058616 | -0.00064309 | 0.082922 | -57.4219 | 62.5763 | -60.2463 | -60.2417 | 54.5609 | 8.7204 | -12.1857 | -12.2635 | 62.6495 | -60.2737 | -0.15564 | -0.15106 | 2.6688 | -0.15106 | -8.1665 | -0.18311 | -0.07782 | 2.8244 | 47.905 | 47.8271 | 114.6515 | 122.6669 | 2.6688 | 122.7402 | 68.811 | -0.18311 | 122.6669 | 2.6688 | 68.811 | 114.6515 | 122.7402 | -122.9736 | -123.0011
1035.3281 | 123.0972 | -60.0998 | 62.7045 | -0.042267 | 0.025205 | 0.019574 | 0.012147 | 0.060325 | -0.00042929 | 0.083777 | -57.4814 | 62.5717 | -60.2554 | -60.26 | 54.5609 | 8.6197 | -12.291 | -12.3093 | 62.6358 | -60.2417 | -0.15564 | -0.13275 | 2.6184 | -0.16022 | -8.1436 | -0.14191 | -0.068665 | 2.774 | 47.8088 | 47.7905 | 114.6606 | 122.6715 | 2.6184 | 122.7356 | 68.7195 | -0.14191 | 122.6715 | 2.6184 | 68.7195 | 114.6606 | 122.7356 | -122.9599 | -122.9462
1036.3281 | 123.0011 | -60.054 | 62.7457 | -0.11093 | 0.023496 | 0.017438 | 0.01001 | 0.05883 | -0.0014975 | 0.080145 | -57.431 | 62.6038 | -60.2325 | -60.2188 | 54.6158 | 8.6426 | -12.2726 | -12.2498 | 62.6404 | -60.2692 | -0.17853 | -0.14191 | 2.623 | -0.1648 | -8.1299 | -0.21515 | -0.10529 | 2.8015 | 47.7814 | 47.8043 | 114.6698 | 122.6578 | 2.623 | 122.6944 | 68.6966 | -0.21515 | 122.6578 | 2.623 | 68.6966 | 114.6698 | 122.6944 | -122.9782 | -123.0148
1037.3281 | 123.1247 | -60.0769 | 62.6999 | -0.14145 | 0.024778 | 0.015088 | 0.013215 | 0.058402 | -0.0012839 | 0.081213 | -57.4768 | 62.5946 | -60.2325 | -60.228 | 54.5883 | 8.6563 | -12.3871 | -12.3138 | 62.6404 | -60.2463 | -0.15564 | -0.10529 | 2.6001 | -0.15106 | -8.1116 | -0.16937 | -0.059509 | 2.7557 | 47.6898 | 47.7631 | 114.6652 | 122.6715 | 2.6001 | 122.7173 | 68.7332 | -0.16937 | 122.6715 | 2.6001 | 68.7332 | 114.6652 | 122.7173 | -122.9324 | -122.9462
1038.3281 | 123.1476 | -60.0677 | 62.6999 | -0.14908 | 0.023924 | 0.019574 | 0.011719 | 0.06118 | -0.00085669 | 0.079931 | -57.3898 | 62.59 | -60.2142 | -60.1685 | 54.6295 | 8.432 | -12.4512 | -12.4832 | 62.645 | -60.2692 | -0.14648 | -0.10986 | 2.6779 | -0.10071 | -8.0704 | -0.20142 | -0.054932 | 2.8244 | 47.6166 | 47.5845 | 114.6973 | 122.6578 | 2.6779 | 122.7127 | 68.4998 | -0.20142 | 122.6578 | 2.6779 | 68.4998 | 114.6973 | 122.7127 | -122.9141 | -122.9691
1039.3281 | 123.3032 | -60.0494 | 62.7548 | -0.13382 | 0.026701 | 0.01872 | 0.014924 | 0.058189 | -0.0019247 | 0.082495 | -57.4265 | 62.5946 | -60.2097 | -60.2005 | 54.6204 | 8.5831 | -12.5015 | -12.3962 | 62.6633 | -60.228 | -0.16022 | -0.16022 | 2.623 | -0.15106 | -8.1345 | -0.17853 | -0.091553 | 2.7832 | 47.5479 | 47.6532 | 114.6698 | 122.644 | 2.623 | 122.7127 | 68.6325 | -0.17853 | 122.644 | 2.623 | 68.6325 | 114.6698 | 122.7127 | -122.9645 | -122.9828
1040.3281 | 123.1338 | -60.0815 | 62.7228 | -0.042267 | 0.024565 | 0.019788 | 0.014496 | 0.059898 | -0.0023519 | 0.083349 | -57.4585 | 62.6175 | -60.2371 | -60.2234 | 54.6066 | 8.519 | -12.5244 | -12.4695 | 62.6587 | -60.2554 | -0.15564 | -0.10528 | 2.623 | -0.14191 | -8.1161 | -0.17395 | -0.064087 | 2.7786 | 47.5571 | 47.612 | 114.6881 | 122.699 | 2.623 | 122.7402 | 68.6005 | -0.17395 | 122.699 | 2.623 | 68.6005 | 114.6881 | 122.7402 | -122.9599 | -122.9782
1041.3281 | 123.1293 | -60.0632 | 62.7182 | -0.027008 | 0.027342 | 0.017438 | 0.01236 | 0.056693 | -0.0032065 | 0.082922 | -57.486 | 62.5946 | -60.2325 | -60.2509 | 54.5609 | 8.4229 | -12.6068 | -12.616 | 62.6495 | -60.26 | -0.16937 | -0.1236 | 2.5772 | -0.18768 | -8.1573 | -0.19684 | -0.068665 | 2.7466 | 47.4564 | 47.4472 | 114.624 | 122.6578 | 2.5772 | 122.7127 | 68.486 | -0.19684 | 122.6578 | 2.5772 | 68.486 | 114.624 | 122.7127 | -122.9507 | -122.9782
1042.3281 | 123.0972 | -60.0861 | 62.7136 | 0.056915 | 0.024137 | 0.019574 | 0.013642 | 0.058189 | -0.0014975 | 0.082068 | -57.5134 | 62.6266 | -60.2371 | -60.2921 | 54.5288 | 8.3908 | -12.6297 | -12.6114 | 62.6678 | -60.2463 | -0.15106 | -0.086975 | 2.5726 | -0.20599 | -8.1848 | -0.16022 | -0.045776 | 2.7237 | 47.4564 | 47.4747 | 114.6149 | 122.7127 | 2.5726 | 122.7539 | 68.4769 | -0.16022 | 122.7127 | 2.5726 | 68.4769 | 114.6149 | 122.7539 | -122.9507 | -122.9599
1043.3281 | 123.0743 | -60.0861 | 62.6816 | 0.16373 | 0.027983 | 0.018079 | 0.012574 | 0.059043 | -0.00042929 | 0.082068 | -57.5043 | 62.6083 | -60.228 | -60.2875 | 54.5288 | 8.4229 | -12.6297 | -12.5336 | 62.6266 | -60.2737 | -0.14191 | -0.073243 | 2.5818 | -0.20142 | -8.1528 | -0.18768 | -0.054932 | 2.7237 | 47.4564 | 47.5525 | 114.6149 | 122.6944 | 2.5818 | 122.7127 | 68.5089 | -0.18768 | 122.6944 | 2.5818 | 68.5089 | 114.6149 | 122.7127 | -122.9095 | -122.9553
1044.3281 | 123.0698 | -60.0769 | 62.7365 | 0.018768 | 0.025633 | 0.017224 | 0.013642 | 0.059043 | -0.00085669 | 0.08399 | -57.4905 | 62.5854 | -60.2097 | -60.2692 | 54.5563 | 8.4229 | -12.7258 | -12.6572 | 62.6633 | -60.2417 | -0.13275 | -0.15106 | 2.5864 | -0.19226 | -8.1802 | -0.16479 | -0.073242 | 2.7191 | 47.3511 | 47.4197 | 114.6332 | 122.6624 | 2.5864 | 122.7402 | 68.4998 | -0.16479 | 122.6624 | 2.5864 | 68.4998 | 114.6332 | 122.7402 | -122.9462 | -122.9782
1045.3281 | 123.1201 | -60.0677 | 62.7274 | 0.0035097 | 0.025419 | 0.015302 | 0.013001 | 0.057762 | -0.00064309 | 0.081 | -57.4997 | 62.6404 | -60.2051 | -60.2371 | 54.5837 | 8.3954 | -12.7258 | -12.6846 | 62.6633 | -60.228 | -0.13733 | -0.086975 | 2.5681 | -0.16937 | -8.1436 | -0.16022 | -0.064087 | 2.7054 | 47.3419 | 47.3831 | 114.6515 | 122.7081 | 2.5681 | 122.731 | 68.4631 | -0.16022 | 122.7081 | 2.5681 | 68.4631 | 114.6515 | 122.731 | -122.9324 | -122.9553
1046.3281 | 123.143 | -60.054 | 62.7274 | 0.041657 | 0.026914 | 0.011884 | 0.012147 | 0.058616 | -0.0014975 | 0.083349 | -57.5409 | 62.6266 | -60.1913 | -60.2509 | 54.5837 | 8.2855 | -12.8998 | -12.8174 | 62.6678 | -60.228 | -0.13733 | -0.10071 | 2.5131 | -0.19684 | -8.1436 | -0.17395 | -0.059509 | 2.6505 | 47.1542 | 47.2366 | 114.6378 | 122.6807 | 2.5131 | 122.7219 | 68.3395 | -0.17395 | 122.6807 | 2.5131 | 68.3395 | 114.6378 | 122.7219 | -122.9187 | -122.9553
1047.3281 | 123.0927 | -60.0449 | 62.7411 | 0.018768 | 0.022215 | 0.016584 | 0.012787 | 0.058402 | -0.0019247 | 0.081427 | -57.518 | 62.6083 | -60.2234 | -60.2692 | 54.57 | 8.2764 | -12.8632 | -12.7579 | 62.6678 | -60.2371 | -0.17853 | -0.13275 | 2.5269 | -0.2243 | -8.1711 | -0.19226 | -0.073242 | 2.7054 | 47.1817 | 47.287 | 114.6149 | 122.6532 | 2.5269 | 122.7127 | 68.3212 | -0.19226 | 122.6532 | 2.5269 | 68.3212 | 114.6149 | 122.7127 | -122.9645 | -122.9782
1048.3281 | 123.0698 | -60.0723 | 62.7548 | 0.072174 | 0.025205 | 0.015729 | 0.011292 | 0.058402 | -2.092e-06 | 0.081427 | -57.4905 | 62.6266 | -60.2325 | -60.2783 | 54.5654 | 8.1711 | -12.8952 | -12.8906 | 62.6678 | -60.2234 | -0.16022 | -0.12817 | 2.5818 | -0.20599 | -8.1894 | -0.15106 | -0.086975 | 2.742 | 47.1771 | 47.1817 | 114.6378 | 122.699 | 2.5818 | 122.7402 | 68.2434 | -0.15106 | 122.699 | 2.5818 | 68.2434 | 114.6378 | 122.7402 | -122.9874 | -122.9782
1049.3281 | 123.0652 | -60.0677 | 62.7274 | 0.18662 | 0.024351 | 0.021711 | 0.013428 | 0.058616 | -0.0023519 | 0.082922 | -57.518 | 62.5854 | -60.2051 | -60.2509 | 54.5654 | 8.1345 | -13.0554 | -13.028 | 62.6724 | -60.2325 | -0.13733 | -0.14191 | 2.5497 | -0.1831 | -8.1619 | -0.16479 | -0.054932 | 2.6871 | 47.0123 | 47.0398 | 114.6332 | 122.6532 | 2.5497 | 122.7402 | 68.2022 | -0.16479 | 122.6532 | 2.5497 | 68.2022 | 114.6332 | 122.7402 | -122.9324 | -122.9599
1050.3281 | 123.0743 | -60.0632 | 62.7228 | 0.17899 | 0.025205 | 0.015729 | 0.017487 | 0.058616 | -0.0029929 | 0.082068 | -57.5226 | 62.6312 | -60.2188 | -60.2509 | 54.5837 | 8.226 | -12.9272 | -12.7625 | 62.645 | -60.2554 | -0.15564 | -0.091552 | 2.5406 | -0.18768 | -8.139 | -0.19226 | -0.07782 | 2.6962 | 47.1359 | 47.3007 | 114.6469 | 122.6944 | 2.5406 | 122.7081 | 68.2892 | -0.19226 | 122.6944 | 2.5406 | 68.2892 | 114.6469 | 122.7081 | -122.9416 | -122.9782
1051.3281 | 123.0789 | -60.0632 | 62.7411 | 0.12558 | 0.026914 | 0.017011 | 0.013215 | 0.057334 | -0.00085669 | 0.083136 | -57.5317 | 62.645 | -60.2051 | -60.2554 | 54.5746 | 8.1436 | -12.9959 | -12.8723 | 62.645 | -60.2509 | -0.14191 | -0.096131 | 2.5314 | -0.19226 | -8.1665 | -0.18768 | -0.096131 | 2.6733 | 47.0673 | 47.1909 | 114.6378 | 122.7081 | 2.5314 | 122.7081 | 68.2068 | -0.18768 | 122.7081 | 2.5314 | 68.2068 | 114.6378 | 122.7081 | -122.9462 | -122.9919
1052.3281 | 123.0423 | -60.0586 | 62.7045 | -0.95016 | 0.027342 | 0.016156 | 0.013215 | 0.05883 | 0.00063871 | 0.081854 | -57.6324 | 62.6129 | -60.2142 | -60.2737 | 54.5792 | 8.1436 | -13.0325 | -12.9684 | 62.6862 | -60.2509 | -0.15564 | -0.091553 | 2.4261 | -0.21515 | -8.1253 | -0.19226 | -0.018311 | 2.5818 | 47.0261 | 47.0901 | 114.6378 | 122.6715 | 2.4261 | 122.7448 | 68.2022 | -0.19226 | 122.6715 | 2.4261 | 68.2022 | 114.6378 | 122.7448 | -122.9187 | -122.9553
1053.3281 | 123.0972 | -60.0723 | 62.7274 | 0.18662 | 0.02606 | 0.020215 | 0.01706 | 0.058189 | -0.0010703 | 0.082708 | -57.4905 | 62.6266 | -60.2005 | -60.2417 | 54.5929 | 8.1711 | -13.1012 | -12.9044 | 62.677 | -60.2325 | -0.12817 | -0.10071 | 2.5818 | -0.16937 | -8.1345 | -0.16022 | -0.050354 | 2.71 | 46.9711 | 47.168 | 114.6652 | 122.699 | 2.5818 | 122.7493 | 68.2434 | -0.16022 | 122.699 | 2.5818 | 68.2434 | 114.6652 | 122.7493 | -122.9279 | -122.9599
1054.3281 | 123.0835 | -60.0677 | 62.7548 | 0.14084 | 0.026701 | 0.013593 | 0.014283 | 0.059684 | -0.0014975 | 0.085486 | -57.5089 | 62.6312 | -60.1822 | -60.2646 | 54.6066 | 8.1024 | -13.1653 | -13.0875 | 62.6587 | -60.2188 | -0.11444 | -0.1236 | 2.5589 | -0.19684 | -8.1482 | -0.15106 | -0.096131 | 2.6733 | 46.9025 | 46.9803 | 114.6744 | 122.699 | 2.5589 | 122.7264 | 68.1702 | -0.15106 | 122.699 | 2.5589 | 68.1702 | 114.6744 | 122.7264 | -122.937 | -122.9736
1055.3281 | 123.0789 | -60.054 | 62.7411 | 0.17899 | 0.026274 | 0.017865 | 0.013642 | 0.059257 | 0.00021151 | 0.082495 | -57.5363 | 62.6312 | -60.2051 | -60.2554 | 54.5837 | 8.1116 | -13.2568 | -13.1012 | 62.645 | -60.2509 | -0.15106 | -0.10986 | 2.5177 | -0.20142 | -8.1573 | -0.19684 | -0.096131 | 2.6688 | 46.7972 | 46.9528 | 114.6378 | 122.6852 | 2.5177 | 122.699 | 68.1656 | -0.19684 | 122.6852 | 2.5177 | 68.1656 | 114.6378 | 122.699 | -122.9462 | -122.9919
1056.3281 | 123.0972 | -60.0357 | 62.7274 | 0.23239 | 0.026701 | 0.018293 | 0.015992 | 0.059471 | -0.00042929 | 0.083349 | -57.4905 | 62.6495 | -60.1959 | -60.2097 | 54.6387 | 8.1161 | -13.4125 | -13.1287 | 62.6266 | -60.2188 | -0.16022 | -0.07782 | 2.5452 | -0.17395 | -8.0887 | -0.18311 | -0.10071 | 2.7054 | 46.6232 | 46.907 | 114.6744 | 122.6852 | 2.5452 | 122.6624 | 68.1519 | -0.18311 | 122.6852 | 2.5452 | 68.1519 | 114.6744 | 122.6624 | -122.9233 | -122.9462
1057.3281 | 123.1338 | -60.0266 | 62.7319 | -0.76706 | 0.025846 | 0.019147 | 0.01941 | 0.060325 | 0.00021151 | 0.082922 | -57.399 | 62.677 | -60.1685 | -60.1913 | 54.6112 | 8.0612 | -13.4445 | -13.2431 | 62.6221 | -60.2234 | -0.14191 | -0.054932 | 2.6276 | -0.16479 | -8.1207 | -0.19684 | -0.10986 | 2.7695 | 46.582 | 46.7834 | 114.6378 | 122.7036 | 2.6276 | 122.6486 | 68.0878 | -0.19684 | 122.7036 | 2.6276 | 68.0878 | 114.6378 | 122.6486 | -122.9004 | -122.9553
1058.3281 | 123.0972 | -60.0494 | 62.7319 | 0.2095 | 0.028196 | 0.020429 | 0.01471 | 0.055625 | -0.0010703 | 0.082495 | -57.5592 | 62.6541 | -60.2097 | -60.26 | 54.6112 | 8.0338 | -13.3163 | -13.1241 | 62.6358 | -60.2325 | -0.16022 | -0.07782 | 2.4902 | -0.21057 | -8.1207 | -0.18311 | -0.096131 | 2.6505 | 46.7331 | 46.9254 | 114.6606 | 122.7036 | 2.4902 | 122.6852 | 68.0832 | -0.18311 | 122.7036 | 2.4902 | 68.0832 | 114.6606 | 122.6852 | -122.9416 | -122.9645
1059.3281 | 123.1247 | -60.022 | 62.7411 | 0.34683 | 0.027983 | 0.022779 | 0.016633 | 0.062461 | -0.00085669 | 0.083349 | -57.4631 | 62.6587 | -60.1639 | -60.1959 | 54.6478 | 8.0475 | -13.4262 | -13.1699 | 62.645 | -60.2051 | -0.14191 | -0.082398 | 2.5589 | -0.17395 | -8.0933 | -0.1831 | -0.096131 | 2.7008 | 46.5958 | 46.8521 | 114.6698 | 122.6807 | 2.5589 | 122.6669 | 68.0695 | -0.1831 | 122.6807 | 2.5589 | 68.0695 | 114.6698 | 122.6669 | -122.905 | -122.9462
1060.3281 | 123.1064 | -60.0357 | 62.7457 | 0.2095 | 0.02606 | 0.019147 | 0.015565 | 0.061607 | -0.0023519 | 0.083136 | -57.5317 | 62.6816 | -60.1776 | -60.2097 | 54.6341 | 7.988 | -13.4308 | -13.2248 | 62.6587 | -60.2005 | -0.14191 | -0.064087 | 2.504 | -0.17395 | -8.1116 | -0.16479 | -0.086976 | 2.6459 | 46.6049 | 46.8109 | 114.6698 | 122.7173 | 2.504 | 122.6944 | 68.0237 | -0.16479 | 122.7173 | 2.504 | 68.0237 | 114.6698 | 122.6944 | -122.9233 | -122.9462
1061.3281 | 123.1247 | -60.0449 | 62.7319 | -0.034637 | 0.027555 | 0.021924 | 0.015778 | 0.057121 | -0.0012839 | 0.083777 | -57.5089 | 62.6633 | -60.1547 | -60.1913 | 54.6478 | 7.8873 | -13.623 | -13.3438 | 62.6541 | -60.2188 | -0.10986 | -0.068665 | 2.536 | -0.14648 | -8.0841 | -0.17395 | -0.07782 | 2.6459 | 46.4218 | 46.701 | 114.6927 | 122.7081 | 2.536 | 122.699 | 67.9321 | -0.17395 | 122.7081 | 2.536 | 67.9321 | 114.6927 | 122.699 | -122.8867 | -122.9507
1062.3281 | 123.143 | -60.0403 | 62.7502 | 0.21713 | 0.027342 | 0.020642 | 0.021119 | 0.058402 | -0.0025657 | 0.08399 | -57.4814 | 62.6816 | -60.1639 | -60.2371 | 54.6295 | 7.9651 | -13.5544 | -13.2889 | 62.6495 | -60.228 | -0.1236 | -0.068664 | 2.5589 | -0.19684 | -8.1207 | -0.18768 | -0.10071 | 2.6825 | 46.4859 | 46.7514 | 114.6698 | 122.7219 | 2.5589 | 122.6898 | 68.0054 | -0.18768 | 122.7219 | 2.5589 | 68.0054 | 114.6698 | 122.6898 | -122.9141 | -122.9782
1063.3281 | 123.0286 | -60.0311 | 62.7731 | 0.20187 | 0.027128 | 0.021711 | 0.019837 | 0.060325 | -0.00042929 | 0.082922 | -57.5912 | 62.7502 | -60.1959 | -60.2829 | 54.5792 | 7.8598 | -13.4995 | -13.4857 | 62.6907 | -60.2737 | -0.16479 | -0.022888 | 2.4399 | -0.25177 | -8.194 | -0.24262 | -0.082397 | 2.6047 | 46.5317 | 46.5454 | 114.6103 | 122.7814 | 2.4399 | 122.7219 | 67.8909 | -0.24262 | 122.7814 | 2.4399 | 67.8909 | 114.6103 | 122.7219 | -122.9691 | -123.0469
1064.3281 | 122.9874 | -60.054 | 62.7914 | 0.20187 | 0.028623 | 0.022565 | 0.017274 | 0.06182 | -0.00021569 | 0.081854 | -57.5775 | 62.7869 | -60.2188 | -60.2966 | 54.5654 | 7.6859 | -13.5864 | -13.5956 | 62.7045 | -60.2737 | -0.1648 | -0.004578 | 2.4765 | -0.24262 | -8.226 | -0.21973 | -0.086975 | 2.6413 | 46.4676 | 46.4584 | 114.6194 | 122.8409 | 2.4765 | 122.7585 | 67.7399 | -0.21973 | 122.8409 | 2.4765 | 67.7399 | 114.6194 | 122.7585 | -123.0103 | -123.0652
1065.3281 | 123.2117 | -60.0449 | 62.7548 | 0.36209 | 0.029264 | 0.020642 | 0.015992 | 0.060752 | -2.092e-06 | 0.082495 | -57.5317 | 62.6816 | -60.2005 | -60.1959 | 54.657 | 7.9239 | -13.5635 | -13.4674 | 62.6358 | -60.2554 | -0.15564 | -0.073242 | 2.5131 | -0.15106 | -8.0978 | -0.21057 | -0.11902 | 2.6688 | 46.4813 | 46.5775 | 114.7018 | 122.7264 | 2.5131 | 122.6807 | 67.9688 | -0.21057 | 122.7264 | 2.5131 | 67.9688 | 114.7018 | 122.6807 | -122.9553 | -123.0103
1066.3281 | 123.1155 | -60.0311 | 62.7365 | 0.2858 | 0.027128 | 0.02107 | 0.015992 | 0.061607 | 0.0012795 | 0.083349 | -57.55 | 62.764 | -60.2005 | -60.228 | 54.6387 | 7.7911 | -13.6002 | -13.3347 | 62.6816 | -60.2554 | -0.16937 | 0.027466 | 2.4811 | -0.19684 | -8.0978 | -0.2243 | -0.054931 | 2.6505 | 46.431 | 46.6965 | 114.6698 | 122.7951 | 2.4811 | 122.7127 | 67.8223 | -0.2243 | 122.7951 | 2.4811 | 67.8223 | 114.6698 | 122.7127 | -122.937 | -122.9919
1067.3281 | 123.0652 | -60.0403 | 62.7686 | 0.24765 | 0.030119 | 0.02107 | 0.018128 | 0.062248 | 0.00063871 | 0.081427 | -57.5821 | 62.764 | -60.2051 | -60.2692 | 54.5929 | 7.6904 | -13.6368 | -13.4445 | 62.6816 | -60.2829 | -0.16479 | -0.004578 | 2.4582 | -0.22888 | -8.1757 | -0.24262 | -0.086975 | 2.623 | 46.4035 | 46.5958 | 114.6332 | 122.8043 | 2.4582 | 122.7219 | 67.7307 | -0.24262 | 122.8043 | 2.4582 | 67.7307 | 114.6332 | 122.7219 | -122.9736 | -123.0515
1068.3281 | 123.024 | -60.054 | 62.7777 | 0.22476 | 0.029692 | 0.020002 | 0.017274 | 0.060966 | 0.00042511 | 0.082708 | -57.5912 | 62.8052 | -60.1959 | -60.2737 | 54.6158 | 7.7866 | -13.5956 | -13.5269 | 62.7182 | -60.2829 | -0.14191 | 0.027466 | 2.4628 | -0.21973 | -8.1619 | -0.22888 | -0.059509 | 2.6047 | 46.4584 | 46.5271 | 114.6698 | 122.8592 | 2.4628 | 122.7722 | 67.8406 | -0.22888 | 122.8592 | 2.4628 | 67.8406 | 114.6698 | 122.7722 | -122.9736 | -123.0606
1069.3281 | 123.024 | -60.0449 | 62.7914 | 0.13321 | 0.028837 | 0.019788 | 0.016846 | 0.061607 | 0.00085231 | 0.082495 | -57.6096 | 62.8006 | -60.1913 | -60.2966 | 54.5746 | 7.6996 | -13.5956 | -13.5818 | 62.7136 | -60.3012 | -0.14648 | 0.009155 | 2.4353 | -0.25177 | -8.2169 | -0.25635 | -0.07782 | 2.5818 | 46.4493 | 46.463 | 114.6194 | 122.8455 | 2.4353 | 122.7585 | 67.7444 | -0.25635 | 122.8455 | 2.4353 | 67.7444 | 114.6194 | 122.7585 | -122.9828 | -123.0927
1070.3281 | 122.9828 | -60.0449 | 62.8189 | 0.087433 | 0.027983 | 0.018079 | 0.015778 | 0.064811 | 0.00021151 | 0.082708 | -57.5821 | 62.8326 | -60.1822 | -60.2737 | 54.57 | 7.5668 | -13.6505 | -13.6047 | 62.7411 | -60.2692 | -0.13733 | 0.013733 | 2.4628 | -0.22888 | -8.2489 | -0.2243 | -0.07782 | 2.6001 | 46.3943 | 46.4401 | 114.6149 | 122.8775 | 2.4628 | 122.7859 | 67.6117 | -0.2243 | 122.8775 | 2.4628 | 67.6117 | 114.6149 | 122.7859 | -123.0011 | -123.0881
1071.3281 | 122.9828 | -60.0632 | 62.8006 | 0.095062 | 0.027769 | 0.020642 | 0.018342 | 0.063529 | 0.00063871 | 0.08399 | -57.5638 | 62.8143 | -60.1776 | -60.2554 | 54.6295 | 7.6309 | -13.6597 | -13.6276 | 62.7319 | -60.2783 | -0.11444 | 0.013733 | 2.4994 | -0.19226 | -8.1711 | -0.21515 | -0.068664 | 2.6138 | 46.4035 | 46.4355 | 114.6927 | 122.8775 | 2.4994 | 122.7951 | 67.6941 | -0.21515 | 122.8775 | 2.4994 | 67.6941 | 114.6927 | 122.7951 | -122.9782 | -123.0789
1072.3281 | 123.0057 | -60.0723 | 62.8098 | 0.22476 | 0.029905 | 0.021497 | 0.014283 | 0.063316 | 0.00085231 | 0.082922 | -57.605 | 62.8189 | -60.1776 | -60.2966 | 54.5746 | 7.5577 | -13.8153 | -13.8336 | 62.7594 | -60.2692 | -0.10529 | 0.009156 | 2.4673 | -0.2243 | -8.2352 | -0.19684 | -0.050354 | 2.5726 | 46.257 | 46.2387 | 114.6469 | 122.8912 | 2.4673 | 122.8317 | 67.63 | -0.19684 | 122.8912 | 2.4673 | 67.63 | 114.6469 | 122.8317 | -122.9874 | -123.0789
1073.3281 | 123.0194 | -60.054 | 62.8098 | -1.9038 | 0.026274 | 0.017865 | 0.014496 | 0.062461 | 0.0014933 | 0.083563 | -57.6416 | 62.8326 | -60.1685 | -60.3149 | 54.5929 | 7.5348 | -13.8886 | -13.8382 | 62.7457 | -60.2875 | -0.11444 | 0.022889 | 2.4124 | -0.26093 | -8.2169 | -0.23346 | -0.064086 | 2.5269 | 46.1655 | 46.2158 | 114.6469 | 122.8867 | 2.4124 | 122.7997 | 67.5888 | -0.23346 | 122.8867 | 2.4124 | 67.5888 | 114.6469 | 122.7997 | -122.9782 | -123.0972
1074.3281 | 123.0469 | -60.0311 | 62.8006 | 0.095062 | 0.029478 | 0.018506 | 0.015137 | 0.062034 | -0.0010703 | 0.084631 | -57.6462 | 62.8418 | -60.1959 | -60.2646 | 54.1626 | 7.2327 | -13.353 | -13.6963 | 62.7731 | -60.26 | -0.16479 | 0.041199 | 2.3849 | -0.23346 | -8.638 | -0.22888 | -0.027466 | 2.5497 | 46.6782 | 46.3348 | 114.1937 | 122.8729 | 2.3849 | 122.8043 | 67.2638 | -0.22888 | 122.8729 | 2.3849 | 67.2638 | 114.1937 | 122.8043 | -122.9965 | -123.0606
1075.3281 | 122.9874 | -60.0403 | 62.7914 | 0.087433 | 0.028623 | 0.020002 | 0.017701 | 0.063316 | 0.00085231 | 0.08399 | -57.6187 | 62.8372 | -60.1639 | -60.2966 | 54.6158 | 7.576 | -13.7787 | -13.7924 | 62.7548 | -60.2646 | -0.1236 | 0.045776 | 2.4216 | -0.25635 | -8.1757 | -0.2243 | -0.036621 | 2.5452 | 46.2616 | 46.2479 | 114.6561 | 122.8775 | 2.4216 | 122.7951 | 67.6163 | -0.2243 | 122.8775 | 2.4216 | 67.6163 | 114.6561 | 122.7951 | -122.9553 | -123.056
1076.3281 | 122.9691 | -60.0403 | 62.8143 | 0.14084 | 0.029264 | 0.016584 | 0.016633 | 0.062461 | -0.0010703 | 0.082495 | -57.5821 | 62.8052 | -60.1685 | -60.2646 | 54.5929 | 7.4936 | -13.8336 | -13.6688 | 62.7869 | -60.2554 | -0.12817 | -0.009155 | 2.4582 | -0.2243 | -8.2214 | -0.21515 | -0.027466 | 2.5864 | 46.2067 | 46.3715 | 114.6332 | 122.8455 | 2.4582 | 122.8271 | 67.5339 | -0.21515 | 122.8455 | 2.4582 | 67.5339 | 114.6332 | 122.8271 | -122.9828 | -123.0698
1077.3281 | 123.0331 | -60.022 | 62.8189 | -0.049896 | 0.029905 | 0.019361 | 0.015565 | 0.064384 | 0.0014933 | 0.083777 | -57.5272 | 62.8281 | -60.1639 | -60.2097 | 54.6616 | 7.5897 | -13.8748 | -13.7192 | 62.764 | -60.2554 | -0.14191 | 0.009155 | 2.4948 | -0.18768 | -8.1573 | -0.23346 | -0.054932 | 2.6367 | 46.1472 | 46.3028 | 114.6835 | 122.85 | 2.4948 | 122.7859 | 67.6117 | -0.23346 | 122.85 | 2.4948 | 67.6117 | 114.6835 | 122.7859 | -122.9828 | -123.0743
1078.3281 | 123.0515 | -60.0037 | 62.796 | 0.056915 | 0.030332 | 0.020642 | 0.014069 | 0.064811 | -0.0017111 | 0.082281 | -57.5592 | 62.8418 | -60.1501 | -60.2051 | 54.6844 | 7.5348 | -14.0121 | -13.7924 | 62.7869 | -60.2554 | -0.14648 | 0.045776 | 2.4445 | -0.20142 | -8.1116 | -0.25177 | -0.009156 | 2.5909 | 45.9915 | 46.2112 | 114.6881 | 122.8455 | 2.4445 | 122.7905 | 67.5385 | -0.25177 | 122.8455 | 2.4445 | 67.5385 | 114.6881 | 122.7905 | -122.9462 | -123.0515
1079.3281 | 122.9782 | -60.0174 | 62.8326 | 0.049286 | 0.029051 | 0.020856 | 0.014496 | 0.064384 | 0.0019205 | 0.084417 | -57.6004 | 62.8418 | -60.1593 | -60.2554 | 54.6249 | 7.37 | -14.0305 | -13.9709 | 62.7869 | -60.2325 | -0.14191 | 0.009155 | 2.417 | -0.23804 | -8.2077 | -0.21515 | -0.045777 | 2.5589 | 45.9869 | 46.0464 | 114.6423 | 122.8592 | 2.417 | 122.8043 | 67.3874 | -0.21515 | 122.8592 | 2.417 | 67.3874 | 114.6423 | 122.8043 | -122.9919 | -123.0652
1080.3281 | 122.9965 | -60.0266 | 62.8235 | 0.087433 | 0.029051 | 0.020856 | 0.015565 | 0.061393 | 0.0023477 | 0.084631 | -57.5821 | 62.8555 | -60.141 | -60.2325 | 54.6249 | 7.4432 | -14.0579 | -13.9847 | 62.7777 | -60.2234 | -0.11444 | 0.032044 | 2.4445 | -0.20599 | -8.1985 | -0.19684 | -0.045776 | 2.5589 | 45.9686 | 46.0419 | 114.6515 | 122.8821 | 2.4445 | 122.8043 | 67.4698 | -0.19684 | 122.8821 | 2.4445 | 67.4698 | 114.6515 | 122.8043 | -122.9645 | -123.0469
1081.3281 | 123.0194 | -60.022 | 62.8372 | 0.026398 | 0.029051 | 0.021711 | 0.016846 | 0.062889 | 0.00085231 | 0.084417 | -57.5363 | 62.851 | -60.1593 | -60.2371 | 54.6753 | 7.457 | -14.1037 | -13.8153 | 62.7731 | -60.2325 | -0.13733 | 0.013733 | 2.4857 | -0.21515 | -8.1619 | -0.21057 | -0.064087 | 2.623 | 45.9183 | 46.2067 | 114.6973 | 122.8729 | 2.4857 | 122.7951 | 67.4789 | -0.21057 | 122.8729 | 2.4857 | 67.4789 | 114.6973 | 122.7951 | -122.9965 | -123.0698
1082.3281 | 123.0148 | -59.9991 | 62.8235 | 0.011139 | 0.030546 | 0.018506 | 0.016846 | 0.062248 | 0.0010659 | 0.081854 | -57.5729 | 62.851 | -60.141 | -60.2097 | 54.657 | 7.3837 | -14.1907 | -13.9343 | 62.8235 | -60.2463 | -0.14191 | 0.027466 | 2.4261 | -0.21057 | -8.1665 | -0.24719 | 0 | 2.5681 | 45.8084 | 46.0648 | 114.6561 | 122.85 | 2.4261 | 122.8226 | 67.3828 | -0.24719 | 122.85 | 2.4261 | 67.3828 | 114.6561 | 122.8226 | -122.9645 | -123.0698
1083.3281 | 123.0103 | -60.0082 | 62.8281 | 0.29343 | 0.027555 | 0.018293 | 0.017914 | 0.062034 | -0.00021569 | 0.081854 | -57.518 | 62.8647 | -60.1227 | -60.1959 | 54.6844 | 7.3563 | -14.2044 | -13.9069 | 62.8006 | -60.2097 | -0.11444 | 0.036621 | 2.4902 | -0.18768 | -8.1436 | -0.20142 | -0.027466 | 2.6047 | 45.8038 | 46.1014 | 114.6927 | 122.8729 | 2.4902 | 122.8088 | 67.3645 | -0.20142 | 122.8729 | 2.4902 | 67.3645 | 114.6927 | 122.8088 | -122.9507 | -123.0377
1084.3281 | 123.0423 | -60.0174 | 62.8326 | -0.16434 | 0.030546 | 0.019147 | 0.013215 | 0.062034 | -0.00042929 | 0.084631 | -57.5546 | 62.8693 | -60.1501 | -60.1959 | 54.689 | 7.338 | -14.209 | -13.9481 | 62.8189 | -60.2142 | -0.13275 | 0.036621 | 2.4628 | -0.17853 | -8.1436 | -0.19684 | -0.013733 | 2.5955 | 45.8084 | 46.0693 | 114.7064 | 122.8867 | 2.4628 | 122.8363 | 67.3553 | -0.19684 | 122.8867 | 2.4628 | 67.3553 | 114.7064 | 122.8363 | -122.9828 | -123.0469
1085.3281 | 123.0148 | -59.9808 | 62.8647 | -0.14908 | 0.025633 | 0.017865 | 0.014496 | 0.062034 | 0.00042511 | 0.080786 | -57.5958 | 62.8693 | -60.1227 | -60.2325 | 54.6936 | 7.3425 | -14.1907 | -14.0442 | 62.8601 | -60.228 | -0.14191 | 0.004578 | 2.3849 | -0.25177 | -8.1711 | -0.24719 | -0.004578 | 2.5269 | 45.7901 | 45.9366 | 114.6744 | 122.85 | 2.3849 | 122.8409 | 67.3233 | -0.24719 | 122.85 | 2.3849 | 67.3233 | 114.6744 | 122.8409 | -122.9874 | -123.0927
1086.3281 | 123.0148 | -59.9854 | 62.8647 | -0.56107 | 0.028196 | 0.016797 | 0.014924 | 0.06182 | -2.092e-06 | 0.082068 | -57.5684 | 62.8876 | -60.1181 | -60.1868 | 54.7073 | 7.3196 | -14.3692 | -14.0854 | 62.8189 | -60.2097 | -0.13275 | 0.022888 | 2.417 | -0.20142 | -8.1573 | -0.2243 | -0.045776 | 2.5497 | 45.6161 | 45.9 | 114.6927 | 122.8729 | 2.417 | 122.8043 | 67.305 | -0.2243 | 122.8729 | 2.417 | 67.305 | 114.6927 | 122.8043 | -122.9828 | -123.0743
1087.3281 | 123.056 | -59.9854 | 62.8464 | -0.057526 | 0.028196 | 0.019361 | 0.015565 | 0.062675 | -0.0010703 | 0.083136 | -57.518 | 62.8693 | -60.1089 | -60.3745 | 54.7256 | 7.4295 | -14.3829 | -14.0167 | 62.8647 | -60.1822 | -0.1236 | 0.022888 | 2.4673 | -0.3891 | -8.1207 | -0.19684 | 0.01831 | 2.5909 | 45.6024 | 45.9686 | 114.711 | 122.8546 | 2.4673 | 122.85 | 67.4149 | -0.19684 | 122.8546 | 2.4673 | 67.4149 | 114.711 | 122.85 | -122.9553 | -123.0286
1088.3281 | 123.0652 | -59.967 | 62.883 | -0.095673 | 0.027769 | 0.020215 | 0.015137 | 0.063102 | -0.00085669 | 0.082068 | -57.5455 | 62.8784 | -60.0906 | -60.1685 | 54.7028 | 7.196 | -14.3509 | -14.1907 | 62.8326 | -60.2097 | -0.1236 | -0.004578 | 2.4216 | -0.20142 | -8.1802 | -0.24262 | -0.050354 | 2.5452 | 45.6162 | 45.7764 | 114.6698 | 122.8455 | 2.4216 | 122.7997 | 67.1631 | -0.24262 | 122.8455 | 2.4216 | 67.1631 | 114.6698 | 122.7997 | -122.9736 | -123.0927
1089.3281 | 123.0423 | -59.9716 | 62.8647 | -0.15671 | 0.027128 | 0.010175 | 0.014924 | 0.060966 | -0.0012839 | 0.082281 | -57.5546 | 62.8922 | -60.1181 | -60.1959 | 54.689 | 7.1869 | -14.4104 | -14.2319 | 62.8555 | -60.2051 | -0.14648 | 0.027466 | 2.417 | -0.2243 | -8.1757 | -0.23346 | -0.009155 | 2.5635 | 45.5612 | 45.7397 | 114.6606 | 122.8638 | 2.417 | 122.8271 | 67.1585 | -0.23346 | 122.8638 | 2.417 | 67.1585 | 114.6606 | 122.8271 | -122.9828 | -123.0698
1090.3281 | 123.0331 | -59.9579 | 62.8555 | -0.14145 | 0.025419 | 0.019361 | 0.015137 | 0.063316 | 0.00042511 | 0.082922 | -57.605 | 62.883 | -60.1364 | -60.2097 | 54.6844 | 7.196 | -14.2914 | -14.1403 | 62.8693 | -60.1685 | -0.17853 | 0.027466 | 2.3529 | -0.25177 | -8.1711 | -0.21057 | 0.013733 | 2.5314 | 45.6665 | 45.8176 | 114.6423 | 122.8409 | 2.3529 | 122.8271 | 67.1539 | -0.21057 | 122.8409 | 2.3529 | 67.1539 | 114.6423 | 122.8271 | -122.9919 | -123.024
1091.3281 | 122.9828 | -59.9579 | 62.8738 | -0.19485 | 0.026487 | 0.020002 | 0.011506 | 0.058402 | 0.00063871 | 0.084631 | -57.6096 | 62.851 | -60.1227 | -60.3928 | 54.5105 | 7.1045 | -14.5065 | -14.415 | 62.8555 | -60.1913 | -0.16479 | -0.022888 | 2.3483 | -0.43487 | -8.3633 | -0.23346 | -0.01831 | 2.5131 | 45.4514 | 45.5429 | 114.4684 | 122.8088 | 2.3483 | 122.8134 | 67.0624 | -0.23346 | 122.8088 | 2.3483 | 67.0624 | 114.4684 | 122.8134 | -122.9965 | -123.0652
1092.3281 | 123.0103 | -59.9808 | 62.8967 | -0.1796 | 0.024778 | 0.019574 | 0.011079 | 0.061607 | 0.0010659 | 0.082708 | -57.5546 | 62.8235 | -60.1089 | -60.1776 | 54.6982 | 7.2739 | -14.3784 | -14.2136 | 62.883 | -60.1639 | -0.12817 | -0.073243 | 2.4261 | -0.19684 | -8.1985 | -0.18311 | -0.013733 | 2.5543 | 45.6024 | 45.7672 | 114.679 | 122.8043 | 2.4261 | 122.8638 | 67.2546 | -0.18311 | 122.8043 | 2.4261 | 67.2546 | 114.679 | 122.8638 | -123.0057 | -123.0606
1093.3281 | 122.9828 | -59.9487 | 62.8693 | -0.14145 | 0.02606 | 0.015302 | 0.016205 | 0.061393 | -0.0014975 | 0.08164 | -57.605 | 62.8464 | -60.1089 | -60.2005 | 54.6936 | 7.2739 | -14.3829 | -14.241 | 62.8738 | -60.1639 | -0.16022 | -0.022888 | 2.3438 | -0.25177 | -8.1757 | -0.21515 | 0.004577 | 2.504 | 45.5658 | 45.7077 | 114.6423 | 122.7951 | 2.3438 | 122.8226 | 67.2226 | -0.21515 | 122.7951 | 2.3438 | 67.2226 | 114.6423 | 122.8226 | -122.9782 | -123.0331
1094.3281 | 122.9919 | -59.9854 | 62.883 | -0.1796 | 0.027342 | 0.017865 | 0.013428 | 0.061607 | -0.0014975 | 0.082708 | -57.5821 | 62.8738 | -60.1044 | -60.2005 | 54.689 | 7.1686 | -14.4836 | -14.3143 | 62.8738 | -60.1868 | -0.11902 | -0.009156 | 2.4033 | -0.21515 | -8.194 | -0.20142 | -0.009156 | 2.5223 | 45.5017 | 45.6711 | 114.6744 | 122.8592 | 2.4033 | 122.8592 | 67.1539 | -0.20142 | 122.8592 | 2.4033 | 67.1539 | 114.6744 | 122.8592 | -122.9874 | -123.0698
1095.3281 | 123.0148 | -59.9625 | 62.8876 | -0.78995 | 0.028623 | 0.021924 | 0.010651 | 0.06182 | -0.00064309 | 0.084204 | -57.8064 | 62.8372 | -60.1273 | -60.228 | 54.689 | 7.1045 | -14.5386 | -14.3921 | 62.9013 | -60.1776 | -0.16479 | -0.050354 | 2.1561 | -0.2655 | -8.1985 | -0.21515 | 0.013733 | 2.3209 | 45.4239 | 45.5704 | 114.6515 | 122.7997 | 2.1561 | 122.8638 | 67.067 | -0.21515 | 122.7997 | 2.1561 | 67.067 | 114.6515 | 122.8638 | -123.0148 | -123.0652
1096.3281 | 122.9553 | -59.935 | 62.9013 | -0.16434 | 0.026274 | 0.020215 | 0.010224 | 0.060752 | -0.00085669 | 0.080145 | -57.6004 | 62.8464 | -60.0906 | -60.1913 | 54.689 | 7.2144 | -14.3188 | -14.0671 | 62.9379 | -60.1135 | -0.15564 | -0.054931 | 2.3346 | -0.25635 | -8.2123 | -0.17853 | 0.036621 | 2.4902 | 45.6162 | 45.8679 | 114.624 | 122.7814 | 2.3346 | 122.8729 | 67.1494 | -0.17853 | 122.7814 | 2.3346 | 67.1494 | 114.624 | 122.8729 | -122.9919 | -123.0148
1097.3281 | 122.9782 | -59.9625 | 62.9013 | -0.17197 | 0.026914 | 0.015729 | 0.010865 | 0.05883 | 0.00042511 | 0.083349 | -57.5455 | 62.8143 | -60.0952 | -60.1776 | 54.7073 | 7.0633 | -14.5889 | -14.4196 | 62.8601 | -60.1456 | -0.13275 | -0.086975 | 2.417 | -0.21515 | -8.194 | -0.18311 | -0.041199 | 2.5497 | 45.3735 | 45.5429 | 114.6698 | 122.7768 | 2.417 | 122.8226 | 67.0258 | -0.18311 | 122.7768 | 2.417 | 67.0258 | 114.6698 | 122.8226 | -122.9965 | -123.0469
1098.3281 | 123.1155 | -59.9213 | 62.883 | -0.18723 | 0.024351 | 0.015729 | 0.010651 | 0.059257 | 0.00063871 | 0.082495 | -57.4768 | 62.7731 | -60.0632 | -60.0723 | 54.8035 | 7.1274 | -14.8178 | -14.3738 | 62.8464 | -60.1181 | -0.14191 | -0.10986 | 2.4445 | -0.15106 | -8.0795 | -0.19684 | -0.036621 | 2.5864 | 45.1035 | 45.5475 | 114.7247 | 122.6944 | 2.4445 | 122.7676 | 67.0486 | -0.19684 | 122.6944 | 2.4445 | 67.0486 | 114.7247 | 122.7676 | -122.9462 | -123.0011
1099.3281 | 123.1293 | -59.9121 | 62.8647 | 2.3305 | 0.024351 | 0.01637 | 0.011719 | 0.061393 | -0.0023519 | 0.083349 | -57.3944 | 62.764 | -60.0906 | -60.0998 | 54.7806 | 7.1732 | -14.8544 | -14.447 | 62.8555 | -60.0952 | -0.17853 | -0.10071 | 2.5177 | -0.18768 | -8.0841 | -0.18311 | -0.009155 | 2.6962 | 45.0577 | 45.4651 | 114.6927 | 122.6761 | 2.5177 | 122.7676 | 67.0853 | -0.18311 | 122.6761 | 2.5177 | 67.0853 | 114.6927 | 122.7676 | -122.9553 | -122.9599
1100.3281 | 123.0515 | -59.9213 | 62.8967 | -0.20248 | 0.023069 | 0.017224 | 0.011079 | 0.058402 | -0.00064309 | 0.082708 | -57.5592 | 62.8143 | -60.0769 | -60.1364 | 54.7577 | 7.0404 | -14.8544 | -14.4653 | 62.8555 | -60.1456 | -0.15564 | -0.082398 | 2.3621 | -0.21515 | -8.139 | -0.2243 | -0.041199 | 2.5177 | 45.0668 | 45.4559 | 114.679 | 122.7356 | 2.3621 | 122.7768 | 66.9617 | -0.2243 | 122.7356 | 2.3621 | 66.9617 | 114.679 | 122.7768 | -122.9736 | -123.0423
1101.3281 | 123.0515 | -59.9167 | 62.9105 | -0.15671 | 0.025419 | 0.017224 | 0.011719 | 0.059257 | -0.0027793 | 0.081427 | -57.5089 | 62.7914 | -60.0586 | -60.0952 | 54.7623 | 7.0953 | -14.8544 | -14.4745 | 62.851 | -60.1044 | -0.14191 | -0.11902 | 2.4078 | -0.17853 | -8.1482 | -0.18768 | -0.059509 | 2.5497 | 45.0623 | 45.4422 | 114.679 | 122.7081 | 2.4078 | 122.7676 | 67.012 | -0.18768 | 122.7081 | 2.4078 | 67.012 | 114.679 | 122.7676 | -122.9691 | -123.0148
1102.3281 | 123.111 | -59.8892 | 62.8784 | -0.14145 | 0.025419 | 0.016156 | 0.011719 | 0.060966 | -0.0017111 | 0.082495 | -57.5089 | 62.7731 | -60.0769 | -60.0586 | 54.7852 | 7.0999 | -14.9506 | -14.4974 | 62.8464 | -60.1089 | -0.18768 | -0.10529 | 2.3804 | -0.16937 | -8.0933 | -0.21973 | -0.032043 | 2.5681 | 44.9387 | 45.3918 | 114.6744 | 122.6624 | 2.3804 | 122.7356 | 66.9891 | -0.21973 | 122.6624 | 2.3804 | 66.9891 | 114.6744 | 122.7356 | -122.9553 | -122.9874
1103.3281 | 123.143 | -59.8938 | 62.8967 | 0.22476 | 0.026274 | 0.017865 | 0.010438 | 0.058402 | -0.0012839 | 0.082068 | -57.7148 | 62.7457 | -60.0677 | -60.0494 | 54.8126 | 7.0496 | -14.9826 | -14.4974 | 62.8143 | -60.0769 | -0.17395 | -0.15106 | 2.179 | -0.15564 | -8.0841 | -0.1831 | -0.082398 | 2.3529 | 44.9112 | 45.3964 | 114.7064 | 122.6395 | 2.179 | 122.7081 | 66.9434 | -0.1831 | 122.6395 | 2.179 | 66.9434 | 114.7064 | 122.7081 | -122.9645 | -122.9736
1104.3281 | 123.1476 | -59.8892 | 62.9425 | -0.17197 | 0.023924 | 0.014875 | 0.013428 | 0.057548 | -0.0019247 | 0.082708 | -57.5089 | 62.7686 | -60.0403 | -60.054 | 54.8264 | 7.0038 | -15.0558 | -14.534 | 62.8693 | -60.0677 | -0.15106 | -0.17395 | 2.3804 | -0.16479 | -8.1161 | -0.17853 | -0.073242 | 2.5314 | 44.8334 | 45.3552 | 114.7156 | 122.6578 | 2.3804 | 122.7585 | 66.893 | -0.17853 | 122.6578 | 2.3804 | 66.893 | 114.7156 | 122.7585 | -122.9828 | -123.0103
1105.3281 | 123.0698 | -59.8801 | 62.8784 | 0.041657 | 0.023924 | 0.014875 | 0.010865 | 0.06118 | -0.00042929 | 0.082068 | -57.5912 | 62.7686 | -60.0723 | -60.1227 | 54.7531 | 6.9901 | -15.033 | -14.6713 | 62.8464 | -60.0998 | -0.19226 | -0.10986 | 2.2888 | -0.24262 | -8.1253 | -0.21973 | -0.032043 | 2.4811 | 44.8471 | 45.2087 | 114.6332 | 122.6486 | 2.2888 | 122.7264 | 66.8701 | -0.21973 | 122.6486 | 2.2888 | 66.8701 | 114.6332 | 122.7264 | -122.9507 | -122.9782
1106.3281 | 123.1018 | -59.9258 | 62.8738 | -0.0041198 | 0.024565 | 0.017652 | 0.012574 | 0.058189 | -0.0032065 | 0.083349 | -57.5775 | 62.8052 | -60.0494 | -60.0906 | 54.7806 | 6.9305 | -15.1474 | -14.7675 | 62.8281 | -60.0952 | -0.1236 | -0.068664 | 2.3483 | -0.16479 | -8.0933 | -0.16937 | -0.045776 | 2.4719 | 44.7784 | 45.1584 | 114.7064 | 122.731 | 2.3483 | 122.7539 | 66.8564 | -0.16937 | 122.731 | 2.3483 | 66.8564 | 114.7064 | 122.7539 | -122.9233 | -122.9691
1107.3281 | 123.1155 | -59.903 | 62.8738 | -0.049896 | 0.024565 | 0.017438 | 0.011933 | 0.056907 | -0.00021569 | 0.080359 | -57.5272 | 62.7686 | -60.054 | -60.0723 | 54.8126 | 6.9168 | -15.2252 | -14.8132 | 62.8418 | -60.0769 | -0.15106 | -0.10529 | 2.3758 | -0.16937 | -8.0612 | -0.17395 | -0.032043 | 2.5269 | 44.6777 | 45.0897 | 114.7156 | 122.6715 | 2.3758 | 122.7448 | 66.8198 | -0.17395 | 122.6715 | 2.3758 | 66.8198 | 114.7156 | 122.7448 | -122.9279 | -122.9507
1108.3438 | 122.9736 | -59.935 | 62.9379 | -0.1796 | 0.024565 | 0.016584 | 0.017274 | 0.05883 | -0.0021383 | 0.080145 | -57.5684 | 62.8601 | -60.0632 | -60.1364 | 54.7211 | 6.7154 | -14.8544 | -14.7995 | 62.9471 | -60.0952 | -0.12817 | -0.07782 | 2.3666 | -0.20142 | -8.2169 | -0.16022 | 0.009156 | 2.4948 | 45.0806 | 45.1355 | 114.6561 | 122.7951 | 2.3666 | 122.8821 | 66.6504 | -0.16022 | 122.7951 | 2.3666 | 66.6504 | 114.6561 | 122.8821 | -123.0011 | -123.0331
1109.3281 | 123.0972 | -59.9121 | 62.9013 | 0.049286 | 0.022642 | 0.017865 | 0.013215 | 0.057334 | -0.0017111 | 0.082068 | -57.5775 | 62.7914 | -60.0632 | -60.1135 | 54.7852 | 6.9168 | -15.2252 | -14.8132 | 62.8326 | -60.0815 | -0.15106 | -0.10986 | 2.3346 | -0.20142 | -8.1161 | -0.16937 | -0.068664 | 2.4857 | 44.6869 | 45.0989 | 114.6973 | 122.7036 | 2.3346 | 122.7448 | 66.8289 | -0.16937 | 122.7036 | 2.3346 | 66.8289 | 114.6973 | 122.7448 | -122.9645 | -122.9828
1110.3281 | 123.0835 | -59.935 | 62.8784 | 0.62912 | 0.02371 | 0.018079 | 0.014069 | 0.057121 | -0.0036337 | 0.080572 | -57.5729 | 62.764 | -60.0677 | -60.1227 | 54.7577 | 6.9717 | -15.1886 | -14.9185 | 62.8372 | -60.1089 | -0.13275 | -0.11444 | 2.3621 | -0.18768 | -8.1207 | -0.17395 | -0.041199 | 2.4948 | 44.7464 | 45.0165 | 114.6927 | 122.699 | 2.3621 | 122.7722 | 66.9067 | -0.17395 | 122.699 | 2.3621 | 66.9067 | 114.6927 | 122.7722 | -122.9462 | -122.9874
1111.3281 | 123.0698 | -59.9121 | 62.9013 | 0.19424 | 0.025205 | 0.016584 | 0.015351 | 0.05883 | 0.0010659 | 0.082068 | -57.55 | 62.7731 | -60.0677 | -60.0906 | 54.7852 | 6.8436 | -15.2618 | -14.8956 | 62.796 | -60.1089 | -0.15564 | -0.12817 | 2.3621 | -0.17853 | -8.1161 | -0.19684 | -0.10528 | 2.5177 | 44.6503 | 45.0165 | 114.6973 | 122.6852 | 2.3621 | 122.7081 | 66.7557 | -0.19684 | 122.6852 | 2.3621 | 66.7557 | 114.6973 | 122.7081 | -122.9691 | -123.0103
1112.3281 | 123.0881 | -59.8892 | 62.8876 | 0.19424 | 0.026701 | 0.020215 | 0.016846 | 0.059684 | -0.0019247 | 0.082281 | -57.5409 | 62.7686 | -60.054 | -60.0769 | 54.808 | 6.9168 | -15.3809 | -15.0009 | 62.7869 | -60.1044 | -0.16479 | -0.11902 | 2.3483 | -0.18768 | -8.0795 | -0.21515 | -0.10071 | 2.5131 | 44.5084 | 44.8883 | 114.6973 | 122.6578 | 2.3483 | 122.6761 | 66.806 | -0.21515 | 122.6578 | 2.3483 | 66.806 | 114.6973 | 122.6761 | -122.9416 | -122.9919
1113.3438 | 122.9965 | -59.9258 | 62.9471 | -0.67551 | 0.025846 | 0.018079 | 0.015992 | 0.058402 | -0.0014975 | 0.082068 | -57.6233 | 62.8922 | -60.0677 | -60.1227 | 54.7531 | 6.7383 | -15.0833 | -15.0146 | 62.9013 | -60.1273 | -0.14191 | -0.054932 | 2.3026 | -0.19684 | -8.194 | -0.20142 | -0.045777 | 2.4445 | 44.8425 | 44.9112 | 114.679 | 122.818 | 2.3026 | 122.8271 | 66.6641 | -0.20142 | 122.818 | 2.3026 | 66.6641 | 114.679 | 122.8271 | -123.0148 | -123.0743
1114.3281 | 123.056 | -59.9075 | 62.8922 | 0.18662 | 0.023069 | 0.017652 | 0.011079 | 0.059898 | 0.00063871 | 0.082281 | -57.5775 | 62.7914 | -60.0494 | -60.1181 | 54.8035 | 6.8619 | -15.3534 | -15.0009 | 62.8555 | -60.0861 | -0.14191 | -0.10071 | 2.33 | -0.21057 | -8.0887 | -0.17853 | -0.036621 | 2.4719 | 44.5541 | 44.9066 | 114.711 | 122.699 | 2.33 | 122.7631 | 66.7694 | -0.17853 | 122.699 | 2.33 | 66.7694 | 114.711 | 122.7631 | -122.9416 | -122.9782
1115.3281 | 123.0743 | -59.903 | 62.8693 | 0.16373 | 0.025633 | 0.01872 | 0.014924 | 0.059471 | -0.00085669 | 0.082281 | -57.5638 | 62.7869 | -60.0403 | -60.1089 | 54.7897 | 6.72 | -15.4221 | -15.0192 | 62.8098 | -60.1181 | -0.13733 | -0.082398 | 2.3392 | -0.20599 | -8.0795 | -0.21515 | -0.05951 | 2.4765 | 44.4809 | 44.8837 | 114.6927 | 122.6898 | 2.3392 | 122.7127 | 66.6229 | -0.21515 | 122.6898 | 2.3392 | 66.6229 | 114.6927 | 122.7127 | -122.9095 | -122.9874
1116.3281 | 123.0972 | -59.8892 | 62.8647 | 0.1561 | 0.025205 | 0.017865 | 0.015565 | 0.059471 | -0.00042929 | 0.081854 | -57.5409 | 62.8098 | -60.054 | -60.0906 | 54.8309 | 6.7291 | -15.4312 | -15.0146 | 62.7914 | -60.0861 | -0.16479 | -0.054932 | 2.3483 | -0.20142 | -8.0338 | -0.19684 | -0.073242 | 2.5131 | 44.458 | 44.8746 | 114.7202 | 122.699 | 2.3483 | 122.6807 | 66.6183 | -0.19684 | 122.699 | 2.3483 | 66.6183 | 114.7202 | 122.6807 | -122.9187 | -122.9507
1117.3281 | 123.0835 | -59.8984 | 62.883 | 0.19424 | 0.026487 | 0.021283 | 0.015137 | 0.059043 | -2.092e-06 | 0.08164 | -57.5317 | 62.8189 | -60.0494 | -60.0586 | 54.8492 | 6.6925 | -15.4221 | -14.9506 | 62.8052 | -60.1135 | -0.15106 | -0.064087 | 2.3666 | -0.16022 | -8.0338 | -0.21515 | -0.07782 | 2.5177 | 44.4763 | 44.9478 | 114.7476 | 122.7173 | 2.3666 | 122.7036 | 66.5909 | -0.21515 | 122.7173 | 2.3666 | 66.5909 | 114.7476 | 122.7036 | -122.9324 | -122.9965
1118.3438 | 123.0927 | -59.848 | 62.9379 | -0.11856 | 0.024778 | 0.012525 | 0.014924 | 0.059257 | -0.0023519 | 0.082922 | -57.5317 | 62.8326 | -60.022 | -60.0082 | 54.9271 | 6.7612 | -15.4221 | -14.9734 | 62.8372 | -60.0723 | -0.17395 | -0.10529 | 2.3163 | -0.16022 | -8.0109 | -0.22431 | -0.10071 | 2.4902 | 44.426 | 44.8746 | 114.7751 | 122.6807 | 2.3163 | 122.6852 | 66.6092 | -0.22431 | 122.6807 | 2.3163 | 66.6092 | 114.7751 | 122.6852 | -122.9599 | -123.0103
1119.3281 | 123.0286 | -59.9258 | 62.9059 | 0.21713 | 0.027128 | 0.017438 | 0.01941 | 0.060539 | -0.0027793 | 0.081427 | -57.6096 | 62.8922 | -60.0632 | -60.1181 | 54.776 | 6.6696 | -15.4358 | -15.1337 | 62.851 | -60.1044 | -0.13733 | -0.013733 | 2.3163 | -0.19226 | -8.1299 | -0.17853 | -0.054932 | 2.4536 | 44.4901 | 44.7922 | 114.7018 | 122.818 | 2.3163 | 122.7768 | 66.5955 | -0.17853 | 122.818 | 2.3163 | 66.5955 | 114.7018 | 122.7768 | -122.9691 | -123.0103
1120.3281 | 123.0835 | -59.8984 | 62.883 | 0.24765 | 0.02841 | 0.017011 | 0.018128 | 0.060325 | 0.00085231 | 0.081854 | -57.5867 | 62.883 | -60.054 | -60.0769 | 54.8492 | 6.7612 | -15.5457 | -15.097 | 62.8189 | -60.1227 | -0.15564 | 0 | 2.3117 | -0.17853 | -8.0338 | -0.22431 | -0.064087 | 2.4673 | 44.3527 | 44.8013 | 114.7476 | 122.7814 | 2.3117 | 122.7173 | 66.6595 | -0.22431 | 122.7814 | 2.3117 | 66.6595 | 114.7476 | 122.7173 | -122.937 | -123.0057
1121.3281 | 123.1247 | -59.8801 | 62.8922 | 0.25528 | 0.025846 | 0.018293 | 0.018555 | 0.06182 | -0.0025657 | 0.08164 | -57.55 | 62.8967 | -60.0449 | -60.0082 | 54.8126 | 6.7383 | -15.509 | -15.1291 | 62.8052 | -60.0906 | -0.16479 | 0.004578 | 2.33 | -0.12817 | -8.0795 | -0.21057 | -0.086975 | 2.4948 | 44.371 | 44.751 | 114.6927 | 122.7768 | 2.33 | 122.6852 | 66.6183 | -0.21057 | 122.7768 | 2.33 | 66.6183 | 114.6927 | 122.6852 | -122.937 | -122.9828
1122.3594 | 123.1247 | -59.8618 | 62.9333 | -0.1033 | 0.025205 | 0.015729 | 0.011506 | 0.057548 | 0.0017069 | 0.082281 | -57.5546 | 62.851 | -60.0403 | -60.0403 | 54.9179 | 6.665 | -15.6692 | -15.1291 | 62.8326 | -60.0677 | -0.17853 | -0.082398 | 2.3071 | -0.17853 | -8.0154 | -0.20599 | -0.10071 | 2.4857 | 44.1925 | 44.7327 | 114.7797 | 122.7127 | 2.3071 | 122.6944 | 66.5268 | -0.20599 | 122.7127 | 2.3071 | 66.5268 | 114.7797 | 122.6944 | -122.9736 | -123.0011
1123.3438 | 123.1338 | -59.8434 | 62.9471 | -0.19485 | 0.02606 | 0.018506 | 0.0095832 | 0.059257 | -0.00042929 | 0.08164 | -57.5043 | 62.8693 | -59.9945 | -60.0037 | 54.9316 | 6.7474 | -15.6143 | -15.0558 | 62.8647 | -60.0677 | -0.15106 | -0.07782 | 2.3392 | -0.16022 | -8.0154 | -0.2243 | -0.082398 | 2.4902 | 44.2291 | 44.7876 | 114.7751 | 122.7127 | 2.3392 | 122.7081 | 66.5909 | -0.2243 | 122.7127 | 2.3392 | 66.5909 | 114.7751 | 122.7081 | -122.9416 | -123.0148
1124.3438 | 123.1201 | -59.8297 | 62.9288 | 0.064545 | 0.023496 | 0.013379 | 0.013428 | 0.057975 | -0.00021569 | 0.081854 | -57.5455 | 62.8189 | -60.0311 | -60.0174 | 54.9362 | 6.6513 | -15.6876 | -15.0925 | 62.8555 | -60.0311 | -0.20142 | -0.10986 | 2.2842 | -0.18768 | -7.9926 | -0.20142 | -0.073242 | 2.4857 | 44.1422 | 44.7372 | 114.7659 | 122.6486 | 2.2842 | 122.6852 | 66.481 | -0.20142 | 122.6486 | 2.2842 | 66.481 | 114.7659 | 122.6852 | -122.9599 | -122.9599
1125.4375 | 122.9874 | -59.9213 | 62.9425 | 2.2466 | 0.025846 | 0.018293 | 0.019837 | 0.06118 | -2.092e-06 | 0.082708 | -57.312 | 62.9333 | -60.0357 | -60.1227 | 54.7119 | 6.4819 | -15.6372 | -15.4358 | 62.883 | -60.1273 | -0.11444 | -0.009155 | 2.6093 | -0.20142 | -8.2306 | -0.20599 | -0.059509 | 2.7237 | 44.2841 | 44.4855 | 114.6332 | 122.8546 | 2.6093 | 122.8043 | 66.4032 | -0.20599 | 122.8546 | 2.6093 | 66.4032 | 114.6332 | 122.8043 | -122.9782 | -123.0698
1126.6094 | 123.0286 | -59.8892 | 62.9608 | -0.18723 | 0.025419 | 0.012952 | 0.01236 | 0.059043 | -0.0021383 | 0.082068 | -57.4997 | 62.9379 | -59.9991 | -60.054 | 54.8721 | 6.5048 | -15.7379 | -15.3122 | 62.9013 | -60.0815 | -0.10986 | -0.022888 | 2.3895 | -0.16479 | -8.0887 | -0.19226 | -0.059509 | 2.4994 | 44.1513 | 44.577 | 114.7614 | 122.8271 | 2.3895 | 122.7905 | 66.394 | -0.19226 | 122.8271 | 2.3895 | 66.394 | 114.7614 | 122.7905 | -122.9599 | -123.0423
1127.375 | 123.1522 | -59.8709 | 62.9059 | -0.47714 | 0.026487 | 0.016797 | 0.013856 | 0.06182 | -0.0010703 | 0.082708 | -57.5409 | 62.8418 | -60.0311 | -60.0311 | 54.895 | 6.6101 | -15.8707 | -15.2939 | 62.8464 | -60.0815 | -0.16022 | -0.064087 | 2.33 | -0.16022 | -8.0109 | -0.21057 | -0.059509 | 2.4902 | 44.0002 | 44.577 | 114.7659 | 122.7127 | 2.33 | 122.7173 | 66.481 | -0.21057 | 122.7127 | 2.33 | 66.481 | 114.7659 | 122.7173 | -122.937 | -122.9874
1128.4688 | 122.937 | -59.9304 | 62.8693 | 0.11795 | 0.026487 | 0.020856 | 0.017701 | 0.063102 | -0.0012839 | 0.082495 | -57.6096 | 62.9333 | -60.0403 | -60.1593 | 54.7806 | 6.4682 | -15.6143 | -15.3671 | 62.8922 | -60.1135 | -0.10986 | 0.064087 | 2.3209 | -0.22888 | -8.0887 | -0.18311 | 0.022888 | 2.4307 | 44.3161 | 44.5633 | 114.711 | 122.8638 | 2.3209 | 122.8226 | 66.3986 | -0.18311 | 122.8638 | 2.3209 | 66.3986 | 114.711 | 122.8226 | -122.9095 | -122.9828
1129.8281 | 122.9782 | -59.8984 | 62.97 | -0.1796 | 0.025419 | 0.018506 | 0.011079 | 0.057121 | 0.00063871 | 0.084845 | -57.6141 | 62.9242 | -60.0128 | -60.2829 | 54.7989 | 6.4911 | -15.715 | -15.3305 | 62.9242 | -60.0723 | -0.11444 | -0.045777 | 2.2842 | -0.38452 | -8.1711 | -0.17395 | -0.045777 | 2.3987 | 44.1833 | 44.5679 | 114.6973 | 122.8226 | 2.2842 | 122.8226 | 66.3895 | -0.17395 | 122.8226 | 2.2842 | 66.3895 | 114.6973 | 122.8226 | -122.9828 | -123.0423
1130.3438 | 123.1201 | -59.8618 | 62.9105 | 0.30106 | 0.025846 | 0.017652 | 0.011079 | 0.06118 | -0.0010703 | 0.08399 | -57.4997 | 62.8464 | -60.022 | -60.0403 | 54.9042 | 6.4865 | -15.9302 | -15.3122 | 62.8418 | -60.0449 | -0.16022 | -0.064086 | 2.3621 | -0.17853 | -8.0063 | -0.18311 | -0.068664 | 2.5223 | 43.9316 | 44.5496 | 114.7659 | 122.7081 | 2.3621 | 122.7036 | 66.3483 | -0.18311 | 122.7081 | 2.3621 | 66.3483 | 114.7659 | 122.7036 | -122.9324 | -122.9553
1131.3281 | 122.9507 | -59.9121 | 62.9791 | 0.095062 | 0.027983 | 0.02107 | 0.017274 | 0.060325 | 0.00063871 | 0.082281 | -57.6187 | 62.9562 | -60.0311 | -60.1776 | 54.7852 | 6.2851 | -16.0767 | -15.0513 | 62.8555 | -60.1318 | -0.11902 | -0.022888 | 2.2934 | -0.2655 | -8.194 | -0.21973 | -0.1236 | 2.4124 | 43.8354 | 44.8608 | 114.6973 | 122.8683 | 2.2934 | 122.7676 | 66.1972 | -0.21973 | 122.8683 | 2.2934 | 66.1972 | 114.6973 | 122.7676 | -123.0103 | -123.111
1132.3281 | 122.9919 | -59.9258 | 62.9517 | 0.11032 | 0.028196 | 0.02107 | 0.017701 | 0.063102 | -0.0012839 | 0.081854 | -57.5821 | 62.9654 | -60.022 | -60.1456 | 54.7852 | 6.2668 | -15.7242 | -15.4404 | 62.9196 | -60.1318 | -0.096131 | 0.013733 | 2.3438 | -0.21973 | -8.1665 | -0.20599 | -0.032043 | 2.4399 | 44.2017 | 44.4855 | 114.711 | 122.8912 | 2.3438 | 122.8455 | 66.1926 | -0.20599 | 122.8912 | 2.3438 | 66.1926 | 114.711 | 122.8455 | -122.9736 | -123.0835
1133.4531 | 123.0743 | -59.8526 | 62.9196 | 0.22476 | 0.023496 | 0.013806 | 0.0095832 | 0.062034 | 0.00021151 | 0.082068 | -57.5821 | 62.8647 | -60.0357 | -60.0769 | 54.8904 | 6.4133 | -15.889 | -15.3809 | 62.883 | -60.054 | -0.18311 | -0.054932 | 2.2705 | -0.2243 | -8.0292 | -0.20142 | -0.036621 | 2.4536 | 43.9636 | 44.4717 | 114.743 | 122.7173 | 2.2705 | 122.7356 | 66.2659 | -0.20142 | 122.7173 | 2.2705 | 66.2659 | 114.743 | 122.7356 | -122.9553 | -122.9736
1134.7188 | 122.9691 | -59.8801 | 63.0066 | -0.20248 | 0.024778 | 0.018079 | 0.013001 | 0.060325 | -0.00021569 | 0.082495 | -57.6141 | 62.9013 | -60.0128 | -60.0403 | 55.1788 | 6.459 | -16.0126 | -15.4404 | 62.9517 | -60.0632 | -0.13275 | -0.10529 | 2.2659 | -0.16022 | -7.8278 | -0.1831 | -0.054932 | 2.3987 | 43.8675 | 44.4397 | 115.0589 | 122.7814 | 2.2659 | 122.8317 | 66.3391 | -0.1831 | 122.7814 | 2.2659 | 66.3391 | 115.0589 | 122.8317 | -123.0194 | -123.0698
1135.3594 | 123.0148 | -59.8572 | 63.0066 | -0.17197 | 0.02606 | 0.014875 | 0.015565 | 0.060752 | -0.0017111 | 0.080359 | -57.605 | 62.9242 | -60.0082 | -60.0723 | 54.8767 | 6.3858 | -15.7471 | -15.4083 | 62.9059 | -60.0677 | -0.15106 | -0.082398 | 2.2522 | -0.21515 | -8.1299 | -0.21057 | -0.10071 | 2.4033 | 44.1101 | 44.4489 | 114.7339 | 122.7814 | 2.2522 | 122.7631 | 66.243 | -0.21057 | 122.7814 | 2.2522 | 66.243 | 114.7339 | 122.7631 | -123.0148 | -123.0743
1136.3438 | 123.0331 | -59.8297 | 62.9745 | 1.9795 | 0.024565 | 0.017652 | 0.017914 | 0.061607 | -0.0027793 | 0.080786 | -57.3807 | 62.9288 | -60.0037 | -60.0403 | 54.9179 | 6.3812 | -15.8615 | -15.4633 | 62.9379 | -60.0677 | -0.17395 | -0.045776 | 2.449 | -0.21057 | -8.0566 | -0.23804 | -0.036621 | 2.623 | 43.9682 | 44.3665 | 114.7476 | 122.7585 | 2.449 | 122.7676 | 66.2109 | -0.23804 | 122.7585 | 2.449 | 66.2109 | 114.7476 | 122.7676 | -122.9782 | -123.0423
1137.3594 | 123.1155 | -59.8206 | 62.9471 | -0.042267 | 0.023069 | 0.019788 | 0.0059516 | 0.059471 | -0.00064309 | 0.082281 | -57.55 | 62.9333 | -59.9716 | -60.0494 | 54.9545 | 6.3675 | -16.1087 | -15.4633 | 62.8738 | -60.0449 | -0.15106 | -0.013733 | 2.2705 | -0.22888 | -7.9926 | -0.2243 | -0.073243 | 2.4216 | 43.7119 | 44.3573 | 114.7751 | 122.7539 | 2.2705 | 122.6944 | 66.1881 | -0.2243 | 122.7539 | 2.2705 | 66.1881 | 114.7751 | 122.6944 | -122.9187 | -122.9919
1138.3438 | 123.0377 | -59.8663 | 62.9608 | 0.018768 | 0.028196 | 0.018079 | 0.018555 | 0.059257 | -0.0012839 | 0.084204 | -57.5134 | 62.9791 | -59.9854 | -60.054 | 54.9088 | 6.2942 | -15.9302 | -15.4678 | 62.9013 | -60.0861 | -0.11902 | 0.018311 | 2.3529 | -0.18768 | -8.0521 | -0.21973 | -0.059509 | 2.4719 | 43.9362 | 44.3985 | 114.7751 | 122.8455 | 2.3529 | 122.7676 | 66.1606 | -0.21973 | 122.8455 | 2.3529 | 66.1606 | 114.7751 | 122.7676 | -122.9462 | -123.0469
1139.3438 | 123.1247 | -59.8434 | 62.9654 | -0.019379 | 0.022856 | 0.013806 | 0.008515 | 0.059471 | 0.00042511 | 0.082495 | -57.605 | 62.8738 | -59.9899 | -60.022 | 54.9637 | 6.3309 | -16.0355 | -15.3625 | 62.9013 | -60.0037 | -0.14648 | -0.091553 | 2.2385 | -0.17853 | -8.0017 | -0.16022 | -0.064087 | 2.3849 | 43.808 | 44.4809 | 114.8071 | 122.7173 | 2.2385 | 122.7448 | 66.1743 | -0.16022 | 122.7173 | 2.2385 | 66.1743 | 114.8071 | 122.7448 | -122.9553 | -122.9691
1140.3594 | 123.1201 | -59.8389 | 62.9196 | 0.3392 | 0.027555 | 0.013379 | 0.014496 | 0.060966 | -0.00042929 | 0.082281 | -57.5363 | 62.9059 | -59.9716 | -60.0357 | 54.9408 | 6.2851 | -16.1545 | -15.4495 | 62.8372 | -60.0723 | -0.13275 | -0.013733 | 2.3026 | -0.19684 | -7.9788 | -0.23346 | -0.082398 | 2.4353 | 43.6844 | 44.3893 | 114.7797 | 122.7448 | 2.3026 | 122.6761 | 66.124 | -0.23346 | 122.7448 | 2.3026 | 66.124 | 114.7797 | 122.6761 | -122.8912 | -122.9919
1141.375 | 123.0972 | -59.8389 | 62.9242 | 0.056915 | 0.025419 | 0.018293 | 0.010651 | 0.057548 | -0.0034201 | 0.081427 | -57.6004 | 62.851 | -59.9945 | -60.0723 | 54.9225 | 6.1844 | -15.9576 | -15.7013 | 62.9379 | -60.0082 | -0.15564 | -0.073242 | 2.2385 | -0.23346 | -8.0017 | -0.16937 | 0.013733 | 2.3941 | 43.8812 | 44.1376 | 114.7614 | 122.6898 | 2.2385 | 122.7768 | 66.0233 | -0.16937 | 122.6898 | 2.2385 | 66.0233 | 114.7614 | 122.7768 | -122.9187 | -122.9324
1142.3438 | 123.056 | -59.8526 | 62.97 | 0.11795 | 0.023924 | 0.014875 | 0.012787 | 0.059043 | -0.0044883 | 0.081854 | -57.5592 | 62.851 | -60.0037 | -59.9808 | 54.689 | 6.134 | -16.0904 | -15.6876 | 62.8922 | -60.0128 | -0.15106 | -0.11902 | 2.2934 | -0.12817 | -8.2809 | -0.16022 | -0.07782 | 2.4445 | 43.7622 | 44.165 | 114.5416 | 122.7036 | 2.2934 | 122.7448 | 65.9866 | -0.16022 | 122.7036 | 2.2934 | 65.9866 | 114.5416 | 122.7448 | -122.9736 | -122.9828
1143.3281 | 123.024 | -59.8343 | 62.9929 | -0.027008 | 0.027769 | 0.020002 | 0.020692 | 0.06118 | -0.0017111 | 0.08164 | -57.5409 | 63.002 | -59.9854 | -60.0311 | 54.8996 | 6.0516 | -15.9988 | -15.6464 | 62.9288 | -60.0906 | -0.15106 | 0.009155 | 2.2934 | -0.19684 | -8.0933 | -0.25635 | -0.064087 | 2.4445 | 43.8355 | 44.1879 | 114.7339 | 122.8363 | 2.2934 | 122.7631 | 65.8859 | -0.25635 | 122.8363 | 2.2934 | 65.8859 | 114.7339 | 122.7631 | -122.9782 | -123.0835
1144.3906 | 123.1201 | -59.8389 | 62.9654 | -0.034637 | 0.024992 | 0.019361 | 0.0083014 | 0.060111 | -0.00021569 | 0.081427 | -57.5546 | 62.8876 | -59.9854 | -60.0266 | 55.0049 | 6.2393 | -16.0172 | -15.477 | 62.9059 | -60.022 | -0.14648 | -0.07782 | 2.2842 | -0.18768 | -7.9605 | -0.18311 | -0.059509 | 2.4307 | 43.8217 | 44.3619 | 114.8438 | 122.7264 | 2.2842 | 122.7448 | 66.0782 | -0.18311 | 122.7264 | 2.2842 | 66.0782 | 114.8438 | 122.7448 | -122.9507 | -122.9874
1148.0938 | 123.0057 | -59.8526 | 63.002 | 0.13321 | 0.025846 | 0.017652 | 0.020051 | 0.058402 | -0.00042929 | 0.080359 | -57.6324 | 63.002 | -60.0174 | -60.141 | 54.9728 | 6.2759 | -16.0675 | -15.6235 | 62.9837 | -60.0906 | -0.16479 | 0 | 2.2202 | -0.28839 | -8.0292 | -0.23804 | -0.01831 | 2.3849 | 43.7851 | 44.2291 | 114.8254 | 122.8546 | 2.2202 | 122.8363 | 66.1285 | -0.23804 | 122.8546 | 2.2202 | 66.1285 | 114.8254 | 122.8363 | -123.0194 | -123.0927
1148.5469 | 123.0927 | -59.8251 | 62.9517 | 0.18662 | 0.024565 | 0.018293 | 0.01471 | 0.061607 | -0.00042929 | 0.081 | -57.5638 | 62.9333 | -59.9716 | -60.0266 | 55.0049 | 6.2759 | -16.1682 | -15.5365 | 62.9059 | -60.0449 | -0.14648 | -0.01831 | 2.2614 | -0.20142 | -7.9468 | -0.21973 | -0.045776 | 2.4078 | 43.6569 | 44.2886 | 114.83 | 122.7585 | 2.2614 | 122.731 | 66.1011 | -0.21973 | 122.7585 | 2.2614 | 66.1011 | 114.83 | 122.731 | -122.9233 | -122.9965
1149.3281 | 123.0148 | -59.8343 | 62.9929 | -0.19485 | 0.027769 | 0.019147 | 0.019623 | 0.062248 | -0.0027793 | 0.081427 | -57.518 | 63.0066 | -60.0128 | -60.0266 | 54.9683 | 6.1844 | -16.1133 | -15.7196 | 62.9562 | -60.0769 | -0.17853 | 0.013733 | 2.3163 | -0.19226 | -8.0246 | -0.24261 | -0.036621 | 2.4948 | 43.721 | 44.1147 | 114.8026 | 122.8409 | 2.3163 | 122.7905 | 66.0187 | -0.24261 | 122.8409 | 2.3163 | 66.0187 | 114.8026 | 122.7905 | -123.0057 | -123.0698
1150.3281 | 123.0469 | -59.8343 | 62.9929 | -0.58395 | 0.025846 | 0.020642 | 0.019196 | 0.062034 | -0.0014975 | 0.082281 | -57.5226 | 63.0295 | -59.9762 | -59.9945 | 55.014 | 6.0928 | -16.1407 | -15.7745 | 62.9608 | -60.0311 | -0.14191 | 0.036621 | 2.3117 | -0.16022 | -7.9788 | -0.19684 | -0.032044 | 2.4536 | 43.6935 | 44.0598 | 114.8483 | 122.8638 | 2.3117 | 122.7951 | 65.9271 | -0.19684 | 122.8638 | 2.3117 | 65.9271 | 114.8483 | 122.7951 | -122.9691 | -123.024
1151.375 | 123.0515 | -59.8251 | 62.9837 | 0.88089 | 0.023069 | 0.013593 | 0.009156 | 0.061607 | -2.092e-06 | 0.082708 | -57.5409 | 62.883 | -59.9991 | -60.0632 | 54.9683 | 6.1615 | -16.2552 | -15.7242 | 62.9105 | -60.0082 | -0.17395 | -0.10071 | 2.2842 | -0.23804 | -8.0154 | -0.18311 | -0.073243 | 2.4582 | 43.5699 | 44.101 | 114.7934 | 122.7081 | 2.2842 | 122.7356 | 65.9866 | -0.18311 | 122.7081 | 2.2842 | 65.9866 | 114.7934 | 122.7356 | -122.9828 | -122.9919
1152.3281 | 122.9965 | -59.8389 | 63.0112 | 0.11032 | 0.028623 | 0.021711 | 0.017487 | 0.060111 | -0.0019247 | 0.083136 | -57.6004 | 63.0432 | -59.9854 | -60.1135 | 54.8859 | 5.9463 | -16.2048 | -15.8569 | 62.9562 | -60.1135 | -0.14648 | 0.032044 | 2.2385 | -0.27466 | -8.1253 | -0.27466 | -0.054931 | 2.3849 | 43.634 | 43.9819 | 114.7247 | 122.8821 | 2.2385 | 122.7951 | 65.7852 | -0.27466 | 122.8821 | 2.2385 | 65.7852 | 114.7247 | 122.7951 | -122.9965 | -123.1247
1153.3281 | 123.0331 | -59.816 | 63.0295 | -0.14145 | 0.026487 | 0.019574 | 0.013642 | 0.06182 | -2.092e-06 | 0.082922 | -57.5638 | 63.0432 | -59.9625 | -60.0357 | 54.9728 | 5.9189 | -16.2918 | -15.8844 | 63.002 | -60.0266 | -0.14648 | 0.013733 | 2.2522 | -0.21973 | -8.0566 | -0.21057 | -0.027466 | 2.3987 | 43.5242 | 43.9316 | 114.7888 | 122.8592 | 2.2522 | 122.818 | 65.7349 | -0.21057 | 122.8592 | 2.2522 | 65.7349 | 114.7888 | 122.818 | -122.9919 | -123.056
1154.375 | 123.024 | -59.8434 | 63.0157 | 0.12558 | 0.025419 | 0.020429 | 0.014496 | 0.063743 | 0.0040567 | 0.079718 | -57.6416 | 63.0478 | -59.9945 | -59.9854 | 55.2429 | 5.9647 | -16.2781 | -15.8844 | 63.002 | -60.0586 | -0.15106 | 0.032044 | 2.2018 | -0.14191 | -7.7728 | -0.21515 | -0.013733 | 2.3529 | 43.5654 | 43.959 | 115.0864 | 122.8912 | 2.2018 | 122.8455 | 65.8081 | -0.21515 | 122.8912 | 2.2018 | 65.8081 | 115.0864 | 122.8455 | -123.0103 | -123.0743
1155.3281 | 123.0103 | -59.8068 | 63.0249 | -0.088043 | 0.025205 | 0.018293 | 0.018128 | 0.063743 | 0.00021151 | 0.082281 | -57.5455 | 63.0341 | -59.9487 | -59.9945 | 54.9957 | 6.0196 | -16.6534 | -15.8752 | 62.9517 | -60.0357 | -0.14191 | 0.009156 | 2.2614 | -0.18768 | -8.0292 | -0.22888 | -0.073242 | 2.4033 | 43.1534 | 43.9316 | 114.8026 | 122.8409 | 2.2614 | 122.7585 | 65.8264 | -0.22888 | 122.8409 | 2.2614 | 65.8264 | 114.8026 | 122.7585 | -122.9736 | -123.0606
1156.3281 | 123.056 | -59.8114 | 63.0157 | -0.1033 | 0.027555 | 0.013593 | 0.015351 | 0.063102 | -0.0012839 | 0.081854 | -57.5363 | 63.0341 | -59.9625 | -60.0037 | 55.0003 | 5.9738 | -16.2094 | -15.8432 | 62.9837 | -60.0266 | -0.15106 | 0.018311 | 2.2751 | -0.19226 | -8.0154 | -0.21515 | -0.032043 | 2.4261 | 43.602 | 43.9682 | 114.8117 | 122.8455 | 2.2751 | 122.7951 | 65.7852 | -0.21515 | 122.8455 | 2.2751 | 65.7852 | 114.8117 | 122.7951 | -122.9782 | -123.0423
1157.3281 | 123.0469 | -59.816 | 63.0203 | -0.13382 | 0.025205 | 0.020215 | 0.016205 | 0.061607 | 0.00042511 | 0.080359 | -57.5684 | 63.0478 | -59.9762 | -60.0082 | 54.982 | 6.0013 | -16.2094 | -15.8478 | 62.9929 | -60.0403 | -0.16022 | 0.027466 | 2.2476 | -0.19226 | -8.0383 | -0.2243 | -0.027466 | 2.4078 | 43.6066 | 43.9682 | 114.798 | 122.8638 | 2.2476 | 122.8088 | 65.8173 | -0.2243 | 122.8638 | 2.2476 | 65.8173 | 114.798 | 122.8088 | -122.9965 | -123.0606
1158.3281 | 123.0331 | -59.7931 | 63.0295 | -0.14145 | 0.027769 | 0.016156 | 0.013856 | 0.063529 | -0.00064309 | 0.081854 | -57.55 | 63.0524 | -59.9579 | -60.0082 | 54.982 | 5.8365 | -16.3467 | -16.008 | 62.9883 | -60.0174 | -0.1648 | 0.022888 | 2.243 | -0.21515 | -8.0475 | -0.2243 | -0.041199 | 2.4078 | 43.4463 | 43.7851 | 114.7751 | 122.8455 | 2.243 | 122.7814 | 65.6296 | -0.2243 | 122.8455 | 2.243 | 65.6296 | 114.7751 | 122.7814 | -122.9874 | -123.0469
1159.3281 | 123.0377 | -59.8114 | 63.0249 | -0.1796 | 0.027342 | 0.013806 | 0.013856 | 0.062034 | -0.00085669 | 0.082708 | -57.5821 | 63.0341 | -59.9533 | -60.0266 | 55.0049 | 5.8548 | -16.3422 | -16.0995 | 63.0249 | -59.9854 | -0.14191 | 0.009156 | 2.2293 | -0.21515 | -8.02 | -0.17395 | 0 | 2.3712 | 43.4692 | 43.7119 | 114.8163 | 122.8455 | 2.2293 | 122.8363 | 65.6662 | -0.17395 | 122.8455 | 2.2293 | 65.6662 | 114.8163 | 122.8363 | -122.9782 | -123.0103
1160.3281 | 123.0011 | -59.8068 | 63.0569 | -0.24063 | 0.027128 | 0.015943 | 0.008515 | 0.063102 | -2.092e-06 | 0.081854 | -57.3578 | 63.0844 | -59.9442 | -60.0311 | 54.9774 | 5.8273 | -16.2552 | -15.9943 | 63.0386 | -59.9899 | -0.13733 | 0.027466 | 2.449 | -0.2243 | -8.0795 | -0.1831 | -0.018311 | 2.5864 | 43.5516 | 43.8126 | 114.7842 | 122.8912 | 2.449 | 122.8455 | 65.6342 | -0.1831 | 122.8912 | 2.449 | 65.6342 | 114.7842 | 122.8455 | -123.0011 | -123.0469
1161.3281 | 123.0515 | -59.8389 | 63.0615 | -0.21774 | 0.023496 | 0.011029 | 0.010651 | 0.060966 | 0.00021151 | 0.084204 | -57.6324 | 63.0203 | -59.9396 | -60.0586 | 54.9911 | 5.7129 | -15.8661 | -16.1041 | 63.0798 | -60.0128 | -0.10071 | -0.041198 | 2.2064 | -0.21973 | -8.0704 | -0.17395 | 0.018311 | 2.3071 | 43.9728 | 43.7347 | 114.83 | 122.8592 | 2.2064 | 122.9187 | 65.5518 | -0.17395 | 122.8592 | 2.2064 | 65.5518 | 114.83 | 122.9187 | -123.0011 | -123.0743
1162.3281 | 123.0148 | -59.7977 | 63.0661 | -0.14145 | 0.02606 | 0.017652 | 0.015565 | 0.062889 | -0.0040609 | 0.082281 | -57.5729 | 63.0203 | -59.9487 | -60.0128 | 54.9866 | 5.7587 | -16.2964 | -16.1041 | 63.0569 | -60.0082 | -0.15106 | -0.045776 | 2.2247 | -0.21515 | -8.0795 | -0.21057 | -0.009155 | 2.3758 | 43.5013 | 43.6935 | 114.7842 | 122.818 | 2.2247 | 122.8546 | 65.5563 | -0.21057 | 122.818 | 2.2247 | 65.5563 | 114.7842 | 122.8546 | -123.0148 | -123.0743
1163.3281 | 123.0286 | -59.8114 | 63.0661 | -0.16434 | 0.025846 | 0.014234 | 0.014069 | 0.062034 | -0.0014975 | 0.082708 | -57.5867 | 63.0524 | -59.9487 | -60.0311 | 54.9637 | 5.7495 | -16.1957 | -16.0492 | 63.0386 | -59.9991 | -0.13733 | -0.013733 | 2.2247 | -0.21973 | -8.1024 | -0.18768 | -0.027466 | 2.3621 | 43.6157 | 43.7622 | 114.7751 | 122.8638 | 2.2247 | 122.85 | 65.5609 | -0.18768 | 122.8638 | 2.2247 | 65.5609 | 114.7751 | 122.85 | -123.0148 | -123.0652
1164.3281 | 123.0057 | -59.7656 | 63.0707 | -0.17197 | 0.028196 | 0.014234 | 0.011506 | 0.06182 | 0.00042511 | 0.082495 | -57.5867 | 63.0386 | -59.9442 | -60.054 | 54.9866 | 5.6351 | -16.3925 | -16.1957 | 63.0432 | -59.9854 | -0.17853 | -0.032044 | 2.179 | -0.28839 | -8.0841 | -0.21973 | -0.027466 | 2.3575 | 43.3731 | 43.5699 | 114.7522 | 122.8043 | 2.179 | 122.8088 | 65.4007 | -0.21973 | 122.8043 | 2.179 | 65.4007 | 114.7522 | 122.8088 | -123.0148 | -123.056
1165.3281 | 123.0698 | -59.7748 | 63.0386 | 0.5986 | 0.027555 | 0.018079 | 0.017914 | 0.064384 | -0.0010703 | 0.080572 | -57.4768 | 63.0753 | -59.935 | -59.9716 | 55.0323 | 5.5984 | -16.4795 | -16.04 | 63.0249 | -59.9945 | -0.16022 | 0.036621 | 2.298 | -0.19684 | -8.0063 | -0.21973 | -0.013733 | 2.4582 | 43.2953 | 43.7347 | 114.8071 | 122.85 | 2.298 | 122.7997 | 65.3732 | -0.21973 | 122.85 | 2.298 | 65.3732 | 114.8071 | 122.7997 | -122.9736 | -123.0331
1166.3281 | 122.9828 | -59.7702 | 63.0524 | -0.15671 | 0.025205 | 0.011243 | 0.010865 | 0.06182 | 0.00042511 | 0.080572 | -57.605 | 63.0432 | -59.9533 | -60.0037 | 54.9591 | 5.5298 | -16.3559 | -16.2186 | 63.0615 | -59.9899 | -0.1831 | -0.009155 | 2.1652 | -0.23346 | -8.0933 | -0.21973 | 0.009155 | 2.3483 | 43.4143 | 43.5516 | 114.7293 | 122.8134 | 2.1652 | 122.8317 | 65.3 | -0.21973 | 122.8134 | 2.1652 | 65.3 | 114.7293 | 122.8317 | -123.0057 | -123.0423
1167.3281 | 123.0606 | -59.7473 | 63.0478 | -0.21774 | 0.023924 | 0.012952 | 0.010438 | 0.060752 | -0.0014975 | 0.083349 | -57.5409 | 62.9654 | -59.8938 | -59.9716 | 55.0644 | 5.6168 | -16.5161 | -16.1041 | 63.0249 | -59.9487 | -0.14648 | -0.082398 | 2.2064 | -0.2243 | -7.9834 | -0.20142 | -0.022889 | 2.3529 | 43.2312 | 43.6432 | 114.8117 | 122.7127 | 2.2064 | 122.7722 | 65.3641 | -0.20142 | 122.7127 | 2.2064 | 65.3641 | 114.8117 | 122.7722 | -122.9416 | -122.9965
1168.3594 | 123.0515 | -59.7885 | 63.0249 | 0.22476 | 0.024778 | 0.014875 | 0.01001 | 0.059898 | -0.0032065 | 0.082495 | -57.5775 | 62.9471 | -59.935 | -60.022 | 55.0232 | 5.6259 | -16.4978 | -16.0446 | 62.9791 | -59.9716 | -0.14648 | -0.077819 | 2.211 | -0.23346 | -8.0017 | -0.18311 | -0.045776 | 2.3575 | 43.2907 | 43.7439 | 114.8117 | 122.7356 | 2.211 | 122.7676 | 65.4144 | -0.18311 | 122.7356 | 2.211 | 65.4144 | 114.8117 | 122.7676 | -122.9599 | -122.9965
1169.3281 | 123.0469 | -59.8068 | 63.0478 | -0.21011 | 0.026914 | 0.015515 | 0.014283 | 0.060111 | -0.0012839 | 0.081 | -57.5867 | 63.0249 | -59.9304 | -60.0174 | 55.0003 | 5.5206 | -16.1087 | -16.3055 | 63.0844 | -59.9625 | -0.1236 | -0.022889 | 2.2202 | -0.21057 | -8.0475 | -0.15564 | 0.036621 | 2.3438 | 43.6981 | 43.5013 | 114.8071 | 122.8317 | 2.2202 | 122.8912 | 65.3275 | -0.15564 | 122.8317 | 2.2202 | 65.3275 | 114.8071 | 122.8912 | -122.9782 | -123.0103
1170.3438 | 123.0331 | -59.7565 | 63.0478 | 0.011139 | 0.027769 | 0.017011 | 0.018342 | 0.061393 | -0.0017111 | 0.080145 | -57.5134 | 63.0341 | -59.9121 | -59.9625 | 55.0232 | 5.5069 | -16.4978 | -16.1179 | 63.0341 | -60.0128 | -0.15564 | -0.013733 | 2.243 | -0.20599 | -8.0246 | -0.25635 | -0.013733 | 2.3987 | 43.2587 | 43.6386 | 114.7797 | 122.7905 | 2.243 | 122.7905 | 65.2634 | -0.25635 | 122.7905 | 2.243 | 65.2634 | 114.7797 | 122.7905 | -122.9599 | -123.0606
1171.3281 | 123.0515 | -59.7885 | 63.0569 | -0.1796 | 0.022642 | 0.017652 | 0.01001 | 0.059471 | -0.00064309 | 0.08164 | -57.5684 | 62.9837 | -59.935 | -59.9487 | 55.0644 | 5.5161 | -16.5619 | -16.1407 | 63.0569 | -59.935 | -0.14648 | -0.073242 | 2.2202 | -0.16022 | -7.9926 | -0.14648 | 0 | 2.3666 | 43.2266 | 43.6478 | 114.8529 | 122.7722 | 2.2202 | 122.8455 | 65.3046 | -0.14648 | 122.7722 | 2.2202 | 65.3046 | 114.8529 | 122.8455 | -122.9919 | -122.9919
1172.3281 | 123.0103 | -59.7931 | 63.0753 | -0.16434 | 0.026914 | 0.016156 | 0.014283 | 0.060752 | -2.092e-06 | 0.081 | -57.6096 | 63.0432 | -59.9396 | -60.0128 | 54.9866 | 5.4337 | -16.4246 | -16.1362 | 63.0524 | -59.9716 | -0.14648 | -0.032043 | 2.1835 | -0.21973 | -8.0887 | -0.17853 | -0.022888 | 2.33 | 43.3685 | 43.6569 | 114.7797 | 122.8363 | 2.1835 | 122.8455 | 65.2267 | -0.17853 | 122.8363 | 2.1835 | 65.2267 | 114.7797 | 122.8455 | -123.0148 | -123.0469
1173.3281 | 123.111 | -59.7198 | 63.0661 | -0.14908 | 0.024137 | 0.015515 | 0.0097968 | 0.062675 | -0.0017111 | 0.08164 | -57.5226 | 62.9654 | -59.8709 | -59.9075 | 55.1102 | 5.452 | -16.7587 | -16.2048 | 63.0249 | -59.9167 | -0.15106 | -0.10071 | 2.1973 | -0.18768 | -7.9559 | -0.19684 | -0.041199 | 2.3483 | 42.9611 | 43.515 | 114.83 | 122.6852 | 2.1973 | 122.7448 | 65.1718 | -0.19684 | 122.6852 | 2.1973 | 65.1718 | 114.83 | 122.7448 | -122.937 | -122.9828
1174.3281 | 123.111 | -59.7382 | 63.0569 | -0.042267 | 0.022856 | 0.013379 | 0.009156 | 0.06118 | -0.0021383 | 0.082281 | -57.5272 | 62.9562 | -59.8938 | -59.903 | 55.1422 | 5.5435 | -16.7496 | -16.1087 | 63.0295 | -59.9304 | -0.15564 | -0.10071 | 2.211 | -0.16479 | -7.9147 | -0.19226 | -0.027466 | 2.3666 | 42.9886 | 43.6295 | 114.8804 | 122.6944 | 2.211 | 122.7676 | 65.2817 | -0.19226 | 122.6944 | 2.211 | 65.2817 | 114.8804 | 122.7676 | -122.9507 | -122.9874
1175.3438 | 123.0194 | -59.7748 | 63.0707 | -0.11856 | 0.028837 | 0.017865 | 0.018128 | 0.062248 | -0.0014975 | 0.079504 | -57.4997 | 63.0661 | -59.9075 | -59.9442 | 55.0781 | 5.4565 | -16.5665 | -16.1041 | 63.0478 | -59.9854 | -0.13275 | -0.004578 | 2.2751 | -0.16937 | -7.9926 | -0.21057 | -0.022888 | 2.4078 | 43.2083 | 43.6707 | 114.8529 | 122.8409 | 2.2751 | 122.8226 | 65.2313 | -0.21057 | 122.8409 | 2.2751 | 65.2313 | 114.8529 | 122.8226 | -122.9782 | -123.056
1176.3281 | 123.111 | -59.7061 | 63.0386 | -0.072784 | 0.024137 | 0.016797 | 0.01001 | 0.058616 | -0.0010703 | 0.082708 | -57.4768 | 62.9883 | -59.903 | -59.8984 | 55.1422 | 5.4062 | -16.6946 | -16.1041 | 63.0157 | -59.9258 | -0.19684 | -0.050354 | 2.2293 | -0.19226 | -7.8964 | -0.21973 | -0.022888 | 2.4261 | 43.0115 | 43.602 | 114.8483 | 122.6944 | 2.2293 | 122.7219 | 65.1123 | -0.21973 | 122.6944 | 2.2293 | 65.1123 | 114.8483 | 122.7219 | -122.9416 | -122.9645
1177.3438 | 123.0103 | -59.7885 | 63.0661 | 0.056915 | 0.025846 | 0.020215 | 0.020264 | 0.060752 | -2.092e-06 | 0.081854 | -57.5363 | 63.0661 | -59.8938 | -59.9991 | 55.0323 | 5.3741 | -16.5985 | -16.2964 | 63.0478 | -59.9762 | -0.10529 | 0 | 2.2522 | -0.21057 | -8.0338 | -0.18768 | -0.01831 | 2.3575 | 43.19 | 43.4921 | 114.8209 | 122.8546 | 2.2522 | 122.8363 | 65.1627 | -0.18768 | 122.8546 | 2.2522 | 65.1627 | 114.8209 | 122.8363 | -122.9599 | -123.0423
1178.3281 | 123.3261 | -59.7061 | 63.1073 | -0.1796 | 0.022428 | 0.015302 | 0.0087286 | 0.059471 | -0.00064309 | 0.080786 | -57.5272 | 62.97 | -59.8892 | -59.8984 | 55.1559 | 5.4565 | -16.6351 | -16.0446 | 63.0249 | -59.9213 | -0.1831 | -0.13733 | 2.179 | -0.19226 | -7.9514 | -0.21515 | -0.082398 | 2.3621 | 43.071 | 43.6615 | 114.8621 | 122.6761 | 2.179 | 122.731 | 65.1627 | -0.21515 | 122.6761 | 2.179 | 65.1627 | 114.8621 | 122.731 | -122.9965 | -123.0286
1179.3281 | 123.1201 | -59.7382 | 63.0432 | -0.057526 | 0.024137 | 0.013166 | 0.010438 | 0.058189 | -0.00042929 | 0.082495 | -57.518 | 62.9608 | -59.903 | -59.9304 | 55.1193 | 5.4611 | -16.658 | -16.1179 | 63.0341 | -59.9121 | -0.16479 | -0.082398 | 2.2202 | -0.19226 | -7.9239 | -0.17395 | -0.009155 | 2.3849 | 43.0801 | 43.6203 | 114.8575 | 122.699 | 2.2202 | 122.7722 | 65.1993 | -0.17395 | 122.699 | 2.2202 | 65.1993 | 114.8575 | 122.7722 | -122.9462 | -122.9553
1180.3438 | 123.0103 | -59.7656 | 63.1027 | 0.049286 | 0.027342 | 0.017224 | 0.018555 | 0.060325 | 0.00021151 | 0.081213 | -57.5226 | 63.0707 | -59.8938 | -59.9716 | 55.0186 | 5.2597 | -16.6489 | -16.3101 | 63.0478 | -60.0037 | -0.12817 | -0.032043 | 2.243 | -0.20599 | -8.0841 | -0.23804 | -0.054931 | 2.3712 | 43.1168 | 43.4555 | 114.7842 | 122.8363 | 2.243 | 122.8134 | 65.0253 | -0.23804 | 122.8363 | 2.243 | 65.0253 | 114.7842 | 122.8134 | -122.9965 | -123.1064
1181.3281 | 123.0698 | -59.761 | 63.0432 | 0.53757 | 0.023496 | 0.015302 | 0.009156 | 0.060752 | -0.00064309 | 0.082281 | -57.5775 | 62.9517 | -59.9075 | -59.9854 | 55.0552 | 5.2963 | -16.6534 | -16.2323 | 62.9837 | -59.935 | -0.14649 | -0.091553 | 2.1835 | -0.22431 | -7.988 | -0.17395 | -0.059509 | 2.33 | 43.1076 | 43.5287 | 114.8163 | 122.7127 | 2.1835 | 122.7448 | 65.0574 | -0.17395 | 122.7127 | 2.1835 | 65.0574 | 114.8163 | 122.7448 | -122.9507 | -122.9782
1182.3594 | 123.0148 | -59.7702 | 63.0661 | 0.072174 | 0.028837 | 0.015729 | 0.020051 | 0.062248 | -0.0012839 | 0.081427 | -57.6004 | 63.0753 | -59.903 | -60.0174 | 54.9911 | 5.2826 | -16.5665 | -16.3788 | 63.0478 | -59.9854 | -0.13275 | 0.009155 | 2.1698 | -0.24719 | -8.075 | -0.21515 | -0.01831 | 2.3026 | 43.2037 | 43.3914 | 114.7614 | 122.8455 | 2.1698 | 122.818 | 65.0528 | -0.21515 | 122.8455 | 2.1698 | 65.0528 | 114.7614 | 122.818 | -122.9691 | -123.0515
1183.3438 | 123.0011 | -59.7702 | 63.1302 | -0.20248 | 0.025419 | 0.0086796 | 0.014496 | 0.058616 | -0.00064309 | 0.082495 | -57.4951 | 63.1119 | -59.8846 | -60.022 | 55.0873 | 5.3513 | -16.539 | -16.3605 | 63.0569 | -60.0037 | -0.11444 | -0.018311 | 2.2751 | -0.25177 | -8.0429 | -0.23346 | -0.073242 | 2.3895 | 43.2312 | 43.4097 | 114.8575 | 122.8821 | 2.2751 | 122.8271 | 65.1215 | -0.23346 | 122.8821 | 2.2751 | 65.1215 | 114.8575 | 122.8271 | -123.0148 | -123.1338
1184.3281 | 123.1247 | -59.7244 | 63.0707 | -0.042267 | 0.022642 | 0.015515 | 0.009156 | 0.058189 | 0.00042511 | 0.081213 | -57.5638 | 62.97 | -59.903 | -59.9304 | 55.1285 | 5.3925 | -16.6718 | -16.2643 | 63.0386 | -59.9121 | -0.17853 | -0.10071 | 2.1606 | -0.20599 | -7.9422 | -0.18768 | -0.032044 | 2.3392 | 43.0527 | 43.4601 | 114.8529 | 122.6944 | 2.1606 | 122.7631 | 65.1169 | -0.18768 | 122.6944 | 2.1606 | 65.1169 | 114.8529 | 122.7631 | -122.9736 | -122.9828
1185.3438 | 123.143 | -59.7382 | 63.0661 | -0.11856 | 0.027342 | 0.012311 | 0.016419 | 0.060966 | -2.092e-06 | 0.079718 | -57.5089 | 63.0707 | -59.8709 | -59.9258 | 55.101 | 5.3467 | -16.6855 | -16.4154 | 63.0707 | -59.9716 | -0.13275 | 0.004578 | 2.2293 | -0.18768 | -7.9651 | -0.23346 | 0.004578 | 2.3621 | 43.0527 | 43.3228 | 114.8392 | 122.8088 | 2.2293 | 122.8088 | 65.0848 | -0.23346 | 122.8088 | 2.2293 | 65.0848 | 114.8392 | 122.8088 | -122.937 | -123.0377
1186.3281 | 123.0881 | -59.7382 | 63.0524 | 0.018768 | 0.021147 | 0.018506 | 0.0078742 | 0.05883 | 0.0023477 | 0.082495 | -57.5912 | 62.9883 | -59.9121 | -59.9579 | 55.1193 | 5.3055 | -16.7816 | -16.3651 | 63.0295 | -59.9213 | -0.17395 | -0.064087 | 2.1469 | -0.21973 | -7.933 | -0.18311 | -0.022888 | 2.3209 | 42.9565 | 43.3731 | 114.8575 | 122.7264 | 2.1469 | 122.7676 | 65.0436 | -0.18311 | 122.7264 | 2.1469 | 65.0436 | 114.8575 | 122.7676 | -122.9645 | -122.9736
1187.3281 | 123.0515 | -59.7519 | 63.0524 | 0.20187 | 0.024992 | 0.019147 | 0.0087286 | 0.058616 | -0.00021569 | 0.081854 | -57.5958 | 62.9654 | -59.9167 | -59.9625 | 55.101 | 5.3192 | -16.6809 | -16.3193 | 63.0112 | -59.9167 | -0.1648 | -0.086975 | 2.1561 | -0.21057 | -7.9514 | -0.1648 | -0.041199 | 2.3209 | 43.071 | 43.4326 | 114.8529 | 122.7173 | 2.1561 | 122.7631 | 65.0711 | -0.1648 | 122.7173 | 2.1561 | 65.0711 | 114.8529 | 122.7631 | -122.9691 | -122.9691
1188.3281 | 123.056 | -59.7198 | 63.0707 | 0.14847 | 0.022001 | 0.016156 | 0.013428 | 0.057548 | -0.00085669 | 0.082922 | -57.5775 | 62.9654 | -59.8846 | -59.9533 | 55.1147 | 5.3009 | -16.9144 | -16.4566 | 63.0157 | -59.9258 | -0.16479 | -0.10529 | 2.1423 | -0.23346 | -7.9559 | -0.20599 | -0.054932 | 2.3071 | 42.8055 | 43.2632 | 114.8346 | 122.6852 | 2.1423 | 122.7356 | 65.0208 | -0.20599 | 122.6852 | 2.1423 | 65.0208 | 114.8346 | 122.7356 | -122.9553 | -122.9965
1189.3281 | 123.056 | -59.7107 | 63.089 | 0.17136 | 0.024351 | 0.014234 | 0.013428 | 0.057548 | -0.00042929 | 0.081854 | -57.5317 | 62.97 | -59.8846 | -59.9258 | 55.0964 | 5.2597 | -16.951 | -16.5024 | 63.0066 | -59.903 | -0.17395 | -0.11902 | 2.179 | -0.21515 | -7.9926 | -0.19226 | -0.082397 | 2.3529 | 42.7597 | 43.2083 | 114.8071 | 122.6807 | 2.179 | 122.7173 | 64.9704 | -0.19226 | 122.6807 | 2.179 | 64.9704 | 114.8071 | 122.7173 | -122.9736 | -122.9919
1190.3438 | 123.0011 | -59.761 | 63.0936 | 0.23239 | 0.027128 | 0.020215 | 0.017274 | 0.060539 | 0.00042511 | 0.079931 | -57.5821 | 63.089 | -59.9075 | -60.0037 | 55.0278 | 5.0812 | -16.8823 | -16.6397 | 63.0569 | -59.9625 | -0.14649 | -0.004578 | 2.179 | -0.24262 | -8.0658 | -0.20142 | -0.036621 | 2.3254 | 42.8787 | 43.1213 | 114.7888 | 122.85 | 2.179 | 122.818 | 64.8422 | -0.20142 | 122.85 | 2.179 | 64.8422 | 114.7888 | 122.818 | -123.0011 | -123.056
1191.3281 | 123.0789 | -59.729 | 63.1073 | -0.019379 | 0.024992 | 0.012952 | 0.011079 | 0.059257 | -0.0014975 | 0.080359 | -57.5821 | 63.002 | -59.8846 | -59.9579 | 55.0919 | 5.1224 | -16.9418 | -16.5161 | 63.0112 | -59.9213 | -0.15564 | -0.10529 | 2.1469 | -0.22888 | -8.0154 | -0.19226 | -0.096131 | 2.3026 | 42.7872 | 43.2129 | 114.8209 | 122.731 | 2.1469 | 122.7402 | 64.8514 | -0.19226 | 122.731 | 2.1469 | 64.8514 | 114.8209 | 122.7402 | -122.9919 | -123.0286
1192.3281 | 123.1155 | -59.6878 | 63.1027 | 3.3223 | 0.024351 | 0.020856 | 0.014283 | 0.057762 | -0.0010703 | 0.081213 | -57.399 | 62.9929 | -59.8846 | -59.8526 | 55.1605 | 5.2322 | -16.8915 | -16.3788 | 63.0157 | -59.8526 | -0.19684 | -0.10986 | 2.2888 | -0.1648 | -7.9422 | -0.1648 | -0.086975 | 2.4857 | 42.7963 | 43.309 | 114.8483 | 122.6807 | 2.2888 | 122.7036 | 64.92 | -0.1648 | 122.6807 | 2.2888 | 64.92 | 114.8483 | 122.7036 | -122.9874 | -122.9553
1193.3438 | 123.1338 | -59.7336 | 63.1256 | -0.11093 | 0.027342 | 0.017865 | 0.020051 | 0.061393 | -0.0017111 | 0.081 | -57.5089 | 63.1302 | -59.8526 | -59.8984 | 55.1239 | 5.072 | -16.9647 | -16.658 | 63.0203 | -59.9716 | -0.11902 | 0.004578 | 2.2247 | -0.16479 | -8.0017 | -0.23804 | -0.10529 | 2.3438 | 42.7689 | 43.0756 | 114.8575 | 122.8638 | 2.2247 | 122.7539 | 64.8056 | -0.23804 | 122.8638 | 2.2247 | 64.8056 | 114.8575 | 122.7539 | -122.9782 | -123.0972
1194.3438 | 123.1064 | -59.697 | 63.0615 | -0.11093 | 0.023496 | 0.0099612 | 0.010651 | 0.058189 | 0.00021151 | 0.080145 | -57.5592 | 62.9837 | -59.8618 | -59.8846 | 55.1697 | 5.2322 | -16.9373 | -16.4566 | 63.0478 | -59.9075 | -0.1648 | -0.077819 | 2.1378 | -0.18768 | -7.8918 | -0.21057 | -0.013732 | 2.3026 | 42.7597 | 43.2404 | 114.8666 | 122.6807 | 2.1378 | 122.7448 | 64.9292 | -0.21057 | 122.6807 | 2.1378 | 64.9292 | 114.8666 | 122.7448 | -122.9233 | -122.9691
1195.3438 | 123.1155 | -59.697 | 63.089 | -0.011749 | 0.023283 | 0.015943 | 0.011719 | 0.059257 | -0.0012839 | 0.082922 | -57.5409 | 62.9883 | -59.8755 | -59.8892 | 55.1788 | 5.159 | -16.9327 | -16.5573 | 63.0524 | -59.8618 | -0.17853 | -0.10071 | 2.1561 | -0.19226 | -7.9102 | -0.1648 | -0.036621 | 2.3346 | 42.7643 | 43.1396 | 114.8758 | 122.6852 | 2.1561 | 122.7493 | 64.856 | -0.1648 | 122.6852 | 2.1561 | 64.856 | 114.8758 | 122.7493 | -122.9645 | -122.9507
1196.3438 | 123.111 | -59.7015 | 63.0661 | -0.011749 | 0.022856 | 0.012311 | 0.010438 | 0.057334 | -0.0021383 | 0.082068 | -57.5638 | 62.9974 | -59.8663 | -59.903 | 55.1651 | 5.1407 | -16.951 | -16.5756 | 63.0249 | -59.8801 | -0.16479 | -0.068664 | 2.1378 | -0.20142 | -7.901 | -0.17853 | -0.041199 | 2.3026 | 42.7505 | 43.1259 | 114.8666 | 122.699 | 2.1378 | 122.7264 | 64.8422 | -0.17853 | 122.699 | 2.1378 | 64.8422 | 114.8666 | 122.7264 | -122.9324 | -122.9462
1197.3438 | 123.1018 | -59.6924 | 63.1256 | -0.14908 | 0.022642 | 0.013593 | 0.014924 | 0.057334 | -0.0021383 | 0.082281 | -57.4997 | 63.0066 | -59.8389 | -59.8618 | 55.22 | 5.2139 | -16.8686 | -16.4612 | 63.0478 | -59.8801 | -0.14648 | -0.11902 | 2.1927 | -0.16937 | -7.9056 | -0.18768 | -0.077819 | 2.3392 | 42.8238 | 43.2312 | 114.9124 | 122.699 | 2.1927 | 122.7402 | 64.9063 | -0.18768 | 122.699 | 2.1927 | 64.9063 | 114.9124 | 122.7402 | -122.9645 | -123.0057
1198.3438 | 123.1201 | -59.6558 | 63.1073 | -0.13382 | 0.022856 | 0.014661 | 0.014283 | 0.05883 | -0.0012839 | 0.083777 | -57.4768 | 62.9929 | -59.848 | -59.8389 | 55.2155 | 5.1224 | -17.0563 | -16.5756 | 63.0753 | -59.8389 | -0.19226 | -0.11444 | 2.179 | -0.1831 | -7.8918 | -0.1831 | -0.032044 | 2.3712 | 42.5995 | 43.0801 | 114.8712 | 122.6486 | 2.179 | 122.731 | 64.7781 | -0.1831 | 122.6486 | 2.179 | 64.7781 | 114.8712 | 122.731 | -122.9553 | -122.9462
1199.3438 | 123.0698 | -59.6878 | 63.1393 | -0.16434 | 0.026274 | 0.014875 | 0.013642 | 0.05883 | -0.0036337 | 0.081 | -57.5089 | 63.0203 | -59.8297 | -59.848 | 55.2017 | 5.0812 | -17.0013 | -16.571 | 63.0615 | -59.8526 | -0.14191 | -0.11902 | 2.179 | -0.16022 | -7.9376 | -0.1648 | -0.07782 | 2.3209 | 42.6865 | 43.1168 | 114.8895 | 122.7081 | 2.179 | 122.7493 | 64.769 | -0.1648 | 122.7081 | 2.179 | 64.769 | 114.8895 | 122.7493 | -122.9691 | -122.9919
1200.3438 | 123.111 | -59.7015 | 63.0432 | 0.26291 | 0.025205 | 0.014661 | 0.015992 | 0.060966 | 0.00021151 | 0.079931 | -57.5134 | 63.0341 | -59.8572 | -60.0266 | 55.3299 | 5.1773 | -17.1982 | -16.5848 | 63.0524 | -59.8801 | -0.15564 | -0.009155 | 2.1881 | -0.32501 | -7.7133 | -0.17853 | 0.009155 | 2.3438 | 42.5034 | 43.1168 | 115.0314 | 122.7356 | 2.1881 | 122.7539 | 64.8788 | -0.17853 | 122.7356 | 2.1881 | 64.8788 | 115.0314 | 122.7539 | -122.9004 | -122.9233
1201.3438 | 123.0148 | -59.7015 | 63.1531 | -0.19485 | 0.024137 | 0.019574 | 0.014924 | 0.059043 | 0.0012795 | 0.082495 | -57.5684 | 63.1119 | -59.848 | -59.9167 | 55.0369 | 4.985 | -16.7679 | -16.8869 | 63.1073 | -59.935 | -0.14648 | -0.041199 | 2.1332 | -0.21515 | -8.1161 | -0.23346 | -0.045776 | 2.2797 | 42.9337 | 42.8146 | 114.7385 | 122.8134 | 2.1332 | 122.8088 | 64.6866 | -0.23346 | 122.8134 | 2.1332 | 64.6866 | 114.7385 | 122.8088 | -123.0011 | -123.0881
1202.3438 | 123.1247 | -59.6832 | 63.0707 | -0.042267 | 0.023924 | 0.012952 | 0.011079 | 0.05883 | -0.0025657 | 0.081213 | -57.5134 | 63.0112 | -59.8434 | -59.8526 | 55.2155 | 5.072 | -17.0197 | -16.5527 | 63.0661 | -59.8709 | -0.16022 | -0.05951 | 2.1698 | -0.16937 | -7.8552 | -0.18768 | -0.004578 | 2.33 | 42.6636 | 43.1305 | 114.8987 | 122.6944 | 2.1698 | 122.7493 | 64.7552 | -0.18768 | 122.6944 | 2.1698 | 64.7552 | 114.8987 | 122.7493 | -122.9141 | -122.9416
1203.3438 | 122.9965 | -59.6649 | 63.121 | -0.095673 | 0.022428 | 0.017438 | 0.012574 | 0.059471 | -0.0034201 | 0.081427 | -57.4768 | 63.0066 | -59.8206 | -59.8022 | 55.2475 | 5.1224 | -16.9876 | -16.008 | 63.121 | -59.8297 | -0.15564 | -0.11444 | 2.1881 | -0.13733 | -7.8735 | -0.16479 | 0 | 2.3438 | 42.6773 | 43.6569 | 114.9124 | 122.6715 | 2.1881 | 122.7859 | 64.7873 | -0.16479 | 122.6715 | 2.1881 | 64.7873 | 114.9124 | 122.7859 | -122.9416 | -122.9507
1204.3438 | 123.1155 | -59.6832 | 63.1073 | 1.2318 | 0.026487 | 0.0093204 | 0.013428 | 0.05883 | -0.0017111 | 0.081213 | -57.4219 | 63.0249 | -59.8343 | -59.8068 | 55.2246 | 5.1132 | -17.0013 | -16.5573 | 63.0524 | -59.8526 | -0.15106 | -0.082398 | 2.2614 | -0.1236 | -7.8827 | -0.16937 | -0.054932 | 2.4124 | 42.6819 | 43.1259 | 114.9078 | 122.7081 | 2.2614 | 122.7356 | 64.7964 | -0.16937 | 122.7081 | 2.2614 | 64.7964 | 114.9078 | 122.7356 | -122.9416 | -122.9599
1205.3594 | 123.0286 | -59.7244 | 63.1485 | 0.018768 | 0.025419 | 0.01872 | 0.020905 | 0.063316 | -0.0019247 | 0.081 | -57.486 | 63.1302 | -59.8297 | -59.8755 | 55.1651 | 4.9805 | -16.9876 | -16.6534 | 63.089 | -59.9121 | -0.10529 | -0.018311 | 2.2385 | -0.15106 | -7.9834 | -0.18768 | -0.05951 | 2.3438 | 42.7368 | 43.071 | 114.8895 | 122.8546 | 2.2385 | 122.8134 | 64.7049 | -0.18768 | 122.8546 | 2.2385 | 64.7049 | 114.8895 | 122.8134 | -122.9782 | -123.0606
1206.3594 | 123.0194 | -59.7153 | 63.1668 | -0.15671 | 0.025633 | 0.015302 | 0.017487 | 0.060966 | -0.0023519 | 0.079931 | -57.5409 | 63.1256 | -59.8434 | -59.9121 | 55.1468 | 4.9576 | -16.8457 | -16.6489 | 63.1393 | -59.8846 | -0.12817 | -0.041199 | 2.1744 | -0.19684 | -8.02 | -0.16937 | -0.027466 | 2.3026 | 42.8696 | 43.0664 | 114.8621 | 122.8409 | 2.1744 | 122.8546 | 64.6729 | -0.16937 | 122.8409 | 2.1744 | 64.6729 | 114.8621 | 122.8546 | -123.0103 | -123.0515
1207.3438 | 123.1018 | -59.6603 | 63.1302 | -0.14908 | 0.020506 | 0.012097 | 0.010438 | 0.060325 | -0.0023519 | 0.082495 | -57.5043 | 63.0341 | -59.8206 | -59.8068 | 55.2658 | 5.0354 | -17.0471 | -16.571 | 63.089 | -59.848 | -0.16022 | -0.09613 | 2.1561 | -0.14648 | -7.8644 | -0.18768 | -0.041199 | 2.3163 | 42.6132 | 43.0893 | 114.9261 | 122.6944 | 2.1561 | 122.7493 | 64.6957 | -0.18768 | 122.6944 | 2.1561 | 64.6957 | 114.9261 | 122.7493 | -122.9507 | -122.9782
1208.3438 | 123.0606 | -59.6695 | 63.1485 | -0.17197 | 0.025205 | 0.017652 | 0.013856 | 0.05883 | -0.0017111 | 0.08164 | -57.4905 | 63.0478 | -59.8114 | -59.8389 | 55.2292 | 5.0629 | -16.8915 | -16.539 | 63.0936 | -59.8343 | -0.14191 | -0.10071 | 2.179 | -0.16937 | -7.9193 | -0.1648 | -0.054932 | 2.3209 | 42.778 | 43.1305 | 114.8987 | 122.7173 | 2.179 | 122.7631 | 64.7324 | -0.1648 | 122.7173 | 2.179 | 64.7324 | 114.8987 | 122.7631 | -122.9599 | -122.9828
1209.3438 | 123.056 | -59.6878 | 63.1027 | 0.026398 | 0.022001 | 0.018293 | 0.0097968 | 0.057334 | -0.00064309 | 0.082708 | -57.5684 | 63.0386 | -59.8389 | -59.8755 | 55.1971 | 4.9576 | -17.0471 | -16.6397 | 63.0936 | -59.8389 | -0.15106 | -0.064087 | 2.1194 | -0.18768 | -7.9056 | -0.15106 | -0.009155 | 2.2705 | 42.6407 | 43.0481 | 114.8849 | 122.7264 | 2.1194 | 122.7814 | 64.6454 | -0.15106 | 122.7264 | 2.1194 | 64.6454 | 114.8849 | 122.7814 | -122.9416 | -122.9416
1210.3594 | 123.056 | -59.6512 | 63.176 | -0.17197 | 0.025205 | 0.016584 | 0.012787 | 0.057334 | -0.0025657 | 0.081427 | -57.5089 | 63.0798 | -59.8297 | -59.8572 | 55.2109 | 4.9805 | -16.983 | -16.6809 | 63.0936 | -59.8663 | -0.17853 | -0.09613 | 2.1423 | -0.20599 | -7.9651 | -0.21515 | -0.082397 | 2.3209 | 42.6682 | 42.9703 | 114.8621 | 122.731 | 2.1423 | 122.7448 | 64.6317 | -0.21515 | 122.731 | 2.1423 | 64.6317 | 114.8621 | 122.7448 | -123.0057 | -123.0423
1211.3438 | 123.0698 | -59.6878 | 63.1531 | 0.11032 | 0.024778 | 0.02107 | 0.010224 | 0.058189 | -0.0029929 | 0.083136 | -57.5455 | 63.0432 | -59.8251 | -59.9167 | 55.1697 | 4.8614 | -17.1112 | -16.7221 | 63.0432 | -59.8572 | -0.13733 | -0.10986 | 2.1423 | -0.22888 | -7.9834 | -0.16937 | -0.10986 | 2.2797 | 42.5766 | 42.9657 | 114.8575 | 122.731 | 2.1423 | 122.731 | 64.5493 | -0.16937 | 122.731 | 2.1423 | 64.5493 | 114.8575 | 122.731 | -122.9782 | -123.0103
1212.3438 | 123.111 | -59.6832 | 63.1393 | -0.011749 | 0.023496 | 0.015729 | 0.01236 | 0.057762 | -0.00042929 | 0.081 | -57.5317 | 63.0295 | -59.8206 | -59.8755 | 55.2109 | 4.953 | -17.189 | -16.7404 | 63.0615 | -59.848 | -0.13733 | -0.10986 | 2.1515 | -0.19226 | -7.9285 | -0.16479 | -0.07782 | 2.2888 | 42.4942 | 42.9428 | 114.8941 | 122.7127 | 2.1515 | 122.7448 | 64.6362 | -0.16479 | 122.7127 | 2.1515 | 64.6362 | 114.8941 | 122.7448 | -122.9599 | -122.9874
1213.3438 | 123.1064 | -59.6375 | 63.1256 | -0.027008 | 0.023496 | 0.012525 | 0.01471 | 0.059898 | -0.0010703 | 0.081 | -57.4997 | 63.0295 | -59.816 | -59.8343 | 55.2475 | 4.953 | -17.189 | -16.6443 | 63.0707 | -59.8343 | -0.17853 | -0.09613 | 2.1378 | -0.19684 | -7.8781 | -0.19684 | -0.054931 | 2.3163 | 42.4484 | 42.9932 | 114.8849 | 122.6669 | 2.1378 | 122.7081 | 64.5905 | -0.19684 | 122.6669 | 2.1378 | 64.5905 | 114.8849 | 122.7081 | -122.9416 | -122.9599
1214.3438 | 123.1201 | -59.6375 | 63.1119 | -0.072784 | 0.023496 | 0.012738 | 0.012574 | 0.059257 | -0.0025657 | 0.082708 | -57.5272 | 63.0341 | -59.816 | -59.816 | 55.2704 | 5.0125 | -17.1295 | -16.6214 | 63.0844 | -59.816 | -0.17853 | -0.077819 | 2.1103 | -0.17853 | -7.8415 | -0.17853 | -0.027465 | 2.2888 | 42.5079 | 43.0161 | 114.9078 | 122.6715 | 2.1103 | 122.7219 | 64.65 | -0.17853 | 122.6715 | 2.1103 | 64.65 | 114.9078 | 122.7219 | -122.9279 | -122.9279
1215.3594 | 122.9828 | -59.6649 | 63.1805 | -0.21011 | 0.026914 | 0.0093204 | 0.017914 | 0.058402 | -0.00085669 | 0.081427 | -57.3212 | 63.1714 | -59.8114 | -59.8846 | 55.2063 | 4.8981 | -16.9098 | -16.6992 | 63.1119 | -59.8938 | -0.14648 | -0.009155 | 2.3438 | -0.21973 | -7.9742 | -0.22888 | -0.068665 | 2.4902 | 42.7551 | 42.9657 | 114.8712 | 122.8363 | 2.3438 | 122.7768 | 64.563 | -0.22888 | 122.8363 | 2.3438 | 64.563 | 114.8712 | 122.7768 | -122.9919 | -123.0743
1216.3594 | 123.0972 | -59.6741 | 63.1393 | 0.079804 | 0.025205 | 0.015302 | 0.01236 | 0.058616 | -0.0012839 | 0.082708 | -57.3395 | 63.0661 | -59.7839 | -59.9075 | 55.188 | 4.834 | -17.0151 | -16.6672 | 63.0844 | -59.8389 | -0.10986 | -0.073242 | 2.3346 | -0.23346 | -7.9514 | -0.16479 | -0.054931 | 2.4445 | 42.659 | 43.0069 | 114.8621 | 122.7402 | 2.3346 | 122.7585 | 64.5081 | -0.16479 | 122.7402 | 2.3346 | 64.5081 | 114.8621 | 122.7585 | -122.9233 | -122.9782
1217.3438 | 123.1293 | -59.6375 | 63.1531 | 0.14084 | 0.022428 | 0.013593 | 0.015137 | 0.057762 | -0.0034201 | 0.079931 | -57.4402 | 63.0753 | -59.7885 | -59.7885 | 55.2887 | 4.9393 | -17.1616 | -16.6718 | 63.1027 | -59.8297 | -0.15106 | -0.07782 | 2.1973 | -0.15106 | -7.8644 | -0.19226 | -0.050354 | 2.3483 | 42.4759 | 42.9657 | 114.9261 | 122.7127 | 2.1973 | 122.7402 | 64.5767 | -0.19226 | 122.7127 | 2.1973 | 64.5767 | 114.9261 | 122.7402 | -122.9416 | -122.9828
1218.3438 | 123.0652 | -59.6466 | 63.1256 | -0.072784 | 0.024778 | 0.01637 | 0.014069 | 0.057762 | -0.00021569 | 0.079077 | -57.4677 | 63.0524 | -59.7885 | -59.7794 | 55.3848 | 5.2643 | -17.3218 | -16.9647 | 63.1027 | -59.8297 | -0.14191 | -0.073242 | 2.179 | -0.13275 | -7.7408 | -0.18311 | -0.022888 | 2.3209 | 42.3248 | 42.6819 | 115.0314 | 122.699 | 2.179 | 122.7493 | 64.9109 | -0.18311 | 122.699 | 2.179 | 64.9109 | 115.0314 | 122.7493 | -122.9141 | -122.9553
1219.3594 | 123.1384 | -59.6558 | 63.1119 | 0.21713 | 0.022215 | 0.019361 | 0.017914 | 0.059898 | -0.00085669 | 0.082495 | -57.6736 | 63.002 | -59.8434 | -59.848 | 55.2383 | 4.9026 | -17.1982 | -16.7404 | 63.0569 | -59.848 | -0.18768 | -0.10986 | 1.9821 | -0.19226 | -7.8735 | -0.19226 | -0.054931 | 2.1698 | 42.4576 | 42.9153 | 114.8941 | 122.6578 | 1.9821 | 122.7127 | 64.5584 | -0.19226 | 122.6578 | 1.9821 | 64.5584 | 114.8941 | 122.7127 | -122.9553 | -122.9599
1220.3594 | 122.9919 | -59.6924 | 63.1668 | 0.44601 | 0.028623 | 0.020429 | 0.018128 | 0.061393 | -2.092e-06 | 0.080572 | -57.5272 | 63.1577 | -59.8434 | -59.9304 | 55.1331 | 4.7974 | -16.9922 | -16.9052 | 63.0844 | -59.9167 | -0.15106 | -0.009155 | 2.1652 | -0.23804 | -8.0338 | -0.2243 | -0.082397 | 2.3163 | 42.7002 | 42.7872 | 114.8254 | 122.85 | 2.1652 | 122.7768 | 64.4897 | -0.2243 | 122.85 | 2.1652 | 64.4897 | 114.8254 | 122.7768 | -123.0103 | -123.0835
1221.3438 | 123.056 | -59.6375 | 63.1531 | -0.16434 | 0.025205 | 0.01637 | 0.010224 | 0.059043 | 0.00085231 | 0.08164 | -57.4905 | 63.0844 | -59.816 | -59.8068 | 55.3207 | 4.9484 | -17.0792 | -16.6946 | 63.0844 | -59.8389 | -0.17853 | -0.068664 | 2.1469 | -0.16937 | -7.8323 | -0.20142 | -0.068664 | 2.3254 | 42.5583 | 42.9428 | 114.9582 | 122.7219 | 2.1469 | 122.7219 | 64.5859 | -0.20142 | 122.7219 | 2.1469 | 64.5859 | 114.9582 | 122.7219 | -122.9691 | -122.9919
1222.3438 | 123.0698 | -59.6558 | 63.1714 | -0.1796 | 0.022642 | 0.014875 | 0.013215 | 0.059043 | -0.0036337 | 0.080572 | -57.4997 | 63.1119 | -59.7931 | -59.8297 | 55.2933 | 4.8614 | -17.0105 | -16.658 | 63.121 | -59.816 | -0.13733 | -0.05951 | 2.1561 | -0.17395 | -7.8781 | -0.16022 | -0.050354 | 2.2934 | 42.6453 | 42.9977 | 114.949 | 122.7676 | 2.1561 | 122.7768 | 64.5172 | -0.16022 | 122.7676 | 2.1561 | 64.5172 | 114.949 | 122.7768 | -122.9645 | -122.9874
1223.3438 | 122.9553 | -59.6832 | 63.1485 | 0.064545 | 0.025419 | 0.016797 | 0.020051 | 0.061607 | -0.0014975 | 0.081427 | -57.5775 | 63.1668 | -59.8434 | -59.9167 | 55.1605 | 4.8386 | -16.9418 | -16.7953 | 63.1622 | -59.8846 | -0.16022 | 0.01831 | 2.1057 | -0.23346 | -7.988 | -0.20142 | 0.013732 | 2.2659 | 42.7414 | 42.8879 | 114.8438 | 122.85 | 2.1057 | 122.8455 | 64.5218 | -0.20142 | 122.85 | 2.1057 | 64.5218 | 114.8438 | 122.8455 | -122.9919 | -123.0331
1224.3438 | 123.0194 | -59.7015 | 63.1531 | 0.056915 | 0.026274 | 0.01872 | 0.019623 | 0.060966 | -0.0010703 | 0.083136 | -57.5363 | 63.1805 | -59.8343 | -59.8846 | 55.188 | 4.6921 | -17.1249 | -16.9373 | 63.1348 | -59.9167 | -0.13275 | 0.027466 | 2.1652 | -0.18311 | -7.9651 | -0.21515 | -0.01831 | 2.298 | 42.5766 | 42.7643 | 114.8895 | 122.8821 | 2.1652 | 122.8363 | 64.3936 | -0.21515 | 122.8821 | 2.1652 | 64.3936 | 114.8895 | 122.8363 | -122.9874 | -123.0698
1225.3438 | 123.0469 | -59.6191 | 63.176 | -0.20248 | 0.024351 | 0.020215 | 0.010865 | 0.059898 | -0.0025657 | 0.082281 | -57.4997 | 63.121 | -59.816 | -59.8526 | 55.2658 | 4.866 | -17.0242 | -16.7862 | 63.1302 | -59.816 | -0.19684 | -0.054931 | 2.1194 | -0.23346 | -7.9102 | -0.19684 | -0.045776 | 2.3163 | 42.5949 | 42.8329 | 114.8849 | 122.7402 | 2.1194 | 122.7493 | 64.4852 | -0.19684 | 122.7402 | 2.1194 | 64.4852 | 114.8849 | 122.7493 | -122.9919 | -122.9919
1226.3438 | 122.9965 | -59.6558 | 63.1668 | 0.034027 | 0.027983 | 0.014661 | 0.017274 | 0.061607 | -0.0017111 | 0.081854 | -57.5363 | 63.1851 | -59.8114 | -59.8755 | 55.2017 | 4.715 | -17.0242 | -16.8869 | 63.1485 | -59.8846 | -0.15564 | 0.018311 | 2.1194 | -0.21973 | -7.9651 | -0.22888 | -0.01831 | 2.2751 | 42.6315 | 42.7689 | 114.8575 | 122.8409 | 2.1194 | 122.8043 | 64.3707 | -0.22888 | 122.8409 | 2.1194 | 64.3707 | 114.8575 | 122.8043 | -122.9782 | -123.0515
1227.3438 | 122.9919 | -59.6649 | 63.176 | 0.056915 | 0.024778 | 0.01872 | 0.016633 | 0.062889 | -0.0010703 | 0.082068 | -57.55 | 63.1714 | -59.8434 | -59.9075 | 55.1834 | 4.747 | -16.9373 | -16.9006 | 63.121 | -59.8984 | -0.17853 | -0.004577 | 2.1149 | -0.24262 | -7.9926 | -0.23346 | -0.054931 | 2.2934 | 42.7277 | 42.7643 | 114.8483 | 122.8363 | 2.1149 | 122.7859 | 64.4119 | -0.23346 | 122.8363 | 2.1149 | 64.4119 | 114.8483 | 122.7859 | -123.0194 | -123.0743
1228.3438 | 123.111 | -59.6741 | 63.1027 | 0.072174 | 0.026487 | 0.022565 | 0.016633 | 0.059043 | 0.00021151 | 0.079931 | -57.5958 | 63.176 | -59.848 | -59.9396 | 55.1697 | 4.6646 | -17.0242 | -16.9556 | 63.1165 | -59.8938 | -0.17395 | 0.073242 | 2.0782 | -0.2655 | -7.933 | -0.21973 | 0.013733 | 2.2522 | 42.6498 | 42.7185 | 114.8438 | 122.85 | 2.0782 | 122.7905 | 64.3387 | -0.21973 | 122.85 | 2.0782 | 64.3387 | 114.8438 | 122.7905 | -122.9507 | -122.9965
1229.3438 | 123.0194 | -59.6649 | 63.1805 | 0.041657 | 0.025633 | 0.014234 | 0.016205 | 0.060966 | 0.0017069 | 0.082708 | -57.5226 | 63.2034 | -59.7748 | -59.8618 | 55.2292 | 4.7058 | -17.0929 | -16.9006 | 63.0936 | -59.8984 | -0.10986 | 0.022888 | 2.1423 | -0.19684 | -7.9514 | -0.23346 | -0.086975 | 2.2522 | 42.572 | 42.7643 | 114.8941 | 122.8683 | 2.1423 | 122.7585 | 64.3707 | -0.23346 | 122.8683 | 2.1423 | 64.3707 | 114.8941 | 122.7585 | -122.9553 | -123.0789
1230.3438 | 123.1659 | -59.6603 | 63.1165 | 0.17899 | 0.025633 | 0.019788 | 0.010865 | 0.062461 | 0.0010659 | 0.079931 | -57.5226 | 63.1073 | -59.816 | -59.9716 | 54.9911 | 4.7745 | -16.9739 | -16.8045 | 63.0844 | -59.8434 | -0.15564 | -0.009155 | 2.1378 | -0.31128 | -8.1253 | -0.18311 | -0.032043 | 2.2934 | 42.6865 | 42.8558 | 114.6515 | 122.7676 | 2.1378 | 122.7448 | 64.4348 | -0.18311 | 122.7676 | 2.1378 | 64.4348 | 114.6515 | 122.7448 | -122.9324 | -122.9599
1231.3438 | 123.0148 | -59.6695 | 63.1897 | 0.087433 | 0.027983 | 0.018933 | 0.018342 | 0.063102 | 0.00042511 | 0.084845 | -57.5546 | 63.1989 | -59.7931 | -59.903 | 55.1926 | 4.7058 | -17.0288 | -17.0105 | 63.1577 | -59.8755 | -0.1236 | 0.009156 | 2.1149 | -0.23346 | -7.9971 | -0.20599 | -0.032043 | 2.2385 | 42.6407 | 42.659 | 114.8621 | 122.8683 | 2.1149 | 122.8271 | 64.3753 | -0.20599 | 122.8683 | 2.1149 | 64.3753 | 114.8621 | 122.8271 | -122.9828 | -123.0652
1232.3438 | 123.0377 | -59.6512 | 63.1668 | 0.034027 | 0.025419 | 0.018079 | 0.016419 | 0.063957 | -0.0027793 | 0.083349 | -57.4768 | 63.2217 | -59.8114 | -59.8434 | 55.2475 | 4.7058 | -17.0288 | -16.9098 | 63.1256 | -59.8801 | -0.16022 | 0.054932 | 2.1744 | -0.19226 | -7.9193 | -0.22888 | -0.041199 | 2.3346 | 42.6224 | 42.7414 | 114.8987 | 122.8729 | 2.1744 | 122.7768 | 64.357 | -0.22888 | 122.8729 | 2.1744 | 64.357 | 114.8987 | 122.7768 | -122.9782 | -123.0469
1233.3438 | 123.0377 | -59.6375 | 63.2217 | -0.16434 | 0.024778 | 0.013806 | 0.015992 | 0.062889 | 0.00063871 | 0.082922 | -57.5363 | 63.2172 | -59.7794 | -59.8618 | 55.2612 | 4.6188 | -17.0105 | -16.8823 | 63.1622 | -59.8526 | -0.14191 | -0.004578 | 2.1011 | -0.2243 | -7.9605 | -0.21515 | -0.05951 | 2.243 | 42.627 | 42.7551 | 114.8987 | 122.8546 | 2.1011 | 122.7997 | 64.2563 | -0.21515 | 122.8546 | 2.1011 | 64.2563 | 114.8987 | 122.7997 | -123.0011 | -123.0743
1234.3438 | 123.0103 | -59.6191 | 63.2217 | -0.17197 | 0.023924 | 0.016584 | 0.013642 | 0.062248 | 0.0012795 | 0.081854 | -57.5592 | 63.1989 | -59.7885 | -59.8846 | 55.2475 | 4.4769 | -17.1387 | -17.0334 | 63.1989 | -59.8709 | -0.16937 | -0.022888 | 2.0599 | -0.2655 | -7.9742 | -0.25177 | -0.022888 | 2.2293 | 42.4805 | 42.5858 | 114.8666 | 122.818 | 2.0599 | 122.818 | 64.0961 | -0.25177 | 122.818 | 2.0599 | 64.0961 | 114.8666 | 122.818 | -123.0103 | -123.0927
1235.3438 | 122.9874 | -59.6512 | 63.1851 | 0.17136 | 0.026914 | 0.017224 | 0.0095832 | 0.062034 | 0.00042511 | 0.080572 | -57.4402 | 63.1851 | -59.8068 | -59.8389 | 55.1834 | 4.5639 | -16.9876 | -16.9876 | 63.2034 | -59.8526 | -0.15564 | 0 | 2.211 | -0.18768 | -8.0017 | -0.20142 | 0.01831 | 2.3666 | 42.6636 | 42.6636 | 114.8346 | 122.8363 | 2.211 | 122.8546 | 64.2151 | -0.20142 | 122.8363 | 2.211 | 64.2151 | 114.8346 | 122.8546 | -122.9919 | -123.0377
1236.3438 | 123.0194 | -59.6512 | 63.1805 | 0.0035097 | 0.023924 | 0.015088 | 0.017701 | 0.061393 | -0.00064309 | 0.082068 | -57.5317 | 63.208 | -59.7748 | -59.8755 | 55.2429 | 4.5364 | -17.1661 | -16.983 | 63.1439 | -59.8709 | -0.1236 | 0.027466 | 2.1194 | -0.2243 | -7.9376 | -0.21973 | -0.036621 | 2.243 | 42.485 | 42.6682 | 114.8941 | 122.8592 | 2.1194 | 122.7951 | 64.1876 | -0.21973 | 122.8592 | 2.1194 | 64.1876 | 114.8941 | 122.7951 | -122.9553 | -123.0515
1237.3438 | 123.1018 | -59.5917 | 63.1851 | -0.32455 | 0.023924 | 0.015729 | 0.009156 | 0.060966 | 0.0012795 | 0.083136 | -57.4905 | 63.1393 | -59.761 | -59.7885 | 55.3436 | 4.6509 | -17.276 | -16.8365 | 63.1439 | -59.7839 | -0.16937 | -0.045777 | 2.1011 | -0.19684 | -7.8415 | -0.19226 | -0.041199 | 2.2705 | 42.3157 | 42.7551 | 114.9353 | 122.731 | 2.1011 | 122.7356 | 64.2426 | -0.19226 | 122.731 | 2.1011 | 64.2426 | 114.9353 | 122.7356 | -122.9462 | -122.9691
1238.3438 | 123.0103 | -59.6146 | 63.2309 | -0.21774 | 0.023924 | 0.017438 | 0.01001 | 0.059898 | -0.0038473 | 0.082495 | -57.4951 | 63.1577 | -59.7794 | -59.848 | 55.2704 | 4.5822 | -17.0929 | -16.8732 | 63.2034 | -59.8022 | -0.1648 | -0.073242 | 2.1194 | -0.23346 | -7.9605 | -0.18768 | -0.027466 | 2.2842 | 42.5217 | 42.7414 | 114.8849 | 122.7722 | 2.1194 | 122.818 | 64.1968 | -0.18768 | 122.7722 | 2.1194 | 64.1968 | 114.8849 | 122.818 | -123.0103 | -123.0331
1239.3438 | 123.0057 | -59.6375 | 63.2446 | -0.14145 | 0.023283 | 0.017438 | 0.01236 | 0.059684 | -0.00064309 | 0.080572 | -57.5317 | 63.1851 | -59.761 | -59.8755 | 55.2383 | 4.4952 | -16.7496 | -16.7358 | 63.2629 | -59.7885 | -0.1236 | -0.059509 | 2.1057 | -0.23804 | -8.0063 | -0.15106 | 0.01831 | 2.2293 | 42.8879 | 42.9016 | 114.8758 | 122.8226 | 2.1057 | 122.9004 | 64.1327 | -0.15106 | 122.8226 | 2.1057 | 64.1327 | 114.8758 | 122.9004 | -123.0057 | -123.0331
1240.3438 | 123.0377 | -59.6237 | 63.2446 | -0.13382 | 0.025846 | 0.014661 | 0.014924 | 0.061607 | -0.0012839 | 0.081427 | -57.55 | 63.2126 | -59.7931 | -59.848 | 55.2246 | 4.5181 | -17.0654 | -16.9968 | 63.2034 | -59.8251 | -0.16937 | -0.032044 | 2.0737 | -0.2243 | -8.02 | -0.20142 | -0.041199 | 2.243 | 42.5583 | 42.627 | 114.8483 | 122.8363 | 2.0737 | 122.8271 | 64.1418 | -0.20142 | 122.8363 | 2.0737 | 64.1418 | 114.8483 | 122.8271 | -123.0377 | -123.0698
1241.3438 | 122.9782 | -59.6283 | 63.2446 | -0.18723 | 0.02606 | 0.016584 | 0.013642 | 0.059898 | -2.092e-06 | 0.081854 | -57.5638 | 63.1897 | -59.7748 | -59.7839 | 55.5588 | 4.6555 | -17.276 | -16.9327 | 63.1943 | -59.8343 | -0.14648 | -0.054932 | 2.0645 | -0.15564 | -7.6859 | -0.20599 | -0.050354 | 2.211 | 42.3523 | 42.6956 | 115.1871 | 122.818 | 2.0645 | 122.8226 | 64.2838 | -0.20599 | 122.818 | 2.0645 | 64.2838 | 115.1871 | 122.8226 | -123.0194 | -123.0789
1242.375 | 123.0972 | -59.6329 | 63.1714 | 0.17899 | 0.021574 | 0.01872 | 0.010224 | 0.059684 | -0.0012839 | 0.082708 | -57.5363 | 63.0844 | -59.7885 | -59.8251 | 55.275 | 4.5776 | -17.3126 | -16.9739 | 63.1393 | -59.8251 | -0.15564 | -0.086975 | 2.0966 | -0.19226 | -7.8964 | -0.19226 | -0.032044 | 2.2522 | 42.3203 | 42.659 | 114.9078 | 122.7173 | 2.0966 | 122.7722 | 64.2105 | -0.19226 | 122.7173 | 2.0966 | 64.2105 | 114.9078 | 122.7722 | -122.9599 | -122.9965
1243.3438 | 123.0469 | -59.5963 | 63.2263 | -0.14908 | 0.023283 | 0.012952 | 0.012787 | 0.057975 | -0.0012839 | 0.081427 | -57.5134 | 63.1439 | -59.7382 | -59.8022 | 55.275 | 4.6371 | -17.0929 | -16.8732 | 63.1943 | -59.816 | -0.14191 | -0.082397 | 2.0828 | -0.20599 | -7.9514 | -0.21973 | -0.032043 | 2.2247 | 42.5034 | 42.7231 | 114.8712 | 122.7402 | 2.0828 | 122.7905 | 64.2334 | -0.21973 | 122.7402 | 2.0828 | 64.2334 | 114.8712 | 122.7905 | -122.9645 | -123.0423
1244.3438 | 123.0515 | -59.5917 | 63.2172 | -0.20248 | 0.022428 | 0.017438 | 0.013001 | 0.058616 | -0.0027793 | 0.080359 | -57.486 | 63.1393 | -59.7473 | -59.7794 | 55.3299 | 4.7058 | -17.1524 | -16.8549 | 63.1714 | -59.8114 | -0.15564 | -0.07782 | 2.1057 | -0.18768 | -7.8873 | -0.21973 | -0.045776 | 2.2614 | 42.4393 | 42.7368 | 114.9216 | 122.731 | 2.1057 | 122.7631 | 64.2975 | -0.21973 | 122.731 | 2.1057 | 64.2975 | 114.9216 | 122.7631 | -122.9645 | -123.0286
1245.3438 | 122.9736 | -59.6466 | 63.2126 | 0.14084 | 0.026914 | 0.018079 | 0.020692 | 0.060325 | 0.00085231 | 0.082281 | -57.55 | 63.2217 | -59.7839 | -59.8938 | 55.1834 | 4.509 | -17.038 | -17.0059 | 63.2217 | -59.8663 | -0.13733 | 0.009156 | 2.0966 | -0.24719 | -8.0292 | -0.21973 | 0.009156 | 2.2339 | 42.6086 | 42.6407 | 114.83 | 122.8683 | 2.0966 | 122.8683 | 64.1556 | -0.21973 | 122.8683 | 2.0966 | 64.1556 | 114.83 | 122.8683 | -122.9965 | -123.0789
1246.3594 | 123.0789 | -59.5917 | 63.1714 | 0.19424 | 0.023069 | 0.018506 | 0.010224 | 0.059257 | -0.0023519 | 0.081854 | -57.5089 | 63.121 | -59.7473 | -59.7977 | 55.307 | 4.5639 | -17.2897 | -16.9327 | 63.1119 | -59.816 | -0.15564 | -0.050354 | 2.0828 | -0.20599 | -7.8644 | -0.2243 | -0.05951 | 2.2385 | 42.3019 | 42.659 | 114.8987 | 122.7127 | 2.0828 | 122.7036 | 64.1556 | -0.2243 | 122.7127 | 2.0828 | 64.1556 | 114.8987 | 122.7036 | -122.9187 | -122.9874
1247.3438 | 123.0927 | -59.5779 | 63.1805 | -0.13382 | 0.021787 | 0.012952 | 0.0093696 | 0.055625 | -0.0021383 | 0.083136 | -57.4768 | 63.1439 | -59.7336 | -60.0632 | 55.1971 | 4.5731 | -17.4362 | -16.9189 | 63.121 | -59.7977 | -0.15564 | -0.036621 | 2.1011 | -0.48523 | -7.9834 | -0.21973 | -0.059509 | 2.2568 | 42.1417 | 42.659 | 114.7751 | 122.7219 | 2.1011 | 122.699 | 64.151 | -0.21973 | 122.7219 | 2.1011 | 64.151 | 114.7751 | 122.699 | -122.9141 | -122.9782
1248.3438 | 123.1064 | -59.5642 | 63.2538 | -0.042267 | 0.023069 | 0.017652 | 0.011719 | 0.058402 | -0.0017111 | 0.081854 | -57.4905 | 63.1577 | -59.7244 | -59.729 | 55.3665 | 4.5319 | -17.2211 | -16.8961 | 63.1805 | -59.8022 | -0.16022 | -0.09613 | 2.0737 | -0.1648 | -7.8873 | -0.23804 | -0.073242 | 2.2339 | 42.3431 | 42.6682 | 114.9307 | 122.7219 | 2.0737 | 122.7448 | 64.0961 | -0.23804 | 122.7219 | 2.0737 | 64.0961 | 114.9307 | 122.7448 | -122.9782 | -123.056
1249.3438 | 123.0743 | -59.5734 | 63.2172 | 0.049286 | 0.022428 | 0.012952 | 0.011933 | 0.057548 | -0.0010703 | 0.080786 | -57.5455 | 63.1256 | -59.7565 | -59.8206 | 55.2887 | 4.5593 | -17.1936 | -16.9876 | 63.1851 | -59.7885 | -0.18311 | -0.091553 | 2.0279 | -0.24719 | -7.9285 | -0.21515 | -0.032043 | 2.211 | 42.3798 | 42.5858 | 114.8621 | 122.699 | 2.0279 | 122.7585 | 64.1327 | -0.21515 | 122.699 | 2.0279 | 64.1327 | 114.8621 | 122.7585 | -122.9736 | -123.0057
1250.3438 | 123.1384 | -59.5551 | 63.2217 | -0.14908 | 0.021787 | 0.013806 | 0.013428 | 0.058189 | -0.0019247 | 0.082495 | -57.4585 | 63.1348 | -59.7153 | -59.7198 | 55.3574 | 4.6143 | -17.2623 | -16.8823 | 63.1714 | -59.761 | -0.16022 | -0.086975 | 2.0966 | -0.1648 | -7.8644 | -0.20599 | -0.050354 | 2.2568 | 42.2928 | 42.6727 | 114.9124 | 122.6898 | 2.0966 | 122.7264 | 64.1693 | -0.20599 | 122.6898 | 2.0966 | 64.1693 | 114.9124 | 122.7264 | -122.937 | -122.9828
1251.3438 | 123.1064 | -59.5825 | 63.208 | 0.034027 | 0.023069 | 0.015943 | 0.012574 | 0.057548 | -0.00085669 | 0.08164 | -57.5363 | 63.1302 | -59.7244 | -59.7931 | 55.3162 | 4.4952 | -17.1844 | -16.864 | 63.1577 | -59.7656 | -0.14191 | -0.07782 | 2.0462 | -0.21057 | -7.8918 | -0.1831 | -0.050354 | 2.1881 | 42.3981 | 42.7185 | 114.8987 | 122.7127 | 2.0462 | 122.7402 | 64.0778 | -0.1831 | 122.7127 | 2.0462 | 64.0778 | 114.8987 | 122.7402 | -122.9324 | -122.9736
1252.3438 | 123.1064 | -59.5551 | 63.2172 | -0.034637 | 0.020933 | 0.011457 | 0.015137 | 0.057975 | -0.0012839 | 0.080145 | -57.5043 | 63.1302 | -59.7336 | -59.7473 | 55.3253 | 4.4495 | -17.2165 | -16.8869 | 63.176 | -59.7656 | -0.17853 | -0.086975 | 2.0508 | -0.19226 | -7.8918 | -0.21057 | -0.041199 | 2.2293 | 42.3386 | 42.6682 | 114.8804 | 122.6852 | 2.0508 | 122.731 | 64.0045 | -0.21057 | 122.6852 | 2.0508 | 64.0045 | 114.8804 | 122.731 | -122.9507 | -122.9828
1253.3594 | 123.1796 | -59.5642 | 63.208 | -0.088043 | 0.026701 | 0.013806 | 0.013428 | 0.057121 | -0.0019247 | 0.083563 | -57.4402 | 63.1348 | -59.7198 | -59.7107 | 55.3802 | 4.4083 | -16.7587 | -16.6626 | 63.2446 | -59.7519 | -0.15564 | -0.073242 | 2.124 | -0.14648 | -7.8278 | -0.18768 | 0.036621 | 2.2797 | 42.8055 | 42.9016 | 114.9445 | 122.699 | 2.124 | 122.8088 | 63.9725 | -0.18768 | 122.699 | 2.124 | 63.9725 | 114.9445 | 122.8088 | -122.9279 | -122.9599
1254.3438 | 123.111 | -59.5642 | 63.2492 | -0.15671 | 0.02606 | 0.014447 | 0.012787 | 0.059257 | -0.0053427 | 0.080786 | -57.4493 | 63.1531 | -59.697 | -59.7107 | 55.3802 | 4.4449 | -17.2348 | -16.9464 | 63.2034 | -59.761 | -0.13275 | -0.096131 | 2.1149 | -0.14648 | -7.869 | -0.19684 | -0.045777 | 2.2476 | 42.3294 | 42.6178 | 114.9445 | 122.7173 | 2.1149 | 122.7676 | 64.0091 | -0.19684 | 122.7173 | 2.1149 | 64.0091 | 114.9445 | 122.7676 | -122.9462 | -123.0103
1255.3438 | 123.024 | -59.6191 | 63.2584 | -0.1796 | 0.024992 | 0.013593 | 0.017487 | 0.059684 | 0.00042511 | 0.080359 | -57.5089 | 63.2492 | -59.7702 | -59.7931 | 55.2658 | 4.2755 | -17.1021 | -17.1066 | 63.2538 | -59.8022 | -0.15106 | -0.009155 | 2.1103 | -0.17395 | -7.9926 | -0.1831 | -0.004578 | 2.2614 | 42.5171 | 42.5125 | 114.8849 | 122.8683 | 2.1103 | 122.8729 | 63.8947 | -0.1831 | 122.8683 | 2.1103 | 63.8947 | 114.8849 | 122.8729 | -123.0286 | -123.0606
1256.3438 | 123.1247 | -59.5734 | 63.1851 | -0.019379 | 0.020292 | 0.013593 | 0.010438 | 0.060325 | -0.0023519 | 0.082068 | -57.4997 | 63.1165 | -59.729 | -59.729 | 55.3848 | 4.4769 | -17.2165 | -16.9464 | 63.1943 | -59.7336 | -0.15564 | -0.068665 | 2.0737 | -0.15564 | -7.8003 | -0.16022 | 0.009155 | 2.2293 | 42.3569 | 42.627 | 114.9582 | 122.6898 | 2.0737 | 122.7676 | 64.0503 | -0.16022 | 122.6898 | 2.0737 | 64.0503 | 114.9582 | 122.7676 | -122.9141 | -122.9187
1257.3594 | 123.0789 | -59.5871 | 63.2355 | 0.11032 | 0.022001 | 0.01637 | 0.013428 | 0.059471 | -0.0025657 | 0.079718 | -57.5272 | 63.1165 | -59.7382 | -59.8343 | 55.2567 | 4.4174 | -17.2302 | -17.07 | 63.1897 | -59.7565 | -0.15106 | -0.11902 | 2.0599 | -0.24719 | -7.9788 | -0.16937 | -0.045777 | 2.211 | 42.3569 | 42.5171 | 114.8438 | 122.7036 | 2.0599 | 122.7768 | 64.0045 | -0.16937 | 122.7036 | 2.0599 | 64.0045 | 114.8438 | 122.7768 | -122.9736 | -122.9919
1258.3438 | 123.0972 | -59.5688 | 63.176 | 0.19424 | 0.024565 | 0.01637 | 0.015992 | 0.060325 | -0.0040609 | 0.08164 | -57.4722 | 63.1027 | -59.761 | -59.761 | 55.3436 | 4.4998 | -17.2852 | -17.0059 | 63.1577 | -59.7565 | -0.19226 | -0.073242 | 2.0966 | -0.19226 | -7.8323 | -0.18768 | -0.01831 | 2.2888 | 42.2836 | 42.5629 | 114.9124 | 122.6715 | 2.0966 | 122.7264 | 64.0686 | -0.18768 | 122.6715 | 2.0966 | 64.0686 | 114.9124 | 122.7264 | -122.937 | -122.9324
1259.3438 | 123.0698 | -59.5871 | 63.2401 | 0.10269 | 0.022856 | 0.012311 | 0.011292 | 0.059898 | -0.00021569 | 0.081854 | -57.5317 | 63.121 | -59.7244 | -59.7977 | 55.2063 | 4.3762 | -17.1478 | -17.0013 | 63.1577 | -59.7702 | -0.13733 | -0.11902 | 2.0554 | -0.21057 | -8.0338 | -0.18311 | -0.082397 | 2.1927 | 42.4393 | 42.5858 | 114.7934 | 122.7081 | 2.0554 | 122.7448 | 63.9633 | -0.18311 | 122.7081 | 2.0554 | 63.9633 | 114.7934 | 122.7448 | -122.9645 | -123.0103
1260.3438 | 123.0011 | -59.5917 | 63.3087 | -0.1796 | 0.02606 | 0.012525 | 0.015565 | 0.055198 | 0.00042511 | 0.082068 | -57.3898 | 63.2675 | -59.7015 | -59.8068 | 55.3116 | 4.3304 | -17.0105 | -17.0654 | 63.2446 | -59.8297 | -0.10986 | -0.041199 | 2.2018 | -0.21515 | -7.9971 | -0.23804 | -0.064087 | 2.3117 | 42.5812 | 42.5262 | 114.9033 | 122.8592 | 2.2018 | 122.8363 | 63.9221 | -0.23804 | 122.8592 | 2.2018 | 63.9221 | 114.9033 | 122.8363 | -123.0103 | -123.1384
1261.3438 | 123.0927 | -59.5505 | 63.2172 | 0.1561 | 0.023496 | 0.017652 | 0.010865 | 0.058189 | -0.00064309 | 0.083563 | -57.5317 | 63.1256 | -59.761 | -59.7794 | 55.3024 | 4.3396 | -17.1753 | -17.0837 | 63.1622 | -59.7565 | -0.21057 | -0.091553 | 2.0187 | -0.22888 | -7.9147 | -0.20599 | -0.054932 | 2.2293 | 42.3752 | 42.4667 | 114.8529 | 122.6761 | 2.0187 | 122.7127 | 63.8901 | -0.20599 | 122.6761 | 2.0187 | 63.8901 | 114.8529 | 122.7127 | -122.9782 | -122.9736
1262.3438 | 123.1155 | -59.5596 | 63.2401 | 0.018768 | 0.022642 | 0.013593 | 0.011719 | 0.057334 | -0.0021383 | 0.083777 | -57.486 | 63.1668 | -59.7244 | -59.7107 | 55.394 | 4.4769 | -17.1982 | -16.9876 | 63.1531 | -59.7519 | -0.16479 | -0.073242 | 2.0737 | -0.15106 | -7.8461 | -0.19226 | -0.086975 | 2.2385 | 42.3615 | 42.572 | 114.9536 | 122.7264 | 2.0737 | 122.7127 | 64.0366 | -0.19226 | 122.7264 | 2.0737 | 64.0366 | 114.9536 | 122.7127 | -122.9645 | -122.9919
1263.3438 | 123.0927 | -59.5734 | 63.208 | 0.1561 | 0.021574 | 0.014875 | 0.014069 | 0.058402 | -0.00064309 | 0.081213 | -57.4585 | 63.1531 | -59.729 | -59.7519 | 55.3436 | 4.3716 | -17.2256 | -17.0242 | 63.1577 | -59.7748 | -0.15564 | -0.054932 | 2.1149 | -0.17853 | -7.8644 | -0.20142 | -0.050354 | 2.2705 | 42.3477 | 42.5491 | 114.917 | 122.7264 | 2.1149 | 122.731 | 63.945 | -0.20142 | 122.7264 | 2.1149 | 63.945 | 114.917 | 122.731 | -122.937 | -122.9828
1264.3438 | 123.0652 | -59.5688 | 63.2172 | 0.2095 | 0.026701 | 0.018293 | 0.013642 | 0.059684 | -0.00042929 | 0.081213 | -57.4768 | 63.1622 | -59.7336 | -59.7748 | 55.3345 | 4.3579 | -17.2073 | -17.0929 | 63.1393 | -59.7748 | -0.16479 | -0.054932 | 2.092 | -0.20599 | -7.8827 | -0.20599 | -0.07782 | 2.2568 | 42.3615 | 42.4759 | 114.9033 | 122.731 | 2.092 | 122.7081 | 63.9267 | -0.20599 | 122.731 | 2.092 | 63.9267 | 114.9033 | 122.7081 | -122.9507 | -122.9919
1265.3438 | 123.0972 | -59.5825 | 63.2217 | 0.24002 | 0.02371 | 0.019361 | 0.019196 | 0.059257 | -0.00085669 | 0.080786 | -57.5409 | 63.1668 | -59.7382 | -59.761 | 55.3528 | 4.3625 | -17.2714 | -17.1112 | 63.1302 | -59.7885 | -0.15564 | -0.054932 | 2.0416 | -0.17853 | -7.869 | -0.20599 | -0.091553 | 2.1973 | 42.3111 | 42.4713 | 114.9353 | 122.7493 | 2.0416 | 122.7127 | 63.945 | -0.20599 | 122.7493 | 2.0416 | 63.945 | 114.9353 | 122.7127 | -122.9599 | -123.0103
1266.3438 | 123.1522 | -59.5367 | 63.208 | 0.21713 | 0.024778 | 0.015515 | 0.017914 | 0.059471 | 0.00063871 | 0.081854 | -57.4768 | 63.1714 | -59.7336 | -59.7748 | 55.0781 | 4.097 | -16.951 | -17.0151 | 63.1531 | -59.7977 | -0.19684 | -0.036621 | 2.0599 | -0.23804 | -8.1299 | -0.26093 | -0.054932 | 2.2568 | 42.5858 | 42.5217 | 114.6149 | 122.7081 | 2.0599 | 122.6898 | 63.6337 | -0.26093 | 122.7081 | 2.0599 | 63.6337 | 114.6149 | 122.6898 | -122.9416 | -123.0057
1267.3594 | 123.0515 | -59.5825 | 63.2355 | 0.20187 | 0.026701 | 0.018293 | 0.017274 | 0.058616 | 0.00063871 | 0.082495 | -57.5226 | 63.2217 | -59.7382 | -59.8068 | 55.307 | 4.1428 | -17.1158 | -17.1524 | 63.1485 | -59.848 | -0.15564 | -0.013733 | 2.0599 | -0.2243 | -7.9285 | -0.2655 | -0.086975 | 2.2156 | 42.4667 | 42.4301 | 114.8895 | 122.8043 | 2.0599 | 122.731 | 63.7253 | -0.2655 | 122.8043 | 2.0599 | 63.7253 | 114.8895 | 122.731 | -122.9736 | -123.0835
1268.3438 | 123.1201 | -59.5779 | 63.1989 | 0.22476 | 0.025633 | 0.017011 | 0.015778 | 0.060539 | -0.0017111 | 0.081854 | -57.5043 | 63.2034 | -59.729 | -59.729 | 55.3436 | 4.2114 | -17.2302 | -17.0746 | 63.1348 | -59.7702 | -0.15106 | 0.004577 | 2.0737 | -0.15106 | -7.8552 | -0.19226 | -0.064087 | 2.2247 | 42.3477 | 42.5034 | 114.9216 | 122.7814 | 2.0737 | 122.7127 | 63.7894 | -0.19226 | 122.7814 | 2.0737 | 63.7894 | 114.9216 | 122.7127 | -122.9279 | -122.9691
1269.3438 | 123.0881 | -59.5551 | 63.208 | 0.14847 | 0.024992 | 0.013593 | 0.013001 | 0.057334 | -2.092e-06 | 0.082068 | -57.55 | 63.176 | -59.7198 | -59.7977 | 55.3253 | 4.1931 | -17.1295 | -17.0792 | 63.1577 | -59.7473 | -0.1648 | -0.032044 | 2.005 | -0.24261 | -7.8827 | -0.19226 | -0.050354 | 2.1698 | 42.4255 | 42.4759 | 114.8804 | 122.731 | 2.005 | 122.7127 | 63.7482 | -0.19226 | 122.731 | 2.005 | 63.7482 | 114.8804 | 122.7127 | -122.9279 | -122.9553
1270.3438 | 123.0881 | -59.5367 | 63.2401 | 0.018768 | 0.025846 | 0.019361 | 0.011933 | 0.055839 | -0.0012839 | 0.083136 | -57.5272 | 63.176 | -59.6924 | -59.7427 | 55.3665 | 4.3396 | -17.0563 | -16.9693 | 63.1393 | -59.7565 | -0.15564 | -0.064087 | 2.0096 | -0.20599 | -7.8735 | -0.21973 | -0.10071 | 2.1652 | 42.4805 | 42.5674 | 114.9033 | 122.7127 | 2.0096 | 122.6761 | 63.8763 | -0.21973 | 122.7127 | 2.0096 | 63.8763 | 114.9033 | 122.6761 | -122.9324 | -122.9965
1271.3438 | 122.9919 | -59.6146 | 63.2858 | 0.26291 | 0.024778 | 0.013166 | 0.022614 | 0.058616 | -0.00021569 | 0.080786 | -57.2754 | 63.2767 | -59.7153 | -59.8297 | 55.2292 | 4.2023 | -17.0883 | -17.2348 | 63.2263 | -59.816 | -0.10071 | -0.009156 | 2.3392 | -0.21515 | -8.0566 | -0.20142 | -0.05951 | 2.4399 | 42.5262 | 42.3798 | 114.8438 | 122.8912 | 2.3392 | 122.8409 | 63.8168 | -0.20142 | 122.8912 | 2.3392 | 63.8168 | 114.8438 | 122.8409 | -123.0011 | -123.1018
1272.3438 | 123.111 | -59.523 | 63.2126 | 0.18662 | 0.024992 | 0.014661 | 0.014496 | 0.058616 | -0.0010703 | 0.083349 | -57.4905 | 63.1577 | -59.7244 | -59.7427 | 55.3711 | 4.3488 | -17.189 | -17.0609 | 63.1531 | -59.761 | -0.20142 | -0.054931 | 2.0325 | -0.21973 | -7.8415 | -0.23804 | -0.059509 | 2.2339 | 42.334 | 42.4622 | 114.8941 | 122.6807 | 2.0325 | 122.6761 | 63.8718 | -0.23804 | 122.6807 | 2.0325 | 63.8718 | 114.8941 | 122.6761 | -122.937 | -122.9736
1273.3438 | 123.0927 | -59.5505 | 63.2492 | 0.17899 | 0.025205 | 0.012738 | 0.016633 | 0.060325 | 0.00085231 | 0.080359 | -57.518 | 63.2263 | -59.7473 | -59.761 | 55.3482 | 4.3167 | -17.2485 | -17.1295 | 63.1393 | -59.7977 | -0.19684 | -0.022889 | 2.0325 | -0.21057 | -7.901 | -0.24719 | -0.10986 | 2.2293 | 42.3019 | 42.421 | 114.8987 | 122.7768 | 2.0325 | 122.6898 | 63.8672 | -0.24719 | 122.7768 | 2.0325 | 63.8672 | 114.8987 | 122.6898 | -122.9965 | -123.0469
1274.3438 | 123.0835 | -59.5505 | 63.2584 | 0.22476 | 0.025633 | 0.016156 | 0.017914 | 0.060966 | -2.092e-06 | 0.082708 | -57.5134 | 63.2629 | -59.7107 | -59.7885 | 55.3253 | 4.248 | -17.2668 | -17.1982 | 63.1851 | -59.7794 | -0.16022 | 0.004577 | 2.037 | -0.23804 | -7.933 | -0.22888 | -0.073242 | 2.1973 | 42.2836 | 42.3523 | 114.8758 | 122.8134 | 2.037 | 122.7356 | 63.7985 | -0.22888 | 122.8134 | 2.037 | 63.7985 | 114.8758 | 122.7356 | -122.9691 | -123.0377
1275.3438 | 123.0881 | -59.523 | 63.2492 | 0.072174 | 0.023283 | 0.012525 | 0.0083014 | 0.055839 | -0.0025657 | 0.082068 | -57.5317 | 63.2126 | -59.7015 | -59.761 | 55.3619 | 4.2847 | -17.1982 | -17.0654 | 63.1714 | -59.7473 | -0.17853 | -0.036622 | 1.9913 | -0.23804 | -7.8873 | -0.2243 | -0.07782 | 2.1698 | 42.3248 | 42.4576 | 114.8849 | 122.7356 | 1.9913 | 122.6944 | 63.8077 | -0.2243 | 122.7356 | 1.9913 | 63.8077 | 114.8849 | 122.6944 | -122.9507 | -122.9965
1276.3438 | 123.1018 | -59.5459 | 63.2355 | 0.21713 | 0.026487 | 0.012952 | 0.019837 | 0.059043 | 0.00085231 | 0.079718 | -57.5363 | 63.2355 | -59.7244 | -59.7565 | 55.3482 | 4.2023 | -17.2028 | -17.0334 | 63.1805 | -59.7519 | -0.17853 | 0 | 2.0096 | -0.21057 | -7.8873 | -0.20599 | -0.054932 | 2.1881 | 42.3431 | 42.5125 | 114.8941 | 122.7814 | 2.0096 | 122.7264 | 63.7482 | -0.20599 | 122.7814 | 2.0096 | 63.7482 | 114.8941 | 122.7264 | -122.9599 | -122.9874
1277.3438 | 123.0469 | -59.5642 | 63.2812 | 0.24002 | 0.029478 | 0.014661 | 0.018128 | 0.060325 | 0.00042511 | 0.081854 | -57.5272 | 63.2538 | -59.7198 | -59.8022 | 55.3253 | 4.0558 | -17.2394 | -17.1616 | 63.1989 | -59.7839 | -0.15564 | -0.027466 | 2.037 | -0.23804 | -7.9559 | -0.21973 | -0.082397 | 2.1927 | 42.3248 | 42.4026 | 114.8895 | 122.818 | 2.037 | 122.7631 | 63.62 | -0.21973 | 122.818 | 2.037 | 63.62 | 114.8895 | 122.7631 | -123.0011 | -123.0652
1278.3438 | 123.0881 | -59.5413 | 63.2492 | 0.24002 | 0.026701 | 0.015729 | 0.015778 | 0.058616 | -0.0010703 | 0.082922 | -57.5043 | 63.2446 | -59.7244 | -59.7336 | 55.3848 | 4.1428 | -17.2668 | -17.0792 | 63.1805 | -59.7748 | -0.1831 | -0.004578 | 2.037 | -0.19226 | -7.8644 | -0.23346 | -0.068665 | 2.2202 | 42.2745 | 42.4622 | 114.9261 | 122.786 | 2.037 | 122.7219 | 63.6841 | -0.23346 | 122.786 | 2.037 | 63.6841 | 114.9261 | 122.7219 | -122.9736 | -123.024
1279.3438 | 123.024 | -59.5459 | 63.3179 | -0.0041198 | 0.027128 | 0.01872 | 0.01706 | 0.06118 | -0.0025657 | 0.08164 | -57.4265 | 63.3133 | -59.6649 | -59.7153 | 55.4031 | 4.0695 | -17.1616 | -17.1204 | 63.2538 | -59.7839 | -0.11902 | -0.004578 | 2.1194 | -0.16937 | -7.9147 | -0.23804 | -0.064087 | 2.2385 | 42.3843 | 42.4255 | 114.949 | 122.8592 | 2.1194 | 122.7997 | 63.6154 | -0.23804 | 122.8592 | 2.1194 | 63.6154 | 114.949 | 122.7997 | -122.9828 | -123.1018
1280.3438 | 123.0972 | -59.5413 | 63.2446 | 0.18662 | 0.024351 | 0.013593 | 0.0097968 | 0.059257 | 0.00042511 | 0.082708 | -57.4997 | 63.1943 | -59.7153 | -59.7336 | 55.4031 | 4.1473 | -17.2165 | -17.0883 | 63.1577 | -59.7107 | -0.17395 | -0.050354 | 2.0416 | -0.19226 | -7.8415 | -0.16937 | -0.086975 | 2.2156 | 42.3248 | 42.453 | 114.9445 | 122.7356 | 2.0416 | 122.699 | 63.6887 | -0.16937 | 122.7356 | 2.0416 | 63.6887 | 114.9445 | 122.699 | -122.9599 | -122.9553
1281.3438 | 122.9919 | -59.5505 | 63.3087 | 0.11795 | 0.023924 | 0.01637 | 0.018342 | 0.059471 | 0.00063871 | 0.084417 | -57.5455 | 63.3041 | -59.7061 | -60.0769 | 55.5359 | 4.3304 | -17.1158 | -17.1158 | 63.2629 | -59.7748 | -0.15564 | -0.004578 | 2.005 | -0.52643 | -7.7728 | -0.2243 | -0.045777 | 2.1606 | 42.4347 | 42.4347 | 115.0864 | 122.8546 | 2.005 | 122.8134 | 63.8809 | -0.2243 | 122.8546 | 2.005 | 63.8809 | 115.0864 | 122.8134 | -123.0148 | -123.0835
1282.3438 | 122.9874 | -59.5459 | 63.3087 | 0.60623 | 0.02606 | 0.018933 | 0.017701 | 0.059257 | -2.092e-06 | 0.081427 | -57.4402 | 63.3224 | -59.6741 | -59.7015 | 55.3757 | 4.1611 | -17.07 | -17.1204 | 63.2217 | -59.7839 | -0.12817 | 0.013733 | 2.1057 | -0.15564 | -7.933 | -0.23804 | -0.086975 | 2.2339 | 42.4759 | 42.4255 | 114.9216 | 122.8683 | 2.1057 | 122.7676 | 63.707 | -0.23804 | 122.8683 | 2.1057 | 63.707 | 114.9216 | 122.7676 | -122.9828 | -123.0927
1283.3438 | 123.0286 | -59.5322 | 63.2767 | -0.0041198 | 0.026274 | 0.014661 | 0.015351 | 0.063102 | 0.00063871 | 0.079931 | -57.486 | 63.3316 | -59.697 | -59.7519 | 55.3619 | 4.0924 | -17.0883 | -17.1066 | 63.2721 | -59.7656 | -0.16479 | 0.054932 | 2.0462 | -0.21973 | -7.9147 | -0.23346 | -0.004577 | 2.211 | 42.4438 | 42.4255 | 114.8941 | 122.8638 | 2.0462 | 122.8043 | 63.6246 | -0.23346 | 122.8638 | 2.0462 | 63.6246 | 114.8941 | 122.8043 | -122.9736 | -123.0423
1284.3438 | 123.0148 | -59.5688 | 63.3041 | 0.11032 | 0.027342 | 0.019147 | 0.015565 | 0.065238 | 0.0023477 | 0.078863 | -57.5592 | 63.3179 | -59.7153 | -59.4955 | 55.3757 | 4.0192 | -16.8091 | -17.0929 | 63.295 | -59.7702 | -0.14648 | 0.013733 | 2.0096 | 0.073243 | -7.9285 | -0.20142 | -0.009155 | 2.1561 | 42.7597 | 42.4759 | 114.9445 | 122.8867 | 2.0096 | 122.8638 | 63.588 | -0.20142 | 122.8867 | 2.0096 | 63.588 | 114.9445 | 122.8638 | -123.0194 | -123.0743
1285.3438 | 123.0331 | -59.5367 | 63.2996 | -0.12619 | 0.025419 | 0.017652 | 0.014496 | 0.063743 | -0.0014975 | 0.081 | -57.5043 | 63.3087 | -59.697 | -59.7244 | 55.4077 | 4.2801 | -16.9235 | -16.9739 | 63.2675 | -59.7702 | -0.16022 | 0.009155 | 2.0325 | -0.18768 | -7.8918 | -0.23346 | -0.032044 | 2.1927 | 42.6132 | 42.5629 | 114.9445 | 122.8455 | 2.0325 | 122.8043 | 63.8168 | -0.23346 | 122.8455 | 2.0325 | 63.8168 | 114.9445 | 122.8043 | -122.9965 | -123.0698
1286.3438 | 122.9782 | -59.5459 | 63.2767 | -1.1256 | 0.025205 | 0.014234 | 0.015351 | 0.063957 | -0.00021569 | 0.081427 | -57.5958 | 63.3133 | -59.7107 | -59.8114 | 55.2933 | 4.0695 | -17.0609 | -17.1661 | 63.2675 | -59.7656 | -0.16479 | 0.036621 | 1.9501 | -0.2655 | -7.9834 | -0.21973 | -0.009155 | 2.1149 | 42.485 | 42.3798 | 114.8392 | 122.8592 | 1.9501 | 122.8134 | 63.6154 | -0.21973 | 122.8592 | 1.9501 | 63.6154 | 114.8392 | 122.8134 | -122.9874 | -123.0423
1287.3594 | 123.056 | -59.5184 | 63.2904 | -0.11856 | 0.024992 | 0.01637 | 0.015351 | 0.061393 | -0.0012839 | 0.079718 | -57.7057 | 63.3133 | -59.697 | -59.7244 | 55.3848 | 4.1702 | -17.1066 | -17.0151 | 63.2675 | -59.7519 | -0.17853 | 0.022888 | 1.8127 | -0.20599 | -7.9056 | -0.23346 | -0.022888 | 1.9913 | 42.4118 | 42.5034 | 114.9033 | 122.8317 | 1.8127 | 122.7859 | 63.6887 | -0.23346 | 122.8317 | 1.8127 | 63.6887 | 114.9033 | 122.7859 | -122.9874 | -123.0423
1288.3438 | 122.9828 | -59.5505 | 63.3041 | 0.2095 | 0.025419 | 0.014447 | 0.013215 | 0.062248 | 0.00063871 | 0.082922 | -57.5821 | 63.327 | -59.7382 | -59.816 | 55.3116 | 4.1565 | -17.1066 | -17.1982 | 63.2446 | -59.7794 | -0.18768 | 0.022888 | 1.9684 | -0.2655 | -7.9926 | -0.22888 | -0.059509 | 2.1561 | 42.4438 | 42.3523 | 114.8621 | 122.8775 | 1.9684 | 122.7951 | 63.707 | -0.22888 | 122.8775 | 1.9684 | 63.707 | 114.8621 | 122.7951 | -123.0423 | -123.0835
1289.3281 | 123.0423 | -59.5276 | 63.3087 | -0.14145 | 0.024992 | 0.015515 | 0.014069 | 0.060539 | -0.0010703 | 0.080572 | -57.518 | 63.3224 | -59.7244 | -59.7656 | 55.3574 | 4.2343 | -16.9647 | -17.0746 | 63.2675 | -59.7336 | -0.19684 | 0.013733 | 2.0096 | -0.23804 | -7.9514 | -0.20599 | -0.041199 | 2.2064 | 42.5629 | 42.453 | 114.8849 | 122.85 | 2.0096 | 122.7951 | 63.7619 | -0.20599 | 122.85 | 2.0096 | 63.7619 | 114.8849 | 122.7951 | -123.0331 | -123.0423
1290.3438 | 122.9553 | -59.5413 | 63.3179 | 0.11032 | 0.027342 | 0.015943 | 0.015992 | 0.061393 | 0.0019205 | 0.082495 | -57.4997 | 63.327 | -59.6878 | -59.7931 | 55.3207 | 4.2114 | -16.9693 | -17.0654 | 63.2629 | -59.7519 | -0.14648 | 0.009155 | 2.0416 | -0.25177 | -7.9971 | -0.21057 | -0.054932 | 2.1881 | 42.572 | 42.4759 | 114.8621 | 122.8683 | 2.0416 | 122.8043 | 63.7527 | -0.21057 | 122.8683 | 2.0416 | 63.7527 | 114.8621 | 122.8043 | -123.0057 | -123.0698
1291.3438 | 123.0194 | -59.5322 | 63.2812 | -0.11856 | 0.027342 | 0.017224 | 0.015137 | 0.062034 | -2.092e-06 | 0.080786 | -57.4677 | 63.3179 | -59.6603 | -59.7198 | 55.426 | 4.3671 | -17.0197 | -17.0425 | 63.2904 | -59.729 | -0.12817 | 0.036621 | 2.0645 | -0.18768 | -7.8552 | -0.19684 | 0.009155 | 2.1927 | 42.5125 | 42.4896 | 114.9582 | 122.85 | 2.0645 | 122.8226 | 63.8992 | -0.19684 | 122.85 | 2.0645 | 63.8992 | 114.9582 | 122.8226 | -122.9416 | -123.0103
1292.3438 | 123.0194 | -59.523 | 63.3224 | -0.14908 | 0.024778 | 0.014661 | 0.01471 | 0.059684 | -0.00085669 | 0.080572 | -57.486 | 63.3362 | -59.6924 | -59.7198 | 55.3986 | 4.3442 | -17.0059 | -17.0837 | 63.3224 | -59.7427 | -0.16937 | 0.013733 | 2.037 | -0.19684 | -7.9239 | -0.21973 | 0 | 2.2064 | 42.5171 | 42.4393 | 114.9216 | 122.8592 | 2.037 | 122.8455 | 63.8672 | -0.21973 | 122.8592 | 2.037 | 63.8672 | 114.9216 | 122.8455 | -123.0148 | -123.0652
1293.3438 | 122.9965 | -59.5596 | 63.3362 | -0.095673 | 0.024565 | 0.013593 | 0.014496 | 0.060325 | -0.00042929 | 0.081427 | -57.5409 | 63.3499 | -59.6924 | -59.7748 | 55.3528 | 4.2709 | -16.9922 | -17.1524 | 63.3224 | -59.7382 | -0.13275 | 0.013733 | 2.0187 | -0.21515 | -7.9834 | -0.17853 | -0.013733 | 2.1515 | 42.5674 | 42.4072 | 114.9124 | 122.9095 | 2.0187 | 122.8821 | 63.8306 | -0.17853 | 122.9095 | 2.0187 | 63.8306 | 114.9124 | 122.8821 | -123.0286 | -123.0743
1294.3438 | 123.0423 | -59.523 | 63.3224 | -0.13382 | 0.025633 | 0.017224 | 0.015565 | 0.062034 | 0.0014933 | 0.082281 | -57.4539 | 63.3041 | -59.6558 | -59.7244 | 55.3894 | 4.3945 | -16.951 | -17.0151 | 63.3133 | -59.7336 | -0.13275 | -0.018311 | 2.0691 | -0.20142 | -7.933 | -0.21057 | -0.009156 | 2.2018 | 42.572 | 42.5079 | 114.9124 | 122.8271 | 2.0691 | 122.8363 | 63.9175 | -0.21057 | 122.8271 | 2.0691 | 63.9175 | 114.9124 | 122.8363 | -122.9782 | -123.056
1295.3438 | 122.9919 | -59.5459 | 63.3041 | 0.064545 | 0.025846 | 0.015943 | 0.01706 | 0.061607 | 0.0017069 | 0.080572 | -57.5089 | 63.327 | -59.697 | -59.7748 | 55.3299 | 4.2526 | -16.9189 | -17.1432 | 63.3087 | -59.729 | -0.15106 | 0.022888 | 2.037 | -0.22888 | -7.9742 | -0.18311 | 0.004578 | 2.1881 | 42.627 | 42.4026 | 114.8758 | 122.8729 | 2.037 | 122.8546 | 63.7985 | -0.18311 | 122.8729 | 2.037 | 63.7985 | 114.8758 | 122.8546 | -123.0011 | -123.0331
1296.3438 | 123.024 | -59.5047 | 63.3224 | -0.11856 | 0.027128 | 0.015302 | 0.01471 | 0.063102 | -0.00064309 | 0.083136 | -57.5089 | 63.3545 | -59.7015 | -59.7519 | 55.3711 | 4.1428 | -16.8961 | -17.0792 | 63.3133 | -59.761 | -0.19684 | 0.032043 | 1.9958 | -0.24719 | -7.9514 | -0.25635 | -0.009156 | 2.1927 | 42.6086 | 42.4255 | 114.8758 | 122.8592 | 1.9958 | 122.818 | 63.6475 | -0.25635 | 122.8592 | 1.9958 | 63.6475 | 114.8758 | 122.818 | -123.024 | -123.0835
1297.3438 | 123.0377 | -59.5184 | 63.3179 | -0.12619 | 0.024565 | 0.013593 | 0.01471 | 0.062034 | -0.0029929 | 0.080359 | -57.4722 | 63.3499 | -59.6832 | -59.7107 | 55.4031 | 4.2068 | -16.9464 | -17.0197 | 63.3224 | -59.7427 | -0.16479 | 0.032044 | 2.0462 | -0.19226 | -7.9147 | -0.2243 | 0.004578 | 2.211 | 42.572 | 42.4988 | 114.9216 | 122.8683 | 2.0462 | 122.8409 | 63.7253 | -0.2243 | 122.8683 | 2.0462 | 63.7253 | 114.9216 | 122.8409 | -123.0011 | -123.0606
1298.3438 | 123.0423 | -59.4955 | 63.3316 | -0.11856 | 0.024992 | 0.013379 | 0.015351 | 0.062461 | -0.0012839 | 0.084845 | -57.4448 | 63.3408 | -59.6603 | -59.7107 | 55.4306 | 4.2252 | -16.9922 | -16.832 | 63.3087 | -59.7519 | -0.16479 | 0.009155 | 2.0508 | -0.21515 | -7.901 | -0.25635 | -0.022888 | 2.2156 | 42.5034 | 42.6636 | 114.9261 | 122.8363 | 2.0508 | 122.8043 | 63.7207 | -0.25635 | 122.8363 | 2.0508 | 63.7207 | 114.9261 | 122.8043 | -122.9919 | -123.0835
1299.3438 | 123.056 | -59.5367 | 63.3224 | -0.19485 | 0.023283 | 0.018293 | 0.01001 | 0.059898 | 0.00063871 | 0.082708 | -57.4814 | 63.295 | -59.6695 | -59.7198 | 55.4214 | 4.2618 | -16.7862 | -16.9144 | 63.295 | -59.729 | -0.13275 | -0.027466 | 2.0554 | -0.18311 | -7.901 | -0.19226 | -0.027466 | 2.1881 | 42.7505 | 42.6224 | 114.9582 | 122.8317 | 2.0554 | 122.8317 | 63.7985 | -0.19226 | 122.8317 | 2.0554 | 63.7985 | 114.9582 | 122.8317 | -122.9919 | -123.0515
1300.3594 | 123.0103 | -59.5367 | 63.3453 | -0.17197 | 0.023496 | 0.015088 | 0.014496 | 0.059898 | -0.0014975 | 0.08164 | -57.4905 | 63.327 | -59.6558 | -59.7656 | 55.394 | 4.216 | -16.8045 | -16.9922 | 63.3499 | -59.7244 | -0.11902 | -0.018311 | 2.0462 | -0.22888 | -7.9514 | -0.18768 | 0.004578 | 2.1652 | 42.7322 | 42.5446 | 114.9307 | 122.8638 | 2.0462 | 122.8867 | 63.7527 | -0.18768 | 122.8638 | 2.0462 | 63.7527 | 114.9307 | 122.8867 | -123.0011 | -123.0698
1301.3438 | 123.0515 | -59.5276 | 63.3179 | -0.11856 | 0.02606 | 0.01872 | 0.015778 | 0.062034 | -0.00042929 | 0.080572 | -57.4539 | 63.3362 | -59.642 | -59.7015 | 55.426 | 4.1885 | -16.983 | -17.0654 | 63.3316 | -59.7336 | -0.11444 | 0.018311 | 2.0737 | -0.17395 | -7.8918 | -0.20599 | 0.013733 | 2.1881 | 42.5446 | 42.4622 | 114.9536 | 122.8638 | 2.0737 | 122.8592 | 63.7161 | -0.20599 | 122.8638 | 2.0737 | 63.7161 | 114.9536 | 122.8592 | -122.9599 | -123.0515
1302.3438 | 123.0698 | -59.4864 | 63.327 | -0.1796 | 0.021574 | 0.013806 | 0.009156 | 0.060752 | -0.00085669 | 0.081854 | -57.4905 | 63.2767 | -59.6283 | -59.6786 | 55.4581 | 4.1519 | -17.0197 | -16.9785 | 63.3408 | -59.6741 | -0.14191 | -0.050354 | 1.9958 | -0.19226 | -7.869 | -0.18768 | 0.013733 | 2.1378 | 42.4667 | 42.5079 | 114.9445 | 122.7631 | 1.9958 | 122.8271 | 63.6383 | -0.18768 | 122.7631 | 1.9958 | 63.6383 | 114.9445 | 122.8271 | -122.9553 | -123.0011
1303.3438 | 123.0194 | -59.5001 | 63.3362 | -0.1796 | 0.022856 | 0.018079 | 0.010224 | 0.057762 | 0.00042511 | 0.081213 | -57.4814 | 63.3041 | -59.6512 | -59.7336 | 55.4077 | 4.01 | -16.9464 | -17.0242 | 63.3362 | -59.7107 | -0.15106 | -0.032044 | 2.0187 | -0.23346 | -7.9285 | -0.21057 | 0 | 2.1698 | 42.5537 | 42.4759 | 114.9078 | 122.8043 | 2.0187 | 122.8363 | 63.5101 | -0.21057 | 122.8043 | 2.0187 | 63.5101 | 114.9078 | 122.8363 | -122.9874 | -123.0469
1304.3438 | 123.0789 | -59.4681 | 63.327 | -0.11856 | 0.022215 | 0.012525 | 0.010438 | 0.058189 | -0.00042929 | 0.080572 | -57.4265 | 63.2355 | -59.6375 | -59.6329 | 55.4993 | 4.2435 | -17.0792 | -16.9052 | 63.2996 | -59.6695 | -0.16937 | -0.091552 | 2.0416 | -0.16479 | -7.8278 | -0.20142 | -0.027465 | 2.211 | 42.3889 | 42.5629 | 114.9673 | 122.7036 | 2.0416 | 122.7676 | 63.7115 | -0.20142 | 122.7036 | 2.0416 | 63.7115 | 114.9673 | 122.7676 | -122.9645 | -122.9965
1305.3438 | 123.024 | -59.5047 | 63.3545 | -0.15671 | 0.023496 | 0.012311 | 0.016633 | 0.060325 | -0.0027793 | 0.080572 | -57.5043 | 63.3591 | -59.6466 | -59.7427 | 55.394 | 4.1061 | -16.7953 | -16.9281 | 63.3545 | -59.7244 | -0.14191 | 0.004578 | 2.0004 | -0.23804 | -7.9605 | -0.21973 | 0 | 2.1423 | 42.7094 | 42.5766 | 114.8987 | 122.8638 | 2.0004 | 122.8592 | 63.6108 | -0.21973 | 122.8638 | 2.0004 | 63.6108 | 114.8987 | 122.8592 | -123.0011 | -123.0789
1306.3438 | 122.9828 | -59.5413 | 63.3362 | 0.026398 | 0.023283 | 0.016584 | 0.018555 | 0.062889 | -0.00021569 | 0.082495 | -57.3212 | 63.3408 | -59.6649 | -59.7977 | 55.3253 | 4.0878 | -16.9281 | -17.0792 | 63.327 | -59.729 | -0.1236 | 0.004577 | 2.2202 | -0.25635 | -8.0109 | -0.18768 | -0.009156 | 2.3438 | 42.6132 | 42.4622 | 114.8666 | 122.8821 | 2.2202 | 122.8683 | 63.6292 | -0.18768 | 122.8821 | 2.2202 | 63.6292 | 114.8666 | 122.8683 | -123.0011 | -123.0652
1307.3438 | 123.1293 | -59.4635 | 63.3362 | -0.088043 | 0.022428 | 0.014234 | 0.0080878 | 0.059257 | 0.00042511 | 0.08164 | -57.4768 | 63.2584 | -59.6375 | -59.6649 | 55.481 | 4.2526 | -17.038 | -16.8777 | 63.2858 | -59.6695 | -0.17395 | -0.07782 | 1.9867 | -0.20142 | -7.8552 | -0.20599 | -0.050354 | 2.1606 | 42.4255 | 42.5858 | 114.9445 | 122.7219 | 1.9867 | 122.7493 | 63.7161 | -0.20599 | 122.7219 | 1.9867 | 63.7161 | 114.9445 | 122.7493 | -122.9736 | -123.0057
1308.3438 | 123.1338 | -59.4589 | 63.3224 | -0.027008 | 0.023283 | 0.01167 | 0.01236 | 0.05648 | -0.0012839 | 0.080359 | -57.4585 | 63.2401 | -59.6237 | -59.6237 | 55.5038 | 4.216 | -17.0288 | -16.8411 | 63.2904 | -59.6329 | -0.16479 | -0.082398 | 2.0004 | -0.16479 | -7.8186 | -0.17395 | -0.032044 | 2.1652 | 42.4301 | 42.6178 | 114.9628 | 122.699 | 2.0004 | 122.7493 | 63.6749 | -0.17395 | 122.699 | 2.0004 | 63.6749 | 114.9628 | 122.7493 | -122.9462 | -122.9553
1309.3438 | 123.111 | -59.4589 | 63.3087 | -0.16434 | 0.022001 | 0.016156 | 0.01471 | 0.058189 | -0.0036337 | 0.082708 | -57.4127 | 63.2446 | -59.6375 | -59.6329 | 55.4855 | 4.184 | -16.9418 | -16.8686 | 63.3133 | -59.6329 | -0.17853 | -0.064087 | 2.0462 | -0.17395 | -7.8232 | -0.17395 | 0.004577 | 2.2247 | 42.5171 | 42.5903 | 114.9445 | 122.7036 | 2.0462 | 122.7722 | 63.6429 | -0.17395 | 122.7036 | 2.0462 | 63.6429 | 114.9445 | 122.7722 | -122.9462 | -122.9416
1310.3438 | 123.0423 | -59.4452 | 63.3362 | -0.19485 | 0.022642 | 0.013593 | 0.013428 | 0.057975 | -0.0023519 | 0.079718 | -57.431 | 63.2675 | -59.6329 | -59.6512 | 55.4581 | 4.1428 | -16.9006 | -16.8686 | 63.3316 | -59.6695 | -0.18768 | -0.068665 | 2.0142 | -0.20599 | -7.8781 | -0.22431 | -0.004578 | 2.2018 | 42.5446 | 42.5766 | 114.9033 | 122.7127 | 2.0142 | 122.7768 | 63.588 | -0.22431 | 122.7127 | 2.0142 | 63.588 | 114.9033 | 122.7768 | -122.9691 | -123.0057
1311.3438 | 123.024 | -59.4635 | 63.3362 | -0.18723 | 0.021787 | 0.012311 | 0.013001 | 0.058616 | -0.0025657 | 0.080359 | -57.4585 | 63.2904 | -59.6375 | -59.6878 | 55.4398 | 4.1245 | -16.7725 | -16.8045 | 63.3408 | -59.6878 | -0.17395 | -0.045777 | 2.005 | -0.2243 | -7.8964 | -0.2243 | 0.004577 | 2.179 | 42.691 | 42.659 | 114.9033 | 122.7539 | 2.005 | 122.8043 | 63.588 | -0.2243 | 122.7539 | 2.005 | 63.588 | 114.9033 | 122.8043 | -122.9736 | -123.024
1312.3438 | 123.0881 | -59.4543 | 63.3179 | 0.041657 | 0.022856 | 0.010816 | 0.012574 | 0.060539 | -0.0019247 | 0.082922 | -57.4951 | 63.2263 | -59.6512 | -59.6832 | 55.4398 | 4.129 | -16.8411 | -16.864 | 63.295 | -59.6878 | -0.19684 | -0.091553 | 1.9592 | -0.22888 | -7.8781 | -0.23346 | -0.022888 | 2.1561 | 42.6132 | 42.5903 | 114.8941 | 122.6807 | 1.9592 | 122.7493 | 63.5834 | -0.23346 | 122.6807 | 1.9592 | 63.5834 | 114.8941 | 122.7493 | -122.9691 | -123.0057
1313.3438 | 123.0835 | -59.4864 | 63.3362 | 0.29343 | 0.022856 | 0.017224 | 0.013001 | 0.057975 | -0.0025657 | 0.081213 | -57.5043 | 63.2309 | -59.6512 | -59.7061 | 55.4214 | 4.1702 | -16.8274 | -16.8732 | 63.2996 | -59.6786 | -0.16479 | -0.10529 | 1.9821 | -0.21973 | -7.9147 | -0.19226 | -0.036621 | 2.1469 | 42.659 | 42.6132 | 114.9078 | 122.7173 | 1.9821 | 122.7859 | 63.6566 | -0.19226 | 122.7173 | 1.9821 | 63.6566 | 114.9078 | 122.7859 | -122.9874 | -123.0148
1314.3438 | 123.0698 | -59.4772 | 63.3133 | 0.16373 | 0.026914 | 0.017011 | 0.012574 | 0.058189 | -0.0017111 | 0.08164 | -57.4631 | 63.2355 | -59.6512 | -59.6924 | 55.4398 | 4.2252 | -16.8137 | -16.7953 | 63.2675 | -59.6786 | -0.17395 | -0.077819 | 2.0142 | -0.21515 | -7.8735 | -0.20142 | -0.045776 | 2.1881 | 42.6636 | 42.6819 | 114.917 | 122.7127 | 2.0142 | 122.7448 | 63.7024 | -0.20142 | 122.7127 | 2.0142 | 63.7024 | 114.917 | 122.7448 | -122.9645 | -122.9919
1315.3438 | 123.0606 | -59.4727 | 63.3179 | 1.6209 | 0.023283 | 0.01167 | 0.012787 | 0.056907 | -0.00085669 | 0.082068 | -57.4677 | 63.2401 | -59.6512 | -59.7427 | 55.4123 | 4.1702 | -16.7038 | -16.7816 | 63.2538 | -59.6878 | -0.17853 | -0.07782 | 2.005 | -0.27008 | -7.9056 | -0.21515 | -0.064087 | 2.1835 | 42.7689 | 42.691 | 114.8849 | 122.7127 | 2.005 | 122.7264 | 63.6429 | -0.21515 | 122.7127 | 2.005 | 63.6429 | 114.8849 | 122.7264 | -122.9691 | -123.0057
1316.3438 | 122.9828 | -59.491 | 63.3728 | -0.16434 | 0.023924 | 0.017865 | 0.018342 | 0.058402 | -0.0029929 | 0.080786 | -57.5089 | 63.3499 | -59.6283 | -59.7015 | 55.4031 | 4.1336 | -16.4795 | -16.7725 | 63.327 | -59.7382 | -0.13733 | -0.022888 | 1.9821 | -0.21057 | -7.9697 | -0.24719 | -0.045777 | 2.1194 | 43.0115 | 42.7185 | 114.8941 | 122.8409 | 1.9821 | 122.818 | 63.6246 | -0.24719 | 122.8409 | 1.9821 | 63.6246 | 114.8941 | 122.818 | -123.0011 | -123.111
1317.3438 | 123.143 | -59.4635 | 63.3316 | -0.1033 | 0.022428 | 0.012952 | 0.012147 | 0.05883 | 0.00042511 | 0.083136 | -57.4402 | 63.2538 | -59.6329 | -59.6329 | 55.4993 | 4.184 | -16.7175 | -16.6168 | 63.3133 | -59.6329 | -0.16937 | -0.07782 | 2.0233 | -0.16937 | -7.8323 | -0.16937 | -0.018311 | 2.1927 | 42.746 | 42.8467 | 114.9628 | 122.7173 | 2.0233 | 122.7768 | 63.6475 | -0.16937 | 122.7173 | 2.0233 | 63.6475 | 114.9628 | 122.7768 | -122.9645 | -122.9645
1318.3438 | 123.0652 | -59.4818 | 63.3133 | 0.1561 | 0.024778 | 0.017438 | 0.013642 | 0.058402 | -0.0032065 | 0.081 | -57.4905 | 63.2126 | -59.6603 | -59.697 | 55.4031 | 4.1382 | -16.7496 | -16.7908 | 63.2812 | -59.6786 | -0.17853 | -0.10071 | 1.9913 | -0.21515 | -7.9102 | -0.19684 | -0.032043 | 2.1698 | 42.7322 | 42.691 | 114.8849 | 122.6944 | 1.9913 | 122.7631 | 63.62 | -0.19684 | 122.6944 | 1.9913 | 63.62 | 114.8849 | 122.7631 | -122.9736 | -122.9919
1319.3438 | 123.0423 | -59.4864 | 63.3545 | 0.10269 | 0.02606 | 0.015302 | 0.020692 | 0.05883 | -0.0017111 | 0.081427 | -57.399 | 63.3591 | -59.6146 | -59.642 | 55.4443 | 4.0558 | -16.6855 | -16.7313 | 63.327 | -59.7107 | -0.12817 | 0.004578 | 2.0874 | -0.15564 | -7.9102 | -0.2243 | -0.027466 | 2.2156 | 42.8009 | 42.7551 | 114.9307 | 122.8455 | 2.0874 | 122.8134 | 63.5422 | -0.2243 | 122.8455 | 2.0874 | 63.5422 | 114.9307 | 122.8134 | -122.9691 | -123.0652
1320.3438 | 123.0743 | -59.4864 | 63.295 | 0.17136 | 0.02136 | 0.013806 | 0.010865 | 0.060539 | -0.00085669 | 0.081854 | -57.4677 | 63.2355 | -59.6191 | -59.6786 | 55.4352 | 4.0512 | -16.6946 | -16.6901 | 63.2858 | -59.6603 | -0.13275 | -0.059509 | 2.0187 | -0.19226 | -7.8598 | -0.17395 | -0.009155 | 2.1515 | 42.7917 | 42.7963 | 114.9216 | 122.7219 | 2.0187 | 122.7722 | 63.5376 | -0.17395 | 122.7219 | 2.0187 | 63.5376 | 114.9216 | 122.7722 | -122.9141 | -122.9553
1321.3438 | 123.1064 | -59.4498 | 63.3408 | -0.11093 | 0.024351 | 0.015729 | 0.01236 | 0.056907 | 0.0010659 | 0.081427 | -57.4173 | 63.2812 | -59.6146 | -59.6008 | 55.5222 | 4.1153 | -16.6534 | -16.6031 | 63.3133 | -59.6512 | -0.16479 | -0.059509 | 2.0325 | -0.15106 | -7.8186 | -0.20142 | -0.027466 | 2.1973 | 42.7963 | 42.8467 | 114.9719 | 122.731 | 2.0325 | 122.7631 | 63.5651 | -0.20142 | 122.731 | 2.0325 | 63.5651 | 114.9719 | 122.7631 | -122.9553 | -122.9919
1322.3438 | 123.1155 | -59.4543 | 63.2996 | 0.19424 | 0.025205 | 0.015515 | 0.016205 | 0.059684 | -0.0017111 | 0.080145 | -57.4448 | 63.2492 | -59.6329 | -59.642 | 55.4855 | 4.0695 | -16.8182 | -16.6672 | 63.2812 | -59.6832 | -0.17853 | -0.050354 | 2.0096 | -0.18768 | -7.814 | -0.22888 | -0.018311 | 2.1881 | 42.6361 | 42.7872 | 114.9399 | 122.7036 | 2.0096 | 122.7356 | 63.5239 | -0.22888 | 122.7036 | 2.0096 | 63.5239 | 114.9399 | 122.7356 | -122.9324 | -122.9828
1323.3438 | 123.024 | -59.5184 | 63.3545 | 0.14847 | 0.026487 | 0.015302 | 0.014924 | 0.060539 | -2.092e-06 | 0.080145 | -57.3532 | 63.3591 | -59.6786 | -59.6558 | 55.3848 | 3.9642 | -16.539 | -16.8823 | 63.3179 | -59.7427 | -0.16022 | 0.004578 | 2.1652 | -0.13733 | -7.9697 | -0.2243 | -0.036621 | 2.3254 | 42.9794 | 42.6361 | 114.9033 | 122.8775 | 2.1652 | 122.8363 | 63.4827 | -0.2243 | 122.8775 | 2.1652 | 63.4827 | 114.9033 | 122.8363 | -123.0331 | -123.0972
1324.3438 | 123.0331 | -59.4818 | 63.3316 | 0.2095 | 0.025633 | 0.018079 | 0.016419 | 0.060111 | 0.00042511 | 0.082495 | -57.518 | 63.3499 | -59.6512 | -59.7015 | 55.394 | 3.9413 | -16.8457 | -16.9464 | 63.2904 | -59.7153 | -0.16937 | 0.018311 | 1.9638 | -0.21973 | -7.9376 | -0.23346 | -0.041199 | 2.1332 | 42.6361 | 42.5354 | 114.8758 | 122.8317 | 1.9638 | 122.7722 | 63.4232 | -0.23346 | 122.8317 | 1.9638 | 63.4232 | 114.8758 | 122.7722 | -122.9828 | -123.0469
1325.3438 | 123.0927 | -59.4864 | 63.3133 | 0.18662 | 0.022642 | 0.015088 | 0.011506 | 0.057975 | 0.00063871 | 0.080359 | -57.4631 | 63.2767 | -59.642 | -59.6558 | 55.4718 | 4.1016 | -16.7953 | -16.6763 | 63.2675 | -59.6741 | -0.15564 | -0.036621 | 2.0233 | -0.16937 | -7.8415 | -0.18768 | -0.045776 | 2.179 | 42.691 | 42.8101 | 114.9582 | 122.7631 | 2.0233 | 122.7539 | 63.588 | -0.18768 | 122.7631 | 2.0233 | 63.588 | 114.9582 | 122.7539 | -122.9553 | -122.9874
1326.3438 | 122.9599 | -59.4864 | 63.3408 | 0.018768 | 0.02606 | 0.020215 | 0.017274 | 0.062248 | 0.00042511 | 0.083563 | -57.4585 | 63.3682 | -59.642 | -59.7015 | 55.394 | 4.0512 | -16.539 | -16.7221 | 63.2584 | -59.7427 | -0.15564 | 0.027466 | 2.0279 | -0.21515 | -7.9468 | -0.25635 | -0.082397 | 2.1835 | 42.9474 | 42.7643 | 114.8804 | 122.8546 | 2.0279 | 122.7448 | 63.5376 | -0.25635 | 122.8546 | 2.0279 | 63.5376 | 114.8804 | 122.7448 | -122.9828 | -123.0835
1327.3438 | 122.9965 | -59.491 | 63.3636 | 0.026398 | 0.024137 | 0.015943 | 0.018769 | 0.06118 | -0.00085669 | 0.082068 | -57.4905 | 63.3865 | -59.6283 | -59.6695 | 55.426 | 3.9688 | -16.6306 | -16.7358 | 63.3041 | -59.7153 | -0.13733 | 0.022889 | 2.0004 | -0.17853 | -7.9376 | -0.2243 | -0.059509 | 2.1378 | 42.8604 | 42.7551 | 114.917 | 122.8775 | 2.0004 | 122.7951 | 63.4598 | -0.2243 | 122.8775 | 2.0004 | 63.4598 | 114.917 | 122.7951 | -122.9919 | -123.0789
1328.3438 | 122.9782 | -59.5001 | 63.3774 | 0.064545 | 0.026274 | 0.015943 | 0.015992 | 0.06118 | 0.00021151 | 0.081213 | -57.4814 | 63.3865 | -59.6603 | -59.7107 | 55.4169 | 3.9825 | -16.6122 | -16.7953 | 63.3408 | -59.7061 | -0.16022 | 0.009156 | 2.0187 | -0.21057 | -7.9605 | -0.20599 | -0.036621 | 2.179 | 42.8879 | 42.7048 | 114.917 | 122.8867 | 2.0187 | 122.8409 | 63.4827 | -0.20599 | 122.8867 | 2.0187 | 63.4827 | 114.917 | 122.8409 | -123.0377 | -123.0835
1329.3438 | 123.0057 | -59.5001 | 63.3591 | 0.57571 | 0.026914 | 0.012311 | 0.014924 | 0.06182 | -2.092e-06 | 0.083349 | -57.4722 | 63.3957 | -59.6375 | -59.7519 | 55.3711 | 4.0146 | -16.5802 | -16.7999 | 63.3362 | -59.7336 | -0.13733 | 0.036621 | 2.0279 | -0.25177 | -7.988 | -0.23346 | -0.022888 | 2.1652 | 42.9199 | 42.7002 | 114.8712 | 122.8958 | 2.0279 | 122.8363 | 63.5147 | -0.23346 | 122.8958 | 2.0279 | 63.5147 | 114.8712 | 122.8363 | -122.9965 | -123.0927
1330.3438 | 123.056 | -59.4589 | 63.327 | 0.17899 | 0.022856 | 0.015729 | 0.0053106 | 0.062461 | 0.00021151 | 0.082922 | -57.5409 | 63.2721 | -59.6375 | -59.7061 | 55.4672 | 4.1061 | -16.7221 | -16.713 | 63.2996 | -59.6695 | -0.17853 | -0.054931 | 1.918 | -0.24719 | -7.8598 | -0.21057 | -0.027465 | 2.0966 | 42.7368 | 42.746 | 114.9261 | 122.731 | 1.918 | 122.7585 | 63.5651 | -0.21057 | 122.731 | 1.918 | 63.5651 | 114.9261 | 122.7585 | -122.9645 | -122.9965
1331.3438 | 123.0606 | -59.4635 | 63.382 | 2.4449 | 0.02136 | 0.017652 | 0.019623 | 0.060539 | -0.0012839 | 0.081854 | -57.2617 | 63.3865 | -59.6054 | -59.6375 | 55.481 | 4.0054 | -16.6718 | -16.7221 | 63.3408 | -59.7198 | -0.14191 | 0.004578 | 2.2018 | -0.17395 | -7.901 | -0.25635 | -0.041199 | 2.3438 | 42.7917 | 42.7414 | 114.9445 | 122.85 | 2.2018 | 122.8043 | 63.4689 | -0.25635 | 122.85 | 2.2018 | 63.4689 | 114.9445 | 122.8043 | -122.9874 | -123.1018
1332.3438 | 123.0377 | -59.4543 | 63.3957 | -0.19485 | 0.021787 | 0.013806 | 0.013856 | 0.059684 | 0.00042511 | 0.082281 | -57.5134 | 63.3682 | -59.6283 | -59.697 | 55.4169 | 3.8589 | -16.1636 | -16.7999 | 63.3911 | -59.6741 | -0.17395 | -0.027466 | 1.9409 | -0.24261 | -7.9788 | -0.21973 | -0.004578 | 2.1149 | 43.2907 | 42.6544 | 114.8712 | 122.8226 | 1.9409 | 122.8455 | 63.3133 | -0.21973 | 122.8226 | 1.9409 | 63.3133 | 114.8712 | 122.8455 | -123.024 | -123.0698
1333.3438 | 122.9736 | -59.491 | 63.3682 | 0.034027 | 0.026914 | 0.01637 | 0.017274 | 0.063957 | 0.00021151 | 0.080145 | -57.5043 | 63.3865 | -59.6375 | -59.7656 | 55.3619 | 3.8773 | -16.5344 | -16.8228 | 63.3408 | -59.7061 | -0.14648 | 0.018311 | 1.9867 | -0.27466 | -8.0063 | -0.21515 | -0.027466 | 2.1332 | 42.9565 | 42.6682 | 114.8529 | 122.8775 | 1.9867 | 122.8317 | 63.3682 | -0.21515 | 122.8775 | 1.9867 | 63.3682 | 114.8529 | 122.8317 | -123.0057 | -123.0743
1334.3438 | 123.024 | -59.4543 | 63.3636 | 0.026398 | 0.022428 | 0.018506 | 0.016633 | 0.059684 | 0.0012795 | 0.08164 | -57.4448 | 63.4003 | -59.6237 | -59.6649 | 55.4398 | 3.8773 | -16.6031 | -16.7496 | 63.3545 | -59.7061 | -0.16937 | 0.036622 | 2.0096 | -0.21057 | -7.9239 | -0.25177 | -0.009155 | 2.179 | 42.8513 | 42.7048 | 114.8941 | 122.8546 | 2.0096 | 122.8088 | 63.3316 | -0.25177 | 122.8546 | 2.0096 | 63.3316 | 114.8941 | 122.8088 | -122.9874 | -123.0698
1335.3438 | 122.85 | -59.5139 | 63.3453 | 0.19424 | 0.027769 | 0.017865 | 0.015992 | 0.060966 | -0.0014975 | 0.080359 | -57.4997 | 63.3865 | -59.6466 | -59.7473 | 55.3711 | 3.8498 | -16.6122 | -16.7953 | 63.3591 | -59.7198 | -0.13275 | 0.041199 | 2.0142 | -0.23346 | -7.9742 | -0.20599 | 0.013733 | 2.1469 | 42.9016 | 42.7185 | 114.8849 | 122.9004 | 2.0142 | 122.8729 | 63.3636 | -0.20599 | 122.9004 | 2.0142 | 63.3636 | 114.8849 | 122.8729 | -122.9919 | -123.0652
1336.3438 | 123.0469 | -59.4681 | 63.3774 | -0.13382 | 0.025633 | 0.019788 | 0.016846 | 0.059257 | 0.0019205 | 0.082495 | -57.605 | 63.3957 | -59.6283 | -59.6283 | 55.4901 | 3.9093 | -16.6397 | -16.6855 | 63.3636 | -59.6649 | -0.16022 | 0.018311 | 1.8631 | -0.16022 | -7.8873 | -0.19684 | -0.013733 | 2.0233 | 42.8284 | 42.7826 | 114.9582 | 122.8638 | 1.8631 | 122.8317 | 63.3774 | -0.19684 | 122.8638 | 1.8631 | 63.3774 | 114.9582 | 122.8317 | -123.0057 | -123.0423
1337.3438 | 123.0286 | -59.4543 | 63.3911 | -0.0041198 | 0.02606 | 0.018933 | 0.016846 | 0.062034 | 0.00042511 | 0.081 | -57.4493 | 63.3957 | -59.6191 | -59.6466 | 55.4626 | 3.891 | -16.6443 | -16.7313 | 63.3545 | -59.7061 | -0.16479 | 0.004578 | 2.005 | -0.19226 | -7.9285 | -0.25177 | -0.036621 | 2.1698 | 42.8101 | 42.7231 | 114.917 | 122.85 | 2.005 | 122.8088 | 63.3453 | -0.25177 | 122.85 | 2.005 | 63.3453 | 114.917 | 122.8088 | -123.0103 | -123.0972
1338.3438 | 122.9828 | -59.4818 | 63.4003 | 0.14084 | 0.024778 | 0.015729 | 0.015137 | 0.060966 | 0.0012795 | 0.083777 | -57.5546 | 63.4277 | -59.6466 | -59.7519 | 55.3986 | 3.8269 | -16.6443 | -16.8503 | 63.3316 | -59.7198 | -0.16479 | 0.027465 | 1.9272 | -0.27008 | -8.0017 | -0.23804 | -0.068665 | 2.092 | 42.8375 | 42.6315 | 114.8804 | 122.9095 | 1.9272 | 122.8134 | 63.3087 | -0.23804 | 122.9095 | 1.9272 | 63.3087 | 114.8804 | 122.8134 | -123.0469 | -123.1201
1339.3438 | 123.0469 | -59.4406 | 63.4094 | -0.14145 | 0.024137 | 0.01872 | 0.013856 | 0.059043 | 0.0014933 | 0.082708 | -57.486 | 63.446 | -59.5779 | -59.6741 | 55.4535 | 3.8315 | -16.6534 | -16.7633 | 63.3774 | -59.6924 | -0.13733 | 0.036621 | 1.9547 | -0.23346 | -7.9559 | -0.25177 | -0.032044 | 2.092 | 42.7872 | 42.6773 | 114.8941 | 122.8867 | 1.9547 | 122.818 | 63.2721 | -0.25177 | 122.8867 | 1.9547 | 63.2721 | 114.8941 | 122.818 | -122.9874 | -123.1018
1340.3438 | 122.9599 | -59.4772 | 63.4048 | 0.12558 | 0.025205 | 0.01637 | 0.013642 | 0.062248 | 0.0014933 | 0.085058 | -57.518 | 63.4232 | -59.6329 | -60.1044 | 55.4718 | 4.1473 | -16.7725 | -16.8091 | 63.3774 | -59.6603 | -0.15564 | 0.018311 | 1.9592 | -0.62714 | -7.933 | -0.1831 | -0.027466 | 2.1149 | 42.7048 | 42.6682 | 114.949 | 122.9004 | 1.9592 | 122.8546 | 63.6246 | -0.1831 | 122.9004 | 1.9592 | 63.6246 | 114.949 | 122.8546 | -123.0377 | -123.0652
1341.3438 | 123.0194 | -59.4269 | 63.4232 | -0.15671 | 0.023924 | 0.01637 | 0.015351 | 0.060111 | -0.0012839 | 0.082068 | -57.431 | 63.4644 | -59.5963 | -59.6603 | 55.481 | 3.8681 | -16.6168 | -16.7221 | 63.3865 | -59.6649 | -0.16937 | 0.041198 | 1.9958 | -0.23346 | -7.9422 | -0.23804 | -0.036621 | 2.1652 | 42.8101 | 42.7048 | 114.9078 | 122.8912 | 1.9958 | 122.8134 | 63.295 | -0.23804 | 122.8912 | 1.9958 | 63.295 | 114.9078 | 122.8134 | -123.0194 | -123.0881
1342.3438 | 123.024 | -59.4452 | 63.414 | 0.011139 | 0.026701 | 0.014447 | 0.015351 | 0.062034 | -0.00064309 | 0.082068 | -57.4219 | 63.4277 | -59.5688 | -59.642 | 55.4306 | 3.8956 | -16.5436 | -16.6992 | 63.3728 | -59.6603 | -0.1236 | 0.013733 | 2.0233 | -0.19684 | -7.9834 | -0.21515 | -0.041198 | 2.1469 | 42.9016 | 42.746 | 114.8758 | 122.8729 | 2.0233 | 122.818 | 63.3408 | -0.21515 | 122.8729 | 2.0233 | 63.3408 | 114.8758 | 122.818 | -122.9828 | -123.0743
1343.3438 | 123.0194 | -59.4681 | 63.4415 | -0.64499 | 0.025419 | 0.013806 | 0.012574 | 0.059898 | 0.0010659 | 0.081854 | -57.5729 | 63.4094 | -59.6054 | -59.7015 | 55.4443 | 3.8315 | -16.4154 | -16.6031 | 63.3865 | -59.6466 | -0.13733 | -0.032043 | 1.8951 | -0.23346 | -7.9971 | -0.17853 | -0.054931 | 2.0325 | 43.0527 | 42.865 | 114.9124 | 122.8775 | 1.8951 | 122.8546 | 63.2996 | -0.17853 | 122.8775 | 1.8951 | 63.2996 | 114.9124 | 122.8546 | -123.0469 | -123.0881
1344.3438 | 123.0377 | -59.4269 | 63.4003 | -0.17197 | 0.024137 | 0.014875 | 0.013215 | 0.059898 | 0.00042511 | 0.082068 | -57.4585 | 63.4506 | -59.5963 | -59.6558 | 55.4718 | 3.9093 | -16.4932 | -16.5573 | 63.4094 | -59.6603 | -0.16937 | 0.050354 | 1.9684 | -0.22888 | -7.9285 | -0.23346 | 0.009155 | 2.1378 | 42.9337 | 42.8696 | 114.8987 | 122.8775 | 1.9684 | 122.8363 | 63.3362 | -0.23346 | 122.8775 | 1.9684 | 63.3362 | 114.8987 | 122.8363 | -122.9965 | -123.0606
1345.3438 | 123.0606 | -59.4543 | 63.4003 | 0.026398 | 0.02841 | 0.017438 | 0.016205 | 0.060325 | -0.0017111 | 0.080572 | -57.431 | 63.4094 | -59.5825 | -59.6466 | 55.4672 | 3.8177 | -16.5527 | -16.6855 | 63.3957 | -59.6603 | -0.12817 | 0.009155 | 2.0233 | -0.19226 | -7.933 | -0.20599 | -0.004578 | 2.1515 | 42.9016 | 42.7689 | 114.9216 | 122.8638 | 2.0233 | 122.85 | 63.2721 | -0.20599 | 122.8638 | 2.0233 | 63.2721 | 114.9216 | 122.85 | -122.9828 | -123.0606
1346.3438 | 123.0606 | -59.4315 | 63.4003 | -0.22537 | 0.023496 | 0.016584 | 0.018555 | 0.062461 | -0.0023519 | 0.082068 | -57.4219 | 63.4323 | -59.5734 | -59.6375 | 55.4764 | 3.7903 | -16.571 | -16.6855 | 63.4003 | -59.6558 | -0.14191 | 0.032043 | 2.0096 | -0.20599 | -7.9239 | -0.2243 | 0 | 2.1515 | 42.8604 | 42.746 | 114.9078 | 122.8638 | 2.0096 | 122.8317 | 63.2217 | -0.2243 | 122.8638 | 2.0096 | 63.2217 | 114.9078 | 122.8317 | -122.9736 | -123.056
1347.3438 | 123.024 | -59.4223 | 63.4094 | -0.19485 | 0.024137 | 0.014234 | 0.010224 | 0.059898 | -0.00042929 | 0.083777 | -57.5272 | 63.3911 | -59.6008 | -59.6878 | 55.4489 | 3.7308 | -16.0721 | -16.6672 | 63.4644 | -59.61 | -0.17853 | -0.018311 | 1.8951 | -0.2655 | -7.9605 | -0.18768 | 0.054931 | 2.0737 | 43.3502 | 42.7551 | 114.8712 | 122.8134 | 1.8951 | 122.8867 | 63.1531 | -0.18768 | 122.8134 | 1.8951 | 63.1531 | 114.8712 | 122.8867 | -123.0103 | -123.0194
1348.3438 | 123.0148 | -59.4177 | 63.4323 | -0.1796 | 0.023924 | 0.013379 | 0.011292 | 0.06118 | -0.00064309 | 0.081854 | -57.4768 | 63.3774 | -59.5825 | -59.642 | 55.4626 | 3.8406 | -16.4337 | -16.5527 | 63.4277 | -59.6283 | -0.1648 | -0.054932 | 1.9409 | -0.2243 | -7.9697 | -0.21057 | -0.004578 | 2.1057 | 42.984 | 42.865 | 114.8804 | 122.7951 | 1.9409 | 122.8455 | 63.2584 | -0.21057 | 122.7951 | 1.9409 | 63.2584 | 114.8804 | 122.8455 | -123.0148 | -123.0606
1349.3438 | 122.9736 | -59.436 | 63.4552 | -0.1796 | 0.024137 | 0.010816 | 0.016846 | 0.060539 | -0.0010703 | 0.080572 | -57.6096 | 63.4323 | -59.5734 | -59.729 | 55.4077 | 3.7903 | -16.4017 | -16.7038 | 63.4323 | -59.6237 | -0.13733 | -0.022888 | 1.8265 | -0.29297 | -8.0475 | -0.18768 | -0.022888 | 1.9638 | 43.0344 | 42.7322 | 114.8438 | 122.8683 | 1.8265 | 122.8683 | 63.2263 | -0.18768 | 122.8683 | 1.8265 | 63.2263 | 114.8438 | 122.8683 | -123.0286 | -123.0789
1350.3438 | 122.9874 | -59.4589 | 63.4048 | 0.064545 | 0.026274 | 0.016156 | 0.018128 | 0.061393 | -0.00064309 | 0.079931 | -57.4722 | 63.414 | -59.5871 | -59.6878 | 55.4031 | 3.7674 | -16.4612 | -16.6901 | 63.4232 | -59.6695 | -0.12817 | 0.009155 | 1.9867 | -0.22888 | -8.0017 | -0.21057 | 0.018311 | 2.1149 | 42.9977 | 42.7689 | 114.8621 | 122.8729 | 1.9867 | 122.8821 | 63.2263 | -0.21057 | 122.8729 | 1.9867 | 63.2263 | 114.8621 | 122.8821 | -122.9919 | -123.0743
1351.3438 | 123.0057 | -59.3994 | 63.4232 | -0.27115 | 0.02606 | 0.015943 | 0.011292 | 0.059471 | -0.0023519 | 0.082281 | -57.5134 | 63.4003 | -59.6008 | -59.6741 | 55.4352 | 3.685 | -16.3879 | -16.5894 | 63.4277 | -59.6558 | -0.20142 | -0.022888 | 1.886 | -0.27466 | -7.988 | -0.25635 | 0.004577 | 2.0874 | 43.0115 | 42.8101 | 114.8346 | 122.7997 | 1.886 | 122.8271 | 63.0844 | -0.25635 | 122.7997 | 1.886 | 63.0844 | 114.8346 | 122.8271 | -123.024 | -123.0789
1352.3438 | 123.0606 | -59.3903 | 63.4048 | -0.15671 | 0.022428 | 0.015302 | 0.011719 | 0.06118 | -0.0017111 | 0.082281 | -57.4539 | 63.3682 | -59.5825 | -59.6191 | 55.513 | 3.7949 | -16.452 | -16.5024 | 63.4277 | -59.61 | -0.19226 | -0.036621 | 1.9363 | -0.22888 | -7.8918 | -0.21973 | 0.022888 | 2.1286 | 42.9382 | 42.8879 | 114.9033 | 122.7585 | 1.9363 | 122.818 | 63.1851 | -0.21973 | 122.7585 | 1.9363 | 63.1851 | 114.9033 | 122.818 | -122.9874 | -123.0148
1353.3438 | 122.9828 | -59.4177 | 63.4277 | -0.26352 | 0.023069 | 0.012952 | 0.013001 | 0.059898 | 0.00021151 | 0.083349 | -57.4997 | 63.4048 | -59.5917 | -59.6603 | 55.4535 | 3.7308 | -16.4429 | -16.5298 | 63.4323 | -59.6237 | -0.17395 | -0.022888 | 1.918 | -0.24261 | -7.9742 | -0.20599 | 0.004578 | 2.092 | 42.9749 | 42.8879 | 114.8712 | 122.8226 | 1.918 | 122.85 | 63.1485 | -0.20599 | 122.8226 | 1.918 | 63.1485 | 114.8712 | 122.85 | -123.0194 | -123.0515
1354.3438 | 123.0148 | -59.3857 | 63.446 | -0.22537 | 0.021574 | 0.012952 | 0.014924 | 0.059257 | -0.0021383 | 0.078863 | -57.3532 | 63.4186 | -59.5688 | -59.6329 | 55.4306 | 3.6758 | -16.3651 | -16.5665 | 63.4644 | -59.6146 | -0.18311 | -0.027466 | 2.0325 | -0.24719 | -8.0154 | -0.22888 | 0.01831 | 2.2156 | 43.0206 | 42.8192 | 114.8163 | 122.8043 | 2.0325 | 122.85 | 63.0615 | -0.22888 | 122.8043 | 2.0325 | 63.0615 | 114.8163 | 122.85 | -123.0148 | -123.0606
1355.3438 | 123.0743 | -59.3903 | 63.3957 | -0.18723 | 0.022001 | 0.012738 | 0.011933 | 0.060111 | -0.0012839 | 0.082922 | -57.4219 | 63.3453 | -59.5596 | -59.5734 | 55.513 | 3.7399 | -16.4932 | -16.4841 | 63.4277 | -59.5917 | -0.16937 | -0.050354 | 1.9684 | -0.1831 | -7.8827 | -0.20142 | 0.032043 | 2.1378 | 42.897 | 42.9062 | 114.9033 | 122.7356 | 1.9684 | 122.818 | 63.1302 | -0.20142 | 122.7356 | 1.9684 | 63.1302 | 114.9033 | 122.818 | -122.9553 | -122.9874
1356.3438 | 123.0972 | -59.3628 | 63.4415 | -0.21774 | 0.023283 | 0.016797 | 0.011506 | 0.058616 | -0.0021383 | 0.081854 | -57.4081 | 63.3499 | -59.5505 | -59.5779 | 55.5817 | 3.8544 | -16.4978 | -16.42 | 63.4186 | -59.5459 | -0.18768 | -0.091552 | 1.9547 | -0.21515 | -7.8598 | -0.1831 | -0.022888 | 2.1423 | 42.865 | 42.9428 | 114.9445 | 122.7127 | 1.9547 | 122.7814 | 63.2172 | -0.1831 | 122.7127 | 1.9547 | 63.2172 | 114.9445 | 122.7814 | -122.9919 | -122.9874
1357.3438 | 123.0469 | -59.3811 | 63.4277 | -0.19485 | 0.023069 | 0.011243 | 0.012574 | 0.057762 | -0.0014975 | 0.081213 | -57.4173 | 63.3408 | -59.5505 | -59.6008 | 55.5176 | 3.7765 | -16.4978 | -16.4978 | 63.4003 | -59.5871 | -0.16937 | -0.086975 | 1.9638 | -0.21973 | -7.9102 | -0.20599 | -0.027465 | 2.1332 | 42.8833 | 42.8833 | 114.8987 | 122.7219 | 1.9638 | 122.7814 | 63.1577 | -0.20599 | 122.7219 | 1.9638 | 63.1577 | 114.8987 | 122.7814 | -122.9782 | -123.0148
1358.375 | 123.0515 | -59.3857 | 63.4186 | -0.17197 | 0.024137 | 0.013379 | 0.013428 | 0.059257 | -0.0019247 | 0.082068 | -57.4356 | 63.3591 | -59.5551 | -59.5963 | 55.5084 | 3.8223 | -16.3925 | -16.4566 | 63.4323 | -59.61 | -0.16937 | -0.059509 | 1.9501 | -0.21057 | -7.9102 | -0.2243 | 0.013733 | 2.1194 | 42.9932 | 42.9291 | 114.8941 | 122.7448 | 1.9501 | 122.818 | 63.208 | -0.2243 | 122.7448 | 1.9501 | 63.208 | 114.8941 | 122.818 | -122.9736 | -123.0286
1359.3438 | 123.0972 | -59.3628 | 63.3957 | -0.0041198 | 0.023283 | 0.010602 | 0.011079 | 0.058189 | -0.0012839 | 0.082281 | -57.4631 | 63.3224 | -59.5596 | -59.5963 | 55.5222 | 3.9413 | -16.4841 | -16.3834 | 63.3636 | -59.5734 | -0.19684 | -0.073242 | 1.8997 | -0.23346 | -7.8735 | -0.21057 | -0.032044 | 2.0966 | 42.8787 | 42.9794 | 114.8849 | 122.6852 | 1.8997 | 122.7264 | 63.3041 | -0.21057 | 122.6852 | 1.8997 | 63.3041 | 114.8849 | 122.7264 | -122.9553 | -122.9691
1360.3438 | 123.0927 | -59.3536 | 63.4415 | -0.17197 | 0.021787 | 0.015943 | 0.013856 | 0.05648 | -0.0034201 | 0.079931 | -57.4081 | 63.327 | -59.5322 | -59.5505 | 55.5634 | 3.8544 | -16.4474 | -16.3284 | 63.4094 | -59.5688 | -0.17853 | -0.11444 | 1.9455 | -0.19684 | -7.8781 | -0.21515 | -0.032043 | 2.124 | 42.9062 | 43.0252 | 114.917 | 122.6807 | 1.9455 | 122.7631 | 63.208 | -0.21515 | 122.6807 | 1.9455 | 63.208 | 114.917 | 122.7631 | -122.9736 | -123.0103
1361.3594 | 122.9782 | -59.4086 | 63.4735 | -0.18723 | 0.023283 | 0.015515 | 0.015992 | 0.057975 | -0.00064309 | 0.081427 | -57.4036 | 63.446 | -59.5276 | -59.6558 | 55.4901 | 3.7079 | -16.4062 | -16.4795 | 63.414 | -59.6512 | -0.11902 | -0.027466 | 2.005 | -0.24719 | -7.9834 | -0.24262 | -0.05951 | 2.124 | 43.0023 | 42.9291 | 114.8987 | 122.8546 | 2.005 | 122.8226 | 63.1165 | -0.24262 | 122.8546 | 2.005 | 63.1165 | 114.8987 | 122.8226 | -123.0011 | -123.1247
1362.3438 | 123.1201 | -59.3582 | 63.414 | -0.042267 | 0.022428 | 0.010388 | 0.01001 | 0.057762 | -0.0017111 | 0.082281 | -57.4402 | 63.3408 | -59.5505 | -59.5688 | 55.5542 | 3.804 | -16.5207 | -16.301 | 63.4094 | -59.6054 | -0.19226 | -0.073242 | 1.918 | -0.21057 | -7.8598 | -0.24719 | -0.004577 | 2.1103 | 42.8375 | 43.0573 | 114.9124 | 122.699 | 1.918 | 122.7676 | 63.1622 | -0.24719 | 122.699 | 1.918 | 63.1622 | 114.9124 | 122.7676 | -122.9645 | -123.0194
1363.3438 | 123.0652 | -59.404 | 63.414 | 0.14084 | 0.023069 | 0.012738 | 0.01236 | 0.056907 | -0.00042929 | 0.081 | -57.4539 | 63.2996 | -59.5459 | -59.61 | 55.481 | 3.7216 | -16.539 | -16.4291 | 63.3499 | -59.5963 | -0.14191 | -0.11444 | 1.9501 | -0.20599 | -7.933 | -0.19226 | -0.064086 | 2.092 | 42.865 | 42.9749 | 114.8849 | 122.7036 | 1.9501 | 122.7539 | 63.1256 | -0.19226 | 122.7036 | 1.9501 | 63.1256 | 114.8849 | 122.7539 | -122.9599 | -123.0103
1364.3438 | 123.0835 | -59.3857 | 63.3957 | 0.087433 | 0.023069 | 0.015729 | 0.012574 | 0.056266 | -0.0021383 | 0.076941 | -57.4722 | 63.3224 | -59.5459 | -59.4635 | 55.3619 | 3.4607 | -16.4658 | -16.4749 | 63.3179 | -59.61 | -0.16022 | -0.073242 | 1.9135 | -0.07782 | -8.0338 | -0.2243 | -0.07782 | 2.0737 | 42.9199 | 42.9108 | 114.7476 | 122.7081 | 1.9135 | 122.7036 | 62.8464 | -0.2243 | 122.7081 | 1.9135 | 62.8464 | 114.7476 | 122.7036 | -122.9416 | -123.0057
1365.3438 | 123.0743 | -59.3903 | 63.446 | -0.1796 | 0.022215 | 0.011457 | 0.016419 | 0.055839 | -0.00085669 | 0.082495 | -57.399 | 63.382 | -59.5367 | -59.5642 | 55.545 | 3.7216 | -16.3696 | -16.301 | 63.4048 | -59.5779 | -0.14648 | -0.064087 | 1.9913 | -0.17395 | -7.901 | -0.18768 | -0.041199 | 2.1378 | 43.0206 | 43.0893 | 114.9353 | 122.7722 | 1.9913 | 122.7951 | 63.1119 | -0.18768 | 122.7722 | 1.9913 | 63.1119 | 114.9353 | 122.7951 | -122.9828 | -123.024
1366.3438 | 123.0835 | -59.3445 | 63.446 | -0.17197 | 0.024778 | 0.017438 | 0.013642 | 0.057548 | -0.0036337 | 0.079718 | -57.3486 | 63.3499 | -59.5001 | -59.5367 | 55.5496 | 3.6987 | -16.4795 | -16.3376 | 63.4232 | -59.5917 | -0.15564 | -0.09613 | 1.9958 | -0.19226 | -7.8964 | -0.24719 | -0.022888 | 2.1515 | 42.865 | 43.0069 | 114.8941 | 122.6944 | 1.9958 | 122.7676 | 63.0432 | -0.24719 | 122.6944 | 1.9958 | 63.0432 | 114.8941 | 122.7676 | -122.9462 | -123.0377
1367.3438 | 123.0835 | -59.3948 | 63.4094 | 0.18662 | 0.024351 | 0.012311 | 0.013215 | 0.057334 | 0.0010659 | 0.080572 | -57.4265 | 63.3224 | -59.5688 | -59.5825 | 55.5222 | 3.6484 | -16.5207 | -16.301 | 63.3682 | -59.5963 | -0.17395 | -0.086975 | 1.9684 | -0.18768 | -7.8873 | -0.20142 | -0.041199 | 2.1423 | 42.8741 | 43.0939 | 114.917 | 122.7173 | 1.9684 | 122.7631 | 63.0432 | -0.20142 | 122.7173 | 1.9684 | 63.0432 | 114.917 | 122.7631 | -122.9782 | -123.0057
1368.3438 | 123.0881 | -59.3628 | 63.4048 | 0.049286 | 0.020719 | 0.012097 | 0.012147 | 0.05883 | -0.00021569 | 0.081854 | -57.486 | 63.3316 | -59.5642 | -59.5871 | 55.513 | 3.7308 | -16.3513 | -16.2643 | 63.3911 | -59.5871 | -0.20142 | -0.073242 | 1.8768 | -0.2243 | -7.8918 | -0.2243 | -0.013733 | 2.0782 | 43.0115 | 43.0984 | 114.8758 | 122.6944 | 1.8768 | 122.7539 | 63.0936 | -0.2243 | 122.6944 | 1.8768 | 63.0936 | 114.8758 | 122.7539 | -122.9691 | -122.9919
1369.3438 | 123.0652 | -59.3582 | 63.4048 | 0.18662 | 0.022428 | 0.015088 | 0.013001 | 0.059898 | -0.0040609 | 0.083349 | -57.4265 | 63.327 | -59.5596 | -59.5688 | 55.513 | 3.7811 | -16.4886 | -16.3651 | 63.3362 | -59.5871 | -0.20142 | -0.07782 | 1.9318 | -0.21057 | -7.8918 | -0.22888 | -0.068664 | 2.1332 | 42.8696 | 42.9932 | 114.8712 | 122.6852 | 1.9318 | 122.6944 | 63.1393 | -0.22888 | 122.6852 | 1.9318 | 63.1393 | 114.8712 | 122.6944 | -122.9645 | -122.9919
1370.3438 | 123.1522 | -59.3582 | 63.4415 | -0.011749 | 0.024778 | 0.0093204 | 0.012574 | 0.056907 | -0.0019247 | 0.080145 | -57.3944 | 63.382 | -59.5139 | -59.5184 | 55.5725 | 3.8223 | -16.4246 | -16.2689 | 63.3865 | -59.5871 | -0.15564 | -0.059509 | 1.9638 | -0.16022 | -7.869 | -0.22888 | -0.054931 | 2.1194 | 42.9337 | 43.0893 | 114.9307 | 122.7402 | 1.9638 | 122.7448 | 63.1805 | -0.22888 | 122.7402 | 1.9638 | 63.1805 | 114.9307 | 122.7448 | -122.9553 | -123.0286
1371.3438 | 123.0881 | -59.3674 | 63.4323 | 0.049286 | 0.023496 | 0.011029 | 0.013001 | 0.057762 | -2.092e-06 | 0.081213 | -57.486 | 63.3453 | -59.5459 | -59.5963 | 55.4855 | 3.8635 | -16.3467 | -16.3239 | 63.3728 | -59.5871 | -0.17853 | -0.086975 | 1.8814 | -0.22888 | -7.9468 | -0.21973 | -0.059509 | 2.0599 | 43.0206 | 43.0435 | 114.8529 | 122.7127 | 1.8814 | 122.7402 | 63.2309 | -0.21973 | 122.7127 | 1.8814 | 63.2309 | 114.8529 | 122.7402 | -122.9782 | -123.0194
1372.3438 | 123.0927 | -59.3765 | 63.4048 | 0.19424 | 0.022215 | 0.011029 | 0.015137 | 0.059898 | -0.0019247 | 0.080786 | -57.4173 | 63.3408 | -59.5413 | -59.5459 | 55.5176 | 3.8406 | -16.4154 | -16.3101 | 63.3362 | -59.6008 | -0.1648 | -0.064087 | 1.9592 | -0.16937 | -7.8873 | -0.2243 | -0.068664 | 2.124 | 42.9611 | 43.0664 | 114.8941 | 122.7173 | 1.9592 | 122.7127 | 63.2172 | -0.2243 | 122.7173 | 1.9592 | 63.2172 | 114.8941 | 122.7127 | -122.9462 | -123.0057
1373.3438 | 123.0606 | -59.3765 | 63.4094 | 0.17899 | 0.023283 | 0.013806 | 0.013428 | 0.059471 | 0.00063871 | 0.082068 | -57.4173 | 63.3453 | -59.5413 | -59.5734 | 55.5176 | 3.8177 | -16.42 | -16.2552 | 63.3499 | -59.6146 | -0.1648 | -0.064087 | 1.9592 | -0.19684 | -7.8918 | -0.23804 | -0.059509 | 2.124 | 42.9565 | 43.1213 | 114.8941 | 122.7219 | 1.9592 | 122.7264 | 63.1943 | -0.23804 | 122.7219 | 1.9592 | 63.1943 | 114.8941 | 122.7264 | -122.9507 | -123.024
1374.3438 | 123.0972 | -59.3948 | 63.4003 | 0.20187 | 0.024565 | 0.013166 | 0.013428 | 0.058402 | -0.0014975 | 0.081 | -57.4402 | 63.3362 | -59.5642 | -59.61 | 55.4947 | 3.7445 | -16.4612 | -16.3284 | 63.3499 | -59.6191 | -0.16937 | -0.064087 | 1.9547 | -0.21515 | -7.9056 | -0.22431 | -0.050354 | 2.124 | 42.9337 | 43.0664 | 114.8895 | 122.731 | 1.9547 | 122.7448 | 63.1393 | -0.22431 | 122.731 | 1.9547 | 63.1393 | 114.8895 | 122.7448 | -122.9645 | -123.0194
1375.3281 | 123.1201 | -59.3491 | 63.4323 | -0.21011 | 0.023496 | 0.011457 | 0.014496 | 0.057548 | 0.0010659 | 0.079504 | -57.3715 | 63.4186 | -59.491 | -59.5001 | 55.5862 | 3.8635 | -16.4154 | -16.1957 | 63.3774 | -59.6054 | -0.14191 | -0.013733 | 1.9775 | -0.15106 | -7.8461 | -0.25635 | -0.054932 | 2.1194 | 42.9337 | 43.1534 | 114.9353 | 122.7676 | 1.9775 | 122.7264 | 63.2126 | -0.25635 | 122.7676 | 1.9775 | 63.2126 | 114.9353 | 122.7264 | -122.9233 | -123.0377
1376.3438 | 123.0423 | -59.3628 | 63.4277 | 0.18662 | 0.023924 | 0.019574 | 0.018983 | 0.060752 | -0.0010703 | 0.080572 | -57.4677 | 63.4186 | -59.5551 | -59.6283 | 55.4855 | 3.7994 | -16.3055 | -16.2415 | 63.414 | -59.6008 | -0.19226 | -0.009155 | 1.8951 | -0.2655 | -7.9422 | -0.23804 | -0.013733 | 2.0874 | 43.0573 | 43.1213 | 114.8483 | 122.7814 | 1.8951 | 122.7768 | 63.1622 | -0.23804 | 122.7814 | 1.8951 | 63.1622 | 114.8483 | 122.7768 | -122.9828 | -123.0286
1377.3438 | 123.0423 | -59.3948 | 63.4506 | -0.12619 | 0.023283 | 0.0091068 | 0.020264 | 0.060539 | -0.00064309 | 0.082281 | -57.4631 | 63.5056 | -59.5322 | -59.5642 | 55.5267 | 3.772 | -16.2735 | -16.1682 | 63.3957 | -59.6146 | -0.13733 | 0.054931 | 1.9318 | -0.16937 | -7.9239 | -0.21973 | -0.054932 | 2.0691 | 43.1213 | 43.2266 | 114.9216 | 122.9004 | 1.9318 | 122.7905 | 63.1668 | -0.21973 | 122.9004 | 1.9318 | 63.1668 | 114.9216 | 122.7905 | -122.9828 | -123.0652
1378.3438 | 123.111 | -59.3811 | 63.3865 | 0.2095 | 0.025846 | 0.016584 | 0.014496 | 0.061607 | -0.0014975 | 0.081213 | -57.4448 | 63.4094 | -59.5871 | -59.5642 | 55.5359 | 3.8956 | -16.4566 | -16.127 | 63.3408 | -59.6054 | -0.20599 | 0.022888 | 1.9363 | -0.1831 | -7.8506 | -0.2243 | -0.045777 | 2.1423 | 42.9245 | 43.2541 | 114.917 | 122.7905 | 1.9363 | 122.7219 | 63.2767 | -0.2243 | 122.7905 | 1.9363 | 63.2767 | 114.917 | 122.7219 | -122.9736 | -122.9919
1379.3438 | 123.1064 | -59.3857 | 63.4048 | 0.17899 | 0.023069 | 0.015729 | 0.014069 | 0.059471 | -0.00085669 | 0.082281 | -57.4539 | 63.3957 | -59.5505 | -59.5596 | 55.5725 | 3.8315 | -16.4429 | -16.1316 | 63.3362 | -59.5825 | -0.1648 | -0.009155 | 1.9318 | -0.17395 | -7.8323 | -0.19684 | -0.068664 | 2.0966 | 42.9428 | 43.2541 | 114.9582 | 122.7814 | 1.9318 | 122.7219 | 63.2172 | -0.19684 | 122.7814 | 1.9318 | 63.2172 | 114.9582 | 122.7219 | -122.9553 | -122.9874
1380.3281 | 123.056 | -59.3857 | 63.414 | 0.24765 | 0.02841 | 0.017011 | 0.016846 | 0.060111 | -0.00021569 | 0.083777 | -57.4768 | 63.4415 | -59.5688 | -59.5917 | 55.5222 | 3.7765 | -16.3971 | -16.2735 | 63.3591 | -59.6146 | -0.18311 | 0.027466 | 1.9089 | -0.20599 | -7.8918 | -0.22888 | -0.054931 | 2.092 | 42.9886 | 43.1122 | 114.9078 | 122.8271 | 1.9089 | 122.7448 | 63.1622 | -0.22888 | 122.8271 | 1.9089 | 63.1622 | 114.9078 | 122.7448 | -122.9828 | -123.0286
1381.3438 | 123.0331 | -59.4315 | 63.4323 | 0.14847 | 0.025846 | 0.01637 | 0.018342 | 0.061607 | -0.00064309 | 0.083349 | -57.5134 | 63.4644 | -59.5779 | -59.6466 | 55.4123 | 3.7079 | -16.301 | -16.3696 | 63.3957 | -59.6191 | -0.14648 | 0.032043 | 1.918 | -0.21515 | -8.02 | -0.18768 | -0.036621 | 2.0645 | 43.1305 | 43.0618 | 114.8438 | 122.8958 | 1.918 | 122.8271 | 63.1393 | -0.18768 | 122.8958 | 1.918 | 63.1393 | 114.8438 | 122.8271 | -123.0103 | -123.0515
1382.3438 | 122.9736 | -59.4223 | 63.4415 | 0.2095 | 0.025846 | 0.023419 | 0.019837 | 0.059257 | -0.00064309 | 0.080572 | -57.7835 | 63.4415 | -59.61 | -59.6832 | 55.4443 | 3.7582 | -16.2781 | -16.4062 | 63.4003 | -59.642 | -0.18768 | 0 | 1.6388 | -0.26093 | -7.9971 | -0.21973 | -0.041198 | 1.8265 | 43.1442 | 43.0161 | 114.8666 | 122.8638 | 1.6388 | 122.8226 | 63.1805 | -0.21973 | 122.8638 | 1.6388 | 63.1805 | 114.8666 | 122.8226 | -123.0515 | -123.0835
1383.3438 | 123.0011 | -59.3994 | 63.4827 | 0.018768 | 0.023496 | 0.016156 | 0.015778 | 0.059684 | -0.00064309 | 0.082922 | -57.4585 | 63.4598 | -59.5276 | -59.6008 | 55.4947 | 3.6346 | -16.2964 | -16.2827 | 63.3911 | -59.6146 | -0.12817 | -0.022888 | 1.9409 | -0.20142 | -7.988 | -0.21515 | -0.091553 | 2.0691 | 43.103 | 43.1168 | 114.8941 | 122.8592 | 1.9409 | 122.7905 | 63.0341 | -0.21515 | 122.8592 | 1.9409 | 63.0341 | 114.8941 | 122.7905 | -123.0103 | -123.0972
1384.3438 | 122.9553 | -59.3857 | 63.4781 | 0.079804 | 0.024565 | 0.016797 | 0.01471 | 0.061393 | 0.0021341 | 0.087195 | -57.5089 | 63.4735 | -59.5642 | -60.0723 | 55.2979 | 3.7857 | -16.4612 | -16.4246 | 63.4323 | -59.61 | -0.17853 | -0.004577 | 1.8768 | -0.68665 | -8.1802 | -0.2243 | -0.045776 | 2.0554 | 42.9245 | 42.9611 | 114.6835 | 122.8592 | 1.8768 | 122.818 | 63.1714 | -0.2243 | 122.8592 | 1.8768 | 63.1714 | 114.6835 | 122.818 | -123.0423 | -123.0881
1385.3281 | 123.0286 | -59.3765 | 63.446 | 0.22476 | 0.024137 | 0.017011 | 0.013428 | 0.062461 | -2.092e-06 | 0.082068 | -57.5317 | 63.4644 | -59.5688 | -59.3308 | 55.6274 | 3.6072 | -16.0721 | -16.2369 | 63.446 | -59.5871 | -0.19226 | 0.01831 | 1.8448 | 0.045776 | -7.8186 | -0.21057 | 0 | 2.037 | 43.3044 | 43.1396 | 115.004 | 122.8409 | 1.8448 | 122.8226 | 62.9837 | -0.21057 | 122.8409 | 1.8448 | 62.9837 | 115.004 | 122.8226 | -123.0148 | -123.0331
1386.3438 | 122.9782 | -59.3994 | 63.4827 | 0.049286 | 0.025846 | 0.017438 | 0.017274 | 0.06182 | -0.0017111 | 0.082922 | -57.4905 | 63.4827 | -59.5367 | -59.6054 | 55.5176 | 3.7033 | -16.2369 | -16.1819 | 63.414 | -59.6008 | -0.13733 | 0 | 1.9089 | -0.20599 | -7.9651 | -0.20142 | -0.068665 | 2.0462 | 43.1625 | 43.2175 | 114.917 | 122.8821 | 1.9089 | 122.8134 | 63.1027 | -0.20142 | 122.8821 | 1.9089 | 63.1027 | 114.917 | 122.8134 | -123.0194 | -123.0835
1387.3438 | 123.1247 | -59.3536 | 63.4323 | 0.74356 | 0.02606 | 0.01637 | 0.011292 | 0.060966 | 0.0025613 | 0.083136 | -57.3624 | 63.4323 | -59.5276 | -59.5734 | 55.5862 | 3.7125 | -16.42 | -16.095 | 63.3636 | -59.6054 | -0.17395 | 0 | 1.9913 | -0.21973 | -7.8461 | -0.25177 | -0.068665 | 2.1652 | 42.9337 | 43.2587 | 114.9399 | 122.7859 | 1.9913 | 122.7173 | 63.0661 | -0.25177 | 122.7859 | 1.9913 | 63.0661 | 114.9399 | 122.7173 | -122.9599 | -123.0377
1388.3438 | 123.0469 | -59.3674 | 63.4918 | -0.13382 | 0.023283 | 0.015515 | 0.01706 | 0.059898 | -0.0012839 | 0.081854 | -57.4448 | 63.4598 | -59.5505 | -59.5734 | 55.5588 | 3.6026 | -16.2598 | -16.127 | 63.4552 | -59.5688 | -0.18311 | -0.032043 | 1.9226 | -0.20599 | -7.933 | -0.20142 | -0.036621 | 2.1057 | 43.1076 | 43.2404 | 114.9261 | 122.8271 | 1.9226 | 122.8226 | 62.97 | -0.20142 | 122.8271 | 1.9226 | 62.97 | 114.9261 | 122.8226 | -123.0423 | -123.0606
1389.3438 | 123.0103 | -59.3857 | 63.5056 | -0.13382 | 0.02136 | 0.016584 | 0.013642 | 0.059898 | -0.0029929 | 0.082281 | -57.4951 | 63.446 | -59.5139 | -59.61 | 55.5222 | 3.5522 | -16.1957 | -16.1545 | 63.4781 | -59.5551 | -0.12817 | -0.059509 | 1.8906 | -0.2243 | -7.9834 | -0.16937 | -0.027466 | 2.0187 | 43.19 | 43.2312 | 114.9078 | 122.8317 | 1.8906 | 122.8638 | 62.9379 | -0.16937 | 122.8317 | 1.8906 | 62.9379 | 114.9078 | 122.8638 | -123.0194 | -123.0606
1390.3281 | 123.0057 | -59.3948 | 63.4735 | 0.20187 | 0.026914 | 0.015515 | 0.014924 | 0.060752 | 0.0061929 | 0.084417 | -57.5089 | 63.4323 | -59.5779 | -59.8892 | 55.8151 | 3.7582 | -16.3193 | -16.1407 | 63.4689 | -59.5505 | -0.18311 | -0.041199 | 1.886 | -0.49439 | -7.6584 | -0.15564 | -0.004578 | 2.0691 | 43.0756 | 43.2541 | 115.21 | 122.8271 | 1.886 | 122.8638 | 63.1531 | -0.15564 | 122.8271 | 1.886 | 63.1531 | 115.21 | 122.8638 | -123.0515 | -123.024
1391.3438 | 123.0331 | -59.3628 | 63.4552 | 0.064545 | 0.025205 | 0.014447 | 0.016846 | 0.060966 | -0.0023519 | 0.082281 | -57.4814 | 63.446 | -59.5505 | -59.6054 | 55.4947 | 3.5065 | -16.2277 | -16.1957 | 63.4506 | -59.5871 | -0.18768 | -0.009155 | 1.8814 | -0.24261 | -7.9605 | -0.2243 | -0.004577 | 2.0691 | 43.1351 | 43.1671 | 114.8575 | 122.8088 | 1.8814 | 122.8134 | 62.8693 | -0.2243 | 122.8088 | 1.8814 | 62.8693 | 114.8575 | 122.8134 | -123.0057 | -123.0423
1392.3438 | 123.0469 | -59.3491 | 63.4735 | 0.011139 | 0.025205 | 0.012738 | 0.017487 | 0.06118 | -0.00042929 | 0.082068 | -57.4173 | 63.4598 | -59.5276 | -59.5734 | 55.5405 | 3.6896 | -16.1087 | -16.095 | 63.4232 | -59.5871 | -0.17853 | -0.013733 | 1.9318 | -0.2243 | -7.933 | -0.23804 | -0.050354 | 2.1103 | 43.2404 | 43.2541 | 114.8895 | 122.8088 | 1.9318 | 122.7722 | 63.0386 | -0.23804 | 122.8088 | 1.9318 | 63.0386 | 114.8895 | 122.7722 | -123.0011 | -123.0606
1393.3281 | 123.0423 | -59.3353 | 63.4964 | -0.17197 | 0.022642 | 0.014447 | 0.013856 | 0.062034 | -0.0021383 | 0.082708 | -57.486 | 63.4781 | -59.5505 | -59.5871 | 55.5313 | 3.6209 | -16.1133 | -16.1591 | 63.4872 | -59.5413 | -0.21515 | -0.018311 | 1.8494 | -0.25177 | -7.9651 | -0.20599 | -0.009155 | 2.0645 | 43.222 | 43.1763 | 114.8666 | 122.8134 | 1.8494 | 122.8226 | 62.9562 | -0.20599 | 122.8134 | 1.8494 | 62.9562 | 114.8666 | 122.8226 | -123.0469 | -123.0377
1394.3438 | 123.056 | -59.3216 | 63.4552 | -0.080414 | 0.024565 | 0.018506 | 0.015137 | 0.059684 | -0.00042929 | 0.080359 | -57.4265 | 63.446 | -59.5322 | -59.5734 | 55.5405 | 3.5339 | -16.1041 | -16.04 | 63.4552 | -59.5367 | -0.21057 | -0.009155 | 1.8951 | -0.25177 | -7.9147 | -0.21515 | 0 | 2.1057 | 43.2175 | 43.2816 | 114.8621 | 122.7676 | 1.8951 | 122.7768 | 62.8555 | -0.21515 | 122.7676 | 1.8951 | 62.8555 | 114.8621 | 122.7768 | -122.9874 | -122.9919
1395.3438 | 123.0423 | -59.3491 | 63.4644 | 0.034027 | 0.024351 | 0.017011 | 0.01471 | 0.062034 | -0.00064309 | 0.081 | -57.4356 | 63.4369 | -59.5551 | -59.5779 | 55.5176 | 3.6392 | -16.127 | -16.1087 | 63.4735 | -59.5596 | -0.20599 | -0.027465 | 1.9135 | -0.22888 | -7.9468 | -0.21057 | 0.009156 | 2.1194 | 43.222 | 43.2404 | 114.8666 | 122.7859 | 1.9135 | 122.8226 | 62.9883 | -0.21057 | 122.7859 | 1.9135 | 62.9883 | 114.8666 | 122.8226 | -123.0194 | -123.024
1396.3281 | 123.0423 | -59.3262 | 63.4872 | -0.088043 | 0.024351 | 0.016156 | 0.015992 | 0.060111 | -0.0021383 | 0.083349 | -57.431 | 63.4323 | -59.5139 | -59.5688 | 55.7053 | 3.6484 | -16.0034 | -15.8478 | 63.446 | -59.5642 | -0.18768 | -0.054932 | 1.8951 | -0.24262 | -7.782 | -0.23804 | -0.041199 | 2.0828 | 43.3228 | 43.4784 | 115.0314 | 122.7585 | 1.8951 | 122.7722 | 62.9745 | -0.23804 | 122.7585 | 1.8951 | 62.9745 | 115.0314 | 122.7722 | -123.0011 | -123.0515
1397.3438 | 122.8638 | -59.4269 | 63.4735 | 0.17136 | 0.02606 | 0.014875 | 0.016205 | 0.060111 | 0.0012795 | 0.080359 | -57.4951 | 63.4827 | -59.5322 | -59.6695 | 55.4306 | 3.5522 | -16.0355 | -16.1545 | 63.4552 | -59.6054 | -0.10529 | 0.009155 | 1.9318 | -0.24262 | -8.0429 | -0.17853 | -0.018311 | 2.037 | 43.3914 | 43.2724 | 114.8575 | 122.9095 | 1.9318 | 122.8821 | 62.9791 | -0.17853 | 122.9095 | 1.9318 | 62.9791 | 114.8575 | 122.8821 | -123.0057 | -123.0789
1398.3281 | 123.0103 | -59.3491 | 63.4964 | -0.40085 | 0.023283 | 0.011243 | 0.011719 | 0.059471 | -0.0012839 | 0.079504 | -57.5226 | 63.4644 | -59.5413 | -59.6146 | 55.4901 | 3.5797 | -16.0721 | -16.2277 | 63.4598 | -59.5642 | -0.19226 | -0.032044 | 1.8265 | -0.2655 | -8.0063 | -0.21515 | -0.036621 | 2.0187 | 43.277 | 43.1213 | 114.8392 | 122.8134 | 1.8265 | 122.8088 | 62.9288 | -0.21515 | 122.8134 | 1.8265 | 62.9288 | 114.8392 | 122.8088 | -123.0377 | -123.0606
1399.3594 | 123.0789 | -59.3399 | 63.4506 | 0.19424 | 0.022215 | 0.016156 | 0.008515 | 0.060111 | -0.0021383 | 0.081213 | -57.4173 | 63.3957 | -59.491 | -59.5963 | 55.5222 | 3.6392 | -16.2735 | -16.0995 | 63.4003 | -59.5779 | -0.15106 | -0.054932 | 1.9226 | -0.25635 | -7.9285 | -0.23804 | -0.050354 | 2.0737 | 43.0664 | 43.2404 | 114.8621 | 122.7356 | 1.9226 | 122.7402 | 62.9791 | -0.23804 | 122.7356 | 1.9226 | 62.9791 | 114.8621 | 122.7402 | -122.9416 | -123.0286
1400.3281 | 123.1064 | -59.3124 | 63.4689 | -0.14908 | 0.020506 | 0.011243 | 0.01001 | 0.056693 | -0.0012839 | 0.079718 | -57.4081 | 63.4277 | -59.4818 | -59.5047 | 55.6274 | 3.6667 | -16.1957 | -15.9714 | 63.4232 | -59.5276 | -0.16937 | -0.041199 | 1.9043 | -0.19226 | -7.8415 | -0.21515 | -0.045776 | 2.0737 | 43.1168 | 43.3411 | 114.9399 | 122.7402 | 1.9043 | 122.7356 | 62.9791 | -0.21515 | 122.7402 | 1.9043 | 62.9791 | 114.9399 | 122.7356 | -122.9507 | -122.9965
1401.3281 | 123.0743 | -59.3216 | 63.5056 | -0.19485 | 0.020933 | 0.015943 | 0.011506 | 0.058616 | -0.0023519 | 0.081213 | -57.3807 | 63.4232 | -59.4772 | -59.5184 | 55.6046 | 3.7216 | -16.1453 | -15.9393 | 63.4735 | -59.5047 | -0.15564 | -0.082397 | 1.9409 | -0.19684 | -7.901 | -0.18311 | -0.032043 | 2.0966 | 43.1763 | 43.3823 | 114.9261 | 122.7448 | 1.9409 | 122.7951 | 63.0432 | -0.18311 | 122.7448 | 1.9409 | 63.0432 | 114.9261 | 122.7951 | -122.9828 | -123.0103
1402.3438 | 123.0835 | -59.3628 | 63.4369 | 0.14847 | 0.023496 | 0.013593 | 0.018555 | 0.060752 | -0.0036337 | 0.080572 | -57.4631 | 63.4415 | -59.5505 | -59.642 | 55.4581 | 3.4424 | -16.1545 | -16.2094 | 63.4598 | -59.5459 | -0.18768 | 0.004577 | 1.8997 | -0.27924 | -7.9788 | -0.1831 | 0.022888 | 2.0874 | 43.2083 | 43.1534 | 114.8209 | 122.8043 | 1.8997 | 122.8226 | 62.8052 | -0.1831 | 122.8043 | 1.8997 | 62.8052 | 114.8209 | 122.8226 | -122.9874 | -122.9828
1403.3281 | 123.0194 | -59.3445 | 63.5193 | -0.19485 | 0.024565 | 0.01167 | 0.013001 | 0.058402 | -0.00064309 | 0.081 | -57.3944 | 63.4872 | -59.4772 | -59.5688 | 55.5405 | 3.598 | -16.0538 | -15.9943 | 63.4781 | -59.5322 | -0.13275 | -0.032043 | 1.9501 | -0.22431 | -7.9788 | -0.18768 | -0.041199 | 2.0828 | 43.2907 | 43.3502 | 114.8849 | 122.8317 | 1.9501 | 122.8226 | 62.9425 | -0.18768 | 122.8317 | 1.9501 | 62.9425 | 114.8849 | 122.8226 | -122.9965 | -123.0515
1404.3281 | 123.0743 | -59.3445 | 63.4735 | -0.22537 | 0.024778 | 0.015088 | 0.010224 | 0.059684 | -0.00042929 | 0.081854 | -57.5272 | 63.4186 | -59.5093 | -59.5871 | 55.5588 | 3.6484 | -16.1179 | -15.9668 | 63.4506 | -59.5734 | -0.16479 | -0.054932 | 1.8173 | -0.24262 | -7.9147 | -0.22888 | -0.022888 | 1.9821 | 43.2266 | 43.3777 | 114.9033 | 122.7631 | 1.8173 | 122.7951 | 62.9929 | -0.22888 | 122.7631 | 1.8173 | 62.9929 | 114.9033 | 122.7951 | -122.9828 | -123.0469
1405.3281 | 123.0927 | -59.3308 | 63.4781 | 0.056915 | 0.023496 | 0.015088 | 0.010224 | 0.058616 | -0.0021383 | 0.080786 | -57.431 | 63.4415 | -59.491 | -59.5642 | 55.5542 | 3.5294 | -16.1545 | -15.9714 | 63.4415 | -59.5642 | -0.16022 | -0.036621 | 1.8997 | -0.23346 | -7.9239 | -0.23346 | -0.036621 | 2.0599 | 43.1763 | 43.3594 | 114.8849 | 122.7722 | 1.8997 | 122.7722 | 62.8601 | -0.23346 | 122.7722 | 1.8997 | 62.8601 | 114.8849 | 122.7722 | -122.9691 | -123.0423
1406.3281 | 123.143 | -59.3308 | 63.4689 | -0.065155 | 0.022856 | 0.012525 | 0.014283 | 0.057762 | -0.00085669 | 0.081213 | -57.3807 | 63.4323 | -59.4955 | -59.491 | 55.5862 | 3.6758 | -16.1636 | -15.9256 | 63.4644 | -59.5276 | -0.16479 | -0.036621 | 1.9501 | -0.16022 | -7.8827 | -0.19684 | -0.004578 | 2.1149 | 43.1671 | 43.4052 | 114.917 | 122.7631 | 1.9501 | 122.7951 | 63.0066 | -0.19684 | 122.7631 | 1.9501 | 63.0066 | 114.917 | 122.7951 | -122.9645 | -122.9965
1407.3438 | 123.0103 | -59.3445 | 63.4827 | 0.041657 | 0.02606 | 0.014875 | 0.020478 | 0.060752 | -0.0027793 | 0.081427 | -57.4265 | 63.4918 | -59.4955 | -59.5642 | 55.4855 | 3.5294 | -16.0172 | -15.9988 | 63.4781 | -59.5688 | -0.15106 | 0.009155 | 1.918 | -0.21973 | -7.9971 | -0.22431 | -0.004578 | 2.0691 | 43.3273 | 43.3456 | 114.83 | 122.8363 | 1.918 | 122.8226 | 62.8738 | -0.22431 | 122.8363 | 1.918 | 62.8738 | 114.83 | 122.8226 | -122.9782 | -123.0515
1408.3281 | 123.1247 | -59.3124 | 63.4689 | -0.11856 | 0.023069 | 0.010602 | 0.0095832 | 0.062034 | 0.0014933 | 0.081854 | -57.3166 | 63.4598 | -59.4589 | -59.5413 | 55.5496 | 3.5889 | -16.1591 | -15.8432 | 63.4506 | -59.5596 | -0.14648 | -0.009155 | 1.9958 | -0.22888 | -7.9193 | -0.24719 | -0.01831 | 2.1423 | 43.1534 | 43.4692 | 114.8621 | 122.7722 | 1.9958 | 122.7631 | 62.9013 | -0.24719 | 122.7722 | 1.9958 | 62.9013 | 114.8621 | 122.7631 | -122.9279 | -123.0286
1409.3281 | 122.9965 | -59.3857 | 63.4872 | 0.14084 | 0.025633 | 0.015943 | 0.017914 | 0.062034 | -0.00042929 | 0.080359 | -57.5317 | 63.4781 | -59.5505 | -59.6329 | 55.4626 | 3.4012 | -16.0172 | -16.0721 | 63.4964 | -59.5963 | -0.1648 | -0.009156 | 1.8539 | -0.24719 | -8.0246 | -0.21057 | 0.009155 | 2.0187 | 43.3685 | 43.3136 | 114.8483 | 122.8638 | 1.8539 | 122.8821 | 62.7869 | -0.21057 | 122.8638 | 1.8539 | 62.7869 | 114.8483 | 122.8821 | -123.0377 | -123.0835
1410.3281 | 123.1247 | -59.3445 | 63.4415 | 0.034027 | 0.024351 | 0.018079 | 0.01471 | 0.060966 | 0.00042511 | 0.081213 | -57.3898 | 63.4369 | -59.491 | -59.5322 | 55.5588 | 3.6026 | -16.2231 | -15.8569 | 63.4094 | -59.5917 | -0.14648 | -0.004577 | 1.9547 | -0.18768 | -7.8827 | -0.24719 | -0.032043 | 2.1011 | 43.1213 | 43.4875 | 114.9033 | 122.7814 | 1.9547 | 122.7539 | 62.9471 | -0.24719 | 122.7814 | 1.9547 | 62.9471 | 114.9033 | 122.7539 | -122.9324 | -123.0331
1411.3281 | 123.0423 | -59.3628 | 63.4644 | 0.21713 | 0.026274 | 0.014447 | 0.017274 | 0.062034 | -0.00042929 | 0.081854 | -57.4402 | 63.5147 | -59.5367 | -59.5779 | 55.5176 | 3.479 | -16.0172 | -15.8524 | 63.446 | -59.5917 | -0.17395 | 0.050354 | 1.9226 | -0.21515 | -7.9468 | -0.22888 | -0.01831 | 2.0966 | 43.3456 | 43.5104 | 114.8804 | 122.8775 | 1.9226 | 122.8088 | 62.8418 | -0.22888 | 122.8775 | 1.9226 | 62.8418 | 114.8804 | 122.8088 | -123.0011 | -123.056
1412.3438 | 123.0331 | -59.3353 | 63.4964 | 0.19424 | 0.025633 | 0.015302 | 0.018555 | 0.061393 | 0.0019205 | 0.078222 | -57.4539 | 63.501 | -59.5184 | -59.5917 | 55.4901 | 3.3279 | -16.0584 | -15.9439 | 63.4644 | -59.5734 | -0.18311 | 0.004578 | 1.8814 | -0.25635 | -8.0063 | -0.23804 | -0.032044 | 2.0645 | 43.277 | 43.3914 | 114.8254 | 122.8363 | 1.8814 | 122.7997 | 62.6633 | -0.23804 | 122.8363 | 1.8814 | 62.6633 | 114.8254 | 122.7997 | -123.0148 | -123.0698
1413.3281 | 123.024 | -59.3536 | 63.5101 | 0.034027 | 0.024778 | 0.01637 | 0.016419 | 0.060539 | -0.00021569 | 0.081854 | -57.399 | 63.5147 | -59.5276 | -59.5642 | 55.5405 | 3.479 | -15.9302 | -15.8478 | 63.4552 | -59.5963 | -0.17395 | 0.004577 | 1.9547 | -0.21057 | -7.9697 | -0.24261 | -0.054932 | 2.1286 | 43.4235 | 43.5059 | 114.8941 | 122.8683 | 1.9547 | 122.8088 | 62.8326 | -0.24261 | 122.8683 | 1.9547 | 62.8326 | 114.8941 | 122.8088 | -123.0377 | -123.1064
1414.3438 | 123.1201 | -59.3262 | 63.4232 | 0.43839 | 0.020292 | 0.014447 | 0.014496 | 0.06118 | -0.00085669 | 0.081 | -57.2754 | 63.4369 | -59.491 | -59.5139 | 55.5725 | 3.4973 | -16.1728 | -15.8203 | 63.4323 | -59.5596 | -0.16479 | 0.013733 | 2.0508 | -0.18768 | -7.8506 | -0.23346 | 0.009155 | 2.2156 | 43.1534 | 43.5059 | 114.8987 | 122.7631 | 2.0508 | 122.7585 | 62.8235 | -0.23346 | 122.7631 | 2.0508 | 62.8235 | 114.8987 | 122.7585 | -122.9141 | -122.9828
1415.3281 | 122.9782 | -59.3308 | 63.5056 | 0.11795 | 0.024351 | 0.018293 | 0.012574 | 0.059898 | 0.0023477 | 0.081427 | -57.4951 | 63.5559 | -59.5459 | -59.5505 | 55.4672 | 3.3646 | -15.9897 | -15.9485 | 63.4781 | -59.5963 | -0.21515 | 0.050354 | 1.8356 | -0.21973 | -8.0383 | -0.2655 | -0.027466 | 2.0508 | 43.3411 | 43.3823 | 114.798 | 122.8867 | 1.8356 | 122.8088 | 62.6953 | -0.2655 | 122.8867 | 1.8356 | 62.6953 | 114.798 | 122.8088 | -123.0515 | -123.1018
1416.3281 | 123.0286 | -59.3353 | 63.5239 | -0.1033 | 0.026274 | 0.014661 | 0.017487 | 0.05883 | 0.0010659 | 0.079931 | -57.4036 | 63.5696 | -59.4681 | -59.5047 | 55.5588 | 3.3966 | -15.9943 | -15.9393 | 63.4918 | -59.5596 | -0.13275 | 0.045776 | 1.9318 | -0.16937 | -7.9651 | -0.2243 | -0.032044 | 2.0645 | 43.3411 | 43.396 | 114.8941 | 122.905 | 1.9318 | 122.8271 | 62.7319 | -0.2243 | 122.905 | 1.9318 | 62.7319 | 114.8941 | 122.8271 | -122.9919 | -123.0835
1417.3281 | 123.0331 | -59.3079 | 63.501 | -0.16434 | 0.024992 | 0.012311 | 0.014924 | 0.060539 | -0.00042929 | 0.082708 | -57.4127 | 63.5376 | -59.5093 | -59.5276 | 55.545 | 3.3829 | -15.9027 | -15.8432 | 63.533 | -59.5596 | -0.20142 | 0.036621 | 1.8951 | -0.21973 | -7.9559 | -0.25177 | 0.032043 | 2.0966 | 43.4052 | 43.4647 | 114.8529 | 122.8455 | 1.8951 | 122.8409 | 62.6907 | -0.25177 | 122.8455 | 1.8951 | 62.6907 | 114.8529 | 122.8409 | -123.0103 | -123.0606
1418.3281 | 123.024 | -59.3124 | 63.5101 | -0.1033 | 0.023924 | 0.010816 | 0.013856 | 0.062675 | -0.0023519 | 0.082922 | -57.399 | 63.5559 | -59.4864 | -59.5139 | 55.5588 | 3.4378 | -15.9348 | -15.8752 | 63.446 | -59.5779 | -0.17395 | 0.045776 | 1.9135 | -0.20142 | -7.9514 | -0.2655 | -0.064087 | 2.0874 | 43.3777 | 43.4372 | 114.8712 | 122.8683 | 1.9135 | 122.7585 | 62.7502 | -0.2655 | 122.8683 | 1.9135 | 62.7502 | 114.8712 | 122.7585 | -122.9965 | -123.0881
1419.3438 | 123.0377 | -59.3124 | 63.5101 | -0.080414 | 0.025633 | 0.011457 | 0.015351 | 0.062461 | -2.092e-06 | 0.080786 | -57.4127 | 63.5422 | -59.4864 | -59.5093 | 55.5771 | 3.4287 | -16.008 | -15.8432 | 63.4872 | -59.5505 | -0.17395 | 0.032043 | 1.8997 | -0.19684 | -7.933 | -0.23804 | -0.022888 | 2.0737 | 43.3044 | 43.4692 | 114.8895 | 122.8546 | 1.8997 | 122.7997 | 62.7411 | -0.23804 | 122.8546 | 1.8997 | 62.7411 | 114.8895 | 122.7997 | -122.9965 | -123.0606
1420.3281 | 123.0148 | -59.3216 | 63.5101 | -0.16434 | 0.025419 | 0.020215 | 0.012787 | 0.062248 | 0.00021151 | 0.080359 | -57.4356 | 63.533 | -59.5047 | -59.5688 | 55.5313 | 3.4195 | -15.889 | -15.9073 | 63.5147 | -59.5322 | -0.18311 | 0.022888 | 1.886 | -0.24719 | -7.9788 | -0.21057 | 0.004577 | 2.0691 | 43.4326 | 43.4143 | 114.8529 | 122.8546 | 1.886 | 122.8363 | 62.7411 | -0.21057 | 122.8546 | 1.886 | 62.7411 | 114.8529 | 122.8363 | -123.0148 | -123.0423
1421.3438 | 123.0331 | -59.317 | 63.5239 | 0.018768 | 0.025419 | 0.019147 | 0.015778 | 0.06118 | -0.00042929 | 0.082068 | -57.4036 | 63.533 | -59.4772 | -59.5505 | 55.5222 | 3.4149 | -15.9943 | -15.9073 | 63.4964 | -59.5551 | -0.16022 | 0.009155 | 1.9135 | -0.23346 | -8.0017 | -0.23804 | -0.027466 | 2.0737 | 43.3228 | 43.4097 | 114.8392 | 122.85 | 1.9135 | 122.8134 | 62.7319 | -0.23804 | 122.85 | 1.9135 | 62.7319 | 114.8392 | 122.8134 | -123.0011 | -123.0789
1422.3438 | 122.9782 | -59.3262 | 63.501 | 0.011139 | 0.022856 | 0.015302 | 0.016846 | 0.06182 | 0.0021341 | 0.082708 | -57.4448 | 63.5284 | -59.4818 | -59.5734 | 55.5038 | 3.4012 | -15.9851 | -15.9485 | 63.4735 | -59.5551 | -0.15564 | 0.027465 | 1.8814 | -0.24719 | -7.9971 | -0.22888 | -0.027466 | 2.037 | 43.3411 | 43.3777 | 114.83 | 122.8546 | 1.8814 | 122.7997 | 62.7274 | -0.22888 | 122.8546 | 1.8814 | 62.7274 | 114.83 | 122.7997 | -122.9828 | -123.056
1423.3438 | 123.0148 | -59.3353 | 63.5239 | 0.10269 | 0.024137 | 0.017011 | 0.014496 | 0.060111 | -0.00064309 | 0.082708 | -57.4677 | 63.5422 | -59.523 | -59.6008 | 55.4764 | 3.3463 | -15.9851 | -15.9439 | 63.4644 | -59.5551 | -0.18768 | 0.01831 | 1.8677 | -0.2655 | -8.0475 | -0.21973 | -0.05951 | 2.0554 | 43.3502 | 43.3914 | 114.8117 | 122.8775 | 1.8677 | 122.7997 | 62.6816 | -0.21973 | 122.8775 | 1.8677 | 62.6816 | 114.8117 | 122.7997 | -123.0469 | -123.0789
1424.3281 | 122.9965 | -59.3033 | 63.5422 | -0.1796 | 0.020292 | 0.013166 | 0.01001 | 0.057975 | -0.00042929 | 0.083136 | -57.4356 | 63.4872 | -59.4818 | -59.5642 | 55.5222 | 3.4103 | -15.889 | -15.8203 | 63.5239 | -59.5322 | -0.17853 | -0.054931 | 1.8677 | -0.26093 | -8.02 | -0.22888 | -0.01831 | 2.0462 | 43.4143 | 43.483 | 114.8254 | 122.7905 | 1.8677 | 122.8271 | 62.7136 | -0.22888 | 122.7905 | 1.8677 | 62.7136 | 114.8254 | 122.8271 | -123.024 | -123.0743
1425.3281 | 122.9965 | -59.3124 | 63.5559 | -0.20248 | 0.024351 | 0.015943 | 0.014283 | 0.058616 | -0.0012839 | 0.079931 | -57.5638 | 63.5101 | -59.4452 | -59.5917 | 55.481 | 3.3142 | -15.8249 | -15.834 | 63.5605 | -59.5093 | -0.13275 | -0.045776 | 1.7487 | -0.27924 | -8.075 | -0.19684 | 0.004578 | 1.8814 | 43.4875 | 43.4784 | 114.7934 | 122.8226 | 1.7487 | 122.8729 | 62.6266 | -0.19684 | 122.8226 | 1.7487 | 62.6266 | 114.7934 | 122.8729 | -123.0011 | -123.0652
1426.3281 | 122.9462 | -59.285 | 63.588 | -0.14145 | 0.02136 | 0.011029 | 0.010865 | 0.059898 | 0.0010659 | 0.079931 | -57.4127 | 63.5513 | -59.4727 | -59.5413 | 55.5359 | 3.3188 | -15.8615 | -15.7608 | 63.5376 | -59.523 | -0.18768 | -0.036621 | 1.8723 | -0.25635 | -8.0521 | -0.23804 | -0.050354 | 2.0599 | 43.4235 | 43.5242 | 114.8209 | 122.8363 | 1.8723 | 122.8226 | 62.6038 | -0.23804 | 122.8363 | 1.8723 | 62.6038 | 114.8209 | 122.8226 | -123.0606 | -123.111
1427.3281 | 123.0194 | -59.2896 | 63.5605 | -0.20248 | 0.021787 | 0.013806 | 0.01236 | 0.057334 | -0.0010703 | 0.08164 | -57.399 | 63.4872 | -59.4589 | -59.5139 | 55.5817 | 3.3691 | -15.9119 | -15.7333 | 63.5193 | -59.4818 | -0.16937 | -0.073242 | 1.8906 | -0.2243 | -7.9788 | -0.19226 | -0.041199 | 2.0599 | 43.3777 | 43.5562 | 114.8712 | 122.7768 | 1.8906 | 122.8088 | 62.6587 | -0.19226 | 122.7768 | 1.8906 | 62.6587 | 114.8712 | 122.8088 | -123.0194 | -123.0423
1428.3281 | 122.9965 | -59.2712 | 63.5788 | -0.22537 | 0.022001 | 0.011029 | 0.011933 | 0.057548 | -0.0027793 | 0.081 | -57.4356 | 63.4964 | -59.4498 | -59.5413 | 55.5496 | 3.3783 | -15.8798 | -15.7425 | 63.5559 | -59.4955 | -0.17853 | -0.082397 | 1.8356 | -0.27008 | -8.0292 | -0.2243 | -0.022888 | 2.0142 | 43.3914 | 43.5287 | 114.8209 | 122.7676 | 1.8356 | 122.8271 | 62.6495 | -0.2243 | 122.7676 | 1.8356 | 62.6495 | 114.8209 | 122.8271 | -123.0286 | -123.0743
1429.3281 | 123.0057 | -59.2941 | 63.5742 | -0.19485 | 0.022856 | 0.011457 | 0.013428 | 0.059471 | -0.0010703 | 0.079718 | -57.3898 | 63.4827 | -59.4589 | -59.5093 | 55.5771 | 3.3737 | -15.9164 | -15.7608 | 63.5559 | -59.4727 | -0.16479 | -0.091553 | 1.9043 | -0.21515 | -7.9971 | -0.17853 | -0.018311 | 2.0691 | 43.3777 | 43.5333 | 114.8712 | 122.7768 | 1.9043 | 122.85 | 62.6678 | -0.17853 | 122.7768 | 1.9043 | 62.6678 | 114.8712 | 122.85 | -123.0331 | -123.0469
1430.3281 | 123.0881 | -59.2621 | 63.5284 | -0.21011 | 0.022215 | 0.01637 | 0.010865 | 0.058189 | -0.0029929 | 0.080359 | -57.3715 | 63.4872 | -59.4406 | -59.4543 | 55.6412 | 3.4836 | -16.0675 | -15.7471 | 63.5376 | -59.4635 | -0.17853 | -0.041198 | 1.8906 | -0.19226 | -7.8873 | -0.20142 | 0.009156 | 2.0691 | 43.1946 | 43.515 | 114.9033 | 122.7493 | 1.8906 | 122.7997 | 62.7457 | -0.20142 | 122.7493 | 1.8906 | 62.7457 | 114.9033 | 122.7997 | -122.9691 | -122.9919
1431.3438 | 122.9874 | -59.2896 | 63.5788 | -0.19485 | 0.020506 | 0.010816 | 0.017914 | 0.058616 | -0.0036337 | 0.081213 | -57.399 | 63.5147 | -59.4818 | -59.5184 | 55.5725 | 3.3005 | -15.8936 | -15.8386 | 63.5742 | -59.4818 | -0.19226 | -0.064087 | 1.8906 | -0.22888 | -8.0063 | -0.19226 | -0.004577 | 2.0828 | 43.396 | 43.4509 | 114.8621 | 122.8043 | 1.8906 | 122.8638 | 62.59 | -0.19226 | 122.8043 | 1.8906 | 62.59 | 114.8621 | 122.8638 | -123.0606 | -123.0606
1432.3438 | 123.056 | -59.2712 | 63.6017 | -0.37033 | 0.022856 | 0.010175 | 0.013856 | 0.060111 | -0.0014975 | 0.080786 | -57.4219 | 63.5147 | -59.436 | -59.5322 | 55.5679 | 3.2959 | -15.8844 | -15.8615 | 63.533 | -59.491 | -0.16479 | -0.086976 | 1.8494 | -0.26093 | -8.0338 | -0.21973 | -0.068665 | 2.0142 | 43.3868 | 43.4097 | 114.8392 | 122.7859 | 1.8494 | 122.8043 | 62.5671 | -0.21973 | 122.7859 | 1.8494 | 62.5671 | 114.8392 | 122.8043 | -123.0377 | -123.0927
1433.3281 | 123.1476 | -59.2575 | 63.5193 | -0.12619 | 0.021574 | 0.01402 | 0.010438 | 0.055412 | -0.0010703 | 0.081 | -57.3303 | 63.4369 | -59.436 | -59.198 | 56.0165 | 3.6163 | -16.3834 | -15.7471 | 63.4689 | -59.4818 | -0.17853 | -0.082397 | 1.9272 | 0.059509 | -7.5027 | -0.22431 | -0.050354 | 2.1057 | 42.8741 | 43.5104 | 115.274 | 122.6944 | 1.9272 | 122.7264 | 62.8738 | -0.22431 | 122.6944 | 1.9272 | 62.8738 | 115.274 | 122.7264 | -122.9553 | -123.0011
1434.3438 | 123.1064 | -59.2804 | 63.5284 | -0.011749 | 0.02136 | 0.0097476 | 0.011292 | 0.057548 | -0.00021569 | 0.080786 | -57.3944 | 63.4323 | -59.4452 | -59.4681 | 55.6137 | 3.36 | -16.0904 | -15.8249 | 63.5147 | -59.4727 | -0.16479 | -0.09613 | 1.886 | -0.18768 | -7.9147 | -0.19226 | -0.013733 | 2.0508 | 43.19 | 43.4555 | 114.8941 | 122.7127 | 1.886 | 122.7951 | 62.6404 | -0.19226 | 122.7127 | 1.886 | 62.6404 | 114.8941 | 122.7951 | -122.9736 | -123.0011
1435.3281 | 123.1201 | -59.2529 | 63.5376 | 0.026398 | 0.023496 | 0.014234 | 0.011933 | 0.057548 | -0.0019247 | 0.082495 | -57.3944 | 63.4552 | -59.4406 | -59.4681 | 55.6366 | 3.4012 | -16.0446 | -15.7333 | 63.5147 | -59.4498 | -0.18768 | -0.082398 | 1.8585 | -0.21515 | -7.901 | -0.19684 | -0.022889 | 2.0462 | 43.2083 | 43.5196 | 114.8895 | 122.7081 | 1.8585 | 122.7676 | 62.6541 | -0.19684 | 122.7081 | 1.8585 | 62.6541 | 114.8895 | 122.7676 | -122.9782 | -122.9874
1436.3594 | 123.1201 | -59.2529 | 63.5147 | -0.072784 | 0.023496 | 0.012952 | 0.012574 | 0.056266 | -0.0025657 | 0.079718 | -57.3212 | 63.4827 | -59.3994 | -59.4177 | 55.6595 | 3.3463 | -16.0584 | -15.6326 | 63.5193 | -59.4635 | -0.14648 | -0.032043 | 1.9318 | -0.16479 | -7.8552 | -0.21057 | 0.004578 | 2.0782 | 43.1946 | 43.6203 | 114.9124 | 122.7356 | 1.9318 | 122.7722 | 62.5992 | -0.21057 | 122.7356 | 1.9318 | 62.5992 | 114.9124 | 122.7722 | -122.9141 | -122.9782
1437.3281 | 123.0469 | -59.2621 | 63.533 | 0.1561 | 0.024351 | 0.014447 | 0.013215 | 0.057762 | -0.0014975 | 0.080359 | -57.4173 | 63.4277 | -59.4635 | -59.5093 | 55.5771 | 3.3234 | -16.0446 | -15.8112 | 63.4964 | -59.4727 | -0.20142 | -0.10529 | 1.8448 | -0.24719 | -7.9559 | -0.21057 | -0.036621 | 2.0462 | 43.2175 | 43.4509 | 114.8392 | 122.6898 | 1.8448 | 122.7585 | 62.5854 | -0.21057 | 122.6898 | 1.8448 | 62.5854 | 114.8392 | 122.7585 | -122.9965 | -123.0057
1438.3281 | 123.0743 | -59.2667 | 63.5147 | 0.17136 | 0.021787 | 0.012097 | 0.015992 | 0.056907 | -0.0023519 | 0.081854 | -57.3807 | 63.4415 | -59.4635 | -59.4681 | 55.6229 | 3.4103 | -16.0995 | -15.715 | 63.4827 | -59.4772 | -0.19684 | -0.073242 | 1.886 | -0.20142 | -7.8918 | -0.21057 | -0.032043 | 2.0828 | 43.1671 | 43.5516 | 114.8895 | 122.7081 | 1.886 | 122.7493 | 62.677 | -0.21057 | 122.7081 | 1.886 | 62.677 | 114.8895 | 122.7493 | -122.9782 | -122.9919
1439.3281 | 123.0835 | -59.2804 | 63.5147 | 0.14084 | 0.021574 | 0.013166 | 0.01471 | 0.058189 | -0.00021569 | 0.082068 | -57.4356 | 63.4552 | -59.4635 | -59.5184 | 55.6183 | 3.4378 | -15.9119 | -15.6097 | 63.5101 | -59.4818 | -0.1831 | -0.059509 | 1.8448 | -0.23804 | -7.8964 | -0.20142 | -0.004577 | 2.0279 | 43.3685 | 43.6707 | 114.8987 | 122.7356 | 1.8448 | 122.7905 | 62.7182 | -0.20142 | 122.7356 | 1.8448 | 62.7182 | 114.8987 | 122.7905 | -122.9782 | -122.9965
1440.3281 | 123.1018 | -59.2667 | 63.5056 | 0.18662 | 0.023496 | 0.015515 | 0.014069 | 0.059043 | -0.0010703 | 0.082068 | -57.3898 | 63.4277 | -59.4452 | -59.4772 | 55.6046 | 3.4607 | -15.9485 | -15.5869 | 63.4781 | -59.5139 | -0.17853 | -0.07782 | 1.8768 | -0.21057 | -7.901 | -0.24719 | -0.027466 | 2.0554 | 43.3182 | 43.6798 | 114.8712 | 122.6944 | 1.8768 | 122.7448 | 62.7274 | -0.24719 | 122.6944 | 1.8768 | 62.7274 | 114.8712 | 122.7448 | -122.9507 | -123.0194
1441.3281 | 123.0652 | -59.285 | 63.5056 | 0.17136 | 0.022428 | 0.012311 | 0.014496 | 0.057121 | -0.0025657 | 0.081427 | -57.4081 | 63.4277 | -59.4589 | -59.5139 | 55.5771 | 3.3508 | -15.9576 | -15.6052 | 63.4872 | -59.4772 | -0.17395 | -0.07782 | 1.8768 | -0.22888 | -7.9285 | -0.19226 | -0.01831 | 2.0508 | 43.3273 | 43.6798 | 114.8621 | 122.7127 | 1.8768 | 122.7722 | 62.6358 | -0.19226 | 122.7127 | 1.8768 | 62.6358 | 114.8621 | 122.7722 | -122.9645 | -122.9828
1442.3281 | 123.0606 | -59.2987 | 63.5193 | 0.19424 | 0.021574 | 0.013806 | 0.015992 | 0.058402 | -0.0034201 | 0.082068 | -57.3853 | 63.4186 | -59.4955 | -59.4772 | 55.6046 | 3.4012 | -15.9393 | -15.5319 | 63.446 | -59.4315 | -0.19684 | -0.10071 | 1.9135 | -0.17853 | -7.9147 | -0.13275 | -0.073242 | 2.1103 | 43.3594 | 43.7668 | 114.9033 | 122.7173 | 1.9135 | 122.7448 | 62.6999 | -0.13275 | 122.7173 | 1.9135 | 62.6999 | 114.9033 | 122.7448 | -123.0148 | -122.9507
1443.3281 | 123.1201 | -59.2896 | 63.5193 | 0.18662 | 0.024565 | 0.012525 | 0.016633 | 0.059257 | -0.0038473 | 0.081213 | -57.3853 | 63.4323 | -59.4543 | -59.4589 | 55.6137 | 3.4012 | -16.0034 | -15.5319 | 63.4415 | -59.5001 | -0.16479 | -0.086975 | 1.9043 | -0.16937 | -7.9056 | -0.21057 | -0.07782 | 2.0691 | 43.2861 | 43.7576 | 114.9033 | 122.7219 | 1.9043 | 122.731 | 62.6907 | -0.21057 | 122.7219 | 1.9043 | 62.6907 | 114.9033 | 122.731 | -122.9736 | -123.0194
1444.3281 | 123.0606 | -59.285 | 63.5239 | 0.24002 | 0.027555 | 0.013806 | 0.01941 | 0.059898 | -0.0027793 | 0.080359 | -57.4127 | 63.5239 | -59.4727 | -59.5184 | 55.5634 | 3.3096 | -15.9119 | -15.6464 | 63.4964 | -59.523 | -0.18768 | 0 | 1.8723 | -0.23346 | -7.9605 | -0.23804 | -0.027466 | 2.0599 | 43.3731 | 43.6386 | 114.8483 | 122.8088 | 1.8723 | 122.7814 | 62.5946 | -0.23804 | 122.8088 | 1.8723 | 62.5946 | 114.8483 | 122.7814 | -122.9965 | -123.0469
1445.375 | 123.0972 | -59.2667 | 63.5605 | 0.13321 | 0.022428 | 0.009534 | 0.012574 | 0.05883 | -0.00064309 | 0.082068 | -57.2067 | 63.5193 | -59.4177 | -59.5093 | 55.6183 | 3.3554 | -15.8936 | -15.6189 | 63.4644 | -59.4772 | -0.15106 | -0.041199 | 2.0599 | -0.24261 | -7.9422 | -0.21057 | -0.096131 | 2.211 | 43.3731 | 43.6478 | 114.8849 | 122.7859 | 2.0599 | 122.731 | 62.6221 | -0.21057 | 122.7859 | 2.0599 | 62.6221 | 114.8849 | 122.731 | -122.9782 | -123.0377
1446.3281 | 123.1064 | -59.2621 | 63.5147 | 0.2095 | 0.02371 | 0.015088 | 0.013642 | 0.060752 | -0.0023519 | 0.082068 | -57.3441 | 63.4552 | -59.4543 | -59.4452 | 55.6229 | 3.3829 | -15.9073 | -15.477 | 63.4827 | -59.4635 | -0.19226 | -0.059509 | 1.918 | -0.1831 | -7.8918 | -0.20142 | -0.032043 | 2.1103 | 43.3548 | 43.7851 | 114.8849 | 122.7173 | 1.918 | 122.7448 | 62.645 | -0.20142 | 122.7173 | 1.918 | 62.645 | 114.8849 | 122.7448 | -122.9691 | -122.9782
1447.3281 | 123.1338 | -59.2712 | 63.5056 | 0.45364 | 0.023283 | 0.015515 | 0.017487 | 0.059257 | -0.0029929 | 0.080786 | -57.3212 | 63.4644 | -59.4131 | -59.436 | 55.6458 | 3.4836 | -15.9622 | -15.4953 | 63.4689 | -59.4681 | -0.14191 | -0.041199 | 1.9501 | -0.16479 | -7.8598 | -0.19684 | -0.036621 | 2.092 | 43.309 | 43.7759 | 114.917 | 122.7356 | 1.9501 | 122.7402 | 62.7548 | -0.19684 | 122.7356 | 1.9501 | 62.7548 | 114.917 | 122.7402 | -122.9187 | -122.9736
1448.3281 | 123.111 | -59.2529 | 63.5147 | 0.24002 | 0.023496 | 0.015729 | 0.016205 | 0.061607 | -0.00021569 | 0.081427 | -57.3349 | 63.4827 | -59.4315 | -59.4543 | 55.4947 | 3.1586 | -15.7791 | -15.303 | 63.4644 | -59.4864 | -0.17853 | -0.032043 | 1.918 | -0.20142 | -8.02 | -0.23346 | -0.050354 | 2.0966 | 43.4738 | 43.9499 | 114.7476 | 122.7356 | 1.918 | 122.7173 | 62.4115 | -0.23346 | 122.7356 | 1.918 | 62.4115 | 114.7476 | 122.7173 | -122.9462 | -123.0011
1449.3281 | 123.0789 | -59.2712 | 63.5147 | 0.20187 | 0.025633 | 0.010602 | 0.017274 | 0.059471 | -0.0019247 | 0.079291 | -57.3578 | 63.5101 | -59.4772 | -59.4498 | 55.6091 | 3.4012 | -15.8798 | -15.4541 | 63.4369 | -59.523 | -0.20599 | -0.004577 | 1.9135 | -0.17853 | -7.9056 | -0.25177 | -0.077819 | 2.1194 | 43.3914 | 43.8171 | 114.8804 | 122.7814 | 1.9135 | 122.7081 | 62.6724 | -0.25177 | 122.7814 | 1.9135 | 62.6724 | 114.8804 | 122.7081 | -122.9919 | -123.0377
1450.3281 | 123.0652 | -59.2758 | 63.533 | 0.22476 | 0.025846 | 0.014234 | 0.018342 | 0.060325 | -0.0019247 | 0.080359 | -57.4173 | 63.5422 | -59.4681 | -59.5139 | 55.5634 | 3.36 | -15.8157 | -15.5319 | 63.4918 | -59.5184 | -0.19226 | 0.009155 | 1.8585 | -0.23804 | -7.9697 | -0.24262 | -0.041199 | 2.0508 | 43.4601 | 43.7439 | 114.8392 | 122.818 | 1.8585 | 122.7676 | 62.6358 | -0.24262 | 122.818 | 1.8585 | 62.6358 | 114.8392 | 122.7676 | -123.0011 | -123.0515
1451.3281 | 123.0148 | -59.3079 | 63.5834 | 0.2858 | 0.024992 | 0.015088 | 0.016633 | 0.06118 | -0.0025657 | 0.082922 | -57.399 | 63.5742 | -59.4543 | -59.5505 | 55.5084 | 3.2181 | -15.7837 | -15.6235 | 63.5284 | -59.5184 | -0.14648 | -0.009155 | 1.9089 | -0.24262 | -8.075 | -0.21057 | -0.054932 | 2.0554 | 43.5242 | 43.6844 | 114.8163 | 122.8821 | 1.9089 | 122.8363 | 62.5259 | -0.21057 | 122.8821 | 1.9089 | 62.5259 | 114.8163 | 122.8363 | -123.0377 | -123.1018
1452.3438 | 122.9691 | -59.2987 | 63.588 | 0.064545 | 0.025633 | 0.015729 | 0.018769 | 0.059898 | -0.00085669 | 0.081213 | -57.4265 | 63.588 | -59.4681 | -59.5093 | 55.5267 | 3.2501 | -15.7837 | -15.6418 | 63.5284 | -59.5322 | -0.16937 | 0 | 1.8723 | -0.21057 | -8.0612 | -0.23346 | -0.05951 | 2.0416 | 43.515 | 43.6569 | 114.8254 | 122.8867 | 1.8723 | 122.8271 | 62.5488 | -0.23346 | 122.8867 | 1.8723 | 62.5488 | 114.8254 | 122.8271 | -123.056 | -123.1201
1453.3281 | 123.0377 | -59.2712 | 63.5422 | 0.20187 | 0.022856 | 0.015943 | 0.015992 | 0.060752 | -0.00064309 | 0.081427 | -57.4265 | 63.5788 | -59.4498 | -59.5093 | 55.5679 | 3.2272 | -15.889 | -15.5502 | 63.4918 | -59.5367 | -0.17853 | 0.036621 | 1.8448 | -0.23804 | -7.9742 | -0.2655 | -0.050354 | 2.0233 | 43.3823 | 43.721 | 114.8392 | 122.85 | 1.8448 | 122.7631 | 62.4985 | -0.2655 | 122.85 | 1.8448 | 62.4985 | 114.8392 | 122.7631 | -122.9919 | -123.0789
1454.3281 | 122.9874 | -59.285 | 63.5742 | 0.17136 | 0.025846 | 0.017011 | 0.01706 | 0.060325 | 0.0023477 | 0.082281 | -57.4265 | 63.5971 | -59.4498 | -59.5413 | 55.5405 | 3.1952 | -15.8157 | -15.6418 | 63.5147 | -59.523 | -0.16479 | 0.022888 | 1.8585 | -0.25635 | -8.0338 | -0.23804 | -0.05951 | 2.0233 | 43.4692 | 43.6432 | 114.8254 | 122.8821 | 1.8585 | 122.7997 | 62.4802 | -0.23804 | 122.8821 | 1.8585 | 62.4802 | 114.8254 | 122.7997 | -123.024 | -123.0972
1455.3281 | 122.9919 | -59.2941 | 63.5422 | 0.1561 | 0.024351 | 0.015515 | 0.014924 | 0.06182 | 0.0029885 | 0.083777 | -57.4493 | 63.6154 | -59.4589 | -59.5551 | 55.5084 | 3.1998 | -15.7974 | -15.5777 | 63.5284 | -59.523 | -0.16479 | 0.073242 | 1.8448 | -0.26093 | -8.0338 | -0.22888 | -0.013733 | 2.0096 | 43.4967 | 43.7164 | 114.8026 | 122.9095 | 1.8448 | 122.8226 | 62.4939 | -0.22888 | 122.9095 | 1.8448 | 62.4939 | 114.8026 | 122.8226 | -123.0011 | -123.0652
1456.3281 | 122.9691 | -59.2941 | 63.5788 | 0.095062 | 0.024992 | 0.01637 | 0.016633 | 0.062034 | 0.0019205 | 0.082068 | -57.4219 | 63.6154 | -59.4543 | -59.5459 | 55.5038 | 3.154 | -15.683 | -15.477 | 63.5056 | -59.5276 | -0.16022 | 0.036621 | 1.8723 | -0.25177 | -8.075 | -0.23346 | -0.073242 | 2.0325 | 43.6111 | 43.8171 | 114.798 | 122.9095 | 1.8723 | 122.7997 | 62.4481 | -0.23346 | 122.9095 | 1.8723 | 62.4481 | 114.798 | 122.7997 | -123.0331 | -123.1064
1457.3281 | 123.0011 | -59.2987 | 63.5559 | 0.17136 | 0.02371 | 0.014661 | 0.018769 | 0.058189 | -0.0012839 | 0.083563 | -57.4631 | 63.6063 | -59.4681 | -59.491 | 55.5588 | 3.1815 | -15.6189 | -15.3946 | 63.5468 | -59.5276 | -0.16937 | 0.050354 | 1.8356 | -0.19226 | -7.9971 | -0.22888 | -0.009155 | 2.005 | 43.6798 | 43.9041 | 114.8575 | 122.905 | 1.8356 | 122.8455 | 62.4802 | -0.22888 | 122.905 | 1.8356 | 62.4802 | 114.8575 | 122.8455 | -123.024 | -123.0835
1458.3281 | 122.9782 | -59.2804 | 63.5788 | 0.026398 | 0.025205 | 0.012097 | 0.017274 | 0.061607 | 0.00063871 | 0.080359 | -57.3898 | 63.6108 | -59.4269 | -59.4864 | 55.545 | 3.1128 | -15.715 | -15.4724 | 63.5468 | -59.5276 | -0.14648 | 0.032044 | 1.8906 | -0.20599 | -8.0338 | -0.24719 | -0.032043 | 2.037 | 43.5654 | 43.808 | 114.8254 | 122.8912 | 1.8906 | 122.8271 | 62.3932 | -0.24719 | 122.8912 | 1.8906 | 62.3932 | 114.8254 | 122.8271 | -123.0057 | -123.1064
1459.3281 | 123.024 | -59.2758 | 63.5925 | 0.056915 | 0.025205 | 0.015515 | 0.016846 | 0.061607 | 0.00063871 | 0.081 | -57.3807 | 63.62 | -59.4269 | -59.4772 | 55.5679 | 3.1677 | -15.7516 | -15.509 | 63.5284 | -59.5093 | -0.15106 | 0.027466 | 1.8951 | -0.20142 | -8.0246 | -0.23346 | -0.064087 | 2.0462 | 43.5242 | 43.7668 | 114.8438 | 122.8958 | 1.8951 | 122.8043 | 62.4435 | -0.23346 | 122.8958 | 1.8951 | 62.4435 | 114.8438 | 122.8043 | -123.0194 | -123.1018
1460.3281 | 122.9782 | -59.2896 | 63.5834 | 0.17899 | 0.025205 | 0.018079 | 0.013642 | 0.064811 | 0.0010659 | 0.079931 | -57.4356 | 63.6429 | -59.4498 | -59.3216 | 55.6 | 3.3279 | -15.6692 | -15.4861 | 63.5468 | -59.5367 | -0.16022 | 0.059509 | 1.8539 | -0.032043 | -7.9834 | -0.24719 | -0.036621 | 2.0142 | 43.6203 | 43.8034 | 114.8895 | 122.9324 | 1.8539 | 122.8363 | 62.6175 | -0.24719 | 122.9324 | 1.8539 | 62.6175 | 114.8895 | 122.8363 | -123.0331 | -123.1201
1461.3281 | 122.9919 | -59.2804 | 63.6017 | 0.011139 | 0.024992 | 0.015302 | 0.015778 | 0.061607 | -0.00064309 | 0.081213 | -57.3807 | 63.62 | -59.4406 | -59.5047 | 55.5634 | 3.2181 | -15.6876 | -15.3214 | 63.5605 | -59.5001 | -0.16022 | 0.01831 | 1.8997 | -0.2243 | -8.0383 | -0.21973 | -0.041199 | 2.0599 | 43.5928 | 43.959 | 114.8438 | 122.9004 | 1.8997 | 122.8409 | 62.4985 | -0.21973 | 122.9004 | 1.8997 | 62.4985 | 114.8438 | 122.8409 | -123.0423 | -123.1018
1462.3281 | 122.9507 | -59.2804 | 63.5742 | 0.064545 | 0.02606 | 0.012738 | 0.017487 | 0.062461 | -0.00064309 | 0.082922 | -57.4081 | 63.6246 | -59.4498 | -59.5322 | 55.5359 | 3.2135 | -15.6143 | -15.3763 | 63.5422 | -59.523 | -0.16937 | 0.050354 | 1.8723 | -0.25177 | -8.0383 | -0.24261 | -0.032044 | 2.0416 | 43.6661 | 43.9041 | 114.8163 | 122.905 | 1.8723 | 122.8226 | 62.4939 | -0.24261 | 122.905 | 1.8723 | 62.4939 | 114.8163 | 122.8226 | -123.024 | -123.0972
1463.3281 | 123.0331 | -59.2529 | 63.5971 | 0.041657 | 0.024778 | 0.016584 | 0.015351 | 0.06182 | 0.00042511 | 0.082708 | -57.4265 | 63.6429 | -59.4269 | -59.5139 | 55.5496 | 3.1998 | -15.6876 | -15.358 | 63.5468 | -59.5139 | -0.17395 | 0.045776 | 1.8265 | -0.26093 | -8.0475 | -0.26093 | -0.050354 | 2.0004 | 43.5654 | 43.895 | 114.8026 | 122.8958 | 1.8265 | 122.7997 | 62.4527 | -0.26093 | 122.8958 | 1.8265 | 62.4527 | 114.8026 | 122.7997 | -123.024 | -123.111
1464.3281 | 123.0377 | -59.2712 | 63.5742 | 0.0035097 | 0.026274 | 0.015302 | 0.017274 | 0.060966 | 0.0017069 | 0.080572 | -57.4081 | 63.6292 | -59.4223 | -59.4818 | 55.5588 | 3.2089 | -15.7516 | -15.3488 | 63.5422 | -59.5139 | -0.15106 | 0.054931 | 1.8631 | -0.21057 | -8.0154 | -0.24262 | -0.032044 | 2.0142 | 43.5196 | 43.9224 | 114.83 | 122.9004 | 1.8631 | 122.8134 | 62.4802 | -0.24262 | 122.9004 | 1.8631 | 62.4802 | 114.83 | 122.8134 | -122.9965 | -123.0881
1465.3281 | 123.0652 | -59.2712 | 63.5834 | -0.11856 | 0.024992 | 0.017224 | 0.015992 | 0.059898 | -0.0025657 | 0.081213 | -57.3944 | 63.6246 | -59.4269 | -59.4727 | 55.6091 | 3.2867 | -15.6784 | -15.3854 | 63.5239 | -59.5093 | -0.15564 | 0.041199 | 1.8768 | -0.20142 | -7.9742 | -0.23804 | -0.059509 | 2.0325 | 43.5928 | 43.8858 | 114.8804 | 122.8958 | 1.8768 | 122.7951 | 62.558 | -0.23804 | 122.8958 | 1.8768 | 62.558 | 114.8804 | 122.7951 | -123.0103 | -123.0927
1466.3281 | 123.0469 | -59.2575 | 63.6063 | -0.095673 | 0.024351 | 0.015302 | 0.015137 | 0.060966 | -0.00042929 | 0.082922 | -57.3898 | 63.652 | -59.4315 | -59.4772 | 55.5954 | 3.241 | -15.6647 | -15.2939 | 63.5559 | -59.5322 | -0.17395 | 0.045777 | 1.8677 | -0.21973 | -8.0109 | -0.27466 | -0.050354 | 2.0416 | 43.5928 | 43.9636 | 114.8529 | 122.9095 | 1.8677 | 122.8134 | 62.4985 | -0.27466 | 122.9095 | 1.8677 | 62.4985 | 114.8529 | 122.8134 | -123.0377 | -123.1384
1467.3438 | 123.0515 | -59.2346 | 63.5971 | -0.18723 | 0.02371 | 0.01402 | 0.0093696 | 0.057334 | 0.00063871 | 0.082708 | -57.3898 | 63.5788 | -59.4315 | -59.4681 | 55.6366 | 3.3417 | -15.5548 | -15.2206 | 63.5239 | -59.4498 | -0.19684 | -0.018311 | 1.8448 | -0.23346 | -7.9605 | -0.21515 | -0.073242 | 2.0416 | 43.6798 | 44.014 | 114.8712 | 122.8134 | 1.8448 | 122.7585 | 62.5763 | -0.21515 | 122.8134 | 1.8448 | 62.5763 | 114.8712 | 122.7585 | -123.0286 | -123.0469
1468.3281 | 123.0606 | -59.2621 | 63.5651 | -0.088043 | 0.025633 | 0.014234 | 0.015565 | 0.061393 | 0.0014933 | 0.082495 | -57.3486 | 63.6246 | -59.4177 | -59.4818 | 55.5954 | 3.241 | -15.6189 | -15.239 | 63.5559 | -59.5184 | -0.15564 | 0.05951 | 1.9135 | -0.21973 | -7.9697 | -0.25635 | -0.009155 | 2.0691 | 43.6432 | 44.0231 | 114.8575 | 122.8867 | 1.9135 | 122.818 | 62.5031 | -0.25635 | 122.8867 | 1.9135 | 62.5031 | 114.8575 | 122.818 | -122.9828 | -123.0835
1469.3281 | 123.0331 | -59.2529 | 63.5696 | -0.065155 | 0.02606 | 0.016156 | 0.016633 | 0.062889 | -0.0017111 | 0.08164 | -57.3715 | 63.6108 | -59.4086 | -59.4543 | 55.6549 | 3.3737 | -15.683 | -15.3076 | 63.5651 | -59.4772 | -0.15564 | 0.041199 | 1.8814 | -0.20142 | -7.9147 | -0.2243 | -0.004578 | 2.037 | 43.5699 | 43.9453 | 114.9078 | 122.8638 | 1.8814 | 122.818 | 62.6266 | -0.2243 | 122.8638 | 1.8814 | 62.6266 | 114.9078 | 122.818 | -122.9782 | -123.0469
1470.3281 | 123.056 | -59.2484 | 63.5971 | -0.11856 | 0.022428 | 0.014661 | 0.01471 | 0.060111 | 0.0010659 | 0.081 | -57.3853 | 63.6383 | -59.4681 | -59.4589 | 55.5817 | 3.2913 | -15.6601 | -15.3671 | 63.5468 | -59.523 | -0.21973 | 0.041199 | 1.8631 | -0.21057 | -8.0154 | -0.27466 | -0.050354 | 2.0828 | 43.5883 | 43.8812 | 114.83 | 122.8867 | 1.8631 | 122.7951 | 62.5397 | -0.27466 | 122.8867 | 1.8631 | 62.5397 | 114.83 | 122.7951 | -123.0652 | -123.1201
1471.3281 | 122.9416 | -59.2484 | 63.5971 | -0.17197 | 0.022642 | 0.011457 | 0.011079 | 0.059471 | 0.00085231 | 0.082068 | -57.4585 | 63.62 | -59.436 | -59.5001 | 55.5588 | 3.2318 | -15.2344 | -15.065 | 63.5971 | -59.4635 | -0.18768 | 0.022888 | 1.7899 | -0.25177 | -8.0383 | -0.21515 | 0 | 1.9775 | 44.014 | 44.1833 | 114.8071 | 122.8683 | 1.7899 | 122.8455 | 62.4802 | -0.21515 | 122.8683 | 1.7899 | 62.4802 | 114.8071 | 122.8455 | -123.0331 | -123.0606
1472.3281 | 123.0011 | -59.2621 | 63.5834 | 0.43839 | 0.024992 | 0.013379 | 0.011719 | 0.060325 | 0.00021151 | 0.080786 | -57.4493 | 63.6292 | -59.4223 | -59.5139 | 55.5496 | 3.2135 | -15.5502 | -15.3442 | 63.5925 | -59.5047 | -0.16022 | 0.045776 | 1.8127 | -0.25177 | -8.0338 | -0.24262 | 0.009155 | 1.973 | 43.7119 | 43.9178 | 114.8117 | 122.8912 | 1.8127 | 122.8546 | 62.4756 | -0.24262 | 122.8912 | 1.8127 | 62.4756 | 114.8117 | 122.8546 | -123.0057 | -123.0881
1473.3281 | 123.0011 | -59.2346 | 63.6108 | -0.19485 | 0.02371 | 0.01402 | 0.012574 | 0.061393 | 0.0019205 | 0.082495 | -57.431 | 63.6063 | -59.4223 | -59.5184 | 55.545 | 3.2364 | -15.6006 | -15.3442 | 63.5513 | -59.4955 | -0.18768 | -0.004578 | 1.8036 | -0.28381 | -8.0658 | -0.26093 | -0.059509 | 1.9913 | 43.634 | 43.8904 | 114.7797 | 122.8409 | 1.8036 | 122.7859 | 62.471 | -0.26093 | 122.8409 | 1.8036 | 62.471 | 114.7797 | 122.7859 | -123.0331 | -123.1064
1474.3438 | 123.1155 | -59.2438 | 63.5513 | 0.018768 | 0.020078 | 0.013593 | 0.0093696 | 0.056693 | -0.0017111 | 0.082281 | -57.4219 | 63.5101 | -59.4452 | -59.4772 | 55.5908 | 3.2455 | -15.715 | -15.303 | 63.5056 | -59.4543 | -0.20142 | -0.041199 | 1.8219 | -0.23346 | -7.9605 | -0.21057 | -0.045777 | 2.0233 | 43.5287 | 43.9407 | 114.8346 | 122.7539 | 1.8219 | 122.7493 | 62.4893 | -0.21057 | 122.7539 | 1.8219 | 62.4893 | 114.8346 | 122.7493 | -122.9965 | -123.0057
1475.3281 | 122.9965 | -59.2438 | 63.6154 | -0.17197 | 0.02371 | 0.016156 | 0.015351 | 0.057121 | -0.00064309 | 0.079291 | -57.4402 | 63.6017 | -59.4223 | -59.5139 | 55.5405 | 3.2043 | -15.5823 | -15.3122 | 63.5925 | -59.4681 | -0.17853 | -0.013732 | 1.8036 | -0.27008 | -8.075 | -0.22431 | -0.022888 | 1.9821 | 43.6615 | 43.9316 | 114.7842 | 122.8455 | 1.8036 | 122.8363 | 62.4481 | -0.22431 | 122.8455 | 1.8036 | 62.4481 | 114.7842 | 122.8363 | -123.0377 | -123.0835
1476.3281 | 123.0148 | -59.2529 | 63.6063 | -0.1796 | 0.022856 | 0.013379 | 0.016846 | 0.060111 | -0.0012839 | 0.079504 | -57.486 | 63.6246 | -59.3948 | -59.5322 | 55.4855 | 3.1815 | -15.6097 | -15.4221 | 63.6108 | -59.4864 | -0.14191 | 0.018311 | 1.767 | -0.27924 | -8.1207 | -0.23346 | 0.004578 | 1.9089 | 43.6432 | 43.8309 | 114.7385 | 122.8775 | 1.767 | 122.8638 | 62.4344 | -0.23346 | 122.8775 | 1.767 | 62.4344 | 114.7385 | 122.8638 | -123.0011 | -123.0927
1477.3281 | 123.0057 | -59.2438 | 63.5971 | -0.20248 | 0.023924 | 0.013379 | 0.012574 | 0.058616 | -0.00042929 | 0.079931 | -57.3898 | 63.5834 | -59.3903 | -59.4772 | 55.5267 | 3.1677 | -15.6097 | -15.3122 | 63.6017 | -59.436 | -0.14648 | -0.013733 | 1.8539 | -0.23346 | -8.0704 | -0.19226 | 0.004578 | 2.0004 | 43.634 | 43.9316 | 114.7705 | 122.8271 | 1.8539 | 122.8455 | 62.4115 | -0.19226 | 122.8271 | 1.8539 | 62.4115 | 114.7705 | 122.8455 | -122.9874 | -123.0331
1478.3438 | 122.9828 | -59.2621 | 63.6108 | 0.11032 | 0.027555 | 0.013379 | 0.018769 | 0.06182 | -0.0010703 | 0.078863 | -57.4081 | 63.6063 | -59.4177 | -59.523 | 55.4993 | 3.1815 | -15.6143 | -15.39 | 63.588 | -59.523 | -0.15564 | -0.004578 | 1.8539 | -0.26093 | -8.1116 | -0.26093 | -0.022888 | 2.0096 | 43.6478 | 43.8721 | 114.7614 | 122.8683 | 1.8539 | 122.85 | 62.4435 | -0.26093 | 122.8683 | 1.8539 | 62.4435 | 114.7614 | 122.85 | -123.0286 | -123.1338
1479.3281 | 123.1293 | -59.2255 | 63.5559 | -0.21774 | 0.019438 | 0.0091068 | 0.006806 | 0.052635 | -0.00064309 | 0.083349 | -57.3257 | 63.5193 | -59.3811 | -59.6237 | 55.5222 | 3.2593 | -15.7745 | -15.2161 | 63.5284 | -59.4223 | -0.15564 | -0.036621 | 1.8997 | -0.39825 | -8.0338 | -0.19684 | -0.027466 | 2.0554 | 43.4509 | 44.0094 | 114.7476 | 122.7448 | 1.8997 | 122.7539 | 62.4847 | -0.19684 | 122.7448 | 1.8997 | 62.4847 | 114.7476 | 122.7539 | -122.937 | -122.9782
1480.3281 | 123.1522 | -59.1843 | 63.5788 | 0.44601 | 0.022428 | 0.013379 | 0.011292 | 0.058402 | -0.0012839 | 0.079077 | -57.2891 | 63.5239 | -59.404 | -59.3536 | 55.6458 | 3.2959 | -15.8432 | -15.1794 | 63.5788 | -59.3903 | -0.21973 | -0.054931 | 1.8951 | -0.16937 | -7.933 | -0.20599 | 0 | 2.1149 | 43.3411 | 44.0048 | 114.83 | 122.7081 | 1.8951 | 122.7631 | 62.4802 | -0.20599 | 122.7081 | 1.8951 | 62.4802 | 114.83 | 122.7631 | -122.9828 | -122.9691
1481.3281 | 123.143 | -59.2163 | 63.588 | -0.080414 | 0.021787 | 0.0084658 | 0.013001 | 0.058616 | -0.0023519 | 0.082068 | -57.3257 | 63.5193 | -59.3674 | -59.3811 | 55.6641 | 3.2227 | -15.8432 | -15.1932 | 63.5788 | -59.4131 | -0.15106 | -0.068665 | 1.8906 | -0.16479 | -7.9239 | -0.19684 | -0.009156 | 2.0416 | 43.3731 | 44.0231 | 114.8804 | 122.7356 | 1.8906 | 122.7951 | 62.439 | -0.19684 | 122.7356 | 1.8906 | 62.439 | 114.8804 | 122.7951 | -122.9553 | -123.0011
1482.3281 | 123.0972 | -59.2026 | 63.5834 | -0.1033 | 0.019865 | 0.0088932 | 0.0093696 | 0.059471 | -0.0010703 | 0.082281 | -57.3166 | 63.4964 | -59.3628 | -59.4177 | 55.6091 | 3.2959 | -15.7288 | -15.152 | 63.5696 | -59.3903 | -0.16022 | -0.086975 | 1.886 | -0.21515 | -7.9742 | -0.18768 | -0.013733 | 2.0462 | 43.4738 | 44.0506 | 114.8117 | 122.699 | 1.886 | 122.7722 | 62.4985 | -0.18768 | 122.699 | 1.886 | 62.4985 | 114.8117 | 122.7722 | -122.9462 | -122.9736
1483.3438 | 123.0469 | -59.2163 | 63.6337 | -0.15671 | 0.022428 | 0.012311 | 0.021332 | 0.058616 | -0.0025657 | 0.079931 | -57.3257 | 63.6154 | -59.3811 | -59.404 | 55.6183 | 3.2867 | -15.8386 | -15.2847 | 63.5788 | -59.4452 | -0.16479 | -0.018311 | 1.8906 | -0.18768 | -8.0154 | -0.22888 | -0.054932 | 2.0554 | 43.3777 | 43.9316 | 114.8346 | 122.8317 | 1.8906 | 122.7951 | 62.5031 | -0.22888 | 122.8317 | 1.8906 | 62.5031 | 114.8346 | 122.7951 | -123.0148 | -123.0789
1484.3281 | 123.1064 | -59.2072 | 63.588 | 0.026398 | 0.019651 | 0.014661 | 0.010438 | 0.058402 | -0.00042929 | 0.080359 | -57.3761 | 63.533 | -59.404 | -59.3948 | 55.6641 | 3.2547 | -15.8203 | -15.152 | 63.5559 | -59.4086 | -0.19684 | -0.054932 | 1.8311 | -0.18768 | -7.9239 | -0.20142 | -0.032044 | 2.0279 | 43.3868 | 44.0552 | 114.8712 | 122.7402 | 1.8311 | 122.7631 | 62.4619 | -0.20142 | 122.7402 | 1.8311 | 62.4619 | 114.8712 | 122.7631 | -122.9919 | -122.9965
1485.3281 | 123.0515 | -59.2117 | 63.5742 | 0.13321 | 0.023283 | 0.011029 | 0.013215 | 0.057548 | -0.00085669 | 0.082068 | -57.3898 | 63.5147 | -59.3994 | -59.4452 | 55.6091 | 3.2501 | -15.8157 | -15.2802 | 63.5742 | -59.404 | -0.18768 | -0.05951 | 1.8219 | -0.23346 | -7.9651 | -0.19226 | 0 | 2.0096 | 43.396 | 43.9316 | 114.8209 | 122.7264 | 1.8219 | 122.7859 | 62.4619 | -0.19226 | 122.7264 | 1.8219 | 62.4619 | 114.8209 | 122.7859 | -122.9736 | -122.9782
1486.3281 | 123.0789 | -59.2072 | 63.5788 | 0.16373 | 0.022428 | 0.011884 | 0.013215 | 0.059471 | -0.0023519 | 0.080786 | -57.3669 | 63.5101 | -59.3765 | -59.4315 | 55.6274 | 3.2272 | -15.7516 | -15.1566 | 63.5742 | -59.4131 | -0.16937 | -0.068664 | 1.8402 | -0.22431 | -7.9514 | -0.20599 | -0.004577 | 2.0096 | 43.4555 | 44.0506 | 114.8346 | 122.7173 | 1.8402 | 122.7814 | 62.4344 | -0.20599 | 122.7173 | 1.8402 | 62.4344 | 114.8346 | 122.7814 | -122.9553 | -122.9919
1487.3281 | 123.0881 | -59.1705 | 63.6063 | 0.11795 | 0.023496 | 0.011457 | 0.010438 | 0.058616 | -0.0038473 | 0.081427 | -57.3761 | 63.5239 | -59.3674 | -59.4269 | 55.6412 | 3.186 | -15.6784 | -15.0742 | 63.5925 | -59.3903 | -0.19684 | -0.082397 | 1.7944 | -0.25635 | -7.9651 | -0.21973 | -0.013733 | 1.9913 | 43.4921 | 44.0964 | 114.8117 | 122.6944 | 1.7944 | 122.7631 | 62.3566 | -0.21973 | 122.6944 | 1.7944 | 62.3566 | 114.8117 | 122.7631 | -122.9736 | -122.9965
1488.3438 | 122.9919 | -59.2392 | 63.6154 | 0.072174 | 0.022856 | 0.012097 | 0.018128 | 0.059257 | -0.0025657 | 0.078436 | -57.3898 | 63.6154 | -59.3719 | -59.4452 | 55.5908 | 3.2135 | -15.4724 | -15.0742 | 63.6658 | -59.4269 | -0.13275 | 0 | 1.8494 | -0.20599 | -8.0246 | -0.18768 | 0.050354 | 1.9821 | 43.7668 | 44.165 | 114.83 | 122.8546 | 1.8494 | 122.905 | 62.4527 | -0.18768 | 122.8546 | 1.8494 | 62.4527 | 114.83 | 122.905 | -122.9874 | -123.0423
1489.3281 | 123.0423 | -59.2117 | 63.588 | 0.14084 | 0.02136 | 0.012525 | 0.011719 | 0.059257 | -0.00021569 | 0.082068 | -57.3669 | 63.5101 | -59.4223 | -59.4406 | 55.6137 | 3.3142 | -15.683 | -15.065 | 63.5513 | -59.4269 | -0.21057 | -0.07782 | 1.8448 | -0.22888 | -7.9742 | -0.21515 | -0.036621 | 2.0554 | 43.5287 | 44.1467 | 114.8254 | 122.7219 | 1.8448 | 122.7631 | 62.5259 | -0.21515 | 122.7219 | 1.8448 | 62.5259 | 114.8254 | 122.7631 | -123.0103 | -123.0148
1490.3281 | 123.0606 | -59.2026 | 63.5696 | 0.17136 | 0.021787 | 0.013379 | 0.013856 | 0.05883 | -0.0017111 | 0.082495 | -57.3486 | 63.5101 | -59.3765 | -59.4223 | 55.632 | 3.3508 | -15.7837 | -15.1611 | 63.5422 | -59.404 | -0.17395 | -0.059509 | 1.8539 | -0.21973 | -7.9376 | -0.20142 | -0.027466 | 2.0279 | 43.4189 | 44.0414 | 114.8346 | 122.7127 | 1.8539 | 122.7448 | 62.5534 | -0.20142 | 122.7127 | 1.8539 | 62.5534 | 114.8346 | 122.7448 | -122.9462 | -122.9736
1491.3281 | 123.0972 | -59.2117 | 63.588 | 0.17899 | 0.021787 | 0.013166 | 0.017701 | 0.057548 | -0.0019247 | 0.080359 | -57.3441 | 63.5376 | -59.3765 | -59.3765 | 55.6641 | 3.3737 | -15.7242 | -15.0742 | 63.5239 | -59.4269 | -0.16479 | -0.050354 | 1.8677 | -0.16479 | -7.9239 | -0.21515 | -0.064087 | 2.0325 | 43.4875 | 44.1376 | 114.8758 | 122.7493 | 1.8677 | 122.7356 | 62.5854 | -0.21515 | 122.7493 | 1.8677 | 62.5854 | 114.8758 | 122.7356 | -122.9645 | -123.0148
1492.3281 | 123.0148 | -59.2438 | 63.5971 | 0.20187 | 0.024137 | 0.012952 | 0.019837 | 0.059684 | 0.00021151 | 0.081213 | -57.3853 | 63.6292 | -59.4086 | -59.4772 | 55.5771 | 3.1952 | -15.6967 | -15.2161 | 63.6063 | -59.4498 | -0.16479 | 0.032043 | 1.8585 | -0.23346 | -8.02 | -0.20599 | 0.009155 | 2.0233 | 43.5471 | 44.0277 | 114.8209 | 122.8729 | 1.8585 | 122.85 | 62.439 | -0.20599 | 122.8729 | 1.8585 | 62.439 | 114.8209 | 122.85 | -123.0057 | -123.0469
1493.3438 | 123.1064 | -59.1934 | 63.5971 | 0.018768 | 0.018583 | 0.0065432 | 0.010438 | 0.057334 | -0.0019247 | 0.080786 | -57.3898 | 63.5147 | -59.3857 | -59.3948 | 55.6641 | 3.2043 | -15.7471 | -15.1245 | 63.5605 | -59.3903 | -0.19226 | -0.082398 | 1.8036 | -0.20142 | -7.933 | -0.19684 | -0.036621 | 1.9958 | 43.4464 | 44.0689 | 114.8575 | 122.7081 | 1.8036 | 122.7539 | 62.3978 | -0.19684 | 122.7081 | 1.8036 | 62.3978 | 114.8575 | 122.7539 | -122.9828 | -122.9874
1494.3281 | 123.1018 | -59.2209 | 63.6063 | 0.21713 | 0.022856 | 0.015515 | 0.016419 | 0.062461 | -0.00064309 | 0.081854 | -57.3578 | 63.5788 | -59.3765 | -59.404 | 55.6549 | 3.2867 | -15.802 | -15.2115 | 63.5605 | -59.4315 | -0.15564 | -0.027466 | 1.8631 | -0.18311 | -7.9514 | -0.21057 | -0.045776 | 2.0187 | 43.4189 | 44.0094 | 114.8758 | 122.7997 | 1.8631 | 122.7814 | 62.5076 | -0.21057 | 122.7997 | 1.8631 | 62.5076 | 114.8758 | 122.7814 | -122.9828 | -123.0377
1495.3281 | 123.1613 | -59.2117 | 63.5971 | 0.19424 | 0.023283 | 0.01402 | 0.013428 | 0.059684 | -0.0017111 | 0.081427 | -57.3074 | 63.5513 | -59.3811 | -59.3903 | 55.6641 | 3.2639 | -15.7425 | -15.2252 | 63.5239 | -59.4772 | -0.16937 | -0.045776 | 1.9043 | -0.17853 | -7.933 | -0.2655 | -0.073242 | 2.0737 | 43.4692 | 43.9865 | 114.8758 | 122.7631 | 1.9043 | 122.7356 | 62.4756 | -0.2655 | 122.7631 | 1.9043 | 62.4756 | 114.8758 | 122.7356 | -122.9782 | -123.0743
1496.3281 | 123.0331 | -59.23 | 63.62 | 0.17136 | 0.025633 | 0.01402 | 0.019196 | 0.061607 | -0.00021569 | 0.079077 | -57.4081 | 63.652 | -59.3948 | -59.491 | 55.5862 | 3.1723 | -15.6052 | -15.2161 | 63.5971 | -59.4498 | -0.16479 | 0.032044 | 1.8219 | -0.26093 | -8.0338 | -0.21973 | -0.022888 | 1.9867 | 43.6249 | 44.014 | 114.8163 | 122.8821 | 1.8219 | 122.8271 | 62.4023 | -0.21973 | 122.8821 | 1.8219 | 62.4023 | 114.8163 | 122.8271 | -123.0148 | -123.0698
1497.3281 | 123.0331 | -59.2438 | 63.5925 | 0.19424 | 0.024992 | 0.017224 | 0.017914 | 0.060752 | 0.0012795 | 0.083136 | -57.3853 | 63.6475 | -59.3948 | -59.4727 | 55.6229 | 3.1586 | -15.5869 | -15.1474 | 63.5468 | -59.4727 | -0.15106 | 0.054932 | 1.8585 | -0.22888 | -7.9697 | -0.22888 | -0.045776 | 2.0096 | 43.6569 | 44.0964 | 114.8666 | 122.8912 | 1.8585 | 122.7905 | 62.4023 | -0.22888 | 122.8912 | 1.8585 | 62.4023 | 114.8666 | 122.7905 | -122.9874 | -123.0652
1498.3281 | 123.0515 | -59.2255 | 63.6017 | 0.24002 | 0.026487 | 0.014234 | 0.015351 | 0.060752 | -0.00021569 | 0.082708 | -57.3853 | 63.6429 | -59.3857 | -59.4406 | 55.6366 | 3.1769 | -15.6921 | -15.1382 | 63.5696 | -59.4589 | -0.16022 | 0.041198 | 1.8402 | -0.21515 | -7.9651 | -0.23346 | -0.032044 | 2.0004 | 43.5333 | 44.0872 | 114.8621 | 122.8683 | 1.8402 | 122.7951 | 62.4023 | -0.23346 | 122.8683 | 1.8402 | 62.4023 | 114.8621 | 122.7951 | -122.9874 | -123.0606
1499.3594 | 123.0148 | -59.23 | 63.6475 | -0.15671 | 0.024565 | 0.012952 | 0.01471 | 0.060111 | -0.0017111 | 0.081427 | -57.4265 | 63.652 | -59.4131 | -59.4635 | 55.5862 | 3.2593 | -15.477 | -15.1199 | 63.6063 | -59.4406 | -0.18311 | 0.004578 | 1.8036 | -0.23346 | -8.0612 | -0.21057 | -0.041199 | 1.9867 | 43.7531 | 44.1101 | 114.8163 | 122.8821 | 1.8036 | 122.8363 | 62.4893 | -0.21057 | 122.8821 | 1.8036 | 62.4893 | 114.8163 | 122.8363 | -123.0606 | -123.0881
1500.3281 | 122.9965 | -59.2117 | 63.6383 | 0.064545 | 0.025633 | 0.015515 | 0.018128 | 0.06118 | -0.00085669 | 0.082495 | -57.3486 | 63.6658 | -59.3857 | -59.4452 | 55.6 | 3.2593 | -15.4861 | -15.1245 | 63.5742 | -59.4681 | -0.17395 | 0.027465 | 1.8631 | -0.23346 | -8.0383 | -0.25635 | -0.064087 | 2.037 | 43.7256 | 44.0872 | 114.8117 | 122.8775 | 1.8631 | 122.7859 | 62.471 | -0.25635 | 122.8775 | 1.8631 | 62.471 | 114.8117 | 122.7859 | -123.024 | -123.1064
1501.3594 | 123.0469 | -59.2209 | 63.5971 | 0.20187 | 0.024992 | 0.010388 | 0.016205 | 0.061393 | -0.00042929 | 0.082281 | -57.3898 | 63.6292 | -59.4223 | -59.4727 | 55.5954 | 3.1998 | -15.564 | -14.9963 | 63.5742 | -59.436 | -0.20142 | 0.032043 | 1.8311 | -0.25177 | -8.0017 | -0.21515 | -0.022888 | 2.0325 | 43.6569 | 44.2245 | 114.8163 | 122.85 | 1.8311 | 122.7951 | 62.4207 | -0.21515 | 122.85 | 1.8311 | 62.4207 | 114.8163 | 122.7951 | -123.0194 | -123.0331
1502.3281 | 122.9691 | -59.2117 | 63.6292 | 0.11032 | 0.023069 | 0.012311 | 0.015565 | 0.061393 | -0.0029929 | 0.081213 | -57.4127 | 63.6932 | -59.4177 | -59.4864 | 55.5725 | 3.1082 | -15.509 | -15.097 | 63.6108 | -59.4498 | -0.20599 | 0.064087 | 1.799 | -0.27466 | -8.0566 | -0.23804 | -0.01831 | 2.005 | 43.7027 | 44.1147 | 114.7842 | 122.905 | 1.799 | 122.8226 | 62.3199 | -0.23804 | 122.905 | 1.799 | 62.3199 | 114.7842 | 122.8226 | -123.0469 | -123.0789
1503.3438 | 123.0743 | -59.2026 | 63.6566 | -0.12619 | 0.026487 | 0.015302 | 0.017274 | 0.060752 | -0.0029929 | 0.078863 | -57.3486 | 63.6749 | -59.3674 | -59.3948 | 55.4718 | 3.0899 | -15.3946 | -14.9048 | 63.6337 | -59.4452 | -0.16479 | 0.018311 | 1.8539 | -0.19226 | -8.1848 | -0.24261 | -0.022888 | 2.0187 | 43.808 | 44.2978 | 114.6744 | 122.8775 | 1.8539 | 122.8363 | 62.2925 | -0.24261 | 122.8775 | 1.8539 | 62.2925 | 114.6744 | 122.8363 | -123.024 | -123.1018
1504.3281 | 123.0286 | -59.2255 | 63.6566 | 0.0035097 | 0.024565 | 0.019147 | 0.018555 | 0.062675 | 0.00042511 | 0.081427 | -57.3486 | 63.6749 | -59.404 | -59.4131 | 55.6274 | 3.2227 | -15.6372 | -15.0558 | 63.6063 | -59.4543 | -0.17853 | 0.018311 | 1.8768 | -0.18768 | -8.0292 | -0.22888 | -0.050354 | 2.0554 | 43.5883 | 44.1696 | 114.8529 | 122.9004 | 1.8768 | 122.8317 | 62.4481 | -0.22888 | 122.9004 | 1.8768 | 62.4481 | 114.8529 | 122.8317 | -123.0606 | -123.111
1505.3438 | 123.1018 | -59.1705 | 63.6108 | -0.057526 | 0.022428 | 0.0069706 | 0.0048834 | 0.059043 | -0.0040609 | 0.082068 | -57.3944 | 63.5513 | -59.3857 | -59.404 | 55.719 | 3.3142 | -15.7516 | -15.0192 | 63.5788 | -59.3994 | -0.21515 | -0.059509 | 1.7761 | -0.23346 | -7.8918 | -0.22888 | -0.032044 | 1.9913 | 43.4189 | 44.1513 | 114.8895 | 122.7219 | 1.7761 | 122.7493 | 62.4847 | -0.22888 | 122.7219 | 1.7761 | 62.4847 | 114.8895 | 122.7493 | -122.9965 | -123.0103
1506.3281 | 123.0377 | -59.1797 | 63.6658 | -0.14145 | 0.022428 | 0.016584 | 0.01706 | 0.059043 | -0.00021569 | 0.08164 | -57.3624 | 63.6658 | -59.3719 | -59.4543 | 55.6 | 3.1723 | -15.5273 | -15.0879 | 63.6475 | -59.4269 | -0.19226 | 0 | 1.8173 | -0.27466 | -8.0658 | -0.24719 | -0.01831 | 2.0096 | 43.6523 | 44.0918 | 114.7797 | 122.8455 | 1.8173 | 122.8271 | 62.352 | -0.24719 | 122.8455 | 1.8173 | 62.352 | 114.7797 | 122.8271 | -123.0377 | -123.0927
1507.3594 | 122.9919 | -59.2438 | 63.62 | 0.12558 | 0.026701 | 0.011029 | 0.017274 | 0.060111 | 0.00063871 | 0.083777 | -57.3944 | 63.6703 | -59.3811 | -59.4864 | 55.5496 | 3.1677 | -15.5594 | -15.1108 | 63.5971 | -59.4772 | -0.13733 | 0.050354 | 1.8494 | -0.24262 | -8.0704 | -0.23346 | -0.022888 | 1.9867 | 43.6844 | 44.133 | 114.7934 | 122.9141 | 1.8494 | 122.8409 | 62.4115 | -0.23346 | 122.9141 | 1.8494 | 62.4115 | 114.7934 | 122.8409 | -123.0011 | -123.0972
1508.3281 | 123.0377 | -59.2255 | 63.6383 | -0.11093 | 0.023283 | 0.019361 | 0.016205 | 0.06182 | 0.00042511 | 0.079504 | -57.3532 | 63.6932 | -59.3765 | -59.4086 | 55.632 | 3.2639 | -15.5777 | -15.0284 | 63.6108 | -59.436 | -0.15106 | 0.054931 | 1.8723 | -0.1831 | -8.0063 | -0.21057 | -0.027466 | 2.0233 | 43.6478 | 44.1971 | 114.8575 | 122.9187 | 1.8723 | 122.8363 | 62.4893 | -0.21057 | 122.9187 | 1.8723 | 62.4893 | 114.8575 | 122.8363 | -123.0148 | -123.0743
1509.3438 | 123.1567 | -59.1568 | 63.62 | -0.095673 | 0.022428 | 0.0091068 | 0.0078742 | 0.059043 | -0.00042929 | 0.082708 | -57.3532 | 63.5742 | -59.3308 | -59.3582 | 55.6961 | 3.2639 | -15.7242 | -14.8636 | 63.6154 | -59.3445 | -0.17395 | -0.045776 | 1.8036 | -0.20142 | -7.9239 | -0.18768 | -0.004578 | 1.9775 | 43.4326 | 44.2932 | 114.8529 | 122.731 | 1.8036 | 122.7722 | 62.4207 | -0.18768 | 122.731 | 1.8036 | 62.4207 | 114.8529 | 122.7722 | -122.9507 | -122.9645
1510.3281 | 123.0148 | -59.198 | 63.6658 | -0.14908 | 0.023283 | 0.014661 | 0.013856 | 0.060752 | -0.0034201 | 0.081854 | -57.3853 | 63.6795 | -59.3765 | -59.4269 | 55.6046 | 3.1311 | -15.5273 | -15.0513 | 63.6658 | -59.4315 | -0.17853 | 0.013733 | 1.8127 | -0.22888 | -8.0612 | -0.23346 | 0 | 1.9913 | 43.6707 | 44.1467 | 114.8026 | 122.8775 | 1.8127 | 122.8638 | 62.3291 | -0.23346 | 122.8775 | 1.8127 | 62.3291 | 114.8026 | 122.8638 | -123.0423 | -123.0972
1511.3438 | 123.0927 | -59.1843 | 63.6063 | 0.20187 | 0.022001 | 0.014234 | 0.010651 | 0.062675 | -0.0021383 | 0.081213 | -57.3532 | 63.5513 | -59.3811 | -59.4315 | 55.6549 | 3.2501 | -15.77 | -14.9826 | 63.5925 | -59.3811 | -0.19684 | -0.054931 | 1.8311 | -0.24719 | -7.9514 | -0.19684 | -0.013733 | 2.0279 | 43.4143 | 44.2017 | 114.8392 | 122.7356 | 1.8311 | 122.7768 | 62.4344 | -0.19684 | 122.7356 | 1.8311 | 62.4344 | 114.8392 | 122.7768 | -122.9874 | -122.9874
1512.3281 | 122.9599 | -59.1843 | 63.707 | -0.21011 | 0.022001 | 0.010816 | 0.014924 | 0.056907 | -0.0012839 | 0.081427 | -57.3761 | 63.6246 | -59.3582 | -59.4269 | 55.6229 | 3.1403 | -15.5594 | -14.9506 | 63.6566 | -59.3948 | -0.17395 | -0.082397 | 1.8082 | -0.24261 | -8.0841 | -0.21057 | -0.050354 | 1.9821 | 43.6249 | 44.2337 | 114.8071 | 122.8088 | 1.8082 | 122.8409 | 62.3245 | -0.21057 | 122.8088 | 1.8082 | 62.3245 | 114.8071 | 122.8409 | -123.0652 | -123.1018
1513.3438 | 122.9919 | -59.1705 | 63.6795 | -0.13382 | 0.024137 | 0.011457 | 0.016633 | 0.057334 | -0.0012839 | 0.080572 | -57.3715 | 63.6795 | -59.3719 | -59.4269 | 55.6137 | 3.1998 | -15.5685 | -15.0101 | 63.652 | -59.4177 | -0.20142 | 0 | 1.799 | -0.25635 | -8.0658 | -0.24719 | -0.027465 | 2.0004 | 43.602 | 44.1605 | 114.7842 | 122.85 | 1.799 | 122.8226 | 62.3703 | -0.24719 | 122.85 | 1.799 | 62.3703 | 114.7842 | 122.8226 | -123.0515 | -123.0972
1514.3281 | 123.1338 | -59.1614 | 63.6246 | 0.70541 | 0.022856 | 0.010602 | 0.013428 | 0.057548 | -0.0012839 | 0.082068 | -57.3578 | 63.5559 | -59.3308 | -59.3353 | 55.7602 | 3.2776 | -15.7379 | -14.8178 | 63.5834 | -59.3719 | -0.16937 | -0.068665 | 1.8036 | -0.17395 | -7.8644 | -0.21057 | -0.041199 | 1.973 | 43.4235 | 44.3436 | 114.9216 | 122.7173 | 1.8036 | 122.7448 | 62.439 | -0.21057 | 122.7173 | 1.8036 | 62.439 | 114.9216 | 122.7448 | -122.9553 | -122.9965
1515.3594 | 123.0377 | -59.1385 | 63.6703 | -0.19485 | 0.020292 | 0.016797 | 0.012574 | 0.058616 | -0.0025657 | 0.084631 | -57.3212 | 63.6154 | -59.3491 | -59.3811 | 55.7053 | 3.1952 | -15.6418 | -14.9734 | 63.6475 | -59.3857 | -0.21057 | -0.054932 | 1.8173 | -0.24262 | -7.9651 | -0.24719 | -0.022888 | 2.0279 | 43.4967 | 44.165 | 114.8438 | 122.7539 | 1.8173 | 122.7859 | 62.3337 | -0.24719 | 122.7539 | 1.8173 | 62.3337 | 114.8438 | 122.7859 | -123.0194 | -123.056
1516.3281 | 123.0972 | -59.1431 | 63.6383 | -0.15671 | 0.019224 | 0.018293 | 0.013215 | 0.057762 | -0.0021383 | 0.078222 | -57.3166 | 63.5605 | -59.3308 | -59.3216 | 55.7556 | 3.2227 | -15.7288 | -14.8727 | 63.6383 | -59.3536 | -0.18768 | -0.07782 | 1.8265 | -0.17853 | -7.8827 | -0.21057 | 0 | 2.0142 | 43.4143 | 44.2703 | 114.8987 | 122.7036 | 1.8265 | 122.7814 | 62.3657 | -0.21057 | 122.7036 | 1.8265 | 62.3657 | 114.8987 | 122.7814 | -122.9691 | -122.9919
1517.3438 | 123.1064 | -59.1522 | 63.6337 | -0.011749 | 0.020933 | 0.010602 | 0.010651 | 0.05648 | -0.0014975 | 0.08164 | -57.3303 | 63.5559 | -59.3674 | -59.3674 | 55.6961 | 3.2547 | -15.7837 | -15.0009 | 63.5971 | -59.3445 | -0.21515 | -0.07782 | 1.8219 | -0.21515 | -7.9376 | -0.19226 | -0.036621 | 2.037 | 43.3685 | 44.1513 | 114.8483 | 122.7081 | 1.8219 | 122.7493 | 62.4069 | -0.19226 | 122.7081 | 1.8219 | 62.4069 | 114.8483 | 122.7493 | -123.0011 | -122.9782
1518.3281 | 123.1476 | -59.1385 | 63.6475 | -0.12619 | 0.020078 | 0.0091068 | 0.011933 | 0.056907 | -0.0025657 | 0.081 | -57.3166 | 63.5788 | -59.3491 | -59.317 | 55.7327 | 3.2593 | -15.8066 | -14.946 | 63.62 | -59.3262 | -0.21057 | -0.068665 | 1.8219 | -0.17853 | -7.9147 | -0.18768 | -0.027466 | 2.0325 | 43.3319 | 44.1925 | 114.8712 | 122.7173 | 1.8219 | 122.7585 | 62.3978 | -0.18768 | 122.7173 | 1.8219 | 62.3978 | 114.8712 | 122.7585 | -122.9965 | -122.9736
1519.3594 | 123.1338 | -59.111 | 63.6429 | -0.39322 | 0.022856 | 0.014875 | 0.015137 | 0.059043 | -0.0042747 | 0.078863 | -57.3257 | 63.5559 | -59.3445 | -59.3033 | 55.7236 | 3.3325 | -15.7654 | -14.9094 | 63.6154 | -59.3353 | -0.23346 | -0.086975 | 1.7853 | -0.19226 | -7.9193 | -0.2243 | -0.027466 | 2.0187 | 43.3456 | 44.2017 | 114.8346 | 122.6669 | 1.7853 | 122.7264 | 62.4435 | -0.2243 | 122.6669 | 1.7853 | 62.4435 | 114.8346 | 122.7264 | -122.9874 | -122.9782
1520.3281 | 123.0698 | -59.1843 | 63.6475 | 0.049286 | 0.020506 | 0.010602 | 0.01471 | 0.057975 | -0.00042929 | 0.083349 | -57.2708 | 63.5788 | -59.3445 | -59.3857 | 55.6091 | 3.1036 | -15.7562 | -15.0146 | 63.62 | -59.3765 | -0.16022 | -0.068665 | 1.9135 | -0.20142 | -8.0383 | -0.19226 | -0.027466 | 2.0737 | 43.428 | 44.1696 | 114.7934 | 122.7631 | 1.9135 | 122.8043 | 62.2879 | -0.19226 | 122.7631 | 1.9135 | 62.2879 | 114.7934 | 122.8043 | -122.9919 | -123.024
1521.5156 | 123.0698 | -59.1476 | 63.6154 | 0.17136 | 0.022642 | 0.011457 | 0.015565 | 0.057334 | -0.0012839 | 0.082922 | -57.3257 | 63.5468 | -59.3262 | -59.3948 | 55.6366 | 3.1815 | -15.7791 | -14.9826 | 63.5834 | -59.3857 | -0.17853 | -0.068664 | 1.8219 | -0.24719 | -7.9788 | -0.23804 | -0.032043 | 2.0004 | 43.3685 | 44.165 | 114.7842 | 122.6944 | 1.8219 | 122.731 | 62.3291 | -0.23804 | 122.6944 | 1.8219 | 62.3291 | 114.7842 | 122.731 | -122.9416 | -123.0011
1522.3281 | 123.1201 | -59.1476 | 63.6337 | 0.034027 | 0.020078 | 0.012311 | 0.013642 | 0.054771 | -0.0029929 | 0.081 | -57.3807 | 63.5605 | -59.3536 | -59.3811 | 55.6595 | 3.2455 | -15.7104 | -14.9597 | 63.5651 | -59.3765 | -0.20599 | -0.073242 | 1.767 | -0.23346 | -7.9742 | -0.22888 | -0.068665 | 1.973 | 43.4372 | 44.1879 | 114.8071 | 122.7081 | 1.767 | 122.7127 | 62.3932 | -0.22888 | 122.7081 | 1.767 | 62.3932 | 114.8071 | 122.7127 | -122.9874 | -123.0103
1523.3281 | 123.0606 | -59.166 | 63.6429 | -0.27878 | 0.02136 | 0.013166 | 0.01471 | 0.055625 | -0.0010703 | 0.082495 | -57.3715 | 63.5605 | -59.3445 | -59.3994 | 55.6366 | 3.2089 | -15.7425 | -15.0421 | 63.6017 | -59.3628 | -0.17853 | -0.082397 | 1.7944 | -0.23346 | -8.0063 | -0.19684 | -0.041198 | 1.973 | 43.4235 | 44.1238 | 114.8026 | 122.7264 | 1.7944 | 122.7676 | 62.3749 | -0.19684 | 122.7264 | 1.7944 | 62.3749 | 114.8026 | 122.7676 | -122.9874 | -123.0057
1524.3281 | 123.0881 | -59.1614 | 63.6383 | 0.079804 | 0.022001 | 0.012525 | 0.013001 | 0.056907 | -0.0027793 | 0.081213 | -57.3624 | 63.5513 | -59.3445 | -59.3857 | 55.6229 | 3.0853 | -15.5594 | -14.9734 | 63.62 | -59.3811 | -0.1831 | -0.086975 | 1.799 | -0.2243 | -8.0154 | -0.21973 | -0.018311 | 1.9821 | 43.602 | 44.1879 | 114.7842 | 122.7127 | 1.799 | 122.7814 | 62.2467 | -0.21973 | 122.7127 | 1.799 | 62.2467 | 114.7842 | 122.7814 | -122.9828 | -123.0194
1525.3281 | 123.1018 | -59.1568 | 63.6749 | -0.019379 | 0.018583 | 0.012525 | 0.013215 | 0.055625 | -0.0014975 | 0.079931 | -57.3257 | 63.5605 | -59.3262 | -59.3262 | 55.7236 | 3.1769 | -15.6784 | -14.8727 | 63.6017 | -59.3674 | -0.16937 | -0.11444 | 1.8311 | -0.16937 | -7.9514 | -0.21057 | -0.073242 | 2.0004 | 43.4784 | 44.2841 | 114.8804 | 122.7173 | 1.8311 | 122.7585 | 62.3337 | -0.21057 | 122.7173 | 1.8311 | 62.3337 | 114.8804 | 122.7585 | -123.0011 | -123.0423
1526.3281 | 123.1018 | -59.1843 | 63.6063 | 0.16373 | 0.022001 | 0.013166 | 0.013856 | 0.056693 | -0.00021569 | 0.082281 | -57.3212 | 63.5559 | -59.3719 | -59.3674 | 55.6732 | 3.1631 | -15.6738 | -14.8819 | 63.5696 | -59.3948 | -0.18768 | -0.050354 | 1.8631 | -0.18311 | -7.933 | -0.21057 | -0.036621 | 2.0508 | 43.5104 | 44.3024 | 114.8575 | 122.7402 | 1.8631 | 122.7539 | 62.3474 | -0.21057 | 122.7402 | 1.8631 | 62.3474 | 114.8575 | 122.7539 | -122.9782 | -123.0011
1527.3281 | 123.0881 | -59.166 | 63.62 | 0.21713 | 0.024778 | 0.012311 | 0.019837 | 0.05883 | -0.0014975 | 0.078436 | -57.3807 | 63.6337 | -59.3582 | -59.3857 | 55.6366 | 3.1174 | -15.8203 | -15.0925 | 63.5971 | -59.4131 | -0.19226 | 0.013733 | 1.7853 | -0.21973 | -7.9834 | -0.24719 | -0.022888 | 1.9775 | 43.3456 | 44.0735 | 114.8026 | 122.7997 | 1.7853 | 122.7631 | 62.2833 | -0.24719 | 122.7997 | 1.7853 | 62.2833 | 114.8026 | 122.7631 | -122.9782 | -123.0331
1528.3281 | 123.111 | -59.166 | 63.5925 | 0.21713 | 0.024137 | 0.012738 | 0.017914 | 0.062034 | 0.00063871 | 0.081213 | -57.3257 | 63.62 | -59.3811 | -59.3765 | 55.6366 | 3.0991 | -15.8478 | -15.0467 | 63.5788 | -59.3948 | -0.21515 | 0.027466 | 1.8402 | -0.21057 | -7.9559 | -0.22888 | -0.013733 | 2.0554 | 43.3182 | 44.1193 | 114.8026 | 122.7859 | 1.8402 | 122.7448 | 62.265 | -0.22888 | 122.7859 | 1.8402 | 62.265 | 114.8026 | 122.7448 | -122.9736 | -122.9874
1529.3281 | 123.1155 | -59.166 | 63.6063 | 0.17136 | 0.020933 | 0.012952 | 0.016419 | 0.059043 | -0.0027793 | 0.082708 | -57.3441 | 63.5788 | -59.3399 | -59.3399 | 55.6778 | 3.1631 | -15.5731 | -14.8819 | 63.5696 | -59.404 | -0.17395 | -0.027466 | 1.8219 | -0.17395 | -7.9285 | -0.23804 | -0.036621 | 1.9959 | 43.5928 | 44.2841 | 114.8438 | 122.7448 | 1.8219 | 122.7356 | 62.3291 | -0.23804 | 122.7448 | 1.8219 | 62.3291 | 114.8438 | 122.7356 | -122.9462 | -123.0103
1530.3281 | 123.1064 | -60.3973 | 62.3795 | -0.65262 | 0.023924 | 0.0080386 | 0.019623 | 0.058189 | -2.092e-06 | 0.083777 | -58.5754 | 62.3337 | -60.553 | -60.5759 | 54.776 | 5.3604 | 52.8854 | 6.3217 | 62.3291 | -60.6354 | -0.15564 | -0.045777 | 1.8219 | -0.17853 | -7.6035 | -0.23804 | -0.050354 | 1.9775 | 113.2828 | 66.7191 | 115.1733 | 122.731 | 1.8219 | 122.7264 | 65.7578 | -0.23804 | 122.731 | 1.8219 | 65.7578 | 115.1733 | 122.7264 | -122.9324 | -123.0148
1531.3281 | 123.1338 | -60.4385 | 62.3199 | 0.24765 | 0.024778 | 0.016797 | 0.018983 | 0.058616 | -0.0019247 | 0.084417 | -58.5709 | 62.3383 | -60.6033 | -60.6125 | 54.7668 | 5.4703 | 53.6362 | 6.665 | 62.2971 | -60.672 | -0.16479 | 0.018311 | 1.8677 | -0.17395 | -7.5531 | -0.23346 | -0.022888 | 2.0325 | 114.0747 | 67.1036 | 115.2054 | 122.7768 | 1.8677 | 122.7356 | 65.9088 | -0.23346 | 122.7768 | 1.8677 | 65.9088 | 115.2054 | 122.7356 | -122.9233 | -122.9919
1532.3281 | 123.1201 | -60.4385 | 62.3474 | 0.21713 | 0.024992 | 0.014875 | 0.019837 | 0.057975 | -2.092e-06 | 0.084204 | -58.6349 | 62.3657 | -60.64 | -60.64 | 54.7119 | 5.3696 | 53.9841 | 6.7886 | 62.3245 | -60.6903 | -0.20142 | 0.018311 | 1.8036 | -0.20142 | -7.6355 | -0.25177 | -0.022888 | 2.005 | 114.4226 | 67.2272 | 115.1505 | 122.8043 | 1.8036 | 122.7631 | 65.8081 | -0.25177 | 122.8043 | 1.8036 | 65.8081 | 115.1505 | 122.7631 | -122.9874 | -123.0377
1533.3281 | 123.0835 | -60.4477 | 62.3383 | 0.17899 | 0.021787 | 0.014447 | 0.015137 | 0.059898 | 0.00042511 | 0.085913 | -58.6258 | 62.3383 | -60.6171 | -60.6308 | 54.7348 | 5.4749 | 54.1351 | 6.8253 | 62.2971 | -60.6674 | -0.16937 | 0 | 1.8219 | -0.1831 | -7.6035 | -0.21973 | -0.041199 | 1.9913 | 114.5828 | 67.2729 | 115.1825 | 122.7859 | 1.8219 | 122.7448 | 65.9225 | -0.21973 | 122.7859 | 1.8219 | 65.9225 | 115.1825 | 122.7448 | -122.9553 | -123.0057
1534.3281 | 122.9599 | -60.4614 | 62.4207 | 0.17899 | 0.025205 | 0.012738 | 0.022401 | 0.060539 | -0.00085669 | 0.082922 | -58.6899 | 62.4252 | -60.64 | -60.7498 | 54.6158 | 5.5069 | 53.7872 | 6.7245 | 62.3062 | -60.7407 | -0.17853 | 0.004578 | 1.7715 | -0.28839 | -7.8049 | -0.27924 | -0.11444 | 1.9501 | 114.2487 | 67.186 | 115.0772 | 122.8867 | 1.7715 | 122.7676 | 65.9683 | -0.27924 | 122.8867 | 1.7715 | 65.9683 | 115.0772 | 122.7676 | -123.0606 | -123.1613
1535.3438 | 123.0194 | -60.4523 | 62.3795 | -0.13382 | 0.023283 | 0.020002 | 0.021546 | 0.05883 | -0.0014975 | 0.084417 | -58.6304 | 62.4207 | -60.6354 | -60.6262 | 54.7485 | 5.5527 | 54.3823 | 7.0862 | 62.3383 | -60.7086 | -0.1831 | 0.041198 | 1.8219 | -0.17395 | -7.6309 | -0.25635 | -0.041199 | 2.005 | 114.8346 | 67.5385 | 115.2008 | 122.8729 | 1.8219 | 122.7905 | 66.0049 | -0.25635 | 122.8729 | 1.8219 | 66.0049 | 115.2008 | 122.7905 | -123.0148 | -123.0881
1536.3281 | 123.0148 | -60.4935 | 62.3703 | 0.17899 | 0.022428 | 0.010175 | 0.020264 | 0.062461 | -0.0034201 | 0.083563 | -58.6624 | 62.4161 | -60.6766 | -60.7269 | 54.6478 | 5.452 | 54.3915 | 7.0084 | 62.3428 | -60.7178 | -0.18311 | 0.045777 | 1.8311 | -0.23346 | -7.7225 | -0.2243 | -0.027466 | 2.0142 | 114.8849 | 67.5018 | 115.1413 | 122.9095 | 1.8311 | 122.8363 | 65.9454 | -0.2243 | 122.9095 | 1.8311 | 65.9454 | 115.1413 | 122.8363 | -123.0469 | -123.0881
1537.3281 | 122.9919 | -60.498 | 62.3611 | 0.35446 | 0.024778 | 0.011457 | 0.021973 | 0.059898 | -0.0010703 | 0.085699 | -58.5068 | 62.4298 | -60.64 | -60.7315 | 54.6433 | 5.4474 | 54.5242 | 7.0999 | 62.3383 | -60.7315 | -0.14191 | 0.068665 | 1.9913 | -0.23346 | -7.7179 | -0.23346 | -0.022888 | 2.1332 | 115.0223 | 67.598 | 115.1413 | 122.9279 | 1.9913 | 122.8363 | 65.9454 | -0.23346 | 122.9279 | 1.9913 | 65.9454 | 115.1413 | 122.8363 | -123.0011 | -123.0927
1538.3281 | 122.9965 | -60.4797 | 62.3245 | 0.064545 | 0.024137 | 0.014447 | 0.021119 | 0.060966 | -0.00042929 | 0.084204 | -58.6807 | 62.4161 | -60.6674 | -60.7452 | 54.6387 | 5.4291 | 54.3823 | 7.0084 | 62.3337 | -60.7224 | -0.18768 | 0.091553 | 1.799 | -0.2655 | -7.6859 | -0.24262 | 0.009155 | 1.9867 | 114.8621 | 67.4881 | 115.1184 | 122.8958 | 1.799 | 122.8134 | 65.9088 | -0.24262 | 122.8958 | 1.799 | 65.9088 | 115.1184 | 122.8134 | -122.9919 | -123.0469
1539.3281 | 122.9782 | -60.4797 | 62.3749 | 0.095062 | 0.025205 | 0.014875 | 0.020905 | 0.060752 | 0.00021151 | 0.084417 | -58.6761 | 62.4115 | -60.64 | -60.7086 | 54.6616 | 5.3925 | 54.3045 | 7.0953 | 62.3108 | -60.7178 | -0.16022 | 0.036621 | 1.8036 | -0.22888 | -7.7133 | -0.23804 | -0.064087 | 1.9638 | 114.7842 | 67.5751 | 115.1413 | 122.8912 | 1.8036 | 122.7905 | 65.8722 | -0.23804 | 122.8912 | 1.8036 | 65.8722 | 115.1413 | 122.7905 | -123.0148 | -123.0927
1540.3281 | 123.024 | -60.466 | 62.3611 | 0.0035097 | 0.024992 | 0.010602 | 0.020478 | 0.060539 | -0.00085669 | 0.08399 | -58.6212 | 62.4298 | -60.6354 | -60.6674 | 54.7165 | 5.4657 | 54.3961 | 7.2556 | 62.3657 | -60.7132 | -0.16937 | 0.068665 | 1.8448 | -0.20142 | -7.6447 | -0.24719 | 0.004578 | 2.0142 | 114.8621 | 67.7216 | 115.1825 | 122.8958 | 1.8448 | 122.8317 | 65.9317 | -0.24719 | 122.8958 | 1.8448 | 65.9317 | 115.1825 | 122.8317 | -122.9965 | -123.0743
1541.3281 | 123.024 | -60.4477 | 62.3978 | -0.065155 | 0.025846 | 0.012952 | 0.018342 | 0.060539 | -0.0017111 | 0.08399 | -58.6121 | 62.4161 | -60.6262 | -60.64 | 54.7256 | 5.5023 | 54.4785 | 7.2281 | 62.3428 | -60.6903 | -0.17853 | 0.018311 | 1.8356 | -0.19226 | -7.6721 | -0.24262 | -0.054932 | 2.0142 | 114.9261 | 67.6758 | 115.1733 | 122.8638 | 1.8356 | 122.7905 | 65.95 | -0.24262 | 122.8638 | 1.8356 | 65.95 | 115.1733 | 122.7905 | -123.024 | -123.0881
1542.3281 | 123.056 | -60.4523 | 62.384 | -0.16434 | 0.023283 | 0.014661 | 0.017487 | 0.059471 | -0.0019247 | 0.085272 | -58.6395 | 62.4527 | -60.6216 | -60.6674 | 54.7485 | 5.3696 | 54.3228 | 7.2556 | 62.3886 | -60.6903 | -0.16937 | 0.068665 | 1.8127 | -0.21515 | -7.6355 | -0.23804 | 0.004578 | 1.9821 | 114.7751 | 67.7078 | 115.2008 | 122.905 | 1.8127 | 122.8409 | 65.8218 | -0.23804 | 122.905 | 1.8127 | 65.8218 | 115.2008 | 122.8409 | -123.0057 | -123.0743
1543.3281 | 123.0377 | -60.4752 | 62.3886 | -0.15671 | 0.024778 | 0.01637 | 0.01941 | 0.062889 | 0.00021151 | 0.084631 | -58.5754 | 62.4435 | -60.6125 | -60.64 | 54.7714 | 5.4291 | 54.3686 | 7.283 | 62.3703 | -60.7132 | -0.13733 | 0.054931 | 1.8997 | -0.1648 | -7.6172 | -0.23804 | -0.018311 | 2.037 | 114.8438 | 67.7582 | 115.2466 | 122.9187 | 1.8997 | 122.8455 | 65.9042 | -0.23804 | 122.9187 | 1.8997 | 65.9042 | 115.2466 | 122.8455 | -123.0011 | -123.1018
1544.3281 | 122.937 | -60.4385 | 62.3795 | -0.16434 | 0.02371 | 0.013593 | 0.017274 | 0.059684 | -0.0025657 | 0.084204 | -58.5938 | 62.4344 | -60.6171 | -60.6491 | 54.7348 | 5.3329 | 54.5609 | 7.2235 | 62.3611 | -60.6766 | -0.17853 | 0.054931 | 1.8448 | -0.21057 | -7.6447 | -0.23804 | -0.018311 | 2.0233 | 114.9994 | 67.662 | 115.1733 | 122.8729 | 1.8448 | 122.7997 | 65.7715 | -0.23804 | 122.8729 | 1.8448 | 65.7715 | 115.1733 | 122.7997 | -122.9965 | -123.056
1545.3281 | 123.0515 | -60.4477 | 62.3978 | -0.13382 | 0.026274 | 0.0097476 | 0.018342 | 0.062461 | -0.00064309 | 0.083136 | -58.6395 | 62.4664 | -60.6354 | -60.6537 | 54.7256 | 5.397 | 54.4006 | 7.1136 | 62.3749 | -60.64 | -0.18768 | 0.068665 | 1.8082 | -0.20599 | -7.6721 | -0.19226 | -0.022888 | 1.9959 | 114.8483 | 67.5613 | 115.1733 | 122.9141 | 1.8082 | 122.8226 | 65.8447 | -0.19226 | 122.9141 | 1.8082 | 65.8447 | 115.1733 | 122.8226 | -123.0331 | -123.0377
1546.3281 | 123.056 | -60.466 | 62.3611 | 0.018768 | 0.026274 | 0.015088 | 0.018342 | 0.060966 | -0.0023519 | 0.085058 | -58.6212 | 62.4252 | -60.6216 | -60.6766 | 54.7073 | 5.4657 | 54.4693 | 7.0541 | 62.384 | -60.6949 | -0.15564 | 0.064087 | 1.8448 | -0.21057 | -7.6538 | -0.22888 | 0.022888 | 2.0004 | 114.9353 | 67.5201 | 115.1733 | 122.8912 | 1.8448 | 122.85 | 65.9317 | -0.22888 | 122.8912 | 1.8448 | 65.9317 | 115.1733 | 122.85 | -122.9828 | -123.056
1547.3281 | 123.0148 | -60.4523 | 62.4069 | -0.16434 | 0.024137 | 0.014447 | 0.016419 | 0.060111 | -0.0012839 | 0.08399 | -58.6761 | 62.4252 | -60.6308 | -60.704 | 54.7119 | 5.4153 | 54.5425 | 7.2281 | 62.4252 | -60.6674 | -0.17853 | 0.018311 | 1.7761 | -0.25177 | -7.695 | -0.21515 | 0.018311 | 1.9547 | 114.9948 | 67.6804 | 115.1642 | 122.8775 | 1.7761 | 122.8775 | 65.8676 | -0.21515 | 122.8775 | 1.7761 | 65.8676 | 115.1642 | 122.8775 | -123.0377 | -123.0743
1548.3281 | 123.0377 | -60.434 | 62.3932 | -0.21011 | 0.019438 | 0.010175 | 0.012574 | 0.06118 | -0.0025657 | 0.085486 | -58.6349 | 62.3795 | -60.6079 | -60.6537 | 54.7806 | 5.4703 | 54.5563 | 7.4387 | 62.4161 | -60.6262 | -0.17395 | -0.013732 | 1.799 | -0.21973 | -7.6126 | -0.19226 | 0.022889 | 1.973 | 114.9902 | 67.8726 | 115.2145 | 122.8134 | 1.799 | 122.85 | 65.9042 | -0.19226 | 122.8134 | 1.799 | 65.9042 | 115.2145 | 122.85 | -123.0011 | -123.0194
1549.3281 | 122.9782 | -60.4568 | 62.4115 | -0.19485 | 0.023069 | 0.012311 | 0.015351 | 0.059898 | -0.0014975 | 0.083136 | -58.6212 | 62.3795 | -60.5942 | -60.6674 | 54.7577 | 5.5481 | 54.4785 | 7.3929 | 62.3978 | -60.6537 | -0.13733 | -0.032043 | 1.8356 | -0.21057 | -7.6538 | -0.19684 | -0.013733 | 1.973 | 114.9353 | 67.8497 | 115.2145 | 122.8363 | 1.8356 | 122.8546 | 66.0049 | -0.19684 | 122.8363 | 1.8356 | 66.0049 | 115.2145 | 122.8546 | -123.0057 | -123.0652
1550.3281 | 123.0148 | -60.4889 | 62.4344 | -0.19485 | 0.025205 | 0.011029 | 0.016846 | 0.06182 | -0.0029929 | 0.084845 | -58.6578 | 62.3749 | -60.6125 | -60.6903 | 54.7119 | 5.452 | 55.0415 | 7.3334 | 62.4344 | -60.6583 | -0.1236 | -0.059509 | 1.8311 | -0.20142 | -7.7225 | -0.16937 | 0 | 1.9547 | 115.5304 | 67.8223 | 115.2008 | 122.8638 | 1.8311 | 122.9233 | 65.9409 | -0.16937 | 122.8638 | 1.8311 | 65.9409 | 115.2008 | 122.9233 | -123.0469 | -123.0927
1551.3281 | 123.0148 | -60.4294 | 62.4252 | -0.22537 | 0.022215 | 0.012097 | 0.014283 | 0.060111 | -0.0034201 | 0.082708 | -58.6166 | 62.3428 | -60.6079 | -60.6537 | 54.7302 | 5.5344 | 54.8264 | 7.5119 | 62.4207 | -60.6583 | -0.17853 | -0.082398 | 1.8127 | -0.22431 | -7.695 | -0.22888 | -0.004578 | 1.9913 | 115.2557 | 67.9413 | 115.1596 | 122.7722 | 1.8127 | 122.85 | 65.9637 | -0.22888 | 122.7722 | 1.8127 | 65.9637 | 115.1596 | 122.85 | -123.0331 | -123.0835
1552.3281 | 123.0743 | -60.4202 | 62.4161 | -0.17197 | 0.019651 | 0.0088932 | 0.015351 | 0.059684 | -0.0023519 | 0.082281 | -58.5663 | 62.3337 | -60.6125 | -60.6125 | 54.7531 | 5.5847 | 54.3869 | 7.5165 | 62.3657 | -60.6216 | -0.19226 | -0.082398 | 1.8539 | -0.19226 | -7.663 | -0.20142 | -0.050354 | 2.0462 | 114.8071 | 67.9367 | 115.1733 | 122.7539 | 1.8539 | 122.7859 | 66.0049 | -0.20142 | 122.7539 | 1.8539 | 66.0049 | 115.1733 | 122.7859 | -123.0286 | -123.0377
1553.3281 | 123.0743 | -60.4294 | 62.3795 | -0.088043 | 0.019651 | 0.010602 | 0.014924 | 0.059043 | -0.00021569 | 0.083136 | -58.5983 | 62.3062 | -60.6079 | -60.585 | 54.7943 | 5.7541 | 54.5517 | 7.6447 | 62.3795 | -60.6125 | -0.17853 | -0.073243 | 1.8311 | -0.15564 | -7.5851 | -0.18311 | 0 | 2.0096 | 114.9811 | 68.074 | 115.2237 | 122.7356 | 1.8311 | 122.8088 | 66.1835 | -0.18311 | 122.7356 | 1.8311 | 66.1835 | 115.2237 | 122.8088 | -122.9874 | -122.9919
1554.3281 | 123.1064 | -60.3928 | 62.3795 | 1.2852 | 0.023069 | 0.009534 | 0.015992 | 0.057121 | -0.0027793 | 0.084631 | -58.58 | 62.2833 | -60.6216 | -60.5942 | 54.8218 | 5.7129 | 54.6066 | 7.7179 | 62.3749 | -60.6079 | -0.22888 | -0.096131 | 1.8127 | -0.20142 | -7.5577 | -0.21515 | -0.004578 | 2.0416 | 114.9994 | 68.1107 | 115.2145 | 122.6761 | 1.8127 | 122.7676 | 66.1057 | -0.21515 | 122.6761 | 1.8127 | 66.1057 | 115.2145 | 122.7676 | -123.0011 | -122.9874
1555.3281 | 123.1064 | -60.4111 | 62.3657 | -0.0041198 | 0.01837 | 0.010388 | 0.014496 | 0.05648 | -0.0019247 | 0.084204 | -58.6212 | 62.2742 | -60.6125 | -60.6308 | 54.7577 | 5.5664 | 54.7028 | 7.7545 | 62.3657 | -60.6125 | -0.20142 | -0.091553 | 1.7899 | -0.21973 | -7.608 | -0.20142 | 0 | 1.9913 | 115.1138 | 68.1656 | 115.1688 | 122.6852 | 1.7899 | 122.7768 | 65.9775 | -0.20142 | 122.6852 | 1.7899 | 65.9775 | 115.1688 | 122.7768 | -122.9782 | -122.9782
1556.3281 | 123.143 | -60.379 | 62.3703 | -0.080414 | 0.020506 | 0.011457 | 0.020264 | 0.057121 | -0.0029929 | 0.083136 | -58.5251 | 62.2925 | -60.5667 | -60.6125 | 54.8035 | 5.571 | 54.3777 | 7.7179 | 62.3474 | -60.6033 | -0.18768 | -0.07782 | 1.8539 | -0.23346 | -7.5668 | -0.22431 | -0.022888 | 2.0416 | 114.7568 | 68.0969 | 115.1825 | 122.6715 | 1.8539 | 122.7264 | 65.95 | -0.22431 | 122.6715 | 1.8539 | 65.95 | 115.1825 | 122.7264 | -122.937 | -122.9736
1557.3281 | 123.1155 | -60.4019 | 62.3795 | -0.095673 | 0.021787 | 0.010602 | 0.016419 | 0.058402 | -0.0014975 | 0.084417 | -58.5846 | 62.3016 | -60.5988 | -60.5804 | 54.8035 | 5.4657 | 54.4281 | 7.7225 | 62.352 | -60.5942 | -0.19684 | -0.07782 | 1.8173 | -0.17853 | -7.576 | -0.19226 | -0.027466 | 2.0142 | 114.83 | 68.1244 | 115.2054 | 122.7036 | 1.8173 | 122.7539 | 65.8676 | -0.19226 | 122.7036 | 1.8173 | 65.8676 | 115.2054 | 122.7539 | -122.9782 | -122.9736
1558.3281 | 123.0835 | -60.3928 | 62.3886 | -0.072784 | 0.021787 | 0.010602 | 0.01706 | 0.057762 | -0.0034201 | 0.083563 | -58.5892 | 62.3154 | -60.5759 | -60.5896 | 54.776 | 5.4703 | 54.4876 | 7.7087 | 62.384 | -60.6079 | -0.18311 | -0.073242 | 1.8036 | -0.19684 | -7.6126 | -0.21515 | -0.004578 | 1.9867 | 114.8804 | 68.1015 | 115.1688 | 122.7081 | 1.8036 | 122.7768 | 65.863 | -0.21515 | 122.7081 | 1.8036 | 65.863 | 115.1688 | 122.7768 | -122.9645 | -122.9965
1559.3438 | 123.0057 | -60.4385 | 62.4069 | -0.26352 | 0.022642 | 0.0080386 | 0.020692 | 0.056907 | -0.0025657 | 0.084631 | -58.6258 | 62.3886 | -60.5942 | -60.6445 | 54.7028 | 5.4108 | 54.7211 | 7.6859 | 62.4161 | -60.64 | -0.15564 | -0.01831 | 1.8127 | -0.20599 | -7.7042 | -0.20142 | 0.009156 | 1.9684 | 115.1596 | 68.1244 | 115.1413 | 122.8271 | 1.8127 | 122.8546 | 65.8493 | -0.20142 | 122.8271 | 1.8127 | 65.8493 | 115.1413 | 122.8546 | -123.0011 | -123.0469
1560.3594 | 123.0423 | -60.5072 | 62.4023 | 0.19424 | 0.02371 | 0.010175 | 0.024323 | 0.060966 | -0.0032065 | 0.082281 | -58.6349 | 62.3886 | -60.6216 | -60.6995 | 54.6341 | 5.3879 | 54.7119 | 7.5851 | 62.3657 | -60.7086 | -0.11444 | -0.013733 | 1.8723 | -0.19226 | -7.7683 | -0.20142 | -0.036621 | 1.9867 | 115.2191 | 68.0923 | 115.1413 | 122.8958 | 1.8723 | 122.8729 | 65.8951 | -0.20142 | 122.8958 | 1.8723 | 65.8951 | 115.1413 | 122.8729 | -123.024 | -123.111
1561.3281 | 123.0881 | -60.4294 | 62.3886 | 0.14847 | 0.022001 | 0.012952 | 0.010865 | 0.057334 | -0.00042929 | 0.084204 | -58.6899 | 62.3245 | -60.5988 | -60.672 | 54.6616 | 5.4245 | 54.4739 | 7.6859 | 62.3245 | -60.6583 | -0.16937 | -0.064087 | 1.7395 | -0.24262 | -7.7271 | -0.22888 | -0.064087 | 1.9089 | 114.9033 | 68.1152 | 115.0909 | 122.7539 | 1.7395 | 122.7539 | 65.8539 | -0.22888 | 122.7539 | 1.7395 | 65.8539 | 115.0909 | 122.7539 | -122.9874 | -123.0469
1562.3281 | 123.1476 | -60.4111 | 62.3474 | 1.4989 | 0.024565 | 0.013166 | 0.018128 | 0.061393 | -0.0029929 | 0.082708 | -58.5342 | 62.2833 | -60.6125 | -60.6125 | 54.7485 | 5.5344 | 54.3137 | 7.7728 | 62.3108 | -60.64 | -0.20142 | -0.064087 | 1.8768 | -0.20142 | -7.5989 | -0.22888 | -0.036621 | 2.0782 | 114.7247 | 68.1839 | 115.1596 | 122.6944 | 1.8768 | 122.7219 | 65.9454 | -0.22888 | 122.6944 | 1.8768 | 65.9454 | 115.1596 | 122.7219 | -122.9599 | -122.9874
1563.3281 | 123.0881 | -60.4156 | 62.3611 | 0.19424 | 0.025205 | 0.013806 | 0.016419 | 0.057975 | -0.00021569 | 0.084631 | -58.6349 | 62.2925 | -60.6079 | -60.64 | 54.7256 | 5.5206 | 54.4098 | 7.8003 | 62.3108 | -60.6583 | -0.19226 | -0.068665 | 1.7807 | -0.22431 | -7.6355 | -0.24262 | -0.050354 | 1.973 | 114.8254 | 68.2159 | 115.1413 | 122.7081 | 1.7807 | 122.7264 | 65.9363 | -0.24262 | 122.7081 | 1.7807 | 65.9363 | 115.1413 | 122.7264 | -122.9691 | -123.0194
1564.3594 | 123.0515 | -60.434 | 62.3428 | 0.14084 | 0.02136 | 0.015088 | 0.016846 | 0.056693 | -0.0025657 | 0.084417 | -58.6807 | 62.2604 | -60.6491 | -60.6903 | 54.6616 | 5.5023 | 56.1264 | 8.3176 | 62.3016 | -60.6903 | -0.21515 | -0.082397 | 1.7532 | -0.25635 | -7.6813 | -0.25635 | -0.041198 | 1.9684 | 116.5604 | 68.7515 | 115.0955 | 122.6944 | 1.7532 | 122.7356 | 65.9363 | -0.25635 | 122.6944 | 1.7532 | 65.9363 | 115.0955 | 122.7356 | -122.9919 | -123.0331
1565.3281 | 123.0789 | -60.4523 | 62.3428 | 0.18662 | 0.021147 | 0.0099612 | 0.019837 | 0.055198 | 0.00021151 | 0.085272 | -58.6624 | 62.2787 | -60.6308 | -60.672 | 54.6799 | 5.5389 | 56.3553 | 8.3496 | 62.265 | -60.704 | -0.17853 | -0.064086 | 1.7899 | -0.21973 | -7.663 | -0.25177 | -0.077819 | 1.9684 | 116.8076 | 68.8019 | 115.1321 | 122.731 | 1.7899 | 122.7173 | 65.9912 | -0.25177 | 122.731 | 1.7899 | 65.9912 | 115.1321 | 122.7173 | -122.9736 | -123.0469
1566.3281 | 123.0789 | -60.4202 | 62.352 | 0.14847 | 0.022642 | 0.01167 | 0.020478 | 0.057975 | -0.00085669 | 0.083136 | -58.6304 | 62.2787 | -60.6354 | -60.6216 | 54.7119 | 5.5298 | 56.0944 | 8.3313 | 62.2833 | -60.6674 | -0.21515 | -0.073242 | 1.7899 | -0.20142 | -7.6401 | -0.24719 | -0.068665 | 2.005 | 116.5146 | 68.7515 | 115.1321 | 122.699 | 1.7899 | 122.7036 | 65.95 | -0.24719 | 122.699 | 1.7899 | 65.95 | 115.1321 | 122.7036 | -122.9874 | -123.0194
1567.3281 | 123.1155 | -60.4614 | 62.3428 | 0.17899 | 0.022215 | 0.014661 | 0.020051 | 0.057334 | -0.0014975 | 0.083349 | -58.6258 | 62.2833 | -60.6216 | -60.6216 | 54.6982 | 5.484 | 56.2454 | 8.4549 | 62.2879 | -60.7086 | -0.16022 | -0.059509 | 1.8356 | -0.16022 | -7.6447 | -0.24719 | -0.054931 | 1.9958 | 116.7068 | 68.9163 | 115.1596 | 122.7448 | 1.8356 | 122.7493 | 65.9454 | -0.24719 | 122.7448 | 1.8356 | 65.9454 | 115.1596 | 122.7493 | -122.9645 | -123.0515
1568.3281 | 123.0972 | -60.4202 | 62.4023 | 0.25528 | 0.02371 | 0.013379 | 0.023041 | 0.058616 | -2.092e-06 | 0.084631 | -58.5754 | 62.3337 | -60.5988 | -60.5484 | 54.7119 | 5.4657 | 54.0848 | 7.7225 | 62.3291 | -60.6537 | -0.17853 | -0.068665 | 1.8448 | -0.12817 | -7.6904 | -0.23346 | -0.073242 | 2.0233 | 114.505 | 68.1427 | 115.1321 | 122.7539 | 1.8448 | 122.7493 | 65.8859 | -0.23346 | 122.7539 | 1.8448 | 65.8859 | 115.1321 | 122.7493 | -123.0011 | -123.056
1569.375 | 123.0698 | -60.4248 | 62.3703 | 0.16373 | 0.022856 | 0.0097476 | 0.016205 | 0.057548 | -0.00021569 | 0.084845 | -58.699 | 62.2971 | -60.6354 | -60.6583 | 54.6707 | 5.5206 | 55.632 | 8.1619 | 62.3154 | -60.6674 | -0.21057 | -0.073242 | 1.7258 | -0.23346 | -7.6996 | -0.24261 | -0.054931 | 1.9363 | 116.0568 | 68.5867 | 115.0955 | 122.7219 | 1.7258 | 122.7402 | 65.9454 | -0.24261 | 122.7219 | 1.7258 | 65.9454 | 115.0955 | 122.7402 | -123.0057 | -123.0377
1570.3281 | 123.056 | -60.4614 | 62.3428 | 0.23239 | 0.023283 | 0.017652 | 0.021546 | 0.059898 | -0.0017111 | 0.08399 | -58.6807 | 62.3703 | -60.6491 | -60.6903 | 54.6295 | 5.4932 | 56.1401 | 8.3176 | 62.3291 | -60.6903 | -0.18768 | 0.027466 | 1.7807 | -0.22888 | -7.7133 | -0.22888 | -0.013732 | 1.9684 | 116.6016 | 68.779 | 115.0909 | 122.8317 | 1.7807 | 122.7905 | 65.9546 | -0.22888 | 122.8317 | 1.7807 | 65.9546 | 115.0909 | 122.7905 | -122.9919 | -123.0331
1571.3438 | 122.9691 | -60.4935 | 62.3703 | 0.095062 | 0.02371 | 0.015088 | 0.023682 | 0.060111 | -0.0017111 | 0.083136 | -58.6807 | 62.3932 | -60.6445 | -60.7178 | 54.6249 | 5.4108 | 56.2637 | 8.2993 | 62.352 | -60.704 | -0.15106 | 0.022888 | 1.8127 | -0.2243 | -7.7454 | -0.21057 | -0.01831 | 1.9638 | 116.7572 | 68.7927 | 115.1184 | 122.8867 | 1.8127 | 122.8455 | 65.9042 | -0.21057 | 122.8867 | 1.8127 | 65.9042 | 115.1184 | 122.8455 | -123.0148 | -123.0743
1572.3281 | 123.0377 | -60.4706 | 62.3611 | 0.2095 | 0.022856 | 0.017438 | 0.021973 | 0.060752 | -0.0010703 | 0.085058 | -58.7219 | 62.3795 | -60.6812 | -60.7178 | 54.6433 | 5.4703 | 56.1493 | 8.3267 | 62.3199 | -60.7224 | -0.21057 | 0.018311 | 1.7487 | -0.24719 | -7.7179 | -0.25177 | -0.041199 | 1.9592 | 116.6199 | 68.7973 | 115.1138 | 122.85 | 1.7487 | 122.7905 | 65.9409 | -0.25177 | 122.85 | 1.7487 | 65.9409 | 115.1138 | 122.7905 | -123.0423 | -123.0835
1573.3594 | 123.024 | -60.498 | 62.3428 | 0.22476 | 0.025633 | 0.01402 | 0.019837 | 0.059684 | -0.0023519 | 0.083136 | -58.7173 | 62.4069 | -60.6262 | -60.7178 | 54.6204 | 5.5344 | 56.1172 | 8.3405 | 62.3108 | -60.7178 | -0.12817 | 0.064087 | 1.7807 | -0.21973 | -7.7225 | -0.21973 | -0.032043 | 1.9089 | 116.6153 | 68.8385 | 115.1184 | 122.905 | 1.7807 | 122.8088 | 66.0324 | -0.21973 | 122.905 | 1.7807 | 66.0324 | 115.1184 | 122.8088 | -122.9691 | -123.0606
1574.3281 | 122.9691 | -60.4843 | 62.3886 | 0.81985 | 0.024351 | 0.017011 | 0.019837 | 0.059257 | -0.0010703 | 0.086767 | -58.5159 | 62.4207 | -60.6674 | -60.7132 | 54.6021 | 5.5847 | 56.1447 | 8.3725 | 62.3108 | -60.7224 | -0.18311 | 0.032043 | 1.9684 | -0.22888 | -7.7866 | -0.23804 | -0.07782 | 2.1515 | 116.629 | 68.8568 | 115.0864 | 122.905 | 1.9684 | 122.7951 | 66.069 | -0.23804 | 122.905 | 1.9684 | 66.069 | 115.0864 | 122.7951 | -123.056 | -123.111
1575.3438 | 123.0011 | -60.466 | 62.3932 | 0.11032 | 0.022215 | 0.012311 | 0.019837 | 0.058189 | -2.092e-06 | 0.083136 | -58.699 | 62.3978 | -60.6445 | -60.7132 | 54.6433 | 5.5756 | 56.3187 | 8.5373 | 62.3749 | -60.6995 | -0.17853 | 0.004578 | 1.767 | -0.24719 | -7.7499 | -0.23346 | -0.01831 | 1.9455 | 116.7847 | 69.0033 | 115.1093 | 122.8638 | 1.767 | 122.8409 | 66.0416 | -0.23346 | 122.8638 | 1.767 | 66.0416 | 115.1093 | 122.8409 | -123.0377 | -123.0927
1576.3281 | 123.024 | -60.4614 | 62.3886 | -0.065155 | 0.025205 | 0.015302 | 0.020692 | 0.060752 | -0.00021569 | 0.082281 | -58.6258 | 62.4207 | -60.6125 | -60.6583 | 54.6661 | 5.6259 | 56.2592 | 8.5236 | 62.3566 | -60.704 | -0.15106 | 0.032043 | 1.8356 | -0.19684 | -7.7225 | -0.24261 | -0.032044 | 1.9867 | 116.7206 | 68.985 | 115.1276 | 122.8821 | 1.8356 | 122.818 | 66.0873 | -0.24261 | 122.8821 | 1.8356 | 66.0873 | 115.1276 | 122.818 | -123.0011 | -123.0927
1577.3281 | 122.9965 | -60.4889 | 62.384 | 0.049286 | 0.024565 | 0.015943 | 0.020692 | 0.061607 | -0.0010703 | 0.083136 | -58.6533 | 62.4298 | -60.6354 | -60.7086 | 54.6158 | 5.5618 | 56.3553 | 8.4824 | 62.3474 | -60.7269 | -0.14648 | 0.045777 | 1.8356 | -0.21973 | -7.7682 | -0.23804 | -0.036621 | 1.9821 | 116.8442 | 68.9713 | 115.1047 | 122.9187 | 1.8356 | 122.8363 | 66.0507 | -0.23804 | 122.9187 | 1.8356 | 66.0507 | 115.1047 | 122.8363 | -123.0194 | -123.111
1578.3281 | 123.0057 | -60.4889 | 62.3749 | 0.026398 | 0.024137 | 0.019574 | 0.019196 | 0.061607 | 0.00042511 | 0.082068 | -58.6578 | 62.4435 | -60.6491 | -60.704 | 54.6524 | 5.6168 | 56.3736 | 8.6151 | 62.3383 | -60.7224 | -0.16022 | 0.068664 | 1.8311 | -0.21515 | -7.7225 | -0.23346 | -0.036621 | 1.9913 | 116.8625 | 69.104 | 115.1413 | 122.9324 | 1.8311 | 122.8271 | 66.1057 | -0.23346 | 122.9324 | 1.8311 | 66.1057 | 115.1413 | 122.8271 | -123.024 | -123.0972
1579.3281 | 123.0652 | -60.4431 | 62.3749 | 0.011139 | 0.025419 | 0.011457 | 0.020478 | 0.059898 | 0.0023477 | 0.085272 | -58.6441 | 62.439 | -60.6171 | -60.6628 | 54.6799 | 5.7266 | 56.2958 | 8.6151 | 62.352 | -60.7132 | -0.17395 | 0.064087 | 1.799 | -0.21973 | -7.695 | -0.27008 | -0.022888 | 1.973 | 116.7389 | 69.0582 | 115.123 | 122.8821 | 1.799 | 122.7951 | 66.1697 | -0.27008 | 122.8821 | 1.799 | 66.1697 | 115.123 | 122.7951 | -122.9919 | -123.0881
1580.3281 | 123.0652 | -60.4477 | 62.3749 | -0.057526 | 0.023924 | 0.012952 | 0.021973 | 0.06118 | -0.0025657 | 0.08399 | -58.6533 | 62.4252 | -60.6125 | -60.6354 | 54.7531 | 5.658 | 56.3736 | 8.7158 | 62.3657 | -60.6995 | -0.16479 | 0.050354 | 1.7944 | -0.18768 | -7.6218 | -0.25177 | -0.009155 | 1.9592 | 116.8213 | 69.1635 | 115.2008 | 122.8729 | 1.7944 | 122.8134 | 66.1057 | -0.25177 | 122.8729 | 1.7944 | 66.1057 | 115.2008 | 122.8134 | -122.9874 | -123.0743
1581.3281 | 123.0515 | -60.5209 | 62.3199 | -0.13382 | 0.024778 | 0.012738 | 0.01941 | 0.059471 | -0.00042929 | 0.083777 | -58.7265 | 62.3657 | -60.6812 | -60.7132 | 54.6478 | 5.658 | 58.6761 | 9.4345 | 62.3108 | -60.7361 | -0.16022 | 0.045777 | 1.7944 | -0.19226 | -7.6721 | -0.21515 | -0.009155 | 1.9547 | 119.1971 | 69.9554 | 115.1688 | 122.8867 | 1.7944 | 122.8317 | 66.1789 | -0.21515 | 122.8867 | 1.7944 | 66.1789 | 115.1688 | 122.8317 | -123.0011 | -123.056
1582.3281 | 123.0011 | -60.5072 | 62.3337 | -0.21011 | 0.022856 | 0.01402 | 0.016419 | 0.060966 | -0.0014975 | 0.085486 | -58.7631 | 62.3703 | -60.6995 | -60.7773 | 54.5975 | 5.6763 | 58.9233 | 9.4528 | 62.3749 | -60.7361 | -0.19226 | 0.036621 | 1.7441 | -0.27008 | -7.7362 | -0.22888 | 0.041199 | 1.9363 | 119.4305 | 69.96 | 115.1047 | 122.8775 | 1.7441 | 122.8821 | 66.1835 | -0.22888 | 122.8775 | 1.7441 | 66.1835 | 115.1047 | 122.8821 | -123.0331 | -123.0698
1583.3438 | 123.1201 | -60.4797 | 62.2833 | -0.0041198 | 0.018156 | 0.010175 | 0.010651 | 0.059471 | -0.00085669 | 0.084845 | -58.7036 | 62.2421 | -60.6995 | -60.6812 | 54.6936 | 5.7861 | 58.6395 | 9.5398 | 62.2971 | -60.672 | -0.21973 | -0.041199 | 1.7761 | -0.20142 | -7.5897 | -0.19226 | 0.013733 | 1.9959 | 119.1193 | 70.0195 | 115.1733 | 122.7219 | 1.7761 | 122.7768 | 66.2659 | -0.19226 | 122.7219 | 1.7761 | 66.2659 | 115.1733 | 122.7768 | -122.9828 | -122.9553
1584.3281 | 123.0469 | -60.5026 | 62.3749 | -0.17197 | 0.023069 | 0.014875 | 0.020692 | 0.061607 | -0.0017111 | 0.082922 | -58.7128 | 62.3749 | -60.6857 | -60.7315 | 54.6021 | 5.6854 | 58.8684 | 9.5627 | 62.3428 | -60.7315 | -0.1831 | 0 | 1.7899 | -0.22888 | -7.7728 | -0.22888 | -0.032044 | 1.973 | 119.371 | 70.0653 | 115.1047 | 122.8775 | 1.7899 | 122.8455 | 66.1881 | -0.22888 | 122.8775 | 1.7899 | 66.1881 | 115.1047 | 122.8455 | -123.0606 | -123.1064
1585.3281 | 123.0057 | -60.5164 | 62.3383 | -0.17197 | 0.021787 | 0.012952 | 0.018128 | 0.059043 | -0.00021569 | 0.084204 | -58.7311 | 62.3749 | -60.6857 | -60.7452 | 54.5837 | 5.6854 | 58.9096 | 9.5169 | 62.3566 | -60.7224 | -0.16937 | 0.036621 | 1.7853 | -0.22888 | -7.7545 | -0.20599 | 0.01831 | 1.9547 | 119.426 | 70.0333 | 115.1001 | 122.8912 | 1.7853 | 122.8729 | 66.2018 | -0.20599 | 122.8912 | 1.7853 | 66.2018 | 115.1001 | 122.8729 | -123.024 | -123.0606
1586.3281 | 122.9828 | -60.5072 | 62.3337 | -0.24063 | 0.023924 | 0.014234 | 0.016633 | 0.06118 | -0.0023519 | 0.08399 | -58.7585 | 62.3657 | -60.672 | -60.7544 | 54.5837 | 5.722 | 58.9417 | 9.4528 | 62.352 | -60.7132 | -0.16479 | 0.032044 | 1.7487 | -0.24719 | -7.7499 | -0.20599 | 0.018311 | 1.9135 | 119.4489 | 69.96 | 115.0909 | 122.8729 | 1.7487 | 122.8592 | 66.2292 | -0.20599 | 122.8729 | 1.7487 | 66.2292 | 115.0909 | 122.8592 | -123.0057 | -123.0469
1587.3281 | 122.9919 | -60.5896 | 62.2925 | -0.21011 | 0.022428 | 0.011457 | 0.015778 | 0.060325 | -0.00085669 | 0.084417 | -58.8135 | 62.2696 | -60.7452 | -60.5896 | 54.6112 | 5.7449 | 61.235 | 10.2173 | 62.3108 | -60.7636 | -0.15564 | -0.022888 | 1.7761 | 0 | -7.6813 | -0.17395 | 0.018311 | 1.9318 | 121.8246 | 70.8069 | 115.2008 | 122.8592 | 1.7761 | 122.9004 | 66.3345 | -0.17395 | 122.8592 | 1.7761 | 66.3345 | 115.2008 | 122.9004 | -123.0377 | -123.056
1588.3281 | 123.0148 | -60.5438 | 62.3337 | -0.20248 | 0.019224 | 0.011029 | 0.016633 | 0.059898 | -0.0021383 | 0.084631 | -58.7311 | 62.2879 | -60.6812 | -60.7544 | 54.5746 | 5.8685 | 60.3104 | 9.9014 | 62.3428 | -60.7269 | -0.13733 | -0.045776 | 1.8127 | -0.21057 | -7.7591 | -0.18311 | 0.009155 | 1.9501 | 120.8542 | 70.4453 | 115.1184 | 122.8317 | 1.8127 | 122.8867 | 66.4124 | -0.18311 | 122.8317 | 1.8127 | 66.4124 | 115.1184 | 122.8867 | -123.0148 | -123.0606
1589.3281 | 123.0698 | -60.5484 | 62.2971 | -0.1796 | 0.022215 | 0.0099612 | 0.014924 | 0.057975 | -0.0023519 | 0.083136 | -58.7357 | 62.2467 | -60.7086 | -60.7452 | 54.5883 | 5.9418 | 62.1735 | 10.5698 | 62.2467 | -60.7498 | -0.16022 | -0.050354 | 1.8127 | -0.19684 | -7.7087 | -0.20142 | -0.050354 | 1.973 | 122.7219 | 71.1182 | 115.1367 | 122.7951 | 1.8127 | 122.7951 | 66.4902 | -0.20142 | 122.7951 | 1.8127 | 66.4902 | 115.1367 | 122.7951 | -123.0057 | -123.0469
1590.3438 | 123.0835 | -60.5621 | 62.2238 | 0.24002 | 0.024137 | 0.013593 | 0.022401 | 0.059684 | -0.0025657 | 0.083777 | -58.7677 | 62.2467 | -60.7361 | -60.7864 | 54.5517 | 5.9372 | 62.0682 | 10.4919 | 62.2101 | -60.7956 | -0.17395 | 0.022888 | 1.7944 | -0.2243 | -7.6721 | -0.23346 | -0.013733 | 1.9684 | 122.6303 | 71.0541 | 115.1138 | 122.8088 | 1.7944 | 122.7722 | 66.4993 | -0.23346 | 122.8088 | 1.7944 | 66.4993 | 115.1138 | 122.7722 | -122.9599 | -123.0194
1591.3438 | 123.0011 | -60.5576 | 62.3245 | -0.17197 | 0.021787 | 0.010602 | 0.018983 | 0.058616 | -0.00021569 | 0.08399 | -58.6304 | 62.3199 | -60.7224 | -60.7956 | 54.5334 | 5.8914 | 62.2925 | 10.5103 | 62.2879 | -60.8047 | -0.1648 | -0.004578 | 1.9272 | -0.23804 | -7.7911 | -0.24719 | -0.036621 | 2.092 | 122.85 | 71.0678 | 115.0909 | 122.8775 | 1.9272 | 122.8455 | 66.449 | -0.24719 | 122.8775 | 1.9272 | 66.449 | 115.0909 | 122.8455 | -123.0469 | -123.1293
1592.3281 | 123.056 | -60.5164 | 62.2879 | -0.21011 | 0.020506 | 0.0099612 | 0.017701 | 0.059471 | -0.0027793 | 0.083349 | -58.7219 | 62.2147 | -60.7315 | -60.7086 | 54.6204 | 5.864 | 62.1918 | 10.5011 | 62.265 | -60.7315 | -0.21515 | -0.073242 | 1.7944 | -0.19226 | -7.6675 | -0.21515 | -0.022888 | 2.0096 | 122.7081 | 71.0175 | 115.1367 | 122.731 | 1.7944 | 122.7814 | 66.3803 | -0.21515 | 122.731 | 1.7944 | 66.3803 | 115.1367 | 122.7814 | -123.0194 | -123.0194
1593.3281 | 123.1018 | -60.5209 | 62.2604 | -0.14908 | 0.020506 | 0.011029 | 0.014924 | 0.057762 | -0.00085669 | 0.084631 | -58.7402 | 62.2375 | -60.704 | -60.6903 | 54.6478 | 5.9875 | 62.1506 | 10.7208 | 62.2604 | -60.7224 | -0.18311 | -0.022888 | 1.7807 | -0.16937 | -7.6126 | -0.20142 | 0 | 1.9638 | 122.6715 | 71.2418 | 115.1688 | 122.7585 | 1.7807 | 122.7814 | 66.5085 | -0.20142 | 122.7585 | 1.7807 | 66.5085 | 115.1688 | 122.7814 | -122.9645 | -122.9828
1594.3281 | 123.1201 | -60.5209 | 62.2971 | -0.22537 | 0.020078 | 0.011243 | 0.015137 | 0.058616 | -0.0029929 | 0.083349 | -58.6945 | 62.2147 | -60.6903 | -60.6903 | 54.657 | 5.8365 | 62.1368 | 10.7437 | 62.2696 | -60.7315 | -0.16937 | -0.082397 | 1.8265 | -0.16937 | -7.6401 | -0.21057 | -0.027466 | 1.9959 | 122.6578 | 71.2646 | 115.1779 | 122.7356 | 1.8265 | 122.7905 | 66.3574 | -0.21057 | 122.7356 | 1.8265 | 66.3574 | 115.1779 | 122.7905 | -122.9874 | -123.0286
1595.3281 | 123.1064 | -60.5209 | 62.2696 | 1.4149 | 0.019865 | 0.010816 | 0.015565 | 0.057975 | -0.0027793 | 0.084417 | -58.7494 | 62.1826 | -60.7178 | -60.6583 | 54.6616 | 5.8594 | 62.114 | 10.8032 | 62.2742 | -60.7086 | -0.19684 | -0.086975 | 1.7715 | -0.13733 | -7.608 | -0.18768 | 0.004578 | 1.9684 | 122.6349 | 71.3242 | 115.1825 | 122.7036 | 1.7715 | 122.7951 | 66.3803 | -0.18768 | 122.7036 | 1.7715 | 66.3803 | 115.1825 | 122.7951 | -122.9874 | -122.9782
1596.3281 | 123.1155 | -60.5347 | 62.2513 | -0.072784 | 0.020292 | 0.011243 | 0.017487 | 0.058616 | -0.0034201 | 0.082922 | -58.754 | 62.1918 | -60.6903 | -60.7132 | 54.6021 | 5.8731 | 62.1094 | 10.8124 | 62.2559 | -60.7315 | -0.15564 | -0.05951 | 1.7807 | -0.17853 | -7.6492 | -0.19684 | 0.004577 | 1.9363 | 122.644 | 71.347 | 115.1367 | 122.7264 | 1.7807 | 122.7905 | 66.4078 | -0.19684 | 122.7264 | 1.7807 | 66.4078 | 115.1367 | 122.7905 | -122.9416 | -122.9828
1597.3281 | 123.0606 | -60.5255 | 62.2879 | -1.5834 | 0.018156 | 0.011457 | 0.016205 | 0.056907 | -0.0021383 | 0.086767 | -58.8501 | 62.2147 | -60.7132 | -60.7727 | 54.538 | 5.8273 | 62.1414 | 10.7346 | 62.2421 | -60.7407 | -0.18768 | -0.073242 | 1.6754 | -0.24719 | -7.7499 | -0.21515 | -0.045777 | 1.8631 | 122.6669 | 71.2601 | 115.0635 | 122.7402 | 1.6754 | 122.7676 | 66.3528 | -0.21515 | 122.7402 | 1.6754 | 66.3528 | 115.0635 | 122.7676 | -123.0011 | -123.0286
1598.3281 | 123.0972 | -60.5118 | 62.265 | -0.042267 | 0.020719 | 0.011029 | 0.017274 | 0.057548 | -0.0012839 | 0.084845 | -58.7265 | 62.2055 | -60.6949 | -60.7178 | 54.6249 | 5.9509 | 62.1277 | 10.8444 | 62.2147 | -60.7224 | -0.1831 | -0.05951 | 1.7853 | -0.20599 | -7.6401 | -0.21057 | -0.050354 | 1.9684 | 122.6395 | 71.3562 | 115.1367 | 122.7173 | 1.7853 | 122.7264 | 66.4627 | -0.21057 | 122.7173 | 1.7853 | 66.4627 | 115.1367 | 122.7264 | -122.9599 | -122.9874
1599.3281 | 123.1247 | -60.5072 | 62.3016 | -0.042267 | 0.023283 | 0.0088932 | 0.016633 | 0.055412 | -0.0025657 | 0.08399 | -58.7677 | 62.1826 | -60.7132 | -60.7132 | 54.5837 | 5.8548 | 62.1277 | 10.8444 | 62.2513 | -60.7178 | -0.20599 | -0.11902 | 1.7395 | -0.20599 | -7.7179 | -0.21057 | -0.050354 | 1.9455 | 122.6349 | 71.3516 | 115.0909 | 122.6898 | 1.7395 | 122.7585 | 66.362 | -0.21057 | 122.6898 | 1.7395 | 66.362 | 115.0909 | 122.7585 | -123.0148 | -123.0194
1600.3281 | 123.111 | -60.5209 | 62.265 | -0.027008 | 0.021147 | 0.0091068 | 0.016633 | 0.054771 | -0.00021569 | 0.083563 | -58.754 | 62.2192 | -60.704 | -60.6995 | 54.5975 | 5.8548 | 62.1185 | 10.7941 | 62.2421 | -60.7407 | -0.18311 | -0.045777 | 1.767 | -0.17853 | -7.6675 | -0.21973 | -0.022889 | 1.9501 | 122.6395 | 71.315 | 115.1184 | 122.7402 | 1.767 | 122.7631 | 66.3757 | -0.21973 | 122.7402 | 1.767 | 66.3757 | 115.1184 | 122.7631 | -122.9691 | -123.0057
1601.3281 | 123.0881 | -60.498 | 62.265 | -0.027008 | 0.01901 | 0.012311 | 0.017701 | 0.055625 | -0.0012839 | 0.083563 | -58.7769 | 62.1872 | -60.7086 | -60.7224 | 54.5837 | 5.8502 | 62.1506 | 10.9039 | 62.2421 | -60.7132 | -0.21057 | -0.07782 | 1.7212 | -0.2243 | -7.6813 | -0.21515 | -0.022889 | 1.9318 | 122.6486 | 71.402 | 115.0818 | 122.6852 | 1.7212 | 122.7402 | 66.3483 | -0.21515 | 122.6852 | 1.7212 | 66.3483 | 115.0818 | 122.7402 | -122.9736 | -122.9782
1602.3281 | 123.0972 | -60.5301 | 62.2787 | 0.034027 | 0.019438 | 0.011457 | 0.017487 | 0.056266 | -0.0029929 | 0.081854 | -58.7906 | 62.1872 | -60.704 | -60.7407 | 54.5425 | 5.7587 | 62.1414 | 10.7803 | 62.2513 | -60.7269 | -0.17395 | -0.091553 | 1.7395 | -0.21057 | -7.7362 | -0.19684 | -0.027466 | 1.9135 | 122.6715 | 71.3104 | 115.0726 | 122.7173 | 1.7395 | 122.7814 | 66.2888 | -0.19684 | 122.7173 | 1.7395 | 66.2888 | 115.0726 | 122.7814 | -122.9828 | -123.0057
1603.3281 | 123.0881 | -60.5164 | 62.2833 | 0.14847 | 0.021574 | 0.0082522 | 0.017487 | 0.059043 | -0.0023519 | 0.08399 | -58.7631 | 62.2055 | -60.7224 | -60.7452 | 54.5425 | 5.7861 | 62.1231 | 10.8261 | 62.2375 | -60.7269 | -0.20599 | -0.07782 | 1.7532 | -0.22888 | -7.7408 | -0.21057 | -0.045776 | 1.9592 | 122.6395 | 71.3425 | 115.0589 | 122.7219 | 1.7532 | 122.7539 | 66.3025 | -0.21057 | 122.7219 | 1.7532 | 66.3025 | 115.0589 | 122.7539 | -123.0057 | -123.0103
1604.3281 | 123.0881 | -60.4065 | 62.4161 | 0.17899 | 0.022428 | 0.013806 | 0.016846 | 0.055839 | -0.00042929 | 0.082495 | -58.5983 | 62.3337 | -60.5896 | -60.5759 | 54.6844 | 5.6488 | 54.3594 | 8.3954 | 62.3611 | -60.5713 | -0.18311 | -0.082398 | 1.8082 | -0.16937 | -7.7316 | -0.16479 | -0.054932 | 1.9913 | 114.7659 | 68.8019 | 115.0909 | 122.7402 | 1.8082 | 122.7676 | 66.0553 | -0.16479 | 122.7402 | 1.8082 | 66.0553 | 115.0909 | 122.7676 | -123.0057 | -122.9874
1605.3281 | 123.1018 | -60.4568 | 62.3474 | 0.37735 | 0.019651 | 0.012525 | 0.015992 | 0.056266 | 0.00042511 | 0.084631 | -58.7311 | 62.2559 | -60.6949 | -60.7178 | 54.5746 | 5.7083 | 59.1705 | 9.9655 | 62.2742 | -60.704 | -0.23804 | -0.091553 | 1.7258 | -0.26093 | -7.7728 | -0.24719 | -0.073242 | 1.9638 | 119.6274 | 70.4224 | 115.0314 | 122.7127 | 1.7258 | 122.731 | 66.1652 | -0.24719 | 122.7127 | 1.7258 | 66.1652 | 115.0314 | 122.731 | -123.0423 | -123.0515
1606.3281 | 123.0515 | -60.4797 | 62.3108 | 0.064545 | 0.021147 | 0.006116 | 0.016846 | 0.055839 | -0.00021569 | 0.083349 | -58.7128 | 62.2238 | -60.6628 | -60.6949 | 54.451 | 5.8411 | 58.9142 | 9.8328 | 62.3108 | -60.6903 | -0.18311 | -0.086975 | 1.767 | -0.21515 | -7.8598 | -0.21057 | 0 | 1.9501 | 119.3939 | 70.3125 | 114.9307 | 122.7036 | 1.767 | 122.7905 | 66.3208 | -0.21057 | 122.7036 | 1.767 | 66.3208 | 114.9307 | 122.7905 | -122.9736 | -123.0011
1607.3281 | 123.0972 | -60.4706 | 62.3474 | 0.11032 | 0.020292 | 0.010388 | 0.019623 | 0.056907 | -0.0019247 | 0.083563 | -58.7128 | 62.2284 | -60.6583 | -60.6812 | 54.5654 | 5.7358 | 59.1751 | 9.9472 | 62.265 | -60.704 | -0.18768 | -0.11902 | 1.7578 | -0.21057 | -7.782 | -0.23346 | -0.082397 | 1.9455 | 119.6457 | 70.4178 | 115.036 | 122.699 | 1.7578 | 122.7356 | 66.2064 | -0.23346 | 122.699 | 1.7578 | 66.2064 | 115.036 | 122.7356 | -123.0057 | -123.0515
1608.3281 | 123.0789 | -60.4935 | 62.3108 | 0.17136 | 0.018797 | 0.011884 | 0.018555 | 0.056907 | -0.0014975 | 0.082708 | -58.7219 | 62.233 | -60.6766 | -60.6903 | 54.5792 | 5.7266 | 59.1614 | 9.9976 | 62.265 | -60.7086 | -0.18311 | -0.07782 | 1.7715 | -0.19684 | -7.7316 | -0.21515 | -0.045776 | 1.9547 | 119.6548 | 70.491 | 115.0726 | 122.7264 | 1.7715 | 122.7585 | 66.2201 | -0.21515 | 122.7264 | 1.7715 | 66.2201 | 115.0726 | 122.7585 | -122.9874 | -123.0194
1609.3594 | 122.9645 | -60.5301 | 62.3108 | -0.095673 | 0.024565 | 0.013379 | 0.023255 | 0.057762 | -0.0021383 | 0.083777 | -58.7082 | 62.3703 | -60.6995 | -60.6812 | 54.5654 | 5.809 | 60.6491 | 10.5743 | 62.2742 | -60.7361 | -0.16937 | 0.059509 | 1.8219 | -0.15106 | -7.7454 | -0.20599 | -0.036621 | 1.9913 | 121.1792 | 71.1044 | 115.0955 | 122.9004 | 1.8219 | 122.8043 | 66.3391 | -0.20599 | 122.9004 | 1.8219 | 66.3391 | 115.0955 | 122.8043 | -123.0103 | -123.0469
1610.3281 | 123.1293 | -60.5072 | 62.2742 | 0.22476 | 0.021574 | 0.015515 | 0.017274 | 0.059257 | 0.00063871 | 0.084631 | -58.699 | 62.2238 | -60.7407 | -60.6583 | 54.5975 | 5.8731 | 60.1227 | 10.405 | 62.233 | -60.7269 | -0.23346 | -0.050354 | 1.8082 | -0.15106 | -7.6767 | -0.21973 | -0.041199 | 2.0416 | 120.6299 | 70.9122 | 115.1047 | 122.731 | 1.8082 | 122.7402 | 66.3803 | -0.21973 | 122.731 | 1.8082 | 66.3803 | 115.1047 | 122.7402 | -123.0148 | -123.0011
1611.3438 | 123.0286 | -60.5209 | 62.3566 | 0.14084 | 0.024351 | 0.012097 | 0.02411 | 0.058616 | -0.0012839 | 0.083777 | -58.7814 | 62.384 | -60.6766 | -60.759 | 54.4281 | 5.452 | 59.317 | 10.231 | 62.2467 | -60.7773 | -0.15564 | 0.027466 | 1.7395 | -0.23804 | -7.9285 | -0.25635 | -0.10986 | 1.8951 | 119.838 | 70.752 | 114.949 | 122.905 | 1.7395 | 122.7676 | 65.9729 | -0.25635 | 122.905 | 1.7395 | 65.9729 | 114.949 | 122.7676 | -123.0331 | -123.1338
1612.3281 | 123.0789 | -60.4752 | 62.265 | 0.20187 | 0.020292 | 0.014875 | 0.015992 | 0.058189 | 0.00021151 | 0.083136 | -58.7311 | 62.2513 | -60.704 | -60.6812 | 54.5746 | 5.8731 | 58.8455 | 10.0159 | 62.2421 | -60.7086 | -0.22888 | -0.013733 | 1.7441 | -0.20599 | -7.6904 | -0.23346 | -0.022889 | 1.973 | 119.3207 | 70.491 | 115.0497 | 122.7264 | 1.7441 | 122.7173 | 66.3483 | -0.23346 | 122.7264 | 1.7441 | 66.3483 | 115.0497 | 122.7173 | -122.9691 | -122.9736
1613.3438 | 123.056 | -60.498 | 62.2925 | 0.18662 | 0.022001 | 0.011243 | 0.017487 | 0.057975 | -0.0019247 | 0.083777 | -58.7677 | 62.2604 | -60.672 | -60.6949 | 54.5563 | 5.8319 | 58.9783 | 10.0708 | 62.2513 | -60.6995 | -0.17395 | -0.032043 | 1.7303 | -0.19684 | -7.7362 | -0.20142 | -0.041198 | 1.9043 | 119.4763 | 70.5688 | 115.0543 | 122.7585 | 1.7303 | 122.7493 | 66.33 | -0.20142 | 122.7585 | 1.7303 | 66.33 | 115.0543 | 122.7493 | -122.9645 | -122.9919
1614.3281 | 123.111 | -60.4935 | 62.3062 | 0.20187 | 0.021787 | 0.01637 | 0.020692 | 0.057762 | -0.0021383 | 0.084845 | -58.6899 | 62.265 | -60.6674 | -60.6674 | 54.5975 | 5.7999 | 58.9096 | 10.0571 | 62.2375 | -60.7086 | -0.17395 | -0.041198 | 1.8036 | -0.17395 | -7.7087 | -0.21515 | -0.068664 | 1.9775 | 119.4031 | 70.5505 | 115.0909 | 122.7585 | 1.8036 | 122.731 | 66.2933 | -0.21515 | 122.7585 | 1.8036 | 66.2933 | 115.0909 | 122.731 | -122.9736 | -123.0148
1615.3281 | 123.1201 | -60.4752 | 62.2971 | -0.11093 | 0.023283 | 0.014875 | 0.020692 | 0.058189 | -0.0010703 | 0.085058 | -58.6853 | 62.2742 | -60.6445 | -60.6674 | 54.5975 | 5.8731 | 58.8135 | 9.9976 | 62.2421 | -60.7315 | -0.16937 | -0.022888 | 1.7899 | -0.19226 | -7.6996 | -0.25635 | -0.054932 | 1.9592 | 119.2886 | 70.4727 | 115.0726 | 122.7493 | 1.7899 | 122.7173 | 66.3483 | -0.25635 | 122.7493 | 1.7899 | 66.3483 | 115.0726 | 122.7173 | -122.9416 | -123.0286
1616.3281 | 123.0972 | -60.4935 | 62.2925 | 0.18662 | 0.02136 | 0.011243 | 0.018128 | 0.058189 | -0.0012839 | 0.084631 | -58.6716 | 62.2787 | -60.6766 | -60.6857 | 54.6204 | 5.8228 | 58.7494 | 10.0525 | 62.2604 | -60.7086 | -0.18311 | -0.013732 | 1.8219 | -0.19226 | -7.6721 | -0.21515 | -0.032043 | 2.005 | 119.2429 | 70.546 | 115.1138 | 122.7722 | 1.8219 | 122.7539 | 66.3162 | -0.21515 | 122.7722 | 1.8219 | 66.3162 | 115.1138 | 122.7539 | -122.9691 | -123.0011
1617.3281 | 123.0606 | -60.5118 | 62.233 | 0.30869 | 0.023924 | 0.015302 | 0.020478 | 0.059684 | -0.0019247 | 0.08399 | -58.699 | 62.2971 | -60.6949 | -60.6766 | 54.5654 | 5.7587 | 59.1843 | 10.1761 | 62.2375 | -60.7132 | -0.1831 | 0.064087 | 1.8127 | -0.16479 | -7.6675 | -0.20142 | 0.004578 | 1.9958 | 119.696 | 70.6879 | 115.0772 | 122.8088 | 1.8127 | 122.7493 | 66.2704 | -0.20142 | 122.8088 | 1.8127 | 66.2704 | 115.0772 | 122.7493 | -122.9279 | -122.9462
1618.3438 | 123.0194 | -60.498 | 62.3337 | 0.072174 | 0.024565 | 0.014447 | 0.023041 | 0.059471 | -0.00042929 | 0.084417 | -58.7265 | 62.3657 | -60.6766 | -60.7086 | 54.5334 | 5.7037 | 59.3216 | 10.0937 | 62.2787 | -60.759 | -0.17853 | 0.032044 | 1.7715 | -0.21057 | -7.8003 | -0.26093 | -0.054931 | 1.9501 | 119.8196 | 70.5917 | 115.0314 | 122.8638 | 1.7715 | 122.7768 | 66.2018 | -0.26093 | 122.8638 | 1.7715 | 66.2018 | 115.0314 | 122.7768 | -123.0103 | -123.0927
1619.3281 | 123.1247 | -60.4889 | 62.2925 | 0.25528 | 0.022642 | 0.016584 | 0.019196 | 0.059898 | -0.0017111 | 0.083349 | -58.6807 | 62.2971 | -60.6628 | -60.5896 | 54.5792 | 5.9097 | 58.7585 | 10.1395 | 62.2787 | -60.6949 | -0.17395 | 0.004578 | 1.8082 | -0.10071 | -7.7133 | -0.20599 | -0.013732 | 1.9821 | 119.2474 | 70.6284 | 115.0681 | 122.7859 | 1.8082 | 122.7676 | 66.3986 | -0.20599 | 122.7859 | 1.8082 | 66.3986 | 115.0681 | 122.7676 | -122.9553 | -122.9874
1620.3281 | 123.143 | -60.5026 | 62.2696 | 0.19424 | 0.022215 | 0.011457 | 0.019623 | 0.059471 | -0.0025657 | 0.084204 | -58.7173 | 62.3062 | -60.6857 | -60.6674 | 54.5746 | 5.8365 | 58.6166 | 10.0937 | 62.2696 | -60.6995 | -0.1831 | 0.036621 | 1.7853 | -0.16479 | -7.695 | -0.19684 | 0 | 1.9684 | 119.1193 | 70.5963 | 115.0772 | 122.8088 | 1.7853 | 122.7722 | 66.3391 | -0.19684 | 122.8088 | 1.7853 | 66.3391 | 115.0772 | 122.7722 | -122.9553 | -122.9691
1621.3438 | 123.0927 | -60.4752 | 62.3062 | 0.16373 | 0.020506 | 0.012525 | 0.015565 | 0.059257 | -0.0027793 | 0.082495 | -58.7219 | 62.2604 | -60.6674 | -60.6857 | 54.5746 | 5.8456 | 58.754 | 10.231 | 62.2375 | -60.704 | -0.19226 | -0.045776 | 1.7532 | -0.21057 | -7.7316 | -0.22888 | -0.068664 | 1.9455 | 119.2291 | 70.7062 | 115.0497 | 122.7356 | 1.7532 | 122.7127 | 66.3208 | -0.22888 | 122.7356 | 1.7532 | 66.3208 | 115.0497 | 122.7127 | -122.9736 | -123.0103
1622.3281 | 123.0377 | -60.4935 | 62.3154 | 0.21713 | 0.024992 | 0.012311 | 0.020905 | 0.060966 | -2.092e-06 | 0.084417 | -58.7448 | 62.3337 | -60.6766 | -60.7315 | 54.5151 | 5.8731 | 58.9645 | 10.1898 | 62.2879 | -60.7407 | -0.18311 | 0.01831 | 1.7487 | -0.23804 | -7.8003 | -0.24719 | -0.027466 | 1.9318 | 119.458 | 70.6833 | 115.0085 | 122.8271 | 1.7487 | 122.7814 | 66.3666 | -0.24719 | 122.8271 | 1.7487 | 66.3666 | 115.0085 | 122.7814 | -122.9919 | -123.056
1623.3281 | 123.0103 | -60.5164 | 62.3291 | 0.20187 | 0.027769 | 0.013166 | 0.020692 | 0.062889 | -0.0010703 | 0.08399 | -58.7906 | 62.3428 | -60.7132 | -60.7544 | 54.4968 | 5.7266 | 59.1568 | 10.1807 | 62.2696 | -60.759 | -0.19684 | 0.013732 | 1.7258 | -0.23804 | -7.8323 | -0.24262 | -0.05951 | 1.9226 | 119.6732 | 70.697 | 115.0131 | 122.8592 | 1.7258 | 122.7859 | 66.243 | -0.24262 | 122.8592 | 1.7258 | 66.243 | 115.0131 | 122.7859 | -123.0423 | -123.0881
1624.3281 | 123.0652 | -60.5301 | 62.3566 | 0.19424 | 0.024351 | 0.013806 | 0.023041 | 0.060325 | -0.0036337 | 0.085272 | -58.7769 | 62.3611 | -60.7132 | -60.791 | 54.4418 | 5.8044 | 58.8821 | 9.668 | 62.2787 | -60.7681 | -0.18311 | 0.004578 | 1.7532 | -0.26093 | -7.9147 | -0.23804 | -0.077819 | 1.9363 | 119.4122 | 70.1981 | 114.9719 | 122.8912 | 1.7532 | 122.8088 | 66.3345 | -0.23804 | 122.8912 | 1.7532 | 66.3345 | 114.9719 | 122.8088 | -123.0698 | -123.1247
1625.3281 | 122.9965 | -60.5392 | 62.3062 | 0.17899 | 0.025419 | 0.013593 | 0.022401 | 0.060752 | -0.0017111 | 0.083349 | -58.7448 | 62.3703 | -60.7178 | -60.7773 | 54.451 | 5.722 | 59.111 | 10.1166 | 62.3199 | -60.7727 | -0.17853 | 0.064087 | 1.7944 | -0.23804 | -7.8552 | -0.23346 | 0.013733 | 1.973 | 119.6503 | 70.6558 | 114.9902 | 122.9095 | 1.7944 | 122.8592 | 66.2613 | -0.23346 | 122.9095 | 1.7944 | 66.2613 | 114.9902 | 122.8592 | -123.024 | -123.0789
1626.3281 | 122.9965 | -60.5301 | 62.3337 | 0.16373 | 0.024778 | 0.014447 | 0.021119 | 0.062461 | -0.0014975 | 0.081854 | -58.786 | 62.3566 | -60.6995 | -60.7773 | 54.4693 | 5.777 | 58.9417 | 10.0616 | 62.3383 | -60.7544 | -0.16937 | 0.022888 | 1.7441 | -0.24719 | -7.8644 | -0.22431 | 0.004578 | 1.9135 | 119.4717 | 70.5917 | 114.9994 | 122.8867 | 1.7441 | 122.8683 | 66.3071 | -0.22431 | 122.8867 | 1.7441 | 66.3071 | 114.9994 | 122.8683 | -123.0331 | -123.0881
1627.3438 | 123.0652 | -60.5118 | 62.3291 | 0.22476 | 0.024351 | 0.014875 | 0.018342 | 0.060966 | -0.00064309 | 0.083777 | -58.7997 | 62.3428 | -60.704 | -60.7544 | 54.5013 | 5.7266 | 58.7769 | 10.0937 | 62.3016 | -60.7636 | -0.19226 | 0.013732 | 1.712 | -0.24262 | -7.8278 | -0.25177 | -0.027466 | 1.9043 | 119.2886 | 70.6055 | 115.0131 | 122.8546 | 1.712 | 122.8134 | 66.2384 | -0.25177 | 122.8546 | 1.712 | 66.2384 | 115.0131 | 122.8134 | -123.0331 | -123.0927
1628.3281 | 123.024 | -60.5072 | 62.3474 | 0.14084 | 0.022856 | 0.013379 | 0.020478 | 0.061393 | 0.00042511 | 0.081427 | -58.786 | 62.3978 | -60.6766 | -60.5438 | 54.5609 | 5.7404 | 58.9371 | 9.8877 | 62.3245 | -60.759 | -0.16937 | 0.050354 | 1.7212 | -0.036621 | -7.7866 | -0.25177 | -0.022888 | 1.8906 | 119.4443 | 70.3949 | 115.0681 | 122.905 | 1.7212 | 122.8317 | 66.2476 | -0.25177 | 122.905 | 1.7212 | 66.2476 | 115.0681 | 122.8317 | -123.024 | -123.1064
1629.3281 | 123.1018 | -60.4752 | 62.2833 | 0.22476 | 0.025419 | 0.015943 | 0.017487 | 0.06182 | -0.00042929 | 0.085699 | -58.7311 | 62.3291 | -60.6903 | -60.6857 | 54.538 | 5.8502 | 58.6533 | 10.0479 | 62.2696 | -60.7269 | -0.21515 | 0.045777 | 1.7441 | -0.21057 | -7.7454 | -0.25177 | -0.013733 | 1.9592 | 119.1284 | 70.5231 | 115.0131 | 122.8043 | 1.7441 | 122.7448 | 66.3254 | -0.25177 | 122.8043 | 1.7441 | 66.3254 | 115.0131 | 122.7448 | -122.9736 | -123.0103
1630.3281 | 122.9874 | -60.5255 | 62.3566 | 0.095062 | 0.024137 | 0.01402 | 0.02176 | 0.06118 | -0.00042929 | 0.083777 | -58.7357 | 62.3886 | -60.704 | -60.7544 | 54.4647 | 5.7907 | 58.8501 | 9.9792 | 62.3154 | -60.7864 | -0.17853 | 0.032044 | 1.7899 | -0.22888 | -7.8918 | -0.26093 | -0.041198 | 1.9684 | 119.3756 | 70.5048 | 114.9902 | 122.9141 | 1.7899 | 122.8409 | 66.3162 | -0.26093 | 122.9141 | 1.7899 | 66.3162 | 114.9902 | 122.8409 | -123.0606 | -123.143
1631.3281 | 122.9874 | -60.5255 | 62.3291 | -0.049896 | 0.023283 | 0.013379 | 0.01941 | 0.061607 | -0.0029929 | 0.08399 | -58.6853 | 62.3978 | -60.6903 | -60.7178 | 54.5334 | 5.8914 | 59.3033 | 10.1715 | 62.3154 | -60.7498 | -0.1648 | 0.068664 | 1.8402 | -0.19226 | -7.7957 | -0.2243 | -0.013733 | 2.005 | 119.8288 | 70.697 | 115.0589 | 122.9233 | 1.8402 | 122.8409 | 66.4169 | -0.2243 | 122.9233 | 1.8402 | 66.4169 | 115.0589 | 122.8409 | -123.0194 | -123.0789
1632.3281 | 123.0469 | -60.4706 | 62.3566 | 0.011139 | 0.027342 | 0.013593 | 0.018555 | 0.062889 | -0.00021569 | 0.084845 | -58.6899 | 62.4023 | -60.704 | -60.7224 | 54.5197 | 5.8365 | 58.7997 | 9.9792 | 62.3474 | -60.7269 | -0.23346 | 0.045777 | 1.7807 | -0.25177 | -7.8369 | -0.25635 | -0.009155 | 2.0142 | 119.2703 | 70.4498 | 114.9902 | 122.8729 | 1.7807 | 122.818 | 66.3071 | -0.25635 | 122.8729 | 1.7807 | 66.3071 | 114.9902 | 122.818 | -123.0606 | -123.0835
1633.3281 | 123.0148 | -60.5209 | 62.352 | 0.072174 | 0.026487 | 0.01637 | 0.017274 | 0.062889 | 0.00021151 | 0.082922 | -58.7357 | 62.3703 | -60.672 | -60.7498 | 54.4647 | 5.777 | 59.111 | 10.2219 | 62.3383 | -60.759 | -0.15106 | 0.01831 | 1.7853 | -0.22888 | -7.8873 | -0.23804 | -0.013733 | 1.9363 | 119.632 | 70.7428 | 114.9857 | 122.8912 | 1.7853 | 122.8592 | 66.2979 | -0.23804 | 122.8912 | 1.7853 | 66.2979 | 114.9857 | 122.8592 | -123.024 | -123.111
1634.3438 | 123.0927 | -60.5301 | 62.2696 | 0.041657 | 0.020506 | 0.010602 | 0.010651 | 0.059043 | -0.0023519 | 0.085486 | -58.8318 | 62.2101 | -60.7452 | -60.7773 | 54.5288 | 5.9372 | 61.9995 | 11.2518 | 62.2375 | -60.7407 | -0.21515 | -0.059509 | 1.6983 | -0.24719 | -7.7408 | -0.21057 | -0.032043 | 1.9135 | 122.5296 | 71.7819 | 115.0589 | 122.7402 | 1.6983 | 122.7676 | 66.4673 | -0.21057 | 122.7402 | 1.6983 | 66.4673 | 115.0589 | 122.7676 | -123.0148 | -123.0103
1635.3281 | 122.9919 | -60.5942 | 62.2604 | 0.13321 | 0.025205 | 0.012738 | 0.018983 | 0.060325 | 0.0012795 | 0.084417 | -58.8409 | 62.3199 | -60.7636 | -60.8597 | 54.3961 | 5.8456 | 62.1185 | 11.1649 | 62.233 | -60.8597 | -0.16937 | 0.059509 | 1.7532 | -0.2655 | -7.8644 | -0.2655 | -0.027466 | 1.9226 | 122.7127 | 71.759 | 114.9902 | 122.9141 | 1.7532 | 122.8271 | 66.4398 | -0.2655 | 122.9141 | 1.7532 | 66.4398 | 114.9902 | 122.8271 | -123.024 | -123.1201
1636.3281 | 123.0423 | -60.5667 | 62.2696 | 0.056915 | 0.02371 | 0.01167 | 0.020264 | 0.062034 | -0.0021383 | 0.084204 | -58.7402 | 62.3108 | -60.7269 | -60.759 | 54.4968 | 5.8594 | 62.1323 | 11.3205 | 62.265 | -60.8093 | -0.16022 | 0.041199 | 1.8265 | -0.19226 | -7.7728 | -0.24262 | -0.004577 | 1.9867 | 122.699 | 71.8872 | 115.0635 | 122.8775 | 1.8265 | 122.8317 | 66.4261 | -0.24262 | 122.8775 | 1.8265 | 66.4261 | 115.0635 | 122.8317 | -122.9965 | -123.0789
1637.3281 | 122.9874 | -60.585 | 62.2787 | 0.17136 | 0.026701 | 0.012311 | 0.020905 | 0.058402 | -0.0023519 | 0.087408 | -58.8547 | 62.3245 | -60.7498 | -60.7681 | 54.4464 | 5.8182 | 62.2009 | 11.2518 | 62.3108 | -60.8139 | -0.16479 | 0.045776 | 1.7303 | -0.1831 | -7.8323 | -0.22888 | 0.032043 | 1.8951 | 122.7859 | 71.8369 | 115.0314 | 122.9095 | 1.7303 | 122.8958 | 66.4032 | -0.22888 | 122.9095 | 1.7303 | 66.4032 | 115.0314 | 122.8958 | -123.0286 | -123.0927
1638.3281 | 123.0377 | -60.5621 | 62.2833 | -0.17197 | 0.022428 | 0.015729 | 0.020478 | 0.060111 | -0.0014975 | 0.084845 | -58.8181 | 62.3383 | -60.759 | -60.7956 | 54.4785 | 5.9555 | 62.3474 | 11.4624 | 62.2833 | -60.7956 | -0.19684 | 0.054932 | 1.7441 | -0.23346 | -7.8049 | -0.23346 | 0 | 1.9409 | 122.9095 | 72.0245 | 115.0406 | 122.9004 | 1.7441 | 122.8455 | 66.5176 | -0.23346 | 122.9004 | 1.7441 | 66.5176 | 115.0406 | 122.8455 | -123.0423 | -123.0789
1639.3438 | 123.0286 | -60.5484 | 62.2879 | -0.16434 | 0.023283 | 0.012738 | 0.020905 | 0.063316 | 0.00021151 | 0.083777 | -58.7173 | 62.3291 | -60.7224 | -60.7544 | 54.5151 | 6.0745 | 62.2696 | 11.467 | 62.2925 | -60.8185 | -0.17395 | 0.041199 | 1.8311 | -0.20599 | -7.7728 | -0.27008 | 0.004577 | 2.005 | 122.818 | 72.0154 | 115.0635 | 122.8775 | 1.8311 | 122.8409 | 66.6229 | -0.27008 | 122.8775 | 1.8311 | 66.6229 | 115.0635 | 122.8409 | -123.0103 | -123.1064
1640.3281 | 123.0377 | -60.5759 | 62.3062 | -0.072784 | 0.023496 | 0.012738 | 0.020692 | 0.060966 | 0.0029885 | 0.084631 | -58.7677 | 62.3199 | -60.7636 | -60.8185 | 54.5837 | 6.0379 | 62.3657 | 11.618 | 62.3062 | -60.7773 | -0.18768 | 0.013733 | 1.8082 | -0.24261 | -7.7225 | -0.20142 | 0 | 1.9959 | 122.9416 | 72.1939 | 115.1596 | 122.8958 | 1.8082 | 122.8821 | 66.6138 | -0.20142 | 122.8958 | 1.8082 | 66.6138 | 115.1596 | 122.8821 | -123.0698 | -123.0835
1641.3281 | 123.0698 | -60.5164 | 62.2971 | -0.12619 | 0.023924 | 0.0071842 | 0.018983 | 0.060539 | -0.0021383 | 0.082708 | -58.786 | 62.3337 | -60.7407 | -60.7727 | 54.5013 | 6.0837 | 62.2971 | 11.5128 | 62.2787 | -60.7819 | -0.22431 | 0.036621 | 1.7303 | -0.25635 | -7.7957 | -0.2655 | -0.01831 | 1.9547 | 122.8134 | 72.0291 | 115.0177 | 122.85 | 1.7303 | 122.7951 | 66.6 | -0.2655 | 122.85 | 1.7303 | 66.6 | 115.0177 | 122.7951 | -123.0377 | -123.0789
1642.3281 | 123.0194 | -60.5667 | 62.2971 | -0.14145 | 0.022428 | 0.014875 | 0.018555 | 0.061607 | -0.0019247 | 0.083563 | -58.7906 | 62.3245 | -60.7315 | -60.7727 | 54.4647 | 6.1661 | 62.3245 | 11.5173 | 62.3154 | -60.7956 | -0.1648 | 0.027466 | 1.7761 | -0.20599 | -7.8323 | -0.22888 | 0.018311 | 1.9409 | 122.8912 | 72.084 | 115.0314 | 122.8912 | 1.7761 | 122.8821 | 66.7328 | -0.22888 | 122.8912 | 1.7761 | 66.7328 | 115.0314 | 122.8821 | -123.0286 | -123.0927
1643.3281 | 123.0148 | -60.5713 | 62.2971 | -0.18723 | 0.021147 | 0.010602 | 0.017914 | 0.060539 | -0.0023519 | 0.084845 | -58.7997 | 62.3108 | -60.7544 | -60.7956 | 54.4418 | 6.102 | 62.3611 | 11.4578 | 62.3245 | -60.791 | -0.18311 | 0.013733 | 1.7715 | -0.2243 | -7.8552 | -0.21973 | 0.027466 | 1.9547 | 122.9324 | 72.0291 | 115.0131 | 122.8821 | 1.7715 | 122.8958 | 66.6733 | -0.21973 | 122.8821 | 1.7715 | 66.6733 | 115.0131 | 122.8958 | -123.0515 | -123.0881
1644.3281 | 122.9919 | -60.5804 | 62.3062 | -0.19485 | 0.020933 | 0.009534 | 0.015565 | 0.061607 | -0.0021383 | 0.082495 | -58.8455 | 62.2925 | -60.7452 | -60.8276 | 54.4601 | 6.1615 | 62.3611 | 11.4349 | 62.3062 | -60.7956 | -0.16479 | -0.013733 | 1.7349 | -0.24719 | -7.8461 | -0.21515 | 0 | 1.8997 | 122.9416 | 72.0154 | 115.0406 | 122.8729 | 1.7349 | 122.8867 | 66.7419 | -0.21515 | 122.8729 | 1.7349 | 66.7419 | 115.0406 | 122.8867 | -123.0515 | -123.1018
1645.3281 | 123.0057 | -60.5621 | 62.2925 | -0.24826 | 0.024778 | 0.010175 | 0.015351 | 0.059043 | 0.00042511 | 0.084845 | -58.6075 | 62.3199 | -60.7269 | -60.8322 | 54.4601 | 6.1661 | 62.3657 | 11.4761 | 62.3062 | -60.8047 | -0.16479 | 0.027466 | 1.9547 | -0.27008 | -7.8323 | -0.24262 | 0.013733 | 2.1194 | 122.9279 | 72.0383 | 115.0223 | 122.8821 | 1.9547 | 122.8683 | 66.7282 | -0.24262 | 122.8821 | 1.9547 | 66.7282 | 115.0223 | 122.8683 | -123.0194 | -123.0972
1646.3281 | 122.9782 | -60.5438 | 62.3245 | -0.22537 | 0.023924 | 0.011884 | 0.014069 | 0.059684 | 0.00042511 | 0.084631 | -58.8181 | 62.2787 | -60.7315 | -60.791 | 54.4739 | 6.2347 | 62.3657 | 11.5036 | 62.3154 | -60.791 | -0.18768 | -0.045776 | 1.7258 | -0.24719 | -7.8506 | -0.24719 | -0.009155 | 1.9135 | 122.9095 | 72.0474 | 115.0177 | 122.8226 | 1.7258 | 122.8592 | 66.7786 | -0.24719 | 122.8226 | 1.7258 | 66.7786 | 115.0177 | 122.8592 | -123.056 | -123.1155
1647.3438 | 123.0011 | -60.553 | 62.3199 | -0.13382 | 0.023069 | 0.015302 | 0.020264 | 0.059043 | -0.0014975 | 0.08399 | -58.8089 | 62.3108 | -60.7224 | -60.8093 | 54.4601 | 6.2027 | 62.3428 | 11.6043 | 62.3337 | -60.7727 | -0.16937 | -0.009155 | 1.7441 | -0.25635 | -7.8598 | -0.21973 | 0.013733 | 1.9135 | 122.8958 | 72.1573 | 115.0131 | 122.8638 | 1.7441 | 122.8867 | 66.7557 | -0.21973 | 122.8638 | 1.7441 | 66.7557 | 115.0131 | 122.8867 | -123.0423 | -123.0927
1648.3281 | 123.0286 | -60.5438 | 62.3199 | -0.21011 | 0.021147 | 0.013166 | 0.013215 | 0.059684 | -0.00085669 | 0.084845 | -58.8089 | 62.2787 | -60.7361 | -60.759 | 54.4785 | 6.134 | 62.3657 | 11.6913 | 62.2925 | -60.7727 | -0.19226 | -0.041198 | 1.7349 | -0.21515 | -7.8415 | -0.22888 | -0.027466 | 1.9272 | 122.9095 | 72.2351 | 115.0223 | 122.8226 | 1.7349 | 122.8363 | 66.6779 | -0.22888 | 122.8226 | 1.7349 | 66.6779 | 115.0223 | 122.8363 | -123.056 | -123.0927
1649.3281 | 123.0331 | -60.5255 | 62.3154 | -0.18723 | 0.022428 | 0.012738 | 0.016633 | 0.05648 | -0.00021569 | 0.083563 | -58.786 | 62.2421 | -60.704 | -60.7407 | 54.5334 | 6.1798 | 62.3016 | 11.6409 | 62.2833 | -60.7498 | -0.17853 | -0.073243 | 1.7395 | -0.21515 | -7.782 | -0.2243 | -0.032044 | 1.918 | 122.8271 | 72.1664 | 115.0589 | 122.7676 | 1.7395 | 122.8088 | 66.7053 | -0.2243 | 122.7676 | 1.7395 | 66.7053 | 115.0589 | 122.8088 | -123.0194 | -123.0652
1650.3438 | 122.9599 | -60.5621 | 62.3062 | 0.1561 | 0.024992 | 0.011884 | 0.020051 | 0.059898 | -0.0023519 | 0.082922 | -58.8501 | 62.3062 | -60.7498 | -61.0199 | 53.9886 | 5.9097 | 62.5717 | 11.6043 | 62.2833 | -60.8093 | -0.18768 | 0 | 1.712 | -0.45776 | -8.3176 | -0.24719 | -0.022888 | 1.8997 | 123.1338 | 72.1664 | 114.5508 | 122.8683 | 1.712 | 122.8455 | 66.4719 | -0.24719 | 122.8683 | 1.712 | 66.4719 | 114.5508 | 122.8455 | -123.056 | -123.1155
1651.3281 | 123.0972 | -60.5255 | 62.2787 | -0.20248 | 0.020078 | 0.0099612 | 0.014069 | 0.058616 | -0.0012839 | 0.08164 | -58.7448 | 62.2101 | -60.7086 | -60.7132 | 54.5654 | 6.2714 | 62.2101 | 11.6638 | 62.2925 | -60.7224 | -0.18311 | -0.068665 | 1.7807 | -0.18768 | -7.7133 | -0.19684 | 0.013732 | 1.9638 | 122.7356 | 72.1893 | 115.0909 | 122.7356 | 1.7807 | 122.818 | 66.7969 | -0.19684 | 122.7356 | 1.7807 | 66.7969 | 115.0909 | 122.818 | -122.9874 | -123.0011
1652.3281 | 123.0972 | -60.5118 | 62.2787 | -0.049896 | 0.019651 | 0.0086796 | 0.013215 | 0.057334 | 0.00063871 | 0.085272 | -58.7997 | 62.2147 | -60.7315 | -60.7178 | 54.538 | 6.2851 | 62.2009 | 11.7783 | 62.2238 | -60.7315 | -0.21973 | -0.064087 | 1.712 | -0.20599 | -7.7408 | -0.21973 | -0.054932 | 1.9318 | 122.7127 | 72.29 | 115.0497 | 122.7264 | 1.712 | 122.7356 | 66.7969 | -0.21973 | 122.7264 | 1.712 | 66.7969 | 115.0497 | 122.7356 | -123.0103 | -123.0103
1653.3438 | 123.1018 | -60.5164 | 62.2879 | -0.16434 | 0.022642 | 0.009534 | 0.014069 | 0.055412 | -0.0010703 | 0.084417 | -58.7494 | 62.2375 | -60.7086 | -60.6903 | 54.57 | 6.3446 | 62.2147 | 11.8469 | 62.2421 | -60.7315 | -0.19226 | -0.050354 | 1.767 | -0.17395 | -7.7179 | -0.21515 | -0.045777 | 1.9592 | 122.731 | 72.3633 | 115.0864 | 122.7539 | 1.767 | 122.7585 | 66.861 | -0.21515 | 122.7539 | 1.767 | 66.861 | 115.0864 | 122.7585 | -122.9965 | -123.0194
1654.3281 | 123.1293 | -60.4935 | 62.2925 | -1.9344 | 0.02136 | 0.011029 | 0.015992 | 0.055198 | -0.00042929 | 0.084845 | -58.9554 | 62.2238 | -60.7361 | -60.7132 | 54.5471 | 6.3446 | 62.2147 | 11.7737 | 62.2421 | -60.7452 | -0.24262 | -0.068664 | 1.5381 | -0.21973 | -7.7454 | -0.25177 | -0.050354 | 1.7807 | 122.7081 | 72.2672 | 115.0406 | 122.7173 | 1.5381 | 122.7356 | 66.8381 | -0.25177 | 122.7173 | 1.5381 | 66.8381 | 115.0406 | 122.7356 | -123.0286 | -123.0377
1655.3438 | 123.0515 | -60.553 | 62.3199 | -0.84335 | 0.024565 | 0.0093204 | 0.023896 | 0.059043 | -0.0021383 | 0.084631 | -58.7906 | 62.2971 | -60.7224 | -60.7132 | 54.4739 | 6.2347 | 62.265 | 11.792 | 62.2787 | -60.7956 | -0.16937 | -0.022888 | 1.7624 | -0.16022 | -7.8461 | -0.24261 | -0.041198 | 1.9318 | 122.818 | 72.345 | 115.0269 | 122.85 | 1.7624 | 122.8317 | 66.7877 | -0.24261 | 122.85 | 1.7624 | 66.7877 | 115.0269 | 122.8317 | -123.0423 | -123.1155
1656.3281 | 123.0286 | -60.5301 | 62.3016 | -0.15671 | 0.019224 | 0.007825 | 0.017274 | 0.057121 | -0.0029929 | 0.08399 | -58.8043 | 62.2421 | -60.7361 | -60.7178 | 54.5013 | 6.2164 | 62.352 | 11.8149 | 62.2971 | -60.7636 | -0.20599 | -0.05951 | 1.7258 | -0.18768 | -7.8003 | -0.23346 | -0.004578 | 1.9318 | 122.8821 | 72.345 | 115.0314 | 122.7722 | 1.7258 | 122.8271 | 66.7465 | -0.23346 | 122.7722 | 1.7258 | 66.7465 | 115.0314 | 122.8271 | -123.0377 | -123.0652
1657.3281 | 123.1247 | -60.5209 | 62.265 | -0.034637 | 0.01901 | 0.012311 | 0.013642 | 0.057762 | -0.0027793 | 0.084631 | -58.8089 | 62.1964 | -60.7452 | -60.7224 | 54.5151 | 6.4041 | 62.2055 | 11.8698 | 62.2375 | -60.7452 | -0.2243 | -0.068665 | 1.712 | -0.20142 | -7.7499 | -0.2243 | -0.027466 | 1.9363 | 122.7264 | 72.3907 | 115.036 | 122.7173 | 1.712 | 122.7585 | 66.925 | -0.2243 | 122.7173 | 1.712 | 66.925 | 115.036 | 122.7585 | -123.0103 | -123.0103
1658.3281 | 123.1155 | -60.5072 | 62.2879 | -0.0041198 | 0.020933 | 0.010388 | 0.016205 | 0.055198 | -0.0012839 | 0.084204 | -58.8318 | 62.2238 | -60.7407 | -60.759 | 54.4739 | 6.2393 | 62.2147 | 11.9476 | 62.2192 | -60.759 | -0.23346 | -0.064087 | 1.6754 | -0.25177 | -7.814 | -0.25177 | -0.068665 | 1.9089 | 122.7219 | 72.4548 | 114.9811 | 122.731 | 1.6754 | 122.7264 | 66.7465 | -0.25177 | 122.731 | 1.6754 | 66.7465 | 114.9811 | 122.7264 | -123.0286 | -123.0469
1659.3281 | 122.9919 | -60.5484 | 62.265 | 0.11795 | 0.018583 | 0.0086796 | 0.016205 | 0.057121 | 0.00021151 | 0.082281 | -58.8272 | 62.2147 | -60.7132 | -60.7956 | 54.451 | 6.2622 | 62.2101 | 11.9064 | 62.2055 | -60.7727 | -0.1648 | -0.050354 | 1.7212 | -0.24719 | -7.814 | -0.2243 | -0.05951 | 1.886 | 122.7585 | 72.4548 | 114.9994 | 122.7631 | 1.7212 | 122.7539 | 66.8106 | -0.2243 | 122.7631 | 1.7212 | 66.8106 | 114.9994 | 122.7539 | -122.9782 | -123.0377
1660.3438 | 123.0423 | -60.5301 | 62.3062 | -0.13382 | 0.021574 | 0.010816 | 0.021119 | 0.057548 | -0.0021383 | 0.082708 | -58.8135 | 62.3245 | -60.7269 | -60.7407 | 54.4418 | 6.1707 | 62.3291 | 11.911 | 62.2833 | -60.8002 | -0.19684 | 0.018311 | 1.7166 | -0.21057 | -7.8644 | -0.27008 | -0.022888 | 1.9135 | 122.8592 | 72.4411 | 114.9719 | 122.8546 | 1.7166 | 122.8134 | 66.7007 | -0.27008 | 122.8546 | 1.7166 | 66.7007 | 114.9719 | 122.8134 | -123.0331 | -123.1064
1661.3281 | 123.1064 | -60.5255 | 62.2787 | 0.064545 | 0.020933 | 0.007825 | 0.013001 | 0.056266 | -2.092e-06 | 0.083349 | -58.8409 | 62.2147 | -60.7315 | -60.759 | 54.5013 | 6.2531 | 62.2147 | 12.0026 | 62.2604 | -60.7178 | -0.20599 | -0.064087 | 1.6846 | -0.23346 | -7.7774 | -0.19226 | -0.018311 | 1.8906 | 122.7402 | 72.5281 | 115.0269 | 122.7402 | 1.6846 | 122.7859 | 66.7786 | -0.19226 | 122.7402 | 1.6846 | 66.7786 | 115.0269 | 122.7859 | -123.0103 | -122.9965
1662.3438 | 123.1064 | -60.5301 | 62.2833 | -0.019379 | 0.024137 | 0.010388 | 0.01471 | 0.054771 | -0.00064309 | 0.084417 | -58.8272 | 62.2101 | -60.7132 | -60.7224 | 54.4876 | 6.1707 | 62.2055 | 12.0255 | 62.2375 | -60.7361 | -0.18311 | -0.073242 | 1.7029 | -0.19226 | -7.7957 | -0.20599 | -0.045776 | 1.886 | 122.7356 | 72.5555 | 115.0177 | 122.7402 | 1.7029 | 122.7676 | 66.7007 | -0.20599 | 122.7402 | 1.7029 | 66.7007 | 115.0177 | 122.7676 | -122.9965 | -123.0194
1663.3281 | 123.3032 | -60.4752 | 62.3016 | -0.080414 | 0.020506 | 0.0080386 | 0.015992 | 0.053275 | -0.0021383 | 0.084845 | -58.7906 | 62.2192 | -60.7086 | -60.6491 | 54.5425 | 6.3354 | 62.1689 | 12.1719 | 62.2238 | -60.7452 | -0.23346 | -0.082398 | 1.6846 | -0.17395 | -7.7591 | -0.27008 | -0.07782 | 1.918 | 122.644 | 72.6471 | 115.0177 | 122.6944 | 1.6846 | 122.699 | 66.8106 | -0.27008 | 122.6944 | 1.6846 | 66.8106 | 115.0177 | 122.699 | -123.0103 | -123.0469
1664.3281 | 123.1384 | -60.5026 | 62.2742 | -0.019379 | 0.021787 | 0.009534 | 0.016205 | 0.056907 | -0.0017111 | 0.082281 | -58.8181 | 62.1918 | -60.7315 | -60.6949 | 54.4922 | 6.2119 | 62.1689 | 12.0712 | 62.2238 | -60.7498 | -0.22888 | -0.082398 | 1.6846 | -0.19226 | -7.782 | -0.24719 | -0.050354 | 1.9135 | 122.6715 | 72.5739 | 114.9948 | 122.6944 | 1.6846 | 122.7264 | 66.7145 | -0.24719 | 122.6944 | 1.6846 | 66.7145 | 114.9948 | 122.7264 | -123.0057 | -123.024
1665.3281 | 123.024 | -60.5209 | 62.3245 | -0.18723 | 0.021147 | 0.012738 | 0.018983 | 0.054557 | 0.00021151 | 0.084204 | -58.7723 | 62.2421 | -60.7086 | -60.7224 | 54.4785 | 6.2027 | 62.3062 | 11.9797 | 62.2604 | -60.759 | -0.18768 | -0.082398 | 1.7487 | -0.20142 | -7.8461 | -0.23804 | -0.064087 | 1.9363 | 122.8271 | 72.5006 | 114.9994 | 122.7631 | 1.7487 | 122.7814 | 66.7236 | -0.23804 | 122.7631 | 1.7487 | 66.7236 | 114.9994 | 122.7814 | -123.0331 | -123.0835
1666.3281 | 123.1064 | -60.553 | 62.2375 | 0.2095 | 0.019865 | 0.0082522 | 0.016419 | 0.05648 | 0.0010659 | 0.084631 | -58.7952 | 62.1872 | -60.7361 | -60.7407 | 54.4739 | 6.2714 | 62.1277 | 12.0163 | 62.2055 | -60.7727 | -0.1831 | -0.050354 | 1.7578 | -0.18768 | -7.7637 | -0.21973 | -0.032044 | 1.9409 | 122.6807 | 72.5693 | 115.0269 | 122.7402 | 1.7578 | 122.7585 | 66.8243 | -0.21973 | 122.7402 | 1.7578 | 66.8243 | 115.0269 | 122.7585 | -122.9736 | -123.0103
1667.3281 | 123.0789 | -60.5347 | 62.2192 | 0.17899 | 0.023069 | 0.0091068 | 0.016419 | 0.05648 | 0.0012795 | 0.083349 | -58.8272 | 62.1964 | -60.7407 | -60.7544 | 54.4373 | 6.2347 | 62.1689 | 11.9568 | 62.2192 | -60.7636 | -0.20599 | -0.022888 | 1.7075 | -0.21973 | -7.782 | -0.22888 | 0 | 1.9135 | 122.7036 | 72.4915 | 114.9719 | 122.731 | 1.7075 | 122.7539 | 66.7694 | -0.22888 | 122.731 | 1.7075 | 66.7694 | 114.9719 | 122.7539 | -122.9599 | -122.9828
1668.3281 | 123.0881 | -60.5484 | 62.2559 | 0.20187 | 0.020506 | 0.0080386 | 0.018342 | 0.054771 | -0.00021569 | 0.084631 | -58.7952 | 62.2192 | -60.7452 | -60.7315 | 54.4647 | 6.1615 | 62.146 | 12.0071 | 62.1964 | -60.7636 | -0.19684 | -0.036621 | 1.7532 | -0.18311 | -7.7911 | -0.21515 | -0.059509 | 1.9501 | 122.6944 | 72.5555 | 115.0131 | 122.7676 | 1.7532 | 122.7448 | 66.7099 | -0.21515 | 122.7676 | 1.7532 | 66.7099 | 115.0131 | 122.7448 | -123.0011 | -123.0194
1669.3281 | 123.1155 | -60.5392 | 62.2467 | 0.17899 | 0.019865 | 0.012311 | 0.018342 | 0.056907 | -0.0021383 | 0.083349 | -58.7997 | 62.2101 | -60.7224 | -60.7178 | 54.483 | 6.2256 | 62.1002 | 12.085 | 62.2009 | -60.7773 | -0.18311 | -0.036621 | 1.7395 | -0.17853 | -7.7637 | -0.23804 | -0.045776 | 1.9226 | 122.6395 | 72.6242 | 115.0223 | 122.7493 | 1.7395 | 122.7402 | 66.7648 | -0.23804 | 122.7493 | 1.7395 | 66.7648 | 115.0223 | 122.7402 | -122.9691 | -123.024
1670.3281 | 123.1201 | -60.5347 | 62.2284 | 0.29343 | 0.021147 | 0.013806 | 0.01941 | 0.057548 | -0.00042929 | 0.083136 | -58.8043 | 62.2147 | -60.7315 | -60.704 | 54.4739 | 6.1569 | 62.0865 | 12.0804 | 62.1964 | -60.7727 | -0.19684 | -0.013733 | 1.7303 | -0.16937 | -7.7545 | -0.23804 | -0.032044 | 1.9272 | 122.6212 | 72.6151 | 115.0085 | 122.7493 | 1.7303 | 122.731 | 66.6916 | -0.23804 | 122.7493 | 1.7303 | 66.6916 | 115.0085 | 122.731 | -122.9599 | -123.0011
1671.3281 | 123.111 | -61.1984 | 61.6241 | 0.24765 | 0.022001 | 0.016584 | 0.02411 | 0.057548 | 0.00042511 | 0.084631 | -59.4635 | 61.6196 | -61.3815 | -61.3632 | 54.0115 | 6.4865 | 61.5051 | 55.3436 | 61.5692 | -61.4365 | -0.18311 | -0.004578 | 1.7349 | -0.16479 | -7.6126 | -0.23804 | -0.054932 | 1.918 | 122.7036 | 116.5421 | 115.21 | 122.818 | 1.7349 | 122.7676 | 67.6849 | -0.23804 | 122.818 | 1.7349 | 67.6849 | 115.21 | 122.7676 | -123.0057 | -123.0606
1672.3281 | 123.0148 | -61.2213 | 61.615 | -0.38559 | 0.024565 | 0.010388 | 0.026246 | 0.058402 | -0.0025657 | 0.085699 | -59.5001 | 61.6699 | -61.4182 | -61.4594 | 53.9703 | 6.4499 | 61.6333 | 55.6412 | 61.6058 | -61.4777 | -0.19684 | 0.054932 | 1.7212 | -0.23804 | -7.6447 | -0.25635 | -0.009155 | 1.918 | 122.8546 | 116.8625 | 115.1917 | 122.8912 | 1.7212 | 122.8271 | 67.6712 | -0.25635 | 122.8912 | 1.7212 | 67.6712 | 115.1917 | 122.8271 | -123.0331 | -123.0927
1673.3281 | 122.9782 | -61.2076 | 61.6333 | 0.16373 | 0.024992 | 0.017865 | 0.023682 | 0.063102 | 0.0021341 | 0.083136 | -59.5322 | 61.6791 | -61.4044 | -61.3586 | 54.1809 | 6.4682 | 61.7477 | 55.7648 | 61.647 | -61.4365 | -0.19684 | 0.045776 | 1.6754 | -0.15106 | -7.4524 | -0.22888 | 0.013733 | 1.8723 | 122.9553 | 116.9724 | 115.3885 | 122.8867 | 1.6754 | 122.8546 | 67.6758 | -0.22888 | 122.8867 | 1.6754 | 67.6758 | 115.3885 | 122.8546 | -123.0377 | -123.0698
1674.3281 | 123.0469 | -61.1984 | 61.6104 | 0.22476 | 0.02371 | 0.012952 | 0.02411 | 0.062248 | -0.0017111 | 0.085913 | -59.5322 | 61.6425 | -61.3907 | -61.4273 | 53.9886 | 6.5598 | 61.5417 | 56.0211 | 61.5784 | -61.4594 | -0.19226 | 0.032043 | 1.6663 | -0.22888 | -7.6218 | -0.26093 | -0.032044 | 1.8585 | 122.7402 | 117.2195 | 115.1871 | 122.8409 | 1.6663 | 122.7768 | 67.7582 | -0.26093 | 122.8409 | 1.6663 | 67.7582 | 115.1871 | 122.7768 | -123.0011 | -123.0698
1675.3281 | 123.0194 | -61.235 | 61.6104 | 0.20187 | 0.027128 | 0.011243 | 0.023469 | 0.060325 | -0.0012839 | 0.087622 | -59.5184 | 61.6425 | -61.3998 | -61.4868 | 53.9429 | 6.5735 | 61.5921 | 56.0715 | 61.5875 | -61.4868 | -0.1648 | 0.032043 | 1.7166 | -0.25177 | -7.6675 | -0.25177 | -0.022889 | 1.8814 | 122.8271 | 117.3065 | 115.1779 | 122.8775 | 1.7166 | 122.8226 | 67.8085 | -0.25177 | 122.8775 | 1.7166 | 67.8085 | 115.1779 | 122.8226 | -123.0103 | -123.0972
1676.3281 | 123.0377 | -61.2122 | 61.5967 | 0.20187 | 0.023069 | 0.016156 | 0.020905 | 0.060752 | 0.00021151 | 0.086554 | -59.5413 | 61.6196 | -61.4273 | -61.4456 | 53.9932 | 6.6284 | 61.5555 | 56.2088 | 61.5417 | -61.496 | -0.21515 | 0.022888 | 1.6708 | -0.23346 | -7.6035 | -0.28381 | -0.054932 | 1.886 | 122.7676 | 117.421 | 115.2054 | 122.8317 | 1.6708 | 122.7539 | 67.8406 | -0.28381 | 122.8317 | 1.6708 | 67.8406 | 115.2054 | 122.7539 | -123.024 | -123.0927
1677.3281 | 123.024 | -61.2442 | 61.5784 | 0.20187 | 0.024778 | 0.013166 | 0.022401 | 0.059684 | -0.0012839 | 0.087408 | -59.5322 | 61.6425 | -61.4365 | -61.496 | 53.9566 | 6.6833 | 61.5784 | 56.4056 | 61.5784 | -61.5005 | -0.19226 | 0.064087 | 1.712 | -0.25177 | -7.6218 | -0.25635 | 0 | 1.9043 | 122.8226 | 117.6498 | 115.2008 | 122.8867 | 1.712 | 122.8226 | 67.9276 | -0.25635 | 122.8867 | 1.712 | 67.9276 | 115.2008 | 122.8226 | -123.0148 | -123.0789
1678.3281 | 123.0148 | -61.2396 | 61.6013 | 0.21713 | 0.025205 | 0.014447 | 0.021332 | 0.060111 | -0.0025657 | 0.086981 | -59.5551 | 61.647 | -61.4227 | -61.5051 | 53.9429 | 6.5506 | 61.6196 | 56.4468 | 61.615 | -61.4868 | -0.1831 | 0.045777 | 1.6846 | -0.2655 | -7.6584 | -0.24719 | 0.013733 | 1.8677 | 122.8592 | 117.6865 | 115.1825 | 122.8867 | 1.6846 | 122.8546 | 67.7902 | -0.24719 | 122.8867 | 1.6846 | 67.7902 | 115.1825 | 122.8546 | -123.024 | -123.0881
1679.3281 | 122.9965 | -61.2305 | 61.6241 | 0.011139 | 0.025205 | 0.016797 | 0.022187 | 0.06182 | -0.0032065 | 0.087622 | -59.5047 | 61.6745 | -61.409 | -61.4502 | 53.9703 | 6.5689 | 61.647 | 56.6116 | 61.6379 | -61.4639 | -0.17853 | 0.050354 | 1.7258 | -0.21973 | -7.6538 | -0.23346 | 0.013732 | 1.9043 | 122.8775 | 117.8421 | 115.2008 | 122.905 | 1.7258 | 122.8683 | 67.7994 | -0.23346 | 122.905 | 1.7258 | 67.7994 | 115.2008 | 122.8683 | -123.0331 | -123.0881
1680.3281 | 122.9874 | -61.2167 | 61.615 | 0.049286 | 0.023069 | 0.014447 | 0.02176 | 0.062034 | -0.0027793 | 0.085913 | -59.4543 | 61.6745 | -61.3907 | -61.4319 | 53.9932 | 6.5735 | 61.6379 | 56.6574 | 61.6287 | -61.4685 | -0.17395 | 0.05951 | 1.7624 | -0.21515 | -7.6218 | -0.25177 | 0.013733 | 1.9363 | 122.8546 | 117.8741 | 115.21 | 122.8912 | 1.7624 | 122.8455 | 67.7902 | -0.25177 | 122.8912 | 1.7624 | 67.7902 | 115.21 | 122.8455 | -123.0057 | -123.0835
1681.3281 | 122.9874 | -61.2259 | 61.6058 | 0.049286 | 0.022856 | 0.019147 | 0.021546 | 0.062034 | -0.0010703 | 0.085913 | -59.5184 | 61.6837 | -61.4227 | -61.4731 | 53.9658 | 6.5414 | 61.6379 | 56.7444 | 61.5875 | -61.5143 | -0.19684 | 0.07782 | 1.7075 | -0.24719 | -7.6401 | -0.28839 | -0.018311 | 1.9043 | 122.8638 | 117.9703 | 115.1916 | 122.9095 | 1.7075 | 122.8134 | 67.7673 | -0.28839 | 122.9095 | 1.7075 | 67.7673 | 115.1916 | 122.8134 | -123.0286 | -123.1201
1682.3281 | 123.0194 | -61.235 | 61.615 | 0.11032 | 0.026914 | 0.010816 | 0.02176 | 0.062248 | -2.092e-06 | 0.087195 | -59.5093 | 61.6562 | -61.4136 | -61.4731 | 53.9795 | 6.5918 | 61.6379 | 56.7719 | 61.6241 | -61.5005 | -0.17853 | 0.041199 | 1.7258 | -0.23804 | -7.6355 | -0.2655 | 0.009156 | 1.9043 | 122.8729 | 118.0069 | 115.2145 | 122.8912 | 1.7258 | 122.8592 | 67.8268 | -0.2655 | 122.8912 | 1.7258 | 67.8268 | 115.2145 | 122.8592 | -123.0286 | -123.1155
1683.3281 | 123.0194 | -61.2396 | 61.6287 | -0.0041198 | 0.026914 | 0.012738 | 0.021119 | 0.062889 | -0.0014975 | 0.085058 | -59.4864 | 61.6791 | -61.377 | -61.441 | 53.9932 | 6.6238 | 61.6379 | 56.9 | 61.6516 | -61.4685 | -0.13733 | 0.050354 | 1.7532 | -0.20142 | -7.6355 | -0.22888 | 0.022888 | 1.8906 | 122.8775 | 118.1396 | 115.2328 | 122.9187 | 1.7532 | 122.8912 | 67.8635 | -0.22888 | 122.9187 | 1.7532 | 67.8635 | 115.2328 | 122.8912 | -123.0057 | -123.0972
1684.3281 | 123.0377 | -61.2259 | 61.6013 | -0.0041198 | 0.025419 | 0.016156 | 0.022401 | 0.062889 | -0.00021569 | 0.085272 | -59.4681 | 61.6653 | -61.4044 | -61.4319 | 54.0207 | 6.6559 | 61.6196 | 56.9321 | 61.6379 | -61.4731 | -0.17853 | 0.064087 | 1.7578 | -0.20599 | -7.5806 | -0.24719 | 0.036621 | 1.9363 | 122.8455 | 118.158 | 115.2466 | 122.8912 | 1.7578 | 122.8638 | 67.8818 | -0.24719 | 122.8912 | 1.7578 | 67.8818 | 115.2466 | 122.8638 | -123.0057 | -123.0743
1685.3281 | 123.0515 | -61.2259 | 61.6196 | -0.87387 | 0.02371 | 0.010388 | 0.020905 | 0.062034 | -0.0012839 | 0.087195 | -59.4269 | 61.6928 | -61.3907 | -61.3861 | 54.0298 | 6.6925 | 61.615 | 57.0465 | 61.6425 | -61.4456 | -0.1648 | 0.073242 | 1.799 | -0.16022 | -7.5897 | -0.21973 | 0.022888 | 1.9638 | 122.8409 | 118.2724 | 115.2557 | 122.9187 | 1.799 | 122.8683 | 67.9184 | -0.21973 | 122.9187 | 1.799 | 67.9184 | 115.2557 | 122.8683 | -123.0103 | -123.0652
1686.3281 | 123.0194 | -61.2259 | 61.647 | -0.16434 | 0.022856 | 0.010602 | 0.018555 | 0.062248 | -0.0021383 | 0.084204 | -59.5093 | 61.6562 | -61.4136 | -61.4594 | 54.007 | 6.5826 | 61.7065 | 57.0145 | 61.6608 | -61.4456 | -0.18768 | 0.009155 | 1.7166 | -0.23346 | -7.6401 | -0.21973 | 0.013733 | 1.9043 | 122.9324 | 118.2404 | 115.2328 | 122.8821 | 1.7166 | 122.8867 | 67.8085 | -0.21973 | 122.8821 | 1.7166 | 67.8085 | 115.2328 | 122.8867 | -123.0606 | -123.0927
1687.3281 | 122.9965 | -61.2396 | 61.647 | -0.15671 | 0.022856 | 0.012952 | 0.017274 | 0.06118 | -0.0012839 | 0.088049 | -59.5093 | 61.6791 | -61.3998 | -61.4822 | 53.9795 | 6.6559 | 61.7249 | 57.1243 | 61.6516 | -61.4456 | -0.16022 | 0.032043 | 1.7303 | -0.24262 | -7.6675 | -0.20599 | 0.004577 | 1.8906 | 122.9645 | 118.364 | 115.2191 | 122.9187 | 1.7303 | 122.8912 | 67.8955 | -0.20599 | 122.9187 | 1.7303 | 67.8955 | 115.2191 | 122.8912 | -123.0469 | -123.0927
1688.3594 | 123.056 | -61.2259 | 61.6287 | -0.049896 | 0.02371 | 0.0097476 | 0.01941 | 0.062034 | -0.0012839 | 0.086767 | -59.4589 | 61.6745 | -61.3998 | -61.4182 | 53.9291 | 6.5231 | 61.7386 | 57.5089 | 61.615 | -61.4639 | -0.17395 | 0.045777 | 1.767 | -0.19226 | -7.6996 | -0.23804 | -0.013733 | 1.9409 | 122.9645 | 118.7347 | 115.155 | 122.9004 | 1.767 | 122.8409 | 67.749 | -0.23804 | 122.9004 | 1.767 | 67.749 | 115.155 | 122.8409 | -123.0286 | -123.0927
1689.3281 | 123.056 | -61.2442 | 61.615 | -0.19485 | 0.022001 | 0.012738 | 0.020051 | 0.060752 | -0.00064309 | 0.083563 | -59.5001 | 61.6516 | -61.4227 | -61.4502 | 54.0161 | 6.72 | 61.6608 | 57.9987 | 61.6241 | -61.4685 | -0.17853 | 0.036621 | 1.7441 | -0.20599 | -7.5989 | -0.2243 | 0.009156 | 1.9226 | 122.905 | 119.2429 | 115.2603 | 122.8958 | 1.7441 | 122.8683 | 67.9642 | -0.2243 | 122.8958 | 1.7441 | 67.9642 | 115.2603 | 122.8683 | -123.0377 | -123.0835
1690.3438 | 123.0057 | -61.2076 | 61.6379 | -0.1796 | 0.022642 | 0.011457 | 0.015778 | 0.060325 | -0.0047019 | 0.085913 | -59.5322 | 61.6241 | -61.3998 | -61.496 | 53.9566 | 6.6879 | 61.6974 | 58.9508 | 61.6196 | -61.4365 | -0.19226 | -0.013732 | 1.6754 | -0.28839 | -7.6813 | -0.22888 | -0.01831 | 1.8677 | 122.905 | 120.1584 | 115.1642 | 122.8317 | 1.6754 | 122.8271 | 67.8955 | -0.22888 | 122.8317 | 1.6754 | 67.8955 | 115.1642 | 122.8271 | -123.0377 | -123.0743
1691.3281 | 123.0103 | -61.2854 | 61.6058 | -0.16434 | 0.024565 | 0.015302 | 0.017487 | 0.059898 | -0.0010703 | 0.08634 | -59.5825 | 61.615 | -61.4365 | -61.5005 | 53.9154 | 6.6696 | 61.6928 | 59.9899 | 61.5967 | -61.5005 | -0.15106 | 0.009155 | 1.7029 | -0.21515 | -7.6904 | -0.21515 | -0.009155 | 1.8539 | 122.9782 | 121.2753 | 115.2008 | 122.9004 | 1.7029 | 122.8821 | 67.955 | -0.21515 | 122.9004 | 1.7029 | 67.955 | 115.2008 | 122.8821 | -123.0423 | -123.1064
1692.3281 | 123.0103 | -61.235 | 61.6333 | -0.1796 | 0.021787 | 0.014234 | 0.020051 | 0.058189 | -0.00064309 | 0.08399 | -59.5551 | 61.6241 | -61.441 | -61.4868 | 53.9337 | 6.5643 | 61.7111 | 58.786 | 61.6287 | -61.4731 | -0.20599 | -0.009155 | 1.68 | -0.25177 | -7.6996 | -0.23804 | -0.004578 | 1.886 | 122.9462 | 120.0211 | 115.1688 | 122.8592 | 1.68 | 122.8638 | 67.7994 | -0.23804 | 122.8592 | 1.68 | 67.7994 | 115.1688 | 122.8638 | -123.0743 | -123.1064
1693.3281 | 123.0652 | -61.2076 | 61.615 | -0.18723 | 0.01901 | 0.0080386 | 0.017701 | 0.05883 | -0.0021383 | 0.084845 | -59.4864 | 61.5784 | -61.3724 | -61.4365 | 54.0115 | 6.6925 | 61.615 | 58.7814 | 61.6196 | -61.4319 | -0.16479 | -0.036621 | 1.7212 | -0.22888 | -7.6035 | -0.2243 | 0.004578 | 1.886 | 122.8226 | 119.989 | 115.2191 | 122.7859 | 1.7212 | 122.8271 | 67.9001 | -0.2243 | 122.7859 | 1.7212 | 67.9001 | 115.2191 | 122.8271 | -122.9874 | -123.0469
1694.3281 | 123.0881 | -61.203 | 61.5967 | -0.16434 | 0.020292 | 0.010175 | 0.016205 | 0.058402 | -0.0029929 | 0.08399 | -59.4681 | 61.5555 | -61.4182 | -61.3998 | 54.0207 | 6.7017 | 61.5738 | 59.7061 | 61.5829 | -61.4319 | -0.21515 | -0.041199 | 1.7349 | -0.19684 | -7.576 | -0.22888 | -0.013733 | 1.9501 | 122.7768 | 120.9091 | 115.2237 | 122.7585 | 1.7349 | 122.7859 | 67.9047 | -0.22888 | 122.7585 | 1.7349 | 67.9047 | 115.2237 | 122.7859 | -123.0148 | -123.0286
1695.3281 | 122.9691 | -61.2534 | 61.6196 | -0.233 | 0.021787 | 0.0099612 | 0.020905 | 0.057548 | -0.0023519 | 0.084631 | -59.5825 | 61.5829 | -61.3998 | -61.4319 | 54.1992 | 6.7429 | 61.5646 | 59.0836 | 61.6379 | -61.4731 | -0.14648 | -0.036621 | 1.6708 | -0.17853 | -7.4203 | -0.21973 | 0.01831 | 1.8173 | 122.818 | 120.3369 | 115.4526 | 122.8363 | 1.6708 | 122.8912 | 67.9962 | -0.21973 | 122.8363 | 1.6708 | 67.9962 | 115.4526 | 122.8912 | -123.0194 | -123.0927
1696.3281 | 123.1155 | -61.2122 | 61.5921 | -0.14908 | 0.021147 | 0.0099612 | 0.018983 | 0.057334 | -2.092e-06 | 0.086767 | -59.4864 | 61.5005 | -61.4456 | -61.4136 | 54.0344 | 6.7337 | 61.5601 | 60.2737 | 61.5509 | -61.4319 | -0.23346 | -0.091553 | 1.7258 | -0.20142 | -7.5577 | -0.21973 | -0.041199 | 1.9592 | 122.7722 | 121.4859 | 115.2466 | 122.7127 | 1.7258 | 122.7631 | 67.9459 | -0.21973 | 122.7127 | 1.7258 | 67.9459 | 115.2466 | 122.7631 | -123.0377 | -123.024
1697.3281 | 123.024 | -61.2076 | 61.6241 | -0.21011 | 0.019224 | 0.0082522 | 0.019837 | 0.054771 | 0.00042511 | 0.085272 | -59.491 | 61.5646 | -61.4182 | -61.4227 | 54.007 | 6.7474 | 61.6379 | 59.6054 | 61.6058 | -61.4273 | -0.21057 | -0.05951 | 1.7166 | -0.21515 | -7.6172 | -0.21973 | -0.018311 | 1.9272 | 122.8455 | 120.813 | 115.2145 | 122.7722 | 1.7166 | 122.8134 | 67.955 | -0.21973 | 122.7722 | 1.7166 | 67.955 | 115.2145 | 122.8134 | -123.0423 | -123.0515
1698.3281 | 123.0743 | -61.2259 | 61.6058 | -0.21011 | 0.020292 | 0.011029 | 0.017701 | 0.058402 | -0.0032065 | 0.08634 | -59.4818 | 61.5326 | -61.3907 | -61.3998 | 54.0207 | 6.7657 | 61.5829 | 59.4635 | 61.6013 | -61.4273 | -0.1648 | -0.073242 | 1.7441 | -0.17395 | -7.5851 | -0.20142 | -0.004578 | 1.9089 | 122.8088 | 120.6894 | 115.2466 | 122.7585 | 1.7441 | 122.8271 | 67.9916 | -0.20142 | 122.7585 | 1.7441 | 67.9916 | 115.2466 | 122.8271 | -122.9965 | -123.0331
1699.3281 | 123.0881 | -61.2167 | 61.5692 | -0.1796 | 0.020292 | 0.010816 | 0.018769 | 0.054771 | -0.0032065 | 0.085058 | -59.4772 | 61.5234 | -61.4044 | -61.4044 | 54.0436 | 6.7795 | 61.5463 | 60.2829 | 61.5829 | -61.4365 | -0.18768 | -0.045777 | 1.7395 | -0.18768 | -7.5256 | -0.21973 | 0.013733 | 1.9272 | 122.7631 | 121.4996 | 115.2603 | 122.7402 | 1.7395 | 122.7997 | 67.9962 | -0.21973 | 122.7402 | 1.7395 | 67.9962 | 115.2603 | 122.7997 | -122.9736 | -123.0057
1700.3281 | 123.2758 | -61.1984 | 61.6608 | -0.13382 | 0.022642 | 0.0091068 | 0.017487 | 0.055198 | -0.00064309 | 0.085058 | -59.4818 | 61.5097 | -61.3953 | -61.3815 | 54.0665 | 6.8527 | 61.5097 | 59.2484 | 61.5692 | -61.3998 | -0.19684 | -0.15106 | 1.7166 | -0.18311 | -7.5943 | -0.20142 | -0.091553 | 1.9135 | 122.7081 | 120.4468 | 115.2649 | 122.7081 | 1.7166 | 122.7676 | 68.0511 | -0.20142 | 122.7081 | 1.7166 | 68.0511 | 115.2649 | 122.7676 | -123.056 | -123.0606
1701.3281 | 123.1338 | -61.2259 | 61.5967 | 0.32394 | 0.020933 | 0.010175 | 0.018555 | 0.055198 | -0.0021383 | 0.085913 | -59.4864 | 61.5143 | -61.3953 | -61.3724 | 54.039 | 6.7657 | 61.528 | 59.0744 | 61.5326 | -61.4456 | -0.16937 | -0.082398 | 1.7395 | -0.14648 | -7.5577 | -0.21973 | -0.064087 | 1.9089 | 122.7539 | 120.3003 | 115.2649 | 122.7402 | 1.7395 | 122.7585 | 67.9916 | -0.21973 | 122.7402 | 1.7395 | 67.9916 | 115.2649 | 122.7585 | -122.9919 | -123.0423
1702.3281 | 123.0835 | -61.2213 | 61.5738 | -0.15671 | 0.01837 | 0.0084658 | 0.018555 | 0.055625 | -0.0027793 | 0.086981 | -59.5001 | 61.528 | -61.4136 | -61.3724 | 54.0298 | 6.7245 | 61.5417 | 59.2804 | 61.5692 | -61.4365 | -0.19226 | -0.045777 | 1.7212 | -0.15106 | -7.5439 | -0.21515 | -0.004578 | 1.9135 | 122.7631 | 120.5017 | 115.2512 | 122.7493 | 1.7212 | 122.7905 | 67.9459 | -0.21515 | 122.7493 | 1.7212 | 67.9459 | 115.2512 | 122.7905 | -122.9874 | -123.0103
1703.3281 | 123.1018 | -61.2122 | 61.5784 | -0.088043 | 0.019438 | 0.012952 | 0.017274 | 0.055198 | -0.0021383 | 0.085272 | -59.4727 | 61.5463 | -61.4044 | -61.3632 | 54.039 | 6.8069 | 61.5189 | 59.1614 | 61.5646 | -61.409 | -0.19226 | -0.032043 | 1.7395 | -0.15106 | -7.5394 | -0.19684 | -0.013733 | 1.9318 | 122.731 | 120.3735 | 115.2512 | 122.7585 | 1.7395 | 122.7768 | 68.0191 | -0.19684 | 122.7585 | 1.7395 | 68.0191 | 115.2512 | 122.7768 | -122.9828 | -122.9874
1704.3281 | 123.0972 | -61.203 | 61.5738 | -0.45425 | 0.016874 | 0.0069706 | 0.018983 | 0.055839 | -0.0053427 | 0.083777 | -59.5184 | 61.4822 | -61.4227 | -61.377 | 54.0573 | 6.8802 | 61.5189 | 59.4727 | 61.5326 | -61.4044 | -0.21973 | -0.091553 | 1.6846 | -0.17395 | -7.5165 | -0.20142 | -0.041199 | 1.9043 | 122.7219 | 120.6757 | 115.2603 | 122.6852 | 1.6846 | 122.7356 | 68.0832 | -0.20142 | 122.6852 | 1.6846 | 68.0832 | 115.2603 | 122.7356 | -122.9965 | -122.9782
1705.3281 | 123.1247 | -61.2167 | 61.5784 | -0.095673 | 0.017729 | 0.013166 | 0.017487 | 0.054557 | -0.0064109 | 0.08634 | -59.4864 | 61.5051 | -61.4136 | -61.2671 | 53.7186 | 6.6742 | 61.3953 | 60.0128 | 61.5234 | -61.4502 | -0.19684 | -0.073242 | 1.7303 | -0.050354 | -7.8598 | -0.23346 | -0.054932 | 1.9272 | 122.612 | 121.2296 | 114.9353 | 122.7219 | 1.7303 | 122.7402 | 67.8909 | -0.23346 | 122.7219 | 1.7303 | 67.8909 | 114.9353 | 122.7402 | -122.9919 | -123.0286
1706.3281 | 123.1522 | -61.2259 | 61.5463 | -0.049896 | 0.020933 | 0.0037662 | 0.017701 | 0.054557 | -0.0012839 | 0.085913 | -59.4864 | 61.4868 | -61.4136 | -61.3907 | 54.0344 | 6.9168 | 61.4685 | 60.8185 | 61.5326 | -61.4548 | -0.18768 | -0.05951 | 1.7395 | -0.1648 | -7.5119 | -0.22888 | -0.013733 | 1.9272 | 122.6944 | 122.0444 | 115.2603 | 122.7127 | 1.7395 | 122.7585 | 68.1427 | -0.22888 | 122.7127 | 1.7395 | 68.1427 | 115.2603 | 122.7585 | -122.9599 | -123.0011
1707.3281 | 123.0881 | -61.2305 | 61.5417 | 0.041657 | 0.016661 | 0.012738 | 0.016419 | 0.054344 | -0.0042747 | 0.08399 | -59.5642 | 61.496 | -61.4365 | -61.441 | 53.9886 | 6.8756 | 61.496 | 61.2991 | 61.5143 | -61.4777 | -0.20599 | -0.045776 | 1.6663 | -0.21057 | -7.5531 | -0.24719 | -0.027466 | 1.8723 | 122.7264 | 122.5296 | 115.2191 | 122.7264 | 1.6663 | 122.7448 | 68.1061 | -0.24719 | 122.7264 | 1.6663 | 68.1061 | 115.2191 | 122.7448 | -122.9782 | -123.0194
1708.3281 | 123.1247 | -61.235 | 61.5601 | -0.080414 | 0.020292 | 0.011457 | 0.018983 | 0.054984 | -0.0010703 | 0.085486 | -59.5139 | 61.4731 | -61.4319 | -61.4227 | 53.9978 | 6.8115 | 61.4868 | 61.322 | 61.5234 | -61.4594 | -0.19684 | -0.086976 | 1.7212 | -0.18768 | -7.5623 | -0.22431 | -0.036622 | 1.918 | 122.7219 | 122.5571 | 115.2328 | 122.7081 | 1.7212 | 122.7585 | 68.0466 | -0.22431 | 122.7081 | 1.7212 | 68.0466 | 115.2328 | 122.7585 | -122.9919 | -123.0194
1709.3281 | 123.2849 | -61.171 | 61.6379 | -0.11856 | 0.021147 | 0.0076114 | 0.01706 | 0.054771 | -0.0012839 | 0.085272 | -59.4406 | 61.5189 | -61.3815 | -61.3312 | 54.0848 | 6.8298 | 61.4868 | 60.0769 | 61.5463 | -61.409 | -0.21057 | -0.11902 | 1.7303 | -0.16022 | -7.5531 | -0.23804 | -0.091552 | 1.9409 | 122.6578 | 121.2479 | 115.2557 | 122.6898 | 1.7303 | 122.7173 | 68.0008 | -0.23804 | 122.6898 | 1.7303 | 68.0008 | 115.2557 | 122.7173 | -123.0194 | -123.0469
1710.3281 | 123.1384 | -61.1938 | 61.5784 | -0.072784 | 0.018156 | 0.012311 | 0.018769 | 0.055198 | -0.0025657 | 0.084845 | -59.5047 | 61.5051 | -61.4273 | -61.3724 | 54.0253 | 6.8527 | 61.496 | 61.1664 | 61.5234 | -61.4182 | -0.23346 | -0.073242 | 1.6891 | -0.17853 | -7.5531 | -0.2243 | -0.054932 | 1.9226 | 122.6898 | 122.3602 | 115.2191 | 122.699 | 1.6891 | 122.7173 | 68.0466 | -0.2243 | 122.699 | 1.6891 | 68.0466 | 115.2191 | 122.7173 | -123.0057 | -122.9965
1711.3281 | 123.1201 | -61.203 | 61.5692 | -0.065155 | 0.020292 | 0.012311 | 0.017914 | 0.053703 | 0.00063871 | 0.084631 | -59.5139 | 61.5234 | -61.409 | -61.3632 | 54.0436 | 6.8802 | 61.5372 | 60.0586 | 61.5326 | -61.4136 | -0.20599 | -0.045777 | 1.6891 | -0.16022 | -7.5256 | -0.21057 | -0.036621 | 1.8951 | 122.7402 | 121.2616 | 115.2466 | 122.7264 | 1.6891 | 122.7356 | 68.0832 | -0.21057 | 122.7264 | 1.6891 | 68.0832 | 115.2466 | 122.7356 | -122.9782 | -122.9828
1712.3281 | 123.0515 | -61.2167 | 61.6013 | -0.18723 | 0.019651 | 0.0056888 | 0.019623 | 0.056907 | -0.0025657 | 0.083136 | -59.4955 | 61.528 | -61.4136 | -61.3907 | 53.9841 | 6.8436 | 61.6013 | 61.2213 | 61.5601 | -61.4456 | -0.19684 | -0.073242 | 1.7212 | -0.17395 | -7.6172 | -0.22888 | -0.041198 | 1.918 | 122.818 | 122.438 | 115.2008 | 122.7448 | 1.7212 | 122.7768 | 68.0603 | -0.22888 | 122.7448 | 1.7212 | 68.0603 | 115.2008 | 122.7768 | -123.0148 | -123.0469
1713.3281 | 123.1247 | -61.203 | 61.5829 | -0.011749 | 0.020292 | 0.005048 | 0.016846 | 0.054984 | -0.00064309 | 0.08634 | -59.5322 | 61.5097 | -61.4319 | -61.4044 | 53.9932 | 6.8985 | 61.5234 | 59.8755 | 61.5326 | -61.4273 | -0.22888 | -0.073242 | 1.6708 | -0.20142 | -7.5897 | -0.2243 | -0.050354 | 1.8997 | 122.7264 | 121.0785 | 115.1962 | 122.7127 | 1.6708 | 122.7356 | 68.1015 | -0.2243 | 122.7127 | 1.6708 | 68.1015 | 115.1962 | 122.7356 | -123.0148 | -123.0103
1714.3281 | 123.0835 | -61.235 | 61.5463 | 0.58334 | 0.022856 | 0.013379 | 0.018983 | 0.056693 | -0.0029929 | 0.085913 | -59.5825 | 61.4914 | -61.4456 | -61.4914 | 53.9062 | 6.8665 | 61.5234 | 61.2076 | 61.5143 | -61.4685 | -0.21057 | -0.054932 | 1.6525 | -0.25635 | -7.6401 | -0.23346 | -0.032044 | 1.8631 | 122.7585 | 122.4426 | 115.1413 | 122.7264 | 1.6525 | 122.7493 | 68.1015 | -0.23346 | 122.7264 | 1.6525 | 68.1015 | 115.1413 | 122.7493 | -122.9919 | -123.0148
1715.3281 | 123.0835 | -61.2213 | 61.5509 | 0.018768 | 0.022642 | 0.0099612 | 0.016846 | 0.055198 | -0.0012839 | 0.08634 | -59.5779 | 61.4731 | -61.441 | -61.4548 | 53.92 | 6.8481 | 61.4868 | 61.4594 | 61.4868 | -61.4685 | -0.21973 | -0.07782 | 1.6434 | -0.23346 | -7.6309 | -0.24719 | -0.064087 | 1.8631 | 122.7081 | 122.6807 | 115.1413 | 122.6944 | 1.6434 | 122.7081 | 68.0695 | -0.24719 | 122.6944 | 1.6434 | 68.0695 | 115.1413 | 122.7081 | -122.9919 | -123.0194
1716.3281 | 123.1064 | -61.2442 | 61.5555 | -0.019379 | 0.019224 | 0.006116 | 0.021119 | 0.053275 | -0.0017111 | 0.085486 | -59.5367 | 61.4777 | -61.4273 | -61.4227 | 53.9658 | 6.871 | 61.4822 | 61.5097 | 61.5051 | -61.4502 | -0.1831 | -0.07782 | 1.7075 | -0.17853 | -7.5897 | -0.20599 | -0.050354 | 1.8906 | 122.7264 | 122.7539 | 115.21 | 122.7219 | 1.7075 | 122.7493 | 68.1152 | -0.20599 | 122.7219 | 1.7075 | 68.1152 | 115.21 | 122.7493 | -122.9828 | -123.0057
1717.3281 | 123.1064 | -61.2305 | 61.5509 | -0.034637 | 0.020933 | 0.0084658 | 0.017274 | 0.05648 | -0.00042929 | 0.084204 | -59.5642 | 61.4868 | -61.4365 | -61.4182 | 53.9566 | 6.9489 | 61.4868 | 61.5509 | 61.5051 | -61.4273 | -0.20599 | -0.064087 | 1.6663 | -0.18768 | -7.5943 | -0.19684 | -0.045776 | 1.8723 | 122.7173 | 122.7814 | 115.1871 | 122.7173 | 1.6663 | 122.7356 | 68.1793 | -0.19684 | 122.7173 | 1.6663 | 68.1793 | 115.1871 | 122.7356 | -122.9874 | -122.9782
1718.3281 | 123.0835 | -61.2625 | 61.5463 | 0.0035097 | 0.019438 | 0.0076114 | 0.018342 | 0.055198 | -0.0019247 | 0.087408 | -59.5596 | 61.4822 | -61.4685 | -61.4456 | 53.92 | 6.8436 | 61.4914 | 61.528 | 61.496 | -61.4639 | -0.20599 | -0.064087 | 1.7029 | -0.18311 | -7.6263 | -0.20142 | -0.050354 | 1.9089 | 122.7539 | 122.7905 | 115.1825 | 122.7448 | 1.7029 | 122.7585 | 68.1061 | -0.20142 | 122.7448 | 1.7029 | 68.1061 | 115.1825 | 122.7585 | -123.0148 | -123.0103
1719.3438 | 123.0103 | -61.2579 | 61.615 | -0.33218 | 0.023496 | 0.012311 | 0.022401 | 0.055839 | -0.0027793 | 0.083777 | -59.5825 | 61.5738 | -61.4273 | -61.4731 | 53.8742 | 6.7612 | 61.6608 | 61.4594 | 61.5601 | -61.5005 | -0.16937 | -0.041198 | 1.6754 | -0.21515 | -7.7408 | -0.24261 | -0.054931 | 1.8448 | 122.9187 | 122.7173 | 115.1321 | 122.8317 | 1.6754 | 122.818 | 68.0191 | -0.24261 | 122.8317 | 1.6754 | 68.0191 | 115.1321 | 122.818 | -123.0423 | -123.1155
1720.3281 | 123.1018 | -61.2671 | 61.5555 | 0.049286 | 0.019865 | 0.0056888 | 0.017701 | 0.056266 | -0.0027793 | 0.086554 | -59.5779 | 61.5097 | -61.4319 | -61.4456 | 53.8925 | 6.9077 | 61.5097 | 61.5234 | 61.5189 | -61.3998 | -0.16479 | -0.045776 | 1.6891 | -0.17853 | -7.663 | -0.13275 | -0.036621 | 1.8539 | 122.7768 | 122.7905 | 115.1596 | 122.7768 | 1.6891 | 122.7859 | 68.1747 | -0.13275 | 122.7768 | 1.6891 | 68.1747 | 115.1596 | 122.7859 | -122.9874 | -122.9553
1721.3281 | 123.0515 | -61.2579 | 61.5646 | 0.16373 | 0.019224 | 0.0086796 | 0.019623 | 0.054771 | -0.0012839 | 0.083136 | -59.5871 | 61.496 | -61.441 | -61.4639 | 53.9017 | 6.8573 | 61.5097 | 61.4822 | 61.5005 | -61.4548 | -0.1831 | -0.068664 | 1.6708 | -0.20599 | -7.663 | -0.19684 | -0.064087 | 1.8539 | 122.7676 | 122.7402 | 115.1596 | 122.7539 | 1.6708 | 122.7585 | 68.1152 | -0.19684 | 122.7539 | 1.6708 | 68.1152 | 115.1596 | 122.7585 | -123.0057 | -123.0194
1722.3281 | 123.0789 | -61.2488 | 61.5372 | -0.088043 | 0.020719 | 0.011243 | 0.01706 | 0.056693 | -0.0019247 | 0.084204 | -59.6512 | 61.4777 | -61.441 | -61.4685 | 53.8834 | 6.9214 | 61.5189 | 61.4868 | 61.496 | -61.4502 | -0.19226 | -0.059509 | 1.5976 | -0.21973 | -7.6538 | -0.20142 | -0.041198 | 1.7899 | 122.7676 | 122.7356 | 115.1321 | 122.7264 | 1.5976 | 122.7448 | 68.1702 | -0.20142 | 122.7264 | 1.5976 | 68.1702 | 115.1321 | 122.7448 | -122.9782 | -122.9874
1723.3281 | 123.0835 | -61.235 | 61.5692 | 0.018768 | 0.019651 | 0.012097 | 0.018342 | 0.055198 | 0.0014933 | 0.087195 | -59.5871 | 61.496 | -61.4227 | -61.4548 | 53.9291 | 6.9397 | 61.5051 | 61.5326 | 61.5097 | -61.4639 | -0.18768 | -0.073242 | 1.6479 | -0.21973 | -7.6401 | -0.22888 | -0.059509 | 1.8356 | 122.7402 | 122.7676 | 115.1642 | 122.731 | 1.6479 | 122.7448 | 68.1747 | -0.22888 | 122.731 | 1.6479 | 68.1747 | 115.1642 | 122.7448 | -122.9919 | -123.0331
1724.3281 | 123.0652 | -61.2259 | 61.5601 | 0.056915 | 0.018583 | 0.011884 | 0.017274 | 0.055412 | -0.0023519 | 0.084845 | -59.6008 | 61.5005 | -61.441 | -61.4319 | 53.9291 | 6.8985 | 61.496 | 61.5417 | 61.5097 | -61.4273 | -0.21515 | -0.05951 | 1.6251 | -0.20599 | -7.6309 | -0.20142 | -0.050354 | 1.8402 | 122.7219 | 122.7676 | 115.155 | 122.7264 | 1.6251 | 122.7356 | 68.1244 | -0.20142 | 122.7264 | 1.6251 | 68.1244 | 115.155 | 122.7356 | -123.0011 | -122.9874
1725.3281 | 123.0515 | -61.2488 | 61.5555 | 0.087433 | 0.02136 | 0.011243 | 0.019623 | 0.055839 | 0.00021151 | 0.085913 | -59.6008 | 61.4868 | -61.441 | -61.4594 | 53.8971 | 6.8298 | 61.528 | 61.5097 | 61.4914 | -61.4594 | -0.19226 | -0.068665 | 1.6479 | -0.21057 | -7.6584 | -0.21057 | -0.064087 | 1.8402 | 122.7768 | 122.7585 | 115.1459 | 122.7356 | 1.6479 | 122.7402 | 68.0786 | -0.21057 | 122.7356 | 1.6479 | 68.0786 | 115.1459 | 122.7402 | -122.9965 | -123.0148
1726.3594 | 123.0057 | -61.2625 | 61.5875 | -0.14908 | 0.024137 | 0.006757 | 0.022828 | 0.057548 | -0.0019247 | 0.084417 | -59.5688 | 61.615 | -61.441 | -61.4731 | 53.8605 | 6.871 | 61.647 | 61.4822 | 61.5372 | -61.5097 | -0.17853 | 0.027466 | 1.6937 | -0.21057 | -7.727 | -0.24719 | -0.050354 | 1.8723 | 122.9095 | 122.7448 | 115.123 | 122.8775 | 1.6937 | 122.7997 | 68.1335 | -0.24719 | 122.8775 | 1.6937 | 68.1335 | 115.123 | 122.7997 | -123.0286 | -123.0972
1727.3281 | 123.1064 | -61.2305 | 61.5189 | -0.14908 | 0.020292 | 0.012311 | 0.015992 | 0.057334 | -0.00042929 | 0.083563 | -59.5184 | 61.4731 | -61.441 | -61.2167 | 53.6728 | 6.7932 | 61.377 | 61.5463 | 61.4822 | -61.4502 | -0.21057 | -0.045777 | 1.712 | 0.013733 | -7.8461 | -0.21973 | -0.036621 | 1.9226 | 122.6074 | 122.7768 | 114.9033 | 122.7036 | 1.712 | 122.7127 | 68.0237 | -0.21973 | 122.7036 | 1.712 | 68.0237 | 114.9033 | 122.7127 | -122.9599 | -122.9691
1728.3281 | 123.0743 | -61.2671 | 61.5143 | 0.17136 | 0.020078 | 0.01167 | 0.020051 | 0.056907 | -0.00085669 | 0.084204 | -59.5779 | 61.4502 | -61.4731 | -61.4685 | 53.8971 | 6.958 | 61.4273 | 61.528 | 61.4822 | -61.4502 | -0.20599 | -0.064087 | 1.6891 | -0.20142 | -7.6172 | -0.1831 | -0.032043 | 1.8951 | 122.6944 | 122.7951 | 115.1642 | 122.7173 | 1.6891 | 122.7493 | 68.2251 | -0.1831 | 122.7173 | 1.6891 | 68.2251 | 115.1642 | 122.7493 | -122.9874 | -122.9645
1729.3438 | 123.0927 | -61.2534 | 61.5509 | 0.056915 | 0.020933 | 0.011243 | 0.017701 | 0.054984 | -0.0010703 | 0.085913 | -59.5963 | 61.5097 | -61.4502 | -61.4685 | 53.9154 | 6.9992 | 61.5005 | 61.5463 | 61.4822 | -61.4731 | -0.19684 | -0.041198 | 1.6571 | -0.21515 | -7.6355 | -0.21973 | -0.068664 | 1.8539 | 122.7539 | 122.7997 | 115.1688 | 122.7631 | 1.6571 | 122.7356 | 68.2526 | -0.21973 | 122.7631 | 1.6571 | 68.2526 | 115.1688 | 122.7356 | -123.0011 | -123.024
1730.3281 | 123.0515 | -61.2534 | 61.5372 | 0.14847 | 0.021787 | 0.010602 | 0.020692 | 0.055625 | -0.00085669 | 0.085486 | -59.5688 | 61.4868 | -61.4502 | -61.4777 | 53.8788 | 7.0175 | 61.5051 | 61.5234 | 61.5143 | -61.4548 | -0.19684 | -0.050354 | 1.6846 | -0.2243 | -7.6584 | -0.20142 | -0.022888 | 1.8814 | 122.7585 | 122.7768 | 115.1321 | 122.7402 | 1.6846 | 122.7676 | 68.2709 | -0.20142 | 122.7402 | 1.6846 | 68.2709 | 115.1321 | 122.7676 | -122.9874 | -122.9919
1731.3438 | 123.0515 | -61.2762 | 61.5509 | -0.14908 | 0.022215 | 0.012738 | 0.025819 | 0.056266 | -0.0012839 | 0.087408 | -59.5413 | 61.5967 | -61.4456 | -61.4548 | 53.8834 | 6.9626 | 61.6104 | 61.5234 | 61.5372 | -61.4914 | -0.16937 | 0.045777 | 1.7349 | -0.17853 | -7.6675 | -0.21515 | -0.013733 | 1.9043 | 122.8867 | 122.7997 | 115.1596 | 122.8729 | 1.7349 | 122.8134 | 68.2388 | -0.21515 | 122.8729 | 1.7349 | 68.2388 | 115.1596 | 122.8134 | -122.9965 | -123.0423
1732.3281 | 123.0835 | -61.2534 | 61.5372 | 0.14847 | 0.01901 | 0.013379 | 0.01941 | 0.057548 | -0.0017111 | 0.084204 | -59.5642 | 61.4868 | -61.441 | -61.4685 | 53.8971 | 6.9992 | 61.5005 | 61.5326 | 61.5189 | -61.4502 | -0.18768 | -0.050354 | 1.6891 | -0.21515 | -7.6401 | -0.19684 | -0.01831 | 1.8768 | 122.7539 | 122.7859 | 115.1505 | 122.7402 | 1.6891 | 122.7722 | 68.2526 | -0.19684 | 122.7402 | 1.6891 | 68.2526 | 115.1505 | 122.7722 | -122.9782 | -122.9874
1733.3281 | 123.0698 | -61.2579 | 61.5463 | 0.14084 | 0.01901 | 0.010602 | 0.018983 | 0.056266 | -0.0036337 | 0.087408 | -59.4681 | 61.5234 | -61.441 | -61.496 | 53.9154 | 7.0038 | 61.4731 | 61.5326 | 61.4822 | -61.4685 | -0.1831 | -0.022889 | 1.7899 | -0.23804 | -7.6309 | -0.21057 | -0.064087 | 1.973 | 122.731 | 122.7905 | 115.1733 | 122.7814 | 1.7899 | 122.7402 | 68.2617 | -0.21057 | 122.7814 | 1.7899 | 68.2617 | 115.1733 | 122.7402 | -122.9874 | -123.0148
1734.3281 | 123.0652 | -61.2396 | 61.528 | 0.19424 | 0.021574 | 0.0099612 | 0.020264 | 0.053703 | -0.0019247 | 0.085058 | -59.5688 | 61.5143 | -61.4273 | -61.4594 | 53.9246 | 6.9901 | 61.4731 | 61.5463 | 61.4822 | -61.4639 | -0.18768 | -0.013733 | 1.6708 | -0.21973 | -7.6035 | -0.2243 | -0.045776 | 1.8585 | 122.7127 | 122.7859 | 115.1642 | 122.7539 | 1.6708 | 122.7219 | 68.2297 | -0.2243 | 122.7539 | 1.6708 | 68.2297 | 115.1642 | 122.7219 | -122.9553 | -122.9919
1735.3281 | 123.111 | -61.2259 | 61.5234 | 0.22476 | 0.021787 | 0.014875 | 0.021546 | 0.057121 | -0.0017111 | 0.085486 | -59.523 | 61.5143 | -61.4365 | -61.3998 | 53.9154 | 6.9946 | 61.4136 | 61.5692 | 61.4685 | -61.4868 | -0.21057 | -0.009155 | 1.7029 | -0.17395 | -7.608 | -0.26093 | -0.054931 | 1.9135 | 122.6395 | 122.7951 | 115.1413 | 122.7402 | 1.7029 | 122.6944 | 68.2205 | -0.26093 | 122.7402 | 1.7029 | 68.2205 | 115.1413 | 122.6944 | -122.9599 | -123.0103
1736.3438 | 123.0377 | -61.2534 | 61.5921 | -0.21011 | 0.020506 | 0.0052616 | 0.020905 | 0.055412 | -0.0023519 | 0.085913 | -59.523 | 61.5692 | -61.4227 | -61.409 | 53.9383 | 6.9534 | 61.6287 | 61.5875 | 61.5326 | -61.4914 | -0.16937 | -0.022888 | 1.7303 | -0.15564 | -7.6538 | -0.23804 | -0.059509 | 1.8997 | 122.8821 | 122.8409 | 115.1917 | 122.8226 | 1.7303 | 122.7859 | 68.2068 | -0.23804 | 122.8226 | 1.7303 | 68.2068 | 115.1917 | 122.7859 | -123.0148 | -123.0835
1737.3438 | 123.0927 | -61.235 | 61.5692 | -0.019379 | 0.020506 | 0.009534 | 0.018128 | 0.055625 | -0.0023519 | 0.086767 | -59.5688 | 61.5097 | -61.441 | -61.4319 | 53.9566 | 7.0267 | 61.5097 | 61.6013 | 61.4868 | -61.4227 | -0.20599 | -0.059509 | 1.6663 | -0.19684 | -7.6126 | -0.18768 | -0.082398 | 1.8723 | 122.7448 | 122.8363 | 115.1916 | 122.7448 | 1.6663 | 122.7219 | 68.2617 | -0.18768 | 122.7448 | 1.6663 | 68.2617 | 115.1916 | 122.7219 | -123.0103 | -122.9919
1738.3281 | 123.0606 | -61.2442 | 61.5784 | 0.2095 | 0.01901 | 0.007825 | 0.020264 | 0.056053 | -0.0038473 | 0.086981 | -59.5596 | 61.5189 | -61.4456 | -61.4365 | 53.9154 | 6.9214 | 61.4914 | 61.5555 | 61.496 | -61.4731 | -0.20142 | -0.059509 | 1.6846 | -0.19226 | -7.663 | -0.22888 | -0.082397 | 1.886 | 122.7356 | 122.7997 | 115.1596 | 122.7631 | 1.6846 | 122.7402 | 68.1656 | -0.22888 | 122.7631 | 1.6846 | 68.1656 | 115.1596 | 122.7402 | -123.024 | -123.0515
1739.3281 | 123.0927 | -61.2442 | 61.5829 | 0.11032 | 0.021147 | 0.014234 | 0.017274 | 0.054557 | -0.0029929 | 0.085486 | -59.5734 | 61.528 | -61.441 | -61.3266 | 54.0573 | 7.0084 | 61.4639 | 61.5005 | 61.5097 | -61.441 | -0.19684 | -0.054932 | 1.6708 | -0.082397 | -7.5256 | -0.19684 | -0.073242 | 1.8677 | 122.7081 | 122.7448 | 115.3015 | 122.7722 | 1.6708 | 122.7539 | 68.2526 | -0.19684 | 122.7722 | 1.6708 | 68.2526 | 115.3015 | 122.7539 | -123.024 | -123.024
1740.3281 | 123.0972 | -61.2305 | 61.5509 | 0.19424 | 0.024992 | 0.01637 | 0.022828 | 0.056266 | -0.0021383 | 0.087622 | -59.5505 | 61.5097 | -61.4227 | -61.4273 | 53.9337 | 7.045 | 61.4639 | 61.5921 | 61.5189 | -61.4456 | -0.19226 | -0.041198 | 1.68 | -0.19684 | -7.6172 | -0.21515 | -0.032043 | 1.8723 | 122.6944 | 122.8226 | 115.1642 | 122.7402 | 1.68 | 122.7493 | 68.2755 | -0.21515 | 122.7402 | 1.68 | 68.2755 | 115.1642 | 122.7493 | -122.9736 | -122.9965
1741.3438 | 122.9645 | -61.2396 | 61.6196 | -0.42374 | 0.022428 | 0.0097476 | 0.020264 | 0.054771 | -0.0014975 | 0.083563 | -59.6146 | 61.5967 | -61.409 | -61.4685 | 53.9062 | 6.9901 | 61.9308 | 61.7203 | 61.6058 | -61.4502 | -0.16937 | -0.022888 | 1.6251 | -0.22888 | -7.7133 | -0.21057 | -0.013733 | 1.7944 | 123.1705 | 122.9599 | 115.1459 | 122.8363 | 1.6251 | 122.8455 | 68.2297 | -0.21057 | 122.8363 | 1.6251 | 68.2297 | 115.1459 | 122.8455 | -123.0286 | -123.0698
1742.3281 | 123.111 | -61.2396 | 61.5509 | 0.18662 | 0.021574 | 0.012097 | 0.020051 | 0.056907 | -0.0014975 | 0.085699 | -59.5459 | 61.5097 | -61.4502 | -61.3953 | 53.9612 | 7.0587 | 61.4319 | 61.5692 | 61.4868 | -61.441 | -0.21057 | -0.041198 | 1.6937 | -0.15564 | -7.5897 | -0.20142 | -0.064087 | 1.9043 | 122.6715 | 122.8088 | 115.2008 | 122.7493 | 1.6937 | 122.7264 | 68.2983 | -0.20142 | 122.7493 | 1.6937 | 68.2983 | 115.2008 | 122.7264 | -123.0011 | -122.9919
1743.3281 | 123.0789 | -61.2305 | 61.5509 | 0.16373 | 0.020719 | 0.010602 | 0.016419 | 0.05648 | -0.0017111 | 0.08634 | -59.6054 | 61.5234 | -61.4182 | -61.4639 | 53.9062 | 6.9077 | 61.8027 | 61.5417 | 61.5463 | -61.4502 | -0.18768 | -0.027466 | 1.6251 | -0.23346 | -7.6447 | -0.21973 | -0.004577 | 1.8127 | 123.0331 | 122.7722 | 115.1367 | 122.7539 | 1.6251 | 122.7768 | 68.1381 | -0.21973 | 122.7539 | 1.6251 | 68.1381 | 115.1367 | 122.7768 | -122.9691 | -123.0011
1744.3281 | 123.0515 | -61.2259 | 61.5692 | 0.13321 | 0.019865 | 0.0069706 | 0.020051 | 0.055839 | -0.0012839 | 0.085486 | -59.5963 | 61.5051 | -61.441 | -61.4822 | 53.9108 | 6.9946 | 61.5051 | 61.5463 | 61.496 | -61.4777 | -0.21515 | -0.064087 | 1.6296 | -0.25635 | -7.6584 | -0.25177 | -0.073242 | 1.8448 | 122.731 | 122.7722 | 115.1367 | 122.731 | 1.6296 | 122.7219 | 68.2205 | -0.25177 | 122.731 | 1.6296 | 68.2205 | 115.1367 | 122.7219 | -123.0103 | -123.0469
1745.3281 | 123.111 | -61.2213 | 61.5051 | 0.16373 | 0.020933 | 0.0097476 | 0.022187 | 0.059257 | -0.0012839 | 0.086767 | -59.5047 | 61.4868 | -61.4136 | -61.4319 | 53.9246 | 7.0267 | 61.4273 | 61.5601 | 61.4914 | -61.4685 | -0.19226 | -0.018311 | 1.7166 | -0.21057 | -7.5806 | -0.24719 | -0.013733 | 1.9089 | 122.6486 | 122.7814 | 115.1459 | 122.7081 | 1.7166 | 122.7127 | 68.248 | -0.24719 | 122.7081 | 1.7166 | 68.248 | 115.1459 | 122.7127 | -122.9187 | -122.9736
1746.3438 | 123.0743 | -61.2625 | 61.528 | 0.24002 | 0.024137 | 0.013379 | 0.024323 | 0.057334 | -0.0025657 | 0.083777 | -59.5963 | 61.5417 | -61.4639 | -61.4639 | 53.8696 | 6.9901 | 61.4731 | 61.528 | 61.5097 | -61.496 | -0.20142 | 0.013733 | 1.6663 | -0.20142 | -7.6584 | -0.23346 | -0.01831 | 1.8677 | 122.7356 | 122.7905 | 115.1321 | 122.8043 | 1.6663 | 122.7722 | 68.2526 | -0.23346 | 122.8043 | 1.6663 | 68.2526 | 115.1321 | 122.7722 | -122.9919 | -123.024
1747.3281 | 123.1155 | -61.2442 | 61.5509 | 0.36209 | 0.020719 | 0.0099612 | 0.021546 | 0.058189 | -0.0021383 | 0.08634 | -59.5139 | 61.5143 | -61.4227 | -61.4182 | 53.9337 | 7.1136 | 61.4044 | 61.6104 | 61.4868 | -61.4731 | -0.17853 | -0.036621 | 1.7303 | -0.17395 | -7.6172 | -0.22888 | -0.064087 | 1.9089 | 122.6486 | 122.8546 | 115.1779 | 122.7585 | 1.7303 | 122.731 | 68.3578 | -0.22888 | 122.7585 | 1.7303 | 68.3578 | 115.1779 | 122.731 | -122.9736 | -123.024
1748.3281 | 123.1018 | -61.2442 | 61.528 | 0.21713 | 0.02136 | 0.013806 | 0.020905 | 0.060966 | -0.0017111 | 0.085272 | -59.5871 | 61.5463 | -61.4685 | -61.4548 | 53.8925 | 7.1228 | 61.4685 | 61.5646 | 61.5005 | -61.4685 | -0.2243 | 0.018311 | 1.6571 | -0.21057 | -7.6355 | -0.2243 | -0.027466 | 1.8814 | 122.7127 | 122.8088 | 115.1367 | 122.7905 | 1.6571 | 122.7448 | 68.367 | -0.2243 | 122.7905 | 1.6571 | 68.367 | 115.1367 | 122.7448 | -122.9965 | -122.9965
1749.3281 | 123.1247 | -61.2213 | 61.5646 | 0.26291 | 0.023496 | 0.014875 | 0.023682 | 0.059471 | -0.0047019 | 0.086981 | -59.5367 | 61.528 | -61.4594 | -61.6287 | 53.92 | 7.1686 | 61.5234 | 61.5967 | 61.4914 | -61.4319 | -0.23804 | -0.036621 | 1.6846 | -0.40741 | -7.6447 | -0.21057 | -0.073242 | 1.9226 | 122.7448 | 122.818 | 115.1413 | 122.7493 | 1.6846 | 122.7127 | 68.3899 | -0.21057 | 122.7493 | 1.6846 | 68.3899 | 115.1413 | 122.7127 | -123.024 | -122.9965
1750.3281 | 123.1018 | -61.2259 | 61.5417 | 0.21713 | 0.022856 | 0.009534 | 0.022187 | 0.058616 | -0.00064309 | 0.085913 | -59.5367 | 61.5189 | -61.409 | -61.4136 | 53.9566 | 7.1457 | 61.4319 | 61.6287 | 61.5097 | -61.4502 | -0.18311 | -0.022888 | 1.6891 | -0.18768 | -7.5851 | -0.2243 | -0.032043 | 1.8723 | 122.6578 | 122.8546 | 115.1825 | 122.7448 | 1.6891 | 122.7356 | 68.3716 | -0.2243 | 122.7448 | 1.6891 | 68.3716 | 115.1825 | 122.7356 | -122.9507 | -122.9919
1751.3281 | 123.0789 | -61.2305 | 61.5463 | 0.16373 | 0.020933 | 0.012525 | 0.020905 | 0.057548 | -0.0019247 | 0.085272 | -59.5642 | 61.5005 | -61.4227 | -61.4548 | 53.8971 | 7.0908 | 61.4548 | 61.5829 | 61.4868 | -61.4777 | -0.19226 | -0.045777 | 1.6663 | -0.2243 | -7.6492 | -0.24719 | -0.05951 | 1.8585 | 122.6852 | 122.8134 | 115.1276 | 122.731 | 1.6663 | 122.7173 | 68.3212 | -0.24719 | 122.731 | 1.6663 | 68.3212 | 115.1276 | 122.7173 | -122.9691 | -123.024
1752.3438 | 123.1338 | -61.2396 | 61.528 | 0.1561 | 0.022642 | 0.011029 | 0.022614 | 0.058402 | -0.0040609 | 0.08634 | -59.523 | 61.5326 | -61.4319 | -61.4273 | 53.9108 | 7.0084 | 61.4456 | 61.5784 | 61.5051 | -61.4822 | -0.19226 | 0.004578 | 1.7166 | -0.18768 | -7.6172 | -0.24262 | -0.022888 | 1.9089 | 122.6852 | 122.818 | 115.1505 | 122.7722 | 1.7166 | 122.7448 | 68.248 | -0.24262 | 122.7722 | 1.7166 | 68.248 | 115.1505 | 122.7448 | -122.9599 | -123.0103
1753.3281 | 123.1201 | -61.2259 | 61.5417 | 0.20187 | 0.023069 | 0.013593 | 0.021332 | 0.057334 | -0.0027793 | 0.086126 | -59.5184 | 61.5189 | -61.4227 | -61.4502 | 53.9658 | 7.0999 | 61.3998 | 61.615 | 61.4914 | -61.4548 | -0.19684 | -0.022888 | 1.7075 | -0.2243 | -7.576 | -0.22888 | -0.050354 | 1.9043 | 122.6257 | 122.8409 | 115.1916 | 122.7448 | 1.7075 | 122.7173 | 68.3258 | -0.22888 | 122.7448 | 1.7075 | 68.3258 | 115.1916 | 122.7173 | -122.9645 | -122.9965
1754.3594 | 123.1018 | -61.2305 | 61.5143 | 0.16373 | 0.021787 | 0.010388 | 0.021119 | 0.060325 | -0.0032065 | 0.085913 | -59.5505 | 61.5051 | -61.4456 | -61.4456 | 53.9154 | 7.0541 | 61.441 | 61.6058 | 61.528 | -61.4639 | -0.21515 | -0.009155 | 1.68 | -0.21515 | -7.5989 | -0.23346 | 0.013733 | 1.8951 | 122.6715 | 122.8363 | 115.1459 | 122.7356 | 1.68 | 122.7585 | 68.2846 | -0.23346 | 122.7356 | 1.68 | 68.2846 | 115.1459 | 122.7585 | -122.9599 | -122.9782
1755.3281 | 123.0377 | -61.2625 | 61.5646 | 0.20187 | 0.024137 | 0.010816 | 0.022401 | 0.056693 | -0.0019247 | 0.084417 | -59.5963 | 61.5875 | -61.4639 | -61.496 | 53.8467 | 6.9901 | 61.5463 | 61.5234 | 61.5234 | -61.5097 | -0.20142 | 0.022888 | 1.6663 | -0.23346 | -7.7179 | -0.24719 | -0.041199 | 1.8677 | 122.8088 | 122.7859 | 115.1093 | 122.85 | 1.6663 | 122.7859 | 68.2526 | -0.24719 | 122.85 | 1.6663 | 68.2526 | 115.1093 | 122.7859 | -123.0286 | -123.0743
1756.3594 | 123.0789 | -61.2259 | 61.5417 | 0.16373 | 0.019438 | 0.012952 | 0.017274 | 0.058189 | -0.0032065 | 0.087408 | -59.5413 | 61.5143 | -61.4319 | -61.4731 | 53.8834 | 7.0541 | 61.4868 | 61.5921 | 61.5005 | -61.441 | -0.20599 | -0.027466 | 1.6846 | -0.24719 | -7.6584 | -0.21515 | -0.041199 | 1.8906 | 122.7127 | 122.818 | 115.1093 | 122.7402 | 1.6846 | 122.7264 | 68.28 | -0.21515 | 122.7402 | 1.6846 | 68.28 | 115.1093 | 122.7264 | -122.9736 | -122.9828
1757.3281 | 123.0835 | -61.2167 | 61.5509 | 0.056915 | 0.02136 | 0.010816 | 0.020478 | 0.060752 | -0.0025657 | 0.083777 | -59.4086 | 61.5234 | -61.4365 | -61.3998 | 53.9154 | 7.0541 | 61.4365 | 61.6196 | 61.5005 | -61.4456 | -0.21973 | -0.027466 | 1.8082 | -0.18311 | -7.6355 | -0.22888 | -0.050354 | 2.0279 | 122.6532 | 122.8363 | 115.1321 | 122.7402 | 1.8082 | 122.7173 | 68.2709 | -0.22888 | 122.7402 | 1.8082 | 68.2709 | 115.1321 | 122.7173 | -122.9874 | -122.9965
1758.3438 | 123.0148 | -61.2579 | 61.5601 | 0.018768 | 0.024351 | 0.015943 | 0.024537 | 0.060752 | -0.0029929 | 0.08634 | -59.523 | 61.6058 | -61.441 | -61.4502 | 53.8834 | 6.9717 | 61.6058 | 61.5738 | 61.5784 | -61.5005 | -0.1831 | 0.045776 | 1.7349 | -0.19226 | -7.6767 | -0.24261 | 0.01831 | 1.918 | 122.8638 | 122.8317 | 115.1413 | 122.8638 | 1.7349 | 122.8363 | 68.2297 | -0.24261 | 122.8638 | 1.7349 | 68.2297 | 115.1413 | 122.8363 | -123.0011 | -123.0606
1759.3281 | 123.1384 | -61.2442 | 61.5555 | 0.2095 | 0.019865 | 0.0080386 | 0.020051 | 0.059471 | -0.0014975 | 0.087195 | -59.5322 | 61.5463 | -61.4456 | -61.4273 | 53.9108 | 6.9946 | 61.4319 | 61.6241 | 61.528 | -61.4502 | -0.20142 | -0.009155 | 1.712 | -0.1831 | -7.6447 | -0.20599 | -0.027466 | 1.9135 | 122.6761 | 122.8683 | 115.155 | 122.7905 | 1.712 | 122.7722 | 68.2388 | -0.20599 | 122.7905 | 1.712 | 68.2388 | 115.155 | 122.7722 | -123.0011 | -123.0057
1760.3281 | 123.111 | -61.2259 | 61.5509 | 0.22476 | 0.024565 | 0.0097476 | 0.023682 | 0.060325 | -0.00064309 | 0.086981 | -59.5505 | 61.5509 | -61.4319 | -61.4273 | 53.9246 | 7.0358 | 61.4594 | 61.6058 | 61.5417 | -61.4914 | -0.20599 | 0 | 1.6754 | -0.20142 | -7.6263 | -0.2655 | -0.009155 | 1.8814 | 122.6852 | 122.8317 | 115.1505 | 122.7768 | 1.6754 | 122.7676 | 68.2617 | -0.2655 | 122.7768 | 1.6754 | 68.2617 | 115.1505 | 122.7676 | -122.9828 | -123.0423
1761.3281 | 123.1247 | -61.235 | 61.5326 | 0.25528 | 0.02371 | 0.015515 | 0.021973 | 0.058616 | -0.0017111 | 0.08634 | -59.5871 | 61.5738 | -61.4548 | -61.4319 | 53.8696 | 6.9901 | 61.4502 | 61.5784 | 61.5189 | -61.4822 | -0.21973 | 0.041199 | 1.6479 | -0.19684 | -7.663 | -0.24719 | -0.013733 | 1.8677 | 122.6852 | 122.8134 | 115.1047 | 122.8088 | 1.6479 | 122.7539 | 68.2251 | -0.24719 | 122.8088 | 1.6479 | 68.2251 | 115.1047 | 122.7539 | -122.9874 | -123.0148
1762.3281 | 123.1064 | -61.2442 | 61.5463 | 0.23239 | 0.023924 | 0.010388 | 0.02411 | 0.060111 | -0.00064309 | 0.087622 | -59.5871 | 61.5738 | -61.4594 | -61.4914 | 53.8742 | 6.9717 | 61.4822 | 61.5738 | 61.5234 | -61.5143 | -0.21515 | 0.027466 | 1.6571 | -0.24719 | -7.6721 | -0.27008 | -0.022889 | 1.8723 | 122.7264 | 122.818 | 115.1184 | 122.818 | 1.6571 | 122.7676 | 68.2159 | -0.27008 | 122.818 | 1.6571 | 68.2159 | 115.1184 | 122.7676 | -123.0057 | -123.0606
1763.3281 | 123.0469 | -61.2305 | 61.5555 | 0.21713 | 0.023069 | 0.012525 | 0.021546 | 0.05883 | -0.0012839 | 0.086981 | -59.6146 | 61.6013 | -61.4685 | -61.4868 | 53.833 | 6.9901 | 61.5234 | 61.5692 | 61.5326 | -61.5051 | -0.23804 | 0.045776 | 1.6159 | -0.25635 | -7.7225 | -0.27466 | -0.022888 | 1.8539 | 122.7539 | 122.7997 | 115.0635 | 122.8317 | 1.6159 | 122.7631 | 68.2205 | -0.27466 | 122.8317 | 1.6159 | 68.2205 | 115.0635 | 122.7631 | -123.024 | -123.0606
1764.3281 | 123.1384 | -61.2579 | 61.5417 | 0.27817 | 0.022001 | 0.010816 | 0.021119 | 0.060111 | -0.00085669 | 0.086554 | -59.523 | 61.5372 | -61.409 | -61.441 | 53.8696 | 7.0724 | 61.4456 | 61.6287 | 61.5189 | -61.4822 | -0.15106 | -0.004578 | 1.7349 | -0.1831 | -7.6721 | -0.2243 | -0.022888 | 1.886 | 122.7036 | 122.8867 | 115.1276 | 122.7951 | 1.7349 | 122.7768 | 68.3304 | -0.2243 | 122.7951 | 1.7349 | 68.3304 | 115.1276 | 122.7768 | -122.9507 | -123.024
1765.3281 | 123.1293 | -61.2305 | 61.528 | 0.18662 | 0.022001 | 0.010388 | 0.020478 | 0.060966 | -0.00042929 | 0.084845 | -59.5413 | 61.5372 | -61.4136 | -61.4319 | 53.8788 | 7.0541 | 61.4182 | 61.6379 | 61.5005 | -61.4731 | -0.1831 | 0.009155 | 1.6891 | -0.20142 | -7.6492 | -0.24261 | -0.027466 | 1.8723 | 122.6486 | 122.8683 | 115.1093 | 122.7676 | 1.6891 | 122.731 | 68.2846 | -0.24261 | 122.7676 | 1.6891 | 68.2846 | 115.1093 | 122.731 | -122.9416 | -123.0011
1766.3281 | 123.1201 | -61.2213 | 61.5372 | 0.22476 | 0.02371 | 0.013379 | 0.022187 | 0.059471 | -0.0017111 | 0.085486 | -59.5779 | 61.5829 | -61.4456 | -61.4548 | 53.8467 | 7.0541 | 61.4548 | 61.6104 | 61.5097 | -61.4914 | -0.22431 | 0.045777 | 1.6434 | -0.23346 | -7.6904 | -0.27008 | -0.027465 | 1.8677 | 122.6761 | 122.8317 | 115.0681 | 122.8043 | 1.6434 | 122.731 | 68.2755 | -0.27008 | 122.8043 | 1.6434 | 68.2755 | 115.0681 | 122.731 | -122.9828 | -123.0286
1767.3281 | 123.1201 | -61.2213 | 61.5555 | -0.78232 | 0.022215 | 0.016797 | 0.01941 | 0.060325 | -0.0012839 | 0.087408 | -59.5734 | 61.5326 | -61.4319 | -61.4227 | 53.8879 | 7.1045 | 61.4456 | 61.6333 | 61.5051 | -61.4548 | -0.21057 | -0.022888 | 1.6479 | -0.20142 | -7.6675 | -0.23346 | -0.050354 | 1.8585 | 122.6669 | 122.8546 | 115.1093 | 122.7539 | 1.6479 | 122.7264 | 68.3258 | -0.23346 | 122.7539 | 1.6479 | 68.3258 | 115.1093 | 122.7264 | -122.9874 | -123.0103
1768.3281 | 123.0606 | -61.2579 | 61.5326 | 0.23239 | 0.023924 | 0.0091068 | 0.021546 | 0.059257 | -0.0027793 | 0.085699 | -59.6146 | 61.5921 | -61.4639 | -61.5005 | 53.8193 | 7.077 | 61.528 | 61.5646 | 61.5372 | -61.5005 | -0.20599 | 0.059509 | 1.6434 | -0.24261 | -7.7133 | -0.24261 | 0.004577 | 1.8494 | 122.786 | 122.8226 | 115.0772 | 122.85 | 1.6434 | 122.7951 | 68.335 | -0.24261 | 122.85 | 1.6434 | 68.335 | 115.0772 | 122.7951 | -122.9965 | -123.0331
1769.3281 | 122.9645 | -61.2762 | 61.6058 | 0.17136 | 0.023069 | 0.0076114 | 0.023255 | 0.059471 | -0.0025657 | 0.085272 | -59.6283 | 61.6013 | -61.4548 | -61.5326 | 53.7506 | 7.0038 | 61.6013 | 61.5051 | 61.5829 | -61.5097 | -0.17853 | -0.004578 | 1.6479 | -0.25635 | -7.8552 | -0.23346 | -0.022888 | 1.8265 | 122.8775 | 122.7814 | 115.0269 | 122.8775 | 1.6479 | 122.8592 | 68.28 | -0.23346 | 122.8775 | 1.6479 | 68.28 | 115.0269 | 122.8592 | -123.0606 | -123.1155
1770.3281 | 123.0423 | -61.2442 | 61.5601 | 0.20187 | 0.024351 | 0.011029 | 0.021332 | 0.059471 | 0.00021151 | 0.086981 | -59.6283 | 61.5875 | -61.496 | -61.5097 | 53.7964 | 6.9901 | 61.5509 | 61.528 | 61.5829 | -61.5051 | -0.25177 | 0.027465 | 1.6159 | -0.2655 | -7.7637 | -0.26093 | 0.022888 | 1.8677 | 122.7951 | 122.7722 | 115.0406 | 122.8317 | 1.6159 | 122.8271 | 68.2343 | -0.26093 | 122.8317 | 1.6159 | 68.2343 | 115.0406 | 122.8271 | -123.056 | -123.0652
1771.3281 | 123.0835 | -61.2488 | 61.5417 | 0.22476 | 0.023496 | 0.0086796 | 0.020051 | 0.060325 | -0.00021569 | 0.082922 | -59.5963 | 61.5463 | -61.4502 | -61.4868 | 53.8101 | 7.1091 | 61.4685 | 61.5967 | 61.5372 | -61.5143 | -0.20142 | 0.004578 | 1.6525 | -0.23804 | -7.7316 | -0.2655 | -0.004578 | 1.8539 | 122.7173 | 122.8455 | 115.0589 | 122.7951 | 1.6525 | 122.7859 | 68.3578 | -0.2655 | 122.7951 | 1.6525 | 68.3578 | 115.0589 | 122.7859 | -122.9919 | -123.056
1772.3281 | 123.1018 | -61.2671 | 61.5326 | 0.24002 | 0.023069 | 0.013806 | 0.022614 | 0.060325 | 0.00063871 | 0.085486 | -59.6146 | 61.5921 | -61.4365 | -61.4868 | 53.8376 | 7.0908 | 61.4914 | 61.5875 | 61.5234 | -61.4914 | -0.16937 | 0.059509 | 1.6525 | -0.21973 | -7.695 | -0.2243 | -0.009156 | 1.8219 | 122.7585 | 122.8546 | 115.1047 | 122.8592 | 1.6525 | 122.7905 | 68.3578 | -0.2243 | 122.8592 | 1.6525 | 68.3578 | 115.1047 | 122.7905 | -122.9691 | -123.024
1773.3281 | 123.1201 | -61.2305 | 61.5509 | 0.25528 | 0.022642 | 0.013806 | 0.017701 | 0.060752 | -0.0019247 | 0.086554 | -59.4131 | 61.5417 | -61.441 | -61.3907 | 53.8834 | 7.1594 | 61.4502 | 61.6425 | 61.5417 | -61.4777 | -0.21057 | -0.009155 | 1.8173 | -0.16022 | -7.6675 | -0.24719 | -0.009155 | 2.0279 | 122.6807 | 122.8729 | 115.1138 | 122.7722 | 1.8173 | 122.7722 | 68.3899 | -0.24719 | 122.7722 | 1.8173 | 68.3899 | 115.1138 | 122.7722 | -122.9919 | -123.0286
1774.3281 | 123.0652 | -61.235 | 61.5692 | 0.21713 | 0.023924 | 0.011457 | 0.023255 | 0.060539 | -0.0027793 | 0.084845 | -59.6008 | 61.6196 | -61.4365 | -61.5005 | 53.7918 | 7.0724 | 61.528 | 61.5555 | 61.5463 | -61.5097 | -0.20142 | 0.050354 | 1.6342 | -0.2655 | -7.7774 | -0.27466 | -0.022888 | 1.8356 | 122.7631 | 122.7905 | 115.0269 | 122.8546 | 1.6342 | 122.7814 | 68.3075 | -0.27466 | 122.8546 | 1.6342 | 68.3075 | 115.0269 | 122.7814 | -123.0057 | -123.0789
1775.3281 | 123.111 | -61.2442 | 61.5143 | 0.19424 | 0.022215 | 0.014661 | 0.020264 | 0.059043 | 0.00021151 | 0.087408 | -59.5413 | 61.5692 | -61.4456 | -61.4273 | 53.8467 | 7.1045 | 61.4548 | 61.6196 | 61.5372 | -61.4777 | -0.20142 | 0.054932 | 1.7029 | -0.1831 | -7.6675 | -0.23346 | 0.022888 | 1.9043 | 122.699 | 122.8638 | 115.0909 | 122.8134 | 1.7029 | 122.7814 | 68.3487 | -0.23346 | 122.8134 | 1.7029 | 68.3487 | 115.0909 | 122.7814 | -122.9599 | -122.9919
1776.3281 | 123.0011 | -61.2717 | 61.5875 | 1.537 | 0.022428 | 0.014661 | 0.02411 | 0.060325 | -0.00021569 | 0.08634 | -59.4269 | 61.6196 | -61.4594 | -61.5143 | 53.7598 | 7.0541 | 61.615 | 61.496 | 61.5967 | -61.528 | -0.18768 | 0.032044 | 1.8448 | -0.24262 | -7.8278 | -0.25635 | 0.009156 | 2.0325 | 122.8867 | 122.7676 | 115.0314 | 122.8912 | 1.8448 | 122.8683 | 68.3258 | -0.25635 | 122.8912 | 1.8448 | 68.3258 | 115.0314 | 122.8683 | -123.0469 | -123.1155
1777.3281 | 123.0515 | -61.2625 | 61.5921 | 0.20187 | 0.023283 | 0.011029 | 0.02176 | 0.059898 | -0.0025657 | 0.086981 | -59.5963 | 61.615 | -61.4594 | -61.5051 | 53.7781 | 7.0404 | 61.5967 | 61.5372 | 61.6287 | -61.4777 | -0.19684 | 0.022888 | 1.6663 | -0.24262 | -7.814 | -0.21515 | 0.036621 | 1.8631 | 122.8592 | 122.7997 | 115.0406 | 122.8775 | 1.6663 | 122.8912 | 68.3029 | -0.21515 | 122.8775 | 1.6663 | 68.3029 | 115.0406 | 122.8912 | -123.0515 | -123.0698
1778.3281 | 123.0789 | -61.2167 | 61.5555 | 0.25528 | 0.023069 | 0.013166 | 0.020264 | 0.059898 | -0.0027793 | 0.087195 | -59.5642 | 61.6013 | -61.441 | -61.4548 | 53.8055 | 7.0129 | 61.5234 | 61.5875 | 61.5738 | -61.4731 | -0.2243 | 0.045776 | 1.6525 | -0.23804 | -7.7499 | -0.25635 | 0.018311 | 1.8768 | 122.7402 | 122.8043 | 115.0223 | 122.818 | 1.6525 | 122.7905 | 68.2297 | -0.25635 | 122.818 | 1.6525 | 68.2297 | 115.0223 | 122.7905 | -122.9965 | -123.0286
1779.3438 | 123.0469 | -61.2259 | 61.5692 | -1.6826 | 0.020933 | 0.011884 | 0.013215 | 0.060325 | -0.0012839 | 0.085913 | -59.6786 | 61.528 | -61.4044 | -61.4777 | 53.7964 | 7.0633 | 61.5601 | 61.6241 | 61.6013 | -61.441 | -0.17853 | -0.041199 | 1.5472 | -0.25177 | -7.7728 | -0.21515 | 0.032043 | 1.7258 | 122.7859 | 122.85 | 115.0223 | 122.7539 | 1.5472 | 122.8271 | 68.2892 | -0.21515 | 122.7539 | 1.5472 | 68.2892 | 115.0223 | 122.8271 | -122.9736 | -123.0103
1780.3281 | 123.0515 | -61.2213 | 61.5921 | 0.23239 | 0.024351 | 0.01167 | 0.021332 | 0.059898 | 0.0010659 | 0.086767 | -59.6008 | 61.6104 | -61.4319 | -61.4731 | 53.7872 | 7.0129 | 61.5463 | 61.5875 | 61.5829 | -61.496 | -0.21057 | 0.018311 | 1.6205 | -0.25177 | -7.8049 | -0.27466 | -0.009155 | 1.8311 | 122.7676 | 122.8088 | 115.0085 | 122.8317 | 1.6205 | 122.8043 | 68.2343 | -0.27466 | 122.8317 | 1.6205 | 68.2343 | 115.0085 | 122.8043 | -123.024 | -123.0881
1781.3281 | 123.1567 | -61.2213 | 61.5601 | 0.16373 | 0.020719 | 0.010816 | 0.01941 | 0.060752 | 0.00021151 | 0.085913 | -59.523 | 61.5784 | -61.4182 | -61.4136 | 53.8284 | 7.1365 | 61.3403 | 61.4227 | 61.4914 | -61.5097 | -0.19684 | 0.01831 | 1.6983 | -0.19226 | -7.7316 | -0.28839 | -0.068665 | 1.8951 | 122.5616 | 122.644 | 115.0497 | 122.7997 | 1.6983 | 122.7127 | 68.3578 | -0.28839 | 122.7997 | 1.6983 | 68.3578 | 115.0497 | 122.7127 | -122.9782 | -123.0698
1782.3281 | 123.0423 | -61.2442 | 61.5692 | 0.24002 | 0.022215 | 0.015729 | 0.022187 | 0.059043 | -0.00042929 | 0.089331 | -59.6054 | 61.5921 | -61.441 | -61.4822 | 53.7872 | 6.9763 | 61.5372 | 61.5601 | 61.5829 | -61.4868 | -0.19684 | 0.022888 | 1.6388 | -0.23804 | -7.782 | -0.24261 | 0.013733 | 1.8356 | 122.7814 | 122.8043 | 115.0314 | 122.8363 | 1.6388 | 122.8271 | 68.2205 | -0.24261 | 122.8363 | 1.6388 | 68.2205 | 115.0314 | 122.8271 | -123.0103 | -123.056
1783.3281 | 123.0972 | -61.2762 | 61.5143 | 0.22476 | 0.022642 | 0.017011 | 0.020264 | 0.060325 | -0.0017111 | 0.086554 | -59.5505 | 61.5555 | -61.4273 | -61.4227 | 53.8696 | 7.2052 | 61.4456 | 61.6196 | 61.5463 | -61.4548 | -0.15106 | 0.041199 | 1.7258 | -0.14648 | -7.6447 | -0.17853 | 0.032044 | 1.8768 | 122.7219 | 122.8958 | 115.1459 | 122.8317 | 1.7258 | 122.8226 | 68.4814 | -0.17853 | 122.8317 | 1.7258 | 68.4814 | 115.1459 | 122.8226 | -122.9416 | -122.9691
1784.3281 | 123.0515 | -61.235 | 61.5601 | 0.25528 | 0.024565 | 0.0099612 | 0.021973 | 0.060111 | -0.0019247 | 0.086554 | -59.61 | 61.5967 | -61.441 | -61.4822 | 53.7827 | 7.0541 | 61.5646 | 61.5601 | 61.5829 | -61.4868 | -0.20599 | 0.036621 | 1.6251 | -0.24719 | -7.7774 | -0.25177 | 0.022888 | 1.8311 | 122.7997 | 122.7951 | 115.0177 | 122.8317 | 1.6251 | 122.818 | 68.2892 | -0.25177 | 122.8317 | 1.6251 | 68.2892 | 115.0177 | 122.818 | -123.0011 | -123.0469
1785.3438 | 123.0835 | -61.235 | 61.5646 | 0.24765 | 0.024351 | 0.018079 | 0.021546 | 0.059898 | -0.00042929 | 0.086126 | -59.5779 | 61.5875 | -61.4319 | -61.4685 | 53.8147 | 7.0541 | 61.5189 | 61.5601 | 61.5738 | -61.4548 | -0.19684 | 0.022888 | 1.6571 | -0.23346 | -7.7499 | -0.21973 | 0.009156 | 1.8539 | 122.7539 | 122.7951 | 115.0497 | 122.8226 | 1.6571 | 122.8088 | 68.2892 | -0.21973 | 122.8226 | 1.6571 | 68.2892 | 115.0497 | 122.8088 | -122.9965 | -123.0194
1786.3281 | 123.1201 | -61.2076 | 61.5509 | 0.3392 | 0.024137 | 0.014875 | 0.02176 | 0.060752 | -0.0019247 | 0.085913 | -59.5322 | 61.5509 | -61.4273 | -61.4273 | 53.8513 | 7.164 | 61.441 | 61.6196 | 61.5601 | -61.4914 | -0.21973 | 0 | 1.6754 | -0.21973 | -7.6996 | -0.28381 | 0.009156 | 1.8951 | 122.6486 | 122.8271 | 115.0589 | 122.7585 | 1.6754 | 122.7676 | 68.3716 | -0.28381 | 122.7585 | 1.6754 | 68.3716 | 115.0589 | 122.7676 | -122.9782 | -123.0423
1787.3281 | 123.0972 | -61.1984 | 61.5372 | 0.29343 | 0.023924 | 0.015302 | 0.020905 | 0.059043 | -0.00085669 | 0.086126 | -59.5459 | 61.5555 | -61.441 | -61.4182 | 53.8284 | 7.1136 | 61.4685 | 61.6196 | 61.5417 | -61.4777 | -0.24262 | 0.018311 | 1.6525 | -0.21973 | -7.7087 | -0.27924 | 0.004578 | 1.8951 | 122.6669 | 122.818 | 115.0269 | 122.7539 | 1.6525 | 122.7402 | 68.3121 | -0.27924 | 122.7539 | 1.6525 | 68.3121 | 115.0269 | 122.7402 | -122.9782 | -123.0148
1788.3281 | 123.1201 | -61.2076 | 61.5646 | 0.17899 | 0.022856 | 0.014447 | 0.020264 | 0.060539 | -0.0019247 | 0.087622 | -59.5551 | 61.5829 | -61.4365 | -61.409 | 53.833 | 7.1503 | 61.4456 | 61.6241 | 61.5646 | -61.4639 | -0.22888 | 0.018311 | 1.6525 | -0.20142 | -7.7316 | -0.25635 | 0 | 1.8814 | 122.6532 | 122.8317 | 115.0406 | 122.7905 | 1.6525 | 122.7722 | 68.3578 | -0.25635 | 122.7905 | 1.6525 | 68.3578 | 115.0406 | 122.7722 | -123.0011 | -123.0286
1789.3281 | 123.111 | -61.2259 | 61.5555 | 0.19424 | 0.022215 | 0.010602 | 0.018128 | 0.057762 | -0.0021383 | 0.086767 | -59.5413 | 61.5143 | -61.4273 | -61.4136 | 53.8513 | 7.164 | 61.441 | 61.6333 | 61.5189 | -61.4639 | -0.20142 | -0.041199 | 1.6846 | -0.18768 | -7.7042 | -0.23804 | -0.036621 | 1.886 | 122.6669 | 122.8592 | 115.0772 | 122.7402 | 1.6846 | 122.7448 | 68.3899 | -0.23804 | 122.7402 | 1.6846 | 68.3899 | 115.0772 | 122.7448 | -122.9828 | -123.0194
1790.3281 | 123.0469 | -61.2671 | 61.5738 | 0.21713 | 0.023283 | 0.012311 | 0.023896 | 0.058189 | -0.00064309 | 0.085699 | -59.6146 | 61.6058 | -61.4365 | -61.496 | 53.7689 | 7.1457 | 61.5692 | 61.5189 | 61.5601 | -61.5234 | -0.16937 | 0.032043 | 1.6525 | -0.22888 | -7.8049 | -0.25635 | -0.013733 | 1.8219 | 122.8363 | 122.7859 | 115.036 | 122.8729 | 1.6525 | 122.8271 | 68.4128 | -0.25635 | 122.8729 | 1.6525 | 68.4128 | 115.036 | 122.8271 | -123.0103 | -123.0972
1791.3438 | 123.0652 | -61.2305 | 61.5601 | 0.19424 | 0.019651 | 0.010816 | 0.015351 | 0.058402 | -0.00042929 | 0.085486 | -59.5551 | 61.5189 | -61.4639 | -61.4273 | 53.8605 | 7.3013 | 61.4777 | 61.615 | 61.5509 | -61.4456 | -0.23346 | -0.041199 | 1.6754 | -0.19684 | -7.6996 | -0.21515 | -0.009156 | 1.9089 | 122.7081 | 122.8455 | 115.0909 | 122.7493 | 1.6754 | 122.7814 | 68.5318 | -0.21515 | 122.7493 | 1.6754 | 68.5318 | 115.0909 | 122.7814 | -123.024 | -123.0057
1792.3281 | 123.1064 | -61.1984 | 61.5509 | 0.13321 | 0.020933 | 0.011457 | 0.021332 | 0.057762 | -0.0019247 | 0.083563 | -59.5276 | 61.5692 | -61.4044 | -61.4182 | 53.8788 | 7.2189 | 61.4685 | 61.647 | 61.5463 | -61.4502 | -0.20599 | 0.018311 | 1.6708 | -0.21973 | -7.6721 | -0.25177 | -0.004577 | 1.8768 | 122.6669 | 122.8455 | 115.0772 | 122.7676 | 1.6708 | 122.7448 | 68.4174 | -0.25177 | 122.7676 | 1.6708 | 68.4174 | 115.0772 | 122.7448 | -122.9553 | -123.0011
1793.3281 | 123.1018 | -61.2167 | 61.5738 | -0.59921 | 0.020719 | 0.014875 | 0.020051 | 0.059684 | -0.0017111 | 0.084845 | -59.4223 | 61.5417 | -61.4044 | -61.4182 | 53.8742 | 7.2235 | 61.4456 | 61.6562 | 61.528 | -61.4594 | -0.18768 | -0.032044 | 1.7944 | -0.20142 | -7.6996 | -0.24262 | -0.045777 | 1.9821 | 122.6624 | 122.8729 | 115.0909 | 122.7585 | 1.7944 | 122.7448 | 68.4402 | -0.24262 | 122.7585 | 1.7944 | 68.4402 | 115.0909 | 122.7448 | -122.9782 | -123.0331
1794.3281 | 123.1201 | -61.1984 | 61.5601 | 0.19424 | 0.023069 | 0.010816 | 0.022187 | 0.060325 | -0.00021569 | 0.085699 | -59.7336 | 61.528 | -61.441 | -61.3815 | 53.8376 | 7.2006 | 61.4548 | 61.6425 | 61.5463 | -61.4502 | -0.24262 | -0.032044 | 1.4648 | -0.18311 | -7.7225 | -0.25177 | -0.013733 | 1.7075 | 122.6532 | 122.8409 | 115.036 | 122.7264 | 1.4648 | 122.7448 | 68.399 | -0.25177 | 122.7264 | 1.4648 | 68.399 | 115.036 | 122.7448 | -123.0011 | -123.0103
1795.3281 | 123.1293 | -61.1893 | 61.5692 | 0.2095 | 0.02136 | 0.013806 | 0.026246 | 0.059257 | -0.0036337 | 0.084845 | -59.5367 | 61.5372 | -61.4136 | -61.3037 | 53.8742 | 7.1548 | 61.5005 | 61.6287 | 61.5417 | -61.4319 | -0.2243 | -0.032044 | 1.6525 | -0.11444 | -7.695 | -0.24262 | -0.027466 | 1.8768 | 122.6898 | 122.818 | 115.0635 | 122.7264 | 1.6525 | 122.731 | 68.3441 | -0.24262 | 122.7264 | 1.6525 | 68.3441 | 115.0635 | 122.731 | -122.9828 | -123.0011
1796.3281 | 123.1064 | -61.2076 | 61.5692 | 0.19424 | 0.021787 | 0.010602 | 0.023041 | 0.059471 | -0.0012839 | 0.08634 | -59.5184 | 61.5875 | -61.409 | -61.3953 | 53.6865 | 7.0724 | 61.5921 | 61.7477 | 61.5189 | -61.4639 | -0.20142 | 0.01831 | 1.6891 | -0.18768 | -7.8827 | -0.25635 | -0.050354 | 1.8906 | 122.7997 | 122.9553 | 114.8941 | 122.7951 | 1.6891 | 122.7264 | 68.28 | -0.25635 | 122.7951 | 1.6891 | 68.28 | 114.8941 | 122.7264 | -122.9782 | -123.0331
1797.3281 | 123.0469 | -61.2305 | 61.5784 | 0.17136 | 0.022428 | 0.014661 | 0.024964 | 0.060111 | -0.0029929 | 0.086554 | -59.5963 | 61.5829 | -61.4319 | -61.4639 | 53.7781 | 7.077 | 61.5692 | 61.5555 | 61.5646 | -61.4868 | -0.20142 | 0.004578 | 1.6342 | -0.23346 | -7.8003 | -0.25635 | -0.013733 | 1.8356 | 122.7997 | 122.7859 | 115.0085 | 122.8134 | 1.6342 | 122.7951 | 68.3075 | -0.25635 | 122.8134 | 1.6342 | 68.3075 | 115.0085 | 122.7951 | -123.0103 | -123.0652
1798.3281 | 123.111 | -61.1847 | 61.528 | 0.16373 | 0.020292 | 0.017438 | 0.019837 | 0.062461 | -0.0029929 | 0.085272 | -59.5322 | 61.5875 | -61.4182 | -61.3907 | 53.8376 | 7.164 | 61.4777 | 61.6333 | 61.5463 | -61.4456 | -0.23346 | 0.059509 | 1.6525 | -0.20599 | -7.6904 | -0.26093 | 0.018311 | 1.886 | 122.6624 | 122.818 | 115.0223 | 122.7722 | 1.6525 | 122.731 | 68.3487 | -0.26093 | 122.7722 | 1.6525 | 68.3487 | 115.0223 | 122.731 | -122.9462 | -122.9736
1799.3594 | 123.0743 | -61.2076 | 61.5784 | 0.19424 | 0.022215 | 0.010175 | 0.015992 | 0.05648 | -0.0017111 | 0.085699 | -59.5642 | 61.5372 | -61.4319 | -61.4319 | 53.8559 | 7.2647 | 61.5234 | 61.615 | 61.5646 | -61.4319 | -0.2243 | -0.041199 | 1.6434 | -0.2243 | -7.7225 | -0.2243 | -0.013733 | 1.8677 | 122.731 | 122.8226 | 115.0635 | 122.7448 | 1.6434 | 122.7722 | 68.4723 | -0.2243 | 122.7448 | 1.6434 | 68.4723 | 115.0635 | 122.7722 | -123.0103 | -123.0103
1800.3281 | 123.1247 | -61.1801 | 61.5829 | 0.018768 | 0.020506 | 0.012738 | 0.019623 | 0.059043 | -0.0034201 | 0.085486 | -59.5322 | 61.5601 | -61.4136 | -61.3861 | 53.8696 | 7.2372 | 61.4731 | 61.6425 | 61.5601 | -61.4822 | -0.23346 | -0.022888 | 1.6479 | -0.20599 | -7.7133 | -0.30212 | -0.022888 | 1.8814 | 122.6532 | 122.8226 | 115.0497 | 122.7402 | 1.6479 | 122.7402 | 68.4174 | -0.30212 | 122.7402 | 1.6479 | 68.4174 | 115.0497 | 122.7402 | -122.9965 | -123.0652
1801.3281 | 123.1247 | -61.1893 | 61.5555 | 2.0253 | 0.023283 | 0.0088932 | 0.022187 | 0.059684 | -0.0017111 | 0.085058 | -59.491 | 61.5417 | -61.409 | -61.3998 | 53.8879 | 7.2601 | 61.4731 | 61.6425 | 61.5463 | -61.4685 | -0.21973 | -0.013733 | 1.6983 | -0.21057 | -7.6675 | -0.27924 | -0.009155 | 1.918 | 122.6624 | 122.8317 | 115.0772 | 122.731 | 1.6983 | 122.7356 | 68.4494 | -0.27924 | 122.731 | 1.6983 | 68.4494 | 115.0772 | 122.7356 | -122.9645 | -123.024
1802.3281 | 123.1018 | -61.1847 | 61.5921 | 0.18662 | 0.023283 | 0.006757 | 0.022401 | 0.059684 | -0.0021383 | 0.088263 | -59.5047 | 61.5829 | -61.3815 | -61.2762 | 53.9337 | 7.1869 | 61.5097 | 61.6653 | 61.5646 | -61.4456 | -0.19684 | -0.009155 | 1.68 | -0.091553 | -7.6584 | -0.26093 | -0.027466 | 1.8768 | 122.6944 | 122.85 | 115.1184 | 122.7676 | 1.68 | 122.7493 | 68.3716 | -0.26093 | 122.7676 | 1.68 | 68.3716 | 115.1184 | 122.7493 | -122.9736 | -123.0377
1803.3281 | 123.111 | -61.203 | 61.5646 | 0.17136 | 0.024137 | 0.012097 | 0.023896 | 0.059043 | -2.092e-06 | 0.086126 | -59.5184 | 61.5646 | -61.3953 | -61.3815 | 53.8467 | 7.2784 | 61.1847 | 61.7477 | 61.5234 | -61.4868 | -0.19226 | 0 | 1.6846 | -0.17853 | -7.7179 | -0.28381 | -0.041199 | 1.8768 | 122.3877 | 122.9507 | 115.0497 | 122.7676 | 1.6846 | 122.7264 | 68.4814 | -0.28381 | 122.7676 | 1.6846 | 68.4814 | 115.0497 | 122.7264 | -122.9599 | -123.0515
1804.3281 | 123.0331 | -61.2167 | 61.5921 | 0.18662 | 0.022428 | 0.011884 | 0.023255 | 0.05883 | -0.00064309 | 0.087195 | -59.5779 | 61.6241 | -61.4273 | -61.4685 | 53.7918 | 7.1869 | 61.5829 | 61.5601 | 61.5829 | -61.4685 | -0.21057 | 0.032044 | 1.6388 | -0.25177 | -7.8003 | -0.25177 | -0.009155 | 1.8494 | 122.7997 | 122.7768 | 115.0085 | 122.8409 | 1.6388 | 122.7997 | 68.4036 | -0.25177 | 122.8409 | 1.6388 | 68.4036 | 115.0085 | 122.7997 | -123.0194 | -123.0606
1805.3281 | 123.111 | -61.1664 | 61.5921 | 0.21713 | 0.021574 | 0.013166 | 0.023255 | 0.059684 | -0.00064309 | 0.085058 | -59.5367 | 61.5967 | -61.4273 | -61.4044 | 53.833 | 7.283 | 61.5005 | 61.6333 | 61.5692 | -61.441 | -0.26093 | 0.004578 | 1.6296 | -0.23804 | -7.7591 | -0.27466 | -0.022888 | 1.8906 | 122.6669 | 122.7997 | 114.9994 | 122.7631 | 1.6296 | 122.7356 | 68.4494 | -0.27466 | 122.7631 | 1.6296 | 68.4494 | 114.9994 | 122.7356 | -123.0194 | -123.0331
1806.3281 | 123.0972 | -61.203 | 61.5875 | -0.4924 | 0.021787 | 0.012097 | 0.020264 | 0.059043 | -0.0014975 | 0.086767 | -59.4589 | 61.5784 | -61.3998 | -61.3907 | 53.8559 | 7.283 | 61.4731 | 61.6699 | 61.5738 | -61.4456 | -0.19684 | -0.009155 | 1.7441 | -0.18768 | -7.7316 | -0.24262 | -0.013732 | 1.9409 | 122.6761 | 122.8729 | 115.0589 | 122.7814 | 1.7441 | 122.7768 | 68.486 | -0.24262 | 122.7814 | 1.7441 | 68.486 | 115.0589 | 122.7768 | -122.9874 | -123.0331
1807.3281 | 123.1155 | -61.1938 | 61.5967 | 0.2095 | 0.022001 | 0.009534 | 0.01941 | 0.057548 | -2.092e-06 | 0.086126 | -59.5139 | 61.5646 | -61.4182 | -61.4044 | 53.8971 | 7.2922 | 61.4502 | 61.6653 | 61.5601 | -61.4502 | -0.2243 | -0.032044 | 1.68 | -0.21057 | -7.6996 | -0.25635 | -0.036621 | 1.9043 | 122.644 | 122.8592 | 115.0909 | 122.7585 | 1.68 | 122.7539 | 68.486 | -0.25635 | 122.7585 | 1.68 | 68.486 | 115.0909 | 122.7539 | -123.0148 | -123.0469
1808.3281 | 123.1476 | -61.1984 | 61.5738 | 0.20187 | 0.020933 | 0.010602 | 0.017701 | 0.060325 | -0.0023519 | 0.085486 | -59.5322 | 61.5601 | -61.4319 | -61.3861 | 53.8742 | 7.3151 | 61.4731 | 61.6562 | 61.528 | -61.4456 | -0.23346 | -0.013733 | 1.6663 | -0.18768 | -7.6996 | -0.24719 | -0.045777 | 1.8997 | 122.6715 | 122.8546 | 115.0726 | 122.7585 | 1.6663 | 122.7264 | 68.5135 | -0.24719 | 122.7585 | 1.6663 | 68.5135 | 115.0726 | 122.7264 | -123.0057 | -123.0194
1809.3438 | 123.0103 | -61.1984 | 61.6516 | -0.16434 | 0.02371 | 0.011457 | 0.024537 | 0.059043 | -0.0021383 | 0.083777 | -59.5734 | 61.6516 | -61.3907 | -61.4182 | 53.8101 | 7.2556 | 61.7203 | 61.6058 | 61.6287 | -61.4639 | -0.19226 | 0 | 1.6251 | -0.21973 | -7.8415 | -0.2655 | -0.022888 | 1.8173 | 122.9187 | 122.8043 | 115.0085 | 122.85 | 1.6251 | 122.8271 | 68.454 | -0.2655 | 122.85 | 1.6251 | 68.454 | 115.0085 | 122.8271 | -123.0423 | -123.1155
1810.3281 | 123.111 | -61.1893 | 61.5692 | 0.36972 | 0.021147 | 0.010816 | 0.020905 | 0.058402 | -0.0019247 | 0.084845 | -59.5139 | 61.5509 | -61.3998 | -61.3907 | 53.8605 | 7.37 | 61.4731 | 61.6653 | 61.5463 | -61.441 | -0.21057 | -0.018311 | 1.6754 | -0.20142 | -7.7087 | -0.25177 | -0.022888 | 1.886 | 122.6624 | 122.8546 | 115.0497 | 122.7402 | 1.6754 | 122.7356 | 68.5593 | -0.25177 | 122.7402 | 1.6754 | 68.5593 | 115.0497 | 122.7356 | -122.9691 | -123.0103
1811.3281 | 123.0972 | -61.2076 | 61.5829 | 0.25528 | 0.02136 | 0.012525 | 0.024537 | 0.058616 | -0.0047019 | 0.087195 | -59.6008 | 61.5875 | -61.4044 | -61.4365 | 53.8101 | 7.2006 | 61.5189 | 61.6013 | 61.5646 | -61.4685 | -0.19684 | 0.004577 | 1.6068 | -0.22888 | -7.7728 | -0.26093 | -0.018311 | 1.8036 | 122.7264 | 122.8088 | 115.0177 | 122.7951 | 1.6068 | 122.7722 | 68.4082 | -0.26093 | 122.7951 | 1.6068 | 68.4082 | 115.0177 | 122.7722 | -122.9874 | -123.0515
1812.3281 | 123.1247 | -61.1801 | 61.5692 | 0.2095 | 0.02136 | 0.012738 | 0.020905 | 0.059898 | -0.0021383 | 0.087622 | -59.5184 | 61.5509 | -61.4273 | -61.2946 | 53.7415 | 7.0312 | 61.5967 | 61.7752 | 61.5417 | -61.4456 | -0.24719 | -0.018311 | 1.6617 | -0.11444 | -7.8278 | -0.2655 | -0.027466 | 1.9089 | 122.7768 | 122.9553 | 114.9216 | 122.731 | 1.6617 | 122.7219 | 68.2114 | -0.2655 | 122.731 | 1.6617 | 68.2114 | 114.9216 | 122.7219 | -122.9965 | -123.0148
1813.3281 | 123.0927 | -61.1984 | 61.5829 | 0.24002 | 0.02371 | 0.010816 | 0.020478 | 0.059684 | -0.00021569 | 0.085058 | -59.5322 | 61.5829 | -61.3907 | -61.3815 | 53.8834 | 7.2006 | 61.4868 | 61.6745 | 61.5601 | -61.4273 | -0.19226 | 0 | 1.6663 | -0.18311 | -7.6996 | -0.22888 | -0.022888 | 1.8585 | 122.6852 | 122.8729 | 115.0818 | 122.7814 | 1.6663 | 122.7585 | 68.399 | -0.22888 | 122.7814 | 1.6663 | 68.399 | 115.0818 | 122.7585 | -122.9736 | -123.0103
1814.3281 | 123.1155 | -61.1893 | 61.5967 | 1.3615 | 0.022001 | 0.012311 | 0.020905 | 0.059898 | -0.00021569 | 0.085699 | -59.4406 | 61.5784 | -61.3907 | -61.3861 | 53.8696 | 7.2006 | 61.4777 | 61.6745 | 61.5692 | -61.441 | -0.20142 | -0.018311 | 1.7487 | -0.19684 | -7.7271 | -0.25177 | -0.027466 | 1.9501 | 122.6669 | 122.8638 | 115.0589 | 122.7676 | 1.7487 | 122.7585 | 68.3899 | -0.25177 | 122.7676 | 1.7487 | 68.3899 | 115.0589 | 122.7585 | -122.9874 | -123.0377
1815.3438 | 123.0331 | -61.1984 | 61.6608 | -0.011749 | 0.025633 | 0.014661 | 0.023682 | 0.060539 | -0.0023519 | 0.084631 | -59.491 | 61.6653 | -61.3678 | -61.3907 | 53.8513 | 7.1411 | 61.6425 | 61.6287 | 61.6241 | -61.4639 | -0.16937 | 0.004577 | 1.7075 | -0.19226 | -7.8094 | -0.2655 | -0.036621 | 1.8768 | 122.8409 | 122.8271 | 115.0497 | 122.8638 | 1.7075 | 122.8226 | 68.3395 | -0.2655 | 122.8638 | 1.7075 | 68.3395 | 115.0497 | 122.8226 | -123.0286 | -123.1247
1816.3281 | 123.0743 | -61.1847 | 61.5784 | 0.25528 | 0.022642 | 0.011884 | 0.017914 | 0.061393 | -0.0010703 | 0.086767 | -59.5459 | 61.6241 | -61.3953 | -61.4319 | 53.8925 | 7.2556 | 61.4822 | 61.6608 | 61.5875 | -61.441 | -0.21057 | 0.045777 | 1.6388 | -0.24719 | -7.6859 | -0.25635 | 0.009155 | 1.8494 | 122.6669 | 122.8455 | 115.0772 | 122.8088 | 1.6388 | 122.7722 | 68.4402 | -0.25635 | 122.8088 | 1.6388 | 68.4402 | 115.0772 | 122.7722 | -122.9736 | -123.0194
1817.3438 | 123.1018 | -61.1572 | 61.6425 | -0.080414 | 0.018156 | 0.013379 | 0.016846 | 0.057975 | -0.00085669 | 0.086554 | -59.5139 | 61.5692 | -61.3815 | -61.322 | 53.9291 | 7.2327 | 61.5784 | 61.7569 | 61.6058 | -61.3953 | -0.2243 | -0.073242 | 1.6434 | -0.16479 | -7.7133 | -0.23804 | -0.036621 | 1.8677 | 122.7356 | 122.9141 | 115.0864 | 122.7264 | 1.6434 | 122.7631 | 68.3899 | -0.23804 | 122.7264 | 1.6434 | 68.3899 | 115.0864 | 122.7631 | -123.024 | -123.0377
1818.3281 | 123.0057 | -61.2213 | 61.6287 | 0.20187 | 0.023496 | 0.010388 | 0.024537 | 0.059471 | -0.0019247 | 0.086767 | -59.5963 | 61.6699 | -61.3953 | -61.4868 | 53.7415 | 7.0496 | 61.6562 | 61.5372 | 61.615 | -61.4685 | -0.17395 | 0.041199 | 1.6251 | -0.2655 | -7.8873 | -0.24719 | -0.013733 | 1.799 | 122.8775 | 122.7585 | 114.9628 | 122.8912 | 1.6251 | 122.8363 | 68.2709 | -0.24719 | 122.8912 | 1.6251 | 68.2709 | 114.9628 | 122.8363 | -123.024 | -123.0972
1819.3438 | 123.0881 | -61.2167 | 61.5921 | 0.24002 | 0.023283 | 0.014447 | 0.021119 | 0.060111 | -0.0019247 | 0.085272 | -59.5367 | 61.6013 | -61.4273 | -61.3953 | 53.8239 | 7.2281 | 61.4914 | 61.647 | 61.6013 | -61.4502 | -0.21057 | 0.009155 | 1.68 | -0.17853 | -7.7682 | -0.23346 | 0.009155 | 1.8906 | 122.7081 | 122.8638 | 115.0406 | 122.818 | 1.68 | 122.818 | 68.4448 | -0.23346 | 122.818 | 1.68 | 68.4448 | 115.0406 | 122.818 | -123.0194 | -123.0423
1820.3281 | 123.0606 | -61.203 | 61.6013 | 0.23239 | 0.02136 | 0.013166 | 0.020051 | 0.060111 | -0.00064309 | 0.086554 | -59.5596 | 61.6241 | -61.4182 | -61.4273 | 53.8055 | 7.1594 | 61.528 | 61.6196 | 61.5829 | -61.4594 | -0.21515 | 0.022889 | 1.6434 | -0.2243 | -7.7957 | -0.25635 | -0.01831 | 1.8585 | 122.731 | 122.8226 | 115.0085 | 122.8271 | 1.6434 | 122.7859 | 68.3624 | -0.25635 | 122.8271 | 1.6434 | 68.3624 | 115.0085 | 122.7859 | -123.0194 | -123.0606
1821.3281 | 123.0652 | -61.2213 | 61.5921 | 0.24002 | 0.023496 | 0.015943 | 0.021332 | 0.060752 | -0.0012839 | 0.086554 | -59.5917 | 61.6379 | -61.4456 | -61.4502 | 53.8147 | 7.1503 | 61.5738 | 61.5829 | 61.6013 | -61.4594 | -0.22431 | 0.045776 | 1.6296 | -0.22888 | -7.7774 | -0.23804 | 0.009155 | 1.8539 | 122.7951 | 122.8043 | 115.036 | 122.8592 | 1.6296 | 122.8226 | 68.3716 | -0.23804 | 122.8592 | 1.6296 | 68.3716 | 115.036 | 122.8226 | -123.0377 | -123.0515
1822.3438 | 123.1155 | -61.1526 | 61.6196 | -0.13382 | 0.022001 | 0.0056888 | 0.011719 | 0.056693 | 0.00042511 | 0.085486 | -59.5184 | 61.5646 | -61.3586 | -61.441 | 53.833 | 7.2418 | 61.6058 | 61.6882 | 61.615 | -61.3907 | -0.20599 | -0.054932 | 1.6342 | -0.28839 | -7.7866 | -0.23804 | -0.004578 | 1.8402 | 122.7585 | 122.8409 | 114.9857 | 122.7173 | 1.6342 | 122.7676 | 68.3945 | -0.23804 | 122.7173 | 1.6342 | 68.3945 | 114.9857 | 122.7676 | -122.9782 | -123.0103
1823.3281 | 123.111 | -61.1572 | 61.5921 | 0.19424 | 0.022642 | 0.015515 | 0.020264 | 0.056907 | -0.00085669 | 0.084631 | -59.4955 | 61.6333 | -61.3541 | -61.377 | 53.8559 | 7.2418 | 61.5189 | 61.6837 | 61.5875 | -61.4136 | -0.19684 | 0.041199 | 1.6617 | -0.21973 | -7.7362 | -0.25635 | -0.004578 | 1.8585 | 122.6761 | 122.8409 | 115.0131 | 122.7905 | 1.6617 | 122.7448 | 68.399 | -0.25635 | 122.7905 | 1.6617 | 68.399 | 115.0131 | 122.7448 | -122.9462 | -123.0057
1824.3281 | 122.9965 | -61.2076 | 61.6241 | 0.16373 | 0.023924 | 0.016797 | 0.020905 | 0.058616 | 0.0014933 | 0.087195 | -59.5779 | 61.6791 | -61.4182 | -61.4685 | 53.746 | 7.0999 | 61.6608 | 61.5417 | 61.6241 | -61.4914 | -0.21057 | 0.054931 | 1.6296 | -0.26093 | -7.8781 | -0.28381 | 0 | 1.8402 | 122.8683 | 122.7493 | 114.9536 | 122.8867 | 1.6296 | 122.8317 | 68.3075 | -0.28381 | 122.8867 | 1.6296 | 68.3075 | 114.9536 | 122.8317 | -123.0423 | -123.1155
1825.3281 | 122.9919 | -61.2213 | 61.6333 | -0.37033 | 0.021574 | 0.013166 | 0.02475 | 0.061393 | -0.0010703 | 0.08399 | -59.61 | 61.6974 | -61.3953 | -61.4822 | 53.7552 | 7.0953 | 61.6562 | 61.5372 | 61.6425 | -61.4685 | -0.17395 | 0.064087 | 1.6113 | -0.26093 | -7.8781 | -0.24719 | 0.009155 | 1.7853 | 122.8775 | 122.7585 | 114.9765 | 122.9187 | 1.6113 | 122.8638 | 68.3166 | -0.24719 | 122.9187 | 1.6113 | 68.3166 | 114.9765 | 122.8638 | -123.0286 | -123.1018
1826.3281 | 123.0103 | -61.2213 | 61.6562 | 0.16373 | 0.022856 | 0.012738 | 0.02411 | 0.068229 | -0.0010703 | 0.084631 | -59.6146 | 61.6745 | -61.4182 | -61.2259 | 53.8834 | 7.0816 | 61.702 | 61.5326 | 61.6653 | -61.4685 | -0.19684 | 0.018311 | 1.6068 | -0.004578 | -7.7728 | -0.24719 | 0.009155 | 1.8036 | 122.9233 | 122.7539 | 115.1047 | 122.8958 | 1.6068 | 122.8867 | 68.3029 | -0.24719 | 122.8958 | 1.6068 | 68.3029 | 115.1047 | 122.8867 | -123.0743 | -123.1247
1827.3438 | 123.0927 | -61.2076 | 61.6104 | 0.056915 | 0.019865 | 0.011029 | 0.014496 | 0.061393 | -0.0012839 | 0.088904 | -59.61 | 61.5692 | -61.409 | -61.4731 | 53.8284 | 7.1365 | 61.5784 | 61.6104 | 61.5784 | -61.4182 | -0.20142 | -0.041199 | 1.5976 | -0.2655 | -7.782 | -0.21057 | -0.032044 | 1.799 | 122.7859 | 122.818 | 115.036 | 122.7768 | 1.5976 | 122.7859 | 68.3441 | -0.21057 | 122.7768 | 1.5976 | 68.3441 | 115.036 | 122.7859 | -123.0194 | -123.0286
1828.3281 | 122.9919 | -61.235 | 61.615 | 0.1561 | 0.024351 | 0.012738 | 0.023469 | 0.057975 | 0.00021151 | 0.085913 | -59.6191 | 61.6791 | -61.3998 | -61.5051 | 53.7323 | 7.0358 | 61.6608 | 61.5143 | 61.6287 | -61.4777 | -0.1648 | 0.064087 | 1.6159 | -0.27008 | -7.8827 | -0.24262 | 0.013733 | 1.7807 | 122.8958 | 122.7493 | 114.9673 | 122.9141 | 1.6159 | 122.8638 | 68.2709 | -0.24262 | 122.9141 | 1.6159 | 68.2709 | 114.9673 | 122.8638 | -123.0148 | -123.0927
1829.3281 | 122.9691 | -61.2305 | 61.6287 | 0.14084 | 0.022642 | 0.015088 | 0.025178 | 0.065666 | -0.0029929 | 0.085058 | -59.6146 | 61.6882 | -61.4136 | -61.2396 | 53.8559 | 7.1136 | 61.6791 | 61.5326 | 61.6379 | -61.4777 | -0.1831 | 0.059509 | 1.6159 | -0.009155 | -7.7728 | -0.24719 | 0.009155 | 1.799 | 122.9095 | 122.7631 | 115.0864 | 122.9187 | 1.6159 | 122.8683 | 68.3441 | -0.24719 | 122.9187 | 1.6159 | 68.3441 | 115.0864 | 122.8683 | -123.0423 | -123.1064
1830.3438 | 123.0011 | -61.2259 | 61.647 | -0.20248 | 0.02136 | 0.009534 | 0.017487 | 0.057975 | -0.0014975 | 0.084845 | -59.5871 | 61.6425 | -61.4182 | -61.4319 | 53.801 | 7.1182 | 61.7157 | 61.6425 | 61.6516 | -61.441 | -0.19226 | -0.004578 | 1.6388 | -0.20599 | -7.8461 | -0.21515 | 0.004577 | 1.8311 | 122.9416 | 122.8683 | 115.0269 | 122.8683 | 1.6388 | 122.8775 | 68.3441 | -0.21515 | 122.8683 | 1.6388 | 68.3441 | 115.0269 | 122.8775 | -123.0652 | -123.0881
1831.3281 | 123.0103 | -61.2442 | 61.6562 | 0.11032 | 0.025205 | 0.017865 | 0.024964 | 0.059043 | -0.00085669 | 0.086554 | -59.61 | 61.6699 | -61.3998 | -61.4594 | 53.714 | 7.0816 | 61.6425 | 61.5601 | 61.6058 | -61.5005 | -0.15564 | 0.013733 | 1.6342 | -0.21515 | -7.9422 | -0.25635 | -0.050354 | 1.7899 | 122.8867 | 122.8043 | 114.9582 | 122.9141 | 1.6342 | 122.85 | 68.3258 | -0.25635 | 122.9141 | 1.6342 | 68.3258 | 114.9582 | 122.85 | -123.056 | -123.1567
1832.3438 | 123.0606 | -61.1893 | 61.6104 | 0.011139 | 0.019651 | 0.0080386 | 0.015351 | 0.059043 | -0.0017111 | 0.085913 | -59.6146 | 61.5738 | -61.4182 | -61.4502 | 53.8193 | 7.1274 | 61.5921 | 61.6608 | 61.6058 | -61.3907 | -0.22888 | -0.036621 | 1.5747 | -0.26093 | -7.7911 | -0.20142 | -0.004578 | 1.8036 | 122.7814 | 122.85 | 115.0085 | 122.7631 | 1.5747 | 122.7951 | 68.3166 | -0.20142 | 122.7631 | 1.5747 | 68.3166 | 115.0085 | 122.7951 | -123.0286 | -123.0011
1833.3281 | 122.9736 | -61.235 | 61.6104 | 0.079804 | 0.024351 | 0.01402 | 0.025819 | 0.06182 | -2.092e-06 | 0.084845 | -59.5688 | 61.6608 | -61.4227 | -61.4914 | 53.714 | 7.0175 | 61.6745 | 61.5372 | 61.6287 | -61.5005 | -0.18768 | 0.050354 | 1.6663 | -0.25635 | -7.8964 | -0.2655 | 0.01831 | 1.8539 | 122.9095 | 122.7722 | 114.949 | 122.8958 | 1.6663 | 122.8638 | 68.2526 | -0.2655 | 122.8958 | 1.6663 | 68.2526 | 114.949 | 122.8638 | -123.0331 | -123.111
1834.3281 | 122.9965 | -61.2259 | 61.615 | 0.095062 | 0.022642 | 0.013166 | 0.02176 | 0.060325 | -0.0014975 | 0.084845 | -59.5871 | 61.6608 | -61.4273 | -61.4685 | 53.7186 | 6.9763 | 61.6699 | 61.5509 | 61.6516 | -61.4777 | -0.20142 | 0.045777 | 1.6388 | -0.24262 | -7.8964 | -0.25177 | 0.036621 | 1.8402 | 122.8958 | 122.7768 | 114.9445 | 122.8867 | 1.6388 | 122.8775 | 68.2022 | -0.25177 | 122.8867 | 1.6388 | 68.2022 | 114.9445 | 122.8775 | -123.0423 | -123.0927
1835.3281 | 123.056 | -61.2488 | 61.6104 | 0.23239 | 0.019865 | 0.014661 | 0.022187 | 0.06118 | 0.0014933 | 0.085058 | -59.5779 | 61.6379 | -61.4044 | -61.4548 | 53.7552 | 7.0496 | 61.5555 | 61.615 | 61.6058 | -61.4777 | -0.15564 | 0.027465 | 1.6708 | -0.20599 | -7.8552 | -0.22888 | -0.004578 | 1.8265 | 122.8043 | 122.8638 | 115.004 | 122.8867 | 1.6708 | 122.8546 | 68.2983 | -0.22888 | 122.8867 | 1.6708 | 68.2983 | 115.004 | 122.8546 | -123.0148 | -123.0881
1836.3281 | 122.9965 | -61.2305 | 61.6241 | -0.019379 | 0.024137 | 0.014875 | 0.023682 | 0.061607 | 0.00042511 | 0.084845 | -59.5459 | 61.6699 | -61.4182 | -61.4594 | 53.7598 | 7.0496 | 61.6379 | 61.6104 | 61.615 | -61.4639 | -0.18768 | 0.045776 | 1.6846 | -0.22888 | -7.8644 | -0.23346 | -0.009156 | 1.8723 | 122.8683 | 122.8409 | 114.9902 | 122.9004 | 1.6846 | 122.8455 | 68.28 | -0.23346 | 122.9004 | 1.6846 | 68.28 | 114.9902 | 122.8455 | -123.0423 | -123.0881
1837.3281 | 123.0377 | -61.2259 | 61.6196 | -0.019379 | 0.022856 | 0.014234 | 0.02411 | 0.062034 | -0.0012839 | 0.084631 | -59.5413 | 61.6882 | -61.409 | -61.4227 | 53.7781 | 7.0541 | 61.6653 | 61.6196 | 61.6379 | -61.4594 | -0.18311 | 0.068664 | 1.6846 | -0.19684 | -7.8415 | -0.23346 | 0.01831 | 1.8677 | 122.8912 | 122.8455 | 115.004 | 122.9141 | 1.6846 | 122.8638 | 68.28 | -0.23346 | 122.9141 | 1.6846 | 68.28 | 115.004 | 122.8638 | -123.0286 | -123.0789
1838.3281 | 123.0469 | -61.203 | 61.6425 | 0.011139 | 0.025205 | 0.013166 | 0.022614 | 0.062675 | -0.0017111 | 0.087195 | -59.523 | 61.6928 | -61.409 | -61.4182 | 53.801 | 7.0953 | 61.6516 | 61.6425 | 61.615 | -61.4685 | -0.20599 | 0.050354 | 1.68 | -0.21515 | -7.8415 | -0.2655 | -0.027466 | 1.886 | 122.8546 | 122.8455 | 115.004 | 122.8958 | 1.68 | 122.818 | 68.2983 | -0.2655 | 122.8958 | 1.68 | 68.2983 | 115.004 | 122.818 | -123.0515 | -123.111
1839.3438 | 123.0606 | -61.235 | 61.6058 | 0.23239 | 0.022642 | 0.01167 | 0.01941 | 0.062461 | -0.0014975 | 0.087408 | -59.61 | 61.6425 | -61.4182 | -61.4822 | 53.7735 | 7.0404 | 61.5875 | 61.5921 | 61.6196 | -61.4639 | -0.18311 | 0.036621 | 1.6251 | -0.24719 | -7.8323 | -0.22888 | 0.013733 | 1.8082 | 122.8226 | 122.8271 | 115.0085 | 122.8775 | 1.6251 | 122.8546 | 68.2755 | -0.22888 | 122.8775 | 1.6251 | 68.2755 | 115.0085 | 122.8546 | -123.024 | -123.0698
1840.3281 | 122.9919 | -61.1938 | 61.6379 | 0.0035097 | 0.024778 | 0.012525 | 0.021546 | 0.062248 | -0.0025657 | 0.085272 | -59.5459 | 61.6882 | -61.3953 | -61.409 | 53.7781 | 7.1365 | 61.6608 | 61.6196 | 61.6241 | -61.4639 | -0.20142 | 0.050354 | 1.648 | -0.21515 | -7.8598 | -0.27008 | -0.013732 | 1.8494 | 122.8546 | 122.8134 | 114.9719 | 122.8821 | 1.648 | 122.818 | 68.3304 | -0.27008 | 122.8821 | 1.648 | 68.3304 | 114.9719 | 122.818 | -123.0331 | -123.1018
1841.3281 | 123.0377 | -61.1847 | 61.6196 | 0.018768 | 0.022856 | 0.010175 | 0.022614 | 0.062889 | -0.0017111 | 0.085272 | -59.5184 | 61.6837 | -61.409 | -61.4136 | 53.7964 | 7.1182 | 61.647 | 61.6562 | 61.6699 | -61.4548 | -0.22431 | 0.064087 | 1.6663 | -0.22888 | -7.8232 | -0.27008 | 0.050354 | 1.8906 | 122.8317 | 122.8409 | 114.9811 | 122.8683 | 1.6663 | 122.8546 | 68.3029 | -0.27008 | 122.8683 | 1.6663 | 68.3029 | 114.9811 | 122.8546 | -123.0286 | -123.0743
1842.3281 | 123.0286 | -61.203 | 61.6333 | 0.20187 | 0.023069 | 0.014661 | 0.022614 | 0.060111 | -0.0051291 | 0.088049 | -59.4955 | 61.7065 | -61.409 | -61.4182 | 53.7735 | 7.0953 | 61.6379 | 61.6425 | 61.6653 | -61.4365 | -0.20599 | 0.073242 | 1.7075 | -0.21515 | -7.8598 | -0.23346 | 0.032043 | 1.9135 | 122.8409 | 122.8455 | 114.9765 | 122.9095 | 1.7075 | 122.8683 | 68.2983 | -0.23346 | 122.9095 | 1.7075 | 68.2983 | 114.9765 | 122.8683 | -123.0423 | -123.0698
1843.3594 | 123.0194 | -61.2305 | 61.6196 | 0.011139 | 0.024565 | 0.015088 | 0.022187 | 0.062889 | 0.00063871 | 0.084417 | -59.5596 | 61.6791 | -61.4319 | -61.441 | 53.7323 | 7.0679 | 61.6516 | 61.5967 | 61.647 | -61.496 | -0.20142 | 0.059509 | 1.6708 | -0.21057 | -7.8873 | -0.2655 | 0.027466 | 1.8723 | 122.8821 | 122.8271 | 114.9628 | 122.9095 | 1.6708 | 122.8775 | 68.2983 | -0.2655 | 122.9095 | 1.6708 | 68.2983 | 114.9628 | 122.8775 | -123.0515 | -123.1155
1844.3281 | 123.0331 | -61.203 | 61.6425 | -0.14908 | 0.020506 | 0.010388 | 0.020051 | 0.060966 | -0.00021569 | 0.085913 | -59.5825 | 61.6699 | -61.4136 | -61.441 | 53.746 | 7.0496 | 61.734 | 61.615 | 61.6699 | -61.4502 | -0.21057 | 0.027466 | 1.6205 | -0.23804 | -7.8964 | -0.24719 | 0.027466 | 1.8311 | 122.937 | 122.818 | 114.949 | 122.8729 | 1.6205 | 122.8729 | 68.2526 | -0.24719 | 122.8729 | 1.6205 | 68.2526 | 114.949 | 122.8729 | -123.056 | -123.0927
1845.3281 | 122.9965 | -61.203 | 61.6791 | -0.14908 | 0.02136 | 0.0080386 | 0.019623 | 0.059471 | -0.0027793 | 0.085699 | -59.6054 | 61.6928 | -61.4227 | -61.4639 | 53.7369 | 7.0084 | 61.7477 | 61.6241 | 61.6699 | -61.4365 | -0.21973 | 0.013733 | 1.5976 | -0.26093 | -7.9422 | -0.23346 | -0.009155 | 1.8173 | 122.9507 | 122.8271 | 114.9399 | 122.8958 | 1.5976 | 122.8729 | 68.2114 | -0.23346 | 122.8958 | 1.5976 | 68.2114 | 114.9399 | 122.8729 | -123.1018 | -123.1155
1846.3281 | 122.9874 | -61.1984 | 61.6745 | -0.18723 | 0.023924 | 0.01402 | 0.020051 | 0.059898 | -0.00085669 | 0.085486 | -59.6054 | 61.6837 | -61.4182 | -61.4731 | 53.7369 | 7.0587 | 61.7569 | 61.6425 | 61.6699 | -61.4365 | -0.21973 | 0.009155 | 1.593 | -0.27466 | -7.9376 | -0.23804 | -0.004578 | 1.8127 | 122.9553 | 122.8409 | 114.9353 | 122.8821 | 1.593 | 122.8683 | 68.2571 | -0.23804 | 122.8821 | 1.593 | 68.2571 | 114.9353 | 122.8683 | -123.0927 | -123.111
1847.3281 | 123.0148 | -61.1664 | 61.6928 | -0.15671 | 0.021574 | 0.015088 | 0.020692 | 0.059898 | 0.00085231 | 0.085272 | -59.5596 | 61.6882 | -61.3815 | -61.4548 | 53.7369 | 7.077 | 61.734 | 61.6516 | 61.6791 | -61.4319 | -0.21515 | -0.004578 | 1.6068 | -0.28839 | -7.9559 | -0.2655 | -0.013733 | 1.8219 | 122.9004 | 122.818 | 114.9033 | 122.8546 | 1.6068 | 122.8455 | 68.2434 | -0.2655 | 122.8546 | 1.6068 | 68.2434 | 114.9033 | 122.8455 | -123.0743 | -123.1247
1848.3281 | 123.0103 | -61.203 | 61.6562 | -0.14145 | 0.022856 | 0.0073978 | 0.020905 | 0.05883 | 0.00021151 | 0.08634 | -59.5917 | 61.6928 | -61.409 | -61.4548 | 53.7323 | 7.0541 | 61.7661 | 61.6333 | 61.702 | -61.4182 | -0.20599 | 0.036621 | 1.6113 | -0.25177 | -7.9239 | -0.21515 | 0.045776 | 1.8173 | 122.9691 | 122.8363 | 114.9353 | 122.8958 | 1.6113 | 122.905 | 68.2571 | -0.21515 | 122.8958 | 1.6113 | 68.2571 | 114.9353 | 122.905 | -123.0652 | -123.0743
1849.3281 | 123.0011 | -61.203 | 61.6333 | 0.079804 | 0.023283 | 0.015729 | 0.023469 | 0.062889 | -0.00021569 | 0.087195 | -59.5367 | 61.6745 | -61.4044 | -61.4319 | 53.7323 | 7.0724 | 61.6745 | 61.6104 | 61.6745 | -61.4273 | -0.20142 | 0.041199 | 1.6663 | -0.22888 | -7.901 | -0.2243 | 0.041199 | 1.8677 | 122.8775 | 122.8134 | 114.9353 | 122.8775 | 1.6663 | 122.8775 | 68.2755 | -0.2243 | 122.8775 | 1.6663 | 68.2755 | 114.9353 | 122.8775 | -123.0377 | -123.0606
1850.3438 | 123.143 | -61.1664 | 61.6241 | -0.019379 | 0.021574 | 0.0071842 | 0.011719 | 0.059257 | -0.0034201 | 0.086126 | -59.5413 | 61.5509 | -61.3678 | -61.3495 | 53.8834 | 7.251 | 61.5646 | 61.7706 | 61.647 | -61.3815 | -0.20142 | -0.073243 | 1.6251 | -0.18311 | -7.7408 | -0.21515 | 0.022888 | 1.8265 | 122.731 | 122.937 | 115.0497 | 122.7173 | 1.6251 | 122.8134 | 68.4174 | -0.21515 | 122.7173 | 1.6251 | 68.4174 | 115.0497 | 122.8134 | -122.9919 | -123.0057
1851.3281 | 122.9736 | -61.2259 | 61.6608 | 0.034027 | 0.024565 | 0.0086796 | 0.024537 | 0.059471 | -0.0027793 | 0.088049 | -59.5688 | 61.6882 | -61.4136 | -61.4594 | 53.7323 | 7.077 | 61.6791 | 61.6058 | 61.6287 | -61.4639 | -0.18768 | 0.027465 | 1.6571 | -0.23346 | -7.9285 | -0.23804 | -0.032044 | 1.8448 | 122.905 | 122.8317 | 114.9582 | 122.9141 | 1.6571 | 122.8546 | 68.3029 | -0.23804 | 122.9141 | 1.6571 | 68.3029 | 114.9582 | 122.8546 | -123.0743 | -123.1247
1852.3281 | 123.0423 | -61.1801 | 61.7111 | -0.11856 | 0.021574 | 0.009534 | 0.018342 | 0.057762 | -0.0010703 | 0.086126 | -59.5413 | 61.6882 | -61.3815 | -61.4319 | 53.7781 | 7.1365 | 61.7477 | 61.6516 | 61.6882 | -61.4182 | -0.20142 | -0.022889 | 1.6388 | -0.25177 | -7.933 | -0.23804 | -0.022889 | 1.8402 | 122.9279 | 122.8317 | 114.9582 | 122.8683 | 1.6388 | 122.8683 | 68.3167 | -0.23804 | 122.8683 | 1.6388 | 68.3167 | 114.9582 | 122.8683 | -123.0927 | -123.1293
1853.3281 | 123.0057 | -61.2076 | 61.6516 | 0.095062 | 0.021787 | 0.012952 | 0.018555 | 0.057762 | -0.00064309 | 0.084204 | -59.5505 | 61.702 | -61.3815 | -61.4639 | 53.7689 | 7.1594 | 61.7523 | 61.647 | 61.7065 | -61.4456 | -0.17395 | 0.050354 | 1.6571 | -0.25635 | -7.8827 | -0.23804 | 0.054932 | 1.8311 | 122.9599 | 122.8546 | 114.9765 | 122.9095 | 1.6571 | 122.9141 | 68.367 | -0.23804 | 122.9095 | 1.6571 | 68.367 | 114.9765 | 122.9141 | -123.0331 | -123.0972
1854.3281 | 123.024 | -61.1755 | 61.6745 | -0.14908 | 0.021147 | 0.010388 | 0.022614 | 0.060325 | -0.0027793 | 0.087408 | -59.5642 | 61.6699 | -61.3953 | -61.4273 | 53.746 | 7.0724 | 61.734 | 61.6379 | 61.6928 | -61.4502 | -0.21973 | -0.004578 | 1.6113 | -0.25177 | -7.9285 | -0.27466 | 0.01831 | 1.8311 | 122.9095 | 122.8134 | 114.9216 | 122.8455 | 1.6113 | 122.8683 | 68.248 | -0.27466 | 122.8455 | 1.6113 | 68.248 | 114.9216 | 122.8683 | -123.0698 | -123.1247
1855.3281 | 123.0057 | -61.2122 | 61.6562 | -0.1796 | 0.023496 | 0.010816 | 0.020905 | 0.059684 | -0.0019247 | 0.085699 | -59.5734 | 61.6791 | -61.3998 | -61.4319 | 53.7689 | 7.132 | 61.7706 | 61.6333 | 61.6974 | -61.4456 | -0.18768 | 0.022888 | 1.6388 | -0.21973 | -7.8873 | -0.23346 | 0.041199 | 1.8265 | 122.9828 | 122.8455 | 114.9811 | 122.8912 | 1.6388 | 122.9095 | 68.3441 | -0.23346 | 122.8912 | 1.6388 | 68.3441 | 114.9811 | 122.9095 | -123.056 | -123.1018
1856.3594 | 123.0194 | -61.2213 | 61.6699 | -0.24063 | 0.022001 | 0.0080386 | 0.021546 | 0.05648 | -0.0036337 | 0.085272 | -59.5871 | 61.6699 | -61.409 | -61.29 | 53.6407 | 6.9534 | 61.6974 | 61.6882 | 61.6974 | -61.4365 | -0.18768 | 0 | 1.6342 | -0.068665 | -8.0292 | -0.21515 | 0.027466 | 1.8219 | 122.9187 | 122.9095 | 114.8621 | 122.8912 | 1.6342 | 122.9187 | 68.1747 | -0.21515 | 122.8912 | 1.6342 | 68.1747 | 114.8621 | 122.9187 | -123.0789 | -123.1064
1857.3281 | 122.9919 | -61.1847 | 61.6882 | -0.057526 | 0.023069 | 0.012311 | 0.018983 | 0.058402 | -0.0023519 | 0.084417 | -59.5963 | 61.6791 | -61.3678 | -61.4182 | 53.7506 | 7.1045 | 61.7569 | 61.6379 | 61.6791 | -61.441 | -0.18311 | -0.009155 | 1.5884 | -0.23346 | -7.9376 | -0.25635 | -0.009155 | 1.7715 | 122.9416 | 122.8226 | 114.9353 | 122.8638 | 1.5884 | 122.8638 | 68.2892 | -0.25635 | 122.8638 | 1.5884 | 68.2892 | 114.9353 | 122.8638 | -123.056 | -123.1293
1858.3438 | 123.0652 | -61.2076 | 61.6425 | 0.087433 | 0.021147 | 0.010602 | 0.014283 | 0.058189 | -2.092e-06 | 0.087195 | -59.6191 | 61.5738 | -61.377 | -61.4456 | 53.714 | 7.0541 | 61.5738 | 61.6699 | 61.6287 | -61.4044 | -0.16937 | -0.068664 | 1.5884 | -0.23804 | -7.9285 | -0.19684 | -0.013733 | 1.7578 | 122.7814 | 122.8775 | 114.9216 | 122.7814 | 1.5884 | 122.8363 | 68.2617 | -0.19684 | 122.7814 | 1.5884 | 68.2617 | 114.9216 | 122.8363 | -123.0194 | -123.0469
1859.3281 | 123.0606 | -61.1755 | 61.6699 | -0.18723 | 0.019224 | 0.0073978 | 0.018342 | 0.055839 | -0.0032065 | 0.085272 | -59.5505 | 61.6333 | -61.3815 | -61.3678 | 53.7964 | 7.1045 | 61.6608 | 61.7157 | 61.6287 | -61.409 | -0.20599 | -0.036621 | 1.6251 | -0.19226 | -7.8735 | -0.23346 | -0.041199 | 1.8311 | 122.8363 | 122.8912 | 114.9719 | 122.8088 | 1.6251 | 122.8043 | 68.28 | -0.23346 | 122.8088 | 1.6251 | 68.28 | 114.9719 | 122.8043 | -123.0515 | -123.0789
1860.3438 | 123.1201 | -61.1572 | 61.6425 | -0.042267 | 0.019438 | 0.0082522 | 0.016846 | 0.057334 | -0.0029929 | 0.08399 | -59.5413 | 61.5692 | -61.3678 | -61.3678 | 53.8147 | 7.1228 | 61.5692 | 61.7432 | 61.6104 | -61.3815 | -0.21057 | -0.073242 | 1.6159 | -0.21057 | -7.8278 | -0.2243 | -0.032043 | 1.8265 | 122.7264 | 122.9004 | 114.9719 | 122.7264 | 1.6159 | 122.7676 | 68.28 | -0.2243 | 122.7264 | 1.6159 | 68.28 | 114.9719 | 122.7676 | -123.0103 | -123.024
1861.3281 | 123.024 | -61.1893 | 61.6699 | -0.22537 | 0.022001 | 0.010175 | 0.021119 | 0.056266 | 0.0017069 | 0.086981 | -59.5459 | 61.6791 | -61.3724 | -61.409 | 53.7369 | 7.0404 | 61.7569 | 61.647 | 61.6791 | -61.4365 | -0.1831 | 0.009155 | 1.6434 | -0.21973 | -7.933 | -0.24719 | 0.009155 | 1.8265 | 122.9462 | 122.8363 | 114.9261 | 122.8683 | 1.6434 | 122.8683 | 68.2297 | -0.24719 | 122.8683 | 1.6434 | 68.2297 | 114.9261 | 122.8683 | -123.0423 | -123.1064
1862.3438 | 123.0652 | -61.1481 | 61.6516 | -0.21774 | 0.01901 | 0.010175 | 0.018769 | 0.057762 | -0.0029929 | 0.087835 | -59.5047 | 61.6287 | -61.3312 | -61.3449 | 53.833 | 7.196 | 61.6699 | 61.734 | 61.6745 | -61.4044 | -0.18311 | -0.022888 | 1.6434 | -0.19684 | -7.8186 | -0.25635 | 0.022889 | 1.8265 | 122.818 | 122.8821 | 114.9811 | 122.7768 | 1.6434 | 122.8226 | 68.3441 | -0.25635 | 122.7768 | 1.6434 | 68.3441 | 114.9811 | 122.8226 | -122.9828 | -123.056
1863.3281 | 122.9874 | -61.1481 | 61.6928 | -0.29404 | 0.022001 | 0.0069706 | 0.022614 | 0.05648 | -0.0017111 | 0.083349 | -59.5734 | 61.6974 | -61.3815 | -61.4182 | 53.7735 | 7.0541 | 61.7661 | 61.647 | 61.6974 | -61.4273 | -0.23346 | 0.004578 | 1.5747 | -0.27008 | -7.9193 | -0.27924 | 0.004578 | 1.8082 | 122.9141 | 122.7951 | 114.9216 | 122.8455 | 1.5747 | 122.8455 | 68.2022 | -0.27924 | 122.8455 | 1.5747 | 68.2022 | 114.9216 | 122.8455 | -123.0743 | -123.1201
1864.3438 | 123.0423 | -61.1893 | 61.6196 | 0.1561 | 0.020506 | 0.0069706 | 0.020692 | 0.059898 | -0.0021383 | 0.085913 | -59.5596 | 61.5875 | -61.377 | -61.4182 | 53.7964 | 7.1182 | 61.5646 | 61.6745 | 61.6196 | -61.4136 | -0.18768 | -0.032044 | 1.6296 | -0.22888 | -7.8232 | -0.2243 | 0 | 1.8173 | 122.7539 | 122.8638 | 114.9857 | 122.7768 | 1.6296 | 122.8088 | 68.3075 | -0.2243 | 122.7768 | 1.6296 | 68.3075 | 114.9857 | 122.8088 | -122.9965 | -123.0331
1865.3281 | 123.0286 | -61.1755 | 61.6837 | -1.2325 | 0.023496 | 0.0091068 | 0.023469 | 0.056053 | -0.0012839 | 0.08634 | -59.6283 | 61.702 | -61.3678 | -61.409 | 53.7552 | 7.0587 | 61.7661 | 61.6608 | 61.6882 | -61.4319 | -0.19226 | 0.01831 | 1.5472 | -0.23346 | -7.9285 | -0.25635 | 0.004577 | 1.7395 | 122.9416 | 122.8363 | 114.9307 | 122.8775 | 1.5472 | 122.8638 | 68.2343 | -0.25635 | 122.8775 | 1.5472 | 68.2343 | 114.9307 | 122.8638 | -123.0515 | -123.1155
1866.3438 | 123.1567 | -61.1343 | 61.647 | -0.057526 | 0.018583 | 0.0076114 | 0.015565 | 0.058402 | -0.0017111 | 0.085058 | -59.5596 | 61.5784 | -61.3678 | -61.3312 | 53.8193 | 7.1228 | 61.5555 | 61.7615 | 61.6196 | -61.377 | -0.23346 | -0.068665 | 1.5747 | -0.19684 | -7.8278 | -0.24262 | -0.027466 | 1.8082 | 122.6898 | 122.8958 | 114.9536 | 122.7127 | 1.5747 | 122.7539 | 68.2571 | -0.24262 | 122.7127 | 1.5747 | 68.2571 | 114.9536 | 122.7539 | -123.0148 | -123.024
1867.3281 | 122.9828 | -61.1938 | 61.6928 | -0.15671 | 0.02136 | 0.0080386 | 0.020692 | 0.055625 | -0.0019247 | 0.084417 | -59.5688 | 61.6699 | -61.3541 | -61.3449 | 54.0207 | 7.0541 | 61.615 | 61.5829 | 61.6699 | -61.441 | -0.16022 | -0.022888 | 1.6251 | -0.15106 | -7.6721 | -0.24719 | -0.022888 | 1.7853 | 122.8088 | 122.7768 | 115.2145 | 122.8638 | 1.6251 | 122.8638 | 68.248 | -0.24719 | 122.8638 | 1.6251 | 68.248 | 115.2145 | 122.8638 | -123.0469 | -123.1338
1868.3594 | 122.9965 | -61.1938 | 61.7111 | -0.14145 | 0.021787 | 0.0091068 | 0.023682 | 0.057762 | -0.0042747 | 0.085272 | -59.5505 | 61.7065 | -61.3815 | -61.4044 | 53.7415 | 7.0129 | 61.7477 | 61.6608 | 61.6837 | -61.4273 | -0.18768 | -0.004578 | 1.6434 | -0.21057 | -7.9697 | -0.23346 | -0.027466 | 1.8311 | 122.9416 | 122.8546 | 114.9353 | 122.9004 | 1.6434 | 122.8775 | 68.2068 | -0.23346 | 122.9004 | 1.6434 | 68.2068 | 114.9353 | 122.8775 | -123.0927 | -123.1384
1869.3281 | 123.0148 | -61.1801 | 61.7065 | -0.13382 | 0.022001 | 0.0069706 | 0.020478 | 0.055198 | -0.0019247 | 0.084845 | -59.5963 | 61.7065 | -61.3586 | -61.4182 | 53.7415 | 6.9489 | 61.7569 | 61.6516 | 61.6882 | -61.4273 | -0.17853 | 0 | 1.5839 | -0.23804 | -7.9651 | -0.24719 | -0.018311 | 1.7624 | 122.937 | 122.8317 | 114.9216 | 122.8867 | 1.5839 | 122.8683 | 68.129 | -0.24719 | 122.8867 | 1.5839 | 68.129 | 114.9216 | 122.8683 | -123.0652 | -123.1338
1870.3281 | 122.9965 | -61.1938 | 61.7065 | -0.39322 | 0.020292 | 0.0082522 | 0.019623 | 0.059043 | -0.0032065 | 0.086554 | -59.5917 | 61.6653 | -61.3678 | -61.3953 | 53.7735 | 7.0175 | 61.7615 | 61.6516 | 61.6699 | -61.3998 | -0.17395 | -0.041199 | 1.6022 | -0.20142 | -7.933 | -0.20599 | -0.036621 | 1.7761 | 122.9553 | 122.8455 | 114.9673 | 122.8592 | 1.6022 | 122.8638 | 68.2114 | -0.20599 | 122.8592 | 1.6022 | 68.2114 | 114.9673 | 122.8638 | -123.0743 | -123.1064
1871.3281 | 122.9919 | -61.1893 | 61.6791 | -0.1796 | 0.020506 | 0.0091068 | 0.018555 | 0.058402 | -0.00085669 | 0.086126 | -59.5963 | 61.6699 | -61.3861 | -61.4914 | 53.7872 | 7.0038 | 61.7432 | 61.6516 | 61.6837 | -61.4136 | -0.19684 | -0.009155 | 1.593 | -0.30212 | -7.8918 | -0.2243 | 0.004578 | 1.7899 | 122.9324 | 122.8409 | 114.9765 | 122.8592 | 1.593 | 122.8729 | 68.1931 | -0.2243 | 122.8592 | 1.593 | 68.1931 | 114.9765 | 122.8729 | -123.0652 | -123.0927
1872.3281 | 123.0194 | -61.1389 | 61.7065 | -0.35507 | 0.018797 | 0.0080386 | 0.017914 | 0.056907 | -0.0017111 | 0.085913 | -59.5596 | 61.6745 | -61.3861 | -61.409 | 53.7689 | 6.9992 | 61.7523 | 61.6653 | 61.6562 | -61.4044 | -0.24719 | -0.032043 | 1.5793 | -0.27008 | -7.9376 | -0.2655 | -0.050354 | 1.8265 | 122.8912 | 122.8043 | 114.9078 | 122.8134 | 1.5793 | 122.7951 | 68.1381 | -0.2655 | 122.8134 | 1.5793 | 68.1381 | 114.9078 | 122.7951 | -123.0927 | -123.111
1873.3281 | 123.1064 | -61.1755 | 61.6516 | -0.15671 | 0.019651 | 0.007825 | 0.017701 | 0.057762 | -0.0027793 | 0.086554 | -59.5047 | 61.615 | -61.3312 | -61.322 | 53.8651 | 7.1457 | 61.6379 | 61.7661 | 61.6562 | -61.3724 | -0.15564 | -0.036621 | 1.6708 | -0.14648 | -7.7866 | -0.19684 | 0.004578 | 1.8265 | 122.8134 | 122.9416 | 115.0406 | 122.7905 | 1.6708 | 122.8317 | 68.3212 | -0.19684 | 122.7905 | 1.6708 | 68.3212 | 115.0406 | 122.8317 | -122.9828 | -123.024
1874.3438 | 123.1064 | -61.171 | 61.6425 | -0.0041198 | 0.016874 | 0.011884 | 0.015565 | 0.056907 | -0.0010703 | 0.086126 | -59.5459 | 61.5875 | -61.3541 | -61.3312 | 53.8467 | 7.1548 | 61.5829 | 61.7477 | 61.615 | -61.3495 | -0.18311 | -0.054932 | 1.6251 | -0.16022 | -7.7957 | -0.17853 | -0.027466 | 1.8082 | 122.7539 | 122.9187 | 115.0177 | 122.7585 | 1.6251 | 122.7859 | 68.3258 | -0.17853 | 122.7585 | 1.6251 | 68.3258 | 115.0177 | 122.7859 | -122.9965 | -122.9919
1875.3281 | 123.0286 | -61.1343 | 61.734 | -0.30167 | 0.020292 | 0.0080386 | 0.020905 | 0.054984 | -0.0014975 | 0.084631 | -59.5779 | 61.6699 | -61.3632 | -61.3953 | 53.7735 | 7.0038 | 61.7706 | 61.6699 | 61.6653 | -61.3998 | -0.22888 | -0.064087 | 1.5564 | -0.26093 | -7.9605 | -0.2655 | -0.068665 | 1.7853 | 122.905 | 122.8043 | 114.9078 | 122.8043 | 1.5564 | 122.7997 | 68.1381 | -0.2655 | 122.8043 | 1.5564 | 68.1381 | 114.9078 | 122.7997 | -123.0972 | -123.1338
1876.3281 | 123.0103 | -61.1572 | 61.6745 | -0.20248 | 0.017942 | 0.011884 | 0.020905 | 0.056907 | -2.092e-06 | 0.084845 | -59.5459 | 61.6653 | -61.3724 | -61.377 | 53.801 | 7.0129 | 61.7569 | 61.6837 | 61.6928 | -61.3953 | -0.21515 | -0.009156 | 1.6113 | -0.21973 | -7.8735 | -0.23804 | 0.01831 | 1.8265 | 122.9141 | 122.8409 | 114.9582 | 122.8226 | 1.6113 | 122.85 | 68.1702 | -0.23804 | 122.8226 | 1.6113 | 68.1702 | 114.9582 | 122.85 | -123.0469 | -123.0698
1877.3281 | 123.0469 | -61.1618 | 61.6928 | -0.19485 | 0.020506 | 0.010602 | 0.01941 | 0.058189 | -0.00085669 | 0.085058 | -59.5093 | 61.6333 | -61.322 | -61.3403 | 53.833 | 7.0587 | 61.6928 | 61.7386 | 61.6562 | -61.3632 | -0.16022 | -0.059509 | 1.6525 | -0.17853 | -7.8598 | -0.20142 | -0.036621 | 1.8127 | 122.8546 | 122.9004 | 114.9948 | 122.7951 | 1.6525 | 122.818 | 68.2205 | -0.20142 | 122.7951 | 1.6525 | 68.2205 | 114.9948 | 122.818 | -123.0148 | -123.056
1878.3281 | 123.056 | -61.116 | 61.7111 | -0.19485 | 0.018156 | 0.009534 | 0.019196 | 0.057334 | -0.0021383 | 0.085486 | -59.4955 | 61.6516 | -61.3358 | -61.3083 | 53.8605 | 7.1274 | 61.6791 | 61.7615 | 61.6745 | -61.3632 | -0.21973 | -0.05951 | 1.6205 | -0.19226 | -7.8506 | -0.24719 | -0.036621 | 1.8402 | 122.7951 | 122.8775 | 114.9765 | 122.7676 | 1.6205 | 122.7905 | 68.2434 | -0.24719 | 122.7676 | 1.6205 | 68.2434 | 114.9765 | 122.7905 | -123.0469 | -123.0743
1879.3281 | 123.0789 | -61.1206 | 61.6974 | -0.14908 | 0.017301 | 0.0086796 | 0.018128 | 0.057121 | -0.0032065 | 0.086554 | -59.4864 | 61.615 | -61.3312 | -61.29 | 53.8605 | 7.1365 | 61.6608 | 61.8027 | 61.6562 | -61.3541 | -0.21057 | -0.082398 | 1.6342 | -0.16937 | -7.8369 | -0.23346 | -0.041199 | 1.8448 | 122.7814 | 122.9233 | 114.9811 | 122.7356 | 1.6342 | 122.7768 | 68.2571 | -0.23346 | 122.7356 | 1.6342 | 68.2571 | 114.9811 | 122.7768 | -123.0286 | -123.0515
1880.3281 | 123.0972 | -61.1114 | 61.6882 | -0.1033 | 0.017729 | 0.007825 | 0.018555 | 0.056053 | -0.0019247 | 0.085272 | -59.4955 | 61.6058 | -61.3403 | -61.29 | 53.8925 | 7.2556 | 61.5829 | 61.8073 | 61.6287 | -61.3495 | -0.22888 | -0.082397 | 1.6159 | -0.17853 | -7.7957 | -0.23804 | -0.059509 | 1.8448 | 122.6944 | 122.9187 | 115.004 | 122.7173 | 1.6159 | 122.7402 | 68.367 | -0.23804 | 122.7173 | 1.6159 | 68.367 | 115.004 | 122.7402 | -123.0286 | -123.0377
1881.3281 | 123.0652 | -61.1435 | 61.6653 | -0.15671 | 0.020719 | 0.010816 | 0.019837 | 0.056266 | -0.0021383 | 0.08634 | -59.4818 | 61.647 | -61.3495 | -61.3174 | 53.8513 | 7.2006 | 61.6608 | 61.7798 | 61.647 | -61.3815 | -0.20599 | -0.01831 | 1.6617 | -0.17395 | -7.814 | -0.23804 | -0.01831 | 1.8677 | 122.8043 | 122.9233 | 114.9948 | 122.7905 | 1.6617 | 122.7905 | 68.3441 | -0.23804 | 122.7905 | 1.6617 | 68.3441 | 114.9948 | 122.7905 | -123.0148 | -123.0469
1882.3281 | 123.1155 | -61.1206 | 61.6745 | -0.1796 | 0.018797 | 0.011884 | 0.01941 | 0.054771 | -0.0049155 | 0.085913 | -59.491 | 61.6104 | -61.3266 | -61.2991 | 53.8742 | 7.1503 | 61.6287 | 61.7844 | 61.6333 | -61.3495 | -0.20599 | -0.064087 | 1.6296 | -0.17853 | -7.8003 | -0.22888 | -0.041199 | 1.8356 | 122.7493 | 122.905 | 114.9948 | 122.731 | 1.6296 | 122.7539 | 68.2709 | -0.22888 | 122.731 | 1.6296 | 68.2709 | 114.9948 | 122.7539 | -123.0011 | -123.024
1883.3438 | 123.0606 | -61.1343 | 61.7065 | -0.17197 | 0.019438 | 0.0048342 | 0.021332 | 0.057548 | -0.0038473 | 0.086126 | -59.5093 | 61.6425 | -61.3266 | -61.322 | 53.8605 | 7.1136 | 61.702 | 61.734 | 61.6608 | -61.3358 | -0.19226 | -0.064087 | 1.6251 | -0.18768 | -7.8461 | -0.20142 | -0.045776 | 1.8173 | 122.8363 | 122.8683 | 114.9948 | 122.7768 | 1.6251 | 122.7951 | 68.248 | -0.20142 | 122.7768 | 1.6251 | 68.248 | 114.9948 | 122.7951 | -123.0331 | -123.0423
1884.3281 | 123.1384 | -61.116 | 61.6791 | 0.14084 | 0.017942 | 0.0071842 | 0.022828 | 0.055198 | -0.0029929 | 0.08634 | -59.5047 | 61.6058 | -61.3586 | -61.2762 | 53.9062 | 7.1411 | 61.5921 | 61.7889 | 61.6379 | -61.3358 | -0.24262 | -0.073242 | 1.6113 | -0.16022 | -7.7728 | -0.21973 | -0.041199 | 1.8539 | 122.7081 | 122.905 | 115.0223 | 122.7219 | 1.6113 | 122.7539 | 68.2571 | -0.21973 | 122.7219 | 1.6113 | 68.2571 | 115.0223 | 122.7539 | -123.0377 | -123.0148
1885.3281 | 123.1155 | -61.1252 | 61.6516 | -0.080414 | 0.01837 | -7.9006e-05 | 0.021973 | 0.05648 | -0.0010703 | 0.085058 | -59.4223 | 61.6425 | -61.3083 | -61.2579 | 53.8284 | 7.0862 | 61.5738 | 61.7752 | 61.6013 | -61.3403 | -0.18311 | -0.009155 | 1.7029 | -0.13275 | -7.8232 | -0.21515 | -0.050354 | 1.886 | 122.699 | 122.9004 | 114.9536 | 122.7676 | 1.7029 | 122.7264 | 68.2114 | -0.21515 | 122.7676 | 1.7029 | 68.2114 | 114.9536 | 122.7264 | -122.9599 | -122.9919
1886.3281 | 123.024 | -61.1069 | 61.6333 | -0.12619 | 0.020506 | 0.0076114 | 0.019837 | 0.054771 | -0.0010703 | 0.086554 | -59.5001 | 61.6058 | -61.3403 | -61.2625 | 53.8971 | 7.1915 | 61.5784 | 62.1735 | 61.6562 | -61.3174 | -0.23346 | -0.027466 | 1.6068 | -0.15564 | -7.7362 | -0.21057 | 0.022888 | 1.8402 | 122.6852 | 123.2803 | 115.004 | 122.7127 | 1.6068 | 122.7631 | 68.2983 | -0.21057 | 122.7127 | 1.6068 | 68.2983 | 115.004 | 122.7631 | -122.9736 | -122.9507
1887.3281 | 123.0972 | -61.1252 | 61.6699 | -0.011749 | 0.01837 | 0.0063296 | 0.018342 | 0.053489 | -0.0014975 | 0.088263 | -59.5413 | 61.6104 | -61.3632 | -61.3403 | 53.833 | 7.0633 | 61.6058 | 61.7432 | 61.6379 | -61.3678 | -0.23804 | -0.059509 | 1.5839 | -0.21515 | -7.8369 | -0.24262 | -0.032044 | 1.8219 | 122.731 | 122.8683 | 114.9582 | 122.7356 | 1.5839 | 122.7631 | 68.1885 | -0.24262 | 122.7356 | 1.5839 | 68.1885 | 114.9582 | 122.7631 | -123.0331 | -123.0377
1888.3281 | 123.0698 | -61.1343 | 61.6379 | 0.064545 | 0.018156 | 0.0054752 | 0.018128 | 0.053489 | -0.0025657 | 0.086981 | -59.5642 | 61.6058 | -61.3632 | -61.3403 | 53.801 | 7.0404 | 61.6013 | 61.734 | 61.6058 | -61.3541 | -0.22888 | -0.032043 | 1.5701 | -0.20599 | -7.8369 | -0.21973 | -0.032043 | 1.799 | 122.7356 | 122.8683 | 114.9353 | 122.7402 | 1.5701 | 122.7402 | 68.1747 | -0.21973 | 122.7402 | 1.5701 | 68.1747 | 114.9353 | 122.7402 | -123.0011 | -122.9919
1889.3281 | 123.1705 | -61.1298 | 61.6425 | 0.0035097 | 0.017942 | 0.011457 | 0.020051 | 0.053062 | -0.0042747 | 0.086767 | -59.5596 | 61.6013 | -61.3632 | -61.3266 | 53.8193 | 7.0358 | 61.5921 | 61.7615 | 61.6379 | -61.3495 | -0.23346 | -0.041199 | 1.5701 | -0.19684 | -7.8232 | -0.21973 | -0.004578 | 1.8036 | 122.7219 | 122.8912 | 114.949 | 122.731 | 1.5701 | 122.7676 | 68.1656 | -0.21973 | 122.731 | 1.5701 | 68.1656 | 114.949 | 122.7676 | -123.0057 | -122.9919
1890.3281 | 123.1064 | -61.1298 | 61.6562 | -0.027008 | 0.019651 | 0.0076114 | 0.020905 | 0.054771 | -0.00021569 | 0.085058 | -59.5688 | 61.6013 | -61.3449 | -61.322 | 53.8147 | 7.0084 | 61.6013 | 61.7294 | 61.6058 | -61.3724 | -0.21515 | -0.054932 | 1.561 | -0.19226 | -7.8415 | -0.24261 | -0.050354 | 1.7761 | 122.731 | 122.8592 | 114.9445 | 122.731 | 1.561 | 122.7356 | 68.1381 | -0.24261 | 122.731 | 1.561 | 68.1381 | 114.9445 | 122.7356 | -123.0011 | -123.0286
1891.3281 | 123.0881 | -61.1572 | 61.6287 | 0.026398 | 0.020719 | 0.009534 | 0.018555 | 0.054344 | -0.0014975 | 0.085486 | -59.5779 | 61.5738 | -61.3861 | -61.3586 | 53.801 | 7.0175 | 61.6013 | 61.7157 | 61.6196 | -61.3586 | -0.22888 | -0.054931 | 1.5793 | -0.20142 | -7.8278 | -0.20142 | -0.009155 | 1.8082 | 122.7585 | 122.8729 | 114.9582 | 122.731 | 1.5793 | 122.7768 | 68.1747 | -0.20142 | 122.731 | 1.5793 | 68.1747 | 114.9582 | 122.7768 | -123.0148 | -122.9874
1892.3281 | 123.0881 | -61.1664 | 61.6608 | 0.018768 | 0.019651 | 0.010175 | 0.018128 | 0.055625 | -0.0025657 | 0.083777 | -59.5779 | 61.5921 | -61.3541 | -61.3586 | 53.7598 | 6.9809 | 61.5967 | 61.6928 | 61.6058 | -61.3907 | -0.18768 | -0.068665 | 1.5884 | -0.19226 | -7.901 | -0.2243 | -0.054932 | 1.7761 | 122.7631 | 122.8592 | 114.9261 | 122.7585 | 1.5884 | 122.7722 | 68.1473 | -0.2243 | 122.7585 | 1.5884 | 68.1473 | 114.9261 | 122.7722 | -123.0148 | -123.0515
1893.3281 | 123.0835 | -61.1343 | 61.6287 | 0.095062 | 0.02136 | 0.012525 | 0.020264 | 0.054771 | -0.0025657 | 0.08634 | -59.6054 | 61.5601 | -61.3586 | -61.3724 | 53.7552 | 6.9809 | 61.6196 | 61.6974 | 61.6333 | -61.3815 | -0.22431 | -0.068664 | 1.5289 | -0.23804 | -7.8735 | -0.24719 | 0.004578 | 1.7532 | 122.7539 | 122.8317 | 114.8895 | 122.6944 | 1.5289 | 122.7676 | 68.1152 | -0.24719 | 122.6944 | 1.5289 | 68.1152 | 114.8895 | 122.7676 | -122.9874 | -123.0103
1894.3281 | 123.0835 | -61.1435 | 61.647 | 0.18662 | 0.019224 | 0.0059024 | 0.019196 | 0.055412 | -0.0023519 | 0.086554 | -59.5367 | 61.5829 | -61.3541 | -61.3586 | 53.7689 | 7.0129 | 61.5921 | 61.6837 | 61.5921 | -61.3632 | -0.21057 | -0.064087 | 1.6068 | -0.21515 | -7.8781 | -0.21973 | -0.054932 | 1.8173 | 122.7356 | 122.8271 | 114.9124 | 122.7264 | 1.6068 | 122.7356 | 68.1564 | -0.21973 | 122.7264 | 1.6068 | 68.1564 | 114.9124 | 122.7356 | -123.0011 | -123.0103
1895.3281 | 123.0881 | -61.1389 | 61.647 | 0.064545 | 0.019438 | 0.010602 | 0.021973 | 0.055839 | -0.0034201 | 0.085699 | -59.5596 | 61.6196 | -61.3541 | -61.2946 | 53.9291 | 7.0404 | 61.5326 | 61.647 | 61.5829 | -61.3678 | -0.21515 | -0.027466 | 1.5793 | -0.15564 | -7.7179 | -0.22888 | -0.064087 | 1.7944 | 122.6715 | 122.7859 | 115.0681 | 122.7585 | 1.5793 | 122.7219 | 68.1793 | -0.22888 | 122.7585 | 1.5793 | 68.1793 | 115.0681 | 122.7219 | -123.0011 | -123.0148
1896.3281 | 123.1064 | -61.1343 | 61.6562 | 0.011139 | 0.017942 | 0.0080386 | 0.016846 | 0.055198 | -0.0019247 | 0.085272 | -59.6008 | 61.6013 | -61.3541 | -61.3403 | 53.7598 | 6.9992 | 61.615 | 61.702 | 61.6058 | -61.3495 | -0.21973 | -0.054932 | 1.5335 | -0.20599 | -7.8964 | -0.21515 | -0.050354 | 1.7532 | 122.7493 | 122.8363 | 114.8941 | 122.7356 | 1.5335 | 122.7402 | 68.1335 | -0.21515 | 122.7356 | 1.5335 | 68.1335 | 114.8941 | 122.7402 | -123.0103 | -123.0057
1897.3281 | 123.0881 | -61.1526 | 61.6516 | -0.11093 | 0.020506 | 0.0086796 | 0.019196 | 0.054344 | -0.00064309 | 0.086554 | -59.61 | 61.5829 | -61.3541 | -61.3724 | 53.7506 | 6.9489 | 61.6104 | 61.6882 | 61.615 | -61.3953 | -0.20142 | -0.068664 | 1.5427 | -0.21973 | -7.901 | -0.24262 | -0.036621 | 1.7441 | 122.7631 | 122.8409 | 114.9033 | 122.7356 | 1.5427 | 122.7676 | 68.1015 | -0.24262 | 122.7356 | 1.5427 | 68.1015 | 114.9033 | 122.7676 | -123.0057 | -123.0469
1898.3281 | 123.0698 | -61.1572 | 61.6516 | 0.087433 | 0.020719 | 0.0084658 | 0.019623 | 0.051139 | -0.00021569 | 0.084631 | -59.5642 | 61.5875 | -61.3449 | -61.4456 | 53.6957 | 6.9809 | 61.5692 | 61.7111 | 61.6013 | -61.3815 | -0.18768 | -0.064087 | 1.593 | -0.28839 | -7.9559 | -0.2243 | -0.050354 | 1.7807 | 122.7264 | 122.8683 | 114.8529 | 122.7448 | 1.593 | 122.7585 | 68.1381 | -0.2243 | 122.7448 | 1.593 | 68.1381 | 114.8529 | 122.7585 | -122.9965 | -123.0331
1899.3281 | 122.9553 | -61.1206 | 61.7157 | -0.18723 | 0.019438 | 0.0097476 | 0.022614 | 0.053916 | -0.0017111 | 0.085486 | -59.5642 | 61.6745 | -61.3632 | -61.3632 | 53.7277 | 6.9214 | 61.853 | 61.8988 | 61.6928 | -61.3403 | -0.24262 | -0.041198 | 1.5564 | -0.24262 | -7.988 | -0.21973 | -0.022888 | 1.799 | 122.9736 | 123.0194 | 114.8483 | 122.7951 | 1.5564 | 122.8134 | 68.042 | -0.21973 | 122.7951 | 1.5564 | 68.042 | 114.8483 | 122.8134 | -123.0789 | -123.056
1900.3281 | 123.0881 | -61.1435 | 61.6745 | 0.12558 | 0.019438 | 0.011884 | 0.019196 | 0.057334 | -0.0012839 | 0.087408 | -59.5917 | 61.615 | -61.3358 | -61.3678 | 53.7506 | 6.9717 | 61.5875 | 61.6837 | 61.6241 | -61.3495 | -0.19226 | -0.05951 | 1.5518 | -0.2243 | -7.9239 | -0.20599 | -0.050354 | 1.7441 | 122.731 | 122.8271 | 114.8941 | 122.7585 | 1.5518 | 122.7676 | 68.1152 | -0.20599 | 122.7585 | 1.5518 | 68.1152 | 114.8941 | 122.7676 | -123.0103 | -123.024
1901.3281 | 123.1064 | -61.1572 | 61.6653 | 0.2095 | 0.022642 | 0.011884 | 0.023255 | 0.056693 | -0.0021383 | 0.085486 | -59.5093 | 61.5875 | -61.3586 | -61.3083 | 53.7827 | 7.0084 | 61.5234 | 61.734 | 61.5784 | -61.3815 | -0.20142 | -0.07782 | 1.648 | -0.15106 | -7.8827 | -0.2243 | -0.086975 | 1.8494 | 122.6807 | 122.8912 | 114.9399 | 122.7448 | 1.648 | 122.7356 | 68.1656 | -0.2243 | 122.7448 | 1.648 | 68.1656 | 114.9399 | 122.7356 | -123.024 | -123.0469
1902.3281 | 123.0881 | -61.1298 | 61.6425 | 0.2095 | 0.01837 | 0.012525 | 0.02176 | 0.055198 | -0.00064309 | 0.086126 | -59.5596 | 61.5784 | -61.3449 | -61.3312 | 53.7643 | 6.9946 | 61.5463 | 61.7065 | 61.6058 | -61.3632 | -0.21515 | -0.064087 | 1.5701 | -0.20142 | -7.8781 | -0.23346 | -0.036621 | 1.7853 | 122.6761 | 122.8363 | 114.8941 | 122.7081 | 1.5701 | 122.7356 | 68.1244 | -0.23346 | 122.7081 | 1.5701 | 68.1244 | 114.8941 | 122.7356 | -122.9874 | -123.0057
1903.3281 | 123.0835 | -61.1252 | 61.6608 | 0.12558 | 0.021147 | 0.013593 | 0.018769 | 0.056907 | -0.0012839 | 0.086767 | -59.5734 | 61.6058 | -61.3449 | -61.3541 | 53.7506 | 6.9534 | 61.5921 | 61.702 | 61.5967 | -61.3953 | -0.21973 | -0.054932 | 1.5518 | -0.22888 | -7.9102 | -0.27008 | -0.064087 | 1.7715 | 122.7173 | 122.8271 | 114.8758 | 122.731 | 1.5518 | 122.7219 | 68.0786 | -0.27008 | 122.731 | 1.5518 | 68.0786 | 114.8758 | 122.7219 | -123.0057 | -123.056
1904.3281 | 123.0698 | -61.1252 | 61.6562 | 0.0035097 | 0.018583 | 0.014875 | 0.020692 | 0.058189 | -0.0059835 | 0.087195 | -59.5825 | 61.6104 | -61.3358 | -61.4182 | 53.7048 | 6.9626 | 61.5646 | 61.7157 | 61.5875 | -61.3586 | -0.21057 | -0.045776 | 1.5427 | -0.29297 | -7.9514 | -0.23346 | -0.068665 | 1.7532 | 122.6898 | 122.8409 | 114.83 | 122.7356 | 1.5427 | 122.7127 | 68.0878 | -0.23346 | 122.7356 | 1.5427 | 68.0878 | 114.83 | 122.7127 | -122.9919 | -123.0148
1905.3281 | 123.0789 | -61.1435 | 61.6653 | 0.14847 | 0.020506 | 0.0091068 | 0.020478 | 0.056053 | -0.0014975 | 0.085272 | -59.5596 | 61.615 | -61.3403 | -61.3449 | 53.7323 | 6.958 | 61.6196 | 61.702 | 61.6058 | -61.3678 | -0.19684 | -0.050354 | 1.5839 | -0.20142 | -7.933 | -0.2243 | -0.059509 | 1.7807 | 122.7631 | 122.8455 | 114.8758 | 122.7585 | 1.5839 | 122.7493 | 68.1015 | -0.2243 | 122.7585 | 1.5839 | 68.1015 | 114.8758 | 122.7493 | -123.0057 | -123.0331
1906.3281 | 123.0789 | -61.1206 | 61.6562 | 0.11795 | 0.019224 | 0.010602 | 0.017487 | 0.055412 | -0.0017111 | 0.087408 | -59.5688 | 61.5921 | -61.3632 | -61.3495 | 53.7186 | 6.9397 | 61.6104 | 61.7111 | 61.5921 | -61.3724 | -0.24262 | -0.064087 | 1.5518 | -0.22888 | -7.9376 | -0.25177 | -0.064087 | 1.7944 | 122.731 | 122.8317 | 114.8392 | 122.7127 | 1.5518 | 122.7127 | 68.0603 | -0.25177 | 122.7127 | 1.5518 | 68.0603 | 114.8392 | 122.7127 | -123.0194 | -123.0286
1907.3281 | 123.0881 | -61.1343 | 61.6333 | 0.17136 | 0.022215 | 0.0084658 | 0.019623 | 0.055198 | -0.0023519 | 0.085913 | -59.5322 | 61.6058 | -61.3266 | -61.3358 | 53.7277 | 6.9672 | 61.5646 | 61.7294 | 61.5967 | -61.3678 | -0.19226 | -0.027466 | 1.6022 | -0.20142 | -7.9056 | -0.23346 | -0.036621 | 1.7944 | 122.699 | 122.8638 | 114.8621 | 122.7402 | 1.6022 | 122.731 | 68.1015 | -0.23346 | 122.7402 | 1.6022 | 68.1015 | 114.8621 | 122.731 | -122.9599 | -123.0011
1908.3438 | 123.1522 | -61.1206 | 61.6653 | -0.027008 | 0.01901 | 0.011243 | 0.019196 | 0.055198 | -0.0027793 | 0.085486 | -59.5505 | 61.6379 | -61.322 | -61.3129 | 53.7781 | 6.9214 | 61.615 | 61.7981 | 61.6241 | -61.3403 | -0.20142 | -0.027466 | 1.5701 | -0.19226 | -7.8873 | -0.21973 | -0.041198 | 1.7715 | 122.7356 | 122.9187 | 114.8987 | 122.7585 | 1.5701 | 122.7448 | 68.042 | -0.21973 | 122.7585 | 1.5701 | 68.042 | 114.8987 | 122.7448 | -122.9874 | -123.0057
1909.3281 | 123.0927 | -61.116 | 61.6653 | 0.2095 | 0.01837 | 0.0080386 | 0.022614 | 0.055412 | -0.0014975 | 0.08634 | -59.5093 | 61.6013 | -61.3449 | -61.3129 | 53.7277 | 6.9168 | 61.528 | 61.7432 | 61.6058 | -61.3586 | -0.22888 | -0.064087 | 1.6068 | -0.19684 | -7.9376 | -0.24262 | -0.059509 | 1.8356 | 122.644 | 122.8592 | 114.8438 | 122.7173 | 1.6068 | 122.7219 | 68.0328 | -0.24262 | 122.7173 | 1.6068 | 68.0328 | 114.8438 | 122.7219 | -123.0103 | -123.024
1910.3281 | 123.0789 | -61.1298 | 61.6699 | 0.17899 | 0.020719 | 0.013166 | 0.018342 | 0.056693 | -0.0021383 | 0.085913 | -59.5413 | 61.6104 | -61.3358 | -61.3358 | 53.7186 | 6.9351 | 61.6013 | 61.7249 | 61.6104 | -61.3678 | -0.20599 | -0.059509 | 1.5884 | -0.20599 | -7.9514 | -0.23804 | -0.059509 | 1.7944 | 122.731 | 122.8546 | 114.8483 | 122.7402 | 1.5884 | 122.7402 | 68.0649 | -0.23804 | 122.7402 | 1.5884 | 68.0649 | 114.8483 | 122.7402 | -123.0057 | -123.0377
1911.3281 | 123.0652 | -61.1526 | 61.6608 | 0.17136 | 0.022215 | 0.0091068 | 0.01941 | 0.054771 | -0.0019247 | 0.086554 | -59.5184 | 61.6013 | -61.3266 | -61.3312 | 53.7277 | 6.926 | 61.5875 | 61.7157 | 61.5921 | -61.3678 | -0.17395 | -0.05951 | 1.6342 | -0.17853 | -7.933 | -0.21515 | -0.068665 | 1.8082 | 122.7402 | 122.8683 | 114.8804 | 122.7539 | 1.6342 | 122.7448 | 68.0786 | -0.21515 | 122.7539 | 1.6342 | 68.0786 | 114.8804 | 122.7448 | -122.9874 | -123.0286
1912.3281 | 123.0789 | -61.1343 | 61.6562 | 0.17136 | 0.021787 | 0.010175 | 0.020692 | 0.05648 | -0.0010703 | 0.08634 | -59.5322 | 61.6104 | -61.3495 | -61.3312 | 53.7506 | 6.8893 | 61.5692 | 61.734 | 61.6013 | -61.3358 | -0.21515 | -0.045776 | 1.6022 | -0.19684 | -7.9056 | -0.20142 | -0.054932 | 1.8173 | 122.7036 | 122.8683 | 114.8849 | 122.7448 | 1.6022 | 122.7356 | 68.0237 | -0.20142 | 122.7448 | 1.6022 | 68.0237 | 114.8849 | 122.7356 | -123.0057 | -122.9919
1913.3438 | 123.0698 | -61.1664 | 61.7203 | -0.11093 | 0.021147 | 0.011243 | 0.027527 | 0.055198 | -0.0021383 | 0.085058 | -59.5093 | 61.734 | -61.3495 | -61.3129 | 53.7231 | 6.9443 | 61.7294 | 61.7111 | 61.6745 | -61.4044 | -0.18311 | 0.013733 | 1.6571 | -0.14648 | -7.9971 | -0.23804 | -0.045776 | 1.8402 | 122.8958 | 122.8775 | 114.8895 | 122.9004 | 1.6571 | 122.8409 | 68.1107 | -0.23804 | 122.9004 | 1.6571 | 68.1107 | 114.8895 | 122.8409 | -123.0698 | -123.1247
1914.3281 | 123.111 | -61.1114 | 61.6608 | 0.17899 | 0.021147 | 0.0097476 | 0.020051 | 0.057548 | -0.0023519 | 0.085272 | -59.523 | 61.6379 | -61.3312 | -61.3266 | 53.7277 | 7.0267 | 61.5555 | 61.7569 | 61.6241 | -61.3495 | -0.21973 | -0.022889 | 1.5884 | -0.21515 | -7.933 | -0.23804 | -0.036621 | 1.8082 | 122.6669 | 122.8683 | 114.8392 | 122.7493 | 1.5884 | 122.7356 | 68.1381 | -0.23804 | 122.7493 | 1.5884 | 68.1381 | 114.8392 | 122.7356 | -122.9919 | -123.0103
1915.3281 | 123.1201 | -61.1252 | 61.6516 | 0.21713 | 0.023283 | 0.016156 | 0.024323 | 0.056907 | -0.00085669 | 0.084845 | -59.5001 | 61.6425 | -61.3495 | -61.2991 | 53.746 | 6.9717 | 61.5463 | 61.7432 | 61.615 | -61.3541 | -0.2243 | -0.009155 | 1.6251 | -0.17395 | -7.9056 | -0.22888 | -0.036621 | 1.8494 | 122.6715 | 122.8683 | 114.8712 | 122.7676 | 1.6251 | 122.7402 | 68.0969 | -0.22888 | 122.7676 | 1.6251 | 68.0969 | 114.8712 | 122.7402 | -123.0011 | -123.0057
1916.3281 | 123.1247 | -61.1069 | 61.647 | 0.19424 | 0.01901 | 0.010175 | 0.021119 | 0.057762 | -0.0027793 | 0.085913 | -59.5047 | 61.615 | -61.3358 | -61.3037 | 53.7277 | 6.9717 | 61.5463 | 61.7523 | 61.615 | -61.3358 | -0.22888 | -0.032044 | 1.6022 | -0.19684 | -7.9193 | -0.22888 | -0.032044 | 1.8311 | 122.6532 | 122.8592 | 114.8346 | 122.7219 | 1.6022 | 122.7219 | 68.0786 | -0.22888 | 122.7219 | 1.6022 | 68.0786 | 114.8346 | 122.7219 | -122.9828 | -122.9828
1917.3281 | 123.0652 | -61.1114 | 61.6699 | 0.20187 | 0.022001 | 0.0076114 | 0.020264 | 0.057762 | 0.00042511 | 0.085699 | -59.5459 | 61.615 | -61.3449 | -61.3358 | 53.7094 | 6.9077 | 61.5967 | 61.7294 | 61.615 | -61.3678 | -0.23346 | -0.054932 | 1.5656 | -0.2243 | -7.9605 | -0.25635 | -0.054932 | 1.799 | 122.7081 | 122.8409 | 114.8209 | 122.7264 | 1.5656 | 122.7264 | 68.0191 | -0.25635 | 122.7264 | 1.5656 | 68.0191 | 114.8209 | 122.7264 | -123.0148 | -123.0377
1918.3438 | 123.0789 | -61.1023 | 61.7065 | -0.17197 | 0.020292 | 0.0099612 | 0.021546 | 0.055625 | -0.0036337 | 0.084845 | -59.4864 | 61.6608 | -61.2717 | -61.2808 | 53.7827 | 6.9809 | 61.6745 | 61.7981 | 61.6516 | -61.3495 | -0.16937 | -0.045776 | 1.6159 | -0.17853 | -7.9239 | -0.24719 | -0.054932 | 1.7853 | 122.7768 | 122.9004 | 114.8849 | 122.7631 | 1.6159 | 122.7539 | 68.0832 | -0.24719 | 122.7631 | 1.6159 | 68.0832 | 114.8849 | 122.7539 | -122.9782 | -123.056
1919.3281 | 123.0972 | -61.1847 | 61.6653 | 0.20187 | 0.021574 | 0.009534 | 0.022401 | 0.05413 | -0.00085669 | 0.087195 | -59.5367 | 61.615 | -61.3449 | -61.3403 | 53.7048 | 7.0312 | 61.5692 | 61.734 | 61.5967 | -61.3678 | -0.16022 | -0.050354 | 1.6479 | -0.15564 | -7.9605 | -0.18311 | -0.068664 | 1.8082 | 122.7539 | 122.9187 | 114.8895 | 122.7997 | 1.6479 | 122.7814 | 68.2159 | -0.18311 | 122.7997 | 1.6479 | 68.2159 | 114.8895 | 122.7814 | -123.0103 | -123.0331
1920.3281 | 123.1018 | -61.1252 | 61.6608 | 0.16373 | 0.020292 | 0.012097 | 0.022187 | 0.056053 | -0.0029929 | 0.087408 | -59.5276 | 61.6196 | -61.3449 | -61.3312 | 53.7277 | 7.0175 | 61.5692 | 61.7294 | 61.615 | -61.3449 | -0.21973 | -0.041199 | 1.5976 | -0.20599 | -7.933 | -0.21973 | -0.045777 | 1.8173 | 122.6944 | 122.8546 | 114.8529 | 122.7448 | 1.5976 | 122.7402 | 68.1427 | -0.21973 | 122.7448 | 1.5976 | 68.1427 | 114.8529 | 122.7402 | -123.0057 | -123.0057
1921.3438 | 122.9965 | -61.1664 | 61.6791 | 0.049286 | 0.022856 | 0.015088 | 0.02945 | 0.059684 | -0.0021383 | 0.085272 | -59.5459 | 61.7477 | -61.3403 | -61.3541 | 53.6179 | 6.9122 | 61.7111 | 61.6699 | 61.6608 | -61.4273 | -0.17395 | 0.068665 | 1.6205 | -0.18768 | -8.0612 | -0.26093 | -0.01831 | 1.7944 | 122.8775 | 122.8363 | 114.7842 | 122.9141 | 1.6205 | 122.8271 | 68.0786 | -0.26093 | 122.9141 | 1.6205 | 68.0786 | 114.7842 | 122.8271 | -123.0194 | -123.1064
1922.3281 | 123.0881 | -61.1343 | 61.6333 | 0.20187 | 0.020078 | 0.009534 | 0.022187 | 0.059043 | -2.092e-06 | 0.087622 | -59.5505 | 61.6013 | -61.3541 | -61.3312 | 53.7186 | 7.0175 | 61.5509 | 61.7477 | 61.6333 | -61.3541 | -0.21973 | -0.032044 | 1.5839 | -0.19684 | -7.9147 | -0.21973 | 0 | 1.8036 | 122.6852 | 122.8821 | 114.8529 | 122.7356 | 1.5839 | 122.7676 | 68.1519 | -0.21973 | 122.7356 | 1.5839 | 68.1519 | 114.8529 | 122.7676 | -122.9874 | -122.9874
1923.3438 | 123.1018 | -61.0977 | 61.6699 | -0.20248 | 0.021574 | 0.0088932 | 0.021119 | 0.057121 | -0.0023519 | 0.087835 | -59.523 | 61.6196 | -61.3358 | -61.2671 | 53.801 | 7.0541 | 61.6196 | 61.8301 | 61.6333 | -61.3541 | -0.23804 | -0.050354 | 1.5747 | -0.16937 | -7.869 | -0.25635 | -0.036621 | 1.8127 | 122.7173 | 122.9279 | 114.8987 | 122.7173 | 1.5747 | 122.731 | 68.1519 | -0.25635 | 122.7173 | 1.5747 | 68.1519 | 114.8987 | 122.731 | -123.0057 | -123.024
1924.3281 | 123.056 | -61.1526 | 61.6745 | 0.19424 | 0.020933 | 0.0084658 | 0.021119 | 0.057334 | -0.0032065 | 0.086126 | -59.5551 | 61.5921 | -61.3586 | -61.3678 | 53.6911 | 6.9992 | 61.5875 | 61.7065 | 61.6241 | -61.3495 | -0.20599 | -0.082398 | 1.5976 | -0.21515 | -7.9834 | -0.19684 | -0.050354 | 1.8036 | 122.7402 | 122.8592 | 114.8438 | 122.7448 | 1.5976 | 122.7768 | 68.1519 | -0.19684 | 122.7448 | 1.5976 | 68.1519 | 114.8438 | 122.7768 | -123.0331 | -123.024
1925.3281 | 123.0881 | -61.1389 | 61.6653 | 0.23239 | 0.019438 | 0.012097 | 0.021119 | 0.053703 | -0.0021383 | 0.086767 | -59.5459 | 61.6013 | -61.3266 | -61.3586 | 53.6774 | 7.0404 | 61.5875 | 61.7157 | 61.6104 | -61.3815 | -0.18768 | -0.064087 | 1.593 | -0.21973 | -7.988 | -0.24262 | -0.054931 | 1.7807 | 122.7264 | 122.8546 | 114.8163 | 122.7402 | 1.593 | 122.7493 | 68.1793 | -0.24262 | 122.7402 | 1.593 | 68.1793 | 114.8163 | 122.7493 | -122.9919 | -123.0469
1926.3281 | 123.0515 | -61.1389 | 61.6562 | 0.17136 | 0.019865 | 0.013593 | 0.022187 | 0.056053 | -0.00064309 | 0.086126 | -59.5596 | 61.5829 | -61.3632 | -61.3541 | 53.6682 | 7.0816 | 61.5738 | 61.7203 | 61.615 | -61.3907 | -0.2243 | -0.073242 | 1.5793 | -0.21515 | -7.988 | -0.25177 | -0.041199 | 1.8036 | 122.7127 | 122.8592 | 114.8071 | 122.7219 | 1.5793 | 122.7539 | 68.2205 | -0.25177 | 122.7219 | 1.5793 | 68.2205 | 114.8071 | 122.7539 | -123.0194 | -123.0469
1927.3281 | 123.0972 | -61.1389 | 61.6699 | 0.17899 | 0.017729 | 0.010816 | 0.021546 | 0.054557 | -0.0012839 | 0.086126 | -59.5413 | 61.615 | -61.3678 | -61.3403 | 53.6682 | 7.1045 | 61.5646 | 61.7249 | 61.5829 | -61.3861 | -0.22888 | -0.054932 | 1.5976 | -0.20142 | -8.0017 | -0.24719 | -0.086975 | 1.8265 | 122.7036 | 122.8638 | 114.8071 | 122.7539 | 1.5976 | 122.7219 | 68.2434 | -0.24719 | 122.7539 | 1.5976 | 68.2434 | 114.8071 | 122.7219 | -123.0377 | -123.056
1928.3281 | 123.1338 | -61.1114 | 61.647 | 0.24002 | 0.021574 | 0.012311 | 0.022614 | 0.056053 | -0.0019247 | 0.087408 | -59.523 | 61.6196 | -61.3541 | -61.2991 | 53.7003 | 7.0953 | 61.5189 | 61.7569 | 61.5921 | -61.3678 | -0.24262 | -0.027466 | 1.5884 | -0.18768 | -7.9468 | -0.25635 | -0.054932 | 1.8311 | 122.6303 | 122.8683 | 114.8117 | 122.731 | 1.5884 | 122.7036 | 68.2068 | -0.25635 | 122.731 | 1.5884 | 68.2068 | 114.8117 | 122.7036 | -123.0011 | -123.0148
1929.3281 | 123.0972 | -61.0931 | 61.6608 | 0.20187 | 0.01837 | 0.011884 | 0.022828 | 0.055198 | -0.0029929 | 0.084417 | -59.5459 | 61.615 | -61.3632 | -61.3266 | 53.6728 | 7.0221 | 61.5738 | 61.7432 | 61.6333 | -61.3724 | -0.27008 | -0.045777 | 1.5472 | -0.23346 | -7.988 | -0.27923 | -0.027466 | 1.8173 | 122.6669 | 122.8363 | 114.7659 | 122.7081 | 1.5472 | 122.7264 | 68.1152 | -0.27923 | 122.7081 | 1.5472 | 68.1152 | 114.7659 | 122.7264 | -123.024 | -123.0331
1930.3281 | 123.0789 | -61.1252 | 61.647 | 0.17899 | 0.020078 | 0.0063296 | 0.02176 | 0.056693 | -0.0025657 | 0.085699 | -59.5184 | 61.6104 | -61.3449 | -61.322 | 53.6591 | 7.0358 | 61.5509 | 61.7477 | 61.5921 | -61.3358 | -0.21973 | -0.036621 | 1.6067 | -0.19684 | -7.988 | -0.21057 | -0.054932 | 1.8265 | 122.6761 | 122.8729 | 114.7842 | 122.7356 | 1.6067 | 122.7173 | 68.161 | -0.21057 | 122.7356 | 1.6067 | 68.161 | 114.7842 | 122.7173 | -122.9919 | -122.9828
1931.3281 | 123.0789 | -61.1252 | 61.6699 | 0.12558 | 0.020078 | 0.0097476 | 0.020692 | 0.056053 | -0.0021383 | 0.086554 | -59.5551 | 61.6241 | -61.3449 | -61.3586 | 53.6499 | 6.9901 | 61.6241 | 61.7249 | 61.6379 | -61.3678 | -0.21973 | -0.045776 | 1.5701 | -0.23346 | -8.02 | -0.24262 | -0.032044 | 1.7899 | 122.7493 | 122.85 | 114.7751 | 122.7493 | 1.5701 | 122.7631 | 68.1152 | -0.24262 | 122.7493 | 1.5701 | 68.1152 | 114.7751 | 122.7631 | -123.0148 | -123.0377
1932.3281 | 123.0881 | -61.0748 | 61.6699 | 0.20187 | 0.018583 | 0.011884 | 0.021332 | 0.05413 | -0.0017111 | 0.086981 | -59.5276 | 61.6562 | -61.3495 | -61.322 | 53.714 | 6.9992 | 61.6104 | 61.7249 | 61.6241 | -61.3541 | -0.27466 | -0.013733 | 1.5472 | -0.24719 | -7.9559 | -0.27924 | -0.045776 | 1.8219 | 122.6852 | 122.7997 | 114.7888 | 122.731 | 1.5472 | 122.699 | 68.074 | -0.27924 | 122.731 | 1.5472 | 68.074 | 114.7888 | 122.699 | -123.0194 | -123.024
1933.3281 | 123.0743 | -61.1206 | 61.6791 | 0.14847 | 0.017515 | 0.0086796 | 0.020692 | 0.055839 | -0.0014975 | 0.084631 | -59.523 | 61.6104 | -61.3266 | -61.3266 | 53.6957 | 6.9626 | 61.5829 | 61.7203 | 61.6196 | -61.3541 | -0.20599 | -0.068664 | 1.5976 | -0.20599 | -7.9834 | -0.23346 | -0.059509 | 1.8036 | 122.7036 | 122.8409 | 114.8163 | 122.731 | 1.5976 | 122.7402 | 68.0832 | -0.23346 | 122.731 | 1.5976 | 68.0832 | 114.8163 | 122.7402 | -123.0057 | -123.0331
1934.3281 | 123.0789 | -61.116 | 61.6699 | 0.20187 | 0.018797 | 0.014234 | 0.02411 | 0.056053 | -0.0025657 | 0.087835 | -59.5413 | 61.6196 | -61.3495 | -61.322 | 53.6865 | 6.9443 | 61.5555 | 61.734 | 61.5875 | -61.3541 | -0.23346 | -0.050354 | 1.5747 | -0.20599 | -7.9834 | -0.23804 | -0.082398 | 1.8082 | 122.6715 | 122.85 | 114.8026 | 122.7356 | 1.5747 | 122.7036 | 68.0603 | -0.23804 | 122.7356 | 1.5747 | 68.0603 | 114.8026 | 122.7036 | -123.0194 | -123.024
1935.3281 | 123.111 | -61.1252 | 61.6516 | 0.27817 | 0.019865 | 0.0093204 | 0.022828 | 0.057975 | -0.0025657 | 0.088049 | -59.3948 | 61.615 | -61.3495 | -61.2854 | 53.7323 | 7.0084 | 61.5326 | 61.7569 | 61.6104 | -61.3541 | -0.2243 | -0.036621 | 1.7303 | -0.16022 | -7.9193 | -0.22888 | -0.041198 | 1.9547 | 122.6578 | 122.8821 | 114.8575 | 122.7402 | 1.7303 | 122.7356 | 68.1335 | -0.22888 | 122.7402 | 1.7303 | 68.1335 | 114.8575 | 122.7356 | -123.0011 | -123.0057
1936.3281 | 123.111 | -61.1252 | 61.6882 | 0.19424 | 0.020719 | 0.013166 | 0.022187 | 0.055412 | -0.0014975 | 0.087408 | -59.5184 | 61.6379 | -61.3358 | -61.2854 | 53.6728 | 7.0129 | 61.5417 | 61.7432 | 61.6425 | -61.3358 | -0.21057 | -0.050354 | 1.6067 | -0.16022 | -8.0154 | -0.21057 | -0.045776 | 1.8173 | 122.6669 | 122.8683 | 114.798 | 122.7631 | 1.6067 | 122.7676 | 68.1381 | -0.21057 | 122.7631 | 1.6067 | 68.1381 | 114.798 | 122.7676 | -123.024 | -123.024
1937.3281 | 123.0698 | -61.1206 | 61.6791 | 0.19424 | 0.020292 | 0.015515 | 0.021332 | 0.05648 | -0.0023519 | 0.085486 | -59.5551 | 61.6379 | -61.3403 | -61.322 | 53.6728 | 7.0724 | 61.6013 | 61.7203 | 61.6333 | -61.3632 | -0.21973 | -0.041199 | 1.5656 | -0.20142 | -8.0063 | -0.24262 | -0.045776 | 1.7853 | 122.7219 | 122.8409 | 114.7934 | 122.7585 | 1.5656 | 122.7539 | 68.1931 | -0.24262 | 122.7585 | 1.5656 | 68.1931 | 114.7934 | 122.7539 | -123.0194 | -123.0423
1938.3281 | 123.1155 | -61.0931 | 61.6562 | 0.34683 | 0.021787 | 0.0088932 | 0.025391 | 0.057548 | -0.0014975 | 0.085272 | -59.4727 | 61.6287 | -61.3266 | -61.29 | 53.714 | 7.1136 | 61.5417 | 61.7569 | 61.615 | -61.3632 | -0.23346 | -0.027466 | 1.6205 | -0.19684 | -7.9422 | -0.27008 | -0.041199 | 1.8539 | 122.6349 | 122.85 | 114.8071 | 122.7219 | 1.6205 | 122.7081 | 68.2068 | -0.27008 | 122.7219 | 1.6205 | 68.2068 | 114.8071 | 122.7081 | -122.9828 | -123.0194
1939.3281 | 123.1155 | -61.0794 | 61.6562 | 0.52231 | 0.020933 | 0.006116 | 0.022614 | 0.056266 | -0.0021383 | 0.085913 | -59.404 | 61.6287 | -61.3037 | -61.2717 | 53.7643 | 7.1228 | 61.5417 | 61.7569 | 61.647 | -61.3586 | -0.2243 | -0.027466 | 1.6754 | -0.19226 | -7.8918 | -0.27924 | -0.009155 | 1.8997 | 122.6212 | 122.8363 | 114.8438 | 122.7081 | 1.6754 | 122.7264 | 68.2022 | -0.27924 | 122.7081 | 1.6754 | 68.2022 | 114.8438 | 122.7264 | -122.9599 | -123.0148
1940.3281 | 123.1201 | -61.1069 | 61.6425 | 0.22476 | 0.022001 | 0.012097 | 0.029236 | 0.060325 | -0.0029929 | 0.085913 | -59.4864 | 61.6608 | -61.3129 | -61.2076 | 53.8101 | 7.0816 | 61.5601 | 61.7661 | 61.6196 | -61.3678 | -0.20599 | 0.018311 | 1.6205 | -0.10071 | -7.8323 | -0.26093 | -0.022888 | 1.8265 | 122.6669 | 122.8729 | 114.917 | 122.7676 | 1.6205 | 122.7264 | 68.1885 | -0.26093 | 122.7676 | 1.6205 | 68.1885 | 114.917 | 122.7264 | -122.9553 | -123.0103
1941.3281 | 123.1659 | -61.1206 | 61.6699 | 0.30869 | 0.023496 | 0.013166 | 0.023469 | 0.060325 | -0.0029929 | 0.086981 | -59.5139 | 61.6882 | -61.3266 | -61.2854 | 53.6728 | 7.0358 | 61.5784 | 61.5646 | 61.6058 | -61.3724 | -0.20599 | 0.01831 | 1.6067 | -0.1648 | -7.9971 | -0.25177 | -0.064087 | 1.8127 | 122.699 | 122.6852 | 114.7934 | 122.8088 | 1.6067 | 122.7264 | 68.1564 | -0.25177 | 122.8088 | 1.6067 | 68.1564 | 114.7934 | 122.7264 | -122.9965 | -123.0423
1942.3281 | 123.0331 | -61.1298 | 61.6974 | 0.21713 | 0.025419 | 0.010816 | 0.026032 | 0.058616 | 0.00063871 | 0.086126 | -59.5825 | 61.7249 | -61.3449 | -61.3586 | 53.6087 | 6.9809 | 61.6699 | 61.6425 | 61.6608 | -61.3953 | -0.21515 | 0.027466 | 1.5472 | -0.22888 | -8.0887 | -0.2655 | -0.036621 | 1.7624 | 122.7997 | 122.7722 | 114.7385 | 122.8546 | 1.5472 | 122.7905 | 68.1107 | -0.2655 | 122.8546 | 1.5472 | 68.1107 | 114.7385 | 122.7905 | -123.0423 | -123.0927
1943.3281 | 123.1018 | -61.1389 | 61.6653 | 0.24002 | 0.022428 | 0.013379 | 0.023682 | 0.057975 | -0.0019247 | 0.08634 | -59.5413 | 61.6837 | -61.3129 | -61.322 | 53.6591 | 7.0221 | 61.5967 | 61.7065 | 61.6333 | -61.3541 | -0.17395 | 0.018311 | 1.5976 | -0.1831 | -8.0063 | -0.21515 | -0.032043 | 1.7715 | 122.7356 | 122.8455 | 114.798 | 122.8226 | 1.5976 | 122.7722 | 68.161 | -0.21515 | 122.8226 | 1.5976 | 68.161 | 114.798 | 122.7722 | -122.9782 | -123.0194
1944.3281 | 123.111 | -61.1206 | 61.6699 | 0.2095 | 0.022856 | 0.012952 | 0.022401 | 0.060325 | -0.0029929 | 0.086126 | -59.6283 | 61.6516 | -61.3632 | -61.2808 | 53.6819 | 7.0084 | 61.5784 | 61.7523 | 61.6379 | -61.3586 | -0.24262 | -0.018311 | 1.4923 | -0.16022 | -7.988 | -0.23804 | -0.032044 | 1.7349 | 122.699 | 122.8729 | 114.8026 | 122.7722 | 1.4923 | 122.7585 | 68.129 | -0.23804 | 122.7722 | 1.4923 | 68.129 | 114.8026 | 122.7585 | -123.0331 | -123.0286
1945.3281 | 123.1476 | -61.0794 | 61.6745 | 0.24765 | 0.022856 | 0.01167 | 0.023469 | 0.058189 | -0.0014975 | 0.087195 | -59.5001 | 61.6562 | -61.3174 | -61.3953 | 53.5034 | 7.0129 | 61.6974 | 61.8439 | 61.6425 | -61.3449 | -0.23804 | -0.018311 | 1.5793 | -0.31586 | -8.1711 | -0.2655 | -0.032044 | 1.8173 | 122.7768 | 122.9233 | 114.5828 | 122.7356 | 1.5793 | 122.7219 | 68.0923 | -0.2655 | 122.7356 | 1.5793 | 68.0923 | 114.5828 | 122.7219 | -122.9919 | -123.0194
1946.3281 | 123.111 | -61.1023 | 61.6653 | 0.19424 | 0.022428 | 0.011243 | 0.023469 | 0.059471 | -0.0019247 | 0.087622 | -59.4955 | 61.6745 | -61.3174 | -61.3037 | 53.7003 | 7.045 | 61.5784 | 61.7661 | 61.6287 | -61.3495 | -0.21515 | 0.009156 | 1.6068 | -0.20142 | -7.9651 | -0.24719 | -0.036621 | 1.8219 | 122.6807 | 122.8683 | 114.8026 | 122.7768 | 1.6068 | 122.731 | 68.1473 | -0.24719 | 122.7768 | 1.6068 | 68.1473 | 114.8026 | 122.731 | -122.9828 | -123.0148
1947.3281 | 123.1018 | -61.1069 | 61.6791 | 0.30106 | 0.02136 | 0.011029 | 0.021973 | 0.056907 | -0.0021383 | 0.087622 | -59.5001 | 61.6653 | -61.3083 | -61.29 | 53.6728 | 7.0221 | 61.5646 | 61.7615 | 61.6333 | -61.3541 | -0.20142 | -0.013733 | 1.6068 | -0.1831 | -8.0063 | -0.24719 | -0.045776 | 1.8082 | 122.6715 | 122.8683 | 114.7797 | 122.7722 | 1.6068 | 122.7402 | 68.129 | -0.24719 | 122.7722 | 1.6068 | 68.129 | 114.7797 | 122.7402 | -122.9874 | -123.0331
1948.3281 | 123.111 | -61.1206 | 61.6562 | -0.088043 | 0.020933 | 0.012311 | 0.024964 | 0.057762 | -0.0012839 | 0.088476 | -59.3948 | 61.6608 | -61.3083 | -61.2762 | 53.6911 | 7.0404 | 61.5417 | 61.7706 | 61.615 | -61.3586 | -0.18768 | 0.004578 | 1.7258 | -0.15564 | -7.9651 | -0.23804 | -0.041199 | 1.9135 | 122.6624 | 122.8912 | 114.8117 | 122.7814 | 1.7258 | 122.7356 | 68.161 | -0.23804 | 122.7814 | 1.7258 | 68.161 | 114.8117 | 122.7356 | -122.9645 | -123.0148
1949.3281 | 123.0743 | -61.1252 | 61.6745 | 0.23239 | 0.022215 | 0.013593 | 0.024964 | 0.058616 | -0.0021383 | 0.085486 | -59.5505 | 61.7249 | -61.3312 | -61.3449 | 53.6133 | 6.9214 | 61.6241 | 61.6974 | 61.6653 | -61.3632 | -0.20599 | 0.050354 | 1.5747 | -0.21973 | -8.0612 | -0.23804 | -0.009156 | 1.7807 | 122.7493 | 122.8226 | 114.7385 | 122.85 | 1.5747 | 122.7905 | 68.0466 | -0.23804 | 122.85 | 1.5747 | 68.0466 | 114.7385 | 122.7905 | -123.0057 | -123.0377
1950.3281 | 123.1705 | -61.1114 | 61.6653 | 0.17136 | 0.021574 | 0.015943 | 0.022614 | 0.059898 | -0.0025657 | 0.086554 | -59.491 | 61.6928 | -61.3129 | -61.29 | 53.7323 | 6.9672 | 61.5738 | 61.6699 | 61.6516 | -61.3632 | -0.20142 | 0.027466 | 1.6205 | -0.17853 | -7.933 | -0.25177 | -0.013733 | 1.8219 | 122.6852 | 122.7814 | 114.8438 | 122.8043 | 1.6205 | 122.7631 | 68.0786 | -0.25177 | 122.8043 | 1.6205 | 68.0786 | 114.8438 | 122.7631 | -122.9782 | -123.0286
1951.3281 | 123.111 | -61.0794 | 61.6837 | 0.2858 | 0.022001 | 0.0099612 | 0.021332 | 0.057334 | -0.0032065 | 0.088476 | -59.5001 | 61.6745 | -61.3037 | -61.2671 | 53.7598 | 6.9077 | 61.5875 | 61.7889 | 61.6608 | -61.3174 | -0.2243 | -0.009155 | 1.5793 | -0.18768 | -7.9239 | -0.23804 | -0.022888 | 1.8036 | 122.6669 | 122.8683 | 114.8392 | 122.7539 | 1.5793 | 122.7402 | 67.9871 | -0.23804 | 122.7539 | 1.5793 | 67.9871 | 114.8392 | 122.7402 | -122.9874 | -123.0011
1952.3281 | 123.1338 | -61.1114 | 61.6608 | 0.095062 | 0.022856 | 0.010175 | 0.022401 | 0.05883 | -0.0029929 | 0.088049 | -59.4955 | 61.6699 | -61.2991 | -61.29 | 53.7186 | 6.9443 | 61.5738 | 61.7706 | 61.647 | -61.3449 | -0.18768 | 0.009155 | 1.6159 | -0.17853 | -7.9422 | -0.23346 | -0.013733 | 1.8036 | 122.6852 | 122.8821 | 114.83 | 122.7814 | 1.6159 | 122.7585 | 68.0557 | -0.23346 | 122.7814 | 1.6159 | 68.0557 | 114.83 | 122.7585 | -122.9599 | -123.0057
1953.3281 | 123.1338 | -61.1069 | 61.6653 | 0.24002 | 0.02136 | 0.0088932 | 0.019196 | 0.056693 | -0.0038473 | 0.08634 | -59.4864 | 61.6562 | -61.3129 | -61.2991 | 53.7598 | 6.9534 | 61.5646 | 61.7935 | 61.6287 | -61.3632 | -0.20599 | -0.009155 | 1.6205 | -0.19226 | -7.9056 | -0.25635 | -0.036621 | 1.8265 | 122.6715 | 122.9004 | 114.8666 | 122.7631 | 1.6205 | 122.7356 | 68.0603 | -0.25635 | 122.7631 | 1.6205 | 68.0603 | 114.8666 | 122.7356 | -122.9782 | -123.0286
1954.3281 | 123.1201 | -61.0748 | 61.6882 | 0.20187 | 0.020292 | 0.009534 | 0.023255 | 0.059471 | -0.00064309 | 0.088049 | -59.4864 | 61.6928 | -61.2854 | -61.2991 | 53.6819 | 6.7612 | 61.5692 | 61.9263 | 61.6241 | -61.3678 | -0.21057 | 0.004578 | 1.5884 | -0.2243 | -8.0063 | -0.29297 | -0.064086 | 1.799 | 122.644 | 123.0011 | 114.7568 | 122.7676 | 1.5884 | 122.699 | 67.836 | -0.29297 | 122.7676 | 1.5884 | 67.836 | 114.7568 | 122.699 | -122.9736 | -123.056
1955.3281 | 123.1201 | -61.084 | 61.6837 | 0.19424 | 0.020078 | 0.012311 | 0.024323 | 0.05883 | -0.0017111 | 0.088049 | -59.5139 | 61.702 | -61.3129 | -61.2991 | 53.6819 | 6.9305 | 61.5646 | 61.7615 | 61.6562 | -61.3815 | -0.22888 | 0.01831 | 1.5701 | -0.21515 | -8.0017 | -0.29755 | -0.027466 | 1.799 | 122.6486 | 122.8455 | 114.7659 | 122.7859 | 1.5701 | 122.7402 | 68.0145 | -0.29755 | 122.7859 | 1.5701 | 68.0145 | 114.7659 | 122.7402 | -122.9965 | -123.0652
1956.3281 | 123.0927 | -61.0977 | 61.6608 | 0.23239 | 0.021787 | 0.0097476 | 0.025178 | 0.058402 | -0.0019247 | 0.087195 | -59.5367 | 61.6974 | -61.3403 | -61.322 | 53.627 | 6.958 | 61.6013 | 61.7432 | 61.6562 | -61.3586 | -0.24261 | 0.036621 | 1.561 | -0.2243 | -8.0338 | -0.26093 | -0.004578 | 1.8036 | 122.699 | 122.8409 | 114.7247 | 122.7951 | 1.561 | 122.7539 | 68.0557 | -0.26093 | 122.7951 | 1.561 | 68.0557 | 114.7247 | 122.7539 | -123.0011 | -123.0194
1957.3281 | 123.0972 | -61.0748 | 61.6928 | 0.21713 | 0.022856 | 0.012952 | 0.026032 | 0.058616 | -0.0012839 | 0.086981 | -59.5505 | 61.7294 | -61.322 | -61.3083 | 53.6362 | 6.9489 | 61.6333 | 61.7477 | 61.6516 | -61.3632 | -0.24719 | 0.036621 | 1.5244 | -0.23346 | -8.0566 | -0.28839 | -0.041199 | 1.7715 | 122.7081 | 122.8226 | 114.711 | 122.8043 | 1.5244 | 122.7264 | 68.0237 | -0.28839 | 122.8043 | 1.5244 | 68.0237 | 114.711 | 122.7264 | -123.0148 | -123.056
1958.3281 | 123.1064 | -61.0931 | 61.6837 | 0.24765 | 0.020506 | 0.012311 | 0.021546 | 0.057121 | -0.0025657 | 0.089117 | -59.4864 | 61.6882 | -61.3037 | -61.2717 | 53.6316 | 6.9809 | 61.5875 | 61.7569 | 61.6608 | -61.322 | -0.21057 | 0.004577 | 1.6068 | -0.17853 | -8.0521 | -0.22888 | -0.022888 | 1.8173 | 122.6807 | 122.85 | 114.7247 | 122.7814 | 1.6068 | 122.7539 | 68.074 | -0.22888 | 122.7814 | 1.6068 | 68.074 | 114.7247 | 122.7539 | -122.9874 | -123.0057
1959.3281 | 123.1247 | -61.0474 | 61.7157 | 0.12558 | 0.020292 | 0.014875 | 0.022828 | 0.058616 | -0.0017111 | 0.088476 | -59.491 | 61.6974 | -61.3083 | -61.3861 | 53.4302 | 6.9489 | 61.7111 | 61.8484 | 61.6608 | -61.3449 | -0.26093 | -0.01831 | 1.5564 | -0.33875 | -8.2855 | -0.29755 | -0.054931 | 1.8173 | 122.7585 | 122.8958 | 114.4775 | 122.7448 | 1.5564 | 122.7081 | 67.9962 | -0.29755 | 122.7448 | 1.5564 | 67.9962 | 114.4775 | 122.7081 | -123.024 | -123.0606
1960.3281 | 123.1476 | -61.1023 | 61.702 | 0.14847 | 0.022856 | 0.010388 | 0.023469 | 0.059043 | -0.00064309 | 0.084845 | -59.4955 | 61.7157 | -61.2991 | -61.2808 | 53.6545 | 6.9763 | 61.5921 | 61.5601 | 61.647 | -61.4044 | -0.19684 | 0.013733 | 1.6068 | -0.17853 | -8.0475 | -0.30212 | -0.054931 | 1.8036 | 122.6944 | 122.6624 | 114.7568 | 122.818 | 1.6068 | 122.7493 | 68.0786 | -0.30212 | 122.818 | 1.6068 | 68.0786 | 114.7568 | 122.7493 | -123.0011 | -123.1064
1961.3281 | 123.1293 | -61.0977 | 61.6562 | 0.18662 | 0.023069 | 0.012952 | 0.022187 | 0.060325 | -0.0019247 | 0.085058 | -59.523 | 61.7065 | -61.3174 | -61.2854 | 53.627 | 6.9397 | 61.5784 | 61.7889 | 61.6974 | -61.3632 | -0.21973 | 0.050354 | 1.5747 | -0.18768 | -8.0292 | -0.2655 | 0.041199 | 1.7944 | 122.6761 | 122.8867 | 114.7247 | 122.8043 | 1.5747 | 122.7951 | 68.0374 | -0.2655 | 122.8043 | 1.5747 | 68.0374 | 114.7247 | 122.7951 | -122.9736 | -123.0194
1962.3281 | 123.1064 | -61.0794 | 61.6974 | 0.26291 | 0.019865 | 0.011457 | 0.023255 | 0.059043 | -0.0017111 | 0.087195 | -59.5139 | 61.702 | -61.3403 | -61.2808 | 53.6224 | 6.8893 | 61.5784 | 61.7615 | 61.6653 | -61.3678 | -0.26092 | 0.004577 | 1.5656 | -0.20142 | -8.075 | -0.28839 | -0.032044 | 1.8265 | 122.6578 | 122.8409 | 114.7018 | 122.7814 | 1.5656 | 122.7448 | 67.9688 | -0.28839 | 122.7814 | 1.5656 | 67.9688 | 114.7018 | 122.7448 | -123.0377 | -123.0652
1963.3281 | 123.0331 | -61.1389 | 61.702 | 0.17899 | 0.021787 | 0.0091068 | 0.023896 | 0.058189 | -0.00042929 | 0.087408 | -59.5825 | 61.7477 | -61.3403 | -61.377 | 53.5721 | 6.8344 | 61.702 | 61.6653 | 61.6974 | -61.3907 | -0.20142 | 0.045777 | 1.5564 | -0.23804 | -8.1299 | -0.25177 | -0.004577 | 1.7578 | 122.8409 | 122.8043 | 114.711 | 122.8867 | 1.5564 | 122.8363 | 67.9733 | -0.25177 | 122.8867 | 1.5564 | 67.9733 | 114.711 | 122.8363 | -123.0423 | -123.0927
1964.3281 | 123.1018 | -61.084 | 61.6974 | 0.24002 | 0.022215 | 0.014447 | 0.023896 | 0.059684 | -0.0012839 | 0.085913 | -59.5459 | 61.702 | -61.3174 | -61.2854 | 53.595 | 6.9717 | 61.6013 | 61.7706 | 61.6974 | -61.3403 | -0.23346 | 0.004577 | 1.5381 | -0.20142 | -8.1024 | -0.25635 | 0 | 1.7715 | 122.6852 | 122.8546 | 114.679 | 122.7859 | 1.5381 | 122.7814 | 68.0557 | -0.25635 | 122.7859 | 1.5381 | 68.0557 | 114.679 | 122.7814 | -123.0148 | -123.0377
1965.3281 | 123.1293 | -61.1069 | 61.6882 | 0.29343 | 0.022215 | 0.012097 | 0.021332 | 0.059043 | -0.0034201 | 0.086767 | -59.5047 | 61.6837 | -61.3037 | -61.2946 | 53.6407 | 6.8939 | 61.5738 | 61.7844 | 61.6699 | -61.3495 | -0.19684 | -0.004577 | 1.6022 | -0.18768 | -8.0475 | -0.24261 | -0.01831 | 1.799 | 122.6807 | 122.8912 | 114.7476 | 122.7905 | 1.6022 | 122.7768 | 68.0008 | -0.24261 | 122.7905 | 1.6022 | 68.0008 | 114.7476 | 122.7768 | -122.9919 | -123.0377
1966.3281 | 123.1201 | -61.0931 | 61.6882 | 0.92667 | 0.019438 | 0.013379 | 0.019837 | 0.057762 | -0.0019247 | 0.086767 | -59.404 | 61.6974 | -61.3083 | -61.2671 | 53.6133 | 6.871 | 61.5875 | 61.7889 | 61.6516 | -61.3312 | -0.21515 | 0.009156 | 1.6891 | -0.17395 | -8.075 | -0.23804 | -0.036621 | 1.9043 | 122.6807 | 122.8821 | 114.7064 | 122.7905 | 1.6891 | 122.7448 | 67.9642 | -0.23804 | 122.7905 | 1.6891 | 67.9642 | 114.7064 | 122.7448 | -122.9965 | -123.0194
1967.3281 | 123.111 | -61.0703 | 61.702 | 0.21713 | 0.022642 | 0.013379 | 0.023255 | 0.059471 | -0.0021383 | 0.083563 | -59.6558 | 61.6699 | -61.29 | -61.2625 | 53.6224 | 6.9031 | 61.6196 | 61.7981 | 61.6745 | -61.3495 | -0.21973 | -0.032043 | 1.4145 | -0.19226 | -8.0795 | -0.27924 | -0.027465 | 1.6342 | 122.6898 | 122.8683 | 114.6927 | 122.7402 | 1.4145 | 122.7448 | 67.9733 | -0.27924 | 122.7402 | 1.4145 | 67.9733 | 114.6927 | 122.7448 | -122.9919 | -123.0515
1968.3281 | 123.1201 | -61.0748 | 61.6837 | 0.24002 | 0.020292 | 0.012097 | 0.022828 | 0.061607 | -0.0012839 | 0.086126 | -59.4818 | 61.6837 | -61.2946 | -61.1847 | 53.7552 | 7.0038 | 61.5601 | 61.8393 | 61.6928 | -61.3495 | -0.21973 | 0 | 1.593 | -0.10986 | -7.9285 | -0.27466 | 0.009155 | 1.8127 | 122.6349 | 122.9141 | 114.83 | 122.7585 | 1.593 | 122.7676 | 68.0786 | -0.27466 | 122.7585 | 1.593 | 68.0786 | 114.83 | 122.7676 | -122.9782 | -123.0331
1969.3281 | 123.0972 | -61.0657 | 61.6837 | 0.20187 | 0.019865 | 0.012952 | 0.020051 | 0.057762 | -0.0021383 | 0.085486 | -59.4727 | 61.7065 | -61.29 | -61.2762 | 53.6407 | 6.7932 | 61.5372 | 61.9354 | 61.647 | -61.3449 | -0.2243 | 0.022888 | 1.593 | -0.21057 | -8.0429 | -0.27924 | -0.036621 | 1.8173 | 122.6028 | 123.0011 | 114.7064 | 122.7722 | 1.593 | 122.7127 | 67.8589 | -0.27924 | 122.7722 | 1.593 | 67.8589 | 114.7064 | 122.7127 | -122.9736 | -123.0286
1970.3281 | 123.0515 | -61.116 | 61.7065 | 0.2095 | 0.024351 | 0.013593 | 0.02411 | 0.057121 | -0.0014975 | 0.088049 | -59.5459 | 61.7615 | -61.3129 | -61.3449 | 53.595 | 6.8756 | 61.702 | 61.702 | 61.7157 | -61.3632 | -0.19684 | 0.054932 | 1.5701 | -0.22888 | -8.1116 | -0.24719 | 0.009155 | 1.767 | 122.818 | 122.818 | 114.711 | 122.8775 | 1.5701 | 122.8317 | 67.9916 | -0.24719 | 122.8775 | 1.5701 | 67.9916 | 114.711 | 122.8317 | -123.0194 | -123.0698
1971.3281 | 123.1247 | -61.0794 | 61.7203 | 0.24765 | 0.021147 | 0.011884 | 0.021973 | 0.06118 | -0.0029929 | 0.08634 | -59.5184 | 61.6974 | -61.3037 | -61.2854 | 53.6453 | 6.926 | 61.6196 | 61.7935 | 61.7065 | -61.3266 | -0.2243 | -0.022888 | 1.561 | -0.20599 | -8.075 | -0.24719 | -0.013733 | 1.7853 | 122.699 | 122.8729 | 114.7247 | 122.7768 | 1.561 | 122.786 | 68.0054 | -0.24719 | 122.7768 | 1.561 | 68.0054 | 114.7247 | 122.786 | -123.024 | -123.0469
1972.3281 | 123.1155 | -61.0428 | 61.6974 | 0.095062 | 0.022642 | 0.015943 | 0.021119 | 0.05883 | -2.092e-06 | 0.085272 | -59.4635 | 61.7249 | -61.2854 | -61.2442 | 53.6545 | 6.9534 | 61.6058 | 61.8256 | 61.6837 | -61.3266 | -0.24261 | 0.027466 | 1.5793 | -0.20142 | -8.0429 | -0.28381 | -0.013733 | 1.8219 | 122.6486 | 122.8683 | 114.6973 | 122.7676 | 1.5793 | 122.7264 | 67.9962 | -0.28381 | 122.7676 | 1.5793 | 67.9962 | 114.6973 | 122.7264 | -122.9828 | -123.024
1973.3281 | 123.1201 | -61.0611 | 61.7111 | 1.5828 | 0.020078 | 0.010388 | 0.021973 | 0.059043 | -0.00064309 | 0.085058 | -59.4406 | 61.7065 | -61.2946 | -61.2534 | 53.7003 | 6.9351 | 61.5921 | 61.7981 | 61.6699 | -61.322 | -0.23346 | -0.004578 | 1.6205 | -0.19226 | -8.0109 | -0.26093 | -0.041199 | 1.8539 | 122.6532 | 122.8592 | 114.7614 | 122.7676 | 1.6205 | 122.731 | 67.9962 | -0.26093 | 122.7676 | 1.6205 | 67.9962 | 114.7614 | 122.731 | -123.0057 | -123.0331
1974.3281 | 123.1293 | -61.0611 | 61.7111 | 0.24765 | 0.021787 | 0.013806 | 0.021546 | 0.060539 | -0.0025657 | 0.08634 | -59.4635 | 61.7111 | -61.2717 | -61.1343 | 53.801 | 6.9168 | 61.6241 | 61.853 | 61.7157 | -61.3129 | -0.21057 | 0 | 1.5976 | -0.073242 | -7.9102 | -0.25177 | 0.004577 | 1.8082 | 122.6852 | 122.9141 | 114.8621 | 122.7722 | 1.5976 | 122.7768 | 67.9779 | -0.25177 | 122.7722 | 1.5976 | 67.9779 | 114.8621 | 122.7768 | -122.9828 | -123.024
1975.3281 | 123.1796 | -61.0474 | 61.7203 | 0.27817 | 0.01901 | 0.0093204 | 0.022828 | 0.058402 | -0.00042929 | 0.088049 | -59.4681 | 61.7249 | -61.2625 | -61.2488 | 53.6362 | 6.958 | 61.615 | 61.615 | 61.6882 | -61.3678 | -0.21515 | 0.004578 | 1.5793 | -0.20142 | -8.0841 | -0.32044 | -0.032044 | 1.7944 | 122.6624 | 122.6624 | 114.6835 | 122.7722 | 1.5793 | 122.7356 | 68.0054 | -0.32044 | 122.7722 | 1.5793 | 68.0054 | 114.6835 | 122.7356 | -122.9828 | -123.0881
1976.3281 | 123.111 | -61.0565 | 61.734 | 0.21713 | 0.02136 | 0.0082522 | 0.023469 | 0.059471 | -0.0012839 | 0.08634 | -59.491 | 61.7157 | -61.2808 | -61.2488 | 53.6362 | 6.9763 | 61.6287 | 61.7752 | 61.6928 | -61.3312 | -0.2243 | -0.018311 | 1.5656 | -0.19226 | -8.0978 | -0.27466 | -0.041199 | 1.7899 | 122.6852 | 122.8317 | 114.6927 | 122.7722 | 1.5656 | 122.7493 | 68.0328 | -0.27466 | 122.7722 | 1.5656 | 68.0328 | 114.6927 | 122.7493 | -123.0148 | -123.0652
1977.3281 | 123.0194 | -61.0748 | 61.7386 | 0.17899 | 0.021147 | 0.0099612 | 0.024537 | 0.060752 | -0.0032065 | 0.088263 | -59.5367 | 61.8073 | -61.2854 | -61.3495 | 53.5263 | 6.871 | 61.7477 | 61.6791 | 61.7386 | -61.3678 | -0.21057 | 0.068665 | 1.5381 | -0.27466 | -8.2123 | -0.29297 | 0 | 1.7487 | 122.8226 | 122.7539 | 114.6011 | 122.8821 | 1.5381 | 122.8134 | 67.9459 | -0.29297 | 122.8821 | 1.5381 | 67.9459 | 114.6011 | 122.8134 | -123.024 | -123.1064
1978.3281 | 123.0927 | -61.0657 | 61.7249 | 0.25528 | 0.022428 | 0.0084658 | 0.020905 | 0.059898 | -0.0012839 | 0.088476 | -59.5184 | 61.7294 | -61.2808 | -61.3037 | 53.6133 | 6.8573 | 61.6562 | 61.7523 | 61.7249 | -61.3129 | -0.21515 | 0.004577 | 1.5472 | -0.23804 | -8.1116 | -0.24719 | 0 | 1.7624 | 122.7219 | 122.818 | 114.679 | 122.7951 | 1.5472 | 122.7905 | 67.923 | -0.24719 | 122.7951 | 1.5472 | 67.923 | 114.679 | 122.7905 | -123.0057 | -123.0377
1979.3281 | 123.143 | -61.0474 | 61.7249 | 0.20187 | 0.022215 | 0.012738 | 0.01941 | 0.057975 | -2.092e-06 | 0.087622 | -59.4681 | 61.7386 | -61.2579 | -61.4548 | 53.7094 | 7.0038 | 61.702 | 61.7981 | 61.7294 | -61.3129 | -0.21057 | 0.013732 | 1.5793 | -0.40741 | -8.0154 | -0.2655 | 0.004577 | 1.7899 | 122.7493 | 122.8455 | 114.7568 | 122.7859 | 1.5793 | 122.7768 | 68.0511 | -0.2655 | 122.7859 | 1.5793 | 68.0511 | 114.7568 | 122.7768 | -122.9828 | -123.0377
1980.3281 | 123.0743 | -61.0611 | 61.6745 | 0.19424 | 0.020506 | 0.014875 | 0.022401 | 0.059471 | -0.0014975 | 0.088904 | -59.4635 | 61.7432 | -61.2808 | -61.2396 | 53.6545 | 6.9763 | 61.6058 | 61.7798 | 61.7065 | -61.3312 | -0.21973 | 0.068664 | 1.5976 | -0.17853 | -8.02 | -0.27008 | 0.032043 | 1.8173 | 122.6669 | 122.8409 | 114.7156 | 122.8043 | 1.5976 | 122.7676 | 68.0374 | -0.27008 | 122.8043 | 1.5976 | 68.0374 | 114.7156 | 122.7676 | -122.9553 | -123.0057
1981.3281 | 123.1064 | -61.0611 | 61.7294 | 0.17136 | 0.02136 | 0.01167 | 0.021332 | 0.060539 | -0.00042929 | 0.089758 | -59.4818 | 61.7157 | -61.29 | -61.2625 | 53.6545 | 6.926 | 61.615 | 61.8073 | 61.7111 | -61.3449 | -0.22888 | -0.013733 | 1.5793 | -0.20142 | -8.075 | -0.28381 | -0.01831 | 1.8082 | 122.6761 | 122.8683 | 114.7156 | 122.7768 | 1.5793 | 122.7722 | 67.9871 | -0.28381 | 122.7768 | 1.5793 | 67.9871 | 114.7156 | 122.7722 | -123.0194 | -123.0743
1982.3281 | 123.1064 | -61.0428 | 61.7065 | 0.23239 | 0.021147 | 0.0099612 | 0.022401 | 0.05883 | -0.0032065 | 0.08634 | -59.5001 | 61.7569 | -61.2717 | -61.2305 | 53.6728 | 6.9717 | 61.615 | 61.7752 | 61.7157 | -61.3449 | -0.22888 | 0.050354 | 1.5427 | -0.18768 | -8.0338 | -0.30212 | 0.009155 | 1.7715 | 122.6578 | 122.818 | 114.7156 | 122.7997 | 1.5427 | 122.7585 | 68.0145 | -0.30212 | 122.7997 | 1.5427 | 68.0145 | 114.7156 | 122.7585 | -122.9782 | -123.0515
1983.3281 | 123.024 | -61.0794 | 61.734 | 0.17899 | 0.02606 | 0.013806 | 0.02411 | 0.059898 | 0.0010659 | 0.085058 | -59.5413 | 61.7889 | -61.3174 | -61.3266 | 53.5675 | 6.9077 | 61.7386 | 61.6699 | 61.7386 | -61.3678 | -0.23804 | 0.054931 | 1.5381 | -0.24719 | -8.1665 | -0.28839 | 0.004577 | 1.7761 | 122.818 | 122.7493 | 114.6469 | 122.8683 | 1.5381 | 122.818 | 67.9871 | -0.28839 | 122.8683 | 1.5381 | 67.9871 | 114.6469 | 122.818 | -123.0515 | -123.1018
1984.3281 | 123.0469 | -61.1023 | 61.7203 | 0.17899 | 0.023283 | 0.010175 | 0.024537 | 0.059471 | -0.0012839 | 0.08634 | -59.5596 | 61.7935 | -61.3083 | -61.3541 | 53.5583 | 6.8893 | 61.7523 | 61.6791 | 61.7569 | -61.3586 | -0.20599 | 0.073242 | 1.5427 | -0.25177 | -8.1619 | -0.25635 | 0.036621 | 1.7487 | 122.8546 | 122.7814 | 114.6606 | 122.8958 | 1.5427 | 122.8592 | 67.9916 | -0.25635 | 122.8958 | 1.5427 | 67.9916 | 114.6606 | 122.8592 | -123.0286 | -123.0789
1985.3281 | 123.0423 | -61.0886 | 61.7386 | 0.17899 | 0.021574 | 0.0046206 | 0.023896 | 0.058616 | 0.00042511 | 0.086767 | -59.5688 | 61.7981 | -61.3266 | -61.3678 | 53.5172 | 6.9214 | 61.7523 | 61.6562 | 61.7432 | -61.3632 | -0.23804 | 0.05951 | 1.5198 | -0.27924 | -8.2214 | -0.27466 | 0.004578 | 1.7578 | 122.8409 | 122.7448 | 114.6057 | 122.8867 | 1.5198 | 122.8317 | 68.0099 | -0.27466 | 122.8867 | 1.5198 | 68.0099 | 114.6057 | 122.8317 | -123.0652 | -123.1018
1986.3281 | 123.0515 | -61.0748 | 61.7203 | 0.24002 | 0.022001 | 0.0084658 | 0.021119 | 0.060752 | -0.0021383 | 0.088476 | -59.5276 | 61.7844 | -61.2991 | -61.29 | 53.6087 | 6.8665 | 61.6882 | 61.7294 | 61.7386 | -61.3403 | -0.2243 | 0.064087 | 1.5472 | -0.21515 | -8.1116 | -0.2655 | 0.01831 | 1.7715 | 122.7631 | 122.8043 | 114.6835 | 122.8592 | 1.5472 | 122.8134 | 67.9413 | -0.2655 | 122.8592 | 1.5472 | 67.9413 | 114.6835 | 122.8134 | -123.0194 | -123.0606
1987.3281 | 123.0469 | -61.0703 | 61.734 | 0.24002 | 0.023069 | 0.014875 | 0.022401 | 0.062034 | -0.00064309 | 0.086767 | -59.523 | 61.7935 | -61.29 | -61.3083 | 53.5812 | 6.8481 | 61.7249 | 61.7203 | 61.7523 | -61.3403 | -0.21973 | 0.059509 | 1.5472 | -0.23804 | -8.1528 | -0.27008 | 0.01831 | 1.767 | 122.7951 | 122.7905 | 114.6515 | 122.8638 | 1.5472 | 122.8226 | 67.9184 | -0.27008 | 122.8638 | 1.5472 | 67.9184 | 114.6515 | 122.8226 | -123.024 | -123.0743
1988.3281 | 123.0469 | -61.0657 | 61.7569 | 0.19424 | 0.021787 | 0.014447 | 0.023255 | 0.060752 | -0.0010703 | 0.086126 | -59.5184 | 61.7798 | -61.29 | -61.3129 | 53.6041 | 6.7474 | 61.7065 | 61.7111 | 61.734 | -61.3403 | -0.2243 | 0.022888 | 1.5472 | -0.24719 | -8.1528 | -0.27466 | -0.022888 | 1.7715 | 122.7722 | 122.7768 | 114.6698 | 122.8455 | 1.5472 | 122.7997 | 67.8131 | -0.27466 | 122.8455 | 1.5472 | 67.8131 | 114.6698 | 122.7997 | -123.0469 | -123.0972
1989.3438 | 123.1384 | -61.0016 | 61.7752 | -2.7965 | 0.022642 | 0.0088932 | 0.016633 | 0.059471 | -0.00064309 | 0.085913 | -59.6786 | 61.7294 | -61.2625 | -61.2213 | 53.6728 | 6.871 | 61.7157 | 61.8988 | 61.7523 | -61.2488 | -0.26093 | -0.045777 | 1.3229 | -0.21973 | -8.1024 | -0.24719 | -0.022889 | 1.5839 | 122.7173 | 122.9004 | 114.6744 | 122.731 | 1.3229 | 122.7539 | 67.8726 | -0.24719 | 122.731 | 1.3229 | 67.8726 | 114.6744 | 122.7539 | -123.0377 | -123.024
1990.3281 | 123.0972 | -61.0611 | 61.6837 | 0.11032 | 0.023069 | 0.011884 | 0.023682 | 0.060325 | -0.0021383 | 0.088904 | -59.5001 | 61.7386 | -61.2625 | -61.2442 | 53.6224 | 6.8573 | 61.647 | 61.7981 | 61.7203 | -61.3174 | -0.20142 | 0.054931 | 1.561 | -0.18311 | -8.0612 | -0.25635 | 0.036621 | 1.7624 | 122.7081 | 122.8592 | 114.6835 | 122.7997 | 1.561 | 122.7814 | 67.9184 | -0.25635 | 122.7997 | 1.561 | 67.9184 | 114.6835 | 122.7814 | -122.9462 | -123.0011
1991.3281 | 123.1247 | -61.0519 | 61.734 | 0.19424 | 0.020506 | 0.009534 | 0.021546 | 0.059257 | -0.0019247 | 0.08634 | -59.4635 | 61.734 | -61.2717 | -61.2534 | 53.6591 | 6.8619 | 61.6379 | 61.7935 | 61.734 | -61.322 | -0.21973 | 0 | 1.5884 | -0.20142 | -8.075 | -0.27008 | 0 | 1.8082 | 122.6898 | 122.8455 | 114.711 | 122.7859 | 1.5884 | 122.7859 | 67.9138 | -0.27008 | 122.7859 | 1.5884 | 67.9138 | 114.711 | 122.7859 | -123.0057 | -123.056
1992.3281 | 123.1018 | -61.0428 | 61.7477 | 0.26291 | 0.020933 | 0.012311 | 0.02176 | 0.058189 | -0.0029929 | 0.085272 | -59.4955 | 61.7569 | -61.2625 | -61.2396 | 53.6911 | 6.8207 | 61.6608 | 61.8256 | 61.7386 | -61.2991 | -0.21973 | 0.009155 | 1.5472 | -0.19684 | -8.0566 | -0.25635 | -0.009156 | 1.767 | 122.7036 | 122.8683 | 114.7339 | 122.7997 | 1.5472 | 122.7814 | 67.8635 | -0.25635 | 122.7997 | 1.5472 | 67.8635 | 114.7339 | 122.7814 | -123.0103 | -123.0469
1993.3281 | 123.111 | -61.0291 | 61.7249 | 0.24765 | 0.020078 | 0.011884 | 0.021119 | 0.058402 | -0.0023519 | 0.087195 | -59.4681 | 61.7249 | -61.2442 | -61.2305 | 53.714 | 6.839 | 61.6287 | 61.8439 | 61.7569 | -61.2854 | -0.21515 | 0 | 1.561 | -0.20142 | -8.0109 | -0.25635 | 0.032043 | 1.7761 | 122.6578 | 122.8729 | 114.743 | 122.7539 | 1.561 | 122.7859 | 67.868 | -0.25635 | 122.7539 | 1.561 | 67.868 | 114.743 | 122.7859 | -122.9691 | -123.0103
1994.3438 | 123.0698 | -61.0245 | 61.8118 | -0.14908 | 0.020292 | 0.0063296 | 0.019196 | 0.055839 | -0.0021383 | 0.087195 | -59.4681 | 61.7798 | -61.2488 | -61.2213 | 53.6453 | 6.8298 | 61.8256 | 61.853 | 61.8027 | -61.2534 | -0.2243 | -0.032044 | 1.5564 | -0.19684 | -8.1665 | -0.22888 | -0.009156 | 1.7807 | 122.85 | 122.8775 | 114.6698 | 122.8043 | 1.5564 | 122.8271 | 67.8543 | -0.22888 | 122.8043 | 1.5564 | 67.8543 | 114.6698 | 122.8271 | -123.0606 | -123.0652
1995.3281 | 123.1247 | -61.0199 | 61.734 | 0.42313 | 0.021787 | 0.01402 | 0.022401 | 0.056693 | -0.0025657 | 0.086981 | -59.4543 | 61.7157 | -61.2534 | -61.2442 | 53.6591 | 6.8985 | 61.6333 | 61.8622 | 61.734 | -61.2946 | -0.23346 | -0.018311 | 1.5656 | -0.22431 | -8.075 | -0.27466 | 0 | 1.799 | 122.6532 | 122.8821 | 114.679 | 122.7356 | 1.5656 | 122.7539 | 67.9184 | -0.27466 | 122.7356 | 1.5656 | 67.9184 | 114.679 | 122.7539 | -122.9874 | -123.0286
1996.3281 | 123.1384 | -61.0519 | 61.7615 | 0.23239 | 0.021787 | 0.012525 | 0.021546 | 0.060111 | -0.0012839 | 0.085272 | -59.4315 | 61.7477 | -61.2305 | -61.1298 | 53.7827 | 6.8802 | 61.6653 | 61.8668 | 61.7432 | -61.2808 | -0.17853 | -0.013733 | 1.6205 | -0.07782 | -7.9788 | -0.22888 | -0.018311 | 1.799 | 122.7173 | 122.9187 | 114.8346 | 122.7997 | 1.6205 | 122.7951 | 67.9321 | -0.22888 | 122.7997 | 1.6205 | 67.9321 | 114.8346 | 122.7951 | -122.9919 | -123.0423
1997.3281 | 123.1842 | -61.0519 | 61.7157 | 0.43076 | 0.022642 | 0.011884 | 0.023255 | 0.059471 | -0.0014975 | 0.086126 | -59.4543 | 61.7432 | -61.2534 | -61.2442 | 53.6774 | 6.8756 | 61.6379 | 61.8393 | 61.7065 | -61.3129 | -0.20142 | 0.027466 | 1.5976 | -0.19226 | -8.0383 | -0.26093 | -0.009155 | 1.799 | 122.6898 | 122.8912 | 114.7293 | 122.7951 | 1.5976 | 122.7585 | 67.9276 | -0.26093 | 122.7951 | 1.5976 | 67.9276 | 114.7293 | 122.7585 | -122.9691 | -123.0286
1998.3281 | 123.0286 | -61.0657 | 61.7661 | 0.22476 | 0.024351 | 0.011243 | 0.023896 | 0.058616 | -0.0010703 | 0.087835 | -59.5184 | 61.8027 | -61.2717 | -61.2946 | 53.5858 | 6.8344 | 61.7523 | 61.7432 | 61.7706 | -61.3266 | -0.20599 | 0.036621 | 1.5472 | -0.22888 | -8.1802 | -0.26093 | 0.004578 | 1.7532 | 122.818 | 122.8088 | 114.6515 | 122.8683 | 1.5472 | 122.8363 | 67.9001 | -0.26093 | 122.8683 | 1.5472 | 67.9001 | 114.6515 | 122.8363 | -123.0377 | -123.0927
1999.3438 | 123.1064 | -61.0062 | 61.7889 | -0.21011 | 0.019865 | 0.0097476 | 0.018128 | 0.056693 | -0.0032065 | 0.085699 | -59.4131 | 61.7477 | -61.2305 | -61.171 | 53.7231 | 6.9305 | 61.7249 | 61.9217 | 61.7706 | -61.2717 | -0.2243 | -0.041198 | 1.593 | -0.16479 | -8.0658 | -0.2655 | -0.01831 | 1.8173 | 122.731 | 122.9279 | 114.7293 | 122.7539 | 1.593 | 122.7768 | 67.9367 | -0.2655 | 122.7539 | 1.593 | 67.9367 | 114.7293 | 122.7768 | -123.0194 | -123.0606
2000.3281 | 123.1155 | -61.0382 | 61.7661 | 0.24002 | 0.020933 | 0.016156 | 0.020905 | 0.060111 | -0.0025657 | 0.085913 | -59.4452 | 61.7477 | -61.2579 | -61.1298 | 53.746 | 7.0221 | 61.615 | 61.8851 | 61.7477 | -61.2762 | -0.21973 | -0.01831 | 1.593 | -0.091553 | -8.02 | -0.23804 | -0.01831 | 1.8127 | 122.6532 | 122.9233 | 114.7842 | 122.7859 | 1.593 | 122.7859 | 68.0603 | -0.23804 | 122.7859 | 1.593 | 68.0603 | 114.7842 | 122.7859 | -123.024 | -123.0423
2001.3281 | 123.1659 | -61.0474 | 61.7249 | 0.29343 | 0.021147 | 0.014875 | 0.025178 | 0.058616 | -0.0010703 | 0.088904 | -59.4543 | 61.7477 | -61.2488 | -61.2167 | 53.6179 | 6.9397 | 61.6287 | 61.8347 | 61.7569 | -61.3174 | -0.20142 | 0.022888 | 1.593 | -0.16937 | -8.107 | -0.27008 | 0.032043 | 1.7944 | 122.6761 | 122.8821 | 114.6652 | 122.7951 | 1.593 | 122.8043 | 67.9871 | -0.27008 | 122.7951 | 1.593 | 67.9871 | 114.6652 | 122.8043 | -122.9736 | -123.0423
2002.3281 | 123.1155 | -61.0428 | 61.7569 | 0.25528 | 0.022001 | 0.01167 | 0.023896 | 0.057762 | -0.0021383 | 0.085058 | -59.4818 | 61.7523 | -61.2579 | -61.2534 | 53.6224 | 6.9214 | 61.6608 | 61.821 | 61.734 | -61.29 | -0.21515 | -0.004578 | 1.561 | -0.21057 | -8.1345 | -0.24719 | -0.022888 | 1.7761 | 122.7036 | 122.8638 | 114.6652 | 122.7951 | 1.561 | 122.7768 | 67.9642 | -0.24719 | 122.7951 | 1.561 | 67.9642 | 114.6652 | 122.7768 | -123.0148 | -123.0469
2003.3281 | 123.0789 | -61.0565 | 61.7523 | 0.23239 | 0.02371 | 0.012738 | 0.025819 | 0.059043 | -0.0012839 | 0.085486 | -59.5184 | 61.8118 | -61.2625 | -61.2671 | 53.6316 | 6.8298 | 61.6837 | 61.7889 | 61.7661 | -61.3129 | -0.20599 | 0.05951 | 1.5381 | -0.21057 | -8.1207 | -0.25635 | 0.013733 | 1.7441 | 122.7402 | 122.8455 | 114.6881 | 122.8683 | 1.5381 | 122.8226 | 67.8864 | -0.25635 | 122.8683 | 1.5381 | 67.8864 | 114.6881 | 122.8226 | -123.0148 | -123.0652
2004.3281 | 122.9965 | -61.0382 | 61.821 | -0.16434 | 0.020933 | 0.010602 | 0.021119 | 0.057975 | -0.0025657 | 0.08869 | -59.4681 | 61.7935 | -61.2396 | -61.2579 | 53.595 | 6.8985 | 61.8576 | 61.8256 | 61.8118 | -61.3174 | -0.20142 | -0.027466 | 1.5701 | -0.21973 | -8.226 | -0.27924 | -0.009155 | 1.7715 | 122.8958 | 122.8638 | 114.6332 | 122.8317 | 1.5701 | 122.85 | 67.9367 | -0.27924 | 122.8317 | 1.5701 | 67.9367 | 114.6332 | 122.85 | -123.0606 | -123.1384
2005.3281 | 123.0515 | -61.0611 | 61.7661 | 0.21713 | 0.022428 | 0.011457 | 0.023469 | 0.059471 | -0.0017111 | 0.088049 | -59.5459 | 61.8118 | -61.3037 | -61.2946 | 53.5309 | 6.8436 | 61.7432 | 61.7523 | 61.7706 | -61.3403 | -0.24262 | 0.045777 | 1.5152 | -0.23346 | -8.2352 | -0.27924 | 0.004578 | 1.7578 | 122.8043 | 122.8134 | 114.592 | 122.8729 | 1.5152 | 122.8317 | 67.9047 | -0.27924 | 122.8729 | 1.5152 | 67.9047 | 114.592 | 122.8317 | -123.0698 | -123.1064
2006.3281 | 123.0377 | -61.0703 | 61.7798 | 0.18662 | 0.020292 | 0.010816 | 0.025178 | 0.059257 | 0.0012795 | 0.086554 | -59.5322 | 61.8073 | -61.2762 | -61.3174 | 53.54 | 6.839 | 61.7752 | 61.7203 | 61.7981 | -61.3266 | -0.20599 | 0.027466 | 1.5381 | -0.24719 | -8.2397 | -0.25635 | 0.018311 | 1.7441 | 122.8455 | 122.7905 | 114.6103 | 122.8775 | 1.5381 | 122.8683 | 67.9092 | -0.25635 | 122.8775 | 1.5381 | 67.9092 | 114.6103 | 122.8683 | -123.056 | -123.1064
2007.3281 | 123.0743 | -61.0611 | 61.7569 | 0.22476 | 0.022428 | 0.0082522 | 0.022187 | 0.060752 | -0.0017111 | 0.086126 | -59.5001 | 61.7798 | -61.2671 | -61.2762 | 53.5767 | 6.8848 | 61.6928 | 61.7752 | 61.7706 | -61.3129 | -0.20599 | 0.022888 | 1.561 | -0.21515 | -8.1802 | -0.25177 | 0.013733 | 1.767 | 122.7539 | 122.8363 | 114.6378 | 122.8409 | 1.561 | 122.8317 | 67.9459 | -0.25177 | 122.8409 | 1.561 | 67.9459 | 114.6378 | 122.8317 | -123.024 | -123.0698
2008.3281 | 123.0515 | -61.0428 | 61.7523 | 0.19424 | 0.020933 | 0.010175 | 0.023041 | 0.061607 | -0.0014975 | 0.085913 | -59.5093 | 61.8118 | -61.2717 | -61.2808 | 53.5446 | 6.8253 | 61.7294 | 61.7661 | 61.7477 | -61.322 | -0.22888 | 0.05951 | 1.5335 | -0.23804 | -8.2077 | -0.27923 | -0.004577 | 1.7624 | 122.7722 | 122.8088 | 114.5874 | 122.8546 | 1.5335 | 122.7905 | 67.868 | -0.27923 | 122.8546 | 1.5335 | 67.868 | 114.5874 | 122.7905 | -123.024 | -123.0743
2009.3281 | 123.0377 | -61.0382 | 61.7569 | 0.18662 | 0.024137 | 0.014661 | 0.021332 | 0.058616 | -0.0010703 | 0.088263 | -59.5322 | 61.8393 | -61.2946 | -61.2854 | 53.54 | 6.8436 | 61.7432 | 61.7569 | 61.7798 | -61.322 | -0.25635 | 0.082397 | 1.506 | -0.24719 | -8.2169 | -0.28381 | 0.022888 | 1.7624 | 122.7814 | 122.7951 | 114.5782 | 122.8775 | 1.506 | 122.818 | 67.8818 | -0.28381 | 122.8775 | 1.506 | 67.8818 | 114.5782 | 122.818 | -123.0515 | -123.0789
2010.3281 | 123.0331 | -61.0291 | 61.7981 | 0.18662 | 0.023924 | 0.010816 | 0.024323 | 0.058189 | -0.0019247 | 0.088049 | -59.5505 | 61.853 | -61.2579 | -61.3083 | 53.508 | 6.7429 | 61.7798 | 61.734 | 61.8073 | -61.3266 | -0.22888 | 0.054931 | 1.4786 | -0.27924 | -8.2901 | -0.29755 | 0.009155 | 1.7075 | 122.8088 | 122.7631 | 114.537 | 122.8821 | 1.4786 | 122.8363 | 67.7719 | -0.29755 | 122.8821 | 1.4786 | 67.7719 | 114.537 | 122.8363 | -123.056 | -123.1247
2011.3281 | 123.024 | -61.0428 | 61.7661 | 0.17899 | 0.023069 | 0.0084658 | 0.024964 | 0.059043 | 0.0012795 | 0.084204 | -59.5367 | 61.8347 | -61.2717 | -61.3266 | 53.5172 | 6.8024 | 61.7935 | 61.7249 | 61.8073 | -61.3358 | -0.22888 | 0.068665 | 1.506 | -0.28381 | -8.2489 | -0.29297 | 0.041199 | 1.7349 | 122.8363 | 122.7676 | 114.5599 | 122.8775 | 1.506 | 122.85 | 67.8452 | -0.29297 | 122.8775 | 1.506 | 67.8452 | 114.5599 | 122.85 | -123.0377 | -123.1018
2012.3281 | 123.0057 | -61.0657 | 61.7981 | 0.2095 | 0.02136 | 0.0063296 | 0.025391 | 0.059257 | -0.00085669 | 0.087195 | -59.5276 | 61.821 | -61.2625 | -61.3083 | 53.5034 | 6.7612 | 61.8164 | 61.7432 | 61.8164 | -61.3037 | -0.19684 | 0.022888 | 1.5381 | -0.24262 | -8.2947 | -0.23804 | 0.01831 | 1.7349 | 122.8821 | 122.8088 | 114.5691 | 122.8867 | 1.5381 | 122.8821 | 67.8268 | -0.23804 | 122.8867 | 1.5381 | 67.8268 | 114.5691 | 122.8821 | -123.0606 | -123.1018
2013.3281 | 122.9874 | -61.0886 | 61.8073 | -0.0041198 | 0.024992 | 0.009534 | 0.021119 | 0.062034 | -0.0032065 | 0.08869 | -59.5322 | 61.8393 | -61.2671 | -61.322 | 53.4714 | 6.7749 | 61.8118 | 61.7249 | 61.7889 | -61.3358 | -0.17853 | 0.032043 | 1.5564 | -0.23346 | -8.3359 | -0.24719 | -0.018311 | 1.7349 | 122.9004 | 122.8134 | 114.5599 | 122.9279 | 1.5564 | 122.8775 | 67.8635 | -0.24719 | 122.9279 | 1.5564 | 67.8635 | 114.5599 | 122.8775 | -123.0743 | -123.143
2014.3281 | 123.0606 | -61.0611 | 61.7706 | 0.22476 | 0.025846 | 0.01402 | 0.023682 | 0.060966 | -0.00085669 | 0.089758 | -59.523 | 61.8439 | -61.2854 | -61.3312 | 53.4988 | 6.7291 | 61.7661 | 61.7294 | 61.7889 | -61.3312 | -0.2243 | 0.073242 | 1.5381 | -0.27008 | -8.2718 | -0.27008 | 0.01831 | 1.7624 | 122.8271 | 122.7905 | 114.5599 | 122.905 | 1.5381 | 122.85 | 67.7902 | -0.27008 | 122.905 | 1.5381 | 67.7902 | 114.5599 | 122.85 | -123.056 | -123.1018
2015.3281 | 123.024 | -61.0474 | 61.8027 | 0.18662 | 0.022642 | 0.01167 | 0.02411 | 0.058616 | -0.00021569 | 0.08634 | -59.5596 | 61.8347 | -61.2717 | -61.322 | 53.4988 | 6.665 | 61.7844 | 61.734 | 61.7569 | -61.3495 | -0.2243 | 0.032044 | 1.4877 | -0.27466 | -8.3038 | -0.30212 | -0.045776 | 1.712 | 122.8317 | 122.7814 | 114.5462 | 122.8821 | 1.4877 | 122.8043 | 67.7124 | -0.30212 | 122.8821 | 1.4877 | 67.7124 | 114.5462 | 122.8043 | -123.0743 | -123.1522
2016.3281 | 123.0194 | -61.0794 | 61.7798 | 0.21713 | 0.023283 | 0.011243 | 0.02176 | 0.059898 | 0.00021151 | 0.087835 | -59.5551 | 61.8439 | -61.3037 | -61.3449 | 53.4668 | 6.7017 | 61.8027 | 61.7157 | 61.7844 | -61.3129 | -0.2243 | 0.064087 | 1.5244 | -0.2655 | -8.313 | -0.23346 | 0.004578 | 1.7487 | 122.8821 | 122.7951 | 114.5462 | 122.9233 | 1.5244 | 122.8638 | 67.7811 | -0.23346 | 122.9233 | 1.5244 | 67.7811 | 114.5462 | 122.8638 | -123.0835 | -123.0927
2017.3281 | 122.9828 | -61.0977 | 61.7569 | 0.20187 | 0.023283 | 0.011457 | 0.023896 | 0.059898 | -0.0012839 | 0.088904 | -59.5551 | 61.8164 | -61.2854 | -61.3586 | 53.4302 | 6.7474 | 61.8027 | 61.7065 | 61.7889 | -61.3495 | -0.18768 | 0.059509 | 1.5427 | -0.26093 | -8.3267 | -0.25177 | 0.032043 | 1.7303 | 122.9004 | 122.8043 | 114.5279 | 122.9141 | 1.5427 | 122.8867 | 67.8452 | -0.25177 | 122.9141 | 1.5427 | 67.8452 | 114.5279 | 122.8867 | -123.0423 | -123.1064
2018.3438 | 123.1064 | -60.997 | 61.7661 | -0.13382 | 0.018797 | 0.011029 | 0.015137 | 0.060325 | -0.0012839 | 0.087835 | -59.4681 | 61.7477 | -61.2488 | -61.2762 | 53.54 | 6.9626 | 61.6562 | 61.8988 | 61.7615 | -61.2442 | -0.25177 | -0.01831 | 1.5289 | -0.27924 | -8.226 | -0.24719 | -0.004577 | 1.7807 | 122.6532 | 122.8958 | 114.537 | 122.7448 | 1.5289 | 122.7585 | 67.9596 | -0.24719 | 122.7448 | 1.5289 | 67.9596 | 114.537 | 122.7585 | -123.0148 | -123.0103
2019.3281 | 123.0148 | -61.0703 | 61.7981 | 0.10269 | 0.026274 | 0.0086796 | 0.02475 | 0.059043 | -0.00085669 | 0.086554 | -59.6786 | 61.7889 | -61.29 | -61.3083 | 53.4668 | 6.7657 | 61.7844 | 61.7203 | 61.7752 | -61.3495 | -0.21973 | -0.009156 | 1.3916 | -0.23804 | -8.3313 | -0.27924 | -0.022888 | 1.6113 | 122.8546 | 122.7905 | 114.537 | 122.8592 | 1.3916 | 122.8455 | 67.836 | -0.27924 | 122.8592 | 1.3916 | 67.836 | 114.537 | 122.8455 | -123.0881 | -123.1476
2020.3438 | 123.0835 | -61.0703 | 61.7432 | 0.22476 | 0.022215 | 0.0080386 | 0.023682 | 0.05883 | -2.092e-06 | 0.087622 | -59.5276 | 61.8118 | -61.2488 | -61.2579 | 53.508 | 6.7932 | 61.6699 | 61.8164 | 61.7706 | -61.322 | -0.17853 | 0.068665 | 1.5427 | -0.18768 | -8.2352 | -0.25177 | 0.027466 | 1.7212 | 122.7402 | 122.8867 | 114.5782 | 122.8821 | 1.5427 | 122.8409 | 67.8635 | -0.25177 | 122.8821 | 1.5427 | 67.8635 | 114.5782 | 122.8409 | -122.9919 | -123.0652
2021.3281 | 123.0103 | -61.0794 | 61.7569 | 0.12558 | 0.023924 | 0.013166 | 0.023896 | 0.058189 | -0.0010703 | 0.086981 | -59.5505 | 61.821 | -61.2717 | -61.3358 | 53.4622 | 6.72 | 61.7844 | 61.7157 | 61.7981 | -61.322 | -0.19226 | 0.064087 | 1.5289 | -0.25635 | -8.2947 | -0.24261 | 0.041199 | 1.7212 | 122.8638 | 122.7951 | 114.5416 | 122.9004 | 1.5289 | 122.8775 | 67.7994 | -0.24261 | 122.9004 | 1.5289 | 67.7994 | 114.5416 | 122.8775 | -123.0286 | -123.0789
2022.3281 | 122.9919 | -61.0886 | 61.7706 | 0.11795 | 0.022642 | 0.013379 | 0.024323 | 0.059471 | -0.0010703 | 0.086981 | -59.5505 | 61.8393 | -61.2854 | -61.3449 | 53.4622 | 6.7978 | 61.8073 | 61.7111 | 61.7569 | -61.3358 | -0.19684 | 0.068664 | 1.5381 | -0.25635 | -8.3084 | -0.24719 | -0.013733 | 1.7349 | 122.8958 | 122.7997 | 114.5508 | 122.9279 | 1.5381 | 122.8455 | 67.8864 | -0.24719 | 122.9279 | 1.5381 | 67.8864 | 114.5508 | 122.8455 | -123.056 | -123.1064
2023.3281 | 123.0057 | -61.0886 | 61.7752 | 0.011139 | 0.023924 | 0.010388 | 0.02411 | 0.059684 | -0.00021569 | 0.087195 | -59.5459 | 61.8347 | -61.2442 | -61.3403 | 53.421 | 6.7291 | 61.8301 | 61.7111 | 61.8027 | -61.3495 | -0.15564 | 0.059509 | 1.5427 | -0.25177 | -8.3542 | -0.26093 | 0.027465 | 1.6983 | 122.9187 | 122.7997 | 114.5096 | 122.9233 | 1.5427 | 122.8912 | 67.8177 | -0.26093 | 122.9233 | 1.5427 | 67.8177 | 114.5096 | 122.8912 | -123.0194 | -123.1247
2024.3281 | 123.0057 | -61.0657 | 61.7752 | 0.23239 | 0.021147 | 0.01167 | 0.023682 | 0.06118 | -0.0010703 | 0.087408 | -59.4223 | 61.8576 | -61.2534 | -61.3083 | 53.4485 | 6.6833 | 61.8256 | 61.7157 | 61.8256 | -61.3312 | -0.18768 | 0.082397 | 1.6434 | -0.24262 | -8.3267 | -0.2655 | 0.050354 | 1.8311 | 122.8912 | 122.7814 | 114.5142 | 122.9233 | 1.6434 | 122.8912 | 67.749 | -0.2655 | 122.9233 | 1.6434 | 67.749 | 114.5142 | 122.8912 | -123.0286 | -123.1064
2025.3281 | 123.0331 | -61.0519 | 61.7889 | 0.041657 | 0.023283 | 0.013166 | 0.026887 | 0.060111 | -2.092e-06 | 0.088904 | -59.4681 | 61.8301 | -61.2579 | -61.2534 | 53.5492 | 6.72 | 61.7935 | 61.7935 | 61.8164 | -61.3083 | -0.20599 | 0.041199 | 1.5839 | -0.20142 | -8.2397 | -0.25635 | 0.027466 | 1.7899 | 122.8455 | 122.8455 | 114.6011 | 122.8821 | 1.5839 | 122.8683 | 67.7719 | -0.25635 | 122.8821 | 1.5839 | 67.7719 | 114.6011 | 122.8683 | -123.0469 | -123.0972
2026.3281 | 123.0148 | -61.0611 | 61.7981 | 0.041657 | 0.021787 | 0.015088 | 0.023469 | 0.062675 | -0.0021383 | 0.087835 | -59.5139 | 61.8484 | -61.2671 | -61.2717 | 53.5034 | 6.6879 | 61.8118 | 61.7615 | 61.8164 | -61.3129 | -0.20599 | 0.050354 | 1.5472 | -0.21057 | -8.2947 | -0.25177 | 0.01831 | 1.7532 | 122.8729 | 122.8226 | 114.5645 | 122.9095 | 1.5472 | 122.8775 | 67.749 | -0.25177 | 122.9095 | 1.5472 | 67.749 | 114.5645 | 122.8775 | -123.0652 | -123.111
2027.3281 | 122.7905 | -61.0886 | 61.7661 | 0.14084 | 0.024778 | 0.01167 | 0.024323 | 0.061607 | -0.00021569 | 0.088904 | -59.5322 | 61.8439 | -61.2808 | -61.3358 | 53.4439 | 6.7108 | 61.8484 | 61.702 | 61.7935 | -61.3586 | -0.19226 | 0.07782 | 1.5564 | -0.24719 | -8.3221 | -0.27008 | 0.027466 | 1.7487 | 122.937 | 122.7905 | 114.5325 | 122.9324 | 1.5564 | 122.8821 | 67.7994 | -0.27008 | 122.9324 | 1.5564 | 67.7994 | 114.5325 | 122.8821 | -123.0469 | -123.1247
2028.3281 | 122.9965 | -61.0794 | 61.7752 | 0.20187 | 0.02371 | 0.007825 | 0.025391 | 0.062461 | -0.0014975 | 0.087622 | -59.5596 | 61.8576 | -61.2808 | -61.3266 | 53.4439 | 6.7657 | 61.8164 | 61.6974 | 61.8073 | -61.3449 | -0.20142 | 0.082397 | 1.5198 | -0.24719 | -8.3313 | -0.2655 | 0.032043 | 1.7212 | 122.8958 | 122.7768 | 114.5233 | 122.937 | 1.5198 | 122.8867 | 67.8452 | -0.2655 | 122.937 | 1.5198 | 67.8452 | 114.5233 | 122.8867 | -123.056 | -123.1201
2029.3281 | 123.0148 | -61.0703 | 61.7844 | -0.011749 | 0.023069 | 0.010816 | 0.023682 | 0.061607 | -0.0023519 | 0.089331 | -59.5642 | 61.8576 | -61.29 | -61.3449 | 53.421 | 6.6879 | 61.8164 | 61.7065 | 61.8164 | -61.3449 | -0.21973 | 0.073242 | 1.506 | -0.27466 | -8.3633 | -0.27466 | 0.032043 | 1.7258 | 122.8867 | 122.7768 | 114.4913 | 122.9279 | 1.506 | 122.8867 | 67.7582 | -0.27466 | 122.9279 | 1.506 | 67.7582 | 114.4913 | 122.8867 | -123.0743 | -123.1293
2030.3281 | 123.0057 | -61.0336 | 61.8164 | 0.049286 | 0.023283 | 0.010816 | 0.024964 | 0.060752 | -0.0025657 | 0.088263 | -59.5322 | 61.8668 | -61.2579 | -61.3129 | 53.4714 | 6.6879 | 61.8347 | 61.7157 | 61.8301 | -61.3083 | -0.22431 | 0.050354 | 1.5015 | -0.27924 | -8.345 | -0.27466 | 0.013733 | 1.7258 | 122.8683 | 122.7493 | 114.505 | 122.9004 | 1.5015 | 122.8638 | 67.7216 | -0.27466 | 122.9004 | 1.5015 | 67.7216 | 114.505 | 122.8638 | -123.0743 | -123.1247
2031.3281 | 123.0057 | -61.0703 | 61.7889 | 0.072174 | 0.025419 | 0.012738 | 0.02411 | 0.060111 | -0.0021383 | 0.087835 | -59.4955 | 61.8622 | -61.2717 | -61.3083 | 53.4851 | 6.7749 | 61.8393 | 61.7386 | 61.8256 | -61.3312 | -0.20142 | 0.073243 | 1.5747 | -0.23804 | -8.3038 | -0.26093 | 0.036622 | 1.7761 | 122.9095 | 122.8088 | 114.5554 | 122.9324 | 1.5747 | 122.8958 | 67.8452 | -0.26093 | 122.9324 | 1.5747 | 67.8452 | 114.5554 | 122.8958 | -123.0606 | -123.1201
2032.3281 | 122.9691 | -61.0657 | 61.7981 | 0.034027 | 0.022001 | 0.010388 | 0.023682 | 0.060966 | -0.0010703 | 0.088904 | -59.5184 | 61.8484 | -61.2671 | -61.3174 | 53.4485 | 6.8069 | 61.8347 | 61.7523 | 61.8484 | -61.3495 | -0.20142 | 0.050354 | 1.5472 | -0.25177 | -8.3496 | -0.28381 | 0.050354 | 1.7487 | 122.9004 | 122.818 | 114.5142 | 122.9141 | 1.5472 | 122.9141 | 67.8726 | -0.28381 | 122.9141 | 1.5472 | 67.8726 | 114.5142 | 122.9141 | -123.0652 | -123.1476
2033.3281 | 122.9919 | -61.0611 | 61.7798 | 0.16373 | 0.02136 | 0.013166 | 0.023896 | 0.062034 | -0.0010703 | 0.088263 | -59.5505 | 61.8484 | -61.2854 | -61.3312 | 53.0914 | 6.5323 | 62.1964 | 61.8347 | 61.8439 | -61.3083 | -0.2243 | 0.068665 | 1.5106 | -0.27008 | -8.6884 | -0.24719 | 0.064087 | 1.7349 | 123.2574 | 122.8958 | 114.1525 | 122.9095 | 1.5106 | 122.905 | 67.5934 | -0.24719 | 122.9095 | 1.5106 | 67.5934 | 114.1525 | 122.905 | -123.0652 | -123.0881
2034.3281 | 123.0148 | -61.0565 | 61.7844 | 0.2095 | 0.023069 | 0.013379 | 0.024964 | 0.060111 | -0.0017111 | 0.087408 | -59.5367 | 61.8576 | -61.2579 | -61.3358 | 53.4622 | 6.7657 | 61.7981 | 61.7294 | 61.8393 | -61.3266 | -0.20142 | 0.073242 | 1.5198 | -0.27923 | -8.3221 | -0.27008 | 0.054931 | 1.7212 | 122.8546 | 122.7859 | 114.5187 | 122.9141 | 1.5198 | 122.8958 | 67.8223 | -0.27008 | 122.9141 | 1.5198 | 67.8223 | 114.5187 | 122.8958 | -123.0423 | -123.111
2035.3281 | 122.9965 | -61.0611 | 61.7889 | 0.20187 | 0.024351 | 0.010175 | 0.02411 | 0.063529 | 0.00042511 | 0.088263 | -59.5459 | 61.8393 | -61.2854 | -61.3312 | 53.5034 | 6.7932 | 61.8256 | 61.7386 | 61.8164 | -61.3266 | -0.2243 | 0.050354 | 1.5152 | -0.27008 | -8.2855 | -0.2655 | 0.027466 | 1.7395 | 122.8867 | 122.7997 | 114.5645 | 122.9004 | 1.5152 | 122.8775 | 67.8543 | -0.2655 | 122.9004 | 1.5152 | 67.8543 | 114.5645 | 122.8775 | -123.0743 | -123.1155
2036.3281 | 122.9919 | -61.0382 | 61.7798 | -0.034637 | 0.021787 | 0.013593 | 0.024537 | 0.059684 | -0.0021383 | 0.086767 | -59.5596 | 61.8622 | -61.2717 | -61.322 | 53.4668 | 6.7703 | 61.8484 | 61.7386 | 61.8393 | -61.3358 | -0.23346 | 0.082398 | 1.4786 | -0.28381 | -8.313 | -0.29755 | 0.059509 | 1.712 | 122.8867 | 122.7768 | 114.505 | 122.9004 | 1.4786 | 122.8775 | 67.8085 | -0.29755 | 122.9004 | 1.4786 | 67.8085 | 114.505 | 122.8775 | -123.0515 | -123.1155
2037.3281 | 122.9874 | -61.0657 | 61.8118 | 0.5452 | 0.022001 | 0.014875 | 0.024964 | 0.062034 | -0.00042929 | 0.088476 | -59.491 | 61.8851 | -61.2534 | -61.3449 | 53.4851 | 6.7245 | 61.853 | 61.7477 | 61.8256 | -61.3312 | -0.18768 | 0.073242 | 1.5747 | -0.27924 | -8.3267 | -0.2655 | 0.013733 | 1.7624 | 122.9187 | 122.8134 | 114.5508 | 122.9507 | 1.5747 | 122.8912 | 67.7902 | -0.2655 | 122.9507 | 1.5747 | 67.7902 | 114.5508 | 122.8912 | -123.0652 | -123.143
2038.3438 | 123.024 | -61.0336 | 61.8301 | -0.16434 | 0.022215 | 0.010602 | 0.022187 | 0.058616 | -0.0025657 | 0.085486 | -59.5184 | 61.8484 | -61.2717 | -61.2808 | 53.5034 | 6.7749 | 61.9034 | 61.8027 | 61.8668 | -61.2808 | -0.23804 | 0.018311 | 1.5152 | -0.24719 | -8.3267 | -0.24719 | 0.036621 | 1.7532 | 122.937 | 122.8363 | 114.537 | 122.8821 | 1.5152 | 122.9004 | 67.8085 | -0.24719 | 122.8821 | 1.5152 | 67.8085 | 114.537 | 122.9004 | -123.1018 | -123.111
2039.3281 | 122.9965 | -61.0428 | 61.8256 | 0.064545 | 0.02371 | 0.011029 | 0.026459 | 0.060111 | -0.00064309 | 0.087195 | -59.4818 | 61.8622 | -61.2442 | -61.2946 | 53.4897 | 6.72 | 61.8484 | 61.7569 | 61.853 | -61.3129 | -0.20142 | 0.036621 | 1.561 | -0.25177 | -8.3359 | -0.27008 | 0.027465 | 1.7624 | 122.8912 | 122.7997 | 114.5325 | 122.905 | 1.561 | 122.8958 | 67.7628 | -0.27008 | 122.905 | 1.561 | 67.7628 | 114.5325 | 122.8958 | -123.0698 | -123.1384
2040.3281 | 122.9965 | -61.0245 | 61.8484 | 0.13321 | 0.020506 | 0.009534 | 0.02475 | 0.060539 | -0.0034201 | 0.087622 | -59.5276 | 61.8713 | -61.2442 | -61.5784 | 53.0548 | 6.5872 | 62.1002 | 61.7935 | 61.8896 | -61.322 | -0.21973 | 0.022888 | 1.4969 | -0.55389 | -8.7936 | -0.29755 | 0.041198 | 1.7166 | 123.1247 | 122.818 | 114.0793 | 122.8958 | 1.4969 | 122.9141 | 67.6117 | -0.29755 | 122.8958 | 1.4969 | 67.6117 | 114.0793 | 122.9141 | -123.0927 | -123.1705
2041.3281 | 122.9965 | -61.0611 | 61.8073 | 0.18662 | 0.022642 | 0.012311 | 0.023255 | 0.061607 | -0.0025657 | 0.086981 | -59.5322 | 61.8576 | -61.2808 | -61.3266 | 53.4485 | 6.752 | 61.8301 | 61.7477 | 61.821 | -61.322 | -0.21973 | 0.050354 | 1.5289 | -0.2655 | -8.3588 | -0.26093 | 0.013733 | 1.7487 | 122.8912 | 122.8088 | 114.5096 | 122.9187 | 1.5289 | 122.8821 | 67.8131 | -0.26093 | 122.9187 | 1.5289 | 67.8131 | 114.5096 | 122.8821 | -123.0881 | -123.1293
2042.3281 | 123.0057 | -61.0474 | 61.8027 | 0.21713 | 0.024137 | 0.013806 | 0.024323 | 0.060966 | -0.0014975 | 0.08869 | -59.5322 | 61.8805 | -61.2534 | -61.3129 | 53.4576 | 6.5964 | 61.853 | 61.7294 | 61.8301 | -61.3174 | -0.20599 | 0.07782 | 1.5152 | -0.2655 | -8.345 | -0.27008 | 0.027466 | 1.7212 | 122.9004 | 122.7768 | 114.505 | 122.9279 | 1.5152 | 122.8775 | 67.6437 | -0.27008 | 122.9279 | 1.5152 | 67.6437 | 114.505 | 122.8775 | -123.056 | -123.1201
2043.3281 | 123.0194 | -61.0474 | 61.821 | 0.087433 | 0.02371 | 0.013593 | 0.02411 | 0.060111 | -0.00085669 | 0.087195 | -59.4772 | 61.8484 | -61.2579 | -61.3129 | 53.5034 | 6.633 | 61.853 | 61.7477 | 61.8576 | -61.3358 | -0.21057 | 0.027466 | 1.5701 | -0.2655 | -8.3176 | -0.28839 | 0.036621 | 1.7807 | 122.9004 | 122.7951 | 114.5508 | 122.8958 | 1.5701 | 122.905 | 67.6804 | -0.28839 | 122.8958 | 1.5701 | 67.6804 | 114.5508 | 122.905 | -123.0789 | -123.1567
2044.3281 | 122.9965 | -61.0703 | 61.8256 | 0.75119 | 0.02606 | 0.0084658 | 0.02411 | 0.060752 | -0.0036337 | 0.086981 | -59.697 | 61.8164 | -61.2762 | -61.2808 | 53.476 | 6.7337 | 61.8256 | 61.734 | 61.8484 | -61.2991 | -0.20599 | -0.009156 | 1.3733 | -0.21057 | -8.3496 | -0.22888 | 0.022888 | 1.5793 | 122.8958 | 122.8043 | 114.5462 | 122.8867 | 1.3733 | 122.9187 | 67.804 | -0.22888 | 122.8867 | 1.3733 | 67.804 | 114.5462 | 122.9187 | -123.1018 | -123.1247
2045.3281 | 123.0057 | -61.0428 | 61.8301 | 0.18662 | 0.023283 | 0.010175 | 0.022828 | 0.060752 | 0.0014933 | 0.08869 | -59.523 | 61.8851 | -61.2534 | -61.5555 | 53.7415 | 6.8481 | 61.9446 | 61.8027 | 61.8759 | -61.2991 | -0.21057 | 0.054932 | 1.5198 | -0.5127 | -8.0887 | -0.25635 | 0.045777 | 1.7303 | 122.9874 | 122.8455 | 114.7842 | 122.9279 | 1.5198 | 122.9187 | 67.8909 | -0.25635 | 122.9279 | 1.5198 | 67.8909 | 114.7842 | 122.9187 | -123.0835 | -123.1293
2046.3281 | 122.9919 | -61.0382 | 61.8073 | 0.034027 | 0.023496 | 0.010816 | 0.023255 | 0.062675 | -0.0025657 | 0.08869 | -59.4681 | 61.8851 | -61.235 | -61.2488 | 53.4851 | 6.7474 | 61.8576 | 61.8027 | 61.8668 | -61.2991 | -0.19684 | 0.07782 | 1.5701 | -0.21057 | -8.3221 | -0.26093 | 0.059509 | 1.767 | 122.8958 | 122.8409 | 114.5233 | 122.9233 | 1.5701 | 122.905 | 67.7856 | -0.26093 | 122.9233 | 1.5701 | 67.7856 | 114.5233 | 122.905 | -123.0423 | -123.1064
2047.3281 | 123.0011 | -61.0474 | 61.8256 | 0.19424 | 0.023496 | 0.013593 | 0.02475 | 0.062675 | -0.0029929 | 0.088049 | -59.523 | 61.8576 | -61.2625 | -61.3129 | 53.4668 | 6.7062 | 61.853 | 61.7249 | 61.8668 | -61.322 | -0.21515 | 0.032043 | 1.5244 | -0.2655 | -8.3588 | -0.27466 | 0.041198 | 1.7395 | 122.9004 | 122.7722 | 114.5142 | 122.905 | 1.5244 | 122.9141 | 67.7536 | -0.27466 | 122.905 | 1.5244 | 67.7536 | 114.5142 | 122.9141 | -123.0881 | -123.1476
2048.3281 | 123.0057 | -61.0519 | 61.8073 | 0.049286 | 0.022215 | 0.014875 | 0.02411 | 0.061607 | 0.00021151 | 0.085486 | -59.5413 | 61.9034 | -61.2442 | -61.3129 | 53.4714 | 6.7108 | 61.8301 | 61.7249 | 61.8713 | -61.3312 | -0.19226 | 0.09613 | 1.5106 | -0.26093 | -8.3359 | -0.27924 | 0.064087 | 1.7029 | 122.8821 | 122.7768 | 114.5233 | 122.9553 | 1.5106 | 122.9233 | 67.7628 | -0.27924 | 122.9553 | 1.5106 | 67.7628 | 114.5233 | 122.9233 | -123.0515 | -123.1384
2049.3281 | 122.9691 | -61.0611 | 61.8027 | 0.1561 | 0.023924 | 0.011884 | 0.020264 | 0.060111 | -0.00042929 | 0.086554 | -59.5322 | 61.8622 | -61.2625 | -61.2946 | 53.4668 | 6.6605 | 61.8713 | 61.7523 | 61.8896 | -61.3083 | -0.20142 | 0.05951 | 1.5289 | -0.23346 | -8.3359 | -0.24719 | 0.086975 | 1.7303 | 122.9324 | 122.8134 | 114.5279 | 122.9233 | 1.5289 | 122.9507 | 67.7216 | -0.24719 | 122.9233 | 1.5289 | 67.7216 | 114.5279 | 122.9507 | -123.0652 | -123.111
2050.3281 | 123.0194 | -61.0336 | 61.8256 | 0.13321 | 0.022215 | 0.012097 | 0.025819 | 0.060966 | -0.0027793 | 0.086981 | -59.523 | 61.9034 | -61.2442 | -61.322 | 53.4805 | 6.7291 | 61.5005 | 61.3861 | 61.7889 | -61.3358 | -0.21057 | 0.077819 | 1.5106 | -0.28839 | -8.345 | -0.30212 | -0.036622 | 1.7212 | 122.5342 | 122.4197 | 114.5142 | 122.937 | 1.5106 | 122.8226 | 67.7628 | -0.30212 | 122.937 | 1.5106 | 67.7628 | 114.5142 | 122.8226 | -123.0698 | -123.1613
2051.3281 | 123.0011 | -61.0291 | 61.8256 | 0.11795 | 0.02371 | 0.012525 | 0.025391 | 0.060539 | -0.0012839 | 0.089331 | -59.5047 | 61.8851 | -61.2305 | -61.2808 | 53.5172 | 6.6696 | 61.8851 | 61.7477 | 61.8713 | -61.3312 | -0.20142 | 0.059509 | 1.5244 | -0.25177 | -8.3084 | -0.30212 | 0.045776 | 1.7258 | 122.9141 | 122.7768 | 114.5462 | 122.9141 | 1.5244 | 122.9004 | 67.6987 | -0.30212 | 122.9141 | 1.5244 | 67.6987 | 114.5462 | 122.9004 | -123.056 | -123.1567
2052.3281 | 123.0057 | -61.0565 | 61.8301 | 0.056915 | 0.024778 | 0.011884 | 0.024964 | 0.060752 | -0.00064309 | 0.087622 | -59.4864 | 61.8805 | -61.2442 | -61.29 | 53.5034 | 6.7566 | 61.8759 | 61.7477 | 61.853 | -61.2991 | -0.18768 | 0.050354 | 1.5701 | -0.23346 | -8.3267 | -0.24261 | 0.022888 | 1.7578 | 122.9324 | 122.8043 | 114.5599 | 122.937 | 1.5701 | 122.9095 | 67.8131 | -0.24261 | 122.937 | 1.5701 | 67.8131 | 114.5599 | 122.9095 | -123.0743 | -123.1293
2053.3281 | 123.024 | -61.0153 | 61.821 | 0.056915 | 0.023496 | 0.013166 | 0.02475 | 0.06182 | -0.0029929 | 0.090613 | -59.4818 | 61.9171 | -61.235 | -61.2717 | 53.4897 | 6.6971 | 61.8668 | 61.7752 | 61.853 | -61.3083 | -0.21973 | 0.09613 | 1.5335 | -0.25635 | -8.3313 | -0.29297 | 0.032043 | 1.7532 | 122.8821 | 122.7905 | 114.505 | 122.9324 | 1.5335 | 122.8683 | 67.7124 | -0.29297 | 122.9324 | 1.5335 | 67.7124 | 114.505 | 122.8683 | -123.056 | -123.1293
2054.3281 | 123.0103 | -61.0199 | 61.8118 | 0.041657 | 0.021147 | 0.011029 | 0.025178 | 0.060325 | -0.0040609 | 0.087622 | -59.4681 | 61.8942 | -61.2259 | -61.2717 | 53.476 | 6.6193 | 61.8668 | 61.7889 | 61.8576 | -61.3083 | -0.20599 | 0.082397 | 1.5518 | -0.25177 | -8.3359 | -0.28839 | 0.045776 | 1.7578 | 122.8867 | 122.8088 | 114.4958 | 122.9141 | 1.5518 | 122.8775 | 67.6392 | -0.28839 | 122.9141 | 1.5518 | 67.6392 | 114.4958 | 122.8775 | -123.0377 | -123.1201
2055.3281 | 122.9874 | -61.0245 | 61.8073 | 0.079804 | 0.023924 | 0.016156 | 0.024964 | 0.062461 | -0.0051291 | 0.085913 | -59.5001 | 61.8988 | -61.2396 | -61.3083 | 53.4531 | 6.6833 | 61.8713 | 61.7477 | 61.8484 | -61.322 | -0.21515 | 0.091553 | 1.5244 | -0.28381 | -8.3542 | -0.29755 | 0.041199 | 1.7395 | 122.8958 | 122.7722 | 114.4775 | 122.9233 | 1.5244 | 122.8729 | 67.7078 | -0.29755 | 122.9233 | 1.5244 | 67.7078 | 114.4775 | 122.8729 | -123.0469 | -123.1293
2056.3281 | 123.0194 | -61.0199 | 61.8439 | 0.079804 | 0.024351 | 0.01402 | 0.025178 | 0.060752 | -0.0021383 | 0.087408 | -59.4955 | 61.8942 | -61.235 | -61.2671 | 53.4714 | 6.6879 | 61.853 | 61.7752 | 61.8805 | -61.3037 | -0.21515 | 0.050354 | 1.5244 | -0.24719 | -8.3725 | -0.28381 | 0.036621 | 1.7395 | 122.8729 | 122.7951 | 114.4913 | 122.9141 | 1.5244 | 122.9004 | 67.7078 | -0.28381 | 122.9141 | 1.5244 | 67.7078 | 114.4913 | 122.9004 | -123.0789 | -123.1476
2057.3438 | 123.0331 | -61.0245 | 61.8576 | -0.14145 | 0.020506 | 0.0088932 | 0.020905 | 0.059043 | 0.00063871 | 0.086126 | -59.5139 | 61.9034 | -61.2213 | -61.2534 | 53.5034 | 6.6879 | 61.9308 | 61.8073 | 61.9034 | -61.2534 | -0.19684 | 0.045776 | 1.5106 | -0.22888 | -8.3542 | -0.22888 | 0.045776 | 1.7075 | 122.9553 | 122.8317 | 114.5279 | 122.9279 | 1.5106 | 122.9279 | 67.7124 | -0.22888 | 122.9279 | 1.5106 | 67.7124 | 114.5279 | 122.9279 | -123.0789 | -123.111
2058.3281 | 123.0469 | -61.0245 | 61.853 | 0.011139 | 0.022428 | 0.011457 | 0.023255 | 0.060325 | -0.0019247 | 0.087408 | -59.4681 | 61.8851 | -61.2167 | -61.2534 | 53.4851 | 6.7245 | 61.8484 | 61.7981 | 61.8484 | -61.2946 | -0.19226 | 0.032044 | 1.5564 | -0.22888 | -8.3679 | -0.27008 | -0.004577 | 1.7487 | 122.8729 | 122.8226 | 114.5096 | 122.9095 | 1.5564 | 122.8729 | 67.749 | -0.27008 | 122.9095 | 1.5564 | 67.749 | 114.5096 | 122.8729 | -123.0698 | -123.1476
2059.3281 | 123.0103 | -61.0153 | 61.8393 | -0.034637 | 0.022856 | 0.012952 | 0.025605 | 0.059898 | -0.0023519 | 0.088049 | -59.4315 | 61.8851 | -61.2534 | -61.2396 | 53.4851 | 6.7337 | 61.8347 | 61.8164 | 61.8576 | -61.2946 | -0.23804 | 0.045777 | 1.5839 | -0.2243 | -8.3542 | -0.27924 | 0.018311 | 1.8219 | 122.85 | 122.8317 | 114.5004 | 122.9004 | 1.5839 | 122.8729 | 67.749 | -0.27924 | 122.9004 | 1.5839 | 67.749 | 114.5004 | 122.8729 | -123.0927 | -123.1338
2060.3281 | 123.024 | -61.0245 | 61.8347 | 0.011139 | 0.02371 | 0.010816 | 0.02411 | 0.061393 | -0.0014975 | 0.088049 | -59.4452 | 61.9034 | -61.2305 | -61.2076 | 53.5263 | 6.8069 | 61.8439 | 61.8301 | 61.8805 | -61.3037 | -0.20599 | 0.068664 | 1.5793 | -0.18311 | -8.3084 | -0.27924 | 0.045776 | 1.7853 | 122.8683 | 122.8546 | 114.5508 | 122.9279 | 1.5793 | 122.905 | 67.8314 | -0.27924 | 122.9279 | 1.5793 | 67.8314 | 114.5508 | 122.905 | -123.0652 | -123.1384
2061.3281 | 123.0515 | -60.997 | 61.8256 | 0.14847 | 0.020933 | 0.011243 | 0.025819 | 0.061393 | -0.0049155 | 0.085486 | -59.3948 | 61.908 | -61.1984 | -61.203 | 53.5538 | 6.8115 | 61.8484 | 61.8439 | 61.9034 | -61.2854 | -0.20142 | 0.082397 | 1.6022 | -0.20599 | -8.2718 | -0.28839 | 0.077819 | 1.8036 | 122.8455 | 122.8409 | 114.5508 | 122.905 | 1.6022 | 122.9004 | 67.8085 | -0.28839 | 122.905 | 1.6022 | 67.8085 | 114.5508 | 122.9004 | -123.024 | -123.111
2062.3281 | 123.0743 | -60.997 | 61.8347 | -0.0041198 | 0.022856 | 0.0091068 | 0.025391 | 0.06182 | 0.0014933 | 0.087622 | -59.4498 | 61.8896 | -61.2122 | -61.1572 | 53.5995 | 6.8298 | 61.9125 | 61.8393 | 61.8851 | -61.2671 | -0.21515 | 0.054931 | 1.5472 | -0.16022 | -8.2352 | -0.27008 | 0.050354 | 1.7624 | 122.9095 | 122.8363 | 114.5966 | 122.8867 | 1.5472 | 122.8821 | 67.8268 | -0.27008 | 122.8867 | 1.5472 | 67.8268 | 114.5966 | 122.8821 | -123.0469 | -123.1018
2063.3281 | 123.0331 | -60.9924 | 61.8439 | -0.0041198 | 0.02136 | 0.012311 | 0.02411 | 0.060752 | -0.0012839 | 0.085272 | -59.4315 | 61.8851 | -61.2122 | -61.2122 | 53.5583 | 6.752 | 61.8484 | 61.8439 | 61.9034 | -61.2579 | -0.21973 | 0.041199 | 1.561 | -0.21973 | -8.2855 | -0.2655 | 0.059509 | 1.7807 | 122.8409 | 122.8363 | 114.5508 | 122.8775 | 1.561 | 122.8958 | 67.7444 | -0.2655 | 122.8775 | 1.561 | 67.7444 | 114.5508 | 122.8958 | -123.056 | -123.1018
2064.3281 | 123.0469 | -60.9924 | 61.8942 | -0.1796 | 0.02136 | 0.010816 | 0.025819 | 0.057762 | -0.0021383 | 0.088476 | -59.3903 | 61.9308 | -61.203 | -61.1893 | 53.5675 | 6.72 | 61.8576 | 61.8622 | 61.8805 | -61.2442 | -0.21057 | 0.036621 | 1.6022 | -0.19684 | -8.3267 | -0.25177 | -0.013733 | 1.8127 | 122.85 | 122.8546 | 114.5599 | 122.9233 | 1.6022 | 122.8729 | 67.7124 | -0.25177 | 122.9233 | 1.6022 | 67.7124 | 114.5599 | 122.8729 | -123.0972 | -123.1384
2065.3281 | 123.0698 | -60.9924 | 61.8668 | -0.088043 | 0.022642 | 0.012097 | 0.023255 | 0.060966 | -0.0023519 | 0.087622 | -59.4315 | 61.8942 | -61.1755 | -61.1389 | 53.5904 | 6.5918 | 61.8622 | 61.8851 | 61.9308 | -61.2762 | -0.1831 | 0.027466 | 1.561 | -0.14648 | -8.2764 | -0.28381 | 0.064087 | 1.7441 | 122.8546 | 122.8775 | 114.5828 | 122.8867 | 1.561 | 122.9233 | 67.5842 | -0.28381 | 122.8867 | 1.561 | 67.5842 | 114.5828 | 122.9233 | -123.0423 | -123.143
2066.3281 | 123.0469 | -60.9924 | 61.8851 | -0.11093 | 0.023069 | 0.013166 | 0.026673 | 0.062675 | -0.0029929 | 0.088476 | -59.4177 | 61.9263 | -61.2122 | -61.1847 | 53.5583 | 6.6742 | 61.8073 | 61.6425 | 61.8805 | -61.2625 | -0.21973 | 0.041199 | 1.5747 | -0.19226 | -8.3267 | -0.27008 | -0.004578 | 1.7944 | 122.7997 | 122.6349 | 114.5508 | 122.9187 | 1.5747 | 122.8729 | 67.6666 | -0.27008 | 122.9187 | 1.5747 | 67.6666 | 114.5508 | 122.8729 | -123.0972 | -123.1476
2067.3281 | 123.0331 | -60.9833 | 61.8805 | -0.14908 | 0.022642 | 0.013806 | 0.024537 | 0.06182 | -0.0010703 | 0.087622 | -59.436 | 61.9308 | -61.1984 | -61.1801 | 53.5629 | 6.7154 | 61.8942 | 61.8942 | 61.9034 | -61.2579 | -0.21515 | 0.050354 | 1.5472 | -0.19684 | -8.3176 | -0.27466 | 0.022888 | 1.7624 | 122.8775 | 122.8775 | 114.5462 | 122.9141 | 1.5472 | 122.8867 | 67.6987 | -0.27466 | 122.9141 | 1.5472 | 67.6987 | 114.5462 | 122.8867 | -123.0789 | -123.1384
2068.3281 | 123.0423 | -60.9924 | 61.8942 | -0.12619 | 0.021787 | 0.013379 | 0.024537 | 0.05883 | -0.0021383 | 0.08869 | -59.4406 | 61.9537 | -61.1893 | -61.1801 | 53.5675 | 6.7474 | 61.9217 | 61.8896 | 61.9308 | -61.2442 | -0.19684 | 0.059509 | 1.5518 | -0.18768 | -8.3267 | -0.25177 | 0.036621 | 1.7487 | 122.9141 | 122.8821 | 114.5599 | 122.9462 | 1.5518 | 122.9233 | 67.7399 | -0.25177 | 122.9462 | 1.5518 | 67.7399 | 114.5599 | 122.9233 | -123.0835 | -123.1384
2069.3281 | 123.056 | -60.9695 | 61.8668 | -0.065155 | 0.023924 | 0.013379 | 0.0271 | 0.05883 | -0.0019247 | 0.087622 | -59.4131 | 61.9354 | -61.1938 | -61.1526 | 53.627 | 6.8161 | 61.9125 | 61.8759 | 61.9125 | -61.2396 | -0.22431 | 0.068665 | 1.5564 | -0.18311 | -8.2397 | -0.27008 | 0.045777 | 1.7807 | 122.8821 | 122.8455 | 114.5966 | 122.905 | 1.5564 | 122.8821 | 67.7856 | -0.27008 | 122.905 | 1.5564 | 67.7856 | 114.5966 | 122.8821 | -123.0606 | -123.1064
2070.3281 | 123.024 | -60.9879 | 61.8942 | 0.011139 | 0.021787 | 0.011029 | 0.026246 | 0.060539 | -0.0023519 | 0.086767 | -59.4223 | 61.9308 | -61.1984 | -61.1755 | 53.5858 | 6.7337 | 61.8759 | 61.8851 | 61.9125 | -61.2213 | -0.21057 | 0.036621 | 1.5656 | -0.18768 | -8.3084 | -0.23346 | 0.018311 | 1.7761 | 122.8638 | 122.8729 | 114.5737 | 122.9187 | 1.5656 | 122.9004 | 67.7216 | -0.23346 | 122.9187 | 1.5656 | 67.7216 | 114.5737 | 122.9004 | -123.0927 | -123.1155
2071.3281 | 123.056 | -60.9879 | 61.8805 | -0.072784 | 0.020078 | 0.009534 | 0.02475 | 0.060539 | -0.0025657 | 0.087408 | -59.4223 | 61.9125 | -61.1664 | -61.171 | 53.5583 | 6.7886 | 61.8988 | 61.8851 | 61.9034 | -61.2213 | -0.17853 | 0.032044 | 1.5656 | -0.18311 | -8.3221 | -0.23346 | 0.022888 | 1.7441 | 122.8867 | 122.8729 | 114.5462 | 122.9004 | 1.5656 | 122.8912 | 67.7765 | -0.23346 | 122.9004 | 1.5656 | 67.7765 | 114.5462 | 122.8912 | -123.0469 | -123.1018
2072.3281 | 123.0469 | -60.9695 | 61.8759 | -0.14908 | 0.021787 | 0.006757 | 0.024964 | 0.057975 | -0.0025657 | 0.088476 | -59.4543 | 61.9308 | -61.1938 | -61.1984 | 53.5217 | 6.7291 | 61.908 | 61.8713 | 61.9263 | -61.2579 | -0.22431 | 0.054931 | 1.5152 | -0.22888 | -8.3542 | -0.28839 | 0.050354 | 1.7395 | 122.8775 | 122.8409 | 114.4913 | 122.9004 | 1.5152 | 122.8958 | 67.6987 | -0.28839 | 122.9004 | 1.5152 | 67.6987 | 114.4913 | 122.8958 | -123.0698 | -123.1339
2073.3281 | 123.0148 | -60.9741 | 61.8713 | -0.15671 | 0.017729 | 0.007825 | 0.023682 | 0.062889 | -0.0036337 | 0.087195 | -59.4543 | 61.9171 | -61.171 | -61.1938 | 53.5309 | 6.6788 | 61.9217 | 61.8713 | 61.908 | -61.2534 | -0.19684 | 0.045776 | 1.5198 | -0.21973 | -8.3405 | -0.27924 | 0.036621 | 1.7166 | 122.8958 | 122.8455 | 114.505 | 122.8912 | 1.5198 | 122.8821 | 67.6529 | -0.27924 | 122.8912 | 1.5198 | 67.6529 | 114.505 | 122.8821 | -123.0423 | -123.1247
2074.3281 | 123.0148 | -60.997 | 61.8759 | -0.17197 | 0.01901 | 0.014234 | 0.021332 | 0.059257 | -0.00085669 | 0.087835 | -59.4681 | 61.9308 | -61.1801 | -61.1984 | 53.508 | 6.6605 | 61.9308 | 61.8668 | 61.9263 | -61.2717 | -0.18311 | 0.054931 | 1.5289 | -0.20142 | -8.3679 | -0.27466 | 0.050354 | 1.712 | 122.9279 | 122.8638 | 114.505 | 122.9279 | 1.5289 | 122.9233 | 67.6575 | -0.27466 | 122.9279 | 1.5289 | 67.6575 | 114.505 | 122.9233 | -123.056 | -123.1476
2075.3438 | 123.1384 | -60.9604 | 61.8118 | 0.24002 | 0.020078 | 0.0076114 | 0.021546 | 0.058616 | -0.0010703 | 0.090399 | -59.4223 | 61.8256 | -61.171 | -61.2854 | 53.3295 | 6.8024 | 61.8439 | 61.972 | 61.8484 | -61.1847 | -0.21057 | 0.013733 | 1.5381 | -0.32501 | -8.4824 | -0.2243 | 0.036621 | 1.7487 | 122.8043 | 122.9324 | 114.2899 | 122.7859 | 1.5381 | 122.8088 | 67.7628 | -0.2243 | 122.7859 | 1.5381 | 67.7628 | 114.2899 | 122.8088 | -122.9828 | -122.9965
2076.3281 | 123.024 | -60.9879 | 61.8805 | -0.12619 | 0.023069 | 0.0069706 | 0.02411 | 0.057975 | -0.0019247 | 0.088476 | -59.436 | 61.94 | -61.1801 | -61.1664 | 53.5309 | 6.6925 | 61.9034 | 61.8576 | 61.8942 | -61.2671 | -0.19226 | 0.059509 | 1.5518 | -0.17853 | -8.3496 | -0.27924 | 0.013733 | 1.7441 | 122.8912 | 122.8455 | 114.5187 | 122.9279 | 1.5518 | 122.8821 | 67.6804 | -0.27924 | 122.9279 | 1.5518 | 67.6804 | 114.5187 | 122.8821 | -123.0606 | -123.1476
2077.3438 | 123.111 | -60.9512 | 61.8805 | -0.16434 | 0.020506 | 0.0093204 | 0.015565 | 0.057975 | -0.0012839 | 0.089544 | -59.4269 | 61.8118 | -61.1526 | -61.1252 | 53.6133 | 6.72 | 61.821 | 61.972 | 61.8988 | -61.1847 | -0.20142 | -0.068664 | 1.5244 | -0.17395 | -8.2672 | -0.23346 | 0.018311 | 1.7258 | 122.7722 | 122.9233 | 114.5645 | 122.7631 | 1.5244 | 122.85 | 67.6712 | -0.23346 | 122.7631 | 1.5244 | 67.6712 | 114.5645 | 122.85 | -123.0331 | -123.0652
2078.3281 | 123.0148 | -60.9604 | 61.9034 | -0.19485 | 0.022642 | 0.005048 | 0.026032 | 0.057548 | -0.0012839 | 0.088904 | -59.4543 | 61.9125 | -61.1755 | -61.1847 | 53.5263 | 6.6833 | 61.94 | 61.8851 | 61.9308 | -61.2488 | -0.21515 | 0.009156 | 1.506 | -0.2243 | -8.3771 | -0.28839 | 0.027466 | 1.7212 | 122.9004 | 122.8455 | 114.4867 | 122.8729 | 1.506 | 122.8912 | 67.6437 | -0.28839 | 122.8729 | 1.506 | 67.6437 | 114.4867 | 122.8912 | -123.0789 | -123.1522
2079.3281 | 123.0194 | -60.9421 | 61.8988 | -0.16434 | 0.022856 | 0.006757 | 0.025178 | 0.059471 | -0.0034201 | 0.088263 | -59.4543 | 61.9217 | -61.1435 | -61.1984 | 53.4897 | 6.5689 | 61.9492 | 61.8713 | 61.9492 | -61.2122 | -0.20142 | 0.022888 | 1.4877 | -0.25635 | -8.4091 | -0.27008 | 0.050354 | 1.6891 | 122.8912 | 122.8134 | 114.4318 | 122.8638 | 1.4877 | 122.8912 | 67.511 | -0.27008 | 122.8638 | 1.4877 | 67.511 | 114.4318 | 122.8912 | -123.0423 | -123.111
2080.3438 | 122.9919 | -60.997 | 61.8713 | 0.1561 | 0.023283 | 0.011243 | 0.024537 | 0.06118 | -0.0017111 | 0.08869 | -59.4864 | 61.9263 | -61.1893 | -61.2488 | 53.4393 | 6.5231 | 61.8759 | 61.7889 | 61.9217 | -61.2579 | -0.19226 | 0.054932 | 1.5106 | -0.25177 | -8.432 | -0.26093 | 0.050354 | 1.7029 | 122.8729 | 122.7859 | 114.4363 | 122.9233 | 1.5106 | 122.9187 | 67.5201 | -0.26093 | 122.9233 | 1.5106 | 67.5201 | 114.4363 | 122.9187 | -123.0606 | -123.1293
2081.3281 | 123.024 | -60.9924 | 61.8988 | -0.17197 | 0.020933 | 0.006757 | 0.024537 | 0.05883 | 0.00021151 | 0.088904 | -59.4498 | 61.9629 | -61.1893 | -61.2076 | 53.4531 | 6.6513 | 61.9812 | 61.853 | 61.9308 | -61.2259 | -0.19684 | 0.064087 | 1.5427 | -0.21515 | -8.4457 | -0.23346 | 0.032043 | 1.7395 | 122.9736 | 122.8455 | 114.4455 | 122.9553 | 1.5427 | 122.9233 | 67.6437 | -0.23346 | 122.9553 | 1.5427 | 67.6437 | 114.4455 | 122.9233 | -123.0881 | -123.1247
2082.3281 | 122.9874 | -60.9604 | 61.8896 | -0.17197 | 0.021787 | 0.006757 | 0.024964 | 0.057548 | -0.0021383 | 0.086767 | -59.4864 | 61.9354 | -61.1755 | -61.2076 | 53.4485 | 6.6788 | 61.9904 | 61.853 | 61.9217 | -61.2167 | -0.21515 | 0.045777 | 1.474 | -0.24719 | -8.4412 | -0.25635 | 0.032044 | 1.6891 | 122.9507 | 122.8134 | 114.4089 | 122.8958 | 1.474 | 122.8821 | 67.6392 | -0.25635 | 122.8958 | 1.474 | 67.6392 | 114.4089 | 122.8821 | -123.0652 | -123.1064
2083.3281 | 123.056 | -60.9787 | 61.9034 | -0.15671 | 0.02136 | 0.007825 | 0.02411 | 0.060752 | -0.0025657 | 0.088476 | -59.4635 | 61.9308 | -61.1755 | -61.1801 | 53.4805 | 6.752 | 61.9446 | 61.8851 | 61.9354 | -61.2213 | -0.19684 | 0.027466 | 1.5152 | -0.20142 | -8.4229 | -0.24261 | 0.032044 | 1.712 | 122.9233 | 122.8638 | 114.4592 | 122.9095 | 1.5152 | 122.9141 | 67.7307 | -0.24261 | 122.9095 | 1.5152 | 67.7307 | 114.4592 | 122.9141 | -123.0789 | -123.1247
2084.3281 | 123.0423 | -60.9512 | 61.9125 | -0.17197 | 0.022428 | 0.0080386 | 0.022401 | 0.056693 | -0.0036337 | 0.087835 | -59.4589 | 61.9492 | -61.1847 | -61.1801 | 53.4485 | 6.8161 | 61.9446 | 61.8896 | 61.9492 | -61.1938 | -0.23346 | 0.036621 | 1.4923 | -0.22888 | -8.4641 | -0.24262 | 0.036621 | 1.7258 | 122.8958 | 122.8409 | 114.3997 | 122.9004 | 1.4923 | 122.9004 | 67.7673 | -0.24262 | 122.9004 | 1.4923 | 67.7673 | 114.3997 | 122.9004 | -123.0972 | -123.1064
2085.3438 | 123.0972 | -60.9375 | 61.853 | 0.21713 | 0.020078 | 0.010388 | 0.022187 | 0.058402 | -0.0019247 | 0.086981 | -59.4131 | 61.8668 | -61.1526 | -61.1435 | 53.627 | 6.7383 | 61.6058 | 62.0911 | 61.853 | -61.1938 | -0.21515 | 0.013733 | 1.5244 | -0.20599 | -8.226 | -0.25635 | 0 | 1.7395 | 122.5433 | 123.0286 | 114.5645 | 122.8043 | 1.5244 | 122.7905 | 67.6758 | -0.25635 | 122.8043 | 1.5244 | 67.6758 | 114.5645 | 122.7905 | -123.0057 | -123.0469
2086.3281 | 123.0103 | -60.9558 | 61.9308 | -0.14908 | 0.020292 | 0.0082522 | 0.021546 | 0.057548 | -0.0019247 | 0.089331 | -59.4635 | 61.94 | -61.1572 | -61.1664 | 53.4714 | 6.7245 | 61.9904 | 61.8851 | 61.9446 | -61.2076 | -0.20142 | 0.009155 | 1.4923 | -0.21057 | -8.4595 | -0.25177 | 0.013733 | 1.6937 | 122.9462 | 122.8409 | 114.4272 | 122.8958 | 1.4923 | 122.9004 | 67.6804 | -0.25177 | 122.8958 | 1.4923 | 67.6804 | 114.4272 | 122.9004 | -123.0881 | -123.1384
2087.3281 | 122.9874 | -60.9512 | 61.9308 | -0.15671 | 0.020292 | 0.0086796 | 0.022828 | 0.059043 | -0.0014975 | 0.087195 | -59.4589 | 61.9629 | -61.1435 | -61.1801 | 53.4897 | 6.6513 | 61.9949 | 61.8896 | 61.9537 | -61.1984 | -0.19226 | 0.032044 | 1.4923 | -0.22888 | -8.4412 | -0.24719 | 0.022888 | 1.6846 | 122.9462 | 122.8409 | 114.4409 | 122.9141 | 1.4923 | 122.905 | 67.6025 | -0.24719 | 122.9141 | 1.4923 | 67.6025 | 114.4409 | 122.905 | -123.0743 | -123.1293
2088.3281 | 123.024 | -60.9604 | 61.9354 | -0.14145 | 0.020506 | 0.0088932 | 0.020478 | 0.058616 | -0.0025657 | 0.087835 | -59.4543 | 61.9537 | -61.1664 | -61.1847 | 53.476 | 6.6696 | 61.9766 | 61.8668 | 61.9308 | -61.1984 | -0.20599 | 0.01831 | 1.506 | -0.2243 | -8.4595 | -0.23804 | -0.004578 | 1.712 | 122.937 | 122.8271 | 114.4363 | 122.9141 | 1.506 | 122.8912 | 67.63 | -0.23804 | 122.9141 | 1.506 | 67.63 | 114.4363 | 122.8912 | -123.1018 | -123.1338
2089.3281 | 122.9965 | -60.9421 | 61.9308 | -0.13382 | 0.022856 | 0.009534 | 0.023041 | 0.058616 | -0.00021569 | 0.089117 | -59.4589 | 61.9675 | -61.1389 | -61.1893 | 53.4851 | 6.6742 | 61.9858 | 61.8851 | 61.9446 | -61.1847 | -0.19684 | 0.036621 | 1.4832 | -0.24719 | -8.4457 | -0.24261 | 0.013733 | 1.68 | 122.9279 | 122.8271 | 114.4272 | 122.9095 | 1.4832 | 122.8867 | 67.6163 | -0.24261 | 122.9095 | 1.4832 | 67.6163 | 114.4272 | 122.8867 | -123.0698 | -123.1155
2090.3281 | 123.0515 | -60.9421 | 61.9354 | -0.15671 | 0.023069 | 0.007825 | 0.026032 | 0.05883 | -0.00042929 | 0.088476 | -59.4406 | 61.9583 | -61.1618 | -61.1572 | 53.508 | 6.7886 | 61.9858 | 61.9125 | 61.9537 | -61.1664 | -0.21973 | 0.022888 | 1.5015 | -0.21515 | -8.4274 | -0.2243 | 0.01831 | 1.7212 | 122.9279 | 122.8546 | 114.4501 | 122.9004 | 1.5015 | 122.8958 | 67.7307 | -0.2243 | 122.9004 | 1.5015 | 67.7307 | 114.4501 | 122.8958 | -123.0972 | -123.1018
2091.3281 | 123.0194 | -60.9467 | 61.94 | -0.16434 | 0.020292 | 0.0069706 | 0.021973 | 0.058616 | -0.00085669 | 0.086981 | -59.4543 | 61.9537 | -61.1389 | -61.1755 | 53.4851 | 6.7383 | 61.9949 | 61.8896 | 61.94 | -61.1984 | -0.19226 | 0.013733 | 1.4923 | -0.22888 | -8.4549 | -0.25177 | 0 | 1.6846 | 122.9416 | 122.8363 | 114.4318 | 122.9004 | 1.4923 | 122.8867 | 67.6849 | -0.25177 | 122.9004 | 1.4923 | 67.6849 | 114.4318 | 122.8867 | -123.0789 | -123.1384
2092.3281 | 123.0194 | -60.9604 | 61.9125 | -0.13382 | 0.019865 | 0.011029 | 0.023682 | 0.059684 | -0.0017111 | 0.087835 | -59.4589 | 61.9766 | -61.1664 | -61.1893 | 53.508 | 6.8665 | 62.0041 | 61.8988 | 61.9583 | -61.1938 | -0.20599 | 0.064087 | 1.5015 | -0.22888 | -8.4045 | -0.23346 | 0.045776 | 1.7075 | 122.9645 | 122.8592 | 114.4684 | 122.937 | 1.5015 | 122.9187 | 67.8268 | -0.23346 | 122.937 | 1.5015 | 67.8268 | 114.4684 | 122.9187 | -123.0789 | -123.1064
2093.3281 | 123.0148 | -60.9375 | 61.9263 | -0.1796 | 0.022001 | 0.007825 | 0.019623 | 0.058402 | 0.00063871 | 0.088904 | -59.4543 | 61.9675 | -61.1435 | -61.1801 | 53.4714 | 6.839 | 61.9904 | 61.8759 | 61.9492 | -61.1847 | -0.20599 | 0.041198 | 1.4832 | -0.24262 | -8.4549 | -0.24719 | 0.022888 | 1.6891 | 122.9279 | 122.8134 | 114.4089 | 122.905 | 1.4832 | 122.8867 | 67.7765 | -0.24719 | 122.905 | 1.4832 | 67.7765 | 114.4089 | 122.8867 | -123.0698 | -123.111
2094.3281 | 123.0148 | -60.9375 | 61.9446 | -0.15671 | 0.020719 | 0.009534 | 0.023682 | 0.059898 | -0.0029929 | 0.088263 | -59.4498 | 61.9537 | -61.1618 | -61.1664 | 53.4622 | 6.8024 | 62.0178 | 61.8942 | 61.9537 | -61.1572 | -0.2243 | 0.009155 | 1.4877 | -0.22888 | -8.4824 | -0.21973 | 0.009155 | 1.712 | 122.9553 | 122.8317 | 114.3997 | 122.8912 | 1.4877 | 122.8912 | 67.7399 | -0.21973 | 122.8912 | 1.4877 | 67.7399 | 114.3997 | 122.8912 | -123.1064 | -123.1018
2095.3281 | 123.0011 | -60.9283 | 61.9537 | -0.14145 | 0.021147 | 0.009534 | 0.022614 | 0.059043 | -0.0027793 | 0.08869 | -59.4406 | 61.9537 | -61.1435 | -61.1664 | 53.4576 | 6.7932 | 62.0087 | 61.908 | 61.9629 | -61.1847 | -0.21515 | 0 | 1.4877 | -0.23804 | -8.4961 | -0.25635 | 0.009156 | 1.7029 | 122.937 | 122.8363 | 114.386 | 122.8821 | 1.4877 | 122.8912 | 67.7216 | -0.25635 | 122.8821 | 1.4877 | 67.7216 | 114.386 | 122.8912 | -123.0972 | -123.1384
2096.3438 | 123.0606 | -60.9146 | 61.9354 | -0.065155 | 0.020719 | 0.012525 | 0.025391 | 0.057762 | -0.0025657 | 0.088049 | -59.3948 | 61.94 | -61.1343 | -61.1206 | 53.508 | 6.7795 | 61.94 | 61.7249 | 61.9308 | -61.1526 | -0.21973 | 0.004577 | 1.5198 | -0.20599 | -8.4274 | -0.23804 | -0.004578 | 1.7395 | 122.8546 | 122.6395 | 114.4226 | 122.8546 | 1.5198 | 122.8455 | 67.6941 | -0.23804 | 122.8546 | 1.5198 | 67.6941 | 114.4226 | 122.8455 | -123.0698 | -123.0881
2097.3281 | 123.0377 | -60.9283 | 61.9446 | -0.18723 | 0.021787 | 0.010816 | 0.02475 | 0.059684 | -0.0027793 | 0.088049 | -59.4315 | 61.9583 | -61.1481 | -61.1618 | 53.476 | 6.8207 | 62.0087 | 61.908 | 61.972 | -61.1664 | -0.21973 | 0.013733 | 1.4969 | -0.23346 | -8.4686 | -0.23804 | 0.027466 | 1.7166 | 122.937 | 122.8363 | 114.4043 | 122.8867 | 1.4969 | 122.9004 | 67.749 | -0.23804 | 122.8867 | 1.4969 | 67.749 | 114.4043 | 122.9004 | -123.0927 | -123.111
2098.3281 | 123.0194 | -60.9421 | 61.9583 | 0.62149 | 0.022856 | 0.010175 | 0.019837 | 0.05883 | -0.0017111 | 0.088476 | -59.5276 | 61.9492 | -61.1526 | -61.1664 | 53.4485 | 6.8665 | 62.0224 | 61.8759 | 61.972 | -61.1664 | -0.21057 | -0.009155 | 1.4145 | -0.2243 | -8.5098 | -0.2243 | 0.013733 | 1.6251 | 122.9645 | 122.818 | 114.3906 | 122.8912 | 1.4145 | 122.9141 | 67.8085 | -0.2243 | 122.8912 | 1.4145 | 67.8085 | 114.3906 | 122.9141 | -123.111 | -123.1247
2099.3281 | 123.0194 | -60.9512 | 61.9492 | -0.18723 | 0.019651 | 0.0052616 | 0.021332 | 0.059471 | -0.00085669 | 0.088049 | -59.4727 | 61.94 | -61.1206 | -61.1572 | 53.3981 | 6.8298 | 62.0361 | 61.8759 | 61.9492 | -61.1801 | -0.16937 | -0.009156 | 1.4786 | -0.20599 | -8.551 | -0.22888 | 0 | 1.6479 | 122.9874 | 122.8271 | 114.3494 | 122.8912 | 1.4786 | 122.9004 | 67.7811 | -0.22888 | 122.8912 | 1.4786 | 67.7811 | 114.3494 | 122.9004 | -123.0698 | -123.1293
2100.3281 | 122.9782 | -60.91 | 61.9308 | -0.21774 | 0.01901 | 0.0084658 | 0.020905 | 0.055625 | -0.0017111 | 0.083349 | -59.4681 | 61.9446 | -61.1298 | -61.0611 | 53.6865 | 6.8756 | 61.8759 | 61.8118 | 61.9446 | -61.1847 | -0.21973 | 0.013733 | 1.442 | -0.15106 | -8.2443 | -0.27466 | 0.013733 | 1.6617 | 122.7859 | 122.7219 | 114.5966 | 122.8546 | 1.442 | 122.8546 | 67.7856 | -0.27466 | 122.8546 | 1.442 | 67.7856 | 114.5966 | 122.8546 | -123.0606 | -123.1155
2101.3281 | 122.9736 | -60.9009 | 61.972 | -0.13382 | 0.02136 | 0.0097476 | 0.02176 | 0.055412 | -0.0019247 | 0.086126 | -59.4406 | 61.94 | -61.1298 | -61.1526 | 53.4485 | 6.8665 | 62.027 | 61.9034 | 61.972 | -61.1526 | -0.22888 | -0.032044 | 1.4603 | -0.25177 | -8.5236 | -0.25177 | 0 | 1.6891 | 122.9279 | 122.8043 | 114.3494 | 122.8409 | 1.4603 | 122.8729 | 67.7673 | -0.25177 | 122.8409 | 1.4603 | 67.7673 | 114.3494 | 122.8729 | -123.1018 | -123.1247
2102.3281 | 123.0103 | -60.9467 | 61.94 | -0.13382 | 0.019438 | 0.006116 | 0.020905 | 0.057975 | -0.0014975 | 0.087622 | -59.4315 | 61.9171 | -61.1298 | -61.1664 | 53.4485 | 6.9214 | 62.0132 | 61.8942 | 61.9858 | -61.1526 | -0.18311 | -0.022888 | 1.5152 | -0.21973 | -8.4915 | -0.20599 | 0.045777 | 1.6983 | 122.9599 | 122.8409 | 114.3951 | 122.8638 | 1.5152 | 122.9324 | 67.868 | -0.20599 | 122.8638 | 1.5152 | 67.868 | 114.3951 | 122.9324 | -123.0698 | -123.0927
2103.3281 | 122.4106 | -62.7228 | 59.5779 | -0.11093 | 0.021147 | 0.0088932 | 0.047608 | -0.0088888 | -0.0064109 | 0.035498 | -61.2259 | 59.5779 | -62.9379 | 59.0332 | 59.5093 | 59.5413 | 59.642 | 59.5459 | 59.5734 | -62.9654 | -0.21515 | 0 | 1.4969 | 121.756 | -0.068665 | -0.24262 | -0.004578 | 1.712 | 122.3648 | 122.2687 | 122.2321 | 122.3007 | 1.4969 | 122.2961 | 122.2641 | -0.24262 | 122.3007 | 1.4969 | 122.2641 | 122.2321 | 122.2961 | -122.5159 | -122.5433
2104.3281 | 122.5891 | -62.8326 | 59.6512 | -0.057526 | 0.021147 | 0.012525 | 0.045045 | -0.0084616 | -0.0038473 | 0.036566 | -61.3449 | 59.642 | -63.0203 | 59.1934 | 59.61 | 59.6466 | 59.7382 | 59.6512 | 59.6786 | -63.0615 | -0.18768 | -0.009155 | 1.4877 | 122.0261 | -0.041199 | -0.22888 | 0.027466 | 1.6754 | 122.5708 | 122.4838 | 122.4426 | 122.4747 | 1.4877 | 122.5113 | 122.4792 | -0.22888 | 122.4747 | 1.4877 | 122.4792 | 122.4426 | 122.5113 | -122.6715 | -122.7127
2105.3281 | 122.6578 | -62.8464 | 59.697 | -0.77469 | 0.019224 | 0.0082522 | 0.049744 | -0.0078206 | -0.0038473 | 0.035925 | -61.4273 | 59.6649 | -63.0844 | 59.2117 | 59.6329 | 59.6603 | 59.7748 | 59.6741 | 59.7015 | -63.0798 | -0.23804 | -0.032043 | 1.4191 | 122.0581 | -0.064086 | -0.23346 | 0.004578 | 1.6571 | 122.6212 | 122.5204 | 122.4792 | 122.5113 | 1.4191 | 122.5479 | 122.5067 | -0.23346 | 122.5113 | 1.4191 | 122.5067 | 122.4792 | 122.5479 | -122.7814 | -122.7768
2106.3281 | 122.6944 | -62.8464 | 59.7107 | -0.17197 | 0.019651 | 0.009534 | 0.049103 | -0.0078206 | -0.0061973 | 0.037634 | -61.3495 | 59.7244 | -63.0753 | 59.2621 | 59.6695 | 59.6924 | 59.7839 | 59.7198 | 59.7198 | -63.1027 | -0.22888 | 0.013733 | 1.4969 | 122.1085 | -0.041198 | -0.25635 | 0.009156 | 1.7258 | 122.6303 | 122.5662 | 122.5159 | 122.5708 | 1.4969 | 122.5662 | 122.5388 | -0.25635 | 122.5708 | 1.4969 | 122.5388 | 122.5159 | 122.5662 | -122.7859 | -122.8134
2107.3281 | 122.7219 | -62.8555 | 59.7382 | -0.19485 | 0.020719 | 0.0071842 | 0.049317 | -0.0084616 | -0.0051291 | 0.038916 | -61.3678 | 59.7382 | -63.0386 | 59.2575 | 59.6878 | 59.729 | 59.8114 | 59.729 | 59.7702 | -63.1119 | -0.1831 | 0 | 1.4877 | 122.113 | -0.050354 | -0.25635 | 0.032044 | 1.6708 | 122.6669 | 122.5845 | 122.5433 | 122.5937 | 1.4877 | 122.6257 | 122.5845 | -0.25635 | 122.5937 | 1.4877 | 122.5845 | 122.5433 | 122.6257 | -122.7768 | -122.85
2108.3281 | 122.6715 | -62.8922 | 59.7748 | -0.15671 | 0.017729 | 0.006757 | 0.04889 | -0.010598 | -0.0070517 | 0.041052 | -61.3815 | 59.7107 | -63.0844 | 59.2667 | 59.7015 | 59.7519 | 59.8114 | 59.7427 | 59.761 | -63.1256 | -0.19226 | -0.064087 | 1.5106 | 122.1588 | -0.073242 | -0.23346 | -0.013733 | 1.7029 | 122.7036 | 122.6349 | 122.5937 | 122.6028 | 1.5106 | 122.6532 | 122.644 | -0.23346 | 122.6028 | 1.5106 | 122.644 | 122.5937 | 122.6532 | -122.8592 | -122.9004
2109.3281 | 122.7539 | -62.8738 | 59.7748 | -0.29404 | 0.020933 | 0.005048 | 0.049744 | -0.0069662 | -0.0053427 | 0.039984 | -61.3861 | 59.7885 | -63.1165 | 59.2712 | 59.7061 | 59.7427 | 59.8389 | 59.7473 | 59.761 | -63.1256 | -0.24262 | 0.013733 | 1.4877 | 122.1451 | -0.068664 | -0.25177 | -0.013733 | 1.7303 | 122.7127 | 122.6212 | 122.58 | 122.6624 | 1.4877 | 122.6349 | 122.6166 | -0.25177 | 122.6624 | 1.4877 | 122.6166 | 122.58 | 122.6349 | -122.8912 | -122.9004
2110.3281 | 122.7722 | -62.8738 | 59.7748 | -0.14908 | 0.020933 | 0.0091068 | 0.052521 | -0.009316 | -0.0055563 | 0.039343 | -61.3815 | 59.7885 | -63.0615 | 59.3033 | 59.7473 | 59.7748 | 59.8526 | 59.7885 | 59.7794 | -63.1119 | -0.18768 | 0.013733 | 1.4923 | 122.1771 | -0.027466 | -0.23804 | 0.004578 | 1.68 | 122.7264 | 122.6624 | 122.6212 | 122.6624 | 1.4923 | 122.6532 | 122.6486 | -0.23804 | 122.6624 | 1.4923 | 122.6486 | 122.6212 | 122.6532 | -122.8363 | -122.8867
2111.3281 | 122.8043 | -62.9105 | 59.7702 | -0.1796 | 0.021574 | 0.012738 | 0.050599 | -0.0080344 | -0.0064109 | 0.041052 | -61.4044 | 59.7931 | -63.0798 | 59.3033 | 59.7382 | 59.761 | 59.8389 | 59.7794 | 59.7931 | -63.1393 | -0.16937 | 0.022888 | 1.506 | 122.2137 | -0.032044 | -0.22888 | 0.022888 | 1.6754 | 122.7493 | 122.6898 | 122.6486 | 122.7036 | 1.506 | 122.7036 | 122.6715 | -0.22888 | 122.7036 | 1.506 | 122.6715 | 122.6486 | 122.7036 | -122.85 | -122.9095
2112.3281 | 122.8226 | -62.9105 | 59.7931 | -0.072784 | 0.022428 | 0.0086796 | 0.050812 | -0.0054708 | -0.0076925 | 0.041052 | -61.4044 | 59.8022 | -63.0798 | 59.317 | 59.7336 | 59.7748 | 59.8846 | 59.7839 | 59.7977 | -63.1393 | -0.16937 | 0.009155 | 1.506 | 122.2275 | -0.059509 | -0.22888 | 0.004577 | 1.6754 | 122.7951 | 122.6944 | 122.644 | 122.7127 | 1.506 | 122.7081 | 122.6852 | -0.22888 | 122.7127 | 1.506 | 122.6852 | 122.644 | 122.7081 | -122.8729 | -122.9324
2113.3281 | 122.7859 | -62.8784 | 59.7885 | -1.8733 | 0.021147 | 0.010175 | 0.050599 | -0.009316 | -0.0055563 | 0.040625 | -61.4044 | 59.8251 | -63.0753 | 59.3216 | 59.7473 | 59.7839 | 59.9075 | 59.7977 | 59.8389 | -63.1439 | -0.19684 | 0.036621 | 1.474 | 122.2 | -0.041199 | -0.2655 | 0.050354 | 1.6708 | 122.786 | 122.6761 | 122.6257 | 122.7036 | 1.474 | 122.7173 | 122.6624 | -0.2655 | 122.7036 | 1.474 | 122.6624 | 122.6257 | 122.7173 | -122.8638 | -122.9324
2114.3281 | 122.8409 | -62.8647 | 59.8434 | -0.20248 | 0.019651 | 0.0076114 | 0.050385 | -0.009316 | -0.0066245 | 0.041906 | -61.3998 | 59.8526 | -63.0798 | 59.3857 | 59.8434 | 60.0311 | 59.8618 | 59.6924 | 59.8755 | -63.0936 | -0.21515 | 0.009155 | 1.4648 | 122.2504 | 0 | -0.22888 | 0.032043 | 1.68 | 122.7264 | 122.5571 | 122.7081 | 122.7173 | 1.4648 | 122.7402 | 122.8958 | -0.22888 | 122.7173 | 1.4648 | 122.8958 | 122.7081 | 122.7402 | -122.9233 | -122.937
2115.3281 | 122.8775 | -62.8372 | 59.8343 | -0.24063 | 0.01837 | 0.011457 | 0.050812 | -0.0097434 | -0.0083335 | 0.043402 | -61.3129 | 59.7794 | -63.0432 | 59.4681 | 59.8663 | 59.9258 | 59.8206 | 59.935 | 59.8068 | -63.0615 | -0.20599 | -0.054932 | 1.5244 | 122.3053 | 0.032043 | -0.2243 | -0.027466 | 1.7303 | 122.6578 | 122.7722 | 122.7036 | 122.6166 | 1.5244 | 122.644 | 122.7631 | -0.2243 | 122.6166 | 1.5244 | 122.7631 | 122.7036 | 122.644 | -122.8775 | -122.8958
2116.3281 | 122.8409 | -62.883 | 59.848 | -0.19485 | 0.01837 | 0.0071842 | 0.051026 | -0.009957 | -0.0061973 | 0.041479 | -61.3449 | 59.8251 | -63.0661 | 59.3765 | 59.8434 | 59.8892 | 59.8526 | 59.8618 | 59.8389 | -63.1348 | -0.18311 | -0.022888 | 1.5381 | 122.2595 | -0.004577 | -0.25177 | -0.009155 | 1.7212 | 122.7356 | 122.7448 | 122.7264 | 122.7081 | 1.5381 | 122.7219 | 122.7722 | -0.25177 | 122.7081 | 1.5381 | 122.7722 | 122.7264 | 122.7219 | -122.9141 | -122.9828
2117.3281 | 122.8363 | -62.8784 | 59.848 | -0.22537 | 0.017729 | 0.0071842 | 0.057007 | -0.0086752 | -0.0055563 | 0.043402 | -61.3953 | 59.8389 | -63.0844 | 59.3811 | 59.7382 | 59.8068 | 59.935 | 59.8114 | 59.8297 | -63.1119 | -0.20599 | -0.009155 | 1.4832 | 122.2595 | -0.10986 | -0.23346 | -0.01831 | 1.6891 | 122.8134 | 122.6898 | 122.6166 | 122.7173 | 1.4832 | 122.7081 | 122.6852 | -0.23346 | 122.7173 | 1.4832 | 122.6852 | 122.6166 | 122.7081 | -122.9324 | -122.9599
2118.3281 | 122.8134 | -62.883 | 59.8297 | -0.21774 | 0.018583 | 0.0020572 | 0.05359 | -0.0088888 | -0.0068381 | 0.043829 | -61.4182 | 59.8114 | -63.1119 | 59.3765 | 59.7794 | 59.7519 | 60.173 | 59.9625 | 59.8892 | -63.1256 | -0.22888 | -0.018311 | 1.4648 | 122.2595 | -0.050354 | -0.24261 | 0.059509 | 1.6937 | 123.056 | 122.8455 | 122.6624 | 122.6944 | 1.4648 | 122.7722 | 122.6349 | -0.24261 | 122.6944 | 1.4648 | 122.6349 | 122.6624 | 122.7722 | -122.9416 | -122.9553
2119.3281 | 122.8455 | -62.8876 | 59.8526 | -0.18723 | 0.020292 | 0.012525 | 0.052521 | -0.011025 | -0.0057699 | 0.044256 | -61.4273 | 59.7977 | -63.1165 | 59.3811 | 59.7794 | 59.8251 | 59.903 | 59.8251 | 59.8297 | -63.1393 | -0.22888 | -0.054932 | 1.4603 | 122.2687 | -0.073242 | -0.25177 | -0.022888 | 1.6891 | 122.7905 | 122.7127 | 122.6669 | 122.6852 | 1.4603 | 122.7173 | 122.7127 | -0.25177 | 122.6852 | 1.4603 | 122.7127 | 122.6669 | 122.7173 | -122.9691 | -122.9919
2120.3281 | 122.8546 | -62.883 | 59.8434 | -0.21011 | 0.019865 | 0.007825 | 0.054658 | -0.011666 | -0.0064109 | 0.044684 | -61.3815 | 59.7839 | -63.0844 | 59.404 | 59.7931 | 59.8389 | 59.8938 | 59.8663 | 59.8297 | -63.1256 | -0.20142 | -0.059509 | 1.5015 | 122.287 | -0.050354 | -0.24261 | -0.013733 | 1.7029 | 122.7768 | 122.7493 | 122.6761 | 122.6669 | 1.5015 | 122.7127 | 122.7219 | -0.24261 | 122.6669 | 1.5015 | 122.7219 | 122.6761 | 122.7127 | -122.9279 | -122.9691
2121.3281 | 122.9279 | -62.9196 | 59.8297 | -0.18723 | 0.01901 | 0.0088932 | 0.052094 | -0.010384 | -0.0051291 | 0.043829 | -61.3724 | 59.7839 | -63.1165 | 59.4223 | 59.8251 | 59.8572 | 59.8251 | 59.8801 | 59.8343 | -63.1439 | -0.19684 | -0.045776 | 1.5472 | 122.3419 | -0.004578 | -0.2243 | 0.004578 | 1.7441 | 122.7448 | 122.7997 | 122.7448 | 122.7036 | 1.5472 | 122.7539 | 122.7768 | -0.2243 | 122.7036 | 1.5472 | 122.7768 | 122.7448 | 122.7539 | -122.9462 | -122.9736
2122.3281 | 122.9965 | -62.851 | 59.8068 | -0.011749 | 0.016874 | 0.009534 | 0.052521 | -0.010171 | -0.0074789 | 0.044256 | -61.377 | 59.7473 | -63.1073 | 59.4955 | 59.8755 | 59.9396 | 59.7519 | 59.9625 | 59.7977 | -63.1256 | -0.25635 | -0.05951 | 1.474 | 122.3465 | 0.068664 | -0.27466 | -0.009156 | 1.7303 | 122.6028 | 122.8134 | 122.7264 | 122.5983 | 1.474 | 122.6486 | 122.7905 | -0.27466 | 122.5983 | 1.474 | 122.7905 | 122.7264 | 122.6486 | -122.9141 | -122.9324
2123.3281 | 122.9599 | -62.8784 | 59.7931 | -0.17197 | 0.019224 | 0.0088932 | 0.054017 | -0.013161 | -0.0066245 | 0.042975 | -61.377 | 59.7473 | -63.1073 | 59.4543 | 59.8938 | 59.935 | 59.7885 | 59.9487 | 59.7977 | -63.121 | -0.22888 | -0.045777 | 1.5015 | 122.3328 | 0.10071 | -0.24261 | 0.004577 | 1.7303 | 122.6669 | 122.8271 | 122.7722 | 122.6257 | 1.5015 | 122.6761 | 122.8134 | -0.24261 | 122.6257 | 1.5015 | 122.8134 | 122.7722 | 122.6761 | -122.9004 | -122.9141
2124.3281 | 122.9462 | -62.8967 | 59.8068 | -0.21774 | 0.018583 | 0.0088932 | 0.057007 | -0.010171 | -0.0064109 | 0.04447 | -61.3998 | 59.8022 | -63.1027 | 59.3765 | 59.8343 | 59.8618 | 59.8526 | 59.8755 | 59.8068 | -63.1668 | -0.20599 | -0.004578 | 1.4969 | 122.2733 | 0.027466 | -0.27008 | 0 | 1.7029 | 122.7493 | 122.7722 | 122.731 | 122.699 | 1.4969 | 122.7036 | 122.7585 | -0.27008 | 122.699 | 1.4969 | 122.7585 | 122.731 | 122.7036 | -122.9095 | -122.9736
2125.3281 | 122.9828 | -62.8876 | 59.8526 | -0.17197 | 0.017088 | 0.0065432 | 0.058716 | -0.012093 | -0.0064109 | 0.047247 | -61.3724 | 59.7794 | -63.0707 | 59.3994 | 59.8663 | 59.9167 | 59.8297 | 59.9396 | 59.816 | -63.1256 | -0.18311 | -0.073242 | 1.5152 | 122.287 | 0.013733 | -0.23804 | -0.036621 | 1.6983 | 122.7173 | 122.8271 | 122.7539 | 122.6669 | 1.5152 | 122.7036 | 122.8043 | -0.23804 | 122.6669 | 1.5152 | 122.8043 | 122.7539 | 122.7036 | -122.9233 | -122.9782
2126.3281 | 122.9736 | -62.8693 | 59.8526 | -0.15671 | 0.018797 | 0.0071842 | 0.057435 | -0.01252 | -0.0076925 | 0.048742 | -61.3358 | 59.7702 | -63.0798 | 59.436 | 59.8984 | 59.9487 | 59.8206 | 59.9716 | 59.8251 | -63.1073 | -0.21057 | -0.082397 | 1.5335 | 122.3053 | 0.045776 | -0.23804 | -0.027466 | 1.7441 | 122.6898 | 122.8409 | 122.7676 | 122.6395 | 1.5335 | 122.6944 | 122.818 | -0.23804 | 122.6395 | 1.5335 | 122.818 | 122.7676 | 122.6944 | -122.9324 | -122.9599
2127.3281 | 122.7356 | -59.4315 | 63.0432 | -0.14908 | 0.018156 | 0.0048342 | 0.032654 | -0.0071798 | 0.0036295 | 0.038061 | -57.9391 | 62.9654 | -59.6603 | 57.2113 | 49.0906 | 14.5065 | 1.2543 | 1.4969 | 62.9745 | -59.6649 | -0.22888 | -0.07782 | 1.4923 | 116.6428 | -13.9526 | -0.23346 | -0.068665 | 1.7212 | 60.6857 | 60.9283 | 108.522 | 122.3969 | 1.4923 | 122.406 | 73.938 | -0.23346 | 122.3969 | 1.4923 | 73.938 | 108.522 | 122.406 | -122.7036 | -122.7081
2128.3281 | 122.818 | -56.7581 | 65.7578 | -0.14908 | 0.020506 | 0.002698 | 0.036927 | -0.0037618 | 0.0036295 | 0.044897 | -55.275 | 65.7028 | -56.9733 | 53.8971 | 48.6191 | -33.7097 | -48.0377 | -47.6669 | 65.7166 | -56.9778 | -0.21515 | -0.054931 | 1.4832 | 110.6552 | -17.1387 | -0.21973 | -0.041198 | 1.6983 | 8.7204 | 9.0912 | 105.3772 | 122.4609 | 1.4832 | 122.4747 | 23.0484 | -0.21973 | 122.4609 | 1.4832 | 23.0484 | 105.3772 | 122.4747 | -122.731 | -122.7356
2129.3281 | 122.8867 | -56.5201 | 66.0461 | 0.079804 | 0.021147 | 0.0076114 | 0.034791 | -0.0067526 | 0.0034159 | 0.045111 | -55.0781 | 66.0004 | -56.7215 | 53.1601 | 48.2437 | -41.8396 | -49.7223 | -49.3607 | 66.0049 | -56.7352 | -0.20142 | -0.045777 | 1.442 | 109.6802 | -17.8024 | -0.21515 | -0.041199 | 1.6434 | 6.7978 | 7.1594 | 104.7638 | 122.5204 | 1.442 | 122.525 | 14.6805 | -0.21515 | 122.5204 | 1.442 | 14.6805 | 104.7638 | 122.525 | -122.7676 | -122.7814
2130.3281 | 122.9095 | -56.4468 | 66.1377 | -0.080414 | 0.017088 | 0.0065432 | 0.030518 | -0.00483 | 0.0046975 | 0.048315 | -54.9728 | 66.1057 | -56.6483 | 52.5879 | 47.85 | -42.659 | -50.1663 | -49.8734 | 66.1148 | -56.662 | -0.20142 | -0.032043 | 1.474 | 109.0347 | -18.2877 | -0.21515 | -0.022888 | 1.6754 | 6.2805 | 6.5735 | 104.2969 | 122.5525 | 1.474 | 122.5616 | 13.7878 | -0.21515 | 122.5525 | 1.474 | 13.7878 | 104.2969 | 122.5616 | -122.7859 | -122.7997
2131.3281 | 122.9004 | -56.3324 | 66.2384 | -0.14145 | 0.018156 | 0.0046206 | 0.0365 | -0.0044028 | 0.0042703 | 0.049383 | -54.8538 | 66.1697 | -56.5613 | 52.2812 | 47.6212 | -43.5928 | -50.4776 | -50.1022 | 66.2201 | -56.5567 | -0.22888 | -0.068664 | 1.4786 | 108.6136 | -18.6172 | -0.22431 | -0.01831 | 1.7075 | 5.8548 | 6.2302 | 103.9536 | 122.5021 | 1.4786 | 122.5525 | 12.7396 | -0.22431 | 122.5021 | 1.4786 | 12.7396 | 103.9536 | 122.5525 | -122.7997 | -122.7951
2132.3281 | 122.9279 | -56.2546 | 66.3391 | 0.17136 | 0.017942 | 0.0073978 | 0.039277 | -0.0041892 | 0.0049111 | 0.048102 | -54.8309 | 66.2659 | -56.5018 | 51.9974 | 47.3923 | -43.6066 | -50.6058 | -50.2487 | 66.2933 | -56.4926 | -0.24719 | -0.073242 | 1.4236 | 108.252 | -18.9468 | -0.23804 | -0.045776 | 1.6708 | 5.6488 | 6.0059 | 103.6469 | 122.5204 | 1.4236 | 122.5479 | 12.648 | -0.23804 | 122.5204 | 1.4236 | 12.648 | 103.6469 | 122.5479 | -122.8409 | -122.8317
2133.3281 | 122.9645 | -56.2408 | 66.3757 | -0.14145 | 0.016233 | 0.007825 | 0.037141 | -0.00055764 | 0.0055521 | 0.049383 | -54.7623 | 66.3208 | -56.456 | 51.5671 | 47.0398 | -43.3868 | -50.1068 | -49.6902 | 66.3162 | -56.4743 | -0.21515 | -0.054931 | 1.4786 | 107.8079 | -19.3359 | -0.23346 | -0.059509 | 1.6937 | 6.134 | 6.5506 | 103.2806 | 122.5616 | 1.4786 | 122.5571 | 12.854 | -0.23346 | 122.5616 | 1.4786 | 12.854 | 103.2806 | 122.5571 | -122.8317 | -122.85
2134.3281 | 123.143 | -55.9296 | 66.7191 | -0.19485 | 0.018797 | 0.0071842 | 0.045685 | -0.0035482 | 0.0049111 | 0.062414 | -54.5059 | 66.6046 | -56.1584 | 51.2375 | 46.7697 | -46.3348 | -52.5604 | -52.4048 | 66.5955 | -56.163 | -0.22888 | -0.11444 | 1.4236 | 107.1671 | -19.9493 | -0.23346 | -0.1236 | 1.6525 | 3.3691 | 3.5248 | 102.6993 | 122.5342 | 1.4236 | 122.525 | 9.5947 | -0.23346 | 122.5342 | 1.4236 | 9.5947 | 102.6993 | 122.525 | -122.8775 | -122.8821
2135.3281 | 122.9507 | -56.3232 | 66.1926 | -0.1033 | 0.026274 | 0.0059024 | 0.07367 | -0.00098484 | 0.0023477 | 0.11454 | -54.5929 | 66.3986 | -56.0394 | 51.3611 | 47.7905 | -9.6588 | -48.6282 | -52.1759 | 66.1377 | -53.2196 | 0.28381 | 0.20599 | 1.7303 | 107.6843 | -18.4021 | 3.1036 | -0.054932 | 1.4465 | 7.695 | 4.1473 | 104.1138 | 122.7219 | 1.7303 | 122.4609 | 46.6644 | 3.1036 | 122.7219 | 1.7303 | 46.6644 | 104.1138 | 122.4609 | -122.2321 | -119.4122
2136.3281 | 122.8683 | -58.6716 | 64.0594 | 0.0035097 | 0.016233 | 0.009534 | 0.074097 | -0.010171 | 0.0055521 | 0.072882 | -57.431 | 63.6703 | -59.0973 | 55.3802 | 46.7148 | 2.9205 | -0.21515 | 1.3229 | 63.7756 | -58.3694 | -0.42572 | -0.3891 | 1.2405 | 114.0518 | -17.3447 | 0.30212 | -0.28381 | 1.6663 | 58.4564 | 59.9945 | 105.3864 | 122.3419 | 1.2405 | 122.4472 | 61.5921 | 0.30212 | 122.3419 | 1.2405 | 61.5921 | 105.3864 | 122.4472 | -123.1567 | -122.4289
2137.3281 | 122.3099 | -58.0261 | 64.0045 | -0.042267 | 0.018583 | 0.0029116 | 0.025391 | -0.0022666 | 0.02371 | 0.052374 | -56.4926 | 64.0778 | -58.1589 | 55.4764 | 21.9772 | 13.8199 | -0.48523 | 0.50812 | 64.0915 | -58.1406 | -0.13275 | 0.073242 | 1.5335 | 113.5025 | -42.0273 | -0.11444 | 0.086975 | 1.6663 | 57.5409 | 58.5342 | 80.0034 | 122.1039 | 1.5335 | 122.1176 | 71.846 | -0.11444 | 122.1039 | 1.5335 | 71.846 | 80.0034 | 122.1176 | -122.1634 | -122.1451
2138.3281 | 122.0215 | -52.5192 | 69.1498 | -0.049896 | 0.018583 | 0.006116 | 0.024964 | 0.049003 | 0.046781 | 0.12308 | -53.0045 | 67.1951 | -54.0619 | -40.4846 | -9.407 | -22.9431 | -47.1085 | -46.3806 | 68.9346 | -51.709 | -1.5427 | -1.9547 | -0.48523 | 12.0346 | -78.5568 | 0.81024 | -0.21515 | 1.0574 | 5.4108 | 6.1386 | 43.1122 | 119.7144 | -0.48523 | 121.4539 | 29.5761 | 0.81024 | 119.7144 | -0.48523 | 29.5761 | 43.1122 | 121.4539 | -123.2117 | -120.8588
2139.3281 | 122.4426 | -54.8035 | 67.218 | -0.080414 | 0.017729 | 0.0071842 | 0.20398 | -0.0011984 | 0.063871 | 0.28138 | -53.4943 | 67.1402 | -55.0552 | 48.349 | -55.0552 | 48.2025 | -17.7704 | -21.1029 | 67.2226 | -54.4281 | -0.25177 | -0.07782 | 1.3092 | 103.1525 | -122.2733 | 0.37537 | 0.004577 | 1.561 | 37.0331 | 33.7006 | -0.25177 | 121.9437 | 1.3092 | 122.0261 | 103.006 | 0.37537 | 121.9437 | 1.3092 | 103.006 | -0.25177 | 122.0261 | -122.2733 | -121.6461
2140.3281 | 122.4701 | -50.885 | 71.2738 | -0.057526 | 0.015806 | 0.0052616 | 0.034577 | 0.050071 | 0.063871 | 0.16431 | -49.53 | 71.2234 | -51.1276 | -45.8267 | -51.0132 | -46.5088 | -51.0727 | -50.7065 | 71.2097 | -51.123 | -0.24262 | -0.050354 | 1.355 | 5.0583 | -122.287 | -0.23804 | -0.064087 | 1.5976 | -0.18768 | 0.17853 | -0.12817 | 122.1085 | 1.355 | 122.0947 | 4.3762 | -0.23804 | 122.1085 | 1.355 | 4.3762 | -0.12817 | 122.0947 | -122.4014 | -122.3969
2141.3281 | 122.4792 | -50.5783 | 71.6492 | 0.041657 | 0.01901 | 0.0063296 | 0.0365 | 0.051139 | 0.059812 | 0.16602 | -49.2325 | 71.5713 | -50.8118 | -45.8725 | -50.7156 | -46.4447 | -50.7523 | -50.4227 | 71.5759 | -50.8072 | -0.23346 | -0.07782 | 1.3458 | 4.7058 | -122.3648 | -0.22888 | -0.073242 | 1.5793 | -0.17395 | 0.15564 | -0.13733 | 122.1497 | 1.3458 | 122.1542 | 4.1336 | -0.22888 | 122.1497 | 1.3458 | 4.1336 | -0.13733 | 122.1542 | -122.4609 | -122.4564
2142.3281 | 122.5433 | -50.3494 | 71.9376 | 0.095062 | 0.019438 | 0.007825 | 0.0365 | 0.051567 | 0.060881 | 0.16495 | -48.9899 | 71.8643 | -50.5417 | -45.6665 | -50.4868 | -46.17 | -50.386 | -50.1297 | 71.8735 | -50.5371 | -0.19226 | -0.073242 | 1.3596 | 4.6829 | -122.4243 | -0.18768 | -0.064087 | 1.5518 | -0.036621 | 0.21973 | -0.13733 | 122.2137 | 1.3596 | 122.2229 | 4.1794 | -0.18768 | 122.2137 | 1.3596 | 4.1794 | -0.13733 | 122.2229 | -122.4792 | -122.4747
2143.3281 | 122.5662 | -50.061 | 72.2351 | 0.14084 | 0.020078 | 0.0086796 | 0.040345 | 0.052635 | 0.064512 | 0.16645 | -48.6969 | 72.171 | -50.2762 | -45.5292 | -50.1984 | -46.0281 | -49.9191 | -49.6445 | 72.171 | -50.2625 | -0.21515 | -0.064086 | 1.3641 | 4.5319 | -122.4335 | -0.20142 | -0.064086 | 1.5793 | 0.14191 | 0.41656 | -0.13733 | 122.2321 | 1.3641 | 122.2321 | 4.0329 | -0.20142 | 122.2321 | 1.3641 | 4.0329 | -0.13733 | 122.2321 | -122.5113 | -122.4976
2144.3281 | 122.5662 | -51.4252 | 70.8847 | 0.19424 | 0.020078 | 0.0099612 | 0.037354 | 0.003715 | 0.059812 | 0.11796 | -50.0381 | 70.8481 | -51.6129 | 38.8779 | -51.5533 | 38.8138 | -48.3902 | -48.0972 | 70.8481 | -51.6174 | -0.18768 | -0.036622 | 1.387 | 90.303 | -122.4381 | -0.19226 | -0.036622 | 1.5747 | 3.035 | 3.3279 | -0.12817 | 122.2733 | 1.387 | 122.2733 | 90.239 | -0.19226 | 122.2733 | 1.387 | 90.239 | -0.12817 | 122.2733 | -122.4976 | -122.5021
2145.3281 | 122.58 | -51.265 | 71.0632 | 0.14847 | 0.021147 | 0.0091068 | 0.037354 | 0.004783 | 0.061735 | 0.11881 | -49.8688 | 71.0403 | -51.4709 | 37.3901 | -51.384 | 37.3123 | -47.0581 | -46.669 | 71.0266 | -51.4893 | -0.20599 | -0.022888 | 1.3962 | 88.6551 | -122.4472 | -0.2243 | -0.036621 | 1.6022 | 4.2068 | 4.5959 | -0.11902 | 122.3053 | 1.3962 | 122.2916 | 88.5773 | -0.2243 | 122.3053 | 1.3962 | 88.5773 | -0.11902 | 122.2916 | -122.5342 | -122.5525
2146.3281 | 122.5937 | -50.7706 | 71.5851 | 0.21713 | 0.018583 | 0.009534 | 0.0365 | 0.012901 | 0.063871 | 0.12436 | -49.4202 | 71.5439 | -50.972 | 25.7034 | -50.8942 | 25.946 | -46.138 | -45.845 | 71.5302 | -50.9537 | -0.20142 | -0.041199 | 1.3504 | 76.474 | -122.4792 | -0.1831 | -0.054932 | 1.5518 | 4.6326 | 4.9255 | -0.1236 | 122.3145 | 1.3504 | 122.3007 | 76.7166 | -0.1831 | 122.3145 | 1.3504 | 76.7166 | -0.1236 | 122.3007 | -122.5571 | -122.5388
2147.3281 | 122.6257 | -49.118 | 73.2422 | 0.16373 | 0.017729 | 0.0065432 | 0.03885 | 0.053275 | 0.06323 | 0.16431 | -47.7264 | 73.2056 | -49.3286 | -43.8171 | -49.2508 | -44.3161 | -47.1542 | -46.8796 | 73.1964 | -49.3195 | -0.21057 | -0.036621 | 1.3916 | 5.3009 | -122.493 | -0.20142 | -0.045776 | 1.6022 | 1.9638 | 2.2385 | -0.13275 | 122.3236 | 1.3916 | 122.3145 | 4.8019 | -0.20142 | 122.3236 | 1.3916 | 4.8019 | -0.13275 | 122.3145 | -122.5708 | -122.5616
2148.3281 | 122.644 | -48.7747 | 73.5489 | 0.1561 | 0.017729 | 0.0088932 | 0.037781 | 0.053489 | 0.061735 | 0.16538 | -47.4106 | 73.526 | -49.0448 | -43.9682 | -48.9304 | -44.458 | -46.8475 | -46.5683 | 73.5168 | -49.0082 | -0.27008 | -0.022888 | 1.3641 | 4.8065 | -122.4792 | -0.23346 | -0.032043 | 1.6342 | 1.9272 | 2.2064 | -0.15564 | 122.3007 | 1.3641 | 122.2916 | 4.3167 | -0.23346 | 122.3007 | 1.3641 | 4.3167 | -0.15564 | 122.2916 | -122.5937 | -122.5571
2149.3281 | 122.644 | -48.4909 | 73.8739 | 0.14847 | 0.020078 | 0.0080386 | 0.037995 | 0.052848 | 0.06259 | 0.16688 | -47.1268 | 73.8831 | -48.7015 | -43.6752 | -48.642 | -44.22 | -46.5408 | -46.2982 | 73.819 | -48.6969 | -0.21057 | 0.009156 | 1.3641 | 4.8157 | -122.5159 | -0.20599 | -0.054931 | 1.5747 | 1.9501 | 2.1927 | -0.15106 | 122.374 | 1.3641 | 122.3099 | 4.2709 | -0.20599 | 122.374 | 1.3641 | 4.2709 | -0.15106 | 122.3099 | -122.5754 | -122.5708
2150.3281 | 122.6532 | -48.2025 | 74.1806 | 0.17136 | 0.019865 | 0.0099612 | 0.039918 | 0.052635 | 0.059385 | 0.16538 | -46.7651 | 74.1806 | -48.3902 | -42.7917 | -48.2986 | -43.2907 | -46.6644 | -46.2982 | 74.1302 | -48.3902 | -0.18768 | 0 | 1.4374 | 5.4108 | -122.4792 | -0.18768 | -0.050354 | 1.6251 | 1.5381 | 1.9043 | -0.09613 | 122.3831 | 1.4374 | 122.3328 | 4.9118 | -0.18768 | 122.3831 | 1.4374 | 4.9118 | -0.09613 | 122.3328 | -122.5708 | -122.5708
2151.3281 | 122.6532 | -47.8912 | 74.5056 | 0.12558 | 0.018797 | 0.0088932 | 0.037995 | 0.053062 | 0.061735 | 0.16581 | -46.5088 | 74.4553 | -48.1155 | -43.6066 | -48.0331 | -44.0964 | -47.3282 | -47.0627 | 74.4507 | -48.0835 | -0.22431 | -0.050354 | 1.3824 | 4.2847 | -122.5388 | -0.19226 | -0.054931 | 1.6068 | 0.56305 | 0.82855 | -0.14191 | 122.3465 | 1.3824 | 122.3419 | 3.7949 | -0.19226 | 122.3465 | 1.3824 | 3.7949 | -0.14191 | 122.3419 | -122.6212 | -122.5891
2152.3281 | 122.6578 | -47.5067 | 74.8718 | 0.17136 | 0.019865 | 0.0073978 | 0.036286 | 0.051567 | 0.063658 | 0.16709 | -46.1014 | 74.8398 | -47.7493 | -43.8309 | -47.6395 | -44.3344 | -47.319 | -47.0169 | 74.826 | -47.7036 | -0.24262 | -0.032043 | 1.4053 | 3.6758 | -122.5113 | -0.19684 | -0.045776 | 1.648 | 0.18768 | 0.48981 | -0.13275 | 122.3465 | 1.4053 | 122.3328 | 3.1723 | -0.19684 | 122.3465 | 1.4053 | 3.1723 | -0.13275 | 122.3328 | -122.6212 | -122.5754
2153.3281 | 122.7127 | -47.2641 | 75.0916 | 0.17899 | 0.018583 | 0.0093204 | 0.039063 | 0.053916 | 0.06259 | 0.16559 | -45.8633 | 75.1007 | -47.5021 | -43.7439 | -47.4152 | -44.2703 | -47.2092 | -46.8475 | 75.0549 | -47.4976 | -0.23804 | 0.009155 | 1.4008 | 3.5202 | -122.5067 | -0.23346 | -0.036621 | 1.6388 | 0.054932 | 0.41656 | -0.15106 | 122.3648 | 1.4008 | 122.319 | 2.9938 | -0.23346 | 122.3648 | 1.4008 | 2.9938 | -0.15106 | 122.319 | -122.5937 | -122.5891
2154.3594 | 122.6807 | -46.8613 | 75.6088 | -0.21774 | 0.017942 | 0.010602 | 0.040558 | 0.052207 | 0.061949 | 0.16624 | -45.4193 | 75.5951 | -47.0581 | -43.3365 | -46.962 | -43.9087 | -46.8063 | -46.6095 | 75.5356 | -47.0718 | -0.19684 | -0.013733 | 1.442 | 3.5248 | -122.5708 | -0.21057 | -0.073243 | 1.6388 | 0.054932 | 0.25177 | -0.10071 | 122.4564 | 1.442 | 122.3969 | 2.9526 | -0.21057 | 122.4564 | 1.442 | 2.9526 | -0.10071 | 122.3969 | -122.6669 | -122.6807
2155.3281 | 122.6852 | -46.5271 | 75.8835 | 0.18662 | 0.020078 | 0.010816 | 0.041627 | 0.055198 | 0.06259 | 0.16837 | -45.0897 | 75.8698 | -46.7239 | -43.0206 | -46.6232 | -43.5608 | -46.7102 | -46.3577 | 75.8148 | -46.756 | -0.19684 | -0.013733 | 1.4374 | 3.5065 | -122.5067 | -0.22888 | -0.068665 | 1.6342 | -0.18311 | 0.16937 | -0.09613 | 122.3969 | 1.4374 | 122.3419 | 2.9663 | -0.22888 | 122.3969 | 1.4374 | 2.9663 | -0.09613 | 122.3419 | -122.6074 | -122.6395
2156.3438 | 122.6898 | -46.0327 | 76.4191 | -0.095673 | 0.017729 | 0.0086796 | 0.038636 | 0.054984 | 0.061094 | 0.16666 | -44.5816 | 76.3687 | -46.2433 | -42.5308 | -46.1105 | -43.103 | -46.2204 | -45.8588 | 76.3596 | -46.2341 | -0.21057 | -0.050354 | 1.4511 | 3.5019 | -122.5296 | -0.20142 | -0.059509 | 1.6617 | -0.18768 | 0.17395 | -0.07782 | 122.4014 | 1.4511 | 122.3923 | 2.9297 | -0.20142 | 122.4014 | 1.4511 | 2.9297 | -0.07782 | 122.3923 | -122.6624 | -122.6532
2157.3281 | 122.7951 | -45.575 | 76.8356 | 0.18662 | 0.020933 | 0.012952 | 0.042695 | 0.056907 | 0.061949 | 0.16923 | -44.1101 | 76.8402 | -45.7718 | -42.2333 | -45.6619 | -42.7505 | -45.8176 | -45.4239 | 76.799 | -45.7764 | -0.19684 | 0.004578 | 1.4648 | 3.3417 | -122.4976 | -0.20142 | -0.036621 | 1.6617 | -0.24262 | 0.15106 | -0.086975 | 122.4152 | 1.4648 | 122.374 | 2.8244 | -0.20142 | 122.4152 | 1.4648 | 2.8244 | -0.086975 | 122.374 | -122.6074 | -122.612
2158.3281 | 122.7219 | -45.0256 | 77.3987 | 0.1561 | 0.019438 | 0.011029 | 0.043122 | 0.054984 | 0.061949 | 0.16901 | -43.6157 | 77.4078 | -45.2316 | -41.6428 | -45.1767 | -42.1875 | -45.2911 | -44.9478 | 77.3346 | -45.2499 | -0.20599 | 0.009155 | 1.4099 | 3.3829 | -122.5754 | -0.2243 | -0.064087 | 1.6159 | -0.2655 | 0.07782 | -0.15106 | 122.4335 | 1.4099 | 122.3602 | 2.8381 | -0.2243 | 122.4335 | 1.4099 | 2.8381 | -0.15106 | 122.3602 | -122.6303 | -122.6486
2159.3281 | 122.1085 | -47.0032 | 74.8077 | 0.24765 | 0.022428 | 0.010388 | 0.030518 | 0.040458 | 0.063871 | 0.14573 | -45.4971 | 74.7482 | -47.2733 | -10.9314 | -47.0947 | -11.0184 | -14.0167 | -13.9755 | 74.7665 | -47.2046 | -0.27008 | -0.059509 | 1.506 | 36.0718 | -121.9025 | -0.20142 | -0.041198 | 1.7761 | 32.9865 | 33.0276 | -0.091553 | 121.7514 | 1.506 | 121.7697 | 35.9848 | -0.20142 | 121.7514 | 1.506 | 35.9848 | -0.091553 | 121.7697 | -122.081 | -122.0123
2160.3438 | 122.2504 | -44.632 | 77.3163 | 0.1561 | 0.021147 | 0.0063296 | 0.03415 | 0.049217 | 0.063444 | 0.16068 | -43.2495 | 77.2934 | -44.8929 | -30.3131 | -44.8151 | -30.2994 | -32.8629 | -32.7484 | 77.2797 | -44.8654 | -0.26093 | -0.022888 | 1.3824 | 14.3188 | -122.1313 | -0.23346 | -0.036621 | 1.6434 | 11.7691 | 11.8835 | -0.18311 | 121.9254 | 1.3824 | 121.9116 | 14.3326 | -0.23346 | 121.9254 | 1.3824 | 14.3326 | -0.18311 | 121.9116 | -122.2092 | -122.1817
2161.3438 | 122.2458 | -44.2108 | 77.9022 | -0.20248 | 0.019224 | 0.0091068 | 0.037354 | 0.049644 | 0.062803 | 0.16025 | -42.778 | 77.8564 | -44.4031 | -30.7571 | -44.3527 | -30.7846 | -32.634 | -32.7484 | 77.8473 | -44.4031 | -0.19226 | -0.045777 | 1.4328 | 13.4537 | -122.2549 | -0.19226 | -0.054932 | 1.6251 | 11.5768 | 11.4624 | -0.14191 | 122.0673 | 1.4328 | 122.0581 | 13.4262 | -0.19226 | 122.0673 | 1.4328 | 13.4262 | -0.14191 | 122.0581 | -122.3053 | -122.3053
2162.3281 | 122.3373 | -43.8263 | 78.2501 | 0.087433 | 0.022642 | 0.0076114 | 0.027955 | 0.053275 | 0.062803 | 0.16196 | -42.4438 | 78.2684 | -44.0414 | -30.5283 | -44.0231 | -30.5328 | -32.4738 | -32.4783 | 78.1906 | -44.0552 | -0.21515 | 0.018311 | 1.3824 | 13.298 | -122.2733 | -0.22888 | -0.059509 | 1.5976 | 11.3525 | 11.348 | -0.19684 | 122.0947 | 1.3824 | 122.0169 | 13.2935 | -0.22888 | 122.0947 | 1.3824 | 13.2935 | -0.19684 | 122.0169 | -122.2916 | -122.3053
2163.3281 | 122.4106 | -42.8146 | 79.2847 | 0.22476 | 0.019438 | 0.011029 | 0.041199 | 0.052848 | 0.063871 | 0.16282 | -41.3452 | 79.303 | -43.0435 | -35.1654 | -42.9565 | -35.0876 | -37.5458 | -37.3627 | 79.1656 | -43.071 | -0.22888 | 0.018311 | 1.4694 | 7.6492 | -122.2412 | -0.25635 | -0.11902 | 1.6983 | 5.2689 | 5.452 | -0.14191 | 122.1176 | 1.4694 | 121.9803 | 7.7271 | -0.25635 | 122.1176 | 1.4694 | 7.7271 | -0.14191 | 121.9803 | -122.3282 | -122.3557
2164.3281 | 122.4564 | -41.9724 | 80.1407 | 0.20187 | 0.019865 | 0.011457 | 0.039063 | 0.056907 | 0.061094 | 0.16431 | -40.5396 | 80.1453 | -42.2195 | -38.8641 | -42.128 | -39.1708 | -39.7659 | -39.5828 | 80.0766 | -42.2058 | -0.24719 | 0.004578 | 1.4328 | 3.1082 | -122.2687 | -0.23346 | -0.064087 | 1.68 | 2.2064 | 2.3895 | -0.15564 | 122.1176 | 1.4328 | 122.049 | 2.8015 | -0.23346 | 122.1176 | 1.4328 | 2.8015 | -0.15564 | 122.049 | -122.3602 | -122.3465
2165.3281 | 122.4564 | -41.4093 | 80.7129 | 0.26291 | 0.022642 | 0.012952 | 0.039704 | 0.057548 | 0.06323 | 0.16666 | -39.9765 | 80.7449 | -41.6656 | -39.1479 | -41.5833 | -39.505 | -39.8621 | -39.6103 | 80.6992 | -41.6382 | -0.25635 | 0.032043 | 1.4328 | 2.2614 | -122.2961 | -0.22888 | -0.013733 | 1.6891 | 1.5472 | 1.799 | -0.17395 | 122.1542 | 1.4328 | 122.1085 | 1.9043 | -0.22888 | 122.1542 | 1.4328 | 1.9043 | -0.17395 | 122.1085 | -122.3785 | -122.3511
2166.3438 | 122.3831 | -40.9058 | 81.3538 | -0.16434 | 0.022215 | 0.01167 | 0.038209 | 0.058189 | 0.062803 | 0.16794 | -39.4638 | 81.4133 | -41.0889 | -38.9328 | -41.066 | -39.3173 | -39.3402 | -39.3311 | 81.3309 | -41.1209 | -0.1831 | 0.059509 | 1.442 | 1.973 | -122.4197 | -0.21515 | -0.022888 | 1.6251 | 1.5656 | 1.5747 | -0.16022 | 122.319 | 1.442 | 122.2366 | 1.5884 | -0.21515 | 122.319 | 1.442 | 1.5884 | -0.16022 | 122.2366 | -122.4426 | -122.4747
2167.3594 | 122.438 | -40.2054 | 82.0404 | -0.057526 | 0.023924 | 0.011457 | 0.042267 | 0.058616 | 0.06259 | 0.16709 | -38.7405 | 82.0679 | -40.4205 | -38.3789 | -40.3427 | -38.6124 | -38.8321 | -38.6948 | 82.0129 | -40.4434 | -0.21515 | 0.027466 | 1.4648 | 1.8265 | -122.3831 | -0.23804 | -0.027466 | 1.68 | 1.3733 | 1.5106 | -0.13733 | 122.2733 | 1.4648 | 122.2183 | 1.593 | -0.23804 | 122.2733 | 1.4648 | 1.593 | -0.13733 | 122.2183 | -122.4609 | -122.4838
2168.3281 | 122.525 | -39.6561 | 82.5165 | 0.18662 | 0.021787 | 0.012311 | 0.03885 | 0.060111 | 0.061735 | 0.16987 | -38.1683 | 82.5714 | -39.8758 | -38.205 | -39.7888 | -38.5574 | -38.7817 | -38.4842 | 82.5073 | -39.8804 | -0.21973 | 0.054932 | 1.4877 | 1.4511 | -122.3053 | -0.2243 | -0.009155 | 1.7075 | 0.87433 | 1.1719 | -0.13275 | 122.2275 | 1.4877 | 122.1634 | 1.0986 | -0.2243 | 122.2275 | 1.4877 | 1.0986 | -0.13275 | 122.1634 | -122.3923 | -122.3969
2169.3594 | 122.4976 | -38.7634 | 83.4366 | -0.13382 | 0.020078 | 0.0076114 | 0.0318 | 0.055625 | 0.059812 | 0.16666 | -37.294 | 83.4549 | -38.9923 | -37.2986 | -38.6627 | -38.063 | -38.1226 | -37.7792 | 83.4045 | -38.9694 | -0.22888 | 0.018311 | 1.4694 | 1.4648 | -122.0993 | -0.20599 | -0.032043 | 1.6983 | 0.64087 | 0.98419 | 0.10071 | 122.2183 | 1.4694 | 122.168 | 0.70038 | -0.20599 | 122.2183 | 1.4694 | 0.70038 | 0.10071 | 122.168 | -122.4289 | -122.406
2170.3281 | 122.5159 | -38.2004 | 84.0317 | 0.2095 | 0.022642 | 0.007825 | 0.040558 | 0.059257 | 0.061308 | 0.16559 | -36.6943 | 84.0958 | -38.4018 | -37.1338 | -38.356 | -37.4405 | -37.5412 | -37.3032 | 84.0225 | -38.4109 | -0.20142 | 0.064087 | 1.506 | 1.0666 | -122.3877 | -0.21057 | -0.009155 | 1.7075 | 0.65918 | 0.89722 | -0.15564 | 122.2961 | 1.506 | 122.2229 | 0.75989 | -0.21057 | 122.2961 | 1.506 | 0.75989 | -0.15564 | 122.2229 | -122.4335 | -122.4426
2171.375 | 122.4564 | -37.4771 | 84.819 | -0.0041198 | 0.024137 | 0.012097 | 0.042267 | 0.059684 | 0.062162 | 0.16837 | -35.8933 | 84.9014 | -37.6419 | -36.4105 | -37.6328 | -36.7722 | -36.731 | -36.5799 | 84.8053 | -37.6831 | -0.1648 | 0.082397 | 1.5839 | 1.0666 | -122.4518 | -0.20599 | -0.013733 | 1.7487 | 0.74616 | 0.89722 | -0.15564 | 122.3785 | 1.5839 | 122.2824 | 0.70496 | -0.20599 | 122.3785 | 1.5839 | 0.70496 | -0.15564 | 122.2824 | -122.4609 | -122.5021
2172.3281 | 122.4609 | -36.7722 | 85.4919 | 0.19424 | 0.023069 | 0.013166 | 0.03885 | 0.061393 | 0.061735 | 0.16944 | -35.257 | 85.556 | -37.0148 | -35.9207 | -36.9965 | -36.2411 | -36.1633 | -36.0168 | 85.4874 | -37.0102 | -0.24262 | 0.064087 | 1.5152 | 0.85144 | -122.4884 | -0.23804 | -0.004577 | 1.7578 | 0.60883 | 0.75531 | -0.2243 | 122.3282 | 1.5152 | 122.2595 | 0.53101 | -0.23804 | 122.3282 | 1.5152 | 0.53101 | -0.2243 | 122.2595 | -122.5067 | -122.5021
2173.3594 | 122.4518 | -36.1496 | 86.1694 | 0.072174 | 0.023496 | 0.0093204 | 0.043336 | 0.060325 | 0.061308 | 0.1688 | -34.5566 | 86.2793 | -36.351 | -35.3348 | -36.3373 | -35.6689 | -35.4996 | -35.4218 | 86.1603 | -36.351 | -0.20142 | 0.10986 | 1.593 | 0.81482 | -122.5067 | -0.20142 | -0.009156 | 1.7944 | 0.65002 | 0.72784 | -0.18768 | 122.4289 | 1.593 | 122.3099 | 0.48065 | -0.20142 | 122.4289 | 1.593 | 0.48065 | -0.18768 | 122.3099 | -122.5204 | -122.5204
2174.3281 | 122.5296 | -35.5637 | 86.6959 | 0.21713 | 0.022215 | 0.010175 | 0.036927 | 0.059898 | 0.061735 | 0.17008 | -33.9844 | 86.7828 | -35.7925 | -34.7351 | -35.7513 | -35.0327 | -35.0143 | -34.7992 | 86.7279 | -35.7971 | -0.22888 | 0.086975 | 1.5793 | 0.82855 | -122.4472 | -0.23346 | 0.032043 | 1.8082 | 0.54932 | 0.76447 | -0.18768 | 122.3465 | 1.5793 | 122.2916 | 0.53101 | -0.23346 | 122.3465 | 1.5793 | 0.53101 | -0.18768 | 122.2916 | -122.4884 | -122.493
2175.3594 | 122.5204 | -34.8999 | 87.4146 | -0.1033 | 0.02371 | 0.012952 | 0.041627 | 0.060966 | 0.062376 | 0.16987 | -33.2245 | 87.5061 | -35.1105 | -34.0576 | -35.0601 | -34.3872 | -34.2499 | -34.1034 | 87.4512 | -35.1196 | -0.21057 | 0.091553 | 1.6754 | 0.84228 | -122.4747 | -0.21973 | 0.036621 | 1.886 | 0.65002 | 0.79651 | -0.16022 | 122.406 | 1.6754 | 122.3511 | 0.5127 | -0.21973 | 122.406 | 1.6754 | 0.5127 | -0.16022 | 122.3511 | -122.525 | -122.5342
2176.3438 | 122.5616 | -34.2041 | 88.1104 | -0.13382 | 0.019651 | 0.0093204 | 0.033936 | 0.059684 | 0.059385 | 0.17051 | -32.5058 | 88.0829 | -34.4192 | -33.3755 | -34.314 | -33.6502 | -33.6685 | -33.3572 | 88.0875 | -34.3735 | -0.21515 | -0.027466 | 1.6983 | 0.82855 | -122.4243 | -0.16937 | -0.022889 | 1.9135 | 0.53558 | 0.84686 | -0.10986 | 122.287 | 1.6983 | 122.2916 | 0.55389 | -0.16937 | 122.287 | 1.6983 | 0.55389 | -0.10986 | 122.2916 | -122.5296 | -122.4838
2177.3594 | 122.4884 | -33.5907 | 88.7833 | -0.19485 | 0.022215 | 0.01167 | 0.039704 | 0.060325 | 0.06259 | 0.17072 | -31.9199 | 88.7741 | -33.8196 | -32.9819 | -33.8287 | -33.1467 | -32.7942 | -33.0734 | 88.829 | -33.7555 | -0.22888 | -0.009155 | 1.6708 | 0.60883 | -122.612 | -0.16479 | 0.045777 | 1.8997 | 0.79651 | 0.51727 | -0.23804 | 122.3648 | 1.6708 | 122.4197 | 0.44403 | -0.16479 | 122.3648 | 1.6708 | 0.44403 | -0.23804 | 122.4197 | -122.6028 | -122.5388
2178.3281 | 122.4518 | -32.9636 | 89.3875 | -0.47714 | 0.022642 | 0.015943 | 0.042481 | 0.060111 | 0.063017 | 0.17051 | -31.2836 | 89.4928 | -33.1833 | -32.5058 | -33.2245 | -32.7988 | -32.5287 | -32.4738 | 89.3784 | -33.2108 | -0.21973 | 0.10529 | 1.68 | 0.45776 | -122.612 | -0.24719 | -0.009155 | 1.8997 | 0.43488 | 0.48981 | -0.26093 | 122.4564 | 1.68 | 122.3419 | 0.1648 | -0.24719 | 122.4564 | 1.68 | 0.1648 | -0.26093 | 122.3419 | -122.5708 | -122.5983
2179.3594 | 122.5525 | -32.3639 | 89.9551 | -0.17197 | 0.021147 | 0.0048342 | 0.035432 | 0.056053 | 0.064298 | 0.17051 | -30.5649 | 89.9872 | -32.5699 | -31.8192 | -32.4966 | -32.0892 | -31.9839 | -31.7184 | 89.9734 | -32.5333 | -0.20599 | 0.032044 | 1.799 | 0.54474 | -122.4518 | -0.16937 | 0.018311 | 2.005 | 0.37994 | 0.64545 | -0.13275 | 122.3511 | 1.799 | 122.3373 | 0.27466 | -0.16937 | 122.3511 | 1.799 | 0.27466 | -0.13275 | 122.3373 | -122.525 | -122.4884
2180.3281 | 122.5021 | -31.7368 | 90.6418 | 0.16373 | 0.026487 | 0.013806 | 0.040345 | 0.058189 | 0.061308 | 0.17222 | -29.8508 | 90.7379 | -31.9336 | -31.2973 | -31.9565 | -31.5537 | -31.3248 | -31.2241 | 90.6876 | -31.9244 | -0.19684 | 0.09613 | 1.886 | 0.43945 | -122.5983 | -0.18768 | 0.045776 | 2.0828 | 0.41199 | 0.51269 | -0.21973 | 122.4747 | 1.886 | 122.4243 | 0.1831 | -0.18768 | 122.4747 | 1.886 | 0.1831 | -0.21973 | 122.4243 | -122.5754 | -122.5662
2181.375 | 122.525 | -31.0776 | 91.2689 | -0.072784 | 0.020933 | 0.012311 | 0.032654 | 0.055839 | 0.06024 | 0.17435 | -29.1367 | 91.2415 | -31.2744 | -30.5466 | -31.1646 | -30.7983 | -30.7892 | -30.0842 | 91.301 | -31.2332 | -0.19684 | -0.027466 | 1.9409 | 0.53101 | -122.4335 | -0.15564 | 0.032043 | 2.1378 | 0.28839 | 0.99335 | -0.086975 | 122.319 | 1.9409 | 122.3785 | 0.27924 | -0.15564 | 122.319 | 1.9409 | 0.27924 | -0.086975 | 122.3785 | -122.5433 | -122.5021
2182.3281 | 122.4884 | -30.5099 | 91.9052 | 0.087433 | 0.024351 | 0.013806 | 0.044831 | 0.059684 | 0.061094 | 0.17158 | -28.5645 | 91.9876 | -30.7068 | -30.1071 | -30.7205 | -30.3726 | -30.0797 | -30.0522 | 91.9144 | -30.7205 | -0.19684 | 0.082398 | 1.9455 | 0.40283 | -122.6257 | -0.21057 | 0.009156 | 2.1423 | 0.4303 | 0.45776 | -0.21057 | 122.4976 | 1.9455 | 122.4243 | 0.13733 | -0.21057 | 122.4976 | 1.9455 | 0.13733 | -0.21057 | 122.4243 | -122.612 | -122.6257
2183.3594 | 122.5479 | -29.8141 | 92.5964 | -0.072784 | 0.022642 | 0.014234 | 0.043336 | 0.05883 | 0.062376 | 0.1735 | -27.8412 | 92.6559 | -30.0201 | -29.3793 | -29.9881 | -29.6448 | -29.4342 | -29.2877 | 92.6193 | -30.0339 | -0.20599 | 0.059509 | 1.973 | 0.43488 | -122.5845 | -0.21973 | 0.022888 | 2.179 | 0.37994 | 0.52643 | -0.17395 | 122.4701 | 1.973 | 122.4335 | 0.16937 | -0.21973 | 122.4701 | 1.973 | 0.16937 | -0.17395 | 122.4335 | -122.6166 | -122.6303
2184.3281 | 122.5113 | -29.1779 | 93.2327 | 0.049286 | 0.026274 | 0.0080386 | 0.044404 | 0.06182 | 0.061094 | 0.17393 | -27.1866 | 93.3289 | -29.3564 | -28.8071 | -29.393 | -29.068 | -28.8025 | -28.7338 | 93.2602 | -29.4067 | -0.17853 | 0.09613 | 1.9913 | 0.37079 | -122.6257 | -0.22888 | 0.027466 | 2.1698 | 0.37537 | 0.44403 | -0.21515 | 122.5067 | 1.9913 | 122.438 | 0.10986 | -0.22888 | 122.5067 | 1.9913 | 0.10986 | -0.21515 | 122.438 | -122.5891 | -122.6395
2185.3594 | 122.6028 | -28.3585 | 94.0384 | -0.19485 | 0.021147 | 0.012525 | 0.037568 | 0.057762 | 0.063658 | 0.17286 | -26.3489 | 94.0475 | -28.569 | -27.9419 | -28.5141 | -28.1662 | -28.006 | -27.8137 | 94.0247 | -28.5599 | -0.21057 | 0.009155 | 2.0096 | 0.41656 | -122.5525 | -0.20142 | -0.013733 | 2.2202 | 0.35248 | 0.54474 | -0.15564 | 122.406 | 2.0096 | 122.3831 | 0.19226 | -0.20142 | 122.406 | 2.0096 | 0.19226 | -0.15564 | 122.3831 | -122.6074 | -122.5983
2186.3438 | 122.5433 | -27.6535 | 94.7983 | -0.16434 | 0.021787 | 0.011457 | 0.044617 | 0.060325 | 0.064085 | 0.17542 | -25.6027 | 94.8624 | -27.8641 | -27.6398 | -27.8549 | -27.9007 | -27.5299 | -27.4521 | 94.8257 | -27.8412 | -0.21057 | 0.064087 | 2.0508 | 0.013732 | -122.6532 | -0.18768 | 0.027466 | 2.2614 | 0.1236 | 0.20142 | -0.20142 | 122.5159 | 2.0508 | 122.4792 | -0.24719 | -0.18768 | 122.5159 | 2.0508 | -0.24719 | -0.20142 | 122.4792 | -122.6624 | -122.6395
2187.3594 | 122.6669 | -26.9073 | 95.4529 | -0.011749 | 0.022215 | 0.013806 | 0.033936 | 0.05883 | 0.061308 | 0.17414 | -24.8474 | 95.4575 | -27.1179 | -26.9028 | -27.0538 | -27.1133 | -26.9943 | -26.6464 | 95.4895 | -27.1179 | -0.21057 | 0.004577 | 2.0599 | 0.004578 | -122.5067 | -0.21057 | 0.036621 | 2.2705 | -0.086975 | 0.26093 | -0.14648 | 122.3648 | 2.0599 | 122.3969 | -0.20599 | -0.21057 | 122.3648 | 2.0599 | -0.20599 | -0.14648 | 122.3969 | -122.5708 | -122.5708
2188.3281 | 122.5067 | -26.2848 | 96.1624 | 0.14084 | 0.024565 | 0.012952 | 0.046754 | 0.058189 | 0.063444 | 0.17457 | -24.1653 | 96.2448 | -26.4999 | -26.3489 | -26.5182 | -26.5961 | -26.1795 | -26.1566 | 96.167 | -26.5091 | -0.21515 | 0.082397 | 2.1194 | -0.064087 | -122.6807 | -0.2243 | 0.004577 | 2.3346 | 0.10529 | 0.12817 | -0.23346 | 122.5296 | 2.1194 | 122.4518 | -0.31128 | -0.2243 | 122.5296 | 2.1194 | -0.31128 | -0.23346 | 122.4518 | -122.6624 | -122.6715
2189.3594 | 122.6532 | -25.6027 | 96.7804 | -0.14145 | 0.022642 | 0.011884 | 0.037141 | 0.05883 | 0.066007 | 0.17563 | -23.4238 | 96.8124 | -25.7858 | -25.5981 | -25.7401 | -25.7996 | -25.6577 | -25.3235 | 96.8079 | -25.8041 | -0.18311 | 0.032043 | 2.179 | 0.004577 | -122.5204 | -0.20142 | 0.027465 | 2.3621 | -0.054932 | 0.27924 | -0.13733 | 122.4152 | 2.179 | 122.4106 | -0.19684 | -0.20142 | 122.4152 | 2.179 | -0.19684 | -0.13733 | 122.4106 | -122.5662 | -122.5845
2190.3281 | 122.612 | -25.0351 | 97.3709 | 0.20187 | 0.026487 | 0.013593 | 0.046113 | 0.060325 | 0.064726 | 0.17628 | -22.8378 | 97.4442 | -25.2365 | -25.0763 | -25.2228 | -25.2731 | -25.0717 | -24.8199 | 97.3984 | -25.2457 | -0.20142 | 0.073242 | 2.1973 | -0.041199 | -122.5937 | -0.21057 | 0.027465 | 2.3987 | -0.036621 | 0.21515 | -0.18768 | 122.4792 | 2.1973 | 122.4335 | -0.23804 | -0.21057 | 122.4792 | 2.1973 | -0.23804 | -0.18768 | 122.4335 | -122.6074 | -122.6166
2191.375 | 122.6074 | -24.4583 | 97.9385 | 0.087433 | 0.022215 | 0.01167 | 0.037354 | 0.056266 | 0.062376 | 0.1782 | -22.3068 | 97.9294 | -24.6735 | -24.5224 | -24.6552 | -24.7009 | -24.4904 | -24.234 | 97.9614 | -24.6414 | -0.21515 | -0.009156 | 2.1515 | -0.064087 | -122.5937 | -0.18311 | 0.022888 | 2.3666 | -0.032043 | 0.2243 | -0.19684 | 122.3877 | 2.1515 | 122.4197 | -0.24262 | -0.18311 | 122.3877 | 2.1515 | -0.24262 | -0.19684 | 122.4197 | -122.612 | -122.58
2192.3438 | 122.5388 | -23.9548 | 98.5062 | 0.095062 | 0.025205 | 0.014661 | 0.048676 | 0.059898 | 0.063017 | 0.17521 | -21.7117 | 98.5657 | -24.1516 | -24.0189 | -24.1745 | -24.2477 | -23.8586 | -23.8037 | 98.5291 | -24.1608 | -0.19684 | 0.059509 | 2.243 | -0.064087 | -122.6807 | -0.20599 | 0.022888 | 2.4399 | 0.09613 | 0.15106 | -0.21973 | 122.5204 | 2.243 | 122.4838 | -0.29297 | -0.20599 | 122.5204 | 2.243 | -0.29297 | -0.21973 | 122.4838 | -122.6578 | -122.6669
2193.3594 | 122.6349 | -25.502 | 96.8811 | -0.19485 | 0.014097 | -0.0049924 | 0.037354 | 0.057762 | 0.059812 | 0.17991 | -0.018311 | 0.068665 | -0.23804 | -25.4883 | -25.7401 | -25.5432 | -25.5432 | -25.5112 | 96.9131 | -25.708 | 25.264 | -96.8124 | 25.4837 | 0.013733 | -122.6212 | -0.20599 | 0.032043 | 0.21973 | -0.041199 | -0.009155 | -0.23804 | 25.5707 | 25.4837 | 122.4152 | -0.041199 | -0.20599 | 25.5707 | 25.4837 | -0.041199 | -0.23804 | 122.4152 | -97.1191 | -122.5891
2194.3438 | 122.7081 | -24.9664 | 97.4304 | 0.2858 | 0.017515 | -0.0047788 | 0.043122 | 0.058616 | 0.06259 | 0.17948 | 0.018311 | 0.050354 | -0.22888 | -24.9435 | -25.0763 | -25.1495 | -25.0809 | -24.9664 | 97.4258 | -25.1816 | 24.7375 | -97.3801 | 24.9847 | 0.022889 | -122.5067 | -0.21515 | -0.004578 | 0.24719 | -0.11444 | 0 | -0.10986 | 25.0168 | 24.9847 | 122.3923 | -0.18311 | -0.21515 | 25.0168 | 24.9847 | -0.18311 | -0.10986 | 122.3923 | -97.6593 | -122.612
2195.3594 | 122.6212 | -24.3118 | 98.1171 | -0.21774 | 0.013029 | -0.003497 | 0.043122 | 0.057121 | 0.062162 | 0.17969 | 0.004578 | 0.09613 | -0.21973 | -24.3301 | -24.4629 | -24.5361 | -24.2798 | -24.0646 | 98.1262 | -24.5316 | 24.0921 | -98.0209 | 24.3164 | -0.01831 | -122.58 | -0.21973 | 0.009156 | 0.22431 | 0.032044 | 0.24719 | -0.15106 | 24.408 | 24.3164 | 122.4381 | -0.2243 | -0.21973 | 24.408 | 24.3164 | -0.2243 | -0.15106 | 122.4381 | -98.3368 | -122.6486
2196.3594 | 122.5845 | -23.6984 | 98.7991 | -0.50766 | 0.019438 | -0.0047788 | 0.048463 | 0.057762 | 0.063444 | 0.17948 | -0.07782 | 0.11902 | -0.24261 | -23.7488 | -23.8998 | -23.9685 | -23.6252 | -23.5245 | 98.8037 | -23.877 | 23.4558 | -98.6801 | 23.6206 | -0.050354 | -122.699 | -0.17853 | 0.004578 | 0.16479 | 0.073242 | 0.17395 | -0.20142 | 23.8174 | 23.6206 | 122.5021 | -0.27008 | -0.17853 | 23.8174 | 23.6206 | -0.27008 | -0.20142 | 122.5021 | -99.0417 | -122.6761
2197.3594 | 122.6395 | -22.9935 | 99.4308 | 0.19424 | 0.017942 | -0.0024288 | 0.044404 | 0.058616 | 0.059812 | 0.18247 | 0.022888 | 0.082397 | -0.20142 | -23.0118 | -23.14 | -23.1949 | -23.0713 | -22.7417 | 99.4354 | -23.2178 | 22.7921 | -99.3484 | 23.0164 | -0.018311 | -122.5708 | -0.2243 | 0.004578 | 0.2243 | -0.07782 | 0.25177 | -0.14648 | 23.0759 | 23.0164 | 122.4289 | -0.20142 | -0.2243 | 23.0759 | 23.0164 | -0.20142 | -0.14648 | 122.4289 | -99.6323 | -122.6486
2198.3438 | 122.6486 | -22.4396 | 100.0122 | 0.20187 | 0.018797 | -0.0022152 | 0.049744 | 0.059043 | 0.063444 | 0.1829 | 0.004578 | 0.09613 | -0.22888 | -22.4533 | -22.6135 | -22.6685 | -22.4625 | -22.2015 | 100.0031 | -22.6547 | 22.2107 | -99.9161 | 22.4442 | -0.013733 | -122.6257 | -0.21515 | -0.009155 | 0.23346 | -0.022888 | 0.23804 | -0.17395 | 22.5357 | 22.4442 | 122.4426 | -0.22888 | -0.21515 | 22.5357 | 22.4442 | -0.22888 | -0.17395 | 122.4426 | -100.2411 | -122.6669
2199.3594 | 122.7173 | -21.936 | 100.4837 | -0.11856 | 0.014311 | -0.0081968 | 0.043336 | 0.056693 | 0.063444 | 0.18397 | 0.050354 | 0.09613 | -0.18768 | -21.8674 | -22.0413 | -22.0963 | -21.9589 | -21.5607 | 100.4883 | -22.1512 | 21.7484 | -100.3876 | 21.9864 | 0.068664 | -122.525 | -0.21515 | 0.004577 | 0.23804 | -0.022888 | 0.37537 | -0.10529 | 22.0322 | 21.9864 | 122.4243 | -0.16022 | -0.21515 | 22.0322 | 21.9864 | -0.16022 | -0.10529 | 122.4243 | -100.6714 | -122.6349
2200.3438 | 122.699 | -21.2814 | 101.1154 | 0.19424 | 0.016233 | -0.0041378 | 0.049103 | 0.057121 | 0.060667 | 0.1861 | 0.054932 | 0.086975 | -0.20599 | -21.2585 | -21.4462 | -21.4783 | -21.3318 | -20.9885 | 101.1566 | -21.4966 | 21.0754 | -101.0284 | 21.3364 | 0.022888 | -122.5616 | -0.21515 | 0.041199 | 0.26093 | -0.050354 | 0.29297 | -0.1648 | 21.3684 | 21.3364 | 122.438 | -0.19684 | -0.21515 | 21.3684 | 21.3364 | -0.19684 | -0.1648 | 122.438 | -101.3214 | -122.612
2201.375 | 122.6349 | -20.7138 | 101.7151 | -0.19485 | 0.01132 | -0.005206 | 0.047822 | 0.058402 | 0.061949 | 0.18674 | 0.050354 | 0.10071 | -0.19226 | -20.6406 | -20.8328 | -20.9152 | -20.5948 | -20.3384 | 101.7471 | -20.9152 | 20.5215 | -101.6144 | 20.7642 | 0.073242 | -122.5479 | -0.20142 | 0.032043 | 0.24261 | 0.11902 | 0.37537 | -0.11902 | 20.8145 | 20.7642 | 122.4609 | -0.20142 | -0.20142 | 20.8145 | 20.7642 | -0.20142 | -0.11902 | 122.4609 | -101.9073 | -122.6303
2202.3438 | 122.6807 | -20.2194 | 102.2232 | 0.19424 | 0.013029 | -0.0037106 | 0.050812 | 0.056266 | 0.061949 | 0.18482 | 0.045776 | 0.086975 | -0.1831 | -20.1599 | -20.3339 | -20.3842 | -20.2377 | -19.8624 | 102.2232 | -20.4208 | 20.0363 | -102.1362 | 20.2652 | 0.059509 | -122.5571 | -0.20142 | 0 | 0.22888 | -0.018311 | 0.35705 | -0.11444 | 20.3064 | 20.2652 | 122.4426 | -0.16479 | -0.20142 | 20.3064 | 20.2652 | -0.16479 | -0.11444 | 122.4426 | -102.4063 | -122.644
2203.3594 | 122.6944 | -19.5511 | 102.887 | -0.049896 | 0.014311 | -0.0043514 | 0.049317 | 0.054771 | 0.062803 | 0.18867 | 0.027466 | 0.10529 | -0.18768 | -19.5236 | -19.6976 | -19.7388 | -19.4778 | -19.1391 | 102.8687 | -19.7525 | 19.3634 | -102.7817 | 19.5786 | 0.027465 | -122.5845 | -0.20142 | -0.018311 | 0.21515 | 0.073242 | 0.41199 | -0.14648 | 19.6564 | 19.5786 | 122.4197 | -0.18768 | -0.20142 | 19.6564 | 19.5786 | -0.18768 | -0.14648 | 122.4197 | -103.0746 | -122.6395
2204.3438 | 122.6578 | -17.1432 | 105.3452 | 0.12558 | 0.016447 | -0.0032834 | 0.052735 | 0.054984 | 0.06259 | 0.18995 | 0.013733 | 0.091553 | -0.19226 | -17.0792 | -17.276 | -17.3035 | -16.9464 | -16.6992 | 105.3131 | -17.3218 | 16.951 | -105.2536 | 17.157 | 0.064087 | -122.6212 | -0.17853 | -0.032044 | 0.20599 | 0.19684 | 0.44403 | -0.13275 | 17.2348 | 17.157 | 122.4564 | -0.16022 | -0.17853 | 17.2348 | 17.157 | -0.16022 | -0.13275 | 122.4564 | -105.5374 | -122.6669
2205.3594 | 122.6944 | -16.3696 | 106.1188 | -0.16434 | 0.013029 | -0.0058468 | 0.056794 | 0.054771 | 0.062376 | 0.19443 | 0.068665 | 0.09613 | -0.17395 | -16.1911 | -16.4291 | -16.4795 | -16.0904 | -15.77 | 106.0913 | -16.5619 | 16.1957 | -106.0226 | 16.4383 | 0.17853 | -122.5479 | -0.19226 | -0.027465 | 0.24261 | 0.27924 | 0.59967 | -0.059509 | 16.4658 | 16.4383 | 122.4609 | -0.10986 | -0.19226 | 16.4658 | 16.4383 | -0.10986 | -0.059509 | 122.4609 | -106.2927 | -122.6807
2206.3594 | 117.9794 | -44.5084 | 73.2788 | 0.1561 | 0.014952 | -0.00093361 | 6.9523 | 0.0075602 | 0.0038431 | 7.0278 | 0.045776 | 0.091553 | -0.17853 | 30.1163 | 38.063 | 38.3789 | 54.9774 | 7.3746 | 63.5422 | -34.5703 | 44.3298 | -73.1873 | 44.5541 | 74.6246 | -35.2158 | 9.938 | -9.7366 | 0.2243 | 99.4858 | 51.8829 | 82.5714 | 44.5999 | 44.5541 | 108.0505 | 82.8873 | 9.938 | 44.5999 | 44.5541 | 82.8873 | 82.5714 | 108.0505 | -73.4573 | -107.8491
2207.3594 | 121.9757 | -17.6147 | 104.1687 | 0.14847 | 0.01602 | -0.0047788 | 0.074952 | -0.0026938 | -0.0023519 | 0.087622 | 0.036621 | 0.10986 | -0.16022 | 94.519 | 101.8662 | 79.0741 | -16.8594 | -16.6992 | 104.0726 | -17.8024 | 17.4545 | -104.0588 | 17.6514 | 112.1338 | -2.3026 | -0.18768 | -0.09613 | 0.19684 | 0.75531 | 0.91553 | 119.4809 | 17.7246 | 17.6514 | 121.6873 | 96.6888 | -0.18768 | 17.7246 | 17.6514 | 96.6888 | 119.4809 | 121.6873 | -104.3289 | -121.9711
2208.3438 | 122.0901 | -16.9647 | 104.9011 | 0.24002 | 0.015592 | -0.0013608 | 0.081788 | -0.0026938 | -0.0055563 | 0.086554 | 0.068665 | 0.1236 | -0.19684 | 95.0684 | 103.3539 | 79.8569 | -16.1133 | -15.9348 | 104.9103 | -17.1982 | 16.7679 | -104.7775 | 17.0334 | 112.0331 | -1.5472 | -0.23346 | 0.009155 | 0.2655 | 0.85144 | 1.03 | 120.3186 | 17.0883 | 17.0334 | 121.875 | 96.8216 | -0.23346 | 17.0883 | 17.0334 | 96.8216 | 120.3186 | 121.875 | -105.098 | -122.0993
2209.3594 | 122.1451 | -21.2173 | 100.7034 | -0.065155 | 0.013456 | -0.0041378 | 0.79401 | -0.0039754 | 0.0029885 | 0.82249 | 0.041199 | 0.11444 | -0.15564 | 88.1744 | 84.7275 | 4.0466 | -18.5715 | -18.1549 | 100.5524 | -21.4005 | 21.0617 | -100.589 | 21.2585 | 109.3918 | -15.976 | -0.18311 | -0.15106 | 0.19684 | 2.6459 | 3.0624 | 105.9448 | 21.3318 | 21.2585 | 121.7697 | 25.264 | -0.18311 | 21.3318 | 21.2585 | 25.264 | 105.9448 | 121.7697 | -100.8591 | -122.1039
2210.3438 | 122.2229 | -14.653 | 107.3456 | 0.24002 | 0.014524 | -0.0015744 | 0.24799 | -0.003121 | -0.0025657 | 0.24869 | 0.082397 | 0.086975 | -0.17395 | 94.4092 | 102.9785 | 10.9863 | -12.5885 | -12.0895 | 107.2495 | -14.8682 | 14.4791 | -107.2586 | 14.7354 | 109.0622 | -4.3671 | -0.21515 | -0.09613 | 0.25635 | 2.0645 | 2.5635 | 117.6315 | 14.74 | 14.7354 | 121.9025 | 25.6393 | -0.21515 | 14.74 | 14.7354 | 25.6393 | 117.6315 | 121.9025 | -107.5195 | -122.2137
2211.375 | 122.2275 | -14.7629 | 107.2632 | 0.072174 | 0.014097 | -0.0043514 | 0.14096 | -0.011025 | -0.0040609 | 0.14957 | -0.07782 | 0.10529 | -0.21973 | 106.6772 | 105.2032 | -5.722 | -13.6139 | -14.1403 | 107.2723 | -14.9368 | 14.5432 | -107.1579 | 14.6851 | 121.4401 | -2.0599 | -0.17395 | 0.009155 | 0.14191 | 1.149 | 0.62256 | 119.9661 | 14.8682 | 14.6851 | 122.0352 | 9.0408 | -0.17395 | 14.8682 | 14.6851 | 9.0408 | 119.9661 | 122.0352 | -107.4829 | -122.2
2212.3438 | 122.2137 | -13.5269 | 108.5358 | -0.41611 | 0.015165 | -0.001788 | 0.097809 | -0.011025 | -0.0059835 | 0.098517 | -0.064087 | 0.082397 | -0.21515 | 108.2886 | 108.1787 | -3.5248 | -12.1902 | -12.7625 | 108.5495 | -13.71 | 13.3118 | -108.4534 | 13.4628 | 121.8155 | -0.35706 | -0.18311 | 0.013733 | 0.15106 | 1.3367 | 0.76447 | 121.7056 | 13.6093 | 13.4628 | 122.0764 | 10.0021 | -0.18311 | 13.6093 | 13.4628 | 10.0021 | 121.7056 | 122.0764 | -108.7509 | -122.2458
2213.3594 | 122.3007 | -13.7833 | 108.2932 | -0.019379 | 0.013243 | -0.0049924 | 0.073029 | -0.012948 | -0.0066245 | 0.078009 | 0.054932 | 0.14191 | -0.13733 | 108.078 | 107.9727 | -4.6738 | -12.323 | -13.1744 | 108.3023 | -13.9435 | 13.6459 | -108.1512 | 13.8382 | 121.8613 | -0.32044 | -0.16022 | 0.009155 | 0.19226 | 1.4603 | 0.60883 | 121.756 | 13.9252 | 13.8382 | 122.0856 | 9.1095 | -0.16022 | 13.9252 | 13.8382 | 9.1095 | 121.756 | 122.0856 | -108.4305 | -122.2366
2214.3438 | 122.2504 | -17.5095 | 104.599 | 0.079804 | 0.015379 | -0.0058468 | 0.12387 | -0.01188 | -0.0055563 | 0.12116 | 0.036621 | 0.10529 | -0.15106 | 104.2603 | 103.8528 | -8.8531 | -16.0217 | -17.3447 | 104.512 | -17.6926 | 17.3584 | -104.4937 | 17.5461 | 121.7697 | -0.74616 | -0.18311 | -0.086975 | 0.18768 | 1.4877 | 0.16479 | 121.3623 | 17.6147 | 17.5461 | 122.0215 | 8.6563 | -0.18311 | 17.6147 | 17.5461 | 8.6563 | 121.3623 | 122.0215 | -104.7501 | -122.2916
2215.3594 | 122.3465 | -14.2044 | 107.9315 | 0.43839 | 0.015165 | -0.0056332 | 0.51459 | -0.010598 | -0.0012839 | 0.51188 | 0.13275 | 0.11902 | -0.15106 | 107.5058 | 103.2166 | -4.3488 | -12.5885 | -13.9389 | 107.7209 | -14.4516 | 14.0533 | -107.8125 | 14.3372 | 121.7102 | -4.715 | -0.24719 | -0.21057 | 0.28381 | 1.6159 | 0.2655 | 117.421 | 14.3234 | 14.3372 | 121.9254 | 9.8557 | -0.24719 | 14.3234 | 14.3372 | 9.8557 | 117.421 | 121.9254 | -108.0826 | -122.3831
2216.3594 | 122.319 | -22.2382 | 99.8886 | -0.049896 | 0.016661 | -0.003497 | 1.4836 | -0.0086752 | -0.0021383 | 1.4794 | 0.091553 | 0.17395 | -0.15564 | 99.408 | 92.2348 | 18.6356 | -18.2785 | -19.6014 | 99.6918 | -22.3663 | 22.0825 | -99.7147 | 22.3297 | 121.6461 | -7.6538 | -0.12817 | -0.19684 | 0.24719 | 3.9597 | 2.6367 | 114.473 | 22.4121 | 22.3297 | 121.9299 | 40.8737 | -0.12817 | 22.4121 | 22.3297 | 40.8737 | 114.473 | 121.9299 | -100.0443 | -122.2549
2217.3594 | 122.2 | -12.8586 | 109.314 | 0.12558 | 0.016447 | -0.0032834 | 0.14395 | -0.0078206 | -0.0040609 | 0.14765 | 0.050354 | 0.17853 | -0.17853 | 108.8837 | 108.5815 | 63.2492 | -9.874 | -12.7945 | 109.3277 | -13.0188 | 12.6801 | -109.1354 | 12.9089 | 121.7422 | -0.73242 | -0.16022 | 0.013733 | 0.22888 | 2.9846 | 0.064087 | 121.4401 | 13.0371 | 12.9089 | 122.1863 | 76.1078 | -0.16022 | 13.0371 | 12.9089 | 76.1078 | 121.4401 | 122.1863 | -109.4925 | -122.3328
2218.3438 | 122.2916 | -21.2448 | 100.8041 | -0.15671 | 0.013243 | -0.0045652 | 1.5883 | -0.0086752 | -0.0040609 | 1.6011 | 0.082397 | 0.11902 | -0.1236 | 100.1724 | 95.4025 | 61.4914 | -19.0292 | -20.8054 | 100.676 | -21.3226 | 21.1212 | -100.6851 | 21.3272 | 121.4172 | -5.4016 | -0.07782 | -0.12817 | 0.20599 | 2.2156 | 0.43945 | 116.6473 | 21.3638 | 21.3272 | 121.9208 | 82.7362 | -0.07782 | 21.3638 | 21.3272 | 82.7362 | 116.6473 | 121.9208 | -100.9277 | -122.1268
2219.3438 | 122.2504 | -15.3122 | 106.8604 | 0.072174 | 0.01367 | -0.0047788 | 0.32083 | -0.010598 | 0.0074747 | 0.3476 | 0.073242 | 0.10986 | -0.17395 | 106.2149 | 83.9859 | 19.0979 | -13.1973 | -15.152 | 106.7688 | -15.4953 | 15.1382 | -106.7505 | 15.3854 | 121.5271 | -22.8745 | -0.18311 | -0.091553 | 0.24719 | 2.1149 | 0.16022 | 99.2981 | 15.4221 | 15.3854 | 122.081 | 34.4101 | -0.18311 | 15.4221 | 15.3854 | 34.4101 | 99.2981 | 122.081 | -107.0343 | -122.3557
2220.3438 | 122.2183 | -17.9581 | 104.2145 | -0.20248 | 0.01602 | -0.0049924 | 0.70642 | -0.0091024 | 0.019651 | 0.71247 | 0.036621 | 0.15106 | -0.1236 | 103.4409 | 55.22 | 58.9371 | -15.4724 | -17.6834 | 104.1092 | -18.0908 | 17.8345 | -104.0634 | 17.9947 | 121.3989 | -48.9944 | -0.13275 | -0.10529 | 0.16022 | 2.4857 | 0.27466 | 73.1781 | 18.1091 | 17.9947 | 122.0673 | 76.8951 | -0.13275 | 18.1091 | 17.9947 | 76.8951 | 73.1781 | 122.0673 | -104.3381 | -122.3053
2221.3594 | 122.2824 | -17.6056 | 104.512 | -0.057526 | 0.016233 | -0.0045652 | 0.88138 | -0.010171 | 0.021147 | 0.92737 | 0.09613 | 0.16479 | -0.009155 | 103.2578 | 53.6728 | 46.7148 | -15.39 | -17.3355 | 104.4113 | -17.7658 | 17.5964 | -104.3472 | 17.7017 | 120.8633 | -50.8392 | -0.16022 | -0.10071 | 0.10528 | 2.2156 | 0.27008 | 71.2784 | 17.7704 | 17.7017 | 122.0169 | 64.3204 | -0.16022 | 17.7704 | 17.7017 | 64.3204 | 71.2784 | 122.0169 | -104.5212 | -122.2778
2222.375 | 122.3511 | -21.5561 | 100.5112 | 0.14084 | 0.016233 | -0.0028562 | 1.1012 | -0.007607 | -0.0010703 | 1.0882 | 0.091553 | 0.091553 | -0.14191 | 99.5361 | 91.8503 | 46.4264 | -18.3884 | -21.286 | 100.4562 | -21.6476 | 21.4142 | -100.4196 | 21.6476 | 121.0922 | -8.6609 | -0.091553 | -0.054931 | 0.23346 | 3.1677 | 0.27008 | 113.4064 | 21.6476 | 21.6476 | 122.0123 | 67.9825 | -0.091553 | 21.6476 | 21.6476 | 67.9825 | 113.4064 | 122.0123 | -100.6531 | -122.1588
2223.3438 | 122.1634 | -23.2178 | 98.8312 | 0.10269 | 0.018797 | -0.0043514 | 2.7188 | -0.007607 | 0.023924 | 2.7771 | 0.10071 | 0.17853 | -0.07782 | 97.1466 | 47.0993 | 42.0136 | -18.8919 | -22.5998 | 98.5977 | -23.1812 | 23.14 | -98.6526 | 23.3185 | 120.3644 | -51.7319 | 0.036621 | -0.23346 | 0.17853 | 4.3259 | 0.61798 | 70.3171 | 23.3963 | 23.3185 | 121.8155 | 65.2313 | 0.036621 | 23.3963 | 23.3185 | 65.2313 | 70.3171 | 121.8155 | -98.909 | -122.0123
2224.3594 | 122.406 | -17.8986 | 104.4891 | 0.17136 | 0.015379 | -0.0013608 | 0.634 | -0.008248 | 0.032255 | 0.7396 | 0.082397 | 0.082397 | -0.13275 | 101.8021 | 36.763 | 29.1321 | -14.0121 | -17.5049 | 103.775 | -18.4479 | 17.7658 | -104.4067 | 17.981 | 119.7006 | -67.7261 | -0.54932 | -0.71411 | 0.21515 | 3.8864 | 0.39368 | 54.6616 | 17.981 | 17.981 | 121.6736 | 47.0306 | -0.54932 | 17.981 | 17.981 | 47.0306 | 54.6616 | 121.6736 | -104.6219 | -122.937
2225.3438 | 122.2092 | -12.3367 | 109.9182 | 0.0035097 | 0.017088 | -0.0026426 | 0.30695 | -0.0088888 | 0.050413 | 0.29548 | 0.027466 | 0.16479 | 0.44403 | 109.0897 | 9.7458 | 24.9069 | -8.0429 | -12.355 | 109.8404 | -12.3779 | 12.7808 | -109.7534 | 12.3642 | 121.4264 | -100.1724 | -0.041199 | -0.07782 | -0.41657 | 4.2938 | -0.018311 | 22.0825 | 12.5015 | 12.3642 | 122.1771 | 37.2437 | -0.041199 | 12.5015 | 12.3642 | 37.2437 | 22.0825 | 122.1771 | -109.4742 | -122.2961
2226.375 | 115.7593 | -63.1073 | 52.446 | 0.36972 | 0.018797 | 0.002698 | 6.9523 | 0.0062784 | -0.00085669 | 7.0278 | 0.11902 | 0.19226 | -0.17395 | 2.3941 | 1.1902 | 2.1973 | 1.8814 | 1.0757 | 31.8649 | -43.1534 | 62.9334 | -52.2537 | 63.2263 | 65.5014 | -51.2558 | 19.9539 | -20.5811 | 0.29297 | 64.9887 | 64.183 | 64.2975 | 63.2996 | 63.2263 | 94.9722 | 65.3046 | 19.9539 | 63.2996 | 63.2263 | 65.3046 | 64.2975 | 94.9722 | -52.6199 | -95.5994
2227.3438 | 121.5866 | -98.8541 | 22.4716 | -0.034637 | 0.017942 | -0.0011472 | 0.037568 | 0.003715 | 0.0038431 | 0.034857 | 0.082397 | 0.17395 | -0.15564 | 5.4153 | 5.4062 | 5.3925 | 5.365 | 5.4016 | 22.4991 | -99.1608 | 98.6984 | -22.2977 | 98.9365 | 104.2694 | -17.0654 | -0.3067 | 0.027465 | 0.23804 | 104.2191 | 104.2557 | 104.2603 | 99.028 | 98.9365 | 121.3531 | 104.2465 | -0.3067 | 99.028 | 98.9365 | 104.2465 | 104.2603 | 121.3531 | -22.6273 | -121.6324
2228.3438 | 121.6415 | -63.6566 | 57.8476 | -0.439 | 0.01901 | -0.0045652 | 0.040131 | 0.024436 | 0.025419 | 0.087622 | 0.1236 | 0.20142 | -0.09613 | 2.8885 | 2.8381 | 2.8107 | 2.8244 | 2.8107 | 57.8339 | -63.8763 | 63.5605 | -57.6462 | 63.7802 | 66.5451 | -55.0095 | -0.21973 | -0.013733 | 0.21973 | 66.481 | 66.4673 | 66.4948 | 63.858 | 63.7802 | 121.4905 | 66.4673 | -0.21973 | 63.858 | 63.7802 | 66.4673 | 66.4948 | 121.4905 | -57.9437 | -121.7239
2229.3438 | 121.6553 | -54.2953 | 67.2729 | -0.011749 | 0.016447 | -0.0060604 | 0.041199 | 0.025932 | 0.027983 | 0.096594 | 0.018311 | 0.15106 | -0.17395 | 8.7753 | 8.6609 | 8.7204 | 8.812 | 8.5556 | 67.2867 | -54.4968 | 54.1214 | -67.1219 | 54.3137 | 63.0707 | -58.6121 | -0.20142 | 0.013733 | 0.19226 | 63.1073 | 62.851 | 62.9562 | 54.4464 | 54.3137 | 121.582 | 63.0157 | -0.20142 | 54.4464 | 54.3137 | 63.0157 | 62.9562 | 121.582 | -67.4469 | -121.7697
2230.3438 | 121.7697 | -98.9685 | 22.5449 | -0.17197 | 0.017301 | -0.0047788 | 0.036072 | 0.003715 | 0.0051249 | 0.039557 | 0.022888 | 0.17395 | -0.17395 | 4.0604 | 4.0146 | 4.0512 | 4.0741 | 4.0466 | 22.5952 | -99.2844 | 98.7946 | -22.3709 | 98.9914 | 103.0289 | -18.5303 | -0.31586 | 0.050354 | 0.19684 | 103.0426 | 103.0151 | 102.9831 | 99.1425 | 98.9914 | 121.5637 | 103.0197 | -0.31586 | 99.1425 | 98.9914 | 103.0197 | 102.9831 | 121.5637 | -22.7188 | -121.8292
2231.3906 | 121.8613 | -97.2656 | 24.3118 | -0.16434 | 0.014952 | -0.0054196 | 0.030091 | 0.003074 | 0.0055521 | 0.044043 | 0.073242 | 0.1236 | -0.12817 | 3.8177 | 3.7857 | 3.8406 | 3.7308 | 3.8315 | 24.3439 | -97.4991 | 97.1375 | -24.1882 | 97.3389 | 101.0834 | -20.5261 | -0.23346 | 0.032043 | 0.20142 | 100.9964 | 101.0971 | 101.0513 | 97.3892 | 97.3389 | 121.6095 | 101.1063 | -0.23346 | 97.3892 | 97.3389 | 101.1063 | 101.0513 | 121.6095 | -24.44 | -121.8109
2232.3438 | 121.8109 | -96.6064 | 25.0809 | 0.041657 | 0.017301 | 0.00056179 | 0.039277 | 0.0060648 | 0.0064065 | 0.044043 | 0.050354 | 0.15106 | -0.16937 | 3.5706 | 3.4607 | 3.5843 | 3.5843 | 3.5065 | 25.1129 | -96.8536 | 96.4371 | -24.9298 | 96.6568 | 100.177 | -21.6202 | -0.24719 | 0.032043 | 0.21973 | 100.1907 | 100.1129 | 100.0671 | 96.7575 | 96.6568 | 121.7194 | 100.1907 | -0.24719 | 96.7575 | 96.6568 | 100.1907 | 100.0671 | 121.7194 | -25.2502 | -121.9345
2233.3594 | 121.8796 | -82.4066 | 39.0747 | 0.14847 | 0.015379 | -0.0041378 | 0.035004 | 0.012687 | 0.015379 | 0.069677 | 0.059509 | 0.11444 | -0.16937 | 2.417 | 1.8539 | 2.3621 | 2.2293 | 2.2385 | 38.887 | -82.8094 | 82.2372 | -38.9603 | 82.4661 | 84.8236 | -37.2208 | -0.40283 | -0.18768 | 0.22888 | 84.6359 | 84.6451 | 84.2606 | 82.5211 | 82.4661 | 121.2936 | 84.7687 | -0.40283 | 82.5211 | 82.4661 | 84.7687 | 84.2606 | 121.2936 | -39.2441 | -121.8842
2234.3438 | 121.8704 | -14.0396 | 107.6111 | 0.11032 | 0.016661 | -0.0030698 | 0.27191 | 0.051567 | 0.058531 | 0.35593 | 0.032043 | 0.14191 | -0.17395 | -2.7191 | -7.9193 | -3.2455 | -1.9913 | -3.5934 | 107.8629 | -14.0396 | 13.8657 | -107.4692 | 14.0717 | 11.3205 | -115.5304 | 0 | 0.25177 | 0.20599 | 12.0483 | 10.4462 | 6.1203 | 14.1815 | 14.0717 | 121.9025 | 10.7941 | 0 | 14.1815 | 14.0717 | 10.7941 | 6.1203 | 121.9025 | -107.785 | -121.6507
2235.3438 | 121.9025 | -8.5098 | 113.3377 | -0.21774 | 0.016233 | -0.0060604 | 0.052308 | 0.053275 | 0.058744 | 0.18311 | 0.050354 | 0.12817 | -0.16022 | -3.7399 | -5.8868 | -3.8406 | -3.8086 | -3.9505 | 113.3423 | -8.67 | 8.3496 | -113.2095 | 8.5602 | 4.7699 | -119.2245 | -0.16022 | 0.004577 | 0.21057 | 4.7012 | 4.5593 | 2.623 | 8.638 | 8.5602 | 121.8521 | 4.6692 | -0.16022 | 8.638 | 8.5602 | 4.6692 | 2.623 | 121.8521 | -113.4979 | -122.0078
2236.3438 | 121.7743 | -14.6942 | 107.2678 | 0.12558 | 0.017942 | -0.0049924 | 0.45969 | 0.053916 | 0.06024 | 0.56315 | 0.045776 | 0.12817 | -0.15564 | -5.0125 | -9.7595 | -5.397 | -4.3488 | -2.0737 | 107.0618 | -14.8407 | 14.5386 | -107.1396 | 14.74 | 9.6817 | -117.0273 | -0.14648 | -0.20599 | 0.20142 | 10.3455 | 12.6205 | 4.9347 | 14.8224 | 14.74 | 121.756 | 9.2972 | -0.14648 | 14.8224 | 14.74 | 9.2972 | 4.9347 | 121.756 | -107.4234 | -122.1085
2237.3594 | 121.8292 | -72.7478 | 48.9395 | -0.24826 | 0.016661 | -0.0013608 | 0.25311 | 0.018882 | 0.020719 | 0.29313 | 0.022888 | 0.15564 | -0.1831 | 2.0233 | -0.98419 | 1.3824 | 1.8768 | 1.2039 | 49.2737 | -72.6654 | 72.5647 | -48.7839 | 72.7707 | 74.7711 | -49.9237 | 0.082398 | 0.33417 | 0.20599 | 74.6246 | 73.9517 | 71.7636 | 72.9034 | 72.7707 | 122.0215 | 74.1302 | 0.082398 | 72.9034 | 72.7707 | 74.1302 | 71.7636 | 122.0215 | -49.1226 | -121.6049
2238.3438 | 121.6324 | -55.7602 | 65.7944 | -0.20248 | 0.017729 | -0.0045652 | 0.081574 | 0.028068 | 0.032682 | 0.14445 | 0.054932 | 0.13275 | -0.16022 | -0.054932 | -1.0254 | -0.39368 | -0.064087 | -0.073242 | 66.5634 | -55.4123 | 55.6 | -65.6616 | 55.8151 | 55.7053 | -66.8198 | 0.3479 | 0.76904 | 0.21515 | 55.6961 | 55.687 | 54.7348 | 55.8929 | 55.8151 | 122.3236 | 55.3665 | 0.3479 | 55.8929 | 55.8151 | 55.3665 | 54.7348 | 122.3236 | -65.9546 | -121.2067
2239.3594 | 121.9849 | -60.3104 | 61.2762 | -0.12619 | 0.014952 | -0.0084104 | 0.11768 | 0.026359 | 0.028196 | 0.15769 | 0.07782 | 0.11902 | -0.10986 | 0.62256 | -0.54932 | 0.36163 | 0.40741 | 0.42114 | 61.2854 | -60.2509 | 60.2005 | -61.1572 | 60.3882 | 60.9329 | -61.8256 | 0.05951 | 0.009155 | 0.18768 | 60.7178 | 60.7315 | 59.761 | 60.4294 | 60.3882 | 121.5958 | 60.672 | 0.05951 | 60.4294 | 60.3882 | 60.672 | 59.761 | 121.5958 | -61.3861 | -121.5271
2240.3438 | 121.8842 | -55.8517 | 66.0553 | -0.21011 | 0.014524 | 0.00098899 | 0.070466 | 0.026359 | 0.031614 | 0.13099 | 0.041199 | 0.16022 | -0.1831 | 0.054932 | -0.6546 | -0.22888 | 0.004578 | -0.11902 | 65.8997 | -56.0165 | 55.6686 | -65.8951 | 55.8929 | 55.9067 | -66.7099 | -0.16479 | -0.15564 | 0.2243 | 55.8563 | 55.7327 | 55.1971 | 56.012 | 55.8929 | 121.7514 | 55.6229 | -0.16479 | 56.012 | 55.8929 | 55.6229 | 55.1971 | 121.7514 | -66.2384 | -122.0718
2241.3594 | 121.9757 | -63.3133 | 58.873 | -0.11093 | 0.015379 | 0.00056179 | 0.18796 | 0.0223 | 0.023496 | 0.22413 | 0.032043 | 0.15564 | -0.17395 | 1.2039 | -1.1948 | 0.6958 | 1.0345 | 0.27008 | 57.2479 | -63.7482 | 63.1393 | -58.7173 | 63.3453 | 64.5172 | -60.0677 | -0.43488 | -1.6251 | 0.20599 | 64.3478 | 63.5834 | 62.1185 | 63.4689 | 63.3453 | 120.5612 | 64.0091 | -0.43488 | 63.4689 | 63.3453 | 64.0091 | 62.1185 | 120.5612 | -59.0469 | -122.6212
2242.3438 | 121.9162 | -54.6295 | 67.1494 | -0.011749 | 0.017515 | -0.0073422 | 0.089265 | 0.028922 | 0.032896 | 0.1673 | 0.054932 | 0.15564 | -0.1236 | -0.32959 | -1.6983 | -0.9201 | -0.64545 | 0.37079 | 67.6529 | -54.4785 | 54.5059 | -66.9937 | 54.6844 | 54.2999 | -68.8477 | 0.15106 | 0.50354 | 0.17853 | 53.9841 | 55.0003 | 52.9312 | 54.7852 | 54.6844 | 122.2824 | 53.7094 | 0.15106 | 54.7852 | 54.6844 | 53.7094 | 52.9312 | 122.2824 | -67.2729 | -121.6278
2243.3438 | 122.0398 | -50.9766 | 70.7108 | 0.10269 | 0.011961 | -0.0030698 | 0.10486 | 0.028709 | 0.037168 | 0.20276 | 0 | 0.12817 | -0.14648 | -0.93384 | -2.8061 | -1.1993 | -0.95215 | 0.21057 | 70.8115 | -51.1047 | 50.8301 | -70.5826 | 50.9766 | 50.0427 | -73.5168 | -0.12817 | 0.10071 | 0.14648 | 50.0244 | 51.1871 | 48.1705 | 51.1047 | 50.9766 | 121.788 | 49.7772 | -0.12817 | 51.1047 | 50.9766 | 49.7772 | 48.1705 | 121.788 | -70.8572 | -121.8155
2244.3438 | 122.0901 | -40.2008 | 81.665 | -0.20248 | 0.014952 | -0.008624 | 0.085847 | 0.037254 | 0.04315 | 0.18183 | -0.032043 | 0.19684 | -0.17395 | -0.63171 | -2.1927 | -0.87433 | -0.42114 | -0.78735 | 81.4774 | -40.5258 | 40.0269 | -81.4682 | 40.1688 | 39.5691 | -83.8577 | -0.32501 | -0.18768 | 0.14191 | 39.7797 | 39.4135 | 38.0081 | 40.3976 | 40.1688 | 121.6782 | 39.3265 | -0.32501 | 40.3976 | 40.1688 | 39.3265 | 38.0081 | 121.6782 | -81.839 | -122.1909
2245.3594 | 122.0032 | -42.2928 | 79.5685 | -0.17197 | 0.014524 | -0.008624 | 0.079011 | 0.033409 | 0.039518 | 0.1579 | -0.004578 | 0.15564 | -0.20142 | -0.61798 | -1.7715 | -0.84228 | -0.56763 | -0.6134 | 79.5364 | -42.4713 | 42.0914 | -79.4128 | 42.2882 | 41.6748 | -81.34 | -0.17853 | -0.032043 | 0.19684 | 41.7252 | 41.6794 | 40.5212 | 42.4484 | 42.2882 | 121.8292 | 41.4505 | -0.17853 | 42.4484 | 42.2882 | 41.4505 | 40.5212 | 121.8292 | -79.7699 | -122.0398
2246.3438 | 121.9986 | -44.6686 | 77.3071 | -0.011749 | 0.016874 | 0.00098899 | 0.087128 | 0.03704 | 0.0408 | 0.16752 | 0.032043 | 0.16479 | -0.19226 | -0.4715 | -1.6296 | -0.64545 | -0.50812 | -0.53558 | 77.3117 | -44.9112 | 44.4763 | -77.1423 | 44.7006 | 44.1971 | -78.9368 | -0.24262 | 0.004578 | 0.2243 | 44.1605 | 44.133 | 43.0389 | 44.8334 | 44.7006 | 121.9803 | 44.0231 | -0.24262 | 44.8334 | 44.7006 | 44.0231 | 43.0389 | 121.9803 | -77.4994 | -122.2183
2247.3594 | 121.6324 | -57.605 | 64.3204 | -0.21011 | 0.014097 | -0.0062742 | 0.53168 | 0.024223 | 0.032469 | 0.6063 | 0.032043 | 0.11902 | -0.11444 | 1.4374 | -4.9805 | 0.3479 | 1.0071 | 0.27008 | 63.3774 | -57.4951 | 57.4905 | -64.2014 | 57.637 | 59.0424 | -69.3008 | 0.10986 | -0.94299 | 0.14648 | 58.6121 | 57.8751 | 52.6245 | 57.724 | 57.637 | 120.9824 | 57.9529 | 0.10986 | 57.724 | 57.637 | 57.9529 | 52.6245 | 120.9824 | -64.4348 | -121.8155
2248.3438 | 121.9025 | -42.3569 | 79.4769 | -0.31693 | 0.014097 | -0.0037106 | 0.12943 | 0.033195 | 0.039732 | 0.22349 | 0.009155 | 0.15564 | -0.18768 | -0.51727 | -1.8173 | -0.77362 | -0.48065 | -0.48523 | 78.6392 | -43.0573 | 42.1692 | -79.3213 | 42.366 | 41.8396 | -81.2943 | -0.70038 | -0.83771 | 0.19684 | 41.8762 | 41.8716 | 40.5396 | 42.5125 | 42.366 | 120.9961 | 41.5833 | -0.70038 | 42.5125 | 42.366 | 41.5833 | 40.5396 | 120.9961 | -79.6646 | -122.5342
2249.3594 | 122.0444 | -36.8546 | 85.2722 | -0.26352 | 0.015592 | -0.0049924 | 0.15463 | 0.035972 | 0.042723 | 0.19187 | 0.004578 | 0.20142 | -0.15564 | -0.6546 | -1.9547 | -0.83771 | -0.52185 | -0.67291 | 84.4849 | -37.2482 | 36.6989 | -85.0708 | 36.8591 | 36.2 | -87.2269 | -0.39368 | -0.78735 | 0.16022 | 36.3327 | 36.1816 | 34.8999 | 37.056 | 36.8591 | 121.3394 | 36.0168 | -0.39368 | 37.056 | 36.8591 | 36.0168 | 34.8999 | 121.3394 | -85.4279 | -122.5204
2250.3438 | 122.0901 | -64.357 | 57.7972 | -0.19485 | 0.016661 | -0.0043514 | 0.06897 | 0.024009 | 0.024565 | 0.11283 | 0.045776 | 0.14648 | -0.18768 | 0.4715 | -0.20599 | 0.28381 | 0.36163 | 0.28839 | 56.4468 | -65.2359 | 64.1693 | -57.6508 | 64.4028 | 64.8285 | -58.0032 | -0.87891 | -1.3504 | 0.23346 | 64.7186 | 64.6454 | 64.151 | 64.5035 | 64.4028 | 120.8038 | 64.6408 | -0.87891 | 64.5035 | 64.4028 | 64.6408 | 64.151 | 120.8038 | -57.9849 | -123.0331
2251.3594 | 122.1497 | -60.9192 | 60.7132 | 0.072174 | 0.016874 | -0.0045652 | 0.07132 | 0.022514 | 0.026274 | 0.13334 | 0.009155 | 0.07782 | -0.19226 | 0.25177 | -0.40283 | 0.22888 | 0.10071 | 0.19684 | 60.9924 | -60.9558 | 60.7269 | -60.6354 | 60.9283 | 61.171 | -61.116 | -0.036622 | 0.27924 | 0.20142 | 61.0199 | 61.116 | 60.5164 | 60.997 | 60.9283 | 121.9116 | 61.1481 | -0.036622 | 60.997 | 60.9283 | 61.1481 | 60.5164 | 121.9116 | -60.9055 | -121.669
2252.3438 | 122.0856 | -59.4864 | 61.7249 | 0.20187 | 0.015592 | -0.006915 | 0.21701 | 0.026145 | 0.030546 | 0.29761 | 0.086975 | 0.10071 | -0.16022 | 0.50812 | -2.1561 | 0.1831 | 0.10986 | 0.27008 | 63.7573 | -58.7723 | 59.3262 | -61.6241 | 59.5734 | 59.9945 | -63.8809 | 0.71411 | 2.0325 | 0.24719 | 59.5963 | 59.7565 | 57.3303 | 59.5871 | 59.5734 | 123.2437 | 59.6695 | 0.71411 | 59.5871 | 59.5734 | 59.6695 | 57.3303 | 123.2437 | -61.8851 | -120.4971
2253.3438 | 121.9162 | -34.0851 | 87.6663 | -0.16434 | 0.018156 | -0.0028562 | 0.085206 | 0.039176 | 0.046354 | 0.17435 | 0.082397 | 0.20142 | -0.12817 | -0.59509 | -1.7578 | -0.78735 | -0.66834 | -0.55389 | 89.0396 | -33.3801 | 33.9569 | -87.4649 | 34.1675 | 33.49 | -89.4241 | 0.70496 | 1.3733 | 0.21057 | 33.4167 | 33.5312 | 32.3273 | 34.2865 | 34.1675 | 123.1247 | 33.2977 | 0.70496 | 34.2865 | 34.1675 | 33.2977 | 32.3273 | 123.1247 | -87.7945 | -121.0464
2254.3438 | 122.0261 | -30.1071 | 91.983 | -0.27878 | 0.014524 | -0.0045652 | 0.073456 | 0.041526 | 0.046995 | 0.17798 | -0.022888 | 0.15564 | -0.19684 | -0.51727 | -1.8402 | -0.8606 | -0.5722 | -0.63629 | 91.7084 | -30.4092 | 29.9103 | -91.8274 | 30.0842 | 29.5898 | -93.8232 | -0.30212 | -0.27466 | 0.17395 | 29.5349 | 29.4708 | 28.2669 | 30.2628 | 30.0842 | 121.8155 | 29.2465 | -0.30212 | 30.2628 | 30.0842 | 29.2465 | 28.2669 | 121.8155 | -92.1799 | -122.3923
2255.3438 | 122.1268 | -34.0256 | 88.0463 | -0.24063 | 0.01602 | -0.00050621 | 0.090974 | 0.037681 | 0.044218 | 0.16773 | -0.022888 | 0.15106 | -0.19684 | -0.49896 | -1.6663 | -0.71411 | -0.46692 | -0.51727 | 87.7533 | -34.3735 | 33.8287 | -87.8952 | 34.0027 | 33.5266 | -89.7125 | -0.3479 | -0.29297 | 0.17395 | 33.5587 | 33.5083 | 32.3593 | 34.1766 | 34.0027 | 121.7789 | 33.3115 | -0.3479 | 34.1766 | 34.0027 | 33.3115 | 32.3593 | 121.7789 | -88.2431 | -122.4197
2256.3438 | 121.994 | -53.4622 | 68.3578 | 0.087433 | 0.015806 | -0.0028562 | 0.22556 | 0.030845 | 0.035032 | 0.29975 | 0.004578 | 0.13733 | -0.14191 | 0.27924 | -2.2476 | 0.17395 | 0.21515 | -0.064087 | 68.6646 | -52.034 | 53.3203 | -68.2205 | 53.4668 | 53.7415 | -70.6055 | 1.4282 | 0.3067 | 0.14649 | 53.6774 | 53.3981 | 51.2146 | 53.5995 | 53.4668 | 122.1268 | 53.6362 | 1.4282 | 53.5995 | 53.4668 | 53.6362 | 51.2146 | 122.1268 | -68.4998 | -120.3918
2257.3594 | 122.1725 | -35.9665 | 86.1191 | -0.1033 | 0.018156 | -0.0022152 | 0.13947 | 0.039604 | 0.044859 | 0.24485 | 0.068665 | 0.15106 | -0.17853 | -0.009155 | -1.8723 | -0.3067 | -0.30212 | -0.26093 | 85.8856 | -36.2366 | 35.788 | -85.968 | 36.0352 | 35.9573 | -87.9913 | -0.27008 | -0.23346 | 0.24719 | 35.6644 | 35.7056 | 34.0942 | 36.1176 | 36.0352 | 121.8521 | 35.6598 | -0.27008 | 36.1176 | 36.0352 | 35.6598 | 34.0942 | 121.8521 | -86.2976 | -122.3557
2258.3438 | 122.1771 | -18.1 | 103.9764 | -0.17197 | 0.012388 | -0.0030698 | 0.069825 | 0.046653 | 0.052763 | 0.19742 | 0.054932 | 0.09613 | -0.15564 | -0.53558 | -1.799 | -0.97961 | -0.89264 | -0.57678 | 103.7292 | -18.3609 | 17.9443 | -103.8803 | 18.1549 | 17.5644 | -105.7755 | -0.26092 | -0.24719 | 0.21057 | 17.2073 | 17.5232 | 16.301 | 18.1961 | 18.1549 | 121.8292 | 17.1204 | -0.26092 | 18.1961 | 18.1549 | 17.1204 | 16.301 | 121.8292 | -104.1321 | -122.3373
2259.3438 | 122.1863 | -25.5524 | 96.2036 | 0.16373 | 0.016233 | -0.0049924 | 0.22385 | 0.043662 | 0.048277 | 0.36619 | 0.050354 | 0.10071 | -0.14648 | -0.29755 | -2.948 | -0.35248 | -0.42114 | -0.41199 | 96.6568 | -25.4562 | 25.4059 | -96.1029 | 25.6027 | 25.2548 | -99.1516 | 0.09613 | 0.45319 | 0.19684 | 25.1312 | 25.1404 | 22.6044 | 25.6531 | 25.6027 | 122.2092 | 25.1999 | 0.09613 | 25.6531 | 25.6027 | 25.1999 | 22.6044 | 122.2092 | -96.3501 | -121.6599
2260.3438 | 122.0993 | -57.0465 | 65.4694 | -0.14145 | 0.016233 | -0.0045652 | 0.37231 | 0.021659 | 0.030973 | 0.5123 | 0.036621 | 0.1236 | -0.13733 | 1.4008 | -4.4266 | 0.2655 | 1.0986 | 0.53558 | 63.9313 | -57.9895 | 56.9092 | -65.3458 | 57.0831 | 58.4473 | -69.8959 | -0.94299 | -1.5381 | 0.17395 | 58.1451 | 57.5821 | 52.6199 | 57.1701 | 57.0831 | 120.9778 | 57.312 | -0.94299 | 57.1701 | 57.0831 | 57.312 | 52.6199 | 120.9778 | -65.6067 | -123.4589
2261.3438 | 122.319 | -42.572 | 79.1245 | 0.095062 | 0.015379 | -0.0049924 | 0.15933 | 0.033622 | 0.039305 | 0.23032 | 0.07782 | 0.10071 | -0.14648 | 0.17853 | -1.5427 | -0.13733 | -0.064087 | 0.022888 | 79.2664 | -42.8558 | 42.4255 | -79.0237 | 42.6498 | 42.7505 | -80.6671 | -0.28381 | 0.14191 | 0.2243 | 42.5079 | 42.5949 | 41.0294 | 42.6727 | 42.6498 | 121.8384 | 42.4347 | -0.28381 | 42.6727 | 42.6498 | 42.4347 | 41.0294 | 121.8384 | -79.2709 | -121.9803
2262.3438 | 121.8979 | -35.5225 | 85.9772 | -0.19485 | 0.012815 | -0.0077694 | 0.091187 | 0.035118 | 0.045713 | 0.20789 | 0.082397 | 0.1236 | -0.14648 | -0.21515 | -1.767 | -0.41199 | -0.36621 | -0.14648 | 89.3555 | -33.6639 | 35.376 | -85.8536 | 35.6049 | 35.3073 | -87.7441 | 1.8585 | 3.3783 | 0.22888 | 35.1562 | 35.376 | 33.7555 | 35.6461 | 35.6049 | 124.8779 | 35.1105 | 1.8585 | 35.6461 | 35.6049 | 35.1105 | 33.7555 | 124.8779 | -86.1237 | -119.6411
2263.3594 | 122.0947 | -43.1396 | 78.2593 | -0.019379 | 0.010679 | -0.0058468 | 0.33984 | 0.032127 | 0.040373 | 0.43006 | 0.082397 | 0.082397 | -0.1236 | 0.33417 | -4.1245 | 0.10071 | 0.068665 | 0.15564 | 79.3671 | -42.6682 | 43.0161 | -78.1769 | 43.222 | 43.4738 | -82.3837 | 0.4715 | 1.1078 | 0.20599 | 43.2083 | 43.2953 | 39.0152 | 43.222 | 43.222 | 122.5067 | 43.2404 | 0.4715 | 43.222 | 43.222 | 43.2404 | 39.0152 | 122.5067 | -78.3829 | -120.9274
2264.3438 | 122.1313 | -27.1179 | 94.6106 | -0.27878 | 0.01602 | -0.0049924 | 0.16232 | 0.038963 | 0.04785 | 0.25019 | 0.050354 | 0.10986 | -0.17853 | -0.24719 | -2.5085 | -0.50354 | -0.25177 | -0.22888 | 95.3842 | -26.944 | 26.9394 | -94.5007 | 27.1683 | 26.8707 | -97.1191 | 0.17395 | 0.77362 | 0.22888 | 26.8662 | 26.889 | 24.6094 | 27.2278 | 27.1683 | 122.5021 | 26.6144 | 0.17395 | 27.2278 | 27.1683 | 26.6144 | 24.6094 | 122.5021 | -94.7891 | -121.5546
2265.3594 | 122.2504 | -39.7247 | 82.1045 | 0.1561 | 0.012388 | -0.010333 | 0.13626 | 0.034263 | 0.041868 | 0.24805 | 0.018311 | 0.059509 | -0.18768 | -0.004578 | -1.8814 | -0.086975 | -0.15106 | -0.11444 | 83.2901 | -39.3219 | 39.537 | -82.045 | 39.743 | 39.7202 | -83.9859 | 0.40283 | 1.1856 | 0.20599 | 39.5737 | 39.6103 | 37.8433 | 39.7842 | 39.743 | 123.0148 | 39.6378 | 0.40283 | 39.7842 | 39.743 | 39.6378 | 37.8433 | 123.0148 | -82.2922 | -121.4264
2266.3438 | 122.1954 | -20.8191 | 101.4679 | -0.042267 | 0.015592 | -0.0049924 | 0.11725 | 0.046867 | 0.050413 | 0.22242 | 0.073242 | 0.12817 | -0.1831 | -0.33417 | -1.8997 | -0.59052 | -0.37994 | -0.31128 | 100.9781 | -21.2311 | 20.636 | -101.3397 | 20.8923 | 20.4849 | -103.3676 | -0.41199 | -0.48981 | 0.25635 | 20.4391 | 20.5078 | 18.9194 | 20.9473 | 20.8923 | 121.7972 | 20.2286 | -0.41199 | 20.9473 | 20.8923 | 20.2286 | 18.9194 | 121.7972 | -101.651 | -122.699
2267.3438 | 122.1268 | -25.1404 | 96.7209 | -0.21774 | 0.014311 | -0.0077694 | 0.14929 | 0.044303 | 0.049131 | 0.2613 | 0.009155 | 0.13275 | -0.1831 | -0.27466 | -2.1973 | -0.45776 | -0.16937 | -0.18768 | 97.1191 | -25.1816 | 24.9573 | -96.5881 | 25.1495 | 24.8657 | -98.9182 | -0.041199 | 0.39826 | 0.19226 | 24.971 | 24.9527 | 22.9431 | 25.2731 | 25.1495 | 122.2595 | 24.6826 | -0.041199 | 25.2731 | 25.1495 | 24.6826 | 22.9431 | 122.2595 | -96.904 | -121.9025
2268.3438 | 122.0169 | -19.5694 | 102.9007 | -0.29404 | 0.014524 | -0.0077694 | 0.15143 | 0.045799 | 0.051267 | 0.29633 | 0.082397 | 0.10071 | -0.14191 | -0.19684 | -2.3895 | -0.37537 | -0.3891 | 0.086975 | 102.269 | -19.9356 | 19.4275 | -102.8 | 19.6518 | 19.3726 | -105.2902 | -0.36621 | -0.63171 | 0.2243 | 19.1803 | 19.6564 | 17.1799 | 19.6701 | 19.6518 | 121.8384 | 19.194 | -0.36621 | 19.6701 | 19.6518 | 19.194 | 17.1799 | 121.8384 | -103.0426 | -122.8363
2269.3438 | 122.113 | -37.999 | 84.0408 | -0.11856 | 0.01602 | -0.0060604 | 0.16724 | 0.035545 | 0.043363 | 0.25211 | 0.050354 | 0.12817 | -0.17853 | 0.09613 | -1.5656 | -0.15564 | 0.09613 | -0.068665 | 83.7799 | -38.3652 | 37.8204 | -83.9127 | 38.0493 | 38.0951 | -85.6064 | -0.36621 | -0.26093 | 0.22888 | 38.0951 | 37.9303 | 36.4334 | 38.1271 | 38.0493 | 121.7789 | 37.8433 | -0.36621 | 38.1271 | 38.0493 | 37.8433 | 36.4334 | 121.7789 | -84.2194 | -122.406
2270.3438 | 122.1588 | -18.9606 | 103.2349 | -0.25589 | 0.013883 | -0.0060604 | 0.29691 | 0.047721 | 0.053617 | 0.40293 | 0.064087 | 0.11444 | -0.15106 | -0.11902 | -4.39 | -0.58136 | 0.36621 | 0.64545 | 103.2944 | -18.9377 | 18.8095 | -103.1204 | 19.0247 | 18.8416 | -107.6248 | 0.022888 | 0.05951 | 0.21515 | 19.3268 | 19.606 | 14.5706 | 19.075 | 19.0247 | 122.2549 | 18.3792 | 0.022888 | 19.075 | 19.0247 | 18.3792 | 14.5706 | 122.2549 | -103.3859 | -122.1725
2271.3438 | 121.3074 | -17.2714 | 104.8325 | 0.0035097 | 0.019438 | -0.0060604 | 0.3172 | 0.050071 | 0.054258 | 0.42408 | 0.07782 | 0.12817 | -0.18768 | -0.32044 | -4.8614 | -0.92468 | 0.42114 | 1.9272 | 104.8965 | -17.308 | 17.0837 | -104.7043 | 17.3492 | 16.951 | -109.6939 | -0.036621 | 0.064087 | 0.2655 | 17.6926 | 19.1986 | 12.41 | 17.3996 | 17.3492 | 122.168 | 16.3467 | -0.036621 | 17.3996 | 17.3492 | 16.3467 | 12.41 | 122.168 | -105.0201 | -122.1405
2272.3594 | 122.1954 | -32.5195 | 89.7263 | 0.17136 | 0.014524 | -0.0062742 | 0.61777 | 0.039176 | 0.049559 | 0.72123 | 0.050354 | 0.091553 | -0.13733 | 0.27924 | -7.37 | -0.27008 | -0.10529 | -0.21515 | 89.1541 | -32.8674 | 32.3822 | -89.6347 | 32.5699 | 32.7988 | -97.0963 | -0.3479 | -0.5722 | 0.18768 | 32.4142 | 32.3044 | 25.1495 | 32.6111 | 32.5699 | 121.6736 | 32.2495 | -0.3479 | 32.6111 | 32.5699 | 32.2495 | 25.1495 | 121.6736 | -89.8636 | -122.5937
2273.3438 | 122.0718 | -26.1108 | 95.993 | -0.24063 | 0.016447 | -0.0026426 | 1.4289 | 0.039817 | 0.056608 | 1.5768 | 0.15564 | 0.16937 | -0.14648 | 1.062 | -18.0084 | 0.87891 | 0.76446 | 0.37537 | 95.7825 | -26.2482 | 25.9644 | -95.8237 | 26.2665 | 27.1729 | -114.0015 | -0.13733 | -0.21057 | 0.30212 | 26.8753 | 26.4862 | 8.1024 | 26.2802 | 26.2665 | 121.8933 | 26.9897 | -0.13733 | 26.2802 | 26.2665 | 26.9897 | 8.1024 | 121.8933 | -96.1395 | -122.2412
2274.375 | 122.168 | -12.6114 | 109.4009 | 0.1561 | 0.013456 | -0.005206 | 0.22321 | 0.049858 | 0.055754 | 0.36149 | 0.027466 | 0.086975 | -0.13733 | -0.21973 | -2.7649 | -0.26093 | -0.42114 | -0.32044 | 109.4559 | -12.7487 | 12.4741 | -109.314 | 12.6389 | 12.3917 | -112.1658 | -0.13733 | 0.054932 | 0.16479 | 12.1902 | 12.291 | 9.8465 | 12.6984 | 12.6389 | 122.0673 | 12.3505 | -0.13733 | 12.6984 | 12.6389 | 12.3505 | 9.8465 | 122.0673 | -109.5383 | -122.1497
2275.3438 | 122.0581 | -5.8868 | 116.3361 | -0.233 | 0.016661 | -0.0056332 | 0.095673 | 0.052635 | 0.059385 | 0.24186 | 0.018311 | 0.14191 | -0.16937 | -0.22888 | -4.5227 | -0.37994 | -0.16937 | -0.16479 | 116.2949 | -6.0059 | 5.7175 | -116.1942 | 5.9052 | 5.658 | -120.8588 | -0.11902 | -0.041199 | 0.18768 | 5.7175 | 5.722 | 1.3641 | 6.0287 | 5.9052 | 122.1817 | 5.5069 | -0.11902 | 6.0287 | 5.9052 | 5.5069 | 1.3641 | 122.1817 | -116.5054 | -122.3419
2276.3594 | 121.5775 | -4.0146 | 118.1808 | -0.72891 | 0.016447 | -0.0039242 | 0.14011 | 0.056053 | 0.060026 | 0.26151 | 0.07782 | 0.19684 | -0.10529 | -0.24719 | -2.8381 | -0.4715 | -0.3067 | -0.10529 | 118.2541 | -4.0558 | 3.9093 | -117.984 | 4.0924 | 3.7674 | -121.019 | -0.041199 | 0.073242 | 0.18311 | 3.7079 | 3.9093 | 1.1765 | 4.2114 | 4.0924 | 122.2687 | 3.5431 | -0.041199 | 4.2114 | 4.0924 | 3.5431 | 1.1765 | 122.2687 | -118.2861 | -122.2366
2277.3438 | 121.4355 | -4.0878 | 118.2404 | -0.24063 | 0.016447 | -0.0028562 | 0.28003 | 0.05648 | 0.061949 | 0.42258 | -0.004578 | 0.17395 | -0.1831 | -0.1236 | -3.2318 | -0.36621 | -0.018311 | 0.082397 | 118.1122 | -4.2435 | 3.9047 | -118.0664 | 4.0833 | 3.9642 | -121.4722 | -0.15564 | -0.12817 | 0.17853 | 4.0695 | 4.1702 | 0.85602 | 4.2618 | 4.0833 | 122.2 | 3.7216 | -0.15564 | 4.2618 | 4.0833 | 3.7216 | 0.85602 | 122.2 | -118.4235 | -122.4838
2278.3594 | 122.2733 | -3.3234 | 118.4647 | 0.14084 | 0.014524 | -0.0030698 | 0.089478 | 0.05648 | 0.061521 | 0.24186 | 0.036621 | 0.10529 | -0.14648 | -0.15564 | -2.7054 | -0.29297 | -0.24719 | 0.018311 | 118.8583 | -3.4744 | 3.1769 | -118.3594 | 3.36 | 3.1677 | -121.17 | -0.15106 | 0.39368 | 0.18311 | 3.0762 | 3.3417 | 0.61798 | 3.4287 | 3.36 | 122.1817 | 3.0304 | -0.15106 | 3.4287 | 3.36 | 3.0304 | 0.61798 | 122.1817 | -118.6111 | -121.9391
2279.3438 | 122.3831 | -9.6405 | 112.3627 | -0.15671 | 0.011961 | -0.0054196 | 0.35651 | 0.050926 | 0.059172 | 0.49628 | 0.068665 | 0.11444 | -0.14648 | -1.7303 | -8.4274 | -1.9821 | -1.8814 | -1.712 | 112.4588 | -9.7733 | 9.494 | -112.2482 | 9.7092 | 7.9102 | -120.7901 | -0.13275 | 0.09613 | 0.21515 | 7.7591 | 7.9285 | 1.2131 | 9.7549 | 9.7092 | 122.0993 | 7.6584 | -0.13275 | 9.7549 | 9.7092 | 7.6584 | 1.2131 | 122.0993 | -112.5092 | -122.1359
2280.3594 | 122.3328 | -4.6509 | 117.3294 | 0.14847 | 0.016874 | -0.0067014 | 0.10785 | 0.05413 | 0.061521 | 0.24378 | 0.068665 | 0.09613 | -0.16022 | -0.013733 | -4.0833 | -0.13733 | -0.14191 | -0.004578 | 117.4667 | -4.8203 | 4.4907 | -117.2333 | 4.7195 | 4.6371 | -121.4127 | -0.16937 | 0.13733 | 0.22888 | 4.509 | 4.6463 | 0.56763 | 4.747 | 4.7195 | 122.1176 | 4.5135 | -0.16937 | 4.747 | 4.7195 | 4.5135 | 0.56763 | 122.1176 | -117.4896 | -122.1497
2281.3438 | 118.4875 | -4.5959 | 117.3889 | 0.026398 | 0.018797 | -0.0045652 | 0.12131 | 0.05648 | 0.064085 | 0.24592 | 0.045776 | 0.1236 | -0.17853 | -0.004578 | -3.5202 | -0.18768 | -0.054932 | -0.041199 | 117.897 | -4.3076 | 4.4174 | -117.2653 | 4.6417 | 4.5914 | -120.9091 | 0.28839 | 0.50812 | 0.2243 | 4.541 | 4.5547 | 1.0757 | 4.7195 | 4.6417 | 122.493 | 4.4083 | 0.28839 | 4.7195 | 4.6417 | 4.4083 | 1.0757 | 122.493 | -117.5674 | -121.6965
2282.3594 | 122.319 | -6.6147 | 115.1459 | -0.20248 | 0.015165 | -0.0043514 | 0.11896 | 0.052635 | 0.060453 | 0.31598 | 0.054932 | 0.12817 | -0.16022 | 0.25635 | -5.9143 | 0 | 0.16937 | 0.15106 | 115.9561 | -6.4774 | 6.4545 | -115.0177 | 6.6696 | 6.871 | -121.0602 | 0.13733 | 0.81024 | 0.21515 | 6.7841 | 6.7657 | 0.70038 | 6.7429 | 6.6696 | 122.5708 | 6.6147 | 0.13733 | 6.7429 | 6.6696 | 6.6147 | 0.70038 | 122.5708 | -115.3061 | -121.6232
2283.3438 | 122.2549 | -30.7938 | 91.3193 | -0.065155 | 0.017088 | -0.0043514 | 0.76346 | 0.040885 | 0.060667 | 0.83829 | 0.009155 | 0.14191 | -0.17395 | -1.8448 | -29.4708 | -2.7054 | -1.973 | -2.6367 | 91.0263 | -31.1188 | 30.6198 | -91.1774 | 30.8029 | 28.949 | -120.7901 | -0.32501 | -0.29297 | 0.1831 | 28.8208 | 28.157 | 1.3229 | 30.9357 | 30.8029 | 121.8201 | 28.0884 | -0.32501 | 30.9357 | 30.8029 | 28.0884 | 1.3229 | 121.8201 | -91.4932 | -122.438
2284.3594 | 115.2512 | -65.7166 | 49.4019 | 0.12558 | 0.013883 | -0.0026426 | 6.9523 | -0.00034384 | 0.0034159 | 7.0278 | 0.036621 | 0.09613 | -0.12817 | 1.4786 | -6.926 | -0.27008 | 1.7487 | 1.0757 | 27.3651 | -44.4901 | 65.5884 | -49.3057 | 65.7532 | 67.1951 | -56.3278 | 21.2265 | -22.0367 | 0.1648 | 67.4652 | 66.7923 | 58.7906 | 65.8127 | 65.7532 | 93.0817 | 65.4465 | 21.2265 | 65.8127 | 65.7532 | 65.4465 | 58.7906 | 93.0817 | -49.53 | -93.8919
2285.3438 | 121.3852 | -45.3094 | 76.0986 | -0.22537 | 0.013456 | -0.0058468 | 0.11234 | 0.032554 | 0.036527 | 0.19465 | 0.032043 | 0.13275 | -0.17395 | 0.050354 | 0.091553 | 0.086975 | -0.009155 | -2.2797 | 75.7416 | -45.7489 | 45.1355 | -75.9659 | 45.3415 | 45.3598 | -76.0071 | -0.43945 | -0.35706 | 0.20599 | 45.3003 | 43.0298 | 45.401 | 45.4422 | 45.3415 | 121.051 | 45.3964 | -0.43945 | 45.4422 | 45.3415 | 45.3964 | 45.401 | 121.051 | -76.2726 | -121.8475
2286.3594 | 121.5317 | -23.1583 | 97.5311 | -0.11856 | 0.015806 | -0.0045652 | 0.1322 | 0.041526 | 0.051267 | 0.24271 | 0.018311 | 0.13275 | -0.19226 | 0.15564 | -0.36163 | 0.13275 | 0.13733 | -1.5198 | 98.7671 | -23.053 | 22.966 | -97.3984 | 23.1766 | 23.3139 | -97.8928 | 0.10528 | 1.236 | 0.21057 | 23.2956 | 21.6385 | 22.7966 | 23.291 | 23.1766 | 121.9254 | 23.291 | 0.10528 | 23.291 | 23.1766 | 23.291 | 22.7966 | 121.9254 | -97.7234 | -120.5841
2287.3438 | 121.8658 | -40.5487 | 80.6488 | -0.088043 | 0.013883 | -0.0028562 | 0.36035 | 0.036186 | 0.039091 | 0.45292 | 0.041199 | 0.11902 | -0.15106 | 0.17853 | -0.24719 | 0.52643 | -0.29755 | -4.9896 | 81.8481 | -40.2145 | 40.3976 | -80.5298 | 40.5899 | 40.7272 | -80.896 | 0.33417 | 1.1993 | 0.19226 | 40.2512 | 35.5591 | 40.3015 | 40.6677 | 40.5899 | 122.3969 | 41.0751 | 0.33417 | 40.6677 | 40.5899 | 41.0751 | 40.3015 | 122.3969 | -80.7999 | -120.8633
2288.3594 | 120.8267 | -0.52643 | 120.8725 | -0.24826 | 0.017088 | -0.0058468 | 0.034363 | -0.013802 | -0.0044883 | 0.042547 | -0.009155 | 0.14648 | -0.19226 | -0.16937 | -0.21515 | -0.10986 | -0.022888 | -0.068665 | 0.036621 | -0.75073 | 0.33417 | -120.726 | 0.51727 | 0.35706 | -121.0876 | -0.2243 | -120.8359 | 0.18311 | 0.50354 | 0.45776 | 0.31128 | 0.67291 | 0.51727 | 0.56305 | 0.41657 | -0.2243 | 0.67291 | 0.51727 | 0.41657 | 0.31128 | 0.56305 | -121.0648 | -121.6232
2289.3438 | 121.8018 | -0.54932 | 121.1288 | 2.1092 | 0.013243 | -0.007983 | 0.035218 | -0.009316 | -0.0051291 | 0.041266 | 0.086975 | 0.059509 | -0.17853 | 0.004578 | -0.036621 | 0.004578 | -0.1831 | 0.073242 | -0.036621 | -0.6958 | 0.37079 | -121.0693 | 0.63629 | 0.55389 | -121.1655 | -0.14648 | -121.1655 | 0.2655 | 0.36621 | 0.62256 | 0.5127 | 0.60883 | 0.63629 | 0.5127 | 0.55389 | -0.14648 | 0.60883 | 0.63629 | 0.55389 | 0.5127 | 0.5127 | -121.3074 | -121.8246
2290.3594 | 121.8338 | -0.56763 | 121.2112 | 0.34683 | 0.013883 | -0.006915 | 0.036072 | -0.01252 | -0.0053427 | 0.041906 | -0.036621 | 0.041199 | -0.21057 | -0.10529 | -0.1236 | -0.041199 | -0.16022 | 0.009155 | -0.050354 | -0.72327 | 0.35706 | -121.17 | 0.53101 | 0.46234 | -121.3348 | -0.15564 | -121.2616 | 0.17395 | 0.40741 | 0.57678 | 0.44403 | 0.60883 | 0.53101 | 0.51727 | 0.52643 | -0.15564 | 0.60883 | 0.53101 | 0.52643 | 0.44403 | 0.51727 | -121.4218 | -121.9345
2291.3438 | 121.8567 | -0.56305 | 121.2204 | -0.20248 | 0.012815 | -0.011828 | 0.037354 | -0.013589 | -0.0053427 | 0.040625 | 0.07782 | 0.10529 | -0.15564 | -0.018311 | -0.059509 | -0.018311 | -0.14191 | 0.073242 | -0.054932 | -0.68665 | 0.40741 | -121.1151 | 0.64087 | 0.54474 | -121.2799 | -0.1236 | -121.2753 | 0.23346 | 0.42114 | 0.63629 | 0.50354 | 0.66834 | 0.64087 | 0.50812 | 0.54474 | -0.1236 | 0.66834 | 0.64087 | 0.54474 | 0.50354 | 0.50812 | -121.376 | -121.907
2292.3438 | 121.9299 | -0.58594 | 121.2021 | 0.2858 | 0.01602 | -0.0026426 | 0.042054 | -0.01252 | -0.0027793 | 0.042975 | 0.10071 | 0.09613 | -0.13733 | -0.022888 | -0.086975 | 0.018311 | -0.25177 | 0.041199 | -0.032043 | -0.71869 | 0.44861 | -121.106 | 0.68665 | 0.56305 | -121.2891 | -0.13275 | -121.2341 | 0.23804 | 0.33417 | 0.62714 | 0.49896 | 0.68207 | 0.68665 | 0.55389 | 0.60425 | -0.13275 | 0.68207 | 0.68665 | 0.60425 | 0.49896 | 0.55389 | -121.3394 | -121.9208
2293.3438 | 121.8704 | -0.60883 | 121.1288 | -0.21011 | 0.014311 | -0.0088376 | 0.039704 | -0.012307 | -0.0059835 | 0.041479 | 0.041199 | 0.10986 | -0.17395 | -0.054932 | -0.11444 | -0.059509 | -0.07782 | 0.018311 | -0.032043 | -0.76446 | 0.43488 | -121.019 | 0.65002 | 0.55389 | -121.2433 | -0.15564 | -121.1609 | 0.21515 | 0.53101 | 0.62714 | 0.49438 | 0.71869 | 0.65002 | 0.57678 | 0.54932 | -0.15564 | 0.71869 | 0.65002 | 0.54932 | 0.49438 | 0.57678 | -121.3028 | -121.8933
2294.3438 | 121.9345 | -0.64087 | 121.2158 | 0.064545 | 0.014097 | -0.0058468 | 0.037781 | -0.012948 | -0.0053427 | 0.044897 | -0.054932 | 0.082397 | -0.19684 | -0.07782 | -0.11902 | -0.059509 | -0.15106 | -0.004578 | -0.068665 | -0.79193 | 0.44403 | -121.1334 | 0.58594 | 0.56305 | -121.3348 | -0.15106 | -121.2845 | 0.14191 | 0.48981 | 0.63629 | 0.52185 | 0.72327 | 0.58594 | 0.5722 | 0.58136 | -0.15106 | 0.72327 | 0.58594 | 0.58136 | 0.52185 | 0.5722 | -121.4127 | -122.0078
2295.3438 | 121.9711 | -0.58136 | 121.2296 | -0.027008 | 0.01367 | -0.008624 | 0.037568 | -0.015725 | -0.0036337 | 0.043829 | 0.027466 | 0.11902 | -0.15106 | -0.036621 | -0.073242 | -0.004578 | -0.16479 | 0.050354 | -0.022888 | -0.75531 | 0.4303 | -121.1105 | 0.60883 | 0.54474 | -121.3028 | -0.17395 | -121.2524 | 0.17853 | 0.41656 | 0.63171 | 0.50812 | 0.70038 | 0.60883 | 0.55847 | 0.57678 | -0.17395 | 0.70038 | 0.60883 | 0.57678 | 0.50812 | 0.55847 | -121.3806 | -121.9849
2296.3438 | 121.9986 | -0.61798 | 121.2296 | -0.11856 | 0.014311 | -0.0075558 | 0.036713 | -0.015725 | -0.0038473 | 0.039557 | 0.073242 | 0.10529 | -0.15564 | -0.032043 | -0.07782 | -0.027466 | -0.17853 | 0.041199 | -0.073242 | -0.76446 | 0.46234 | -121.1243 | 0.69122 | 0.58594 | -121.3074 | -0.14648 | -121.3028 | 0.22888 | 0.43945 | 0.65918 | 0.54016 | 0.72327 | 0.69122 | 0.54474 | 0.59052 | -0.14648 | 0.72327 | 0.69122 | 0.59052 | 0.54016 | 0.54474 | -121.3852 | -121.994
2297.3594 | 122.0032 | -0.61798 | 121.2479 | -3.5289 | 0.010679 | -0.0049924 | 0.03885 | -0.015298 | -0.0057699 | 0.04212 | 0.1236 | 0.09613 | -0.15564 | -0.009155 | -0.054932 | -0.004578 | -0.16022 | 0.082397 | -0.050354 | -0.75989 | 0.46234 | -121.1517 | 0.74158 | 0.60883 | -121.3028 | -0.14191 | -121.2982 | 0.27924 | 0.45776 | 0.70038 | 0.56305 | 0.71411 | 0.74158 | 0.56763 | 0.6134 | -0.14191 | 0.71411 | 0.74158 | 0.6134 | 0.56305 | 0.56763 | -121.4035 | -122.0078
2298.3438 | 121.9391 | -0.6134 | 121.2479 | -0.1033 | 0.015165 | -0.0084104 | 0.037995 | -0.013161 | -0.0087607 | 0.044043 | 0.091553 | 0.09613 | -0.13275 | 0.032043 | -0.041199 | 0.027466 | -0.18768 | 0.091553 | -0.050354 | -0.75073 | 0.48065 | -121.1517 | 0.70496 | 0.64545 | -121.2891 | -0.13733 | -121.2982 | 0.2243 | 0.42572 | 0.70496 | 0.5722 | 0.70953 | 0.70496 | 0.56305 | 0.64087 | -0.13733 | 0.70953 | 0.70496 | 0.64087 | 0.5722 | 0.56305 | -121.3806 | -121.9986
2299.3594 | 122.0215 | -0.61798 | 121.3028 | -0.11856 | 0.014524 | -0.005206 | 0.040131 | -0.01252 | -0.0047019 | 0.040625 | 0.09613 | 0.10071 | -0.14648 | 0.013733 | -0.050354 | 0 | -0.13275 | 0.086975 | -0.009155 | -0.77362 | 0.4715 | -121.2021 | 0.71411 | 0.63171 | -121.3531 | -0.15564 | -121.312 | 0.24261 | 0.48523 | 0.70496 | 0.56763 | 0.71869 | 0.71411 | 0.60883 | 0.61798 | -0.15564 | 0.71869 | 0.71411 | 0.61798 | 0.56763 | 0.60883 | -121.4493 | -122.0764
2300.3438 | 122.0901 | -0.61798 | 121.3028 | -0.065155 | 0.013243 | -0.007983 | 0.03949 | -0.0091024 | -0.0096151 | 0.040411 | 0.10071 | 0.10529 | -0.11902 | 0.036621 | -0.027466 | 0.036621 | -0.21057 | 0.10529 | -0.004578 | -0.74616 | 0.49896 | -121.1975 | 0.71869 | 0.6546 | -121.3303 | -0.12817 | -121.3074 | 0.21973 | 0.40741 | 0.72327 | 0.59052 | 0.72327 | 0.71869 | 0.6134 | 0.6546 | -0.12817 | 0.72327 | 0.71869 | 0.6546 | 0.59052 | 0.6134 | -121.4218 | -122.049
2301.3594 | 122.0398 | -0.64545 | 121.2982 | -0.20248 | 0.013029 | -0.012042 | 0.040986 | -0.013589 | -0.0053427 | 0.041052 | 0.068665 | 0.10986 | -0.15564 | -0.004578 | -0.064087 | -0.018311 | -0.091553 | 0.041199 | 0.022888 | -0.79193 | 0.48981 | -121.1884 | 0.71411 | 0.64087 | -121.3623 | -0.14648 | -121.2753 | 0.22431 | 0.55389 | 0.68665 | 0.58136 | 0.75531 | 0.71411 | 0.66834 | 0.62714 | -0.14648 | 0.75531 | 0.71411 | 0.62714 | 0.58136 | 0.66834 | -121.4539 | -122.0901
2302.3438 | 122.0673 | -0.66834 | 121.3211 | -0.16434 | 0.015592 | -0.0071286 | 0.039277 | -0.012734 | -0.0079061 | 0.040838 | 0.082397 | 0.09613 | -0.15106 | 0.022888 | -0.041199 | 0.009155 | -0.15564 | 0.07782 | 0.036621 | -0.78735 | 0.51727 | -121.225 | 0.75073 | 0.69122 | -121.3623 | -0.11902 | -121.2845 | 0.23346 | 0.5127 | 0.74616 | 0.62714 | 0.76446 | 0.75073 | 0.70496 | 0.67749 | -0.11902 | 0.76446 | 0.75073 | 0.67749 | 0.62714 | 0.70496 | -121.4722 | -122.1085
2303.3594 | 122.0764 | -0.70496 | 121.2616 | -0.095673 | 0.013456 | -0.01076 | 0.038636 | -0.011452 | -0.0072653 | 0.040625 | 0.10529 | 0.086975 | -0.14191 | 0.032043 | -0.018311 | 0.022888 | -0.082397 | 0.32501 | -0.009155 | -0.84228 | 0.56305 | -121.1746 | 0.81024 | 0.737 | -121.2799 | -0.13733 | -121.2708 | 0.24719 | 0.62256 | 1.03 | 0.68665 | 0.79193 | 0.81024 | 0.6958 | 0.72784 | -0.13733 | 0.79193 | 0.81024 | 0.72784 | 0.68665 | 0.6958 | -121.4035 | -122.1039
2304.3438 | 122.113 | -0.67749 | 121.3211 | 0.041657 | 0.014524 | -0.01076 | 0.037141 | -0.01487 | -0.0059835 | 0.043188 | 0.027466 | 0.09613 | -0.14191 | -0.009155 | -0.054932 | 0.013733 | -0.15106 | 0.064087 | 0.013733 | -0.81024 | 0.53558 | -121.225 | 0.70496 | 0.66834 | -121.376 | -0.13275 | -121.3074 | 0.16937 | 0.52643 | 0.74158 | 0.62256 | 0.77362 | 0.70496 | 0.69122 | 0.69122 | -0.13275 | 0.77362 | 0.70496 | 0.69122 | 0.62256 | 0.69122 | -121.463 | -122.1313
2305.3594 | 122.1634 | -0.68207 | 121.2891 | -0.095673 | 0.015379 | -0.0062742 | 0.039918 | -0.012093 | -0.0042747 | 0.042334 | 0.10071 | 0.10986 | -0.13275 | 0.013733 | -0.004578 | 0.032043 | -0.19226 | 0.09613 | 0.032043 | -0.8194 | 0.54932 | -121.1792 | 0.78278 | 0.6958 | -121.2936 | -0.13733 | -121.257 | 0.23346 | 0.48981 | 0.7782 | 0.67749 | 0.79193 | 0.78278 | 0.71411 | 0.71411 | -0.13733 | 0.79193 | 0.78278 | 0.71411 | 0.67749 | 0.71411 | -121.4218 | -122.1085
2306.3438 | 122.168 | -0.72327 | 121.2891 | -0.034637 | 0.012174 | -0.0084104 | 0.03885 | -0.012093 | -0.0079061 | 0.040838 | 0.086975 | 0.082397 | -0.13275 | 0.041199 | 0 | 0.050354 | -0.19226 | 0.09613 | -0.004578 | -0.84228 | 0.59052 | -121.2067 | 0.81024 | 0.76447 | -121.2891 | -0.11902 | -121.2936 | 0.21973 | 0.53101 | 0.8194 | 0.72327 | 0.80566 | 0.81024 | 0.71869 | 0.77362 | -0.11902 | 0.80566 | 0.81024 | 0.77362 | 0.72327 | 0.71869 | -121.4218 | -122.1313
2307.3438 | 122.049 | -0.71411 | 121.4172 | -0.049896 | 0.016874 | -0.0047788 | 0.046113 | -0.0097434 | -0.0059835 | 0.041052 | 0.059509 | 0.1236 | -0.16937 | -0.013733 | -0.10529 | -0.064087 | -0.086975 | -0.009155 | 0.032043 | -0.87433 | 0.54474 | -121.2936 | 0.77362 | 0.70038 | -121.5225 | -0.16022 | -121.3852 | 0.22888 | 0.62714 | 0.70496 | 0.60883 | 0.83771 | 0.77362 | 0.74615 | 0.65002 | -0.16022 | 0.83771 | 0.77362 | 0.65002 | 0.60883 | 0.74615 | -121.5866 | -122.2916
2308.3438 | 122.1451 | -0.73242 | 121.3074 | 0.056915 | 0.013243 | -0.0058468 | 0.035859 | -0.011239 | -0.0044883 | 0.042334 | 0.041199 | 0.10529 | -0.15564 | -0.032043 | -0.050354 | -0.004578 | -0.14648 | 0.032043 | 0.022888 | -0.85602 | 0.57678 | -121.2021 | 0.77362 | 0.70038 | -121.3577 | -0.1236 | -121.2845 | 0.19684 | 0.58594 | 0.76447 | 0.68207 | 0.83771 | 0.77362 | 0.75531 | 0.72784 | -0.1236 | 0.83771 | 0.77362 | 0.72784 | 0.68207 | 0.75531 | -121.463 | -122.1634
2309.3438 | 122.1497 | -0.737 | 121.2753 | 0.19424 | 0.015165 | -0.00093361 | 0.040131 | -0.010811 | -0.0029929 | 0.042975 | 0.091553 | 0.091553 | -0.15106 | 0 | -0.059509 | 0.013733 | -0.20599 | 0.045776 | 0.022888 | -0.86517 | 0.58594 | -121.1838 | 0.82855 | 0.737 | -121.3348 | -0.12817 | -121.2524 | 0.24261 | 0.53101 | 0.78278 | 0.67749 | 0.82855 | 0.82855 | 0.75989 | 0.75073 | -0.12817 | 0.82855 | 0.82855 | 0.75073 | 0.67749 | 0.75989 | -121.4264 | -122.1405
2310.3438 | 122.1817 | -0.75531 | 121.2753 | -0.080414 | 0.014738 | -0.0073422 | 0.039063 | -0.011666 | -0.0038473 | 0.043188 | 0.09613 | 0.10986 | -0.12817 | 0.018311 | 0.004578 | 0.045776 | -0.1831 | 0.091553 | 0.022888 | -0.88348 | 0.62714 | -121.1655 | 0.85144 | 0.77362 | -121.2708 | -0.12817 | -121.2524 | 0.2243 | 0.57221 | 0.84686 | 0.75989 | 0.86517 | 0.85144 | 0.7782 | 0.80109 | -0.12817 | 0.86517 | 0.85144 | 0.80109 | 0.75989 | 0.7782 | -121.4035 | -122.1588
2311.3594 | 122.081 | -0.80109 | 121.3211 | -0.0041198 | 0.017515 | -0.0037106 | 0.048463 | -0.011025 | -0.0057699 | 0.039343 | 0.073242 | 0.13275 | -0.17395 | -0.045776 | -0.10529 | -0.064087 | -0.073242 | -0.032043 | 0.032043 | -0.92926 | 0.62714 | -121.1884 | 0.87433 | 0.75531 | -121.4264 | -0.12817 | -121.2891 | 0.24719 | 0.72784 | 0.76904 | 0.6958 | 0.93384 | 0.87433 | 0.83313 | 0.737 | -0.12817 | 0.93384 | 0.87433 | 0.737 | 0.6958 | 0.83313 | -121.4951 | -122.2504
2312.3438 | 122.1634 | -0.75989 | 121.2891 | 0.095062 | 0.016661 | -0.0041378 | 0.0365 | -0.011666 | -0.0040609 | 0.041693 | 0 | 0.050354 | -0.19684 | -0.041199 | -0.068665 | -0.018311 | -0.13275 | 0.018311 | 0.018311 | -0.88806 | 0.56305 | -121.2387 | 0.75989 | 0.71869 | -121.3577 | -0.12817 | -121.2708 | 0.19684 | 0.62714 | 0.7782 | 0.69122 | 0.81024 | 0.75989 | 0.7782 | 0.74158 | -0.12817 | 0.81024 | 0.75989 | 0.74158 | 0.69122 | 0.7782 | -121.4859 | -122.1771
2313.3438 | 122.2092 | -0.77362 | 121.3074 | 0.0035097 | 0.016447 | -0.0067014 | 0.038422 | -0.012307 | -0.0042747 | 0.042547 | 0.045776 | 0.10071 | -0.14648 | -0.013733 | -0.050354 | 0.022888 | -0.14648 | 0.068665 | 0.018311 | -0.90179 | 0.62714 | -121.2067 | 0.8194 | 0.75989 | -121.3577 | -0.12817 | -121.2891 | 0.19226 | 0.62714 | 0.84229 | 0.72327 | 0.87433 | 0.8194 | 0.79193 | 0.79651 | -0.12817 | 0.87433 | 0.8194 | 0.79651 | 0.72327 | 0.79193 | -121.4539 | -122.2092
2314.3438 | 122.1817 | -0.76904 | 121.3074 | 0.18662 | 0.015592 | -0.0047788 | 0.040131 | -0.012093 | -0.0066245 | 0.040838 | 0.068665 | 0.10071 | -0.16022 | -0.022888 | -0.064087 | 0.004578 | -0.17853 | 0.036621 | 0.009155 | -0.90637 | 0.60883 | -121.2067 | 0.83771 | 0.74616 | -121.3715 | -0.13733 | -121.2982 | 0.22888 | 0.59052 | 0.80566 | 0.70496 | 0.86975 | 0.83771 | 0.7782 | 0.77362 | -0.13733 | 0.86975 | 0.83771 | 0.77362 | 0.70496 | 0.7782 | -121.4676 | -122.2137
2315.3438 | 122.2 | -0.78278 | 121.3211 | 0.17899 | 0.015165 | -0.00050621 | 0.041199 | -0.011666 | -0.0055563 | 0.041479 | 0.073242 | 0.082397 | -0.14191 | 0 | -0.064087 | 0.022888 | -0.19684 | 0.064087 | 0.009155 | -0.91095 | 0.64087 | -121.2387 | 0.85602 | 0.78278 | -121.3852 | -0.12817 | -121.312 | 0.21515 | 0.58594 | 0.84686 | 0.71869 | 0.86517 | 0.85602 | 0.79193 | 0.80566 | -0.12817 | 0.86517 | 0.85602 | 0.80566 | 0.71869 | 0.79193 | -121.463 | -122.2321
2316.375 | 122.1725 | -0.84228 | 121.3028 | 0.2095 | 0.015592 | -0.0056332 | 0.045258 | -0.0095296 | -0.0072653 | 0.040838 | 0.009155 | 0.14191 | -0.1831 | -0.07782 | -0.14648 | -0.073242 | -0.10529 | -0.054932 | 0.027466 | -0.94757 | 0.65918 | -121.1609 | 0.85144 | 0.76446 | -121.4493 | -0.10529 | -121.2753 | 0.19226 | 0.737 | 0.78735 | 0.6958 | 0.98419 | 0.85144 | 0.86975 | 0.76904 | -0.10529 | 0.98419 | 0.85144 | 0.76904 | 0.6958 | 0.86975 | -121.4859 | -122.2504
2317.3438 | 122.2137 | -0.79651 | 121.2936 | 0.18662 | 0.013883 | -0.0056332 | 0.039918 | -0.011666 | -0.0055563 | 0.043188 | 0.054932 | 0.09613 | -0.13275 | 0.009155 | -0.054932 | 0.032043 | -0.20142 | 0.054932 | 0.022888 | -0.94757 | 0.66376 | -121.1975 | 0.85144 | 0.80566 | -121.3486 | -0.15106 | -121.2708 | 0.18768 | 0.59509 | 0.85144 | 0.74158 | 0.89264 | 0.85144 | 0.8194 | 0.82855 | -0.15106 | 0.89264 | 0.85144 | 0.82855 | 0.74158 | 0.8194 | -121.4264 | -122.2412
2318.3438 | 122.1817 | -0.87891 | 121.3028 | 0.034027 | 0.017088 | -0.0028562 | 0.043763 | -0.0088888 | -0.0044883 | 0.041479 | 0.068665 | 0.13733 | -0.17853 | -0.022888 | -0.11902 | -0.068665 | -0.059509 | -0.009155 | 0.018311 | -1.0208 | 0.70038 | -121.1655 | 0.94757 | 0.85602 | -121.4218 | -0.14191 | -121.2845 | 0.24719 | 0.8194 | 0.86975 | 0.75989 | 1.0162 | 0.94757 | 0.89722 | 0.81024 | -0.14191 | 1.0162 | 0.94757 | 0.81024 | 0.75989 | 0.89722 | -121.4813 | -122.3236
2319.3438 | 122.2778 | -0.8606 | 121.2753 | 0.064545 | 0.016447 | -0.0039242 | 0.039918 | -0.0088888 | -0.0064109 | 0.042334 | 0.073242 | 0.045776 | -0.16022 | 0.013733 | -0.036621 | 0.022888 | -0.21515 | 0.068665 | -0.009155 | -1.0025 | 0.70038 | -121.2296 | 0.93384 | 0.87433 | -121.312 | -0.14191 | -121.2845 | 0.23346 | 0.64545 | 0.92926 | 0.82398 | 0.90637 | 0.93384 | 0.85144 | 0.88348 | -0.14191 | 0.90637 | 0.93384 | 0.88348 | 0.82398 | 0.85144 | -121.4355 | -122.2778
2320.3594 | 122.2 | -0.87433 | 121.2662 | 0.20187 | 0.01901 | -0.003497 | 0.043336 | -0.0084616 | -0.0049155 | 0.041052 | 0.009155 | 0.12817 | -0.18768 | -0.082397 | -0.13733 | -0.07782 | -0.10986 | -0.032043 | 0.022888 | -1.0254 | 0.68665 | -121.138 | 0.88348 | 0.79193 | -121.4035 | -0.15106 | -121.2433 | 0.19684 | 0.76447 | 0.84229 | 0.737 | 1.0025 | 0.88348 | 0.89722 | 0.79651 | -0.15106 | 1.0025 | 0.88348 | 0.79651 | 0.737 | 0.89722 | -121.4539 | -122.2916
2321.3438 | 122.2458 | -0.92468 | 121.257 | 0.10269 | 0.01367 | -0.0032834 | 0.037781 | -0.011666 | -0.0047019 | 0.042334 | -0.009155 | 0.10071 | -0.17395 | -0.14191 | -0.11444 | -0.045776 | -0.16479 | 0.018311 | -0.054932 | -1.0574 | 0.75073 | -121.1563 | 0.91553 | 0.78278 | -121.3715 | -0.13275 | -121.312 | 0.16479 | 0.75989 | 0.94299 | 0.81024 | 1.0254 | 0.91553 | 0.86975 | 0.87891 | -0.13275 | 1.0254 | 0.91553 | 0.87891 | 0.81024 | 0.86975 | -121.431 | -122.3145
2322.3438 | 122.2 | -0.88348 | 121.3211 | -0.233 | 0.016447 | -0.0067014 | 0.039918 | -0.01188 | -0.0049155 | 0.042975 | 0.041199 | 0.10529 | -0.16937 | -0.036621 | -0.086975 | -0.036621 | -0.022888 | 0.032043 | 0.050354 | -1.0208 | 0.71411 | -121.2158 | 0.92468 | 0.84686 | -121.4081 | -0.13733 | -121.2708 | 0.21057 | 0.8606 | 0.91553 | 0.79651 | 0.98877 | 0.92468 | 0.93384 | 0.84686 | -0.13733 | 0.98877 | 0.92468 | 0.84686 | 0.79651 | 0.93384 | -121.4905 | -122.3419
2323.3438 | 122.2183 | -0.89264 | 121.3165 | 0.19424 | 0.015379 | -0.0030698 | 0.04419 | -0.010811 | -0.0029929 | 0.04212 | 0.004578 | 0.13275 | -0.19684 | -0.091553 | -0.15564 | -0.086975 | -0.073242 | -0.059509 | 0.064087 | -1.0529 | 0.6958 | -121.1838 | 0.89722 | 0.80109 | -121.4722 | -0.16022 | -121.2524 | 0.20142 | 0.8194 | 0.83313 | 0.737 | 1.0254 | 0.89722 | 0.95673 | 0.80566 | -0.16022 | 1.0254 | 0.89722 | 0.80566 | 0.737 | 0.95673 | -121.5134 | -122.3694
2324.3438 | 122.2275 | -0.87891 | 121.3669 | -0.019379 | 0.017515 | -0.00093361 | 0.04419 | -0.009957 | -0.0059835 | 0.04212 | 0.068665 | 0.13733 | -0.16479 | -0.027466 | -0.11902 | -0.059509 | -0.068665 | 0.009155 | 0.050354 | -1.0071 | 0.71411 | -121.2296 | 0.94757 | 0.85144 | -121.4859 | -0.12817 | -121.3165 | 0.23346 | 0.81024 | 0.88806 | 0.75989 | 1.0162 | 0.94757 | 0.92926 | 0.8194 | -0.12817 | 1.0162 | 0.94757 | 0.8194 | 0.75989 | 0.92926 | -121.5317 | -122.374
2325.3438 | 122.3373 | -0.85602 | 121.312 | -0.057526 | 0.015806 | -0.0054196 | 0.039277 | -0.0067526 | -0.0081199 | 0.040838 | 0.054932 | 0.045776 | -0.1831 | 0 | -0.036621 | 0.032043 | -0.21973 | 0.073242 | 0.027466 | -0.97046 | 0.67291 | -121.2662 | 0.91095 | 0.85602 | -121.3486 | -0.11444 | -121.2845 | 0.23804 | 0.63629 | 0.92926 | 0.8194 | 0.90179 | 0.91095 | 0.88348 | 0.88806 | -0.11444 | 0.90179 | 0.91095 | 0.88806 | 0.8194 | 0.88348 | -121.4951 | -122.2824
2326.3594 | 122.2092 | -0.91095 | 121.3394 | 2.6662 | 0.01367 | -0.0054196 | 0.043549 | -0.010384 | -0.0083335 | 0.041906 | 0.13275 | 0.12817 | -0.16479 | -0.086975 | -0.15564 | -0.09613 | -0.045776 | -0.064087 | 0.068665 | -1.0162 | 0.74616 | -121.2112 | 1.0437 | 0.82398 | -121.4951 | -0.10528 | -121.2708 | 0.29755 | 0.86517 | 0.84686 | 0.75531 | 1.0391 | 1.0437 | 0.97962 | 0.81482 | -0.10528 | 1.0391 | 1.0437 | 0.81482 | 0.75531 | 0.97962 | -121.5042 | -122.3557
2327.3438 | 122.2778 | -0.9201 | 121.3028 | 0.19424 | 0.01602 | -0.0067014 | 0.042481 | -0.0056844 | -0.0055563 | 0.040198 | 0.027466 | 0.11902 | -0.1831 | -0.07782 | -0.11444 | -0.045776 | -0.13275 | -0.004578 | 0.027466 | -1.0529 | 0.737 | -121.1838 | 0.94757 | 0.84228 | -121.4172 | -0.13275 | -121.2753 | 0.21057 | 0.78735 | 0.91553 | 0.80566 | 1.0391 | 0.94757 | 0.94757 | 0.87433 | -0.13275 | 1.0391 | 0.94757 | 0.87433 | 0.80566 | 0.94757 | -121.4859 | -122.3557
2328.3438 | 122.3282 | -0.87433 | 121.2799 | 0.24765 | 0.017729 | -0.0045652 | 0.04184 | -0.008248 | -0.0057699 | 0.042761 | 0.064087 | 0.10071 | -0.16937 | 0 | -0.050354 | 0.032043 | -0.19226 | 0.068665 | 0.018311 | -1.0071 | 0.70496 | -121.1792 | 0.93842 | 0.87433 | -121.3303 | -0.13275 | -121.2616 | 0.23346 | 0.68207 | 0.94299 | 0.82398 | 0.97504 | 0.93842 | 0.89264 | 0.90637 | -0.13275 | 0.97504 | 0.93842 | 0.90637 | 0.82398 | 0.89264 | -121.4493 | -122.287
2329.3438 | 122.3419 | -0.88806 | 121.2936 | 0.23239 | 0.017088 | -0.0073422 | 0.043336 | -0.0086752 | -0.0068381 | 0.043615 | 0.09613 | 0.091553 | -0.14191 | 0.013733 | -0.091553 | 0.022888 | -0.21515 | 0.032043 | -0.045776 | -1.0391 | 0.74616 | -121.2021 | 0.98419 | 0.9018 | -121.3852 | -0.15106 | -121.3394 | 0.23804 | 0.67291 | 0.92011 | 0.79651 | 0.97962 | 0.98419 | 0.84229 | 0.91095 | -0.15106 | 0.97962 | 0.98419 | 0.91095 | 0.79651 | 0.84229 | -121.4355 | -122.3328
2330.3438 | 122.3328 | -0.95215 | 121.2387 | 0.17899 | 0.015806 | -0.0030698 | 0.039704 | -0.0097434 | -0.0072653 | 0.04212 | 0.07782 | 0.07782 | -0.16022 | 0 | -0.041199 | 0.032043 | -0.19226 | 0.091553 | 0 | -1.0483 | 0.79193 | -121.1609 | 1.03 | 0.95215 | -121.2799 | -0.096131 | -121.2387 | 0.23804 | 0.75989 | 1.0437 | 0.91095 | 1.03 | 1.03 | 0.95215 | 0.98419 | -0.096131 | 1.03 | 1.03 | 0.98419 | 0.91095 | 0.95215 | -121.3989 | -122.287
2331.3438 | 122.2824 | -0.95215 | 121.2891 | 0.21713 | 0.017729 | -0.0045652 | 0.043549 | -0.010384 | -0.0053427 | 0.043829 | 0.004578 | 0.13275 | -0.19226 | -0.086975 | -0.14648 | -0.07782 | -0.082397 | -0.004578 | 0.036621 | -1.0986 | 0.75989 | -121.1563 | 0.95673 | 0.86517 | -121.4355 | -0.14648 | -121.2524 | 0.19684 | 0.86975 | 0.94757 | 0.80566 | 1.0849 | 0.95673 | 0.98877 | 0.87433 | -0.14648 | 1.0849 | 0.95673 | 0.87433 | 0.80566 | 0.98877 | -121.4813 | -122.3877
2332.3438 | 122.3053 | -0.9201 | 121.3028 | -0.21011 | 0.016661 | -0.0045652 | 0.039063 | -0.0086752 | -0.0055563 | 0.041266 | 0.059509 | 0.09613 | -0.14191 | -0.009155 | -0.045776 | 0.004578 | -0.054932 | 0.09613 | 0.027466 | -1.0391 | 0.7782 | -121.2067 | 0.97961 | 0.91095 | -121.3486 | -0.11902 | -121.2753 | 0.20142 | 0.86517 | 1.0162 | 0.87433 | 1.0162 | 0.97961 | 0.94757 | 0.92468 | -0.11902 | 1.0162 | 0.97961 | 0.92468 | 0.87433 | 0.94757 | -121.4447 | -122.3419
2333.3438 | 122.2916 | -0.92468 | 121.3211 | 0.22476 | 0.01901 | -0.0022152 | 0.042908 | -0.0069662 | -0.0055563 | 0.041693 | 0.013733 | 0.10986 | -0.20142 | -0.068665 | -0.13275 | -0.059509 | -0.11444 | -0.013733 | 0.018311 | -1.0391 | 0.72327 | -121.2112 | 0.93842 | 0.85602 | -121.4539 | -0.11444 | -121.3028 | 0.21515 | 0.81024 | 0.91095 | 0.79193 | 1.0345 | 0.93842 | 0.94299 | 0.86517 | -0.11444 | 1.0345 | 0.93842 | 0.86517 | 0.79193 | 0.94299 | -121.5225 | -122.3602
2334.3594 | 122.2961 | -0.89722 | 121.3531 | -0.049896 | 0.016874 | -0.0011472 | 0.04184 | -0.0078206 | -0.0066245 | 0.041479 | 0.13275 | 0.16022 | -0.10986 | -0.004578 | -0.07782 | -0.013733 | -0.064087 | 0.054932 | 0.09613 | -1.0254 | 0.78735 | -121.1929 | 1.03 | 0.89264 | -121.431 | -0.12817 | -121.257 | 0.24261 | 0.83313 | 0.95215 | 0.8194 | 1.0574 | 1.03 | 0.99335 | 0.88348 | -0.12817 | 1.0574 | 1.03 | 0.88348 | 0.8194 | 0.99335 | -121.463 | -122.3785
2335.3438 | 122.0856 | -0.91553 | 121.4035 | 0.14084 | 0.018797 | -0.003497 | 0.043976 | -0.008248 | -0.0057699 | 0.042761 | -0.013733 | 0.1236 | -0.20599 | -0.1236 | -0.17395 | -0.10986 | 0 | -0.064087 | 0.045776 | -1.0437 | 0.70953 | -121.2799 | 0.90179 | 0.79193 | -121.5775 | -0.12817 | -121.3577 | 0.19226 | 0.91553 | 0.85144 | 0.74158 | 1.0391 | 0.90179 | 0.9613 | 0.80566 | -0.12817 | 1.0391 | 0.90179 | 0.80566 | 0.74158 | 0.9613 | -121.6095 | -122.4472
2336.3594 | 122.2733 | -0.92468 | 121.3669 | 0.17136 | 0.017942 | -0.0037106 | 0.043122 | -0.0067526 | -0.0049155 | 0.042334 | 0 | 0.13275 | -0.19226 | -0.10071 | -0.15106 | -0.091553 | -0.036621 | -0.041199 | 0.032043 | -1.0437 | 0.73242 | -121.2341 | 0.92468 | 0.82398 | -121.5179 | -0.11902 | -121.3348 | 0.19226 | 0.88806 | 0.88348 | 0.77362 | 1.0574 | 0.92468 | 0.95673 | 0.83313 | -0.11902 | 1.0574 | 0.92468 | 0.83313 | 0.77362 | 0.95673 | -121.5591 | -122.4106
2337.3438 | 122.2549 | -0.88806 | 121.4172 | 0.11032 | 0.019651 | -0.0058468 | 0.040131 | -0.0078206 | -0.0059835 | 0.04682 | -0.018311 | 0.15106 | -0.20142 | -0.12817 | -0.36163 | -0.12817 | 0.15106 | -0.054932 | 0.068665 | -1.0025 | 0.68665 | -121.2662 | 0.86975 | 0.75989 | -121.7789 | -0.11444 | -121.3486 | 0.18311 | 1.0391 | 0.83313 | 0.52643 | 1.0391 | 0.86975 | 0.95673 | 0.75989 | -0.11444 | 1.0391 | 0.86975 | 0.75989 | 0.52643 | 0.95673 | -121.6187 | -122.4197
2338.3594 | 122.2824 | -0.89264 | 121.3898 | 0.1561 | 0.016233 | -0.0037106 | 0.040772 | -0.0078206 | -0.0038473 | 0.043829 | -0.004578 | 0.12817 | -0.20599 | -0.10986 | -0.16479 | -0.073242 | -0.054932 | -0.032043 | 0.036621 | -1.0254 | 0.68664 | -121.2616 | 0.88806 | 0.78278 | -121.5546 | -0.13275 | -121.3531 | 0.20142 | 0.83771 | 0.8606 | 0.72784 | 1.0208 | 0.88806 | 0.92926 | 0.8194 | -0.13275 | 1.0208 | 0.88806 | 0.8194 | 0.72784 | 0.92926 | -121.5958 | -122.4152
2339.3438 | 122.3099 | -0.89264 | 121.4081 | 0.20187 | 0.017729 | -0.001788 | 0.04184 | -0.0078206 | -0.0042747 | 0.04212 | -0.004578 | 0.13733 | -0.1831 | -0.10529 | -0.14191 | -0.07782 | -0.07782 | -0.032043 | 0.045776 | -1.0208 | 0.70953 | -121.2708 | 0.88806 | 0.78735 | -121.55 | -0.12817 | -121.3623 | 0.17853 | 0.81482 | 0.8606 | 0.75073 | 1.03 | 0.88806 | 0.93841 | 0.81482 | -0.12817 | 1.03 | 0.88806 | 0.81482 | 0.75073 | 0.93841 | -121.5912 | -122.4289
2340.3438 | 122.2641 | -0.90179 | 121.4355 | 0.23239 | 0.014311 | -0.0043514 | 0.042908 | -0.0078206 | -0.0066245 | 0.04212 | -0.018311 | 0.12817 | -0.1831 | -0.1236 | -0.16937 | -0.10986 | 0.004578 | -0.059509 | 0.07782 | -1.0391 | 0.71869 | -121.3074 | 0.88348 | 0.7782 | -121.6049 | -0.13733 | -121.3577 | 0.16479 | 0.90637 | 0.84228 | 0.73242 | 1.03 | 0.88348 | 0.97961 | 0.79193 | -0.13733 | 1.03 | 0.88348 | 0.79193 | 0.73242 | 0.97961 | -121.6187 | -122.4747
2341.3438 | 122.3328 | -0.93384 | 121.3898 | 0.2095 | 0.016874 | -0.0054196 | 0.039918 | -0.007607 | -0.0068381 | 0.04212 | 0.004578 | 0.12817 | -0.19226 | -0.10529 | -0.15106 | -0.07782 | -0.07782 | -0.022888 | 0.054932 | -1.0483 | 0.74158 | -121.2616 | 0.93842 | 0.82855 | -121.5408 | -0.11444 | -121.3348 | 0.19684 | 0.85602 | 0.91095 | 0.78278 | 1.062 | 0.93842 | 0.98877 | 0.85602 | -0.11444 | 1.062 | 0.93842 | 0.85602 | 0.78278 | 0.98877 | -121.582 | -122.438
2342.3438 | 122.3145 | -0.93842 | 121.376 | 0.041657 | 0.017515 | -0.0037106 | 0.043122 | -0.0067526 | -0.0059835 | 0.042334 | 0.036621 | 0.1236 | -0.18768 | -0.073242 | -0.14648 | -0.086975 | -0.050354 | -0.013733 | 0.054932 | -1.0666 | 0.75073 | -121.2524 | 0.97504 | 0.86517 | -121.5225 | -0.12817 | -121.3211 | 0.2243 | 0.88806 | 0.92468 | 0.79193 | 1.062 | 0.97504 | 0.99335 | 0.85144 | -0.12817 | 1.062 | 0.97504 | 0.85144 | 0.79193 | 0.99335 | -121.5637 | -122.4426
2343.3438 | 122.3557 | -0.93842 | 121.3806 | 0.17136 | 0.014524 | -0.0073422 | 0.040345 | -0.0061118 | -0.0049155 | 0.04447 | 0 | 0.13275 | -0.1831 | -0.11444 | -0.14648 | -0.054932 | -0.082397 | -0.004578 | 0.041199 | -1.0437 | 0.75531 | -121.2479 | 0.93842 | 0.82398 | -121.5271 | -0.10528 | -121.3394 | 0.1831 | 0.85602 | 0.93384 | 0.79193 | 1.0712 | 0.93842 | 0.97962 | 0.88348 | -0.10528 | 1.0712 | 0.93842 | 0.88348 | 0.79193 | 0.97962 | -121.5637 | -122.4243
2344.3594 | 122.3969 | -0.89264 | 121.3852 | 0.13321 | 0.012815 | -0.0071286 | 0.032227 | -0.010598 | -0.0059835 | 0.042547 | 0.009155 | 0.10986 | -0.14191 | -0.07782 | -0.091553 | -0.013733 | -0.11902 | 0.068665 | 0.022888 | -1.0208 | 0.75073 | -121.2753 | 0.90179 | 0.81482 | -121.4767 | -0.12817 | -121.3623 | 0.15106 | 0.77362 | 0.9613 | 0.80109 | 1.0025 | 0.90179 | 0.91553 | 0.87891 | -0.12817 | 1.0025 | 0.90179 | 0.87891 | 0.80109 | 0.91553 | -121.5271 | -122.406
2345.3438 | 122.3648 | -0.94757 | 121.3852 | 0.026398 | 0.018583 | -0.0049924 | 0.043976 | -0.010811 | -0.0049155 | 0.041906 | 0.32959 | 0.13733 | -0.14648 | -0.009155 | -0.068665 | -0.032043 | -0.032043 | 0.050354 | 0.091553 | -1.062 | 0.80109 | -121.2479 | 1.2772 | 0.93842 | -121.4539 | -0.11444 | -121.2936 | 0.47607 | 0.91553 | 0.99793 | 0.87891 | 1.0849 | 1.2772 | 1.0391 | 0.91553 | -0.11444 | 1.0849 | 1.2772 | 0.91553 | 0.87891 | 1.0391 | -121.5317 | -122.4472
2346.3594 | 122.3557 | -1.0208 | 121.3348 | -0.19485 | 0.017301 | -0.0056332 | 0.043549 | -0.010171 | -0.0059835 | 0.042547 | 0.018311 | 0.12817 | -0.19684 | -0.054932 | -0.10986 | -0.068665 | -0.045776 | 0.036621 | 0.050354 | -1.1398 | 0.82397 | -121.2067 | 1.0391 | 0.96588 | -121.4447 | -0.11902 | -121.2845 | 0.21515 | 0.97504 | 1.0574 | 0.91095 | 1.149 | 1.0391 | 1.0712 | 0.95215 | -0.11902 | 1.149 | 1.0391 | 0.95215 | 0.91095 | 1.0712 | -121.5317 | -122.4747
2347.3438 | 122.374 | -1.0208 | 121.3348 | -0.14908 | 0.015592 | -0.0060604 | 0.039918 | -0.009957 | -0.0051291 | 0.042975 | -0.013733 | 0.13733 | -0.18768 | -0.082397 | -0.12817 | -0.086975 | 0.004578 | -0.004578 | 0.059509 | -1.1536 | 0.83313 | -121.1975 | 1.0071 | 0.93842 | -121.463 | -0.13275 | -121.2753 | 0.17395 | 1.0254 | 1.0162 | 0.89264 | 1.1581 | 1.0071 | 1.0803 | 0.93384 | -0.13275 | 1.1581 | 1.0071 | 0.93384 | 0.89264 | 1.0803 | -121.5225 | -122.4884
2348.3438 | 122.4655 | -0.99792 | 121.3211 | -0.080414 | 0.012174 | -0.0047788 | 0.032441 | -0.0086752 | -0.0047019 | 0.043188 | 0.032043 | 0.086975 | -0.15106 | -0.004578 | -0.022888 | 0.054932 | -0.1236 | 0.13275 | 0.045776 | -1.1169 | 0.84686 | -121.2341 | 1.03 | 0.99335 | -121.344 | -0.11902 | -121.2753 | 0.18311 | 0.87433 | 1.1307 | 0.97504 | 1.0849 | 1.03 | 1.0437 | 1.0529 | -0.11902 | 1.0849 | 1.03 | 1.0529 | 0.97504 | 1.0437 | -121.4722 | -122.438
2349.3438 | 122.374 | -1.0803 | 121.4081 | -0.095673 | 0.016233 | -0.0049924 | 0.043763 | -0.0095296 | -0.0061973 | 0.041693 | 0.050354 | 0.1236 | -0.1831 | -0.036621 | -0.10071 | -0.054932 | -0.07782 | 0.032043 | 0.054932 | -1.181 | 0.89722 | -121.2845 | 1.1307 | 1.0437 | -121.5088 | -0.10071 | -121.3531 | 0.23346 | 1.0025 | 1.1124 | 0.97961 | 1.2039 | 1.1307 | 1.1353 | 1.0254 | -0.10071 | 1.2039 | 1.1307 | 1.0254 | 0.97961 | 1.1353 | -121.5912 | -122.5891
2350.3438 | 122.3557 | -1.1124 | 121.257 | 0.0035097 | 0.019651 | -0.0047788 | 0.043976 | -0.0069662 | -0.0036337 | 0.040838 | 0.032043 | 0.11444 | -0.19226 | -0.086975 | -0.14191 | -0.086975 | -0.059509 | -0.018311 | 0.041199 | -1.2543 | 0.9201 | -121.1426 | 1.1444 | 1.0254 | -121.3989 | -0.14191 | -121.2158 | 0.2243 | 1.0529 | 1.0941 | 0.97046 | 1.2268 | 1.1444 | 1.1536 | 1.0254 | -0.14191 | 1.2268 | 1.1444 | 1.0254 | 0.97046 | 1.1536 | -121.4493 | -122.5113
2351.3438 | 122.3511 | -1.1078 | 121.2936 | -0.1796 | 0.018156 | -0.0037106 | 0.039063 | -0.010171 | -0.0059835 | 0.041479 | -0.027466 | 0.14191 | -0.18768 | -0.10529 | -0.13275 | -0.086975 | 0.027466 | -0.009155 | 0.068665 | -1.2268 | 0.9201 | -121.1517 | 1.0803 | 1.0025 | -121.4264 | -0.11902 | -121.225 | 0.16022 | 1.1353 | 1.0986 | 0.97504 | 1.2497 | 1.0803 | 1.1765 | 1.0208 | -0.11902 | 1.2497 | 1.0803 | 1.0208 | 0.97504 | 1.1765 | -121.4813 | -122.5204
2352.375 | 122.374 | -1.1444 | 121.2479 | 0.049286 | 0.018156 | -0.005206 | 0.042908 | -0.006539 | -0.0040609 | 0.041266 | 0.041199 | 0.1236 | -0.18768 | -0.07782 | -0.13733 | -0.082397 | -0.050354 | -0.022888 | 0.032043 | -1.268 | 0.95673 | -121.1243 | 1.1856 | 1.0666 | -121.3852 | -0.1236 | -121.2158 | 0.22888 | 1.0941 | 1.1215 | 1.0071 | 1.268 | 1.1856 | 1.1765 | 1.062 | -0.1236 | 1.268 | 1.1856 | 1.062 | 1.0071 | 1.1765 | -121.4355 | -122.5159
2353.3438 | 122.4106 | -1.1261 | 121.2799 | -0.13382 | 0.016447 | -0.0022152 | 0.043122 | -0.0095296 | -0.0042747 | 0.043615 | 0.022888 | 0.10529 | -0.1831 | -0.068665 | -0.11444 | -0.059509 | -0.045776 | 0.027466 | 0.027466 | -1.2497 | 0.94299 | -121.1746 | 1.149 | 1.0574 | -121.3943 | -0.1236 | -121.2524 | 0.20599 | 1.0803 | 1.1536 | 1.0117 | 1.2314 | 1.149 | 1.1536 | 1.0666 | -0.1236 | 1.2314 | 1.149 | 1.0666 | 1.0117 | 1.1536 | -121.463 | -122.5296
2354.3594 | 122.5067 | -1.0712 | 121.2387 | -0.080414 | 0.014097 | -0.0054196 | 0.034363 | -0.010598 | -0.0053427 | 0.041693 | 0.068665 | 0.086975 | -0.13733 | 0.027466 | 0.004578 | 0.059509 | -0.16479 | 0.15106 | 0.022888 | -1.2039 | 0.93384 | -121.1517 | 1.1398 | 1.0986 | -121.2341 | -0.13275 | -121.2158 | 0.20599 | 0.90637 | 1.2222 | 1.0757 | 1.1581 | 1.1398 | 1.0941 | 1.1307 | -0.13275 | 1.1581 | 1.1398 | 1.1307 | 1.0757 | 1.0941 | -121.376 | -122.4426
2355.3438 | 122.4106 | -1.1078 | 121.3165 | -0.12619 | 0.016233 | -0.0056332 | 0.045258 | -0.0069662 | -0.0044883 | 0.043188 | 0.10986 | 0.19684 | -0.10529 | -0.032043 | -0.10071 | -0.036621 | -0.086975 | 0.036621 | 0.059509 | -1.2543 | 1.0025 | -121.1197 | 1.2177 | 1.0757 | -121.4172 | -0.14648 | -121.257 | 0.21515 | 1.0208 | 1.1444 | 1.0071 | 1.3046 | 1.2177 | 1.1673 | 1.0712 | -0.14648 | 1.3046 | 1.2177 | 1.0712 | 1.0071 | 1.1673 | -121.4218 | -122.5708
2356.3594 | 122.3557 | -1.1307 | 121.3211 | 0.10269 | 0.01837 | -0.00093361 | 0.043549 | -0.0073934 | -0.0057699 | 0.041906 | -0.004578 | 0.13733 | -0.19226 | -0.11902 | -0.16479 | -0.11444 | -0.018311 | -0.082397 | 0.045776 | -1.2497 | 0.93841 | -121.1838 | 1.1261 | 1.0117 | -121.4859 | -0.11902 | -121.2753 | 0.18768 | 1.1124 | 1.0483 | 0.96588 | 1.268 | 1.1261 | 1.1765 | 1.0162 | -0.11902 | 1.268 | 1.1261 | 1.0162 | 0.96588 | 1.1765 | -121.5134 | -122.5708
2357.3438 | 122.374 | -1.0986 | 121.344 | 0.16373 | 0.014738 | -0.007983 | 0.039063 | -0.0095296 | -0.0059835 | 0.043402 | 0.013733 | 0.19684 | -0.15564 | -0.10071 | -0.13275 | -0.09613 | 0.027466 | -0.009155 | 0.082397 | -1.2177 | 0.94299 | -121.1472 | 1.1124 | 0.99792 | -121.4767 | -0.11902 | -121.2616 | 0.16937 | 1.1261 | 1.0895 | 0.96588 | 1.2955 | 1.1124 | 1.181 | 1.0025 | -0.11902 | 1.2955 | 1.1124 | 1.0025 | 0.96588 | 1.181 | -121.4996 | -122.5616
2358.3594 | 122.3923 | -1.0849 | 121.3165 | 0.072174 | 0.016447 | -0.005206 | 0.043549 | -0.0067526 | -0.0059835 | 0.042975 | 0.022888 | 0.11902 | -0.1831 | -0.091553 | -0.14648 | -0.10986 | -0.064087 | -0.027466 | 0.036621 | -1.2131 | 0.9018 | -121.1975 | 1.1078 | 0.99335 | -121.463 | -0.12817 | -121.2799 | 0.20599 | 1.0208 | 1.0574 | 0.93842 | 1.2039 | 1.1078 | 1.1215 | 0.97504 | -0.12817 | 1.2039 | 1.1078 | 0.97504 | 0.93842 | 1.1215 | -121.4996 | -122.5296
2359.3438 | 122.4106 | -1.0849 | 121.3486 | -0.1796 | 0.016661 | -0.0026426 | 0.042481 | -0.009957 | -0.0057699 | 0.041266 | -0.013733 | 0.15564 | -0.19684 | -0.091553 | -0.12817 | -0.086975 | -0.018311 | -0.013733 | 0.045776 | -1.2222 | 0.88806 | -121.1929 | 1.0712 | 0.99335 | -121.4767 | -0.13733 | -121.3028 | 0.18311 | 1.0666 | 1.0712 | 0.95673 | 1.2405 | 1.0712 | 1.1307 | 0.99792 | -0.13733 | 1.2405 | 1.0712 | 0.99792 | 0.95673 | 1.1307 | -121.5454 | -122.5708
2360.3594 | 122.438 | -1.0849 | 121.3577 | -0.16434 | 0.014952 | -0.0064878 | 0.041413 | -0.0091024 | -0.0068381 | 0.043402 | 0 | 0.11444 | -0.19684 | -0.091553 | -0.13733 | -0.09613 | -0.009155 | -0.009155 | 0.054932 | -1.2131 | 0.88806 | -121.2433 | 1.0849 | 0.99335 | -121.4951 | -0.12817 | -121.3028 | 0.19684 | 1.0757 | 1.0757 | 0.94757 | 1.1993 | 1.0849 | 1.1398 | 0.98877 | -0.12817 | 1.1993 | 1.0849 | 0.98877 | 0.94757 | 1.1398 | -121.5546 | -122.5708
2361.3281 | 122.4106 | -1.0941 | 121.344 | 0.064545 | 0.014952 | -0.0028562 | 0.042267 | -0.0063254 | -0.0053427 | 0.041479 | 0.009155 | 0.10071 | -0.21515 | -0.10529 | -0.14648 | -0.10071 | -0.059509 | -0.041199 | 0.036621 | -1.2039 | 0.87891 | -121.2433 | 1.1032 | 0.98877 | -121.4905 | -0.10986 | -121.3074 | 0.2243 | 1.0345 | 1.0529 | 0.94757 | 1.1948 | 1.1032 | 1.1307 | 0.99335 | -0.10986 | 1.1948 | 1.1032 | 0.99335 | 0.94757 | 1.1307 | -121.5591 | -122.5479
2362.3594 | 122.4792 | -1.0666 | 121.3898 | -0.19485 | 0.014952 | -0.0024288 | 0.034791 | -0.0086752 | -0.0068381 | 0.041052 | 0.068665 | 0.07782 | -0.16022 | -0.013733 | -0.036621 | 0.004578 | -0.10071 | 0.082397 | 0.027466 | -1.181 | 0.90637 | -121.312 | 1.1353 | 1.0529 | -121.4264 | -0.11444 | -121.3623 | 0.22888 | 0.96588 | 1.149 | 1.03 | 1.1444 | 1.1353 | 1.0941 | 1.0712 | -0.11444 | 1.1444 | 1.1353 | 1.0712 | 1.03 | 1.0941 | -121.55 | -122.5708
2363.3438 | 122.4243 | -1.0941 | 121.3806 | -0.42374 | 0.015806 | -0.0084104 | 0.039704 | -0.010598 | -0.0061973 | 0.041693 | -0.045776 | 0.11444 | -0.20142 | -0.091553 | -0.13275 | -0.09613 | 0.009155 | -0.022888 | 0.059509 | -1.2085 | 0.89264 | -121.2662 | 1.0483 | 1.0025 | -121.5134 | -0.11444 | -121.3211 | 0.15564 | 1.1032 | 1.0712 | 0.9613 | 1.2085 | 1.0483 | 1.1536 | 0.99792 | -0.11444 | 1.2085 | 1.0483 | 0.99792 | 0.9613 | 1.1536 | -121.582 | -122.5891
2364.3438 | 122.4884 | -1.0574 | 121.3394 | 0.14847 | 0.017088 | -0.0073422 | 0.036072 | -0.010598 | -0.0040609 | 0.042761 | 0.064087 | 0.10071 | -0.14191 | -0.045776 | -0.068665 | -0.004578 | -0.16479 | 0.054932 | 0.027466 | -1.1856 | 0.91553 | -121.2387 | 1.1215 | 1.0117 | -121.4081 | -0.12817 | -121.312 | 0.20599 | 0.89264 | 1.1124 | 0.98877 | 1.1581 | 1.1215 | 1.0849 | 1.0529 | -0.12817 | 1.1581 | 1.1215 | 1.0529 | 0.98877 | 1.0849 | -121.4813 | -122.525
2365.3438 | 122.5754 | -1.0345 | 121.3257 | -0.088043 | 0.012174 | -0.0056332 | 0.034577 | -0.011025 | -0.0049155 | 0.043188 | 0.068665 | 0.091553 | -0.1236 | 0.022888 | -0.013733 | 0.041199 | -0.16479 | 0.1236 | 0.004578 | -1.1719 | 0.91095 | -121.2341 | 1.1032 | 1.0574 | -121.3394 | -0.13733 | -121.3211 | 0.19226 | 0.86975 | 1.1581 | 1.0208 | 1.1261 | 1.1032 | 1.0391 | 1.0757 | -0.13733 | 1.1261 | 1.1032 | 1.0757 | 1.0208 | 1.0391 | -121.4493 | -122.4976
2366.3594 | 122.4335 | -1.0712 | 121.4172 | -0.18723 | 0.015379 | -0.001788 | 0.040772 | -0.013589 | -0.0061973 | 0.041052 | -0.018311 | 0.14648 | -0.17395 | -0.10071 | -0.15564 | -0.09613 | 0.013733 | -0.036621 | 0.068665 | -1.1902 | 0.89722 | -121.2708 | 1.0529 | 0.97046 | -121.5729 | -0.11902 | -121.3486 | 0.15564 | 1.0849 | 1.0345 | 0.91553 | 1.2177 | 1.0529 | 1.1398 | 0.97504 | -0.11902 | 1.2177 | 1.0529 | 0.97504 | 0.91553 | 1.1398 | -121.5912 | -122.6074
2367.3438 | 122.4197 | -1.0437 | 121.4447 | -0.21011 | 0.014097 | -0.0077694 | 0.04184 | -0.011666 | -0.0070517 | 0.042334 | -0.009155 | 0.13733 | -0.1831 | -0.10986 | -0.14648 | -0.054932 | 0.35706 | -0.036621 | 0.073242 | -1.1627 | 0.8606 | -121.3074 | 1.0345 | 0.93384 | -121.5912 | -0.11902 | -121.3715 | 0.17395 | 1.4008 | 1.0071 | 0.89722 | 1.181 | 1.0345 | 1.1169 | 0.98877 | -0.11902 | 1.181 | 1.0345 | 0.98877 | 0.89722 | 1.1169 | -121.6278 | -122.6074
2368.3438 | 122.525 | -1.0529 | 121.3898 | 0.21713 | 0.017729 | -0.0049924 | 0.044617 | -0.0091024 | -0.0049155 | 0.041052 | 0.050354 | 0.086975 | -0.19226 | -0.054932 | -0.086975 | -0.045776 | -0.1831 | 0.018311 | 0.022888 | -1.1719 | 0.86059 | -121.3028 | 1.1032 | 0.99792 | -121.4767 | -0.11902 | -121.3669 | 0.24261 | 0.86975 | 1.0712 | 0.96588 | 1.1398 | 1.1032 | 1.0757 | 1.0071 | -0.11902 | 1.1398 | 1.1032 | 1.0071 | 0.96588 | 1.0757 | -121.582 | -122.5616
2369.3438 | 122.4426 | -1.0437 | 121.376 | -0.088043 | 0.01367 | -0.0049924 | 0.036713 | -0.012307 | -0.0047019 | 0.043615 | 0.07782 | 0.064087 | -0.13275 | 0.041199 | 0 | 0.032043 | -0.14648 | 0.17395 | 0.013733 | -1.1719 | 0.91095 | -121.312 | 1.1215 | 1.0849 | -121.376 | -0.12817 | -121.3623 | 0.21057 | 0.89722 | 1.2177 | 1.0437 | 1.1078 | 1.1215 | 1.0574 | 1.0757 | -0.12817 | 1.1078 | 1.1215 | 1.0757 | 1.0437 | 1.0574 | -121.5088 | -122.5479
2370.3594 | 122.3145 | -1.0162 | 121.3898 | -0.13382 | 0.013243 | -0.0058468 | 0.035859 | -0.015084 | -0.0059835 | 0.044256 | 0.086975 | 0.082397 | -0.14191 | 0.027466 | 0.004578 | 0.050354 | -0.1831 | 0.13733 | 0.013733 | -1.149 | 0.87433 | -121.3074 | 1.1032 | 1.0437 | -121.3852 | -0.13275 | -121.376 | 0.22888 | 0.83313 | 1.1536 | 1.0208 | 1.0986 | 1.1032 | 1.03 | 1.0666 | -0.13275 | 1.0986 | 1.1032 | 1.0666 | 1.0208 | 1.03 | -121.5317 | -122.5388
2371.3438 | 122.4472 | -1.0757 | 121.4081 | 0.049286 | 0.016447 | -0.0024288 | 0.044617 | -0.009957 | -0.0072653 | 0.041266 | 0.027466 | 0.11444 | -0.20142 | -0.068665 | -0.14191 | -0.09613 | -0.07782 | -0.054932 | 0.027466 | -1.2085 | 0.87433 | -121.2936 | 1.1032 | 1.0071 | -121.55 | -0.13275 | -121.3806 | 0.22888 | 0.99792 | 1.0208 | 0.93384 | 1.1902 | 1.1032 | 1.1032 | 0.97961 | -0.13275 | 1.1902 | 1.1032 | 0.97961 | 0.93384 | 1.1032 | -121.6095 | -122.6166
2372.3594 | 122.5113 | -1.0529 | 121.3806 | 0.079804 | 0.013883 | -0.0039242 | 0.0365 | -0.01188 | -0.0081199 | 0.04447 | -0.004578 | 0.064087 | -0.1831 | -0.054932 | -0.073242 | -0.013733 | -0.13733 | 0.018311 | 0.041199 | -1.181 | 0.86975 | -121.3165 | 1.0483 | 0.99792 | -121.4539 | -0.12817 | -121.3394 | 0.17853 | 0.91553 | 1.0712 | 0.97961 | 1.1169 | 1.0483 | 1.0941 | 1.0391 | -0.12817 | 1.1169 | 1.0483 | 1.0391 | 0.97961 | 1.0941 | -121.5637 | -122.5616
2373.3438 | 122.5342 | -1.0529 | 121.3852 | 0.011139 | 0.014311 | -0.001788 | 0.0365 | -0.011239 | -0.0074789 | 0.041693 | 0.018311 | 0.068665 | -0.16479 | -0.041199 | -0.073242 | -0.004578 | -0.14191 | 0.032043 | 0.027466 | -1.181 | 0.88806 | -121.3165 | 1.0712 | 1.0117 | -121.4584 | -0.12817 | -121.3577 | 0.18311 | 0.91095 | 1.0849 | 0.97961 | 1.1215 | 1.0712 | 1.0803 | 1.0483 | -0.12817 | 1.1215 | 1.0712 | 1.0483 | 0.97961 | 1.0803 | -121.55 | -122.5662
2374.3594 | 122.5479 | -1.062 | 121.4172 | 0.041657 | 0.014738 | -0.005206 | 0.038422 | -0.013589 | -0.0040609 | 0.041266 | 0 | 0.064087 | -0.15564 | -0.041199 | -0.09613 | -0.022888 | -0.15564 | 0.018311 | 0.018311 | -1.1856 | 0.90637 | -121.3531 | 1.062 | 1.0208 | -121.5134 | -0.1236 | -121.3989 | 0.15564 | 0.90637 | 1.0803 | 0.96588 | 1.1261 | 1.062 | 1.0803 | 1.0391 | -0.1236 | 1.1261 | 1.062 | 1.0391 | 0.96588 | 1.0803 | -121.5729 | -122.6028
2375.3438 | 122.5754 | -1.0437 | 121.3898 | -0.11856 | 0.012388 | -0.010119 | 0.0365 | -0.011025 | -0.0021383 | 0.043188 | 0.09613 | 0.10071 | -0.14191 | 0.013733 | -0.054932 | -0.009155 | -0.17395 | 0.050354 | -0.009155 | -1.1902 | 0.90179 | -121.2891 | 1.1398 | 1.0574 | -121.4447 | -0.14648 | -121.3989 | 0.23804 | 0.86975 | 1.0941 | 0.98877 | 1.1444 | 1.1398 | 1.0345 | 1.0345 | -0.14648 | 1.1444 | 1.1398 | 1.0345 | 0.98877 | 1.0345 | -121.5317 | -122.58
2376.3438 | 122.5296 | -1.062 | 121.4172 | -0.18723 | 0.014097 | -0.0054196 | 0.04184 | -0.012948 | -0.0047019 | 0.040838 | 0.073242 | 0.086975 | -0.13733 | -0.013733 | -0.073242 | -0.036621 | -0.086975 | 0.054932 | 0.009155 | -1.2177 | 0.92468 | -121.3303 | 1.1353 | 1.0483 | -121.4905 | -0.15564 | -121.4081 | 0.21057 | 0.97504 | 1.1169 | 0.98877 | 1.149 | 1.1353 | 1.0712 | 1.0254 | -0.15564 | 1.149 | 1.1353 | 1.0254 | 0.98877 | 1.0712 | -121.5546 | -122.6349
2377.3438 | 122.5204 | -1.1032 | 121.3394 | 0.10269 | 0.01602 | -0.007983 | 0.038209 | -0.012948 | -0.0068381 | 0.042761 | 0.032043 | 0.086975 | -0.16479 | -0.041199 | -0.07782 | -0.032043 | -0.14648 | -0.009155 | 0.004578 | -1.2039 | 0.93841 | -121.2524 | 1.1353 | 1.062 | -121.4172 | -0.10071 | -121.3348 | 0.19684 | 0.95673 | 1.0941 | 1.0254 | 1.1902 | 1.1353 | 1.1078 | 1.0712 | -0.10071 | 1.1902 | 1.1353 | 1.0712 | 1.0254 | 1.1078 | -121.5042 | -122.5433
2378.3438 | 122.5479 | -1.0895 | 121.4035 | 0.4155 | 0.014738 | -0.0020016 | 0.039918 | -0.011666 | -0.0044883 | 0.039984 | 0.032043 | 0.027466 | -0.20599 | -0.07782 | -0.10071 | -0.054932 | -0.15106 | 0.009155 | -0.041199 | -1.2085 | 0.88348 | -121.376 | 1.1215 | 1.0117 | -121.5042 | -0.11902 | -121.4447 | 0.23804 | 0.93842 | 1.0986 | 0.98877 | 1.1169 | 1.1215 | 1.0483 | 1.0345 | -0.11902 | 1.1169 | 1.1215 | 1.0345 | 0.98877 | 1.0483 | -121.6095 | -122.612
2379.3594 | 122.4289 | -1.0483 | 121.5775 | -0.080414 | 0.015592 | -0.0064878 | 0.046967 | -0.012093 | -0.0057699 | 0.03977 | 0.068665 | 0.10986 | -0.17853 | -0.032043 | -0.09613 | -0.07782 | -0.091553 | -0.004578 | 0.018311 | -1.2268 | 0.86975 | -121.4676 | 1.1169 | 1.0162 | -121.6736 | -0.17853 | -121.5591 | 0.24719 | 0.95673 | 1.0437 | 0.95215 | 1.1581 | 1.1169 | 1.0666 | 0.97046 | -0.17853 | 1.1581 | 1.1169 | 0.97046 | 0.95215 | 1.0666 | -121.756 | -122.8043
2380.3438 | 122.58 | -1.0574 | 121.3989 | 0.2095 | 0.017088 | -0.005206 | 0.043336 | -0.009316 | -0.0042747 | 0.043615 | 0.09613 | 0.09613 | -0.16479 | 0.004578 | -0.036621 | 0.022888 | -0.21973 | 0.041199 | -0.018311 | -1.1856 | 0.89264 | -121.3028 | 1.1536 | 1.062 | -121.4355 | -0.12817 | -121.4172 | 0.26092 | 0.83771 | 1.0986 | 1.0208 | 1.1536 | 1.1536 | 1.0391 | 1.0803 | -0.12817 | 1.1536 | 1.1536 | 1.0803 | 1.0208 | 1.0391 | -121.5637 | -122.5845
2381.3438 | 122.5937 | -1.0391 | 121.3898 | 0.26291 | 0.015592 | -0.0056332 | 0.045685 | -0.0088888 | -0.0042747 | 0.043188 | 0.068665 | 0.086975 | -0.16937 | 0 | -0.050354 | 0.009155 | -0.21515 | 0.013733 | -0.018311 | -1.1948 | 0.86975 | -121.3028 | 1.1078 | 1.0391 | -121.4401 | -0.15564 | -121.4081 | 0.23804 | 0.82397 | 1.0529 | 0.98877 | 1.1261 | 1.1078 | 1.0208 | 1.0483 | -0.15564 | 1.1261 | 1.1078 | 1.0483 | 0.98877 | 1.0208 | -121.5591 | -122.5845
2382.3438 | 122.5983 | -1.0208 | 121.4035 | 0.17136 | 0.014952 | -0.0041378 | 0.03949 | -0.009957 | -0.0057699 | 0.042761 | 0.086975 | 0.10071 | -0.14648 | -0.004578 | -0.041199 | 0.013733 | -0.21973 | 0.027466 | -0.022888 | -1.1581 | 0.87433 | -121.3028 | 1.1078 | 1.0162 | -121.4447 | -0.13733 | -121.4264 | 0.23346 | 0.80109 | 1.0483 | 0.97961 | 1.1215 | 1.1078 | 0.99792 | 1.0345 | -0.13733 | 1.1215 | 1.1078 | 1.0345 | 0.97961 | 0.99792 | -121.55 | -122.5616
2383.3594 | 122.4792 | -1.0803 | 121.4218 | -0.35507 | 0.016661 | -0.00029261 | 0.044404 | -0.0088888 | -0.0044883 | 0.040838 | 0 | 0.14191 | -0.1831 | -0.11902 | -0.15564 | -0.11444 | -0.073242 | -0.10071 | 0.032043 | -1.2222 | 0.89722 | -121.2799 | 1.0803 | 0.9613 | -121.5775 | -0.14191 | -121.3898 | 0.1831 | 1.0071 | 0.97961 | 0.92468 | 1.2222 | 1.0803 | 1.1124 | 0.96588 | -0.14191 | 1.2222 | 1.0803 | 0.96588 | 0.92468 | 1.1124 | -121.6049 | -122.644
2384.3438 | 122.5708 | -1.0391 | 121.4493 | 0.16373 | 0.014952 | -0.0064878 | 0.03949 | -0.009316 | -0.0057699 | 0.042975 | 0.064087 | 0.073242 | -0.14191 | -0.022888 | -0.064087 | -0.004578 | -0.17395 | 0.009155 | 0.004578 | -1.1627 | 0.89722 | -121.376 | 1.1032 | 1.0162 | -121.5134 | -0.1236 | -121.4447 | 0.20599 | 0.86517 | 1.0483 | 0.97504 | 1.1124 | 1.1032 | 1.0437 | 1.0345 | -0.1236 | 1.1124 | 1.1032 | 1.0345 | 0.97504 | 1.0437 | -121.5912 | -122.612
2385.3594 | 122.5479 | -1.062 | 121.463 | -0.14908 | 0.018156 | -0.0028562 | 0.044404 | -0.01188 | -0.0059835 | 0.042761 | 0.050354 | 0.12817 | -0.19226 | -0.045776 | -0.091553 | -0.068665 | -0.07782 | -0.027466 | 0.009155 | -1.2039 | 0.86975 | -121.3348 | 1.1124 | 1.0162 | -121.5546 | -0.14191 | -121.4539 | 0.24261 | 0.98419 | 1.0345 | 0.97046 | 1.1902 | 1.1124 | 1.0712 | 0.99335 | -0.14191 | 1.1902 | 1.1124 | 0.99335 | 0.97046 | 1.0712 | -121.6553 | -122.6669
2386.3281 | 122.5388 | -1.0849 | 121.4218 | 0.18662 | 0.01901 | -0.0060604 | 0.042054 | -0.006539 | -0.0051291 | 0.042975 | -0.004578 | 0.14191 | -0.18768 | -0.11902 | -0.14648 | -0.10071 | -0.091553 | -0.09613 | 0.018311 | -1.2222 | 0.89722 | -121.2799 | 1.0803 | 0.96588 | -121.5683 | -0.13733 | -121.4035 | 0.1831 | 0.99335 | 0.98877 | 0.93842 | 1.2268 | 1.0803 | 1.1032 | 0.98419 | -0.13733 | 1.2268 | 1.0803 | 0.98419 | 0.93842 | 1.1032 | -121.6095 | -122.644
2387.3594 | 122.5342 | -1.0803 | 121.4493 | 0.034027 | 0.015806 | -0.001788 | 0.045258 | -0.0084616 | -0.0059835 | 0.044043 | 0.050354 | 0.11444 | -0.19684 | -0.054932 | -0.10986 | -0.064087 | -0.086975 | -0.045776 | 0 | -1.2177 | 0.88348 | -121.3348 | 1.1307 | 1.0254 | -121.5591 | -0.13733 | -121.4493 | 0.24719 | 0.99335 | 1.0345 | 0.97046 | 1.1948 | 1.1307 | 1.0803 | 1.0162 | -0.13733 | 1.1948 | 1.1307 | 1.0162 | 0.97046 | 1.0803 | -121.6461 | -122.6669
2388.3438 | 122.6166 | -1.0437 | 121.4218 | 0.17899 | 0.014738 | -0.0024288 | 0.038636 | -0.0080344 | -0.0049155 | 0.043188 | 0.07782 | 0.050354 | -0.17853 | -0.004578 | -0.036621 | 0.022888 | -0.24261 | 0.032043 | -0.032043 | -1.1627 | 0.86517 | -121.3715 | 1.1215 | 1.0391 | -121.4584 | -0.11902 | -121.4539 | 0.25635 | 0.80109 | 1.0757 | 1.0071 | 1.0941 | 1.1215 | 1.0117 | 1.0666 | -0.11902 | 1.0941 | 1.1215 | 1.0666 | 1.0071 | 1.0117 | -121.6003 | -122.5845
2389.3438 | 122.5159 | -1.1032 | 121.4447 | -0.027008 | 0.014097 | -0.0077694 | 0.040131 | -0.009316 | -0.0076925 | 0.041906 | -0.036621 | 0.16022 | -0.15564 | -0.10986 | -0.13733 | -0.091553 | 0.009155 | -0.045776 | 0.041199 | -1.2222 | 0.94757 | -121.2845 | 1.0666 | 0.99335 | -121.582 | -0.11902 | -121.4035 | 0.11902 | 1.1124 | 1.0574 | 0.96588 | 1.2634 | 1.0666 | 1.1444 | 1.0117 | -0.11902 | 1.2634 | 1.0666 | 1.0117 | 0.96588 | 1.1444 | -121.6003 | -122.6669
2390.3281 | 122.6349 | -1.0574 | 121.4218 | 0.2095 | 0.014738 | -0.003497 | 0.039063 | -0.0095296 | -0.0047019 | 0.04212 | 0.07782 | 0.064087 | -0.12817 | -0.004578 | -0.032043 | 0.022888 | -0.21973 | 0.032043 | -0.013733 | -1.1856 | 0.92926 | -121.3577 | 1.1353 | 1.0529 | -121.4539 | -0.12817 | -121.4355 | 0.20599 | 0.83771 | 1.0895 | 1.0254 | 1.1215 | 1.1353 | 1.0437 | 1.0803 | -0.12817 | 1.1215 | 1.1353 | 1.0803 | 1.0254 | 1.0437 | -121.55 | -122.6074
2391.3438 | 122.6257 | -1.0529 | 121.4127 | 0.23239 | 0.015592 | -0.0045652 | 0.04184 | -0.0095296 | -0.0057699 | 0.042761 | 0.064087 | 0.10529 | -0.17853 | -0.022888 | -0.064087 | 0.004578 | -0.19684 | 0.004578 | -0.018311 | -1.1993 | 0.87433 | -121.3074 | 1.1169 | 1.03 | -121.4767 | -0.14648 | -121.431 | 0.24261 | 0.85602 | 1.0574 | 0.98877 | 1.1581 | 1.1169 | 1.0345 | 1.0574 | -0.14648 | 1.1581 | 1.1169 | 1.0574 | 0.98877 | 1.0345 | -121.5912 | -122.612
2392.3438 | 122.6212 | -1.0986 | 121.3943 | 0.22476 | 0.01602 | -0.0077694 | 0.041413 | -0.010598 | -0.0051291 | 0.042334 | 0.10071 | 0.086975 | -0.16479 | -0.018311 | -0.027466 | -0.20142 | -0.3479 | 0.12817 | -0.059509 | -1.2405 | 0.93384 | -121.3074 | 1.1993 | 1.0803 | -121.4218 | -0.14191 | -121.4539 | 0.2655 | 0.75073 | 1.2268 | 1.0712 | 1.1856 | 1.1993 | 1.0391 | 0.89722 | -0.14191 | 1.1856 | 1.1993 | 0.89722 | 1.0712 | 1.0391 | -121.5591 | -122.6349
2393.3281 | 122.6074 | -1.0895 | 121.4401 | 0.18662 | 0.013883 | -0.0064878 | 0.037354 | -0.011025 | -0.0047019 | 0.041479 | 0.041199 | 0.10071 | -0.15564 | -0.050354 | -0.082397 | -0.013733 | -0.16479 | 0.013733 | -0.009155 | -1.1993 | 0.93384 | -121.3394 | 1.1307 | 1.0391 | -121.5225 | -0.10986 | -121.4493 | 0.19684 | 0.92468 | 1.1032 | 1.0071 | 1.1902 | 1.1307 | 1.0803 | 1.0757 | -0.10986 | 1.1902 | 1.1307 | 1.0757 | 1.0071 | 1.0803 | -121.5958 | -122.6395
2394.3438 | 122.58 | -1.1169 | 121.4355 | 0.12558 | 0.014311 | -0.007983 | 0.048463 | -0.009957 | -0.0064109 | 0.044684 | 0.11902 | 0.19226 | -0.07782 | -0.022888 | -0.09613 | -0.054932 | -0.10071 | -0.009155 | 0.004578 | -1.2222 | 1.0391 | -121.2433 | 1.236 | 1.0941 | -121.5317 | -0.10529 | -121.431 | 0.19684 | 1.0162 | 1.1078 | 1.0208 | 1.3092 | 1.236 | 1.1215 | 1.062 | -0.10529 | 1.3092 | 1.236 | 1.062 | 1.0208 | 1.1215 | -121.5134 | -122.6578
2395.3438 | 122.5433 | -1.1307 | 121.4859 | 0.072174 | 0.015165 | -0.0058468 | 0.045899 | -0.0078206 | -0.0089743 | 0.044684 | -0.004578 | 0.11902 | -0.19684 | -0.10529 | -0.16022 | -0.13275 | -0.073242 | -0.086975 | 0.004578 | -1.2314 | 0.93384 | -121.3669 | 1.1261 | 1.0254 | -121.6461 | -0.10071 | -121.4813 | 0.19226 | 1.0574 | 1.0437 | 0.97046 | 1.2497 | 1.1261 | 1.1353 | 0.99792 | -0.10071 | 1.2497 | 1.1261 | 0.99792 | 0.97046 | 1.1353 | -121.6827 | -122.7173
2396.3438 | 122.5708 | -1.1307 | 121.431 | -0.14908 | 0.017729 | -0.005206 | 0.041627 | -0.0078206 | -0.0079061 | 0.043615 | 0.004578 | 0.10071 | -0.20142 | -0.064087 | -0.11444 | -0.082397 | -0.064087 | -0.036621 | 0.013733 | -1.2543 | 0.92926 | -121.3303 | 1.1353 | 1.0666 | -121.5454 | -0.1236 | -121.4172 | 0.20599 | 1.0666 | 1.0941 | 1.0162 | 1.2314 | 1.1353 | 1.1444 | 1.0483 | -0.1236 | 1.2314 | 1.1353 | 1.0483 | 1.0162 | 1.1444 | -121.6324 | -122.6852
2397.3281 | 122.6074 | -1.1078 | 121.463 | -0.12619 | 0.015806 | -0.0049924 | 0.041199 | -0.0088888 | -0.0091879 | 0.039343 | 0.018311 | 0.1236 | -0.19226 | -0.073242 | -0.11444 | -0.07782 | -0.064087 | -0.032043 | -0.018311 | -1.2451 | 0.91553 | -121.3394 | 1.1261 | 1.0345 | -121.5775 | -0.13733 | -121.4813 | 0.21057 | 1.0437 | 1.0757 | 0.99335 | 1.2314 | 1.1261 | 1.0895 | 1.03 | -0.13733 | 1.2314 | 1.1261 | 1.03 | 0.99335 | 1.0895 | -121.6553 | -122.7081
2398.3281 | 122.5845 | -1.1215 | 121.5042 | -0.1033 | 0.015806 | -0.0056332 | 0.042481 | -0.009957 | -0.0083335 | 0.042334 | 0.045776 | 0.082397 | -0.18768 | -0.073242 | -0.10986 | -0.059509 | -0.091553 | -0.032043 | 0 | -1.2314 | 0.93384 | -121.4218 | 1.1673 | 1.0483 | -121.6141 | -0.10986 | -121.5042 | 0.23346 | 1.03 | 1.0895 | 1.0117 | 1.2039 | 1.1673 | 1.1215 | 1.062 | -0.10986 | 1.2039 | 1.1673 | 1.062 | 1.0117 | 1.1215 | -121.6919 | -122.7356
2399.3281 | 122.6028 | -1.0712 | 121.4996 | -0.065155 | 0.014524 | -0.0047788 | 0.042054 | -0.0091024 | -0.0066245 | 0.044043 | 0.27924 | 0.11444 | -0.13733 | -0.032043 | -0.068665 | -0.045776 | -0.054932 | 0.032043 | 0.064087 | -1.1856 | 0.93384 | -121.3852 | 1.3504 | 1.0391 | -121.5683 | -0.11444 | -121.4355 | 0.41656 | 1.0162 | 1.1032 | 1.0025 | 1.1856 | 1.3504 | 1.1353 | 1.0254 | -0.11444 | 1.1856 | 1.3504 | 1.0254 | 1.0025 | 1.1353 | -121.637 | -122.6852
2400.3438 | 122.6486 | -1.0895 | 121.4493 | 0.11032 | 0.015592 | -0.006915 | 0.034577 | -0.010598 | -0.0057699 | 0.043615 | 0.009155 | 0.045776 | -0.17395 | -0.082397 | -0.10529 | -0.032043 | -0.12817 | -0.004578 | 0 | -1.2085 | 0.91553 | -121.4035 | 1.0986 | 1.0071 | -121.5546 | -0.11902 | -121.4493 | 0.1831 | 0.9613 | 1.0849 | 0.98419 | 1.1353 | 1.0986 | 1.0895 | 1.0574 | -0.11902 | 1.1353 | 1.0986 | 1.0574 | 0.98419 | 1.0895 | -121.6232 | -122.6578
2401.3281 | 122.5571 | -1.1353 | 121.4813 | -0.18723 | 0.016233 | -0.0064878 | 0.042481 | -0.010598 | -0.0066245 | 0.041906 | -0.018311 | 0.11444 | -0.19684 | -0.10986 | -0.15106 | -0.10986 | -0.013733 | -0.059509 | 0 | -1.2497 | 0.93842 | -121.3669 | 1.1169 | 1.0254 | -121.6324 | -0.11444 | -121.4813 | 0.17853 | 1.1215 | 1.0757 | 0.98419 | 1.2497 | 1.1169 | 1.1353 | 1.0254 | -0.11444 | 1.2497 | 1.1169 | 1.0254 | 0.98419 | 1.1353 | -121.6782 | -122.731
2402.3438 | 122.6624 | -1.1215 | 121.4355 | -0.1796 | 0.014311 | -0.0056332 | 0.038636 | -0.013375 | -0.0053427 | 0.042334 | 0.064087 | 0.091553 | -0.16022 | -0.045776 | -0.054932 | -0.018311 | -0.091553 | 0.032043 | -0.018311 | -1.2451 | 0.9613 | -121.344 | 1.1856 | 1.0757 | -121.4905 | -0.1236 | -121.4539 | 0.2243 | 1.03 | 1.1536 | 1.0666 | 1.2131 | 1.1856 | 1.1032 | 1.1032 | -0.1236 | 1.2131 | 1.1856 | 1.1032 | 1.0666 | 1.1032 | -121.5958 | -122.6807
2403.3281 | 122.6212 | -1.1124 | 121.4539 | -0.065155 | 0.015165 | -0.0024288 | 0.044404 | -0.0097434 | -0.0081199 | 0.04212 | 0.036621 | 0.10071 | -0.19226 | 0.009155 | -0.054932 | -0.054932 | -0.050354 | 0.018311 | 0.050354 | -1.2085 | 0.9201 | -121.3531 | 1.149 | 1.1215 | -121.5088 | -0.09613 | -121.4035 | 0.22888 | 1.062 | 1.1307 | 1.0574 | 1.2131 | 1.149 | 1.1627 | 1.0574 | -0.09613 | 1.2131 | 1.149 | 1.0574 | 1.0574 | 1.1627 | -121.6461 | -122.6624
2404.3594 | 122.5754 | -1.1536 | 121.4447 | -0.1796 | 0.016447 | -0.0060604 | 0.040345 | -0.010598 | -0.0066245 | 0.042547 | -0.013733 | 0.10986 | -0.20142 | -0.10071 | -0.16022 | -0.10529 | -0.013733 | -0.068665 | 0.004578 | -1.268 | 0.95215 | -121.3348 | 1.1398 | 1.0529 | -121.6049 | -0.11444 | -121.4401 | 0.18768 | 1.1398 | 1.0849 | 0.99335 | 1.2634 | 1.1398 | 1.1581 | 1.0483 | -0.11444 | 1.2634 | 1.1398 | 1.0483 | 0.99335 | 1.1581 | -121.6461 | -122.7127
2405.3281 | 122.5891 | -1.1719 | 121.4401 | -0.0041198 | 0.016447 | -0.0013608 | 0.042054 | -0.007607 | -0.0085471 | 0.04447 | 0.018311 | 0.10071 | -0.17853 | -0.082397 | -0.13733 | -0.09613 | -0.082397 | -0.059509 | 0 | -1.268 | 0.99335 | -121.3394 | 1.1902 | 1.0895 | -121.5775 | -0.09613 | -121.4401 | 0.19684 | 1.0895 | 1.1124 | 1.0345 | 1.2726 | 1.1902 | 1.1719 | 1.0757 | -0.09613 | 1.2726 | 1.1902 | 1.0757 | 1.0345 | 1.1719 | -121.6187 | -122.7081
2406.3594 | 122.5754 | -1.1353 | 121.4539 | -0.19485 | 0.014952 | -0.012042 | 0.039918 | -0.0095296 | -0.0087607 | 0.038916 | -0.013733 | 0.1236 | -0.20142 | 0.13275 | -0.045776 | -0.10986 | -0.050354 | -0.027466 | 0.064087 | -1.2497 | 0.93384 | -121.3303 | 1.1215 | 1.268 | -121.4996 | -0.11444 | -121.3898 | 0.18768 | 1.0849 | 1.1078 | 1.0895 | 1.2589 | 1.1215 | 1.1993 | 1.0254 | -0.11444 | 1.2589 | 1.1215 | 1.0254 | 1.0895 | 1.1993 | -121.6553 | -122.7036
2407.3281 | 122.7081 | -1.1307 | 121.3989 | -0.042267 | 0.012388 | -0.0067014 | 0.035645 | -0.0097434 | -0.0076925 | 0.044043 | 0.068665 | 0.091553 | -0.14648 | 0 | -0.032043 | 0.036621 | -0.19684 | 0.091553 | -0.013733 | -1.2451 | 0.98419 | -121.3074 | 1.1993 | 1.1307 | -121.431 | -0.11444 | -121.4127 | 0.21515 | 0.93384 | 1.2222 | 1.0986 | 1.2222 | 1.1993 | 1.1169 | 1.1673 | -0.11444 | 1.2222 | 1.1993 | 1.1673 | 1.0986 | 1.1169 | -121.5454 | -122.644
2408.3594 | 122.5616 | -1.1307 | 121.4951 | -0.17197 | 0.013456 | -0.0062742 | 0.03885 | -0.011452 | -0.010256 | 0.040411 | -0.018311 | 0.10529 | -0.21057 | -0.032043 | -0.16479 | -0.16022 | 0.032043 | -0.036621 | 0.064087 | -1.2772 | 0.9201 | -121.3898 | 1.1124 | 1.0986 | -121.6599 | -0.14648 | -121.431 | 0.19226 | 1.1627 | 1.0941 | 0.96588 | 1.236 | 1.1124 | 1.1948 | 0.97046 | -0.14648 | 1.236 | 1.1124 | 0.97046 | 0.96588 | 1.1948 | -121.7056 | -122.7722
2409.3281 | 122.6166 | -1.1673 | 121.3211 | 0.11032 | 0.014311 | -0.005206 | 0.036927 | -0.0091024 | -0.0051291 | 0.042975 | 0.027466 | 0.086975 | -0.15106 | -0.086975 | -0.10071 | -0.036621 | -0.15106 | -0.022888 | -0.018311 | -1.268 | 1.0162 | -121.2341 | 1.1948 | 1.0803 | -121.4218 | -0.10071 | -121.3394 | 0.17853 | 1.0162 | 1.1444 | 1.0666 | 1.2543 | 1.1948 | 1.149 | 1.1307 | -0.10071 | 1.2543 | 1.1948 | 1.1307 | 1.0666 | 1.149 | -121.4722 | -122.5891
2410.3281 | 122.6532 | -1.1719 | 121.3852 | 0.17136 | 0.015592 | -0.0075558 | 0.039704 | -0.010811 | -0.0029929 | 0.042547 | 0.041199 | 0.10529 | -0.14191 | -0.054932 | -0.10529 | -0.018311 | -0.16937 | -0.009155 | -0.013733 | -1.2634 | 1.03 | -121.2799 | 1.2131 | 1.1169 | -121.4905 | -0.091553 | -121.3989 | 0.18311 | 1.0025 | 1.1627 | 1.0666 | 1.2772 | 1.2131 | 1.1581 | 1.1536 | -0.091553 | 1.2772 | 1.2131 | 1.1536 | 1.0666 | 1.1581 | -121.5271 | -122.6486
2411.3281 | 122.6944 | -1.1353 | 121.3898 | -0.080414 | 0.013029 | -0.0060604 | 0.03949 | -0.01252 | -0.0068381 | 0.040625 | 0.091553 | 0.086975 | -0.14191 | 0.022888 | -0.022888 | 0.027466 | -0.1831 | 0.10529 | -0.036621 | -1.2909 | 0.99335 | -121.3028 | 1.2268 | 1.1581 | -121.4127 | -0.15564 | -121.4264 | 0.23346 | 0.95215 | 1.2405 | 1.1124 | 1.2222 | 1.2268 | 1.0986 | 1.1627 | -0.15564 | 1.2222 | 1.2268 | 1.1627 | 1.1124 | 1.0986 | -121.5317 | -122.6807
2412.3281 | 122.731 | -1.1444 | 121.376 | 0.5986 | 0.014524 | -0.0073422 | 0.038422 | -0.012734 | -0.0079061 | 0.042547 | 0.045776 | 0.054932 | -0.17395 | 0 | -0.045776 | 0.009155 | -0.17853 | 0.068665 | -0.050354 | -1.2909 | 0.97046 | -121.3211 | 1.1902 | 1.1444 | -121.4218 | -0.14648 | -121.4264 | 0.21973 | 0.96588 | 1.2131 | 1.0986 | 1.1993 | 1.1902 | 1.0941 | 1.1536 | -0.14648 | 1.1993 | 1.1902 | 1.1536 | 1.0986 | 1.0941 | -121.55 | -122.6669
2413.3438 | 122.6624 | -1.1719 | 121.4584 | 0.095062 | 0.015806 | -0.0060604 | 0.046113 | -0.010171 | -0.0059835 | 0.042761 | 0.022888 | 0.14191 | -0.19684 | -0.13275 | -0.20142 | -0.15106 | -0.064087 | -0.11902 | -0.013733 | -1.3275 | 0.97504 | -121.3165 | 1.1948 | 1.0391 | -121.6599 | -0.15564 | -121.4722 | 0.21973 | 1.1078 | 1.0529 | 0.97046 | 1.3138 | 1.1948 | 1.1581 | 1.0208 | -0.15564 | 1.3138 | 1.1948 | 1.0208 | 0.97046 | 1.1581 | -121.6553 | -122.7859
2414.3281 | 122.6807 | -1.1398 | 121.4218 | 0.18662 | 0.015165 | -0.0071286 | 0.038636 | -0.0095296 | -0.0070517 | 0.043188 | 0.073242 | 0.091553 | -0.14648 | -0.013733 | -0.073242 | -0.009155 | -0.24261 | 0.009155 | -0.054932 | -1.268 | 0.99335 | -121.3303 | 1.2131 | 1.1261 | -121.4951 | -0.12817 | -121.4767 | 0.21973 | 0.89722 | 1.149 | 1.0666 | 1.2314 | 1.2131 | 1.0849 | 1.1307 | -0.12817 | 1.2314 | 1.2131 | 1.1307 | 1.0666 | 1.0849 | -121.5683 | -122.6898
2415.3438 | 122.6715 | -1.1581 | 121.3669 | 0.16373 | 0.014952 | -0.0045652 | 0.040345 | -0.011239 | -0.0049155 | 0.043188 | 0.068665 | 0.10071 | -0.14648 | -0.032043 | -0.086975 | -0.013733 | -0.19684 | 0 | -0.064087 | -1.2817 | 1.0117 | -121.2662 | 1.2268 | 1.1261 | -121.4539 | -0.1236 | -121.431 | 0.21515 | 0.9613 | 1.1581 | 1.0712 | 1.2589 | 1.2268 | 1.0941 | 1.1444 | -0.1236 | 1.2589 | 1.2268 | 1.1444 | 1.0712 | 1.0941 | -121.5134 | -122.6486
2416.3281 | 122.7356 | -1.1856 | 121.3898 | 0.24002 | 0.015165 | -0.0022152 | 0.040986 | -0.010811 | -0.0036337 | 0.043188 | -0.018311 | 0.059509 | -0.18768 | 0.013733 | -0.086975 | -0.032043 | -0.25177 | 0.004578 | -0.10071 | -1.3275 | 0.99792 | -121.3303 | 1.1673 | 1.1993 | -121.4767 | -0.14191 | -121.4905 | 0.16937 | 0.93384 | 1.1902 | 1.0986 | 1.2451 | 1.1673 | 1.0849 | 1.1536 | -0.14191 | 1.2451 | 1.1673 | 1.1536 | 1.0986 | 1.0849 | -121.5775 | -122.7173
2417.3438 | 122.6669 | -1.236 | 121.3852 | 0.10269 | 0.015379 | -0.0028562 | 0.038209 | -0.010811 | -0.0044883 | 0.041479 | 0.041199 | 0.09613 | -0.15564 | -0.064087 | -0.10986 | -0.045776 | -0.21973 | -0.17853 | -0.07782 | -1.3504 | 1.0803 | -121.2891 | 1.2772 | 1.1719 | -121.4951 | -0.11444 | -121.463 | 0.19684 | 1.0162 | 1.0574 | 1.1261 | 1.3321 | 1.2772 | 1.1581 | 1.1902 | -0.11444 | 1.3321 | 1.2772 | 1.1902 | 1.1261 | 1.1581 | -121.5408 | -122.7356
2418.3438 | 122.7219 | -1.1673 | 121.4172 | -0.034637 | 0.015379 | -0.0047788 | 0.037995 | -0.011666 | -0.0049155 | 0.040838 | 0.064087 | 0.11902 | -0.13733 | -0.022888 | -0.064087 | -0.013733 | -0.16022 | 0.032043 | -0.050354 | -1.2955 | 1.03 | -121.2982 | 1.2314 | 1.1444 | -121.4813 | -0.12817 | -121.4676 | 0.20142 | 1.0071 | 1.1993 | 1.1032 | 1.2863 | 1.2314 | 1.1169 | 1.1536 | -0.12817 | 1.2863 | 1.2314 | 1.1536 | 1.1032 | 1.1169 | -121.5546 | -122.7127
2419.3281 | 122.7173 | -1.1536 | 121.3852 | 0.18662 | 0.01602 | -0.006915 | 0.043549 | -0.012307 | -0.0036337 | 0.043188 | 0.07782 | 0.082397 | -0.15564 | -0.018311 | -0.086975 | 0.004578 | -0.20142 | 0.022888 | -0.068665 | -1.3046 | 0.99792 | -121.3028 | 1.2314 | 1.1353 | -121.4722 | -0.15106 | -121.4539 | 0.23346 | 0.95215 | 1.1765 | 1.0666 | 1.236 | 1.2314 | 1.0849 | 1.1581 | -0.15106 | 1.236 | 1.2314 | 1.1581 | 1.0666 | 1.0849 | -121.5408 | -122.6898
2420.3438 | 122.6532 | -1.1398 | 121.463 | -0.034637 | 0.017088 | -0.0043514 | 0.045899 | -0.010171 | -0.0061973 | 0.038275 | 0.073242 | 0.13275 | -0.18768 | 0.064087 | -0.041199 | -0.068665 | -0.022888 | 0.009155 | 0.027466 | -1.268 | 0.95215 | -121.3303 | 1.2131 | 1.2039 | -121.5042 | -0.12817 | -121.4355 | 0.26092 | 1.1169 | 1.149 | 1.0986 | 1.2726 | 1.2131 | 1.1673 | 1.0712 | -0.12817 | 1.2726 | 1.2131 | 1.0712 | 1.0986 | 1.1673 | -121.6507 | -122.731
2421.3281 | 122.644 | -1.2497 | 121.4127 | 0.21713 | 0.01901 | -0.0062742 | 0.043976 | -0.0091024 | -0.0027793 | 0.04447 | 0.018311 | 0.13275 | -0.19684 | -0.09613 | -0.14648 | -0.082397 | -0.14648 | -0.09613 | -0.050354 | -1.3641 | 1.0529 | -121.2799 | 1.268 | 1.1536 | -121.5591 | -0.11444 | -121.463 | 0.21515 | 1.1032 | 1.1536 | 1.1032 | 1.3824 | 1.268 | 1.1993 | 1.1673 | -0.11444 | 1.3824 | 1.268 | 1.1673 | 1.1032 | 1.1993 | -121.6095 | -122.7768
2422.3594 | 122.5937 | -1.2543 | 121.3989 | -0.19485 | 0.016447 | -0.0060604 | 0.042695 | -0.011452 | -0.0072653 | 0.043829 | -0.059509 | 0.16022 | -0.17395 | -0.091553 | -0.17853 | -0.11444 | 0.004578 | -0.068665 | 0.013733 | -1.3779 | 1.0803 | -121.2387 | 1.1948 | 1.1627 | -121.5775 | -0.1236 | -121.3852 | 0.11444 | 1.2589 | 1.1856 | 1.0757 | 1.4145 | 1.1948 | 1.268 | 1.1398 | -0.1236 | 1.4145 | 1.1948 | 1.1398 | 1.0757 | 1.268 | -121.5729 | -122.7768
2423.3281 | 122.6166 | -1.2634 | 121.376 | -0.080414 | 0.018583 | -0.0047788 | 0.042267 | -0.008248 | -0.0074789 | 0.042547 | 0.009155 | 0.16479 | -0.18768 | -0.1236 | -0.18768 | -0.11902 | -0.07782 | -0.10529 | -0.054932 | -1.4053 | 1.0757 | -121.2112 | 1.2726 | 1.1398 | -121.5637 | -0.14191 | -121.431 | 0.19684 | 1.1856 | 1.1581 | 1.0757 | 1.4282 | 1.2726 | 1.2085 | 1.1444 | -0.14191 | 1.4282 | 1.2726 | 1.1444 | 1.0757 | 1.2085 | -121.5637 | -122.7814
2424.3594 | 122.7127 | -1.2177 | 121.376 | 0.0035097 | 0.01602 | -0.0030698 | 0.035432 | -0.011025 | -0.0049155 | 0.042547 | 0.013733 | 0.086975 | -0.15564 | -0.068665 | -0.10986 | -0.036621 | -0.16022 | 0.004578 | -0.064087 | -1.3641 | 1.062 | -121.2891 | 1.2314 | 1.149 | -121.4859 | -0.14648 | -121.4401 | 0.16937 | 1.0574 | 1.2222 | 1.1078 | 1.3046 | 1.2314 | 1.1536 | 1.181 | -0.14648 | 1.3046 | 1.2314 | 1.181 | 1.1078 | 1.1536 | -121.5317 | -122.7402
2425.3281 | 122.612 | -1.2726 | 121.3623 | 0.20187 | 0.018583 | -0.0047788 | 0.044831 | -0.010811 | -0.0040609 | 0.040838 | 0.013733 | 0.15106 | -0.21057 | -0.1236 | -0.19226 | -0.13275 | -0.07782 | -0.11902 | -0.050354 | -1.4145 | 1.062 | -121.2112 | 1.2863 | 1.149 | -121.5546 | -0.14191 | -121.4127 | 0.2243 | 1.1948 | 1.1536 | 1.0803 | 1.4236 | 1.2863 | 1.2222 | 1.1398 | -0.14191 | 1.4236 | 1.2863 | 1.1398 | 1.0803 | 1.2222 | -121.5729 | -122.7768
2426.3438 | 122.6349 | -1.2817 | 121.3486 | 0.064545 | 0.016661 | -0.0015744 | 0.044404 | -0.0088888 | -0.0059835 | 0.042334 | 0.036621 | 0.14191 | -0.21057 | -0.10986 | -0.17853 | -0.11902 | -0.09613 | -0.091553 | -0.068665 | -1.4145 | 1.0712 | -121.2067 | 1.3184 | 1.1719 | -121.5271 | -0.13275 | -121.4172 | 0.24719 | 1.1856 | 1.1902 | 1.1032 | 1.4236 | 1.3184 | 1.2131 | 1.1627 | -0.13275 | 1.4236 | 1.3184 | 1.1627 | 1.1032 | 1.2131 | -121.5591 | -122.7631
2427.3438 | 122.644 | -1.2863 | 121.3715 | 0.18662 | 0.017942 | -0.0056332 | 0.042695 | -0.009316 | -0.0057699 | 0.044256 | -0.004578 | 0.1236 | -0.21057 | -0.1236 | -0.1831 | -0.10986 | -0.10986 | -0.10529 | -0.054932 | -1.4145 | 1.0757 | -121.2479 | 1.2817 | 1.1627 | -121.5546 | -0.12817 | -121.4264 | 0.20599 | 1.1765 | 1.181 | 1.1032 | 1.4099 | 1.2817 | 1.2314 | 1.1765 | -0.12817 | 1.4099 | 1.2817 | 1.1765 | 1.1032 | 1.2314 | -121.582 | -122.7859
2428.3438 | 122.7036 | -1.2955 | 121.3577 | 0.24002 | 0.017515 | -0.005206 | 0.040345 | -0.008248 | -0.0036337 | 0.042975 | 0.013733 | 0.12817 | -0.18768 | -0.07782 | -0.12817 | -0.054932 | -0.1831 | -0.054932 | -0.07782 | -1.4191 | 1.1078 | -121.2296 | 1.3092 | 1.2177 | -121.4859 | -0.1236 | -121.4355 | 0.20142 | 1.1124 | 1.2405 | 1.1673 | 1.4236 | 1.3092 | 1.2177 | 1.2405 | -0.1236 | 1.4236 | 1.3092 | 1.2405 | 1.1673 | 1.2177 | -121.5454 | -122.7768
2429.3438 | 122.7585 | -1.2543 | 121.3531 | -0.019379 | 0.012815 | -0.0037106 | 0.035004 | -0.012948 | -0.0047019 | 0.04447 | 0.045776 | 0.12817 | -0.14648 | -0.032043 | -0.064087 | 0.018311 | -0.16937 | 0.054932 | -0.041199 | -1.3733 | 1.1078 | -121.225 | 1.3 | 1.2222 | -121.4172 | -0.11902 | -121.3943 | 0.19226 | 1.0849 | 1.3092 | 1.1902 | 1.3824 | 1.3 | 1.2131 | 1.2726 | -0.11902 | 1.3824 | 1.3 | 1.2726 | 1.1902 | 1.2131 | -121.4996 | -122.7264
2430.3438 | 122.6395 | -1.3275 | 121.3348 | 0.056915 | 0.015806 | -0.0039242 | 0.042908 | -0.011452 | -0.0059835 | 0.042334 | 0.032043 | 0.14191 | -0.18768 | -0.091553 | -0.16937 | -0.10071 | -0.10529 | -0.07782 | -0.068665 | -1.4603 | 1.1398 | -121.1929 | 1.3596 | 1.236 | -121.5042 | -0.13275 | -121.4035 | 0.21973 | 1.2222 | 1.2497 | 1.1581 | 1.4694 | 1.3596 | 1.2589 | 1.2268 | -0.13275 | 1.4694 | 1.3596 | 1.2268 | 1.1581 | 1.2589 | -121.5225 | -122.7951
2431.3281 | 122.6303 | -1.3321 | 121.3303 | 0.064545 | 0.017729 | -0.0024288 | 0.042695 | -0.0084616 | -0.0034201 | 0.042334 | 0.027466 | 0.14648 | -0.19684 | -0.11902 | -0.1831 | -0.12817 | -0.082397 | -0.10529 | -0.054932 | -1.4648 | 1.1353 | -121.1838 | 1.3596 | 1.2131 | -121.5134 | -0.13275 | -121.3852 | 0.2243 | 1.2497 | 1.2268 | 1.149 | 1.4786 | 1.3596 | 1.2772 | 1.2039 | -0.13275 | 1.4786 | 1.3596 | 1.2039 | 1.149 | 1.2772 | -121.5271 | -122.7951
2432.3594 | 122.612 | -1.3 | 121.3348 | 0.17136 | 0.016661 | -0.0024288 | 0.042695 | -0.008248 | -0.0038473 | 0.043402 | -0.009155 | 0.15106 | -0.18768 | -0.16937 | -0.21973 | 0 | -0.45319 | -0.1236 | -0.027466 | -1.442 | 1.1124 | -121.1838 | 1.2909 | 1.1307 | -121.5546 | -0.14191 | -121.3623 | 0.17853 | 0.84686 | 1.1765 | 1.0803 | 1.4511 | 1.2909 | 1.2726 | 1.3 | -0.14191 | 1.4511 | 1.2909 | 1.3 | 1.0803 | 1.2726 | -121.5225 | -122.7768
2433.3281 | 122.6578 | -1.3504 | 121.2936 | 0.16373 | 0.018797 | -0.001788 | 0.044831 | -0.0061118 | -0.0047019 | 0.041906 | 0.004578 | 0.14648 | -0.20142 | -0.1236 | -0.18768 | -0.11444 | -0.10529 | -0.11902 | -0.045776 | -1.474 | 1.149 | -121.1472 | 1.355 | 1.2268 | -121.4813 | -0.1236 | -121.3394 | 0.20599 | 1.2451 | 1.2314 | 1.1627 | 1.4969 | 1.355 | 1.3046 | 1.236 | -0.1236 | 1.4969 | 1.355 | 1.236 | 1.1627 | 1.3046 | -121.4951 | -122.7676
2434.3438 | 122.7585 | -1.3184 | 121.2891 | -0.0041198 | 0.013456 | -0.0077694 | 0.031373 | -0.010811 | -0.0057699 | 0.042761 | 0.022888 | 0.1236 | -0.16022 | -0.050354 | -0.073242 | 0.004578 | -0.16022 | 0.018311 | -0.059509 | -1.4648 | 1.1581 | -121.1655 | 1.3412 | 1.268 | -121.3623 | -0.14648 | -121.3486 | 0.1831 | 1.1581 | 1.3367 | 1.2451 | 1.442 | 1.3412 | 1.2589 | 1.3229 | -0.14648 | 1.442 | 1.3412 | 1.3229 | 1.2451 | 1.2589 | -121.4493 | -122.7539
2435.3281 | 122.6486 | -1.3733 | 121.3028 | 0.041657 | 0.019438 | -0.0022152 | 0.042054 | -0.0084616 | -0.0055563 | 0.039984 | 0.032043 | 0.13733 | -0.20142 | -0.11444 | -0.20599 | -0.1236 | -0.086975 | -0.10071 | -0.082397 | -1.506 | 1.1719 | -121.1655 | 1.4053 | 1.2589 | -121.5088 | -0.13275 | -121.3852 | 0.23346 | 1.2863 | 1.2726 | 1.1673 | 1.5106 | 1.4053 | 1.2909 | 1.2497 | -0.13275 | 1.5106 | 1.4053 | 1.2497 | 1.1673 | 1.2909 | -121.5042 | -122.8088
2436.3281 | 122.6532 | -1.3824 | 121.2936 | 0.041657 | 0.019224 | -0.0032834 | 0.042695 | -0.008248 | -0.0059835 | 0.041906 | 0.022888 | 0.13733 | -0.1831 | -0.091553 | -0.17853 | -0.11444 | -0.091553 | -0.086975 | -0.050354 | -1.5106 | 1.1993 | -121.1563 | 1.4053 | 1.2909 | -121.4722 | -0.12817 | -121.344 | 0.20599 | 1.2909 | 1.2955 | 1.2039 | 1.5198 | 1.4053 | 1.3321 | 1.268 | -0.12817 | 1.5198 | 1.4053 | 1.268 | 1.2039 | 1.3321 | -121.4767 | -122.8043
2437.3281 | 122.6898 | -1.3962 | 121.2891 | 0.018768 | 0.017942 | -0.0067014 | 0.045045 | -0.008248 | -0.0049155 | 0.042334 | 0.054932 | 0.12817 | -0.1831 | -0.082397 | -0.16022 | -0.086975 | -0.10071 | -0.054932 | -0.041199 | -1.5472 | 1.2131 | -121.1609 | 1.4511 | 1.3138 | -121.4493 | -0.15106 | -121.3303 | 0.23804 | 1.2955 | 1.3412 | 1.236 | 1.5244 | 1.4511 | 1.355 | 1.3092 | -0.15106 | 1.5244 | 1.4511 | 1.3092 | 1.236 | 1.355 | -121.4722 | -122.8363
2438.3438 | 122.6486 | -1.3641 | 121.3165 | -0.27878 | 0.014524 | -0.0058468 | 0.036713 | -0.010171 | -0.0021383 | 0.042975 | -0.050354 | 0.11902 | -0.19684 | -0.13275 | -0.16479 | -0.1831 | 0.38452 | 0.013733 | -0.004578 | -1.5015 | 1.1673 | -121.1975 | 1.3138 | 1.2314 | -121.4813 | -0.13733 | -121.3211 | 0.14648 | 1.7487 | 1.3779 | 1.1993 | 1.4832 | 1.3138 | 1.3596 | 1.181 | -0.13733 | 1.4832 | 1.3138 | 1.181 | 1.1993 | 1.3596 | -121.5134 | -122.818
2439.3438 | 122.6349 | -1.4282 | 121.2891 | 0.10269 | 0.017942 | -0.0032834 | 0.042267 | -0.005898 | -0.0051291 | 0.041906 | -0.009155 | 0.11902 | -0.20599 | -0.15564 | -0.20599 | -0.14191 | -0.054932 | -0.13733 | -0.041199 | -1.5564 | 1.2222 | -121.17 | 1.4191 | 1.2726 | -121.4951 | -0.12817 | -121.3303 | 0.19684 | 1.3733 | 1.2909 | 1.2222 | 1.5472 | 1.4191 | 1.387 | 1.2863 | -0.12817 | 1.5472 | 1.4191 | 1.2863 | 1.2222 | 1.387 | -121.4951 | -122.8455
2440.3438 | 122.6715 | -1.4145 | 121.2433 | -0.13382 | 0.013456 | -0.007983 | 0.039918 | -0.0097434 | -0.0072653 | 0.042761 | -0.013733 | 0.13275 | -0.19684 | -0.12817 | -0.17853 | -0.1236 | -0.027466 | -0.07782 | -0.045776 | -1.5289 | 1.2177 | -121.1105 | 1.4008 | 1.2863 | -121.4218 | -0.11444 | -121.2891 | 0.18311 | 1.387 | 1.3367 | 1.236 | 1.5472 | 1.4008 | 1.3687 | 1.2909 | -0.11444 | 1.5472 | 1.4008 | 1.2909 | 1.236 | 1.3687 | -121.4401 | -122.7722
2441.3281 | 122.7173 | -1.387 | 121.2799 | -0.11093 | 0.016661 | -0.0022152 | 0.040772 | -0.0084616 | -0.0057699 | 0.04212 | 0.050354 | 0.13733 | -0.20142 | -0.082397 | 0 | 0.11444 | 0.10529 | 0.086975 | 0 | -1.5015 | 1.1856 | -121.1426 | 1.4374 | 1.3046 | -121.2799 | -0.11444 | -121.2799 | 0.25177 | 1.4923 | 1.474 | 1.387 | 1.5244 | 1.4374 | 1.387 | 1.5015 | -0.11444 | 1.5244 | 1.4374 | 1.5015 | 1.387 | 1.387 | -121.4813 | -122.7814
2442.3438 | 122.8088 | -1.4374 | 121.1792 | -0.072784 | 0.014311 | -0.0049924 | 0.033082 | -0.0086752 | -0.0053427 | 0.043829 | 0.068665 | 0.10071 | -0.15106 | -0.027466 | -0.07782 | 0.018311 | -0.19226 | 0.07782 | -0.064087 | -1.5518 | 1.2863 | -121.0785 | 1.506 | 1.4099 | -121.257 | -0.11444 | -121.2433 | 0.21973 | 1.2451 | 1.5152 | 1.3596 | 1.5381 | 1.506 | 1.3733 | 1.4557 | -0.11444 | 1.5381 | 1.506 | 1.4557 | 1.3596 | 1.3733 | -121.3303 | -122.731
2443.3281 | 122.699 | -1.4877 | 121.1792 | -0.31693 | 0.01837 | -0.0049924 | 0.043976 | -0.010384 | -0.0053427 | 0.042761 | 0.11444 | 0.21515 | -0.10071 | -0.059509 | -0.14191 | -0.07782 | -0.10071 | -0.027466 | -0.041199 | -1.6067 | 1.387 | -120.9641 | 1.6022 | 1.4282 | -121.3211 | -0.11902 | -121.2204 | 0.21515 | 1.387 | 1.4603 | 1.3458 | 1.7029 | 1.6022 | 1.4465 | 1.4099 | -0.11902 | 1.7029 | 1.6022 | 1.4099 | 1.3458 | 1.4465 | -121.2799 | -122.7859
2444.3438 | 122.7814 | -1.4786 | 121.17 | -0.12619 | 0.013029 | -0.0049924 | 0.036713 | -0.01188 | -0.0061973 | 0.042334 | 0.054932 | 0.10529 | -0.15564 | -0.022888 | -0.07782 | -0.018311 | -0.15106 | 0.064087 | -0.068665 | -1.5884 | 1.3229 | -121.0648 | 1.5335 | 1.4557 | -121.2479 | -0.10986 | -121.2387 | 0.21057 | 1.3275 | 1.5427 | 1.4008 | 1.5839 | 1.5335 | 1.4099 | 1.4603 | -0.10986 | 1.5839 | 1.5335 | 1.4603 | 1.4008 | 1.4099 | -121.3257 | -122.7585
2445.3281 | 122.7402 | -1.4603 | 121.225 | -0.080414 | 0.018797 | -0.001788 | 0.043763 | -0.0080344 | -0.0070517 | 0.041479 | 0.045776 | 0.13275 | -0.1831 | -0.059509 | -0.16022 | 0.17853 | 0 | 0.13275 | -0.027466 | -1.5976 | 1.2772 | -121.0922 | 1.506 | 1.4008 | -121.3852 | -0.13733 | -121.2524 | 0.22888 | 1.4603 | 1.593 | 1.3 | 1.593 | 1.506 | 1.4328 | 1.6388 | -0.13733 | 1.593 | 1.506 | 1.6388 | 1.3 | 1.4328 | -121.4081 | -122.8226
2446.3438 | 122.7264 | -1.5427 | 121.1197 | -0.0041198 | 0.012602 | -0.003497 | 0.035218 | -0.01188 | -0.0053427 | 0.044256 | -0.050354 | 0.064087 | -0.2243 | -0.11902 | -0.16937 | -0.082397 | -0.15106 | -0.041199 | -0.10529 | -1.6525 | 1.3184 | -121.0556 | 1.4923 | 1.4236 | -121.2891 | -0.10986 | -121.225 | 0.17395 | 1.3916 | 1.5015 | 1.3733 | 1.6068 | 1.4923 | 1.4374 | 1.4603 | -0.10986 | 1.6068 | 1.4923 | 1.4603 | 1.3733 | 1.4374 | -121.344 | -122.7722
2447.3281 | 122.7264 | -1.5427 | 121.1609 | -0.16434 | 0.017088 | -0.0075558 | 0.044831 | -0.010598 | -0.0068381 | 0.040838 | 0.018311 | 0.12817 | -0.20142 | -0.086975 | -0.16937 | -0.10071 | -0.082397 | -0.027466 | -0.059509 | -1.6846 | 1.3412 | -121.0327 | 1.561 | 1.4557 | -121.3303 | -0.14191 | -121.2204 | 0.21973 | 1.4603 | 1.5152 | 1.3733 | 1.6708 | 1.561 | 1.4832 | 1.442 | -0.14191 | 1.6708 | 1.561 | 1.442 | 1.3733 | 1.4832 | -121.3623 | -122.8455
2448.3438 | 122.6852 | -1.5289 | 121.1838 | -0.233 | 0.014738 | -0.0088376 | 0.0365 | -0.010384 | -0.0042747 | 0.044043 | -0.018311 | 0.15564 | -0.18768 | -0.15564 | -0.15564 | -0.10071 | -0.045776 | -0.036621 | 0.013733 | -1.6617 | 1.3412 | -121.0281 | 1.5106 | 1.3733 | -121.3394 | -0.13275 | -121.17 | 0.16937 | 1.4832 | 1.4923 | 1.3733 | 1.6846 | 1.5106 | 1.5427 | 1.4282 | -0.13275 | 1.6846 | 1.5106 | 1.4282 | 1.3733 | 1.5427 | -121.3715 | -122.8455
2449.3281 | 122.7219 | -1.5518 | 121.1472 | -0.11093 | 0.017942 | -0.0037106 | 0.042481 | -0.0069662 | -0.0079061 | 0.042334 | 0.059509 | 0.1236 | -0.19684 | -0.068665 | -0.15564 | -0.10071 | -0.091553 | -0.027466 | -0.036621 | -1.6983 | 1.355 | -121.0236 | 1.6113 | 1.4832 | -121.3028 | -0.14648 | -121.1838 | 0.25635 | 1.4603 | 1.5244 | 1.3962 | 1.6754 | 1.6113 | 1.5152 | 1.4511 | -0.14648 | 1.6754 | 1.6113 | 1.4511 | 1.3962 | 1.5152 | -121.344 | -122.8455
2450.3438 | 122.7814 | -1.5701 | 121.0556 | -0.14145 | 0.0074747 | -0.0060604 | 0.035218 | -0.01252 | -0.0049155 | 0.040838 | 0.25177 | 0.086975 | -0.1831 | -0.050354 | -0.07782 | 0 | -0.16479 | 0.086975 | -0.09613 | -1.6891 | 1.387 | -120.9686 | 1.8219 | 1.5198 | -121.1334 | -0.11902 | -121.1517 | 0.43488 | 1.4053 | 1.6571 | 1.4923 | 1.6571 | 1.8219 | 1.474 | 1.5701 | -0.11902 | 1.6571 | 1.8219 | 1.5701 | 1.4923 | 1.474 | -121.2387 | -122.7448
2451.3281 | 122.7448 | -1.6251 | 121.0556 | -0.15671 | 0.016661 | -0.0064878 | 0.043763 | -0.010171 | -0.0061973 | 0.041266 | 0.013733 | 0.16479 | -0.21515 | -0.10071 | -0.18768 | -0.11444 | -0.086975 | -0.064087 | -0.045776 | -1.7487 | 1.4099 | -120.8908 | 1.6388 | 1.5244 | -121.2433 | -0.1236 | -121.1014 | 0.22888 | 1.5381 | 1.561 | 1.4374 | 1.7899 | 1.6388 | 1.5793 | 1.5106 | -0.1236 | 1.7899 | 1.6388 | 1.5106 | 1.4374 | 1.5793 | -121.2708 | -122.8043
2452.3438 | 122.7951 | -1.5976 | 121.0327 | 0.27817 | 0.014311 | -0.0067014 | 0.036072 | -0.01188 | -0.0070517 | 0.042761 | 0.050354 | 0.086975 | -0.16479 | -0.013733 | -0.086975 | 0 | -0.19226 | 0.054932 | -0.086975 | -1.7395 | 1.4328 | -120.9457 | 1.6479 | 1.5839 | -121.1197 | -0.14191 | -121.1197 | 0.21515 | 1.4053 | 1.6525 | 1.5106 | 1.6846 | 1.6479 | 1.5106 | 1.5976 | -0.14191 | 1.6846 | 1.6479 | 1.5976 | 1.5106 | 1.5106 | -121.1975 | -122.7722
2453.3281 | 122.6807 | -1.6754 | 121.0464 | -0.1796 | 0.017088 | -0.006915 | 0.042054 | -0.011239 | -0.0070517 | 0.041479 | 0.004578 | 0.14191 | -0.18768 | -0.13275 | -0.20142 | -0.13733 | -0.045776 | -0.073242 | -0.045776 | -1.799 | 1.4877 | -120.9045 | 1.68 | 1.5427 | -121.2479 | -0.1236 | -121.0922 | 0.19226 | 1.6296 | 1.6022 | 1.474 | 1.8173 | 1.68 | 1.6296 | 1.5381 | -0.1236 | 1.8173 | 1.68 | 1.5381 | 1.474 | 1.6296 | -121.2341 | -122.8455
2454.3438 | 122.8043 | -1.6388 | 121.0144 | 0.19424 | 0.016447 | -0.0067014 | 0.037141 | -0.0088888 | -0.0059835 | 0.045752 | 0.073242 | 0.10071 | -0.15106 | -0.059509 | -0.10071 | -0.027466 | -0.23804 | 0.018311 | -0.07782 | -1.7624 | 1.4877 | -120.9137 | 1.712 | 1.5793 | -121.1151 | -0.1236 | -121.0922 | 0.2243 | 1.4008 | 1.6571 | 1.5381 | 1.7395 | 1.712 | 1.561 | 1.6113 | -0.1236 | 1.7395 | 1.712 | 1.6113 | 1.5381 | 1.561 | -121.1655 | -122.7768
2455.3281 | 122.6852 | -1.7029 | 121.019 | -0.21011 | 0.015379 | -0.0090512 | 0.03949 | -0.0095296 | -0.0047019 | 0.039984 | 0.25177 | 0.16937 | -0.15564 | -0.1236 | -0.17853 | -0.11902 | -0.022888 | -0.059509 | -0.004578 | -1.8173 | 1.5472 | -120.8496 | 1.9547 | 1.5793 | -121.1975 | -0.11444 | -121.0236 | 0.40741 | 1.68 | 1.6434 | 1.5244 | 1.8723 | 1.9547 | 1.6983 | 1.5839 | -0.11444 | 1.8723 | 1.9547 | 1.5839 | 1.5244 | 1.6983 | -121.1746 | -122.8363
2456.3281 | 122.6944 | -1.7349 | 121.0052 | -0.15671 | 0.014311 | -0.0075558 | 0.040131 | -0.0084616 | -0.0079061 | 0.040838 | 0.004578 | 0.13733 | -0.19226 | -0.1236 | -0.20142 | -0.13733 | -0.036621 | -0.073242 | -0.041199 | -1.8494 | 1.5427 | -120.8679 | 1.7395 | 1.6113 | -121.2067 | -0.11444 | -121.0464 | 0.19684 | 1.6983 | 1.6617 | 1.5335 | 1.8723 | 1.7395 | 1.6937 | 1.5976 | -0.11444 | 1.8723 | 1.7395 | 1.5976 | 1.5335 | 1.6937 | -121.1975 | -122.8546
2457.3281 | 122.6898 | -1.7395 | 120.9824 | -0.034637 | 0.014524 | -0.0062742 | 0.040558 | -0.010171 | -0.0072653 | 0.040838 | -0.004578 | 0.20142 | -0.16022 | -0.12817 | -0.19226 | -0.12817 | -0.027466 | -0.064087 | -0.032043 | -1.8677 | 1.5793 | -120.7809 | 1.7349 | 1.6113 | -121.1746 | -0.12817 | -121.0144 | 0.15564 | 1.712 | 1.6754 | 1.5472 | 1.9409 | 1.7349 | 1.7075 | 1.6113 | -0.12817 | 1.9409 | 1.7349 | 1.6113 | 1.5472 | 1.7075 | -121.1426 | -122.85
2458.3281 | 122.699 | -1.712 | 120.9732 | -0.21774 | 0.012815 | -0.011187 | 0.03885 | -0.011666 | -0.0081199 | 0.04212 | -0.027466 | 0.13733 | -0.19226 | -0.1831 | 0.073242 | 0.064087 | -0.059509 | -0.13733 | -0.009155 | -1.8494 | 1.5198 | -120.8359 | 1.6846 | 1.5289 | -120.9 | -0.13733 | -120.9824 | 0.16479 | 1.6525 | 1.5747 | 1.7853 | 1.8494 | 1.6846 | 1.7029 | 1.7761 | -0.13733 | 1.8494 | 1.6846 | 1.7761 | 1.7853 | 1.7029 | -121.1655 | -122.8226
2459.3281 | 122.7036 | -1.7761 | 120.9412 | -0.17197 | 0.012602 | -0.0058468 | 0.039704 | -0.010598 | -0.0079061 | 0.041906 | -0.022888 | 0.13275 | -0.18768 | -0.1236 | -0.1831 | -0.12817 | -0.054932 | -0.064087 | -0.054932 | -1.9043 | 1.5884 | -120.8084 | 1.7532 | 1.6525 | -121.1243 | -0.12817 | -120.9961 | 0.16479 | 1.7212 | 1.712 | 1.593 | 1.9089 | 1.7532 | 1.7212 | 1.6479 | -0.12817 | 1.9089 | 1.7532 | 1.6479 | 1.593 | 1.7212 | -121.1288 | -122.8455
2460.3438 | 122.8226 | -1.7487 | 120.9183 | -0.17197 | 0.0061929 | -0.015246 | 0.037781 | -0.012734 | -0.0076925 | 0.043615 | 0.19226 | 0.09613 | -0.17395 | -0.054932 | -0.10986 | -0.004578 | -0.21515 | 0.086975 | -0.11902 | -1.8723 | 1.5747 | -120.8221 | 1.9409 | 1.6937 | -121.0281 | -0.1236 | -121.0373 | 0.36621 | 1.5335 | 1.8356 | 1.6388 | 1.8448 | 1.9409 | 1.6296 | 1.7441 | -0.1236 | 1.8448 | 1.9409 | 1.7441 | 1.6388 | 1.6296 | -121.0922 | -122.7905
2461.3281 | 122.7722 | -1.799 | 120.9137 | -0.19485 | 0.014097 | -0.0056332 | 0.037995 | -0.010811 | -0.0079061 | 0.041693 | 0.054932 | 0.10529 | -0.16022 | -0.036621 | -0.12817 | -0.041199 | -0.13275 | 0.032043 | -0.068665 | -1.9043 | 1.6388 | -120.8084 | 1.8539 | 1.7624 | -121.0419 | -0.10529 | -120.9824 | 0.21515 | 1.6663 | 1.8311 | 1.6708 | 1.9043 | 1.8539 | 1.7303 | 1.7578 | -0.10529 | 1.9043 | 1.8539 | 1.7578 | 1.6708 | 1.7303 | -121.0739 | -122.818
2462.3281 | 122.8043 | -1.8219 | 120.8405 | -0.14145 | 0.012602 | -0.010333 | 0.039063 | -0.011666 | -0.0066245 | 0.043615 | 0.045776 | 0.10529 | -0.15106 | -0.032043 | -0.10071 | -0.032043 | -0.16937 | 0.054932 | -0.082397 | -1.9501 | 1.6708 | -120.7352 | 1.8677 | 1.7899 | -120.9412 | -0.12817 | -120.9229 | 0.19684 | 1.6525 | 1.8768 | 1.7212 | 1.9272 | 1.8677 | 1.7395 | 1.7899 | -0.12817 | 1.9272 | 1.8677 | 1.7899 | 1.7212 | 1.7395 | -120.9915 | -122.7905
2463.3438 | 122.7859 | -1.8082 | 120.8679 | 0.20187 | 0.013883 | -0.0084104 | 0.039277 | -0.011452 | -0.0061973 | 0.04212 | 0.054932 | 0.09613 | -0.16022 | -0.054932 | -0.13733 | -0.036621 | -0.22888 | 0 | -0.09613 | -1.9455 | 1.648 | -120.7718 | 1.8631 | 1.7532 | -121.0052 | -0.13733 | -120.9641 | 0.21515 | 1.5793 | 1.8082 | 1.6708 | 1.9043 | 1.8631 | 1.712 | 1.7715 | -0.13733 | 1.9043 | 1.8631 | 1.7715 | 1.6708 | 1.712 | -121.0281 | -122.8134
2464.3281 | 122.7951 | -1.8494 | 120.8588 | -0.13382 | 0.01132 | -0.0075558 | 0.037354 | -0.013589 | -0.0044883 | 0.041266 | 0.064087 | 0.12817 | -0.1236 | -0.027466 | -0.10529 | -0.027466 | -0.14191 | 0.041199 | -0.07782 | -1.9867 | 1.7258 | -120.7306 | 1.9135 | 1.8219 | -120.9641 | -0.13733 | -120.9366 | 0.18768 | 1.7075 | 1.8906 | 1.7441 | 1.9775 | 1.9135 | 1.7715 | 1.8219 | -0.13733 | 1.9775 | 1.9135 | 1.8219 | 1.7441 | 1.7715 | -120.9824 | -122.8455
2465.3594 | 122.8134 | -1.8585 | 120.813 | -0.095673 | 0.012388 | -0.006915 | 0.036713 | -0.011025 | -0.0059835 | 0.041479 | 0.091553 | 0.12817 | -0.14648 | 0.004578 | -0.082397 | 0.013733 | -0.19684 | 0.07782 | -0.091553 | -1.9821 | 1.712 | -120.6848 | 1.9501 | 1.8631 | -120.8954 | -0.1236 | -120.9045 | 0.23804 | 1.6617 | 1.9363 | 1.7761 | 1.9867 | 1.9501 | 1.767 | 1.8723 | -0.1236 | 1.9867 | 1.9501 | 1.8723 | 1.7761 | 1.767 | -120.9595 | -122.7951
2466.3281 | 122.8088 | -1.8677 | 120.7855 | -0.14145 | 0.012815 | -0.0064878 | 0.037354 | -0.012093 | -0.0059835 | 0.039984 | 0.064087 | 0.11902 | -0.13275 | -0.009155 | -0.09613 | 0 | -0.19684 | 0.091553 | -0.07782 | -2.005 | 1.7349 | -120.6665 | 1.9318 | 1.8585 | -120.8817 | -0.13733 | -120.8633 | 0.19684 | 1.6708 | 1.9592 | 1.7715 | 1.9867 | 1.9318 | 1.7899 | 1.8677 | -0.13733 | 1.9867 | 1.9318 | 1.8677 | 1.7715 | 1.7899 | -120.9183 | -122.7905
2467.3281 | 122.7081 | -1.9821 | 120.7993 | -0.1796 | 0.013243 | -0.0058468 | 0.041199 | -0.01252 | -0.0072653 | 0.041266 | -0.013733 | 0.13733 | -0.17853 | -0.11902 | -0.20599 | -0.15106 | -0.036621 | -0.068665 | -0.036621 | -2.1103 | 1.8036 | -120.6619 | 1.9684 | 1.8631 | -121.0052 | -0.12817 | -120.8359 | 0.16479 | 1.9455 | 1.9135 | 1.7761 | 2.1194 | 1.9684 | 1.9455 | 1.8311 | -0.12817 | 2.1194 | 1.9684 | 1.8311 | 1.7761 | 1.9455 | -120.9778 | -122.9095
2468.3281 | 122.8271 | -1.9501 | 120.6985 | -0.11093 | 0.014524 | -0.0047788 | 0.038636 | -0.011666 | -0.0061973 | 0.042975 | 0.050354 | 0.13733 | -0.11902 | 0.004578 | -0.07782 | 0.004578 | -0.20599 | 0.073242 | -0.073242 | -2.0737 | 1.8311 | -120.5612 | 2.0004 | 1.9547 | -120.7764 | -0.1236 | -120.7718 | 0.16937 | 1.7441 | 2.0233 | 1.8723 | 2.0874 | 2.0004 | 1.8768 | 1.9547 | -0.1236 | 2.0874 | 2.0004 | 1.9547 | 1.8723 | 1.8768 | -120.8176 | -122.7722
2469.3281 | 122.8592 | -2.037 | 120.6528 | 0.011139 | 0.013029 | -0.0077694 | 0.038422 | -0.012093 | -0.0068381 | 0.041906 | 0.09613 | 0.1236 | -0.13275 | -0.004578 | -0.10071 | -0.004578 | -0.19684 | 0.036621 | -0.045776 | -2.1606 | 1.9043 | -120.5292 | 2.1332 | 2.0325 | -120.7535 | -0.1236 | -120.6985 | 0.22888 | 1.8402 | 2.0737 | 1.9363 | 2.1606 | 2.1332 | 1.9913 | 2.0325 | -0.1236 | 2.1606 | 2.1332 | 2.0325 | 1.9363 | 1.9913 | -120.7855 | -122.8134
2470.3438 | 122.8134 | -2.0828 | 120.6436 | 0.21713 | 0.01602 | -0.0060604 | 0.04419 | -0.010171 | -0.0057699 | 0.040625 | 0.013733 | 0.10986 | -0.17395 | -0.050354 | -0.15564 | -0.054932 | -0.24719 | -0.032043 | -0.07782 | -2.1927 | 1.9089 | -120.5338 | 2.0966 | 2.0325 | -120.7993 | -0.10986 | -120.7214 | 0.18768 | 1.8356 | 2.0508 | 1.9272 | 2.1927 | 2.0966 | 2.005 | 2.0279 | -0.10986 | 2.1927 | 2.0966 | 2.0279 | 1.9272 | 2.005 | -120.8176 | -122.8363
2471.3281 | 122.8317 | -2.0782 | 120.6207 | -0.034637 | 0.011961 | -0.01311 | 0.036286 | -0.013589 | -0.0055563 | 0.042334 | 0.036621 | 0.14191 | -0.13275 | -0.041199 | -0.10529 | -0.027466 | -0.1831 | 0.045776 | -0.032043 | -2.1927 | 1.9455 | -120.4788 | 2.1149 | 2.037 | -120.726 | -0.11444 | -120.6528 | 0.16937 | 1.8951 | 2.124 | 1.973 | 2.2202 | 2.1149 | 2.0462 | 2.0508 | -0.11444 | 2.2202 | 2.1149 | 2.0508 | 1.973 | 2.0462 | -120.7535 | -122.8134
2472.3438 | 122.8043 | -2.1057 | 120.6024 | 0.16373 | 0.013456 | -0.0056332 | 0.039063 | -0.01252 | -0.0051291 | 0.042334 | 0.009155 | 0.10529 | -0.15106 | -0.091553 | -0.16022 | -0.068665 | -0.19684 | -0.045776 | -0.054932 | -2.2293 | 1.9547 | -120.4971 | 2.1149 | 2.0142 | -120.7626 | -0.1236 | -120.6573 | 0.16022 | 1.9089 | 2.0599 | 1.9455 | 2.211 | 2.1149 | 2.0508 | 2.037 | -0.1236 | 2.211 | 2.1149 | 2.037 | 1.9455 | 2.0508 | -120.7535 | -122.8317
2473.3281 | 122.8226 | -2.0966 | 120.575 | -0.019379 | 0.014952 | -0.0058468 | 0.039063 | -0.015084 | -0.0076925 | 0.043615 | -0.009155 | 0.11444 | -0.14648 | -0.07782 | -0.16937 | -0.07782 | -0.1831 | -0.036621 | -0.054932 | -2.2293 | 1.9501 | -120.4605 | 2.0874 | 2.0187 | -120.7443 | -0.13275 | -120.6299 | 0.13733 | 1.9135 | 2.0599 | 1.9272 | 2.211 | 2.0874 | 2.0416 | 2.0187 | -0.13275 | 2.211 | 2.0874 | 2.0187 | 1.9272 | 2.0416 | -120.7214 | -122.8043
2474.3281 | 122.8638 | -2.1423 | 120.5521 | -0.088043 | 0.010679 | -0.0073422 | 0.039704 | -0.014443 | -0.0061973 | 0.041693 | 0.050354 | 0.09613 | -0.16022 | -0.009155 | -0.10529 | -0.013733 | -0.22888 | 0.064087 | -0.059509 | -2.2751 | 1.9821 | -120.4559 | 2.1927 | 2.1332 | -120.6573 | -0.13275 | -120.6116 | 0.21057 | 1.9135 | 2.2064 | 2.037 | 2.2385 | 2.1927 | 2.0828 | 2.1286 | -0.13275 | 2.2385 | 2.1927 | 2.1286 | 2.037 | 2.0828 | -120.7123 | -122.8271
2475.3281 | 122.7997 | -2.1652 | 120.5612 | 0.14847 | 0.013456 | -0.0047788 | 0.041199 | -0.015725 | -0.0074789 | 0.043188 | -0.004578 | 0.10071 | -0.15564 | -0.091553 | -0.17395 | -0.064087 | -0.19226 | -0.045776 | -0.041199 | -2.2888 | 2.0096 | -120.4605 | 2.1606 | 2.0737 | -120.7352 | -0.1236 | -120.6024 | 0.15106 | 1.973 | 2.1194 | 1.9913 | 2.2659 | 2.1606 | 2.124 | 2.1011 | -0.1236 | 2.2659 | 2.1606 | 2.1011 | 1.9913 | 2.124 | -120.7169 | -122.85
2476.3281 | 122.8134 | -2.179 | 120.5521 | 0.17136 | 0.014738 | -0.0039242 | 0.040558 | -0.011239 | -0.0070517 | 0.042547 | 0.054932 | 0.10529 | -0.15106 | -0.064087 | -0.16022 | -0.054932 | -0.23804 | -0.041199 | -0.050354 | -2.3117 | 2.0279 | -120.4468 | 2.2339 | 2.1149 | -120.7123 | -0.13275 | -120.6024 | 0.20599 | 1.9409 | 2.1378 | 2.0187 | 2.2842 | 2.2339 | 2.1286 | 2.124 | -0.13275 | 2.2842 | 2.2339 | 2.124 | 2.0187 | 2.1286 | -120.7031 | -122.8638
2477.3438 | 122.85 | -2.1927 | 120.5017 | 0.24765 | 0.016447 | -0.003497 | 0.042908 | -0.013375 | -0.0051291 | 0.041052 | 0.086975 | 0.09613 | -0.13275 | -0.009155 | -0.14191 | -0.032043 | -0.28381 | -0.009155 | -0.068665 | -2.3254 | 2.0599 | -120.4056 | 2.2797 | 2.1835 | -120.6436 | -0.13275 | -120.5704 | 0.21973 | 1.9089 | 2.1835 | 2.0508 | 2.2888 | 2.2797 | 2.124 | 2.1606 | -0.13275 | 2.2888 | 2.2797 | 2.1606 | 2.0508 | 2.124 | -120.6345 | -122.8271
2478.3281 | 122.8226 | -2.2202 | 120.4697 | 0.2095 | 0.01602 | -0.005206 | 0.040558 | -0.0095296 | -0.0070517 | 0.04212 | 0.036621 | 0.073242 | -0.14648 | -0.064087 | -0.14191 | -0.050354 | -0.25635 | -0.022888 | -0.041199 | -2.3575 | 2.0737 | -120.3964 | 2.2568 | 2.1561 | -120.6116 | -0.13733 | -120.5109 | 0.18311 | 1.9638 | 2.1973 | 2.0782 | 2.2934 | 2.2568 | 2.179 | 2.1698 | -0.13733 | 2.2934 | 2.2568 | 2.1698 | 2.0782 | 2.179 | -120.6162 | -122.8271
2479.3438 | 122.7356 | -2.3117 | 120.4926 | 0.12558 | 0.019865 | -7.9006e-05 | 0.046967 | -0.011452 | -0.0064109 | 0.03977 | -0.027466 | 0.16022 | -0.20142 | -0.11902 | -0.23804 | -0.15564 | -0.10986 | -0.15106 | -0.004578 | -2.4124 | 2.1103 | -120.3323 | 2.2842 | 2.1927 | -120.7306 | -0.10071 | -120.4971 | 0.17395 | 2.2018 | 2.1606 | 2.0737 | 2.4719 | 2.2842 | 2.3071 | 2.1561 | -0.10071 | 2.4719 | 2.2842 | 2.1561 | 2.0737 | 2.3071 | -120.694 | -122.905
2480.3281 | 122.8592 | -2.2293 | 120.4559 | 0.2095 | 0.017729 | -0.0041378 | 0.040986 | -0.0097434 | -0.0038473 | 0.043402 | 0.064087 | 0.11444 | -0.13275 | -0.027466 | -0.1236 | -0.018311 | -0.27924 | 0 | -0.07782 | -2.3895 | 2.0966 | -120.3415 | 2.2934 | 2.2018 | -120.5795 | -0.16022 | -120.5338 | 0.19684 | 1.9501 | 2.2293 | 2.1057 | 2.3438 | 2.2934 | 2.1515 | 2.211 | -0.16022 | 2.3438 | 2.2934 | 2.211 | 2.1057 | 2.1515 | -120.5887 | -122.8455
2481.3594 | 122.8775 | -2.2385 | 120.4468 | 0.24765 | 0.016233 | -0.00093361 | 0.042481 | -0.010598 | -0.0051291 | 0.04212 | 0.068665 | 0.086975 | -0.15564 | -0.036621 | -0.13275 | -0.013733 | -0.27008 | 0.004578 | -0.068665 | -2.3941 | 2.0828 | -120.3598 | 2.3071 | 2.2018 | -120.5795 | -0.15564 | -120.5154 | 0.22431 | 1.9684 | 2.243 | 2.1057 | 2.3254 | 2.3071 | 2.1698 | 2.2247 | -0.15564 | 2.3254 | 2.3071 | 2.2247 | 2.1057 | 2.1698 | -120.6024 | -122.8409
2482.3281 | 122.8271 | -2.2614 | 120.4376 | 0.24002 | 0.016661 | -0.0026426 | 0.043763 | -0.011025 | -0.0061973 | 0.040198 | 0.004578 | 0.13275 | -0.16937 | -0.041199 | -0.14648 | -0.054932 | -0.24261 | -0.018311 | -0.050354 | -2.3895 | 2.092 | -120.3049 | 2.2659 | 2.2202 | -120.5841 | -0.12817 | -120.488 | 0.17395 | 2.0187 | 2.243 | 2.1149 | 2.3941 | 2.2659 | 2.211 | 2.2064 | -0.12817 | 2.3941 | 2.2659 | 2.2064 | 2.1149 | 2.211 | -120.607 | -122.8271
2483.3281 | 122.7539 | -2.3438 | 120.4651 | 0.14084 | 0.015592 | -0.0037106 | 0.043336 | -0.010171 | -0.0017111 | 0.041906 | -0.032043 | 0.15564 | -0.18768 | -0.13733 | -0.23346 | -0.15106 | -0.10529 | -0.15106 | -0.041199 | -2.4719 | 2.1561 | -120.3094 | 2.3117 | 2.2064 | -120.6985 | -0.12817 | -120.5063 | 0.15564 | 2.2385 | 2.1927 | 2.1103 | 2.4994 | 2.3117 | 2.3026 | 2.1927 | -0.12817 | 2.4994 | 2.3117 | 2.1927 | 2.1103 | 2.3026 | -120.6528 | -122.937
2484.3281 | 122.8271 | -2.3071 | 120.4056 | 0.23239 | 0.016874 | -0.0024288 | 0.042908 | -0.0088888 | -0.0047019 | 0.041266 | 0.004578 | 0.1236 | -0.17395 | -0.082397 | -0.17853 | -0.064087 | -0.23804 | -0.054932 | -0.068665 | -2.4261 | 2.1332 | -120.282 | 2.3117 | 2.2247 | -120.5841 | -0.11902 | -120.4742 | 0.17853 | 2.0691 | 2.2522 | 2.1286 | 2.4307 | 2.3117 | 2.2385 | 2.243 | -0.11902 | 2.4307 | 2.3117 | 2.243 | 2.1286 | 2.2385 | -120.5795 | -122.8317
2485.3281 | 122.7768 | -2.3392 | 120.4102 | 0.20187 | 0.017729 | -0.0013608 | 0.043122 | -0.010598 | -0.0038473 | 0.043615 | -0.022888 | 0.15106 | -0.1831 | -0.11444 | -0.20142 | -0.11444 | -0.15106 | -0.10986 | -0.064087 | -2.4765 | 2.1561 | -120.2591 | 2.3163 | 2.2247 | -120.6116 | -0.13733 | -120.4742 | 0.16022 | 2.1881 | 2.2293 | 2.1378 | 2.4902 | 2.3163 | 2.2751 | 2.2247 | -0.13733 | 2.4902 | 2.3163 | 2.2247 | 2.1378 | 2.2751 | -120.5933 | -122.8867
2486.3438 | 122.7905 | -2.3621 | 120.3964 | -0.057526 | 0.017515 | -0.0073422 | 0.045258 | -0.0086752 | -0.0076925 | 0.041479 | 0.027466 | 0.13275 | -0.17395 | -0.064087 | -0.17395 | -0.10529 | -0.1236 | -0.045776 | -0.041199 | -2.4948 | 2.1881 | -120.2637 | 2.3895 | 2.298 | -120.5704 | -0.13275 | -120.4376 | 0.20142 | 2.2385 | 2.3163 | 2.1881 | 2.4948 | 2.3895 | 2.3209 | 2.2568 | -0.13275 | 2.4948 | 2.3895 | 2.2568 | 2.1881 | 2.3209 | -120.5704 | -122.8912
2487.3281 | 122.7356 | -2.3941 | 120.3735 | 0.16373 | 0.015806 | -0.00072001 | 0.042481 | -0.0095296 | -0.0053427 | 0.041906 | -0.027466 | 0.14191 | -0.19226 | -0.16022 | -0.23804 | -0.14648 | -0.10986 | -0.16937 | -0.041199 | -2.5177 | 2.2018 | -120.2316 | 2.3666 | 2.2339 | -120.6116 | -0.1236 | -120.4147 | 0.16479 | 2.2842 | 2.2247 | 2.1561 | 2.536 | 2.3666 | 2.3529 | 2.2476 | -0.1236 | 2.536 | 2.3666 | 2.2476 | 2.1561 | 2.3529 | -120.5658 | -122.8912
2488.3438 | 122.7539 | -2.4124 | 120.3873 | -0.46951 | 0.015592 | -0.0075558 | 0.038209 | -0.01252 | -0.0049155 | 0.042547 | -0.073242 | 0.13275 | -0.19226 | -0.15106 | -0.22888 | -0.14648 | -0.032043 | -0.10071 | -0.036621 | -2.536 | 2.2202 | -120.2545 | 2.3392 | 2.2614 | -120.6162 | -0.1236 | -120.4239 | 0.11902 | 2.3804 | 2.3117 | 2.1835 | 2.5452 | 2.3392 | 2.3758 | 2.2659 | -0.1236 | 2.5452 | 2.3392 | 2.2659 | 2.1835 | 2.3758 | -120.5795 | -122.9233
2489.3281 | 122.7219 | -2.4353 | 120.3552 | 0.10269 | 0.017301 | -0.00050621 | 0.043976 | -0.0078206 | -0.0076925 | 0.042334 | -0.036621 | 0.11902 | -0.21057 | -0.17853 | -0.2655 | -0.15564 | -0.086975 | -0.16479 | -0.054932 | -2.5452 | 2.2247 | -120.2362 | 2.3987 | 2.2568 | -120.6207 | -0.10986 | -120.4102 | 0.17395 | 2.3483 | 2.2705 | 2.1698 | 2.5543 | 2.3987 | 2.3804 | 2.2797 | -0.10986 | 2.5543 | 2.3987 | 2.2797 | 2.1698 | 2.3804 | -120.5658 | -122.9004
2490.3438 | 122.7905 | -2.3895 | 120.3644 | -0.18723 | 0.014524 | -0.007983 | 0.037141 | -0.0088888 | -0.0057699 | 0.040838 | 0.009155 | 0.11444 | -0.15564 | -0.082397 | -0.14648 | -0.068665 | -0.11444 | -0.022888 | -0.054932 | -2.5177 | 2.2339 | -120.2499 | 2.3987 | 2.3071 | -120.5109 | -0.12817 | -120.4193 | 0.16479 | 2.2751 | 2.3666 | 2.243 | 2.504 | 2.3987 | 2.3346 | 2.3209 | -0.12817 | 2.504 | 2.3987 | 2.3209 | 2.243 | 2.3346 | -120.52 | -122.8821
2491.3281 | 122.7402 | -2.4353 | 120.369 | 0.11032 | 0.018583 | -0.0039242 | 0.043763 | -0.010171 | -0.0057699 | 0.042761 | -0.032043 | 0.12817 | -0.1831 | -0.17395 | -0.28381 | -0.16479 | -0.086975 | -0.1831 | -0.045776 | -2.5635 | 2.2522 | -120.2408 | 2.4033 | 2.2614 | -120.6528 | -0.12817 | -120.4147 | 0.15106 | 2.3483 | 2.2522 | 2.1515 | 2.5635 | 2.4033 | 2.3895 | 2.2705 | -0.12817 | 2.5635 | 2.4033 | 2.2705 | 2.1515 | 2.3895 | -120.5521 | -122.9324
2492.3594 | 122.7768 | -2.449 | 120.3461 | 0.095062 | 0.017301 | -0.00029261 | 0.042481 | -0.0086752 | -0.0055563 | 0.043829 | 0.004578 | 0.13733 | -0.19226 | -0.11444 | -0.23804 | -0.14648 | -0.10986 | -0.11902 | -0.050354 | -2.5818 | 2.2568 | -120.2087 | 2.4536 | 2.3346 | -120.5841 | -0.13275 | -120.3964 | 0.19684 | 2.3392 | 2.33 | 2.211 | 2.5864 | 2.4536 | 2.3987 | 2.3026 | -0.13275 | 2.5864 | 2.4536 | 2.3026 | 2.211 | 2.3987 | -120.5383 | -122.9279
2493.3281 | 122.7631 | -2.449 | 120.3369 | 0.072174 | 0.016447 | -0.0020016 | 0.042908 | -0.008248 | -0.0038473 | 0.043402 | -0.018311 | 0.16937 | -0.16937 | -0.14191 | -0.2243 | -0.14191 | -0.091553 | -0.1236 | -0.073242 | -2.5909 | 2.2797 | -120.1675 | 2.4307 | 2.3071 | -120.5612 | -0.14191 | -120.4102 | 0.15106 | 2.3575 | 2.3254 | 2.2247 | 2.6184 | 2.4307 | 2.3758 | 2.3071 | -0.14191 | 2.6184 | 2.4307 | 2.3071 | 2.2247 | 2.3758 | -120.5063 | -122.9279
2494.3594 | 122.7585 | -2.4765 | 120.314 | 0.14847 | 0.018156 | -0.0024288 | 0.041627 | -0.0084616 | -0.0070517 | 0.044684 | -0.036621 | 0.14648 | -0.19226 | -0.17395 | -0.23346 | -0.15564 | -0.091553 | -0.16479 | -0.050354 | -2.6001 | 2.2842 | -120.1675 | 2.4399 | 2.3026 | -120.5475 | -0.1236 | -120.3644 | 0.15564 | 2.3849 | 2.3117 | 2.243 | 2.623 | 2.4399 | 2.4261 | 2.3209 | -0.1236 | 2.623 | 2.4399 | 2.3209 | 2.243 | 2.4261 | -120.5063 | -122.9141
2495.3281 | 122.7676 | -2.4628 | 120.3003 | 0.2095 | 0.016447 | -0.0037106 | 0.040558 | -0.0080344 | -0.0029929 | 0.044256 | -0.036621 | 0.16022 | -0.17853 | -0.16022 | -0.24719 | -0.1236 | -0.1236 | -0.15564 | -0.073242 | -2.6184 | 2.2842 | -120.1401 | 2.4261 | 2.3026 | -120.5475 | -0.15564 | -120.3735 | 0.14191 | 2.3392 | 2.3071 | 2.2156 | 2.623 | 2.4261 | 2.3895 | 2.3392 | -0.15564 | 2.623 | 2.4261 | 2.3392 | 2.2156 | 2.3895 | -120.4788 | -122.9187
2496.3438 | 122.8638 | -2.4353 | 120.2637 | -0.14908 | 0.013456 | -0.0092648 | 0.032441 | -0.011666 | -0.0061973 | 0.043615 | 0.004578 | 0.091553 | -0.14191 | -0.045776 | -0.10529 | -0.022888 | -0.21057 | 0.027466 | -0.11444 | -2.5909 | 2.2934 | -120.1721 | 2.4399 | 2.3895 | -120.369 | -0.15564 | -120.3781 | 0.14649 | 2.2247 | 2.4628 | 2.33 | 2.5269 | 2.4399 | 2.3209 | 2.4124 | -0.15564 | 2.5269 | 2.4399 | 2.4124 | 2.33 | 2.3209 | -120.4056 | -122.8546
2497.3281 | 122.7905 | -2.4902 | 120.2591 | -0.034637 | 0.01901 | -0.0054196 | 0.043336 | -0.009316 | -0.0059835 | 0.042547 | 0.036621 | 0.15106 | -0.16937 | -0.10071 | -0.20142 | -0.10071 | -0.14191 | -0.073242 | -0.086975 | -2.6413 | 2.3209 | -120.108 | 2.5269 | 2.3895 | -120.4605 | -0.15106 | -120.3461 | 0.20599 | 2.3483 | 2.417 | 2.2888 | 2.6413 | 2.5269 | 2.4033 | 2.3895 | -0.15106 | 2.6413 | 2.5269 | 2.3895 | 2.2888 | 2.4033 | -120.4285 | -122.9004
2498.3594 | 122.7951 | -2.5223 | 120.2682 | 0.011139 | 0.016661 | -0.0032834 | 0.043763 | -0.008248 | -0.0055563 | 0.043188 | 0.022888 | 0.13275 | -0.16937 | -0.10986 | -0.22888 | -0.1236 | -0.12817 | -0.11444 | -0.073242 | -2.655 | 2.3529 | -120.1355 | 2.5452 | 2.4124 | -120.4971 | -0.13275 | -120.3415 | 0.19226 | 2.3941 | 2.4078 | 2.2934 | 2.655 | 2.5452 | 2.449 | 2.3987 | -0.13275 | 2.655 | 2.5452 | 2.3987 | 2.2934 | 2.449 | -120.4376 | -122.9233
2499.3281 | 122.8088 | -2.5177 | 120.2591 | -0.095673 | 0.017088 | -0.0058468 | 0.042267 | -0.0078206 | -0.0076925 | 0.041906 | 0.036621 | 0.13733 | -0.17395 | -0.086975 | -0.19226 | -0.10071 | -0.14191 | -0.086975 | -0.07782 | -2.6413 | 2.3438 | -120.1218 | 2.5543 | 2.4307 | -120.4514 | -0.1236 | -120.3369 | 0.21057 | 2.3758 | 2.4307 | 2.3254 | 2.655 | 2.5543 | 2.4399 | 2.417 | -0.1236 | 2.655 | 2.5543 | 2.417 | 2.3254 | 2.4399 | -120.433 | -122.9004
2500.3281 | 122.7905 | -2.536 | 120.2316 | -0.095673 | 0.017729 | -0.00072001 | 0.040986 | -0.0069662 | -0.0057699 | 0.040411 | 0.018311 | 0.15106 | -0.17853 | -0.091553 | -0.20599 | -0.10071 | -0.13275 | -0.07782 | -0.082397 | -2.6596 | 2.3575 | -120.0806 | 2.5543 | 2.4445 | -120.4376 | -0.1236 | -120.314 | 0.19684 | 2.4033 | 2.4582 | 2.33 | 2.6871 | 2.5543 | 2.4536 | 2.4353 | -0.1236 | 2.6871 | 2.5543 | 2.4353 | 2.33 | 2.4536 | -120.4102 | -122.8912
2501.3281 | 122.7951 | -2.5314 | 120.2225 | -0.080414 | 0.018797 | -0.0028562 | 0.040558 | -0.0086752 | -0.0059835 | 0.04447 | 0.018311 | 0.14648 | -0.17395 | -0.09613 | -0.19226 | -0.10529 | -0.11902 | -0.07782 | -0.086975 | -2.6825 | 2.3575 | -120.076 | 2.5497 | 2.4353 | -120.4147 | -0.15106 | -120.3094 | 0.19226 | 2.4124 | 2.4536 | 2.3392 | 2.6779 | 2.5497 | 2.4445 | 2.4261 | -0.15106 | 2.6779 | 2.5497 | 2.4261 | 2.3392 | 2.4445 | -120.3964 | -122.905
2502.3281 | 122.8271 | -2.5772 | 120.2179 | -0.1796 | 0.018583 | -0.0045652 | 0.040345 | -0.0084616 | -0.0064109 | 0.044043 | -0.009155 | 0.13275 | -0.17853 | -0.10071 | -0.20142 | -0.10986 | -0.091553 | -0.09613 | -0.091553 | -2.7283 | 2.3987 | -120.0851 | 2.5681 | 2.4765 | -120.4193 | -0.15106 | -120.3094 | 0.16937 | 2.4857 | 2.4811 | 2.3758 | 2.71 | 2.5681 | 2.4857 | 2.4673 | -0.15106 | 2.71 | 2.5681 | 2.4673 | 2.3758 | 2.4857 | -120.3964 | -122.9462
2503.3594 | 122.7859 | -2.5909 | 120.2087 | -0.15671 | 0.016233 | -0.0039242 | 0.037568 | -0.0091024 | -0.0055563 | 0.042761 | -0.064087 | 0.14191 | -0.20142 | -0.14191 | -0.23346 | -0.15564 | -0.045776 | -0.14191 | -0.09613 | -2.7191 | 2.3895 | -120.0668 | 2.5269 | 2.449 | -120.4422 | -0.12817 | -120.3049 | 0.13733 | 2.5452 | 2.449 | 2.3575 | 2.7328 | 2.5269 | 2.4948 | 2.4353 | -0.12817 | 2.7328 | 2.5269 | 2.4353 | 2.3575 | 2.4948 | -120.4102 | -122.9279
2504.3281 | 122.7997 | -2.6276 | 120.1813 | -0.15671 | 0.015806 | -0.0041378 | 0.03949 | -0.010171 | -0.0057699 | 0.041052 | -0.036621 | 0.15106 | -0.18768 | -0.12817 | -0.23804 | -0.13733 | -0.064087 | -0.12817 | -0.09613 | -2.774 | 2.4399 | -120.0302 | 2.5909 | 2.4994 | -120.4193 | -0.14649 | -120.2774 | 0.15106 | 2.5635 | 2.4994 | 2.3895 | 2.7786 | 2.5909 | 2.5314 | 2.4902 | -0.14649 | 2.7786 | 2.5909 | 2.4902 | 2.3895 | 2.5314 | -120.369 | -122.9553

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2
-0.824 | 20.6933 | 19.89 | 20.0708
0.176 | 20.6848 | 19.896 | 20.0698
1.176 | 20.6817 | 19.8864 | 20.0772
2.176 | 20.6939 | 19.8816 | 20.0727
3.176 | 20.776 | 19.8928 | 20.0762
4.176 | 21.3753 | 19.8954 | 20.0751
5.176 | 22.6882 | 19.8976 | 20.0832
6.176 | 24.6696 | 19.8964 | 20.0802
7.176 | 27.2504 | 19.8998 | 20.0854
8.176 | 30.3341 | 19.8933 | 20.0875
9.176 | 33.8433 | 19.9065 | 20.1082
10.176 | 37.7257 | 19.914 | 20.1129
11.176 | 41.8896 | 19.9464 | 20.1277
12.176 | 46.2638 | 19.9506 | 20.1559
13.176 | 50.885 | 19.9786 | 20.1809
14.176 | 55.7075 | 20.0204 | 20.2228
15.176 | 60.6523 | 20.0493 | 20.2682
16.176 | 65.7418 | 20.0859 | 20.3076
17.176 | 70.9863 | 20.1409 | 20.3696
18.176 | 76.385 | 20.1929 | 20.4328
19.176 | 81.8682 | 20.246 | 20.497
20.176 | 87.4529 | 20.3229 | 20.5806
21.176 | 93.1844 | 20.4115 | 20.668
22.176 | 98.9652 | 20.4813 | 20.7536
23.176 | 104.814 | 20.5774 | 20.8671
24.176 | 110.7474 | 20.6813 | 20.9755
25.176 | 116.7081 | 20.8037 | 21.0893
26.176 | 122.598 | 20.922 | 21.2211
27.176 | 128.5624 | 21.0515 | 21.3671
28.176 | 134.5741 | 21.1905 | 21.513
29.176 | 140.5936 | 21.3363 | 21.6571
30.176 | 146.5503 | 21.5058 | 21.833
31.176 | 152.5766 | 21.6577 | 22.0164
32.176 | 158.5106 | 21.8424 | 22.2103
33.176 | 164.3818 | 22.0392 | 22.4134
34.176 | 170.3322 | 22.2368 | 22.6352
35.176 | 176.327 | 22.4604 | 22.8613
36.176 | 182.1887 | 22.6795 | 23.0995
37.176 | 188.1145 | 22.9172 | 23.3532
38.176 | 193.9583 | 23.182 | 23.6191
39.176 | 199.8046 | 23.4398 | 23.8976
40.176 | 205.677 | 23.7274 | 24.1951
41.176 | 211.6125 | 24.0032 | 24.5001
42.176 | 217.4838 | 24.3248 | 24.8223
43.176 | 223.2119 | 24.65 | 25.1564
44.176 | 229.016 | 24.9734 | 25.5112
45.176 | 234.8415 | 25.3194 | 25.8722
46.176 | 240.6311 | 25.6928 | 26.2443
47.176 | 246.3895 | 26.0638 | 26.656
48.176 | 252.0384 | 26.485 | 27.0708
49.176 | 257.634 | 26.8765 | 27.4957
50.176 | 263.298 | 27.3169 | 27.9349
51.176 | 268.9337 | 27.7446 | 28.3979
52.176 | 274.5623 | 28.2113 | 28.8714
53.176 | 280.0748 | 28.6665 | 29.362
54.176 | 285.5514 | 29.1841 | 29.8682
55.176 | 290.9123 | 29.6944 | 30.394
56.176 | 296.4181 | 30.207 | 30.9408
57.176 | 301.812 | 30.7535 | 31.4947
58.176 | 307.2441 | 31.2986 | 32.0778
59.176 | 312.5607 | 31.8924 | 32.6768
60.176 | 317.7543 | 32.4893 | 33.2923
61.176 | 323.0389 | 33.1059 | 33.917
62.176 | 328.4889 | 33.7415 | 34.568
63.176 | 333.7351 | 34.4161 | 35.227
64.176 | 339.0397 | 35.0976 | 35.9067
65.176 | 344.1918 | 35.7927 | 36.6074
66.176 | 349.2562 | 36.5211 | 37.318
67.176 | 354.3207 | 37.2789 | 38.0421
68.176 | 359.3149 | 38.0411 | 38.7771
69.176 | 364.3392 | 38.8226 | 39.5414
70.176 | 369.4801 | 39.6425 | 40.314
71.176 | 374.3888 | 40.4587 | 41.1161
72.176 | 379.3362 | 41.3081 | 41.9355
73.176 | 384.1787 | 42.1978 | 42.7679
74.176 | 388.7889 | 43.0981 | 43.6337
75.176 | 393.6067 | 44.0232 | 44.5128
76.176 | 398.5287 | 44.9877 | 45.422
77.176 | 403.2763 | 45.9931 | 46.3688
78.176 | 407.9805 | 47.0138 | 47.3106
79.176 | 412.7386 | 48.0769 | 48.2939
80.176 | 417.2168 | 49.1916 | 49.2952
81.176 | 421.5889 | 50.3569 | 50.3121
82.176 | 425.5665 | 51.5662 | 51.3571
83.176 | 429.2175 | 52.7847 | 52.4199
84.176 | 432.5405 | 54.088 | 53.4888
85.176 | 435.4914 | 55.3957 | 54.5788
86.176 | 438.4396 | 56.7343 | 55.6767
87.176 | 441.1179 | 58.1023 | 56.7823
88.176 | 443.9377 | 59.4825 | 57.9023
89.176 | 446.5729 | 60.8775 | 59.0195
90.176 | 449.1166 | 62.3149 | 60.1339
91.176 | 451.4912 | 63.7532 | 61.2557
92.176 | 453.6895 | 65.2108 | 62.3776
93.176 | 455.8991 | 66.6955 | 63.5083
94.176 | 457.899 | 68.1991 | 64.6387
95.176 | 459.7289 | 69.7056 | 65.7528
96.176 | 461.2992 | 71.2458 | 66.8749
97.176 | 462.3095 | 72.8106 | 67.9942
98.176 | 463.352 | 74.3729 | 69.1012
99.176 | 464.2918 | 75.9067 | 70.198
100.176 | 465.1507 | 77.4346 | 71.2895
101.176 | 465.8046 | 78.9778 | 72.3722
102.176 | 466.3438 | 80.4904 | 73.4426
103.176 | 466.7185 | 81.976 | 74.5312
104.176 | 466.7277 | 83.4873 | 75.5926
105.176 | 466.7558 | 84.9792 | 76.6441
106.176 | 467.0076 | 86.4423 | 77.6911
107.176 | 467.1888 | 87.8961 | 78.7634
108.176 | 467.2128 | 89.3317 | 79.8308
109.176 | 467.2219 | 90.7554 | 80.9029
110.176 | 467.2014 | 92.1617 | 81.9874
111.176 | 467.0375 | 93.569 | 83.08
112.176 | 467.1167 | 94.9546 | 84.1992
113.176 | 466.6859 | 96.3382 | 85.3262
114.176 | 466.6686 | 97.731 | 86.4617
115.176 | 466.5723 | 99.116 | 87.5957
116.176 | 466.5254 | 100.5189 | 88.7375
117.176 | 466.3156 | 101.8995 | 89.9103
118.176 | 466.3425 | 103.3247 | 91.1266
119.176 | 466.5427 | 104.7576 | 92.3887
120.176 | 466.6363 | 106.2075 | 93.6752
121.176 | 466.7859 | 107.6676 | 94.9666
122.176 | 467.0206 | 109.1668 | 96.242
123.176 | 467.4307 | 110.6969 | 97.544
124.176 | 467.7271 | 112.2336 | 98.8438
125.176 | 467.7469 | 113.7943 | 100.1531
126.176 | 467.9037 | 115.368 | 101.4713
127.176 | 468.1246 | 116.9325 | 102.835
128.176 | 468.3982 | 118.4949 | 104.1992
129.176 | 468.5071 | 120.0529 | 105.5931
130.176 | 468.6053 | 121.5922 | 107.001
131.176 | 468.7521 | 123.0953 | 108.4324
132.176 | 469.1846 | 124.5544 | 109.8552
133.176 | 469.4065 | 125.9509 | 111.2925
134.176 | 469.5459 | 127.3011 | 112.7418
135.176 | 469.9081 | 128.5869 | 114.1948
136.176 | 470.2366 | 129.8169 | 115.6324
137.176 | 470.444 | 130.9854 | 117.0427
138.176 | 470.5991 | 132.1055 | 118.4249
139.176 | 470.6855 | 133.1406 | 119.7649
140.176 | 470.8441 | 134.1315 | 121.0805
141.176 | 471.0338 | 135.0924 | 122.3863
142.176 | 471.1888 | 135.9871 | 123.6613
143.176 | 471.2766 | 136.9179 | 124.9109
144.176 | 471.315 | 137.8148 | 126.1191
145.176 | 471.4537 | 138.7066 | 127.2891
146.176 | 471.8309 | 139.6498 | 128.4316
147.176 | 472.1556 | 140.5749 | 129.5522
148.176 | 472.348 | 141.5055 | 130.6487
149.176 | 472.5104 | 142.4379 | 131.7157
150.176 | 472.6003 | 143.3648 | 132.739
151.176 | 472.5986 | 144.2963 | 133.737
152.176 | 472.7491 | 145.2503 | 134.7135
153.176 | 472.567 | 146.182 | 135.6651
154.176 | 472.3319 | 147.1067 | 136.5981
155.176 | 472.4061 | 148.0657 | 137.5354
156.176 | 472.3839 | 149.0019 | 138.4701
157.176 | 472.2641 | 149.9239 | 139.4152
158.176 | 472.2995 | 150.9031 | 140.3592
159.176 | 472.406 | 151.8477 | 141.302
160.176 | 472.4038 | 152.8017 | 142.2595
161.176 | 472.2651 | 153.7932 | 143.2041
162.176 | 472.2996 | 154.7914 | 144.1415
163.176 | 472.2402 | 155.8102 | 145.1003
164.176 | 472.4051 | 156.8011 | 146.0459
165.176 | 472.6164 | 157.7928 | 147.0007
166.176 | 472.6835 | 158.7439 | 147.952
167.176 | 472.5708 | 159.6718 | 148.9089
168.176 | 472.3534 | 160.5535 | 149.8576
169.176 | 472.4746 | 161.4319 | 150.8029
170.176 | 472.3659 | 162.2866 | 151.7338
171.176 | 472.2758 | 163.1214 | 152.6527
172.176 | 472.3799 | 163.8751 | 153.5428
173.176 | 472.2263 | 164.611 | 154.4384
174.176 | 472.0437 | 165.242 | 155.317
175.176 | 471.9453 | 165.8717 | 156.1974
176.176 | 471.9283 | 166.5093 | 157.0629
177.176 | 471.7818 | 167.1537 | 157.8991
178.176 | 471.8236 | 167.8276 | 158.7315
179.176 | 471.9365 | 168.5009 | 159.5552
180.176 | 471.8946 | 169.1861 | 160.354
181.176 | 471.9513 | 169.8653 | 161.1196
182.176 | 471.817 | 170.5443 | 161.8696
183.176 | 471.8521 | 171.2201 | 162.5965
184.176 | 472.103 | 171.8826 | 163.3218
185.176 | 472.3069 | 172.5595 | 164.0351
186.176 | 472.4256 | 173.2191 | 164.7389
187.176 | 472.6129 | 173.8998 | 165.4211
188.176 | 472.7422 | 174.5436 | 166.0871
189.176 | 472.7712 | 175.1542 | 166.7461
190.176 | 472.7328 | 175.7598 | 167.3997
191.176 | 472.7166 | 176.3361 | 168.037
192.176 | 472.6554 | 176.9221 | 168.6809
193.176 | 472.7094 | 177.5055 | 169.3246
194.176 | 472.8239 | 178.0766 | 169.9821
195.176 | 472.833 | 178.5953 | 170.6192
196.176 | 472.9799 | 179.0899 | 171.2461
197.176 | 472.943 | 179.5312 | 171.869
198.176 | 472.8271 | 179.9205 | 172.4631
199.176 | 472.6921 | 180.2979 | 173.0193
200.176 | 472.6515 | 180.6971 | 173.5152
201.176 | 472.7435 | 181.2234 | 173.9408
202.176 | 472.6075 | 181.7705 | 174.3698
203.176 | 472.6474 | 182.4497 | 174.7532
204.176 | 472.6098 | 183.1847 | 175.0382
205.176 | 472.4949 | 183.9698 | 175.4514
206.176 | 472.2423 | 184.9044 | 175.9783
207.176 | 472.049 | 185.9534 | 176.5287
208.176 | 472.0415 | 187.0555 | 177.0087
209.176 | 472.0382 | 188.1676 | 177.6127
210.176 | 472.1269 | 189.2904 | 178.1792
211.176 | 472.1777 | 190.3767 | 178.7774
212.176 | 472.0277 | 191.5182 | 179.4188
213.176 | 472.0145 | 192.6237 | 179.928
214.176 | 472.2116 | 193.6451 | 180.3149
215.176 | 472.216 | 194.7468 | 180.2882
216.176 | 472.1394 | 195.8668 | 179.8685
217.176 | 472.1853 | 196.8467 | 179.6441
218.176 | 472.0561 | 197.9096 | 179.3885
219.176 | 472.0174 | 198.9781 | 179.6086
220.176 | 472.0872 | 199.9778 | 179.8358
221.176 | 471.9686 | 200.8833 | 180.1554
222.176 | 471.9695 | 201.9413 | 180.8648
223.176 | 471.9394 | 202.9073 | 180.7359
224.176 | 471.8328 | 203.847 | 179.8536
225.176 | 471.7632 | 204.4236 | 180.4664
226.176 | 471.8399 | 205.3041 | 180.3234
227.176 | 471.8881 | 206.1279 | 180.5568
228.176 | 471.9964 | 206.7237 | 182.1955
229.176 | 472.1908 | 207.6164 | 182.3234
230.176 | 472.349 | 208.4795 | 182.9186
231.176 | 472.3424 | 209.0422 | 183.6006
232.176 | 472.3634 | 209.7451 | 184.819
233.176 | 472.2981 | 210.5575 | 185.6103
234.176 | 472.2074 | 211.303 | 185.7656
235.176 | 472.0801 | 212.04 | 186.2802
236.176 | 471.895 | 212.7678 | 186.5765
237.176 | 471.7758 | 213.6037 | 186.9491
238.176 | 471.6148 | 214.206 | 187.4883
239.176 | 471.529 | 214.8056 | 188.0736
240.176 | 471.6474 | 215.4975 | 188.8746
241.176 | 471.7918 | 216.304 | 189.5545
242.176 | 472.0628 | 216.982 | 190.5658
243.176 | 471.9624 | 217.4773 | 191.2814
244.176 | 471.9197 | 218.1683 | 191.5092
245.176 | 472.0906 | 218.9033 | 191.3061
246.176 | 471.9401 | 219.589 | 190.8165
247.176 | 471.8707 | 220.0064 | 191.8776
248.176 | 471.8201 | 220.5127 | 192.8831
249.176 | 471.4881 | 221.23 | 193.3287
250.176 | 471.4935 | 221.7988 | 194.5759
251.176 | 471.5139 | 222.6267 | 194.3865
252.176 | 471.4319 | 223.2432 | 195.069
253.176 | 471.5272 | 223.8332 | 196.4111
254.176 | 471.8276 | 224.3673 | 196.72
255.176 | 471.8623 | 224.9422 | 197.5651
256.176 | 471.9252 | 225.6896 | 198.6313
257.176 | 471.9027 | 226.3032 | 198.633
258.176 | 471.9724 | 227.0237 | 198.8631
259.176 | 471.979 | 227.6767 | 199.3458
260.176 | 471.9628 | 228.3338 | 199.2723
261.176 | 471.9458 | 228.9878 | 199.1552
262.176 | 471.9827 | 229.4612 | 199.6837
263.176 | 471.7567 | 230.0075 | 201.0395
264.176 | 471.4529 | 230.5891 | 202.4016
265.176 | 471.4892 | 231.2017 | 203.5098
266.176 | 471.5696 | 231.7162 | 204.2225
267.176 | 471.4295 | 231.6605 | 205.3413
268.176 | 471.1341 | 232.4882 | 205.9806
269.176 | 471.0753 | 233.2545 | 205.7712
270.176 | 471.1151 | 233.8984 | 205.4045
271.176 | 471.2731 | 234.4669 | 206.0264
272.176 | 471.1959 | 235.0247 | 206.7513
273.176 | 471.0777 | 235.7393 | 207.1167
274.176 | 471.1023 | 236.3632 | 207.1367
275.176 | 471.0338 | 236.921 | 207.944
276.176 | 471.0823 | 237.7108 | 207.8076
277.176 | 471.2011 | 238.1983 | 207.7597
278.176 | 471.2557 | 238.6714 | 208.8449
279.176 | 471.2161 | 239.1784 | 209.4116
280.176 | 471.2495 | 239.5472 | 210.8553
281.176 | 471.1816 | 240.2576 | 211.7945
282.176 | 470.9999 | 240.8767 | 212.135
283.176 | 471.0626 | 241.5857 | 212.5883
284.176 | 471.0848 | 241.9703 | 212.7962
285.176 | 471.1891 | 242.5205 | 213.1963
286.1917 | 471.3158 | 243.1099 | 214.0803
287.176 | 471.2749 | 243.776 | 214.6443
288.176 | 471.4138 | 244.545 | 214.5499
289.176 | 471.3644 | 245.0659 | 215.4493
290.176 | 471.2733 | 245.6841 | 215.649
291.176 | 471.517 | 246.366 | 215.9189
292.176 | 471.7239 | 246.7851 | 216.7187
293.176 | 471.848 | 247.2914 | 217.9593
294.176 | 471.8045 | 248.0162 | 218.0716
295.176 | 471.6057 | 248.8568 | 218.5321
296.176 | 471.4766 | 249.5155 | 218.3799
297.176 | 471.535 | 250.277 | 218.1438
298.176 | 471.409 | 250.858 | 218.5597
299.176 | 471.3243 | 251.4939 | 218.4369
300.176 | 471.0672 | 251.8637 | 218.8999
301.176 | 471.1744 | 252.2933 | 219.4206
302.176 | 471.2481 | 253.0162 | 218.0206
303.176 | 471.3057 | 253.8369 | 219.4812
304.176 | 471.3136 | 254.4289 | 220.1833
305.176 | 471.1586 | 255.3299 | 220.4136
306.176 | 471.2283 | 256.7574 | 219.4552
307.176 | 471.3105 | 257.2045 | 220.7291
308.176 | 471.2195 | 258.701 | 221.6344
309.176 | 471.3193 | 259.4106 | 222.2658
310.176 | 471.3473 | 260.7334 | 222.7695
311.176 | 471.4033 | 262.2183 | 223.9688
312.176 | 471.3766 | 263.6994 | 224.2109
313.176 | 471.307 | 264.8029 | 224.4746
314.176 | 471.4032 | 265.0696 | 225.7704
315.176 | 471.2513 | 266.7515 | 225.5732
316.176 | 471.31 | 267.9567 | 225.2242
317.176 | 471.1589 | 268.4443 | 224.7036
318.176 | 471.2024 | 268.4095 | 224.767
319.176 | 471.1846 | 270.0538 | 225.4248
320.176 | 471.1715 | 271.0056 | 226.8852
321.176 | 471.261 | 272.3103 | 227.8534
322.176 | 471.1957 | 273.3823 | 229.1542
323.176 | 471.3083 | 273.8307 | 230.1498
324.176 | 471.0477 | 275.1841 | 230.3109
325.176 | 471.0789 | 275.9115 | 231.8482
326.176 | 471.0739 | 277.0193 | 232.3765
327.176 | 471.1879 | 278.2307 | 233.7133
328.176 | 471.1054 | 278.8063 | 234.3468
329.176 | 471.0208 | 279.0968 | 234.3103
330.176 | 471.0108 | 280.7409 | 233.6377
331.176 | 470.9275 | 281.4953 | 234.0917
332.176 | 470.7726 | 282.1043 | 235.4847
333.176 | 470.7506 | 281.6342 | 236.152
334.176 | 470.8166 | 282.0394 | 237.1594
335.176 | 470.935 | 283.0032 | 238.1366
336.176 | 470.9376 | 282.8216 | 238.5539
337.176 | 470.8729 | 283.8945 | 237.6447
338.176 | 470.8048 | 283.8654 | 238.9856
339.176 | 470.7665 | 283.9286 | 238.663
340.176 | 470.6651 | 286.0445 | 238.0251
341.176 | 470.3772 | 287.7951 | 238.2817
342.176 | 470.2735 | 288.3676 | 239.3578
343.176 | 470.1782 | 290.0441 | 239.126
344.176 | 470.0366 | 290.0747 | 240.2033
345.176 | 470.0855 | 291.3244 | 240.8579
346.176 | 470.1741 | 292.3456 | 241.5124
347.176 | 470.2345 | 292.4514 | 242.416
348.176 | 469.9488 | 294.0349 | 242.1662
349.176 | 469.819 | 293.8738 | 243.5369
350.176 | 469.7292 | 294.0743 | 244.1631
351.176 | 469.8518 | 294.7232 | 243.8078
352.176 | 469.8566 | 294.9748 | 244.3317
353.176 | 469.705 | 295.7132 | 244.3271
354.176 | 469.5568 | 295.6966 | 245.8899
355.176 | 469.5408 | 296.79 | 245.6667
356.176 | 469.5585 | 297.948 | 246.1872
357.176 | 469.4417 | 297.4956 | 246.5618
358.176 | 469.5165 | 297.1481 | 245.679
359.176 | 469.6918 | 297.9618 | 246.0982
360.176 | 469.913 | 298.9094 | 246.7584
361.176 | 470.1215 | 299.0966 | 247.0005
362.176 | 470.1428 | 299.4713 | 247.7963
363.176 | 470.1527 | 299.9067 | 248.9427
364.176 | 470.3047 | 300.1481 | 249.5001
365.176 | 470.4339 | 299.787 | 250.1746
366.176 | 470.3864 | 298.7336 | 251.2432
367.176 | 470.202 | 300.3926 | 251.1292
368.176 | 470.1357 | 301.0697 | 251.6968
369.176 | 470.0804 | 301.853 | 251.9979
370.176 | 470.0398 | 303.0929 | 252.2752
371.176 | 469.9967 | 302.7256 | 252.1115
372.176 | 470.0416 | 302.5683 | 252.2961
373.176 | 469.9463 | 303.2766 | 253.7072
374.176 | 469.9199 | 302.9253 | 254.1737
375.176 | 469.9917 | 304.5063 | 255.2285
376.176 | 470.0199 | 304.5621 | 255.9086
377.176 | 469.951 | 305.1586 | 255.6729
378.176 | 469.9594 | 306.331 | 255.7337
379.176 | 470.0558 | 305.6453 | 254.5826
380.176 | 470.118 | 304.715 | 256.6723
381.176 | 470.1001 | 306.135 | 257.0607
382.176 | 470.1801 | 305.4172 | 257.3756
383.176 | 470.2624 | 305.7234 | 256.6625
384.176 | 470.3188 | 306.4824 | 257.3243
385.176 | 470.399 | 306.5457 | 257.6431
386.176 | 470.2601 | 306.6546 | 258.2155
387.176 | 470.2597 | 306.636 | 257.7389
388.176 | 470.3182 | 306.719 | 257.6008
389.176 | 470.3013 | 306.7962 | 257.8585
390.176 | 470.2579 | 307.4746 | 257.9574
391.176 | 470.4466 | 306.1578 | 258.1303
392.176 | 470.3651 | 305.6067 | 258.7922
393.176 | 470.3827 | 305.4742 | 259.7466
394.176 | 470.392 | 304.2586 | 261.2986
395.176 | 470.2065 | 305.0746 | 261.5431
396.176 | 470.1476 | 305.6879 | 262.8068
397.176 | 470.1997 | 306.5371 | 262.0706
398.176 | 470.2567 | 308.3487 | 261.4989
399.176 | 470.1709 | 307.0479 | 261.8418
400.176 | 469.9487 | 306.2853 | 261.5031
401.176 | 469.8692 | 306.2179 | 261.8372
402.176 | 469.8583 | 308.3612 | 261.4896
403.176 | 469.8766 | 309.8946 | 261.9138
404.176 | 470.0118 | 310.1842 | 261.7087
405.176 | 470.1179 | 310.898 | 261.6698
406.176 | 470.0817 | 311.8158 | 261.735
407.176 | 469.9744 | 312.9696 | 262.8607
408.176 | 469.8716 | 313.469 | 264.7644
409.176 | 470.0073 | 315.2067 | 266.2916
410.176 | 469.9448 | 315.0833 | 266.4561
411.176 | 469.9347 | 315.733 | 266.9341
412.176 | 469.905 | 315.8541 | 266.3452
413.176 | 469.925 | 315.4562 | 268.7379
414.176 | 469.9365 | 316.2385 | 268.5271
415.176 | 469.8701 | 316.2222 | 268.5676
416.176 | 469.8649 | 316.2902 | 269.1909
417.176 | 469.9777 | 317.6879 | 270.6492
418.176 | 470.0868 | 318.8421 | 271.6414
419.176 | 470.1733 | 317.6044 | 272.2752
420.176 | 470.2352 | 318.0729 | 272.7563
421.176 | 470.283 | 318.6967 | 273.5635
422.176 | 470.4031 | 318.5074 | 274.7495
423.176 | 470.2958 | 318.0077 | 274.5065
424.176 | 470.2408 | 316.9203 | 275.3379
425.176 | 470.1343 | 317.8196 | 275.1979
426.176 | 470.2903 | 317.5877 | 274.8346
427.176 | 470.1124 | 318.9357 | 274.203
428.176 | 469.7934 | 320.218 | 273.8547
429.176 | 469.556 | 320.9988 | 274.6923
430.176 | 469.6641 | 321.8172 | 275.4365
431.176 | 469.7257 | 323.1921 | 276.6688
432.176 | 469.7027 | 323.6345 | 276.884
433.176 | 469.667 | 322.8499 | 277.1468
434.176 | 469.6052 | 321.7275 | 277.9523
435.176 | 469.4331 | 321.6928 | 277.6091
436.176 | 469.383 | 322.479 | 277.6503
437.176 | 469.3846 | 323.0531 | 277.3519
438.176 | 469.498 | 323.2229 | 278.9029
439.176 | 469.6084 | 322.9768 | 278.6535
440.176 | 469.7503 | 324.261 | 279.1224
441.176 | 469.8729 | 324.9813 | 279.0373
442.176 | 469.7812 | 326.5121 | 279.3643
443.176 | 469.9048 | 327.2779 | 278.9887
444.176 | 470.0483 | 327.3053 | 279.7469
445.176 | 470.1748 | 325.657 | 281.5271
446.176 | 470.1122 | 326.9539 | 281.3674
447.176 | 470.2165 | 326.6884 | 281.605
448.176 | 470.0851 | 325.3136 | 281.839
449.176 | 470.0377 | 326.0335 | 281.475
450.176 | 469.9546 | 326.3327 | 282.2434
451.176 | 470.0233 | 328.8946 | 283.7933
452.176 | 470.0253 | 329.808 | 284.7886
453.176 | 470.0319 | 330.3364 | 284.0173
454.176 | 469.9154 | 330.2548 | 284.2797
455.176 | 469.9417 | 329.452 | 283.5846
456.176 | 470.0779 | 330.3969 | 284.1775
457.176 | 470.1527 | 331.1752 | 284.1335
458.176 | 470.0557 | 331.0372 | 283.4172
459.176 | 470.0965 | 332.0162 | 283.506
460.176 | 470.2688 | 331.2414 | 285.0792
461.176 | 470.1016 | 333.3413 | 283.5065
462.176 | 470.1079 | 330.1594 | 284.2379
463.176 | 470.0256 | 329.1885 | 283.8405
464.176 | 469.8847 | 329.7073 | 285.0658
465.176 | 469.8715 | 331.5567 | 285.4175
466.176 | 469.7868 | 331.0366 | 286.3298
467.176 | 469.919 | 331.2934 | 287.1284
468.176 | 469.7548 | 332.5273 | 287.5472
469.176 | 469.6144 | 333.257 | 287.0171
470.176 | 469.5488 | 333.8448 | 287.6905
471.176 | 469.5225 | 332.3529 | 288.787
472.176 | 469.482 | 332.5199 | 288.1441
473.176 | 469.3483 | 333.6931 | 288.6215
474.176 | 469.2713 | 334.095 | 289.0432
475.176 | 469.3272 | 335.3458 | 289.2402
476.176 | 469.3964 | 337.1194 | 289.9613
477.176 | 469.1655 | 335.7257 | 290.1188
478.176 | 469.251 | 338.0667 | 292.2273
479.176 | 469.3827 | 338.7694 | 292.5734
480.176 | 469.5296 | 339.2049 | 292.425
481.176 | 469.4441 | 339.358 | 292.2563
482.176 | 469.4666 | 338.6321 | 293.1021
483.176 | 469.4755 | 336.5245 | 292.5879
484.176 | 469.6986 | 337.1713 | 291.8818
485.176 | 469.6939 | 338.0354 | 291.6734
486.176 | 469.601 | 339.5488 | 291.4452
487.176 | 469.486 | 339.6345 | 291.1194
488.176 | 469.5059 | 339.2322 | 290.8858
489.176 | 469.544 | 340.8402 | 290.6261
490.176 | 469.5135 | 341.063 | 290.2571
491.176 | 469.5943 | 340.6894 | 289.9941
492.176 | 469.5898 | 338.3899 | 291.0516
493.176 | 469.627 | 337.3371 | 291.1272
494.176 | 469.5009 | 336.7543 | 290.8399
495.176 | 469.5847 | 338.0274 | 291.261
496.176 | 469.8566 | 340.1377 | 291.3788
497.176 | 470.0718 | 341.2287 | 292.2604
498.176 | 470.1395 | 338.6083 | 293.2606
499.176 | 470.331 | 338.0922 | 293.6758
500.176 | 470.3891 | 339.2814 | 294.3713
501.176 | 470.5519 | 339.5952 | 296.0948
502.176 | 470.8416 | 340.965 | 296.8301
503.176 | 470.9166 | 340.5199 | 295.944
504.176 | 470.7982 | 340.4939 | 295.8369
505.176 | 470.6977 | 340.2109 | 296.2306
506.176 | 470.749 | 339.2595 | 296.8046
507.176 | 470.8695 | 339.545 | 297.3766
508.176 | 470.9938 | 341.1899 | 297.4142
509.176 | 470.78 | 339.7815 | 299.0329
510.176 | 470.7152 | 341.2521 | 297.8905
511.176 | 470.7595 | 341.5578 | 298.6686
512.176 | 470.7694 | 342.4397 | 298.5941
513.176 | 470.8035 | 342.3414 | 298.3868
514.176 | 470.7285 | 340.495 | 298.2159
515.176 | 470.7579 | 339.2739 | 298.3103
516.176 | 470.6013 | 340.5788 | 298.5505
517.176 | 470.2747 | 340.9685 | 299.1586
518.176 | 470.3542 | 339.7438 | 299.7553
519.176 | 470.4136 | 337.7911 | 300.8495
520.176 | 470.3757 | 339.1369 | 302.2415
521.176 | 470.2576 | 340.5862 | 302.2189
522.176 | 470.2007 | 341.1522 | 302.4426
523.176 | 470.0842 | 342.1332 | 303.2866
524.176 | 470.0831 | 343.2774 | 303.1598
525.176 | 469.9447 | 342.904 | 303.5712
526.176 | 469.8572 | 344.1473 | 303.0275
527.176 | 470.0394 | 343.7143 | 302.7337
528.176 | 470.1603 | 346.1125 | 302.0029
529.176 | 470.0712 | 346.6125 | 302.5874
530.176 | 470.0616 | 346.2473 | 302.6303
531.176 | 470.2149 | 345.2176 | 304.4907
532.176 | 470.3388 | 344.6795 | 305.2189
533.176 | 470.4199 | 344.7316 | 303.935
534.176 | 470.3749 | 345.8189 | 302.9401
535.176 | 470.4217 | 346.1205 | 304.3312
536.176 | 470.4868 | 347.5752 | 303.6514
537.176 | 470.5934 | 346.9109 | 303.5533
538.176 | 470.6149 | 347.2369 | 304.109
539.176 | 470.5409 | 347.7188 | 304.0045
540.176 | 470.4851 | 348.9755 | 305.3628
541.176 | 470.6953 | 349.0896 | 305.7101
542.176 | 470.725 | 349.9502 | 306.5885
543.176 | 470.7166 | 349.355 | 305.8473
544.176 | 470.7958 | 349.3393 | 306.0722
545.176 | 470.7254 | 346.8289 | 306.6259
546.176 | 470.7159 | 347.827 | 305.9649
547.176 | 470.8546 | 348.1331 | 305.2223
548.176 | 470.8712 | 346.6365 | 305.9037
549.176 | 470.902 | 346.0686 | 306.6169
550.176 | 470.8432 | 345.1813 | 307.2588
551.176 | 470.7701 | 346.4553 | 306.4267
552.176 | 470.7367 | 347.9211 | 307.233
553.176 | 470.6359 | 346.812 | 309.4965
554.176 | 470.5899 | 346.5372 | 310.3021
555.176 | 470.7028 | 348.0171 | 310.9743
556.176 | 470.6395 | 349.8173 | 310.8277
557.176 | 470.5305 | 348.7298 | 312.479
558.176 | 470.4113 | 349.4584 | 313.0522
559.176 | 470.4773 | 351.1858 | 313.6041
560.176 | 470.4189 | 350.9814 | 312.9863
561.176 | 470.4422 | 351.3089 | 312.5824
562.176 | 470.3186 | 350.6412 | 311.8995
563.176 | 470.4673 | 349.6791 | 312.2988
564.176 | 470.5975 | 351.4839 | 311.9493
565.176 | 470.494 | 351.2016 | 311.6016
566.176 | 470.4051 | 352.9112 | 311.8865
567.176 | 470.323 | 351.9332 | 312.6184
568.176 | 470.1468 | 350.7666 | 312.5771
569.176 | 470.1423 | 350.0507 | 312.1131
570.176 | 469.9899 | 350.0039 | 310.9304
571.176 | 470.0119 | 350.6396 | 311.3979
572.176 | 469.9875 | 349.5376 | 312.0278
573.176 | 469.4617 | 350.9437 | 311.8651
574.176 | 469.4909 | 352.3794 | 311.7769
575.176 | 469.4526 | 354.15 | 311.4037
576.176 | 469.4553 | 354.4699 | 312.0698
577.176 | 469.661 | 354.7166 | 312.7846
578.176 | 469.916 | 354.8514 | 312.2765
579.176 | 469.8778 | 354.4134 | 312.5506
580.176 | 469.8438 | 354.6026 | 310.5552
581.176 | 469.7718 | 352.8133 | 310.4239
582.176 | 469.809 | 351.588 | 311.4605
583.176 | 469.8246 | 351.5718 | 311.461
584.176 | 469.7022 | 352.5949 | 311.7528
585.176 | 469.8669 | 351.0579 | 312.0211
586.176 | 470.0705 | 351.0925 | 311.0236
587.176 | 470.3252 | 350.3928 | 311.2734
588.176 | 470.3126 | 350.4898 | 313.015
589.176 | 470.0915 | 351.0303 | 313.3788
590.176 | 470.0979 | 351.0469 | 312.8556
591.176 | 469.9998 | 349.8131 | 314.8428
592.176 | 470.0691 | 351.377 | 313.3121
593.176 | 470.1341 | 351.5419 | 314.5122
594.176 | 470.022 | 351.0964 | 314.7319
595.176 | 469.7894 | 350.5623 | 316.0853
596.176 | 469.7714 | 350.5529 | 317.133
597.176 | 469.8334 | 350.2959 | 317.0842
598.176 | 469.8803 | 350.6456 | 316.8171
599.176 | 469.9235 | 351.7093 | 317.4845
600.176 | 469.8619 | 352.0578 | 317.8161
601.176 | 469.7239 | 352.3727 | 317.4829
602.176 | 469.6349 | 350.5636 | 318.1532
603.176 | 469.575 | 347.9472 | 318.9838
604.176 | 469.6931 | 348.7489 | 319.3151
605.176 | 469.7379 | 349.9245 | 319.0312
606.176 | 469.6055 | 351.4521 | 319.8703
607.176 | 469.5489 | 352.4377 | 319.5288
608.176 | 469.5637 | 351.4621 | 321.7238
609.176 | 469.5969 | 350.8927 | 322.8209
610.176 | 469.5919 | 351.241 | 323.0522
611.176 | 469.5321 | 352.8564 | 322.373
612.176 | 469.4891 | 353.9689 | 321.7129
613.176 | 469.3402 | 353.9334 | 320.6432
614.176 | 469.46 | 354.8765 | 320.5713
615.176 | 469.4677 | 355.3194 | 320.7276
616.176 | 469.3562 | 354.2802 | 321.052
617.176 | 469.3944 | 353.3597 | 321.7652
618.176 | 469.5144 | 355.3993 | 320.6874
619.176 | 469.5846 | 354.8275 | 321.1038
620.176 | 469.5643 | 354.8698 | 322.1505
621.176 | 469.7023 | 355.3527 | 323.311
622.176 | 469.8562 | 357.3943 | 324.4624
623.176 | 470.1759 | 358.1603 | 323.1769
624.176 | 470.2594 | 358.8881 | 323.3274
625.176 | 470.2534 | 358.9687 | 323.0357
626.176 | 470.3612 | 360.1055 | 322.7731
627.176 | 470.33 | 358.226 | 323.02
628.176 | 470.3337 | 358.8226 | 322.8332
629.176 | 470.4307 | 358.9998 | 323.1996
630.176 | 470.5587 | 358.6088 | 322.4509
631.176 | 470.5862 | 357.7328 | 322.259
632.176 | 470.4993 | 359.1332 | 323.984
633.176 | 470.3882 | 359.4911 | 324.7793
634.176 | 470.1807 | 359.2643 | 324.9285
635.176 | 470.1405 | 359.6669 | 324.6026
636.176 | 470.1155 | 360.8401 | 324.4465
637.176 | 469.9964 | 360.8961 | 324.1832
638.176 | 469.741 | 359.44 | 324.5516
639.176 | 469.7082 | 361.4594 | 325.0644
640.176 | 469.5471 | 362.1926 | 326.0493
641.176 | 469.6172 | 363.8337 | 326.5342
642.176 | 469.6255 | 364.4734 | 326.5123
643.176 | 469.7485 | 365.9726 | 327.5172
644.176 | 469.8822 | 365.8861 | 327.8017
645.176 | 469.9763 | 366.5042 | 329.1657
646.176 | 470.1021 | 365.573 | 328.6749
647.176 | 470.1028 | 366.7792 | 328.6311
648.176 | 470.1643 | 365.4124 | 329.23
649.176 | 470.1286 | 365.3665 | 327.6076
650.176 | 470.0741 | 365.0979 | 327.2252
651.176 | 470.0792 | 364.516 | 326.9572
652.176 | 469.9927 | 365.8943 | 326.8086
653.176 | 469.847 | 366.2855 | 327.6076
654.176 | 469.9362 | 366.7877 | 328.3452
655.176 | 470.0489 | 366.2709 | 328.8537
656.176 | 469.9871 | 367.6281 | 328.265
657.176 | 469.7941 | 368.8713 | 328.0112
658.176 | 469.7241 | 368.2932 | 326.8698
659.176 | 469.5888 | 367.3065 | 328.847
660.176 | 469.5525 | 367.0578 | 329.5848
661.176 | 469.5541 | 367.1769 | 329.877
662.176 | 469.3936 | 366.2816 | 330.7341
663.176 | 469.3053 | 367.4761 | 331.2675
664.176 | 469.2112 | 368.7023 | 331.0547
665.176 | 469.0286 | 369.1612 | 330.5237
666.176 | 468.8503 | 368.7202 | 330.1474
667.176 | 468.8683 | 369.2989 | 330.2986
668.176 | 469.0046 | 368.9797 | 329.7602
669.176 | 469.0717 | 369.2502 | 329.3553
670.176 | 469.0986 | 368.8984 | 329.7791
671.176 | 469.2873 | 370.09 | 331.1117
672.176 | 469.289 | 371.1973 | 331.4729
673.176 | 469.5224 | 371.6806 | 332.2689
674.176 | 469.6681 | 371.9839 | 332.4505
675.176 | 469.6177 | 371.3453 | 333.3774
676.176 | 469.5216 | 371.1156 | 333.0283
677.176 | 469.5684 | 371.641 | 332.4312
678.176 | 469.7271 | 370.9277 | 331.7152
679.176 | 469.8835 | 370.8523 | 332.5103
680.176 | 470.1737 | 372.5411 | 331.9559
681.176 | 470.3612 | 371.0352 | 334.1061
682.176 | 470.4649 | 371.325 | 335.4807
683.176 | 470.5011 | 372.2052 | 335.0541
684.176 | 470.2988 | 371.779 | 336.7229
685.176 | 470.3557 | 372.9022 | 336.0101
686.176 | 470.2298 | 373.4652 | 335.0564
687.176 | 470.2498 | 373.8876 | 335.8903
688.176 | 470.206 | 374.4603 | 334.2709
689.176 | 470.2542 | 374.3264 | 335.1794
690.176 | 470.3009 | 373.6314 | 335.0805
691.176 | 470.1784 | 373.829 | 334.4189
692.176 | 470.098 | 373.5307 | 333.3542
693.176 | 469.932 | 373.2783 | 334.5585
694.176 | 469.4558 | 373.6483 | 333.6311
695.176 | 469.3097 | 373.1118 | 333.6769
696.176 | 469.3078 | 374.2649 | 333.785
697.176 | 469.4476 | 375.0643 | 333.8198
698.176 | 469.3164 | 375.0092 | 333.4736
699.176 | 469.5022 | 376.3768 | 333.3185
700.176 | 469.6837 | 375.4948 | 334.4728
701.176 | 469.7767 | 375.5854 | 334.9756
702.176 | 469.8259 | 376.0748 | 335.1158
703.176 | 469.8914 | 376.5795 | 335.0165
704.176 | 469.932 | 377.0088 | 333.769
705.176 | 469.965 | 376.9452 | 334.7781
706.176 | 470.0053 | 377.2684 | 335.0042
707.176 | 470.1103 | 377.7036 | 334.7463
708.176 | 470.1827 | 377.5655 | 335.3501
709.176 | 470.101 | 378.1305 | 334.3959
710.176 | 469.979 | 378.6932 | 334.6166
711.176 | 470.1631 | 378.8781 | 334.7668
712.176 | 470.3039 | 379.147 | 334.6814
713.176 | 470.4635 | 380.413 | 333.9115
714.176 | 470.587 | 380.577 | 333.0364
715.176 | 470.6321 | 379.781 | 335.1447
716.176 | 470.746 | 379.3111 | 336.5922
717.176 | 470.7782 | 379.3727 | 336.7395
718.176 | 470.838 | 379.7464 | 335.9276
719.176 | 470.7768 | 380.2656 | 335.7781
720.176 | 470.9512 | 379.6741 | 336.6
721.176 | 470.9439 | 378.2762 | 338.1554
722.176 | 470.8684 | 379.6158 | 338.2202
723.176 | 470.8343 | 380.9474 | 338.7031
724.176 | 471.0694 | 382.2632 | 337.8083
725.176 | 471.015 | 383.2529 | 336.6159
726.1917 | 470.9382 | 383.4098 | 338.1235
727.176 | 470.9698 | 383.3733 | 339.1353
728.176 | 471.0313 | 383.8221 | 339.9695
729.176 | 470.7666 | 384.0676 | 340.715
730.176 | 470.6058 | 384.8747 | 340.7373
731.176 | 470.561 | 385.3626 | 339.5951
732.176 | 470.4031 | 385.7591 | 339.1852
733.176 | 470.2665 | 385.3835 | 340.2748
734.176 | 470.278 | 385.8092 | 340.5948
735.176 | 470.1876 | 386.6877 | 340.3539
736.176 | 470.0006 | 386.4918 | 339.942
737.176 | 469.8961 | 386.0539 | 341.6871
738.176 | 469.7909 | 386.3806 | 343.1831
739.176 | 469.9083 | 386.7849 | 342.9744
740.176 | 469.8862 | 387.1312 | 341.4027
741.176 | 469.9679 | 387.2197 | 341.0557
742.176 | 469.9376 | 387.1879 | 340.8089
743.176 | 469.788 | 386.1893 | 340.9583
744.176 | 469.8113 | 385.7353 | 343.0059
745.176 | 469.7261 | 386.4115 | 342.1095
746.176 | 469.585 | 386.469 | 341.4541
747.176 | 469.6328 | 387.2985 | 339.5031
748.176 | 469.6613 | 387.5214 | 338.173
749.176 | 469.5802 | 387.7268 | 338.2847
750.176 | 469.3551 | 388.3772 | 338.7862
751.176 | 469.3324 | 388.7295 | 338.5358
752.176 | 469.3687 | 388.9911 | 338.1898
753.176 | 469.4225 | 389.1927 | 337.926
754.176 | 469.2803 | 389.4825 | 337.747
755.176 | 469.3672 | 390.2446 | 339.4785
756.176 | 469.5588 | 391.1776 | 339.827
757.176 | 469.7474 | 391.8365 | 339.1514
758.176 | 469.8159 | 391.7734 | 339.7956
759.176 | 469.8993 | 392.0786 | 339.237
760.176 | 470.009 | 392.2432 | 340.4582
761.176 | 470.0094 | 392.429 | 340.5369
762.176 | 469.9313 | 393.2821 | 339.9148
763.176 | 469.7945 | 393.1701 | 341.075
764.176 | 469.8399 | 393.5081 | 341.4753
765.176 | 469.7 | 394.0595 | 341.134
766.176 | 469.6759 | 393.3832 | 341.135
767.176 | 469.5279 | 393.5823 | 342.8996
768.176 | 469.3578 | 393.9709 | 343.5503
769.176 | 469.0882 | 394.4234 | 343.1095
770.176 | 469.1773 | 394.6542 | 342.5594
771.176 | 469.4915 | 395.3831 | 342.3994
772.176 | 469.4293 | 396.0727 | 343.4064
773.176 | 469.4298 | 395.649 | 344.7725
774.176 | 469.3434 | 395.9171 | 345.48
775.176 | 469.4659 | 396.2641 | 345.2425
776.176 | 469.2715 | 396.3362 | 345.0334
777.176 | 469.2637 | 395.3874 | 344.5989
778.176 | 469.1762 | 396.1308 | 343.954
779.176 | 469.2991 | 396.667 | 343.6367
780.176 | 469.3904 | 397.5764 | 342.7781
781.176 | 469.5644 | 397.2723 | 343.1782
782.176 | 469.6686 | 396.6325 | 343.8321
783.176 | 469.741 | 396.4653 | 345.0416
784.176 | 469.8352 | 396.6112 | 345.1287
785.176 | 469.7258 | 396.8051 | 345.3424
786.176 | 469.7627 | 396.4623 | 345.5906
787.176 | 469.914 | 397.1862 | 345.1518
788.176 | 469.9488 | 397.7441 | 344.9367
789.176 | 470.0306 | 397.7755 | 345.2702
790.176 | 470.0653 | 395.9367 | 346.3737
791.176 | 470.0153 | 395.823 | 346.3711
792.176 | 469.7656 | 396.1359 | 346.0012
793.176 | 469.5802 | 396.3251 | 346.1999
794.176 | 469.5762 | 395.4388 | 346.2613
795.176 | 469.7481 | 394.8956 | 346.5176
796.176 | 469.818 | 394.4683 | 346.9703
797.176 | 469.9274 | 393.8591 | 348.4248
798.176 | 469.9442 | 393.2221 | 349.1497
799.176 | 469.9957 | 393.1023 | 349.8794
800.176 | 470.0511 | 393.2311 | 349.4621
801.176 | 470.1455 | 393.4956 | 348.6791
802.176 | 470.0347 | 394.191 | 348.1716
803.176 | 469.8904 | 393.5546 | 348.0365
804.176 | 469.8822 | 392.5516 | 349.1701
805.176 | 469.6893 | 391.8452 | 349.2122
806.176 | 469.6483 | 391.5598 | 349.863
807.176 | 469.3637 | 390.9909 | 349.822
808.176 | 469.4609 | 391.2191 | 349.0075
809.176 | 469.385 | 390.6192 | 349.2819
810.176 | 469.495 | 389.6799 | 350.2633
811.176 | 469.5755 | 389.6545 | 350.4378
812.176 | 469.7746 | 389.968 | 350.7043
813.176 | 469.7497 | 390.1334 | 351.2195
814.176 | 469.7077 | 389.2418 | 351.374
815.176 | 469.6854 | 390.2742 | 352.0619
816.176 | 469.7498 | 389.57 | 352.2441
817.176 | 469.6261 | 389.9377 | 352.2891
818.176 | 469.5828 | 389.9962 | 352.8597
819.176 | 469.5286 | 390.2766 | 353.9916
820.176 | 469.5775 | 391.1483 | 354.4877
821.176 | 469.7481 | 390.4404 | 355.4328
822.176 | 469.9451 | 390.419 | 354.7729
823.176 | 469.8518 | 388.5892 | 354.5565
824.176 | 469.8332 | 388.467 | 354.8496
825.176 | 469.8179 | 388.6362 | 355.5747
826.176 | 469.8028 | 388.4752 | 356.1322
827.176 | 469.7142 | 387.8387 | 356.6364
828.176 | 469.6752 | 387.9176 | 356.5642
829.176 | 469.8714 | 387.9155 | 356.6273
830.176 | 469.7225 | 387.7152 | 355.993
831.176 | 469.6075 | 387.4804 | 356.4085
832.176 | 469.5111 | 386.3952 | 356.7944
833.176 | 469.5168 | 386.2973 | 356.1941
834.176 | 469.444 | 385.1095 | 356.0015
835.176 | 469.6197 | 384.9099 | 356.403
836.176 | 469.7398 | 384.8338 | 356.7883
837.176 | 469.837 | 384.854 | 356.6196
838.176 | 469.8482 | 385.2399 | 357.8608
839.176 | 469.9546 | 385.9155 | 358.2608
840.176 | 469.91 | 385.8869 | 359.0668
841.176 | 469.7056 | 383.905 | 360.1879
842.176 | 469.7845 | 385.1958 | 361.05
843.176 | 470.0696 | 385.8556 | 360.0123
844.176 | 469.8944 | 386.0148 | 359.2193
845.176 | 470.0315 | 384.5228 | 359.9782
846.176 | 470.1427 | 384.3487 | 360.0453
847.176 | 470.064 | 384.1084 | 359.7235
848.176 | 469.9331 | 384.581 | 359.8062
849.176 | 470.0309 | 385.4468 | 359.2857
850.176 | 470.0909 | 386.2089 | 359.3714
851.176 | 470.0491 | 386.1992 | 359.8057
852.176 | 470.0003 | 385.9468 | 360.1081
853.176 | 469.9045 | 386.0205 | 359.2541
854.176 | 469.9953 | 385.9631 | 359.1797
855.176 | 470.0506 | 385.7712 | 358.314
856.176 | 470.0487 | 386.4299 | 358.3366
857.176 | 470.1463 | 386.028 | 358.4841
858.176 | 470.0282 | 386.4134 | 359.3094
859.176 | 470.1082 | 386.8806 | 359.3397
860.176 | 470.1531 | 386.683 | 359.5021
861.176 | 470.209 | 386.5954 | 359.3764
862.176 | 470.1473 | 386.2017 | 359.5351
863.176 | 470.3116 | 386.0603 | 359.3782
864.176 | 470.396 | 386.6143 | 358.9626
865.176 | 470.5294 | 386.7911 | 358.6688
866.176 | 470.6356 | 386.8629 | 358.3464
867.176 | 470.5778 | 387.485 | 358.0513
868.176 | 470.5074 | 386.517 | 358.5041
869.176 | 470.5849 | 387.2149 | 358.2699
870.176 | 470.6545 | 387.4886 | 358.5122
871.176 | 470.5493 | 387.57 | 358.6695
872.176 | 470.4007 | 388.0075 | 359.4385
873.176 | 470.4441 | 388.5229 | 360.1785
874.176 | 470.4557 | 388.2336 | 360.688
875.176 | 470.5367 | 388.7543 | 361.2469
876.176 | 470.7067 | 388.6444 | 361.8357
877.176 | 470.6215 | 388.8916 | 361.4888
878.176 | 470.6321 | 387.7486 | 361.4982
879.176 | 470.4983 | 387.474 | 361.2782
880.176 | 470.2432 | 387.2931 | 361.1759
881.176 | 470.1705 | 386.7749 | 361.2604
882.176 | 470.1247 | 385.732 | 361.7275
883.176 | 470.283 | 386.229 | 362.0106
884.176 | 470.3084 | 386.9288 | 362.1599
885.176 | 470.3174 | 387.4125 | 361.867
886.176 | 470.1973 | 387.1082 | 362.3022
887.176 | 470.3023 | 386.0948 | 362.3525
888.176 | 470.2533 | 386.4993 | 361.4307
889.176 | 470.1764 | 386.4802 | 361.316
890.176 | 470.1064 | 386.2578 | 361.5094
891.176 | 469.9257 | 387.0141 | 360.9249
892.176 | 470.0479 | 386.4376 | 361.1584
893.176 | 470.1507 | 386.5692 | 362.0621
894.176 | 469.954 | 387.0471 | 361.9437
895.176 | 469.8646 | 387.358 | 361.5707
896.176 | 469.9234 | 387.6786 | 361.4024
897.176 | 469.8819 | 387.8441 | 361.277
898.176 | 469.9463 | 387.2871 | 361.1297
899.176 | 469.878 | 387.122 | 361.7793
900.176 | 469.708 | 387.6565 | 361.7565
901.176 | 469.8186 | 388.0067 | 362.0937
902.176 | 469.9298 | 387.7378 | 362.7072
903.176 | 469.8358 | 386.83 | 362.7037
904.176 | 469.9622 | 386.0672 | 362.41
905.176 | 469.946 | 386.4895 | 362.4279
906.176 | 470.0416 | 387.3989 | 362.5892
907.176 | 470.0055 | 387.6276 | 362.3781
908.176 | 469.94 | 387.5319 | 362.4446
909.176 | 469.9566 | 387.0943 | 363.0796
910.176 | 469.9753 | 387.1034 | 363.4889
911.176 | 469.9886 | 386.9574 | 362.9924
912.176 | 469.9996 | 386.4439 | 362.5714
913.176 | 470.0057 | 387.3287 | 361.7693
914.176 | 469.8554 | 386.0281 | 362.7021
915.176 | 469.9022 | 386.4777 | 363.0471
916.176 | 469.9171 | 386.6842 | 362.5956
917.176 | 469.7917 | 386.9562 | 362.4299
918.176 | 469.7794 | 387.02 | 362.4376
919.176 | 469.7119 | 387.2552 | 362.597
920.176 | 469.5757 | 386.7391 | 362.4161
921.176 | 469.5316 | 387.0376 | 362.7009
922.176 | 469.5361 | 386.9927 | 362.5665
923.176 | 469.383 | 387.248 | 362.6525
924.176 | 469.5337 | 386.5443 | 362.6042
925.176 | 469.6344 | 387.0974 | 362.2075
926.176 | 469.5592 | 387.1536 | 362.0485
927.176 | 469.5884 | 386.8647 | 362.464
928.176 | 469.7077 | 387.814 | 362.0942
929.176 | 469.841 | 388.0053 | 361.347
930.176 | 470.0373 | 389.0557 | 360.6128
931.176 | 470.1707 | 388.4256 | 360.743
932.176 | 470.2817 | 387.9066 | 360.563
933.176 | 470.4004 | 386.3843 | 361.4857
934.176 | 470.4996 | 386.7822 | 361.215
935.176 | 470.4739 | 387.7764 | 361.1377
936.176 | 470.3685 | 388.1851 | 361.0709
937.176 | 470.1767 | 388.1087 | 361.1562
938.176 | 469.9791 | 388.2116 | 361.8519
939.176 | 469.9237 | 387.4652 | 362.2484
940.176 | 469.8006 | 387.7755 | 362.3787
941.176 | 469.7289 | 387.9801 | 362.292
942.176 | 469.6834 | 388.2692 | 362.0009
943.176 | 469.6309 | 387.3343 | 362.2911
944.176 | 469.4589 | 387.0778 | 362.731
945.176 | 469.5012 | 387.3566 | 363.1944
946.176 | 469.4903 | 387.3778 | 363.2271
947.176 | 469.4252 | 388.4131 | 364.0151
948.176 | 469.4269 | 388.3265 | 363.9386
949.176 | 469.4228 | 388.8066 | 364.3554
950.176 | 469.4573 | 388.144 | 364.076
951.176 | 469.1466 | 387.4864 | 364.0777
952.176 | 469.163 | 387.1523 | 363.9463
953.176 | 469.2028 | 388.3857 | 363.1127
954.176 | 469.2094 | 388.6285 | 362.6529
955.176 | 468.9247 | 387.8995 | 362.8247
956.176 | 468.8462 | 387.5489 | 363.2111
957.176 | 468.9706 | 387.691 | 362.9276
958.176 | 468.8757 | 387.7865 | 362.9076
959.176 | 468.7554 | 388.5293 | 362.7547
960.176 | 468.7613 | 388.5365 | 362.6771
961.176 | 468.9539 | 387.9533 | 362.8587
962.176 | 469.1197 | 388.2492 | 363.128
963.176 | 469.0707 | 388.5031 | 363.2017
964.176 | 468.8818 | 388.3711 | 363.3351
965.176 | 468.6576 | 388.1026 | 363.2296
966.176 | 468.4406 | 388.5204 | 363.9864
967.176 | 468.2655 | 389.3069 | 363.5598
968.176 | 468.2499 | 389.4778 | 363.3278
969.176 | 468.1598 | 389.6058 | 363.4677
970.176 | 467.9869 | 389.1643 | 363.7423
971.176 | 468.011 | 389.2512 | 364.6256
972.176 | 468.1898 | 390.0465 | 364.3488
973.176 | 468.4381 | 389.6831 | 364.5484
974.176 | 468.6707 | 389.8624 | 364.4319
975.176 | 468.4353 | 388.7776 | 364.9055
976.176 | 468.4023 | 389.3408 | 365.1728
977.176 | 468.3714 | 388.7254 | 366.1472
978.176 | 468.4465 | 388.5944 | 365.877
979.176 | 468.5758 | 389.3078 | 364.6926
980.176 | 468.6911 | 389.2239 | 364.5378
981.176 | 468.6256 | 388.5975 | 364.2131
982.176 | 468.7236 | 389.2959 | 363.8816
983.176 | 468.8973 | 389.4294 | 363.7439
984.176 | 468.9942 | 389.6752 | 363.5591
985.176 | 469.1421 | 389.8284 | 363.6782
986.176 | 469.1325 | 389.6876 | 363.2355
987.176 | 469.3722 | 390.0363 | 363.4106
988.176 | 469.3406 | 390.2196 | 363.6265
989.176 | 469.1983 | 390.0991 | 363.3144
990.176 | 469.2155 | 390.1192 | 363.9106
991.176 | 469.2887 | 390.7679 | 363.9833
992.176 | 469.2269 | 390.7557 | 364.424
993.176 | 469.292 | 390.6335 | 363.9397
994.176 | 469.2981 | 390.3234 | 364.5128
995.176 | 469.3285 | 390.7103 | 364.452
996.176 | 469.2108 | 390.2373 | 365.3316
997.176 | 469.2044 | 390.8961 | 364.6174
998.176 | 469.1728 | 390.5829 | 365.2449
999.176 | 469.3304 | 390.516 | 365.6725
1000.176 | 469.6184 | 390.3454 | 365.6053
1001.176 | 469.7988 | 390.5216 | 365.3049
1002.176 | 469.8251 | 389.8599 | 365.6693
1003.176 | 469.7916 | 389.947 | 366.0893
1004.176 | 469.6286 | 390.1485 | 366.0181
1005.176 | 469.4262 | 390.0603 | 366.2886
1006.176 | 469.5704 | 389.9212 | 366.6622
1007.176 | 469.6072 | 390.428 | 365.7379
1008.176 | 469.4181 | 390.7325 | 365.9775
1009.176 | 469.3476 | 390.304 | 366.4413
1010.176 | 469.5168 | 390.2076 | 366.9191
1011.176 | 469.5874 | 389.9712 | 366.7443
1012.176 | 469.3386 | 389.8174 | 366.1309
1013.176 | 469.0693 | 390.2222 | 365.978
1014.176 | 468.783 | 390.6128 | 366.5578
1015.176 | 468.6419 | 391.1369 | 366.9481
1016.176 | 468.6771 | 391.1226 | 367.0316
1017.176 | 468.9162 | 391.4917 | 366.2334
1018.176 | 468.9908 | 391.3443 | 365.4878
1019.176 | 469.2152 | 391.0775 | 365.5344
1020.176 | 469.2658 | 390.9145 | 365.7767
1021.176 | 469.399 | 391.0181 | 366.156
1022.176 | 469.4683 | 391.1345 | 365.7454
1023.176 | 469.5443 | 390.7295 | 365.6165
1024.176 | 469.6396 | 391.1017 | 365.6414
1025.176 | 469.7363 | 391.8841 | 364.9014
1026.176 | 469.9148 | 391.7451 | 364.7391
1027.176 | 469.825 | 391.8166 | 364.5876
1028.176 | 469.7342 | 391.2997 | 364.3469
1029.176 | 469.6901 | 391.1816 | 364.1222
1030.176 | 469.7219 | 391.1137 | 363.6376
1031.176 | 469.7684 | 390.6561 | 363.9845
1032.176 | 469.973 | 390.936 | 363.6128
1033.176 | 470.0993 | 391.0347 | 363.8247
1034.176 | 470.0348 | 391.3124 | 363.958
1035.176 | 469.9387 | 390.7056 | 364.2857
1036.176 | 469.891 | 390.471 | 365.2527
1037.176 | 469.9831 | 390.8876 | 366.1775
1038.176 | 469.9257 | 391.5129 | 366.555
1039.176 | 469.7949 | 390.9539 | 367.1215
1040.176 | 469.6718 | 390.5775 | 367.3037
1041.176 | 469.511 | 391.3846 | 367.9924
1042.176 | 469.3807 | 391.3718 | 367.8474
1043.176 | 469.44 | 391.485 | 367.9849
1044.176 | 469.4056 | 391.5021 | 367.9861
1045.176 | 469.449 | 392.3311 | 367.6177
1046.176 | 469.3893 | 391.9971 | 366.8975
1047.176 | 469.2347 | 391.2683 | 366.5735
1048.176 | 469.1095 | 391.1252 | 366.9065
1049.176 | 469.0089 | 391.1933 | 366.8055
1050.176 | 468.9833 | 391.9751 | 366.4619
1051.176 | 468.9556 | 392.74 | 366.5029
1052.176 | 468.9984 | 392.7836 | 366.6341
1053.176 | 469.0568 | 392.9961 | 366.1943
1054.176 | 469.2661 | 392.7865 | 367.2334
1055.176 | 469.2148 | 391.7482 | 367.6093
1056.176 | 468.9909 | 391.4957 | 367.5707
1057.176 | 468.8815 | 391.8885 | 366.928
1058.176 | 468.9123 | 392.12 | 366.6044
1059.176 | 468.9654 | 391.9428 | 366.299
1060.176 | 469.0703 | 391.7486 | 365.9914
1061.176 | 469.183 | 391.1911 | 365.6053
1062.176 | 469.0656 | 391.7575 | 364.9917
1063.176 | 468.8973 | 392.2426 | 364.6873
1064.176 | 468.8084 | 391.7627 | 364.4233
1065.176 | 468.9256 | 392.1266 | 363.6879
1066.176 | 469.0899 | 392.3067 | 363.4095
1067.176 | 469.1493 | 391.9488 | 363.6243
1068.176 | 469.203 | 390.811 | 363.9169
1069.176 | 469.1143 | 391.4792 | 364.0991
1070.176 | 469.133 | 391.8003 | 364.0255
1071.176 | 469.2026 | 391.9284 | 364.2488
1072.176 | 469.303 | 392.1769 | 364.0081
1073.176 | 469.3003 | 391.5664 | 364.0844
1074.176 | 469.3399 | 390.7377 | 364.4218
1075.176 | 469.3612 | 391.597 | 364.0888
1076.176 | 469.2732 | 391.9045 | 363.7062
1077.176 | 469.1604 | 391.8419 | 363.4459
1078.176 | 469.2898 | 391.5619 | 363.6271
1079.176 | 469.3942 | 391.4842 | 364.6471
1080.176 | 469.3807 | 391.5819 | 364.6521
1081.176 | 469.4066 | 392.0764 | 364.7503
1082.176 | 469.465 | 392.8532 | 364.5412
1083.176 | 469.6479 | 392.7019 | 364.5422
1084.176 | 469.6229 | 391.8565 | 364.4432
1085.176 | 469.3627 | 392.1147 | 364.154
1086.176 | 469.2644 | 391.0173 | 364.182
1087.176 | 469.0867 | 390.4246 | 364.6845
1088.176 | 469.137 | 390.6636 | 364.7384
1089.176 | 469.2243 | 390.5838 | 364.7637
1090.176 | 469.2666 | 390.879 | 364.4632
1091.176 | 469.3072 | 390.5875 | 364.4164
1092.176 | 469.2126 | 390.4089 | 364.9041
1093.176 | 469.2479 | 391.1906 | 364.3901
1094.176 | 469.3199 | 390.515 | 364.5386
1095.176 | 469.4198 | 389.9509 | 364.6168
1096.176 | 469.2066 | 389.7664 | 364.9871
1097.176 | 468.9687 | 390.5541 | 365.201
1098.176 | 469.0988 | 390.7064 | 365.1955
1099.176 | 469.112 | 390.9718 | 364.8158
1100.176 | 469.1413 | 390.8811 | 365.4011
1101.176 | 469.059 | 390.8437 | 366.222
1102.176 | 469.1201 | 391.2078 | 365.8343
1103.176 | 469.0927 | 390.8596 | 365.9783
1104.176 | 469.1958 | 390.6409 | 366.0784
1105.176 | 469.2947 | 390.0678 | 365.9988
1106.176 | 469.4036 | 390.1685 | 365.7269
1107.176 | 469.5429 | 390.8293 | 365.9343
1108.176 | 469.6674 | 390.7317 | 366.209
1109.176 | 469.6558 | 390.8096 | 365.9836
1110.176 | 469.5529 | 390.827 | 366.394
1111.176 | 469.4877 | 390.7915 | 366.4044
1112.176 | 469.4896 | 391.1587 | 366.3004
1113.176 | 469.5731 | 391.1304 | 366.2965
1114.176 | 469.6914 | 391.4144 | 366.1281
1115.176 | 469.7407 | 392.055 | 365.6185
1116.176 | 469.6543 | 391.4401 | 366.074
1117.176 | 469.7062 | 391.5584 | 365.9629
1118.176 | 469.7314 | 391.2817 | 365.8164
1119.176 | 469.8978 | 391.3497 | 365.6868
1120.176 | 469.7412 | 391.2319 | 365.6815
1121.176 | 469.6702 | 391.7974 | 365.0102
1122.176 | 469.5391 | 391.2364 | 364.8041
1123.176 | 469.7525 | 390.8725 | 364.6251
1124.176 | 469.8243 | 391.4329 | 364.3782
1125.176 | 469.8492 | 391.848 | 364.207
1126.176 | 469.8701 | 391.2714 | 364.2337
1127.176 | 469.8317 | 391.0952 | 363.6412
1128.176 | 469.9973 | 391.1972 | 363.5942
1129.176 | 470.1256 | 391.261 | 363.9579
1130.176 | 470.1921 | 391.222 | 364.2966
1131.176 | 470.2726 | 391.283 | 364.5162
1132.176 | 470.359 | 390.9402 | 364.6777
1133.176 | 470.3593 | 390.419 | 364.803
1134.176 | 470.4284 | 390.3919 | 364.6135
1135.176 | 470.2455 | 390.5877 | 364.5709
1136.176 | 470.3027 | 390.6012 | 364.2593
1137.176 | 470.1378 | 390.0425 | 364.3437
1138.176 | 470.0678 | 389.6986 | 364.9168
1139.176 | 469.922 | 390.1327 | 365.0515
1140.176 | 469.8705 | 389.8424 | 364.9071
1141.176 | 469.962 | 390.146 | 364.4166
1142.176 | 469.8788 | 391.0343 | 364.3838
1143.176 | 469.8776 | 391.3736 | 363.8542
1144.176 | 469.8712 | 390.5856 | 364.4006
1145.176 | 469.9611 | 390.6242 | 364.0413
1146.176 | 469.973 | 390.4705 | 363.8229
1147.176 | 470.0223 | 391.0012 | 364.1002
1148.176 | 469.7813 | 391.192 | 363.7896
1149.176 | 469.7439 | 390.501 | 363.757
1150.176 | 469.9014 | 390.2916 | 364.3595
1151.176 | 470.0933 | 390.3876 | 364.4492
1152.176 | 470.2304 | 390.8585 | 363.9528
1153.176 | 470.2936 | 390.3803 | 364.0945
1154.176 | 470.181 | 391.0376 | 363.51
1155.176 | 470.2205 | 391.0122 | 363.4764
1156.176 | 470.4759 | 391.8736 | 363.3408
1157.176 | 470.511 | 392.2237 | 362.9671
1158.176 | 470.5809 | 391.7431 | 363.387
1159.176 | 470.516 | 391.6466 | 363.4176
1160.176 | 470.3915 | 392.0408 | 363.048
1161.176 | 470.4337 | 392.1333 | 362.4493
1162.176 | 470.4744 | 390.0439 | 362.8874
1163.176 | 470.4692 | 390.1198 | 363.0568
1164.176 | 470.2456 | 390.7068 | 362.8795
1165.176 | 470.2485 | 390.6759 | 362.5642
1166.176 | 470.0807 | 390.164 | 363.2739
1167.176 | 470.0589 | 390.5706 | 362.737
1168.176 | 469.8306 | 390.7684 | 362.5025
1169.176 | 469.7863 | 390.9262 | 362.0932
1170.176 | 469.8325 | 389.7134 | 362.1372
1171.176 | 469.8795 | 389.519 | 362.647
1172.176 | 469.8687 | 389.9551 | 363.0771
1173.176 | 469.7157 | 389.8172 | 362.8225
1174.176 | 469.6631 | 389.6122 | 362.5151
1175.176 | 469.8026 | 388.1287 | 363.4545
1176.176 | 469.9975 | 388.3578 | 364.4312
1177.176 | 470.0419 | 387.9268 | 364.8973
1178.176 | 470.17 | 387.2805 | 365.3568
1179.176 | 470.2196 | 387.7049 | 364.6436
1180.176 | 470.2051 | 387.5573 | 364.3917
1181.176 | 470.3324 | 388.1098 | 364.4761
1182.176 | 470.4012 | 388.8715 | 364.2177
1183.176 | 470.2148 | 389.4935 | 363.8954
1184.176 | 469.9253 | 388.4304 | 364.0383
1185.176 | 469.9199 | 388.5683 | 364.1335
1186.176 | 469.9852 | 389.4629 | 363.9684
1187.176 | 469.9208 | 389.4867 | 363.8839
1188.176 | 470.0407 | 389.6694 | 363.741
1189.176 | 470.0315 | 388.9307 | 363.9256
1190.176 | 470.0078 | 388.6293 | 363.7067
1191.176 | 470.0603 | 388.6265 | 363.2321
1192.176 | 470.1422 | 389.4783 | 363.1771
1193.176 | 470.2477 | 390.1291 | 363.1368
1194.176 | 470.2486 | 390.5606 | 362.418
1195.176 | 470.1232 | 390.6768 | 362.2819
1196.176 | 470.1111 | 390.2948 | 362.4446
1197.176 | 470.1786 | 390.2686 | 362.5347
1198.176 | 470.1073 | 389.6677 | 363.3243
1199.176 | 470.101 | 389.3771 | 363.3782
1200.176 | 470.1117 | 388.9886 | 363.3961
1201.176 | 469.9187 | 389.3706 | 363.2495
1202.176 | 469.7782 | 389.3541 | 363.259
1203.176 | 469.6217 | 388.8322 | 363.6702
1204.176 | 469.7659 | 389.6931 | 363.097
1205.176 | 469.747 | 389.1691 | 363.0397
1206.176 | 469.6805 | 389.7465 | 363.4737
1207.176 | 469.8169 | 390.8202 | 363.6868
1208.176 | 469.8167 | 390.6132 | 363.7117
1209.176 | 469.7513 | 390.3901 | 363.7976
1210.176 | 469.6872 | 390.2992 | 363.2671
1211.176 | 469.3787 | 390.1502 | 363.4555
1212.176 | 469.4911 | 389.4151 | 363.8938
1213.176 | 469.6361 | 388.733 | 364.4654
1214.176 | 469.4551 | 388.3862 | 364.579
1215.176 | 469.5546 | 389.0002 | 364.2808
1216.176 | 469.6454 | 388.5513 | 363.9843
1217.176 | 469.7739 | 389.1896 | 363.188
1218.176 | 469.6058 | 389.2213 | 363.4
1219.176 | 469.7316 | 388.4181 | 363.7288
1220.176 | 469.865 | 387.3447 | 363.7472
1221.176 | 469.7844 | 386.9732 | 363.7829
1222.176 | 469.8616 | 387.3377 | 364.1671
1223.176 | 470.0346 | 386.868 | 364.6896
1224.176 | 469.9079 | 386.693 | 364.503
1225.176 | 470.0572 | 386.77 | 364.7336
1226.176 | 470.0886 | 387.7146 | 364.5687
1227.176 | 470.0821 | 387.0121 | 364.984
1228.176 | 470.2984 | 386.9779 | 364.6226
1229.176 | 470.362 | 387.3265 | 364.0181
1230.176 | 470.4395 | 386.8089 | 363.9843
1231.176 | 470.3633 | 386.6175 | 364.1728
1232.176 | 470.4101 | 387.5197 | 364.6264
1233.176 | 470.5175 | 388.1522 | 364.4066
1234.176 | 470.4527 | 387.8981 | 364.5734
1235.176 | 470.4143 | 387.9733 | 364.4886
1236.176 | 470.3103 | 387.5446 | 364.7968
1237.176 | 470.3716 | 387.2876 | 364.5667
1238.176 | 470.3505 | 386.2362 | 364.7354
1239.176 | 470.4108 | 386.2424 | 364.409
1240.176 | 470.4898 | 385.9561 | 364.4218
1241.176 | 470.5192 | 385.6672 | 364.4593
1242.176 | 470.4898 | 385.3141 | 364.9253
1243.176 | 470.549 | 385.845 | 364.9589
1244.176 | 470.5373 | 386.193 | 364.8354
1245.176 | 470.5432 | 386.0417 | 364.2411
1246.176 | 470.5608 | 386.1591 | 364.1928
1247.176 | 470.3873 | 386.038 | 364.3328
1248.176 | 470.3756 | 385.7476 | 364.3277
1249.176 | 470.4367 | 385.811 | 364.2257
1250.176 | 470.3999 | 385.4381 | 364.3578
1251.176 | 470.3964 | 385.6798 | 364.7344
1252.176 | 470.1362 | 385.7729 | 364.7802
1253.176 | 470.0202 | 386.3866 | 364.3068
1254.176 | 470.016 | 386.4503 | 364.3518
1255.176 | 469.9694 | 387.1439 | 363.5911
1256.176 | 470.0787 | 387.2776 | 363.3999
1257.176 | 470.1709 | 386.6686 | 363.9894
1258.176 | 470.1529 | 385.6383 | 364.4033
1259.176 | 470.107 | 386.1005 | 365.2116
1260.176 | 469.9304 | 386.2282 | 365.0128
1261.176 | 470.0195 | 385.978 | 365.3967
1262.176 | 470.0866 | 385.9956 | 364.9031
1263.176 | 470.1247 | 385.8403 | 364.7249
1264.176 | 470.1946 | 385.8844 | 365.2141
1265.176 | 470.3282 | 385.4237 | 365.1
1266.176 | 470.472 | 385.7088 | 364.9097
1267.176 | 470.6092 | 385.4502 | 364.768
1268.176 | 470.5983 | 385.5196 | 364.553
1269.176 | 470.3278 | 385.4498 | 364.7992
1270.176 | 470.3943 | 385.2059 | 364.7627
1271.176 | 470.5886 | 385.7387 | 364.228
1272.176 | 470.5681 | 384.9742 | 364.0724
1273.176 | 470.5171 | 384.4778 | 363.7295
1274.176 | 470.4799 | 384.5872 | 364.0519
1275.176 | 470.1867 | 383.5242 | 364.2535
1276.176 | 470.2652 | 384.5328 | 364.1873
1277.176 | 470.1246 | 384.1217 | 364.3077
1278.176 | 470.0616 | 382.9299 | 364.63
1279.176 | 470.1945 | 383.0753 | 364.6911
1280.176 | 470.323 | 382.0458 | 365.0159
1281.176 | 470.3187 | 382.2502 | 365.2056
1282.176 | 470.2553 | 382.7992 | 364.8947
1283.176 | 470.1641 | 383.4859 | 364.4901
1284.176 | 470.0516 | 384.1204 | 364.39
1285.176 | 470.1751 | 382.8001 | 364.7057
1286.176 | 470.1653 | 383.652 | 364.9363
1287.176 | 470.1733 | 382.4408 | 365.433
1288.176 | 470.1267 | 383.1486 | 365.6056
1289.176 | 469.9968 | 382.8034 | 365.7011
1290.176 | 470.0174 | 383.6209 | 365.3378
1291.176 | 470.0721 | 384.5296 | 365.1685
1292.176 | 470.085 | 385.6041 | 364.1381
1293.176 | 470.0315 | 385.0323 | 364.3916
1294.176 | 470.005 | 384.9342 | 364.8398
1295.176 | 470.0538 | 384.4653 | 365.1258
1296.176 | 470.0684 | 383.7398 | 365.4541
1297.176 | 470.1742 | 383.3395 | 365.4246
1298.176 | 469.9819 | 382.7606 | 365.6892
1299.176 | 470.0313 | 383.4113 | 365.3891
1300.176 | 469.9022 | 383.4691 | 365.5558
1301.176 | 469.8952 | 384.097 | 365.3411
1302.176 | 469.975 | 384.5555 | 365.4827
1303.176 | 469.9313 | 384.518 | 365.2943
1304.176 | 469.9974 | 384.2134 | 365.4957
1305.176 | 469.9219 | 384.2832 | 366.3277
1306.176 | 469.8151 | 384.0751 | 366.6724
1307.176 | 469.7696 | 384.4425 | 366.5494
1308.176 | 469.7005 | 384.3032 | 366.217
1309.176 | 469.6346 | 384.5166 | 365.8639
1310.176 | 469.5037 | 384.4837 | 365.664
1311.176 | 469.5257 | 384.5543 | 365.5878
1312.176 | 469.6404 | 384.3491 | 365.7441
1313.176 | 469.8222 | 385.0074 | 366.1158
1314.176 | 469.7779 | 385.2202 | 365.5778
1315.176 | 469.6442 | 385.0467 | 365.4853
1316.176 | 469.6829 | 384.9931 | 365.3948
1317.176 | 469.7385 | 383.7822 | 366.0062
1318.176 | 469.705 | 383.0756 | 366.6796
1319.176 | 469.8961 | 384.2757 | 366.8542
1320.176 | 469.9692 | 383.8969 | 366.893
1321.176 | 469.8359 | 384.7604 | 366.6608
1322.176 | 469.5782 | 385.1496 | 366.267
1323.176 | 469.3945 | 385.4448 | 365.8278
1324.176 | 469.3795 | 385.3229 | 366.4243
1325.176 | 469.4613 | 383.174 | 366.9046
1326.176 | 469.5488 | 383.5962 | 367.0085
1327.176 | 469.3002 | 384.0955 | 366.6383
1328.176 | 469.0797 | 384.837 | 366.3295
1329.176 | 469.0981 | 384.7932 | 366.359
1330.176 | 469.2128 | 384.3159 | 366.2758
1331.176 | 469.0881 | 384.9382 | 366.6581
1332.176 | 468.8442 | 385.6242 | 366.8454
1333.176 | 468.7265 | 386.4105 | 366.9256
1334.176 | 468.8245 | 385.3956 | 366.9936
1335.176 | 468.8677 | 384.5107 | 366.5819
1336.176 | 468.7799 | 384.6889 | 366.137
1337.176 | 468.847 | 385.0814 | 366.2288
1338.176 | 468.8239 | 385.1524 | 365.8887
1339.176 | 468.7965 | 385.0221 | 365.5138
1340.176 | 468.7583 | 384.3169 | 365.6491
1341.176 | 468.6076 | 384.403 | 365.3255
1342.176 | 468.6004 | 385.1868 | 364.796
1343.176 | 468.7022 | 384.212 | 364.8104
1344.176 | 468.8336 | 383.5362 | 365.3586
1345.176 | 468.9315 | 383.2236 | 365.18
1346.176 | 469.0686 | 383.5702 | 364.8733
1347.176 | 469.1651 | 382.9513 | 364.943
1348.176 | 469.2197 | 382.5413 | 365.1959
1349.176 | 469.1653 | 382.8254 | 365.0607
1350.176 | 469.176 | 382.8519 | 365.1236
1351.176 | 469.2675 | 382.6102 | 365.5712
1352.176 | 469.3145 | 382.9724 | 365.1821
1353.176 | 469.5248 | 382.0523 | 364.9957
1354.176 | 469.4818 | 382.1391 | 364.5631
1355.176 | 469.545 | 381.5116 | 364.665
1356.176 | 469.4651 | 382.0518 | 364.5136
1357.176 | 469.5027 | 381.4629 | 364.4721
1358.176 | 469.3532 | 381.5446 | 364.4775
1359.176 | 469.4058 | 382.0036 | 364.5532
1360.176 | 469.3631 | 383.0525 | 363.9062
1361.176 | 469.1641 | 383.0056 | 363.9445
1362.176 | 469.1439 | 381.976 | 364.4115
1363.176 | 468.9191 | 382.0769 | 365.0422
1364.176 | 468.8638 | 382.0709 | 365.4103
1365.176 | 468.8488 | 382.5633 | 365.2656
1366.176 | 468.8555 | 382.0629 | 365.1463
1367.176 | 468.9238 | 382.4033 | 365.6545
1368.176 | 468.9706 | 381.394 | 366.1364
1369.176 | 469.1047 | 381.684 | 366.2598
1370.176 | 469.115 | 381.1279 | 366.1652
1371.176 | 469.1889 | 381.1857 | 365.6818
1372.176 | 469.2642 | 381.0554 | 365.389
1373.176 | 469.1726 | 381.3854 | 365.4976
1374.176 | 469.3113 | 380.9203 | 365.3056
1375.176 | 469.5227 | 380.8401 | 365.2957
1376.176 | 469.6754 | 380.749 | 365.5406
1377.176 | 469.6819 | 381.1949 | 365.2169
1378.176 | 469.5929 | 381.5764 | 365.1262
1379.176 | 469.4445 | 380.5769 | 365.3551
1380.176 | 469.3901 | 378.9459 | 365.438
1381.176 | 469.4094 | 379.2882 | 365.1565
1382.176 | 469.3756 | 378.5563 | 365.9643
1383.176 | 469.2471 | 378.2384 | 366.5275
1384.176 | 469.2893 | 377.9601 | 366.7533
1385.176 | 469.2148 | 379.0012 | 365.9968
1386.176 | 469.1398 | 380.368 | 365.3629
1387.176 | 469.208 | 379.3075 | 365.5736
1388.176 | 469.2767 | 377.6305 | 365.5058
1389.176 | 469.3587 | 377.4193 | 365.3758
1390.176 | 469.4785 | 378.0393 | 364.7715
1391.176 | 469.4701 | 378.3702 | 364.6246
1392.176 | 469.3798 | 379.0295 | 364.0968
1393.176 | 469.3544 | 378.8294 | 364.4189
1394.176 | 469.513 | 378.9599 | 364.7592
1395.176 | 469.6098 | 379.7382 | 364.9357
1396.176 | 469.5319 | 378.4083 | 365.2664
1397.176 | 469.6433 | 379.2145 | 365.9682
1398.176 | 469.7823 | 379.6705 | 366.0998
1399.176 | 469.8081 | 378.9069 | 366.2878
1400.176 | 469.7729 | 377.6475 | 366.6529
1401.176 | 469.7466 | 376.4984 | 367.3822
1402.176 | 469.8843 | 375.8129 | 367.8537
1403.176 | 469.6838 | 376.1524 | 367.3541
1404.176 | 469.5945 | 377.2587 | 367.0979
1405.176 | 469.3579 | 377.7496 | 366.886
1406.176 | 469.6074 | 378.774 | 366.6021
1407.176 | 469.6216 | 379.8867 | 366.0977
1408.176 | 469.4615 | 380.4322 | 365.6826
1409.176 | 469.1497 | 380.7312 | 365.3662
1410.176 | 469.0868 | 380.5013 | 364.7644
1411.176 | 469.1303 | 380.5628 | 365.0315
1412.176 | 469.2527 | 381.0415 | 365.3083
1413.176 | 469.3764 | 381.3757 | 364.9377
1414.176 | 469.455 | 381.4608 | 364.5193
1415.176 | 469.6591 | 379.6821 | 364.6939
1416.176 | 469.8665 | 377.897 | 365.4255
1417.176 | 469.7715 | 378.23 | 364.8688
1418.176 | 469.6621 | 378.2087 | 364.9126
1419.176 | 469.714 | 379.5339 | 365.3169
1420.176 | 469.8166 | 379.6906 | 365.7542
1421.176 | 469.8069 | 379.5205 | 366.0947
1422.176 | 469.6848 | 379.5708 | 365.9674
1423.176 | 469.6926 | 378.8372 | 365.912
1424.176 | 469.617 | 379.4977 | 365.9644
1425.176 | 469.6768 | 379.9177 | 365.5779
1426.176 | 469.7923 | 380.2706 | 365.4279
1427.176 | 469.7921 | 380.5818 | 365.3423
1428.176 | 469.7852 | 379.0832 | 366.0244
1429.176 | 469.9111 | 377.0833 | 366.1946
1430.176 | 469.9666 | 377.3347 | 366.2903
1431.176 | 469.91 | 377.4038 | 366.0294
1432.176 | 469.8026 | 378.8399 | 365.1582
1433.176 | 469.9622 | 378.2573 | 365.2507
1434.176 | 470.0435 | 377.9903 | 364.9644
1435.176 | 469.9458 | 378.3338 | 364.7181
1436.176 | 469.7598 | 377.9763 | 364.2159
1437.176 | 469.77 | 376.9162 | 364.5778
1438.176 | 469.627 | 376.2948 | 365.0051
1439.176 | 469.5095 | 377.3527 | 364.4415
1440.176 | 469.3559 | 377.9665 | 364.3571
1441.176 | 469.1591 | 378.583 | 364.1529
1442.176 | 469.1355 | 376.8854 | 364.4986
1443.176 | 469.2648 | 377.3322 | 364.9359
1444.176 | 469.2264 | 378.9685 | 364.7228
1445.176 | 469.4111 | 377.8739 | 364.7051
1446.176 | 469.5193 | 378.2003 | 365.4992
1447.176 | 469.4033 | 378.0854 | 365.577
1448.176 | 469.5674 | 378.2548 | 365.2046
1449.176 | 469.693 | 378.5759 | 365.1384
1450.176 | 469.6406 | 378.292 | 365.2778
1451.176 | 469.688 | 378.6224 | 364.7231
1452.176 | 469.8082 | 378.8524 | 364.4401
1453.176 | 469.5484 | 378.5323 | 364.5611
1454.176 | 469.5828 | 377.9165 | 364.6065
1455.176 | 469.7195 | 377.0299 | 365.2131
1456.176 | 469.7639 | 376.0797 | 365.5602
1457.176 | 469.9163 | 376.2163 | 365.4025
1458.176 | 470.013 | 375.9815 | 365.531
1459.176 | 469.9779 | 376.3241 | 365.6731
1460.176 | 469.8268 | 375.8289 | 365.7286
1461.176 | 469.9746 | 375.3465 | 365.6998
1462.176 | 470.0766 | 375.178 | 365.6067
1463.176 | 470.0002 | 375.4405 | 365.9782
1464.176 | 469.9112 | 375.4158 | 366.045
1465.176 | 469.8404 | 376.6026 | 365.9118
1466.176 | 469.7455 | 376.3445 | 365.7473
1467.176 | 469.7828 | 377.8214 | 364.8871
1468.176 | 469.8015 | 377.3461 | 365.424
1469.176 | 469.763 | 377.279 | 365.3212
1470.176 | 469.6585 | 375.6911 | 365.4982
1471.176 | 469.68 | 375.9313 | 365.4916
1472.176 | 469.8746 | 376.3082 | 365.9495
1473.176 | 470.0487 | 376.7252 | 366.4189
1474.176 | 470.0856 | 377.7012 | 367.0823
1475.176 | 470.0219 | 377.517 | 366.6399
1476.176 | 469.9867 | 377.6533 | 365.7642
1477.176 | 469.9598 | 377.8191 | 365.6212
1478.176 | 470.0698 | 378.0626 | 366.0805
1479.176 | 470.1366 | 378.3448 | 366.0094
1480.176 | 470.3234 | 377.4372 | 366.1351
1481.176 | 470.3123 | 377.1548 | 366.0101
1482.176 | 470.123 | 378.4064 | 366.0442
1483.176 | 470.1687 | 378.8918 | 365.9494
1484.176 | 470.2712 | 379.1933 | 365.787
1485.176 | 470.3004 | 378.9861 | 366.4541
1486.176 | 470.1085 | 378.5942 | 366.4563
1487.176 | 470.0715 | 378.3186 | 367.0126
1488.176 | 470.0873 | 378.727 | 366.9406
1489.176 | 470.2346 | 377.3944 | 367.0108
1490.176 | 470.3318 | 377.6044 | 366.8598
1491.176 | 470.4641 | 377.7025 | 366.8331
1492.176 | 470.3054 | 377.4206 | 366.6698
1493.176 | 470.2463 | 376.7123 | 366.8235
1494.176 | 470.2005 | 376.7518 | 366.459
1495.176 | 470.0523 | 377.5096 | 365.973
1496.176 | 470.0979 | 377.423 | 365.6703
1497.176 | 470.3216 | 377.9088 | 365.2466
1498.176 | 470.4206 | 375.785 | 365.4548
1499.176 | 470.3225 | 374.905 | 365.9139
1500.176 | 470.4373 | 375.6934 | 365.8553
1501.176 | 470.5631 | 374.7687 | 366.011
1502.176 | 470.5643 | 374.6656 | 366.6573
1503.176 | 470.4214 | 375.4248 | 366.5054
1504.176 | 470.2878 | 376.006 | 366.0346
1505.176 | 470.0522 | 373.132 | 366.0217
1506.176 | 470.0882 | 373.9299 | 366.07
1507.176 | 470.1456 | 374.6056 | 366.5822
1508.176 | 470.212 | 375.6624 | 366.2759
1509.176 | 470.2549 | 376.0556 | 366.8392
1510.176 | 470.0347 | 375.8979 | 366.3843
1511.176 | 469.9491 | 376.726 | 366.0833
1512.176 | 469.8184 | 376.2846 | 365.8883
1513.176 | 469.984 | 376.1125 | 365.0449
1514.176 | 469.8932 | 375.3731 | 365.1994
1515.176 | 469.7908 | 375.1843 | 365.4265
1516.176 | 469.9718 | 375.3935 | 365.0928
1517.176 | 470.0189 | 376.7715 | 364.8675
1518.176 | 470.0861 | 375.8563 | 364.6397
1519.176 | 470.1131 | 374.6886 | 364.9183
1520.176 | 470.1296 | 374.9581 | 365.1512
1521.176 | 470.0892 | 375.0091 | 364.9637
1522.176 | 470.1554 | 375.4571 | 364.9671
1523.176 | 470.0784 | 375.2267 | 364.8272
1524.176 | 470.0716 | 375.9632 | 364.5542
1525.176 | 470.0191 | 375.9177 | 364.6574
1526.176 | 470.1263 | 376.5272 | 364.5478
1527.176 | 470.1786 | 376.5163 | 364.1033
1528.176 | 470.2766 | 377.1381 | 363.7129
1529.176 | 470.3925 | 374.5462 | 364.3874
1530.176 | 470.5404 | 374.6773 | 364.5507
1531.176 | 470.4961 | 375.4843 | 365.1038
1532.176 | 470.6358 | 375.2521 | 364.9517
1533.176 | 470.9079 | 375.411 | 364.9889
1534.176 | 470.9659 | 376.2782 | 364.7095
1535.176 | 470.9228 | 374.6824 | 365.4492
1536.176 | 470.9984 | 373.8704 | 366.148
1537.176 | 471.019 | 374.4133 | 366.3077
1538.176 | 471.0215 | 374.6416 | 366.3821
1539.176 | 471.0636 | 375.5566 | 365.9843
1540.176 | 471.1213 | 375.591 | 365.8295
1541.176 | 470.9978 | 376.6168 | 366.1
1542.176 | 470.9384 | 377.0323 | 366.0842
1543.176 | 471.0321 | 376.2557 | 366.2303
1544.176 | 470.9287 | 375.5387 | 366.4345
1545.176 | 471.1501 | 374.7414 | 366.3816
1546.176 | 471.0799 | 375.7825 | 366.1424
1547.176 | 471.0432 | 375.3751 | 366.314
1548.176 | 470.8244 | 374.0336 | 366.5002
1549.176 | 470.4759 | 374.8787 | 366.3947
1550.176 | 470.2488 | 375.5695 | 366.3675
1551.176 | 470.2932 | 374.6833 | 366.3304
1552.176 | 470.3733 | 375.3228 | 366.1981
1553.176 | 470.2722 | 374.5722 | 366.9275
1554.176 | 470.2481 | 374.779 | 366.8315
1555.176 | 470.1828 | 375.3288 | 366.8505
1556.176 | 470.0851 | 374.4545 | 366.7878
1557.176 | 469.9268 | 374.1159 | 366.2816
1558.176 | 469.911 | 372.6072 | 366.7342
1559.176 | 469.9177 | 372.3034 | 367.2217
1560.176 | 469.9076 | 372.9994 | 367.2858
1561.176 | 469.9288 | 372.7149 | 367.5738
1562.176 | 469.9313 | 374.0568 | 366.9741
1563.176 | 470.0148 | 373.8083 | 367.1518
1564.176 | 470.0285 | 373.3647 | 367.3468
1565.176 | 469.9432 | 373.1956 | 367.2201
1566.176 | 470.0028 | 372.0616 | 367.3145
1567.176 | 470.0239 | 372.0225 | 367.8931
1568.176 | 469.9544 | 372.7378 | 367.4191
1569.176 | 470.0269 | 373.1168 | 367.3696
1570.176 | 470.008 | 373.9246 | 367.0911
1571.176 | 470.0969 | 375.148 | 366.7604
1572.176 | 469.8874 | 374.0857 | 366.8522
1573.176 | 469.695 | 373.3271 | 367.1646
1574.176 | 469.6591 | 373.7856 | 367.4761
1575.176 | 469.78 | 373.823 | 367.4795
1576.176 | 469.8843 | 372.6483 | 367.9348
1577.176 | 469.9733 | 372.0961 | 367.5679
1578.176 | 469.9289 | 373.5019 | 366.8019
1579.176 | 469.9037 | 373.6627 | 366.5448
1580.176 | 469.8944 | 373.2849 | 366.4993
1581.176 | 469.8636 | 372.8665 | 366.3752
1582.176 | 469.9236 | 373.9045 | 365.8848
1583.176 | 469.763 | 373.8958 | 366.0131
1584.176 | 469.7846 | 373.1355 | 365.8854
1585.176 | 469.8413 | 373.2178 | 365.6071
1586.176 | 469.842 | 373.2906 | 365.0784
1587.176 | 469.7724 | 371.5976 | 365.617
1588.176 | 469.8598 | 370.9418 | 365.6906
1589.176 | 469.9554 | 372.0108 | 364.7561
1590.176 | 470.0379 | 373.0506 | 365.0988
1591.176 | 470.1881 | 373.6314 | 365.2957
1592.176 | 470.102 | 374.5861 | 365.4833
1593.176 | 470.0462 | 375.7113 | 365.3489
1594.176 | 469.8508 | 376.0109 | 365.5504
1595.176 | 469.7092 | 376.6192 | 365.4846
1596.176 | 469.8131 | 376.5333 | 365.4037
1597.176 | 469.804 | 375.7307 | 365.4833
1598.176 | 469.9286 | 374.965 | 366.2766
1599.176 | 470.0082 | 373.8687 | 365.8923
1600.176 | 470.0567 | 372.9312 | 366.4039
1601.176 | 470.205 | 373.5902 | 367.2011
1602.176 | 470.2933 | 374.6519 | 367.5008
1603.176 | 470.539 | 375.3311 | 367.6997
1604.176 | 470.6957 | 376.0828 | 367.9221
1605.176 | 470.4837 | 376.8786 | 368.5447
1606.176 | 470.6876 | 375.8687 | 368.0352
1607.176 | 470.6636 | 375.7927 | 368.3739
1608.176 | 470.6205 | 375.129 | 368.557
1609.176 | 470.5375 | 374.644 | 369.1806
1610.176 | 470.4168 | 374.3423 | 368.7822
1611.176 | 470.3069 | 375.0111 | 368.6623
1612.176 | 470.2887 | 374.9016 | 368.6706
1613.176 | 470.0999 | 375.3112 | 368.3896
1614.176 | 470.1099 | 375.3258 | 368.2932
1615.176 | 469.8195 | 375.9369 | 368.0547
1616.176 | 469.6729 | 375.2412 | 368.33
1617.176 | 469.4457 | 375.844 | 367.4815
1618.176 | 469.4761 | 374.9932 | 367.373
1619.176 | 469.3768 | 375.4491 | 367.0859
1620.176 | 469.4236 | 375.8167 | 367.2296
1621.176 | 469.4736 | 376.4571 | 366.9554
1622.176 | 469.4753 | 377.0017 | 366.2596
1623.176 | 469.47 | 376.1101 | 365.9003
1624.176 | 469.463 | 373.7898 | 365.8058
1625.176 | 469.4228 | 373.7102 | 365.6905
1626.176 | 469.5973 | 374.4958 | 365.2528
1627.176 | 469.7766 | 374.4604 | 364.9553
1628.176 | 469.7658 | 373.6784 | 365.0232
1629.176 | 469.6075 | 373.3864 | 365.0012
1630.176 | 469.6433 | 372.9213 | 365.8469
1631.176 | 469.8251 | 374.2027 | 366.3031
1632.176 | 470.0231 | 374.5525 | 365.8295
1633.176 | 470.0568 | 374.5524 | 365.2622
1634.176 | 470.0676 | 375.3392 | 365.0565
1635.176 | 469.9516 | 374.9248 | 365.4785
1636.176 | 469.9712 | 375.0869 | 365.4249
1637.176 | 469.7938 | 375.2788 | 365.7334
1638.176 | 469.7999 | 374.946 | 365.9248
1639.176 | 469.6857 | 376.4301 | 365.5616
1640.176 | 469.7834 | 376.7146 | 365.552
1641.176 | 469.8063 | 375.6709 | 365.6199
1642.176 | 469.8117 | 375.2305 | 365.6761
1643.176 | 469.8434 | 375.0423 | 365.5319
1644.176 | 469.8361 | 374.2688 | 365.5981
1645.176 | 469.9076 | 373.2586 | 366.4453
1646.176 | 469.6478 | 373.2645 | 366.7244
1647.176 | 469.6899 | 372.7164 | 366.4454
1648.176 | 469.7441 | 371.0561 | 366.5444
1649.176 | 469.7147 | 371.2141 | 366.6725
1650.176 | 469.6908 | 372.7083 | 366.4799
1651.176 | 469.8091 | 373.106 | 365.9751
1652.176 | 469.8032 | 372.915 | 365.9098
1653.176 | 469.8349 | 372.4137 | 366.1887
1654.176 | 469.8363 | 371.8695 | 366.2632
1655.176 | 469.8045 | 373.2416 | 366.098
1656.176 | 469.8417 | 373.351 | 366.0876
1657.176 | 469.8184 | 373.8363 | 365.6398
1658.176 | 469.7996 | 373.5481 | 365.5182
1659.176 | 469.8008 | 373.4395 | 365.1257
1660.176 | 469.6774 | 373.6691 | 364.8659
1661.176 | 469.8653 | 372.6464 | 365.1441
1662.176 | 470.1407 | 373.1772 | 365.2457
1663.176 | 470.1667 | 374.1535 | 365.1499
1664.176 | 470.2924 | 373.7427 | 365.2072
1665.176 | 470.3141 | 374.1183 | 364.7038
1666.176 | 470.3276 | 374.1369 | 364.3222
1667.176 | 470.3062 | 373.1896 | 364.637
1668.176 | 470.4509 | 371.3286 | 365.6018
1669.176 | 470.4775 | 371.7563 | 366.1258
1670.176 | 470.4471 | 372.7557 | 365.8098
1671.176 | 470.4199 | 373.6523 | 365.6237
1672.176 | 470.2317 | 373.5536 | 365.0928
1673.176 | 470.3036 | 372.9253 | 365.0739
1674.176 | 470.2883 | 373.1526 | 364.8799
1675.176 | 470.4019 | 371.8933 | 364.9442
1676.176 | 470.5421 | 372.923 | 365.0164
1677.176 | 470.5516 | 372.8215 | 365.2928
1678.176 | 470.3983 | 372.7078 | 363.9101
1679.176 | 470.2357 | 372.935 | 364.1389
1680.176 | 470.2165 | 373.906 | 363.6776
1681.176 | 469.9944 | 374.4479 | 363.9482
1682.176 | 470.0046 | 374.4368 | 363.9046
1683.176 | 469.9347 | 373.1068 | 364.1462
1684.176 | 469.8845 | 373.2918 | 364.2647
1685.176 | 469.9153 | 373.0107 | 364.1759
1686.176 | 469.7468 | 370.6708 | 364.1606
1687.176 | 469.7923 | 371.0906 | 364.6619
1688.176 | 469.74 | 370.606 | 364.9884
1689.176 | 469.6626 | 371.1749 | 364.9142
1690.176 | 469.8155 | 373.2171 | 364.4103
1691.176 | 470.011 | 373.3189 | 364.365
1692.176 | 470.1146 | 373.0247 | 364.4932
1693.176 | 469.9664 | 371.6728 | 364.4413
1694.176 | 469.7889 | 371.2439 | 364.9162
1695.176 | 469.794 | 371.7075 | 365.1512
1696.176 | 469.925 | 371.6324 | 364.7978
1697.176 | 469.9357 | 372.1944 | 365.2269
1698.176 | 470.1232 | 372.558 | 365.1262
1699.176 | 470.4091 | 372.9497 | 364.9641
1700.176 | 470.4681 | 372.4767 | 364.8642
1701.176 | 470.5628 | 371.9903 | 364.9384
1702.176 | 470.6201 | 372.0852 | 364.5143
1703.176 | 470.6163 | 371.7009 | 364.7207
1704.176 | 470.5419 | 372.5254 | 364.4693
1705.176 | 470.4378 | 373.5128 | 364.4403
1706.176 | 470.3757 | 373.9624 | 364.4566
1707.176 | 470.1617 | 374.3243 | 364.229
1708.176 | 470.2217 | 374.7887 | 363.928
1709.176 | 470.2101 | 374.5451 | 364.0984
1710.176 | 470.105 | 374.4743 | 364.219
1711.176 | 470.083 | 374.326 | 364.291
1712.176 | 470.1886 | 374.5974 | 364.3944
1713.176 | 470.2853 | 375.5092 | 363.572
1714.176 | 470.2279 | 374.1032 | 363.4313
1715.176 | 470.1197 | 374.7283 | 364.2313
1716.176 | 470.1568 | 373.999 | 364.5569
1717.1917 | 470.1339 | 374.4245 | 364.6677
1718.176 | 470.1946 | 374.0004 | 365.0261
1719.176 | 470.137 | 375.0212 | 365.2709
1720.176 | 469.9922 | 375.0596 | 364.7505
1721.176 | 469.8231 | 375.4882 | 364.4926
1722.176 | 469.7018 | 374.4057 | 364.418
1723.176 | 469.5953 | 373.9295 | 364.4005
1724.176 | 469.5328 | 373.6678 | 365.1779
1725.176 | 469.4979 | 372.7319 | 365.1202
1726.176 | 469.4202 | 373.77 | 365.0796
1727.176 | 469.3282 | 373.881 | 364.304
1728.176 | 469.313 | 374.2066 | 363.6959
1729.176 | 469.4085 | 375.159 | 363.4998
1730.176 | 469.5458 | 375.5654 | 364.3119
1731.176 | 469.5372 | 375.8266 | 364.906
1732.176 | 469.6407 | 376.1753 | 364.7865
1733.176 | 469.7323 | 375.6873 | 365.1022
1734.176 | 469.6556 | 374.3454 | 365.5971
1735.176 | 469.9117 | 373.0964 | 365.5312
1736.176 | 469.9107 | 374.509 | 364.9902
1737.176 | 469.7743 | 374.1271 | 364.5992
1738.176 | 469.7399 | 373.6895 | 364.3794
1739.176 | 469.7967 | 372.7323 | 364.5995
1740.176 | 469.855 | 371.647 | 365.0144
1741.176 | 469.7416 | 372.3969 | 364.9655
1742.176 | 469.6768 | 372.7563 | 364.525
1743.176 | 469.5629 | 371.0614 | 364.5665
1744.176 | 469.5585 | 371.0644 | 363.6773
1745.176 | 469.6683 | 371.3739 | 363.4822
1746.176 | 469.8309 | 372.7925 | 363.5652
1747.176 | 469.8705 | 372.7493 | 363.4568
1748.176 | 469.8364 | 372.1655 | 363.1832
1749.176 | 469.9008 | 372.6026 | 363.2958
1750.176 | 469.9359 | 373.0686 | 362.9632
1751.176 | 469.9946 | 373.5129 | 362.8139
1752.176 | 470.0381 | 373.0489 | 363.1751
1753.176 | 470.0327 | 372.7097 | 363.358
1754.176 | 469.912 | 372.9138 | 363.5794
1755.176 | 469.7155 | 372.7157 | 363.5765
1756.176 | 469.3462 | 372.7344 | 363.7572
1757.176 | 469.3159 | 373.7136 | 363.4838
1758.176 | 469.4212 | 372.9803 | 363.2424
1759.176 | 469.6545 | 373.9303 | 363.0366
1760.176 | 469.6394 | 372.9112 | 363.4169
1761.176 | 469.6217 | 373.0571 | 363.9883
1762.176 | 469.6231 | 373.2887 | 363.6559
1763.176 | 469.5424 | 373.572 | 363.0994
1764.176 | 469.7318 | 373.9005 | 363.9466
1765.176 | 469.932 | 373.9827 | 363.7315
1766.176 | 469.9707 | 374.0837 | 363.4106
1767.176 | 470.0081 | 373.6987 | 363.26
1768.176 | 470.0575 | 373.3162 | 363.1828
1769.176 | 469.9317 | 373.4655 | 362.696
1770.176 | 469.8296 | 373.641 | 362.2525
1771.176 | 469.9636 | 373.591 | 362.3543
1772.176 | 470.1089 | 373.6035 | 362.0732
1773.176 | 469.9999 | 373.4355 | 362.7796
1774.176 | 470.0656 | 374.1451 | 362.04
1775.176 | 470.1992 | 373.9134 | 362.9379
1776.176 | 470.3441 | 372.723 | 363.3909
1777.176 | 470.3172 | 372.5772 | 363.4564
1778.176 | 470.4394 | 372.2538 | 363.1255
1779.176 | 470.3749 | 373.5389 | 363.0195
1780.176 | 470.4931 | 374.955 | 362.4634
1781.176 | 470.5575 | 375.2876 | 362.9951
1782.176 | 470.5167 | 375.305 | 363.0149
1783.176 | 470.4995 | 375.3048 | 363.4392
1784.176 | 470.4658 | 375.0731 | 362.9833
1785.176 | 470.4422 | 374.2756 | 363.7062
1786.176 | 470.2109 | 373.7624 | 363.7842
1787.176 | 470.0334 | 374.7733 | 363.6319
1788.176 | 469.9223 | 375.4672 | 363.7453
1789.176 | 469.8752 | 374.2983 | 363.9203
1790.176 | 469.8726 | 373.6861 | 363.8723
1791.176 | 469.8432 | 373.3094 | 363.3198
1792.176 | 469.9046 | 373.1565 | 363.8784
1793.176 | 469.8937 | 373.637 | 363.6267
1794.176 | 469.8876 | 373.6502 | 364.181
1795.176 | 469.7901 | 373.2701 | 363.8958
1796.176 | 469.6893 | 372.5453 | 363.8264
1797.176 | 469.4864 | 372.9141 | 364.3764
1798.176 | 469.5553 | 373.5859 | 364.3635
1799.176 | 469.4739 | 372.7855 | 364.0878
1800.176 | 469.4826 | 373.4429 | 364.359
1801.176 | 469.605 | 374.5718 | 364.4232
1802.176 | 469.5567 | 374.6168 | 364.7305
1803.176 | 469.6488 | 374.7663 | 364.4501
1804.176 | 469.6693 | 375.0962 | 364.8192
1805.176 | 469.4734 | 374.3162 | 364.7577
1806.176 | 469.3131 | 373.2771 | 365.1638
1807.176 | 469.1205 | 372.8422 | 365.3812
1808.176 | 469.0124 | 373.3279 | 365.1592
1809.176 | 469.0073 | 372.6044 | 365.2183
1810.176 | 469.1237 | 372.831 | 365.4302
1811.176 | 469.0144 | 372.3613 | 366.2255
1812.176 | 469.0692 | 373.0686 | 365.746
1813.176 | 469.2142 | 373.7801 | 365.3202
1814.176 | 469.2878 | 373.4561 | 365.497
1815.176 | 469.1608 | 373.2786 | 364.6287
1816.176 | 469.0849 | 373.1902 | 363.8526
1817.176 | 469.2159 | 374.3894 | 364.176
1818.176 | 469.261 | 374.5602 | 364.7344
1819.176 | 469.472 | 375.1601 | 365.3514
1820.176 | 469.4395 | 376.4414 | 364.6948
1821.176 | 469.5096 | 375.9289 | 364.6511
1822.176 | 469.5176 | 375.5186 | 364.8965
1823.176 | 469.6487 | 375.9965 | 365.239
1824.176 | 469.6949 | 374.241 | 365.5273
1825.176 | 469.6177 | 374.9495 | 365.5606
1826.176 | 469.6085 | 374.4044 | 365.2271
1827.176 | 469.5539 | 374.8839 | 364.9985
1828.176 | 469.4554 | 374.5726 | 365.959
1829.176 | 469.4211 | 374.9153 | 365.8495
1830.176 | 469.3185 | 375.2785 | 365.6819
1831.176 | 469.2788 | 375.5697 | 365.1462
1832.176 | 469.4143 | 374.9579 | 365.1869
1833.176 | 469.6137 | 375.6102 | 365.2988
1834.176 | 469.7713 | 374.9658 | 365.2252
1835.176 | 469.7416 | 375.5483 | 364.537
1836.176 | 469.6499 | 375.0984 | 364.1289
1837.176 | 469.5716 | 375.2842 | 364.3974
1838.176 | 469.57 | 375.4992 | 365.1962
1839.176 | 469.4948 | 376.3022 | 365.0327
1840.176 | 469.5338 | 377.3223 | 364.2808
1841.176 | 469.5793 | 377.2704 | 364.8024
1842.176 | 469.6637 | 376.674 | 365.1051
1843.176 | 469.5442 | 375.7084 | 365.998
1844.176 | 469.5661 | 376.0222 | 366.0003
1845.176 | 469.722 | 375.3563 | 366.0435
1846.176 | 469.6399 | 376.4048 | 365.4077
1847.176 | 469.6771 | 376.2959 | 365.8056
1848.176 | 469.5584 | 375.7095 | 365.5718
1849.176 | 469.4455 | 374.5002 | 365.3466
1850.176 | 469.5973 | 372.3946 | 364.8511
1851.176 | 469.8253 | 372.5794 | 364.2727
1852.176 | 469.666 | 372.905 | 364.4468
1853.176 | 469.566 | 373.4414 | 364.4799
1854.176 | 469.5885 | 373.1228 | 364.0555
1855.176 | 469.5736 | 371.673 | 364.5888
1856.176 | 469.5442 | 372.6202 | 364.3406
1857.176 | 469.5777 | 373.6751 | 363.9167
1858.176 | 469.6445 | 374.9765 | 363.4865
1859.176 | 469.6736 | 375.9167 | 363.1949
1860.176 | 469.7594 | 376.1999 | 362.7392
1861.176 | 469.9217 | 376.3794 | 362.6009
1862.176 | 469.9232 | 373.7643 | 363.5361
1863.176 | 469.8729 | 373.9628 | 363.7856
1864.176 | 469.8102 | 374.1128 | 364.4711
1865.176 | 469.7798 | 374.8835 | 364.4089
1866.176 | 469.7679 | 375.4254 | 363.9398
1867.176 | 469.806 | 375.5787 | 364.213
1868.176 | 469.9128 | 374.6523 | 364.6177
1869.176 | 469.9768 | 375.0995 | 363.8453
1870.176 | 469.9607 | 375.4342 | 363.7822
1871.176 | 469.8829 | 375.1066 | 364.265
1872.176 | 469.8899 | 375.3181 | 363.9899
1873.176 | 469.8699 | 375.3683 | 363.7322
1874.176 | 469.8648 | 376.5803 | 363.4689
1875.176 | 469.9098 | 376.9908 | 363.0993
1876.176 | 470.0375 | 375.9252 | 363.0982
1877.176 | 470.3163 | 375.2978 | 362.9987
1878.176 | 470.284 | 375.1091 | 363.005
1879.176 | 470.0163 | 374.6598 | 362.9513
1880.176 | 469.8521 | 374.9733 | 362.6645
1881.176 | 469.6951 | 374.7056 | 362.7722
1882.176 | 469.5795 | 373.004 | 362.5801
1883.176 | 469.4828 | 373.93 | 363.0072
1884.176 | 469.2446 | 374.1061 | 363.3324
1885.176 | 469.4261 | 373.2199 | 364.0038
1886.176 | 469.6519 | 374.2446 | 363.5809
1887.176 | 469.7678 | 375.3853 | 363.2727
1888.176 | 469.9285 | 375.7053 | 362.94
1889.176 | 470.0336 | 375.756 | 363.0602
1890.176 | 470.0717 | 374.8694 | 362.6706
1891.176 | 470.1162 | 375.3173 | 361.9305
1892.176 | 470.1514 | 376.3447 | 362.0053
1893.176 | 470.3353 | 376.7565 | 362.4036
1894.176 | 470.3399 | 377.4289 | 362.8856
1895.176 | 470.3851 | 376.8986 | 362.4314
1896.176 | 470.293 | 376.947 | 362.7642
1897.176 | 470.1996 | 376.8331 | 362.324
1898.176 | 470.2797 | 376.9782 | 362.6591
1899.176 | 470.1241 | 377.8104 | 361.9448
1900.176 | 470.1661 | 376.2122 | 362.3222
1901.176 | 470.3152 | 375.7454 | 362.26
1902.176 | 470.3124 | 375.8023 | 361.9211
1903.176 | 470.2372 | 375.6387 | 362.1742
1904.176 | 470.2488 | 375.667 | 363.0482
1905.176 | 470.4085 | 375.9455 | 363.6134
1906.176 | 470.3489 | 377.2616 | 363.3574
1907.176 | 470.2275 | 375.8916 | 363.744
1908.176 | 470.079 | 374.6988 | 363.9386
1909.176 | 469.7824 | 374.3587 | 363.8476
1910.176 | 469.7078 | 374.5829 | 363.7602
1911.176 | 469.575 | 374.2513 | 363.8294
1912.176 | 469.6247 | 374.9163 | 363.2616
1913.176 | 469.6666 | 375.3086 | 363.1088
1914.176 | 469.5464 | 375.5647 | 363.4119
1915.176 | 469.4145 | 375.0473 | 364.0316
1916.176 | 469.3257 | 375.5221 | 363.5049
1917.176 | 469.2924 | 374.9783 | 363.4776
1918.176 | 468.9988 | 374.0915 | 363.423
1919.176 | 468.9334 | 374.3766 | 362.973
1920.176 | 469.1282 | 373.1268 | 363.2256
1921.176 | 468.9696 | 372.4328 | 363.4336
1922.176 | 468.8432 | 372.2993 | 363.4836
1923.176 | 468.9085 | 370.9486 | 363.2555
1924.176 | 469.0257 | 372.0847 | 364.2496
1925.176 | 469.1067 | 372.3911 | 364.6822
1926.176 | 469.069 | 372.7751 | 364.8095
1927.176 | 469.1359 | 373.2976 | 364.5649
1928.176 | 469.0856 | 374.2098 | 364.1579
1929.176 | 469.2107 | 374.2179 | 364.254
1930.176 | 469.3408 | 374.2893 | 363.4657
1931.176 | 469.326 | 373.6277 | 363.4949
1932.176 | 469.3057 | 373.9876 | 363.4228
1933.176 | 469.4782 | 374.8895 | 363.2161
1934.176 | 469.5572 | 375.3541 | 363.3846
1935.176 | 469.636 | 374.5044 | 363.7729
1936.176 | 469.4118 | 374.8231 | 364.2882
1937.176 | 469.3906 | 374.5321 | 364.7113
1938.176 | 469.2096 | 372.996 | 365.0794
1939.176 | 468.9946 | 373.1455 | 365.315
1940.176 | 468.8339 | 374.2094 | 364.5402
1941.176 | 468.8361 | 374.1464 | 363.7409
1942.176 | 468.9221 | 374.2551 | 363.1701
1943.176 | 468.9887 | 374.1034 | 362.7354
1944.176 | 469.0892 | 373.846 | 362.5101
1945.176 | 469.0953 | 373.5107 | 362.8217
1946.176 | 469.0146 | 373.9485 | 362.6451
1947.176 | 469.0145 | 374.0044 | 362.3668
1948.176 | 468.9006 | 373.3115 | 362.5545
1949.176 | 469.0414 | 372.7366 | 362.8536
1950.176 | 469.0318 | 372.8905 | 363.0987
1951.176 | 469.0941 | 371.9385 | 362.8284
1952.176 | 469.1338 | 371.7713 | 362.2898
1953.176 | 469.1195 | 371.6817 | 362.1719
1954.176 | 468.986 | 372.9333 | 361.4184
1955.176 | 468.9729 | 372.9023 | 361.1563
1956.176 | 469.0493 | 373.2388 | 361.3939
1957.176 | 469.1413 | 372.9707 | 361.6297
1958.176 | 469.1592 | 372.7612 | 361.6892
1959.176 | 469.1954 | 372.8185 | 361.6027
1960.176 | 469.1721 | 373.0562 | 360.898
1961.176 | 469.2631 | 373.6943 | 361.2313
1962.176 | 469.3219 | 373.976 | 361.7611
1963.176 | 469.2941 | 373.9647 | 361.3531
1964.176 | 469.304 | 374.9297 | 361.1587
1965.176 | 469.255 | 375.7125 | 360.7484
1966.176 | 469.267 | 373.861 | 361.5629
1967.176 | 469.2926 | 372.8445 | 362.2015
1968.176 | 469.158 | 372.9443 | 362.5085
1969.176 | 469.1433 | 373.555 | 362.5014
1970.176 | 469.1656 | 374.8005 | 362.3218
1971.176 | 469.3624 | 374.3833 | 362.4623
1972.176 | 469.2421 | 373.6484 | 362.3131
1973.176 | 469.3054 | 374.4741 | 362.3709
1974.176 | 469.3321 | 373.6538 | 362.3729
1975.176 | 469.2425 | 373.5309 | 363.0247
1976.176 | 469.2638 | 374.5454 | 363.0503
1977.176 | 469.5097 | 374.3352 | 363.6067
1978.176 | 469.656 | 374.7641 | 362.7226
1979.176 | 469.5507 | 375.431 | 362.5567
1980.176 | 469.5607 | 375.7778 | 362.744
1981.176 | 469.5322 | 375.7608 | 362.7487
1982.176 | 469.6242 | 374.382 | 362.7593
1983.176 | 469.6524 | 373.8815 | 362.3137
1984.176 | 469.6068 | 373.921 | 362.6291
1985.176 | 469.6002 | 373.8765 | 362.4905
1986.176 | 469.6801 | 374.2895 | 361.9542
1987.176 | 469.5596 | 373.5097 | 361.6467
1988.176 | 469.5499 | 373.2097 | 362.4096
1989.176 | 469.5327 | 373.5583 | 363.0875
1990.176 | 469.3314 | 374.0939 | 363.4747
1991.176 | 469.2367 | 373.715 | 364.0734
1992.176 | 469.2757 | 374.9668 | 363.8041
1993.176 | 469.281 | 375.0085 | 364.2919
1994.176 | 469.3954 | 375.088 | 363.8926
1995.176 | 469.6173 | 373.8084 | 363.9938
1996.176 | 469.7093 | 374.1983 | 364.2701
1997.176 | 469.6126 | 374.325 | 364.0572
1998.176 | 469.7654 | 374.2628 | 363.5389
1999.176 | 469.8637 | 374.5628 | 363.0159
2000.176 | 469.7589 | 374.6352 | 362.5744
2001.176 | 469.7623 | 373.9589 | 362.3967
2002.176 | 469.7932 | 374.0632 | 363.1431
2003.176 | 469.7426 | 373.3517 | 362.9726
2004.176 | 469.7201 | 373.9876 | 362.3626
2005.176 | 469.5092 | 373.9753 | 361.9378
2006.176 | 469.4796 | 373.8551 | 362.154
2007.176 | 469.571 | 372.9769 | 362.2016
2008.176 | 469.7327 | 371.5286 | 362.5444
2009.176 | 469.7662 | 371.6725 | 362.5603
2010.176 | 469.6551 | 372.096 | 362.3503
2011.176 | 469.7898 | 372.1832 | 362.6519
2012.176 | 469.7513 | 371.9282 | 363.2387
2013.176 | 469.7333 | 372.4215 | 363.3111
2014.176 | 469.55 | 373.0848 | 363.2712
2015.176 | 469.4233 | 373.7696 | 363.0778
2016.176 | 469.3817 | 374.1155 | 362.8364
2017.176 | 469.5395 | 374.071 | 362.2772
2018.176 | 469.6565 | 373.4458 | 362.2602
2019.176 | 469.5874 | 372.9208 | 363.1233
2020.176 | 469.2956 | 373.5334 | 362.916
2021.176 | 469.2878 | 373.8968 | 362.4851
2022.176 | 469.2814 | 372.705 | 363.1704
2023.176 | 469.3323 | 372.2406 | 362.8551
2024.176 | 469.4684 | 372.795 | 363.7283
2025.176 | 469.5816 | 373.2193 | 363.8638
2026.176 | 469.5724 | 373.2311 | 363.3973
2027.176 | 469.5533 | 374.1144 | 362.6292
2028.176 | 469.5577 | 374.139 | 362.5028
2029.176 | 469.4185 | 373.4469 | 362.3722
2030.176 | 469.5035 | 373.7221 | 362.2347
2031.176 | 469.4638 | 373.216 | 362.1852
2032.176 | 469.3786 | 374.1459 | 362.479
2033.176 | 469.3781 | 374.0535 | 362.2648
2034.176 | 469.4207 | 373.9647 | 362.3811
2035.176 | 469.6018 | 372.8651 | 362.4715
2036.176 | 469.7696 | 372.4046 | 362.964
2037.176 | 469.7114 | 372.3386 | 363.7014
2038.176 | 469.8962 | 372.8948 | 363.4615
2039.176 | 469.8937 | 373.1428 | 363.0652
2040.176 | 469.963 | 372.3977 | 363.5993
2041.176 | 469.9178 | 372.8259 | 363.1233
2042.176 | 469.9714 | 371.3997 | 362.9577
2043.176 | 469.9334 | 371.3947 | 363.0144
2044.176 | 469.9163 | 370.6458 | 362.9391
2045.176 | 469.9745 | 370.4814 | 363.2931
2046.176 | 470.0227 | 371.6126 | 363.4858
2047.176 | 470.0238 | 371.9417 | 362.8912
2048.176 | 470.2003 | 372.4005 | 362.8232
2049.176 | 470.26 | 372.3432 | 363.1166
2050.176 | 470.2146 | 374.0752 | 361.8632
2051.176 | 470.2354 | 373.0586 | 361.6119
2052.176 | 470.347 | 373.3474 | 361.7134
2053.176 | 470.3892 | 372.2831 | 361.9347
2054.176 | 470.5271 | 371.8593 | 362.1668
2055.176 | 470.596 | 373.0922 | 362.4094
2056.176 | 470.4035 | 372.4742 | 362.1176
2057.176 | 470.4643 | 372.5264 | 361.8215
2058.176 | 470.4335 | 371.7352 | 361.6424
2059.176 | 470.5633 | 371.8798 | 361.5265
2060.176 | 470.5646 | 371.9381 | 361.781
2061.176 | 470.4902 | 372.5643 | 362.1456
2062.176 | 470.6283 | 372.7942 | 361.5408
2063.176 | 470.7451 | 373.0803 | 360.7553
2064.176 | 470.6855 | 373.9441 | 360.6932
2065.176 | 470.6221 | 374.1346 | 361.001
2066.176 | 470.6419 | 373.3235 | 361.7878
2067.176 | 470.6413 | 372.6306 | 361.3427
2068.176 | 470.6929 | 372.3725 | 361.6856
2069.176 | 470.7098 | 371.8235 | 361.5085
2070.176 | 470.6196 | 373.3565 | 361.0807
2071.176 | 470.3735 | 373.3005 | 360.7693
2072.176 | 470.3423 | 373.7571 | 360.8909
2073.176 | 470.4858 | 373.8339 | 361.5571
2074.176 | 470.5192 | 373.1749 | 362.1074
2075.176 | 470.5234 | 373.6684 | 361.5675
2076.176 | 470.6989 | 374.2873 | 361.4045
2077.176 | 470.776 | 374.3227 | 361.4608
2078.176 | 470.8402 | 374.7961 | 360.9807
2079.176 | 470.8219 | 375.2125 | 360.9874
2080.176 | 470.7259 | 373.4722 | 362.0021
2081.176 | 470.6718 | 373.2999 | 361.5856
2082.176 | 470.7014 | 372.4927 | 361.4361
2083.176 | 470.589 | 372.9881 | 361.7262
2084.176 | 470.611 | 372.2196 | 362.3177
2085.176 | 470.7149 | 372.7571 | 362.3008
2086.176 | 470.7179 | 374.0654 | 361.802
2087.176 | 470.7216 | 374.1415 | 361.7041
2088.176 | 470.7251 | 374.224 | 361.7281
2089.176 | 470.5098 | 373.4148 | 361.9009
2090.176 | 470.5703 | 372.8167 | 361.8545
2091.176 | 470.7385 | 372.3565 | 362.6141
2092.176 | 470.6871 | 373.0279 | 362.4182
2093.176 | 470.6741 | 373.1259 | 362.1495
2094.176 | 470.6958 | 373.5968 | 362.0673
2095.176 | 470.733 | 374.4228 | 361.6593
2096.176 | 470.8083 | 374.9971 | 361.7479
2097.176 | 470.7708 | 374.9398 | 361.4918
2098.176 | 470.5023 | 375.3608 | 360.7713
2099.176 | 470.5323 | 375.736 | 360.7324
2100.176 | 470.5735 | 375.8359 | 361.5354
2101.176 | 470.5991 | 376.1479 | 361.3661
2102.176 | 470.5515 | 375.7632 | 360.5512
2103.176 | 470.4368 | 375.7074 | 360.7124
2104.176 | 470.3603 | 375.8663 | 361.008
2105.176 | 470.2067 | 375.9714 | 361.1327
2106.176 | 470.2233 | 380.6102 | 360.3923
2107.176 | 470.2678 | 380.6407 | 360.0063
2108.176 | 470.2243 | 381.0333 | 359.967
2109.176 | 470.2681 | 381.6779 | 360.0366
2110.176 | 470.3848 | 383.301 | 359.644
2111.176 | 470.3959 | 384.8423 | 359.1198
2112.176 | 470.292 | 385.7563 | 359.1271
2113.176 | 470.414 | 386.8314 | 359.2688
2114.176 | 470.4412 | 387.4649 | 358.9975
2115.176 | 470.2525 | 387.5187 | 358.7352
2116.176 | 470.2162 | 389.7991 | 358.8463
2117.176 | 470.1557 | 391.2028 | 358.6759
2118.176 | 469.8935 | 392.3899 | 358.833
2119.176 | 469.764 | 393.4125 | 359.4747
2120.176 | 469.8665 | 394.0324 | 359.8957
2121.176 | 469.8036 | 395.1291 | 359.8352
2122.176 | 469.6472 | 395.8221 | 359.0573
2123.176 | 469.5173 | 396.014 | 359.1467
2124.176 | 469.2966 | 397.0985 | 359.3923
2125.176 | 469.3172 | 398.1018 | 358.3579
2126.176 | 469.3264 | 398.3335 | 357.715
2127.176 | 469.2657 | 398.3379 | 358.0976
2128.176 | 469.3108 | 398.633 | 358.0291
2129.176 | 469.4722 | 403.7366 | 360.4616
2130.176 | 469.4618 | 405.5708 | 359.5207
2131.176 | 469.4148 | 407.0804 | 359.1724
2132.176 | 469.4602 | 409.858 | 358.9453
2133.176 | 469.6319 | 431.0012 | 359.1136
2134.176 | 469.7784 | 462.766 | 359.3154
2135.176 | 469.8204 | 487.7057 | 359.8805
2136.176 | 469.9631 | 507.9809 | 359.5578
2137.176 | 469.9116 | 524.8299 | 359.4557
2138.176 | 469.9305 | 533.4704 | 359.2963
2139.176 | 470.0288 | 541.9513 | 359.385
2140.176 | 470.2468 | 556.3001 | 361.3999
2141.176 | 470.3773 | 576.473 | 361.7093
2142.176 | 470.4328 | 575.1505 | 362.6343
2143.176 | 470.5098 | 566.4476 | 362.1108
2144.176 | 470.5545 | 566.3899 | 362.0918
2145.176 | 470.5931 | 569.363 | 362.0525
2146.176 | 470.7087 | 568.8902 | 362.8587
2147.176 | 470.7664 | 588.6384 | 365.3292
2148.176 | 470.8473 | 598.0059 | 367.419
2149.176 | 470.6374 | 613.0667 | 366.6927
2150.176 | 470.5176 | 618.9814 | 367.7081
2151.176 | 470.729 | 611.9764 | 369.2013
2152.176 | 470.7789 | 604.2169 | 368.3592
2153.176 | 470.8552 | 598.4631 | 381.2641
2154.176 | 470.6657 | 593.7192 | 393.2299
2155.176 | 470.6581 | 586.6655 | 414.3116
2156.176 | 470.5957 | 580.2996 | 432.726
2157.176 | 470.3521 | 577.5881 | 447.6477
2158.176 | 470.4753 | 574.943 | 460.6715
2159.176 | 470.4059 | 578.9234 | 466.4582
2160.176 | 470.1469 | 589.6794 | 473.0398
2161.176 | 470.2844 | 592.1547 | 480.111
2162.176 | 470.367 | 594.3908 | 488.0093
2163.176 | 470.1665 | 593.477 | 495.5039
2164.176 | 470.0673 | 598.0796 | 501.8085
2165.176 | 470.1223 | 603.1064 | 508.9303
2166.176 | 470.0681 | 601.3905 | 517.5715
2167.176 | 470.1028 | 602.3407 | 526.2829
2168.176 | 470.1077 | 604.8926 | 530.7556
2169.176 | 470.0527 | 607.2756 | 527.0931
2170.176 | 470.0209 | 611.1374 | 529.6122
2171.176 | 470.2142 | 610.1105 | 538.7754
2172.176 | 470.1875 | 612.0351 | 543.742
2173.176 | 469.9642 | 616.0159 | 547.7517
2174.176 | 469.8406 | 617.3434 | 550.1789
2175.176 | 469.6255 | 619.5432 | 552.9736
2176.176 | 469.5643 | 619.7642 | 555.0854
2177.176 | 469.423 | 625.7731 | 554.0272
2178.176 | 469.3696 | 625.0036 | 553.7843
2179.176 | 469.4178 | 625.6313 | 556.5528
2180.176 | 469.3575 | 629.0877 | 557.1718
2181.176 | 469.3154 | 628.2984 | 556.2042
2182.176 | 469.2669 | 632.0236 | 554.001
2183.176 | 469.2979 | 631.8983 | 550.0627
2184.176 | 469.3551 | 633.6378 | 546.6246
2185.176 | 469.2891 | 632.4171 | 546.1808
2186.176 | 469.2808 | 631.9162 | 545.8433
2187.176 | 469.3659 | 637.3666 | 549.7694
2188.176 | 469.5244 | 639.745 | 548.0439
2189.176 | 469.6642 | 638.3201 | 547.9455
2190.176 | 469.6304 | 636.4859 | 546.2061
2191.176 | 469.5223 | 641.1827 | 544.7579
2192.176 | 469.3245 | 642.3918 | 540.5435
2193.176 | 469.3111 | 643.7003 | 539.8541
2194.176 | 469.2503 | 646.0926 | 541.2822
2195.176 | 469.224 | 651.5918 | 543.9544
2196.176 | 469.3338 | 654.4315 | 543.596
2197.176 | 469.3849 | 656.4312 | 543.8523
2198.176 | 469.4813 | 654.8735 | 540.6665
2199.176 | 469.4767 | 655.5501 | 542.794
2200.176 | 469.485 | 654.7736 | 539.2726
2201.176 | 469.3487 | 656.4499 | 541.9037
2202.176 | 469.1266 | 659.459 | 544.2154
2203.176 | 468.8822 | 661.1721 | 546.9278
2204.176 | 468.5627 | 664.339 | 548.1078
2205.176 | 468.4277 | 664.5769 | 546.0349
2206.176 | 468.2549 | 661.5676 | 545.2425
2207.176 | 468.0175 | 667.9059 | 549.6846
2208.176 | 467.8036 | 669.2194 | 550.3883
2209.176 | 467.7796 | 678.9594 | 551.4037
2210.176 | 467.7917 | 679.3582 | 550.8193
2211.176 | 467.7766 | 676.9233 | 552.5188
2212.176 | 467.62 | 671.7115 | 547.9405
2213.176 | 467.6157 | 672.5865 | 550.2761
2214.176 | 467.5429 | 670.7184 | 551.8538
2215.176 | 467.2886 | 673.4538 | 558.0662
2216.176 | 467.3183 | 677.887 | 559.3686
2217.176 | 467.23 | 672.6382 | 551.5185
2218.176 | 467.1523 | 668.6913 | 550.1343
2219.176 | 467.0631 | 665.4756 | 552.1512
2220.176 | 466.9765 | 667.128 | 550.3934
2221.176 | 467.0007 | 670.4593 | 552.8924
2222.176 | 467.0554 | 669.3348 | 551.7
2223.176 | 467.1006 | 668.6209 | 551.3872
2224.176 | 467.0194 | 671.2234 | 554.5741
2225.176 | 466.9771 | 672.658 | 556.3027
2226.176 | 467.1119 | 674.548 | 555.8115
2227.176 | 467.0987 | 669.9879 | 552.9997
2228.176 | 467.1101 | 679.989 | 558.1313
2229.176 | 467.1517 | 693.0414 | 556.9564
2230.176 | 467.3608 | 692.9953 | 557.1276
2231.176 | 467.3268 | 686.2611 | 555.6914
2232.176 | 467.1801 | 684.0387 | 557.5952
2233.176 | 466.9503 | 684.469 | 558.8617
2234.176 | 466.8272 | 684.4621 | 559.2666
2235.176 | 466.9096 | 681.4393 | 557.6941
2236.176 | 467.0654 | 680.6114 | 559.9024
2237.176 | 467.0566 | 679.0936 | 558.1619
2238.176 | 467.018 | 677.4481 | 562.1682
2239.176 | 466.8967 | 680.6934 | 566.2031
2240.176 | 466.6764 | 681.5533 | 568.8535
2241.176 | 466.4537 | 682.4249 | 571.911
2242.176 | 466.4805 | 681.3703 | 571.047
2243.176 | 466.4236 | 675.8334 | 570.1135
2244.176 | 466.4379 | 671.5481 | 570.2475
2245.176 | 466.4859 | 667.6736 | 571.4408
2246.176 | 466.5383 | 665.3755 | 573.383
2247.176 | 466.6577 | 660.6618 | 573.1644
2248.176 | 466.6396 | 654.9673 | 573.423
2249.176 | 466.4931 | 650.946 | 576.8342
2250.176 | 466.3532 | 645.9647 | 578.3482
2251.176 | 466.4009 | 644.6237 | 579.3778
2252.176 | 466.4613 | 640.8479 | 579.3034
2253.176 | 466.6231 | 637.8449 | 579.3642
2254.176 | 466.5601 | 635.3104 | 583.4556
2255.176 | 466.5467 | 630.7422 | 583.0582
2256.176 | 466.5561 | 627.5527 | 584.8888
2257.176 | 466.4582 | 622.1011 | 577.6482
2258.176 | 466.295 | 618.8582 | 574.3987
2259.176 | 466.2691 | 616.1968 | 572.5652
2260.176 | 466.1048 | 613.2514 | 571.7134
2261.176 | 466.0189 | 612.4522 | 571.9192
2262.176 | 465.9461 | 609.3512 | 572.4706
2263.176 | 465.9944 | 607.044 | 572.8898
2264.176 | 465.8698 | 606.6279 | 573.8131
2265.176 | 465.9531 | 606.1743 | 575.7638
2266.176 | 465.9926 | 605.5448 | 577.5629
2267.176 | 466.0204 | 603.7084 | 580.2841
2268.176 | 466.0625 | 602.9767 | 582.6218
2269.176 | 466.0223 | 601.8513 | 584.5355
2270.176 | 466.0968 | 600.6631 | 586.2111
2271.176 | 466.084 | 599.2459 | 587.8402
2272.176 | 465.9288 | 598.6258 | 589.1378
2273.176 | 465.8888 | 598.0175 | 590.5134
2274.176 | 465.7954 | 597.7423 | 590.9907
2275.176 | 465.5655 | 597.5439 | 591.3234
2276.176 | 465.4886 | 597.079 | 591.8029
2277.176 | 465.4485 | 596.9884 | 592.0987
2278.176 | 465.5169 | 596.4713 | 592.1119
2279.176 | 465.3475 | 595.6872 | 591.6286
2280.176 | 465.1832 | 594.7304 | 591.1967
2281.176 | 465.4111 | 595.5878 | 591.0572
2282.176 | 465.682 | 594.5441 | 590.6305
2283.176 | 465.368 | 594.8824 | 590.1057
2284.176 | 465.5269 | 594.5009 | 589.8328
2285.176 | 465.4018 | 593.5944 | 590.3002
2286.176 | 465.4379 | 592.0888 | 591.3915
2287.176 | 465.3744 | 594.3744 | 591.0344
2288.176 | 465.6224 | 595.1166 | 590.4588
2289.176 | 465.6804 | 595.034 | 590.2182
2290.176 | 465.6328 | 594.1899 | 591.6386
2291.176 | 465.6401 | 593.9025 | 592.3854
2292.176 | 465.6551 | 593.7742 | 592.6621
2293.176 | 465.7215 | 593.3321 | 592.4242
2294.176 | 465.7944 | 592.4625 | 592.7278
2295.176 | 465.8051 | 591.9911 | 592.4291
2296.176 | 465.8112 | 591.7708 | 592.9689
2297.176 | 465.7383 | 591.2017 | 593.3001
2298.176 | 465.6711 | 591.6853 | 593.5668
2299.176 | 465.4863 | 590.0277 | 594.4607
2300.176 | 465.2877 | 590.3457 | 594.79
2301.176 | 465.2895 | 590.1193 | 594.8406
2302.176 | 465.2585 | 590.0264 | 595.9409
2303.176 | 465.1849 | 589.5979 | 595.8724
2304.176 | 465.3177 | 589.3546 | 596.3337
2305.176 | 465.2916 | 589.6081 | 597.0732
2306.176 | 465.2492 | 589.1614 | 598.3372
2307.176 | 465.3579 | 589.0986 | 598.2661
2308.176 | 465.3906 | 588.9782 | 598.4891
2309.176 | 465.3966 | 588.0414 | 598.59
2310.176 | 465.3655 | 587.0247 | 598.7975
2311.176 | 465.272 | 586.8132 | 598.1125
2312.176 | 465.3052 | 586.5457 | 598.7134
2313.176 | 465.4305 | 586.8369 | 598.8279
2314.176 | 465.3788 | 586.9451 | 599.498
2315.176 | 465.3144 | 585.424 | 599.7012
2316.176 | 465.3286 | 585.3096 | 599.5788
2317.176 | 465.3607 | 586.2841 | 599.6692
2318.176 | 465.3439 | 586.0642 | 599.4366
2319.176 | 465.2989 | 585.4491 | 600.1669
2320.176 | 465.3385 | 584.358 | 600.3165
2321.176 | 465.3371 | 584.5209 | 600.5871
2322.176 | 465.4414 | 583.9917 | 600.2146
2323.176 | 465.3752 | 584.4323 | 600.9439
2324.176 | 465.4666 | 584.5228 | 600.7592
2325.176 | 465.5104 | 584.8475 | 600.7394
2326.176 | 465.5609 | 584.1141 | 599.8697
2327.176 | 465.601 | 584.4274 | 599.6066
2328.176 | 465.6591 | 583.5151 | 600.5125
2329.176 | 465.6728 | 583.4639 | 600.7459
2330.176 | 465.7438 | 583.9878 | 598.4028
2331.176 | 465.9679 | 582.899 | 596.5934
2332.176 | 466.1602 | 583.1185 | 593.7969
2333.176 | 466.161 | 582.1594 | 591.3928
2334.176 | 466.1736 | 581.3987 | 589.6509
2335.176 | 466.1596 | 580.7912 | 588.0192
2336.176 | 466.4037 | 578.9906 | 587.5072
2337.176 | 466.5962 | 579.1622 | 586.2181
2338.176 | 466.7181 | 579.9195 | 584.8741
2339.176 | 466.7195 | 579.9209 | 583.6784
2340.176 | 466.6006 | 580.0797 | 582.6368
2341.176 | 466.7204 | 580.1118 | 582.6689
2342.176 | 466.9 | 580.2937 | 581.8355
2343.176 | 466.8995 | 580.5736 | 581.2711
2344.176 | 466.9 | 579.248 | 581.3055
2345.176 | 466.7795 | 578.7967 | 580.5434
2346.176 | 466.8114 | 578.588 | 579.8879
2347.176 | 467.0963 | 579.0159 | 579.7521
2348.176 | 467.2772 | 578.1426 | 580.3467
2349.176 | 467.2675 | 576.3717 | 580.7029
2350.176 | 467.2084 | 574.7352 | 580.1942
2351.176 | 467.1132 | 573.9612 | 579.7104
2352.176 | 466.8707 | 573.9073 | 579.6224
2353.176 | 466.7318 | 573.7447 | 579.2038
2354.176 | 466.7289 | 573.1569 | 579.3882
2355.176 | 466.61 | 572.2976 | 579.6945
2356.176 | 466.4914 | 572.803 | 580.1648
2357.176 | 466.5252 | 571.8784 | 580.6753
2358.176 | 466.4943 | 571.6519 | 580.9248
2359.176 | 466.5519 | 572.1482 | 580.7782
2360.176 | 466.6394 | 571.9604 | 580.8953
2361.176 | 466.696 | 571.4337 | 581.8829
2362.176 | 466.6706 | 570.7518 | 582.6447
2363.176 | 466.6883 | 570.952 | 583.2964
2364.176 | 466.6905 | 570.9237 | 583.7089
2365.176 | 466.6523 | 570.6392 | 583.428
2366.176 | 466.5995 | 570.9048 | 583.257
2367.176 | 466.7277 | 571.0749 | 583.1266
2368.176 | 466.6652 | 570.9315 | 583.6065
2369.176 | 466.5153 | 570.5932 | 582.9591
2370.176 | 466.4392 | 570.6255 | 583.2062
2371.176 | 466.3881 | 570.5164 | 583.457
2372.176 | 466.3185 | 570.9928 | 583.6504
2373.176 | 466.3403 | 571.1925 | 583.8204
2374.176 | 466.5286 | 571.9747 | 583.9635
2375.176 | 466.5948 | 572.2425 | 583.9313
2376.176 | 466.4738 | 571.9421 | 584.2274
2377.176 | 466.5941 | 572.4523 | 584.0351
2378.176 | 466.5593 | 572.2627 | 584.27
2379.176 | 466.4649 | 573.0827 | 584.3062
2380.176 | 466.4657 | 573.8989 | 584.2224
2381.176 | 466.377 | 574.1243 | 584.2559
2382.176 | 466.166 | 574.92 | 584.8437
2383.176 | 466.0315 | 575.4071 | 584.9775
2384.176 | 466.0528 | 576.0888 | 584.9616
2385.176 | 466.22 | 577.0017 | 585.0419
2386.176 | 466.3048 | 575.9452 | 585.4662
2387.176 | 466.2387 | 576.9908 | 585.421
2388.176 | 466.4265 | 578.7918 | 586.2297
2389.176 | 466.5519 | 578.6959 | 585.7989
2390.176 | 466.5499 | 578.4309 | 585.544
2391.176 | 466.6584 | 580.006 | 586.282
2392.176 | 466.5397 | 580.2504 | 586.039
2393.176 | 466.5722 | 580.8818 | 586.0698
2394.176 | 466.6916 | 581.5121 | 586.4342
2395.176 | 466.7714 | 582.4887 | 586.2493
2396.176 | 466.9532 | 582.743 | 586.0566
2397.176 | 467.0695 | 582.9306 | 585.9805
2398.176 | 467.0862 | 582.8711 | 586.6197
2399.176 | 467.1417 | 583.7195 | 586.4736
2400.176 | 467.104 | 584.0983 | 587.1201
2401.176 | 467.1481 | 584.1256 | 587.3673
2402.176 | 467.0211 | 584.1097 | 587.6868
2403.176 | 466.9763 | 584.9048 | 587.8145
2404.176 | 466.845 | 585.1572 | 588.2837
2405.176 | 467.0518 | 586.1767 | 587.3511
2406.176 | 467.134 | 586.5472 | 587.6009
2407.176 | 467.1059 | 586.6917 | 588.1189
2408.176 | 467.0505 | 586.4831 | 589.3019
2409.176 | 467.3379 | 586.9069 | 588.9473
2410.176 | 467.6859 | 586.8745 | 588.9037
2411.176 | 467.6919 | 587.0346 | 588.3627
2412.176 | 467.7934 | 587.3582 | 588.9012
2413.176 | 467.8666 | 588.1987 | 589.1577
2414.176 | 467.9617 | 587.5445 | 589.3208
2415.176 | 467.9648 | 587.5511 | 589.1764
2416.176 | 467.995 | 587.1893 | 588.7964
2417.176 | 467.81 | 587.4635 | 588.3843
2418.176 | 467.6524 | 587.2171 | 589.0466
2419.176 | 467.6977 | 587.9149 | 589.385
2420.176 | 467.8342 | 588.1282 | 588.8779
2421.176 | 467.977 | 588.0674 | 588.7765
2422.176 | 468.1136 | 587.3627 | 589.0035
2423.176 | 468.09 | 586.903 | 589.2053
2424.176 | 468.0503 | 587.8708 | 587.5855
2425.176 | 468.1912 | 587.49 | 588.5943
2426.176 | 468.3307 | 587.5747 | 589.1161
2427.176 | 468.2898 | 587.3935 | 589.5462
2428.176 | 468.2295 | 587.2001 | 589.4608
2429.176 | 468.0825 | 586.8888 | 588.829
2430.176 | 468.1119 | 586.6444 | 588.8627
2431.176 | 468.002 | 586.9724 | 587.8785
2432.176 | 467.9135 | 587.4467 | 587.4867
2433.176 | 467.8783 | 587.6105 | 587.3455
2434.176 | 467.9251 | 587.3117 | 587.5378
2435.176 | 467.999 | 587.4705 | 587.4616
2436.176 | 468.0121 | 587.8061 | 587.1661
2437.176 | 468.0596 | 588.0198 | 586.699
2438.176 | 468.0067 | 588.6498 | 586.2942
2439.176 | 467.9738 | 588.3702 | 586.954
2440.176 | 467.955 | 588.7962 | 586.5282
2441.176 | 467.8845 | 588.778 | 586.7418
2442.176 | 468.0001 | 588.6169 | 586.4591
2443.176 | 468.1701 | 588.726 | 585.9139
2444.176 | 468.1105 | 588.6008 | 585.8354
2445.176 | 468.0964 | 588.5042 | 585.8067
2446.176 | 468.2592 | 588.1325 | 586.3854
2447.176 | 468.3413 | 588.1315 | 585.5714
2448.176 | 468.329 | 588.468 | 585.2704
2449.176 | 468.3492 | 589.1048 | 584.5081
2450.176 | 468.3449 | 588.8007 | 584.9733
2451.176 | 468.4436 | 589.4298 | 585.6308
2452.176 | 468.3799 | 589.2105 | 586.0537
2453.176 | 468.4082 | 588.8765 | 586.5364
2454.176 | 468.3501 | 588.6872 | 585.5257
2455.176 | 468.2782 | 587.8175 | 585.1053
2456.176 | 468.1997 | 587.187 | 585.5925
2457.176 | 468.2536 | 587.6596 | 585.7907
2458.176 | 468.2894 | 587.4316 | 585.4222
2459.176 | 468.3866 | 587.3339 | 585.3823
2460.176 | 468.4477 | 586.7125 | 585.3044
2461.176 | 468.4601 | 587.434 | 584.6889
2462.176 | 468.5923 | 587.9201 | 584.2762
2463.176 | 468.6209 | 587.5847 | 584.0835
2464.176 | 468.6328 | 587.0212 | 585.6241
2465.176 | 468.7526 | 585.9961 | 585.8564
2466.176 | 468.9626 | 585.2558 | 586.2009
2467.176 | 469.0615 | 586.4358 | 585.0942
2468.176 | 469.3058 | 587.0806 | 584.543
2469.176 | 470.1069 | 586.7913 | 584.8352
2470.176 | 471.7499 | 587.4125 | 584.8771
2471.176 | 473.9719 | 587.4759 | 584.0842
2472.176 | 476.4705 | 588.3151 | 583.2898
2473.176 | 479.3895 | 588.973 | 582.8363
2474.176 | 482.4967 | 589.7286 | 584.2951
2475.176 | 485.9034 | 590.134 | 584.6952
2476.176 | 489.0474 | 590.9216 | 584.7955
2477.176 | 491.2749 | 590.4564 | 585.4223
2478.176 | 492.9609 | 590.6526 | 586.2883
2479.176 | 493.9725 | 591.3174 | 586.0945
2480.176 | 494.5875 | 591.3484 | 586.9819
2481.176 | 494.7735 | 591.5812 | 587.7476
2482.176 | 494.6071 | 591.1378 | 588.1687
2483.176 | 494.2405 | 590.438 | 587.1104
2484.176 | 493.7776 | 590.5401 | 585.8496
2485.176 | 493.1591 | 590.4 | 585.7052
2486.176 | 492.6253 | 590.4041 | 584.9139
2487.176 | 491.8354 | 590.0887 | 584.6302
2488.176 | 491.2818 | 589.3251 | 584.4176
2489.176 | 490.4958 | 588.6684 | 584.503
2490.176 | 489.6931 | 587.0574 | 585.2191
2491.176 | 488.8586 | 587.5816 | 585.1949
2492.176 | 488.0398 | 587.9667 | 584.5588
2493.176 | 487.1029 | 588.0771 | 583.2719
2494.176 | 486.1103 | 587.7632 | 582.7141
2495.176 | 485.1024 | 587.3336 | 583.3053
2496.176 | 484.2862 | 587.1888 | 583.1514
2497.176 | 483.2968 | 586.8445 | 582.4794
2498.176 | 482.275 | 586.7438 | 582.1738
2499.176 | 481.1985 | 586.3871 | 581.2972
2500.176 | 480.086 | 586.6073 | 581.6162
2501.176 | 479.1238 | 586.8388 | 582.4023
2502.176 | 478.2075 | 586.5492 | 582.311
2503.176 | 477.0526 | 586.7096 | 581.2646
2504.176 | 476.0319 | 586.4675 | 580.9056