## Test Conditions
DESIREE-FIRE Test Number 23 - Circuit Simulator Data Only
Test Date: | 2009-07-16
DCSim DAQ Start Time | 15:39
DCSim Time for Synchronization | 15:38
Heat Source Synchronization | 0:02 | hour:minutes:seconds
Heat Source DAQ Start Time | 15:36
Fire Time | 15:42
Offset | 0:03 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 180 | seconds
Heat Source Offset | 0:06 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 358 | seconds
Heat Source Stop Time | 15:52
Test Duration | 0:10 | hour:minutes:seconds
| 600 | seconds
CT500 turns | 1 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 1 | 1 or 5
Pre-Test Baseline: |  | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SOV 1 | EPR, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
SOV 2 | EPR, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SOV-1_CT500 | SOV-1_CT35_1_P | SOV-1_CT35_2_S1 | SOV-1_CT35_3_G | SOV-1_CT35_4_S2 | SOV-1_CT35_5_N | SOV-2_CT500 | SOV-2_CT35_1_P | SOV-2_CT35_2_S1 | SOV-2_CT35_3_G | SOV-2_CT35_4_S2 | SOV-2_CT35_5_N | SOV-1_VT7_1_R | SOV-1_VT7_2_SP | SOV-1_VT7_3_S | SOV-1_VTU_1_P | SOV-1_VTU_2_S1 | SOV-1_VTU_3_G | SOV-1_VTU_4_N | SOV-2_VT7_1_R | SOV-2_VT7_2_SP | SOV-2_VT7_3_S | SOV-2_VTU_1_P | SOV-2_VTU_2_S1 | SOV-2_VTU_3_G | SOV-2_VTU_4_N | {SOV1} V(N) - V(Batt -) | {SOV1} V(P) - V(Batt +) | {SOV1} V(R) - V(Batt -) | {SOV1} V(S) - V(Batt -) | {SOV1} V(S) - V(N) | {SOV1} V(S1) - V(Batt +) | {SOV1} V(G) - V(Batt +) | {SOV2} V(N) - V(Batt -) | {SOV2} V(P) - V(Batt +) | {SOV2} V(R) - V(Batt -) | {SOV2} V(S) - V(Batt -) | {SOV2} V(S) - V(N) | {SOV2} V(S1) - V(Batt +) | {SOV2} V(G) - V(Batt +) | {SOV1} V(P) - V(Batt -) | {SOV1} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV1} V(SP) - V(Batt -) | {SOV1} V(N) - V(Batt +) | {SOV2} V(P) - V(Batt -) | {SOV2} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV2} V(SP) - V(Batt -) | {SOV2} V(N) - V(Batt +)
-0.0625 | 123.3307 | -66.7465 | 56.2775 | 0.033173 | 0.0033103 | -0.0014454 | 0.056476 | 0.0030161 | 0.057481 | 0.041238 | 0.0018748 | 0.0014765 | 0.067555 | -0.0070592 | 0.066549 | -64.5496 | 0.0243 | -66.6911 | 56.2518 | 56.0143 | 56.152 | -66.865 | -66.7291 | 0.023253 | -66.846 | 55.9834 | 56.2847 | 56.0682 | -66.9599 | -0.11847 | -0.025627 | 2.1969 | 0.055456 | 0.17392 | -0.26312 | -0.12545 | -0.21341 | -0.29411 | 0.017451 | -0.099471 | 0.11394 | 0.007265 | -0.20931 | 122.9984 | 122.7609 | 122.8985 | 66.7708 | -123.1425 | 122.7299 | 123.0313 | 122.8147 | 66.7698 | -123.2374
0.9375 | 123.3124 | -66.7511 | 56.2683 | 0.048435 | 0.0065153 | -0.00037739 | 0.058613 | 0.0019481 | 0.059618 | 0.056499 | 0.00080679 | -0.00065947 | 0.065418 | -0.0059912 | 0.066549 | -64.5496 | 0.015142 | -66.7002 | 56.2518 | 56.0098 | 56.1474 | -66.8604 | -66.7382 | 0.014095 | -66.8414 | 55.9788 | 56.2893 | 56.0361 | -66.9599 | -0.10931 | -0.016472 | 2.2015 | 0.050877 | 0.16019 | -0.25855 | -0.12088 | -0.20884 | -0.28953 | 0.012872 | -0.090314 | 0.11852 | 0.020999 | -0.2322 | 123.0029 | 122.7609 | 122.8985 | 66.7662 | -123.1287 | 122.7299 | 123.0404 | 122.7872 | 66.7652 | -123.2282
1.9375 | 123.2071 | -66.7603 | 56.3004 | 0.048435 | 0.0022413 | 0.0017596 | 0.057544 | 0.00088012 | 0.056413 | 0.041238 | -0.00026221 | -0.00065947 | 0.065418 | -0.0049232 | 0.066549 | -64.5084 | 0.019721 | -66.6956 | 56.2518 | 56.0052 | 56.1566 | -66.865 | -66.7245 | 0.014095 | -66.8414 | 55.9834 | 56.2847 | 56.0178 | -66.9554 | -0.10473 | -0.048515 | 2.2518 | 0.06461 | 0.16934 | -0.29517 | -0.14377 | -0.1951 | -0.317 | 0.035763 | -0.081159 | 0.11394 | -0.015623 | -0.28256 | 123.0121 | 122.7654 | 122.9168 | 66.78 | -123.1653 | 122.7436 | 123.045 | 122.778 | 66.7743 | -123.2557
2.9375 | 123.2483 | -66.774 | 56.3004 | 0.078959 | 0.0033103 | -0.00037739 | 0.057544 | 0.00088012 | 0.057481 | 0.07176 | 0.0018748 | 0.00040853 | 0.066487 | -0.0049232 | 0.065481 | -64.513 | 0.019721 | -66.6956 | 56.2564 | 56.0143 | 56.1612 | -66.8055 | -66.7382 | 0.023253 | -66.8414 | 55.9879 | 56.2802 | 56.0636 | -66.9599 | -0.031474 | -0.043937 | 2.261 | 0.078343 | 0.10982 | -0.28601 | -0.13919 | -0.18595 | -0.31242 | 0.03576 | -0.067426 | 0.11852 | -0.020201 | -0.23677 | 123.0304 | 122.7883 | 122.9352 | 66.7937 | -123.1058 | 122.7619 | 123.0541 | 122.8376 | 66.7972 | -123.2603
3.9375 | 123.3398 | -66.7328 | 56.2866 | 0.063697 | 0.0033103 | -0.00037739 | 0.058613 | 0.00088012 | 0.057481 | 0.041238 | 0.00080679 | 0.00040853 | 0.067555 | -0.0059912 | 0.067618 | -64.5542 | 0.015142 | -66.7002 | 56.2518 | 56.0098 | 56.152 | -66.8604 | -66.7245 | 0.027831 | -66.8414 | 55.9834 | 56.2802 | 56.059 | -66.9599 | -0.12762 | -0.034782 | 2.1786 | 0.032566 | 0.16019 | -0.27686 | -0.13461 | -0.22715 | -0.30326 | 0.008297 | -0.10863 | 0.11852 | -0.006468 | -0.22762 | 122.9846 | 122.7426 | 122.8848 | 66.7479 | -123.147 | 122.7161 | 123.0129 | 122.7918 | 66.7606 | -123.2466
4.9375 | 123.3307 | -66.7511 | 56.2363 | 0.063697 | 0.0054463 | -0.0014454 | 0.058613 | 0.0019481 | 0.057481 | 0.056499 | 0.0018748 | 0.00040853 | 0.065418 | -0.0049232 | 0.065481 | -64.5313 | 0.0243 | -66.6911 | 56.2564 | 56.0006 | 56.1566 | -66.8558 | -66.7291 | 0.018674 | -66.8414 | 55.9834 | 56.2939 | 56.0819 | -66.9645 | -0.10473 | 0.02015 | 2.2198 | 0.060034 | 0.16477 | -0.23566 | -0.079678 | -0.21341 | -0.25291 | 0.022029 | -0.090314 | 0.1231 | 0.057622 | -0.15437 | 123.0075 | 122.7517 | 122.9077 | 66.7754 | -123.0921 | 122.7345 | 123.045 | 122.833 | 66.7698 | -123.2008
5.9375 | 123.2941 | -66.7786 | 56.3004 | 0.048435 | 0.0043783 | 0.00069161 | 0.060749 | 0.00088012 | 0.057481 | 0.056499 | 0.0029428 | 0.0014765 | 0.066487 | -0.0049232 | 0.066549 | -64.5313 | 0.0243 | -66.6956 | 56.2518 | 56.0143 | 56.152 | -66.8192 | -66.7245 | 0.014095 | -66.8414 | 55.9879 | 56.2847 | 56.027 | -66.9691 | -0.040634 | -0.048515 | 2.2472 | 0.08292 | 0.12355 | -0.28601 | -0.14834 | -0.19053 | -0.31242 | 0.054073 | -0.062849 | 0.12768 | -0.015623 | -0.2734 | 123.0304 | 122.7929 | 122.9306 | 66.8029 | -123.1196 | 122.7665 | 123.0633 | 122.8055 | 66.7927 | -123.2694
6.9375 | 123.2895 | -66.7648 | 56.2592 | 0.048435 | 0.0043783 | 0.00069161 | 0.057544 | 0.00088012 | 0.057481 | 0.056499 | 0.0029428 | 0.00040853 | 0.065418 | -0.0059912 | 0.066549 | -64.5313 | 0.028878 | -66.6819 | 56.2564 | 56.0143 | 56.1612 | -66.8604 | -66.7336 | 0.014095 | -66.8368 | 55.9788 | 56.2847 | 56.1231 | -66.9599 | -0.095576 | -0.002738 | 2.2335 | 0.082923 | 0.1785 | -0.24481 | -0.097987 | -0.1951 | -0.28038 | 0.031183 | -0.072002 | 0.1231 | 0.025576 | -0.13605 | 123.0212 | 122.7792 | 122.926 | 66.7937 | -123.1196 | 122.7436 | 123.0496 | 122.8879 | 66.7789 | -123.2191
7.9375 | 123.3215 | -66.7145 | 56.2729 | 0.048435 | 0.0022413 | 0.00069161 | 0.057544 | 0.0030161 | 0.059618 | 0.056499 | 0.0029428 | 0.00040853 | 0.066487 | -0.0070592 | 0.065481 | -64.5405 | 0.019721 | -66.6911 | 56.2473 | 56.0189 | 56.1612 | -66.865 | -66.7336 | 0.023253 | -66.8368 | 55.9742 | 56.2847 | 56.0498 | -66.9737 | -0.15051 | -0.025628 | 2.174 | 0.023413 | 0.17392 | -0.25397 | -0.11172 | -0.25919 | -0.29869 | -0.019171 | -0.12236 | 0.13684 | 0.011843 | -0.22304 | 122.9617 | 122.7334 | 122.8756 | 66.7342 | -123.1379 | 122.6887 | 122.9992 | 122.7643 | 66.7377 | -123.2466
8.9531 | 123.3353 | -66.7328 | 56.2912 | 0.094221 | 0.0033103 | 0.00069161 | 0.057544 | 0.0019481 | 0.057481 | 0.07176 | 0.0018748 | 0.0025445 | 0.066487 | -0.0059912 | 0.064413 | -64.5908 | 0.0243 | -66.7002 | 56.2564 | 56.0098 | 56.1612 | -66.8604 | -66.7336 | 0.018674 | -66.8414 | 55.9834 | 56.2893 | 56.0911 | -66.9645 | -0.12762 | -0.034782 | 2.1419 | 0.032566 | 0.16019 | -0.28144 | -0.13003 | -0.23172 | -0.30784 | -0.000861 | -0.10863 | 0.1231 | -0.001889 | -0.20015 | 122.9892 | 122.7426 | 122.894 | 66.7571 | -123.1516 | 122.7161 | 123.0221 | 122.8238 | 66.7515 | -123.2557
9.9375 | 123.2254 | -66.7831 | 56.3141 | 0.048435 | 0.0054463 | 0.00069161 | 0.058613 | 0.0019481 | 0.057481 | 0.041238 | 0.0018748 | 0.0014765 | 0.065418 | -0.0049232 | 0.065481 | -64.513 | 0.019721 | -66.7002 | 56.2473 | 56.0098 | 56.1566 | -66.8696 | -66.7336 | 0.014095 | -66.8414 | 55.9788 | 56.2893 | 56.0956 | -66.9599 | -0.086424 | -0.066827 | 2.2701 | 0.08292 | 0.16934 | -0.30432 | -0.1575 | -0.17679 | -0.33531 | 0.049493 | -0.058271 | 0.11852 | -0.024777 | -0.21845 | 123.0304 | 122.7929 | 122.9397 | 66.8029 | -123.1837 | 122.7619 | 123.0725 | 122.8788 | 66.7972 | -123.274
10.9375 | 123.2483 | -66.7694 | 56.2912 | 0.048435 | 0.0033103 | 0.00069161 | 0.060749 | 0.00088012 | 0.056413 | 0.041238 | 0.00080679 | 0.0025445 | 0.066487 | -0.0049232 | 0.066549 | -64.5268 | 0.0243 | -66.6911 | 56.2518 | 56.0098 | 56.1612 | -66.8375 | -66.7291 | 0.023253 | -66.8323 | 55.9879 | 56.2847 | 56.0224 | -66.9645 | -0.068105 | -0.03936 | 2.2427 | 0.078344 | 0.14645 | -0.28144 | -0.13003 | -0.1951 | -0.30326 | 0.040339 | -0.062847 | 0.13226 | -0.006468 | -0.26882 | 123.0212 | 122.7792 | 122.9306 | 66.7937 | -123.1287 | 122.7573 | 123.0541 | 122.7918 | 66.7927 | -123.2557
11.9375 | 123.3078 | -66.7282 | 56.3095 | 0.048435 | 0.0043783 | 0.00069161 | 0.058613 | 0.00088012 | 0.057481 | 0.056499 | 0.00080679 | 0.00040853 | 0.066487 | -0.0049232 | 0.066549 | -64.5954 | 0.019721 | -66.6819 | 56.2564 | 56.0235 | 56.1657 | -66.8604 | -66.7336 | 0.018674 | -66.8368 | 55.9788 | 56.2893 | 56.0865 | -66.9645 | -0.1322 | -0.053092 | 2.1328 | 0.046301 | 0.1785 | -0.28601 | -0.14376 | -0.2363 | -0.33073 | -0.005439 | -0.10862 | 0.12768 | -0.020199 | -0.22303 | 122.9846 | 122.7517 | 122.894 | 66.7479 | -123.1699 | 122.707 | 123.0175 | 122.8147 | 66.7469 | -123.274
12.9375 | 123.2483 | -66.7923 | 56.3095 | 0.063697 | 0.0043783 | -0.00037739 | 0.058613 | 0.00088012 | 0.057481 | 0.056499 | 0.0018748 | 0.0014765 | 0.067555 | -0.0059912 | 0.066549 | -64.5176 | 0.0243 | -66.6865 | 56.2518 | 56.0189 | 56.1612 | -66.865 | -66.7199 | 0.018674 | -66.846 | 55.9971 | 56.2893 | 56.0865 | -66.9645 | -0.07269 | -0.05767 | 2.2747 | 0.10581 | 0.1785 | -0.29059 | -0.14834 | -0.17222 | -0.31242 | 0.072385 | -0.053695 | 0.11852 | -0.020199 | -0.22303 | 123.0441 | 122.8112 | 122.9535 | 66.8166 | -123.1745 | 122.7894 | 123.0816 | 122.8788 | 66.811 | -123.274
13.9531 | 123.2574 | -66.7465 | 56.2958 | 0.048435 | 0.0043783 | 0.00069161 | 0.058613 | -0.00018888 | 0.055345 | 0.07176 | 0.00080679 | 0.0014765 | 0.067555 | -0.0070592 | 0.066549 | -64.5954 | 0.019721 | -66.6911 | 56.2564 | 56.0098 | 56.1612 | -66.8513 | -66.7336 | 0.018674 | -66.8414 | 55.9788 | 56.2893 | 56.1139 | -66.9691 | -0.10473 | -0.039359 | 2.1511 | 0.055456 | 0.16019 | -0.28601 | -0.13461 | -0.22257 | -0.317 | 0.012872 | -0.094892 | 0.12768 | -0.006466 | -0.18183 | 123.0029 | 122.7563 | 122.9077 | 66.7662 | -123.147 | 122.7253 | 123.0358 | 122.8605 | 66.7652 | -123.2649
14.9375 | 123.2391 | -66.7786 | 56.3049 | 0.048435 | 0.0011733 | 0.00069161 | 0.057544 | 0.0019481 | 0.057481 | 0.041238 | 0.0018748 | 0.0014765 | 0.067555 | -0.0049232 | 0.065481 | -64.5634 | 0.019721 | -66.6911 | 56.2564 | 56.0143 | 56.152 | -66.865 | -66.7382 | 0.018674 | -66.8414 | 55.9879 | 56.2847 | 56.0453 | -66.9691 | -0.086423 | -0.048515 | 2.2152 | 0.087499 | 0.17392 | -0.29059 | -0.15292 | -0.19053 | -0.317 | 0.040337 | -0.062849 | 0.12768 | -0.020201 | -0.25966 | 123.035 | 122.7929 | 122.9306 | 66.7983 | -123.1699 | 122.7665 | 123.0633 | 122.8238 | 66.7972 | -123.274
15.9688 | 123.1934 | -66.7786 | 56.3461 | 0.078959 | 0.0033103 | -0.0014454 | 0.057544 | 0.0019481 | 0.05855 | 0.07176 | 0.00080679 | 0.0014765 | 0.065418 | -0.0059912 | 0.066549 | -64.5405 | 0.0243 | -66.6911 | 56.2518 | 56.0143 | 56.1612 | -66.8696 | -66.7245 | 0.023253 | -66.8414 | 55.9925 | 56.2893 | 56.1277 | -66.9645 | -0.091002 | -0.094291 | 2.2381 | 0.087499 | 0.1785 | -0.33179 | -0.18496 | -0.18595 | -0.35362 | 0.054073 | -0.062849 | 0.1231 | -0.05682 | -0.21845 | 123.0304 | 122.7929 | 122.9397 | 66.8029 | -123.2157 | 122.7711 | 123.0679 | 122.9062 | 66.8018 | -123.3106
16.9375 | 123.262 | -66.7328 | 56.282 | 0.048435 | 0.0033103 | -0.0014454 | 0.056476 | 0.00088012 | 0.056413 | 0.041238 | 0.00080679 | 0.00040853 | 0.066487 | -0.0049232 | 0.065481 | -64.6229 | 0.0243 | -66.6956 | 56.2518 | 56.0235 | 56.1657 | -66.8513 | -66.7291 | 0.018674 | -66.846 | 55.9788 | 56.2893 | 56.1231 | -66.9645 | -0.11846 | -0.030204 | 2.1099 | 0.037144 | 0.15561 | -0.25854 | -0.1163 | -0.23172 | -0.30327 | 0.003718 | -0.1132 | 0.11852 | 0.007267 | -0.15894 | 122.9846 | 122.7563 | 122.8985 | 66.7571 | -123.1333 | 122.7116 | 123.0221 | 122.8559 | 66.7515 | -123.2466
17.9531 | 123.2162 | -66.7557 | 56.3004 | 0.063697 | 0.0022413 | 0.00069161 | 0.057544 | -0.00018888 | 0.057481 | 0.07176 | -0.00026221 | 0.0014765 | 0.065418 | -0.0027862 | 0.066549 | -64.5451 | 0.0243 | -66.6911 | 56.2518 | 56.0143 | 56.1657 | -66.8604 | -66.7336 | 0.014095 | -66.8368 | 55.9788 | 56.2893 | 56.0361 | -66.9645 | -0.10473 | -0.048515 | 2.2106 | 0.064611 | 0.16934 | -0.28601 | -0.13461 | -0.20884 | -0.32158 | 0.022027 | -0.081158 | 0.12768 | -0.011044 | -0.26424 | 123.0075 | 122.77 | 122.9214 | 66.78 | -123.1608 | 122.7345 | 123.045 | 122.7918 | 66.7698 | -123.2649
18.9375 | 123.1888 | -66.7786 | 56.3141 | 0.048435 | 0.0033103 | 0.00069161 | 0.056476 | -0.00018888 | 0.05855 | 0.07176 | -0.00026221 | 0.00040853 | 0.066487 | -0.0038542 | 0.066549 | -64.5451 | 0.0243 | -66.6956 | 56.261 | 56.0143 | 56.1612 | -66.8604 | -66.7382 | 0.023253 | -66.8414 | 55.9925 | 56.2893 | 56.1048 | -66.9554 | -0.081844 | -0.053092 | 2.2335 | 0.08292 | 0.16476 | -0.29974 | -0.15292 | -0.17679 | -0.32157 | 0.040337 | -0.062849 | 0.11394 | -0.024777 | -0.2093 | 123.0396 | 122.7929 | 122.9397 | 66.8029 | -123.1745 | 122.7711 | 123.0679 | 122.8834 | 66.8018 | -123.2694
19.9531 | 123.2391 | -66.7648 | 56.3461 | 0.063697 | 0.0033103 | 0.0017596 | 0.058613 | -0.00018888 | 0.056413 | 0.07176 | 0.00080679 | 0.00040853 | 0.067555 | -0.0038542 | 0.066549 | -64.5405 | 0.0243 | -66.6911 | 56.2564 | 56.0189 | 56.1612 | -66.8696 | -66.7245 | 0.018674 | -66.8323 | 55.9879 | 56.2893 | 56.0544 | -66.9554 | -0.10473 | -0.089713 | 2.2243 | 0.073767 | 0.1785 | -0.32721 | -0.18496 | -0.19052 | -0.3582 | 0.040341 | -0.067424 | 0.1231 | -0.05682 | -0.29171 | 123.0212 | 122.7838 | 122.926 | 66.7891 | -123.2157 | 122.7528 | 123.0541 | 122.8193 | 66.7835 | -123.3015
20.9375 | 123.1842 | -66.7969 | 56.3004 | 0.048435 | 0.0022413 | -0.00037739 | 0.057544 | -0.00018888 | 0.057481 | 0.07176 | 0.00080679 | 0.0025445 | 0.066487 | -0.0059912 | 0.065481 | -64.5496 | 0.019721 | -66.6956 | 56.2518 | 56.0098 | 56.1566 | -66.865 | -66.7382 | 0.014095 | -66.8414 | 55.9834 | 56.2847 | 56.1139 | -66.9645 | -0.068112 | -0.048515 | 2.2472 | 0.10123 | 0.16934 | -0.29059 | -0.14377 | -0.16764 | -0.317 | 0.058648 | -0.044538 | 0.1231 | -0.015623 | -0.18641 | 123.0487 | 122.8066 | 122.9535 | 66.8166 | -123.1653 | 122.7802 | 123.0816 | 122.9108 | 66.811 | -123.2649
21.9531 | 123.3307 | -66.7557 | 56.2546 | 0.048435 | 0.0022413 | 0.00069161 | 0.057544 | 0.0019481 | 0.05855 | 0.041238 | 0.00080679 | 0.0014765 | 0.066487 | -0.0038542 | 0.065481 | -64.6137 | 0.0243 | -66.6865 | 56.2473 | 56.0189 | 56.1657 | -66.865 | -66.7336 | 0.018674 | -66.846 | 55.9788 | 56.2847 | 56.1185 | -66.9645 | -0.10931 | -0.007318 | 2.1419 | 0.069189 | 0.1785 | -0.23566 | -0.088832 | -0.20884 | -0.2758 | 0.022027 | -0.090316 | 0.11852 | 0.030153 | -0.13605 | 123.0029 | 122.7746 | 122.9214 | 66.78 | -123.1196 | 122.7345 | 123.0404 | 122.8742 | 66.7743 | -123.2191
22.9375 | 123.1842 | -66.774 | 56.3324 | 0.048435 | 0.0011733 | -0.00037739 | 0.057544 | 0.00088012 | 0.056413 | 0.07176 | 0.0018748 | -0.00065947 | 0.06435 | -0.0038542 | 0.066549 | -64.5405 | 0.019721 | -66.7002 | 56.2564 | 56.0235 | 56.1703 | -66.865 | -66.7291 | 0.018674 | -66.846 | 55.9788 | 56.2893 | 56.0636 | -66.9691 | -0.091 | -0.07598 | 2.2335 | 0.073765 | 0.16477 | -0.3089 | -0.16207 | -0.1951 | -0.35362 | 0.044917 | -0.072005 | 0.1231 | -0.043087 | -0.26882 | 123.0304 | 122.7975 | 122.9443 | 66.7937 | -123.1974 | 122.7528 | 123.0633 | 122.8376 | 66.7927 | -123.3015
23.9375 | 123.2574 | -66.7694 | 56.3095 | 0.048435 | 0.0022413 | 0.00069161 | 0.057544 | 0.0019481 | 0.057481 | 0.056499 | -0.00026221 | 0.0014765 | 0.065418 | -0.0038542 | 0.065481 | -64.5405 | 0.019721 | -66.6911 | 56.2518 | 56.0189 | 56.1657 | -66.865 | -66.7336 | 0.023253 | -66.8368 | 55.9696 | 56.2893 | 56.0498 | -66.9691 | -0.095578 | -0.05767 | 2.2289 | 0.078344 | 0.17392 | -0.29059 | -0.14376 | -0.19968 | -0.33989 | 0.03576 | -0.067425 | 0.13226 | -0.020199 | -0.25966 | 123.0212 | 122.7883 | 122.9352 | 66.7891 | -123.1745 | 122.739 | 123.0587 | 122.8193 | 66.7927 | -123.2786
24.9375 | 123.2162 | -66.7969 | 56.3232 | 0.033173 | 0.0022413 | 0.00069161 | 0.057544 | -0.00018888 | 0.057481 | 0.041238 | 0.00080679 | 0.0025445 | 0.06435 | -0.0049232 | 0.065481 | -64.5405 | 0.019721 | -66.6911 | 56.2518 | 56.0281 | 56.1703 | -66.8696 | -66.7245 | 0.023253 | -66.8368 | 55.9788 | 56.2847 | 56.0911 | -66.9691 | -0.072691 | -0.071403 | 2.2564 | 0.10581 | 0.1785 | -0.29516 | -0.15292 | -0.17222 | -0.34446 | 0.072384 | -0.039959 | 0.13226 | -0.038511 | -0.23219 | 123.0487 | 122.825 | 122.9672 | 66.8166 | -123.1928 | 122.7757 | 123.0816 | 122.8879 | 66.8201 | -123.2923
25.9375 | 123.3078 | -66.7465 | 56.2592 | 0.048435 | 0.0022413 | 0.00069161 | 0.057544 | -0.00018888 | 0.057481 | 0.087021 | -0.0013302 | 0.00040853 | 0.066487 | -0.0027862 | 0.067618 | -64.6321 | 0.0243 | -66.6911 | 56.2518 | 56.0189 | 56.1657 | -66.865 | -66.7336 | 0.018674 | -66.8414 | 55.9742 | 56.2847 | 56.1414 | -66.9645 | -0.11847 | -0.007316 | 2.1145 | 0.055456 | 0.17392 | -0.24023 | -0.093409 | -0.21799 | -0.28496 | 0.012872 | -0.094892 | 0.1231 | 0.025576 | -0.11774 | 122.9984 | 122.7654 | 122.9123 | 66.7708 | -123.1241 | 122.7207 | 123.0313 | 122.8879 | 66.7652 | -123.2237
26.9375 | 123.2941 | -66.7191 | 56.2546 | 0.048435 | 0.0022413 | 0.00069161 | 0.056476 | 0.0019481 | 0.057481 | 0.056499 | 0.00080679 | -0.00065947 | 0.066487 | -0.0038542 | 0.066549 | -64.5954 | 0.019721 | -66.6911 | 56.261 | 56.0098 | 56.1612 | -66.8604 | -66.7245 | 0.023253 | -66.846 | 55.9696 | 56.2847 | 56.1002 | -66.9599 | -0.14135 | 0.006417 | 2.1236 | 0.02799 | 0.16934 | -0.24481 | -0.09341 | -0.24088 | -0.28496 | -0.005436 | -0.12694 | 0.11394 | 0.030153 | -0.15437 | 122.9801 | 122.7288 | 122.8802 | 66.7388 | -123.115 | 122.6887 | 123.0038 | 122.8193 | 66.7423 | -123.2145
27.9375 | 123.23 | -66.7603 | 56.3141 | 0.033173 | 0.0011733 | -0.00037739 | 0.057544 | -0.00018888 | 0.056413 | 0.07176 | 0.00080679 | -0.00065947 | 0.065418 | -0.0027862 | 0.065481 | -64.5405 | 0.0243 | -66.6956 | 56.2564 | 56.0143 | 56.1657 | -66.8741 | -66.7291 | 0.023253 | -66.846 | 55.965 | 56.2893 | 56.1048 | -66.9645 | -0.11389 | -0.05767 | 2.2198 | 0.06461 | 0.1785 | -0.29974 | -0.14834 | -0.20426 | -0.34905 | 0.031184 | -0.085738 | 0.11852 | -0.024777 | -0.2093 | 123.0167 | 122.7746 | 122.926 | 66.7846 | -123.1882 | 122.7253 | 123.0496 | 122.865 | 66.7835 | -123.2786
28.9531 | 123.2849 | -66.7374 | 56.3278 | 0.033173 | 0.0022413 | 0.0017596 | 0.057544 | -0.00018888 | 0.05855 | 0.07176 | 0.00080679 | -0.0017285 | 0.065418 | -0.0017182 | 0.066549 | -64.5725 | 0.019721 | -66.6911 | 56.2518 | 56.0235 | 56.1657 | -66.865 | -66.7336 | 0.023253 | -66.8414 | 55.9696 | 56.2802 | 56.146 | -66.9645 | -0.12762 | -0.075981 | 2.1648 | 0.046301 | 0.17392 | -0.30432 | -0.16207 | -0.22715 | -0.3582 | 0.003717 | -0.10405 | 0.1231 | -0.047667 | -0.18182 | 122.9892 | 122.7609 | 122.9031 | 66.7571 | -123.1928 | 122.707 | 123.0175 | 122.8834 | 66.7606 | -123.2923
29.9375 | 123.2483 | -66.7419 | 56.3187 | 0.048435 | 0.0033103 | 0.00069161 | 0.057544 | 0.00088012 | 0.057481 | 0.056499 | 0.00080679 | 0.0014765 | 0.066487 | -0.0027862 | 0.065481 | -64.5359 | 0.0243 | -66.7002 | 56.2564 | 56.0235 | 56.1703 | -66.865 | -66.7291 | 0.014095 | -66.8368 | 55.9788 | 56.2847 | 56.0636 | -66.9599 | -0.12304 | -0.062248 | 2.206 | 0.041721 | 0.16477 | -0.29516 | -0.14834 | -0.21799 | -0.33989 | 0.012873 | -0.094891 | 0.1231 | -0.033934 | -0.25508 | 122.9984 | 122.7654 | 122.9123 | 66.7662 | -123.1837 | 122.7207 | 123.0267 | 122.8055 | 66.756 | -123.2786
30.9844 | 123.2803 | -66.7282 | 56.3187 | 0.048435 | 0.0022413 | 0.00069161 | 0.057544 | 0.0019481 | 0.057481 | 0.056499 | 0.00080679 | 0.0014765 | 0.066487 | -0.0017182 | 0.066549 | -64.5863 | 0.028878 | -66.6865 | 56.2564 | 56.0189 | 56.1749 | -66.865 | -66.7291 | 0.014095 | -66.846 | 55.9788 | 56.2802 | 56.0865 | -66.9599 | -0.13678 | -0.062248 | 2.1419 | 0.041723 | 0.1785 | -0.29974 | -0.14376 | -0.23172 | -0.33989 | -0.00086 | -0.11778 | 0.11394 | -0.038512 | -0.23219 | 122.9846 | 122.7471 | 122.9031 | 66.7571 | -123.1837 | 122.707 | 123.0084 | 122.8147 | 66.7423 | -123.2786
31.9375 | 123.2986 | -66.7511 | 56.282 | 0.063697 | 0.0022413 | -0.00037739 | 0.057544 | 0.00088012 | 0.056413 | 0.056499 | 0.00080679 | 0.00040853 | 0.065418 | -0.0027862 | 0.064413 | -64.6183 | 0.019721 | -66.6956 | 56.2564 | 56.0143 | 56.1612 | -66.8604 | -66.7291 | 0.018674 | -66.846 | 55.9696 | 56.2756 | 56.0956 | -66.9645 | -0.10931 | -0.025626 | 2.1328 | 0.055455 | 0.16476 | -0.2677 | -0.12087 | -0.21341 | -0.31242 | 0.022029 | -0.094893 | 0.11852 | -0.006469 | -0.18641 | 123.0075 | 122.7654 | 122.9123 | 66.7708 | -123.1425 | 122.7207 | 123.0267 | 122.8467 | 66.7698 | -123.2466
32.9531 | 123.2895 | -66.7419 | 56.2775 | 0.048435 | 0.0011733 | 0.00069161 | 0.057544 | -0.00018888 | 0.059618 | 0.056499 | -0.00026221 | -0.0017285 | 0.066487 | -0.0038542 | 0.065481 | -64.5863 | 0.019721 | -66.6911 | 56.2564 | 56.0143 | 56.1612 | -66.8604 | -66.7291 | 0.018674 | -66.846 | 55.9696 | 56.2847 | 56.0224 | -66.9645 | -0.11847 | -0.021049 | 2.1557 | 0.050878 | 0.16934 | -0.26312 | -0.1163 | -0.22257 | -0.30785 | 0.012873 | -0.10405 | 0.11852 | 0.007265 | -0.25509 | 122.9984 | 122.7563 | 122.9031 | 66.7617 | -123.1379 | 122.7116 | 123.0267 | 122.7643 | 66.7606 | -123.242
33.9375 | 123.2712 | -66.7419 | 56.3095 | 0.048435 | 0.0022413 | -0.00037739 | 0.057544 | 0.00088012 | 0.057481 | 0.056499 | -0.00026221 | -0.0017285 | 0.065418 | -0.0017182 | 0.066549 | -64.5313 | 0.0243 | -66.6956 | 56.2564 | 56.0189 | 56.1703 | -66.8741 | -66.7336 | 0.018674 | -66.8414 | 55.9742 | 56.2802 | 56.1323 | -66.9645 | -0.1322 | -0.053092 | 2.2106 | 0.046299 | 0.1785 | -0.29059 | -0.13918 | -0.22257 | -0.33531 | 0.008294 | -0.09947 | 0.1231 | -0.029356 | -0.17725 | 122.9984 | 122.7609 | 122.9123 | 66.7662 | -123.1837 | 122.7161 | 123.0221 | 122.8742 | 66.7606 | -123.274
34.9688 | 123.381 | -66.7007 | 56.282 | 0.063697 | 0.0011733 | 0.00069161 | 0.055407 | 0.00088012 | 0.056413 | 0.056499 | 0.0018748 | 0.00040853 | 0.066487 | -0.0027862 | 0.065481 | -64.6412 | 0.010564 | -66.7277 | 56.2793 | 56.0098 | 56.1795 | -66.8879 | -66.7565 | 0.018674 | -66.846 | 56.0932 | 56.2847 | 56.0727 | -66.9599 | -0.18714 | -0.002734 | 2.0595 | -0.026947 | 0.16019 | -0.27228 | -0.10256 | -0.25919 | -0.1888 | -0.055797 | -0.14525 | 0.11394 | 0.002688 | -0.20931 | 122.9801 | 122.7105 | 122.8802 | 66.7113 | -123.1699 | 122.794 | 122.9855 | 122.7735 | 66.7194 | -123.242
35.9375 | 123.262 | -66.7648 | 56.3049 | 0.048435 | 0.0022413 | -0.00037739 | 0.057544 | -0.00018888 | 0.055345 | 0.087021 | -0.00026221 | 0.0014765 | 0.066487 | -0.0017182 | 0.064413 | -64.5588 | 0.019721 | -66.714 | 56.2839 | 56.0281 | 56.1886 | -66.9062 | -66.7474 | 0.014095 | -66.8323 | 56.1253 | 56.2847 | 56.0682 | -66.9645 | -0.14137 | -0.021045 | 2.206 | 0.050875 | 0.19224 | -0.27685 | -0.11629 | -0.19968 | -0.17964 | 0.017447 | -0.067424 | 0.13226 | -0.020201 | -0.23677 | 123.0487 | 122.7929 | 122.9535 | 66.7846 | -123.2111 | 122.8901 | 123.0496 | 122.833 | 66.7789 | -123.2694
36.9531 | 123.3673 | -66.7374 | 56.3004 | 0.048435 | 0.0001043 | 0.00069161 | 0.057544 | 0.00088012 | 0.056413 | 0.07176 | 0.00080679 | -0.00065947 | 0.063282 | -0.0027862 | 0.065481 | -64.6321 | 0.019721 | -66.7185 | 56.2793 | 55.996 | 56.1932 | -66.8879 | -66.752 | 0.009516 | -66.8368 | 56.1207 | 56.2893 | 56.0544 | -66.9691 | -0.15052 | -0.021045 | 2.1053 | 0.018831 | 0.16935 | -0.30433 | -0.10714 | -0.23173 | -0.17964 | -0.014597 | -0.099468 | 0.13226 | -0.011044 | -0.24593 | 123.0167 | 122.7334 | 122.9306 | 66.7571 | -123.1882 | 122.8581 | 123.0267 | 122.7918 | 66.7469 | -123.2694
37.9375 | 123.175 | -66.7648 | 56.3187 | 0.063697 | 0.0011733 | -0.00037739 | 0.057544 | -0.0012569 | 0.056413 | 0.07176 | 0.00080679 | -0.00065947 | 0.065418 | -0.0017182 | 0.065481 | -64.568 | 0.028878 | -66.7185 | 56.2839 | 56.0235 | 56.1932 | -66.8604 | -66.752 | 0.014095 | -66.846 | 56.1207 | 56.2847 | 56.0407 | -66.9645 | -0.095576 | -0.034778 | 2.1969 | 0.046297 | 0.14187 | -0.29516 | -0.12545 | -0.19968 | -0.19795 | 0.012869 | -0.08116 | 0.11852 | -0.033934 | -0.27798 | 123.0487 | 122.7883 | 122.9581 | 66.7937 | -123.1791 | 122.8855 | 123.0496 | 122.8055 | 66.7789 | -123.2832
38.9531 | 123.1979 | -66.7557 | 56.3095 | 0.063697 | -0.0009637 | 0.00069161 | 0.058613 | 0.00088012 | 0.057481 | 0.056499 | 0.00080679 | -0.0017285 | 0.065418 | -0.00064921 | 0.064413 | -64.5771 | 0.0243 | -66.7185 | 56.2793 | 56.0189 | 56.1795 | -66.8055 | -66.7565 | 0.014095 | -66.846 | 56.0887 | 56.2939 | 56.0498 | -66.9691 | -0.049785 | -0.0302 | 2.1786 | 0.037141 | 0.086926 | -0.29059 | -0.13003 | -0.21342 | -0.22085 | -0.000866 | -0.090316 | 0.1231 | -0.01562 | -0.25966 | 123.035 | 122.7746 | 122.9352 | 66.78 | -123.115 | 122.8443 | 123.0496 | 122.8055 | 66.7698 | -123.2786
39.9375 | 123.2117 | -66.7465 | 56.3507 | 0.063697 | -0.0009637 | 0.00069161 | 0.056476 | -0.0012569 | 0.056413 | 0.10228 | -0.00026221 | -0.00065947 | 0.065418 | -0.0027862 | 0.064413 | -64.5451 | 0.015142 | -66.714 | 56.2747 | 56.0189 | 56.1841 | -66.9016 | -66.752 | 0.009516 | -66.846 | 56.107 | 56.2893 | 56.0636 | -66.9645 | -0.1551 | -0.075977 | 2.2015 | 0.032564 | 0.18766 | -0.33179 | -0.16665 | -0.21799 | -0.24373 | -0.005442 | -0.099471 | 0.11852 | -0.061398 | -0.28713 | 123.0213 | 122.7654 | 122.9306 | 66.7617 | -123.2523 | 122.8535 | 123.0358 | 122.8101 | 66.756 | -123.3152
40.9531 | 123.1934 | -66.7831 | 56.3461 | 0.078959 | 0.0022413 | -0.00037739 | 0.056476 | 0.00088012 | 0.055345 | 0.087021 | -0.0013302 | -0.00065947 | 0.06435 | -0.0017182 | 0.064413 | -64.5634 | 0.0243 | -66.7277 | 56.293 | 56.0189 | 56.1932 | -66.8879 | -66.7657 | 0.014095 | -66.846 | 56.1161 | 56.2847 | 56.0727 | -66.9737 | -0.10474 | -0.053086 | 2.2198 | 0.05545 | 0.16019 | -0.32721 | -0.15291 | -0.19053 | -0.23 | 0.017443 | -0.06285 | 0.12768 | -0.061399 | -0.27339 | 123.0762 | 122.8021 | 122.9764 | 66.8074 | -123.234 | 122.8993 | 123.0679 | 122.8559 | 66.7972 | -123.3198
41.9375 | 123.262 | -66.7557 | 56.3141 | 0.078959 | 0.0001043 | -0.00037739 | 0.055407 | -0.0012569 | 0.055345 | 0.087021 | -0.00026221 | 0.00040853 | 0.065418 | 0.00041879 | 0.065481 | -64.5451 | 0.0243 | -66.7277 | 56.2839 | 56.0189 | 56.1932 | -66.8192 | -66.7657 | 0.023253 | -66.8414 | 56.1116 | 56.2847 | 56.0865 | -66.9737 | -0.063522 | -0.0302 | 2.2106 | 0.027984 | 0.091506 | -0.29516 | -0.12087 | -0.21799 | -0.20253 | -0.010023 | -0.085737 | 0.13226 | -0.029356 | -0.22761 | 123.0396 | 122.7746 | 122.9489 | 66.78 | -123.1333 | 122.8672 | 123.0404 | 122.8422 | 66.7789 | -123.2878
42.9531 | 123.2712 | -66.7465 | 56.2637 | 0.063697 | 0.0001043 | 0.00069161 | 0.056476 | 0.00088012 | 0.055345 | 0.087021 | 0.00080679 | 0.00040853 | 0.065418 | -0.0017182 | 0.064413 | -64.5863 | 0.019721 | -66.7185 | 56.2702 | 56.0006 | 56.1886 | -66.8329 | -66.7611 | 0.014095 | -66.846 | 56.0429 | 56.2802 | 56.0773 | -66.9599 | -0.086414 | 0.006419 | 2.1603 | 0.027986 | 0.1144 | -0.26313 | -0.075094 | -0.21341 | -0.22086 | -0.0146 | -0.099471 | 0.11394 | 0.01642 | -0.18642 | 123.0167 | 122.7471 | 122.9352 | 66.7662 | -123.0967 | 122.7894 | 123.0267 | 122.8238 | 66.7606 | -123.2237
43.9375 | 123.2071 | -66.7694 | 56.3416 | 0.048435 | 0.0022413 | -0.00037739 | 0.056476 | -0.00018888 | 0.056413 | 0.07176 | -0.00026221 | -0.00065947 | 0.065418 | -0.00064921 | 0.065481 | -64.5817 | 0.028878 | -66.7094 | 56.2793 | 56.0418 | 56.1932 | -66.8925 | -66.7382 | 0.018674 | -66.8414 | 56.1161 | 56.2939 | 56.0819 | -66.9691 | -0.12305 | -0.062244 | 2.1877 | 0.06003 | 0.18308 | -0.29974 | -0.14833 | -0.19968 | -0.22542 | 0.031182 | -0.072004 | 0.12768 | -0.047664 | -0.25966 | 123.0487 | 122.8112 | 122.9626 | 66.7983 | -123.234 | 122.8855 | 123.0633 | 122.8513 | 66.7881 | -123.3106
44.9375 | 123.2712 | -66.7328 | 56.2683 | 0.063697 | 0.0001043 | 0.0017596 | 0.055407 | 0.00088012 | 0.055345 | 0.041238 | 0.00080679 | 0.0014765 | 0.06435 | -0.0017182 | 0.063345 | -64.6595 | 0.019721 | -66.6911 | 56.2656 | 56.0418 | 56.1703 | -66.8879 | -66.7382 | 0.009516 | -66.8368 | 56.1116 | 56.2893 | 56.1872 | -66.9737 | -0.15509 | -0.002737 | 2.0733 | 0.041723 | 0.19682 | -0.22649 | -0.097986 | -0.24088 | -0.15676 | -0.005439 | -0.10405 | 0.13684 | 0.020999 | -0.081107 | 122.9984 | 122.7746 | 122.9031 | 66.7525 | -123.1562 | 122.8443 | 123.0221 | 122.92 | 66.7423 | -123.242
45.9375 | 123.2071 | -66.7694 | 56.3507 | 0.048435 | -0.0020317 | -0.00037739 | 0.054339 | -0.0012569 | 0.059618 | 0.056499 | 0.00080679 | -0.00065947 | 0.065418 | -0.00064921 | 0.064413 | -64.6046 | 0.019721 | -66.6911 | 56.2564 | 56.1105 | 56.1657 | -66.8741 | -66.7291 | 0.014095 | -66.8414 | 56.0932 | 56.2847 | 56.2788 | -66.9737 | -0.10474 | -0.094291 | 2.1648 | 0.078344 | 0.18308 | -0.24021 | -0.18496 | -0.20426 | -0.25747 | 0.040339 | -0.072004 | 0.13226 | -0.065977 | -0.071932 | 123.0258 | 122.8799 | 122.9352 | 66.7891 | -123.2249 | 122.8626 | 123.0541 | 123.0482 | 66.7835 | -123.3244
46.9531 | 123.2758 | -66.7557 | 56.2866 | 0.063697 | -0.0009637 | 0.00069161 | 0.055407 | -0.00018888 | 0.05855 | 0.041238 | 0.00080679 | 0.0014765 | 0.065418 | -0.0017182 | 0.065481 | -64.6916 | 0.019721 | -66.6956 | 56.2564 | 56.1059 | 56.1749 | -66.8741 | -66.7336 | 0.018674 | -66.8414 | 56.0749 | 56.2939 | 56.2605 | -66.9691 | -0.11847 | -0.030204 | 2.0641 | 0.060032 | 0.1785 | -0.1807 | -0.11172 | -0.21342 | -0.21169 | 0.022027 | -0.085737 | 0.12768 | 0.007268 | -0.02616 | 123.0121 | 122.8616 | 122.9306 | 66.7754 | -123.1608 | 122.8306 | 123.0496 | 123.0161 | 66.7743 | -123.2557
47.9375 | 123.1613 | -66.7786 | 56.3461 | 0.063697 | 0.0033103 | 0.0017596 | 0.055407 | 0.00088012 | 0.057481 | 0.056499 | -0.00026221 | 0.0014765 | 0.065418 | 0.0014878 | 0.065481 | -64.5817 | 0.0243 | -66.6956 | 56.2564 | 56.1105 | 56.1749 | -66.8741 | -66.7336 | 0.023253 | -66.8323 | 56.0658 | 56.2893 | 56.2605 | -66.9691 | -0.095581 | -0.089713 | 2.1969 | 0.08292 | 0.1785 | -0.23563 | -0.17123 | -0.19053 | -0.28036 | 0.044915 | -0.053692 | 0.13684 | -0.05682 | -0.085669 | 123.035 | 122.8891 | 122.9535 | 66.8029 | -123.2203 | 122.8443 | 123.0679 | 123.039 | 66.8018 | -123.3152
48.9531 | 123.2574 | -66.7465 | 56.3049 | 0.048435 | 0.0001043 | 0.0017596 | 0.057544 | 0.00088012 | 0.05855 | 0.07176 | -0.00026221 | -0.00065947 | 0.066487 | -0.00064921 | 0.066549 | -64.6549 | 0.0243 | -66.6956 | 56.2564 | 56.0968 | 56.1749 | -66.8696 | -66.7291 | 0.009516 | -66.8414 | 56.0566 | 56.2802 | 56.2284 | -66.9737 | -0.12305 | -0.048515 | 2.0916 | 0.050877 | 0.17392 | -0.20817 | -0.13003 | -0.22715 | -0.24832 | 0.017451 | -0.094892 | 0.13226 | -0.024779 | -0.076521 | 123.0029 | 122.8433 | 122.9214 | 66.7708 | -123.1745 | 122.8031 | 123.0267 | 122.9749 | 66.756 | -123.2786
49.9375 | 123.1888 | -66.7465 | 56.3416 | 0.063697 | -0.0009637 | -0.00037739 | 0.057544 | -0.00018888 | 0.057481 | 0.087021 | -0.0023982 | -0.0017285 | 0.06435 | -0.0017182 | 0.065481 | -64.5542 | 0.019721 | -66.6911 | 56.2564 | 56.0922 | 56.1749 | -66.8833 | -66.7336 | 0.014095 | -66.8368 | 56.0566 | 56.2802 | 56.2055 | -66.9599 | -0.13678 | -0.085136 | 2.1923 | 0.055456 | 0.19224 | -0.24937 | -0.16665 | -0.21341 | -0.28494 | 0.012872 | -0.090313 | 0.1231 | -0.0614 | -0.13603 | 123.0029 | 122.8387 | 122.9214 | 66.7662 | -123.2249 | 122.8031 | 123.0267 | 122.952 | 66.7606 | -123.3015
50.9375 | 123.23 | -66.7511 | 56.2958 | 0.094221 | 0.0011733 | 0.00069161 | 0.056476 | -0.00018888 | 0.056413 | 0.087021 | 0.00080679 | -0.0017285 | 0.066487 | -0.00064921 | 0.064413 | -64.5634 | 0.015142 | -66.6911 | 56.2564 | 56.0876 | 56.1703 | -66.865 | -66.7382 | 0.023253 | -66.8368 | 56.0566 | 56.2802 | 56.2147 | -66.9737 | -0.11389 | -0.039359 | 2.1877 | 0.060034 | 0.17392 | -0.20817 | -0.12545 | -0.22257 | -0.23916 | 0.012872 | -0.085735 | 0.13684 | -0.015623 | -0.081101 | 123.0075 | 122.8387 | 122.9214 | 66.7662 | -123.1608 | 122.8077 | 123.0313 | 122.9658 | 66.7744 | -123.2694
51.9375 | 123.2895 | -66.7374 | 56.3187 | 0.078959 | 0.0001043 | -0.0025134 | 0.056476 | -0.00018888 | 0.057481 | 0.07176 | 0.00080679 | 0.00040853 | 0.06435 | 0.00041879 | 0.064413 | -64.5725 | 0.015142 | -66.6865 | 56.2656 | 56.0922 | 56.1657 | -66.8741 | -66.7336 | 0.014095 | -66.846 | 56.052 | 56.2847 | 56.2376 | -66.9645 | -0.13678 | -0.053091 | 2.1648 | 0.050879 | 0.18766 | -0.22648 | -0.15292 | -0.22715 | -0.26663 | 0.003717 | -0.10863 | 0.11852 | -0.033934 | -0.081097 | 123.0029 | 122.8296 | 122.9031 | 66.7525 | -123.1928 | 122.7894 | 123.0221 | 122.9749 | 66.7515 | -123.2832
52.9375 | 123.2071 | -66.7648 | 56.3461 | 0.063697 | 0.0001043 | -0.00037739 | 0.057544 | 0.00088012 | 0.057481 | 0.056499 | 0.00080679 | -0.0017285 | 0.06435 | 0.00041879 | 0.064413 | -64.5542 | 0.0243 | -66.6911 | 56.2564 | 56.0693 | 56.1657 | -66.8741 | -66.7336 | 0.018674 | -66.8368 | 56.052 | 56.2802 | 56.2421 | -66.9645 | -0.10931 | -0.089713 | 2.2106 | 0.073767 | 0.18308 | -0.27684 | -0.18038 | -0.19968 | -0.2941 | 0.031183 | -0.072002 | 0.12768 | -0.065977 | -0.10398 | 123.0212 | 122.8341 | 122.9306 | 66.7891 | -123.2203 | 122.8169 | 123.045 | 123.007 | 66.7835 | -123.3106
53.9375 | 123.2025 | -66.7419 | 56.3416 | 0.048435 | -0.0020317 | -0.00037739 | 0.056476 | -0.00018888 | 0.055345 | 0.07176 | -0.0013302 | 0.00040853 | 0.063282 | 0.0014878 | 0.066549 | -64.5496 | 0.0243 | -66.6865 | 56.2564 | 56.0739 | 56.1703 | -66.8741 | -66.7291 | 0.014095 | -66.8368 | 56.0429 | 56.2802 | 56.2467 | -66.9737 | -0.1322 | -0.085136 | 2.1923 | 0.055456 | 0.18766 | -0.26768 | -0.17123 | -0.23173 | -0.29868 | 0.012873 | -0.094891 | 0.13684 | -0.0614 | -0.094828 | 122.9984 | 122.8158 | 122.9123 | 66.7662 | -123.2157 | 122.7848 | 123.0221 | 122.9887 | 66.756 | -123.3152
54.9531 | 123.3124 | -66.7282 | 56.3187 | 0.063697 | -0.0009637 | -0.0035824 | 0.055407 | -0.0023249 | 0.054276 | 0.087021 | -0.0013302 | 0.00040853 | 0.06435 | 0.0014878 | 0.064413 | -64.6 | 0.019721 | -66.6865 | 56.2564 | 56.0693 | 56.1612 | -66.8696 | -66.7291 | 0.009516 | -66.8414 | 56.0383 | 56.2893 | 56.233 | -66.9737 | -0.14136 | -0.062248 | 2.1282 | 0.041723 | 0.18308 | -0.24938 | -0.1575 | -0.24546 | -0.28037 | -0.00086 | -0.1132 | 0.13226 | -0.029355 | -0.085675 | 122.9846 | 122.7975 | 122.8894 | 66.7479 | -123.1882 | 122.7665 | 123.0175 | 122.9612 | 66.7377 | -123.2923
55.9375 | 123.1842 | -66.7419 | 56.3507 | 0.063697 | -0.0020317 | -0.00037739 | 0.055407 | -0.0012569 | 0.055345 | 0.087021 | 0.00080679 | -0.00065947 | 0.063282 | 0.00041879 | 0.065481 | -64.5359 | 0.019721 | -66.6956 | 56.2518 | 56.0784 | 56.1657 | -66.8604 | -66.7291 | 0.018674 | -66.8368 | 56.0383 | 56.2893 | 56.2376 | -66.9691 | -0.11847 | -0.098869 | 2.206 | 0.046299 | 0.16476 | -0.27226 | -0.18496 | -0.22715 | -0.31241 | 0.012873 | -0.094891 | 0.13226 | -0.061398 | -0.11314 | 122.9938 | 122.8204 | 122.9077 | 66.7617 | -123.2111 | 122.7802 | 123.0313 | 122.9795 | 66.7606 | -123.3198
56.9375 | 123.2071 | -66.7374 | 56.3416 | 0.078959 | -0.0009637 | -0.00037739 | 0.057544 | 0.0019481 | 0.055345 | 0.07176 | -0.00026221 | -0.00065947 | 0.06435 | 0.0014878 | 0.065481 | -64.5405 | 0.019721 | -66.6956 | 56.2473 | 56.0647 | 56.1749 | -66.865 | -66.7336 | 0.018674 | -66.8414 | 56.0429 | 56.2893 | 56.233 | -66.9691 | -0.12762 | -0.094293 | 2.1969 | 0.041722 | 0.16934 | -0.27684 | -0.16665 | -0.23173 | -0.29868 | 0.003717 | -0.10405 | 0.12768 | -0.052243 | -0.10856 | 122.9846 | 122.8021 | 122.9123 | 66.7571 | -123.2065 | 122.7802 | 123.0267 | 122.9704 | 66.756 | -123.3106
57.9375 | 123.2941 | -66.7145 | 56.3049 | 0.033173 | -0.0009637 | -0.0025134 | 0.058613 | -0.0023249 | 0.056413 | 0.07176 | -0.00026221 | -0.0017285 | 0.065418 | 0.00041879 | 0.065481 | -64.5588 | 0.015142 | -66.6956 | 56.261 | 56.0739 | 56.1657 | -66.8604 | -66.7336 | 0.018674 | -66.846 | 56.0291 | 56.2802 | 56.233 | -66.9645 | -0.14593 | -0.043937 | 2.1557 | 0.018834 | 0.16476 | -0.23106 | -0.13919 | -0.25003 | -0.27579 | -0.019171 | -0.13151 | 0.11852 | -0.024779 | -0.071942 | 122.9755 | 122.7883 | 122.8802 | 66.7296 | -123.1653 | 122.7436 | 122.9946 | 122.9475 | 66.7332 | -123.2694
58.9375 | 123.2803 | -66.7328 | 56.3049 | 0.078959 | -0.0009637 | -0.00037739 | 0.058613 | -0.0023249 | 0.055345 | 0.07176 | -0.0013302 | -0.0027965 | 0.065418 | 0.0014878 | 0.066549 | -64.5451 | 0.015142 | -66.6819 | 56.2518 | 56.0693 | 56.1657 | -66.8696 | -66.7245 | 0.018674 | -66.846 | 56.0429 | 56.2893 | 56.233 | -66.9737 | -0.13678 | -0.053093 | 2.1877 | 0.050879 | 0.18766 | -0.23564 | -0.13919 | -0.24088 | -0.26206 | 0.008297 | -0.1132 | 0.12768 | -0.015622 | -0.071942 | 122.9846 | 122.8021 | 122.8985 | 66.7479 | -123.1745 | 122.7757 | 123.0221 | 122.9658 | 66.7515 | -123.2786
59.9375 | 123.3536 | -66.6916 | 56.3004 | 0.048435 | 0.0001043 | 0.00069161 | 0.055407 | -0.0033929 | 0.053208 | 0.056499 | 0.0018748 | 0.00040853 | 0.06435 | 0.0036238 | 0.065481 | -64.5863 | 0.019721 | -66.6956 | 56.2518 | 56.0739 | 56.1703 | -66.8696 | -66.7291 | 0.023253 | -66.8368 | 56.0429 | 56.2893 | 56.2421 | -66.9782 | -0.17798 | -0.048515 | 2.1053 | -0.004055 | 0.17392 | -0.22648 | -0.13003 | -0.28666 | -0.25748 | -0.037481 | -0.14525 | 0.14142 | -0.011044 | -0.058207 | 122.9434 | 122.7655 | 122.8619 | 66.7113 | -123.1699 | 122.7345 | 122.9809 | 122.9337 | 66.7148 | -123.2786
60.9375 | 123.2254 | -66.7786 | 56.3324 | 0.033173 | -0.0009637 | 0.00069161 | 0.058613 | -0.00018888 | 0.055345 | 0.07176 | -0.0023982 | -0.0017285 | 0.063282 | 0.0025558 | 0.065481 | -64.5496 | 0.0243 | -66.6911 | 56.2564 | 56.083 | 56.1703 | -66.8741 | -66.7245 | 0.018674 | -66.846 | 56.0383 | 56.2939 | 56.2284 | -66.9737 | -0.095581 | -0.07598 | 2.2289 | 0.087499 | 0.18308 | -0.24937 | -0.16207 | -0.19511 | -0.2941 | 0.054073 | -0.067428 | 0.12768 | -0.038508 | -0.10399 | 123.035 | 122.8616 | 122.9489 | 66.8029 | -123.2065 | 122.8169 | 123.0725 | 123.007 | 66.7972 | -123.3061
61.9531 | 123.2895 | -66.7374 | 56.2912 | 0.033173 | -0.0020317 | -0.00037739 | 0.056476 | -0.0012569 | 0.056413 | 0.056499 | -0.00026221 | -0.00065947 | 0.063282 | 0.0014878 | 0.064413 | -64.6229 | 0.0243 | -66.6911 | 56.2564 | 56.0739 | 56.1703 | -66.8696 | -66.7336 | 0.018674 | -66.8414 | 56.0383 | 56.2802 | 56.2238 | -66.9737 | -0.1322 | -0.034782 | 2.1145 | 0.046301 | 0.1785 | -0.21733 | -0.12087 | -0.2363 | -0.2529 | 0.003717 | -0.10405 | 0.13226 | -0.011046 | -0.067367 | 122.9938 | 122.8112 | 122.9077 | 66.7617 | -123.1608 | 122.7757 | 123.0175 | 122.9612 | 66.756 | -123.2649
62.9375 | 123.2803 | -66.7236 | 56.3004 | 0.063697 | -0.0009637 | 0.0017596 | 0.056476 | 0.00088012 | 0.056413 | 0.087021 | -0.0013302 | -0.0027965 | 0.06435 | 0.0036238 | 0.064413 | -64.5588 | 0.019721 | -66.6911 | 56.261 | 56.0739 | 56.1657 | -66.8696 | -66.7245 | 0.014095 | -66.8414 | 56.0337 | 56.2847 | 56.2421 | -66.9737 | -0.14593 | -0.039359 | 2.1648 | 0.032568 | 0.1785 | -0.22648 | -0.13461 | -0.25004 | -0.26664 | -0.000858 | -0.11778 | 0.13226 | -0.015623 | -0.058207 | 122.9846 | 122.7975 | 122.8894 | 66.7434 | -123.1699 | 122.7574 | 123.0084 | 122.9658 | 66.7377 | -123.274
63.9531 | 123.2803 | -66.7236 | 56.2729 | 0.063697 | -0.0020317 | -0.00037739 | 0.056476 | -0.0023249 | 0.057481 | 0.056499 | -0.0013302 | -0.00065947 | 0.063282 | 0.0014878 | 0.066549 | -64.6137 | 0.019721 | -66.6911 | 56.261 | 56.0739 | 56.1703 | -66.8741 | -66.7336 | 0.023253 | -66.846 | 56.0475 | 56.2802 | 56.2376 | -66.9691 | -0.15051 | -0.011893 | 2.1099 | 0.032568 | 0.18308 | -0.19902 | -0.10256 | -0.24546 | -0.22543 | -0.010016 | -0.12236 | 0.1231 | 0.007265 | -0.03532 | 122.9846 | 122.7975 | 122.894 | 66.7434 | -123.147 | 122.7711 | 123.0038 | 122.9612 | 66.7469 | -123.242
64.9375 | 123.3673 | -66.7099 | 56.2958 | 0.094221 | -0.0020317 | -0.00037739 | 0.054339 | -0.00018888 | 0.055345 | 0.087021 | -0.0013302 | -0.0017285 | 0.06435 | 0.0014878 | 0.064413 | -64.6046 | 0.019721 | -66.6911 | 56.2564 | 56.0922 | 56.1795 | -66.865 | -66.7291 | 0.018674 | -66.8414 | 56.0383 | 56.2893 | 56.2467 | -66.9691 | -0.15509 | -0.039359 | 2.1053 | 0.018835 | 0.17392 | -0.20359 | -0.11629 | -0.25919 | -0.25748 | -0.01917 | -0.13151 | 0.12768 | -0.006466 | -0.049051 | 122.9663 | 122.8021 | 122.8894 | 66.7296 | -123.1608 | 122.7482 | 122.9992 | 122.9566 | 66.7286 | -123.2649
65.9375 | 123.3353 | -66.7053 | 56.282 | 0.063697 | -0.0009637 | -0.00037739 | 0.057544 | -0.0023249 | 0.055345 | 0.056499 | -0.0023982 | -0.00065947 | 0.065418 | 0.0014878 | 0.063345 | -64.5908 | 0.028878 | -66.6911 | 56.2564 | 56.083 | 56.1703 | -66.8741 | -66.7245 | 0.014095 | -66.846 | 56.0475 | 56.2893 | 56.2467 | -66.9645 | -0.16882 | -0.025626 | 2.1145 | 0.014257 | 0.18308 | -0.19902 | -0.11172 | -0.25919 | -0.23459 | -0.019169 | -0.14067 | 0.11852 | 0.007267 | -0.035318 | 122.9617 | 122.7883 | 122.8756 | 66.7342 | -123.1562 | 122.7528 | 122.9946 | 122.952 | 66.7194 | -123.2466
66.9531 | 123.1979 | -66.7511 | 56.3461 | 0.063697 | -0.0020317 | -0.0014454 | 0.056476 | -0.00018888 | 0.054276 | 0.07176 | -0.0013302 | -0.0017285 | 0.065418 | 0.0036238 | 0.064413 | -64.5634 | 0.0243 | -66.7002 | 56.2564 | 56.0784 | 56.1841 | -66.8696 | -66.7336 | 0.014095 | -66.8368 | 56.052 | 56.2847 | 56.2238 | -66.9691 | -0.11847 | -0.089713 | 2.1877 | 0.050877 | 0.16934 | -0.26768 | -0.16207 | -0.21799 | -0.2941 | 0.01745 | -0.085735 | 0.13226 | -0.061399 | -0.1223 | 123.0075 | 122.8295 | 122.9352 | 66.7754 | -123.2157 | 122.8031 | 123.0358 | 122.9749 | 66.7652 | -123.3152
67.9375 | 123.3627 | -66.7236 | 56.3141 | 0.078959 | -0.0009637 | 0.00069161 | 0.056476 | 0.00088012 | 0.057481 | 0.07176 | -0.00026221 | 0.00040853 | 0.063282 | 0.0025558 | 0.066549 | -64.6137 | 0.019721 | -66.6865 | 56.2564 | 56.0876 | 56.1749 | -66.8696 | -66.7245 | 0.014095 | -66.8368 | 56.0475 | 56.2939 | 56.233 | -66.9645 | -0.14593 | -0.05767 | 2.1099 | 0.037146 | 0.18308 | -0.22648 | -0.13918 | -0.24088 | -0.26663 | -0.000858 | -0.1132 | 0.12768 | -0.020198 | -0.081097 | 122.9801 | 122.8112 | 122.8985 | 66.7434 | -123.1837 | 122.7711 | 123.0175 | 122.9566 | 66.7377 | -123.2786
68.9375 | 123.349 | -66.7099 | 56.2866 | 0.048435 | -0.0041687 | 0.00069161 | 0.056476 | -0.00018888 | 0.055345 | 0.10228 | 0.00080679 | -0.0027965 | 0.065418 | 0.0014878 | 0.064413 | -64.5863 | 0.028878 | -66.6911 | 56.2564 | 56.083 | 56.1703 | -66.865 | -66.7291 | 0.014095 | -66.8323 | 56.052 | 56.2893 | 56.2238 | -66.9737 | -0.15509 | -0.030204 | 2.1236 | 0.018835 | 0.17392 | -0.20359 | -0.1163 | -0.26377 | -0.23459 | -0.01917 | -0.12236 | 0.14141 | 0.002689 | -0.062789 | 122.9663 | 122.7929 | 122.8802 | 66.7388 | -123.1516 | 122.7619 | 122.9992 | 122.9337 | 66.724 | -123.2603
69.9375 | 123.3582 | -66.7099 | 56.3141 | 0.033173 | -0.0020317 | -0.00037739 | 0.057544 | -0.0012569 | 0.056413 | 0.07176 | -0.0013302 | 0.00040853 | 0.06435 | 0.0025558 | 0.062276 | -64.6275 | 0.019721 | -66.6956 | 56.2564 | 56.0968 | 56.1795 | -66.8741 | -66.7291 | 0.018674 | -66.8414 | 56.0612 | 56.2847 | 56.2376 | -66.9737 | -0.16424 | -0.05767 | 2.0824 | 0.014256 | 0.1785 | -0.21732 | -0.13461 | -0.26377 | -0.2529 | -0.01917 | -0.13151 | 0.13226 | -0.029356 | -0.076519 | 122.9663 | 122.8067 | 122.8894 | 66.7296 | -123.1882 | 122.7711 | 122.9946 | 122.9475 | 66.7286 | -123.2878
70.9375 | 123.3261 | -66.7191 | 56.3141 | 0.033173 | 0.0001043 | -0.0014454 | 0.054339 | -0.00018888 | 0.05855 | 0.056499 | -0.0013302 | 0.00040853 | 0.06435 | 0.0025558 | 0.066549 | -64.6412 | 0.0243 | -66.6956 | 56.2564 | 56.0968 | 56.1795 | -66.8696 | -66.7382 | 0.018674 | -66.8414 | 56.0566 | 56.2893 | 56.2559 | -66.9737 | -0.15051 | -0.05767 | 2.0778 | 0.023411 | 0.17392 | -0.21732 | -0.13461 | -0.25462 | -0.25747 | -0.019172 | -0.12236 | 0.13226 | -0.024777 | -0.058204 | 122.9755 | 122.8158 | 122.8985 | 66.7434 | -123.1837 | 122.7757 | 123.0084 | 122.9749 | 66.7377 | -123.2878
71.9531 | 123.3124 | -66.7419 | 56.2912 | 0.063697 | -0.0020317 | 0.0017596 | 0.055407 | -0.0012569 | 0.054276 | 0.07176 | -0.00026221 | 0.00040853 | 0.06435 | 0.0025558 | 0.063345 | -64.6183 | 0.0243 | -66.7002 | 56.2564 | 56.0922 | 56.1703 | -66.8741 | -66.7291 | 0.018674 | -66.8414 | 56.0475 | 56.2893 | 56.2193 | -66.9691 | -0.1322 | -0.034782 | 2.1236 | 0.041721 | 0.17392 | -0.19901 | -0.12087 | -0.22715 | -0.24374 | 0.012873 | -0.09947 | 0.12768 | -0.001889 | -0.071945 | 122.9984 | 122.8341 | 122.9123 | 66.7662 | -123.1653 | 122.7894 | 123.0313 | 122.9612 | 66.7606 | -123.2603
72.9375 | 123.3215 | -66.7328 | 56.3049 | 0.078959 | -0.0009637 | 0.00069161 | 0.057544 | -0.0033929 | 0.055345 | 0.10228 | 0.0018748 | -0.00065947 | 0.065418 | 0.0014878 | 0.063345 | -64.6321 | 0.0243 | -66.6956 | 56.2702 | 56.0922 | 56.1795 | -66.8741 | -66.7336 | 0.018674 | -66.8323 | 56.052 | 56.2939 | 56.2101 | -66.9737 | -0.14136 | -0.03478 | 2.1007 | 0.037144 | 0.1785 | -0.21275 | -0.12545 | -0.24088 | -0.2529 | -0.000861 | -0.099468 | 0.14141 | -0.011043 | -0.094835 | 123.0029 | 122.825 | 122.9123 | 66.7571 | -123.1791 | 122.7848 | 123.0267 | 122.9429 | 66.7515 | -123.2786
73.9375 | 123.3124 | -66.7191 | 56.3095 | 0.048435 | -0.0031007 | -0.00037739 | 0.055407 | -0.00018888 | 0.057481 | 0.07176 | -0.0013302 | -0.00065947 | 0.065418 | 0.0025558 | 0.064413 | -64.6458 | 0.015142 | -66.7002 | 56.2564 | 56.0922 | 56.1749 | -66.865 | -66.7382 | 0.014095 | -66.8368 | 56.0658 | 56.2939 | 56.2513 | -66.9782 | -0.14593 | -0.053092 | 2.0733 | 0.018833 | 0.16477 | -0.21732 | -0.13461 | -0.25919 | -0.24374 | -0.019172 | -0.11778 | 0.14142 | -0.01562 | -0.058205 | 122.9755 | 122.8112 | 122.894 | 66.7342 | -123.1745 | 122.7848 | 123.0129 | 122.9704 | 66.7331 | -123.2878
74.9375 | 123.2712 | -66.7282 | 56.3232 | 0.063697 | -0.0009637 | -0.0014454 | 0.055407 | -0.00018888 | 0.057481 | 0.056499 | -0.0023982 | -0.00065947 | 0.06435 | 0.0014878 | 0.064413 | -64.6595 | 0.0243 | -66.6956 | 56.2656 | 56.0922 | 56.1795 | -66.865 | -66.7199 | 0.014095 | -66.8323 | 56.0658 | 56.2893 | 56.233 | -66.9691 | -0.13678 | -0.057668 | 2.0687 | 0.032566 | 0.16934 | -0.23106 | -0.14376 | -0.24088 | -0.25747 | 0.008298 | -0.10405 | 0.13684 | -0.033932 | -0.090252 | 122.9938 | 122.8204 | 122.9077 | 66.7525 | -123.1882 | 122.794 | 123.0175 | 122.9612 | 66.7423 | -123.2923
75.9375 | 123.3261 | -66.7145 | 56.2912 | 0.063697 | -0.0020317 | 0.0017596 | 0.055407 | -0.00018888 | 0.057481 | 0.041238 | -0.00026221 | 0.00040853 | 0.06435 | 0.0025558 | 0.063345 | -64.6458 | 0.019721 | -66.6956 | 56.261 | 56.0968 | 56.1749 | -66.8741 | -66.7336 | 0.018674 | -66.8323 | 56.0612 | 56.2893 | 56.2605 | -66.9782 | -0.15967 | -0.030204 | 2.0687 | 0.018834 | 0.1785 | -0.19443 | -0.1163 | -0.26377 | -0.23001 | -0.019171 | -0.11778 | 0.14599 | -0.001889 | -0.030738 | 122.9755 | 122.8112 | 122.8894 | 66.7342 | -123.1653 | 122.7757 | 123.0038 | 122.9749 | 66.7332 | -123.2694
76.9375 | 123.2986 | -66.7282 | 56.3049 | 0.063697 | -0.0020317 | -0.0014454 | 0.053271 | -0.0012569 | 0.055345 | 0.087021 | -0.0013302 | -0.00065947 | 0.063282 | 0.0025558 | 0.064413 | -64.6595 | 0.0243 | -66.6956 | 56.2564 | 56.1059 | 56.1749 | -66.8696 | -66.7291 | 0.023253 | -66.8368 | 56.0658 | 56.2893 | 56.2513 | -66.9737 | -0.14136 | -0.048515 | 2.0687 | 0.032566 | 0.17392 | -0.19901 | -0.13003 | -0.24546 | -0.23916 | -0.00086 | -0.10862 | 0.13684 | -0.015622 | -0.053628 | 122.9846 | 122.8341 | 122.9031 | 66.7525 | -123.1745 | 122.794 | 123.0175 | 122.9795 | 66.7515 | -123.2786
77.9375 | 123.2895 | -66.7191 | 56.2912 | 0.063697 | 0.0001043 | -0.0014454 | 0.055407 | -0.00018888 | 0.055345 | 0.087021 | -0.00026221 | 0.00040853 | 0.066487 | 0.0046928 | 0.065481 | -64.6595 | 0.019721 | -66.7002 | 56.261 | 56.0968 | 56.1703 | -66.8696 | -66.7199 | 0.014095 | -66.8414 | 56.0612 | 56.2893 | 56.2421 | -66.9645 | -0.15051 | -0.030204 | 2.0595 | 0.018833 | 0.16934 | -0.19443 | -0.12087 | -0.24546 | -0.23001 | -0.000857 | -0.12236 | 0.1231 | -0.001889 | -0.049052 | 122.9801 | 122.8158 | 122.8894 | 66.7388 | -123.1608 | 122.7802 | 123.0084 | 122.9612 | 66.7331 | -123.2557
78.9375 | 123.3032 | -66.7603 | 56.282 | 0.078959 | -0.0020317 | 0.00069161 | 0.057544 | -0.0012569 | 0.055345 | 0.07176 | -0.00026221 | -0.00065947 | 0.06435 | 0.0036238 | 0.063345 | -64.6504 | 0.019721 | -66.6956 | 56.261 | 56.0968 | 56.1703 | -66.865 | -66.7245 | 0.018674 | -66.8414 | 56.0658 | 56.2893 | 56.2605 | -66.9691 | -0.10473 | -0.021048 | 2.1099 | 0.06461 | 0.16934 | -0.18528 | -0.11172 | -0.20884 | -0.21627 | 0.035763 | -0.081159 | 0.12768 | 0.007267 | -0.021582 | 123.0212 | 122.857 | 122.9306 | 66.78 | -123.147 | 122.826 | 123.0496 | 123.0207 | 66.7789 | -123.2511
79.9375 | 123.2849 | -66.7648 | 56.3004 | 0.063697 | -0.0009637 | -0.00037739 | 0.055407 | -0.00018888 | 0.057481 | 0.07176 | -0.0023982 | 0.00040853 | 0.065418 | 0.0036238 | 0.063345 | -64.6321 | 0.015142 | -66.6956 | 56.261 | 56.1013 | 56.1795 | -66.8696 | -66.7291 | 0.018674 | -66.8323 | 56.0703 | 56.2893 | 56.2513 | -66.9782 | -0.10473 | -0.039359 | 2.1328 | 0.069188 | 0.17392 | -0.19901 | -0.12087 | -0.21342 | -0.23001 | 0.035762 | -0.067424 | 0.14599 | -0.011044 | -0.04905 | 123.0258 | 122.8662 | 122.9443 | 66.78 | -123.1699 | 122.8352 | 123.0541 | 123.0161 | 66.7835 | -123.2786
80.9375 | 123.2941 | -66.7511 | 56.3095 | 0.048435 | -0.0031007 | -0.00037739 | 0.056476 | -0.0012569 | 0.055345 | 0.07176 | -0.0013302 | 0.00040853 | 0.065418 | 0.0057608 | 0.063345 | -64.6229 | 0.019721 | -66.6956 | 56.2564 | 56.1105 | 56.1749 | -66.8696 | -66.7336 | 0.014095 | -66.8414 | 56.0749 | 56.2847 | 56.2376 | -66.9782 | -0.11847 | -0.053092 | 2.1282 | 0.055455 | 0.17392 | -0.19901 | -0.13461 | -0.22715 | -0.23458 | 0.01745 | -0.090314 | 0.13684 | -0.024778 | -0.071941 | 123.0075 | 122.8616 | 122.926 | 66.7708 | -123.1791 | 122.826 | 123.0358 | 122.9887 | 66.7652 | -123.2878
81.9375 | 123.2849 | -66.7648 | 56.2592 | 0.048435 | -0.0041687 | 0.00069161 | 0.054339 | -0.00018888 | 0.055345 | 0.056499 | -0.00026221 | -0.0017285 | 0.065418 | 0.0025558 | 0.064413 | -64.6366 | 0.015142 | -66.6911 | 56.2564 | 56.1105 | 56.1749 | -66.8696 | -66.7382 | 0.023253 | -66.846 | 56.0658 | 56.2893 | 56.2696 | -66.9782 | -0.10473 | -0.002738 | 2.1282 | 0.073767 | 0.1785 | -0.14865 | -0.084251 | -0.21342 | -0.19339 | 0.026605 | -0.08116 | 0.13226 | 0.030155 | 0.010463 | 123.0212 | 122.8753 | 122.9397 | 66.78 | -123.1287 | 122.8306 | 123.0541 | 123.0344 | 66.7881 | -123.2374
82.9375 | 123.262 | -66.7328 | 56.3187 | 0.063697 | -0.0020317 | -0.00037739 | 0.055407 | -0.0023249 | 0.05855 | 0.056499 | -0.0013302 | 0.00040853 | 0.065418 | 0.0046928 | 0.064413 | -64.5359 | 0.0243 | -66.6956 | 56.2656 | 56.1059 | 56.1795 | -66.8741 | -66.7291 | 0.023253 | -66.8368 | 56.0703 | 56.2847 | 56.265 | -66.9737 | -0.14136 | -0.053091 | 2.1969 | 0.037144 | 0.1785 | -0.21274 | -0.13918 | -0.24088 | -0.24832 | 0.003718 | -0.10405 | 0.13684 | -0.033934 | -0.053625 | 122.9984 | 122.8387 | 122.9123 | 66.7571 | -123.1928 | 122.8031 | 123.0175 | 122.9978 | 66.756 | -123.2923
83.9375 | 123.2666 | -66.7557 | 56.3049 | 0.063697 | -0.0031007 | -0.00037739 | 0.054339 | -0.0023249 | 0.056413 | 0.056499 | -0.0013302 | 0.00040853 | 0.06435 | 0.0046928 | 0.065481 | -64.6504 | 0.0243 | -66.6911 | 56.2702 | 56.1197 | 56.1841 | -66.8696 | -66.7382 | 0.018674 | -66.846 | 56.0703 | 56.2847 | 56.2559 | -66.9691 | -0.11389 | -0.03478 | 2.1053 | 0.064611 | 0.1785 | -0.18527 | -0.12087 | -0.21342 | -0.23459 | 0.017449 | -0.090316 | 0.1231 | -0.020201 | -0.049049 | 123.0258 | 122.8753 | 122.9397 | 66.78 | -123.1745 | 122.826 | 123.0404 | 123.0116 | 66.7743 | -123.274
84.9375 | 123.2712 | -66.7419 | 56.3049 | 0.078959 | -0.0031007 | -0.0014454 | 0.055407 | 0.00088012 | 0.056413 | 0.10228 | -0.00026221 | -0.00065947 | 0.06435 | 0.0036238 | 0.063345 | -64.6229 | 0.0243 | -66.6956 | 56.2702 | 56.1151 | 56.1657 | -66.8696 | -66.7291 | 0.014095 | -66.8506 | 56.0795 | 56.2847 | 56.2513 | -66.9737 | -0.12762 | -0.03478 | 2.119 | 0.046299 | 0.17392 | -0.18985 | -0.13919 | -0.23173 | -0.22543 | 0.012873 | -0.10863 | 0.1231 | -0.020201 | -0.053628 | 123.0121 | 122.857 | 122.9077 | 66.7662 | -123.1745 | 122.8214 | 123.0267 | 122.9932 | 66.756 | -123.2786
85.9375 | 123.1705 | -66.7419 | 56.3553 | 0.078959 | -0.0031007 | -0.00037739 | 0.056476 | -0.00018888 | 0.055345 | 0.056499 | -0.0023982 | 0.00040853 | 0.06435 | 0.0046928 | 0.064413 | -64.5542 | 0.019721 | -66.6956 | 56.2656 | 56.1105 | 56.1841 | -66.8787 | -66.7245 | 0.023253 | -66.8414 | 56.0795 | 56.2939 | 56.2696 | -66.9691 | -0.13678 | -0.089712 | 2.1877 | 0.046299 | 0.18308 | -0.24479 | -0.17122 | -0.22715 | -0.27578 | 0.017452 | -0.09947 | 0.12768 | -0.061397 | -0.085668 | 123.0075 | 122.8524 | 122.926 | 66.7617 | -123.234 | 122.8214 | 123.0358 | 123.0116 | 66.7652 | -123.3244
86.9375 | 123.262 | -66.7465 | 56.2866 | 0.048435 | -0.0041687 | -0.0014454 | 0.055407 | -0.00018888 | 0.054276 | 0.07176 | -0.0013302 | -0.00065947 | 0.062214 | 0.0046928 | 0.063345 | -64.6321 | 0.015142 | -66.6911 | 56.261 | 56.1013 | 56.1841 | -66.8741 | -66.7245 | 0.018674 | -66.8368 | 56.0749 | 56.2893 | 56.2605 | -66.9782 | -0.12762 | -0.025626 | 2.1145 | 0.055456 | 0.18308 | -0.18528 | -0.10256 | -0.23173 | -0.21169 | 0.02203 | -0.090313 | 0.14142 | 0.002689 | -0.02616 | 123.0075 | 122.8479 | 122.9306 | 66.7617 | -123.1608 | 122.8214 | 123.0358 | 123.007 | 66.7652 | -123.2649
87.9375 | 123.2895 | -66.7465 | 56.282 | 0.063697 | -0.0020317 | 0.00069161 | 0.057544 | 0.00088012 | 0.055345 | 0.087021 | -0.00026221 | 0.00040853 | 0.063282 | 0.0046928 | 0.064413 | -64.6137 | 0.019721 | -66.6911 | 56.261 | 56.1013 | 56.1795 | -66.8696 | -66.7336 | 0.018674 | -66.8414 | 56.0749 | 56.2893 | 56.2605 | -66.9828 | -0.12305 | -0.021048 | 2.1328 | 0.055456 | 0.1785 | -0.1807 | -0.10256 | -0.23631 | -0.20712 | 0.012872 | -0.094892 | 0.14141 | 0.007267 | -0.021582 | 123.0075 | 122.8479 | 122.926 | 66.7662 | -123.1516 | 122.8214 | 123.0358 | 123.007 | 66.7652 | -123.2649
88.9531 | 123.2803 | -66.7328 | 56.2912 | 0.048435 | -0.0041687 | -0.00037739 | 0.055407 | -0.00018888 | 0.055345 | 0.07176 | -0.0013302 | 0.0014765 | 0.063282 | 0.0057608 | 0.063345 | -64.6183 | 0.019721 | -66.7048 | 56.2564 | 56.1059 | 56.1795 | -66.8741 | -66.7291 | 0.018674 | -66.8414 | 56.0795 | 56.2847 | 56.2605 | -66.9737 | -0.14136 | -0.034782 | 2.1145 | 0.027988 | 0.16934 | -0.18528 | -0.11172 | -0.24088 | -0.21169 | 0.003718 | -0.10863 | 0.13226 | -0.006468 | -0.030738 | 122.9892 | 122.8387 | 122.9123 | 66.7525 | -123.1653 | 122.8123 | 123.0175 | 122.9932 | 66.7515 | -123.2649
89.9375 | 123.2941 | -66.7419 | 56.2912 | 0.048435 | -0.0031007 | -0.00037739 | 0.055407 | -0.0012569 | 0.056413 | 0.07176 | -0.00026221 | 0.00040853 | 0.06435 | 0.0057608 | 0.065481 | -64.6183 | 0.019721 | -66.6911 | 56.261 | 56.1013 | 56.1749 | -66.8787 | -66.7336 | 0.018674 | -66.8414 | 56.0841 | 56.2939 | 56.2284 | -66.9737 | -0.13678 | -0.030204 | 2.1236 | 0.050878 | 0.18766 | -0.18986 | -0.1163 | -0.23173 | -0.20712 | 0.008294 | -0.09947 | 0.13226 | 0.00269 | -0.062788 | 123.0029 | 122.8433 | 122.9168 | 66.7617 | -123.1699 | 122.826 | 123.0358 | 122.9704 | 66.7606 | -123.2649
90.9375 | 123.2529 | -66.7282 | 56.3004 | 0.063697 | -0.0041687 | -0.00037739 | 0.054339 | -0.0012569 | 0.057481 | 0.056499 | -0.00026221 | 0.00040853 | 0.065418 | 0.0057608 | 0.064413 | -64.6229 | 0.0243 | -66.7002 | 56.2702 | 56.0968 | 56.1795 | -66.8696 | -66.7245 | 0.018674 | -66.846 | 56.0795 | 56.2893 | 56.2055 | -66.9737 | -0.14136 | -0.030202 | 2.1053 | 0.027988 | 0.16934 | -0.20359 | -0.12087 | -0.24546 | -0.22085 | 0.003719 | -0.11778 | 0.12768 | -0.011044 | -0.094836 | 122.9984 | 122.825 | 122.9077 | 66.7525 | -123.1699 | 122.8077 | 123.0175 | 122.9337 | 66.7469 | -123.274
91.9375 | 123.3078 | -66.7374 | 56.2729 | 0.048435 | -0.0041687 | -0.00037739 | 0.054339 | -0.0012569 | 0.056413 | 0.056499 | 0.00080679 | -0.00065947 | 0.062214 | 0.0046928 | 0.066549 | -64.5954 | 0.0243 | -66.7048 | 56.2564 | 56.1105 | 56.1795 | -66.8741 | -66.7336 | 0.018674 | -66.8368 | 56.0749 | 56.2893 | 56.2421 | -66.9737 | -0.13678 | -0.016471 | 2.1419 | 0.032566 | 0.16934 | -0.16239 | -0.093406 | -0.2363 | -0.19796 | 0.003717 | -0.099468 | 0.13684 | 0.016422 | -0.030741 | 122.9938 | 122.8479 | 122.9168 | 66.7617 | -123.147 | 122.8123 | 123.0267 | 122.9795 | 66.756 | -123.2466
92.9531 | 123.2391 | -66.7328 | 56.3004 | 0.033173 | -0.0031007 | 0.00069161 | 0.053271 | 0.00088012 | 0.056413 | 0.056499 | -0.0013302 | 0.0014765 | 0.06435 | 0.0068288 | 0.064413 | -64.5634 | 0.028878 | -66.6956 | 56.2702 | 56.1059 | 56.1749 | -66.8787 | -66.7245 | 0.018674 | -66.8414 | 56.0703 | 56.2893 | 56.233 | -66.9782 | -0.14594 | -0.030202 | 2.1694 | 0.037144 | 0.18308 | -0.19443 | -0.12545 | -0.24546 | -0.23001 | 0.008297 | -0.10863 | 0.13684 | -0.011044 | -0.067364 | 123.0029 | 122.8387 | 122.9077 | 66.7617 | -123.1791 | 122.8031 | 123.0221 | 122.9658 | 66.7515 | -123.2786
93.9375 | 123.3398 | -66.7419 | 56.2958 | 0.063697 | -0.0031007 | -0.00037739 | 0.057544 | 0.00088012 | 0.055345 | 0.056499 | -0.0013302 | -0.0017285 | 0.06435 | 0.0057608 | 0.065481 | -64.6046 | 0.0243 | -66.6865 | 56.261 | 56.0968 | 56.1703 | -66.8787 | -66.7291 | 0.009516 | -66.8414 | 56.0658 | 56.2802 | 56.2605 | -66.9874 | -0.13678 | -0.034781 | 2.1374 | 0.055456 | 0.19224 | -0.19901 | -0.12545 | -0.24546 | -0.23001 | 0.012873 | -0.09947 | 0.14599 | -0.015623 | -0.035315 | 123.0029 | 122.8387 | 122.9123 | 66.7662 | -123.1745 | 122.8077 | 123.0221 | 123.0024 | 66.7515 | -123.2832
94.9531 | 123.2895 | -66.7648 | 56.282 | 0.048435 | -0.0041687 | -0.0014454 | 0.053271 | -0.0012569 | 0.057481 | 0.041238 | -0.0013302 | -0.0017285 | 0.065418 | 0.0068288 | 0.065481 | -64.568 | 0.015142 | -66.6911 | 56.261 | 56.1105 | 56.1841 | -66.8741 | -66.7291 | 0.018674 | -66.8414 | 56.0749 | 56.2893 | 56.2605 | -66.9691 | -0.10931 | -0.021048 | 2.1969 | 0.073767 | 0.18308 | -0.17154 | -0.097982 | -0.20426 | -0.20712 | 0.035762 | -0.076581 | 0.12768 | 0.007267 | -0.021582 | 123.0258 | 122.8753 | 122.9489 | 66.78 | -123.1562 | 122.8398 | 123.0541 | 123.0253 | 66.7835 | -123.2511
95.9375 | 123.349 | -66.7328 | 56.2683 | 0.063697 | -0.0031007 | 0.00069161 | 0.055407 | -0.0012569 | 0.057481 | 0.041238 | -0.00026221 | 0.0014765 | 0.06435 | 0.0068288 | 0.065481 | -64.5863 | 0.015142 | -66.6911 | 56.261 | 56.1013 | 56.1749 | -66.8787 | -66.7199 | 0.027831 | -66.846 | 56.0703 | 56.2939 | 56.1964 | -66.9828 | -0.14594 | -0.007316 | 2.1465 | 0.041723 | 0.18766 | -0.16697 | -0.093407 | -0.25004 | -0.19796 | 0.012876 | -0.1132 | 0.13684 | 0.025578 | -0.07195 | 122.9938 | 122.8341 | 122.9077 | 66.7479 | -123.147 | 122.8031 | 123.0267 | 122.9291 | 66.7606 | -123.2511
96.9375 | 123.2849 | -66.7328 | 56.282 | 0.033173 | -0.0052367 | 0.00069161 | 0.055407 | 0.00088012 | 0.055345 | 0.025977 | -0.00026221 | 0.00040853 | 0.065418 | 0.0068288 | 0.062276 | -64.6046 | 0.019721 | -66.6911 | 56.261 | 56.1059 | 56.1749 | -66.8741 | -66.7245 | 0.023253 | -66.8414 | 56.0703 | 56.2893 | 56.2513 | -66.9782 | -0.14136 | -0.021048 | 2.1282 | 0.041723 | 0.18308 | -0.17612 | -0.10714 | -0.24546 | -0.2117 | 0.008297 | -0.10863 | 0.13684 | 0.007267 | -0.030739 | 122.9938 | 122.8387 | 122.9077 | 66.7525 | -123.1562 | 122.8031 | 123.0221 | 122.9841 | 66.756 | -123.2603
97.9375 | 123.349 | -66.7511 | 56.282 | 0.033173 | -0.0041687 | -0.0014454 | 0.055407 | -0.0012569 | 0.054276 | 0.056499 | -0.0034662 | -0.00065947 | 0.06435 | 0.0068288 | 0.064413 | -64.6046 | 0.019721 | -66.6911 | 56.2564 | 56.1059 | 56.1749 | -66.8741 | -66.7336 | 0.014095 | -66.8368 | 56.0749 | 56.2985 | 56.2284 | -66.9782 | -0.12305 | -0.025626 | 2.1465 | 0.060034 | 0.18308 | -0.17612 | -0.10714 | -0.22715 | -0.20712 | 0.01745 | -0.085735 | 0.14142 | 0.016424 | -0.053632 | 123.0075 | 122.857 | 122.926 | 66.7708 | -123.1562 | 122.826 | 123.0496 | 122.9795 | 66.7652 | -123.2603
98.9375 | 123.317 | -66.7236 | 56.2729 | 0.048435 | -0.0041687 | -0.00037739 | 0.055407 | -0.0012569 | 0.056413 | 0.056499 | -0.00026221 | -0.0017285 | 0.062214 | 0.0068288 | 0.065481 | -64.5863 | 0.033457 | -66.6956 | 56.2564 | 56.1059 | 56.1795 | -66.8787 | -66.7291 | 0.018674 | -66.8414 | 56.0749 | 56.2985 | 56.2513 | -66.9691 | -0.15509 | -0.016471 | 2.1374 | 0.027989 | 0.18308 | -0.16697 | -0.093406 | -0.24546 | -0.19796 | -0.005437 | -0.11778 | 0.12768 | 0.025579 | -0.021584 | 122.9801 | 122.8296 | 122.9031 | 66.7571 | -123.1516 | 122.7986 | 123.0221 | 122.9749 | 66.7423 | -123.242
99.9531 | 123.2666 | -66.7648 | 56.3004 | 0.063697 | -0.0041687 | 0.0017596 | 0.055407 | -0.0012569 | 0.055345 | 0.07176 | -0.0013302 | -0.00065947 | 0.065418 | 0.0078978 | 0.064413 | -64.5634 | 0.028878 | -66.6956 | 56.2702 | 56.1059 | 56.1841 | -66.8696 | -66.7291 | 0.009516 | -66.8368 | 56.0749 | 56.2985 | 56.2467 | -66.9737 | -0.10473 | -0.030202 | 2.2015 | 0.069188 | 0.17392 | -0.19443 | -0.11629 | -0.20884 | -0.22543 | 0.035762 | -0.072002 | 0.13684 | -0.001887 | -0.053629 | 123.035 | 122.8708 | 122.9489 | 66.7937 | -123.1699 | 122.8398 | 123.0633 | 123.0116 | 66.7743 | -123.274
100.9375 | 123.2986 | -66.7419 | 56.2637 | 0.033173 | -0.0031007 | -0.0014454 | 0.055407 | -0.00018888 | 0.057481 | 0.07176 | 0.00080679 | 0.00040853 | 0.065418 | 0.0068288 | 0.063345 | -64.5954 | 0.019721 | -66.6956 | 56.2564 | 56.1059 | 56.1795 | -66.8741 | -66.7199 | 0.018674 | -66.8368 | 56.0703 | 56.2893 | 56.2559 | -66.9737 | -0.1322 | -0.007316 | 2.1465 | 0.046299 | 0.1785 | -0.15781 | -0.084251 | -0.23173 | -0.19339 | 0.022031 | -0.094891 | 0.13684 | 0.025577 | -0.00785 | 122.9984 | 122.8479 | 122.9214 | 66.7617 | -123.1379 | 122.8123 | 123.0313 | 122.9978 | 66.7606 | -123.2374
101.9375 | 123.3078 | -66.7236 | 56.2775 | 0.078959 | -0.0041687 | 0.00069161 | 0.055407 | -0.00018888 | 0.055345 | 0.087021 | -0.0013302 | 0.00040853 | 0.062214 | 0.0068288 | 0.064413 | -64.5908 | 0.0243 | -66.6956 | 56.2564 | 56.1013 | 56.1749 | -66.8787 | -66.7291 | 0.018674 | -66.8414 | 56.0703 | 56.2939 | 56.2605 | -66.9737 | -0.15509 | -0.021049 | 2.1328 | 0.027989 | 0.18308 | -0.17612 | -0.10256 | -0.25004 | -0.20712 | -0.005437 | -0.11778 | 0.13226 | 0.016423 | -0.017005 | 122.9801 | 122.825 | 122.8985 | 66.7479 | -123.1562 | 122.794 | 123.0175 | 122.9841 | 66.7423 | -123.2511
102.9531 | 123.3856 | -66.7236 | 56.2729 | 0.048435 | -0.0063057 | 0.00069161 | 0.055407 | -0.00018888 | 0.056413 | 0.056499 | -0.0023982 | -0.0027965 | 0.06435 | 0.0057608 | 0.063345 | -64.6 | 0.0243 | -66.6956 | 56.261 | 56.1013 | 56.1703 | -66.8696 | -66.7382 | 0.023253 | -66.8414 | 56.0795 | 56.2893 | 56.2513 | -66.9828 | -0.14593 | -0.011893 | 2.1236 | 0.027989 | 0.17392 | -0.17155 | -0.10256 | -0.25919 | -0.19338 | -0.014594 | -0.11778 | 0.14141 | 0.016422 | -0.021584 | 122.9846 | 122.825 | 122.894 | 66.7479 | -123.1425 | 122.8031 | 123.0129 | 122.9749 | 66.7469 | -123.2557
103.9375 | 123.3215 | -66.7465 | 56.2775 | 0.063697 | -0.0020317 | -0.00037739 | 0.054339 | -0.0012569 | 0.056413 | 0.07176 | -0.00026221 | -0.0017285 | 0.06435 | 0.0068288 | 0.065481 | -64.5817 | 0.019721 | -66.6911 | 56.261 | 56.1059 | 56.1795 | -66.8787 | -66.7245 | 0.018674 | -66.8414 | 56.0795 | 56.2985 | 56.2421 | -66.9782 | -0.1322 | -0.016471 | 2.1648 | 0.055456 | 0.18766 | -0.17154 | -0.097984 | -0.23173 | -0.19796 | 0.02203 | -0.094892 | 0.13684 | 0.021001 | -0.035319 | 123.0075 | 122.8524 | 122.926 | 66.7662 | -123.1562 | 122.826 | 123.045 | 122.9887 | 66.7652 | -123.2557
104.9375 | 123.3261 | -66.7419 | 56.2592 | 0.048435 | -0.0052367 | 0.00069161 | 0.055407 | 0.00088012 | 0.056413 | 0.056499 | -0.0034662 | -0.0017285 | 0.065418 | 0.0068288 | 0.063345 | -64.5725 | 0.0243 | -66.6865 | 56.2564 | 56.0922 | 56.1841 | -66.8741 | -66.7245 | 0.023253 | -66.8368 | 56.0658 | 56.2893 | 56.2421 | -66.9737 | -0.1322 | -0.002738 | 2.1694 | 0.055456 | 0.18766 | -0.16697 | -0.075094 | -0.23173 | -0.19339 | 0.017452 | -0.094891 | 0.13684 | 0.030155 | -0.017008 | 122.9984 | 122.8341 | 122.926 | 66.7662 | -123.1333 | 122.8077 | 123.0313 | 122.9841 | 66.7652 | -123.2328
105.9375 | 123.1934 | -66.7557 | 56.3416 | 0.063697 | -0.0041687 | 0.00069161 | 0.055407 | -0.0012569 | 0.056413 | 0.056499 | 0.00080679 | -0.00065947 | 0.06435 | 0.0068288 | 0.062276 | -64.5359 | 0.0243 | -66.6911 | 56.2564 | 56.1059 | 56.1841 | -66.8696 | -66.7336 | 0.018674 | -66.8368 | 56.0612 | 56.2985 | 56.233 | -66.9691 | -0.11389 | -0.085136 | 2.2198 | 0.064611 | 0.1785 | -0.23563 | -0.15749 | -0.21342 | -0.28036 | 0.022027 | -0.081158 | 0.13226 | -0.043086 | -0.10856 | 123.0121 | 122.8616 | 122.9397 | 66.78 | -123.2111 | 122.8169 | 123.0541 | 122.9887 | 66.7743 | -123.3106
106.9375 | 123.317 | -66.7511 | 56.2912 | 0.063697 | -0.0041687 | -0.00037739 | 0.055407 | -0.0023249 | 0.055345 | 0.041238 | -0.00026221 | -0.0017285 | 0.06435 | 0.0078978 | 0.065481 | -64.568 | 0.019721 | -66.7002 | 56.2564 | 56.1059 | 56.1841 | -66.8741 | -66.7291 | 0.018674 | -66.8368 | 56.0566 | 56.2847 | 56.2238 | -66.9782 | -0.12305 | -0.034782 | 2.1831 | 0.050877 | 0.17392 | -0.18528 | -0.10714 | -0.22715 | -0.23459 | 0.022029 | -0.085735 | 0.14142 | -0.006468 | -0.067367 | 123.0075 | 122.857 | 122.9352 | 66.7708 | -123.1653 | 122.8077 | 123.0358 | 122.9749 | 66.7698 | -123.2694
107.9375 | 123.3032 | -66.7236 | 56.2912 | 0.063697 | -0.0031007 | -0.00037739 | 0.055407 | -0.0012569 | 0.055345 | 0.041238 | -0.0013302 | -0.0017285 | 0.062214 | 0.0078978 | 0.063345 | -64.6137 | 0.019721 | -66.6956 | 56.2564 | 56.1013 | 56.1795 | -66.8696 | -66.7336 | 0.018674 | -66.8414 | 56.0612 | 56.2893 | 56.2284 | -66.9782 | -0.14593 | -0.034782 | 2.1099 | 0.027989 | 0.17392 | -0.18986 | -0.11172 | -0.25462 | -0.23001 | -0.010016 | -0.11778 | 0.13684 | -0.001889 | -0.062788 | 122.9801 | 122.825 | 122.9031 | 66.7434 | -123.1608 | 122.7848 | 123.0129 | 122.952 | 66.7423 | -123.2694
108.9531 | 123.1842 | -66.7831 | 56.3416 | 0.048435 | -0.0052367 | 0.00069161 | 0.056476 | -0.0012569 | 0.056413 | 0.07176 | -0.0023982 | -0.00065947 | 0.065418 | 0.0078978 | 0.063345 | -64.5268 | 0.0243 | -66.6911 | 56.2656 | 56.1013 | 56.1886 | -66.8696 | -66.7336 | 0.018674 | -66.8414 | 56.0612 | 56.2939 | 56.2467 | -66.9828 | -0.086424 | -0.075979 | 2.2564 | 0.092077 | 0.1785 | -0.24021 | -0.15291 | -0.19969 | -0.28036 | 0.049493 | -0.058271 | 0.14141 | -0.047664 | -0.094828 | 123.0487 | 122.8845 | 122.9718 | 66.8074 | -123.2111 | 122.8443 | 123.077 | 123.0299 | 66.8018 | -123.3244
109.9375 | 123.3078 | -66.7374 | 56.2592 | 0.063697 | -0.0052367 | 0.00069161 | 0.056476 | -0.00018888 | 0.055345 | 0.087021 | -0.00026221 | 0.00040853 | 0.065418 | 0.0078978 | 0.063345 | -64.5771 | 0.019721 | -66.6956 | 56.261 | 56.1013 | 56.1795 | -66.8741 | -66.7291 | 0.018674 | -66.8323 | 56.0703 | 56.2939 | 56.2284 | -66.9737 | -0.13678 | 0.00184 | 2.1603 | 0.041722 | 0.1785 | -0.15781 | -0.079673 | -0.2363 | -0.18881 | 0.008296 | -0.09489 | 0.14141 | 0.034734 | -0.030744 | 122.9984 | 122.8387 | 122.9168 | 66.7571 | -123.1333 | 122.8077 | 123.0313 | 122.9658 | 66.756 | -123.2328
110.9375 | 123.317 | -66.7282 | 56.2729 | 0.063697 | -0.0052367 | -0.00037739 | 0.056476 | -0.00018888 | 0.055345 | 0.07176 | -0.0023982 | -0.0017285 | 0.061145 | 0.0068288 | 0.063345 | -64.568 | 0.019721 | -66.7002 | 56.2656 | 56.0968 | 56.1749 | -66.8787 | -66.7291 | 0.023253 | -66.8323 | 56.0612 | 56.2985 | 56.2376 | -66.9691 | -0.15051 | -0.007314 | 2.1603 | 0.027988 | 0.1785 | -0.17612 | -0.097984 | -0.24088 | -0.2117 | -0.00086 | -0.10405 | 0.13684 | 0.025579 | -0.03532 | 122.9938 | 122.825 | 122.9031 | 66.7479 | -123.1516 | 122.7894 | 123.0267 | 122.9658 | 66.7515 | -123.242
111.9375 | 123.3078 | -66.7191 | 56.282 | 0.048435 | -0.0063057 | 0.00069161 | 0.055407 | -0.00018888 | 0.055345 | 0.041238 | -0.0023982 | -0.0017285 | 0.061145 | 0.0089658 | 0.064413 | -64.5588 | 0.019721 | -66.6956 | 56.261 | 56.1059 | 56.1886 | -66.8741 | -66.7336 | 0.014095 | -66.8368 | 56.0612 | 56.2893 | 56.2559 | -66.9782 | -0.15509 | -0.021048 | 2.1603 | 0.023411 | 0.1785 | -0.17612 | -0.093404 | -0.25919 | -0.22085 | -0.014594 | -0.11778 | 0.14142 | 0.007267 | -0.02616 | 122.9801 | 122.825 | 122.9077 | 66.7388 | -123.1562 | 122.7802 | 123.0084 | 122.9749 | 66.7331 | -123.2603
112.9375 | 123.3032 | -66.7053 | 56.3095 | 0.078959 | -0.0073737 | 0.00069161 | 0.056476 | -0.0012569 | 0.056413 | 0.07176 | -0.0013302 | -0.0017285 | 0.063282 | 0.0078978 | 0.062276 | -64.5588 | 0.0243 | -66.6956 | 56.2564 | 56.0922 | 56.1886 | -66.8741 | -66.7291 | 0.009516 | -66.8414 | 56.0703 | 56.2985 | 56.2055 | -66.9737 | -0.16882 | -0.053092 | 2.1465 | 0.009678 | 0.1785 | -0.21732 | -0.12087 | -0.26835 | -0.23916 | -0.023748 | -0.13609 | 0.13226 | -0.011042 | -0.10399 | 122.9617 | 122.7975 | 122.894 | 66.7296 | -123.1837 | 122.7757 | 123.0038 | 122.9108 | 66.7148 | -123.2832
113.9375 | 123.2803 | -66.7465 | 56.282 | 0.048435 | -0.0063057 | 0.00069161 | 0.054339 | -0.00018888 | 0.056413 | 0.056499 | -0.00026221 | -0.00065947 | 0.06435 | 0.0089658 | 0.063345 | -64.5496 | 0.019721 | -66.6956 | 56.261 | 56.0968 | 56.1841 | -66.8741 | -66.7199 | 0.018674 | -66.8368 | 56.0566 | 56.2893 | 56.2513 | -66.9782 | -0.12762 | -0.021048 | 2.1969 | 0.050877 | 0.1785 | -0.18528 | -0.097982 | -0.23173 | -0.22543 | 0.026609 | -0.090313 | 0.14142 | 0.007267 | -0.030739 | 123.0075 | 122.8433 | 122.9306 | 66.7662 | -123.1562 | 122.8031 | 123.0358 | 122.9978 | 66.7652 | -123.2603
114.9375 | 123.2574 | -66.7191 | 56.3507 | 0.063697 | -0.0063057 | -0.00037739 | 0.056476 | -0.00018888 | 0.055345 | 0.10228 | -0.00026221 | 0.00040853 | 0.063282 | 0.0078978 | 0.062276 | -64.5405 | 0.019721 | -66.7048 | 56.2564 | 56.1013 | 56.1795 | -66.865 | -66.7245 | 0.009516 | -66.846 | 56.0658 | 56.2939 | 56.233 | -66.9737 | -0.14593 | -0.094291 | 2.1786 | 0.014255 | 0.16019 | -0.24937 | -0.17123 | -0.25462 | -0.28494 | -0.005436 | -0.12694 | 0.12768 | -0.056819 | -0.11772 | 122.9755 | 122.8204 | 122.8985 | 66.7388 | -123.2157 | 122.7848 | 123.0129 | 122.952 | 66.7286 | -123.3244
115.9375 | 123.2849 | -66.7419 | 56.3049 | 0.048435 | -0.0052367 | -0.00037739 | 0.054339 | -0.0012569 | 0.056413 | 0.041238 | -0.0023982 | -0.0017285 | 0.063282 | 0.011103 | 0.064413 | -64.5588 | 0.0243 | -66.7002 | 56.261 | 56.1013 | 56.1886 | -66.8741 | -66.7382 | 0.014095 | -66.8414 | 56.0612 | 56.2939 | 56.2513 | -66.992 | -0.1322 | -0.043937 | 2.1831 | 0.041721 | 0.17392 | -0.20359 | -0.11629 | -0.25004 | -0.24374 | 0.003716 | -0.09947 | 0.15057 | -0.011043 | -0.053628 | 123.0029 | 122.8433 | 122.9306 | 66.7662 | -123.1791 | 122.8031 | 123.0358 | 122.9932 | 66.756 | -123.2969
116.9531 | 123.2117 | -66.7374 | 56.3095 | 0.033173 | -0.0063057 | -0.00037739 | 0.057544 | -0.0023249 | 0.053208 | 0.041238 | 0.00080679 | -0.00065947 | 0.061145 | 0.0078978 | 0.065481 | -64.5084 | 0.019721 | -66.6956 | 56.2656 | 56.1105 | 56.1886 | -66.8741 | -66.7382 | 0.023253 | -66.8368 | 56.0703 | 56.2893 | 56.2284 | -66.9782 | -0.13678 | -0.043935 | 2.2289 | 0.041722 | 0.1785 | -0.19901 | -0.12087 | -0.24088 | -0.23916 | -0.000861 | -0.099468 | 0.14142 | -0.020199 | -0.081098 | 123.0029 | 122.8479 | 122.926 | 66.7571 | -123.1837 | 122.8077 | 123.0267 | 122.9658 | 66.7606 | -123.2878
117.9375 | 123.2986 | -66.7694 | 56.2958 | 0.048435 | -0.0052367 | -0.0025134 | 0.055407 | -0.0033929 | 0.055345 | 0.041238 | -0.00026221 | -0.0017285 | 0.06435 | 0.0078978 | 0.064413 | -64.6137 | 0.019721 | -66.7002 | 56.2564 | 56.0922 | 56.1886 | -66.8696 | -66.7291 | 0.014095 | -66.8368 | 56.0566 | 56.2802 | 56.2238 | -66.9782 | -0.10016 | -0.039359 | 2.1557 | 0.069187 | 0.16934 | -0.20359 | -0.10714 | -0.20884 | -0.23916 | 0.040339 | -0.067425 | 0.14142 | -0.015623 | -0.071944 | 123.0258 | 122.8616 | 122.958 | 66.7891 | -123.1653 | 122.826 | 123.0496 | 122.9932 | 66.7835 | -123.274
118.9531 | 123.2025 | -66.7465 | 56.3187 | 0.048435 | -0.0063057 | 0.00069161 | 0.056476 | -0.0012569 | 0.053208 | 0.041238 | -0.0023982 | -0.00065947 | 0.065418 | 0.010034 | 0.063345 | -64.513 | 0.0243 | -66.7002 | 56.2656 | 56.1105 | 56.1932 | -66.8833 | -66.7245 | 0.018674 | -66.8368 | 56.0612 | 56.2893 | 56.2467 | -66.9828 | -0.13678 | -0.053091 | 2.2335 | 0.046299 | 0.18308 | -0.20817 | -0.12545 | -0.23631 | -0.25747 | 0.02203 | -0.090313 | 0.14599 | -0.029355 | -0.07194 | 123.0121 | 122.857 | 122.9397 | 66.7708 | -123.202 | 122.8077 | 123.0358 | 122.9932 | 66.7652 | -123.3015
119.9375 | 123.1842 | -66.7923 | 56.2958 | 0.048435 | -0.0052367 | -0.0014454 | 0.055407 | -0.0012569 | 0.055345 | 0.07176 | -0.0013302 | -0.0017285 | 0.06435 | 0.0089658 | 0.062276 | -64.5405 | 0.0243 | -66.7002 | 56.261 | 56.1013 | 56.1886 | -66.8741 | -66.7245 | 0.023253 | -66.8414 | 56.0612 | 56.2893 | 56.2467 | -66.9782 | -0.081848 | -0.034781 | 2.2518 | 0.092075 | 0.17392 | -0.19443 | -0.10714 | -0.18595 | -0.23459 | 0.067806 | -0.049116 | 0.13684 | -0.006466 | -0.049051 | 123.0533 | 122.8936 | 122.9809 | 66.8166 | -123.1699 | 122.8535 | 123.0816 | 123.039 | 66.8156 | -123.274
120.9531 | 123.2758 | -66.7557 | 56.2775 | 0.063697 | -0.0084417 | -0.0014454 | 0.056476 | -0.0023249 | 0.053208 | 0.056499 | -0.0013302 | -0.00065947 | 0.063282 | 0.0089658 | 0.063345 | -64.5863 | 0.0243 | -66.7002 | 56.2656 | 56.1105 | 56.1841 | -66.8741 | -66.7336 | 0.014095 | -66.8368 | 56.0658 | 56.2893 | 56.2376 | -66.9782 | -0.11847 | -0.011892 | 2.1694 | 0.055454 | 0.17392 | -0.16697 | -0.093405 | -0.22257 | -0.2117 | 0.022027 | -0.081158 | 0.14142 | 0.011844 | -0.039898 | 123.0212 | 122.8662 | 122.9397 | 66.78 | -123.1516 | 122.8214 | 123.045 | 122.9932 | 66.7698 | -123.2557
121.9375 | 123.2574 | -66.7557 | 56.3049 | 0.048435 | -0.0063057 | -0.00037739 | 0.057544 | -0.0023249 | 0.057481 | 0.041238 | 0.00080679 | -0.0027965 | 0.06435 | 0.0089658 | 0.064413 | -64.5359 | 0.0243 | -66.6956 | 56.2518 | 56.0968 | 56.1749 | -66.8741 | -66.7291 | 0.018674 | -66.8368 | 56.0658 | 56.2985 | 56.2238 | -66.9828 | -0.11847 | -0.053093 | 2.2198 | 0.060032 | 0.1785 | -0.20817 | -0.13003 | -0.22715 | -0.23916 | 0.026606 | -0.081158 | 0.14599 | -0.006465 | -0.0811 | 123.0075 | 122.8524 | 122.9306 | 66.78 | -123.1791 | 122.8214 | 123.0541 | 122.9795 | 66.7743 | -123.2878
122.9375 | 123.2803 | -66.7236 | 56.3004 | 0.048435 | -0.0041687 | -0.0014454 | 0.055407 | -0.0023249 | 0.055345 | 0.07176 | -0.0013302 | -0.00065947 | 0.065418 | 0.0078978 | 0.064413 | -64.5542 | 0.015142 | -66.7048 | 56.2518 | 56.0922 | 56.1886 | -66.8741 | -66.7291 | 0.018674 | -66.8368 | 56.0612 | 56.2939 | 56.233 | -66.9828 | -0.15051 | -0.048515 | 2.1694 | 0.018833 | 0.16934 | -0.20817 | -0.11171 | -0.25919 | -0.23916 | -0.005437 | -0.1132 | 0.14599 | -0.006465 | -0.067364 | 122.9755 | 122.8158 | 122.9123 | 66.7388 | -123.1745 | 122.7848 | 123.0175 | 122.9566 | 66.7423 | -123.2832
123.9375 | 123.317 | -66.7282 | 56.2546 | 0.033173 | -0.0063057 | 0.00069161 | 0.055407 | -0.0012569 | 0.057481 | 0.041238 | -0.0013302 | 0.00040853 | 0.063282 | 0.011103 | 0.061208 | -64.5496 | 0.0243 | -66.7002 | 56.2656 | 56.1013 | 56.1886 | -66.8696 | -66.7291 | 0.018674 | -66.8277 | 56.0612 | 56.2939 | 56.2376 | -66.9737 | -0.14136 | 0.010996 | 2.1786 | 0.027988 | 0.16934 | -0.15324 | -0.065939 | -0.24546 | -0.19339 | -0.00086 | -0.099467 | 0.14599 | 0.039311 | -0.01701 | 122.9938 | 122.8296 | 122.9168 | 66.7525 | -123.1241 | 122.7894 | 123.0221 | 122.9658 | 66.7469 | -123.2282
124.9375 | 123.3032 | -66.7831 | 56.2637 | 0.017911 | -0.0063057 | -0.0014454 | 0.055407 | -0.0012569 | 0.056413 | 0.041238 | -0.0013302 | -0.0017285 | 0.063282 | 0.0078978 | 0.062276 | -64.5542 | 0.0243 | -66.6956 | 56.2702 | 56.0968 | 56.1886 | -66.8787 | -66.7336 | 0.018674 | -66.8414 | 56.0658 | 56.2847 | 56.2238 | -66.9782 | -0.095582 | 0.006419 | 2.2289 | 0.087498 | 0.18308 | -0.16697 | -0.075094 | -0.19511 | -0.19796 | 0.049493 | -0.058271 | 0.13684 | 0.020998 | -0.039901 | 123.0533 | 122.8799 | 122.9718 | 66.8074 | -123.1425 | 122.8489 | 123.0679 | 123.007 | 66.8018 | -123.242
125.9375 | 123.2162 | -66.774 | 56.3141 | 0.048435 | -0.0052367 | -0.00037739 | 0.056476 | -0.0012569 | 0.055345 | 0.056499 | -0.0013302 | -0.00065947 | 0.062214 | 0.010034 | 0.062276 | -64.5405 | 0.019721 | -66.7002 | 56.2656 | 56.1059 | 56.1841 | -66.8787 | -66.7291 | 0.014095 | -66.8414 | 56.0658 | 56.2893 | 56.2421 | -66.9828 | -0.10474 | -0.048513 | 2.2335 | 0.073765 | 0.1785 | -0.20817 | -0.13003 | -0.20884 | -0.24832 | 0.044917 | -0.067426 | 0.14141 | -0.024777 | -0.07194 | 123.0396 | 122.8799 | 122.958 | 66.7937 | -123.1928 | 122.8398 | 123.0633 | 123.0161 | 66.7881 | -123.2969
126.9375 | 123.1842 | -66.806 | 56.3095 | 0.078959 | -0.0073737 | -0.00037739 | 0.055407 | -0.0023249 | 0.055345 | 0.056499 | -0.0013302 | -0.00065947 | 0.063282 | 0.0089658 | 0.063345 | -64.5313 | 0.019721 | -66.7002 | 56.261 | 56.1059 | 56.1886 | -66.8741 | -66.7336 | 0.009516 | -66.8323 | 56.0749 | 56.3076 | 56.2193 | -66.9874 | -0.068115 | -0.048514 | 2.2747 | 0.10581 | 0.17392 | -0.20359 | -0.12087 | -0.18138 | -0.23458 | 0.072381 | -0.026226 | 0.15515 | -0.001885 | -0.090255 | 123.067 | 122.912 | 122.9947 | 66.8258 | -123.1837 | 122.881 | 123.1137 | 123.0253 | 66.8155 | -123.2969
127.9375 | 123.3032 | -66.7419 | 56.3049 | 0.063697 | -0.0052367 | -0.0014454 | 0.054339 | -0.0033929 | 0.055345 | 0.056499 | -0.0023982 | -0.0017285 | 0.063282 | 0.010034 | 0.064413 | -64.6046 | 0.019721 | -66.6956 | 56.2564 | 56.1013 | 56.1886 | -66.8741 | -66.7291 | 0.014095 | -66.8414 | 56.0658 | 56.303 | 56.2559 | -66.9782 | -0.1322 | -0.048515 | 2.1374 | 0.046299 | 0.1785 | -0.20359 | -0.11629 | -0.23631 | -0.23916 | 0.012873 | -0.09947 | 0.13684 | -0.001886 | -0.049049 | 122.9984 | 122.8433 | 122.9306 | 66.7617 | -123.1791 | 122.8077 | 123.045 | 122.9978 | 66.756 | -123.2832
128.9375 | 123.2391 | -66.7831 | 56.3004 | 0.048435 | -0.0084417 | -0.00037739 | 0.055407 | -0.0012569 | 0.055345 | 0.056499 | -0.0013302 | -0.0027965 | 0.063282 | 0.010034 | 0.064413 | -64.5359 | 0.028878 | -66.6956 | 56.2564 | 56.1105 | 56.1841 | -66.8787 | -66.7291 | 0.014095 | -66.8323 | 56.0703 | 56.2939 | 56.233 | -66.9828 | -0.095582 | -0.043937 | 2.2472 | 0.087498 | 0.18308 | -0.18985 | -0.11629 | -0.19969 | -0.23001 | 0.054072 | -0.049114 | 0.15057 | -0.006465 | -0.067364 | 123.0396 | 122.8936 | 122.9672 | 66.812 | -123.1791 | 122.8535 | 123.077 | 123.0161 | 66.7972 | -123.2832
129.9375 | 123.2117 | -66.774 | 56.2958 | 0.048435 | -0.0084417 | -0.0014454 | 0.055407 | -0.0023249 | 0.054276 | 0.025977 | -0.0023982 | -0.0017285 | 0.061145 | 0.0078978 | 0.06014 | -64.5313 | 0.0243 | -66.7002 | 56.2656 | 56.1059 | 56.1841 | -66.8741 | -66.7245 | 0.018674 | -66.8414 | 56.0658 | 56.2985 | 56.1735 | -66.9828 | -0.10016 | -0.030202 | 2.2427 | 0.073765 | 0.17392 | -0.18985 | -0.11171 | -0.20884 | -0.23001 | 0.049496 | -0.067426 | 0.14141 | 0.002691 | -0.12231 | 123.0396 | 122.8799 | 122.958 | 66.7983 | -123.1699 | 122.8398 | 123.0725 | 122.9475 | 66.7927 | -123.2786
130.9375 | 123.3124 | -66.7831 | 56.2683 | 0.063697 | -0.0095107 | 0.00069161 | 0.055407 | -0.0012569 | 0.056413 | 0.07176 | -0.0013302 | -0.0017285 | 0.063282 | 0.010034 | 0.062276 | -64.5542 | 0.0243 | -66.7002 | 56.261 | 56.1013 | 56.1886 | -66.8787 | -66.7291 | 0.014095 | -66.8323 | 56.0612 | 56.2847 | 56.2467 | -66.9737 | -0.095582 | -0.007316 | 2.2289 | 0.08292 | 0.1785 | -0.16697 | -0.079672 | -0.19053 | -0.20712 | 0.054072 | -0.049114 | 0.14141 | 0.01642 | -0.021586 | 123.0441 | 122.8845 | 122.9718 | 66.8074 | -123.147 | 122.8443 | 123.0679 | 123.0299 | 66.7972 | -123.242
131.9531 | 123.2941 | -66.7694 | 56.2729 | 0.048435 | -0.0095107 | 0.0017596 | 0.055407 | -0.0023249 | 0.055345 | 0.056499 | -0.0013302 | -0.0017285 | 0.063282 | 0.010034 | 0.062276 | -64.5725 | 0.019721 | -66.7048 | 56.2656 | 56.1059 | 56.1932 | -66.8741 | -66.7336 | 0.009516 | -66.8368 | 56.0658 | 56.2939 | 56.233 | -66.9828 | -0.10474 | -0.007314 | 2.1969 | 0.064609 | 0.16934 | -0.16697 | -0.07967 | -0.21342 | -0.20712 | 0.03576 | -0.067425 | 0.14599 | 0.021001 | -0.039898 | 123.035 | 122.8753 | 122.9626 | 66.7891 | -123.147 | 122.8352 | 123.0633 | 123.0024 | 66.7789 | -123.2557
132.9375 | 123.2117 | -66.7877 | 56.3278 | 0.063697 | -0.0084417 | -0.0014454 | 0.056476 | -0.0012569 | 0.054276 | 0.07176 | -0.0013302 | -0.0017285 | 0.062214 | 0.011103 | 0.062276 | -64.5359 | 0.0243 | -66.7048 | 56.2702 | 56.1059 | 56.1886 | -66.8696 | -66.7245 | 0.018674 | -66.8368 | 56.0703 | 56.2939 | 56.2605 | -66.9874 | -0.081846 | -0.057668 | 2.2518 | 0.08292 | 0.16477 | -0.2219 | -0.13918 | -0.19969 | -0.25747 | 0.063229 | -0.049114 | 0.15057 | -0.033931 | -0.067359 | 123.0579 | 122.8936 | 122.9764 | 66.812 | -123.1974 | 122.8581 | 123.0816 | 123.0482 | 66.8064 | -123.3152
133.9375 | 123.1705 | -66.7969 | 56.3232 | 0.048435 | -0.0095107 | -0.00037739 | 0.057544 | -0.0012569 | 0.054276 | 0.07176 | -0.0013302 | -0.00065947 | 0.063282 | 0.012171 | 0.061208 | -64.5222 | 0.019721 | -66.7002 | 56.261 | 56.0968 | 56.2024 | -66.8787 | -66.7291 | 0.014095 | -66.8368 | 56.0612 | 56.2939 | 56.2513 | -66.9782 | -0.081849 | -0.062247 | 2.2747 | 0.096653 | 0.1785 | -0.22648 | -0.12087 | -0.18137 | -0.26205 | 0.067805 | -0.039959 | 0.14142 | -0.029353 | -0.071938 | 123.0579 | 122.8936 | 122.9993 | 66.8166 | -123.202 | 122.8581 | 123.0908 | 123.0482 | 66.811 | -123.3015
134.9531 | 123.2758 | -66.7328 | 56.2866 | 0.063697 | -0.0073737 | -0.00037739 | 0.056476 | -0.0012569 | 0.055345 | 0.041238 | -0.0013302 | -0.0017285 | 0.06435 | 0.011103 | 0.062276 | -64.5954 | 0.015142 | -66.6956 | 56.261 | 56.1013 | 56.1932 | -66.8696 | -66.7291 | 0.018674 | -66.8368 | 56.0612 | 56.2893 | 56.2376 | -66.9782 | -0.13678 | -0.025626 | 2.1374 | 0.037144 | 0.17392 | -0.18528 | -0.093403 | -0.24546 | -0.22543 | 0.003718 | -0.10405 | 0.14142 | 0.002689 | -0.049053 | 122.9938 | 122.8341 | 122.926 | 66.7479 | -123.1562 | 122.794 | 123.0221 | 122.9704 | 66.7515 | -123.2649
135.9375 | 123.23 | -66.7786 | 56.3324 | 0.063697 | -0.0095107 | 0.00069161 | 0.058613 | -0.0012569 | 0.054276 | 0.056499 | -0.0013302 | -0.00065947 | 0.062214 | 0.0089658 | 0.064413 | -64.5176 | 0.015142 | -66.7002 | 56.2702 | 56.1013 | 56.1978 | -66.8787 | -66.7336 | 0.018674 | -66.8414 | 56.0566 | 56.2893 | 56.2421 | -66.9782 | -0.10016 | -0.062245 | 2.261 | 0.078342 | 0.1785 | -0.23105 | -0.1346 | -0.19969 | -0.27578 | 0.044915 | -0.062849 | 0.13684 | -0.043087 | -0.09025 | 123.0487 | 122.8799 | 122.9764 | 66.7937 | -123.2111 | 122.8352 | 123.0679 | 123.0207 | 66.7972 | -123.3106
136.9375 | 123.1888 | -66.7603 | 56.3095 | 0.048435 | -0.010579 | -0.0014454 | 0.056476 | -0.00018888 | 0.053208 | 0.041238 | -0.0023982 | -0.00065947 | 0.06435 | 0.012171 | 0.063345 | -64.5176 | 0.010564 | -66.6956 | 56.2747 | 56.1013 | 56.1886 | -66.8741 | -66.7336 | 0.018674 | -66.8368 | 56.0566 | 56.2893 | 56.1918 | -66.9874 | -0.11389 | -0.034778 | 2.2427 | 0.06461 | 0.1785 | -0.20817 | -0.12087 | -0.22715 | -0.2529 | 0.026605 | -0.07658 | 0.15057 | -0.020199 | -0.11773 | 123.035 | 122.8616 | 122.9489 | 66.7708 | -123.1837 | 122.8169 | 123.0496 | 122.952 | 66.7789 | -123.2969
137.9531 | 123.3215 | -66.7282 | 56.282 | 0.063697 | -0.011648 | -0.0014454 | 0.054339 | -0.0012569 | 0.053208 | 0.087021 | -0.0013302 | -0.00065947 | 0.063282 | 0.011103 | 0.063345 | -64.5542 | 0.0243 | -66.6956 | 56.261 | 56.1013 | 56.1978 | -66.8741 | -66.7291 | 0.009516 | -66.846 | 56.0566 | 56.2939 | 56.2559 | -66.9828 | -0.14593 | -0.021048 | 2.174 | 0.032566 | 0.1785 | -0.1807 | -0.084246 | -0.25462 | -0.22543 | -0.00086 | -0.11778 | 0.13684 | 0.011846 | -0.02616 | 122.9892 | 122.8296 | 122.926 | 66.7525 | -123.1562 | 122.7848 | 123.0221 | 122.9841 | 66.7377 | -123.2649
138.9375 | 123.1979 | -66.7831 | 56.3049 | 0.048435 | -0.0095107 | -0.0014454 | 0.054339 | -0.0012569 | 0.053208 | 0.07176 | -0.0013302 | -0.0017285 | 0.063282 | 0.011103 | 0.063345 | -64.5268 | 0.0243 | -66.6911 | 56.261 | 56.0922 | 56.1841 | -66.8696 | -66.7291 | 0.018674 | -66.8368 | 56.052 | 56.2939 | 56.2147 | -66.9828 | -0.086424 | -0.043937 | 2.2564 | 0.092077 | 0.1785 | -0.21275 | -0.12087 | -0.19969 | -0.2529 | 0.054072 | -0.053692 | 0.14599 | -0.011043 | -0.090257 | 123.0441 | 122.8753 | 122.9672 | 66.8074 | -123.1745 | 122.8352 | 123.077 | 122.9978 | 66.8018 | -123.2878
139.9531 | 123.0652 | -66.8243 | 56.2546 | 0.063697 | -0.010579 | 0.0017596 | 0.055407 | -0.0023249 | 0.056413 | 0.087021 | -0.0023982 | -0.0027965 | 0.062214 | 0.012171 | 0.062276 | -64.513 | 0.019721 | -66.6911 | 56.2656 | 56.1059 | 56.1932 | -66.8741 | -66.7291 | 0.014095 | -66.8368 | 56.0566 | 56.2893 | 56.2467 | -66.9828 | -0.049804 | 0.010996 | 2.3113 | 0.13328 | 0.18308 | -0.14866 | -0.06136 | -0.15849 | -0.19797 | 0.095271 | -0.012493 | 0.14599 | 0.034732 | -0.007853 | 123.0899 | 122.9303 | 123.0176 | 66.8441 | -123.1287 | 122.881 | 123.1137 | 123.0711 | 66.8384 | -123.2374
140.9375 | 123.1613 | -66.774 | 56.3095 | 0.063697 | -0.0095107 | 0.0017596 | 0.055407 | -0.0012569 | 0.056413 | 0.07176 | -0.0013302 | 0.00040853 | 0.063282 | 0.011103 | 0.061208 | -64.4993 | 0.001407 | -66.6956 | 56.2656 | 56.0922 | 56.1886 | -66.8787 | -66.7199 | 0.018674 | -66.8323 | 56.0658 | 56.2939 | 56.2559 | -66.9782 | -0.10474 | -0.043935 | 2.2747 | 0.078343 | 0.18308 | -0.21732 | -0.12087 | -0.20426 | -0.24374 | 0.054075 | -0.058269 | 0.14599 | -0.01562 | -0.053626 | 123.0396 | 122.8662 | 122.9626 | 66.7754 | -123.1882 | 122.8398 | 123.0679 | 123.0299 | 66.7927 | -123.2878
141.9375 | 123.1064 | -66.8198 | 56.2912 | 0.033173 | -0.0095107 | -0.00037739 | 0.055407 | -0.0012569 | 0.054276 | 0.056499 | -0.00026221 | -0.0017285 | 0.063282 | 0.010034 | 0.06014 | -64.5176 | 0.015142 | -66.7002 | 56.2702 | 56.1059 | 56.1978 | -66.8787 | -66.7245 | 0.014095 | -66.8414 | 56.0612 | 56.2893 | 56.2513 | -66.9828 | -0.058961 | -0.021047 | 2.3022 | 0.11954 | 0.1785 | -0.18528 | -0.093402 | -0.16307 | -0.23001 | 0.095272 | -0.02165 | 0.14141 | -0.001889 | -0.039895 | 123.0899 | 122.9257 | 123.0176 | 66.8349 | -123.1699 | 122.881 | 123.1091 | 123.0711 | 66.8339 | -123.274
142.9375 | 123.1613 | -66.774 | 56.3187 | 0.033173 | -0.010579 | -0.0014454 | 0.055407 | -0.0023249 | 0.055345 | 0.056499 | -0.0045342 | -0.0017285 | 0.06435 | 0.010034 | 0.062276 | -64.513 | 0.015142 | -66.6956 | 56.2656 | 56.1059 | 56.1932 | -66.8741 | -66.7291 | 0.009516 | -66.8368 | 56.0612 | 56.2939 | 56.2467 | -66.9782 | -0.10016 | -0.053091 | 2.261 | 0.078343 | 0.1785 | -0.21274 | -0.12545 | -0.20426 | -0.25747 | 0.044917 | -0.062847 | 0.14142 | -0.024776 | -0.07194 | 123.0396 | 122.8799 | 122.9672 | 66.7891 | -123.1928 | 122.8352 | 123.0679 | 123.0207 | 66.7835 | -123.2969
143.9375 | 123.2025 | -66.7831 | 56.3416 | 0.063697 | -0.010579 | -0.0014454 | 0.054339 | -0.0023249 | 0.053208 | 0.056499 | -0.0023982 | -0.0027965 | 0.06435 | 0.011103 | 0.063345 | -64.5084 | 0.015142 | -66.6911 | 56.2656 | 56.0968 | 56.1841 | -66.8741 | -66.7291 | 0.014095 | -66.8368 | 56.0612 | 56.2893 | 56.2421 | -66.9782 | -0.091003 | -0.075979 | 2.2747 | 0.092077 | 0.18308 | -0.24479 | -0.15749 | -0.19511 | -0.28036 | 0.054072 | -0.053692 | 0.14142 | -0.052243 | -0.099406 | 123.0487 | 122.8799 | 122.9672 | 66.7983 | -123.2157 | 122.8443 | 123.0725 | 123.0253 | 66.7972 | -123.3198
144.9531 | 123.1705 | -66.7877 | 56.3049 | 0.017911 | -0.011648 | -0.0014454 | 0.055407 | -0.0023249 | 0.054276 | 0.087021 | -0.0034662 | -0.0017285 | 0.063282 | 0.012171 | 0.064413 | -64.5039 | 0.019721 | -66.6956 | 56.2702 | 56.1013 | 56.1932 | -66.8787 | -66.7291 | 0.018674 | -66.8323 | 56.0612 | 56.2939 | 56.2284 | -66.9782 | -0.091004 | -0.03478 | 2.2839 | 0.092076 | 0.18308 | -0.20359 | -0.11171 | -0.19053 | -0.24374 | 0.05865 | -0.044536 | 0.14599 | -0.011043 | -0.076521 | 123.0579 | 122.8891 | 122.9809 | 66.8074 | -123.1837 | 122.8489 | 123.0816 | 123.0161 | 66.8064 | -123.2832
145.9375 | 123.1979 | -66.7831 | 56.3187 | 0.033173 | -0.0084417 | 0.00069161 | 0.057544 | -0.0012569 | 0.054276 | 0.041238 | -0.0023982 | -0.0017285 | 0.062214 | 0.012171 | 0.062276 | -64.5176 | 0.010564 | -66.6956 | 56.2656 | 56.1059 | 56.1932 | -66.8696 | -66.7428 | 0.014095 | -66.8323 | 56.0658 | 56.2893 | 56.2055 | -66.9828 | -0.086424 | -0.053091 | 2.2655 | 0.087498 | 0.17392 | -0.21274 | -0.12545 | -0.19969 | -0.2529 | 0.040336 | -0.049114 | 0.15057 | -0.029355 | -0.11315 | 123.0487 | 122.8891 | 122.9764 | 66.7937 | -123.1882 | 122.8489 | 123.0725 | 122.9887 | 66.7972 | -123.3015
146.9375 | 123.2162 | -66.7557 | 56.3095 | 0.063697 | -0.0095107 | 0.00069161 | 0.055407 | -0.0023249 | 0.055345 | 0.056499 | -0.0023982 | -0.0017285 | 0.061145 | 0.012171 | 0.063345 | -64.4993 | 0.005985 | -66.7002 | 56.2702 | 56.1105 | 56.1932 | -66.8787 | -66.7382 | 0.014095 | -66.8414 | 56.0566 | 56.2939 | 56.2467 | -66.9828 | -0.12305 | -0.039357 | 2.2564 | 0.055454 | 0.1785 | -0.19901 | -0.11629 | -0.22715 | -0.2529 | 0.017449 | -0.085737 | 0.14141 | -0.01562 | -0.062784 | 123.0258 | 122.8662 | 122.9489 | 66.7617 | -123.1882 | 122.8123 | 123.0496 | 123.0024 | 66.7698 | -123.2923
147.9531 | 123.1796 | -66.7923 | 56.3049 | 0.063697 | -0.0095107 | -0.0014454 | 0.055407 | -0.0023249 | 0.054276 | 0.041238 | -0.0034662 | -0.0027965 | 0.063282 | 0.011103 | 0.062276 | -64.5039 | 0.015142 | -66.7048 | 56.2656 | 56.1013 | 56.1932 | -66.8833 | -66.7291 | 0.014095 | -66.8323 | 56.0703 | 56.2985 | 56.2513 | -66.9782 | -0.091006 | -0.039358 | 2.2884 | 0.087497 | 0.1785 | -0.20359 | -0.11171 | -0.18595 | -0.23459 | 0.063227 | -0.039959 | 0.14599 | -0.006465 | -0.053628 | 123.0579 | 122.8936 | 122.9855 | 66.8074 | -123.1882 | 122.8626 | 123.0908 | 123.0436 | 66.8064 | -123.2832
148.9375 | 123.2208 | -66.7923 | 56.3004 | 0.033173 | -0.010579 | -0.0014454 | 0.053271 | -0.0012569 | 0.054276 | 0.041238 | -0.0023982 | -0.0017285 | 0.063282 | 0.01324 | 0.062276 | -64.513 | 0.005985 | -66.6911 | 56.261 | 56.1013 | 56.1932 | -66.8787 | -66.7245 | 0.018674 | -66.8368 | 56.0658 | 56.2893 | 56.2513 | -66.9782 | -0.086427 | -0.039359 | 2.2793 | 0.10123 | 0.18766 | -0.19901 | -0.10714 | -0.18595 | -0.23458 | 0.067806 | -0.044537 | 0.14142 | -0.011044 | -0.04905 | 123.0533 | 122.8936 | 122.9855 | 66.7983 | -123.1791 | 122.8581 | 123.0816 | 123.0436 | 66.811 | -123.2786
149.9531 | 123.2483 | -66.7328 | 56.3095 | 0.063697 | -0.0095107 | -0.00037739 | 0.057544 | -0.00018888 | 0.05214 | 0.07176 | -0.0013302 | -0.00065947 | 0.063282 | 0.012171 | 0.062276 | -64.5084 | 0.010564 | -66.7048 | 56.2747 | 56.1059 | 56.1978 | -66.8787 | -66.7291 | 0.014095 | -66.8414 | 56.0703 | 56.2939 | 56.2513 | -66.9737 | -0.14594 | -0.034778 | 2.2244 | 0.027988 | 0.17392 | -0.20359 | -0.11171 | -0.24088 | -0.23916 | 0.003718 | -0.10863 | 0.13226 | -0.01562 | -0.058205 | 123.0075 | 122.8387 | 122.9306 | 66.7434 | -123.1882 | 122.8031 | 123.0267 | 122.9841 | 66.7469 | -123.2832
150.9375 | 123.23 | -66.7648 | 56.3004 | 0.048435 | -0.011648 | 0.00069161 | 0.056476 | -0.0023249 | 0.053208 | 0.07176 | -0.0023982 | -0.00065947 | 0.062214 | 0.014308 | 0.063345 | -64.513 | 0.005985 | -66.7002 | 56.2702 | 56.1105 | 56.1886 | -66.8787 | -66.7291 | 0.004938 | -66.8368 | 56.0703 | 56.2985 | 56.2284 | -66.9828 | -0.11389 | -0.030202 | 2.2518 | 0.06461 | 0.1785 | -0.18985 | -0.11171 | -0.218 | -0.23001 | 0.035762 | -0.072002 | 0.14599 | -0.001887 | -0.071943 | 123.035 | 122.8753 | 122.9535 | 66.7708 | -123.1791 | 122.8352 | 123.0633 | 122.9932 | 66.7698 | -123.2832
151.9375 | 123.2162 | -66.7786 | 56.3004 | 0.033173 | -0.0095107 | 0.00069161 | 0.056476 | -0.0012569 | 0.05214 | 0.07176 | -0.0023982 | -0.0027965 | 0.062214 | 0.01324 | 0.062276 | -64.5176 | 0.005985 | -66.7048 | 56.2702 | 56.1105 | 56.1978 | -66.8787 | -66.7245 | 0.004938 | -66.8323 | 56.0749 | 56.2985 | 56.2284 | -66.9828 | -0.10016 | -0.030202 | 2.261 | 0.073764 | 0.17392 | -0.18985 | -0.10256 | -0.20426 | -0.22543 | 0.054073 | -0.053692 | 0.15057 | -0.001887 | -0.071943 | 123.0487 | 122.8891 | 122.9764 | 66.7845 | -123.1791 | 122.8535 | 123.077 | 123.007 | 66.7835 | -123.2832
152.9375 | 123.2346 | -66.7603 | 56.3324 | 0.063697 | -0.0095107 | -0.00037739 | 0.055407 | -0.0023249 | 0.055345 | 0.041238 | -0.0023982 | -0.0017285 | 0.063282 | 0.012171 | 0.062276 | -64.5176 | 0.005985 | -66.7002 | 56.261 | 56.1105 | 56.2024 | -66.8787 | -66.7291 | 0.004938 | -66.8368 | 56.0658 | 56.2939 | 56.2055 | -66.9828 | -0.11847 | -0.071402 | 2.2427 | 0.060032 | 0.1785 | -0.2219 | -0.13002 | -0.22257 | -0.26663 | 0.031184 | -0.07658 | 0.14599 | -0.038508 | -0.12688 | 123.0212 | 122.8708 | 122.9626 | 66.7662 | -123.2111 | 122.826 | 123.0541 | 122.9658 | 66.7652 | -123.3152
153.9375 | 123.1201 | -66.7786 | 56.3232 | 0.063697 | -0.0095107 | -0.0014454 | 0.054339 | -0.0012569 | 0.054276 | 0.087021 | -0.0034662 | -0.0017285 | 0.061145 | 0.012171 | 0.061208 | -64.5084 | 0.001407 | -66.7002 | 56.2656 | 56.1151 | 56.1932 | -66.8696 | -66.7291 | 0.004938 | -66.8277 | 56.0749 | 56.2939 | 56.2147 | -66.9782 | -0.091002 | -0.057668 | 2.2701 | 0.078342 | 0.16934 | -0.20816 | -0.13002 | -0.19969 | -0.24832 | 0.049494 | -0.049113 | 0.15057 | -0.029353 | -0.10857 | 123.0441 | 122.8936 | 122.9718 | 66.78 | -123.1928 | 122.8535 | 123.0725 | 122.9932 | 66.7835 | -123.3015
154.9531 | 123.349 | -66.7831 | 56.3553 | 0.063697 | -0.010579 | 0.0017596 | 0.055407 | -0.0023249 | 0.054276 | 0.041238 | -0.0034662 | -0.00065947 | 0.062214 | 0.012171 | 0.062276 | -64.513 | 0.010564 | -66.7002 | 56.261 | 56.1105 | 56.1841 | -66.8833 | -66.7291 | 0.009516 | -66.846 | 56.0703 | 56.2939 | 56.2238 | -66.9782 | -0.10016 | -0.094291 | 2.2701 | 0.08292 | 0.18308 | -0.24479 | -0.17122 | -0.19511 | -0.28494 | 0.054072 | -0.06285 | 0.13226 | -0.061397 | -0.13145 | 123.0441 | 122.8936 | 122.9672 | 66.7937 | -123.2386 | 122.8535 | 123.077 | 123.007 | 66.7927 | -123.3335
155.9375 | 123.2529 | -66.7694 | 56.3095 | 0.078959 | -0.012716 | -0.0014454 | 0.055407 | -0.0033929 | 0.053208 | 0.056499 | -0.0023982 | -0.0017285 | 0.062214 | 0.014308 | 0.064413 | -64.5084 | 0.010564 | -66.7002 | 56.2702 | 56.1013 | 56.1886 | -66.8696 | -66.7382 | 0.009516 | -66.8368 | 56.0612 | 56.2985 | 56.2376 | -66.9782 | -0.10016 | -0.039357 | 2.261 | 0.069187 | 0.16934 | -0.20817 | -0.12087 | -0.20884 | -0.24832 | 0.031182 | -0.067425 | 0.14142 | -0.011042 | -0.071941 | 123.0396 | 122.8708 | 122.958 | 66.78 | -123.1791 | 122.8306 | 123.0679 | 123.007 | 66.7789 | -123.2878
156.9531 | 123.2574 | -66.7694 | 56.3141 | 0.063697 | -0.012716 | -0.0025134 | 0.054339 | -0.0033929 | 0.054276 | 0.07176 | -0.0013302 | -0.0027965 | 0.062214 | 0.01324 | 0.064413 | -64.4993 | 0.001407 | -66.7002 | 56.2702 | 56.1059 | 56.1978 | -66.8879 | -66.7291 | 0.009516 | -66.8368 | 56.0749 | 56.2939 | 56.2376 | -66.9828 | -0.11847 | -0.043935 | 2.2701 | 0.069187 | 0.18766 | -0.20817 | -0.11629 | -0.21342 | -0.23916 | 0.040339 | -0.067425 | 0.14599 | -0.020198 | -0.076519 | 123.0396 | 122.8753 | 122.9672 | 66.7708 | -123.202 | 122.8443 | 123.0633 | 123.007 | 66.7789 | -123.2969
157.9375 | 123.2254 | -66.7511 | 56.3324 | 0.078959 | -0.011648 | -0.0014454 | 0.055407 | -0.00018888 | 0.05214 | 0.087021 | -0.0023982 | -0.0017285 | 0.061145 | 0.012171 | 0.061208 | -64.513 | 0.001407 | -66.7002 | 56.2702 | 56.1013 | 56.207 | -66.8787 | -66.7336 | 0.000359 | -66.8368 | 56.0658 | 56.2985 | 56.2101 | -66.9874 | -0.12763 | -0.062245 | 2.2381 | 0.050877 | 0.1785 | -0.23105 | -0.12544 | -0.23631 | -0.26663 | 0.01745 | -0.085735 | 0.15057 | -0.03393 | -0.1223 | 123.0213 | 122.8524 | 122.9581 | 66.7525 | -123.2111 | 122.8169 | 123.0496 | 122.9612 | 66.7515 | -123.3198
158.9375 | 123.2483 | -66.7831 | 56.3049 | 0.048435 | -0.0095107 | -0.00037739 | 0.055407 | -0.0023249 | 0.055345 | 0.07176 | -0.0013302 | -0.00065947 | 0.062214 | 0.014308 | 0.061208 | -64.513 | -0.003172 | -66.7002 | 56.2564 | 56.1105 | 56.1978 | -66.8833 | -66.7245 | 0.009516 | -66.8323 | 56.0658 | 56.303 | 56.2513 | -66.9828 | -0.10016 | -0.048515 | 2.2701 | 0.08292 | 0.18308 | -0.19443 | -0.10713 | -0.19969 | -0.23916 | 0.058651 | -0.049114 | 0.15057 | -0.001886 | -0.053628 | 123.0396 | 122.8936 | 122.9809 | 66.78 | -123.1882 | 122.8489 | 123.0862 | 123.0344 | 66.7927 | -123.2878
159.9375 | 123.2208 | -66.7557 | 56.3324 | 0.063697 | -0.011648 | -0.00037739 | 0.055407 | -0.0023249 | 0.05214 | 0.056499 | -0.0023982 | -0.0027965 | 0.063282 | 0.01324 | 0.061208 | -64.5268 | -0.003172 | -66.7002 | 56.2656 | 56.1151 | 56.1932 | -66.8741 | -66.7245 | 0.000359 | -66.8414 | 56.0658 | 56.303 | 56.1918 | -66.9874 | -0.11847 | -0.066823 | 2.2289 | 0.055454 | 0.17392 | -0.21732 | -0.13918 | -0.23173 | -0.26663 | 0.031185 | -0.085737 | 0.14599 | -0.029351 | -0.14061 | 123.0212 | 122.8708 | 122.9489 | 66.7525 | -123.2065 | 122.8214 | 123.0587 | 122.9475 | 66.756 | -123.3198
160.9375 | 123.2666 | -66.7603 | 56.3232 | 0.048435 | -0.011648 | -0.0014454 | 0.056476 | -0.0044619 | 0.053208 | 0.041238 | -0.0034662 | -0.0017285 | 0.061145 | 0.014308 | 0.061208 | -64.5039 | -0.007751 | -66.6956 | 56.2656 | 56.1059 | 56.1932 | -66.8879 | -66.7382 | -0.00422 | -66.8368 | 56.0703 | 56.2985 | 56.2193 | -66.9874 | -0.12763 | -0.057668 | 2.2564 | 0.06461 | 0.19224 | -0.21732 | -0.13002 | -0.22715 | -0.2529 | 0.022027 | -0.07658 | 0.15057 | -0.024775 | -0.10399 | 123.0258 | 122.8662 | 122.9535 | 66.7525 | -123.2111 | 122.8306 | 123.0587 | 122.9795 | 66.756 | -123.3106
161.9531 | 123.2986 | -66.7145 | 56.3187 | 0.063697 | -0.010579 | -0.0014454 | 0.056476 | -0.0023249 | 0.053208 | 0.07176 | -0.0013302 | -0.0017285 | 0.060077 | 0.012171 | 0.06014 | -64.5405 | -0.012329 | -66.6956 | 56.261 | 56.1059 | 56.1932 | -66.8741 | -66.7291 | 0.000359 | -66.8414 | 56.0658 | 56.2985 | 56.2284 | -66.9874 | -0.15967 | -0.05767 | 2.174 | 0.018834 | 0.1785 | -0.21274 | -0.12545 | -0.27293 | -0.2529 | -0.014592 | -0.12694 | 0.14599 | -0.020198 | -0.090254 | 122.9755 | 122.8204 | 122.9077 | 66.7021 | -123.1928 | 122.7802 | 123.0129 | 122.9429 | 66.7148 | -123.3061
162.9375 | 123.3032 | -66.7694 | 56.2775 | 0.063697 | -0.013784 | -0.0025134 | 0.055407 | -0.0012569 | 0.053208 | 0.07176 | -0.0023982 | -0.00065947 | 0.062214 | 0.015376 | 0.061208 | -64.4947 | -0.007751 | -66.7002 | 56.261 | 56.1059 | 56.1886 | -66.8696 | -66.7245 | -0.00422 | -66.8414 | 56.0658 | 56.303 | 56.2467 | -66.9737 | -0.10016 | -0.016471 | 2.2747 | 0.069187 | 0.16934 | -0.17154 | -0.088827 | -0.20426 | -0.2117 | 0.044918 | -0.072004 | 0.13226 | 0.02558 | -0.030741 | 123.0304 | 122.8753 | 122.958 | 66.7617 | -123.147 | 122.8352 | 123.0725 | 123.0161 | 66.7652 | -123.2511
163.9531 | 123.317 | -66.7191 | 56.2912 | 0.078959 | -0.011648 | -0.00037739 | 0.054339 | -0.0012569 | 0.05214 | 0.10228 | -0.0034662 | -0.0027965 | 0.062214 | 0.015376 | 0.062276 | -64.5542 | -0.016908 | -66.7002 | 56.261 | 56.1013 | 56.1932 | -66.8696 | -66.7291 | -0.00422 | -66.8414 | 56.0612 | 56.303 | 56.2559 | -66.992 | -0.15051 | -0.030204 | 2.1648 | 0.018833 | 0.16934 | -0.18986 | -0.097981 | -0.27293 | -0.23001 | -0.010015 | -0.12236 | 0.15057 | 0.011847 | -0.035316 | 122.9801 | 122.8204 | 122.9123 | 66.7021 | -123.1608 | 122.7802 | 123.0221 | 122.9749 | 66.7148 | -123.2832
164.9375 | 123.2529 | -66.7419 | 56.3232 | 0.063697 | -0.010579 | -0.00037739 | 0.056476 | -0.0023249 | 0.054276 | 0.056499 | -0.0034662 | -0.00065947 | 0.061145 | 0.015376 | 0.062276 | -64.5039 | -0.007751 | -66.6956 | 56.2656 | 56.1105 | 56.1932 | -66.8787 | -66.7291 | -0.00422 | -66.8414 | 56.0703 | 56.2939 | 56.2513 | -66.9874 | -0.13678 | -0.057668 | 2.2381 | 0.046299 | 0.18308 | -0.21274 | -0.13002 | -0.24546 | -0.2529 | 0.012873 | -0.09947 | 0.14599 | -0.029353 | -0.071938 | 123.0075 | 122.8524 | 122.9352 | 66.7342 | -123.202 | 122.8123 | 123.0358 | 122.9932 | 66.7377 | -123.3106
165.9375 | 123.2254 | -66.7694 | 56.2958 | 0.063697 | -0.013784 | -0.0014454 | 0.056476 | -0.0033929 | 0.05214 | 0.056499 | -0.0034662 | -0.0027965 | 0.063282 | 0.014308 | 0.061208 | -64.5084 | -0.012329 | -66.7048 | 56.2747 | 56.1105 | 56.1932 | -66.8833 | -66.7291 | -0.00422 | -66.8368 | 56.0703 | 56.303 | 56.2559 | -66.9782 | -0.11389 | -0.021045 | 2.261 | 0.064609 | 0.1785 | -0.18528 | -0.10256 | -0.20884 | -0.22543 | 0.040339 | -0.067425 | 0.14142 | 0.00727 | -0.039893 | 123.0441 | 122.8799 | 122.9626 | 66.7571 | -123.1791 | 122.8398 | 123.0725 | 123.0253 | 66.7652 | -123.274
166.9531 | 123.2529 | -66.7603 | 56.3232 | 0.033173 | -0.0095107 | -0.00037739 | 0.055407 | -0.0023249 | 0.054276 | 0.07176 | -0.0023982 | -0.0017285 | 0.063282 | 0.014308 | 0.061208 | -64.5176 | -0.016908 | -66.7094 | 56.2656 | 56.1105 | 56.1932 | -66.8833 | -66.7336 | -0.013377 | -66.8414 | 56.0749 | 56.2985 | 56.2238 | -66.9828 | -0.12305 | -0.057668 | 2.2427 | 0.050875 | 0.17392 | -0.21274 | -0.13002 | -0.22257 | -0.24832 | 0.026605 | -0.081159 | 0.14141 | -0.024775 | -0.09941 | 123.0258 | 122.8708 | 122.9535 | 66.7433 | -123.2065 | 122.8352 | 123.0587 | 122.9841 | 66.7469 | -123.3061
167.9375 | 123.2574 | -66.7831 | 56.3232 | 0.094221 | -0.012716 | -0.00037739 | 0.055407 | -0.0044619 | 0.05214 | 0.056499 | -0.0013302 | -0.00065947 | 0.062214 | 0.014308 | 0.06014 | -64.5084 | -0.021486 | -66.7002 | 56.2656 | 56.1105 | 56.1978 | -66.8833 | -66.7291 | -0.008798 | -66.8368 | 56.0612 | 56.2985 | 56.2101 | -66.9828 | -0.10016 | -0.057668 | 2.2747 | 0.08292 | 0.18308 | -0.21274 | -0.12544 | -0.19969 | -0.26205 | 0.054072 | -0.053692 | 0.14599 | -0.024775 | -0.11315 | 123.0487 | 122.8936 | 122.9809 | 66.7617 | -123.2065 | 122.8443 | 123.0816 | 122.9932 | 66.7743 | -123.3061
168.9375 | 123.3124 | -66.7694 | 56.3278 | 0.063697 | -0.013784 | -0.0014454 | 0.053271 | -0.0023249 | 0.054276 | 0.07176 | -0.0034662 | -0.00065947 | 0.060077 | 0.015376 | 0.062276 | -64.4993 | -0.026065 | -66.6956 | 56.2747 | 56.1105 | 56.1978 | -66.8787 | -66.7382 | -0.013377 | -66.8368 | 56.0612 | 56.2985 | 56.2559 | -66.9828 | -0.10932 | -0.053089 | 2.2701 | 0.073765 | 0.18308 | -0.21732 | -0.13002 | -0.21342 | -0.26663 | 0.031182 | -0.067425 | 0.14599 | -0.029353 | -0.071937 | 123.0441 | 122.8799 | 122.9672 | 66.7433 | -123.2065 | 122.8306 | 123.0679 | 123.0253 | 66.756 | -123.3106
169.9375 | 123.0927 | -66.7694 | 56.3095 | 0.033173 | -0.011648 | -0.00037739 | 0.055407 | -0.0023249 | 0.05214 | 0.087021 | -0.0023982 | -0.00065947 | 0.062214 | 0.015376 | 0.062276 | -64.513 | -0.030644 | -66.7048 | 56.2656 | 56.1151 | 56.1978 | -66.8833 | -66.7382 | -0.013377 | -66.8368 | 56.0703 | 56.2985 | 56.2605 | -66.9874 | -0.11389 | -0.043935 | 2.2564 | 0.064609 | 0.1785 | -0.19443 | -0.11171 | -0.218 | -0.23916 | 0.031182 | -0.067425 | 0.15057 | -0.011042 | -0.049048 | 123.035 | 122.8845 | 122.9672 | 66.7388 | -123.1928 | 122.8398 | 123.0679 | 123.0299 | 66.756 | -123.2969
170.9375 | 123.2346 | -66.7603 | 56.3141 | 0.063697 | -0.011648 | -0.0014454 | 0.055407 | -0.0023249 | 0.054276 | 0.056499 | -0.0034662 | 0.00040853 | 0.063282 | 0.014308 | 0.061208 | -64.5084 | -0.035222 | -66.7002 | 56.2656 | 56.1151 | 56.2024 | -66.8833 | -66.7291 | -0.017956 | -66.8323 | 56.0658 | 56.2939 | 56.2193 | -66.9828 | -0.12305 | -0.048513 | 2.2518 | 0.060032 | 0.18308 | -0.19901 | -0.11171 | -0.22257 | -0.24832 | 0.031184 | -0.072002 | 0.15057 | -0.020198 | -0.094833 | 123.0258 | 122.8753 | 122.9626 | 66.725 | -123.1974 | 122.826 | 123.0541 | 122.9795 | 66.7423 | -123.2969
171.9375 | 123.2391 | -66.7648 | 56.3049 | 0.063697 | -0.011648 | -0.00037739 | 0.055407 | -0.0023249 | 0.054276 | 0.041238 | -0.0023982 | -0.00065947 | 0.063282 | 0.018581 | 0.061208 | -64.5039 | -0.035222 | -66.7002 | 56.2747 | 56.1151 | 56.207 | -66.8741 | -66.7382 | -0.022535 | -66.8368 | 56.0703 | 56.2985 | 56.2238 | -66.9737 | -0.10931 | -0.030201 | 2.261 | 0.06461 | 0.17392 | -0.18985 | -0.097978 | -0.20884 | -0.23459 | 0.026605 | -0.072002 | 0.13684 | -0.006465 | -0.0811 | 123.0396 | 122.8799 | 122.9718 | 66.7296 | -123.1791 | 122.8352 | 123.0633 | 122.9887 | 66.7423 | -123.2786
172.9375 | 123.2391 | -66.7374 | 56.3141 | 0.048435 | -0.011648 | -0.00037739 | 0.053271 | -0.0033929 | 0.053208 | 0.056499 | -0.0023982 | -0.0017285 | 0.062214 | 0.014308 | 0.062276 | -64.5039 | -0.035222 | -66.7002 | 56.2702 | 56.1105 | 56.1932 | -66.8741 | -66.7291 | -0.022535 | -66.8277 | 56.0703 | 56.303 | 56.1826 | -66.9782 | -0.13678 | -0.043935 | 2.2335 | 0.037144 | 0.17392 | -0.20359 | -0.12087 | -0.24088 | -0.24374 | 0.008296 | -0.090311 | 0.15057 | -0.011041 | -0.13146 | 123.0075 | 122.8479 | 122.9306 | 66.7021 | -123.1882 | 122.8077 | 123.0404 | 122.92 | 66.7148 | -123.2923
173.9375 | 123.23 | -66.7328 | 56.3232 | 0.063697 | -0.011648 | -0.0014454 | 0.054339 | -0.0033929 | 0.055345 | 0.056499 | -0.0013302 | 0.0014765 | 0.062214 | 0.016445 | 0.06014 | -64.513 | -0.048958 | -66.7094 | 56.2702 | 56.1151 | 56.2024 | -66.8787 | -66.7336 | -0.031692 | -66.8323 | 56.0658 | 56.2985 | 56.2238 | -66.9828 | -0.14594 | -0.05309 | 2.2198 | 0.023409 | 0.16935 | -0.20816 | -0.12087 | -0.25004 | -0.25747 | -0.000861 | -0.099468 | 0.15057 | -0.024775 | -0.09941 | 123.0029 | 122.8479 | 122.9352 | 66.6838 | -123.202 | 122.7986 | 123.0313 | 122.9566 | 66.7011 | -123.3061
174.9375 | 123.2529 | -66.7648 | 56.2958 | 0.063697 | -0.013784 | -0.0014454 | 0.054339 | -0.0023249 | 0.051071 | 0.041238 | -0.0034662 | -0.0027965 | 0.063282 | 0.014308 | 0.063345 | -64.5084 | -0.053537 | -66.7002 | 56.2747 | 56.1105 | 56.2024 | -66.8833 | -66.7382 | -0.031692 | -66.8414 | 56.0749 | 56.303 | 56.2559 | -66.9874 | -0.11847 | -0.021045 | 2.2564 | 0.06461 | 0.18308 | -0.18528 | -0.093401 | -0.22258 | -0.22085 | 0.026605 | -0.076581 | 0.14599 | 0.00727 | -0.039893 | 123.0396 | 122.8753 | 122.9672 | 66.7113 | -123.1791 | 122.8398 | 123.0679 | 123.0207 | 66.7331 | -123.2832
175.9375 | 123.2437 | -66.7648 | 56.2866 | 0.063697 | -0.012716 | -0.0014454 | 0.054339 | -0.0012569 | 0.054276 | 0.041238 | -0.0034662 | -0.0017285 | 0.060077 | 0.016445 | 0.061208 | -64.4993 | -0.053537 | -66.7002 | 56.2656 | 56.1059 | 56.2024 | -66.8741 | -66.7291 | -0.036271 | -66.846 | 56.0749 | 56.303 | 56.2467 | -66.9828 | -0.10931 | -0.021047 | 2.2656 | 0.06461 | 0.17392 | -0.1807 | -0.084246 | -0.218 | -0.21169 | 0.035762 | -0.08116 | 0.13684 | 0.016425 | -0.039896 | 123.0304 | 122.8708 | 122.9672 | 66.7113 | -123.1608 | 122.8398 | 123.0679 | 123.0116 | 66.7286 | -123.2694
176.9375 | 123.2483 | -66.774 | 56.3095 | 0.048435 | -0.010579 | -0.00037739 | 0.055407 | -0.0033929 | 0.053208 | 0.07176 | -0.0034662 | 0.00040853 | 0.061145 | 0.014308 | 0.061208 | -64.4993 | -0.067272 | -66.7002 | 56.2702 | 56.1105 | 56.2024 | -66.8787 | -66.7336 | -0.040849 | -66.8323 | 56.0658 | 56.2985 | 56.2559 | -66.9828 | -0.10474 | -0.039357 | 2.2747 | 0.073765 | 0.1785 | -0.19901 | -0.10713 | -0.20884 | -0.24374 | 0.040338 | -0.058269 | 0.15057 | -0.011042 | -0.053626 | 123.0441 | 122.8845 | 122.9764 | 66.7067 | -123.1882 | 122.8398 | 123.0725 | 123.0299 | 66.7331 | -123.2923
177.9375 | 123.2346 | -66.7419 | 56.3278 | 0.048435 | -0.013784 | 0.00069161 | 0.053271 | -0.0044619 | 0.05214 | 0.07176 | -0.0023982 | -0.0017285 | 0.061145 | 0.015376 | 0.061208 | -64.5084 | -0.058115 | -66.7048 | 56.2702 | 56.1105 | 56.1978 | -66.8741 | -66.7291 | -0.036271 | -66.8414 | 56.0703 | 56.303 | 56.2055 | -66.9874 | -0.1322 | -0.057668 | 2.2335 | 0.037143 | 0.16934 | -0.21732 | -0.13002 | -0.24546 | -0.25747 | 0.012873 | -0.09947 | 0.14599 | -0.024774 | -0.1223 | 123.0121 | 122.8524 | 122.9397 | 66.6838 | -123.202 | 122.8123 | 123.045 | 122.9475 | 66.7057 | -123.3152
178.9375 | 123.2483 | -66.7603 | 56.3004 | 0.063697 | -0.014853 | -0.0014454 | 0.054339 | -0.0023249 | 0.053208 | 0.07176 | -0.0023982 | -0.0027965 | 0.060077 | 0.015376 | 0.062276 | -64.513 | -0.067272 | -66.7002 | 56.2702 | 56.1059 | 56.2024 | -66.8879 | -66.7291 | -0.045428 | -66.8368 | 56.0703 | 56.303 | 56.2147 | -66.9874 | -0.12763 | -0.030202 | 2.2472 | 0.060032 | 0.18766 | -0.19443 | -0.097979 | -0.22715 | -0.23001 | 0.031184 | -0.07658 | 0.15057 | 0.002692 | -0.085679 | 123.0304 | 122.8662 | 122.9626 | 66.693 | -123.1882 | 122.8306 | 123.0633 | 122.9749 | 66.7148 | -123.2878
179.9375 | 123.2391 | -66.7419 | 56.3004 | 0.048435 | -0.013784 | -0.00037739 | 0.054339 | -0.0012569 | 0.054276 | 0.07176 | -0.0034662 | -0.0027965 | 0.062214 | 0.016445 | 0.06014 | -64.513 | -0.067272 | -66.7002 | 56.2656 | 56.1197 | 56.2024 | -66.8696 | -66.7291 | -0.045428 | -66.8368 | 56.0703 | 56.2985 | 56.2147 | -66.9874 | -0.12762 | -0.03478 | 2.2289 | 0.041721 | 0.16934 | -0.1807 | -0.097979 | -0.24546 | -0.23001 | 0.012873 | -0.094891 | 0.15057 | -0.001887 | -0.085679 | 123.0075 | 122.8616 | 122.9443 | 66.6747 | -123.1699 | 122.8123 | 123.0404 | 122.9566 | 66.6965 | -123.2878
180.9375 | 123.2391 | -66.7374 | 56.3187 | 0.078959 | -0.012716 | 0.00069161 | 0.055407 | -0.0023249 | 0.053208 | 0.056499 | -0.0013302 | -0.0027965 | 0.061145 | 0.015376 | 0.061208 | -64.5084 | -0.07643 | -66.7048 | 56.2656 | 56.1197 | 56.2207 | -66.8833 | -66.7245 | -0.050007 | -66.8277 | 56.0703 | 56.2985 | 56.265 | -66.9828 | -0.14594 | -0.053091 | 2.2289 | 0.032566 | 0.1785 | -0.19901 | -0.097975 | -0.24546 | -0.24832 | 0.012875 | -0.090311 | 0.15515 | -0.020198 | -0.053625 | 123.0029 | 122.857 | 122.9581 | 66.6609 | -123.202 | 122.8077 | 123.0358 | 123.0024 | 66.6874 | -123.3015
181.9375 | 123.2254 | -66.7511 | 56.337 | 0.094221 | -0.013784 | -0.0014454 | 0.054339 | -0.0044619 | 0.051071 | 0.07176 | -0.0023982 | -0.0027965 | 0.062214 | 0.018581 | 0.062276 | -64.513 | -0.085587 | -66.6956 | 56.2793 | 56.1151 | 56.1978 | -66.8833 | -66.7291 | -0.054586 | -66.8368 | 56.0795 | 56.2939 | 56.2605 | -66.9874 | -0.1322 | -0.057666 | 2.2381 | 0.055455 | 0.18766 | -0.2219 | -0.13918 | -0.23631 | -0.25747 | 0.022029 | -0.085735 | 0.15057 | -0.043086 | -0.076514 | 123.0304 | 122.8662 | 122.9489 | 66.6655 | -123.2203 | 122.8306 | 123.045 | 123.0116 | 66.6965 | -123.3244
182.9375 | 123.2483 | -66.7557 | 56.3095 | 0.048435 | -0.013784 | -0.00037739 | 0.055407 | -0.0033929 | 0.054276 | 0.056499 | -0.0045342 | -0.0027965 | 0.061145 | 0.015376 | 0.059071 | -64.5084 | -0.090166 | -66.6956 | 56.2702 | 56.1197 | 56.2024 | -66.8741 | -66.7336 | -0.063743 | -66.8414 | 56.0795 | 56.2939 | 56.2605 | -66.9874 | -0.11847 | -0.039357 | 2.2472 | 0.060032 | 0.1785 | -0.18985 | -0.10713 | -0.23173 | -0.23 | 0.022027 | -0.085737 | 0.14599 | -0.01562 | -0.049048 | 123.0258 | 122.8753 | 122.9581 | 66.6655 | -123.1837 | 122.8352 | 123.0496 | 123.0161 | 66.6919 | -123.2969
183.9375 | 123.23 | -66.774 | 56.3141 | 0.048435 | -0.011648 | -0.0014454 | 0.057544 | -0.0033929 | 0.053208 | 0.07176 | -0.00026221 | -0.0027965 | 0.061145 | 0.017513 | 0.06014 | -64.513 | -0.099323 | -66.7094 | 56.2747 | 56.1151 | 56.2024 | -66.8696 | -66.7291 | -0.068322 | -66.8323 | 56.0749 | 56.2985 | 56.2101 | -66.9828 | -0.095579 | -0.039356 | 2.261 | 0.064608 | 0.16019 | -0.19901 | -0.11171 | -0.20884 | -0.23916 | 0.044917 | -0.058269 | 0.15057 | -0.01562 | -0.10399 | 123.0487 | 122.8891 | 122.9764 | 66.6747 | -123.1837 | 122.8489 | 123.0725 | 122.9841 | 66.7057 | -123.2969
184.9375 | 123.2437 | -66.7511 | 56.3278 | 0.063697 | -0.013784 | -0.0025134 | 0.055407 | -0.0033929 | 0.053208 | 0.087021 | -0.0034662 | -0.0017285 | 0.061145 | 0.016445 | 0.061208 | -64.513 | -0.1039 | -66.7002 | 56.2747 | 56.1059 | 56.2024 | -66.8741 | -66.7291 | -0.0729 | -66.8277 | 56.0703 | 56.3076 | 56.2147 | -66.9874 | -0.12305 | -0.053089 | 2.2381 | 0.050877 | 0.17392 | -0.2219 | -0.12544 | -0.23631 | -0.25747 | 0.022029 | -0.076578 | 0.15973 | -0.020196 | -0.11315 | 123.0258 | 122.857 | 122.9535 | 66.6472 | -123.202 | 122.8214 | 123.0587 | 122.9658 | 66.6782 | -123.3152
185.9375 | 123.2391 | -66.7648 | 56.3232 | 0.048435 | -0.013784 | -0.0014454 | 0.055407 | -0.0023249 | 0.05214 | 0.07176 | -0.0013302 | -0.00065947 | 0.062214 | 0.016445 | 0.061208 | -64.5176 | -0.10848 | -66.6956 | 56.2702 | 56.1151 | 56.2161 | -66.8833 | -66.7336 | -0.0729 | -66.8414 | 56.0703 | 56.2939 | 56.2421 | -66.9874 | -0.11847 | -0.05309 | 2.2472 | 0.069188 | 0.18766 | -0.20816 | -0.10713 | -0.22258 | -0.2529 | 0.031183 | -0.076581 | 0.14599 | -0.029353 | -0.081095 | 123.035 | 122.8799 | 122.9809 | 66.6564 | -123.2065 | 122.8352 | 123.0587 | 123.007 | 66.6919 | -123.3106
186.9375 | 123.1201 | -66.7557 | 56.3324 | 0.048435 | -0.013784 | -0.0014454 | 0.054339 | -0.0044619 | 0.05214 | 0.056499 | -0.0034662 | -0.0017285 | 0.062214 | 0.016445 | 0.06014 | -64.513 | -0.12222 | -66.6956 | 56.2747 | 56.1105 | 56.2115 | -66.8696 | -66.7291 | -0.082058 | -66.8368 | 56.0658 | 56.2985 | 56.233 | -66.9828 | -0.11389 | -0.057666 | 2.2427 | 0.060032 | 0.17392 | -0.2219 | -0.12087 | -0.22715 | -0.26663 | 0.026606 | -0.081158 | 0.14599 | -0.03393 | -0.099407 | 123.0304 | 122.8662 | 122.9672 | 66.6335 | -123.202 | 122.8214 | 123.0541 | 122.9887 | 66.6736 | -123.3152
187.9375 | 123.2391 | -66.7557 | 56.3461 | 0.063697 | -0.012716 | -0.0014454 | 0.055407 | -0.0033929 | 0.053208 | 0.07176 | -0.0023982 | -0.0017285 | 0.063282 | 0.018581 | 0.06014 | -64.5084 | -0.12679 | -66.7002 | 56.2747 | 56.1105 | 56.1978 | -66.8787 | -66.7245 | -0.082058 | -66.8368 | 56.0658 | 56.303 | 56.2513 | -66.9782 | -0.12305 | -0.071399 | 2.2472 | 0.055454 | 0.1785 | -0.23563 | -0.14833 | -0.22257 | -0.28036 | 0.031185 | -0.081158 | 0.14142 | -0.043084 | -0.094826 | 123.0304 | 122.8662 | 122.9535 | 66.6289 | -123.2249 | 122.8214 | 123.0587 | 123.007 | 66.6736 | -123.3244
188.9375 | 123.1979 | -66.7465 | 56.3461 | 0.063697 | -0.015921 | -0.0025134 | 0.054339 | -0.0033929 | 0.053208 | 0.087021 | -0.0023982 | -0.0017285 | 0.061145 | 0.017513 | 0.06014 | -64.5084 | -0.13595 | -66.6911 | 56.2747 | 56.1105 | 56.1978 | -66.8787 | -66.7245 | -0.10037 | -66.8323 | 56.0703 | 56.2893 | 56.2559 | -66.9874 | -0.1322 | -0.071399 | 2.2381 | 0.055456 | 0.18766 | -0.23563 | -0.14833 | -0.24089 | -0.27578 | 0.02203 | -0.085735 | 0.15515 | -0.05682 | -0.090247 | 123.0213 | 122.857 | 122.9443 | 66.6106 | -123.2249 | 122.8169 | 123.0358 | 123.0024 | 66.6461 | -123.3335
189.9375 | 123.262 | -66.7419 | 56.3461 | 0.094221 | -0.015921 | -0.0025134 | 0.054339 | -0.0033929 | 0.053208 | 0.056499 | -0.0034662 | -0.0017285 | 0.060077 | 0.018581 | 0.061208 | -64.4947 | -0.14053 | -66.6956 | 56.2702 | 56.1105 | 56.2024 | -66.8787 | -66.7199 | -0.095794 | -66.8277 | 56.0749 | 56.303 | 56.2605 | -66.9874 | -0.13678 | -0.075978 | 2.2472 | 0.046299 | 0.18308 | -0.23563 | -0.14375 | -0.24546 | -0.2712 | 0.022031 | -0.085734 | 0.15973 | -0.043084 | -0.085669 | 123.0121 | 122.8524 | 122.9443 | 66.6014 | -123.2249 | 122.8169 | 123.045 | 123.0024 | 66.6461 | -123.3335
190.9375 | 123.2117 | -66.7557 | 56.3461 | 0.063697 | -0.014853 | -0.0014454 | 0.053271 | -0.0033929 | 0.054276 | 0.056499 | -0.00026221 | -0.0038645 | 0.062214 | 0.017513 | 0.061208 | -64.4947 | -0.14969 | -66.6911 | 56.2702 | 56.1151 | 56.207 | -66.8741 | -66.7291 | -0.10037 | -66.8323 | 56.0703 | 56.303 | 56.2559 | -66.9828 | -0.11847 | -0.075978 | 2.261 | 0.064611 | 0.18308 | -0.23105 | -0.13918 | -0.22715 | -0.27578 | 0.026606 | -0.07658 | 0.15057 | -0.043084 | -0.090247 | 123.0258 | 122.8708 | 122.9626 | 66.606 | -123.2203 | 122.826 | 123.0587 | 123.0116 | 66.6553 | -123.329
191.9375 | 123.2025 | -66.7465 | 56.3599 | 0.063697 | -0.013784 | -0.0014454 | 0.054339 | -0.0044619 | 0.054276 | 0.056499 | -0.0034662 | -0.0027965 | 0.061145 | 0.018581 | 0.061208 | -64.4993 | -0.14511 | -66.6911 | 56.2747 | 56.1105 | 56.1978 | -66.8741 | -66.7291 | -0.11411 | -66.8368 | 56.0658 | 56.303 | 56.2559 | -66.9874 | -0.12762 | -0.085132 | 2.2472 | 0.055456 | 0.18308 | -0.24936 | -0.16207 | -0.24089 | -0.29409 | 0.017451 | -0.090313 | 0.15057 | -0.056817 | -0.10398 | 123.0213 | 122.857 | 122.9443 | 66.6014 | -123.234 | 122.8123 | 123.0496 | 123.0024 | 66.6324 | -123.3473
192.9375 | 123.2391 | -66.7511 | 56.337 | 0.033173 | -0.011648 | -0.0014454 | 0.054339 | -0.0044619 | 0.053208 | 0.07176 | -0.0034662 | -0.0017285 | 0.059009 | 0.01965 | 0.06014 | -64.5039 | -0.168 | -66.6911 | 56.2702 | 56.1105 | 56.207 | -66.8741 | -66.7153 | -0.10495 | -66.8368 | 56.0703 | 56.2985 | 56.2513 | -66.9828 | -0.12305 | -0.066823 | 2.2472 | 0.060034 | 0.18308 | -0.22648 | -0.13002 | -0.23173 | -0.26663 | 0.035765 | -0.085735 | 0.14599 | -0.038508 | -0.085671 | 123.0213 | 122.8616 | 122.9581 | 66.5831 | -123.2111 | 122.8214 | 123.0496 | 123.0024 | 66.6461 | -123.3198
193.9375 | 123.2437 | -66.7557 | 56.3507 | 0.048435 | -0.013784 | -0.0025134 | 0.054339 | -0.0023249 | 0.053208 | 0.056499 | -0.0034662 | -0.0017285 | 0.061145 | 0.017513 | 0.062276 | -64.5039 | -0.168 | -66.6956 | 56.2793 | 56.1105 | 56.2024 | -66.8787 | -66.7245 | -0.12327 | -66.8414 | 56.0658 | 56.2939 | 56.2605 | -66.9782 | -0.12305 | -0.071399 | 2.2518 | 0.060032 | 0.18308 | -0.24021 | -0.14833 | -0.22257 | -0.28494 | 0.031185 | -0.085737 | 0.13684 | -0.056819 | -0.090247 | 123.035 | 122.8662 | 122.9581 | 66.5877 | -123.2294 | 122.8214 | 123.0496 | 123.0161 | 66.6324 | -123.329
194.9375 | 123.1934 | -66.7557 | 56.369 | 0.048435 | -0.013784 | -0.00037739 | 0.054339 | -0.0044619 | 0.05214 | 0.087021 | -0.0034662 | -0.0017285 | 0.061145 | 0.01965 | 0.062276 | -64.513 | -0.18632 | -66.6956 | 56.2656 | 56.1197 | 56.2024 | -66.8741 | -66.7336 | -0.13242 | -66.8414 | 56.0658 | 56.303 | 56.2559 | -66.992 | -0.11847 | -0.10345 | 2.2427 | 0.060032 | 0.1785 | -0.24936 | -0.16664 | -0.23631 | -0.30325 | 0.022027 | -0.085737 | 0.15057 | -0.065973 | -0.11314 | 123.0212 | 122.8753 | 122.9581 | 66.5694 | -123.2432 | 122.8214 | 123.0587 | 123.0116 | 66.6233 | -123.361
195.9375 | 123.23 | -66.7557 | 56.3507 | 0.063697 | -0.013784 | -0.0014454 | 0.055407 | -0.0023249 | 0.053208 | 0.087021 | -0.0023982 | -0.00065947 | 0.061145 | 0.01965 | 0.06014 | -64.5222 | -0.1909 | -66.6956 | 56.2702 | 56.1197 | 56.1978 | -66.8741 | -66.7336 | -0.137 | -66.8368 | 56.0703 | 56.2985 | 56.2376 | -66.9874 | -0.11847 | -0.080556 | 2.2335 | 0.060032 | 0.1785 | -0.23105 | -0.15291 | -0.23173 | -0.28036 | 0.022027 | -0.081158 | 0.15057 | -0.052241 | -0.11314 | 123.0258 | 122.8753 | 122.9535 | 66.5648 | -123.2249 | 122.826 | 123.0541 | 122.9932 | 66.6187 | -123.3381
196.9375 | 123.1567 | -66.7648 | 56.3324 | 0.063697 | -0.014853 | -0.0025134 | 0.054339 | -0.0033929 | 0.053208 | 0.10228 | -0.0045342 | -0.0038645 | 0.061145 | 0.020718 | 0.059071 | -64.513 | -0.20463 | -66.6956 | 56.2747 | 56.1151 | 56.207 | -66.8833 | -66.7199 | -0.14616 | -66.8368 | 56.0658 | 56.3076 | 56.265 | -66.9782 | -0.11847 | -0.057666 | 2.2518 | 0.069188 | 0.18766 | -0.21732 | -0.12544 | -0.21342 | -0.26663 | 0.04492 | -0.072002 | 0.14142 | -0.024773 | -0.067357 | 123.0396 | 122.8799 | 122.9718 | 66.5602 | -123.2157 | 122.8306 | 123.0725 | 123.0299 | 66.6187 | -123.3106
197.9375 | 123.2208 | -66.7419 | 56.337 | 0.048435 | -0.015921 | -0.0014454 | 0.053271 | -0.0023249 | 0.053208 | 0.07176 | -0.0023982 | -0.0027965 | 0.061145 | 0.020718 | 0.06014 | -64.5176 | -0.20463 | -66.6911 | 56.2702 | 56.1151 | 56.207 | -66.8696 | -66.7199 | -0.15074 | -66.8277 | 56.0658 | 56.3122 | 56.2513 | -66.9874 | -0.12762 | -0.066823 | 2.2243 | 0.050878 | 0.1785 | -0.2219 | -0.13002 | -0.24546 | -0.27121 | 0.022031 | -0.085734 | 0.15973 | -0.024772 | -0.085671 | 123.0121 | 122.857 | 122.9489 | 66.5373 | -123.2065 | 122.8077 | 123.0541 | 122.9932 | 66.5912 | -123.3244
198.9375 | 123.2117 | -66.7236 | 56.3599 | 0.063697 | -0.013784 | -0.00037739 | 0.053271 | -0.0033929 | 0.053208 | 0.056499 | -0.0034662 | -0.0027965 | 0.063282 | 0.017513 | 0.06014 | -64.5268 | -0.20921 | -66.6911 | 56.2747 | 56.1197 | 56.2115 | -66.8696 | -66.7199 | -0.1599 | -66.8323 | 56.0658 | 56.3168 | 56.2605 | -66.9874 | -0.14593 | -0.085132 | 2.1969 | 0.032568 | 0.1785 | -0.2402 | -0.14833 | -0.26377 | -0.29409 | 0.003721 | -0.10862 | 0.15515 | -0.043081 | -0.099402 | 122.9984 | 122.8433 | 122.9352 | 66.5144 | -123.2294 | 122.7894 | 123.0404 | 122.9841 | 66.5637 | -123.3473
199.9375 | 123.1064 | -66.7282 | 56.3416 | 0.078959 | -0.016989 | -0.00037739 | 0.055407 | -0.0055299 | 0.051071 | 0.07176 | -0.0034662 | -0.0017285 | 0.062214 | 0.01965 | 0.06014 | -64.5176 | -0.22295 | -66.6956 | 56.2747 | 56.1151 | 56.2024 | -66.8741 | -66.7245 | -0.16905 | -66.8368 | 56.0749 | 56.2985 | 56.2238 | -66.9874 | -0.14593 | -0.066822 | 2.2106 | 0.032566 | 0.1785 | -0.22647 | -0.13918 | -0.2592 | -0.26663 | 0.003719 | -0.10862 | 0.15057 | -0.043086 | -0.11772 | 123.0029 | 122.8433 | 122.9306 | 66.5053 | -123.2157 | 122.8031 | 123.0267 | 122.952 | 66.5592 | -123.329
200.9375 | 123.1842 | -66.7648 | 56.337 | 0.048435 | -0.013784 | -0.0025134 | 0.055407 | -0.0044619 | 0.053208 | 0.087021 | -0.0034662 | -0.0038645 | 0.060077 | 0.020718 | 0.06014 | -64.5222 | -0.24584 | -66.6911 | 56.2702 | 56.1151 | 56.207 | -66.8741 | -66.7245 | -0.18279 | -66.8323 | 56.0703 | 56.3122 | 56.2421 | -66.9828 | -0.10931 | -0.066823 | 2.2427 | 0.073767 | 0.18308 | -0.2219 | -0.13002 | -0.218 | -0.26663 | 0.040341 | -0.067424 | 0.15057 | -0.024772 | -0.094828 | 123.035 | 122.8799 | 122.9718 | 66.519 | -123.2111 | 122.8352 | 123.077 | 123.007 | 66.582 | -123.3198
201.9375 | 123.3078 | -66.7191 | 56.3004 | 0.078959 | -0.015921 | 0.00069161 | 0.053271 | -0.0033929 | 0.054276 | 0.041238 | -0.0023982 | -0.0017285 | 0.063282 | 0.01965 | 0.06014 | -64.5451 | -0.255 | -66.6911 | 56.2747 | 56.1197 | 56.207 | -66.8741 | -66.7199 | -0.18279 | -66.8231 | 56.0749 | 56.3076 | 56.2467 | -66.9828 | -0.15509 | -0.025623 | 2.174 | 0.02799 | 0.18308 | -0.1807 | -0.0934 | -0.26377 | -0.22543 | -0.000857 | -0.10404 | 0.15973 | 0.00727 | -0.053629 | 122.9938 | 122.8387 | 122.926 | 66.4641 | -123.1745 | 122.794 | 123.0267 | 122.9658 | 66.5363 | -123.2832
202.9375 | 123.3307 | -66.7145 | 56.3004 | 0.063697 | -0.015921 | -0.0025134 | 0.054339 | -0.0044619 | 0.05214 | 0.07176 | -0.0023982 | -0.0027965 | 0.062214 | 0.020718 | 0.06014 | -64.5542 | -0.25042 | -66.6956 | 56.2747 | 56.1151 | 56.2161 | -66.8696 | -66.7291 | -0.19653 | -66.8323 | 56.0795 | 56.303 | 56.2559 | -66.9828 | -0.15509 | -0.025623 | 2.1603 | 0.018834 | 0.17392 | -0.18527 | -0.084243 | -0.26835 | -0.22085 | -0.014592 | -0.11778 | 0.15057 | 0.002692 | -0.044471 | 122.9892 | 122.8296 | 122.9306 | 66.4641 | -123.1699 | 122.794 | 123.0175 | 122.9704 | 66.518 | -123.2832
203.9375 | 123.2803 | -66.7145 | 56.3232 | 0.048435 | -0.015921 | -0.00037739 | 0.053271 | -0.0033929 | 0.05214 | 0.087021 | -0.0034662 | -0.0027965 | 0.062214 | 0.01965 | 0.06014 | -64.5313 | -0.255 | -66.6911 | 56.2656 | 56.1197 | 56.2024 | -66.8696 | -66.7199 | -0.21026 | -66.8277 | 56.0795 | 56.303 | 56.2147 | -66.9874 | -0.15509 | -0.057668 | 2.1831 | 0.023413 | 0.1785 | -0.20358 | -0.12087 | -0.27293 | -0.24374 | -0.005434 | -0.1132 | 0.15973 | -0.020196 | -0.10857 | 122.9801 | 122.8341 | 122.9169 | 66.4595 | -123.1928 | 122.794 | 123.0175 | 122.9292 | 66.5042 | -123.3106
204.9375 | 123.2803 | -66.7145 | 56.3049 | 0.048435 | -0.016989 | -0.0014454 | 0.055407 | -0.0044619 | 0.05214 | 0.087021 | -0.0034662 | -0.0027965 | 0.061145 | 0.021786 | 0.059071 | -64.5588 | -0.27789 | -66.7002 | 56.2747 | 56.1242 | 56.2161 | -66.8696 | -66.7245 | -0.21484 | -66.8277 | 56.0749 | 56.3076 | 56.2421 | -66.9737 | -0.15509 | -0.030201 | 2.1557 | 0.014256 | 0.16934 | -0.1807 | -0.088821 | -0.25919 | -0.23001 | -0.010013 | -0.1132 | 0.14599 | 0.002692 | -0.062785 | 122.9892 | 122.8387 | 122.9306 | 66.4366 | -123.1745 | 122.7894 | 123.0221 | 122.9566 | 66.4996 | -123.2786
205.9375 | 123.3032 | -66.7007 | 56.3095 | 0.078959 | -0.016989 | -0.0025134 | 0.053271 | -0.0033929 | 0.053208 | 0.087021 | -0.0034662 | -0.0017285 | 0.062214 | 0.020718 | 0.059071 | -64.5542 | -0.28247 | -66.6956 | 56.2656 | 56.1242 | 56.2161 | -66.8741 | -66.7291 | -0.224 | -66.8277 | 56.0795 | 56.3122 | 56.2376 | -66.9782 | -0.1734 | -0.043935 | 2.1465 | 0.005101 | 0.1785 | -0.18527 | -0.093398 | -0.2775 | -0.23 | -0.028325 | -0.12693 | 0.15057 | 0.002694 | -0.071941 | 122.9663 | 122.825 | 122.9169 | 66.4183 | -123.1837 | 122.7802 | 123.0129 | 122.9383 | 66.4767 | -123.2878
206.9375 | 123.2758 | -66.7328 | 56.3278 | 0.048435 | -0.014853 | -0.0014454 | 0.053271 | -0.0023249 | 0.054276 | 0.07176 | -0.0045342 | -0.0017285 | 0.060077 | 0.021786 | 0.061208 | -64.5405 | -0.30078 | -66.6911 | 56.2747 | 56.1151 | 56.2161 | -66.8741 | -66.7245 | -0.23316 | -66.8231 | 56.0749 | 56.3076 | 56.265 | -66.9874 | -0.14136 | -0.053089 | 2.1923 | 0.041723 | 0.18308 | -0.21274 | -0.11171 | -0.25462 | -0.25289 | 0.008297 | -0.09031 | 0.16431 | -0.020196 | -0.06278 | 123.0075 | 122.8479 | 122.9489 | 66.432 | -123.202 | 122.8077 | 123.0404 | 122.9978 | 66.4996 | -123.3152
207.9375 | 123.3078 | -66.7145 | 56.3324 | 0.063697 | -0.015921 | -0.0014454 | 0.054339 | -0.0023249 | 0.053208 | 0.056499 | -0.0034662 | -0.0017285 | 0.059009 | 0.018581 | 0.06014 | -64.5451 | -0.30994 | -66.7002 | 56.2747 | 56.1197 | 56.2115 | -66.8741 | -66.7245 | -0.24689 | -66.8368 | 56.0795 | 56.3122 | 56.2559 | -66.9874 | -0.15967 | -0.057666 | 2.1694 | 0.014256 | 0.17392 | -0.21274 | -0.12087 | -0.27293 | -0.25289 | -0.010013 | -0.12236 | 0.15057 | -0.020194 | -0.076514 | 122.9892 | 122.8341 | 122.926 | 66.4045 | -123.2065 | 122.794 | 123.0267 | 122.9704 | 66.4676 | -123.3198
208.9375 | 123.2941 | -66.7328 | 56.2775 | 0.048435 | -0.015921 | -0.0014454 | 0.053271 | -0.0033929 | 0.055345 | 0.056499 | -0.0023982 | -0.0027965 | 0.062214 | 0.020718 | 0.059071 | -64.5817 | -0.32367 | -66.7002 | 56.2747 | 56.1197 | 56.2115 | -66.8696 | -66.7245 | -0.26063 | -66.8231 | 56.0841 | 56.3122 | 56.2376 | -66.9737 | -0.13678 | -0.002735 | 2.1511 | 0.032566 | 0.16934 | -0.15781 | -0.065934 | -0.24088 | -0.19338 | 0.008297 | -0.09031 | 0.15057 | 0.034737 | -0.039898 | 123.0075 | 122.8524 | 122.9443 | 66.4091 | -123.147 | 122.8169 | 123.045 | 122.9704 | 66.4722 | -123.2511
209.9375 | 123.1842 | -66.806 | 56.3278 | 0.048435 | -0.018058 | -0.0025134 | 0.054339 | -0.0044619 | 0.051071 | 0.087021 | -0.0034662 | -0.0017285 | 0.061145 | 0.01965 | 0.059071 | -64.513 | -0.32825 | -66.6956 | 56.2747 | 56.1288 | 56.2115 | -66.8741 | -66.7153 | -0.26978 | -66.8277 | 56.0795 | 56.3076 | 56.265 | -66.9782 | -0.068115 | -0.053089 | 2.293 | 0.11039 | 0.1785 | -0.199 | -0.11629 | -0.17222 | -0.24832 | 0.090696 | -0.021647 | 0.15057 | -0.020196 | -0.06278 | 123.0808 | 122.9348 | 123.0176 | 66.4778 | -123.202 | 122.8855 | 123.1137 | 123.0711 | 66.5362 | -123.3061
210.9375 | 123.3307 | -66.7007 | 56.3187 | 0.078959 | -0.014853 | -0.00037739 | 0.052202 | -0.0033929 | 0.054276 | 0.056499 | -0.0034662 | -0.0027965 | 0.062214 | 0.01965 | 0.059071 | -64.5542 | -0.34657 | -66.6911 | 56.2793 | 56.1242 | 56.2115 | -66.8696 | -66.7153 | -0.2881 | -66.8231 | 56.0795 | 56.3168 | 56.2605 | -66.9874 | -0.16882 | -0.039356 | 2.1465 | 0.00968 | 0.1785 | -0.19443 | -0.10713 | -0.28666 | -0.23916 | -0.014589 | -0.12235 | 0.16431 | -0.001883 | -0.058204 | 122.9801 | 122.825 | 122.9123 | 66.3542 | -123.1882 | 122.7802 | 123.0175 | 122.9612 | 66.4126 | -123.3061
211.9531 | 123.1796 | -66.7694 | 56.3095 | 0.063697 | -0.016989 | -0.0014454 | 0.054339 | -0.0044619 | 0.053208 | 0.07176 | -0.0034662 | -0.0027965 | 0.061145 | 0.01965 | 0.061208 | -64.4993 | -0.36946 | -66.6911 | 56.2793 | 56.1197 | 56.2161 | -66.8696 | -66.7153 | -0.29726 | -66.8231 | 56.0795 | 56.3076 | 56.2238 | -66.9782 | -0.10016 | -0.0302 | 2.2701 | 0.078344 | 0.1785 | -0.18985 | -0.093398 | -0.20884 | -0.23 | 0.054075 | -0.053689 | 0.15515 | -0.001885 | -0.085677 | 123.0487 | 122.8891 | 122.9855 | 66.3999 | -123.1791 | 122.8489 | 123.077 | 122.9932 | 66.4722 | -123.2878
212.9375 | 123.3032 | -66.7053 | 56.3141 | 0.063697 | -0.015921 | 0.00069161 | 0.054339 | -0.0044619 | 0.053208 | 0.087021 | -0.0045342 | -0.0038645 | 0.057941 | 0.022855 | 0.06014 | -64.5405 | -0.3832 | -66.6911 | 56.2747 | 56.1242 | 56.2161 | -66.8741 | -66.7153 | -0.31099 | -66.8277 | 56.0749 | 56.3122 | 56.2376 | -66.9782 | -0.16882 | -0.039356 | 2.1648 | 0.014257 | 0.18308 | -0.18985 | -0.097976 | -0.27293 | -0.23916 | -0.010012 | -0.12235 | 0.15057 | -0.001884 | -0.076519 | 122.9801 | 122.8296 | 122.9214 | 66.3221 | -123.1882 | 122.7802 | 123.0175 | 122.9429 | 66.3943 | -123.2923
213.9531 | 123.2529 | -66.7557 | 56.3278 | 0.094221 | -0.016989 | -0.0025134 | 0.053271 | -0.0033929 | 0.05214 | 0.056499 | -0.0034662 | -0.0038645 | 0.061145 | 0.01965 | 0.059071 | -64.4947 | -0.39693 | -66.6956 | 56.2747 | 56.1242 | 56.2207 | -66.8696 | -66.7153 | -0.32015 | -66.8185 | 56.0795 | 56.3122 | 56.2742 | -66.9828 | -0.11389 | -0.053089 | 2.261 | 0.060032 | 0.17392 | -0.20358 | -0.10713 | -0.22715 | -0.24832 | 0.040342 | -0.062843 | 0.16431 | -0.015617 | -0.053623 | 123.0304 | 122.8799 | 122.9764 | 66.3587 | -123.1974 | 122.8352 | 123.0679 | 123.0299 | 66.4355 | -123.3106
214.9375 | 123.3032 | -66.7007 | 56.3141 | 0.048435 | -0.016989 | -0.0014454 | 0.054339 | -0.0023249 | 0.05214 | 0.07176 | -0.0023982 | -0.0027965 | 0.060077 | 0.021786 | 0.062276 | -64.5496 | -0.41983 | -66.6911 | 56.2702 | 56.1242 | 56.2115 | -66.8741 | -66.7199 | -0.33389 | -66.8185 | 56.0841 | 56.303 | 56.265 | -66.9782 | -0.1734 | -0.043935 | 2.1511 | 0.00968 | 0.18308 | -0.18985 | -0.10256 | -0.2775 | -0.23 | -0.019167 | -0.11777 | 0.15973 | -0.011041 | -0.049047 | 122.9709 | 122.825 | 122.9123 | 66.2809 | -123.1882 | 122.7848 | 123.0038 | 122.9658 | 66.3669 | -123.2923
215.9375 | 123.3307 | -66.6824 | 56.3049 | 0.063697 | -0.015921 | 0.00069161 | 0.054339 | -0.0033929 | 0.05214 | 0.07176 | -0.0034662 | -0.0038645 | 0.061145 | 0.021786 | 0.06014 | -64.5908 | -0.43356 | -66.6819 | 56.2747 | 56.1197 | 56.2161 | -66.8696 | -66.7199 | -0.3522 | -66.8231 | 56.0841 | 56.3168 | 56.2193 | -66.9782 | -0.18713 | -0.030201 | 2.0916 | 0.000525 | 0.18766 | -0.18527 | -0.088821 | -0.29582 | -0.22085 | -0.037478 | -0.14066 | 0.15515 | 0.01185 | -0.085678 | 122.9572 | 122.8021 | 122.8985 | 66.2489 | -123.1745 | 122.7665 | 122.9992 | 122.9017 | 66.3302 | -123.2832
216.9531 | 123.3078 | -66.7191 | 56.2958 | 0.048435 | -0.016989 | -0.0014454 | 0.054339 | -0.0033929 | 0.05214 | 0.056499 | -0.0045342 | -0.0038645 | 0.061145 | 0.020718 | 0.062276 | -64.568 | -0.4473 | -66.6911 | 56.2747 | 56.1288 | 56.2207 | -66.865 | -66.7199 | -0.36136 | -66.8277 | 56.0841 | 56.3076 | 56.2421 | -66.9737 | -0.14593 | -0.021045 | 2.1511 | 0.02799 | 0.17392 | -0.16696 | -0.075086 | -0.25462 | -0.21169 | -0.000857 | -0.10862 | 0.14599 | 0.011848 | -0.053629 | 122.9938 | 122.8479 | 122.9397 | 66.2718 | -123.1608 | 122.8031 | 123.0267 | 122.9612 | 66.3577 | -123.2694
217.9375 | 123.5413 | -66.6687 | 56.3782 | 0.048435 | -0.014853 | 0.00069161 | 0.053271 | -0.0023249 | 0.053208 | 0.07176 | -0.0023982 | -0.0017285 | 0.062214 | 0.022855 | 0.059071 | -64.5817 | -0.47477 | -66.6819 | 56.2793 | 56.1334 | 56.2207 | -66.8696 | -66.7153 | -0.37967 | -66.8277 | 56.0841 | 56.3076 | 56.2605 | -66.9782 | -0.20087 | -0.098865 | 2.087 | -0.013208 | 0.18766 | -0.24478 | -0.15748 | -0.30955 | -0.29409 | -0.046633 | -0.15898 | 0.15057 | -0.07055 | -0.11771 | 122.948 | 122.8021 | 122.8894 | 66.1939 | -123.2477 | 122.7528 | 122.9763 | 122.9292 | 66.289 | -123.3564
218.9375 | 123.2437 | -66.7557 | 56.3278 | 0.063697 | -0.014853 | 0.00069161 | 0.054339 | -0.0023249 | 0.053208 | 0.056499 | -0.0034662 | -0.0017285 | 0.062214 | 0.020718 | 0.06014 | -64.5084 | -0.4885 | -66.6911 | 56.2747 | 56.1334 | 56.2161 | -66.8787 | -66.7108 | -0.36136 | -66.8231 | 56.0795 | 56.3168 | 56.2696 | -66.9828 | -0.12305 | -0.053089 | 2.2472 | 0.064611 | 0.18766 | -0.19443 | -0.11171 | -0.22715 | -0.24832 | 0.044921 | -0.067422 | 0.15973 | -0.011038 | -0.058202 | 123.0304 | 122.8891 | 122.9718 | 66.2672 | -123.2065 | 122.8352 | 123.0725 | 123.0253 | 66.3943 | -123.3106
219.9375 | 123.3307 | -66.7007 | 56.3232 | 0.078959 | -0.019126 | -0.0014454 | 0.054339 | -0.0033929 | 0.050003 | 0.087021 | -0.0045342 | -0.0027965 | 0.061145 | 0.021786 | 0.059071 | -64.5588 | -0.52513 | -66.6911 | 56.2793 | 56.1242 | 56.2253 | -66.865 | -66.7108 | -0.38883 | -66.8185 | 56.0749 | 56.3122 | 56.2605 | -66.9828 | -0.16424 | -0.043933 | 2.1419 | 0.00968 | 0.17392 | -0.199 | -0.097974 | -0.28208 | -0.24832 | -0.01001 | -0.11777 | 0.16431 | -0.011039 | -0.062781 | 122.9801 | 122.825 | 122.926 | 66.1756 | -123.1882 | 122.7757 | 123.0129 | 122.9612 | 66.3119 | -123.3061
220.9375 | 123.3078 | -66.7099 | 56.3095 | 0.078959 | -0.018058 | -0.0014454 | 0.053271 | -0.0044619 | 0.050003 | 0.056499 | -0.0023982 | -0.0027965 | 0.061145 | 0.01965 | 0.06014 | -64.5588 | -0.54345 | -66.6911 | 56.2793 | 56.138 | 56.2207 | -66.865 | -66.7199 | -0.40715 | -66.8231 | 56.0841 | 56.3076 | 56.2696 | -66.9828 | -0.15509 | -0.0302 | 2.1511 | 0.018835 | 0.17392 | -0.17153 | -0.088819 | -0.27293 | -0.22543 | -0.010012 | -0.1132 | 0.15973 | -0.001885 | -0.039891 | 122.9892 | 122.8479 | 122.9306 | 66.1665 | -123.1745 | 122.794 | 123.0175 | 122.9795 | 66.3028 | -123.2923
221.9375 | 123.175 | -66.774 | 56.3187 | 0.048435 | -0.015921 | -0.00037739 | 0.053271 | -0.0033929 | 0.05214 | 0.056499 | -0.0045342 | -0.00065947 | 0.060077 | 0.021786 | 0.059071 | -64.5222 | -0.55718 | -66.6865 | 56.2839 | 56.1242 | 56.2207 | -66.865 | -66.7016 | -0.42088 | -66.8231 | 56.0795 | 56.3076 | 56.265 | -66.9828 | -0.091 | -0.034778 | 2.2518 | 0.0875 | 0.1785 | -0.19443 | -0.097975 | -0.20884 | -0.23916 | 0.072389 | -0.049111 | 0.15973 | -0.011041 | -0.053625 | 123.0579 | 122.8982 | 122.9947 | 66.2168 | -123.1837 | 122.8535 | 123.0816 | 123.039 | 66.3531 | -123.3015
222.9375 | 123.3353 | -66.7007 | 56.3416 | 0.048435 | -0.016989 | -0.0025134 | 0.052202 | -0.0033929 | 0.05214 | 0.07176 | -0.0045342 | -0.0027965 | 0.061145 | 0.020718 | 0.059071 | -64.5908 | -0.58923 | -66.6819 | 56.2793 | 56.1334 | 56.2161 | -66.8604 | -66.7108 | -0.43462 | -66.8323 | 56.0795 | 56.3122 | 56.2284 | -66.9782 | -0.15966 | -0.062244 | 2.1099 | 0.018836 | 0.1785 | -0.20816 | -0.12544 | -0.2775 | -0.26205 | -0.01001 | -0.13151 | 0.14599 | -0.02935 | -0.11314 | 122.9801 | 122.8341 | 122.9169 | 66.1115 | -123.202 | 122.7802 | 123.0129 | 122.9292 | 66.2661 | -123.3198
223.9531 | 123.23 | -66.7236 | 56.3232 | 0.048435 | -0.016989 | -0.00037739 | 0.053271 | -0.0033929 | 0.05214 | 0.07176 | -0.0034662 | -0.0027965 | 0.061145 | 0.022855 | 0.06014 | -64.4855 | -0.61213 | -66.6865 | 56.2793 | 56.1288 | 56.2298 | -66.8741 | -66.7108 | -0.44836 | -66.8277 | 56.0841 | 56.3122 | 56.2696 | -66.9782 | -0.15051 | -0.043933 | 2.2381 | 0.037146 | 0.18766 | -0.19443 | -0.093395 | -0.25462 | -0.23916 | 0.012878 | -0.10404 | 0.15057 | -0.011039 | -0.053624 | 123.0029 | 122.8524 | 122.9535 | 66.1115 | -123.1974 | 122.8077 | 123.0358 | 122.9933 | 66.2753 | -123.3015
224.9375 | 123.3124 | -66.6916 | 56.3965 | 0.063697 | -0.016989 | 0.00069161 | 0.055407 | -0.0033929 | 0.05214 | 0.056499 | -0.0045342 | -0.0038645 | 0.060077 | 0.021786 | 0.06014 | -64.5588 | -0.64418 | -66.6819 | 56.2793 | 56.1242 | 56.2161 | -66.8604 | -66.7108 | -0.46667 | -66.8185 | 56.0841 | 56.3122 | 56.2605 | -66.9782 | -0.16882 | -0.11718 | 2.1328 | 0.00968 | 0.1785 | -0.27225 | -0.18037 | -0.28666 | -0.3124 | -0.019166 | -0.12693 | 0.15973 | -0.084281 | -0.13602 | 122.9709 | 122.8158 | 122.9077 | 66.0474 | -123.2569 | 122.7757 | 123.0038 | 122.952 | 66.2249 | -123.3747
225.9375 | 123.2437 | -66.7557 | 56.2958 | 0.033173 | -0.015921 | -0.0014454 | 0.054339 | -0.0044619 | 0.053208 | 0.056499 | -0.0023982 | -0.0027965 | 0.060077 | 0.023923 | 0.059071 | -64.5313 | -0.67165 | -66.6865 | 56.2839 | 56.1242 | 56.2253 | -66.865 | -66.7108 | -0.48041 | -66.8185 | 56.0795 | 56.3214 | 56.2605 | -66.9691 | -0.10931 | -0.011889 | 2.2243 | 0.069189 | 0.1785 | -0.17154 | -0.070508 | -0.21342 | -0.21627 | 0.044921 | -0.062843 | 0.15057 | 0.025584 | -0.035315 | 123.0396 | 122.8799 | 122.9809 | 66.084 | -123.1608 | 122.8352 | 123.077 | 123.0161 | 66.2753 | -123.2649
226.9375 | 123.3307 | -66.7053 | 56.3232 | 0.094221 | -0.016989 | -0.0035824 | 0.056476 | -0.0044619 | 0.053208 | 0.07176 | -0.0034662 | -0.0017285 | 0.059009 | 0.021786 | 0.059071 | -64.5496 | -0.7037 | -66.6865 | 56.2747 | 56.1334 | 56.2253 | -66.865 | -66.7108 | -0.51246 | -66.8277 | 56.0841 | 56.3122 | 56.265 | -66.9782 | -0.15967 | -0.048511 | 2.1557 | 0.018835 | 0.1785 | -0.18985 | -0.097974 | -0.27293 | -0.23916 | -0.005433 | -0.12235 | 0.15057 | -0.011039 | -0.058202 | 122.9801 | 122.8387 | 122.9306 | 66.0016 | -123.1882 | 122.7894 | 123.0175 | 122.9704 | 66.1929 | -123.3015
227.9531 | 123.3032 | -66.7099 | 56.3049 | 0.017911 | -0.016989 | -0.0014454 | 0.053271 | -0.0033929 | 0.051071 | 0.07176 | -0.0034662 | -0.0027965 | 0.059009 | 0.022855 | 0.059071 | -64.5863 | -0.73575 | -66.6865 | 56.2885 | 56.1288 | 56.2207 | -66.8558 | -66.7062 | -0.52619 | -66.8185 | 56.0795 | 56.3214 | 56.265 | -66.9737 | -0.14593 | -0.016466 | 2.1236 | 0.023413 | 0.16934 | -0.17612 | -0.084242 | -0.26377 | -0.22543 | 0.003724 | -0.10862 | 0.15515 | 0.016428 | -0.039892 | 122.9984 | 122.8387 | 122.9306 | 65.9742 | -123.1608 | 122.7894 | 123.0313 | 122.9749 | 66.1837 | -123.2786
228.9375 | 123.2529 | -66.7465 | 56.369 | 0.078959 | -0.019126 | -0.0014454 | 0.055407 | -0.0033929 | 0.05214 | 0.056499 | -0.0034662 | -0.0038645 | 0.057941 | 0.021786 | 0.059071 | -64.4993 | -0.77696 | -66.6773 | 56.2885 | 56.138 | 56.2298 | -66.8696 | -66.7016 | -0.54909 | -66.8185 | 56.0887 | 56.3214 | 56.2742 | -66.9782 | -0.12305 | -0.080553 | 2.2472 | 0.06919 | 0.19224 | -0.23105 | -0.13917 | -0.23173 | -0.28036 | 0.044923 | -0.071998 | 0.15973 | -0.047659 | -0.094822 | 123.035 | 122.8845 | 122.9764 | 65.9696 | -123.2386 | 122.8352 | 123.0679 | 123.0207 | 66.1974 | -123.3473
229.9375 | 123.3582 | -66.6779 | 56.3324 | 0.078959 | -0.018058 | -0.0014454 | 0.055407 | -0.0033929 | 0.05214 | 0.087021 | -0.0045342 | -0.0038645 | 0.060077 | 0.023923 | 0.059071 | -64.5725 | -0.80443 | -66.6819 | 56.2839 | 56.1334 | 56.2253 | -66.8558 | -66.7062 | -0.57656 | -66.8139 | 56.0887 | 56.3214 | 56.2284 | -66.9828 | -0.17797 | -0.04851 | 2.1053 | -0.004053 | 0.17392 | -0.199 | -0.10713 | -0.30497 | -0.24374 | -0.02832 | -0.13608 | 0.16889 | -0.011037 | -0.10399 | 122.9617 | 122.8113 | 122.9031 | 65.8734 | -123.1882 | 122.7665 | 122.9992 | 122.9063 | 66.1013 | -123.3152
230.9375 | 123.3536 | -66.7007 | 56.3232 | 0.078959 | -0.020194 | -0.0014454 | 0.054339 | -0.0044619 | 0.053208 | 0.056499 | -0.0045342 | -0.0017285 | 0.061145 | 0.023923 | 0.06014 | -64.5588 | -0.85021 | -66.6819 | 56.2885 | 56.1426 | 56.2253 | -66.8604 | -66.7062 | -0.60403 | -66.8139 | 56.0887 | 56.3168 | 56.265 | -66.9828 | -0.15966 | -0.034776 | 2.1419 | 0.018836 | 0.1785 | -0.18069 | -0.097974 | -0.28208 | -0.23458 | -0.005431 | -0.1132 | 0.16889 | -0.00646 | -0.058202 | 122.9892 | 122.8433 | 122.926 | 65.8505 | -123.1837 | 122.7894 | 123.0175 | 122.9658 | 66.0967 | -123.3061
231.9375 | 123.4085 | -66.6595 | 56.369 | 0.063697 | -0.018058 | -0.0025134 | 0.054339 | -0.0044619 | 0.051071 | 0.056499 | -0.0023982 | -0.0017285 | 0.060077 | 0.023923 | 0.059071 | -64.5542 | -0.88226 | -66.6773 | 56.2885 | 56.1334 | 56.2161 | -66.8604 | -66.7062 | -0.62235 | -66.8139 | 56.0887 | 56.3076 | 56.2742 | -66.9737 | -0.20086 | -0.080553 | 2.1053 | -0.017785 | 0.18308 | -0.23562 | -0.15291 | -0.31412 | -0.28036 | -0.04663 | -0.15439 | 0.15973 | -0.061395 | -0.094822 | 122.948 | 122.7929 | 122.8757 | 65.7773 | -123.2294 | 122.7482 | 122.9672 | 122.9337 | 66.0372 | -123.3427
232.9531 | 123.2803 | -66.7374 | 56.2866 | 0.078959 | -0.019126 | 0.00069161 | 0.053271 | -0.0065979 | 0.053208 | 0.056499 | -0.0056032 | -0.0038645 | 0.059009 | 0.024992 | 0.06014 | -64.5817 | -0.92805 | -66.6728 | 56.2839 | 56.138 | 56.2207 | -66.865 | -66.7062 | -0.64982 | -66.8139 | 56.0841 | 56.3214 | 56.2696 | -66.9782 | -0.12762 | -0.002734 | 2.1557 | 0.064614 | 0.19223 | -0.14865 | -0.065931 | -0.24088 | -0.20254 | 0.03119 | -0.076575 | 0.16431 | 0.034739 | -0.017003 | 123.0213 | 122.8753 | 122.9581 | 65.8093 | -123.1516 | 122.8214 | 123.0587 | 123.007 | 66.0875 | -123.2649
233.9375 | 123.1888 | -66.7557 | 56.3599 | 0.048435 | -0.019126 | -0.0014454 | 0.052202 | -0.0055299 | 0.05214 | 0.056499 | -0.0034662 | -0.0038645 | 0.057941 | 0.024992 | 0.061208 | -64.4855 | -0.9601 | -66.6819 | 56.293 | 56.138 | 56.2253 | -66.8604 | -66.7016 | -0.67271 | -66.8048 | 56.0841 | 56.3168 | 56.2559 | -66.9737 | -0.10473 | -0.066819 | 2.2701 | 0.073767 | 0.1785 | -0.22189 | -0.13459 | -0.21799 | -0.27578 | 0.054078 | -0.049107 | 0.16889 | -0.043081 | -0.10398 | 123.0487 | 122.8936 | 122.9809 | 65.7956 | -123.2203 | 122.8398 | 123.0725 | 123.0116 | 66.083 | -123.3335
234.9375 | 123.3078 | -66.7007 | 56.3324 | 0.078959 | -0.019126 | -0.0014454 | 0.054339 | -0.0044619 | 0.054276 | 0.056499 | -0.0056032 | -0.0038645 | 0.059009 | 0.022855 | 0.058003 | -64.5359 | -1.0059 | -66.6728 | 56.2839 | 56.1426 | 56.2298 | -66.8558 | -66.697 | -0.70934 | -66.8094 | 56.0841 | 56.3122 | 56.2788 | -66.9737 | -0.15508 | -0.04851 | 2.1648 | 0.027993 | 0.18308 | -0.18984 | -0.10255 | -0.27293 | -0.24831 | 0.003726 | -0.10862 | 0.16431 | -0.020194 | -0.053621 | 122.9846 | 122.8433 | 122.9306 | 65.6949 | -123.1882 | 122.7848 | 123.0129 | 122.9795 | 65.9914 | -123.3061
235.9375 | 123.3719 | -66.6962 | 56.3141 | 0.078959 | -0.018058 | -0.00037739 | 0.053271 | -0.0055299 | 0.053208 | 0.087021 | -0.0023982 | -0.0027965 | 0.060077 | 0.023923 | 0.059071 | -64.5451 | -1.0517 | -66.6819 | 56.2885 | 56.138 | 56.2298 | -66.865 | -66.697 | -0.72766 | -66.8094 | 56.0795 | 56.3168 | 56.2696 | -66.9691 | -0.16882 | -0.025621 | 2.1511 | 0.014258 | 0.18308 | -0.17611 | -0.08424 | -0.27293 | -0.23458 | -0.000852 | -0.11319 | 0.15973 | 0.002695 | -0.044469 | 122.9846 | 122.8341 | 122.926 | 65.6445 | -123.1791 | 122.7757 | 123.0129 | 122.9658 | 65.9685 | -123.2832
236.9375 | 123.3353 | -66.6916 | 56.3095 | 0.048435 | -0.018058 | -0.0014454 | 0.053271 | -0.0055299 | 0.05214 | 0.056499 | -0.0056032 | -0.0038645 | 0.060077 | 0.02606 | 0.06014 | -64.5725 | -1.0883 | -66.6728 | 56.2885 | 56.1334 | 56.2344 | -66.8604 | -66.697 | -0.75971 | -66.8094 | 56.0795 | 56.3305 | 56.2788 | -66.9828 | -0.16882 | -0.021043 | 2.1191 | 0.018837 | 0.18766 | -0.17611 | -0.075084 | -0.29124 | -0.23 | -0.00543 | -0.11777 | 0.17347 | 0.021008 | -0.030733 | 122.9801 | 122.825 | 122.926 | 65.6033 | -123.1699 | 122.7711 | 123.0221 | 122.9704 | 65.9319 | -123.2923
237.9531 | 123.2208 | -66.7236 | 56.3553 | 0.063697 | -0.020194 | -0.0014454 | 0.054339 | -0.0044619 | 0.05214 | 0.056499 | -0.0023982 | -0.0038645 | 0.059009 | 0.023923 | 0.059071 | -64.4993 | -1.1249 | -66.6773 | 56.293 | 56.1334 | 56.2298 | -66.8604 | -66.7016 | -0.79634 | -66.8139 | 56.0841 | 56.3168 | 56.2559 | -66.9691 | -0.13678 | -0.062242 | 2.2244 | 0.046302 | 0.18308 | -0.22189 | -0.12544 | -0.24546 | -0.2712 | 0.022035 | -0.090308 | 0.15515 | -0.038504 | -0.099403 | 123.0167 | 122.857 | 122.9535 | 65.5987 | -123.2157 | 122.8077 | 123.0404 | 122.9795 | 65.9273 | -123.3244
238.9375 | 123.3444 | -66.687 | 56.3324 | 0.078959 | -0.019126 | -0.0025134 | 0.054339 | -0.0055299 | 0.05214 | 0.056499 | -0.0034662 | -0.0038645 | 0.060077 | 0.024992 | 0.059071 | -64.5451 | -1.1845 | -66.6682 | 56.2885 | 56.138 | 56.2298 | -66.8604 | -66.6924 | -0.83754 | -66.8048 | 56.0887 | 56.3168 | 56.2696 | -66.9691 | -0.1734 | -0.043931 | 2.1419 | 0.018838 | 0.19223 | -0.19442 | -0.10255 | -0.28208 | -0.24374 | -0.005428 | -0.11777 | 0.16431 | -0.015615 | -0.062779 | 122.9755 | 122.825 | 122.9169 | 65.5026 | -123.1928 | 122.7757 | 123.0038 | 122.9566 | 65.8495 | -123.3015
239.9375 | 123.349 | -66.6824 | 56.3187 | 0.063697 | -0.019126 | -0.0025134 | 0.051134 | -0.0044619 | 0.051071 | 0.056499 | -0.0045342 | -0.0017285 | 0.060077 | 0.023923 | 0.059071 | -64.5542 | -1.2257 | -66.6636 | 56.293 | 56.1334 | 56.2298 | -66.8558 | -66.7016 | -0.85586 | -66.8094 | 56.0932 | 56.3259 | 56.2696 | -66.9691 | -0.1734 | -0.025621 | 2.1282 | 0.018838 | 0.19223 | -0.18527 | -0.088818 | -0.28666 | -0.22543 | -0.019164 | -0.12693 | 0.15973 | 0.007274 | -0.049047 | 122.9755 | 122.8158 | 122.9123 | 65.4568 | -123.1745 | 122.7757 | 123.0084 | 122.9521 | 65.8266 | -123.2878
240.9531 | 123.3444 | -66.6733 | 56.3232 | 0.048435 | -0.018058 | -0.00037739 | 0.051134 | -0.0033929 | 0.053208 | 0.056499 | -0.0045342 | -0.0017285 | 0.060077 | 0.023923 | 0.056935 | -64.5542 | -1.276 | -66.659 | 56.293 | 56.138 | 56.2344 | -66.8513 | -66.697 | -0.89249 | -66.8048 | 56.0887 | 56.3214 | 56.2742 | -66.9782 | -0.17797 | -0.030198 | 2.1191 | 0.014262 | 0.19223 | -0.18527 | -0.088817 | -0.30497 | -0.23458 | -0.02374 | -0.1315 | 0.17347 | -0.001882 | -0.049045 | 122.9663 | 122.8113 | 122.9077 | 65.3973 | -123.1745 | 122.7619 | 122.9946 | 122.9475 | 65.7808 | -123.3015
241.9375 | 123.3902 | -66.6412 | 56.3644 | 0.048435 | -0.016989 | -0.0035824 | 0.053271 | -0.0044619 | 0.054276 | 0.07176 | -0.0056032 | -0.0017285 | 0.060077 | 0.024992 | 0.059071 | -64.5451 | -1.3264 | -66.6728 | 56.293 | 56.138 | 56.2344 | -66.8513 | -66.697 | -0.94285 | -66.8094 | 56.0978 | 56.3351 | 56.2605 | -66.9737 | -0.21002 | -0.071397 | 2.0962 | -0.031517 | 0.1785 | -0.22647 | -0.13002 | -0.33244 | -0.26662 | -0.055784 | -0.16813 | 0.16431 | -0.029345 | -0.10398 | 122.9343 | 122.7792 | 122.8757 | 65.3148 | -123.2157 | 122.7391 | 122.9763 | 122.9017 | 65.6984 | -123.3381
242.9531 | 123.2895 | -66.7099 | 56.2912 | 0.063697 | -0.020194 | -0.00037739 | 0.052202 | -0.0076669 | 0.051071 | 0.056499 | -0.0056032 | -0.0017285 | 0.060077 | 0.027128 | 0.058003 | -64.5542 | -1.3859 | -66.6636 | 56.2976 | 56.1426 | 56.2344 | -66.8513 | -66.697 | -0.98406 | -66.8094 | 56.0978 | 56.3259 | 56.2834 | -66.9599 | -0.14135 | 0.006424 | 2.1557 | 0.046304 | 0.18766 | -0.14865 | -0.056774 | -0.25003 | -0.19338 | 0.012881 | -0.099462 | 0.15057 | 0.03474 | -0.007845 | 123.0075 | 122.8525 | 122.9443 | 65.324 | -123.1424 | 122.8077 | 123.0358 | 122.9933 | 65.7258 | -123.2511
243.9375 | 123.2941 | -66.6779 | 56.3736 | 0.033173 | -0.019126 | -0.00037739 | 0.053271 | -0.0065979 | 0.05214 | 0.056499 | -0.0034662 | -0.0027965 | 0.060077 | 0.02606 | 0.06014 | -64.5634 | -1.4409 | -66.6636 | 56.2976 | 56.138 | 56.2298 | -66.8513 | -66.6879 | -1.0115 | -66.8002 | 56.0978 | 56.3259 | 56.2788 | -66.9737 | -0.17339 | -0.075973 | 2.1145 | 0.01426 | 0.18766 | -0.23562 | -0.14375 | -0.29581 | -0.27578 | -0.010005 | -0.12235 | 0.17346 | -0.047657 | -0.09482 | 122.9755 | 122.8158 | 122.9077 | 65.237 | -123.2248 | 122.7757 | 123.0038 | 122.9566 | 65.6663 | -123.3473
244.9375 | 123.3215 | -66.7007 | 56.3324 | 0.048435 | -0.021263 | -0.00037739 | 0.052202 | -0.0033929 | 0.051071 | 0.07176 | -0.0034662 | -0.0038645 | 0.060077 | 0.027128 | 0.059071 | -64.5634 | -1.5004 | -66.6636 | 56.2976 | 56.1471 | 56.2253 | -66.865 | -66.697 | -1.0573 | -66.8094 | 56.0978 | 56.3351 | 56.2788 | -66.9645 | -0.16424 | -0.034774 | 2.1374 | 0.037149 | 0.20139 | -0.18527 | -0.10713 | -0.26377 | -0.23458 | 0.003726 | -0.10862 | 0.15515 | 0.002699 | -0.053621 | 122.9984 | 122.8479 | 122.926 | 65.2004 | -123.1974 | 122.7986 | 123.0358 | 122.9795 | 65.6434 | -123.2969
245.9375 | 123.3307 | -66.6916 | 56.3416 | 0.063697 | -0.020194 | -0.0014454 | 0.053271 | -0.0044619 | 0.05214 | 0.056499 | -0.0045342 | -0.0027965 | 0.059009 | 0.023923 | 0.061208 | -64.5588 | -1.5553 | -66.6728 | 56.2976 | 56.1471 | 56.2344 | -66.8513 | -66.6924 | -1.094 | -66.8048 | 56.0932 | 56.3351 | 56.2834 | -66.9645 | -0.15966 | -0.04393 | 2.1328 | 0.018837 | 0.1785 | -0.19442 | -0.10713 | -0.27292 | -0.24831 | -0.000851 | -0.11319 | 0.15973 | -0.006457 | -0.058199 | 122.9892 | 122.8387 | 122.926 | 65.1363 | -123.1928 | 122.7848 | 123.0267 | 122.9749 | 65.5976 | -123.3061
246.9375 | 123.2986 | -66.687 | 56.3324 | 0.063697 | -0.021263 | -0.0014454 | 0.052202 | -0.0065979 | 0.05214 | 0.087021 | -0.0034662 | -0.0038645 | 0.060077 | 0.027128 | 0.059071 | -64.568 | -1.624 | -66.6636 | 56.293 | 56.1426 | 56.2436 | -66.8467 | -66.6924 | -1.1352 | -66.8002 | 56.0932 | 56.3351 | 56.2788 | -66.9645 | -0.15966 | -0.039353 | 2.1191 | 0.023416 | 0.18308 | -0.18984 | -0.088814 | -0.2775 | -0.23916 | -0.005428 | -0.11319 | 0.16431 | 0.002699 | -0.053621 | 122.9801 | 122.8296 | 122.9306 | 65.063 | -123.1791 | 122.7803 | 123.0221 | 122.9658 | 65.5519 | -123.2969
247.9375 | 123.381 | -66.6641 | 56.3416 | 0.063697 | -0.021263 | -0.0014454 | 0.052202 | -0.0055299 | 0.053208 | 0.056499 | -0.0034662 | -0.0038645 | 0.059009 | 0.028197 | 0.058003 | -64.5359 | -1.6789 | -66.6682 | 56.3022 | 56.1517 | 56.2344 | -66.8421 | -66.6833 | -1.1901 | -66.8002 | 56.0932 | 56.3397 | 56.2513 | -66.9645 | -0.17797 | -0.039352 | 2.1282 | -0.00405 | 0.17392 | -0.18984 | -0.10713 | -0.30039 | -0.24831 | -0.019159 | -0.13608 | 0.16431 | -0.001878 | -0.090249 | 122.9663 | 122.8158 | 122.8985 | 64.9852 | -123.1836 | 122.7574 | 123.0038 | 122.9154 | 65.474 | -123.3061
248.9375 | 123.3536 | -66.687 | 56.3553 | 0.048435 | -0.020194 | -0.0046504 | 0.053271 | -0.0055299 | 0.05214 | 0.07176 | -0.0045342 | -0.0038645 | 0.060077 | 0.024992 | 0.059071 | -64.5451 | -1.7522 | -66.659 | 56.3022 | 56.1609 | 56.2344 | -66.8421 | -66.6879 | -1.245 | -66.791 | 56.1024 | 56.3351 | 56.2788 | -66.9599 | -0.15508 | -0.053085 | 2.1419 | 0.027995 | 0.18308 | -0.19442 | -0.12086 | -0.27292 | -0.25289 | -0.000849 | -0.10404 | 0.16889 | -0.02019 | -0.07651 | 122.9892 | 122.8479 | 122.9214 | 64.9348 | -123.1974 | 122.7894 | 123.0221 | 122.9658 | 65.442 | -123.3152
249.9375 | 123.3124 | -66.6824 | 56.3278 | 0.063697 | -0.020194 | -0.0014454 | 0.053271 | -0.0055299 | 0.051071 | 0.087021 | -0.0045342 | -0.0049335 | 0.060077 | 0.027128 | 0.06014 | -64.5588 | -1.8209 | -66.6636 | 56.2976 | 56.1471 | 56.2436 | -66.8558 | -66.6924 | -1.3 | -66.8002 | 56.0978 | 56.3351 | 56.2788 | -66.9691 | -0.1734 | -0.030197 | 2.1236 | 0.018838 | 0.19223 | -0.18069 | -0.084237 | -0.28666 | -0.23 | -0.010006 | -0.11777 | 0.16889 | 0.007276 | -0.049044 | 122.9801 | 122.8296 | 122.926 | 64.8616 | -123.1837 | 122.7803 | 123.0175 | 122.9612 | 65.3824 | -123.2969
250.9531 | 123.3124 | -66.7007 | 56.3004 | 0.078959 | -0.021263 | -0.0025134 | 0.053271 | -0.0044619 | 0.050003 | 0.041238 | -0.0056032 | -0.0038645 | 0.059009 | 0.02606 | 0.059071 | -64.5588 | -1.8896 | -66.659 | 56.3022 | 56.1517 | 56.239 | -66.8467 | -66.6833 | -1.3504 | -66.7956 | 56.1024 | 56.3397 | 56.2879 | -66.9599 | -0.14593 | 0.001847 | 2.1419 | 0.041728 | 0.18765 | -0.14864 | -0.06135 | -0.25919 | -0.19796 | 0.017462 | -0.094881 | 0.16431 | 0.039321 | -0.012421 | 123.0029 | 122.8525 | 122.9397 | 64.8112 | -123.147 | 122.8031 | 123.0404 | 122.9887 | 65.3504 | -123.2603
251.9375 | 123.2803 | -66.6962 | 56.3461 | 0.048435 | -0.022331 | -0.00037739 | 0.053271 | -0.0044619 | 0.051071 | 0.056499 | -0.0045342 | -0.0038645 | 0.059009 | 0.02606 | 0.059071 | -64.568 | -1.9582 | -66.6499 | 56.293 | 56.1517 | 56.2482 | -66.8421 | -66.6833 | -1.4007 | -66.7865 | 56.1116 | 56.3397 | 56.2834 | -66.9599 | -0.14593 | -0.053086 | 2.1282 | 0.046306 | 0.19223 | -0.19442 | -0.097969 | -0.26377 | -0.23458 | 0.012884 | -0.090302 | 0.17347 | -0.006455 | -0.062776 | 122.9892 | 122.8479 | 122.9443 | 64.7379 | -123.1882 | 122.8077 | 123.0358 | 122.9795 | 65.2954 | -123.3061
252.9375 | 123.3078 | -66.687 | 56.337 | 0.033173 | -0.022331 | -0.0035824 | 0.053271 | -0.0033929 | 0.051071 | 0.041238 | -0.0045342 | -0.0027965 | 0.061145 | 0.02606 | 0.059071 | -64.5588 | -2.0315 | -66.6499 | 56.3022 | 56.1563 | 56.2436 | -66.8467 | -66.6833 | -1.4602 | -66.8002 | 56.107 | 56.3305 | 56.2879 | -66.9645 | -0.15966 | -0.034774 | 2.1282 | 0.037151 | 0.19681 | -0.18069 | -0.093392 | -0.2775 | -0.23 | 0.003729 | -0.11319 | 0.16431 | -0.006458 | -0.049042 | 122.9892 | 122.8433 | 122.9306 | 64.6555 | -123.1836 | 122.794 | 123.0175 | 122.9749 | 65.2268 | -123.3015
253.9375 | 123.3261 | -66.7099 | 56.3049 | 0.048435 | -0.0234 | -0.0025134 | 0.053271 | -0.0055299 | 0.050003 | 0.07176 | -0.0034662 | -0.0027965 | 0.059009 | 0.02606 | 0.059071 | -64.5496 | -2.1139 | -66.6682 | 56.3068 | 56.1609 | 56.2573 | -66.8421 | -66.6833 | -1.5106 | -66.7956 | 56.1024 | 56.3397 | 56.2925 | -66.9554 | -0.13219 | 0.001847 | 2.1603 | 0.041726 | 0.17392 | -0.14406 | -0.047614 | -0.24545 | -0.20253 | 0.026617 | -0.085726 | 0.15973 | 0.034743 | -0.012421 | 123.0167 | 122.8708 | 122.9672 | 64.596 | -123.147 | 122.8123 | 123.0496 | 123.0024 | 65.1993 | -123.2603
254.9375 | 123.2986 | -66.6733 | 56.337 | 0.063697 | -0.022331 | -0.0014454 | 0.054339 | -0.0065979 | 0.051071 | 0.07176 | -0.0056032 | -0.0038645 | 0.057941 | 0.027128 | 0.059071 | -64.5496 | -2.1872 | -66.6544 | 56.3068 | 56.1563 | 56.2482 | -66.8375 | -66.6924 | -1.5747 | -66.791 | 56.1116 | 56.3443 | 56.2925 | -66.9554 | -0.16424 | -0.030196 | 2.1236 | 0.01884 | 0.18308 | -0.18069 | -0.088814 | -0.28208 | -0.22542 | -0.019161 | -0.11777 | 0.16431 | 0.007278 | -0.044464 | 122.9801 | 122.8296 | 122.9214 | 64.4861 | -123.1745 | 122.7848 | 123.0175 | 122.9658 | 65.0986 | -123.2923
255.9531 | 123.317 | -66.6641 | 56.3278 | 0.048435 | -0.022331 | -0.00037739 | 0.052202 | -0.0055299 | 0.051071 | 0.056499 | -0.0034662 | -0.0027965 | 0.059009 | 0.028197 | 0.059071 | -64.5222 | -2.2604 | -66.6544 | 56.3068 | 56.1517 | 56.2527 | -66.8375 | -66.6741 | -1.6205 | -66.791 | 56.107 | 56.3397 | 56.2971 | -66.9554 | -0.17339 | -0.021041 | 2.142 | 0.009685 | 0.18308 | -0.17611 | -0.07508 | -0.29123 | -0.22085 | -0.010001 | -0.12692 | 0.16431 | 0.011855 | -0.03073 | 122.9709 | 122.8158 | 122.9169 | 64.4037 | -123.1653 | 122.7711 | 123.0038 | 122.9612 | 65.0436 | -123.2832
256.9375 | 123.3078 | -66.7099 | 56.3324 | 0.048435 | -0.022331 | -0.0025134 | 0.052202 | -0.0065979 | 0.051071 | 0.056499 | -0.0056032 | -0.0038645 | 0.057941 | 0.027128 | 0.059071 | -64.5405 | -2.3428 | -66.6544 | 56.3114 | 56.1517 | 56.2527 | -66.8375 | -66.6695 | -1.6938 | -66.7819 | 56.1161 | 56.3397 | 56.2879 | -66.9599 | -0.12761 | -0.021039 | 2.1694 | 0.055461 | 0.18308 | -0.18069 | -0.079657 | -0.25003 | -0.21626 | 0.040353 | -0.07199 | 0.17804 | 0.007278 | -0.044464 | 123.0213 | 122.8616 | 122.9626 | 64.3671 | -123.1699 | 122.826 | 123.0496 | 122.9978 | 65.0161 | -123.2923
257.9531 | 123.3078 | -66.6916 | 56.3278 | 0.078959 | -0.020194 | -0.00037739 | 0.052202 | -0.0044619 | 0.051071 | 0.056499 | -0.0034662 | -0.0027965 | 0.060077 | 0.027128 | 0.055867 | -64.4993 | -2.4207 | -66.6499 | 56.3205 | 56.1563 | 56.2482 | -66.8421 | -66.6695 | -1.7624 | -66.7865 | 56.107 | 56.3488 | 56.3017 | -66.9462 | -0.1505 | -0.007306 | 2.1923 | 0.041728 | 0.19223 | -0.17153 | -0.079659 | -0.25461 | -0.22085 | 0.022042 | -0.09488 | 0.15973 | 0.021012 | -0.026151 | 123.0121 | 122.8479 | 122.9398 | 64.2709 | -123.1699 | 122.7986 | 123.0404 | 122.9933 | 64.9291 | -123.274
258.9375 | 123.2712 | -66.6824 | 56.3416 | 0.063697 | -0.022331 | -0.00037739 | 0.053271 | -0.0055299 | 0.053208 | 0.056499 | -0.0023982 | -0.0027965 | 0.060077 | 0.02606 | 0.058003 | -64.5359 | -2.4985 | -66.6407 | 56.3114 | 56.1609 | 56.2619 | -66.8467 | -66.6741 | -1.822 | -66.7865 | 56.1161 | 56.3488 | 56.3017 | -66.9508 | -0.16424 | -0.030195 | 2.1465 | 0.04173 | 0.20597 | -0.18068 | -0.079656 | -0.26834 | -0.22542 | 0.008309 | -0.10403 | 0.16431 | 0.007279 | -0.039884 | 122.9938 | 122.8433 | 122.9443 | 64.1839 | -123.1882 | 122.7986 | 123.0313 | 122.9841 | 64.8605 | -123.2923
259.9375 | 123.2803 | -66.7145 | 56.3141 | 0.078959 | -0.022331 | 0.00069161 | 0.054339 | -0.0033929 | 0.05214 | 0.056499 | -0.0056032 | -0.00065947 | 0.059009 | 0.027128 | 0.06014 | -64.5359 | -2.5855 | -66.6499 | 56.3159 | 56.17 | 56.2573 | -66.8375 | -66.6604 | -1.8998 | -66.7819 | 56.1116 | 56.3488 | 56.3017 | -66.9462 | -0.12304 | 0.001849 | 2.1786 | 0.064617 | 0.18765 | -0.14406 | -0.056769 | -0.23172 | -0.20253 | 0.054089 | -0.067412 | 0.16431 | 0.034745 | -0.012418 | 123.0304 | 122.8845 | 122.9718 | 64.129 | -123.1516 | 122.826 | 123.0633 | 123.0161 | 64.8147 | -123.2603
260.9375 | 123.3078 | -66.687 | 56.3599 | 0.063697 | -0.020194 | -0.0014454 | 0.054339 | -0.0044619 | 0.05214 | 0.056499 | -0.0045342 | -0.00065947 | 0.060077 | 0.027128 | 0.056935 | -64.5222 | -2.6908 | -66.6453 | 56.3114 | 56.1609 | 56.2619 | -66.8329 | -66.6741 | -1.9776 | -66.7819 | 56.1024 | 56.3534 | 56.2925 | -66.9508 | -0.14592 | -0.048505 | 2.1648 | 0.041729 | 0.18765 | -0.19899 | -0.097966 | -0.26376 | -0.25747 | 0.012887 | -0.094878 | 0.16889 | -0.006453 | -0.067352 | 122.9984 | 122.8479 | 122.9489 | 63.9962 | -123.1928 | 122.7894 | 123.0404 | 122.9795 | 64.7094 | -123.3106
261.9375 | 123.262 | -66.6779 | 56.3461 | 0.048435 | -0.022331 | -0.0014454 | 0.051134 | -0.0044619 | 0.051071 | 0.041238 | -0.0056032 | -0.0038645 | 0.057941 | 0.029265 | 0.061208 | -64.5268 | -2.7824 | -66.6453 | 56.3114 | 56.1746 | 56.2619 | -66.8375 | -66.6558 | -2.0417 | -66.7773 | 56.1207 | 56.358 | 56.3062 | -66.9508 | -0.15966 | -0.034772 | 2.1511 | 0.032573 | 0.19223 | -0.17153 | -0.084233 | -0.27292 | -0.22542 | 0.022046 | -0.099455 | 0.17347 | 0.011859 | -0.039883 | 122.9892 | 122.8525 | 122.9398 | 63.8955 | -123.1836 | 122.7986 | 123.0358 | 122.9841 | 64.6361 | -123.2969
262.9531 | 123.2666 | -66.6779 | 56.369 | 0.063697 | -0.021263 | -0.00037739 | 0.052202 | -0.0033929 | 0.050003 | 0.056499 | -0.0066712 | -0.0027965 | 0.059009 | 0.028197 | 0.056935 | -64.5451 | -2.8923 | -66.6361 | 56.3205 | 56.17 | 56.2573 | -66.8375 | -66.6604 | -2.1287 | -66.7727 | 56.1207 | 56.3534 | 56.3062 | -66.9462 | -0.15966 | -0.048505 | 2.1328 | 0.04173 | 0.20139 | -0.19899 | -0.1117 | -0.26834 | -0.24831 | 0.017467 | -0.094876 | 0.17347 | -0.015609 | -0.062772 | 122.9984 | 122.8479 | 122.9352 | 63.7856 | -123.2065 | 122.7986 | 123.0313 | 122.9841 | 64.5491 | -123.3152
263.9375 | 123.3078 | -66.6779 | 56.3324 | 0.048435 | -0.021263 | -0.0014454 | 0.052202 | -0.0055299 | 0.051071 | 0.07176 | -0.0034662 | -0.00065947 | 0.059009 | 0.028197 | 0.056935 | -64.4947 | -2.9793 | -66.6361 | 56.3205 | 56.1792 | 56.2573 | -66.8284 | -66.6604 | -2.202 | -66.7636 | 56.1207 | 56.358 | 56.3154 | -66.9416 | -0.1505 | -0.011883 | 2.1832 | 0.04173 | 0.19223 | -0.15321 | -0.075079 | -0.26376 | -0.21169 | 0.017467 | -0.085719 | 0.17804 | 0.025592 | -0.016993 | 122.9984 | 122.857 | 122.9352 | 63.6986 | -123.1608 | 122.7986 | 123.0358 | 122.9933 | 64.4759 | -123.274
264.9531 | 123.2574 | -66.655 | 56.3919 | 0.078959 | -0.021263 | -0.0014454 | 0.053271 | -0.0033929 | 0.051071 | 0.056499 | -0.0045342 | -0.0049335 | 0.060077 | 0.027128 | 0.059071 | -64.4718 | -3.0892 | -66.6361 | 56.3205 | 56.1746 | 56.2711 | -66.8284 | -66.6604 | -2.2798 | -66.7773 | 56.1299 | 56.3534 | 56.2467 | -66.9462 | -0.17339 | -0.071393 | 2.1832 | 0.018842 | 0.19223 | -0.2173 | -0.12085 | -0.29123 | -0.26204 | -0.005421 | -0.12234 | 0.16889 | -0.038497 | -0.14518 | 122.9755 | 122.8296 | 122.926 | 63.5658 | -123.2203 | 122.7848 | 123.0084 | 122.9017 | 64.3751 | -123.3381
265.9375 | 123.2986 | -66.6824 | 56.2912 | 0.048435 | -0.0234 | -0.0035824 | 0.054339 | -0.0055299 | 0.051071 | 0.07176 | -0.0056032 | -0.0017285 | 0.060077 | 0.030333 | 0.059071 | -64.4947 | -3.2036 | -66.627 | 56.3251 | 56.1792 | 56.2756 | -66.8329 | -66.6512 | -2.3668 | -66.7682 | 56.1207 | 56.358 | 56.3154 | -66.9462 | -0.1505 | 0.033894 | 2.1877 | 0.055464 | 0.20597 | -0.11201 | -0.015566 | -0.26376 | -0.17049 | 0.031202 | -0.08572 | 0.17804 | 0.06679 | 0.024205 | 123.0075 | 122.8616 | 122.9581 | 63.4788 | -123.1241 | 122.8031 | 123.0404 | 122.9978 | 64.3156 | -123.2374
266.9375 | 123.3078 | -66.6824 | 56.3507 | 0.033173 | -0.0234 | -0.0025134 | 0.054339 | -0.0055299 | 0.051071 | 0.056499 | -0.0034662 | -0.0017285 | 0.059009 | 0.029265 | 0.058003 | -64.4764 | -3.3272 | -66.627 | 56.3205 | 56.1746 | 56.2619 | -66.8238 | -66.6558 | -2.4447 | -66.759 | 56.1344 | 56.358 | 56.2742 | -66.937 | -0.14134 | -0.030194 | 2.206 | 0.055464 | 0.19681 | -0.1761 | -0.088811 | -0.25461 | -0.21626 | 0.026624 | -0.076562 | 0.17804 | 0.007281 | -0.076511 | 123.0029 | 122.857 | 122.9443 | 63.3552 | -123.1745 | 122.8169 | 123.0404 | 122.9566 | 64.2378 | -123.2877
267.9531 | 123.1842 | -66.7099 | 56.3828 | 0.048435 | -0.022331 | -0.0035824 | 0.054339 | -0.0044619 | 0.05214 | 0.056499 | -0.0034662 | -0.0038645 | 0.059009 | 0.028197 | 0.06014 | -64.4443 | -3.4417 | -66.627 | 56.3342 | 56.1746 | 56.2711 | -66.8238 | -66.6512 | -2.5454 | -66.7636 | 56.1253 | 56.3671 | 56.3154 | -66.9325 | -0.11388 | -0.048501 | 2.2656 | 0.08293 | 0.19681 | -0.20815 | -0.1117 | -0.22256 | -0.25746 | 0.058668 | -0.053675 | 0.16889 | -0.015605 | -0.067347 | 123.0442 | 122.8845 | 122.981 | 63.2682 | -123.2065 | 122.8352 | 123.077 | 123.0253 | 64.1645 | -123.3152
268.9375 | 123.3215 | -66.6733 | 56.3416 | 0.048435 | -0.022331 | -0.00037739 | 0.052202 | -0.0055299 | 0.051071 | 0.041238 | -0.0045342 | -0.0027965 | 0.059009 | 0.028197 | 0.058003 | -64.4718 | -3.5653 | -66.6224 | 56.3388 | 56.1792 | 56.2756 | -66.8192 | -66.6512 | -2.637 | -66.7636 | 56.1436 | 56.3671 | 56.2788 | -66.937 | -0.14592 | -0.002725 | 2.2015 | 0.050888 | 0.19681 | -0.16237 | -0.06592 | -0.26376 | -0.19795 | 0.022047 | -0.090296 | 0.17346 | 0.025593 | -0.062777 | 123.0121 | 122.8525 | 122.9489 | 63.108 | -123.1608 | 122.8169 | 123.0404 | 122.9521 | 64.0363 | -123.2786
269.9531 | 123.2986 | -66.6641 | 56.3507 | 0.048435 | -0.0234 | -0.0014454 | 0.053271 | -0.0065979 | 0.051071 | 0.056499 | -0.0066712 | -0.0049335 | 0.057941 | 0.029265 | 0.056935 | -64.4947 | -3.7073 | -66.6178 | 56.3342 | 56.1746 | 56.2848 | -66.8146 | -66.6467 | -2.7331 | -66.759 | 56.1482 | 56.3626 | 56.32 | -66.937 | -0.15049 | -0.016458 | 2.1694 | 0.046311 | 0.19681 | -0.1761 | -0.065918 | -0.27292 | -0.20253 | 0.017471 | -0.094872 | 0.17804 | 0.01186 | -0.030725 | 122.9984 | 122.8387 | 122.9489 | 62.9569 | -123.1653 | 122.8123 | 123.0267 | 122.9841 | 63.931 | -123.2877
270.9375 | 123.2025 | -66.7191 | 56.3919 | 0.048435 | -0.022331 | -0.0025134 | 0.052202 | -0.0044619 | 0.051071 | 0.056499 | -0.0045342 | -0.0027965 | 0.060077 | 0.029265 | 0.056935 | -64.4443 | -3.8309 | -66.6178 | 56.3342 | 56.1838 | 56.2894 | -66.8146 | -66.6421 | -2.843 | -66.759 | 56.1344 | 56.3671 | 56.3108 | -66.9325 | -0.095564 | -0.057657 | 2.2747 | 0.10124 | 0.19681 | -0.20814 | -0.10254 | -0.21341 | -0.25746 | 0.076981 | -0.039941 | 0.17347 | -0.024761 | -0.081081 | 123.0533 | 122.9028 | 123.0084 | 62.8882 | -123.2065 | 122.8535 | 123.0862 | 123.0299 | 63.876 | -123.3244
271.9375 | 123.1705 | -66.6962 | 56.3782 | 0.078959 | -0.022331 | -0.0046504 | 0.054339 | -0.0044619 | 0.051071 | 0.041238 | -0.0045342 | -0.0038645 | 0.059009 | 0.029265 | 0.056935 | -64.4352 | -3.9728 | -66.6178 | 56.3388 | 56.1838 | 56.2802 | -66.81 | -66.6375 | -2.9621 | -66.7498 | 56.1436 | 56.3671 | 56.2879 | -66.9325 | -0.11387 | -0.039346 | 2.261 | 0.078354 | 0.19223 | -0.19441 | -0.097963 | -0.23629 | -0.23457 | 0.058671 | -0.053672 | 0.18262 | -0.011028 | -0.090241 | 123.035 | 122.8799 | 122.9764 | 62.7233 | -123.1882 | 122.8398 | 123.0633 | 122.9841 | 63.7341 | -123.3106
272.9531 | 123.1705 | -66.7099 | 56.3873 | 0.048435 | -0.021263 | -0.0035824 | 0.054339 | -0.0055299 | 0.051071 | 0.087021 | -0.0056032 | -0.0027965 | 0.059009 | 0.028197 | 0.055867 | -64.4398 | -4.1148 | -66.6087 | 56.3388 | 56.1838 | 56.2848 | -66.81 | -66.6375 | -3.0765 | -66.7453 | 56.1436 | 56.3717 | 56.2788 | -66.9279 | -0.10014 | -0.048501 | 2.2701 | 0.10124 | 0.20138 | -0.20357 | -0.10254 | -0.21798 | -0.24373 | 0.072404 | -0.03536 | 0.18262 | -0.015604 | -0.10855 | 123.0487 | 122.8937 | 122.9947 | 62.5951 | -123.1974 | 122.8535 | 123.0816 | 122.9887 | 63.6334 | -123.3152
273.9375 | 123.1888 | -66.7236 | 56.3828 | 0.063697 | -0.0234 | -0.0014454 | 0.053271 | -0.0044619 | 0.05214 | 0.041238 | -0.0034662 | -0.0017285 | 0.059009 | 0.029265 | 0.058003 | -64.426 | -4.2704 | -66.6087 | 56.3388 | 56.1929 | 56.2894 | -66.8146 | -66.6421 | -3.2002 | -66.7453 | 56.139 | 56.3763 | 56.3246 | -66.9233 | -0.090986 | -0.043923 | 2.2976 | 0.11498 | 0.20596 | -0.18983 | -0.093382 | -0.19967 | -0.24373 | 0.081559 | -0.021627 | 0.17804 | -0.006448 | -0.058189 | 123.0625 | 122.9166 | 123.013 | 62.4532 | -123.1974 | 122.8627 | 123.0999 | 123.0482 | 63.5235 | -123.3061
274.9531 | 123.3078 | -66.6504 | 56.3828 | 0.063697 | -0.022331 | -0.0014454 | 0.051134 | -0.0055299 | 0.051071 | 0.056499 | -0.0045342 | -0.0017285 | 0.060077 | 0.031402 | 0.059071 | -64.5084 | -4.4169 | -66.5995 | 56.3434 | 56.1838 | 56.2894 | -66.81 | -66.6283 | -3.3192 | -66.7453 | 56.1436 | 56.3809 | 56.3337 | -66.9233 | -0.15965 | -0.039345 | 2.142 | 0.050891 | 0.21054 | -0.19899 | -0.093382 | -0.27291 | -0.23915 | 0.022053 | -0.094869 | 0.17804 | -0.001869 | -0.049032 | 122.9938 | 122.8342 | 122.9398 | 62.2334 | -123.1928 | 122.794 | 123.0313 | 122.9841 | 63.3312 | -123.3061
275.9375 | 123.1613 | -66.7007 | 56.4011 | 0.033173 | -0.021263 | -0.0025134 | 0.053271 | -0.0055299 | 0.051071 | 0.056499 | -0.0034662 | -0.0027965 | 0.060077 | 0.027128 | 0.056935 | -64.426 | -4.5726 | -66.5995 | 56.3434 | 56.1975 | 56.2985 | -66.81 | -66.6192 | -3.4474 | -66.7453 | 56.139 | 56.3855 | 56.3383 | -66.9325 | -0.1093 | -0.057656 | 2.2747 | 0.10124 | 0.21054 | -0.20356 | -0.10254 | -0.23172 | -0.26204 | 0.081564 | -0.044515 | 0.1872 | -0.015601 | -0.062765 | 123.0442 | 122.8982 | 122.9993 | 62.1281 | -123.2111 | 122.8398 | 123.0862 | 123.039 | 63.2533 | -123.3335
276.9375 | 123.2666 | -66.6641 | 56.4148 | 0.048435 | -0.0234 | -0.0014454 | 0.053271 | -0.0065979 | 0.051071 | 0.087021 | -0.0045342 | -0.0038645 | 0.060077 | 0.029265 | 0.056935 | -64.4031 | -4.7374 | -66.5995 | 56.3526 | 56.1975 | 56.2939 | -66.8055 | -66.6283 | -3.571 | -66.7315 | 56.1528 | 56.3855 | 56.2925 | -66.9187 | -0.14134 | -0.062232 | 2.261 | 0.064624 | 0.20596 | -0.2173 | -0.12085 | -0.2546 | -0.26203 | 0.035786 | -0.0674 | 0.1872 | -0.029334 | -0.12228 | 123.0167 | 122.8616 | 122.9581 | 61.9267 | -123.2203 | 122.8169 | 123.0496 | 122.9566 | 63.0931 | -123.3335
277.9375 | 123.1842 | -66.687 | 56.4102 | 0.033173 | -0.021263 | -0.0014454 | 0.052202 | -0.0044619 | 0.051071 | 0.056499 | -0.0056032 | -0.00065947 | 0.059009 | 0.028197 | 0.058003 | -64.4031 | -4.9206 | -66.5903 | 56.3571 | 56.2021 | 56.3031 | -66.8009 | -66.6146 | -3.6855 | -66.7269 | 56.1528 | 56.39 | 56.3429 | -66.9141 | -0.11387 | -0.053075 | 2.2839 | 0.096669 | 0.21054 | -0.20814 | -0.10711 | -0.22713 | -0.25746 | 0.07241 | -0.039933 | 0.1872 | -0.020178 | -0.067341 | 123.0442 | 122.8891 | 122.9901 | 61.7664 | -123.2111 | 122.8398 | 123.0771 | 123.0299 | 63.0015 | -123.3244
278.9375 | 123.2071 | -66.7099 | 56.4285 | 0.033173 | -0.022331 | -0.0025134 | 0.053271 | -0.0055299 | 0.051071 | 0.056499 | -0.0045342 | -0.0027965 | 0.059009 | 0.031402 | 0.059071 | -64.3986 | -5.0717 | -66.5903 | 56.3526 | 56.2067 | 56.3031 | -66.7963 | -66.61 | -3.832 | -66.7269 | 56.1528 | 56.3855 | 56.3429 | -66.9141 | -0.086404 | -0.075965 | 2.3113 | 0.11956 | 0.20596 | -0.22187 | -0.12542 | -0.20425 | -0.27577 | 0.099877 | -0.017045 | 0.1872 | -0.043067 | -0.085652 | 123.0625 | 122.9166 | 123.013 | 61.6382 | -123.2248 | 122.8627 | 123.0954 | 123.0528 | 62.8779 | -123.3427
279.9531 | 123.175 | -66.6595 | 56.4651 | 0.063697 | -0.0234 | -0.0025134 | 0.051134 | -0.0065979 | 0.048935 | 0.07176 | -0.0056032 | -0.0038645 | 0.057941 | 0.031402 | 0.056935 | -64.4077 | -5.2411 | -66.5858 | 56.3571 | 56.2112 | 56.2985 | -66.7917 | -66.61 | -3.974 | -66.7315 | 56.1482 | 56.3946 | 56.3475 | -66.9141 | -0.13218 | -0.10801 | 2.2518 | 0.073781 | 0.20596 | -0.25391 | -0.16662 | -0.2546 | -0.31697 | 0.049523 | -0.071978 | 0.18262 | -0.070531 | -0.11769 | 123.0167 | 122.8708 | 122.9581 | 61.4185 | -123.2569 | 122.8077 | 123.0542 | 123.007 | 62.6856 | -123.3793
280.9375 | 123.2071 | -66.6779 | 56.4102 | 0.063697 | -0.025536 | -0.0014454 | 0.055407 | -0.0055299 | 0.050003 | 0.07176 | -0.0056032 | -0.0038645 | 0.061145 | 0.03247 | 0.059071 | -64.3848 | -5.4242 | -66.5903 | 56.3663 | 56.2112 | 56.3123 | -66.7917 | -66.6054 | -4.1067 | -66.7224 | 56.1619 | 56.3992 | 56.3475 | -66.9096 | -0.11387 | -0.043919 | 2.293 | 0.087513 | 0.20138 | -0.19898 | -0.097955 | -0.23171 | -0.2483 | 0.072411 | -0.044511 | 0.1872 | -0.01102 | -0.062762 | 123.0442 | 122.8891 | 122.9901 | 61.2536 | -123.2019 | 122.8398 | 123.0771 | 123.0253 | 62.5711 | -123.3198
281.9531 | 123.1705 | -66.7191 | 56.4056 | 0.048435 | -0.024468 | -0.0014454 | 0.053271 | -0.0044619 | 0.050003 | 0.056499 | -0.0077392 | -0.0027965 | 0.059009 | 0.029265 | 0.058003 | -64.3894 | -5.6165 | -66.5766 | 56.3709 | 56.2021 | 56.3077 | -66.7963 | -66.5963 | -4.2533 | -66.7132 | 56.1573 | 56.4038 | 56.3337 | -66.9096 | -0.077249 | -0.034763 | 2.3297 | 0.14245 | 0.2197 | -0.20356 | -0.097957 | -0.19051 | -0.2483 | 0.12277 | 0.005846 | 0.19636 | -0.001865 | -0.071921 | 123.0899 | 122.9211 | 123.0267 | 61.1025 | -123.2019 | 122.8764 | 123.1228 | 123.0528 | 62.4658 | -123.3152
282.9375 | 123.2025 | -66.6687 | 56.4239 | 0.048435 | -0.025536 | -0.0014454 | 0.053271 | -0.0065979 | 0.051071 | 0.056499 | -0.0056032 | -0.0027965 | 0.057941 | 0.030333 | 0.059071 | -64.3802 | -5.7997 | -66.5766 | 56.3709 | 56.2112 | 56.3123 | -66.7826 | -66.6009 | -4.3998 | -66.7178 | 56.1711 | 56.4038 | 56.3658 | -66.905 | -0.11387 | -0.053073 | 2.2885 | 0.092093 | 0.20596 | -0.21271 | -0.11169 | -0.23629 | -0.25288 | 0.067835 | -0.049087 | 0.1872 | -0.020175 | -0.058181 | 123.0396 | 122.8799 | 122.981 | 60.869 | -123.2065 | 122.8398 | 123.0725 | 123.0345 | 62.2689 | -123.3289
283.9375 | 123.2346 | -66.6412 | 56.4285 | 0.048435 | -0.026605 | -0.0035824 | 0.052202 | -0.0055299 | 0.05214 | 0.07176 | -0.0056032 | -0.0027965 | 0.059009 | 0.03247 | 0.058003 | -64.3802 | -5.9782 | -66.5675 | 56.3755 | 56.225 | 56.3214 | -66.7826 | -66.5963 | -4.5646 | -66.7132 | 56.1757 | 56.4129 | 56.3612 | -66.905 | -0.14133 | -0.053073 | 2.261 | 0.073783 | 0.21511 | -0.20356 | -0.10711 | -0.26375 | -0.25288 | 0.044948 | -0.071974 | 0.19178 | -0.015596 | -0.067338 | 123.0167 | 122.8662 | 122.9627 | 60.663 | -123.2111 | 122.8169 | 123.0542 | 123.0024 | 62.0766 | -123.3335
284.9375 | 123.2437 | -66.6504 | 56.4239 | 0.078959 | -0.024468 | -0.0035824 | 0.055407 | -0.0055299 | 0.050003 | 0.07176 | -0.0056032 | -0.0049335 | 0.059009 | 0.03247 | 0.06014 | -64.3711 | -6.166 | -66.572 | 56.3755 | 56.2296 | 56.3214 | -66.778 | -66.5963 | -4.7249 | -66.7041 | 56.1894 | 56.4175 | 56.3658 | -66.8958 | -0.1276 | -0.048495 | 2.2793 | 0.078361 | 0.20596 | -0.1944 | -0.10253 | -0.24544 | -0.23456 | 0.054104 | -0.053661 | 0.19178 | -0.006439 | -0.058181 | 123.0258 | 122.8799 | 122.9718 | 60.4844 | -123.2019 | 122.8398 | 123.0679 | 123.0162 | 61.9255 | -123.3198
285.9375 | 123.2391 | -66.6412 | 56.4148 | 0.048435 | -0.0234 | -0.0014454 | 0.054339 | -0.0065979 | 0.051071 | 0.056499 | -0.0045342 | -0.0027965 | 0.059009 | 0.031402 | 0.059071 | -64.3711 | -6.3583 | -66.572 | 56.38 | 56.225 | 56.3214 | -66.7826 | -66.5826 | -4.8805 | -66.6995 | 56.194 | 56.4175 | 56.3566 | -66.8913 | -0.14133 | -0.034761 | 2.2701 | 0.069205 | 0.21054 | -0.18982 | -0.093376 | -0.25002 | -0.22083 | 0.058684 | -0.058238 | 0.19178 | 0.002716 | -0.058183 | 123.0213 | 122.8662 | 122.9627 | 60.283 | -123.1974 | 122.8352 | 123.0587 | 122.9978 | 61.7607 | -123.306
286.9375 | 123.3032 | -66.6138 | 56.4331 | 0.063697 | -0.024468 | -0.0035824 | 0.051134 | -0.0044619 | 0.050003 | 0.07176 | -0.0056032 | -0.0038645 | 0.059009 | 0.031402 | 0.058003 | -64.4627 | -6.5689 | -66.5491 | 56.38 | 56.2387 | 56.326 | -66.7734 | -66.5688 | -5.0454 | -66.6949 | 56.2031 | 56.4221 | 56.3658 | -66.8958 | -0.15964 | -0.053071 | 2.1511 | 0.064631 | 0.22427 | -0.1944 | -0.10711 | -0.28206 | -0.22998 | 0.044955 | -0.081124 | 0.20094 | -0.011015 | -0.067336 | 122.9938 | 122.8525 | 122.9398 | 60.0449 | -123.2065 | 122.8169 | 123.0359 | 122.9795 | 61.5684 | -123.3289
287.9375 | 123.2391 | -66.6504 | 56.3873 | 0.063697 | -0.024468 | -0.0035824 | 0.053271 | -0.0065979 | 0.05214 | 0.056499 | -0.0045342 | -0.0027965 | 0.059009 | 0.03247 | 0.056935 | -64.3711 | -6.7703 | -66.5629 | 56.3892 | 56.2479 | 56.3352 | -66.7734 | -66.5734 | -5.2148 | -66.6949 | 56.1848 | 56.4267 | 56.3749 | -66.8913 | -0.12302 | 0.001861 | 2.2793 | 0.087517 | 0.21054 | -0.13946 | -0.052174 | -0.24086 | -0.20252 | 0.076997 | -0.044503 | 0.19636 | 0.039339 | -0.012403 | 123.0396 | 122.8983 | 122.9855 | 59.88 | -123.1607 | 122.8352 | 123.0771 | 123.0253 | 61.4356 | -123.2786
288.9375 | 123.2254 | -66.6458 | 56.4423 | 0.048435 | -0.0234 | -0.0025134 | 0.052202 | -0.0055299 | 0.050003 | 0.087021 | -0.0056032 | -0.0038645 | 0.057941 | 0.03247 | 0.059071 | -64.3665 | -6.9901 | -66.5537 | 56.3892 | 56.2433 | 56.3352 | -66.7688 | -66.5688 | -5.3888 | -66.6857 | 56.2031 | 56.4221 | 56.3795 | -66.8821 | -0.12302 | -0.053071 | 2.2793 | 0.092096 | 0.21511 | -0.19897 | -0.10711 | -0.23628 | -0.23914 | 0.076998 | -0.039924 | 0.19636 | -0.020171 | -0.062756 | 123.035 | 122.8891 | 122.981 | 59.6557 | -123.2111 | 122.8489 | 123.0679 | 123.0253 | 61.257 | -123.3244
289.9375 | 123.2437 | -66.6275 | 56.4468 | 0.033173 | -0.024468 | -0.0025134 | 0.054339 | -0.0055299 | 0.051071 | 0.056499 | -0.0034662 | -0.0027965 | 0.059009 | 0.031402 | 0.056935 | -64.3574 | -7.2053 | -66.5491 | 56.3938 | 56.2387 | 56.3443 | -66.7688 | -66.5642 | -5.5765 | -66.6857 | 56.2169 | 56.4267 | 56.3703 | -66.8775 | -0.14133 | -0.053069 | 2.2702 | 0.078363 | 0.21969 | -0.20813 | -0.10253 | -0.25001 | -0.22998 | 0.063266 | -0.058235 | 0.19178 | -0.02017 | -0.07649 | 123.0213 | 122.8662 | 122.9718 | 59.4222 | -123.2157 | 122.8444 | 123.0542 | 122.9978 | 61.051 | -123.3244
290.9375 | 123.2483 | -66.6367 | 56.4377 | 0.078959 | -0.0234 | -0.0025134 | 0.054339 | -0.0044619 | 0.05214 | 0.07176 | -0.0056032 | -0.0027965 | 0.057941 | 0.031402 | 0.055867 | -64.3574 | -7.4297 | -66.5446 | 56.3983 | 56.2479 | 56.3443 | -66.7688 | -66.5642 | -5.7551 | -66.6812 | 56.2169 | 56.4312 | 56.3703 | -66.8729 | -0.13217 | -0.039336 | 2.2793 | 0.092098 | 0.22427 | -0.18982 | -0.093371 | -0.23628 | -0.22082 | 0.072422 | -0.0445 | 0.19178 | -0.006436 | -0.067335 | 123.035 | 122.8845 | 122.981 | 59.207 | -123.2065 | 122.8535 | 123.0679 | 123.007 | 60.8816 | -123.3106
291.9531 | 123.1613 | -66.6183 | 56.4926 | 0.048435 | -0.024468 | -0.0014454 | 0.053271 | -0.0044619 | 0.050003 | 0.07176 | -0.0056032 | -0.0027965 | 0.059009 | 0.03247 | 0.059071 | -64.3574 | -7.654 | -66.5354 | 56.3938 | 56.2433 | 56.3443 | -66.7551 | -66.5505 | -5.9428 | -66.672 | 56.194 | 56.4312 | 56.3887 | -66.8775 | -0.13675 | -0.098846 | 2.261 | 0.082943 | 0.21969 | -0.24933 | -0.1483 | -0.25917 | -0.29865 | 0.067847 | -0.053654 | 0.20551 | -0.061368 | -0.10395 | 123.0121 | 122.8616 | 122.9627 | 58.9643 | -123.2477 | 122.8123 | 123.0496 | 123.007 | 60.6755 | -123.3701
292.9375 | 123.262 | -66.6229 | 56.4194 | 0.063697 | -0.027673 | -0.0025134 | 0.053271 | -0.0055299 | 0.050003 | 0.07176 | -0.0056032 | -0.0038645 | 0.057941 | 0.033539 | 0.058003 | -64.339 | -7.8875 | -66.5354 | 56.4075 | 56.2662 | 56.3489 | -66.7551 | -66.5597 | -6.126 | -66.672 | 56.2169 | 56.4312 | 56.3658 | -66.8729 | -0.13217 | -0.011869 | 2.2839 | 0.087521 | 0.21969 | -0.15319 | -0.070483 | -0.25001 | -0.20251 | 0.063267 | -0.049076 | 0.20094 | 0.011874 | -0.053604 | 123.0304 | 122.8891 | 122.9718 | 58.7354 | -123.1745 | 122.8398 | 123.0542 | 122.9887 | 60.497 | -123.2923
293.9688 | 123.2162 | -66.6 | 56.4697 | 0.048435 | -0.025536 | -0.0046504 | 0.053271 | -0.0055299 | 0.05214 | 0.07176 | -0.0056032 | -0.0027965 | 0.057941 | 0.03247 | 0.056935 | -64.3436 | -8.1256 | -66.5217 | 56.4121 | 56.2616 | 56.3535 | -66.7551 | -66.5413 | -6.3274 | -66.6583 | 56.2306 | 56.445 | 56.3749 | -66.8638 | -0.15506 | -0.057645 | 2.2564 | 0.078368 | 0.23342 | -0.20812 | -0.11626 | -0.26374 | -0.23913 | 0.058694 | -0.058228 | 0.20551 | -0.024744 | -0.094801 | 123.0121 | 122.8616 | 122.9535 | 58.4744 | -123.2248 | 122.8306 | 123.045 | 122.975 | 60.2726 | -123.3335
294.9375 | 123.2529 | -66.5909 | 56.456 | 0.063697 | -0.026605 | -0.0025134 | 0.053271 | -0.0065979 | 0.05214 | 0.056499 | -0.0045342 | -0.0027965 | 0.057941 | 0.030333 | 0.056935 | -64.3253 | -8.35 | -66.5171 | 56.4167 | 56.2708 | 56.3535 | -66.7505 | -66.5459 | -6.5106 | -66.6537 | 56.2214 | 56.4404 | 56.3658 | -66.8638 | -0.15963 | -0.039333 | 2.2656 | 0.07379 | 0.23342 | -0.18523 | -0.10252 | -0.2729 | -0.23456 | 0.04496 | -0.062805 | 0.21009 | -0.01559 | -0.090225 | 123.0075 | 122.8616 | 122.9443 | 58.2409 | -123.2065 | 122.8123 | 123.0313 | 122.9566 | 60.0803 | -123.3198
295.9375 | 123.2254 | -66.6138 | 56.4514 | 0.048435 | -0.0234 | -0.0025134 | 0.053271 | -0.0055299 | 0.051071 | 0.041238 | -0.0056032 | -0.00065947 | 0.059009 | 0.033539 | 0.058003 | -64.3253 | -8.5972 | -66.5125 | 56.4121 | 56.2708 | 56.3626 | -66.7414 | -66.5368 | -6.7075 | -66.6445 | 56.2352 | 56.4541 | 56.3749 | -66.8638 | -0.12759 | -0.039334 | 2.2885 | 0.10126 | 0.22884 | -0.18065 | -0.08879 | -0.25001 | -0.21624 | 0.077006 | -0.030759 | 0.21925 | 0.002724 | -0.07649 | 123.0259 | 122.8845 | 122.9764 | 58.0166 | -123.1928 | 122.8489 | 123.0679 | 122.9887 | 59.9063 | -123.3152
296.9375 | 123.2574 | -66.6046 | 56.4926 | 0.048435 | -0.024468 | -0.0014454 | 0.052202 | -0.0055299 | 0.05214 | 0.056499 | -0.0066712 | -0.0017285 | 0.059009 | 0.033539 | 0.058003 | -64.3116 | -8.8628 | -66.5125 | 56.4212 | 56.2753 | 56.3672 | -66.7368 | -66.5322 | -6.8998 | -66.6491 | 56.226 | 56.4541 | 56.407 | -66.8546 | -0.13216 | -0.071376 | 2.293 | 0.092101 | 0.22427 | -0.21727 | -0.12541 | -0.25001 | -0.2666 | 0.072429 | -0.044493 | 0.20551 | -0.038475 | -0.085639 | 123.0259 | 122.88 | 122.9718 | 57.7418 | -123.2294 | 122.8306 | 123.0588 | 123.0116 | 59.7049 | -123.3472
297.9375 | 123.2254 | -66.6183 | 56.4743 | 0.048435 | -0.0234 | -0.0025134 | 0.053271 | -0.0055299 | 0.051071 | 0.056499 | -0.0045342 | -0.0017285 | 0.060077 | 0.029265 | 0.055867 | -64.3024 | -9.1054 | -66.5034 | 56.4258 | 56.2708 | 56.3764 | -66.7414 | -66.5322 | -7.115 | -66.6354 | 56.2352 | 56.4541 | 56.4116 | -66.8592 | -0.12301 | -0.048487 | 2.3159 | 0.11499 | 0.238 | -0.20354 | -0.097942 | -0.24085 | -0.23913 | 0.086162 | -0.017024 | 0.22383 | -0.020164 | -0.062749 | 123.0442 | 122.8891 | 122.9947 | 57.5129 | -123.2157 | 122.8535 | 123.0725 | 123.0299 | 59.5034 | -123.3335
298.9375 | 123.2529 | -66.6458 | 56.4606 | 0.063697 | -0.025536 | -0.0025134 | 0.051134 | -0.0055299 | 0.050003 | 0.07176 | -0.0056032 | -0.0017285 | 0.057941 | 0.03247 | 0.056935 | -64.2978 | -9.3344 | -66.4988 | 56.4258 | 56.2753 | 56.3672 | -66.7414 | -66.5139 | -7.3347 | -66.6399 | 56.2214 | 56.4541 | 56.3841 | -66.8455 | -0.095543 | -0.034754 | 2.348 | 0.14704 | 0.24258 | -0.18523 | -0.093366 | -0.19965 | -0.23913 | 0.13194 | 0.005863 | 0.20551 | -0.006431 | -0.076488 | 123.0716 | 122.9212 | 123.013 | 57.3114 | -123.2019 | 122.8673 | 123.1 | 123.0299 | 59.3111 | -123.306
299.9375 | 123.2117 | -66.6 | 56.4835 | 0.048435 | -0.025536 | -0.00037739 | 0.054339 | -0.0055299 | 0.050003 | 0.087021 | -0.0056032 | -0.0027965 | 0.060077 | 0.03247 | 0.056935 | -64.2978 | -9.5816 | -66.485 | 56.4304 | 56.2799 | 56.3809 | -66.7322 | -66.5093 | -7.5545 | -66.6262 | 56.2398 | 56.4587 | 56.4207 | -66.8409 | -0.13216 | -0.053063 | 2.3022 | 0.11499 | 0.24716 | -0.20354 | -0.10252 | -0.24085 | -0.24371 | 0.090745 | -0.026177 | 0.21467 | -0.024741 | -0.062747 | 123.0304 | 122.88 | 122.981 | 57.0184 | -123.2157 | 122.8398 | 123.0588 | 123.0207 | 59.0455 | -123.3243
300.9375 | 123.2071 | -66.6 | 56.4926 | 0.048435 | -0.026605 | -0.0025134 | 0.052202 | -0.0076669 | 0.050003 | 0.07176 | -0.0045342 | -0.0038645 | 0.057941 | 0.031402 | 0.055867 | -64.2795 | -9.8243 | -66.485 | 56.4441 | 56.2891 | 56.3809 | -66.7276 | -66.5093 | -7.7697 | -66.6216 | 56.2352 | 56.4679 | 56.4024 | -66.8363 | -0.12758 | -0.048484 | 2.3205 | 0.11499 | 0.24258 | -0.20354 | -0.11167 | -0.23627 | -0.25744 | 0.090745 | -0.021598 | 0.21467 | -0.024739 | -0.090217 | 123.0442 | 122.8891 | 122.981 | 56.7758 | -123.2202 | 122.8352 | 123.0679 | 123.0024 | 58.8303 | -123.3289
301.9531 | 123.1705 | -66.5863 | 56.5018 | 0.048435 | -0.027673 | -0.0035824 | 0.052202 | -0.0076669 | 0.050003 | 0.056499 | -0.0066712 | -0.0049335 | 0.059009 | 0.033539 | 0.056935 | -64.2933 | -10.0578 | -66.4805 | 56.4304 | 56.2891 | 56.3809 | -66.7185 | -66.5093 | -7.9986 | -66.6171 | 56.2535 | 56.4679 | 56.4299 | -66.8409 | -0.13216 | -0.071374 | 2.2931 | 0.10584 | 0.238 | -0.21269 | -0.12083 | -0.25458 | -0.24828 | 0.077012 | -0.030752 | 0.22383 | -0.033894 | -0.071901 | 123.0167 | 122.8754 | 122.9672 | 56.5285 | -123.2202 | 122.8398 | 123.0542 | 123.0162 | 58.5877 | -123.3427
302.9375 | 123.2208 | -66.5955 | 56.4789 | 0.063697 | -0.026605 | -0.0025134 | 0.052202 | -0.0065979 | 0.047866 | 0.041238 | -0.0034662 | -0.0027965 | 0.057941 | 0.033539 | 0.055867 | -64.2795 | -10.3096 | -66.4713 | 56.4487 | 56.2891 | 56.3993 | -66.723 | -66.4956 | -8.223 | -66.6171 | 56.2489 | 56.477 | 56.3841 | -66.8271 | -0.12758 | -0.030173 | 2.3159 | 0.12415 | 0.25173 | -0.1898 | -0.079627 | -0.23169 | -0.22997 | 0.099903 | -0.021597 | 0.21009 | -0.001849 | -0.094799 | 123.0442 | 122.8845 | 122.9947 | 56.2859 | -123.2019 | 122.8444 | 123.0725 | 122.9795 | 58.3725 | -123.306
303.9375 | 123.2254 | -66.5817 | 56.4789 | 0.048435 | -0.025536 | -0.0025134 | 0.052202 | -0.0055299 | 0.05214 | 0.041238 | -0.0056032 | -0.0049335 | 0.057941 | 0.031402 | 0.055867 | -64.2658 | -10.5294 | -66.4622 | 56.4533 | 56.2937 | 56.3993 | -66.7093 | -66.4864 | -8.4748 | -66.6079 | 56.2626 | 56.4816 | 56.4299 | -66.8271 | -0.12758 | -0.025594 | 2.3159 | 0.11957 | 0.24715 | -0.18522 | -0.079627 | -0.24542 | -0.21624 | 0.095328 | -0.026173 | 0.21925 | 0.002729 | -0.049013 | 123.035 | 122.8754 | 122.981 | 56.0523 | -123.1882 | 122.8444 | 123.0633 | 123.0116 | 58.1069 | -123.306
304.9375 | 123.1888 | -66.5817 | 56.4972 | 0.078959 | -0.025536 | -0.0014454 | 0.053271 | -0.0055299 | 0.050003 | 0.056499 | -0.0045342 | -0.0017285 | 0.057941 | 0.03247 | 0.056935 | -64.252 | -10.7675 | -66.4576 | 56.4487 | 56.3074 | 56.3947 | -66.7139 | -66.4818 | -8.6855 | -66.5987 | 56.2672 | 56.4908 | 56.4344 | -66.8271 | -0.13216 | -0.048483 | 2.3297 | 0.12415 | 0.25631 | -0.1898 | -0.10251 | -0.24542 | -0.22997 | 0.099907 | -0.017015 | 0.22841 | -0.006423 | -0.062744 | 123.0304 | 122.8891 | 122.9764 | 55.8143 | -123.2111 | 122.8489 | 123.0725 | 123.0162 | 57.8963 | -123.3243
305.9375 | 123.23 | -66.5817 | 56.5018 | 0.078959 | -0.026605 | -0.0035824 | 0.054339 | -0.0055299 | 0.05214 | 0.056499 | -0.0045342 | -0.0027965 | 0.059009 | 0.033539 | 0.055867 | -64.2475 | -11.0193 | -66.4484 | 56.4487 | 56.3074 | 56.4084 | -66.7001 | -66.4772 | -8.9098 | -66.5896 | 56.2581 | 56.4953 | 56.4436 | -66.818 | -0.11842 | -0.053061 | 2.3343 | 0.13331 | 0.25173 | -0.19438 | -0.093358 | -0.23627 | -0.2437 | 0.10448 | -0.007858 | 0.22841 | -0.006423 | -0.058165 | 123.0304 | 122.8891 | 122.9901 | 55.5624 | -123.2019 | 122.8398 | 123.0771 | 123.0253 | 57.6719 | -123.3198
306.9531 | 123.1934 | -66.5863 | 56.5063 | 0.048435 | -0.026605 | -0.00037739 | 0.054339 | -0.0055299 | 0.051071 | 0.041238 | -0.0045342 | -0.0038645 | 0.056873 | 0.033539 | 0.054798 | -64.2429 | -11.2711 | -66.4484 | 56.467 | 56.2982 | 56.4084 | -66.6956 | -66.4681 | -9.1479 | -66.585 | 56.2535 | 56.4953 | 56.439 | -66.8134 | -0.10926 | -0.039325 | 2.3434 | 0.13789 | 0.24715 | -0.20811 | -0.097936 | -0.22711 | -0.25286 | 0.11822 | 0.001299 | 0.22841 | -0.011001 | -0.067321 | 123.0533 | 122.8845 | 122.9947 | 55.3152 | -123.2019 | 122.8398 | 123.0817 | 123.0253 | 57.4384 | -123.3198
307.9375 | 123.2391 | -66.568 | 56.5384 | 0.048435 | -0.027673 | -0.0035824 | 0.052202 | -0.0055299 | 0.051071 | 0.087021 | -0.0066712 | -0.0038645 | 0.056873 | 0.033539 | 0.056935 | -64.2337 | -11.5 | -66.4301 | 56.4716 | 56.3028 | 56.4176 | -66.691 | -66.4589 | -9.3768 | -66.585 | 56.2581 | 56.5091 | 56.4528 | -66.8088 | -0.123 | -0.06679 | 2.3343 | 0.13789 | 0.26089 | -0.23558 | -0.12082 | -0.24084 | -0.28033 | 0.10907 | -0.017012 | 0.22383 | -0.029308 | -0.085629 | 123.0396 | 122.8708 | 122.9856 | 55.068 | -123.2294 | 122.8261 | 123.0771 | 123.0208 | 57.1912 | -123.3472
308.9375 | 123.2483 | -66.568 | 56.5018 | 0.063697 | -0.028741 | -0.0035824 | 0.055407 | -0.0065979 | 0.051071 | 0.041238 | -0.0066712 | -0.0027965 | 0.055804 | 0.03247 | 0.055867 | -64.2337 | -11.7656 | -66.4301 | 56.4762 | 56.3166 | 56.4176 | -66.6956 | -66.4589 | -9.5966 | -66.5758 | 56.2672 | 56.5091 | 56.4619 | -66.8043 | -0.12757 | -0.02559 | 2.3343 | 0.13789 | 0.26546 | -0.18522 | -0.0842 | -0.23626 | -0.23455 | 0.10907 | -0.007855 | 0.22841 | 0.007313 | -0.03985 | 123.0442 | 122.8845 | 122.9856 | 54.8024 | -123.1973 | 122.8352 | 123.0771 | 123.0299 | 56.9714 | -123.306
309.9688 | 123.2346 | -66.5909 | 56.5109 | 0.048435 | -0.027673 | -0.0035824 | 0.054339 | -0.0065979 | 0.051071 | 0.041238 | -0.0066712 | -0.0027965 | 0.056873 | 0.033539 | 0.055867 | -64.2246 | -12.0495 | -66.4209 | 56.4853 | 56.3166 | 56.4221 | -66.6818 | -66.4452 | -9.8347 | -66.5575 | 56.2764 | 56.5137 | 56.4573 | -66.8043 | -0.090949 | -0.025589 | 2.3663 | 0.16993 | 0.26088 | -0.19437 | -0.088777 | -0.21337 | -0.23455 | 0.14569 | 0.033348 | 0.24672 | 0.002737 | -0.053584 | 123.0762 | 122.9074 | 123.013 | 54.5414 | -123.1928 | 122.8673 | 123.1045 | 123.0482 | 56.7562 | -123.3152
310.9375 | 123.7747 | -66.5771 | 56.5109 | 0.048435 | -0.026605 | -0.0025134 | 0.053271 | -0.0065979 | 0.050003 | 0.056499 | -0.0045342 | -0.0038645 | 0.057941 | 0.034607 | 0.054798 | -63.8675 | -12.2464 | -66.3111 | 56.4808 | 56.3303 | 56.4267 | -66.6818 | -66.4956 | -9.8759 | -66.553 | 56.281 | 56.5137 | 56.4665 | -66.7905 | -0.10468 | -0.030167 | 2.7097 | 0.26608 | 0.37076 | -0.18064 | -0.084198 | -0.21337 | -0.22997 | 0.081592 | 0.024194 | 0.23756 | 0.002737 | -0.044427 | 123.0579 | 122.9074 | 123.0039 | 54.3308 | -123.1928 | 122.8581 | 123.0908 | 123.0436 | 56.7012 | -123.3014
311.9531 | 123.7152 | -66.5588 | 56.5063 | 0.033173 | -0.028741 | -0.0035824 | 0.053271 | -0.0076669 | 0.050003 | 0.056499 | -0.0066712 | -0.0049335 | 0.059009 | 0.034607 | 0.055867 | -63.8949 | -12.5485 | -66.334 | 56.4808 | 56.3303 | 56.4267 | -66.6681 | -66.4635 | -10.1506 | -66.5209 | 56.2855 | 56.5182 | 56.4665 | -66.7905 | -0.10926 | -0.02559 | 2.6639 | 0.22488 | 0.33413 | -0.17606 | -0.079621 | -0.23168 | -0.22081 | 0.095333 | 0.037935 | 0.26962 | 0.011892 | -0.03985 | 123.0396 | 122.8891 | 122.9856 | 54.0103 | -123.1744 | 122.8444 | 123.0771 | 123.0253 | 56.4082 | -123.2969
312.9375 | 124.0952 | -66.5451 | 56.5292 | 0.078959 | -0.028741 | -0.0035824 | 0.052202 | -0.0055299 | 0.050003 | 0.041238 | -0.0066712 | -0.0027965 | 0.056873 | 0.034607 | 0.056935 | -64.1239 | -12.8645 | -66.3569 | 56.4899 | 56.3394 | 56.4405 | -66.6681 | -66.4131 | -10.3979 | -66.466 | 56.2993 | 56.5137 | 56.4802 | -66.7905 | -0.12299 | -0.039321 | 2.4213 | 0.18825 | 0.31124 | -0.18979 | -0.088773 | -0.24541 | -0.22996 | 0.13197 | 0.079146 | 0.32456 | -0.015574 | -0.049002 | 123.035 | 122.8846 | 122.9856 | 53.6806 | -123.1973 | 122.8444 | 123.0588 | 123.0253 | 56.1472 | -123.3198
313.9375 | 123.2483 | -66.5359 | 56.5155 | 0.048435 | -0.028741 | -0.0025134 | 0.053271 | -0.0076669 | 0.050003 | 0.056499 | -0.0056032 | -0.0038645 | 0.059009 | 0.033539 | 0.055867 | -64.1925 | -13.217 | -66.3843 | 56.4991 | 56.3394 | 56.4496 | -66.6635 | -66.4223 | -10.6818 | -66.5346 | 56.3084 | 56.5228 | 56.4848 | -66.7768 | -0.12757 | -0.016431 | 2.3434 | 0.15163 | 0.27919 | -0.17606 | -0.065883 | -0.24083 | -0.20707 | 0.11365 | 0.001311 | 0.24214 | 0.007316 | -0.03069 | 123.035 | 122.8754 | 122.9856 | 53.3189 | -123.179 | 122.8444 | 123.0588 | 123.0208 | 55.8542 | -123.2923
314.9531 | 123.3398 | -66.4948 | 56.5201 | 0.033173 | -0.028741 | -0.0025134 | 0.053271 | -0.0055299 | 0.05214 | 0.07176 | -0.0045342 | -0.0049335 | 0.057941 | 0.033539 | 0.054798 | -64.2429 | -13.5009 | -66.3797 | 56.4945 | 56.3578 | 56.4496 | -66.6544 | -66.4177 | -10.9244 | -66.5346 | 56.3038 | 56.532 | 56.4894 | -66.7814 | -0.15961 | -0.025588 | 2.2519 | 0.11501 | 0.27462 | -0.16232 | -0.070461 | -0.28661 | -0.21623 | 0.077033 | -0.039888 | 0.24672 | 0.011895 | -0.03069 | 122.9892 | 122.8525 | 122.9444 | 52.9939 | -123.1744 | 122.7986 | 123.0267 | 122.9841 | 55.5703 | -123.3014
315.9375 | 123.2346 | -66.5359 | 56.5338 | 0.048435 | -0.02981 | -0.0046504 | 0.053271 | -0.0065979 | 0.050003 | 0.087021 | -0.0066712 | -0.0049335 | 0.057941 | 0.034607 | 0.05373 | -64.1834 | -13.7802 | -66.3706 | 56.5128 | 56.3532 | 56.4496 | -66.6498 | -66.3994 | -11.19 | -66.5209 | 56.3176 | 56.5366 | 56.4802 | -66.7768 | -0.11383 | -0.021006 | 2.3526 | 0.16536 | 0.27919 | -0.18063 | -0.084193 | -0.24083 | -0.21623 | 0.13655 | 0.015047 | 0.25588 | 0.002742 | -0.053579 | 123.0488 | 122.8891 | 122.9856 | 52.7558 | -123.1836 | 122.8535 | 123.0725 | 123.0162 | 55.3459 | -123.3106
316.9531 | 123.2117 | -66.4993 | 56.5842 | 0.048435 | -0.02981 | -0.0025134 | 0.052202 | -0.0065979 | 0.05214 | 0.07176 | -0.0045342 | -0.0038645 | 0.057941 | 0.034607 | 0.054798 | -64.1971 | -14.0778 | -66.366 | 56.5128 | 56.3578 | 56.4634 | -66.6406 | -66.3857 | -11.4739 | -66.5117 | 56.3267 | 56.5457 | 56.494 | -66.7722 | -0.14129 | -0.07136 | 2.3022 | 0.13332 | 0.27461 | -0.2264 | -0.12081 | -0.27287 | -0.25742 | 0.11366 | -0.012417 | 0.26046 | -0.038455 | -0.090197 | 123.0121 | 122.8571 | 122.9627 | 52.4215 | -123.2248 | 122.8261 | 123.045 | 122.9933 | 55.0254 | -123.3564
317.9375 | 123.1934 | -66.5497 | 56.5613 | 0.063697 | -0.027673 | -0.0014454 | 0.052202 | -0.0076669 | 0.047866 | 0.056499 | -0.0056032 | -0.0027965 | 0.057941 | 0.034607 | 0.056935 | -64.1788 | -14.3708 | -66.3523 | 56.5174 | 56.3669 | 56.4679 | -66.636 | -66.3857 | -11.6937 | -66.5072 | 56.3313 | 56.5503 | 56.4619 | -66.7676 | -0.086358 | -0.043894 | 2.3709 | 0.19741 | 0.28377 | -0.19436 | -0.093345 | -0.21794 | -0.22996 | 0.16402 | 0.042516 | 0.26046 | -0.010989 | -0.099359 | 123.0671 | 122.9166 | 123.0176 | 52.1789 | -123.1973 | 122.881 | 123.1 | 123.0116 | 54.856 | -123.3289
318.9375 | 123.2483 | -66.5085 | 56.5659 | 0.048435 | -0.027673 | -0.0035824 | 0.053271 | -0.0076669 | 0.050003 | 0.07176 | -0.0045342 | -0.0038645 | 0.057941 | 0.034607 | 0.056935 | -64.0323 | -14.6684 | -66.4209 | 56.5265 | 56.3669 | 56.4725 | -66.636 | -66.3261 | -11.6937 | -66.4614 | 56.3405 | 56.5549 | 56.5031 | -66.7539 | -0.12756 | -0.039315 | 2.4762 | 0.087537 | 0.21509 | -0.19894 | -0.093344 | -0.2454 | -0.22538 | 0.18234 | 0.047104 | 0.29251 | -0.010988 | -0.06273 | 123.035 | 122.8754 | 122.981 | 51.84 | -123.2019 | 122.849 | 123.0634 | 123.0116 | 54.8148 | -123.3197
319.9375 | 123.7885 | -66.4856 | 56.5384 | 0.048435 | -0.02981 | -0.0025134 | 0.052202 | -0.0087349 | 0.050003 | 0.056499 | -0.0066712 | -0.0038645 | 0.057941 | 0.035675 | 0.054798 | -63.6294 | -14.9065 | -66.4164 | 56.522 | 56.3761 | 56.4725 | -66.636 | -66.2712 | -11.6067 | -66.4751 | 56.3496 | 56.5594 | 56.5077 | -66.7447 | -0.15045 | -0.016427 | 2.8562 | 0.069227 | 0.21967 | -0.16231 | -0.065878 | -0.25913 | -0.18876 | 0.2144 | 0.01048 | 0.26961 | 0.021057 | -0.030685 | 123.0076 | 122.8617 | 122.9581 | 51.5791 | -123.1744 | 122.8352 | 123.045 | 122.9933 | 54.8789 | -123.2831
320.9375 | 123.8068 | -66.4856 | 56.5659 | 0.033173 | -0.028741 | -0.0035824 | 0.052202 | -0.0076669 | 0.050003 | 0.056499 | -0.0056032 | -0.0038645 | 0.057941 | 0.035675 | 0.055867 | -63.6157 | -15.1812 | -66.3981 | 56.5357 | 56.3852 | 56.4817 | -66.6315 | -66.2666 | -11.8951 | -66.466 | 56.3496 | 56.5549 | 56.526 | -66.7356 | -0.14587 | -0.030158 | 2.8699 | 0.087541 | 0.23341 | -0.18062 | -0.084187 | -0.24998 | -0.21622 | 0.21898 | 0.019637 | 0.26961 | -0.010988 | -0.039837 | 123.0213 | 122.8708 | 122.9673 | 51.3044 | -123.1973 | 122.8352 | 123.0405 | 123.0116 | 54.5905 | -123.3014
321.9531 | 123.6328 | -66.5085 | 56.5842 | 0.063697 | -0.02981 | -0.0014454 | 0.051134 | -0.0076669 | 0.050003 | 0.07176 | -0.0056032 | -0.0049335 | 0.056873 | 0.036744 | 0.054798 | -63.5836 | -15.488 | -66.3752 | 56.5357 | 56.3898 | 56.4908 | -66.6177 | -66.2483 | -12.1103 | -66.4614 | 56.3451 | 56.564 | 56.526 | -66.7402 | -0.10924 | -0.048468 | 2.9249 | 0.13332 | 0.24256 | -0.19435 | -0.09334 | -0.23167 | -0.23911 | 0.26018 | 0.047104 | 0.27877 | -0.020141 | -0.058147 | 123.0442 | 122.8983 | 122.9993 | 51.0205 | -123.2019 | 122.8535 | 123.0725 | 123.0345 | 54.3982 | -123.3243
322.9375 | 123.2437 | -66.5085 | 56.575 | 0.063697 | -0.028741 | -0.0025134 | 0.053271 | -0.0076669 | 0.050003 | 0.041238 | -0.0066712 | -0.0038645 | 0.060077 | 0.035675 | 0.056935 | -64.1101 | -15.8131 | -66.3065 | 56.5403 | 56.3898 | 56.5 | -66.6131 | -66.3536 | -12.9437 | -66.4614 | 56.3542 | 56.5823 | 56.5398 | -66.7356 | -0.10466 | -0.034735 | 2.3984 | 0.20199 | 0.30666 | -0.1852 | -0.075028 | -0.22709 | -0.2208 | 0.15487 | 0.047104 | 0.27419 | 0.007329 | -0.035256 | 123.0488 | 122.8983 | 123.0085 | 50.6954 | -123.1882 | 122.8627 | 123.0908 | 123.0482 | 53.5648 | -123.3106
323.9844 | 123.2391 | -66.4764 | 56.6208 | 0.063697 | -0.027673 | -0.0025134 | 0.051134 | -0.0087349 | 0.051071 | 0.07176 | -0.0045342 | -0.0038645 | 0.056873 | 0.036744 | 0.055867 | -64.1147 | -16.1061 | -66.2973 | 56.5494 | 56.399 | 56.4954 | -66.6086 | -66.3261 | -13.2321 | -66.4476 | 56.3542 | 56.5823 | 56.5214 | -66.7218 | -0.13213 | -0.071355 | 2.3617 | 0.17911 | 0.31124 | -0.22182 | -0.12538 | -0.2454 | -0.26658 | 0.1503 | 0.028796 | 0.27419 | -0.038448 | -0.099347 | 123.0259 | 122.8754 | 122.9718 | 50.3703 | -123.2294 | 122.8307 | 123.0588 | 122.9979 | 53.2443 | -123.3426
324.9375 | 123.2666 | -66.449 | 56.5613 | 0.063697 | -0.028741 | -0.0035824 | 0.052202 | -0.0065979 | 0.050003 | 0.07176 | -0.0056032 | -0.0049335 | 0.059009 | 0.037812 | 0.054798 | -64.1971 | -16.4037 | -66.2836 | 56.5586 | 56.399 | 56.5046 | -66.6086 | -66.317 | -13.4427 | -66.4476 | 56.3634 | 56.5869 | 56.4894 | -66.731 | -0.15959 | -0.002688 | 2.2519 | 0.16538 | 0.32497 | -0.16231 | -0.056716 | -0.28202 | -0.19791 | 0.13199 | 0.001331 | 0.28335 | 0.02564 | -0.071888 | 123.0076 | 122.8479 | 122.9535 | 50.0452 | -123.1698 | 122.8123 | 123.0359 | 122.9384 | 53.0062 | -123.2923
325.9375 | 123.2346 | -66.4581 | 56.6208 | 0.048435 | -0.027673 | -0.0025134 | 0.051134 | -0.0055299 | 0.051071 | 0.041238 | -0.0045342 | -0.0017285 | 0.057941 | 0.036744 | 0.056935 | -64.0826 | -16.6876 | -66.2836 | 56.5632 | 56.4127 | 56.5091 | -66.6086 | -66.3033 | -13.69 | -66.4339 | 56.3863 | 56.5915 | 56.494 | -66.7218 | -0.15044 | -0.05762 | 2.3755 | 0.17453 | 0.32497 | -0.20808 | -0.11165 | -0.26371 | -0.23453 | 0.15488 | 0.024222 | 0.28793 | -0.029291 | -0.12682 | 123.0213 | 122.8708 | 122.9673 | 49.7705 | -123.2294 | 122.8444 | 123.0496 | 122.9521 | 52.7681 | -123.3426
326.9531 | 123.2483 | -66.5085 | 56.5567 | 0.048435 | -0.02981 | -0.0025134 | 0.053271 | -0.0065979 | 0.050003 | 0.056499 | -0.0066712 | -0.0049335 | 0.057941 | 0.036744 | 0.056935 | -64.0872 | -16.9806 | -66.2653 | 56.5677 | 56.4173 | 56.5137 | -66.5994 | -66.3033 | -13.9418 | -66.4202 | 56.3725 | 56.5961 | 56.5169 | -66.7127 | -0.090926 | 0.011045 | 2.4213 | 0.2432 | 0.33413 | -0.13941 | -0.042982 | -0.20419 | -0.18417 | 0.20523 | 0.088312 | 0.29251 | 0.039374 | -0.039839 | 123.0762 | 122.9258 | 123.0222 | 49.5279 | -123.1561 | 122.881 | 123.1046 | 123.0253 | 52.5667 | -123.2694
327.9375 | 123.2483 | -66.4627 | 56.6254 | 0.063697 | -0.027673 | -0.0025134 | 0.051134 | -0.0065979 | 0.050003 | 0.056499 | -0.0056032 | -0.0027965 | 0.056873 | 0.036744 | 0.054798 | -64.0689 | -17.2233 | -66.2607 | 56.5723 | 56.4264 | 56.5183 | -66.5857 | -66.2941 | -14.1799 | -66.4248 | 56.3954 | 56.6007 | 56.5214 | -66.7127 | -0.12296 | -0.05304 | 2.3938 | 0.202 | 0.32497 | -0.19892 | -0.10707 | -0.24997 | -0.22995 | 0.16862 | 0.037958 | 0.28793 | -0.024711 | -0.10392 | 123.035 | 122.8892 | 122.981 | 49.2394 | -123.211 | 122.8581 | 123.0634 | 122.9841 | 52.2828 | -123.338
328.9688 | 123.2574 | -66.4673 | 56.5704 | 0.048435 | -0.028741 | -0.00037739 | 0.052202 | -0.0065979 | 0.050003 | 0.041238 | -0.0056032 | -0.0038645 | 0.056873 | 0.035675 | 0.055867 | -64.0964 | -17.5575 | -66.2516 | 56.5723 | 56.4264 | 56.532 | -66.5811 | -66.2849 | -14.4684 | -66.4064 | 56.4 | 56.6098 | 56.5626 | -66.7081 | -0.11381 | 0.001891 | 2.3709 | 0.21573 | 0.32954 | -0.14399 | -0.0384 | -0.24081 | -0.17044 | 0.18235 | 0.060849 | 0.30166 | 0.039377 | -0.007786 | 123.0396 | 122.8937 | 122.9993 | 48.9098 | -123.1515 | 122.8673 | 123.0771 | 123.0299 | 51.9989 | -123.2785
329.9375 | 123.3307 | -66.4444 | 56.5704 | 0.033173 | -0.02981 | -0.0025134 | 0.052202 | -0.0087349 | 0.05214 | 0.041238 | -0.0056032 | -0.0038645 | 0.056873 | 0.036744 | 0.055867 | -64.0964 | -17.8414 | -66.2424 | 56.5815 | 56.4264 | 56.532 | -66.5811 | -66.2758 | -14.679 | -66.3973 | 56.4092 | 56.6144 | 56.5535 | -66.6989 | -0.1367 | 0.011048 | 2.348 | 0.202 | 0.3387 | -0.14399 | -0.0384 | -0.25454 | -0.16128 | 0.16862 | 0.047119 | 0.30166 | 0.043956 | -0.016943 | 123.0259 | 122.8708 | 122.9764 | 48.603 | -123.1515 | 122.8536 | 123.0588 | 122.9979 | 51.7654 | -123.2694
330.9375 | 123.23 | -66.4261 | 56.6162 | 0.063697 | -0.030878 | -0.0014454 | 0.052202 | -0.0065979 | 0.051071 | 0.07176 | -0.0066712 | -0.0038645 | 0.057941 | 0.036744 | 0.054798 | -64.0369 | -18.0978 | -66.2332 | 56.5906 | 56.4356 | 56.5458 | -66.5857 | -66.2712 | -14.9674 | -66.3881 | 56.3954 | 56.6235 | 56.581 | -66.7035 | -0.15959 | -0.025572 | 2.3892 | 0.19285 | 0.35244 | -0.18061 | -0.070441 | -0.27743 | -0.22079 | 0.15489 | 0.037965 | 0.3154 | 0.007337 | -0.035248 | 123.0167 | 122.8617 | 122.9719 | 48.3283 | -123.2019 | 122.8215 | 123.0496 | 123.007 | 51.4586 | -123.3197
331.9531 | 123.1934 | -66.4307 | 56.6391 | 0.063697 | -0.02981 | -0.0014454 | 0.053271 | -0.0076669 | 0.051071 | 0.07176 | -0.0045342 | -0.0049335 | 0.056873 | 0.037812 | 0.055867 | -64.0918 | -18.4 | -66.2149 | 56.5906 | 56.4493 | 56.5458 | -66.5719 | -66.2529 | -15.2284 | -66.3744 | 56.4046 | 56.6281 | 56.5764 | -66.6898 | -0.14127 | -0.04846 | 2.3389 | 0.21574 | 0.35701 | -0.18976 | -0.093329 | -0.25912 | -0.23452 | 0.17778 | 0.056279 | 0.3154 | -0.010972 | -0.062714 | 123.0213 | 122.88 | 122.9764 | 48.0307 | -123.211 | 122.8352 | 123.0588 | 123.007 | 51.2022 | -123.3289
332.9375 | 123.2254 | -66.4398 | 56.6528 | 0.063697 | -0.028741 | -0.0014454 | 0.053271 | -0.0065979 | 0.050003 | 0.07176 | -0.0056032 | -0.0038645 | 0.060077 | 0.037812 | 0.054798 | -64.0643 | -18.6976 | -66.2103 | 56.5998 | 56.4448 | 56.5503 | -66.5582 | -66.2483 | -15.4024 | -66.3652 | 56.4 | 56.6327 | 56.5535 | -66.6852 | -0.11838 | -0.053036 | 2.3755 | 0.22947 | 0.34785 | -0.20807 | -0.10248 | -0.24539 | -0.25283 | 0.19151 | 0.074592 | 0.31998 | -0.020127 | -0.09934 | 123.0396 | 122.8846 | 122.9902 | 47.7422 | -123.211 | 122.8398 | 123.0725 | 122.9933 | 51.0374 | -123.338
333.9688 | 123.2162 | -66.4398 | 56.6254 | 0.063697 | -0.028741 | -0.0014454 | 0.054339 | -0.0055299 | 0.048935 | 0.056499 | -0.0066712 | -0.0049335 | 0.057941 | 0.036744 | 0.055867 | -64.0552 | -18.9586 | -66.2058 | 56.6044 | 56.4539 | 56.5549 | -66.5628 | -66.2391 | -15.7092 | -66.3561 | 56.4046 | 56.6327 | 56.5581 | -66.6806 | -0.12296 | -0.020991 | 2.3846 | 0.23405 | 0.35701 | -0.17145 | -0.070438 | -0.24081 | -0.22079 | 0.20067 | 0.083749 | 0.32456 | 0.007339 | -0.067296 | 123.0442 | 122.8937 | 122.9947 | 47.4812 | -123.1881 | 122.8444 | 123.0725 | 122.9979 | 50.7306 | -123.306
334.9375 | 123.2254 | -66.4124 | 56.6483 | 0.078959 | -0.030878 | -0.0014454 | 0.052202 | -0.0065979 | 0.05214 | 0.087021 | -0.0056032 | -0.0027965 | 0.057941 | 0.037812 | 0.055867 | -64.0369 | -19.2013 | -66.1875 | 56.6135 | 56.4539 | 56.5549 | -66.5582 | -66.2208 | -15.9656 | -66.3515 | 56.4092 | 56.6419 | 56.5855 | -66.6715 | -0.14585 | -0.034723 | 2.3755 | 0.2249 | 0.37074 | -0.19433 | -0.093326 | -0.25912 | -0.2391 | 0.19152 | 0.060863 | 0.31998 | -0.006392 | -0.062712 | 123.0259 | 122.8663 | 122.9673 | 47.2111 | -123.2065 | 122.8215 | 123.0542 | 122.9979 | 50.4468 | -123.3197
335.9375 | 124.7589 | -66.4032 | 56.6528 | 0.017911 | -0.02981 | -0.0014454 | 0.052202 | -0.0065979 | 0.053208 | 0.07176 | -0.0045342 | -0.0027965 | 0.055804 | 0.035675 | 0.054798 | -63.1532 | -19.3752 | -65.9219 | 56.6044 | 56.4585 | 56.5641 | -66.5445 | -66.2346 | -16.1625 | -66.3469 | 56.4275 | 56.6556 | 56.5947 | -66.6715 | -0.14126 | -0.048457 | 3.25 | 0.48128 | 0.62255 | -0.19433 | -0.088747 | -0.26827 | -0.22536 | 0.16863 | 0.056286 | 0.32456 | 0.002766 | -0.058133 | 123.0076 | 122.8617 | 122.9673 | 47.028 | -123.1973 | 122.8307 | 123.0588 | 122.9979 | 50.2407 | -123.3243
336.9688 | 124.7406 | -66.394 | 56.6528 | 0.094221 | -0.030878 | -0.00037739 | 0.052202 | -0.0087349 | 0.051071 | 0.07176 | -0.0066712 | -0.0027965 | 0.057941 | 0.036744 | 0.05373 | -63.0525 | -19.6683 | -65.9311 | 56.6135 | 56.4631 | 56.5687 | -66.5399 | -66.2117 | -16.4097 | -66.3332 | 56.4275 | 56.651 | 56.5993 | -66.6623 | -0.14584 | -0.039301 | 3.3415 | 0.46297 | 0.60881 | -0.18975 | -0.084169 | -0.26827 | -0.22536 | 0.18237 | 0.060867 | 0.32914 | -0.001812 | -0.053554 | 123.0076 | 122.8571 | 122.9627 | 46.7258 | -123.1927 | 122.8215 | 123.0451 | 122.9933 | 49.9843 | -123.3151
337.9375 | 124.7864 | -66.4078 | 56.6483 | 0.078959 | -0.033015 | -0.0025134 | 0.052202 | -0.0065979 | 0.050003 | 0.041238 | -0.0066712 | -0.0027965 | 0.059009 | 0.037812 | 0.055867 | -63.0159 | -19.9064 | -65.9128 | 56.6181 | 56.4768 | 56.5824 | -66.5399 | -66.1888 | -16.6661 | -66.3286 | 56.432 | 56.6556 | 56.5855 | -66.6669 | -0.13211 | -0.030144 | 3.3919 | 0.49502 | 0.62713 | -0.17144 | -0.065855 | -0.25911 | -0.21621 | 0.21899 | 0.079178 | 0.33829 | 0.007344 | -0.062712 | 123.0259 | 122.8846 | 122.9902 | 46.5014 | -123.1881 | 122.8398 | 123.0634 | 122.9933 | 49.7416 | -123.3151
338.9688 | 124.6353 | -66.3895 | 56.6757 | 0.048435 | -0.02981 | -0.0014454 | 0.051134 | -0.0076669 | 0.048935 | 0.056499 | -0.0066712 | -0.0049335 | 0.055804 | 0.036744 | 0.056935 | -62.9747 | -20.2681 | -65.8853 | 56.6227 | 56.4722 | 56.587 | -66.5353 | -66.1705 | -16.8447 | -66.3103 | 56.4366 | 56.6648 | 56.613 | -66.6532 | -0.14584 | -0.053032 | 3.4148 | 0.50418 | 0.65002 | -0.20349 | -0.088742 | -0.26369 | -0.23909 | 0.219 | 0.079182 | 0.34287 | -0.010965 | -0.062706 | 123.0122 | 122.8617 | 122.9764 | 46.1214 | -123.211 | 122.8261 | 123.0542 | 123.0025 | 49.5448 | -123.3289
339.9375 | 124.2508 | -66.3803 | 56.694 | 0.048435 | -0.030878 | -0.0014454 | 0.051134 | -0.0044619 | 0.048935 | 0.07176 | -0.0066712 | -0.0038645 | 0.057941 | 0.036744 | 0.056935 | -63.2631 | -20.6206 | -66.0226 | 56.6227 | 56.4722 | 56.5778 | -66.5216 | -66.2254 | -16.95 | -66.2828 | 56.4412 | 56.6693 | 56.6039 | -66.6532 | -0.14126 | -0.071343 | 3.1172 | 0.35767 | 0.49893 | -0.2218 | -0.11621 | -0.27284 | -0.25283 | 0.1549 | 0.0975 | 0.37034 | -0.024697 | -0.090175 | 123.003 | 122.8525 | 122.9581 | 45.7597 | -123.2156 | 122.8215 | 123.0496 | 122.9842 | 49.4303 | -123.3472
340.9375 | 124.6765 | -66.3803 | 56.7078 | 0.048435 | -0.030878 | -0.0014454 | 0.053271 | -0.0076669 | 0.050003 | 0.056499 | -0.0056032 | -0.0038645 | 0.056873 | 0.037812 | 0.058003 | -63.1807 | -20.8724 | -65.9448 | 56.6273 | 56.4814 | 56.5916 | -66.5124 | -66.317 | -17.3438 | -66.2324 | 56.4275 | 56.6693 | 56.581 | -66.644 | -0.1321 | -0.080498 | 3.1996 | 0.4355 | 0.5676 | -0.22637 | -0.11621 | -0.26369 | -0.28029 | 0.063324 | 0.14786 | 0.41155 | -0.03843 | -0.1268 | 123.0076 | 122.8617 | 122.9719 | 45.5079 | -123.2202 | 122.8078 | 123.0496 | 122.9613 | 49.0365 | -123.3518
341.9375 | 124.4934 | -66.3712 | 56.6986 | 0.063697 | -0.031946 | -0.0025134 | 0.054339 | -0.0065979 | 0.050003 | 0.087021 | -0.0066712 | -0.0038645 | 0.057941 | 0.037812 | 0.05373 | -63.0525 | -21.2021 | -65.9311 | 56.641 | 56.4906 | 56.5916 | -66.5216 | -66.3353 | -17.6048 | -66.2233 | 56.4458 | 56.6739 | 56.6222 | -66.6348 | -0.15041 | -0.057606 | 3.3186 | 0.44008 | 0.5905 | -0.20806 | -0.10705 | -0.26368 | -0.25282 | 0.035854 | 0.14787 | 0.41155 | -0.024695 | -0.076437 | 123.0122 | 122.8617 | 122.9627 | 45.1691 | -123.2202 | 122.8169 | 123.0451 | 122.9933 | 48.7664 | -123.3334
342.9375 | 124.205 | -66.362 | 56.6208 | 0.048435 | -0.02981 | -0.00037739 | 0.052202 | -0.0065979 | 0.051071 | 0.056499 | -0.0045342 | -0.0038645 | 0.057941 | 0.037812 | 0.054798 | -63.5561 | -21.5501 | -65.8303 | 56.6364 | 56.486 | 56.6007 | -66.5078 | -66.3399 | -17.8429 | -66.2828 | 56.4412 | 56.6831 | 56.6222 | -66.6348 | -0.14583 | 0.015634 | 2.8059 | 0.53165 | 0.67748 | -0.13482 | -0.020075 | -0.27284 | -0.17958 | 0.022121 | 0.07919 | 0.35203 | 0.062281 | 0.001382 | 122.9984 | 122.848 | 122.9627 | 44.8119 | -123.1286 | 122.8032 | 123.0451 | 122.9842 | 48.5191 | -123.2556
343.9688 | 123.1659 | -66.3895 | 56.7123 | 0.063697 | -0.031946 | -0.0025134 | 0.051134 | -0.0065979 | 0.050003 | 0.07176 | -0.0056032 | -0.0027965 | 0.056873 | 0.037812 | 0.055867 | -63.9087 | -21.9438 | -66.0959 | 56.6547 | 56.4906 | 56.6099 | -66.5078 | -66.143 | -18.1817 | -66.2645 | 56.4412 | 56.6876 | 56.6405 | -66.6303 | -0.11837 | -0.057604 | 2.4808 | 0.29358 | 0.41194 | -0.22179 | -0.10247 | -0.24079 | -0.27114 | 0.24647 | 0.12497 | 0.36576 | -0.024693 | -0.071856 | 123.0442 | 122.88 | 122.9993 | 44.4456 | -123.2202 | 122.8307 | 123.0771 | 123.0299 | 48.2078 | -123.3426
344.9375 | 123.2574 | -66.3712 | 56.7261 | 0.063697 | -0.031946 | -0.0014454 | 0.054339 | -0.0065979 | 0.048935 | 0.07176 | -0.0066712 | -0.0038645 | 0.056873 | 0.037812 | 0.054798 | -63.9041 | -22.2002 | -66.0913 | 56.6547 | 56.5043 | 56.6053 | -66.5033 | -66.1338 | -18.374 | -66.2599 | 56.4549 | 56.6922 | 56.6405 | -66.6303 | -0.1321 | -0.071337 | 2.4671 | 0.27984 | 0.41194 | -0.22179 | -0.12078 | -0.2591 | -0.27113 | 0.23732 | 0.11124 | 0.37034 | -0.033847 | -0.085589 | 123.0259 | 122.8754 | 122.9764 | 44.1709 | -123.2293 | 122.8261 | 123.0634 | 123.0116 | 47.9972 | -123.3563
345.9375 | 123.2346 | -66.3483 | 56.7123 | 0.063697 | -0.031946 | -0.0025134 | 0.052202 | -0.0065979 | 0.048935 | 0.056499 | -0.0066712 | -0.0038645 | 0.057941 | 0.03888 | 0.054798 | -63.8858 | -22.5757 | -66.0776 | 56.6547 | 56.5089 | 56.6236 | -66.5033 | -66.1247 | -18.6899 | -66.2508 | 56.4641 | 56.7014 | 56.6496 | -66.6211 | -0.15498 | -0.057604 | 2.4625 | 0.27069 | 0.42568 | -0.20347 | -0.088734 | -0.27283 | -0.24824 | 0.22359 | 0.097508 | 0.37034 | -0.010957 | -0.062699 | 123.003 | 122.8571 | 122.9719 | 43.7726 | -123.2156 | 122.8124 | 123.0497 | 122.9979 | 47.6583 | -123.3334
346.9375 | 123.2025 | -66.3712 | 56.7352 | 0.063697 | -0.031946 | -0.0014454 | 0.053271 | -0.0065979 | 0.047866 | 0.07176 | -0.0045342 | -0.0049335 | 0.057941 | 0.03888 | 0.054798 | -63.927 | -22.8504 | -66.0638 | 56.6685 | 56.518 | 56.6144 | -66.4987 | -66.0972 | -18.9418 | -66.2416 | 56.4824 | 56.706 | 56.6496 | -66.6119 | -0.12752 | -0.066757 | 2.4442 | 0.30731 | 0.43483 | -0.2172 | -0.12078 | -0.24079 | -0.25282 | 0.27395 | 0.12955 | 0.37034 | -0.029266 | -0.085587 | 123.0396 | 122.8892 | 122.9856 | 43.5208 | -123.2339 | 122.8536 | 123.0771 | 123.0208 | 47.4294 | -123.3472
347.9375 | 123.262 | -66.3574 | 56.7398 | 0.063697 | -0.033015 | -0.0025134 | 0.051134 | -0.0076669 | 0.048935 | 0.07176 | -0.0077392 | -0.0038645 | 0.056873 | 0.03888 | 0.056935 | -63.9178 | -23.148 | -66.0501 | 56.6731 | 56.518 | 56.6328 | -66.4941 | -66.1064 | -19.1753 | -66.2187 | 56.4961 | 56.7014 | 56.6359 | -66.6074 | -0.13667 | -0.066757 | 2.4396 | 0.30732 | 0.44399 | -0.22178 | -0.10704 | -0.24994 | -0.24366 | 0.25106 | 0.13871 | 0.38866 | -0.038423 | -0.1039 | 123.0305 | 122.8754 | 122.9902 | 43.2094 | -123.2339 | 122.8536 | 123.0588 | 122.9933 | 47.1821 | -123.3472
348.9688 | 123.3444 | -66.3254 | 56.6803 | 0.048435 | -0.033015 | -0.0014454 | 0.052202 | -0.0076669 | 0.047866 | 0.087021 | -0.0066712 | -0.0038645 | 0.056873 | 0.03888 | 0.05373 | -63.9545 | -23.4181 | -66.0409 | 56.6776 | 56.5226 | 56.6328 | -66.4804 | -66.0835 | -19.4317 | -66.2141 | 56.5007 | 56.7197 | 56.5718 | -66.6119 | -0.15498 | -0.002669 | 2.3709 | 0.28443 | 0.43941 | -0.15769 | -0.047534 | -0.28657 | -0.17957 | 0.24191 | 0.11125 | 0.39781 | 0.039401 | -0.10849 | 123.003 | 122.848 | 122.9581 | 42.9072 | -123.1607 | 122.8261 | 123.0451 | 122.8972 | 46.8937 | -123.2922
349.9375 | 123.2208 | -66.3391 | 56.7627 | 0.063697 | -0.031946 | -0.0035824 | 0.051134 | -0.0087349 | 0.05214 | 0.056499 | -0.0056032 | -0.0027965 | 0.056873 | 0.03888 | 0.055867 | -63.8949 | -23.702 | -66.0364 | 56.6868 | 56.5363 | 56.6373 | -66.4895 | -66.0743 | -19.7339 | -66.205 | 56.5236 | 56.7197 | 56.6725 | -66.5982 | -0.1504 | -0.075909 | 2.4442 | 0.30274 | 0.45314 | -0.22635 | -0.12535 | -0.2591 | -0.23908 | 0.2648 | 0.13414 | 0.39324 | -0.042996 | -0.09016 | 123.0259 | 122.8755 | 122.9765 | 42.6371 | -123.2522 | 122.8627 | 123.0588 | 123.0116 | 46.6052 | -123.3609
350.9375 | 123.2574 | -66.3437 | 56.7444 | 0.048435 | -0.031946 | -0.0014454 | 0.053271 | -0.0065979 | 0.050003 | 0.056499 | -0.0045342 | -0.0038645 | 0.057941 | 0.039949 | 0.054798 | -63.8949 | -23.9538 | -66.0181 | 56.6868 | 56.5363 | 56.6419 | -66.4758 | -66.0652 | -19.9491 | -66.2004 | 56.5236 | 56.7197 | 56.6725 | -66.5936 | -0.13209 | -0.057599 | 2.4488 | 0.32563 | 0.45772 | -0.20804 | -0.10246 | -0.24994 | -0.22077 | 0.27853 | 0.14329 | 0.39324 | -0.024686 | -0.07185 | 123.0305 | 122.88 | 122.9856 | 42.3898 | -123.2202 | 122.8673 | 123.0634 | 123.0162 | 46.3946 | -123.338
351.9375 | 123.2712 | -66.3208 | 56.7444 | 0.078959 | -0.033015 | -0.00037739 | 0.051134 | -0.0055299 | 0.051071 | 0.07176 | -0.0066712 | -0.0049335 | 0.056873 | 0.039949 | 0.054798 | -63.8675 | -24.2698 | -66.0135 | 56.6959 | 56.5501 | 56.6557 | -66.4712 | -66.0652 | -20.2009 | -66.1958 | 56.5236 | 56.7243 | 56.6542 | -66.5845 | -0.1504 | -0.048443 | 2.4533 | 0.30732 | 0.45772 | -0.19431 | -0.088728 | -0.26367 | -0.22077 | 0.25564 | 0.12499 | 0.38866 | -0.020108 | -0.090164 | 123.0167 | 122.8709 | 122.9765 | 42.051 | -123.2156 | 122.8444 | 123.0451 | 122.975 | 46.1199 | -123.3289
352.9375 | 123.2483 | -66.3162 | 56.7581 | 0.048435 | -0.031946 | -0.0014454 | 0.053271 | -0.0076669 | 0.051071 | 0.041238 | -0.0056032 | -0.0038645 | 0.056873 | 0.039949 | 0.054798 | -63.8629 | -24.5399 | -65.9952 | 56.7051 | 56.5547 | 56.6648 | -66.4712 | -66.0514 | -20.5031 | -66.1775 | 56.519 | 56.7334 | 56.6496 | -66.5799 | -0.15498 | -0.053019 | 2.4533 | 0.32106 | 0.47603 | -0.20346 | -0.093304 | -0.26367 | -0.23908 | 0.2648 | 0.13872 | 0.40239 | -0.024684 | -0.10848 | 123.0213 | 122.8709 | 122.981 | 41.7763 | -123.2293 | 122.8353 | 123.0497 | 122.9659 | 45.8131 | -123.338
353.9375 | 123.3307 | -66.3025 | 56.7261 | 0.063697 | -0.033015 | -0.0035824 | 0.053271 | -0.0065979 | 0.050003 | 0.056499 | -0.0056032 | -0.0027965 | 0.057941 | 0.039949 | 0.056935 | -63.8858 | -24.7963 | -65.9769 | 56.7005 | 56.5638 | 56.6557 | -66.4575 | -66.0285 | -20.7275 | -66.1592 | 56.5328 | 56.738 | 56.6908 | -66.5845 | -0.15497 | -0.025553 | 2.4167 | 0.32564 | 0.48061 | -0.16226 | -0.070417 | -0.28198 | -0.1933 | 0.27396 | 0.14331 | 0.42529 | 0.011939 | -0.035224 | 123.003 | 122.8663 | 122.9581 | 41.5062 | -123.1835 | 122.8353 | 123.0405 | 122.9933 | 45.575 | -123.3105
354.9375 | 123.2254 | -66.2979 | 56.7581 | 0.017911 | -0.034083 | -0.0014454 | 0.051134 | -0.0087349 | 0.050003 | 0.056499 | -0.0066712 | -0.0017285 | 0.056873 | 0.03888 | 0.054798 | -63.8354 | -25.1076 | -65.9723 | 56.7143 | 56.5592 | 56.6648 | -66.4575 | -66.0285 | -20.961 | -66.1592 | 56.5374 | 56.738 | 56.6908 | -66.5753 | -0.15955 | -0.043862 | 2.4625 | 0.32564 | 0.48519 | -0.19888 | -0.093304 | -0.2774 | -0.22076 | 0.26939 | 0.13873 | 0.41613 | -0.020105 | -0.067268 | 123.0122 | 122.8571 | 122.9627 | 41.1903 | -123.2156 | 122.8353 | 123.0359 | 122.9888 | 45.3369 | -123.3334
355.9531 | 123.1705 | -66.3437 | 56.781 | 0.063697 | -0.02981 | -0.0014454 | 0.051134 | -0.0055299 | 0.051071 | 0.07176 | -0.0056032 | -0.0027965 | 0.057941 | 0.039949 | 0.05373 | -63.8308 | -25.4739 | -65.9585 | 56.7143 | 56.5684 | 56.6602 | -66.4391 | -66.0056 | -21.1762 | -66.1317 | 56.5511 | 56.738 | 56.6908 | -66.5707 | -0.095458 | -0.06675 | 2.5129 | 0.38515 | 0.48061 | -0.21261 | -0.12077 | -0.22705 | -0.22992 | 0.33805 | 0.21198 | 0.43902 | -0.042993 | -0.090156 | 123.0579 | 122.9121 | 123.0039 | 40.8698 | -123.2202 | 122.8948 | 123.0817 | 123.0345 | 45.1675 | -123.3517
356.9375 | 123.2758 | -66.3254 | 56.7535 | 0.048435 | -0.031946 | -0.0025134 | 0.052202 | -0.0055299 | 0.050003 | 0.041238 | -0.0077392 | -0.0038645 | 0.057941 | 0.03888 | 0.054798 | -63.8079 | -25.6617 | -65.9494 | 56.7234 | 56.5821 | 56.6786 | -66.4483 | -66.0011 | -21.515 | -66.1317 | 56.5557 | 56.7517 | 56.7092 | -66.5707 | -0.12293 | -0.030127 | 2.5174 | 0.37599 | 0.49892 | -0.17141 | -0.07499 | -0.24536 | -0.19787 | 0.32432 | 0.19366 | 0.43902 | -0.001791 | -0.044376 | 123.0488 | 122.9075 | 123.0039 | 40.6637 | -123.2018 | 122.881 | 123.0771 | 123.0345 | 44.8104 | -123.3243
357.9375 | 123.1659 | -66.3345 | 56.7856 | 0.078959 | -0.031946 | -0.0025134 | 0.052202 | -0.0076669 | 0.048935 | 0.07176 | -0.0045342 | -0.0038645 | 0.057941 | 0.03888 | 0.05373 | -63.8034 | -26.0005 | -65.9448 | 56.7326 | 56.5821 | 56.6877 | -66.4437 | -65.9827 | -21.7851 | -66.1226 | 56.5602 | 56.7609 | 56.6863 | -66.557 | -0.10919 | -0.053014 | 2.5312 | 0.38973 | 0.49892 | -0.20345 | -0.097876 | -0.22246 | -0.22534 | 0.35179 | 0.21198 | 0.43444 | -0.024677 | -0.099312 | 123.0671 | 122.9167 | 123.0222 | 40.3341 | -123.2293 | 122.8948 | 123.0954 | 123.0208 | 44.5494 | -123.3426
358.9688 | 123.1567 | -66.3345 | 56.7627 | 0.063697 | -0.033015 | -0.0025134 | 0.048997 | -0.0065979 | 0.050003 | 0.07176 | -0.0066712 | -0.0027965 | 0.057941 | 0.039949 | 0.05373 | -63.7988 | -26.2935 | -65.9219 | 56.7326 | 56.5821 | 56.6969 | -66.4346 | -65.969 | -22.0278 | -66.1134 | 56.5648 | 56.7655 | 56.7092 | -66.5524 | -0.10003 | -0.030126 | 2.5357 | 0.41262 | 0.51265 | -0.18057 | -0.065831 | -0.21788 | -0.19787 | 0.36553 | 0.22114 | 0.43902 | 0.00279 | -0.053531 | 123.0671 | 122.9167 | 123.0314 | 40.041 | -123.1973 | 122.8994 | 123.1 | 123.0437 | 44.3067 | -123.3151
359.9375 | 123.2346 | -66.3071 | 56.7902 | 0.048435 | -0.033015 | -0.0035824 | 0.051134 | -0.0076669 | 0.048935 | 0.056499 | -0.0066712 | -0.0027965 | 0.057941 | 0.042085 | 0.054798 | -63.7713 | -26.5911 | -65.9128 | 56.7371 | 56.5867 | 56.6923 | -66.4346 | -65.9598 | -22.1835 | -66.0997 | 56.5557 | 56.7746 | 56.6725 | -66.5616 | -0.1275 | -0.053013 | 2.5358 | 0.39431 | 0.52181 | -0.20345 | -0.097875 | -0.25451 | -0.23449 | 0.34722 | 0.20741 | 0.46192 | -0.015519 | -0.11763 | 123.0442 | 122.8938 | 122.9994 | 39.716 | -123.2247 | 122.8627 | 123.0817 | 122.9796 | 44.1236 | -123.3517
360.9375 | 123.23 | -66.2842 | 56.8085 | 0.078959 | -0.035152 | -0.0046504 | 0.051134 | -0.0076669 | 0.050003 | 0.056499 | -0.0066712 | -0.0038645 | 0.057941 | 0.039949 | 0.055867 | -63.753 | -26.8521 | -65.9036 | 56.7417 | 56.5959 | 56.706 | -66.43 | -65.9507 | -22.5269 | -66.0859 | 56.5648 | 56.7746 | 56.7137 | -66.5433 | -0.14581 | -0.066746 | 2.5312 | 0.38058 | 0.52639 | -0.21261 | -0.10245 | -0.25908 | -0.24365 | 0.33349 | 0.19825 | 0.45734 | -0.03383 | -0.094729 | 123.0259 | 122.88 | 122.9902 | 39.4321 | -123.2385 | 122.849 | 123.0588 | 122.9979 | 43.7573 | -123.3517
361.9375 | 123.23 | -66.2796 | 56.7764 | 0.048435 | -0.037288 | -0.0046504 | 0.053271 | -0.0087349 | 0.047866 | 0.087021 | -0.0066712 | -0.0038645 | 0.057941 | 0.041017 | 0.055867 | -63.7438 | -27.1268 | -65.8853 | 56.7509 | 56.6004 | 56.7014 | -66.4254 | -65.937 | -22.71 | -66.0722 | 56.5877 | 56.7838 | 56.7458 | -66.5433 | -0.14581 | -0.025545 | 2.5358 | 0.39431 | 0.54012 | -0.17598 | -0.074985 | -0.26366 | -0.18871 | 0.34265 | 0.20741 | 0.47107 | 0.007371 | -0.030635 | 123.0305 | 122.88 | 122.981 | 39.1528 | -123.2018 | 122.8673 | 123.0634 | 123.0254 | 43.5696 | -123.3197
362.9375 | 123.2346 | -66.3025 | 56.7993 | 0.033173 | -0.035152 | -0.0035824 | 0.050065 | -0.0087349 | 0.048935 | 0.056499 | -0.0045342 | -0.0038645 | 0.056873 | 0.041017 | 0.055867 | -63.7393 | -27.4244 | -65.8716 | 56.76 | 56.605 | 56.706 | -66.4163 | -65.9324 | -23.0168 | -66.063 | 56.5786 | 56.7884 | 56.7046 | -66.5387 | -0.11376 | -0.039276 | 2.5632 | 0.43094 | 0.5447 | -0.19429 | -0.093295 | -0.23619 | -0.22076 | 0.37012 | 0.23946 | 0.47565 | -0.010938 | -0.09473 | 123.0625 | 122.9075 | 123.0085 | 38.8781 | -123.2156 | 122.8811 | 123.0909 | 123.0071 | 43.2857 | -123.338
363.9844 | 123.3078 | -66.2704 | 56.7581 | 0.063697 | -0.035152 | -0.0025134 | 0.052202 | -0.0076669 | 0.048935 | 0.087021 | -0.0056032 | -0.0027965 | 0.056873 | 0.042085 | 0.05373 | -63.8034 | -27.7541 | -65.8578 | 56.7555 | 56.6188 | 56.7198 | -66.4071 | -65.9095 | -23.2778 | -66.0447 | 56.5923 | 56.793 | 56.7366 | -66.5341 | -0.13665 | -0.002657 | 2.4671 | 0.41263 | 0.54928 | -0.13936 | -0.038361 | -0.26366 | -0.16582 | 0.36097 | 0.22573 | 0.48939 | 0.034838 | -0.021482 | 123.0259 | 122.8892 | 122.9902 | 38.5164 | -123.1652 | 122.8627 | 123.0634 | 123.0071 | 42.9926 | -123.2922
364.9375 | 123.2208 | -66.2567 | 56.7993 | 0.078959 | -0.03622 | -0.0025134 | 0.051134 | -0.0076669 | 0.050003 | 0.056499 | -0.0056032 | -0.0049335 | 0.054736 | 0.041017 | 0.05373 | -63.6981 | -28.0334 | -65.8441 | 56.7646 | 56.6142 | 56.7243 | -66.4025 | -65.9003 | -23.5754 | -66.0401 | 56.6015 | 56.7975 | 56.7504 | -66.5249 | -0.1458 | -0.034698 | 2.5587 | 0.41263 | 0.55843 | -0.18513 | -0.07498 | -0.26823 | -0.19786 | 0.35639 | 0.21658 | 0.48481 | -0.001781 | -0.048944 | 123.0213 | 122.8709 | 122.9811 | 38.2233 | -123.2018 | 122.8582 | 123.0542 | 123.0071 | 42.6813 | -123.3243
365.9375 | 123.2437 | -66.2567 | 56.7764 | 0.063697 | -0.034083 | -0.0035824 | 0.053271 | -0.0076669 | 0.050003 | 0.056499 | -0.0066712 | -0.0027965 | 0.055804 | 0.042085 | 0.054798 | -63.6889 | -28.3447 | -65.8349 | 56.7692 | 56.6279 | 56.7289 | -66.3979 | -65.8866 | -23.7494 | -66.031 | 56.5923 | 56.8021 | 56.755 | -66.5249 | -0.14122 | -0.007231 | 2.5678 | 0.42179 | 0.56301 | -0.14851 | -0.047514 | -0.26823 | -0.18413 | 0.37013 | 0.22573 | 0.49397 | 0.025686 | -0.021478 | 123.0259 | 122.8846 | 122.9856 | 37.912 | -123.1744 | 122.849 | 123.0588 | 123.0117 | 42.5073 | -123.3014
366.9375 | 123.7473 | -66.2704 | 56.8222 | 0.048435 | -0.033015 | -0.0046504 | 0.051134 | -0.0076669 | 0.050003 | 0.07176 | -0.0056032 | -0.0049335 | 0.055804 | 0.039949 | 0.054798 | -62.8327 | -28.4592 | -65.725 | 56.7646 | 56.6188 | 56.7243 | -66.3842 | -65.9507 | -23.8364 | -65.9852 | 56.5969 | 56.7975 | 56.7504 | -66.5066 | -0.11375 | -0.057587 | 3.4377 | 0.5454 | 0.65915 | -0.20344 | -0.097869 | -0.23618 | -0.22533 | 0.31976 | 0.28525 | 0.52144 | -0.02467 | -0.071833 | 123.0351 | 122.8892 | 122.9948 | 37.8113 | -123.2064 | 122.8673 | 123.068 | 123.0208 | 42.434 | -123.3288
367.9375 | 123.4314 | -66.2292 | 56.813 | 0.063697 | -0.03622 | -0.0035824 | 0.051134 | -0.0087349 | 0.050003 | 0.07176 | -0.0066712 | -0.0038645 | 0.055804 | 0.041017 | 0.054798 | -63.4737 | -28.8575 | -65.8212 | 56.7738 | 56.6279 | 56.7289 | -66.3842 | -65.9507 | -24.1157 | -66.0127 | 56.5969 | 56.8113 | 56.7641 | -66.5021 | -0.15495 | -0.039274 | 2.7555 | 0.40806 | 0.56301 | -0.18513 | -0.084135 | -0.2728 | -0.21617 | 0.27856 | 0.21658 | 0.48939 | -0.001778 | -0.048942 | 123.003 | 122.8572 | 122.9582 | 37.3717 | -123.1972 | 122.8261 | 123.0405 | 122.9934 | 42.1135 | -123.3151
368.9688 | 123.5458 | -66.2521 | 56.8268 | 0.078959 | -0.035152 | -0.0025134 | 0.052202 | -0.0065979 | 0.048935 | 0.056499 | -0.0056032 | -0.0038645 | 0.056873 | 0.042085 | 0.054798 | -63.4325 | -29.1689 | -65.78 | 56.7784 | 56.6325 | 56.7381 | -66.3842 | -65.9507 | -24.4316 | -65.9989 | 56.606 | 56.8158 | 56.7504 | -66.5112 | -0.13206 | -0.048429 | 2.8196 | 0.47215 | 0.60421 | -0.19428 | -0.08871 | -0.25907 | -0.22075 | 0.30145 | 0.25321 | 0.51228 | -0.010933 | -0.07641 | 123.0305 | 122.8846 | 122.9902 | 37.0833 | -123.211 | 122.8582 | 123.068 | 123.0025 | 41.8205 | -123.338
369.9375 | 123.5184 | -66.2567 | 56.8222 | 0.078959 | -0.035152 | -0.0035824 | 0.052202 | -0.0087349 | 0.050003 | 0.056499 | -0.0056032 | -0.0038645 | 0.055804 | 0.042085 | 0.054798 | -63.4005 | -29.3886 | -65.7708 | 56.7875 | 56.6417 | 56.7564 | -66.3842 | -65.9324 | -24.656 | -65.9806 | 56.5969 | 56.825 | 56.7687 | -66.4975 | -0.12749 | -0.034695 | 2.8562 | 0.48588 | 0.61337 | -0.18055 | -0.065819 | -0.24076 | -0.22533 | 0.32434 | 0.2761 | 0.51686 | 0.002802 | -0.053519 | 123.0442 | 122.8984 | 123.0131 | 36.8681 | -123.2064 | 122.8536 | 123.0817 | 123.0254 | 41.6007 | -123.3197
370.9688 | 123.5367 | -66.2201 | 56.8634 | 0.063697 | -0.033015 | -0.0025134 | 0.052202 | -0.0065979 | 0.051071 | 0.056499 | -0.0066712 | -0.0038645 | 0.056873 | 0.043154 | 0.05373 | -63.4508 | -29.6908 | -65.7525 | 56.7875 | 56.6462 | 56.7518 | -66.3705 | -65.9141 | -24.9857 | -65.976 | 56.5923 | 56.825 | 56.7687 | -66.5021 | -0.15037 | -0.075893 | 2.7693 | 0.46758 | 0.61795 | -0.21717 | -0.1116 | -0.28196 | -0.27111 | 0.30603 | 0.24406 | 0.52602 | -0.038396 | -0.094717 | 123.0076 | 122.8663 | 122.9719 | 36.5293 | -123.2339 | 122.8124 | 123.0451 | 122.9888 | 41.2344 | -123.3655
371.9375 | 123.1705 | -66.275 | 56.8405 | 0.063697 | -0.034083 | -0.0014454 | 0.053271 | -0.0076669 | 0.050003 | 0.056499 | -0.0056032 | -0.0049335 | 0.056873 | 0.043154 | 0.052662 | -63.6019 | -29.9472 | -65.7434 | 56.7967 | 56.6554 | 56.7564 | -66.3705 | -65.8042 | -25.3474 | -65.944 | 56.6015 | 56.8296 | 56.7778 | -66.4883 | -0.09544 | -0.043848 | 2.6731 | 0.53166 | 0.6271 | -0.18512 | -0.084129 | -0.21329 | -0.23906 | 0.47085 | 0.33104 | 0.54433 | -0.01093 | -0.062672 | 123.0717 | 122.9304 | 123.0314 | 36.3278 | -123.211 | 122.8765 | 123.1046 | 123.0529 | 40.9276 | -123.3288
372.9531 | 123.1842 | -66.2613 | 56.8634 | 0.048435 | -0.035152 | -0.0025134 | 0.052202 | -0.0065979 | 0.051071 | 0.07176 | -0.0066712 | -0.0049335 | 0.057941 | 0.043154 | 0.055867 | -63.5928 | -30.1807 | -65.7296 | 56.7967 | 56.6554 | 56.7655 | -66.3567 | -65.795 | -25.6129 | -65.9486 | 56.6198 | 56.8387 | 56.7321 | -66.4883 | -0.095435 | -0.066736 | 2.6685 | 0.53167 | 0.6271 | -0.20801 | -0.09786 | -0.22702 | -0.24364 | 0.46628 | 0.31273 | 0.53975 | -0.024661 | -0.13135 | 123.058 | 122.9167 | 123.0268 | 36.0806 | -123.2201 | 122.8811 | 123.1 | 122.9933 | 40.6483 | -123.3517
373.9531 | 123.3261 | -66.1926 | 56.8405 | 0.078959 | -0.034083 | -0.0025134 | 0.052202 | -0.0087349 | 0.051071 | 0.07176 | -0.0077392 | -0.0027965 | 0.056873 | 0.042085 | 0.054798 | -63.6294 | -30.5287 | -65.7159 | 56.8058 | 56.6645 | 56.7655 | -66.3567 | -65.7813 | -25.9289 | -65.9257 | 56.6472 | 56.8525 | 56.7916 | -66.4746 | -0.1641 | -0.034691 | 2.5632 | 0.47674 | 0.64084 | -0.17597 | -0.074972 | -0.28195 | -0.19328 | 0.41135 | 0.26696 | 0.54891 | 0.011963 | -0.048936 | 122.9985 | 122.8572 | 122.9582 | 35.6639 | -123.1972 | 122.8399 | 123.0451 | 122.9842 | 40.2638 | -123.3151
374.9531 | 123.2986 | -66.1697 | 56.8497 | 0.048435 | -0.034083 | -0.0025134 | 0.051134 | -0.0087349 | 0.050003 | 0.07176 | -0.0056032 | -0.0027965 | 0.057941 | 0.043154 | 0.054798 | -63.6294 | -30.7943 | -65.693 | 56.8104 | 56.6645 | 56.7701 | -66.3476 | -65.7721 | -26.1487 | -65.9119 | 56.6335 | 56.8525 | 56.7733 | -66.4792 | -0.17783 | -0.039268 | 2.5404 | 0.47674 | 0.65457 | -0.18512 | -0.079548 | -0.30942 | -0.21617 | 0.39762 | 0.2578 | 0.56722 | 0.002808 | -0.076405 | 122.9801 | 122.8343 | 122.9399 | 35.3755 | -123.1972 | 122.8032 | 123.0222 | 122.943 | 40.0211 | -123.3288
375.9375 | 123.2483 | -66.1972 | 56.8954 | 0.033173 | -0.037288 | -0.0014454 | 0.051134 | -0.0087349 | 0.050003 | 0.056499 | -0.0077392 | -0.0038645 | 0.054736 | 0.043154 | 0.054798 | -63.5287 | -31.0278 | -65.6838 | 56.815 | 56.6645 | 56.7793 | -66.3476 | -65.7538 | -26.4005 | -65.9028 | 56.6381 | 56.8571 | 56.7641 | -66.47 | -0.15036 | -0.080467 | 2.6685 | 0.51336 | 0.66372 | -0.2309 | -0.11617 | -0.2728 | -0.25737 | 0.4434 | 0.29443 | 0.56722 | -0.03839 | -0.13134 | 123.0122 | 122.8618 | 122.9765 | 35.1694 | -123.243 | 122.8353 | 123.0543 | 122.9613 | 39.7967 | -123.3654
376.9375 | 123.1934 | -66.1972 | 56.8954 | 0.033173 | -0.037288 | -0.0014454 | 0.053271 | -0.0087349 | 0.050003 | 0.087021 | -0.0077392 | -0.0049335 | 0.055804 | 0.044222 | 0.05373 | -63.5149 | -31.2201 | -65.6747 | 56.8287 | 56.6737 | 56.7747 | -66.343 | -65.7309 | -26.6569 | -65.8845 | 56.6656 | 56.8616 | 56.8099 | -66.47 | -0.14579 | -0.066731 | 2.6823 | 0.52252 | 0.6683 | -0.22174 | -0.12075 | -0.2728 | -0.22989 | 0.46629 | 0.31274 | 0.58554 | -0.033812 | -0.085554 | 123.0259 | 122.8709 | 122.9719 | 34.9771 | -123.2384 | 122.8628 | 123.0588 | 123.0071 | 39.5403 | -123.3654
377.9531 | 123.1705 | -66.2064 | 56.8726 | 0.048435 | -0.035152 | -0.0014454 | 0.054339 | -0.0087349 | 0.048935 | 0.07176 | -0.0045342 | -0.0027965 | 0.056873 | 0.043154 | 0.05373 | -63.5149 | -31.4261 | -65.6518 | 56.8241 | 56.6783 | 56.7839 | -66.3338 | -65.7263 | -26.9408 | -65.8753 | 56.6427 | 56.8616 | 56.8053 | -66.47 | -0.12747 | -0.048422 | 2.6914 | 0.55456 | 0.68204 | -0.19427 | -0.088701 | -0.26364 | -0.2299 | 0.48003 | 0.33106 | 0.5947 | -0.010924 | -0.067244 | 123.0305 | 122.8846 | 122.9902 | 34.7802 | -123.2064 | 122.849 | 123.068 | 123.0117 | 39.2656 | -123.3426
378.9531 | 123.2941 | -66.1377 | 56.8405 | 0.048435 | -0.035152 | -0.0035824 | 0.051134 | -0.0065979 | 0.048935 | 0.056499 | -0.0056032 | -0.0049335 | 0.054736 | 0.042085 | 0.05373 | -63.5424 | -31.6917 | -65.6335 | 56.8379 | 56.6829 | 56.7839 | -66.3293 | -65.7034 | -27.1605 | -65.8616 | 56.6427 | 56.8662 | 56.8145 | -66.4608 | -0.19156 | -0.002643 | 2.5953 | 0.50421 | 0.69577 | -0.15765 | -0.056657 | -0.32315 | -0.19786 | 0.43426 | 0.27613 | 0.59927 | 0.025699 | -0.026043 | 122.9756 | 122.8206 | 122.9216 | 34.446 | -123.1698 | 122.7804 | 123.0039 | 122.9522 | 38.9771 | -123.3014
379.9375 | 123.2391 | -66.2064 | 56.8817 | 0.063697 | -0.035152 | -0.0035824 | 0.052202 | -0.0087349 | 0.050003 | 0.041238 | -0.0066712 | -0.0027965 | 0.055804 | 0.045291 | 0.05373 | -63.4554 | -31.829 | -65.6243 | 56.8425 | 56.6874 | 56.7976 | -66.3293 | -65.6989 | -27.3849 | -65.8387 | 56.6701 | 56.8754 | 56.787 | -66.4563 | -0.12289 | -0.039263 | 2.751 | 0.58203 | 0.70493 | -0.19427 | -0.08412 | -0.2499 | -0.21158 | 0.5075 | 0.36768 | 0.61759 | -0.006343 | -0.094714 | 123.0488 | 122.8938 | 123.004 | 34.3773 | -123.211 | 122.8765 | 123.0817 | 122.9934 | 38.8215 | -123.338
380.9375 | 123.1522 | -66.1652 | 56.8863 | 0.048435 | -0.034083 | -0.0035824 | 0.051134 | -0.0076669 | 0.048935 | 0.087021 | -0.0066712 | -0.0049335 | 0.057941 | 0.042085 | 0.054798 | -63.4508 | -32.2365 | -65.606 | 56.847 | 56.7012 | 56.8068 | -66.3247 | -65.6805 | -27.5635 | -65.8204 | 56.661 | 56.8754 | 56.8191 | -66.4379 | -0.15951 | -0.039263 | 2.7143 | 0.55915 | 0.71866 | -0.18511 | -0.079541 | -0.27279 | -0.22532 | 0.48462 | 0.3448 | 0.61759 | -0.010921 | -0.067241 | 123.0122 | 122.8663 | 122.9719 | 33.9286 | -123.211 | 122.8261 | 123.0405 | 122.9842 | 38.6017 | -123.3242
381.9375 | 123.1979 | -66.1697 | 56.9275 | 0.063697 | -0.037288 | -0.0025134 | 0.052202 | -0.0087349 | 0.050003 | 0.087021 | -0.0056032 | -0.0060015 | 0.056873 | 0.043154 | 0.051594 | -63.4417 | -32.4609 | -65.5831 | 56.8516 | 56.7103 | 56.8159 | -66.3155 | -65.6577 | -27.8657 | -65.8112 | 56.6884 | 56.8845 | 56.8419 | -66.4379 | -0.14578 | -0.075883 | 2.7281 | 0.58662 | 0.73239 | -0.21715 | -0.11158 | -0.26821 | -0.23905 | 0.51209 | 0.35854 | 0.62675 | -0.042962 | -0.085546 | 123.0213 | 122.8801 | 122.9856 | 33.7089 | -123.243 | 122.8582 | 123.0543 | 123.0117 | 38.3041 | -123.3654
382.9375 | 123.3948 | -66.1743 | 56.8954 | 0.078959 | -0.035152 | -0.0014454 | 0.050065 | -0.0065979 | 0.050003 | 0.056499 | -0.0045342 | -0.0027965 | 0.057941 | 0.044222 | 0.054798 | -63.3913 | -32.6486 | -65.5877 | 56.8516 | 56.7058 | 56.8068 | -66.3109 | -65.7355 | -28.0534 | -65.7975 | 56.6884 | 56.8891 | 56.8465 | -66.4334 | -0.13662 | -0.04384 | 2.783 | 0.58662 | 0.72324 | -0.18969 | -0.088696 | -0.25905 | -0.207 | 0.43883 | 0.37685 | 0.6359 | -0.00634 | -0.048925 | 123.0259 | 122.8801 | 122.9811 | 33.5257 | -123.2064 | 122.8628 | 123.0634 | 123.0208 | 38.1209 | -123.3288
383.9375 | 123.4543 | -66.2109 | 56.8909 | 0.063697 | -0.035152 | -0.0035824 | 0.051134 | -0.0087349 | 0.048935 | 0.041238 | -0.0056032 | -0.0038645 | 0.056873 | 0.044222 | 0.05373 | -63.2906 | -32.786 | -65.574 | 56.8562 | 56.7149 | 56.8205 | -66.3109 | -65.7126 | -28.232 | -65.7929 | 56.6793 | 56.8891 | 56.8374 | -66.4242 | -0.1 | -0.034683 | 2.9204 | 0.63697 | 0.73697 | -0.17595 | -0.070382 | -0.21327 | -0.21158 | 0.49834 | 0.41805 | 0.63132 | -0.001762 | -0.053504 | 123.0671 | 122.9259 | 123.0314 | 33.425 | -123.2018 | 122.8902 | 123.1 | 123.0483 | 37.979 | -123.3151
384.9375 | 123.5733 | -66.1606 | 56.9092 | 0.063697 | -0.037288 | -0.0025134 | 0.052202 | -0.0076669 | 0.050003 | 0.087021 | -0.0077392 | -0.0038645 | 0.057941 | 0.043154 | 0.054798 | -63.2769 | -32.8913 | -65.5557 | 56.8562 | 56.7241 | 56.8205 | -66.3064 | -65.7172 | -28.525 | -65.7792 | 56.693 | 56.8891 | 56.8465 | -66.4379 | -0.14578 | -0.052994 | 2.8837 | 0.60493 | 0.75071 | -0.1851 | -0.088693 | -0.27737 | -0.21616 | 0.44341 | 0.38143 | 0.6588 | -0.020073 | -0.062658 | 123.0168 | 122.8847 | 122.9811 | 33.2693 | -123.2155 | 122.8536 | 123.0497 | 123.0071 | 37.6356 | -123.3471
385.9375 | 123.5138 | -66.1514 | 56.9 | 0.063697 | -0.031946 | -0.00037739 | 0.051134 | -0.0076669 | 0.051071 | 0.041238 | -0.0056032 | -0.0038645 | 0.055804 | 0.044222 | 0.05373 | -63.2631 | -33.1706 | -65.5465 | 56.8653 | 56.7149 | 56.8251 | -66.3018 | -65.6851 | -28.7082 | -65.7608 | 56.6976 | 56.8937 | 56.8465 | -66.4196 | -0.15035 | -0.034681 | 2.8883 | 0.60493 | 0.75529 | -0.18511 | -0.074959 | -0.26821 | -0.20242 | 0.4663 | 0.39059 | 0.6588 | -0.006338 | -0.053502 | 123.0168 | 122.8663 | 122.9765 | 32.9809 | -123.2018 | 122.849 | 123.0451 | 122.998 | 37.4433 | -123.3197
386.9375 | 123.4726 | -66.1697 | 56.9275 | 0.078959 | -0.034083 | -0.0014454 | 0.052202 | -0.0076669 | 0.051071 | 0.056499 | -0.0066712 | -0.0038645 | 0.055804 | 0.043154 | 0.054798 | -63.2494 | -33.4361 | -65.5236 | 56.8653 | 56.7195 | 56.8296 | -66.2926 | -65.6668 | -28.7494 | -65.7517 | 56.7068 | 56.8983 | 56.8465 | -66.4242 | -0.12288 | -0.062147 | 2.9204 | 0.64614 | 0.76902 | -0.20799 | -0.097846 | -0.25447 | -0.22073 | 0.50293 | 0.41806 | 0.67253 | -0.029226 | -0.080968 | 123.0351 | 122.8892 | 122.9994 | 32.7336 | -123.2201 | 122.8765 | 123.068 | 123.0163 | 37.4204 | -123.3517
387.9375 | 123.4314 | -66.1789 | 56.9183 | 0.048435 | -0.038357 | -0.0025134 | 0.053271 | -0.0065979 | 0.051071 | 0.056499 | -0.0056032 | -0.0038645 | 0.055804 | 0.045291 | 0.05373 | -63.2173 | -33.5964 | -65.4961 | 56.8699 | 56.7241 | 56.8388 | -66.2835 | -65.6485 | -29.0516 | -65.7379 | 56.7159 | 56.912 | 56.8557 | -66.4196 | -0.10457 | -0.048414 | 2.9616 | 0.68276 | 0.78733 | -0.19426 | -0.079534 | -0.24074 | -0.20242 | 0.5304 | 0.44095 | 0.68169 | -0.006335 | -0.062655 | 123.0488 | 122.903 | 123.0177 | 32.5825 | -123.2018 | 122.8948 | 123.0909 | 123.0346 | 37.1273 | -123.338
388.9375 | 123.8525 | -66.1469 | 56.9046 | 0.078959 | -0.03622 | -0.0025134 | 0.052202 | -0.0076669 | 0.050003 | 0.056499 | -0.0056032 | -0.0038645 | 0.054736 | 0.044222 | 0.054798 | -63.1624 | -33.72 | -65.4778 | 56.8745 | 56.7287 | 56.8388 | -66.2926 | -65.6531 | -29.2713 | -65.7151 | 56.6976 | 56.9166 | 56.8557 | -66.4059 | -0.14577 | -0.030103 | 2.9845 | 0.66903 | 0.8148 | -0.17595 | -0.065801 | -0.25905 | -0.207 | 0.49378 | 0.4318 | 0.69085 | 0.011977 | -0.048922 | 123.0213 | 122.8755 | 122.9857 | 32.4268 | -123.1972 | 122.8445 | 123.0634 | 123.0025 | 36.8755 | -123.3105
389.9375 | 123.1659 | -66.1789 | 56.9504 | 0.063697 | -0.03622 | -0.0025134 | 0.051134 | -0.0087349 | 0.047866 | 0.07176 | -0.0077392 | -0.0049335 | 0.054736 | 0.045291 | 0.05373 | -63.2769 | -33.7978 | -65.4458 | 56.8745 | 56.7287 | 56.8388 | -66.2835 | -65.5707 | -29.5003 | -65.6738 | 56.7068 | 56.912 | 56.8557 | -66.4105 | -0.10457 | -0.075879 | 2.902 | 0.73312 | 0.83769 | -0.22172 | -0.11158 | -0.23158 | -0.24362 | 0.60824 | 0.50505 | 0.73663 | -0.038378 | -0.094698 | 123.0534 | 122.9075 | 123.0177 | 32.3811 | -123.2338 | 122.8857 | 123.0909 | 123.0346 | 36.6786 | -123.3609
390.9375 | 123.2803 | -66.1285 | 56.955 | 0.048435 | -0.037288 | -0.0035824 | 0.051134 | -0.0087349 | 0.047866 | 0.056499 | -0.0066712 | -0.0027965 | 0.056873 | 0.042085 | 0.05373 | -63.2631 | -34.0359 | -65.432 | 56.8837 | 56.7378 | 56.8342 | -66.2789 | -65.5157 | -29.72 | -65.683 | 56.7068 | 56.912 | 56.8419 | -66.4059 | -0.15035 | -0.0713 | 2.8654 | 0.6965 | 0.84685 | -0.21714 | -0.12073 | -0.27736 | -0.2482 | 0.61283 | 0.44554 | 0.7229 | -0.042956 | -0.11301 | 123.0122 | 122.8664 | 122.9628 | 32.0926 | -123.2338 | 122.8353 | 123.0405 | 122.9705 | 36.4085 | -123.3609
391.9531 | 123.2803 | -66.1057 | 56.9504 | 0.063697 | -0.03622 | -0.0035824 | 0.051134 | -0.0076669 | 0.048935 | 0.07176 | -0.0066712 | -0.0049335 | 0.056873 | 0.044222 | 0.054798 | -63.2311 | -34.4663 | -65.4091 | 56.8928 | 56.7424 | 56.8525 | -66.2743 | -65.502 | -29.9765 | -65.6601 | 56.7205 | 56.9257 | 56.8694 | -66.3922 | -0.16865 | -0.057565 | 2.8746 | 0.69651 | 0.86516 | -0.20799 | -0.097841 | -0.28651 | -0.22989 | 0.60368 | 0.44555 | 0.73206 | -0.024642 | -0.080963 | 122.9985 | 122.848 | 122.9582 | 31.6393 | -123.2247 | 122.8261 | 123.0314 | 122.9751 | 36.1292 | -123.3425
392.9375 | 123.1934 | -66.1377 | 56.9504 | 0.063697 | -0.037288 | -0.0035824 | 0.052202 | -0.0076669 | 0.051071 | 0.07176 | -0.0056032 | -0.0038645 | 0.053668 | 0.043154 | 0.054798 | -63.1944 | -34.6495 | -65.3817 | 56.8974 | 56.747 | 56.8617 | -66.2743 | -65.4791 | -30.2558 | -65.6464 | 56.7159 | 56.9395 | 56.8969 | -66.3922 | -0.13661 | -0.052987 | 2.9433 | 0.75602 | 0.89263 | -0.20341 | -0.088684 | -0.25447 | -0.23446 | 0.65861 | 0.49132 | 0.74579 | -0.010906 | -0.053491 | 123.0351 | 122.8847 | 122.9994 | 31.4882 | -123.2247 | 122.8536 | 123.0772 | 123.0346 | 35.8819 | -123.3425
393.9688 | 123.349 | -66.1102 | 56.9366 | 0.048435 | -0.03622 | -0.0035824 | 0.050065 | -0.0076669 | 0.048935 | 0.07176 | -0.0077392 | -0.0038645 | 0.055804 | 0.044222 | 0.05373 | -63.254 | -34.7639 | -65.3588 | 56.902 | 56.7516 | 56.8663 | -66.256 | -65.4562 | -30.4343 | -65.6281 | 56.7205 | 56.9486 | 56.8969 | -66.383 | -0.14576 | -0.034676 | 2.8563 | 0.75144 | 0.8972 | -0.1851 | -0.070373 | -0.27277 | -0.21615 | 0.65404 | 0.48217 | 0.75495 | 0.011983 | -0.039759 | 123.0122 | 122.8618 | 122.9765 | 31.3463 | -123.1926 | 122.8307 | 123.0589 | 123.0071 | 35.6759 | -123.3196
394.9375 | 123.349 | -66.0919 | 56.9321 | 0.048435 | -0.03622 | -0.0035824 | 0.051134 | -0.0076669 | 0.050003 | 0.056499 | -0.0066712 | -0.0049335 | 0.057941 | 0.044222 | 0.05373 | -63.2082 | -34.8463 | -65.3359 | 56.9065 | 56.7561 | 56.8663 | -66.2651 | -65.4516 | -30.5442 | -65.6097 | 56.7434 | 56.944 | 56.8923 | -66.3922 | -0.17323 | -0.02552 | 2.8837 | 0.75603 | 0.92925 | -0.17594 | -0.065795 | -0.30024 | -0.18868 | 0.64031 | 0.48218 | 0.78242 | 0.011982 | -0.03976 | 122.9985 | 122.848 | 122.9582 | 31.2456 | -123.1972 | 122.8353 | 123.036 | 122.9842 | 35.5477 | -123.3242
395.9375 | 123.317 | -66.0919 | 56.9412 | 0.078959 | -0.038357 | -0.0035824 | 0.051134 | -0.0087349 | 0.051071 | 0.056499 | -0.0077392 | -0.0049335 | 0.055804 | 0.045291 | 0.05373 | -63.167 | -34.9104 | -65.3176 | 56.902 | 56.7561 | 56.8617 | -66.256 | -65.415 | -30.6266 | -65.6052 | 56.7388 | 56.9486 | 56.8969 | -66.383 | -0.16407 | -0.039253 | 2.9249 | 0.77434 | 0.93841 | -0.18509 | -0.079529 | -0.29108 | -0.20242 | 0.67694 | 0.48676 | 0.77784 | 0.007406 | -0.044336 | 122.9939 | 122.848 | 122.9536 | 31.1815 | -123.1972 | 122.8307 | 123.0405 | 122.9888 | 35.4653 | -123.3242
396.9531 | 123.2849 | -66.1331 | 56.9229 | 0.048435 | -0.037288 | -0.0025134 | 0.050065 | -0.0098029 | 0.048935 | 0.041238 | -0.0077392 | -0.0038645 | 0.057941 | 0.046359 | 0.05373 | -63.1899 | -34.9974 | -65.2947 | 56.9065 | 56.7561 | 56.8754 | -66.2514 | -65.3967 | -30.6678 | -65.596 | 56.7525 | 56.9486 | 56.8923 | -66.3784 | -0.11829 | -0.016365 | 2.9433 | 0.83843 | 0.95672 | -0.16678 | -0.047483 | -0.24531 | -0.17037 | 0.73645 | 0.53711 | 0.78242 | 0.025716 | -0.030605 | 123.0397 | 122.8892 | 123.0085 | 31.1357 | -123.1743 | 122.8857 | 123.0817 | 123.0254 | 35.4653 | -123.3013
397.9375 | 123.2803 | -66.0507 | 56.955 | 0.063697 | -0.035152 | -0.0014454 | 0.048997 | -0.0065979 | 0.050003 | 0.056499 | -0.0056032 | -0.0038645 | 0.057941 | 0.044222 | 0.05373 | -63.1349 | -35.0295 | -65.281 | 56.9111 | 56.7699 | 56.8709 | -66.2606 | -65.3875 | -30.7136 | -65.5777 | 56.7342 | 56.9486 | 56.8969 | -66.383 | -0.20985 | -0.043829 | 2.9158 | 0.76976 | 0.97961 | -0.18509 | -0.084105 | -0.33228 | -0.22073 | 0.66321 | 0.47303 | 0.80531 | -0.006327 | -0.058069 | 122.9618 | 122.8206 | 122.9216 | 31.0212 | -123.2155 | 122.7849 | 122.9993 | 122.9476 | 35.3371 | -123.338
398.9375 | 123.2208 | -66.1377 | 56.9824 | 0.063697 | -0.038357 | -0.0035824 | 0.050065 | -0.0076669 | 0.048935 | 0.056499 | -0.0077392 | -0.0049335 | 0.055804 | 0.047427 | 0.052662 | -63.0617 | -35.0615 | -65.2626 | 56.9203 | 56.7744 | 56.8754 | -66.256 | -65.36 | -30.7274 | -65.5548 | 56.748 | 56.9578 | 56.8969 | -66.3876 | -0.1183 | -0.062139 | 3.076 | 0.87505 | 0.99335 | -0.20798 | -0.10699 | -0.24989 | -0.23446 | 0.77766 | 0.5829 | 0.83279 | -0.024636 | -0.085535 | 123.058 | 122.9121 | 123.0131 | 31.0762 | -123.2384 | 122.8857 | 123.0955 | 123.0346 | 35.4103 | -123.37
399.9375 | 123.3124 | -66.0782 | 56.9412 | 0.048435 | -0.038357 | -0.0035824 | 0.053271 | -0.0076669 | 0.050003 | 0.041238 | -0.0077392 | -0.0027965 | 0.055804 | 0.047427 | 0.05373 | -63.0937 | -35.0066 | -65.2443 | 56.9157 | 56.779 | 56.8754 | -66.2468 | -65.3371 | -30.7548 | -65.5502 | 56.748 | 56.9578 | 56.9106 | -66.3784 | -0.16865 | -0.025518 | 2.9845 | 0.83386 | 1.0025 | -0.1622 | -0.065793 | -0.30024 | -0.19326 | 0.74104 | 0.52797 | 0.82821 | 0.016563 | -0.0306 | 122.9939 | 122.8572 | 122.9536 | 31.0716 | -123.1881 | 122.8262 | 123.036 | 122.9888 | 35.3234 | -123.3196
400.9375 | 123.2758 | -66.1011 | 56.9687 | 0.063697 | -0.037288 | -0.0025134 | 0.052202 | -0.0044619 | 0.051071 | 0.07176 | -0.0045342 | -0.0038645 | 0.057941 | 0.045291 | 0.05373 | -63.0662 | -34.9608 | -65.2214 | 56.9157 | 56.7744 | 56.8754 | -66.2423 | -65.3188 | -30.8189 | -65.5411 | 56.748 | 56.9578 | 56.8969 | -66.3784 | -0.14118 | -0.052984 | 3.0348 | 0.87964 | 1.0208 | -0.19424 | -0.093259 | -0.27735 | -0.22072 | 0.78225 | 0.56001 | 0.83736 | -0.010903 | -0.071802 | 123.0168 | 122.8755 | 122.9765 | 31.1403 | -123.2109 | 122.849 | 123.0589 | 122.998 | 35.2821 | -123.3471
401.9375 | 123.2758 | -66.0965 | 56.9412 | 0.063697 | -0.037288 | -0.0035824 | 0.051134 | -0.0055299 | 0.051071 | 0.056499 | -0.0056032 | -0.0027965 | 0.055804 | 0.046359 | 0.05373 | -63.1029 | -34.9242 | -65.1894 | 56.9249 | 56.779 | 56.8846 | -66.2423 | -65.3051 | -30.9563 | -65.5182 | 56.7525 | 56.9624 | 56.9152 | -66.3784 | -0.14576 | -0.016361 | 2.9936 | 0.90711 | 1.0529 | -0.1622 | -0.056636 | -0.28193 | -0.18868 | 0.79141 | 0.57833 | 0.86026 | 0.021142 | -0.026022 | 123.0214 | 122.8755 | 122.9811 | 31.1723 | -123.1835 | 122.849 | 123.0589 | 123.0117 | 35.1402 | -123.3196
402.9375 | 123.23 | -66.0965 | 56.9962 | 0.048435 | -0.038357 | -0.00037739 | 0.053271 | -0.0098029 | 0.048935 | 0.087021 | -0.0066712 | -0.0038645 | 0.056873 | 0.046359 | 0.054798 | -62.9701 | -34.8418 | -65.1665 | 56.934 | 56.7882 | 56.8892 | -66.2423 | -65.273 | -31.6156 | -65.4907 | 56.7709 | 56.9715 | 56.9152 | -66.3647 | -0.14576 | -0.062137 | 3.1264 | 0.93 | 1.0758 | -0.20797 | -0.10699 | -0.26819 | -0.2253 | 0.82346 | 0.6058 | 0.87399 | -0.024633 | -0.080954 | 123.0305 | 122.8847 | 122.9857 | 31.2547 | -123.2384 | 122.8674 | 123.068 | 123.0117 | 34.4809 | -123.3608
403.9375 | 123.262 | -66.1102 | 57.0053 | 0.063697 | -0.03622 | -0.0025134 | 0.051134 | -0.0076669 | 0.050003 | 0.056499 | -0.0066712 | -0.0038645 | 0.056873 | 0.046359 | 0.05373 | -62.9335 | -34.7914 | -65.1345 | 56.9386 | 56.7973 | 56.8983 | -66.2331 | -65.2456 | -32.1239 | -65.4586 | 56.7754 | 56.9715 | 56.9289 | -66.3601 | -0.12287 | -0.066713 | 3.1768 | 0.97578 | 1.0986 | -0.20797 | -0.10699 | -0.24988 | -0.22987 | 0.86466 | 0.65159 | 0.90147 | -0.033788 | -0.076373 | 123.0488 | 122.9076 | 123.0086 | 31.3188 | -123.2384 | 122.8857 | 123.0818 | 123.0392 | 33.9864 | -123.3654
404.9531 | 123.2941 | -66.0919 | 56.9092 | 0.048435 | -0.038357 | -0.0025134 | 0.050065 | -0.0087349 | 0.048935 | 0.056499 | -0.0056032 | -0.0038645 | 0.056873 | 0.046359 | 0.052662 | -63.0159 | -34.709 | -65.1207 | 56.9432 | 56.7928 | 56.8983 | -66.2194 | -65.2227 | -32.362 | -65.4403 | 56.78 | 56.9898 | 56.9244 | -66.3555 | -0.12744 | 0.033995 | 3.076 | 0.9712 | 1.0986 | -0.11642 | -0.010857 | -0.26361 | -0.12917 | 0.86925 | 0.65159 | 0.9152 | 0.080656 | 0.015179 | 123.0351 | 122.8847 | 122.9902 | 31.3829 | -123.1285 | 122.8719 | 123.0818 | 123.0163 | 33.73 | -123.2647
405.9375 | 123.2666 | -66.0782 | 56.9824 | 0.063697 | -0.038357 | -0.0046504 | 0.051134 | -0.0098029 | 0.050003 | 0.056499 | -0.0056032 | -0.0038645 | 0.056873 | 0.047427 | 0.052662 | -62.9884 | -34.5808 | -65.0978 | 56.9523 | 56.8065 | 56.9121 | -66.2194 | -65.2044 | -32.5405 | -65.4174 | 56.7892 | 56.9807 | 56.9289 | -66.3464 | -0.14117 | -0.03009 | 3.0898 | 0.98036 | 1.1215 | -0.17592 | -0.070363 | -0.26819 | -0.19325 | 0.87383 | 0.66075 | 0.92894 | -0.001743 | -0.053485 | 123.0305 | 122.8847 | 122.9902 | 31.4974 | -123.2018 | 122.8674 | 123.0589 | 123.0071 | 33.5377 | -123.3288
406.9531 | 123.2941 | -66.0507 | 56.9687 | 0.078959 | -0.039425 | -0.0035824 | 0.051134 | -0.0098029 | 0.050003 | 0.056499 | -0.0066712 | -0.0038645 | 0.055804 | 0.047427 | 0.054798 | -62.9152 | -34.4709 | -65.0612 | 56.9523 | 56.8065 | 56.9121 | -66.2102 | -65.1128 | -32.5588 | -65.39 | 56.7846 | 56.9853 | 56.9427 | -66.3464 | -0.15948 | -0.016357 | 3.1356 | 0.98952 | 1.149 | -0.16219 | -0.05663 | -0.29565 | -0.1841 | 0.93793 | 0.66076 | 0.95641 | 0.016569 | -0.026016 | 123.0031 | 122.8572 | 122.9628 | 31.5798 | -123.1789 | 122.8353 | 123.036 | 122.9934 | 33.4919 | -123.3151
407.9375 | 123.3078 | -66.0919 | 56.9641 | 0.063697 | -0.040493 | -0.0025134 | 0.051134 | -0.0076669 | 0.048935 | 0.07176 | -0.0077392 | -0.0038645 | 0.056873 | 0.048496 | 0.052662 | -62.938 | -34.3335 | -65.0383 | 56.9615 | 56.8202 | 56.9166 | -66.201 | -65.1403 | -32.7466 | -65.3625 | 56.7892 | 56.9898 | 56.9015 | -66.3418 | -0.10912 | -0.002622 | 3.1539 | 1.0536 | 1.1627 | -0.14388 | -0.047474 | -0.24987 | -0.17494 | 0.95166 | 0.72943 | 0.9793 | 0.025725 | -0.062645 | 123.0534 | 122.9122 | 123.0086 | 31.7584 | -123.1652 | 122.8811 | 123.0818 | 122.9934 | 33.3453 | -123.3059
408.9375 | 123.7701 | -66.0553 | 57.0053 | 0.048435 | -0.038357 | -0.0035824 | 0.052202 | -0.0076669 | 0.050003 | 0.087021 | -0.0056032 | -0.0038645 | 0.055804 | 0.047427 | 0.05373 | -62.5718 | -34.1504 | -65.1024 | 56.9615 | 56.8157 | 56.9212 | -66.2056 | -64.893 | -32.4719 | -65.3671 | 56.7892 | 56.9898 | 56.9381 | -66.3281 | -0.15032 | -0.043821 | 3.4835 | 0.9529 | 1.1032 | -0.18966 | -0.084094 | -0.27276 | -0.21614 | 1.1623 | 0.68823 | 0.96099 | -0.015474 | -0.067216 | 123.0168 | 122.871 | 122.9765 | 31.9049 | -123.2109 | 122.8445 | 123.0451 | 122.9934 | 33.5834 | -123.3334
409.9375 | 123.5687 | -66.0324 | 56.9824 | 0.078959 | -0.038357 | -0.0046504 | 0.052202 | -0.0076669 | 0.048935 | 0.041238 | -0.0066712 | -0.0038645 | 0.055804 | 0.047427 | 0.05373 | -62.3474 | -34.1824 | -65.0429 | 56.9661 | 56.8248 | 56.9258 | -66.1919 | -64.9205 | -32.6046 | -65.3304 | 56.8075 | 56.9944 | 56.9473 | -66.3281 | -0.15948 | -0.016355 | 3.685 | 0.98953 | 1.149 | -0.15761 | -0.056628 | -0.29565 | -0.17494 | 1.1119 | 0.70197 | 0.99762 | 0.011993 | -0.03517 | 122.9985 | 122.8572 | 122.9582 | 31.85 | -123.1743 | 122.8399 | 123.0268 | 122.9797 | 33.4278 | -123.3105
410.9375 | 123.6923 | -66.0461 | 56.9916 | 0.033173 | -0.037288 | -0.0025134 | 0.052202 | -0.0076669 | 0.048935 | 0.025977 | -0.0066712 | -0.0027965 | 0.056873 | 0.047427 | 0.054798 | -62.32 | -34.0268 | -65.0383 | 56.9661 | 56.8294 | 56.9212 | -66.1919 | -64.9388 | -32.6779 | -65.3213 | 56.7983 | 57.0127 | 56.9518 | -66.3235 | -0.14574 | -0.02551 | 3.7262 | 1.0078 | 1.1536 | -0.16219 | -0.070361 | -0.27733 | -0.19325 | 1.1073 | 0.72486 | 1.0022 | 0.021152 | -0.039747 | 123.0122 | 122.8755 | 122.9674 | 32.0194 | -123.1835 | 122.8445 | 123.0589 | 122.998 | 33.3683 | -123.3151
411.9531 | 123.4177 | -66.0645 | 56.9916 | 0.063697 | -0.03622 | -0.0046504 | 0.052202 | -0.0087349 | 0.051071 | 0.056499 | -0.0077392 | -0.0027965 | 0.055804 | 0.046359 | 0.054798 | -62.3658 | -33.9031 | -64.9467 | 56.9661 | 56.8294 | 56.935 | -66.1827 | -64.8655 | -32.8015 | -65.303 | 56.8121 | 57.0127 | 56.9564 | -66.3235 | -0.11827 | -0.02551 | 3.6987 | 1.1177 | 1.236 | -0.16219 | -0.056625 | -0.25902 | -0.17951 | 1.1989 | 0.76149 | 1.0205 | 0.021152 | -0.035168 | 123.0305 | 122.8938 | 122.9994 | 32.1613 | -123.1743 | 122.8765 | 123.0772 | 123.0209 | 33.2629 | -123.3151
412.9375 | 123.7381 | -66.0049 | 56.9778 | 0.048435 | -0.038357 | -0.0046504 | 0.050065 | -0.0087349 | 0.048935 | 0.056499 | -0.0077392 | -0.0049335 | 0.054736 | 0.047427 | 0.05373 | -62.5443 | -33.839 | -64.9467 | 56.9752 | 56.8385 | 56.935 | -66.1736 | -64.8655 | -32.9068 | -65.2801 | 56.8166 | 57.0219 | 56.961 | -66.3097 | -0.16863 | -0.00262 | 3.4606 | 1.0582 | 1.2268 | -0.13929 | -0.042892 | -0.3048 | -0.1612 | 1.1394 | 0.72487 | 1.0297 | 0.044042 | -0.016857 | 122.9802 | 122.8435 | 122.9399 | 32.1659 | -123.1514 | 122.8216 | 123.0268 | 122.9659 | 33.0981 | -123.2876
413.9531 | 123.5367 | -66.0416 | 57.0328 | 0.048435 | -0.040493 | -0.0025134 | 0.053271 | -0.0087349 | 0.050003 | 0.087021 | -0.0077392 | -0.0038645 | 0.055804 | 0.046359 | 0.05373 | -62.3154 | -33.7292 | -64.9238 | 56.9981 | 56.8477 | 56.9533 | -66.1781 | -64.8472 | -32.9068 | -65.2526 | 56.8258 | 57.031 | 56.9656 | -66.3097 | -0.13658 | -0.03466 | 3.7262 | 1.1177 | 1.2543 | -0.18507 | -0.07951 | -0.26818 | -0.20698 | 1.1943 | 0.78896 | 1.0571 | -0.001732 | -0.06721 | 123.0397 | 122.8893 | 122.9948 | 32.3124 | -123.2109 | 122.8674 | 123.0726 | 123.0071 | 33.1347 | -123.3425
414.9375 | 123.6603 | -66.0461 | 56.9916 | 0.033173 | -0.038357 | -0.0025134 | 0.052202 | -0.0076669 | 0.050003 | 0.056499 | -0.0056032 | -0.0017285 | 0.056873 | 0.046359 | 0.052662 | -62.1964 | -33.6696 | -64.9055 | 56.9935 | 56.8477 | 56.9533 | -66.1644 | -64.8472 | -32.8977 | -65.2114 | 56.835 | 57.0356 | 56.9381 | -66.296 | -0.11827 | 0.001961 | 3.8498 | 1.1406 | 1.2589 | -0.14387 | -0.038311 | -0.24986 | -0.15662 | 1.1989 | 0.83475 | 1.0846 | 0.044045 | -0.053483 | 123.0397 | 122.8939 | 122.9994 | 32.3765 | -123.156 | 122.8811 | 123.0818 | 122.9842 | 33.1485 | -123.2876
415.9375 | 123.6465 | -66.0141 | 57.0053 | 0.063697 | -0.038357 | -0.0025134 | 0.050065 | -0.0087349 | 0.050003 | 0.056499 | -0.0056032 | -0.0038645 | 0.056873 | 0.047427 | 0.054798 | -62.2559 | -33.7017 | -64.8552 | 57.0027 | 56.8569 | 56.9624 | -66.1598 | -64.7785 | -32.8885 | -65.2068 | 56.8441 | 57.0402 | 56.9885 | -66.2868 | -0.14573 | -0.002616 | 3.7582 | 1.1589 | 1.3047 | -0.14845 | -0.042887 | -0.27275 | -0.1612 | 1.2356 | 0.80729 | 1.08 | 0.034891 | -0.016851 | 123.0168 | 122.871 | 122.9765 | 32.3124 | -123.1651 | 122.8582 | 123.0543 | 123.0026 | 33.1256 | -123.2922
416.9531 | 123.3994 | -66.0004 | 57.0511 | 0.048435 | -0.03622 | -0.0025134 | 0.050065 | -0.0076669 | 0.05214 | 0.07176 | -0.0066712 | -0.0038645 | 0.056873 | 0.047427 | 0.05373 | -62.3383 | -33.7063 | -64.8598 | 57.0119 | 56.8706 | 56.9853 | -66.1598 | -64.8381 | -33.0671 | -65.1244 | 56.8533 | 57.0539 | 56.993 | -66.2823 | -0.15947 | -0.039235 | 3.6621 | 1.1406 | 1.3001 | -0.18048 | -0.06577 | -0.2819 | -0.19782 | 1.1623 | 0.87597 | 1.1579 | 0.002851 | -0.058048 | 123.0122 | 122.871 | 122.9857 | 32.2941 | -123.2109 | 122.8536 | 123.0543 | 122.9934 | 32.9333 | -123.3334
417.9375 | 123.2162 | -66.0553 | 57.0602 | 0.048435 | -0.039425 | -0.0025134 | 0.052202 | -0.0076669 | 0.051071 | 0.041238 | -0.0056032 | -0.0027965 | 0.055804 | 0.048496 | 0.052662 | -62.5306 | -33.7521 | -64.7682 | 57.0164 | 56.8752 | 56.9807 | -66.1553 | -64.8701 | -33.1953 | -65.1564 | 56.8624 | 57.0539 | 57.0022 | -66.2823 | -0.099956 | -0.043813 | 3.5247 | 1.2871 | 1.3871 | -0.18506 | -0.079504 | -0.22697 | -0.19782 | 1.1852 | 0.89885 | 1.1258 | -0.006305 | -0.058047 | 123.0717 | 122.9305 | 123.036 | 32.3032 | -123.2155 | 122.9177 | 123.1092 | 123.0575 | 32.86 | -123.3425
418.9531 | 123.3261 | -65.9866 | 57.0236 | 0.063697 | -0.039425 | -0.0014454 | 0.052202 | -0.0076669 | 0.050003 | 0.056499 | -0.0066712 | -0.0027965 | 0.055804 | 0.048496 | 0.051594 | -62.4939 | -33.8024 | -64.7316 | 57.0256 | 56.8935 | 56.9945 | -66.1461 | -64.8381 | -33.2731 | -65.1244 | 56.867 | 57.0677 | 57.0205 | -66.2731 | -0.15946 | 0.001965 | 3.4927 | 1.2551 | 1.4145 | -0.13012 | -0.029148 | -0.28648 | -0.15662 | 1.1486 | 0.86224 | 1.1487 | 0.044051 | -0.003112 | 123.0122 | 122.8801 | 122.9811 | 32.1842 | -123.1697 | 122.8536 | 123.0543 | 123.0071 | 32.7135 | -123.2967
419.9375 | 123.2437 | -66.0095 | 57.0694 | 0.063697 | -0.037288 | -0.0025134 | 0.052202 | -0.0076669 | 0.05214 | 0.07176 | -0.0077392 | -0.0027965 | 0.055804 | 0.048496 | 0.051594 | -62.4436 | -33.9672 | -64.6949 | 57.0347 | 56.8935 | 56.9991 | -66.1278 | -64.8106 | -33.2273 | -65.1107 | 56.8762 | 57.0768 | 56.993 | -66.2502 | -0.11826 | -0.034654 | 3.5659 | 1.3146 | 1.4328 | -0.1759 | -0.070345 | -0.2407 | -0.19324 | 1.1989 | 0.89886 | 1.1396 | 0.007433 | -0.076359 | 123.0443 | 122.903 | 123.0086 | 32.0423 | -123.1972 | 122.8857 | 123.0864 | 123.0026 | 32.7822 | -123.3196
420.9375 | 123.3627 | -65.9409 | 57.106 | 0.048435 | -0.038357 | -0.0025134 | 0.051134 | -0.0065979 | 0.050003 | 0.07176 | -0.0056032 | -0.0027965 | 0.056873 | 0.047427 | 0.05373 | -62.4298 | -34.0771 | -64.64 | 57.0485 | 56.9072 | 57.0128 | -66.1232 | -64.7694 | -33.1724 | -65.0695 | 56.8807 | 57.086 | 57.0434 | -66.2548 | -0.18235 | -0.05754 | 3.511 | 1.3009 | 1.4832 | -0.19879 | -0.09323 | -0.31394 | -0.22528 | 1.1715 | 0.8714 | 1.1853 | -0.020031 | -0.062616 | 122.9893 | 122.8481 | 122.9536 | 31.8637 | -123.2292 | 122.8216 | 123.0268 | 122.9843 | 32.7685 | -123.3608
421.9531 | 123.3307 | -65.95 | 57.0694 | 0.063697 | -0.039425 | -0.0025134 | 0.052202 | -0.0065979 | 0.050003 | 0.07176 | -0.0066712 | -0.0027965 | 0.053668 | 0.048496 | 0.054798 | -62.3612 | -34.2282 | -64.5805 | 57.0576 | 56.9164 | 57.0311 | -66.1003 | -64.7236 | -33.1724 | -65.0557 | 56.9082 | 57.1043 | 57.0205 | -66.2319 | -0.15029 | -0.011762 | 3.5888 | 1.3695 | 1.5198 | -0.15301 | -0.038295 | -0.28189 | -0.16119 | 1.2264 | 0.8943 | 1.1762 | 0.034904 | -0.048888 | 123.0076 | 122.8664 | 122.9811 | 31.7218 | -123.1697 | 122.8582 | 123.0543 | 122.9705 | 32.7776 | -123.3013
422.9375 | 123.2025 | -65.9729 | 57.1152 | 0.048435 | -0.040493 | -0.0014454 | 0.053271 | -0.0087349 | 0.048935 | 0.07176 | -0.0066712 | -0.0038645 | 0.053668 | 0.049564 | 0.054798 | -62.2513 | -34.3427 | -64.5347 | 57.0805 | 56.9347 | 57.0403 | -66.1003 | -64.687 | -33.1495 | -65.0099 | 56.9174 | 57.1135 | 57.0709 | -66.2136 | -0.12741 | -0.034646 | 3.7216 | 1.4382 | 1.5656 | -0.18047 | -0.074914 | -0.24069 | -0.1978 | 1.2859 | 0.96297 | 1.2037 | -0.001714 | -0.044299 | 123.0534 | 122.9076 | 123.0132 | 31.6302 | -123.2155 | 122.8903 | 123.0864 | 123.0438 | 32.8234 | -123.3288
423.9531 | 123.2758 | -65.9409 | 57.1564 | 0.048435 | -0.039425 | -0.0046504 | 0.051134 | -0.0087349 | 0.048935 | 0.07176 | -0.0077392 | -0.0038645 | 0.053668 | 0.050632 | 0.052662 | -62.3017 | -34.5258 | -64.4889 | 57.0805 | 56.9393 | 57.0448 | -66.0866 | -64.6595 | -33.1266 | -64.9825 | 56.9265 | 57.1272 | 57.0617 | -66.209 | -0.14571 | -0.075845 | 3.6392 | 1.4519 | 1.5977 | -0.21709 | -0.11153 | -0.26815 | -0.22985 | 1.2814 | 0.9584 | 1.2266 | -0.029178 | -0.094655 | 123.0214 | 122.8801 | 122.9857 | 31.415 | -123.2429 | 122.8674 | 123.0681 | 123.0026 | 32.8142 | -123.3654
424.9375 | 123.1842 | -65.9592 | 57.1289 | 0.048435 | -0.038357 | -0.00037739 | 0.051134 | -0.0065979 | 0.051071 | 0.025977 | -0.0056032 | -0.0017285 | 0.056873 | 0.048496 | 0.052662 | -62.1643 | -34.6632 | -64.434 | 57.0988 | 56.9484 | 57.0586 | -66.0728 | -64.6274 | -33.1861 | -64.9596 | 56.9403 | 57.1409 | 57.08 | -66.209 | -0.11367 | -0.030066 | 3.7949 | 1.5252 | 1.6389 | -0.18046 | -0.070332 | -0.24984 | -0.18865 | 1.3317 | 0.9996 | 1.2494 | 0.012024 | -0.048875 | 123.058 | 122.9076 | 123.0177 | 31.296 | -123.2017 | 122.8994 | 123.1001 | 123.0392 | 32.773 | -123.3379
425.9375 | 123.2529 | -65.9088 | 57.0923 | 0.033173 | -0.039425 | -0.0025134 | 0.053271 | -0.0065979 | 0.051071 | 0.056499 | -0.0056032 | -0.0027965 | 0.054736 | 0.049564 | 0.054798 | -62.1506 | -34.7868 | -64.379 | 57.108 | 56.9668 | 57.0723 | -66.0545 | -64.5633 | -33.2411 | -64.9184 | 56.9494 | 57.1547 | 57.0892 | -66.1907 | -0.14571 | 0.015712 | 3.7582 | 1.5298 | 1.6755 | -0.12553 | -0.019975 | -0.28188 | -0.14287 | 1.3455 | 0.99046 | 1.2723 | 0.062381 | -0.003097 | 123.0168 | 122.8756 | 122.9811 | 31.122 | -123.1468 | 122.8582 | 123.0635 | 122.998 | 32.6677 | -123.283
426.9375 | 123.6328 | -65.918 | 57.1655 | 0.048435 | -0.039425 | -0.0025134 | 0.053271 | -0.0087349 | 0.050003 | 0.056499 | -0.0056032 | -0.0027965 | 0.054736 | 0.049564 | 0.052662 | -62.1918 | -34.9013 | -64.2417 | 57.1217 | 56.9805 | 57.086 | -66.0545 | -64.6686 | -33.0946 | -64.8726 | 56.9586 | 57.1638 | 57.1029 | -66.1724 | -0.13655 | -0.043795 | 3.7262 | 1.6763 | 1.8128 | -0.18503 | -0.079482 | -0.25441 | -0.20695 | 1.2493 | 1.0454 | 1.2998 | -0.001704 | -0.062603 | 123.0397 | 122.8985 | 123.004 | 31.0167 | -123.22 | 122.8765 | 123.0818 | 123.0209 | 32.8234 | -123.3379
427.9375 | 123.5779 | -65.9271 | 57.1793 | 0.063697 | -0.041562 | -0.0046504 | 0.052202 | -0.0076669 | 0.05214 | 0.041238 | -0.0066712 | -0.0027965 | 0.056873 | 0.049564 | 0.052662 | -62.0315 | -34.9516 | -64.2188 | 57.1355 | 56.9897 | 57.1044 | -66.0454 | -64.6686 | -33.0213 | -64.8497 | 56.9632 | 57.1638 | 57.0846 | -66.1632 | -0.11824 | -0.043792 | 3.8956 | 1.7083 | 1.8266 | -0.18961 | -0.0749 | -0.2361 | -0.21611 | 1.2585 | 1.0775 | 1.3135 | -0.015437 | -0.09465 | 123.0626 | 122.9168 | 123.0315 | 30.9755 | -123.2246 | 122.8903 | 123.0909 | 123.0117 | 32.9058 | -123.3425
428.9531 | 123.6786 | -65.8722 | 57.1884 | 0.063697 | -0.039425 | -0.0014454 | 0.052202 | -0.0076669 | 0.048935 | 0.041238 | -0.0066712 | -0.0027965 | 0.055804 | 0.047427 | 0.052662 | -62.0773 | -35.002 | -64.1455 | 57.1492 | 56.9988 | 57.1089 | -66.027 | -64.4947 | -33.0121 | -64.7947 | 56.986 | 57.1821 | 57.1304 | -66.1541 | -0.15485 | -0.039213 | 3.7949 | 1.7267 | 1.8815 | -0.1896 | -0.079477 | -0.28187 | -0.20237 | 1.3775 | 1.0775 | 1.3593 | -0.006278 | -0.05802 | 123.0214 | 122.871 | 122.9811 | 30.8702 | -123.2155 | 122.8582 | 123.0543 | 123.0026 | 32.8601 | -123.3425
429.9375 | 123.7701 | -65.863 | 57.2479 | 0.078959 | -0.041562 | -0.0025134 | 0.051134 | -0.0087349 | 0.051071 | 0.07176 | -0.0066712 | -0.0038645 | 0.054736 | 0.049564 | 0.052662 | -61.9216 | -35.1302 | -64.0677 | 57.1629 | 57.0125 | 57.1227 | -66.0133 | -64.5679 | -33.0533 | -64.7352 | 56.9906 | 57.1959 | 57.1396 | -66.1357 | -0.15027 | -0.084987 | 3.9414 | 1.7953 | 1.9456 | -0.23538 | -0.12525 | -0.27271 | -0.2573 | 1.2951 | 1.1278 | 1.4005 | -0.052052 | -0.10837 | 123.026 | 122.8756 | 122.9857 | 30.7328 | -123.2612 | 122.8537 | 123.0589 | 123.0026 | 32.8097 | -123.3837
430.9531 | 124.4431 | -65.863 | 57.1976 | 0.063697 | -0.041562 | -0.0025134 | 0.052202 | -0.0065979 | 0.050003 | 0.087021 | -0.0066712 | -0.0038645 | 0.057941 | 0.048496 | 0.051594 | -61.9537 | -35.1806 | -64.0814 | 57.1721 | 57.0354 | 57.141 | -65.9904 | -64.4397 | -32.8153 | -64.6482 | 56.9998 | 57.2096 | 57.1304 | -66.122 | -0.12738 | -0.025476 | 3.9093 | 1.7816 | 1.909 | -0.16213 | -0.056582 | -0.25897 | -0.19779 | 1.4233 | 1.2148 | 1.4738 | 0.012038 | -0.067175 | 123.0351 | 122.8985 | 123.004 | 30.6825 | -123.188 | 122.8628 | 123.0726 | 122.9934 | 33.0478 | -123.3196
431.9375 | 123.23 | -65.8813 | 57.2662 | 0.048435 | -0.040493 | -0.00037739 | 0.052202 | -0.0076669 | 0.050003 | 0.056499 | -0.0066712 | -0.0038645 | 0.055804 | 0.050632 | 0.052662 | -61.5554 | -35.295 | -64.0311 | 57.1996 | 57.0492 | 57.1547 | -65.9767 | -64.2749 | -32.9114 | -64.6482 | 57.0227 | 57.2325 | 57.1808 | -66.1083 | -0.095328 | -0.06667 | 4.326 | 1.8503 | 1.9456 | -0.21706 | -0.11151 | -0.22693 | -0.24356 | 1.6065 | 1.2331 | 1.4601 | -0.033733 | -0.085475 | 123.0809 | 122.9305 | 123.0361 | 30.5863 | -123.2429 | 122.904 | 123.1138 | 123.0621 | 32.9699 | -123.3745
432.9375 | 123.2208 | -65.8218 | 57.2571 | 0.063697 | -0.040493 | -0.00037739 | 0.052202 | -0.0087349 | 0.050003 | 0.087021 | -0.0056032 | -0.0027965 | 0.054736 | 0.049564 | 0.05373 | -61.6698 | -35.3179 | -63.9304 | 57.2133 | 57.0721 | 57.1776 | -65.9584 | -64.2383 | -33.003 | -64.6482 | 57.0456 | 57.2508 | 57.1808 | -66.0808 | -0.13652 | -0.04378 | 4.152 | 1.8915 | 2.028 | -0.18501 | -0.079462 | -0.25896 | -0.21151 | 1.5836 | 1.1736 | 1.4326 | -0.006263 | -0.07632 | 123.0351 | 122.8939 | 122.9995 | 30.5039 | -123.2154 | 122.8674 | 123.0727 | 123.0026 | 32.8189 | -123.3379
433.9375 | 123.3078 | -65.7761 | 57.2662 | 0.033173 | -0.039425 | -0.0035824 | 0.052202 | -0.0087349 | 0.050003 | 0.087021 | -0.0066712 | -0.0049335 | 0.054736 | 0.050632 | 0.054798 | -61.6607 | -35.437 | -63.8388 | 57.2499 | 57.1041 | 57.2097 | -65.9126 | -64.165 | -32.948 | -64.5795 | 57.0776 | 57.2874 | 57.2265 | -66.0579 | -0.13651 | -0.016308 | 4.1154 | 1.9373 | 2.0738 | -0.16211 | -0.056567 | -0.28185 | -0.18862 | 1.6111 | 1.1965 | 1.4784 | 0.02121 | -0.039689 | 123.026 | 122.8802 | 122.9857 | 30.3391 | -123.1788 | 122.8537 | 123.0635 | 123.0026 | 32.828 | -123.3241
434.9375 | 123.2025 | -65.7761 | 57.312 | 0.078959 | -0.039425 | -0.0025134 | 0.053271 | -0.0087349 | 0.051071 | 0.056499 | -0.0066712 | -0.0038645 | 0.055804 | 0.049564 | 0.054798 | -61.5233 | -35.5057 | -63.7747 | 57.2591 | 57.1179 | 57.2234 | -65.9034 | -64.1055 | -32.861 | -64.5337 | 57.1005 | 57.3058 | 57.2494 | -66.035 | -0.12735 | -0.052928 | 4.2527 | 2.0014 | 2.1287 | -0.19415 | -0.088608 | -0.25895 | -0.2115 | 1.6706 | 1.2423 | 1.5013 | -0.006252 | -0.062573 | 123.0351 | 122.8939 | 122.9995 | 30.2704 | -123.2154 | 122.8766 | 123.0818 | 123.0255 | 32.915 | -123.347
435.9531 | 123.3444 | -65.7211 | 57.2891 | 0.078959 | -0.04263 | -0.0035824 | 0.051134 | -0.0087349 | 0.05214 | 0.07176 | -0.0077392 | -0.0017285 | 0.054736 | 0.050632 | 0.051594 | -61.5187 | -35.3958 | -63.706 | 57.2637 | 57.127 | 57.228 | -65.8988 | -64.0551 | -32.8885 | -64.4925 | 57.0959 | 57.3103 | 57.254 | -66.0304 | -0.1777 | -0.025462 | 4.2024 | 2.0151 | 2.1928 | -0.1621 | -0.061142 | -0.3093 | -0.19319 | 1.666 | 1.2286 | 1.5379 | 0.021214 | -0.035106 | 122.9848 | 122.8482 | 122.9491 | 30.3254 | -123.188 | 122.8171 | 123.0315 | 122.9751 | 32.8326 | -123.3196
436.9375 | 123.2574 | -65.7303 | 57.3486 | 0.078959 | -0.041562 | -0.0025134 | 0.052202 | -0.0076669 | 0.047866 | 0.07176 | -0.0066712 | -0.0027965 | 0.054736 | 0.052769 | 0.05373 | -61.418 | -35.2493 | -63.6145 | 57.2957 | 57.1545 | 57.2646 | -65.8714 | -63.9681 | -32.8702 | -64.433 | 57.1188 | 57.3378 | 57.2815 | -66.003 | -0.14107 | -0.052922 | 4.3123 | 2.1158 | 2.2569 | -0.19414 | -0.084022 | -0.27267 | -0.22981 | 1.7622 | 1.2973 | 1.5699 | -0.010823 | -0.067143 | 123.026 | 122.8848 | 122.9949 | 30.481 | -123.22 | 122.8491 | 123.0681 | 123.0118 | 32.8601 | -123.3516
437.9531 | 123.2574 | -65.7028 | 57.3578 | 0.063697 | -0.040493 | -0.0025134 | 0.051134 | -0.0065979 | 0.051071 | 0.041238 | -0.0066712 | -0.0027965 | 0.054736 | 0.052769 | 0.05373 | -61.3539 | -35.1348 | -63.5366 | 57.3003 | 57.1591 | 57.2738 | -65.853 | -63.8903 | -32.9343 | -64.3872 | 57.1326 | 57.347 | 57.2952 | -65.9938 | -0.15022 | -0.057498 | 4.3489 | 2.1662 | 2.3164 | -0.19871 | -0.08402 | -0.29098 | -0.22523 | 1.8126 | 1.3156 | 1.6066 | -0.010821 | -0.062563 | 123.0031 | 122.8619 | 122.9766 | 30.568 | -123.2108 | 122.8354 | 123.0498 | 122.998 | 32.7685 | -123.3516
438.9375 | 123.2162 | -65.712 | 57.3486 | 0.048435 | -0.041562 | -0.00037739 | 0.050065 | -0.0076669 | 0.050003 | 0.056499 | -0.0056032 | -0.0027965 | 0.055804 | 0.051701 | 0.052662 | -61.2669 | -35.2676 | -63.4588 | 57.3278 | 57.1865 | 57.2921 | -65.8347 | -63.7987 | -33.0213 | -64.3323 | 57.1509 | 57.3744 | 57.3135 | -65.9663 | -0.12275 | -0.020873 | 4.445 | 2.2532 | 2.3759 | -0.16208 | -0.05655 | -0.25436 | -0.19776 | 1.9133 | 1.3797 | 1.6341 | 0.025806 | -0.035093 | 123.0397 | 122.8985 | 123.0041 | 30.4444 | -123.1834 | 122.8628 | 123.0864 | 123.0255 | 32.6907 | -123.315
439.9375 | 123.2483 | -65.6525 | 57.4127 | 0.078959 | -0.040493 | -0.0014454 | 0.052202 | -0.0076669 | 0.050003 | 0.056499 | -0.0088072 | -0.0038645 | 0.055804 | 0.052769 | 0.05373 | -61.1525 | -35.5789 | -63.3581 | 57.3644 | 57.2186 | 57.3333 | -65.8027 | -63.6934 | -32.8839 | -64.2544 | 57.2012 | 57.4111 | 57.3639 | -65.9389 | -0.15021 | -0.048333 | 4.5 | 2.2944 | 2.4446 | -0.19412 | -0.07943 | -0.28639 | -0.21149 | 1.9591 | 1.398 | 1.6844 | -0.001652 | -0.048816 | 123.0169 | 122.8711 | 122.9858 | 30.0736 | -123.2154 | 122.8537 | 123.0635 | 123.0164 | 32.7685 | -123.3516
440.9531 | 123.2117 | -65.6754 | 57.4402 | 0.048435 | -0.040493 | -0.0014454 | 0.051134 | -0.0087349 | 0.050003 | 0.10228 | -0.0077392 | -0.0049335 | 0.054736 | 0.051701 | 0.05373 | -61.0792 | -35.8811 | -63.2802 | 57.3781 | 57.2278 | 57.3379 | -65.7889 | -63.6064 | -33.1129 | -64.1858 | 57.2104 | 57.4156 | 57.3776 | -65.9297 | -0.11359 | -0.062064 | 4.5961 | 2.3951 | 2.5087 | -0.21243 | -0.10232 | -0.25435 | -0.22979 | 2.069 | 1.4896 | 1.7439 | -0.02454 | -0.062546 | 123.0535 | 122.9031 | 123.0132 | 29.7943 | -123.2291 | 122.8857 | 123.091 | 123.053 | 32.5625 | -123.3699
441.9531 | 123.2849 | -65.6433 | 57.4219 | 0.063697 | -0.041562 | -0.0025134 | 0.050065 | -0.0087349 | 0.048935 | 0.056499 | -0.0077392 | -0.0049335 | 0.056873 | 0.050632 | 0.05373 | -61.1067 | -36.3893 | -63.2207 | 57.3735 | 57.2186 | 57.3333 | -65.7935 | -63.5331 | -33.209 | -64.1583 | 57.1875 | 57.4111 | 57.3502 | -65.9343 | -0.15021 | -0.048331 | 4.5366 | 2.4226 | 2.5728 | -0.20327 | -0.088585 | -0.29097 | -0.23438 | 2.1102 | 1.485 | 1.776 | -0.010807 | -0.071706 | 123.0169 | 122.8619 | 122.9766 | 29.254 | -123.2154 | 122.8308 | 123.0544 | 122.9935 | 32.4343 | -123.3562
442.9531 | 123.2758 | -65.593 | 57.431 | 0.063697 | -0.04263 | -0.0025134 | 0.053271 | -0.0087349 | 0.051071 | 0.041238 | -0.0066712 | -0.0038645 | 0.055804 | 0.050632 | 0.054798 | -61.006 | -36.7465 | -63.12 | 57.401 | 57.2552 | 57.3608 | -65.766 | -63.4049 | -33.3006 | -64.0667 | 57.2058 | 57.4385 | 57.3731 | -65.8976 | -0.17309 | -0.030016 | 4.587 | 2.4729 | 2.646 | -0.1758 | -0.070268 | -0.30469 | -0.22522 | 2.188 | 1.5262 | 1.8309 | 0.007509 | -0.057968 | 122.994 | 122.8482 | 122.9537 | 28.8465 | -123.1971 | 122.7988 | 123.0315 | 122.966 | 32.2924 | -123.3287
443.9375 | 123.3261 | -65.5655 | 57.4585 | 0.048435 | -0.04263 | -0.0014454 | 0.051134 | -0.0087349 | 0.05214 | 0.056499 | -0.0066712 | -0.0027965 | 0.053668 | 0.052769 | 0.05373 | -60.8411 | -37.1036 | -63.0055 | 57.4468 | 57.2919 | 57.4065 | -65.7111 | -63.2584 | -33.3372 | -63.966 | 57.2241 | 57.4889 | 57.4234 | -65.8564 | -0.14561 | -0.011698 | 4.7243 | 2.5599 | 2.7055 | -0.16663 | -0.051948 | -0.29095 | -0.23437 | 2.3071 | 1.5995 | 1.8905 | 0.030408 | -0.03507 | 123.0123 | 122.8574 | 122.972 | 28.4619 | -123.1696 | 122.7896 | 123.0544 | 122.9889 | 32.2283 | -123.3149
444.9375 | 123.2483 | -65.4694 | 57.5729 | 0.063697 | -0.043699 | -0.00037739 | 0.053271 | -0.0076669 | 0.050003 | 0.087021 | -0.0088072 | -0.0049335 | 0.055804 | 0.053837 | 0.052662 | -60.7038 | -37.1677 | -62.8819 | 57.5063 | 57.356 | 57.4615 | -65.6516 | -63.1073 | -33.3693 | -63.8561 | 57.3111 | 57.5438 | 57.4784 | -65.7878 | -0.18221 | -0.06662 | 4.7656 | 2.5874 | 2.7696 | -0.21697 | -0.11145 | -0.3184 | -0.26182 | 2.362 | 1.6133 | 1.9317 | -0.02909 | -0.094568 | 122.9757 | 122.8253 | 122.9309 | 28.3017 | -123.2245 | 122.7805 | 123.0132 | 122.9477 | 32.1001 | -123.3607
445.9375 | 123.3398 | -65.4053 | 57.5912 | 0.033173 | -0.04263 | -0.0025134 | 0.050065 | -0.0098029 | 0.051071 | 0.07176 | -0.0066712 | -0.0049335 | 0.054736 | 0.051701 | 0.052662 | -60.5481 | -37.186 | -62.7263 | 57.5658 | 57.4155 | 57.5347 | -65.5966 | -62.9516 | -33.6028 | -63.737 | 57.3752 | 57.6171 | 57.547 | -65.7237 | -0.19135 | -0.025412 | 4.8571 | 2.679 | 2.8704 | -0.17575 | -0.056499 | -0.31838 | -0.21603 | 2.4536 | 1.6682 | 1.9866 | 0.025857 | -0.0442 | 122.9711 | 122.8208 | 122.94 | 28.2193 | -123.1879 | 122.7805 | 123.0224 | 122.9523 | 31.8025 | -123.3149
446.9375 | 123.3215 | -65.3183 | 57.6828 | 0.063697 | -0.04263 | -0.0014454 | 0.051134 | -0.0076669 | 0.05214 | 0.07176 | -0.0077392 | -0.0027965 | 0.055804 | 0.051701 | 0.055867 | -60.3055 | -37.2181 | -62.566 | 57.6574 | 57.4933 | 57.6172 | -65.5005 | -62.7639 | -33.7127 | -63.5631 | 57.4347 | 57.7087 | 57.6295 | -65.6412 | -0.18217 | -0.025396 | 5.0128 | 2.7523 | 2.9344 | -0.18946 | -0.065637 | -0.32294 | -0.24806 | 2.5544 | 1.7552 | 2.0782 | 0.025877 | -0.053337 | 122.9757 | 122.8116 | 122.9355 | 28.1002 | -123.1833 | 122.753 | 123.027 | 122.9478 | 31.6056 | -123.324
447.9375 | 123.1796 | -65.3778 | 57.724 | 0.048435 | -0.044767 | -0.0014454 | 0.053271 | -0.0076669 | 0.05214 | 0.087021 | -0.0077392 | -0.0027965 | 0.054736 | 0.054906 | 0.054798 | -60.0033 | -36.7236 | -62.4333 | 57.6986 | 57.53 | 57.6584 | -65.473 | -62.622 | -33.8088 | -63.4394 | 57.4851 | 57.7361 | 57.6524 | -65.6 | -0.095186 | -0.02539 | 5.3745 | 2.9445 | 3.0397 | -0.19403 | -0.065628 | -0.22222 | -0.2389 | 2.7558 | 1.9384 | 2.1606 | 0.012149 | -0.071643 | 123.0764 | 122.9078 | 123.0362 | 28.6542 | -123.197 | 122.8629 | 123.114 | 123.0302 | 31.569 | -123.324
448.9375 | 123.2117 | -65.3458 | 57.7744 | 0.063697 | -0.04263 | -0.0014454 | 0.053271 | -0.0065979 | 0.05214 | 0.041238 | -0.0077392 | -0.0027965 | 0.056873 | 0.051701 | 0.05373 | -59.7194 | -36.2749 | -62.3051 | 57.7352 | 57.5712 | 57.695 | -65.4455 | -62.4571 | -33.9187 | -63.2792 | 57.5584 | 57.7819 | 57.6981 | -65.5634 | -0.099757 | -0.039117 | 5.6263 | 3.0407 | 3.1404 | -0.20318 | -0.079353 | -0.21763 | -0.21599 | 2.8886 | 2.0666 | 2.2842 | 0.007581 | -0.076211 | 123.081 | 122.9169 | 123.0408 | 29.0709 | -123.2199 | 122.9041 | 123.1277 | 123.0439 | 31.427 | -123.3377
449.9531 | 123.3398 | -65.2084 | 57.7927 | 0.078959 | -0.04263 | 0.0017596 | 0.053271 | -0.0087349 | 0.051071 | 0.056499 | -0.0088072 | -0.0017285 | 0.054736 | 0.052769 | 0.054798 | -59.4951 | -35.8994 | -62.186 | 57.7535 | 57.5941 | 57.7179 | -65.4089 | -62.2877 | -34.0469 | -63.1281 | 57.5858 | 57.8002 | 57.7119 | -65.5405 | -0.20045 | -0.039114 | 5.7133 | 3.0224 | 3.2229 | -0.19859 | -0.074771 | -0.33207 | -0.20684 | 2.9207 | 2.0804 | 2.4124 | 0.007585 | -0.080786 | 122.962 | 122.8025 | 122.9263 | 29.309 | -123.2016 | 122.7943 | 123.0087 | 122.9203 | 31.1615 | -123.3332
450.9375 | 123.2849 | -65.1947 | 57.811 | 0.033173 | -0.04263 | -0.00037739 | 0.052202 | -0.0065979 | 0.05214 | 0.041238 | -0.0077392 | -0.0027965 | 0.054736 | 0.052769 | 0.05373 | -59.2067 | -35.7025 | -62.0533 | 57.7948 | 57.6215 | 57.7591 | -65.3677 | -62.1229 | -34.1797 | -62.9907 | 57.6041 | 57.8323 | 57.7485 | -65.5084 | -0.17298 | -0.016219 | 5.988 | 3.1414 | 3.3144 | -0.18943 | -0.051874 | -0.31375 | -0.20683 | 3.0718 | 2.204 | 2.5177 | 0.021325 | -0.062467 | 122.9895 | 122.8162 | 122.9538 | 29.4922 | -123.1787 | 122.7988 | 123.027 | 122.9432 | 31.015 | -123.3194
451.9375 | 123.3353 | -65.1855 | 57.7881 | 0.078959 | -0.04263 | -0.0014454 | 0.053271 | -0.0076669 | 0.051071 | 0.056499 | -0.0077392 | -0.00065947 | 0.055804 | 0.052769 | 0.05373 | -58.9365 | -35.7941 | -61.9159 | 57.7993 | 57.6261 | 57.7637 | -65.3585 | -61.9581 | -34.3949 | -62.8442 | 57.6408 | 57.8506 | 57.7577 | -65.4947 | -0.17297 | 0.011248 | 6.249 | 3.2696 | 3.4426 | -0.16196 | -0.024407 | -0.30917 | -0.14731 | 3.2275 | 2.3413 | 2.6505 | 0.062528 | -0.030422 | 122.9849 | 122.8117 | 122.9492 | 29.3914 | -123.1466 | 122.8263 | 123.0362 | 122.9432 | 30.7906 | -123.2828
452.9375 | 123.2574 | -65.1627 | 57.8705 | 0.033173 | -0.043699 | 0.00069161 | 0.052202 | -0.0076669 | 0.05214 | 0.07176 | -0.0077392 | -0.0027965 | 0.057941 | 0.051701 | 0.054798 | -58.5703 | -35.4416 | -61.6962 | 57.8634 | 57.6765 | 57.8232 | -65.3036 | -61.7657 | -34.514 | -62.6794 | 57.682 | 57.901 | 57.8172 | -65.4489 | -0.14091 | -0.007052 | 6.5924 | 3.4665 | 3.6074 | -0.19399 | -0.047283 | -0.28627 | -0.18851 | 3.3969 | 2.4833 | 2.7696 | 0.030495 | -0.053297 | 123.0261 | 122.8392 | 122.9859 | 29.7211 | -123.1741 | 122.8446 | 123.0636 | 122.9798 | 30.6487 | -123.3194
453.9375 | 123.1842 | -65.1993 | 57.93 | 0.078959 | -0.043699 | -0.00037739 | 0.054339 | -0.0076669 | 0.053208 | 0.07176 | -0.0066712 | -0.0017285 | 0.055804 | 0.053837 | 0.054798 | -58.1903 | -35.0615 | -61.5313 | 57.8634 | 57.6811 | 57.8232 | -65.299 | -61.6421 | -34.4636 | -62.5466 | 57.6957 | 57.901 | 57.8126 | -65.4352 | -0.099715 | -0.066562 | 7.009 | 3.6679 | 3.7677 | -0.24892 | -0.10679 | -0.23591 | -0.23428 | 3.5572 | 2.6527 | 2.8886 | -0.029015 | -0.11739 | 123.0627 | 122.8804 | 123.0225 | 30.1377 | -123.229 | 122.895 | 123.1003 | 123.0119 | 30.7357 | -123.3652
454.9531 | 123.2071 | -65.1443 | 57.9208 | 0.033173 | -0.043699 | 0.0017596 | 0.055407 | -0.0076669 | 0.053208 | 0.07176 | -0.0066712 | -0.0017285 | 0.056873 | 0.053837 | 0.054798 | -57.9064 | -34.915 | -61.3207 | 57.8863 | 57.704 | 57.8598 | -65.2807 | -61.5231 | -34.7429 | -62.4092 | 57.714 | 57.933 | 57.8355 | -65.4215 | -0.13633 | -0.034514 | 7.2379 | 3.8236 | 3.9599 | -0.21687 | -0.061008 | -0.2771 | -0.20681 | 3.6213 | 2.7351 | 3.0122 | 0.012191 | -0.085337 | 123.0307 | 122.8483 | 123.0042 | 30.2293 | -123.2015 | 122.8584 | 123.0774 | 122.9798 | 30.4015 | -123.3423
455.9375 | 123.2712 | -65.0665 | 57.9575 | 0.063697 | -0.045835 | 0.00069161 | 0.053271 | -0.0076669 | 0.05214 | 0.10228 | -0.0066712 | -0.0038645 | 0.055804 | 0.053837 | 0.056935 | -57.6637 | -34.9013 | -61.1147 | 57.9458 | 57.7635 | 57.9102 | -65.2212 | -61.3353 | -34.894 | -62.2535 | 57.7781 | 57.9834 | 57.8859 | -65.3619 | -0.15463 | -0.011616 | 7.4028 | 3.9518 | 4.1064 | -0.19397 | -0.047264 | -0.2954 | -0.17933 | 3.7312 | 2.813 | 3.1084 | 0.025935 | -0.071593 | 123.0124 | 122.83 | 122.9767 | 30.1652 | -123.1786 | 122.8447 | 123.0499 | 122.9524 | 30.1725 | -123.3194
456.9375 | 123.3078 | -65.0803 | 57.93 | 0.063697 | -0.044767 | -0.00037739 | 0.052202 | -0.0076669 | 0.05214 | 0.056499 | -0.0088072 | -0.0027965 | 0.054736 | 0.055974 | 0.054798 | -57.4028 | -34.8601 | -61.0048 | 57.9138 | 57.7177 | 57.8781 | -65.2578 | -61.23 | -34.6879 | -62.1482 | 57.7552 | 57.9513 | 57.776 | -65.394 | -0.17752 | -0.0162 | 7.6775 | 4.0754 | 4.2529 | -0.21229 | -0.051849 | -0.31372 | -0.17476 | 3.8502 | 2.932 | 3.2457 | 0.02135 | -0.15401 | 122.9941 | 122.798 | 122.9584 | 30.2202 | -123.1878 | 122.8355 | 123.0316 | 122.8562 | 30.3923 | -123.324
457.9375 | 123.2574 | -65.0482 | 57.9666 | 0.063697 | -0.043699 | 0.00069161 | 0.052202 | -0.0076669 | 0.05214 | 0.056499 | -0.0066712 | -0.0027965 | 0.056873 | 0.053837 | 0.054798 | -57.0914 | -34.329 | -60.7439 | 57.955 | 57.7635 | 57.9148 | -65.212 | -61.0103 | -34.4361 | -61.988 | 57.7873 | 58.0017 | 57.8767 | -65.3482 | -0.16378 | -0.011615 | 7.9568 | 4.3043 | 4.4681 | -0.20312 | -0.051841 | -0.29997 | -0.17933 | 4.038 | 3.0602 | 3.3602 | 0.035093 | -0.089906 | 123.0032 | 122.8117 | 122.963 | 30.7193 | -123.1786 | 122.8355 | 123.0499 | 122.9249 | 30.6121 | -123.3148
458.9375 | 123.2254 | -65.0665 | 58.0261 | 0.078959 | -0.044767 | -0.00037739 | 0.052202 | -0.0076669 | 0.05214 | 0.087021 | -0.0088072 | -0.0038645 | 0.059009 | 0.055974 | 0.054798 | -56.8167 | -34.3564 | -60.5653 | 57.9458 | 57.7543 | 57.9194 | -65.2257 | -60.85 | -33.3281 | -61.8506 | 57.7873 | 57.9788 | 57.8584 | -65.3573 | -0.1592 | -0.080281 | 8.2498 | 4.5012 | 4.6604 | -0.27179 | -0.10677 | -0.29082 | -0.23884 | 4.2165 | 3.2159 | 3.5067 | -0.047309 | -0.16773 | 123.0124 | 122.8209 | 122.9859 | 30.7101 | -123.2519 | 122.8538 | 123.0453 | 122.9249 | 31.7385 | -123.3835
459.9531 | 123.1842 | -65.0757 | 58.017 | 0.063697 | -0.044767 | 0.00069161 | 0.054339 | -0.0044619 | 0.053208 | 0.087021 | -0.0077392 | -0.0017285 | 0.055804 | 0.054906 | 0.054798 | -56.4688 | -33.6101 | -60.2815 | 57.987 | 57.791 | 57.9468 | -65.1845 | -60.6669 | -33.1861 | -61.6995 | 57.8193 | 58.0246 | 57.8721 | -65.3116 | -0.10884 | -0.02992 | 8.6069 | 4.7942 | 4.903 | -0.226 | -0.070145 | -0.23588 | -0.19764 | 4.4088 | 3.3762 | 3.612 | 0.007632 | -0.14484 | 123.0627 | 122.8666 | 123.0225 | 31.4656 | -123.2015 | 122.895 | 123.1003 | 122.9478 | 31.8896 | -123.3285
460.9375 | 123.2849 | -64.4577 | 58.5617 | 0.063697 | -0.046904 | 0.0038966 | 0.053271 | -0.0044619 | 0.053208 | 0.10228 | -0.0077392 | -0.0038645 | 0.056873 | 0.054906 | 0.056935 | -55.7775 | -32.0809 | -59.4528 | 58.4907 | 58.2992 | 58.455 | -64.6763 | -60.0167 | -32.9892 | -61.1089 | 58.3321 | 58.5328 | 58.3712 | -64.817 | -0.21856 | -0.071037 | 8.6803 | 5.0049 | 5.2235 | -0.26248 | -0.10666 | -0.35935 | -0.22958 | 4.441 | 3.3488 | 3.7082 | -0.028882 | -0.19051 | 122.9484 | 122.7569 | 122.9128 | 32.3768 | -123.238 | 122.7898 | 122.9905 | 122.8289 | 31.4685 | -123.3788
461.9375 | 123.2574 | -64.2746 | 58.7631 | 0.063697 | -0.046904 | -0.00037739 | 0.055407 | -0.0055299 | 0.053208 | 0.07176 | -0.0077392 | -0.0027965 | 0.054736 | 0.055974 | 0.054798 | -55.2189 | -31.2521 | -58.734 | 58.7654 | 58.5694 | 58.7389 | -64.3878 | -59.6 | -32.4856 | -60.738 | 58.6023 | 58.8121 | 58.6368 | -64.5286 | -0.11319 | 0.002251 | 9.0557 | 5.5406 | 5.6538 | -0.19374 | -0.024202 | -0.25399 | -0.16087 | 4.6746 | 3.5366 | 3.7906 | 0.048997 | -0.12637 | 123.04 | 122.844 | 123.0135 | 33.0225 | -123.1509 | 122.8769 | 123.0867 | 122.9114 | 31.789 | -123.2917
462.9375 | 123.2254 | -64.1556 | 58.9188 | 0.063697 | -0.044767 | 0.00069161 | 0.055407 | -0.0065979 | 0.054276 | 0.07176 | -0.0066712 | -0.0017285 | 0.056873 | 0.055974 | 0.054798 | -54.9442 | -30.7622 | -58.2762 | 58.8524 | 58.661 | 58.8168 | -64.3054 | -59.3711 | -32.4673 | -60.5503 | 58.6847 | 58.8945 | 58.7192 | -64.4507 | -0.14979 | -0.066399 | 9.2114 | 5.8794 | 6.0292 | -0.2578 | -0.102 | -0.29516 | -0.23409 | 4.7845 | 3.6053 | 3.9005 | -0.024227 | -0.19959 | 123.0079 | 122.8165 | 122.9723 | 33.3934 | -123.2241 | 122.8402 | 123.0501 | 122.8748 | 31.6883 | -123.3695
463.9375 | 123.1888 | -64.1052 | 59.0195 | 0.048435 | -0.045835 | 0.0017596 | 0.054339 | -0.0055299 | 0.054276 | 0.087021 | -0.0066712 | -0.0027965 | 0.056873 | 0.055974 | 0.055867 | -54.6237 | -30.7073 | -57.855 | 58.9348 | 58.7342 | 58.8946 | -64.2367 | -59.1101 | -31.9636 | -60.3259 | 58.7625 | 58.9678 | 58.8474 | -64.3821 | -0.13146 | -0.084696 | 9.4815 | 6.2502 | 6.3817 | -0.28525 | -0.12488 | -0.27683 | -0.25697 | 4.9951 | 3.7793 | 4.0562 | -0.051677 | -0.1721 | 123.04 | 122.8394 | 122.9998 | 33.3979 | -123.2562 | 122.8677 | 123.073 | 122.9526 | 32.1416 | -123.4015
464.9531 | 123.317 | -63.9816 | 59.0424 | 0.048435 | -0.043699 | 0.0028286 | 0.055407 | -0.0033929 | 0.055345 | 0.07176 | -0.0088072 | -0.0017285 | 0.056873 | 0.055974 | 0.055867 | -54.3719 | -30.6844 | -57.4063 | 59.0447 | 58.8487 | 59.0091 | -64.1268 | -58.7209 | -30.9242 | -60.042 | 58.877 | 59.0868 | 58.9389 | -64.2493 | -0.14516 | 0.002297 | 9.6097 | 6.5753 | 6.7205 | -0.19366 | -0.033299 | -0.26765 | -0.16539 | 5.2607 | 3.9396 | 4.2072 | 0.044478 | -0.10341 | 123.0263 | 122.8303 | 122.9907 | 33.2972 | -123.1691 | 122.8586 | 123.0685 | 122.9206 | 33.0574 | -123.2916
465.9375 | 123.262 | -63.8489 | 59.1293 | 0.048435 | -0.047972 | 0.00069161 | 0.055407 | -0.0055299 | 0.057481 | 0.10228 | -0.0066712 | 0.00040853 | 0.056873 | 0.055974 | 0.058003 | -54.0148 | -30.0846 | -56.9576 | 59.1042 | 58.9174 | 59.0732 | -64.0535 | -58.3958 | -30.5992 | -59.8223 | 58.9502 | 59.1555 | 59.0397 | -64.1943 | -0.20465 | -0.025159 | 9.8341 | 6.8912 | 7.0959 | -0.21195 | -0.056174 | -0.34545 | -0.17911 | 5.4531 | 4.0266 | 4.3721 | 0.026182 | -0.08966 | 122.9531 | 122.7663 | 122.922 | 33.7643 | -123.1829 | 122.7991 | 123.0044 | 122.8886 | 33.2497 | -123.3237
466.9375 | 123.2162 | -63.8397 | 59.2072 | 0.063697 | -0.044767 | 0.00069161 | 0.055407 | -0.0076669 | 0.054276 | 0.07176 | -0.0066712 | -0.00065947 | 0.055804 | 0.058111 | 0.055867 | -54.0239 | -29.8831 | -56.4907 | 59.1912 | 58.9952 | 59.1464 | -63.9803 | -58.144 | -30.7548 | -59.6345 | 59.0189 | 59.2196 | 59.1175 | -64.1211 | -0.14054 | -0.015989 | 9.8158 | 7.3491 | 7.4896 | -0.21193 | -0.060736 | -0.28134 | -0.18825 | 5.6957 | 4.2052 | 4.4865 | 0.012463 | -0.089644 | 123.0309 | 122.8349 | 122.9861 | 33.9566 | -123.1874 | 122.8586 | 123.0593 | 122.9572 | 33.0849 | -123.3282
467.9375 | 123.2895 | -63.9038 | 59.1202 | 0.033173 | -0.045835 | 0.0017596 | 0.056476 | -0.0044619 | 0.053208 | 0.07176 | -0.0066712 | -0.0027965 | 0.056873 | 0.057043 | 0.056935 | -54.4085 | -30.1716 | -56.2709 | 59.0813 | 58.9036 | 59.0503 | -64.081 | -57.9013 | -30.1962 | -59.5567 | 58.9182 | 59.1235 | 59.0214 | -64.2126 | -0.17719 | -0.038896 | 9.4953 | 7.6329 | 7.8101 | -0.21653 | -0.069912 | -0.30883 | -0.20201 | 6.0025 | 4.3471 | 4.656 | 0.003287 | -0.098819 | 122.9851 | 122.8075 | 122.9541 | 33.7322 | -123.2012 | 122.822 | 123.0273 | 122.9252 | 33.7076 | -123.3328
468.9375 | 123.2849 | -63.7573 | 59.2667 | 0.033173 | -0.047972 | 0.0017596 | 0.055407 | -0.0044619 | 0.053208 | 0.07176 | -0.0077392 | -0.0017285 | 0.056873 | 0.058111 | 0.058003 | -54.5276 | -30.2952 | -55.868 | 59.2232 | 59.0456 | 59.1922 | -63.9436 | -57.3931 | -29.308 | -59.2224 | 59.0601 | 59.2517 | 59.1587 | -64.0844 | -0.18631 | -0.043451 | 9.2298 | 7.8893 | 8.0756 | -0.22107 | -0.07446 | -0.32711 | -0.20656 | 6.3642 | 4.5349 | 4.862 | -0.014997 | -0.10795 | 122.9805 | 122.8029 | 122.9495 | 33.4621 | -123.2103 | 122.8174 | 123.009 | 122.916 | 34.4494 | -123.3511
469.9531 | 123.2346 | -63.414 | 59.6558 | 0.063697 | -0.045835 | 0.0017596 | 0.053271 | -0.0044619 | 0.056413 | 0.087021 | -0.0088072 | -0.00065947 | 0.056873 | 0.057043 | 0.056935 | -54.2849 | -30.4371 | -55.3827 | 59.5254 | 59.3386 | 59.4898 | -63.6506 | -56.7612 | -29.4133 | -58.76 | 59.3623 | 59.5584 | 59.4655 | -63.7685 | -0.23658 | -0.13038 | 9.1291 | 8.0313 | 8.2679 | -0.31712 | -0.16595 | -0.3545 | -0.29348 | 6.6528 | 4.654 | 5.0085 | -0.09733 | -0.19028 | 122.9394 | 122.7526 | 122.9038 | 32.9769 | -123.3063 | 122.7763 | 122.9724 | 122.8795 | 34.0007 | -123.4243
470.9375 | 123.1979 | -63.2584 | 59.848 | 0.048435 | -0.046904 | 0.0017596 | 0.057544 | -0.0055299 | 0.054276 | 0.07176 | -0.0088072 | -0.0027965 | 0.057941 | 0.060248 | 0.058003 | -53.8408 | -31.5223 | -55.0851 | 59.8047 | 59.6225 | 59.7645 | -63.3667 | -56.1797 | -29.4316 | -58.325 | 59.6416 | 59.8423 | 59.7494 | -63.4983 | -0.10833 | -0.043354 | 9.4176 | 8.1732 | 8.2816 | -0.22549 | -0.083494 | -0.23999 | -0.20645 | 7.0786 | 4.9333 | 5.1733 | -0.005716 | -0.098666 | 123.063 | 122.8809 | 123.0229 | 31.7361 | -123.2147 | 122.8999 | 123.1007 | 123.0077 | 33.8268 | -123.3464
471.9375 | 123.2208 | -63.4323 | 59.61 | 0.048435 | -0.044767 | 0.0017596 | 0.057544 | -0.0055299 | 0.056413 | 0.056499 | -0.0077392 | 0.0025445 | 0.056873 | 0.058111 | 0.055867 | -53.9232 | -30.7485 | -55.1172 | 59.6627 | 59.4806 | 59.618 | -63.5041 | -56.0149 | -29.6559 | -58.3296 | 59.4905 | 59.7004 | 59.6074 | -63.6403 | -0.071745 | 0.052753 | 9.5091 | 8.3151 | 8.3869 | -0.1294 | 0.008028 | -0.20798 | -0.1195 | 7.4174 | 5.1027 | 5.3107 | 0.090384 | -0.002565 | 123.0951 | 122.9129 | 123.0503 | 32.6838 | -123.114 | 122.9228 | 123.1327 | 123.0397 | 33.7764 | -123.2503
472.9375 | 123.2346 | -63.6108 | 59.4223 | 0.048435 | -0.046904 | 0.0017596 | 0.055407 | -0.0033929 | 0.054276 | 0.056499 | -0.0056032 | 0.00040853 | 0.056873 | 0.057043 | 0.056935 | -53.9827 | -30.9042 | -55.0073 | 59.4796 | 59.302 | 59.4578 | -63.6872 | -55.9325 | -30.123 | -58.3708 | 59.3165 | 59.5126 | 59.4197 | -63.8143 | -0.076374 | 0.0573 | 9.6281 | 8.6035 | 8.6799 | -0.12029 | 0.03546 | -0.20345 | -0.1058 | 7.6784 | 5.24 | 5.4435 | 0.090344 | -0.002605 | 123.0904 | 122.9129 | 123.0686 | 32.7067 | -123.1095 | 122.9273 | 123.1235 | 123.0305 | 33.4879 | -123.2366
473.9375 | 123.2666 | -63.4918 | 59.5413 | 0.048435 | -0.043699 | 0.0028286 | 0.055407 | -0.0023249 | 0.056413 | 0.07176 | -0.0056032 | -0.00065947 | 0.060077 | 0.057043 | 0.058003 | -54.1018 | -31.591 | -54.8928 | 59.5574 | 59.3799 | 59.5219 | -63.614 | -55.612 | -30.2832 | -58.1785 | 59.376 | 59.5859 | 59.4609 | -63.7456 | -0.12213 | 0.016114 | 9.3901 | 8.599 | 8.7211 | -0.16147 | -0.019459 | -0.25378 | -0.1653 | 7.8799 | 5.3133 | 5.5671 | 0.044583 | -0.080417 | 123.0493 | 122.8717 | 123.0137 | 31.9009 | -123.1553 | 122.8678 | 123.0777 | 122.9527 | 33.2086 | -123.2869
474.9531 | 123.2483 | -62.9517 | 60.1318 | 0.048435 | -0.044767 | 0.0038966 | 0.056476 | -0.0023249 | 0.055345 | 0.087021 | -0.0088072 | 0.00040853 | 0.057941 | 0.058111 | 0.058003 | -53.7034 | -30.1578 | -53.9863 | 60.116 | 59.9339 | 60.0713 | -63.0507 | -54.8656 | -29.9444 | -57.4505 | 59.9438 | 60.1491 | 60.0653 | -63.187 | -0.099083 | -0.015838 | 9.2482 | 8.9653 | 9.0644 | -0.19793 | -0.060542 | -0.23533 | -0.18808 | 8.086 | 5.5012 | 5.7365 | 0.017236 | -0.066556 | 123.0677 | 122.8856 | 123.023 | 32.7938 | -123.1826 | 122.8954 | 123.1007 | 123.0169 | 33.0073 | -123.3188
475.9375 | 123.2437 | -62.5031 | 60.5896 | 0.063697 | -0.045835 | 0.00069161 | 0.056476 | -0.0044619 | 0.055345 | 0.041238 | -0.0088072 | 0.00040853 | 0.057941 | 0.058111 | 0.056935 | -53.6577 | -28.9674 | -53.4553 | 60.5372 | 60.3643 | 60.5063 | -62.6249 | -54.2338 | -29.9352 | -56.8827 | 60.3696 | 60.5749 | 60.4453 | -62.752 | -0.12185 | -0.05239 | 8.8454 | 9.0478 | 9.1696 | -0.22528 | -0.083338 | -0.24895 | -0.22005 | 8.2693 | 5.6203 | 5.8693 | -0.014718 | -0.1443 | 123.0403 | 122.8674 | 123.0093 | 33.5356 | -123.2145 | 122.8726 | 123.0779 | 122.9484 | 32.5678 | -123.3416
476.9375 | 123.1613 | -62.2513 | 60.8643 | 0.033173 | -0.043699 | 0.0017596 | 0.056476 | -0.0012569 | 0.056413 | 0.056499 | -0.0077392 | 0.00040853 | 0.059009 | 0.059179 | 0.056935 | -53.2639 | -28.3447 | -53.0707 | 60.8806 | 60.7032 | 60.8359 | -62.2815 | -53.5744 | -29.6239 | -56.3974 | 60.7084 | 60.9 | 60.8345 | -62.4223 | -0.030202 | 0.016331 | 8.9874 | 9.1806 | 9.2108 | -0.1611 | -0.028337 | -0.17104 | -0.1559 | 8.6768 | 5.8539 | 6.0249 | 0.035705 | -0.029773 | 123.1319 | 122.9544 | 123.0872 | 33.9066 | -123.1457 | 122.9596 | 123.1512 | 123.0858 | 32.6274 | -123.2866
477.9375 | 123.1979 | -61.8164 | 61.2534 | 0.033173 | -0.047972 | 0.0017596 | 0.056476 | -0.0033929 | 0.054276 | 0.056499 | -0.0066712 | 0.0014765 | 0.059009 | 0.060248 | 0.056935 | -52.5268 | -28.4638 | -52.6174 | 61.2285 | 61.0603 | 61.1885 | -61.9426 | -52.9563 | -28.6166 | -55.8937 | 61.0563 | 61.2663 | 61.1458 | -62.0789 | -0.12624 | -0.024811 | 9.2896 | 9.199 | 9.3252 | -0.19304 | -0.064884 | -0.26251 | -0.19703 | 8.8601 | 5.9227 | 6.1852 | 0.012894 | -0.10753 | 123.045 | 122.8767 | 123.0049 | 33.3526 | -123.196 | 122.8727 | 123.0827 | 122.9622 | 33.1998 | -123.3323
478.9375 | 123.1842 | -61.441 | 61.647 | 0.048435 | -0.046904 | 0.0017596 | 0.056476 | -0.0044619 | 0.055345 | 0.07176 | -0.0077392 | 0.00040853 | 0.056873 | 0.060248 | 0.058003 | -52.362 | -28.4088 | -52.036 | 61.6406 | 61.4816 | 61.6005 | -61.5168 | -52.068 | -27.8474 | -55.2939 | 61.4776 | 61.6829 | 61.5945 | -61.6485 | -0.075764 | -0.006433 | 9.0791 | 9.4051 | 9.4808 | -0.16545 | -0.046486 | -0.20747 | -0.16948 | 9.373 | 6.1471 | 6.3546 | 0.03587 | -0.052501 | 123.0816 | 122.9226 | 123.0416 | 33.0322 | -123.1638 | 122.9186 | 123.1239 | 123.0356 | 33.5937 | -123.2955
479.9531 | 123.2437 | -62.0728 | 61.0153 | 0.063697 | -0.045835 | 0.0028286 | 0.056476 | -0.0044619 | 0.055345 | 0.041238 | -0.0077392 | 0.0036135 | 0.057941 | 0.059179 | 0.058003 | -53.0854 | -29.7137 | -52.8143 | 60.8394 | 60.6665 | 60.7993 | -62.3181 | -52.59 | -28.8226 | -56.0082 | 60.6672 | 60.8725 | 60.8024 | -62.4498 | -0.24536 | -0.17594 | 8.9874 | 9.2585 | 9.5038 | -0.34879 | -0.21603 | -0.37704 | -0.34816 | 9.4827 | 6.0646 | 6.4416 | -0.14283 | -0.21288 | 122.9121 | 122.7393 | 122.872 | 32.359 | -123.3334 | 122.7399 | 122.9452 | 122.8752 | 33.2501 | -123.4651
480.9375 | 123.1659 | -62.8555 | 60.2005 | 0.033173 | -0.044767 | 0.00069161 | 0.056476 | -0.0023249 | 0.055345 | 0.07176 | -0.0088072 | 0.0014765 | 0.057941 | 0.060248 | 0.058003 | -53.2639 | -30.4783 | -53.1302 | 60.235 | 60.0575 | 60.1903 | -62.9363 | -52.8281 | -29.4774 | -56.5805 | 60.0491 | 60.2681 | 60.1797 | -63.0771 | -0.08074 | 0.034536 | 9.5916 | 9.7253 | 9.8061 | -0.14297 | -0.010162 | -0.22157 | -0.15144 | 10.0274 | 6.275 | 6.4966 | 0.067616 | -0.020755 | 123.0906 | 122.9131 | 123.0459 | 32.3772 | -123.1368 | 122.9046 | 123.1236 | 123.0353 | 33.3782 | -123.2776
481.9531 | 123.2346 | -91.0767 | 31.9611 | 0.063697 | -0.044767 | 0.012444 | 0.057544 | -0.0012569 | 0.05855 | 0.041238 | -0.0066712 | 0.0036135 | 0.059009 | 0.060248 | 0.06014 | -75.1166 | -50.7295 | -74.8038 | 37.5491 | 37.2179 | 37.6499 | -85.4783 | -74.8975 | -47.4305 | -78.9201 | 37.1795 | 37.43 | 37.1997 | -85.6003 | 5.5983 | 5.5881 | 15.9601 | 16.2729 | 10.6745 | 5.2568 | 5.6888 | 5.4764 | 5.2184 | 16.1792 | 12.1566 | 6.6802 | 5.469 | 5.2387 | 128.6258 | 128.2945 | 128.7265 | 40.3472 | -117.4394 | 128.2561 | 128.5067 | 128.2764 | 43.6462 | -117.5614
482.9375 | 123.1888 | -93.3197 | 29.7501 | 0.033173 | -0.044767 | 0.013512 | 0.057544 | -0.0023249 | 0.056413 | 0.041238 | -0.0066712 | 0.0025445 | 0.060077 | 0.060248 | 0.06014 | -82.1078 | -59.7906 | -82.4999 | 29.862 | 29.7863 | 29.8891 | -93.464 | -81.6969 | -53.5248 | -86.017 | 29.7394 | 29.8341 | 29.9014 | -93.5171 | -0.14426 | 0.11195 | 11.2119 | 10.8198 | 10.9641 | 0.036202 | 0.13909 | -0.19737 | -0.01064 | 11.6228 | 7.3027 | 7.5 | 0.084084 | 0.15139 | 123.1817 | 123.106 | 123.2088 | 33.5291 | -123.214 | 123.0591 | 123.1538 | 123.2211 | 39.7949 | -123.2671
483.9375 | 123.3444 | -63.8992 | 59.166 | 0.033173 | -0.044767 | 0.0028286 | 0.056476 | -0.0033929 | 0.056413 | 0.041238 | -0.0088072 | 0.00040853 | 0.056873 | 0.061316 | 0.06014 | -54.6329 | -33.0744 | -53.9955 | 59.095 | 58.9265 | 59.0686 | -64.0581 | -52.6633 | -29.5873 | -57.1803 | 58.9273 | 59.1418 | 59.0626 | -64.1943 | -0.15888 | -0.070937 | 9.2664 | 9.9037 | 10.0626 | -0.23942 | -0.097375 | -0.2951 | -0.23863 | 11.236 | 6.7189 | 7.014 | -0.024176 | -0.10339 | 122.9942 | 122.8258 | 122.9678 | 30.8248 | -123.2241 | 122.8266 | 123.041 | 122.9618 | 34.312 | -123.3603
484.9375 | 123.2574 | -63.8214 | 59.2804 | 0.063697 | -0.046904 | 0.0017596 | 0.057544 | -0.0044619 | 0.057481 | 0.07176 | -0.0066712 | 0.0036135 | 0.056873 | 0.062384 | 0.06014 | -52.2017 | -33.2988 | -54.2153 | 59.1728 | 58.9952 | 59.1189 | -63.994 | -52.1321 | -29.1889 | -56.9148 | 58.996 | 59.2013 | 59.1129 | -64.1302 | -0.17259 | -0.10755 | 11.6197 | 9.6062 | 9.7788 | -0.28517 | -0.16145 | -0.30881 | -0.28439 | 11.6893 | 6.9066 | 7.2155 | -0.079095 | -0.16746 | 122.9943 | 122.8166 | 122.9404 | 30.5226 | -123.2744 | 122.8174 | 123.0227 | 122.9343 | 34.6325 | -123.4106
485.9375 | 123.2391 | -63.4232 | 59.6512 | 0.063697 | -0.047972 | 0.0038966 | 0.057544 | -0.0012569 | 0.059618 | 0.056499 | -0.0066712 | 0.0036135 | 0.056873 | 0.062384 | 0.06014 | -51.4463 | -33.1248 | -54.7692 | 59.5117 | 59.3478 | 59.4761 | -63.6506 | -51.9673 | -28.9508 | -56.4157 | 59.3531 | 59.5401 | 59.4792 | -63.7868 | -0.22742 | -0.13953 | 11.9769 | 8.6539 | 8.8814 | -0.30338 | -0.17511 | -0.36366 | -0.29806 | 11.4558 | 7.0075 | 7.3711 | -0.11107 | -0.17197 | 122.9348 | 122.771 | 122.8992 | 30.2984 | -123.3018 | 122.7763 | 122.9633 | 122.9024 | 34.4723 | -123.438
486.9531 | 123.2849 | -63.7985 | 59.2438 | 0.063697 | -0.043699 | 0.0038966 | 0.056476 | -0.0033929 | 0.05855 | 0.056499 | -0.0077392 | 0.0046815 | 0.060077 | 0.061316 | 0.06014 | -50.9839 | -33.9901 | -54.8837 | 59.1774 | 59.009 | 59.151 | -63.9757 | -53.0616 | -29.9856 | -56.6996 | 59.0143 | 59.2196 | 59.1312 | -64.1119 | -0.17716 | -0.066345 | 12.8146 | 8.9148 | 9.092 | -0.23481 | -0.092779 | -0.31339 | -0.22945 | 10.7369 | 7.099 | 7.4123 | -0.024158 | -0.11253 | 122.976 | 122.8075 | 122.9495 | 29.8084 | -123.2195 | 122.8128 | 123.0181 | 122.9298 | 33.8129 | -123.3557
487.9375 | 123.1796 | -68.6783 | 54.4052 | 0.063697 | -0.04904 | 0.059453 | 0.085323 | 0.079935 | 0.064959 | 0.07176 | -0.0088072 | 0.0025445 | 0.056873 | 0.062384 | 0.06014 | -52.481 | 6.5671 | 52.3809 | 54.5212 | 54.3568 | 54.5037 | -68.5958 | -57.6541 | -34.0698 | -61.2188 | 54.3351 | 54.5815 | 54.484 | -68.7594 | 0.082463 | 0.116 | 16.1973 | 121.0591 | 120.9767 | -0.04844 | 0.098502 | -0.081125 | -0.070115 | 11.0242 | 7.4595 | 7.5407 | 0.17628 | 0.078751 | 123.1995 | 123.0351 | 123.182 | 75.2454 | -123.001 | 123.0134 | 123.2598 | 123.1622 | 34.6085 | -123.1646
488.9531 | 123.1705 | -69.2963 | 53.801 | 0.063697 | -0.050109 | 0.10967 | 0.10455 | 0.08314 | 0.13013 | 0.07176 | -0.0066712 | 0.0025445 | 0.059009 | 0.059179 | 0.06014 | 53.5773 | 52.6737 | 53.5712 | 53.5597 | 53.3998 | 53.5239 | -69.5574 | -59.829 | -34.3537 | -62.2307 | 53.3873 | 53.62 | 53.5453 | -69.7026 | -0.26113 | -0.24122 | 122.8736 | 122.8675 | 123.1286 | -0.40119 | -0.27707 | -0.40638 | -0.41362 | 9.4673 | 7.0656 | 7.472 | -0.18098 | -0.25561 | 122.856 | 122.696 | 122.8202 | 121.9699 | -123.3584 | 122.6836 | 122.9163 | 122.8416 | 34.9426 | -123.5036
489.9375 | 123.143 | -68.2755 | 54.8172 | 0.048435 | -0.051177 | 0.11287 | 0.10135 | 0.081003 | 0.12906 | 0.056499 | -0.0077392 | -0.00065947 | 0.057941 | 0.061316 | 0.058003 | 54.5113 | 54.615 | 54.4686 | 54.4434 | 54.2972 | 54.4213 | -68.6553 | -59.5359 | -32.4215 | -61.434 | 54.2939 | 54.5082 | 54.4473 | -68.8052 | -0.3799 | -0.37382 | 122.7868 | 122.744 | 123.1239 | -0.51995 | -0.3959 | -0.52975 | -0.52331 | 8.7395 | 6.8415 | 7.3712 | -0.30897 | -0.36986 | 122.7188 | 122.5727 | 122.6968 | 122.8904 | -123.4725 | 122.5693 | 122.7837 | 122.7228 | 35.854 | -123.6224
490.9375 | 123.3078 | -67.8818 | 55.1147 | 0.063697 | -0.050109 | 0.11287 | 0.10028 | 0.08314 | 0.13013 | 0.07176 | -0.0056032 | 0.00040853 | 0.057941 | 0.060248 | 0.06014 | 55.0104 | 55.114 | 54.963 | 54.9241 | 54.7735 | 54.8883 | -68.1791 | -59.1925 | -31.0708 | -61.086 | 54.738 | 54.9844 | 54.9189 | -68.3336 | -0.29736 | -0.19064 | 122.8922 | 122.8448 | 123.1421 | -0.34129 | -0.22643 | -0.4518 | -0.37674 | 8.6893 | 6.7958 | 7.2476 | -0.13034 | -0.19581 | 122.8059 | 122.6552 | 122.7701 | 122.9958 | -123.2939 | 122.6198 | 122.8662 | 122.8007 | 36.811 | -123.4483
491.9375 | 123.2071 | -67.2958 | 55.751 | 0.033173 | -0.052245 | 0.11074 | 0.10028 | 0.082072 | 0.12799 | 0.07176 | -0.0077392 | -0.00065947 | 0.057941 | 0.063453 | 0.059071 | 55.7475 | 55.8558 | 55.7047 | 55.6566 | 55.5107 | 55.6346 | -67.4374 | -58.0249 | -30.0451 | -60.8708 | 55.4751 | 55.7216 | 55.6652 | -67.5964 | -0.14152 | -0.09439 | 123.0433 | 123.0005 | 123.142 | -0.24038 | -0.11641 | -0.30055 | -0.27589 | 9.2709 | 6.4251 | 6.7256 | -0.029475 | -0.085795 | 122.9525 | 122.8065 | 122.9305 | 123.1516 | -123.1884 | 122.771 | 123.0174 | 122.9611 | 37.2507 | -123.3474
492.9375 | 123.1934 | -72.464 | 50.6058 | 0.078959 | 0.0011733 | -0.0014454 | -0.009766 | -0.052536 | 0.028637 | 0.07176 | -0.0066712 | 0.0014765 | 0.057941 | 0.060248 | 0.06014 | 50.6151 | 50.7918 | 50.5679 | 50.506 | 50.364 | 50.4929 | 8.5178 | -62.4983 | -34.5872 | -66.0585 | 50.4388 | 50.5386 | 50.4777 | -72.7842 | 80.9818 | -0.099812 | 123.0791 | 123.0318 | 42.05 | -0.24182 | -0.11292 | -0.3202 | -0.16698 | 9.9656 | 6.4055 | 6.7257 | -0.067189 | -0.12809 | 122.97 | 122.8279 | 122.9568 | 123.2558 | -42.0879 | 122.9028 | 123.0026 | 122.9417 | 37.8768 | -123.39
493.9375 | 123.2391 | -72.9767 | 50.0931 | 0.063697 | -0.0009637 | -0.0014454 | -0.007629 | -0.052536 | 0.030773 | 0.10228 | -0.0077392 | 0.00040853 | 0.057941 | 0.061316 | 0.06014 | 50.0566 | 50.16 | 50.0093 | 49.9474 | 49.8053 | 49.9388 | 8.5728 | -62.361 | -37.0185 | -67.0246 | 49.8802 | 49.9983 | 49.9054 | -73.3474 | 81.5495 | -0.14568 | 123.0332 | 122.986 | 41.4365 | -0.28776 | -0.15423 | -0.3707 | -0.21286 | 10.6157 | 5.9521 | 6.3228 | -0.094769 | -0.18772 | 122.9241 | 122.782 | 122.9155 | 123.1367 | -41.5203 | 122.8569 | 122.975 | 122.882 | 35.9582 | -123.4405
494.9375 | 123.1842 | -77.8473 | 45.2591 | 0.063697 | 0.0033103 | -0.0025134 | -0.007629 | -0.052536 | 0.030773 | 0.087021 | -0.0077392 | 0.066643 | 0.055804 | 0.062384 | 0.1221 | 45.5514 | 45.6547 | 45.5043 | 45.4423 | 45.2905 | 45.4381 | 8.5865 | 41.5071 | -34.7292 | -71.008 | 45.3567 | 45.4701 | 45.3863 | -77.8667 | 86.4338 | 0.18317 | 123.3987 | 123.3516 | 36.9177 | 0.031408 | 0.17899 | -0.019387 | 0.097574 | 119.3543 | 6.8393 | 6.8586 | 0.21098 | 0.12719 | 123.2896 | 123.1378 | 123.2854 | 123.5019 | -36.6726 | 123.204 | 123.3174 | 123.2336 | 43.1181 | -123.1258
495.9531 | 123.2803 | -79.8706 | 43.1351 | 0.048435 | 0.0022413 | -0.0014454 | -0.008698 | -0.053604 | 0.030773 | 0.07176 | -0.0066712 | 0.06878 | 0.055804 | 0.063453 | 0.12637 | 43.2943 | 43.3791 | 43.2426 | 43.1805 | 43.0468 | 43.1808 | 8.582 | 43.1325 | -37.0368 | -73.1371 | 43.1086 | 43.2082 | 43.1336 | -80.1149 | 88.4526 | 0.04547 | 123.1649 | 123.1132 | 34.6607 | -0.088242 | 0.045759 | -0.24427 | -0.026444 | 123.0031 | 6.7335 | 6.9777 | 0.073172 | -0.001463 | 123.0511 | 122.9174 | 123.0514 | 123.2497 | -34.5531 | 122.9792 | 123.0788 | 123.0042 | 42.8338 | -123.2499
496.9375 | 123.1842 | -78.7033 | 44.4397 | 0.078959 | 0.0011733 | -0.0025134 | -0.007629 | -0.052536 | 0.028637 | 0.07176 | -0.0077392 | 0.069848 | 0.056873 | 0.061316 | 0.12424 | 43.2119 | 43.2875 | 43.1556 | 43.089 | 42.9598 | 43.0938 | 8.5865 | 43.105 | -37.5359 | -73.0822 | 43.0262 | 43.1304 | 43.0695 | -80.1927 | 87.2898 | -1.3507 | 121.9152 | 121.8589 | 34.5691 | -1.4799 | -1.3459 | -1.4894 | -1.4135 | 121.8083 | 5.6211 | 7.1105 | -1.3093 | -1.3702 | 121.7923 | 121.6631 | 121.7971 | 121.9908 | -35.8532 | 121.7295 | 121.8337 | 121.7728 | 41.1674 | -124.6324
497.9531 | 123.2162 | -75.3708 | 47.699 | 0.048435 | -0.0009637 | -0.0025134 | -0.009766 | -0.053604 | 0.029705 | 0.041238 | -0.0098752 | 0.13181 | -0.029655 | 0.066658 | 0.0088629 | 47.7445 | 47.8432 | 47.6973 | 47.6307 | 47.493 | 47.6312 | 8.5911 | 0.033099 | 0.023253 | -0.1525 | 0.098244 | 0.20143 | 0.21379 | -0.29693 | 83.9619 | -0.068241 | 123.1153 | 123.0681 | 39.1062 | -0.20601 | -0.067744 | 75.0739 | -47.6007 | 75.4039 | 75.2183 | 0.14443 | -47.4975 | -47.4852 | 123.0015 | 122.8638 | 123.002 | 123.214 | -39.1079 | 75.469 | 75.5722 | 75.5846 | 75.394 | -47.9959
498.9375 | 123.2391 | -102.4475 | 20.5765 | 0.048435 | 0.0001043 | 0.00069161 | -0.006561 | -0.050399 | 0.029705 | 0.07176 | -0.0088072 | 0.13181 | -0.02645 | 0.065589 | 0.0067259 | 21.1532 | 21.2782 | 21.1845 | 21.1677 | 21.0955 | 21.231 | 8.6873 | -0.003531 | 0.009516 | -0.092981 | 0.043302 | 0.15564 | 0.18174 | -0.25115 | 111.1348 | 0.59118 | 123.6007 | 123.632 | 12.4972 | 0.51899 | 0.65453 | 102.1964 | -20.5332 | 102.444 | 102.3545 | 0.15817 | -20.4208 | -20.3947 | 123.6152 | 123.543 | 123.6785 | 123.7257 | -11.8892 | 102.4908 | 102.6032 | 102.6292 | 102.457 | -20.8276
499.9375 | 123.1842 | -102.5894 | 20.5124 | 0.063697 | -0.0009637 | -0.0014454 | -0.005492 | -0.051468 | 0.030773 | 0.07176 | -0.0098752 | 0.13074 | -0.027518 | 0.064521 | 0.0067259 | 23.5248 | 23.6362 | 23.5468 | 23.3882 | 23.5589 | 23.5157 | 8.6644 | -0.003531 | 0.014095 | -0.088402 | 0.043302 | 0.14191 | 0.168 | -0.25115 | 111.2538 | 2.8758 | 126.1142 | 126.1363 | 14.8825 | 3.0465 | 3.0033 | 102.3383 | -20.4691 | 102.5859 | 102.501 | 0.16274 | -20.3705 | -20.3444 | 125.9776 | 126.1483 | 126.1051 | 126.2256 | -11.848 | 102.6327 | 102.7313 | 102.7574 | 102.6035 | -20.7635
500.9375 | 123.2391 | -75.7736 | 47.3602 | 0.078959 | 0.0011733 | -0.0025134 | -0.006561 | -0.052536 | 0.030773 | 0.056499 | -0.012012 | 0.13181 | -0.02645 | 0.063453 | 0.0067259 | 43.8254 | 43.8232 | 43.7828 | 43.6796 | 43.7657 | 43.6158 | 8.5911 | -0.003531 | 0.009516 | -0.074666 | 0.038723 | 0.15107 | 0.17716 | -0.23283 | 84.3647 | -3.6806 | 119.599 | 119.5565 | 35.1917 | -3.5945 | -3.7444 | 75.5408 | -47.3215 | 75.7701 | 75.699 | 0.15817 | -47.2092 | -47.1831 | 119.4532 | 119.5393 | 119.3894 | 119.5968 | -38.7691 | 75.8123 | 75.9247 | 75.9508 | 75.7831 | -47.5931
501.9375 | 123.2346 | -75.6775 | 47.438 | 0.048435 | 0.0011733 | -0.0014454 | -0.008698 | -0.052536 | 0.030773 | 0.07176 | -0.010944 | 0.13074 | -0.027518 | 0.064521 | 0.0099309 | 47.4331 | 47.5365 | 47.3905 | 47.3194 | 47.1862 | 47.3107 | 8.5957 | 0.005626 | 0.018674 | -0.06093 | 0.04788 | 0.15107 | 0.18632 | -0.21452 | 84.2732 | -0.11865 | 123.1106 | 123.068 | 38.7948 | -0.25187 | -0.12732 | 75.463 | -47.3902 | 75.6831 | 75.6166 | 0.15359 | -47.287 | -47.2517 | 122.9969 | 122.8637 | 122.9882 | 123.2139 | -38.8424 | 75.7254 | 75.8286 | 75.8638 | 75.6962 | -47.6526
502.9531 | 123.3032 | -76.0117 | 47.0032 | 0.078959 | -0.0020317 | -0.0014454 | -0.009766 | -0.053604 | 0.030773 | 0.087021 | -0.0098752 | 0.13181 | -0.02645 | 0.066658 | 0.0077949 | 47.1539 | 47.2572 | 47.1067 | 47.0447 | 46.9069 | 47.0406 | 8.5911 | 0.001048 | 0.014095 | -0.056351 | 0.052459 | 0.15564 | -0.097557 | -0.2191 | 84.6028 | 0.041527 | 123.1655 | 123.1183 | 38.5156 | -0.096312 | 0.037418 | 75.7926 | -46.9507 | 76.0127 | 75.9553 | 0.16274 | -46.8475 | -47.1007 | 123.0564 | 122.9185 | 123.0522 | 123.2688 | -38.4121 | 76.0641 | 76.1673 | 75.9141 | 76.0258 | -47.2223
503.9375 | 123.2391 | -76.3092 | 46.8201 | 0.033173 | -0.0009637 | -0.0025134 | -0.008698 | -0.053604 | 0.029705 | 0.07176 | -0.010944 | 0.13074 | -0.02645 | 0.064521 | 0.0067259 | 46.9204 | 47.0145 | 46.8732 | 46.7975 | 46.6642 | 46.7979 | 8.5865 | 0.005626 | 0.023253 | -0.047194 | 0.052459 | 0.16022 | -0.10671 | -0.20994 | 84.8957 | -0.0226 | 123.2296 | 123.1824 | 38.2867 | -0.15589 | -0.022142 | 76.0993 | -46.7676 | 76.3148 | 76.262 | 0.16274 | -46.6598 | -46.9268 | 123.1067 | 122.9734 | 123.1071 | 123.3237 | -38.2335 | 76.3617 | 76.4694 | 76.2025 | 76.3325 | -47.03
504.9531 | 123.2849 | -83.3496 | 39.679 | 0.048435 | 0.0011733 | -0.0014454 | -0.008698 | -0.052536 | 0.036115 | 0.056499 | -0.0098752 | 0.13074 | -0.025382 | 0.064521 | 0.0077949 | 39.801 | 39.9543 | 39.7723 | 39.6827 | 39.5531 | 39.6965 | 8.5957 | 0.010205 | 0.018674 | -0.047194 | 0.04788 | 0.16022 | -0.083821 | -0.20994 | 91.9453 | 0.003698 | 123.1506 | 123.1219 | 31.1766 | -0.12585 | 0.017558 | 83.1397 | -39.6311 | 83.3598 | 83.3024 | 0.16274 | -39.5187 | -39.7628 | 123.0323 | 122.9027 | 123.0461 | 123.3039 | -31.0833 | 83.3975 | 83.5098 | 83.2658 | 83.3683 | -39.8889
505.9375 | 123.3856 | -84.6359 | 38.4338 | 0.094221 | 0.0043783 | -0.0014454 | -0.006561 | -0.053604 | 0.033978 | 0.07176 | -0.0098752 | 0.13074 | -0.02645 | 0.065589 | 0.0067259 | 38.5282 | 38.686 | 38.4858 | 38.4144 | 38.2939 | 38.4282 | 8.5957 | 0.005626 | 0.018674 | -0.038036 | 0.061616 | 0.16938 | -0.0243 | -0.20536 | 93.2316 | -0.019398 | 123.1641 | 123.1217 | 29.8901 | -0.13993 | -0.005598 | 84.4306 | -38.3722 | 84.6416 | 84.5979 | 0.16732 | -38.2645 | -38.4581 | 123.0504 | 122.9298 | 123.0642 | 123.3219 | -29.8381 | 84.6975 | 84.8053 | 84.6116 | 84.6546 | -38.6392
506.9531 | 123.2162 | -84.4162 | 38.6856 | 0.048435 | 0.0043783 | -0.0014454 | -0.006561 | -0.054673 | 0.033978 | 0.056499 | -0.014148 | 0.13074 | -0.02645 | 0.063453 | 0.0077949 | 38.574 | 38.6631 | 38.5361 | 38.4556 | 38.3305 | 38.4832 | 8.6003 | 0.019362 | 0.027831 | -0.033458 | 0.061616 | 0.1648 | -0.051771 | -0.1962 | 93.0165 | -0.22996 | 122.9902 | 122.9523 | 29.9359 | -0.35507 | -0.20243 | 84.22 | -38.624 | 84.4356 | 84.3827 | 0.16274 | -38.5208 | -38.7374 | 122.8718 | 122.7467 | 122.8994 | 123.0793 | -30.0853 | 84.4778 | 84.581 | 84.3644 | 84.444 | -38.8818
507.9375 | 123.2025 | -85.8582 | 37.2574 | 0.048435 | 0.0054463 | -0.0014454 | -0.006561 | -0.054673 | 0.03291 | 0.07176 | -0.0098752 | 0.13074 | -0.027518 | 0.066658 | 0.0067259 | 37.3744 | 37.4635 | 37.332 | 37.2607 | 37.1309 | 37.279 | 8.6003 | 0.019362 | 0.050725 | -0.0243 | 0.066194 | 0.1648 | -0.051771 | -0.1962 | 94.4584 | 0.003301 | 123.2326 | 123.1902 | 28.7318 | -0.12653 | 0.021626 | 85.662 | -37.1912 | 85.8775 | 85.8339 | 0.1719 | -37.0926 | -37.3092 | 123.1188 | 122.989 | 123.1372 | 123.3217 | -28.6571 | 85.9243 | 86.023 | 85.8064 | 85.9089 | -37.4536
508.9375 | 123.2941 | -86.9934 | 36.0992 | 0.063697 | 0.0054463 | -0.00037739 | -0.008698 | -0.052536 | 0.035047 | 0.087021 | -0.012012 | 0.12967 | -0.024314 | 0.063453 | 0.0067259 | 36.3534 | 36.4379 | 36.3111 | 36.2397 | 36.1098 | 36.2717 | 8.6048 | 0.023941 | 0.036989 | -0.019721 | 0.057037 | 0.1648 | -0.074664 | -0.20078 | 95.5983 | 0.14046 | 123.3469 | 123.3045 | 27.7062 | 0.010515 | 0.17247 | 86.7926 | -36.0422 | 87.0173 | 86.9737 | 0.18106 | -35.9344 | -36.1739 | 123.2331 | 123.1032 | 123.2651 | 123.4313 | -27.4944 | 87.0504 | 87.1582 | 86.9187 | 87.0304 | -36.3
509.9375 | 123.1567 | -87.5519 | 35.6049 | 0.063697 | 0.0054463 | 0.00069161 | -0.006561 | -0.053604 | 0.035047 | 0.041238 | -0.010944 | 0.13181 | -0.025382 | 0.065589 | 0.0056579 | 35.6163 | 35.6962 | 35.5786 | 35.5026 | 35.3771 | 35.5208 | 8.6003 | 0.023941 | 0.036989 | -0.0243 | 0.061616 | 0.16938 | -0.0243 | -0.18704 | 96.1521 | -0.10227 | 123.1682 | 123.1304 | 26.9783 | -0.22773 | -0.08403 | 87.3648 | -35.5432 | 87.5758 | 87.5276 | 0.16274 | -35.4355 | -35.6292 | 123.0545 | 122.929 | 123.0727 | 123.2481 | -27.0046 | 87.6135 | 87.7213 | 87.5276 | 87.5889 | -35.7919
510.9375 | 123.3673 | -88.4125 | 34.639 | 0.063697 | 0.0054463 | 0.00069161 | -0.008698 | -0.053604 | 0.036115 | 0.07176 | -0.0098752 | 0.13181 | -0.02645 | 0.065589 | 0.0077949 | 34.8197 | 34.8995 | 34.7774 | 34.7059 | 34.5758 | 34.7379 | 8.6003 | 0.023941 | 0.027831 | -0.033458 | 0.061616 | 0.17396 | -0.047193 | -0.19162 | 97.0127 | 0.066968 | 123.2322 | 123.1898 | 26.1771 | -0.063159 | 0.09891 | 88.2209 | -34.5774 | 88.4364 | 88.379 | 0.15816 | -34.465 | -34.6862 | 123.1184 | 122.9883 | 123.1504 | 123.312 | -26.0387 | 88.4741 | 88.5864 | 88.3653 | 88.4403 | -34.8306
511.9531 | 123.3215 | -89.0259 | 34.0118 | 0.063697 | 0.0043783 | -0.0014454 | -0.009766 | -0.052536 | 0.03291 | 0.056499 | -0.0088072 | 0.13181 | -0.02645 | 0.064521 | 0.0077949 | 34.1421 | 34.2173 | 34.0906 | 34.0238 | 33.9027 | 34.0511 | 8.6048 | 0.010205 | 0.03241 | -0.033458 | 0.057037 | 0.16022 | -0.028878 | -0.20536 | 97.6307 | 0.011925 | 123.168 | 123.1165 | 25.4858 | -0.10912 | 0.039255 | 88.8205 | -33.9548 | 89.0361 | 88.9924 | 0.1719 | -33.8516 | -34.0407 | 123.0496 | 122.9286 | 123.077 | 123.2432 | -25.407 | 89.0829 | 89.1861 | 88.997 | 89.0583 | -34.2172
512.9375 | 123.2895 | -89.6667 | 33.4167 | 0.063697 | 0.0043783 | -0.0014454 | -0.009766 | -0.053604 | 0.035047 | 0.056499 | -0.012012 | 0.13181 | -0.025382 | 0.065589 | 0.0067259 | 33.611 | 33.6862 | 33.5824 | 33.4973 | 33.3716 | 33.5291 | 8.5957 | 0.005626 | 0.03241 | -0.038036 | 0.04788 | 0.16022 | -0.019721 | -0.20078 | 98.2624 | 0.080503 | 123.2777 | 123.2492 | 24.9867 | -0.045187 | 0.11239 | 89.466 | -33.3689 | 89.6724 | 89.6287 | 0.16274 | -33.2565 | -33.4365 | 123.164 | 123.0383 | 123.1959 | 123.3529 | -24.8211 | 89.7146 | 89.827 | 89.647 | 89.6992 | -33.6175
513.9375 | 123.2712 | -90.6281 | 32.4829 | 0.048435 | 0.0022413 | -0.0014454 | -0.007629 | -0.054673 | 0.035047 | 0.056499 | -0.0098752 | 0.13181 | -0.02645 | 0.065589 | 0.0056579 | 32.6358 | 32.7109 | 32.5981 | 32.5266 | 32.3963 | 32.563 | 8.6003 | 0.005626 | 0.03241 | -0.042615 | 0.04788 | 0.15564 | -0.10214 | -0.20994 | 99.2283 | 0.043723 | 123.2638 | 123.2262 | 23.9978 | -0.08666 | 0.08014 | 90.4181 | -32.435 | 90.6337 | 90.5854 | 0.16732 | -32.3273 | -32.585 | 123.1547 | 123.0243 | 123.1911 | 123.339 | -23.8826 | 90.6759 | 90.7837 | 90.5259 | 90.6605 | -32.6928
514.9375 | 123.317 | -91.3376 | 31.7642 | 0.048435 | 0.0033103 | -0.0025134 | -0.009766 | -0.052536 | 0.03291 | 0.056499 | -0.0098752 | 0.13074 | -0.027518 | 0.065589 | 0.0077949 | 31.9124 | 31.9829 | 31.8702 | 31.7987 | 31.6728 | 31.8351 | 8.6003 | -0.003531 | 0.023253 | -0.038036 | 0.043302 | 0.15564 | -0.11129 | -0.20078 | 99.9379 | 0.034448 | 123.25 | 123.2077 | 23.2699 | -0.091441 | 0.070832 | 91.1368 | -31.7209 | 91.3341 | 91.2995 | 0.16274 | -31.6086 | -31.8755 | 123.1363 | 123.0104 | 123.1726 | 123.3205 | -23.164 | 91.3809 | 91.4932 | 91.2263 | 91.3608 | -31.965
515.9375 | 123.317 | -91.626 | 31.4484 | 0.063697 | 0.0043783 | -0.00037739 | -0.007629 | -0.052536 | 0.035047 | 0.087021 | -0.0098752 | 0.13074 | -0.027518 | 0.065589 | 0.0067259 | 31.5553 | 31.6258 | 31.5131 | 31.4507 | 31.3294 | 31.4779 | 8.6094 | -0.00811 | 0.023253 | -0.033458 | 0.052459 | 0.15564 | -0.033457 | -0.1962 | 100.2354 | 0.002348 | 123.1813 | 123.139 | 22.9036 | -0.119 | 0.029558 | 91.4298 | -31.3959 | 91.6179 | 91.5925 | 0.16274 | -31.2927 | -31.4818 | 123.0767 | 122.9553 | 123.1039 | 123.2518 | -22.8389 | 91.6784 | 91.7816 | 91.5925 | 91.6492 | -31.6446
516.9375 | 123.2346 | -94.0842 | 29.0405 | 0.048435 | 0.0033103 | 0.00069161 | -0.010834 | -0.052536 | 0.03291 | 0.056499 | -0.0098752 | 0.13074 | -0.02645 | 0.066658 | 0.0056579 | 29.2341 | 29.3228 | 29.2056 | 29.134 | 29.0124 | 29.184 | 8.6048 | -0.003531 | 0.036989 | -0.038036 | 0.052459 | 0.15564 | -0.060928 | -0.1962 | 102.689 | 0.09352 | 123.3182 | 123.2898 | 20.6008 | -0.028102 | 0.14352 | 93.888 | -28.9881 | 94.0806 | 94.0461 | 0.15816 | -28.8849 | -29.1015 | 123.2182 | 123.0966 | 123.2682 | 123.4069 | -20.4357 | 94.1366 | 94.2398 | 94.0232 | 94.1212 | -29.2367
517.9375 | 123.349 | -103.5965 | 19.4412 | 0.063697 | 0.0054463 | 0.00069161 | -0.007629 | -0.052536 | 0.03291 | 0.041238 | -0.0088072 | 0.13394 | -0.02645 | 0.065589 | 0.0067259 | 20.5534 | 20.6189 | 20.5206 | 20.4992 | 20.3537 | 20.5625 | 8.6048 | -0.012689 | 0.018674 | -0.042615 | 0.052459 | 0.16022 | -0.0243 | -0.20078 | 112.2013 | 1.058 | 124.1499 | 124.1171 | 11.9158 | 0.91246 | 1.1213 | 103.3957 | -19.3888 | 103.5838 | 103.5539 | 0.15816 | -19.281 | -19.4655 | 124.0957 | 123.9502 | 124.159 | 124.2154 | -10.8364 | 103.649 | 103.7567 | 103.5722 | 103.6152 | -19.642
518.9375 | 123.3307 | -109.3414 | 13.7512 | 0.10948 | 0.0065153 | -0.00037739 | -0.005492 | -0.052536 | 0.035047 | 0.07176 | -0.0098752 | 0.13181 | -0.028587 | 0.066658 | 0.0077949 | 14.0521 | 14.1172 | 14.0286 | 14.0528 | 13.9294 | 14.125 | 8.6048 | -0.012689 | 0.03241 | -0.047194 | 0.04788 | 0.15564 | -0.0884 | -0.1962 | 117.9463 | 0.30162 | 123.3936 | 123.37 | 5.4238 | 0.17823 | 0.3738 | 109.1452 | -13.7033 | 109.3287 | 109.2942 | 0.14901 | -13.5956 | -13.8396 | 123.3943 | 123.2709 | 123.4664 | 123.4587 | -5.1464 | 109.3893 | 109.4971 | 109.253 | 109.3738 | -13.9474
519.9375 | 123.2986 | -112.7197 | 10.4004 | 0.063697 | 0.0065153 | -0.00037739 | -0.008698 | -0.051468 | 0.035047 | 0.056499 | -0.0088072 | 0.13288 | -0.02645 | 0.066658 | 0.0077949 | 10.6595 | 10.6879 | 10.6407 | 10.6694 | 10.5639 | 10.7689 | 8.5316 | -0.012689 | 0.027831 | -0.038036 | 0.043302 | 0.1648 | -0.065507 | -0.20078 | 121.2513 | 0.26902 | 123.3793 | 123.3604 | 2.1091 | 0.16355 | 0.36851 | 112.5189 | -10.3571 | 112.707 | 112.6817 | 0.16274 | -10.2356 | -10.4659 | 123.3891 | 123.2837 | 123.4886 | 123.4076 | -1.8688 | 112.763 | 112.8845 | 112.6542 | 112.7476 | -10.6012
520.9375 | 123.3078 | -114.6194 | 8.5007 | 0.063697 | 0.0054463 | 0.00069161 | -0.006561 | -0.052536 | 0.036115 | 0.025977 | -0.0098752 | 0.12967 | -0.027518 | 0.065589 | 0.0067259 | 8.6222 | 8.6412 | 8.5896 | 8.6458 | 8.5446 | 8.7406 | 7.9134 | -0.00811 | 0.027831 | -0.028879 | 0.057037 | 0.1648 | -0.015142 | -0.1962 | 122.5329 | 0.14509 | 123.2416 | 123.209 | 0.67617 | 0.043961 | 0.23991 | 114.4232 | -8.4436 | 114.6113 | 114.5906 | 0.16732 | -8.3359 | -8.5158 | 123.2652 | 123.1641 | 123.36 | 123.2607 | -0.58724 | 114.6765 | 114.7842 | 114.6043 | 114.6473 | -8.6969
521.9375 | 123.2849 | -118.8263 | 4.3671 | 0.063697 | 0.0054463 | 0.0017596 | -0.004424 | -0.050399 | 0.033978 | 0.056499 | -0.0098752 | 0.13288 | -0.025382 | 0.066658 | 0.0056579 | 4.6664 | 4.6853 | 4.6294 | 4.7312 | 4.6205 | 4.835 | 4.3602 | -0.003531 | 0.03241 | -0.042615 | 0.043302 | 0.15107 | -0.12045 | -0.20078 | 123.1865 | 0.36417 | 123.4927 | 123.4557 | 0.2692 | 0.25343 | 0.46797 | 118.6255 | -4.3238 | 118.8228 | 118.7837 | 0.15816 | -4.216 | -4.4875 | 123.5575 | 123.4468 | 123.6613 | 123.5116 | -0.006881 | 118.8696 | 118.9774 | 118.7058 | 118.8587 | -4.5678
522.9531 | 123.3032 | -121.3028 | 1.8723 | 0.048435 | 0.0043783 | -0.00037739 | -0.008698 | -0.053604 | 0.035047 | 0.07176 | -0.0088072 | 0.13181 | -0.027518 | 0.065589 | 0.0067259 | 1.9194 | 1.9336 | 1.8916 | 2.0071 | 1.8915 | 2.1108 | 1.6724 | -0.012689 | 0.027831 | -0.033458 | 0.04788 | 0.14649 | -0.074664 | -0.20536 | 122.9751 | 0.13485 | 123.2222 | 123.1944 | 0.21922 | 0.019202 | 0.23851 | 121.0974 | -1.8244 | 121.2901 | 121.2693 | 0.1719 | -1.7258 | -1.9469 | 123.3099 | 123.1942 | 123.4136 | 123.2364 | -0.1999 | 121.3507 | 121.4493 | 121.2281 | 121.3306 | -2.0776
523.9375 | 123.3582 | -122.2321 | 0.94757 | 0.048435 | 0.0033103 | 0.00069161 | -0.004424 | -0.053604 | 0.033978 | 0.07176 | -0.0098752 | 0.13181 | -0.027518 | 0.067726 | 0.0056579 | 0.88468 | 0.89423 | 0.84773 | 0.95407 | 0.85662 | 1.076 | 0.64668 | -0.017267 | 0.018674 | -0.047194 | 0.034145 | 0.14191 | -0.10214 | -0.21452 | 122.8787 | 0.006499 | 123.1167 | 123.0798 | 0.20105 | -0.090953 | 0.12843 | 122.0175 | -0.91343 | 122.2148 | 122.1849 | 0.16732 | -0.80566 | -1.0497 | 123.1861 | 123.0887 | 123.3081 | 123.1263 | -0.3009 | 122.2662 | 122.374 | 122.1299 | 122.2507 | -1.1621
524.9531 | 123.3353 | -122.5983 | 0.5722 | 0.048435 | 0.0054463 | -0.0014454 | -0.002287 | -0.052536 | 0.035047 | 0.041238 | -0.010944 | 0.13288 | -0.025382 | 0.065589 | 0.0077949 | 0.48178 | 0.48216 | 0.44484 | 0.55575 | 0.45825 | 0.67766 | 0.26663 | -0.021846 | 0.018674 | -0.047194 | 0.024988 | 0.15107 | -0.060928 | -0.21452 | 122.8649 | -0.016455 | 123.08 | 123.0431 | 0.17822 | -0.11395 | 0.10546 | 122.3838 | -0.54722 | 122.5764 | 122.5511 | 0.16732 | -0.42114 | -0.63313 | 123.154 | 123.0565 | 123.2759 | 123.0804 | -0.30558 | 122.6233 | 122.7493 | 122.5373 | 122.6169 | -0.78672
525.9375 | 123.3215 | -122.7356 | 0.40283 | 0.063697 | 0.0033103 | -0.00037739 | -0.003356 | -0.051468 | 0.035047 | 0.07176 | -0.010944 | 0.13074 | -0.02645 | 0.066658 | 0.0067259 | 0.34443 | 0.3448 | 0.30749 | 0.40466 | 0.30257 | 0.53115 | 0.11552 | -0.012689 | 0.023253 | -0.047194 | 0.038723 | 0.14191 | -0.12961 | -0.20536 | 122.8511 | 0.001832 | 123.08 | 123.0431 | 0.19197 | -0.10026 | 0.12832 | 122.5302 | -0.36411 | 122.7229 | 122.6884 | 0.15816 | -0.26093 | -0.53244 | 123.1403 | 123.0382 | 123.2667 | 123.0804 | -0.28731 | 122.7743 | 122.8775 | 122.606 | 122.7588 | -0.60819
526.9375 | 123.2208 | -122.8592 | 0.39825 | 0.033173 | 0.0011733 | -0.0025134 | -0.002287 | -0.053604 | 0.033978 | 0.056499 | -0.0088072 | 0.12967 | -0.028587 | 0.067726 | 0.0088629 | 0.26202 | 0.27154 | 0.24797 | 0.33599 | 0.24304 | 0.45331 | 0.097205 | -0.026425 | 0.018674 | -0.051772 | 0.020409 | 0.13275 | -0.11129 | -0.21452 | 122.9564 | -0.062266 | 123.1212 | 123.1072 | 0.15077 | -0.15521 | 0.055057 | 122.6447 | -0.37784 | 122.8328 | 122.8074 | 0.16274 | -0.2655 | -0.50955 | 123.1952 | 123.1022 | 123.3125 | 123.1307 | -0.30105 | 122.8796 | 122.9919 | 122.7479 | 122.8779 | -0.61277
527.9531 | 123.3765 | -122.85 | 0.31128 | 0.048435 | 0.0033103 | -0.0025134 | -0.002287 | -0.051468 | 0.036115 | 0.056499 | -0.010944 | 0.13074 | -0.028587 | 0.066658 | 0.0056579 | 0.20708 | 0.22118 | 0.1793 | 0.28105 | 0.19267 | 0.39837 | 0.07431 | -0.026425 | 0.014095 | -0.047194 | 0.034145 | 0.14191 | -0.12045 | -0.21452 | 122.9243 | -0.030232 | 123.0571 | 123.0293 | 0.10499 | -0.1186 | 0.087089 | 122.6355 | -0.27713 | 122.8236 | 122.8028 | 0.16732 | -0.16937 | -0.43173 | 123.1311 | 123.0427 | 123.2484 | 123.0712 | -0.23697 | 122.8842 | 122.9919 | 122.7296 | 122.8641 | -0.5258
528.9375 | 123.3215 | -122.9324 | 0.27924 | 0.048435 | 0.0001043 | -0.0014454 | -0.002287 | -0.053604 | 0.033978 | 0.056499 | -0.0088072 | 0.13074 | -0.028587 | 0.068795 | 0.0077949 | 0.17045 | 0.18455 | 0.15641 | 0.249 | 0.1652 | 0.35258 | 0.055995 | -0.026425 | 0.018674 | -0.047194 | 0.029566 | 0.12817 | -0.10214 | -0.2191 | 122.9884 | -0.030238 | 123.1029 | 123.0888 | 0.10041 | -0.11404 | 0.073346 | 122.7133 | -0.24967 | 122.906 | 122.8852 | 0.1719 | -0.15106 | -0.38137 | 123.1814 | 123.0976 | 123.285 | 123.117 | -0.22324 | 122.962 | 123.0606 | 122.8303 | 122.9511 | -0.49833
530.0469 | 123.3536 | -122.9828 | 0.19226 | 0.033173 | 0.0043783 | -0.0014454 | -0.005492 | -0.052536 | 0.035047 | 0.056499 | -0.0098752 | 0.13181 | -0.028587 | 0.067726 | 0.0077949 | 0.074302 | 0.097557 | 0.064843 | 0.16201 | 0.087359 | 0.27017 | 0.001048 | -0.00811 | 0.018674 | -0.038036 | 0.043302 | 0.13275 | -0.051771 | -0.20078 | 122.9838 | -0.030252 | 123.0571 | 123.0476 | 0.063795 | -0.1049 | 0.077906 | 122.782 | -0.14896 | 122.9747 | 122.9448 | 0.16274 | -0.059511 | -0.24403 | 123.1448 | 123.0701 | 123.253 | 123.0803 | -0.19121 | 123.0261 | 123.1155 | 122.931 | 123.0015 | -0.39304
530.9375 | 123.349 | -123.0835 | 0.11444 | 0.048435 | 0.0075833 | 0.00069161 | -0.006561 | -0.051468 | 0.033978 | 0.087021 | -0.0088072 | 0.13181 | -0.027518 | 0.066658 | 0.0056579 | 0.023939 | 0.05635 | 0.023639 | 0.1208 | 0.018675 | 0.22896 | -0.003531 | -0.012689 | 0.027831 | -0.042615 | 0.043302 | 0.15564 | -0.083821 | -0.20078 | 123.08 | 0.006363 | 123.1074 | 123.1071 | 0.02717 | -0.095766 | 0.11452 | 122.8827 | -0.071139 | 123.0708 | 123.0409 | 0.15816 | 0.041202 | -0.19826 | 123.2043 | 123.1022 | 123.3125 | 123.1398 | -0.11797 | 123.1268 | 123.2391 | 122.9997 | 123.1113 | -0.31522
531.9375 | 123.3215 | -123.0927 | 0.1236 | 0.033173 | 0.0075833 | -0.00037739 | -0.006561 | -0.053604 | 0.035047 | 0.041238 | -0.0098752 | 0.13181 | -0.028587 | 0.068795 | 0.0067259 | 0.005626 | 0.047193 | 0.014482 | 0.10707 | -0.00422 | 0.21522 | -0.044742 | -0.00811 | 0.023253 | -0.033458 | 0.034145 | 0.14649 | -0.047193 | -0.19162 | 123.0479 | -0.016528 | 123.0983 | 123.1071 | 0.059224 | -0.12782 | 0.091628 | 122.901 | -0.089451 | 123.0845 | 123.0592 | 0.15816 | 0.02289 | -0.17079 | 123.1997 | 123.0884 | 123.3079 | 123.1398 | -0.16834 | 123.1268 | 123.2391 | 123.0455 | 123.1159 | -0.31522
532.9375 | 123.3032 | -123.0835 | 0.091553 | 0.063697 | 0.0075833 | -0.0014454 | -0.007629 | -0.050399 | 0.035047 | 0.056499 | -0.0098752 | 0.13181 | -0.025382 | 0.067726 | 0.0077949 | 0.010204 | 0.051771 | 0.014482 | 0.11622 | -0.013378 | 0.21522 | -0.012689 | -0.012689 | 0.03241 | -0.038036 | 0.043302 | 0.14649 | -0.097557 | -0.20078 | 123.0708 | 0.024672 | 123.0937 | 123.098 | 0.027171 | -0.10493 | 0.12367 | 122.8827 | -0.048251 | 123.0708 | 123.0455 | 0.16274 | 0.054933 | -0.18911 | 123.1997 | 123.0701 | 123.2987 | 123.1353 | -0.10424 | 123.1268 | 123.23 | 122.9859 | 123.1159 | -0.29233
533.9375 | 123.3353 | -123.0881 | 0.11902 | 0.078959 | 0.011856 | -0.00037739 | -0.009766 | -0.052536 | 0.036115 | 0.07176 | -0.0088072 | 0.13074 | -0.02645 | 0.068795 | 0.0056579 | 0.010204 | 0.047193 | 0.01906 | 0.10707 | 0.004938 | 0.21522 | -0.076794 | -0.00811 | 0.027831 | -0.038036 | 0.04788 | 0.14191 | -0.042614 | -0.19162 | 123.0113 | -0.011951 | 123.0983 | 123.1071 | 0.095854 | -0.11408 | 0.096205 | 122.8965 | -0.071139 | 123.08 | 123.05 | 0.15359 | 0.022888 | -0.16163 | 123.1951 | 123.093 | 123.3033 | 123.1353 | -0.19581 | 123.136 | 123.23 | 123.0455 | 123.1159 | -0.31064
534.9375 | 123.3353 | -123.0835 | 0.091553 | 0.063697 | 0.0065153 | 0.00069161 | -0.010834 | -0.054673 | 0.033978 | 0.07176 | -0.0098752 | 0.13074 | -0.027518 | 0.068795 | 0.0067259 | 0.005626 | 0.042614 | 0.009904 | 0.11165 | -0.013378 | 0.20607 | -0.053899 | 0.001048 | 0.036989 | -0.028879 | 0.052459 | 0.16938 | -0.079243 | -0.18246 | 123.0296 | 0.020094 | 123.0891 | 123.0934 | 0.063803 | -0.10493 | 0.11451 | 122.901 | -0.039094 | 123.0845 | 123.0546 | 0.15358 | 0.077826 | -0.1708 | 123.1951 | 123.0701 | 123.2896 | 123.1261 | -0.14545 | 123.136 | 123.2529 | 123.0043 | 123.1205 | -0.27402
535.9375 | 123.317 | -123.0789 | 0.1236 | 0.048435 | 0.0065153 | -0.0014454 | -0.007629 | -0.054673 | 0.033978 | 0.087021 | -0.010944 | 0.13181 | -0.028587 | 0.069863 | 0.0088629 | 0.005626 | 0.047193 | 0.014482 | 0.10707 | -0.022536 | 0.21064 | -0.031005 | 0.001048 | 0.036989 | -0.028879 | 0.04788 | 0.16022 | -0.097557 | -0.19162 | 123.0479 | -0.016528 | 123.0845 | 123.0934 | 0.045487 | -0.14613 | 0.087049 | 122.8873 | -0.075716 | 123.08 | 123.05 | 0.16274 | 0.036626 | -0.22115 | 123.186 | 123.0564 | 123.2896 | 123.1261 | -0.1546 | 123.1268 | 123.2391 | 122.9814 | 123.1159 | -0.31522
536.9375 | 123.3353 | -123.0698 | 0.10986 | 0.033173 | 0.0075833 | -0.0025134 | -0.007629 | -0.053604 | 0.036115 | 0.087021 | -0.0098752 | 0.13074 | -0.029655 | 0.068795 | 0.0045899 | 0.001048 | 0.042614 | 0.005325 | 0.097912 | -0.017957 | 0.20149 | -0.026426 | -0.003531 | 0.036989 | -0.028879 | 0.057037 | 0.15107 | -0.079243 | -0.18704 | 123.0433 | -0.011951 | 123.0708 | 123.0751 | 0.031751 | -0.12782 | 0.091625 | 122.8827 | -0.052826 | 123.0662 | 123.0409 | 0.15816 | 0.041202 | -0.18911 | 123.1677 | 123.0518 | 123.2713 | 123.1124 | -0.13629 | 123.1268 | 123.2208 | 122.9905 | 123.1068 | -0.29691
537.9531 | 123.3307 | -123.1567 | 0.064087 | 0.063697 | 0.0075833 | -0.00037739 | -0.009766 | -0.052536 | 0.033978 | 0.087021 | -0.0098752 | 0.13394 | -0.02645 | 0.067726 | 0.0077949 | 0.005626 | 0.047193 | 0.005325 | 0.11165 | -0.00422 | 0.20607 | -0.058478 | -0.00811 | 0.027831 | -0.033458 | 0.04788 | 0.15107 | -0.079243 | -0.18704 | 123.0983 | 0.04756 | 123.1624 | 123.1621 | 0.063803 | -0.068307 | 0.14198 | 122.9697 | -0.016207 | 123.1486 | 123.1233 | 0.15358 | 0.086978 | -0.14333 | 123.2684 | 123.1525 | 123.3628 | 123.2039 | -0.12257 | 123.2046 | 123.3078 | 123.0775 | 123.1846 | -0.25113
538.9375 | 123.3765 | -123.0606 | 0.1236 | 0.063697 | 0.0086513 | -0.0014454 | -0.009766 | -0.054673 | 0.033978 | 0.07176 | -0.010944 | 0.13074 | -0.029655 | 0.067726 | 0.0056579 | 0.010204 | 0.038035 | 0.009904 | 0.10249 | -0.00422 | 0.21064 | -0.067636 | 0.005626 | 0.03241 | -0.028879 | 0.043302 | 0.15564 | -0.051771 | -0.18704 | 122.993 | -0.021106 | 123.0708 | 123.0705 | 0.07754 | -0.12782 | 0.087049 | 122.8736 | -0.080294 | 123.0662 | 123.0317 | 0.15816 | 0.032047 | -0.17537 | 123.1631 | 123.0564 | 123.2713 | 123.0986 | -0.19123 | 123.1039 | 123.2163 | 123.0088 | 123.093 | -0.31064
539.9375 | 123.3078 | -123.1293 | 0.07782 | 0.048435 | 0.0054463 | 0.00069161 | -0.007629 | -0.052536 | 0.033978 | 0.07176 | -0.012012 | 0.13181 | -0.027518 | 0.069863 | 0.0056579 | 0.005626 | 0.042614 | 0.005325 | 0.10249 | -0.027115 | 0.20607 | -0.067636 | 0.001048 | 0.036989 | -0.028879 | 0.04788 | 0.15564 | -0.0884 | -0.17788 | 123.0616 | 0.02467 | 123.1349 | 123.1346 | 0.072961 | -0.10494 | 0.12825 | 122.9514 | -0.02994 | 123.1303 | 123.1004 | 0.14901 | 0.077823 | -0.16622 | 123.2318 | 123.1022 | 123.3353 | 123.1719 | -0.14546 | 123.1772 | 123.2849 | 123.0409 | 123.1663 | -0.2557
540.9375 | 123.3856 | -123.0743 | 0.10071 | 0.048435 | 0.0086513 | 0.0017596 | -0.007629 | -0.051468 | 0.035047 | 0.07176 | -0.0098752 | 0.13501 | -0.027518 | 0.068795 | 0.0045899 | 0.005626 | 0.038035 | 0.01906 | 0.11165 | -0.031693 | 0.20607 | -0.085952 | -0.00811 | 0.027831 | -0.038036 | 0.04788 | 0.15564 | -0.070086 | -0.1962 | 122.9884 | 0.010939 | 123.08 | 123.0934 | 0.10501 | -0.1324 | 0.10536 | 122.8781 | -0.052828 | 123.0662 | 123.0363 | 0.15816 | 0.054935 | -0.17079 | 123.186 | 123.0426 | 123.2804 | 123.1124 | -0.18666 | 123.1222 | 123.23 | 123.0043 | 123.1022 | -0.29691
541.9375 | 123.3765 | -123.0606 | 0.11444 | 0.078959 | 0.0065153 | 0.00069161 | -0.007629 | -0.053604 | 0.033978 | 0.07176 | -0.0098752 | 0.13394 | -0.028587 | 0.069863 | 0.0067259 | 0.005626 | 0.042614 | 0.01906 | 0.11165 | 0.009517 | 0.21064 | -0.090531 | 0.001048 | 0.041567 | -0.033458 | 0.04788 | 0.15107 | -0.051771 | -0.19162 | 122.9701 | -0.002794 | 123.0662 | 123.0797 | 0.10959 | -0.10492 | 0.096204 | 122.869 | -0.066561 | 123.0617 | 123.0272 | 0.15816 | 0.036624 | -0.16621 | 123.1723 | 123.0701 | 123.2713 | 123.1032 | -0.20497 | 123.1085 | 123.2117 | 123.0088 | 123.1022 | -0.30606
542.9531 | 123.3902 | -123.0881 | 0.10986 | 0.063697 | 0.0065153 | -0.0014454 | -0.006561 | -0.052536 | 0.035047 | 0.056499 | -0.0098752 | 0.13394 | -0.028587 | 0.067726 | 0.0067259 | 0.010204 | 0.047193 | 0.014482 | 0.10707 | 0.014096 | 0.21064 | -0.10427 | 0.001048 | 0.027831 | -0.028879 | 0.04788 | 0.16022 | -0.05635 | -0.19162 | 122.9838 | -0.002795 | 123.0983 | 123.1026 | 0.11875 | -0.095767 | 0.10078 | 122.8965 | -0.061983 | 123.0891 | 123.0592 | 0.16274 | 0.050359 | -0.16621 | 123.1951 | 123.1022 | 123.2987 | 123.1353 | -0.21413 | 123.136 | 123.2483 | 123.0317 | 123.1159 | -0.30149
543.9375 | 123.3124 | -123.0789 | 0.11902 | 0.063697 | 0.0065153 | -0.00037739 | -0.008698 | -0.053604 | 0.036115 | 0.056499 | -0.010944 | 0.13501 | -0.027518 | 0.069863 | 0.0067259 | 0.010204 | 0.033457 | 0.014482 | 0.10249 | 0.009517 | 0.21064 | -0.072215 | -0.00811 | 0.03241 | -0.038036 | 0.04788 | 0.15564 | -0.0884 | -0.19162 | 123.0067 | -0.016529 | 123.0891 | 123.0934 | 0.086697 | -0.1095 | 0.091626 | 122.8873 | -0.071139 | 123.0708 | 123.0409 | 0.15359 | 0.036624 | -0.20742 | 123.1814 | 123.0884 | 123.2896 | 123.1124 | -0.19123 | 123.1268 | 123.2346 | 122.9905 | 123.1113 | -0.31064
544.9375 | 123.3673 | -123.0515 | 0.09613 | 0.063697 | 0.0043783 | -0.00037739 | -0.007629 | -0.053604 | 0.033978 | 0.025977 | -0.0098752 | 0.13394 | -0.029655 | 0.067726 | 0.0067259 | 0.005626 | 0.047193 | 0.014482 | 0.10707 | 0.018675 | 0.20607 | -0.063057 | -0.003531 | 0.023253 | -0.0243 | 0.04788 | 0.15107 | -0.019721 | -0.1962 | 122.9884 | 0.010938 | 123.0571 | 123.0659 | 0.077539 | -0.077455 | 0.10994 | 122.8553 | -0.04825 | 123.0479 | 123.0272 | 0.1719 | 0.054935 | -0.11585 | 123.1585 | 123.0701 | 123.2575 | 123.0986 | -0.15919 | 123.0993 | 123.2025 | 123.0317 | 123.0747 | -0.29233
545.9531 | 123.23 | -123.1476 | 0.15564 | 0.048435 | 0.0054463 | -0.0025134 | -0.006561 | -0.051468 | 0.035047 | 0.07176 | -0.0098752 | 0.13501 | -0.027518 | 0.069863 | 0.0067259 | 0.010204 | 0.047193 | 0.009904 | 0.11165 | 0.014096 | 0.21064 | -0.081373 | -0.017267 | 0.027831 | -0.047194 | 0.034145 | 0.13733 | -0.079243 | -0.20078 | 123.0662 | -0.043993 | 123.1578 | 123.1575 | 0.091277 | -0.14154 | 0.055005 | 122.9468 | -0.12149 | 123.1303 | 123.1004 | 0.15359 | -0.018311 | -0.23488 | 123.2592 | 123.1617 | 123.3582 | 123.1948 | -0.23701 | 123.1817 | 123.2849 | 123.0683 | 123.1754 | -0.35642
546.9375 | 123.2803 | -123.1293 | 0.12817 | 0.048435 | 0.0033103 | -0.0014454 | -0.006561 | -0.053604 | 0.031842 | 0.07176 | -0.010944 | 0.13288 | -0.027518 | 0.072 | 0.0056579 | 0.010204 | 0.042614 | 0.01906 | 0.10707 | -0.017957 | 0.2198 | -0.063057 | -0.026425 | 0.018674 | -0.051772 | 0.024988 | 0.13733 | -0.10671 | -0.21452 | 123.0662 | -0.021106 | 123.1395 | 123.1483 | 0.082117 | -0.14613 | 0.091628 | 122.9148 | -0.10319 | 123.1028 | 123.0775 | 0.16274 | 0.009155 | -0.23489 | 123.2363 | 123.1113 | 123.3491 | 123.1719 | -0.19123 | 123.1543 | 123.2666 | 123.0226 | 123.1479 | -0.34269
547.9531 | 123.2758 | -123.111 | 0.12817 | 0.048435 | 0.0043783 | -0.0025134 | -0.005492 | -0.053604 | 0.033978 | 0.056499 | -0.010944 | 0.13288 | -0.028587 | 0.072 | 0.0077949 | 0.005626 | 0.042614 | 0.014482 | 0.10707 | -0.00422 | 0.21064 | -0.067636 | -0.026425 | 0.014095 | -0.06093 | 0.024988 | 0.12359 | -0.097557 | -0.2191 | 123.0433 | -0.021106 | 123.1166 | 123.1254 | 0.082118 | -0.13239 | 0.082471 | 122.8919 | -0.10319 | 123.0845 | 123.05 | 0.15817 | -0.004581 | -0.22573 | 123.218 | 123.1067 | 123.3216 | 123.1536 | -0.19581 | 123.1359 | 123.2346 | 123.0134 | 123.1251 | -0.34727
548.9375 | 123.3307 | -123.0652 | 0.1236 | 0.048435 | 0.0033103 | -0.0035824 | -0.004424 | -0.053604 | 0.035047 | 0.056499 | -0.010944 | 0.13288 | -0.02645 | 0.070931 | 0.0077949 | 0.010204 | 0.042614 | 0.014482 | 0.10249 | 0.018675 | 0.2198 | -0.072215 | -0.026425 | 0.014095 | -0.065509 | 0.020409 | 0.12817 | -0.083821 | -0.21452 | 122.993 | -0.021106 | 123.0754 | 123.0797 | 0.086697 | -0.10492 | 0.096206 | 122.8507 | -0.10319 | 123.0388 | 122.9997 | 0.14901 | 0.004576 | -0.20742 | 123.1677 | 123.0839 | 123.285 | 123.1078 | -0.19581 | 123.0856 | 123.1934 | 122.9814 | 123.0793 | -0.33811
549.9375 | 123.3261 | -123.0835 | 0.1236 | 0.048435 | 0.0022413 | -0.0046504 | -0.005492 | -0.052536 | 0.035047 | 0.041238 | -0.010944 | 0.13394 | -0.029655 | 0.072 | 0.0077949 | 0.005626 | 0.033457 | 0.005325 | 0.11165 | 0.009517 | 0.21064 | -0.058478 | -0.035582 | 0.004938 | -0.06093 | 0.015831 | 0.12359 | -0.079243 | -0.2191 | 123.025 | -0.011949 | 123.0891 | 123.0888 | 0.063803 | -0.11408 | 0.087049 | 122.8644 | -0.10776 | 123.0479 | 123.0226 | 0.15817 | -3e-06 | -0.20284 | 123.1951 | 123.093 | 123.2941 | 123.117 | -0.18207 | 123.0993 | 123.2071 | 123.0043 | 123.0884 | -0.34269
550.9375 | 123.2712 | -123.1247 | 0.13275 | 0.063697 | 0.0022413 | -0.0014454 | -0.003356 | -0.052536 | 0.033978 | 0.056499 | -0.010944 | 0.13501 | -0.028587 | 0.070931 | 0.0067259 | 0.010204 | 0.038035 | 0.01906 | 0.10707 | 0.032411 | 0.20149 | -0.085952 | -0.026425 | 0.014095 | -0.06093 | 0.024988 | 0.13275 | -0.065507 | -0.20536 | 123.0387 | -0.025683 | 123.1349 | 123.1438 | 0.10501 | -0.10034 | 0.068737 | 122.9193 | -0.10776 | 123.0983 | 123.0638 | 0.14443 | -1e-06 | -0.19826 | 123.2318 | 123.1571 | 123.3262 | 123.1627 | -0.2187 | 123.1497 | 123.2574 | 123.0592 | 123.1388 | -0.33811
551.9375 | 123.3673 | -123.0881 | 0.11902 | 0.017911 | 0.0043783 | -0.0014454 | -0.005492 | -0.053604 | 0.03291 | 0.056499 | -0.0098752 | 0.13608 | -0.030723 | 0.073068 | 0.0077949 | 0.001048 | 0.033457 | 0.005325 | 0.093333 | 0.000359 | 0.20149 | -0.067636 | -0.017267 | 0.023253 | -0.042615 | 0.034145 | 0.14191 | -0.060928 | -0.20078 | 123.0204 | -0.025686 | 123.0891 | 123.0934 | 0.072961 | -0.11866 | 0.082469 | 122.8873 | -0.084874 | 123.0708 | 123.0455 | 0.15816 | 0.022888 | -0.17995 | 123.1814 | 123.0884 | 123.2896 | 123.1215 | -0.18666 | 123.1222 | 123.23 | 123.0271 | 123.1113 | -0.3198
552.9531 | 123.262 | -123.1522 | 0.1236 | 0.063697 | 0.0054463 | -0.0046504 | -0.008698 | -0.053604 | 0.03291 | 0.041238 | -0.0088072 | 0.13394 | -0.028587 | 0.070931 | 0.0067259 | 0.005626 | 0.038035 | 0.009904 | 0.093333 | -0.095798 | 0.20149 | 0.088047 | -0.012689 | 0.018674 | -0.042615 | 0.038723 | 0.13733 | -0.15708 | -0.20078 | 123.2402 | -0.030263 | 123.1578 | 123.1621 | -0.078143 | -0.21939 | 0.077892 | 122.9514 | -0.084873 | 123.1395 | 123.1095 | 0.15816 | 0.013733 | -0.28068 | 123.2455 | 123.0564 | 123.3536 | 123.1902 | -0.035549 | 123.1909 | 123.2895 | 122.9951 | 123.1708 | -0.32438
553.9375 | 123.3627 | -123.1293 | 0.086975 | 0.048435 | 0.0054463 | -0.00037739 | -0.007629 | -0.053604 | 0.03291 | 0.041238 | -0.0098752 | 0.13394 | -0.028587 | 0.070931 | 0.0056579 | -0.008109 | 0.038035 | 0.009904 | 0.088755 | -0.008799 | 0.19691 | -0.063057 | -0.012689 | 0.027831 | -0.047194 | 0.038723 | 0.14191 | -0.10671 | -0.1962 | 123.0662 | 0.00178 | 123.1212 | 123.1392 | 0.072961 | -0.095774 | 0.10993 | 122.9331 | -0.048252 | 123.1166 | 123.0821 | 0.14901 | 0.054932 | -0.19369 | 123.218 | 123.1205 | 123.3262 | 123.1673 | -0.15003 | 123.168 | 123.2712 | 123.0226 | 123.1571 | -0.28318
554.9531 | 123.2071 | -123.143 | 0.13275 | 0.033173 | 0.0043783 | -0.0025134 | -0.007629 | -0.053604 | 0.03291 | 0.07176 | -0.012012 | 0.13288 | -0.030723 | 0.069863 | 0.0067259 | -0.003531 | 0.033457 | 0.005325 | 0.097912 | -0.04543 | 0.19691 | -0.049321 | -0.00811 | 0.027831 | -0.038036 | 0.043302 | 0.14649 | -0.13876 | -0.1962 | 123.0937 | -0.034839 | 123.1395 | 123.1483 | 0.054646 | -0.17818 | 0.064158 | 122.9468 | -0.089449 | 123.1349 | 123.105 | 0.15816 | 0.013735 | -0.27152 | 123.2409 | 123.0976 | 123.3399 | 123.1765 | -0.18207 | 123.1863 | 123.2895 | 123.0042 | 123.1708 | -0.32895
555.9375 | 123.3765 | -123.1064 | 0.10071 | 0.063697 | 0.0054463 | -0.0025134 | -0.006561 | -0.054673 | 0.035047 | 0.07176 | -0.012012 | 0.13288 | -0.027518 | 0.070931 | 0.0056579 | -0.012688 | 0.033457 | 0.000747 | 0.097912 | -0.040851 | 0.19691 | -0.026426 | -0.00811 | 0.027831 | -0.042615 | 0.038723 | 0.14649 | -0.12503 | -0.19162 | 123.08 | -0.002796 | 123.0937 | 123.1071 | 0.027173 | -0.14156 | 0.096201 | 122.9148 | -0.061985 | 123.0983 | 123.0638 | 0.14901 | 0.045778 | -0.22574 | 123.2043 | 123.0655 | 123.3033 | 123.1398 | -0.12713 | 123.1451 | 123.2529 | 122.9814 | 123.1342 | -0.29233
556.9375 | 123.3536 | -123.1155 | 0.07782 | 0.048435 | 0.0022413 | -0.0014454 | -0.007629 | -0.052536 | 0.035047 | 0.056499 | -0.012012 | 0.13288 | -0.029655 | 0.072 | 0.0045899 | -0.008109 | 0.038035 | 0.009904 | 0.097912 | 0.000359 | 0.20149 | -0.099689 | -0.00811 | 0.027831 | -0.038036 | 0.043302 | 0.15107 | -0.092979 | -0.20078 | 123.0159 | 0.020092 | 123.1074 | 123.1254 | 0.10959 | -0.077461 | 0.12367 | 122.9148 | -0.034518 | 123.1074 | 123.0775 | 0.16274 | 0.073245 | -0.1708 | 123.2135 | 123.1159 | 123.317 | 123.1536 | -0.17751 | 123.1588 | 123.2666 | 123.0226 | 123.1434 | -0.2786
557.9375 | 123.349 | -123.1201 | 0.10529 | 0.048435 | 0.0022413 | -0.00037739 | -0.007629 | -0.052536 | 0.03291 | 0.056499 | -0.0088072 | 0.13501 | -0.027518 | 0.069863 | 0.0056579 | 0.005626 | 0.038035 | 0.000747 | 0.10707 | -0.008799 | 0.19691 | -0.058478 | -0.012689 | 0.018674 | -0.038036 | 0.043302 | 0.14649 | -0.097557 | -0.18704 | 123.0616 | 0.001782 | 123.1257 | 123.1209 | 0.059225 | -0.11409 | 0.091623 | 122.9331 | -0.061984 | 123.1074 | 123.0821 | 0.14901 | 0.0412 | -0.20284 | 123.2272 | 123.1113 | 123.317 | 123.1582 | -0.16376 | 123.1634 | 123.2666 | 123.0226 | 123.1388 | -0.29233
558.9375 | 123.381 | -123.0606 | 0.11902 | 0.048435 | 0.0022413 | -0.0025134 | -0.006561 | -0.051468 | 0.035047 | 0.041238 | -0.012012 | 0.13288 | -0.028587 | 0.073068 | 0.0035219 | 0.005626 | 0.033457 | 0.014482 | 0.10249 | -0.077483 | 0.20607 | 0.065153 | -0.012689 | 0.023253 | -0.038036 | 0.043302 | 0.14191 | -0.11587 | -0.18704 | 123.1258 | -0.016529 | 123.0662 | 123.0751 | -0.050671 | -0.1965 | 0.087047 | 122.8736 | -0.075717 | 123.0479 | 123.0226 | 0.14901 | 0.022888 | -0.23489 | 123.1631 | 122.9831 | 123.2667 | 123.0941 | -0.053866 | 123.1039 | 123.2025 | 122.9447 | 123.0839 | -0.30606
559.9531 | 123.2803 | -123.1293 | 0.11444 | 0.033173 | 0.0033103 | -0.0035824 | -0.006561 | -0.054673 | 0.035047 | 0.041238 | -0.010944 | 0.13394 | -0.029655 | 0.072 | 0.0067259 | -0.003531 | 0.042614 | 0.005325 | 0.093333 | -0.059167 | 0.20149 | 0.0331 | -0.003531 | 0.023253 | -0.038036 | 0.034145 | 0.15107 | -0.092979 | -0.1962 | 123.1624 | -0.021108 | 123.1257 | 123.1346 | -0.027775 | -0.17361 | 0.087047 | 122.9331 | -0.080296 | 123.1257 | 123.0912 | 0.15816 | 0.036624 | -0.20742 | 123.2226 | 123.0701 | 123.3308 | 123.1719 | -0.081341 | 123.1634 | 123.2803 | 123.0363 | 123.1525 | -0.31064
560.9375 | 123.2391 | -123.1247 | 0.14191 | 0.033173 | 0.0022413 | -0.0025134 | -0.004424 | -0.053604 | 0.03291 | 0.07176 | -0.0098752 | 0.13288 | -0.028587 | 0.072 | 0.0067259 | 0.001048 | 0.038035 | 0.01906 | 0.097912 | -0.013378 | 0.19691 | -0.031005 | -0.00811 | 0.027831 | -0.038036 | 0.038723 | 0.15107 | -0.10671 | -0.19162 | 123.0937 | -0.043995 | 123.1257 | 123.1438 | 0.050065 | -0.15529 | 0.055002 | 122.9331 | -0.10318 | 123.1166 | 123.0867 | 0.15359 | 0.009158 | -0.24862 | 123.2226 | 123.1113 | 123.3216 | 123.1627 | -0.17291 | 123.1634 | 123.2758 | 123.018 | 123.1525 | -0.33353
561.9375 | 123.2483 | -123.1842 | 0.12817 | 0.063697 | 0.0022413 | -0.00037739 | -0.007629 | -0.053604 | 0.03291 | 0.056499 | -0.010944 | 0.13288 | -0.028587 | 0.070931 | 0.0077949 | -0.012688 | 0.042614 | 0.009904 | 0.10249 | -0.050009 | 0.20149 | 0.010206 | -0.003531 | 0.023253 | -0.028879 | 0.038723 | 0.14191 | -0.1525 | -0.18704 | 123.1944 | -0.025684 | 123.1715 | 123.1941 | -0.000302 | -0.17818 | 0.073314 | 122.9972 | -0.089451 | 123.1807 | 123.1553 | 0.15816 | 0.013733 | -0.28067 | 123.2867 | 123.1342 | 123.3857 | 123.2268 | -0.11797 | 123.2229 | 123.3261 | 123.0317 | 123.2075 | -0.31522
562.9375 | 123.2666 | -123.1338 | 0.16022 | 0.048435 | 0.0043783 | -0.0014454 | -0.007629 | -0.052536 | 0.033978 | 0.07176 | -0.010944 | 0.13181 | -0.028587 | 0.073068 | 0.0067259 | 0.005626 | 0.047193 | 0.014482 | 0.10249 | 0.014096 | 0.19691 | -0.072215 | -0.012689 | 0.023253 | -0.033458 | 0.038723 | 0.15107 | -0.042614 | -0.19162 | 123.0616 | -0.057727 | 123.1395 | 123.1483 | 0.086697 | -0.14612 | 0.036692 | 122.9422 | -0.12149 | 123.1212 | 123.1004 | 0.15816 | -0.009152 | -0.20283 | 123.2363 | 123.1479 | 123.3308 | 123.181 | -0.23243 | 123.1726 | 123.2849 | 123.0912 | 123.1571 | -0.35184
563.9375 | 123.3719 | -123.0972 | 0.1236 | 0.063697 | 0.0011733 | -0.0014454 | -0.005492 | -0.053604 | 0.033978 | 0.07176 | -0.010944 | 0.13501 | -0.028587 | 0.072 | 0.0067259 | 0.023939 | 0.033457 | 0.023639 | 0.1208 | -0.008799 | 0.21064 | 0.083468 | -0.00811 | 0.027831 | -0.042615 | 0.029566 | 0.15107 | -0.13419 | -0.1962 | 123.1807 | -0.002792 | 123.1212 | 123.1209 | -0.059829 | -0.13239 | 0.087049 | 122.901 | -0.09403 | 123.0891 | 123.0546 | 0.15359 | 0.027469 | -0.25778 | 123.218 | 123.0884 | 123.3079 | 123.1307 | -0.040128 | 123.1268 | 123.2483 | 122.963 | 123.1251 | -0.3198
564.9531 | 123.2712 | -123.0652 | 0.20599 | 0.048435 | -0.0009637 | -0.0046504 | -0.005492 | -0.051468 | 0.03291 | 0.056499 | -0.0088072 | 0.13181 | -0.027518 | 0.072 | 0.0045899 | 0.074302 | 0.033457 | 0.074 | 0.17117 | 0.064464 | 0.27017 | 0.1201 | -0.012689 | 0.036989 | -0.038036 | 0.038723 | 0.15564 | -0.12961 | -0.18704 | 123.1853 | -0.034828 | 123.1395 | 123.1392 | -0.0461 | -0.14153 | 0.064173 | 122.8781 | -0.16727 | 123.0525 | 123.0271 | 0.14901 | -0.050351 | -0.3356 | 123.2364 | 123.1296 | 123.3354 | 123.0986 | -0.085894 | 123.1039 | 123.2208 | 122.9356 | 123.1022 | -0.39304
565.9375 | 123.3948 | -122.9736 | 0.26093 | 0.063697 | -0.0020317 | -0.0046504 | -0.002287 | -0.054673 | 0.033978 | 0.07176 | -0.012012 | 0.13288 | -0.027518 | 0.072 | 0.0067259 | 0.1384 | 0.13419 | 0.13352 | 0.22611 | 0.11483 | 0.32053 | 0.10636 | -0.00811 | 0.023253 | -0.028879 | 0.038723 | 0.15107 | -0.1525 | -0.19162 | 123.08 | -0.034819 | 123.112 | 123.1072 | 0.027154 | -0.14609 | 0.059606 | 122.782 | -0.2222 | 122.9655 | 122.9448 | 0.16274 | -0.10986 | -0.41343 | 123.1997 | 123.0885 | 123.2942 | 123.1078 | -0.15456 | 123.0124 | 123.1247 | 122.8211 | 122.9969 | -0.45255
566.9531 | 123.3078 | -122.9462 | 0.33417 | 0.063697 | 0.0001043 | -0.0046504 | -0.003356 | -0.054673 | 0.033978 | 0.041238 | -0.0098752 | 0.13181 | -0.028587 | 0.072 | 0.0056579 | 0.19334 | 0.21202 | 0.17472 | 0.26273 | 0.15146 | 0.37548 | 0.078889 | -0.00811 | 0.03241 | -0.033458 | 0.038723 | 0.15564 | -0.097557 | -0.19162 | 123.0251 | -0.071433 | 123.1395 | 123.1209 | 0.095833 | -0.1827 | 0.041308 | 122.7545 | -0.29544 | 122.9381 | 122.9127 | 0.15816 | -0.17852 | -0.43172 | 123.2089 | 123.0976 | 123.3216 | 123.1582 | -0.25528 | 122.9849 | 123.1018 | 122.8486 | 122.9786 | -0.52579
567.9375 | 123.2391 | -122.9141 | 0.35248 | 0.063697 | -0.0009637 | -0.0035824 | -0.004424 | -0.053604 | 0.035047 | 0.07176 | -0.0098752 | 0.13394 | -0.027518 | 0.073068 | 0.0067259 | 0.21165 | 0.22576 | 0.19304 | 0.28105 | 0.1652 | 0.38921 | 0.078889 | -0.00811 | 0.027831 | -0.028879 | 0.043302 | 0.15564 | -0.10214 | -0.18704 | 122.993 | -0.071431 | 123.1258 | 123.1072 | 0.11415 | -0.18728 | 0.036733 | 122.7271 | -0.30918 | 122.906 | 122.8852 | 0.15816 | -0.19684 | -0.45461 | 123.1952 | 123.0793 | 123.3033 | 123.1399 | -0.27359 | 122.9574 | 123.0698 | 122.812 | 122.942 | -0.53952
568.9531 | 123.262 | -122.9691 | 0.33875 | 0.048435 | -0.0020317 | -0.0025134 | -0.004424 | -0.054673 | 0.03291 | 0.07176 | -0.012012 | 0.13181 | -0.029655 | 0.073068 | 0.0045899 | 0.21623 | 0.22576 | 0.19761 | 0.27189 | 0.16062 | 0.38921 | 0.07431 | -0.003531 | 0.023253 | -0.033458 | 0.043302 | 0.15107 | -0.16166 | -0.18704 | 123.0434 | -0.066855 | 123.1853 | 123.1667 | 0.1233 | -0.17812 | 0.050466 | 122.782 | -0.29544 | 122.9655 | 122.9356 | 0.15358 | -0.18768 | -0.5004 | 123.2409 | 123.1297 | 123.3583 | 123.1948 | -0.26444 | 123.0124 | 123.1201 | 122.8074 | 122.9923 | -0.52579
569.9375 | 123.2803 | -122.8775 | 0.37994 | 0.078959 | -0.0041687 | -0.0046504 | -0.001219 | -0.052536 | 0.033978 | 0.041238 | -0.010944 | 0.13288 | -0.028587 | 0.070931 | 0.0067259 | 0.24828 | 0.25323 | 0.22508 | 0.3131 | 0.19267 | 0.42584 | 0.07431 | 0.001048 | 0.03241 | -0.038036 | 0.043302 | 0.15564 | -0.12503 | -0.18246 | 122.9518 | -0.066848 | 123.1258 | 123.1026 | 0.15077 | -0.18727 | 0.045895 | 122.695 | -0.33664 | 122.8786 | 122.8395 | 0.14443 | -0.2243 | -0.50497 | 123.1906 | 123.0702 | 123.3033 | 123.1307 | -0.30563 | 122.9208 | 123.0331 | 122.7525 | 122.9099 | -0.56241
570.9375 | 123.3032 | -121.4722 | 1.7853 | 0.063697 | -0.0009637 | -0.0025134 | -0.005492 | -0.051468 | 0.03291 | 0.07176 | -0.010944 | 0.13501 | -0.028587 | 0.072 | 0.0056579 | 1.4616 | 1.4711 | 1.42 | 1.5172 | 1.3878 | 1.6254 | 1.2328 | 0.005626 | 0.03241 | -0.042615 | 0.043302 | 0.14649 | -0.13419 | -0.19162 | 122.7049 | -0.26807 | 122.9337 | 122.8922 | 0.18724 | -0.3975 | -0.15985 | 121.2805 | -1.742 | 121.4778 | 121.4296 | 0.14901 | -1.6388 | -1.9195 | 122.9894 | 122.8599 | 123.0976 | 122.9433 | -0.5525 | 121.5155 | 121.6187 | 121.338 | 121.5046 | -1.9769
571.9375 | 123.2712 | -121.257 | 1.9638 | 0.017911 | 0.0001043 | -0.00037739 | -0.006561 | -0.054673 | 0.035047 | 0.041238 | -0.010944 | 0.13394 | -0.029655 | 0.073068 | 0.0056579 | 1.9423 | 1.9198 | 1.8687 | 2.0025 | 1.8548 | 2.1108 | 1.6907 | 0.001048 | 0.03241 | -0.042615 | 0.038723 | 0.15107 | -0.060928 | -0.17788 | 122.9477 | 0.038715 | 123.1993 | 123.1257 | 0.17802 | -0.10898 | 0.14696 | 121.0791 | -1.9251 | 121.2581 | 121.2144 | 0.13527 | -1.8127 | -2.0247 | 123.2595 | 123.1118 | 123.3678 | 123.1769 | -0.27313 | 121.2957 | 121.4081 | 121.1961 | 121.2894 | -2.1417
572.9375 | 123.2758 | -120.5978 | 2.6321 | 0.048435 | 0.0001043 | 0.00069161 | -0.005492 | -0.053604 | 0.033978 | 0.056499 | -0.010944 | 0.13074 | -0.028587 | 0.070931 | 0.0067259 | 2.5008 | 1.2559 | 1.2094 | 2.5702 | 2.4226 | 2.6694 | 2.2585 | -0.00811 | 0.03241 | -0.033458 | 0.043302 | 0.14649 | -0.10214 | -0.18246 | 122.8563 | -0.0619 | 123.0987 | 121.8073 | -1.049 | -0.20953 | 0.037214 | 120.4154 | -2.5888 | 120.5897 | 120.5644 | 0.14901 | -2.4857 | -2.7343 | 123.1681 | 123.0204 | 123.2672 | 121.8538 | -0.37368 | 120.6411 | 120.7443 | 120.4957 | 120.6302 | -2.8146
573.9531 | 123.3124 | -120.2957 | 2.98 | 0.078959 | 0.0033103 | 0.00069161 | -0.007629 | -0.053604 | 0.033978 | 0.056499 | -0.010944 | 0.13501 | -0.028587 | 0.074136 | 0.0067259 | 2.7572 | 0.95833 | 0.9164 | 2.8449 | 2.7111 | 2.9441 | 2.524 | -0.003531 | 0.027831 | -0.038036 | 0.043302 | 0.15107 | -0.092979 | -0.18704 | 122.8197 | -0.1351 | 123.053 | 121.2121 | -1.6076 | -0.26896 | -0.035971 | 120.1087 | -2.9367 | 120.2922 | 120.2577 | 0.14901 | -2.829 | -3.073 | 123.1407 | 123.0068 | 123.2398 | 121.254 | -0.45601 | 120.339 | 120.4468 | 120.2027 | 120.3235 | -3.1671
574.9375 | 123.3124 | -119.9158 | 3.3417 | 0.063697 | 0.0022413 | -0.00037739 | -0.007629 | -0.054673 | 0.035047 | 0.07176 | -0.012012 | 0.13394 | -0.029655 | 0.074136 | 0.0077949 | 3.1464 | 0.77519 | 0.73327 | 3.2662 | 3.1186 | 3.3561 | 2.9407 | 0.001048 | 0.036989 | -0.038036 | 0.043302 | 0.15564 | -0.14334 | -0.17788 | 122.8565 | -0.075519 | 123.0622 | 120.649 | -2.2074 | -0.22307 | 0.01447 | 119.7379 | -3.2984 | 119.9168 | 119.8777 | 0.13985 | -3.186 | -3.485 | 123.1819 | 123.0344 | 123.2719 | 120.691 | -0.40096 | 119.9591 | 120.0714 | 119.7724 | 119.9528 | -3.5196
575.9531 | 123.3215 | -121.9299 | 1.3138 | 0.033173 | 0.0043783 | -0.0035824 | -0.009766 | -0.053604 | 0.03291 | 0.056499 | -0.010944 | 0.13394 | -0.029655 | 0.075205 | 0.0067259 | 1.1914 | 1.1049 | 1.0766 | 1.2562 | 1.1268 | 1.3736 | 0.96262 | -0.012689 | 0.027831 | -0.028879 | 0.043302 | 0.15107 | -0.12961 | -0.19162 | 122.8926 | -0.057538 | 123.1214 | 123.0066 | 0.11402 | -0.18701 | 0.059828 | 121.7383 | -1.2705 | 121.9172 | 121.9011 | 0.16274 | -1.1627 | -1.4434 | 123.1862 | 123.0567 | 123.3035 | 123.0348 | -0.35116 | 121.9732 | 122.081 | 121.8003 | 121.9578 | -1.5054
576.9375 | 123.317 | -120.4193 | 2.8336 | 0.048435 | 0.0001043 | -0.00037739 | -0.009766 | -0.054673 | 0.035047 | 0.041238 | -0.010944 | 0.13394 | -0.028587 | 0.072 | 0.0056579 | 2.7572 | 0.69278 | 0.65544 | 2.8449 | 2.6882 | 2.9441 | 2.4966 | -0.00811 | 0.036989 | -0.033458 | 0.04788 | 0.16022 | -0.11129 | -0.18246 | 122.9159 | 0.011387 | 123.1765 | 121.0748 | -1.8411 | -0.14537 | 0.11051 | 120.2368 | -2.7857 | 120.4112 | 120.3859 | 0.14901 | -2.6733 | -2.9448 | 123.2643 | 123.1075 | 123.3634 | 121.1121 | -0.33699 | 120.4672 | 120.5795 | 120.308 | 120.4563 | -3.016
577.9375 | 123.2666 | -120.7169 | 2.5269 | 0.033173 | -0.0009637 | 0.00069161 | -0.009766 | -0.055741 | 0.035047 | 0.056499 | -0.0098752 | 0.13394 | -0.030723 | 0.072 | 0.0045899 | 2.2902 | 0.99038 | 1.008 | 2.4146 | 2.2807 | 2.5228 | 1.7181 | -0.00811 | 0.03241 | -0.033458 | 0.04788 | 0.15564 | -0.092979 | -0.19162 | 122.435 | -0.11228 | 123.0071 | 121.7248 | -0.71018 | -0.24619 | -0.004016 | 120.5252 | -2.479 | 120.7087 | 120.6834 | 0.15816 | -2.3712 | -2.6198 | 123.1314 | 122.9975 | 123.2397 | 121.7072 | -0.80871 | 120.7647 | 120.8725 | 120.6239 | 120.7493 | -2.7185
578.9375 | 123.3124 | -120.7489 | 2.4902 | 0.063697 | 0.0011733 | 0.00069161 | -0.009766 | -0.052536 | 0.036115 | 0.025977 | -0.0098752 | 0.13501 | -0.029655 | 0.075205 | 0.0056579 | 1.7958 | 1.0499 | 1.4841 | 2.1857 | 2.0563 | 2.2985 | 1.4663 | 0.001048 | 0.027831 | -0.033458 | 0.043302 | 0.15107 | -0.10214 | -0.18246 | 122.2152 | -0.30458 | 122.5447 | 122.233 | 0.017806 | -0.43394 | -0.19175 | 120.5664 | -2.4469 | 120.7499 | 120.7154 | 0.14901 | -2.3392 | -2.5924 | 122.9346 | 122.8052 | 123.0474 | 121.7988 | -1.0239 | 120.7922 | 120.9 | 120.6468 | 120.7767 | -2.6727
579.9375 | 123.3032 | -119.8105 | 3.4515 | 0.078959 | -0.0052367 | 0.0049646 | -0.008698 | -0.055741 | 0.033978 | 0.056499 | -0.0098752 | 0.13288 | -0.028587 | 0.073068 | 0.0067259 | 3.1006 | 0.57373 | 1.333 | 3.4997 | 3.3567 | 3.608 | 2.6568 | 0.001048 | 0.03241 | -0.0243 | 0.043302 | 0.15564 | -0.083821 | -0.17331 | 122.4673 | 0.048116 | 122.9111 | 121.1435 | -1.3238 | -0.094827 | 0.15643 | 119.6372 | -3.4082 | 119.8115 | 119.7862 | 0.14901 | -3.2959 | -3.5354 | 123.3101 | 123.1672 | 123.4185 | 120.3842 | -0.79471 | 119.8538 | 119.9661 | 119.7267 | 119.8429 | -3.6248
580.9375 | 123.2849 | -119.7235 | 3.566 | 0.078959 | -0.0063057 | 0.0049646 | -0.008698 | -0.056809 | 0.035047 | 0.087021 | -0.0098752 | 0.13288 | -0.031791 | 0.073068 | 0.0056579 | 2.6611 | 0.60578 | 0.58677 | 3.1975 | 3.0591 | 3.2966 | 2.2859 | 0.001048 | 0.03241 | -0.028879 | 0.043302 | 0.15107 | -0.11587 | -0.18704 | 122.0094 | -0.3685 | 122.3846 | 120.3103 | -1.6992 | -0.5069 | -0.26936 | 119.5365 | -3.5227 | 119.7246 | 119.6946 | 0.15816 | -3.4149 | -3.6819 | 122.921 | 122.7826 | 123.0201 | 120.3293 | -1.28 | 119.7668 | 119.8746 | 119.6076 | 119.7559 | -3.753
581.9375 | 123.3307 | -119.989 | 3.273 | 0.063697 | -0.0031007 | 0.0017596 | -0.007629 | -0.054673 | 0.035047 | 0.041238 | -0.010944 | 0.13608 | -0.029655 | 0.074136 | 0.0056579 | 2.162 | 0.49132 | 0.46315 | 3.2478 | 3.114 | 3.3653 | 1.7365 | 0.001048 | 0.027831 | -0.033458 | 0.04788 | 0.15107 | -0.16624 | -0.17788 | 121.7255 | -0.025168 | 122.1511 | 120.4522 | -1.2733 | -0.15898 | 0.092292 | 119.8111 | -3.2251 | 119.9901 | 119.9556 | 0.14443 | -3.1219 | -3.4392 | 123.2369 | 123.103 | 123.3543 | 120.4803 | -1.5366 | 120.0369 | 120.1401 | 119.8228 | 120.0168 | -3.4509
582.9531 | 123.2849 | -119.8746 | 3.3691 | 0.048435 | -0.0009637 | 0.00069161 | -0.007629 | -0.054673 | 0.035047 | 0.041238 | -0.010944 | 0.13288 | -0.029655 | 0.075205 | 0.0056579 | 2.3131 | 0.41348 | 0.3899 | 3.1471 | 3.0041 | 3.2463 | 1.9883 | -0.003531 | 0.027831 | -0.028879 | 0.04788 | 0.14649 | -0.1525 | -0.18246 | 121.8629 | -0.22202 | 122.1877 | 120.2645 | -1.5984 | -0.36501 | -0.12288 | 119.6921 | -3.3213 | 119.871 | 119.8457 | 0.15358 | -3.2227 | -3.5216 | 123.0217 | 122.8787 | 123.1208 | 120.2881 | -1.3808 | 119.9225 | 120.0211 | 119.7221 | 119.9024 | -3.5516
583.9375 | 123.2803 | -121.9116 | 1.3321 | 0.048435 | -0.0052367 | -0.0035824 | -0.003356 | -0.053604 | 0.033978 | 0.07176 | -0.0098752 | 0.13394 | -0.029655 | 0.074136 | 0.0056579 | 1.1456 | 0.91255 | 0.8752 | 1.27 | 1.1314 | 1.3828 | 0.95346 | 0.001048 | 0.03241 | -0.028879 | 0.04788 | 0.15564 | -0.16166 | -0.17788 | 122.8651 | -0.062113 | 123.0573 | 122.7868 | -0.078265 | -0.20074 | 0.050675 | 121.7337 | -1.2842 | 121.9127 | 121.8827 | 0.14901 | -1.1764 | -1.4938 | 123.1816 | 123.043 | 123.2944 | 122.8242 | -0.37863 | 121.9595 | 122.0673 | 121.75 | 121.944 | -1.51
584.9375 | 123.2849 | -121.1746 | 2.1149 | 0.063697 | -0.0020317 | 0.00069161 | -0.004424 | -0.053604 | 0.033978 | 0.025977 | -0.0098752 | 0.13288 | -0.029655 | 0.073068 | 0.0045899 | 1.5257 | 0.6882 | 0.6646 | 2.204 | 2.0655 | 2.3122 | 1.2282 | -0.003531 | 0.036989 | -0.028879 | 0.04788 | 0.15107 | -0.13419 | -0.18246 | 122.4028 | 0.089102 | 122.7003 | 121.8392 | -0.5636 | -0.049414 | 0.19736 | 120.9922 | -2.067 | 121.1711 | 121.1457 | 0.15358 | -1.9638 | -2.2491 | 123.3786 | 123.2401 | 123.4868 | 121.8628 | -0.88667 | 121.2225 | 121.3257 | 121.0404 | 121.2116 | -2.2973
585.9375 | 123.2941 | -121.431 | 1.8219 | 0.048435 | -0.0073737 | -0.00037739 | -0.005492 | -0.053604 | 0.03291 | 0.041238 | -0.010944 | 0.13181 | -0.029655 | 0.076273 | 0.0056579 | 1.2509 | 0.72025 | 0.67375 | 1.8102 | 1.6671 | 1.9185 | 0.96262 | 0.001048 | 0.023253 | -0.033458 | 0.043302 | 0.15564 | -0.097557 | -0.17788 | 122.3936 | -0.01167 | 122.6819 | 122.1047 | -0.28887 | -0.15481 | 0.096565 | 121.2531 | -1.7786 | 121.432 | 121.3975 | 0.14443 | -1.6663 | -1.9195 | 123.2412 | 123.0981 | 123.3494 | 122.1512 | -0.85928 | 121.4743 | 121.5866 | 121.3334 | 121.4542 | -1.9998
586.9375 | 123.2803 | -121.1243 | 2.1881 | 0.063697 | -0.0031007 | -0.00037739 | -0.005492 | -0.054673 | 0.031842 | 0.056499 | -0.010944 | 0.13501 | -0.028587 | 0.073068 | 0.0056579 | 1.7408 | 0.56915 | 0.53641 | 1.8789 | 1.7449 | 1.9917 | 1.4984 | -0.003531 | 0.036989 | -0.038036 | 0.04788 | 0.15564 | -0.12961 | -0.18246 | 122.6226 | -0.30921 | 122.8651 | 121.6607 | -0.96195 | -0.44318 | -0.19639 | 120.9418 | -2.1402 | 121.1207 | 121.0862 | 0.14443 | -2.0325 | -2.3177 | 123.0032 | 122.8692 | 123.116 | 121.6934 | -0.68975 | 121.1721 | 121.2799 | 120.9947 | 121.1613 | -2.3706
587.9531 | 123.4085 | -120.7306 | 2.4765 | 0.033173 | -0.0031007 | 0.00069161 | -0.009766 | -0.055741 | 0.035047 | 0.07176 | -0.0098752 | 0.13288 | -0.029655 | 0.074136 | 0.0067259 | 1.9377 | 0.43179 | 0.3899 | 2.5199 | 2.386 | 2.6419 | 1.6403 | -0.00811 | 0.023253 | -0.033458 | 0.052459 | 0.15107 | -0.12961 | -0.17788 | 122.3709 | 0.043378 | 122.6683 | 121.1205 | -1.2504 | -0.090522 | 0.16538 | 120.5527 | -2.424 | 120.7225 | 120.6971 | 0.14443 | -2.3254 | -2.6061 | 123.2505 | 123.1166 | 123.3725 | 121.1624 | -0.8362 | 120.7831 | 120.8817 | 120.601 | 120.7538 | -2.6544
588.9375 | 123.3215 | -120.5154 | 2.7054 | 0.078959 | -0.0073737 | 0.0038966 | -0.006561 | -0.054673 | 0.03291 | 0.056499 | -0.012012 | 0.13181 | -0.029655 | 0.077342 | 0.0056579 | 2.2857 | 0.31733 | 0.2846 | 2.5977 | 2.4776 | 2.7106 | 1.9242 | -0.003531 | 0.036989 | -0.028879 | 0.04788 | 0.15107 | -0.17081 | -0.18246 | 122.4396 | -0.10767 | 122.8011 | 120.8 | -1.6396 | -0.22783 | 0.005179 | 120.333 | -2.6575 | 120.5119 | 120.4866 | 0.15358 | -2.5543 | -2.8762 | 123.1132 | 122.993 | 123.226 | 120.8328 | -0.78119 | 120.5633 | 120.6665 | 120.3446 | 120.5524 | -2.8878
589.9531 | 123.3032 | -120.9641 | 2.2751 | 0.048435 | -0.0084417 | 0.0060336 | -0.009766 | -0.055741 | 0.033978 | 0.056499 | -0.010944 | 0.13074 | -0.028587 | 0.077342 | 0.0045899 | 2.1346 | 0.36312 | 0.31665 | 2.2269 | 2.0883 | 2.3351 | 1.7456 | -0.003531 | 0.036989 | -0.033458 | 0.04788 | 0.15107 | -0.12045 | -0.17788 | 122.7097 | -0.048223 | 123.0986 | 121.2807 | -1.429 | -0.18674 | 0.060032 | 120.7862 | -2.2272 | 120.9605 | 120.9306 | 0.14443 | -2.124 | -2.3955 | 123.1909 | 123.0524 | 123.2992 | 121.3272 | -0.52947 | 121.0119 | 121.1151 | 120.8436 | 121.001 | -2.453
590.9375 | 123.2941 | -122.2916 | 0.97504 | 0.048435 | -0.0073737 | -0.00037739 | -0.004424 | -0.053604 | 0.031842 | 0.056499 | -0.012012 | 0.13288 | -0.029655 | 0.074136 | 0.0056579 | 0.91215 | 0.61036 | 0.57303 | 0.97696 | 0.8383 | 1.0943 | 0.61004 | 0.001048 | 0.036989 | -0.033458 | 0.043302 | 0.15107 | -0.16166 | -0.18246 | 122.9016 | 0.001925 | 123.2037 | 122.8646 | -0.037013 | -0.13674 | 0.11928 | 122.1091 | -0.93174 | 122.2926 | 122.2581 | 0.14901 | -0.82397 | -1.1367 | 123.2685 | 123.1299 | 123.3859 | 122.9019 | -0.36499 | 122.3349 | 122.4426 | 122.1299 | 122.3286 | -1.1575
591.9375 | 123.2895 | -121.1884 | 2.0782 | 0.063697 | -0.0084417 | 0.0049646 | -0.009766 | -0.053604 | 0.033978 | 0.07176 | -0.012012 | 0.13288 | -0.028587 | 0.076273 | 0.0067259 | 1.9423 | 0.30359 | 0.27087 | 2.03 | 1.8915 | 2.1337 | 1.535 | -0.00811 | 0.03241 | -0.042615 | 0.052459 | 0.15107 | -0.14334 | -0.18246 | 122.7233 | -0.048256 | 123.1306 | 121.4592 | -1.2641 | -0.18679 | 0.055411 | 121.0059 | -2.0258 | 121.1802 | 121.1457 | 0.13985 | -1.9272 | -2.2216 | 123.2183 | 123.0798 | 123.322 | 121.4919 | -0.54326 | 121.2408 | 121.3394 | 121.045 | 121.2208 | -2.2607
592.9375 | 123.2895 | -121.3943 | 1.8814 | 0.048435 | -0.0084417 | 0.0028286 | -0.005492 | -0.053604 | 0.03291 | 0.041238 | -0.010944 | 0.13288 | -0.029655 | 0.077342 | 0.0045899 | 1.6218 | 0.41348 | 0.38074 | 1.7003 | 1.5664 | 1.8132 | 1.2236 | 0.005626 | 0.036989 | -0.028879 | 0.04788 | 0.17396 | -0.12961 | -0.17788 | 122.618 | -0.18106 | 123.0161 | 121.7751 | -0.84288 | -0.31506 | -0.068253 | 121.2165 | -1.8335 | 121.4 | 121.3655 | 0.14901 | -1.7075 | -2.011 | 123.0947 | 122.9607 | 123.2075 | 121.8078 | -0.65779 | 121.4422 | 121.5683 | 121.2647 | 121.4313 | -2.0593
593.9375 | 123.2666 | -121.5546 | 1.7212 | 0.063697 | -0.0073737 | 0.0038966 | -0.007629 | -0.054673 | 0.033978 | 0.07176 | -0.010944 | 0.13288 | -0.029655 | 0.074136 | 0.0067259 | 1.6081 | 0.36769 | 0.33496 | 1.6912 | 1.548 | 1.7994 | 1.2374 | -0.003531 | 0.03241 | -0.033458 | 0.04788 | 0.15564 | -0.083821 | -0.18704 | 122.7919 | -0.03 | 123.1626 | 121.8895 | -0.9024 | -0.17316 | 0.078229 | 121.3675 | -1.6733 | 121.551 | 121.5211 | 0.15358 | -1.5655 | -1.805 | 123.2458 | 123.1026 | 123.354 | 121.9223 | -0.48383 | 121.6024 | 121.7102 | 121.4707 | 121.587 | -1.9082
594.9531 | 123.3948 | -121.6461 | 1.6022 | 0.063697 | -0.0073737 | 0.0038966 | -0.008698 | -0.052536 | 0.033978 | 0.056499 | -0.0098752 | 0.13394 | -0.027518 | 0.074136 | 0.0067259 | 1.4799 | 0.37685 | 0.33496 | 1.5584 | 1.4152 | 1.6712 | 1.1229 | -0.00811 | 0.036989 | -0.028879 | 0.043302 | 0.15107 | -0.12961 | -0.18246 | 122.769 | -0.043756 | 123.126 | 121.9811 | -0.78792 | -0.18693 | 0.069046 | 121.4637 | -1.5589 | 121.638 | 121.6172 | 0.15358 | -1.4511 | -1.7318 | 123.2045 | 123.0614 | 123.3173 | 122.023 | -0.47929 | 121.6894 | 121.7972 | 121.5165 | 121.6831 | -1.7846
595.9375 | 123.2849 | -121.756 | 1.561 | 0.048435 | -0.0063057 | 0.0049646 | -0.006561 | -0.053604 | 0.033978 | 0.041238 | -0.012012 | 0.13181 | -0.027518 | 0.075205 | 0.0056579 | 1.4249 | 0.35396 | 0.31207 | 1.5081 | 1.3786 | 1.6209 | 1.0725 | -0.012689 | 0.041567 | -0.0243 | 0.043302 | 0.16022 | -0.11587 | -0.18246 | 122.8285 | -0.052919 | 123.1809 | 122.0681 | -0.76045 | -0.18236 | 0.059881 | 121.5735 | -1.5177 | 121.7433 | 121.7317 | 0.15816 | -1.4008 | -1.6768 | 123.264 | 123.1346 | 123.3768 | 122.1099 | -0.48846 | 121.7993 | 121.9162 | 121.6401 | 121.7975 | -1.7434
596.9375 | 123.3582 | -121.7331 | 1.5015 | 0.063697 | -0.0073737 | 0.0028286 | -0.008698 | -0.053604 | 0.031842 | 0.056499 | -0.0098752 | 0.13181 | -0.028587 | 0.077342 | 0.0056579 | 1.3288 | 0.34938 | 0.31665 | 1.4394 | 1.3008 | 1.5384 | 0.97178 | -0.012689 | 0.041567 | -0.0243 | 0.052459 | 0.14649 | -0.12961 | -0.18704 | 122.7049 | -0.062086 | 123.0619 | 122.0497 | -0.65513 | -0.20069 | 0.036975 | 121.546 | -1.449 | 121.7204 | 121.7088 | 0.16274 | -1.355 | -1.6311 | 123.1725 | 123.0339 | 123.2715 | 122.0825 | -0.52969 | 121.7856 | 121.8796 | 121.6035 | 121.7747 | -1.6885
597.9375 | 123.3215 | -121.7926 | 1.4648 | 0.048435 | -0.0084417 | 0.0038966 | -0.007629 | -0.052536 | 0.035047 | 0.056499 | -0.010944 | 0.13288 | -0.028587 | 0.07841 | 0.0045899 | 1.3242 | 0.31275 | 0.2846 | 1.4348 | 1.2825 | 1.5384 | 0.9672 | -0.00811 | 0.036989 | -0.0243 | 0.052459 | 0.15564 | -0.15708 | -0.16873 | 122.7598 | -0.030043 | 123.1168 | 122.0772 | -0.6826 | -0.18239 | 0.073596 | 121.6239 | -1.4124 | 121.7845 | 121.7683 | 0.14443 | -1.3092 | -1.6219 | 123.2274 | 123.0751 | 123.331 | 122.1054 | -0.49764 | 121.8451 | 121.9482 | 121.6355 | 121.8296 | -1.6336
598.9375 | 123.317 | -121.9299 | 1.3733 | 0.078959 | -0.0073737 | 0.0028286 | -0.007629 | -0.053604 | 0.036115 | 0.056499 | -0.0088072 | 0.13394 | -0.027518 | 0.077342 | 0.0045899 | 1.1731 | 0.34022 | 0.30749 | 1.2883 | 1.1542 | 1.3965 | 0.82525 | -0.00811 | 0.041567 | -0.015143 | 0.04788 | 0.15564 | -0.16624 | -0.18246 | 122.7552 | -0.084999 | 123.103 | 122.2374 | -0.51776 | -0.21904 | 0.023212 | 121.7475 | -1.3254 | 121.9218 | 121.9148 | 0.16732 | -1.2176 | -1.5395 | 123.2182 | 123.0842 | 123.3264 | 122.2702 | -0.54804 | 121.9778 | 122.0856 | 121.7637 | 121.9715 | -1.5558
599.9531 | 123.2895 | -121.9666 | 1.3275 | 0.048435 | -0.0073737 | 0.0038966 | -0.008698 | -0.055741 | 0.033978 | 0.041238 | -0.0088072 | 0.13394 | -0.029655 | 0.075205 | 0.0067259 | 1.2281 | 0.26697 | 0.22508 | 1.3844 | 1.2412 | 1.4927 | 0.78862 | -0.003531 | 0.03241 | -0.015143 | 0.043302 | 0.15564 | -0.16624 | -0.18246 | 122.7552 | 0.056924 | 123.1946 | 122.1916 | -0.56354 | -0.086267 | 0.16514 | 121.7841 | -1.2842 | 121.963 | 121.9514 | 0.16732 | -1.1719 | -1.4938 | 123.351 | 123.2078 | 123.4592 | 122.2335 | -0.53889 | 122.0099 | 122.1222 | 121.8003 | 121.999 | -1.51
600.9375 | 123.4085 | -121.7285 | 1.4648 | 0.048435 | -0.0073737 | 0.0060336 | -0.008698 | -0.052536 | 0.035047 | 0.056499 | -0.010944 | 0.13288 | -0.030723 | 0.076273 | 0.0067259 | 1.2967 | 0.19371 | 0.15641 | 1.4348 | 1.3008 | 1.543 | 0.91683 | -0.00811 | 0.036989 | -0.0243 | 0.043302 | 0.15107 | -0.17081 | -0.18704 | 122.6453 | -0.030043 | 123.0252 | 121.8849 | -0.76042 | -0.16407 | 0.078174 | 121.5415 | -1.4215 | 121.7204 | 121.7042 | 0.16274 | -1.3138 | -1.6357 | 123.1633 | 123.0293 | 123.2715 | 121.9222 | -0.54801 | 121.7718 | 121.8796 | 121.5577 | 121.7655 | -1.6519

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2
-0.1677 | 21.4941 | 20.56 | 20.6681
0.8323 | 21.4906 | 20.5617 | 20.6727
1.8323 | 21.4904 | 20.5598 | 20.6722
2.8323 | 21.5587 | 20.5585 | 20.6683
3.8323 | 22.0433 | 20.5652 | 20.6766
4.8323 | 23.2334 | 20.5676 | 20.6736
5.8323 | 25.1288 | 20.5588 | 20.6587
6.8323 | 27.671 | 20.5542 | 20.6737
7.8323 | 30.7085 | 20.561 | 20.6793
8.8323 | 34.2041 | 20.5612 | 20.6869
9.8323 | 38.071 | 20.5696 | 20.6836
10.8323 | 42.2453 | 20.5766 | 20.699
11.8323 | 46.6506 | 20.587 | 20.7148
12.8323 | 51.2455 | 20.5889 | 20.7264
13.8323 | 56.03 | 20.6092 | 20.7605
14.8323 | 61.0424 | 20.6246 | 20.788
15.8323 | 66.2384 | 20.6499 | 20.8273
16.8323 | 71.4784 | 20.6646 | 20.8661
17.8323 | 76.8916 | 20.6981 | 20.9298
18.8323 | 82.4414 | 20.739 | 20.9842
19.8323 | 88.0241 | 20.7811 | 21.0533
20.8323 | 93.7578 | 20.8176 | 21.1249
21.8323 | 99.5245 | 20.872 | 21.2059
22.8323 | 105.4188 | 20.9314 | 21.2987
23.8323 | 111.3775 | 20.9967 | 21.4033
24.8323 | 117.3557 | 21.0691 | 21.5202
25.8323 | 123.4049 | 21.1451 | 21.6478
26.8323 | 129.5201 | 21.2365 | 21.7854
27.8323 | 135.626 | 21.3357 | 21.9389
28.8323 | 141.7615 | 21.4377 | 22.1145
29.8323 | 147.8473 | 21.5558 | 22.2948
30.8323 | 153.9402 | 21.6865 | 22.4939
31.8323 | 160.019 | 21.8185 | 22.7084
32.8323 | 166.0489 | 21.9753 | 22.9305
33.8323 | 172.1233 | 22.132 | 23.1724
34.8323 | 178.0287 | 22.3047 | 23.4262
35.8323 | 184.0834 | 22.4901 | 23.7152
36.8323 | 190.1324 | 22.6826 | 24.0143
37.8323 | 195.9814 | 22.9026 | 24.3368
38.8323 | 201.9077 | 23.1274 | 24.6641
39.8323 | 207.9381 | 23.3673 | 25.0169
40.8323 | 213.9372 | 23.6155 | 25.3949
41.8323 | 219.8551 | 23.8852 | 25.796
42.8323 | 225.7659 | 24.1724 | 26.2108
43.8323 | 231.5843 | 24.4718 | 26.6482
44.8323 | 237.4195 | 24.7809 | 27.1105
45.8323 | 243.385 | 25.117 | 27.5757
46.8323 | 249.2164 | 25.4678 | 28.0787
47.8323 | 254.9522 | 25.8317 | 28.5851
48.8323 | 260.8164 | 26.2078 | 29.1271
49.8323 | 266.5952 | 26.6 | 29.6943
50.8323 | 272.5081 | 27.0158 | 30.2624
51.8323 | 278.3355 | 27.4446 | 30.8617
52.8323 | 284.0473 | 27.9127 | 31.4737
53.8323 | 289.7538 | 28.3708 | 32.1103
54.8323 | 295.4282 | 28.8475 | 32.7639
55.8323 | 301.0705 | 29.3496 | 33.4355
56.8323 | 306.6714 | 29.8601 | 34.1425
57.8323 | 312.1973 | 30.3922 | 34.8648
58.8323 | 317.719 | 30.9383 | 35.6187
59.8323 | 323.1326 | 31.5058 | 36.389
60.8323 | 328.4671 | 32.0915 | 37.1753
61.8323 | 333.9412 | 32.6904 | 37.9955
62.8323 | 339.3572 | 33.3138 | 38.8317
63.8323 | 344.7333 | 33.9568 | 39.7033
64.8323 | 350.2138 | 34.6096 | 40.6092
65.8323 | 355.6217 | 35.2835 | 41.5371
66.8323 | 360.8268 | 35.9825 | 42.4869
67.8323 | 366.1 | 36.6966 | 43.4542
68.8323 | 371.2277 | 37.4447 | 44.4435
69.8323 | 376.5023 | 38.1836 | 45.4427
70.8323 | 381.7558 | 38.9508 | 46.4564
71.8323 | 387.0578 | 39.7382 | 47.5037
72.8323 | 392.0866 | 40.5451 | 48.5633
73.8323 | 397.1216 | 41.3761 | 49.656
74.8323 | 402.3152 | 42.2355 | 50.7789
75.8323 | 407.4171 | 43.1252 | 51.9255
76.8323 | 412.3879 | 44.0411 | 53.1179
77.8323 | 417.2695 | 44.9941 | 54.3537
78.8323 | 422.0488 | 45.9783 | 55.6155
79.8323 | 426.9452 | 47.0021 | 56.9501
80.8323 | 431.9043 | 48.0533 | 58.3011
81.8323 | 436.4524 | 49.1219 | 59.6931
82.8323 | 440.5782 | 50.2251 | 61.1171
83.8323 | 444.3442 | 51.3567 | 62.5775
84.8323 | 447.7751 | 52.5038 | 64.0633
85.8323 | 450.9358 | 53.6642 | 65.5658
86.8323 | 453.9631 | 54.8512 | 67.1119
87.8323 | 456.937 | 56.0593 | 68.6451
88.8323 | 459.735 | 57.2718 | 70.1899
89.8479 | 462.1661 | 58.5119 | 71.7293
90.8323 | 464.5521 | 59.7529 | 73.2876
91.8323 | 466.9416 | 61.0037 | 74.8463
92.8479 | 469.1132 | 62.2764 | 76.4248
93.8323 | 470.9562 | 63.5494 | 77.9888
94.8323 | 472.5507 | 64.8367 | 79.5541
95.8323 | 473.8245 | 66.1234 | 81.136
96.8323 | 474.9877 | 67.4286 | 82.7072
97.8323 | 475.9588 | 68.7293 | 84.2919
98.8323 | 476.6811 | 70.0271 | 85.8851
99.8323 | 477.1649 | 71.3208 | 87.4437
100.8323 | 477.4818 | 72.6264 | 89.0032
101.8323 | 477.5607 | 73.9237 | 90.5413
102.8323 | 477.5876 | 75.2304 | 92.0685
103.8479 | 477.5595 | 76.5294 | 93.5875
104.8323 | 477.374 | 77.8101 | 95.1068
105.8323 | 477.203 | 79.0973 | 96.5808
106.8323 | 476.9343 | 80.3725 | 98.0494
107.8323 | 476.7067 | 81.6466 | 99.5073
108.8323 | 476.4047 | 82.9156 | 100.9484
109.8323 | 476.0694 | 84.1819 | 102.363
110.8323 | 475.7403 | 85.4512 | 103.7875
111.8323 | 475.3237 | 86.697 | 105.1712
112.8323 | 474.9402 | 87.9432 | 106.5514
113.8323 | 474.5446 | 89.184 | 107.8979
114.8323 | 474.1921 | 90.4068 | 109.233
115.8323 | 473.7885 | 91.626 | 110.5589
116.8323 | 473.4471 | 92.8414 | 111.8607
117.8323 | 473.159 | 94.0421 | 113.1574
118.8323 | 473.0368 | 95.2305 | 114.4219
119.8323 | 472.9195 | 96.4217 | 115.6652
120.8323 | 472.7726 | 97.5882 | 116.9024
121.8323 | 472.6732 | 98.7667 | 118.1193
122.8323 | 472.6041 | 99.9225 | 119.3154
123.8323 | 472.5531 | 101.088 | 120.504
124.8323 | 472.5564 | 102.2335 | 121.6792
125.8323 | 472.5551 | 103.3777 | 122.8414
126.8323 | 472.6168 | 104.523 | 123.9879
127.8323 | 472.7555 | 105.659 | 125.1277
128.8323 | 472.8805 | 106.7715 | 126.2523
129.8323 | 472.9625 | 107.8891 | 127.3718
130.8323 | 473.09 | 109.0039 | 128.4816
131.8323 | 473.325 | 110.1031 | 129.5707
132.8323 | 473.5175 | 111.2149 | 130.6519
133.8479 | 473.6595 | 112.3151 | 131.7214
134.8323 | 473.9102 | 113.4194 | 132.7793
135.8323 | 474.1162 | 114.4981 | 133.8193
136.8323 | 474.2763 | 115.5697 | 134.8644
137.8323 | 474.4699 | 116.6493 | 135.884
138.8323 | 474.8043 | 117.721 | 136.904
139.8323 | 475.1047 | 118.774 | 137.9087
140.8323 | 475.2973 | 119.8228 | 138.9105
141.8323 | 475.5236 | 120.8836 | 139.9136
142.8323 | 475.8711 | 121.929 | 140.8944
143.8323 | 476.0907 | 122.9759 | 141.891
144.8323 | 476.2095 | 124.0107 | 142.8688
145.8323 | 476.2948 | 125.0395 | 143.8328
146.8323 | 476.4816 | 126.0502 | 144.7937
147.8323 | 476.6285 | 127.0717 | 145.7499
148.8323 | 476.8536 | 128.0738 | 146.7007
149.8323 | 477.1192 | 129.0671 | 147.6427
150.8323 | 477.3255 | 130.0529 | 148.591
151.8323 | 477.3589 | 131.0205 | 149.5248
152.8323 | 477.4688 | 131.9892 | 150.4577
153.8323 | 477.46 | 132.9425 | 151.396
154.8323 | 477.3856 | 133.8952 | 152.326
155.8323 | 477.389 | 134.8221 | 153.254
156.8323 | 477.4095 | 135.7521 | 154.1792
157.8323 | 477.4578 | 136.6654 | 155.1
158.8323 | 477.3778 | 137.564 | 156.0208
159.8323 | 477.4963 | 138.4569 | 156.9301
160.8323 | 477.5376 | 139.3477 | 157.8373
161.8323 | 477.4563 | 140.2178 | 158.7466
162.8323 | 477.4781 | 141.1066 | 159.6524
163.8323 | 477.6064 | 141.9827 | 160.557
164.8323 | 477.6511 | 142.8236 | 161.476
165.8323 | 477.6178 | 143.6667 | 162.3709
166.8323 | 477.5825 | 144.5072 | 163.254
167.8323 | 477.5038 | 145.3483 | 164.1369
168.8323 | 477.5244 | 146.1769 | 165.0112
169.8323 | 477.6427 | 147.0104 | 165.8788
170.8323 | 477.7542 | 147.8565 | 166.7364
171.8323 | 477.8384 | 148.6979 | 167.5943
172.8323 | 477.944 | 149.5571 | 168.4507
173.8323 | 478.0687 | 150.4034 | 169.3061
174.8323 | 478.1558 | 151.2536 | 170.1529
175.8323 | 478.1161 | 152.1389 | 171.02
176.8323 | 478.2106 | 152.9725 | 171.8722
177.8323 | 478.2468 | 153.8549 | 172.7134
178.8323 | 478.1319 | 154.7113 | 173.5665
179.8323 | 478.078 | 155.5664 | 174.406
180.8323 | 478.0177 | 156.4278 | 175.2427
181.8323 | 478.0374 | 157.2886 | 176.0785
182.8323 | 478.1051 | 158.1483 | 176.9185
183.8323 | 478.0813 | 158.9991 | 177.7683
184.8323 | 478.0159 | 159.8753 | 178.6149
185.8323 | 477.8259 | 160.74 | 179.4568
186.8323 | 477.8014 | 161.6187 | 180.3071
187.8323 | 477.7674 | 162.4959 | 181.1805
188.8323 | 477.9013 | 163.369 | 182.045
189.8323 | 477.8905 | 164.2656 | 182.9083
190.8323 | 478.0056 | 165.1461 | 183.7668
191.8323 | 478.0214 | 166.023 | 184.6228
192.8323 | 477.9634 | 166.9114 | 185.4929
193.8479 | 478.0413 | 167.7908 | 186.3668
194.8323 | 478.0171 | 168.6767 | 187.2404
195.8323 | 477.87 | 169.5582 | 188.1043
196.8323 | 477.8085 | 170.444 | 188.9674
197.8323 | 477.7154 | 171.3488 | 189.8464
198.8323 | 477.7108 | 172.2333 | 190.7119
199.8323 | 477.6914 | 173.1285 | 191.5676
200.8323 | 477.6795 | 174.0102 | 192.4188
201.8323 | 477.5898 | 174.8998 | 193.2624
202.8323 | 477.5752 | 175.796 | 194.1066
203.8323 | 477.5356 | 176.676 | 194.9611
204.8323 | 477.4778 | 177.5717 | 195.8015
205.8323 | 477.4466 | 178.4632 | 196.6559
206.8323 | 477.4648 | 179.3497 | 197.4971
207.8323 | 477.5584 | 180.2492 | 198.3444
208.8323 | 477.5024 | 181.1632 | 199.1839
209.8323 | 477.5805 | 182.0508 | 200.0242
210.8323 | 477.6513 | 182.95 | 200.881
211.8323 | 477.7634 | 183.8383 | 201.7116
212.8323 | 477.7675 | 184.749 | 202.5546
213.8323 | 477.7806 | 185.6425 | 203.3877
214.8323 | 477.6565 | 186.5379 | 204.2195
215.8323 | 477.6123 | 187.4344 | 205.0562
216.8323 | 477.5324 | 188.324 | 205.8774
217.8323 | 477.573 | 189.2255 | 206.7065
218.8323 | 477.5702 | 190.1162 | 207.5145
219.8323 | 477.3743 | 191.0221 | 208.3299
220.8323 | 477.2897 | 191.9115 | 209.1462
221.8323 | 477.3203 | 192.8084 | 209.9565
222.8323 | 477.1551 | 193.6931 | 210.7707
223.8323 | 477.199 | 194.593 | 211.5724
224.8323 | 477.3255 | 195.4689 | 212.3684
225.8323 | 477.4009 | 196.3493 | 213.1716
226.8323 | 477.4021 | 197.2318 | 213.9638
227.8323 | 477.3415 | 198.1118 | 214.7565
228.8323 | 477.4486 | 198.9719 | 215.5396
229.8323 | 477.4816 | 199.8354 | 216.3272
230.8323 | 477.3494 | 200.6992 | 217.098
231.8323 | 477.2622 | 201.5591 | 217.8827
232.8323 | 477.2796 | 202.3977 | 218.6529
233.8323 | 477.3083 | 203.2408 | 219.4268
234.8323 | 477.3057 | 204.0361 | 220.2133
235.8323 | 477.2102 | 204.8391 | 220.98
236.8323 | 477.11 | 205.6641 | 221.7598
237.8323 | 477.0124 | 206.5022 | 222.5445
238.8323 | 476.9925 | 207.3297 | 223.3198
239.8323 | 476.9953 | 208.1155 | 224.1071
240.8323 | 477.0054 | 208.8507 | 225.0024
241.8323 | 477.0832 | 209.4379 | 225.8517
242.8323 | 477.1081 | 209.8895 | 226.6478
243.8323 | 477.1171 | 210.3333 | 227.4769
244.8323 | 477.1716 | 210.7262 | 228.3575
245.8323 | 477.2642 | 211.0765 | 229.2396
246.8323 | 477.2531 | 211.1354 | 230.1087
247.8323 | 477.2209 | 210.8438 | 230.9442
248.8323 | 477.1087 | 210.4211 | 231.7982
249.8323 | 477.1394 | 210.0064 | 232.6485
250.8323 | 477.2312 | 209.693 | 233.4675
251.8323 | 477.2884 | 209.5228 | 234.2688
252.8323 | 477.2738 | 209.4843 | 235.0448
253.8323 | 477.2194 | 209.5581 | 235.8512
254.8323 | 477.2149 | 209.7043 | 236.6986
255.8323 | 477.1776 | 209.9294 | 237.645
256.8323 | 477.1762 | 210.1971 | 238.6775
257.8323 | 477.1472 | 210.486 | 239.6654
258.8323 | 477.0948 | 210.8123 | 240.713
259.8323 | 477.0295 | 211.1462 | 241.7559
260.8323 | 476.9822 | 211.5049 | 242.7644
261.8323 | 476.9146 | 211.8731 | 243.7012
262.8323 | 476.8362 | 212.2697 | 244.5763
263.8323 | 476.8018 | 212.7204 | 245.5827
264.8323 | 476.8901 | 213.1946 | 246.7487
265.8323 | 476.8886 | 213.6609 | 248.0577
266.8323 | 476.9018 | 214.1278 | 249.1494
267.8323 | 476.871 | 214.5616 | 250.2689
268.8323 | 476.7723 | 214.9837 | 251.1038
269.8323 | 476.6491 | 215.4089 | 251.8798
270.8323 | 476.496 | 215.8032 | 252.5855
271.8323 | 476.4531 | 216.2035 | 253.3547
272.8323 | 476.39 | 216.5786 | 253.9962
273.8323 | 476.3152 | 216.9376 | 254.5928
274.8323 | 476.3491 | 217.2964 | 255.1396
275.8323 | 476.6359 | 217.649 | 255.7456
276.8323 | 476.9462 | 218.0275 | 256.1965
277.8323 | 477.4897 | 218.4174 | 256.5951
278.8323 | 478.0519 | 218.822 | 257.118
279.8323 | 478.4959 | 219.2492 | 257.6699
280.8323 | 478.9033 | 219.6931 | 258.2603
281.8323 | 479.072 | 220.181 | 258.9663
282.8323 | 479.0241 | 220.695 | 259.5178
283.8323 | 478.998 | 221.3024 | 259.1723
284.8323 | 478.9811 | 222.0145 | 260.3343
285.8323 | 478.7888 | 222.7555 | 261.1072
286.8323 | 478.6129 | 223.5616 | 261.5535
287.8323 | 478.39 | 225.4043 | 262.1282
288.8323 | 478.098 | 226.296 | 262.5561
289.8323 | 477.7385 | 227.3118 | 262.2925
290.8323 | 477.258 | 228.4199 | 261.7745
291.8323 | 476.7785 | 229.4759 | 261.6052
292.8323 | 476.2244 | 230.5869 | 261.6019
293.8323 | 475.6151 | 231.7682 | 261.6411
294.8323 | 475.1522 | 233.1012 | 261.7769
295.8323 | 474.7752 | 234.4779 | 262.0792
296.8323 | 474.3801 | 236.2717 | 262.351
297.8323 | 473.9211 | 238.2135 | 262.5152
298.8323 | 473.4054 | 240.0756 | 262.7162
299.8323 | 472.9028 | 242.0628 | 262.9975
300.8323 | 472.3404 | 244.167 | 263.299
301.8323 | 471.8969 | 246.5216 | 263.5992
302.8323 | 471.4416 | 249.164 | 264.0896
303.8323 | 471.0172 | 252.5162 | 264.7643
304.8323 | 470.6237 | 256.5301 | 265.5837
305.8323 | 470.1911 | 260.3629 | 266.4832
306.8323 | 469.7109 | 263.3405 | 267.5091
307.8323 | 469.3108 | 266.0404 | 268.5789
308.8323 | 469.0006 | 268.9356 | 269.6229
309.8323 | 468.6371 | 271.5644 | 270.6938
310.8323 | 468.3699 | 273.9673 | 271.8361
311.8323 | 468.1515 | 276.2382 | 273.6954
312.8323 | 467.9286 | 278.4094 | 275.3802
313.8323 | 467.5914 | 280.7043 | 277.1091
314.8323 | 467.4331 | 282.9486 | 278.8146
315.8323 | 467.2808 | 284.6957 | 280.4674
316.8323 | 467.049 | 286.7561 | 281.9391
317.8323 | 466.7774 | 288.8996 | 283.6499
318.8323 | 466.6564 | 290.9518 | 285.5
319.8323 | 466.6651 | 292.8978 | 287.0409
320.8323 | 466.5174 | 294.9212 | 288.6574
321.8323 | 466.3075 | 297.3746 | 290.3558
322.8323 | 466.2169 | 299.1907 | 291.821
323.8323 | 466.2617 | 301.0724 | 293.3599
324.8323 | 466.2892 | 303.1175 | 295.3014
325.8323 | 466.2634 | 305.0974 | 297.2814
326.8323 | 466.1493 | 307.4486 | 299.3623
327.8323 | 466.0895 | 309.318 | 301.5793
328.8323 | 466.1816 | 311.3855 | 303.5569
329.8323 | 466.2388 | 313.6154 | 305.9327
330.8323 | 466.1643 | 315.519 | 308.0452
331.8323 | 466.171 | 317.9561 | 310.5921
332.8323 | 466.2648 | 320.3692 | 312.5984
333.8323 | 466.2834 | 321.8812 | 314.2286
334.8323 | 466.2342 | 323.9773 | 315.4107
335.8323 | 466.1979 | 326.0378 | 317.4212
336.8323 | 466.2084 | 327.9026 | 318.8922
337.8479 | 466.2543 | 329.9404 | 320.3673
338.8323 | 466.2761 | 331.2822 | 322.0426
339.8323 | 466.2279 | 333.2561 | 324.1291
340.8323 | 466.247 | 334.8293 | 326.2441
341.8323 | 466.3071 | 336.2867 | 328.1568
342.8323 | 466.4232 | 338.163 | 330.2425
343.8479 | 466.4567 | 340.3957 | 332.3007
344.8323 | 466.4807 | 342.9544 | 334.7561
345.8323 | 466.4761 | 344.0186 | 336.3474
346.8323 | 466.5351 | 345.683 | 338.9335
347.8323 | 466.6536 | 346.5359 | 341.0245
348.8323 | 466.7387 | 347.8308 | 343.3667
349.8323 | 466.777 | 349.3716 | 346.0188
350.8323 | 466.7558 | 352.3954 | 348.8768
351.8323 | 466.7425 | 354.3796 | 350.9188
352.8323 | 466.814 | 355.7942 | 353.2264
353.8323 | 466.8111 | 356.4861 | 354.846
354.8323 | 466.7914 | 357.4442 | 356.4922
355.8479 | 466.7692 | 358.8366 | 358.6005
356.8323 | 466.7691 | 361.6942 | 360.0753
357.8323 | 466.7981 | 362.7803 | 362.1874
358.8323 | 466.8457 | 363.0754 | 364.2484
359.8323 | 466.9249 | 366.8729 | 366.1638
360.8323 | 466.8863 | 368.2469 | 368.1001
361.8323 | 466.8556 | 367.7481 | 370.518
362.8323 | 466.8703 | 368.8456 | 372.5707
363.8323 | 466.9739 | 370.7294 | 374.6638
364.8323 | 466.9742 | 373.1992 | 375.9788
365.8323 | 466.9713 | 374.3119 | 378.2906
366.8323 | 467.0123 | 374.0535 | 379.6156
367.8323 | 467.0573 | 376.4312 | 382.0775
368.8323 | 467.0749 | 380.5196 | 383.7487
369.8323 | 467.0462 | 380.5596 | 385.1803
370.8323 | 466.9519 | 382.2657 | 386.7991
371.8323 | 466.932 | 383.4933 | 388.7827
372.8323 | 467.0436 | 383.8576 | 390.3355
373.8323 | 467.0329 | 392.0737 | 391.4316
374.8323 | 467.0123 | 388.8765 | 392.8231
375.8323 | 467.0595 | 392.2544 | 394.1484
376.8323 | 467.0052 | 390.2297 | 395.323
377.8323 | 466.9628 | 391.6998 | 397.377
378.8323 | 466.9176 | 395.1764 | 398.8658
379.8323 | 466.8828 | 395.4426 | 400.3433
380.8323 | 466.8842 | 399.4206 | 401.8323
381.8323 | 466.8941 | 400.0695 | 403.4881
382.8323 | 466.8592 | 400.944 | 404.7411
383.8323 | 466.8882 | 401.7541 | 405.9997
384.8323 | 466.928 | 404.6292 | 407.3239
385.8323 | 466.91 | 409.9214 | 408.3003
386.8323 | 466.8395 | 406.9198 | 410.6046
387.8323 | 466.7766 | 410.7056 | 411.6033
388.8323 | 466.696 | 411.0298 | 413.2416
389.8323 | 466.7061 | 415.0941 | 414.5489
390.8323 | 466.7274 | 416.3876 | 414.7559
391.8323 | 466.7997 | 416.6 | 415.7215
392.8323 | 466.8176 | 417.1445 | 416.9904
393.8323 | 466.7847 | 418.6066 | 418.6
394.8323 | 466.8397 | 420.4209 | 419.5864
395.8323 | 466.8384 | 420.1289 | 420.5558
396.8323 | 466.8219 | 422.3188 | 421.7211
397.8323 | 466.8304 | 423.2877 | 422.7686
398.8323 | 466.8339 | 422.8116 | 423.8148
399.8323 | 466.843 | 425.5973 | 424.8868
400.8323 | 466.8989 | 426.0933 | 425.7743
401.8323 | 466.8282 | 428.6157 | 427.3056
402.8323 | 466.7904 | 426.8555 | 428.604
403.8323 | 466.8091 | 431.3338 | 429.9278
404.8323 | 466.7811 | 429.7288 | 430.8225
405.8323 | 466.789 | 432.3377 | 431.2352
406.8323 | 466.752 | 432.8106 | 432.6486
407.8323 | 466.7186 | 432.3299 | 433.9567
408.8323 | 466.7348 | 435.7717 | 434.8822
409.8323 | 466.7009 | 434.0254 | 435.4842
410.8323 | 466.6642 | 437.1689 | 436.9327
411.8323 | 466.6325 | 436.1123 | 437.744
412.8323 | 466.6272 | 438.8231 | 438.8862
413.8323 | 466.6412 | 439.5471 | 438.9309
414.8323 | 466.5824 | 438.912 | 439.7076
415.8323 | 466.5347 | 439.844 | 440.4933
416.8323 | 466.5015 | 439.0947 | 441.2721
417.8323 | 466.4866 | 439.3954 | 441.768
418.8323 | 466.4304 | 439.9369 | 442.332
419.8323 | 466.5117 | 438.6412 | 443.2015
420.8323 | 466.5029 | 438.8462 | 443.3395
421.8323 | 466.4902 | 437.8658 | 443.5936
422.8323 | 466.4394 | 436.004 | 444.6133
423.8323 | 466.4227 | 436.2032 | 444.4843
424.8323 | 466.3433 | 432.4447 | 445.1102
425.8323 | 466.2609 | 433.6007 | 445.3225
426.8323 | 466.2094 | 432.7097 | 446.2735
427.8323 | 466.1596 | 431.8612 | 446.8041
428.8323 | 466.1074 | 430.1053 | 446.4002
429.8323 | 466.0287 | 429.2385 | 446.7326
430.8323 | 466.0214 | 428.1381 | 447.676
431.8323 | 466.1064 | 428.1802 | 448.125
432.8323 | 466.0889 | 427.2306 | 447.7939
433.8323 | 465.9805 | 426.3678 | 448.9122
434.8323 | 465.9839 | 425.6869 | 449.0713
435.8323 | 465.9843 | 424.7912 | 449.6293
436.8323 | 465.9171 | 424.9644 | 450.0579
437.8323 | 465.8928 | 425.1431 | 450.9684
438.8323 | 465.8548 | 425.084 | 450.9199
439.8323 | 465.8595 | 425.3063 | 451.7423
440.8323 | 465.8163 | 425.6079 | 452.6839
441.8323 | 465.8085 | 426.1129 | 452.7379
442.8323 | 465.8264 | 426.8156 | 453.398
443.8323 | 465.8194 | 427.3896 | 454.1184
444.8323 | 465.8384 | 428.3488 | 454.8682
445.8323 | 465.8854 | 429.2927 | 455.3741
446.8323 | 465.9437 | 430.7337 | 456.2412
447.8323 | 466.0249 | 432.8588 | 457.3034
448.8323 | 466.0861 | 434.9123 | 457.7633
449.8323 | 466.039 | 436.5252 | 458.4064
450.8323 | 466.0481 | 438.5039 | 459.4241
451.8323 | 466.0656 | 440.836 | 459.7521
452.8323 | 466.0375 | 441.978 | 460.2929
453.8323 | 465.9882 | 444.1142 | 461.5148
454.8323 | 465.9906 | 445.6252 | 462.3578
455.8323 | 466.0149 | 447.2578 | 463.1467
456.8323 | 466.06 | 448.8176 | 464.1122
457.8323 | 466.0143 | 450.5593 | 464.7238
458.8323 | 465.9793 | 451.9736 | 465.505
459.8323 | 465.9816 | 454.1928 | 466.3908
460.8323 | 465.92 | 456.1615 | 467.2052
461.8323 | 465.9711 | 457.9512 | 468.0868
462.8323 | 465.9925 | 459.7345 | 469.0989
463.8323 | 465.995 | 461.6599 | 469.9044
464.8323 | 465.9585 | 463.3098 | 470.8214
465.8323 | 465.9961 | 465.0217 | 471.9099
466.8323 | 465.9421 | 466.858 | 472.6312
467.8323 | 465.905 | 468.8302 | 473.5556
468.8323 | 465.8476 | 470.8655 | 474.3225
469.8323 | 465.8422 | 472.5768 | 475.2282
470.8323 | 465.7986 | 474.101 | 475.9615
471.8323 | 465.7149 | 475.8204 | 476.6949
472.8323 | 465.7142 | 478.6292 | 477.3149
473.8323 | 465.7078 | 481.0983 | 478.1656
474.8323 | 465.6477 | 483.6633 | 478.9824
475.8323 | 465.6137 | 486.1175 | 479.6007
476.8323 | 465.6336 | 489.4168 | 480.2333
477.8323 | 465.4707 | 491.529 | 481.0344
478.8323 | 465.4181 | 493.7534 | 481.7711
479.8323 | 465.4478 | 496.0334 | 482.5693
480.8323 | 465.3676 | 498.7394 | 483.2295
481.8323 | 465.3534 | 500.614 | 483.901
482.8323 | 465.2986 | 502.2377 | 484.5092
483.8323 | 465.2305 | 503.4934 | 485.1563
484.8323 | 465.1927 | 505.0257 | 485.7993
485.8323 | 465.216 | 506.3139 | 486.6331
486.8479 | 465.1516 | 508.8025 | 487.3555
487.8323 | 465.0786 | 510.9809 | 488.0795
488.8323 | 465.0845 | 512.7722 | 488.748
489.8323 | 465.0322 | 515.2187 | 489.5454
490.8323 | 464.9603 | 517.352 | 490.2179
491.8479 | 464.9003 | 520.5119 | 491.0486
492.8323 | 464.9998 | 522.9485 | 491.7617
493.8479 | 465.0465 | 525.2169 | 492.4313
494.8323 | 465.0485 | 525.4761 | 493.1821
495.8479 | 464.9008 | 526.9505 | 493.8937
496.8479 | 464.7712 | 528.328 | 494.4903
497.8479 | 464.7187 | 529.5441 | 495.0629
498.8479 | 464.7401 | 531.7461 | 495.7323
499.8479 | 464.7197 | 530.9841 | 496.4523
500.8323 | 464.7004 | 529.1393 | 497.1585
501.8479 | 464.632 | 528.8818 | 497.7911
502.8323 | 464.5726 | 529.6196 | 498.4236
503.8323 | 464.562 | 530.6666 | 499.1197
504.8323 | 464.5211 | 530.4008 | 499.8272
505.8323 | 464.5435 | 529.022 | 500.437
506.8323 | 464.4793 | 527.9068 | 501.1686
507.8323 | 464.4185 | 526.9966 | 501.9919
508.8323 | 464.289 | 526.1218 | 502.6664
509.8323 | 464.1781 | 525.2585 | 503.4652
510.8323 | 464.1086 | 524.3937 | 503.9789
511.8323 | 464.0785 | 524.1976 | 504.6527
512.8323 | 464.0898 | 522.7993 | 505.1386
513.8323 | 463.9982 | 522.1415 | 505.7418
514.8479 | 463.9208 | 521.7332 | 506.057
515.8323 | 463.8333 | 522.1217 | 506.5212
516.8323 | 463.7043 | 522.8265 | 506.9893
517.8323 | 463.668 | 521.7591 | 507.4175
518.8323 | 463.6316 | 521.2875 | 507.7942
519.8323 | 463.5773 | 520.6922 | 508.1117
520.8323 | 463.541 | 520.3987 | 507.9059
521.8323 | 463.5398 | 519.6344 | 506.3226
522.8323 | 463.4785 | 519.3596 | 505.6374
523.8323 | 463.4669 | 519.5286 | 505.3909
524.8323 | 463.5026 | 518.8946 | 504.9846
525.8323 | 463.4253 | 518.2592 | 504.7626
526.8323 | 463.3184 | 517.3295 | 504.7187
527.8323 | 463.1096 | 516.9245 | 504.6691
528.8323 | 463.0173 | 516.6523 | 504.7861
529.8323 | 462.9542 | 516.136 | 504.8599
530.8323 | 463.0192 | 516.1483 | 504.9252
531.8323 | 463.0934 | 515.9626 | 504.8654
532.8323 | 463.068 | 516.1641 | 504.943
533.8323 | 463.0854 | 516.4643 | 504.8608
534.8323 | 463.1519 | 516.5265 | 505.0808
535.8323 | 463.2049 | 516.0949 | 505.1769
536.8323 | 463.2145 | 516.2206 | 505.2861
537.8323 | 463.2179 | 516.066 | 505.4208
538.8323 | 463.3017 | 516.362 | 505.6715
539.8323 | 463.4027 | 516.6942 | 506.048
540.8323 | 463.512 | 516.8 | 506.0626
541.8323 | 463.6461 | 516.8969 | 506.2158
542.8323 | 463.7198 | 517.0469 | 506.4489
543.8323 | 463.8561 | 517.3484 | 506.7796
544.8323 | 464.0014 | 517.5916 | 507.1808
545.8323 | 464.1664 | 518.0419 | 507.6246
546.8323 | 464.278 | 518.0054 | 508.2862
547.8323 | 464.2751 | 517.652 | 508.7788
548.8323 | 464.2901 | 517.7703 | 509.0912
549.8323 | 464.3298 | 518.4164 | 509.288
550.8323 | 464.3867 | 519.164 | 509.1785
551.8323 | 464.4661 | 519.2471 | 509.4362
552.8323 | 464.556 | 520.201 | 509.6476
553.8323 | 464.6547 | 520.1996 | 509.884
554.8323 | 464.7734 | 520.9255 | 510.0636
555.8479 | 464.8581 | 521.4755 | 510.1924
556.8479 | 464.9838 | 521.7634 | 510.3898
557.8323 | 464.9384 | 521.8315 | 510.5607
558.8479 | 464.8681 | 522.2623 | 510.6361
559.8479 | 464.8784 | 522.857 | 510.7417
560.8323 | 464.8653 | 523.4105 | 510.9076
561.8323 | 464.946 | 524.296 | 510.9287
562.8323 | 464.9331 | 524.675 | 511.0871
563.8323 | 464.9429 | 525.31 | 511.3281
564.8323 | 464.913 | 525.6513 | 511.5446
565.8479 | 465.0013 | 525.7992 | 511.8673
566.8323 | 465.0335 | 526.129 | 512.1569
567.8323 | 465.059 | 527.3825 | 512.5535
568.8479 | 465.0762 | 527.6719 | 512.673
569.8323 | 465.1114 | 527.6269 | 512.6935
570.8323 | 465.0853 | 528.0316 | 512.7698
571.8323 | 465.072 | 528.9906 | 512.7425
572.8323 | 465.0111 | 529.2142 | 512.924
573.8323 | 465.0091 | 529.2841 | 513.0254
574.8479 | 464.9708 | 529.5479 | 513.3165
575.8479 | 464.9402 | 529.9834 | 513.4544
576.8479 | 464.9936 | 530.083 | 513.5474
577.8323 | 465.0193 | 531.0322 | 513.6474
578.8479 | 465.0643 | 531.1451 | 513.7109
579.8479 | 465.0244 | 531.0365 | 513.8281
580.8323 | 464.9991 | 531.2749 | 514.0686
581.8479 | 465.0031 | 531.4383 | 514.2422
582.8479 | 465.095 | 531.8528 | 514.5267
583.8479 | 465.1906 | 532.3571 | 514.6609
584.8479 | 465.226 | 533.1356 | 514.8123
585.8479 | 465.2469 | 533.5644 | 515.0059
586.8479 | 465.287 | 534.1941 | 515.1805
587.8479 | 465.3428 | 535.1491 | 515.4133
588.8479 | 465.3676 | 535.9118 | 515.6907
589.8479 | 465.4077 | 535.8332 | 515.746
590.8479 | 465.4266 | 535.9052 | 515.8119
591.8323 | 465.492 | 535.948 | 515.939
592.8479 | 465.4893 | 535.6738 | 515.8363
593.8479 | 465.6015 | 535.3472 | 515.8506
594.8479 | 465.7632 | 535.0889 | 515.824
595.8479 | 465.8047 | 534.9447 | 515.6735
596.8479 | 465.8785 | 535.0912 | 515.7222
597.8479 | 465.9849 | 534.8775 | 515.5947
598.8479 | 466.0583 | 535.1238 | 515.4514
599.8479 | 466.0954 | 535.144 | 515.475
600.8479 | 466.128 | 534.8663 | 515.48
601.8479 | 466.2112 | 535.159 | 515.3826
602.8323 | 466.1885 | 534.6553 | 515.2806
603.8323 | 466.1767 | 534.0637 | 515.0467
604.8323 | 466.0605 | 533.743 | 514.9128
605.8323 | 466.03 | 534.0475 | 514.6763
606.8323 | 466.0776 | 534.5145 | 514.4919
607.8323 | 466.0812 | 534.831 | 514.3063
608.8323 | 466.0842 | 535.295 | 514.0913
609.8323 | 465.9665 | 535.4023 | 514.0258
610.8323 | 465.8672 | 535.901 | 513.8579
611.8323 | 465.8414 | 536.3381 | 513.7307
612.8323 | 465.8144 | 536.1715 | 513.6089
613.8323 | 465.7484 | 537.1003 | 513.4186
614.8323 | 465.7197 | 537.3786 | 513.238
615.8323 | 465.7887 | 537.9168 | 513.0205
616.8323 | 465.8805 | 538.448 | 512.888
617.8323 | 465.8434 | 539.3428 | 512.6669
618.8323 | 465.766 | 540.3042 | 512.509
619.8323 | 465.7632 | 540.824 | 512.2942
620.8323 | 465.7538 | 541.1203 | 512.2697
621.8323 | 465.6686 | 541.428 | 512.202
622.8323 | 465.62 | 541.7382 | 512.1933
623.8323 | 465.5602 | 542.6087 | 512.2017
624.8323 | 465.543 | 543.0869 | 512.1893
625.8323 | 465.5404 | 543.8314 | 512.2385
626.8323 | 465.5234 | 544.3151 | 512.3042
627.8323 | 465.5502 | 544.8578 | 512.5433
628.8323 | 465.5188 | 545.2326 | 512.7259
629.8323 | 465.5125 | 545.239 | 512.9762
630.8323 | 465.4503 | 545.3326 | 513.1897
631.8323 | 465.3315 | 545.3877 | 513.4505
632.8323 | 465.2894 | 545.3991 | 513.7401
633.8323 | 465.1844 | 545.7869 | 514.1381
634.8323 | 465.1134 | 546.7427 | 513.9405
635.8323 | 465.1052 | 547.2678 | 514.4985
636.8323 | 465.1826 | 547.8595 | 515.2475
637.8479 | 465.2298 | 548.5721 | 515.7531
638.8479 | 465.206 | 548.9975 | 516.2965
639.8479 | 465.2005 | 549.5408 | 516.7199
640.8479 | 465.1589 | 550.0593 | 517.1211
641.8323 | 465.0771 | 550.3177 | 517.8542
642.8323 | 464.9403 | 550.8078 | 518.4297
643.8323 | 464.9011 | 551.2543 | 518.9058
644.8479 | 464.9745 | 551.6678 | 519.5148
645.8323 | 464.9827 | 552.7433 | 520.3702
646.8323 | 464.9454 | 553.4018 | 520.9806
647.8323 | 464.9045 | 553.7073 | 521.6027
648.8323 | 465.0044 | 553.9589 | 522.3405
649.8323 | 464.9693 | 554.9574 | 522.8964
650.8323 | 464.9472 | 555.4724 | 523.934
651.8323 | 464.9672 | 556.0904 | 524.6926
652.8323 | 464.899 | 557.277 | 525.5461
653.8323 | 464.8373 | 557.3178 | 526.2818
654.8323 | 464.8052 | 557.5064 | 526.5827
655.8323 | 464.8006 | 557.7948 | 527.3952
656.8323 | 464.7725 | 558.3594 | 527.9578
657.8323 | 464.77 | 558.3758 | 527.0453
658.8323 | 464.7644 | 559.2415 | 530.2088
659.8323 | 464.7561 | 559.8076 | 530.7522
660.8323 | 464.6572 | 560.6327 | 531.6315
661.8323 | 464.4428 | 561.6113 | 532.3314
662.8323 | 464.4014 | 561.8449 | 533.1219
663.8323 | 464.3749 | 562.8664 | 534.0701
664.8323 | 464.4324 | 563.9217 | 535.0046
665.8323 | 464.4639 | 565.2065 | 535.8488
666.8323 | 464.5812 | 566.2823 | 536.6437
667.8323 | 464.7303 | 567.5785 | 537.6507
668.8323 | 464.7879 | 568.5174 | 538.5591
669.8323 | 464.708 | 569.7347 | 539.4537
670.8323 | 464.6863 | 570.3936 | 540.4565
671.8323 | 464.8268 | 571.7137 | 541.3127
672.8323 | 464.935 | 572.227 | 542.3225
673.8323 | 464.9366 | 572.8037 | 543.2612
674.8323 | 464.9911 | 574.1403 | 544.4741
675.8323 | 465.047 | 574.9491 | 545.4173
676.8323 | 464.9536 | 575.4916 | 546.3187
677.8323 | 464.8569 | 576.1639 | 547.3376
678.8323 | 464.8465 | 576.3315 | 548.186
679.8323 | 464.9224 | 576.9674 | 549.1203
680.8323 | 464.9537 | 577.3362 | 549.8718
681.8323 | 464.8917 | 577.0358 | 550.5315
682.8323 | 464.8734 | 577.6563 | 551.4264
683.8323 | 464.9592 | 578.3777 | 552.3338
684.8323 | 465.0597 | 578.7234 | 552.9894
685.8323 | 465.1445 | 578.8755 | 553.7379
686.8323 | 465.1024 | 579.5218 | 554.4082
687.8323 | 465.0551 | 579.7136 | 555.0803
688.8323 | 464.9624 | 580.7031 | 555.7791
689.8323 | 464.8612 | 581.9065 | 556.6374
690.8323 | 464.8297 | 582.6759 | 557.3946
691.8323 | 464.8591 | 583.2404 | 558.0278
692.8323 | 464.9302 | 583.5012 | 558.8528
693.8323 | 464.8916 | 584.1298 | 559.6052
694.8323 | 464.8433 | 584.6445 | 560.3551
695.8323 | 464.8318 | 585.2005 | 560.8844
696.8323 | 464.8368 | 585.7921 | 561.511
697.8323 | 464.773 | 585.9304 | 562.2395
698.8323 | 464.7196 | 586.9006 | 562.8718
699.8323 | 464.706 | 587.4371 | 563.464
700.8323 | 464.744 | 588.0696 | 564.2784
701.8323 | 464.7809 | 588.9479 | 564.7699
702.8323 | 464.8172 | 590.0619 | 565.447
703.8323 | 464.8245 | 590.7817 | 566.0191
704.8323 | 464.7495 | 591.2431 | 566.6959
705.8323 | 464.669 | 591.7448 | 567.365
706.8323 | 464.6269 | 592.3459 | 567.7543
707.8323 | 464.6461 | 592.936 | 568.6066
708.8323 | 464.6612 | 593.2983 | 569.1504
709.8323 | 464.6683 | 593.7042 | 569.6632
710.8323 | 464.6854 | 594.3875 | 570.2699
711.8323 | 464.7285 | 594.5299 | 570.7575
712.8323 | 464.8363 | 595.0645 | 571.0095
713.8323 | 464.9701 | 595.3965 | 571.5143
714.8323 | 465.0343 | 596.2017 | 572.1368
715.8323 | 465.098 | 596.0893 | 572.6395
716.8323 | 465.1772 | 596.4828 | 572.8511
717.8323 | 465.2834 | 596.9215 | 573.426
718.8323 | 465.4355 | 597.0326 | 573.9988
719.8323 | 465.6239 | 596.9741 | 574.5627
720.8323 | 465.7772 | 597.0604 | 575.4066
721.8323 | 465.8865 | 597.2218 | 575.8065
722.8323 | 465.9939 | 597.5289 | 576.4096
723.8323 | 466.155 | 597.8058 | 576.9592
724.8323 | 466.2971 | 598.0199 | 577.56
725.8323 | 466.391 | 598.2827 | 578.1845
726.8323 | 466.4899 | 598.3982 | 578.5594
727.8323 | 466.6165 | 598.343 | 579.0811
728.8323 | 466.7357 | 598.8881 | 579.4043
729.8323 | 466.8693 | 599.1064 | 579.9824
730.8323 | 467.1268 | 599.4687 | 580.5641
731.8323 | 467.28 | 599.4844 | 580.961
732.8323 | 467.3463 | 599.5839 | 581.3519
733.8323 | 467.4384 | 599.4976 | 581.7267
734.8323 | 467.5318 | 599.6643 | 582.2957
735.8323 | 467.5804 | 600.2132 | 582.6945
736.8323 | 467.6473 | 600.4924 | 583.1397
737.8323 | 467.7672 | 600.4509 | 583.5826
738.8323 | 467.876 | 600.1255 | 583.8447
739.8323 | 467.9468 | 599.831 | 584.1151
740.8323 | 467.9821 | 600.1678 | 584.6352
741.8323 | 468.0355 | 600.628 | 585.0097
742.8323 | 468.102 | 601.0763 | 585.4076
743.8323 | 468.15 | 601.4655 | 585.7307
744.8323 | 468.1882 | 601.9037 | 586.016
745.8323 | 468.2582 | 602.2195 | 586.3058
746.8323 | 468.2725 | 602.1509 | 586.6881
747.8323 | 468.3166 | 602.3534 | 587.0902
748.8323 | 468.3914 | 602.2931 | 587.4313
749.8323 | 468.4544 | 601.9662 | 587.7292
750.8323 | 468.4703 | 601.9733 | 588.0755
751.8323 | 468.4121 | 602.1174 | 587.7877
752.8323 | 468.3505 | 602.5824 | 588.4093
753.8323 | 468.2686 | 602.7995 | 588.8847
754.8323 | 468.1946 | 603.2466 | 589.12
755.8323 | 468.1126 | 603.2909 | 589.1969
756.8323 | 468.0873 | 603.6559 | 589.5079
757.8323 | 468.1187 | 603.7733 | 589.5813
758.8323 | 468.0862 | 604.1442 | 589.7752
759.8323 | 468.0167 | 603.8848 | 589.9038
760.8323 | 467.9948 | 603.8321 | 589.9553
761.8323 | 467.8394 | 603.6628 | 589.9906
762.8323 | 467.7356 | 603.7854 | 590.06
763.8323 | 467.7077 | 604.1354 | 589.8059
764.8323 | 467.6484 | 604.3928 | 589.7524
765.8323 | 467.6294 | 604.1003 | 589.6583
766.8323 | 467.5987 | 604.1212 | 589.68
767.8323 | 467.5703 | 603.8284 | 589.5583
768.8323 | 467.5567 | 603.7681 | 589.6167
769.8323 | 467.5333 | 603.5961 | 589.6307
770.8323 | 467.4646 | 603.6226 | 589.5742
771.8323 | 467.3756 | 603.4746 | 589.5819
772.8323 | 467.2816 | 604.3733 | 589.5294
773.8323 | 467.1459 | 604.7827 | 589.5679
774.8323 | 467.0361 | 604.6375 | 589.4425
775.8323 | 466.9491 | 604.2031 | 589.3253
776.8323 | 466.8742 | 603.6358 | 589.2065
777.8323 | 466.8423 | 603.2815 | 589.1105
778.8323 | 466.8043 | 602.6537 | 588.9078
779.8323 | 466.8286 | 602.4651 | 588.7785
780.8323 | 466.89 | 602.0286 | 588.4745
781.8323 | 466.9169 | 601.5409 | 588.4841
782.8323 | 466.9297 | 600.9128 | 588.4706
783.8323 | 466.9059 | 600.6677 | 588.4086
784.8323 | 466.871 | 600.0388 | 588.4227
785.8323 | 466.8465 | 600.0458 | 588.5724
786.8323 | 466.8487 | 600.1139 | 588.6339
787.8323 | 466.8492 | 600.3958 | 588.6371
788.8323 | 466.7739 | 600.6497 | 588.6705
789.8323 | 466.7286 | 600.2649 | 588.6723
790.8323 | 466.7287 | 599.6943 | 588.6498
791.8323 | 466.7161 | 599.2302 | 588.2854
792.8323 | 466.6715 | 598.8749 | 588.2857
793.8323 | 466.6314 | 598.5484 | 588.3447
794.8323 | 466.5563 | 598.8059 | 588.2856
795.8323 | 466.5563 | 599.0073 | 588.0535
796.8323 | 466.5573 | 599.0561 | 587.878
797.8323 | 466.4925 | 598.9989 | 587.8087
798.8479 | 466.4769 | 599.2183 | 587.6309
799.8323 | 466.5225 | 599.5665 | 587.3442
800.8479 | 466.5159 | 599.5554 | 586.9078
801.8323 | 466.4697 | 599.3276 | 586.694
802.8323 | 466.4825 | 598.3727 | 586.0964
803.8323 | 466.5101 | 597.7248 | 585.8106
804.8323 | 466.5315 | 597.1228 | 585.5629
805.8323 | 466.5282 | 596.0242 | 585.5219
806.8323 | 466.4786 | 594.8246 | 585.0812
807.8323 | 466.4306 | 593.8491 | 584.9966
808.8323 | 466.4326 | 592.8654 | 585.1115
809.8323 | 466.4474 | 592.3319 | 584.9464
810.8323 | 466.4293 | 591.5549 | 584.9325
811.8323 | 466.387 | 591.3465 | 584.6027
812.8323 | 466.343 | 590.5918 | 584.6633
813.8323 | 466.3442 | 589.9671 | 584.6699
814.8323 | 466.3497 | 589.6587 | 584.5716
815.8323 | 466.3312 | 589.4442 | 584.6274
816.8323 | 466.3222 | 589.4613 | 584.451
817.8323 | 466.3028 | 589.0479 | 584.1346
818.8323 | 466.3174 | 588.6287 | 584.2151
819.8323 | 466.3214 | 588.3689 | 584.3312
820.8323 | 466.3474 | 588.7212 | 584.7401
821.8323 | 466.3543 | 588.6693 | 584.7319
822.8323 | 466.4139 | 589.0687 | 584.8371
823.8323 | 466.4711 | 589.2034 | 584.9745
824.8323 | 466.4848 | 589.6759 | 585.0831
825.8323 | 466.5166 | 589.608 | 585.4115
826.8323 | 466.5711 | 590.1286 | 585.4328
827.8323 | 466.5774 | 590.8482 | 585.6275
828.8323 | 466.6256 | 590.8718 | 585.8604
829.8323 | 466.69 | 590.8179 | 586.0379
830.8323 | 466.6927 | 591.2126 | 586.517
831.8323 | 466.7287 | 591.6505 | 586.7616
832.8323 | 466.7854 | 592.518 | 586.8777
833.8323 | 466.8188 | 592.7481 | 586.9385
834.8323 | 466.8684 | 593.1154 | 586.9557
835.8323 | 466.9227 | 594.0043 | 587.6684
836.8323 | 466.9927 | 594.2599 | 587.4434
837.8323 | 467.0103 | 593.7447 | 587.407
838.8323 | 467.0227 | 593.5928 | 587.7264
839.8323 | 467.0571 | 593.8459 | 588.2934
840.8323 | 467.0536 | 594.2685 | 588.7876
841.8323 | 467.0167 | 594.4903 | 588.8502
842.8323 | 467.009 | 594.5154 | 589.2338
843.8323 | 467.0312 | 594.3978 | 589.6128
844.8323 | 467.0739 | 594.2948 | 589.7855
845.8323 | 467.0588 | 594.4599 | 590.2376
846.8323 | 467.1034 | 594.3465 | 590.3795
847.8323 | 467.1549 | 594.3563 | 590.565
848.8323 | 467.2283 | 594.1667 | 590.9983
849.8323 | 467.2975 | 594.2651 | 591.341
850.8323 | 467.3667 | 594.556 | 591.5948
851.8323 | 467.3899 | 594.2155 | 591.5426
852.8323 | 467.3888 | 593.9376 | 591.5938
853.8323 | 467.3877 | 593.6604 | 591.8549
854.8323 | 467.3772 | 593.5905 | 591.9083
855.8323 | 467.3763 | 593.1214 | 592.0047
856.8323 | 467.4171 | 592.9223 | 591.6385
857.8323 | 467.4676 | 593.1851 | 591.5583
858.8323 | 467.4977 | 593.5596 | 591.515
859.8323 | 467.5055 | 594.3355 | 591.6169
860.8323 | 467.4642 | 594.7302 | 591.8241
861.8323 | 467.4273 | 594.3578 | 591.7654
862.8323 | 467.4558 | 593.8369 | 592.0328
863.8323 | 467.473 | 593.9807 | 592.1062
864.8323 | 467.498 | 593.4206 | 592.6559
865.8323 | 467.5187 | 593.6617 | 593.2206
866.8323 | 467.5243 | 593.1539 | 592.8143
867.8323 | 467.5491 | 593.7994 | 593.0807
868.8323 | 467.5827 | 594.7674 | 593.2215
869.8323 | 467.5981 | 595.7996 | 593.3628
870.8323 | 467.6567 | 596.0179 | 593.8669
871.8323 | 467.6957 | 595.6501 | 593.6907
872.8323 | 467.716 | 595.8726 | 593.827
873.8323 | 467.7057 | 595.286 | 594.1444
874.8323 | 467.714 | 594.5227 | 594.2245
875.8323 | 467.7396 | 594.7502 | 594.6771
876.8323 | 467.7852 | 594.7886 | 595.1722
877.8323 | 467.8152 | 594.3804 | 594.7334
878.8323 | 467.8284 | 593.8482 | 594.7426
879.8323 | 467.7952 | 593.1134 | 594.0998
880.8323 | 467.8015 | 592.7279 | 594.0122
881.8323 | 467.815 | 592.36 | 593.0401
882.8323 | 467.7854 | 592.0892 | 592.7793
883.8323 | 467.769 | 591.7701 | 592.6308
884.8323 | 467.7758 | 591.8484 | 592.1388
885.8323 | 467.7613 | 591.9859 | 592.1388
886.8323 | 467.7565 | 591.9525 | 591.24
887.8323 | 467.7621 | 591.7242 | 591.0468
888.8323 | 467.7512 | 591.2769 | 590.7922
889.8323 | 467.7381 | 592.4555 | 590.567
890.8323 | 467.7087 | 593.2606 | 590.8317
891.8323 | 467.708 | 593.3669 | 590.4888
892.8323 | 467.6925 | 593.7384 | 590.6162
893.8323 | 467.6473 | 593.6935 | 590.8849
894.8323 | 467.6226 | 593.9622 | 591.1567
895.8323 | 467.6014 | 594.3872 | 591.4138
896.8323 | 467.5867 | 594.9811 | 591.7215
897.8323 | 467.5792 | 595.7331 | 592.2123
898.8323 | 467.5683 | 596.3078 | 592.6755
899.8323 | 467.5733 | 597.0699 | 593.2114
900.8323 | 467.5687 | 598.0086 | 594.3676
901.8323 | 467.5989 | 598.161 | 594.5021
902.8323 | 467.5825 | 598.2519 | 594.792
903.8323 | 467.5765 | 598.0586 | 595.1655
904.8323 | 467.5874 | 597.739 | 595.2674
905.8323 | 467.5813 | 597.6907 | 595.6581
906.8323 | 467.6371 | 597.9817 | 595.5209
907.8323 | 467.6682 | 598.4996 | 595.9725
908.8323 | 467.7025 | 598.307 | 595.8094
909.8323 | 467.7013 | 598.4937 | 596.4485
910.8323 | 467.7115 | 598.4202 | 596.7111
911.8323 | 467.7 | 598.383 | 596.5665
912.8323 | 467.6949 | 598.7688 | 596.8568
913.8323 | 467.6891 | 598.8883 | 597.2381
914.8323 | 467.6811 | 599.0021 | 597.6217
915.8479 | 467.6924 | 598.9635 | 598.5072
916.8323 | 467.6848 | 599.033 | 598.3236
917.8323 | 467.6908 | 599.3456 | 598.4859
918.8323 | 467.7567 | 599.6503 | 598.8059
919.8323 | 467.7624 | 599.8213 | 599.412
920.8323 | 467.7498 | 600.0154 | 600.0931
921.8323 | 467.7643 | 599.9904 | 599.8415
922.8323 | 467.7743 | 600.3225 | 600.2654
923.8323 | 467.7536 | 600.3937 | 600.7232
924.8323 | 467.7548 | 600.4452 | 601.1913
925.8323 | 467.7529 | 600.6787 | 602.0893
926.8323 | 467.7857 | 600.7256 | 602.1185
927.8323 | 467.7807 | 600.9011 | 602.6292
928.8323 | 467.7815 | 600.8814 | 603.069
929.8323 | 467.8032 | 600.3423 | 603.5266
930.8323 | 467.8006 | 599.9951 | 604.39
931.8323 | 467.7966 | 599.431 | 604.5499
932.8323 | 467.795 | 599.3426 | 604.6874
933.8323 | 467.7942 | 599.113 | 604.5526
934.8323 | 467.7968 | 599.0625 | 604.6899
935.8323 | 467.7914 | 599.2769 | 605.4012
936.8323 | 467.8221 | 599.0693 | 605.4661
937.8323 | 467.8537 | 598.9026 | 605.6032
938.8323 | 467.8748 | 598.9169 | 605.3471
939.8323 | 467.9046 | 599.3689 | 605.103
940.8323 | 467.8923 | 599.8503 | 605.527
941.8323 | 467.8932 | 600.1934 | 605.0991
942.8323 | 467.8774 | 600.5816 | 605.202
943.8323 | 467.8598 | 600.6029 | 605.5317
944.8323 | 467.85 | 600.3832 | 605.8774
945.8323 | 467.8233 | 601.0721 | 606.7946
946.8323 | 467.8719 | 601.2046 | 606.7018
947.8323 | 467.9394 | 601.5635 | 607.0131
948.8323 | 467.947 | 601.8284 | 607.3585
949.8323 | 467.972 | 601.8237 | 607.7652
950.8323 | 467.9927 | 602.1458 | 608.8308
951.8323 | 468.0319 | 601.9903 | 609.1238
952.8323 | 468.0806 | 602.0017 | 609.5666
953.8323 | 468.1329 | 602.5093 | 610.3933
954.8479 | 468.1366 | 603.0535 | 611.0318
955.8323 | 468.1282 | 603.4315 | 611.3986
956.8323 | 468.1414 | 603.5364 | 611.464
957.8479 | 468.1665 | 603.8958 | 611.7975
958.8479 | 468.2126 | 603.9998 | 612.1286
959.8323 | 468.2653 | 603.9672 | 612.4009
960.8323 | 468.2805 | 604.1782 | 612.5971
961.8323 | 468.2861 | 604.0884 | 612.5587
962.8323 | 468.3473 | 603.7108 | 612.487
963.8323 | 468.4001 | 603.5797 | 612.5446
964.8323 | 468.4352 | 603.2832 | 613.1361
965.8323 | 468.4773 | 603.5187 | 613.7384
966.8323 | 468.5328 | 603.3439 | 613.5488
967.8323 | 468.5831 | 603.6594 | 613.7324
968.8323 | 468.635 | 604.6049 | 613.7859
969.8323 | 468.6487 | 605.3673 | 613.7301
970.8323 | 468.6712 | 605.8721 | 614.0773
971.8323 | 468.6926 | 605.3607 | 613.8412
972.8323 | 468.7521 | 604.9568 | 614.0809
973.8323 | 468.7536 | 605.4338 | 614.3456
974.8323 | 468.8075 | 605.575 | 614.768
975.8323 | 468.8326 | 605.9863 | 615.0061
976.8323 | 468.8595 | 606.0386 | 615.0957
977.8323 | 468.9187 | 606.4662 | 615.181
978.8323 | 468.9561 | 605.9909 | 615.2396
979.8323 | 468.9742 | 605.8327 | 615.3104
980.8323 | 469.0051 | 605.5467 | 615.8713
981.8323 | 469.0735 | 605.1168 | 615.9124
982.8323 | 469.1328 | 605.4144 | 616.1511
983.8323 | 469.1941 | 605.8511 | 616.4546
984.8323 | 469.2323 | 606.0805 | 616.9496
985.8323 | 469.2605 | 606.3791 | 617.781
986.8323 | 469.2829 | 606.4344 | 617.8049
987.8323 | 469.3363 | 606.0983 | 617.9005
988.8323 | 469.3221 | 606.0732 | 618.3892
989.8323 | 469.3617 | 606.3394 | 619.0002
990.8323 | 469.3995 | 606.6038 | 619.6968
991.8323 | 469.4442 | 606.5439 | 619.2289
992.8323 | 469.4855 | 606.6255 | 619.5146
993.8323 | 469.49 | 606.6235 | 619.7299
994.8323 | 469.5193 | 606.5131 | 620.2647
995.8323 | 469.519 | 606.7644 | 621.0875
996.8323 | 469.5193 | 606.6056 | 621.3105
997.8323 | 469.4979 | 606.4631 | 621.6633
998.8323 | 469.5226 | 606.7262 | 622.1121
999.8323 | 469.5437 | 606.8548 | 622.8129
1000.8323 | 469.5543 | 606.749 | 623.3532
1001.8323 | 469.5266 | 606.73 | 623.7178
1002.8323 | 469.4904 | 606.738 | 624.3577
1003.8323 | 469.4818 | 606.6722 | 624.8361
1004.8323 | 469.4735 | 606.832 | 625.3312
1005.8323 | 469.4865 | 606.9932 | 625.8566
1006.8323 | 469.5221 | 606.9049 | 625.7684
1007.8323 | 469.5395 | 607.2288 | 625.6706
1008.8323 | 469.524 | 607.3549 | 626.1072
1009.8323 | 469.558 | 607.3018 | 626.5499
1010.8323 | 469.5666 | 607.2875 | 626.8047
1011.8323 | 469.529 | 607.4568 | 626.4338
1012.8323 | 469.5178 | 607.9597 | 626.2655
1013.8323 | 469.5446 | 607.9227 | 626.4923
1014.8323 | 469.5875 | 607.4286 | 626.7034
1015.8323 | 469.5788 | 606.6936 | 627.0663
1016.8323 | 469.5796 | 606.7295 | 627.4199
1017.8323 | 469.4992 | 606.8792 | 627.2058
1018.8323 | 469.4849 | 607.3591 | 627.137
1019.8323 | 469.5162 | 607.4214 | 627.5932
1020.8323 | 469.5158 | 607.3199 | 628.3064
1021.8323 | 469.4005 | 607.7228 | 628.4911
1022.8323 | 469.2082 | 608.0985 | 628.845
1023.8323 | 468.9499 | 608.4563 | 629.179
1024.8323 | 468.6633 | 608.6653 | 629.4744
1025.8323 | 468.3493 | 608.7756 | 629.7136
1026.8323 | 467.9753 | 608.6367 | 630.0369
1027.8323 | 467.6149 | 608.1181 | 629.8106
1028.8323 | 467.1676 | 608.0065 | 630.1756
1029.8323 | 466.6635 | 607.943 | 630.8405
1030.8323 | 466.1683 | 607.4709 | 631.3698
1031.8323 | 465.6793 | 607.5739 | 631.3989
1032.8323 | 465.171 | 607.5783 | 632.2664
1033.8323 | 464.6614 | 607.4533 | 633.2442
1034.8323 | 464.1542 | 607.0876 | 633.4384
1035.8323 | 463.6493 | 606.2672 | 633.0897
1036.8323 | 463.12 | 605.9563 | 633.5661
1037.8323 | 462.5984 | 606.0213 | 633.8379
1038.8323 | 462.0755 | 606.3135 | 634.686
1039.8323 | 461.5353 | 606.2733 | 634.9735
1040.8323 | 461.0149 | 605.7749 | 635.092
1041.8479 | 460.4747 | 605.2754 | 635.0658
1042.8323 | 459.9481 | 605.3481 | 635.8185
1043.8323 | 459.3876 | 605.0975 | 636.1196
1044.8479 | 458.8146 | 604.7788 | 636.0918
1045.8323 | 458.2864 | 604.639 | 636.144
1047.0042 | 457.652 | 593.96 | 619.9384
1047.8323 | 457.2116 | 604.3703 | 636.2653
1048.8323 | 456.6797 | 604.5171 | 636.6301
1049.8323 | 456.1142 | 604.4018 | 636.3983
1050.8323 | 455.532 | 604.1128 | 636.4406
1051.8323 | 454.9019 | 603.0412 | 635.5868
1052.8323 | 454.2989 | 603.4069 | 636.436
1053.8323 | 453.6821 | 603.8034 | 636.198
1055.0667 | 452.9719 | 598.5859 | 629.1175
1055.8323 | 452.544 | 604.0914 | 637.4277
1056.8479 | 451.9481 | 603.6271 | 637.2605
1057.8323 | 451.3934 | 603.425 | 637.7277
1058.8323 | 450.8226 | 603.1573 | 638.1206
1059.8323 | 450.2651 | 603.339 | 638.5197
1060.8323 | 449.6558 | 602.7537 | 636.904
1062.4573 | 448.6754 | 590.6805 | 620.0152
1062.9885 | 448.3103 | 600.8086 | 635.1794
1063.8323 | 447.7712 | 602.5045 | 638.3237
1064.8479 | 447.2123 | 602.3412 | 638.0059
1065.8323 | 446.6872 | 602.2225 | 637.7784
1066.8323 | 446.1337 | 602.2662 | 637.7136
1067.8635 | 445.56 | 597.4854 | 630.6425
1068.8323 | 445.0419 | 602.5802 | 637.8197