## Test Conditions
DESIREE-FIRE Test Number 25 - Circuit Simulator Data Only
Test Date: | 2009-07-16
DCSim DAQ Start Time | 13:02
DCSim Time for Synchronization | 13:03
Heat Source Synchronization | 4:40 | minutes:seconds
Heat Source DAQ Start Time | 12:58
Fire Time | 13:04
Offset | 0:01 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 70 | seconds
Heat Source Offset | 0:05 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 320 | seconds
Heat Source Stop Time | 13:15
Test Duration | 0:12 | minutes:seconds
| 690 | seconds
CT500 turns | 1 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 1 | 1 or 5
Pre-Test Baseline: | Not Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
MOV 1 | EPR/CSPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
MOV 2 | EPR/CSPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | MOV-1_CT500 | MOV-1a_CT35_1_P | MOV-1a_CT35_2_N | MOV-1b_CT35_1_G | MOV-1b_CT35_2_R | MOV-1b_CT35_3_YO | MOV-1b_CT35_4_YC | MOV-2_CT500 | MOV-2a_CT35_1_P | MOV-2a_CT35_2_N | MOV-2b_CT35_1_G | MOV-2b_CT35_2_R | MOV-2b_CT35_3_YO | 2b_CT35_4_YC1 | MOV-1a_VT7_1_SP | MOV-1a_VTU_1_P | MOV-1a_VTU_2_N | MOV-1b_VT7_1_G | MOV-1b_VT7_2_R | MOV-1b_VT7_3_YO1 | MOV-1b_VT7_4_YC1 | MOV-2a_VT7_1_SP | MOV-2a_VTU_1_P | MOV-2a_VTU_2_N | MOV-2b_VT7_1_G | MOV-2b_VT7_2_R | 2b_VT7_3_YO1 | MOV-2b_VT7_4_YC1 | {MOV1} V(N) - V(Batt -) | {MOV1} V(P) - V(Batt +) | {MOV1} V(G) - V(Batt +) | {MOV1} V(R) - V(Batt -) | {MOV1} V(YC1) - V(Batt -) | {MOV1} V(YO1) - V(Batt -) | {MOV1} V(YC1) - V(N) | {MOV1} V(YO1) - V(N) | {MOV2} V(N) - V(Batt -) | {MOV2} V(P) - V(Batt +) | {MOV2} V(G) - V(Batt +) | {MOV2} V(R) - V(Batt -) | {MOV2} V(YC1) - V(Batt -) | {MOV2} V(YO1) - V(Batt -) | {MOV2} V(YC1) - V(N) | {MOV2} V(YO1) - V(N) | {MOV-1} V(R) - V(N) | {MOV-1} V(G) - V(N) | {MOV-2} V(R) - V(N) | {MOV-2} V(G) - V(N) | {MOV-1} V(P) - V(N) | {MOV-2} V(P) - V(N) | {MOV-1} V(P) - V(Batt -) | {MOV-2} V(P) - V(Batt -) | {MOV-1} V(N) - V(Batt +) | {MOV-2} V(N) - V(Batt +) | {MOV-1} V(G) - V(Batt -) | {MOV2} V(G) - V(Batt-) | {MOV1} V(SP) - V(Batt -) | {MOV2} V(SP) - V(Batt -)
-0.046875 | 123.2208 | -59.5551 | 63.4048 | 0.19033 | 0.0056153 | 0.068989 | 0.059782 | -0.0067466 | 0.015048 | 0.0045582 | 0.24348 | -0.0061336 | 0.080744 | 0.051979 | -0.0074348 | -0.0039768 | -0.0061756 | -0.004578 | 63.2538 | -59.5825 | 63.6887 | -59.5322 | -59.7977 | -59.8343 | 0.041199 | 63.295 | -59.5551 | 63.588 | -59.6283 | -59.6924 | -59.729 | -0.027466 | -0.15106 | 0.28381 | 0.022888 | -0.27924 | -0.24261 | -0.25177 | -0.21515 | 0 | -0.10986 | 0.18311 | -0.073242 | -0.17395 | -0.13733 | -0.17395 | -0.13733 | 0.050354 | 123.2712 | -0.073242 | 123.143 | 122.8363 | 122.85 | 122.8088 | 122.85 | -122.9874 | -122.9599 | 123.2437 | 123.143 | 59.5505 | 59.5963
0.95312 | 123.23 | -59.523 | 63.3957 | 0.0072204 | 0.0034793 | 0.064717 | 0.065123 | 0.0071384 | -0.0020407 | -0.011464 | 0.029861 | -0.012543 | 0.052973 | 0.064796 | 0.0011102 | -0.0071808 | 0.0013004 | -0.009155 | 63.2355 | -59.5734 | 63.5193 | -59.5413 | -59.9167 | -59.8984 | 0.004578 | 63.2629 | -59.5734 | 63.62 | -59.5505 | -59.7107 | -59.6741 | -0.050354 | -0.16022 | 0.1236 | -0.018311 | -0.37537 | -0.39368 | -0.32501 | -0.34332 | -0.050354 | -0.13275 | 0.2243 | -0.027466 | -0.15106 | -0.18768 | -0.10071 | -0.13733 | 0.032043 | 123.0927 | 0.022888 | 123.1934 | 122.8088 | 122.8363 | 122.7585 | 122.7859 | -122.9691 | -122.9691 | 123.0423 | 123.143 | 59.5139 | 59.5276
1.9531 | 123.2574 | -59.5322 | 63.3911 | 0.037738 | -0.0018617 | 0.070057 | 0.067259 | 0.01141 | 0.024662 | 0.00028524 | -0.061691 | -0.0039976 | 0.052973 | 0.049842 | -0.0010258 | -0.0039768 | -0.018994 | 0 | 63.2034 | -59.5917 | 63.5605 | -59.6146 | -59.8755 | -59.8984 | 0.045776 | 63.2492 | -59.5734 | 63.6246 | -59.6008 | -59.6191 | -59.7565 | -0.059509 | -0.18768 | 0.16937 | -0.082397 | -0.36621 | -0.34332 | -0.3067 | -0.28381 | -0.041198 | -0.14191 | 0.23346 | -0.068664 | -0.2243 | -0.086975 | -0.18311 | -0.045777 | -0.022888 | 123.1522 | -0.027466 | 123.1979 | 122.7951 | 122.8226 | 122.7356 | 122.7814 | -122.9828 | -122.9645 | 123.0927 | 123.1567 | 59.5322 | 59.5779
2.9531 | 123.2117 | -59.5505 | 63.4048 | 0.052997 | 0.0034793 | 0.062581 | 0.062986 | -0.0024746 | 0.01398 | 0.0098982 | -0.015915 | 0.0066834 | 0.051905 | 0.065864 | -0.0042298 | 0.0077732 | -0.0061756 | 0.018311 | 63.2126 | -59.5825 | 63.533 | -59.5779 | -59.848 | -59.9213 | -0.004578 | 63.2767 | -59.5642 | 63.5788 | -59.5779 | -59.7107 | -59.6878 | -0.032044 | -0.19226 | 0.12817 | -0.027466 | -0.37079 | -0.29755 | -0.33874 | -0.2655 | -0.013733 | -0.12817 | 0.17395 | -0.027466 | -0.13733 | -0.16022 | -0.1236 | -0.14648 | 0.004578 | 123.1155 | -0.013733 | 123.143 | 122.7951 | 122.8409 | 122.7631 | 122.8271 | -122.9874 | -122.9691 | 123.0835 | 123.1293 | 59.5688 | 59.5459
3.9531 | 123.2025 | -59.5184 | 63.4048 | -0.16063 | -0.0061337 | 0.064717 | 0.059782 | -0.0024746 | 0.016117 | 0.013103 | 0.13667 | 0.0024114 | 0.090358 | 0.071205 | 0.0032462 | 0.0067052 | -0.0083126 | -0.032043 | 63.2172 | -59.5688 | 63.5651 | -59.5688 | -59.8801 | -59.8846 | 0.050354 | 63.2858 | -59.5779 | 63.6337 | -59.5917 | -59.6878 | -59.7382 | -0.050354 | -0.18768 | 0.16022 | -0.050354 | -0.36621 | -0.36163 | -0.31586 | -0.31128 | -0.059509 | -0.11902 | 0.22888 | -0.073242 | -0.21973 | -0.16937 | -0.16022 | -0.10986 | 0 | 123.1338 | -0.013733 | 123.2117 | 122.7859 | 122.8638 | 122.7356 | 122.8043 | -122.9736 | -122.9828 | 123.0835 | 123.1522 | 59.4864 | 59.5688
4.9531 | 123.2162 | -59.5367 | 63.3865 | 0.068255 | -0.0039977 | 0.071125 | 0.059782 | 0.0060704 | -0.020199 | -0.0018508 | 0.10615 | -0.0029296 | 0.056178 | 0.027412 | -0.0085028 | -0.010385 | 0.00023236 | 0.045776 | 63.208 | -59.5825 | 63.5513 | -59.6146 | -59.8572 | -59.9213 | -0.022888 | 63.2721 | -59.5413 | 63.5513 | -59.5413 | -59.7153 | -59.6832 | -0.045777 | -0.17853 | 0.16479 | -0.07782 | -0.38452 | -0.32043 | -0.33874 | -0.27466 | -0.004578 | -0.11444 | 0.16479 | -0.004578 | -0.14648 | -0.17853 | -0.14191 | -0.17395 | -0.032043 | 123.1339 | 0 | 123.0927 | 122.7905 | 122.8134 | 122.7448 | 122.8088 | -122.9691 | -122.9279 | 123.0881 | 123.0881 | 59.5825 | 59.5139
5.9531 | 123.2162 | -59.5322 | 63.382 | -0.13011 | -0.0061337 | 0.066853 | 0.059782 | 0.0017974 | -0.014859 | -0.012532 | -0.015915 | -0.010407 | 0.066859 | 0.065864 | 0.0011102 | -0.0007718 | 0.0013004 | -0.018311 | 63.1989 | -59.5825 | 63.5193 | -59.5596 | -59.9304 | -59.8618 | 0.041199 | 63.2858 | -59.5642 | 63.652 | -59.6329 | -59.6786 | -59.7107 | -0.050354 | -0.1831 | 0.13733 | -0.027465 | -0.32959 | -0.39825 | -0.27923 | -0.3479 | -0.032043 | -0.09613 | 0.27008 | -0.10071 | -0.17853 | -0.14648 | -0.14648 | -0.11444 | 0.022889 | 123.1018 | -0.068665 | 123.2162 | 122.7814 | 122.85 | 122.731 | 122.818 | -122.9645 | -122.9462 | 123.0515 | 123.1842 | 59.5139 | 59.5734
6.9531 | 123.1796 | -59.5276 | 63.414 | 0.0072204 | 0.0056153 | 0.064717 | 0.05551 | 0.0028664 | 0.0011633 | -0.00078276 | 0.16719 | 0.0056154 | 0.0722 | 0.070137 | -0.0085028 | -0.0050448 | 0.015186 | -0.041199 | 63.2263 | -59.61 | 63.6292 | -59.5184 | -59.7702 | -59.8892 | -0.032043 | 63.2629 | -59.5596 | 63.5422 | -59.5276 | -59.761 | -59.7198 | -0.082397 | -0.18768 | 0.21515 | 0.009155 | -0.36163 | -0.24262 | -0.27924 | -0.16022 | -0.032043 | -0.15106 | 0.12817 | 0 | -0.19226 | -0.23346 | -0.16022 | -0.20142 | 0.091552 | 123.2391 | 0.032043 | 123.1018 | 122.8363 | 122.8226 | 122.7539 | 122.7905 | -123.024 | -122.9736 | 123.1567 | 123.0698 | 59.4864 | 59.4955
8.0312 | 123.1293 | -59.5551 | 63.4781 | 0.11403 | -0.0018617 | 0.052968 | 0.059782 | 0.00072943 | -0.0031087 | 0.0077622 | 0.075638 | 0.0013434 | 0.06045 | 0.096839 | 0.011791 | -0.0029078 | -0.00083564 | 0.07782 | 63.2812 | -59.5779 | 63.6749 | -59.4543 | -59.7519 | -59.7656 | -0.009155 | 63.3636 | -59.5459 | 63.5284 | -59.6191 | -59.7839 | -59.7244 | -0.022888 | -0.19684 | 0.19684 | 0.10071 | -0.21057 | -0.19684 | -0.18768 | -0.17395 | 0.009156 | -0.11444 | 0.050354 | -0.064087 | -0.16937 | -0.22888 | -0.17853 | -0.23804 | 0.1236 | 123.2529 | -0.073243 | 123.0743 | 122.8592 | 122.9095 | 122.8363 | 122.9187 | -123.056 | -123.024 | 123.23 | 123.0835 | 59.6329 | 59.5459
8.9531 | 123.1934 | -59.5413 | 63.3957 | -0.023297 | 0.0024113 | 0.071125 | 0.056578 | 0.00072943 | 0.0097083 | 0.014171 | 0.13667 | -0.0082696 | 0.078608 | 0.043434 | 0.0043152 | -0.0071808 | 0.01305 | 0.013733 | 63.2355 | -59.5688 | 63.5971 | -59.5917 | -59.8526 | -59.9075 | 0.036621 | 63.2721 | -59.5688 | 63.5971 | -59.5779 | -59.7198 | -59.6878 | -0.027466 | -0.16022 | 0.20142 | -0.050354 | -0.36621 | -0.31128 | -0.33875 | -0.28381 | -0.027466 | -0.1236 | 0.20142 | -0.036621 | -0.14648 | -0.17853 | -0.11902 | -0.15106 | -0.022888 | 123.1659 | -0.009155 | 123.1659 | 122.8043 | 122.8409 | 122.7768 | 122.8134 | -122.9645 | -122.9645 | 123.1384 | 123.1384 | 59.5551 | 59.5779
10.0312 | 123.1613 | -59.5551 | 63.4689 | 0.098773 | 0.0045473 | 0.063649 | 0.067259 | -0.0078156 | -0.013791 | 0.0045582 | 0.15193 | 0.0034794 | 0.064723 | 0.08509 | 0.0064512 | 0.0045682 | 0.0034374 | 0.07782 | 63.2538 | -59.5596 | 63.6246 | -59.5047 | -59.7656 | -59.8389 | 0.032043 | 63.3179 | -59.5596 | 63.5147 | -59.5688 | -59.7519 | -59.7336 | -0.004577 | -0.21515 | 0.15564 | 0.050354 | -0.28381 | -0.21057 | -0.27924 | -0.20599 | -0.004577 | -0.15106 | 0.045776 | -0.013733 | -0.17853 | -0.19684 | -0.17395 | -0.19226 | 0.054931 | 123.1842 | -0.009156 | 123.0743 | 122.8134 | 122.8775 | 122.8088 | 122.8729 | -123.0286 | -123.0286 | 123.1796 | 123.0698 | 59.6329 | 59.5871
10.9531 | 123.1934 | -59.5688 | 63.4186 | 0.052997 | -0.0050657 | 0.064717 | 0.048033 | 0.019955 | 0.015048 | -0.0039868 | 0.12141 | 0.0013434 | 0.07754 | 0.044502 | 0.0011102 | 0.0045682 | -0.0029716 | -0.022888 | 63.2446 | -59.5734 | 63.6887 | -59.5322 | -59.7931 | -59.8206 | 0.018311 | 63.3087 | -59.5734 | 63.5559 | -59.6329 | -59.7015 | -59.7244 | -0.004577 | -0.17395 | 0.27008 | 0.036621 | -0.25177 | -0.2243 | -0.24719 | -0.21973 | -0.004577 | -0.10986 | 0.13733 | -0.064087 | -0.15564 | -0.13275 | -0.15106 | -0.12817 | 0.041198 | 123.262 | -0.05951 | 123.1293 | 122.818 | 122.8821 | 122.8134 | 122.8775 | -122.9919 | -122.9919 | 123.2574 | 123.1247 | 59.5459 | 59.5871
12.0312 | 123.1934 | -59.5413 | 63.4506 | 0.12929 | 0.0034793 | 0.070057 | 0.061918 | -0.012088 | 9.5287e-05 | 0.010966 | 0.075638 | 0.0002754 | 0.065791 | 0.10111 | -0.0074348 | -0.0018398 | 0.024799 | 0.12817 | 63.2721 | -59.5596 | 63.6475 | -59.5184 | -59.7794 | -59.8297 | 0.073242 | 63.3179 | -59.5367 | 63.5513 | -59.5551 | -59.7107 | -59.7061 | -0.01831 | -0.17853 | 0.19684 | 0.022888 | -0.28839 | -0.23804 | -0.27008 | -0.21973 | 0.004578 | -0.13275 | 0.10071 | -0.013733 | -0.16479 | -0.16937 | -0.16937 | -0.17395 | 0.041198 | 123.2071 | -0.018311 | 123.0881 | 122.8317 | 122.8546 | 122.8134 | 122.8592 | -123.0103 | -122.9874 | 123.1888 | 123.0927 | 59.6695 | 59.6146
12.9531 | 123.2346 | -59.5413 | 63.382 | 0.0072204 | -0.0029297 | 0.067921 | 0.067259 | -0.0046106 | 0.0022313 | -0.0093278 | -0.046432 | -0.0093376 | 0.045497 | 0.053047 | -0.0020938 | -0.0071808 | -0.033947 | 0 | 63.2217 | -59.61 | 63.5422 | -59.5917 | -59.8846 | -59.8892 | 0.045776 | 63.2858 | -59.5642 | 63.6154 | -59.5963 | -59.6008 | -59.7336 | -0.068664 | -0.16022 | 0.16022 | -0.050354 | -0.3479 | -0.34332 | -0.27924 | -0.27466 | -0.022888 | -0.09613 | 0.23346 | -0.054931 | -0.19226 | -0.059509 | -0.16937 | -0.036621 | 0.01831 | 123.1522 | -0.032043 | 123.1796 | 122.8317 | 122.85 | 122.7631 | 122.8271 | -122.9919 | -122.9462 | 123.0835 | 123.1567 | 59.5413 | 59.5871
14.0312 | 123.1201 | -59.5551 | 63.446 | 0.17507 | 0.00027529 | 0.051899 | 0.054442 | 0.012479 | 0.0011633 | -0.00078276 | -0.046432 | 0.0034794 | 0.056178 | 0.071205 | -0.0031618 | -0.0061128 | -0.017926 | 0.032043 | 63.2904 | -59.5917 | 63.7482 | -59.404 | -59.6924 | -59.7336 | -0.032043 | 63.3682 | -59.5688 | 63.5101 | -59.6283 | -59.7656 | -59.7656 | -0.036621 | -0.15564 | 0.30212 | 0.15106 | -0.17853 | -0.13733 | -0.14191 | -0.10071 | -0.013733 | -0.07782 | 0.064087 | -0.073242 | -0.21057 | -0.21057 | -0.19684 | -0.19684 | 0.18768 | 123.3398 | -0.059509 | 123.0789 | 122.8821 | 122.937 | 122.8455 | 122.9233 | -123.0377 | -123.0148 | 123.3032 | 123.0652 | 59.5871 | 59.523
14.9531 | 123.2803 | -59.5093 | 63.4003 | 0.14455 | -0.0039977 | 0.062581 | 0.053373 | 0.01141 | 0.023593 | 0.0066942 | 0.060379 | -0.0061336 | 0.073268 | 0.048774 | -0.0052988 | 0.0002962 | 0.00023236 | 0.018311 | 63.2401 | -59.5779 | 63.62 | -59.5413 | -59.848 | -59.8618 | 0.10529 | 63.2858 | -59.5413 | 63.6566 | -59.5139 | -59.6054 | -59.6741 | -0.068665 | -0.16022 | 0.21973 | -0.032044 | -0.35248 | -0.33875 | -0.28381 | -0.27008 | -0.032044 | -0.11444 | 0.25635 | -0.004578 | -0.1648 | -0.096131 | -0.13275 | -0.064087 | 0.036621 | 123.1979 | 0.027466 | 123.1979 | 122.818 | 122.8271 | 122.7493 | 122.7951 | -122.9782 | -122.9416 | 123.1293 | 123.1659 | 59.5276 | 59.6146
16.0312 | 123.1064 | -59.5276 | 63.4644 | 0.19033 | 0.0066833 | 0.064717 | 0.056578 | -0.0035426 | -0.0063137 | -0.0029188 | 0.075638 | -0.010407 | 0.068995 | 0.069068 | 0.0043152 | -0.0071808 | 0.01305 | 0.022888 | 63.3087 | -59.5871 | 63.7756 | -59.4452 | -59.697 | -59.7061 | 0.009155 | 63.3682 | -59.5642 | 63.5193 | -59.6603 | -59.7473 | -59.7656 | -0.059509 | -0.15564 | 0.31128 | 0.082398 | -0.17853 | -0.16937 | -0.11902 | -0.10986 | -0.036621 | -0.09613 | 0.054932 | -0.13275 | -0.23804 | -0.21973 | -0.20142 | -0.18311 | 0.14191 | 123.3627 | -0.09613 | 123.0835 | 122.8958 | 122.9324 | 122.8363 | 122.8958 | -123.0515 | -123.0286 | 123.3032 | 123.0469 | 59.5505 | 59.5367
16.9531 | 123.262 | -59.523 | 63.3957 | 0.068255 | 0.0066833 | 0.062581 | 0.053373 | -0.013156 | 0.016117 | 0.014171 | 0.13667 | 0.0002754 | 0.062587 | 0.066932 | -0.0052988 | -0.0018398 | 0.0013004 | -0.022888 | 63.1714 | -59.5963 | 63.5376 | -59.5459 | -59.9396 | -59.8618 | 0.036621 | 63.2721 | -59.5688 | 63.652 | -59.6191 | -59.6649 | -59.697 | -0.073242 | -0.2243 | 0.14191 | -0.022888 | -0.33875 | -0.41656 | -0.2655 | -0.34332 | -0.045777 | -0.1236 | 0.25635 | -0.096131 | -0.17395 | -0.14191 | -0.12817 | -0.09613 | 0.050354 | 123.1338 | -0.050354 | 123.2208 | 122.7676 | 122.8409 | 122.6944 | 122.7951 | -122.9919 | -122.9645 | 123.0606 | 123.175 | 59.5001 | 59.5596
18.0312 | 123.1064 | -59.5459 | 63.4689 | 0.20559 | 0.0024113 | 0.059376 | 0.058714 | 0.0028664 | 0.0086403 | -0.00078276 | 0.10615 | -0.0007936 | 0.06045 | 0.031684 | 0.0085872 | -0.0071808 | 0.01305 | 0.064087 | 63.2675 | -59.5505 | 63.6749 | -59.4727 | -59.761 | -59.7519 | 0.013733 | 63.3316 | -59.5779 | 63.5422 | -59.6283 | -59.7015 | -59.8206 | -0.004578 | -0.20142 | 0.20599 | 0.073242 | -0.20599 | -0.21515 | -0.20142 | -0.21057 | -0.032044 | -0.13733 | 0.073242 | -0.082398 | -0.27466 | -0.15564 | -0.24262 | -0.1236 | 0.07782 | 123.2254 | -0.050354 | 123.1201 | 122.818 | 122.9095 | 122.8134 | 122.8775 | -123.0194 | -123.0469 | 123.2208 | 123.0881 | 59.61 | 59.5596
18.9531 | 123.2391 | -59.5322 | 63.3774 | -0.038556 | -0.0018617 | 0.062581 | 0.066191 | -0.0014066 | -0.0020407 | 0.014171 | 0.13667 | -0.010407 | 0.051905 | 0.018867 | -0.0010258 | 0.0024322 | 0.0013004 | -0.018311 | 63.1897 | -59.5917 | 63.533 | -59.5688 | -59.8984 | -59.8343 | 0.004578 | 63.2446 | -59.5642 | 63.62 | -59.5779 | -59.6924 | -59.6649 | -0.059509 | -0.18768 | 0.15564 | -0.036621 | -0.30212 | -0.36621 | -0.24262 | -0.3067 | -0.032043 | -0.13275 | 0.24262 | -0.045776 | -0.13275 | -0.16022 | -0.10071 | -0.12817 | 0.022888 | 123.1247 | -0.013733 | 123.1842 | 122.7814 | 122.8088 | 122.7219 | 122.7768 | -122.9691 | -122.9416 | 123.0652 | 123.1522 | 59.5139 | 59.5367
19.9531 | 123.2666 | -59.5184 | 63.3957 | 0.037738 | -0.0072017 | 0.068989 | 0.053373 | 0.0028664 | 0.0011633 | 0.0056262 | 0.16719 | -0.0029296 | 0.078608 | 0.063728 | 0.0064512 | -0.0018398 | 0.0066414 | 0.013733 | 63.2217 | -59.5871 | 63.5788 | -59.6146 | -59.8755 | -59.935 | 0.027466 | 63.2675 | -59.5551 | 63.6063 | -59.5505 | -59.697 | -59.6558 | -0.068664 | -0.17395 | 0.1831 | -0.09613 | -0.41656 | -0.35705 | -0.3479 | -0.28839 | -0.036621 | -0.12817 | 0.21057 | -0.032043 | -0.13733 | -0.17853 | -0.10071 | -0.14191 | -0.027466 | 123.1659 | 0.004578 | 123.1613 | 122.8088 | 122.8226 | 122.7402 | 122.7859 | -122.9828 | -122.9507 | 123.0972 | 123.1247 | 59.5322 | 59.5459
21.0156 | 123.0927 | -59.5779 | 63.4369 | -0.038556 | 0.0077523 | 0.075398 | 0.06085 | 0.00072943 | 0.0043673 | -0.00078276 | -0.12273 | 0.0045474 | 0.065791 | 0.081886 | 0.0053832 | -0.0029078 | -0.0093806 | 0 | 63.2904 | -59.6283 | 63.6749 | -59.4177 | -59.7244 | -59.7382 | -0.20599 | 63.3408 | -59.5734 | 63.446 | -59.7061 | -59.8938 | -59.7931 | -0.050354 | -0.14648 | 0.23804 | 0.16022 | -0.16022 | -0.14648 | -0.10986 | -0.09613 | 0.004578 | -0.096131 | 0.009155 | -0.12817 | -0.21515 | -0.31586 | -0.21973 | -0.32044 | 0.21057 | 123.3032 | -0.13275 | 123.0194 | 122.9187 | 122.9141 | 122.8683 | 122.9187 | -123.0652 | -123.0103 | 123.2529 | 123.024 | 59.5779 | 59.3719
21.9531 | 123.23 | -59.5596 | 63.3591 | -0.069074 | 0.0045473 | 0.067921 | 0.065123 | 0.00072943 | -0.0052457 | 0.0045582 | -0.046432 | 0.0002754 | 0.056178 | 0.063728 | 0.0096552 | 0.0002962 | 0.014118 | -0.045776 | 63.2355 | -59.6054 | 63.6795 | -59.5505 | -59.7885 | -59.8343 | 0.009155 | 63.2996 | -59.6008 | 63.6063 | -59.5871 | -59.6924 | -59.697 | -0.045777 | -0.1236 | 0.32043 | 0.009155 | -0.27466 | -0.22888 | -0.22888 | -0.18311 | -0.041199 | -0.059509 | 0.24719 | -0.027466 | -0.13733 | -0.13275 | -0.09613 | -0.091553 | 0.054932 | 123.2849 | 0.013733 | 123.2071 | 122.8409 | 122.9004 | 122.7951 | 122.8592 | -122.9645 | -122.9599 | 123.2391 | 123.1659 | 59.5139 | 59.5688
22.9531 | 123.2025 | -59.5367 | 63.4003 | 0.17507 | 0.00027529 | 0.071125 | 0.059782 | 0.00072943 | -0.0052457 | 0.014171 | 0.090897 | 0.0002754 | 0.071131 | 0.073341 | 0.0053832 | -0.0061128 | -0.015789 | -0.022888 | 63.2263 | -59.5688 | 63.501 | -59.5459 | -59.903 | -59.8846 | -0.009155 | 63.2584 | -59.5596 | 63.6246 | -59.5367 | -59.7427 | -59.6466 | -0.032044 | -0.17395 | 0.10071 | -0.009155 | -0.3479 | -0.36621 | -0.31586 | -0.33417 | -0.022888 | -0.14191 | 0.2243 | 0 | -0.10986 | -0.20599 | -0.086975 | -0.18311 | 0.022889 | 123.0698 | 0.022888 | 123.1842 | 122.7951 | 122.818 | 122.7631 | 122.7951 | -122.9691 | -122.9599 | 123.0377 | 123.1613 | 59.5139 | 59.5276
24.0312 | 123.2941 | -59.5093 | 63.4323 | 0.12929 | -0.0018617 | 0.062581 | 0.065123 | -0.027042 | 0.0054353 | 0.0024222 | 0.24348 | -0.010407 | 0.066859 | 0.055183 | 4.2208e-05 | -0.0039768 | -0.00083564 | 0.004578 | 63.2492 | -59.5413 | 63.533 | -59.5276 | -59.8892 | -59.848 | 0.1236 | 63.2904 | -59.5322 | 63.6932 | -59.5139 | -59.5963 | -59.6512 | -0.032044 | -0.18311 | 0.10071 | -0.018311 | -0.33875 | -0.37994 | -0.3067 | -0.3479 | -0.022889 | -0.14191 | 0.26093 | -0.004578 | -0.14191 | -0.086975 | -0.11902 | -0.064086 | 0.013733 | 123.0743 | 0.018311 | 123.2254 | 122.7905 | 122.8226 | 122.7585 | 122.7997 | -122.9736 | -122.9645 | 123.0423 | 123.2025 | 59.5139 | 59.6329
24.9531 | 123.2574 | -59.5184 | 63.4369 | 0.15981 | 0.0013433 | 0.060444 | 0.059782 | -0.0078156 | 0.0011633 | 0.0056262 | 0.274 | -0.0082696 | 0.064723 | 0.077613 | 0.0064512 | -0.0029078 | -0.012585 | 0.054932 | 63.2309 | -59.5505 | 63.5605 | -59.5688 | -59.8755 | -59.8663 | 0.11444 | 63.3041 | -59.5322 | 63.6612 | -59.4681 | -59.6191 | -59.5779 | -0.032043 | -0.20599 | 0.1236 | -0.050354 | -0.3479 | -0.35705 | -0.31586 | -0.32501 | -0.013733 | -0.13275 | 0.2243 | 0.050354 | -0.059509 | -0.10071 | -0.045776 | -0.086975 | -0.018311 | 123.111 | 0.064087 | 123.1934 | 122.7814 | 122.8363 | 122.7493 | 122.8226 | -122.9874 | -122.9691 | 123.0789 | 123.1796 | 59.5734 | 59.6329
26.0312 | 123.2529 | -59.4955 | 63.4369 | 0.17507 | -0.0072017 | 0.063649 | 0.064055 | 0.0082064 | -0.0095177 | 0.0024222 | 0.060379 | -0.0018616 | 0.068995 | 0.047706 | -0.0042298 | -0.016794 | 0.0034374 | 0.073242 | 63.2401 | -59.5413 | 63.5284 | -59.5779 | -59.903 | -59.8938 | 0.09613 | 63.3133 | -59.5413 | 63.652 | -59.5139 | -59.6283 | -59.6603 | -0.045777 | -0.19684 | 0.091552 | -0.082398 | -0.39825 | -0.40741 | -0.35248 | -0.36163 | -0.045777 | -0.1236 | 0.21515 | -0.018311 | -0.16479 | -0.13275 | -0.11902 | -0.086975 | -0.036621 | 123.0698 | 0.027466 | 123.1934 | 122.7814 | 122.8546 | 122.7356 | 122.8088 | -122.9782 | -122.9782 | 123.024 | 123.1476 | 59.5688 | 59.5917
26.9688 | 123.2025 | -59.5596 | 63.4369 | 0.11403 | -0.0072017 | 0.072194 | 0.06085 | 0.0017974 | -0.011654 | -0.011464 | 0.25874 | 0.0066834 | 0.076472 | 0.05091 | -0.0074348 | -0.019998 | 0.014118 | -0.009155 | 63.2217 | -59.5734 | 63.6108 | -59.5001 | -59.7931 | -59.8801 | -0.027466 | 63.2996 | -59.5367 | 63.5651 | -59.5642 | -59.7885 | -59.6741 | -0.013733 | -0.21515 | 0.17395 | 0.059509 | -0.32043 | -0.23346 | -0.3067 | -0.21973 | 0.022888 | -0.13733 | 0.12817 | -0.004578 | -0.11444 | -0.22888 | -0.13733 | -0.25177 | 0.073242 | 123.1842 | -0.027466 | 123.1018 | 122.7951 | 122.8363 | 122.7814 | 122.8592 | -123.0103 | -122.9736 | 123.1705 | 123.1247 | 59.5505 | 59.5322
28.0312 | 123.262 | -59.5093 | 63.4415 | 0.052997 | 0.0045473 | 0.062581 | 0.057646 | 0.0039344 | -0.015927 | 0.0077622 | 0.274 | 0.0013434 | 0.057246 | 0.016731 | 0.0021782 | -0.0018398 | 0.011982 | 0.045776 | 63.2355 | -59.5551 | 63.5376 | -59.5596 | -59.8709 | -59.8618 | 0.10986 | 63.295 | -59.523 | 63.6475 | -59.4681 | -59.6283 | -59.5917 | -0.045777 | -0.20599 | 0.096131 | -0.050354 | -0.35248 | -0.36163 | -0.3067 | -0.31586 | -0.013733 | -0.14648 | 0.20599 | 0.041198 | -0.082398 | -0.11902 | -0.068665 | -0.10529 | -0.004577 | 123.0927 | 0.054931 | 123.1705 | 122.7905 | 122.818 | 122.7448 | 122.8043 | -122.9965 | -122.9645 | 123.0469 | 123.1567 | 59.5551 | 59.6191
28.9531 | 123.2208 | -59.523 | 63.382 | 0.083514 | -0.0050657 | 0.062581 | 0.075804 | 0.0060704 | -0.023404 | -0.011464 | -0.22954 | -0.0061336 | 0.063655 | 0.076545 | 4.2208e-05 | 0.0035002 | -0.00083564 | -0.022888 | 63.2355 | -59.6008 | 63.6017 | -59.5596 | -59.7977 | -59.903 | -0.027466 | 63.2812 | -59.5734 | 63.5742 | -59.5413 | -59.7427 | -59.6649 | -0.07782 | -0.14648 | 0.21973 | -0.036621 | -0.37994 | -0.27466 | -0.30212 | -0.19684 | -0.050354 | -0.10071 | 0.19226 | -0.018311 | -0.14191 | -0.21973 | -0.091553 | -0.16937 | 0.041199 | 123.2025 | 0.032043 | 123.1476 | 122.8363 | 122.8546 | 122.7585 | 122.8043 | -122.9828 | -122.9553 | 123.1247 | 123.0972 | 59.5001 | 59.4955
30.0312 | 123.1842 | -59.5276 | 63.4323 | 0.083514 | -0.0018617 | 0.065785 | 0.04376 | -0.0067466 | 0.0054353 | 0.0045582 | 0.13667 | 0.0066834 | 0.061518 | 0.076545 | -0.0020938 | -0.0061128 | -0.0083126 | 0.022888 | 63.2309 | -59.5688 | 63.5742 | -59.4818 | -59.8114 | -59.8434 | -0.086975 | 63.2904 | -59.5596 | 63.5605 | -59.5413 | -59.7198 | -59.6786 | -0.041199 | -0.20142 | 0.14191 | 0.045776 | -0.31586 | -0.28381 | -0.27466 | -0.24261 | -0.032043 | -0.14191 | 0.12817 | -0.013733 | -0.15106 | -0.19226 | -0.11902 | -0.16022 | 0.086975 | 123.143 | 0.01831 | 123.1201 | 122.7997 | 122.85 | 122.7585 | 122.818 | -123.0011 | -122.9919 | 123.1018 | 123.0881 | 59.5505 | 59.4406
30.9531 | 123.1842 | -59.5596 | 63.3774 | 0.0072204 | 0.0034793 | 0.064717 | 0.059782 | -0.0099516 | -0.015927 | -0.017873 | -0.12273 | 0.0034794 | 0.064723 | 0.053047 | -0.0020938 | -0.0039768 | -0.0040396 | -0.050354 | 63.2584 | -59.6146 | 63.6795 | -59.5413 | -59.7748 | -59.8251 | -0.050354 | 63.3087 | -59.5825 | 63.5468 | -59.6054 | -59.7656 | -59.7382 | -0.054932 | -0.11902 | 0.30212 | 0.01831 | -0.2655 | -0.21515 | -0.21057 | -0.16022 | -0.022889 | -0.068664 | 0.16937 | -0.045777 | -0.17853 | -0.20599 | -0.15564 | -0.1831 | 0.073242 | 123.2941 | -0.022888 | 123.1293 | 122.8729 | 122.8912 | 122.818 | 122.8683 | -122.9919 | -122.9599 | 123.2391 | 123.1064 | 59.5093 | 59.5093
31.9531 | 123.2712 | -59.523 | 63.382 | -0.084332 | 0.0056153 | 0.060444 | 0.059782 | -0.021701 | -0.0052457 | 0.0034902 | -0.015915 | -0.0061336 | 0.07754 | 0.056251 | 0.0043152 | -0.010385 | -0.013653 | -0.036621 | 63.2263 | -59.5917 | 63.4781 | -59.5642 | -59.9121 | -59.8801 | -0.004578 | 63.2675 | -59.5734 | 63.6337 | -59.5642 | -59.7107 | -59.6649 | -0.068665 | -0.15564 | 0.09613 | -0.041199 | -0.35706 | -0.3891 | -0.28839 | -0.32043 | -0.050354 | -0.11444 | 0.25177 | -0.041199 | -0.14191 | -0.18768 | -0.091553 | -0.13733 | 0.027466 | 123.0698 | 0.009155 | 123.2071 | 122.818 | 122.8409 | 122.7493 | 122.7905 | -122.9736 | -122.9553 | 123.0011 | 123.1567 | 59.4864 | 59.5184
33.0312 | 123.2666 | -59.5322 | 63.4048 | 0.022479 | 0.0034793 | 0.065785 | 0.05551 | -0.00033857 | 0.011844 | 0.0013532 | 0.24348 | -0.0018616 | 0.063655 | 0.075477 | -0.0085028 | 0.0099092 | -0.0083126 | 0.07782 | 63.2675 | -59.5367 | 63.5468 | -59.5505 | -59.9304 | -59.8572 | 0.15106 | 63.3133 | -59.5184 | 63.6887 | -59.5596 | -59.6008 | -59.6512 | -0.004577 | -0.13733 | 0.14191 | -0.01831 | -0.32501 | -0.39825 | -0.32043 | -0.39368 | 0.013733 | -0.091553 | 0.28381 | -0.027465 | -0.11902 | -0.068664 | -0.13275 | -0.082397 | -0.013733 | 123.0835 | -0.041198 | 123.2071 | 122.8043 | 122.8317 | 122.7997 | 122.8455 | -122.9416 | -122.9233 | 123.0789 | 123.2208 | 59.61 | 59.6832
33.9531 | 123.2254 | -59.5367 | 63.4232 | 0.083514 | 0.0013433 | 0.070057 | 0.053373 | 0.013547 | 0.010776 | 0.0024222 | -0.046432 | 0.0002754 | 0.049769 | 0.076545 | -0.0042298 | 0.0013642 | 0.0055734 | 0 | 63.2172 | -59.6054 | 63.5422 | -59.5322 | -59.8892 | -59.8984 | -0.013733 | 63.2584 | -59.5688 | 63.6154 | -59.5276 | -59.7107 | -59.642 | -0.068665 | -0.20599 | 0.11902 | 0.004577 | -0.36163 | -0.35248 | -0.29297 | -0.28381 | -0.032044 | -0.1648 | 0.19226 | 0.009155 | -0.10529 | -0.17395 | -0.073242 | -0.14191 | 0.073242 | 123.1476 | 0.041199 | 123.1842 | 122.8226 | 122.8271 | 122.7539 | 122.7951 | -123.0286 | -122.9919 | 123.0789 | 123.1522 | 59.5367 | 59.523
35.0312 | 123.2162 | -59.5276 | 63.382 | 0.098773 | -0.0039977 | 0.062581 | 0.067259 | -0.0088836 | 0.023593 | 0.0045582 | 0.21297 | 0.0056154 | 0.06045 | 0.076545 | -0.0010258 | -0.0039768 | 0.00023236 | -0.050354 | 63.2584 | -59.5917 | 63.5651 | -59.5047 | -59.8618 | -59.7702 | 0.018311 | 63.2767 | -59.5551 | 63.6063 | -59.5688 | -59.6375 | -59.697 | -0.064087 | -0.1236 | 0.18311 | 0.022888 | -0.24262 | -0.33417 | -0.17853 | -0.27008 | -0.027466 | -0.10529 | 0.2243 | -0.041199 | -0.16937 | -0.10986 | -0.14191 | -0.082397 | 0.086975 | 123.1567 | -0.013733 | 123.1613 | 122.85 | 122.8317 | 122.7859 | 122.8043 | -122.9736 | -122.937 | 123.0927 | 123.1338 | 59.4772 | 59.5459
35.9531 | 123.2162 | -59.5413 | 63.4277 | 0.17507 | -0.0029297 | 0.066853 | 0.059782 | -0.013156 | 0.018253 | -0.00078276 | 0.014603 | -0.0050656 | 0.058314 | 0.056251 | -0.0010258 | 0.0013642 | -0.016858 | -0.027466 | 63.2309 | -59.5871 | 63.6063 | -59.4955 | -59.7977 | -59.8434 | -0.032043 | 63.2996 | -59.5779 | 63.5696 | -59.5779 | -59.761 | -59.6512 | -0.045776 | -0.19684 | 0.17853 | 0.045777 | -0.30212 | -0.25635 | -0.25635 | -0.21057 | -0.036621 | -0.12817 | 0.14191 | -0.036621 | -0.10986 | -0.21973 | -0.073242 | -0.1831 | 0.091553 | 123.1934 | 0 | 123.1476 | 122.818 | 122.8775 | 122.7722 | 122.8409 | -123.0148 | -123.0057 | 123.1476 | 123.111 | 59.5139 | 59.5093
37.0312 | 123.2346 | -59.523 | 63.4186 | -0.038556 | 0.00027529 | 0.062581 | 0.070463 | -0.0024746 | -0.011654 | -0.015736 | 0.36555 | 0.0013434 | 0.073268 | 0.064796 | -0.0031618 | -0.0018398 | -0.00083564 | 0 | 63.2355 | -59.5734 | 63.5468 | -59.4955 | -59.8709 | -59.8343 | 0.027466 | 63.3179 | -59.5688 | 63.6063 | -59.523 | -59.6283 | -59.6466 | -0.050354 | -0.1831 | 0.12817 | 0.027466 | -0.31128 | -0.3479 | -0.26093 | -0.29755 | -0.045777 | -0.10071 | 0.18768 | 0 | -0.1236 | -0.10529 | -0.077819 | -0.059509 | 0.07782 | 123.1201 | 0.045777 | 123.175 | 122.8088 | 122.8867 | 122.7585 | 122.8409 | -122.9919 | -122.9874 | 123.0698 | 123.1293 | 59.523 | 59.5505
37.9531 | 123.2346 | -59.5184 | 63.4048 | 0.068255 | -0.00079271 | 0.071125 | 0.067259 | 0.0071384 | -0.0095177 | 0.00028524 | 0.014603 | -0.0007936 | 0.062587 | 0.07975 | -0.0010258 | 0.0035002 | -0.011517 | 0.027466 | 63.2446 | -59.5917 | 63.5559 | -59.5963 | -59.8572 | -59.903 | -0.009155 | 63.2767 | -59.5734 | 63.5696 | -59.5505 | -59.7015 | -59.6603 | -0.073242 | -0.16022 | 0.15106 | -0.077819 | -0.38452 | -0.33874 | -0.31128 | -0.2655 | -0.054931 | -0.12817 | 0.16479 | -0.032043 | -0.14191 | -0.1831 | -0.086975 | -0.12817 | -0.004577 | 123.1476 | 0.022888 | 123.143 | 122.8363 | 122.85 | 122.7631 | 122.7951 | -122.9965 | -122.9782 | 123.0743 | 123.0881 | 59.5459 | 59.5093
39.0312 | 123.2437 | -59.5047 | 63.382 | 0.098773 | -0.0018617 | 0.061512 | 0.058714 | -0.012088 | -0.016995 | 0.019511 | 0.13667 | -0.0039976 | 0.06045 | 0.081886 | 0.0011102 | -0.0007718 | -0.0051076 | 0.032043 | 63.2858 | -59.5734 | 63.5605 | -59.4955 | -59.8801 | -59.8618 | 0.086975 | 63.3133 | -59.5047 | 63.6383 | -59.5001 | -59.6329 | -59.61 | -0.068664 | -0.09613 | 0.17853 | 0.009156 | -0.35706 | -0.37537 | -0.28839 | -0.3067 | 0 | -0.068665 | 0.25635 | 0.004578 | -0.10529 | -0.12817 | -0.10529 | -0.12817 | 0.07782 | 123.1338 | 0.004578 | 123.143 | 122.8592 | 122.818 | 122.7905 | 122.818 | -122.9553 | -122.8867 | 123.0652 | 123.143 | 59.5367 | 59.5917
39.9531 | 123.1934 | -59.5459 | 63.4094 | 0.083514 | 0.0024113 | 0.058308 | 0.069395 | 0.00072943 | -0.0063137 | 0.0045582 | 0.18245 | 0.0013434 | 0.064723 | 0.071205 | -0.0020938 | -0.0029078 | 0.019458 | -0.022888 | 63.2217 | -59.6054 | 63.6108 | -59.5184 | -59.761 | -59.8801 | -0.032043 | 63.3133 | -59.5459 | 63.5284 | -59.5322 | -59.7473 | -59.697 | -0.05951 | -0.18768 | 0.20142 | 0.027465 | -0.33417 | -0.21515 | -0.27466 | -0.15564 | 0 | -0.096131 | 0.11902 | 0.013732 | -0.15106 | -0.20142 | -0.15106 | -0.20142 | 0.086975 | 123.2162 | 0.013732 | 123.0743 | 122.8271 | 122.8592 | 122.7676 | 122.8592 | -123.0148 | -122.9553 | 123.1567 | 123.0743 | 59.523 | 59.5139
41.0312 | 123.2117 | -59.5276 | 63.4277 | 0.11403 | -0.00079271 | 0.058308 | 0.057646 | -0.0056786 | -0.0041777 | 0.00028524 | 0.19771 | -0.0018616 | 0.079676 | 0.054115 | 0.0011102 | -0.0061128 | 0.0023694 | 0.013733 | 63.2492 | -59.5779 | 63.6063 | -59.5093 | -59.8068 | -59.848 | -0.032043 | 63.295 | -59.5688 | 63.5696 | -59.5779 | -59.7473 | -59.6375 | -0.050354 | -0.17853 | 0.17853 | 0.018311 | -0.32043 | -0.27924 | -0.27008 | -0.22888 | -0.041199 | -0.13275 | 0.14191 | -0.050354 | -0.10986 | -0.21973 | -0.068664 | -0.17853 | 0.068665 | 123.1842 | -0.009155 | 123.1384 | 122.8271 | 122.8638 | 122.7768 | 122.8226 | -123.0057 | -122.9965 | 123.1338 | 123.0972 | 59.5413 | 59.4955
41.9531 | 123.0972 | -59.5734 | 63.4277 | 0.068255 | -0.0061337 | 0.058308 | 0.0726 | -0.0078156 | -0.0020407 | -0.0061228 | -0.22954 | 0.0077514 | 0.06045 | 0.093635 | 4.2208e-05 | 0.0077732 | 0.0087774 | -0.018311 | 63.2584 | -59.6283 | 63.7207 | -59.4269 | -59.7244 | -59.7519 | -0.13275 | 63.327 | -59.5917 | 63.4689 | -59.7198 | -59.8892 | -59.8114 | -0.054932 | -0.16937 | 0.29297 | 0.14648 | -0.17853 | -0.15106 | -0.1236 | -0.09613 | -0.018311 | -0.10071 | 0.041199 | -0.14649 | -0.23804 | -0.31586 | -0.21973 | -0.29755 | 0.20142 | 123.349 | -0.12817 | 123.0606 | 122.8867 | 122.9187 | 122.8317 | 122.9004 | -123.056 | -123.0194 | 123.2941 | 123.0423 | 59.5551 | 59.4406
43.0312 | 123.1979 | -59.5139 | 63.382 | -0.023297 | -0.0029297 | 0.077534 | 0.057646 | -0.01102 | -0.014859 | -0.0082598 | 0.060379 | -0.0082696 | 0.048701 | 0.073341 | 0.0064512 | 0.0035002 | 0.01839 | -0.018311 | 63.2217 | -59.61 | 63.5834 | -59.5367 | -59.8068 | -59.9075 | -0.027466 | 63.2812 | -59.5825 | 63.5696 | -59.5734 | -59.761 | -59.6878 | -0.09613 | -0.16022 | 0.20142 | -0.022888 | -0.39368 | -0.29297 | -0.29755 | -0.19684 | -0.068665 | -0.10071 | 0.18768 | -0.059509 | -0.17395 | -0.24719 | -0.10528 | -0.17853 | 0.073242 | 123.1934 | 0.009156 | 123.1522 | 122.8317 | 122.8638 | 122.7356 | 122.7951 | -122.9919 | -122.9645 | 123.0972 | 123.0835 | 59.4955 | 59.4864
43.9531 | 123.0927 | -59.5642 | 63.4415 | 0.083514 | -0.0072017 | 0.064717 | 0.068327 | -0.0035426 | 0.011844 | -0.00078276 | -0.1685 | 0.0045474 | 0.039088 | 0.040229 | -0.0063668 | 0.0035002 | 0.0013004 | 0.018311 | 63.2812 | -59.6375 | 63.7573 | -59.491 | -59.7198 | -59.761 | -0.064087 | 63.3499 | -59.5917 | 63.4918 | -59.6878 | -59.816 | -59.7885 | -0.073242 | -0.16022 | 0.31586 | 0.073242 | -0.19684 | -0.15564 | -0.1236 | -0.082398 | -0.027466 | -0.091552 | 0.050354 | -0.1236 | -0.2243 | -0.25177 | -0.19684 | -0.2243 | 0.14648 | 123.3948 | -0.09613 | 123.0835 | 122.9187 | 122.9416 | 122.8455 | 122.9141 | -123.0789 | -123.0331 | 123.3215 | 123.056 | 59.5825 | 59.5001
44.9531 | 123.1293 | -59.5734 | 63.4277 | 0.0072204 | -0.00079271 | 0.064717 | 0.057646 | 0.01141 | -0.020199 | 0.00028524 | -0.13799 | 0.010956 | 0.061518 | 0.076545 | 0.0021782 | -0.0050448 | -0.013653 | -0.041199 | 63.2767 | -59.642 | 63.6566 | -59.3994 | -59.7748 | -59.7702 | -0.16022 | 63.3087 | -59.5871 | 63.5376 | -59.6512 | -59.8434 | -59.7427 | -0.068665 | -0.15106 | 0.22888 | 0.17395 | -0.19684 | -0.20142 | -0.12817 | -0.13275 | -0.013733 | -0.11902 | 0.10986 | -0.07782 | -0.16937 | -0.27008 | -0.15564 | -0.25635 | 0.24262 | 123.2986 | -0.064087 | 123.1247 | 122.9187 | 122.8958 | 122.85 | 122.8821 | -123.0698 | -123.0148 | 123.23 | 123.111 | 59.5322 | 59.4131
46.0312 | 123.1384 | -59.5367 | 63.4598 | 0.098773 | 0.019501 | 0.061512 | 0.06085 | 0.0050024 | 0.020389 | -0.012532 | 0.075638 | 0.0077514 | 0.058314 | 0.058387 | 0.0043152 | 0.0045682 | -0.020062 | 0.013733 | 63.295 | -59.5688 | 63.6429 | -59.3903 | -59.7748 | -59.7336 | -0.013733 | 63.327 | -59.5551 | 63.588 | -59.5963 | -59.7427 | -59.7061 | -0.032044 | -0.16479 | 0.1831 | 0.14648 | -0.19684 | -0.23804 | -0.16479 | -0.20599 | -0.018311 | -0.13275 | 0.12817 | -0.059509 | -0.16937 | -0.20599 | -0.15106 | -0.18768 | 0.17853 | 123.2117 | -0.041198 | 123.143 | 122.8638 | 122.8821 | 122.8317 | 122.8638 | -123.0286 | -123.0148 | 123.1796 | 123.1247 | 59.5505 | 59.523
46.9531 | 123.0789 | -59.5779 | 63.4186 | 0.022479 | 0.0056153 | 0.073262 | 0.064055 | 0.00072943 | 0.0022313 | -0.012532 | -0.092209 | 0.0056154 | 0.056178 | 0.053047 | 0.012859 | 0.0045682 | -0.02113 | -0.022888 | 63.2904 | -59.6283 | 63.6795 | -59.404 | -59.729 | -59.7427 | -0.16937 | 63.3224 | -59.61 | 63.4506 | -59.7153 | -59.903 | -59.7473 | -0.050354 | -0.12817 | 0.26093 | 0.17395 | -0.16479 | -0.15106 | -0.11444 | -0.10071 | -0.032043 | -0.09613 | 0.032044 | -0.13733 | -0.16937 | -0.32501 | -0.13733 | -0.29297 | 0.2243 | 123.3078 | -0.10529 | 123.0606 | 122.9187 | 122.9324 | 122.8683 | 122.9004 | -123.0469 | -123.0286 | 123.2574 | 123.0286 | 59.5551 | 59.4086
48.0312 | 123.1338 | -59.5551 | 63.4232 | -0.0080386 | 0.010956 | 0.063649 | 0.067259 | -0.0056786 | 0.0075723 | 0.0013532 | 0.014603 | -0.0018616 | 0.068995 | 0.042366 | 0.0064512 | -0.0018398 | 0.023731 | -0.027466 | 63.2675 | -59.6146 | 63.6292 | -59.436 | -59.7977 | -59.7015 | -0.041199 | 63.3408 | -59.5917 | 63.533 | -59.6924 | -59.7885 | -59.7519 | -0.059509 | -0.15564 | 0.20599 | 0.11902 | -0.14648 | -0.24261 | -0.086975 | -0.18311 | -0.036621 | -0.082398 | 0.10986 | -0.13733 | -0.19684 | -0.23346 | -0.16022 | -0.19684 | 0.17853 | 123.2437 | -0.10071 | 123.1247 | 122.8821 | 122.9324 | 122.8226 | 122.8958 | -123.0377 | -123.0148 | 123.1842 | 123.0881 | 59.5276 | 59.5139
48.9531 | 123.1201 | -59.5688 | 63.4598 | 0.037738 | 0.0013433 | 0.055104 | 0.059782 | 0.015683 | -0.018063 | -0.016805 | 0.029861 | -0.0072016 | 0.082881 | 0.066932 | 0.0075192 | 0.0002962 | 0.0098454 | 0.041199 | 63.2858 | -59.6146 | 63.6658 | -59.4864 | -59.729 | -59.7748 | -0.073242 | 63.3362 | -59.5963 | 63.5101 | -59.6191 | -59.8068 | -59.7382 | -0.045776 | -0.17395 | 0.20599 | 0.082398 | -0.20599 | -0.16022 | -0.16022 | -0.11444 | -0.027465 | -0.1236 | 0.050354 | -0.050354 | -0.16937 | -0.23804 | -0.14191 | -0.21057 | 0.12817 | 123.2803 | -0.022889 | 123.1064 | 122.9004 | 122.9324 | 122.8546 | 122.905 | -123.0743 | -123.056 | 123.2346 | 123.0789 | 59.61 | 59.4955
50.0312 | 123.23 | -59.5367 | 63.4094 | 0.068255 | 0.00027529 | 0.059376 | 0.056578 | 0.0060704 | -0.011654 | 0.0045582 | 0.31978 | -0.0061336 | 0.0722 | 0.063728 | 0.012859 | -0.0061128 | -0.00083564 | -0.004578 | 63.2401 | -59.5505 | 63.5788 | -59.4498 | -59.8526 | -59.8297 | -0.032043 | 63.3041 | -59.5505 | 63.5971 | -59.5642 | -59.7107 | -59.6786 | -0.013733 | -0.16937 | 0.16937 | 0.086975 | -0.29297 | -0.31586 | -0.27924 | -0.30212 | -0.013733 | -0.10529 | 0.18768 | -0.027466 | -0.14191 | -0.17395 | -0.12817 | -0.16022 | 0.10071 | 123.1293 | -0.013733 | 123.1476 | 122.7905 | 122.8546 | 122.7768 | 122.8409 | -122.9599 | -122.9599 | 123.1155 | 123.1338 | 59.5322 | 59.5047
50.9531 | 123.1338 | -59.5825 | 63.3911 | 0.098773 | -0.0082697 | 0.063649 | 0.069395 | 0.0071384 | 0.0097083 | -0.0039868 | -0.092209 | -0.0018616 | 0.066859 | 0.060523 | 0.0011102 | 0.0077732 | -0.0061756 | -0.073242 | 63.2538 | -59.6466 | 63.6932 | -59.4681 | -59.7015 | -59.8206 | -0.10986 | 63.3133 | -59.5825 | 63.4872 | -59.6283 | -59.8572 | -59.761 | -0.064086 | -0.13733 | 0.30212 | 0.11444 | -0.23804 | -0.11902 | -0.17395 | -0.054932 | 0 | -0.07782 | 0.096131 | -0.045776 | -0.17853 | -0.27466 | -0.17853 | -0.27466 | 0.17853 | 123.3398 | -0.045776 | 123.0698 | 122.9004 | 122.8958 | 122.8363 | 122.8958 | -123.0377 | -122.9736 | 123.2758 | 123.0698 | 59.5093 | 59.4727
52.0312 | 123.2025 | -59.5551 | 63.3728 | 0.083514 | -0.0029297 | 0.068989 | 0.066191 | -0.0035426 | 0.015048 | 0.0034902 | 0.18245 | -0.012543 | 0.064723 | 0.06266 | -0.0020938 | -0.0050448 | 0.016254 | 0.013733 | 63.2034 | -59.5871 | 63.4918 | -59.5551 | -59.8618 | -59.9121 | -0.022888 | 63.2675 | -59.5596 | 63.5605 | -59.5322 | -59.7473 | -59.6741 | -0.032043 | -0.16937 | 0.11902 | 0 | -0.35706 | -0.3067 | -0.32501 | -0.27466 | -0.004577 | -0.10529 | 0.18768 | 0.022888 | -0.11902 | -0.19226 | -0.11444 | -0.18768 | 0.032043 | 123.0789 | 0.027465 | 123.1201 | 122.7905 | 122.8271 | 122.7585 | 122.8226 | -122.9599 | -122.9324 | 123.0469 | 123.1155 | 59.5688 | 59.5322
52.9688 | 123.1842 | -59.5505 | 63.3865 | 0.037738 | 0.0088203 | 0.066853 | 0.059782 | -0.00033857 | -0.0073817 | -0.011464 | 0.15193 | 0.0024114 | 0.080744 | 0.097908 | 0.0032462 | -0.0082488 | -0.014721 | -0.027466 | 63.2446 | -59.5825 | 63.5834 | -59.6054 | -59.7931 | -59.8846 | 0.004578 | 63.2812 | -59.5642 | 63.5559 | -59.6008 | -59.697 | -59.7107 | -0.032044 | -0.14191 | 0.19684 | -0.054932 | -0.33417 | -0.24261 | -0.30212 | -0.21057 | -0.013733 | -0.10529 | 0.16937 | -0.050354 | -0.16022 | -0.14648 | -0.14648 | -0.13275 | -0.022888 | 123.1659 | -0.036621 | 123.1201 | 122.8271 | 122.8455 | 122.7951 | 122.8317 | -122.9691 | -122.9507 | 123.1338 | 123.1064 | 59.523 | 59.5551
54.0312 | 123.1888 | -59.5551 | 63.4094 | 0.037738 | -0.0018617 | 0.065785 | 0.059782 | 0.0071384 | 0.02573 | 0.0088302 | 0.10615 | -0.0018616 | 0.080744 | 0.071205 | -0.0063668 | -0.014658 | 0.0087774 | -0.004578 | 63.2629 | -59.6008 | 63.5284 | -59.5551 | -59.8297 | -59.8755 | -0.073242 | 63.2767 | -59.5505 | 63.5284 | -59.5917 | -59.7473 | -59.7015 | -0.045776 | -0.14648 | 0.11902 | 0 | -0.32043 | -0.27466 | -0.27466 | -0.22888 | 0.004578 | -0.13275 | 0.11902 | -0.036621 | -0.14648 | -0.19226 | -0.15106 | -0.19684 | 0.045776 | 123.1293 | -0.041199 | 123.0789 | 122.8638 | 122.8271 | 122.818 | 122.8317 | -123.0103 | -122.9599 | 123.0835 | 123.0835 | 59.5505 | 59.4818
54.9531 | 123.23 | -59.5184 | 63.3728 | 0.037738 | 0.0088203 | 0.064717 | 0.068327 | -0.0099516 | -0.011654 | 0.0024222 | 0.04512 | -0.0093376 | 0.058314 | 0.059455 | -0.012775 | -0.0039768 | -0.017926 | -0.054932 | 63.2217 | -59.6008 | 63.62 | -59.5642 | -59.8663 | -59.8892 | 0.018311 | 63.295 | -59.5688 | 63.6108 | -59.5642 | -59.6649 | -59.7198 | -0.082397 | -0.15106 | 0.24719 | -0.045776 | -0.37079 | -0.3479 | -0.28839 | -0.2655 | -0.050354 | -0.07782 | 0.23804 | -0.045776 | -0.20142 | -0.14648 | -0.15106 | -0.09613 | 0.036621 | 123.2208 | 0.004578 | 123.1796 | 122.8226 | 122.8638 | 122.7402 | 122.8134 | -122.9736 | -122.9416 | 123.1384 | 123.1293 | 59.4635 | 59.5367
55.9531 | 123.1384 | -59.5276 | 63.4369 | 0.052997 | -0.011475 | 0.064717 | 0.066191 | 0.016751 | -0.013791 | 0.0056262 | -0.092209 | 0.0077514 | 0.057246 | 0.080818 | -0.0052988 | 0.0099092 | -0.013653 | 0.022888 | 63.2721 | -59.5825 | 63.6292 | -59.4223 | -59.7931 | -59.7702 | -0.059509 | 63.3087 | -59.5688 | 63.5513 | -59.6054 | -59.816 | -59.7061 | -0.054932 | -0.16479 | 0.19226 | 0.10529 | -0.24262 | -0.2655 | -0.18768 | -0.21057 | -0.041199 | -0.12817 | 0.11444 | -0.07782 | -0.17853 | -0.28839 | -0.13733 | -0.24719 | 0.16022 | 123.2117 | -0.036621 | 123.1201 | 122.8546 | 122.8775 | 122.7997 | 122.8363 | -123.0194 | -123.0057 | 123.1567 | 123.0789 | 59.5505 | 59.4681
56.9531 | 123.0972 | -59.5825 | 63.4186 | 0.098773 | -0.0093377 | 0.07433 | 0.070463 | -0.0014066 | -0.033017 | -0.0082598 | -0.1685 | -0.0018616 | 0.063655 | 0.059455 | 0.010723 | -0.0007718 | 0.0023694 | -0.07782 | 63.2629 | -59.6329 | 63.7344 | -59.3765 | -59.6924 | -59.7382 | -0.1236 | 63.3316 | -59.6054 | 63.4872 | -59.7061 | -59.7839 | -59.8251 | -0.050354 | -0.15564 | 0.31586 | 0.20599 | -0.15564 | -0.10986 | -0.10529 | -0.059509 | -0.022888 | -0.086975 | 0.068665 | -0.1236 | -0.24261 | -0.20142 | -0.21973 | -0.17853 | 0.25635 | 123.3673 | -0.10071 | 123.0927 | 122.8958 | 122.937 | 122.8455 | 122.9141 | -123.0515 | -123.024 | 123.317 | 123.0698 | 59.5047 | 59.4589
58.0312 | 123.1384 | -59.5505 | 63.4506 | 0.20559 | -0.0082697 | 0.059376 | 0.065123 | 0.01141 | -0.0095177 | 0.0045582 | 0.21297 | -0.0007936 | 0.065791 | 0.044502 | 0.010723 | 0.0035002 | -0.0051076 | 0.091553 | 63.2904 | -59.5642 | 63.6383 | -59.5047 | -59.7656 | -59.8068 | 0.027466 | 63.327 | -59.5825 | 63.5284 | -59.61 | -59.7336 | -59.7565 | -0.013733 | -0.16022 | 0.18768 | 0.045776 | -0.25635 | -0.21515 | -0.24262 | -0.20142 | -0.032044 | -0.1236 | 0.077819 | -0.059509 | -0.20599 | -0.18311 | -0.17395 | -0.15106 | 0.059509 | 123.2025 | -0.027465 | 123.111 | 122.8546 | 122.9095 | 122.8409 | 122.8775 | -123.0148 | -123.0331 | 123.1888 | 123.0789 | 59.642 | 59.5779
58.9531 | 123.1155 | -59.5413 | 63.4323 | -0.0080386 | 0.0013433 | 0.070057 | 0.068327 | 0.0092744 | -0.00097271 | -0.015736 | -0.07695 | -0.0029296 | 0.064723 | 0.066932 | -0.0010258 | 0.0035002 | 0.01305 | -0.027466 | 63.2767 | -59.6008 | 63.6612 | -59.4543 | -59.7565 | -59.7473 | -0.050354 | 63.3362 | -59.5688 | 63.5147 | -59.6878 | -59.8068 | -59.7748 | -0.059509 | -0.15564 | 0.22888 | 0.086975 | -0.20599 | -0.21515 | -0.14648 | -0.15564 | -0.027466 | -0.09613 | 0.082397 | -0.14648 | -0.23346 | -0.2655 | -0.20599 | -0.23804 | 0.14648 | 123.262 | -0.11902 | 123.0835 | 122.8775 | 122.905 | 122.818 | 122.8775 | -123.0331 | -123.0011 | 123.2025 | 123.056 | 59.5139 | 59.491
60.0312 | 123.2849 | -59.523 | 63.4232 | 0.052997 | 0.0024113 | 0.064717 | 0.052305 | 0.0060704 | -0.0052457 | -0.0082598 | 0.28926 | -0.0050656 | 0.074336 | 0.031684 | -0.0010258 | -0.0071808 | -0.0051076 | 0.064087 | 63.2629 | -59.5871 | 63.5971 | -59.6146 | -59.8434 | -59.8892 | 0.16479 | 63.327 | -59.5184 | 63.6429 | -59.5093 | -59.5779 | -59.6283 | -0.064087 | -0.16022 | 0.17395 | -0.091553 | -0.36621 | -0.32044 | -0.30212 | -0.25635 | 0.004577 | -0.096131 | 0.21973 | 0.013733 | -0.10529 | -0.054932 | -0.10986 | -0.059509 | -0.027466 | 123.1842 | 0.009156 | 123.1613 | 122.85 | 122.8455 | 122.7859 | 122.85 | -123.0103 | -122.9416 | 123.1201 | 123.1659 | 59.5871 | 59.6878
60.9531 | 123.1384 | -59.5505 | 63.4369 | 0.037738 | 0.0024113 | 0.065785 | 0.064055 | -0.00033857 | 0.019321 | -0.029622 | -0.092209 | -0.0093376 | 0.049769 | 0.043434 | -0.0074348 | -0.0007718 | 0.00023236 | 0 | 63.2675 | -59.5871 | 63.6383 | -59.4223 | -59.816 | -59.729 | -0.004578 | 63.3591 | -59.5505 | 63.6108 | -59.7061 | -59.7702 | -59.761 | -0.036621 | -0.16937 | 0.20142 | 0.12817 | -0.17853 | -0.2655 | -0.14191 | -0.22888 | 0 | -0.07782 | 0.17395 | -0.15564 | -0.21057 | -0.21973 | -0.21057 | -0.21973 | 0.16479 | 123.2254 | -0.15564 | 123.1613 | 122.8546 | 122.9095 | 122.818 | 122.9095 | -123.024 | -122.9874 | 123.1888 | 123.1613 | 59.5505 | 59.5459
62.0312 | 123.2666 | -59.5093 | 63.3636 | 0.068255 | 0.0098883 | 0.075398 | 0.054442 | -0.0078156 | 0.010776 | 0.0024222 | -0.13799 | -0.0072016 | 0.03802 | 0.082954 | 0.0021782 | 0.0045682 | -0.0029716 | -0.004578 | 63.2263 | -59.5779 | 63.5834 | -59.5825 | -59.8801 | -59.8892 | 0.068665 | 63.2721 | -59.5642 | 63.6383 | -59.5825 | -59.6649 | -59.6695 | -0.068665 | -0.13733 | 0.21973 | -0.073243 | -0.37994 | -0.37079 | -0.31128 | -0.30212 | -0.054932 | -0.091552 | 0.27466 | -0.073243 | -0.16022 | -0.15564 | -0.10529 | -0.10071 | -0.004578 | 123.1613 | -0.018311 | 123.2025 | 122.8043 | 122.8363 | 122.7356 | 122.7814 | -122.9416 | -122.9279 | 123.0927 | 123.1476 | 59.5047 | 59.5779
62.9688 | 123.2117 | -59.5413 | 63.3865 | 0.14455 | 0.0098883 | 0.058308 | 0.05551 | -0.013156 | 0.012912 | 0.015239 | 0.10615 | -0.0093376 | 0.075404 | 0.04557 | 4.2208e-05 | -0.0061128 | 0.024799 | -0.064087 | 63.2217 | -59.5642 | 63.4689 | -59.5505 | -59.9075 | -59.8114 | -0.022888 | 63.295 | -59.5779 | 63.6475 | -59.5963 | -59.7015 | -59.697 | -0.022888 | -0.16479 | 0.082397 | -0.009155 | -0.27008 | -0.36621 | -0.24719 | -0.34332 | -0.036621 | -0.091553 | 0.26093 | -0.054931 | -0.15564 | -0.16022 | -0.11902 | -0.1236 | 0.013733 | 123.0331 | -0.01831 | 123.2254 | 122.7859 | 122.8729 | 122.7631 | 122.8363 | -122.9507 | -122.9645 | 123.0103 | 123.1888 | 59.4772 | 59.5184
64.0312 | 123.1888 | -59.5276 | 63.4094 | 0.17507 | -0.0018617 | 0.066853 | 0.06085 | 0.01141 | 0.02573 | 0.0098982 | 0.274 | 0.0056154 | 0.079676 | 0.040229 | 0.0053832 | 0.0035002 | 0.011982 | -0.064087 | 63.2584 | -59.5779 | 63.6063 | -59.5047 | -59.8297 | -59.8389 | -0.027466 | 63.2812 | -59.5825 | 63.5925 | -59.6237 | -59.6924 | -59.7473 | -0.050354 | -0.15106 | 0.19684 | 0.022888 | -0.31128 | -0.30212 | -0.26093 | -0.25177 | -0.054932 | -0.12817 | 0.1831 | -0.09613 | -0.21973 | -0.16479 | -0.16479 | -0.10986 | 0.073242 | 123.1842 | -0.041198 | 123.175 | 122.8363 | 122.8638 | 122.7859 | 122.8088 | -122.9874 | -122.9919 | 123.1338 | 123.1201 | 59.4635 | 59.5001
64.9531 | 123.1934 | -59.5734 | 63.4232 | 0.11403 | -0.0029297 | 0.068989 | 0.054442 | -0.00033857 | 0.011844 | 0.0013532 | 0.10615 | 0.0098884 | 0.063655 | 0.060523 | -0.0031618 | 0.0013642 | -0.0051076 | -0.10529 | 63.2904 | -59.6375 | 63.6429 | -59.3994 | -59.7656 | -59.7748 | -0.15106 | 63.3087 | -59.6237 | 63.5239 | -59.6924 | -59.8206 | -59.8022 | -0.064087 | -0.13275 | 0.21973 | 0.17395 | -0.20142 | -0.19226 | -0.13733 | -0.12817 | -0.050354 | -0.11444 | 0.10071 | -0.11902 | -0.22888 | -0.24719 | -0.17853 | -0.19684 | 0.23804 | 123.2803 | -0.068665 | 123.1476 | 122.9279 | 122.9324 | 122.8638 | 122.8821 | -123.0606 | -123.0469 | 123.2162 | 123.0972 | 59.4681 | 59.4223
66.0312 | 123.2071 | -59.5367 | 63.4003 | -0.11485 | 0.0013433 | 0.073262 | 0.064055 | -0.013156 | 0.011844 | 0.0045582 | 0.12141 | 0.0024114 | 0.059382 | 0.035957 | -0.014912 | 0.0024322 | 0.011982 | -0.036621 | 63.2034 | -59.5871 | 63.5284 | -59.5825 | -59.9075 | -59.816 | -0.004578 | 63.2767 | -59.5734 | 63.6429 | -59.6329 | -59.6924 | -59.6924 | -0.050354 | -0.19684 | 0.12817 | -0.045777 | -0.27924 | -0.37079 | -0.22888 | -0.32044 | -0.036621 | -0.1236 | 0.24261 | -0.096131 | -0.15564 | -0.15564 | -0.11902 | -0.11902 | 0.004577 | 123.1155 | -0.05951 | 123.2162 | 122.7905 | 122.85 | 122.7402 | 122.8134 | -122.9874 | -122.9736 | 123.0652 | 123.1796 | 59.5001 | 59.5322
66.9531 | 123.1338 | -59.5642 | 63.4415 | 0.14455 | 0.0013433 | 0.071125 | 0.06085 | -0.0099516 | 0.0086403 | 0.0045582 | -0.12273 | 0.0098884 | 0.06045 | 0.042366 | -0.0042298 | 0.0056372 | 0.014118 | -0.073242 | 63.2584 | -59.6466 | 63.6566 | -59.3811 | -59.7794 | -59.761 | -0.13733 | 63.2996 | -59.6054 | 63.5193 | -59.6741 | -59.8618 | -59.7336 | -0.082397 | -0.18311 | 0.21515 | 0.1831 | -0.19684 | -0.21515 | -0.11444 | -0.13275 | -0.041199 | -0.14191 | 0.07782 | -0.10986 | -0.16937 | -0.29755 | -0.12817 | -0.25635 | 0.2655 | 123.3032 | -0.068664 | 123.1247 | 122.905 | 122.905 | 122.8226 | 122.8638 | -123.0881 | -123.0469 | 123.2208 | 123.0835 | 59.491 | 59.4269
68.0312 | 123.1247 | -59.5413 | 63.4415 | 0.068255 | 0.0024113 | 0.065785 | 0.06085 | -0.013156 | -0.0095177 | 0.0013532 | 0.060379 | 0.0034794 | 0.079676 | 0.053047 | 0.0075192 | -0.0007718 | 0.0045054 | -0.022888 | 63.3316 | -59.5642 | 63.6703 | -59.3399 | -59.7565 | -59.6786 | -0.059509 | 63.3408 | -59.5871 | 63.5559 | -59.6603 | -59.7473 | -59.7427 | -0.022888 | -0.10986 | 0.22888 | 0.20142 | -0.13733 | -0.21515 | -0.11444 | -0.19226 | -0.045776 | -0.10071 | 0.11444 | -0.11902 | -0.20142 | -0.20599 | -0.15564 | -0.16022 | 0.2243 | 123.2346 | -0.073242 | 123.143 | 122.8958 | 122.9279 | 122.8729 | 122.8821 | -123.0057 | -123.0286 | 123.2117 | 123.0972 | 59.5184 | 59.4818
68.9531 | 123.0927 | -59.5642 | 63.4415 | -0.069074 | -0.0029297 | 0.058308 | 0.058714 | 0.0060704 | -0.012723 | -0.0061228 | -0.10747 | 0.013092 | 0.059382 | 0.077613 | 0.0053832 | 0.012045 | -0.011517 | -0.041199 | 63.2767 | -59.6191 | 63.6932 | -59.3811 | -59.7382 | -59.7519 | -0.16479 | 63.327 | -59.5917 | 63.446 | -59.7153 | -59.903 | -59.7336 | -0.054932 | -0.1648 | 0.25177 | 0.1831 | -0.18768 | -0.17395 | -0.13275 | -0.11902 | -0.027466 | -0.11444 | 0.004578 | -0.15106 | -0.16937 | -0.33875 | -0.14191 | -0.31128 | 0.23804 | 123.3124 | -0.1236 | 123.0377 | 122.8958 | 122.9187 | 122.8409 | 122.8912 | -123.0606 | -123.0331 | 123.2574 | 123.0103 | 59.523 | 59.3994
69.9531 | 123.1201 | -59.5825 | 63.4232 | 0.0072204 | -0.0029297 | 0.062581 | 0.065123 | 0.01141 | -0.021267 | 0.0013532 | 0.029861 | 0.0002754 | 0.057246 | 0.054115 | -0.0020938 | -0.0039768 | 0.0087774 | -0.09613 | 63.2675 | -59.6329 | 63.6978 | -59.3994 | -59.7427 | -59.7473 | -0.11902 | 63.3087 | -59.6146 | 63.5284 | -59.7061 | -59.8206 | -59.816 | -0.050354 | -0.15564 | 0.27466 | 0.18311 | -0.16479 | -0.16022 | -0.11444 | -0.10986 | -0.032043 | -0.11444 | 0.10528 | -0.1236 | -0.23346 | -0.23804 | -0.20142 | -0.20599 | 0.23346 | 123.3307 | -0.091553 | 123.143 | 122.9004 | 122.9233 | 122.85 | 122.8912 | -123.056 | -123.0377 | 123.2803 | 123.111 | 59.4864 | 59.4635
71.0312 | 123.1659 | -59.5322 | 63.3774 | 0.0072204 | 0.0034793 | 0.061512 | 0.050169 | 0.012479 | -0.0031087 | 0.0056262 | 0.274 | 0.0077514 | 0.052973 | 0.054115 | 0.012859 | -0.0029078 | 0.01305 | -0.041199 | 63.2126 | -59.5871 | 63.6337 | -59.5825 | -59.8022 | -59.8618 | 0.032043 | 63.295 | -59.5825 | 63.5651 | -59.6191 | -59.7015 | -59.7107 | -0.054931 | -0.1648 | 0.25635 | -0.050354 | -0.32959 | -0.27008 | -0.27466 | -0.21515 | -0.050354 | -0.082397 | 0.18768 | -0.086975 | -0.17853 | -0.16937 | -0.12817 | -0.11902 | 0.004577 | 123.2208 | -0.036621 | 123.1476 | 122.7997 | 122.8775 | 122.7448 | 122.8271 | -122.9645 | -122.9599 | 123.1659 | 123.0972 | 59.491 | 59.5642
71.9531 | 123.1155 | -59.5917 | 63.414 | 0.0072204 | 0.0066833 | 0.059376 | 0.062986 | 0.0017974 | 0.0075723 | 0.0024222 | -0.092209 | 0.0045474 | 0.061518 | 0.068 | 0.0011102 | 0.0013642 | -0.0040396 | -0.10071 | 63.2721 | -59.6283 | 63.7115 | -59.3719 | -59.7656 | -59.7336 | -0.11444 | 63.3224 | -59.6008 | 63.5513 | -59.7519 | -59.8206 | -59.7931 | -0.036621 | -0.14191 | 0.29755 | 0.21973 | -0.14191 | -0.17395 | -0.10529 | -0.13733 | -0.009155 | -0.091552 | 0.13733 | -0.16022 | -0.20142 | -0.22888 | -0.19226 | -0.21973 | 0.25635 | 123.3398 | -0.15106 | 123.1522 | 122.9004 | 122.9233 | 122.8638 | 122.9141 | -123.0423 | -123.0148 | 123.3032 | 123.143 | 59.491 | 59.4772
73.0312 | 123.1338 | -59.5413 | 63.4415 | 0.14455 | -0.0039977 | 0.05724 | 0.064055 | 0.0050024 | 0.015048 | -0.00078276 | 0.18245 | -0.0007936 | 0.066859 | 0.094703 | 0.0096552 | 0.0013642 | -0.0072446 | 0.009155 | 63.327 | -59.5871 | 63.7573 | -59.3857 | -59.7198 | -59.7015 | -0.004578 | 63.382 | -59.5596 | 63.5239 | -59.61 | -59.729 | -59.7153 | -0.045776 | -0.11444 | 0.31586 | 0.15564 | -0.16022 | -0.17853 | -0.11444 | -0.13275 | -0.01831 | -0.059509 | 0.082398 | -0.068664 | -0.17395 | -0.18768 | -0.15564 | -0.16937 | 0.20142 | 123.3444 | -0.050354 | 123.0835 | 122.9141 | 122.9416 | 122.8683 | 122.9233 | -123.0286 | -123.0011 | 123.2986 | 123.0652 | 59.5505 | 59.5367
73.9531 | 123.1293 | -59.5688 | 63.4186 | 0.12929 | -0.00079271 | 0.070057 | 0.053373 | 0.0082064 | -0.0031087 | -0.015736 | 0.12141 | 0.0045474 | 0.075404 | 0.10645 | 0.0053832 | 0.0035002 | 0.022663 | -0.073242 | 63.2538 | -59.642 | 63.6932 | -59.404 | -59.7702 | -59.697 | -0.13275 | 63.3041 | -59.61 | 63.533 | -59.7061 | -59.8068 | -59.7839 | -0.073242 | -0.16479 | 0.27466 | 0.16479 | -0.12817 | -0.20142 | -0.054931 | -0.12817 | -0.041198 | -0.11444 | 0.11444 | -0.13733 | -0.21515 | -0.23804 | -0.17395 | -0.19684 | 0.23804 | 123.3353 | -0.096131 | 123.143 | 122.8958 | 122.9141 | 122.8226 | 122.8729 | -123.0606 | -123.0286 | 123.262 | 123.1018 | 59.4955 | 59.436
75.0312 | 123.2071 | -59.523 | 63.3774 | -0.069074 | 0.0013433 | 0.067921 | 0.065123 | -0.019565 | 0.0011633 | 0.0066942 | 0.12141 | -0.0050656 | 0.064723 | 0.058387 | 4.2208e-05 | 0.0035002 | -0.0072446 | -0.004578 | 63.2309 | -59.5917 | 63.5422 | -59.6054 | -59.8938 | -59.8389 | 0.041199 | 63.2812 | -59.5871 | 63.6337 | -59.6191 | -59.6786 | -59.6786 | -0.068665 | -0.14648 | 0.16479 | -0.082398 | -0.31586 | -0.37079 | -0.24719 | -0.30212 | -0.064087 | -0.09613 | 0.25635 | -0.096131 | -0.15564 | -0.15564 | -0.091553 | -0.091553 | -0.013733 | 123.1338 | -0.032044 | 123.2208 | 122.8226 | 122.8683 | 122.7539 | 122.8043 | -122.9691 | -122.9645 | 123.0652 | 123.1567 | 59.5184 | 59.5642
75.9531 | 123.0606 | -59.5688 | 63.4415 | 0.14455 | 0.0056153 | 0.071125 | 0.058714 | 0.0082064 | -0.010586 | -0.0018508 | -0.10747 | 0.0045474 | 0.082881 | 0.080818 | -0.0042298 | 0.0099092 | 0.011982 | -0.045776 | 63.2904 | -59.6054 | 63.6154 | -59.4131 | -59.761 | -59.7107 | -0.11444 | 63.3408 | -59.5825 | 63.501 | -59.697 | -59.8434 | -59.8022 | -0.036621 | -0.15106 | 0.17395 | 0.15564 | -0.14191 | -0.19226 | -0.10529 | -0.15564 | -0.013733 | -0.10071 | 0.05951 | -0.12817 | -0.23346 | -0.27466 | -0.21973 | -0.26093 | 0.19226 | 123.2208 | -0.11444 | 123.0835 | 122.8958 | 122.9233 | 122.8592 | 122.9095 | -123.0469 | -123.024 | 123.1842 | 123.0698 | 59.523 | 59.4543
77.0312 | 123.1842 | -59.5596 | 63.3865 | -0.0080386 | -0.0072017 | 0.063649 | 0.06085 | 0.0092744 | -0.0063137 | -0.0082598 | 0.21297 | 0.0024114 | 0.074336 | 0.064796 | 0.0085872 | -0.0018398 | -0.0083126 | -0.068665 | 63.2584 | -59.5871 | 63.5925 | -59.4864 | -59.8434 | -59.8114 | 0 | 63.3041 | -59.5551 | 63.6246 | -59.6558 | -59.697 | -59.7153 | -0.027466 | -0.12817 | 0.20599 | 0.073242 | -0.25177 | -0.28381 | -0.2243 | -0.25635 | 0.004577 | -0.082398 | 0.23804 | -0.096131 | -0.15564 | -0.13733 | -0.16022 | -0.14191 | 0.10071 | 123.1796 | -0.10071 | 123.1796 | 122.8455 | 122.8592 | 122.818 | 122.8638 | -122.9736 | -122.9416 | 123.1522 | 123.1842 | 59.491 | 59.5596
77.9531 | 123.0652 | -59.5871 | 63.4552 | 0.052997 | -0.0072017 | 0.060444 | 0.068327 | -0.0088836 | -0.0031087 | -0.0050548 | -0.092209 | 0.0013434 | 0.051905 | 0.073341 | -0.0010258 | 0.0067052 | 0.0055734 | -0.041199 | 63.2675 | -59.6283 | 63.6749 | -59.3765 | -59.7519 | -59.7382 | -0.17853 | 63.3591 | -59.5963 | 63.4735 | -59.7107 | -59.8938 | -59.7839 | -0.041199 | -0.18768 | 0.21973 | 0.21057 | -0.15106 | -0.16479 | -0.10986 | -0.1236 | -0.009155 | -0.09613 | 0.018311 | -0.1236 | -0.19684 | -0.3067 | -0.18768 | -0.29755 | 0.25177 | 123.3032 | -0.11444 | 123.0698 | 122.8958 | 122.9553 | 122.8546 | 122.9462 | -123.0835 | -123.0515 | 123.262 | 123.0606 | 59.5459 | 59.4086
79.0312 | 123.1796 | -59.5505 | 63.4003 | 0.022479 | 0.0098883 | 0.062581 | 0.057646 | -0.013156 | 0.0086403 | -0.0061228 | 0.21297 | 0.0066834 | 0.074336 | 0.029548 | 0.0085872 | -0.010385 | 0.00023236 | -0.045776 | 63.2492 | -59.5917 | 63.5422 | -59.5551 | -59.8801 | -59.8022 | -0.009155 | 63.2675 | -59.5551 | 63.5605 | -59.61 | -59.6695 | -59.7244 | -0.041199 | -0.15106 | 0.14191 | -0.004578 | -0.25177 | -0.32959 | -0.21057 | -0.28839 | -0.004578 | -0.13275 | 0.16022 | -0.059509 | -0.17395 | -0.11902 | -0.16937 | -0.11444 | 0.036621 | 123.1338 | -0.054931 | 123.1155 | 122.8409 | 122.8226 | 122.7997 | 122.818 | -122.9919 | -122.9553 | 123.0927 | 123.111 | 59.5047 | 59.5413
79.9531 | 123.1064 | -59.5779 | 63.446 | 0.098773 | 0.0066833 | 0.071125 | 0.069395 | 0.0017974 | 0.01398 | -0.0018508 | 0.014603 | -0.0082696 | 0.058314 | 0.086158 | -0.0020938 | -0.0007718 | 0.0034374 | -0.004578 | 63.2812 | -59.6283 | 63.6566 | -59.4315 | -59.761 | -59.7794 | -0.086975 | 63.3453 | -59.6008 | 63.5101 | -59.6695 | -59.8434 | -59.7382 | -0.050354 | -0.16479 | 0.21057 | 0.14648 | -0.20142 | -0.1831 | -0.15106 | -0.13275 | -0.022888 | -0.10071 | 0.064087 | -0.091553 | -0.16022 | -0.2655 | -0.13733 | -0.24262 | 0.19684 | 123.2849 | -0.068665 | 123.111 | 122.9095 | 122.9462 | 122.8592 | 122.9233 | -123.0743 | -123.0469 | 123.2346 | 123.0881 | 59.5734 | 59.491
81.0312 | 123.1842 | -59.5367 | 63.414 | 0.068255 | 0.0077523 | 0.056172 | 0.070463 | 0.0028664 | 0.017185 | 0.0013532 | 0.36555 | 0.0066834 | 0.059382 | 0.10004 | 0.0011102 | -0.0039768 | -0.011517 | -0.07782 | 63.2446 | -59.5963 | 63.5742 | -59.5001 | -59.816 | -59.8343 | -0.059509 | 63.2996 | -59.5688 | 63.5925 | -59.5963 | -59.7244 | -59.6786 | -0.059509 | -0.16937 | 0.16022 | 0.036621 | -0.29755 | -0.27924 | -0.23804 | -0.21973 | -0.032044 | -0.11444 | 0.17853 | -0.059509 | -0.14191 | -0.18768 | -0.10986 | -0.15564 | 0.09613 | 123.1705 | -0.027465 | 123.1613 | 122.8409 | 122.8683 | 122.7814 | 122.8363 | -123.0103 | -122.9828 | 123.111 | 123.1293 | 59.4589 | 59.4772
81.9531 | 123.175 | -59.5551 | 63.4506 | 0.14455 | -0.0018617 | 0.05724 | 0.066191 | 0.0050024 | -0.0031087 | 0.00028524 | -0.031174 | -0.0039976 | 0.064723 | 0.06266 | -0.0031618 | 0.0067052 | -0.0061756 | 0.054932 | 63.2904 | -59.6146 | 63.6429 | -59.5001 | -59.7336 | -59.7794 | -0.018311 | 63.3133 | -59.5642 | 63.533 | -59.5688 | -59.7656 | -59.7107 | -0.059509 | -0.16022 | 0.19226 | 0.054932 | -0.2243 | -0.17853 | -0.1648 | -0.11902 | -0.009155 | -0.13733 | 0.082397 | -0.013733 | -0.15564 | -0.21057 | -0.14648 | -0.20142 | 0.11444 | 123.2574 | -0.004578 | 123.0972 | 122.905 | 122.8775 | 122.8455 | 122.8683 | -123.0652 | -123.0148 | 123.1979 | 123.0881 | 59.61 | 59.5367
82.9531 | 123.143 | -59.5413 | 63.4232 | 0.15981 | -0.0039977 | 0.059376 | 0.067259 | 0.022092 | -0.0020407 | -0.0050548 | -0.00065608 | 0.013092 | 0.067927 | 0.044502 | 0.0011102 | 0.0077732 | -0.0029716 | -0.013733 | 63.2721 | -59.5871 | 63.6383 | -59.4315 | -59.816 | -59.7519 | 0.009155 | 63.3316 | -59.5734 | 63.6063 | -59.6786 | -59.7519 | -59.7473 | -0.045776 | -0.15106 | 0.21515 | 0.10986 | -0.21057 | -0.27466 | -0.16479 | -0.22888 | -0.032043 | -0.091553 | 0.1831 | -0.13733 | -0.20599 | -0.21057 | -0.17395 | -0.17853 | 0.15564 | 123.2254 | -0.10529 | 123.1796 | 122.8592 | 122.905 | 122.8134 | 122.8729 | -123.0103 | -122.9965 | 123.1796 | 123.1476 | 59.5276 | 59.5505
84.0312 | 123.175 | -59.5367 | 63.4094 | 0.037738 | -0.0061337 | 0.058308 | 0.057646 | -0.01102 | 0.016117 | -0.0082598 | 0.13667 | -0.010407 | 0.078608 | 0.065864 | 0.0011102 | 0.0013642 | -0.012585 | -0.045776 | 63.2309 | -59.5917 | 63.6063 | -59.5322 | -59.8068 | -59.8526 | -0.013733 | 63.2904 | -59.5779 | 63.5742 | -59.6283 | -59.6512 | -59.7473 | -0.054932 | -0.17853 | 0.19684 | 0.004577 | -0.31586 | -0.27008 | -0.26093 | -0.21515 | -0.041199 | -0.11902 | 0.16479 | -0.091553 | -0.21057 | -0.11444 | -0.16937 | -0.073242 | 0.059509 | 123.1979 | -0.050354 | 123.1522 | 122.8226 | 122.8683 | 122.7676 | 122.8271 | -123.0011 | -122.9874 | 123.143 | 123.111 | 59.491 | 59.523
84.9531 | 123.0927 | -59.5367 | 63.4277 | -0.099591 | -0.015747 | 0.063649 | 0.067259 | 0.0028664 | -0.015927 | -0.0018508 | 0.014603 | -0.0029296 | 0.071131 | 0.051979 | -0.011707 | 0.0099092 | 0.0013004 | -0.10986 | 63.2721 | -59.642 | 63.6429 | -59.3719 | -59.7794 | -59.7382 | -0.11444 | 63.3362 | -59.5917 | 63.5422 | -59.697 | -59.8206 | -59.7702 | -0.10529 | -0.15564 | 0.21515 | 0.16479 | -0.20142 | -0.24262 | -0.09613 | -0.13733 | -0.054932 | -0.091552 | 0.11444 | -0.16022 | -0.23346 | -0.28381 | -0.17853 | -0.22888 | 0.27008 | 123.2849 | -0.10528 | 123.1338 | 122.9141 | 122.9279 | 122.8088 | 122.8729 | -123.0698 | -123.0194 | 123.1796 | 123.0789 | 59.4269 | 59.4223
86.0312 | 123.1659 | -59.523 | 63.382 | -0.2827 | 0.0024113 | 0.062581 | 0.057646 | -0.00033857 | -0.018063 | -0.00078276 | 0.19771 | 0.0034794 | 0.062587 | 0.035957 | -0.013843 | 0.0067052 | -0.0019036 | -0.027466 | 63.2217 | -59.61 | 63.5376 | -59.5963 | -59.8663 | -59.8892 | 0.050354 | 63.2812 | -59.5642 | 63.6154 | -59.5963 | -59.6603 | -59.7061 | -0.086975 | -0.16022 | 0.15564 | -0.073242 | -0.36621 | -0.34332 | -0.27924 | -0.25635 | -0.041199 | -0.10071 | 0.23346 | -0.073242 | -0.18311 | -0.13733 | -0.14191 | -0.09613 | 0.013733 | 123.1476 | -0.032043 | 123.1796 | 122.8317 | 122.8455 | 122.7448 | 122.8043 | -122.9919 | -122.9462 | 123.0606 | 123.1384 | 59.4955 | 59.5734
86.9531 | 123.175 | -59.5367 | 63.4232 | 0.022479 | -0.00079271 | 0.070057 | 0.070463 | -0.0046106 | 0.0097083 | 0.0045582 | 0.060379 | 0.0034794 | 0.068995 | 0.087226 | -0.0042298 | 0.0099092 | -0.011517 | -0.009155 | 63.2721 | -59.5963 | 63.6017 | -59.4589 | -59.7977 | -59.7565 | -0.054932 | 63.3362 | -59.5551 | 63.5376 | -59.642 | -59.7839 | -59.7427 | -0.059509 | -0.15106 | 0.17853 | 0.07782 | -0.21973 | -0.26093 | -0.16022 | -0.20142 | -0.018311 | -0.086975 | 0.11444 | -0.10529 | -0.20599 | -0.24719 | -0.18768 | -0.22888 | 0.13733 | 123.1979 | -0.086975 | 123.0927 | 122.8683 | 122.8912 | 122.8088 | 122.8729 | -123.0194 | -122.9782 | 123.1384 | 123.0743 | 59.5276 | 59.4818
88.0312 | 123.1705 | -59.5596 | 63.382 | 0.11403 | 0.0045473 | 0.061512 | 0.066191 | 0.00072943 | -0.010586 | 0.0066942 | 0.12141 | -0.011475 | 0.066859 | 0.049842 | -0.0031618 | -0.0007718 | -0.0072446 | -0.036621 | 63.2492 | -59.5596 | 63.5193 | -59.5322 | -59.8389 | -59.8755 | 0.064087 | 63.2767 | -59.5642 | 63.6429 | -59.6603 | -59.6786 | -59.6832 | 0 | -0.13275 | 0.13733 | 0.027465 | -0.31586 | -0.27924 | -0.31586 | -0.27924 | -0.004578 | -0.10529 | 0.26093 | -0.10071 | -0.1236 | -0.11902 | -0.11902 | -0.11444 | 0.027465 | 123.0789 | -0.09613 | 123.2071 | 122.8088 | 122.8409 | 122.8088 | 122.8363 | -122.9416 | -122.9462 | 123.0789 | 123.2025 | 59.523 | 59.6237
88.9531 | 123.1201 | -59.5734 | 63.4552 | 0.068255 | -0.0050657 | 0.054036 | 0.057646 | -0.0078156 | 0.0054353 | 0.015239 | -0.07695 | 0.0066834 | 0.093562 | 0.084022 | -0.0042298 | 0.010977 | -0.025402 | -0.022888 | 63.2904 | -59.6054 | 63.6383 | -59.4177 | -59.7885 | -59.729 | -0.091553 | 63.3408 | -59.5505 | 63.5284 | -59.6832 | -59.8434 | -59.7427 | -0.032044 | -0.16479 | 0.18311 | 0.15564 | -0.15564 | -0.21515 | -0.1236 | -0.18311 | 0.022888 | -0.11444 | 0.073242 | -0.10986 | -0.16937 | -0.27008 | -0.19226 | -0.29297 | 0.18768 | 123.2437 | -0.13275 | 123.0789 | 122.8958 | 122.8912 | 122.8638 | 122.9141 | -123.0606 | -123.0057 | 123.2117 | 123.1018 | 59.5505 | 59.4818
90.0312 | 123.2346 | -59.5367 | 63.3911 | 0.037738 | -0.0082697 | 0.061512 | 0.062986 | -0.0035426 | -0.013791 | -0.0050548 | 0.12141 | 0.0088204 | 0.073268 | 0.054115 | 4.2208e-05 | 0.0077732 | -0.010449 | -0.10986 | 63.2263 | -59.6283 | 63.5742 | -59.4818 | -59.8343 | -59.8206 | -0.041199 | 63.2812 | -59.5871 | 63.6063 | -59.6054 | -59.6924 | -59.7015 | -0.091553 | -0.16479 | 0.18311 | 0.054931 | -0.28381 | -0.29755 | -0.19226 | -0.20599 | -0.050354 | -0.10986 | 0.21515 | -0.068665 | -0.16479 | -0.15564 | -0.11444 | -0.10529 | 0.14648 | 123.2025 | -0.018311 | 123.1934 | 122.8546 | 122.8683 | 122.7631 | 122.818 | -123.0194 | -122.9782 | 123.111 | 123.143 | 59.4269 | 59.4955
90.9531 | 123.1567 | -59.5322 | 63.4323 | 0.22084 | -0.0050657 | 0.058308 | 0.064055 | -0.0099516 | -0.0031087 | 0.0045582 | -0.00065608 | 0.0045474 | 0.075404 | 0.054115 | -0.012775 | -0.0018398 | -0.0029716 | 0.045776 | 63.2996 | -59.5734 | 63.6566 | -59.4406 | -59.7473 | -59.761 | -0.004578 | 63.3408 | -59.5551 | 63.5559 | -59.5917 | -59.7794 | -59.6512 | -0.041198 | -0.13275 | 0.2243 | 0.091553 | -0.22888 | -0.21515 | -0.18768 | -0.17395 | -0.022888 | -0.091553 | 0.1236 | -0.059509 | -0.11902 | -0.24719 | -0.09613 | -0.2243 | 0.13275 | 123.23 | -0.036621 | 123.111 | 122.8729 | 122.8958 | 122.8317 | 122.8729 | -123.0057 | -122.9874 | 123.1888 | 123.0881 | 59.5779 | 59.5276
92.0312 | 123.2208 | -59.5139 | 63.4003 | 0.022479 | 0.0013433 | 0.064717 | 0.057646 | -0.0078156 | 0.0022313 | 0.0066942 | 0.24348 | -0.0082696 | 0.074336 | 0.055183 | 0.0085872 | -0.0050448 | 0.017322 | -0.059509 | 63.1851 | -59.61 | 63.5284 | -59.5367 | -59.8618 | -59.8663 | -0.045776 | 63.2721 | -59.5551 | 63.5742 | -59.6054 | -59.7198 | -59.6786 | -0.09613 | -0.21515 | 0.12817 | -0.022888 | -0.35248 | -0.3479 | -0.25635 | -0.25177 | -0.041199 | -0.12817 | 0.17395 | -0.091553 | -0.16479 | -0.20599 | -0.1236 | -0.1648 | 0.073242 | 123.1384 | -0.050354 | 123.1293 | 122.7951 | 122.8271 | 122.699 | 122.7859 | -123.0103 | -122.9553 | 123.0423 | 123.0881 | 59.4543 | 59.4681
92.9531 | 123.1979 | -59.5871 | 63.4506 | 0.083514 | 0.0013433 | 0.056172 | 0.064055 | 0.010342 | -0.011654 | 0.0098982 | -0.00065608 | 0.0066834 | 0.078608 | 0.057319 | 0.0043152 | 0.0056372 | 0.020526 | 0.041199 | 63.2996 | -59.5917 | 63.6475 | -59.4772 | -59.7565 | -59.7794 | -0.059509 | 63.3499 | -59.5688 | 63.5056 | -59.6191 | -60.1318 | -60.0082 | -0.004578 | -0.15106 | 0.19684 | 0.10986 | -0.19226 | -0.16937 | -0.18768 | -0.16479 | 0.01831 | -0.10071 | 0.054931 | -0.032044 | -0.42114 | -0.54474 | -0.43945 | -0.56305 | 0.11444 | 123.2391 | -0.050354 | 123.0743 | 122.8912 | 122.9187 | 122.8867 | 122.937 | -123.0423 | -123.0194 | 123.2346 | 123.0927 | 59.6283 | 59.5276
93.9531 | 123.1522 | -59.5413 | 63.446 | 0.19033 | -0.0029297 | 0.056172 | 0.069395 | 0.0017974 | 0.011844 | -0.0039868 | -0.061691 | 0.0056154 | 0.076472 | 0.066932 | -0.0031618 | 0.0013642 | 0.0045054 | 0.004578 | 63.3087 | -59.6054 | 63.652 | -59.436 | -59.8068 | -59.7336 | 0.041199 | 63.3545 | -59.5688 | 63.6246 | -59.6466 | -59.7153 | -59.7153 | -0.064087 | -0.13733 | 0.20599 | 0.10529 | -0.19226 | -0.2655 | -0.12817 | -0.20142 | -0.027466 | -0.091553 | 0.17853 | -0.10528 | -0.17395 | -0.17395 | -0.14648 | -0.14648 | 0.16937 | 123.2574 | -0.077819 | 123.1934 | 122.9141 | 122.9233 | 122.85 | 122.8958 | -123.0515 | -123.0148 | 123.1934 | 123.1659 | 59.5459 | 59.5825
94.9531 | 123.2529 | -59.5596 | 63.382 | 0.15981 | -0.0029297 | 0.070057 | 0.066191 | 0.0050024 | 0.0022313 | 0.0013532 | 0.075638 | -0.0029296 | 0.073268 | 0.084022 | -0.011707 | -0.0018398 | -0.0061756 | -0.009155 | 63.1989 | -59.5917 | 63.5513 | -59.5734 | -59.8389 | -59.9625 | -0.004578 | 63.2858 | -59.5642 | 63.5971 | -59.5047 | -59.7427 | -59.6375 | -0.032044 | -0.1831 | 0.16937 | -0.013733 | -0.40283 | -0.27924 | -0.37079 | -0.24719 | -0.004578 | -0.09613 | 0.21515 | 0.054931 | -0.07782 | -0.18311 | -0.073242 | -0.17853 | 0.018311 | 123.143 | 0.059509 | 123.1613 | 122.7905 | 122.85 | 122.7585 | 122.8455 | -122.9736 | -122.9462 | 123.111 | 123.1567 | 59.5505 | 59.5551
96.0312 | 123.2437 | -59.5505 | 63.382 | 0.037738 | -0.010406 | 0.059376 | 0.068327 | -0.0078156 | -0.011654 | -0.0018508 | -0.061691 | 0.0045474 | 0.06045 | 0.059455 | -0.0020938 | 0.017386 | 0.00023236 | -0.036621 | 63.2629 | -59.61 | 63.5284 | -59.5276 | -59.848 | -59.8526 | -0.041199 | 63.2721 | -59.5688 | 63.62 | -59.5779 | -59.7382 | -59.6191 | -0.059509 | -0.11902 | 0.14648 | 0.022888 | -0.30212 | -0.29755 | -0.24262 | -0.23804 | -0.018311 | -0.10986 | 0.23804 | -0.027466 | -0.068665 | -0.18768 | -0.050354 | -0.16937 | 0.082397 | 123.1384 | -0.009155 | 123.1888 | 122.8729 | 122.8409 | 122.8134 | 122.8226 | -122.9919 | -122.9507 | 123.0789 | 123.1705 | 59.5139 | 59.5093
96.9531 | 123.1384 | -59.5413 | 63.4506 | 0.22084 | -0.0061337 | 0.064717 | 0.075804 | -0.0035426 | -0.010586 | 0.0045582 | 0.014603 | 0.0098884 | 0.068995 | 0.073341 | -0.0095708 | -0.0018398 | 0.016254 | 0.041199 | 63.2812 | -59.5871 | 63.6841 | -59.491 | -59.7519 | -59.8114 | 0.013733 | 63.327 | -59.5779 | 63.533 | -59.6237 | -59.761 | -59.7153 | -0.045776 | -0.16937 | 0.23346 | 0.050354 | -0.27008 | -0.21057 | -0.2243 | -0.16479 | -0.036621 | -0.1236 | 0.082397 | -0.082397 | -0.17395 | -0.21973 | -0.13733 | -0.1831 | 0.09613 | 123.2712 | -0.045776 | 123.111 | 122.8683 | 122.905 | 122.8226 | 122.8683 | -123.0377 | -123.0286 | 123.2254 | 123.0743 | 59.5825 | 59.5551
98.0312 | 123.2437 | -59.5367 | 63.3865 | 0.12929 | 0.0098883 | 0.070057 | 0.066191 | 0.013547 | -0.0031087 | -0.0071918 | 0.029861 | 0.013092 | 0.064723 | 0.066932 | -0.010639 | 0.0045682 | 0.0034374 | -0.045776 | 63.2584 | -59.6008 | 63.5971 | -59.5139 | -59.816 | -59.8801 | -0.054932 | 63.295 | -59.5963 | 63.5468 | -59.5642 | -59.7382 | -59.6603 | -0.064087 | -0.12817 | 0.21057 | 0.022888 | -0.34332 | -0.27924 | -0.27924 | -0.21515 | -0.059509 | -0.091553 | 0.16022 | -0.027466 | -0.1236 | -0.20142 | -0.064087 | -0.14191 | 0.086975 | 123.1979 | 0.032043 | 123.143 | 122.8592 | 122.8912 | 122.7951 | 122.8317 | -122.9874 | -122.9828 | 123.1338 | 123.0835 | 59.491 | 59.4818
98.9531 | 123.111 | -59.5596 | 63.4323 | 0.15981 | -0.00079271 | 0.065785 | 0.067259 | 0.0039344 | -0.0052457 | 0.00028524 | -0.046432 | 0.01416 | 0.064723 | 0.071205 | 0.010723 | 0.012045 | 0.0098454 | 0.027466 | 63.2904 | -59.6008 | 63.7161 | -59.5001 | -59.7382 | -59.7565 | -0.032043 | 63.327 | -59.5779 | 63.5513 | -59.5734 | -59.697 | -59.7427 | -0.041199 | -0.14191 | 0.28381 | 0.059509 | -0.19684 | -0.17853 | -0.15564 | -0.13733 | -0.018311 | -0.10529 | 0.11902 | -0.013733 | -0.18311 | -0.13733 | -0.16479 | -0.11902 | 0.10071 | 123.317 | 0.004578 | 123.1293 | 122.8912 | 122.905 | 122.85 | 122.8867 | -123.0331 | -123.0103 | 123.2758 | 123.111 | 59.5871 | 59.5276
100.0312 | 123.2483 | -59.5322 | 63.3865 | 0.0072204 | 0.0066833 | 0.073262 | 0.059782 | 0.0050024 | -0.0041777 | -0.0093278 | 0.029861 | -0.010407 | 0.074336 | 0.046638 | -0.0010258 | 0.0077732 | -0.0083126 | 0.027466 | 63.2309 | -59.5734 | 63.5284 | -59.6054 | -59.8343 | -59.9625 | 0.004578 | 63.2675 | -59.5688 | 63.5696 | -59.5047 | -59.729 | -59.6512 | -0.041198 | -0.15564 | 0.14191 | -0.073242 | -0.4303 | -0.30212 | -0.3891 | -0.26093 | -0.036621 | -0.11902 | 0.1831 | 0.027466 | -0.11902 | -0.19684 | -0.082397 | -0.16022 | -0.032044 | 123.1018 | 0.064087 | 123.1384 | 122.8043 | 122.8363 | 122.7631 | 122.7997 | -122.9599 | -122.9553 | 123.0606 | 123.1018 | 59.5596 | 59.5367
100.9531 | 123.0789 | -59.5734 | 63.4048 | 0.068255 | 0.0024113 | 0.062581 | 0.064055 | 0.0071384 | -0.0084497 | 0.010966 | -0.061691 | 0.0066834 | 0.057246 | 0.072273 | 0.017132 | 0.0045682 | 0.0023694 | -0.054932 | 63.2904 | -59.6191 | 63.5284 | -59.4131 | -59.4818 | -59.6649 | -0.050354 | 63.3545 | -59.5963 | 63.5056 | -59.729 | -59.848 | -59.8206 | -0.045777 | -0.11444 | 0.1236 | 0.16022 | -0.091553 | 0.091552 | -0.045776 | 0.13733 | -0.022888 | -0.050354 | 0.10071 | -0.15564 | -0.24719 | -0.27466 | -0.22431 | -0.25177 | 0.20599 | 123.1476 | -0.13275 | 123.1018 | 122.9095 | 122.9507 | 122.8638 | 122.9279 | -123.024 | -123.0011 | 123.1018 | 123.0789 | 59.5184 | 59.523
102.0312 | 123.1476 | -59.5734 | 63.414 | 0.0072204 | -0.00079271 | 0.049763 | 0.068327 | 0.0017974 | -0.0020407 | -0.0039868 | -0.046432 | -0.010407 | 0.065791 | 0.043434 | -0.0020938 | 0.0024322 | -0.0051076 | -0.054932 | 63.3041 | -59.61 | 63.7115 | -59.4772 | -59.6786 | -59.7748 | -0.12817 | 63.3224 | -59.5871 | 63.4552 | -59.6512 | -59.8068 | -59.7702 | -0.036621 | -0.10986 | 0.29755 | 0.09613 | -0.20142 | -0.10529 | -0.16479 | -0.068665 | -0.013733 | -0.091552 | 0.041199 | -0.07782 | -0.19684 | -0.23346 | -0.18311 | -0.21973 | 0.13275 | 123.3215 | -0.064087 | 123.0423 | 122.9141 | 122.9095 | 122.8775 | 122.8958 | -123.024 | -123.0011 | 123.2849 | 123.0286 | 59.5184 | 59.4452
102.9531 | 123.1705 | -59.5413 | 63.4232 | 0.022479 | -0.0072017 | 0.070057 | 0.074736 | 0.0060704 | -0.024472 | -0.0039868 | 0.10615 | 0.0045474 | 0.056178 | 0.030616 | -0.0063668 | -0.0029078 | -0.0083126 | 0.050354 | 63.2996 | -59.5963 | 63.652 | -59.4635 | -59.7839 | -59.7656 | 0.032043 | 63.3316 | -59.5688 | 63.6017 | -59.6237 | -59.7198 | -59.729 | -0.054931 | -0.1236 | 0.22888 | 0.07782 | -0.2243 | -0.24261 | -0.16937 | -0.18768 | -0.027466 | -0.091553 | 0.17853 | -0.082397 | -0.18768 | -0.17853 | -0.16022 | -0.15106 | 0.13275 | 123.2483 | -0.054931 | 123.1705 | 122.8958 | 122.9004 | 122.8409 | 122.8729 | -123.0194 | -122.9919 | 123.1934 | 123.143 | 59.5917 | 59.5734
104.0312 | 123.1888 | -59.5551 | 63.4048 | 0.0072204 | 0.010956 | 0.066853 | 0.064055 | -0.0046106 | -0.0031087 | 0.0013532 | 0.24348 | -0.0029296 | 0.054042 | 0.066932 | -0.0052988 | -0.0050448 | 0.0066414 | -0.004578 | 63.2355 | -59.5642 | 63.6108 | -59.5871 | -59.8251 | -59.8618 | 0 | 63.2904 | -59.5505 | 63.5376 | -59.5963 | -59.697 | -59.697 | -0.009155 | -0.16937 | 0.20599 | -0.032043 | -0.3067 | -0.27008 | -0.29755 | -0.26093 | 0.004578 | -0.11444 | 0.13275 | -0.041198 | -0.14191 | -0.14191 | -0.14648 | -0.14648 | -0.022888 | 123.175 | -0.045776 | 123.0881 | 122.7997 | 122.8409 | 122.7905 | 122.8455 | -122.9691 | -122.9553 | 123.1659 | 123.0927 | 59.5505 | 59.5551
104.9531 | 123.1888 | -59.5322 | 63.3911 | 0.068255 | 0.0056153 | 0.061512 | 0.057646 | -0.0067466 | -0.0063137 | -0.0071918 | 0.090897 | -0.0061336 | 0.073268 | 0.039161 | -0.0042298 | -0.0007718 | -0.010449 | -0.045776 | 63.1989 | -59.5825 | 63.5101 | -59.5505 | -59.8984 | -59.8755 | 0.018311 | 63.295 | -59.5734 | 63.6063 | -59.5963 | -59.6695 | -59.7107 | -0.050354 | -0.19226 | 0.11902 | -0.01831 | -0.34332 | -0.36621 | -0.29297 | -0.31586 | -0.041198 | -0.09613 | 0.21515 | -0.064086 | -0.17853 | -0.13733 | -0.13733 | -0.096131 | 0.032044 | 123.0927 | -0.022888 | 123.1796 | 122.7814 | 122.8683 | 122.731 | 122.8271 | -122.9736 | -122.9645 | 123.0423 | 123.1384 | 59.4864 | 59.5505
106.0312 | 123.175 | -59.5551 | 63.4735 | 0.068255 | 0.0024113 | 0.064717 | 0.059782 | 0.0017974 | 0.0086403 | -0.011464 | 0.014603 | 0.0034794 | 0.067927 | 0.066932 | -0.0063668 | 0.0002962 | -0.0040396 | 0.013733 | 63.3316 | -59.5734 | 63.7436 | -59.3948 | -59.7336 | -59.7244 | 0.013733 | 63.382 | -59.5779 | 63.5925 | -59.6649 | -59.729 | -59.729 | -0.01831 | -0.14191 | 0.27008 | 0.16022 | -0.16937 | -0.17853 | -0.15106 | -0.16022 | -0.022888 | -0.091553 | 0.11902 | -0.10986 | -0.17395 | -0.17395 | -0.15106 | -0.15106 | 0.17853 | 123.317 | -0.086975 | 123.1705 | 122.905 | 122.9599 | 122.8867 | 122.937 | -123.0469 | -123.0515 | 123.2986 | 123.1476 | 59.5688 | 59.5688
106.9531 | 123.1018 | -59.5413 | 63.4598 | 0.068255 | -0.0082697 | 0.056172 | 0.069395 | -0.00033857 | -0.031949 | -0.0018508 | 0.060379 | 0.0088204 | 0.071131 | 0.053047 | -0.0074348 | -0.0018398 | 0.016254 | -0.009155 | 63.2812 | -59.61 | 63.6337 | -59.4406 | -59.7977 | -59.7244 | -0.045776 | 63.3499 | -59.5734 | 63.533 | -59.6786 | -59.7656 | -59.7656 | -0.068664 | -0.17853 | 0.17395 | 0.10071 | -0.1831 | -0.25635 | -0.11444 | -0.18768 | -0.032043 | -0.10986 | 0.073242 | -0.13733 | -0.2243 | -0.2243 | -0.19226 | -0.19226 | 0.16937 | 123.2437 | -0.10529 | 123.1064 | 122.8912 | 122.9233 | 122.8226 | 122.8912 | -123.0698 | -123.0331 | 123.175 | 123.0743 | 59.5322 | 59.4955
107.9531 | 123.143 | -59.5505 | 63.4369 | 0.022479 | -0.0050657 | 0.061512 | 0.068327 | -0.0046106 | -0.038357 | 0.0013532 | -0.046432 | 0.0024114 | 0.0722 | 0.05091 | -0.013843 | 0.018454 | -0.0019036 | 0.027466 | 63.2904 | -59.6237 | 63.6932 | -59.4681 | -59.7427 | -59.7794 | -0.059509 | 63.3591 | -59.5596 | 63.5147 | -59.6146 | -59.8114 | -59.761 | -0.073242 | -0.14648 | 0.25635 | 0.082397 | -0.22888 | -0.19226 | -0.15564 | -0.11902 | -0.009155 | -0.07782 | 0.077819 | -0.064087 | -0.21057 | -0.26092 | -0.20142 | -0.25177 | 0.15564 | 123.317 | -0.054932 | 123.0743 | 122.9141 | 122.9187 | 122.8409 | 122.9095 | -123.0606 | -122.9965 | 123.2437 | 123.0652 | 59.5779 | 59.491
109.0312 | 123.2208 | -59.5551 | 63.4094 | 0.083514 | 0.0013433 | 0.044423 | 0.05551 | 0.0017974 | 0.012912 | -0.0082598 | 0.30452 | -0.0007936 | 0.068995 | 0.069068 | 0.012859 | 0.0035002 | 0.014118 | 0.022888 | 63.2858 | -59.6008 | 63.5925 | -59.5184 | -59.8114 | -59.8389 | 0.073242 | 63.3133 | -59.5551 | 63.5284 | -59.5596 | -59.7198 | -59.7015 | -0.045776 | -0.1236 | 0.1831 | 0.036621 | -0.28381 | -0.25635 | -0.23804 | -0.21057 | 0 | -0.096131 | 0.11902 | -0.004577 | -0.14648 | -0.1648 | -0.14648 | -0.1648 | 0.082397 | 123.1934 | -0.004577 | 123.0835 | 122.8867 | 122.8683 | 122.8409 | 122.8683 | -123.0103 | -122.9645 | 123.1476 | 123.0835 | 59.5779 | 59.6283
109.9531 | 123.1293 | -59.5779 | 63.4369 | 0.083514 | 0.0077523 | 0.067921 | 0.067259 | 0.0039344 | 0.018253 | 0.0088302 | 0.060379 | 0.0098884 | 0.068995 | 0.046638 | 4.2208e-05 | -0.0007718 | -0.018994 | -0.050354 | 63.2996 | -59.642 | 63.6475 | -59.3353 | -59.6146 | -59.7244 | -0.054932 | 63.3316 | -59.5871 | 63.4872 | -59.7107 | -59.816 | -59.8022 | -0.064087 | -0.13733 | 0.21057 | 0.24262 | -0.14648 | -0.036621 | -0.082397 | 0.027466 | -0.009155 | -0.10529 | 0.050354 | -0.13275 | -0.2243 | -0.23804 | -0.21515 | -0.22888 | 0.3067 | 123.2895 | -0.1236 | 123.0743 | 122.9416 | 122.9187 | 122.8775 | 122.9095 | -123.0789 | -123.024 | 123.2254 | 123.0652 | 59.5276 | 59.523
111.0312 | 123.1842 | -59.5413 | 63.414 | 0.11403 | 0.0024113 | 0.059376 | 0.070463 | 0.018887 | 0.0097083 | -0.010396 | 0.33504 | 0.0002754 | 0.065791 | 0.053047 | -0.0063668 | 0.0045682 | -0.015789 | -0.022888 | 63.2538 | -59.5871 | 63.588 | -59.523 | -59.7885 | -59.8801 | -0.054932 | 63.3087 | -59.5596 | 63.5422 | -59.5367 | -59.7656 | -59.6786 | -0.045776 | -0.16022 | 0.17395 | 0.018311 | -0.33874 | -0.24719 | -0.29297 | -0.20142 | -0.01831 | -0.10529 | 0.12817 | 0.004578 | -0.13733 | -0.2243 | -0.11902 | -0.20599 | 0.064087 | 123.175 | 0.022888 | 123.1018 | 122.8409 | 122.8683 | 122.7951 | 122.85 | -123.0011 | -122.9736 | 123.1293 | 123.0835 | 59.5184 | 59.4864
111.9531 | 123.1338 | -59.5871 | 63.4186 | 0.11403 | 0.0045473 | 0.083943 | 0.068327 | -0.01102 | 0.0032993 | 0.0056262 | -0.046432 | 0.010956 | 0.071131 | 0.057319 | -0.010639 | 0.0045682 | -0.018994 | -0.26093 | 63.2355 | -59.6878 | 63.6429 | -59.4498 | -59.697 | -59.7198 | -0.10529 | 63.3224 | -59.5963 | 63.5284 | -59.7061 | -59.7794 | -59.8068 | -0.10071 | -0.1831 | 0.2243 | 0.13733 | -0.13275 | -0.10986 | -0.032044 | -0.009155 | -0.009155 | -0.09613 | 0.10986 | -0.11902 | -0.21973 | -0.19226 | -0.21057 | -0.18311 | 0.23804 | 123.3307 | -0.10986 | 123.1247 | 122.9233 | 122.9187 | 122.8226 | 122.9095 | -123.1064 | -123.0148 | 123.23 | 123.1155 | 59.3262 | 59.4818
113.0312 | 123.2025 | -59.5093 | 63.414 | -0.023297 | -0.013611 | 0.072194 | 0.064055 | -0.0046106 | 0.0032993 | -0.0071918 | 0.16719 | -0.0018616 | 0.076472 | 0.090431 | 0.0053832 | -0.0050448 | -0.010449 | 0.004578 | 63.2812 | -59.5688 | 63.6017 | -59.5322 | -59.7748 | -59.848 | -0.041199 | 63.2996 | -59.5825 | 63.5834 | -59.5688 | -59.6832 | -59.6649 | -0.05951 | -0.13275 | 0.18768 | -0.022889 | -0.33875 | -0.2655 | -0.27923 | -0.20599 | -0.073243 | -0.11444 | 0.16937 | -0.05951 | -0.15564 | -0.17395 | -0.082397 | -0.10071 | 0.036621 | 123.1705 | 0.013733 | 123.1659 | 122.85 | 122.8821 | 122.7905 | 122.8088 | -122.9828 | -122.9965 | 123.111 | 123.0927 | 59.5139 | 59.4681
113.9531 | 123.2025 | -59.5871 | 63.4415 | 0.052997 | 0.0066833 | 0.058308 | 0.0726 | 0.0017974 | 0.0022313 | -0.0061228 | -0.15324 | 0.0056154 | 0.063655 | 0.033821 | -0.0010258 | 0.0024322 | -0.011517 | -0.082397 | 63.2858 | -59.6466 | 63.707 | -59.3628 | -59.7153 | -59.7198 | -0.12817 | 63.3224 | -59.6008 | 63.5147 | -59.729 | -60.0586 | -60.0632 | -0.059509 | -0.15564 | 0.2655 | 0.2243 | -0.13275 | -0.12817 | -0.073243 | -0.068665 | -0.013733 | -0.11902 | 0.073242 | -0.14191 | -0.47607 | -0.4715 | -0.46234 | -0.45776 | 0.28381 | 123.3536 | -0.12817 | 123.1155 | 122.9324 | 122.9233 | 122.8729 | 122.9095 | -123.0881 | -123.0423 | 123.2941 | 123.1018 | 59.5047 | 59.4589
115.0312 | 123.2529 | -59.5047 | 63.4277 | 0.068255 | 0.0088203 | 0.054036 | 0.058714 | 0.0060704 | -0.011654 | -0.0029188 | 0.18245 | -0.0061336 | 0.059382 | 0.037025 | -0.0063668 | 0.0035002 | -0.0061756 | 0.059509 | 63.2584 | -59.5734 | 63.6108 | -59.5917 | -59.8297 | -59.8618 | 0.10529 | 63.2996 | -59.5276 | 63.6017 | -59.523 | -59.5871 | -59.5963 | -0.068664 | -0.16937 | 0.18311 | -0.086975 | -0.35706 | -0.32501 | -0.28839 | -0.25635 | -0.022888 | -0.12817 | 0.17395 | -0.01831 | -0.091552 | -0.082397 | -0.068664 | -0.059509 | -0.018311 | 123.1842 | 0.004578 | 123.1293 | 122.8317 | 122.8271 | 122.7631 | 122.8043 | -123.0011 | -122.9553 | 123.1155 | 123.1064 | 59.5642 | 59.61
115.9531 | 123.1659 | -59.5505 | 63.3957 | 0.20559 | -0.0050657 | 0.055104 | 0.069395 | 0.01141 | 0.0011633 | 0.010966 | 0.014603 | 0.0077514 | 0.047633 | 0.055183 | -0.0020938 | -0.0039768 | -0.0029716 | -0.10071 | 63.2721 | -59.6329 | 63.6658 | -59.4177 | -59.8022 | -59.7473 | -0.068665 | 63.3224 | -59.5825 | 63.5971 | -59.7198 | -59.7656 | -59.7519 | -0.082398 | -0.1236 | 0.27008 | 0.13275 | -0.19684 | -0.25177 | -0.11444 | -0.16937 | -0.032044 | -0.073242 | 0.20142 | -0.16937 | -0.20142 | -0.21515 | -0.16937 | -0.1831 | 0.21515 | 123.2986 | -0.13733 | 123.1796 | 122.905 | 122.905 | 122.8226 | 122.8729 | -123.0286 | -122.9782 | 123.2162 | 123.1476 | 59.4498 | 59.4818
117.0312 | 123.1934 | -59.5367 | 63.414 | 0.022479 | 0.0045473 | 0.065785 | 0.059782 | 0.0028664 | 0.0054353 | 0.012035 | 0.42659 | 0.0024114 | 0.03802 | 0.10645 | -0.012775 | -0.0039768 | 0.0034374 | -0.027466 | 63.2584 | -59.5505 | 63.6383 | -59.5139 | -59.7977 | -59.8251 | 0.068665 | 63.3453 | -59.5322 | 63.5788 | -59.642 | -59.6649 | -59.7656 | -0.013733 | -0.15564 | 0.22431 | 0.022888 | -0.28839 | -0.26093 | -0.27466 | -0.24719 | 0.004577 | -0.068664 | 0.16479 | -0.10529 | -0.22888 | -0.12817 | -0.23346 | -0.13275 | 0.036621 | 123.1888 | -0.10986 | 123.111 | 122.8088 | 122.8775 | 122.7951 | 122.8821 | -122.9645 | -122.9462 | 123.175 | 123.1155 | 59.5093 | 59.6054
117.9531 | 123.262 | -59.523 | 63.3774 | 0.20559 | 0.0077523 | 0.064717 | 0.0726 | -0.0035426 | -0.0052457 | 0.012035 | 0.090897 | 0.010956 | 0.068995 | 0.058387 | -0.010639 | 0.0024322 | -0.0072446 | -0.009155 | 63.2309 | -59.5551 | 63.4644 | -59.5596 | -59.903 | -59.8846 | 0.018311 | 63.295 | -59.5322 | 63.6383 | -59.5734 | -59.7061 | -59.6603 | -0.032044 | -0.14648 | 0.086975 | -0.036621 | -0.36163 | -0.37994 | -0.32959 | -0.3479 | -0.009156 | -0.082397 | 0.26093 | -0.050354 | -0.13733 | -0.18311 | -0.12817 | -0.17395 | -0.004577 | 123.0194 | -0.041198 | 123.1705 | 122.7859 | 122.8271 | 122.7539 | 122.818 | -122.9324 | -122.9095 | 122.9874 | 123.1613 | 59.5139 | 59.5413
118.9531 | 123.1476 | -59.5367 | 63.4186 | -0.67942 | 0.0077523 | 0.055104 | 0.0726 | -0.0035426 | 0.0022313 | -0.0082598 | -0.1685 | 0.010956 | 0.082881 | 0.069068 | -0.013843 | -0.0050448 | -0.0051076 | 0.10986 | 63.2721 | -59.6054 | 63.7665 | -59.4086 | -59.7107 | -59.8114 | -0.10986 | 63.3545 | -59.5825 | 63.4827 | -59.6924 | -59.816 | -59.7885 | -0.068665 | -0.14648 | 0.3479 | 0.12817 | -0.27466 | -0.17395 | -0.20599 | -0.10529 | -0.045777 | -0.064087 | 0.064087 | -0.15564 | -0.25177 | -0.27924 | -0.20599 | -0.23346 | 0.19684 | 123.3719 | -0.10986 | 123.0652 | 122.8775 | 122.937 | 122.8088 | 122.8912 | -123.024 | -123.0011 | 123.3032 | 123.0194 | 59.6466 | 59.4269
119.9531 | 123.1796 | -59.5184 | 63.4048 | 0.083514 | 0.0098883 | 0.060444 | 0.051237 | -0.0014066 | -0.0063137 | 0.0056262 | 0.029861 | -0.0093376 | 0.045497 | 0.090431 | -0.0042298 | -0.0050448 | 0.0087774 | -0.10529 | 63.2492 | -59.5963 | 63.5559 | -59.4635 | -59.8251 | -59.8114 | -0.027466 | 63.3041 | -59.5551 | 63.5971 | -59.5734 | -59.697 | -59.6786 | -0.077819 | -0.15564 | 0.15106 | 0.054932 | -0.29297 | -0.3067 | -0.21515 | -0.22888 | -0.036621 | -0.10071 | 0.19226 | -0.054931 | -0.16022 | -0.17853 | -0.1236 | -0.14191 | 0.13275 | 123.1522 | -0.01831 | 123.1522 | 122.8455 | 122.8592 | 122.7676 | 122.8226 | -123.0011 | -122.9599 | 123.0743 | 123.1155 | 59.4131 | 59.491
121.0312 | 123.2071 | -59.523 | 63.446 | -0.053815 | 0.012024 | 0.063649 | 0.069395 | 0.0071384 | 0.0097083 | -0.011464 | 0.25874 | 0.0034794 | 0.07754 | 0.063728 | -0.0095708 | 0.0056372 | -0.0061756 | 0.041199 | 63.2584 | -59.5551 | 63.5559 | -59.5367 | -59.8938 | -59.8206 | 0.15564 | 63.3316 | -59.5184 | 63.6887 | -59.5596 | -59.61 | -59.6375 | -0.032044 | -0.18768 | 0.10986 | -0.013733 | -0.29755 | -0.37079 | -0.2655 | -0.33875 | 0.004577 | -0.11444 | 0.24262 | -0.036621 | -0.11444 | -0.086975 | -0.11902 | -0.091552 | 0.018311 | 123.111 | -0.041198 | 123.2071 | 122.8134 | 122.85 | 122.7814 | 122.8546 | -123.0011 | -122.9645 | 123.0789 | 123.2117 | 59.5642 | 59.6786
121.9688 | 123.2254 | -59.5413 | 63.4186 | 0.25136 | -0.0072017 | 0.060444 | 0.059782 | 0.0017974 | 0.012912 | -0.016805 | 0.19771 | 0.0056154 | 0.073268 | 0.034889 | -0.0010258 | -0.0061128 | -0.013653 | -0.009155 | 63.2584 | -59.5642 | 63.5605 | -59.5093 | -59.8343 | -59.8526 | 0.009155 | 63.327 | -59.5596 | 63.6063 | -59.5551 | -59.6603 | -59.6283 | -0.022888 | -0.16022 | 0.14191 | 0.032044 | -0.31128 | -0.29297 | -0.28839 | -0.27008 | -0.01831 | -0.091553 | 0.18768 | -0.013733 | -0.086975 | -0.11902 | -0.068665 | -0.10071 | 0.054932 | 123.1247 | 0.004577 | 123.1659 | 122.8226 | 122.8867 | 122.7997 | 122.8683 | -122.9828 | -122.9782 | 123.1018 | 123.1476 | 59.5322 | 59.5505
123.0312 | 123.1705 | -59.5139 | 63.4186 | -0.023297 | 0.00027529 | 0.059376 | 0.066191 | 0.021024 | 0.0032993 | 0.0034902 | 0.16719 | -0.0029296 | 0.088221 | 0.073341 | -0.0063668 | 0.0045682 | 0.010913 | -0.068665 | 63.2446 | -59.5779 | 63.5559 | -59.4681 | -59.848 | -59.8206 | -0.032043 | 63.3041 | -59.5734 | 63.6108 | -59.6054 | -59.7061 | -59.6878 | -0.064087 | -0.17395 | 0.13733 | 0.045776 | -0.3067 | -0.33417 | -0.24262 | -0.27008 | -0.059509 | -0.11444 | 0.19226 | -0.091553 | -0.17395 | -0.19226 | -0.11444 | -0.13275 | 0.10986 | 123.1338 | -0.032044 | 123.1842 | 122.8226 | 122.8775 | 122.7585 | 122.818 | -122.9965 | -122.9919 | 123.0698 | 123.1247 | 59.4452 | 59.4818
123.9531 | 123.2162 | -59.5276 | 63.3636 | 0.11403 | -0.0050657 | 0.071125 | 0.071531 | -0.0056786 | 0.01398 | -0.0018508 | 0.060379 | -0.0029296 | 0.062587 | 0.06266 | -0.013843 | 0.0067052 | -0.015789 | 0.009155 | 63.2309 | -59.6054 | 63.5239 | -59.5642 | -59.8343 | -60.0266 | 0.14191 | 63.2996 | -59.523 | 63.6108 | -59.5642 | -59.7244 | -59.5871 | -0.07782 | -0.13275 | 0.16022 | -0.036621 | -0.49896 | -0.3067 | -0.42114 | -0.22888 | 0.004578 | -0.064086 | 0.24719 | -0.036621 | -0.059509 | -0.19684 | -0.064087 | -0.20142 | 0.041199 | 123.1293 | -0.041199 | 123.1338 | 122.8363 | 122.8226 | 122.7585 | 122.8271 | -122.9691 | -122.8867 | 123.0515 | 123.1384 | 59.5367 | 59.6695
125.0312 | 123.111 | -59.5459 | 63.4689 | 0.15981 | 0.0034793 | 0.058308 | 0.067259 | 0.012479 | 0.0011633 | 0.00028524 | 0.090897 | 0.0056154 | 0.058314 | 0.063728 | -0.0010258 | 0.010977 | 0.0055734 | 0.004578 | 63.295 | -59.6054 | 63.6292 | -59.2575 | -59.5139 | -59.7519 | -0.091553 | 63.3591 | -59.5688 | 63.5559 | -59.6237 | -59.7748 | -59.7336 | -0.05951 | -0.17395 | 0.16022 | 0.28839 | -0.20599 | 0.032043 | -0.14648 | 0.091553 | -0.022889 | -0.10986 | 0.086975 | -0.07782 | -0.18768 | -0.22888 | -0.16479 | -0.20599 | 0.3479 | 123.2346 | -0.054931 | 123.1247 | 122.9004 | 122.9279 | 122.8409 | 122.905 | -123.0743 | -123.0377 | 123.175 | 123.1018 | 59.5505 | 59.4543
125.9531 | 123.2117 | -59.5276 | 63.3911 | 0.037738 | 0.0066833 | 0.063649 | 0.079008 | 0.01141 | -0.015927 | -0.00078276 | 0.060379 | 0.0056154 | 0.07754 | 0.038093 | -0.0010258 | 0.0035002 | 0.0045054 | 0.022888 | 63.2309 | -59.5871 | 63.5147 | -59.6191 | -59.8526 | -59.903 | -0.004578 | 63.2767 | -59.5734 | 63.5696 | -59.5413 | -59.7198 | -59.6375 | -0.059509 | -0.16022 | 0.1236 | -0.091553 | -0.37537 | -0.32501 | -0.31586 | -0.2655 | -0.045776 | -0.11444 | 0.17853 | -0.013733 | -0.10986 | -0.19226 | -0.064087 | -0.14649 | -0.032044 | 123.1018 | 0.032043 | 123.143 | 122.818 | 122.85 | 122.7585 | 122.8043 | -122.9782 | -122.9645 | 123.0423 | 123.0972 | 59.5505 | 59.523
127.0312 | 123.2437 | -59.5367 | 63.4277 | 0.12929 | -0.0029297 | 0.063649 | 0.065123 | 0.0071384 | -0.0031087 | -0.014668 | 0.15193 | -0.0061336 | 0.047633 | 0.038093 | -0.0095708 | -0.0050448 | -0.010449 | 0.054932 | 63.2767 | -59.5734 | 63.5193 | -59.5459 | -59.8938 | -59.8572 | 0.13275 | 63.3133 | -59.5459 | 63.7711 | -59.7336 | -59.7656 | -59.7061 | -0.036621 | -0.15106 | 0.091553 | -0.009155 | -0.32043 | -0.35706 | -0.28381 | -0.32044 | -0.009155 | -0.11444 | 0.34332 | -0.19684 | -0.16937 | -0.22888 | -0.16022 | -0.21973 | 0.027466 | 123.0927 | -0.18768 | 123.317 | 122.85 | 122.8592 | 122.8134 | 122.85 | -123.0011 | -122.9736 | 123.056 | 123.3078 | 59.5917 | 59.6695
127.9531 | 123.2437 | -59.5139 | 63.4048 | 0.052997 | -0.0029297 | 0.064717 | 0.067259 | 0.00072943 | -0.0073817 | 0.0045582 | -0.00065608 | 0.0077514 | 0.066859 | 0.060523 | -0.0063668 | 0.0045682 | -0.0083126 | -0.018311 | 63.2263 | -59.6237 | 63.5468 | -59.5642 | -59.8343 | -59.9396 | -0.15106 | 63.2263 | -59.6008 | 63.5925 | -59.523 | -59.7382 | -59.6283 | -0.10986 | -0.17853 | 0.14191 | -0.050354 | -0.42572 | -0.32044 | -0.31586 | -0.21057 | -0.086975 | -0.17853 | 0.18768 | -0.009155 | -0.11444 | -0.2243 | -0.027466 | -0.13733 | 0.059509 | 123.1705 | 0.07782 | 123.1934 | 122.85 | 122.8271 | 122.7402 | 122.7402 | -123.0286 | -123.0057 | 123.0606 | 123.1064 | 59.4955 | 59.3628
129.0312 | 123.23 | -59.5093 | 63.4048 | 0.11403 | 0.017365 | 0.059376 | 0.059782 | -0.01102 | -0.013791 | 0.0077622 | 0.16719 | -0.0018616 | 0.068995 | 0.041297 | -0.0052988 | 0.0077732 | -0.025402 | 0.009155 | 63.2721 | -59.5963 | 63.5422 | -59.5093 | -59.8343 | -59.848 | -0.036621 | 63.2858 | -59.5688 | 63.5925 | -59.5093 | -59.6603 | -59.6329 | -0.086975 | -0.13275 | 0.13733 | 0 | -0.33875 | -0.32501 | -0.25177 | -0.23804 | -0.05951 | -0.11902 | 0.18768 | 0 | -0.1236 | -0.15106 | -0.064087 | -0.091552 | 0.086975 | 123.1384 | 0.05951 | 123.1613 | 122.8683 | 122.8546 | 122.7814 | 122.7951 | -123.0011 | -122.9736 | 123.0515 | 123.1018 | 59.5184 | 59.4727
129.9531 | 123.1338 | -59.5505 | 63.4415 | 0.098773 | -0.0050657 | 0.059376 | 0.064055 | 0.01141 | 0.0097083 | 0.0013532 | 0.090897 | -0.0093376 | 0.049769 | 0.071205 | 0.0021782 | 0.0002962 | -0.02113 | 0.11444 | 63.295 | -59.5734 | 63.6246 | -59.5551 | -59.7473 | -59.8114 | 0.068665 | 63.3636 | -59.5734 | 63.5239 | -59.5642 | -59.7336 | -59.7015 | -0.022888 | -0.14648 | 0.18311 | -0.004578 | -0.26092 | -0.19684 | -0.23804 | -0.17395 | -0.022888 | -0.07782 | 0.082398 | -0.013733 | -0.15106 | -0.18311 | -0.12817 | -0.16022 | 0.01831 | 123.1979 | 0.009155 | 123.0972 | 122.8683 | 122.937 | 122.8455 | 122.9141 | -123.0148 | -123.0148 | 123.175 | 123.0743 | 59.6649 | 59.6191
131.0312 | 123.2162 | -59.5322 | 63.4598 | 0.068255 | -0.0029297 | 0.068989 | 0.067259 | 0.0028664 | -0.0084497 | -0.0061228 | 0.15193 | 0.0066834 | 0.068995 | 0.058387 | 0.010723 | 0.012045 | -0.0083126 | 0.11902 | 63.2629 | -59.5596 | 63.5788 | -59.5551 | -59.816 | -59.8343 | 0.036621 | 63.3087 | -59.5413 | 63.5605 | -59.5184 | -59.6878 | -59.642 | -0.027465 | -0.19684 | 0.11902 | -0.022888 | -0.30212 | -0.28381 | -0.27466 | -0.25635 | -0.009155 | -0.15106 | 0.10071 | 0.013733 | -0.10986 | -0.15564 | -0.10071 | -0.14648 | 0.004577 | 123.1384 | 0.022888 | 123.1018 | 122.8226 | 122.85 | 122.7951 | 122.8409 | -123.0194 | -123.0011 | 123.111 | 123.0927 | 59.6512 | 59.5688
131.9531 | 123.2391 | -59.5047 | 63.3865 | 0.083514 | 0.0024113 | 0.064717 | 0.064055 | 0.017819 | -0.021267 | 0.0034902 | -0.015915 | 0.010956 | 0.057246 | 0.077613 | -0.0010258 | 0.0056372 | -0.0061756 | -0.004578 | 63.2584 | -59.6329 | 63.6658 | -59.5688 | -59.8206 | -59.8663 | 0.022888 | 63.295 | -59.5825 | 63.588 | -59.5779 | -59.697 | -59.6603 | -0.12817 | -0.12817 | 0.27923 | -0.064087 | -0.36163 | -0.31586 | -0.23346 | -0.18768 | -0.07782 | -0.091553 | 0.20142 | -0.073242 | -0.15564 | -0.19226 | -0.077819 | -0.11444 | 0.064087 | 123.2986 | 0.004578 | 123.1705 | 122.8912 | 122.8775 | 122.7631 | 122.7997 | -123.0194 | -122.9691 | 123.1705 | 123.0927 | 59.5001 | 59.5276
132.9531 | 123.2162 | -59.4955 | 63.382 | 0.022479 | 0.0034793 | 0.065785 | 0.066191 | 0.0039344 | -0.0084497 | -0.0082598 | -0.10747 | 0.0034794 | 0.066859 | 0.04557 | 4.2208e-05 | 0.012045 | 0.0045054 | -0.064087 | 63.2538 | -59.6146 | 63.588 | -59.4498 | -59.8572 | -59.8251 | -0.082397 | 63.2858 | -59.5963 | 63.5971 | -59.5825 | -59.7427 | -59.6191 | -0.11902 | -0.12817 | 0.20599 | 0.045776 | -0.32959 | -0.36163 | -0.21057 | -0.24262 | -0.10071 | -0.09613 | 0.21515 | -0.086976 | -0.1236 | -0.24719 | -0.022889 | -0.14648 | 0.16479 | 123.2025 | 0.013732 | 123.1934 | 122.8683 | 122.8821 | 122.7493 | 122.7814 | -122.9965 | -122.9782 | 123.0835 | 123.0927 | 59.4315 | 59.4131
134.0312 | 123.0698 | -59.5459 | 63.4506 | 0.098773 | 0.0056153 | 0.056172 | 0.075804 | -0.0067466 | 0.016117 | 0.0088302 | 0.12141 | -0.0029296 | 0.076472 | 0.065864 | -0.0052988 | 0.0099092 | -0.015789 | -0.018311 | 63.3224 | -59.5917 | 63.5971 | -59.5139 | -59.761 | -59.6558 | -0.045776 | 63.3728 | -59.5551 | 63.533 | -59.6603 | -59.7198 | -59.7885 | -0.045777 | -0.12817 | 0.14648 | 0.032043 | -0.10986 | -0.21515 | -0.064087 | -0.16937 | -0.009156 | -0.07782 | 0.082397 | -0.11444 | -0.24262 | -0.17395 | -0.23346 | -0.1648 | 0.07782 | 123.1888 | -0.10529 | 123.0881 | 122.9141 | 122.9279 | 122.8683 | 122.9187 | -123.0423 | -123.0057 | 123.143 | 123.0789 | 59.5276 | 59.5001
134.9531 | 123.2208 | -59.5367 | 63.3865 | -0.0080386 | 0.0024113 | 0.072194 | 0.074736 | -0.0014066 | -0.019131 | -0.00078276 | 0.12141 | -0.0029296 | 0.085017 | 0.017799 | -0.0074348 | 0.010977 | -0.010449 | 0 | 63.2263 | -59.5779 | 63.501 | -59.5688 | -59.8892 | -59.9167 | -0.009155 | 63.2858 | -59.5688 | 63.6017 | -59.5505 | -59.7519 | -59.6146 | -0.041199 | -0.16022 | 0.11444 | -0.032044 | -0.37994 | -0.35248 | -0.33875 | -0.31128 | -0.032044 | -0.10071 | 0.21515 | -0.013733 | -0.07782 | -0.21515 | -0.045776 | -0.1831 | 0.009155 | 123.0789 | 0.018311 | 123.1705 | 122.8043 | 122.8546 | 122.7631 | 122.8226 | -122.9645 | -122.9553 | 123.0377 | 123.1384 | 59.5367 | 59.5276
136.0312 | 123.1293 | -59.5413 | 63.4552 | 0.11403 | 0.0034793 | 0.062581 | 0.071531 | -0.0099516 | -0.043698 | -0.0093278 | 0.33504 | 0.0066834 | 0.079676 | 0.04557 | -0.0010258 | 0.0067052 | 0.0055734 | 0 | 63.3316 | -59.5917 | 63.6383 | -59.3903 | -59.7519 | -59.7107 | -0.054932 | 63.3545 | -59.5779 | 63.5605 | -59.61 | -59.729 | -59.6878 | -0.050354 | -0.1236 | 0.18311 | 0.15106 | -0.16937 | -0.21057 | -0.11902 | -0.16022 | -0.036621 | -0.10071 | 0.10529 | -0.068664 | -0.14648 | -0.18768 | -0.10986 | -0.15106 | 0.20142 | 123.23 | -0.032043 | 123.1384 | 122.9233 | 122.9324 | 122.8729 | 122.8958 | -123.0469 | -123.0331 | 123.1796 | 123.1018 | 59.5413 | 59.4864
136.9531 | 123.2025 | -59.5276 | 63.3865 | 0.083514 | 0.0045473 | 0.067921 | 0.06085 | -0.0056786 | -0.016995 | -0.0029188 | 0.19771 | 0.0034794 | 0.064723 | 0.089363 | 0.0011102 | 0.0088412 | 0.0077094 | 0.032043 | 63.2401 | -59.6008 | 63.5422 | -59.5825 | -59.8526 | -59.9258 | -0.004578 | 63.2812 | -59.5734 | 63.5788 | -59.5551 | -59.7656 | -59.6237 | -0.073242 | -0.14648 | 0.15564 | -0.054932 | -0.39825 | -0.32501 | -0.32501 | -0.25177 | -0.045776 | -0.10529 | 0.19226 | -0.027466 | -0.09613 | -0.23804 | -0.050354 | -0.19226 | 0.01831 | 123.143 | 0.01831 | 123.1522 | 122.8409 | 122.8546 | 122.7676 | 122.8088 | -122.9874 | -122.9599 | 123.0698 | 123.1064 | 59.5596 | 59.523
138.0312 | 123.2346 | -59.5276 | 63.4186 | -0.084332 | 0.0045473 | 0.062581 | 0.064055 | -0.016361 | 0.0022313 | -0.0071918 | 0.31978 | 0.0002754 | 0.087153 | 0.068 | -0.0052988 | -0.0071808 | -0.022198 | 0.032043 | 63.2538 | -59.5642 | 63.533 | -59.4772 | -59.8846 | -59.8343 | 0.036621 | 63.2904 | -59.5413 | 63.62 | -59.5093 | -59.642 | -59.6146 | -0.036621 | -0.16479 | 0.11444 | 0.050354 | -0.3067 | -0.35706 | -0.27008 | -0.32044 | -0.013733 | -0.12817 | 0.20142 | 0.018311 | -0.086975 | -0.11444 | -0.073242 | -0.10071 | 0.086975 | 123.0972 | 0.032044 | 123.1613 | 122.818 | 122.8317 | 122.7814 | 122.818 | -122.9828 | -122.9599 | 123.0606 | 123.1476 | 59.5596 | 59.5642
138.9531 | 123.2071 | -59.5505 | 63.3957 | -0.038556 | -0.012543 | 0.071125 | 0.06085 | -0.0035426 | 9.5287e-05 | -0.0050548 | -0.07695 | 0.0098884 | 0.05511 | 0.049842 | -0.0010258 | 0.018454 | -0.025402 | -0.059509 | 63.2675 | -59.6558 | 63.6108 | -59.5001 | -59.7656 | -59.8663 | -0.054932 | 63.3179 | -59.5642 | 63.5468 | -59.5322 | -59.7336 | -59.6283 | -0.10529 | -0.12817 | 0.21515 | 0.050354 | -0.31586 | -0.21515 | -0.21057 | -0.10986 | -0.013733 | -0.07782 | 0.15106 | 0.01831 | -0.07782 | -0.18311 | -0.064087 | -0.16937 | 0.15564 | 123.2666 | 0.032043 | 123.111 | 122.9233 | 122.8821 | 122.818 | 122.8683 | -123.0515 | -122.9599 | 123.1613 | 123.0972 | 59.491 | 59.4955
140.0312 | 123.1338 | -59.5596 | 63.4644 | 0.32766 | -0.00079271 | 0.047627 | 0.058714 | 0.00072943 | 0.019321 | 0.0024222 | 0.060379 | 0.0066834 | 0.080744 | 0.061592 | 0.0011102 | 0.010977 | 0.0013004 | 0.027466 | 63.3362 | -59.5871 | 63.6749 | -59.2896 | -59.5093 | -59.7382 | -0.054932 | 63.3499 | -59.5825 | 63.5239 | -59.61 | -59.8114 | -59.7015 | -0.027466 | -0.12817 | 0.21057 | 0.27008 | -0.17853 | 0.050354 | -0.15106 | 0.07782 | -0.022889 | -0.11444 | 0.05951 | -0.050354 | -0.14191 | -0.25177 | -0.11902 | -0.22888 | 0.29755 | 123.262 | -0.027465 | 123.1064 | 122.9233 | 122.9324 | 122.8958 | 122.9095 | -123.0515 | -123.0469 | 123.2346 | 123.0835 | 59.5871 | 59.5047
140.9531 | 123.1979 | -59.5413 | 63.4003 | 0.068255 | -0.0039977 | 0.061512 | 0.067259 | -0.013156 | 0.0054353 | 0.0066942 | 0.075638 | -0.0029296 | 0.05511 | 0.072273 | -0.0020938 | -0.0018398 | -0.013653 | 0.009155 | 63.2492 | -59.6008 | 63.5788 | -59.6146 | -59.8068 | -59.9258 | 0.018311 | 63.2858 | -59.5734 | 63.5284 | -59.5596 | -59.7198 | -59.6832 | -0.059509 | -0.15106 | 0.17853 | -0.073242 | -0.38452 | -0.2655 | -0.32501 | -0.20599 | -0.032043 | -0.11444 | 0.12817 | -0.01831 | -0.14191 | -0.17853 | -0.10986 | -0.14649 | -0.013733 | 123.1796 | 0.013733 | 123.1018 | 122.85 | 122.8592 | 122.7905 | 122.8271 | -123.0011 | -122.9736 | 123.1201 | 123.0698 | 59.5505 | 59.5596
142.0312 | 123.2162 | -59.5139 | 63.4506 | 0.022479 | -0.0093377 | 0.060444 | 0.07794 | -0.013156 | -0.02554 | 0.0024222 | 0.16719 | 0.0002754 | 0.049769 | 0.058387 | 0.0075192 | 0.029135 | -0.014721 | 0.11902 | 63.3041 | -59.5596 | 63.5605 | -59.5367 | -59.8251 | -59.8526 | 0.059509 | 63.3179 | -59.5413 | 63.5788 | -59.5047 | -59.6741 | -59.6191 | -0.045776 | -0.14648 | 0.10986 | -0.022888 | -0.33875 | -0.31128 | -0.29297 | -0.2655 | -0.027466 | -0.13275 | 0.12817 | 0.009155 | -0.10529 | -0.16022 | -0.07782 | -0.13275 | 0.022888 | 123.1201 | 0.036621 | 123.1201 | 122.8638 | 122.8592 | 122.818 | 122.8317 | -123.0103 | -122.9919 | 123.0743 | 123.0927 | 59.6329 | 59.5734
142.9531 | 123.2437 | -59.5413 | 63.3728 | -0.0080386 | 0.0056153 | 0.056172 | 0.069395 | 0.024228 | -0.00097271 | -0.0093278 | 0.014603 | 0.010956 | 0.054042 | 0.071205 | -0.0042298 | 0.0067052 | -0.014721 | -0.036621 | 63.2812 | -59.6146 | 63.6841 | -59.5459 | -59.7885 | -59.8297 | -0.027466 | 63.327 | -59.5779 | 63.6154 | -59.5963 | -59.7473 | -59.7061 | -0.073242 | -0.091553 | 0.31128 | -0.004577 | -0.28839 | -0.24719 | -0.21515 | -0.17395 | -0.036621 | -0.045777 | 0.24261 | -0.054931 | -0.16479 | -0.20599 | -0.12817 | -0.16937 | 0.068665 | 123.2986 | -0.01831 | 123.1934 | 122.8958 | 122.905 | 122.8226 | 122.8683 | -122.9874 | -122.9507 | 123.2254 | 123.1567 | 59.5047 | 59.5139
144.0312 | 123.262 | -59.5047 | 63.4094 | 0.083514 | 0.0024113 | 0.055104 | 0.064055 | -0.0088836 | 0.018253 | -0.00078276 | 0.38081 | 0.0045474 | 0.033747 | 0.066932 | -0.0010258 | 0.0013642 | 0.017322 | 0.050354 | 63.2629 | -59.5596 | 63.5147 | -59.5917 | -59.8343 | -59.9075 | 0.12817 | 63.3591 | -59.5322 | 63.5376 | -59.4589 | -59.5825 | -59.5734 | -0.054931 | -0.14648 | 0.10529 | -0.086975 | -0.40283 | -0.32959 | -0.3479 | -0.27466 | -0.027466 | -0.050354 | 0.12817 | 0.045777 | -0.068664 | -0.07782 | -0.041198 | -0.050354 | -0.032044 | 123.0743 | 0.073243 | 123.0698 | 122.8226 | 122.8912 | 122.7676 | 122.8638 | -122.9691 | -122.9416 | 123.0194 | 123.0423 | 59.5551 | 59.6329
144.9531 | 123.2346 | -59.5322 | 63.382 | 0.11403 | 0.0034793 | 0.066853 | 0.0726 | 0.016751 | -0.0073817 | -0.0039868 | -0.061691 | 0.0088204 | 0.06045 | 0.055183 | -0.014912 | 0.016318 | -0.0019036 | 0.009155 | 63.2355 | -59.61 | 63.5284 | -59.5963 | -59.8984 | -59.8618 | 0.07782 | 63.2812 | -59.5871 | 63.6292 | -59.5642 | -59.6786 | -59.6512 | -0.077819 | -0.14648 | 0.14648 | -0.064086 | -0.32959 | -0.36621 | -0.25177 | -0.28839 | -0.054931 | -0.10071 | 0.24719 | -0.032043 | -0.11902 | -0.14648 | -0.064087 | -0.091553 | 0.013733 | 123.1384 | 0.022888 | 123.2162 | 122.8455 | 122.8683 | 122.7676 | 122.8134 | -122.9919 | -122.9691 | 123.0606 | 123.1613 | 59.5413 | 59.61
145.9531 | 123.1796 | -59.5551 | 63.3362 | 0.083514 | 0.0034793 | 0.064717 | 0.073668 | 0.0092744 | -0.014859 | 0.0056262 | -0.046432 | 0.0066834 | 0.066859 | 0.059455 | -0.018116 | 0.0077732 | -0.010449 | -0.045776 | 63.2446 | -59.6191 | 63.5651 | -59.5367 | -59.8526 | -59.8434 | -0.018311 | 63.2904 | -59.5825 | 63.6063 | -59.5734 | -59.6741 | -59.6466 | -0.064087 | -0.091553 | 0.22888 | 0.018311 | -0.28839 | -0.29755 | -0.2243 | -0.23346 | -0.027466 | -0.045777 | 0.27008 | -0.01831 | -0.091552 | -0.11902 | -0.064086 | -0.091552 | 0.082398 | 123.1842 | 0.009156 | 123.1888 | 122.8638 | 122.8729 | 122.7997 | 122.8455 | -122.9553 | -122.9187 | 123.1201 | 123.1613 | 59.5093 | 59.5367
147.0312 | 123.2117 | -59.523 | 63.4094 | 0.068255 | -0.00079271 | 0.051899 | 0.064055 | -0.0024746 | 0.0054353 | 0.019511 | 0.12141 | 0.017364 | 0.065791 | 0.065864 | -0.0010258 | 0.0024322 | 0.0045054 | -0.013733 | 63.2996 | -59.5825 | 63.5147 | -59.5276 | -59.8801 | -59.8068 | 0.036621 | 63.3133 | -59.5688 | 63.6383 | -59.5322 | -59.6191 | -59.6283 | -0.05951 | -0.10986 | 0.10529 | -0.004578 | -0.28381 | -0.35706 | -0.2243 | -0.29755 | -0.045777 | -0.096131 | 0.22888 | -0.009156 | -0.10529 | -0.096131 | -0.059509 | -0.050354 | 0.054932 | 123.0972 | 0.036621 | 123.2071 | 122.8821 | 122.8821 | 122.8226 | 122.8363 | -122.9919 | -122.9782 | 123.0377 | 123.1613 | 59.5093 | 59.5596
147.9531 | 123.1796 | -59.5505 | 63.3911 | 0.098773 | -0.0082697 | 0.059376 | 0.068327 | -0.0035426 | 0.020389 | 0.0088302 | -0.015915 | -0.0029296 | 0.063655 | 0.035957 | -0.0052988 | 0.0035002 | -0.010449 | -0.018311 | 63.2675 | -59.6237 | 63.588 | -59.4864 | -59.7885 | -59.8251 | -0.10529 | 63.3087 | -59.5917 | 63.5422 | -59.5734 | -59.7519 | -59.6695 | -0.073242 | -0.1236 | 0.19684 | 0.064087 | -0.27466 | -0.23804 | -0.20142 | -0.1648 | -0.041199 | -0.082397 | 0.15106 | -0.022888 | -0.11902 | -0.20142 | -0.07782 | -0.16022 | 0.13733 | 123.2117 | 0.018311 | 123.1338 | 122.8912 | 122.9004 | 122.818 | 122.8592 | -123.0148 | -122.9828 | 123.1384 | 123.0927 | 59.5322 | 59.4452
149.0469 | 123.1064 | -59.5551 | 63.4048 | -0.0080386 | 0.0045473 | 0.063649 | 0.070463 | -0.00033857 | 0.011844 | -0.011464 | -0.19902 | 0.0077514 | 0.04336 | 0.068 | 0.0043152 | 0.0056372 | 0.00023236 | -0.07782 | 63.2675 | -59.6558 | 63.6887 | -59.4223 | -59.7931 | -59.729 | -0.19226 | 63.3499 | -59.6054 | 63.4918 | -59.6878 | -59.8297 | -59.7336 | -0.10071 | -0.13733 | 0.28381 | 0.13275 | -0.17395 | -0.23804 | -0.073242 | -0.13733 | -0.050354 | -0.054931 | 0.086975 | -0.13275 | -0.17853 | -0.27466 | -0.12817 | -0.2243 | 0.23346 | 123.3444 | -0.082397 | 123.0972 | 122.9233 | 122.9553 | 122.8226 | 122.905 | -123.0606 | -123.0103 | 123.2437 | 123.0469 | 59.4772 | 59.3628
149.9531 | 123.175 | -59.5779 | 63.3957 | 0.14455 | 0.0024113 | 0.056172 | 0.065123 | -0.0035426 | 0.0022313 | 0.0045582 | -0.00065608 | 0.0088204 | 0.054042 | 0.070137 | -0.0031618 | 0.0056372 | 0.0087774 | -0.050354 | 63.2721 | -59.6466 | 63.652 | -59.4772 | -59.7244 | -59.8434 | -0.11902 | 63.3224 | -59.5779 | 63.5513 | -59.5871 | -59.8068 | -59.7198 | -0.068664 | -0.1236 | 0.25635 | 0.10071 | -0.2655 | -0.14648 | -0.19684 | -0.07782 | 0 | -0.073242 | 0.15564 | -0.009155 | -0.14191 | -0.22888 | -0.14191 | -0.22888 | 0.16937 | 123.2986 | -0.009155 | 123.1293 | 122.9187 | 122.9004 | 122.85 | 122.9004 | -123.0423 | -122.9736 | 123.23 | 123.1293 | 59.5276 | 59.4589
151.0156 | 123.1155 | -59.5551 | 63.4277 | 0.15981 | 0.00027529 | 0.067921 | 0.081144 | -0.00033857 | -0.013791 | 0.0013532 | -0.12273 | 0.012024 | 0.061518 | 0.073341 | -0.010639 | 0.012045 | -0.0051076 | 0.004578 | 63.2996 | -59.6054 | 63.6337 | -59.4406 | -59.7702 | -59.7565 | -0.064087 | 63.3499 | -59.5688 | 63.5468 | -59.6512 | -59.8022 | -59.7107 | -0.050354 | -0.12817 | 0.20599 | 0.11444 | -0.20142 | -0.21515 | -0.15106 | -0.1648 | -0.013733 | -0.077819 | 0.11902 | -0.09613 | -0.15564 | -0.24719 | -0.14191 | -0.23346 | 0.16479 | 123.2391 | -0.082397 | 123.1155 | 122.905 | 122.9187 | 122.8546 | 122.905 | -123.0331 | -122.9965 | 123.1888 | 123.1018 | 59.5596 | 59.491
151.9531 | 123.2391 | -59.523 | 63.4003 | -0.0080386 | 0.0024113 | 0.067921 | 0.064055 | 0.0071384 | 0.010776 | 0.0098982 | 0.12141 | -0.0061336 | 0.062587 | 0.055183 | -0.0074348 | 0.0056372 | -0.0061756 | 0.009155 | 63.2172 | -59.5963 | 63.533 | -59.5963 | -59.8938 | -59.9213 | -0.009155 | 63.2767 | -59.5642 | 63.6246 | -59.523 | -59.6786 | -59.6283 | -0.073242 | -0.18311 | 0.13275 | -0.073242 | -0.39825 | -0.37079 | -0.32501 | -0.29755 | -0.041199 | -0.1236 | 0.2243 | 0 | -0.10529 | -0.15564 | -0.064087 | -0.11444 | 0 | 123.1293 | 0.041199 | 123.1888 | 122.8134 | 122.8409 | 122.7402 | 122.7997 | -122.9965 | -122.9645 | 123.056 | 123.1476 | 59.5322 | 59.5139
153.0312 | 123.2117 | -59.5047 | 63.4644 | -0.0080386 | -0.0082697 | 0.059376 | 0.070463 | 0.0050024 | -0.0073817 | 0.015239 | 0.21297 | -0.0029296 | 0.080744 | 0.029548 | 0.0053832 | 0.013113 | 0.0045054 | 0.10986 | 63.3041 | -59.5596 | 63.5376 | -59.5596 | -59.8434 | -59.848 | 0.059509 | 63.327 | -59.523 | 63.5788 | -59.491 | -59.6603 | -59.6146 | -0.054931 | -0.16022 | 0.073243 | -0.054931 | -0.34332 | -0.33875 | -0.28839 | -0.28381 | -0.01831 | -0.13733 | 0.11444 | 0.013733 | -0.10986 | -0.15564 | -0.091553 | -0.13733 | 0 | 123.0972 | 0.032043 | 123.1018 | 122.8638 | 122.85 | 122.8088 | 122.8317 | -123.024 | -122.9874 | 123.0423 | 123.0835 | 59.6146 | 59.5642
153.9688 | 123.1842 | -59.5093 | 63.4232 | -0.0080386 | 0.0034793 | 0.063649 | 0.0726 | 0.00072943 | 0.010776 | -0.0029188 | 0.13667 | 0.0034794 | 0.083949 | 0.082954 | 0.012859 | 0.0024322 | -0.0040396 | 0.073242 | 63.2767 | -59.5505 | 63.6017 | -59.5322 | -59.7977 | -59.8434 | 0.07782 | 63.3453 | -59.5596 | 63.5696 | -59.5642 | -59.6786 | -59.6786 | -0.041199 | -0.14649 | 0.17853 | -0.022889 | -0.33417 | -0.28839 | -0.29297 | -0.24719 | -0.050354 | -0.07782 | 0.14648 | -0.054932 | -0.16937 | -0.16937 | -0.11902 | -0.11902 | 0.01831 | 123.1522 | -0.004578 | 123.1293 | 122.8271 | 122.905 | 122.7859 | 122.8546 | -122.9736 | -122.9828 | 123.111 | 123.0789 | 59.5825 | 59.5871
155.0312 | 123.111 | -59.5413 | 63.4735 | 0.11403 | 0.0024113 | 0.055104 | 0.067259 | 0.0060704 | -0.0031087 | -0.0039868 | 0.39607 | 0.020569 | 0.067927 | 0.063728 | -0.0052988 | 0.0035002 | -0.02113 | 0.032043 | 63.3179 | -59.5871 | 63.707 | -59.4086 | -59.6603 | -59.7885 | -0.14191 | 63.3911 | -59.5688 | 63.4964 | -59.5825 | -59.7931 | -59.7244 | -0.045776 | -0.15564 | 0.23346 | 0.13275 | -0.24719 | -0.11902 | -0.20142 | -0.073242 | -0.027466 | -0.082398 | 0.022888 | -0.041199 | -0.1831 | -0.25177 | -0.15564 | -0.2243 | 0.17853 | 123.2941 | -0.013733 | 123.0652 | 122.905 | 122.9599 | 122.8592 | 122.9324 | -123.0606 | -123.0423 | 123.2483 | 123.0377 | 59.5734 | 59.3994
155.9531 | 123.262 | -59.5276 | 63.3957 | 0.0072204 | -0.0029297 | 0.063649 | 0.07794 | -0.020633 | -0.0031087 | -0.00078276 | 0.04512 | 0.0002754 | 0.068995 | 0.032752 | -0.0074348 | 0.0024322 | 0.0045054 | -0.018311 | 63.2355 | -59.6329 | 63.5513 | -59.5825 | -59.8663 | -59.8892 | 0.13733 | 63.295 | -59.6008 | 63.5971 | -59.5734 | -59.7015 | -59.6924 | -0.10529 | -0.16022 | 0.15564 | -0.054932 | -0.36163 | -0.33874 | -0.25635 | -0.23346 | -0.073242 | -0.10071 | 0.20142 | -0.045776 | -0.16479 | -0.17395 | -0.091553 | -0.10071 | 0.050354 | 123.1842 | 0.027466 | 123.1979 | 122.8683 | 122.8958 | 122.7631 | 122.8226 | -123.0286 | -122.9965 | 123.0789 | 123.1247 | 59.5093 | 59.6649
156.9531 | 123.1705 | -59.5734 | 63.4186 | 0.052997 | -0.011475 | 0.059376 | 0.0726 | -0.0056786 | 0.010776 | -0.0093278 | 0.075638 | 0.0045474 | 0.065791 | 0.081886 | -0.0020938 | 0.010977 | 0.0055734 | -0.073242 | 63.2675 | -59.6283 | 63.6154 | -59.4635 | -59.7702 | -59.7977 | -0.10529 | 63.3133 | -59.6054 | 63.5468 | -59.61 | -59.8206 | -59.6558 | -0.054932 | -0.15106 | 0.19684 | 0.10986 | -0.2243 | -0.19684 | -0.16937 | -0.14191 | -0.032044 | -0.10529 | 0.12817 | -0.036621 | -0.082398 | -0.24719 | -0.050354 | -0.21515 | 0.16479 | 123.2437 | -0.004577 | 123.1522 | 122.8958 | 122.9187 | 122.8409 | 122.8867 | -123.0469 | -123.024 | 123.1888 | 123.1201 | 59.5001 | 59.4681
157.9531 | 123.1201 | -59.5505 | 63.3911 | 0.0072204 | 0.0088203 | 0.052968 | 0.065123 | 0.0039344 | 0.0097083 | 0.0045582 | 0.18245 | 0.0045474 | 0.067927 | 0.060523 | -0.0042298 | 0.0056372 | 0.014118 | -0.10986 | 63.2584 | -59.6649 | 63.6475 | -59.4315 | -59.7656 | -59.7794 | -0.064087 | 63.3591 | -59.5917 | 63.5605 | -59.6695 | -59.7748 | -59.7519 | -0.11444 | -0.13275 | 0.25635 | 0.11902 | -0.22888 | -0.21515 | -0.11444 | -0.10071 | -0.041199 | -0.032043 | 0.16937 | -0.11902 | -0.20142 | -0.2243 | -0.16022 | -0.1831 | 0.23346 | 123.3124 | -0.07782 | 123.1522 | 122.9233 | 122.9507 | 122.8088 | 122.9095 | -123.056 | -122.9828 | 123.1979 | 123.111 | 59.4406 | 59.4864
159.0312 | 123.1659 | -59.5276 | 63.446 | 0.11403 | 0.0045473 | 0.064717 | 0.076872 | -0.0088836 | -0.011654 | 0.0066942 | 0.075638 | 0.0034794 | 0.046565 | 0.069068 | -0.0074348 | 0.012045 | -0.0029716 | 0.036621 | 63.3087 | -59.61 | 63.7436 | -59.4315 | -59.6878 | -59.7198 | -0.032043 | 63.382 | -59.5734 | 63.5559 | -59.6191 | -59.7336 | -59.7198 | -0.082397 | -0.13733 | 0.29755 | 0.09613 | -0.19226 | -0.16022 | -0.10986 | -0.07782 | -0.045776 | -0.064087 | 0.10986 | -0.091553 | -0.19226 | -0.20599 | -0.14649 | -0.16022 | 0.17853 | 123.3536 | -0.045777 | 123.1293 | 122.9187 | 122.9553 | 122.8363 | 122.9095 | -123.056 | -123.0194 | 123.2712 | 123.0835 | 59.5642 | 59.4955
159.9531 | 123.2025 | -59.5322 | 63.3865 | 0.022479 | 0.015228 | 0.066853 | 0.054442 | 0.0071384 | 9.5287e-05 | 0.00028524 | 0.13667 | -0.0018616 | 0.068995 | 0.076545 | -0.013843 | 0.012045 | -0.02113 | -0.041199 | 63.2446 | -59.5825 | 63.5284 | -59.5917 | -59.8938 | -59.8572 | 0.032043 | 63.2721 | -59.5825 | 63.6017 | -59.6054 | -59.6512 | -59.7061 | -0.050354 | -0.14191 | 0.14191 | -0.059509 | -0.32501 | -0.36163 | -0.27466 | -0.31128 | -0.050354 | -0.11444 | 0.21515 | -0.073242 | -0.17395 | -0.11902 | -0.1236 | -0.068664 | -0.009155 | 123.111 | -0.022888 | 123.1842 | 122.8271 | 122.8546 | 122.7768 | 122.8043 | -122.9691 | -122.9691 | 123.0606 | 123.1339 | 59.491 | 59.5642
161.0312 | 123.1155 | -59.5367 | 63.4323 | 0.12929 | 0.0077523 | 0.059376 | 0.067259 | -0.0035426 | 0.0011633 | 0.014171 | 0.014603 | 0.0024114 | 0.074336 | 0.082954 | -0.0020938 | 0.010977 | 0.0023694 | 0.07782 | 63.3041 | -59.5642 | 63.6383 | -59.4864 | -59.7565 | -59.7839 | 0.041199 | 63.3911 | -59.5551 | 63.5422 | -59.642 | -59.7015 | -59.7702 | -0.027466 | -0.12817 | 0.20599 | 0.050354 | -0.24719 | -0.21973 | -0.21973 | -0.19226 | -0.018311 | -0.041199 | 0.10986 | -0.10529 | -0.23346 | -0.16479 | -0.21515 | -0.14648 | 0.07782 | 123.2025 | -0.086975 | 123.0972 | 122.8683 | 122.9462 | 122.8409 | 122.9279 | -122.9965 | -122.9874 | 123.175 | 123.0789 | 59.6146 | 59.5779
161.9531 | 123.2208 | -59.5322 | 63.4048 | -0.023297 | 0.0013433 | 0.066853 | 0.068327 | -0.014224 | 0.0032993 | 0.010966 | 0.04512 | -0.0029296 | 0.066859 | 0.04557 | -0.010639 | 0.0067052 | -0.011517 | -0.032043 | 63.2355 | -59.6054 | 63.5284 | -59.436 | -59.8206 | -59.8434 | 0.004578 | 63.2858 | -59.5779 | 63.6292 | -59.5596 | -59.6512 | -59.6512 | -0.073242 | -0.16937 | 0.1236 | 0.096131 | -0.31128 | -0.28839 | -0.23804 | -0.21515 | -0.045776 | -0.11902 | 0.2243 | -0.027465 | -0.11902 | -0.11902 | -0.073242 | -0.073242 | 0.16937 | 123.1338 | 0.018311 | 123.2071 | 122.8409 | 122.8638 | 122.7676 | 122.818 | -123.0103 | -122.9828 | 123.0606 | 123.1613 | 59.5001 | 59.5367
163.0312 | 123.2162 | -59.5001 | 63.4323 | -0.13011 | -0.00079271 | 0.070057 | 0.066191 | 0.0060704 | -0.0073817 | 0.0024222 | 0.28926 | -0.0050656 | 0.0722 | 0.046638 | 0.0021782 | 0.0099092 | -0.0072446 | 0.045776 | 63.2812 | -59.5734 | 63.5468 | -59.5596 | -59.8526 | -59.8297 | 0.1236 | 63.3316 | -59.5551 | 63.6566 | -59.5322 | -59.61 | -59.6375 | -0.073242 | -0.15106 | 0.11444 | -0.059509 | -0.32959 | -0.35248 | -0.25635 | -0.27924 | -0.054932 | -0.10071 | 0.2243 | -0.032044 | -0.13733 | -0.10986 | -0.082397 | -0.054931 | 0.013733 | 123.1201 | 0.022888 | 123.2117 | 122.8546 | 122.8867 | 122.7814 | 122.8317 | -123.0057 | -122.9874 | 123.0469 | 123.1567 | 59.5459 | 59.6237
163.9688 | 123.2803 | -59.5093 | 63.4277 | -0.023297 | 0.0098883 | 0.051899 | 0.058714 | 0.0050024 | -0.0052457 | 0.0034902 | 0.28926 | -0.0018616 | 0.095698 | 0.066932 | -0.0085028 | -0.0018398 | -0.013653 | 0.013733 | 63.2858 | -59.5917 | 63.5605 | -59.5413 | -59.8984 | -59.8206 | 0.09613 | 63.3133 | -59.5413 | 63.6566 | -59.5367 | -59.6237 | -59.5871 | -0.082398 | -0.14191 | 0.13275 | -0.032044 | -0.31128 | -0.3891 | -0.22888 | -0.3067 | -0.032044 | -0.11444 | 0.22888 | -0.027466 | -0.07782 | -0.11444 | -0.045776 | -0.082397 | 0.050354 | 123.1522 | 0.004578 | 123.1979 | 122.8775 | 122.8546 | 122.7951 | 122.8226 | -123.0194 | -122.9691 | 123.0698 | 123.1659 | 59.523 | 59.6054
165.0312 | 123.2117 | -59.5459 | 63.4094 | 0.068255 | -0.00079271 | 0.062581 | 0.071531 | -0.0067466 | -0.011654 | 0.0034902 | 0.21297 | 0.0002754 | 0.075404 | 0.039161 | -0.0042298 | 0.0045682 | -0.013653 | -0.022888 | 63.2629 | -59.5871 | 63.5925 | -59.5184 | -59.8572 | -59.8389 | 0.07782 | 63.3179 | -59.5779 | 63.6703 | -59.6054 | -59.6558 | -59.6649 | -0.041199 | -0.14648 | 0.1831 | 0.027465 | -0.29297 | -0.31128 | -0.25177 | -0.27008 | -0.032044 | -0.091553 | 0.26093 | -0.05951 | -0.11902 | -0.10986 | -0.086975 | -0.07782 | 0.068664 | 123.1796 | -0.027466 | 123.2483 | 122.85 | 122.8958 | 122.8088 | 122.8638 | -122.9965 | -122.9874 | 123.1384 | 123.2162 | 59.523 | 59.6237
165.9688 | 123.2574 | -59.5047 | 63.4369 | -0.0080386 | 0.0088203 | 0.055104 | 0.083281 | -0.012088 | 9.5287e-05 | -0.0050548 | -0.00065608 | 0.0088204 | 0.068995 | 0.08509 | 4.2208e-05 | 0.0045682 | -0.0029716 | 0.07782 | 63.2629 | -59.5505 | 63.3865 | -59.7015 | -59.8801 | -59.8572 | 0.07782 | 63.295 | -59.5322 | 63.6337 | -59.5001 | -59.6329 | -59.5963 | -0.045776 | -0.17395 | -0.050354 | -0.19684 | -0.35248 | -0.37537 | -0.3067 | -0.32959 | -0.027466 | -0.14191 | 0.19684 | 0.004578 | -0.091552 | -0.12817 | -0.064086 | -0.10071 | -0.15106 | 122.937 | 0.032044 | 123.1659 | 122.8134 | 122.8271 | 122.7676 | 122.7997 | -122.9874 | -122.9691 | 122.8912 | 123.1384 | 59.5825 | 59.5825
166.9531 | 123.175 | -59.5367 | 63.4323 | 0.083514 | 0.0024113 | 0.073262 | 0.082213 | -0.0035426 | -0.020199 | 0.0066942 | -0.13799 | 0.0034794 | 0.056178 | 0.038093 | -0.011707 | 0.0035002 | 0.011982 | -0.064087 | 63.2401 | -59.6558 | 63.6703 | -59.4772 | -59.7382 | -59.8068 | -0.054932 | 63.3316 | -59.5825 | 63.5239 | -59.6603 | -59.7198 | -59.761 | -0.11902 | -0.19226 | 0.23804 | 0.059509 | -0.27008 | -0.20142 | -0.15106 | -0.082397 | -0.045777 | -0.10071 | 0.091553 | -0.1236 | -0.2243 | -0.18311 | -0.17853 | -0.13733 | 0.17853 | 123.3261 | -0.077819 | 123.1064 | 122.8958 | 122.9141 | 122.7768 | 122.8683 | -123.0881 | -123.0148 | 123.2071 | 123.0606 | 59.4727 | 59.4818
167.9531 | 123.2574 | -59.5322 | 63.382 | 0.022479 | 0.013092 | 0.062581 | 0.06085 | 0.012479 | 0.0022313 | 0.010966 | 0.10615 | 0.0034794 | 0.059382 | 0.043434 | -0.0042298 | 0.010977 | 0.0013004 | -0.013733 | 63.2263 | -59.6237 | 63.5147 | -59.5688 | -59.8801 | -59.8892 | 0.009155 | 63.2812 | -59.5505 | 63.6246 | -59.5505 | -59.7244 | -59.5963 | -0.091552 | -0.15564 | 0.13275 | -0.036621 | -0.35706 | -0.3479 | -0.2655 | -0.25635 | -0.01831 | -0.10071 | 0.24262 | -0.01831 | -0.064086 | -0.19226 | -0.045776 | -0.17395 | 0.054931 | 123.1384 | 0 | 123.175 | 122.85 | 122.8317 | 122.7585 | 122.8134 | -123.0057 | -122.9324 | 123.0469 | 123.1567 | 59.5184 | 59.5413
168.9688 | 123.2162 | -59.5093 | 63.4598 | -0.023297 | 0.0045473 | 0.052968 | 0.070463 | 0.0050024 | 0.01398 | -0.0071918 | 0.19771 | -0.0029296 | 0.06045 | 0.034889 | -0.0052988 | 0.0035002 | -0.012585 | 0.07782 | 63.2538 | -59.5642 | 63.5651 | -59.5413 | -59.8526 | -59.8068 | 0.12817 | 63.3362 | -59.523 | 63.652 | -59.5825 | -59.6008 | -59.6558 | -0.054932 | -0.20599 | 0.10529 | -0.032044 | -0.29755 | -0.34332 | -0.24262 | -0.28839 | -0.013733 | -0.1236 | 0.19226 | -0.073243 | -0.14649 | -0.091553 | -0.13275 | -0.07782 | 0.022888 | 123.1293 | -0.05951 | 123.175 | 122.818 | 122.8592 | 122.7631 | 122.8455 | -123.024 | -122.9828 | 123.0743 | 123.1613 | 59.5871 | 59.6375
169.9531 | 123.2391 | -59.5734 | 63.3728 | 0.098773 | 0.0024113 | 0.051899 | 0.069395 | -0.0035426 | 0.0086403 | 0.0045582 | -0.07695 | 0.0045474 | 0.052973 | 0.074409 | 0.0053832 | 0.0002962 | -0.0019036 | -0.004578 | 63.2492 | -59.6237 | 63.5376 | -59.5459 | -59.8206 | -59.8755 | -0.050354 | 63.2858 | -59.5871 | 63.5651 | -59.5413 | -59.7153 | -59.8206 | -0.050354 | -0.1236 | 0.1648 | 0.027466 | -0.30212 | -0.24719 | -0.25177 | -0.19684 | -0.013733 | -0.086975 | 0.19226 | 0.032043 | -0.24719 | -0.14191 | -0.23346 | -0.12817 | 0.07782 | 123.1613 | 0.045776 | 123.1522 | 122.8729 | 122.8729 | 122.8226 | 122.8592 | -122.9965 | -122.9599 | 123.111 | 123.1384 | 59.5688 | 59.523
171.0312 | 123.2666 | -59.5047 | 63.4323 | 0.19033 | 0.0024113 | 0.060444 | 0.061918 | -0.0035426 | 0.019321 | -0.0082598 | 0.18245 | 0.0056154 | 0.083949 | 0.078681 | -0.0010258 | -0.0039768 | -0.012585 | 0.009155 | 63.2904 | -59.5779 | 63.5193 | -59.4818 | -59.8984 | -59.8343 | 0.10529 | 63.3087 | -59.5551 | 63.6703 | -59.5184 | -59.6466 | -59.5963 | -0.073242 | -0.14191 | 0.086975 | 0.022888 | -0.32959 | -0.39368 | -0.25635 | -0.32043 | -0.050354 | -0.1236 | 0.23804 | -0.013733 | -0.091552 | -0.14191 | -0.041198 | -0.091552 | 0.09613 | 123.0972 | 0.036621 | 123.2254 | 122.8683 | 122.8638 | 122.7951 | 122.8134 | -123.0103 | -122.9874 | 123.024 | 123.175 | 59.5139 | 59.61
171.9531 | 123.3307 | -59.5322 | 63.3453 | 0.11403 | 0.0056153 | 0.062581 | 0.069395 | 0.0039344 | -0.013791 | -0.0071918 | -0.1685 | 0.0024114 | 0.091426 | 0.081886 | 0.0032462 | 0.0013642 | -0.0061756 | -0.041199 | 63.2812 | -59.6146 | 63.5696 | -59.5551 | -59.7977 | -59.9075 | -0.027466 | 63.2858 | -59.5734 | 63.5742 | -59.5047 | -59.7519 | -59.6237 | -0.082397 | -0.064087 | 0.2243 | -0.022888 | -0.37537 | -0.2655 | -0.29297 | -0.18311 | -0.041198 | -0.059509 | 0.22888 | 0.027466 | -0.091552 | -0.21973 | -0.050354 | -0.17853 | 0.059509 | 123.1842 | 0.068664 | 123.1476 | 122.8958 | 122.8592 | 122.8134 | 122.818 | -122.9599 | -122.9187 | 123.1018 | 123.1064 | 59.491 | 59.5047
172.9531 | 123.23 | -59.5093 | 63.4003 | 0.037738 | 0.0066833 | 0.060444 | 0.0726 | 0.0071384 | -0.022336 | -0.012532 | 0.04512 | 0.0034794 | 0.078608 | 0.064796 | -0.0042298 | 0.0099092 | -0.016858 | 0.13275 | 63.2538 | -59.5688 | 63.5101 | -59.6008 | -59.9396 | -59.8572 | 0.018311 | 63.2629 | -59.5642 | 63.62 | -59.5917 | -59.6603 | -59.6695 | -0.05951 | -0.14648 | 0.10986 | -0.091553 | -0.3479 | -0.4303 | -0.28839 | -0.37079 | -0.054932 | -0.13733 | 0.21973 | -0.082398 | -0.16022 | -0.15106 | -0.10529 | -0.09613 | -0.032043 | 123.0789 | -0.027466 | 123.1842 | 122.8226 | 122.8271 | 122.7631 | 122.7722 | -122.9691 | -122.9645 | 123.0194 | 123.1293 | 59.642 | 59.5276
173.9531 | 123.2666 | -59.5322 | 63.382 | 0.068255 | 0.0098883 | 0.055104 | 0.0726 | -0.0046106 | 0.0054353 | -0.0082598 | -0.00065608 | 0.015228 | 0.068995 | 0.040229 | -0.0010258 | 0.0002962 | 0.0023694 | -0.032043 | 63.2538 | -59.6329 | 63.6154 | -59.5367 | -59.8022 | -59.8755 | -0.027466 | 63.295 | -59.5459 | 63.588 | -59.5596 | -59.7382 | -59.642 | -0.10071 | -0.12817 | 0.23346 | -0.004577 | -0.34332 | -0.27008 | -0.24261 | -0.16937 | -0.013732 | -0.086975 | 0.20599 | -0.027465 | -0.10986 | -0.20599 | -0.096131 | -0.19226 | 0.096131 | 123.2483 | -0.013733 | 123.1338 | 122.8867 | 122.8409 | 122.7859 | 122.8271 | -123.0148 | -122.9279 | 123.1476 | 123.1201 | 59.5001 | 59.5047
174.9531 | 123.2071 | -59.5367 | 63.4277 | 0.022479 | -0.00079271 | 0.058308 | 0.058714 | 0.0028664 | -0.027676 | 0.0024222 | 0.22823 | -0.0018616 | 0.078608 | 0.044502 | 0.0032462 | 0.0002962 | -0.0051076 | -0.041199 | 63.2675 | -59.5963 | 63.5696 | -59.4818 | -59.8709 | -59.7702 | -0.054932 | 63.3041 | -59.5779 | 63.588 | -59.6191 | -59.7107 | -59.6512 | -0.059509 | -0.16022 | 0.14191 | 0.054931 | -0.23346 | -0.33417 | -0.17395 | -0.27466 | -0.041199 | -0.1236 | 0.16022 | -0.082398 | -0.11444 | -0.17395 | -0.073242 | -0.13275 | 0.11444 | 123.1659 | -0.041199 | 123.1659 | 122.8638 | 122.8821 | 122.8043 | 122.8409 | -123.024 | -123.0057 | 123.1064 | 123.1247 | 59.4955 | 59.4818
175.9531 | 123.2529 | -59.5001 | 63.414 | -0.069074 | 0.0024113 | 0.062581 | 0.066191 | 0.0050024 | -0.020199 | 0.00028524 | 0.04512 | 0.012024 | 0.081813 | 0.072273 | -0.0042298 | 0.0099092 | -0.014721 | 0.013733 | 63.2446 | -59.6054 | 63.588 | -59.6466 | -59.8892 | -59.9167 | 0.018311 | 63.2858 | -59.5871 | 63.5925 | -59.5413 | -59.6695 | -59.61 | -0.10529 | -0.16937 | 0.17395 | -0.14648 | -0.41657 | -0.3891 | -0.31128 | -0.28381 | -0.086975 | -0.12817 | 0.17853 | -0.041199 | -0.10986 | -0.16937 | -0.022888 | -0.082398 | -0.041198 | 123.1934 | 0.045776 | 123.1796 | 122.85 | 122.8729 | 122.7448 | 122.7859 | -123.0194 | -123.0011 | 123.0881 | 123.0927 | 59.5139 | 59.5184
176.9531 | 123.2391 | -59.5184 | 63.4003 | -0.0080386 | 0.0066833 | 0.065785 | 0.097166 | 0.0017974 | -0.023404 | -0.015736 | -0.00065608 | 0.0098884 | 0.047633 | 0.054115 | -0.0085028 | 0.0077732 | -0.011517 | -0.041199 | 63.2401 | -59.6191 | 63.533 | -59.3765 | -59.8526 | -59.8938 | -0.004578 | 63.2721 | -59.5551 | 63.6383 | -59.5642 | -59.7107 | -59.6008 | -0.10071 | -0.16022 | 0.13275 | 0.14191 | -0.37537 | -0.33417 | -0.27466 | -0.23346 | -0.036621 | -0.12817 | 0.23804 | -0.045776 | -0.082397 | -0.19226 | -0.045776 | -0.15564 | 0.24262 | 123.1522 | -0.009155 | 123.1934 | 122.8592 | 122.8271 | 122.7585 | 122.7905 | -123.0194 | -122.9553 | 123.0515 | 123.1567 | 59.4772 | 59.5139
177.9531 | 123.2346 | -59.5413 | 63.382 | 0.0072204 | 0.0077523 | 0.066853 | 0.059782 | 0.01141 | -0.00097271 | -0.012532 | -0.015915 | -0.0061336 | 0.078608 | 0.061592 | 0.0011102 | 0.0024322 | -0.012585 | -0.032043 | 63.2355 | -59.5917 | 63.5651 | -59.6466 | -60.0586 | -59.8892 | 0.022888 | 63.3316 | -59.5459 | 63.588 | -59.5734 | -59.6375 | -59.6741 | -0.050354 | -0.14648 | 0.18311 | -0.10528 | -0.3479 | -0.51727 | -0.29755 | -0.46692 | -0.004577 | -0.050354 | 0.20599 | -0.032043 | -0.13275 | -0.09613 | -0.12817 | -0.091553 | -0.054931 | 123.1567 | -0.027466 | 123.1338 | 122.8271 | 122.8775 | 122.7768 | 122.8729 | -122.9736 | -122.9279 | 123.1064 | 123.1293 | 59.5093 | 59.5642
178.9531 | 123.2071 | -59.5505 | 63.4003 | 0.052997 | 0.0045473 | 0.054036 | 0.058714 | -0.0014066 | -0.0073817 | -0.010396 | 0.15193 | 0.0045474 | 0.036952 | 0.071205 | 4.2208e-05 | 0.0056372 | -0.0083126 | -0.013733 | 63.2492 | -59.6008 | 63.5376 | -59.5413 | -59.848 | -59.8709 | -0.045776 | 63.2812 | -59.5596 | 63.588 | -59.5963 | -59.7565 | -59.6878 | -0.050354 | -0.15106 | 0.13733 | 0.009155 | -0.32043 | -0.29755 | -0.27008 | -0.24719 | -0.009155 | -0.11902 | 0.18768 | -0.045776 | -0.13733 | -0.20599 | -0.12817 | -0.19684 | 0.059509 | 123.1384 | -0.036621 | 123.1476 | 122.85 | 122.8409 | 122.7997 | 122.8317 | -123.0011 | -122.9599 | 123.0881 | 123.1384 | 59.5367 | 59.5047
179.9531 | 123.1888 | -59.5139 | 63.4186 | 0.098773 | -0.0072017 | 0.062581 | 0.071531 | 0.01141 | -0.0020407 | 0.0034902 | 0.10615 | 0.0002754 | 0.071131 | 0.091499 | -0.0052988 | 0.0045682 | -0.013653 | -0.054932 | 63.2538 | -59.5963 | 63.6017 | -59.4818 | -59.761 | -59.8663 | 0.022888 | 63.2996 | -59.5688 | 63.5788 | -59.6649 | -59.6878 | -59.729 | -0.082397 | -0.16479 | 0.18311 | 0.032043 | -0.35248 | -0.24719 | -0.27008 | -0.16479 | -0.054932 | -0.11902 | 0.16022 | -0.15106 | -0.21515 | -0.17395 | -0.16022 | -0.11902 | 0.11444 | 123.1979 | -0.09613 | 123.1476 | 122.85 | 122.8683 | 122.7676 | 122.8134 | -123.0148 | -122.9874 | 123.1155 | 123.0927 | 59.4589 | 59.5367
180.9531 | 123.2849 | -59.5139 | 63.3957 | -0.0080386 | 0.010956 | 0.068989 | 0.070463 | -0.00033857 | 0.0022313 | 0.0024222 | -0.13799 | -0.0082696 | 0.064723 | 0.08509 | 0.0021782 | 0.014181 | -0.0072446 | 0.018311 | 63.2538 | -59.6146 | 63.5056 | -59.5871 | -59.8526 | -59.9075 | -0.036621 | 63.2858 | -59.5871 | 63.5696 | -59.3582 | -59.61 | -59.6329 | -0.10071 | -0.14191 | 0.10986 | -0.073242 | -0.39368 | -0.33875 | -0.29297 | -0.23804 | -0.073242 | -0.10986 | 0.17395 | 0.15564 | -0.11902 | -0.09613 | -0.045777 | -0.022888 | 0.027466 | 123.1201 | 0.22888 | 123.1567 | 122.8683 | 122.8729 | 122.7676 | 122.7997 | -123.0103 | -122.9828 | 123.0194 | 123.0835 | 59.5322 | 59.4772
181.9531 | 123.2254 | -59.523 | 63.4048 | 0.052997 | 0.0034793 | 0.07433 | 0.074736 | 0.0039344 | 0.0075723 | -0.015736 | -0.031174 | -0.0050656 | 0.06045 | 0.033821 | -0.0095708 | 0.012045 | -0.0083126 | -0.041199 | 63.2263 | -59.6054 | 63.533 | -59.5688 | -59.903 | -59.8618 | 0.054932 | 63.295 | -59.5734 | 63.6795 | -59.5963 | -59.6558 | -59.6786 | -0.082398 | -0.17853 | 0.12817 | -0.045777 | -0.33875 | -0.37994 | -0.25635 | -0.29755 | -0.050354 | -0.10986 | 0.27466 | -0.073242 | -0.15564 | -0.13275 | -0.10529 | -0.082398 | 0.036621 | 123.1384 | -0.022888 | 123.2529 | 122.8317 | 122.8683 | 122.7493 | 122.818 | -123.0103 | -122.9782 | 123.056 | 123.2025 | 59.4818 | 59.5779
182.9531 | 123.1842 | -59.5551 | 63.4003 | 0.037738 | 0.0066833 | 0.059376 | 0.070463 | -0.0067466 | -0.014859 | -0.0029188 | 0.10615 | 0.0013434 | 0.068995 | 0.082954 | -0.014912 | 0.0045682 | -0.016858 | -0.004578 | 63.2355 | -59.5917 | 63.5422 | -59.5779 | -59.8068 | -59.9304 | -0.004578 | 63.2904 | -59.5642 | 63.5834 | -59.523 | -59.7336 | -59.6558 | -0.036621 | -0.16479 | 0.14191 | -0.022888 | -0.37537 | -0.25177 | -0.33874 | -0.21515 | -0.009155 | -0.10986 | 0.1831 | 0.032044 | -0.10071 | -0.17853 | -0.091553 | -0.16937 | 0.013733 | 123.1338 | 0.041199 | 123.1476 | 122.8271 | 122.8546 | 122.7905 | 122.8455 | -122.9919 | -122.9645 | 123.0972 | 123.1384 | 59.5505 | 59.5505
183.9531 | 123.2117 | -59.5367 | 63.3728 | -0.023297 | -0.0018617 | 0.063649 | 0.07794 | -0.01102 | -0.0073817 | -0.0136 | 0.029861 | -0.0039976 | 0.063655 | 0.051979 | -0.010639 | 0.0024322 | -0.028607 | -0.004578 | 63.2401 | -59.5871 | 63.4827 | -59.5779 | -59.9167 | -59.8297 | 0.036621 | 63.3133 | -59.5734 | 63.6475 | -59.5825 | -59.6558 | -59.6649 | -0.050354 | -0.13275 | 0.10986 | -0.041199 | -0.29297 | -0.37994 | -0.24262 | -0.32959 | -0.036621 | -0.05951 | 0.27466 | -0.045777 | -0.12817 | -0.11902 | -0.091553 | -0.082398 | 0.009155 | 123.0698 | -0.009156 | 123.2208 | 122.8271 | 122.8867 | 122.7768 | 122.85 | -122.9599 | -122.9462 | 123.0194 | 123.1842 | 59.5322 | 59.5734
184.9531 | 123.2162 | -59.5276 | 63.3911 | -0.084332 | -0.00079271 | 0.058308 | 0.0726 | -0.0014066 | 0.0054353 | 0.0056262 | 0.10615 | -0.0050656 | 0.075404 | 0.046638 | -0.0042298 | 0.010977 | -0.00083564 | 0.004578 | 63.2629 | -59.6146 | 63.5422 | -59.5825 | -59.8572 | -59.903 | 0.013733 | 63.3041 | -59.5596 | 63.5834 | -59.5688 | -59.6924 | -59.6695 | -0.086975 | -0.12817 | 0.15106 | -0.054932 | -0.37537 | -0.32959 | -0.28839 | -0.24262 | -0.032043 | -0.086975 | 0.19226 | -0.041199 | -0.14191 | -0.16479 | -0.10986 | -0.13275 | 0.032043 | 123.1567 | -0.009156 | 123.143 | 122.8775 | 122.8638 | 122.7905 | 122.8317 | -123.0057 | -122.9507 | 123.0698 | 123.111 | 59.5322 | 59.5413
185.9531 | 123.2529 | -59.5139 | 63.3865 | -0.45054 | 0.0088203 | 0.061512 | 0.074736 | -0.0056786 | -0.00097271 | -0.0029188 | -0.00065608 | -0.0029296 | 0.087153 | 0.077613 | -0.010639 | -0.0029078 | -0.020062 | -0.059509 | 63.1851 | -59.6146 | 63.4598 | -59.5551 | -59.9121 | -59.8938 | 0.004578 | 63.2858 | -59.6008 | 63.6566 | -59.5688 | -59.6832 | -59.6649 | -0.10071 | -0.20142 | 0.073242 | -0.041199 | -0.37994 | -0.39825 | -0.27924 | -0.29755 | -0.086975 | -0.10071 | 0.27008 | -0.054932 | -0.15106 | -0.16937 | -0.064087 | -0.082398 | 0.059509 | 123.0743 | 0.032043 | 123.2574 | 122.7997 | 122.8867 | 122.699 | 122.7997 | -123.0011 | -122.9874 | 122.9736 | 123.1705 | 59.4543 | 59.5184
186.9531 | 123.2254 | -59.5367 | 63.3682 | 0.083514 | 0.0077523 | 0.064717 | 0.071531 | -0.015292 | -0.0031087 | -0.00078276 | 0.12141 | 0.0034794 | 0.056178 | 0.051979 | -0.0052988 | 0.012045 | -0.0093806 | 0.004578 | 63.2446 | -59.6008 | 63.5742 | -59.6329 | -59.8389 | -59.8801 | 0.036621 | 63.2904 | -59.5825 | 63.5742 | -59.5963 | -59.6924 | -59.6786 | -0.064087 | -0.1236 | 0.20599 | -0.096131 | -0.34332 | -0.30212 | -0.27924 | -0.23804 | -0.045777 | -0.07782 | 0.20599 | -0.059509 | -0.14191 | -0.15564 | -0.09613 | -0.10986 | -0.032044 | 123.175 | -0.013732 | 123.1567 | 122.8455 | 122.8729 | 122.7814 | 122.8271 | -122.9691 | -122.9507 | 123.111 | 123.111 | 59.5413 | 59.5734
187.9531 | 123.2346 | -59.5184 | 63.382 | -0.099591 | 0.0098883 | 0.063649 | 0.087553 | -0.00033857 | 0.0054353 | -0.011464 | -0.07695 | 0.0002754 | 0.065791 | 0.040229 | -0.010639 | 0.0045682 | -0.0051076 | -0.018311 | 63.2355 | -59.5825 | 63.6246 | -59.4681 | -59.9304 | -59.8938 | -0.022888 | 63.2767 | -59.5779 | 63.652 | -59.5367 | -59.6924 | -59.5963 | -0.064087 | -0.14648 | 0.24262 | 0.050354 | -0.37537 | -0.41199 | -0.31128 | -0.3479 | -0.059509 | -0.10529 | 0.27008 | -0.01831 | -0.077819 | -0.17395 | -0.01831 | -0.11444 | 0.11444 | 123.2071 | 0.041199 | 123.23 | 122.818 | 122.8546 | 122.7539 | 122.7951 | -122.9645 | -122.9599 | 123.143 | 123.1705 | 59.5001 | 59.4955
188.9531 | 123.1979 | -59.5367 | 63.3728 | -0.0080386 | 0.0034793 | 0.067921 | 0.075804 | -0.018497 | -0.04263 | 0.0056262 | 0.029861 | -0.0007936 | 0.056178 | 0.061592 | 4.2208e-05 | 0.0099092 | -0.0051076 | -0.027466 | 63.2355 | -59.6008 | 63.533 | -59.6054 | -59.8526 | -59.9167 | 0.027466 | 63.3087 | -59.5688 | 63.6108 | -59.5963 | -59.6558 | -59.7061 | -0.064087 | -0.13733 | 0.16022 | -0.068665 | -0.37994 | -0.31586 | -0.31586 | -0.25177 | -0.032044 | -0.064087 | 0.23804 | -0.059509 | -0.16937 | -0.11902 | -0.13733 | -0.086975 | -0.004578 | 123.1338 | -0.027465 | 123.1796 | 122.8363 | 122.8775 | 122.7722 | 122.8455 | -122.9736 | -122.9416 | 123.0698 | 123.1476 | 59.5093 | 59.5642
189.9531 | 123.1979 | -59.523 | 63.4094 | 0.037738 | -0.0018617 | 0.060444 | 0.071531 | 0.014615 | 0.015048 | 0.0034902 | 0.10615 | 0.0034794 | 0.063655 | 0.097908 | -0.0031618 | 0.0056372 | 0.010913 | -0.009155 | 63.2492 | -59.5917 | 63.5239 | -59.4498 | -59.8206 | -59.8068 | -0.10071 | 63.3133 | -59.5779 | 63.5696 | -59.5505 | -59.7427 | -59.6558 | -0.068665 | -0.16022 | 0.11444 | 0.073242 | -0.28381 | -0.29755 | -0.21515 | -0.22888 | -0.054932 | -0.096131 | 0.16022 | -0.027466 | -0.13275 | -0.21973 | -0.07782 | -0.16479 | 0.14191 | 123.1155 | 0.027466 | 123.1476 | 122.8409 | 122.8912 | 122.7722 | 122.8363 | -123.0011 | -122.9874 | 123.0469 | 123.0927 | 59.5139 | 59.4223
190.9531 | 123.1842 | -59.5139 | 63.4415 | 0.068255 | 0.013092 | 0.062581 | 0.066191 | 0.0082064 | 0.0054353 | 0.0066942 | 0.10615 | -0.0072016 | 0.049769 | 0.047706 | -0.0063668 | 0.0024322 | -0.0019036 | -0.041199 | 63.2812 | -59.5917 | 63.5696 | -59.491 | -59.7839 | -59.8389 | -0.009155 | 63.3362 | -59.5871 | 63.5788 | -59.6375 | -59.6512 | -59.6832 | -0.07782 | -0.16022 | 0.12817 | 0.022888 | -0.32501 | -0.27008 | -0.24719 | -0.19226 | -0.073242 | -0.10529 | 0.13733 | -0.1236 | -0.16937 | -0.13733 | -0.096131 | -0.064087 | 0.10071 | 123.1613 | -0.050354 | 123.1659 | 122.8729 | 122.9233 | 122.7951 | 122.85 | -123.0331 | -123.0286 | 123.0835 | 123.0927 | 59.4727 | 59.5047
191.9531 | 123.2391 | -59.5413 | 63.3957 | -0.038556 | -0.0061337 | 0.063649 | 0.07794 | -0.014224 | -0.0041777 | 0.010966 | -0.046432 | 0.0024114 | 0.083949 | -0.0014268 | -0.0010258 | 0.012045 | -0.013653 | 0.027466 | 63.2446 | -59.6054 | 63.4918 | -59.6008 | -59.8709 | -59.9075 | -0.018311 | 63.295 | -59.5734 | 63.5788 | -59.5551 | -59.6924 | -59.6375 | -0.064087 | -0.15106 | 0.09613 | -0.059509 | -0.36621 | -0.32959 | -0.30212 | -0.2655 | -0.032043 | -0.10071 | 0.1831 | -0.013733 | -0.09613 | -0.15106 | -0.064087 | -0.11902 | 0.004578 | 123.0972 | 0.01831 | 123.1522 | 122.85 | 122.8683 | 122.786 | 122.8363 | -123.0011 | -122.9691 | 123.0331 | 123.1201 | 59.5688 | 59.523
192.9531 | 123.1888 | -59.5551 | 63.4094 | 0.12929 | -0.0050657 | 0.065785 | 0.075804 | 0.0060704 | 0.010776 | -0.0018508 | -0.061691 | -0.0007936 | 0.068995 | 0.095771 | -0.0074348 | -0.0029078 | -0.010449 | -0.054932 | 63.2721 | -59.5871 | 63.5834 | -59.5001 | -59.8618 | -59.7336 | 0.004578 | 63.3362 | -59.5779 | 63.5788 | -59.6375 | -59.7015 | -59.7427 | -0.032043 | -0.13733 | 0.17395 | 0.054932 | -0.17853 | -0.3067 | -0.14648 | -0.27466 | -0.022888 | -0.073242 | 0.16937 | -0.082397 | -0.18768 | -0.14648 | -0.16479 | -0.1236 | 0.086975 | 123.1705 | -0.059509 | 123.1567 | 122.8592 | 122.9141 | 122.8271 | 122.8912 | -122.9965 | -122.9874 | 123.1384 | 123.1338 | 59.5001 | 59.5596
193.9531 | 123.1888 | -59.523 | 63.3911 | 0.037738 | 0.0056153 | 0.065785 | 0.076872 | 0.0039344 | 9.5287e-05 | 0.0034902 | 0.075638 | -0.0007936 | 0.071131 | 0.053047 | -0.010639 | 0.013113 | -0.018994 | -0.018311 | 63.2629 | -59.5963 | 63.5513 | -59.5779 | -59.816 | -59.9075 | -0.022888 | 63.3133 | -59.5871 | 63.5696 | -59.5551 | -59.7656 | -59.6558 | -0.073242 | -0.12817 | 0.16022 | -0.054932 | -0.38452 | -0.29297 | -0.31128 | -0.21973 | -0.064087 | -0.07782 | 0.17853 | -0.032044 | -0.13275 | -0.24262 | -0.068665 | -0.17853 | 0.01831 | 123.1476 | 0.032043 | 123.1567 | 122.8592 | 122.9004 | 122.7859 | 122.8363 | -122.9874 | -122.9782 | 123.0743 | 123.0927 | 59.5047 | 59.5001
194.9531 | 123.2117 | -59.491 | 63.4277 | 0.15981 | 0.0056153 | 0.055104 | 0.067259 | -0.022769 | -0.0052457 | 0.0013532 | 0.10615 | -0.0093376 | 0.073268 | 0.095771 | 0.0021782 | 0.0067052 | -0.029675 | -0.082397 | 63.2721 | -59.6054 | 63.5559 | -59.4635 | -59.8526 | -59.8114 | -0.004578 | 63.327 | -59.5413 | 63.6383 | -59.5779 | -59.6649 | -59.6603 | -0.11444 | -0.15564 | 0.12817 | 0.027466 | -0.32043 | -0.36163 | -0.20599 | -0.24719 | -0.050354 | -0.10071 | 0.21057 | -0.086975 | -0.16937 | -0.17395 | -0.11902 | -0.1236 | 0.14191 | 123.1613 | -0.036621 | 123.1796 | 122.8775 | 122.8683 | 122.7631 | 122.818 | -123.0331 | -122.9691 | 123.0469 | 123.1293 | 59.4086 | 59.4864
195.9531 | 123.2254 | -59.523 | 63.4094 | -0.038556 | 0.0056153 | 0.058308 | 0.087553 | -0.0024746 | -0.021267 | -0.00078276 | 0.04512 | 0.0024114 | 0.041224 | 0.058387 | -0.0052988 | 0.012045 | -0.0061756 | 0.004578 | 63.2538 | -59.5917 | 63.5513 | -59.5963 | -59.8572 | -59.9213 | 0.004578 | 63.295 | -59.5734 | 63.5788 | -59.5871 | -59.7198 | -59.6512 | -0.068665 | -0.15564 | 0.14191 | -0.073242 | -0.39825 | -0.33417 | -0.32959 | -0.2655 | -0.050354 | -0.11444 | 0.16937 | -0.064087 | -0.12817 | -0.19684 | -0.07782 | -0.14649 | -0.004577 | 123.143 | -0.013733 | 123.1522 | 122.8455 | 122.8683 | 122.7768 | 122.818 | -123.0011 | -122.9828 | 123.0743 | 123.1018 | 59.5276 | 59.5276
196.9531 | 123.1796 | -59.5276 | 63.3911 | -0.023297 | 0.0066833 | 0.056172 | 0.081144 | -0.0035426 | 0.0032993 | 0.00028524 | 0.13667 | 0.0045474 | 0.088221 | 0.066932 | -0.0031618 | 0.0045682 | 0.0066414 | -0.068665 | 63.2446 | -59.6008 | 63.5422 | -59.5047 | -59.8434 | -59.8343 | -0.045776 | 63.3179 | -59.5642 | 63.588 | -59.61 | -59.6924 | -59.6741 | -0.073242 | -0.14648 | 0.15106 | 0.022888 | -0.3067 | -0.31586 | -0.23346 | -0.24262 | -0.036621 | -0.073242 | 0.19684 | -0.082397 | -0.14648 | -0.16479 | -0.10986 | -0.12817 | 0.09613 | 123.143 | -0.045776 | 123.1522 | 122.8455 | 122.8821 | 122.7722 | 122.8455 | -122.9919 | -122.9553 | 123.0698 | 123.1155 | 59.4589 | 59.4818
197.9531 | 123.2391 | -59.5413 | 63.4003 | 0.12929 | 0.01416 | 0.052968 | 0.062986 | -0.0056786 | -0.010586 | 0.0013532 | -0.015915 | -0.013611 | 0.063655 | 0.076545 | -0.0085028 | -0.0061128 | -0.0083126 | 0.013733 | 63.2584 | -59.6191 | 63.5696 | -59.6512 | -59.8434 | -59.9121 | 0.036621 | 63.2996 | -59.5596 | 63.5742 | -59.5779 | -59.6695 | -59.6695 | -0.07782 | -0.14191 | 0.16937 | -0.10986 | -0.37079 | -0.30212 | -0.29297 | -0.2243 | -0.01831 | -0.10071 | 0.17395 | -0.036621 | -0.12817 | -0.12817 | -0.10986 | -0.10986 | -0.032043 | 123.1888 | -0.018311 | 123.1338 | 122.8775 | 122.8592 | 122.7997 | 122.8409 | -123.0194 | -122.9599 | 123.111 | 123.1155 | 59.5551 | 59.5779
198.9531 | 123.1934 | -59.5322 | 63.4003 | -0.0080386 | 0.0013433 | 0.059376 | 0.065123 | -0.01102 | 0.020389 | 0.0013532 | 0.014603 | 0.0045474 | 0.062587 | 0.091499 | 0.0021782 | 0.0024322 | 0.0055734 | -0.027466 | 63.2355 | -59.5917 | 63.5193 | -59.4955 | -59.8892 | -59.8434 | -0.022888 | 63.3087 | -59.5688 | 63.6017 | -59.5871 | -59.7336 | -59.6695 | -0.059509 | -0.16479 | 0.11902 | 0.036622 | -0.31128 | -0.35706 | -0.25177 | -0.29755 | -0.036621 | -0.091553 | 0.20142 | -0.054931 | -0.13733 | -0.20142 | -0.10071 | -0.16479 | 0.096131 | 123.111 | -0.01831 | 123.1705 | 122.8271 | 122.8775 | 122.7676 | 122.8409 | -122.9919 | -122.9691 | 123.0515 | 123.1339 | 59.5047 | 59.5093
199.9531 | 123.1796 | -59.5367 | 63.4369 | 0.098773 | -0.00079271 | 0.059376 | 0.070463 | -0.0056786 | -0.020199 | -0.0018508 | 0.12141 | 0.0045474 | 0.076472 | 0.035957 | -0.0052988 | 0.0067052 | -0.00083564 | -0.032043 | 63.2446 | -59.61 | 63.5971 | -59.5139 | -59.7885 | -59.8572 | -0.004578 | 63.3041 | -59.5825 | 63.6154 | -59.6008 | -59.7244 | -59.6695 | -0.073242 | -0.19226 | 0.16022 | 0.022888 | -0.32043 | -0.25177 | -0.24719 | -0.17853 | -0.045777 | -0.13275 | 0.17853 | -0.064087 | -0.13275 | -0.18768 | -0.086975 | -0.14191 | 0.09613 | 123.2071 | -0.01831 | 123.1979 | 122.8546 | 122.8867 | 122.7814 | 122.8409 | -123.0469 | -123.0194 | 123.1338 | 123.1522 | 59.5047 | 59.5322
200.9531 | 123.3353 | -59.5367 | 63.4232 | 0.037738 | 0.00027529 | 0.059376 | 0.083281 | -0.0035426 | 0.0011633 | 0.0024222 | 0.04512 | 0.0088204 | 0.064723 | 0.06266 | -0.0020938 | -0.0007718 | -0.0061756 | -0.041199 | 63.2538 | -59.5917 | 63.5651 | -59.5093 | -59.8251 | -59.8206 | -0.045776 | 63.3316 | -59.5688 | 63.5742 | -59.5642 | -59.7244 | -59.7565 | -0.054932 | -0.16937 | 0.14191 | 0.027466 | -0.28381 | -0.28839 | -0.22888 | -0.23346 | -0.032044 | -0.091553 | 0.15106 | -0.027466 | -0.21973 | -0.18768 | -0.18768 | -0.15564 | 0.082398 | 123.1567 | 0.004578 | 123.143 | 122.8455 | 122.9004 | 122.7905 | 122.8683 | -123.0148 | -122.9919 | 123.1018 | 123.111 | 59.4955 | 59.491
201.9531 | 123.2391 | -59.5184 | 63.3957 | 0.052997 | 0.0066833 | 0.065785 | 0.075804 | 0.00072943 | -0.0063137 | 0.016307 | 0.21297 | 0.0066834 | 0.058314 | 0.053047 | -0.0052988 | 0.022726 | 0.028003 | -0.013733 | 63.2446 | -59.61 | 63.3636 | -59.7565 | -59.8801 | -59.7565 | 0.018311 | 63.3087 | -59.5734 | 63.6337 | -59.5642 | -59.6741 | -59.6558 | -0.091552 | -0.15106 | -0.032044 | -0.23804 | -0.23804 | -0.36163 | -0.14648 | -0.27008 | -0.054931 | -0.086975 | 0.23804 | -0.045776 | -0.13733 | -0.15564 | -0.082398 | -0.10071 | -0.14648 | 122.9736 | 0.009155 | 123.2071 | 122.8546 | 122.8821 | 122.7631 | 122.8271 | -123.0057 | -122.9691 | 122.8821 | 123.1522 | 59.5047 | 59.5367
202.9531 | 123.1796 | -59.5184 | 63.3911 | -0.023297 | -0.0039977 | 0.064717 | 0.070463 | 0.0050024 | 0.0075723 | -0.0050548 | -0.00065608 | -0.011475 | 0.054042 | 0.075477 | -0.0042298 | 0.0002962 | -0.0061756 | 0.004578 | 63.2492 | -59.6191 | 63.5193 | -59.5505 | -59.8434 | -59.8526 | -0.054932 | 63.2858 | -59.5642 | 63.5513 | -59.5734 | -59.7336 | -59.6741 | -0.10071 | -0.14191 | 0.12817 | -0.032043 | -0.33417 | -0.32501 | -0.23346 | -0.2243 | -0.045776 | -0.10528 | 0.16022 | -0.054931 | -0.15564 | -0.21515 | -0.10986 | -0.16937 | 0.068665 | 123.1384 | -0.009155 | 123.1155 | 122.8683 | 122.85 | 122.7676 | 122.8043 | -123.0103 | -122.9553 | 123.0377 | 123.0698 | 59.523 | 59.4635
203.9531 | 123.23 | -59.5276 | 63.3591 | 0.0072204 | 0.0066833 | 0.058308 | 0.065123 | -0.015292 | -0.0095177 | 0.012035 | -0.015915 | -0.0039976 | 0.058314 | 0.039161 | -0.010639 | 0.01525 | -0.0083126 | -0.027466 | 63.2446 | -59.5825 | 63.5422 | -59.5779 | -59.8938 | -59.8709 | 0.059509 | 63.327 | -59.5688 | 63.6795 | -59.6054 | -59.6649 | -59.642 | -0.054932 | -0.11444 | 0.1831 | -0.050354 | -0.34332 | -0.36621 | -0.28839 | -0.31128 | -0.041199 | -0.032044 | 0.32043 | -0.07782 | -0.11444 | -0.13733 | -0.073242 | -0.09613 | 0.004578 | 123.1247 | -0.036621 | 123.2483 | 122.8271 | 122.8958 | 122.7722 | 122.8546 | -122.9416 | -122.9279 | 123.0698 | 123.2071 | 59.5001 | 59.5871
204.9531 | 123.2025 | -59.5413 | 63.3957 | -0.0080386 | -0.0050657 | 0.050831 | 0.068327 | 0.015683 | -0.0073817 | -0.0093278 | -0.00065608 | -0.0072016 | 0.056178 | 0.065864 | 0.0011102 | 0.0002962 | -0.013653 | -0.018311 | 63.2629 | -59.5963 | 63.5284 | -59.5871 | -59.8343 | -59.935 | -0.022888 | 63.2904 | -59.5505 | 63.5742 | -59.5184 | -59.7519 | -59.6466 | -0.054931 | -0.13275 | 0.13275 | -0.045776 | -0.39368 | -0.29297 | -0.33875 | -0.23804 | -0.009155 | -0.10529 | 0.17853 | 0.022888 | -0.10528 | -0.21057 | -0.09613 | -0.20142 | 0.009155 | 123.1247 | 0.032043 | 123.1247 | 122.8592 | 122.8409 | 122.8043 | 122.8317 | -122.9919 | -122.9462 | 123.0698 | 123.1155 | 59.523 | 59.5184
205.9531 | 123.2483 | -59.5505 | 63.3774 | 0.098773 | -0.0018617 | 0.052968 | 0.071531 | -0.0067466 | -0.041562 | -0.0071918 | -0.1685 | 0.0066834 | 0.061518 | 0.068 | -0.012775 | 0.012045 | -0.014721 | -0.022888 | 63.2584 | -59.61 | 63.5239 | -59.5779 | -59.9167 | -59.8389 | -0.20599 | 63.2217 | -59.61 | 63.6108 | -59.5459 | -59.6466 | -59.6786 | -0.059509 | -0.11902 | 0.14648 | -0.027466 | -0.28839 | -0.36621 | -0.22888 | -0.3067 | -0.059509 | -0.15564 | 0.23346 | 0.004578 | -0.12817 | -0.09613 | -0.068665 | -0.036621 | 0.032043 | 123.1338 | 0.064087 | 123.2208 | 122.8683 | 122.8317 | 122.8088 | 122.7722 | -122.9874 | -122.9874 | 123.0743 | 123.1613 | 59.5276 | 59.3445
206.9531 | 123.2437 | -59.5184 | 63.3774 | 0.037738 | 0.0045473 | 0.065785 | 0.069395 | -0.0024746 | 0.019321 | -0.00078276 | -0.015915 | -0.0093376 | 0.042292 | 0.08509 | -0.0074348 | 0.0088412 | -0.016858 | 0 | 63.2675 | -59.5963 | 63.5422 | -59.5917 | -59.8572 | -59.9075 | 0.009155 | 63.3041 | -59.5688 | 63.588 | -59.5459 | -59.7061 | -59.6054 | -0.077819 | -0.10986 | 0.16479 | -0.073242 | -0.3891 | -0.33874 | -0.31128 | -0.26093 | -0.050354 | -0.073242 | 0.21057 | -0.027465 | -0.086975 | -0.18768 | -0.036621 | -0.13733 | 0.004577 | 123.1384 | 0.022889 | 123.1567 | 122.8638 | 122.8729 | 122.7859 | 122.8226 | -122.9736 | -122.9462 | 123.0606 | 123.1064 | 59.5184 | 59.5276
207.9531 | 123.2483 | -59.5322 | 63.4048 | 0.022479 | 0.0034793 | 0.056172 | 0.069395 | 0.0071384 | 0.0054353 | 0.0034902 | -0.061691 | 0.0002754 | 0.045497 | 0.068 | -0.0031618 | 0.018454 | -0.036084 | -0.10529 | 63.2538 | -59.6191 | 63.533 | -59.5139 | -59.8572 | -59.8297 | -0.027466 | 63.2996 | -59.5596 | 63.6337 | -59.5825 | -59.7107 | -59.642 | -0.086975 | -0.15106 | 0.12817 | 0.018311 | -0.29755 | -0.32501 | -0.21057 | -0.23804 | -0.027465 | -0.10529 | 0.22888 | -0.050354 | -0.10986 | -0.17853 | -0.082398 | -0.15106 | 0.10529 | 123.1522 | -0.022889 | 123.1934 | 122.8729 | 122.8592 | 122.7859 | 122.8317 | -123.024 | -122.9645 | 123.0652 | 123.1659 | 59.4269 | 59.5047
208.9531 | 123.2254 | -59.523 | 63.382 | 0.022479 | -0.00079271 | 0.063649 | 0.073668 | -0.0024746 | 0.0032993 | 0.0024222 | 0.04512 | -0.0007936 | 0.067927 | 0.073341 | -0.0020938 | 0.0045682 | 0.010913 | 0.013733 | 63.2584 | -59.6191 | 63.5605 | -59.6329 | -59.8663 | -59.903 | 0.036621 | 63.2812 | -59.5459 | 63.6154 | -59.5734 | -59.6924 | -59.6695 | -0.096131 | -0.1236 | 0.17853 | -0.10986 | -0.37994 | -0.34332 | -0.28381 | -0.24719 | -0.022888 | -0.10071 | 0.23346 | -0.050354 | -0.14648 | -0.16937 | -0.1236 | -0.14648 | -0.013733 | 123.1796 | -0.027466 | 123.1613 | 122.8775 | 122.8271 | 122.7814 | 122.8043 | -123.0011 | -122.9279 | 123.0835 | 123.1384 | 59.5367 | 59.5596
209.9531 | 123.2437 | -59.5001 | 63.3911 | -0.084332 | 0.0013433 | 0.070057 | 0.079008 | 0.0039344 | 0.0065043 | 0.013103 | -0.13799 | -0.0007936 | 0.061518 | 0.053047 | -0.0052988 | 0.013113 | -0.014721 | -0.041199 | 63.2538 | -59.6054 | 63.5101 | -59.5184 | -59.9121 | -59.8709 | -0.009155 | 63.2996 | -59.5688 | 63.4598 | -59.3262 | -59.5642 | -59.5505 | -0.10529 | -0.13733 | 0.11902 | -0.018311 | -0.37079 | -0.41199 | -0.2655 | -0.3067 | -0.068665 | -0.091552 | 0.068665 | 0.17395 | -0.050354 | -0.064087 | 0.018311 | 0.004578 | 0.086975 | 123.1155 | 0.24262 | 123.0286 | 122.8592 | 122.8683 | 122.7539 | 122.7997 | -122.9965 | -122.9599 | 123.0103 | 122.9599 | 59.4589 | 59.491
210.9531 | 123.1888 | -59.5367 | 63.3682 | 0.052997 | 0.0077523 | 0.064717 | 0.070463 | 0.013547 | 9.5287e-05 | 0.0056262 | 0.22823 | 0.0098884 | 0.066859 | 0.012458 | 4.2208e-05 | 0.01525 | -0.014721 | -0.027466 | 63.2492 | -59.61 | 63.5834 | -59.61 | -59.8709 | -59.8984 | 0.022888 | 63.3041 | -59.5642 | 63.5971 | -59.5917 | -59.7061 | -59.6603 | -0.073242 | -0.11902 | 0.21515 | -0.073242 | -0.36163 | -0.33417 | -0.28839 | -0.26093 | -0.027466 | -0.064087 | 0.22888 | -0.054932 | -0.1236 | -0.16937 | -0.09613 | -0.14191 | 0 | 123.1934 | -0.027466 | 123.1613 | 122.8592 | 122.8683 | 122.7859 | 122.8409 | -122.9782 | -122.9324 | 123.1201 | 123.1338 | 59.5093 | 59.5596
211.9531 | 123.2208 | -59.5596 | 63.3453 | 0.083514 | 0.0013433 | 0.059376 | 0.075804 | 0.0017974 | -0.013791 | -0.0050548 | 0.014603 | 0.0056154 | 0.076472 | 0.032752 | -0.0074348 | 0.012045 | 0.0023694 | -0.073242 | 63.2904 | -59.6558 | 63.588 | -59.4727 | -59.8068 | -59.8068 | -0.09613 | 63.3224 | -59.5825 | 63.588 | -59.5825 | -59.7153 | -59.5917 | -0.096131 | -0.054932 | 0.24262 | 0.086975 | -0.24719 | -0.24719 | -0.15106 | -0.15106 | -0.022889 | -0.022888 | 0.24262 | -0.022889 | -0.032044 | -0.15564 | -0.009155 | -0.13275 | 0.18311 | 123.2437 | 0 | 123.1705 | 122.9462 | 122.905 | 122.85 | 122.8821 | -123.0011 | -122.9279 | 123.1476 | 123.1476 | 59.4864 | 59.4635
212.9531 | 123.2483 | -59.5047 | 63.414 | -0.038556 | 0.0045473 | 0.063649 | 0.079008 | 0.0028664 | -0.021267 | -0.010396 | -0.19902 | -0.0018616 | 0.073268 | 0.080818 | -0.010639 | 0.030203 | 0.0055734 | -0.064087 | 63.2492 | -59.6054 | 63.5559 | -59.5551 | -59.8755 | -59.8846 | -0.004578 | 63.3224 | -59.61 | 63.4186 | -59.3353 | -59.5276 | -59.5871 | -0.10071 | -0.16479 | 0.14191 | -0.050354 | -0.37994 | -0.37079 | -0.27924 | -0.27008 | -0.10529 | -0.091552 | 0.004578 | 0.16937 | -0.082397 | -0.022888 | 0.022888 | 0.082397 | 0.050354 | 123.1613 | 0.27466 | 123.0286 | 122.8546 | 122.9324 | 122.7539 | 122.8271 | -123.0194 | -123.024 | 123.0606 | 122.9233 | 59.4406 | 59.5001
213.9531 | 123.2483 | -59.5322 | 63.3957 | 0.19033 | -0.00079271 | 0.051899 | 0.067259 | 0.0039344 | 9.5287e-05 | 0.0098982 | -0.092209 | -0.0018616 | 0.062587 | 0.059455 | -0.010639 | 0.014181 | 0.0077094 | -0.050354 | 63.2629 | -59.6283 | 63.5376 | -59.5413 | -59.8297 | -59.8526 | -0.07782 | 63.3041 | -59.5917 | 63.5788 | -59.5367 | -59.697 | -59.6329 | -0.09613 | -0.13275 | 0.14191 | -0.009155 | -0.32043 | -0.29755 | -0.2243 | -0.20142 | -0.059509 | -0.091553 | 0.1831 | -0.004577 | -0.10071 | -0.16479 | -0.041199 | -0.10528 | 0.086975 | 123.1659 | 0.054932 | 123.1705 | 122.8912 | 122.8958 | 122.7951 | 122.8363 | -123.024 | -122.9874 | 123.0698 | 123.111 | 59.4818 | 59.4543
214.9531 | 123.2071 | -59.5459 | 63.3774 | -0.0080386 | -0.0018617 | 0.059376 | 0.075804 | 0.0017974 | 0.012912 | -0.0061228 | 0.090897 | -0.0007936 | 0.06045 | 0.01139 | 0.0043152 | 0.0002962 | -0.02113 | -0.050354 | 63.2401 | -59.5688 | 63.5147 | -59.5734 | -59.8709 | -59.8801 | 0.009155 | 63.3087 | -59.5505 | 63.62 | -59.5871 | -59.6741 | -59.7015 | -0.022889 | -0.13733 | 0.13733 | -0.027466 | -0.33417 | -0.32501 | -0.31128 | -0.30212 | -0.004578 | -0.068664 | 0.24262 | -0.041199 | -0.15564 | -0.12817 | -0.15106 | -0.1236 | -0.004577 | 123.0835 | -0.036621 | 123.1705 | 122.8088 | 122.8592 | 122.7859 | 122.8546 | -122.9462 | -122.9279 | 123.0606 | 123.1659 | 59.4955 | 59.5551
215.9531 | 123.1934 | -59.5642 | 63.4094 | 0.15981 | -0.0029297 | 0.05724 | 0.0726 | -0.0099516 | -0.0063137 | 0.0024222 | -0.10747 | 0.010956 | 0.066859 | 0.065864 | -0.0063668 | 0.017386 | -0.00083564 | -0.082397 | 63.2767 | -59.6466 | 63.6337 | -59.4727 | -59.7519 | -59.8389 | -0.11902 | 63.3087 | -59.5871 | 63.5239 | -59.5642 | -59.816 | -59.6786 | -0.082397 | -0.13275 | 0.2243 | 0.091553 | -0.27466 | -0.18768 | -0.19226 | -0.10529 | -0.022888 | -0.10071 | 0.11444 | 0 | -0.11444 | -0.25177 | -0.091553 | -0.22888 | 0.17395 | 123.2803 | 0.022888 | 123.111 | 122.9233 | 122.8958 | 122.8409 | 122.8729 | -123.056 | -122.9965 | 123.1979 | 123.0881 | 59.4818 | 59.4452
216.9531 | 123.2346 | -59.5367 | 63.3545 | 0.052997 | 0.0034793 | 0.065785 | 0.062986 | -0.013156 | 0.0011633 | -0.0082598 | -0.031174 | -0.0007936 | 0.070063 | 0.047706 | -0.0020938 | 0.014181 | 0.00023236 | -0.07782 | 63.2584 | -59.6375 | 63.5651 | -59.5184 | -59.8663 | -59.8114 | -0.041199 | 63.3224 | -59.5871 | 63.652 | -59.61 | -59.6832 | -59.6283 | -0.10071 | -0.09613 | 0.21057 | 0.01831 | -0.27466 | -0.32959 | -0.17395 | -0.22888 | -0.050354 | -0.032043 | 0.29755 | -0.073242 | -0.091553 | -0.14648 | -0.041199 | -0.096131 | 0.11902 | 123.2025 | -0.022888 | 123.2391 | 122.8958 | 122.9095 | 122.7951 | 122.8592 | -122.9919 | -122.9416 | 123.1018 | 123.1888 | 59.4589 | 59.4955
217.9531 | 123.1934 | -59.523 | 63.3957 | 0.068255 | 0.0024113 | 0.055104 | 0.097166 | 0.0039344 | -0.010586 | -0.00078276 | -0.12273 | 0.0066834 | 0.05511 | 0.061592 | -0.0095708 | 0.010977 | -0.0083126 | -0.073242 | 63.2675 | -59.6146 | 63.6246 | -59.5047 | -59.7931 | -59.8251 | -0.086975 | 63.3179 | -59.5688 | 63.5422 | -59.5596 | -59.7153 | -59.642 | -0.091553 | -0.12817 | 0.22888 | 0.01831 | -0.30212 | -0.27008 | -0.21057 | -0.17853 | -0.045777 | -0.07782 | 0.14648 | -0.036621 | -0.11902 | -0.19226 | -0.073242 | -0.14648 | 0.10986 | 123.2391 | 0.009156 | 123.111 | 122.8821 | 122.8867 | 122.7905 | 122.8409 | -123.0103 | -122.9645 | 123.1476 | 123.0652 | 59.4498 | 59.436
218.9531 | 123.1201 | -59.5734 | 63.4094 | -0.038556 | 0.0077523 | 0.060444 | 0.068327 | -0.016361 | 0.022525 | -0.0039868 | -0.12273 | 0.016296 | 0.073268 | 0.075477 | -0.012775 | 0.012045 | 0.0087774 | -0.059509 | 63.327 | -59.6283 | 63.6246 | -59.3903 | -59.7519 | -59.7382 | -0.16479 | 63.3316 | -59.5917 | 63.5101 | -59.7015 | -59.816 | -59.7519 | -0.054932 | -0.082398 | 0.21515 | 0.1831 | -0.1648 | -0.17853 | -0.10986 | -0.1236 | -0.018311 | -0.07782 | 0.10071 | -0.12817 | -0.17853 | -0.24262 | -0.16022 | -0.2243 | 0.23804 | 123.2529 | -0.10986 | 123.1018 | 122.9553 | 122.9233 | 122.9004 | 122.905 | -123.0377 | -123.0011 | 123.1979 | 123.0835 | 59.5139 | 59.4086
219.9531 | 123.1613 | -59.5688 | 63.4003 | 0.098773 | 0.0077523 | 0.05724 | 0.066191 | -0.00033857 | -0.0041777 | 0.019511 | -0.07695 | 0.0088204 | 0.052973 | 0.057319 | -0.0042298 | 0.014181 | -0.020062 | -0.054932 | 63.2629 | -59.6375 | 63.6932 | -59.491 | -59.7427 | -59.7885 | -0.1236 | 63.3087 | -59.61 | 63.501 | -59.6512 | -59.7839 | -59.7015 | -0.068664 | -0.13733 | 0.29297 | 0.07782 | -0.21973 | -0.17395 | -0.15106 | -0.10529 | -0.041198 | -0.091553 | 0.10071 | -0.082397 | -0.13275 | -0.21515 | -0.091553 | -0.17395 | 0.14648 | 123.3307 | -0.041199 | 123.111 | 122.9004 | 122.9187 | 122.8317 | 122.8775 | -123.0377 | -123.0103 | 123.262 | 123.0698 | 59.5139 | 59.4452
220.9531 | 123.1384 | -59.5596 | 63.414 | 0.11403 | -0.0072017 | 0.05724 | 0.062986 | 0.0060704 | 0.0075723 | 0.0013532 | -0.15324 | 0.0002754 | 0.064723 | 0.057319 | -0.0085028 | 0.016318 | -0.0061756 | -0.10986 | 63.2996 | -59.6146 | 63.6337 | -59.3674 | -59.7839 | -59.7382 | -0.16937 | 63.3224 | -59.6146 | 63.5513 | -59.6878 | -59.8206 | -59.7244 | -0.054932 | -0.11444 | 0.21973 | 0.19226 | -0.17853 | -0.2243 | -0.1236 | -0.16937 | -0.054932 | -0.091552 | 0.13733 | -0.12817 | -0.16479 | -0.26093 | -0.10986 | -0.20599 | 0.24719 | 123.2483 | -0.073242 | 123.1659 | 122.9141 | 122.937 | 122.8592 | 122.8821 | -123.0286 | -123.0286 | 123.1934 | 123.111 | 59.4498 | 59.3903
221.9531 | 123.0698 | -59.5871 | 63.3591 | 0.037738 | 0.0045473 | 0.071125 | 0.07794 | 0.0060704 | -0.0063137 | 0.0098982 | -0.19902 | 0.0098884 | 0.049769 | 0.089363 | 0.0064512 | 0.0099092 | -0.0040396 | -0.050354 | 63.2904 | -59.6283 | 63.6932 | -59.3994 | -59.6832 | -59.7702 | -0.17395 | 63.3316 | -59.6054 | 63.4918 | -59.7427 | -59.8251 | -59.7977 | -0.041199 | -0.068665 | 0.33417 | 0.18768 | -0.18311 | -0.096131 | -0.14191 | -0.054932 | -0.018311 | -0.027466 | 0.13275 | -0.15564 | -0.21057 | -0.23804 | -0.19226 | -0.21973 | 0.22888 | 123.3215 | -0.13733 | 123.0972 | 122.9187 | 122.937 | 122.8775 | 122.9187 | -122.9874 | -122.9645 | 123.2803 | 123.0789 | 59.5367 | 59.4131
222.9531 | 123.0881 | -59.5688 | 63.4598 | 0.12929 | 0.0045473 | 0.059376 | 0.064055 | 0.0017974 | -0.0095177 | -0.0082598 | 0.04512 | 0.0002754 | 0.063655 | 0.070137 | 4.2208e-05 | 0.014181 | -0.0040396 | -0.027466 | 63.295 | -59.6237 | 63.652 | -59.3994 | -59.7427 | -59.7336 | -0.16937 | 63.3545 | -59.5734 | 63.5101 | -59.697 | -59.8297 | -59.6924 | -0.054931 | -0.16479 | 0.19226 | 0.16937 | -0.16479 | -0.17395 | -0.10986 | -0.11902 | -0.004577 | -0.10529 | 0.050354 | -0.12817 | -0.1236 | -0.26093 | -0.11902 | -0.25635 | 0.2243 | 123.2758 | -0.1236 | 123.0835 | 122.9187 | 122.9279 | 122.8638 | 122.9233 | -123.0835 | -123.0331 | 123.2208 | 123.0789 | 59.5413 | 59.3994
223.9531 | 123.0881 | -59.5551 | 63.4232 | -0.0080386 | 0.010956 | 0.056172 | 0.069395 | 0.00072943 | -0.0084497 | -0.010396 | 0.060379 | 0.0034794 | 0.080744 | 0.057319 | 0.0053832 | 0.0088412 | 0.0055734 | -0.11444 | 63.2904 | -59.6558 | 63.7024 | -59.404 | -59.7015 | -59.7198 | -0.47607 | 63.2812 | -59.6695 | 63.5056 | -59.7519 | -59.7702 | -59.7565 | -0.10071 | -0.13275 | 0.27924 | 0.15106 | -0.1648 | -0.14648 | -0.064087 | -0.045776 | -0.11444 | -0.14191 | 0.082397 | -0.19684 | -0.20142 | -0.21515 | -0.086975 | -0.10071 | 0.25177 | 123.3582 | -0.082397 | 123.175 | 122.9462 | 122.9507 | 122.8455 | 122.8363 | -123.0789 | -123.0927 | 123.2574 | 123.0606 | 59.4406 | 59.079
224.9531 | 123.2483 | -59.5322 | 63.3728 | 0.11403 | 0.0045473 | 0.059376 | 0.066191 | 0.012479 | 9.5287e-05 | -0.0018508 | -0.015915 | 0.0034794 | 0.051905 | 0.073341 | -0.0085028 | -0.0018398 | -0.011517 | -0.050354 | 63.2355 | -59.6008 | 63.5239 | -59.5596 | -59.8801 | -59.8984 | -0.050354 | 63.2812 | -59.5734 | 63.7527 | -59.5322 | -59.6741 | -59.5505 | -0.068664 | -0.13733 | 0.15106 | -0.027465 | -0.36621 | -0.3479 | -0.29755 | -0.27924 | -0.041198 | -0.091553 | 0.37994 | 0 | -0.01831 | -0.14191 | 0.022888 | -0.10071 | 0.041199 | 123.1247 | 0.041198 | 123.3261 | 122.8363 | 122.8546 | 122.7676 | 122.8134 | -122.9736 | -122.9462 | 123.056 | 123.2849 | 59.4818 | 59.4818
225.9531 | 123.0743 | -59.5779 | 63.446 | 0.052997 | 0.0024113 | 0.061512 | 0.084349 | 0.027432 | -0.0041777 | -0.0039868 | 0.075638 | 0.0088204 | 0.061518 | 0.049842 | -0.0020938 | 0.02059 | -0.00083564 | -0.054932 | 63.3087 | -59.6191 | 63.6749 | -59.4223 | -59.7473 | -59.7244 | -0.12817 | 63.3774 | -59.5917 | 63.5376 | -59.7244 | -59.8068 | -59.761 | -0.041199 | -0.13733 | 0.22888 | 0.15564 | -0.14648 | -0.16937 | -0.10529 | -0.12817 | -0.013733 | -0.068665 | 0.091553 | -0.14648 | -0.1831 | -0.22888 | -0.16937 | -0.21515 | 0.19684 | 123.2941 | -0.13275 | 123.1293 | 122.9279 | 122.9691 | 122.8867 | 122.9553 | -123.0652 | -123.0377 | 123.2529 | 123.1155 | 59.523 | 59.4498
226.9531 | 123.0927 | -59.5779 | 63.446 | 0.022479 | -0.00079271 | 0.058308 | 0.074736 | -0.01102 | -0.018063 | -0.00078276 | -0.046432 | -0.0007936 | 0.067927 | 0.04557 | 0.0021782 | 0.0056372 | -0.0019036 | -0.10529 | 63.2812 | -59.6283 | 63.6795 | -59.3994 | -59.697 | -59.7473 | -0.091553 | 63.3133 | -59.6329 | 63.5101 | -59.761 | -59.8572 | -59.6786 | -0.050354 | -0.16479 | 0.23346 | 0.17853 | -0.16937 | -0.11902 | -0.11902 | -0.068664 | -0.054932 | -0.13275 | 0.064087 | -0.1831 | -0.10071 | -0.27924 | -0.045776 | -0.2243 | 0.22888 | 123.3078 | -0.12817 | 123.143 | 122.9095 | 122.9462 | 122.8592 | 122.8912 | -123.0743 | -123.0789 | 123.2574 | 123.0881 | 59.4727 | 59.4864
227.9531 | 122.9691 | -59.6146 | 63.3957 | 0.11403 | 0.010956 | 0.056172 | 0.064055 | 0.022092 | -0.021267 | 0.0034902 | -0.15324 | 0.0066834 | 0.065791 | 0.069068 | -0.0020938 | 0.0077732 | -0.0040396 | -0.09613 | 63.295 | -59.6329 | 63.6703 | -59.3857 | -59.7061 | -59.6878 | -0.20142 | 63.3453 | -59.61 | 63.4872 | -59.7519 | -59.9075 | -60.0815 | -0.018311 | -0.10071 | 0.27466 | 0.22888 | -0.073242 | -0.091553 | -0.054931 | -0.073242 | 0.004578 | -0.050354 | 0.091553 | -0.13733 | -0.46692 | -0.29297 | -0.4715 | -0.29755 | 0.24719 | 123.3032 | -0.14191 | 123.0972 | 122.9279 | 122.9553 | 122.9095 | 122.9599 | -123.0286 | -123.0057 | 123.2849 | 123.1018 | 59.5184 | 59.4131
228.9531 | 123.1201 | -59.5963 | 63.4323 | 0.0072204 | 0.0056153 | 0.060444 | 0.076872 | -0.0014066 | -0.011654 | -0.0039868 | -0.061691 | 0.0098884 | 0.054042 | 0.068 | -0.0020938 | 0.0099092 | -0.0083126 | -0.036621 | 63.295 | -59.6466 | 63.6749 | -59.4269 | -59.7153 | -59.7519 | -0.19226 | 63.3545 | -59.5917 | 63.4552 | -59.7015 | -59.8709 | -59.7382 | -0.050354 | -0.13733 | 0.24261 | 0.16937 | -0.15564 | -0.11902 | -0.10529 | -0.068665 | 0.004577 | -0.07782 | 0.022888 | -0.10529 | -0.14191 | -0.27466 | -0.14648 | -0.27924 | 0.21973 | 123.3215 | -0.10986 | 123.0469 | 122.9416 | 122.9462 | 122.8912 | 122.9507 | -123.0789 | -123.024 | 123.2712 | 123.0515 | 59.5596 | 59.404
229.9531 | 123.1155 | -59.5871 | 63.4369 | -0.0080386 | -0.010406 | 0.05724 | 0.070463 | 0.0050024 | -0.0063137 | -0.0039868 | 0.25874 | 0.0066834 | 0.063655 | 0.034889 | -0.013843 | 0.017386 | -0.0040396 | -0.10529 | 63.2812 | -59.6283 | 63.7024 | -59.166 | -59.8663 | -59.9579 | -0.17853 | 63.3682 | -59.6008 | 63.501 | -59.7427 | -59.7839 | -59.7244 | -0.041199 | -0.15564 | 0.2655 | 0.42114 | -0.37079 | -0.27924 | -0.32959 | -0.23804 | -0.013733 | -0.068665 | 0.064087 | -0.15564 | -0.13733 | -0.19684 | -0.1236 | -0.18311 | 0.46234 | 123.3307 | -0.14191 | 123.1018 | 122.9095 | 122.9691 | 122.8683 | 122.9553 | -123.0652 | -123.0377 | 123.2895 | 123.0881 | 59.4818 | 59.4086
230.9531 | 123.0698 | -59.5551 | 63.4323 | 0.037738 | 0.0034793 | 0.073262 | 0.061918 | -0.0035426 | -0.0095177 | -0.0082598 | -0.031174 | -0.0007936 | 0.081813 | 0.070137 | -0.0042298 | 0.0056372 | 0.0066414 | -0.10529 | 63.3179 | -59.6283 | 63.7024 | -59.3948 | -59.6924 | -59.7748 | -0.22888 | 63.3499 | -59.6054 | 63.7024 | -59.7427 | -59.6786 | -59.7015 | -0.073242 | -0.11444 | 0.27008 | 0.16022 | -0.21973 | -0.13733 | -0.14648 | -0.064087 | -0.050354 | -0.082397 | 0.27008 | -0.18768 | -0.14648 | -0.1236 | -0.09613 | -0.073242 | 0.23346 | 123.3307 | -0.13733 | 123.3078 | 122.9462 | 122.9553 | 122.8729 | 122.905 | -123.0606 | -123.0377 | 123.2574 | 123.2574 | 59.4498 | 59.3262
231.9531 | 123.1522 | -59.5734 | 63.4598 | 0.098773 | 0.01416 | 0.066853 | 0.067259 | -0.0078156 | 0.0011633 | 0.0088302 | -0.031174 | 0.0034794 | 0.054042 | 0.040229 | -0.0095708 | 0.014181 | -0.0051076 | -0.054932 | 63.2996 | -59.6191 | 63.6337 | -59.4086 | -59.7931 | -59.7244 | -0.11444 | 63.3453 | -59.5917 | 63.5422 | -59.6695 | -59.7794 | -59.7107 | -0.045777 | -0.16022 | 0.17395 | 0.16479 | -0.15106 | -0.21973 | -0.10529 | -0.17395 | -0.018311 | -0.11444 | 0.082397 | -0.096131 | -0.13733 | -0.20599 | -0.11902 | -0.18768 | 0.21057 | 123.2529 | -0.07782 | 123.1338 | 122.9187 | 122.937 | 122.8729 | 122.9187 | -123.0789 | -123.0515 | 123.2071 | 123.1155 | 59.5184 | 59.4589
232.9531 | 123.1018 | -59.5642 | 63.4186 | 0.068255 | 0.0077523 | 0.060444 | 0.065123 | -0.0088836 | -0.034085 | 0.0066942 | 0.16719 | 0.0056154 | 0.061518 | 0.073341 | -0.0085028 | 0.0035002 | -0.017926 | -0.064087 | 63.3179 | -59.6329 | 63.7115 | -59.4315 | -59.7061 | -59.7565 | -0.19684 | 63.3453 | -59.6191 | 63.446 | -59.7153 | -59.8297 | -59.7565 | -0.068665 | -0.10071 | 0.29297 | 0.13275 | -0.19226 | -0.14191 | -0.1236 | -0.073242 | -0.054932 | -0.073242 | 0.027466 | -0.15106 | -0.19226 | -0.2655 | -0.13733 | -0.21057 | 0.20142 | 123.3444 | -0.09613 | 123.0652 | 122.9507 | 122.9645 | 122.8821 | 122.9095 | -123.0515 | -123.0377 | 123.2758 | 123.0103 | 59.5001 | 59.3674
233.9531 | 123.143 | -59.5551 | 63.4506 | 0.14455 | -0.0050657 | 0.059376 | 0.070463 | 0.00072943 | -0.015927 | -0.011464 | 0.04512 | 0.0066834 | 0.052973 | 0.064796 | -0.0085028 | 0.017386 | 0.024799 | -0.050354 | 63.2904 | -59.6191 | 63.6154 | -59.4498 | -59.7931 | -59.7473 | -0.10986 | 63.3362 | -59.5779 | 63.5468 | -59.6191 | -59.7656 | -59.6603 | -0.064087 | -0.16022 | 0.16479 | 0.10529 | -0.19226 | -0.23804 | -0.12817 | -0.17395 | -0.022888 | -0.11444 | 0.09613 | -0.064087 | -0.10529 | -0.21057 | -0.082397 | -0.18768 | 0.16937 | 123.2346 | -0.041199 | 123.1247 | 122.9095 | 122.9141 | 122.8455 | 122.8912 | -123.0698 | -123.0286 | 123.1705 | 123.1018 | 59.5047 | 59.4452
234.9531 | 123.1064 | -59.5413 | 63.4277 | 0.052997 | 0.0077523 | 0.061512 | 0.0726 | 0.019955 | -0.021267 | 0.0024222 | 0.075638 | 0.0098884 | 0.081813 | 0.04557 | 0.0064512 | 0.0099092 | -0.0019036 | -0.10529 | 63.3224 | -59.6466 | 63.707 | -59.4223 | -59.7015 | -59.7107 | -0.11902 | 63.3179 | -59.6558 | 63.5376 | -59.8251 | -59.7748 | -59.7107 | -0.10528 | -0.10529 | 0.27924 | 0.11902 | -0.16937 | -0.16022 | -0.064087 | -0.054932 | -0.11444 | -0.10986 | 0.10986 | -0.28381 | -0.16937 | -0.23346 | -0.054931 | -0.11902 | 0.2243 | 123.3536 | -0.16937 | 123.1934 | 122.9691 | 122.9736 | 122.8638 | 122.8592 | -123.0743 | -123.0835 | 123.2483 | 123.0789 | 59.436 | 59.4223
236.0312 | 123.2025 | -59.5276 | 63.4277 | 0.083514 | 0.010956 | 0.063649 | 0.0726 | 0.030637 | -0.012723 | -0.0018508 | 0.41133 | 0.0013434 | 0.067927 | 0.027412 | -0.0074348 | 0.01525 | -0.015789 | 0.036621 | 63.295 | -59.5779 | 63.62 | -59.5642 | -59.7885 | -59.8251 | -0.064087 | 63.3041 | -59.5459 | 63.5239 | -59.5871 | -59.697 | -59.6603 | -0.050354 | -0.13275 | 0.19226 | -0.036621 | -0.29755 | -0.26093 | -0.24719 | -0.21057 | -0.01831 | -0.1236 | 0.096131 | -0.059509 | -0.13275 | -0.16937 | -0.11444 | -0.15106 | 0.013733 | 123.1979 | -0.041199 | 123.0698 | 122.8729 | 122.85 | 122.8226 | 122.8317 | -123.0057 | -122.9736 | 123.1476 | 123.0515 | 59.5642 | 59.4635
236.9531 | 123.175 | -59.5505 | 63.4506 | 0.022479 | -0.0072017 | 0.055104 | 0.069395 | -0.0067466 | -0.015927 | 0.0024222 | 0.075638 | 0.0045474 | 0.068995 | 0.068 | -0.0063668 | 0.0056372 | -0.0072446 | -0.022888 | 63.2904 | -59.6237 | 63.6108 | -59.4635 | -59.7656 | -59.761 | 0 | 63.382 | -59.5367 | 63.588 | -59.6603 | -59.7107 | -59.7107 | -0.073242 | -0.16022 | 0.16022 | 0.086975 | -0.21057 | -0.21515 | -0.13733 | -0.14191 | 0.013733 | -0.068665 | 0.13733 | -0.10986 | -0.16022 | -0.16022 | -0.17395 | -0.17395 | 0.16022 | 123.2346 | -0.1236 | 123.1247 | 122.9141 | 122.9187 | 122.8409 | 122.9324 | -123.0743 | -122.9874 | 123.1613 | 123.1384 | 59.5276 | 59.5505
237.9531 | 123.1338 | -59.5505 | 63.4506 | 0.17507 | 0.0024113 | 0.064717 | 0.081144 | -0.012088 | -0.0073817 | -0.0050548 | -0.00065608 | 0.0056154 | 0.074336 | 0.061592 | -0.0020938 | 0.0002962 | 0.0023694 | -0.032043 | 63.2767 | -59.6054 | 63.6429 | -59.4589 | -59.7336 | -59.7931 | -0.14191 | 63.3728 | -59.5871 | 63.5193 | -59.5963 | -59.8343 | -59.7061 | -0.054932 | -0.17395 | 0.19226 | 0.091553 | -0.24261 | -0.18311 | -0.18768 | -0.12817 | -0.036621 | -0.07782 | 0.068664 | -0.045776 | -0.15564 | -0.28381 | -0.11902 | -0.24719 | 0.14648 | 123.2483 | -0.009155 | 123.1064 | 122.8821 | 122.9599 | 122.8271 | 122.9233 | -123.056 | -123.0377 | 123.1934 | 123.0698 | 59.5184 | 59.4086
238.9531 | 123.1338 | -59.5413 | 63.4415 | 0.037738 | 0.0056153 | 0.058308 | 0.075804 | 0.0039344 | -0.018063 | -0.0029188 | -0.00065608 | -0.0050656 | 0.078608 | 0.058387 | 4.2208e-05 | 0.0088412 | -0.016858 | -0.050354 | 63.3316 | -59.6054 | 63.6246 | -59.4589 | -59.7794 | -59.697 | -0.10986 | 63.3499 | -59.5779 | 63.5513 | -59.6466 | -59.729 | -59.7382 | -0.064087 | -0.10986 | 0.18311 | 0.082398 | -0.15564 | -0.23804 | -0.091552 | -0.17395 | -0.036621 | -0.091552 | 0.10986 | -0.10528 | -0.19684 | -0.18768 | -0.16022 | -0.15106 | 0.14648 | 123.23 | -0.068664 | 123.1293 | 122.937 | 122.9279 | 122.8729 | 122.8912 | -123.0469 | -123.0194 | 123.1659 | 123.0927 | 59.491 | 59.4315
239.9531 | 123.1338 | -59.5734 | 63.4232 | 0.0072204 | 0.010956 | 0.062581 | 0.06085 | 0.014615 | 9.5287e-05 | -0.0082598 | 0.13667 | 0.010956 | 0.064723 | 0.064796 | -0.011707 | 0.0077732 | -0.010449 | -0.10529 | 63.2812 | -59.6603 | 63.6658 | -59.4543 | -59.7015 | -59.7794 | -0.2243 | 63.327 | -59.5871 | 63.4415 | -59.6146 | -59.8206 | -59.7198 | -0.086975 | -0.14191 | 0.24261 | 0.11902 | -0.20599 | -0.12817 | -0.11902 | -0.041199 | -0.013733 | -0.096131 | 0.01831 | -0.041199 | -0.14649 | -0.24719 | -0.13275 | -0.23346 | 0.20599 | 123.3261 | -0.027466 | 123.0286 | 122.9416 | 122.9141 | 122.8546 | 122.9004 | -123.0835 | -123.0103 | 123.2391 | 123.0148 | 59.4681 | 59.3491
240.9531 | 123.1247 | -59.5413 | 63.4644 | 0.19033 | 0.0034793 | 0.050831 | 0.070463 | 0.025296 | -0.010586 | 0.00028524 | 0.029861 | 0.01416 | 0.075404 | 0.055183 | -0.0095708 | 0.013113 | 0.00023236 | -0.10071 | 63.3133 | -59.5963 | 63.6108 | -59.436 | -59.7931 | -59.7519 | -0.1236 | 63.3408 | -59.5779 | 63.5834 | -59.6283 | -59.7382 | -59.7061 | -0.054931 | -0.15106 | 0.14649 | 0.10529 | -0.21057 | -0.25177 | -0.15564 | -0.19684 | -0.036621 | -0.1236 | 0.11902 | -0.086975 | -0.16479 | -0.19684 | -0.12817 | -0.16022 | 0.16022 | 123.2071 | -0.050354 | 123.1613 | 122.9095 | 122.9187 | 122.8546 | 122.8821 | -123.0606 | -123.0423 | 123.1522 | 123.1247 | 59.4406 | 59.4177
241.9531 | 123.1338 | -59.5688 | 63.4369 | 0.22084 | -0.00079271 | 0.058308 | 0.06085 | 0.00072943 | 9.5287e-05 | -0.0018508 | 0.04512 | 0.0013434 | 0.063655 | 0.035957 | -0.0031618 | 0.0099092 | 0.0023694 | -0.13733 | 63.3133 | -59.6237 | 63.6887 | -59.4315 | -59.7198 | -59.7977 | -0.23346 | 63.3453 | -59.61 | 63.4918 | -59.6832 | -59.8206 | -59.7336 | -0.054931 | -0.1236 | 0.25177 | 0.13733 | -0.22888 | -0.15106 | -0.17395 | -0.096131 | -0.041198 | -0.091553 | 0.054931 | -0.11444 | -0.16479 | -0.25177 | -0.1236 | -0.21057 | 0.19226 | 123.3124 | -0.073243 | 123.1018 | 122.937 | 122.9553 | 122.8821 | 122.9141 | -123.0606 | -123.0469 | 123.2574 | 123.0606 | 59.4315 | 59.3353
242.9531 | 123.1613 | -59.5322 | 63.4506 | 0.14455 | 0.0066833 | 0.065785 | 0.068327 | -0.01102 | -0.0020407 | -0.0071918 | 0.060379 | 0.0066834 | 0.065791 | 0.049842 | -0.0063668 | 0.010977 | 0.0098454 | -0.059509 | 63.3408 | -59.6054 | 63.5742 | -59.3719 | -59.8206 | -59.7748 | -0.10071 | 63.3591 | -59.5413 | 63.5788 | -59.6375 | -59.7473 | -59.6695 | -0.073242 | -0.10986 | 0.1236 | 0.16022 | -0.24261 | -0.28839 | -0.16937 | -0.21515 | -0.009155 | -0.091553 | 0.12817 | -0.10529 | -0.13733 | -0.21515 | -0.12817 | -0.20599 | 0.23346 | 123.1796 | -0.09613 | 123.1201 | 122.9462 | 122.9004 | 122.8729 | 122.8912 | -123.056 | -122.9919 | 123.1064 | 123.111 | 59.4727 | 59.4315
243.9531 | 123.1384 | -59.5779 | 63.4415 | 0.11403 | 0.013092 | 0.051899 | 0.071531 | 0.022092 | -0.018063 | -0.0050548 | 0.38081 | 0.015228 | 0.066859 | 0.051979 | -0.0031618 | 0.0088412 | 0.0087774 | -0.27466 | 63.2355 | -59.6008 | 63.6932 | -59.3719 | -59.6924 | -59.7656 | -0.21973 | 63.3591 | -59.5917 | 63.5147 | -59.7107 | -59.8068 | -59.7519 | -0.022888 | -0.20599 | 0.25177 | 0.20599 | -0.18768 | -0.11444 | -0.16479 | -0.091553 | -0.013733 | -0.082397 | 0.073242 | -0.13275 | -0.17395 | -0.22888 | -0.16022 | -0.21515 | 0.22888 | 123.2941 | -0.11902 | 123.1064 | 122.8363 | 122.9507 | 122.8134 | 122.937 | -123.0423 | -123.0331 | 123.2712 | 123.0927 | 59.3033 | 59.3582
244.9531 | 123.111 | -59.5779 | 63.446 | 0.12929 | -0.0018617 | 0.051899 | 0.066191 | 0.010342 | -0.018063 | -0.012532 | 0.04512 | -0.0018616 | 0.0722 | 0.057319 | -0.0052988 | 0.012045 | 0.0066414 | -0.13275 | 63.2996 | -59.6008 | 63.6108 | -59.3857 | -59.7336 | -59.7244 | -0.27924 | 63.3636 | -59.5917 | 63.5056 | -59.7198 | -59.8526 | -59.7336 | -0.022888 | -0.14648 | 0.1648 | 0.19226 | -0.14648 | -0.15564 | -0.1236 | -0.13275 | -0.013733 | -0.082398 | 0.059509 | -0.14191 | -0.15564 | -0.27466 | -0.14191 | -0.26093 | 0.21515 | 123.2117 | -0.12817 | 123.0972 | 122.9004 | 122.9553 | 122.8775 | 122.9416 | -123.0469 | -123.0377 | 123.1888 | 123.0835 | 59.4452 | 59.2987
245.9531 | 123.0881 | -59.5642 | 63.446 | 0.083514 | -0.0050657 | 0.066853 | 0.067259 | 0.010342 | -0.016995 | -0.0071918 | -0.031174 | 0.0034794 | 0.06045 | 0.064796 | 0.0043152 | 0.01525 | 0.0045054 | -0.10071 | 63.2904 | -59.6146 | 63.6841 | -59.4681 | -59.7244 | -59.7427 | -0.22888 | 63.3591 | -59.5917 | 63.4918 | -59.761 | -59.8068 | -59.7565 | -0.050354 | -0.15564 | 0.23804 | 0.09613 | -0.17853 | -0.16022 | -0.12817 | -0.10986 | -0.027466 | -0.086975 | 0.045776 | -0.19684 | -0.19226 | -0.24262 | -0.16479 | -0.21515 | 0.14648 | 123.2986 | -0.16937 | 123.0835 | 122.905 | 122.9507 | 122.8546 | 122.9233 | -123.0606 | -123.0377 | 123.2483 | 123.056 | 59.4635 | 59.3353
246.9531 | 123.1247 | -59.5505 | 63.4598 | 0.068255 | 0.0024113 | 0.060444 | 0.065123 | 0.0071384 | -0.013791 | -0.0082598 | 0.04512 | 0.0088204 | 0.064723 | 0.056251 | -0.013843 | 0.012045 | 0.0023694 | -0.068665 | 63.3224 | -59.5871 | 63.6017 | -59.4452 | -59.7656 | -59.7519 | -0.19684 | 63.3499 | -59.5551 | 63.5101 | -59.6054 | -59.7748 | -59.6741 | -0.036621 | -0.13733 | 0.14191 | 0.10529 | -0.20142 | -0.21515 | -0.16479 | -0.17853 | -0.004578 | -0.10986 | 0.050354 | -0.054932 | -0.1236 | -0.2243 | -0.11902 | -0.21973 | 0.14191 | 123.1888 | -0.050354 | 123.0652 | 122.9095 | 122.905 | 122.8729 | 122.9004 | -123.0469 | -123.0148 | 123.1522 | 123.0606 | 59.4818 | 59.3536
247.9531 | 123.0743 | -59.5596 | 63.4598 | 0.11403 | -0.0082697 | 0.054036 | 0.070463 | 0.0082064 | 0.010776 | 0.010966 | 0.060379 | 0.013092 | 0.068995 | 0.071205 | 4.2208e-05 | 0.0077732 | 0.010913 | -0.11902 | 63.3041 | -59.5871 | 63.6658 | -59.4177 | -59.7473 | -59.7244 | -0.26093 | 63.3453 | -59.5871 | 63.4918 | -59.6832 | -59.7839 | -59.8022 | -0.027466 | -0.15564 | 0.20599 | 0.14191 | -0.16479 | -0.18768 | -0.13733 | -0.16022 | -0.027466 | -0.11444 | 0.032043 | -0.1236 | -0.24261 | -0.2243 | -0.21515 | -0.19684 | 0.16937 | 123.2529 | -0.096131 | 123.0789 | 122.8912 | 122.9324 | 122.8638 | 122.905 | -123.0469 | -123.0469 | 123.2254 | 123.0515 | 59.4406 | 59.2987
248.9531 | 123.1522 | -59.5688 | 63.4506 | 0.068255 | 0.016296 | 0.062581 | 0.069395 | 0.00072943 | -0.019131 | -0.012532 | 0.13667 | 0.010956 | 0.075404 | 0.04557 | -0.010639 | 0.022726 | -0.0029716 | -0.10529 | 63.2812 | -59.61 | 63.6612 | -59.4315 | -59.7107 | -59.7382 | -0.25635 | 63.3682 | -59.5642 | 63.4827 | -59.6558 | -59.8114 | -59.7244 | -0.041198 | -0.16937 | 0.21057 | 0.13733 | -0.16937 | -0.14191 | -0.12817 | -0.10071 | 0.004578 | -0.082398 | 0.032043 | -0.086975 | -0.15564 | -0.24261 | -0.16022 | -0.24719 | 0.17853 | 123.2712 | -0.091553 | 123.0469 | 122.8912 | 122.9324 | 122.85 | 122.937 | -123.0606 | -123.0148 | 123.23 | 123.0515 | 59.4635 | 59.3124
249.9531 | 123.1659 | -59.5367 | 63.414 | 0.068255 | -0.0082697 | 0.060444 | 0.069395 | 0.00072943 | -0.02554 | 0.0066942 | 0.42659 | 0.0024114 | 0.082881 | 0.059455 | -0.0063668 | 0.014181 | 0.0045054 | -0.17395 | 63.2675 | -59.5963 | 63.5788 | -59.4772 | -59.8297 | -59.7931 | -0.21057 | 63.3499 | -59.5596 | 63.5605 | -59.6008 | -59.6786 | -59.642 | -0.059509 | -0.14648 | 0.16479 | 0.059509 | -0.25635 | -0.29297 | -0.19684 | -0.23346 | -0.022888 | -0.064086 | 0.14648 | -0.064087 | -0.10529 | -0.14191 | -0.082398 | -0.11902 | 0.11902 | 123.175 | -0.041199 | 123.1201 | 122.8638 | 122.9095 | 122.8043 | 122.8867 | -123.0103 | -122.9736 | 123.1155 | 123.0972 | 59.3628 | 59.3262
250.9531 | 123.1659 | -59.5459 | 63.4186 | 0.0072204 | 0.0077523 | 0.055104 | 0.081144 | -0.0035426 | 0.015048 | -0.012532 | 0.04512 | 0.0066834 | 0.051905 | 0.069068 | -0.014912 | 0.0035002 | 0.0013004 | -0.018311 | 63.2904 | -59.6008 | 63.6795 | -59.4955 | -59.7473 | -59.7839 | -0.19226 | 63.3591 | -59.5779 | 63.5376 | -59.5917 | -59.7519 | -59.6466 | -0.054932 | -0.12817 | 0.26093 | 0.050354 | -0.23804 | -0.20142 | -0.18311 | -0.14648 | -0.032044 | -0.059509 | 0.11902 | -0.045777 | -0.10071 | -0.20599 | -0.068664 | -0.17395 | 0.10529 | 123.2803 | -0.013733 | 123.1155 | 122.8912 | 122.937 | 122.8363 | 122.905 | -123.0194 | -122.9965 | 123.2254 | 123.0835 | 59.5276 | 59.3536
251.9531 | 123.1201 | -59.5642 | 63.4415 | 0.26662 | -0.00079271 | 0.056172 | 0.067259 | -0.00033857 | -0.0073817 | 0.0034902 | 0.04512 | 0.0002754 | 0.085017 | 0.056251 | -0.0085028 | 0.0067052 | 0.0045054 | -0.23346 | 63.3087 | -59.6146 | 63.6566 | -59.3811 | -59.7839 | -59.7153 | -0.30212 | 63.3545 | -59.5917 | 63.5239 | -59.7336 | -59.8022 | -59.7427 | -0.050354 | -0.13275 | 0.21515 | 0.1831 | -0.15106 | -0.21973 | -0.10071 | -0.16937 | -0.027466 | -0.086975 | 0.082398 | -0.16937 | -0.17853 | -0.23804 | -0.15106 | -0.21057 | 0.23346 | 123.2712 | -0.14191 | 123.1155 | 122.9233 | 122.9462 | 122.8729 | 122.9187 | -123.056 | -123.0331 | 123.2208 | 123.0881 | 59.3307 | 59.2621
252.9531 | 123.1659 | -59.523 | 63.4735 | 0.037738 | -0.0061337 | 0.063649 | 0.069395 | 0.0082064 | -0.00097271 | 0.0056262 | 0.029861 | 0.0098884 | 0.064723 | 0.072273 | -0.0010258 | 0.0099092 | -0.013653 | -0.068665 | 63.3133 | -59.6329 | 63.6795 | -59.5001 | -59.729 | -59.761 | -0.22888 | 63.3453 | -59.5505 | 63.4918 | -59.6146 | -59.8114 | -59.6558 | -0.10986 | -0.16022 | 0.20599 | 0.022888 | -0.23804 | -0.20599 | -0.12817 | -0.09613 | -0.027466 | -0.12817 | 0.01831 | -0.091553 | -0.13275 | -0.28839 | -0.10529 | -0.26092 | 0.13275 | 123.3124 | -0.064087 | 123.0423 | 122.9462 | 122.8958 | 122.8363 | 122.8683 | -123.1064 | -123.024 | 123.2025 | 123.0148 | 59.4543 | 59.2941
253.9531 | 123.0927 | -59.5688 | 63.4552 | 0.083514 | -0.0018617 | 0.060444 | 0.073668 | 0.015683 | -0.015927 | -0.00078276 | 0.060379 | 0.0066834 | 0.062587 | 0.046638 | -0.0052988 | 0.0099092 | -0.015789 | -0.17395 | 63.3224 | -59.6146 | 63.6292 | -59.3903 | -59.7198 | -59.7107 | -0.32959 | 63.3545 | -59.5825 | 63.4689 | -59.729 | -59.8206 | -59.7519 | -0.045776 | -0.13275 | 0.17395 | 0.17853 | -0.14191 | -0.15106 | -0.09613 | -0.10529 | -0.013733 | -0.10071 | 0.013733 | -0.16022 | -0.1831 | -0.25177 | -0.16937 | -0.23804 | 0.2243 | 123.2437 | -0.14648 | 123.0515 | 122.937 | 122.937 | 122.8912 | 122.9233 | -123.0698 | -123.0377 | 123.1979 | 123.0377 | 59.3948 | 59.2392
254.9688 | 123.2758 | -59.4955 | 63.4415 | 0.12929 | -0.00079271 | 0.051899 | 0.071531 | 0.0028664 | -0.013791 | -0.00078276 | 0.274 | -0.0039976 | 0.086085 | -0.0014268 | -0.012775 | 0.01525 | 0.00023236 | -0.054932 | 63.295 | -59.5596 | 63.5468 | -59.5963 | -59.8251 | -59.8984 | -0.068665 | 63.3408 | -59.5276 | 63.4003 | -59.4543 | -59.697 | -59.6878 | -0.064087 | -0.14648 | 0.10529 | -0.10071 | -0.40283 | -0.32959 | -0.33874 | -0.2655 | -0.032044 | -0.10071 | -0.041198 | 0.041198 | -0.19226 | -0.20142 | -0.16022 | -0.16937 | -0.036621 | 123.1064 | 0.073242 | 122.9279 | 122.8546 | 122.8683 | 122.7905 | 122.8363 | -123.0011 | -122.9691 | 123.0423 | 122.8958 | 59.4406 | 59.4269
255.9531 | 123.1064 | -59.5459 | 63.4369 | 0.052997 | 0.012024 | 0.065785 | 0.067259 | 0.0060704 | -0.0020407 | -0.0029188 | -0.44316 | -0.0018616 | 0.082881 | 0.070137 | -0.0095708 | 0.014181 | -0.0019036 | -0.21515 | 63.3224 | -59.6329 | 63.6475 | -59.3491 | -59.7382 | -59.7153 | -0.082397 | 63.3774 | -59.5505 | 63.5696 | -59.7015 | -59.8389 | -59.7244 | -0.086976 | -0.11444 | 0.21057 | 0.19684 | -0.16937 | -0.19226 | -0.082397 | -0.10529 | -0.004578 | -0.05951 | 0.13275 | -0.15564 | -0.17853 | -0.29297 | -0.17395 | -0.28839 | 0.28381 | 123.2803 | -0.15106 | 123.1201 | 122.9553 | 122.9279 | 122.8683 | 122.9233 | -123.0698 | -122.9874 | 123.1934 | 123.1155 | 59.3307 | 59.4635
257.0312 | 123.2483 | -59.523 | 63.4186 | 0.052997 | -0.0029297 | 0.055104 | 0.067259 | -0.00033857 | -0.016995 | -0.0136 | 0.24348 | 0.0002754 | 0.062587 | 0.053047 | 0.0085872 | 0.0088412 | -0.0083126 | -0.15564 | 63.2858 | -59.5917 | 63.5376 | -59.5093 | -59.8526 | -59.8389 | -0.16479 | 63.3179 | -59.523 | 63.652 | -59.5322 | -59.6283 | -59.6146 | -0.068665 | -0.13275 | 0.11902 | 0.013733 | -0.31586 | -0.32959 | -0.24719 | -0.26093 | 0 | -0.10071 | 0.23346 | -0.009156 | -0.091553 | -0.10529 | -0.091553 | -0.10529 | 0.082398 | 123.1293 | -0.009156 | 123.175 | 122.8775 | 122.8409 | 122.8088 | 122.8409 | -123.0103 | -122.9416 | 123.0606 | 123.175 | 59.3674 | 59.3582
257.9531 | 123.111 | -59.5322 | 63.4598 | 0.083514 | 0.0024113 | 0.058308 | 0.089689 | 0.0071384 | 0.0097083 | -0.0093278 | -0.046432 | 0.013092 | 0.062587 | 0.055183 | -0.0052988 | 0.019522 | 0.0077094 | -0.12817 | 63.2996 | -59.6237 | 63.6612 | -59.4589 | -59.761 | -59.7656 | -0.28839 | 63.3636 | -59.5779 | 63.5193 | -59.6466 | -59.848 | -59.6649 | -0.091552 | -0.16022 | 0.20142 | 0.073243 | -0.23346 | -0.22888 | -0.14191 | -0.13733 | -0.045776 | -0.096131 | 0.059509 | -0.11444 | -0.13275 | -0.31586 | -0.086975 | -0.27008 | 0.16479 | 123.2849 | -0.068664 | 123.0972 | 122.9233 | 122.9416 | 122.8317 | 122.8958 | -123.0835 | -123.0377 | 123.1934 | 123.0515 | 59.404 | 59.2438
258.9531 | 123.1567 | -59.5276 | 63.4644 | 0.12929 | 0.0088203 | 0.060444 | 0.079008 | -0.022769 | 0.0065043 | -0.0136 | 0.029861 | 0.0045474 | 0.064723 | 0.04557 | -0.0095708 | 0.0099092 | 0.014118 | -0.15564 | 63.3316 | -59.5825 | 63.6795 | -59.4452 | -59.7702 | -59.7473 | -0.25177 | 63.3453 | -59.5825 | 63.533 | -59.6603 | -59.761 | -59.7656 | -0.054932 | -0.13275 | 0.21515 | 0.082398 | -0.21973 | -0.24262 | -0.16479 | -0.18768 | -0.054932 | -0.11902 | 0.068665 | -0.13275 | -0.23804 | -0.23346 | -0.1831 | -0.17853 | 0.13733 | 123.262 | -0.077819 | 123.1155 | 122.9141 | 122.9279 | 122.8592 | 122.8729 | -123.0469 | -123.0469 | 123.2071 | 123.0606 | 59.3719 | 59.2758
259.9688 | 123.1293 | -59.5413 | 63.4827 | -0.053815 | 0.0077523 | 0.052968 | 0.064055 | 0.0071384 | 0.017185 | 0.00028524 | 0.18245 | -0.0072016 | 0.067927 | 0.040229 | 0.0043152 | 0.01525 | -0.016858 | -0.073242 | 63.327 | -59.5779 | 63.6108 | -59.4955 | -59.7336 | -59.8251 | -0.2243 | 63.382 | -59.5505 | 63.4964 | -59.5322 | -59.7015 | -59.642 | -0.036621 | -0.15564 | 0.12817 | 0.045777 | -0.28381 | -0.19226 | -0.24719 | -0.15564 | -0.009155 | -0.10071 | 0.013733 | 0.009155 | -0.10071 | -0.16022 | -0.091553 | -0.15106 | 0.082398 | 123.1888 | 0.01831 | 123.0469 | 122.905 | 122.9324 | 122.8683 | 122.9233 | -123.0606 | -123.0331 | 123.1522 | 123.0377 | 59.4681 | 59.317
261.0312 | 123.1842 | -59.5551 | 63.4048 | 0.0072204 | 0.0013433 | 0.062581 | 0.086485 | 0.0028664 | 0.0097083 | -0.0039868 | 0.060379 | 0.0077514 | 0.074336 | 0.071205 | -0.0052988 | 0.0088412 | 0.0066414 | -0.17395 | 63.2584 | -59.5871 | 63.5056 | -59.5596 | -59.8801 | -59.8343 | -0.22888 | 63.2767 | -59.5642 | 63.5788 | -59.5688 | -59.697 | -59.6191 | -0.032043 | -0.14648 | 0.10071 | -0.004577 | -0.27924 | -0.32501 | -0.24719 | -0.29297 | -0.009155 | -0.12817 | 0.17395 | -0.013733 | -0.064087 | -0.14191 | -0.054932 | -0.13275 | 0.027466 | 123.0927 | -0.004578 | 123.143 | 122.8455 | 122.8409 | 122.8134 | 122.8317 | -122.9919 | -122.9691 | 123.0606 | 123.1338 | 59.3811 | 59.3262
261.9531 | 123.2437 | -59.5139 | 63.4003 | 0.083514 | -0.0050657 | 0.071125 | 0.066191 | 0.00072943 | -0.0095177 | 0.0034902 | 0.13667 | -0.0050656 | 0.071131 | 0.030616 | -0.011707 | 0.0088412 | -0.0083126 | -0.10529 | 63.2767 | -59.6146 | 63.501 | -59.5917 | -59.8343 | -59.8846 | -0.27924 | 63.3133 | -59.5642 | 63.5468 | -59.5047 | -59.7061 | -59.6054 | -0.10071 | -0.1236 | 0.10071 | -0.07782 | -0.37079 | -0.32044 | -0.27008 | -0.21973 | -0.050354 | -0.086976 | 0.14648 | 0.009155 | -0.091553 | -0.19226 | -0.041199 | -0.14191 | 0.022888 | 123.1155 | 0.059509 | 123.111 | 122.8912 | 122.8775 | 122.7905 | 122.8271 | -123.0148 | -122.9645 | 123.0148 | 123.0606 | 59.4086 | 59.2346
263.0312 | 123.2208 | -59.523 | 63.4369 | 0.037738 | 0.0013433 | 0.062581 | 0.074736 | 0.0028664 | 0.011844 | -0.0050548 | 0.15193 | 0.0024114 | 0.057246 | 0.031684 | 0.011791 | 0.0056372 | -0.00083564 | -0.17395 | 63.2629 | -59.5779 | 63.4506 | -59.5734 | -59.8572 | -59.8709 | -0.29297 | 63.3179 | -59.5505 | 63.5834 | -59.5505 | -59.7107 | -59.6008 | -0.054932 | -0.17395 | 0.013733 | -0.050354 | -0.3479 | -0.33417 | -0.29297 | -0.27924 | -0.027466 | -0.11902 | 0.14648 | -0.027466 | -0.07782 | -0.18768 | -0.050354 | -0.16022 | 0.004578 | 123.0286 | 0 | 123.1338 | 122.8409 | 122.8683 | 122.7859 | 122.8409 | -123.0148 | -122.9874 | 122.9736 | 123.1064 | 59.3491 | 59.23
263.9531 | 123.1155 | -59.5413 | 63.446 | 0.037738 | 0.0077523 | 0.055104 | 0.082213 | -0.016361 | -0.019131 | -0.014668 | -0.00065608 | 0.0098884 | 0.070063 | 0.047706 | -0.0085028 | 0.0045682 | 0.0013004 | -0.19226 | 63.2996 | -59.6237 | 63.6887 | -59.4177 | -59.697 | -59.7656 | -0.39368 | 63.3545 | -59.5596 | 63.4827 | -59.6878 | -59.8709 | -59.729 | -0.082397 | -0.14648 | 0.24262 | 0.1236 | -0.2243 | -0.15564 | -0.14191 | -0.073242 | -0.01831 | -0.091553 | 0.036621 | -0.14648 | -0.18768 | -0.32959 | -0.16937 | -0.31128 | 0.20599 | 123.3124 | -0.12817 | 123.0423 | 122.9233 | 122.9141 | 122.8409 | 122.8958 | -123.0698 | -123.0057 | 123.23 | 123.024 | 59.3491 | 59.1476
265.0312 | 123.111 | -59.5596 | 63.4872 | 0.25136 | 0.00027529 | 0.046559 | 0.068327 | 0.0017974 | -0.013791 | 0.013103 | -0.046432 | -0.0061336 | 0.068995 | 0.05091 | 4.2208e-05 | 0.012045 | -0.012585 | -0.15106 | 63.3682 | -59.5917 | 63.7299 | -59.4131 | -59.7061 | -59.6558 | -0.32501 | 63.3774 | -59.5459 | 63.5147 | -59.6191 | -59.7931 | -59.7061 | -0.032044 | -0.11902 | 0.24261 | 0.14648 | -0.096131 | -0.14648 | -0.064087 | -0.11444 | 0.013733 | -0.10986 | 0.027465 | -0.05951 | -0.14648 | -0.23346 | -0.16022 | -0.24719 | 0.17853 | 123.3215 | -0.073243 | 123.0606 | 122.9599 | 122.9233 | 122.9279 | 122.937 | -123.0789 | -123.0331 | 123.2895 | 123.0743 | 59.4086 | 59.2346
265.9531 | 123.1155 | -59.5322 | 63.4369 | 0.083514 | 0.0013433 | 0.050831 | 0.074736 | 0.0092744 | -0.0084497 | -0.0029188 | -0.061691 | 0.010956 | 0.092494 | 0.088294 | -0.0074348 | 0.014181 | -0.012585 | -0.16937 | 63.3224 | -59.61 | 63.6703 | -59.5001 | -59.7748 | -59.7748 | -0.27008 | 63.3499 | -59.5688 | 63.5605 | -59.6008 | -59.7427 | -59.6878 | -0.077819 | -0.11444 | 0.23346 | 0.032044 | -0.24261 | -0.24261 | -0.16479 | -0.16479 | -0.036621 | -0.086975 | 0.1236 | -0.068664 | -0.15564 | -0.21057 | -0.11902 | -0.17395 | 0.10986 | 123.2803 | -0.032043 | 123.1293 | 122.9324 | 122.9187 | 122.8546 | 122.8821 | -123.0469 | -123.0057 | 123.2025 | 123.0927 | 59.3628 | 59.2621
267.0312 | 123.2071 | -59.5322 | 63.414 | 0.20559 | 0.0024113 | 0.048695 | 0.069395 | -0.015292 | -0.0020407 | 0.0077622 | 0.19771 | 0.0013434 | 0.058314 | 0.043434 | 0.0011102 | 0.0067052 | 0.0023694 | -0.20599 | 63.2767 | -59.5963 | 63.5651 | -59.5367 | -59.8068 | -59.8663 | -0.33875 | 63.327 | -59.5734 | 63.5651 | -59.5688 | -59.7107 | -59.6054 | -0.064086 | -0.13733 | 0.15106 | -0.004577 | -0.33417 | -0.27466 | -0.27008 | -0.21057 | -0.041198 | -0.086975 | 0.15106 | -0.036621 | -0.073242 | -0.17853 | -0.032044 | -0.13733 | 0.059509 | 123.1613 | 0.004577 | 123.1384 | 122.8729 | 122.9004 | 122.8088 | 122.8592 | -123.0103 | -122.9874 | 123.0972 | 123.0972 | 59.3262 | 59.1934
267.9531 | 123.1155 | -59.5459 | 63.446 | 0.022479 | -0.0018617 | 0.062581 | 0.081144 | 0.0071384 | 0.010776 | -0.022145 | 0.090897 | 0.0034794 | 0.06045 | 0.084022 | -0.0063668 | 0.014181 | -0.0061756 | -0.17395 | 63.327 | -59.6146 | 63.6612 | -59.491 | -59.7244 | -59.7519 | -0.31586 | 63.3682 | -59.5963 | 63.5422 | -59.6558 | -59.7519 | -59.7336 | -0.068665 | -0.11902 | 0.21515 | 0.054931 | -0.20599 | -0.17853 | -0.13733 | -0.10986 | -0.050354 | -0.07782 | 0.09613 | -0.10986 | -0.18768 | -0.20599 | -0.13733 | -0.15564 | 0.1236 | 123.2758 | -0.05951 | 123.1384 | 122.9416 | 122.9645 | 122.8729 | 122.9141 | -123.0606 | -123.0423 | 123.2071 | 123.0881 | 59.3719 | 59.23
269.0312 | 123.1842 | -59.5276 | 63.4277 | 0.037738 | 0.0056153 | 0.063649 | 0.070463 | 0.0082064 | 0.01398 | -0.0136 | -0.061691 | 0.01416 | 0.079676 | 0.044502 | -0.0085028 | 0.010977 | 0.020526 | -0.23346 | 63.3133 | -59.642 | 63.6795 | -59.4772 | -59.7382 | -59.7748 | -0.4303 | 63.327 | -59.5917 | 63.501 | -59.61 | -59.7702 | -59.697 | -0.11444 | -0.11444 | 0.25177 | 0.050354 | -0.24719 | -0.21057 | -0.13275 | -0.09613 | -0.064087 | -0.10071 | 0.073243 | -0.082397 | -0.16937 | -0.24262 | -0.10528 | -0.17853 | 0.16479 | 123.3215 | -0.01831 | 123.0927 | 122.9553 | 122.9187 | 122.8409 | 122.8546 | -123.0698 | -123.0194 | 123.2071 | 123.0286 | 59.2941 | 59.0973
269.9688 | 123.1842 | -59.5322 | 63.4094 | 0.068255 | 0.00027529 | 0.061512 | 0.068327 | 0.01141 | -0.028744 | 0.017375 | 0.274 | 0.0013434 | 0.074336 | 0.033821 | -0.0042298 | -0.0007718 | -0.014721 | -0.26093 | 63.2996 | -59.5871 | 63.5925 | -59.5779 | -59.7977 | -59.761 | -0.37537 | 63.3179 | -59.5734 | 63.6108 | -59.6512 | -59.697 | -59.6649 | -0.054931 | -0.10986 | 0.1831 | -0.045776 | -0.22888 | -0.2655 | -0.17395 | -0.21057 | -0.041198 | -0.091553 | 0.20142 | -0.11902 | -0.13275 | -0.16479 | -0.091553 | -0.1236 | 0.009155 | 123.1796 | -0.07782 | 123.1842 | 122.8867 | 122.8912 | 122.8317 | 122.85 | -122.9965 | -122.9828 | 123.1247 | 123.143 | 59.2712 | 59.1568
270.9531 | 123.175 | -59.5139 | 63.4598 | 0.098773 | 0.0013433 | 0.050831 | 0.080076 | -0.012088 | 0.0075723 | 0.0088302 | -0.07695 | 0.0013434 | 0.049769 | 0.07975 | -0.011707 | 0.01525 | 0.00023236 | -0.15106 | 63.3224 | -59.61 | 63.6246 | -59.4589 | -59.7794 | -59.7839 | -0.27466 | 63.3911 | -59.5642 | 63.5742 | -59.5413 | -59.7244 | -59.6283 | -0.09613 | -0.13733 | 0.16479 | 0.054932 | -0.27008 | -0.2655 | -0.17395 | -0.16937 | -0.050354 | -0.068665 | 0.11444 | -0.027466 | -0.11444 | -0.21057 | -0.064087 | -0.16022 | 0.15106 | 123.2346 | 0.022888 | 123.1384 | 122.9324 | 122.9553 | 122.8363 | 122.905 | -123.0698 | -123.024 | 123.1384 | 123.0881 | 59.3628 | 59.2392
272.0312 | 123.1888 | -59.5139 | 63.4323 | -0.023297 | -0.0018617 | 0.056172 | 0.07794 | -0.015292 | -0.024472 | 0.0077622 | 0.18245 | -0.0050656 | 0.07754 | 0.030616 | -0.0042298 | 0.0045682 | -0.010449 | -0.28839 | 63.2812 | -59.6054 | 63.5651 | -59.4955 | -59.8206 | -59.7885 | -0.38452 | 63.3224 | -59.5413 | 63.7711 | -59.7656 | -59.697 | -59.5734 | -0.091553 | -0.15106 | 0.13275 | 0.018311 | -0.27466 | -0.3067 | -0.18311 | -0.21515 | -0.027466 | -0.10986 | 0.33874 | -0.25177 | -0.059509 | -0.1831 | -0.032043 | -0.15564 | 0.10986 | 123.1705 | -0.2243 | 123.3124 | 122.8867 | 122.8638 | 122.7951 | 122.8363 | -123.0377 | -122.9736 | 123.0789 | 123.2849 | 59.2255 | 59.1293
272.9531 | 123.1659 | -59.5139 | 63.4644 | 0.11403 | 0.016296 | 0.055104 | 0.081144 | 0.0039344 | 0.0011633 | -0.0071918 | -0.00065608 | -0.0007936 | 0.080744 | 0.057319 | -0.010639 | 0.0056372 | -0.0083126 | -0.18768 | 63.3362 | -59.6191 | 63.6292 | -59.4635 | -59.7198 | -59.7519 | -0.3891 | 63.3636 | -59.5596 | 63.5193 | -59.5322 | -59.7565 | -59.6375 | -0.10529 | -0.12817 | 0.1648 | 0.050354 | -0.23804 | -0.20599 | -0.13275 | -0.10071 | -0.045776 | -0.10071 | 0.054932 | -0.018311 | -0.1236 | -0.24262 | -0.07782 | -0.19684 | 0.15564 | 123.2483 | 0.027465 | 123.0789 | 122.9553 | 122.9233 | 122.85 | 122.8775 | -123.0835 | -123.024 | 123.143 | 123.0331 | 59.3262 | 59.1248
274.0312 | 123.1796 | -59.5413 | 63.4048 | 0.14455 | 0.00027529 | 0.058308 | 0.079008 | 0.0017974 | 0.0011633 | 0.0024222 | 0.91487 | 0.0056154 | 0.075404 | 0.030616 | -0.0063668 | 0.018454 | 0.010913 | -0.27924 | 63.3041 | -59.5779 | 63.5651 | -59.4955 | -59.848 | -59.8114 | -0.54474 | 63.3224 | -59.5505 | 63.5651 | -59.5871 | -59.7702 | -59.6191 | -0.036621 | -0.10071 | 0.16022 | 0.045777 | -0.27008 | -0.3067 | -0.23346 | -0.27008 | -0.009155 | -0.082397 | 0.16022 | -0.045776 | -0.07782 | -0.22888 | -0.068665 | -0.21973 | 0.082398 | 123.143 | -0.036621 | 123.1155 | 122.8821 | 122.8729 | 122.8455 | 122.8638 | -122.9828 | -122.9553 | 123.1064 | 123.1064 | 59.2621 | 58.9966
274.9531 | 123.1247 | -59.5367 | 63.4735 | 0.022479 | 0.0034793 | 0.050831 | 0.079008 | -0.0088836 | -0.0063137 | -0.0029188 | -0.13799 | 0.0088204 | 0.091426 | 0.074409 | -0.014912 | 0.010977 | 0.00023236 | -0.27008 | 63.3316 | -59.6237 | 63.6841 | -59.4452 | -59.7107 | -59.8022 | -0.4715 | 63.3865 | -59.5779 | 63.5056 | -59.6558 | -59.8343 | -59.7015 | -0.086975 | -0.14191 | 0.21057 | 0.091553 | -0.2655 | -0.17395 | -0.17853 | -0.086975 | -0.041199 | -0.086975 | 0.032043 | -0.11902 | -0.16479 | -0.29755 | -0.1236 | -0.25635 | 0.17853 | 123.3078 | -0.07782 | 123.0835 | 122.9553 | 122.9645 | 122.8683 | 122.9233 | -123.0972 | -123.0515 | 123.2208 | 123.0423 | 59.2667 | 59.0652
276.0312 | 123.2254 | -59.5413 | 63.4048 | -0.0080386 | 0.0013433 | 0.059376 | 0.069395 | 0.015683 | 0.021457 | 0.00028524 | -0.07695 | 0.0045474 | 0.052973 | 0.066932 | -0.0010258 | 0.017386 | 0.0034374 | -0.32501 | 63.3179 | -59.6375 | 63.5834 | -59.491 | -59.8022 | -59.8389 | -0.48065 | 63.3316 | -59.5688 | 63.5925 | -59.5184 | -59.7565 | -59.5963 | -0.09613 | -0.086975 | 0.17853 | 0.050354 | -0.29755 | -0.26092 | -0.20142 | -0.16479 | -0.027466 | -0.073242 | 0.18768 | 0.022888 | -0.054931 | -0.21515 | -0.027465 | -0.18768 | 0.14648 | 123.2208 | 0.050354 | 123.1613 | 122.9553 | 122.9004 | 122.8592 | 122.8729 | -123.0423 | -122.9736 | 123.1247 | 123.1338 | 59.2163 | 59.0607
276.9531 | 123.1384 | -59.5413 | 63.4415 | 0.068255 | 0.0088203 | 0.046559 | 0.074736 | 0.01141 | -0.00097271 | 0.0056262 | -0.13799 | 0.0098884 | 0.064723 | 0.061592 | -0.013843 | 0.0045682 | 0.0098454 | -0.24719 | 63.3133 | -59.6054 | 63.6932 | -59.4589 | -59.7198 | -59.761 | -0.4303 | 63.382 | -59.5642 | 63.5193 | -59.6329 | -59.7794 | -59.697 | -0.064087 | -0.12817 | 0.25177 | 0.082398 | -0.21973 | -0.17853 | -0.15564 | -0.11444 | -0.022888 | -0.059509 | 0.07782 | -0.091553 | -0.15564 | -0.23804 | -0.13275 | -0.21515 | 0.14648 | 123.2986 | -0.068665 | 123.0835 | 122.9187 | 122.9462 | 122.8546 | 122.9233 | -123.0469 | -123.0057 | 123.2346 | 123.0606 | 59.2941 | 59.111
278.0312 | 123.1705 | -59.5596 | 63.4186 | 0.11403 | 0.0045473 | 0.047627 | 0.067259 | -0.0035426 | -0.013791 | -0.010396 | -0.061691 | 0.0077514 | 0.073268 | 0.042366 | -0.0052988 | 0.018454 | 0.0023694 | -0.34332 | 63.3179 | -59.6329 | 63.6429 | -59.4635 | -59.7427 | -59.7977 | -0.54474 | 63.3728 | -59.5871 | 63.533 | -59.6054 | -59.7748 | -59.642 | -0.073243 | -0.10071 | 0.2243 | 0.09613 | -0.23804 | -0.18311 | -0.16479 | -0.10986 | -0.027466 | -0.045776 | 0.11444 | -0.045777 | -0.082398 | -0.21515 | -0.054932 | -0.18768 | 0.16937 | 123.2758 | -0.018311 | 123.1201 | 122.9507 | 122.9599 | 122.8775 | 122.9324 | -123.0515 | -123.0057 | 123.2025 | 123.0927 | 59.2163 | 59.0149
278.9531 | 123.143 | -59.523 | 63.4872 | 0.083514 | 0.0013433 | 0.059376 | 0.064055 | -0.0088836 | -0.00097271 | 0.0045582 | 0.04512 | 0.0056154 | 0.048701 | 0.024208 | -0.012775 | 0.0045682 | -0.00083564 | -0.27924 | 63.4048 | -59.6054 | 63.7115 | -59.4223 | -59.6649 | -59.6924 | -0.46234 | 63.4048 | -59.5596 | 63.5376 | -59.6054 | -59.7107 | -59.6832 | -0.082398 | -0.082398 | 0.2243 | 0.10071 | -0.16937 | -0.14191 | -0.086975 | -0.059509 | -0.036621 | -0.082398 | 0.050354 | -0.082398 | -0.16022 | -0.18768 | -0.1236 | -0.15106 | 0.18311 | 123.317 | -0.045777 | 123.0972 | 123.0103 | 122.9645 | 122.9279 | 122.9279 | -123.0927 | -123.0469 | 123.2346 | 123.0606 | 59.2438 | 59.0607
280.0312 | 123.2346 | -59.491 | 63.4277 | 0.022479 | -0.00079271 | 0.05724 | 0.071531 | -0.0078156 | 0.011844 | -0.0039868 | 0.18245 | -0.0082696 | 0.071131 | 0.013526 | -0.013843 | 0.0099092 | -0.014721 | -0.27008 | 63.2812 | -59.5963 | 63.5742 | -59.5596 | -59.8251 | -59.8892 | -0.36621 | 63.327 | -59.5322 | 63.6154 | -59.4635 | -59.6375 | -59.5688 | -0.10529 | -0.14648 | 0.14648 | -0.068664 | -0.39825 | -0.33417 | -0.29297 | -0.22888 | -0.041199 | -0.10071 | 0.18768 | 0.027466 | -0.07782 | -0.14648 | -0.036621 | -0.10529 | 0.036621 | 123.1705 | 0.068665 | 123.1476 | 122.8775 | 122.8592 | 122.7722 | 122.818 | -123.024 | -122.9599 | 123.0652 | 123.1064 | 59.2209 | 59.1248
280.9531 | 123.1613 | -59.5093 | 63.4872 | 0.083514 | 0.00027529 | 0.060444 | 0.07794 | 0.0050024 | 0.0011633 | 0.0024222 | 0.12141 | 0.015228 | 0.048701 | 0.024208 | -0.020252 | 0.013113 | -0.032879 | -0.3067 | 63.3224 | -59.6008 | 63.6429 | -59.4269 | -59.7565 | -59.7702 | -0.42114 | 63.3774 | -59.5642 | 63.6108 | -59.5871 | -59.6741 | -59.7061 | -0.091553 | -0.16479 | 0.15564 | 0.082397 | -0.26093 | -0.24719 | -0.16937 | -0.15564 | -0.054932 | -0.10986 | 0.1236 | -0.07782 | -0.19684 | -0.1648 | -0.14191 | -0.10986 | 0.17395 | 123.2437 | -0.022888 | 123.175 | 122.9233 | 122.9416 | 122.8317 | 122.8867 | -123.0881 | -123.0515 | 123.1522 | 123.1201 | 59.2026 | 59.0881
282.0312 | 123.1064 | -59.5505 | 63.4369 | -0.069074 | -0.011475 | 0.060444 | 0.069395 | -0.0014066 | -0.016995 | -0.0082598 | 0.014603 | 0.0056154 | 0.0722 | 0.072273 | -0.0010258 | 0.012045 | -0.0019036 | -0.68207 | 63.2492 | -59.6878 | 63.6475 | -59.4315 | -59.6237 | -59.7885 | -0.6134 | 63.3499 | -59.61 | 63.501 | -59.6512 | -59.8114 | -59.7336 | -0.13733 | -0.18768 | 0.21057 | 0.11902 | -0.23804 | -0.073242 | -0.10071 | 0.064087 | -0.059509 | -0.086975 | 0.064087 | -0.10071 | -0.18311 | -0.26092 | -0.1236 | -0.20142 | 0.25635 | 123.3353 | -0.041199 | 123.111 | 122.937 | 122.9599 | 122.7997 | 122.9004 | -123.1247 | -123.0469 | 123.1979 | 123.0515 | 58.8684 | 58.9371
282.9531 | 123.1201 | -59.523 | 63.4735 | 0.38869 | -0.0082697 | 0.056172 | 0.074736 | 0.016751 | -0.0041777 | 0.0024222 | 0.029861 | 0.0066834 | 0.078608 | 0.014595 | 0.0085872 | 0.0099092 | -0.0029716 | -0.37079 | 63.4186 | -59.5551 | 63.707 | -59.3719 | -59.7198 | -59.6375 | -0.51727 | 63.4094 | -59.5551 | 63.5696 | -59.6512 | -59.7153 | -59.6878 | -0.032044 | -0.054932 | 0.23346 | 0.15106 | -0.11444 | -0.19684 | -0.082397 | -0.1648 | -0.032044 | -0.064087 | 0.09613 | -0.12817 | -0.16479 | -0.19226 | -0.13275 | -0.16022 | 0.18311 | 123.262 | -0.09613 | 123.1247 | 122.9736 | 122.9645 | 122.9416 | 122.9324 | -123.0286 | -123.0286 | 123.23 | 123.0927 | 59.1522 | 59.0057
283.9531 | 123.1247 | -59.5184 | 63.501 | 0.12929 | -0.0039977 | 0.048695 | 0.0726 | -0.00033857 | -0.0020407 | -0.021077 | 0.15193 | 0.0098884 | 0.06045 | 0.066932 | -0.0085028 | 0.0013642 | -0.0061756 | -0.32501 | 63.3636 | -59.6054 | 63.7024 | -59.3994 | -59.6603 | -59.7198 | -0.58594 | 63.3957 | -59.5779 | 63.501 | -59.5459 | -59.7382 | -59.6603 | -0.086975 | -0.13733 | 0.20142 | 0.11902 | -0.20142 | -0.14191 | -0.11444 | -0.054931 | -0.059509 | -0.10529 | 0 | -0.027465 | -0.14191 | -0.21973 | -0.082397 | -0.16022 | 0.20599 | 123.3078 | 0.032044 | 123.0789 | 122.9691 | 122.9736 | 122.8821 | 122.9141 | -123.1064 | -123.0789 | 123.2208 | 123.0194 | 59.1934 | 58.9325
285.0312 | 123.1247 | -59.5642 | 63.4872 | 0.12929 | -0.0018617 | 0.064717 | 0.081144 | -0.00033857 | -0.021267 | 0.0098982 | -0.15324 | 0.0098884 | 0.071131 | 0.066932 | 0.0021782 | 0.0035002 | 0.011982 | -0.43488 | 63.3133 | -59.61 | 63.6429 | -59.3353 | -59.7153 | -59.7061 | -0.74616 | 63.3499 | -59.6054 | 63.5468 | -60.0449 | -59.697 | -59.4681 | -0.045776 | -0.17395 | 0.15564 | 0.22888 | -0.14191 | -0.15106 | -0.096131 | -0.10529 | -0.041199 | -0.13733 | 0.059509 | -0.48065 | 0.09613 | -0.13275 | 0.13733 | -0.091552 | 0.27466 | 123.2529 | -0.43945 | 123.1522 | 122.9233 | 122.9553 | 122.8775 | 122.9141 | -123.0972 | -123.0927 | 123.2071 | 123.111 | 59.1293 | 58.8181
285.9531 | 123.175 | -59.523 | 63.4964 | 0.12929 | 0.0056153 | 0.048695 | 0.079008 | 0.01141 | 0.0022313 | -0.010396 | 0.04512 | 0.0024114 | 0.061518 | 0.068 | -0.0063668 | 0.016318 | 0.01305 | -0.33875 | 63.3545 | -59.5871 | 63.6795 | -59.3994 | -59.6924 | -59.7656 | -0.54932 | 63.3957 | -59.5459 | 63.5651 | -59.5596 | -59.7565 | -59.6283 | -0.064087 | -0.14191 | 0.18311 | 0.1236 | -0.24262 | -0.16937 | -0.17853 | -0.10529 | -0.022888 | -0.10071 | 0.068664 | -0.036621 | -0.10529 | -0.23346 | -0.082398 | -0.21057 | 0.18768 | 123.2666 | -0.013733 | 123.111 | 122.9416 | 122.9416 | 122.8775 | 122.9187 | -123.0835 | -123.0423 | 123.2025 | 123.0881 | 59.1843 | 58.9737
287.0312 | 123.2071 | -59.5551 | 63.3545 | 0.068255 | 0.0056153 | 0.060444 | 0.073668 | -0.0078156 | -0.028744 | -0.0061228 | 0.090897 | -0.0029296 | 0.051905 | 0.037025 | -0.011707 | 0.0099092 | -0.011517 | -0.43488 | 63.2904 | -59.5779 | 63.5376 | -59.5322 | -59.8297 | -59.9075 | -0.58136 | 63.3133 | -59.5505 | 63.6108 | -59.491 | -59.7382 | -59.5963 | -0.022888 | -0.064087 | 0.18311 | 0.022888 | -0.35248 | -0.27466 | -0.32959 | -0.25177 | 0.004578 | -0.041199 | 0.25635 | 0.064087 | -0.041198 | -0.18311 | -0.045776 | -0.18768 | 0.045776 | 123.1155 | 0.059509 | 123.1613 | 122.8683 | 122.8638 | 122.8455 | 122.8683 | -122.9324 | -122.905 | 123.0927 | 123.1659 | 59.1202 | 58.9737
287.9531 | 123.1567 | -59.5413 | 63.4506 | 0.0072204 | -0.00079271 | 0.051899 | 0.083281 | -0.0024746 | -0.0031087 | 0.00028524 | -0.10747 | 0.0077514 | 0.081813 | 0.037025 | -0.0095708 | 0.014181 | -0.010449 | -0.35248 | 63.3591 | -59.5917 | 63.6978 | -59.4727 | -59.7519 | -59.7519 | -0.50812 | 63.3957 | -59.5505 | 63.5971 | -59.7885 | -59.6191 | -59.5825 | -0.050354 | -0.091553 | 0.24719 | 0.068665 | -0.21057 | -0.21057 | -0.16022 | -0.16022 | -0.009155 | -0.054932 | 0.14648 | -0.24719 | -0.041199 | -0.07782 | -0.032044 | -0.068665 | 0.11902 | 123.2895 | -0.23804 | 123.1476 | 122.9507 | 122.9462 | 122.9004 | 122.937 | -123.0423 | -123.0011 | 123.2391 | 123.1384 | 59.1888 | 59.0332
289.0312 | 123.1201 | -59.5642 | 63.4598 | 0.037738 | 0.0013433 | 0.048695 | 0.074736 | 0.013547 | 0.0054353 | 0.0077622 | -0.39739 | 0.0045474 | 0.083949 | 0.041297 | 0.0021782 | 0.013113 | 0.019458 | -0.48981 | 63.327 | -59.6558 | 63.6795 | -59.6329 | -60.0174 | -59.5413 | -0.6546 | 63.3865 | -59.5871 | 63.5101 | -59.6786 | -59.8068 | -59.6832 | -0.091553 | -0.13275 | 0.21973 | -0.068665 | 0.022888 | -0.45319 | 0.11444 | -0.36163 | -0.022888 | -0.073242 | 0.050354 | -0.11444 | -0.11902 | -0.24262 | -0.096131 | -0.21973 | 0.022888 | 123.3353 | -0.091553 | 123.0972 | 122.9828 | 122.9736 | 122.8912 | 122.9507 | -123.1155 | -123.0469 | 123.2437 | 123.0743 | 59.0744 | 58.9096
289.9531 | 123.1659 | -59.5413 | 63.4781 | 0.11403 | 0.0077523 | 0.056172 | 0.070463 | 0.0039344 | 0.0011633 | 0.0024222 | 0.13667 | -0.0039976 | 0.073268 | 0.060523 | -0.0031618 | -0.0007718 | 0.0077094 | -0.36163 | 63.3774 | -59.5917 | 63.6749 | -59.4818 | -59.729 | -59.729 | -0.58136 | 63.3865 | -59.5505 | 63.5742 | -59.5917 | -59.6878 | -59.6786 | -0.050354 | -0.10071 | 0.19684 | 0.059509 | -0.18768 | -0.18768 | -0.13733 | -0.13733 | -0.009155 | -0.091552 | 0.096131 | -0.050354 | -0.13733 | -0.14648 | -0.12817 | -0.13733 | 0.10986 | 123.2666 | -0.041199 | 123.1247 | 122.9691 | 122.937 | 122.9187 | 122.9279 | -123.0698 | -123.0286 | 123.2162 | 123.1155 | 59.1797 | 58.96
291.0312 | 123.1705 | -59.5642 | 63.4277 | 0.0072204 | -0.00079271 | 0.059376 | 0.07794 | 0.0082064 | 0.010776 | 0.0066942 | -0.046432 | 0.010956 | 0.0722 | 0.076545 | -0.0020938 | 0.023794 | 0.0013004 | -0.46234 | 63.3408 | -59.6512 | 63.6978 | -59.4589 | -59.7015 | -59.7519 | -0.737 | 63.3499 | -59.6008 | 63.4827 | -59.6283 | -59.7977 | -59.6878 | -0.086975 | -0.086975 | 0.27008 | 0.10529 | -0.18768 | -0.13733 | -0.10071 | -0.050354 | -0.036621 | -0.077819 | 0.054932 | -0.064087 | -0.1236 | -0.23346 | -0.086975 | -0.19684 | 0.19226 | 123.349 | -0.027466 | 123.0835 | 122.9919 | 122.9507 | 122.905 | 122.9141 | -123.0789 | -123.0286 | 123.262 | 123.0469 | 59.1019 | 58.8272
291.9531 | 123.1201 | -59.5551 | 63.4735 | 0.068255 | 0.010956 | 0.055104 | 0.083281 | 0.0082064 | -0.0063137 | -0.00078276 | 0.274 | 0.0056154 | 0.065791 | 0.090431 | -0.0052988 | 0.014181 | -0.017926 | -0.46692 | 63.3728 | -59.5688 | 63.707 | -59.2987 | -59.4223 | -59.7336 | -0.72327 | 63.3591 | -59.5505 | 63.5513 | -59.6146 | -59.729 | -59.7336 | -0.013733 | -0.10071 | 0.23346 | 0.25635 | -0.17853 | 0.13275 | -0.16479 | 0.14648 | 0.004578 | -0.11444 | 0.07782 | -0.059509 | -0.17853 | -0.17395 | -0.18311 | -0.17853 | 0.27008 | 123.2758 | -0.064087 | 123.1018 | 122.9416 | 122.9095 | 122.9279 | 122.9141 | -123.0423 | -123.024 | 123.262 | 123.1064 | 59.0881 | 58.8318
293.0312 | 123.143 | -59.5596 | 63.4598 | 0.022479 | 0.0013433 | 0.056172 | 0.07794 | -0.017429 | 0.0011633 | -0.00078276 | -0.061691 | 0.013092 | 0.067927 | 0.070137 | -0.0020938 | 0.0056372 | 0.0077094 | -0.52185 | 63.3224 | -59.6191 | 63.6978 | -59.4177 | -59.6695 | -59.7794 | -0.75989 | 63.3774 | -59.5871 | 63.4918 | -59.6329 | -59.8022 | -59.7061 | -0.05951 | -0.13733 | 0.23804 | 0.14191 | -0.21973 | -0.10986 | -0.16022 | -0.050354 | -0.027466 | -0.082398 | 0.032043 | -0.073243 | -0.14648 | -0.24261 | -0.11902 | -0.21515 | 0.20142 | 123.317 | -0.045777 | 123.0789 | 122.9416 | 122.9645 | 122.8821 | 122.937 | -123.0789 | -123.0469 | 123.2574 | 123.0515 | 59.0378 | 58.7997
293.9531 | 123.1201 | -59.5093 | 63.4598 | 0.11403 | 0.0045473 | 0.050831 | 0.089689 | 0.01141 | -0.019131 | 0.0077622 | -0.1685 | 0.0013434 | 0.076472 | 0.089363 | -0.013843 | 0.016318 | -0.00083564 | -0.5127 | 63.3133 | -59.5779 | 63.6749 | -59.4406 | -59.7382 | -59.7198 | -0.68665 | 63.4048 | -59.5688 | 63.5788 | -59.6512 | -59.729 | -59.7061 | -0.068665 | -0.14648 | 0.21515 | 0.068664 | -0.21057 | -0.22888 | -0.14191 | -0.16022 | -0.05951 | -0.054932 | 0.11902 | -0.14191 | -0.19684 | -0.21973 | -0.13733 | -0.16022 | 0.13733 | 123.2529 | -0.082397 | 123.1476 | 122.8912 | 122.9736 | 122.8226 | 122.9141 | -123.0377 | -123.0286 | 123.1842 | 123.0881 | 58.9966 | 58.8226
295.0312 | 123.23 | -59.5139 | 63.4186 | 0.022479 | 0.028046 | 0.058308 | 0.084349 | 0.0071384 | -0.0084497 | 0.0034902 | 0.18245 | 0.0045474 | 0.059382 | 0.040229 | -0.0052988 | 0.0056372 | 0.00023236 | -0.48981 | 63.3041 | -59.5551 | 63.533 | -59.6054 | -59.8297 | -59.8663 | -0.64545 | 63.3362 | -59.5322 | 63.6292 | -59.5779 | -59.6375 | -59.6283 | -0.041199 | -0.11444 | 0.11444 | -0.091553 | -0.35248 | -0.31586 | -0.31128 | -0.27466 | -0.018311 | -0.082397 | 0.21057 | -0.064087 | -0.11444 | -0.1236 | -0.09613 | -0.10529 | -0.050354 | 123.0881 | -0.045776 | 123.1613 | 122.8592 | 122.8683 | 122.818 | 122.85 | -122.9736 | -122.9507 | 123.0469 | 123.143 | 59.024 | 58.8684
295.9531 | 123.1476 | -59.523 | 63.5147 | 0.17507 | 0.00027529 | 0.062581 | 0.079008 | -0.01102 | -0.013791 | -0.0061228 | 0.075638 | 0.0045474 | 0.065791 | 0.058387 | -0.0095708 | 0.0088412 | 0.0077094 | -0.48065 | 63.3774 | -59.5917 | 63.7024 | -59.3536 | -59.7427 | -59.6191 | -0.72784 | 63.4277 | -59.5688 | 63.5559 | -59.6603 | -59.6786 | -59.697 | -0.068665 | -0.13733 | 0.18768 | 0.16937 | -0.096131 | -0.21973 | -0.027466 | -0.15106 | -0.045777 | -0.086975 | 0.041199 | -0.13733 | -0.17395 | -0.15564 | -0.12817 | -0.10986 | 0.23804 | 123.2941 | -0.091552 | 123.1247 | 122.9691 | 122.9965 | 122.9004 | 122.9507 | -123.1064 | -123.0835 | 123.2254 | 123.0789 | 59.0424 | 58.7952
296.9531 | 123.1705 | -59.5413 | 63.4918 | 0.11403 | 0.0024113 | 0.051899 | 0.085417 | 0.0060704 | -0.016995 | 0.0013532 | -0.031174 | 0.0066834 | 0.05511 | 0.0039132 | -0.0020938 | 0.0056372 | -0.015789 | -0.43488 | 63.3545 | -59.5963 | 63.6841 | -59.4177 | -59.697 | -59.7794 | -0.72327 | 63.4232 | -59.5367 | 63.5605 | -59.5459 | -59.729 | -59.6191 | -0.054931 | -0.13733 | 0.19226 | 0.1236 | -0.23804 | -0.15564 | -0.18311 | -0.10071 | 0.004578 | -0.068664 | 0.068665 | -0.004577 | -0.07782 | -0.18768 | -0.082398 | -0.19226 | 0.17853 | 123.2803 | -0.009155 | 123.0972 | 122.9507 | 122.9599 | 122.8958 | 122.9645 | -123.0881 | -123.0286 | 123.2254 | 123.1018 | 59.1064 | 58.8181
298.0312 | 123.2025 | -59.5322 | 63.4232 | 0.098773 | 0.0024113 | 0.065785 | 0.066191 | 0.016751 | 0.0022313 | 0.00028524 | 0.060379 | 0.010956 | 0.064723 | 0.055183 | -0.019184 | 0.010977 | 0.0098454 | -0.56305 | 63.3041 | -59.6054 | 63.6292 | -59.4269 | -59.7519 | -59.7977 | -0.86517 | 63.3545 | -59.5825 | 63.5971 | -59.5367 | -59.7702 | -59.642 | -0.073242 | -0.11902 | 0.20599 | 0.10529 | -0.2655 | -0.21973 | -0.19226 | -0.14648 | -0.050354 | -0.068665 | 0.17395 | -0.004577 | -0.10986 | -0.23804 | -0.059509 | -0.18768 | 0.17853 | 123.2346 | 0.045777 | 123.1796 | 122.9095 | 122.937 | 122.8363 | 122.8867 | -123.0286 | -123.0057 | 123.1613 | 123.1293 | 58.9691 | 58.667
298.9531 | 123.1338 | -59.5459 | 63.4964 | 0.22084 | -0.0072017 | 0.059376 | 0.073668 | 0.0017974 | -0.012723 | 0.0088302 | 0.16719 | 0.017364 | 0.083949 | 0.04557 | 4.2208e-05 | 0.013113 | -0.012585 | -0.48523 | 63.3865 | -59.5963 | 63.7619 | -59.3948 | -59.6558 | -59.6741 | -0.81024 | 63.414 | -59.5459 | 63.533 | -59.6054 | -59.729 | -59.6649 | -0.050354 | -0.10986 | 0.2655 | 0.15106 | -0.12817 | -0.10986 | -0.07782 | -0.05951 | 0 | -0.082398 | 0.036621 | -0.05951 | -0.11902 | -0.18311 | -0.11902 | -0.18311 | 0.20142 | 123.3582 | -0.05951 | 123.0789 | 122.9828 | 122.9599 | 122.9324 | 122.9599 | -123.0927 | -123.0423 | 123.3078 | 123.0789 | 59.0607 | 58.7357
300.0312 | 123.2071 | -59.5184 | 63.414 | 0.083514 | 0.0013433 | 0.063649 | 0.075804 | 0.0039344 | 0.0075723 | -0.0039868 | -0.046432 | 0.0045474 | 0.071131 | 0.049842 | -0.01598 | 0.016318 | 0.0055734 | -0.59052 | 63.3133 | -59.6146 | 63.6337 | -59.4498 | -59.7473 | -59.7931 | -0.90179 | 63.3545 | -59.5688 | 63.5559 | -59.5551 | -59.7519 | -59.61 | -0.09613 | -0.10071 | 0.21973 | 0.068665 | -0.27466 | -0.22888 | -0.17853 | -0.13275 | -0.050354 | -0.059509 | 0.14191 | -0.036621 | -0.091552 | -0.23346 | -0.041198 | -0.1831 | 0.16479 | 123.2483 | 0.013733 | 123.1247 | 122.9279 | 122.9233 | 122.8317 | 122.8729 | -123.0286 | -122.9828 | 123.1522 | 123.0743 | 58.9279 | 58.6166
300.9531 | 123.0789 | -59.5322 | 63.4506 | 0.19033 | -0.0018617 | 0.058308 | 0.075804 | -0.0078156 | -0.0073817 | 0.0024222 | 0.10615 | 0.020569 | 0.075404 | 0.053047 | -0.0052988 | 0.010977 | -0.018994 | -0.54932 | 63.3636 | -59.6008 | 63.7024 | -59.4406 | -59.7061 | -59.7244 | -0.95673 | 63.3911 | -59.5825 | 63.501 | -59.697 | -59.7702 | -59.7336 | -0.068664 | -0.086976 | 0.25177 | 0.091553 | -0.19226 | -0.17395 | -0.1236 | -0.10529 | -0.050354 | -0.05951 | 0.050354 | -0.16479 | -0.20142 | -0.23804 | -0.15106 | -0.18768 | 0.16022 | 123.3032 | -0.11444 | 123.0835 | 122.9645 | 122.9736 | 122.8958 | 122.9233 | -123.0515 | -123.0331 | 123.2346 | 123.0331 | 58.9828 | 58.5754
302.0312 | 123.23 | -59.5001 | 63.4323 | 0.068255 | 0.0088203 | 0.056172 | 0.068327 | 0.0092744 | -0.010586 | -0.0061228 | 0.21297 | 0.0002754 | 0.047633 | 0.054115 | -0.0074348 | 0.0035002 | -0.0019036 | -0.54474 | 63.2767 | -59.6054 | 63.5605 | -59.5734 | -59.8251 | -59.8709 | -0.85602 | 63.3316 | -59.5367 | 63.5742 | -59.5047 | -59.6649 | -59.5963 | -0.10529 | -0.15564 | 0.12817 | -0.073242 | -0.37079 | -0.32501 | -0.2655 | -0.21973 | -0.036621 | -0.10071 | 0.14191 | -0.004578 | -0.09613 | -0.1648 | -0.059509 | -0.12817 | 0.032044 | 123.1659 | 0.032043 | 123.111 | 122.8821 | 122.8683 | 122.7768 | 122.8317 | -123.0377 | -122.9691 | 123.0606 | 123.0743 | 58.9554 | 58.6441
302.9531 | 123.1567 | -59.5139 | 63.4735 | 0.083514 | 0.0024113 | 0.064717 | 0.081144 | 0.0060704 | -0.0052457 | -0.0018508 | 0.12141 | 0.0066834 | 0.062587 | 0.049842 | -0.0095708 | -0.0007718 | -0.011517 | -0.58136 | 63.3774 | -59.5917 | 63.6932 | -59.3811 | -59.7244 | -59.6832 | -0.88806 | 63.4003 | -59.5551 | 63.588 | -59.5825 | -59.6878 | -59.6786 | -0.07782 | -0.096131 | 0.21973 | 0.13275 | -0.16937 | -0.21057 | -0.091553 | -0.13275 | -0.041199 | -0.073242 | 0.11444 | -0.068665 | -0.16479 | -0.17395 | -0.1236 | -0.13275 | 0.21057 | 123.2849 | -0.027466 | 123.143 | 122.9691 | 122.9553 | 122.8912 | 122.9141 | -123.0652 | -123.0286 | 123.2071 | 123.1018 | 58.9325 | 58.6258
304.0312 | 123.1796 | -59.5276 | 63.4277 | -0.023297 | 0.012024 | 0.056172 | 0.079008 | 0.00072943 | 0.0054353 | -0.0071918 | -0.015915 | 0.0077514 | 0.081813 | 0.040229 | -0.0063668 | 0.016318 | -0.0061756 | -0.65918 | 63.327 | -59.61 | 63.6749 | -59.4727 | -59.6786 | -59.8068 | -1.0025 | 63.3728 | -59.5688 | 63.5422 | -59.5596 | -59.7565 | -59.6603 | -0.082397 | -0.10071 | 0.24719 | 0.054932 | -0.27924 | -0.15106 | -0.19684 | -0.068665 | -0.041199 | -0.054931 | 0.11444 | -0.032043 | -0.13275 | -0.22888 | -0.091552 | -0.18768 | 0.13733 | 123.2849 | 0.009156 | 123.111 | 122.937 | 122.9416 | 122.8546 | 122.9004 | -123.0377 | -122.9965 | 123.2025 | 123.0698 | 58.8684 | 58.5251
304.9531 | 123.0927 | -59.5596 | 63.446 | 0.083514 | 0.0056153 | 0.066853 | 0.084349 | 0.0071384 | -0.0063137 | -0.0136 | -0.10747 | 0.0066834 | 0.067927 | 0.10325 | -0.012775 | 0.014181 | 0.022663 | -0.66376 | 63.3316 | -59.5917 | 63.6887 | -59.3903 | -59.729 | -59.6924 | -1.0391 | 63.3728 | -59.5871 | 63.5651 | -59.6832 | -59.7839 | -59.7519 | -0.032044 | -0.11444 | 0.24262 | 0.16937 | -0.13275 | -0.16937 | -0.10071 | -0.13733 | -0.027466 | -0.073242 | 0.11902 | -0.1236 | -0.19226 | -0.2243 | -0.16479 | -0.19684 | 0.20142 | 123.2803 | -0.096131 | 123.1522 | 122.9233 | 122.9599 | 122.8912 | 122.9324 | -123.0377 | -123.0331 | 123.2483 | 123.1247 | 58.8959 | 58.5205
306.0312 | 123.2117 | -59.523 | 63.414 | 0.11403 | 0.0066833 | 0.060444 | 0.074736 | -0.0035426 | -0.0041777 | 0.0013532 | 0.075638 | 0.0088204 | 0.067927 | 0.060523 | -0.0074348 | 0.0099092 | 0.017322 | -0.65918 | 63.3087 | -59.5642 | 63.5605 | -59.5734 | -59.7794 | -59.8663 | -0.97961 | 63.3179 | -59.5322 | 63.5788 | -59.5642 | -59.6558 | -59.6283 | -0.041199 | -0.10529 | 0.14648 | -0.050354 | -0.34332 | -0.25635 | -0.30212 | -0.21515 | -0.009156 | -0.09613 | 0.16479 | -0.041199 | -0.10529 | -0.13275 | -0.09613 | -0.1236 | -0.009155 | 123.1247 | -0.032043 | 123.111 | 122.8729 | 122.85 | 122.8317 | 122.8409 | -122.9782 | -122.9462 | 123.0835 | 123.1018 | 58.8638 | 58.5434
306.9531 | 123.175 | -59.5001 | 63.4644 | 0.19033 | 0.0056153 | 0.061512 | 0.0726 | 0.010342 | -0.035153 | 0.0066942 | 0.090897 | 0.0098884 | 0.067927 | 0.078681 | 4.2208e-05 | 0.0035002 | 0.0023694 | -0.64545 | 63.3636 | -59.5917 | 63.6383 | -59.4223 | -59.7885 | -59.6832 | -1.0071 | 63.4094 | -59.5367 | 63.6749 | -59.729 | -59.642 | -59.5825 | -0.091553 | -0.10071 | 0.17395 | 0.07782 | -0.18311 | -0.28839 | -0.091553 | -0.19684 | -0.036621 | -0.054931 | 0.21057 | -0.22888 | -0.082398 | -0.14191 | -0.045777 | -0.10529 | 0.16937 | 123.23 | -0.19226 | 123.2117 | 122.9553 | 122.9462 | 122.8638 | 122.9095 | -123.056 | -123.0011 | 123.1384 | 123.175 | 58.8547 | 58.493
307.9531 | 123.1705 | -59.5047 | 63.4781 | 0.11403 | 0.0013433 | 0.055104 | 0.081144 | -0.0014066 | -0.018063 | 0.0013532 | -0.00065608 | 0.013092 | 0.068995 | 0.054115 | 0.0064512 | 0.0045682 | -0.010449 | -0.6134 | 63.3636 | -59.6054 | 63.6566 | -59.4635 | -59.7198 | -59.8022 | -1.062 | 63.3865 | -59.5367 | 63.6017 | -59.6466 | -59.6695 | -59.5825 | -0.10071 | -0.11444 | 0.17853 | 0.041199 | -0.29755 | -0.21515 | -0.19684 | -0.11444 | -0.032043 | -0.091552 | 0.1236 | -0.14191 | -0.07782 | -0.16479 | -0.045777 | -0.13275 | 0.14191 | 123.262 | -0.10986 | 123.1384 | 122.9691 | 122.9233 | 122.8683 | 122.8912 | -123.0835 | -123.0148 | 123.1613 | 123.1064 | 58.8913 | 58.4427
308.9531 | 123.1567 | -59.5047 | 63.4735 | 0.037738 | 0.0034793 | 0.054036 | 0.082213 | -0.0099516 | 9.5287e-05 | -0.0018508 | 0.04512 | 0.0077514 | 0.059382 | 0.072273 | -0.010639 | 0.0035002 | -0.013653 | -0.66834 | 63.3453 | -59.6008 | 63.6292 | -59.4131 | -59.7565 | -59.6924 | -1.0986 | 63.4003 | -59.5413 | 63.5376 | -59.5459 | -59.6466 | -59.642 | -0.09613 | -0.12817 | 0.15564 | 0.091553 | -0.18768 | -0.25177 | -0.091553 | -0.15564 | -0.036621 | -0.073242 | 0.064087 | -0.041198 | -0.13733 | -0.14191 | -0.10071 | -0.10528 | 0.18768 | 123.23 | -0.004577 | 123.0789 | 122.9462 | 122.9416 | 122.85 | 122.905 | -123.0743 | -123.0148 | 123.1338 | 123.0423 | 58.8364 | 58.4061
310.0312 | 123.2025 | -59.5184 | 63.4506 | -0.0080386 | 0.010956 | 0.065785 | 0.074736 | 0.0060704 | 0.0075723 | 0.0013532 | 0.22823 | 0.0077514 | 0.064723 | 0.054115 | -0.0042298 | 0.0077732 | -0.011517 | -0.73242 | 63.3133 | -59.5825 | 63.5651 | -59.5413 | -59.8251 | -59.8068 | -1.1307 | 63.3316 | -59.5642 | 63.6154 | -59.5779 | -59.6466 | -59.6329 | -0.064087 | -0.13733 | 0.11444 | -0.022888 | -0.28839 | -0.3067 | -0.2243 | -0.24261 | -0.045776 | -0.11902 | 0.16479 | -0.059509 | -0.11444 | -0.12817 | -0.068665 | -0.082397 | 0.041199 | 123.1476 | -0.013733 | 123.1796 | 122.8958 | 122.8958 | 122.8317 | 122.85 | -123.0331 | -123.0148 | 123.0835 | 123.1338 | 58.786 | 58.3878
310.9531 | 123.2208 | -59.5001 | 63.4415 | 0.11403 | 0.0034793 | 0.052968 | 0.079008 | 0.0071384 | 0.010776 | -0.026418 | 0.04512 | -0.0007936 | 0.066859 | 0.04557 | -0.01598 | 0.012045 | -0.0061756 | -0.78278 | 63.2767 | -59.5871 | 63.4827 | -59.4955 | -59.8938 | -59.8297 | -1.3962 | 63.2675 | -59.5551 | 63.6475 | -59.491 | -59.642 | -59.5734 | -0.086975 | -0.1648 | 0.041199 | 0.004578 | -0.32959 | -0.39368 | -0.24262 | -0.3067 | -0.054932 | -0.17395 | 0.20599 | 0.009155 | -0.073242 | -0.14191 | -0.01831 | -0.086975 | 0.091553 | 123.0698 | 0.064087 | 123.2025 | 122.8638 | 122.8226 | 122.7768 | 122.7676 | -123.0286 | -122.9965 | 122.9828 | 123.1476 | 58.7173 | 58.1039
312.0312 | 123.1979 | -59.523 | 63.4277 | -0.31321 | 0.0013433 | 0.049763 | 0.065123 | 0.014615 | -0.0084497 | 0.0077622 | 0.075638 | 0.0024114 | 0.066859 | 0.049842 | -0.010639 | 0.014181 | 0.0077094 | -0.80109 | 63.2767 | -59.5688 | 63.5376 | -59.5184 | -59.8251 | -59.8206 | -1.2177 | 63.3362 | -59.5596 | 63.6246 | -59.5825 | -59.6695 | -59.642 | -0.045777 | -0.15106 | 0.10986 | 0.004577 | -0.29755 | -0.30212 | -0.25177 | -0.25635 | -0.036621 | -0.091552 | 0.19684 | -0.05951 | -0.11902 | -0.14648 | -0.082398 | -0.10986 | 0.050354 | 123.1064 | -0.022889 | 123.1842 | 122.8455 | 122.8958 | 122.7997 | 122.8592 | -122.9965 | -122.9874 | 123.0606 | 123.1476 | 58.7219 | 58.3054
312.9531 | 123.0835 | -59.5505 | 63.4827 | 0.052997 | 0.0034793 | 0.058308 | 0.070463 | 0.0092744 | 0.015048 | -0.017873 | -0.061691 | -0.0018616 | 0.071131 | 0.072273 | -0.012775 | 0.010977 | -0.0093806 | -0.78278 | 63.3408 | -59.5917 | 63.6795 | -59.3811 | -59.7336 | -59.6741 | -1.4191 | 63.3957 | -59.5459 | 63.5239 | -59.6603 | -59.8618 | -59.6786 | -0.041199 | -0.14191 | 0.19684 | 0.16937 | -0.1236 | -0.18311 | -0.082397 | -0.14191 | 0.004578 | -0.086975 | 0.041199 | -0.10986 | -0.12817 | -0.31128 | -0.13275 | -0.31586 | 0.21057 | 123.2712 | -0.11444 | 123.0698 | 122.9324 | 122.9416 | 122.8912 | 122.9462 | -123.0743 | -123.0286 | 123.23 | 123.0743 | 58.7677 | 58.1314
314.0312 | 123.2025 | -59.4635 | 63.446 | 0.098773 | 0.0066833 | 0.065785 | 0.076872 | -0.0046106 | -0.018063 | 0.0034902 | -0.015915 | 0.013092 | 0.088221 | 0.047706 | -0.0063668 | 0.028067 | -0.02113 | -0.82855 | 63.3041 | -59.5734 | 63.5193 | -59.4681 | -59.9121 | -59.8114 | -1.2726 | 63.3408 | -59.5322 | 63.5147 | -59.5139 | -59.3994 | -59.4177 | -0.10986 | -0.14191 | 0.073242 | -0.004578 | -0.3479 | -0.44861 | -0.23804 | -0.33875 | -0.068665 | -0.10529 | 0.068664 | -0.050354 | 0.045776 | 0.064087 | 0.11444 | 0.13275 | 0.10528 | 123.0927 | 0.018311 | 123.0469 | 122.8775 | 122.8729 | 122.7676 | 122.8043 | -123.0194 | -122.9782 | 122.9828 | 122.9782 | 58.6349 | 58.1909
314.9531 | 123.1293 | -59.5413 | 63.4644 | 0.068255 | -0.0039977 | 0.065785 | 0.079008 | 0.014615 | -0.022336 | -0.0018508 | 0.014603 | 0.0077514 | 0.073268 | 0.06266 | -0.020252 | 0.01525 | -0.0029716 | -0.81482 | 63.3591 | -59.6054 | 63.6703 | -59.3811 | -59.729 | -59.7015 | -1.4877 | 63.4003 | -59.5596 | 63.5239 | -59.6512 | -59.816 | -59.7061 | -0.064087 | -0.10528 | 0.20599 | 0.16022 | -0.16022 | -0.18768 | -0.09613 | -0.1236 | -0.01831 | -0.064086 | 0.05951 | -0.10986 | -0.16479 | -0.27466 | -0.14648 | -0.25635 | 0.2243 | 123.2758 | -0.091553 | 123.0835 | 122.9645 | 122.9599 | 122.9004 | 122.9416 | -123.0698 | -123.024 | 123.2117 | 123.0652 | 58.7265 | 58.0536
316.0312 | 123.1979 | -59.5001 | 63.4506 | 0.0072204 | 0.0088203 | 0.049763 | 0.064055 | 0.01141 | 0.0022313 | -0.010396 | 0.64021 | 0.017364 | 0.070063 | 0.051979 | 0.0021782 | 0.012045 | -0.0040396 | -0.87433 | 63.3224 | -59.5551 | 63.5834 | -59.4589 | -59.7977 | -59.7656 | -1.4877 | 63.3728 | -59.523 | 63.6246 | -59.61 | -59.7061 | -59.6329 | -0.054932 | -0.12817 | 0.13275 | 0.041199 | -0.2655 | -0.29755 | -0.21057 | -0.24261 | -0.022888 | -0.07782 | 0.17395 | -0.10986 | -0.13275 | -0.20599 | -0.10986 | -0.18311 | 0.096131 | 123.1384 | -0.086975 | 123.1476 | 122.8775 | 122.8958 | 122.8226 | 122.8729 | -123.0057 | -122.9736 | 123.0835 | 123.1247 | 58.6258 | 58.0124
316.9531 | 123.1201 | -59.5367 | 63.4872 | 0.098773 | -0.0039977 | 0.059376 | 0.081144 | 0.0017974 | 0.01398 | -0.0018508 | -0.046432 | 0.0056154 | 0.071131 | 0.072273 | 0.0043152 | 0.026999 | 0.0034374 | -0.86517 | 63.3499 | -59.5871 | 63.6566 | -59.3857 | -59.642 | -59.7198 | -1.6067 | 63.4186 | -59.5596 | 63.4552 | -59.6237 | -59.8206 | -59.6741 | -0.050354 | -0.13733 | 0.16937 | 0.15106 | -0.18311 | -0.10529 | -0.13275 | -0.054932 | -0.022888 | -0.068665 | -0.032044 | -0.086975 | -0.13733 | -0.28381 | -0.11444 | -0.26093 | 0.20142 | 123.2437 | -0.064087 | 123.0148 | 122.937 | 122.9782 | 122.8867 | 122.9553 | -123.0743 | -123.0469 | 123.1934 | 122.9919 | 58.6716 | 57.93
318.0312 | 123.2391 | -59.4818 | 63.4232 | 0.052997 | 0.0045473 | 0.062581 | 0.0726 | 0.0092744 | -0.0041777 | -0.021077 | 0.41133 | 0.0066834 | 0.070063 | 0.032752 | -0.013843 | 0.016318 | -0.0051076 | -0.89264 | 63.2812 | -59.5642 | 63.4918 | -59.5139 | -59.8572 | -59.8251 | -1.506 | 63.3179 | -59.5459 | 63.6475 | -59.5276 | -59.6512 | -59.5642 | -0.082397 | -0.14191 | 0.068664 | -0.032043 | -0.34332 | -0.37537 | -0.26093 | -0.29297 | -0.064086 | -0.10529 | 0.2243 | -0.045776 | -0.082397 | -0.16937 | -0.018311 | -0.10529 | 0.050354 | 123.056 | 0.01831 | 123.1934 | 122.8455 | 122.8638 | 122.7631 | 122.7997 | -122.9874 | -122.9691 | 122.9736 | 123.1293 | 58.5892 | 57.9758
318.9531 | 123.1293 | -59.5139 | 63.4918 | 0.068255 | -0.0050657 | 0.067921 | 0.076872 | -0.019565 | -0.03088 | -0.0018508 | 0.029861 | -0.0039976 | 0.065791 | 0.056251 | -0.012775 | 0.0077732 | -0.00083564 | -0.88806 | 63.382 | -59.5734 | 63.6703 | -59.4315 | -59.7107 | -59.7656 | -1.5564 | 63.4094 | -59.5367 | 63.5605 | -59.5825 | -59.7656 | -59.642 | -0.059509 | -0.10986 | 0.17853 | 0.082397 | -0.25177 | -0.19684 | -0.19226 | -0.13733 | -0.022888 | -0.082397 | 0.068665 | -0.068665 | -0.12817 | -0.25177 | -0.10529 | -0.22888 | 0.14191 | 123.2437 | -0.045777 | 123.0972 | 122.9553 | 122.9462 | 122.8958 | 122.9233 | -123.0652 | -123.0286 | 123.1842 | 123.0743 | 58.6258 | 57.9575
320.0312 | 123.1979 | -59.5001 | 63.4552 | -0.069074 | 0.0098883 | 0.049763 | 0.071531 | -0.0088836 | 0.0065043 | -0.0061228 | 0.090897 | 0.0013434 | 0.079676 | 0.046638 | -0.012775 | 0.012045 | -0.02113 | -0.96588 | 63.3316 | -59.5459 | 63.5651 | -59.491 | -59.8251 | -59.8343 | -1.6113 | 63.3316 | -59.5367 | 63.6017 | -59.5276 | -59.6924 | -59.5642 | -0.045776 | -0.1236 | 0.10986 | 0.009155 | -0.33417 | -0.32501 | -0.28839 | -0.27924 | -0.036621 | -0.1236 | 0.14649 | -0.027466 | -0.064087 | -0.19226 | -0.027466 | -0.15564 | 0.054931 | 123.111 | 0.009155 | 123.1384 | 122.8775 | 122.8683 | 122.8317 | 122.8317 | -123.0011 | -122.9919 | 123.0652 | 123.1018 | 58.5342 | 57.8888
320.9531 | 123.1293 | -59.5413 | 63.4781 | 0.052997 | 0.017365 | 0.052968 | 0.082213 | -0.0024746 | 0.0011633 | -0.0061228 | -0.046432 | 0.0034794 | 0.066859 | 0.060523 | -0.013843 | 0.016318 | -0.012585 | -0.95673 | 63.3499 | -59.5825 | 63.7207 | -59.3903 | -59.6832 | -59.7198 | -1.7303 | 63.4186 | -59.5505 | 63.533 | -59.6741 | -59.816 | -59.6924 | -0.041199 | -0.12817 | 0.24262 | 0.15106 | -0.17853 | -0.14191 | -0.13733 | -0.10071 | -0.009155 | -0.059509 | 0.054932 | -0.13275 | -0.15106 | -0.27466 | -0.14191 | -0.2655 | 0.19226 | 123.3032 | -0.1236 | 123.0835 | 122.9324 | 122.9691 | 122.8912 | 122.9599 | -123.0606 | -123.0286 | 123.262 | 123.0743 | 58.5846 | 57.811
321.9531 | 123.1842 | -59.5139 | 63.446 | 0.11403 | -0.0050657 | 0.045491 | 0.073668 | 0.0017974 | -0.0020407 | -0.012532 | -0.12273 | 0.010956 | 0.076472 | 0.044502 | 0.0011102 | 0.0013642 | 0.0045054 | -1.1078 | 63.3408 | -59.6008 | 63.6063 | -59.3399 | -59.7473 | -59.7153 | -1.8265 | 63.4003 | -59.5413 | 63.6108 | -59.6054 | -59.7519 | -59.6558 | -0.086975 | -0.10529 | 0.16022 | 0.17395 | -0.20142 | -0.23346 | -0.11444 | -0.14648 | -0.027466 | -0.045776 | 0.1648 | -0.091553 | -0.14191 | -0.23804 | -0.11444 | -0.21057 | 0.26093 | 123.2071 | -0.064087 | 123.1522 | 122.9416 | 122.9416 | 122.8546 | 122.9141 | -123.0469 | -122.9874 | 123.1201 | 123.1247 | 58.4061 | 57.6874
323.0312 | 123.2117 | -59.5047 | 63.4186 | 0.068255 | 0.012024 | 0.049763 | 0.081144 | -0.0024746 | 0.0065043 | -0.021077 | 0.04512 | 0.0024114 | 0.042292 | 0.054115 | -0.013843 | 0.016318 | 0.0098454 | -1.0345 | 63.3087 | -59.5688 | 63.5376 | -59.523 | -59.848 | -59.816 | -1.7166 | 63.3545 | -59.523 | 63.6795 | -59.5367 | -59.6191 | -59.5779 | -0.064087 | -0.10986 | 0.11902 | -0.01831 | -0.31128 | -0.34332 | -0.24719 | -0.27923 | -0.01831 | -0.064087 | 0.26093 | -0.032043 | -0.073242 | -0.11444 | -0.054932 | -0.096131 | 0.045777 | 123.1064 | -0.013733 | 123.2025 | 122.8775 | 122.8775 | 122.8134 | 122.8592 | -122.9874 | -122.9416 | 123.0423 | 123.1842 | 58.4702 | 57.7881
323.9531 | 123.1064 | -59.5322 | 63.5101 | 0.098773 | 0.0045473 | 0.061512 | 0.084349 | 0.0039344 | -0.00097271 | -0.010396 | 0.13667 | 0.0002754 | 0.062587 | 0.042366 | -0.0031618 | 0.013113 | -0.0072446 | -1.0941 | 63.3636 | -59.6191 | 63.7207 | -59.1751 | -59.8343 | -59.9304 | -1.918 | 63.4277 | -59.5551 | 63.5559 | -59.6237 | -59.8526 | -59.6283 | -0.086975 | -0.14648 | 0.21057 | 0.35706 | -0.39825 | -0.30212 | -0.31128 | -0.21515 | -0.022888 | -0.082398 | 0.045776 | -0.091552 | -0.09613 | -0.32043 | -0.073242 | -0.29755 | 0.44403 | 123.3398 | -0.068664 | 123.111 | 122.9828 | 122.9828 | 122.8958 | 122.9599 | -123.1293 | -123.0652 | 123.2529 | 123.0881 | 58.4381 | 57.6141
325.0312 | 123.2574 | -59.4543 | 63.446 | 0.26662 | -0.00079271 | 0.058308 | 0.064055 | 0.01141 | 0.0011633 | -0.0039868 | 0.21297 | -0.0007936 | 0.051905 | 0.032752 | -0.0085028 | 0.0056372 | -0.0029716 | -1.0483 | 63.3545 | -59.5139 | 63.5696 | -59.4818 | -59.7931 | -59.7656 | -1.8036 | 63.3636 | -59.5322 | 63.707 | -59.4727 | -59.5322 | -59.5459 | -0.059509 | -0.091553 | 0.1236 | -0.027466 | -0.31128 | -0.33874 | -0.25177 | -0.27924 | -0.07782 | -0.082398 | 0.26093 | -0.01831 | -0.091552 | -0.07782 | -0.013732 | 0 | 0.032043 | 123.0835 | 0.05951 | 123.2391 | 122.8683 | 122.8958 | 122.8088 | 122.818 | -122.9599 | -122.9782 | 123.024 | 123.1613 | 58.4061 | 57.6508
325.9531 | 123.2437 | -59.4772 | 63.4369 | 0.068255 | 0.0034793 | 0.061512 | 0.076872 | 0.019955 | -0.013791 | -0.0050548 | -0.046432 | 0.0034794 | 0.064723 | 0.041297 | -0.010639 | 0.021658 | -0.013653 | -1.1078 | 63.3224 | -59.6054 | 63.6017 | -59.4635 | -59.7977 | -59.8022 | -1.9592 | 63.3636 | -59.5184 | 63.6292 | -59.5139 | -59.6695 | -59.5413 | -0.12817 | -0.11444 | 0.1648 | 0.013733 | -0.32501 | -0.32043 | -0.19684 | -0.19226 | -0.041199 | -0.073243 | 0.19226 | -0.036621 | -0.064087 | -0.19226 | -0.022888 | -0.15106 | 0.14191 | 123.2071 | 0.004578 | 123.1476 | 122.9279 | 122.8821 | 122.7997 | 122.8409 | -123.0423 | -122.9553 | 123.0789 | 123.1064 | 58.3694 | 57.518
327.0312 | 123.2117 | -59.4589 | 63.4872 | 0.11403 | 0.0045473 | 0.051899 | 0.079008 | 0.010342 | -0.0041777 | 0.0024222 | 0.13667 | 0.018433 | 0.0722 | 0.043434 | -0.010639 | 0.0035002 | -0.014721 | -1.149 | 63.3362 | -59.5459 | 63.5971 | -59.4589 | -59.7977 | -59.729 | -2.0142 | 63.3591 | -59.5093 | 63.6749 | -59.523 | -59.6191 | -59.5734 | -0.086975 | -0.15106 | 0.10986 | 0 | -0.27008 | -0.33875 | -0.18311 | -0.25177 | -0.050354 | -0.12817 | 0.18768 | -0.064087 | -0.11444 | -0.16022 | -0.064087 | -0.10986 | 0.086975 | 123.143 | -0.013733 | 123.1842 | 122.8821 | 122.8683 | 122.7951 | 122.818 | -123.0331 | -122.9965 | 123.056 | 123.1338 | 58.3099 | 57.4448
327.9531 | 123.1201 | -59.5367 | 63.501 | -0.038556 | -0.0018617 | 0.058308 | 0.076872 | 0.0017974 | 0.016117 | -0.0050548 | -0.22954 | 0.0013434 | 0.067927 | 0.073341 | -0.017048 | 0.017386 | -0.014721 | -1.2085 | 63.3636 | -59.6375 | 63.7482 | -59.3445 | -59.642 | -59.7519 | -2.0416 | 63.4277 | -59.5001 | 63.5559 | -59.61 | -59.7977 | -59.6375 | -0.10071 | -0.13733 | 0.24719 | 0.19226 | -0.21515 | -0.10529 | -0.11444 | -0.004578 | 0.036621 | -0.073243 | 0.054931 | -0.073242 | -0.10071 | -0.26093 | -0.13733 | -0.29755 | 0.29297 | 123.3856 | -0.10986 | 123.056 | 123.0011 | 122.9279 | 122.9004 | 122.9645 | -123.1384 | -123.0011 | 123.2849 | 123.0927 | 58.3282 | 57.4951
329.0312 | 123.2346 | -59.4635 | 63.4781 | 0.037738 | 0.013092 | 0.054036 | 0.075804 | 0.017819 | 0.0086403 | -0.0039868 | 0.18245 | 0.016296 | 0.089289 | 0.021003 | -0.0052988 | 0.0045682 | -0.013653 | -1.2314 | 63.3682 | -59.5459 | 63.5788 | -59.4223 | -59.7656 | -59.7656 | -2.1744 | 63.3774 | -59.5276 | 63.6246 | -59.5093 | -59.6191 | -59.5596 | -0.082397 | -0.10986 | 0.10071 | 0.041199 | -0.30212 | -0.30212 | -0.21973 | -0.21973 | -0.064087 | -0.10071 | 0.14648 | -0.045776 | -0.09613 | -0.15564 | -0.032043 | -0.091553 | 0.1236 | 123.1247 | 0.018311 | 123.1522 | 122.9141 | 122.905 | 122.8317 | 122.8409 | -123.024 | -123.0057 | 123.0423 | 123.0881 | 58.2321 | 57.2891
329.9531 | 123.2483 | -59.4818 | 63.4552 | 0.098773 | -0.0018617 | 0.052968 | 0.085417 | -0.0046106 | 0.011844 | 0.0024222 | 0.090897 | 0.0056154 | 0.07754 | 0.075477 | -0.022388 | 0.016318 | 0.0023694 | -1.268 | 63.3224 | -59.5642 | 63.6383 | -59.4772 | -59.7519 | -59.848 | -2.2202 | 63.3957 | -59.5184 | 63.652 | -59.5139 | -59.6695 | -59.5459 | -0.082397 | -0.13275 | 0.18311 | 0.004578 | -0.36621 | -0.27008 | -0.28381 | -0.18768 | -0.036621 | -0.059509 | 0.19684 | -0.032043 | -0.064086 | -0.18768 | -0.027465 | -0.15106 | 0.086975 | 123.2025 | 0.004578 | 123.1705 | 122.8867 | 122.9141 | 122.8043 | 122.8775 | -123.0194 | -122.9736 | 123.1201 | 123.1339 | 58.2138 | 57.2617
331.0312 | 123.2117 | -59.4681 | 63.4781 | 0.14455 | 0.0088203 | 0.056172 | 0.07794 | -0.0035426 | -0.011654 | -0.00078276 | 0.31978 | 0.0056154 | 0.068995 | 0.0049812 | -0.013843 | 0.013113 | -0.016858 | -1.268 | 63.3499 | -59.5688 | 63.6017 | -59.4086 | -59.7748 | -59.7794 | -2.3209 | 63.3728 | -59.491 | 63.62 | -59.4452 | -59.6649 | -59.5596 | -0.10071 | -0.12817 | 0.1236 | 0.05951 | -0.31128 | -0.3067 | -0.21057 | -0.20599 | -0.022888 | -0.10529 | 0.14191 | 0.022889 | -0.091552 | -0.19684 | -0.068664 | -0.17395 | 0.16022 | 123.1705 | 0.045777 | 123.111 | 122.9187 | 122.8638 | 122.818 | 122.8409 | -123.0469 | -122.9691 | 123.0698 | 123.0881 | 58.2001 | 57.1472
331.9531 | 123.2208 | -59.4589 | 63.4506 | 0.068255 | 0.0077523 | 0.064717 | 0.07794 | 0.0017974 | -0.02554 | -0.0071918 | 0.075638 | -0.0039976 | 0.056178 | 0.068 | -0.010639 | 0.0077732 | -0.02113 | -1.2543 | 63.2858 | -59.5734 | 63.6841 | -59.5963 | -59.8022 | -59.8434 | -2.3346 | 63.3774 | -59.5459 | 63.6703 | -59.4818 | -59.5825 | -59.5276 | -0.11444 | -0.16479 | 0.23346 | -0.13733 | -0.38452 | -0.34332 | -0.27008 | -0.22888 | -0.086975 | -0.073243 | 0.21973 | -0.022889 | -0.068665 | -0.1236 | 0.01831 | -0.036622 | -0.022888 | 123.2574 | 0.064086 | 123.2162 | 122.8592 | 122.9233 | 122.7448 | 122.8363 | -123.024 | -122.9965 | 123.143 | 123.1293 | 58.2047 | 57.1243
332.9531 | 123.1338 | -59.523 | 63.4872 | 0.068255 | -0.0018617 | 0.058308 | 0.07794 | 0.022092 | 0.017185 | 0.0034902 | 0.62495 | 0.0088204 | 0.050837 | 0.033821 | -0.011707 | 0.0088412 | -0.0093806 | -1.4648 | 63.3408 | -59.5779 | 63.6841 | -59.1202 | -59.697 | -59.9442 | -2.6413 | 63.446 | -59.5322 | 63.5742 | -59.6283 | -59.7794 | -59.6558 | -0.054932 | -0.14648 | 0.19684 | 0.40283 | -0.42114 | -0.17395 | -0.36621 | -0.11902 | -0.009156 | -0.041199 | 0.086975 | -0.10529 | -0.13275 | -0.25635 | -0.1236 | -0.24719 | 0.45776 | 123.262 | -0.09613 | 123.1064 | 122.9187 | 122.9782 | 122.8638 | 122.9691 | -123.0652 | -123.0194 | 123.2071 | 123.0972 | 58.0582 | 56.8817
333.9531 | 123.1705 | -59.4955 | 63.4918 | 0.11403 | -0.0072017 | 0.051899 | 0.071531 | -0.0024746 | -0.028744 | -0.0050548 | -0.12273 | 0.0034794 | 0.066859 | 0.044502 | 4.2208e-05 | 0.019522 | -0.02113 | -1.442 | 63.3362 | -59.6054 | 63.7344 | -59.4315 | -59.6558 | -59.7061 | -2.623 | 63.4094 | -59.5688 | 63.5651 | -59.5871 | -59.7061 | -59.642 | -0.10986 | -0.15564 | 0.24262 | 0.064086 | -0.21057 | -0.16022 | -0.10071 | -0.050354 | -0.073243 | -0.082397 | 0.073242 | -0.091553 | -0.14648 | -0.21057 | -0.073242 | -0.13733 | 0.17395 | 123.3398 | -0.01831 | 123.1338 | 122.9416 | 122.9782 | 122.8317 | 122.905 | -123.0972 | -123.0606 | 123.23 | 123.0606 | 58.0536 | 56.8726
335.0312 | 123.2574 | -59.4315 | 63.4872 | 0.083514 | 0.0066833 | 0.054036 | 0.0726 | -0.0024746 | 0.01398 | -0.0018508 | 0.060379 | 0.0024114 | 0.079676 | 0.070137 | -0.0095708 | 0.0002962 | -0.011517 | -1.3184 | 63.3774 | -59.5184 | 63.5605 | -59.7198 | -59.6878 | -59.5734 | -2.4994 | 63.3774 | -59.4818 | 63.7115 | -59.3857 | -59.5963 | -59.5001 | -0.086975 | -0.10986 | 0.073242 | -0.28839 | -0.14191 | -0.25635 | -0.054931 | -0.16937 | -0.050354 | -0.10986 | 0.2243 | 0.045777 | -0.068664 | -0.16479 | -0.01831 | -0.11444 | -0.20142 | 123.0789 | 0.096131 | 123.1934 | 122.8958 | 122.8592 | 122.8088 | 122.8088 | -123.0057 | -122.9691 | 122.9919 | 123.143 | 58.1131 | 56.9321
335.9531 | 123.2162 | -59.4727 | 63.4552 | 0.0072204 | 0.010956 | 0.046559 | 0.070463 | -0.00033857 | -0.010586 | -0.0071918 | 0.075638 | -0.0050656 | 0.068995 | 0.033821 | -0.0010258 | 0.0035002 | 0.0055734 | -1.474 | 63.3316 | -59.5734 | 63.5925 | -59.523 | -59.816 | -59.8343 | -2.6459 | 63.3682 | -59.4955 | 63.6703 | -59.5184 | -59.6008 | -59.6146 | -0.10071 | -0.1236 | 0.13733 | -0.050354 | -0.36163 | -0.34332 | -0.26093 | -0.24262 | -0.022888 | -0.086975 | 0.21515 | -0.045777 | -0.14191 | -0.12817 | -0.11902 | -0.10529 | 0.050354 | 123.1659 | -0.022889 | 123.1659 | 122.905 | 122.8638 | 122.8043 | 122.8409 | -123.0286 | -122.9507 | 123.0652 | 123.143 | 57.9987 | 56.8268
337.0312 | 123.175 | -59.4681 | 63.501 | 0.022479 | 0.00027529 | 0.062581 | 0.064055 | 0.016751 | 0.0054353 | 0.00028524 | 0.274 | 0.0024114 | 0.089289 | 0.024208 | -0.0063668 | 0.017386 | -0.014721 | -1.5381 | 63.3545 | -59.5734 | 63.6475 | -59.4452 | -59.7015 | -59.8206 | -2.8336 | 63.4094 | -59.523 | 63.6703 | -59.4818 | -59.7473 | -59.5871 | -0.10528 | -0.14648 | 0.14648 | 0.022889 | -0.35248 | -0.23346 | -0.24719 | -0.12817 | -0.054931 | -0.091553 | 0.16937 | -0.013733 | -0.11902 | -0.27923 | -0.064087 | -0.2243 | 0.12817 | 123.2208 | 0.041198 | 123.1934 | 122.9279 | 122.9324 | 122.8226 | 122.8775 | -123.0743 | -123.024 | 123.1155 | 123.1384 | 57.93 | 56.6345
337.9531 | 123.23 | -59.4727 | 63.4644 | 0.037738 | -0.00079271 | 0.058308 | 0.080076 | -0.0067466 | -0.019131 | -0.0050548 | -0.031174 | -0.0029296 | 0.046565 | 0.05091 | -0.011707 | 0.018454 | -0.023266 | -1.6479 | 63.3545 | -59.5779 | 63.6795 | -59.4406 | -59.761 | -59.7519 | -2.8656 | 63.3957 | -59.5001 | 63.6932 | -59.5139 | -59.6146 | -59.5505 | -0.10529 | -0.10986 | 0.21515 | 0.032043 | -0.27924 | -0.28839 | -0.17395 | -0.1831 | -0.027466 | -0.068664 | 0.22888 | -0.041199 | -0.07782 | -0.14191 | -0.050354 | -0.11444 | 0.13733 | 123.2574 | -0.013733 | 123.1934 | 122.9324 | 122.8958 | 122.8271 | 122.8683 | -123.0423 | -122.9645 | 123.1522 | 123.1659 | 57.8247 | 56.6071
339.0312 | 123.2391 | -59.4543 | 63.5056 | 0.11403 | -0.0039977 | 0.050831 | 0.074736 | 0.014615 | 0.0065043 | -0.011464 | 0.15193 | 0.020569 | 0.052973 | 0.013526 | -0.012775 | 0.012045 | -0.0019036 | -1.4832 | 63.382 | -59.5093 | 63.6154 | -59.5642 | -59.7656 | -59.8297 | -2.4765 | 63.4689 | -59.436 | 63.7482 | -59.4315 | -59.5505 | -59.523 | -0.054931 | -0.1236 | 0.10986 | -0.10986 | -0.37537 | -0.31128 | -0.32044 | -0.25635 | 0.018311 | -0.036621 | 0.24262 | 0.022888 | -0.068664 | -0.09613 | -0.086975 | -0.11444 | -0.054932 | 123.1247 | 0.004577 | 123.1842 | 122.8912 | 122.905 | 122.8363 | 122.9233 | -123.0148 | -122.9416 | 123.0698 | 123.2025 | 57.9712 | 56.9778
339.9531 | 123.2437 | -59.4406 | 63.4552 | -0.0080386 | -0.0029297 | 0.056172 | 0.080076 | -0.0046106 | 0.010776 | 0.0056262 | 0.12141 | 0.0024114 | 0.065791 | 0.043434 | -0.0074348 | 0.0067052 | -0.0029716 | -1.6617 | 63.327 | -59.5505 | 63.5696 | -59.4498 | -60.0037 | -59.8526 | -3.0396 | 63.414 | -59.5184 | 63.6841 | -59.5413 | -59.5596 | -59.5505 | -0.10986 | -0.12817 | 0.11444 | -0.009155 | -0.41199 | -0.56305 | -0.30212 | -0.45319 | -0.07782 | -0.041199 | 0.22888 | -0.10071 | -0.10986 | -0.11902 | -0.032043 | -0.041198 | 0.10071 | 123.1201 | -0.022888 | 123.2025 | 122.8775 | 122.9324 | 122.7676 | 122.8546 | -123.0057 | -122.9736 | 123.0103 | 123.1247 | 57.7789 | 56.4011
341.0312 | 123.2758 | -59.4498 | 63.5101 | 0.037738 | 0.0088203 | 0.058308 | 0.073668 | -0.014224 | 9.5287e-05 | -0.0061228 | 0.15193 | 0.0002754 | 0.065791 | 0.010322 | -0.0052988 | 0.0088412 | -0.0083126 | -1.6708 | 63.3774 | -59.5047 | 63.6841 | -59.4864 | -59.7656 | -59.7931 | -3.1174 | 63.3957 | -59.4772 | 63.6887 | -59.4269 | -59.5596 | -59.5139 | -0.054932 | -0.13275 | 0.17395 | -0.036621 | -0.34332 | -0.31586 | -0.28839 | -0.26093 | -0.027466 | -0.11444 | 0.17853 | 0.022888 | -0.064087 | -0.10986 | -0.036621 | -0.082397 | 0.018311 | 123.1888 | 0.050354 | 123.1659 | 122.8821 | 122.8729 | 122.8271 | 122.8455 | -123.0148 | -122.9874 | 123.1338 | 123.1384 | 57.7789 | 56.3324
341.9531 | 123.1613 | -59.4406 | 63.4827 | 0.083514 | 0.00027529 | 0.05724 | 0.080076 | -0.0067466 | 0.0086403 | 0.00028524 | -0.07695 | 0.0002754 | 0.068995 | 0.073341 | -0.013843 | 0.013113 | -0.0093806 | -1.8311 | 63.3636 | -59.5688 | 63.6658 | -59.3903 | -59.729 | -59.6924 | -3.392 | 63.4048 | -59.5322 | 63.6841 | -59.5322 | -59.6329 | -59.5505 | -0.12817 | -0.11902 | 0.1831 | 0.050354 | -0.25177 | -0.28839 | -0.1236 | -0.16022 | -0.091553 | -0.07782 | 0.20142 | -0.091553 | -0.10986 | -0.19226 | -0.01831 | -0.10071 | 0.17853 | 123.2346 | 0 | 123.2162 | 122.9324 | 122.937 | 122.8043 | 122.8455 | -123.0515 | -123.0148 | 123.1064 | 123.1247 | 57.6096 | 56.0486
343.0312 | 123.2483 | -59.4086 | 63.5101 | -0.0080386 | 0.0045473 | 0.055104 | 0.086485 | -0.015292 | -0.0031087 | 0.0088302 | 0.12141 | 0.0034794 | 0.0722 | 0.05091 | -0.0052988 | 0.019522 | 0.0077094 | -1.7624 | 63.382 | -59.4864 | 63.6337 | -59.4772 | -59.7656 | -59.7702 | -3.2959 | 63.4323 | -59.4727 | 63.7436 | -59.4223 | -59.5139 | -59.523 | -0.07782 | -0.12817 | 0.1236 | -0.068665 | -0.36163 | -0.35706 | -0.28381 | -0.27924 | -0.064087 | -0.07782 | 0.23346 | -0.013733 | -0.11444 | -0.10529 | -0.050354 | -0.041199 | 0.009155 | 123.1201 | 0.050354 | 123.2162 | 122.8683 | 122.905 | 122.7905 | 122.8409 | -122.9965 | -122.9828 | 123.0423 | 123.1522 | 57.6462 | 56.1127
343.9531 | 123.1842 | -59.4131 | 63.501 | 0.083514 | 0.0088203 | 0.044423 | 0.079008 | -0.0024746 | -0.0020407 | -0.0082598 | 0.014603 | -0.0050656 | 0.071131 | 0.054115 | -0.0063668 | 0.0067052 | -0.0093806 | -1.886 | 63.3591 | -59.5505 | 63.5559 | -59.436 | -59.816 | -59.8068 | -3.5568 | 63.414 | -59.4955 | 63.707 | -59.7153 | -59.3399 | -59.2804 | -0.13733 | -0.14191 | 0.054931 | -0.022888 | -0.39368 | -0.40283 | -0.25635 | -0.2655 | -0.082397 | -0.086976 | 0.20599 | -0.30212 | 0.13275 | 0.073242 | 0.21515 | 0.15564 | 0.11444 | 123.1064 | -0.21973 | 123.2025 | 122.9095 | 122.9095 | 122.7722 | 122.8271 | -123.0515 | -122.9965 | 122.9691 | 123.1201 | 57.5272 | 55.8563
345.0312 | 123.23 | -59.4223 | 63.4781 | 0.0072204 | 0.00027529 | 0.052968 | 0.074736 | 0.00072943 | -0.0095177 | 0.010966 | 0.13667 | 0.0056154 | 0.068995 | 0.081886 | -0.010639 | 0.013113 | -0.0072446 | -1.9455 | 63.3636 | -59.5459 | 63.6475 | -59.4177 | -59.7565 | -59.7244 | -3.6667 | 63.4048 | -59.4727 | 63.7207 | -59.4681 | -59.5459 | -59.5367 | -0.1236 | -0.11444 | 0.16937 | 0.004577 | -0.30212 | -0.33417 | -0.17853 | -0.21057 | -0.050354 | -0.073242 | 0.24262 | -0.045777 | -0.11444 | -0.1236 | -0.064087 | -0.073242 | 0.12817 | 123.1934 | 0.004577 | 123.1934 | 122.9095 | 122.8775 | 122.7859 | 122.8271 | -123.024 | -122.9507 | 123.0698 | 123.143 | 57.4768 | 55.7556
345.9531 | 123.262 | -59.4406 | 63.4781 | 0.098773 | 0.0024113 | 0.049763 | 0.081144 | 0.0082064 | -0.029812 | -0.0082598 | -0.061691 | 0.0077514 | 0.065791 | 0.066932 | -0.019184 | 0.01525 | -0.012585 | -1.9867 | 63.3682 | -59.5413 | 63.6108 | -59.4269 | -59.7977 | -59.761 | -3.8315 | 63.3911 | -59.5139 | 63.7207 | -59.4681 | -59.6191 | -59.4818 | -0.10071 | -0.10986 | 0.13275 | 0.013733 | -0.32043 | -0.35706 | -0.21973 | -0.25635 | -0.073242 | -0.086975 | 0.24262 | -0.027466 | -0.041199 | -0.17853 | 0.032043 | -0.10529 | 0.11444 | 123.1522 | 0.045776 | 123.2346 | 122.9095 | 122.905 | 122.8088 | 122.8317 | -123.0194 | -122.9919 | 123.0515 | 123.1613 | 57.4539 | 55.6091
346.9531 | 123.2437 | -59.4315 | 63.4781 | -0.023297 | 0.0024113 | 0.050831 | 0.089689 | 0.0050024 | 0.0022313 | 0.017375 | -0.00065608 | 0.012024 | 0.063655 | 0.058387 | -0.01598 | 0.016318 | -0.032879 | -2.0508 | 63.3774 | -59.5505 | 63.6658 | -59.4452 | -59.7519 | -59.7565 | -3.978 | 63.4094 | -59.5047 | 63.6978 | -59.491 | -59.5779 | -59.5734 | -0.11902 | -0.10071 | 0.18768 | -0.013732 | -0.32501 | -0.32043 | -0.20599 | -0.20142 | -0.073242 | -0.068664 | 0.21973 | -0.059509 | -0.14191 | -0.14648 | -0.068664 | -0.073242 | 0.10529 | 123.2162 | 0.013733 | 123.2025 | 122.9279 | 122.9141 | 122.8088 | 122.8409 | -123.0286 | -122.9828 | 123.0972 | 123.1293 | 57.3807 | 55.4535
348.0312 | 123.2529 | -59.4086 | 63.501 | 0.022479 | -0.00079271 | 0.051899 | 0.073668 | 0.014615 | -0.0073817 | 0.0045582 | 0.25874 | -0.0018616 | 0.06045 | 0.027412 | -0.01598 | 0.0067052 | -0.0019036 | -2.0325 | 63.4094 | -59.5001 | 63.6475 | -59.4543 | -59.7244 | -59.7977 | -4.0512 | 63.4415 | -59.4727 | 63.6978 | -59.3628 | -59.5459 | -59.4955 | -0.091553 | -0.091553 | 0.14648 | -0.045777 | -0.3891 | -0.31586 | -0.29755 | -0.2243 | -0.064087 | -0.05951 | 0.19684 | 0.045776 | -0.086975 | -0.13733 | -0.022888 | -0.073242 | 0.045776 | 123.1476 | 0.10986 | 123.1705 | 122.9095 | 122.9141 | 122.818 | 122.85 | -123.0011 | -122.9736 | 123.056 | 123.1064 | 57.3761 | 55.3574
348.9531 | 123.2437 | -59.436 | 63.4735 | 0.0072204 | -0.00079271 | 0.048695 | 0.091826 | -0.0099516 | -0.0052457 | -0.0061228 | -0.12273 | 0.012024 | 0.056178 | 0.037025 | -0.013843 | 0.01525 | 0.010913 | -2.2202 | 63.4094 | -59.5642 | 63.7161 | -59.3857 | -59.7153 | -59.697 | -4.2435 | 63.414 | -59.4864 | 63.7115 | -59.5001 | -59.6375 | -59.5505 | -0.12817 | -0.064087 | 0.24261 | 0.050354 | -0.26093 | -0.27924 | -0.13275 | -0.15106 | -0.050354 | -0.05951 | 0.23804 | -0.064087 | -0.11444 | -0.20142 | -0.064087 | -0.15106 | 0.17853 | 123.2803 | -0.013733 | 123.1979 | 122.9736 | 122.9004 | 122.8455 | 122.85 | -123.0377 | -122.9599 | 123.1522 | 123.1476 | 57.2159 | 55.1926
350.0312 | 123.1796 | -59.4269 | 63.5101 | 0.0072204 | -0.00079271 | 0.054036 | 0.073668 | 0.0039344 | -0.0095177 | 0.0088302 | 0.24348 | 0.0024114 | 0.0722 | 0.044502 | -0.017048 | 0.0099092 | -0.0061756 | -2.1332 | 63.4094 | -59.491 | 63.6246 | -59.5276 | -59.7244 | -59.7839 | -4.2389 | 63.4506 | -59.4406 | 63.62 | -58.9828 | -59.3124 | -59.6054 | -0.064087 | -0.10071 | 0.11444 | -0.10071 | -0.35706 | -0.29755 | -0.29297 | -0.23346 | -0.013733 | -0.059509 | 0.10986 | 0.44403 | -0.17853 | 0.11444 | -0.16479 | 0.12817 | -0.036621 | 123.1155 | 0.45776 | 123.0606 | 122.9004 | 122.8912 | 122.8363 | 122.8775 | -123.0011 | -122.9507 | 123.0515 | 123.0469 | 57.2937 | 55.188
350.9688 | 123.2025 | -59.4131 | 63.5788 | 0.052997 | 0.0056153 | 0.039082 | 0.070463 | 0.0050024 | -0.0041777 | -0.0061228 | 0.21297 | 0.0045474 | 0.063655 | 0.044502 | -0.02132 | 0.0077732 | -0.027539 | -2.2293 | 63.4232 | -59.4635 | 63.6429 | -59.4086 | -59.7382 | -59.6878 | -4.454 | 63.4781 | -59.4223 | 63.7482 | -59.4589 | -59.5367 | -59.523 | -0.050354 | -0.15564 | 0.064087 | 0.004578 | -0.27466 | -0.32501 | -0.2243 | -0.27466 | -0.009155 | -0.10071 | 0.16937 | -0.045776 | -0.10986 | -0.1236 | -0.10071 | -0.11444 | 0.054932 | 123.1064 | -0.036621 | 123.1705 | 122.8867 | 122.9004 | 122.8363 | 122.8912 | -123.0423 | -123.0011 | 123.056 | 123.1613 | 57.1838 | 54.9591
352.0312 | 123.2666 | -59.4131 | 63.533 | -0.0080386 | -0.0029297 | 0.049763 | 0.07794 | -0.01102 | 0.0097083 | -0.0071918 | 0.24348 | -0.0093376 | 0.066859 | 0.037025 | -0.014912 | 0.0045682 | 0.0013004 | -2.3483 | 63.3865 | -59.5139 | 63.7253 | -59.4269 | -59.7153 | -59.7107 | -4.6326 | 63.4552 | -59.4589 | 63.7253 | -59.4498 | -59.5413 | -59.523 | -0.10071 | -0.14648 | 0.19226 | -0.013733 | -0.29755 | -0.30212 | -0.19684 | -0.20142 | -0.045776 | -0.07782 | 0.19226 | -0.036621 | -0.10986 | -0.12817 | -0.064087 | -0.082398 | 0.086975 | 123.2391 | 0.009155 | 123.1842 | 122.9004 | 122.9141 | 122.7997 | 122.8683 | -123.0469 | -122.9919 | 123.1384 | 123.1384 | 57.0648 | 54.7806
352.9531 | 123.2071 | -59.4406 | 63.5056 | 0.052997 | 0.0045473 | 0.048695 | 0.07794 | -0.01102 | 0.0065043 | -0.0071918 | 0.029861 | 0.01416 | 0.071131 | 0.051979 | -0.0020938 | 0.0099092 | -0.015789 | -2.4628 | 63.3545 | -59.491 | 63.5971 | -59.4452 | -59.7656 | -59.7336 | -4.8431 | 63.4506 | -59.4635 | 63.707 | -59.4818 | -59.5734 | -59.5093 | -0.050354 | -0.15106 | 0.091553 | -0.004577 | -0.29297 | -0.32501 | -0.24262 | -0.27466 | -0.022888 | -0.054931 | 0.20142 | -0.041199 | -0.068664 | -0.13275 | -0.045776 | -0.10986 | 0.045777 | 123.0881 | -0.018311 | 123.1705 | 122.8455 | 122.9141 | 122.7951 | 122.8912 | -122.9965 | -122.9691 | 123.0377 | 123.1476 | 56.9778 | 54.5975
354.0312 | 123.23 | -59.4131 | 63.533 | 0.15981 | 0.021637 | 0.056172 | 0.076872 | -0.022769 | -0.0063137 | -0.0050548 | 0.04512 | 0.0034794 | 0.067927 | 0.063728 | -0.010639 | 0.016318 | -0.020062 | -2.504 | 63.4186 | -59.491 | 63.6795 | -59.3857 | -59.7153 | -59.6786 | -5.0446 | 63.4735 | -59.4681 | 63.7299 | -59.4589 | -59.491 | -59.5367 | -0.07782 | -0.11444 | 0.14648 | 0.027466 | -0.2655 | -0.30212 | -0.18768 | -0.2243 | -0.054932 | -0.059509 | 0.19684 | -0.045776 | -0.1236 | -0.07782 | -0.068664 | -0.022888 | 0.10529 | 123.1705 | 0.009156 | 123.1979 | 122.9095 | 122.9416 | 122.8317 | 122.8867 | -123.024 | -123.0011 | 123.0927 | 123.143 | 56.9092 | 54.3686
354.9531 | 123.2574 | -59.436 | 63.5422 | 0.11403 | 0.0056153 | 0.051899 | 0.080076 | -0.00033857 | -0.00097271 | -0.0136 | 0.04512 | -0.0039976 | 0.065791 | 0.046638 | -0.022388 | 0.0013642 | -0.015789 | -2.623 | 63.3728 | -59.5139 | 63.6063 | -59.3536 | -59.7473 | -59.6832 | -5.2139 | 63.446 | -59.4452 | 63.7756 | -59.4269 | -59.5367 | -59.5001 | -0.07782 | -0.16937 | 0.064087 | 0.082397 | -0.24719 | -0.31128 | -0.16937 | -0.23346 | -0.009155 | -0.09613 | 0.23346 | 0.009155 | -0.064087 | -0.10071 | -0.054932 | -0.091553 | 0.16022 | 123.1201 | 0.01831 | 123.2208 | 122.8867 | 122.8912 | 122.8088 | 122.8821 | -123.056 | -122.9874 | 123.0423 | 123.2117 | 56.813 | 54.2221
356.0312 | 122.9782 | -59.4772 | 63.4964 | 0.022479 | -0.0050657 | 0.061512 | 0.089689 | -0.0088836 | -0.022336 | 0.00028524 | -0.21428 | 0.0034794 | 0.075404 | 0.040229 | -0.0085028 | 0.018454 | -0.0061756 | -2.71 | 63.4369 | -59.5413 | 63.8031 | -59.2941 | -59.6191 | -59.5917 | -5.5527 | 63.4964 | -59.4818 | 63.6246 | -59.6054 | -59.6512 | -59.5779 | -0.064087 | -0.059509 | 0.3067 | 0.18311 | -0.11444 | -0.14191 | -0.050354 | -0.07782 | -0.004578 | 0 | 0.12817 | -0.12817 | -0.10071 | -0.17395 | -0.09613 | -0.16937 | 0.24719 | 123.3444 | -0.1236 | 123.1064 | 122.9782 | 122.9782 | 122.9141 | 122.9736 | -123.0377 | -122.9782 | 123.2803 | 123.1018 | 56.7673 | 53.9246
356.9531 | 123.1979 | -59.3994 | 63.5239 | 0.052997 | 0.00027529 | 0.051899 | 0.069395 | 0.021024 | 0.0011633 | -0.00078276 | -0.00065608 | 0.0045474 | 0.076472 | 0.04557 | -0.0063668 | 0.013113 | -0.0019036 | -2.7557 | 63.4048 | -59.4681 | 63.6246 | -59.3628 | -59.7198 | -59.7198 | -5.6488 | 63.4598 | -59.4681 | 63.6978 | -59.4406 | -59.5825 | -59.523 | -0.068665 | -0.11902 | 0.10071 | 0.036621 | -0.32044 | -0.32044 | -0.25177 | -0.25177 | -0.068665 | -0.064087 | 0.17395 | -0.041199 | -0.1236 | -0.18311 | -0.054931 | -0.11444 | 0.10529 | 123.0927 | 0.027466 | 123.1659 | 122.8729 | 122.9279 | 122.8043 | 122.8592 | -122.9919 | -122.9919 | 123.024 | 123.0972 | 56.6437 | 53.7506
357.9531 | 123.2117 | -59.4406 | 63.5284 | -0.023297 | 0.00027529 | 0.056172 | 0.073668 | -0.0046106 | 0.0097083 | -0.012532 | -0.12273 | 0.0013434 | 0.067927 | 0.017799 | -0.012775 | 0.026999 | 0.0034374 | -2.8702 | 63.414 | -59.5001 | 63.7115 | -59.3536 | -59.6649 | -59.697 | -5.7907 | 63.4598 | -59.4589 | 63.7207 | -59.4589 | -59.5642 | -59.5688 | -0.059509 | -0.11444 | 0.18311 | 0.086975 | -0.25635 | -0.2243 | -0.19684 | -0.1648 | -0.01831 | -0.068664 | 0.19226 | -0.01831 | -0.12817 | -0.1236 | -0.10986 | -0.10529 | 0.14648 | 123.2117 | 0 | 123.1796 | 122.9141 | 122.9187 | 122.8546 | 122.9004 | -123.0286 | -122.9874 | 123.1522 | 123.1613 | 56.5704 | 53.6499
358.9531 | 123.2254 | -59.4452 | 63.533 | -0.084332 | 0.0045473 | 0.054036 | 0.080076 | -0.01102 | -0.0052457 | -0.0039868 | -0.21428 | 0.0056154 | 0.087153 | 0.066932 | -0.013843 | 0.023794 | -0.018994 | -2.9526 | 63.4186 | -59.5184 | 63.6887 | -59.3445 | -59.6695 | -59.6649 | -6.0333 | 63.4644 | -59.4727 | 63.7115 | -59.436 | -59.5917 | -59.4681 | -0.073243 | -0.11444 | 0.15564 | 0.10071 | -0.21973 | -0.22431 | -0.14648 | -0.15106 | -0.027466 | -0.068665 | 0.17853 | 0.009155 | -0.022889 | -0.14649 | 0.004577 | -0.11902 | 0.17395 | 123.2071 | 0.036621 | 123.1842 | 122.937 | 122.937 | 122.8638 | 122.9095 | -123.0515 | -123.0057 | 123.1338 | 123.1567 | 56.4926 | 53.4119
360.0312 | 123.23 | -59.3765 | 63.5376 | 0.098773 | 0.0045473 | 0.051899 | 0.069395 | -0.0056786 | -0.013791 | -0.0050548 | 0.18245 | -0.0007936 | 0.089289 | 0.048774 | -0.011707 | 0.0077732 | -0.015789 | -2.9984 | 63.446 | -59.4406 | 63.6703 | -59.3811 | -59.729 | -59.6649 | -6.0928 | 63.4552 | -59.4315 | 63.7619 | -59.3948 | -59.4772 | -59.4727 | -0.064087 | -0.091553 | 0.13275 | -0.004578 | -0.28839 | -0.35248 | -0.2243 | -0.28839 | -0.054932 | -0.082398 | 0.2243 | -0.01831 | -0.09613 | -0.10071 | -0.041198 | -0.045776 | 0.059509 | 123.111 | 0.036622 | 123.1934 | 122.8867 | 122.8867 | 122.8226 | 122.8317 | -122.9782 | -122.9691 | 123.0469 | 123.1384 | 56.3782 | 53.2837
360.9688 | 123.1613 | -59.3765 | 63.6063 | 0.11403 | -0.010406 | 0.042286 | 0.076872 | 0.0092744 | -0.015927 | -0.00078276 | -0.046432 | 0.0088204 | 0.061518 | 0.02848 | -0.0042298 | 0.024863 | -0.00083564 | -3.0533 | 63.4827 | -59.4818 | 63.7939 | -59.2621 | -59.5551 | -59.61 | -6.4133 | 63.5468 | -59.4406 | 63.652 | -59.3857 | -59.61 | -59.4955 | -0.10529 | -0.1236 | 0.18768 | 0.11444 | -0.23346 | -0.17853 | -0.12817 | -0.073242 | -0.064087 | -0.059509 | 0.045777 | -0.009155 | -0.11902 | -0.23346 | -0.054931 | -0.16937 | 0.21973 | 123.2758 | 0.054932 | 123.0927 | 122.9645 | 122.9874 | 122.8592 | 122.9233 | -123.0881 | -123.0469 | 123.1705 | 123.0286 | 56.3232 | 52.9633
362.0312 | 123.175 | -59.3857 | 63.6063 | 0.14455 | 0.0056153 | 0.042286 | 0.07794 | 0.0071384 | -0.0063137 | -0.0029188 | 0.16719 | -0.0061336 | 0.068995 | 0.039161 | -0.0052988 | -0.0018398 | -0.0083126 | -3.1403 | 63.4781 | -59.4315 | 63.6841 | -59.3079 | -59.7244 | -59.6283 | -6.4957 | 63.5147 | -59.4269 | 63.7299 | -59.4086 | -59.5551 | -59.4589 | -0.045777 | -0.12817 | 0.07782 | 0.07782 | -0.24262 | -0.33875 | -0.19684 | -0.29297 | -0.041199 | -0.091553 | 0.1236 | -0.022888 | -0.073242 | -0.16937 | -0.032043 | -0.12817 | 0.1236 | 123.1155 | 0.018311 | 123.1567 | 122.9095 | 122.9416 | 122.8638 | 122.9004 | -123.0377 | -123.0331 | 123.0698 | 123.1155 | 56.2454 | 52.89
362.9531 | 123.2574 | -59.3948 | 63.5422 | 0.022479 | -0.0018617 | 0.052968 | 0.087553 | -0.0056786 | -0.0095177 | -0.0093278 | 0.12141 | -0.0050656 | 0.0722 | 0.044502 | -0.0074348 | 0.012045 | -0.014721 | -3.3417 | 63.3911 | -59.4818 | 63.6429 | -59.4131 | -59.6878 | -59.7885 | -6.7108 | 63.4415 | -59.4269 | 63.7482 | -59.3628 | -59.5779 | -59.4086 | -0.086976 | -0.15106 | 0.10071 | -0.018311 | -0.39368 | -0.29297 | -0.3067 | -0.20599 | -0.032044 | -0.10071 | 0.20599 | 0.032043 | -0.013733 | -0.18311 | 0.018311 | -0.15106 | 0.068665 | 123.1247 | 0.064087 | 123.175 | 122.8729 | 122.8683 | 122.7859 | 122.8363 | -123.024 | -122.9691 | 123.0377 | 123.143 | 56.0532 | 52.684
364.0312 | 123.0423 | -59.3719 | 63.6063 | 0.17507 | -0.0018617 | 0.048695 | 0.076872 | -0.00033857 | -0.034085 | 0.0013532 | 0.41133 | 0.0002754 | 0.083949 | 0.042366 | -0.0042298 | 0.019522 | -0.013653 | -3.392 | 63.4644 | -59.4681 | 63.7711 | -59.2621 | -59.5734 | -59.5551 | -7.0084 | 63.5284 | -59.4223 | 63.62 | -59.3216 | -59.3124 | -59.4772 | -0.096131 | -0.14191 | 0.16479 | 0.10986 | -0.18311 | -0.20142 | -0.086975 | -0.10528 | -0.050354 | -0.07782 | 0.013733 | 0.050354 | -0.10529 | 0.059509 | -0.054932 | 0.10986 | 0.20599 | 123.2391 | 0.10071 | 123.0423 | 122.9324 | 122.9507 | 122.8363 | 122.9004 | -123.0743 | -123.0286 | 123.143 | 122.9919 | 55.9799 | 52.3636
364.9531 | 123.2071 | -59.3628 | 63.5696 | -0.0080386 | 0.0024113 | 0.047627 | 0.070463 | -0.0056786 | 0.0054353 | -0.0082598 | 0.090897 | -0.011475 | 0.068995 | 0.029548 | -0.0063668 | 0.0088412 | -0.00083564 | -3.566 | 63.414 | -59.4727 | 63.7253 | -59.3536 | -59.61 | -59.7153 | -7.1686 | 63.4872 | -59.4131 | 63.7711 | -59.4589 | -59.5642 | -59.4727 | -0.10986 | -0.15564 | 0.15564 | 0.009155 | -0.35248 | -0.24719 | -0.24262 | -0.13733 | -0.050354 | -0.082397 | 0.20142 | -0.09613 | -0.10986 | -0.20142 | -0.059509 | -0.15106 | 0.11902 | 123.1979 | -0.045776 | 123.1842 | 122.8867 | 122.9004 | 122.7768 | 122.85 | -123.0423 | -122.9828 | 123.0881 | 123.1338 | 55.7968 | 52.1942
366.0312 | 123.1201 | -59.3948 | 63.6154 | 0.022479 | -0.0082697 | 0.048695 | 0.096098 | -0.0056786 | 0.0065043 | 0.0045582 | -0.07695 | 0.0056154 | 0.066859 | 0.064796 | -0.0074348 | 0.013113 | -0.011517 | -3.6621 | 63.4552 | -59.4818 | 63.7802 | -59.285 | -59.5825 | -59.5871 | -7.4707 | 63.5284 | -59.4543 | 63.6658 | -59.4864 | -59.6924 | -59.5093 | -0.086976 | -0.16022 | 0.16479 | 0.10986 | -0.19226 | -0.18768 | -0.10529 | -0.10071 | -0.05951 | -0.086975 | 0.050354 | -0.091553 | -0.11444 | -0.29755 | -0.054931 | -0.23804 | 0.19684 | 123.262 | -0.032043 | 123.1201 | 122.937 | 122.9828 | 122.85 | 122.9233 | -123.0972 | -123.0698 | 123.175 | 123.0606 | 55.7327 | 51.9241
366.9531 | 123.2117 | -59.3765 | 63.5468 | 0.0072204 | 0.0077523 | 0.051899 | 0.079008 | 0.015683 | -0.012723 | -0.0093278 | 0.075638 | -0.0039976 | 0.061518 | 0.057319 | -0.0042298 | 0.024863 | -0.00083564 | -3.7994 | 63.4323 | -59.4681 | 63.739 | -59.3582 | -59.6558 | -59.6695 | -7.5623 | 63.4689 | -59.4452 | 63.8672 | -59.5367 | -59.5322 | -59.4131 | -0.091553 | -0.11444 | 0.19226 | 0.018311 | -0.29297 | -0.27924 | -0.20142 | -0.18768 | -0.068664 | -0.07782 | 0.32043 | -0.16022 | -0.036621 | -0.15564 | 0.032043 | -0.086976 | 0.10986 | 123.2071 | -0.091553 | 123.3124 | 122.9004 | 122.9141 | 122.8088 | 122.8455 | -123.0148 | -122.9919 | 123.1155 | 123.2437 | 55.5771 | 51.8143
368.0312 | 123.1567 | -59.3536 | 63.6703 | 0.022479 | 0.0098883 | 0.043354 | 0.073668 | -0.0024746 | -0.022336 | -0.010396 | -0.00065608 | 0.0013434 | 0.070063 | 0.024208 | 4.2208e-05 | 0.0077732 | -0.0061756 | -3.7994 | 63.4918 | -59.4452 | 63.8031 | -59.2804 | -59.5505 | -59.5642 | -7.8323 | 63.5422 | -59.3948 | 63.6703 | -59.4177 | -59.61 | -59.4818 | -0.091552 | -0.17853 | 0.13275 | 0.073242 | -0.21057 | -0.19684 | -0.11902 | -0.10529 | -0.041198 | -0.12817 | 0 | -0.064087 | -0.12817 | -0.25635 | -0.086976 | -0.21515 | 0.16479 | 123.2483 | -0.022889 | 123.0652 | 122.937 | 122.937 | 122.8455 | 122.8958 | -123.1155 | -123.0652 | 123.1567 | 123.024 | 55.5542 | 51.5213
368.9531 | 123.2071 | -59.3674 | 63.5742 | -0.053815 | 0.0098883 | 0.054036 | 0.076872 | -0.0056786 | -0.010586 | -0.011464 | 0.15193 | 0.0002754 | 0.068995 | 0.015663 | -0.0063668 | 0.023794 | 0.00023236 | -3.9642 | 63.4415 | -59.4452 | 63.7024 | -59.4269 | -59.697 | -59.729 | -7.9697 | 63.4827 | -59.4086 | 63.7527 | -59.404 | -59.5001 | -59.5139 | -0.077819 | -0.13275 | 0.12817 | -0.059509 | -0.36163 | -0.32959 | -0.28381 | -0.25177 | -0.041198 | -0.091553 | 0.17853 | -0.036621 | -0.14648 | -0.13275 | -0.10529 | -0.091553 | 0.01831 | 123.1476 | 0.004577 | 123.1613 | 122.8867 | 122.8912 | 122.8088 | 122.85 | -123.0194 | -122.9828 | 123.0698 | 123.1201 | 55.4031 | 51.3977
370.0312 | 123.2437 | -59.3216 | 63.588 | 0.068255 | -0.0072017 | 0.049763 | 0.045897 | -0.014224 | 0.0075723 | -0.00078276 | 0.30452 | 0.0066834 | 0.064723 | 0.072273 | -0.011707 | -0.010385 | -0.0083126 | -4.0237 | 63.5056 | -59.4269 | 63.5696 | -59.6054 | -59.6237 | -59.7107 | -8.1757 | 63.5101 | -59.3857 | 63.7985 | -59.2896 | -59.4406 | -59.3903 | -0.10529 | -0.082398 | -0.018311 | -0.28381 | -0.3891 | -0.30212 | -0.28381 | -0.19684 | -0.064087 | -0.07782 | 0.21057 | 0.032043 | -0.068665 | -0.11902 | -0.004578 | -0.054932 | -0.17853 | 122.9965 | 0.09613 | 123.1842 | 122.9324 | 122.8958 | 122.8271 | 122.8317 | -123.0148 | -122.9736 | 122.8912 | 123.1201 | 55.2979 | 51.1459
370.9531 | 123.2117 | -59.3536 | 63.5834 | -0.14537 | -0.0029297 | 0.050831 | 0.075804 | -0.0067466 | -0.0073817 | -0.011464 | 0.12141 | 0.0066834 | 0.076472 | 0.040229 | -0.0095708 | 0.013113 | 0.0098454 | -4.2755 | 63.4598 | -59.4315 | 63.739 | -59.3948 | -59.697 | -59.7015 | -8.3862 | 63.4964 | -59.3948 | 63.8123 | -59.4086 | -59.491 | -59.4543 | -0.07782 | -0.1236 | 0.15564 | -0.041198 | -0.3479 | -0.34332 | -0.27008 | -0.2655 | -0.041198 | -0.086975 | 0.22888 | -0.054931 | -0.10071 | -0.13733 | -0.05951 | -0.096131 | 0.036622 | 123.1705 | -0.013733 | 123.2071 | 122.8912 | 122.8912 | 122.8134 | 122.85 | -123.0148 | -122.9782 | 123.0927 | 123.1659 | 55.0781 | 50.9674
371.9531 | 123.2529 | -59.3582 | 63.5651 | -0.40477 | 0.018433 | 0.051899 | 0.080076 | -0.00033857 | -0.010586 | 0.0024222 | 0.029861 | 0.0013434 | 0.062587 | 0.05091 | -0.014912 | 0.010977 | -0.022198 | -4.216 | 63.4277 | -59.4406 | 63.6658 | -59.3628 | -59.697 | -59.761 | -8.6838 | 63.4781 | -59.3903 | 63.7482 | -59.2941 | -59.523 | -59.4086 | -0.082398 | -0.13733 | 0.10071 | -0.004578 | -0.40283 | -0.33874 | -0.32043 | -0.25635 | -0.032044 | -0.086975 | 0.18311 | 0.064087 | -0.050354 | -0.16479 | -0.01831 | -0.13275 | 0.07782 | 123.1064 | 0.096131 | 123.1384 | 122.8683 | 122.8683 | 122.7859 | 122.8363 | -123.0057 | -122.9553 | 123.024 | 123.1064 | 55.1422 | 50.6744
373.0312 | 123.2391 | -59.317 | 63.6154 | 0.068255 | 0.0045473 | 0.045491 | 0.080076 | -0.0014066 | -0.029812 | -0.00078276 | 0.04512 | 0.0056154 | 0.074336 | 0.0071182 | -0.017048 | 0.019522 | -0.00083564 | -4.4952 | 63.4735 | -59.4131 | 63.9175 | -59.317 | -59.9442 | -59.6466 | -8.7433 | 63.4964 | -59.3719 | 63.8397 | -59.3033 | -59.4177 | -59.3674 | -0.09613 | -0.14191 | 0.30212 | 0 | -0.32959 | -0.62714 | -0.23346 | -0.53101 | -0.054931 | -0.11902 | 0.22431 | 0.013733 | -0.050354 | -0.10071 | 0.004577 | -0.045777 | 0.09613 | 123.3307 | 0.068664 | 123.2117 | 122.8867 | 122.8683 | 122.7905 | 122.8134 | -123.0286 | -122.9874 | 123.2346 | 123.1567 | 54.8218 | 50.5737
373.9531 | 123.3261 | -59.3262 | 63.652 | -0.023297 | 0.0013433 | 0.042286 | 0.07794 | 0.0028664 | -0.00097271 | 0.0024222 | 0.22823 | 0.0013434 | 0.063655 | 0.047706 | 4.2208e-05 | 0.0099092 | -0.028607 | -4.7058 | 63.4827 | -59.4269 | 63.7527 | -59.3124 | -59.6008 | -59.6924 | -9.1232 | 63.5376 | -59.3811 | 63.739 | -59.3399 | -59.5688 | -59.436 | -0.10071 | -0.16937 | 0.10071 | 0.013733 | -0.36621 | -0.27466 | -0.2655 | -0.17395 | -0.054932 | -0.11444 | 0.086975 | -0.013733 | -0.10986 | -0.24262 | -0.054931 | -0.18768 | 0.11444 | 123.1796 | 0.041199 | 123.1201 | 122.9095 | 122.9187 | 122.8088 | 122.8638 | -123.0789 | -123.0331 | 123.0789 | 123.0652 | 54.6204 | 50.2029
375.0312 | 123.1842 | -59.3582 | 63.6475 | 0.037738 | 0.0045473 | 0.064717 | 0.075804 | 0.01141 | -0.0095177 | -0.020009 | -0.15324 | 0.01416 | 0.051905 | 0.072273 | 0.0043152 | 0.017386 | -0.00083564 | -4.9255 | 63.501 | -59.4543 | 63.8397 | -59.1476 | -59.5413 | -59.5139 | -9.5032 | 63.5834 | -59.4315 | 63.5788 | -59.111 | -59.6649 | -59.5001 | -0.096131 | -0.14648 | 0.19226 | 0.21057 | -0.15564 | -0.18311 | -0.059509 | -0.086975 | -0.073243 | -0.064087 | -0.068665 | 0.24719 | -0.14191 | -0.3067 | -0.068664 | -0.23346 | 0.3067 | 123.2941 | 0.32043 | 123.0103 | 122.9553 | 123.0148 | 122.8592 | 122.9416 | -123.1018 | -123.0789 | 123.1979 | 122.937 | 54.4327 | 49.855
375.9531 | 123.2346 | -59.3491 | 63.588 | 0.037738 | 0.015228 | 0.045491 | 0.069395 | -0.0035426 | -0.015927 | -0.011464 | 0.014603 | 0.0002754 | 0.064723 | 0.073341 | -0.010639 | 0.0077732 | -0.011517 | -4.985 | 63.4644 | -59.4177 | 63.739 | -59.3857 | -59.642 | -59.697 | -9.494 | 63.5376 | -59.3765 | 63.7756 | -59.3445 | -59.5139 | -59.3994 | -0.068665 | -0.1236 | 0.15106 | -0.036621 | -0.3479 | -0.29297 | -0.27923 | -0.2243 | -0.027466 | -0.050354 | 0.18768 | 0.004578 | -0.050354 | -0.16479 | -0.022888 | -0.13733 | 0.032044 | 123.1567 | 0.032044 | 123.1522 | 122.8821 | 122.9141 | 122.8134 | 122.8867 | -123.0057 | -122.9645 | 123.0881 | 123.1247 | 54.364 | 49.855
377.0312 | 123.1476 | -59.3216 | 63.6932 | 0.17507 | 0.013092 | 0.049763 | 0.0726 | 0.018887 | -0.0020407 | -0.0061228 | 0.13667 | 0.015228 | 0.066859 | 0.044502 | -0.0063668 | 0.016318 | -0.0072446 | -5.0949 | 63.533 | -59.3903 | 63.7756 | -59.23 | -59.5459 | -59.5322 | -9.7778 | 63.5971 | -59.3719 | 63.7115 | -59.3262 | -59.5459 | -59.4498 | -0.068665 | -0.16022 | 0.082398 | 0.091552 | -0.21057 | -0.2243 | -0.14191 | -0.15564 | -0.050354 | -0.09613 | 0.018311 | -0.004578 | -0.12817 | -0.2243 | -0.07782 | -0.17395 | 0.16022 | 123.1659 | 0.045776 | 123.0835 | 122.9233 | 122.9691 | 122.8546 | 122.9187 | -123.0835 | -123.0652 | 123.0972 | 123.0331 | 54.2267 | 49.5438
377.9531 | 123.1888 | -59.3216 | 63.6292 | 0.037738 | -0.0018617 | 0.060444 | 0.071531 | 0.0017974 | 0.0054353 | -0.012532 | 0.090897 | 0.0056154 | 0.070063 | 0.05091 | -0.0020938 | 0.010977 | -0.026471 | -5.3513 | 63.4644 | -59.4131 | 63.7344 | -59.404 | -59.6191 | -59.6924 | -9.874 | 63.5422 | -59.3445 | 63.7802 | -59.3033 | -59.4818 | -59.4086 | -0.091553 | -0.1648 | 0.10529 | -0.082398 | -0.37079 | -0.29755 | -0.27924 | -0.20599 | -0.022888 | -0.086975 | 0.15106 | 0.01831 | -0.086975 | -0.16022 | -0.064087 | -0.13733 | 0.009155 | 123.1476 | 0.041198 | 123.1247 | 122.8775 | 122.8867 | 122.7859 | 122.8638 | -123.0423 | -122.9736 | 123.056 | 123.1018 | 53.9703 | 49.4476
379.0312 | 123.1613 | -59.3262 | 63.7207 | 0.15981 | 0.00027529 | 0.044423 | 0.076872 | -0.00033857 | 0.0043673 | -0.0082598 | -0.046432 | 0.016296 | 0.073268 | 0.057319 | -0.012775 | 0.013113 | 0.010913 | -5.4886 | 63.5788 | -59.404 | 63.8855 | -59.166 | -59.4864 | -59.5413 | -10.2127 | 63.6246 | -59.3491 | 63.7482 | -59.3308 | -59.5596 | -59.3948 | -0.07782 | -0.14191 | 0.16479 | 0.16022 | -0.21515 | -0.16022 | -0.13733 | -0.082397 | -0.022888 | -0.09613 | 0.027466 | -0.004578 | -0.068664 | -0.23346 | -0.045776 | -0.21057 | 0.23804 | 123.2895 | 0.01831 | 123.0972 | 122.9828 | 122.9736 | 122.905 | 122.9507 | -123.1247 | -123.0698 | 123.2117 | 123.0743 | 53.8376 | 49.1135
379.9531 | 123.2162 | -59.2987 | 63.7024 | -0.0080386 | 0.0045473 | 0.050831 | 0.073668 | -0.018497 | 0.0043673 | 0.00028524 | 0.13667 | 0.0024114 | 0.0722 | 0.066932 | -0.0052988 | 0.0077732 | -0.0040396 | -5.6122 | 63.5193 | -59.3628 | 63.7802 | -59.3079 | -59.6008 | -59.6237 | -10.2631 | 63.5834 | -59.3353 | 63.826 | -59.2712 | -59.404 | -59.4086 | -0.064087 | -0.18311 | 0.077819 | -0.009155 | -0.32501 | -0.30212 | -0.26092 | -0.23804 | -0.036621 | -0.11902 | 0.1236 | 0.027466 | -0.10986 | -0.10529 | -0.073242 | -0.068665 | 0.054932 | 123.143 | 0.064087 | 123.1613 | 122.8821 | 122.9187 | 122.818 | 122.8821 | -123.0652 | -123.0377 | 123.0789 | 123.1247 | 53.6865 | 49.0356
381.0312 | 123.1293 | -59.3262 | 63.7299 | 0.022479 | -0.0039977 | 0.04015 | 0.082213 | -0.0035426 | 0.0011633 | -0.014668 | 0.70125 | 0.013092 | 0.067927 | 0.06266 | -0.0063668 | -0.0018398 | 0.014118 | -5.7953 | 63.5925 | -59.3811 | 63.9313 | -59.166 | -59.4635 | -59.4589 | -10.8215 | 63.6703 | -59.3765 | 63.707 | -59.3811 | -59.5139 | -59.4269 | -0.054932 | -0.13733 | 0.20142 | 0.16022 | -0.13275 | -0.13733 | -0.077819 | -0.082397 | -0.050354 | -0.059509 | -0.022888 | -0.054932 | -0.10071 | -0.18768 | -0.050354 | -0.13733 | 0.21515 | 123.3124 | -0.004578 | 123.0835 | 122.9736 | 123.0469 | 122.9187 | 122.9965 | -123.111 | -123.1064 | 123.2574 | 123.0331 | 53.5309 | 48.5046
381.9531 | 123.2346 | -59.2987 | 63.6475 | -0.099591 | 0.0066833 | 0.042286 | 0.075804 | 0.0017974 | -0.020199 | -0.017873 | 0.16719 | 0.010956 | 0.070063 | 0.05091 | -0.0095708 | 0.0088412 | -0.020062 | -6.0562 | 63.4918 | -59.3628 | 63.7802 | -59.2712 | -59.5963 | -59.5871 | -10.8078 | 63.5559 | -59.3399 | 63.8535 | -59.2987 | -59.3491 | -59.4177 | -0.064087 | -0.15564 | 0.13275 | 0.027466 | -0.28839 | -0.29755 | -0.2243 | -0.23346 | -0.041199 | -0.091553 | 0.20599 | 0 | -0.11902 | -0.050354 | -0.07782 | -0.009155 | 0.091553 | 123.143 | 0.041199 | 123.1934 | 122.8546 | 122.8958 | 122.7905 | 122.8546 | -123.0103 | -122.9874 | 123.0789 | 123.1522 | 53.2425 | 48.4909
382.9531 | 123.2208 | -59.3033 | 63.652 | 0.098773 | 0.0077523 | 0.048695 | 0.076872 | 0.0082064 | 0.019321 | -0.00078276 | 0.15193 | 0.0024114 | 0.078608 | 0.051979 | -0.0095708 | 0.017386 | -0.0029716 | -6.189 | 63.501 | -59.3719 | 63.7482 | -59.2804 | -59.6008 | -59.6283 | -11.1237 | 63.5513 | -59.3262 | 63.7665 | -59.2941 | -59.4772 | -59.3719 | -0.068664 | -0.15106 | 0.09613 | 0.022888 | -0.32501 | -0.29755 | -0.25635 | -0.22888 | -0.022888 | -0.10071 | 0.11444 | 0.009156 | -0.068664 | -0.17395 | -0.045776 | -0.15106 | 0.091552 | 123.1201 | 0.032044 | 123.0927 | 122.8729 | 122.8775 | 122.8043 | 122.8546 | -123.024 | -122.9782 | 123.0515 | 123.0698 | 53.1143 | 48.1796
383.9531 | 123.2758 | -59.2667 | 63.6703 | 0.068255 | 0.0013433 | 0.054036 | 0.07794 | 0.0028664 | -0.0020407 | -0.0061228 | 0.18245 | -0.0050656 | 0.083949 | 0.048774 | -0.014912 | 0.013113 | -0.013653 | -6.4041 | 63.5422 | -59.3491 | 63.7665 | -59.3033 | -59.61 | -59.5963 | -11.2061 | 63.5788 | -59.3079 | 63.9038 | -59.2392 | -59.3353 | -59.3353 | -0.082397 | -0.12817 | 0.09613 | -0.036621 | -0.32959 | -0.34332 | -0.24719 | -0.26093 | -0.041198 | -0.091553 | 0.23346 | 0.027466 | -0.068664 | -0.068664 | -0.027466 | -0.027466 | 0.045776 | 123.1155 | 0.068664 | 123.2117 | 122.8912 | 122.8867 | 122.8088 | 122.8455 | -123.0194 | -122.9782 | 123.0331 | 123.1705 | 52.8625 | 48.0606
385.0312 | 123.0652 | -59.285 | 63.7299 | 0.11403 | -0.0082697 | 0.052968 | 0.080076 | -0.01102 | -0.0063137 | -0.0071918 | 0.12141 | 0.0034794 | 0.066859 | 0.05091 | -0.011707 | 0.014181 | -0.00083564 | -6.5826 | 63.6017 | -59.3628 | 63.9084 | -59.1476 | -59.4452 | -59.4818 | -11.5814 | 63.652 | -59.3353 | 63.7024 | -59.1705 | -59.2712 | -59.5367 | -0.07782 | -0.12817 | 0.17853 | 0.13733 | -0.19684 | -0.16022 | -0.11902 | -0.082397 | -0.050354 | -0.077819 | -0.027465 | 0.11444 | -0.25177 | 0.013733 | -0.20142 | 0.064087 | 0.21515 | 123.2712 | 0.16479 | 123.0377 | 122.9645 | 122.9874 | 122.8867 | 122.937 | -123.0927 | -123.0652 | 123.1934 | 122.9874 | 52.7023 | 47.7036
385.9531 | 123.2162 | -59.2667 | 63.6658 | 0.068255 | -0.0029297 | 0.049763 | 0.080076 | 0.012479 | -0.024472 | 0.0088302 | 0.15193 | -0.0007936 | 0.049769 | 0.058387 | -0.0074348 | 0.010977 | 0.0045054 | -6.8069 | 63.5559 | -59.3628 | 63.826 | -59.2163 | -59.5825 | -59.5322 | -11.7599 | 63.6108 | -59.3308 | 63.9084 | -59.3262 | -59.3948 | -59.3582 | -0.09613 | -0.10986 | 0.16022 | 0.050354 | -0.2655 | -0.31586 | -0.16937 | -0.21973 | -0.064087 | -0.054931 | 0.24262 | -0.059509 | -0.091552 | -0.12817 | -0.027465 | -0.064086 | 0.14648 | 123.1888 | 0.004578 | 123.2391 | 122.9187 | 122.9416 | 122.8226 | 122.8775 | -123.0286 | -122.9965 | 123.0927 | 123.175 | 52.4597 | 47.5067
387.0312 | 123.1155 | -59.2896 | 63.7436 | 0.11403 | 0.0077523 | 0.047627 | 0.083281 | -0.014224 | -0.0073817 | -0.014668 | -0.031174 | 0.0045474 | 0.074336 | 0.074409 | -0.0042298 | 0.010977 | -0.011517 | -6.9031 | 63.5971 | -59.3582 | 63.9404 | -59.1751 | -59.4818 | -59.4818 | -11.9797 | 63.6566 | -59.2941 | 63.8214 | -59.3308 | -59.4543 | -59.4315 | -0.068664 | -0.14648 | 0.19684 | 0.11444 | -0.19226 | -0.19226 | -0.1236 | -0.1236 | -0.004577 | -0.086975 | 0.07782 | -0.041199 | -0.14191 | -0.16479 | -0.13733 | -0.16022 | 0.18311 | 123.2986 | -0.036622 | 123.1155 | 122.9553 | 122.9507 | 122.8867 | 122.9462 | -123.1018 | -123.0377 | 123.23 | 123.111 | 52.3865 | 47.3099
387.9531 | 123.2071 | -59.2575 | 63.7024 | 0.083514 | 0.00027529 | 0.039082 | 0.079008 | 0.01141 | -0.00097271 | -0.0018508 | 0.15193 | 0.0066834 | 0.065791 | 0.056251 | -0.0074348 | 0.0088412 | -0.011517 | -7.1136 | 63.5742 | -59.3308 | 63.8077 | -59.2255 | -59.6146 | -59.5184 | -12.2452 | 63.5971 | -59.3079 | 63.913 | -59.2209 | -59.3308 | -59.3216 | -0.073243 | -0.12817 | 0.10529 | 0.032043 | -0.26093 | -0.35706 | -0.18768 | -0.28381 | -0.050354 | -0.10529 | 0.21057 | 0.036621 | -0.064087 | -0.073243 | -0.013733 | -0.022889 | 0.10529 | 123.1384 | 0.086975 | 123.2208 | 122.905 | 122.905 | 122.8317 | 122.8546 | -123.0331 | -123.0103 | 123.0652 | 123.1705 | 52.1439 | 47.0123
389.0312 | 123.1384 | -59.2621 | 63.7665 | 0.098773 | 0.0013433 | 0.046559 | 0.076872 | 0.0060704 | -0.0031087 | 0.0013532 | 0.44185 | 0.0056154 | 0.075404 | 0.051979 | -0.014912 | 0.022726 | 0.0098454 | -7.3013 | 63.6292 | -59.3399 | 63.9542 | -59.111 | -59.4406 | -59.3857 | -12.8265 | 63.6932 | -59.3353 | 63.7894 | -59.3399 | -59.404 | -59.4315 | -0.07782 | -0.13733 | 0.18768 | 0.15106 | -0.1236 | -0.17853 | -0.045776 | -0.10071 | -0.073242 | -0.073242 | 0.022889 | -0.07782 | -0.16937 | -0.14191 | -0.096131 | -0.068665 | 0.22888 | 123.2941 | -0.004578 | 123.1247 | 122.9691 | 123.0286 | 122.8912 | 122.9553 | -123.1064 | -123.1018 | 123.2162 | 123.0515 | 51.9608 | 46.4355
389.9531 | 123.2254 | -59.2575 | 63.6749 | 0.068255 | -0.0029297 | 0.046559 | 0.0726 | -0.0024746 | -0.019131 | -0.0018508 | -0.26006 | 0.0045474 | 0.07754 | 0.047706 | -0.010639 | 0.0088412 | -0.0040396 | -7.5165 | 63.5559 | -59.3399 | 63.8306 | -59.198 | -59.6283 | -59.4223 | -12.7258 | 63.6337 | -59.2941 | 63.8123 | -59.2987 | -59.4269 | -59.3445 | -0.082398 | -0.11902 | 0.15564 | 0.059509 | -0.1648 | -0.37079 | -0.082397 | -0.28839 | -0.036621 | -0.041199 | 0.13733 | -0.041199 | -0.086975 | -0.16937 | -0.050354 | -0.13275 | 0.14191 | 123.1705 | -0.004578 | 123.1064 | 122.8958 | 122.9279 | 122.8134 | 122.8912 | -123.0148 | -122.9691 | 123.0881 | 123.0698 | 51.741 | 46.5317
391.0312 | 123.1979 | -59.2346 | 63.7756 | -0.099591 | 0.0013433 | 0.058308 | 0.081144 | 0.0017974 | -0.021267 | -0.0093278 | 0.15193 | 0.0013434 | 0.070063 | 0.06266 | -0.0052988 | 0.018454 | -0.0072446 | -7.5714 | 63.6017 | -59.317 | 63.8351 | -59.1934 | -59.5459 | -59.4681 | -13.0005 | 63.652 | -59.2575 | 63.8992 | -59.2346 | -59.3353 | -59.3536 | -0.082398 | -0.17395 | 0.059509 | 0.041199 | -0.23346 | -0.31128 | -0.15106 | -0.22888 | -0.022888 | -0.1236 | 0.1236 | 0 | -0.11902 | -0.10071 | -0.096131 | -0.07782 | 0.1236 | 123.1522 | 0.022888 | 123.1567 | 122.9187 | 122.9095 | 122.8363 | 122.8867 | -123.0927 | -123.0331 | 123.0698 | 123.1338 | 51.6632 | 46.2341
391.9531 | 123.2025 | -59.2529 | 63.7207 | 0.068255 | -0.0018617 | 0.043354 | 0.065123 | 0.0060704 | -0.02554 | 0.0066942 | 0.060379 | -0.0039976 | 0.070063 | 0.049842 | -0.0042298 | 0.0099092 | -0.020062 | -7.7774 | 63.5696 | -59.3262 | 63.826 | -59.1431 | -59.5413 | -59.5184 | -13.3896 | 63.6292 | -59.2896 | 63.8763 | -59.2117 | -59.436 | -59.2712 | -0.073242 | -0.15106 | 0.10529 | 0.10986 | -0.2655 | -0.28839 | -0.19226 | -0.21515 | -0.036621 | -0.091553 | 0.15564 | 0.041199 | -0.01831 | -0.1831 | 0.018311 | -0.14648 | 0.18311 | 123.1522 | 0.07782 | 123.1659 | 122.8958 | 122.9187 | 122.8226 | 122.8821 | -123.0469 | -123.0103 | 123.0789 | 123.1293 | 51.4755 | 45.8633
393.0312 | 123.2117 | -59.2255 | 63.7253 | 0.20559 | 0.0056153 | 0.043354 | 0.081144 | 0.0060704 | -0.011654 | 0.0034902 | 0.19771 | 0.0088204 | 0.056178 | 0.043434 | -0.037342 | 0.013113 | -0.0083126 | -7.8964 | 63.5925 | -59.2804 | 63.7756 | -59.2621 | -59.5871 | -59.5001 | -13.504 | 63.6383 | -59.2529 | 63.858 | -59.2712 | -59.3536 | -59.3079 | -0.054932 | -0.13275 | 0.050354 | -0.036621 | -0.27466 | -0.36163 | -0.21973 | -0.3067 | -0.027466 | -0.086975 | 0.13275 | -0.045776 | -0.082397 | -0.12817 | -0.054931 | -0.10071 | 0.018311 | 123.056 | -0.01831 | 123.111 | 122.8729 | 122.8912 | 122.818 | 122.8638 | -123.0057 | -122.9782 | 123.0011 | 123.0835 | 51.329 | 45.7214
393.9531 | 123.2162 | -59.2529 | 63.7161 | 0.0072204 | 0.0034793 | 0.041218 | 0.082213 | 0.0028664 | -0.0084497 | -0.0082598 | 0.060379 | -0.0018616 | 0.065791 | 0.071205 | -0.011707 | 0.0067052 | -0.0061756 | -8.1161 | 63.5788 | -59.3124 | 63.7939 | -59.2209 | -59.5139 | -59.5551 | -13.9023 | 63.6246 | -59.2529 | 63.8535 | -59.2072 | -59.3994 | -59.317 | -0.059509 | -0.13733 | 0.07782 | 0.032044 | -0.30212 | -0.26093 | -0.24262 | -0.20142 | 0 | -0.091552 | 0.13733 | 0.045777 | -0.064087 | -0.14648 | -0.064087 | -0.14648 | 0.091553 | 123.1064 | 0.045777 | 123.1064 | 122.8912 | 122.8775 | 122.8317 | 122.8775 | -123.0286 | -122.9691 | 123.0469 | 123.1064 | 51.1368 | 45.3506
395.0312 | 123.1293 | -59.2117 | 63.7848 | 0.098773 | 0.0034793 | 0.050831 | 0.079008 | -0.0078156 | -0.0073817 | -0.0082598 | 0.090897 | 0.0077514 | 0.074336 | 0.069068 | -0.0095708 | 0.012045 | -0.0040396 | -8.2809 | 63.6429 | -59.3033 | 63.945 | -59.0561 | -59.4589 | -59.3445 | -14.1678 | 63.7161 | -59.2667 | 63.8718 | -59.2758 | -59.436 | -59.3262 | -0.091553 | -0.14191 | 0.16022 | 0.15564 | -0.13275 | -0.24719 | -0.041198 | -0.15564 | -0.054932 | -0.068665 | 0.086975 | -0.064087 | -0.11444 | -0.2243 | -0.059509 | -0.16937 | 0.24719 | 123.2483 | -0.009155 | 123.1384 | 122.9462 | 122.9828 | 122.8546 | 122.9279 | -123.0881 | -123.0515 | 123.1567 | 123.0835 | 50.9308 | 45.0439
395.9531 | 123.2529 | -59.2026 | 63.707 | -0.038556 | 0.0056153 | 0.058308 | 0.085417 | 0.01141 | -0.010586 | -0.011464 | 0.10615 | 0.012024 | 0.067927 | 0.071205 | -0.013843 | 0.014181 | -0.013653 | -8.4 | 63.5742 | -59.3079 | 63.7115 | -59.166 | -59.3674 | -59.6329 | -14.3234 | 63.62 | -59.2529 | 63.9359 | -59.1339 | -59.4086 | -59.2117 | -0.10529 | -0.13275 | 0.004578 | 0.036621 | -0.4303 | -0.16479 | -0.32501 | -0.05951 | -0.050354 | -0.086975 | 0.22888 | 0.068665 | -0.009155 | -0.20599 | 0.041199 | -0.15564 | 0.14191 | 123.0194 | 0.11902 | 123.1888 | 122.8821 | 122.8729 | 122.7768 | 122.8226 | -123.0148 | -122.9599 | 122.9141 | 123.1384 | 50.8026 | 44.8792
396.9531 | 123.2346 | -59.1888 | 63.707 | -0.19114 | 0.0098883 | 0.048695 | 0.07794 | 0.010342 | -0.020199 | -0.0050548 | 0.075638 | -0.0007936 | 0.066859 | 0.065864 | -0.013843 | 0.0099092 | 0.0013004 | -8.6838 | 63.5834 | -59.2896 | 63.8123 | -59.2255 | -59.5779 | -59.5184 | -14.5706 | 63.6246 | -59.2621 | 63.9587 | -59.198 | -59.3445 | -59.3079 | -0.10071 | -0.1236 | 0.10529 | -0.036621 | -0.32959 | -0.3891 | -0.22888 | -0.28839 | -0.073242 | -0.082397 | 0.25177 | -0.009155 | -0.11902 | -0.15564 | -0.045776 | -0.082397 | 0.064087 | 123.1018 | 0.064087 | 123.2208 | 122.8729 | 122.8867 | 122.7722 | 122.8134 | -122.9965 | -122.9691 | 123.0011 | 123.1476 | 50.5051 | 44.6182
398.0312 | 123.1796 | -59.2163 | 63.7985 | 0.0072204 | 0.023773 | 0.051899 | 0.093962 | 0.0039344 | -0.024472 | 0.00028524 | 0.12141 | 0.0077514 | 0.0722 | 0.047706 | -0.010639 | 0.0088412 | -0.0083126 | -8.7799 | 63.6475 | -59.2575 | 63.9267 | -59.1797 | -59.4772 | -59.4681 | -14.7629 | 63.6887 | -59.23 | 63.9267 | -59.1705 | -59.3124 | -59.2712 | -0.041198 | -0.15106 | 0.12817 | 0.036622 | -0.25177 | -0.26093 | -0.21057 | -0.21973 | -0.013733 | -0.10986 | 0.12817 | 0.045777 | -0.054931 | -0.09613 | -0.041198 | -0.082397 | 0.07782 | 123.1842 | 0.05951 | 123.1567 | 122.905 | 122.9187 | 122.8638 | 122.905 | -123.056 | -123.0286 | 123.143 | 123.143 | 50.4364 | 44.4534
398.9531 | 123.1842 | -59.2163 | 63.7619 | -0.038556 | 0.0024113 | 0.039082 | 0.086485 | -0.0078156 | -0.013791 | -0.012532 | 0.21297 | 0.0056154 | 0.065791 | 0.032752 | -0.0052988 | 0.016318 | -0.02113 | -9.0225 | 63.6337 | -59.2667 | 63.858 | -59.1522 | -59.5093 | -59.4269 | -15.0696 | 63.6749 | -59.2529 | 63.9221 | -59.2026 | -59.3308 | -59.2758 | -0.050354 | -0.12817 | 0.09613 | 0.064087 | -0.21057 | -0.29297 | -0.16022 | -0.24261 | -0.036621 | -0.086975 | 0.16022 | 0.013733 | -0.059509 | -0.11444 | -0.022888 | -0.07782 | 0.11444 | 123.1247 | 0.050354 | 123.175 | 122.9004 | 122.9279 | 122.85 | 122.8912 | -123.0286 | -123.0148 | 123.0743 | 123.1384 | 50.1938 | 44.1467
400.0312 | 123.1522 | -59.1888 | 63.8123 | 0.19033 | 0.0045473 | 0.043354 | 0.087553 | 0.012479 | -0.0031087 | 0.0066942 | 0.04512 | -0.0018616 | 0.078608 | 0.065864 | -0.010639 | 0.014181 | 0.0034374 | -9.2102 | 63.6612 | -59.2484 | 63.9221 | -59.1248 | -59.4589 | -59.4086 | -15.2344 | 63.7207 | -59.2346 | 63.9359 | -59.2484 | -59.3124 | -59.3262 | -0.059509 | -0.15106 | 0.10986 | 0.064087 | -0.21973 | -0.27008 | -0.16022 | -0.21057 | -0.045776 | -0.091553 | 0.1236 | -0.059509 | -0.13733 | -0.1236 | -0.091553 | -0.07782 | 0.1236 | 123.1705 | -0.013733 | 123.1705 | 122.9095 | 122.9553 | 122.85 | 122.9095 | -123.0606 | -123.0469 | 123.111 | 123.1247 | 49.9786 | 43.9545
400.9531 | 123.23 | -59.1888 | 63.7573 | -0.023297 | -0.0050657 | 0.049763 | 0.081144 | 0.014615 | -0.011654 | -0.012532 | -0.26006 | 0.0077514 | 0.07754 | 0.035957 | -0.0063668 | 0.012045 | 0.0066414 | -9.5398 | 63.5971 | -59.2667 | 63.8077 | -59.1522 | -59.5139 | -59.5001 | -15.564 | 63.6429 | -59.23 | 63.945 | -59.198 | -59.3353 | -59.2941 | -0.07782 | -0.16022 | 0.050354 | 0.036621 | -0.31128 | -0.32501 | -0.23346 | -0.24719 | -0.041199 | -0.11444 | 0.18768 | -0.009155 | -0.10529 | -0.14648 | -0.064086 | -0.10529 | 0.11444 | 123.0743 | 0.032044 | 123.175 | 122.8638 | 122.8729 | 122.7859 | 122.8317 | -123.024 | -122.9874 | 122.9965 | 123.1338 | 49.649 | 43.6249
402.0312 | 123.262 | -59.1293 | 63.7985 | 0.052997 | 0.0056153 | 0.051899 | 0.085417 | 0.00072943 | -0.0041777 | -0.0061228 | -0.56523 | 0.0066834 | 0.07754 | 0.034889 | -0.013843 | 0.012045 | -0.0040396 | -9.6222 | 63.6795 | -59.2026 | 63.8535 | -59.3033 | -59.5642 | -59.198 | -15.6967 | 63.6612 | -59.2117 | 64.0457 | -59.0973 | -59.1888 | -59.2804 | -0.073243 | -0.11902 | 0.054932 | -0.17395 | -0.068665 | -0.43488 | 0.004578 | -0.36163 | -0.082398 | -0.13733 | 0.24719 | 0.032043 | -0.15106 | -0.05951 | -0.068665 | 0.022888 | -0.10071 | 123.056 | 0.11444 | 123.2574 | 122.8821 | 122.8729 | 122.8088 | 122.7905 | -123.0011 | -123.0103 | 122.9828 | 123.175 | 49.5071 | 43.4326
402.9531 | 123.2208 | -59.1843 | 63.7573 | 0.11403 | 0.0088203 | 0.04015 | 0.076872 | -0.0067466 | 0.0054353 | -0.0136 | -0.00065608 | -0.0007936 | 0.061518 | 0.070137 | -0.0095708 | 0.012045 | -0.011517 | -9.9564 | 63.6429 | -59.3033 | 63.9313 | -59.1019 | -59.4452 | -59.4406 | -16.0904 | 63.6932 | -59.2209 | 63.945 | -59.1568 | -59.3353 | -59.198 | -0.11902 | -0.11444 | 0.17395 | 0.082397 | -0.25635 | -0.26092 | -0.13733 | -0.14191 | -0.036621 | -0.064087 | 0.18768 | 0.027466 | -0.013733 | -0.15106 | 0.022888 | -0.11444 | 0.20142 | 123.2346 | 0.064087 | 123.1659 | 122.9462 | 122.9141 | 122.8271 | 122.8775 | -123.0606 | -122.9782 | 123.1155 | 123.1293 | 49.2279 | 43.0939
404.0312 | 123.2437 | -59.1522 | 63.7894 | 0.068255 | -0.0018617 | 0.041218 | 0.084349 | 0.010342 | -0.0073817 | -0.012532 | 0.075638 | -0.0039976 | 0.054042 | 0.065864 | -0.012775 | 0.010977 | -0.0083126 | -10.1669 | 63.6612 | -59.2529 | 63.8901 | -59.0881 | -59.4727 | -59.4452 | -16.2598 | 63.6841 | -59.2026 | 64.0228 | -59.1339 | -59.2621 | -59.2209 | -0.10071 | -0.12817 | 0.10071 | 0.064087 | -0.29297 | -0.32043 | -0.19226 | -0.21973 | -0.050354 | -0.10529 | 0.23346 | 0.018311 | -0.068664 | -0.10986 | -0.01831 | -0.059509 | 0.16479 | 123.143 | 0.068665 | 123.2254 | 122.9141 | 122.8867 | 122.8134 | 122.8363 | -123.0423 | -122.9919 | 123.0423 | 123.175 | 48.9853 | 42.8925
404.9531 | 123.2483 | -59.1522 | 63.7482 | -0.038556 | 0.012024 | 0.058308 | 0.085417 | 0.0092744 | -0.029812 | -0.0039868 | -0.15324 | 0.0056154 | 0.073268 | 0.091499 | -0.01598 | 0.022726 | -0.0061756 | -10.2722 | 63.6337 | -59.2941 | 63.8351 | -59.1476 | -59.5367 | -59.5093 | -16.4658 | 63.6475 | -59.2346 | 64.0045 | -59.079 | -59.3308 | -59.1476 | -0.14191 | -0.11444 | 0.086975 | 0.004578 | -0.35705 | -0.38452 | -0.21515 | -0.24262 | -0.082397 | -0.10071 | 0.25635 | 0.073243 | 0.004578 | -0.17853 | 0.086975 | -0.096131 | 0.14648 | 123.1293 | 0.15564 | 123.2391 | 122.9279 | 122.8821 | 122.7859 | 122.7997 | -123.0423 | -122.9828 | 122.9874 | 123.1567 | 48.88 | 42.6865
406.0312 | 123.2208 | -59.1797 | 63.7939 | 0.022479 | -0.0039977 | 0.042286 | 0.081144 | 0.012479 | -0.0073817 | 0.0056262 | 0.16719 | -0.0039976 | 0.056178 | 0.015663 | 0.0053832 | 0.01525 | -0.0051076 | -10.6247 | 63.652 | -59.2392 | 63.9175 | -59.0744 | -59.4955 | -59.3903 | -16.7496 | 63.7115 | -59.1843 | 63.9771 | -59.1614 | -59.2896 | -59.2072 | -0.05951 | -0.14191 | 0.1236 | 0.10529 | -0.21057 | -0.31586 | -0.15106 | -0.25635 | -0.004578 | -0.082397 | 0.18311 | 0.01831 | -0.027466 | -0.10986 | -0.022888 | -0.10529 | 0.16479 | 123.1567 | 0.022888 | 123.1613 | 122.8912 | 122.8958 | 122.8317 | 122.8912 | -123.0331 | -122.9782 | 123.0972 | 123.1567 | 48.555 | 42.4301
406.9531 | 123.2025 | -59.2117 | 63.739 | 0.037738 | 0.0045473 | 0.046559 | 0.091826 | -0.014224 | -0.0052457 | -0.0061228 | -0.061691 | 0.0002754 | 0.070063 | 0.10966 | -0.013843 | 0.021658 | -0.014721 | -10.6979 | 63.652 | -59.2621 | 63.8855 | -59.1614 | -59.4955 | -59.5276 | -16.9968 | 63.7024 | -59.1843 | 63.9679 | -59.0881 | -59.3262 | -59.3628 | -0.050354 | -0.086975 | 0.14648 | 0.050354 | -0.31586 | -0.28381 | -0.2655 | -0.23346 | 0.027466 | -0.036621 | 0.22888 | 0.1236 | -0.15106 | -0.11444 | -0.17853 | -0.14191 | 0.10071 | 123.1476 | 0.09613 | 123.1522 | 122.9141 | 122.8867 | 122.8638 | 122.9141 | -123.0011 | -122.9233 | 123.0972 | 123.1796 | 48.5138 | 42.215
407.9531 | 123.2391 | -59.1614 | 63.7619 | -0.16063 | 0.0088203 | 0.045491 | 0.084349 | -0.00033857 | -0.0041777 | 0.00028524 | -0.046432 | 0.0077514 | 0.074336 | 0.035957 | -0.014912 | 0.018454 | 0.010913 | -11.0138 | 63.6703 | -59.2758 | 63.8992 | -59.1019 | -59.4772 | -59.4406 | -17.2302 | 63.6932 | -59.2026 | 64.0091 | -59.166 | -59.2529 | -59.2117 | -0.11444 | -0.091553 | 0.13733 | 0.059509 | -0.27924 | -0.31586 | -0.16479 | -0.20142 | -0.041199 | -0.068665 | 0.24719 | -0.004578 | -0.050354 | -0.091553 | -0.009155 | -0.050354 | 0.17395 | 123.175 | 0.036621 | 123.2117 | 122.9462 | 122.8958 | 122.8317 | 122.8546 | -123.0377 | -122.9645 | 123.0606 | 123.1705 | 48.1476 | 41.9312
408.9531 | 123.1796 | -59.1705 | 63.8489 | 0.11403 | 0.0024113 | 0.045491 | 0.088621 | 0.0017974 | 0.0011633 | 0.013103 | -0.07695 | 0.0056154 | 0.062587 | 0.072273 | -0.010639 | 0.013113 | -0.0029716 | -11.1969 | 63.7115 | -59.2712 | 64.0594 | -59.024 | -59.3262 | -59.3628 | -17.6239 | 63.7527 | -59.2163 | 63.8947 | -59.198 | -59.4086 | -59.3033 | -0.10071 | -0.13733 | 0.21057 | 0.14648 | -0.19226 | -0.15564 | -0.091553 | -0.054932 | -0.045777 | -0.09613 | 0.045776 | -0.027466 | -0.13275 | -0.23804 | -0.086975 | -0.19226 | 0.24719 | 123.3307 | 0.018311 | 123.111 | 122.9828 | 122.9691 | 122.8821 | 122.9233 | -123.1201 | -123.0652 | 123.23 | 123.0652 | 47.9736 | 41.5466
410.0312 | 123.2574 | -59.111 | 63.8123 | 0.17507 | 0.0013433 | 0.048695 | 0.080076 | -0.0067466 | -0.0084497 | -0.0082598 | 0.21297 | 0.0066834 | 0.088221 | 0.029548 | -0.0074348 | 0.0088412 | -0.0019036 | -11.3663 | 63.7253 | -59.2255 | 63.858 | -59.1156 | -59.4589 | -59.4635 | -17.6743 | 63.7299 | -59.1614 | 64.0411 | -58.96 | -59.2026 | -59.1293 | -0.11444 | -0.086975 | 0.045776 | -0.004578 | -0.35248 | -0.3479 | -0.23804 | -0.23346 | -0.050354 | -0.082398 | 0.22888 | 0.15106 | -0.01831 | -0.091553 | 0.032044 | -0.041199 | 0.10986 | 123.0835 | 0.20142 | 123.2025 | 122.9507 | 122.8912 | 122.8363 | 122.8409 | -123.0377 | -122.9736 | 122.9691 | 123.1522 | 47.7448 | 41.4368
410.9531 | 123.2758 | -59.1476 | 63.7848 | 0.037738 | -0.0093377 | 0.048695 | 0.081144 | 0.0082064 | -0.0041777 | -0.0093278 | -0.031174 | 0.0013434 | 0.046565 | 0.068 | -0.0074348 | 0.029135 | -0.013653 | -11.5952 | 63.707 | -59.2484 | 63.9771 | -59.111 | -59.4269 | -59.4498 | -17.9626 | 63.7253 | -59.2072 | 63.9999 | -59.0973 | -59.285 | -59.1705 | -0.10071 | -0.07782 | 0.19226 | 0.036621 | -0.30212 | -0.27924 | -0.20142 | -0.17853 | -0.059509 | -0.059509 | 0.21515 | 0.050354 | -0.022888 | -0.13733 | 0.036621 | -0.07782 | 0.13733 | 123.2254 | 0.10986 | 123.2071 | 122.9553 | 122.9324 | 122.8546 | 122.8729 | -123.0331 | -122.9919 | 123.1247 | 123.1476 | 47.5525 | 41.185
412.0312 | 123.262 | -59.1156 | 63.8443 | 0.068255 | 0.010956 | 0.051899 | 0.083281 | 0.012479 | -0.018063 | -0.0029188 | 0.13667 | 0.0045474 | 0.086085 | 0.065864 | -0.012775 | 0.017386 | 0.010913 | -11.792 | 63.7115 | -59.2026 | 63.945 | -59.079 | -59.3948 | -59.4635 | -18.0634 | 63.7482 | -59.1476 | 64.032 | -59.0149 | -59.2438 | -59.1293 | -0.086975 | -0.13275 | 0.10071 | 0.036622 | -0.3479 | -0.27923 | -0.26093 | -0.19226 | -0.032043 | -0.09613 | 0.18768 | 0.10071 | -0.013732 | -0.12817 | 0.018311 | -0.09613 | 0.1236 | 123.1476 | 0.13275 | 123.1796 | 122.9141 | 122.8958 | 122.8271 | 122.8638 | -123.0469 | -122.9919 | 123.0606 | 123.1476 | 47.3236 | 41.0522
412.9531 | 123.2437 | -59.1431 | 63.8123 | 0.022479 | 0.0077523 | 0.049763 | 0.093962 | 0.0071384 | -0.015927 | -0.0082598 | -0.092209 | -0.0061336 | 0.042292 | 0.087226 | -0.013843 | 0.013113 | -0.011517 | -11.8698 | 63.7024 | -59.1888 | 63.9267 | -59.1934 | -59.4406 | -59.4772 | -18.2922 | 63.739 | -59.1385 | 64.0091 | -59.0881 | -59.2209 | -59.1797 | -0.045777 | -0.10986 | 0.11444 | -0.050354 | -0.33417 | -0.29755 | -0.28839 | -0.25177 | 0.004577 | -0.073242 | 0.19684 | 0.054931 | -0.036621 | -0.07782 | -0.041198 | -0.082397 | -0.004577 | 123.1155 | 0.050354 | 123.1476 | 122.8912 | 122.8775 | 122.8455 | 122.8821 | -123.0011 | -122.9507 | 123.0698 | 123.1522 | 47.2733 | 40.8508
414.0312 | 123.1384 | -59.1248 | 63.8397 | -0.023297 | 0.010956 | 0.03481 | 0.079008 | 0.0060704 | 0.0022313 | -0.0018508 | 0.13667 | 0.0034794 | 0.073268 | 0.019935 | -0.012775 | 0.012045 | -0.027539 | -12.1811 | 63.7299 | -59.1797 | 63.9908 | -59.0744 | -59.3719 | -59.4177 | -18.6401 | 63.7344 | -59.1614 | 63.9679 | -59.0652 | -59.0973 | -59.079 | -0.054931 | -0.10986 | 0.15106 | 0.050354 | -0.29297 | -0.24719 | -0.23804 | -0.19226 | -0.036621 | -0.10529 | 0.12817 | 0.059509 | 0.045777 | 0.027466 | 0.082398 | 0.064087 | 0.10529 | 123.1705 | 0.09613 | 123.1293 | 122.9095 | 122.8958 | 122.8546 | 122.8592 | -123.0194 | -123.0011 | 123.1155 | 123.0927 | 46.9437 | 40.4846
414.9531 | 123.2254 | -59.0973 | 63.8123 | 0.068255 | 0.00027529 | 0.044423 | 0.083281 | -0.020633 | -0.0084497 | -0.0071918 | -0.015915 | 0.0056154 | 0.044429 | 0.056251 | -0.013843 | 0.012045 | -0.014721 | -12.4558 | 63.6841 | -59.198 | 63.9313 | -59.1248 | -59.4315 | -59.4498 | -18.7958 | 63.739 | -59.1705 | 64.0457 | -59.0881 | -59.1614 | -59.2392 | -0.10071 | -0.12817 | 0.11902 | -0.027466 | -0.35248 | -0.33417 | -0.25177 | -0.23346 | -0.073242 | -0.073242 | 0.23346 | 0.009155 | -0.14191 | -0.064087 | -0.068665 | 0.009155 | 0.073242 | 123.1293 | 0.082397 | 123.2162 | 122.8821 | 122.9095 | 122.7814 | 122.8363 | -123.0103 | -122.9828 | 123.0286 | 123.143 | 46.6415 | 40.3015
416.0312 | 123.2117 | -59.0927 | 63.8535 | 0.12929 | 0.0066833 | 0.043354 | 0.075804 | 0.0028664 | -0.018063 | -0.0071918 | 0.22823 | -0.0018616 | 0.052973 | 0.06266 | -0.011707 | 0.013113 | 0.014118 | -12.5656 | 63.7161 | -59.2163 | 63.9954 | -59.1064 | -59.3445 | -59.4223 | -19.1483 | 63.7573 | -59.1431 | 63.9496 | -59.0103 | -59.2255 | -59.1568 | -0.1236 | -0.13733 | 0.14191 | -0.013733 | -0.32959 | -0.25177 | -0.20599 | -0.12817 | -0.050354 | -0.096131 | 0.09613 | 0.082397 | -0.064087 | -0.13275 | -0.013733 | -0.082398 | 0.10986 | 123.2117 | 0.13275 | 123.0927 | 122.9324 | 122.9004 | 122.8088 | 122.85 | -123.0698 | -122.9965 | 123.0881 | 123.0423 | 46.5271 | 39.9445
416.9531 | 123.1476 | -59.1293 | 63.8306 | 0.083514 | 0.0056153 | 0.036946 | 0.091826 | 0.0071384 | -0.021267 | 0.0034902 | -0.10747 | 0.01416 | 0.070063 | 0.054115 | -0.012775 | 0.013113 | -0.016858 | -12.7945 | 63.7482 | -59.23 | 64.1052 | -58.9554 | -59.3124 | -59.3216 | -19.5053 | 63.7848 | -59.1751 | 63.9633 | -59.1888 | -59.3536 | -59.2758 | -0.10071 | -0.082397 | 0.27466 | 0.17395 | -0.19226 | -0.18311 | -0.091552 | -0.082397 | -0.045777 | -0.045776 | 0.13275 | -0.05951 | -0.14648 | -0.2243 | -0.10071 | -0.17853 | 0.27466 | 123.3353 | -0.013733 | 123.1384 | 122.9782 | 122.9599 | 122.8775 | 122.9141 | -123.0606 | -123.0057 | 123.2346 | 123.0927 | 46.3348 | 39.624
418.0312 | 123.2254 | -59.0607 | 63.8489 | -0.2064 | 0.0077523 | 0.039082 | 0.083281 | 0.022092 | -0.0031087 | -0.011464 | 0.19771 | 0.0066834 | 0.042292 | 0.058387 | -0.0020938 | 0.019522 | -0.0072446 | -12.9822 | 63.7436 | -59.1568 | 63.9999 | -59.0332 | -59.3719 | -59.4315 | -19.6518 | 63.7711 | -59.1522 | 64.0366 | -59.024 | -59.2026 | -59.1614 | -0.09613 | -0.10529 | 0.15106 | 0.027466 | -0.37079 | -0.31128 | -0.27466 | -0.21515 | -0.091553 | -0.07782 | 0.18768 | 0.036621 | -0.10071 | -0.14191 | -0.009155 | -0.050354 | 0.1236 | 123.1567 | 0.12817 | 123.1888 | 122.9004 | 122.9233 | 122.8043 | 122.8317 | -123.0057 | -123.0011 | 123.0606 | 123.0972 | 46.0785 | 39.4089
418.9531 | 123.175 | -59.1431 | 63.8763 | 0.052997 | 0.0024113 | 0.045491 | 0.087553 | -0.0024746 | -0.0095177 | -0.0136 | -0.1685 | 0.0077514 | 0.050837 | 0.078681 | -0.0095708 | 0.016318 | -0.025402 | -13.3255 | 63.7207 | -59.2117 | 64.064 | -58.9188 | -59.3491 | -59.2758 | -19.9127 | 63.7939 | -59.1888 | 64.0274 | -59.2026 | -59.3353 | -59.2438 | -0.068665 | -0.15564 | 0.18768 | 0.2243 | -0.13275 | -0.20599 | -0.064087 | -0.13733 | -0.045777 | -0.082398 | 0.15106 | -0.05951 | -0.10071 | -0.19226 | -0.054931 | -0.14648 | 0.29297 | 123.2758 | -0.013733 | 123.2162 | 122.9324 | 122.9828 | 122.8638 | 122.937 | -123.0881 | -123.0652 | 123.2071 | 123.1705 | 45.8176 | 39.2303
420.0312 | 123.2208 | -59.0652 | 63.8763 | 0.083514 | 0.0045473 | 0.039082 | 0.076872 | 0.0039344 | -0.015927 | -0.0029188 | 0.15193 | 0.0045474 | 0.070063 | 0.060523 | -0.0042298 | 0.021658 | -0.013653 | -13.1561 | 63.826 | -59.1202 | 64.0045 | -59.1156 | -59.4177 | -59.3674 | -20.0363 | 63.7848 | -59.1202 | 64.0594 | -58.9966 | -59.0881 | -59.1431 | -0.054931 | -0.050354 | 0.12817 | -0.050354 | -0.30212 | -0.35248 | -0.24719 | -0.29755 | -0.054931 | -0.091553 | 0.18311 | 0.068665 | -0.077819 | -0.022888 | -0.022888 | 0.032043 | 0.004577 | 123.1247 | 0.1236 | 123.1796 | 122.9462 | 122.905 | 122.8912 | 122.85 | -122.9965 | -122.9965 | 123.0698 | 123.1247 | 45.9091 | 39.0289
420.9531 | 123.0743 | -59.1431 | 63.8855 | 0.052997 | 0.013092 | 0.044423 | 0.074736 | -0.0024746 | -0.0084497 | 0.0056262 | -0.29057 | 0.0045474 | 0.052973 | 0.044502 | -0.0074348 | 0.021658 | -0.0040396 | -13.623 | 63.7527 | -59.2072 | 64.0549 | -58.9096 | -59.3216 | -59.2529 | -20.4575 | 63.8306 | -59.166 | 63.9542 | -59.1568 | -59.3216 | -59.2575 | -0.064087 | -0.13275 | 0.16937 | 0.23346 | -0.10986 | -0.17853 | -0.045777 | -0.11444 | -0.022889 | -0.054932 | 0.068665 | -0.013733 | -0.11444 | -0.17853 | -0.091552 | -0.15564 | 0.29755 | 123.262 | 0.009156 | 123.1201 | 122.9599 | 122.9965 | 122.8958 | 122.9736 | -123.0927 | -123.0515 | 123.1979 | 123.0972 | 45.52 | 38.6856
421.9531 | 123.1338 | -59.1797 | 63.858 | 0.14455 | 0.0098883 | 0.055104 | 0.079008 | -0.0056786 | -0.0041777 | -0.012532 | -0.1685 | 0.0066834 | 0.061518 | 0.051979 | -0.0095708 | 0.022726 | 0.00023236 | -13.8245 | 63.7619 | -59.2209 | 64.1281 | -58.9188 | -59.2667 | -59.2941 | -20.8145 | 63.8306 | -59.1797 | 63.9359 | -59.1248 | -59.7061 | -59.5367 | -0.041199 | -0.09613 | 0.27008 | 0.26093 | -0.11444 | -0.086976 | -0.073242 | -0.045777 | 0 | -0.027466 | 0.07782 | 0.054931 | -0.35706 | -0.52643 | -0.35706 | -0.52643 | 0.30212 | 123.349 | 0.054931 | 123.1155 | 122.9828 | 123.0103 | 122.9416 | 123.0103 | -123.0789 | -123.0377 | 123.3078 | 123.1155 | 45.3552 | 38.3652
423.0312 | 123.1979 | -59.0927 | 63.8763 | 0.083514 | 0.012024 | 0.046559 | 0.07794 | 0.0082064 | -0.0041777 | -0.0039868 | -0.22954 | 0.010956 | 0.058314 | 0.046638 | -0.0063668 | 0.017386 | 0.0055734 | -14.0671 | 63.7619 | -59.1614 | 64.0091 | -59.0057 | -59.3765 | -59.3262 | -20.8557 | 63.8031 | -59.1202 | 63.9816 | -59.0378 | -59.285 | -59.111 | -0.068665 | -0.11444 | 0.13275 | 0.086975 | -0.23346 | -0.28381 | -0.16479 | -0.21515 | -0.027466 | -0.073242 | 0.10529 | 0.054931 | -0.018311 | -0.19226 | 0.009155 | -0.16479 | 0.15564 | 123.1705 | 0.082397 | 123.1018 | 122.9233 | 122.9233 | 122.8546 | 122.8958 | -123.0377 | -122.9965 | 123.1018 | 123.0743 | 45.0256 | 38.237
423.9531 | 123.1522 | -59.079 | 63.9084 | 0.068255 | 0.0024113 | 0.043354 | 0.087553 | 0.022092 | -0.0073817 | 0.0013532 | -0.21428 | -0.0007936 | 0.059382 | 0.068 | -0.013843 | 0.025931 | -0.02113 | -14.241 | 63.7848 | -59.1568 | 64.0778 | -58.9737 | -59.285 | -59.3308 | -21.1029 | 63.8351 | -59.1202 | 63.9587 | -59.0607 | -59.2712 | -59.1888 | -0.07782 | -0.1236 | 0.16937 | 0.10528 | -0.25177 | -0.20599 | -0.17395 | -0.12817 | -0.041199 | -0.073242 | 0.050354 | 0.01831 | -0.10986 | -0.19226 | -0.068665 | -0.15106 | 0.1831 | 123.2346 | 0.059509 | 123.0789 | 122.9416 | 122.9553 | 122.8638 | 122.9141 | -123.0652 | -123.0286 | 123.1567 | 123.0377 | 44.838 | 37.9761
425.0312 | 123.2254 | -59.0698 | 63.8855 | 0.083514 | 0.0077523 | 0.045491 | 0.066191 | 0.016751 | -0.0031087 | 0.0034902 | 0.18245 | -0.0018616 | 0.070063 | 0.044502 | -0.014912 | 0.0099092 | 0.01305 | -14.5294 | 63.7848 | -59.1202 | 64.032 | -59.0149 | -59.3628 | -59.3765 | -21.3913 | 63.8031 | -59.0836 | 64.0778 | -58.905 | -59.2026 | -59.0881 | -0.050354 | -0.10071 | 0.14648 | 0.054931 | -0.3067 | -0.29297 | -0.25635 | -0.24262 | -0.013733 | -0.082397 | 0.19226 | 0.16479 | -0.018311 | -0.13275 | -0.004578 | -0.11902 | 0.10529 | 123.1522 | 0.17853 | 123.1613 | 122.905 | 122.8867 | 122.8546 | 122.8729 | -123.0057 | -122.9691 | 123.1018 | 123.1476 | 44.5404 | 37.6785
425.9531 | 123.0972 | -59.1064 | 63.9221 | 0.17507 | -0.0082697 | 0.050831 | 0.085417 | 0.01141 | -0.020199 | 0.0056262 | -0.21428 | 0.0045474 | 0.067927 | 0.057319 | -0.018116 | 0.021658 | -0.018994 | -14.827 | 63.8168 | -59.2026 | 64.1235 | -58.8867 | -59.23 | -59.2484 | -21.7346 | 63.8535 | -59.1156 | 63.9771 | -59.1431 | -59.2987 | -59.2667 | -0.096131 | -0.10529 | 0.20142 | 0.21973 | -0.14191 | -0.1236 | -0.045776 | -0.027466 | -0.009156 | -0.068664 | 0.054932 | -0.036621 | -0.16022 | -0.19226 | -0.15106 | -0.18311 | 0.31586 | 123.3261 | -0.027465 | 123.0927 | 123.0194 | 122.9691 | 122.9233 | 122.9599 | -123.1247 | -123.0377 | 123.23 | 123.0835 | 44.2795 | 37.3718
427.0312 | 123.2071 | -59.0698 | 63.8947 | -0.023297 | 0.0098883 | 0.047627 | 0.082213 | -0.0014066 | 0.0043673 | -0.0082598 | 0.18245 | 0.0056154 | 0.080744 | 0.038093 | -0.010639 | 0.0045682 | 0.020526 | -15.0421 | 63.7711 | -59.1248 | 64.0594 | -59.0149 | -59.2896 | -59.3628 | -21.9086 | 63.8031 | -59.1064 | 63.9267 | -58.9371 | -59.1568 | -59.2209 | -0.054932 | -0.1236 | 0.1648 | 0.054931 | -0.29297 | -0.21973 | -0.23804 | -0.1648 | -0.036621 | -0.091552 | 0.032044 | 0.13275 | -0.15106 | -0.086975 | -0.11444 | -0.050354 | 0.10986 | 123.1842 | 0.16937 | 123.0331 | 122.8958 | 122.9095 | 122.8409 | 122.8729 | -123.0194 | -123.0011 | 123.1293 | 122.9965 | 44.0277 | 37.1613
427.9688 | 123.2162 | -59.0515 | 63.8992 | 0.037738 | 0.01416 | 0.032673 | 0.076872 | -0.00033857 | 0.0065043 | -0.010396 | -0.061691 | 0.0077514 | 0.047633 | 0.046638 | -0.011707 | 0.02059 | -0.022198 | -15.3442 | 63.7848 | -59.1797 | 64.0778 | -58.9417 | -59.3079 | -59.2987 | -22.1741 | 63.8351 | -59.1248 | 64.0823 | -59.0286 | -59.1888 | -59.1431 | -0.12817 | -0.11444 | 0.17853 | 0.10986 | -0.24719 | -0.25635 | -0.11902 | -0.12817 | -0.073242 | -0.064087 | 0.1831 | 0.022889 | -0.091552 | -0.13733 | -0.01831 | -0.064087 | 0.23804 | 123.2574 | 0.096131 | 123.2071 | 122.9645 | 122.9599 | 122.8363 | 122.8867 | -123.0789 | -123.024 | 123.1293 | 123.1338 | 43.7073 | 36.8774
429.0312 | 123.2117 | -59.0652 | 63.8809 | -0.069074 | 0.0013433 | 0.041218 | 0.075804 | 0.022092 | -0.0063137 | 0.0013532 | 0.16719 | 0.0077514 | 0.083949 | 0.042366 | -0.013843 | 0.010977 | -0.010449 | -15.6052 | 63.7665 | -59.1064 | 64.0228 | -59.0195 | -59.3079 | -59.3994 | -22.3755 | 63.8351 | -59.111 | 64.0594 | -59.0378 | -59.2072 | -59.1431 | -0.041198 | -0.11444 | 0.14191 | 0.045777 | -0.33417 | -0.24261 | -0.29297 | -0.20142 | -0.045776 | -0.045776 | 0.17853 | 0.027466 | -0.077819 | -0.14191 | -0.032043 | -0.09613 | 0.086975 | 123.1293 | 0.073242 | 123.1705 | 122.8729 | 122.9462 | 122.8317 | 122.9004 | -122.9874 | -122.9919 | 123.0881 | 123.1247 | 43.4601 | 36.6898
429.9688 | 123.2483 | -59.0286 | 63.8992 | 0.0072204 | 0.0013433 | 0.044423 | 0.082213 | -0.0056786 | 0.0022313 | -0.0082598 | -0.031174 | 0.0045474 | 0.071131 | 0.065864 | -0.0063668 | 0.018454 | -0.0051076 | -15.8157 | 63.7573 | -59.1385 | 64.0228 | -58.8318 | -59.3582 | -59.3765 | -22.4945 | 63.826 | -59.079 | 64.1647 | -59.0012 | -59.1248 | -59.0836 | -0.10986 | -0.14191 | 0.1236 | 0.19684 | -0.3479 | -0.32959 | -0.23804 | -0.21973 | -0.050354 | -0.073242 | 0.2655 | 0.027465 | -0.054932 | -0.096131 | -0.004578 | -0.045777 | 0.3067 | 123.1613 | 0.077819 | 123.2437 | 122.8958 | 122.905 | 122.7859 | 122.8546 | -123.0377 | -122.9782 | 123.0515 | 123.1934 | 43.2129 | 36.5341
431.0312 | 123.2025 | -59.0286 | 63.9038 | 0.0072204 | 0.0013433 | 0.038014 | 0.069395 | 0.013547 | 0.0011633 | 0.0034902 | 0.10615 | 0.0024114 | 0.070063 | 0.033821 | -0.014912 | 0.014181 | -0.02113 | -15.9988 | 63.7802 | -59.1339 | 64.0823 | -58.9783 | -59.3033 | -59.3216 | -22.8333 | 63.8214 | -59.0881 | 64.0732 | -59.0057 | -59.1522 | -59.1202 | -0.10529 | -0.1236 | 0.17853 | 0.050354 | -0.29297 | -0.27466 | -0.18768 | -0.16937 | -0.05951 | -0.082398 | 0.16937 | 0.022888 | -0.091553 | -0.1236 | -0.032043 | -0.064087 | 0.15564 | 123.2162 | 0.082398 | 123.1613 | 122.9141 | 122.9095 | 122.8088 | 122.85 | -123.0377 | -122.9919 | 123.111 | 123.1018 | 43.0298 | 36.1954
431.9688 | 123.2529 | -59.0424 | 63.8626 | 0.052997 | -0.00079271 | 0.042286 | 0.089689 | -0.00033857 | -0.019131 | -0.018941 | -0.10747 | 0.0024114 | 0.070063 | 0.061592 | -0.014912 | 0.02059 | -0.0029716 | -16.2964 | 63.7802 | -59.1248 | 64.0137 | -58.9874 | -59.4131 | -59.2941 | -23.0438 | 63.858 | -59.0973 | 64.1327 | -58.9508 | -59.1248 | -59.079 | -0.082398 | -0.082398 | 0.15106 | 0.054931 | -0.25177 | -0.37079 | -0.16937 | -0.28839 | -0.054932 | -0.004578 | 0.27008 | 0.091552 | -0.036621 | -0.082398 | 0.018311 | -0.027466 | 0.13733 | 123.1384 | 0.14648 | 123.23 | 122.905 | 122.9553 | 122.8226 | 122.9004 | -122.9874 | -122.9599 | 123.056 | 123.175 | 42.746 | 35.9985
432.9531 | 123.175 | -59.0332 | 63.9771 | 0.098773 | -0.00079271 | 0.042286 | 0.0726 | -0.012088 | -0.012723 | -0.0018508 | 0.04512 | 0.0088204 | 0.071131 | 0.016731 | -0.0095708 | 0.017386 | -0.011517 | -16.42 | 63.8947 | -59.1339 | 64.1968 | -58.8776 | -59.1614 | -59.2346 | -23.4238 | 63.913 | -59.0836 | 64.0228 | -58.9325 | -59.2072 | -59.1202 | -0.10071 | -0.082398 | 0.21973 | 0.15564 | -0.20142 | -0.12817 | -0.10071 | -0.027466 | -0.050354 | -0.064087 | 0.045776 | 0.10071 | -0.086975 | -0.17395 | -0.036621 | -0.1236 | 0.25635 | 123.3307 | 0.15106 | 123.1064 | 123.0286 | 122.9965 | 122.9279 | 122.9462 | -123.111 | -123.0606 | 123.23 | 123.056 | 42.6132 | 35.6094
433.9531 | 123.1476 | -59.0469 | 63.9496 | 0.052997 | 0.0034793 | 0.044423 | 0.081144 | 0.0028664 | 0.0086403 | 0.00028524 | 0.029861 | 0.0034794 | 0.074336 | 0.068 | -0.010639 | 0.0099092 | -0.010449 | -16.7404 | 63.8718 | -59.111 | 64.1006 | -58.8547 | -59.2484 | -59.2026 | -23.5886 | 63.9084 | -59.0561 | 64.0961 | -58.9645 | -59.1797 | -59.0881 | -0.064087 | -0.07782 | 0.15106 | 0.19226 | -0.15564 | -0.20142 | -0.091553 | -0.13733 | -0.009155 | -0.041199 | 0.14648 | 0.082397 | -0.041199 | -0.13275 | -0.032044 | -0.1236 | 0.25635 | 123.2117 | 0.091552 | 123.1522 | 122.9828 | 122.9645 | 122.9187 | 122.9553 | -123.0606 | -123.0057 | 123.1476 | 123.143 | 42.3065 | 35.4584
435.0312 | 123.111 | -59.079 | 63.945 | 0.15981 | 0.0056153 | 0.045491 | 0.07794 | 0.01141 | 0.0054353 | -0.0061228 | -0.092209 | 0.0066834 | 0.058314 | 0.054115 | -0.010639 | 0.01525 | 0.0013004 | -17.0837 | 63.8351 | -59.1248 | 64.1647 | -58.8089 | -59.2163 | -59.2026 | -23.9319 | 63.8809 | -59.0927 | 64.0594 | -59.0515 | -59.2575 | -59.1934 | -0.045777 | -0.10986 | 0.21973 | 0.27008 | -0.1236 | -0.13733 | -0.07782 | -0.091553 | -0.013733 | -0.064087 | 0.11444 | 0.027465 | -0.11444 | -0.17853 | -0.10071 | -0.16479 | 0.31586 | 123.2895 | 0.041198 | 123.1522 | 122.9599 | 122.9736 | 122.9141 | 122.9599 | -123.0698 | -123.0377 | 123.2437 | 123.1384 | 41.9952 | 35.1471
435.9531 | 123.1705 | -59.024 | 63.9587 | 0.19033 | -0.0072017 | 0.04015 | 0.086485 | 0.013547 | -0.028744 | 0.0013532 | -0.21428 | 0.0066834 | 0.056178 | 0.043434 | -0.014912 | 0.01525 | -0.011517 | -17.2348 | 63.8535 | -59.0836 | 64.0869 | -58.8455 | -59.2712 | -59.2209 | -24.0555 | 63.8809 | -59.0561 | 63.9542 | -58.7723 | -59.2163 | -59.1339 | -0.059509 | -0.10529 | 0.12817 | 0.17853 | -0.19684 | -0.24719 | -0.13733 | -0.18768 | -0.032043 | -0.07782 | -0.004577 | 0.25177 | -0.10986 | -0.19226 | -0.07782 | -0.16022 | 0.23804 | 123.1705 | 0.28381 | 123.0103 | 122.937 | 122.937 | 122.8775 | 122.905 | -123.0423 | -123.0148 | 123.111 | 122.9782 | 41.7892 | 34.9686
437.0312 | 123.2483 | -58.992 | 63.9175 | 0.022479 | 0.00027529 | 0.036946 | 0.080076 | -0.0067466 | 0.0043673 | -0.010396 | 0.075638 | 0.0066834 | 0.075404 | 0.055183 | -0.0085028 | 0.017386 | -0.0040396 | -17.5552 | 63.7985 | -59.1064 | 63.7985 | -59.1385 | -59.3124 | -59.1797 | -24.2752 | 63.8397 | -59.0607 | 64.1739 | -58.905 | -59.1156 | -59.0378 | -0.11444 | -0.11902 | -0.11902 | -0.14648 | -0.18768 | -0.32043 | -0.073242 | -0.20599 | -0.068665 | -0.07782 | 0.25635 | 0.086975 | -0.045777 | -0.1236 | 0.022888 | -0.054932 | -0.032044 | 122.905 | 0.15564 | 123.2346 | 122.905 | 122.9004 | 122.7905 | 122.8317 | -123.024 | -122.9782 | 122.7905 | 123.1659 | 41.4368 | 34.7168
437.9531 | 123.143 | -59.0149 | 63.9954 | 0.20559 | 0.013092 | 0.031605 | 0.089689 | 0.01141 | 9.5287e-05 | -0.011464 | 0.16719 | 0.0024114 | 0.075404 | 0.084022 | -0.0095708 | 0.013113 | -0.0083126 | -17.6788 | 63.8901 | -59.0881 | 64.1556 | -58.7494 | -59.1476 | -59.1339 | -24.6506 | 63.9359 | -59.0424 | 64.0503 | -58.9417 | -59.1843 | -59.0469 | -0.073242 | -0.10529 | 0.16022 | 0.2655 | -0.11902 | -0.13275 | -0.045776 | -0.059509 | -0.027465 | -0.059509 | 0.054932 | 0.073243 | -0.032043 | -0.16937 | -0.004578 | -0.14191 | 0.33875 | 123.2437 | 0.10071 | 123.0927 | 122.9782 | 122.9782 | 122.905 | 122.9507 | -123.0835 | -123.0377 | 123.1705 | 123.0652 | 41.3361 | 34.3643
439.0312 | 123.2574 | -58.9737 | 63.945 | 0.22084 | -0.0072017 | 0.050831 | 0.084349 | -0.021701 | -0.033017 | 0.0013532 | 0.19771 | 0.0077514 | 0.057246 | 0.023139 | -0.0095708 | 0.012045 | -0.0040396 | -17.9306 | 63.8489 | -59.0744 | 63.9816 | -58.9737 | -59.3857 | -59.285 | -24.6963 | 63.8672 | -59.0515 | 64.1602 | -58.9005 | -59.0744 | -59.0149 | -0.10071 | -0.09613 | 0.036621 | 0 | -0.31128 | -0.41199 | -0.21057 | -0.31128 | -0.07782 | -0.07782 | 0.21515 | 0.073242 | -0.041199 | -0.10071 | 0.036621 | -0.022888 | 0.10071 | 123.056 | 0.15106 | 123.2117 | 122.9233 | 122.9187 | 122.8226 | 122.8409 | -123.0194 | -122.9965 | 122.9553 | 123.1338 | 41.0431 | 34.2773
439.9531 | 123.1613 | -58.992 | 63.9954 | 0.068255 | 0.0024113 | 0.03481 | 0.087553 | 0.0082064 | 0.0086403 | -0.0050548 | -0.00065608 | 0.0045474 | 0.0722 | 0.049842 | -0.012775 | 0.021658 | 0.0023694 | -17.9718 | 63.8901 | -59.0973 | 64.151 | -58.8547 | -59.2072 | -59.2209 | -25.0534 | 63.9359 | -59.0424 | 64.0732 | -58.873 | -59.1568 | -59.0515 | -0.10529 | -0.10529 | 0.15564 | 0.13733 | -0.22888 | -0.21515 | -0.1236 | -0.10986 | -0.050354 | -0.059509 | 0.07782 | 0.11902 | -0.05951 | -0.16479 | -0.009156 | -0.11444 | 0.24262 | 123.2483 | 0.16937 | 123.1155 | 122.9874 | 122.9782 | 122.8821 | 122.9279 | -123.0927 | -123.0377 | 123.143 | 123.0652 | 41.0202 | 33.9386
441.0312 | 123.1384 | -59.0286 | 63.9908 | -0.084332 | -0.013611 | 0.032673 | 0.081144 | -0.0024746 | 0.0065043 | -0.022145 | -0.031174 | 0.013092 | 0.065791 | 0.061592 | -0.0095708 | 0.022726 | 0.0023694 | -18.3746 | 63.8947 | -59.1156 | 64.1739 | -58.7814 | -59.1751 | -59.1705 | -25.4334 | 63.9084 | -59.079 | 64.064 | -58.9691 | -59.23 | -59.1156 | -0.086976 | -0.096131 | 0.18311 | 0.24719 | -0.14191 | -0.14648 | -0.054931 | -0.059509 | -0.050354 | -0.082398 | 0.073242 | 0.059509 | -0.086976 | -0.20142 | -0.036622 | -0.15106 | 0.33417 | 123.2895 | 0.10986 | 123.143 | 123.0103 | 122.9874 | 122.9233 | 122.937 | -123.1064 | -123.0698 | 123.2025 | 123.0927 | 40.654 | 33.5953
441.9531 | 123.1338 | -58.9828 | 64.0457 | 0.26662 | 0.0034793 | 0.029469 | 0.083281 | 0.010342 | 0.0097083 | -0.0029188 | 0.12141 | 0.010956 | 0.068995 | 0.044502 | -0.011707 | 0.02059 | -0.020062 | -18.5989 | 63.9221 | -59.0927 | 64.2471 | -58.7585 | -59.0927 | -59.198 | -25.589 | 63.9359 | -59.0149 | 64.0549 | -58.8821 | -59.198 | -59.0515 | -0.10986 | -0.1236 | 0.20142 | 0.2243 | -0.21515 | -0.10986 | -0.10529 | 0 | -0.032044 | -0.10986 | 0.009156 | 0.10071 | -0.068665 | -0.21515 | -0.036621 | -0.1831 | 0.33417 | 123.3398 | 0.13275 | 123.0698 | 123.0148 | 122.9507 | 122.905 | 122.9187 | -123.1384 | -123.0606 | 123.23 | 123.0377 | 40.3839 | 33.3939
443.0312 | 123.111 | -59.0012 | 64.0045 | 0.15981 | 0.0077523 | 0.041218 | 0.09503 | -0.0024746 | -0.0041777 | -0.0039868 | -0.07695 | 0.0077514 | 0.073268 | 0.055183 | -0.0085028 | 0.02059 | -0.0072446 | -18.7408 | 63.8992 | -59.0881 | 64.1418 | -58.7814 | -59.1751 | -59.166 | -25.9323 | 63.9359 | -59.0469 | 64.0549 | -58.9508 | -59.2392 | -59.111 | -0.086975 | -0.10529 | 0.13733 | 0.21973 | -0.16479 | -0.17395 | -0.07782 | -0.086975 | -0.045776 | -0.068665 | 0.050354 | 0.050354 | -0.10986 | -0.23804 | -0.064087 | -0.19226 | 0.3067 | 123.23 | 0.09613 | 123.1018 | 122.9874 | 122.9828 | 122.9004 | 122.937 | -123.0927 | -123.0515 | 123.143 | 123.056 | 40.2603 | 33.0688
443.9531 | 123.1613 | -58.9783 | 64.032 | 0.19033 | 0.018433 | 0.04015 | 0.088621 | -0.00033857 | 9.5287e-05 | 0.012035 | 0.28926 | 0.0088204 | 0.079676 | 0.027412 | 0.0053832 | 0.0024322 | 0.0066414 | -18.8507 | 63.913 | -59.024 | 64.1602 | -58.8959 | -59.1705 | -59.23 | -26.0056 | 63.9313 | -59.0103 | 64.064 | -58.8501 | -59.1202 | -59.079 | -0.045777 | -0.11902 | 0.12817 | 0.082397 | -0.25177 | -0.19226 | -0.20599 | -0.14648 | -0.032044 | -0.10071 | 0.032044 | 0.12817 | -0.10071 | -0.14191 | -0.068664 | -0.10986 | 0.12817 | 123.1842 | 0.16022 | 123.0743 | 122.937 | 122.9416 | 122.8912 | 122.9095 | -123.056 | -123.0423 | 123.1384 | 123.0423 | 40.1276 | 32.9727
445.0312 | 123.1018 | -59.0012 | 63.9999 | 0.022479 | -0.0039977 | 0.050831 | 0.087553 | 0.0082064 | 0.0075723 | -0.011464 | 0.075638 | 0.013092 | 0.071131 | 0.069068 | -0.0020938 | 0.02059 | -0.015789 | -19.1895 | 63.9038 | -59.0698 | 64.2197 | -58.7311 | -59.1248 | -59.1522 | -26.4587 | 63.9542 | -59.0424 | 64.032 | -58.9645 | -59.285 | -59.0652 | -0.068664 | -0.09613 | 0.21973 | 0.27008 | -0.15106 | -0.1236 | -0.082398 | -0.054932 | -0.041198 | -0.045776 | 0.032043 | 0.036621 | -0.064087 | -0.28381 | -0.022889 | -0.24262 | 0.33874 | 123.2895 | 0.077819 | 123.0743 | 122.9736 | 122.9965 | 122.905 | 122.9553 | -123.0698 | -123.0423 | 123.2208 | 123.0331 | 39.8117 | 32.5424
445.9531 | 123.1293 | -58.9874 | 64.0503 | 0.068255 | 0.0013433 | 0.04015 | 0.076872 | 0.018887 | 0.012912 | -0.0039868 | 0.060379 | 0.01416 | 0.091426 | 0.031684 | -0.010639 | 0.012045 | -0.0093806 | -19.3542 | 63.9359 | -59.0332 | 64.2563 | -58.8226 | -59.111 | -59.1248 | -26.5228 | 63.9633 | -58.992 | 64.0594 | -58.8776 | -59.1248 | -59.079 | -0.045776 | -0.11444 | 0.20599 | 0.16479 | -0.13733 | -0.1236 | -0.091553 | -0.07782 | -0.004577 | -0.086975 | 0.009155 | 0.10986 | -0.091552 | -0.13733 | -0.086975 | -0.13275 | 0.21057 | 123.2895 | 0.11444 | 123.0515 | 122.9691 | 122.9553 | 122.9233 | 122.9507 | -123.0835 | -123.0423 | 123.2437 | 123.0469 | 39.6332 | 32.4646
446.9688 | 123.262 | -58.9508 | 63.9816 | 0.083514 | 0.0013433 | 0.042286 | 0.086485 | 0.01141 | -0.011654 | -0.0071918 | 0.16719 | -0.0072016 | 0.0722 | 0.025276 | -0.012775 | 0.013113 | -0.014721 | -19.5694 | 63.8718 | -59.0515 | 64.0411 | -58.9188 | -59.2758 | -59.2896 | -26.7883 | 63.8947 | -59.0012 | 64.1876 | -58.8135 | -59.0561 | -58.9371 | -0.10071 | -0.10986 | 0.05951 | 0.032044 | -0.33875 | -0.32501 | -0.23804 | -0.2243 | -0.050354 | -0.086975 | 0.20599 | 0.13733 | 0.013733 | -0.10529 | 0.064087 | -0.054931 | 0.13275 | 123.0927 | 0.18768 | 123.1888 | 122.9233 | 122.8958 | 122.8226 | 122.8455 | -123.0331 | -122.9828 | 122.9919 | 123.1384 | 39.3814 | 32.1625
448.0312 | 123.0469 | -58.9828 | 64.0503 | 0.068255 | 0.0066833 | 0.046559 | 0.082213 | 0.00072943 | -0.00097271 | 0.0077622 | -0.07695 | 0.015228 | 0.081813 | 0.05091 | -0.018116 | 0.0099092 | -0.017926 | -19.9814 | 63.9221 | -59.0652 | 64.2242 | -58.6761 | -59.1339 | -59.0973 | -27.1225 | 63.9404 | -59.0149 | 63.9816 | -59.1202 | -58.8547 | -58.8684 | -0.082398 | -0.12817 | 0.17395 | 0.3067 | -0.11444 | -0.15106 | -0.032043 | -0.068664 | -0.032044 | -0.10986 | -0.068665 | -0.13733 | 0.11444 | 0.12817 | 0.14648 | 0.16022 | 0.3891 | 123.2895 | -0.10529 | 122.9965 | 122.9874 | 122.9553 | 122.905 | 122.9233 | -123.1155 | -123.0652 | 123.2071 | 122.9645 | 39.0015 | 31.8604
448.9531 | 123.1522 | -58.9462 | 64.0549 | 0.22084 | -0.0018617 | 0.030537 | 0.081144 | -0.0035426 | -0.027676 | -0.0093278 | 0.15193 | 0.010956 | 0.088221 | 0.060523 | 4.2208e-05 | 0.0088412 | 0.0023694 | -20.1736 | 63.9862 | -59.0057 | 64.2471 | -58.7173 | -59.1156 | -59.0881 | -27.2552 | 64.0137 | -58.9737 | 64.0869 | -58.8638 | -59.1156 | -58.9783 | -0.059509 | -0.068665 | 0.19226 | 0.22888 | -0.14191 | -0.16937 | -0.082398 | -0.10986 | -0.027466 | -0.041199 | 0.032043 | 0.082397 | -0.032043 | -0.16937 | -0.004577 | -0.14191 | 0.28839 | 123.2529 | 0.10986 | 123.0606 | 122.9919 | 122.9874 | 122.9324 | 122.9599 | -123.0606 | -123.0286 | 123.1934 | 123.0331 | 38.7726 | 31.691
450.0312 | 123.1155 | -58.9645 | 64.0594 | 0.14455 | 0.012024 | 0.068989 | 0.089689 | 0.0028664 | -0.0031087 | 0.0013532 | -0.061691 | 0.0045474 | 0.05511 | 0.069068 | -0.012775 | 0.021658 | -0.0019036 | -20.6223 | 63.9038 | -59.0973 | 64.2654 | -58.7219 | -59.198 | -59.0332 | -27.5162 | 63.9816 | -59.0332 | 64.1144 | -58.9462 | -59.1431 | -59.0424 | -0.13275 | -0.15564 | 0.20599 | 0.24262 | -0.068664 | -0.23346 | 0.064087 | -0.10071 | -0.068664 | -0.07782 | 0.054932 | 0.018311 | -0.077819 | -0.17853 | -0.009155 | -0.10986 | 0.37537 | 123.3627 | 0.086975 | 123.1476 | 123.0011 | 123.0148 | 122.8683 | 122.9462 | -123.1567 | -123.0927 | 123.23 | 123.0789 | 38.3423 | 31.4484
450.9531 | 123.1842 | -58.9325 | 64.064 | 0.022479 | 0.010956 | 0.048695 | 0.082213 | -0.0046106 | -0.00097271 | -0.017873 | 0.30452 | 0.0034794 | 0.070063 | 0.072273 | -0.010639 | 0.01525 | -0.015789 | -20.4712 | 63.9313 | -58.9828 | 64.1373 | -58.8455 | -59.1751 | -59.2209 | -27.5391 | 63.9679 | -58.9233 | 64.1785 | -58.7448 | -59.024 | -58.9279 | -0.050354 | -0.13275 | 0.073242 | 0.086975 | -0.28839 | -0.24261 | -0.23804 | -0.19226 | 0.009155 | -0.09613 | 0.11444 | 0.18768 | 0.004578 | -0.091553 | -0.004577 | -0.10071 | 0.13733 | 123.1201 | 0.17853 | 123.1018 | 122.9141 | 122.8912 | 122.8638 | 122.9004 | -123.0469 | -122.9874 | 123.0698 | 123.111 | 38.4613 | 31.3934
452.0469 | 123.1338 | -58.9188 | 64.0961 | 0.037738 | 0.015228 | 0.041218 | 0.080076 | -0.0078156 | -0.029812 | -0.014668 | 0.060379 | 0.016296 | 0.06045 | 0.033821 | -0.013843 | 0.013113 | 0.0077094 | -20.842 | 63.9496 | -58.9691 | 64.1647 | -58.7814 | -59.1522 | -59.1431 | -27.7405 | 64.0137 | -58.96 | 64.1647 | -58.7952 | -59.0652 | -58.9737 | -0.050354 | -0.14648 | 0.068665 | 0.13733 | -0.2243 | -0.23346 | -0.17395 | -0.18311 | -0.041199 | -0.082397 | 0.068665 | 0.1236 | -0.054932 | -0.14648 | -0.013733 | -0.10529 | 0.18768 | 123.1338 | 0.16479 | 123.1247 | 122.9187 | 122.9736 | 122.8683 | 122.9324 | -123.0652 | -123.056 | 123.0835 | 123.0835 | 38.0768 | 31.1783
452.9531 | 123.1567 | -58.8913 | 64.1098 | 0.12929 | -0.0061337 | 0.031605 | 0.083281 | -0.0099516 | -0.019131 | -0.012532 | 0.090897 | 0.021637 | 0.074336 | 0.071205 | -0.0074348 | 0.0099092 | -0.0029716 | -21.0297 | 63.9679 | -58.992 | 64.2838 | -58.6945 | -59.024 | -59.111 | -27.9785 | 64.0137 | -58.96 | 64.1281 | -58.7631 | -59.1019 | -58.9645 | -0.10071 | -0.14191 | 0.17395 | 0.19684 | -0.21973 | -0.13275 | -0.11902 | -0.032044 | -0.068665 | -0.09613 | 0.018311 | 0.12817 | -0.073243 | -0.21057 | -0.004578 | -0.14191 | 0.29755 | 123.2758 | 0.19684 | 123.0881 | 122.9599 | 122.9736 | 122.8592 | 122.905 | -123.1018 | -123.0698 | 123.175 | 123.0194 | 37.8616 | 30.9128
454.0312 | 123.1018 | -58.905 | 64.1144 | 0.083514 | -0.0018617 | 0.038014 | 0.10037 | 0.0017974 | -0.012723 | -0.0136 | -0.061691 | 0.018433 | 0.078608 | 0.065864 | -0.011707 | 0.02059 | 0.024799 | -21.4783 | 63.9175 | -59.0561 | 64.2334 | -58.6578 | -59.0652 | -59.0927 | -28.3585 | 63.9954 | -58.992 | 63.8855 | -58.8913 | -58.873 | -58.8364 | -0.15106 | -0.19684 | 0.11902 | 0.24719 | -0.18768 | -0.16022 | -0.036621 | -0.009156 | -0.086975 | -0.11902 | -0.22888 | 0.013733 | 0.068664 | 0.032043 | 0.15564 | 0.11902 | 0.39825 | 123.2895 | 0.10071 | 122.8775 | 122.9736 | 122.9874 | 122.8226 | 122.9004 | -123.1705 | -123.1064 | 123.1384 | 122.7905 | 37.4268 | 30.5466
454.9531 | 123.1659 | -58.9142 | 64.1144 | 0.14455 | 0.0088203 | 0.041218 | 0.090757 | -0.0035426 | -0.00097271 | -0.0071918 | 0.15193 | 0.0066834 | 0.080744 | 0.080818 | -0.0031618 | 0.010977 | 0.0077094 | -21.6202 | 64.0091 | -58.992 | 64.325 | -58.6624 | -59.0561 | -59.0652 | -28.2806 | 64.0228 | -58.9417 | 64.1418 | -58.8181 | -59.0927 | -58.96 | -0.077819 | -0.10529 | 0.21057 | 0.25177 | -0.15106 | -0.14191 | -0.073243 | -0.064087 | -0.027465 | -0.091553 | 0.027466 | 0.096131 | -0.045776 | -0.17853 | -0.018311 | -0.15106 | 0.32959 | 123.317 | 0.1236 | 123.0835 | 123.0011 | 122.9645 | 122.9233 | 122.937 | -123.1064 | -123.056 | 123.2391 | 123.056 | 37.294 | 30.6335
456.0312 | 123.1476 | -58.9371 | 64.0686 | 0.12929 | 0.0034793 | 0.039082 | 0.084349 | -0.012088 | -0.02554 | 0.00028524 | -0.031174 | 0.012024 | 0.087153 | 0.051979 | -0.0063668 | 0.016318 | -0.013653 | -21.8811 | 63.9679 | -59.0057 | 64.2426 | -58.7265 | -59.0836 | -59.1202 | -28.4912 | 64.0182 | -58.9462 | 64.1418 | -58.7814 | -59.1339 | -58.9462 | -0.068664 | -0.10071 | 0.17395 | 0.21057 | -0.18311 | -0.14648 | -0.11444 | -0.07782 | -0.009155 | -0.050354 | 0.073242 | 0.15564 | -0.009155 | -0.19684 | 0 | -0.18768 | 0.27924 | 123.2483 | 0.16479 | 123.0881 | 122.9736 | 122.9645 | 122.905 | 122.9553 | -123.0743 | -123.0148 | 123.1796 | 123.0789 | 37.056 | 30.4459
456.9688 | 123.1796 | -58.9096 | 64.0549 | 0.11403 | -0.0039977 | 0.033741 | 0.085417 | 0.016751 | -0.019131 | 0.0045582 | -0.015915 | 0.020569 | 0.07754 | 0.04557 | -0.0095708 | 0.017386 | 0.0066414 | -22.1008 | 63.9816 | -59.0286 | 64.2792 | -58.7219 | -59.0607 | -59.1476 | -28.6652 | 63.9999 | -58.9462 | 64.1556 | -58.8272 | -59.0836 | -59.0424 | -0.11902 | -0.073243 | 0.2243 | 0.18768 | -0.23804 | -0.15106 | -0.11902 | -0.032044 | -0.036621 | -0.054932 | 0.10071 | 0.082398 | -0.13275 | -0.17395 | -0.09613 | -0.13733 | 0.3067 | 123.3078 | 0.11902 | 123.1018 | 123.0103 | 122.9462 | 122.8912 | 122.9095 | -123.0835 | -123.0011 | 123.1888 | 123.0652 | 36.8088 | 30.2444
457.9531 | 123.1247 | -58.9188 | 64.1281 | 0.15981 | 0.0045473 | 0.032673 | 0.083281 | -0.015292 | -0.016995 | -0.018941 | 0.12141 | 0.0066834 | 0.073268 | 0.04557 | -0.0095708 | 0.01525 | 0.0045054 | -22.2565 | 64.0091 | -58.9508 | 64.2334 | -58.6533 | -59.0927 | -59.0103 | -28.7064 | 64.0411 | -58.9279 | 64.1876 | -58.7723 | -59.0515 | -58.9691 | -0.032044 | -0.11902 | 0.10528 | 0.2655 | -0.091553 | -0.17395 | -0.059509 | -0.14191 | -0.009155 | -0.086975 | 0.059509 | 0.14648 | -0.050354 | -0.13275 | -0.041199 | -0.1236 | 0.29755 | 123.1842 | 0.15564 | 123.1155 | 122.9599 | 122.9691 | 122.9279 | 122.9599 | -123.0789 | -123.056 | 123.1522 | 123.1064 | 36.6623 | 30.2124
458.9531 | 123.1201 | -58.8959 | 64.119 | 0.25136 | -0.0018617 | 0.025197 | 0.089689 | 0.019955 | 9.5287e-05 | -0.027486 | 0.04512 | 0.0088204 | 0.065791 | 0.039161 | -0.0042298 | 0.0045682 | -0.00083564 | -22.5906 | 64.032 | -58.9691 | 64.3387 | -58.6395 | -59.0515 | -58.9874 | -28.7888 | 64.0594 | -58.9188 | 64.1464 | -58.7997 | -59.0195 | -59.0332 | -0.073242 | -0.086976 | 0.21973 | 0.25635 | -0.091553 | -0.15564 | -0.018311 | -0.082398 | -0.022888 | -0.05951 | 0.027465 | 0.09613 | -0.13733 | -0.1236 | -0.11444 | -0.10071 | 0.32959 | 123.3078 | 0.11902 | 123.0652 | 123.0011 | 122.9782 | 122.9279 | 122.9553 | -123.0881 | -123.0377 | 123.2346 | 123.0423 | 36.3052 | 30.1071
460.0312 | 123.143 | -58.905 | 64.1098 | 0.052997 | 0.0077523 | 0.038014 | 0.085417 | 0.00072943 | 0.010776 | 0.00028524 | 0.029861 | 0.0098884 | 0.056178 | 0.090431 | -0.010639 | 0.017386 | 0.011982 | -22.8012 | 63.9816 | -59.024 | 64.325 | -58.6487 | -58.9691 | -59.0424 | -29.1275 | 64.0045 | -58.9691 | 64.1006 | -58.7631 | -59.1614 | -59.0103 | -0.11902 | -0.12817 | 0.21515 | 0.25635 | -0.13733 | -0.064087 | -0.01831 | 0.054932 | -0.064087 | -0.10528 | -0.009155 | 0.14191 | -0.10529 | -0.25635 | -0.041199 | -0.19226 | 0.37537 | 123.349 | 0.20599 | 123.0698 | 123.0057 | 122.9736 | 122.8867 | 122.9095 | -123.1338 | -123.0789 | 123.23 | 123.0057 | 36.1038 | 29.7775
460.9531 | 123.1064 | -58.8821 | 64.119 | -0.023297 | 0.0045473 | 0.029469 | 0.082213 | 0.01141 | 0.0032993 | -0.0039868 | -0.53471 | 0.0013434 | 0.092494 | 0.038093 | -0.018116 | 0.01525 | 0.0045054 | -23.0026 | 64.0366 | -58.9371 | 64.3478 | -58.6166 | -59.0286 | -59.0012 | -29.155 | 64.119 | -58.8776 | 64.2197 | -58.8226 | -59.0149 | -58.9645 | -0.054932 | -0.082398 | 0.22888 | 0.2655 | -0.11902 | -0.14648 | -0.064087 | -0.091552 | 0.004578 | 0 | 0.10071 | 0.059509 | -0.082398 | -0.13275 | -0.086976 | -0.13733 | 0.32043 | 123.2849 | 0.054931 | 123.0972 | 122.9736 | 122.9965 | 122.9187 | 123.0011 | -123.056 | -122.9965 | 123.23 | 123.1018 | 35.8795 | 29.7272
462.0312 | 123.2574 | -58.8409 | 64.1052 | 0.083514 | 0.0098883 | 0.027333 | 0.07794 | 0.018887 | -0.0041777 | -0.010396 | 0.33504 | 0.0077514 | 0.078608 | 0.02848 | -0.012775 | 0.01525 | -0.011517 | -23.2086 | 63.9908 | -58.9417 | 64.238 | -58.8043 | -59.1431 | -59.1751 | -29.2374 | 64.0091 | -58.9005 | 64.2838 | -58.6075 | -58.8776 | -58.8364 | -0.10071 | -0.11444 | 0.13275 | 0.036621 | -0.33417 | -0.30212 | -0.23346 | -0.20142 | -0.05951 | -0.096131 | 0.17853 | 0.23346 | 0.004577 | -0.036621 | 0.064087 | 0.022889 | 0.13733 | 123.1796 | 0.29297 | 123.1842 | 122.9324 | 122.9095 | 122.8317 | 122.85 | -123.0469 | -123.0057 | 123.0789 | 123.1247 | 35.6323 | 29.6036
462.9688 | 123.1155 | -58.905 | 64.1235 | 0.0072204 | 0.0088203 | 0.03481 | 0.080076 | 0.014615 | 0.021457 | -0.015736 | 0.48762 | 0.010956 | 0.067927 | 0.06266 | -0.012775 | 0.018454 | -0.0083126 | -23.5565 | 63.9908 | -59.0286 | 64.3112 | -58.58 | -59.1156 | -59.2941 | -29.5624 | 64.0549 | -58.9691 | 64.151 | -58.8181 | -59.079 | -59.0149 | -0.1236 | -0.13275 | 0.18768 | 0.32501 | -0.3891 | -0.21057 | -0.2655 | -0.086976 | -0.064087 | -0.068664 | 0.027466 | 0.086975 | -0.10986 | -0.17395 | -0.045777 | -0.10986 | 0.44861 | 123.3398 | 0.15106 | 123.1201 | 123.0194 | 123.024 | 122.8958 | 122.9599 | -123.1522 | -123.0927 | 123.2162 | 123.056 | 35.3485 | 29.3427
464.0312 | 123.2025 | -58.8821 | 64.1144 | 0.17507 | 0.0056153 | 0.039082 | 0.088621 | 0.013547 | -0.010586 | 0.0077622 | -0.82463 | -0.0029296 | 0.068995 | 0.037025 | -0.014912 | 0.016318 | 0.00023236 | -23.5931 | 63.9999 | -58.9737 | 64.3204 | -58.7082 | -59.079 | -59.0652 | -29.4022 | 64.0411 | -58.9371 | 64.2334 | -58.6487 | -58.9645 | -58.9233 | -0.091553 | -0.11444 | 0.20599 | 0.17395 | -0.18311 | -0.19684 | -0.091553 | -0.10528 | -0.054932 | -0.073242 | 0.11902 | 0.23346 | -0.041199 | -0.082398 | 0.013733 | -0.027466 | 0.2655 | 123.2941 | 0.28839 | 123.1705 | 122.9736 | 122.9782 | 122.8821 | 122.9233 | -123.0881 | -123.0515 | 123.2025 | 123.1155 | 35.289 | 29.48
464.9531 | 123.1659 | -58.8684 | 64.119 | 0.14455 | 0.010956 | 0.038014 | 0.088621 | 0.0071384 | -0.00097271 | -0.0093278 | -0.046432 | 0.013092 | 0.065791 | 0.061592 | -0.0020938 | 0.019522 | -0.012585 | -23.8083 | 63.9999 | -58.96 | 64.27 | -58.667 | -59.111 | -59.0149 | -29.6539 | 64.0457 | -58.905 | 64.2471 | -58.7082 | -58.9874 | -58.9233 | -0.091553 | -0.11902 | 0.15106 | 0.20142 | -0.14648 | -0.24262 | -0.054932 | -0.15106 | -0.036621 | -0.073243 | 0.12817 | 0.16022 | -0.054932 | -0.11902 | -0.018311 | -0.082398 | 0.29297 | 123.23 | 0.19684 | 123.1522 | 122.9599 | 122.9507 | 122.8683 | 122.9141 | -123.0789 | -123.024 | 123.1384 | 123.1155 | 35.0601 | 29.2145
466.0312 | 123.111 | -58.9005 | 64.1464 | 0.17507 | 0.00027529 | 0.031605 | 0.093962 | 0.02316 | -0.0063137 | -0.0136 | -0.07695 | 0.0077514 | 0.061518 | 0.059455 | -0.012775 | -0.0071808 | -0.011517 | -24.1196 | 63.9862 | -59.0103 | 64.3524 | -58.6166 | -58.992 | -58.9966 | -29.8233 | 64.0182 | -58.992 | 64.2151 | -58.8684 | -58.9966 | -58.9508 | -0.10986 | -0.16022 | 0.20599 | 0.28381 | -0.09613 | -0.091552 | 0.013733 | 0.018311 | -0.091552 | -0.12817 | 0.068665 | 0.032044 | -0.050354 | -0.09613 | 0.041198 | -0.004578 | 0.39368 | 123.3627 | 0.1236 | 123.2071 | 122.9965 | 123.0103 | 122.8867 | 122.9187 | -123.1567 | -123.1384 | 123.2529 | 123.1155 | 34.7809 | 29.0771
466.9688 | 123.1064 | -58.9096 | 64.1144 | 0.068255 | 0.0077523 | 0.041218 | 0.086485 | 0.00072943 | -0.012723 | -0.0018508 | 0.029861 | 0.0077514 | 0.0722 | 0.071205 | -0.0020938 | 0.012045 | -0.026471 | -24.4308 | 64.0182 | -58.9645 | 64.3021 | -58.5892 | -59.0698 | -58.9966 | -29.8782 | 64.0686 | -58.96 | 64.1739 | -58.7952 | -59.0927 | -58.9554 | -0.054932 | -0.09613 | 0.18768 | 0.32044 | -0.086975 | -0.16022 | -0.032043 | -0.10528 | -0.050354 | -0.045776 | 0.059509 | 0.11444 | -0.045776 | -0.1831 | 0.004578 | -0.13275 | 0.37537 | 123.2666 | 0.16479 | 123.1338 | 122.9828 | 123.0286 | 122.9279 | 122.9782 | -123.0789 | -123.0743 | 123.2117 | 123.0835 | 34.4788 | 29.0314
468.0312 | 123.2758 | -58.8135 | 64.1052 | 0.098773 | 0.0034793 | 0.027333 | 0.089689 | 0.032773 | -0.0041777 | -0.0082598 | 0.41133 | 0.0013434 | 0.092494 | 0.05091 | -0.014912 | 0.013113 | 0.022663 | -24.4308 | 63.9954 | -58.8821 | 64.1876 | -58.7402 | -59.1797 | -59.1064 | -29.5944 | 64.0228 | -58.8913 | 64.3799 | -58.5709 | -58.7906 | -58.7952 | -0.068664 | -0.10986 | 0.082397 | 0.073243 | -0.29297 | -0.36621 | -0.2243 | -0.29755 | -0.077819 | -0.082398 | 0.27466 | 0.24262 | 0.018311 | 0.022889 | 0.09613 | 0.10071 | 0.14191 | 123.0698 | 0.32043 | 123.2712 | 122.8775 | 122.9141 | 122.8088 | 122.8363 | -122.9874 | -122.9965 | 123.0011 | 123.1934 | 34.3826 | 29.2191
468.9531 | 123.1522 | -58.8501 | 64.151 | 0.19033 | 0.0024113 | 0.030537 | 0.088621 | -0.01102 | -0.023404 | -0.0061228 | 0.090897 | 0.021637 | 0.074336 | 0.053047 | -0.013843 | 0.02059 | -0.016858 | -24.5911 | 64.0549 | -58.9233 | 64.2883 | -58.5617 | -59.0698 | -58.9966 | -29.9103 | 64.0778 | -58.873 | 64.2654 | -58.5892 | -58.9966 | -58.8593 | -0.073242 | -0.09613 | 0.13733 | 0.28839 | -0.14648 | -0.21973 | -0.073242 | -0.14648 | -0.022888 | -0.073242 | 0.11444 | 0.26093 | -0.009155 | -0.14648 | 0.013733 | -0.1236 | 0.36163 | 123.2117 | 0.28381 | 123.1384 | 122.9782 | 122.9507 | 122.905 | 122.9279 | -123.0743 | -123.024 | 123.1384 | 123.1155 | 34.259 | 28.9398
470.0312 | 123.2162 | -58.8501 | 64.0961 | -0.023297 | 0.0034793 | 0.024128 | 0.083281 | -0.015292 | 0.01398 | -0.0039868 | -0.031174 | 0.015228 | 0.078608 | 0.053047 | -0.0095708 | 0.014181 | 0.00023236 | -24.9481 | 64.0182 | -58.96 | 64.2517 | -58.6075 | -59.079 | -59.0424 | -30.336 | 64.064 | -58.8913 | 64.2838 | -58.6349 | -58.9508 | -58.8776 | -0.10986 | -0.077819 | 0.15564 | 0.24262 | -0.19226 | -0.22888 | -0.082397 | -0.11902 | -0.041198 | -0.032043 | 0.18768 | 0.21515 | -0.027465 | -0.10071 | 0.013733 | -0.05951 | 0.35248 | 123.2117 | 0.25635 | 123.175 | 122.9782 | 122.9553 | 122.8683 | 122.9141 | -123.056 | -122.9874 | 123.1018 | 123.1339 | 33.902 | 28.5141
470.9531 | 123.1888 | -58.8089 | 64.1876 | 0.20559 | 0.0045473 | 0.032673 | 0.082213 | 0.0060704 | 0.0022313 | 0.0066942 | 0.30452 | 0.015228 | 0.096766 | 0.080818 | -0.0085028 | 0.012045 | 0.0034374 | -24.939 | 64.0732 | -58.9142 | 64.3341 | -58.5846 | -58.9874 | -58.9462 | -30.6656 | 64.0778 | -58.8638 | 64.1876 | -58.5892 | -58.9828 | -58.7311 | -0.10529 | -0.11444 | 0.14648 | 0.2243 | -0.13733 | -0.17853 | -0.032043 | -0.073242 | -0.054932 | -0.10986 | 0 | 0.21973 | 0.07782 | -0.17395 | 0.13275 | -0.11902 | 0.32959 | 123.2483 | 0.27466 | 123.0515 | 122.9874 | 122.9416 | 122.8821 | 122.8867 | -123.1018 | -123.0515 | 123.143 | 122.9965 | 33.8699 | 28.1433
471.9688 | 123.143 | -58.873 | 64.1235 | 0.037738 | -0.00079271 | 0.033741 | 0.083281 | -0.00033857 | -0.027676 | -0.0071918 | 0.029861 | 0.0098884 | 0.068995 | 0.05091 | -0.0085028 | 0.028067 | 0.0023694 | -25.0763 | 64.0686 | -58.9691 | 64.357 | -58.5938 | -59.0195 | -58.9966 | -30.8624 | 64.064 | -58.8959 | 64.238 | -58.6945 | -58.9554 | -58.9233 | -0.09613 | -0.054931 | 0.23346 | 0.27924 | -0.1236 | -0.14648 | -0.027466 | -0.050354 | -0.022888 | -0.059509 | 0.11444 | 0.17853 | -0.050354 | -0.082397 | -0.027466 | -0.059509 | 0.37537 | 123.3261 | 0.20142 | 123.1338 | 123.0377 | 122.9599 | 122.9416 | 122.937 | -123.0927 | -123.0194 | 123.23 | 123.111 | 33.7967 | 28.0106
473.0469 | 123.1705 | -58.8135 | 64.1647 | 0.068255 | 0.010956 | 0.031605 | 0.098234 | -0.0014066 | -0.0063137 | -0.0018508 | 0.029861 | 0.0077514 | 0.068995 | 0.066932 | -0.012775 | 0.016318 | 0.010913 | -25.1312 | 64.0457 | -58.9417 | 64.3066 | -58.6716 | -58.9554 | -59.0561 | -30.8075 | 64.0778 | -58.8547 | 64.2517 | -58.5754 | -58.9188 | -58.8776 | -0.12817 | -0.11902 | 0.14191 | 0.14191 | -0.24261 | -0.14191 | -0.11444 | -0.013733 | -0.041198 | -0.086975 | 0.086975 | 0.23804 | -0.064086 | -0.10529 | -0.022888 | -0.064087 | 0.27008 | 123.2483 | 0.27924 | 123.1064 | 122.9874 | 122.9324 | 122.8592 | 122.8912 | -123.1064 | -123.0194 | 123.1201 | 123.0652 | 33.6823 | 28.006
473.9531 | 123.1705 | -58.8272 | 64.1968 | 0.17507 | 0.0056153 | 0.030537 | 0.085417 | 0.0082064 | -0.0020407 | -0.011464 | 0.060379 | 0.0045474 | 0.082881 | 0.061592 | -0.013843 | 0.021658 | -0.017926 | -25.264 | 64.0869 | -58.8959 | 64.3982 | -58.5068 | -59.0057 | -58.9096 | -30.899 | 64.1373 | -58.8593 | 64.3112 | -58.6212 | -58.8913 | -58.8684 | -0.068665 | -0.10986 | 0.20142 | 0.32043 | -0.082398 | -0.17853 | -0.013733 | -0.10986 | -0.032044 | -0.059509 | 0.11444 | 0.20599 | -0.041199 | -0.064087 | -0.009155 | -0.032043 | 0.3891 | 123.2941 | 0.23804 | 123.1705 | 122.9828 | 122.9965 | 122.9141 | 122.9645 | -123.0927 | -123.056 | 123.2254 | 123.1384 | 33.5632 | 27.9282
475.0312 | 123.111 | -58.8272 | 64.2014 | -0.0080386 | 0.0088203 | 0.033741 | 0.090757 | 0.0082064 | -0.027676 | -0.0071918 | -0.00065608 | 0.013092 | 0.090358 | 0.018867 | -0.019184 | 0.019522 | -0.027539 | -25.4974 | 64.032 | -58.9417 | 64.4394 | -58.5297 | -58.9233 | -58.9645 | -31.0272 | 64.1144 | -58.8913 | 64.2426 | -58.5709 | -58.9554 | -58.9645 | -0.11444 | -0.16937 | 0.23804 | 0.29755 | -0.13733 | -0.096131 | -0.022889 | 0.01831 | -0.064087 | -0.086975 | 0.041199 | 0.25635 | -0.13733 | -0.12817 | -0.073243 | -0.064087 | 0.41199 | 123.381 | 0.32043 | 123.1338 | 122.9736 | 123.0057 | 122.8592 | 122.9416 | -123.143 | -123.0927 | 123.2666 | 123.0698 | 33.3298 | 27.8
475.9531 | 123.111 | -58.8043 | 64.2014 | 0.25136 | 0.0077523 | 0.029469 | 0.086485 | -0.0056786 | -0.0073817 | -0.0093278 | 0.060379 | 0.015228 | 0.0722 | 0.053047 | -0.019184 | 0.010977 | 0.020526 | -25.5478 | 64.1098 | -58.8913 | 64.3936 | -58.4976 | -58.9828 | -58.8638 | -31.0593 | 64.1281 | -58.8638 | 64.2609 | -58.5663 | -58.8821 | -58.8867 | -0.086975 | -0.091553 | 0.19226 | 0.3067 | -0.05951 | -0.17853 | 0.027465 | -0.091553 | -0.05951 | -0.073242 | 0.059509 | 0.23804 | -0.082398 | -0.07782 | -0.022888 | -0.01831 | 0.39368 | 123.2849 | 0.29755 | 123.1247 | 123.0011 | 122.9919 | 122.9141 | 122.9324 | -123.0927 | -123.0652 | 123.1979 | 123.0652 | 33.2565 | 27.7451
477.0312 | 123.2025 | -58.7906 | 64.1602 | 0.022479 | 0.00027529 | 0.033741 | 0.079008 | 0.012479 | -0.0052457 | -0.00078276 | 0.13667 | 0.0066834 | 0.0722 | 0.037025 | -0.0020938 | 0.01525 | -0.016858 | -25.6851 | 64.0137 | -58.9005 | 64.2563 | -58.6624 | -59.0607 | -59.0973 | -30.954 | 64.0594 | -58.8455 | 64.3066 | -58.5251 | -58.8501 | -58.8226 | -0.10986 | -0.14648 | 0.096131 | 0.12817 | -0.3067 | -0.27008 | -0.19684 | -0.16022 | -0.054932 | -0.10071 | 0.14648 | 0.2655 | -0.032044 | -0.05951 | 0.022888 | -0.004578 | 0.23804 | 123.1567 | 0.32044 | 123.1522 | 122.9141 | 122.905 | 122.8043 | 122.85 | -123.0606 | -123.0057 | 123.0469 | 123.0972 | 33.1055 | 27.8366
477.9688 | 123.2208 | -58.7631 | 64.1922 | -0.084332 | 0.0088203 | 0.01772 | 0.07794 | -0.01102 | -0.0084497 | 0.0034902 | 0.04512 | -0.0007936 | 0.082881 | 0.039161 | -0.0052988 | 0.014181 | -0.010449 | -25.7446 | 64.0686 | -58.8364 | 64.2059 | -58.6395 | -59.0927 | -59.0424 | -30.9402 | 64.0869 | -58.8135 | 64.3662 | -58.4198 | -58.7906 | -58.7265 | -0.073242 | -0.1236 | 0.013733 | 0.1236 | -0.27923 | -0.32959 | -0.20599 | -0.25635 | -0.050354 | -0.10529 | 0.17395 | 0.34332 | 0.036622 | -0.027465 | 0.086976 | 0.022889 | 0.19684 | 123.0423 | 0.39368 | 123.1796 | 122.905 | 122.9004 | 122.8317 | 122.85 | -123.0286 | -123.0057 | 122.9691 | 123.1293 | 33.0185 | 27.8229
479.0312 | 123.111 | -58.8043 | 64.2197 | 0.098773 | 0.0056153 | 0.028401 | 0.10251 | -0.0088836 | -0.029812 | 0.00028524 | -0.15324 | 0.015228 | 0.065791 | 0.047706 | -0.017048 | 0.01525 | 0.0087774 | -26.0056 | 64.0869 | -58.8913 | 64.3707 | -58.5342 | -58.96 | -58.9371 | -31.0226 | 64.1281 | -58.8409 | 64.2609 | -58.5846 | -58.9233 | -58.9188 | -0.086975 | -0.13275 | 0.15106 | 0.27008 | -0.13275 | -0.15564 | -0.045777 | -0.068665 | -0.036621 | -0.091553 | 0.041198 | 0.21973 | -0.11444 | -0.11902 | -0.07782 | -0.082398 | 0.35705 | 123.262 | 0.25635 | 123.1018 | 122.9782 | 122.9691 | 122.8912 | 122.9324 | -123.111 | -123.0606 | 123.175 | 123.0652 | 32.7988 | 27.7817
479.9531 | 123.1522 | -58.7769 | 64.2288 | 0.098773 | 0.0034793 | 0.029469 | 0.092894 | -0.0067466 | -0.024472 | -0.0039868 | 0.12141 | 0.0024114 | 0.074336 | 0.051979 | -0.014912 | 0.0099092 | 0.0045054 | -26.0605 | 64.1235 | -58.8638 | 64.3845 | -58.4244 | -58.9691 | -58.8913 | -30.9586 | 64.1556 | -58.8638 | 64.2929 | -58.5159 | -58.905 | -58.8043 | -0.086976 | -0.10529 | 0.15564 | 0.35248 | -0.11444 | -0.19226 | -0.027465 | -0.10529 | -0.086976 | -0.073242 | 0.064087 | 0.26093 | -0.027466 | -0.12817 | 0.05951 | -0.041198 | 0.43945 | 123.2483 | 0.3479 | 123.1567 | 122.9874 | 123.0194 | 122.9004 | 122.9324 | -123.0927 | -123.0927 | 123.1613 | 123.0698 | 32.7164 | 27.8183
481.0312 | 123.0835 | -58.8043 | 64.2105 | 0.037738 | 0.010956 | 0.028401 | 0.087553 | 0.0028664 | 0.0022313 | -0.011464 | -0.00065608 | 0.0077514 | 0.070063 | 0.04557 | -0.0074348 | 0.014181 | -0.0029716 | -26.2756 | 64.0869 | -58.8821 | 64.389 | -58.4564 | -58.9325 | -58.9096 | -30.9448 | 64.151 | -58.8409 | 64.2746 | -58.6166 | -58.9828 | -58.8776 | -0.07782 | -0.1236 | 0.17853 | 0.3479 | -0.10529 | -0.12817 | -0.027466 | -0.050354 | -0.036621 | -0.059509 | 0.064087 | 0.18768 | -0.073242 | -0.17853 | -0.036621 | -0.14191 | 0.42572 | 123.2712 | 0.2243 | 123.1155 | 122.9691 | 122.9919 | 122.8912 | 122.9553 | -123.0927 | -123.0515 | 123.1934 | 123.0789 | 32.5287 | 27.8595
481.9531 | 123.1338 | -58.7677 | 64.2609 | 0.14455 | -0.0093377 | 0.0091751 | 0.079008 | -0.0035426 | -0.0052457 | 0.013103 | 0.10615 | 0.0088204 | 0.056178 | 0.063728 | -0.0010258 | 0.012045 | 0.0077094 | -26.207 | 64.2197 | -58.8181 | 64.4394 | -58.4244 | -58.905 | -58.8776 | -30.899 | 64.1785 | -58.8043 | 64.2654 | -58.4702 | -58.9096 | -58.7677 | -0.050354 | -0.041198 | 0.17853 | 0.34332 | -0.10986 | -0.13733 | -0.059509 | -0.086975 | -0.036621 | -0.082397 | 0.004578 | 0.29755 | 0 | -0.14191 | 0.036621 | -0.10529 | 0.39368 | 123.2574 | 0.33417 | 123.0698 | 123.0377 | 122.9828 | 122.9874 | 122.9462 | -123.0789 | -123.0652 | 123.2071 | 123.0331 | 32.5607 | 27.8687
482.9688 | 123.1842 | -58.7402 | 64.2471 | 0.20559 | 0.0024113 | 0.031605 | 0.084349 | 0.017819 | -0.019131 | -0.0071918 | 0.31978 | 0.0034794 | 0.070063 | 0.044502 | -0.0042298 | 0.01525 | -0.0093806 | -26.7242 | 64.0915 | -58.7997 | 64.3066 | -58.5617 | -59.024 | -58.9783 | -30.6519 | 64.1418 | -58.7769 | 64.3982 | -58.374 | -58.7585 | -58.7402 | -0.05951 | -0.15564 | 0.05951 | 0.17853 | -0.23804 | -0.28381 | -0.17853 | -0.2243 | -0.036621 | -0.10528 | 0.15106 | 0.36621 | 0 | -0.018311 | 0.036621 | 0.01831 | 0.23804 | 123.1064 | 0.40283 | 123.175 | 122.8912 | 122.9187 | 122.8317 | 122.8821 | -123.0469 | -123.024 | 123.0469 | 123.1384 | 32.016 | 28.0884
483.9531 | 123.1522 | -58.7997 | 64.2426 | 0.083514 | -0.0018617 | 0.02306 | 0.07794 | 0.0071384 | -0.012723 | -0.011464 | 0.13667 | 0.019501 | 0.089289 | 0.082954 | -0.011707 | 0.0067052 | -0.0029716 | -26.8204 | 64.1602 | -58.8272 | 64.4257 | -58.4518 | -58.8455 | -58.8867 | -30.7892 | 64.183 | -58.786 | 64.4577 | -58.5571 | -59.0469 | -58.8593 | -0.027465 | -0.082398 | 0.1831 | 0.3479 | -0.086975 | -0.045776 | -0.05951 | -0.018311 | 0.013733 | -0.05951 | 0.21515 | 0.24261 | -0.059509 | -0.24719 | -0.073242 | -0.26093 | 0.37537 | 123.2529 | 0.22888 | 123.2437 | 122.9874 | 122.9691 | 122.9599 | 122.9828 | -123.0698 | -123.0286 | 123.2254 | 123.2574 | 31.9794 | 28.0106
485.0312 | 123.1522 | -58.7723 | 64.2746 | 0.14455 | 0.0088203 | 0.041218 | 0.085417 | -0.0056786 | -0.0084497 | -0.0071918 | -0.061691 | 0.018433 | 0.067927 | 0.10004 | -0.014912 | 0.013113 | -0.00083564 | -26.9943 | 64.1144 | -58.8318 | 64.3616 | -58.4656 | -58.9462 | -58.905 | -30.6519 | 64.1418 | -58.8089 | 64.3433 | -58.4564 | -58.8821 | -58.7769 | -0.059509 | -0.16022 | 0.086975 | 0.3067 | -0.13275 | -0.17395 | -0.073242 | -0.11444 | -0.036621 | -0.13275 | 0.068665 | 0.31586 | -0.004577 | -0.10986 | 0.032044 | -0.073242 | 0.36621 | 123.1934 | 0.35248 | 123.1522 | 122.9462 | 122.9507 | 122.8867 | 122.9141 | -123.1064 | -123.0835 | 123.1338 | 123.1155 | 31.778 | 28.1204
485.9688 | 123.1934 | -58.754 | 64.27 | 0.098773 | 0.0013433 | 0.018788 | 0.091826 | -0.00033857 | -0.0020407 | -0.014668 | 0.10615 | 0.013092 | 0.054042 | 0.057319 | -0.012775 | 0.018454 | -0.010449 | -27.0309 | 64.1373 | -58.8272 | 64.3982 | -58.4702 | -58.8867 | -58.9554 | -30.5969 | 64.1785 | -58.7769 | 64.3295 | -58.3282 | -58.8547 | -58.7357 | -0.073242 | -0.13275 | 0.12817 | 0.28381 | -0.20142 | -0.13275 | -0.12817 | -0.05951 | -0.022888 | -0.091553 | 0.059509 | 0.42572 | 0.01831 | -0.10071 | 0.041198 | -0.07782 | 0.35706 | 123.2254 | 0.44861 | 123.1064 | 122.9645 | 122.9553 | 122.8912 | 122.9324 | -123.0972 | -123.0469 | 123.1522 | 123.0835 | 31.723 | 28.157
487.0312 | 123.1247 | -58.7494 | 64.27 | 0.12929 | 0.0024113 | 0.025197 | 0.090757 | 0.012479 | -0.0020407 | -0.0050548 | -0.031174 | 0.010956 | 0.07754 | 0.070137 | -0.011707 | 0.024863 | 0.0055734 | -27.0767 | 64.1281 | -58.8455 | 64.389 | -58.4244 | -58.9142 | -58.9005 | -30.6198 | 64.1785 | -58.8043 | 64.3204 | -58.4244 | -58.8867 | -58.7677 | -0.09613 | -0.14191 | 0.11902 | 0.32501 | -0.15106 | -0.1648 | -0.054932 | -0.068665 | -0.054931 | -0.091553 | 0.050354 | 0.32501 | -0.01831 | -0.13733 | 0.036621 | -0.082398 | 0.42114 | 123.2346 | 0.37994 | 123.1247 | 122.9736 | 122.9828 | 122.8775 | 122.9279 | -123.1155 | -123.0743 | 123.1384 | 123.0698 | 31.6727 | 28.1296
487.9844 | 123.1018 | -58.7814 | 64.2746 | 0.083514 | 0.0077523 | 0.030537 | 0.082213 | -0.0099516 | -0.016995 | 0.00028524 | -0.092209 | 0.020569 | 0.078608 | 0.063728 | -0.0085028 | 0.021658 | -0.017926 | -27.2507 | 64.1373 | -58.8409 | 64.476 | -58.4518 | -58.7997 | -58.9005 | -30.5786 | 64.1968 | -58.8089 | 64.2517 | -58.4702 | -58.9371 | -58.7997 | -0.059509 | -0.13733 | 0.20142 | 0.32959 | -0.11902 | -0.018311 | -0.05951 | 0.041198 | -0.027466 | -0.07782 | -0.022888 | 0.31128 | -0.018311 | -0.15564 | 0.009155 | -0.12817 | 0.3891 | 123.317 | 0.33874 | 123.0606 | 122.9782 | 123.0057 | 122.9187 | 122.9782 | -123.1155 | -123.0835 | 123.2574 | 123.0331 | 31.5308 | 28.2028
489.0156 | 123.2025 | -58.7082 | 64.2563 | -0.038556 | 0.00027529 | 0.024128 | 0.083281 | 0.01141 | 0.0022313 | -0.0039868 | 0.19771 | 0.0077514 | 0.064723 | 0.064796 | -0.0010258 | 0.0067052 | -0.0029716 | -27.3239 | 64.1098 | -58.7952 | 64.2792 | -58.5114 | -58.9645 | -58.9783 | -30.423 | 64.1418 | -58.7723 | 64.3204 | -58.342 | -58.7814 | -58.6945 | -0.086975 | -0.14648 | 0.022888 | 0.19684 | -0.27008 | -0.25635 | -0.1831 | -0.16937 | -0.064087 | -0.11444 | 0.064087 | 0.36621 | 0.013733 | -0.073242 | 0.07782 | -0.009155 | 0.28381 | 123.0743 | 0.4303 | 123.0927 | 122.905 | 122.9141 | 122.818 | 122.85 | -123.0515 | -123.0286 | 122.9874 | 123.0286 | 31.3843 | 28.2852
489.9531 | 123.111 | -58.754 | 64.2609 | -0.023297 | 0.019501 | 0.026265 | 0.088621 | 0.00072943 | -0.022336 | -0.0039868 | -0.12273 | 0.01416 | 0.071131 | 0.066932 | -0.011707 | 0.018454 | 0.0055734 | -27.4246 | 64.1556 | -58.8272 | 64.476 | -58.4518 | -58.8364 | -58.8959 | -30.3818 | 64.183 | -58.7906 | 64.2654 | -58.4061 | -58.905 | -58.7814 | -0.073242 | -0.10528 | 0.21515 | 0.30212 | -0.14191 | -0.082398 | -0.068665 | -0.009156 | -0.036621 | -0.07782 | 0.004578 | 0.3479 | -0.027466 | -0.15106 | 0.009155 | -0.11444 | 0.37537 | 123.3032 | 0.38452 | 123.056 | 122.9828 | 122.9736 | 122.9095 | 122.937 | -123.0881 | -123.0515 | 123.23 | 123.0194 | 31.3293 | 28.3722
491.0312 | 123.0927 | -58.7494 | 64.2654 | 0.12929 | 0.0077523 | 0.021992 | 0.084349 | -0.0056786 | -0.012723 | -0.0061228 | 0.04512 | 0.018433 | 0.057246 | 0.038093 | -0.0074348 | 0.021658 | -0.0083126 | -27.6031 | 64.1922 | -58.8455 | 64.4852 | -58.3603 | -58.8364 | -58.8409 | -30.3268 | 64.2151 | -58.7814 | 64.2654 | -58.3969 | -58.9417 | -58.7814 | -0.09613 | -0.073242 | 0.21973 | 0.3891 | -0.091552 | -0.086975 | 0.004578 | 0.009155 | -0.032043 | -0.050354 | 0 | 0.35248 | -0.032043 | -0.19226 | 0 | -0.16022 | 0.48523 | 123.3307 | 0.38452 | 123.0469 | 123.0377 | 122.9965 | 122.9416 | 122.9645 | -123.111 | -123.0469 | 123.2346 | 123.0148 | 31.1462 | 28.4225
491.9688 | 123.1293 | -58.7173 | 64.2609 | 0.098773 | 0.0034793 | 0.027333 | 0.087553 | -0.0024746 | -0.012723 | 0.0013532 | -0.015915 | 0.0098884 | 0.067927 | 0.039161 | -0.022388 | 0.013113 | 0.01305 | -27.6764 | 64.2014 | -58.7906 | 64.4806 | -58.4381 | -58.8776 | -58.873 | -30.0156 | 64.2197 | -58.7402 | 64.4394 | -58.5205 | -58.6899 | -58.6029 | -0.073242 | -0.059509 | 0.21973 | 0.27924 | -0.15564 | -0.16022 | -0.082398 | -0.086975 | -0.022888 | -0.041198 | 0.17853 | 0.19684 | 0.11444 | 0.027466 | 0.13733 | 0.050354 | 0.35248 | 123.2712 | 0.21973 | 123.1796 | 122.9919 | 122.9599 | 122.9187 | 122.937 | -123.0515 | -123.0011 | 123.1979 | 123.1567 | 31.041 | 28.7018
493.0469 | 123.143 | -58.7494 | 64.2654 | 0.0072204 | 0.01416 | 0.033741 | 0.066191 | -0.01102 | -0.0063137 | -0.010396 | -0.07695 | 0.0077514 | 0.080744 | 0.069068 | 0.0011102 | 0.018454 | 0.00023236 | -27.7817 | 64.1418 | -58.8455 | 64.5309 | -58.342 | -58.873 | -58.8409 | -29.9835 | 64.2014 | -58.7677 | 64.3158 | -58.3603 | -58.8501 | -58.7448 | -0.09613 | -0.1236 | 0.2655 | 0.40741 | -0.091552 | -0.1236 | 0.004578 | -0.027466 | -0.01831 | -0.064087 | 0.050354 | 0.3891 | 0.004578 | -0.10071 | 0.022888 | -0.082398 | 0.50354 | 123.3765 | 0.40741 | 123.0835 | 122.9874 | 122.9691 | 122.8912 | 122.9507 | -123.111 | -123.0331 | 123.2803 | 123.0652 | 30.9677 | 28.7659
493.9688 | 123.1796 | -58.699 | 64.2975 | 0.12929 | 0.0077523 | 0.029469 | 0.082213 | 0.0082064 | -0.029812 | -0.0029188 | -0.00065608 | 0.013092 | 0.066859 | 0.04557 | -0.018116 | 0.022726 | -0.00083564 | -27.6718 | 64.2059 | -58.7906 | 64.476 | -58.3832 | -58.8593 | -58.8364 | -29.8737 | 64.238 | -58.7585 | 64.4119 | -58.2962 | -58.7082 | -58.7036 | -0.091552 | -0.091552 | 0.17853 | 0.31586 | -0.13733 | -0.16022 | -0.045777 | -0.068665 | -0.059509 | -0.059509 | 0.11444 | 0.40283 | -0.004577 | -0.009155 | 0.054932 | 0.050354 | 0.40741 | 123.2666 | 0.46234 | 123.1705 | 122.9965 | 122.9965 | 122.905 | 122.937 | -123.0881 | -123.056 | 123.175 | 123.111 | 31.0272 | 28.8254
495.0312 | 123.2071 | -58.699 | 64.2517 | 0.052997 | 0.0066833 | 0.021992 | 0.091826 | 0.0060704 | 0.0097083 | -0.0029188 | 0.060379 | 0.0002754 | 0.088221 | 0.017799 | -0.02132 | 0.012045 | -0.02113 | -27.8458 | 64.1785 | -58.8181 | 64.5035 | -58.4244 | -58.8547 | -58.9005 | -29.8691 | 64.1876 | -58.7585 | 64.3707 | -58.2642 | -58.7585 | -58.6945 | -0.11902 | -0.073242 | 0.25177 | 0.27466 | -0.20142 | -0.15564 | -0.082398 | -0.036621 | -0.059509 | -0.064087 | 0.11902 | 0.43488 | 0.004578 | -0.059509 | 0.064087 | 0 | 0.39368 | 123.3215 | 0.49439 | 123.1293 | 122.9965 | 122.9462 | 122.8775 | 122.8867 | -123.0698 | -123.0103 | 123.2025 | 123.0698 | 30.8533 | 28.83
495.9531 | 123.1979 | -58.6578 | 64.3066 | 0.052997 | 0.0045473 | 0.028401 | 0.0726 | -0.013156 | 0.0065043 | -0.021077 | 0.36555 | 0.0066834 | 0.06045 | 0.061592 | -0.013843 | 0.0088412 | -0.0072446 | -28.0563 | 64.2059 | -58.7173 | 64.4211 | -58.3969 | -58.905 | -58.873 | -29.8096 | 64.2288 | -58.7036 | 64.5126 | -58.2413 | -58.6304 | -58.6349 | -0.059509 | -0.10071 | 0.11444 | 0.26093 | -0.21515 | -0.24719 | -0.15564 | -0.18768 | -0.045776 | -0.07782 | 0.20599 | 0.41656 | 0.022888 | 0.027466 | 0.068664 | 0.073242 | 0.32043 | 123.1384 | 0.46234 | 123.2162 | 122.9233 | 122.9324 | 122.8638 | 122.8867 | -123.024 | -123.0103 | 123.0789 | 123.1705 | 30.6015 | 28.8483
496.9531 | 123.1293 | -58.6578 | 64.3478 | 0.11403 | 0.013092 | 0.03481 | 0.086485 | 0.0039344 | -0.011654 | -0.0071918 | 0.15193 | 0.010956 | 0.071131 | 0.070137 | -0.0052988 | 0.014181 | 0.014118 | -28.1067 | 64.2014 | -58.7311 | 64.476 | -58.3374 | -58.7677 | -58.8455 | -29.9423 | 64.2654 | -58.6716 | 64.3753 | -58.1772 | -58.7769 | -58.667 | -0.073242 | -0.14648 | 0.12817 | 0.32044 | -0.18768 | -0.10986 | -0.11444 | -0.036621 | -0.013733 | -0.082397 | 0.027466 | 0.48065 | -0.009155 | -0.11902 | 0.004578 | -0.10528 | 0.39368 | 123.2071 | 0.49439 | 123.0469 | 122.9324 | 122.937 | 122.8592 | 122.9233 | -123.0789 | -123.0194 | 123.1338 | 123.0331 | 30.5511 | 28.7155
497.9688 | 123.2071 | -58.667 | 64.27 | 0.098773 | -0.0018617 | 0.025197 | 0.090757 | -0.018497 | -0.012723 | -0.0039868 | 0.47237 | 0.010956 | 0.0722 | 0.051979 | -0.0095708 | 0.017386 | -0.0040396 | -28.2944 | 64.1876 | -58.7402 | 64.4073 | -58.3374 | -58.8913 | -58.8318 | -30.0156 | 64.2242 | -58.6899 | 64.4119 | -58.2184 | -58.6304 | -58.6395 | -0.073242 | -0.082398 | 0.13733 | 0.32959 | -0.16479 | -0.2243 | -0.091553 | -0.15106 | -0.022888 | -0.045777 | 0.14191 | 0.44861 | 0.027466 | 0.036621 | 0.050354 | 0.059509 | 0.40283 | 123.1476 | 0.4715 | 123.1018 | 122.9279 | 122.9141 | 122.8546 | 122.8912 | -123.0103 | -122.9599 | 123.0743 | 123.0789 | 30.3726 | 28.6514
498.9531 | 123.2849 | -58.6349 | 64.3066 | -0.069074 | 0.00027529 | 0.024128 | 0.079008 | 0.0017974 | -0.0073817 | -0.022145 | 0.28926 | -0.0007936 | 0.07754 | 0.082954 | -0.023456 | 0.01525 | 0.0023694 | -28.0289 | 64.2105 | -58.7082 | 64.4302 | -58.4061 | -58.8593 | -58.9096 | -30.0934 | 64.2334 | -58.6945 | 64.4714 | -58.0627 | -58.5892 | -58.5571 | -0.073242 | -0.096131 | 0.1236 | 0.22888 | -0.27466 | -0.2243 | -0.20142 | -0.15106 | -0.059509 | -0.073243 | 0.16479 | 0.5722 | 0.07782 | 0.045777 | 0.13733 | 0.10529 | 0.30212 | 123.1384 | 0.63171 | 123.1659 | 122.9187 | 122.9279 | 122.8455 | 122.8683 | -123.0148 | -123.0011 | 123.0652 | 123.1064 | 30.6061 | 28.5416
499.9531 | 123.2529 | -58.6029 | 64.3707 | 0.35817 | 0.016296 | 0.021992 | 0.092894 | -0.00033857 | 0.01398 | 0.0034902 | 0.19771 | 0.0077514 | 0.090358 | 0.025276 | -0.02132 | 0.0099092 | -0.0029716 | -28.1067 | 64.2197 | -58.7219 | 64.3707 | -58.3786 | -58.9233 | -58.8638 | -30.1941 | 64.238 | -58.6578 | 64.5309 | -58.0673 | -58.5754 | -58.5617 | -0.11902 | -0.15106 | 0 | 0.2243 | -0.26093 | -0.32044 | -0.14191 | -0.20142 | -0.054932 | -0.13275 | 0.16022 | 0.53558 | 0.041198 | 0.027466 | 0.09613 | 0.082398 | 0.34332 | 123.0927 | 0.59052 | 123.1888 | 122.9416 | 122.8958 | 122.8226 | 122.8409 | -123.0927 | -123.0286 | 122.9736 | 123.1338 | 30.4962 | 28.4088
500.9531 | 123.2666 | -58.6075 | 64.3387 | 0.14455 | 0.0077523 | 0.027333 | 0.081144 | 0.01141 | -0.02554 | 0.0013532 | 0.28926 | 0.0088204 | 0.059382 | 0.047706 | -0.017048 | 0.0099092 | -0.0072446 | -27.7313 | 64.2654 | -58.6533 | 64.4531 | -58.3969 | -58.8455 | -58.9508 | -30.2719 | 64.2654 | -58.667 | 64.4989 | -58.0399 | -58.5709 | -58.5388 | -0.045776 | -0.073242 | 0.11444 | 0.21057 | -0.34332 | -0.23804 | -0.29755 | -0.19226 | -0.059509 | -0.073242 | 0.16022 | 0.56763 | 0.068665 | 0.036621 | 0.12817 | 0.09613 | 0.25635 | 123.1064 | 0.62714 | 123.1659 | 122.9187 | 122.9324 | 122.8729 | 122.8729 | -122.9919 | -123.0057 | 123.0606 | 123.1064 | 30.8762 | 28.3356
502.0312 | 123.2758 | -58.6166 | 64.3066 | 0.17507 | 0.0045473 | 0.025197 | 0.092894 | 0.0082064 | -0.0063137 | -0.00078276 | 0.04512 | 0.016296 | 0.068995 | 0.063728 | -0.02132 | 0.017386 | -0.0061756 | -28.006 | 64.2059 | -58.7448 | 64.4394 | -58.3694 | -58.8593 | -58.9325 | -30.5511 | 64.2563 | -58.6624 | 64.4897 | -58.0215 | -58.6716 | -58.5251 | -0.12817 | -0.10071 | 0.13275 | 0.24719 | -0.31586 | -0.24262 | -0.18768 | -0.11444 | -0.045777 | -0.050354 | 0.1831 | 0.59509 | 0.091553 | -0.054932 | 0.13733 | -0.009155 | 0.37537 | 123.1842 | 0.64087 | 123.1522 | 122.9507 | 122.9187 | 122.8226 | 122.8729 | -123.0515 | -122.9691 | 123.056 | 123.1064 | 30.6107 | 28.0655
502.9688 | 123.1659 | -58.6166 | 64.4073 | 0.14455 | 0.0077523 | 0.019856 | 0.091826 | 0.0071384 | -0.012723 | -0.010396 | -0.13799 | 0.020569 | 0.067927 | 0.06266 | -0.010639 | 0.02059 | -0.0029716 | -27.8549 | 64.2883 | -58.7128 | 64.5767 | -58.2825 | -58.7769 | -58.7677 | -30.7343 | 64.3204 | -58.667 | 64.4943 | -58.0811 | -58.6258 | -58.5938 | -0.096131 | -0.11902 | 0.16937 | 0.33417 | -0.15106 | -0.16022 | -0.054931 | -0.064086 | -0.050354 | -0.086975 | 0.086975 | 0.53558 | 0.022888 | -0.009155 | 0.073242 | 0.041199 | 0.4303 | 123.2895 | 0.58594 | 123.1613 | 123.0011 | 122.9874 | 122.905 | 122.937 | -123.1201 | -123.0743 | 123.1934 | 123.111 | 30.7617 | 27.8824
503.9531 | 123.2574 | -58.58 | 64.3341 | 0.052997 | 0.0013433 | 0.020924 | 0.083281 | -0.0078156 | -0.012723 | -0.0018508 | 0.274 | -0.0029296 | 0.089289 | 0.015663 | -0.02132 | 0.0077732 | 0.0087774 | -28.0243 | 64.2517 | -58.699 | 64.4348 | -58.2916 | -58.8501 | -58.8272 | -30.8853 | 64.2929 | -58.6395 | 64.5447 | -57.9529 | -58.548 | -58.461 | -0.11902 | -0.082397 | 0.10071 | 0.28839 | -0.24719 | -0.27008 | -0.12817 | -0.15106 | -0.059509 | -0.041198 | 0.21057 | 0.62714 | 0.11902 | 0.032043 | 0.17853 | 0.091552 | 0.40741 | 123.1338 | 0.68664 | 123.1842 | 122.9507 | 122.9324 | 122.8317 | 122.8729 | -123.0331 | -122.9736 | 123.0148 | 123.1247 | 30.5557 | 27.6947
504.9531 | 123.143 | -58.5709 | 64.389 | 0.12929 | 0.018433 | 0.025197 | 0.076872 | -0.00033857 | -0.016995 | -0.0093278 | 0.13667 | 0.0056154 | 0.058314 | 0.08509 | -0.013843 | 0.0056372 | -0.0029716 | -28.0243 | 64.2654 | -58.6533 | 64.5264 | -58.255 | -58.754 | -58.7814 | -31.0822 | 64.3295 | -58.6212 | 64.5172 | -58.0032 | -58.5617 | -58.5617 | -0.082397 | -0.1236 | 0.13733 | 0.31586 | -0.21057 | -0.18311 | -0.12817 | -0.10071 | -0.050354 | -0.059509 | 0.12817 | 0.56763 | 0.009155 | 0.009155 | 0.059509 | 0.059509 | 0.39825 | 123.1796 | 0.61798 | 123.1384 | 122.9187 | 122.9507 | 122.8363 | 122.9004 | -123.0423 | -123.0103 | 123.0972 | 123.0881 | 30.5466 | 27.4887
505.9531 | 123.1659 | -58.5892 | 64.4073 | 0.14455 | 0.013092 | 0.030537 | 0.085417 | -0.0014066 | 0.0075723 | 0.0034902 | 0.19771 | 0.0088204 | 0.071131 | 0.065864 | -0.01598 | 0.0099092 | -0.013653 | -27.7588 | 64.2838 | -58.6487 | 64.4714 | -58.2642 | -58.7677 | -58.7906 | -31.3156 | 64.3295 | -58.5938 | 64.5035 | -57.9483 | -58.5709 | -58.5022 | -0.05951 | -0.1236 | 0.064087 | 0.32501 | -0.20142 | -0.17853 | -0.14191 | -0.11902 | -0.004578 | -0.07782 | 0.09613 | 0.64087 | 0.086975 | 0.01831 | 0.091553 | 0.022888 | 0.38452 | 123.1201 | 0.64545 | 123.0972 | 122.9324 | 122.9233 | 122.8729 | 122.9187 | -123.056 | -123.0011 | 123.0606 | 123.0927 | 30.8304 | 27.2736
506.9531 | 123.23 | -58.5571 | 64.389 | 0.12929 | 0.0098883 | 0.020924 | 0.089689 | 0.0028664 | -0.0041777 | -0.015736 | 0.19771 | 0.0056154 | 0.068995 | 0.042366 | -0.0010258 | 0.010977 | -0.013653 | -27.7496 | 64.2838 | -58.6395 | 64.5218 | -58.2504 | -58.7952 | -58.7906 | -31.4529 | 64.3158 | -58.6166 | 64.6225 | -57.9712 | -58.4702 | -58.5068 | -0.082397 | -0.10529 | 0.13275 | 0.3067 | -0.23346 | -0.23804 | -0.15106 | -0.15564 | -0.059509 | -0.073242 | 0.23346 | 0.58594 | 0.050354 | 0.086975 | 0.10986 | 0.14648 | 0.3891 | 123.1613 | 0.64545 | 123.2391 | 122.9233 | 122.9324 | 122.8409 | 122.8729 | -123.0286 | -123.0057 | 123.0789 | 123.1796 | 30.8075 | 27.1042
507.9688 | 123.2071 | -58.5571 | 64.4348 | 0.20559 | 0.0034793 | 0.020924 | 0.099302 | -0.00033857 | -0.0073817 | -0.010396 | -0.12273 | 0.010956 | 0.068995 | 0.10645 | -0.012775 | 0.025931 | -0.0093806 | -27.507 | 64.3295 | -58.6716 | 64.5859 | -58.223 | -58.7128 | -58.7219 | -31.8008 | 64.3707 | -58.6029 | 64.5264 | -57.9163 | -58.58 | -58.5159 | -0.11444 | -0.10529 | 0.15106 | 0.33417 | -0.16479 | -0.15564 | -0.050354 | -0.041199 | -0.045776 | -0.064086 | 0.091553 | 0.64087 | 0.041199 | -0.022888 | 0.086975 | 0.022888 | 0.44861 | 123.2574 | 0.68664 | 123.1293 | 123.0011 | 122.9736 | 122.8867 | 122.9279 | -123.1064 | -123.0377 | 123.143 | 123.0835 | 31.0501 | 26.7563
508.9531 | 123.2574 | -58.5205 | 64.4165 | 0.19033 | 0.0024113 | 0.01772 | 0.090757 | 0.0050024 | -0.0063137 | -0.0050548 | 0.24348 | 0.010956 | 0.064723 | 0.037025 | -0.0063668 | 0.0077732 | 0.0045054 | -27.5024 | 64.3021 | -58.5938 | 64.5035 | -58.255 | -58.8043 | -58.7219 | -31.9656 | 64.3341 | -58.58 | 64.6088 | -57.8659 | -58.4061 | -58.4427 | -0.073242 | -0.11444 | 0.086975 | 0.2655 | -0.20142 | -0.28381 | -0.12817 | -0.21057 | -0.059509 | -0.082398 | 0.19226 | 0.6546 | 0.07782 | 0.11444 | 0.13733 | 0.17395 | 0.33875 | 123.0972 | 0.71411 | 123.1888 | 122.8958 | 122.9141 | 122.8226 | 122.8546 | -123.0103 | -122.9965 | 123.024 | 123.1293 | 31.0181 | 26.5549
509.9531 | 123.1613 | -58.5663 | 64.4669 | 0.0072204 | 0.0024113 | 0.01772 | 0.086485 | 0.0092744 | -0.0041777 | -0.0071918 | 0.090897 | 0.0077514 | 0.071131 | 0.075477 | -0.013843 | 0.0013642 | -0.026471 | -27.2781 | 64.3433 | -58.6166 | 64.5813 | -58.1909 | -58.6945 | -58.7494 | -32.341 | 64.389 | -58.5892 | 64.5126 | -57.8751 | -58.5205 | -58.4702 | -0.050354 | -0.1236 | 0.11444 | 0.37537 | -0.18311 | -0.12817 | -0.13275 | -0.07782 | -0.022888 | -0.07782 | 0.045776 | 0.69122 | 0.09613 | 0.045776 | 0.11902 | 0.068664 | 0.42572 | 123.1979 | 0.71411 | 123.1018 | 122.9599 | 122.9782 | 122.9095 | 122.9553 | -123.0835 | -123.056 | 123.1476 | 123.0789 | 31.2881 | 26.2253
511.0312 | 123.2162 | -58.5388 | 64.4211 | 0.11403 | 0.0034793 | 0.027333 | 0.091826 | 0.00072943 | -0.011654 | -0.0050548 | -0.00065608 | 0.018433 | 0.059382 | 0.044502 | -0.0085028 | 0.01525 | -0.020062 | -27.1729 | 64.3021 | -58.6807 | 64.5355 | -58.1406 | -58.699 | -58.7128 | -32.8033 | 64.357 | -58.6121 | 64.5493 | -57.8796 | -58.5526 | -58.4427 | -0.14191 | -0.11902 | 0.11444 | 0.39825 | -0.17395 | -0.16022 | -0.032044 | -0.018311 | -0.073243 | -0.064087 | 0.12817 | 0.65918 | 0.09613 | -0.013733 | 0.16937 | 0.05951 | 0.54016 | 123.2162 | 0.73242 | 123.1613 | 122.9828 | 122.9691 | 122.8409 | 122.8958 | -123.1018 | -123.0331 | 123.0743 | 123.0881 | 31.366 | 25.7355
511.9688 | 123.2025 | -58.493 | 64.4348 | 0.15981 | 0.0045473 | 0.011311 | 0.075804 | 0.014615 | -0.028744 | -0.00078276 | 0.16719 | 0.0013434 | 0.057246 | 0.077613 | -0.0085028 | 0.0013642 | -0.017926 | -27.0813 | 64.3204 | -58.548 | 64.5172 | -58.2596 | -58.7585 | -58.8135 | -32.8629 | 64.357 | -58.5251 | 64.7415 | -58.0261 | -58.3511 | -58.3694 | -0.054932 | -0.11444 | 0.082398 | 0.23346 | -0.32043 | -0.2655 | -0.2655 | -0.21057 | -0.032043 | -0.077819 | 0.3067 | 0.46692 | 0.1236 | 0.14191 | 0.15564 | 0.17395 | 0.28839 | 123.0652 | 0.49896 | 123.2666 | 122.8683 | 122.8821 | 122.8134 | 122.85 | -122.9828 | -122.9599 | 123.0103 | 123.2346 | 31.4117 | 25.6302
513.0469 | 123.1155 | -58.493 | 64.4989 | 0.068255 | 0.0024113 | 0.01772 | 0.097166 | 0.012479 | -0.015927 | -0.0029188 | -0.1685 | 0.016296 | 0.068995 | 0.049842 | -0.0095708 | 0.02059 | 0.0034374 | -27.15 | 64.3982 | -58.6166 | 64.6774 | -58.0582 | -58.58 | -58.6807 | -33.371 | 64.4531 | -58.5022 | 64.5721 | -57.8156 | -58.5846 | -58.429 | -0.1236 | -0.10071 | 0.17853 | 0.43488 | -0.18768 | -0.086975 | -0.064087 | 0.036621 | -0.009155 | -0.045776 | 0.073243 | 0.67749 | 0.064087 | -0.091553 | 0.073242 | -0.082398 | 0.55847 | 123.2941 | 0.68665 | 123.0743 | 123.0148 | 122.9553 | 122.8912 | 122.9462 | -123.1155 | -123.0011 | 123.1705 | 123.0652 | 31.3431 | 25.1221
513.9531 | 123.2803 | -58.4106 | 64.4943 | 0.037738 | 0.0034793 | 0.020924 | 0.087553 | -0.00033857 | 0.0086403 | -0.0136 | 0.12141 | 0.015228 | 0.07754 | 0.015663 | -0.0085028 | 0.018454 | -0.024334 | -26.9852 | 64.3936 | -58.5159 | 64.6179 | -58.1497 | -58.6533 | -58.7448 | -33.4488 | 64.4119 | -58.4747 | 64.7095 | -57.637 | -58.2642 | -58.342 | -0.10528 | -0.10071 | 0.1236 | 0.26093 | -0.33417 | -0.24261 | -0.22888 | -0.13733 | -0.064086 | -0.082398 | 0.21515 | 0.77362 | 0.068665 | 0.14649 | 0.13275 | 0.21057 | 0.36621 | 123.1338 | 0.83771 | 123.1842 | 122.9095 | 122.8867 | 122.8043 | 122.8226 | -123.0103 | -122.9691 | 123.0286 | 123.1201 | 31.4255 | 24.9619
514.9531 | 123.2254 | -58.4335 | 64.5447 | -0.038556 | 0.0066833 | 0.018788 | 0.080076 | -0.0046106 | -0.010586 | -0.0071918 | 0.28926 | 0.0077514 | 0.074336 | 0.069068 | -0.0052988 | 0.02059 | -0.0093806 | -27.0218 | 64.4211 | -58.5022 | 64.5905 | -58.0627 | -58.6487 | -58.6349 | -33.8058 | 64.4485 | -58.4839 | 64.6866 | -57.6828 | -58.374 | -58.2504 | -0.068664 | -0.1236 | 0.045776 | 0.37079 | -0.20142 | -0.21515 | -0.13275 | -0.14648 | -0.050354 | -0.096131 | 0.14191 | 0.75073 | 0.18311 | 0.05951 | 0.23346 | 0.10986 | 0.43945 | 123.0927 | 0.80109 | 123.1705 | 122.9233 | 122.9324 | 122.8546 | 122.8821 | -123.0469 | -123.0286 | 123.024 | 123.1201 | 31.4117 | 24.6277
515.9531 | 123.1338 | -58.429 | 64.5813 | 0.037738 | 0.013092 | 0.012379 | 0.085417 | -0.0024746 | 0.0011633 | 0.0066942 | 0.19771 | 0.010956 | 0.054042 | 0.053047 | -0.020252 | 0.02059 | -0.00083564 | -27.2278 | 64.4714 | -58.5022 | 64.7095 | -57.9895 | -58.5571 | -58.5434 | -34.2133 | 64.4897 | -58.4747 | 64.6545 | -57.7606 | -58.3923 | -58.3969 | -0.073242 | -0.10986 | 0.12817 | 0.43945 | -0.11444 | -0.12817 | -0.041199 | -0.054932 | -0.045776 | -0.091553 | 0.073242 | 0.66833 | 0.032043 | 0.036621 | 0.077819 | 0.082397 | 0.5127 | 123.2117 | 0.71411 | 123.1293 | 122.9736 | 122.9645 | 122.9004 | 122.9187 | -123.0835 | -123.056 | 123.1384 | 123.0835 | 31.2012 | 24.2157
517.0312 | 123.1293 | -58.4427 | 64.5905 | 0.068255 | 0.00027529 | 0.01772 | 0.098234 | 0.024228 | 0.0054353 | -0.0029188 | -0.07695 | 0.0056154 | 0.071131 | 0.074409 | -0.0052988 | 0.013113 | -0.0093806 | -27.2141 | 64.4623 | -58.5297 | 64.7873 | -57.9941 | -58.5022 | -58.5617 | -34.6802 | 64.5401 | -58.4747 | 64.5905 | -57.756 | -58.4793 | -58.3923 | -0.086975 | -0.12817 | 0.19684 | 0.44861 | -0.11902 | -0.059509 | -0.032044 | 0.027466 | -0.032043 | -0.050354 | 0 | 0.68665 | 0.050354 | -0.036621 | 0.082397 | -0.004578 | 0.53558 | 123.317 | 0.71869 | 123.0652 | 122.9919 | 123.0148 | 122.905 | 122.9828 | -123.1201 | -123.0652 | 123.23 | 123.0331 | 31.2286 | 23.7625
517.9688 | 123.1567 | -58.3649 | 64.5905 | 0.20559 | 0.0024113 | 0.011311 | 0.093962 | 0.014615 | -0.031949 | 0.0066942 | 0.075638 | 0.017364 | 0.073268 | 0.080818 | -0.019184 | 0.018454 | -0.025402 | -27.3193 | 64.5172 | -58.4747 | 64.7552 | -57.9025 | -58.5388 | -58.5114 | -34.8816 | 64.5538 | -58.4335 | 64.7369 | -57.6691 | -58.3282 | -58.3282 | -0.10986 | -0.073242 | 0.1648 | 0.46234 | -0.14648 | -0.17395 | -0.036622 | -0.064087 | -0.068665 | -0.036621 | 0.14648 | 0.6958 | 0.036621 | 0.036621 | 0.10529 | 0.10529 | 0.5722 | 123.23 | 0.76447 | 123.1705 | 122.9919 | 122.9874 | 122.8821 | 122.9187 | -123.0652 | -123.024 | 123.1201 | 123.1018 | 31.0455 | 23.4833
519.0312 | 123.1979 | -58.3511 | 64.6362 | 0.068255 | 0.016296 | 0.016652 | 0.086485 | 0.017819 | -0.012723 | -0.011464 | -0.1685 | 0.016296 | 0.076472 | 0.038093 | 4.2208e-05 | 0.036612 | -0.014721 | -27.5436 | 64.4989 | -58.5068 | 64.8331 | -57.8522 | -58.4061 | -58.4793 | -35.3668 | 64.563 | -58.4335 | 64.595 | -57.4402 | -58.4244 | -58.3694 | -0.15564 | -0.13733 | 0.19684 | 0.49896 | -0.12817 | -0.054932 | 0.027466 | 0.10071 | -0.082398 | -0.073242 | -0.041198 | 0.91095 | -0.018311 | -0.073242 | 0.064087 | 0.009156 | 0.6546 | 123.3398 | 0.99335 | 123.0286 | 123.0057 | 122.9965 | 122.85 | 122.9141 | -123.143 | -123.0698 | 123.1842 | 122.9462 | 30.8075 | 22.9843
519.9688 | 123.1384 | -58.3557 | 64.6362 | 0.11403 | 0.017365 | 0.01772 | 0.097166 | -0.013156 | -0.0052457 | -0.0061228 | -0.10747 | 0.0077514 | 0.073268 | 0.060523 | -0.0063668 | 0.019522 | 0.0045054 | -27.6855 | 64.5447 | -58.4564 | 64.769 | -57.8064 | -58.493 | -58.4564 | -35.495 | 64.5813 | -58.3878 | 64.7781 | -57.6599 | -58.3374 | -58.2916 | -0.10071 | -0.091552 | 0.13275 | 0.54932 | -0.10071 | -0.13733 | 0 | -0.036621 | -0.032043 | -0.054931 | 0.14191 | 0.6958 | 0.064087 | 0.018311 | 0.09613 | 0.050354 | 0.65002 | 123.2254 | 0.72784 | 123.1659 | 123.0011 | 122.9691 | 122.9004 | 122.937 | -123.0927 | -123.024 | 123.1247 | 123.1338 | 30.6702 | 22.8607
520.9531 | 123.262 | -58.2916 | 64.6591 | 0.0072204 | 0.0034793 | 0.0070391 | 0.081144 | 0.0082064 | -0.0084497 | -0.025349 | 0.30452 | -0.0050656 | 0.066859 | 0.015663 | 4.2208e-05 | 0.016318 | 0.022663 | -27.9236 | 64.5401 | -58.3878 | 64.7552 | -57.8979 | -58.5205 | -58.5526 | -35.7101 | 64.5584 | -58.3328 | 64.8056 | -57.4585 | -58.1726 | -58.1085 | -0.09613 | -0.11902 | 0.09613 | 0.39368 | -0.26093 | -0.22888 | -0.16479 | -0.13275 | -0.041199 | -0.10071 | 0.14648 | 0.83313 | 0.1831 | 0.11902 | 0.2243 | 0.16022 | 0.48981 | 123.143 | 0.87433 | 123.1384 | 122.9279 | 122.8912 | 122.8317 | 122.85 | -123.0469 | -122.9919 | 123.0469 | 123.0972 | 30.368 | 22.5815
521.9531 | 123.2162 | -58.2504 | 64.6957 | -0.43528 | 0.013092 | 0.0038341 | 0.088621 | 0.0050024 | -0.016995 | 0.010966 | 0.16719 | 0.0066834 | 0.074336 | 0.051979 | -0.019184 | 0.023794 | 0.015186 | -28.0334 | 64.5493 | -58.3923 | 64.7415 | -57.8522 | -58.5342 | -58.5022 | -35.8795 | 64.6042 | -58.3282 | 64.888 | -57.4265 | -58.1039 | -58.0902 | -0.14191 | -0.14648 | 0.045776 | 0.39825 | -0.25177 | -0.28381 | -0.10986 | -0.14191 | -0.07782 | -0.091553 | 0.19226 | 0.82397 | 0.16022 | 0.14648 | 0.23804 | 0.2243 | 0.54016 | 123.1338 | 0.90179 | 123.2162 | 122.9416 | 122.9324 | 122.7997 | 122.8546 | -123.0881 | -123.024 | 122.9919 | 123.1384 | 30.217 | 22.3709
523.0469 | 123.1201 | -58.2779 | 64.7049 | 0.0072204 | -0.0072017 | 0.010243 | 0.092894 | -0.0014066 | -0.0031087 | 0.0013532 | -0.13799 | 0.0098884 | 0.073268 | 0.049842 | -0.0095708 | 0.029135 | -0.0051076 | -28.2028 | 64.5996 | -58.3832 | 64.8972 | -57.7377 | -58.4198 | -58.3832 | -36.2183 | 64.6591 | -58.3328 | 64.8239 | -57.5958 | -58.2413 | -58.2001 | -0.10529 | -0.10529 | 0.19226 | 0.54016 | -0.10529 | -0.14191 | 0 | -0.036621 | -0.054932 | -0.045776 | 0.11902 | 0.68207 | 0.07782 | 0.036621 | 0.13275 | 0.091553 | 0.64545 | 123.2803 | 0.737 | 123.1567 | 122.9828 | 122.9919 | 122.8775 | 122.937 | -123.0881 | -123.0377 | 123.175 | 123.1018 | 30.0751 | 22.0596
523.9531 | 123.2666 | -58.1909 | 64.6683 | 0.037738 | 0.0024113 | 0.0016981 | 0.082213 | -0.0046106 | -0.039425 | 0.00028524 | 0.21297 | 0.012024 | 0.057246 | 0.043434 | -0.012775 | 0.010977 | 0.0066414 | -28.4225 | 64.6088 | -58.3374 | 64.7644 | -57.7698 | -58.5251 | -58.4702 | -36.2 | 64.6408 | -58.2916 | 64.9658 | -57.3761 | -58.0765 | -58.0536 | -0.14648 | -0.059509 | 0.09613 | 0.42114 | -0.27924 | -0.33417 | -0.13275 | -0.18768 | -0.10071 | -0.027466 | 0.29755 | 0.81482 | 0.13733 | 0.11444 | 0.23804 | 0.21515 | 0.56763 | 123.1018 | 0.91553 | 123.2574 | 122.9462 | 122.9324 | 122.7997 | 122.8317 | -123.0057 | -122.9599 | 122.9553 | 123.1567 | 29.7684 | 21.991
525.0312 | 123.262 | -58.2047 | 64.6957 | 0.0072204 | 0.0098883 | 0.018788 | 0.10037 | 0.012479 | -0.0052457 | 0.0034902 | -0.031174 | 0.0088204 | 0.081813 | 0.064796 | -0.027729 | 0.018454 | -0.014721 | -28.6423 | 64.5996 | -58.3374 | 64.8148 | -57.7469 | -58.461 | -58.3878 | -36.3785 | 64.6271 | -58.287 | 64.9155 | -57.4081 | -58.0765 | -58.1085 | -0.13275 | -0.096131 | 0.11902 | 0.45776 | -0.18311 | -0.25635 | -0.050354 | -0.1236 | -0.082397 | -0.068665 | 0.21973 | 0.79651 | 0.09613 | 0.12817 | 0.17853 | 0.21057 | 0.59051 | 123.1522 | 0.87891 | 123.2025 | 122.937 | 122.9141 | 122.8043 | 122.8317 | -123.0331 | -122.9828 | 123.0194 | 123.1201 | 29.5624 | 21.8262
525.9688 | 123.1659 | -58.2092 | 64.8102 | 0.17507 | 0.00027529 | 0.0016981 | 0.085417 | -0.015292 | -0.010586 | -0.0061228 | 0.075638 | 0.010956 | 0.079676 | 0.053047 | -0.018116 | 0.030203 | 0.00023236 | -28.8437 | 64.6729 | -58.3008 | 64.9521 | -57.5363 | -58.3054 | -58.2779 | -36.6119 | 64.7415 | -58.2413 | 64.8605 | -57.3761 | -58.1726 | -58.0673 | -0.091552 | -0.13733 | 0.14191 | 0.67291 | -0.068664 | -0.09613 | 0.022888 | -0.004578 | -0.032043 | -0.068665 | 0.050354 | 0.83313 | 0.14191 | 0.036622 | 0.17395 | 0.068665 | 0.76447 | 123.2529 | 0.86517 | 123.1018 | 122.9736 | 122.9828 | 122.8821 | 122.9507 | -123.111 | -123.0515 | 123.1613 | 123.0698 | 29.3655 | 21.5973
527.0312 | 123.2117 | -58.1589 | 64.769 | -0.11485 | 0.013092 | 0.016652 | 0.083281 | 0.0050024 | 9.5287e-05 | -0.021077 | 0.12141 | 0.0088204 | 0.061518 | 0.065864 | -0.0074348 | 0.019522 | -0.0051076 | -28.8757 | 64.6729 | -58.2825 | 64.8972 | -57.5867 | -58.3282 | -58.3237 | -36.5524 | 64.7415 | -58.2367 | 64.9704 | -57.3257 | -58.0673 | -58.0215 | -0.1236 | -0.09613 | 0.12817 | 0.57221 | -0.16479 | -0.16937 | -0.041198 | -0.045776 | -0.077819 | -0.027466 | 0.20142 | 0.83313 | 0.13733 | 0.091553 | 0.21515 | 0.16937 | 0.6958 | 123.1796 | 0.91095 | 123.2071 | 122.9553 | 122.9782 | 122.8317 | 122.9004 | -123.0515 | -123.0057 | 123.056 | 123.1293 | 29.2831 | 21.6064
527.9688 | 123.1384 | -58.1314 | 64.8651 | 0.0072204 | 0.013092 | 0.0070391 | 0.10678 | 0.0039344 | -0.0031087 | -0.0050548 | -0.13799 | 0.013092 | 0.076472 | 0.065864 | -0.0042298 | 0.033408 | -0.0061756 | -28.7109 | 64.7461 | -58.2138 | 65.0253 | -57.5409 | -58.223 | -58.2916 | -36.5662 | 64.8056 | -58.1818 | 64.9338 | -57.2754 | -58.136 | -57.9666 | -0.082397 | -0.11902 | 0.16022 | 0.59051 | -0.16022 | -0.091552 | -0.07782 | -0.009155 | -0.050354 | -0.059509 | 0.068665 | 0.85602 | 0.16479 | -0.004577 | 0.21515 | 0.045777 | 0.67291 | 123.2391 | 0.90637 | 123.1155 | 122.9599 | 122.9874 | 122.8775 | 122.937 | -123.0789 | -123.0469 | 123.1567 | 123.0652 | 29.4205 | 21.5652
529.0312 | 123.2712 | -58.0856 | 64.7873 | -0.023297 | 0.0098883 | 0.0016981 | 0.089689 | -0.0067466 | -0.014859 | -0.0082598 | 0.075638 | 0.0045474 | 0.067927 | 0.048774 | -0.0085028 | 0.01525 | -0.029675 | -29.1412 | 64.7415 | -58.1589 | 64.92 | -57.5317 | -58.3511 | -58.3008 | -36.2366 | 64.7644 | -58.136 | 65.0757 | -57.1838 | -57.9895 | -57.8705 | -0.073243 | -0.045776 | 0.13275 | 0.55389 | -0.21515 | -0.2655 | -0.14191 | -0.19226 | -0.050354 | -0.022888 | 0.28839 | 0.90179 | 0.21515 | 0.09613 | 0.2655 | 0.14648 | 0.62714 | 123.0789 | 0.95215 | 123.2117 | 122.9004 | 122.9004 | 122.8271 | 122.85 | -122.9462 | -122.9233 | 123.0057 | 123.1613 | 28.9444 | 21.8491
529.9531 | 123.1247 | -58.0719 | 64.975 | 0.083514 | -0.00079271 | 0.0016981 | 0.085417 | 0.012479 | -0.0095177 | -0.0050548 | 0.28926 | 0.0013434 | 0.071131 | 0.060523 | -0.0085028 | 0.014181 | -0.00083564 | -29.2511 | 64.8468 | -58.1177 | 65.1031 | -57.4219 | -58.0856 | -58.1589 | -35.9436 | 64.8972 | -58.0948 | 65.0116 | -57.1152 | -58.0032 | -57.9117 | -0.045777 | -0.12817 | 0.12817 | 0.65002 | -0.086976 | -0.013733 | -0.041199 | 0.032044 | -0.022889 | -0.07782 | 0.036621 | 0.95673 | 0.16022 | 0.068664 | 0.18311 | 0.091553 | 0.6958 | 123.2208 | 0.97962 | 123.1064 | 122.9645 | 122.9919 | 122.9187 | 122.9691 | -123.0927 | -123.0698 | 123.175 | 123.0835 | 28.8208 | 22.1283
531.0312 | 123.1613 | -58.0765 | 64.9109 | 0.052997 | -0.00079271 | 0.0091751 | 0.10144 | 0.0017974 | -0.0041777 | -0.0136 | -0.1685 | 0.017364 | 0.076472 | 0.042366 | -0.011707 | 0.02059 | -0.00083564 | -29.361 | 64.8239 | -58.1635 | 65.0894 | -57.3578 | -58.1451 | -58.1223 | -35.8933 | 64.8605 | -58.1085 | 65.0436 | -57.1426 | -58.0078 | -57.8751 | -0.086975 | -0.086975 | 0.17853 | 0.71869 | -0.045776 | -0.068665 | 0.041199 | 0.01831 | -0.032044 | -0.050354 | 0.13275 | 0.93384 | 0.20142 | 0.068665 | 0.23346 | 0.10071 | 0.80566 | 123.2529 | 0.96588 | 123.1522 | 122.9874 | 122.9691 | 122.9004 | 122.937 | -123.0743 | -123.0194 | 123.1659 | 123.1201 | 28.7155 | 22.1832
531.9531 | 123.2986 | -57.9849 | 64.9567 | 0.20559 | -0.0072017 | 0.0059701 | 0.086485 | 0.031705 | -0.0063137 | 0.0024222 | 0.274 | 0.0024114 | 0.074336 | 0.015663 | -0.02132 | 0.031271 | -0.012585 | -29.2969 | 64.8468 | -58.0444 | 65.0208 | -57.4768 | -58.168 | -58.2504 | -35.5087 | 64.8926 | -58.0078 | 64.9246 | -56.8542 | -57.8979 | -57.8018 | -0.05951 | -0.10986 | 0.064087 | 0.50812 | -0.2655 | -0.18311 | -0.20599 | -0.1236 | -0.022888 | -0.064087 | -0.032043 | 1.1307 | 0.1831 | 0.086975 | 0.20599 | 0.10986 | 0.56763 | 123.0652 | 1.1536 | 122.9324 | 122.8912 | 122.9004 | 122.8317 | 122.8775 | -123.0011 | -122.9645 | 123.0057 | 122.9095 | 28.688 | 22.4762
532.9531 | 123.1476 | -57.9346 | 65.0711 | 0.037738 | 0.0024113 | 0.0070391 | 0.084349 | 0.0092744 | -0.036221 | -0.0082598 | 0.090897 | 0.0024114 | 0.075404 | 0.037025 | -0.019184 | 0.02059 | 0.0013004 | -29.361 | 64.9429 | -58.0124 | 65.1031 | -57.2937 | -58.0948 | -58.0719 | -35.3851 | 64.9567 | -57.9849 | 65.1535 | -56.9183 | -57.8247 | -57.7881 | -0.07782 | -0.12817 | 0.032043 | 0.64087 | -0.13733 | -0.16022 | -0.059509 | -0.082398 | -0.050354 | -0.11444 | 0.082397 | 1.0162 | 0.14648 | 0.10986 | 0.19684 | 0.16022 | 0.71869 | 123.1155 | 1.0666 | 123.1384 | 122.9553 | 122.9416 | 122.8775 | 122.8912 | -123.0835 | -123.056 | 123.0377 | 123.0881 | 28.5736 | 22.5494
533.9531 | 123.2483 | -57.9025 | 65.0803 | 0.083514 | 0.012024 | -0.018596 | 0.084349 | 0.0050024 | 0.0097083 | -0.0061228 | 0.10615 | 0.0056154 | 0.071131 | 0.059455 | -0.0085028 | 0.023794 | 0.01305 | -29.1138 | 65.0024 | -57.9529 | 65.2039 | -57.3303 | -58.1268 | -58.1451 | -35.1654 | 64.9658 | -57.9254 | 65.2084 | -56.7719 | -57.7011 | -57.6782 | -0.050354 | -0.07782 | 0.1236 | 0.5722 | -0.24262 | -0.2243 | -0.19226 | -0.17395 | -0.022888 | -0.11444 | 0.12817 | 1.1307 | 0.2243 | 0.20142 | 0.24719 | 0.2243 | 0.62256 | 123.1567 | 1.1536 | 123.1338 | 122.9553 | 122.8912 | 122.905 | 122.8683 | -123.0331 | -123.0057 | 123.1064 | 123.111 | 28.7888 | 22.7371
535.0312 | 123.2574 | -57.843 | 65.1077 | 0.022479 | -0.0029297 | 0.0016981 | 0.092894 | 0.0028664 | -0.021267 | -0.0039868 | -0.015915 | 0.01416 | 0.074336 | 0.034889 | -0.014912 | 0.014181 | -0.0061756 | -29.6951 | 64.975 | -57.9483 | 65.213 | -57.2342 | -57.9849 | -58.0719 | -35.083 | 65.0162 | -57.9117 | 65.2634 | -56.6895 | -57.756 | -57.5867 | -0.10529 | -0.13275 | 0.10529 | 0.60883 | -0.22888 | -0.14191 | -0.1236 | -0.036621 | -0.068664 | -0.091553 | 0.15564 | 1.1536 | 0.25635 | 0.086976 | 0.32501 | 0.15564 | 0.71411 | 123.1613 | 1.2222 | 123.175 | 122.9233 | 122.9279 | 122.818 | 122.8592 | -123.056 | -123.0194 | 123.056 | 123.1064 | 28.1479 | 22.76
535.9531 | 123.1155 | -57.811 | 65.2359 | 0.25136 | 0.0034793 | -0.0015059 | 0.090757 | 0.0071384 | -0.0084497 | -0.00078276 | 0.10615 | 0.017364 | 0.078608 | 0.080818 | -0.012775 | 0.026999 | -0.026471 | -29.837 | 65.1031 | -57.8522 | 65.3366 | -57.0969 | -57.8247 | -57.9208 | -35.0647 | 65.1535 | -57.811 | 65.2908 | -56.7032 | -57.6553 | -57.6691 | -0.041199 | -0.13275 | 0.10071 | 0.71411 | -0.10986 | -0.013733 | -0.068664 | 0.027466 | 0 | -0.082398 | 0.054932 | 1.1078 | 0.14191 | 0.15564 | 0.14191 | 0.15564 | 0.75531 | 123.1888 | 1.1078 | 123.1018 | 122.9553 | 122.9645 | 122.9141 | 122.9645 | -123.0881 | -123.0469 | 123.1476 | 123.1018 | 27.9739 | 22.7463
537.0312 | 123.1476 | -57.724 | 65.2679 | 0.14455 | 0.016296 | 0.0027661 | 0.090757 | -0.0067466 | -0.0095177 | 0.0024222 | -0.1685 | 0.0077514 | 0.064723 | 0.10432 | -0.01598 | 0.018454 | -0.014721 | -30.1025 | 65.1764 | -57.811 | 65.451 | -56.9138 | -57.7652 | -57.8247 | -35.1105 | 65.1764 | -57.7881 | 65.3046 | -56.6299 | -57.6874 | -57.5546 | -0.086975 | -0.091552 | 0.18311 | 0.81024 | -0.10071 | -0.041199 | -0.013733 | 0.045776 | -0.064087 | -0.091552 | 0.036621 | 1.0941 | 0.16937 | 0.036621 | 0.23346 | 0.10071 | 0.89722 | 123.262 | 1.1581 | 123.0927 | 122.9874 | 122.9645 | 122.9004 | 122.9004 | -123.0789 | -123.056 | 123.175 | 123.0286 | 27.6215 | 22.6135
537.9688 | 123.1888 | -57.6462 | 65.3 | 0.052997 | 0.0024113 | -0.013256 | 0.092894 | -0.0024746 | 0.0086403 | -0.0061228 | 0.36555 | 0.0045474 | 0.087153 | 0.021003 | -0.0052988 | 0.018454 | -0.0051076 | -30.3314 | 65.1764 | -57.7423 | 65.4282 | -56.9229 | -57.7927 | -57.8064 | -34.9731 | 65.2222 | -57.7057 | 65.4694 | -56.4789 | -57.4722 | -57.4814 | -0.096131 | -0.1236 | 0.12817 | 0.72327 | -0.16022 | -0.14649 | -0.064086 | -0.050354 | -0.059509 | -0.07782 | 0.16937 | 1.1673 | 0.16479 | 0.17395 | 0.2243 | 0.23346 | 0.8194 | 123.1705 | 1.2268 | 123.175 | 122.9187 | 122.9279 | 122.8226 | 122.8683 | -123.0423 | -123.0057 | 123.0743 | 123.1155 | 27.3148 | 22.673
539.0312 | 123.1934 | -57.5729 | 65.4373 | -0.0080386 | 0.0066833 | 0.00063009 | 0.09503 | -0.01102 | 0.0032993 | 0.0034902 | -0.092209 | 0.016296 | 0.066859 | 0.064796 | -0.020252 | 0.02059 | -0.0061756 | -30.4733 | 65.3091 | -57.6691 | 65.5884 | -56.8176 | -57.6233 | -57.6828 | -34.7763 | 65.3412 | -57.6141 | 65.4694 | -56.369 | -57.4905 | -57.3944 | -0.09613 | -0.12817 | 0.15106 | 0.75531 | -0.10986 | -0.050354 | -0.013733 | 0.045776 | -0.041199 | -0.09613 | 0.032043 | 1.2039 | 0.17853 | 0.082397 | 0.21973 | 0.1236 | 0.85144 | 123.2574 | 1.2451 | 123.0835 | 122.9782 | 122.9553 | 122.8821 | 122.9141 | -123.1064 | -123.0515 | 123.1613 | 123.0423 | 27.0996 | 22.7966
539.9531 | 123.1247 | -57.4814 | 65.5197 | 0.15981 | 0.01416 | -0.0036429 | 0.092894 | -0.016361 | 0.01398 | 0.0024222 | 0.16719 | 0.019501 | 0.074336 | 0.057319 | -0.010639 | 0.0067052 | -0.00083564 | -30.7343 | 65.3824 | -57.55 | 65.6342 | -56.6803 | -57.5775 | -57.5729 | -34.4879 | 65.4236 | -57.5317 | 65.625 | -56.3141 | -57.3441 | -57.3669 | -0.068665 | -0.13733 | 0.11444 | 0.80109 | -0.091553 | -0.096131 | -0.022888 | -0.027466 | -0.050354 | -0.09613 | 0.10529 | 1.1673 | 0.11444 | 0.13733 | 0.16479 | 0.18768 | 0.86975 | 123.1842 | 1.2177 | 123.1567 | 122.9324 | 122.9553 | 122.8638 | 122.905 | -123.0698 | -123.0515 | 123.1155 | 123.1064 | 26.7471 | 22.9935
541.0312 | 123.111 | -57.4173 | 65.5792 | 0.12929 | -0.0050657 | 0.0038341 | 0.090757 | 0.0039344 | -0.02554 | 0.0013532 | -0.031174 | 0.015228 | 0.081813 | 0.063728 | -0.0063668 | 0.019522 | 0.0077094 | -31.0043 | 65.451 | -57.5226 | 65.7349 | -56.5796 | -57.4219 | -57.5089 | -34.3094 | 65.4922 | -57.4768 | 65.6204 | -56.2042 | -57.3303 | -57.28 | -0.10529 | -0.12817 | 0.15564 | 0.83771 | -0.091553 | -0.004578 | 0.013733 | 0.10071 | -0.05951 | -0.086975 | 0.041198 | 1.2131 | 0.13733 | 0.086975 | 0.19684 | 0.14648 | 0.94299 | 123.2574 | 1.2726 | 123.0972 | 122.9736 | 122.9691 | 122.8683 | 122.9095 | -123.1018 | -123.056 | 123.1522 | 123.0377 | 26.413 | 23.1079
541.9531 | 123.2483 | -57.3257 | 65.6113 | 0.14455 | 0.0098883 | 0.00063009 | 0.079008 | 0.0028664 | -0.0063137 | -0.00078276 | 0.22823 | 0.0088204 | 0.076472 | 0.058387 | -0.0074348 | 0.022726 | 0.0066414 | -31.1417 | 65.5106 | -57.4219 | 65.7166 | -56.5521 | -57.4997 | -57.4356 | -33.8974 | 65.5426 | -57.3944 | 65.7898 | -56.0806 | -57.0602 | -57.1014 | -0.09613 | -0.10071 | 0.10529 | 0.77362 | -0.10986 | -0.17395 | -0.013733 | -0.07782 | -0.068664 | -0.068664 | 0.17853 | 1.2451 | 0.22431 | 0.2655 | 0.29297 | 0.33417 | 0.86975 | 123.1384 | 1.3138 | 123.1842 | 122.9324 | 122.937 | 122.8363 | 122.8683 | -123.0331 | -123.0057 | 123.0423 | 123.1155 | 26.1841 | 23.4283
543.0469 | 123.2712 | -57.2388 | 65.6845 | 0.037738 | 0.0077523 | 0.0091751 | 0.087553 | -0.012088 | 0.01398 | -0.020009 | -0.07695 | 0.0077514 | 0.062587 | 0.094703 | -0.024525 | 0.02059 | -0.0040396 | -31.3797 | 65.5426 | -57.3532 | 65.7715 | -56.5338 | -57.4493 | -57.4539 | -33.522 | 65.5792 | -57.3074 | 65.7211 | -55.751 | -56.9504 | -57.0053 | -0.11444 | -0.14191 | 0.086975 | 0.70496 | -0.21515 | -0.21057 | -0.10071 | -0.096131 | -0.068664 | -0.10529 | 0.036621 | 1.4877 | 0.23346 | 0.28839 | 0.30212 | 0.35706 | 0.8194 | 123.1247 | 1.5564 | 123.0286 | 122.8958 | 122.8867 | 122.7814 | 122.818 | -123.0377 | -122.9919 | 123.0103 | 122.9599 | 25.8591 | 23.7167
543.9531 | 123.2117 | -57.1609 | 65.7669 | 0.17507 | -0.0029297 | -0.0068469 | 0.093962 | -0.0035426 | -0.0031087 | -0.0018508 | 0.19771 | 0.0077514 | 0.082881 | 0.044502 | -0.022388 | 0.022726 | -0.012585 | -31.7368 | 65.6754 | -57.2571 | 65.8447 | -56.3324 | -57.3166 | -57.312 | -33.2474 | 65.7028 | -57.2388 | 65.9958 | -55.838 | -56.9229 | -56.8954 | -0.09613 | -0.091553 | 0.07782 | 0.82855 | -0.15106 | -0.15564 | -0.054932 | -0.059509 | -0.07782 | -0.064087 | 0.22888 | 1.3229 | 0.2655 | 0.23804 | 0.34332 | 0.31586 | 0.92468 | 123.1018 | 1.4008 | 123.2346 | 122.9324 | 122.9416 | 122.8363 | 122.8638 | -123.024 | -123.0057 | 123.0057 | 123.1567 | 25.4242 | 23.9136
545.0312 | 123.2254 | -57.1426 | 65.7806 | -0.038556 | 0.0098883 | -0.013256 | 0.09503 | -0.021701 | 0.0054353 | -0.0082598 | -0.19902 | 0.013092 | 0.081813 | 0.068 | -0.013843 | 0.013113 | -0.016858 | -31.9656 | 65.6708 | -57.28 | 65.9225 | -56.3232 | -57.28 | -57.28 | -33.0688 | 65.7074 | -57.1976 | 66.037 | -55.7968 | -56.8863 | -56.8314 | -0.13733 | -0.10986 | 0.14191 | 0.8194 | -0.13733 | -0.13733 | 0 | 0 | -0.054932 | -0.073243 | 0.25635 | 1.3458 | 0.31128 | 0.25635 | 0.36621 | 0.31128 | 0.95673 | 123.2025 | 1.4008 | 123.2346 | 122.9507 | 122.905 | 122.8134 | 122.85 | -123.0606 | -122.9782 | 123.0652 | 123.1796 | 25.177 | 24.0738
545.9531 | 123.2758 | -57.0648 | 65.8813 | 0.052997 | -0.0029297 | -0.010051 | 0.090757 | 0.01141 | -0.0052457 | 0.00028524 | 0.075638 | 0.0002754 | 0.0722 | 0.046638 | -0.011707 | 0.0067052 | -0.0019036 | -32.3044 | 65.7349 | -57.1655 | 65.9317 | -56.2683 | -57.2662 | -57.225 | -32.9041 | 65.8035 | -57.1243 | 66.1102 | -55.6183 | -56.7764 | -56.7673 | -0.10071 | -0.14648 | 0.050354 | 0.79651 | -0.16022 | -0.20142 | -0.05951 | -0.10071 | -0.05951 | -0.07782 | 0.22888 | 1.4465 | 0.29755 | 0.28839 | 0.35706 | 0.3479 | 0.89722 | 123.0972 | 1.506 | 123.2346 | 122.9004 | 122.9279 | 122.7997 | 122.8683 | -123.0469 | -123.0057 | 122.9965 | 123.175 | 24.7604 | 24.1608
546.9531 | 123.2071 | -57.0007 | 65.9409 | 0.19033 | 0.0088203 | -0.014324 | 0.091826 | -0.018497 | -0.0063137 | -0.0082598 | 0.18245 | 0.015228 | 0.057246 | 0.059455 | -0.022388 | 0.01525 | -0.0072446 | -32.4875 | 65.8493 | -57.0557 | 66.0324 | -56.2592 | -57.1198 | -57.1747 | -32.8491 | 65.863 | -57.0236 | 66.069 | -55.1331 | -56.5887 | -56.7856 | -0.054932 | -0.091553 | 0.091553 | 0.74158 | -0.17395 | -0.11902 | -0.11902 | -0.064087 | -0.022889 | -0.07782 | 0.12817 | 1.8677 | 0.21515 | 0.41199 | 0.23804 | 0.43488 | 0.79651 | 123.0881 | 1.8906 | 123.0927 | 122.905 | 122.8867 | 122.85 | 122.8638 | -122.9965 | -122.9645 | 123.0331 | 123.0698 | 24.5132 | 24.1516
548.0625 | 123.23 | -56.8634 | 66.1423 | 0.19033 | 0.0077523 | -0.013256 | 0.091826 | 0.0071384 | -0.015927 | -0.0029188 | 0.18245 | 0.0034794 | 0.091426 | 0.053047 | -0.017048 | 0.01525 | -0.0051076 | -32.7438 | 65.9546 | -56.9687 | 66.1331 | -56.1127 | -57.0328 | -57.0694 | -32.4783 | 65.9958 | -56.9138 | 66.2567 | -55.2887 | -56.5521 | -56.5201 | -0.10529 | -0.18768 | -0.009155 | 0.75073 | -0.20599 | -0.16937 | -0.10071 | -0.064087 | -0.050354 | -0.14648 | 0.11444 | 1.5747 | 0.34332 | 0.31128 | 0.39368 | 0.36163 | 0.85602 | 123.1018 | 1.6251 | 123.1705 | 122.9233 | 122.9095 | 122.818 | 122.8592 | -123.111 | -123.056 | 122.9965 | 123.1201 | 24.1196 | 24.3851
548.9531 | 123.2529 | -56.781 | 66.1789 | 0.083514 | 0.0045473 | -0.018596 | 0.079008 | -0.0099516 | -0.0020407 | -0.0071918 | -0.07695 | 0.0066834 | 0.076472 | 0.088294 | -0.0095708 | 0.019522 | -0.012585 | -33.078 | 66.069 | -56.868 | 66.275 | -55.9616 | -56.9046 | -56.9275 | -32.46 | 66.1057 | -56.8176 | 66.3528 | -55.1331 | -56.4651 | -56.4102 | -0.086975 | -0.10986 | 0.09613 | 0.8194 | -0.14648 | -0.1236 | -0.059509 | -0.036621 | -0.036621 | -0.073242 | 0.17395 | 1.6479 | 0.37079 | 0.31586 | 0.40741 | 0.35248 | 0.90637 | 123.143 | 1.6846 | 123.1705 | 122.937 | 122.9233 | 122.85 | 122.8867 | -123.0469 | -122.9965 | 123.056 | 123.1338 | 23.703 | 24.321
550.0312 | 123.175 | -56.781 | 66.2292 | 0.022479 | 0.0024113 | 0.0038341 | 0.092894 | -0.00033857 | -0.0031087 | 0.0024222 | -0.1685 | 0.015228 | 0.057246 | 0.065864 | -0.013843 | 0.02059 | -0.013653 | -33.5815 | 66.1057 | -56.9046 | 66.4536 | -55.8426 | -56.694 | -56.7535 | -32.5104 | 66.1743 | -56.8039 | 66.2933 | -55.1743 | -56.5704 | -56.456 | -0.1236 | -0.1236 | 0.2243 | 0.93842 | 0.027466 | 0.086975 | 0.15106 | 0.21057 | -0.022888 | -0.054932 | 0.064087 | 1.6068 | 0.32501 | 0.21057 | 0.3479 | 0.23346 | 1.062 | 123.3582 | 1.6296 | 123.0972 | 123.0103 | 122.9782 | 122.8867 | 122.9553 | -123.1338 | -123.0331 | 123.2346 | 123.0743 | 23.1995 | 24.2706
550.9531 | 123.1476 | -56.7307 | 66.2659 | 0.052997 | 0.0066833 | -0.018596 | 0.097166 | 0.00072943 | -0.0084497 | 0.0056262 | 0.15193 | 0.0045474 | 0.091426 | 0.058387 | -0.0063668 | 0.019522 | 0.0034374 | -33.4579 | 66.156 | -56.8039 | 66.3986 | -55.7968 | -56.7627 | -56.7856 | -32.2861 | 66.188 | -56.7764 | 66.3895 | -55.0827 | -56.4651 | -56.4102 | -0.073242 | -0.10986 | 0.13275 | 0.93384 | -0.054931 | -0.032043 | 0.018311 | 0.041199 | -0.045776 | -0.07782 | 0.1236 | 1.6479 | 0.32043 | 0.2655 | 0.36621 | 0.31128 | 1.0071 | 123.2025 | 1.6937 | 123.1659 | 122.9599 | 122.9645 | 122.8867 | 122.9187 | -123.0698 | -123.0423 | 123.1293 | 123.1201 | 23.2727 | 24.4446
552.0312 | 123.1064 | -56.7535 | 66.2796 | 0.12929 | 0.010956 | -0.019664 | 0.092894 | 0.0017974 | -0.018063 | -0.0018508 | -0.13799 | 0.018433 | 0.066859 | 0.071205 | -0.018116 | 0.014181 | -0.030743 | -33.5907 | 66.1789 | -56.8268 | 66.5314 | -55.6549 | -56.6162 | -56.7215 | -32.5012 | 66.2018 | -56.781 | 66.3437 | -55.0095 | -56.5247 | -56.4102 | -0.073242 | -0.10071 | 0.25177 | 1.0986 | 0.032043 | 0.13733 | 0.10529 | 0.21057 | -0.027466 | -0.07782 | 0.064087 | 1.7441 | 0.34332 | 0.22888 | 0.37079 | 0.25635 | 1.1719 | 123.3582 | 1.7715 | 123.1247 | 123.0057 | 122.9828 | 122.9324 | 122.9553 | -123.1064 | -123.0606 | 123.2849 | 123.0972 | 23.1628 | 24.2523
552.9688 | 123.1476 | -56.781 | 66.2109 | 0.083514 | 0.0056153 | -0.019664 | 0.091826 | 0.0060704 | -0.015927 | -0.012532 | -0.12273 | 0.012024 | 0.079676 | 0.038093 | -0.0074348 | 0.025931 | 0.00023236 | -33.9249 | 66.1423 | -56.8771 | 66.3757 | -55.7281 | -56.7902 | -56.7215 | -32.5699 | 66.1606 | -56.8039 | 66.3483 | -55.0323 | -56.4697 | -56.4377 | -0.09613 | -0.068664 | 0.16479 | 1.0529 | 0.059509 | -0.009155 | 0.15564 | 0.086975 | -0.022888 | -0.050354 | 0.13733 | 1.7487 | 0.34332 | 0.31128 | 0.36621 | 0.33417 | 1.149 | 123.2529 | 1.7715 | 123.1522 | 123.0194 | 122.9645 | 122.9233 | 122.9416 | -123.0881 | -123.0148 | 123.1567 | 123.1293 | 22.8561 | 24.2111
554.0312 | 123.1247 | -56.6849 | 66.2979 | 0.022479 | 0.010956 | -0.0057789 | 0.10144 | -0.0067466 | 0.0022313 | -0.0082598 | -0.36687 | 0.0056154 | 0.062587 | 0.081886 | -0.024525 | 0.029135 | -0.0083126 | -34.053 | 66.2338 | -56.7856 | 66.5543 | -55.5679 | -56.5842 | -56.6483 | -32.7255 | 66.2613 | -56.749 | 66.3803 | -54.9088 | -56.4697 | -56.3965 | -0.10071 | -0.064087 | 0.25635 | 1.1169 | 0.036621 | 0.10071 | 0.13733 | 0.20142 | -0.064087 | -0.036621 | 0.082397 | 1.7761 | 0.28839 | 0.21515 | 0.35248 | 0.27923 | 1.2177 | 123.3398 | 1.8402 | 123.1293 | 123.0194 | 123.0103 | 122.9187 | 122.9462 | -123.0835 | -123.0469 | 123.2391 | 123.0652 | 22.6318 | 23.9594
554.9531 | 123.1522 | -56.5567 | 66.4215 | 0.12929 | 0.013092 | -0.019664 | 0.087553 | -0.0099516 | -0.03088 | -0.0039868 | 0.16719 | 0.0013434 | 0.087153 | 0.06266 | -0.013843 | 0.018454 | 0.01305 | -34.3597 | 66.2979 | -56.6528 | 66.4764 | -55.5542 | -56.6345 | -56.5979 | -32.6065 | 66.3345 | -56.6299 | 66.5451 | -54.7028 | -56.2363 | -56.2225 | -0.09613 | -0.1236 | 0.054931 | 1.0025 | -0.041198 | -0.077819 | 0.054932 | 0.018311 | -0.073242 | -0.086975 | 0.1236 | 1.8539 | 0.33417 | 0.32044 | 0.40741 | 0.39368 | 1.0986 | 123.1293 | 1.9272 | 123.175 | 122.9507 | 122.9645 | 122.8546 | 122.8912 | -123.0743 | -123.0515 | 123.0331 | 123.1018 | 22.197 | 23.9502
556.0312 | 123.0835 | -56.5155 | 66.4673 | 0.12929 | 0.0056153 | -0.011119 | 0.079008 | -0.0014066 | -0.014859 | -0.0029188 | -0.21428 | 0.01416 | 0.073268 | 0.086158 | -0.0095708 | 0.018454 | -0.012585 | -34.671 | 66.3849 | -56.5933 | 66.7557 | -55.3436 | -56.4102 | -56.4514 | -32.6523 | 66.4444 | -56.5521 | 66.568 | -54.7531 | -56.25 | -56.2454 | -0.07782 | -0.082397 | 0.28839 | 1.1719 | 0.064087 | 0.10529 | 0.14191 | 0.18311 | -0.036621 | -0.022888 | 0.10071 | 1.7624 | 0.27008 | 0.2655 | 0.3067 | 0.30212 | 1.2497 | 123.349 | 1.799 | 123.1201 | 122.9782 | 122.9965 | 122.9004 | 122.9599 | -123.0606 | -123.0194 | 123.2712 | 123.0835 | 21.8445 | 23.8632
556.9688 | 123.1659 | -56.3965 | 66.5909 | 0.14455 | 0.0088203 | -0.0089829 | 0.090757 | 0.016751 | -0.011654 | -0.0093278 | 0.090897 | 0.017364 | 0.066859 | 0.068 | -0.0052988 | 0.022726 | -0.0072446 | -34.8221 | 66.5039 | -56.5155 | 66.7191 | -55.2612 | -56.3919 | -56.3644 | -32.5974 | 66.5176 | -56.4285 | 66.687 | -54.5517 | -56.1127 | -56.0806 | -0.11902 | -0.086975 | 0.12817 | 1.1353 | 0.032043 | 0.004577 | 0.15106 | 0.1236 | -0.032044 | -0.073242 | 0.096131 | 1.8448 | 0.31586 | 0.28381 | 0.3479 | 0.31586 | 1.2543 | 123.2346 | 1.8768 | 123.1155 | 123.0194 | 122.9462 | 122.9004 | 122.9141 | -123.1064 | -123.0194 | 123.1155 | 123.0835 | 21.5744 | 23.7991
557.9531 | 123.1796 | -56.3324 | 66.6687 | 0.052997 | 0.0077523 | -0.01646 | 0.088621 | 0.013547 | 0.0022313 | -0.0018508 | 0.24348 | 0.0088204 | 0.066859 | 0.042366 | -0.010639 | 0.02059 | -0.0061756 | -35.3989 | 66.5588 | -56.3599 | 66.7831 | -55.2612 | -56.3049 | -56.3736 | -32.5882 | 66.5909 | -56.3232 | 66.806 | -54.4373 | -55.957 | -55.9891 | -0.027466 | -0.10986 | 0.11444 | 1.0712 | -0.041199 | 0.027465 | -0.013733 | 0.054931 | 0.009155 | -0.07782 | 0.13733 | 1.8951 | 0.34332 | 0.37537 | 0.33417 | 0.36621 | 1.0986 | 123.143 | 1.886 | 123.1293 | 122.9187 | 122.9141 | 122.8912 | 122.9233 | -123.0286 | -122.9919 | 123.1155 | 123.1384 | 20.9335 | 23.7442
558.9531 | 123.317 | -56.1813 | 66.7969 | 0.068255 | 0.0024113 | -0.017528 | 0.09503 | 0.0028664 | -0.011654 | 0.010966 | 0.274 | 0.0088204 | 0.073268 | 0.04557 | -0.0063668 | 0.025931 | -0.0051076 | -35.5911 | 66.6321 | -56.2912 | 66.7786 | -55.1605 | -56.3004 | -56.2637 | -31.9016 | 66.6595 | -56.2729 | 66.925 | -54.1397 | -55.7968 | -55.8105 | -0.10986 | -0.16479 | -0.018311 | 1.0208 | -0.082398 | -0.11902 | 0.027466 | -0.009155 | -0.091553 | -0.13733 | 0.12817 | 2.0416 | 0.37079 | 0.38452 | 0.46234 | 0.47607 | 1.1307 | 123.0698 | 2.1332 | 123.1979 | 122.9233 | 122.9324 | 122.8134 | 122.8409 | -123.0881 | -123.0698 | 122.9599 | 123.1064 | 20.5902 | 24.2798
560.0312 | 123.143 | -56.1127 | 66.8838 | 0.11403 | 0.0077523 | -0.015392 | 0.097166 | 0.0017974 | 0.0032993 | -0.010396 | -0.092209 | 0.0088204 | 0.074336 | 0.038093 | -0.023456 | 0.025931 | -0.015789 | -35.7605 | 66.7786 | -56.218 | 67.0074 | -54.895 | -56.131 | -56.0532 | -31.2241 | 66.8152 | -56.163 | 67.0212 | -53.9841 | -55.7419 | -55.7968 | -0.10529 | -0.10529 | 0.1236 | 1.2177 | 0.059509 | -0.01831 | 0.16479 | 0.086976 | -0.050354 | -0.068664 | 0.13733 | 2.1286 | 0.31586 | 0.37079 | 0.36621 | 0.42114 | 1.3229 | 123.2254 | 2.179 | 123.1842 | 122.9965 | 122.9782 | 122.8912 | 122.9279 | -123.1018 | -123.0469 | 123.1201 | 123.1338 | 20.3522 | 24.8886
560.9531 | 123.2483 | -56.0349 | 66.9296 | 0.12929 | 0.01416 | -0.028209 | 0.091826 | -0.0035426 | 0.024662 | -0.0082598 | 0.22823 | 0.0034794 | 0.070063 | 0.016731 | -0.0085028 | 0.0099092 | -0.0040396 | -35.7285 | 66.8015 | -56.1127 | 66.9205 | -54.9316 | -56.131 | -56.1172 | -30.629 | 66.8106 | -56.0715 | 67.0761 | -53.6911 | -55.5862 | -55.6137 | -0.07782 | -0.12817 | -0.009155 | 1.1032 | -0.082398 | -0.09613 | -0.004578 | -0.01831 | -0.036621 | -0.11902 | 0.14648 | 2.3438 | 0.42114 | 0.44861 | 0.45776 | 0.48523 | 1.181 | 123.0331 | 2.3804 | 123.1476 | 122.9141 | 122.8821 | 122.8363 | 122.8455 | -123.0423 | -123.0011 | 122.9553 | 123.111 | 20.3064 | 25.4059
562.0312 | 123.2529 | -55.632 | 67.3096 | -0.053815 | 0.015228 | -0.027141 | 0.097166 | 0.0028664 | -0.020199 | -0.010396 | 0.04512 | 0.0088204 | 0.079676 | 0.061592 | -0.019184 | 0.023794 | -0.0061756 | -35.6781 | 67.1768 | -55.7465 | 67.3462 | -54.4739 | -55.7556 | -55.6778 | -29.4571 | 67.2226 | -55.6778 | 67.543 | -53.3066 | -55.2017 | -55.1926 | -0.11444 | -0.13275 | 0.036621 | 1.1581 | -0.045776 | -0.1236 | 0.068665 | -0.009155 | -0.045776 | -0.086975 | 0.23346 | 2.3254 | 0.43945 | 0.4303 | 0.48523 | 0.47607 | 1.2726 | 123.0927 | 2.3712 | 123.2208 | 122.9233 | 122.9004 | 122.8088 | 122.8546 | -123.056 | -122.9874 | 122.9782 | 123.175 | 19.9539 | 26.1749
562.9688 | 123.1979 | -55.4535 | 67.5476 | 0.28188 | 0.0077523 | -0.022869 | 0.099302 | -0.0078156 | -0.0063137 | 0.0013532 | 0.075638 | 0.022705 | 0.063655 | 0.081886 | -0.012775 | 0.026999 | -0.012585 | -35.6964 | 67.4606 | -55.545 | 67.6895 | -54.1626 | -55.3711 | -55.4169 | -29.2236 | 67.5018 | -55.4626 | 67.63 | -53.0457 | -55.0278 | -55.0323 | -0.091553 | -0.086975 | 0.14191 | 1.2909 | 0.036621 | 0.082397 | 0.12817 | 0.17395 | -0.009155 | -0.045776 | 0.082398 | 2.4078 | 0.42114 | 0.42572 | 0.4303 | 0.43487 | 1.3824 | 123.2346 | 2.417 | 123.0927 | 123.0057 | 122.9645 | 122.9141 | 122.9553 | -123.0927 | -123.0103 | 123.143 | 123.0835 | 19.7571 | 26.2299
564.0312 | 123.1659 | -55.22 | 67.7628 | 0.0072204 | 0.01416 | -0.020732 | 0.093962 | -0.0056786 | 0.0011633 | -0.0039868 | 0.39607 | 0.0077514 | 0.066859 | 0.043434 | -0.025593 | 0.016318 | -0.016858 | -35.495 | 67.6666 | -55.3253 | 67.9047 | -53.801 | -55.1193 | -55.2887 | -28.9948 | 67.7032 | -55.2567 | 67.8589 | -52.8809 | -54.8309 | -54.776 | -0.10528 | -0.09613 | 0.14191 | 1.4191 | -0.068664 | 0.10071 | 0.036621 | 0.20599 | -0.036621 | -0.059509 | 0.096131 | 2.3392 | 0.44403 | 0.3891 | 0.48065 | 0.42572 | 1.5244 | 123.23 | 2.3758 | 123.1155 | 122.9919 | 122.9599 | 122.8867 | 122.9233 | -123.0881 | -123.0194 | 123.1247 | 123.0789 | 19.725 | 26.2253
564.9531 | 123.111 | -55.069 | 67.9184 | 0.12929 | -0.0018617 | -0.01646 | 0.097166 | 0.0060704 | -0.014859 | -0.012532 | -0.07695 | 0.013092 | 0.067927 | 0.075477 | -0.0042298 | 0.018454 | -0.0040396 | -35.4401 | 67.8268 | -55.1971 | 68.1015 | -53.6224 | -54.9545 | -55.0095 | -29.361 | 67.8543 | -55.1331 | 67.8864 | -52.7481 | -54.7394 | -54.6982 | -0.12817 | -0.091553 | 0.1831 | 1.4465 | 0.05951 | 0.11444 | 0.18768 | 0.24262 | -0.064087 | -0.064087 | -0.032043 | 2.3209 | 0.37079 | 0.32959 | 0.43488 | 0.39368 | 1.5747 | 123.2986 | 2.3849 | 123.0194 | 123.024 | 122.9874 | 122.8958 | 122.9233 | -123.1155 | -123.0515 | 123.1705 | 122.9553 | 19.6289 | 25.708
566.0312 | 123.1522 | -54.8355 | 68.1747 | 0.098773 | -0.0050657 | -0.0068469 | 0.09503 | 0.0060704 | -0.0095177 | 0.0045582 | -0.046432 | 0.0088204 | 0.073268 | 0.071205 | -0.017048 | 0.019522 | -0.027539 | -35.3989 | 68.0649 | -54.9454 | 68.2938 | -53.3203 | -54.7531 | -54.7577 | -29.5578 | 68.0923 | -54.9088 | 68.2709 | -52.3865 | -54.3549 | -54.4189 | -0.10986 | -0.10986 | 0.11902 | 1.5152 | 0.07782 | 0.082397 | 0.18768 | 0.19226 | -0.073242 | -0.082398 | 0.09613 | 2.449 | 0.41656 | 0.48065 | 0.48981 | 0.55389 | 1.6251 | 123.2391 | 2.5223 | 123.1796 | 123.0103 | 123.0011 | 122.9004 | 122.9279 | -123.1201 | -123.0835 | 123.1293 | 123.1064 | 19.4366 | 25.2777
566.9531 | 123.143 | -54.7348 | 68.3075 | 0.037738 | 0.010956 | -0.03355 | 0.088621 | 0.0050024 | -0.028744 | 0.0034902 | 0.15193 | 0.010956 | 0.075404 | 0.049842 | -0.010639 | 0.019522 | -0.0093806 | -35.3989 | 68.2205 | -54.7577 | 68.4311 | -53.2745 | -54.6524 | -54.7028 | -29.7455 | 68.2251 | -54.7302 | 68.3166 | -52.2446 | -54.1534 | -54.2496 | -0.022888 | -0.086975 | 0.1236 | 1.4603 | 0.032043 | 0.082397 | 0.054931 | 0.10528 | 0.004577 | -0.082397 | 0.009155 | 2.4902 | 0.48523 | 0.58136 | 0.48065 | 0.57678 | 1.4832 | 123.1888 | 2.4857 | 123.0469 | 122.9782 | 122.9553 | 122.9553 | 122.9599 | -123.0652 | -123.0377 | 123.1659 | 123.0515 | 19.3359 | 24.9893
568.0312 | 123.1796 | -54.4647 | 68.4906 | 0.052997 | -0.0018617 | -0.03355 | 0.093962 | 0.0028664 | -0.013791 | 0.00028524 | 0.28926 | 0.0077514 | 0.074336 | 0.030616 | -0.017048 | 0.023794 | -0.0083126 | -35.3897 | 68.3624 | -54.5425 | 68.6005 | -52.9541 | -54.4418 | -54.5013 | -29.8233 | 68.4128 | -54.5151 | 68.5867 | -52.0065 | -53.9062 | -53.8925 | -0.07782 | -0.12817 | 0.10986 | 1.5106 | -0.036621 | 0.022889 | 0.041199 | 0.10071 | -0.050354 | -0.07782 | 0.09613 | 2.4582 | 0.57221 | 0.55847 | 0.62256 | 0.60883 | 1.5884 | 123.143 | 2.5085 | 123.1018 | 122.905 | 122.9279 | 122.8271 | 122.8775 | -123.0331 | -123.0057 | 123.0652 | 123.0515 | 19.075 | 24.6414
568.9531 | 123.2666 | -54.2862 | 68.6554 | 0.17507 | 0.0056153 | -0.026073 | 0.084349 | 0.017819 | -0.0063137 | -0.00078276 | 0.22823 | 0.0098884 | 0.089289 | 0.069068 | -0.022388 | 0.016318 | -0.010449 | -35.1929 | 68.5547 | -54.4052 | 68.7241 | -52.858 | -54.3228 | -54.4235 | -29.2511 | 68.5822 | -54.3274 | 68.8522 | -51.7044 | -53.6041 | -53.7094 | -0.11902 | -0.10071 | 0.068664 | 1.4282 | -0.13733 | -0.036621 | -0.018311 | 0.082397 | -0.041199 | -0.073243 | 0.19684 | 2.5818 | 0.57678 | 0.68207 | 0.61798 | 0.72327 | 1.5472 | 123.1293 | 2.623 | 123.1796 | 122.9599 | 122.9095 | 122.8409 | 122.8683 | -123.0606 | -122.9828 | 123.0103 | 123.1384 | 19.0933 | 25.0351
570.0312 | 123.1705 | -54.2313 | 68.7973 | 0.022479 | 0.0056153 | -0.018596 | 0.090757 | -0.0088836 | -0.011654 | 0.010966 | -0.061691 | 0.0056154 | 0.079676 | 0.13209 | -0.013843 | 0.028067 | -0.0029716 | -35.2158 | 68.6508 | -54.332 | 68.9346 | -52.5742 | -54.1626 | -54.1397 | -29.1962 | 68.7149 | -54.2358 | 68.8614 | -51.7136 | -53.6499 | -53.6499 | -0.10071 | -0.14648 | 0.13733 | 1.6571 | 0.091553 | 0.068664 | 0.19226 | 0.16937 | -0.004578 | -0.082397 | 0.064087 | 2.5177 | 0.58136 | 0.58136 | 0.58594 | 0.58594 | 1.7578 | 123.2666 | 2.5223 | 123.0972 | 122.9828 | 122.9507 | 122.8821 | 122.9462 | -123.1293 | -123.0331 | 123.1659 | 123.0927 | 19.0155 | 25.0351
570.9531 | 123.1888 | -53.8651 | 69.0994 | 0.14455 | 0.016296 | -0.027141 | 0.089689 | -0.0067466 | -0.020199 | -0.0050548 | 0.28926 | 0.0034794 | 0.078608 | 0.040229 | -0.012775 | 0.012045 | -0.0040396 | -34.7351 | 69.0033 | -53.9337 | 69.1269 | -52.4368 | -53.8513 | -53.8696 | -28.363 | 69.017 | -53.9017 | 69.2459 | -51.2833 | -53.1281 | -53.302 | -0.068665 | -0.09613 | 0.027466 | 1.4282 | -0.004578 | 0.013733 | 0.064087 | 0.082398 | -0.036621 | -0.082397 | 0.14649 | 2.5818 | 0.56305 | 0.737 | 0.59967 | 0.77362 | 1.4969 | 123.0606 | 2.6184 | 123.1476 | 122.937 | 122.9187 | 122.8683 | 122.8821 | -123.0331 | -123.0011 | 122.9919 | 123.111 | 19.1299 | 25.502
571.9531 | 123.1293 | -53.3569 | 69.6854 | 0.052997 | -0.0029297 | -0.026073 | 0.092894 | 0.0039344 | 0.0065043 | 0.0024222 | 0.060379 | -0.0018616 | 0.075404 | 0.054115 | -0.011707 | 0.017386 | 0.00023236 | -34.0485 | 69.516 | -53.4302 | 69.7266 | -51.6266 | -53.2654 | -53.2791 | -28.2211 | 69.5938 | -53.3844 | 69.6716 | -50.7889 | -52.6474 | -52.771 | -0.073242 | -0.16937 | 0.041198 | 1.7303 | 0.07782 | 0.091553 | 0.15106 | 0.1648 | -0.027465 | -0.091553 | -0.013733 | 2.5681 | 0.58594 | 0.70953 | 0.6134 | 0.737 | 1.8036 | 123.1567 | 2.5955 | 123.056 | 122.9462 | 122.9782 | 122.8729 | 122.9507 | -123.1155 | -123.0698 | 123.0835 | 123.0286 | 19.3085 | 25.1358
573.0312 | 123.2162 | -52.9449 | 70.0012 | 0.037738 | 0.0066833 | -0.039959 | 0.10251 | -0.0056786 | -0.011654 | -0.0061228 | -0.046432 | 0.012024 | 0.078608 | 0.063728 | -0.01598 | 0.024863 | 0.0087774 | -33.4946 | 69.9097 | -53.0777 | 70.1202 | -51.1322 | -52.9221 | -52.8763 | -27.7863 | 69.9554 | -52.9907 | 70.1981 | -50.3036 | -52.2354 | -52.272 | -0.13275 | -0.091553 | 0.11902 | 1.8127 | 0.068664 | 0.022888 | 0.20142 | 0.15564 | -0.045777 | -0.045777 | 0.19684 | 2.6413 | 0.67291 | 0.70953 | 0.71869 | 0.75531 | 1.9455 | 123.1979 | 2.6871 | 123.1888 | 122.9874 | 122.9462 | 122.8546 | 122.9004 | -123.0789 | -122.9919 | 123.0652 | 123.143 | 19.4504 | 25.1587
573.9531 | 123.175 | -52.8625 | 70.0699 | 0.12929 | 0.0066833 | -0.032482 | 0.099302 | -0.0014066 | -0.03088 | -0.0082598 | 0.274 | 0.012024 | 0.07754 | 0.044502 | -0.018116 | 0.025931 | -0.024334 | -33.7097 | 69.9509 | -52.9495 | 70.1157 | -51.1963 | -52.9037 | -52.9449 | -26.7609 | 69.9829 | -52.8992 | 70.2164 | -50.0519 | -51.86 | -52.0294 | -0.086975 | -0.11902 | 0.045777 | 1.6663 | -0.082397 | -0.041199 | 0.004578 | 0.045776 | -0.036621 | -0.086975 | 0.14648 | 2.8107 | 0.83313 | 1.0025 | 0.86975 | 1.0391 | 1.7532 | 123.0652 | 2.8473 | 123.1155 | 122.9004 | 122.8821 | 122.8134 | 122.8455 | -123.0194 | -122.9691 | 122.9782 | 123.0789 | 19.1528 | 26.1017
575.0312 | 123.0743 | -52.0798 | 70.9213 | 0.11403 | 0.016296 | -0.028209 | 0.10464 | 0.0092744 | -0.018063 | 0.0077622 | -0.13799 | 0.0098884 | 0.063655 | 0.076545 | -0.018116 | 0.018454 | -0.0061756 | -32.8949 | 70.8527 | -52.1484 | 71.0815 | -49.9558 | -51.9196 | -51.947 | -25.7263 | 70.8939 | -52.1027 | 70.9534 | -49.2599 | -51.4435 | -51.4389 | -0.068664 | -0.068665 | 0.16022 | 2.124 | 0.13275 | 0.16022 | 0.20142 | 0.22888 | -0.022888 | -0.027466 | 0.032043 | 2.8198 | 0.64087 | 0.63629 | 0.66376 | 0.65918 | 2.1927 | 123.23 | 2.8427 | 123.056 | 123.0011 | 122.9965 | 122.9324 | 122.9736 | -123.0698 | -123.024 | 123.1613 | 123.0331 | 19.1849 | 26.3535
575.9531 | 123.2071 | -51.8509 | 71.1411 | 0.15981 | 0.0077523 | -0.042095 | 0.09503 | 0.0092744 | -0.0052457 | -0.0082598 | 0.18245 | 0.01416 | 0.075404 | 0.041297 | -0.013843 | 0.014181 | 0.0045054 | -32.6248 | 71.0083 | -51.947 | 71.0861 | -49.791 | -51.7685 | -51.915 | -25.2411 | 71.0449 | -51.8829 | 71.2555 | -48.848 | -51.1414 | -51.1322 | -0.09613 | -0.13275 | -0.054931 | 2.0599 | -0.064087 | 0.082397 | 0.032043 | 0.17853 | -0.032044 | -0.09613 | 0.11444 | 3.0029 | 0.71869 | 0.70953 | 0.75073 | 0.74158 | 2.1561 | 123.0331 | 3.035 | 123.1384 | 122.9553 | 122.9279 | 122.8592 | 122.8958 | -123.0881 | -123.024 | 122.937 | 123.1064 | 19.2261 | 26.6098
577.0312 | 123.1201 | -51.2054 | 71.8048 | 0.15981 | 0.0045473 | -0.034618 | 0.092894 | 0.0017974 | -0.016995 | 0.0024222 | -0.12273 | 0.024841 | 0.066859 | 0.075477 | -0.0031618 | 0.024863 | -0.012585 | -32.0938 | 71.6904 | -51.3016 | 71.965 | -48.9899 | -51.0269 | -51.0544 | -25.0809 | 71.7316 | -51.2512 | 71.846 | -48.2208 | -50.6104 | -50.5829 | -0.096131 | -0.11444 | 0.16022 | 2.2156 | 0.15106 | 0.17853 | 0.24719 | 0.27466 | -0.045777 | -0.073243 | 0.041198 | 2.9846 | 0.62256 | 0.59509 | 0.66833 | 0.64087 | 2.3117 | 123.2666 | 3.0304 | 123.0972 | 122.9919 | 122.9828 | 122.8958 | 122.937 | -123.1064 | -123.056 | 123.1705 | 123.0515 | 19.1116 | 26.1246
577.9688 | 123.0927 | -50.8942 | 72.1527 | 0.037738 | 0.0024113 | -0.027141 | 0.10678 | -0.0099516 | -0.0020407 | -0.010396 | 0.029861 | 0.013092 | 0.096766 | 0.068 | -0.017048 | 0.023794 | -0.0083126 | -32.2769 | 72.0566 | -50.9583 | 72.3404 | -48.587 | -50.6699 | -50.798 | -24.884 | 72.1024 | -50.8987 | 72.1573 | -47.7814 | -50.2945 | -50.2625 | -0.064087 | -0.09613 | 0.18768 | 2.3071 | 0.09613 | 0.2243 | 0.16022 | 0.28839 | -0.004578 | -0.050354 | 0.004578 | 3.1128 | 0.63171 | 0.59967 | 0.63629 | 0.60425 | 2.3712 | 123.2986 | 3.1174 | 123.056 | 123.0148 | 123.0011 | 122.9507 | 122.9965 | -123.111 | -123.0515 | 123.2346 | 123.0515 | 18.6172 | 26.0101
579.0312 | 123.1705 | -50.4822 | 72.5281 | 0.19033 | 0.010956 | -0.029277 | 0.10678 | 0.0092744 | -0.00097271 | -0.0029188 | 0.029861 | 0.019501 | 0.079676 | 0.044502 | -0.01598 | 0.026999 | -0.014721 | -32.2769 | 72.4045 | -50.5783 | 72.6196 | -47.818 | -50.3998 | -50.4501 | -24.7833 | 72.4548 | -50.5051 | 72.5922 | -47.3282 | -49.9374 | -49.7589 | -0.09613 | -0.1236 | 0.091553 | 2.6642 | 0.032044 | 0.082398 | 0.12817 | 0.17853 | -0.022888 | -0.073242 | 0.064087 | 3.154 | 0.72327 | 0.54474 | 0.74616 | 0.56763 | 2.7603 | 123.1979 | 3.1769 | 123.0972 | 122.9828 | 122.9599 | 122.8867 | 122.937 | -123.1064 | -123.0331 | 123.1018 | 123.0743 | 18.2053 | 25.6989
579.9531 | 123.2712 | -52.0889 | 70.8572 | 0.068255 | -0.010406 | -0.030345 | 0.088621 | 0.01141 | 0.0043673 | -0.010396 | -0.39739 | 0.72766 | 0.078608 | 0.049842 | -0.022388 | 0.048361 | 0.71053 | -33.3389 | 70.7565 | -52.1805 | 70.8984 | -49.2554 | -52.0432 | -52.1896 | -21.2952 | 70.6833 | -52.0706 | 70.9579 | -42.0319 | -51.2924 | 70.8527 | -0.091553 | -0.10071 | 0.041198 | 2.8336 | -0.10071 | 0.045776 | -0.009155 | 0.13733 | 0.01831 | -0.17395 | 0.10071 | 10.0571 | 122.9416 | 0.79651 | 122.9233 | 0.7782 | 2.9251 | 123.0789 | 10.0388 | 123.0286 | 122.937 | 122.7539 | 122.8455 | 122.7722 | -123.0377 | -122.9279 | 122.9874 | 123.0469 | 18.75 | 30.7938
581.0312 | 123.0789 | -52.121 | 70.8572 | 0.098773 | 0.0056153 | -0.031414 | 0.092894 | -0.0056786 | -0.0063137 | 0.0024222 | -0.61101 | 0.8067 | 0.085017 | 0.023139 | -0.028797 | 0.06011 | 0.7618 | -32.5058 | 70.7382 | -52.2125 | 70.9396 | -48.9578 | -51.9333 | -52.0523 | -21.8811 | 70.6787 | -52.0889 | 70.7565 | -41.8442 | -51.3702 | 70.7428 | -0.091552 | -0.11902 | 0.082397 | 3.1631 | 0.068665 | 0.18768 | 0.16022 | 0.27923 | 0.032044 | -0.17853 | -0.10071 | 10.2768 | 122.8638 | 0.75073 | 122.8317 | 0.71869 | 3.2547 | 123.1522 | 10.2448 | 122.8455 | 122.9507 | 122.7676 | 122.8592 | 122.7997 | -123.0698 | -122.9462 | 123.0606 | 122.8775 | 19.6152 | 30.2399
581.9531 | 123.0927 | -51.7273 | 71.2418 | 0.068255 | 0.0024113 | -0.041027 | 0.09503 | 0.013547 | 0.0032993 | 0.00028524 | -0.90093 | 0.79602 | 0.09463 | 0.042366 | -0.01598 | 0.051565 | 0.77996 | -31.4804 | 71.1227 | -51.8005 | 71.4249 | -48.2986 | -51.5854 | -51.6403 | -21.7712 | 71.0953 | -51.6724 | 71.2372 | -41.1667 | -50.885 | 71.1502 | -0.073242 | -0.11902 | 0.18311 | 3.4286 | 0.086975 | 0.14191 | 0.16022 | 0.21515 | 0.054932 | -0.14648 | -0.004577 | 10.5606 | 122.8775 | 0.84228 | 122.8226 | 0.78735 | 3.5019 | 123.2254 | 10.5057 | 122.9095 | 122.9233 | 122.7676 | 122.85 | 122.8226 | -123.0423 | -122.9141 | 123.1522 | 122.9645 | 20.2469 | 29.9561
582.9688 | 123.1293 | -55.9891 | 66.9662 | 0.068255 | 0.0024113 | -0.12113 | 0.093962 | 0.0060704 | -0.019131 | -0.012532 | -0.07695 | 0.13165 | 0.095698 | -0.0035628 | 0.058788 | 0.11993 | -0.0093806 | -34.6161 | 66.8838 | -56.0806 | 67.1036 | -52.0752 | -55.8517 | -55.8655 | 4.129 | 66.925 | -56.0028 | -40.3381 | 67.0761 | 66.9525 | 67.1402 | -0.091552 | -0.082398 | 0.13733 | 3.9139 | 0.1236 | 0.13733 | 0.21515 | 0.22888 | -0.013733 | -0.041199 | -107.3044 | 123.0652 | 123.1293 | 122.9416 | 123.143 | 122.9553 | 4.0054 | 123.1842 | 123.0789 | 15.6647 | 122.9645 | 122.9279 | 122.8729 | 122.9141 | -123.0469 | -122.9691 | 123.0927 | 15.6509 | 21.373 | 60.1181
583.9531 | 123.2437 | -57.2845 | 65.6158 | 0.083514 | 0.0077523 | -0.13288 | 0.10037 | -0.0056786 | 0.0054353 | -0.010396 | 0.075638 | 0.12952 | 0.088221 | -0.049492 | 0.067333 | 0.11565 | 0.0066414 | -35.0555 | 65.4922 | -57.3761 | 65.6891 | -53.54 | -57.2754 | -57.3532 | 65.8401 | 65.5289 | -57.3441 | -40.4709 | 65.7806 | 65.7806 | 65.8813 | -0.091553 | -0.1236 | 0.073242 | 3.7445 | -0.068664 | 0.009155 | 0.022889 | 0.10071 | -0.059509 | -0.086975 | -106.0867 | 123.0652 | 123.1659 | 123.0652 | 123.2254 | 123.1247 | 3.8361 | 123.0652 | 123.1247 | 16.8732 | 122.8683 | 122.8729 | 122.7768 | 122.8134 | -122.9919 | -122.9599 | 122.9736 | 16.8137 | 22.229 | 123.1247
585.0312 | 123.056 | -56.7352 | 66.2476 | 0.068255 | 0.0077523 | -0.14463 | 0.098234 | 0.018887 | 0.0097083 | -0.0061228 | -0.27531 | 0.13913 | 0.089289 | -0.016381 | 0.061993 | 0.12206 | -0.0083126 | -33.9706 | 66.1285 | -56.8451 | 66.4169 | -52.3361 | -56.456 | -56.6528 | 66.2201 | 66.1789 | -56.7444 | -39.3997 | 66.2888 | 66.1331 | 66.2796 | -0.10986 | -0.11902 | 0.16937 | 4.3991 | 0.082397 | 0.27923 | 0.19226 | 0.3891 | -0.009156 | -0.068665 | -105.6473 | 123.024 | 123.0148 | 122.8683 | 123.024 | 122.8775 | 4.509 | 123.262 | 123.0331 | 17.3447 | 122.9736 | 122.9233 | 122.8638 | 122.9141 | -123.0927 | -122.9919 | 123.1522 | 17.3355 | 22.7646 | 122.9553
585.9531 | 123.2025 | -56.5979 | 66.2476 | 0.19033 | 0.0034793 | -0.14997 | 0.10037 | 0.017819 | -0.015927 | 0.0077622 | 0.16719 | 0.12952 | 0.089289 | -0.032403 | 0.068401 | 0.12099 | 0.0013004 | -34.2453 | 66.1835 | -56.7123 | 66.2979 | -52.5879 | -56.6254 | -56.6391 | 66.481 | 66.1835 | -56.6711 | -38.15 | 66.4581 | 66.4673 | 66.4169 | -0.11444 | -0.064087 | 0.050354 | 4.01 | -0.041199 | -0.027466 | 0.073242 | 0.086975 | -0.073243 | -0.064087 | -104.3976 | 123.056 | 123.0148 | 123.0652 | 123.0881 | 123.1384 | 4.1245 | 123.0103 | 123.1293 | 18.5211 | 122.8958 | 122.8546 | 122.7814 | 122.7814 | -122.9599 | -122.9187 | 122.8958 | 18.4479 | 22.3526 | 123.0789
587.0312 | 123.1338 | -56.3736 | 66.5817 | 0.19033 | -0.012543 | -0.16066 | 0.093962 | -0.015292 | -0.0020407 | -0.0061228 | -0.015915 | 0.14874 | 0.082881 | -0.047356 | 0.067333 | 0.12527 | 0.0045054 | -34.3597 | 66.481 | -56.4926 | 66.7511 | -52.0386 | -56.1172 | -56.2866 | 66.6092 | 66.5176 | -56.4056 | -37.4222 | 66.6687 | 66.5771 | 66.6412 | -0.11902 | -0.10071 | 0.16937 | 4.335 | 0.086975 | 0.25635 | 0.20599 | 0.37537 | -0.032044 | -0.064087 | -104.0039 | 123.0423 | 123.0148 | 122.9507 | 123.0469 | 122.9828 | 4.454 | 123.2437 | 123.0743 | 18.9835 | 122.9736 | 122.9233 | 122.8546 | 122.8912 | -123.0743 | -122.9874 | 123.1247 | 18.9514 | 22.0139 | 122.9828
587.9688 | 123.056 | -55.9708 | 67.0029 | 0.12929 | 0.019501 | -0.14784 | 0.10678 | 0.0028664 | -0.013791 | 0.0024222 | -0.12273 | 0.13593 | 0.10638 | -0.02279 | 0.067333 | 0.12527 | -0.0072446 | -34.4421 | 66.9022 | -56.044 | 67.1906 | -51.6129 | -55.7007 | -55.8151 | 66.9662 | 66.9525 | -55.9937 | -36.2823 | 66.9754 | 66.9388 | 67.0349 | -0.073242 | -0.10071 | 0.18768 | 4.3579 | 0.15564 | 0.27008 | 0.22888 | 0.34332 | -0.022888 | -0.050354 | -103.2852 | 122.9462 | 123.0057 | 122.9095 | 123.0286 | 122.9324 | 4.4312 | 123.2346 | 122.9691 | 19.7113 | 122.9462 | 122.9462 | 122.8729 | 122.9233 | -123.0469 | -122.9965 | 123.1613 | 19.6884 | 21.5286 | 122.937
589.0312 | 123.1018 | -50.3494 | 72.6013 | 0.15981 | 0.0098883 | -0.14891 | 0.098234 | 0.0039344 | 0.012912 | -0.012532 | 0.014603 | 0.16263 | 0.13095 | 0.027412 | 0.10045 | 0.024863 | 0.00023236 | -29.0726 | 72.5281 | -50.4272 | 72.7753 | -46.2387 | -50.1114 | -50.2808 | -0.37537 | -0.32044 | -0.42114 | -0.3891 | -0.37537 | -0.37079 | -0.37537 | -0.07782 | -0.073242 | 0.17395 | 4.1107 | 0.068664 | 0.23804 | 0.14648 | 0.31586 | 49.9283 | -72.9218 | -72.9904 | 49.9741 | 49.9741 | 49.9786 | 0.045777 | 0.050354 | 4.1885 | 123.2025 | 0.045777 | 0.032044 | 122.9553 | 0.10071 | 122.8775 | 50.029 | -123.0286 | -73.0225 | 123.1247 | 49.9603 | 21.2769 | 49.9741
589.9531 | 123.0652 | -49.4888 | 73.407 | 0.098773 | 0.0098883 | -0.15318 | 0.089689 | -0.00033857 | -0.0052457 | -0.0082598 | 0.41133 | 0.15302 | 0.14163 | -0.031334 | 0.095104 | 0.018454 | -0.00083564 | -28.2761 | 73.32 | -49.5621 | 73.4344 | -45.3323 | -49.4614 | -49.5621 | -0.36163 | -0.39368 | -0.45319 | -0.35248 | -0.35248 | -0.022888 | -0.21515 | -0.073242 | -0.086975 | 0.027466 | 4.1565 | -0.073242 | 0.027466 | 0 | 0.10071 | 49.0356 | -73.8007 | -73.7595 | 49.1364 | 49.2737 | 49.4659 | 0.23804 | 0.4303 | 4.2297 | 122.9965 | 0.10071 | 0.10071 | 122.8821 | 0.059509 | 122.8088 | 49.0952 | -122.9691 | -73.8602 | 122.9233 | 49.1364 | 21.2128 | 49.1272
591.0312 | 123.1293 | -48.1384 | 74.8444 | 0.34291 | 0.00027529 | -0.15852 | 0.092894 | 0.0039344 | -0.014859 | 0.0066942 | 0.060379 | 0.17224 | 0.14804 | -0.037743 | 0.086559 | 0.030203 | -0.0093806 | -25.914 | 74.7894 | -48.2117 | 74.9863 | -43.6249 | -47.8638 | -48.0652 | -0.59967 | -0.47607 | -0.61798 | -0.54474 | -0.58136 | -0.52185 | -0.55389 | -0.073242 | -0.054931 | 0.14191 | 4.5135 | 0.073242 | 0.27466 | 0.14648 | 0.3479 | 47.5204 | -75.3204 | -75.3891 | 47.5571 | 47.5845 | 47.6166 | 0.064087 | 0.09613 | 4.5868 | 123.1979 | 0.036621 | 0.073242 | 123.0011 | 0.14191 | 122.9279 | 47.6624 | -123.056 | -75.4623 | 123.1247 | 47.5937 | 22.2244 | 47.5388
591.9531 | 123.1705 | -47.4609 | 75.4944 | 0.15981 | 0.0056153 | -0.15211 | 0.10678 | -0.0088836 | -0.024472 | 0.0098982 | 0.36555 | 0.1669 | 0.13842 | -0.056969 | 0.10472 | 0.029135 | -0.0029716 | -25.7172 | 75.4303 | -47.5113 | 75.5219 | -42.9703 | -47.2916 | -47.4655 | -0.37537 | -0.37537 | -0.44403 | -0.35248 | -0.30212 | -0.30212 | -0.32959 | -0.050355 | -0.064087 | 0.027466 | 4.4907 | -0.004578 | 0.16937 | 0.045777 | 0.21973 | 47.0169 | -75.8698 | -75.8469 | 47.1588 | 47.1313 | 47.1588 | 0.11444 | 0.14191 | 4.541 | 123.0331 | 0.14191 | 0.091553 | 122.9416 | 0.068665 | 122.8912 | 47.0856 | -123.0057 | -75.9384 | 122.9828 | 47.1085 | 21.7438 | 47.0856
593.0312 | 123.1476 | -47.1634 | 75.7645 | -0.053815 | 0.0088203 | -0.16706 | 0.089689 | -0.013156 | 0.015048 | 0.0034902 | 0.21297 | 0.16263 | 0.15017 | -0.04522 | 0.0919 | 0.017386 | 0.0023694 | -25.4745 | 75.6592 | -47.2458 | 75.8469 | -42.8101 | -46.962 | -47.1451 | -0.42114 | -0.37079 | -0.44861 | -0.37537 | -0.40283 | -0.33875 | -0.3891 | -0.082398 | -0.10528 | 0.082398 | 4.3533 | 0.01831 | 0.20142 | 0.10071 | 0.28381 | 46.7148 | -76.1353 | -76.1398 | 46.7606 | 46.7743 | 46.8246 | 0.059509 | 0.10986 | 4.4357 | 123.0927 | 0.045776 | 0.073242 | 122.905 | 0.077819 | 122.8226 | 46.7926 | -123.0103 | -76.2131 | 123.0103 | 46.788 | 21.6888 | 46.7422
593.9531 | 123.23 | -47.1634 | 75.7828 | 0.068255 | -0.00079271 | -0.1425 | 0.090757 | -0.0014066 | 0.0075723 | -0.0018508 | 0.3503 | 0.15408 | 0.12133 | -0.036675 | 0.0919 | 0.0045682 | 0.0087774 | -25.5844 | 75.6363 | -47.2641 | 75.7828 | -42.9611 | -46.9528 | -47.1909 | -0.3479 | -0.34332 | -0.39368 | -0.32959 | -0.2655 | -0.2243 | -0.28839 | -0.10071 | -0.14648 | 0 | 4.2023 | -0.027466 | 0.21057 | 0.073242 | 0.31128 | 46.7697 | -76.1261 | -76.1124 | 46.8979 | 46.875 | 46.9391 | 0.10529 | 0.16937 | 4.303 | 123.0469 | 0.12817 | 0.064087 | 122.9004 | 0.050354 | 122.7997 | 46.8201 | -123.0469 | -76.1765 | 122.9462 | 46.8338 | 21.579 | 46.8155
595.0312 | 123.1338 | -46.8842 | 76.1215 | 0.068255 | 0.0056153 | -0.16386 | 0.10144 | -0.0014066 | -0.031949 | -0.0050548 | 0.014603 | 0.15942 | 0.14163 | -0.030266 | 0.094036 | 0.013113 | -0.010449 | -25.1404 | 76.0025 | -46.9803 | 76.1902 | -42.6224 | -46.5591 | -46.7743 | -0.31586 | -0.23804 | -0.35706 | -0.31128 | -0.31128 | -0.29297 | -0.31128 | -0.096131 | -0.11902 | 0.068665 | 4.2618 | 0.10986 | 0.32501 | 0.20599 | 0.42114 | 46.5271 | -76.3596 | -76.4328 | 46.5729 | 46.5729 | 46.5912 | 0.045777 | 0.064087 | 4.3579 | 123.1705 | 0.045777 | 0.045777 | 122.9828 | 0.11902 | 122.8867 | 46.6461 | -123.1018 | -76.4786 | 123.0743 | 46.5729 | 21.7438 | 46.5683
595.9531 | 123.2574 | -46.637 | 76.3138 | 0.037738 | 0.0077523 | -0.17027 | 0.085417 | -0.0056786 | -0.0084497 | -0.0050548 | 0.44185 | 0.16049 | 0.13415 | -0.012108 | 0.10685 | 0.0077732 | -0.014721 | -24.4217 | 76.2314 | -46.6965 | 76.3458 | -42.5491 | -46.3852 | -46.6553 | -0.19226 | -0.24261 | -0.29297 | -0.18768 | -0.09613 | -0.14191 | -0.15564 | -0.059509 | -0.082398 | 0.032043 | 4.0878 | -0.01831 | 0.25177 | 0.041199 | 0.31128 | 46.344 | -76.5564 | -76.5015 | 46.5408 | 46.4813 | 46.4951 | 0.13733 | 0.15106 | 4.1473 | 123.0423 | 0.19684 | 0.10529 | 122.9279 | 0.050354 | 122.8683 | 46.3943 | -123.0103 | -76.6068 | 122.9828 | 46.4493 | 22.2153 | 46.4447
596.9531 | 123.2117 | -45.5887 | 77.3438 | -0.038556 | 0.01416 | -0.17134 | 0.10144 | -0.0035426 | -0.026608 | -0.014668 | 0.274 | 0.15408 | 0.15551 | -0.016381 | 0.098309 | 0.019522 | -0.0072446 | -23.7579 | 77.2202 | -45.7077 | 77.4353 | -42.4164 | -45.3003 | -45.5566 | -0.2243 | -0.2243 | -0.3067 | -0.21515 | -0.20142 | -0.14191 | -0.21515 | -0.11902 | -0.1236 | 0.091553 | 3.1723 | 0.032043 | 0.28839 | 0.15106 | 0.40741 | 45.282 | -77.5681 | -77.5589 | 45.3873 | 45.3735 | 45.4468 | 0.091553 | 0.16479 | 3.2913 | 123.143 | 0.10529 | 0.091553 | 122.9279 | 0.082398 | 122.8088 | 45.3644 | -123.0515 | -77.6505 | 123.024 | 45.3735 | 21.8307 | 45.3644
598.0312 | 123.2346 | -45.488 | 77.4399 | -0.0080386 | 0.0045473 | -0.15745 | 0.10464 | 0.017819 | -0.016995 | 0.0024222 | 0.12141 | 0.1637 | 0.13842 | -0.019585 | 0.10258 | 0.02059 | 0.0098454 | -23.3414 | 77.3392 | -45.6116 | 77.5406 | -41.9724 | -45.1904 | -45.4926 | -0.25635 | -0.19226 | -0.24261 | -0.17853 | -0.16479 | -0.16937 | -0.16022 | -0.1236 | -0.10071 | 0.10071 | 3.5156 | -0.004578 | 0.29755 | 0.11902 | 0.42114 | 45.2454 | -77.6321 | -77.6184 | 45.3232 | 45.3278 | 45.3186 | 0.082398 | 0.073242 | 3.6392 | 123.1522 | 0.07782 | 0.064087 | 122.9507 | 0.050354 | 122.8271 | 45.2957 | -123.0515 | -77.6825 | 123.0286 | 45.3094 | 22.1466 | 45.2316
598.9531 | 123.2162 | -44.957 | 77.9755 | 0.098773 | -0.0029297 | -0.17668 | 0.096098 | -0.0046106 | -0.018063 | -0.0029188 | 0.24348 | 0.15729 | 0.15231 | -0.047356 | 0.099377 | 0.02059 | 0.014118 | -22.1008 | 77.9114 | -45.0119 | 77.9938 | -41.7068 | -44.7556 | -44.9341 | -0.12817 | -0.18768 | -0.24261 | -0.12817 | -0.10071 | -0.086975 | -0.15564 | -0.054932 | -0.064087 | 0.01831 | 3.2501 | 0.022888 | 0.20142 | 0.07782 | 0.25635 | 44.7144 | -78.1631 | -78.1036 | 44.8563 | 44.8013 | 44.87 | 0.086975 | 0.15564 | 3.3051 | 123.0057 | 0.14191 | 0.11444 | 122.9233 | 0.054932 | 122.8683 | 44.7693 | -122.9874 | -78.2181 | 122.9507 | 44.8288 | 22.8561 | 44.8288
600.0312 | 123.056 | -45.845 | 77.1515 | 0.068255 | 0.0088203 | -0.18202 | 0.09503 | 0.01141 | 0.012912 | 0.0066942 | 0.13667 | 0.17117 | 0.15872 | -0.036675 | 0.10472 | 0.021658 | -0.0061756 | -22.8012 | 77.0782 | -45.9503 | 77.3254 | -42.6544 | -45.4102 | -45.6665 | -0.2243 | -0.07782 | -0.19684 | -0.22888 | 0.11444 | 0.068665 | -0.22888 | -0.10528 | -0.073242 | 0.17395 | 3.1906 | 0.17853 | 0.43488 | 0.28381 | 0.54016 | 45.6482 | -77.2293 | -77.3804 | 45.9595 | 45.6162 | 45.9137 | -0.032044 | 0.2655 | 3.2959 | 123.2758 | 0.31128 | -0.032044 | 123.0286 | 0.11902 | 122.9233 | 45.7672 | -123.1018 | -77.3483 | 123.1705 | 45.6162 | 23.0438 | 45.6207
600.9531 | 123.1384 | -47.1542 | 75.8423 | 0.022479 | 0.0045473 | -0.1692 | 0.10785 | 0.021024 | -0.0031087 | -0.0071918 | 0.31978 | 0.15515 | 0.14056 | -0.00035879 | 0.098309 | 0.0067052 | -0.0083126 | -23.7076 | 75.6592 | -47.2504 | 75.8423 | -44.1742 | -46.8338 | -47.0215 | -0.086975 | -0.064087 | -0.13733 | -0.10071 | -0.082397 | -0.073242 | -0.091553 | -0.09613 | -0.1831 | 0 | 2.98 | 0.13275 | 0.32043 | 0.22888 | 0.41656 | 47.0169 | -75.9064 | -75.943 | 47.0718 | 47.0627 | 47.081 | 0.045776 | 0.064087 | 3.0762 | 123.0927 | 0.054932 | 0.036621 | 122.9095 | 0.073242 | 122.8134 | 47.0901 | -123.0927 | -75.9796 | 122.9965 | 47.0535 | 23.4467 | 47.0673
602.0312 | 123.1613 | -47.1909 | 75.8148 | 0.11403 | -0.011475 | -0.19377 | 0.10251 | 0.012479 | 0.0032993 | -0.0050548 | 0.090897 | 0.16156 | 0.14376 | -0.00035879 | 0.095104 | 0.021658 | -0.0061756 | -22.0367 | 75.7553 | -47.2778 | 76.0162 | -44.1513 | -46.7743 | -46.9254 | -0.16937 | -0.032043 | -0.15106 | -0.14648 | -0.1236 | -0.10529 | -0.12817 | -0.086975 | -0.059509 | 0.20142 | 3.0396 | 0.2655 | 0.41656 | 0.35248 | 0.50354 | 47.0398 | -75.8469 | -75.9613 | 47.0673 | 47.0627 | 47.0856 | 0.022888 | 0.045776 | 3.1265 | 123.2941 | 0.027466 | 0.004578 | 123.0331 | 0.11902 | 122.9462 | 47.1588 | -123.0927 | -75.9659 | 123.2071 | 47.0444 | 25.1541 | 47.0215
602.9531 | 123.2849 | -46.9208 | 76.0345 | 0.068255 | 0.0013433 | -0.17027 | 0.089689 | 0.018887 | -0.028744 | -0.012532 | 0.22823 | 0.16156 | 0.15017 | -0.029198 | 0.11006 | 0.019522 | -0.0061756 | -19.5923 | 75.9476 | -47.0032 | 76.0574 | -44.1467 | -46.6049 | -46.7789 | -0.041199 | -0.086975 | -0.14191 | -0.036621 | -0.009155 | 0.009155 | -0.018311 | -0.082398 | -0.086975 | 0.022888 | 2.774 | 0.14191 | 0.31586 | 0.2243 | 0.39825 | 46.7789 | -76.1215 | -76.0712 | 46.9116 | 46.9025 | 46.9299 | 0.1236 | 0.15106 | 2.8564 | 123.0606 | 0.13275 | 0.10529 | 122.9507 | 0.054932 | 122.8683 | 46.8338 | -123.0377 | -76.1765 | 122.9782 | 46.8842 | 27.3285 | 46.8796
604.0312 | 123.1796 | -47.9004 | 75.0687 | 0.12929 | 0.0066833 | -0.1724 | 0.10892 | -0.0035426 | -0.016995 | -0.0061228 | -0.07695 | 0.16156 | 0.12667 | -0.021721 | 0.095104 | 0.029135 | -0.00083564 | -19.3085 | 74.9451 | -48.0423 | 75.1602 | -44.9753 | -47.5204 | -47.6532 | -0.14191 | -0.073242 | -0.16937 | -0.10071 | -0.11444 | -0.12817 | -0.14648 | -0.14191 | -0.1236 | 0.091552 | 2.9251 | 0.24719 | 0.37994 | 0.3891 | 0.52185 | 47.731 | -75.1419 | -75.1694 | 47.7859 | 47.7539 | 47.7722 | 0.022889 | 0.041199 | 3.067 | 123.2025 | 0.054932 | 0.068665 | 122.9874 | 0.096131 | 122.8455 | 47.8271 | -123.111 | -75.238 | 123.0606 | 47.7997 | 28.5919 | 47.7585
604.9531 | 123.1384 | -48.6282 | 74.4232 | 0.11403 | -0.00079271 | -0.17668 | 0.10998 | 0.0039344 | -0.015927 | -0.0071918 | 0.22823 | 0.16476 | 0.15658 | -0.052697 | 0.10151 | 0.023794 | -0.015789 | -19.075 | 74.2676 | -48.6649 | 74.4736 | -45.6482 | -48.1613 | -48.2941 | -0.15106 | -0.045776 | -0.14191 | -0.13275 | -0.1236 | -0.1236 | -0.086975 | -0.036621 | -0.15564 | 0.050354 | 2.98 | 0.33417 | 0.46692 | 0.37079 | 0.50354 | 48.4863 | -74.469 | -74.556 | 48.5046 | 48.5413 | 48.5046 | 0.054932 | 0.018311 | 3.0167 | 123.1384 | 0.018311 | 0.009156 | 122.9324 | 0.096131 | 122.8958 | 48.5825 | -123.0881 | -74.5651 | 123.1018 | 48.4955 | 29.5532 | 48.4772
606.0312 | 123.1659 | -48.999 | 74.0204 | 0.098773 | 0.00027529 | -0.18309 | 0.10144 | 0.0092744 | -0.0041777 | -0.0082598 | 0.075638 | 0.15729 | 0.14697 | -0.0067678 | 0.10472 | 0.016318 | 0.0023694 | -18.3334 | 73.9426 | -49.0631 | 74.1623 | -46.0052 | -48.4589 | -48.6008 | -0.16022 | -0.013733 | -0.15106 | -0.10071 | -0.12817 | -0.07782 | -0.082397 | -0.064087 | -0.07782 | 0.14191 | 2.9938 | 0.39825 | 0.54016 | 0.46234 | 0.60425 | 48.848 | -74.0341 | -74.1211 | 48.8708 | 48.9166 | 48.9212 | 0.068665 | 0.073242 | 3.0579 | 123.2254 | 0.022888 | 0.050354 | 123.0057 | 0.13733 | 122.9416 | 48.9853 | -123.0835 | -74.1714 | 123.1613 | 48.8983 | 30.6656 | 48.8388
606.9531 | 123.2666 | -48.7885 | 74.1119 | 0.0072204 | 0.0098883 | -0.18522 | 0.10358 | -0.0014066 | -0.013791 | -0.0039868 | 0.38081 | 0.15836 | 0.14697 | -0.043084 | 0.10472 | 0.019522 | 0.0023694 | -16.8457 | 74.0112 | -48.9029 | 74.1165 | -46.051 | -48.4177 | -48.6374 | 0.022888 | -0.036621 | -0.10529 | -0.013733 | 0.054932 | 0.009155 | 0 | -0.11444 | -0.10071 | 0.004578 | 2.7374 | 0.15106 | 0.37079 | 0.2655 | 0.48523 | 48.6832 | -74.1486 | -74.1257 | 48.8434 | 48.7885 | 48.7976 | 0.10529 | 0.11444 | 2.8519 | 123.0194 | 0.16022 | 0.091553 | 122.9141 | 0.068665 | 122.7997 | 48.7518 | -123.0148 | -74.2172 | 122.905 | 48.7747 | 31.9427 | 48.8113
608.0312 | 123.0972 | -49.3927 | 73.6313 | 0.022479 | 0.0056153 | -0.17774 | 0.098234 | 0.0039344 | -0.0052457 | 0.014171 | -0.1685 | 0.16049 | 0.12774 | -0.019585 | 0.095104 | 0.031271 | -0.00083564 | -15.7791 | 73.5306 | -49.4843 | 73.7778 | -46.4218 | -48.8205 | -48.9395 | -0.20142 | -0.013733 | -0.14648 | -0.15106 | -0.15106 | -0.15106 | -0.10986 | -0.091553 | -0.10071 | 0.14648 | 2.9709 | 0.45319 | 0.5722 | 0.54474 | 0.66376 | 49.2462 | -73.645 | -73.7823 | 49.2416 | 49.2828 | 49.2416 | 0.036621 | -0.004578 | 3.0624 | 123.262 | -0.004578 | -0.004578 | 123.0148 | 0.13275 | 122.9233 | 49.379 | -123.1155 | -73.7778 | 123.1705 | 49.2416 | 33.6136 | 49.1913
608.9531 | 123.2025 | -48.8342 | 74.1486 | 0.037738 | 0.0056153 | -0.17668 | 0.09503 | -0.00033857 | 0.012912 | -0.0039868 | 0.19771 | 0.16797 | 0.15444 | -0.049492 | 0.10365 | 0.025931 | 0.0098454 | -14.3967 | 74.0158 | -48.9258 | 74.1669 | -45.9824 | -48.4131 | -48.5138 | -0.059509 | 0 | -0.054932 | -0.036621 | 0.032043 | 0.018311 | 0.009155 | -0.091552 | -0.13275 | 0.01831 | 2.8519 | 0.32044 | 0.42114 | 0.41199 | 0.5127 | 48.7793 | -74.1486 | -74.1852 | 48.8663 | 48.8434 | 48.8525 | 0.064087 | 0.073243 | 2.9434 | 123.0927 | 0.086975 | 0.018311 | 122.9416 | 0.054932 | 122.85 | 48.8342 | -123.0743 | -74.2035 | 123.0011 | 48.7976 | 34.4376 | 48.7747
609.9531 | 123.1659 | -48.88 | 74.1394 | 0.14455 | 0.016296 | -0.1724 | 0.10144 | 0.0060704 | -0.0095177 | 0.0013532 | -0.046432 | 0.17865 | 0.12988 | -0.020653 | 0.10792 | 0.021658 | 0.016254 | -14.0121 | 74.0479 | -48.9807 | 74.2401 | -45.3415 | -48.4131 | -48.3398 | -0.050354 | 0.032043 | -0.073242 | -0.018311 | -0.027466 | -0.004578 | -0.032043 | -0.10071 | -0.091552 | 0.10071 | 3.5385 | 0.54016 | 0.46692 | 0.64087 | 0.56763 | 48.8068 | -74.1074 | -74.1577 | 48.8525 | 48.848 | 48.8754 | 0.041199 | 0.068664 | 3.6392 | 123.2208 | 0.045776 | 0.054931 | 123.0286 | 0.10529 | 122.9279 | 48.912 | -123.1201 | -74.2126 | 123.1201 | 48.8617 | 34.8679 | 48.8297
611.0312 | 123.1796 | -87.0438 | 35.907 | 0.052997 | 0.03125 | -0.1724 | 0.10571 | -0.0046106 | -0.014859 | 0.013103 | -0.07695 | 0.17331 | 0.13095 | -0.043084 | 0.094036 | 0.026999 | 0.0034374 | 32.6981 | 36.2732 | -86.8103 | 36.3922 | -84.0912 | -85.4233 | -92.8711 | -0.20142 | -0.054932 | -0.16479 | -0.15106 | -0.17395 | -0.14648 | -0.12817 | 0.23346 | 0.36621 | 0.48523 | 2.9526 | -5.8273 | 1.6205 | -6.0608 | 1.387 | 86.879 | -35.9619 | -36.058 | 86.8698 | 86.9156 | 86.8973 | 0.036621 | 0.018311 | 2.7191 | 123.2025 | -0.009155 | 0.013733 | 123.0835 | 0.10986 | 123.317 | 86.9888 | -122.7173 | -36.0718 | 123.436 | 86.8927 | 119.7418 | 86.8423
611.9531 | 123.2208 | -88.9343 | 33.9111 | -0.023297 | 0.021637 | -0.17027 | 0.15057 | -0.0024746 | -0.010586 | 0.073985 | 0.33504 | 0.16049 | 0.1192 | -0.033471 | 0.10685 | 0.017386 | 0.0045054 | 30.5695 | 33.7646 | -89.0671 | 34.3781 | -84.8969 | -87.822 | -87.1353 | 0.059509 | -0.059509 | -0.086975 | 0.018311 | -0.022888 | 0.15564 | -0.018311 | -0.13275 | -0.14648 | 0.46692 | 4.0375 | 1.799 | 1.1124 | 1.9318 | 1.2451 | 88.8474 | -33.9706 | -33.8928 | 88.9114 | 88.916 | 89.09 | 0.068664 | 0.24261 | 4.1702 | 123.4451 | 0.064087 | 0.10529 | 122.8317 | 0.027466 | 122.699 | 88.8748 | -122.9782 | -33.9981 | 123.3124 | 88.9526 | 119.5038 | 88.9938
613.0312 | 123.2574 | -98.9319 | 24.0005 | -0.16063 | 0.028046 | -0.52488 | 0.27447 | -0.0078156 | -0.015927 | 0.093211 | 0.39607 | 0.16156 | 0.14056 | -0.048424 | 0.098309 | 0.014181 | -0.0072446 | 21.9635 | 23.8541 | -99.0646 | 23.8312 | 23.6847 | 12.7899 | 23.8632 | 0.064087 | -0.004578 | -0.018311 | 0.10529 | 0.086975 | 0.10529 | 0.086975 | -0.13275 | -0.14648 | -0.16937 | 122.6166 | 122.7951 | 111.7218 | 122.9279 | 111.8546 | 98.9136 | -24.0051 | -23.8953 | 99.0189 | 99.0189 | 99.0372 | 0.10529 | 0.1236 | 122.7493 | 122.8958 | 0.10529 | 0.1236 | 122.9187 | 0.013733 | 122.7859 | 98.9273 | -123.0652 | -24.0189 | 122.7631 | 99.0372 | 120.8954 | 98.996
613.9531 | 123.2391 | -99.527 | 23.4421 | -0.099591 | 0.017365 | -0.54731 | 0.267 | 0.00072943 | -0.013791 | 0.10069 | 0.38081 | 0.16476 | 0.13415 | -0.0099718 | 0.11647 | 0.029135 | -0.012585 | 21.3959 | 23.2681 | -99.6506 | 23.4146 | 23.3139 | 13.0234 | 23.3459 | 0.054932 | 0.059509 | 0.022888 | 0.11444 | 0.091553 | 0.15106 | 0.10071 | -0.1236 | -0.17395 | -0.027466 | 122.8409 | 122.8729 | 112.5504 | 122.9965 | 112.674 | 99.5499 | -23.3826 | -23.3276 | 99.6185 | 99.6277 | 99.678 | 0.07782 | 0.12817 | 122.9645 | 123.0652 | 0.068665 | 0.091553 | 122.9187 | 0.036621 | 122.7951 | 99.5865 | -123.0927 | -23.4192 | 122.9416 | 99.6414 | 120.9229 | 99.5819
615.0312 | 123.1705 | -99.5544 | 23.4238 | 0.022479 | 0.017365 | -0.5612 | 0.27981 | -0.0067466 | -0.0020407 | 0.11564 | 0.15193 | 0.17011 | 0.14163 | -0.036675 | 0.085491 | 0.028067 | -0.015789 | 21.1304 | 23.291 | -99.6872 | 23.4467 | 23.3231 | 13.0692 | 23.3414 | 0.022888 | 0.082397 | -0.009155 | 0.064087 | 0.013733 | 0.068665 | 0.068665 | -0.13275 | -0.13275 | 0.022888 | 122.8775 | 122.8958 | 112.6236 | 123.0286 | 112.7563 | 99.5453 | -23.3414 | -23.3597 | 99.5682 | 99.6231 | 99.6231 | 0.07782 | 0.07782 | 123.0103 | 123.1338 | 0.022888 | 0.073242 | 122.9782 | 0.091552 | 122.8455 | 99.6368 | -123.111 | -23.4329 | 123.0011 | 99.6185 | 120.6848 | 99.5773
615.9531 | 123.2437 | -99.7925 | 23.1445 | -0.0080386 | 0.029114 | -0.58363 | 0.267 | 0.0050024 | -0.026608 | 0.1071 | 0.39607 | 0.16476 | 0.1256 | -0.012108 | 0.10899 | 0.013113 | 0.0013004 | 20.8328 | 23.0301 | -99.8383 | 23.0713 | 23.0072 | 12.355 | 23.0392 | 0.13733 | 0.064087 | 0.022888 | 0.1236 | 0.14648 | 0.16479 | 0.12817 | -0.045777 | -0.11444 | -0.073242 | 122.7997 | 122.8317 | 112.1475 | 122.8775 | 112.1933 | 99.8154 | -23.0804 | -23.0209 | 99.939 | 99.9207 | 99.9573 | 0.10529 | 0.14191 | 122.8455 | 122.9095 | 0.1236 | 0.10071 | 122.8683 | 0.041199 | 122.8226 | 99.8566 | -122.9828 | -23.1216 | 122.8638 | 99.9161 | 120.6253 | 99.9298
617.0312 | 122.6486 | -51.5625 | 71.5027 | -0.11485 | 0.045136 | -0.55906 | 0.2702 | 0.0082064 | -0.016995 | 0.1103 | 0.10615 | 0.16263 | 0.12988 | -0.032403 | 0.2628 | 0.024863 | -0.0019036 | 71.0541 | 71.3333 | -51.622 | 71.5942 | 71.3699 | 56.8222 | 71.4752 | 0.11902 | 0.14191 | 0.054932 | 0.21973 | 0.16022 | 0.09613 | 0.1236 | -0.059509 | -0.16937 | 0.091552 | 122.9324 | 123.0377 | 108.3847 | 123.0972 | 108.4442 | 51.6174 | -71.3608 | -71.283 | 51.7227 | 51.6861 | 51.6586 | 0.068664 | 0.041198 | 122.9919 | 123.2162 | 0.10528 | 0.16479 | 122.9553 | 0.086975 | 122.8958 | 51.7044 | -123.1247 | -71.4478 | 123.1567 | 51.7822 | 122.6166 | 51.6815
617.9688 | 123.1476 | -97.0367 | 25.9048 | -0.14537 | 0.012024 | -0.5644 | 0.27768 | -0.00033857 | -0.012723 | 0.093211 | 0.10615 | 0.1669 | 0.14483 | -0.0035628 | 0.10792 | 0.030203 | -0.012585 | 25.827 | 25.2045 | -97.3618 | 26.152 | 26.0651 | 26.5961 | 27.0447 | -0.045776 | 0.086975 | 0 | -0.022888 | -0.018311 | -0.050354 | 0.009155 | -0.32501 | -0.70038 | 0.24719 | 123.1018 | 124.0814 | 123.6328 | 124.4064 | 123.9578 | 97.0367 | -25.8179 | -25.9277 | 97.0184 | 97.0459 | 96.9864 | 0.009155 | -0.050354 | 123.4268 | 123.5138 | -0.018311 | -0.022888 | 122.5662 | 0.086975 | 122.2412 | 97.1237 | -123.2666 | -25.9048 | 123.1888 | 97.0139 | 122.8638 | 96.991
619.0312 | 123.1613 | -98.5657 | 24.3805 | -0.038556 | 0.020569 | -0.58576 | 0.27127 | 0.0028664 | -0.013791 | 0.094279 | 0.48762 | 0.17438 | 0.14804 | -0.019585 | 0.10579 | 0.014181 | 0.0013004 | 24.2386 | 24.2981 | -98.6893 | 24.472 | 24.408 | 24.3851 | 24.4171 | -0.22888 | 0.15564 | 0.027466 | 0 | 0.018311 | 0.045776 | 0.013733 | -0.1236 | -0.082397 | 0.091553 | 122.9736 | 122.9828 | 122.9507 | 123.1064 | 123.0743 | 98.5931 | -24.2249 | -24.3805 | 98.584 | 98.5794 | 98.6115 | -0.013733 | 0.01831 | 123.0972 | 123.1613 | -0.009155 | -0.027466 | 122.9874 | 0.12817 | 122.8638 | 98.7213 | -123.0698 | -24.353 | 123.0377 | 98.5657 | 122.8043 | 98.3368
619.9531 | 123.262 | -98.7213 | 24.2111 | -0.099591 | 0.018433 | -0.59645 | 0.27127 | -0.0035426 | -0.026608 | 0.078258 | 0.38081 | 0.14981 | 0.13522 | -0.0089038 | 0.10365 | 0.0077732 | 0.0013004 | 24.2203 | 24.0784 | -98.8083 | 24.1287 | 24.0692 | 24.1104 | 24.0692 | 0.11902 | 0.068665 | 0.022888 | 0.091553 | 0.16022 | 0.15106 | 0.12817 | -0.086976 | -0.13275 | -0.082398 | 122.7905 | 122.7905 | 122.8317 | 122.8775 | 122.9187 | 98.7442 | -24.1425 | -24.1196 | 98.8815 | 98.8495 | 98.8724 | 0.10529 | 0.12817 | 122.8775 | 122.937 | 0.13733 | 0.068665 | 122.8867 | 0.045777 | 122.7997 | 98.79 | -123.0194 | -24.1882 | 122.85 | 98.8129 | 122.9416 | 98.8403
621.0312 | 123.1064 | -75.3983 | 47.644 | -0.038556 | 0.022705 | -0.58576 | 0.27127 | 0.014615 | -0.0041777 | 0.094279 | -0.1685 | 0.15729 | 0.13949 | -0.02813 | 0.10579 | 0.026999 | -0.0072446 | 47.58 | 47.5342 | -75.4257 | 47.6852 | 47.6715 | 47.5891 | 47.6807 | 0.013733 | 0.10529 | 0.004578 | 0.082397 | 0.054932 | 0.082397 | 0.07782 | -0.027466 | -0.10986 | 0.041199 | 123.0698 | 123.0789 | 122.9874 | 123.1064 | 123.0148 | 75.4028 | -47.5388 | -47.5616 | 75.4532 | 75.4761 | 75.4807 | 0.073242 | 0.077819 | 123.0972 | 123.111 | 0.050354 | 0.077819 | 122.9599 | 0.10071 | 122.9324 | 75.5035 | -123.0698 | -47.6395 | 123.0835 | 75.4807 | 122.9782 | 75.412
621.9531 | 123.1796 | -75.4211 | 47.5571 | -0.11485 | 0.050476 | -0.61781 | 0.23175 | 0.01141 | -0.035153 | 0.10176 | 0.28926 | 0.16797 | 0.13415 | -0.031334 | 0.10685 | 0.028067 | 0.0023694 | 47.6028 | 47.4243 | -75.4486 | 47.6303 | 47.4106 | 47.5571 | 47.4747 | 0.050354 | 0.07782 | 0.009155 | 0.091553 | 0.13733 | 0.11902 | 0.10986 | -0.027465 | -0.13275 | 0.073242 | 122.8317 | 122.8958 | 122.9782 | 122.9233 | 123.0057 | 75.4303 | -47.4792 | -47.4655 | 75.5585 | 75.531 | 75.5402 | 0.10071 | 0.10986 | 122.8592 | 123.0789 | 0.12817 | 0.082398 | 122.8729 | 0.068665 | 122.8455 | 75.499 | -123.0057 | -47.5479 | 123.0515 | 75.5127 | 123.024 | 75.4715
622.9688 | 123.111 | -75.531 | 47.4426 | -0.19114 | 0.12631 | -0.62315 | 0.1698 | -0.0067466 | -0.022336 | 0.10496 | 0.36555 | 0.16049 | 0.12454 | 0.013526 | 0.10151 | 0.024863 | -0.00083564 | 47.3969 | 47.2961 | -75.6042 | 47.4838 | 47.3877 | 47.4106 | 47.4426 | 0.059509 | 0.10071 | 0.004578 | 0.018311 | 0.059509 | 0.059509 | 0.032043 | -0.073242 | -0.14648 | 0.041199 | 122.9187 | 122.9736 | 122.9416 | 123.0469 | 123.0148 | 75.5356 | -47.3419 | -47.4243 | 75.5905 | 75.563 | 75.5905 | 0.027465 | 0.054931 | 122.9919 | 123.0881 | 0.054931 | 0.013733 | 122.9004 | 0.09613 | 122.8271 | 75.6317 | -123.0469 | -47.438 | 123.0148 | 75.5493 | 122.9279 | 75.5905
624.0312 | 123.0835 | -41.4688 | 81.5094 | -0.11485 | 0.14768 | -0.67549 | 0.20932 | 0.0028664 | 0.01398 | -0.0082598 | -0.00065608 | 0.17011 | 0.14376 | 0.018867 | 0.10365 | 0.012045 | 0.0045054 | -41.423 | -9.0408 | -41.5695 | -41.4505 | -41.3452 | -41.4551 | -41.4276 | -0.054932 | 0.07782 | -0.022888 | -0.009155 | 0.009155 | 0.013733 | 0.032043 | -0.10071 | -90.5502 | -122.9599 | 0.1236 | 0.041199 | 0.013733 | 0.14191 | 0.11444 | 41.4459 | -81.4316 | -81.5186 | 41.478 | 41.5009 | 41.4825 | 0.054931 | 0.036621 | 0.2243 | 0.11902 | 0.032043 | 0.013733 | 32.5287 | 0.10071 | 32.428 | 41.5466 | -123.0789 | -81.5323 | 0.018311 | 41.4597 | 0.045776 | 41.4139
624.9531 | 123.0743 | -40.5762 | 82.4844 | -0.023297 | 0.15515 | -0.64238 | 0.20398 | -0.0024746 | 0.0086403 | -0.021077 | -0.00065608 | 0.15836 | 0.1459 | -0.012108 | 0.10472 | 0.021658 | 0.0045054 | -40.6952 | -9.0546 | -40.5029 | -40.6906 | -40.5121 | -40.6998 | -40.6265 | -0.036621 | 0.10071 | -0.018311 | -0.009155 | -0.009155 | 0.018311 | 0.013733 | 0.073242 | -91.539 | -123.175 | 0.064087 | -0.050354 | -0.1236 | -0.1236 | -0.19684 | 40.5579 | -82.3837 | -82.4936 | 40.567 | 40.5899 | 40.5945 | 0.032044 | 0.036622 | -0.009155 | -0.18768 | 0.009156 | 0.009156 | 31.4484 | 0.11902 | 31.5216 | 40.6769 | -122.9874 | -82.5027 | -0.11444 | 40.567 | -0.11902 | 40.5396
626.0312 | 123.1155 | -37.9944 | 85.0067 | -0.13011 | 0.14661 | -0.64985 | 0.21252 | -0.0024746 | -0.00097271 | -0.021077 | -0.046432 | 0.16156 | 0.15338 | -0.014245 | 0.11219 | 0.022726 | -0.0093806 | -38.2004 | -9.0454 | -38.0997 | -38.3011 | -38.2095 | -38.3194 | -38.2736 | 0.022888 | 0.073242 | 0.022888 | 0.041199 | 0.059509 | 0.068665 | 0.036621 | -0.10529 | -94.0521 | -123.3078 | -0.21515 | -0.27924 | -0.32501 | -0.17395 | -0.21973 | 38.0173 | -84.9335 | -84.9655 | 38.0539 | 38.031 | 38.0631 | 0.013733 | 0.045777 | -0.10986 | -0.20142 | 0.036621 | 0.018311 | 29.0543 | 0.050354 | 28.949 | 38.0676 | -123.1064 | -84.9838 | -0.3067 | 38.0356 | -0.20599 | 38.0173
626.9531 | 123.143 | -35.6415 | 87.3596 | -0.084332 | 0.14874 | -0.63917 | 0.20505 | 0.0071384 | 0.0022313 | -0.0061228 | 0.12141 | 0.1637 | 0.14269 | -0.02813 | 0.084423 | 0.022726 | -0.0029716 | -34.2865 | -9.0408 | -35.6277 | -35.9665 | -35.8154 | -35.9436 | -35.9116 | 0.013733 | 0.082397 | -0.009155 | -0.022888 | 0.022888 | 0.091553 | 0.082397 | 0.013732 | -96.4005 | -123.3261 | -0.17395 | -0.27008 | -0.30213 | -0.28381 | -0.31586 | 35.6323 | -87.2772 | -87.3825 | 35.6644 | 35.7239 | 35.733 | 0.091552 | 0.10071 | -0.18768 | -0.33875 | 0.032043 | -0.013733 | 26.5869 | 0.091552 | 26.6006 | 35.7239 | -122.9874 | -87.3688 | -0.32501 | 35.6186 | 1.355 | 35.6552
628.0312 | 123.2162 | -61.2808 | 61.6104 | -0.038556 | 0.14981 | -0.66267 | 0.21466 | 0.0017974 | -0.016995 | -0.0082598 | -0.00065608 | 0.17117 | 0.15231 | -0.0089038 | 0.10151 | 0.018454 | -0.013653 | 0 | 0 | -0.050354 | 0.045776 | 0.050354 | -0.004578 | 0.032043 | 0.009155 | 0.091553 | -0.009155 | 0.054932 | 0.045776 | 0.059509 | 0.064087 | 61.2305 | -61.6104 | -61.5646 | 61.3312 | 61.3129 | 61.2762 | 0.082397 | 0.045776 | 61.2717 | -61.5189 | -61.5555 | 61.3266 | 61.3449 | 61.3403 | 0.073242 | 0.068664 | 0.10071 | 0.09613 | 0.054931 | 0.064087 | 0.050354 | 0.10071 | 61.2808 | 61.3724 | -61.6608 | -61.6196 | 61.3266 | 61.3358 | 61.2808 | 61.29
628.9688 | 123.1155 | -61.3403 | 61.6058 | 0.037738 | 0.14233 | -0.66694 | 0.20505 | -0.0024746 | -0.0095177 | -0.0093278 | 0.075638 | 0.17545 | 0.14697 | -0.02279 | 0.095104 | 0.023794 | -0.0040396 | -0.027466 | 0.018311 | -0.027466 | 0.09613 | 0.11444 | 0.07782 | 0.07782 | -0.054932 | 0.10529 | -0.018311 | 0 | 0 | 0.013733 | 0.027466 | 61.3129 | -61.5875 | -61.5097 | 61.4548 | 61.4182 | 61.4182 | 0.10529 | 0.10529 | 61.322 | -61.5005 | -61.6058 | 61.3403 | 61.3678 | 61.3541 | 0.045777 | 0.032044 | 0.14191 | 0.1236 | 0.018311 | 0.018311 | 0.045777 | 0.1236 | 61.3586 | 61.4456 | -61.6333 | -61.6241 | 61.4365 | 61.3403 | 61.3129 | 61.2854
630.0312 | 123.143 | -61.377 | 61.6241 | 0.037738 | 0.14554 | -0.66694 | 0.21573 | -0.0024746 | 9.5287e-05 | -0.012532 | 0.18245 | 0.16797 | 0.13842 | -0.00035879 | 0.10579 | 0.016318 | -0.011517 | -0.032043 | 0.013733 | -0.018311 | 0.10529 | 0.12817 | 0.07782 | 0.10986 | -0.068665 | 0.11444 | -0.018311 | -0.009155 | -0.018311 | 0 | 0.009155 | 61.3586 | -61.6104 | -61.5189 | 61.5051 | 61.4868 | 61.4548 | 0.12817 | 0.096131 | 61.3586 | -61.5097 | -61.6333 | 61.3586 | 61.3861 | 61.377 | 0.027466 | 0.018311 | 0.14649 | 0.1236 | 0 | 0.009156 | 0.032044 | 0.13275 | 61.3907 | 61.4914 | -61.6425 | -61.6425 | 61.4822 | 61.3678 | 61.3449 | 61.3083
630.9531 | 123.2254 | -61.3815 | 61.5646 | -0.099591 | 0.15088 | -0.66374 | 0.19437 | 0.0028664 | -0.026608 | -0.0018508 | 0.274 | 0.15195 | 0.1694 | -0.034539 | 0.095104 | 0.022726 | 0.0077094 | 0.027466 | -0.018311 | 0.018311 | 0.004578 | 0.027466 | 0 | 0.013733 | 0.036621 | 0.07782 | 0.041199 | 0.064087 | 0.064087 | 0.082397 | 0.10071 | 61.3998 | -61.5829 | -61.5601 | 61.409 | 61.3953 | 61.3815 | -0.004578 | -0.018311 | 61.4227 | -61.4868 | -61.5005 | 61.4456 | 61.4822 | 61.4639 | 0.059509 | 0.041198 | 0.009155 | -0.013733 | 0.022888 | 0.022888 | -0.036622 | 0.036621 | 61.3632 | 61.4594 | -61.5463 | -61.5234 | 61.3861 | 61.4456 | 61.409 | 61.4182
632.0312 | 123.1384 | -61.4227 | 61.6196 | 0.022479 | 0.15195 | -0.66801 | 0.20398 | 0.0092744 | -0.021267 | -0.012532 | 0.274 | 0.17545 | 0.13842 | -0.0099718 | 0.097241 | 0.028067 | -0.0061756 | 0.022888 | 0.018311 | 0 | 0.10529 | 0.12817 | 0.073242 | 0.10071 | -0.059509 | 0.09613 | -0.009155 | 0 | 0 | 0.004578 | 0.009155 | 61.4227 | -61.6013 | -61.5143 | 61.5509 | 61.5234 | 61.496 | 0.10071 | 0.073242 | 61.4136 | -61.5234 | -61.6196 | 61.4227 | 61.4319 | 61.4273 | 0.01831 | 0.013733 | 0.12817 | 0.10529 | 0.009155 | 0.009155 | 0.018311 | 0.10528 | 61.441 | 61.5189 | -61.6196 | -61.6287 | 61.528 | 61.4227 | 61.4456 | 61.3632
632.9531 | 123.2666 | -61.3953 | 61.5326 | -0.11485 | 0.14768 | -0.67335 | 0.20718 | -0.0024746 | -0.013791 | 0.00028524 | 0.3503 | 0.17972 | 0.13842 | -0.033471 | 0.10472 | 0.019522 | 0.0066414 | 0.064087 | 0 | 0.013733 | -0.013733 | 0.013733 | -0.022888 | -0.004578 | 0.10071 | 0.073242 | 0.036621 | 0.14191 | 0.14648 | 0.14191 | 0.1236 | 61.409 | -61.5326 | -61.5463 | 61.409 | 61.3907 | 61.3724 | -0.018311 | -0.036621 | 61.4319 | -61.4594 | -61.3907 | 61.5417 | 61.5189 | 61.5372 | 0.086975 | 0.10529 | 0 | -0.027466 | 0.10986 | 0.10529 | -0.013733 | 0.036621 | 61.3953 | 61.4685 | -61.5189 | -61.496 | 61.3815 | 61.5372 | 61.4594 | 61.496
634.0469 | 123.2437 | -61.3907 | 61.5417 | -0.16063 | 0.15729 | -0.68083 | 0.20932 | 0.0028664 | 9.5287e-05 | -0.0018508 | 0.075638 | 0.15515 | 0.14804 | -0.02813 | 0.098309 | 0.014181 | -0.0051076 | 0.073242 | -0.022888 | 0.022888 | -0.11444 | -0.16479 | -0.19684 | -0.032043 | 0.11902 | 0.004578 | -0.027466 | 0.10529 | 0.10529 | 0.086975 | 0.086975 | 61.4136 | -61.5646 | -61.6562 | 61.2259 | 61.3586 | 61.1938 | -0.054931 | -0.21973 | 61.3632 | -61.5372 | -61.4365 | 61.496 | 61.4777 | 61.4777 | 0.11444 | 0.11444 | -0.18768 | -0.13733 | 0.13275 | 0.13275 | -0.045776 | 0.032044 | 61.3678 | 61.3953 | -61.5189 | -61.5692 | 61.2762 | 61.496 | 61.4639 | 61.5097
634.9531 | 123.2483 | -61.4273 | 61.5509 | -0.084332 | 0.14874 | -0.68617 | 0.20291 | 0.00072943 | 0.0043673 | -0.0050548 | 0.25874 | 0.1669 | 0.13735 | -0.027062 | 0.097241 | 0.024863 | -0.012585 | 0.032043 | -0.009155 | 0.018311 | 0.027466 | 0.050354 | 0.009155 | 0.054932 | -0.018311 | 0.027466 | 0.009155 | 0.041199 | 0.041199 | 0.045776 | 0.059509 | 61.4456 | -61.5601 | -61.5234 | 61.4777 | 61.4822 | 61.4365 | 0.036621 | -0.009156 | 61.4365 | -61.5234 | -61.5097 | 61.4685 | 61.4868 | 61.4731 | 0.050354 | 0.036621 | 0.032043 | 0.009155 | 0.032044 | 0.032044 | -0.027466 | 0.018311 | 61.4182 | 61.4548 | -61.5326 | -61.5417 | 61.4548 | 61.4685 | 61.4594 | 61.409
635.9531 | 123.2117 | -61.3861 | 61.5463 | -0.053815 | 0.15622 | -0.66267 | 0.21893 | 0.0060704 | -0.011654 | -0.00078276 | 0.25874 | 0.16049 | 0.13522 | -0.048424 | 0.095104 | 0.0056372 | -0.0093806 | 0.054932 | -0.004578 | 0.045776 | -0.004578 | 0.004578 | -0.013733 | 0.013733 | 0.059509 | 0.050354 | 0 | 0.064087 | 0.059509 | 0.07782 | 0.054932 | 61.4319 | -61.5509 | -61.5509 | 61.3907 | 61.3998 | 61.3724 | -0.032043 | -0.059509 | 61.3861 | -61.496 | -61.4822 | 61.4456 | 61.441 | 61.4639 | 0.054932 | 0.07782 | -0.041198 | -0.050354 | 0.059509 | 0.064087 | -0.050354 | 0.050354 | 61.3815 | 61.4365 | -61.5006 | -61.5463 | 61.3815 | 61.4502 | 61.441 | 61.4456
637.0312 | 123.1293 | -61.4182 | 61.5875 | -0.069074 | 0.13913 | -0.67015 | 0.20825 | 0.016751 | -0.013791 | -0.0093278 | 0.12141 | 0.17117 | 0.13522 | -0.031334 | 0.10258 | 0.017386 | 0.0077094 | 0.032043 | -0.004578 | 0.004578 | 0.064087 | 0.10529 | 0.032043 | 0.091553 | -0.050354 | 0.036621 | -0.041199 | -0.036621 | -0.036621 | 0 | -0.027466 | 61.4227 | -61.5921 | -61.5234 | 61.5234 | 61.5097 | 61.4502 | 0.086975 | 0.027465 | 61.377 | -61.5509 | -61.6241 | 61.3815 | 61.3907 | 61.4182 | 0.013733 | 0.041199 | 0.10071 | 0.059509 | 0.004578 | 0.004578 | -0.009156 | 0.07782 | 61.4136 | 61.4548 | -61.5829 | -61.6287 | 61.4822 | 61.3815 | 61.4502 | 61.3678
637.9531 | 123.23 | -61.4044 | 61.6013 | 0.022479 | 0.1434 | -0.66374 | 0.19437 | -0.0014066 | -0.0073817 | -0.028554 | 0.274 | 0.16263 | 0.12881 | -0.027062 | 0.092968 | 0.016318 | 0.0013004 | 0.032043 | -0.018311 | 0.027466 | 0.022888 | 0.059509 | -0.009155 | 0.027466 | -0.009155 | 0.050354 | -0.004578 | -0.17395 | -0.041199 | -0.054932 | 0.009155 | 61.4319 | -61.6196 | -61.5784 | 61.4639 | 61.4319 | 61.3953 | 0 | -0.036621 | 61.3998 | -61.5509 | -61.7752 | 61.3632 | 61.4136 | 61.3495 | 0.013733 | -0.050354 | 0.032043 | -0.004578 | -0.036621 | -0.16937 | -0.045777 | 0.054932 | 61.3861 | 61.4548 | -61.5738 | -61.6058 | 61.4273 | 61.2305 | 61.4365 | 61.3953
639.0312 | 123.1247 | -61.4273 | 61.5875 | -0.11485 | 0.14981 | -0.6584 | 0.20505 | 0.010342 | -0.021267 | -0.00078276 | -0.12273 | 0.17438 | 0.15658 | -0.013176 | 0.099377 | 0.01525 | -0.012585 | 0.013733 | 0.013733 | 0 | 0.11444 | 0.13733 | 0.073242 | 0.091553 | -0.073242 | 0.059509 | -0.068665 | 0.16022 | -0.15106 | 0.16479 | 0.09613 | 61.4273 | -61.5738 | -61.4731 | 61.5646 | 61.5189 | 61.5005 | 0.091553 | 0.073242 | 61.3586 | -61.528 | -61.4273 | 61.2762 | 61.5234 | 61.5921 | 0.16479 | 0.23346 | 0.13733 | 0.11444 | -0.082397 | 0.22888 | 0.013733 | 0.12817 | 61.441 | 61.4868 | -61.5875 | -61.6562 | 61.5417 | 61.5875 | 61.441 | 61.3541
639.9531 | 123.2208 | -61.4319 | 61.5463 | -0.099591 | 0.15836 | -0.66481 | 0.21146 | -0.01102 | 0.032138 | -0.0082598 | 0.090897 | 0.1637 | 0.15124 | -0.023858 | 0.10365 | 0.014181 | 0.0034374 | 0.050354 | -0.013733 | 0.018311 | -0.018311 | 0.013733 | -0.018311 | 0.009155 | 0.032043 | 0.050354 | -0.004578 | 0.054932 | 0.032043 | 0.050354 | 0.041199 | 61.4502 | -61.5601 | -61.5646 | 61.4456 | 61.441 | 61.4136 | -0.009156 | -0.036622 | 61.4273 | -61.496 | -61.4914 | 61.4639 | 61.4731 | 61.4822 | 0.045777 | 0.054932 | -0.004578 | -0.036622 | 0.036621 | 0.05951 | -0.032044 | 0.054932 | 61.4182 | 61.4822 | -61.528 | -61.5509 | 61.4136 | 61.4868 | 61.4822 | 61.4639
641.0312 | 123.1338 | -61.409 | 61.5921 | 0.15981 | 0.14447 | -0.66801 | 0.20505 | 0.00072943 | -0.0031087 | -0.0050548 | 0.16719 | 0.16904 | 0.14269 | -0.015313 | 0.095104 | 0.018454 | -0.012585 | -0.013733 | 0.009155 | -0.022888 | 0.09613 | 0.11902 | 0.064087 | 0.10986 | -0.09613 | 0.068665 | -0.027466 | -0.022888 | -0.059509 | -0.009155 | -0.004578 | 61.3861 | -61.5829 | -61.496 | 61.528 | 61.5189 | 61.4731 | 0.13275 | 0.086975 | 61.3815 | -61.5234 | -61.615 | 61.3495 | 61.4044 | 61.3998 | 0.022888 | 0.018311 | 0.14191 | 0.11902 | -0.032043 | 0.004578 | 0.032043 | 0.096131 | 61.4182 | 61.4777 | -61.615 | -61.6196 | 61.5051 | 61.3861 | 61.3953 | 61.3129
641.9531 | 123.2346 | -61.3861 | 61.5601 | -0.023297 | 0.14233 | -0.66801 | 0.20398 | 0.0082064 | -0.0031087 | -0.0093278 | 0.28926 | 0.17011 | 0.15124 | -0.012108 | 0.096172 | 0.028067 | -0.0093806 | 0.018311 | 0.004578 | 0.022888 | 0.027466 | 0.018311 | -0.009155 | 0 | -0.004578 | 0.045776 | 0.004578 | -0.009155 | 0.064087 | 0.050354 | 0.032043 | 61.409 | -61.5555 | -61.5326 | 61.4044 | 61.3861 | 61.377 | -0.022888 | -0.032043 | 61.3907 | -61.5143 | -61.5692 | 61.4502 | 61.4182 | 61.4365 | 0.027465 | 0.045776 | -0.004577 | 0.004578 | 0.059509 | -0.013733 | -0.01831 | 0.041198 | 61.3907 | 61.4319 | -61.5372 | -61.5555 | 61.4136 | 61.377 | 61.4044 | 61.3815
643.0312 | 123.2162 | -61.4319 | 61.5738 | -0.0080386 | 0.14661 | -0.6819 | 0.20611 | 0.0028664 | -0.023404 | -0.015736 | -0.046432 | 0.16904 | 0.13201 | 0.0017772 | 0.095104 | 0.025931 | -0.00083564 | 0.045776 | 0.009155 | -0.004578 | 0.045776 | 0.050354 | 0.018311 | 0.073242 | 0 | 0.054932 | -0.013733 | 0.036621 | 0.036621 | 0.004578 | 0.027466 | 61.4273 | -61.5646 | -61.528 | 61.4822 | 61.5051 | 61.4502 | 0.07782 | 0.022889 | 61.4182 | -61.5189 | -61.5372 | 61.4685 | 61.4594 | 61.4365 | 0.041199 | 0.018311 | 0.054932 | 0.050354 | 0.050354 | 0.050354 | 0.013733 | 0.068665 | 61.441 | 61.4868 | -61.5784 | -61.5875 | 61.4777 | 61.4685 | 61.4777 | 61.4319
643.9688 | 123.1796 | -61.4319 | 61.6013 | 0.068255 | 0.14768 | -0.68403 | 0.20825 | 0.0039344 | -0.0041777 | -0.0082598 | 0.075638 | 0.1669 | 0.15444 | -0.021721 | 0.092968 | 0.02059 | -0.0061756 | 0 | 0.018311 | -0.041199 | 0.082397 | 0.10529 | 0.036621 | 0.07782 | -0.064087 | 0.050354 | -0.045776 | -0.009155 | 0.018311 | 0.009155 | 0.022888 | 61.3907 | -61.5829 | -61.5189 | 61.5372 | 61.5097 | 61.4685 | 0.11902 | 0.07782 | 61.3861 | -61.5509 | -61.6104 | 61.4502 | 61.4548 | 61.441 | 0.068664 | 0.054931 | 0.14649 | 0.1236 | 0.064087 | 0.036621 | 0.05951 | 0.09613 | 61.4502 | 61.4822 | -61.6425 | -61.647 | 61.5143 | 61.4227 | 61.4319 | 61.3678
645.0312 | 123.1567 | -61.4502 | 61.615 | 0.098773 | 0.14874 | -0.68724 | 0.20291 | -0.0067466 | -0.016995 | -0.0071918 | 0.18245 | 0.16904 | 0.14056 | -0.024926 | 0.11219 | 0.025931 | -0.0040396 | -0.022888 | 0.004578 | -0.032043 | 0.07782 | 0.13275 | 0.068665 | 0.09613 | -0.09613 | 0.064087 | -0.045776 | 0.022888 | -0.045776 | -0.004578 | 0.022888 | 61.4182 | -61.6104 | -61.5372 | 61.5829 | 61.5463 | 61.5189 | 0.12817 | 0.10071 | 61.4044 | -61.5509 | -61.5921 | 61.4044 | 61.4731 | 61.4456 | 0.068664 | 0.041198 | 0.16479 | 0.10986 | 0 | 0.068664 | 0.036621 | 0.10986 | 61.4548 | 61.5143 | -61.647 | -61.6608 | 61.528 | 61.4731 | 61.4273 | 61.3541
645.9531 | 123.2391 | -61.4365 | 61.5601 | -0.023297 | 0.14233 | -0.7086 | 0.21146 | -0.0035426 | -0.0063137 | 0.0045582 | 0.16719 | 0.16156 | 0.12454 | -0.042016 | 0.098309 | 0.022726 | -0.00083564 | 0.013733 | -0.018311 | 0.027466 | 0.009155 | 0.027466 | 0.004578 | 0.004578 | -0.027466 | 0.045776 | 0.004578 | 0.018311 | 0.059509 | 0.054932 | 0.036621 | 61.4639 | -61.5784 | -61.5509 | 61.4639 | 61.441 | 61.441 | -0.022888 | -0.022888 | 61.441 | -61.5143 | -61.5417 | 61.496 | 61.4731 | 61.4914 | 0.032043 | 0.050354 | 0 | -0.018311 | 0.054931 | 0.013733 | -0.045777 | 0.041198 | 61.4182 | 61.4822 | -61.5326 | -61.5555 | 61.4456 | 61.4548 | 61.4502 | 61.409
647.0312 | 123.2712 | -61.3998 | 61.5692 | 0.052997 | 0.1402 | -0.70112 | 0.20611 | -0.0088836 | 9.5287e-05 | 0.0024222 | 0.3503 | 0.16156 | 0.15765 | -0.025994 | 0.097241 | 0.02059 | -0.014721 | 0.10071 | -0.041199 | 0.036621 | -0.054932 | -0.054932 | -0.059509 | -0.027466 | 0.091553 | 0.027466 | -0.013733 | 0.091553 | 0.13733 | 0.1236 | 0.11444 | 61.4365 | -61.6104 | -61.6241 | 61.3449 | 61.3724 | 61.3403 | -0.064087 | -0.09613 | 61.3861 | -61.5417 | -61.4777 | 61.5372 | 61.5143 | 61.5234 | 0.12817 | 0.13733 | -0.091553 | -0.091553 | 0.15106 | 0.10529 | -0.07782 | 0.041199 | 61.3586 | 61.4273 | -61.5326 | -61.5829 | 61.3449 | 61.4914 | 61.5005 | 61.4914
647.9531 | 123.2529 | -61.4044 | 61.5646 | -0.069074 | 0.14447 | -0.71073 | 0.20718 | -0.0088836 | 0.0022313 | 0.0024222 | 0.274 | 0.1637 | 0.13522 | -0.00035879 | 0.10045 | 0.030203 | -0.00083564 | 0.041199 | -0.013733 | 0.022888 | 0.009155 | 0.045776 | 0.004578 | -0.004578 | 0 | 0.032043 | 0.022888 | 0.027466 | 0.045776 | 0.054932 | 0.064087 | 61.4273 | -61.5784 | -61.5555 | 61.4502 | 61.3998 | 61.409 | -0.027466 | -0.01831 | 61.4273 | -61.5326 | -61.5372 | 61.4502 | 61.4685 | 61.4594 | 0.041199 | 0.032044 | 0.022888 | -0.013733 | 0.022888 | 0.004578 | -0.036621 | 0.009155 | 61.3907 | 61.4365 | -61.5417 | -61.5417 | 61.4136 | 61.4319 | 61.4456 | 61.4044
648.9688 | 123.2025 | -61.409 | 61.6379 | -0.11485 | 0.14874 | -0.71714 | 0.21893 | -0.015292 | -0.013791 | 0.00028524 | 0.24348 | 0.16583 | 0.12667 | -0.033471 | 0.094036 | 0.016318 | -0.014721 | 0.09613 | -0.032043 | 0.041199 | -0.009155 | 0.009155 | -0.018311 | 0.032043 | 0.018311 | 0.036621 | -0.009155 | 0.018311 | 0.050354 | 0.054932 | 0.050354 | 61.4502 | -61.6699 | -61.647 | 61.4182 | 61.441 | 61.3907 | -0.009156 | -0.05951 | 61.3998 | -61.6013 | -61.6196 | 61.4594 | 61.4594 | 61.4639 | 0.059509 | 0.064087 | -0.032044 | -0.050354 | 0.059509 | 0.027466 | -0.073242 | 0.045776 | 61.377 | 61.4456 | -61.5967 | -61.647 | 61.3998 | 61.4273 | 61.5051 | 61.4273
650.0312 | 123.1247 | -61.4594 | 61.6196 | -0.069074 | 0.16263 | -0.72996 | 0.21146 | 0.00072943 | 0.0054353 | -0.0136 | 0.12141 | 0.16797 | 0.1459 | -0.048424 | 0.10045 | 0.022726 | 0.00023236 | -0.013733 | 0 | -0.009155 | 0.10071 | 0.10529 | 0.064087 | 0.10071 | -0.09613 | 0.073242 | -0.032043 | -0.022888 | -0.036621 | -0.009155 | -0.009155 | 61.4502 | -61.6196 | -61.5189 | 61.5646 | 61.5601 | 61.5234 | 0.10986 | 0.073242 | 61.4273 | -61.5463 | -61.6425 | 61.4227 | 61.4502 | 61.4502 | 0.022888 | 0.022888 | 0.11444 | 0.10986 | -0.004578 | 0.009155 | 0.009155 | 0.10529 | 61.4594 | 61.5326 | -61.6287 | -61.6516 | 61.5601 | 61.4365 | 61.4456 | 61.3632
650.9531 | 123.2712 | -61.3724 | 61.5784 | -0.038556 | 0.15408 | -0.71394 | 0.22 | 0.0050024 | 0.027866 | -0.014668 | 0.274 | 0.17117 | 0.13201 | -0.015313 | 0.10258 | 0.018454 | -0.0093806 | 0.073242 | -0.041199 | 0.045776 | -0.10529 | -0.082397 | -0.09613 | -0.054932 | 0.086975 | 0.022888 | -0.004578 | 0.09613 | 0.13275 | 0.13733 | 0.10529 | 61.4182 | -61.6196 | -61.6837 | 61.29 | 61.3174 | 61.2762 | -0.10071 | -0.14191 | 61.3678 | -61.5555 | -61.4822 | 61.5051 | 61.4777 | 61.5097 | 0.10986 | 0.14191 | -0.12817 | -0.15106 | 0.13733 | 0.10071 | -0.086975 | 0.027466 | 61.3312 | 61.3953 | -61.5326 | -61.5829 | 61.2671 | 61.4685 | 61.4456 | 61.4594
652.0312 | 123.1567 | -61.4182 | 61.6333 | 0.15981 | 0.14661 | -0.81968 | 0.21252 | 0.0028664 | -0.010586 | 0.0013532 | 0.19771 | 0.15302 | 0.15124 | -0.013176 | 0.098309 | 0.021658 | -0.0061756 | 0.009155 | -0.009155 | 0 | 0.07782 | 0.10071 | 0.041199 | 0.10071 | -0.068665 | 0.073242 | -0.027466 | -0.045776 | -0.013733 | -0.013733 | -0.022888 | 61.4182 | -61.6425 | -61.5555 | 61.5189 | 61.5189 | 61.4594 | 0.10071 | 0.041199 | 61.3907 | -61.5601 | -61.6791 | 61.4044 | 61.3953 | 61.4044 | 0.004578 | 0.013733 | 0.10071 | 0.07782 | 0.013733 | -0.01831 | -0.009155 | 0.10071 | 61.409 | 61.4914 | -61.6333 | -61.6608 | 61.496 | 61.3724 | 61.4273 | 61.3495
652.9688 | 123.2574 | -61.4136 | 61.6058 | 0.052997 | 0.1402 | -0.79832 | 0.20611 | -0.0078156 | 0.0065043 | -0.0018508 | 0.18245 | 0.16049 | 0.12774 | 0.0049812 | 0.10045 | 0.016318 | -0.012585 | 0.004578 | -0.041199 | 0.013733 | 0 | 0.009155 | -0.013733 | -0.009155 | 0.009155 | 0.032043 | -0.022888 | 0.064087 | 0.054932 | 0.059509 | 0.050354 | 61.4273 | -61.647 | -61.6058 | 61.4227 | 61.4044 | 61.3998 | -0.022888 | -0.027466 | 61.3907 | -61.5738 | -61.5417 | 61.4685 | 61.4639 | 61.4731 | 0.073242 | 0.082397 | -0.004578 | -0.013733 | 0.07782 | 0.086975 | -0.054932 | 0.054931 | 61.3724 | 61.4456 | -61.5921 | -61.6287 | 61.4136 | 61.4777 | 61.4182 | 61.4227
654.0312 | 123.2712 | -61.3998 | 61.5738 | -0.13011 | 0.1637 | -0.83998 | 0.22427 | 0.0028664 | -0.0041777 | -0.011464 | 0.15193 | 0.16904 | 0.12988 | -0.02813 | 0.086559 | 0.013113 | -0.0061756 | 0.07782 | -0.045776 | 0.018311 | -0.073242 | -0.041199 | -0.073242 | -0.036621 | 0.07782 | 0.036621 | -0.013733 | 0.073242 | 0.068665 | 0.11902 | 0.10529 | 61.4182 | -61.6196 | -61.647 | 61.3586 | 61.3632 | 61.3266 | -0.054932 | -0.091553 | 61.3861 | -61.5372 | -61.5005 | 61.4685 | 61.5051 | 61.5189 | 0.11902 | 0.13275 | -0.05951 | -0.091553 | 0.082398 | 0.086975 | -0.064087 | 0.050354 | 61.3541 | 61.4365 | -61.5555 | -61.5875 | 61.3266 | 61.4731 | 61.4777 | 61.4777
654.9531 | 123.2803 | -61.3998 | 61.6058 | -0.038556 | 0.1434 | -0.8357 | 0.20505 | -0.0067466 | 0.0097083 | 0.0045582 | 0.31978 | 0.17224 | 0.14804 | -0.036675 | 0.094036 | 0.01525 | -0.010449 | 0.054932 | -0.036621 | -0.004578 | -0.059509 | -0.054932 | -0.068665 | -0.036621 | 0.086975 | 0.018311 | 0.004578 | 0.07782 | 0.1236 | 0.11902 | 0.082397 | 61.3953 | -61.6425 | -61.6653 | 61.3449 | 61.3632 | 61.3312 | -0.032043 | -0.064087 | 61.4044 | -61.5875 | -61.528 | 61.5234 | 61.4822 | 61.5189 | 0.077819 | 0.11444 | -0.050354 | -0.054931 | 0.11902 | 0.073242 | -0.032043 | 0.013733 | 61.3632 | 61.4182 | -61.6104 | -61.6013 | 61.3403 | 61.4777 | 61.4548 | 61.4868
656.0938 | 123.2437 | -61.409 | 61.5875 | 0.083514 | 0.13806 | -0.82716 | 0.21786 | 0.00072943 | -0.014859 | -0.020009 | 0.21297 | 0.16156 | 0.12881 | 0.0017772 | 0.10685 | 0.016318 | -0.00083564 | 0.041199 | -0.073242 | -0.004578 | -0.027466 | -0.018311 | -0.064087 | 0 | 0.054932 | 0.054932 | -0.009155 | 0.050354 | 0.10071 | 0.07782 | 0.064087 | 61.4044 | -61.6608 | -61.615 | 61.3907 | 61.409 | 61.3449 | 0.004578 | -0.059509 | 61.3998 | -61.5326 | -61.5372 | 61.5097 | 61.4731 | 61.4868 | 0.073242 | 0.086975 | -0.013733 | -0.022888 | 0.10986 | 0.059509 | -0.068664 | 0.064087 | 61.3358 | 61.4639 | -61.5921 | -61.5967 | 61.3815 | 61.4594 | 61.4502 | 61.4639
656.9531 | 123.2346 | -61.4227 | 61.5555 | -0.038556 | 0.15622 | -0.84425 | 0.21252 | -0.0067466 | 0.0032993 | -0.0071918 | 0.10615 | 0.14981 | 0.13629 | -0.021721 | 0.10258 | 0.018454 | -0.018994 | 0.036621 | -0.036621 | 0.027466 | 0 | 0.013733 | 0.004578 | 0.004578 | 0.013733 | 0.054932 | 0.013733 | 0.050354 | 0.050354 | 0.068665 | 0.041199 | 61.4502 | -61.5921 | -61.5555 | 61.4365 | 61.4273 | 61.4273 | -0.022888 | -0.022888 | 61.4365 | -61.5005 | -61.5051 | 61.4731 | 61.4639 | 61.4914 | 0.027466 | 0.054932 | -0.013733 | -0.027466 | 0.036621 | 0.036621 | -0.064087 | 0.041199 | 61.3861 | 61.4777 | -61.528 | -61.5417 | 61.4227 | 61.4731 | 61.4593 | 61.4365
657.9688 | 123.1659 | -61.4319 | 61.6379 | 0.068255 | 0.15302 | -0.83784 | 0.20077 | -0.0046106 | -0.0031087 | -0.016805 | 0.12141 | 0.16049 | 0.15338 | -0.023858 | 0.10045 | 0.021658 | -0.0061756 | 0.009155 | 0 | -0.009155 | 0.064087 | 0.10071 | 0.050354 | 0.073242 | -0.045776 | 0.07782 | -0.041199 | -0.013733 | -0.004578 | -0.027466 | -0.027466 | 61.4227 | -61.6379 | -61.5738 | 61.5326 | 61.5051 | 61.4822 | 0.082397 | 0.059509 | 61.3907 | -61.5601 | -61.6516 | 61.4273 | 61.4044 | 61.4044 | 0.013733 | 0.013733 | 0.10986 | 0.073242 | 0.036621 | 0.027466 | 0.009155 | 0.11902 | 61.4319 | 61.5097 | -61.647 | -61.6791 | 61.496 | 61.4182 | 61.441 | 61.3861
659.0312 | 123.1842 | -61.4456 | 61.6013 | -0.023297 | 0.1434 | -0.84425 | 0.21786 | 0.0060704 | -0.014859 | -0.0018508 | -0.15324 | 0.16263 | 0.1491 | -0.0078358 | 0.10792 | 0.034476 | 0.0034374 | 0.022888 | -0.013733 | -0.032043 | 0.050354 | 0.068665 | 0.036621 | 0.082397 | -0.032043 | 0.09613 | 0.032043 | -0.009155 | 0.004578 | -0.013733 | 0.004578 | 61.4136 | -61.615 | -61.5509 | 61.5143 | 61.528 | 61.4822 | 0.11444 | 0.068664 | 61.4777 | -61.5051 | -61.6104 | 61.4502 | 61.4502 | 61.4319 | -0.027465 | -0.045776 | 0.10071 | 0.082397 | -0.027465 | -0.041198 | 0.01831 | 0.064087 | 61.4319 | 61.5417 | -61.6333 | -61.5692 | 61.496 | 61.4365 | 61.4685 | 61.4136
659.9688 | 123.2895 | -61.3953 | 61.6058 | -0.0080386 | 0.14447 | -0.85173 | 0.20611 | 0.00072943 | -0.00097271 | -0.0018508 | 0.30452 | 0.17011 | 0.15978 | -0.031334 | 0.096172 | 0.013113 | -0.0061756 | 0.054932 | -0.054932 | 0.009155 | -0.07782 | -0.050354 | -0.07782 | -0.032043 | 0.09613 | 0.027466 | -0.009155 | 0.082397 | 0.15106 | 0.13275 | 0.09613 | 61.4044 | -61.6608 | -61.6837 | 61.3449 | 61.3632 | 61.3174 | -0.041198 | -0.086975 | 61.3861 | -61.5784 | -61.5234 | 61.5463 | 61.4914 | 61.528 | 0.10528 | 0.14191 | -0.059509 | -0.086975 | 0.16022 | 0.091552 | -0.064087 | 0.036621 | 61.3403 | 61.4227 | -61.5967 | -61.615 | 61.3174 | 61.4777 | 61.4502 | 61.4914
660.9531 | 123.2162 | -61.4044 | 61.5875 | -0.038556 | 0.13272 | -0.85386 | 0.22427 | 0.013547 | -0.0031087 | -0.0061228 | 0.18245 | 0.16797 | 0.13735 | -0.04522 | 0.10365 | 0.028067 | 0.00023236 | 0.004578 | -0.036621 | 0.004578 | -0.004578 | 0.009155 | -0.009155 | 0.009155 | -0.009155 | 0.036621 | -0.013733 | 0.022888 | 0.050354 | 0.018311 | 0.07782 | 61.409 | -61.6241 | -61.5921 | 61.4136 | 61.4136 | 61.3953 | 0.004577 | -0.013733 | 61.3907 | -61.5509 | -61.5646 | 61.4548 | 61.4822 | 61.4227 | 0.091553 | 0.032044 | 0.004577 | -0.009156 | 0.064087 | 0.036621 | -0.041199 | 0.050354 | 61.3678 | 61.441 | -61.5829 | -61.6013 | 61.3998 | 61.4273 | 61.409 | 61.3953
661.9531 | 123.2529 | -61.4227 | 61.5829 | -0.069074 | 0.15622 | -0.84211 | 0.21039 | 0.017819 | -0.016995 | 0.0066942 | 0.25874 | 0.16049 | 0.14483 | -0.0089038 | 0.098309 | 0.019522 | 0.0066414 | 0.013733 | -0.041199 | 0.022888 | -0.2243 | -0.10986 | -0.073242 | -0.050354 | 0 | 0.009155 | -0.027466 | 0.07782 | 0.07782 | 0.10071 | 0.10071 | 61.4456 | -61.6241 | -61.8073 | 61.3129 | 61.3724 | 61.3495 | -0.073242 | -0.09613 | 61.3953 | -61.5738 | -61.5051 | 61.5005 | 61.5234 | 61.5234 | 0.12817 | 0.12817 | -0.13275 | -0.24719 | 0.10529 | 0.10529 | -0.064087 | 0.036621 | 61.3815 | 61.4319 | -61.5601 | -61.6104 | 61.1984 | 61.5005 | 61.4365 | 61.4227
663.0312 | 123.1522 | -61.441 | 61.615 | 0.022479 | 0.1434 | -0.85279 | 0.20611 | 0.0050024 | -0.011654 | -0.021077 | -0.10747 | 0.17117 | 0.15338 | -0.013176 | 0.096172 | 0.031271 | 0.0045054 | -0.022888 | -0.045776 | -0.027466 | 0.054932 | 0.091553 | 0.036621 | 0.059509 | -0.10986 | 0.059509 | -0.036621 | -0.022888 | -0.064087 | -0.054932 | -0.009155 | 61.4136 | -61.6608 | -61.5601 | 61.5326 | 61.5005 | 61.4777 | 0.086975 | 0.064087 | 61.4044 | -61.5555 | -61.6379 | 61.377 | 61.4319 | 61.3861 | 0.027466 | -0.018311 | 0.11902 | 0.082398 | -0.027466 | 0.013733 | -0.01831 | 0.09613 | 61.3953 | 61.5005 | -61.6425 | -61.6516 | 61.496 | 61.4182 | 61.4182 | 61.3312
663.9688 | 123.2941 | -61.3724 | 61.5829 | 0.098773 | 0.15408 | -0.87095 | 0.20184 | 0.0039344 | -0.011654 | -0.0136 | 0.31978 | 0.1637 | 0.12026 | -0.0046318 | 0.095104 | 0.014181 | -0.0019036 | 0.086975 | -0.041199 | -0.004578 | -0.068665 | -0.064087 | -0.064087 | -0.036621 | 0.091553 | 0.032043 | -0.009155 | 0.086975 | 0.14648 | 0.12817 | 0.09613 | 61.3678 | -61.6241 | -61.6516 | 61.3083 | 61.3358 | 61.3083 | -0.032043 | -0.059509 | 61.3632 | -61.5509 | -61.496 | 61.5189 | 61.4685 | 61.5005 | 0.10528 | 0.13733 | -0.059509 | -0.064087 | 0.15564 | 0.09613 | -0.036621 | 0.041198 | 61.3312 | 61.4044 | -61.5875 | -61.5921 | 61.3037 | 61.4594 | 61.4594 | 61.4639
665.0312 | 123.1476 | -61.4182 | 61.6333 | 0.0072204 | 0.15408 | -0.86668 | 0.21359 | 0.014615 | 9.5287e-05 | -0.0071918 | 0.014603 | 0.16049 | 0.13308 | -0.040947 | 0.10258 | 0.021658 | -0.010449 | -0.013733 | 0 | -0.041199 | 0.059509 | 0.10986 | 0.064087 | 0.07782 | -0.073242 | 0.086975 | -0.041199 | -0.018311 | -0.036621 | 0.19226 | 0.10529 | 61.377 | -61.6333 | -61.5738 | 61.528 | 61.496 | 61.4822 | 0.11902 | 0.10529 | 61.377 | -61.5463 | -61.6516 | 61.3815 | 61.5234 | 61.6104 | 0.14649 | 0.23346 | 0.15106 | 0.10071 | 0.004578 | 0.022888 | 0.041199 | 0.12817 | 61.4182 | 61.5051 | -61.6745 | -61.6745 | 61.4777 | 61.3998 | 61.4044 | 61.3449
665.9531 | 123.2712 | -61.4182 | 61.5875 | 0.022479 | 0.1637 | -0.8592 | 0.21252 | -0.0088836 | 0.0032993 | -0.0082598 | 0.19771 | 0.15515 | 0.15231 | -0.0078358 | 0.090832 | 0.023794 | -0.00083564 | 0.027466 | -0.032043 | 0.009155 | -0.013733 | 0.004578 | 0 | -0.022888 | 0.018311 | 0.045776 | 0.009155 | 0.004578 | 0.036621 | 0.13275 | 0.064087 | 61.4273 | -61.6196 | -61.6013 | 61.4227 | 61.3953 | 61.4182 | -0.032043 | -0.009155 | 61.4273 | -61.5417 | -61.5829 | 61.4548 | 61.4822 | 61.5509 | 0.054932 | 0.1236 | -0.004577 | -0.022888 | 0.027466 | -0.004577 | -0.041198 | 0.036621 | 61.3861 | 61.4639 | -61.5784 | -61.5784 | 61.4044 | 61.4227 | 61.4456 | 61.4365
667.0312 | 123.2025 | -61.4273 | 61.5829 | -0.11485 | 0.15195 | -0.86882 | 0.21359 | 0.0082064 | -0.011654 | -0.014668 | 0.014603 | 0.17331 | 0.15124 | -0.039879 | 0.098309 | 0.031271 | -0.0051076 | -0.018311 | -0.022888 | -0.032043 | 0.082397 | 0.091553 | 0.045776 | 0.050354 | 0.086975 | 0.059509 | -0.013733 | 0.027466 | -0.004578 | -0.018311 | 0.018311 | 61.3953 | -61.6058 | -61.5005 | 61.5189 | 61.4777 | 61.4731 | 0.082397 | 0.077819 | 61.4136 | -61.5234 | -61.5555 | 61.4227 | 61.4456 | 61.409 | 0.032044 | -0.004578 | 0.1236 | 0.11444 | 0.009155 | 0.041199 | 0.009155 | 0.073242 | 61.4044 | 61.4868 | -61.615 | -61.5967 | 61.5097 | 61.4548 | 61.409 | 61.5143
667.9688 | 123.2437 | -61.4319 | 61.6196 | -0.069074 | 0.13593 | -0.99913 | 0.20718 | 0.0092744 | -0.016995 | -0.020009 | 0.060379 | 0.16904 | 0.14804 | -0.0089038 | 0.10365 | 0.023794 | -0.016858 | 0.018311 | -0.022888 | -0.032043 | 0.032043 | 0.036621 | 0.022888 | 0.022888 | 0.018311 | 0.064087 | -0.013733 | 0.022888 | 0.032043 | 0.068665 | 0.022888 | 61.3998 | -61.6425 | -61.5875 | 61.4685 | 61.4548 | 61.4548 | 0.054931 | 0.054931 | 61.4182 | -61.5555 | -61.5967 | 61.4639 | 61.4548 | 61.5006 | 0.036621 | 0.082398 | 0.068664 | 0.064086 | 0.045776 | 0.036621 | 0.009155 | 0.07782 | 61.409 | 61.496 | -61.6516 | -61.6333 | 61.4639 | 61.4548 | 61.4502 | 61.4502
669.0312 | 123.2941 | -61.4136 | 61.5829 | -0.069074 | 0.15088 | -1.0045 | 0.20611 | 0.02316 | -0.029812 | 0.0034902 | 0.075638 | 0.16797 | 0.14269 | -0.017449 | 0.097241 | 0.029135 | 0.0055734 | -0.018311 | -0.036621 | -0.018311 | -0.004578 | 0.022888 | -0.013733 | 0 | -0.009155 | 0.022888 | -0.027466 | 0.091553 | 0.041199 | 0.09613 | 0.11444 | 61.3953 | -61.6196 | -61.5875 | 61.4365 | 61.4136 | 61.3998 | 0.018311 | 0.004578 | 61.3861 | -61.5601 | -61.4914 | 61.4548 | 61.528 | 61.5097 | 0.14191 | 0.1236 | 0.041199 | 0.013733 | 0.068665 | 0.11902 | -0.01831 | 0.050354 | 61.377 | 61.4365 | -61.6013 | -61.6104 | 61.409 | 61.5051 | 61.3953 | 61.4044
669.9688 | 123.2529 | -61.4548 | 61.5829 | -0.13011 | 0.14981 | -1.0312 | 0.20611 | 0.013547 | -0.015927 | 0.00028524 | 0.060379 | 0.1669 | 0.14804 | -0.032403 | 0.10792 | 0.028067 | -0.0093806 | 0 | -0.004578 | -0.018311 | 0.041199 | 0.041199 | 0.027466 | 0.013733 | -0.045776 | 0.032043 | -0.045776 | 0.022888 | 0.032043 | 0.032043 | 0.027466 | 61.4365 | -61.5875 | -61.5417 | 61.496 | 61.4685 | 61.4822 | 0.032044 | 0.045777 | 61.409 | -61.5509 | -61.5601 | 61.4868 | 61.4822 | 61.4868 | 0.073242 | 0.077819 | 0.05951 | 0.05951 | 0.077819 | 0.068664 | 0.013733 | 0.077819 | 61.4502 | 61.4868 | -61.6013 | -61.6287 | 61.496 | 61.4777 | 61.4548 | 61.409
671.0312 | 123.2666 | -61.4136 | 61.6013 | -0.069074 | 0.1637 | -1.0237 | 0.20718 | 0.0060704 | -0.021267 | -0.016805 | 0.274 | 0.16797 | 0.13308 | -0.025994 | 0.10045 | 0.02059 | -0.028607 | 0.045776 | -0.059509 | 0 | -0.10071 | 0.041199 | 0.045776 | -0.1236 | 0.050354 | 0.018311 | -0.022888 | 0.054932 | 0.10986 | 0.091553 | 0.082397 | 61.4136 | -61.6608 | -61.702 | 61.4548 | 61.29 | 61.4593 | -0.1236 | 0.045776 | 61.3907 | -61.5829 | -61.5463 | 61.5234 | 61.496 | 61.5051 | 0.10528 | 0.11444 | 0.041199 | -0.10071 | 0.13275 | 0.07782 | -0.059509 | 0.041199 | 61.3541 | 61.4319 | -61.6013 | -61.6241 | 61.3129 | 61.4685 | 61.4593 | 61.4639
671.9531 | 123.2758 | -61.409 | 61.5692 | -0.14537 | 0.15622 | -1.029 | 0.20932 | -0.0014066 | 0.0032993 | -0.0136 | 0.10615 | 0.1637 | 0.13842 | -0.029198 | 0.092968 | 0.026999 | -0.015789 | 0.082397 | -0.059509 | -0.009155 | -0.07782 | -0.041199 | -0.068665 | -0.064087 | 0.10529 | -0.004578 | -0.018311 | 0.091553 | 0.10986 | 0.11444 | 0.082397 | 61.3998 | -61.6287 | -61.647 | 61.3678 | 61.3449 | 61.3403 | -0.054932 | -0.05951 | 61.3907 | -61.5738 | -61.4777 | 61.5189 | 61.4914 | 61.5234 | 0.10071 | 0.13275 | -0.032044 | -0.068665 | 0.12817 | 0.10986 | -0.050354 | 0.013733 | 61.3495 | 61.4044 | -61.5784 | -61.5875 | 61.3312 | 61.5005 | 61.4914 | 61.5143
673.0625 | 123.2758 | -61.4136 | 61.5601 | -0.084332 | 0.13272 | -1.0429 | 0.20932 | 0.014615 | -0.0084497 | -0.0050548 | 0.42659 | 0.1669 | 0.14163 | -0.0078358 | 0.10365 | 0.013113 | 0.0098454 | -0.07782 | -0.086975 | -0.041199 | -0.041199 | -0.013733 | -0.041199 | -0.022888 | 0.045776 | 0.022888 | 0.004578 | 0.073242 | 0.10529 | 0.11444 | 0.091553 | 61.3724 | -61.647 | -61.6013 | 61.3998 | 61.3907 | 61.3724 | 0.018311 | 0 | 61.4182 | -61.5372 | -61.4868 | 61.5189 | 61.5051 | 61.528 | 0.086975 | 0.10986 | 0.027466 | 0 | 0.10071 | 0.068664 | -0.045776 | 0.01831 | 61.3266 | 61.4365 | -61.6013 | -61.5555 | 61.3724 | 61.4868 | 61.3358 | 61.4593
673.9531 | 123.1476 | -61.4456 | 61.6241 | -0.0080386 | 0.14981 | -1.0643 | 0.21359 | -0.0067466 | -0.0084497 | -0.017873 | 0.33504 | 0.16797 | 0.14163 | 0.021003 | 0.0919 | 0.026999 | 0.00023236 | -0.013733 | -0.013733 | -0.018311 | 0.086975 | 0.10529 | 0.07782 | 0.091553 | -0.068665 | 0.07782 | -0.009155 | -0.018311 | -0.022888 | -0.004578 | -0.013733 | 61.4273 | -61.6379 | -61.5372 | 61.5509 | 61.5372 | 61.5234 | 0.10986 | 0.096131 | 61.4365 | -61.5463 | -61.6425 | 61.4227 | 61.4319 | 61.441 | -0.004578 | 0.004577 | 0.1236 | 0.10529 | -0.013733 | -0.009156 | 0.004578 | 0.086975 | 61.4319 | 61.5234 | -61.6425 | -61.6333 | 61.5326 | 61.4273 | 61.4319 | 61.377
674.9844 | 123.1842 | -61.4502 | 61.6196 | -0.023297 | 0.14447 | -1.0258 | 0.20398 | -0.0067466 | -0.015927 | -0.014668 | 0.15193 | 0.17011 | 0.14804 | -0.021721 | 0.098309 | 0.022726 | 0.00023236 | 0.018311 | -0.018311 | 0.004578 | 0.064087 | 0.073242 | 0.064087 | 0.064087 | -0.07782 | 0.054932 | -0.022888 | -0.045776 | 0.004578 | 0 | -0.013733 | 61.4548 | -61.6379 | -61.5555 | 61.5234 | 61.5143 | 61.5143 | 0.059509 | 0.059509 | 61.4273 | -61.5646 | -61.6653 | 61.4548 | 61.4365 | 61.4502 | 0.009155 | 0.022888 | 0.068664 | 0.059509 | 0.027466 | -0.022888 | -0.022889 | 0.07782 | 61.4319 | 61.5051 | -61.615 | -61.6425 | 61.5143 | 61.4044 | 61.4685 | 61.3724
675.9531 | 123.2666 | -61.4182 | 61.5784 | -0.084332 | 0.15195 | -1.0707 | 0.21039 | 0.0050024 | -0.016995 | 0.0077622 | 0.15193 | 0.16583 | 0.1459 | -0.0099718 | 0.099377 | 0.021658 | 0.0066414 | 0.059509 | -0.086975 | -0.004578 | -0.059509 | -0.054932 | -0.050354 | -0.018311 | 0.09613 | 0.045776 | 0.009155 | 0.07782 | 0.064087 | 0.09613 | 0.059509 | 61.4136 | -61.6653 | -61.6379 | 61.3632 | 61.3998 | 61.3678 | -0.013733 | -0.045776 | 61.4273 | -61.5326 | -61.5005 | 61.4822 | 61.4777 | 61.5143 | 0.050354 | 0.086975 | -0.050354 | -0.054931 | 0.054932 | 0.068665 | -0.082397 | 0.036621 | 61.3312 | 61.4639 | -61.5829 | -61.5692 | 61.3586 | 61.496 | 61.4777 | 61.5143
677.0312 | 123.175 | -61.4548 | 61.6333 | 0.083514 | 0.14768 | -1.091 | 0.20932 | 0.015683 | -0.00097271 | -0.0039868 | 0.21297 | 0.17011 | 0.13522 | -0.017449 | 0.10579 | 0.031271 | -0.0061756 | -0.013733 | 0 | -0.036621 | 0.086975 | 0.10071 | 0.082397 | 0.082397 | -0.054932 | 0.068665 | -0.022888 | -0.022888 | -0.018311 | -0.018311 | -0.013733 | 61.4182 | -61.6333 | -61.5463 | 61.5555 | 61.5372 | 61.5372 | 0.11902 | 0.11902 | 61.4319 | -61.5646 | -61.6562 | 61.4365 | 61.441 | 61.4365 | 0.009155 | 0.004577 | 0.13733 | 0.1236 | 0.004577 | 0 | 0.036621 | 0.091553 | 61.4548 | 61.5234 | -61.6699 | -61.6562 | 61.5417 | 61.4319 | 61.441 | 61.3998
677.9688 | 123.3444 | -61.3953 | 61.6013 | 0.083514 | 0.15088 | -1.0664 | 0.20611 | 0.013547 | -0.011654 | -0.0039868 | 0.274 | 0.1637 | 0.14269 | -0.04522 | 0.092968 | 0.024863 | -0.024334 | 0.07782 | -0.027466 | 0.041199 | -0.050354 | -0.032043 | -0.073242 | -0.036621 | 0.15106 | 0.050354 | 0.013733 | 0.13275 | 0.15564 | 0.17853 | 0.10529 | 61.4365 | -61.6287 | -61.6516 | 61.3632 | 61.3586 | 61.322 | -0.07782 | -0.11444 | 61.409 | -61.5509 | -61.4685 | 61.5509 | 61.5005 | 61.5738 | 0.091553 | 0.16479 | -0.073242 | -0.091553 | 0.14191 | 0.11902 | -0.068665 | 0.036621 | 61.3678 | 61.4456 | -61.5601 | -61.5875 | 61.3449 | 61.528 | 61.4731 | 61.5463
679.0312 | 123.23 | -61.4136 | 61.6013 | 0.022479 | 0.15302 | -1.0814 | 0.20611 | 0.019955 | -0.018063 | -0.016805 | 0.19771 | 0.1637 | 0.12774 | -0.035607 | 0.087628 | 0.016318 | -0.013653 | 0.054932 | -0.059509 | 0.009155 | -0.022888 | 0.004578 | -0.027466 | 0.013733 | 0.041199 | 0.059509 | -0.013733 | 0.041199 | 0.064087 | 0.068665 | 0.041199 | 61.4227 | -61.6608 | -61.6241 | 61.4182 | 61.4273 | 61.3861 | 0.004578 | -0.036621 | 61.3998 | -61.5417 | -61.5601 | 61.4777 | 61.4548 | 61.4822 | 0.054932 | 0.082398 | -0.004577 | -0.032043 | 0.07782 | 0.054932 | -0.068664 | 0.073242 | 61.3541 | 61.4731 | -61.5921 | -61.615 | 61.3907 | 61.4548 | 61.4685 | 61.4548
679.9531 | 123.2941 | -61.4273 | 61.5784 | -0.053815 | 0.1434 | -1.091 | 0.20611 | 0.0060704 | -0.012723 | -0.0093278 | 0.21297 | 0.17117 | 0.1256 | -0.029198 | 0.095104 | 0.016318 | -0.018994 | 0.022888 | -0.032043 | -0.004578 | -0.009155 | 0.013733 | -0.018311 | -0.009155 | -0.14191 | 0.018311 | -0.022888 | 0.032043 | 0.059509 | 0.073242 | 0.059509 | 61.4227 | -61.6104 | -61.5875 | 61.441 | 61.4182 | 61.409 | -0.004577 | -0.013733 | 61.4044 | -61.5601 | -61.5463 | 61.4868 | 61.4868 | 61.5005 | 0.082397 | 0.09613 | 0.018311 | -0.004577 | 0.082397 | 0.054931 | -0.027465 | 0.041199 | 61.3953 | 61.4456 | -61.5829 | -61.6013 | 61.4182 | 61.4594 | 61.4502 | 61.2854
681.0312 | 123.1796 | -61.4456 | 61.6196 | 0.17507 | 0.14554 | -1.1123 | 0.21039 | -0.017429 | -0.031949 | -0.0071918 | 0.19771 | 0.16797 | 0.14269 | -0.039879 | 0.095104 | 0.022726 | -0.013653 | -0.027466 | -0.009155 | -0.027466 | 0.082397 | 0.1236 | 0.054932 | 0.073242 | -0.054932 | 0.082397 | -0.045776 | -0.018311 | -0.004578 | -0.013733 | -0.013733 | 61.4182 | -61.6287 | -61.5372 | 61.5692 | 61.5189 | 61.5006 | 0.10071 | 0.082398 | 61.3998 | -61.5372 | -61.6379 | 61.441 | 61.4319 | 61.4319 | 0.032043 | 0.032043 | 0.15106 | 0.10986 | 0.041198 | 0.027465 | 0.018311 | 0.12817 | 61.4365 | 61.528 | -61.647 | -61.6653 | 61.528 | 61.4273 | 61.4182 | 61.3907
681.9531 | 123.2666 | -61.4319 | 61.5829 | -0.038556 | 0.15088 | -1.1177 | 0.21573 | 0.0060704 | -0.04263 | -0.0071918 | 0.16719 | 0.16476 | 0.13842 | -0.044152 | 0.096172 | 0.021658 | -0.014721 | 0.004578 | -0.022888 | 0.022888 | 0.009155 | 0.027466 | -0.022888 | 0.009155 | 0 | 0.068665 | 0.009155 | 0.027466 | 0.059509 | 0.050354 | 0.068665 | 61.4548 | -61.6058 | -61.5738 | 61.4594 | 61.441 | 61.409 | -0.013733 | -0.045776 | 61.441 | -61.5143 | -61.5555 | 61.4914 | 61.5006 | 61.4822 | 0.05951 | 0.041199 | 0.004578 | -0.013733 | 0.050354 | 0.018311 | -0.045776 | 0.05951 | 61.409 | 61.5006 | -61.5601 | -61.5738 | 61.441 | 61.4594 | 61.4365 | 61.4319
683.0312 | 123.1842 | -61.441 | 61.6013 | -0.038556 | 0.14661 | -1.0953 | 0.20932 | 0.012479 | -0.024472 | -0.0061228 | -0.10747 | 0.16797 | 0.14269 | -0.031334 | 0.095104 | 0.022726 | -0.044629 | -0.032043 | -0.018311 | -0.022888 | 0.082397 | 0.12817 | 0.073242 | 0.091553 | -0.091553 | 0.082397 | -0.054932 | 0 | -0.027466 | -0.050354 | -0.009155 | 61.4182 | -61.6196 | -61.5189 | 61.5692 | 61.5326 | 61.5143 | 0.11444 | 0.09613 | 61.3861 | -61.5189 | -61.6013 | 61.4136 | 61.4319 | 61.3907 | 0.045777 | 0.004578 | 0.15106 | 0.10528 | 0.027466 | 0.054932 | 0.004577 | 0.13733 | 61.4227 | 61.5234 | -61.6241 | -61.6562 | 61.5234 | 61.441 | 61.409 | 61.3495
683.9531 | 123.2483 | -61.4365 | 61.5875 | -0.053815 | 0.15302 | -1.1433 | 0.20718 | 0.0028664 | -0.0073817 | -0.00078276 | 0.04512 | 0.1637 | 0.12133 | -0.038811 | 0.10899 | 0.02059 | -0.016858 | 0.045776 | -0.07782 | 0.013733 | -0.050354 | -0.027466 | -0.050354 | -0.027466 | 0.073242 | 0.050354 | 0.004578 | 0.07782 | 0.086975 | 0.086975 | 0.10071 | 61.4502 | -61.6653 | -61.6379 | 61.409 | 61.409 | 61.3861 | -0.041199 | -0.064087 | 61.441 | -61.5372 | -61.5097 | 61.5234 | 61.5372 | 61.5234 | 0.09613 | 0.082397 | -0.041199 | -0.064087 | 0.082397 | 0.073242 | -0.091553 | 0.045776 | 61.3586 | 61.4868 | -61.5738 | -61.5829 | 61.3861 | 61.5143 | 61.4822 | 61.5097
685.0312 | 123.2025 | -61.4273 | 61.615 | 0.068255 | 0.14661 | -1.1658 | 0.20932 | 0.0017974 | -0.015927 | -0.012532 | 0.15193 | 0.15515 | 0.16619 | -0.023858 | 0.11113 | 0.035544 | -0.0083126 | -0.045776 | 0.018311 | -0.032043 | 0.082397 | 0.10986 | 0.059509 | 0.10529 | -0.091553 | 0.068665 | -0.050354 | -0.018311 | -0.027466 | -0.009155 | -0.013733 | 61.3953 | -61.5967 | -61.5326 | 61.5372 | 61.5326 | 61.4868 | 0.13733 | 0.091552 | 61.377 | -61.5463 | -61.6333 | 61.3998 | 61.4136 | 61.4182 | 0.036621 | 0.041199 | 0.14191 | 0.11444 | 0.022888 | 0.032043 | 0.050354 | 0.11902 | 61.4456 | 61.496 | -61.647 | -61.6653 | 61.5097 | 61.409 | 61.3815 | 61.3358
685.9531 | 123.2712 | -61.4502 | 61.5921 | -0.023297 | 0.14554 | -1.1583 | 0.20611 | 0.025296 | -0.016995 | -0.017873 | 0.274 | 0.15836 | 0.13629 | -0.019585 | 0.097241 | 0.019522 | 0.0077094 | 0.009155 | -0.027466 | 0.018311 | -0.009155 | 0.032043 | -0.013733 | 0 | -0.032043 | 0.041199 | 0.009155 | 0.059509 | 0.082397 | 0.068665 | 0.045776 | 61.4685 | -61.6196 | -61.6013 | 61.4822 | 61.4502 | 61.4365 | -0.018311 | -0.032044 | 61.4594 | -61.5509 | -61.5326 | 61.5326 | 61.496 | 61.5189 | 0.036621 | 0.05951 | 0.013732 | -0.027466 | 0.073242 | 0.050354 | -0.045777 | 0.032044 | 61.4227 | 61.4914 | -61.5738 | -61.5829 | 61.441 | 61.5097 | 61.4594 | 61.4182
687.0312 | 123.2391 | -61.3953 | 61.5829 | 0.12929 | 0.15302 | -1.185 | 0.20718 | -0.0078156 | -0.013791 | -0.0029188 | 0.21297 | 0.1637 | 0.15551 | -0.051629 | 0.089764 | 0.028067 | -0.0029716 | 0.059509 | -0.041199 | 0.027466 | -0.064087 | -0.036621 | -0.073242 | -0.013733 | 0.09613 | 0.045776 | 0.022888 | 0.022888 | 0.1831 | 0.1236 | 0.068665 | 61.4227 | -61.6241 | -61.647 | 61.3586 | 61.3815 | 61.322 | -0.041199 | -0.10071 | 61.4182 | -61.5372 | -61.5601 | 61.5784 | 61.4639 | 61.5189 | 0.045777 | 0.10071 | -0.064087 | -0.091553 | 0.16022 | 0 | -0.068665 | 0.022888 | 61.3541 | 61.441 | -61.5555 | -61.5601 | 61.3312 | 61.4182 | 61.4548 | 61.4914
687.9531 | 123.3307 | -61.3953 | 61.6104 | 0.068255 | 0.15195 | -1.3132 | 0.19971 | -0.0078156 | -0.0031087 | -0.024281 | 0.22823 | 0.16049 | 0.15444 | -0.029198 | 0.097241 | 0.032339 | -0.0093806 | 0.059509 | -0.054932 | 0.032043 | -0.059509 | -0.068665 | -0.064087 | -0.036621 | 0.091553 | 0.036621 | 0.004578 | 0.018311 | 0.23346 | 0.050354 | 0.036621 | 61.4273 | -61.6653 | -61.6699 | 61.3266 | 61.3586 | 61.3312 | -0.068664 | -0.09613 | 61.3998 | -61.5738 | -61.5921 | 61.6287 | 61.4319 | 61.4456 | 0.032043 | 0.045776 | -0.10071 | -0.091552 | 0.22888 | 0.013733 | -0.086975 | 0.032043 | 61.3403 | 61.4319 | -61.5784 | -61.6058 | 61.3358 | 61.4136 | 61.4548 | 61.4868
688.9531 | 123.2803 | -61.4136 | 61.5875 | 0.26662 | 0.14981 | -1.3452 | 0.20398 | 0.0017974 | -0.0084497 | -0.010396 | -0.092209 | 0.16583 | 0.13949 | -0.012108 | 0.10151 | 0.018454 | -0.0083126 | -0.004578 | -0.091553 | 0 | -0.045776 | -0.041199 | -0.050354 | -0.027466 | 0.082397 | 0.041199 | 0.022888 | 0.10071 | 0.086975 | 0.11902 | 0.050354 | 61.4136 | -61.6791 | -61.6333 | 61.3724 | 61.3861 | 61.3632 | -0.027466 | -0.050354 | 61.4365 | -61.5463 | -61.4868 | 61.5005 | 61.4639 | 61.5326 | 0.027466 | 0.096131 | -0.041199 | -0.045776 | 0.064087 | 0.07782 | -0.091553 | 0.018311 | 61.322 | 61.4548 | -61.5875 | -61.5646 | 61.3678 | 61.5143 | 61.409 | 61.496
690.0312 | 123.1979 | -61.4502 | 61.6241 | 0.052997 | 0.1434 | -1.3527 | 0.20932 | -0.0046106 | 0.01398 | -0.0061228 | 0.16719 | 0.16797 | 0.15338 | 0.022071 | 0.083355 | 0.02059 | -0.015789 | -0.018311 | -0.004578 | -0.009155 | 0.086975 | 0.11902 | 0.068665 | 0.091553 | -0.059509 | 0.068665 | -0.036621 | -0.022888 | -0.004578 | -0.004578 | -0.009155 | 61.441 | -61.6287 | -61.5372 | 61.5692 | 61.5417 | 61.5189 | 0.10071 | 0.07782 | 61.4136 | -61.5555 | -61.647 | 61.4456 | 61.441 | 61.4456 | 0.027466 | 0.032043 | 0.12817 | 0.09613 | 0.032043 | 0.013733 | 0.004577 | 0.10529 | 61.4456 | 61.5189 | -61.6333 | -61.6608 | 61.5372 | 61.4273 | 61.4319 | 61.3907

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2
-0.5271 | 20.932 | 19.9765 | 20.0139
0.4729 | 20.9303 | 19.9751 | 20.0127
1.4729 | 21.1659 | 19.9705 | 20.0163
2.4729 | 22.014 | 19.977 | 20.0115
3.4729 | 23.5721 | 19.9832 | 20.0177
4.4729 | 25.8041 | 19.9852 | 20.0197
5.4729 | 28.6248 | 19.9925 | 20.0315
6.4729 | 31.9177 | 20.0025 | 20.0336
7.4729 | 35.5965 | 20.0043 | 20.0478
8.4729 | 39.6361 | 20.0185 | 20.0694
9.4729 | 43.9309 | 20.0385 | 20.0977
10.4729 | 48.4709 | 20.0688 | 20.1299
11.4729 | 53.164 | 20.1013 | 20.1733
12.4729 | 58.0545 | 20.1387 | 20.2211
13.4729 | 63.0789 | 20.1852 | 20.2707
14.4729 | 68.2924 | 20.2314 | 20.3411
15.4729 | 73.6574 | 20.2893 | 20.4161
16.4729 | 79.1512 | 20.3621 | 20.5081
17.4729 | 84.7451 | 20.4378 | 20.6047
18.4729 | 90.3969 | 20.529 | 20.7201
19.4729 | 96.1702 | 20.6399 | 20.8329
20.4729 | 101.987 | 20.7592 | 20.9631
21.4729 | 107.8876 | 20.8775 | 21.0899
22.4729 | 113.8586 | 21.0209 | 21.2408
23.4729 | 119.8407 | 21.1644 | 21.4095
24.4729 | 125.9104 | 21.3272 | 21.591
25.4729 | 131.9739 | 21.504 | 21.7746
26.4729 | 137.9576 | 21.6973 | 21.9878
27.4729 | 144.0087 | 21.9275 | 22.209
28.4729 | 150.0895 | 22.1563 | 22.4482
29.4729 | 156.1367 | 22.4208 | 22.6924
30.4729 | 162.1628 | 22.7057 | 22.9565
31.4729 | 168.1771 | 23.0015 | 23.2435
32.4729 | 174.2727 | 23.3205 | 23.5445
33.4729 | 180.3471 | 23.672 | 23.8624
34.4729 | 186.2981 | 24.0369 | 24.1865
35.4729 | 192.2415 | 24.413 | 24.543
36.4729 | 198.0627 | 24.8135 | 24.9097
37.4729 | 203.8929 | 25.2288 | 25.2946
38.4729 | 209.7768 | 25.6868 | 25.7049
39.4729 | 215.742 | 26.1735 | 26.1456
40.4729 | 221.6728 | 26.6792 | 26.5924
41.4729 | 227.4655 | 27.2124 | 27.0518
42.4729 | 233.1499 | 27.7591 | 27.5427
43.4729 | 238.9018 | 28.332 | 28.049
44.4729 | 244.7718 | 28.931 | 28.5811
45.4729 | 250.6444 | 29.5443 | 29.1361
46.4729 | 256.448 | 30.1832 | 29.712
47.4729 | 262.2499 | 30.8336 | 30.3127
48.4729 | 268.0272 | 31.5087 | 30.9379
49.4729 | 273.8216 | 32.201 | 31.593
50.4729 | 279.5817 | 32.9184 | 32.2802
51.4729 | 285.1541 | 33.6711 | 32.9898
52.4729 | 290.6937 | 34.429 | 33.7511
53.4729 | 296.3765 | 35.1986 | 34.5049
54.4729 | 302.035 | 36.0115 | 35.3025
55.4729 | 307.5733 | 36.8428 | 36.1402
56.4729 | 313.0313 | 37.6965 | 36.9852
57.4729 | 318.4581 | 38.5817 | 37.8678
58.4729 | 323.9968 | 39.4806 | 38.7725
59.4729 | 329.5481 | 40.4141 | 39.6992
60.4729 | 334.9238 | 41.3838 | 40.6497
61.4729 | 340.155 | 42.3616 | 41.6315
62.4729 | 345.3869 | 43.3804 | 42.6415
63.4729 | 350.6998 | 44.4225 | 43.6741
64.4729 | 356.0223 | 45.4979 | 44.7297
65.4729 | 361.3372 | 46.5832 | 45.8168
66.4729 | 366.4807 | 47.6793 | 46.9315
67.4729 | 371.6309 | 48.8016 | 48.0626
68.4729 | 376.9468 | 49.9367 | 49.2208
69.4729 | 382.1594 | 51.0961 | 50.4054
70.4729 | 387.256 | 52.2915 | 51.619
71.4729 | 392.2519 | 53.5061 | 52.8656
72.4729 | 397.2482 | 54.7525 | 54.1375
73.4729 | 402.1648 | 56.0156 | 55.4495
74.4729 | 407.1433 | 57.3014 | 56.7843
75.4729 | 412.151 | 58.6002 | 58.1349
76.4729 | 417.0328 | 59.9168 | 59.5184
77.4729 | 421.723 | 61.2587 | 60.9264
78.4729 | 426.4481 | 62.6287 | 62.372
79.4729 | 431.0216 | 64.005 | 63.8108
80.4729 | 435.4987 | 65.3904 | 65.2868
81.4729 | 439.6447 | 66.8058 | 66.7714
82.4729 | 443.4765 | 68.2207 | 68.2518
83.4729 | 446.9631 | 69.6576 | 69.7499
84.4729 | 450.1885 | 71.0865 | 71.2476
85.4729 | 453.1728 | 72.5275 | 72.746
86.4729 | 456.005 | 73.9787 | 74.2584
87.4729 | 458.5124 | 75.4228 | 75.7686
88.4729 | 461.1668 | 76.879 | 77.2731
89.4729 | 463.8429 | 78.3175 | 78.756
90.4729 | 466.1865 | 79.7631 | 80.2423
91.4729 | 468.3252 | 81.2176 | 81.71
92.4729 | 470.0803 | 82.6744 | 83.1684
93.4729 | 471.7212 | 84.1819 | 84.6069
94.4729 | 472.8084 | 85.6746 | 86.0294
95.4729 | 473.7087 | 87.1745 | 87.4341
96.4729 | 474.3767 | 88.6811 | 88.8318
97.4729 | 474.924 | 90.2083 | 90.2135
98.4729 | 475.2041 | 91.751 | 91.5842
99.4729 | 475.4123 | 93.3085 | 92.9711
100.4729 | 475.6076 | 94.8896 | 94.3357
101.4729 | 475.7034 | 96.4926 | 95.7046
102.4729 | 475.58 | 98.1561 | 97.088
103.4729 | 475.4209 | 99.856 | 98.473
104.4729 | 475.1988 | 101.6225 | 99.8708
105.4729 | 474.9625 | 103.4447 | 101.3144
106.4729 | 474.6414 | 105.2994 | 102.7966
107.4729 | 474.4401 | 107.1908 | 104.3084
108.4729 | 474.2325 | 109.0945 | 105.8554
109.4729 | 473.9908 | 111.0231 | 107.4444
110.4729 | 473.716 | 113.0255 | 109.094
111.4729 | 473.539 | 115.0972 | 110.793
112.4729 | 473.1091 | 117.2767 | 112.5516
113.4729 | 472.833 | 119.564 | 114.3493
114.4729 | 472.5987 | 121.9234 | 116.1909
115.4729 | 472.2325 | 124.2512 | 118.0975
116.4729 | 472.0458 | 126.5608 | 120.0727
117.4729 | 472.0827 | 128.8757 | 122.0812
118.4729 | 472.1169 | 131.2236 | 124.0851
119.4729 | 472.1821 | 133.5814 | 126.0696
120.4729 | 472.2543 | 135.9524 | 128.0164
121.4729 | 472.3148 | 138.4319 | 129.917
122.4729 | 472.3867 | 141.0056 | 131.7836
123.4729 | 472.4453 | 143.6294 | 133.6203
124.4729 | 472.5834 | 146.2849 | 135.417
125.4729 | 472.7662 | 148.9262 | 137.1769
126.4729 | 472.9557 | 151.5382 | 138.913
127.4729 | 473.0161 | 154.1131 | 140.6446
128.4729 | 473.2207 | 156.6774 | 142.3356
129.4729 | 473.4094 | 159.2351 | 143.9847
130.4729 | 473.7887 | 161.7711 | 145.5836
131.4729 | 474.0145 | 164.2725 | 147.1438
132.4729 | 474.359 | 166.7311 | 148.6698
133.4729 | 474.6085 | 169.1492 | 150.1586
134.4729 | 474.8852 | 171.5229 | 151.6165
135.4729 | 475.0589 | 173.8864 | 153.0537
136.4729 | 475.192 | 176.1799 | 154.4747
137.4729 | 475.2847 | 178.3967 | 155.8434
138.4729 | 475.4787 | 180.5842 | 157.203
139.4729 | 475.6956 | 182.6608 | 158.5176
140.4729 | 475.759 | 184.6743 | 159.8031
141.4729 | 475.825 | 186.6521 | 161.0808
142.4729 | 475.9925 | 188.5472 | 162.3675
143.4729 | 476.0082 | 190.4022 | 163.6337
144.4729 | 475.9044 | 192.1523 | 164.8657
145.4729 | 475.8947 | 193.7567 | 166.0811
146.4729 | 475.8744 | 195.2953 | 167.3042
147.4729 | 475.9807 | 196.7788 | 168.5111
148.4729 | 476.0107 | 198.157 | 169.7462
149.4729 | 476.0919 | 199.4924 | 170.9735
150.4729 | 476.1111 | 200.8056 | 172.2192
151.4729 | 476.2494 | 202.0247 | 173.4824
152.4729 | 476.4278 | 203.1808 | 174.7422
153.4729 | 476.542 | 204.2599 | 176.0467
154.4729 | 476.5868 | 205.2834 | 177.396
155.4729 | 476.6944 | 206.2328 | 178.7927
156.4729 | 476.8143 | 207.152 | 180.4105
157.4729 | 476.9274 | 208.0185 | 182.0697
158.4729 | 477.0357 | 209.4175 | 183.3172
159.4729 | 477.0477 | 211.1586 | 184.3181
160.4729 | 477.1652 | 212.7184 | 185.4918
161.4729 | 477.2218 | 214.1822 | 186.8548
162.4729 | 477.4526 | 215.5544 | 188.3467
163.4729 | 477.5262 | 216.8913 | 189.9341
164.4729 | 477.7223 | 218.0059 | 191.5613
165.4729 | 477.9331 | 219.1698 | 193.3593
166.4729 | 477.9872 | 220.2325 | 195.2497
167.4729 | 478.0631 | 221.3519 | 197.2498
168.4729 | 478.1219 | 222.2479 | 199.1245
169.4729 | 478.0949 | 223.2879 | 200.9794
170.4729 | 478.0423 | 224.2329 | 202.8771
171.4729 | 478.217 | 225.1411 | 204.7044
172.4729 | 478.2922 | 226.0955 | 206.4853
173.4729 | 478.3958 | 226.9624 | 208.2378
174.4729 | 478.4687 | 227.7737 | 209.8818
175.4729 | 478.5806 | 228.7123 | 211.6004
176.4729 | 478.7455 | 229.4491 | 213.2733
177.4729 | 478.7043 | 230.2452 | 214.9471
178.4729 | 478.6809 | 230.9494 | 216.6265
179.4729 | 478.7498 | 231.6794 | 218.1864
180.4729 | 478.7637 | 232.4981 | 219.7261
181.4729 | 478.7519 | 233.23 | 221.2216
182.4729 | 478.7833 | 234.0349 | 222.5805
183.4729 | 478.6252 | 234.7336 | 223.9848
184.4729 | 478.5883 | 235.4741 | 225.2877
185.4729 | 478.4384 | 236.0854 | 226.5745
186.4729 | 478.1658 | 236.957 | 227.9093
187.4729 | 478.0891 | 237.5889 | 229.201
188.4729 | 478.0603 | 238.1766 | 230.3468
189.4729 | 478.1315 | 238.8837 | 231.5304
190.4729 | 477.8764 | 239.4323 | 232.7064
191.4729 | 477.6823 | 239.9696 | 233.7778
192.4729 | 477.6068 | 240.4724 | 234.8886
193.4729 | 477.5158 | 240.9754 | 235.9054
194.4729 | 477.4397 | 241.3884 | 236.83
195.4729 | 477.3493 | 241.7931 | 237.755
196.4729 | 477.3451 | 242.1713 | 238.5684
197.4729 | 477.2323 | 242.6355 | 239.4327
198.4729 | 477.2276 | 243.1956 | 240.2946
199.4729 | 477.1522 | 243.7417 | 241.271
200.4729 | 477.0759 | 244.3156 | 242.21
201.4729 | 477.0373 | 244.8637 | 243.0434
202.4729 | 476.9153 | 245.3903 | 243.9306
203.4729 | 476.8332 | 245.8153 | 244.9474
204.4729 | 476.8582 | 246.4066 | 245.9338
205.4729 | 476.8201 | 247.0896 | 246.8152
206.4729 | 476.8361 | 247.7095 | 247.7075
207.4729 | 476.8297 | 248.1558 | 248.6399
208.4729 | 476.7129 | 248.8295 | 249.4609
209.4729 | 476.6819 | 249.4631 | 250.2129
210.4729 | 476.705 | 249.923 | 251.0936
211.4729 | 476.7181 | 250.473 | 252.0394
212.4729 | 476.7208 | 251.0302 | 252.8796
213.4729 | 476.7273 | 251.6406 | 253.6463
214.4729 | 476.6838 | 252.2454 | 254.4405
215.4729 | 476.7514 | 252.8166 | 255.2825
216.4729 | 476.7447 | 253.3652 | 256.0988
217.4729 | 476.8227 | 253.9824 | 256.8249
218.4729 | 476.7848 | 254.5432 | 257.4777
219.4729 | 476.6801 | 254.9796 | 258.1312
220.4729 | 476.6955 | 255.3531 | 258.9221
221.4729 | 476.7497 | 255.9181 | 259.693
222.4729 | 476.8784 | 256.4719 | 260.3882
223.4729 | 477.0681 | 257.1289 | 261.1427
224.4729 | 477.1193 | 257.7098 | 261.8974
225.4729 | 477.0468 | 258.1318 | 262.6276
226.4729 | 476.9947 | 258.7269 | 263.256
227.4729 | 477.0753 | 259.3938 | 263.9515
228.4729 | 477.1743 | 260.0437 | 264.7223
229.4729 | 477.1208 | 260.689 | 265.4496
230.4729 | 477.0095 | 261.2374 | 266.1833
231.4729 | 476.9004 | 261.7965 | 266.9832
232.4729 | 476.8377 | 262.3662 | 267.7452
233.4729 | 476.7582 | 262.8957 | 268.5131
234.4729 | 476.7818 | 263.3831 | 269.1687
235.4729 | 476.6265 | 263.9361 | 269.8716
236.4729 | 476.6134 | 264.5384 | 270.6136
237.4729 | 476.6892 | 265.1066 | 271.3164
238.4729 | 476.8318 | 265.7363 | 272.0852
239.4729 | 476.9338 | 266.2993 | 272.8481
240.4729 | 476.9453 | 266.7735 | 273.6951
241.4729 | 476.8491 | 267.2114 | 274.4944
242.4729 | 476.6221 | 267.604 | 275.2238
243.4729 | 476.5403 | 268.0174 | 276.0324
244.4729 | 476.5755 | 268.4471 | 276.7471
245.4729 | 476.4602 | 268.8564 | 277.5279
246.4729 | 476.4345 | 269.4131 | 278.1474
247.4729 | 476.3607 | 269.8718 | 278.8185
248.4729 | 476.276 | 270.2993 | 279.3897
249.4729 | 476.2121 | 270.7094 | 279.9151
250.4729 | 476.1321 | 271.0885 | 280.5194
251.4729 | 476.1265 | 271.4965 | 281.1254
252.4729 | 476.107 | 271.8046 | 281.7249
253.4729 | 476.1617 | 272.2812 | 282.3684
254.4729 | 476.0546 | 272.7293 | 283.026
255.4729 | 476.0063 | 273.1663 | 283.621
256.4729 | 476.0138 | 273.6506 | 284.2037
257.4729 | 476.0698 | 274.1474 | 284.8007
258.4729 | 476.1569 | 274.6164 | 285.4573
259.4729 | 476.2287 | 275.1883 | 286.0876
260.4729 | 476.2306 | 275.6582 | 286.746
261.4729 | 476.3092 | 275.8748 | 287.3376
262.4729 | 476.2601 | 276.1618 | 287.9029
263.4729 | 476.2123 | 276.3073 | 288.5797
264.4729 | 476.0963 | 276.3914 | 289.2094
265.4729 | 476.137 | 276.566 | 289.7696
266.4729 | 476.0345 | 276.5875 | 290.4965
267.4729 | 475.9599 | 276.855 | 291.0121
268.4729 | 475.8221 | 277.1244 | 291.5803
269.4729 | 475.7688 | 277.2798 | 292.3069
270.4729 | 475.7815 | 277.5014 | 292.8851
271.4729 | 475.7694 | 277.708 | 293.3753
272.4729 | 475.776 | 277.9088 | 293.8238
273.4729 | 475.7573 | 278.1006 | 294.3056
274.4729 | 475.7187 | 278.3134 | 294.7598
275.4729 | 475.5933 | 278.4872 | 295.2581
276.4729 | 475.6004 | 278.6847 | 295.7713
277.4729 | 475.4737 | 278.894 | 296.2515
278.4729 | 475.5136 | 279.1263 | 296.9407
279.4729 | 475.5209 | 279.4853 | 297.4941
280.4729 | 475.5386 | 279.7818 | 298.0308
281.4729 | 475.5596 | 280.106 | 298.508
282.4729 | 475.4857 | 280.518 | 298.9386
283.4729 | 475.3199 | 280.8794 | 299.3371
284.4729 | 475.2704 | 281.2183 | 299.9311
285.4729 | 475.2309 | 281.5015 | 300.6123
286.4729 | 475.2357 | 281.8317 | 301.0676
287.4729 | 475.2831 | 282.1185 | 301.6581
288.4729 | 475.3572 | 282.4645 | 302.2821
289.4729 | 475.3307 | 282.7335 | 302.9777
290.4729 | 475.2504 | 283.0596 | 303.4144
291.4729 | 475.2508 | 283.3057 | 303.8891
292.4729 | 475.275 | 283.6071 | 304.3066
293.4729 | 475.4078 | 283.9666 | 304.9394
294.4729 | 475.3157 | 284.2462 | 305.53
295.4729 | 475.1835 | 284.5994 | 306.045
296.4729 | 475.1769 | 284.9697 | 306.7757
297.4729 | 475.308 | 285.3204 | 307.5063
298.4729 | 475.1796 | 285.707 | 308.2024
299.4729 | 474.9712 | 286.0394 | 309.072
300.4729 | 474.8883 | 286.3814 | 309.9222
301.4729 | 474.8877 | 286.7517 | 310.5275
302.4729 | 474.8497 | 287.1778 | 310.9835
303.4729 | 474.7971 | 287.533 | 311.566
304.4729 | 474.7409 | 287.8811 | 312.0556
305.4729 | 474.7052 | 288.2442 | 312.5653
306.4729 | 474.7033 | 288.5597 | 312.912
307.4729 | 474.7401 | 288.9068 | 313.2248
308.4729 | 474.6138 | 289.3017 | 313.7289
309.4729 | 474.7178 | 289.6696 | 314.1815
310.4729 | 474.7472 | 290.0467 | 314.7456
311.4729 | 474.6644 | 290.4045 | 315.1676
312.4729 | 474.6546 | 290.8113 | 315.6093
313.4729 | 474.5934 | 291.14 | 315.9831
314.4729 | 474.5936 | 291.4886 | 316.4034
315.4729 | 474.5585 | 291.8263 | 316.6825
316.4729 | 474.5672 | 292.2441 | 316.9961
317.4729 | 474.5736 | 292.6135 | 317.2684
318.4729 | 474.5605 | 292.9981 | 317.5748
319.4729 | 474.4982 | 293.3906 | 317.8571
320.4729 | 474.4498 | 293.8044 | 318.1005
321.4729 | 474.4648 | 294.1959 | 318.3565
322.4729 | 474.5219 | 294.6464 | 318.7421
323.4729 | 474.5767 | 295.0955 | 319.1793
324.4729 | 474.5781 | 295.5171 | 319.6331
325.4729 | 474.6082 | 295.9556 | 320.1649
326.4729 | 474.6003 | 296.3713 | 320.681
327.4729 | 474.4982 | 296.8013 | 321.0795
328.4729 | 474.5086 | 297.2253 | 321.4009
329.4729 | 474.578 | 297.6527 | 321.7696
330.4729 | 474.7287 | 298.073 | 322.1454
331.4729 | 474.7316 | 298.5134 | 322.5508
332.4729 | 474.7296 | 298.9428 | 322.9557
333.4729 | 474.712 | 299.337 | 323.3292
334.4729 | 474.7201 | 299.7754 | 323.7094
335.4729 | 474.7041 | 300.233 | 324.1513
336.4729 | 474.7994 | 300.6911 | 324.6293
337.4729 | 474.792 | 301.1421 | 324.9769
338.4729 | 474.8212 | 301.622 | 325.4407
339.4729 | 474.8535 | 302.0594 | 326.0541
340.4729 | 474.7914 | 302.5193 | 326.4912
341.4729 | 474.7337 | 302.9919 | 326.9237
342.4729 | 474.7373 | 303.4094 | 327.3982
343.4729 | 474.6741 | 303.8636 | 327.7455
344.4729 | 474.678 | 304.3348 | 328.1163
345.4729 | 474.6185 | 304.8325 | 328.5307
346.4729 | 474.6871 | 305.2984 | 329.063
347.4729 | 474.6991 | 305.7434 | 329.5069
348.4729 | 474.7793 | 306.2358 | 329.9419
349.4729 | 474.7186 | 306.7279 | 330.444
350.4729 | 474.7565 | 307.216 | 331.043
351.4729 | 474.6574 | 307.715 | 331.712
352.4729 | 474.6527 | 308.2092 | 332.3157
353.4729 | 474.7379 | 308.7376 | 332.9101
354.4729 | 474.7931 | 309.25 | 333.3854
355.4729 | 474.6882 | 309.758 | 333.9048
356.4729 | 474.6711 | 310.3164 | 334.3686
357.4729 | 474.6167 | 310.808 | 334.7897
358.4729 | 474.6399 | 311.3136 | 335.1562
359.4729 | 474.6679 | 311.8172 | 335.5409
360.4729 | 474.6536 | 312.3684 | 336.0213
361.4729 | 474.6294 | 312.9111 | 336.4678
362.4729 | 474.5842 | 313.4664 | 336.8648
363.4729 | 474.5842 | 314.0595 | 337.3233
364.4729 | 474.6517 | 314.5942 | 337.7595
365.4729 | 474.6876 | 315.0972 | 338.1282
366.4729 | 474.6136 | 315.6132 | 338.4497
367.4729 | 474.5837 | 316.165 | 338.8267
368.4729 | 474.4617 | 316.7159 | 339.1895
369.4729 | 474.4212 | 317.2365 | 339.4414
370.4729 | 474.3502 | 317.7987 | 339.7965
371.4729 | 474.3476 | 318.3817 | 340.1708
372.4729 | 474.474 | 319.0019 | 340.6576
373.4729 | 474.4866 | 319.5788 | 341.0369
374.4729 | 474.503 | 320.1699 | 341.4723
375.4729 | 474.5221 | 320.7494 | 341.7911
376.4729 | 474.5136 | 321.3505 | 342.2191
377.4729 | 474.503 | 321.9402 | 342.6083
378.4729 | 474.4928 | 322.5665 | 343.0709
379.4729 | 474.6246 | 323.2349 | 343.5415
380.4729 | 474.7351 | 323.8762 | 343.9449
381.4729 | 474.9013 | 324.5069 | 344.4275
382.4729 | 474.9827 | 325.1049 | 344.7639
383.4729 | 475.0152 | 325.7238 | 345.1365
384.4729 | 475.0343 | 326.3418 | 345.4847
385.4729 | 475.0599 | 326.9476 | 345.7104
386.4729 | 474.9941 | 327.5679 | 346.0427
387.4729 | 474.9998 | 328.1803 | 346.4778
388.4729 | 474.994 | 328.8158 | 346.869
389.4729 | 474.8233 | 329.4637 | 347.3248
390.4729 | 474.8078 | 330.1207 | 347.7506
391.4729 | 474.7075 | 330.7297 | 348.1432
392.4729 | 474.7919 | 331.3876 | 348.6285
393.4729 | 474.7535 | 332.0215 | 349.1325
394.4729 | 474.7185 | 332.6757 | 349.6433
395.4729 | 474.6532 | 333.2826 | 350.0465
396.4729 | 474.6253 | 333.9506 | 350.5851
397.4729 | 474.6406 | 334.6123 | 351.0915
398.4729 | 474.694 | 335.2375 | 351.5153
399.4729 | 474.6373 | 335.8716 | 351.84
400.4729 | 474.5598 | 336.5202 | 352.2929
401.4729 | 474.4128 | 337.1717 | 352.7659
402.4729 | 474.3891 | 337.7902 | 353.1056
403.4729 | 474.4765 | 338.416 | 353.5193
404.4729 | 474.5298 | 339.0703 | 354.0152
405.4729 | 474.5129 | 339.7107 | 354.3912
406.4729 | 474.4912 | 340.3324 | 354.6856
407.4729 | 474.447 | 340.9912 | 355.0717
408.4729 | 474.4417 | 341.6286 | 355.4387
409.4729 | 474.332 | 342.2799 | 355.826
410.4729 | 474.2752 | 342.9053 | 356.1088
411.4729 | 474.1525 | 343.5679 | 356.4955
412.4729 | 474.1024 | 344.2304 | 356.9282
413.4729 | 474.1153 | 344.8732 | 357.3304
414.4729 | 474.0028 | 345.4991 | 357.6699
415.4729 | 474.0058 | 346.1316 | 358.0139
416.4729 | 474.0599 | 346.7456 | 358.3106
417.4729 | 474.0009 | 347.375 | 358.7252
418.4729 | 474.108 | 348.0288 | 359.0861
419.4729 | 474.1316 | 348.6833 | 359.4171
420.4729 | 474.0578 | 349.2933 | 359.6165
421.4729 | 474.0352 | 349.9265 | 359.9347
422.4729 | 473.9371 | 350.5764 | 360.3432
423.4729 | 473.8621 | 351.2188 | 360.6975
424.4729 | 473.9327 | 351.8598 | 361.1165
425.4729 | 473.963 | 352.4759 | 361.3532
426.4729 | 474.1526 | 353.1488 | 361.7269
427.4729 | 474.1758 | 353.7732 | 361.9861
428.4729 | 474.2176 | 354.4165 | 362.4117
429.4729 | 474.1432 | 355.0197 | 362.7031
430.4729 | 474.13 | 355.6739 | 363.009
431.4729 | 474.212 | 356.3134 | 363.3352
432.4729 | 474.3152 | 356.9621 | 363.7723
433.4729 | 474.3541 | 357.6177 | 364.2599
434.4729 | 474.4015 | 358.2503 | 364.5551
435.4729 | 474.448 | 358.8909 | 364.852
436.4729 | 474.5048 | 359.4757 | 364.9417
437.4729 | 474.4126 | 360.094 | 365.2005
438.4729 | 474.4705 | 360.7364 | 365.4122
439.4729 | 474.4067 | 361.3646 | 365.7014
440.4729 | 474.3561 | 361.9989 | 366.0271
441.4729 | 474.3162 | 362.6787 | 366.483
442.4729 | 474.1605 | 363.2952 | 366.8386
443.4729 | 474.1294 | 363.9269 | 367.1896
444.4729 | 474.1373 | 364.5433 | 367.4476
445.4729 | 474.2637 | 365.1786 | 367.8286
446.4729 | 474.2853 | 365.8185 | 368.2905
447.4729 | 474.3599 | 366.4717 | 368.7757
448.4729 | 474.3393 | 367.0858 | 369.1377
449.4729 | 474.318 | 367.7176 | 369.4697
450.4729 | 474.2115 | 368.3426 | 370.0226
451.4729 | 474.1844 | 368.9866 | 370.5387
452.4729 | 474.185 | 369.6286 | 370.9589
453.4729 | 474.08 | 370.2667 | 371.3609
454.4729 | 474.0647 | 370.882 | 371.7809
455.4729 | 474.0588 | 371.4922 | 372.1344
456.4729 | 474.0637 | 372.1205 | 372.4511
457.4729 | 474.0511 | 372.7291 | 372.8335
458.4729 | 474.0908 | 373.3419 | 373.1049
459.4729 | 474.0896 | 373.9629 | 373.4231
460.4729 | 473.9676 | 374.5845 | 373.8512
461.4729 | 473.9516 | 375.1996 | 374.2454
462.4729 | 473.9915 | 375.8059 | 374.6524
463.4729 | 473.9782 | 376.4357 | 375.1261
464.4729 | 473.9459 | 377.0495 | 375.557
465.4729 | 473.8303 | 377.6507 | 375.9391
466.4729 | 473.8506 | 378.2072 | 376.1709
467.4729 | 473.9348 | 378.7656 | 376.4259
468.4729 | 473.9892 | 379.3682 | 376.762
469.4729 | 473.9935 | 379.9353 | 377.1534
470.4729 | 473.8472 | 380.5377 | 377.6956
471.4729 | 473.8473 | 381.0831 | 377.9991
472.4729 | 473.8861 | 381.6278 | 378.3114
473.4729 | 473.908 | 382.1677 | 378.539
474.4729 | 473.9575 | 382.6687 | 378.8253
475.4729 | 474.0009 | 383.207 | 379.167
476.4729 | 473.9603 | 383.7539 | 379.5118
477.4729 | 473.9767 | 384.2956 | 379.8584
478.4729 | 473.9796 | 384.8469 | 380.3372
479.4729 | 473.9867 | 385.403 | 380.8291
480.4729 | 474.0293 | 385.9337 | 381.1063
481.4729 | 474.0797 | 386.4864 | 381.4968
482.4729 | 474.1657 | 386.9854 | 381.6626
483.4729 | 474.1601 | 387.5429 | 381.9802
484.4729 | 474.1342 | 388.0896 | 382.3773
485.4729 | 474.2413 | 388.6304 | 382.7449
486.4729 | 474.2922 | 389.1612 | 383.0234
487.4729 | 474.3272 | 389.7091 | 383.4835
488.4729 | 474.2471 | 390.2404 | 383.9318
489.4729 | 474.2121 | 390.782 | 384.5378
490.4729 | 474.0996 | 391.3279 | 385.1173
491.4729 | 474.0063 | 391.8522 | 385.5888
492.4729 | 474.0686 | 392.3885 | 386.0805
493.4729 | 474.0823 | 392.9016 | 386.5455
494.4729 | 474.0576 | 393.3841 | 386.9187
495.4729 | 474.0104 | 393.8644 | 387.2209
496.4729 | 474.0068 | 394.3782 | 387.5546
497.4729 | 473.9657 | 394.8934 | 387.941
498.4729 | 474.0554 | 395.4321 | 388.3878
499.4729 | 474.0713 | 395.8902 | 388.6628
500.4729 | 474.0188 | 396.347 | 388.9484
501.4729 | 473.9532 | 396.8213 | 389.2373
502.4729 | 473.8742 | 397.3254 | 389.4986
503.4729 | 473.7121 | 397.8172 | 389.7738
504.4729 | 473.6085 | 398.2914 | 390.0873
505.4729 | 473.4761 | 398.7714 | 390.5199
506.4729 | 473.3608 | 399.2364 | 390.9141
507.4729 | 473.3533 | 399.7052 | 391.3636
508.4729 | 473.3294 | 400.1562 | 391.8277
509.4729 | 473.2296 | 400.591 | 392.293
510.4729 | 473.1637 | 401.0511 | 392.8438
511.4729 | 473.1886 | 401.5032 | 393.297
512.4729 | 473.2319 | 401.9431 | 393.762
513.4729 | 473.2704 | 402.382 | 394.2209
514.4729 | 473.261 | 402.7311 | 394.7279
515.4729 | 473.3209 | 403.1154 | 395.2155
516.4729 | 473.4536 | 403.302 | 396.0847
517.4729 | 473.5792 | 403.7714 | 397.0287
518.4729 | 473.7214 | 404.2788 | 398.1788
519.4729 | 473.822 | 405.1239 | 399.3579
520.4729 | 473.9196 | 406.1345 | 400.7161
521.4729 | 473.9307 | 407.2512 | 402.095
522.4729 | 473.9805 | 408.4349 | 403.7643
523.4729 | 474.0315 | 409.7387 | 405.7102
524.4729 | 474.1903 | 410.8746 | 407.974
525.4729 | 474.3164 | 412.0674 | 410.8907
526.4729 | 474.2492 | 413.2525 | 415.2901
527.4729 | 474.2486 | 414.4064 | 421.6929
528.4729 | 474.3327 | 415.6503 | 429.0231
529.4729 | 474.4978 | 416.7072 | 436.8051
530.4729 | 474.6726 | 417.9045 | 444.7251
531.4729 | 474.7113 | 419.2522 | 451.5532
532.4729 | 474.7032 | 420.5405 | 457.4405
533.4729 | 474.7057 | 421.7623 | 463.5204
534.4729 | 474.7183 | 423.0277 | 469.6579
535.4729 | 474.6032 | 424.4334 | 475.5183
536.4729 | 474.5688 | 425.609 | 481.8497
537.4729 | 474.5639 | 426.7036 | 488.0705
538.4729 | 474.7049 | 427.9637 | 494.6578
539.4729 | 475.0024 | 429.0866 | 498.7647
540.4729 | 475.2334 | 430.1249 | 503.2302
541.4729 | 475.3863 | 431.1308 | 508.2434
542.4729 | 475.5592 | 431.993 | 510.5044
543.4729 | 475.634 | 432.8379 | 514.1056
544.4729 | 475.5086 | 433.6083 | 517.9319
545.4729 | 475.4226 | 434.4963 | 522.0509
546.4729 | 475.4279 | 435.1874 | 525.6739
547.4729 | 475.3307 | 435.824 | 528.03
548.4729 | 475.2184 | 436.432 | 529.3588
549.4729 | 475.1771 | 436.9874 | 532.5093
550.4729 | 475.1126 | 437.3193 | 535.6895
551.4729 | 475.0019 | 437.6101 | 534.4774
552.4729 | 474.9104 | 437.9626 | 534.0398
553.4729 | 474.8142 | 438.1886 | 539.2281
554.4729 | 474.7021 | 438.3582 | 542.4761
555.4729 | 474.5646 | 438.7193 | 550.7832
556.4729 | 474.4109 | 439.0328 | 554.4257
557.4729 | 474.1891 | 439.8698 | 559.4039
558.4729 | 473.8281 | 440.6525 | 564.728
559.4729 | 473.46 | 440.8318 | 563.7305
560.4729 | 473.108 | 440.5686 | 561.6104
561.4729 | 472.9604 | 440.1201 | 559.5086
562.4729 | 472.7198 | 439.723 | 556.3001
563.4729 | 472.3946 | 439.422 | 553.6966
564.4729 | 472.1449 | 439.1031 | 553.1831
565.4729 | 471.8058 | 438.5218 | 553.9236
566.4729 | 471.4095 | 437.7691 | 547.2769
567.4729 | 471.0324 | 436.7896 | 535.5577
568.4729 | 470.7085 | 435.8403 | 519.076
569.4729 | 470.6513 | 434.8551 | 521.2546
570.4729 | 470.4852 | 435.5547 | 520.2924
571.4729 | 470.3555 | 436.2689 | 517.1561
572.4729 | 470.15 | 436.1272 | 507.35
573.4729 | 470.0131 | 435.4139 | 504.2821
574.4729 | 469.883 | 435.3899 | 508.7422
575.4729 | 469.7667 | 435.1781 | 505.9325
576.4729 | 469.7088 | 435.3713 | 504.8436
577.4729 | 469.5493 | 435.8207 | 495.4107
578.4729 | 469.4134 | 436.6549 | 493.4569
579.4729 | 469.3161 | 435.5021 | 485.5009
580.4729 | 469.1391 | 435.3327 | 479.5015
581.4729 | 469.0493 | 436.9602 | 481.043
582.4729 | 468.9109 | 436.9839 | 477.3035
583.4729 | 468.7501 | 435.9628 | 471.9573
584.4729 | 468.6676 | 434.4854 | 473.105
585.4729 | 468.466 | 431.6006 | 474.3953
586.4729 | 468.3109 | 430.7771 | 470.5177
587.4729 | 468.206 | 426.2213 | 446.9576
588.4729 | 468.1445 | 422.6099 | 443.8421
589.4729 | 468.0484 | 422.3026 | 444.9011
590.4729 | 468.0076 | 419.0316 | 437.0321
591.4729 | 467.9806 | 418.3015 | 444.1134
592.4729 | 468.0269 | 422.5321 | 451.0435
593.4729 | 468.2782 | 442.4937 | 458.6165
594.4729 | 468.2943 | 445.4594 | 464.0673
595.4729 | 468.2846 | 455.0708 | 473.2599
596.4729 | 468.4307 | 471.8772 | 479.4131
597.4729 | 468.5353 | 475.4464 | 481.1993
598.4729 | 468.5265 | 478.9761 | 475.3435
599.4729 | 468.6076 | 440.7693 | 396.4495
600.4729 | 468.729 | 443.6146 | 385.8128
601.4729 | 468.6764 | 558.4418 | 589.6348
602.4729 | 468.7414 | 540.5339 | 577.3565
603.4729 | 469.0085 | 547.8368 | 578.601
604.4729 | 469.2111 | 556.5613 | 585.5037
605.4729 | 469.3008 | 564.2374 | 589.4249
606.4729 | 469.3409 | 579.4187 | 684.7574
607.4729 | 469.325 | 579.1573 | 590.9017
608.4729 | 469.3017 | 587.8627 | 591.4597
609.4729 | 469.3869 | 601.8905 | 634.2315
610.4729 | 469.46 | 612.0764 | 639.2067
611.4729 | 469.5027 | 619.1523 | 634.302
612.4729 | 469.6587 | 614.5109 | 558.6488
613.4729 | 469.9627 | 611.0009 | 534.7588
614.4729 | 470.2136 | 616.8582 | 551.3847
615.4729 | 470.3863 | 619.9415 | 554.0469
616.4729 | 470.4837 | 629.7237 | 554.0513
617.4729 | 470.6176 | 630.4606 | 552.9833
618.4729 | 470.8902 | 634.0509 | 551.9958
619.4729 | 471.1254 | 634.2124 | 550.2137
620.4729 | 471.1353 | 637.6421 | 550.9353
621.4729 | 471.2844 | 644.089 | 550.7407
622.4729 | 471.2721 | 650.727 | 551.7996
623.4729 | 471.2348 | 651.613 | 551.6467
624.4729 | 471.2674 | 651.4322 | 552.4801
625.4729 | 471.1702 | 656.4512 | 552.417
626.4729 | 471.118 | 653.819 | 552.2892
627.4729 | 470.9937 | 653.2982 | 552.7319
628.4729 | 470.9197 | 651.1381 | 553.3848
629.4729 | 470.9826 | 649.5495 | 552.2791
630.4729 | 471.0237 | 649.4687 | 553.1356
631.4729 | 471.0318 | 653.6048 | 553.3743
632.4729 | 471.0943 | 661.4312 | 554.7741
633.4729 | 471.1055 | 654.9157 | 554.1362
634.4729 | 471.0682 | 649.1575 | 554.2631
635.4729 | 471.0587 | 647.528 | 552.4317
636.4729 | 470.9782 | 640.9873 | 550.2144
637.4729 | 470.9817 | 641.3139 | 549.6693
638.4729 | 470.8641 | 642.1922 | 548.8125
639.4729 | 470.8669 | 638.7541 | 548.3023
640.4729 | 470.7824 | 637.2082 | 550.5062
641.4729 | 470.6584 | 643.9811 | 554.3637
642.4729 | 470.609 | 647.9238 | 558.8603
643.4729 | 470.6308 | 650.5345 | 561.5196
644.4729 | 470.578 | 647.8016 | 561.1006
645.4729 | 470.4463 | 647.3202 | 561.532
646.4729 | 470.3186 | 648.032 | 563.916
647.4729 | 470.4236 | 649.6342 | 566.6973
648.4729 | 470.3549 | 649.0299 | 571.8426
649.4729 | 470.4083 | 647.4448 | 573.8391
650.4729 | 470.3866 | 639.6881 | 572.0121
651.4729 | 470.333 | 636.7154 | 572.1356
652.4729 | 470.3058 | 640.426 | 574.7395
653.4729 | 470.3594 | 645.1034 | 579.0412
654.4729 | 470.3179 | 647.0461 | 581.6214
655.4729 | 470.3206 | 651.8679 | 584.369
656.4729 | 470.4459 | 657.41 | 586.249
657.4729 | 470.3409 | 659.67 | 584.7442
658.4729 | 470.2925 | 667.7393 | 589.3822
659.4729 | 470.2493 | 668.3574 | 589.921
660.4729 | 470.0292 | 671.5593 | 593.4337
661.4729 | 469.8689 | 673.5481 | 595.5808
662.4729 | 469.6686 | 675.3593 | 597.2578
663.4729 | 469.5529 | 680.0916 | 599.2126
664.4729 | 469.4331 | 680.4983 | 599.5145
665.4729 | 469.4725 | 680.0527 | 599.49
666.4729 | 469.4402 | 678.0015 | 597.5094
667.4729 | 469.3008 | 677.639 | 599.3877
668.4729 | 469.1216 | 678.2299 | 600.3593
669.4729 | 468.9744 | 678.0112 | 599.8758
670.4729 | 468.908 | 679.2351 | 599.7571
671.4729 | 468.8542 | 682.1127 | 600.3312
672.4729 | 468.7922 | 681.676 | 600.7591
673.4729 | 468.716 | 680.3447 | 600.0926
674.4729 | 468.6426 | 677.9342 | 596.5624
675.4729 | 468.5457 | 676.3359 | 598.2081
676.4729 | 468.5696 | 679.9258 | 599.7698
677.4729 | 468.6315 | 679.4503 | 600.9041
678.4729 | 468.5861 | 681.0223 | 601.9979
679.4729 | 468.5273 | 679.5234 | 599.7548
680.4729 | 468.4111 | 677.9763 | 601.4714
681.4729 | 468.2693 | 676.5939 | 601.5947
682.4729 | 468.2162 | 673.385 | 600.5343
683.4729 | 468.0738 | 673.3042 | 602.4939
684.4729 | 467.9595 | 676.0493 | 606.5689
685.4729 | 467.8073 | 680.2419 | 610.6247
686.4729 | 467.6595 | 679.086 | 610.8795
687.4729 | 467.4759 | 679.9161 | 612.8449
688.4729 | 467.3113 | 680.5308 | 615.6353
689.4729 | 467.1639 | 682.2807 | 618.6974
690.4729 | 467.0892 | 681.8392 | 617.4135