## Test Conditions
DESIREE-FIRE Test Number 32 - Circuit Simulator Data Only
Test Date: | 2009-09-24
DCSim DAQ Start Time | 13:22
DCSim Time for Synchronization | 13:40
Heat Source Synchronization | 10:15 | minutes:seconds
Heat Source DAQ Start Time | 13:30
Heat Source Start Time | 13:44
DCSim Offset | 0:22 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 1290 | seconds
Heat Source Offset | 0:13 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 795 | seconds
Heat Source Stop Time | 13:57
Test Duration | 0:13 | minutes:seconds
| 810 | seconds
CT500 Turns | 2 |  | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 Turns | 5
Pre-Test Baseline: | Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SWGR Close | PVC/PVC, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
SWGR Trip | PVC/PVC, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SWGR_CT500 | SWGR-a_CT35_1_PC | SWGR-a_CT35_2_N1 | SWGR-b_CT35_1_PT | SWGR-b_CT35_2_G | SWGR-b_CT35_3_R | SWGR-b_CT35_4_N2 | SWGR-a_VT7_1_C1 | SWGR-a_VTU_1_PC | SWGR-a_VTU_2_N1 | SWGR-b_VT7_1_G | SWGR-b_VT7_2_R | SWGR-b_VT7_3_T | SWGR-b_VT7_4_SP | SWGR-b_VT7_5_SP | SWGR-b_VTU_1_PT | SWGR-b_VTU_2_N2 | {SWGR-C} V(N1) - V(Batt -) | {SWGR-C} V(PC) - V(Batt +) | {SWGR-C} V(C1) - V(Batt +) | {SWGR-T} V(G) - V(Batt -) | {SWGR-T} V(R) - V(Batt +) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-T} V(PT) - V(Batt +) | {SWGR-C} V(C1) - V(N1) | {SWGR-T} V(SP1) - V(Batt -) | {SWGR-T} V(SP2) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PC) - V(Batt -) | {SWGR-T} V(C1) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-C} V(PC) - V(Batt -) | {SWGR-C} V(C1) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-C} V(N1) - V(Batt +) | {SWGR-T} V(N2) - V(Batt +)
-0.9375 | 122.7814 | -60.7224 | 61.8988 | -0.29755 | 0.01311 | 0.016735 | -0.0031873 | 0.066574 | 0.00069212 | 0.067885 | -60.8231 | 61.7615 | -60.8505 | -60.91 | 61.5967 | 0.068665 | 0.11902 | 0.13733 | 61.8073 | -60.8871 | -0.12817 | -0.13733 | -0.10071 | -0.18768 | -0.30212 | -0.16479 | -0.091553 | 0.027466 | 60.8414 | 60.8597 | 122.319 | 122.4838 | -0.10071 | 122.5296 | 60.791 | -0.16479 | 122.4838 | -0.10071 | 60.791 | 122.319 | 122.5296 | -122.7493 | -122.7859
0.078125 | 122.731 | -60.7636 | 61.8622 | -6e-08 | 0.013324 | 0.016522 | 0.0034351 | 0.06871 | -0.00058968 | 0.067458 | -60.8322 | 61.8027 | -60.8414 | -60.9421 | 61.5326 | -0.013733 | 0.050354 | -0.041199 | 61.7844 | -60.9421 | -0.07782 | -0.05951 | -0.068664 | -0.17853 | -0.32959 | -0.17853 | -0.07782 | 0.009156 | 60.8139 | 60.7224 | 122.2961 | 122.5662 | -0.068664 | 122.5479 | 60.7498 | -0.17853 | 122.5662 | -0.068664 | 60.7498 | 122.2961 | 122.5479 | -122.7036 | -122.8043
1.0625 | 122.9141 | -60.6903 | 61.8301 | -0.23651 | 0.01076 | 0.019726 | -0.0029735 | 0.066574 | -0.0022987 | 0.06938 | -60.7498 | 61.7111 | -60.8505 | -60.8597 | 61.6837 | 0.14191 | -0.032043 | 0.24261 | 61.7569 | -60.8688 | -0.16022 | -0.11902 | -0.059509 | -0.16937 | -0.14648 | -0.17853 | -0.073242 | 0.10071 | 60.6583 | 60.9329 | 122.374 | 122.4014 | -0.059509 | 122.4472 | 60.8322 | -0.17853 | 122.4014 | -0.059509 | 60.8322 | 122.374 | 122.4472 | -122.6807 | -122.699
2.0625 | 122.8363 | -60.7132 | 61.9217 | -0.19074 | 0.012897 | 0.020367 | 0.0047169 | 0.067855 | 0.0011193 | 0.065108 | -60.7864 | 61.7752 | -60.878 | -60.878 | 61.615 | 0.09613 | 0.059509 | -0.059509 | 61.7523 | -60.9192 | -0.16479 | -0.14648 | -0.073242 | -0.16479 | -0.3067 | -0.20599 | -0.16937 | 0.091553 | 60.7727 | 60.6537 | 122.3282 | 122.4884 | -0.073242 | 122.4655 | 60.8093 | -0.20599 | 122.4884 | -0.073242 | 60.8093 | 122.3282 | 122.4655 | -122.7997 | -122.8409
3.0625 | 122.9279 | -60.672 | 61.8668 | -0.17548 | 0.010119 | 0.017163 | -0.0031873 | 0.06636 | -0.0010169 | 0.067031 | -60.7727 | 61.6882 | -60.8368 | -60.8185 | 61.6791 | 0.17395 | -0.091553 | 0.21973 | 61.7386 | -60.8551 | -0.1648 | -0.17853 | -0.10071 | -0.14648 | -0.18768 | -0.18311 | -0.12817 | 0.064087 | 60.5804 | 60.8917 | 122.3511 | 122.3602 | -0.10071 | 122.4106 | 60.8459 | -0.18311 | 122.3602 | -0.10071 | 60.8459 | 122.3511 | 122.4106 | -122.7036 | -122.7219
4.0625 | 122.8958 | -60.672 | 61.8347 | -0.21362 | 0.010119 | 0.015454 | -0.0048961 | 0.064651 | 0.00069212 | 0.068312 | -60.7361 | 61.7157 | -60.8231 | -60.8276 | 61.6928 | 0.17853 | -0.027466 | 0.23346 | 61.734 | -60.8734 | -0.15106 | -0.11902 | -0.064087 | -0.15564 | -0.14191 | -0.20142 | -0.10071 | 0.086975 | 60.6445 | 60.9055 | 122.3648 | 122.3877 | -0.064087 | 122.406 | 60.8505 | -0.20142 | 122.3877 | -0.064087 | 60.8505 | 122.3648 | 122.406 | -122.6578 | -122.7081
5.0625 | 122.7722 | -60.7224 | 61.9034 | -0.32043 | 0.010547 | 0.014172 | 0.0012989 | 0.065505 | -0.0012305 | 0.068312 | -60.8551 | 61.7889 | -60.8551 | -60.9238 | 61.5784 | 0.064087 | 0.15564 | 0.10986 | 61.7844 | -60.9146 | -0.13275 | -0.11444 | -0.13275 | -0.20142 | -0.32501 | -0.19226 | -0.11902 | 0 | 60.878 | 60.8322 | 122.3007 | 122.5113 | -0.13275 | 122.5067 | 60.7864 | -0.19226 | 122.5113 | -0.13275 | 60.7864 | 122.3007 | 122.5067 | -122.7585 | -122.818
6.0625 | 122.8958 | -60.6674 | 61.8576 | -0.24414 | 0.010974 | 0.015026 | -0.0038281 | 0.064865 | -0.0033667 | 0.069808 | -60.7407 | 61.6882 | -60.8322 | -60.8139 | 61.6974 | 0.16937 | -0.041199 | 0.24261 | 61.7477 | -60.8826 | -0.16479 | -0.16937 | -0.073243 | -0.14648 | -0.16022 | -0.21515 | -0.10986 | 0.091552 | 60.6262 | 60.91 | 122.3648 | 122.3557 | -0.073243 | 122.4152 | 60.8368 | -0.21515 | 122.3557 | -0.073243 | 60.8368 | 122.3648 | 122.4152 | -122.6898 | -122.7402
7.0625 | 122.8088 | -60.7132 | 61.8851 | -0.32043 | 0.010974 | 0.014385 | -0.00019653 | 0.064651 | 0.0015467 | 0.067244 | -60.791 | 61.7386 | -60.8368 | -60.965 | 61.6974 | 0.20142 | 0.091553 | 0.15564 | 61.7844 | -60.8871 | -0.1236 | -0.14649 | -0.07782 | -0.25177 | -0.18768 | -0.17395 | -0.10071 | 0.045776 | 60.8047 | 60.8688 | 122.4106 | 122.4518 | -0.07782 | 122.4976 | 60.9146 | -0.17395 | 122.4518 | -0.07782 | 60.9146 | 122.4106 | 122.4976 | -122.7219 | -122.7722
8.0625 | 122.7814 | -60.7178 | 61.8896 | -0.30518 | 0.011401 | 0.016522 | 0.0017261 | 0.063583 | -0.00037588 | 0.068099 | -60.8093 | 61.7844 | -60.8231 | -60.9329 | 61.5784 | 0.07782 | 0.14648 | 0.10986 | 61.8164 | -60.9146 | -0.10529 | -0.10529 | -0.091553 | -0.21515 | -0.31128 | -0.19684 | -0.073242 | 0.013733 | 60.8643 | 60.8276 | 122.2961 | 122.5021 | -0.091553 | 122.5342 | 60.7956 | -0.19684 | 122.5021 | -0.091553 | 60.7956 | 122.2961 | 122.5342 | -122.7127 | -122.8043
9.0625 | 122.8683 | -60.6995 | 61.8484 | -0.053406 | 0.010974 | 0.015881 | -0.00041013 | 0.065505 | 0.00026492 | 0.068526 | -60.8002 | 61.6928 | -60.8322 | -60.8871 | 61.6333 | 0.073242 | -0.068665 | 0.12817 | 61.7249 | -60.8688 | -0.13275 | -0.15564 | -0.10071 | -0.18768 | -0.21515 | -0.16937 | -0.1236 | 0.032043 | 60.6308 | 60.8276 | 122.3328 | 122.3923 | -0.10071 | 122.4243 | 60.7727 | -0.16937 | 122.3923 | -0.10071 | 60.7727 | 122.3328 | 122.4243 | -122.6807 | -122.7173
10.0625 | 122.7676 | -60.7269 | 61.8851 | -0.30518 | 0.013965 | 0.015026 | 0.00023067 | 0.065505 | -0.0016577 | 0.06874 | -60.8368 | 61.7935 | -60.8688 | -60.9055 | 61.5646 | 0.054932 | 0.16022 | 0.091553 | 61.7523 | -60.9055 | -0.14191 | -0.091553 | -0.10986 | -0.17853 | -0.32044 | -0.17853 | -0.13275 | 0.032043 | 60.8871 | 60.8185 | 122.2916 | 122.5204 | -0.10986 | 122.4792 | 60.7819 | -0.17853 | 122.5204 | -0.10986 | 60.7819 | 122.2916 | 122.4792 | -122.7539 | -122.7905
11.0625 | 122.8867 | -60.7086 | 61.8439 | -0.14496 | 0.012256 | 0.018017 | -0.0019055 | 0.064865 | -0.00058968 | 0.068312 | -60.8002 | 61.7157 | -60.8551 | -60.8688 | 61.6562 | 0.086975 | -0.073242 | 0.14648 | 61.7294 | -60.8643 | -0.14648 | -0.12817 | -0.091553 | -0.16022 | -0.18768 | -0.15564 | -0.11444 | 0.054932 | 60.6354 | 60.8551 | 122.3648 | 122.4243 | -0.091553 | 122.438 | 60.7956 | -0.15564 | 122.4243 | -0.091553 | 60.7956 | 122.3648 | 122.438 | -122.699 | -122.7081
12.0781 | 122.7814 | -60.7544 | 61.8576 | 0.061035 | 0.014605 | 0.015026 | 0.0045033 | 0.067214 | 0.00047852 | 0.068099 | -60.8276 | 61.7706 | -60.8643 | -60.9467 | 61.5326 | -0.036621 | -0.036621 | -0.009155 | 61.7386 | -60.9512 | -0.10986 | -0.086975 | -0.073242 | -0.19226 | -0.32501 | -0.19684 | -0.11902 | 0.036621 | 60.7178 | 60.7452 | 122.287 | 122.525 | -0.073242 | 122.493 | 60.7178 | -0.19684 | 122.525 | -0.073242 | 60.7178 | 122.287 | 122.493 | -122.7219 | -122.8088
13.0625 | 122.8867 | -60.6812 | 61.8073 | -0.061035 | 0.0086239 | 0.017803 | -0.0016919 | 0.066146 | 0.00026492 | 0.069167 | -60.8231 | 61.702 | -60.8414 | -60.8871 | 61.6241 | 0.07782 | -0.064087 | 0.13275 | 61.6974 | -60.878 | -0.16022 | -0.10529 | -0.14191 | -0.20599 | -0.1831 | -0.19684 | -0.10986 | 0.018311 | 60.6171 | 60.8139 | 122.3053 | 122.3831 | -0.14191 | 122.3785 | 60.759 | -0.19684 | 122.3831 | -0.14191 | 60.759 | 122.3053 | 122.3785 | -122.6486 | -122.6852
14.0625 | 122.905 | -60.6766 | 61.853 | -0.13733 | 0.013537 | 0.013104 | -0.0014783 | 0.063796 | 0.0017603 | 0.067031 | -60.8047 | 61.7065 | -60.8322 | -60.8414 | 61.647 | 0.12817 | -0.082397 | 0.14648 | 61.7065 | -60.8963 | -0.15564 | -0.14648 | -0.12817 | -0.16479 | -0.20599 | -0.21973 | -0.14648 | 0.027465 | 60.5942 | 60.8231 | 122.3236 | 122.3831 | -0.12817 | 122.3831 | 60.8047 | -0.21973 | 122.3831 | -0.12817 | 60.8047 | 122.3236 | 122.3831 | -122.6852 | -122.7493
15.0625 | 122.8088 | -60.7452 | 61.8713 | -0.31281 | 0.012469 | 0.017163 | 0.0012989 | 0.065505 | 0.00069212 | 0.06874 | -60.8276 | 61.7798 | -60.8505 | -60.8963 | 61.5967 | 0.054932 | 0.14191 | 0.11902 | 61.7752 | -60.9238 | -0.10529 | -0.091553 | -0.082398 | -0.15106 | -0.27466 | -0.17853 | -0.09613 | 0.022888 | 60.8871 | 60.8643 | 122.3419 | 122.525 | -0.082398 | 122.5204 | 60.8002 | -0.17853 | 122.525 | -0.082398 | 60.8002 | 122.3419 | 122.5204 | -122.7219 | -122.7951
16.0625 | 122.905 | -60.64 | 61.8347 | -0.23651 | 0.011188 | 0.014385 | -0.00083733 | 0.065292 | -0.0012305 | 0.06639 | -60.7361 | 61.6928 | -60.8505 | -60.7956 | 61.6928 | 0.16937 | -0.045776 | 0.24261 | 61.7294 | -60.8643 | -0.21057 | -0.14191 | -0.09613 | -0.15564 | -0.14191 | -0.2243 | -0.10529 | 0.11444 | 60.5942 | 60.8826 | 122.3328 | 122.3328 | -0.09613 | 122.3694 | 60.8093 | -0.2243 | 122.3328 | -0.09613 | 60.8093 | 122.3328 | 122.3694 | -122.6852 | -122.699
17.0625 | 122.7722 | -60.7269 | 61.8805 | 0.0076294 | 0.013324 | 0.017803 | 0.0072803 | 0.064224 | -0.0018713 | 0.068312 | -60.8231 | 61.7798 | -60.8597 | -60.9192 | 61.5463 | -0.027466 | 0.032043 | -0.004578 | 61.7569 | -60.9375 | -0.13275 | -0.10071 | -0.09613 | -0.19226 | -0.33417 | -0.21057 | -0.1236 | 0.036621 | 60.759 | 60.7224 | 122.2733 | 122.5067 | -0.09613 | 122.4838 | 60.6995 | -0.21057 | 122.5067 | -0.09613 | 60.6995 | 122.2733 | 122.4838 | -122.7402 | -122.818
18.0625 | 122.8912 | -60.6995 | 61.8484 | -0.038147 | 0.010547 | 0.017803 | -0.0029735 | 0.067001 | 0.0021875 | 0.066817 | -60.8047 | 61.6928 | -60.8459 | -60.8505 | 61.6653 | 0.10071 | -0.059509 | 0.16479 | 61.7249 | -60.8551 | -0.14648 | -0.15564 | -0.10529 | -0.15106 | -0.18311 | -0.15564 | -0.1236 | 0.041198 | 60.64 | 60.8643 | 122.3648 | 122.3923 | -0.10529 | 122.4243 | 60.8002 | -0.15564 | 122.3923 | -0.10529 | 60.8002 | 122.3648 | 122.4243 | -122.6944 | -122.7036
19.0625 | 122.8546 | -60.7269 | 61.8484 | -0.022888 | 0.0096921 | 0.016735 | -0.00019653 | 0.064224 | 0.0015467 | 0.06938 | -60.8322 | 61.7203 | -60.8643 | -60.9009 | 61.6013 | 0.054932 | -0.068665 | 0.073242 | 61.6974 | -60.8963 | -0.13733 | -0.12817 | -0.10529 | -0.17395 | -0.24719 | -0.16937 | -0.15106 | 0.032044 | 60.6583 | 60.8002 | 122.3282 | 122.4472 | -0.10529 | 122.4243 | 60.7819 | -0.16937 | 122.4472 | -0.10529 | 60.7819 | 122.3282 | 122.4243 | -122.7127 | -122.7448
20.0625 | 122.9141 | -60.6674 | 61.8301 | -0.21362 | 0.011401 | 0.015667 | -0.00041013 | 0.063583 | -0.0016577 | 0.069167 | -60.7452 | 61.702 | -60.8276 | -60.7681 | 61.7065 | 0.16937 | -0.050354 | 0.2243 | 61.702 | -60.8551 | -0.16022 | -0.12817 | -0.07782 | -0.10071 | -0.1236 | -0.18768 | -0.12817 | 0.082398 | 60.6171 | 60.8917 | 122.374 | 122.3694 | -0.07782 | 122.3694 | 60.8368 | -0.18768 | 122.3694 | -0.07782 | 60.8368 | 122.374 | 122.3694 | -122.6578 | -122.6852
21.0625 | 122.8409 | -60.6949 | 61.8393 | -0.48065 | 0.014605 | 0.01759 | 0.00087167 | 0.065505 | 0.00069212 | 0.069167 | -60.8871 | 61.6882 | -60.8414 | -60.9146 | 61.5967 | 0.032043 | -0.091553 | 0.054932 | 61.6882 | -60.91 | -0.14648 | -0.15106 | -0.19226 | -0.21973 | -0.24261 | -0.21515 | -0.15106 | -0.045776 | 60.6033 | 60.7498 | 122.2916 | 122.3831 | -0.19226 | 122.3831 | 60.7269 | -0.21515 | 122.3831 | -0.19226 | 60.7269 | 122.2916 | 122.3831 | -122.6807 | -122.7493
22.0781 | 122.7768 | -60.7498 | 61.8942 | -0.0076296 | 0.012042 | 0.020367 | 0.0059985 | 0.066787 | -0.00080328 | 0.068099 | -60.8047 | 61.7752 | -60.878 | -60.9192 | 61.5463 | -0.004578 | 0.027466 | 0.045776 | 61.7569 | -60.9375 | -0.12817 | -0.11902 | -0.054932 | -0.16937 | -0.3479 | -0.18768 | -0.13733 | 0.073242 | 60.7773 | 60.7956 | 122.2961 | 122.525 | -0.054932 | 122.5067 | 60.7452 | -0.18768 | 122.525 | -0.054932 | 60.7452 | 122.2961 | 122.5067 | -122.7722 | -122.8317
23.0625 | 122.8363 | -60.7269 | 61.8439 | 0.12207 | 0.011828 | 0.013745 | 0.00065787 | 0.065505 | -0.0014441 | 0.068312 | -60.8276 | 61.702 | -60.8414 | -60.8917 | 61.6104 | 0.036621 | -0.07782 | 0.07782 | 61.7203 | -60.878 | -0.11444 | -0.14191 | -0.10071 | -0.1648 | -0.23346 | -0.15106 | -0.1236 | 0.013733 | 60.6491 | 60.8047 | 122.3373 | 122.4289 | -0.10071 | 122.4472 | 60.7635 | -0.15106 | 122.4289 | -0.10071 | 60.7635 | 122.3373 | 122.4472 | -122.6852 | -122.7219
24.0625 | 122.8912 | -60.6949 | 61.8347 | -0.099182 | 0.011401 | 0.016522 | -0.0023327 | 0.065292 | 0.0013329 | 0.06938 | -60.8002 | 61.734 | -60.8093 | -60.8459 | 61.6791 | 0.10986 | -0.073242 | 0.15564 | 61.7294 | -60.9009 | -0.11444 | -0.10071 | -0.10529 | -0.15106 | -0.15564 | -0.20599 | -0.10529 | 0.009155 | 60.6216 | 60.8505 | 122.374 | 122.4289 | -0.10529 | 122.4243 | 60.8047 | -0.20599 | 122.4289 | -0.10529 | 60.8047 | 122.374 | 122.4243 | -122.644 | -122.7356
25.0625 | 122.8867 | -60.6766 | 61.8347 | -0.045777 | 0.012897 | 0.017376 | -0.0016919 | 0.06166 | 0.0021875 | 0.067671 | -60.8047 | 61.7111 | -60.8414 | -60.8643 | 61.6516 | 0.10071 | -0.064087 | 0.15106 | 61.7157 | -60.8871 | -0.16479 | -0.1236 | -0.12817 | -0.18768 | -0.18311 | -0.21057 | -0.11902 | 0.036621 | 60.6125 | 60.8276 | 122.3282 | 122.3877 | -0.12817 | 122.3923 | 60.7773 | -0.21057 | 122.3877 | -0.12817 | 60.7773 | 122.3282 | 122.3923 | -122.6761 | -122.7219
26.0625 | 122.8455 | -60.7086 | 61.8439 | 0.022888 | 0.012683 | 0.01759 | 0.0019397 | 0.064437 | -0.00016228 | 0.06938 | -60.8093 | 61.7111 | -60.8368 | -60.8917 | 61.6013 | 0.036621 | -0.064087 | 0.091553 | 61.702 | -60.9146 | -0.12817 | -0.13275 | -0.10071 | -0.18311 | -0.24262 | -0.20599 | -0.14191 | 0.027466 | 60.6445 | 60.8002 | 122.3099 | 122.4197 | -0.10071 | 122.4106 | 60.7452 | -0.20599 | 122.4197 | -0.10071 | 60.7452 | 122.3099 | 122.4106 | -122.6807 | -122.7585
27.0625 | 122.7539 | -60.704 | 61.908 | -0.37384 | 0.013537 | 0.013745 | 0.0023669 | 0.063583 | -0.00080328 | 0.067458 | -60.8414 | 61.7844 | -60.8276 | -60.9146 | 61.5646 | 0.054932 | 0.16022 | 0.091553 | 61.7706 | -60.9146 | -0.1236 | -0.1236 | -0.13733 | -0.21057 | -0.34332 | -0.21057 | -0.13733 | -0.013733 | 60.8643 | 60.7956 | 122.2687 | 122.4884 | -0.13733 | 122.4747 | 60.759 | -0.21057 | 122.4884 | -0.13733 | 60.759 | 122.2687 | 122.4747 | -122.7356 | -122.8226
28.0625 | 122.8455 | -60.704 | 61.8301 | 0.1297 | 0.012897 | 0.016522 | -0.0012647 | 0.064651 | -0.0027259 | 0.06874 | -60.8276 | 61.6837 | -60.8505 | -60.8917 | 61.5829 | 0.036621 | -0.082397 | 0.064087 | 61.7065 | -60.91 | -0.14648 | -0.14648 | -0.1236 | -0.18768 | -0.24719 | -0.20599 | -0.1236 | 0.022888 | 60.6216 | 60.7681 | 122.287 | 122.3877 | -0.1236 | 122.4106 | 60.7407 | -0.20599 | 122.3877 | -0.1236 | 60.7407 | 122.287 | 122.4106 | -122.6807 | -122.7402
29.0625 | 122.8821 | -60.6903 | 61.8164 | 0.18311 | 0.013324 | 0.018444 | 0.0019397 | 0.065078 | -0.00037588 | 0.068099 | -60.7727 | 61.6745 | -60.8322 | -60.8414 | 61.6516 | 0.068665 | -0.17395 | 0.10071 | 61.6653 | -60.9238 | -0.14191 | -0.14191 | -0.082397 | -0.15106 | -0.16479 | -0.23346 | -0.15106 | 0.059509 | 60.5164 | 60.791 | 122.3419 | 122.3648 | -0.082397 | 122.3557 | 60.759 | -0.23346 | 122.3648 | -0.082397 | 60.759 | 122.3419 | 122.3557 | -122.6486 | -122.7402
30.0625 | 122.8683 | -60.672 | 61.8576 | -0.25177 | 0.011615 | 0.014813 | 0.00065787 | 0.063369 | -0.0010169 | 0.068526 | -60.7636 | 61.7432 | -60.8276 | -60.8276 | 61.6653 | 0.15106 | 0.022888 | 0.21057 | 61.7294 | -60.8734 | -0.15564 | -0.11444 | -0.091553 | -0.15564 | -0.19226 | -0.20142 | -0.12817 | 0.064087 | 60.6949 | 60.8826 | 122.3373 | 122.4152 | -0.091553 | 122.4014 | 60.8231 | -0.20142 | 122.4152 | -0.091553 | 60.8231 | 122.3373 | 122.4014 | -122.6852 | -122.731
31.0625 | 122.8821 | -60.6995 | 61.821 | 0.14496 | 0.013537 | 0.013745 | 0.0034351 | 0.066787 | 0.00047852 | 0.066817 | -60.7636 | 61.7111 | -60.8368 | -60.8505 | 61.6379 | 0.064087 | -0.20142 | 0.10986 | 61.6928 | -60.9192 | -0.13733 | -0.10986 | -0.064087 | -0.15106 | -0.18311 | -0.21973 | -0.12817 | 0.073242 | 60.498 | 60.8093 | 122.3373 | 122.4106 | -0.064087 | 122.3923 | 60.7636 | -0.21973 | 122.4106 | -0.064087 | 60.7636 | 122.3373 | 122.3923 | -122.6578 | -122.7402
32.0625 | 122.7814 | -60.7178 | 61.8759 | -0.29755 | 0.015033 | 0.018871 | 0.0027943 | 0.065292 | -0.0020849 | 0.06874 | -60.8185 | 61.8164 | -60.8688 | -60.91 | 61.5784 | 0.064087 | 0.15564 | 0.10529 | 61.7889 | -60.9283 | -0.15106 | -0.05951 | -0.10071 | -0.19226 | -0.29755 | -0.21057 | -0.086976 | 0.050354 | 60.8734 | 60.8231 | 122.2961 | 122.5342 | -0.10071 | 122.5067 | 60.7819 | -0.21057 | 122.5342 | -0.10071 | 60.7819 | 122.2961 | 122.5067 | -122.7448 | -122.8043
33.0625 | 122.8409 | -60.704 | 61.821 | -6e-08 | 0.012469 | 0.015454 | -0.0027599 | 0.065292 | -0.0033667 | 0.068953 | -60.8231 | 61.7203 | -60.8505 | -60.8963 | 61.615 | 0.059509 | -0.059509 | 0.10529 | 61.7111 | -60.91 | -0.14648 | -0.10071 | -0.11902 | -0.19226 | -0.20599 | -0.20599 | -0.10986 | 0.027466 | 60.6445 | 60.8093 | 122.319 | 122.4243 | -0.11902 | 122.4152 | 60.7635 | -0.20599 | 122.4243 | -0.11902 | 60.7635 | 122.319 | 122.4152 | -122.6715 | -122.731
34.0625 | 122.8546 | -60.7178 | 61.8073 | 0.083923 | 0.014178 | 0.016522 | -0.00062373 | 0.06401 | 0.00069212 | 0.069808 | -60.791 | 61.6974 | -60.8688 | -60.7864 | 61.5921 | -0.013733 | -0.16937 | 0.082397 | 61.6791 | -60.8917 | -0.15106 | -0.10986 | -0.073243 | -0.068665 | -0.21515 | -0.17395 | -0.12817 | 0.077819 | 60.5484 | 60.8002 | 122.3099 | 122.4152 | -0.073243 | 122.3969 | 60.704 | -0.17395 | 122.4152 | -0.073243 | 60.704 | 122.3099 | 122.3969 | -122.6761 | -122.699
35.0625 | 122.9004 | -60.6628 | 61.8576 | -0.26703 | 0.011188 | 0.015667 | -0.0016919 | 0.063369 | 0.00047852 | 0.067885 | -60.7498 | 61.7111 | -60.8276 | -60.8139 | 61.6974 | 0.17395 | -0.041199 | 0.23804 | 61.6882 | -60.878 | -0.1648 | -0.14648 | -0.086975 | -0.15106 | -0.16022 | -0.21515 | -0.16937 | 0.07782 | 60.6216 | 60.9009 | 122.3602 | 122.374 | -0.086975 | 122.3511 | 60.8368 | -0.21515 | 122.374 | -0.086975 | 60.8368 | 122.3602 | 122.3511 | -122.6852 | -122.7356
36.0625 | 122.8546 | -60.7086 | 61.8576 | -0.061035 | 0.013324 | 0.017163 | 0.00065787 | 0.065292 | -0.00080328 | 0.068953 | -60.8231 | 61.7157 | -60.8459 | -60.8871 | 61.615 | 0.068665 | -0.054932 | 0.12817 | 61.6974 | -60.9192 | -0.13733 | -0.14191 | -0.11444 | -0.17853 | -0.24262 | -0.21057 | -0.16022 | 0.022888 | 60.6537 | 60.8368 | 122.3236 | 122.4243 | -0.11444 | 122.406 | 60.7773 | -0.21057 | 122.4243 | -0.11444 | 60.7773 | 122.3236 | 122.406 | -122.7036 | -122.7768
37.0625 | 122.8821 | -60.7132 | 61.8301 | 0.12207 | 0.013324 | 0.01289 | 0.00087167 | 0.064224 | -0.00080328 | 0.070021 | -60.7773 | 61.7065 | -60.8505 | -60.8505 | 61.6333 | 0.064087 | -0.1831 | 0.11444 | 61.6791 | -60.9192 | -0.13733 | -0.1236 | -0.064087 | -0.13733 | -0.19684 | -0.20599 | -0.15106 | 0.073242 | 60.5301 | 60.8276 | 122.3465 | 122.4197 | -0.064087 | 122.3923 | 60.7773 | -0.20599 | 122.4197 | -0.064087 | 60.7773 | 122.3465 | 122.3923 | -122.6807 | -122.7493
38.0625 | 122.8867 | -60.7315 | 61.8073 | 0.10681 | 0.012897 | 0.016949 | 0.0036487 | 0.064224 | -0.00037588 | 0.068953 | -60.759 | 61.7157 | -60.8185 | -60.8414 | 61.6379 | 0.068665 | -0.18768 | 0.10071 | 61.6837 | -60.9055 | -0.086975 | -0.091553 | -0.027466 | -0.10986 | -0.16937 | -0.17395 | -0.1236 | 0.059509 | 60.5438 | 60.8322 | 122.3694 | 122.4472 | -0.027466 | 122.4152 | 60.8002 | -0.17395 | 122.4472 | -0.027466 | 60.8002 | 122.3694 | 122.4152 | -122.6257 | -122.7127
39.0625 | 122.8912 | -60.6995 | 61.8027 | 0.13733 | 0.013965 | 0.016735 | 0.0051441 | 0.066146 | -0.00016228 | 0.068526 | -60.7544 | 61.702 | -60.8597 | -60.8414 | 61.6425 | 0.064087 | -0.19684 | 0.10529 | 61.6882 | -60.91 | -0.16022 | -0.10071 | -0.054932 | -0.14191 | -0.16022 | -0.21057 | -0.11444 | 0.10528 | 60.5026 | 60.8047 | 122.3419 | 122.4014 | -0.054932 | 122.3877 | 60.7636 | -0.21057 | 122.4014 | -0.054932 | 60.7636 | 122.3419 | 122.3877 | -122.6624 | -122.7127
40.0625 | 122.8958 | -60.6857 | 61.8118 | -0.14496 | 0.013751 | 0.019726 | -0.0014783 | 0.066146 | -0.00037588 | 0.068312 | -60.7864 | 61.6882 | -60.8231 | -60.8139 | 61.6882 | 0.15564 | -0.07782 | 0.21057 | 61.7111 | -60.878 | -0.13733 | -0.1236 | -0.10071 | -0.12817 | -0.1236 | -0.19226 | -0.10071 | 0.036621 | 60.6079 | 60.8963 | 122.374 | 122.374 | -0.10071 | 122.3969 | 60.8414 | -0.19226 | 122.374 | -0.10071 | 60.8414 | 122.374 | 122.3969 | -122.6349 | -122.6898
41.0625 | 122.8455 | -60.7086 | 61.8301 | 0.045776 | 0.010119 | 0.018444 | -0.0014783 | 0.062728 | 0.00069212 | 0.068312 | -60.8093 | 61.7249 | -60.8551 | -60.8963 | 61.6196 | 0.036621 | -0.064087 | 0.086975 | 61.7065 | -60.9146 | -0.14648 | -0.10529 | -0.10071 | -0.18768 | -0.21057 | -0.20599 | -0.1236 | 0.045777 | 60.6445 | 60.7956 | 122.3282 | 122.4335 | -0.10071 | 122.4152 | 60.7452 | -0.20599 | 122.4335 | -0.10071 | 60.7452 | 122.3282 | 122.4152 | -122.6852 | -122.7448
42.0625 | 122.8638 | -60.6949 | 61.8347 | -0.053406 | 0.010974 | 0.013958 | 0.00065787 | 0.061447 | -0.00037588 | 0.06938 | -60.8047 | 61.7111 | -60.8368 | -60.8826 | 61.6333 | 0.064087 | -0.054932 | 0.11444 | 61.6974 | -60.9146 | -0.14191 | -0.1236 | -0.10986 | -0.18768 | -0.20142 | -0.21973 | -0.13733 | 0.032043 | 60.64 | 60.8093 | 122.3282 | 122.406 | -0.10986 | 122.3923 | 60.759 | -0.21973 | 122.406 | -0.10986 | 60.759 | 122.3282 | 122.3923 | -122.6715 | -122.7493
43.0625 | 122.9095 | -60.7224 | 61.7889 | 0.083923 | 0.015674 | 0.019726 | 0.0030079 | 0.067642 | 0.00026492 | 0.067031 | -60.7407 | 61.6928 | -60.8322 | -60.8276 | 61.6379 | 0.068665 | -0.18768 | 0.091553 | 61.6974 | -60.8963 | -0.10986 | -0.09613 | -0.018311 | -0.10529 | -0.15106 | -0.17395 | -0.091552 | 0.091552 | 60.5347 | 60.8139 | 122.3602 | 122.4152 | -0.018311 | 122.4197 | 60.791 | -0.17395 | 122.4152 | -0.018311 | 60.791 | 122.3602 | 122.4197 | -122.6212 | -122.6852
44.0625 | 122.8912 | -60.704 | 61.821 | 0.10681 | 0.013751 | 0.016308 | 0.0030079 | 0.067001 | -0.0010169 | 0.06938 | -60.7727 | 61.7065 | -60.8551 | -60.8505 | 61.647 | 0.064087 | -0.17395 | 0.10986 | 61.6882 | -60.9055 | -0.15106 | -0.11444 | -0.068664 | -0.14648 | -0.17395 | -0.20142 | -0.13275 | 0.082398 | 60.5301 | 60.8139 | 122.3511 | 122.4106 | -0.068664 | 122.3923 | 60.7681 | -0.20142 | 122.4106 | -0.068664 | 60.7681 | 122.3511 | 122.3923 | -122.6761 | -122.7264
45.0625 | 122.7997 | -60.7269 | 61.821 | 0.083923 | 0.014392 | 0.019512 | 0.0038623 | 0.067214 | -0.0012305 | 0.06938 | -60.8368 | 61.7752 | -60.8688 | -60.9329 | 61.5692 | -0.018311 | -0.068665 | 0 | 61.6974 | -60.9238 | -0.14191 | -0.045776 | -0.10986 | -0.20599 | -0.25177 | -0.19684 | -0.1236 | 0.032043 | 60.6583 | 60.7269 | 122.2961 | 122.5021 | -0.10986 | 122.4243 | 60.7086 | -0.19684 | 122.5021 | -0.10986 | 60.7086 | 122.2961 | 122.4243 | -122.6898 | -122.7448
46.0625 | 122.8638 | -60.704 | 61.7935 | 0.1297 | 0.012256 | 0.020367 | 0.0057849 | 0.067855 | -0.00080328 | 0.067458 | -60.8093 | 61.7523 | -60.8826 | -60.8551 | 61.6104 | 0.018311 | -0.14191 | 0.07782 | 61.6974 | -60.8963 | -0.17853 | -0.041199 | -0.10529 | -0.15106 | -0.1831 | -0.19226 | -0.09613 | 0.073242 | 60.5621 | 60.7819 | 122.3145 | 122.4564 | -0.10529 | 122.4014 | 60.7224 | -0.19226 | 122.4564 | -0.10529 | 60.7224 | 122.3145 | 122.4014 | -122.6761 | -122.6898
47.0625 | 122.8638 | -60.6903 | 61.8256 | 0.1297 | 0.011188 | 0.02058 | 0.00023067 | 0.065933 | -0.00080328 | 0.069167 | -60.7636 | 61.7065 | -60.8231 | -60.8368 | 61.6562 | 0.068665 | -0.16479 | 0.10529 | 61.6882 | -60.9192 | -0.13275 | -0.11902 | -0.073242 | -0.14648 | -0.16937 | -0.22888 | -0.13733 | 0.059509 | 60.5255 | 60.7956 | 122.3465 | 122.3969 | -0.073242 | 122.3785 | 60.759 | -0.22888 | 122.3969 | -0.073242 | 60.759 | 122.3465 | 122.3785 | -122.6486 | -122.7448
48.0625 | 122.8821 | -60.7132 | 61.7935 | 0.28229 | 0.011828 | 0.015881 | 0.0049305 | 0.066146 | 0.00090572 | 0.06938 | -60.7544 | 61.702 | -60.8276 | -60.8505 | 61.6241 | 0.054932 | -0.17853 | 0.09613 | 61.6882 | -60.8963 | -0.11444 | -0.091553 | -0.041199 | -0.13733 | -0.16937 | -0.1831 | -0.10529 | 0.073242 | 60.5347 | 60.8093 | 122.3373 | 122.4152 | -0.041199 | 122.4014 | 60.7681 | -0.1831 | 122.4152 | -0.041199 | 60.7681 | 122.3373 | 122.4014 | -122.6212 | -122.6898
49.0625 | 122.8867 | -60.704 | 61.8118 | 1.3733 | 0.012683 | 0.021221 | 0.0032215 | 0.067642 | -0.0010169 | 0.070662 | -60.8047 | 61.7569 | -60.8688 | -60.8643 | 61.6287 | 0.068665 | -0.16479 | 0.064087 | 61.6745 | -60.9192 | -0.16479 | -0.054932 | -0.10071 | -0.16022 | -0.18311 | -0.21515 | -0.13733 | 0.064086 | 60.5392 | 60.7681 | 122.3328 | 122.4609 | -0.10071 | 122.3785 | 60.7727 | -0.21515 | 122.4609 | -0.10071 | 60.7727 | 122.3328 | 122.3785 | -122.6807 | -122.731
50.0625 | 122.9004 | -60.6995 | 61.7935 | 0.13733 | 0.0099057 | 0.021649 | 0.0010853 | 0.069992 | -0.00080328 | 0.071303 | -60.7727 | 61.6928 | -60.8826 | -60.8459 | 61.6333 | 0.073242 | -0.17395 | 0.09613 | 61.6928 | -60.8871 | -0.1831 | -0.10071 | -0.073242 | -0.14648 | -0.16022 | -0.18768 | -0.10071 | 0.10986 | 60.5255 | 60.7956 | 122.3328 | 122.3923 | -0.073242 | 122.3923 | 60.7727 | -0.18768 | 122.3923 | -0.073242 | 60.7727 | 122.3328 | 122.3923 | -122.6761 | -122.6807
51.0625 | 122.7768 | -60.7407 | 61.8347 | 0.083923 | 0.014819 | 0.016949 | 0.0053577 | 0.067428 | -0.0022987 | 0.070876 | -60.8551 | 61.7981 | -60.8643 | -60.9467 | 61.5372 | -0.041199 | 0.004578 | -0.036621 | 61.7569 | -60.9604 | -0.1236 | -0.036621 | -0.11444 | -0.20599 | -0.29755 | -0.21973 | -0.07782 | 0.009155 | 60.7452 | 60.704 | 122.2778 | 122.5388 | -0.11444 | 122.4976 | 60.6995 | -0.21973 | 122.5388 | -0.11444 | 60.6995 | 122.2778 | 122.4976 | -122.699 | -122.7951
52.0625 | 122.8043 | -60.7315 | 61.821 | 0.11444 | 0.012897 | 0.019299 | 0.0036487 | 0.069351 | 0.0011193 | 0.069594 | -60.8322 | 61.7798 | -60.8643 | -60.9329 | 61.5555 | -0.004578 | -0.068665 | -0.009155 | 61.7249 | -60.9375 | -0.13275 | -0.041199 | -0.10071 | -0.20142 | -0.2655 | -0.20599 | -0.09613 | 0.032044 | 60.6628 | 60.7224 | 122.287 | 122.5113 | -0.10071 | 122.4564 | 60.7269 | -0.20599 | 122.5113 | -0.10071 | 60.7269 | 122.287 | 122.4564 | -122.6852 | -122.7585
53.0625 | 122.7631 | -60.7178 | 61.8439 | 0.10681 | 0.013965 | 0.018658 | 0.0042895 | 0.06871 | 0.0017603 | 0.070021 | -60.8459 | 61.7752 | -60.8734 | -60.9375 | 61.5417 | -0.022888 | -0.013733 | -0.018311 | 61.734 | -60.9421 | -0.15564 | -0.068664 | -0.12817 | -0.21973 | -0.30212 | -0.22431 | -0.10986 | 0.027466 | 60.704 | 60.6995 | 122.2595 | 122.493 | -0.12817 | 122.4518 | 60.6949 | -0.22431 | 122.493 | -0.12817 | 60.6949 | 122.2595 | 122.4518 | -122.7173 | -122.7859
54.0938 | 122.8821 | -60.672 | 61.8118 | -0.28992 | 0.011188 | 0.016308 | -0.0034009 | 0.065719 | -0.0027259 | 0.069167 | -60.7544 | 61.7249 | -60.8322 | -60.8093 | 61.7065 | 0.18768 | -0.045776 | 0.2243 | 61.7294 | -60.8688 | -0.16022 | -0.086975 | -0.082398 | -0.13733 | -0.10529 | -0.19684 | -0.082398 | 0.077819 | 60.6262 | 60.8963 | 122.3785 | 122.3969 | -0.082398 | 122.4014 | 60.8597 | -0.19684 | 122.3969 | -0.082398 | 60.8597 | 122.3785 | 122.4014 | -122.644 | -122.6807
55.0781 | 122.8363 | -60.6857 | 61.8118 | 0.15259 | 0.011188 | 0.010754 | -0.0036145 | 0.063796 | -0.0012305 | 0.069167 | -60.8368 | 61.6699 | -60.8597 | -60.9146 | 61.6287 | 0.050354 | -0.10986 | 0.073242 | 61.7065 | -60.8963 | -0.17395 | -0.14191 | -0.15106 | -0.22888 | -0.18311 | -0.21057 | -0.10529 | 0.022888 | 60.5759 | 60.759 | 122.3145 | 122.3557 | -0.15106 | 122.3923 | 60.7361 | -0.21057 | 122.3557 | -0.15106 | 60.7361 | 122.3145 | 122.3923 | -122.6715 | -122.7081
56.0625 | 122.8867 | -60.7178 | 61.7935 | 0.022888 | 0.014819 | 0.018231 | 0.0036487 | 0.066146 | -0.0014441 | 0.071944 | -60.8139 | 61.7386 | -60.878 | -60.8688 | 61.6196 | 0.054932 | -0.14648 | 0.073242 | 61.6791 | -60.9558 | -0.16022 | -0.054932 | -0.096131 | -0.15106 | -0.17395 | -0.23804 | -0.11444 | 0.064087 | 60.5713 | 60.791 | 122.3373 | 122.4564 | -0.096131 | 122.3969 | 60.7727 | -0.23804 | 122.4564 | -0.096131 | 60.7727 | 122.3373 | 122.3969 | -122.6715 | -122.7493
57.0625 | 122.7493 | -60.7407 | 61.8256 | 0.083923 | 0.013965 | 0.018231 | 0.0070667 | 0.067855 | -0.0033667 | 0.068953 | -60.8459 | 61.8164 | -60.8871 | -60.9741 | 61.5326 | -0.045776 | 0.004578 | -0.013733 | 61.7523 | -60.9604 | -0.14648 | -0.009156 | -0.10529 | -0.23346 | -0.29297 | -0.21973 | -0.073243 | 0.041199 | 60.7452 | 60.7269 | 122.2733 | 122.5571 | -0.10529 | 122.493 | 60.6949 | -0.21973 | 122.5571 | -0.10529 | 60.6949 | 122.2733 | 122.493 | -122.7127 | -122.7859
58.0625 | 122.8134 | -60.7452 | 61.8073 | 0.076294 | 0.015674 | 0.019512 | 0.0019397 | 0.069351 | 0.00047852 | 0.068312 | -60.8322 | 61.8073 | -60.8826 | -60.9375 | 61.5692 | -0.009155 | -0.07782 | 0.022888 | 61.7386 | -60.9512 | -0.13733 | 0 | -0.086975 | -0.19226 | -0.23804 | -0.20599 | -0.068665 | 0.050354 | 60.6674 | 60.7681 | 122.3145 | 122.5525 | -0.086975 | 122.4838 | 60.7361 | -0.20599 | 122.5525 | -0.086975 | 60.7361 | 122.3145 | 122.4838 | -122.6898 | -122.7585
59.0625 | 122.8043 | -60.7269 | 61.8439 | 0.091553 | 0.014178 | 0.01759 | 0.0023669 | 0.06871 | 0.00047852 | 0.06938 | -60.8459 | 61.821 | -60.8734 | -60.9375 | 61.5372 | -0.027466 | -0.027466 | -0.013733 | 61.7706 | -60.9512 | -0.14648 | -0.022888 | -0.11902 | -0.21057 | -0.3067 | -0.2243 | -0.073242 | 0.027466 | 60.6995 | 60.7132 | 122.2641 | 122.5479 | -0.11902 | 122.4976 | 60.6995 | -0.2243 | 122.5479 | -0.11902 | 60.6995 | 122.2641 | 122.4976 | -122.7173 | -122.7951
60.0781 | 122.8867 | -60.7132 | 61.7752 | 0.16022 | 0.011615 | 0.016949 | 0.0017261 | 0.06871 | 0.00090572 | 0.069808 | -60.7636 | 61.7249 | -60.8459 | -60.8414 | 61.647 | 0.07782 | -0.17395 | 0.10986 | 61.6974 | -60.9055 | -0.13275 | -0.050354 | -0.050354 | -0.12817 | -0.12817 | -0.19226 | -0.07782 | 0.082397 | 60.5392 | 60.8231 | 122.3602 | 122.4381 | -0.050354 | 122.4106 | 60.791 | -0.19226 | 122.4381 | -0.050354 | 60.791 | 122.3602 | 122.4106 | -122.6212 | -122.6807
61.0625 | 122.8958 | -60.6857 | 61.8027 | 0.091553 | 0.014392 | 0.018871 | 0.0015125 | 0.067001 | 0.0019739 | 0.068953 | -60.7452 | 61.7386 | -60.8459 | -60.878 | 61.5509 | -0.1236 | -0.14191 | 0.25177 | 61.6837 | -60.9192 | -0.16022 | -0.064087 | -0.059509 | -0.19226 | -0.25177 | -0.23346 | -0.11902 | 0.10071 | 60.5438 | 60.9375 | 122.2366 | 122.4243 | -0.059509 | 122.3694 | 60.5621 | -0.23346 | 122.4243 | -0.059509 | 60.5621 | 122.2366 | 122.3694 | -122.6486 | -122.7219
62.0625 | 122.7631 | -60.7452 | 61.8393 | 3.1815 | 0.014605 | 0.018444 | 0.0055713 | 0.06871 | -0.00058968 | 0.069167 | -60.7819 | 61.7706 | -60.8688 | -60.9833 | 61.5463 | -0.022888 | 0.004578 | -0.041199 | 61.7432 | -60.9558 | -0.1236 | -0.068664 | -0.036621 | -0.23804 | -0.29297 | -0.21057 | -0.09613 | 0.086975 | 60.7498 | 60.704 | 122.2916 | 122.5159 | -0.036621 | 122.4884 | 60.7224 | -0.21057 | 122.5159 | -0.036621 | 60.7224 | 122.2916 | 122.4884 | -122.7081 | -122.7951
63.0625 | 122.8134 | -60.7636 | 61.8622 | 0.068664 | 0.01311 | 0.022076 | 0.0057849 | 0.067428 | 0.0013329 | 0.06938 | -60.8688 | 61.8164 | -60.8734 | -60.9741 | 61.5189 | -0.050354 | 0.013733 | -0.091553 | 61.7661 | -60.9558 | -0.10986 | -0.045777 | -0.10528 | -0.21057 | -0.34332 | -0.19226 | -0.096131 | 0.004578 | 60.7773 | 60.672 | 122.2824 | 122.58 | -0.10528 | 122.5296 | 60.7132 | -0.19226 | 122.58 | -0.10528 | 60.7132 | 122.2824 | 122.5296 | -122.7356 | -122.818
64.0625 | 122.7539 | -60.7498 | 61.8439 | 0.045776 | 0.016314 | 0.020153 | 0.0040759 | 0.068923 | -0.00080328 | 0.069167 | -60.8688 | 61.8256 | -60.8826 | -60.9604 | 61.5097 | -0.032043 | 0.013733 | -0.022888 | 61.7477 | -60.9604 | -0.13275 | -0.01831 | -0.11902 | -0.21057 | -0.33417 | -0.21057 | -0.09613 | 0.013733 | 60.7636 | 60.7269 | 122.2595 | 122.5754 | -0.11902 | 122.4976 | 60.7178 | -0.21057 | 122.5754 | -0.11902 | 60.7178 | 122.2595 | 122.4976 | -122.7264 | -122.8043
65.0625 | 122.9004 | -60.6949 | 61.821 | -0.11444 | 0.011188 | 0.01289 | -0.0042553 | 0.069137 | 0.0017603 | 0.070449 | -60.8139 | 61.7432 | -60.8597 | -60.8643 | 61.647 | 0.086975 | -0.068665 | 0.16479 | 61.7477 | -60.8734 | -0.16479 | -0.07782 | -0.11902 | -0.16937 | -0.17395 | -0.17853 | -0.073242 | 0.045776 | 60.6262 | 60.8597 | 122.3419 | 122.438 | -0.11902 | 122.4426 | 60.7819 | -0.17853 | 122.438 | -0.11902 | 60.7819 | 122.3419 | 122.4426 | -122.6807 | -122.6944
66.0625 | 122.7768 | -60.7178 | 61.8713 | -0.19836 | 0.012256 | 0.016949 | 0.0068531 | 0.065719 | 0.00047852 | 0.069808 | -60.7956 | 61.821 | -60.8643 | -60.91 | 61.5784 | 0.032043 | 0.041199 | 0.041199 | 61.734 | -60.9604 | -0.14648 | -0.050354 | -0.07782 | -0.19226 | -0.29297 | -0.24262 | -0.13733 | 0.068665 | 60.759 | 60.759 | 122.2961 | 122.5388 | -0.07782 | 122.4518 | 60.7498 | -0.24262 | 122.5388 | -0.07782 | 60.7498 | 122.2961 | 122.4518 | -122.7356 | -122.8317
67.0625 | 122.7585 | -60.7269 | 61.8393 | -0.038147 | 0.014392 | 0.016949 | 0.0059985 | 0.069564 | 5.1318e-05 | 0.070235 | -60.8368 | 61.8073 | -60.8734 | -60.9558 | 61.5326 | -0.027466 | 0.041199 | -0.009155 | 61.7798 | -60.9695 | -0.14648 | -0.032043 | -0.10986 | -0.22888 | -0.3067 | -0.24261 | -0.059509 | 0.036621 | 60.7681 | 60.7178 | 122.2595 | 122.5342 | -0.10986 | 122.5067 | 60.6995 | -0.24261 | 122.5342 | -0.10986 | 60.6995 | 122.2595 | 122.5067 | -122.7127 | -122.8088
68.0625 | 122.7722 | -60.7544 | 61.8301 | 0.076294 | 0.014178 | 0.021862 | 0.0042895 | 0.069351 | -0.0018713 | 0.06874 | -60.8551 | 61.8073 | -60.8917 | -60.9787 | 61.5097 | -0.036621 | 0 | -0.045776 | 61.7523 | -60.9604 | -0.13733 | -0.022888 | -0.10071 | -0.2243 | -0.32043 | -0.20599 | -0.07782 | 0.036621 | 60.7544 | 60.7086 | 122.2641 | 122.5616 | -0.10071 | 122.5067 | 60.7178 | -0.20599 | 122.5616 | -0.10071 | 60.7178 | 122.2641 | 122.5067 | -122.7219 | -122.7905
69.0625 | 122.7448 | -60.7681 | 61.8484 | 0.11444 | 0.012256 | 0.022289 | 0.00065787 | 0.068069 | -0.00016228 | 0.07173 | -60.8917 | 61.8347 | -60.8963 | -60.9695 | 61.5326 | -0.036621 | 0.027466 | -0.027466 | 61.7615 | -60.9787 | -0.12817 | -0.013733 | -0.1236 | -0.20142 | -0.31586 | -0.21057 | -0.086975 | 0.004577 | 60.7956 | 60.7407 | 122.3007 | 122.6028 | -0.1236 | 122.5296 | 60.7315 | -0.21057 | 122.6028 | -0.1236 | 60.7315 | 122.3007 | 122.5296 | -122.7448 | -122.8271
70.0625 | 122.8546 | -60.6949 | 61.821 | 0.091553 | 0.010119 | 0.017163 | -0.0057507 | 0.067214 | -0.0010169 | 0.070021 | -60.8139 | 61.6928 | -60.8643 | -60.9375 | 61.6058 | 0.032043 | -0.091553 | 0.068665 | 61.7386 | -60.9055 | -0.16937 | -0.12817 | -0.11902 | -0.24262 | -0.21515 | -0.21057 | -0.082398 | 0.050354 | 60.6033 | 60.7636 | 122.3007 | 122.3877 | -0.11902 | 122.4335 | 60.7269 | -0.21057 | 122.3877 | -0.11902 | 60.7269 | 122.3007 | 122.4335 | -122.6852 | -122.7264
71.0625 | 122.7493 | -60.7452 | 61.8439 | 0.061035 | 0.012042 | 0.014385 | 0.0038623 | 0.06871 | 0.00026492 | 0.067458 | -60.8459 | 61.8301 | -60.8551 | -60.9879 | 61.5051 | -0.045776 | 0.022888 | 0 | 61.7386 | -60.9833 | -0.10986 | -0.013733 | -0.10071 | -0.24262 | -0.33874 | -0.23804 | -0.10529 | 0.009156 | 60.7681 | 60.7452 | 122.2504 | 122.5754 | -0.10071 | 122.4838 | 60.6995 | -0.23804 | 122.5754 | -0.10071 | 60.6995 | 122.2504 | 122.4838 | -122.699 | -122.8271
72.0625 | 122.7768 | -60.7178 | 61.8484 | -0.083924 | 0.015033 | 0.018231 | 0.0053577 | 0.06871 | -0.0014441 | 0.068312 | -60.8047 | 61.7844 | -60.8597 | -61.0153 | 61.496 | -0.018311 | 0.068665 | 0.068665 | 61.7798 | -60.9558 | -0.14191 | -0.064087 | -0.086976 | -0.29755 | -0.35248 | -0.23804 | -0.068665 | 0.054931 | 60.7864 | 60.7864 | 122.2137 | 122.5021 | -0.086976 | 122.4976 | 60.6995 | -0.23804 | 122.5021 | -0.086976 | 60.6995 | 122.2137 | 122.4976 | -122.7081 | -122.8043
73.0625 | 122.7448 | -60.7727 | 61.8439 | 0.053406 | 0.015674 | 0.019299 | 0.0032215 | 0.071273 | 0.00090572 | 0.06938 | -60.8322 | 61.8301 | -60.8917 | -60.9695 | 61.5326 | -0.036621 | 0.041199 | -0.027466 | 61.7569 | -60.9879 | -0.11902 | -0.013733 | -0.059509 | -0.19684 | -0.31128 | -0.21515 | -0.086975 | 0.05951 | 60.8139 | 60.7452 | 122.3053 | 122.6028 | -0.059509 | 122.5296 | 60.7361 | -0.21515 | 122.6028 | -0.059509 | 60.7361 | 122.3053 | 122.5296 | -122.7356 | -122.8317
74.0625 | 122.7585 | -60.759 | 61.853 | -0.0076296 | 0.013965 | 0.01759 | 0.0010853 | 0.070419 | 0.00090572 | 0.069808 | -60.8322 | 61.8256 | -60.8597 | -60.9604 | 61.5234 | -0.027466 | 0.041199 | -0.041199 | 61.7661 | -60.965 | -0.10071 | -0.027465 | -0.073242 | -0.20142 | -0.32959 | -0.20599 | -0.086975 | 0.027466 | 60.8002 | 60.7178 | 122.2824 | 122.5845 | -0.073242 | 122.525 | 60.7315 | -0.20599 | 122.5845 | -0.073242 | 60.7315 | 122.2824 | 122.525 | -122.7127 | -122.818
75.0625 | 122.8363 | -60.7086 | 61.8118 | 0.1297 | 0.012256 | 0.017163 | -0.0042553 | 0.069137 | 5.1318e-05 | 0.069808 | -60.7956 | 61.7065 | -60.8688 | -60.8871 | 61.6196 | 0.073242 | -0.14648 | 0.10529 | 61.7157 | -60.9009 | -0.16022 | -0.10529 | -0.086975 | -0.17853 | -0.19226 | -0.19226 | -0.096131 | 0.073242 | 60.5621 | 60.8139 | 122.3282 | 122.4152 | -0.086975 | 122.4243 | 60.7819 | -0.19226 | 122.4152 | -0.086975 | 60.7819 | 122.3282 | 122.4243 | -122.6807 | -122.7127
76.0625 | 122.7264 | -60.7361 | 61.8393 | 0.10681 | 0.014605 | 0.014599 | 0.0019397 | 0.067214 | -0.0010169 | 0.067885 | -60.8688 | 61.8164 | -60.8826 | -60.9741 | 61.5097 | -0.027466 | 0.018311 | -0.018311 | 61.7661 | -60.965 | -0.14648 | -0.022888 | -0.13275 | -0.23804 | -0.32959 | -0.22888 | -0.073242 | 0.013733 | 60.7544 | 60.7178 | 122.2458 | 122.5525 | -0.13275 | 122.5021 | 60.7086 | -0.22888 | 122.5525 | -0.13275 | 60.7086 | 122.2458 | 122.5021 | -122.7219 | -122.8043
77.0625 | 122.7402 | -60.7498 | 61.8393 | 0.045776 | 0.014819 | 0.021221 | 0.0049305 | 0.068496 | 5.1318e-05 | 0.069167 | -60.8643 | 61.8256 | -60.8734 | -60.997 | 61.5005 | -0.022888 | 0.013733 | -0.018311 | 61.7615 | -60.9558 | -0.1236 | -0.013732 | -0.11444 | -0.24719 | -0.33875 | -0.20599 | -0.077819 | 0.009155 | 60.7636 | 60.7315 | 122.2504 | 122.5754 | -0.11444 | 122.5113 | 60.7269 | -0.20599 | 122.5754 | -0.11444 | 60.7269 | 122.2504 | 122.5113 | -122.7127 | -122.7951
78.0625 | 122.7264 | -60.7407 | 61.8256 | -6e-08 | 0.016101 | 0.018871 | 0.0045033 | 0.07106 | -0.0012305 | 0.068526 | -60.8551 | 61.8301 | -60.9009 | -60.9741 | 61.5189 | -0.027466 | 0.045776 | -0.022888 | 61.7569 | -60.9604 | -0.16022 | 0.004577 | -0.11444 | -0.23346 | -0.3067 | -0.21973 | -0.068665 | 0.045776 | 60.7864 | 60.7178 | 122.2595 | 122.5708 | -0.11444 | 122.4976 | 60.7132 | -0.21973 | 122.5708 | -0.11444 | 60.7132 | 122.2595 | 122.4976 | -122.7264 | -122.7859
79.0625 | 122.7676 | -60.7086 | 61.8256 | -0.091553 | 0.013537 | 0.01759 | 0.0045033 | 0.068923 | 0.0015467 | 0.068312 | -60.7956 | 61.821 | -60.878 | -60.91 | 61.5829 | 0.032043 | 0.022888 | 0.064087 | 61.7706 | -60.9329 | -0.16937 | -0.004578 | -0.086975 | -0.20142 | -0.24262 | -0.2243 | -0.054932 | 0.082398 | 60.7315 | 60.7727 | 122.2916 | 122.5296 | -0.086975 | 122.4792 | 60.7407 | -0.2243 | 122.5296 | -0.086975 | 60.7407 | 122.2916 | 122.4792 | -122.7036 | -122.7585
80.0625 | 122.7997 | -60.6995 | 61.8576 | -0.061035 | 0.013751 | 0.01994 | 0.0045033 | 0.069351 | 0.00026492 | 0.067458 | -60.7819 | 61.853 | -60.8643 | -60.91 | 61.5875 | 0.054932 | 0.022888 | 0.082397 | 61.821 | -60.9146 | -0.16479 | -0.004578 | -0.082397 | -0.21057 | -0.27008 | -0.21515 | -0.036621 | 0.082398 | 60.7224 | 60.7819 | 122.287 | 122.5525 | -0.082397 | 122.5204 | 60.7544 | -0.21515 | 122.5525 | -0.082397 | 60.7544 | 122.287 | 122.5204 | -122.7219 | -122.7722
81.0625 | 122.7676 | -60.7315 | 61.8393 | -6e-08 | 0.014605 | 0.018658 | 0.0019397 | 0.071273 | 0.0015467 | 0.067458 | -60.7956 | 61.8256 | -60.878 | -60.9924 | 61.5601 | 0.041199 | 0.041199 | 0.045776 | 61.7844 | -60.9421 | -0.14648 | -0.013732 | -0.064087 | -0.26093 | -0.27923 | -0.21057 | -0.054931 | 0.082398 | 60.7727 | 60.7773 | 122.2916 | 122.5571 | -0.064087 | 122.5159 | 60.7727 | -0.21057 | 122.5571 | -0.064087 | 60.7727 | 122.2916 | 122.5159 | -122.7173 | -122.7814
82.0625 | 122.7402 | -60.7407 | 61.853 | -0.053406 | 0.013965 | 0.016308 | 0.0015125 | 0.071273 | -0.00058968 | 0.069808 | -60.8368 | 61.8347 | -60.8734 | -60.9695 | 61.5326 | -0.032043 | 0.045776 | -0.009155 | 61.7935 | -60.9695 | -0.13275 | -0.01831 | -0.09613 | -0.22888 | -0.32043 | -0.22888 | -0.059509 | 0.036621 | 60.7864 | 60.7315 | 122.2733 | 122.5754 | -0.09613 | 122.5342 | 60.7086 | -0.22888 | 122.5754 | -0.09613 | 60.7086 | 122.2733 | 122.5342 | -122.7264 | -122.8226
83.0625 | 122.7585 | -60.7498 | 61.8622 | -0.11444 | 0.012897 | 0.021221 | 0.0027943 | 0.070205 | 0.00090572 | 0.068953 | -60.8276 | 61.8301 | -60.878 | -60.9512 | 61.5372 | 0.013733 | 0.041199 | 0.013733 | 61.7569 | -60.9879 | -0.12817 | -0.032044 | -0.07782 | -0.20142 | -0.32501 | -0.23804 | -0.10529 | 0.050354 | 60.791 | 60.7636 | 122.287 | 122.58 | -0.07782 | 122.5067 | 60.7636 | -0.23804 | 122.58 | -0.07782 | 60.7636 | 122.287 | 122.5067 | -122.7402 | -122.85
84.0625 | 122.7631 | -60.7224 | 61.8713 | -0.053406 | 0.014819 | 0.018658 | 0.00065787 | 0.069778 | -0.0025123 | 0.068099 | -60.8139 | 61.821 | -60.8826 | -60.9924 | 61.5463 | 0.032043 | 0.064087 | 0.050354 | 61.7889 | -60.9558 | -0.16022 | -0.050354 | -0.091553 | -0.27008 | -0.32501 | -0.23346 | -0.082398 | 0.068664 | 60.7864 | 60.7727 | 122.2687 | 122.5433 | -0.091553 | 122.5113 | 60.7544 | -0.23346 | 122.5433 | -0.091553 | 60.7544 | 122.2687 | 122.5113 | -122.7539 | -122.8271
85.0625 | 122.8088 | -60.7498 | 61.8164 | 0.076294 | 0.011615 | 0.016094 | 0.00023067 | 0.070419 | 0.00090572 | 0.068099 | -60.8505 | 61.7981 | -60.9009 | -60.9741 | 61.5601 | -0.004578 | -0.19226 | -0.13275 | 61.7065 | -60.9833 | -0.15106 | -0.01831 | -0.10071 | -0.2243 | -0.25635 | -0.23346 | -0.10986 | 0.050354 | 60.5576 | 60.6171 | 122.3099 | 122.5479 | -0.10071 | 122.4564 | 60.7452 | -0.23346 | 122.5479 | -0.10071 | 60.7452 | 122.3099 | 122.4564 | -122.7173 | -122.7997
86.0625 | 122.818 | -60.7086 | 61.853 | -0.26703 | 0.014819 | 0.023144 | 0.0036487 | 0.069992 | -0.0012305 | 0.068953 | -60.7636 | 61.8118 | -60.8459 | -60.8917 | 61.5967 | 0.091553 | 0.041199 | 0.15106 | 61.7798 | -60.9375 | -0.13733 | -0.041198 | -0.054932 | -0.18311 | -0.25635 | -0.22888 | -0.073242 | 0.082397 | 60.7498 | 60.8597 | 122.3053 | 122.5204 | -0.054932 | 122.4884 | 60.8002 | -0.22888 | 122.5204 | -0.054932 | 60.8002 | 122.3053 | 122.4884 | -122.699 | -122.7905
87.0625 | 122.818 | -60.7361 | 61.853 | -0.16785 | 0.013537 | 0.01759 | 0.0038623 | 0.069564 | -0.00016228 | 0.068099 | -60.7636 | 61.8301 | -60.8734 | -60.8963 | 61.5875 | 0.068665 | 0.027466 | 0.11444 | 61.7706 | -60.9238 | -0.13733 | -0.022888 | -0.027466 | -0.16022 | -0.2655 | -0.18768 | -0.082397 | 0.10986 | 60.7635 | 60.8505 | 122.3236 | 122.5662 | -0.027466 | 122.5067 | 60.8047 | -0.18768 | 122.5662 | -0.027466 | 60.8047 | 122.3236 | 122.5067 | -122.7264 | -122.7768
88.0625 | 122.7722 | -60.7407 | 61.8622 | -0.091553 | 0.012897 | 0.021008 | 0.0027943 | 0.070205 | 0.0015467 | 0.068312 | -60.7773 | 61.8118 | -60.8368 | -60.9146 | 61.5875 | 0.054932 | 0.032043 | 0.07782 | 61.7935 | -60.9329 | -0.09613 | -0.050354 | -0.036621 | -0.17395 | -0.27466 | -0.19226 | -0.068665 | 0.059509 | 60.7727 | 60.8185 | 122.3282 | 122.5525 | -0.036621 | 122.5342 | 60.7956 | -0.19226 | 122.5525 | -0.036621 | 60.7956 | 122.3282 | 122.5342 | -122.699 | -122.7951
89.0625 | 122.8088 | -60.7452 | 61.8393 | -0.083924 | 0.016314 | 0.018658 | 0.0040759 | 0.073196 | 0.00047852 | 0.070662 | -60.7773 | 61.8073 | -60.8826 | -60.9055 | 61.5784 | 0.054932 | 0.022888 | 0.09613 | 61.7981 | -60.9375 | -0.13733 | -0.032043 | -0.032044 | -0.16022 | -0.26093 | -0.19226 | -0.041198 | 0.10529 | 60.7681 | 60.8414 | 122.3236 | 122.5525 | -0.032044 | 122.5433 | 60.8002 | -0.19226 | 122.5525 | -0.032044 | 60.8002 | 122.3236 | 122.5433 | -122.7219 | -122.7768
90.0625 | 122.7997 | -60.7361 | 61.8301 | 0.16785 | 0.013751 | 0.020367 | 0.0019397 | 0.070846 | -0.00037588 | 0.069167 | -61.0382 | 61.7477 | -60.91 | -60.9055 | 61.5509 | -0.013733 | -0.036621 | 0 | 61.7752 | -60.9558 | -0.17395 | -0.082397 | -0.30212 | -0.16937 | -0.27924 | -0.21973 | -0.054931 | -0.12817 | 60.6995 | 60.7361 | 122.287 | 122.4838 | -0.30212 | 122.5113 | 60.7224 | -0.21973 | 122.4838 | -0.30212 | 60.7224 | 122.287 | 122.5113 | -122.7402 | -122.7859
91.0625 | 122.818 | -60.704 | 61.8484 | -0.23651 | 0.012469 | 0.018231 | 0.0027943 | 0.069137 | 0.0019739 | 0.069594 | -60.7819 | 61.8256 | -60.8734 | -60.8871 | 61.6058 | 0.086975 | 0.064087 | 0.11902 | 61.7798 | -60.9467 | -0.16937 | -0.022888 | -0.077819 | -0.18311 | -0.24262 | -0.24261 | -0.068665 | 0.091553 | 60.7681 | 60.8231 | 122.3099 | 122.5296 | -0.077819 | 122.4838 | 60.791 | -0.24261 | 122.5296 | -0.077819 | 60.791 | 122.3099 | 122.4838 | -122.7219 | -122.7951
92.0625 | 122.8271 | -60.6995 | 61.853 | -0.24414 | 0.014178 | 0.016735 | 1.7066e-05 | 0.067001 | -0.0010169 | 0.06874 | -60.7727 | 61.8301 | -60.8643 | -60.8871 | 61.6104 | 0.086975 | 0.050354 | 0.14648 | 61.8073 | -60.9421 | -0.16479 | -0.022888 | -0.073242 | -0.18768 | -0.24261 | -0.24262 | -0.045776 | 0.091553 | 60.7498 | 60.8459 | 122.3099 | 122.5296 | -0.073242 | 122.5067 | 60.7864 | -0.24262 | 122.5296 | -0.073242 | 60.7864 | 122.3099 | 122.5067 | -122.7173 | -122.7951
93.0625 | 122.8409 | -60.7086 | 61.8027 | 0.045776 | 0.011828 | 0.016094 | -0.0070325 | 0.067642 | 0.00069212 | 0.070021 | -60.8368 | 61.7203 | -60.8734 | -60.9283 | 61.6013 | 0.041199 | -0.07782 | 0.091553 | 61.7294 | -60.878 | -0.16479 | -0.082397 | -0.12817 | -0.21973 | -0.20142 | -0.16937 | -0.073242 | 0.036621 | 60.6308 | 60.8002 | 122.3099 | 122.4289 | -0.12817 | 122.438 | 60.7498 | -0.16937 | 122.4289 | -0.12817 | 60.7498 | 122.3099 | 122.438 | -122.6761 | -122.6807
94.0625 | 122.7951 | -60.7132 | 61.8622 | -0.2594 | 0.014392 | 0.018871 | 0.0042895 | 0.065505 | -0.00037588 | 0.069594 | -60.8093 | 61.8256 | -60.8734 | -60.8963 | 61.5784 | 0.059509 | 0.1236 | 0.10071 | 61.8073 | -60.9512 | -0.16022 | -0.036621 | -0.09613 | -0.1831 | -0.28381 | -0.23804 | -0.054932 | 0.064087 | 60.8368 | 60.8139 | 122.2916 | 122.5388 | -0.09613 | 122.5204 | 60.7727 | -0.23804 | 122.5388 | -0.09613 | 60.7727 | 122.2916 | 122.5204 | -122.7356 | -122.8134
95.0625 | 122.7951 | -60.7407 | 61.8576 | 0.083923 | 0.016528 | 0.017163 | 0.0047169 | 0.069778 | 0.0021875 | 0.06874 | -60.8505 | 61.7798 | -60.8917 | -60.9741 | 61.5234 | -0.041199 | 0 | -0.022888 | 61.7935 | -60.9924 | -0.15106 | -0.07782 | -0.10986 | -0.23346 | -0.33417 | -0.25177 | -0.064087 | 0.041199 | 60.7407 | 60.7178 | 122.2641 | 122.5204 | -0.10986 | 122.5342 | 60.6995 | -0.25177 | 122.5204 | -0.10986 | 60.6995 | 122.2641 | 122.5342 | -122.7493 | -122.85
96.0625 | 122.8226 | -60.7269 | 61.8484 | -0.18311 | 0.010974 | 0.017163 | 0.0023669 | 0.068496 | -0.00037588 | 0.06938 | -60.8047 | 61.8301 | -60.8734 | -60.8871 | 61.5875 | 0.086975 | 0.10529 | 0.14191 | 61.8256 | -60.9421 | -0.14648 | -0.018311 | -0.07782 | -0.16022 | -0.26093 | -0.21515 | -0.022888 | 0.068664 | 60.8322 | 60.8688 | 122.3145 | 122.5571 | -0.07782 | 122.5525 | 60.8139 | -0.21515 | 122.5571 | -0.07782 | 60.8139 | 122.3145 | 122.5525 | -122.7219 | -122.7905
97.0625 | 122.7997 | -60.7224 | 61.8988 | -0.17548 | 0.012683 | 0.018231 | 1.7066e-05 | 0.06871 | 0.00069212 | 0.06938 | -60.8231 | 61.8256 | -60.8505 | -60.9192 | 61.5784 | 0.064087 | 0.10986 | 0.11902 | 61.8347 | -60.9283 | -0.12817 | -0.073242 | -0.10071 | -0.19684 | -0.32043 | -0.20599 | -0.064087 | 0.027466 | 60.8322 | 60.8414 | 122.3007 | 122.5479 | -0.10071 | 122.5571 | 60.7864 | -0.20599 | 122.5479 | -0.10071 | 60.7864 | 122.3007 | 122.5571 | -122.7493 | -122.8271
98.0781 | 122.9004 | -60.6674 | 61.821 | 0.13733 | 0.012469 | 0.01994 | -0.0027599 | 0.067855 | -0.00016228 | 0.068312 | -60.7544 | 61.702 | -60.8505 | -60.8643 | 61.6379 | 0.15106 | -0.39368 | -0.013733 | 61.7294 | -60.9238 | -0.18311 | -0.11902 | -0.086976 | -0.19684 | -0.18311 | -0.25635 | -0.091553 | 0.09613 | 60.2737 | 60.6537 | 122.3053 | 122.3694 | -0.086976 | 122.3969 | 60.8185 | -0.25635 | 122.3694 | -0.086976 | 60.8185 | 122.3053 | 122.3969 | -122.6715 | -122.7448
99.0625 | 122.7539 | -60.7407 | 61.9034 | -0.28992 | 0.012683 | 0.016308 | 0.0021533 | 0.067001 | 0.00047852 | 0.06874 | -60.8276 | 61.821 | -60.8826 | -60.9283 | 61.5784 | 0 | 0.41657 | 0.11444 | 61.8301 | -60.9375 | -0.14191 | -0.082397 | -0.086975 | -0.18768 | -0.32501 | -0.19684 | -0.073242 | 0.054931 | 61.1572 | 60.8551 | 122.319 | 122.5616 | -0.086975 | 122.5708 | 60.7407 | -0.19684 | 122.5616 | -0.086975 | 60.7407 | 122.319 | 122.5708 | -122.7859 | -122.8409
100.0625 | 122.7448 | -60.7086 | 61.8484 | -0.10681 | 0.012683 | 0.019085 | 0.0030079 | 0.067642 | 0.00069212 | 0.071089 | -60.7773 | 61.8118 | -60.8459 | -60.8826 | 61.5921 | 0.073242 | 0.032043 | 0.11444 | 61.7844 | -60.9238 | -0.13733 | -0.036621 | -0.068665 | -0.17395 | -0.25635 | -0.21515 | -0.064087 | 0.068664 | 60.7407 | 60.8231 | 122.3007 | 122.5204 | -0.068665 | 122.493 | 60.7819 | -0.21515 | 122.5204 | -0.068665 | 60.7819 | 122.3007 | 122.493 | -122.6944 | -122.7722
101.0625 | 122.7585 | -60.7407 | 61.8851 | -0.2594 | 0.011401 | 0.018017 | 1.7066e-05 | 0.066574 | -0.00058968 | 0.068099 | -60.8368 | 61.7615 | -60.8597 | -60.9283 | 61.5738 | 0.059509 | 0.13275 | 0.12817 | 61.821 | -60.9055 | -0.11902 | -0.1236 | -0.09613 | -0.18768 | -0.31128 | -0.16479 | -0.064087 | 0.022888 | 60.8734 | 60.8688 | 122.3145 | 122.5021 | -0.09613 | 122.5616 | 60.8002 | -0.16479 | 122.5021 | -0.09613 | 60.8002 | 122.3145 | 122.5616 | -122.7448 | -122.7905
102.0625 | 122.7859 | -60.6857 | 61.9171 | -0.35095 | 0.013751 | 0.010754 | 1.7066e-05 | 0.064224 | 0.0011193 | 0.070021 | -60.8459 | 61.8073 | -60.8597 | -60.9329 | 61.5738 | 0.050354 | 0.16937 | 0.10071 | 61.8439 | -60.9192 | -0.17395 | -0.10986 | -0.16022 | -0.24719 | -0.34332 | -0.23346 | -0.073242 | 0.013733 | 60.8551 | 60.7864 | 122.2595 | 122.493 | -0.16022 | 122.5296 | 60.7361 | -0.23346 | 122.493 | -0.16022 | 60.7361 | 122.2595 | 122.5296 | -122.7768 | -122.8363
103.0625 | 122.7127 | -60.7773 | 61.7798 | 0.099182 | 0.012897 | 0.018871 | 0.0032215 | 0.069778 | -0.0012305 | 0.064894 | -60.8368 | 61.7889 | -60.8963 | -60.9787 | 61.5097 | -0.036621 | 0.013733 | -0.032043 | 61.8027 | -60.9375 | -0.11902 | 0.009155 | -0.059509 | -0.20142 | -0.27008 | -0.16022 | 0.022888 | 0.059509 | 60.791 | 60.7452 | 122.287 | 122.5662 | -0.059509 | 122.58 | 60.7407 | -0.16022 | 122.5662 | -0.059509 | 60.7407 | 122.287 | 122.58 | -122.6761 | -122.7173
104.0625 | 122.7631 | -60.7407 | 61.8668 | -0.36621 | 0.012897 | 0.015881 | -0.0021191 | 0.067001 | -0.00016228 | 0.068953 | -60.8093 | 61.7798 | -60.8643 | -60.9283 | 61.5738 | 0.07782 | 0.12817 | 0.14191 | 61.821 | -60.9055 | -0.1236 | -0.086975 | -0.068664 | -0.18768 | -0.29297 | -0.16479 | -0.045776 | 0.054932 | 60.8688 | 60.8826 | 122.3145 | 122.5204 | -0.068664 | 122.5616 | 60.8185 | -0.16479 | 122.5204 | -0.068664 | 60.8185 | 122.3145 | 122.5616 | -122.731 | -122.7722
105.0625 | 122.7997 | -60.6995 | 61.8896 | -0.35095 | 0.011401 | 0.018658 | -0.0012647 | 0.066787 | 0.00047852 | 0.06938 | -60.7773 | 61.734 | -60.8414 | -60.8688 | 61.6333 | 0.10986 | 0.10529 | 0.15106 | 61.7981 | -60.9009 | -0.14191 | -0.15564 | -0.07782 | -0.16937 | -0.25635 | -0.20142 | -0.091552 | 0.064087 | 60.8047 | 60.8505 | 122.3328 | 122.4335 | -0.07782 | 122.4976 | 60.8093 | -0.20142 | 122.4335 | -0.07782 | 60.8093 | 122.3328 | 122.4976 | -122.731 | -122.7905
106.0625 | 122.8821 | -60.6766 | 61.8439 | -0.27466 | 0.010119 | 0.015454 | -0.0057507 | 0.062515 | -0.00016228 | 0.069167 | -60.7452 | 61.7157 | -60.8139 | -61.0245 | 61.4914 | 0.11444 | -0.004578 | 0.17395 | 61.734 | -60.8688 | -0.13733 | -0.12817 | -0.068664 | -0.3479 | -0.35248 | -0.19226 | -0.10986 | 0.068665 | 60.672 | 60.8505 | 122.168 | 122.3923 | -0.068664 | 122.4106 | 60.791 | -0.19226 | 122.3923 | -0.068664 | 60.791 | 122.168 | 122.4106 | -122.6578 | -122.7127
107.0625 | 122.8867 | -60.6628 | 61.8622 | -0.21362 | 0.011828 | 0.016949 | -0.0019055 | 0.064651 | -0.00016228 | 0.070235 | -60.7224 | 61.6974 | -60.8368 | -60.8093 | 61.6653 | 0.15564 | -0.064087 | 0.23804 | 61.7477 | -60.8597 | -0.17395 | -0.1648 | -0.059509 | -0.14648 | -0.19684 | -0.19684 | -0.11444 | 0.11444 | 60.5988 | 60.9009 | 122.3282 | 122.3602 | -0.059509 | 122.4106 | 60.8185 | -0.19684 | 122.3602 | -0.059509 | 60.8185 | 122.3282 | 122.4106 | -122.699 | -122.7219
108.0781 | 122.7539 | -60.7452 | 61.8484 | 0.015259 | 0.014178 | 0.017163 | 0.0064259 | 0.067855 | -0.00016228 | 0.067031 | -60.8231 | 61.7935 | -60.8414 | -60.9512 | 61.5234 | -0.054932 | 0.045776 | 0.004578 | 61.7752 | -60.9375 | -0.096131 | -0.054932 | -0.07782 | -0.20599 | -0.32501 | -0.19226 | -0.073242 | 0.018311 | 60.791 | 60.7498 | 122.2687 | 122.5388 | -0.07782 | 122.5204 | 60.6903 | -0.19226 | 122.5388 | -0.07782 | 60.6903 | 122.2687 | 122.5204 | -122.6898 | -122.7859
109.0625 | 122.8912 | -60.6674 | 61.8484 | -0.27466 | 0.0088375 | 0.011608 | -0.0042553 | 0.065505 | 0.0015467 | 0.069808 | -60.7544 | 61.7111 | -60.8231 | -60.9787 | 61.6882 | 0.24261 | -0.11444 | 0.18768 | 61.7386 | -60.8688 | -0.15564 | -0.13733 | -0.086976 | -0.31128 | -0.16022 | -0.20142 | -0.10986 | 0.068664 | 60.553 | 60.8551 | 122.3557 | 122.3785 | -0.086976 | 122.406 | 60.91 | -0.20142 | 122.3785 | -0.086976 | 60.91 | 122.3557 | 122.406 | -122.6715 | -122.7173
110.0625 | 122.7814 | -60.704 | 61.8942 | -0.25177 | 0.012042 | 0.015667 | 0.0036487 | 0.065933 | -0.00080328 | 0.06874 | -60.8139 | 61.8027 | -60.8597 | -60.9009 | 61.5738 | 0.045776 | 0.10529 | 0.09613 | 61.8073 | -60.9283 | -0.15564 | -0.091553 | -0.10986 | -0.19684 | -0.32043 | -0.2243 | -0.086975 | 0.045776 | 60.8093 | 60.8002 | 122.2778 | 122.5067 | -0.10986 | 122.5113 | 60.7498 | -0.2243 | 122.5067 | -0.10986 | 60.7498 | 122.2778 | 122.5113 | -122.7539 | -122.8226
111.0625 | 122.8867 | -60.6857 | 61.8256 | -0.35095 | 0.012469 | 0.018017 | -0.00041013 | 0.065078 | -0.0025123 | 0.068099 | -60.7498 | 61.7065 | -60.8414 | -60.8185 | 61.6974 | 0.14648 | -0.045776 | 0.22888 | 61.7294 | -60.8826 | -0.15564 | -0.11902 | -0.064087 | -0.13275 | -0.12817 | -0.19684 | -0.096131 | 0.091553 | 60.64 | 60.9146 | 122.3831 | 122.3923 | -0.064087 | 122.4152 | 60.8322 | -0.19684 | 122.3923 | -0.064087 | 60.8322 | 122.3831 | 122.4152 | -122.6669 | -122.7081
112.0625 | 122.8912 | -60.672 | 61.8439 | -2.5406 | 0.01311 | 0.01289 | -0.0010509 | 0.065292 | -0.0016577 | 0.071089 | -60.6766 | 61.7569 | -60.8231 | -60.7819 | 61.6837 | 0.14648 | -0.064087 | 0.25635 | 61.7294 | -60.8688 | -0.15106 | -0.086975 | -0.004578 | -0.10986 | -0.16022 | -0.19684 | -0.11444 | 0.14648 | 60.6079 | 60.9283 | 122.3557 | 122.4289 | -0.004578 | 122.4014 | 60.8185 | -0.19684 | 122.4289 | -0.004578 | 60.8185 | 122.3557 | 122.4014 | -122.6669 | -122.7127
113.0625 | 122.8821 | -60.6857 | 61.8484 | -0.14496 | 0.010333 | 0.016522 | -0.00083733 | 0.063369 | 0.00026492 | 0.069594 | -60.7819 | 61.6882 | -60.8414 | -60.8368 | 61.6653 | 0.1236 | -0.086975 | 0.20142 | 61.7523 | -60.8688 | -0.15564 | -0.16022 | -0.09613 | -0.15106 | -0.18311 | -0.1831 | -0.096131 | 0.05951 | 60.5988 | 60.8871 | 122.3511 | 122.374 | -0.09613 | 122.438 | 60.8093 | -0.1831 | 122.374 | -0.09613 | 60.8093 | 122.3511 | 122.438 | -122.6898 | -122.7173
114.0625 | 122.8821 | -60.6812 | 61.8393 | -0.1297 | 0.011188 | 0.01524 | 1.7066e-05 | 0.062728 | -0.0016577 | 0.067671 | -60.7773 | 61.7157 | -60.8505 | -60.8368 | 61.6699 | 0.1236 | -0.073242 | 0.16937 | 61.7477 | -60.8688 | -0.16937 | -0.1236 | -0.096131 | -0.15564 | -0.16937 | -0.18768 | -0.091552 | 0.073242 | 60.6079 | 60.8505 | 122.3511 | 122.3969 | -0.096131 | 122.4289 | 60.8047 | -0.18768 | 122.3969 | -0.096131 | 60.8047 | 122.3511 | 122.4289 | -122.6898 | -122.7081
115.0625 | 122.7219 | -60.7132 | 61.8851 | -0.28992 | 0.014392 | 0.021649 | 0.0055713 | 0.06401 | -0.0010169 | 0.067031 | -60.8139 | 61.8164 | -60.8505 | -60.9146 | 61.5738 | 0.045776 | 0.1236 | 0.10071 | 61.7844 | -60.9329 | -0.13733 | -0.068665 | -0.10071 | -0.20142 | -0.31128 | -0.21973 | -0.10071 | 0.036621 | 60.8368 | 60.8139 | 122.287 | 122.5296 | -0.10071 | 122.4976 | 60.759 | -0.21973 | 122.5296 | -0.10071 | 60.759 | 122.287 | 122.4976 | -122.7356 | -122.818
116.0625 | 122.8821 | -60.672 | 61.821 | -0.18311 | 0.0096921 | 0.012249 | -0.0012647 | 0.063369 | -0.00037588 | 0.068953 | -60.7544 | 61.6882 | -60.8459 | -60.8139 | 61.6882 | 0.16479 | -0.082397 | 0.23346 | 61.7294 | -60.8643 | -0.17395 | -0.13275 | -0.082398 | -0.14191 | -0.13275 | -0.19226 | -0.091553 | 0.091552 | 60.5896 | 60.9055 | 122.3602 | 122.3602 | -0.082398 | 122.4014 | 60.8368 | -0.19226 | 122.3602 | -0.082398 | 60.8368 | 122.3602 | 122.4014 | -122.6669 | -122.6852
117.0625 | 122.8912 | -60.6583 | 61.853 | -0.2594 | 0.01076 | 0.015026 | 0.0023669 | 0.065078 | -0.0031531 | 0.06874 | -60.6491 | 61.7432 | -60.8093 | -60.8322 | 61.6379 | 0.16022 | -0.073242 | 0.19684 | 61.7294 | -60.8734 | -0.15106 | -0.10986 | 0.009155 | -0.17395 | -0.21515 | -0.21515 | -0.1236 | 0.16022 | 60.585 | 60.8551 | 122.2961 | 122.4014 | 0.009155 | 122.3877 | 60.8185 | -0.21515 | 122.4014 | 0.009155 | 60.8185 | 122.2961 | 122.3877 | -122.6624 | -122.7264
118.0625 | 122.8683 | -60.6537 | 61.853 | -0.2594 | 0.011401 | 0.014172 | -0.00062373 | 0.066787 | -0.0084937 | 0.067458 | -60.7178 | 61.6928 | -60.8047 | -60.5896 | 61.6104 | -0.013733 | -0.15564 | 0.27466 | 61.7157 | -60.8597 | -0.15106 | -0.16022 | -0.064086 | 0.064087 | -0.24261 | -0.20599 | -0.13733 | 0.086976 | 60.498 | 60.9283 | 122.2641 | 122.3465 | -0.064086 | 122.3694 | 60.64 | -0.20599 | 122.3465 | -0.064086 | 60.64 | 122.2641 | 122.3694 | -122.6578 | -122.7127
119.0625 | 122.8134 | -60.6537 | 61.7981 | -0.23651 | 0.0096921 | 0.011608 | 0.0010853 | 0.065292 | -0.00016228 | 0.06938 | -60.7269 | 61.6882 | -60.8414 | -60.7956 | 61.6791 | 0.17395 | -0.027466 | 0.60883 | 61.7798 | -60.8368 | -0.18768 | -0.10986 | -0.073242 | -0.14191 | -0.11902 | -0.18311 | -0.018311 | 0.11444 | 60.6262 | 61.2625 | 122.3328 | 122.3419 | -0.073242 | 122.4335 | 60.8276 | -0.18311 | 122.3419 | -0.073242 | 60.8276 | 122.3328 | 122.4335 | -122.6395 | -122.6349
120.0625 | 122.8775 | -60.6903 | 61.8256 | -0.12207 | 0.012469 | 0.017376 | -0.0010509 | 0.064651 | -0.00058968 | 0.070449 | -60.7727 | 61.6882 | -60.8276 | -60.8414 | 61.6608 | 0.10986 | -0.082397 | 0.17395 | 61.734 | -60.878 | -0.13733 | -0.13733 | -0.082397 | -0.15106 | -0.16479 | -0.18768 | -0.091553 | 0.054932 | 60.6079 | 60.8643 | 122.3511 | 122.3785 | -0.082397 | 122.4243 | 60.8002 | -0.18768 | 122.3785 | -0.082397 | 60.8002 | 122.3511 | 122.4243 | -122.6532 | -122.7036
121.0625 | 122.8729 | -60.6628 | 61.8622 | -0.1297 | 0.011828 | 0.012463 | -0.0012647 | 0.063369 | -0.00080328 | 0.067671 | -60.8002 | 61.6882 | -60.8597 | -60.8414 | 61.6379 | 0.10071 | -0.07782 | 0.15106 | 61.7294 | -60.8826 | -0.19684 | -0.17395 | -0.13733 | -0.17853 | -0.22431 | -0.21973 | -0.13275 | 0.059509 | 60.585 | 60.8139 | 122.3007 | 122.3511 | -0.13733 | 122.3923 | 60.7635 | -0.21973 | 122.3511 | -0.13733 | 60.7635 | 122.3007 | 122.3923 | -122.7219 | -122.7448
122.0625 | 122.905 | -60.6674 | 61.8484 | -0.16022 | 0.0092649 | 0.01759 | -0.00062373 | 0.063156 | 0.00026492 | 0.067244 | -60.7498 | 61.6928 | -60.8231 | -60.7956 | 61.6928 | 0.15106 | -0.09613 | 0.23346 | 61.7294 | -60.8597 | -0.15564 | -0.15564 | -0.082398 | -0.12817 | -0.15564 | -0.19226 | -0.11902 | 0.073242 | 60.5713 | 60.9009 | 122.3602 | 122.3602 | -0.082398 | 122.3969 | 60.8185 | -0.19226 | 122.3602 | -0.082398 | 60.8185 | 122.3602 | 122.3969 | -122.6715 | -122.7081
123.0625 | 122.8867 | -60.6766 | 61.8622 | -0.27466 | 0.010547 | 0.010113 | 0.0015125 | 0.063156 | -0.00016228 | 0.067885 | -60.4523 | 61.7752 | -60.8093 | -60.8139 | 61.702 | 0.16937 | -0.091553 | 0.24261 | 61.7569 | -60.8597 | -0.13275 | -0.086975 | 0.2243 | -0.13733 | -0.16022 | -0.1831 | -0.10529 | 0.35705 | 60.585 | 60.9192 | 122.3785 | 122.4518 | 0.2243 | 122.4335 | 60.8459 | -0.1831 | 122.4518 | 0.2243 | 60.8459 | 122.3785 | 122.4335 | -122.6715 | -122.7219
124.0625 | 122.8958 | -60.6628 | 61.8301 | -0.25177 | 0.010547 | 0.017163 | -0.0038281 | 0.060806 | 5.1318e-05 | 0.067671 | -60.7132 | 61.7065 | -60.8322 | -60.9787 | 61.647 | 0.21515 | -0.11444 | 0.1831 | 61.7432 | -60.8276 | -0.16937 | -0.1236 | -0.050354 | -0.31586 | -0.18311 | -0.1648 | -0.086975 | 0.11902 | 60.5484 | 60.8459 | 122.3099 | 122.3694 | -0.050354 | 122.406 | 60.878 | -0.1648 | 122.3694 | -0.050354 | 60.878 | 122.3099 | 122.406 | -122.6624 | -122.6578
125.0625 | 122.8088 | -60.7224 | 61.8988 | -0.2594 | 0.01311 | 0.019085 | 0.0049305 | 0.06636 | 0.0011193 | 0.067458 | -60.791 | 61.8027 | -60.8459 | -60.8688 | 61.5875 | 0.050354 | 0.11444 | 0.10986 | 61.7706 | -60.9055 | -0.1236 | -0.096131 | -0.068665 | -0.14648 | -0.31128 | -0.18311 | -0.12817 | 0.054931 | 60.8368 | 60.8322 | 122.3099 | 122.525 | -0.068665 | 122.493 | 60.7727 | -0.18311 | 122.525 | -0.068665 | 60.7727 | 122.3099 | 122.493 | -122.7448 | -122.8043
126.0625 | 122.9141 | -60.6674 | 61.9263 | -0.22888 | 0.011828 | 0.013958 | -0.00019653 | 0.066787 | -0.0025123 | 0.067458 | -60.7361 | 61.6974 | -60.8414 | -60.7819 | 61.6882 | 0.17395 | -0.07782 | 0.24261 | 61.7477 | -60.8414 | -0.17395 | -0.22888 | -0.068665 | -0.11444 | -0.23804 | -0.17395 | -0.17853 | 0.10529 | 60.5896 | 60.91 | 122.3557 | 122.3648 | -0.068665 | 122.4152 | 60.8414 | -0.17395 | 122.3648 | -0.068665 | 60.8414 | 122.3557 | 122.4152 | -122.7676 | -122.7676
127.0625 | 122.8775 | -60.6674 | 61.8301 | -0.10681 | 0.0096921 | 0.012676 | -0.0014783 | 0.063796 | 0.00090572 | 0.068312 | -60.7819 | 61.7203 | -60.8276 | -60.8322 | 61.6608 | 0.10529 | -0.07782 | 0.17853 | 61.7477 | -60.8551 | -0.16022 | -0.10986 | -0.11444 | -0.16479 | -0.16937 | -0.18768 | -0.082397 | 0.045777 | 60.5896 | 60.8459 | 122.3282 | 122.3877 | -0.11444 | 122.4152 | 60.7727 | -0.18768 | 122.3877 | -0.11444 | 60.7727 | 122.3282 | 122.4152 | -122.6578 | -122.6852
128.0625 | 122.9279 | -60.6857 | 61.8484 | -0.17548 | 0.011615 | 0.015667 | 0.0012989 | 0.064651 | -0.00016228 | 0.068526 | -60.7452 | 61.7065 | -60.8276 | -60.7773 | 61.7065 | 0.17853 | -0.086975 | 0.23804 | 61.7294 | -60.8597 | -0.14191 | -0.14191 | -0.059509 | -0.091553 | -0.14191 | -0.17395 | -0.11902 | 0.082398 | 60.5988 | 60.9238 | 122.3923 | 122.3923 | -0.059509 | 122.4152 | 60.8643 | -0.17395 | 122.3923 | -0.059509 | 60.8643 | 122.3923 | 122.4152 | -122.6761 | -122.7081
129.0625 | 122.8958 | -60.6674 | 61.8484 | -0.26703 | 0.012469 | 0.014599 | -0.0021191 | 0.064651 | 5.1318e-05 | 0.067671 | -60.7315 | 61.6882 | -60.8368 | -60.7864 | 61.6837 | 0.15106 | -0.09613 | 0.24261 | 61.734 | -60.8276 | -0.16937 | -0.16022 | -0.064087 | -0.11902 | -0.16479 | -0.16022 | -0.11444 | 0.10529 | 60.5713 | 60.91 | 122.3511 | 122.3557 | -0.064087 | 122.4014 | 60.8185 | -0.16022 | 122.3557 | -0.064087 | 60.8185 | 122.3511 | 122.4014 | -122.6852 | -122.6761
130.0625 | 122.7493 | -60.7086 | 61.8988 | -0.28229 | 0.012897 | 0.016308 | 0.0042895 | 0.064224 | -0.0010169 | 0.068953 | -60.8093 | 61.7798 | -60.8414 | -60.9009 | 61.5692 | 0.054932 | 0.13733 | 0.11444 | 61.7844 | -60.8963 | -0.13275 | -0.11902 | -0.10071 | -0.19226 | -0.32959 | -0.18768 | -0.11444 | 0.032044 | 60.8459 | 60.8231 | 122.2778 | 122.4884 | -0.10071 | 122.493 | 60.7636 | -0.18768 | 122.4884 | -0.10071 | 60.7636 | 122.2778 | 122.493 | -122.7402 | -122.7951
131.0625 | 122.8729 | -60.6995 | 61.8484 | -0.28229 | 0.010333 | 0.013958 | -0.0027599 | 0.063156 | 0.00026492 | 0.06938 | -60.7315 | 61.6928 | -60.8322 | -60.8963 | 61.7386 | 0.21515 | -0.12817 | 0.19684 | 61.7294 | -60.8688 | -0.13275 | -0.15564 | -0.032043 | -0.19684 | -0.10986 | -0.16937 | -0.11902 | 0.10071 | 60.5713 | 60.8963 | 122.438 | 122.3923 | -0.032043 | 122.4289 | 60.9146 | -0.16937 | 122.3923 | -0.032043 | 60.9146 | 122.438 | 122.4289 | -122.6807 | -122.7173
132.0625 | 122.8729 | -60.6674 | 61.8347 | -0.26703 | 0.0099057 | 0.016094 | -0.00041013 | 0.065719 | -0.00016228 | 0.068526 | -60.7361 | 61.6928 | -60.8505 | -60.6583 | 61.9629 | 0.40741 | -0.3479 | 0.10071 | 61.7203 | -60.8688 | -0.18311 | -0.14191 | -0.068665 | 0.009155 | 0.12817 | -0.20142 | -0.11444 | 0.11444 | 60.3195 | 60.7681 | 122.6303 | 122.3602 | -0.068665 | 122.3877 | 61.0748 | -0.20142 | 122.3602 | -0.068665 | 61.0748 | 122.6303 | 122.3877 | -122.6852 | -122.7036
133.0625 | 122.8088 | -60.672 | 61.8301 | -0.22888 | 0.012256 | 0.017803 | 0.00087167 | 0.066574 | -0.0020849 | 0.070235 | -60.7132 | 61.7157 | -60.8368 | -60.7773 | 61.702 | 0.1831 | 0.26093 | 0.53101 | 61.7844 | -60.8322 | -0.1648 | -0.11444 | -0.041199 | -0.10529 | -0.12817 | -0.16022 | -0.045776 | 0.1236 | 60.9329 | 61.203 | 122.374 | 122.3877 | -0.041199 | 122.4564 | 60.8551 | -0.16022 | 122.3877 | -0.041199 | 60.8551 | 122.374 | 122.4564 | -122.6669 | -122.6624
134.0625 | 122.9095 | -60.6583 | 61.8576 | -0.15259 | 0.010547 | 0.013317 | -0.0029735 | 0.063583 | 0.0015467 | 0.067885 | -60.7819 | 61.702 | -60.8414 | -60.8139 | 61.6608 | 0.12817 | -0.10071 | 0.1831 | 61.7249 | -60.8505 | -0.18311 | -0.15564 | -0.1236 | -0.15564 | -0.19684 | -0.19226 | -0.13275 | 0.05951 | 60.5576 | 60.8414 | 122.319 | 122.3602 | -0.1236 | 122.3831 | 60.7864 | -0.19226 | 122.3602 | -0.1236 | 60.7864 | 122.319 | 122.3831 | -122.699 | -122.7081
135.0625 | 122.7997 | -60.6766 | 61.8942 | -0.29755 | 0.012897 | 0.016094 | 0.0038623 | 0.065292 | -0.0016577 | 0.068312 | -60.7544 | 61.7523 | -60.8597 | -60.8505 | 61.6241 | 0.086975 | 0.082397 | 0.12817 | 61.7844 | -60.8826 | -0.1831 | -0.14191 | -0.07782 | -0.17395 | -0.27008 | -0.20599 | -0.10986 | 0.10528 | 60.759 | 60.8047 | 122.3007 | 122.4289 | -0.07782 | 122.4609 | 60.7636 | -0.20599 | 122.4289 | -0.07782 | 60.7636 | 122.3007 | 122.4609 | -122.7539 | -122.7768
136.0625 | 122.8958 | -60.6491 | 61.8576 | -0.19836 | 0.011188 | 0.016949 | -0.0010509 | 0.064865 | 0.00069212 | 0.06639 | -60.7407 | 61.7065 | -60.8505 | -60.7864 | 61.7065 | 0.16479 | -0.07782 | 0.2243 | 61.7386 | -60.8459 | -0.20142 | -0.15106 | -0.091553 | -0.13733 | -0.15106 | -0.19684 | -0.11902 | 0.10986 | 60.5713 | 60.8734 | 122.3557 | 122.3557 | -0.091553 | 122.3877 | 60.8139 | -0.19684 | 122.3557 | -0.091553 | 60.8139 | 122.3557 | 122.3877 | -122.7081 | -122.7036
137.0625 | 122.8958 | -60.6949 | 61.8759 | 1.5106 | 0.012256 | 0.01759 | 0.00087167 | 0.065719 | -0.0012305 | 0.069167 | -60.7315 | 61.702 | -60.8734 | -60.791 | 61.6928 | 0.16022 | -0.07782 | 0.23346 | 61.702 | -60.8734 | -0.17853 | -0.17395 | -0.036621 | -0.096131 | -0.18311 | -0.17853 | -0.17395 | 0.14191 | 60.6171 | 60.9283 | 122.3877 | 122.3969 | -0.036621 | 122.3969 | 60.8551 | -0.17853 | 122.3969 | -0.036621 | 60.8551 | 122.3877 | 122.3969 | -122.7493 | -122.7493
138.0625 | 122.8729 | -60.672 | 61.8439 | -0.28229 | 0.010974 | 0.01054 | 0.0030079 | 0.063796 | -0.0025123 | 0.06874 | -60.5484 | 61.7615 | -60.7819 | -60.8231 | 61.6791 | 0.17395 | -0.10071 | 0.19684 | 61.734 | -60.8551 | -0.10986 | -0.082397 | 0.1236 | -0.15106 | -0.16479 | -0.18311 | -0.10986 | 0.23346 | 60.5713 | 60.8688 | 122.3511 | 122.4335 | 0.1236 | 122.406 | 60.8459 | -0.18311 | 122.4335 | 0.1236 | 60.8459 | 122.3511 | 122.406 | -122.6257 | -122.699
139.0625 | 122.9004 | -60.6857 | 61.8393 | -0.28992 | 0.011188 | 0.014385 | -0.0014783 | 0.060378 | -0.0016577 | 0.06938 | -60.7407 | 61.702 | -60.8231 | -60.9924 | 61.4548 | 0.054932 | 0 | 0.17853 | 61.7386 | -60.8551 | -0.13733 | -0.13733 | -0.054932 | -0.3067 | -0.38452 | -0.16937 | -0.10071 | 0.082397 | 60.6857 | 60.8643 | 122.1405 | 122.3877 | -0.054932 | 122.4243 | 60.7407 | -0.16937 | 122.3877 | -0.054932 | 60.7407 | 122.1405 | 122.4243 | -122.6624 | -122.6944
140.0625 | 122.7493 | -60.7178 | 61.8851 | -0.35858 | 0.01076 | 0.01289 | 0.0034351 | 0.065078 | -0.0010169 | 0.06938 | -60.8093 | 61.7706 | -60.8597 | -60.878 | 61.5967 | 0.059509 | 0.11902 | 0.11444 | 61.7615 | -60.9009 | -0.14191 | -0.11444 | -0.091553 | -0.16022 | -0.28839 | -0.18311 | -0.1236 | 0.050354 | 60.8368 | 60.8322 | 122.3145 | 122.4884 | -0.091553 | 122.4792 | 60.7773 | -0.18311 | 122.4884 | -0.091553 | 60.7773 | 122.3145 | 122.4792 | -122.7448 | -122.786
141.0625 | 122.8912 | -60.6674 | 61.821 | -0.15259 | 0.010333 | 0.015454 | 1.7066e-05 | 0.065933 | -0.0012305 | 0.068953 | -60.7681 | 61.702 | -60.8368 | -60.8185 | 61.6653 | 0.1236 | -0.086975 | 0.20142 | 61.734 | -60.8505 | -0.16937 | -0.11902 | -0.10071 | -0.15106 | -0.15564 | -0.18311 | -0.086975 | 0.068665 | 60.5804 | 60.8688 | 122.3328 | 122.3694 | -0.10071 | 122.4014 | 60.791 | -0.18311 | 122.3694 | -0.10071 | 60.791 | 122.3328 | 122.4014 | -122.6578 | -122.6715
142.0625 | 122.8912 | -60.6812 | 61.8347 | -0.10681 | 0.010333 | 0.020153 | -0.0014783 | 0.062301 | -0.00058968 | 0.06938 | -60.7819 | 61.702 | -60.8322 | -60.8185 | 61.6608 | 0.1236 | -0.10529 | 0.16937 | 61.7203 | -60.8414 | -0.15106 | -0.13275 | -0.10071 | -0.13733 | -0.17395 | -0.16022 | -0.11444 | 0.050354 | 60.5759 | 60.8505 | 122.3419 | 122.3831 | -0.10071 | 122.4014 | 60.8047 | -0.16022 | 122.3831 | -0.10071 | 60.8047 | 122.3419 | 122.4014 | -122.6669 | -122.6761
143.0625 | 122.9004 | -60.6537 | 61.8576 | -0.22888 | 0.011188 | 0.013531 | -0.0012647 | 0.064865 | -0.0010169 | 0.067458 | -60.7132 | 61.6974 | -60.8459 | -60.7819 | 61.7157 | 0.16937 | -0.086975 | 0.2243 | 61.7294 | -60.8276 | -0.19226 | -0.16022 | -0.059509 | -0.12817 | -0.14191 | -0.17395 | -0.12817 | 0.13275 | 60.5667 | 60.878 | 122.3694 | 122.3511 | -0.059509 | 122.3831 | 60.8231 | -0.17395 | 122.3511 | -0.059509 | 60.8231 | 122.3694 | 122.3831 | -122.7036 | -122.6852
144.0625 | 122.8821 | -60.6583 | 61.8622 | 1.1902 | 0.01076 | 0.013958 | 0.0027943 | 0.064651 | -0.0020849 | 0.066176 | -60.7224 | 61.7157 | -60.8459 | -60.791 | 61.6974 | 0.16937 | -0.068665 | 0.21057 | 61.7203 | -60.8643 | -0.18768 | -0.14648 | -0.064087 | -0.13275 | -0.1648 | -0.20599 | -0.14191 | 0.1236 | 60.5896 | 60.8688 | 122.3557 | 122.374 | -0.064087 | 122.3785 | 60.8276 | -0.20599 | 122.374 | -0.064087 | 60.8276 | 122.3557 | 122.3785 | -122.7081 | -122.7264
145.0625 | 122.8821 | -60.6766 | 61.8164 | -0.28992 | 0.012897 | 0.015881 | 0.0034351 | 0.065719 | -0.00058968 | 0.066817 | -60.8276 | 61.7111 | -60.8231 | -60.791 | 61.6241 | 0.1236 | -0.07782 | 0.19226 | 61.7477 | -60.8734 | -0.14648 | -0.10529 | -0.15106 | -0.11444 | -0.19226 | -0.19684 | -0.068664 | -0.004578 | 60.5988 | 60.8688 | 122.3007 | 122.3877 | -0.15106 | 122.4243 | 60.8002 | -0.19684 | 122.3877 | -0.15106 | 60.8002 | 122.3007 | 122.4243 | -122.6395 | -122.6898
146.0625 | 122.8729 | -60.6766 | 61.8484 | -0.29755 | 0.010547 | 0.017376 | 0.00087167 | 0.065078 | 5.1318e-05 | 0.067458 | -60.7315 | 61.7065 | -60.8368 | -60.5484 | 61.8484 | 0.059509 | -0.24261 | 0.2243 | 61.6928 | -60.8551 | -0.16022 | -0.14191 | -0.054931 | 0.12817 | 0 | -0.17853 | -0.15564 | 0.10529 | 60.434 | 60.9009 | 122.525 | 122.3831 | -0.054931 | 122.3694 | 60.7361 | -0.17853 | 122.3831 | -0.054931 | 60.7361 | 122.525 | 122.3694 | -122.6852 | -122.7036
147.0625 | 122.9187 | -60.6354 | 61.8622 | -0.23651 | 0.011615 | 0.016308 | 1.7066e-05 | 0.06636 | -0.0018713 | 0.069167 | -60.7315 | 61.6974 | -60.8368 | -60.7956 | 61.6974 | 0.17395 | -0.068665 | 0.22888 | 61.7111 | -60.8276 | -0.20142 | -0.1648 | -0.09613 | -0.16022 | -0.1648 | -0.19226 | -0.15106 | 0.10529 | 60.5667 | 60.8643 | 122.3328 | 122.3328 | -0.09613 | 122.3465 | 60.8093 | -0.19226 | 122.3328 | -0.09613 | 60.8093 | 122.3328 | 122.3465 | -122.699 | -122.6898
148.0625 | 122.9004 | -60.6674 | 61.8439 | -0.12207 | 0.0094785 | 0.016735 | 0.0015125 | 0.065505 | -0.0012305 | 0.068953 | -60.759 | 61.6699 | -60.8414 | -60.8139 | 61.6516 | 0.12817 | -0.10529 | 0.18768 | 61.7294 | -60.8322 | -0.17395 | -0.17395 | -0.091553 | -0.14648 | -0.19226 | -0.16479 | -0.11444 | 0.082398 | 60.5621 | 60.8551 | 122.319 | 122.3373 | -0.091553 | 122.3969 | 60.7956 | -0.16479 | 122.3373 | -0.091553 | 60.7956 | 122.319 | 122.3969 | -122.6852 | -122.6761
149.0625 | 122.8912 | -60.6857 | 61.8301 | -0.1297 | 0.011615 | 0.016949 | -0.00041013 | 0.064437 | 0.0011193 | 0.069167 | -60.7773 | 61.6974 | -60.8505 | -60.8322 | 61.6653 | 0.12817 | -0.10529 | 0.16937 | 61.7111 | -60.8551 | -0.16479 | -0.13275 | -0.091553 | -0.14648 | -0.1648 | -0.16937 | -0.11902 | 0.073242 | 60.5804 | 60.8551 | 122.3511 | 122.3831 | -0.091553 | 122.3969 | 60.8139 | -0.16937 | 122.3831 | -0.091553 | 60.8139 | 122.3511 | 122.3969 | -122.6807 | -122.6852
150.0625 | 122.9141 | -60.6674 | 61.8759 | -0.14496 | 0.01076 | 0.013104 | -0.00083733 | 0.062087 | -0.0022987 | 0.067031 | -60.7407 | 61.6791 | -60.8276 | -60.7773 | 61.6928 | 0.1831 | -0.11444 | 0.23346 | 61.7203 | -60.8551 | -0.16022 | -0.19684 | -0.073243 | -0.10986 | -0.18311 | -0.18768 | -0.15564 | 0.086975 | 60.553 | 60.9009 | 122.3602 | 122.3465 | -0.073243 | 122.3877 | 60.8505 | -0.18768 | 122.3465 | -0.073243 | 60.8505 | 122.3602 | 122.3877 | -122.7036 | -122.731
151.0625 | 122.8683 | -60.6766 | 61.853 | -0.25177 | 0.010547 | 0.010967 | 0.0019397 | 0.065933 | -0.0016577 | 0.070235 | -60.6262 | 61.7386 | -60.7864 | -60.8139 | 61.647 | 0.16479 | -0.07782 | 0.20142 | 61.7294 | -60.8597 | -0.10986 | -0.11444 | 0.050354 | -0.13733 | -0.20599 | -0.1831 | -0.1236 | 0.16022 | 60.5988 | 60.878 | 122.3236 | 122.4152 | 0.050354 | 122.406 | 60.8414 | -0.1831 | 122.4152 | 0.050354 | 60.8414 | 122.3236 | 122.406 | -122.6395 | -122.7127
152.0625 | 122.85 | -60.6628 | 61.8347 | -0.29755 | 0.011828 | 0.015667 | 0.0021533 | 0.065292 | -0.0044349 | 0.068099 | -60.7269 | 61.702 | -60.8459 | -60.5942 | 61.5967 | -0.018311 | -0.15564 | 0.27466 | 61.7157 | -60.8459 | -0.18311 | -0.13275 | -0.064087 | 0.068665 | -0.23804 | -0.18311 | -0.11902 | 0.11902 | 60.5072 | 60.9375 | 122.2595 | 122.3648 | -0.064087 | 122.3785 | 60.6445 | -0.18311 | 122.3648 | -0.064087 | 60.6445 | 122.2595 | 122.3785 | -122.6807 | -122.6807
153.0625 | 122.8088 | -60.6262 | 61.8576 | -0.25177 | 0.0094785 | 0.0071222 | -0.00062373 | 0.067001 | -0.0037939 | 0.067244 | -60.7178 | 61.6882 | -60.8368 | -60.7773 | 61.702 | 0.16479 | -0.086975 | 0.41657 | 61.7615 | -60.8368 | -0.21057 | -0.16937 | -0.091552 | -0.15106 | -0.15564 | -0.21057 | -0.09613 | 0.11902 | 60.5392 | 61.0428 | 122.3282 | 122.3145 | -0.091552 | 122.3877 | 60.791 | -0.21057 | 122.3145 | -0.091552 | 60.791 | 122.3282 | 122.3877 | -122.6944 | -122.6944
154.0625 | 122.8683 | -60.6674 | 61.8484 | -0.2594 | 0.012469 | 0.015454 | 0.00087167 | 0.063156 | 0.00069212 | 0.067885 | -60.7269 | 61.702 | -60.8322 | -60.791 | 61.6974 | 0.16937 | -0.086975 | 0.2243 | 61.7386 | -60.8505 | -0.16479 | -0.14648 | -0.05951 | -0.1236 | -0.15106 | -0.18311 | -0.10986 | 0.10529 | 60.5804 | 60.8917 | 122.3648 | 122.3694 | -0.05951 | 122.406 | 60.8368 | -0.18311 | 122.3694 | -0.05951 | 60.8368 | 122.3648 | 122.406 | -122.6807 | -122.699
155.0625 | 122.8821 | -60.6903 | 61.8301 | -0.12207 | 0.010119 | 0.017803 | -0.00062373 | 0.063583 | 0.0015467 | 0.068312 | -60.7864 | 61.702 | -60.8322 | -60.8276 | 61.647 | 0.09613 | -0.10986 | 0.16022 | 61.7203 | -60.8459 | -0.14191 | -0.12817 | -0.09613 | -0.13733 | -0.18311 | -0.15564 | -0.10986 | 0.045776 | 60.5804 | 60.8505 | 122.3373 | 122.3923 | -0.09613 | 122.4106 | 60.7864 | -0.15564 | 122.3923 | -0.09613 | 60.7864 | 122.3373 | 122.4106 | -122.6624 | -122.6761
156.0625 | 122.8683 | -60.6766 | 61.821 | -0.091553 | 0.0092649 | 0.014813 | 0.0012989 | 0.065078 | -0.0012305 | 0.068312 | -60.7956 | 61.6974 | -60.8505 | -60.8551 | 61.6562 | 0.07782 | -0.10529 | 0.14191 | 61.7294 | -60.8597 | -0.17395 | -0.1236 | -0.11902 | -0.17853 | -0.1648 | -0.1831 | -0.091553 | 0.054932 | 60.5713 | 60.8185 | 122.3328 | 122.374 | -0.11902 | 122.406 | 60.7544 | -0.1831 | 122.374 | -0.11902 | 60.7544 | 122.3328 | 122.406 | -122.6715 | -122.6807
157.0625 | 122.8958 | -60.6674 | 61.8301 | -0.1297 | 0.010974 | 0.013958 | 0.00065787 | 0.062728 | -0.00016228 | 0.06874 | -60.7636 | 61.702 | -60.8597 | -60.8002 | 61.6699 | 0.1236 | -0.13275 | 0.21515 | 61.7111 | -60.8597 | -0.19226 | -0.12817 | -0.096131 | -0.13275 | -0.16022 | -0.19226 | -0.11902 | 0.09613 | 60.5347 | 60.8826 | 122.3373 | 122.3694 | -0.096131 | 122.3785 | 60.791 | -0.19226 | 122.3694 | -0.096131 | 60.791 | 122.3373 | 122.3785 | -122.6898 | -122.6898
158.0625 | 122.8821 | -60.6628 | 61.8576 | -0.16785 | 0.01311 | 0.016522 | 0.00087167 | 0.064437 | -0.00016228 | 0.068312 | -60.7224 | 61.6791 | -60.8551 | -60.7681 | 61.7111 | 0.15106 | -0.11444 | 0.22888 | 61.7157 | -60.8459 | -0.19226 | -0.17853 | -0.059509 | -0.10529 | -0.14648 | -0.18311 | -0.14191 | 0.13275 | 60.5484 | 60.8917 | 122.374 | 122.3419 | -0.059509 | 122.3785 | 60.8139 | -0.18311 | 122.3419 | -0.059509 | 60.8139 | 122.374 | 122.3785 | -122.7127 | -122.7036
159.0625 | 122.9187 | -60.672 | 61.821 | -0.13733 | 0.0094785 | 0.012463 | 1.7066e-05 | 0.063156 | 0.00090572 | 0.068526 | -60.7407 | 61.6882 | -60.8276 | -60.7773 | 61.6837 | 0.15106 | -0.12817 | 0.2243 | 61.7249 | -60.8322 | -0.15564 | -0.13275 | -0.068665 | -0.10529 | -0.13733 | -0.16022 | -0.09613 | 0.086975 | 60.5438 | 60.8963 | 122.3557 | 122.3602 | -0.068665 | 122.3969 | 60.8231 | -0.16022 | 122.3602 | -0.068665 | 60.8231 | 122.3557 | 122.3969 | -122.6486 | -122.6532
160.0625 | 122.7448 | -60.7452 | 61.9034 | -0.30518 | 0.012469 | 0.013958 | 0.0053577 | 0.063369 | -0.0014441 | 0.067458 | -60.8231 | 61.8118 | -60.8597 | -60.7636 | 61.702 | 0.068665 | -0.059509 | 0.027466 | 61.7569 | -60.9192 | -0.11444 | -0.091552 | -0.07782 | -0.018311 | -0.20142 | -0.17395 | -0.14648 | 0.036621 | 60.6857 | 60.7727 | 122.4472 | 122.5571 | -0.07782 | 122.5021 | 60.8139 | -0.17395 | 122.5571 | -0.07782 | 60.8139 | 122.4472 | 122.5021 | -122.7631 | -122.8226
161.0625 | 122.8821 | -60.6949 | 61.853 | -0.1297 | 0.010974 | 0.016522 | -0.0014783 | 0.065078 | 0.00047852 | 0.06874 | -60.7819 | 61.702 | -60.8551 | -60.8093 | 61.6516 | 0.10986 | -0.1236 | 0.14648 | 61.7249 | -60.8505 | -0.16022 | -0.15106 | -0.086975 | -0.11444 | -0.20142 | -0.15564 | -0.12817 | 0.073243 | 60.5713 | 60.8414 | 122.3465 | 122.3969 | -0.086975 | 122.4197 | 60.8047 | -0.15564 | 122.3969 | -0.086975 | 60.8047 | 122.3465 | 122.4197 | -122.7081 | -122.7036
162.0625 | 122.905 | -60.6949 | 61.8484 | 0.038147 | 0.0092649 | 0.015667 | 0.00044427 | 0.065078 | 0.00069212 | 0.069167 | -60.8322 | 61.6974 | -60.8505 | -60.8963 | 61.6013 | 0.022888 | -0.11444 | 0.082397 | 61.6882 | -60.8505 | -0.15564 | -0.15106 | -0.13733 | -0.20142 | -0.24719 | -0.15564 | -0.16022 | 0.018311 | 60.5804 | 60.7773 | 122.2961 | 122.3923 | -0.13733 | 122.3831 | 60.7178 | -0.15564 | 122.3923 | -0.13733 | 60.7178 | 122.2961 | 122.3831 | -122.699 | -122.699
163.0625 | 122.8638 | -60.672 | 61.8347 | 0.045776 | 0.010974 | 0.015667 | 0.00044427 | 0.06401 | 0.00069212 | 0.06874 | -60.8276 | 61.6974 | -60.8734 | -60.8917 | 61.5967 | 0.041199 | -0.13275 | 0.073242 | 61.7157 | -60.8551 | -0.20142 | -0.13733 | -0.15564 | -0.21973 | -0.23804 | -0.18311 | -0.11902 | 0.045776 | 60.5392 | 60.7452 | 122.2687 | 122.3694 | -0.15564 | 122.3877 | 60.7132 | -0.18311 | 122.3694 | -0.15564 | 60.7132 | 122.2687 | 122.3877 | -122.7081 | -122.6898
164.0625 | 122.8546 | -60.6766 | 61.821 | -0.045777 | 0.010333 | 0.015881 | 1.7066e-05 | 0.064437 | 0.00047852 | 0.06938 | -60.8231 | 61.6653 | -60.8414 | -60.8688 | 61.6608 | 0.15564 | -0.10529 | 0.045776 | 61.7294 | -60.8734 | -0.16479 | -0.15564 | -0.14648 | -0.19226 | -0.16022 | -0.19684 | -0.091553 | 0.018311 | 60.5713 | 60.7224 | 122.3373 | 122.3419 | -0.14648 | 122.406 | 60.8322 | -0.19684 | 122.3419 | -0.14648 | 60.8322 | 122.3373 | 122.406 | -122.6624 | -122.6944
165.0625 | 122.8912 | -60.6812 | 61.8347 | -0.15259 | 0.011401 | 0.01524 | -0.00019653 | 0.061874 | -0.0012305 | 0.069167 | -60.7636 | 61.6837 | -60.8414 | -60.8047 | 61.6653 | 0.11902 | -0.13275 | 0.1831 | 61.702 | -60.8505 | -0.16022 | -0.15106 | -0.082398 | -0.1236 | -0.16937 | -0.16937 | -0.13275 | 0.07782 | 60.5484 | 60.8643 | 122.3465 | 122.3648 | -0.082398 | 122.3831 | 60.8002 | -0.16937 | 122.3648 | -0.082398 | 60.8002 | 122.3465 | 122.3831 | -122.6761 | -122.6852
166.0625 | 122.85 | -60.7132 | 61.853 | -0.10681 | 0.0096921 | 0.015881 | 0.00044427 | 0.064437 | -0.00080328 | 0.067458 | -60.8414 | 61.702 | -60.8551 | -60.8917 | 61.615 | 0.041199 | -0.10529 | 0.091553 | 61.734 | -60.8734 | -0.14191 | -0.15106 | -0.12817 | -0.17853 | -0.23804 | -0.16022 | -0.11902 | 0.013733 | 60.6079 | 60.8047 | 122.3282 | 122.4152 | -0.12817 | 122.4472 | 60.7544 | -0.16022 | 122.4152 | -0.12817 | 60.7544 | 122.3282 | 122.4472 | -122.7081 | -122.7264
167.0625 | 122.8455 | -60.6949 | 61.8622 | -0.061035 | 0.012683 | 0.014813 | -0.00041013 | 0.065719 | -0.00037588 | 0.06938 | -60.8185 | 61.6974 | -60.8597 | -60.8734 | 61.5967 | 0.036621 | -0.13733 | 0.068665 | 61.7157 | -60.878 | -0.16479 | -0.1648 | -0.1236 | -0.17853 | -0.2655 | -0.18311 | -0.14648 | 0.041199 | 60.5576 | 60.7636 | 122.2916 | 122.3923 | -0.1236 | 122.4106 | 60.7315 | -0.18311 | 122.3923 | -0.1236 | 60.7315 | 122.2916 | 122.4106 | -122.7219 | -122.7402
168.0625 | 122.8271 | -60.6766 | 61.8347 | 0.0076294 | 0.0099057 | 0.015026 | -0.00083733 | 0.065292 | -0.0010169 | 0.068953 | -60.8185 | 61.6974 | -60.878 | -60.8871 | 61.6104 | 0.022888 | -0.14191 | 0.064087 | 61.7111 | -60.8871 | -0.20142 | -0.13733 | -0.14191 | -0.21057 | -0.2243 | -0.21057 | -0.1236 | 0.05951 | 60.5347 | 60.7407 | 122.287 | 122.374 | -0.14191 | 122.3877 | 60.6995 | -0.21057 | 122.374 | -0.14191 | 60.6995 | 122.287 | 122.3877 | -122.7127 | -122.7219
169.0625 | 122.8455 | -60.6766 | 61.8301 | 0.12207 | 0.012256 | 0.015454 | 0.0015125 | 0.063369 | 0.0026147 | 0.06639 | -60.759 | 61.6791 | -60.8505 | -60.8414 | 61.6333 | 0.045776 | -0.23346 | 0.086975 | 61.6791 | -60.8871 | -0.17395 | -0.15106 | -0.082397 | -0.16479 | -0.19684 | -0.21057 | -0.15106 | 0.091553 | 60.4431 | 60.7636 | 122.3099 | 122.3557 | -0.082397 | 122.3557 | 60.7224 | -0.21057 | 122.3557 | -0.082397 | 60.7224 | 122.3099 | 122.3557 | -122.6807 | -122.7173
170.0625 | 122.8546 | -60.704 | 61.8256 | -0.1297 | 0.012469 | 0.011822 | -0.0023327 | 0.062087 | 0.0011193 | 0.066176 | -60.8276 | 61.6791 | -60.8643 | -60.8505 | 61.615 | 0.064087 | -0.13733 | 0.086975 | 61.7065 | -60.8551 | -0.16022 | -0.14648 | -0.1236 | -0.14648 | -0.21057 | -0.15106 | -0.11902 | 0.036621 | 60.5667 | 60.791 | 122.319 | 122.3831 | -0.1236 | 122.4106 | 60.7681 | -0.15106 | 122.3831 | -0.1236 | 60.7681 | 122.319 | 122.4106 | -122.6898 | -122.6807
171.0625 | 122.8638 | -60.7178 | 61.821 | 0.099182 | 0.01311 | 0.018231 | 0.0017261 | 0.064437 | -0.00016228 | 0.068312 | -60.759 | 61.6791 | -60.8643 | -60.8459 | 61.615 | 0.041199 | -0.21973 | 0.073242 | 61.7065 | -60.8917 | -0.14648 | -0.14191 | -0.041199 | -0.12817 | -0.20599 | -0.17395 | -0.11444 | 0.10529 | 60.498 | 60.791 | 122.3328 | 122.3969 | -0.041199 | 122.4243 | 60.759 | -0.17395 | 122.3969 | -0.041199 | 60.759 | 122.3328 | 122.4243 | -122.6852 | -122.7127
172.0625 | 122.8226 | -60.7132 | 61.8118 | 0.030517 | 0.011615 | 0.016522 | 0.0019397 | 0.063583 | 0.0011193 | 0.068526 | -60.8093 | 61.6974 | -60.8368 | -60.8871 | 61.6058 | 0.004578 | -0.1831 | 0.059509 | 61.6928 | -60.8688 | -0.1236 | -0.11444 | -0.09613 | -0.17395 | -0.20599 | -0.15564 | -0.11902 | 0.027466 | 60.5301 | 60.7727 | 122.319 | 122.4106 | -0.09613 | 122.406 | 60.7178 | -0.15564 | 122.4106 | -0.09613 | 60.7178 | 122.319 | 122.406 | -122.6486 | -122.6807
173.0625 | 122.8409 | -60.6812 | 61.8118 | 0.061035 | 0.012042 | 0.014813 | 0.00087167 | 0.065719 | 5.1318e-05 | 0.068099 | -60.7773 | 61.6699 | -60.8734 | -60.8643 | 61.615 | 0.027466 | -0.21515 | 0.059509 | 61.702 | -60.8734 | -0.19226 | -0.14191 | -0.096131 | -0.18311 | -0.19684 | -0.19226 | -0.10986 | 0.09613 | 60.466 | 60.7407 | 122.2961 | 122.3511 | -0.096131 | 122.3831 | 60.7086 | -0.19226 | 122.3511 | -0.096131 | 60.7086 | 122.2961 | 122.3831 | -122.6852 | -122.6852
174.0625 | 122.8546 | -60.6903 | 61.821 | 0.076294 | 0.012256 | 0.017163 | 0.0012989 | 0.065933 | -0.0010169 | 0.068312 | -60.759 | 61.7249 | -60.8734 | -60.8322 | 61.6287 | 0.059509 | -0.24261 | 0.073242 | 61.6837 | -60.9009 | -0.1831 | -0.09613 | -0.068664 | -0.14191 | -0.19226 | -0.21057 | -0.13733 | 0.11444 | 60.4477 | 60.7636 | 122.319 | 122.4152 | -0.068664 | 122.374 | 60.7498 | -0.21057 | 122.4152 | -0.068664 | 60.7498 | 122.319 | 122.374 | -122.6944 | -122.7219
175.0625 | 122.8271 | -60.6949 | 61.8393 | 0.083923 | 0.010974 | 0.014385 | 0.0017261 | 0.065505 | -0.0010169 | 0.068953 | -60.7956 | 61.6928 | -60.8734 | -60.8688 | 61.5967 | 0.009155 | -0.20599 | 0.054932 | 61.6928 | -60.9009 | -0.17853 | -0.14648 | -0.10071 | -0.17395 | -0.24261 | -0.20599 | -0.14648 | 0.07782 | 60.4889 | 60.7498 | 122.2916 | 122.3877 | -0.10071 | 122.3877 | 60.704 | -0.20599 | 122.3877 | -0.10071 | 60.704 | 122.2916 | 122.3877 | -122.7127 | -122.7402
176.0625 | 122.8821 | -60.6857 | 61.821 | 0.076294 | 0.01311 | 0.014599 | 0.0049305 | 0.065933 | -0.00016228 | 0.06938 | -60.8047 | 61.7203 | -60.8688 | -60.8414 | 61.6333 | 0.045776 | -0.24719 | 0.07782 | 61.6745 | -60.91 | -0.1831 | -0.10071 | -0.11902 | -0.15564 | -0.18768 | -0.2243 | -0.14648 | 0.064086 | 60.4385 | 60.7636 | 122.319 | 122.406 | -0.11902 | 122.3602 | 60.7315 | -0.2243 | 122.406 | -0.11902 | 60.7315 | 122.319 | 122.3602 | -122.6898 | -122.731
177.0625 | 122.8821 | -60.6903 | 61.8164 | 0.068664 | 0.013324 | 0.018871 | 0.0049305 | 0.065933 | 0.00026492 | 0.067244 | -60.791 | 61.7477 | -60.8734 | -60.8414 | 61.5921 | 0.009155 | -0.24261 | 0.054932 | 61.6791 | -60.9283 | -0.1831 | -0.068664 | -0.10071 | -0.15106 | -0.2243 | -0.23804 | -0.13733 | 0.082397 | 60.4477 | 60.7452 | 122.2824 | 122.4381 | -0.10071 | 122.3694 | 60.6995 | -0.23804 | 122.4381 | -0.10071 | 60.6995 | 122.2824 | 122.3694 | -122.6898 | -122.7448
178.0625 | 122.8867 | -60.6812 | 61.8164 | 0.14496 | 0.011188 | 0.017803 | 0.0034351 | 0.065933 | -0.0035803 | 0.067885 | -60.7407 | 61.7249 | -60.8505 | -60.8322 | 61.6379 | 0.045776 | -0.27466 | 0.073242 | 61.6653 | -60.9009 | -0.16937 | -0.091552 | -0.05951 | -0.15106 | -0.17853 | -0.21973 | -0.15106 | 0.10986 | 60.4065 | 60.7544 | 122.319 | 122.406 | -0.05951 | 122.3465 | 60.7269 | -0.21973 | 122.406 | -0.05951 | 60.7269 | 122.319 | 122.3465 | -122.6669 | -122.7173
179.0625 | 122.8592 | -60.6949 | 61.8164 | -0.83923 | 0.012042 | 0.018871 | 0.0027943 | 0.06636 | 0.00069212 | 0.06874 | -60.7269 | 61.7477 | -60.8368 | -60.8414 | 61.6196 | 0.032043 | -0.2655 | 0.09613 | 61.6791 | -60.91 | -0.14191 | -0.068664 | -0.032044 | -0.14648 | -0.19684 | -0.21515 | -0.13733 | 0.10986 | 60.4294 | 60.791 | 122.3145 | 122.4426 | -0.032044 | 122.374 | 60.7269 | -0.21515 | 122.4426 | -0.032044 | 60.7269 | 122.3145 | 122.374 | -122.6532 | -122.7264
180.0625 | 122.8867 | -60.6812 | 61.8439 | -0.16785 | 0.012683 | 0.01289 | -0.00041013 | 0.063583 | -0.0025123 | 0.070876 | -60.7269 | 61.6928 | -60.8322 | -60.7727 | 61.7157 | 0.14191 | -0.15564 | 0.21057 | 61.7203 | -60.8688 | -0.15106 | -0.15106 | -0.045777 | -0.091553 | -0.12817 | -0.18768 | -0.1236 | 0.10529 | 60.5255 | 60.8917 | 122.3969 | 122.374 | -0.045777 | 122.4014 | 60.8231 | -0.18768 | 122.374 | -0.045777 | 60.8231 | 122.3969 | 122.4014 | -122.6761 | -122.7127
181.0625 | 122.9141 | -60.7086 | 61.8256 | 0.16022 | 0.012897 | 0.016308 | 0.0023669 | 0.067214 | -0.0010169 | 0.070021 | -60.7452 | 61.7111 | -60.8276 | -60.8322 | 61.6379 | 0.045776 | -0.28839 | -0.004578 | 61.6562 | -60.91 | -0.11902 | -0.11444 | -0.036621 | -0.1236 | -0.18768 | -0.20142 | -0.16937 | 0.082398 | 60.4202 | 60.704 | 122.3465 | 122.4197 | -0.036621 | 122.3648 | 60.7544 | -0.20142 | 122.4197 | -0.036621 | 60.7544 | 122.3465 | 122.3648 | -122.6532 | -122.7356
182.0625 | 122.8775 | -60.6857 | 61.8347 | 0.15259 | 0.013324 | 0.016735 | 0.0030079 | 0.065933 | -0.0012305 | 0.067885 | -60.7452 | 61.7294 | -60.8551 | -60.8368 | 61.6379 | 0.041199 | -0.29297 | 0.068665 | 61.6928 | -60.878 | -0.16937 | -0.10529 | -0.059509 | -0.15106 | -0.19684 | -0.19226 | -0.14191 | 0.10986 | 60.3928 | 60.7544 | 122.3236 | 122.4152 | -0.059509 | 122.3785 | 60.7269 | -0.19226 | 122.4152 | -0.059509 | 60.7269 | 122.3236 | 122.3785 | -122.6898 | -122.7127
183.0625 | 122.8363 | -60.7269 | 61.8301 | 0.16785 | 0.01311 | 0.017376 | 0.0038623 | 0.066787 | -0.00058968 | 0.06874 | -60.8276 | 61.7661 | -60.91 | -60.9146 | 61.5692 | -0.027466 | -0.18768 | -0.009155 | 61.7203 | -60.9375 | -0.18311 | -0.064087 | -0.10071 | -0.18768 | -0.26093 | -0.21057 | -0.10986 | 0.082397 | 60.5392 | 60.7178 | 122.2961 | 122.493 | -0.10071 | 122.4472 | 60.6995 | -0.21057 | 122.493 | -0.10071 | 60.6995 | 122.2961 | 122.4472 | -122.7402 | -122.7676
184.0625 | 122.8088 | -60.7452 | 61.8256 | 0.099182 | 0.013751 | 0.018444 | 0.0051441 | 0.067642 | -0.00058968 | 0.068099 | -60.8414 | 61.8073 | -60.8917 | -60.9192 | 61.5601 | -0.045776 | -0.16937 | -0.004578 | 61.7157 | -60.9238 | -0.14649 | -0.018311 | -0.096131 | -0.17395 | -0.2655 | -0.17853 | -0.10986 | 0.050354 | 60.5759 | 60.7407 | 122.3053 | 122.5525 | -0.096131 | 122.4609 | 60.6995 | -0.17853 | 122.5525 | -0.096131 | 60.6995 | 122.3053 | 122.4609 | -122.7173 | -122.7493
185.0625 | 122.8455 | -60.6903 | 61.8439 | -0.083924 | 0.011401 | 0.015454 | -0.00083733 | 0.064437 | 0.00026492 | 0.068099 | -60.7132 | 61.7432 | -60.8322 | -60.8734 | 61.6058 | 0.013733 | -0.15564 | 0.082397 | 61.7111 | -60.8871 | -0.14191 | -0.10071 | -0.022888 | -0.1831 | -0.23804 | -0.19684 | -0.13275 | 0.11902 | 60.5347 | 60.7727 | 122.2961 | 122.4335 | -0.022888 | 122.4014 | 60.704 | -0.19684 | 122.4335 | -0.022888 | 60.704 | 122.2961 | 122.4014 | -122.6761 | -122.731
186.0625 | 122.905 | -60.7315 | 61.8027 | 0.1297 | 0.013751 | 0.018231 | 0.0025807 | 0.065292 | -0.0010169 | 0.069167 | -60.7544 | 61.7249 | -60.8688 | -60.8505 | 61.6333 | 0.045776 | -0.29755 | 0.07782 | 61.6562 | -60.9238 | -0.13733 | -0.077819 | -0.022889 | -0.11902 | -0.16937 | -0.19226 | -0.14648 | 0.11444 | 60.434 | 60.8093 | 122.3648 | 122.4564 | -0.022889 | 122.3877 | 60.7773 | -0.19226 | 122.4564 | -0.022889 | 60.7773 | 122.3648 | 122.3877 | -122.6715 | -122.7264
187.0625 | 122.8683 | -60.6995 | 61.7752 | 0.1297 | 0.013324 | 0.017163 | 0.0049305 | 0.063796 | -0.00058968 | 0.069808 | -60.7544 | 61.734 | -60.8414 | -60.8276 | 61.6333 | 0.036621 | -0.29755 | 0.073242 | 61.6882 | -60.8963 | -0.14191 | -0.041199 | -0.054932 | -0.12817 | -0.14191 | -0.19684 | -0.086976 | 0.086975 | 60.4019 | 60.7727 | 122.3328 | 122.4335 | -0.054932 | 122.3877 | 60.7361 | -0.19684 | 122.4335 | -0.054932 | 60.7361 | 122.3328 | 122.3877 | -122.6166 | -122.6715
188.0625 | 122.8821 | -60.6766 | 61.8301 | 0.091553 | 0.012256 | 0.016949 | 0.0030079 | 0.06636 | -0.0018713 | 0.066603 | -60.7498 | 61.7157 | -60.8459 | -60.8551 | 61.6287 | 0.036621 | -0.28381 | 0.064087 | 61.6882 | -60.8963 | -0.16937 | -0.11444 | -0.073242 | -0.17853 | -0.20142 | -0.21973 | -0.14191 | 0.09613 | 60.3928 | 60.7407 | 122.3053 | 122.3923 | -0.073242 | 122.3648 | 60.7132 | -0.21973 | 122.3923 | -0.073242 | 60.7132 | 122.3053 | 122.3648 | -122.6761 | -122.7264
189.0625 | 122.8775 | -60.672 | 61.8164 | -0.18311 | 0.011615 | 0.012463 | -0.00062373 | 0.06401 | -0.00080328 | 0.069808 | -60.7544 | 61.7111 | -60.8597 | -60.8047 | 61.6974 | 0.13733 | -0.19684 | 0.1831 | 61.7111 | -60.8734 | -0.18768 | -0.10529 | -0.082398 | -0.13275 | -0.11902 | -0.20142 | -0.10529 | 0.10528 | 60.4752 | 60.8551 | 122.3694 | 122.3831 | -0.082398 | 122.3831 | 60.8093 | -0.20142 | 122.3831 | -0.082398 | 60.8093 | 122.3694 | 122.3831 | -122.6761 | -122.6898
190.0625 | 122.8683 | -60.6949 | 61.8393 | -0.17548 | 0.0086239 | 0.013317 | -0.00083733 | 0.063156 | -0.0010169 | 0.06938 | -60.8276 | 61.7294 | -60.878 | -60.8871 | 61.6287 | 0.054932 | -0.16937 | 0.09613 | 61.7111 | -60.8963 | -0.18311 | -0.10986 | -0.13275 | -0.19226 | -0.21057 | -0.20142 | -0.12817 | 0.050354 | 60.5255 | 60.791 | 122.3236 | 122.4243 | -0.13275 | 122.406 | 60.7498 | -0.20142 | 122.4243 | -0.13275 | 60.7498 | 122.3236 | 122.406 | -122.7173 | -122.7356
191.0625 | 122.8455 | -60.6903 | 61.8256 | 0.21362 | 0.011401 | 0.013958 | 0.0038623 | 0.067001 | 0.00047852 | 0.069594 | -60.759 | 61.7386 | -60.8643 | -60.8276 | 61.6241 | 0.022888 | -0.28839 | 0.064087 | 61.6837 | -60.9009 | -0.17395 | -0.086976 | -0.068664 | -0.13733 | -0.20142 | -0.21057 | -0.14191 | 0.10529 | 60.4019 | 60.7544 | 122.3145 | 122.4289 | -0.068664 | 122.374 | 60.7132 | -0.21057 | 122.4289 | -0.068664 | 60.7132 | 122.3145 | 122.374 | -122.6898 | -122.7264
192.0625 | 122.8958 | -60.6766 | 61.7935 | 0.23651 | 0.014819 | 0.013958 | 0.0066395 | 0.064651 | 0.00090572 | 0.069808 | -60.759 | 61.7889 | -60.8688 | -60.8505 | 61.6104 | 0.027466 | -0.27008 | 0.068665 | 61.6928 | -60.91 | -0.19226 | -0.004578 | -0.082397 | -0.17395 | -0.1831 | -0.23346 | -0.10071 | 0.10986 | 60.4065 | 60.7452 | 122.287 | 122.4655 | -0.082397 | 122.3694 | 60.704 | -0.23346 | 122.4655 | -0.082397 | 60.704 | 122.287 | 122.3694 | -122.6624 | -122.7036
193.0625 | 122.8592 | -60.6674 | 61.8027 | 0.16022 | 0.011828 | 0.017803 | 0.0040759 | 0.065719 | 0.0013329 | 0.068312 | -60.7681 | 61.7477 | -60.878 | -60.8322 | 61.7065 | 0.041199 | -0.52643 | 0.15564 | 61.6653 | -60.9146 | -0.21057 | -0.054931 | -0.10071 | -0.16479 | -0.09613 | -0.24719 | -0.13733 | 0.10986 | 60.141 | 60.8231 | 122.374 | 122.4152 | -0.10071 | 122.3328 | 60.7086 | -0.24719 | 122.4152 | -0.10071 | 60.7086 | 122.374 | 122.3328 | -122.6807 | -122.7173
194.0781 | 122.7676 | -60.6995 | 61.9125 | -0.30518 | 0.012897 | 0.015667 | 0.0034351 | 0.065292 | -0.0010169 | 0.068099 | -60.8414 | 61.821 | -60.8734 | -60.8917 | 61.5692 | 0.013733 | 0.054932 | 0.07782 | 61.7981 | -60.9146 | -0.17395 | -0.091553 | -0.14191 | -0.19226 | -0.34332 | -0.21515 | -0.11444 | 0.032043 | 60.7544 | 60.7773 | 122.2687 | 122.5204 | -0.14191 | 122.4976 | 60.7132 | -0.21515 | 122.5204 | -0.14191 | 60.7132 | 122.2687 | 122.4976 | -122.7859 | -122.8271
195.0625 | 122.85 | -60.7178 | 61.8393 | 0.0076294 | 0.011401 | 0.014385 | -0.0016919 | 0.064865 | 0.00047852 | 0.068953 | -60.8322 | 61.6974 | -60.8551 | -60.8917 | 61.6653 | 0.13733 | -0.16022 | 0.041199 | 61.7523 | -60.8597 | -0.13733 | -0.14191 | -0.11444 | -0.17395 | -0.17395 | -0.14191 | -0.086975 | 0.022889 | 60.5576 | 60.759 | 122.3831 | 122.4152 | -0.11444 | 122.4701 | 60.8551 | -0.14191 | 122.4152 | -0.11444 | 60.8551 | 122.3831 | 122.4701 | -122.6944 | -122.699
196.0625 | 122.8546 | -60.6766 | 61.8164 | 0.099182 | 0.013537 | 0.016735 | 0.0032215 | 0.067428 | -0.00080328 | 0.068526 | -60.7498 | 61.7111 | -60.8505 | -60.8368 | 61.6241 | 0.041199 | -0.3067 | 0.059509 | 61.6837 | -60.9009 | -0.17395 | -0.10529 | -0.073242 | -0.16022 | -0.19226 | -0.2243 | -0.13275 | 0.10071 | 60.3699 | 60.7361 | 122.3007 | 122.3877 | -0.073242 | 122.3602 | 60.7178 | -0.2243 | 122.3877 | -0.073242 | 60.7178 | 122.3007 | 122.3602 | -122.6669 | -122.7173
197.0625 | 122.8638 | -60.7086 | 61.8301 | 0.11444 | 0.015674 | 0.018658 | 0.0066395 | 0.06636 | -0.0012305 | 0.068526 | -60.8139 | 61.7615 | -60.8963 | -60.8688 | 61.5555 | -0.009155 | -0.25635 | 0.013733 | 61.702 | -60.9329 | -0.18768 | -0.068664 | -0.10529 | -0.16022 | -0.27466 | -0.2243 | -0.12817 | 0.082397 | 60.4523 | 60.7224 | 122.2641 | 122.4701 | -0.10529 | 122.4106 | 60.6995 | -0.2243 | 122.4701 | -0.10529 | 60.6995 | 122.2641 | 122.4106 | -122.7264 | -122.7631
198.0625 | 122.8683 | -60.6949 | 61.7981 | 0.099182 | 0.01311 | 0.015026 | 0.0030079 | 0.067001 | -0.0012305 | 0.06938 | -60.7544 | 61.7386 | -60.8597 | -60.8459 | 61.6333 | 0.041199 | -0.32501 | 0.064087 | 61.7065 | -60.9146 | -0.16479 | -0.05951 | -0.05951 | -0.15106 | -0.16479 | -0.21973 | -0.091553 | 0.10528 | 60.3699 | 60.759 | 122.3282 | 122.4335 | -0.05951 | 122.4014 | 60.7361 | -0.21973 | 122.4335 | -0.05951 | 60.7361 | 122.3282 | 122.4014 | -122.6578 | -122.7127
199.0625 | 122.8912 | -60.672 | 61.8439 | -0.30518 | 0.012256 | 0.017163 | -0.0010509 | 0.063156 | -0.00037588 | 0.068526 | -60.7407 | 61.7432 | -60.8368 | -60.9238 | 61.441 | -0.009155 | -0.11444 | 0.17395 | 61.6974 | -60.8734 | -0.1648 | -0.10071 | -0.068665 | -0.25177 | -0.40283 | -0.20142 | -0.14648 | 0.09613 | 60.5576 | 60.8459 | 122.113 | 122.4152 | -0.068665 | 122.3694 | 60.6628 | -0.20142 | 122.4152 | -0.068665 | 60.6628 | 122.113 | 122.3694 | -122.6807 | -122.7173
200.0625 | 122.905 | -60.672 | 61.8576 | -0.17548 | 0.0096921 | 0.017163 | -0.00062373 | 0.063369 | -0.0018713 | 0.069594 | -60.7315 | 61.702 | -60.8551 | -60.791 | 61.6837 | 0.11902 | -0.2243 | 0.19684 | 61.7065 | -60.8734 | -0.18311 | -0.15564 | -0.059509 | -0.11902 | -0.17395 | -0.20142 | -0.15106 | 0.1236 | 60.4477 | 60.8688 | 122.3557 | 122.374 | -0.059509 | 122.3785 | 60.791 | -0.20142 | 122.374 | -0.059509 | 60.791 | 122.3557 | 122.3785 | -122.7127 | -122.731
201.0625 | 122.85 | -60.6949 | 61.8256 | 0.10681 | 0.012469 | 0.01289 | 0.0038623 | 0.065719 | 0.00047852 | 0.06938 | -60.7498 | 61.7157 | -60.8459 | -60.8551 | 61.615 | 0.013733 | -0.30212 | 0.054932 | 61.702 | -60.8826 | -0.15106 | -0.10986 | -0.054932 | -0.16022 | -0.21057 | -0.18768 | -0.1236 | 0.09613 | 60.3928 | 60.7498 | 122.3099 | 122.4106 | -0.054932 | 122.3969 | 60.7086 | -0.18768 | 122.4106 | -0.054932 | 60.7086 | 122.3099 | 122.3969 | -122.6715 | -122.7081
202.0625 | 122.8546 | -60.672 | 61.821 | 0.068664 | 0.012256 | 0.015454 | 0.0023669 | 0.065078 | -0.00037588 | 0.069167 | -60.7544 | 61.6974 | -60.8505 | -60.8597 | 61.6196 | 0.018311 | -0.29297 | 0.054932 | 61.6928 | -60.9055 | -0.17853 | -0.1236 | -0.082398 | -0.18768 | -0.20142 | -0.23346 | -0.12817 | 0.09613 | 60.379 | 60.7269 | 122.2916 | 122.3694 | -0.082398 | 122.3648 | 60.6903 | -0.23346 | 122.3694 | -0.082398 | 60.6903 | 122.2916 | 122.3648 | -122.6715 | -122.7264
203.0625 | 122.8363 | -60.6995 | 61.7615 | 0.13733 | 0.013965 | 0.017803 | 0.0034351 | 0.064437 | -0.0016577 | 0.068953 | -60.759 | 61.7065 | -60.8551 | -60.8185 | 61.6333 | 0.027466 | -0.34332 | 0.064087 | 61.702 | -60.91 | -0.15564 | -0.054932 | -0.059509 | -0.11902 | -0.12817 | -0.21057 | -0.05951 | 0.096131 | 60.3561 | 60.7636 | 122.3328 | 122.406 | -0.059509 | 122.4014 | 60.7269 | -0.21057 | 122.406 | -0.059509 | 60.7269 | 122.3328 | 122.4014 | -122.6166 | -122.6715
204.0625 | 122.9004 | -60.6903 | 61.8576 | -0.21362 | 0.0094785 | 0.013958 | 1.7066e-05 | 0.063796 | -0.00080328 | 0.06938 | -60.7269 | 61.7294 | -60.8047 | -60.7773 | 61.702 | 0.1236 | -0.2243 | 0.20599 | 61.7157 | -60.8734 | -0.11444 | -0.12817 | -0.036621 | -0.086975 | -0.15564 | -0.1831 | -0.14191 | 0.07782 | 60.466 | 60.8963 | 122.3923 | 122.4197 | -0.036621 | 122.406 | 60.8139 | -0.1831 | 122.4197 | -0.036621 | 60.8139 | 122.3923 | 122.406 | -122.6624 | -122.731
205.0625 | 122.8821 | -60.6766 | 61.8439 | -0.091553 | 0.010974 | 0.017163 | 1.7066e-05 | 0.063369 | -0.0040075 | 0.06938 | -60.7956 | 61.7111 | -60.8688 | -60.8414 | 61.6562 | 0.068665 | -0.19684 | 0.10986 | 61.7477 | -60.8459 | -0.19226 | -0.13275 | -0.11902 | -0.16479 | -0.18768 | -0.16937 | -0.09613 | 0.073242 | 60.4797 | 60.7864 | 122.3328 | 122.3877 | -0.11902 | 122.4243 | 60.7452 | -0.16937 | 122.3877 | -0.11902 | 60.7452 | 122.3328 | 122.4243 | -122.7127 | -122.6898
206.0625 | 122.8455 | -60.7178 | 61.8576 | 0.038147 | 0.011188 | 0.014385 | -0.00019653 | 0.064865 | -0.00058968 | 0.067885 | -60.8093 | 61.702 | -60.8505 | -60.8963 | 61.5967 | -0.013733 | -0.24719 | 0.036621 | 61.7065 | -60.8826 | -0.13275 | -0.15564 | -0.091553 | -0.17853 | -0.26093 | -0.16479 | -0.15106 | 0.041199 | 60.4706 | 60.7544 | 122.3145 | 122.4197 | -0.091553 | 122.4243 | 60.704 | -0.16479 | 122.4197 | -0.091553 | 60.704 | 122.3145 | 122.4243 | -122.7081 | -122.7402
207.0625 | 122.8363 | -60.6903 | 61.8347 | 0.061035 | 0.013537 | 0.016949 | 0.0025807 | 0.062515 | -0.0016577 | 0.067885 | -60.8047 | 61.6837 | -60.8643 | -60.8917 | 61.5738 | -0.022888 | -0.24719 | 0.050354 | 61.7111 | -60.9146 | -0.17395 | -0.15106 | -0.11444 | -0.20142 | -0.26093 | -0.2243 | -0.1236 | 0.059509 | 60.4431 | 60.7407 | 122.2641 | 122.374 | -0.11444 | 122.4014 | 60.6674 | -0.2243 | 122.374 | -0.11444 | 60.6674 | 122.2641 | 122.4014 | -122.699 | -122.7493
208.0625 | 122.8317 | -60.6628 | 61.8622 | 0.099182 | 0.013324 | 0.015881 | 0.0019397 | 0.063369 | -0.00016228 | 0.06874 | -60.8002 | 61.702 | -60.8505 | -60.8734 | 61.5784 | -0.022888 | -0.26093 | 0.041199 | 61.6974 | -60.9146 | -0.18768 | -0.16022 | -0.13733 | -0.21057 | -0.28381 | -0.25177 | -0.1648 | 0.050354 | 60.4019 | 60.704 | 122.2412 | 122.3648 | -0.13733 | 122.3602 | 60.64 | -0.25177 | 122.3648 | -0.13733 | 60.64 | 122.2412 | 122.3602 | -122.7127 | -122.7768
209.0625 | 122.818 | -60.6995 | 61.8439 | 0.061035 | 0.01311 | 0.016735 | 0.0019397 | 0.063583 | -0.0016577 | 0.068312 | -60.8139 | 61.702 | -60.8551 | -60.8597 | 61.5738 | -0.009155 | -0.2655 | 0.018311 | 61.6974 | -60.878 | -0.15564 | -0.14191 | -0.11444 | -0.16022 | -0.27008 | -0.17853 | -0.14648 | 0.041199 | 60.434 | 60.7178 | 122.2733 | 122.4014 | -0.11444 | 122.3969 | 60.6903 | -0.17853 | 122.4014 | -0.11444 | 60.6903 | 122.2733 | 122.3969 | -122.699 | -122.7219
210.0625 | 122.8867 | -60.6812 | 61.8073 | 0.13733 | 0.010119 | 0.015454 | 0.0027943 | 0.064224 | -0.0014441 | 0.067458 | -60.7498 | 61.6791 | -60.8459 | -60.8322 | 61.6241 | 0.018311 | -0.31586 | 0.073242 | 61.7111 | -60.8917 | -0.1648 | -0.12817 | -0.068665 | -0.15106 | -0.1831 | -0.21057 | -0.09613 | 0.09613 | 60.3653 | 60.7544 | 122.3053 | 122.3602 | -0.068665 | 122.3923 | 60.6995 | -0.21057 | 122.3602 | -0.068665 | 60.6995 | 122.3053 | 122.3923 | -122.6532 | -122.699
211.0625 | 122.8821 | -60.672 | 61.821 | -0.37384 | 0.010974 | 0.013531 | 0.0040759 | 0.065719 | 0.00069212 | 0.06874 | -60.7544 | 61.702 | -60.8551 | -60.8322 | 61.6333 | 0.027466 | -0.3067 | 0.064087 | 61.6928 | -60.8917 | -0.18311 | -0.11902 | -0.082398 | -0.16022 | -0.18768 | -0.21973 | -0.12817 | 0.10071 | 60.3653 | 60.7361 | 122.3053 | 122.374 | -0.082398 | 122.3648 | 60.6995 | -0.21973 | 122.374 | -0.082398 | 60.6995 | 122.3053 | 122.3648 | -122.6761 | -122.7127
212.0625 | 122.8317 | -60.6812 | 61.8347 | 0.061035 | 0.0094785 | 0.017376 | 0.0023669 | 0.064224 | -0.0010169 | 0.067458 | -60.7956 | 61.6882 | -60.8551 | -60.8826 | 61.5967 | -0.009155 | -0.27924 | 0.027466 | 61.6974 | -60.9009 | -0.17395 | -0.14648 | -0.11444 | -0.20142 | -0.23804 | -0.21973 | -0.13733 | 0.05951 | 60.4019 | 60.7086 | 122.2778 | 122.3694 | -0.11444 | 122.3785 | 60.672 | -0.21973 | 122.3694 | -0.11444 | 60.672 | 122.2778 | 122.3785 | -122.6898 | -122.7356
213.0625 | 122.8271 | -60.6812 | 61.8347 | -0.061035 | 0.011188 | 0.016094 | 1.7066e-05 | 0.064651 | 0.00090572 | 0.067458 | -60.8185 | 61.702 | -60.8459 | -60.8826 | 61.5875 | -0.009155 | -0.23346 | 0.032043 | 61.702 | -60.878 | -0.1648 | -0.13275 | -0.13733 | -0.20142 | -0.24719 | -0.19684 | -0.13275 | 0.027466 | 60.4477 | 60.7132 | 122.2687 | 122.3831 | -0.13733 | 122.3831 | 60.672 | -0.19684 | 122.3831 | -0.13733 | 60.672 | 122.2687 | 122.3831 | -122.6807 | -122.7127
214.0625 | 122.8409 | -60.6903 | 61.8393 | 0.030517 | 0.012042 | 0.01289 | 0.00023067 | 0.062942 | -0.0020849 | 0.070021 | -60.8047 | 61.6974 | -60.8643 | -60.8688 | 61.6013 | -0.009155 | -0.23804 | 0.022888 | 61.702 | -60.8917 | -0.17395 | -0.14191 | -0.11444 | -0.17853 | -0.23804 | -0.20142 | -0.13733 | 0.059509 | 60.4523 | 60.7132 | 122.2916 | 122.3877 | -0.11444 | 122.3923 | 60.6812 | -0.20142 | 122.3877 | -0.11444 | 60.6812 | 122.2916 | 122.3923 | -122.7036 | -122.731
215.0625 | 122.8775 | -60.6857 | 61.8668 | 0.82397 | 0.010974 | 0.019512 | 0.0027943 | 0.064651 | -0.0037939 | 0.069808 | -60.6903 | 61.7249 | -60.8459 | -60.8047 | 61.7065 | 0.11444 | -0.2243 | 0.1831 | 61.7432 | -60.8871 | -0.16022 | -0.14191 | -0.004578 | -0.11902 | -0.16022 | -0.20142 | -0.1236 | 0.15564 | 60.4614 | 60.8688 | 122.3923 | 122.4106 | -0.004578 | 122.4289 | 60.8002 | -0.20142 | 122.4106 | -0.004578 | 60.8002 | 122.3923 | 122.4289 | -122.7127 | -122.7539
216.0625 | 122.8271 | -60.7086 | 61.8393 | 0.099182 | 0.010547 | 0.01759 | -0.0012647 | 0.062942 | -0.00080328 | 0.068526 | -60.8002 | 61.7111 | -60.8643 | -60.878 | 61.5967 | -0.018311 | -0.28381 | 0.022888 | 61.7065 | -60.878 | -0.15564 | -0.12817 | -0.091553 | -0.16937 | -0.24261 | -0.16937 | -0.13275 | 0.064087 | 60.4248 | 60.7315 | 122.3053 | 122.4197 | -0.091553 | 122.4152 | 60.6903 | -0.16937 | 122.4197 | -0.091553 | 60.6903 | 122.3053 | 122.4152 | -122.7036 | -122.7173
217.0625 | 122.8912 | -60.6812 | 61.8347 | 0.076294 | 0.013324 | 0.021008 | 0.0019397 | 0.063583 | 0.00047852 | 0.06938 | -60.7407 | 61.702 | -60.8459 | -60.8231 | 61.6379 | 0.022888 | -0.32501 | 0.068665 | 61.6653 | -60.8917 | -0.1648 | -0.13275 | -0.05951 | -0.14191 | -0.19684 | -0.21057 | -0.16937 | 0.10529 | 60.3561 | 60.7498 | 122.319 | 122.3831 | -0.05951 | 122.3465 | 60.704 | -0.21057 | 122.3831 | -0.05951 | 60.704 | 122.319 | 122.3465 | -122.6807 | -122.7264
218.0625 | 122.8592 | -60.6903 | 61.8027 | 0.12207 | 0.012469 | 0.018871 | 0.00044427 | 0.065719 | -0.0031531 | 0.067458 | -60.8322 | 61.6562 | -60.8368 | -60.8047 | 61.6608 | 0.022888 | -0.3479 | 0.059509 | 61.6882 | -60.9146 | -0.14648 | -0.14648 | -0.14191 | -0.11444 | -0.14191 | -0.2243 | -0.11444 | 0.004578 | 60.3424 | 60.7498 | 122.3511 | 122.3465 | -0.14191 | 122.3785 | 60.7132 | -0.2243 | 122.3465 | -0.14191 | 60.7132 | 122.3511 | 122.3785 | -122.6395 | -122.7173
219.0625 | 122.8271 | -60.6995 | 61.8164 | 0.11444 | 0.011401 | 0.019512 | 0.0021533 | 0.065292 | 0.00090572 | 0.067031 | -60.7819 | 61.7157 | -60.8826 | -60.8459 | 61.6333 | 0.009155 | -0.33417 | 0.036621 | 61.6928 | -60.9009 | -0.1831 | -0.10071 | -0.082397 | -0.14648 | -0.1831 | -0.20142 | -0.1236 | 0.10071 | 60.3653 | 60.7361 | 122.3328 | 122.4152 | -0.082397 | 122.3923 | 60.7086 | -0.20142 | 122.4152 | -0.082397 | 60.7086 | 122.3328 | 122.3923 | -122.699 | -122.7173
220.0625 | 122.8729 | -60.6674 | 61.8393 | -0.28992 | 0.011401 | 0.012463 | 0.0038623 | 0.064437 | -0.00080328 | 0.067458 | -60.7498 | 61.7203 | -60.8276 | -60.7315 | 61.6882 | 0.082397 | -0.23346 | 0.17395 | 61.7477 | -60.8551 | -0.16022 | -0.11902 | -0.082398 | -0.064087 | -0.15106 | -0.18768 | -0.091552 | 0.07782 | 60.434 | 60.8414 | 122.3557 | 122.3877 | -0.082398 | 122.4152 | 60.7498 | -0.18768 | 122.3877 | -0.082398 | 60.7498 | 122.3557 | 122.4152 | -122.6669 | -122.6944
221.0625 | 122.8363 | -60.6995 | 61.8484 | 0.13733 | 0.013751 | 0.012249 | 0.0012989 | 0.06636 | -0.00080328 | 0.070021 | -60.8047 | 61.6745 | -60.8505 | -60.8551 | 61.6104 | -0.032043 | -0.29297 | 0.018311 | 61.7157 | -60.8917 | -0.15106 | -0.17395 | -0.10529 | -0.15564 | -0.23804 | -0.19226 | -0.13275 | 0.045776 | 60.4065 | 60.7178 | 122.3099 | 122.374 | -0.10529 | 122.4152 | 60.6674 | -0.19226 | 122.374 | -0.10529 | 60.6674 | 122.3099 | 122.4152 | -122.699 | -122.7402
222.0625 | 122.8226 | -60.704 | 61.821 | 0.099182 | 0.012897 | 0.014385 | 0.00023067 | 0.06401 | 5.1318e-05 | 0.068526 | -60.7636 | 61.7157 | -60.8688 | -60.8688 | 61.6104 | -0.004578 | -0.3067 | 0.036621 | 61.702 | -60.9146 | -0.16479 | -0.10529 | -0.059509 | -0.16479 | -0.21057 | -0.21057 | -0.11902 | 0.10528 | 60.3973 | 60.7407 | 122.3145 | 122.4197 | -0.059509 | 122.406 | 60.6995 | -0.21057 | 122.4197 | -0.059509 | 60.6995 | 122.3145 | 122.406 | -122.6898 | -122.7356
223.0625 | 122.8683 | -60.6812 | 61.8347 | 0.083923 | 0.014819 | 0.015026 | 0.0021533 | 0.065292 | -0.0014441 | 0.068312 | -60.7636 | 61.6928 | -60.8688 | -60.8505 | 61.6058 | 0.018311 | -0.35706 | 0.036621 | 61.6974 | -60.8826 | -0.18768 | -0.14191 | -0.082398 | -0.16937 | -0.22888 | -0.20142 | -0.13733 | 0.10528 | 60.3241 | 60.7178 | 122.287 | 122.374 | -0.082398 | 122.3785 | 60.6995 | -0.20142 | 122.374 | -0.082398 | 60.6995 | 122.287 | 122.3785 | -122.7036 | -122.7173
224.0625 | 122.8912 | -60.6903 | 61.7981 | 0.099182 | 0.01311 | 0.019085 | 0.0049305 | 0.064437 | -0.0031531 | 0.069808 | -60.7452 | 61.7203 | -60.8414 | -60.8231 | 61.6287 | 0.018311 | -0.37994 | 0.054932 | 61.6882 | -60.91 | -0.15106 | -0.07782 | -0.054931 | -0.13275 | -0.16937 | -0.21973 | -0.10986 | 0.096131 | 60.3104 | 60.7452 | 122.319 | 122.4106 | -0.054931 | 122.3785 | 60.7086 | -0.21973 | 122.4106 | -0.054931 | 60.7086 | 122.319 | 122.3785 | -122.6395 | -122.7081
225.0625 | 122.7997 | -60.6766 | 61.8439 | 0.022888 | 0.012256 | 0.019085 | -0.0014783 | 0.065505 | -0.0020849 | 0.069167 | -60.8276 | 61.6974 | -60.8734 | -60.878 | 61.5967 | -0.004578 | -0.23804 | 0.059509 | 61.7477 | -60.8917 | -0.19684 | -0.14648 | -0.15106 | -0.20142 | -0.24719 | -0.21515 | -0.09613 | 0.045776 | 60.4385 | 60.7361 | 122.2733 | 122.374 | -0.15106 | 122.4243 | 60.672 | -0.21515 | 122.374 | -0.15106 | 60.672 | 122.2733 | 122.4243 | -122.7173 | -122.7356
226.0625 | 122.8683 | -60.6903 | 61.8347 | 0.12207 | 0.013965 | 0.020367 | 0.0017261 | 0.067855 | -0.0012305 | 0.068312 | -60.7544 | 61.7157 | -60.8734 | -60.8139 | 61.6745 | 0.045776 | -0.33875 | 0.045776 | 61.702 | -60.9055 | -0.1831 | -0.11902 | -0.064087 | -0.1236 | -0.16022 | -0.21515 | -0.13275 | 0.11902 | 60.3516 | 60.7361 | 122.3648 | 122.406 | -0.064087 | 122.3923 | 60.7361 | -0.21515 | 122.406 | -0.064087 | 60.7361 | 122.3648 | 122.3923 | -122.7081 | -122.7402
227.0625 | 122.8271 | -60.6583 | 61.8027 | 0.11444 | 0.013751 | 0.016094 | 0.0015125 | 0.062728 | -0.0010169 | 0.067031 | -60.7681 | 61.7111 | -60.8597 | -60.8322 | 61.6379 | 0.004578 | -0.34332 | 0.036621 | 61.6837 | -60.9146 | -0.20142 | -0.091552 | -0.10986 | -0.17395 | -0.16479 | -0.25635 | -0.11902 | 0.091553 | 60.3149 | 60.6949 | 122.2961 | 122.3694 | -0.10986 | 122.3419 | 60.6628 | -0.25635 | 122.3694 | -0.10986 | 60.6628 | 122.2961 | 122.3419 | -122.6624 | -122.7173
228.0625 | 122.8683 | -60.6857 | 61.821 | 0.10681 | 0.012042 | 0.01759 | 0.0010853 | 0.064437 | 0.0011193 | 0.06874 | -60.7681 | 61.7111 | -60.8551 | -60.8368 | 61.6333 | 0.004578 | -0.36621 | 0.036621 | 61.6745 | -60.91 | -0.16937 | -0.10986 | -0.082397 | -0.15106 | -0.18768 | -0.2243 | -0.14648 | 0.086976 | 60.3195 | 60.7224 | 122.319 | 122.3969 | -0.082397 | 122.3602 | 60.6903 | -0.2243 | 122.3969 | -0.082397 | 60.6903 | 122.319 | 122.3602 | -122.6761 | -122.731
229.0625 | 122.8317 | -60.6766 | 61.8164 | 0.13733 | 0.01311 | 0.019726 | 0.0025807 | 0.065505 | -0.0016577 | 0.068312 | -60.7224 | 61.7249 | -60.8597 | -60.8276 | 61.647 | 0.013733 | -0.3479 | 0.041199 | 61.6791 | -60.8963 | -0.1831 | -0.091552 | -0.045776 | -0.15106 | -0.16937 | -0.21973 | -0.13733 | 0.13733 | 60.3287 | 60.7178 | 122.3236 | 122.4014 | -0.045776 | 122.3557 | 60.6903 | -0.21973 | 122.4014 | -0.045776 | 60.6903 | 122.3236 | 122.3557 | -122.6761 | -122.7127
230.0625 | 122.8683 | -60.6583 | 61.8484 | -0.22888 | 0.0088375 | 0.01289 | 0.0015125 | 0.065719 | -0.0018713 | 0.068953 | -60.7224 | 61.6928 | -60.8185 | -60.7681 | 61.6974 | 0.10986 | -0.23346 | 0.18768 | 61.7203 | -60.8688 | -0.16022 | -0.15564 | -0.064087 | -0.10986 | -0.15106 | -0.21057 | -0.12817 | 0.09613 | 60.4248 | 60.8459 | 122.3557 | 122.3511 | -0.064087 | 122.3785 | 60.7681 | -0.21057 | 122.3511 | -0.064087 | 60.7681 | 122.3557 | 122.3785 | -122.6669 | -122.7173
231.0625 | 122.8409 | -60.6857 | 61.8118 | 0.13733 | 0.014605 | 0.020794 | 0.0049305 | 0.066146 | -0.0018713 | 0.066603 | -60.7819 | 61.7569 | -60.8688 | -60.8688 | 61.6104 | 0.013733 | -0.36163 | 0 | 61.6837 | -60.9238 | -0.1831 | -0.054932 | -0.09613 | -0.1831 | -0.20142 | -0.23804 | -0.12817 | 0.086975 | 60.3241 | 60.6857 | 122.2961 | 122.4426 | -0.09613 | 122.3694 | 60.6995 | -0.23804 | 122.4426 | -0.09613 | 60.6995 | 122.2961 | 122.3694 | -122.6807 | -122.7356
232.0625 | 122.8546 | -60.6766 | 61.8118 | 0.16022 | 0.014392 | 0.015454 | 0.0025807 | 0.067428 | -0.0020849 | 0.06938 | -60.7956 | 61.7661 | -60.8917 | -60.8688 | 61.5967 | -0.032043 | -0.33875 | 0.004578 | 61.702 | -60.9009 | -0.21515 | -0.045777 | -0.11902 | -0.19226 | -0.21515 | -0.2243 | -0.10986 | 0.096131 | 60.3378 | 60.6812 | 122.2733 | 122.4426 | -0.11902 | 122.3785 | 60.6445 | -0.2243 | 122.4426 | -0.11902 | 60.6445 | 122.2733 | 122.3785 | -122.7036 | -122.7127
233.0625 | 122.8592 | -60.6812 | 61.8393 | 0.11444 | 0.014178 | 0.018871 | 0.0040759 | 0.065505 | -0.0016577 | 0.066603 | -60.7544 | 61.7477 | -60.8551 | -60.8459 | 61.6241 | 0.004578 | -0.38452 | 0.032043 | 61.6974 | -60.9192 | -0.17395 | -0.091552 | -0.073243 | -0.1648 | -0.21515 | -0.23804 | -0.14191 | 0.10071 | 60.2966 | 60.7132 | 122.3053 | 122.4289 | -0.073243 | 122.3785 | 60.6857 | -0.23804 | 122.4289 | -0.073243 | 60.6857 | 122.3053 | 122.3785 | -122.6944 | -122.7585
234.0625 | 122.8455 | -60.6812 | 61.8256 | 0.10681 | 0.014392 | 0.019085 | 0.0021533 | 0.065933 | -0.0010169 | 0.069808 | -60.8505 | 61.6837 | -60.8597 | -60.8139 | 61.6516 | 0.013733 | -0.37079 | 0.032043 | 61.6974 | -60.9009 | -0.17853 | -0.14191 | -0.16937 | -0.13275 | -0.17395 | -0.21973 | -0.12817 | 0.009155 | 60.3104 | 60.7132 | 122.3328 | 122.3648 | -0.16937 | 122.3785 | 60.6949 | -0.21973 | 122.3648 | -0.16937 | 60.6949 | 122.3328 | 122.3785 | -122.6852 | -122.7264
235.0625 | 122.8867 | -60.672 | 61.7935 | 0.12207 | 0.012256 | 0.01759 | 0.0015125 | 0.066146 | 0.0024011 | 0.067458 | -60.7544 | 61.7249 | -60.8459 | -60.8551 | 61.4365 | -0.082397 | -0.23804 | 0.14191 | 61.6882 | -60.878 | -0.17395 | -0.068664 | -0.082398 | -0.18311 | -0.35706 | -0.20599 | -0.10529 | 0.091552 | 60.434 | 60.8139 | 122.1085 | 122.3969 | -0.082398 | 122.3602 | 60.5896 | -0.20599 | 122.3969 | -0.082398 | 60.5896 | 122.1085 | 122.3602 | -122.6395 | -122.6715
236.0625 | 122.8775 | -60.6949 | 61.7981 | 0.14496 | 0.012042 | 0.018658 | 0.0030079 | 0.065933 | -0.00058968 | 0.067671 | -60.7452 | 61.734 | -60.8368 | -60.8322 | 61.6425 | -0.004578 | -0.3891 | 0.027466 | 61.6882 | -60.9329 | -0.14191 | -0.064087 | -0.050354 | -0.13733 | -0.15564 | -0.23804 | -0.10986 | 0.091553 | 60.3058 | 60.7224 | 122.3373 | 122.4289 | -0.050354 | 122.3831 | 60.6903 | -0.23804 | 122.4289 | -0.050354 | 60.6903 | 122.3373 | 122.3831 | -122.6349 | -122.731
237.0625 | 122.8775 | -60.6628 | 61.8118 | 0.091553 | 0.014178 | 0.020794 | 0.0068531 | 0.067001 | -0.0014441 | 0.06874 | -60.7407 | 61.7294 | -60.8734 | -60.8322 | 61.6379 | 0.004578 | -0.37994 | 0.032043 | 61.6974 | -60.9192 | -0.21057 | -0.082398 | -0.07782 | -0.16937 | -0.17395 | -0.25635 | -0.11444 | 0.13275 | 60.2829 | 60.6949 | 122.3007 | 122.3923 | -0.07782 | 122.3602 | 60.6674 | -0.25635 | 122.3923 | -0.07782 | 60.6674 | 122.3007 | 122.3602 | -122.6852 | -122.731
238.0625 | 122.7951 | -60.7178 | 61.8301 | 0.076294 | 0.013965 | 0.011395 | 0.0047169 | 0.065292 | -0.00037588 | 0.06938 | -60.8276 | 61.8073 | -60.9192 | -60.9238 | 61.5555 | -0.07782 | -0.25635 | -0.050354 | 61.6974 | -60.9329 | -0.20142 | -0.022888 | -0.10986 | -0.20599 | -0.27466 | -0.21515 | -0.13275 | 0.091552 | 60.4614 | 60.6674 | 122.2733 | 122.525 | -0.10986 | 122.4152 | 60.64 | -0.21515 | 122.525 | -0.10986 | 60.64 | 122.2733 | 122.4152 | -122.7493 | -122.7631
239.0625 | 122.7905 | -60.7361 | 61.8301 | 0.068664 | 0.014178 | 0.019726 | 0.0045033 | 0.067001 | -0.0014441 | 0.069594 | -60.8231 | 61.8164 | -60.8917 | -60.9238 | 61.5417 | -0.07782 | -0.25177 | -0.073242 | 61.7432 | -60.9467 | -0.15564 | -0.013733 | -0.086975 | -0.18768 | -0.28839 | -0.21057 | -0.086975 | 0.068665 | 60.4843 | 60.6628 | 122.2778 | 122.5525 | -0.086975 | 122.4792 | 60.6583 | -0.21057 | 122.5525 | -0.086975 | 60.6583 | 122.2778 | 122.4792 | -122.7219 | -122.7768
240.0625 | 122.8043 | -60.704 | 61.821 | -0.038147 | 0.011188 | 0.019085 | -0.0016919 | 0.064437 | -0.0033667 | 0.06874 | -60.8276 | 61.7065 | -60.878 | -60.8963 | 61.6196 | -0.009155 | -0.19226 | 0.18768 | 61.7432 | -60.8826 | -0.17395 | -0.11444 | -0.1236 | -0.19226 | -0.20142 | -0.17853 | -0.07782 | 0.050354 | 60.5118 | 60.8917 | 122.3236 | 122.4106 | -0.1236 | 122.4472 | 60.6949 | -0.17853 | 122.4106 | -0.1236 | 60.6949 | 122.3236 | 122.4472 | -122.699 | -122.7036
241.0625 | 122.8683 | -60.6857 | 61.8073 | 0.15259 | 0.013751 | 0.016735 | 0.0025807 | 0.067001 | -0.0018713 | 0.067244 | -60.7544 | 61.7294 | -60.8597 | -60.8368 | 61.6196 | 0 | -0.3891 | 0.032043 | 61.6791 | -60.8826 | -0.17395 | -0.07782 | -0.068665 | -0.15106 | -0.18768 | -0.19684 | -0.12817 | 0.10528 | 60.2966 | 60.7178 | 122.3053 | 122.4152 | -0.068665 | 122.3648 | 60.6857 | -0.19684 | 122.4152 | -0.068665 | 60.6857 | 122.3053 | 122.3648 | -122.6669 | -122.6898
242.0625 | 122.8958 | -60.7086 | 61.7935 | 0.22125 | 0.012256 | 0.015667 | 0.0030079 | 0.065933 | -0.00037588 | 0.066603 | -60.7452 | 61.7386 | -60.8459 | -60.8322 | 61.6241 | -0.009155 | -0.37994 | 0.018311 | 61.6837 | -60.9192 | -0.13733 | -0.054932 | -0.036621 | -0.1236 | -0.16937 | -0.21057 | -0.10986 | 0.10071 | 60.3287 | 60.7269 | 122.3328 | 122.4472 | -0.036621 | 122.3923 | 60.6995 | -0.21057 | 122.4472 | -0.036621 | 60.6995 | 122.3328 | 122.3923 | -122.6395 | -122.7127
243.0625 | 122.8638 | -60.704 | 61.821 | 0.14496 | 0.014392 | 0.019512 | 0.0017261 | 0.066787 | 0.0015467 | 0.069808 | -60.7864 | 61.7615 | -60.8551 | -60.8459 | 61.6196 | 0 | -0.37079 | 0.013733 | 61.6928 | -60.91 | -0.15106 | -0.059509 | -0.082397 | -0.14191 | -0.20142 | -0.20599 | -0.12817 | 0.068665 | 60.3333 | 60.7178 | 122.3236 | 122.4655 | -0.082397 | 122.3969 | 60.704 | -0.20599 | 122.4655 | -0.082397 | 60.704 | 122.3236 | 122.3969 | -122.6761 | -122.731
244.0625 | 122.8592 | -60.7086 | 61.7935 | 0.17548 | 0.012897 | 0.016308 | 0.0025807 | 0.067001 | -0.00037588 | 0.068099 | -60.791 | 61.7752 | -60.8826 | -60.8734 | 61.6104 | -0.027466 | -0.3479 | -0.004578 | 61.7249 | -60.9238 | -0.17395 | -0.01831 | -0.082398 | -0.16479 | -0.1831 | -0.21515 | -0.068664 | 0.091552 | 60.3607 | 60.704 | 122.319 | 122.4838 | -0.082398 | 122.4335 | 60.6812 | -0.21515 | 122.4838 | -0.082398 | 60.6812 | 122.319 | 122.4335 | -122.6761 | -122.7173
245.0625 | 122.8455 | -60.6628 | 61.853 | 0.022888 | 0.010547 | 0.018231 | -0.0029735 | 0.063796 | 0.0011193 | 0.067244 | -60.8276 | 61.7203 | -60.8826 | -60.8826 | 61.6104 | -0.022888 | -0.24719 | 0.013733 | 61.7386 | -60.878 | -0.21973 | -0.13275 | -0.1648 | -0.21973 | -0.24261 | -0.21515 | -0.11444 | 0.054931 | 60.4156 | 60.6766 | 122.2733 | 122.3831 | -0.1648 | 122.4014 | 60.64 | -0.21515 | 122.3831 | -0.1648 | 60.64 | 122.2733 | 122.4014 | -122.7356 | -122.731
246.0625 | 122.731 | -60.7224 | 61.853 | 0.10681 | 0.012469 | 0.020794 | 0.0057849 | 0.067855 | -0.0010169 | 0.067244 | -60.8276 | 61.8027 | -60.8871 | -60.7452 | 61.7294 | 0 | -0.25635 | -0.036621 | 61.7661 | -60.9421 | -0.16479 | -0.050354 | -0.10529 | -0.022888 | -0.1236 | -0.21973 | -0.086975 | 0.059509 | 60.466 | 60.6857 | 122.4518 | 122.525 | -0.10529 | 122.4884 | 60.7224 | -0.21973 | 122.525 | -0.10529 | 60.7224 | 122.4518 | 122.4884 | -122.7402 | -122.7951
247.0625 | 122.7951 | -60.7086 | 61.821 | 0.083923 | 0.016314 | 0.021862 | 0.0047169 | 0.065719 | -0.00016228 | 0.068312 | -60.8276 | 61.7935 | -60.8871 | -60.9146 | 61.5463 | -0.09613 | -0.25635 | -0.073242 | 61.702 | -60.965 | -0.17853 | -0.027466 | -0.11902 | -0.20599 | -0.27466 | -0.25635 | -0.11902 | 0.059509 | 60.4523 | 60.6354 | 122.2549 | 122.5021 | -0.11902 | 122.4106 | 60.6125 | -0.25635 | 122.5021 | -0.11902 | 60.6125 | 122.2549 | 122.4106 | -122.7081 | -122.7859
248.0625 | 122.8729 | -60.7086 | 61.8347 | 0.16022 | 0.013751 | 0.013104 | 0.0023669 | 0.066574 | 0.00090572 | 0.068526 | -60.7956 | 61.7661 | -60.8871 | -60.8597 | 61.6058 | -0.022888 | -0.3479 | -0.027466 | 61.7386 | -60.9238 | -0.17853 | -0.068665 | -0.086975 | -0.15106 | -0.22888 | -0.21515 | -0.096131 | 0.091553 | 60.3607 | 60.6812 | 122.3145 | 122.4747 | -0.086975 | 122.4472 | 60.6857 | -0.21515 | 122.4747 | -0.086975 | 60.6857 | 122.3145 | 122.4472 | -122.7219 | -122.7585
249.0625 | 122.8455 | -60.7086 | 61.821 | 0.1297 | 0.014178 | 0.015667 | 0.0051441 | 0.067214 | 0.00069212 | 0.070449 | -60.8139 | 61.7889 | -60.91 | -60.9146 | 61.5738 | -0.054932 | -0.31586 | -0.041199 | 61.7249 | -60.9375 | -0.20142 | -0.032044 | -0.10529 | -0.20599 | -0.24719 | -0.22888 | -0.09613 | 0.09613 | 60.3928 | 60.6674 | 122.2824 | 122.4976 | -0.10529 | 122.4335 | 60.6537 | -0.22888 | 122.4976 | -0.10529 | 60.6537 | 122.2824 | 122.4335 | -122.731 | -122.7585
250.0625 | 122.818 | -60.704 | 61.8073 | -0.022888 | 0.01311 | 0.014172 | -0.0021191 | 0.064651 | 0.0013329 | 0.06874 | -60.8185 | 61.7203 | -60.8734 | -60.8963 | 61.5967 | -0.009155 | -0.26093 | 0.018311 | 61.734 | -60.91 | -0.16937 | -0.086975 | -0.11444 | -0.19226 | -0.21057 | -0.20599 | -0.073242 | 0.054932 | 60.4431 | 60.7224 | 122.3007 | 122.4243 | -0.11444 | 122.4381 | 60.6949 | -0.20599 | 122.4243 | -0.11444 | 60.6949 | 122.3007 | 122.4381 | -122.6807 | -122.7173
251.0625 | 122.7905 | -60.7086 | 61.8256 | 0.045776 | 0.010547 | 0.014813 | 0.0045033 | 0.067214 | 0.0013329 | 0.068953 | -60.8185 | 61.8118 | -60.878 | -60.9146 | 61.5326 | -0.086975 | -0.25635 | -0.082397 | 61.7249 | -60.9467 | -0.16937 | -0.013733 | -0.10986 | -0.20599 | -0.29297 | -0.23804 | -0.10071 | 0.05951 | 60.4523 | 60.6262 | 122.2412 | 122.5204 | -0.10986 | 122.4335 | 60.6216 | -0.23804 | 122.5204 | -0.10986 | 60.6216 | 122.2412 | 122.4335 | -122.7036 | -122.7722
252.0625 | 122.7585 | -60.7178 | 61.8393 | 0.030517 | 0.015246 | 0.020367 | 0.0047169 | 0.069992 | -0.00080328 | 0.06874 | -60.8597 | 61.8256 | -60.8826 | -60.9375 | 61.5097 | -0.11902 | -0.19226 | -0.11444 | 61.7798 | -60.9512 | -0.16479 | -0.013732 | -0.14191 | -0.21973 | -0.32959 | -0.23346 | -0.059509 | 0.022888 | 60.5255 | 60.6033 | 122.2275 | 122.5433 | -0.14191 | 122.4976 | 60.5988 | -0.23346 | 122.5433 | -0.14191 | 60.5988 | 122.2275 | 122.4976 | -122.7219 | -122.7905
253.0625 | 122.7493 | -60.7224 | 61.8576 | 0.022888 | 0.013537 | 0.016949 | 0.0057849 | 0.068923 | -0.00058968 | 0.070021 | -60.8231 | 61.8439 | -60.8826 | -60.9695 | 61.5051 | -0.11444 | -0.17853 | -0.09613 | 61.7523 | -60.9329 | -0.16022 | -0.013733 | -0.10071 | -0.24719 | -0.35248 | -0.21057 | -0.10529 | 0.059509 | 60.5438 | 60.6262 | 122.2275 | 122.5662 | -0.10071 | 122.4747 | 60.6079 | -0.21057 | 122.5662 | -0.10071 | 60.6079 | 122.2275 | 122.4747 | -122.7402 | -122.7905
254.0625 | 122.7722 | -60.7361 | 61.8622 | 0.10681 | 0.014605 | 0.02058 | 0.00065787 | 0.069564 | -0.0010169 | 0.069167 | -60.9238 | 61.7889 | -60.9421 | -60.91 | 61.5601 | -0.10529 | -0.17853 | -0.073242 | 61.7706 | -60.9558 | -0.20599 | -0.073243 | -0.18768 | -0.17395 | -0.30212 | -0.21973 | -0.091553 | 0.018311 | 60.5576 | 60.6628 | 122.2961 | 122.525 | -0.18768 | 122.5067 | 60.6308 | -0.21973 | 122.525 | -0.18768 | 60.6308 | 122.2961 | 122.5067 | -122.8043 | -122.818
255.0625 | 122.8683 | -60.6903 | 61.7935 | 0.28992 | 0.012897 | 0.013958 | -0.00041013 | 0.069778 | 0.00090572 | 0.071089 | -60.7498 | 61.7386 | -60.8734 | -60.8276 | 61.6425 | 0.013733 | -0.36163 | 0.009155 | 61.7432 | -60.9055 | -0.1831 | -0.054932 | -0.059509 | -0.13733 | -0.15106 | -0.21515 | -0.050354 | 0.1236 | 60.3287 | 60.6995 | 122.3328 | 122.4289 | -0.059509 | 122.4335 | 60.704 | -0.21515 | 122.4289 | -0.059509 | 60.704 | 122.3328 | 122.4335 | -122.6669 | -122.699
256.0625 | 122.7722 | -60.7132 | 61.8301 | 0.10681 | 0.013324 | 0.02058 | 0.0030079 | 0.069564 | 0.00026492 | 0.066817 | -60.8368 | 61.821 | -60.8871 | -60.9375 | 61.528 | -0.091553 | -0.25177 | -0.086975 | 61.7432 | -60.9604 | -0.17395 | -0.009155 | -0.1236 | -0.2243 | -0.30212 | -0.24719 | -0.086975 | 0.050354 | 60.4614 | 60.6262 | 122.2412 | 122.5342 | -0.1236 | 122.4564 | 60.6216 | -0.24719 | 122.5342 | -0.1236 | 60.6216 | 122.2412 | 122.4564 | -122.7173 | -122.7905
257.0625 | 122.7905 | -60.7224 | 61.8256 | 0.022888 | 0.013965 | 0.01524 | 0.00023067 | 0.070846 | -0.00016228 | 0.070021 | -60.8505 | 61.8118 | -60.8963 | -60.9238 | 61.5234 | -0.09613 | -0.2243 | -0.091553 | 61.7615 | -60.9604 | -0.17395 | -0.013733 | -0.12817 | -0.20142 | -0.30212 | -0.23804 | -0.064087 | 0.045776 | 60.498 | 60.6308 | 122.2458 | 122.5342 | -0.12817 | 122.4838 | 60.6262 | -0.23804 | 122.5342 | -0.12817 | 60.6262 | 122.2458 | 122.4838 | -122.7219 | -122.7859
258.0625 | 122.7722 | -60.7315 | 61.8439 | -0.56458 | 0.017596 | 0.017803 | 0.0040759 | 0.067001 | -0.00016228 | 0.070662 | -60.9009 | 61.8256 | -60.8963 | -60.9558 | 61.5189 | -0.10529 | -0.20142 | -0.10071 | 61.7798 | -60.965 | -0.16479 | -0.01831 | -0.16937 | -0.2243 | -0.32501 | -0.23346 | -0.064087 | -0.004578 | 60.5301 | 60.6308 | 122.2504 | 122.5571 | -0.16937 | 122.5113 | 60.6262 | -0.23346 | 122.5571 | -0.16937 | 60.6262 | 122.2504 | 122.5113 | -122.7402 | -122.8088
259.0625 | 122.7539 | -60.7498 | 61.853 | 0.038147 | 0.01546 | 0.018231 | 0.0040759 | 0.068283 | -0.00058968 | 0.06874 | -60.8231 | 61.821 | -60.9146 | -60.9695 | 61.5051 | -0.1236 | -0.15106 | -0.10529 | 61.7844 | -60.9787 | -0.16479 | -0.032043 | -0.073242 | -0.21973 | -0.3479 | -0.22888 | -0.068664 | 0.091553 | 60.5988 | 60.6445 | 122.2549 | 122.5708 | -0.073242 | 122.5342 | 60.6262 | -0.22888 | 122.5708 | -0.073242 | 60.6262 | 122.2549 | 122.5342 | -122.7676 | -122.8317
260.0625 | 122.8867 | -60.672 | 61.821 | 0.20599 | 0.013751 | 0.019726 | 0.00065787 | 0.069137 | -0.00016228 | 0.071089 | -60.7544 | 61.7477 | -60.8505 | -60.8505 | 61.615 | -0.004578 | -0.37537 | 0.018311 | 61.7249 | -60.9009 | -0.17853 | -0.073242 | -0.082398 | -0.17853 | -0.20599 | -0.22888 | -0.09613 | 0.09613 | 60.2966 | 60.6903 | 122.287 | 122.4197 | -0.082398 | 122.3969 | 60.6674 | -0.22888 | 122.4197 | -0.082398 | 60.6674 | 122.287 | 122.3969 | -122.6715 | -122.7219
261.0625 | 122.7997 | -60.7498 | 61.8622 | 0.099182 | 0.012042 | 0.016735 | 0.0034351 | 0.06871 | -0.00016228 | 0.067031 | -60.8276 | 61.8256 | -60.8963 | -60.9604 | 61.5051 | -0.11902 | -0.19684 | -0.20142 | 61.7661 | -60.9924 | -0.14648 | -0.036621 | -0.07782 | -0.21057 | -0.35706 | -0.24262 | -0.096131 | 0.068664 | 60.553 | 60.5484 | 122.2549 | 122.5754 | -0.07782 | 122.5159 | 60.6308 | -0.24262 | 122.5754 | -0.07782 | 60.6308 | 122.2549 | 122.5159 | -122.7585 | -122.8546
262.0625 | 122.7814 | -60.7452 | 61.8256 | 0.19836 | 0.014392 | 0.01759 | 0.00087167 | 0.068923 | 5.1318e-05 | 0.069167 | -60.8185 | 61.7981 | -60.9055 | -60.9238 | 61.5372 | -0.10071 | -0.23346 | -0.086975 | 61.7706 | -60.9375 | -0.16022 | -0.027466 | -0.073242 | -0.17853 | -0.28839 | -0.19226 | -0.054932 | 0.086976 | 60.5118 | 60.6583 | 122.2824 | 122.5433 | -0.073242 | 122.5159 | 60.6445 | -0.19226 | 122.5433 | -0.073242 | 60.6445 | 122.2824 | 122.5159 | -122.731 | -122.7631
263.0625 | 122.7722 | -60.7269 | 61.8256 | -0.44251 | 0.01546 | 0.017376 | 0.0023669 | 0.069992 | -0.0014441 | 0.070662 | -60.8368 | 61.8393 | -60.8734 | -60.9421 | 61.5234 | -0.10071 | -0.21057 | -0.073242 | 61.8118 | -60.9741 | -0.14648 | 0.013732 | -0.10986 | -0.21515 | -0.30212 | -0.24719 | -0.013733 | 0.036621 | 60.5164 | 60.6537 | 122.2504 | 122.5662 | -0.10986 | 122.5388 | 60.6262 | -0.24719 | 122.5662 | -0.10986 | 60.6262 | 122.2504 | 122.5388 | -122.699 | -122.7997
264.0625 | 122.7631 | -60.7269 | 61.8439 | 0.64087 | 0.015246 | 0.016522 | 0.0045033 | 0.068923 | -0.0014441 | 0.06938 | -60.6125 | 61.8118 | -60.8643 | -60.9329 | 61.5097 | -0.10986 | -0.21973 | -0.10986 | 61.8073 | -60.9604 | -0.13733 | -0.032043 | 0.11444 | -0.20599 | -0.33417 | -0.23346 | -0.036621 | 0.25177 | 60.5072 | 60.6171 | 122.2366 | 122.5388 | 0.11444 | 122.5342 | 60.6171 | -0.23346 | 122.5388 | 0.11444 | 60.6171 | 122.2366 | 122.5342 | -122.7081 | -122.8043
265.0625 | 122.8546 | -60.6949 | 61.8027 | 0.27466 | 0.010119 | 0.016094 | -0.0016919 | 0.065933 | -0.0012305 | 0.070235 | -60.7636 | 61.7157 | -60.8459 | -60.8597 | 61.615 | -0.018311 | -0.37994 | 0.018311 | 61.7477 | -60.8963 | -0.15106 | -0.086975 | -0.068665 | -0.16479 | -0.18768 | -0.20142 | -0.054931 | 0.082397 | 60.3149 | 60.7132 | 122.3099 | 122.4106 | -0.068665 | 122.4426 | 60.6766 | -0.20142 | 122.4106 | -0.068665 | 60.6766 | 122.3099 | 122.4426 | -122.6486 | -122.699
266.0625 | 122.7402 | -60.7086 | 61.8576 | 0.015259 | 0.015033 | 0.018017 | 0.0062121 | 0.06871 | -0.00080328 | 0.068526 | -60.8231 | 61.821 | -60.8826 | -60.9604 | 61.5005 | -0.10986 | -0.15106 | -0.11902 | 61.7844 | -60.9558 | -0.17395 | -0.036621 | -0.11444 | -0.25177 | -0.35706 | -0.24719 | -0.073242 | 0.059509 | 60.5576 | 60.5896 | 122.2092 | 122.5296 | -0.11444 | 122.493 | 60.5988 | -0.24719 | 122.5296 | -0.11444 | 60.5988 | 122.2092 | 122.493 | -122.7402 | -122.8134
267.0625 | 122.7402 | -60.7178 | 61.8622 | -0.015259 | 0.014392 | 0.01759 | 0.0038623 | 0.068496 | -0.0020849 | 0.068526 | -60.8047 | 61.8256 | -60.8963 | -60.965 | 61.5005 | -0.11902 | -0.16022 | -0.11444 | 61.7935 | -60.9604 | -0.17853 | -0.036621 | -0.086976 | -0.24719 | -0.36163 | -0.24262 | -0.068665 | 0.091552 | 60.5576 | 60.6033 | 122.2183 | 122.5433 | -0.086976 | 122.5113 | 60.5988 | -0.24262 | 122.5433 | -0.086976 | 60.5988 | 122.2183 | 122.5113 | -122.7585 | -122.8226
268.0625 | 122.7859 | -60.7452 | 61.8073 | 0.091553 | 0.013751 | 0.016949 | 0.0049305 | 0.070846 | 0.00026492 | 0.070021 | -60.8322 | 61.8118 | -60.8963 | -60.9695 | 61.496 | -0.12817 | -0.17853 | -0.12817 | 61.7889 | -60.9604 | -0.15106 | 0.004578 | -0.086975 | -0.2243 | -0.31128 | -0.21515 | -0.018311 | 0.064087 | 60.5667 | 60.6171 | 122.2412 | 122.5571 | -0.086975 | 122.5342 | 60.6171 | -0.21515 | 122.5571 | -0.086975 | 60.6171 | 122.2412 | 122.5342 | -122.7036 | -122.7676
269.0625 | 122.7539 | -60.7224 | 61.853 | -0.099182 | 0.012683 | 0.021435 | 0.0025807 | 0.067855 | 0.0026147 | 0.070449 | -60.8505 | 61.8439 | -60.8871 | -60.9329 | 61.5417 | -0.10986 | -0.21515 | -0.091553 | 61.7844 | -60.9238 | -0.16479 | -0.009155 | -0.12817 | -0.21057 | -0.31128 | -0.20142 | -0.068664 | 0.036621 | 60.5072 | 60.6308 | 122.2641 | 122.5662 | -0.12817 | 122.5067 | 60.6125 | -0.20142 | 122.5662 | -0.12817 | 60.6125 | 122.2641 | 122.5067 | -122.7402 | -122.7768
270.0625 | 122.8363 | -60.6812 | 61.8164 | -0.068665 | 0.011401 | 0.01759 | -0.0046825 | 0.067642 | 0.00026492 | 0.070235 | -60.8139 | 61.734 | -60.878 | -60.9009 | 61.6104 | -0.036621 | -0.26093 | 0.11902 | 61.7615 | -60.9009 | -0.19684 | -0.082397 | -0.13275 | -0.21973 | -0.20599 | -0.21973 | -0.054931 | 0.064087 | 60.4202 | 60.8002 | 122.2916 | 122.4152 | -0.13275 | 122.4426 | 60.6445 | -0.21973 | 122.4152 | -0.13275 | 60.6445 | 122.2916 | 122.4426 | -122.6944 | -122.7173
271.0625 | 122.7539 | -60.7269 | 61.8484 | 0.076294 | 0.015033 | 0.018871 | 0.0010853 | 0.066574 | 0.00069212 | 0.067031 | -60.6812 | 61.8164 | -60.9192 | -60.9695 | 61.5555 | -0.068665 | -0.20142 | -0.09613 | 61.7889 | -60.965 | -0.19226 | -0.032044 | 0.045777 | -0.24261 | -0.29297 | -0.23804 | -0.05951 | 0.23804 | 60.5255 | 60.6308 | 122.2824 | 122.5433 | 0.045777 | 122.5159 | 60.6583 | -0.23804 | 122.5433 | 0.045777 | 60.6583 | 122.2824 | 122.5159 | -122.7676 | -122.8134
272.0625 | 122.7905 | -60.7132 | 61.8164 | 0.11444 | 0.014178 | 0.02058 | 0.0021533 | 0.068496 | 0.00047852 | 0.068953 | -60.8322 | 61.7935 | -60.8826 | -60.9375 | 61.5463 | -0.10071 | -0.2655 | -0.091553 | 61.7569 | -60.9558 | -0.16937 | -0.022888 | -0.11902 | -0.2243 | -0.27008 | -0.24261 | -0.059509 | 0.050354 | 60.4477 | 60.6216 | 122.2595 | 122.5067 | -0.11902 | 122.4701 | 60.6125 | -0.24261 | 122.5067 | -0.11902 | 60.6125 | 122.2595 | 122.4701 | -122.699 | -122.7722
273.0625 | 122.7402 | -60.7178 | 61.8622 | -0.015259 | 0.014819 | 0.01759 | 0.0047169 | 0.067855 | 0.0013329 | 0.070449 | -60.7956 | 61.8164 | -60.878 | -60.9421 | 61.528 | -0.10529 | -0.17853 | -0.086975 | 61.821 | -60.9467 | -0.16022 | -0.045777 | -0.07782 | -0.22431 | -0.33417 | -0.22888 | -0.041199 | 0.082398 | 60.5392 | 60.6308 | 122.2458 | 122.5342 | -0.07782 | 122.5388 | 60.6125 | -0.22888 | 122.5342 | -0.07782 | 60.6125 | 122.2458 | 122.5388 | -122.7402 | -122.8088
274.0625 | 122.7585 | -60.7224 | 61.8713 | -0.061035 | 0.015033 | 0.020367 | 0.0047169 | 0.068069 | -0.0012305 | 0.065962 | -60.8002 | 61.8256 | -60.8597 | -60.9283 | 61.5234 | -0.10071 | -0.18768 | -0.07782 | 61.8027 | -60.9604 | -0.13733 | -0.045776 | -0.07782 | -0.20599 | -0.3479 | -0.23804 | -0.068665 | 0.059509 | 60.5347 | 60.6445 | 122.2458 | 122.5479 | -0.07782 | 122.525 | 60.6216 | -0.23804 | 122.5479 | -0.07782 | 60.6216 | 122.2458 | 122.525 | -122.731 | -122.8317
275.0625 | 122.8912 | -60.6857 | 61.8164 | 0.16785 | 0.014605 | 0.01759 | 0.0023669 | 0.069992 | -0.00016228 | 0.06938 | -60.7361 | 61.7569 | -60.8734 | -60.8414 | 61.6241 | -0.032043 | -0.40741 | -0.004578 | 61.7065 | -60.9467 | -0.18768 | -0.059509 | -0.050354 | -0.15564 | -0.19226 | -0.26093 | -0.10986 | 0.13733 | 60.2783 | 60.6812 | 122.3099 | 122.4426 | -0.050354 | 122.3923 | 60.6537 | -0.26093 | 122.4426 | -0.050354 | 60.6537 | 122.3099 | 122.3923 | -122.6898 | -122.7631
276.0625 | 122.7493 | -60.7407 | 61.8576 | 0.10681 | 0.014819 | 0.013531 | 0.0025807 | 0.070419 | -0.0012305 | 0.06938 | -60.8231 | 61.7981 | -60.8826 | -60.7636 | 61.6562 | -0.10529 | -0.21057 | -0.050354 | 61.8027 | -60.9695 | -0.14191 | -0.059509 | -0.082397 | -0.022888 | -0.20142 | -0.22888 | -0.054932 | 0.059509 | 60.5301 | 60.6903 | 122.3969 | 122.5388 | -0.082397 | 122.5433 | 60.6354 | -0.22888 | 122.5388 | -0.082397 | 60.6354 | 122.3969 | 122.5433 | -122.7402 | -122.8271
277.0625 | 122.7081 | -60.7636 | 61.8347 | 0.11444 | 0.015246 | 0.016522 | 0.0023669 | 0.070205 | 0.00026492 | 0.069808 | -60.8276 | 61.8347 | -60.8963 | -60.965 | 61.5097 | -0.12817 | -0.2243 | -0.13275 | 61.7935 | -60.9833 | -0.13275 | 0 | -0.064087 | -0.20142 | -0.32501 | -0.21973 | -0.041199 | 0.068664 | 60.5392 | 60.6308 | 122.2733 | 122.5983 | -0.064087 | 122.5571 | 60.6354 | -0.21973 | 122.5983 | -0.064087 | 60.6354 | 122.2733 | 122.5571 | -122.731 | -122.818
278.0625 | 122.7448 | -60.7315 | 61.8347 | 0.099182 | 0.012256 | 0.016308 | 0.0036487 | 0.067855 | 0.00047852 | 0.069167 | -60.8643 | 61.821 | -60.8826 | -60.9512 | 61.4914 | -0.14191 | -0.19684 | -0.13733 | 61.7798 | -60.9558 | -0.15106 | -0.013733 | -0.13275 | -0.21973 | -0.34332 | -0.2243 | -0.054932 | 0.01831 | 60.5347 | 60.5942 | 122.2229 | 122.5525 | -0.13275 | 122.5113 | 60.5896 | -0.2243 | 122.5525 | -0.13275 | 60.5896 | 122.2229 | 122.5113 | -122.7173 | -122.7905
279.0625 | 122.7356 | -60.7361 | 61.8484 | 0.038147 | 0.01546 | 0.018658 | 0.0021533 | 0.068923 | -0.00037588 | 0.069167 | -60.8414 | 61.821 | -60.8963 | -60.9833 | 61.496 | -0.13275 | -0.19684 | -0.13733 | 61.8118 | -60.9604 | -0.16022 | -0.027466 | -0.10529 | -0.24719 | -0.35248 | -0.2243 | -0.036621 | 0.054931 | 60.5392 | 60.5988 | 122.2321 | 122.5571 | -0.10529 | 122.5479 | 60.6033 | -0.2243 | 122.5571 | -0.10529 | 60.6033 | 122.2321 | 122.5479 | -122.7448 | -122.8088
280.0625 | 122.8683 | -60.6995 | 61.7844 | 0.076294 | 0.012042 | 0.018444 | 0.00065787 | 0.069992 | -0.0022987 | 0.069594 | -60.7452 | 61.7386 | -60.8963 | -60.8459 | 61.6196 | -0.036621 | -0.39825 | -0.013733 | 61.7203 | -60.91 | -0.19684 | -0.045777 | -0.045776 | -0.14648 | -0.16479 | -0.21057 | -0.064087 | 0.15106 | 60.3012 | 60.6857 | 122.319 | 122.438 | -0.045776 | 122.4197 | 60.6628 | -0.21057 | 122.438 | -0.045776 | 60.6628 | 122.319 | 122.4197 | -122.6807 | -122.6944
281.0625 | 122.7036 | -60.7544 | 61.8439 | 0.022888 | 0.014178 | 0.016094 | 0.0057849 | 0.069351 | -0.0010169 | 0.06874 | -60.8093 | 61.8484 | -60.8551 | -60.9512 | 61.5005 | -0.14191 | -0.16937 | -0.10986 | 61.7798 | -60.9741 | -0.10071 | 0.004578 | -0.054931 | -0.19684 | -0.34332 | -0.21973 | -0.064087 | 0.045777 | 60.585 | 60.6445 | 122.2549 | 122.6028 | -0.054931 | 122.5342 | 60.6125 | -0.21973 | 122.6028 | -0.054931 | 60.6125 | 122.2549 | 122.5342 | -122.699 | -122.818
282.0625 | 122.6761 | -60.7315 | 61.7706 | 0.091553 | 0.01546 | 0.02058 | 0.0017261 | 0.067855 | -0.00058968 | 0.071089 | -60.8322 | 61.821 | -60.8871 | -60.9695 | 61.496 | -0.15106 | -0.21057 | -0.13733 | 61.821 | -60.9695 | -0.15564 | 0.050354 | -0.10071 | -0.23804 | -0.27466 | -0.23804 | 0.050354 | 0.054932 | 60.5209 | 60.5942 | 122.2275 | 122.5525 | -0.10071 | 122.5525 | 60.5804 | -0.23804 | 122.5525 | -0.10071 | 60.5804 | 122.2275 | 122.5525 | -122.6578 | -122.7402
283.0625 | 122.7448 | -60.7361 | 61.8622 | 0.068664 | 0.01546 | 0.013958 | 0.0036487 | 0.06871 | -0.0016577 | 0.069594 | -60.8459 | 61.8301 | -60.8917 | -60.9695 | 61.4777 | -0.13733 | -0.2243 | -0.13733 | 61.8256 | -60.9695 | -0.15564 | -0.032044 | -0.10986 | -0.23346 | -0.38452 | -0.23346 | -0.036621 | 0.045777 | 60.5118 | 60.5988 | 122.2137 | 122.5662 | -0.10986 | 122.5616 | 60.5988 | -0.23346 | 122.5662 | -0.10986 | 60.5988 | 122.2137 | 122.5616 | -122.7539 | -122.8317
284.0625 | 122.731 | -60.7544 | 61.8576 | -6e-08 | 0.014605 | 0.017376 | 0.0036487 | 0.06871 | -0.00037588 | 0.068099 | -60.8459 | 61.8484 | -60.8826 | -60.9879 | 61.4914 | -0.14648 | -0.17853 | -0.15106 | 61.8164 | -60.9741 | -0.12817 | -0.009155 | -0.091552 | -0.23346 | -0.36621 | -0.21973 | -0.041199 | 0.036621 | 60.5759 | 60.6033 | 122.2458 | 122.6028 | -0.091552 | 122.5708 | 60.6079 | -0.21973 | 122.6028 | -0.091552 | 60.6079 | 122.2458 | 122.5708 | -122.7402 | -122.8317
285.0781 | 122.7493 | -60.704 | 61.8805 | -0.38147 | 0.011401 | 0.016308 | -0.0023327 | 0.06871 | 5.1318e-05 | 0.068099 | -60.7864 | 61.8118 | -60.8643 | -60.8963 | 61.6058 | -0.013733 | -0.10529 | 0.004578 | 61.8301 | -60.9238 | -0.16022 | -0.068664 | -0.082397 | -0.19226 | -0.27466 | -0.21973 | -0.050354 | 0.07782 | 60.5988 | 60.7086 | 122.3099 | 122.5159 | -0.082397 | 122.5342 | 60.6903 | -0.21973 | 122.5159 | -0.082397 | 60.6903 | 122.3099 | 122.5342 | -122.7448 | -122.8043
286.0625 | 122.7264 | -60.7361 | 61.8713 | -0.0076296 | 0.013324 | 0.018658 | 0.0042895 | 0.069564 | -0.0022987 | 0.068526 | -60.8093 | 61.8439 | -60.878 | -60.9421 | 61.5143 | -0.11902 | -0.18768 | -0.10986 | 61.7935 | -60.9787 | -0.14191 | -0.027466 | -0.073242 | -0.20599 | -0.35706 | -0.24262 | -0.07782 | 0.068665 | 60.5484 | 60.6262 | 122.2504 | 122.58 | -0.073242 | 122.5296 | 60.6171 | -0.24262 | 122.58 | -0.073242 | 60.6171 | 122.2504 | 122.5296 | -122.7493 | -122.85
287.0625 | 122.7905 | -60.7086 | 61.8805 | -0.076294 | 0.013324 | 0.020794 | 0.0053577 | 0.067214 | 0.00026492 | 0.068526 | -60.7544 | 61.8256 | -60.8826 | -60.8826 | 61.5875 | -0.059509 | -0.20142 | -0.004578 | 61.8164 | -60.9421 | -0.17395 | -0.054931 | -0.045777 | -0.17395 | -0.29297 | -0.23346 | -0.064087 | 0.12817 | 60.5072 | 60.704 | 122.2961 | 122.5342 | -0.045777 | 122.525 | 60.6491 | -0.23346 | 122.5342 | -0.045777 | 60.6491 | 122.2961 | 122.525 | -122.7631 | -122.8226
288.0625 | 122.7722 | -60.7224 | 61.853 | -0.10681 | 0.016101 | 0.019726 | 0.0051441 | 0.069137 | -0.0016577 | 0.067671 | -60.7773 | 61.8164 | -60.878 | -60.9146 | 61.5646 | -0.082397 | -0.19684 | -0.068665 | 61.7752 | -60.9604 | -0.15564 | -0.036621 | -0.054932 | -0.19226 | -0.28839 | -0.23804 | -0.077819 | 0.10071 | 60.5255 | 60.6537 | 122.287 | 122.5388 | -0.054932 | 122.4976 | 60.64 | -0.23804 | 122.5388 | -0.054932 | 60.64 | 122.287 | 122.4976 | -122.731 | -122.8134
289.0625 | 122.7448 | -60.7132 | 61.8484 | -0.038147 | 0.01311 | 0.018444 | 0.0032215 | 0.068069 | -0.00058968 | 0.06874 | -60.791 | 61.8484 | -60.8871 | -60.9467 | 61.5189 | -0.13733 | -0.19226 | -0.1236 | 61.8164 | -60.9421 | -0.17395 | 0 | -0.07782 | -0.23346 | -0.32959 | -0.22888 | -0.032044 | 0.09613 | 60.5209 | 60.5896 | 122.2321 | 122.5616 | -0.07782 | 122.5296 | 60.5759 | -0.22888 | 122.5616 | -0.07782 | 60.5759 | 122.2321 | 122.5296 | -122.7356 | -122.7905
290.0781 | 122.905 | -60.6674 | 61.8347 | -0.18311 | 0.0090511 | 0.016094 | -0.0055371 | 0.067855 | -0.0012305 | 0.069167 | -60.759 | 61.7386 | -60.8505 | -60.8002 | 61.6562 | 0.045776 | -0.30212 | 0.11444 | 61.7661 | -60.8551 | -0.18311 | -0.096131 | -0.091553 | -0.13275 | -0.17853 | -0.18768 | -0.068665 | 0.091553 | 60.3653 | 60.7819 | 122.3236 | 122.406 | -0.091553 | 122.4335 | 60.7132 | -0.18768 | 122.406 | -0.091553 | 60.7132 | 122.3236 | 122.4335 | -122.6852 | -122.6898
291.0625 | 122.7859 | -60.6995 | 61.8439 | -0.091553 | 0.01546 | 0.014599 | 0.0038623 | 0.06636 | -0.0012305 | 0.067885 | -60.7773 | 61.8393 | -60.8734 | -60.9055 | 61.5646 | -0.082397 | -0.21057 | -0.064087 | 61.7798 | -60.9695 | -0.17395 | -0.004578 | -0.07782 | -0.20599 | -0.27924 | -0.27008 | -0.064087 | 0.09613 | 60.4889 | 60.6354 | 122.2641 | 122.5388 | -0.07782 | 122.4792 | 60.6171 | -0.27008 | 122.5388 | -0.07782 | 60.6171 | 122.2641 | 122.4792 | -122.7173 | -122.8134
292.0625 | 122.8043 | -60.6995 | 61.8713 | -0.32043 | 0.012683 | 0.015026 | 0.0045033 | 0.069564 | -0.00016228 | 0.068312 | -60.759 | 61.8301 | -60.8505 | -60.8871 | 61.5921 | -0.091553 | -0.21973 | -0.045776 | 61.821 | -60.9375 | -0.15106 | -0.041199 | -0.059509 | -0.18768 | -0.27924 | -0.23804 | -0.050354 | 0.091553 | 60.4797 | 60.6537 | 122.2916 | 122.5296 | -0.059509 | 122.5204 | 60.6079 | -0.23804 | 122.5296 | -0.059509 | 60.6079 | 122.2916 | 122.5204 | -122.7219 | -122.8088
293.0625 | 122.7951 | -60.704 | 61.8713 | -0.10681 | 0.014178 | 0.013104 | 0.0038623 | 0.068283 | 5.1318e-05 | 0.070449 | -60.7498 | 61.8484 | -60.8597 | -60.9467 | 61.4502 | -0.16479 | -0.14191 | -0.009155 | 61.8073 | -60.9283 | -0.15564 | -0.022888 | -0.045776 | -0.24261 | -0.42114 | -0.2243 | -0.064087 | 0.10986 | 60.5621 | 60.6949 | 122.1542 | 122.5525 | -0.045776 | 122.5113 | 60.5392 | -0.2243 | 122.5525 | -0.045776 | 60.5392 | 122.1542 | 122.5113 | -122.731 | -122.7997
294.0625 | 122.7768 | -60.6903 | 61.8988 | -0.30518 | 0.015033 | 0.018658 | 0.0012989 | 0.068923 | -0.00016228 | 0.068526 | -60.7681 | 61.8484 | -60.8688 | -60.8826 | 61.5829 | -0.045776 | -0.16937 | -0.004578 | 61.8347 | -60.9283 | -0.17853 | -0.050354 | -0.077819 | -0.19226 | -0.31586 | -0.23804 | -0.064087 | 0.10071 | 60.5209 | 60.6857 | 122.2733 | 122.5388 | -0.077819 | 122.525 | 60.6445 | -0.23804 | 122.5388 | -0.077819 | 60.6445 | 122.2733 | 122.525 | -122.7676 | -122.8271
295.0781 | 122.8317 | -60.7086 | 61.8301 | 0.15259 | 0.0094785 | 0.013317 | -0.0014783 | 0.06636 | 0.0015467 | 0.06874 | -60.7819 | 61.6974 | -60.8871 | -60.8643 | 61.6241 | -0.064087 | -0.40741 | -0.045776 | 61.7477 | -60.8734 | -0.17853 | -0.13275 | -0.073242 | -0.15564 | -0.20599 | -0.16479 | -0.082397 | 0.10529 | 60.3012 | 60.6628 | 122.3328 | 122.406 | -0.073242 | 122.4564 | 60.6445 | -0.16479 | 122.406 | -0.073242 | 60.6445 | 122.3328 | 122.4564 | -122.7173 | -122.7036
296.0625 | 122.7997 | -60.7132 | 61.8759 | -0.18311 | 0.014178 | 0.021862 | 0.0036487 | 0.069992 | 0.00047852 | 0.068953 | -60.7452 | 61.8164 | -60.8276 | -60.8734 | 61.5921 | -0.068665 | -0.22888 | -0.082397 | 61.7889 | -60.9741 | -0.11444 | -0.05951 | -0.032043 | -0.16022 | -0.28381 | -0.26092 | -0.086976 | 0.082398 | 60.4843 | 60.6308 | 122.3053 | 122.5296 | -0.032043 | 122.5021 | 60.6445 | -0.26092 | 122.5296 | -0.032043 | 60.6445 | 122.3053 | 122.5021 | -122.7036 | -122.85
297.0625 | 122.7814 | -60.704 | 61.8576 | -0.21362 | 0.013965 | 0.020153 | 0.00087167 | 0.069564 | -0.0016577 | 0.068953 | -60.7544 | 61.8347 | -60.8826 | -60.8643 | 61.5784 | -0.064087 | -0.24261 | -0.022888 | 61.8027 | -60.9467 | -0.17853 | -0.022888 | -0.050354 | -0.16022 | -0.27924 | -0.24261 | -0.054932 | 0.12817 | 60.4614 | 60.6812 | 122.2824 | 122.5388 | -0.050354 | 122.5067 | 60.64 | -0.24261 | 122.5388 | -0.050354 | 60.64 | 122.2824 | 122.5067 | -122.7402 | -122.8043
298.0625 | 122.7997 | -60.7086 | 61.853 | -0.27466 | 0.015033 | 0.018017 | 0.0042895 | 0.070419 | 5.1318e-05 | 0.069167 | -60.7452 | 61.8393 | -60.8505 | -60.8643 | 61.5921 | -0.054932 | -0.21973 | -0.032043 | 61.8301 | -60.9421 | -0.14191 | -0.013733 | -0.036621 | -0.15564 | -0.26093 | -0.23346 | -0.022888 | 0.10529 | 60.4889 | 60.6766 | 122.3007 | 122.5479 | -0.036621 | 122.5388 | 60.6537 | -0.23346 | 122.5479 | -0.036621 | 60.6537 | 122.3007 | 122.5388 | -122.7036 | -122.7951
299.0625 | 122.7814 | -60.7269 | 61.8805 | -0.27466 | 0.013324 | 0.014599 | 0.0032215 | 0.066574 | 0.0017603 | 0.067885 | -60.7681 | 61.8256 | -60.8643 | -60.8871 | 61.6104 | -0.045776 | -0.20599 | -0.027466 | 61.7981 | -60.9421 | -0.13733 | -0.054931 | -0.041198 | -0.16022 | -0.27008 | -0.21515 | -0.082397 | 0.096131 | 60.5209 | 60.6995 | 122.3373 | 122.5525 | -0.041198 | 122.525 | 60.6812 | -0.21515 | 122.5525 | -0.041198 | 60.6812 | 122.3373 | 122.525 | -122.7448 | -122.8226
300.0625 | 122.85 | -60.6766 | 61.8347 | -0.099182 | 0.013324 | 0.01524 | -0.0046825 | 0.067642 | 0.0015467 | 0.068953 | -60.7864 | 61.7844 | -60.8505 | -60.8688 | 61.615 | -0.054932 | -0.32044 | 0.004578 | 61.7889 | -60.8963 | -0.17395 | -0.050354 | -0.10986 | -0.19226 | -0.21973 | -0.21973 | -0.045777 | 0.064087 | 60.3561 | 60.6812 | 122.2916 | 122.4609 | -0.10986 | 122.4655 | 60.6216 | -0.21973 | 122.4609 | -0.10986 | 60.6216 | 122.2916 | 122.4655 | -122.6852 | -122.731
301.0625 | 122.7631 | -60.704 | 61.8668 | -0.24414 | 0.013324 | 0.017163 | 0.0049305 | 0.068069 | 0.00069212 | 0.068526 | -60.7956 | 61.8576 | -60.8826 | -60.8871 | 61.5692 | -0.082397 | -0.15106 | -0.032043 | 61.8484 | -60.9375 | -0.17853 | -0.009155 | -0.091552 | -0.18311 | -0.29755 | -0.23346 | -0.01831 | 0.086975 | 60.553 | 60.672 | 122.2733 | 122.5616 | -0.091552 | 122.5525 | 60.6216 | -0.23346 | 122.5616 | -0.091552 | 60.6216 | 122.2733 | 122.5525 | -122.7493 | -122.8043
302.0625 | 122.7951 | -60.6857 | 61.8759 | -0.22125 | 0.014178 | 0.015881 | 0.0042895 | 0.067214 | 0.0013329 | 0.06874 | -60.7498 | 61.8805 | -60.8505 | -60.8505 | 61.5967 | -0.07782 | -0.21973 | -0.045776 | 61.821 | -60.9375 | -0.16479 | 0.004577 | -0.064087 | -0.16479 | -0.27924 | -0.25177 | -0.054932 | 0.10071 | 60.466 | 60.64 | 122.2824 | 122.5662 | -0.064087 | 122.5067 | 60.6079 | -0.25177 | 122.5662 | -0.064087 | 60.6079 | 122.2824 | 122.5067 | -122.7264 | -122.8134
303.0625 | 122.7585 | -60.7224 | 61.8347 | -0.099182 | 0.014178 | 0.016308 | 0.0042895 | 0.06871 | -0.0010169 | 0.066817 | -60.7544 | 61.8301 | -60.8643 | -60.8871 | 61.5875 | -0.11902 | -0.25177 | -0.086975 | 61.8118 | -60.9512 | -0.14191 | -0.004578 | -0.032044 | -0.16479 | -0.24719 | -0.22888 | -0.022888 | 0.10986 | 60.4706 | 60.6354 | 122.3099 | 122.5525 | -0.032044 | 122.5342 | 60.6033 | -0.22888 | 122.5525 | -0.032044 | 60.6033 | 122.3099 | 122.5342 | -122.699 | -122.7859
304.125 | 122.8317 | -60.6766 | 61.8622 | -0.33569 | 0.012042 | 0.017803 | -0.0040417 | 0.068496 | -0.0010169 | 0.068526 | -60.7636 | 61.7706 | -60.8688 | -60.8414 | 61.6196 | -0.045776 | -0.23346 | 0.013733 | 61.8027 | -60.8963 | -0.19226 | -0.091553 | -0.086975 | -0.16479 | -0.24262 | -0.21973 | -0.05951 | 0.10528 | 60.4431 | 60.6903 | 122.2961 | 122.4472 | -0.086975 | 122.4792 | 60.6308 | -0.21973 | 122.4472 | -0.086975 | 60.6308 | 122.2961 | 122.4792 | -122.731 | -122.7585
305.0781 | 122.7997 | -60.7086 | 61.8988 | -0.15259 | 0.012256 | 0.018017 | 0.0040759 | 0.068923 | -0.0020849 | 0.067671 | -60.7315 | 61.8164 | -60.8643 | -60.8551 | 61.5738 | -0.09613 | -0.24719 | -0.045776 | 61.7935 | -60.9283 | -0.15564 | -0.082398 | -0.022888 | -0.14648 | -0.32501 | -0.21973 | -0.10529 | 0.13275 | 60.4614 | 60.6628 | 122.2824 | 122.525 | -0.022888 | 122.5021 | 60.6125 | -0.21973 | 122.525 | -0.022888 | 60.6125 | 122.2824 | 122.5021 | -122.7631 | -122.8271
306.0625 | 122.7997 | -60.6995 | 61.8851 | -0.31281 | 0.014605 | 0.018444 | 0.0030079 | 0.06636 | 0.00026492 | 0.06874 | -60.7727 | 61.853 | -60.878 | -60.8826 | 61.5875 | -0.091553 | -0.2243 | -0.054932 | 61.821 | -60.9329 | -0.17853 | -0.032044 | -0.073242 | -0.1831 | -0.29755 | -0.23346 | -0.064087 | 0.10529 | 60.4752 | 60.6445 | 122.287 | 122.5525 | -0.073242 | 122.5204 | 60.6079 | -0.23346 | 122.5525 | -0.073242 | 60.6079 | 122.287 | 122.5204 | -122.7631 | -122.818
307.1406 | 122.8088 | -60.7361 | 61.8301 | 0.061035 | 0.012683 | 0.014599 | 0.0017261 | 0.066787 | 5.1318e-05 | 0.069808 | -60.8368 | 61.7752 | -60.9192 | -60.9467 | 61.528 | -0.19226 | -0.36163 | -0.18768 | 61.7935 | -60.9329 | -0.18311 | -0.054931 | -0.10071 | -0.21057 | -0.30212 | -0.19684 | -0.036621 | 0.082397 | 60.3745 | 60.5484 | 122.2641 | 122.5113 | -0.10071 | 122.5296 | 60.5438 | -0.19684 | 122.5113 | -0.10071 | 60.5438 | 122.2641 | 122.5296 | -122.7493 | -122.7631
308.0625 | 122.7722 | -60.704 | 61.9171 | -0.32806 | 0.012469 | 0.019512 | 0.00044427 | 0.067214 | 0.00069212 | 0.067885 | -60.8185 | 61.853 | -60.8459 | -60.9283 | 61.5555 | -0.1236 | -0.14648 | -0.086975 | 61.8118 | -60.9467 | -0.14191 | -0.064087 | -0.11444 | -0.2243 | -0.36163 | -0.24261 | -0.10528 | 0.027466 | 60.5576 | 60.6171 | 122.2595 | 122.5571 | -0.11444 | 122.5159 | 60.5804 | -0.24261 | 122.5571 | -0.11444 | 60.5804 | 122.2595 | 122.5159 | -122.7631 | -122.8638
309.0625 | 122.731 | -60.759 | 61.8759 | 0.022888 | 0.011401 | 0.018017 | 0.0047169 | 0.070419 | 0.00090572 | 0.070662 | -60.8047 | 61.7981 | -60.8734 | -60.9604 | 61.5005 | -0.21973 | -0.2655 | -0.20142 | 61.8073 | -60.9558 | -0.11444 | -0.07782 | -0.045777 | -0.20142 | -0.37537 | -0.19684 | -0.068665 | 0.068664 | 60.4935 | 60.5576 | 122.2595 | 122.5571 | -0.045777 | 122.5662 | 60.5392 | -0.19684 | 122.5571 | -0.045777 | 60.5392 | 122.2595 | 122.5662 | -122.7493 | -122.8317
310.0781 | 122.7585 | -60.7132 | 61.8942 | -0.28229 | 0.012256 | 0.017376 | -0.0021191 | 0.067428 | 0.00069212 | 0.067244 | -60.8139 | 61.8301 | -60.8368 | -60.9192 | 61.5509 | -0.13733 | -0.16937 | -0.10071 | 61.821 | -60.9329 | -0.1236 | -0.064087 | -0.10071 | -0.20599 | -0.34332 | -0.21973 | -0.073242 | 0.022888 | 60.5438 | 60.6125 | 122.2641 | 122.5433 | -0.10071 | 122.5342 | 60.5759 | -0.21973 | 122.5433 | -0.10071 | 60.5759 | 122.2641 | 122.5342 | -122.731 | -122.8271
311.0625 | 122.7722 | -60.6949 | 61.8713 | -0.21362 | 0.013965 | 0.01524 | 0.0049305 | 0.069778 | -0.00037588 | 0.069808 | -60.7498 | 61.853 | -60.8643 | -60.8597 | 61.5875 | -0.1236 | -0.27924 | -0.091553 | 61.8256 | -60.9329 | -0.16937 | -0.018311 | -0.054932 | -0.16479 | -0.28381 | -0.23804 | -0.045776 | 0.11444 | 60.4156 | 60.6033 | 122.2824 | 122.5479 | -0.054932 | 122.5204 | 60.5713 | -0.23804 | 122.5479 | -0.054932 | 60.5713 | 122.2824 | 122.5204 | -122.7356 | -122.8043
312.0625 | 122.7631 | -60.6766 | 61.908 | -0.35095 | 0.01076 | 0.014813 | -0.00083733 | 0.067001 | -0.00058968 | 0.070021 | -60.8185 | 61.8301 | -60.8688 | -60.9146 | 61.5646 | -0.15564 | -0.16937 | -0.11902 | 61.8393 | -60.9146 | -0.19226 | -0.07782 | -0.14191 | -0.23804 | -0.34332 | -0.23804 | -0.068665 | 0.050354 | 60.5072 | 60.5576 | 122.2412 | 122.5067 | -0.14191 | 122.5159 | 60.5209 | -0.23804 | 122.5067 | -0.14191 | 60.5209 | 122.2412 | 122.5159 | -122.7768 | -122.8226
313.0625 | 122.7356 | -60.7086 | 61.8851 | -0.29755 | 0.013965 | 0.016094 | -0.0014783 | 0.067214 | 0.00069212 | 0.069167 | -60.8276 | 61.7981 | -60.8734 | -60.9238 | 61.5417 | -0.15564 | -0.1831 | -0.10529 | 61.8301 | -60.9055 | -0.16479 | -0.086975 | -0.11902 | -0.21515 | -0.34332 | -0.19684 | -0.054932 | 0.045776 | 60.5255 | 60.6033 | 122.2504 | 122.5067 | -0.11902 | 122.5388 | 60.553 | -0.19684 | 122.5067 | -0.11902 | 60.553 | 122.2504 | 122.5388 | -122.7585 | -122.7905
314.0625 | 122.7814 | -60.6766 | 61.8896 | -0.30518 | 0.01076 | 0.01289 | -0.0029735 | 0.065933 | -0.0022987 | 0.067031 | -60.7544 | 61.7752 | -60.8322 | -60.8459 | 61.6287 | -0.073242 | -0.30212 | -0.027466 | 61.8027 | -60.8826 | -0.15564 | -0.11444 | -0.07782 | -0.16937 | -0.26093 | -0.20599 | -0.086975 | 0.077819 | 60.3745 | 60.6491 | 122.3053 | 122.4518 | -0.07782 | 122.4792 | 60.6033 | -0.20599 | 122.4518 | -0.07782 | 60.6033 | 122.3053 | 122.4792 | -122.7219 | -122.7722
315.0625 | 122.818 | -60.6857 | 61.8896 | -0.099182 | 0.015033 | 0.019085 | 0.0045033 | 0.067642 | -0.0016577 | 0.069167 | -60.7361 | 61.821 | -60.8505 | -60.8597 | 61.5875 | -0.13733 | -0.3067 | -0.11444 | 61.8393 | -60.9238 | -0.16479 | -0.068664 | -0.050354 | -0.17395 | -0.30212 | -0.23804 | -0.050354 | 0.11444 | 60.379 | 60.5713 | 122.2733 | 122.5067 | -0.050354 | 122.525 | 60.5484 | -0.23804 | 122.5067 | -0.050354 | 60.5484 | 122.2733 | 122.525 | -122.7402 | -122.8134
316.0625 | 122.7402 | -60.7132 | 61.9034 | -0.35095 | 0.0099057 | 0.016735 | 0.0010853 | 0.067214 | 5.1318e-05 | 0.070021 | -60.8047 | 61.7889 | -60.8643 | -60.91 | 61.5692 | -0.15106 | -0.24719 | -0.1236 | 61.8256 | -60.8734 | -0.15106 | -0.11444 | -0.091553 | -0.19684 | -0.33417 | -0.16022 | -0.077819 | 0.059509 | 60.466 | 60.5896 | 122.2824 | 122.5021 | -0.091553 | 122.5388 | 60.5621 | -0.16022 | 122.5021 | -0.091553 | 60.5621 | 122.2824 | 122.5388 | -122.7676 | -122.7768
317.0625 | 122.7081 | -60.7224 | 61.8759 | -0.2594 | 0.011401 | 0.015881 | 0.0027943 | 0.066574 | 0.00090572 | 0.067885 | -60.8276 | 61.8301 | -60.8826 | -60.9192 | 61.5509 | -0.2655 | 0.032043 | -0.045776 | 61.8484 | -60.8963 | -0.16022 | -0.045777 | -0.10529 | -0.19684 | -0.32501 | -0.17395 | -0.027466 | 0.054931 | 60.7544 | 60.6766 | 122.2733 | 122.5525 | -0.10529 | 122.5708 | 60.4568 | -0.17395 | 122.5525 | -0.10529 | 60.4568 | 122.2733 | 122.5708 | -122.7585 | -122.7722
318.0781 | 122.8271 | -60.6903 | 61.8347 | 0.1297 | 0.012897 | 0.016735 | -0.0019055 | 0.065078 | -0.00080328 | 0.06639 | -60.7864 | 61.7111 | -60.8551 | -60.8871 | 61.5738 | -0.19226 | -0.48065 | -0.17395 | 61.7798 | -60.8871 | -0.16479 | -0.1236 | -0.09613 | -0.19684 | -0.26093 | -0.19684 | -0.054932 | 0.068665 | 60.2097 | 60.5164 | 122.2641 | 122.4014 | -0.09613 | 122.4701 | 60.498 | -0.19684 | 122.4014 | -0.09613 | 60.498 | 122.2641 | 122.4701 | -122.6898 | -122.7219
319.0625 | 122.7448 | -60.6949 | 61.908 | -0.2594 | 0.012683 | 0.009472 | 0.0015125 | 0.065933 | -0.00058968 | 0.067458 | -60.7956 | 61.8256 | -60.8688 | -60.8963 | 61.5601 | -0.18768 | -0.21973 | -0.14191 | 61.853 | -60.9146 | -0.17395 | -0.082397 | -0.10071 | -0.20142 | -0.3479 | -0.21973 | -0.054932 | 0.073242 | 60.4752 | 60.553 | 122.2549 | 122.5204 | -0.10071 | 122.5479 | 60.5072 | -0.21973 | 122.5204 | -0.10071 | 60.5072 | 122.2549 | 122.5479 | -122.7768 | -122.8226
320.0938 | 122.7768 | -60.7178 | 61.8668 | -1.7242 | 0.015033 | 0.018231 | 0.0047169 | 0.068283 | -0.00058968 | 0.068312 | -60.8231 | 61.8347 | -60.8871 | -60.9512 | 61.4868 | -0.27008 | -0.39825 | -0.30212 | 61.8118 | -60.9329 | -0.16937 | -0.032043 | -0.10529 | -0.23346 | -0.37994 | -0.21515 | -0.054931 | 0.064087 | 60.3195 | 60.4156 | 122.2046 | 122.5525 | -0.10529 | 122.5296 | 60.4477 | -0.21515 | 122.5525 | -0.10529 | 60.4477 | 122.2046 | 122.5296 | -122.7539 | -122.7997
321.0938 | 122.8363 | -60.6491 | 61.8805 | -0.26703 | 0.011615 | 0.013531 | -0.0016919 | 0.066146 | -0.0012305 | 0.070235 | -60.7407 | 61.7661 | -60.8597 | -60.8185 | 61.6333 | -0.10986 | -0.37537 | -0.082397 | 61.8027 | -60.878 | -0.21057 | -0.11444 | -0.091553 | -0.16937 | -0.24719 | -0.22888 | -0.07782 | 0.11902 | 60.2737 | 60.5667 | 122.2824 | 122.4152 | -0.091553 | 122.4518 | 60.5392 | -0.22888 | 122.4152 | -0.091553 | 60.5392 | 122.2824 | 122.4518 | -122.7402 | -122.7585
322.0625 | 122.731 | -60.6995 | 61.8805 | 0.11444 | 0.013537 | 0.013745 | 0.0045033 | 0.06636 | -0.0016577 | 0.06938 | -60.8276 | 61.8347 | -60.878 | -60.9009 | 61.5417 | -0.20599 | -0.2655 | -0.18768 | 61.8118 | -60.9375 | -0.17853 | -0.045776 | -0.12817 | -0.20142 | -0.33875 | -0.23804 | -0.068664 | 0.050354 | 60.434 | 60.5118 | 122.2412 | 122.5342 | -0.12817 | 122.5113 | 60.4935 | -0.23804 | 122.5342 | -0.12817 | 60.4935 | 122.2412 | 122.5113 | -122.7585 | -122.818
323.0781 | 122.8958 | -60.6445 | 61.8439 | -0.20599 | 0.010119 | 0.015026 | -0.0025463 | 0.065292 | -0.00080328 | 0.066603 | -60.7132 | 61.7661 | -60.8505 | -60.791 | 61.6699 | -0.11444 | -0.46692 | -0.050354 | 61.7889 | -60.8643 | -0.20599 | -0.07782 | -0.068665 | -0.14648 | -0.17395 | -0.21973 | -0.054932 | 0.13733 | 60.1776 | 60.5942 | 122.3145 | 122.4106 | -0.068665 | 122.4335 | 60.5301 | -0.21973 | 122.4106 | -0.068665 | 60.5301 | 122.3145 | 122.4335 | -122.6944 | -122.7081
324.0781 | 122.7219 | -60.7315 | 61.8439 | -6e-08 | 0.012683 | 0.019726 | 0.0053577 | 0.066574 | -0.0014441 | 0.068099 | -60.8322 | 61.8301 | -60.8688 | -60.9421 | 61.4822 | -0.31128 | -0.37994 | -0.32044 | 61.7661 | -60.9558 | -0.13733 | -0.013733 | -0.10071 | -0.21057 | -0.36163 | -0.2243 | -0.07782 | 0.036621 | 60.3516 | 60.4111 | 122.2137 | 122.5616 | -0.10071 | 122.4976 | 60.4202 | -0.2243 | 122.5616 | -0.10071 | 60.4202 | 122.2137 | 122.4976 | -122.7127 | -122.7997
325.0781 | 122.7814 | -60.6949 | 61.8851 | -0.24414 | 0.014819 | 0.017376 | 0.0030079 | 0.065933 | 0.00026492 | 0.069594 | -60.7956 | 61.8393 | -60.8597 | -60.8688 | 61.5509 | -0.20599 | -0.28381 | -0.19684 | 61.8164 | -60.9283 | -0.16479 | -0.045777 | -0.10071 | -0.17395 | -0.33417 | -0.23346 | -0.068665 | 0.064087 | 60.4111 | 60.498 | 122.2458 | 122.5342 | -0.10071 | 122.5113 | 60.4889 | -0.23346 | 122.5342 | -0.10071 | 60.4889 | 122.2458 | 122.5113 | -122.7448 | -122.8134
326.0625 | 122.8134 | -60.6766 | 61.8668 | -0.21362 | 0.014819 | 0.018231 | 0.0062121 | 0.067642 | -0.0014441 | 0.068099 | -60.759 | 61.8759 | -60.8871 | -60.8688 | 61.5875 | -0.19684 | -0.34332 | -0.16937 | 61.8118 | -60.9192 | -0.21057 | 0.009156 | -0.082397 | -0.19226 | -0.27924 | -0.24261 | -0.054931 | 0.12817 | 60.3333 | 60.5072 | 122.2641 | 122.5525 | -0.082397 | 122.4884 | 60.4797 | -0.24261 | 122.5525 | -0.082397 | 60.4797 | 122.2641 | 122.4884 | -122.7539 | -122.7859
327.0938 | 122.7768 | -60.7086 | 61.8713 | -0.23651 | 0.013537 | 0.017803 | 0.0032215 | 0.067001 | 0.0015467 | 0.067671 | -60.791 | 61.853 | -60.8505 | -60.8826 | 61.5738 | -0.21973 | -0.31128 | -0.20599 | 61.8301 | -60.9146 | -0.14191 | -0.018311 | -0.082398 | -0.17395 | -0.29755 | -0.20599 | -0.041199 | 0.059509 | 60.3973 | 60.5026 | 122.2824 | 122.5616 | -0.082398 | 122.5388 | 60.4889 | -0.20599 | 122.5616 | -0.082398 | 60.4889 | 122.2824 | 122.5388 | -122.7219 | -122.7859
328.0625 | 122.7448 | -60.6857 | 61.8896 | -0.30518 | 0.011188 | 0.015881 | -0.00041013 | 0.06636 | -0.0018713 | 0.067031 | -60.791 | 61.8118 | -60.8734 | -60.8826 | 61.5463 | -0.24261 | -0.31586 | -0.21515 | 61.8484 | -60.9009 | -0.18768 | -0.077819 | -0.10529 | -0.19684 | -0.34332 | -0.21515 | -0.041198 | 0.082397 | 60.3699 | 60.4706 | 122.2321 | 122.4976 | -0.10529 | 122.5342 | 60.4431 | -0.21515 | 122.4976 | -0.10529 | 60.4431 | 122.2321 | 122.5342 | -122.7631 | -122.7905
329.0625 | 122.7448 | -60.6995 | 61.8942 | -0.44251 | 0.012683 | 0.015667 | -0.0025463 | 0.067001 | 0.00026492 | 0.067885 | -60.7956 | 61.8073 | -60.8551 | -60.8871 | 61.5646 | -0.24261 | -0.32959 | -0.20599 | 61.8439 | -60.9009 | -0.15564 | -0.086975 | -0.09613 | -0.18768 | -0.32959 | -0.20142 | -0.050354 | 0.05951 | 60.3699 | 60.4935 | 122.2641 | 122.5067 | -0.09613 | 122.5433 | 60.4568 | -0.20142 | 122.5067 | -0.09613 | 60.4568 | 122.2641 | 122.5433 | -122.7493 | -122.7951
330.0781 | 122.7859 | -60.6995 | 61.8896 | -0.28992 | 0.013965 | 0.018231 | 0.0042895 | 0.067001 | -0.00058968 | 0.067885 | -60.7636 | 61.8484 | -60.8505 | -60.8597 | 61.5738 | -0.2243 | -0.36621 | -0.21515 | 61.8301 | -60.9375 | -0.15106 | -0.041198 | -0.064087 | -0.16022 | -0.31586 | -0.23804 | -0.059509 | 0.086975 | 60.3333 | 60.4843 | 122.2733 | 122.5479 | -0.064087 | 122.5296 | 60.4752 | -0.23804 | 122.5479 | -0.064087 | 60.4752 | 122.2733 | 122.5296 | -122.7402 | -122.8271
331.0625 | 122.7814 | -60.7086 | 61.9171 | -0.28229 | 0.012469 | 0.016308 | 0.0051441 | 0.067001 | -0.00080328 | 0.070235 | -60.7819 | 61.8484 | -60.878 | -60.9009 | 61.5784 | -0.26093 | -0.3479 | -0.23346 | 61.821 | -60.9467 | -0.16937 | -0.068664 | -0.073242 | -0.19226 | -0.33874 | -0.23804 | -0.09613 | 0.096131 | 60.3607 | 60.4752 | 122.287 | 122.5571 | -0.073242 | 122.5296 | 60.4477 | -0.23804 | 122.5571 | -0.073242 | 60.4477 | 122.287 | 122.5296 | -122.7951 | -122.8638
332.0625 | 122.7859 | -60.704 | 61.8759 | -0.22888 | 0.014605 | 0.017376 | 0.0015125 | 0.068923 | 0.0015467 | 0.068312 | -60.7407 | 61.8439 | -60.8643 | -60.8459 | 61.5829 | -0.25177 | -0.44403 | -0.22888 | 61.7935 | -60.9238 | -0.16022 | -0.032044 | -0.036621 | -0.14191 | -0.29297 | -0.21973 | -0.082398 | 0.1236 | 60.26 | 60.4752 | 122.287 | 122.5479 | -0.036621 | 122.4976 | 60.4523 | -0.21973 | 122.5479 | -0.036621 | 60.4523 | 122.287 | 122.4976 | -122.7402 | -122.7997
333.0625 | 122.7722 | -60.7269 | 61.8942 | -0.2594 | 0.013965 | 0.015026 | 0.00087167 | 0.069137 | 0.00026492 | 0.068953 | -60.8047 | 61.8484 | -60.8871 | -60.878 | 61.5738 | -0.27008 | -0.3479 | -0.24261 | 61.8347 | -60.9055 | -0.16022 | -0.045776 | -0.07782 | -0.15106 | -0.32043 | -0.17853 | -0.059509 | 0.082397 | 60.379 | 60.4843 | 122.3007 | 122.5754 | -0.07782 | 122.5616 | 60.4568 | -0.17853 | 122.5754 | -0.07782 | 60.4568 | 122.3007 | 122.5616 | -122.7814 | -122.7997
334.0625 | 122.7539 | -60.6903 | 61.9125 | -0.25177 | 0.012256 | 0.01524 | 0.0010853 | 0.067001 | -0.0012305 | 0.068953 | -60.8139 | 61.8484 | -60.878 | -60.8963 | 61.5555 | -0.2655 | -0.34332 | -0.27008 | 61.8347 | -60.91 | -0.18768 | -0.064087 | -0.1236 | -0.20599 | -0.35706 | -0.21973 | -0.07782 | 0.064087 | 60.347 | 60.4202 | 122.2458 | 122.5388 | -0.1236 | 122.525 | 60.4248 | -0.21973 | 122.5388 | -0.1236 | 60.4248 | 122.2458 | 122.525 | -122.7905 | -122.8226
335.0625 | 122.7173 | -60.7269 | 61.8622 | 0.0076294 | 0.01546 | 0.016522 | 0.0045033 | 0.069992 | 0.00026492 | 0.068526 | -60.8093 | 61.853 | -60.8734 | -60.9467 | 61.496 | -0.36621 | -0.44861 | -0.39368 | 61.8301 | -60.9375 | -0.14648 | -0.009156 | -0.082397 | -0.21973 | -0.36621 | -0.21057 | -0.032044 | 0.064087 | 60.2783 | 60.3333 | 122.2229 | 122.58 | -0.082397 | 122.5571 | 60.3607 | -0.21057 | 122.58 | -0.082397 | 60.3607 | 122.2229 | 122.5571 | -122.7356 | -122.7997
336.0625 | 122.7402 | -60.6995 | 61.9125 | -0.2594 | 0.013537 | 0.017376 | 0.00087167 | 0.067214 | 0.0015467 | 0.068312 | -60.8047 | 61.8393 | -60.8734 | -60.91 | 61.5829 | -0.3067 | -0.35248 | -0.27924 | 61.8301 | -60.9146 | -0.17395 | -0.073243 | -0.10529 | -0.21057 | -0.32959 | -0.21515 | -0.082398 | 0.068664 | 60.347 | 60.4202 | 122.2824 | 122.5388 | -0.10529 | 122.5296 | 60.3928 | -0.21515 | 122.5388 | -0.10529 | 60.3928 | 122.2824 | 122.5296 | -122.7859 | -122.8271
337.0625 | 122.7768 | -60.704 | 61.8622 | -0.21362 | 0.012256 | 0.012463 | 0.0027943 | 0.065719 | 0.00069212 | 0.066176 | -60.8047 | 61.8256 | -60.8826 | -60.9009 | 61.5417 | -0.29755 | -0.37079 | -0.27924 | 61.8256 | -60.9238 | -0.17853 | -0.036621 | -0.10071 | -0.19684 | -0.32044 | -0.21973 | -0.036621 | 0.077819 | 60.3333 | 60.4248 | 122.2458 | 122.5296 | -0.10071 | 122.5296 | 60.4065 | -0.21973 | 122.5296 | -0.10071 | 60.4065 | 122.2458 | 122.5296 | -122.7448 | -122.7859
338.0625 | 122.7997 | -60.6949 | 61.8668 | -0.2594 | 0.015674 | 0.017376 | 0.0045033 | 0.069564 | 0.00026492 | 0.070021 | -60.7315 | 61.8256 | -60.8643 | -60.8505 | 61.5738 | -0.29297 | -0.48981 | -0.28381 | 61.8118 | -60.9329 | -0.16937 | -0.041198 | -0.036621 | -0.15564 | -0.29297 | -0.23804 | -0.054931 | 0.13275 | 60.2051 | 60.4111 | 122.2687 | 122.5204 | -0.036621 | 122.5067 | 60.4019 | -0.23804 | 122.5204 | -0.036621 | 60.4019 | 122.2687 | 122.5067 | -122.731 | -122.7997
339.0625 | 122.7814 | -60.6903 | 61.8805 | -0.19836 | 0.011828 | 0.018231 | 0.0045033 | 0.066574 | 0.00069212 | 0.068099 | -60.7681 | 61.821 | -60.8734 | -60.8688 | 61.5692 | -0.28381 | -0.42572 | -0.27924 | 61.8484 | -60.91 | -0.1831 | -0.059509 | -0.077819 | -0.17853 | -0.31128 | -0.21973 | -0.032043 | 0.10529 | 60.2646 | 60.4111 | 122.2595 | 122.5113 | -0.077819 | 122.5388 | 60.4065 | -0.21973 | 122.5113 | -0.077819 | 60.4065 | 122.2595 | 122.5388 | -122.7539 | -122.7905
340.0625 | 122.85 | -60.6766 | 61.8393 | 0.099182 | 0.015033 | 0.018017 | 0.00065787 | 0.067855 | 0.00047852 | 0.070235 | -60.7864 | 61.7889 | -60.878 | -60.878 | 61.6058 | -0.3479 | -0.67291 | -0.37079 | 61.7798 | -60.9055 | -0.20142 | -0.050354 | -0.10986 | -0.20142 | -0.23346 | -0.22888 | -0.059509 | 0.091553 | 60.0037 | 60.3058 | 122.2824 | 122.4655 | -0.10986 | 122.4564 | 60.3287 | -0.22888 | 122.4655 | -0.10986 | 60.3287 | 122.2824 | 122.4564 | -122.7173 | -122.7448
341.0625 | 122.7539 | -60.7086 | 61.8805 | -0.28992 | 0.012469 | 0.016522 | 0.0027943 | 0.069564 | -0.00058968 | 0.06639 | -60.7773 | 61.853 | -60.8688 | -60.8871 | 61.5646 | -0.31586 | -0.42114 | -0.29755 | 61.8073 | -60.9329 | -0.16022 | -0.027466 | -0.068665 | -0.17853 | -0.31586 | -0.2243 | -0.073242 | 0.091552 | 60.2875 | 60.4111 | 122.2733 | 122.5616 | -0.068665 | 122.5159 | 60.3928 | -0.2243 | 122.5616 | -0.068665 | 60.3928 | 122.2733 | 122.5159 | -122.7493 | -122.8134
342.0625 | 122.7859 | -60.6949 | 61.8713 | -0.25177 | 0.014605 | 0.015667 | 0.0030079 | 0.06871 | -0.0012305 | 0.067458 | -60.791 | 61.8439 | -60.8459 | -60.8871 | 61.5601 | -0.33875 | -0.42114 | -0.31128 | 61.853 | -60.9192 | -0.15106 | -0.027466 | -0.096131 | -0.19226 | -0.31128 | -0.2243 | -0.018311 | 0.054931 | 60.2737 | 60.3836 | 122.2549 | 122.5388 | -0.096131 | 122.5479 | 60.3561 | -0.2243 | 122.5388 | -0.096131 | 60.3561 | 122.2549 | 122.5479 | -122.7173 | -122.7905
343.0625 | 122.7402 | -60.7086 | 61.8942 | -0.32043 | 0.012042 | 0.015667 | -0.0029735 | 0.066146 | 0.00047852 | 0.067458 | -60.8047 | 61.8484 | -60.8688 | -60.8963 | 61.5463 | -0.36621 | -0.40283 | -0.33417 | 61.8439 | -60.9375 | -0.16022 | -0.045776 | -0.096131 | -0.18768 | -0.3479 | -0.22888 | -0.050354 | 0.064086 | 60.3058 | 60.3745 | 122.2549 | 122.5571 | -0.096131 | 122.5525 | 60.3424 | -0.22888 | 122.5571 | -0.096131 | 60.3424 | 122.2549 | 122.5525 | -122.7631 | -122.8317
344.0625 | 122.7448 | -60.704 | 61.9125 | -0.22888 | 0.014392 | 0.016949 | 0.0027943 | 0.065505 | -0.00080328 | 0.068099 | -60.8414 | 61.8164 | -60.8963 | -60.9009 | 61.5372 | -0.36163 | -0.43945 | -0.34332 | 61.8256 | -60.9283 | -0.19226 | -0.096131 | -0.13733 | -0.19684 | -0.37537 | -0.2243 | -0.086975 | 0.054931 | 60.2646 | 60.3607 | 122.2412 | 122.5204 | -0.13733 | 122.5296 | 60.3424 | -0.2243 | 122.5204 | -0.13733 | 60.3424 | 122.2412 | 122.5296 | -122.8088 | -122.8409
345.0625 | 122.7631 | -60.6995 | 61.8622 | -0.038147 | 0.014178 | 0.019299 | 0.0053577 | 0.068496 | -0.0014441 | 0.069808 | -60.7224 | 61.8668 | -60.8505 | -60.8643 | 61.5692 | -0.37994 | -0.54016 | -0.36621 | 61.8164 | -60.9467 | -0.15106 | 0.004577 | -0.022888 | -0.16479 | -0.29297 | -0.24719 | -0.045777 | 0.12817 | 60.1593 | 60.3333 | 122.2687 | 122.5662 | -0.022888 | 122.5159 | 60.3195 | -0.24719 | 122.5662 | -0.022888 | 60.3195 | 122.2687 | 122.5159 | -122.7127 | -122.8088
346.0625 | 122.7676 | -60.6766 | 61.8805 | -0.22125 | 0.013965 | 0.01759 | 0.0032215 | 0.069351 | -0.0012305 | 0.067244 | -60.7727 | 61.8622 | -60.8597 | -60.8826 | 61.5829 | -0.36163 | -0.47607 | -0.34332 | 61.8439 | -60.9146 | -0.1831 | -0.01831 | -0.09613 | -0.20599 | -0.29755 | -0.23804 | -0.036621 | 0.086975 | 60.2005 | 60.3333 | 122.2595 | 122.5388 | -0.09613 | 122.5204 | 60.3149 | -0.23804 | 122.5388 | -0.09613 | 60.3149 | 122.2595 | 122.5204 | -122.7402 | -122.7951
347.0625 | 122.7814 | -60.6766 | 61.8988 | -0.23651 | 0.013324 | 0.015667 | 0.0012989 | 0.067214 | -0.0012305 | 0.068099 | -60.7773 | 61.853 | -60.8643 | -60.8734 | 61.5555 | -0.36163 | -0.4715 | -0.3479 | 61.8393 | -60.9421 | -0.18768 | -0.045777 | -0.10071 | -0.19684 | -0.34332 | -0.2655 | -0.05951 | 0.086975 | 60.2051 | 60.3287 | 122.2321 | 122.5296 | -0.10071 | 122.5159 | 60.3149 | -0.2655 | 122.5296 | -0.10071 | 60.3149 | 122.2321 | 122.5159 | -122.7631 | -122.8409
348.0625 | 122.7448 | -60.6903 | 61.908 | -0.2594 | 0.012256 | 0.01289 | 0.0012989 | 0.068496 | -0.0018713 | 0.068953 | -60.7819 | 61.8484 | -60.878 | -60.8871 | 61.5555 | -0.37994 | -0.48065 | -0.36163 | 61.8622 | -60.91 | -0.18768 | -0.059509 | -0.091552 | -0.19684 | -0.35248 | -0.21973 | -0.045776 | 0.096131 | 60.2097 | 60.3287 | 122.2458 | 122.5388 | -0.091552 | 122.5525 | 60.3104 | -0.21973 | 122.5388 | -0.091552 | 60.3104 | 122.2458 | 122.5525 | -122.7859 | -122.818
349.0625 | 122.7402 | -60.6995 | 61.9171 | -0.26703 | 0.010974 | 0.016308 | -0.00083733 | 0.065505 | -0.00058968 | 0.070662 | -60.8139 | 61.8393 | -60.8643 | -60.8917 | 61.5326 | -0.39825 | -0.45319 | -0.38452 | 61.8484 | -60.91 | -0.16479 | -0.07782 | -0.11444 | -0.19226 | -0.38452 | -0.21057 | -0.068664 | 0.050354 | 60.2463 | 60.3149 | 122.2321 | 122.5388 | -0.11444 | 122.5479 | 60.3012 | -0.21057 | 122.5388 | -0.11444 | 60.3012 | 122.2321 | 122.5479 | -122.7814 | -122.8271
350.125 | 122.8638 | -60.6812 | 61.8347 | 0.17548 | 0.012256 | 0.016522 | 0.0036487 | 0.067642 | 0.0024011 | 0.068312 | -60.7544 | 61.7615 | -60.8688 | -60.8505 | 61.5875 | -0.41199 | -0.77362 | -0.41657 | 61.7615 | -60.9009 | -0.18768 | -0.073242 | -0.073243 | -0.16937 | -0.24719 | -0.21973 | -0.073242 | 0.11444 | 59.9075 | 60.2646 | 122.2687 | 122.4426 | -0.073243 | 122.4426 | 60.2692 | -0.21973 | 122.4426 | -0.073243 | 60.2692 | 122.2687 | 122.4426 | -122.7036 | -122.7356
351.0625 | 122.7814 | -60.6995 | 61.8942 | -0.17548 | 0.012683 | 0.020794 | 0.0055713 | 0.066574 | -0.0010169 | 0.065962 | -60.7681 | 61.8622 | -60.8643 | -60.8505 | 61.5738 | -0.39368 | -0.53101 | -0.38452 | 61.8118 | -60.9055 | -0.16479 | -0.032043 | -0.068664 | -0.15106 | -0.32043 | -0.20599 | -0.082397 | 0.096131 | 60.1685 | 60.3149 | 122.2733 | 122.5616 | -0.068664 | 122.5113 | 60.3058 | -0.20599 | 122.5616 | -0.068664 | 60.3058 | 122.2733 | 122.5113 | -122.7585 | -122.7997
352.0625 | 122.8317 | -60.6949 | 61.8439 | 0.19836 | 0.016314 | 0.015026 | 0.0021533 | 0.069351 | -0.0035803 | 0.06938 | -60.7864 | 61.8073 | -60.8826 | -60.9055 | 61.5372 | -0.46234 | -0.75531 | -0.46692 | 61.7706 | -60.9146 | -0.18768 | -0.036621 | -0.091553 | -0.21057 | -0.3067 | -0.21973 | -0.073242 | 0.09613 | 59.9396 | 60.228 | 122.2321 | 122.5021 | -0.091553 | 122.4655 | 60.2325 | -0.21973 | 122.5021 | -0.091553 | 60.2325 | 122.2321 | 122.4655 | -122.7264 | -122.7585
353.0625 | 122.8043 | -60.7086 | 61.8622 | -0.14496 | 0.013537 | 0.018658 | 0.0055713 | 0.068069 | -0.0010169 | 0.070876 | -60.7407 | 61.8576 | -60.8505 | -60.8643 | 61.5738 | -0.40741 | -0.77362 | -0.49896 | 61.8164 | -60.9421 | -0.14191 | -0.004578 | -0.032044 | -0.15564 | -0.28839 | -0.23346 | -0.045777 | 0.10986 | 59.935 | 60.2097 | 122.2824 | 122.5662 | -0.032044 | 122.525 | 60.3012 | -0.23346 | 122.5662 | -0.032044 | 60.3012 | 122.2824 | 122.525 | -122.7127 | -122.8043
354.0625 | 122.7631 | -60.6949 | 61.8668 | -0.32806 | 0.014819 | 0.019726 | 0.0010853 | 0.067214 | -0.00016228 | 0.06874 | -60.8047 | 61.8484 | -60.8734 | -60.9009 | 61.5509 | -0.42114 | -0.52643 | -0.4303 | 61.8759 | -60.9146 | -0.17853 | -0.01831 | -0.10986 | -0.20599 | -0.31586 | -0.21973 | 0.009156 | 0.068664 | 60.1685 | 60.2646 | 122.2458 | 122.5433 | -0.10986 | 122.5708 | 60.2737 | -0.21973 | 122.5433 | -0.10986 | 60.2737 | 122.2458 | 122.5708 | -122.7402 | -122.7814
355.0938 | 122.8363 | -60.6812 | 61.8484 | 0.11444 | 0.011188 | 0.011608 | -0.0034009 | 0.06636 | -0.0027259 | 0.06938 | -60.7636 | 61.7386 | -60.8459 | -60.8734 | 61.5875 | -0.45776 | -0.77362 | -0.46234 | 61.7935 | -60.8826 | -0.1648 | -0.10986 | -0.082398 | -0.19226 | -0.26093 | -0.20142 | -0.054932 | 0.082397 | 59.9075 | 60.2188 | 122.2687 | 122.4197 | -0.082398 | 122.4747 | 60.2234 | -0.20142 | 122.4197 | -0.082398 | 60.2234 | 122.2687 | 122.4747 | -122.6944 | -122.731
356.0625 | 122.7356 | -60.6995 | 61.8988 | -0.32043 | 0.012683 | 0.017376 | 0.0023669 | 0.067001 | 5.1318e-05 | 0.066603 | -60.8002 | 61.8622 | -60.8414 | -60.7315 | 61.5967 | -0.46234 | -0.64545 | -0.44861 | 61.8073 | -60.9283 | -0.14191 | -0.036621 | -0.10071 | -0.032043 | -0.30212 | -0.22888 | -0.091553 | 0.041199 | 60.054 | 60.2509 | 122.2961 | 122.5616 | -0.10071 | 122.5067 | 60.2371 | -0.22888 | 122.5616 | -0.10071 | 60.2371 | 122.2961 | 122.5067 | -122.7402 | -122.8271
357.0625 | 122.7631 | -60.6812 | 61.9583 | -0.35858 | 0.014392 | 0.01289 | 0.0012989 | 0.06636 | -0.00058968 | 0.071089 | -60.791 | 61.853 | -60.8597 | -60.9009 | 61.5417 | -0.46692 | -0.51727 | -0.46234 | 61.8622 | -60.9192 | -0.17853 | -0.10529 | -0.10986 | -0.21973 | -0.41656 | -0.23804 | -0.09613 | 0.068664 | 60.1639 | 60.2188 | 122.2229 | 122.5342 | -0.10986 | 122.5433 | 60.2142 | -0.23804 | 122.5342 | -0.10986 | 60.2142 | 122.2229 | 122.5433 | -122.818 | -122.8775
358.1094 | 122.8912 | -60.6674 | 61.8439 | 0.13733 | 0.0096921 | 0.017376 | 0.0021533 | 0.067001 | -0.0010169 | 0.069167 | -60.7315 | 61.7569 | -60.8688 | -60.8322 | 61.6058 | -0.45319 | -1.0071 | -0.63629 | 61.7157 | -60.9009 | -0.20142 | -0.086975 | -0.064087 | -0.16479 | -0.23804 | -0.23346 | -0.12817 | 0.13733 | 59.6603 | 60.0311 | 122.2733 | 122.4243 | -0.064087 | 122.3831 | 60.2142 | -0.23346 | 122.4243 | -0.064087 | 60.2142 | 122.2733 | 122.3831 | -122.7127 | -122.7448
359.0625 | 122.7676 | -60.704 | 61.8851 | 0.66376 | 0.012256 | 0.020367 | 0.0051441 | 0.065292 | 0.00069212 | 0.068526 | -60.8231 | 61.8484 | -60.8826 | -60.9009 | 61.5509 | -0.44861 | -0.54016 | -0.48065 | 61.8256 | -60.9421 | -0.17853 | -0.036621 | -0.11902 | -0.19684 | -0.33417 | -0.23804 | -0.059509 | 0.059509 | 60.1639 | 60.2234 | 122.2549 | 122.5525 | -0.11902 | 122.5296 | 60.2554 | -0.23804 | 122.5525 | -0.11902 | 60.2554 | 122.2549 | 122.5296 | -122.7676 | -122.8271
360.0938 | 122.7997 | -60.6949 | 61.8439 | 0.091553 | 0.01076 | 0.020153 | 0.0027943 | 0.06871 | -0.00037588 | 0.069167 | -60.8002 | 61.8027 | -60.8688 | -60.9146 | 61.5234 | -0.54932 | -0.76446 | -0.56763 | 61.7981 | -60.9375 | -0.17395 | -0.041199 | -0.10529 | -0.21973 | -0.32043 | -0.24262 | -0.045776 | 0.068664 | 59.9304 | 60.1273 | 122.2183 | 122.4976 | -0.10529 | 122.493 | 60.1456 | -0.24262 | 122.4976 | -0.10529 | 60.1456 | 122.2183 | 122.493 | -122.7127 | -122.7814
361.0625 | 122.7539 | -60.6949 | 61.8713 | 0.70953 | 0.011188 | 0.014172 | 0.0032215 | 0.066787 | 0.00090572 | 0.068526 | -60.5988 | 61.8256 | -60.8734 | -60.9238 | 61.5189 | -0.58136 | -0.71869 | -0.60425 | 61.8393 | -60.9329 | -0.17853 | -0.045776 | 0.09613 | -0.22888 | -0.35248 | -0.23804 | -0.032044 | 0.27466 | 59.9762 | 60.0906 | 122.2137 | 122.5204 | 0.09613 | 122.5342 | 60.1135 | -0.23804 | 122.5204 | 0.09613 | 60.1135 | 122.2137 | 122.5342 | -122.7448 | -122.8043
362.0625 | 122.7631 | -60.6903 | 61.8988 | -0.22888 | 0.011188 | 0.012676 | 0.0036487 | 0.065505 | -0.0014441 | 0.069594 | -60.7773 | 61.8393 | -60.8414 | -60.9009 | 61.5509 | -0.50812 | -0.59052 | -0.48981 | 61.8393 | -60.91 | -0.15106 | -0.05951 | -0.086975 | -0.21057 | -0.3479 | -0.21973 | -0.05951 | 0.064087 | 60.0998 | 60.2005 | 122.2412 | 122.5296 | -0.086975 | 122.5296 | 60.1822 | -0.21973 | 122.5296 | -0.086975 | 60.1822 | 122.2412 | 122.5296 | -122.7402 | -122.8088
363.0625 | 122.8134 | -60.6583 | 61.8896 | -0.31281 | 0.010333 | 0.015454 | -0.0025463 | 0.065719 | -0.00080328 | 0.069808 | -60.7315 | 61.7981 | -60.8231 | -60.8185 | 61.615 | -0.43488 | -0.65002 | -0.41657 | 61.8118 | -60.8643 | -0.16479 | -0.091552 | -0.073242 | -0.16022 | -0.27466 | -0.20599 | -0.077819 | 0.091553 | 60.0082 | 60.2417 | 122.2733 | 122.4564 | -0.073242 | 122.4701 | 60.2234 | -0.20599 | 122.4564 | -0.073242 | 60.2234 | 122.2733 | 122.4701 | -122.7127 | -122.7539
364.0625 | 122.7448 | -60.6857 | 61.9308 | -0.32806 | 0.011828 | 0.019512 | 0.0025807 | 0.065933 | -0.0025123 | 0.06938 | -60.791 | 61.8668 | -60.8597 | -60.8551 | 61.4731 | -0.65002 | -0.60425 | -0.49896 | 61.821 | -60.9467 | -0.17395 | -0.064087 | -0.10529 | -0.16937 | -0.45776 | -0.26093 | -0.10986 | 0.068664 | 60.0815 | 60.1868 | 122.1588 | 122.5525 | -0.10529 | 122.5067 | 60.0357 | -0.26093 | 122.5525 | -0.10529 | 60.0357 | 122.1588 | 122.5067 | -122.7905 | -122.8775
365.0781 | 122.7402 | -60.6857 | 61.8942 | -0.038147 | 0.01311 | 0.019726 | 0.0059985 | 0.068069 | -0.00037588 | 0.067244 | -60.759 | 61.8439 | -60.8459 | -60.9009 | 61.5234 | -0.5722 | -0.70038 | -0.60425 | 61.8164 | -60.8917 | -0.16022 | -0.050354 | -0.073242 | -0.21515 | -0.37079 | -0.20599 | -0.07782 | 0.086975 | 59.9854 | 60.0815 | 122.2092 | 122.5296 | -0.073242 | 122.5021 | 60.1135 | -0.20599 | 122.5296 | -0.073242 | 60.1135 | 122.2092 | 122.5021 | -122.7402 | -122.786
366.0625 | 122.6898 | -60.7315 | 61.8301 | 0.10681 | 0.014605 | 0.013958 | 0.0051441 | 0.068283 | 0.00090572 | 0.069808 | -60.8185 | 61.8118 | -60.8871 | -60.9512 | 61.5143 | -0.62714 | -0.75989 | -0.67291 | 61.8439 | -60.9421 | -0.15564 | -0.01831 | -0.086975 | -0.21973 | -0.31586 | -0.21057 | 0.013733 | 0.068665 | 59.9716 | 60.0586 | 122.2458 | 122.5433 | -0.086975 | 122.5754 | 60.1044 | -0.21057 | 122.5433 | -0.086975 | 60.1044 | 122.2458 | 122.5754 | -122.7173 | -122.7722
367.0625 | 122.7768 | -60.704 | 61.8896 | -0.31281 | 0.013537 | 0.016094 | 0.0032215 | 0.069778 | 0.00047852 | 0.067031 | -60.7498 | 61.8668 | -60.8551 | -60.8551 | 61.5692 | -0.51727 | -0.6546 | -0.5127 | 61.8393 | -60.8917 | -0.15106 | -0.022888 | -0.045776 | -0.15106 | -0.32043 | -0.18768 | -0.050354 | 0.10529 | 60.0494 | 60.1913 | 122.2733 | 122.5708 | -0.045776 | 122.5433 | 60.1868 | -0.18768 | 122.5708 | -0.045776 | 60.1868 | 122.2733 | 122.5433 | -122.7448 | -122.7814
368.2188 | 122.7402 | -60.6995 | 61.8805 | -0.015259 | 0.014605 | 0.021221 | 0.0042895 | 0.068283 | -0.00037588 | 0.06874 | -60.8047 | 61.8942 | -60.8459 | -60.9375 | 61.496 | -0.64545 | -0.70953 | -0.69122 | 61.8347 | -60.9283 | -0.14648 | 0.013733 | -0.10529 | -0.23804 | -0.38452 | -0.22888 | -0.045776 | 0.041198 | 59.9899 | 60.0082 | 122.1954 | 122.5937 | -0.10529 | 122.5342 | 60.054 | -0.22888 | 122.5937 | -0.10529 | 60.054 | 122.1954 | 122.5342 | -122.7264 | -122.8088
369.0625 | 122.7905 | -60.6445 | 61.9171 | -0.28229 | 0.013324 | 0.012676 | -0.0025463 | 0.066146 | 0.00026492 | 0.069167 | -60.7361 | 61.7981 | -60.8322 | -60.8139 | 61.615 | -0.47607 | -0.67749 | -0.50354 | 61.8393 | -60.8551 | -0.18768 | -0.11902 | -0.091553 | -0.16937 | -0.30212 | -0.21057 | -0.07782 | 0.09613 | 59.967 | 60.141 | 122.2595 | 122.4426 | -0.091553 | 122.4838 | 60.1685 | -0.21057 | 122.4426 | -0.091553 | 60.1685 | 122.2595 | 122.4838 | -122.7493 | -122.7722
370.5 | 122.85 | -60.6537 | 61.8668 | 0.24414 | 0.011615 | 0.013317 | -0.0029735 | 0.064651 | 5.1318e-05 | 0.069808 | -60.7773 | 61.7615 | -60.8322 | -60.8551 | 61.5967 | -0.55847 | -0.84686 | -0.55389 | 61.7981 | -60.8414 | -0.17853 | -0.10529 | -0.1236 | -0.20142 | -0.27008 | -0.18768 | -0.068664 | 0.054931 | 59.8068 | 60.0998 | 122.2504 | 122.4152 | -0.1236 | 122.4518 | 60.0952 | -0.18768 | 122.4152 | -0.1236 | 60.0952 | 122.2504 | 122.4518 | -122.699 | -122.7081
371.0781 | 122.7951 | -60.6537 | 61.9217 | -0.19836 | 0.01311 | 0.014385 | 0.0040759 | 0.066574 | -0.0029395 | 0.067244 | -60.7361 | 61.853 | -60.8276 | -60.8185 | 61.5829 | -0.53101 | -0.6958 | -0.53558 | 61.8851 | -60.8597 | -0.17395 | -0.068665 | -0.082397 | -0.16479 | -0.33875 | -0.20599 | -0.036621 | 0.091553 | 59.9579 | 60.1181 | 122.2366 | 122.5067 | -0.082397 | 122.5388 | 60.1227 | -0.20599 | 122.5067 | -0.082397 | 60.1227 | 122.2366 | 122.5388 | -122.7493 | -122.7814
375.7812 | 122.7859 | -60.6583 | 61.94 | -0.14496 | 0.012469 | 0.018231 | 0.0051441 | 0.067642 | -0.00080328 | 0.068953 | -60.6903 | 61.9034 | -60.8276 | -60.8002 | 61.6058 | -0.58594 | -0.79651 | -0.59052 | 61.8576 | -60.8917 | -0.16937 | -0.036621 | -0.032044 | -0.14191 | -0.33417 | -0.23346 | -0.082397 | 0.13733 | 59.8618 | 60.0677 | 122.2641 | 122.5616 | -0.032044 | 122.5159 | 60.0723 | -0.23346 | 122.5616 | -0.032044 | 60.0723 | 122.2641 | 122.5159 | -122.7676 | -122.8317
376.3594 | 122.7722 | -60.64 | 61.94 | -0.29755 | 0.012683 | 0.010113 | -0.0014783 | 0.065505 | -0.0018713 | 0.068312 | -60.7224 | 61.8393 | -60.8139 | -60.8414 | 61.5921 | -0.58594 | -0.70038 | -0.56763 | 61.8622 | -60.8597 | -0.17395 | -0.10071 | -0.082397 | -0.20142 | -0.3479 | -0.21973 | -0.077819 | 0.091553 | 59.9396 | 60.0723 | 122.2321 | 122.4792 | -0.082397 | 122.5021 | 60.054 | -0.21973 | 122.4792 | -0.082397 | 60.054 | 122.2321 | 122.5021 | -122.7539 | -122.7997
377.0625 | 122.7722 | -60.6537 | 61.9263 | 0.10681 | 0.013965 | 0.016522 | 0.0015125 | 0.066787 | 0.00069212 | 0.066603 | -60.7681 | 61.8805 | -60.8368 | -60.8871 | 61.5555 | -0.6958 | -0.91095 | -0.73242 | 61.8118 | -60.9238 | -0.18311 | -0.045777 | -0.11444 | -0.23346 | -0.37079 | -0.27008 | -0.11444 | 0.068665 | 59.7427 | 59.9213 | 122.2092 | 122.5342 | -0.11444 | 122.4655 | 59.9579 | -0.27008 | 122.5342 | -0.11444 | 59.9579 | 122.2092 | 122.4655 | -122.7631 | -122.85
378.3594 | 122.7493 | -60.6628 | 61.9354 | 0.19836 | 0.012469 | 0.014813 | 0.0010853 | 0.066574 | 0.00069212 | 0.067885 | -60.7544 | 61.8988 | -60.8185 | -60.8688 | 61.5692 | -0.61798 | -0.73242 | -0.63629 | 61.8942 | -60.8734 | -0.15564 | -0.036621 | -0.091553 | -0.20599 | -0.36621 | -0.21057 | -0.041199 | 0.064086 | 59.9304 | 60.0266 | 122.2321 | 122.5616 | -0.091553 | 122.5571 | 60.0449 | -0.21057 | 122.5616 | -0.091553 | 60.0449 | 122.2321 | 122.5571 | -122.7539 | -122.8088
380.9375 | 122.7402 | -60.6079 | 61.9812 | -0.34332 | 0.014178 | 0.013317 | 0.0015125 | 0.067001 | -0.0012305 | 0.067458 | -60.7452 | 61.8668 | -60.8185 | -60.8505 | 61.5875 | -0.62256 | -0.72784 | -0.66834 | 61.8942 | -60.8368 | -0.21057 | -0.11444 | -0.13733 | -0.24262 | -0.39368 | -0.22888 | -0.086975 | 0.073242 | 59.8801 | 59.9396 | 122.1954 | 122.4747 | -0.13733 | 122.5021 | 59.9854 | -0.22888 | 122.4747 | -0.13733 | 59.9854 | 122.1954 | 122.5021 | -122.7997 | -122.818
381.3906 | 122.8226 | -60.6171 | 61.9354 | 0.72479 | 0.0077695 | 0.014385 | -0.0014783 | 0.067642 | 0.0015467 | 0.068312 | -60.6125 | 61.8073 | -60.8002 | -60.7407 | 61.7203 | -0.55847 | -0.9201 | -0.53558 | 61.853 | -60.7956 | -0.18311 | -0.12817 | 0.004577 | -0.1236 | -0.21515 | -0.17853 | -0.082398 | 0.18768 | 59.697 | 60.0815 | 122.3373 | 122.4243 | 0.004577 | 122.4701 | 60.0586 | -0.17853 | 122.4243 | 0.004577 | 60.0586 | 122.3373 | 122.4701 | -122.7356 | -122.731
382.0625 | 122.8592 | -60.5804 | 61.9171 | -0.22125 | 0.012042 | 0.016522 | -0.00083733 | 0.067001 | -0.00080328 | 0.067244 | -60.6674 | 61.7981 | -60.7956 | -60.7361 | 61.6699 | -0.5722 | -0.90637 | -0.55847 | 61.8301 | -60.8002 | -0.21515 | -0.11902 | -0.086975 | -0.15564 | -0.24719 | -0.21973 | -0.086975 | 0.12817 | 59.6741 | 60.022 | 122.2504 | 122.3785 | -0.086975 | 122.4106 | 60.0082 | -0.21973 | 122.3785 | -0.086975 | 60.0082 | 122.2504 | 122.4106 | -122.7127 | -122.7173
383.0781 | 122.8226 | -60.6354 | 61.8851 | 0.1297 | 0.011401 | 0.018871 | 0.00087167 | 0.064865 | -0.00058968 | 0.068526 | -60.7086 | 61.7615 | -60.8047 | -60.8322 | 61.615 | -0.68665 | -1.0254 | -0.71411 | 61.8118 | -60.8414 | -0.16937 | -0.1236 | -0.073242 | -0.19684 | -0.27008 | -0.20599 | -0.073242 | 0.096131 | 59.61 | 59.9213 | 122.2504 | 122.3969 | -0.073242 | 122.4472 | 59.9487 | -0.20599 | 122.3969 | -0.073242 | 59.9487 | 122.2504 | 122.4472 | -122.6898 | -122.7264
384.125 | 122.8409 | -60.6354 | 61.9125 | 0.022888 | 0.01311 | 0.015881 | -0.00062373 | 0.065505 | -0.00037588 | 0.068953 | -60.7269 | 61.8118 | -60.8002 | -60.8093 | 61.6058 | -0.67291 | -0.99335 | -0.71411 | 61.8118 | -60.8322 | -0.16479 | -0.10071 | -0.091553 | -0.17395 | -0.3067 | -0.19684 | -0.10071 | 0.073242 | 59.642 | 59.9213 | 122.2412 | 122.4472 | -0.091553 | 122.4472 | 59.9625 | -0.19684 | 122.4472 | -0.091553 | 59.9625 | 122.2412 | 122.4472 | -122.7127 | -122.7448
385.1719 | 122.8455 | -60.6262 | 61.9125 | -0.12207 | 0.011188 | 0.01289 | 0.00065787 | 0.061874 | -0.0020849 | 0.06874 | -60.7178 | 61.7844 | -60.7681 | -60.7636 | 61.6699 | -0.61798 | -1.0025 | -0.62714 | 61.821 | -60.7864 | -0.14191 | -0.12817 | -0.091552 | -0.13733 | -0.24262 | -0.16022 | -0.091553 | 0.050354 | 59.6237 | 59.9991 | 122.2961 | 122.4106 | -0.091552 | 122.4472 | 60.0082 | -0.16022 | 122.4106 | -0.091552 | 60.0082 | 122.2961 | 122.4472 | -122.6807 | -122.699
386.125 | 122.8455 | -60.6216 | 61.8805 | 0.076294 | 0.0094785 | 0.015026 | 0.0045033 | 0.063796 | -0.0012305 | 0.068953 | -60.6812 | 61.7889 | -60.7819 | -60.7636 | 61.6425 | -0.68207 | -1.1032 | -0.71869 | 61.7889 | -60.8551 | -0.16022 | -0.091553 | -0.059509 | -0.14191 | -0.23804 | -0.23346 | -0.091553 | 0.10071 | 59.5184 | 59.903 | 122.2641 | 122.4106 | -0.059509 | 122.4106 | 59.9396 | -0.23346 | 122.4106 | -0.059509 | 59.9396 | 122.2641 | 122.4106 | -122.6624 | -122.7356
387.0625 | 122.7493 | -60.6308 | 61.9492 | -0.36621 | 0.012469 | 0.013317 | 0.0010853 | 0.062087 | -0.0010169 | 0.066176 | -60.6949 | 61.8347 | -60.759 | -60.8047 | 61.6104 | -0.67291 | -0.80109 | -0.68665 | 61.8851 | -60.8276 | -0.12817 | -0.11444 | -0.064087 | -0.17395 | -0.33874 | -0.19684 | -0.064087 | 0.064087 | 59.8297 | 59.9442 | 122.2412 | 122.4655 | -0.064087 | 122.5159 | 59.9579 | -0.19684 | 122.4655 | -0.064087 | 59.9579 | 122.2412 | 122.5159 | -122.7081 | -122.7768
388.0938 | 122.8226 | -60.6079 | 61.9308 | 0.038147 | 0.012256 | 0.016094 | 0.00087167 | 0.06166 | 0.00047852 | 0.068526 | -60.7132 | 61.7844 | -60.8002 | -60.8002 | 61.6058 | -0.72327 | -1.0345 | -0.75989 | 61.8118 | -60.8276 | -0.19226 | -0.14648 | -0.10529 | -0.19226 | -0.32501 | -0.21973 | -0.11902 | 0.086975 | 59.5734 | 59.848 | 122.2137 | 122.3923 | -0.10529 | 122.4197 | 59.8846 | -0.21973 | 122.3923 | -0.10529 | 59.8846 | 122.2137 | 122.4197 | -122.731 | -122.7585
389.125 | 122.8821 | -60.5759 | 61.9217 | -0.18311 | 0.013324 | 0.012249 | -0.0010509 | 0.064224 | -0.0014441 | 0.067031 | -60.6491 | 61.821 | -60.7864 | -60.7224 | 61.6882 | -0.64545 | -1.0437 | -0.6546 | 61.8439 | -60.7727 | -0.21057 | -0.10071 | -0.073242 | -0.14648 | -0.23346 | -0.19684 | -0.07782 | 0.13733 | 59.5322 | 59.9213 | 122.2641 | 122.3969 | -0.073242 | 122.4197 | 59.9304 | -0.19684 | 122.3969 | -0.073242 | 59.9304 | 122.2641 | 122.4197 | -122.7081 | -122.6944
390.0625 | 122.8088 | -60.5804 | 61.9812 | -0.28992 | 0.0092649 | 0.016949 | 0.0015125 | 0.062087 | -0.0025123 | 0.067885 | -60.6491 | 61.8118 | -60.7956 | -60.7315 | 61.6608 | -0.65918 | -0.91553 | -0.6546 | 61.8622 | -60.7773 | -0.21515 | -0.16937 | -0.068665 | -0.15106 | -0.32043 | -0.19684 | -0.11902 | 0.14648 | 59.6649 | 59.9258 | 122.2412 | 122.3923 | -0.068665 | 122.4426 | 59.9213 | -0.19684 | 122.3923 | -0.068665 | 59.9213 | 122.2412 | 122.4426 | -122.7768 | -122.7585
391.0625 | 122.8775 | -60.5667 | 61.9354 | -0.25177 | 0.010547 | 0.016949 | 0.0010853 | 0.063156 | -0.0033667 | 0.068099 | -60.6216 | 61.8164 | -60.7224 | -60.5576 | 61.972 | -0.39825 | -1.3046 | -0.75073 | 61.853 | -60.8139 | -0.15564 | -0.11902 | -0.054932 | 0.009155 | 0.036621 | -0.24719 | -0.082398 | 0.10071 | 59.2621 | 59.816 | 122.5388 | 122.3831 | -0.054932 | 122.4197 | 60.1685 | -0.24719 | 122.3831 | -0.054932 | 60.1685 | 122.5388 | 122.4197 | -122.6578 | -122.7493
392.125 | 122.9004 | -60.5804 | 61.9537 | -0.31281 | 0.011188 | 0.013317 | 1.7066e-05 | 0.065505 | -0.0016577 | 0.069808 | -60.64 | 61.7889 | -60.7681 | -60.6812 | 61.7157 | -0.62256 | -1.0712 | -0.61798 | 61.8301 | -60.7773 | -0.18768 | -0.1648 | -0.05951 | -0.10071 | -0.23804 | -0.19684 | -0.1236 | 0.12817 | 59.5093 | 59.9625 | 122.2961 | 122.3694 | -0.05951 | 122.4106 | 59.9579 | -0.19684 | 122.3694 | -0.05951 | 59.9579 | 122.2961 | 122.4106 | -122.7219 | -122.731
393.0781 | 122.7631 | -60.6262 | 61.9446 | -0.54932 | 0.014178 | 0.014172 | 0.0062121 | 0.065078 | -0.0016577 | 0.068312 | -60.7132 | 61.8805 | -60.8002 | -60.8368 | 61.5463 | -0.85602 | -1.0117 | -0.87433 | 61.8347 | -60.8505 | -0.17395 | -0.064087 | -0.086975 | -0.21057 | -0.39825 | -0.2243 | -0.10986 | 0.086975 | 59.6146 | 59.7519 | 122.1725 | 122.5067 | -0.086975 | 122.4609 | 59.7702 | -0.2243 | 122.5067 | -0.086975 | 59.7702 | 122.1725 | 122.4609 | -122.7448 | -122.7951
394.2188 | 122.7127 | -60.6079 | 61.9766 | -0.30518 | 0.010974 | 0.015881 | 0.0027943 | 0.065078 | -0.0012305 | 0.067458 | -60.6674 | 61.9125 | -60.759 | -60.759 | 61.6104 | -0.74158 | -0.89722 | -0.75989 | 61.9125 | -60.8459 | -0.15106 | -0.064087 | -0.059509 | -0.15106 | -0.36621 | -0.23804 | -0.064087 | 0.091553 | 59.7107 | 59.848 | 122.2183 | 122.5204 | -0.059509 | 122.5204 | 59.8663 | -0.23804 | 122.5204 | -0.059509 | 59.8663 | 122.2183 | 122.5204 | -122.7356 | -122.8226
395.0938 | 122.8363 | -60.5804 | 61.9171 | 0.16022 | 0.011615 | 0.019726 | 0.0038623 | 0.066574 | -0.00080328 | 0.069594 | -60.6308 | 61.8256 | -60.7819 | -60.7224 | 61.7386 | -0.76904 | -1.4099 | -0.69122 | 61.7981 | -60.8185 | -0.20142 | -0.091552 | -0.050354 | -0.14191 | -0.17853 | -0.23804 | -0.11902 | 0.15106 | 59.1705 | 59.8892 | 122.319 | 122.406 | -0.050354 | 122.3785 | 59.8114 | -0.23804 | 122.406 | -0.050354 | 59.8114 | 122.319 | 122.3785 | -122.699 | -122.7356
396.0625 | 122.7631 | -60.5804 | 61.9858 | -0.28229 | 0.01311 | 0.01759 | 0.0025807 | 0.064865 | -0.0014441 | 0.070449 | -60.672 | 61.8896 | -60.7636 | -60.791 | 61.6516 | -0.74616 | -0.90179 | -0.78735 | 61.9263 | -60.7773 | -0.18311 | -0.096131 | -0.091553 | -0.21057 | -0.33417 | -0.19684 | -0.059509 | 0.091553 | 59.6786 | 59.7931 | 122.2321 | 122.4701 | -0.091553 | 122.5067 | 59.8343 | -0.19684 | 122.4701 | -0.091553 | 59.8343 | 122.2321 | 122.5067 | -122.7493 | -122.7631
397.0625 | 122.7722 | -60.6171 | 61.9629 | 0.068664 | 0.01546 | 0.01289 | 0.0068531 | 0.066787 | 0.00026492 | 0.067244 | -60.704 | 61.9217 | -60.7681 | -60.8002 | 61.5875 | -0.85144 | -1.1078 | -0.91553 | 61.8668 | -60.8368 | -0.15106 | -0.041199 | -0.086976 | -0.18311 | -0.37537 | -0.21973 | -0.096131 | 0.064086 | 59.5093 | 59.7015 | 122.2046 | 122.5388 | -0.086976 | 122.4838 | 59.7656 | -0.21973 | 122.5388 | -0.086976 | 59.7656 | 122.2046 | 122.4838 | -122.731 | -122.7997
398.0625 | 122.8592 | -60.5484 | 61.9629 | -0.19836 | 0.0090511 | 0.015026 | -0.0010509 | 0.065719 | 0.00047852 | 0.066176 | -60.6171 | 61.8256 | -60.7636 | -60.6812 | 61.7294 | -0.67291 | -1.0941 | -0.66834 | 61.8118 | -60.7681 | -0.21515 | -0.13733 | -0.068664 | -0.13275 | -0.23346 | -0.21973 | -0.15106 | 0.14649 | 59.4543 | 59.8801 | 122.2778 | 122.374 | -0.068664 | 122.3602 | 59.8755 | -0.21973 | 122.374 | -0.068664 | 59.8755 | 122.2778 | 122.3602 | -122.7264 | -122.731
399.9844 | 122.8088 | -60.6079 | 61.9583 | 0.022888 | 0.010547 | 0.016094 | -0.00062373 | 0.065505 | -0.00037588 | 0.069594 | -60.6812 | 61.8347 | -60.7452 | -60.7864 | 61.6425 | -0.84228 | -1.1581 | -0.86517 | 61.8439 | -60.791 | -0.13733 | -0.1236 | -0.073242 | -0.17853 | -0.31586 | -0.18311 | -0.11444 | 0.064087 | 59.4498 | 59.7427 | 122.2504 | 122.4426 | -0.073242 | 122.4518 | 59.7656 | -0.18311 | 122.4426 | -0.073242 | 59.7656 | 122.2504 | 122.4518 | -122.7036 | -122.7493
400.9531 | 122.7814 | -60.5759 | 61.9766 | -0.16022 | 0.012683 | 0.01994 | 0.0089893 | 0.065292 | -0.0018713 | 0.067885 | -60.6033 | 61.94 | -60.7544 | -60.7269 | 61.6425 | -0.78735 | -1.0666 | -0.84686 | 61.8942 | -60.8185 | -0.17853 | -0.036622 | -0.027466 | -0.15106 | -0.33417 | -0.24261 | -0.082398 | 0.15106 | 59.5093 | 59.729 | 122.2183 | 122.5159 | -0.027466 | 122.4701 | 59.7885 | -0.24261 | 122.5159 | -0.027466 | 59.7885 | 122.2183 | 122.4701 | -122.731 | -122.7951
401.4062 | 122.7814 | -60.6033 | 61.9858 | -0.24414 | 0.014605 | 0.013745 | 0.0059985 | 0.067642 | -0.0027259 | 0.066603 | -60.6354 | 61.9446 | -60.791 | -60.7407 | 61.6653 | -0.78735 | -1.0071 | -0.82855 | 61.9125 | -60.8093 | -0.18768 | -0.041199 | -0.032043 | -0.13733 | -0.32044 | -0.20599 | -0.073242 | 0.15564 | 59.5963 | 59.7748 | 122.2687 | 122.5479 | -0.032043 | 122.5159 | 59.816 | -0.20599 | 122.5479 | -0.032043 | 59.816 | 122.2687 | 122.5159 | -122.7768 | -122.7951
402.0625 | 122.7631 | -60.585 | 61.9766 | -0.32043 | 0.010974 | 0.016522 | -0.0010509 | 0.065505 | 5.1318e-05 | 0.066603 | -60.6537 | 61.908 | -60.7452 | -60.7636 | 61.647 | -0.80109 | -1.0208 | -0.82855 | 61.9354 | -60.759 | -0.16022 | -0.068665 | -0.068665 | -0.17853 | -0.32959 | -0.17395 | -0.041199 | 0.091552 | 59.5642 | 59.7565 | 122.2321 | 122.493 | -0.068665 | 122.5204 | 59.7839 | -0.17395 | 122.493 | -0.068665 | 59.7839 | 122.2321 | 122.5204 | -122.7219 | -122.7356
403.0625 | 122.7493 | -60.5942 | 61.9995 | -0.28992 | 0.012683 | 0.013745 | 0.0038623 | 0.066146 | -0.0012305 | 0.067671 | -60.6812 | 61.9354 | -60.7727 | -60.7727 | 61.6379 | -0.80566 | -0.98419 | -0.85144 | 61.9263 | -60.8047 | -0.17853 | -0.064087 | -0.086975 | -0.17853 | -0.36163 | -0.21057 | -0.073242 | 0.091553 | 59.61 | 59.7427 | 122.2321 | 122.5296 | -0.086975 | 122.5204 | 59.7885 | -0.21057 | 122.5296 | -0.086975 | 59.7885 | 122.2321 | 122.5204 | -122.7722 | -122.8043
404.0625 | 122.6852 | -60.5942 | 62.0087 | -0.33569 | 0.012042 | 0.013958 | 0.0017261 | 0.064865 | 0.00069212 | 0.069167 | -60.704 | 61.9537 | -60.7864 | -60.8047 | 61.6196 | -0.8194 | -0.9613 | -0.87433 | 61.8942 | -60.8093 | -0.19226 | -0.054932 | -0.10986 | -0.21057 | -0.3891 | -0.21515 | -0.11444 | 0.082397 | 59.6329 | 59.7198 | 122.2137 | 122.5479 | -0.10986 | 122.4884 | 59.7748 | -0.21515 | 122.5479 | -0.10986 | 59.7748 | 122.2137 | 122.4884 | -122.7951 | -122.818
405.125 | 122.8317 | -60.5484 | 61.9125 | -0.27466 | 0.0075559 | 0.014599 | -0.0038281 | 0.066787 | -0.0022987 | 0.066817 | -60.6079 | 61.8118 | -60.7498 | -60.672 | 61.7523 | -0.81024 | -0.75073 | -0.51727 | 61.94 | -60.7407 | -0.20142 | -0.10071 | -0.059509 | -0.1236 | -0.16022 | -0.19226 | 0.027465 | 0.14191 | 59.7977 | 60.0311 | 122.3007 | 122.3602 | -0.059509 | 122.4884 | 59.7382 | -0.19226 | 122.3602 | -0.059509 | 59.7382 | 122.3007 | 122.4884 | -122.6624 | -122.6532
406.0625 | 122.7356 | -60.5667 | 61.9949 | -0.29755 | 0.01076 | 0.014172 | 0.0042895 | 0.063369 | -0.00037588 | 0.069594 | -60.6903 | 61.9354 | -60.7498 | -60.791 | 61.6287 | -0.85144 | -0.97046 | -0.89264 | 61.9308 | -60.7956 | -0.18311 | -0.059509 | -0.1236 | -0.22431 | -0.36621 | -0.22888 | -0.064087 | 0.059509 | 59.5963 | 59.6741 | 122.1954 | 122.5021 | -0.1236 | 122.4976 | 59.7153 | -0.22888 | 122.5021 | -0.1236 | 59.7153 | 122.1954 | 122.4976 | -122.7448 | -122.7905
407.125 | 122.818 | -60.553 | 61.9995 | -0.31281 | 0.0094785 | 0.0098994 | 0.0012989 | 0.06401 | -0.0014441 | 0.070662 | -60.6216 | 61.8805 | -60.7224 | -60.7315 | 61.6928 | -0.79193 | -1.0986 | -0.79193 | 61.8851 | -60.7819 | -0.16937 | -0.11902 | -0.068664 | -0.17853 | -0.3067 | -0.22888 | -0.11444 | 0.10071 | 59.4543 | 59.761 | 122.2458 | 122.4335 | -0.068664 | 122.4381 | 59.761 | -0.22888 | 122.4335 | -0.068664 | 59.761 | 122.2458 | 122.4381 | -122.7219 | -122.7814
408.0625 | 122.7905 | -60.5713 | 61.972 | -0.22888 | 0.015246 | 0.016522 | 0.0062121 | 0.068283 | -0.0016577 | 0.069167 | -60.6033 | 61.9537 | -60.7361 | -60.7315 | 61.647 | -0.85602 | -1.1215 | -0.89722 | 61.9125 | -60.8047 | -0.16479 | -0.018311 | -0.032044 | -0.16022 | -0.32501 | -0.23346 | -0.059509 | 0.13275 | 59.4498 | 59.6741 | 122.2183 | 122.525 | -0.032044 | 122.4838 | 59.7153 | -0.23346 | 122.525 | -0.032044 | 59.7153 | 122.2183 | 122.4838 | -122.7081 | -122.7768
409.125 | 122.7631 | -60.5804 | 61.9995 | -1.3809 | 0.014605 | 0.016094 | 0.0010853 | 0.067855 | -0.0022987 | 0.068526 | -60.7407 | 61.9217 | -60.7864 | -60.7956 | 61.6104 | -0.89722 | -1.0254 | -0.92926 | 61.9629 | -60.759 | -0.20599 | -0.07782 | -0.16022 | -0.21515 | -0.3891 | -0.17853 | -0.036621 | 0.045776 | 59.5551 | 59.6512 | 122.1909 | 122.5021 | -0.16022 | 122.5433 | 59.6832 | -0.17853 | 122.5021 | -0.16022 | 59.6832 | 122.1909 | 122.5433 | -122.7859 | -122.7585
410.1094 | 122.8317 | -60.553 | 61.9629 | 0.076294 | 0.012897 | 0.013745 | -0.0038281 | 0.066787 | -0.0010169 | 0.069808 | -60.6628 | 61.8347 | -60.7544 | -60.7544 | 61.6928 | -0.88348 | -1.2543 | -0.90637 | 61.8713 | -60.7636 | -0.20142 | -0.12817 | -0.10986 | -0.20142 | -0.27008 | -0.21057 | -0.091553 | 0.091553 | 59.2987 | 59.6466 | 122.2458 | 122.3877 | -0.10986 | 122.4243 | 59.6695 | -0.21057 | 122.3877 | -0.10986 | 59.6695 | 122.2458 | 122.4243 | -122.7173 | -122.7264
411.1562 | 122.8134 | -60.5576 | 61.9446 | -0.038147 | 0.011615 | 0.016522 | -0.0029735 | 0.062301 | -0.00058968 | 0.067244 | -60.6766 | 61.8942 | -60.7269 | -60.7681 | 61.6425 | -0.93384 | -1.2772 | -0.97046 | 61.8713 | -60.7864 | -0.16937 | -0.050354 | -0.11902 | -0.21057 | -0.30212 | -0.22888 | -0.073242 | 0.050354 | 59.2804 | 59.5871 | 122.2 | 122.4518 | -0.11902 | 122.4289 | 59.6237 | -0.22888 | 122.4518 | -0.11902 | 59.6237 | 122.2 | 122.4289 | -122.6715 | -122.731
412.0625 | 122.7402 | -60.5759 | 62.0361 | -0.33569 | 0.011401 | 0.016094 | 0.0040759 | 0.060592 | 0.00047852 | 0.068312 | -60.6537 | 61.9354 | -60.7361 | -60.7681 | 61.6333 | -0.92468 | -1.0895 | -0.9613 | 61.9217 | -60.791 | -0.16022 | -0.10071 | -0.07782 | -0.19226 | -0.40283 | -0.21515 | -0.11444 | 0.082397 | 59.4864 | 59.6146 | 122.2092 | 122.5113 | -0.07782 | 122.4976 | 59.6512 | -0.21515 | 122.5113 | -0.07782 | 59.6512 | 122.2092 | 122.4976 | -122.7722 | -122.8271
413.125 | 122.7768 | -60.5576 | 61.9904 | -0.11444 | 0.014392 | 0.018017 | 0.0051441 | 0.06401 | 5.1318e-05 | 0.067885 | -60.6079 | 61.9629 | -60.7361 | -60.7086 | 61.6516 | -0.93384 | -1.2222 | -0.97046 | 61.9125 | -60.791 | -0.17853 | -0.027465 | -0.050354 | -0.15106 | -0.33874 | -0.23346 | -0.077819 | 0.12817 | 59.3353 | 59.5871 | 122.2092 | 122.5204 | -0.050354 | 122.4701 | 59.6237 | -0.23346 | 122.5204 | -0.050354 | 59.6237 | 122.2092 | 122.4701 | -122.7264 | -122.7814
414.0625 | 122.7676 | -60.5713 | 62.0178 | -0.22888 | 0.013537 | 0.014172 | 0.0049305 | 0.066574 | -0.0016577 | 0.068099 | -60.6354 | 61.9629 | -60.7407 | -60.7224 | 61.647 | -0.95215 | -1.1536 | -0.98419 | 61.94 | -60.7956 | -0.16937 | -0.054931 | -0.064087 | -0.15106 | -0.37079 | -0.2243 | -0.07782 | 0.10529 | 59.4177 | 59.5871 | 122.2183 | 122.5342 | -0.064087 | 122.5113 | 59.6191 | -0.2243 | 122.5342 | -0.064087 | 59.6191 | 122.2183 | 122.5113 | -122.7585 | -122.8134
415.1562 | 122.8363 | -60.5576 | 61.9537 | 0.11444 | 0.013965 | 0.018444 | 0.0017261 | 0.070419 | -0.00016228 | 0.069808 | -60.6537 | 61.9354 | -60.7727 | -60.7544 | 61.6333 | -1.0208 | -1.3824 | -1.0803 | 61.9034 | -60.7956 | -0.21515 | -0.01831 | -0.096131 | -0.19684 | -0.32043 | -0.23804 | -0.050354 | 0.11902 | 59.1751 | 59.4772 | 122.1909 | 122.493 | -0.096131 | 122.4609 | 59.5367 | -0.23804 | 122.493 | -0.096131 | 59.5367 | 122.1909 | 122.4609 | -122.7264 | -122.7493
416.0625 | 122.8043 | -60.5988 | 62.0178 | -0.28229 | 0.014392 | 0.018658 | 0.0042895 | 0.065719 | -0.0018713 | 0.068526 | -60.6354 | 61.9675 | -60.7452 | -60.7132 | 61.6562 | -0.96588 | -1.1856 | -0.99792 | 61.94 | -60.7773 | -0.14648 | -0.050354 | -0.036621 | -0.11444 | -0.36163 | -0.17853 | -0.07782 | 0.10986 | 59.4131 | 59.6008 | 122.2549 | 122.5662 | -0.036621 | 122.5388 | 59.6329 | -0.17853 | 122.5662 | -0.036621 | 59.6329 | 122.2549 | 122.5388 | -122.7631 | -122.7951
417.125 | 122.8226 | -60.5621 | 61.9904 | -0.21362 | 0.014819 | 0.018231 | 0.0066395 | 0.069778 | -0.0033667 | 0.070021 | -60.6079 | 61.9995 | -60.7361 | -60.7178 | 61.6608 | -0.95673 | -1.2772 | -1.0208 | 61.94 | -60.7956 | -0.17395 | 0.009156 | -0.045776 | -0.15564 | -0.32959 | -0.23346 | -0.050354 | 0.12817 | 59.285 | 59.5413 | 122.2229 | 122.5616 | -0.045776 | 122.5021 | 59.6054 | -0.23346 | 122.5616 | -0.045776 | 59.6054 | 122.2229 | 122.5021 | -122.7264 | -122.7859
418.0625 | 122.731 | -60.5759 | 62.027 | -0.28229 | 0.012897 | 0.01289 | 0.0023669 | 0.070205 | 0.00047852 | 0.068526 | -60.5301 | 62.0224 | -60.7315 | -60.7773 | 61.6287 | -1.0025 | -1.1948 | -1.0345 | 61.972 | -60.7773 | -0.15564 | -0.004578 | 0.045777 | -0.20142 | -0.39825 | -0.20142 | -0.054932 | 0.20142 | 59.3811 | 59.5413 | 122.2046 | 122.5983 | 0.045777 | 122.5479 | 59.5734 | -0.20142 | 122.5983 | 0.045777 | 59.5734 | 122.2046 | 122.5479 | -122.7585 | -122.8043
419.125 | 122.7402 | -60.5484 | 62.0224 | -0.1297 | 0.012256 | 0.01759 | 0.0040759 | 0.067428 | -0.0037939 | 0.06938 | -60.5942 | 61.9492 | -60.7361 | -60.704 | 61.6837 | -1.0117 | -1.3092 | -1.0529 | 61.9629 | -60.7452 | -0.18768 | -0.073242 | -0.045776 | -0.15564 | -0.33874 | -0.19684 | -0.059509 | 0.14191 | 59.2392 | 59.4955 | 122.2321 | 122.4976 | -0.045776 | 122.5113 | 59.5367 | -0.19684 | 122.4976 | -0.045776 | 59.5367 | 122.2321 | 122.5113 | -122.7585 | -122.7676
420.0625 | 122.7814 | -60.5576 | 61.9812 | 0.0076294 | 0.014178 | 0.015667 | 0.0032215 | 0.06871 | -0.00037588 | 0.068099 | -60.6537 | 61.9675 | -60.7636 | -60.7864 | 61.6287 | -1.1169 | -1.3733 | -1.1673 | 61.9537 | -60.791 | -0.20599 | -0.013733 | -0.096131 | -0.22888 | -0.35248 | -0.23346 | -0.027466 | 0.10986 | 59.1843 | 59.3903 | 122.1863 | 122.525 | -0.096131 | 122.5113 | 59.4406 | -0.23346 | 122.525 | -0.096131 | 59.4406 | 122.1863 | 122.5113 | -122.7448 | -122.7722
421.125 | 122.731 | -60.5392 | 62.0316 | -0.091553 | 0.011828 | 0.01759 | 0.0051441 | 0.067214 | -0.0014441 | 0.06938 | -60.5988 | 61.9629 | -60.7269 | -60.7269 | 61.6379 | -1.0803 | -1.3275 | -1.1261 | 61.9583 | -60.7727 | -0.18768 | -0.068664 | -0.059509 | -0.18768 | -0.39368 | -0.23346 | -0.073242 | 0.12817 | 59.2117 | 59.4131 | 122.1771 | 122.5021 | -0.059509 | 122.4976 | 59.4589 | -0.23346 | 122.5021 | -0.059509 | 59.4589 | 122.1771 | 122.4976 | -122.7585 | -122.8043
422.0625 | 122.7905 | -60.5347 | 62.027 | -0.15259 | 0.013965 | 0.015881 | 0.0017261 | 0.069351 | -0.0012305 | 0.067885 | -60.5621 | 62.0178 | -60.6812 | -60.6903 | 61.6791 | -1.03 | -1.3458 | -1.0941 | 61.9904 | -60.7681 | -0.14648 | -0.009156 | -0.027466 | -0.15564 | -0.3479 | -0.23346 | -0.036622 | 0.11902 | 59.1888 | 59.4406 | 122.2137 | 122.5525 | -0.027466 | 122.525 | 59.5047 | -0.23346 | 122.5525 | -0.027466 | 59.5047 | 122.2137 | 122.525 | -122.7081 | -122.7951
423.0625 | 122.7997 | -60.5301 | 62.0316 | -0.14496 | 0.013965 | 0.02058 | 0.0042895 | 0.069137 | -0.0014441 | 0.067244 | -60.5713 | 61.9995 | -60.6949 | -60.6903 | 61.6837 | -1.0437 | -1.3687 | -1.0895 | 62.0041 | -60.7407 | -0.16479 | -0.032043 | -0.041199 | -0.16022 | -0.3479 | -0.21057 | -0.027466 | 0.1236 | 59.1614 | 59.4406 | 122.2137 | 122.5296 | -0.041199 | 122.5342 | 59.4864 | -0.21057 | 122.5296 | -0.041199 | 59.4864 | 122.2137 | 122.5342 | -122.7264 | -122.7722
424.0625 | 122.7676 | -60.5392 | 62.059 | -0.16022 | 0.016314 | 0.017376 | 0.0034351 | 0.069992 | -0.00016228 | 0.06938 | -60.5667 | 62.0361 | -60.7086 | -60.704 | 61.6837 | -1.062 | -1.3916 | -1.1169 | 61.9904 | -60.7727 | -0.16937 | -0.022888 | -0.027465 | -0.16479 | -0.37537 | -0.23346 | -0.068665 | 0.14191 | 59.1476 | 59.4223 | 122.2229 | 122.5754 | -0.027465 | 122.5296 | 59.4772 | -0.23346 | 122.5754 | -0.027465 | 59.4772 | 122.2229 | 122.5296 | -122.7676 | -122.8317
425.0625 | 122.7219 | -60.5484 | 62.0407 | -0.022888 | 0.013965 | 0.016949 | 0.0040759 | 0.069351 | -0.0018713 | 0.068526 | -60.6354 | 62.0453 | -60.6949 | -60.7727 | 61.5921 | -1.1948 | -1.387 | -1.268 | 61.9904 | -60.7727 | -0.14648 | 0.004578 | -0.086975 | -0.2243 | -0.44861 | -0.2243 | -0.050354 | 0.059509 | 59.1614 | 59.2804 | 122.1405 | 122.5937 | -0.086975 | 122.5388 | 59.3536 | -0.2243 | 122.5937 | -0.086975 | 59.3536 | 122.1405 | 122.5388 | -122.7356 | -122.8134
426.125 | 122.7951 | -60.5255 | 62.0453 | -0.076294 | 0.01311 | 0.016094 | 0.0025807 | 0.068496 | -0.0031531 | 0.070876 | -60.5804 | 61.9583 | -60.704 | -60.6903 | 61.702 | -1.1124 | -1.4282 | -1.1765 | 61.9949 | -60.7315 | -0.17853 | -0.086975 | -0.054931 | -0.1648 | -0.34332 | -0.20599 | -0.050354 | 0.1236 | 59.0973 | 59.3491 | 122.2275 | 122.4838 | -0.054931 | 122.5204 | 59.4131 | -0.20599 | 122.4838 | -0.054931 | 59.4131 | 122.2275 | 122.5204 | -122.7493 | -122.7768
427.0781 | 122.8546 | -60.4889 | 61.9995 | 0.18311 | 0.012256 | 0.017163 | -0.0021191 | 0.070846 | -0.0010169 | 0.072585 | -60.5392 | 61.9354 | -60.6583 | -60.672 | 61.734 | -1.1169 | -1.6525 | -1.1765 | 61.9217 | -60.7544 | -0.16937 | -0.064087 | -0.050354 | -0.1831 | -0.2655 | -0.2655 | -0.07782 | 0.11902 | 58.8364 | 59.3124 | 122.2229 | 122.4243 | -0.050354 | 122.4106 | 59.3719 | -0.2655 | 122.4243 | -0.050354 | 59.3719 | 122.2229 | 122.4106 | -122.6578 | -122.7539
428.125 | 122.7859 | -60.5164 | 62.0819 | -0.31281 | 0.012683 | 0.02058 | 0.0027943 | 0.067428 | -0.0027259 | 0.068953 | -60.5988 | 62.0178 | -60.7086 | -60.6949 | 61.6928 | -1.1261 | -1.3916 | -1.1627 | 61.9995 | -60.7315 | -0.19226 | -0.064087 | -0.082398 | -0.17853 | -0.3891 | -0.21515 | -0.082397 | 0.10986 | 59.1248 | 59.3536 | 122.2092 | 122.5342 | -0.082398 | 122.5159 | 59.3903 | -0.21515 | 122.5342 | -0.082398 | 59.3903 | 122.2092 | 122.5159 | -122.7905 | -122.8134
429.0625 | 122.7493 | -60.5484 | 62.0453 | 0.61798 | 0.015033 | 0.018658 | 0.0015125 | 0.068923 | 0.00090572 | 0.070449 | -60.6445 | 62.027 | -60.6903 | -60.7636 | 61.6287 | -1.2405 | -1.5335 | -1.3138 | 62.0087 | -60.7636 | -0.14191 | -0.01831 | -0.09613 | -0.21515 | -0.41656 | -0.21515 | -0.036621 | 0.045777 | 59.0149 | 59.2346 | 122.1771 | 122.5754 | -0.09613 | 122.5571 | 59.3079 | -0.21515 | 122.5754 | -0.09613 | 59.3079 | 122.1771 | 122.5571 | -122.7356 | -122.8088
430.3594 | 122.7493 | -60.5392 | 62.059 | -0.0076296 | 0.014178 | 0.01524 | 0.0027943 | 0.07106 | -0.00037588 | 0.068953 | -60.585 | 61.9812 | -60.6903 | -60.7407 | 61.6333 | -1.2543 | -1.4969 | -1.3321 | 61.9949 | -60.7452 | -0.15106 | -0.07782 | -0.045776 | -0.20142 | -0.42572 | -0.20599 | -0.064087 | 0.10529 | 59.0424 | 59.2072 | 122.1725 | 122.5204 | -0.045776 | 122.5342 | 59.285 | -0.20599 | 122.5204 | -0.045776 | 59.285 | 122.1725 | 122.5342 | -122.7493 | -122.8043
432.0156 | 122.8317 | -60.4706 | 62.0361 | 0.17548 | 0.0084103 | 0.015454 | -0.0029735 | 0.067001 | -0.00080328 | 0.069167 | -60.5118 | 61.9492 | -60.6766 | -60.6262 | 61.7752 | -1.1261 | -1.6067 | -1.1673 | 61.9812 | -60.6949 | -0.20599 | -0.086975 | -0.041199 | -0.15564 | -0.26093 | -0.2243 | -0.054932 | 0.16479 | 58.8638 | 59.3033 | 122.2458 | 122.4197 | -0.041199 | 122.4518 | 59.3445 | -0.2243 | 122.4197 | -0.041199 | 59.3445 | 122.2458 | 122.4518 | -122.7127 | -122.731
432.5781 | 122.7676 | -60.5164 | 62.059 | -0.1297 | 0.015033 | 0.016735 | 0.0083485 | 0.068923 | -0.0035803 | 0.067885 | -60.5209 | 62.0636 | -60.6537 | -60.759 | 61.615 | -1.2131 | -1.5381 | -1.2817 | 62.0041 | -60.7452 | -0.13733 | 0.004578 | -0.004578 | -0.24262 | -0.44403 | -0.22888 | -0.054932 | 0.13275 | 58.9783 | 59.2346 | 122.1313 | 122.58 | -0.004578 | 122.5204 | 59.3033 | -0.22888 | 122.58 | -0.004578 | 59.3033 | 122.1313 | 122.5204 | -122.7127 | -122.8043
433.0625 | 122.7768 | -60.5072 | 62.0453 | -0.083924 | 0.013537 | 0.016522 | 0.0040759 | 0.070419 | 0.00026492 | 0.06938 | -60.553 | 62.0361 | -60.6812 | -60.6857 | 61.6837 | -1.2543 | -1.5656 | -1.3138 | 62.0316 | -60.7361 | -0.17395 | -0.009155 | -0.045777 | -0.17853 | -0.36163 | -0.22888 | -0.013733 | 0.12817 | 58.9417 | 59.1934 | 122.1909 | 122.5433 | -0.045777 | 122.5388 | 59.2529 | -0.22888 | 122.5433 | -0.045777 | 59.2529 | 122.1909 | 122.5388 | -122.7264 | -122.7814
434.125 | 122.7264 | -60.5072 | 62.0453 | -0.015259 | 0.015674 | 0.018017 | 0.0032215 | 0.069992 | -0.0010169 | 0.067885 | -60.5621 | 62.0499 | -60.6674 | -60.704 | 61.6608 | -1.3092 | -1.5747 | -1.3733 | 62.0361 | -60.7544 | -0.16022 | 0.004578 | -0.054932 | -0.19684 | -0.38452 | -0.24719 | -0.009155 | 0.10529 | 58.9325 | 59.1339 | 122.168 | 122.5571 | -0.054932 | 122.5433 | 59.198 | -0.24719 | 122.5571 | -0.054932 | 59.198 | 122.168 | 122.5433 | -122.7127 | -122.7997
435.1094 | 122.7402 | -60.5164 | 62.0636 | 0.12207 | 0.014819 | 0.018658 | 0.0010853 | 0.067428 | 0.00026492 | 0.06874 | -60.6125 | 62.0361 | -60.6995 | -60.8002 | 61.6058 | -1.3367 | -1.5839 | -1.4374 | 62.0453 | -60.7452 | -0.18311 | -0.027466 | -0.096131 | -0.28381 | -0.45776 | -0.22888 | -0.018311 | 0.086975 | 58.9325 | 59.079 | 122.1222 | 122.5525 | -0.096131 | 122.5616 | 59.1797 | -0.22888 | 122.5525 | -0.096131 | 59.1797 | 122.1222 | 122.5616 | -122.7631 | -122.8088
436.125 | 122.7859 | -60.4889 | 62.0728 | -0.64087 | 0.014605 | 0.018658 | 0.0040759 | 0.069992 | -0.0020849 | 0.069594 | -60.4935 | 62.0499 | -60.6903 | -60.6583 | 61.6974 | -1.2863 | -1.6205 | -1.3367 | 62.0407 | -60.7269 | -0.20142 | -0.022888 | -0.004577 | -0.16937 | -0.37537 | -0.23804 | -0.032044 | 0.19684 | 58.8684 | 59.1522 | 122.1863 | 122.5388 | -0.004577 | 122.5296 | 59.2026 | -0.23804 | 122.5388 | -0.004577 | 59.2026 | 122.1863 | 122.5296 | -122.7631 | -122.7997
437.0625 | 122.8043 | -60.4843 | 62.0224 | 0.13733 | 0.013324 | 0.017376 | 0.00087167 | 0.070205 | 0.0015467 | 0.070662 | -60.5804 | 61.9858 | -60.672 | -60.6812 | 61.6974 | -1.3367 | -1.7853 | -1.4191 | 61.9995 | -60.7224 | -0.18768 | -0.036621 | -0.09613 | -0.19684 | -0.32501 | -0.23804 | -0.022888 | 0.091553 | 58.699 | 59.0652 | 122.1817 | 122.4701 | -0.09613 | 122.4838 | 59.1476 | -0.23804 | 122.4701 | -0.09613 | 59.1476 | 122.1817 | 122.4838 | -122.6944 | -122.7448
438.125 | 122.7264 | -60.498 | 62.0499 | -6e-08 | 0.014392 | 0.017803 | 0.0032215 | 0.069137 | -0.00016228 | 0.069167 | -60.5667 | 62.0407 | -60.6537 | -60.7132 | 61.6562 | -1.387 | -1.6617 | -1.4648 | 62.0453 | -60.7407 | -0.15564 | -0.009156 | -0.068664 | -0.21515 | -0.39368 | -0.24262 | -0.004578 | 0.086976 | 58.8364 | 59.0332 | 122.1542 | 122.5388 | -0.068664 | 122.5433 | 59.111 | -0.24262 | 122.5388 | -0.068664 | 59.111 | 122.1542 | 122.5433 | -122.7036 | -122.7905
439.0625 | 122.7585 | -60.5026 | 62.0682 | 0.54169 | 0.014605 | 0.015026 | 0.0030079 | 0.070205 | -0.0010169 | 0.070449 | -60.5896 | 62.0361 | -60.6674 | -60.7361 | 61.647 | -1.4145 | -1.7578 | -1.5244 | 62.0544 | -60.7178 | -0.16479 | -0.032043 | -0.086975 | -0.23346 | -0.42114 | -0.21515 | -0.013733 | 0.077819 | 58.7448 | 58.9783 | 122.1497 | 122.5388 | -0.086975 | 122.5571 | 59.0881 | -0.21515 | 122.5388 | -0.086975 | 59.0881 | 122.1497 | 122.5571 | -122.7356 | -122.7859
440.2344 | 122.7402 | -60.4614 | 62.1231 | -0.29755 | 0.012683 | 0.015881 | -0.0014783 | 0.065505 | -0.0025123 | 0.068312 | -60.5759 | 62.0361 | -60.6628 | -60.6766 | 61.6974 | -1.3641 | -1.6022 | -1.4191 | 62.0956 | -60.6766 | -0.20142 | -0.086975 | -0.11444 | -0.21515 | -0.42572 | -0.21515 | -0.027466 | 0.086975 | 58.8593 | 59.0424 | 122.1588 | 122.4976 | -0.11444 | 122.5571 | 59.0973 | -0.21515 | 122.4976 | -0.11444 | 59.0973 | 122.1588 | 122.5571 | -122.7859 | -122.7997
441.0625 | 122.8271 | -60.4385 | 62.059 | 0.099182 | 0.011188 | 0.020794 | 0.00087167 | 0.067214 | -0.00016228 | 0.069594 | -60.5072 | 61.972 | -60.6033 | -60.6079 | 61.7569 | -1.3779 | -1.9547 | -1.442 | 61.9904 | -60.6766 | -0.16479 | -0.086975 | -0.068664 | -0.16937 | -0.30212 | -0.23804 | -0.068665 | 0.096131 | 58.4839 | 58.9966 | 122.1954 | 122.4106 | -0.068664 | 122.4289 | 59.0607 | -0.23804 | 122.4106 | -0.068664 | 59.0607 | 122.1954 | 122.4289 | -122.6624 | -122.7356
442.125 | 122.7722 | -60.4431 | 62.1323 | 0.71716 | 0.01546 | 0.017163 | 0.0036487 | 0.065505 | -0.00058968 | 0.067458 | -60.5667 | 62.1048 | -60.6308 | -60.6354 | 61.7203 | -1.4053 | -1.6617 | -1.4511 | 62.0956 | -60.704 | -0.18768 | -0.027466 | -0.1236 | -0.19226 | -0.41199 | -0.26093 | -0.036621 | 0.064087 | 58.7814 | 58.992 | 122.1634 | 122.5479 | -0.1236 | 122.5388 | 59.0378 | -0.26093 | 122.5479 | -0.1236 | 59.0378 | 122.1634 | 122.5388 | -122.7631 | -122.8363
443.0625 | 122.8638 | -60.4156 | 62.0728 | 0.16785 | 0.011188 | 0.015667 | -0.00041013 | 0.068069 | -0.0010169 | 0.067885 | -60.4614 | 61.9812 | -60.6216 | -60.585 | 61.7844 | -1.4099 | -2.0233 | -1.474 | 61.9995 | -60.6628 | -0.20599 | -0.091553 | -0.045777 | -0.16937 | -0.28839 | -0.24719 | -0.073242 | 0.16022 | 58.3923 | 58.9417 | 122.2 | 122.3969 | -0.045777 | 122.4152 | 59.0057 | -0.24719 | 122.3969 | -0.045777 | 59.0057 | 122.2 | 122.4152 | -122.6944 | -122.7356
444.1094 | 122.7356 | -60.4294 | 62.1094 | 0.083923 | 0.01546 | 0.017376 | 0.0053577 | 0.068923 | 0.00026492 | 0.071089 | -60.6033 | 62.1002 | -60.6354 | -60.6949 | 61.6791 | -1.5106 | -1.8768 | -1.6067 | 62.0544 | -60.6949 | -0.20599 | -0.009155 | -0.17395 | -0.2655 | -0.4303 | -0.2655 | -0.054932 | 0.032043 | 58.5526 | 58.8226 | 122.1085 | 122.5296 | -0.17395 | 122.4838 | 58.9188 | -0.2655 | 122.5296 | -0.17395 | 58.9188 | 122.1085 | 122.4838 | -122.7448 | -122.8043
445.0625 | 122.8592 | -60.3836 | 62.1094 | -0.068665 | 0.0084103 | 0.015026 | -0.0038281 | 0.06636 | 5.1318e-05 | 0.069808 | -60.5118 | 62.0087 | -60.5988 | -60.6033 | 61.7935 | -1.4145 | -1.9638 | -1.4557 | 62.0636 | -60.6125 | -0.21515 | -0.10071 | -0.12817 | -0.21973 | -0.31586 | -0.22888 | -0.045776 | 0.086975 | 58.4198 | 58.9279 | 122.1771 | 122.3923 | -0.12817 | 122.4472 | 58.9691 | -0.22888 | 122.3923 | -0.12817 | 58.9691 | 122.1771 | 122.4472 | -122.7081 | -122.7219
446.0625 | 122.8043 | -60.4065 | 62.1185 | 0.18311 | 0.01311 | 0.019085 | 0.0057849 | 0.067001 | 0.00026492 | 0.066603 | -60.4935 | 62.0728 | -60.5942 | -60.6079 | 61.734 | -1.5244 | -2.0233 | -1.6022 | 62.0636 | -60.6628 | -0.18768 | -0.045776 | -0.086975 | -0.20142 | -0.38452 | -0.25635 | -0.054931 | 0.10071 | 58.3832 | 58.8043 | 122.1405 | 122.4792 | -0.086975 | 122.4701 | 58.8821 | -0.25635 | 122.4792 | -0.086975 | 58.8821 | 122.1405 | 122.4701 | -122.7127 | -122.7814
447.0625 | 122.8134 | -60.4065 | 62.1323 | 0.10681 | 0.013751 | 0.017376 | 0.0030079 | 0.068283 | -0.00080328 | 0.068312 | -60.5164 | 62.059 | -60.6354 | -60.6308 | 61.7386 | -1.5564 | -2.0279 | -1.6388 | 62.0819 | -60.6537 | -0.22888 | -0.073242 | -0.10986 | -0.2243 | -0.39368 | -0.24719 | -0.050354 | 0.11902 | 58.3786 | 58.7677 | 122.1451 | 122.4655 | -0.10986 | 122.4884 | 58.8501 | -0.24719 | 122.4655 | -0.10986 | 58.8501 | 122.1451 | 122.4884 | -122.7676 | -122.7859
448.0625 | 122.8775 | -60.3882 | 62.0865 | 0.099182 | 0.014392 | 0.016308 | 0.0019397 | 0.06636 | 0.00069212 | 0.068099 | -60.434 | 62.0453 | -60.5896 | -60.5759 | 61.7935 | -1.506 | -2.1378 | -1.6067 | 62.027 | -60.6537 | -0.20142 | -0.041199 | -0.045776 | -0.18768 | -0.29297 | -0.2655 | -0.059509 | 0.15564 | 58.2504 | 58.7814 | 122.1817 | 122.4335 | -0.045776 | 122.4152 | 58.8821 | -0.2655 | 122.4335 | -0.045776 | 58.8821 | 122.1817 | 122.4152 | -122.6761 | -122.7402
449.1094 | 122.8592 | -60.3836 | 62.1185 | 0.083923 | 0.012469 | 0.015667 | 0.0025807 | 0.065505 | -0.00037588 | 0.06874 | -60.466 | 62.0453 | -60.5804 | -60.5484 | 61.8164 | -1.5472 | -2.211 | -1.6434 | 62.0316 | -60.6491 | -0.19684 | -0.073242 | -0.082397 | -0.16479 | -0.30212 | -0.2655 | -0.086975 | 0.11444 | 58.1726 | 58.7402 | 122.2 | 122.4289 | -0.082397 | 122.4152 | 58.8364 | -0.2655 | 122.4289 | -0.082397 | 58.8364 | 122.2 | 122.4152 | -122.699 | -122.7676
450.0625 | 122.8775 | -60.3424 | 62.1277 | -0.16785 | 0.0090511 | 0.015454 | -0.0036145 | 0.063369 | 0.0011193 | 0.067458 | -60.4019 | 62.0224 | -60.5713 | -60.4843 | 61.8988 | -1.442 | -2.124 | -1.5244 | 62.0865 | -60.5667 | -0.22888 | -0.10529 | -0.05951 | -0.14191 | -0.22888 | -0.2243 | -0.041199 | 0.16937 | 58.2184 | 58.8181 | 122.2412 | 122.3648 | -0.05951 | 122.4289 | 58.9005 | -0.2243 | 122.3648 | -0.05951 | 58.9005 | 122.2412 | 122.4289 | -122.699 | -122.6944
451.125 | 122.7814 | -60.3424 | 62.1872 | -0.10681 | 0.015246 | 0.016308 | 0.0070667 | 0.065292 | -0.00058968 | 0.070235 | -60.5301 | 62.1002 | -60.5392 | -60.5576 | 61.7615 | -1.5793 | -2.0462 | -1.6663 | 62.1185 | -60.6125 | -0.19684 | -0.086975 | -0.18768 | -0.21515 | -0.42572 | -0.27008 | -0.068665 | 0.009156 | 58.2962 | 58.6761 | 122.1039 | 122.4426 | -0.18768 | 122.4609 | 58.7631 | -0.27008 | 122.4426 | -0.18768 | 58.7631 | 122.1039 | 122.4609 | -122.7264 | -122.7997
452.0625 | 122.7768 | -60.3928 | 62.1735 | 0.17548 | 0.013965 | 0.018871 | 0.0034351 | 0.067642 | -0.00016228 | 0.067458 | -60.4614 | 62.146 | -60.5713 | -60.5988 | 61.7477 | -1.6937 | -2.1469 | -1.7899 | 62.0865 | -60.6262 | -0.17853 | -0.027466 | -0.068665 | -0.20599 | -0.42572 | -0.23346 | -0.086975 | 0.10986 | 58.2458 | 58.6029 | 122.1405 | 122.5388 | -0.068665 | 122.4792 | 58.699 | -0.23346 | 122.5388 | -0.068665 | 58.699 | 122.1405 | 122.4792 | -122.7448 | -122.7997
453.1562 | 122.9507 | -60.3012 | 62.2421 | -0.2594 | 0.011401 | 0.015454 | -0.0025463 | 0.065505 | 0.00026492 | 0.067031 | -60.3699 | 62.0728 | -60.5347 | -60.4568 | 61.9125 | -1.5289 | -2.1835 | -1.5793 | 62.0865 | -60.553 | -0.23346 | -0.16937 | -0.068665 | -0.15564 | -0.32959 | -0.25177 | -0.15564 | 0.1648 | 58.1177 | 58.7219 | 122.2137 | 122.374 | -0.068665 | 122.3877 | 58.7723 | -0.25177 | 122.374 | -0.068665 | 58.7723 | 122.2137 | 122.3877 | -122.7768 | -122.7951
454.0625 | 122.7264 | -60.3836 | 62.2009 | 0.81635 | 0.014392 | 0.016308 | 0.0034351 | 0.064437 | -0.00037588 | 0.06938 | -60.6766 | 62.1368 | -60.553 | -60.5988 | 61.7294 | -1.7303 | -2.1469 | -1.8585 | 62.1368 | -60.6308 | -0.16937 | -0.064087 | -0.29297 | -0.21515 | -0.4715 | -0.24719 | -0.064087 | -0.1236 | 58.2367 | 58.5251 | 122.113 | 122.5204 | -0.29297 | 122.5204 | 58.6533 | -0.24719 | 122.5204 | -0.29297 | 58.6533 | 122.113 | 122.5204 | -122.7539 | -122.8317
455.125 | 122.8226 | -60.3149 | 62.1872 | 0.14496 | 0.010547 | 0.015454 | -0.00019653 | 0.069992 | -0.00016228 | 0.06874 | -60.4385 | 62.0865 | -60.5301 | -60.5209 | 61.8439 | -1.6525 | -2.2614 | -1.7578 | 62.1368 | -60.5255 | -0.21515 | -0.10071 | -0.1236 | -0.20599 | -0.34332 | -0.21057 | -0.050354 | 0.091552 | 58.0536 | 58.5571 | 122.1588 | 122.4014 | -0.1236 | 122.4518 | 58.6624 | -0.21057 | 122.4014 | -0.1236 | 58.6624 | 122.1588 | 122.4518 | -122.7173 | -122.7127
456.0625 | 122.7356 | -60.3333 | 62.2009 | 0.053406 | 0.014819 | 0.016522 | 0.0066395 | 0.067001 | -0.00037588 | 0.070021 | -60.466 | 62.1643 | -60.5209 | -60.5621 | 61.7889 | -1.7761 | -2.2568 | -1.9043 | 62.146 | -60.6216 | -0.18768 | -0.036621 | -0.13275 | -0.22888 | -0.41199 | -0.28839 | -0.054932 | 0.054932 | 58.0765 | 58.429 | 122.1222 | 122.4976 | -0.13275 | 122.4792 | 58.5571 | -0.28839 | 122.4976 | -0.13275 | 58.5571 | 122.1222 | 122.4792 | -122.7219 | -122.8226
457.1094 | 122.8683 | -60.3149 | 62.1872 | 0.14496 | 0.012897 | 0.018658 | 0.0036487 | 0.068496 | 0.0013329 | 0.068953 | -60.3378 | 62.1323 | -60.4752 | -60.4477 | 61.8988 | -1.7075 | -2.4582 | -1.8356 | 62.1231 | -60.5484 | -0.16022 | -0.054932 | -0.022889 | -0.13275 | -0.28839 | -0.23346 | -0.064087 | 0.13733 | 57.8567 | 58.4793 | 122.2137 | 122.4472 | -0.022889 | 122.438 | 58.6075 | -0.23346 | 122.4472 | -0.022889 | 58.6075 | 122.2137 | 122.438 | -122.6624 | -122.7356
458.1406 | 122.7585 | -60.3149 | 62.2238 | 0.022888 | 0.013537 | 0.021435 | 0.0042895 | 0.066146 | 0.00047852 | 0.06874 | -60.4156 | 62.2238 | -60.5438 | -60.5392 | 61.7981 | -1.8219 | -2.3254 | -1.973 | 62.1414 | -60.5621 | -0.22888 | 0 | -0.10071 | -0.22431 | -0.42572 | -0.24719 | -0.082398 | 0.12817 | 57.9895 | 58.342 | 122.113 | 122.5388 | -0.10071 | 122.4564 | 58.493 | -0.24719 | 122.5388 | -0.10071 | 58.493 | 122.113 | 122.4564 | -122.7676 | -122.7859
459.1094 | 122.7402 | -60.3516 | 62.2513 | -0.030518 | 0.013324 | 0.018658 | 0.0051441 | 0.06871 | -0.0020849 | 0.068312 | -60.379 | 62.233 | -60.498 | -60.498 | 61.8164 | -1.7761 | -2.2156 | -1.9363 | 62.1872 | -60.5576 | -0.14648 | -0.018311 | -0.027466 | -0.14648 | -0.43488 | -0.20599 | -0.064087 | 0.11902 | 58.136 | 58.4152 | 122.168 | 122.5845 | -0.027466 | 122.5388 | 58.5754 | -0.20599 | 122.5845 | -0.027466 | 58.5754 | 122.168 | 122.5388 | -122.7493 | -122.8088
460.0625 | 122.85 | -60.2737 | 62.2284 | 0.015259 | 0.011188 | 0.014813 | -0.0029735 | 0.067214 | 0.00069212 | 0.065749 | -60.3699 | 62.146 | -60.4889 | -60.4889 | 61.8759 | -1.6983 | -2.2888 | -1.8265 | 62.178 | -60.4935 | -0.21515 | -0.082398 | -0.09613 | -0.21515 | -0.35248 | -0.21973 | -0.050354 | 0.11902 | 57.9849 | 58.4473 | 122.1497 | 122.4197 | -0.09613 | 122.4518 | 58.5754 | -0.21973 | 122.4197 | -0.09613 | 58.5754 | 122.1497 | 122.4518 | -122.7173 | -122.7219
461.125 | 122.7768 | -60.2646 | 62.2742 | -0.22888 | 0.013324 | 0.016949 | 0.0055713 | 0.066787 | -0.0020849 | 0.069167 | -60.3104 | 62.2696 | -60.4385 | -60.4294 | 61.8896 | -1.6296 | -2.1835 | -1.8036 | 62.2192 | -60.5301 | -0.17395 | -0.004578 | -0.045777 | -0.16479 | -0.38452 | -0.2655 | -0.054932 | 0.12817 | 58.0811 | 58.461 | 122.1542 | 122.5342 | -0.045777 | 122.4838 | 58.6349 | -0.2655 | 122.5342 | -0.045777 | 58.6349 | 122.1542 | 122.4838 | -122.7127 | -122.8043
462.0625 | 122.7539 | -60.2783 | 62.2971 | 0.076294 | 0.015033 | 0.015026 | 0.0051441 | 0.070419 | -0.0014441 | 0.069167 | -60.3882 | 62.2467 | -60.4935 | -60.5072 | 61.8073 | -1.7441 | -2.2156 | -1.9913 | 62.2192 | -60.5392 | -0.21515 | -0.050354 | -0.10986 | -0.22888 | -0.48981 | -0.26093 | -0.07782 | 0.10528 | 58.0627 | 58.287 | 122.0856 | 122.525 | -0.10986 | 122.4976 | 58.5342 | -0.26093 | 122.525 | -0.10986 | 58.5342 | 122.0856 | 122.4976 | -122.7905 | -122.8363
463.0625 | 122.7539 | -60.2875 | 62.2787 | 0.10681 | 0.015246 | 0.01524 | 0.0034351 | 0.066574 | -0.0014441 | 0.070021 | -60.3699 | 62.2833 | -60.4706 | -60.5255 | 61.7844 | -1.7303 | -2.1973 | -2.0279 | 62.265 | -60.5026 | -0.18311 | 0.004577 | -0.082397 | -0.23804 | -0.49439 | -0.21515 | -0.013733 | 0.10071 | 58.0902 | 58.2596 | 122.0718 | 122.5708 | -0.082397 | 122.5525 | 58.5571 | -0.21515 | 122.5708 | -0.082397 | 58.5571 | 122.0718 | 122.5525 | -122.7493 | -122.7814
464.0625 | 122.731 | -60.2875 | 62.3245 | 0.015259 | 0.015033 | 0.016522 | 0.0064259 | 0.068283 | -0.00058968 | 0.069167 | -60.3195 | 62.2925 | -60.4431 | -60.4889 | 61.8484 | -1.7212 | -2.2156 | -2.0187 | 62.2513 | -60.5072 | -0.15564 | -0.032044 | -0.032043 | -0.20142 | -0.47607 | -0.21973 | -0.073242 | 0.1236 | 58.0719 | 58.2687 | 122.1359 | 122.58 | -0.032043 | 122.5388 | 58.5663 | -0.21973 | 122.58 | -0.032043 | 58.5663 | 122.1359 | 122.5388 | -122.7676 | -122.8317
465.0938 | 122.8592 | -60.1913 | 62.3016 | -0.50354 | 0.010547 | 0.012676 | -0.0038281 | 0.066146 | -0.00080328 | 0.068526 | -60.2234 | 62.2147 | -60.4019 | -60.3378 | 62.0178 | -1.4969 | -2.2339 | -1.767 | 62.2513 | -60.4156 | -0.21057 | -0.086975 | -0.032044 | -0.14648 | -0.28381 | -0.2243 | -0.050354 | 0.17853 | 57.9575 | 58.4244 | 122.2092 | 122.406 | -0.032044 | 122.4426 | 58.6945 | -0.2243 | 122.406 | -0.032044 | 58.6945 | 122.2092 | 122.4426 | -122.7036 | -122.7173
466.1094 | 122.7036 | -60.2646 | 62.3245 | 0.068664 | 0.012469 | 0.018017 | 0.0055713 | 0.068283 | 0.00047852 | 0.068526 | -60.3287 | 62.3154 | -60.4385 | -60.4889 | 61.8484 | -1.6663 | -2.1973 | -2.0325 | 62.2742 | -60.5255 | -0.17395 | -0.009155 | -0.064087 | -0.22431 | -0.47607 | -0.26093 | -0.050354 | 0.10986 | 58.0673 | 58.2321 | 122.113 | 122.58 | -0.064087 | 122.5388 | 58.5983 | -0.26093 | 122.58 | -0.064087 | 58.5983 | 122.113 | 122.5388 | -122.7631 | -122.85
467.1094 | 122.7814 | -60.2005 | 62.3383 | -0.11444 | 0.014392 | 0.017803 | 0.0036487 | 0.068069 | 0.00069212 | 0.06874 | -60.2417 | 62.3016 | -60.4019 | -60.3836 | 61.9263 | -1.6159 | -2.2797 | -2.0142 | 62.2879 | -60.4614 | -0.20142 | -0.036621 | -0.041199 | -0.18311 | -0.41199 | -0.26093 | -0.050354 | 0.16022 | 57.9208 | 58.1863 | 122.1268 | 122.5021 | -0.041199 | 122.4884 | 58.5846 | -0.26093 | 122.5021 | -0.041199 | 58.5846 | 122.1268 | 122.4884 | -122.7402 | -122.7997
468.0625 | 122.7951 | -60.2051 | 62.3657 | -0.038147 | 0.013965 | 0.016735 | 0.0057849 | 0.069137 | -0.0020849 | 0.068099 | -60.2966 | 62.2925 | -60.3928 | -60.379 | 61.9034 | -1.6388 | -2.3666 | -2.0782 | 62.2925 | -60.4156 | -0.18768 | -0.073243 | -0.091553 | -0.17395 | -0.46234 | -0.21057 | -0.073243 | 0.09613 | 57.8384 | 58.1268 | 122.1085 | 122.4976 | -0.091553 | 122.4976 | 58.5663 | -0.21057 | 122.4976 | -0.091553 | 58.5663 | 122.1085 | 122.4976 | -122.7585 | -122.7814
469.0625 | 122.7631 | -60.2097 | 62.3657 | 0.10681 | 0.013751 | 0.015881 | 0.0040759 | 0.067001 | 0.00069212 | 0.069594 | -60.2921 | 62.3474 | -60.3928 | -60.4385 | 61.8118 | -1.799 | -2.4353 | -2.2522 | 62.3337 | -60.4431 | -0.1831 | -0.018311 | -0.082397 | -0.22888 | -0.55389 | -0.23346 | -0.032044 | 0.10071 | 57.7744 | 57.9575 | 122.0215 | 122.5571 | -0.082397 | 122.5433 | 58.4106 | -0.23346 | 122.5571 | -0.082397 | 58.4106 | 122.0215 | 122.5433 | -122.7585 | -122.8088
470.1562 | 122.85 | -60.1547 | 62.3657 | 0.045776 | 0.011401 | 0.017803 | -0.0031873 | 0.067214 | 0.00069212 | 0.070235 | -60.2417 | 62.3062 | -60.3516 | -60.3699 | 61.9766 | -1.8036 | -2.6779 | -2.2522 | 62.3016 | -60.4156 | -0.19684 | -0.05951 | -0.086975 | -0.21515 | -0.3891 | -0.26093 | -0.064087 | 0.10986 | 57.4768 | 57.9025 | 122.1313 | 122.4609 | -0.086975 | 122.4564 | 58.3511 | -0.26093 | 122.4609 | -0.086975 | 58.3511 | 122.1313 | 122.4564 | -122.7173 | -122.7814
471.0781 | 122.7173 | -60.1593 | 62.3932 | -0.16022 | 0.014178 | 0.023358 | 0.0059985 | 0.067855 | -0.00080328 | 0.06874 | -60.1913 | 62.3795 | -60.3287 | -60.3287 | 61.9537 | -1.8631 | -2.6779 | -2.3163 | 62.3245 | -60.4202 | -0.16937 | -0.013732 | -0.032043 | -0.16937 | -0.43945 | -0.26093 | -0.068664 | 0.13733 | 57.4814 | 57.843 | 122.113 | 122.5388 | -0.032043 | 122.4838 | 58.2962 | -0.26093 | 122.5388 | -0.032043 | 58.2962 | 122.113 | 122.4838 | -122.7219 | -122.8134
472.1562 | 122.8638 | -60.1181 | 62.3657 | 0.045776 | 0.012256 | 0.018658 | 1.7066e-05 | 0.069778 | -0.0016577 | 0.070021 | -60.1593 | 62.2971 | -60.3424 | -60.3104 | 61.9949 | -1.9135 | -3.0258 | -2.4124 | 62.3245 | -60.3333 | -0.2243 | -0.068665 | -0.041199 | -0.19226 | -0.37079 | -0.21515 | -0.041199 | 0.18311 | 57.0923 | 57.7057 | 122.113 | 122.4152 | -0.041199 | 122.4426 | 58.2047 | -0.21515 | 122.4152 | -0.041199 | 58.2047 | 122.113 | 122.4426 | -122.7081 | -122.699
473.125 | 122.8271 | -60.141 | 62.3932 | 0.099182 | 0.012042 | 0.015667 | -0.00083733 | 0.067428 | -0.00016228 | 0.068953 | -60.1547 | 62.3337 | -60.2966 | -60.2875 | 62.0224 | -2.092 | -3.1998 | -2.6184 | 62.2971 | -60.3745 | -0.15564 | -0.059509 | -0.013733 | -0.14648 | -0.37079 | -0.23346 | -0.09613 | 0.14191 | 56.9412 | 57.5226 | 122.1634 | 122.4747 | -0.013733 | 122.438 | 58.049 | -0.23346 | 122.4747 | -0.013733 | 58.049 | 122.1634 | 122.438 | -122.6898 | -122.7676
474.1562 | 122.8317 | -60.1318 | 62.4802 | 0.10681 | 0.015033 | 0.01759 | 0.0051441 | 0.065292 | 0.0021875 | 0.069167 | -60.2142 | 62.4298 | -60.2921 | -60.3607 | 61.9217 | -2.4033 | -3.566 | -3.241 | 62.3199 | -60.4202 | -0.16022 | -0.050354 | -0.082397 | -0.22888 | -0.55847 | -0.28839 | -0.16022 | 0.07782 | 56.5659 | 56.8909 | 122.0535 | 122.5616 | -0.082397 | 122.4518 | 57.7286 | -0.28839 | 122.5616 | -0.082397 | 57.7286 | 122.0535 | 122.4518 | -122.7722 | -122.9004
475.1875 | 122.8592 | -60.0449 | 62.4573 | -0.25177 | 0.010974 | 0.012676 | -0.00041013 | 0.068283 | -0.0016577 | 0.068099 | -60.0906 | 62.3749 | -60.228 | -60.1318 | 62.114 | -2.4124 | -3.5477 | -2.9526 | 62.3611 | -60.2875 | -0.18311 | -0.082397 | -0.045776 | -0.086975 | -0.34332 | -0.24262 | -0.09613 | 0.13733 | 56.4972 | 57.0923 | 122.1588 | 122.4197 | -0.045776 | 122.406 | 57.6324 | -0.24262 | 122.4197 | -0.045776 | 57.6324 | 122.1588 | 122.406 | -122.6852 | -122.7448
476.1562 | 122.8271 | -60.0586 | 62.4573 | 0.099182 | 0.012042 | 0.019299 | 0.00087167 | 0.065078 | 0.0017603 | 0.069808 | -60.1089 | 62.3657 | -60.2646 | -60.2463 | 62.0407 | -2.6505 | -3.8727 | -3.2959 | 62.3657 | -60.2875 | -0.20599 | -0.091552 | -0.050354 | -0.18768 | -0.41657 | -0.22888 | -0.091552 | 0.15564 | 56.1859 | 56.7627 | 122.0993 | 122.4243 | -0.050354 | 122.4243 | 57.4081 | -0.22888 | 122.4243 | -0.050354 | 57.4081 | 122.0993 | 122.4243 | -122.7219 | -122.7448
477.0625 | 122.7219 | -60.0586 | 62.4939 | 0.015259 | 0.015674 | 0.016735 | 0.0070667 | 0.066574 | -0.0022987 | 0.068312 | -60.1273 | 62.5031 | -60.2325 | -60.2875 | 61.9537 | -2.916 | -3.9047 | -3.6118 | 62.4207 | -60.3516 | -0.17395 | 0.009156 | -0.068664 | -0.22888 | -0.54016 | -0.29297 | -0.073242 | 0.10529 | 56.1539 | 56.4468 | 122.0123 | 122.5616 | -0.068664 | 122.4792 | 57.1426 | -0.29297 | 122.5616 | -0.068664 | 57.1426 | 122.0123 | 122.4792 | -122.7264 | -122.8455
478.1094 | 122.699 | -60.0632 | 62.5076 | -0.022888 | 0.012469 | 0.016949 | 0.0062121 | 0.067428 | -0.0027259 | 0.069167 | -60.1273 | 62.5076 | -60.2188 | -60.2921 | 61.9537 | -3.0808 | -4.1382 | -3.8452 | 62.4527 | -60.2829 | -0.15564 | 0 | -0.064087 | -0.22888 | -0.55389 | -0.21973 | -0.054931 | 0.091553 | 55.925 | 56.218 | 122.0169 | 122.5708 | -0.064087 | 122.5159 | 56.9824 | -0.21973 | 122.5708 | -0.064087 | 56.9824 | 122.0169 | 122.5159 | -122.7264 | -122.7905
479.0625 | 122.7997 | -60.022 | 62.4893 | 0.14496 | 0.01546 | 0.016094 | 0.0036487 | 0.069137 | 0.0030419 | 0.069167 | -60.0998 | 62.4939 | -60.2417 | -60.2325 | 62.0132 | -3.1815 | -4.5136 | -3.9871 | 62.4664 | -60.2554 | -0.21973 | 0.004577 | -0.077819 | -0.21057 | -0.47607 | -0.23346 | -0.022888 | 0.14191 | 55.5084 | 56.0349 | 122.0352 | 122.5159 | -0.077819 | 122.4884 | 56.8405 | -0.23346 | 122.5159 | -0.077819 | 56.8405 | 122.0352 | 122.4884 | -122.731 | -122.7448
480.125 | 122.8226 | -59.967 | 62.5259 | 0.038147 | 0.0099057 | 0.01524 | -0.0021191 | 0.067642 | -0.00016228 | 0.069594 | -60.0723 | 62.4207 | -60.1776 | -60.1822 | 62.0819 | -3.3188 | -4.7974 | -4.1931 | 62.4664 | -60.1913 | -0.21057 | -0.10529 | -0.10529 | -0.21515 | -0.44403 | -0.2243 | -0.059509 | 0.10529 | 55.1697 | 55.7739 | 122.049 | 122.3877 | -0.10529 | 122.4335 | 56.6483 | -0.2243 | 122.3877 | -0.10529 | 56.6483 | 122.049 | 122.4335 | -122.7036 | -122.7173
481.0781 | 122.8317 | -59.9533 | 62.5259 | 0.038147 | 0.011828 | 0.014172 | -0.0010509 | 0.06636 | 0.00090572 | 0.070876 | -59.9716 | 62.4435 | -60.1318 | -60.1273 | 62.1231 | -3.5065 | -5.2689 | -4.4403 | 62.4481 | -60.1959 | -0.17853 | -0.082398 | -0.018311 | -0.17395 | -0.40283 | -0.24262 | -0.07782 | 0.16022 | 54.6844 | 55.513 | 122.0764 | 122.3969 | -0.018311 | 122.4014 | 56.4468 | -0.24262 | 122.3969 | -0.018311 | 56.4468 | 122.0764 | 122.4014 | -122.6578 | -122.7219
482.1094 | 122.7905 | -59.9258 | 62.6266 | -0.27466 | 0.011401 | 0.016522 | 0.0064259 | 0.065719 | -0.00016228 | 0.070021 | -59.967 | 62.6358 | -60.1181 | -60.0906 | 62.1231 | -3.7857 | -5.4382 | -4.7241 | 62.5488 | -60.2051 | -0.19226 | 0.009155 | -0.041199 | -0.16479 | -0.50354 | -0.27924 | -0.07782 | 0.15106 | 54.4876 | 55.2017 | 122.049 | 122.5616 | -0.041199 | 122.4747 | 56.1401 | -0.27924 | 122.5616 | -0.041199 | 56.1401 | 122.049 | 122.4747 | -122.7448 | -122.8317
483.0625 | 122.8729 | -59.8938 | 62.5534 | 0.12207 | 0.011828 | 0.013745 | -0.00041013 | 0.065933 | -0.0014441 | 0.068953 | -59.9304 | 62.5031 | -60.0677 | -60.0769 | 62.1414 | -4.0604 | -6.0104 | -5.0308 | 62.5305 | -60.1456 | -0.17395 | -0.050354 | -0.036621 | -0.1831 | -0.41199 | -0.25177 | -0.022888 | 0.13733 | 53.8834 | 54.863 | 122.0352 | 122.3969 | -0.036621 | 122.4243 | 55.8334 | -0.25177 | 122.3969 | -0.036621 | 55.8334 | 122.0352 | 122.4243 | -122.6212 | -122.699
484.1094 | 122.7173 | -59.903 | 62.6495 | -0.091553 | 0.015033 | 0.02058 | 0.0051441 | 0.067642 | -0.0027259 | 0.068953 | -59.9533 | 62.6541 | -60.0815 | -60.0815 | 62.1094 | -4.4174 | -6.2485 | -5.3925 | 62.5809 | -60.1364 | -0.17853 | 0.004578 | -0.050354 | -0.17853 | -0.54016 | -0.23346 | -0.068664 | 0.12817 | 53.6545 | 54.5105 | 122.0123 | 122.5571 | -0.050354 | 122.4838 | 55.4855 | -0.23346 | 122.5571 | -0.050354 | 55.4855 | 122.0123 | 122.4838 | -122.731 | -122.7859
485.0781 | 122.7036 | -59.8892 | 62.6724 | 0.053406 | 0.014392 | 0.020367 | 0.0055713 | 0.067855 | 0.0011193 | 0.067458 | -59.9579 | 62.6816 | -60.0861 | -60.141 | 62.0865 | -4.8248 | -6.6833 | -5.7632 | 62.6312 | -60.141 | -0.19684 | 0.009156 | -0.068665 | -0.25177 | -0.58594 | -0.25177 | -0.041198 | 0.12817 | 53.2059 | 54.126 | 121.9757 | 122.5708 | -0.068665 | 122.5204 | 55.0644 | -0.25177 | 122.5708 | -0.068665 | 55.0644 | 121.9757 | 122.5204 | -122.7585 | -122.8134
486.0781 | 122.8226 | -59.7931 | 62.7045 | -0.068665 | 0.012469 | 0.013104 | -0.0034009 | 0.065078 | 0.00069212 | 0.068953 | -59.8755 | 62.6495 | -59.9945 | -60.0037 | 62.2421 | -5.0537 | -7.2418 | -5.9509 | 62.645 | -60.054 | -0.20142 | -0.054932 | -0.082397 | -0.21057 | -0.46234 | -0.26093 | -0.05951 | 0.11902 | 52.5513 | 53.8422 | 122.0352 | 122.4426 | -0.082397 | 122.438 | 54.7394 | -0.26093 | 122.4426 | -0.082397 | 54.7394 | 122.0352 | 122.438 | -122.699 | -122.7585
487.0625 | 122.7493 | -59.8297 | 62.7274 | 0.10681 | 0.011401 | 0.019299 | 0.0040759 | 0.062942 | -0.0012305 | 0.070235 | -59.9258 | 62.7182 | -60.0586 | -60.1181 | 62.1094 | -5.4153 | -7.5302 | -6.3171 | 62.6678 | -60.0952 | -0.22888 | -0.009155 | -0.09613 | -0.28839 | -0.61798 | -0.2655 | -0.059509 | 0.13275 | 52.2995 | 53.5126 | 121.9391 | 122.5479 | -0.09613 | 122.4976 | 54.4144 | -0.2655 | 122.5479 | -0.09613 | 54.4144 | 121.9391 | 122.4976 | -122.7859 | -122.8226
488.0625 | 122.7036 | -59.8389 | 62.7319 | 0.038147 | 0.013751 | 0.020153 | 0.0034351 | 0.069137 | -0.00058968 | 0.06938 | -59.9167 | 62.7136 | -60.0357 | -60.0952 | 62.1094 | -5.7724 | -7.9834 | -6.7108 | 62.677 | -60.0815 | -0.19684 | -0.018311 | -0.07782 | -0.25635 | -0.62256 | -0.24262 | -0.054932 | 0.11902 | 51.8555 | 53.1281 | 121.9482 | 122.5525 | -0.07782 | 122.5159 | 54.0665 | -0.24262 | 122.5525 | -0.07782 | 54.0665 | 121.9482 | 122.5159 | -122.7676 | -122.8134
489.0625 | 122.8546 | -59.8022 | 62.7045 | 0.10681 | 0.014392 | 0.016949 | 0.0021533 | 0.068283 | -0.00037588 | 0.069808 | -59.7931 | 62.6587 | -59.9854 | -59.9442 | 62.2375 | -5.9235 | -8.6243 | -7.0038 | 62.6221 | -60.0311 | -0.18311 | -0.045777 | 0.009155 | -0.14191 | -0.46692 | -0.22888 | -0.082398 | 0.19226 | 51.178 | 52.7985 | 122.0398 | 122.4609 | 0.009155 | 122.4243 | 53.8788 | -0.22888 | 122.4609 | 0.009155 | 53.8788 | 122.0398 | 122.4243 | -122.6898 | -122.7356
490.1406 | 122.7356 | -59.8206 | 62.7686 | -0.0076296 | 0.014819 | 0.019299 | 0.0042895 | 0.068496 | 0.00026492 | 0.070876 | -59.8526 | 62.7457 | -59.9716 | -60.0449 | 62.1506 | -6.3354 | -8.8165 | -7.5485 | 62.709 | -60.0586 | -0.15106 | -0.022888 | -0.032043 | -0.2243 | -0.61798 | -0.23804 | -0.05951 | 0.11902 | 51.004 | 52.272 | 121.9711 | 122.5662 | -0.032043 | 122.5296 | 53.4851 | -0.23804 | 122.5662 | -0.032043 | 53.4851 | 121.9711 | 122.5296 | -122.7402 | -122.8271
491.0625 | 122.9507 | -59.7565 | 62.7228 | 0.13733 | 0.013324 | 0.01994 | 0.00044427 | 0.068283 | 0.00047852 | 0.071089 | -59.7519 | 62.6862 | -59.935 | -59.9167 | 62.2696 | -6.4545 | -9.3521 | -7.6813 | 62.6816 | -59.967 | -0.17853 | -0.036621 | 0.004578 | -0.16022 | -0.45319 | -0.21057 | -0.041198 | 0.18311 | 50.4044 | 52.0752 | 122.0261 | 122.4426 | 0.004578 | 122.4381 | 53.302 | -0.21057 | 122.4426 | 0.004578 | 53.302 | 122.0261 | 122.4381 | -122.6578 | -122.6898
492.1094 | 122.8317 | -59.7153 | 62.7411 | 0.18311 | 0.012897 | 0.01524 | -0.00041013 | 0.067642 | 0.00090572 | 0.071089 | -59.7382 | 62.6953 | -59.9258 | -59.8938 | 62.2696 | -6.6971 | -9.7229 | -7.9926 | 62.677 | -59.9808 | -0.21057 | -0.045777 | -0.022888 | -0.17853 | -0.4715 | -0.2655 | -0.064087 | 0.18768 | 49.9924 | 51.7227 | 121.9849 | 122.4106 | -0.022888 | 122.3923 | 53.0182 | -0.2655 | 122.4106 | -0.022888 | 53.0182 | 121.9849 | 122.3923 | -122.6669 | -122.7219
493.0625 | 122.8226 | -59.7198 | 62.8143 | 0.076294 | 0.010974 | 0.017376 | -0.00041013 | 0.06401 | 0.0019739 | 0.069167 | -59.7427 | 62.7274 | -59.9121 | -59.8846 | 62.2696 | -6.9626 | -10.08 | -8.3267 | 62.709 | -59.9533 | -0.19226 | -0.086975 | -0.022888 | -0.16479 | -0.54474 | -0.23346 | -0.10529 | 0.16937 | 49.6399 | 51.3931 | 121.9894 | 122.4472 | -0.022888 | 122.4289 | 52.7573 | -0.23346 | 122.4472 | -0.022888 | 52.7573 | 121.9894 | 122.4289 | -122.7264 | -122.7676
494.1094 | 122.7722 | -59.7153 | 62.8464 | 0.030517 | 0.014178 | 0.021008 | 0.0038623 | 0.067855 | -0.0022987 | 0.06938 | -59.8022 | 62.8143 | -59.903 | -59.9442 | 62.1964 | -7.4341 | -10.3867 | -8.8257 | 62.7548 | -59.9625 | -0.18768 | -0.032044 | -0.086975 | -0.22888 | -0.65002 | -0.24719 | -0.091553 | 0.10071 | 49.3286 | 50.8896 | 121.9116 | 122.5296 | -0.086975 | 122.4701 | 52.2812 | -0.24719 | 122.5296 | -0.086975 | 52.2812 | 121.9116 | 122.4701 | -122.7493 | -122.8088
495.0625 | 122.8271 | -59.6603 | 62.8647 | -0.10681 | 0.011615 | 0.015667 | -0.0019055 | 0.065078 | 0.0013329 | 0.069167 | -59.6695 | 62.7869 | -59.8206 | -59.8389 | 62.3154 | -7.6675 | -10.7437 | -9.0454 | 62.7731 | -59.8846 | -0.16022 | -0.07782 | -0.009156 | -0.17853 | -0.54932 | -0.22431 | -0.091553 | 0.15106 | 48.9166 | 50.6149 | 121.9757 | 122.4472 | -0.009156 | 122.4335 | 51.9928 | -0.22431 | 122.4472 | -0.009156 | 51.9928 | 121.9757 | 122.4335 | -122.6852 | -122.7493
496.1094 | 122.7539 | -59.6375 | 62.9333 | -0.22125 | 0.014819 | 0.011181 | 0.0062121 | 0.066787 | -0.00016228 | 0.06938 | -59.6603 | 62.8922 | -59.8206 | -59.8068 | 62.2971 | -7.9559 | -10.8902 | -9.288 | 62.8555 | -59.8526 | -0.18311 | -0.041199 | -0.022888 | -0.16937 | -0.63629 | -0.21515 | -0.07782 | 0.16022 | 48.7473 | 50.3494 | 121.9345 | 122.5296 | -0.022888 | 122.493 | 51.6815 | -0.21515 | 122.5296 | -0.022888 | 51.6815 | 121.9345 | 122.493 | -122.7539 | -122.7859
497.0625 | 122.8409 | -59.6008 | 62.9013 | 0.099182 | 0.012897 | 0.013958 | -0.0012647 | 0.065078 | -0.00037588 | 0.06874 | -59.6466 | 62.8281 | -59.8068 | -59.7931 | 62.3245 | -8.3084 | -11.1969 | -9.4986 | 62.7914 | -59.8526 | -0.20599 | -0.073242 | -0.045776 | -0.19226 | -0.57678 | -0.25177 | -0.10986 | 0.16022 | 48.4039 | 50.1022 | 121.9254 | 122.4289 | -0.045776 | 122.3923 | 51.2924 | -0.25177 | 122.4289 | -0.045776 | 51.2924 | 121.9254 | 122.3923 | -122.7081 | -122.7539
498.1094 | 122.7539 | -59.5917 | 62.9608 | -0.27466 | 0.012897 | 0.014172 | 0.0074939 | 0.06636 | -0.0016577 | 0.068099 | -59.6329 | 62.9288 | -59.7702 | -59.7565 | 62.3016 | -8.3679 | -10.2859 | -9.3521 | 62.8967 | -59.8251 | -0.17853 | -0.032043 | -0.041199 | -0.16479 | -0.65918 | -0.23346 | -0.064086 | 0.13733 | 49.3057 | 50.2396 | 121.8933 | 122.5204 | -0.041199 | 122.4884 | 51.2238 | -0.23346 | 122.5204 | -0.041199 | 51.2238 | 121.8933 | 122.4884 | -122.731 | -122.7859
499.0625 | 122.8271 | -59.523 | 62.9654 | 0.091553 | 0.011401 | 0.020153 | -0.0023327 | 0.064224 | -0.0016577 | 0.068526 | -59.5963 | 62.851 | -59.7427 | -59.7153 | 62.3428 | -7.9376 | -6.2531 | -8.7433 | 62.8738 | -59.7473 | -0.21973 | -0.11444 | -0.073242 | -0.19226 | -0.62256 | -0.2243 | -0.091553 | 0.14648 | 53.27 | 50.7797 | 121.8658 | 122.374 | -0.073242 | 122.3969 | 51.5854 | -0.2243 | 122.374 | -0.073242 | 51.5854 | 121.8658 | 122.3969 | -122.7081 | -122.7127
500.125 | 122.85 | -59.4818 | 63.0157 | -0.1297 | 0.012256 | 0.01524 | -0.0021191 | 0.064651 | 0.00026492 | 0.068526 | -59.5642 | 62.9196 | -59.6832 | -59.6603 | 62.3978 | -7.6675 | -4.0375 | -8.3405 | 62.915 | -59.7244 | -0.20142 | -0.09613 | -0.082397 | -0.17853 | -0.61798 | -0.24261 | -0.10071 | 0.11902 | 55.4443 | 51.1414 | 121.8796 | 122.4014 | -0.082397 | 122.3969 | 51.8143 | -0.24261 | 122.4014 | -0.082397 | 51.8143 | 121.8796 | 122.3969 | -122.699 | -122.7402
501.0625 | 122.8638 | -59.4727 | 63.0157 | 0.14496 | 0.012256 | 0.016949 | 0.0034351 | 0.066574 | -0.0014441 | 0.069167 | -59.5139 | 62.915 | -59.6878 | -59.5963 | 62.5168 | -7.5073 | -3.511 | -8.3038 | 62.9333 | -59.7107 | -0.21515 | -0.10071 | -0.041199 | -0.1236 | -0.49896 | -0.23804 | -0.082397 | 0.17395 | 55.9616 | 51.1688 | 121.9894 | 122.3877 | -0.041199 | 122.406 | 51.9653 | -0.23804 | 122.3877 | -0.041199 | 51.9653 | 121.9894 | 122.406 | -122.7036 | -122.7264
502.1094 | 122.7631 | -59.491 | 63.0524 | 0.15259 | 0.012683 | 0.015667 | 0.0036487 | 0.066146 | -0.0012305 | 0.068312 | -59.5871 | 62.9974 | -59.697 | -59.729 | 62.2696 | -7.6538 | -3.0212 | -8.4091 | 62.9745 | -59.7473 | -0.20599 | -0.054931 | -0.09613 | -0.23804 | -0.78278 | -0.25635 | -0.07782 | 0.10986 | 56.4697 | 51.0818 | 121.7606 | 122.4884 | -0.09613 | 122.4655 | 51.8372 | -0.25635 | 122.4884 | -0.09613 | 51.8372 | 121.7606 | 122.4655 | -122.7493 | -122.7997
503.0625 | 122.9004 | -59.4635 | 63.0295 | 0.16022 | 0.012469 | 0.018017 | 0.00087167 | 0.066787 | 0.0011193 | 0.068312 | -59.4727 | 62.9425 | -59.6649 | -59.6008 | 62.3932 | -7.5623 | -3.1174 | -8.5327 | 62.9242 | -59.7244 | -0.20142 | -0.086975 | -0.009155 | -0.13733 | -0.63629 | -0.26093 | -0.10529 | 0.19226 | 56.3461 | 50.9308 | 121.8567 | 122.406 | -0.009155 | 122.3877 | 51.9012 | -0.26093 | 122.406 | -0.009155 | 51.9012 | 121.8567 | 122.3877 | -122.6944 | -122.7539
504.125 | 122.8043 | -59.4772 | 63.1073 | 0.083923 | 0.012042 | 0.016308 | 0.0070667 | 0.065505 | -0.00016228 | 0.06938 | -59.5642 | 63.0432 | -59.7015 | -59.7244 | 62.2559 | -7.6675 | -2.655 | -8.7662 | 62.9517 | -59.761 | -0.2243 | -0.064087 | -0.086975 | -0.24719 | -0.85144 | -0.28381 | -0.15564 | 0.13733 | 56.8222 | 50.7111 | 121.7331 | 122.5204 | -0.086975 | 122.4289 | 51.8097 | -0.28381 | 122.5204 | -0.086975 | 51.8097 | 121.7331 | 122.4289 | -122.8088 | -122.8683
505.0625 | 122.8729 | -59.4086 | 63.089 | -0.2594 | 0.01076 | 0.013745 | -0.0034009 | 0.062942 | 0.0013329 | 0.067031 | -59.4315 | 62.9974 | -59.5779 | -59.7198 | 62.3749 | -7.3929 | -2.4765 | -8.2809 | 63.0432 | -59.6237 | -0.16937 | -0.091552 | -0.022889 | -0.31128 | -0.71411 | -0.21515 | -0.045776 | 0.14648 | 56.9321 | 51.1276 | 121.7834 | 122.406 | -0.022889 | 122.4518 | 52.0157 | -0.21515 | 122.406 | -0.022889 | 52.0157 | 121.7834 | 122.4518 | -122.6669 | -122.7127
506.0625 | 122.8546 | -59.404 | 63.0844 | 0.061035 | 0.014178 | 0.013745 | 0.00087167 | 0.065505 | -0.00037588 | 0.067671 | -59.4452 | 62.9974 | -59.5779 | -59.5642 | 62.3795 | -7.5165 | -2.4445 | -8.3862 | 63.0112 | -59.6237 | -0.17395 | -0.086975 | -0.041198 | -0.16022 | -0.70496 | -0.21973 | -0.073243 | 0.13275 | 56.9595 | 51.0178 | 121.7834 | 122.4014 | -0.041198 | 122.4152 | 51.8875 | -0.21973 | 122.4014 | -0.041198 | 51.8875 | 121.7834 | 122.4152 | -122.6624 | -122.7081
507.1094 | 122.818 | -59.3765 | 63.1256 | 0.11444 | 0.011401 | 0.011822 | -0.00062373 | 0.062087 | 5.1318e-05 | 0.06938 | -59.4589 | 63.002 | -59.5825 | -59.5917 | 62.3657 | -7.608 | -2.3071 | -8.5693 | 63.0203 | -59.6466 | -0.20599 | -0.1236 | -0.082397 | -0.21515 | -0.75989 | -0.27008 | -0.10529 | 0.1236 | 57.0694 | 50.8072 | 121.7422 | 122.3785 | -0.082397 | 122.3969 | 51.7685 | -0.27008 | 122.3785 | -0.082397 | 51.7685 | 121.7422 | 122.3969 | -122.7081 | -122.7722
508.0625 | 122.8775 | -59.3628 | 63.1439 | -0.54169 | 0.012042 | 0.014385 | 0.0025807 | 0.064224 | 0.00026492 | 0.070449 | -59.2987 | 63.0249 | -59.5276 | -59.523 | 62.4023 | -7.6172 | -2.2476 | -8.6105 | 63.0157 | -59.6054 | -0.16479 | -0.11902 | 0.064087 | -0.16022 | -0.74158 | -0.24261 | -0.12817 | 0.22888 | 57.1152 | 50.7523 | 121.7651 | 122.3877 | 0.064087 | 122.3785 | 51.7456 | -0.24261 | 122.3877 | 0.064087 | 51.7456 | 121.7651 | 122.3785 | -122.6715 | -122.7493
509.125 | 122.8043 | -59.3491 | 63.1485 | 0.16022 | 0.012042 | 0.017376 | 0.0070667 | 0.064651 | -0.0022987 | 0.069594 | -59.4315 | 63.1256 | -59.5825 | -59.5505 | 62.3383 | -7.6767 | -2.1194 | -8.7616 | 63.0936 | -59.6054 | -0.23346 | -0.022889 | -0.082398 | -0.20142 | -0.81024 | -0.25635 | -0.054932 | 0.15106 | 57.2296 | 50.5875 | 121.6873 | 122.4747 | -0.082398 | 122.4426 | 51.6724 | -0.25635 | 122.4747 | -0.082398 | 51.6724 | 121.6873 | 122.4426 | -122.731 | -122.7539
510.0781 | 122.8592 | -59.3079 | 63.2034 | 0.27466 | 0.01311 | 0.015881 | 0.0017261 | 0.065078 | -0.00016228 | 0.068312 | -59.3491 | 63.0936 | -59.5093 | -59.4681 | 62.4435 | -7.5714 | -2.037 | -8.7433 | 63.1073 | -59.5688 | -0.20142 | -0.10986 | -0.041199 | -0.16022 | -0.75989 | -0.26093 | -0.09613 | 0.16022 | 57.2708 | 50.5646 | 121.7514 | 122.4014 | -0.041199 | 122.4152 | 51.7365 | -0.26093 | 122.4014 | -0.041199 | 51.7365 | 121.7514 | 122.4152 | -122.7127 | -122.7722
511.1094 | 122.905 | -59.3033 | 63.1851 | 0.16785 | 0.010974 | 0.015454 | 0.0038623 | 0.065078 | -0.00016228 | 0.069594 | -59.3399 | 63.0615 | -59.4955 | -59.4635 | 62.4069 | -7.6263 | -2.179 | -9.1003 | 63.0615 | -59.5734 | -0.19226 | -0.1236 | -0.036621 | -0.16022 | -0.7782 | -0.27008 | -0.1236 | 0.15564 | 57.1243 | 50.2029 | 121.7102 | 122.3648 | -0.036621 | 122.3648 | 51.6769 | -0.27008 | 122.3648 | -0.036621 | 51.6769 | 121.7102 | 122.3648 | -122.6807 | -122.7585
512.0625 | 122.8363 | -59.2941 | 63.2034 | 0.11444 | 0.011401 | 0.01759 | 0.0012989 | 0.065078 | 0.0017603 | 0.067458 | -59.3353 | 63.089 | -59.5047 | -59.4681 | 62.3978 | -7.6447 | -2.1378 | -8.9951 | 63.0753 | -59.5459 | -0.21057 | -0.11444 | -0.041199 | -0.17395 | -0.80566 | -0.25177 | -0.12817 | 0.16937 | 57.1564 | 50.2991 | 121.6919 | 122.3831 | -0.041199 | 122.3694 | 51.6495 | -0.25177 | 122.3831 | -0.041199 | 51.6495 | 121.6919 | 122.3694 | -122.7081 | -122.7493
513.1094 | 122.7356 | -59.3079 | 63.2584 | 2.2736 | 0.014178 | 0.013958 | 0.0045033 | 0.063583 | 0.00026492 | 0.06874 | -59.3903 | 63.1622 | -59.5139 | -59.5276 | 62.2971 | -7.7454 | -1.9409 | -9.1919 | 63.1393 | -59.5413 | -0.20599 | -0.096131 | -0.082398 | -0.21973 | -0.9613 | -0.23346 | -0.11902 | 0.1236 | 57.3669 | 50.116 | 121.6049 | 122.4701 | -0.082398 | 122.4472 | 51.5625 | -0.23346 | 122.4701 | -0.082398 | 51.5625 | 121.6049 | 122.4472 | -122.7722 | -122.7997
514.0625 | 122.85 | -59.2758 | 63.2172 | 0.35858 | 0.012897 | 0.021435 | 0.0019397 | 0.066787 | -0.00080328 | 0.067671 | -59.3674 | 63.1073 | -59.4864 | -59.4223 | 62.4207 | -7.6172 | -2.0828 | -9.0775 | 63.1577 | -59.491 | -0.21057 | -0.10986 | -0.091553 | -0.14648 | -0.79651 | -0.21515 | -0.059509 | 0.11902 | 57.193 | 50.1984 | 121.6965 | 122.3831 | -0.091553 | 122.4335 | 51.6586 | -0.21515 | 122.3831 | -0.091553 | 51.6586 | 121.6965 | 122.4335 | -122.7036 | -122.7081
515.125 | 122.8317 | -59.2941 | 63.2446 | 0.10681 | 0.011828 | 0.016735 | -0.00062373 | 0.063796 | -0.0016577 | 0.070662 | -59.3262 | 63.1256 | -59.4498 | -59.4681 | 62.3566 | -7.5897 | -2.0416 | -9.1049 | 63.1485 | -59.4818 | -0.15564 | -0.11902 | -0.032044 | -0.17395 | -0.88806 | -0.18768 | -0.09613 | 0.1236 | 57.2525 | 50.1892 | 121.6507 | 122.4197 | -0.032044 | 122.4426 | 51.7044 | -0.18768 | 122.4197 | -0.032044 | 51.7044 | 121.6507 | 122.4426 | -122.6944 | -122.7264
516.0625 | 122.8638 | -59.2484 | 63.2355 | 0.15259 | 0.013751 | 0.018871 | 0.0040759 | 0.065719 | -0.00058968 | 0.069808 | -59.2438 | 63.1805 | -59.4177 | -59.3857 | 62.4069 | -7.5623 | -2.0462 | -9.1187 | 63.1714 | -59.4955 | -0.16937 | -0.054932 | 0.004578 | -0.13733 | -0.82855 | -0.24719 | -0.064087 | 0.17395 | 57.2021 | 50.1297 | 121.6553 | 122.4289 | 0.004578 | 122.4197 | 51.6861 | -0.24719 | 122.4289 | 0.004578 | 51.6861 | 121.6553 | 122.4197 | -122.6532 | -122.731
517.1094 | 122.7448 | -59.2758 | 63.3316 | -0.63324 | 0.014392 | 0.01759 | 0.0072803 | 0.064651 | -0.00080328 | 0.068312 | -59.3811 | 63.2538 | -59.4589 | -59.4772 | 62.3108 | -7.6492 | -1.8723 | -9.2606 | 63.2492 | -59.4864 | -0.1831 | -0.07782 | -0.10529 | -0.20142 | -1.0208 | -0.21057 | -0.082397 | 0.077819 | 57.4036 | 50.0153 | 121.5866 | 122.5296 | -0.10529 | 122.525 | 51.6266 | -0.21057 | 122.5296 | -0.10529 | 51.6266 | 121.5866 | 122.525 | -122.7905 | -122.818
518.0625 | 122.8134 | -59.2117 | 63.2996 | 0.068664 | 0.010119 | 0.012463 | -0.00083733 | 0.065505 | -0.0025123 | 0.06938 | -59.2621 | 63.1943 | -59.3994 | -59.4177 | 62.4023 | -7.5531 | -1.9089 | -9.1736 | 63.2126 | -59.4406 | -0.18768 | -0.10529 | -0.050354 | -0.20599 | -0.89722 | -0.22888 | -0.086976 | 0.13733 | 57.3029 | 50.0381 | 121.6141 | 122.406 | -0.050354 | 122.4243 | 51.6586 | -0.22888 | 122.406 | -0.050354 | 51.6586 | 121.6141 | 122.4243 | -122.699 | -122.7402
519.125 | 122.7356 | -59.2346 | 63.3545 | -2.1057 | 0.012897 | 0.017376 | 0.0074939 | 0.066146 | -0.0016577 | 0.071089 | -59.2712 | 63.2721 | -59.4086 | -59.4543 | 62.2971 | -7.5943 | -1.7807 | -9.2514 | 63.2767 | -59.4635 | -0.17395 | -0.082397 | -0.036621 | -0.21973 | -1.0574 | -0.22888 | -0.07782 | 0.13733 | 57.4539 | 49.9832 | 121.5317 | 122.5067 | -0.036621 | 122.5113 | 51.6403 | -0.22888 | 122.5067 | -0.036621 | 51.6403 | 121.5317 | 122.5113 | -122.7631 | -122.818
520.0625 | 122.818 | -59.1888 | 63.2996 | -0.16785 | 0.011401 | 0.01994 | -0.0019055 | 0.063796 | 0.00026492 | 0.068099 | -59.2758 | 63.2263 | -59.3628 | -59.404 | 62.3886 | -7.4387 | -1.8585 | -9.137 | 63.2538 | -59.3994 | -0.17395 | -0.073243 | -0.086975 | -0.21515 | -0.91095 | -0.21057 | -0.045777 | 0.086975 | 57.3303 | 50.0519 | 121.5775 | 122.4152 | -0.086975 | 122.4426 | 51.7502 | -0.21057 | 122.4152 | -0.086975 | 51.7502 | 121.5775 | 122.4426 | -122.6624 | -122.699
521.1094 | 122.7493 | -59.1751 | 63.3682 | 0.14496 | 0.01311 | 0.014599 | 0.0045033 | 0.064437 | -0.00058968 | 0.069808 | -59.2529 | 63.3179 | -59.3903 | -59.4131 | 62.3245 | -7.4936 | -1.7899 | -9.2468 | 63.2629 | -59.4315 | -0.21515 | -0.050354 | -0.07782 | -0.23804 | -1.0437 | -0.25635 | -0.10529 | 0.13733 | 57.3853 | 49.9283 | 121.4996 | 122.493 | -0.07782 | 122.438 | 51.6815 | -0.25635 | 122.493 | -0.07782 | 51.6815 | 121.4996 | 122.438 | -122.7585 | -122.7997
522.0625 | 122.8317 | -59.1293 | 63.3591 | 0.13733 | 0.013965 | 0.018871 | 0.0036487 | 0.067214 | 0.00026492 | 0.070449 | -59.2163 | 63.3133 | -59.3674 | -59.3308 | 62.3795 | -7.4203 | -1.8723 | -9.1644 | 63.2904 | -59.3903 | -0.23804 | -0.045777 | -0.086976 | -0.20142 | -0.97961 | -0.26093 | -0.068665 | 0.15106 | 57.2571 | 49.9649 | 121.5088 | 122.4426 | -0.086976 | 122.4197 | 51.709 | -0.26093 | 122.4426 | -0.086976 | 51.709 | 121.5088 | 122.4197 | -122.7264 | -122.7493
523.1094 | 122.7402 | -59.1431 | 63.3957 | 0.70953 | 0.010547 | 0.013104 | 0.0047169 | 0.067001 | 0.00090572 | 0.069167 | -59.0195 | 63.3499 | -59.3262 | -59.3719 | 62.3245 | -7.4615 | -1.7487 | -9.256 | 63.3408 | -59.3994 | -0.18311 | -0.045776 | 0.1236 | -0.22888 | -1.0712 | -0.25635 | -0.054932 | 0.3067 | 57.3944 | 49.8871 | 121.4676 | 122.493 | 0.1236 | 122.4838 | 51.6815 | -0.25635 | 122.493 | 0.1236 | 51.6815 | 121.4676 | 122.4838 | -122.7219 | -122.7951
524.0625 | 122.8683 | -59.1385 | 63.3774 | -0.9079 | 0.010974 | 0.018017 | 0.00023067 | 0.065933 | -0.00080328 | 0.066603 | -59.111 | 63.295 | -59.317 | -59.2896 | 62.4252 | -7.3288 | -1.886 | -9.1278 | 63.295 | -59.3353 | -0.17853 | -0.082397 | 0.027466 | -0.15106 | -0.95215 | -0.19684 | -0.082397 | 0.20599 | 57.2525 | 50.0107 | 121.5637 | 122.4335 | 0.027466 | 122.4335 | 51.8097 | -0.19684 | 122.4335 | 0.027466 | 51.8097 | 121.5637 | 122.4335 | -122.6944 | -122.7127
525.125 | 122.7448 | -59.1476 | 63.4277 | 2.8229 | 0.014178 | 0.016094 | 0.0057849 | 0.065505 | -0.0020849 | 0.071089 | -59.1202 | 63.3316 | -59.3124 | -59.3674 | 62.3337 | -7.3837 | -1.7487 | -9.2834 | 63.3682 | -59.3491 | -0.16479 | -0.09613 | 0.027466 | -0.21973 | -1.0941 | -0.20142 | -0.059509 | 0.19226 | 57.399 | 49.8642 | 121.4813 | 122.4792 | 0.027466 | 122.5159 | 51.7639 | -0.20142 | 122.4792 | 0.027466 | 51.7639 | 121.4813 | 122.5159 | -122.7402 | -122.7768
526.0625 | 122.8592 | -59.0607 | 63.3957 | 0.12207 | 0.01311 | 0.01524 | 0.0036487 | 0.067428 | 0.00090572 | 0.06938 | -59.0973 | 63.2996 | -59.2941 | -59.2072 | 62.2787 | -7.4158 | -1.8311 | -8.9951 | 63.3087 | -59.2987 | -0.23346 | -0.09613 | -0.036621 | -0.14648 | -1.1169 | -0.23804 | -0.086975 | 0.19684 | 57.2296 | 50.0656 | 121.3394 | 122.3602 | -0.036621 | 122.3694 | 51.6449 | -0.23804 | 122.3602 | -0.036621 | 51.6449 | 121.3394 | 122.3694 | -122.6898 | -122.6944
527.1094 | 122.7356 | -59.1248 | 63.4644 | 0.076294 | 0.013965 | 0.019512 | 0.0055713 | 0.066146 | -0.00037588 | 0.071517 | -59.1843 | 63.4277 | -59.3353 | -59.3628 | 62.3062 | -7.3105 | -1.7075 | -9.2514 | 63.3682 | -59.3445 | -0.21057 | -0.036621 | -0.059509 | -0.23804 | -1.1581 | -0.21973 | -0.09613 | 0.15106 | 57.4173 | 49.8734 | 121.431 | 122.5525 | -0.059509 | 122.493 | 51.8143 | -0.21973 | 122.5525 | -0.059509 | 51.8143 | 121.431 | 122.493 | -122.7997 | -122.8088
528.0625 | 122.8546 | -59.079 | 63.414 | 0.14496 | 0.010119 | 0.013958 | 0.0040759 | 0.06636 | 0.00047852 | 0.069167 | -59.0744 | 63.3499 | -59.2438 | -59.2438 | 62.4115 | -7.0816 | -1.8906 | -9.0591 | 63.3408 | -59.3124 | -0.1648 | -0.064086 | 0.004577 | -0.1648 | -1.0025 | -0.23346 | -0.073242 | 0.16937 | 57.1884 | 50.0198 | 121.4905 | 122.4289 | 0.004577 | 122.4197 | 51.9974 | -0.23346 | 122.4289 | 0.004577 | 51.9974 | 121.4905 | 122.4197 | -122.6578 | -122.7264
529.125 | 122.7219 | -59.1156 | 63.4872 | 0.022888 | 0.010974 | 0.016094 | 0.0057849 | 0.066574 | -0.0010169 | 0.06874 | -59.1705 | 63.4552 | -59.3079 | -59.3399 | 62.2742 | -7.0816 | -1.712 | -9.1415 | 63.4186 | -59.3353 | -0.19226 | -0.032044 | -0.054931 | -0.2243 | -1.2131 | -0.21973 | -0.068665 | 0.13733 | 57.4036 | 49.9741 | 121.3898 | 122.5708 | -0.054931 | 122.5342 | 52.034 | -0.21973 | 122.5708 | -0.054931 | 52.034 | 121.3898 | 122.5342 | -122.7951 | -122.8226
530.0781 | 122.8821 | -59.0195 | 63.4918 | -0.22888 | 0.011401 | 0.014599 | -0.0025463 | 0.064224 | 0.00047852 | 0.067671 | -59.0424 | 63.3774 | -59.2209 | -59.166 | 62.471 | -6.8298 | -1.8082 | -8.8989 | 63.4048 | -59.2346 | -0.20142 | -0.11444 | -0.022888 | -0.14648 | -1.0208 | -0.21515 | -0.086975 | 0.17853 | 57.2113 | 50.1205 | 121.4905 | 122.3969 | -0.022888 | 122.4243 | 52.1896 | -0.21515 | 122.3969 | -0.022888 | 52.1896 | 121.4905 | 122.4243 | -122.7127 | -122.7264
531.1094 | 122.7173 | -59.0424 | 63.5101 | 0.0076294 | 0.01311 | 0.019085 | 0.0057849 | 0.068283 | -0.0012305 | 0.069808 | -59.0927 | 63.4964 | -59.2255 | -59.285 | 62.2971 | -7.0084 | -1.7212 | -9.1461 | 63.4323 | -59.2987 | -0.18311 | -0.013733 | -0.050354 | -0.24262 | -1.2131 | -0.25635 | -0.07782 | 0.13275 | 57.3212 | 49.8962 | 121.3394 | 122.5388 | -0.050354 | 122.4747 | 52.034 | -0.25635 | 122.5388 | -0.050354 | 52.034 | 121.3394 | 122.4747 | -122.7356 | -122.8088
532.0625 | 122.8226 | -59.024 | 63.4506 | 0.1297 | 0.012469 | 0.017376 | -0.00062373 | 0.067642 | -0.0020849 | 0.068953 | -59.0469 | 63.3728 | -59.2209 | -59.198 | 62.384 | -6.8848 | -1.8677 | -9.0775 | 63.3957 | -59.2484 | -0.19684 | -0.07782 | -0.022888 | -0.17395 | -1.0666 | -0.2243 | -0.054932 | 0.17395 | 57.1564 | 49.9466 | 121.4081 | 122.3969 | -0.022888 | 122.4197 | 52.1393 | -0.2243 | 122.3969 | -0.022888 | 52.1393 | 121.4081 | 122.4197 | -122.6715 | -122.699
533.1094 | 122.7448 | -59.0424 | 63.5193 | 0.13733 | 0.013965 | 0.022717 | 0.0049305 | 0.067001 | -0.0010169 | 0.070235 | -59.2667 | 63.4323 | -59.2621 | -59.2255 | 62.3154 | -6.958 | -1.7303 | -9.2239 | 63.4598 | -59.2758 | -0.21973 | -0.086975 | -0.22431 | -0.18311 | -1.2039 | -0.23346 | -0.059509 | -0.004578 | 57.312 | 49.8184 | 121.3577 | 122.4747 | -0.22431 | 122.5021 | 52.0844 | -0.23346 | 122.4747 | -0.22431 | 52.0844 | 121.3577 | 122.5021 | -122.7814 | -122.7951
534.0625 | 122.85 | -58.992 | 63.5056 | 0.053406 | 0.014819 | 0.015026 | 0.0032215 | 0.068923 | -0.0020849 | 0.070021 | -59.0103 | 63.4415 | -59.1934 | -59.1522 | 62.3749 | -6.7612 | -1.9318 | -9.1095 | 63.4277 | -59.2438 | -0.20142 | -0.064087 | -0.018311 | -0.16022 | -1.1307 | -0.25177 | -0.07782 | 0.18311 | 57.0602 | 49.8825 | 121.3669 | 122.4335 | -0.018311 | 122.4197 | 52.2308 | -0.25177 | 122.4335 | -0.018311 | 52.2308 | 121.3669 | 122.4197 | -122.699 | -122.7493
535.125 | 122.7356 | -59.0286 | 63.5376 | 0.19836 | 0.014178 | 0.01759 | 0.0053577 | 0.065505 | -0.0027259 | 0.070235 | -59.0973 | 63.4781 | -59.2392 | -59.2575 | 62.2467 | -6.839 | -1.7166 | -9.2331 | 63.4872 | -59.2484 | -0.21057 | -0.05951 | -0.068665 | -0.22888 | -1.2909 | -0.21973 | -0.050354 | 0.14191 | 57.312 | 49.7955 | 121.2753 | 122.5067 | -0.068665 | 122.5159 | 52.1896 | -0.21973 | 122.5067 | -0.068665 | 52.1896 | 121.2753 | 122.5159 | -122.7768 | -122.7859
536.0625 | 122.7722 | -59.0103 | 63.5376 | 0.16785 | 0.013965 | 0.017163 | 0.0036487 | 0.067855 | 0.00047852 | 0.070021 | -59.0469 | 63.5056 | -59.1888 | -59.2392 | 62.2696 | -6.7474 | -1.7853 | -9.2285 | 63.4872 | -59.2575 | -0.17853 | -0.032044 | -0.036621 | -0.22888 | -1.268 | -0.24719 | -0.050354 | 0.14191 | 57.225 | 49.7818 | 121.2799 | 122.5159 | -0.036621 | 122.4976 | 52.2629 | -0.24719 | 122.5159 | -0.036621 | 52.2629 | 121.2799 | 122.4976 | -122.7264 | -122.7951
537.1094 | 122.7264 | -58.9966 | 63.5834 | 0.038147 | 0.012256 | 0.01759 | 0.0077075 | 0.068283 | -0.0020849 | 0.071517 | -59.0652 | 63.5468 | -59.1705 | -59.2392 | 62.2559 | -6.7841 | -1.7349 | -9.2606 | 63.5193 | -59.2392 | -0.17395 | -0.036621 | -0.068665 | -0.24262 | -1.3275 | -0.24262 | -0.064087 | 0.10529 | 57.2617 | 49.736 | 121.2524 | 122.5433 | -0.068665 | 122.5159 | 52.2125 | -0.24262 | 122.5433 | -0.068665 | 52.2125 | 121.2524 | 122.5159 | -122.7539 | -122.8226
538.0625 | 122.8546 | -58.9508 | 63.5376 | 0.16785 | 0.012683 | 0.016094 | 0.0034351 | 0.069351 | -0.00037588 | 0.070662 | -58.9462 | 63.4872 | -59.1339 | -59.1248 | 62.3703 | -6.6422 | -1.9363 | -9.137 | 63.4872 | -59.2026 | -0.1831 | -0.050354 | 0.004578 | -0.17395 | -1.1673 | -0.25177 | -0.050354 | 0.18768 | 57.0145 | 49.8138 | 121.3211 | 122.4381 | 0.004578 | 122.4381 | 52.3087 | -0.25177 | 122.4381 | 0.004578 | 52.3087 | 121.3211 | 122.4381 | -122.6715 | -122.7402
539.125 | 122.7264 | -58.9508 | 63.62 | -0.030518 | 0.014392 | 0.016522 | 0.0045033 | 0.066574 | 0.00047852 | 0.067031 | -59.0057 | 63.5742 | -59.1751 | -59.1843 | 62.265 | -6.7657 | -1.7624 | -9.2926 | 63.5284 | -59.1797 | -0.2243 | -0.045776 | -0.054931 | -0.23346 | -1.355 | -0.22888 | -0.091553 | 0.16937 | 57.1884 | 49.6582 | 121.2158 | 122.525 | -0.054931 | 122.4792 | 52.1851 | -0.22888 | 122.525 | -0.054931 | 52.1851 | 121.2158 | 122.4792 | -122.7951 | -122.7997
540.0625 | 122.8729 | -58.8913 | 63.5788 | -0.15259 | 0.0099057 | 0.018017 | -0.0048961 | 0.066146 | -0.00058968 | 0.06938 | -58.9417 | 63.4827 | -59.1064 | -59.0744 | 62.4069 | -6.6238 | -1.8539 | -9.1415 | 63.5239 | -59.0927 | -0.21515 | -0.09613 | -0.050354 | -0.18311 | -1.1719 | -0.20142 | -0.054931 | 0.16479 | 57.0374 | 49.7498 | 121.2982 | 122.374 | -0.050354 | 122.4152 | 52.2675 | -0.20142 | 122.374 | -0.050354 | 52.2675 | 121.2982 | 122.4152 | -122.6852 | -122.6715
541.125 | 122.6944 | -58.9233 | 63.6429 | 0.053406 | 0.014605 | 0.015881 | 0.0045033 | 0.066146 | -0.00058968 | 0.068526 | -59.0057 | 63.5971 | -59.111 | -59.1797 | 62.2513 | -6.8802 | -1.7715 | -9.4391 | 63.5559 | -59.1843 | -0.18768 | -0.045776 | -0.082397 | -0.25635 | -1.3916 | -0.26093 | -0.086975 | 0.10529 | 57.1518 | 49.4843 | 121.1746 | 122.5204 | -0.082397 | 122.4792 | 52.0432 | -0.26093 | 122.5204 | -0.082397 | 52.0432 | 121.1746 | 122.4792 | -122.7539 | -122.8271
542.0625 | 122.8226 | -58.873 | 63.6292 | 0.11444 | 0.01076 | 0.01759 | 0.0012989 | 0.068283 | -0.00037588 | 0.070876 | -58.8821 | 63.533 | -59.0561 | -58.992 | 62.3566 | -6.8115 | -1.9913 | -9.3338 | 63.5422 | -59.0973 | -0.18311 | -0.09613 | -0.009155 | -0.11902 | -1.2726 | -0.2243 | -0.086975 | 0.17395 | 56.8817 | 49.5392 | 121.2296 | 122.406 | -0.009155 | 122.4152 | 52.0615 | -0.2243 | 122.406 | -0.009155 | 52.0615 | 121.2296 | 122.4152 | -122.6852 | -122.7264
543.125 | 122.7356 | -58.8638 | 63.6749 | -0.045777 | 0.013751 | 0.015454 | 0.0047169 | 0.067001 | 0.00090572 | 0.071944 | -58.8959 | 63.6658 | -59.0652 | -59.079 | 62.3016 | -6.9168 | -1.8814 | -9.5169 | 63.6108 | -59.1431 | -0.20142 | -0.009156 | -0.032043 | -0.21515 | -1.3733 | -0.27923 | -0.064087 | 0.16937 | 56.9824 | 49.3469 | 121.1655 | 122.5296 | -0.032043 | 122.4747 | 51.947 | -0.27923 | 122.5296 | -0.032043 | 51.947 | 121.1655 | 122.4747 | -122.7402 | -122.818
544.0625 | 122.85 | -58.8089 | 63.6795 | 0.15259 | 0.013324 | 0.013958 | 0.0025807 | 0.067428 | -0.00080328 | 0.070449 | -58.8455 | 63.6063 | -59.0195 | -59.1522 | 62.3749 | -6.7749 | -2.0004 | -9.5261 | 63.6063 | -59.0652 | -0.21057 | -0.073242 | -0.036621 | -0.34332 | -1.3046 | -0.25635 | -0.073242 | 0.17395 | 56.8085 | 49.2828 | 121.1838 | 122.4152 | -0.036621 | 122.4152 | 52.034 | -0.25635 | 122.4152 | -0.036621 | 52.034 | 121.1838 | 122.4152 | -122.699 | -122.7448
545.125 | 122.7631 | -58.8593 | 63.7161 | 0.1297 | 0.010547 | 0.013745 | 0.0059985 | 0.067001 | 5.1318e-05 | 0.071303 | -58.9462 | 63.6566 | -59.0881 | -59.0424 | 62.1964 | -6.9992 | -1.8219 | -9.6497 | 63.6475 | -59.0836 | -0.22888 | -0.059509 | -0.086975 | -0.1831 | -1.5198 | -0.2243 | -0.068664 | 0.14191 | 57.0374 | 49.2096 | 121.0556 | 122.5159 | -0.086975 | 122.5067 | 51.86 | -0.2243 | 122.5159 | -0.086975 | 51.86 | 121.0556 | 122.5067 | -122.8043 | -122.7997
546.0625 | 122.8409 | -58.786 | 63.6658 | 0.13733 | 0.01311 | 0.017376 | 0.0010853 | 0.067001 | -0.0016577 | 0.071303 | -58.8135 | 63.5971 | -59.024 | -58.96 | 62.3245 | -6.9809 | -2.124 | -9.3796 | 63.5971 | -59.0515 | -0.23804 | -0.068664 | -0.027466 | -0.17395 | -1.3412 | -0.2655 | -0.068664 | 0.21057 | 56.662 | 49.4064 | 121.1105 | 122.3831 | -0.027466 | 122.3831 | 51.8051 | -0.2655 | 122.3831 | -0.027466 | 51.8051 | 121.1105 | 122.3831 | -122.6898 | -122.7173
547.125 | 122.7448 | -58.8181 | 63.7573 | -0.076294 | 0.012042 | 0.021435 | 0.0055713 | 0.065719 | -0.00058968 | 0.071089 | -58.8272 | 63.6795 | -59.0057 | -58.9966 | 62.3062 | -6.8939 | -1.9089 | -9.6451 | 63.6795 | -59.0698 | -0.18768 | -0.07782 | -0.009155 | -0.17853 | -1.4511 | -0.25177 | -0.07782 | 0.17853 | 56.9092 | 49.173 | 121.1243 | 122.4976 | -0.009155 | 122.4976 | 51.9241 | -0.25177 | 122.4976 | -0.009155 | 51.9241 | 121.1243 | 122.4976 | -122.7631 | -122.8271
548.0625 | 122.8912 | -58.786 | 63.7024 | 0.15259 | 0.011615 | 0.017163 | 0.0019397 | 0.068496 | -0.0014441 | 0.071303 | -58.7723 | 63.6337 | -58.9645 | -58.9417 | 62.3749 | -6.8207 | -2.0966 | -9.613 | 63.6429 | -59.0195 | -0.17853 | -0.068665 | 0.013733 | -0.15564 | -1.3275 | -0.23346 | -0.05951 | 0.19226 | 56.6895 | 49.173 | 121.1609 | 122.4197 | 0.013733 | 122.4289 | 51.9653 | -0.23346 | 122.4197 | 0.013733 | 51.9653 | 121.1609 | 122.4289 | -122.6669 | -122.7219
549.0625 | 122.8729 | -58.754 | 63.7207 | 0.14496 | 0.011615 | 0.016094 | 0.0025807 | 0.067642 | -0.00016228 | 0.068953 | -58.7631 | 63.6749 | -58.9508 | -58.9325 | 62.3566 | -6.8298 | -2.1194 | -9.6268 | 63.6429 | -59.024 | -0.19684 | -0.045776 | -0.009156 | -0.17853 | -1.3641 | -0.27008 | -0.07782 | 0.18768 | 56.6345 | 49.1272 | 121.1105 | 122.4289 | -0.009156 | 122.3969 | 51.9241 | -0.27008 | 122.4289 | -0.009156 | 51.9241 | 121.1105 | 122.3969 | -122.6715 | -122.7448
550.125 | 122.9187 | -58.7265 | 63.8031 | -0.22888 | 0.012042 | 0.015026 | -0.0021191 | 0.064865 | 0.00090572 | 0.069808 | -58.7173 | 63.6475 | -58.9096 | -58.8593 | 62.4069 | -6.7749 | -2.1286 | -9.5627 | 63.707 | -58.9554 | -0.18311 | -0.15564 | 0.009155 | -0.13275 | -1.3962 | -0.22888 | -0.096131 | 0.19226 | 56.5979 | 49.1638 | 121.1334 | 122.374 | 0.009155 | 122.4335 | 51.9516 | -0.22888 | 122.374 | 0.009155 | 51.9516 | 121.1334 | 122.4335 | -122.7127 | -122.7585
551.0625 | 122.8455 | -58.7219 | 63.7848 | 0.18311 | 0.013751 | 0.011822 | 0.0062121 | 0.065505 | -0.00037588 | 0.06938 | -58.7585 | 63.7482 | -58.9462 | -58.9233 | 62.3291 | -6.8893 | -2.1286 | -9.7824 | 63.7024 | -58.9828 | -0.2243 | -0.036621 | -0.036621 | -0.20142 | -1.4557 | -0.26093 | -0.082397 | 0.18768 | 56.5933 | 48.9395 | 121.051 | 122.4701 | -0.036621 | 122.4243 | 51.8326 | -0.26093 | 122.4701 | -0.036621 | 51.8326 | 121.051 | 122.4243 | -122.731 | -122.7676
552.125 | 122.7356 | -58.7357 | 63.8397 | 0.12207 | 0.012897 | 0.020794 | 0.0040759 | 0.06636 | -0.0010169 | 0.070662 | -58.8181 | 63.7665 | -58.9325 | -58.9737 | 62.2604 | -6.9717 | -1.9913 | -9.9152 | 63.7711 | -58.9508 | -0.19684 | -0.073243 | -0.082397 | -0.23804 | -1.5793 | -0.21515 | -0.068665 | 0.11444 | 56.7444 | 48.8205 | 120.9961 | 122.5021 | -0.082397 | 122.5067 | 51.7639 | -0.21515 | 122.5021 | -0.082397 | 51.7639 | 120.9961 | 122.5067 | -122.7722 | -122.7905
553.0625 | 122.8409 | -58.6716 | 63.8443 | 0.015259 | 0.011188 | 0.016949 | -0.00019653 | 0.067214 | -0.00058968 | 0.070449 | -58.6716 | 63.7436 | -58.8364 | -58.8409 | 62.3886 | -6.8161 | -2.1423 | -9.8099 | 63.7436 | -58.9142 | -0.16479 | -0.10071 | 0 | -0.16937 | -1.4557 | -0.24262 | -0.10071 | 0.16479 | 56.5292 | 48.8617 | 121.0602 | 122.4152 | 0 | 122.4152 | 51.8555 | -0.24262 | 122.4152 | 0 | 51.8555 | 121.0602 | 122.4152 | -122.6807 | -122.7585
554.1094 | 122.7402 | -58.6487 | 63.8947 | 1.8387 | 0.012683 | 0.019299 | 0.0064259 | 0.066574 | -0.00080328 | 0.071089 | -58.9005 | 63.7802 | -58.8593 | -58.9096 | 62.2787 | -6.9397 | -1.9913 | -10.0342 | 63.826 | -58.9233 | -0.21057 | -0.11444 | -0.25177 | -0.26093 | -1.6159 | -0.27466 | -0.068664 | -0.041199 | 56.6574 | 48.6145 | 120.9274 | 122.4289 | -0.25177 | 122.4747 | 51.709 | -0.27466 | 122.4289 | -0.25177 | 51.709 | 120.9274 | 122.4747 | -122.7539 | -122.818
555.0625 | 122.8455 | -58.5983 | 63.8947 | -0.061035 | 0.011828 | 0.012676 | -0.0016919 | 0.064224 | -0.0014441 | 0.068312 | -58.6853 | 63.7711 | -58.8043 | -58.7997 | 62.3886 | -6.8069 | -2.0691 | -9.9243 | 63.8168 | -58.8089 | -0.20599 | -0.1236 | -0.086975 | -0.20142 | -1.506 | -0.21057 | -0.07782 | 0.11902 | 56.5292 | 48.674 | 120.9869 | 122.3694 | -0.086975 | 122.4152 | 51.7914 | -0.21057 | 122.3694 | -0.086975 | 51.7914 | 120.9869 | 122.4152 | -122.699 | -122.7036
556.125 | 122.8409 | -58.6029 | 63.9359 | 0.18311 | 0.01076 | 0.016094 | 0.0066395 | 0.067001 | 0.00090572 | 0.070449 | -58.6304 | 63.858 | -58.786 | -58.754 | 62.3795 | -6.8848 | -2.1103 | -10.1349 | 63.8443 | -58.8272 | -0.18311 | -0.07782 | -0.027466 | -0.15106 | -1.5564 | -0.2243 | -0.091553 | 0.15564 | 56.4926 | 48.468 | 120.9824 | 122.4609 | -0.027466 | 122.4472 | 51.7181 | -0.2243 | 122.4609 | -0.027466 | 51.7181 | 120.9824 | 122.4472 | -122.7219 | -122.7631
557.0781 | 122.7173 | -58.5526 | 64.032 | -0.26703 | 0.011401 | 0.013745 | 0.0032215 | 0.065292 | 5.1318e-05 | 0.069808 | -58.5983 | 63.9816 | -58.7494 | -58.6166 | 62.3291 | -7.0953 | -1.9638 | -10.2585 | 63.9359 | -58.7997 | -0.19684 | -0.050354 | -0.045777 | -0.064087 | -1.7029 | -0.24719 | -0.09613 | 0.15106 | 56.5887 | 48.2941 | 120.8817 | 122.5342 | -0.045777 | 122.4884 | 51.4572 | -0.24719 | 122.5342 | -0.045777 | 51.4572 | 120.8817 | 122.4884 | -122.7814 | -122.8317
558.125 | 122.7493 | -58.5251 | 64.0411 | -1.2817 | 0.012683 | 0.019512 | 0.0040759 | 0.067001 | -0.0016577 | 0.070876 | -58.6166 | 63.9725 | -58.7082 | -58.7631 | 62.3337 | -7.1182 | -2.0233 | -10.4874 | 63.9862 | -58.7723 | -0.18311 | -0.068665 | -0.091553 | -0.23804 | -1.7075 | -0.24719 | -0.054932 | 0.091553 | 56.5018 | 48.0377 | 120.8588 | 122.4976 | -0.091553 | 122.5113 | 51.4069 | -0.24719 | 122.4976 | -0.091553 | 51.4069 | 120.8588 | 122.5113 | -122.7493 | -122.8134
559.0625 | 122.8775 | -58.4427 | 64.0503 | -0.11444 | 0.011615 | 0.012036 | -0.0034009 | 0.06401 | -0.0016577 | 0.069808 | -58.4839 | 63.9633 | -58.6533 | -58.6212 | 62.5214 | -6.9992 | -2.1332 | -10.3821 | 64.0091 | -58.6578 | -0.21057 | -0.086975 | -0.041199 | -0.17853 | -1.5289 | -0.21515 | -0.041199 | 0.16937 | 56.3095 | 48.0606 | 120.9641 | 122.406 | -0.041199 | 122.4518 | 51.4435 | -0.21515 | 122.406 | -0.041199 | 51.4435 | 120.9641 | 122.4518 | -122.7036 | -122.7081
560.125 | 122.8134 | -58.4564 | 64.1006 | 0.16785 | 0.011615 | 0.015454 | 0.0049305 | 0.065719 | -0.0014441 | 0.069167 | -58.5114 | 64.0091 | -58.6487 | -58.6441 | 62.4161 | -7.1411 | -2.1378 | -10.6247 | 64.0228 | -58.6716 | -0.19226 | -0.091553 | -0.054932 | -0.18768 | -1.6846 | -0.21515 | -0.07782 | 0.13733 | 56.3187 | 47.8317 | 120.8725 | 122.4655 | -0.054932 | 122.4792 | 51.3153 | -0.21515 | 122.4655 | -0.054932 | 51.3153 | 120.8725 | 122.4792 | -122.7493 | -122.7722
561.0625 | 122.818 | -58.4015 | 64.0915 | 0.083923 | 0.014178 | 0.018871 | -0.00019653 | 0.065719 | 0.00069212 | 0.070876 | -58.4152 | 64.0182 | -58.5938 | -58.5709 | 62.4756 | -7.1274 | -2.2064 | -10.6293 | 64.0274 | -58.6121 | -0.19226 | -0.073242 | -0.013733 | -0.16937 | -1.6159 | -0.21057 | -0.064087 | 0.17853 | 56.1951 | 47.7722 | 120.8771 | 122.4197 | -0.013733 | 122.4289 | 51.2741 | -0.21057 | 122.4197 | -0.013733 | 51.2741 | 120.8771 | 122.4289 | -122.6852 | -122.7036
562.125 | 122.7631 | -58.3923 | 64.2151 | -0.061035 | 0.015033 | 0.01524 | 0.0062121 | 0.065078 | 0.00047852 | 0.068953 | -58.4335 | 64.1602 | -58.548 | -58.5892 | 62.439 | -7.2327 | -1.9913 | -10.7391 | 64.1281 | -58.6349 | -0.15564 | -0.054932 | -0.041199 | -0.19684 | -1.7761 | -0.24262 | -0.086975 | 0.11444 | 56.4011 | 47.6532 | 120.8313 | 122.5525 | -0.041199 | 122.5204 | 51.1597 | -0.24262 | 122.5525 | -0.041199 | 51.1597 | 120.8313 | 122.5204 | -122.7631 | -122.85
563.0625 | 122.7905 | -58.3466 | 64.1922 | 0.053406 | 0.011401 | 0.015026 | -0.0010509 | 0.065719 | 5.1318e-05 | 0.068953 | -58.3969 | 64.0732 | -58.5297 | -58.5617 | 62.471 | -7.1777 | -2.1561 | -10.7712 | 64.0961 | -58.5526 | -0.1831 | -0.11902 | -0.050354 | -0.21515 | -1.7212 | -0.20599 | -0.096131 | 0.13275 | 56.1905 | 47.5754 | 120.8176 | 122.4197 | -0.050354 | 122.4426 | 51.1688 | -0.20599 | 122.4197 | -0.050354 | 51.1688 | 120.8176 | 122.4426 | -122.7219 | -122.7448
564.125 | 122.8363 | -58.3099 | 64.151 | 0.1297 | 0.012256 | 0.019512 | 0.0025807 | 0.06636 | -0.00037588 | 0.067885 | -58.3054 | 64.0778 | -58.5068 | -58.4656 | 62.5351 | -7.1548 | -2.2522 | -10.8124 | 64.0823 | -58.5159 | -0.19684 | -0.073242 | 0.004578 | -0.15564 | -1.6159 | -0.20599 | -0.068665 | 0.20142 | 56.0577 | 47.4976 | 120.845 | 122.3877 | 0.004578 | 122.3923 | 51.1551 | -0.20599 | 122.3877 | 0.004578 | 51.1551 | 120.845 | 122.3923 | -122.6578 | -122.6669
565.0625 | 122.85 | -58.2596 | 64.2426 | -0.11444 | 0.0088375 | 0.011181 | 1.7066e-05 | 0.061874 | -0.00080328 | 0.070449 | -58.342 | 64.1418 | -58.4839 | -58.4656 | 62.5168 | -7.2144 | -2.179 | -10.8902 | 64.1556 | -58.4793 | -0.2243 | -0.10071 | -0.082397 | -0.20599 | -1.7258 | -0.21973 | -0.086975 | 0.14191 | 56.0806 | 47.3694 | 120.7764 | 122.4014 | -0.082397 | 122.4152 | 51.0452 | -0.21973 | 122.4014 | -0.082397 | 51.0452 | 120.7764 | 122.4152 | -122.7264 | -122.7219
566.1094 | 122.8409 | -58.2642 | 64.2746 | 0.061035 | 0.014392 | 0.016094 | 0.0070667 | 0.065292 | -0.00037588 | 0.070021 | -58.2687 | 64.1647 | -58.4473 | -58.4106 | 62.5397 | -7.2693 | -2.2385 | -11.0138 | 64.1556 | -58.4747 | -0.18311 | -0.10986 | -0.004578 | -0.14649 | -1.7349 | -0.21057 | -0.11902 | 0.17853 | 56.0257 | 47.2504 | 120.8038 | 122.4289 | -0.004578 | 122.4197 | 50.9949 | -0.21057 | 122.4289 | -0.004578 | 50.9949 | 120.8038 | 122.4197 | -122.7219 | -122.7493
567.0781 | 122.7585 | -58.1909 | 64.3478 | -0.28229 | 0.010119 | 0.015881 | 0.00065787 | 0.06401 | -0.0016577 | 0.068526 | -58.2047 | 64.2197 | -58.3878 | -58.3557 | 62.5717 | -7.3288 | -2.1011 | -11.087 | 64.2746 | -58.4518 | -0.19684 | -0.12817 | -0.013733 | -0.16479 | -1.7761 | -0.26092 | -0.073242 | 0.18311 | 56.0898 | 47.1039 | 120.7626 | 122.4106 | -0.013733 | 122.4655 | 50.8621 | -0.26092 | 122.4106 | -0.013733 | 50.8621 | 120.7626 | 122.4655 | -122.7356 | -122.7997
568.125 | 122.7219 | -58.1955 | 64.3799 | -0.015259 | 0.012683 | 0.01759 | 0.0053577 | 0.065933 | -0.0018713 | 0.070235 | -58.2275 | 64.2975 | -58.3923 | -58.4015 | 62.4847 | -7.4524 | -2.092 | -11.2656 | 64.2883 | -58.429 | -0.19684 | -0.082398 | -0.032043 | -0.20599 | -1.8951 | -0.23346 | -0.091553 | 0.16479 | 56.1035 | 46.9299 | 120.6802 | 122.493 | -0.032043 | 122.4838 | 50.7431 | -0.23346 | 122.493 | -0.032043 | 50.7431 | 120.6802 | 122.4838 | -122.7722 | -122.8088
569.0625 | 122.8317 | -58.1635 | 64.3433 | 0.1297 | 0.01311 | 0.017376 | -0.0014783 | 0.067001 | 0.00026492 | 0.068099 | -58.1955 | 64.2517 | -58.3557 | -58.2687 | 62.6404 | -7.3425 | -2.2842 | -11.2244 | 64.2792 | -58.3466 | -0.19226 | -0.091553 | -0.032044 | -0.10529 | -1.7029 | -0.18311 | -0.064087 | 0.16022 | 55.8792 | 46.9391 | 120.8038 | 122.4152 | -0.032044 | 122.4426 | 50.8209 | -0.18311 | 122.4152 | -0.032044 | 50.8209 | 120.8038 | 122.4426 | -122.699 | -122.6898
570.125 | 122.7264 | -58.136 | 64.4623 | 0.10681 | 0.013965 | 0.016094 | 0.0045033 | 0.064865 | 0.0019739 | 0.070235 | -58.2047 | 64.3616 | -58.3649 | -58.3328 | 62.2101 | -7.7225 | -1.8127 | -11.2289 | 64.3433 | -58.3466 | -0.22888 | -0.10071 | -0.068665 | -0.19684 | -2.2522 | -0.21057 | -0.11902 | 0.16022 | 56.3232 | 46.907 | 120.3461 | 122.4976 | -0.068665 | 122.4792 | 50.4135 | -0.21057 | 122.4976 | -0.068665 | 50.4135 | 120.3461 | 122.4792 | -122.8271 | -122.8088
571.0625 | 122.8546 | -58.0673 | 64.4119 | 0.16022 | 0.013537 | 0.01759 | 0.00087167 | 0.067001 | -0.00037588 | 0.070662 | -58.0765 | 64.3341 | -58.2687 | -58.2367 | 62.6175 | -7.3929 | -2.33 | -11.3342 | 64.3341 | -58.2733 | -0.20142 | -0.07782 | -0.009155 | -0.16937 | -1.7944 | -0.20599 | -0.07782 | 0.19226 | 55.7373 | 46.7331 | 120.6848 | 122.4014 | -0.009155 | 122.4014 | 50.6744 | -0.20599 | 122.4014 | -0.009155 | 50.6744 | 120.6848 | 122.4014 | -122.6807 | -122.6852
572.125 | 122.85 | -58.0444 | 64.4257 | 0.083923 | 0.013324 | 0.019299 | 0.0051441 | 0.067214 | -0.0025123 | 0.070235 | -58.0444 | 64.3799 | -58.2184 | -58.2047 | 62.6312 | -7.4158 | -2.3209 | -11.38 | 64.3662 | -58.255 | -0.17395 | -0.045776 | 0 | -0.16022 | -1.7944 | -0.21057 | -0.059509 | 0.17395 | 55.7236 | 46.6644 | 120.6757 | 122.4243 | 0 | 122.4106 | 50.6287 | -0.21057 | 122.4243 | 0 | 50.6287 | 120.6757 | 122.4106 | -122.644 | -122.6807
573.0625 | 122.8317 | -58.017 | 64.4943 | 0.14496 | 0.014392 | 0.014385 | 0.0034351 | 0.067642 | 5.1318e-05 | 0.069808 | -58.0444 | 64.4302 | -58.2367 | -58.2092 | 62.5946 | -7.489 | -2.2659 | -11.4807 | 64.389 | -58.2504 | -0.21973 | -0.064087 | -0.027466 | -0.19226 | -1.8997 | -0.23346 | -0.10529 | 0.19226 | 55.751 | 46.5363 | 120.6116 | 122.4472 | -0.027466 | 122.406 | 50.528 | -0.23346 | 122.4472 | -0.027466 | 50.528 | 120.6116 | 122.406 | -122.731 | -122.7448
574.1094 | 122.7448 | -58.0124 | 64.5401 | -0.083924 | 0.015887 | 0.018444 | 0.0072803 | 0.067214 | -0.0012305 | 0.070235 | -58.017 | 64.5172 | -58.1909 | -58.2092 | 62.5442 | -7.3792 | -2.1652 | -11.4624 | 64.4623 | -58.2596 | -0.17853 | -0.022888 | -0.004578 | -0.19684 | -1.9958 | -0.24719 | -0.07782 | 0.17395 | 55.8472 | 46.55 | 120.5566 | 122.5296 | -0.004578 | 122.4747 | 50.6332 | -0.24719 | 122.5296 | -0.004578 | 50.6332 | 120.5566 | 122.4747 | -122.731 | -122.7997
575.0625 | 122.8546 | -57.9758 | 64.5081 | 0.11444 | 0.012897 | 0.016522 | 0.0023669 | 0.070205 | -0.0014441 | 0.06874 | -58.017 | 64.4669 | -58.1772 | -58.1406 | 62.5717 | -6.9077 | -2.298 | -11.2427 | 64.4714 | -58.2184 | -0.20142 | -0.041199 | -0.041199 | -0.16479 | -1.9363 | -0.24262 | -0.036621 | 0.16022 | 55.6778 | 46.7331 | 120.5475 | 122.4426 | -0.041199 | 122.4472 | 51.0681 | -0.24262 | 122.4426 | -0.041199 | 51.0681 | 120.5475 | 122.4472 | -122.6852 | -122.7264
576.1094 | 122.7173 | -58.0353 | 64.5401 | 0.022888 | 0.01311 | 0.015881 | 0.0049305 | 0.067642 | 5.1318e-05 | 0.072158 | -58.0719 | 64.5264 | -58.2504 | -58.2825 | 62.3383 | -6.221 | -2.0737 | -11.0687 | 64.4897 | -58.255 | -0.21515 | -0.013733 | -0.036621 | -0.24719 | -2.2018 | -0.21973 | -0.050354 | 0.17853 | 55.9616 | 46.9666 | 120.3735 | 122.5616 | -0.036621 | 122.525 | 51.8143 | -0.21973 | 122.5616 | -0.036621 | 51.8143 | 120.3735 | 122.525 | -122.7905 | -122.7951
577.0625 | 122.7539 | -58.0124 | 64.5584 | 0.099182 | 0.015246 | 0.016735 | 0.0049305 | 0.072555 | -0.00016228 | 0.070876 | -58.0719 | 64.5401 | -58.2321 | -58.0673 | 62.5168 | -5.6808 | -2.1057 | -10.762 | 64.5081 | -58.2687 | -0.21973 | -0.018311 | -0.059509 | -0.054932 | -2.0416 | -0.25635 | -0.050354 | 0.16022 | 55.9067 | 47.2504 | 120.5292 | 122.5525 | -0.059509 | 122.5204 | 52.3315 | -0.25635 | 122.5525 | -0.059509 | 52.3315 | 120.5292 | 122.5204 | -122.7905 | -122.8271
578.1094 | 122.7631 | -58.0032 | 64.5493 | -0.25177 | 0.016314 | 0.018017 | 0.0074939 | 0.068283 | 0.00047852 | 0.070021 | -58.0124 | 64.5264 | -58.1955 | -58.1772 | 62.3199 | -5.2643 | -2.037 | -10.5515 | 64.4714 | -58.287 | -0.19226 | -0.022888 | -0.009155 | -0.17395 | -2.2293 | -0.28381 | -0.077819 | 0.18311 | 55.9662 | 47.4518 | 120.3232 | 122.5296 | -0.009155 | 122.4747 | 52.739 | -0.28381 | 122.5296 | -0.009155 | 52.739 | 120.3232 | 122.4747 | -122.7448 | -122.8363
579.0625 | 122.818 | -57.9895 | 64.5309 | 0.19073 | 0.013537 | 0.017376 | 0.0010853 | 0.068496 | 0.00026492 | 0.069808 | -58.0307 | 64.5355 | -58.1863 | -58.1863 | 62.2742 | -5.0034 | -2.1286 | -10.4919 | 64.4623 | -58.2275 | -0.19684 | 0.004577 | -0.041199 | -0.19684 | -2.2568 | -0.23804 | -0.068665 | 0.15564 | 55.8609 | 47.4976 | 120.2637 | 122.525 | -0.041199 | 122.4518 | 52.9861 | -0.23804 | 122.525 | -0.041199 | 52.9861 | 120.2637 | 122.4518 | -122.7173 | -122.7585
580.125 | 122.7402 | -57.9803 | 64.5721 | 2.8305 | 0.011401 | 0.014813 | 0.0019397 | 0.069137 | -0.0010169 | 0.072371 | -58.0627 | 64.4852 | -58.2092 | -58.2184 | 62.1826 | -4.715 | -2.0416 | -10.611 | 64.5081 | -58.1863 | -0.22888 | -0.086976 | -0.082397 | -0.23804 | -2.3895 | -0.20599 | -0.064087 | 0.14648 | 55.9387 | 47.3694 | 120.163 | 122.4655 | -0.082397 | 122.4884 | 53.2654 | -0.20599 | 122.4655 | -0.082397 | 53.2654 | 120.163 | 122.4884 | -122.7814 | -122.7585
581.0625 | 122.8317 | -57.93 | 64.563 | 0.24414 | 0.014819 | 0.016735 | 0.0019397 | 0.069137 | 0.00069212 | 0.069594 | -57.9437 | 64.5859 | -58.1177 | -58.1085 | 62.2604 | -4.248 | -2.2339 | -10.5331 | 64.5126 | -58.1635 | -0.18768 | 0.022888 | -0.013733 | -0.17853 | -2.3026 | -0.23346 | -0.050354 | 0.17395 | 55.6961 | 47.3969 | 120.1904 | 122.5159 | -0.013733 | 122.4426 | 53.6819 | -0.23346 | 122.5159 | -0.013733 | 53.6819 | 120.1904 | 122.4426 | -122.6807 | -122.7264
582.125 | 122.8134 | -57.8888 | 64.6408 | -0.22125 | 0.013965 | 0.015454 | -0.00062373 | 0.065719 | -0.00016228 | 0.070876 | -57.8796 | 64.6133 | -58.049 | -58.0536 | 62.2101 | -3.6621 | -2.0691 | -10.3638 | 64.5584 | -58.136 | -0.16022 | -0.027466 | 0.009155 | -0.1648 | -2.4307 | -0.24719 | -0.082397 | 0.16937 | 55.8197 | 47.525 | 120.0989 | 122.5021 | 0.009155 | 122.4472 | 54.2267 | -0.24719 | 122.5021 | 0.009155 | 54.2267 | 120.0989 | 122.4472 | -122.6898 | -122.7768
583.0625 | 122.7493 | -57.8934 | 64.682 | 0.10681 | 0.01546 | 0.019726 | 0.0053577 | 0.069351 | 0.0019739 | 0.071517 | -57.9391 | 64.6591 | -58.1039 | -58.1451 | 62.027 | -3.3417 | -2.3529 | -10.6613 | 64.5676 | -58.1497 | -0.21057 | -0.022888 | -0.045776 | -0.25177 | -2.655 | -0.25635 | -0.11444 | 0.16479 | 55.5405 | 47.2321 | 119.9203 | 122.5525 | -0.045776 | 122.4609 | 54.5517 | -0.25635 | 122.5525 | -0.045776 | 54.5517 | 119.9203 | 122.4609 | -122.7859 | -122.8317
584.1094 | 122.7768 | -57.8476 | 64.6866 | -0.12207 | 0.014392 | 0.014385 | 0.0045033 | 0.068496 | -0.00080328 | 0.06874 | -57.8384 | 64.6866 | -58.0536 | -58.0215 | 62.0636 | -2.8748 | -2.0966 | -10.4691 | 64.6683 | -58.0582 | -0.20599 | 0 | 0.009155 | -0.17395 | -2.623 | -0.21057 | -0.01831 | 0.21515 | 55.751 | 47.3785 | 119.9112 | 122.5342 | 0.009155 | 122.5159 | 54.9728 | -0.21057 | 122.5342 | 0.009155 | 54.9728 | 119.9112 | 122.5159 | -122.7402 | -122.7448
585.0625 | 122.8088 | -57.7194 | 64.7919 | 0.16022 | 0.012256 | 0.01524 | 0.0023669 | 0.067642 | 0.00090572 | 0.071944 | -57.7744 | 64.7873 | -57.962 | -57.9391 | 62.1231 | -2.3117 | -2.1103 | -8.4366 | 64.7461 | -57.9529 | -0.24262 | -0.004578 | -0.054932 | -0.21973 | -2.6688 | -0.23346 | -0.045776 | 0.18768 | 55.6091 | 49.2828 | 119.8425 | 122.5067 | -0.054932 | 122.4655 | 55.4077 | -0.23346 | 122.5067 | -0.054932 | 55.4077 | 119.8425 | 122.4655 | -122.7539 | -122.7448
586.1094 | 122.7539 | -57.605 | 64.9567 | -0.28992 | 0.012683 | 0.019726 | 0.0023669 | 0.066574 | -0.00037588 | 0.071089 | -57.5912 | 64.9384 | -57.7835 | -57.7789 | 62.2375 | -1.9592 | -1.9913 | -7.0175 | 64.888 | -57.8567 | -0.17853 | -0.018311 | 0.013732 | -0.17395 | -2.7191 | -0.25177 | -0.068665 | 0.19226 | 55.6137 | 50.5875 | 119.8425 | 122.5433 | 0.013732 | 122.493 | 55.6458 | -0.25177 | 122.5433 | 0.013732 | 55.6458 | 119.8425 | 122.493 | -122.7402 | -122.8134
587.0625 | 122.7631 | -57.6004 | 64.9658 | 0.14496 | 0.015246 | 0.016094 | 0.0059985 | 0.066146 | 0.0015467 | 0.070449 | -57.6187 | 64.9567 | -57.7972 | -57.8201 | 62.1231 | -1.9592 | -2.0828 | -7.5211 | 64.9109 | -57.811 | -0.19684 | -0.009155 | -0.01831 | -0.21973 | -2.8427 | -0.21057 | -0.054931 | 0.17853 | 55.5176 | 50.0793 | 119.7235 | 122.5571 | -0.01831 | 122.5113 | 55.6412 | -0.21057 | 122.5571 | -0.01831 | 55.6412 | 119.7235 | 122.5113 | -122.7631 | -122.7768
588.125 | 122.7493 | -57.4997 | 65.1031 | -0.26703 | 0.013965 | 0.016094 | 0.0027943 | 0.066787 | 0.00090572 | 0.070876 | -57.399 | 65.1306 | -57.637 | -57.7057 | 62.1918 | -2.0187 | -2.0096 | -7.3792 | 65.0116 | -57.756 | -0.13733 | 0.027466 | 0.10071 | -0.20599 | -2.9114 | -0.25635 | -0.091552 | 0.23804 | 55.4901 | 50.1205 | 119.6915 | 122.6303 | 0.10071 | 122.5113 | 55.481 | -0.25635 | 122.6303 | 0.10071 | 55.481 | 119.6915 | 122.5113 | -122.7402 | -122.8592
589.0625 | 122.699 | -57.3349 | 65.2679 | 0.022888 | 0.013751 | 0.021435 | 0.0042895 | 0.067001 | 5.1318e-05 | 0.070662 | -57.3669 | 65.2405 | -57.5089 | -57.5821 | 62.265 | -1.7303 | -1.9455 | -4.9347 | 65.181 | -57.5821 | -0.17395 | -0.027465 | -0.032043 | -0.24719 | -3.0029 | -0.24719 | -0.086975 | 0.14191 | 55.3894 | 52.4002 | 119.5999 | 122.5754 | -0.032043 | 122.5159 | 55.6046 | -0.24719 | 122.5754 | -0.032043 | 55.6046 | 119.5999 | 122.5159 | -122.7768 | -122.85
590.125 | 122.7402 | -57.2525 | 65.2817 | -0.038147 | 0.015674 | 0.017803 | 0.0057849 | 0.068496 | -0.00080328 | 0.068099 | -57.2159 | 65.2908 | -57.4677 | -57.4722 | 62.2971 | -1.712 | -2.0691 | -5.3192 | 65.2588 | -57.5134 | -0.21515 | 0.009156 | 0.036621 | -0.21973 | -2.9846 | -0.26093 | -0.022888 | 0.25177 | 55.1834 | 51.9333 | 119.5496 | 122.5433 | 0.036621 | 122.5113 | 55.5405 | -0.26093 | 122.5433 | 0.036621 | 55.5405 | 119.5496 | 122.5113 | -122.7493 | -122.7951
591.0625 | 122.731 | -57.2205 | 65.3549 | 0.10681 | 0.015033 | 0.019512 | 0.0034351 | 0.070632 | 0.0011193 | 0.070662 | -57.2021 | 65.3412 | -57.3853 | -57.4356 | 62.2421 | -1.6479 | -2.0645 | -5.072 | 65.3412 | -57.4631 | -0.1648 | -0.013732 | 0.018311 | -0.21515 | -3.1128 | -0.24262 | -0.013732 | 0.18311 | 55.1559 | 52.1484 | 119.4626 | 122.5616 | 0.018311 | 122.5616 | 55.5725 | -0.24262 | 122.5616 | 0.018311 | 55.5725 | 119.4626 | 122.5616 | -122.7402 | -122.818
592.1094 | 122.7219 | -57.1243 | 65.4785 | -0.30518 | 0.014392 | 0.013317 | -0.00019653 | 0.066787 | 0.00047852 | 0.070235 | -57.0969 | 65.3961 | -57.3486 | -57.3807 | 62.2421 | -1.7349 | -2.0645 | -5.4932 | 65.3824 | -57.4127 | -0.2243 | -0.082398 | 0.027466 | -0.25635 | -3.2364 | -0.28839 | -0.096131 | 0.25177 | 55.0598 | 51.6312 | 119.3665 | 122.5204 | 0.027466 | 122.5067 | 55.3894 | -0.28839 | 122.5204 | 0.027466 | 55.3894 | 119.3665 | 122.5067 | -122.8271 | -122.8912
593.0625 | 122.731 | -57.3853 | 65.1535 | -0.14496 | 0.014819 | 0.016522 | 0.0040759 | 0.068923 | 0.00069212 | 0.071517 | -57.2479 | 65.1855 | -57.5592 | -57.5821 | 61.8896 | -2.6321 | -2.5269 | -11.6135 | 65.1169 | -57.6416 | -0.17395 | 0.032044 | 0.13733 | -0.19684 | -3.2639 | -0.25635 | -0.036621 | 0.31128 | 54.8584 | 45.7718 | 119.2749 | 122.5708 | 0.13733 | 122.5021 | 54.7531 | -0.25635 | 122.5708 | 0.13733 | 54.7531 | 119.2749 | 122.5021 | -122.7127 | -122.7951
594.125 | 122.7859 | -57.2433 | 65.3 | -0.19074 | 0.01311 | 0.016949 | 0.0015125 | 0.067855 | 0.0021875 | 0.070021 | -57.1243 | 65.2908 | -57.4448 | -57.4448 | 61.9537 | -2.5909 | -2.5726 | -11.5723 | 65.2542 | -57.518 | -0.20142 | -0.009155 | 0.11902 | -0.20142 | -3.3463 | -0.27466 | -0.045777 | 0.32043 | 54.6707 | 45.6711 | 119.1971 | 122.5342 | 0.11902 | 122.4976 | 54.6524 | -0.27466 | 122.5342 | 0.11902 | 54.6524 | 119.1971 | 122.4976 | -122.7448 | -122.818
595.0625 | 122.8592 | -57.1381 | 65.3732 | 0.1297 | 0.015246 | 0.017803 | 1.7066e-05 | 0.068496 | 0.0011193 | 0.072371 | -56.9687 | 65.3046 | -57.3212 | -57.3074 | 62.0773 | -2.4582 | -2.774 | -10.8856 | 65.3183 | -57.3395 | -0.18311 | -0.068665 | 0.16937 | -0.16937 | -3.2959 | -0.20142 | -0.054932 | 0.35248 | 54.364 | 46.2524 | 119.2154 | 122.4426 | 0.16937 | 122.4564 | 54.6799 | -0.20142 | 122.4426 | 0.16937 | 54.6799 | 119.2154 | 122.4564 | -122.6944 | -122.7127
596.1094 | 122.7127 | -56.9229 | 65.657 | -0.26703 | 0.013965 | 0.015026 | 0.00065787 | 0.064651 | 0.0017603 | 0.070876 | -56.7947 | 65.6616 | -57.0969 | -57.1198 | 62.1872 | -1.7853 | -2.4719 | -8.2535 | 65.6113 | -57.1793 | -0.17395 | 0.004578 | 0.12817 | -0.19684 | -3.4698 | -0.25635 | -0.045776 | 0.30212 | 54.451 | 48.6694 | 119.1101 | 122.5845 | 0.12817 | 122.5342 | 55.1376 | -0.25635 | 122.5845 | 0.12817 | 55.1376 | 119.1101 | 122.5342 | -122.7539 | -122.8363
597.0625 | 122.7631 | -56.9 | 65.6845 | -0.061035 | 0.016528 | 0.016949 | 0.0053577 | 0.06871 | 0.0017603 | 0.071944 | -56.694 | 65.6662 | -57.074 | -57.0602 | 62.178 | -0.98877 | -2.5589 | -8.2397 | 65.625 | -57.1335 | -0.17395 | -0.01831 | 0.20599 | -0.16022 | -3.5065 | -0.23346 | -0.059509 | 0.37994 | 54.3411 | 48.6603 | 119.0781 | 122.5662 | 0.20599 | 122.525 | 55.9113 | -0.23346 | 122.5662 | 0.20599 | 55.9113 | 119.0781 | 122.525 | -122.7585 | -122.818
598.125 | 122.7356 | -56.8359 | 65.7578 | -0.24414 | 0.014392 | 0.015667 | 0.0021533 | 0.067642 | 0.0017603 | 0.071089 | -56.5704 | 65.7623 | -57.0282 | -57.0465 | 62.1185 | -0.33875 | -2.5543 | -8.3359 | 65.7166 | -57.0877 | -0.19226 | 0.004578 | 0.2655 | -0.21057 | -3.6392 | -0.25177 | -0.041198 | 0.45776 | 54.2816 | 48.5001 | 118.9545 | 122.5983 | 0.2655 | 122.5525 | 56.4972 | -0.25177 | 122.5983 | 0.2655 | 56.4972 | 118.9545 | 122.5525 | -122.7859 | -122.8455
599.0625 | 122.7539 | -56.7673 | 65.8127 | -0.25177 | 0.012042 | 0.014172 | 0.0025807 | 0.068069 | 0.0013329 | 0.07173 | -56.5796 | 65.7852 | -56.9687 | -56.9916 | 62.1094 | 0.1236 | -2.5681 | -8.2947 | 65.744 | -57.0099 | -0.20142 | -0.027466 | 0.18768 | -0.2243 | -3.7033 | -0.24261 | -0.068664 | 0.3891 | 54.1992 | 48.4726 | 118.8766 | 122.5525 | 0.18768 | 122.5113 | 56.8909 | -0.24261 | 122.5525 | 0.18768 | 56.8909 | 118.8766 | 122.5113 | -122.7814 | -122.8226
600.125 | 122.7768 | -56.7627 | 65.8173 | -0.091553 | 0.014819 | 0.014172 | 0.0059985 | 0.067001 | 0.0011193 | 0.073012 | -56.5247 | 65.7578 | -56.9733 | -56.9366 | 62.059 | 0.59052 | -2.5452 | -8.02 | 65.7166 | -57.0145 | -0.21057 | -0.05951 | 0.23804 | -0.17395 | -3.7582 | -0.25177 | -0.10071 | 0.44861 | 54.2175 | 48.7427 | 118.8217 | 122.5204 | 0.23804 | 122.4792 | 57.3532 | -0.25177 | 122.5204 | 0.23804 | 57.3532 | 118.8217 | 122.4792 | -122.7905 | -122.8317
601.0625 | 122.7814 | -56.7627 | 65.8218 | -0.14496 | 0.015674 | 0.018231 | 0.0040759 | 0.06871 | 0.0019739 | 0.072798 | -56.5018 | 65.8035 | -56.9412 | -56.9366 | 61.9995 | 1.1169 | -2.6596 | -7.7454 | 65.7532 | -56.9916 | -0.17853 | -0.01831 | 0.26093 | -0.17395 | -3.8223 | -0.22888 | -0.068664 | 0.43945 | 54.1031 | 49.0173 | 118.7622 | 122.5662 | 0.26093 | 122.5159 | 57.8796 | -0.22888 | 122.5662 | 0.26093 | 57.8796 | 118.7622 | 122.5159 | -122.7631 | -122.8134
602.1094 | 122.7768 | -56.6711 | 65.8859 | -0.099182 | 0.015674 | 0.022503 | 0.0047169 | 0.070632 | 0.0015467 | 0.071089 | -56.4102 | 65.863 | -56.8588 | -56.8726 | 61.9446 | 1.4694 | -2.6733 | -7.1594 | 65.8173 | -56.9138 | -0.18768 | -0.022888 | 0.26093 | -0.20142 | -3.9413 | -0.24261 | -0.068664 | 0.44861 | 53.9978 | 49.5117 | 118.6157 | 122.5342 | 0.26093 | 122.4884 | 58.1406 | -0.24261 | 122.5342 | 0.26093 | 58.1406 | 118.6157 | 122.4884 | -122.7448 | -122.7997
603.0625 | 122.7814 | -56.5613 | 65.9821 | -0.12207 | 0.014819 | 0.019512 | 0.0038623 | 0.06871 | 0.0038965 | 0.073653 | -56.3187 | 65.9546 | -56.7993 | -56.7673 | 61.9171 | 1.6617 | -2.7328 | -6.839 | 65.9317 | -56.7856 | -0.23804 | -0.027466 | 0.24261 | -0.20599 | -4.0649 | -0.2243 | -0.050354 | 0.48065 | 53.8284 | 49.7223 | 118.4784 | 122.5159 | 0.24261 | 122.493 | 58.223 | -0.2243 | 122.5159 | 0.24261 | 58.223 | 118.4784 | 122.493 | -122.7814 | -122.7676
604.1094 | 122.7768 | -9.2514 | 113.475 | -0.28229 | 0.014605 | 0.029553 | -0.0029735 | 0.06636 | 0.0034693 | 0.069594 | -8.8943 | 113.3972 | -9.3887 | -9.2239 | 108.3435 | 36.0352 | 3.511 | 9.1644 | 113.3743 | -9.4025 | -0.13733 | -0.07782 | 0.35706 | 0.027466 | -5.1315 | -0.15106 | -0.10071 | 0.49438 | 12.7625 | 18.4158 | 117.5949 | 122.6486 | 0.35706 | 122.6257 | 45.2866 | -0.15106 | 122.6486 | 0.35706 | 45.2866 | 117.5949 | 122.6257 | -122.8638 | -122.8775
605.0625 | 122.7402 | -9.4986 | 113.1729 | -0.015259 | 0.016742 | 0.031689 | 0.0021533 | 0.068283 | 0.0015467 | 0.074294 | -9.2422 | 113.15 | -9.6725 | -9.5627 | 107.8812 | 36.731 | 3.1586 | 8.5922 | 113.1226 | -9.6954 | -0.17395 | -0.022889 | 0.25635 | -0.064087 | -5.2917 | -0.19684 | -0.050354 | 0.4303 | 12.6572 | 18.0908 | 117.3798 | 122.6486 | 0.25635 | 122.6212 | 46.2296 | -0.19684 | 122.6486 | 0.25635 | 46.2296 | 117.3798 | 122.6212 | -122.8455 | -122.8683
606.125 | 122.8317 | -9.8785 | 112.7014 | -0.26703 | 0.014178 | 0.034039 | -0.0019055 | 0.064224 | 0.0015467 | 0.070021 | -1.6388 | 112.7289 | -10.0021 | -9.8785 | 107.222 | 36.9278 | 2.8839 | 8.6884 | 112.6419 | -10.3271 | -0.1236 | 0.027466 | 8.2397 | 0 | -5.4794 | -0.44861 | -0.059509 | 8.3633 | 12.7625 | 18.5669 | 117.1005 | 122.6074 | 8.2397 | 122.5204 | 46.8063 | -0.44861 | 122.6074 | 8.2397 | 46.8063 | 117.1005 | 122.5204 | -122.7036 | -123.0286
607.0625 | 122.6303 | -68.6371 | 53.8925 | -0.23651 | 2.1705 | 2.1959 | 0.0070667 | 0.0024865 | 0.0019739 | 0.0074299 | 52.8168 | 53.2242 | -69.4016 | 48.9166 | 49.4339 | -67.4789 | 0.43488 | -4.2572 | 53.8055 | -68.9667 | -0.76447 | -0.66833 | 121.4539 | 117.5537 | -4.4586 | -0.32959 | -0.086975 | 122.2183 | 69.072 | 64.3799 | 118.071 | 121.8613 | 121.4539 | 122.4426 | 1.1581 | -0.32959 | 121.8613 | 121.4539 | 1.1581 | 118.071 | 122.4426 | -123.2941 | -122.8592
608.125 | 122.5845 | -122.1817 | 0.13733 | -0.32806 | 0.029132 | 0.010113 | -0.0021191 | 0.00013674 | 0.00026492 | 0.0074299 | 0.004578 | 0.09613 | -0.68207 | -2.7878 | -3.8132 | -121.2891 | -3.6392 | -11.9522 | 0.16022 | -122.5754 | 121.4996 | -0.041199 | 122.1863 | 119.3939 | -3.9505 | -0.39368 | 0.022888 | 0.68665 | 118.5425 | 110.2295 | 118.3685 | 122.2778 | 122.1863 | 122.3419 | 0.89264 | -0.39368 | 122.2778 | 122.1863 | 0.89264 | 118.3685 | 122.3419 | -0.8194 | -122.7127
609.0625 | 122.7081 | -122.4335 | 0.1236 | -0.20599 | 0.033832 | 0.0079768 | 0.0038623 | -0.00071786 | 0.00069212 | 0.0076435 | 0.004578 | 0.1236 | 0.31586 | -2.8519 | -3.9597 | -121.344 | -3.6346 | -12.1628 | 0.15564 | -122.7264 | 122.7493 | 0 | 122.438 | 119.5816 | -4.0833 | -0.29297 | 0.032044 | -0.31128 | 118.7988 | 110.2707 | 118.4738 | 122.5571 | 122.438 | 122.5891 | 1.0895 | -0.29297 | 122.5571 | 122.438 | 1.0895 | 118.4738 | 122.5891 | 0.19226 | -122.85
610.1094 | 122.7036 | -122.4289 | 0.16022 | -0.12207 | 0.031909 | 0.010967 | 0.0049305 | 0.0022729 | 5.1318e-05 | 0.0099933 | 0.27924 | 0.14191 | 0.082397 | -2.9755 | -4.0375 | -121.2891 | -3.7216 | -12.2589 | 0.21973 | -122.7264 | 122.5113 | -0.01831 | 122.7081 | 119.4534 | -4.1977 | -0.29755 | 0.05951 | 0.19684 | 118.7073 | 110.17 | 118.3914 | 122.5708 | 122.7081 | 122.6486 | 1.1398 | -0.29755 | 122.5708 | 122.7081 | 1.1398 | 118.3914 | 122.6486 | -0.07782 | -122.8867
611.0625 | 122.7264 | -122.5067 | 0.14648 | -0.25177 | 0.032336 | 0.011608 | 0.0025807 | 0.00077754 | 0.00090572 | 0.0084979 | -0.009155 | 0.11902 | -0.2243 | -3.2501 | -4.1199 | -121.3028 | -3.7811 | -12.6801 | 0.16022 | -122.7448 | 122.2824 | -0.027465 | 122.4976 | 119.2566 | -4.2664 | -0.23804 | 0.013733 | 0.21515 | 118.7256 | 109.8267 | 118.3868 | 122.6257 | 122.4976 | 122.6669 | 1.2039 | -0.23804 | 122.6257 | 122.4976 | 1.2039 | 118.3868 | 122.6669 | -0.37079 | -122.8912
612.125 | 122.8134 | -122.4472 | 0.14648 | -0.22888 | 0.028064 | 0.012463 | -0.0038281 | 0.00099114 | -0.0022987 | 0.0084979 | 0.09613 | 0.068665 | -0.17853 | -3.4012 | -4.0649 | -121.1609 | -3.9871 | -12.5015 | 0.14191 | -122.7173 | 122.2687 | -0.077819 | 122.5433 | 119.046 | -4.2114 | -0.27008 | -0.004577 | 0.27466 | 118.4601 | 109.9457 | 118.3823 | 122.5159 | 122.5433 | 122.5891 | 1.2863 | -0.27008 | 122.5159 | 122.5433 | 1.2863 | 118.3823 | 122.5891 | -0.32501 | -122.8638
613.0625 | 122.6761 | -122.4838 | 0.14648 | -0.28229 | 0.030627 | 0.0081904 | 0.0034351 | 0.0041955 | 0.0011193 | 0.011061 | -0.082397 | 0.1236 | -0.15564 | -3.7216 | -4.1794 | -121.2387 | -3.9871 | -13.5773 | 0.17395 | -122.7676 | 122.3282 | -0.022888 | 122.4014 | 118.7622 | -4.3259 | -0.28381 | 0.027466 | 0.073243 | 118.4967 | 108.9066 | 118.3044 | 122.6074 | 122.4014 | 122.6578 | 1.2451 | -0.28381 | 122.6074 | 122.4014 | 1.2451 | 118.3044 | 122.6578 | -0.30212 | -122.9141
614.1094 | 122.7356 | -122.5021 | 0.18768 | -0.28229 | 0.030841 | 0.0062678 | 0.0012989 | 0.00035034 | 0.00069212 | 0.0099933 | -0.013733 | 0.10986 | -0.2243 | -4.0009 | -4.2114 | -121.1884 | -3.9825 | -13.5727 | 0.20142 | -122.7493 | 122.2778 | -0.07782 | 122.4884 | 118.5013 | -4.3991 | -0.24719 | 0.013733 | 0.21057 | 118.5196 | 108.9294 | 118.2907 | 122.612 | 122.4884 | 122.7036 | 1.3138 | -0.24719 | 122.612 | 122.4884 | 1.3138 | 118.2907 | 122.7036 | -0.41199 | -122.937
615.0625 | 122.7768 | -122.493 | 0.19226 | -0.091553 | 0.034259 | 0.011395 | 0.0094165 | 0.0044091 | 0.0015467 | 0.0074299 | 0.054932 | 0.11902 | -0.20599 | -3.9413 | -4.0375 | -121.1517 | -4.0558 | -13.2339 | 0.20599 | -122.7448 | 122.287 | -0.073242 | 122.5479 | 118.5516 | -4.2297 | -0.25177 | 0.013733 | 0.26093 | 118.4372 | 109.259 | 118.4555 | 122.612 | 122.5479 | 122.699 | 1.3412 | -0.25177 | 122.612 | 122.5479 | 1.3412 | 118.4555 | 122.699 | -0.39826 | -122.937
616.125 | 122.7859 | -122.4792 | 0.15106 | -0.061035 | 0.029132 | 0.012249 | -0.0025463 | 0.0027001 | -0.00037588 | 0.0099933 | 0.027466 | 0.045776 | -0.17853 | -4.0329 | -0.44861 | -121.0831 | -4.097 | -13.2751 | 0.14648 | -122.7402 | 122.3007 | -0.10529 | 122.5067 | 118.4463 | -0.59967 | -0.26093 | -0.004578 | 0.20599 | 118.3823 | 109.2041 | 122.0306 | 122.525 | 122.5067 | 122.6257 | 1.3962 | -0.26093 | 122.525 | 122.5067 | 1.3962 | 122.0306 | 122.6257 | -0.32959 | -122.8912
617.0625 | 122.7127 | -122.5296 | 0.16022 | 0.19836 | 0.030414 | 0.0096856 | 0.0040759 | 0.00035034 | 0.0015467 | 0.0093525 | 0.022888 | 0.15564 | -0.15106 | -4.0924 | -0.16022 | -121.1838 | -3.9459 | -13.2614 | 0.16937 | -122.7905 | 122.3785 | -0.004577 | 122.5525 | 118.4372 | -0.32043 | -0.26093 | 0.009156 | 0.17395 | 118.5837 | 109.2682 | 122.3694 | 122.6852 | 122.5525 | 122.699 | 1.3458 | -0.26093 | 122.6852 | 122.5525 | 1.3458 | 122.3694 | 122.699 | -0.31128 | -122.9507
618.125 | 122.7951 | -122.4838 | 0.16479 | -0.30518 | 0.02785 | 0.011395 | 0.0027943 | 0.00035034 | -0.0012305 | 0.010634 | 0.041199 | 0.086975 | -0.1831 | -4.0375 | 0.027466 | -121.1105 | -4.0604 | -13.0234 | 0.13733 | -122.7493 | 122.3007 | -0.07782 | 122.525 | 118.4463 | -0.13733 | -0.2655 | -0.027466 | 0.2243 | 118.4235 | 109.4604 | 122.5113 | 122.5708 | 122.525 | 122.6212 | 1.3733 | -0.2655 | 122.5708 | 122.525 | 1.3733 | 122.5113 | 122.6212 | -0.3479 | -122.9141
619.0625 | 122.6944 | -122.493 | 0.20142 | -0.25177 | 0.030627 | 0.008404 | 0.0057849 | -7.686e-05 | -0.0012305 | 0.0091389 | -0.032043 | 0.11444 | -0.20142 | -4.0787 | 0.032043 | -120.9824 | -3.8864 | -13.1927 | 0.21057 | -122.7356 | 122.2916 | -0.086975 | 122.4609 | 118.4143 | -0.16937 | -0.24262 | 0.009155 | 0.16937 | 118.6066 | 109.3002 | 122.525 | 122.6074 | 122.4609 | 122.7036 | 1.5106 | -0.24262 | 122.6074 | 122.4609 | 1.5106 | 122.525 | 122.7036 | -0.40283 | -122.937
620.125 | 122.7585 | -122.4747 | 0.15564 | -0.25177 | 0.032977 | 0.0090448 | 0.010271 | 0.066146 | -0.0010169 | 0.080916 | 0.050354 | 0.091553 | -0.20599 | -122.5067 | 0 | 0.027466 | -0.14191 | -13.3438 | 0.14191 | -122.7905 | 122.2687 | -0.064087 | 122.525 | -0.032044 | -0.15564 | -0.31586 | -0.013733 | 0.25635 | 122.3328 | 109.1309 | 122.4747 | 122.5662 | 122.525 | 122.6166 | 122.5021 | -0.31586 | 122.5662 | 122.525 | 122.5021 | 122.4747 | 122.6166 | -0.36163 | -122.9462
621.0625 | 122.7219 | -122.0764 | 0.16479 | -0.13733 | 0.029773 | 0.01289 | 0.0077075 | 0.065505 | 0.00026492 | 0.079207 | -0.018311 | 0.13733 | 0.36163 | -122.5571 | -0.041199 | -0.018311 | -0.14191 | -12.5473 | 0.13275 | -146.8506 | 122.438 | -0.027466 | 122.0581 | -0.48065 | -0.20599 | -24.7742 | -0.032044 | -0.37994 | 121.9345 | 109.5291 | 122.0352 | 122.2137 | 122.0581 | 122.2092 | 122.0581 | -24.7742 | 122.2137 | 122.0581 | 122.0581 | 122.0352 | 122.2092 | 0.19684 | -147.0154
622.1094 | 121.1929 | -106.3293 | 0.18768 | -0.13733 | 0.024219 | 0.010113 | 0.012834 | 0.0033411 | 0.0051783 | -0.0058147 | 0.064087 | 0.10529 | 3.479 | -1.3687 | -6.8573 | -7.9926 | 0.47607 | -18.6859 | 0.10529 | -149.9954 | 109.8084 | -0.082397 | 106.3934 | 104.9606 | -7.045 | -43.6661 | -0.082397 | -3.4149 | 106.8054 | 87.6434 | 99.472 | 106.4346 | 106.3934 | 106.4346 | 98.3368 | -43.6661 | 106.4346 | 106.3934 | 98.3368 | 99.472 | 106.4346 | 3.2913 | -150.1831
623.0625 | 121.5729 | -121.3852 | 0.16937 | -0.29755 | 0.028491 | 0.007763 | 0.027574 | 0.069992 | 0.064779 | 0.16722 | -0.027466 | 0.1236 | -0.20142 | -121.4264 | -121.312 | -121.6278 | -0.737 | 0.068665 | 0.19226 | -121.637 | 121.1838 | -0.045777 | 121.3577 | -0.041199 | -121.4813 | -0.25177 | 0.022888 | 0.17395 | 120.6482 | 121.4539 | 0.073242 | 121.5088 | 121.3577 | 121.5775 | -0.24262 | -0.25177 | 121.5088 | 121.3577 | -0.24262 | 0.073242 | 121.5775 | -0.37079 | -121.8063
624.1094 | 121.9254 | -121.5775 | 0.12817 | -0.19074 | 0.019946 | 0.0073358 | 0.027147 | 0.0012047 | -0.00080328 | 0.026869 | 0.064087 | 0.064087 | -0.16937 | 0.059509 | 0.082397 | 0.082397 | -3.0716 | -0.027466 | 0.13275 | -121.8109 | 121.4081 | -0.064087 | 121.6415 | 121.637 | -0.045777 | -0.23346 | 0.004577 | 0.23346 | 118.5059 | 121.55 | 121.6599 | 121.6415 | 121.6415 | 121.7102 | 121.6599 | -0.23346 | 121.6415 | 121.6415 | 121.6599 | 121.6599 | 121.7102 | -0.29755 | -121.9391
625.0625 | 121.8521 | -121.6553 | 0.12817 | -0.091553 | 0.0255 | 0.0092584 | 0.025438 | 0.0031275 | 0.066488 | 0.089247 | 0.041199 | 0.10071 | -0.21057 | -0.018311 | -121.6187 | -0.027466 | -0.14648 | 0.036621 | 0.12817 | -121.9391 | 121.4447 | -0.027466 | 121.6965 | 121.637 | -121.7468 | -0.28381 | 0 | 0.25177 | 121.5088 | 121.6919 | 0.036621 | 121.756 | 121.6965 | 121.7834 | 121.6278 | -0.28381 | 121.756 | 121.6965 | 121.6278 | 0.036621 | 121.7834 | -0.33875 | -122.0673
626.125 | 122.0352 | -121.7285 | 0.11902 | 0.083923 | 0.020373 | 0.012036 | 0.023516 | 0.0022729 | 0.066702 | 0.091811 | 0.054932 | 0.064087 | -0.1831 | 0.027466 | -121.6507 | 0.086975 | -6.9717 | 0.13733 | 0.1236 | -121.9437 | 121.5454 | -0.054932 | 121.7834 | 121.756 | -121.7697 | -0.21515 | 0.004577 | 0.23804 | 114.7568 | 121.8658 | 0.07782 | 121.7926 | 121.7834 | 121.8521 | 121.8155 | -0.21515 | 121.7926 | 121.7834 | 121.8155 | 0.07782 | 121.8521 | -0.30212 | -122.0627
627.0625 | 122.0215 | -121.7972 | 0.14191 | -0.31281 | 0.022937 | 0.0090448 | 0.022875 | -0.0034949 | 0.068197 | 0.091597 | 0.050354 | 0.073242 | -0.17853 | 0.045776 | -121.7056 | 0.045776 | -7.2144 | 0.16022 | 0.12817 | -122.0261 | 121.6187 | -0.068665 | 121.8475 | 121.843 | -121.8475 | -0.22888 | -0.013733 | 0.22888 | 114.5828 | 121.9574 | 0.091553 | 121.8704 | 121.8475 | 121.9254 | 121.843 | -0.22888 | 121.8704 | 121.8475 | 121.843 | 0.091553 | 121.9254 | -0.32044 | -122.168
628.1094 | 122.1176 | -121.788 | 0.15106 | -0.26703 | 0.021441 | 0.0073358 | 0.02437 | -0.0013587 | 0.067556 | 0.092238 | 0.050354 | 0.073242 | -0.1831 | 0.059509 | -121.7102 | 0.082397 | -7.2922 | 0.17395 | 0.13733 | -122.0261 | 121.6049 | -0.07782 | 121.8384 | 121.8475 | -121.8613 | -0.23804 | -0.013733 | 0.23346 | 114.4959 | 121.962 | 0.07782 | 121.8613 | 121.8384 | 121.9254 | 121.8704 | -0.23804 | 121.8613 | 121.8384 | 121.8704 | 0.07782 | 121.9254 | -0.33417 | -122.1771
629.0625 | 122.081 | -121.8567 | 0.16479 | -0.22125 | 0.022082 | 0.010967 | 0.032701 | -0.0011451 | 0.064993 | 0.09352 | 0.041199 | 0.091553 | -0.21973 | 0.027466 | -121.7926 | 0.032043 | -6.9534 | 0.10986 | 0.15564 | -122.1039 | 121.637 | -0.073242 | 121.8979 | 121.8842 | -121.9574 | -0.24719 | -0.009155 | 0.26093 | 114.9033 | 121.9666 | 0.064086 | 121.9482 | 121.8979 | 122.0123 | 121.8887 | -0.24719 | 121.9482 | 121.8979 | 121.8887 | 0.064086 | 122.0123 | -0.38452 | -122.2687
630.0625 | 122.1313 | -121.8842 | 0.15106 | -0.20599 | 0.024646 | 0.0096856 | 0.030779 | 0.0031275 | 0.06542 | 0.091597 | 0.032043 | 0.091553 | -0.2243 | 0.032043 | -121.8155 | 0.032043 | -6.7062 | 0.10529 | 0.13275 | -122.113 | 121.6599 | -0.059509 | 121.9162 | 121.9162 | -121.9666 | -0.22888 | -0.018311 | 0.25635 | 115.1779 | 121.9894 | 0.068664 | 121.9757 | 121.9162 | 122.0169 | 121.9162 | -0.22888 | 121.9757 | 121.9162 | 121.9162 | 0.068664 | 122.0169 | -0.37537 | -122.2641
631.125 | 122.2366 | -121.8567 | 0.12817 | -0.16785 | 0.018664 | 0.0092584 | 0.024156 | 0.00056394 | 0.066702 | 0.091811 | 0.10529 | 0.050354 | -0.15564 | 0.091553 | -121.7239 | 0.13275 | -6.7566 | 0.21973 | 0.1236 | -122.0947 | 121.701 | -0.07782 | 121.962 | 121.9482 | -121.8521 | -0.23804 | -0.004578 | 0.26093 | 115.1001 | 122.0764 | 0.13275 | 121.907 | 121.962 | 121.9803 | 121.9894 | -0.23804 | 121.907 | 121.962 | 121.9894 | 0.13275 | 121.9803 | -0.28381 | -122.2229
632.0625 | 121.3715 | -121.1197 | 0.18768 | -0.28992 | 0.033404 | 0.007763 | 0.016893 | -0.0013587 | 0.0024011 | 0.026442 | -0.041199 | 0.10986 | -0.20599 | -120.8817 | -120.9274 | -121.312 | -5.2826 | -120.9274 | -8.8669 | -121.3898 | 120.9137 | -0.07782 | 121.0785 | 0.23804 | -121.1151 | -0.27008 | -9.0546 | 0.1648 | 115.8371 | 0.19226 | 0.19226 | 121.2296 | 121.0785 | 112.2528 | -0.19226 | -0.27008 | 121.2296 | 121.0785 | -0.19226 | 0.19226 | 112.2528 | -0.39368 | -121.5775
633.1094 | 121.6553 | -121.4905 | 0.16479 | -0.28992 | 0.024859 | 0.0079768 | 0.019243 | -0.00071786 | 0.0024011 | 0.017684 | -0.013733 | 0.091553 | -0.20599 | -121.5454 | -121.4539 | -121.7148 | -113.6902 | -121.3898 | -8.8669 | -121.7102 | 121.2845 | -0.073242 | 121.4767 | -0.054931 | -121.6187 | -0.21973 | -9.0317 | 0.19226 | 7.8003 | 0.10071 | 0.036622 | 121.582 | 121.4767 | 112.6236 | -0.2243 | -0.21973 | 121.582 | 121.4767 | -0.2243 | 0.036622 | 112.6236 | -0.37079 | -121.875
634.0625 | 121.4127 | -20.9885 | 100.4425 | -0.25177 | 0.0077695 | 0.0069086 | 0.01433 | -0.00071786 | -0.00080328 | 0.025374 | 0.1236 | 0.050354 | -0.20142 | -0.64087 | -1.3962 | -0.55847 | -0.75989 | -1.3046 | -1.387 | -21.3226 | 20.787 | -100.3922 | 21.1121 | 20.3476 | -101.8387 | -0.33417 | -101.8295 | 0.32501 | 20.2286 | 19.6838 | 19.5923 | 21.0388 | 21.1121 | 19.6014 | 20.43 | -0.33417 | 21.0388 | 21.1121 | 20.43 | 19.5923 | 19.6014 | -100.6439 | -121.7651
635.125 | 121.3852 | -19.8486 | 101.5045 | -0.0076296 | 0.015246 | 0.011395 | 0.023729 | 0.00056394 | 0.0024011 | 0.024306 | 0.013733 | 0.091553 | -0.21057 | -1.1032 | -1.1307 | -1.1124 | -1.03 | -1.0345 | -0.94299 | -20.4666 | 19.6381 | -101.413 | 19.8624 | 18.7454 | -102.6352 | -0.61798 | -102.4475 | 0.2243 | 18.8187 | 18.8141 | 18.718 | 19.9402 | 19.8624 | 18.9056 | 18.7363 | -0.61798 | 19.9402 | 19.8624 | 18.7363 | 18.718 | 18.9056 | -101.7151 | -121.9711
636.0625 | 121.8567 | -20.1416 | 101.6098 | -0.31281 | 0.0092649 | 0.0058404 | 0.01732 | 0.00056394 | -0.0014441 | 0.024092 | 0.009155 | 0.082397 | -0.19684 | -1.181 | -1.6022 | -1.1673 | -1.0895 | -1.5106 | -1.4328 | -20.3384 | 19.9448 | -101.5274 | 20.1508 | 18.9606 | -103.212 | -0.19684 | -103.0426 | 0.20599 | 19.0521 | 18.631 | 18.5394 | 20.224 | 20.1508 | 18.7088 | 18.9743 | -0.19684 | 20.224 | 20.1508 | 18.9743 | 18.5394 | 18.7088 | -101.8066 | -121.9482
637.125 | 121.9482 | -19.1666 | 102.5482 | -0.23651 | 0.0084103 | 0.0062678 | 0.017961 | -0.0011451 | -0.00016228 | 0.02452 | 0.07782 | 0.054932 | -0.16937 | -1.1765 | -1.1673 | -1.1444 | -1.355 | -0.99792 | -1.1536 | -19.3039 | 18.9972 | -102.4933 | 19.2444 | 17.9901 | -103.7155 | -0.13733 | -103.7018 | 0.24719 | 17.8116 | 18.1686 | 17.9993 | 19.2215 | 19.2444 | 18.013 | 18.0222 | -0.13733 | 19.2215 | 19.2444 | 18.0222 | 17.9993 | 18.013 | -102.7176 | -121.8521
638.0625 | 121.9254 | -19.1208 | 102.626 | -0.27466 | 0.01076 | 0.008404 | 0.021379 | -0.0041357 | 0.00047852 | 0.024092 | -0.027466 | 0.09613 | -0.21057 | -1.5884 | -1.5884 | -1.5976 | -1.4603 | -1.4969 | -1.4008 | -19.2993 | 18.9102 | -102.5299 | 19.0933 | 17.5323 | -104.2145 | -0.17853 | -104.0268 | 0.18311 | 17.6605 | 17.6239 | 17.5323 | 19.2169 | 19.0933 | 17.72 | 17.5232 | -0.17853 | 19.2169 | 19.0933 | 17.5232 | 17.5323 | 17.72 | -102.8366 | -121.9254
639.1094 | 121.9025 | -19.2215 | 102.6398 | -0.16785 | 0.011188 | 0.0069086 | 0.018389 | -0.00050406 | 0.0013329 | 0.023451 | -0.027466 | 0.10529 | -0.21515 | -1.4603 | -1.474 | -1.4603 | -1.3596 | -1.3733 | -1.3 | -19.4275 | 19.0063 | -102.5345 | 19.194 | 17.7612 | -104.1138 | -0.20599 | -103.9398 | 0.18768 | 17.8619 | 17.8482 | 17.7475 | 19.3268 | 19.194 | 17.9214 | 17.7612 | -0.20599 | 19.3268 | 19.194 | 17.7612 | 17.7475 | 17.9214 | -102.8549 | -122.0673
640.0781 | 121.9803 | -19.1299 | 102.6718 | -0.076294 | 0.010974 | 0.0081904 | 0.022661 | 0.0020593 | -0.00080328 | 0.023238 | 0.045776 | 0.091553 | -0.009155 | -1.4328 | -1.5244 | -1.4648 | -1.4511 | -1.4236 | -1.3687 | -19.2947 | 19.1208 | -102.5803 | 19.1757 | 17.6971 | -104.1962 | -0.1648 | -104.0405 | 0.054931 | 17.6788 | 17.7063 | 17.6056 | 19.2215 | 19.1757 | 17.7612 | 17.6651 | -0.1648 | 19.2215 | 19.1757 | 17.6651 | 17.6056 | 17.7612 | -102.681 | -121.9666
641.1094 | 121.9986 | -19.0567 | 102.7817 | -0.18311 | 0.011401 | 0.013104 | 0.022875 | -0.00029046 | -0.00058968 | 0.024092 | 0.022888 | 0.07782 | -0.20599 | -1.6022 | -1.6663 | -1.6251 | -1.6434 | -1.5747 | -1.5472 | -19.1711 | 18.8507 | -102.7039 | 19.0796 | 17.4545 | -104.4479 | -0.11444 | -104.3289 | 0.22888 | 17.4133 | 17.482 | 17.3904 | 19.1345 | 19.0796 | 17.5095 | 17.4316 | -0.11444 | 19.1345 | 19.0796 | 17.4316 | 17.3904 | 17.5095 | -102.9877 | -121.9528
642.0625 | 122.0078 | -18.9148 | 102.9099 | -0.26703 | 0.010119 | 0.009472 | 0.017748 | 0.00035034 | -0.00080328 | 0.021315 | 0.036621 | 0.07782 | -0.16937 | -1.6708 | -1.6525 | -1.6434 | -1.6525 | -1.5564 | -1.561 | -19.075 | 18.7454 | -102.832 | 18.9514 | 17.244 | -104.5624 | -0.16022 | -104.4708 | 0.20599 | 17.2623 | 17.3584 | 17.2623 | 18.9926 | 18.9514 | 17.3538 | 17.2714 | -0.16022 | 18.9926 | 18.9514 | 17.2714 | 17.2623 | 17.3538 | -103.0792 | -121.9849
643.0625 | 121.8063 | -4.39 | 117.5446 | -0.29755 | 0.0090511 | 0.008404 | 0.018816 | -0.0013587 | -0.0010169 | 0.026442 | 0.068665 | 0.054932 | -0.17853 | -1.9089 | -1.9272 | -1.9043 | -1.9638 | -1.8173 | -1.8448 | -4.5364 | 4.2114 | -117.4896 | 4.4586 | 2.4811 | -119.4717 | -0.14648 | -119.3893 | 0.24719 | 2.4261 | 2.5726 | 2.4628 | 4.4449 | 4.4586 | 2.5452 | 2.4857 | -0.14648 | 4.4449 | 4.4586 | 2.4857 | 2.4628 | 2.5452 | -117.7231 | -122.081
644.125 | 122.113 | -4.4724 | 117.4438 | -0.083924 | 0.0099057 | 0.0071222 | 0.016893 | -0.0022131 | 5.1318e-05 | 0.026229 | 0.041199 | 0.054932 | -0.19226 | -2.0142 | -2.005 | -1.9592 | -2.1286 | -1.8723 | -1.9318 | -4.6097 | 4.2801 | -117.3889 | 4.5135 | 2.4582 | -119.4489 | -0.13733 | -119.3756 | 0.23346 | 2.3437 | 2.6001 | 2.4673 | 4.5273 | 4.5135 | 2.5406 | 2.5131 | -0.13733 | 4.5273 | 4.5135 | 2.5131 | 2.4673 | 2.5406 | -117.6361 | -122.0535
645.0625 | 121.8201 | -4.5456 | 117.4255 | -0.076294 | 0.011615 | 0.010113 | 0.028856 | -0.0015723 | 0.00069212 | 0.025588 | 0.059509 | 0.10071 | -0.17853 | -2.0279 | -2.0599 | -2.0325 | -2.0874 | -1.9684 | -1.9226 | -4.6875 | 4.3671 | -117.3248 | 4.6051 | 2.5177 | -119.4855 | -0.14191 | -119.3481 | 0.23804 | 2.4582 | 2.5772 | 2.4857 | 4.6463 | 4.6051 | 2.623 | 2.5131 | -0.14191 | 4.6463 | 4.6051 | 2.5131 | 2.4857 | 2.623 | -117.6041 | -122.113
646.1094 | 122.1405 | -4.5685 | 117.3752 | -0.10681 | 0.0090511 | 0.00028617 | 0.016039 | -0.0011451 | -0.00016228 | 0.027083 | 0.050354 | 0.050354 | -0.16479 | -2.0645 | -2.037 | -2.0187 | -2.1973 | -1.9226 | -1.9821 | -4.7012 | 4.4037 | -117.3248 | 4.6188 | 2.504 | -119.4122 | -0.13275 | -119.3573 | 0.21515 | 2.3712 | 2.6459 | 2.5314 | 4.6188 | 4.6188 | 2.5864 | 2.5497 | -0.13275 | 4.6188 | 4.6188 | 2.5497 | 2.5314 | 2.5864 | -117.54 | -122.0764
647.0625 | 122.1451 | -4.7241 | 117.1921 | -0.2594 | 0.0094785 | 0.0062678 | 0.021379 | -0.0017859 | -0.00016228 | 0.025801 | -0.07782 | 0.036621 | -0.1831 | -2.0554 | -2.124 | -2.0828 | -2.243 | -1.9684 | -2.0599 | -4.9072 | 4.541 | -117.1555 | 4.6463 | 2.6688 | -119.3161 | -0.18311 | -119.252 | 0.10528 | 2.4811 | 2.7557 | 2.6001 | 4.7607 | 4.6463 | 2.6642 | 2.6413 | -0.18311 | 4.7607 | 4.6463 | 2.6413 | 2.6001 | 2.6642 | -117.3752 | -122.0993
648.1094 | 122.1268 | -4.01 | 117.9199 | -0.015259 | 0.011188 | 0.004986 | 0.018175 | -0.0030677 | -0.0012305 | 0.027297 | 0.027466 | 0.045776 | -0.11902 | -2.0279 | -2.0142 | -1.9821 | -2.1606 | -1.9135 | -1.9592 | -4.1702 | 3.891 | -117.8741 | 4.0375 | 1.9821 | -119.9341 | -0.16022 | -119.8792 | 0.14649 | 1.8494 | 2.0966 | 1.9959 | 4.0558 | 4.0375 | 2.0508 | 2.0279 | -0.16022 | 4.0558 | 4.0375 | 2.0279 | 1.9959 | 2.0508 | -118.0389 | -122.0901
649.0625 | 122.1268 | -2.1973 | 119.8059 | -0.35858 | 0.0062741 | 0.0079768 | 0.020525 | -0.0026405 | -0.0016577 | 0.027297 | 0.068665 | 0.045776 | -0.15564 | -2.0462 | -2.0325 | -2.0325 | -2.1561 | -1.918 | -1.9821 | -2.3392 | 2.0416 | -119.7601 | 2.2659 | 0.15106 | -121.8384 | -0.14191 | -121.788 | 0.22431 | 0.041199 | 0.27924 | 0.16479 | 2.243 | 2.2659 | 0.21515 | 0.16479 | -0.14191 | 2.243 | 2.2659 | 0.16479 | 0.16479 | 0.21515 | -119.9615 | -122.1451
650.1094 | 122.0901 | -2.211 | 119.8334 | -0.32043 | 0.012683 | 0.010113 | 0.020952 | -0.00071786 | 0.0024011 | 0.027724 | 0.041199 | 0.073242 | -0.1831 | -2.1011 | -2.092 | -2.1103 | -2.0828 | -1.9867 | -1.9638 | -2.3438 | 2.0279 | -119.7601 | 2.2522 | 0.10986 | -121.9254 | -0.13275 | -121.7972 | 0.2243 | 0.12817 | 0.22431 | 0.11902 | 2.2842 | 2.2522 | 0.24719 | 0.10071 | -0.13275 | 2.2842 | 2.2522 | 0.10071 | 0.11902 | 0.24719 | -120.0165 | -122.1771
651.0625 | 122.1771 | -2.1378 | 119.87 | -0.27466 | 0.011188 | 0.0064814 | 0.023088 | -0.0032813 | 0.0013329 | 0.027083 | -0.16022 | 0.050354 | -0.1831 | -2.0096 | -2.0599 | -2.0187 | -2.1881 | -1.8951 | -1.9867 | -2.2797 | 1.9547 | -119.8196 | 1.9775 | 0.12817 | -121.9299 | -0.14191 | -121.8567 | 0.022888 | -0.050354 | 0.24261 | 0.077819 | 2.1881 | 1.9775 | 0.15106 | 0.11902 | -0.14191 | 2.1881 | 1.9775 | 0.11902 | 0.077819 | 0.15106 | -120.0531 | -122.1497
652.125 | 122.168 | -2.2385 | 119.8105 | -0.076294 | 0.0094785 | 0.0071222 | 0.017107 | -0.0049903 | -0.0016577 | 0.025801 | 0.018311 | 0.050354 | -0.14648 | -2.1423 | -2.124 | -2.092 | -2.1835 | -1.9958 | -2.0325 | -2.3117 | 2.092 | -119.7601 | 2.2568 | 0.09613 | -121.9345 | -0.073243 | -121.843 | 0.16479 | 0.054931 | 0.24261 | 0.11444 | 2.2888 | 2.2568 | 0.20599 | 0.14648 | -0.073243 | 2.2888 | 2.2568 | 0.14648 | 0.11444 | 0.20599 | -119.957 | -122.1222
653.0781 | 122.049 | -1.886 | 120.2042 | -6e-08 | 0.010119 | 0.010327 | 0.024584 | -0.00071786 | 0.0011193 | 0.028792 | 0.004578 | 0.10529 | -0.20142 | -1.8265 | -1.8631 | -1.8219 | -1.7715 | -1.7624 | -1.6434 | -2.0462 | 1.6846 | -120.0989 | 1.8906 | 0.059509 | -122.0673 | -0.16022 | -121.8475 | 0.20599 | 0.11444 | 0.1236 | 0.022888 | 1.9913 | 1.8906 | 0.24261 | 0.064087 | -0.16022 | 1.9913 | 1.8906 | 0.064087 | 0.022888 | 0.24261 | -120.4056 | -122.2504
654.1094 | 122.2137 | -1.8677 | 120.1355 | -0.20599 | 0.0096921 | 0.007763 | 0.015612 | -0.0030677 | 5.1318e-05 | 0.028151 | 0.041199 | 0.07782 | -0.15106 | -1.7395 | -1.7487 | -1.712 | -1.8951 | -1.6205 | -1.7029 | -1.9913 | 1.7166 | -120.0577 | 1.9089 | 0.12817 | -121.8842 | -0.1236 | -121.8384 | 0.19226 | -0.027466 | 0.24719 | 0.11902 | 1.9455 | 1.9089 | 0.16479 | 0.15564 | -0.1236 | 1.9455 | 1.9089 | 0.15564 | 0.11902 | 0.16479 | -120.2866 | -122.1268
655.0625 | 122.0718 | -1.9318 | 120.1904 | -0.3891 | 0.010547 | 0.011181 | 0.022661 | -0.0026405 | -0.00016228 | 0.027938 | 0.022888 | 0.14191 | -0.13733 | -1.8265 | -1.8127 | -1.8173 | -1.7349 | -1.7212 | -1.6571 | -2.0462 | 1.7944 | -120.0485 | 1.9547 | 0.10529 | -122.0032 | -0.11444 | -121.8475 | 0.16022 | 0.19684 | 0.21057 | 0.11902 | 2.0737 | 1.9547 | 0.27466 | 0.11444 | -0.11444 | 2.0737 | 1.9547 | 0.11444 | 0.11902 | 0.27466 | -120.3278 | -122.2366
656.125 | 122.1771 | -1.8539 | 120.2225 | -0.030518 | 0.0079831 | 0.0060542 | 0.015398 | -0.0034949 | 0.00069212 | 0.024947 | 0.013733 | 0.045776 | -0.15106 | -1.8356 | -1.7395 | -1.7303 | -1.8494 | -1.6251 | -1.6708 | -1.9455 | 1.7029 | -120.1767 | 1.8677 | 0.018311 | -121.962 | -0.091553 | -121.8933 | 0.16479 | 0.004578 | 0.22888 | 0.11444 | 1.8997 | 1.8677 | 0.18311 | 0.1236 | -0.091553 | 1.8997 | 1.8677 | 0.1236 | 0.11444 | 0.18311 | -120.3735 | -122.168
657.0625 | 122.2504 | -1.7715 | 120.2682 | -0.23651 | 0.010119 | 0.0060542 | 0.01732 | -0.0030677 | -0.0012305 | 0.026656 | 0.073242 | 0.050354 | -0.14648 | -1.6251 | -1.6205 | -1.593 | -1.8082 | -1.4923 | -1.6022 | -1.8997 | 1.6251 | -120.2179 | 1.8448 | 0.14648 | -121.8887 | -0.12817 | -121.8704 | 0.21973 | -0.036622 | 0.27923 | 0.15106 | 1.8219 | 1.8448 | 0.16937 | 0.17853 | -0.12817 | 1.8219 | 1.8448 | 0.17853 | 0.15106 | 0.16937 | -120.4147 | -122.168
658.125 | 122.1725 | -1.8082 | 120.2545 | -0.053406 | 0.0099057 | 0.0096856 | 0.018602 | -0.0039221 | 0.0024011 | 0.028151 | 0.032043 | 0.064087 | -0.15564 | -1.7258 | -1.7258 | -1.6846 | -1.8127 | -1.593 | -1.6251 | -1.9592 | 1.6525 | -120.1904 | 1.8402 | 0.082398 | -121.9803 | -0.15106 | -121.8796 | 0.18768 | -0.004577 | 0.21515 | 0.082398 | 1.8723 | 1.8402 | 0.18311 | 0.1236 | -0.15106 | 1.8723 | 1.8402 | 0.1236 | 0.082398 | 0.18311 | -120.4102 | -122.2137
659.0625 | 122.2504 | -1.7532 | 120.2957 | -0.23651 | 0.0073423 | 0.0090448 | 0.018175 | -0.0028541 | -0.0010169 | 0.027724 | 0.073242 | 0.059509 | -0.15106 | -1.6067 | -1.6022 | -1.5747 | -1.8219 | -1.4648 | -1.6067 | -1.8906 | 1.6022 | -120.2362 | 1.8265 | 0.14649 | -121.8979 | -0.13733 | -121.9025 | 0.2243 | -0.068664 | 0.28839 | 0.15106 | 1.8127 | 1.8265 | 0.14649 | 0.17853 | -0.13733 | 1.8127 | 1.8265 | 0.17853 | 0.15106 | 0.14649 | -120.4468 | -122.1863
660.125 | 122.2458 | -1.7395 | 120.3278 | -0.27466 | 0.0090511 | 0.0062678 | 0.022661 | -0.0017859 | 0.0026147 | 0.025374 | 0.022888 | 0.041199 | -0.16479 | -1.561 | -1.6251 | -1.6113 | -1.7624 | -1.4694 | -1.5747 | -1.8631 | 1.5747 | -120.2866 | 1.7624 | 0.17853 | -121.9528 | -0.1236 | -121.9025 | 0.18768 | -0.022888 | 0.27008 | 0.11444 | 1.7807 | 1.7624 | 0.1648 | 0.12817 | -0.1236 | 1.7807 | 1.7624 | 0.12817 | 0.11444 | 0.1648 | -120.4926 | -122.1909
661.0625 | 122.2458 | -1.712 | 120.3278 | -0.12207 | 0.0086239 | 0.0060542 | 0.017961 | -0.0043495 | -0.0012305 | 0.026869 | 0.054932 | 0.064087 | -0.16022 | -1.5839 | -1.5839 | -1.5747 | -1.7715 | -1.4603 | -1.5656 | -1.8402 | 1.5518 | -120.2637 | 1.767 | 0.12817 | -121.9116 | -0.12817 | -121.8933 | 0.21515 | -0.059509 | 0.25177 | 0.12817 | 1.7761 | 1.767 | 0.14648 | 0.13733 | -0.12817 | 1.7761 | 1.767 | 0.13733 | 0.12817 | 0.14648 | -120.488 | -122.168
662.1094 | 122.2458 | -1.7075 | 120.3369 | 0.15259 | 0.0092649 | 0.007763 | 0.022661 | -0.00093146 | -0.0014441 | 0.027724 | 0.086975 | 0.036621 | -0.17853 | -1.5289 | -1.5427 | -1.5244 | -1.7944 | -1.4374 | -1.5335 | -1.8127 | 1.5289 | -120.3003 | 1.7944 | 0.17853 | -121.8796 | -0.10529 | -121.8704 | 0.2655 | -0.086976 | 0.27008 | 0.16479 | 1.7441 | 1.7944 | 0.17395 | 0.1831 | -0.10529 | 1.7441 | 1.7944 | 0.1831 | 0.16479 | 0.17395 | -120.5154 | -122.1497
663.0781 | 122.113 | -1.8311 | 120.3369 | -0.015259 | 0.012256 | 0.010754 | 0.027147 | -0.0011451 | 0.0013329 | 0.026015 | 0.004578 | 0.07782 | -0.1831 | -1.7487 | -1.7532 | -1.7487 | -1.6937 | -1.6891 | -1.5884 | -1.9455 | 1.648 | -120.2591 | 1.8356 | 0.082398 | -122.0901 | -0.11444 | -121.9254 | 0.18768 | 0.13733 | 0.14191 | 0.07782 | 1.9089 | 1.8356 | 0.24262 | 0.082398 | -0.11444 | 1.9089 | 1.8356 | 0.082398 | 0.07782 | 0.24262 | -120.52 | -122.2824
664.1094 | 122.1222 | -1.7853 | 120.3369 | 0.12207 | 0.012469 | 0.011395 | 0.022875 | 0.0048363 | -0.0018713 | 0.026442 | -0.036621 | 0.082397 | -0.20599 | -1.5839 | -1.5884 | -1.6983 | -1.7212 | -1.5976 | -1.5518 | -1.8997 | 1.5793 | -120.2545 | 1.7487 | 0.20142 | -121.9254 | -0.11444 | -121.8887 | 0.16937 | 0.064087 | 0.18768 | 0.19684 | 1.8677 | 1.7487 | 0.23346 | 0.086975 | -0.11444 | 1.8677 | 1.7487 | 0.086975 | 0.19684 | 0.23346 | -120.5429 | -122.2366
665.0625 | 122.1542 | -1.8402 | 120.2911 | -0.2594 | 0.011401 | 0.0096856 | 0.020311 | -0.00071786 | 0.00026492 | 0.028365 | -0.022888 | 0.10071 | -0.20599 | -1.7532 | -1.7532 | -1.767 | -1.6479 | -1.68 | -1.5884 | -1.9638 | 1.6342 | -120.1904 | 1.8173 | 0.086975 | -122.0444 | -0.1236 | -121.8796 | 0.18311 | 0.19226 | 0.16022 | 0.086975 | 1.9409 | 1.8173 | 0.25177 | 0.073242 | -0.1236 | 1.9409 | 1.8173 | 0.073242 | 0.086975 | 0.25177 | -120.4971 | -122.2549
666.1094 | 122.2275 | -1.799 | 120.3232 | -0.091553 | 0.0062741 | 0.0079768 | 0.014757 | -0.0013587 | 0.00069212 | 0.02452 | 0 | 0.064087 | -0.16937 | -1.8036 | -1.6754 | -1.6434 | -1.8036 | -1.5793 | -1.6022 | -1.886 | 1.6296 | -120.2591 | 1.799 | -0.004578 | -121.9986 | -0.086975 | -121.9254 | 0.16937 | -0.004578 | 0.21973 | 0.1236 | 1.8631 | 1.799 | 0.19684 | 0.15564 | -0.086975 | 1.8631 | 1.799 | 0.15564 | 0.1236 | 0.19684 | -120.4926 | -122.2092
667.0625 | 122.3007 | -1.767 | 120.2682 | -0.22888 | 0.0094785 | 0.0064814 | 0.017748 | -0.0017859 | -0.0012305 | 0.027724 | 0.082397 | 0.064087 | -0.13733 | -1.6251 | -1.6113 | -1.5884 | -1.8402 | -1.506 | -1.6251 | -1.9043 | 1.6296 | -120.2042 | 1.8494 | 0.14191 | -121.8796 | -0.13733 | -121.8933 | 0.21973 | -0.073242 | 0.26093 | 0.15564 | 1.8311 | 1.8494 | 0.14191 | 0.17853 | -0.13733 | 1.8311 | 1.8494 | 0.17853 | 0.15564 | 0.14191 | -120.4056 | -122.1725
668.125 | 122.3145 | -1.7899 | 120.3003 | -0.16785 | 0.0096921 | 0.0079768 | 0.019029 | -0.0062721 | 0.00090572 | 0.028365 | 0.091553 | 0.064087 | -0.13733 | -1.6159 | -1.6251 | -1.6022 | -1.8402 | -1.4923 | -1.6251 | -1.9135 | 1.6525 | -120.2362 | 1.8814 | 0.17395 | -121.9254 | -0.1236 | -121.9254 | 0.22888 | -0.050354 | 0.29755 | 0.16479 | 1.8539 | 1.8814 | 0.16479 | 0.18768 | -0.1236 | 1.8539 | 1.8814 | 0.18768 | 0.16479 | 0.16479 | -120.4376 | -122.2137
669.0625 | 122.2137 | -1.8173 | 120.3049 | -0.053406 | 0.010119 | 0.0060542 | 0.015825 | -0.0034949 | -0.0012305 | 0.029219 | 0.009155 | 0.059509 | -0.16937 | -1.7303 | -1.7303 | -1.6937 | -1.8219 | -1.6159 | -1.6525 | -1.9363 | 1.6479 | -120.2454 | 1.8265 | 0.086975 | -122.0352 | -0.11902 | -121.9574 | 0.17853 | -0.004577 | 0.20142 | 0.086975 | 1.8768 | 1.8265 | 0.1648 | 0.1236 | -0.11902 | 1.8768 | 1.8265 | 0.1236 | 0.086975 | 0.1648 | -120.4742 | -122.2412
670.125 | 122.2504 | -2.1194 | 120.0027 | 0.053406 | 0.0081967 | 0.0092584 | 0.020738 | -0.0049903 | 0.0015467 | 0.027938 | 0.054932 | 0.036621 | -0.15564 | -2.0096 | -2.0187 | -1.9958 | -2.1606 | -1.9272 | -1.9501 | -2.2476 | 1.9638 | -119.9661 | 2.1744 | 0.10986 | -122.0215 | -0.12817 | -121.9528 | 0.21057 | -0.041199 | 0.19226 | 0.10071 | 2.1561 | 2.1744 | 0.16937 | 0.1236 | -0.12817 | 2.1561 | 2.1744 | 0.1236 | 0.10071 | 0.16937 | -120.1584 | -122.2504
671.0625 | 122.3053 | -1.9135 | 120.1447 | -0.21362 | 0.0096921 | 0.0069086 | 0.019884 | -0.0026405 | 0.00090572 | 0.028151 | 0.068665 | 0.050354 | -0.14191 | -1.7761 | -1.7624 | -1.7441 | -2.0004 | -1.6342 | -1.7807 | -2.0645 | 1.7715 | -120.0943 | 1.9821 | 0.13733 | -121.907 | -0.15106 | -121.9254 | 0.21057 | -0.086975 | 0.27924 | 0.15106 | 1.9638 | 1.9821 | 0.13275 | 0.16937 | -0.15106 | 1.9638 | 1.9821 | 0.16937 | 0.15106 | 0.13275 | -120.2866 | -122.2092
672.1094 | 122.2595 | -1.9272 | 120.2133 | -0.1297 | 0.0086239 | 0.006695 | 0.018175 | -0.0024267 | 0.0024011 | 0.028365 | 0.041199 | 0.045776 | -0.13275 | -1.8311 | -1.8219 | -1.7944 | -1.9501 | -1.7075 | -1.7487 | -2.0691 | 1.7944 | -120.1675 | 1.9684 | 0.09613 | -122.0352 | -0.14191 | -121.962 | 0.17395 | -0.022888 | 0.21973 | 0.10529 | 1.973 | 1.9684 | 0.17853 | 0.13275 | -0.14191 | 1.973 | 1.9684 | 0.13275 | 0.10529 | 0.17853 | -120.3461 | -122.2824
673.0625 | 122.3053 | -1.9363 | 120.1492 | -0.16022 | 0.0090511 | 0.0098994 | 0.017534 | -0.0049903 | -0.0010169 | 0.026442 | 0.059509 | 0.059509 | -0.14648 | -1.799 | -1.8082 | -1.767 | -1.9913 | -1.6663 | -1.7761 | -2.0554 | 1.7899 | -120.0897 | 1.9958 | 0.13733 | -121.9574 | -0.11902 | -121.9254 | 0.20599 | -0.054932 | 0.27008 | 0.12817 | 1.9958 | 1.9958 | 0.16022 | 0.16937 | -0.11902 | 1.9958 | 1.9958 | 0.16937 | 0.12817 | 0.16022 | -120.2957 | -122.2046
674.125 | 122.2504 | -1.8951 | 120.2591 | 0.061035 | 0.011828 | 0.0062678 | 0.017107 | -0.0039221 | -0.0018713 | 0.026869 | 0.054932 | 0.050354 | -0.16937 | -1.7853 | -1.799 | -1.7624 | -1.9363 | -1.6846 | -1.7258 | -2.0233 | 1.7258 | -120.2087 | 1.9501 | 0.10986 | -122.0581 | -0.12817 | -121.9849 | 0.22431 | -0.041198 | 0.21057 | 0.096131 | 1.9455 | 1.9501 | 0.16937 | 0.13275 | -0.12817 | 1.9455 | 1.9501 | 0.13275 | 0.096131 | 0.16937 | -120.4285 | -122.2824
675.0625 | 122.287 | -1.9821 | 120.1401 | -0.1297 | 0.0081967 | 0.0096856 | 0.017748 | -0.0026405 | -0.0010169 | 0.026442 | 0.054932 | 0.064087 | -0.14648 | -1.8539 | -1.8585 | -1.8356 | -2.0096 | -1.7395 | -1.8127 | -2.1103 | 1.8356 | -120.076 | 2.037 | 0.12817 | -121.9986 | -0.12817 | -121.9528 | 0.20142 | -0.027466 | 0.24261 | 0.1236 | 2.0462 | 2.037 | 0.16937 | 0.14648 | -0.12817 | 2.0462 | 2.037 | 0.14648 | 0.1236 | 0.16937 | -120.2866 | -122.2504
676.1094 | 122.3053 | -1.9684 | 120.1401 | 0.19073 | 0.010547 | 0.0079768 | 0.023943 | -0.0028541 | 5.1318e-05 | 0.026869 | 0.10071 | 0.027466 | -0.16479 | -1.8402 | -1.8494 | -1.8173 | -2.0737 | -1.7441 | -1.8082 | -2.1057 | 1.8036 | -120.1126 | 2.0691 | 0.12817 | -121.9894 | -0.13733 | -121.9482 | 0.2655 | -0.10529 | 0.2243 | 0.11902 | 1.9958 | 2.0691 | 0.16022 | 0.15106 | -0.13733 | 1.9958 | 2.0691 | 0.15106 | 0.11902 | 0.16022 | -120.3049 | -122.2458
677.0625 | 122.2778 | -1.9958 | 120.1538 | -6e-08 | 0.0088375 | 0.004986 | 0.016893 | -0.0034949 | 0.00069212 | 0.02516 | 0.018311 | 0.022888 | -0.09613 | -1.8997 | -1.8768 | -1.8494 | -2.0142 | -1.7624 | -1.8265 | -2.1194 | 1.8997 | -120.1309 | 2.0142 | 0.096131 | -122.0306 | -0.1236 | -121.9803 | 0.11444 | -0.01831 | 0.23346 | 0.11902 | 2.0187 | 2.0142 | 0.16937 | 0.14648 | -0.1236 | 2.0187 | 2.0142 | 0.14648 | 0.11902 | 0.16937 | -120.2499 | -122.2733
678.1094 | 122.2595 | -2.0279 | 120.1126 | -0.015259 | 0.010119 | 0.0098994 | 0.019457 | -0.0030677 | 0.00047852 | 0.026869 | 0.018311 | 0.054932 | -0.16479 | -1.9363 | -1.9226 | -1.9089 | -2.0325 | -1.8311 | -1.8402 | -2.1515 | 1.8631 | -120.0577 | 2.0462 | 0.091553 | -122.0352 | -0.1236 | -121.9528 | 0.18311 | -0.004578 | 0.19684 | 0.10529 | 2.0828 | 2.0462 | 0.18768 | 0.11902 | -0.1236 | 2.0828 | 2.0462 | 0.11902 | 0.10529 | 0.18768 | -120.2774 | -122.2641
679.0625 | 122.2916 | -2.2797 | 119.9158 | -0.083924 | 0.0079831 | 0.007763 | 0.016893 | -0.0043495 | 0.0015467 | 0.028578 | 0.009155 | 0.054932 | -0.16022 | -2.2018 | -2.1744 | -2.1469 | -2.2385 | -2.0325 | -2.0554 | -2.3621 | 2.1194 | -119.8608 | 2.2888 | 0.07782 | -122.0901 | -0.082398 | -121.9711 | 0.16937 | 0.041199 | 0.24719 | 0.10529 | 2.3346 | 2.2888 | 0.2243 | 0.13275 | -0.082398 | 2.3346 | 2.2888 | 0.13275 | 0.10529 | 0.2243 | -120.076 | -122.2778
680.125 | 122.3007 | -1.9043 | 120.2087 | 0.053406 | 0.0099057 | 0.009472 | 0.01668 | -0.0017859 | 0.00069212 | 0.029006 | 0.022888 | 0.068665 | -0.15564 | -1.8219 | -1.8219 | -1.7944 | -1.9363 | -1.7258 | -1.7349 | -2.0416 | 1.7487 | -120.1401 | 1.9272 | 0.082398 | -122.0306 | -0.13733 | -121.9437 | 0.17853 | -0.032043 | 0.17853 | 0.082398 | 1.973 | 1.9272 | 0.16937 | 0.10986 | -0.13733 | 1.973 | 1.9272 | 0.10986 | 0.082398 | 0.16937 | -120.3644 | -122.2504
681.0625 | 122.2824 | -1.8539 | 120.3003 | -0.022888 | 0.0086239 | 0.0071222 | 0.017961 | -0.0041357 | -0.0012305 | 0.027297 | 0.018311 | 0.068665 | -0.16022 | -1.767 | -1.7487 | -1.7487 | -1.8494 | -1.6388 | -1.68 | -1.9592 | 1.6937 | -120.2316 | 1.8723 | 0.086975 | -122.0489 | -0.10529 | -121.9803 | 0.17853 | 0.004578 | 0.21515 | 0.10529 | 1.9226 | 1.8723 | 0.17395 | 0.10529 | -0.10529 | 1.9226 | 1.8723 | 0.10529 | 0.10529 | 0.17395 | -120.4605 | -122.2595
682.1094 | 122.2504 | -1.8356 | 120.3461 | 0.099182 | 0.010547 | 0.008404 | 0.024156 | -0.0015723 | -0.0012305 | 0.027724 | 0.013733 | 0.064087 | -0.21515 | -1.7349 | -1.7578 | -1.7166 | -1.7944 | -1.6708 | -1.6022 | -1.9409 | 1.6205 | -120.282 | 1.8494 | 0.10071 | -122.1039 | -0.10529 | -121.9482 | 0.22888 | 0.041198 | 0.1648 | 0.07782 | 1.8997 | 1.8494 | 0.23346 | 0.11902 | -0.10529 | 1.8997 | 1.8494 | 0.11902 | 0.07782 | 0.23346 | -120.5612 | -122.287
683.0625 | 122.2778 | -1.7624 | 120.3964 | -0.022888 | 0.011615 | 0.009472 | 0.016252 | -0.0032813 | -0.00080328 | 0.02751 | 0.018311 | 0.059509 | -0.14648 | -1.68 | -1.6525 | -1.6388 | -1.7853 | -1.5656 | -1.5884 | -1.8677 | 1.6159 | -120.3369 | 1.7807 | 0.082397 | -122.049 | -0.10529 | -121.9849 | 0.16479 | -0.022888 | 0.19684 | 0.10986 | 1.8219 | 1.7807 | 0.17395 | 0.1236 | -0.10529 | 1.8219 | 1.7807 | 0.1236 | 0.10986 | 0.17395 | -120.5429 | -122.2641
684.1094 | 122.3236 | -1.7258 | 120.433 | 0.12207 | 0.0073423 | 0.0073358 | 0.021807 | -7.686e-05 | 0.00047852 | 0.025801 | 0.045776 | 0.054932 | -0.17853 | -1.6388 | -1.6571 | -1.593 | -1.8036 | -1.5427 | -1.5793 | -1.8631 | 1.5472 | -120.3781 | 1.7715 | 0.086975 | -122.0901 | -0.13733 | -122.0123 | 0.2243 | -0.07782 | 0.18311 | 0.068665 | 1.7807 | 1.7715 | 0.14648 | 0.13275 | -0.13733 | 1.7807 | 1.7715 | 0.13275 | 0.068665 | 0.14648 | -120.6116 | -122.2961
685.0625 | 122.3557 | -1.7166 | 120.4102 | -0.18311 | 0.0062741 | 0.0069086 | 0.016252 | -0.0026405 | 5.1318e-05 | 0.026869 | 0.073242 | 0.050354 | -0.14648 | -1.561 | -1.5518 | -1.5244 | -1.7944 | -1.4236 | -1.5518 | -1.8402 | 1.5701 | -120.3598 | 1.7899 | 0.15564 | -121.962 | -0.1236 | -121.962 | 0.21973 | -0.07782 | 0.29297 | 0.1648 | 1.767 | 1.7899 | 0.1648 | 0.19226 | -0.1236 | 1.767 | 1.7899 | 0.19226 | 0.1648 | 0.1648 | -120.5566 | -122.2504
686.1094 | 122.2321 | -1.799 | 120.4193 | 0.6485 | 0.011828 | 0.013317 | 0.023302 | -0.0011451 | -0.0016577 | 0.027938 | -0.036621 | 0.10071 | -0.18768 | -1.7303 | -1.7395 | -1.712 | -1.712 | -1.6754 | -1.561 | -1.9226 | 1.6113 | -120.3186 | 1.7624 | 0.068664 | -122.1588 | -0.1236 | -121.9803 | 0.15106 | 0.086975 | 0.1236 | 0.059509 | 1.8997 | 1.7624 | 0.23804 | 0.086975 | -0.1236 | 1.8997 | 1.7624 | 0.086975 | 0.059509 | 0.23804 | -120.607 | -122.3419
687.0625 | 122.3099 | -1.799 | 120.3369 | -0.045777 | 0.0079831 | 0.006695 | 0.018602 | -0.00071786 | -0.00037588 | 0.025374 | 0.018311 | 0.073242 | -0.16479 | -1.7166 | -1.6937 | -1.6708 | -1.7853 | -1.5839 | -1.6022 | -1.9226 | 1.6342 | -120.2637 | 1.8173 | 0.082397 | -122.0306 | -0.1236 | -121.9391 | 0.18311 | 0.013733 | 0.21515 | 0.10528 | 1.8723 | 1.8173 | 0.19684 | 0.12817 | -0.1236 | 1.8723 | 1.8173 | 0.12817 | 0.10528 | 0.19684 | -120.5017 | -122.2595
688.125 | 122.3007 | -1.8127 | 120.3232 | 0.15259 | 0.012042 | 0.010113 | 0.021807 | -0.0041357 | -0.0027259 | 0.028578 | 0.064087 | 0.045776 | -0.14648 | -1.6891 | -1.6983 | -1.6571 | -1.9135 | -1.5884 | -1.6571 | -1.9455 | 1.6663 | -120.2774 | 1.8768 | 0.1236 | -122.0215 | -0.13275 | -121.9803 | 0.21057 | -0.10071 | 0.2243 | 0.11444 | 1.8585 | 1.8768 | 0.15564 | 0.15564 | -0.13275 | 1.8585 | 1.8768 | 0.15564 | 0.11444 | 0.15564 | -120.4697 | -122.2687
689.0625 | 122.3053 | -1.8082 | 120.3415 | 0.10681 | 0.0086239 | 0.0088312 | 0.017534 | -0.0015723 | -0.0010169 | 0.026869 | 0.064087 | 0.032043 | -0.15564 | -1.7166 | -1.7075 | -1.68 | -1.8539 | -1.6113 | -1.6434 | -1.9409 | 1.6525 | -120.3094 | 1.8723 | 0.091553 | -122.049 | -0.13275 | -121.9849 | 0.21973 | -0.045776 | 0.19684 | 0.10071 | 1.8402 | 1.8723 | 0.1648 | 0.12817 | -0.13275 | 1.8402 | 1.8723 | 0.12817 | 0.10071 | 0.1648 | -120.4971 | -122.2824
690.125 | 122.287 | -1.8127 | 120.3644 | -0.061035 | 0.0092649 | 0.0051996 | 0.019243 | -0.0049903 | 5.1318e-05 | 0.027724 | 0.022888 | 0.045776 | -0.15106 | -1.7303 | -1.712 | -1.7029 | -1.8127 | -1.6296 | -1.6525 | -1.9272 | 1.6617 | -120.3186 | 1.8356 | 0.082397 | -122.0764 | -0.11444 | -122.0169 | 0.17395 | 0 | 0.1831 | 0.10071 | 1.8585 | 1.8356 | 0.16022 | 0.10986 | -0.11444 | 1.8585 | 1.8356 | 0.10986 | 0.10071 | 0.16022 | -120.5154 | -122.2916
691.0625 | 122.3145 | -1.8036 | 120.3461 | -0.053406 | 0.010119 | 0.0041314 | 0.019884 | -0.0049903 | 0.0021875 | 0.030287 | -0.11444 | 0.041199 | -0.26093 | -1.7303 | -1.7075 | -1.6983 | -1.8311 | -1.593 | -1.6571 | -1.9592 | 1.5427 | -120.3049 | 1.6891 | 0.073242 | -122.0535 | -0.15564 | -122.0032 | 0.14648 | -0.027466 | 0.21057 | 0.096131 | 1.8448 | 1.6891 | 0.14649 | 0.10529 | -0.15564 | 1.8448 | 1.6891 | 0.10529 | 0.096131 | 0.14649 | -120.607 | -122.3053
692.1094 | 122.3877 | -1.7715 | 120.3873 | -0.22888 | 0.011188 | 0.010113 | 0.018602 | -0.0045631 | 0.00026492 | 0.027938 | 0.068665 | 0.054932 | -0.14648 | -1.6022 | -1.6022 | -1.593 | -1.8311 | -1.4969 | -1.6205 | -1.9226 | 1.6251 | -120.3323 | 1.8402 | 0.16937 | -121.9894 | -0.15106 | -122.0078 | 0.21515 | -0.05951 | 0.27466 | 0.16937 | 1.8265 | 1.8402 | 0.15106 | 0.17853 | -0.15106 | 1.8265 | 1.8402 | 0.17853 | 0.16937 | 0.15106 | -120.5338 | -122.3099
693.0625 | 122.3282 | -1.8127 | 120.4239 | -0.0076296 | 0.0096921 | 0.0096856 | 0.016893 | -0.0041357 | -0.00037588 | 0.027297 | 0.018311 | 0.054932 | -0.14648 | -1.7258 | -1.7715 | -1.6983 | -1.8906 | -1.593 | -1.6113 | -1.8906 | 1.6663 | -120.369 | 1.8311 | 0.086975 | -122.1954 | -0.07782 | -122.0352 | 0.16479 | -0.07782 | 0.21973 | 0.041199 | 1.8677 | 1.8311 | 0.20142 | 0.11444 | -0.07782 | 1.8677 | 1.8311 | 0.11444 | 0.041199 | 0.20142 | -120.5704 | -122.3145
694.0625 | 122.3328 | -1.7853 | 120.3964 | -0.0076296 | 0.0096921 | 0.0086176 | 0.016252 | -0.0054175 | 0.0013329 | 0.027938 | 0.027466 | 0.050354 | -0.15106 | -1.6525 | -1.6388 | -1.6205 | -1.7258 | -1.5472 | -1.5793 | -1.8906 | 1.6342 | -120.3461 | 1.8127 | 0.13275 | -122.0352 | -0.10529 | -121.9757 | 0.17853 | 0.059509 | 0.23804 | 0.14648 | 1.8356 | 1.8127 | 0.20599 | 0.1648 | -0.10529 | 1.8356 | 1.8127 | 0.1648 | 0.14648 | 0.20599 | -120.5475 | -122.287
695.1094 | 122.3099 | -1.712 | 120.4514 | 0.12207 | 0.0099057 | 0.0069086 | 0.017748 | -0.0028541 | 0.0015467 | 0.02751 | 0.050354 | 0.045776 | -0.13733 | -1.6159 | -1.6022 | -1.5839 | -1.7441 | -1.5244 | -1.5427 | -1.8265 | 1.5747 | -120.4056 | 1.7624 | 0.09613 | -122.0535 | -0.11444 | -121.994 | 0.18768 | -0.032044 | 0.18768 | 0.10986 | 1.7578 | 1.7624 | 0.16937 | 0.12817 | -0.11444 | 1.7578 | 1.7624 | 0.12817 | 0.10986 | 0.16937 | -120.5887 | -122.2778
696.0625 | 122.3328 | -1.7532 | 120.4376 | -0.053406 | 0.01076 | 0.0071222 | 0.018602 | -0.0052039 | 0.00047852 | 0.02751 | 0.032043 | 0.027466 | -0.073242 | -1.6479 | -1.6479 | -1.6296 | -1.7624 | -1.5381 | -1.5839 | -1.8677 | 1.68 | -120.4102 | 1.7853 | 0.10529 | -122.0856 | -0.11444 | -122.0215 | 0.10529 | -0.009155 | 0.21515 | 0.10529 | 1.7807 | 1.7853 | 0.16937 | 0.1236 | -0.11444 | 1.7807 | 1.7853 | 0.1236 | 0.10529 | 0.16937 | -120.5109 | -122.3053
697.1094 | 122.3282 | -1.7212 | 120.4697 | 0.0076294 | 0.0094785 | 0.008404 | 0.016039 | -0.0039221 | 0.0011193 | 0.028578 | -0.004578 | 0.064087 | -0.15106 | -1.6479 | -1.6525 | -1.6342 | -1.7395 | -1.5472 | -1.5564 | -1.8448 | 1.5701 | -120.4056 | 1.7166 | 0.073242 | -122.1222 | -0.1236 | -122.0261 | 0.14648 | -0.018311 | 0.17395 | 0.068664 | 1.7853 | 1.7166 | 0.1648 | 0.086975 | -0.1236 | 1.7853 | 1.7166 | 0.086975 | 0.068664 | 0.1648 | -120.6207 | -122.3145
698.0625 | 122.3236 | -1.7532 | 120.4422 | -0.022888 | 0.011615 | 0.0073358 | 0.018389 | -0.0032813 | 0.00026492 | 0.029219 | 0 | -0.009155 | 0 | -1.6296 | -1.6296 | -1.6205 | -1.7441 | -1.5152 | -1.5884 | -1.8768 | 1.7532 | -120.4514 | 1.7532 | 0.1236 | -122.0718 | -0.1236 | -122.0306 | 0 | 0.009155 | 0.23804 | 0.1236 | 1.7441 | 1.7532 | 0.1648 | 0.13275 | -0.1236 | 1.7441 | 1.7532 | 0.13275 | 0.1236 | 0.1648 | -120.4422 | -122.319
699.1094 | 122.3328 | -1.7395 | 120.4559 | 0.099182 | 0.0086239 | 0.0060542 | 0.019243 | -0.0026405 | 0.0013329 | 0.028578 | 0.059509 | 0.036621 | -0.16937 | -1.6251 | -1.6251 | -1.5976 | -1.8082 | -1.5289 | -1.5747 | -1.8585 | 1.5701 | -120.4193 | 1.799 | 0.11444 | -122.081 | -0.11902 | -122.0306 | 0.22888 | -0.068665 | 0.21057 | 0.11444 | 1.7761 | 1.799 | 0.1648 | 0.14191 | -0.11902 | 1.7761 | 1.799 | 0.14191 | 0.11444 | 0.1648 | -120.6253 | -122.3145
700.0625 | 122.2366 | -1.799 | 120.4788 | -0.27466 | 0.011401 | 0.0073358 | 0.022875 | -0.0037085 | 0.0015467 | 0.027083 | -0.018311 | 0.091553 | -0.19684 | -1.7029 | -1.7166 | -1.7303 | -1.6113 | -1.6342 | -1.5472 | -1.9089 | 1.6022 | -120.3873 | 1.7807 | 0.09613 | -122.1954 | -0.10986 | -122.0261 | 0.17853 | 0.18768 | 0.1648 | 0.082397 | 1.8906 | 1.7807 | 0.25177 | 0.068664 | -0.10986 | 1.8906 | 1.7807 | 0.068664 | 0.082397 | 0.25177 | -120.6757 | -122.3877
701.125 | 122.3785 | -1.7258 | 120.4697 | 0.1297 | 0.012042 | 0.0096856 | 0.02202 | -0.0011451 | -0.00016228 | 0.029219 | 0.064087 | 0.050354 | -0.17853 | -1.5976 | -1.6159 | -1.5884 | -1.8402 | -1.5335 | -1.5839 | -1.8585 | 1.5472 | -120.4193 | 1.7899 | 0.12817 | -122.0856 | -0.13275 | -122.0535 | 0.24261 | -0.11444 | 0.19226 | 0.10986 | 1.7761 | 1.7899 | 0.14191 | 0.13733 | -0.13275 | 1.7761 | 1.7899 | 0.13733 | 0.10986 | 0.14191 | -120.6482 | -122.3282
702.0625 | 122.3373 | -1.7395 | 120.4697 | 0.076294 | 0.0094785 | 0.0079768 | 0.01732 | -0.0013587 | -0.00037588 | 0.025801 | 0.041199 | 0.054932 | -0.13733 | -1.6571 | -1.6479 | -1.6113 | -1.7395 | -1.5381 | -1.5747 | -1.8631 | 1.6022 | -120.4147 | 1.7807 | 0.082398 | -122.1176 | -0.1236 | -122.0444 | 0.17853 | 0 | 0.20142 | 0.091553 | 1.7944 | 1.7807 | 0.1648 | 0.12817 | -0.1236 | 1.7944 | 1.7807 | 0.12817 | 0.091553 | 0.1648 | -120.607 | -122.3328
703.1094 | 122.3373 | -1.7303 | 120.4605 | 0.13733 | 0.010974 | 0.0071222 | 0.020098 | -0.0019995 | 0.0026147 | 0.028578 | 0.07782 | 0.004578 | -0.16479 | -1.6022 | -1.6067 | -1.5564 | -1.8173 | -1.5106 | -1.5656 | -1.8585 | 1.5656 | -120.4559 | 1.8082 | 0.12817 | -122.0673 | -0.12817 | -122.0261 | 0.24261 | -0.086975 | 0.21973 | 0.1236 | 1.7349 | 1.8082 | 0.1648 | 0.17395 | -0.12817 | 1.7349 | 1.8082 | 0.17395 | 0.1236 | 0.1648 | -120.6253 | -122.319
704.0625 | 122.3419 | -1.7303 | 120.4514 | -0.083924 | 0.010333 | 0.0064814 | 0.020311 | -0.0030677 | 0.00069212 | 0.027083 | 0.013733 | 0.050354 | -0.16022 | -1.6617 | -1.6388 | -1.6159 | -1.7212 | -1.5289 | -1.5564 | -1.8539 | 1.5701 | -120.401 | 1.7441 | 0.068665 | -122.0901 | -0.1236 | -122.0078 | 0.17395 | 0.009156 | 0.20142 | 0.091553 | 1.7807 | 1.7441 | 0.17395 | 0.11444 | -0.1236 | 1.7807 | 1.7441 | 0.11444 | 0.091553 | 0.17395 | -120.6116 | -122.3053
705.125 | 122.3785 | -1.6937 | 120.5154 | -0.076294 | 0.0094785 | 0.012676 | 0.018816 | -0.0037085 | 0.0017603 | 0.029433 | 0.032043 | 0.054932 | -0.15564 | -1.593 | -1.561 | -1.5472 | -1.7212 | -1.442 | -1.5244 | -1.8082 | 1.5381 | -120.4605 | 1.7258 | 0.10071 | -122.0764 | -0.11444 | -122.0398 | 0.18768 | -0.027465 | 0.25177 | 0.13275 | 1.7487 | 1.7258 | 0.16937 | 0.14648 | -0.11444 | 1.7487 | 1.7258 | 0.14648 | 0.13275 | 0.16937 | -120.6711 | -122.3236
706.0625 | 122.3557 | -1.6525 | 120.5429 | -0.022888 | 0.010333 | 0.0058404 | 0.018175 | -0.0037085 | 0.00090572 | 0.029006 | -0.009155 | 0.022888 | -0.004578 | -1.5747 | -1.5656 | -1.5518 | -1.68 | -1.4465 | -1.5106 | -1.7807 | 1.6479 | -120.52 | 1.6434 | 0.07782 | -122.1085 | -0.12817 | -122.0535 | -0.004577 | -0.027466 | 0.20599 | 0.086975 | 1.6754 | 1.6434 | 0.14191 | 0.10071 | -0.12817 | 1.6754 | 1.6434 | 0.10071 | 0.086975 | 0.14191 | -120.5475 | -122.3236
707.125 | 122.374 | -1.6296 | 120.5704 | -0.045777 | 0.0092649 | 0.0054132 | 0.021593 | -0.0026405 | -0.0016577 | 0.02751 | 0.068665 | 0.004578 | -0.15564 | -1.506 | -1.506 | -1.4832 | -1.7395 | -1.4191 | -1.4969 | -1.7487 | 1.474 | -120.5658 | 1.6983 | 0.1236 | -122.0764 | -0.11902 | -122.0673 | 0.22431 | -0.10986 | 0.21057 | 0.1236 | 1.6342 | 1.6983 | 0.13275 | 0.14648 | -0.11902 | 1.6342 | 1.6983 | 0.14648 | 0.1236 | 0.13275 | -120.726 | -122.319
708.0625 | 122.3785 | -1.6342 | 120.5978 | 0.28229 | 0.012683 | 0.0062678 | 0.01732 | -0.0043495 | 0.0011193 | 0.026442 | -0.009155 | -0.004578 | 0.027466 | -1.5518 | -1.5244 | -1.5015 | -1.6342 | -1.4282 | -1.4786 | -1.7578 | 1.6617 | -120.6024 | 1.6251 | 0.082397 | -122.1222 | -0.1236 | -122.0764 | -0.036621 | 0 | 0.20599 | 0.10986 | 1.6296 | 1.6251 | 0.15564 | 0.13275 | -0.1236 | 1.6296 | 1.6251 | 0.13275 | 0.10986 | 0.15564 | -120.5704 | -122.3557
709.0625 | 122.3602 | -1.6067 | 120.6253 | -0.045777 | 0.010119 | 0.0069086 | 0.01732 | -0.0032813 | 0.0024011 | 0.028151 | -0.15564 | 0.041199 | -0.30212 | -1.4969 | -1.4832 | -1.474 | -1.6022 | -1.3733 | -1.4282 | -1.7166 | 1.3046 | -120.5841 | 1.4511 | 0.10986 | -122.1085 | -0.10986 | -122.0535 | 0.14648 | 0.004577 | 0.23346 | 0.1236 | 1.6479 | 1.4511 | 0.17853 | 0.13275 | -0.10986 | 1.6479 | 1.4511 | 0.13275 | 0.1236 | 0.17853 | -120.9274 | -122.3419
710.1094 | 122.4197 | -1.5289 | 120.6802 | -0.19836 | 0.0075559 | 0.010754 | 0.017107 | -0.0052039 | 5.1318e-05 | 0.026229 | 0.09613 | 0.045776 | -0.14648 | -1.3504 | -1.355 | -1.3412 | -1.5839 | -1.2497 | -1.387 | -1.6663 | 1.3824 | -120.6345 | 1.6251 | 0.17853 | -122.0352 | -0.13733 | -122.0673 | 0.24261 | -0.054931 | 0.27924 | 0.17395 | 1.5747 | 1.6251 | 0.14191 | 0.18768 | -0.13733 | 1.5747 | 1.6251 | 0.18768 | 0.17395 | 0.14191 | -120.8267 | -122.3465
711.0625 | 122.3969 | -1.4603 | 120.7809 | -0.10681 | 0.0090511 | 0.0073358 | 0.014971 | -0.0032813 | -0.00080328 | 0.027297 | 0.045776 | 0.068665 | -0.17395 | -1.3275 | -1.3458 | -1.3092 | -1.4877 | -1.2177 | -1.3092 | -1.5839 | 1.2863 | -120.7123 | 1.506 | 0.13275 | -122.1268 | -0.1236 | -122.0901 | 0.21973 | -0.027466 | 0.24262 | 0.11444 | 1.5289 | 1.506 | 0.15106 | 0.15106 | -0.1236 | 1.5289 | 1.506 | 0.15106 | 0.11444 | 0.15106 | -120.9549 | -122.3648
712.125 | 122.2595 | -1.4603 | 120.8405 | -0.20599 | 0.010547 | 0.0056268 | 0.02202 | -0.0039221 | -0.00016228 | 0.026442 | -0.018311 | 0.086975 | -0.1831 | -1.3779 | -1.3779 | -1.3962 | -1.2863 | -1.2863 | -1.2222 | -1.593 | 1.2772 | -120.7535 | 1.442 | 0.082397 | -122.2183 | -0.13275 | -122.0627 | 0.16479 | 0.17395 | 0.17395 | 0.082397 | 1.5472 | 1.442 | 0.23804 | 0.064087 | -0.13275 | 1.5472 | 1.442 | 0.064087 | 0.082397 | 0.23804 | -121.0236 | -122.4335
713.0625 | 122.3694 | -1.4008 | 120.8359 | -0.11444 | 0.010333 | 0.011822 | 0.01668 | -0.0030677 | 0.00090572 | 0.027724 | 0.027466 | 0.032043 | -0.1236 | -1.2955 | -1.2817 | -1.2589 | -1.4191 | -1.1719 | -1.2268 | -1.5015 | 1.2772 | -120.8038 | 1.4282 | 0.10529 | -122.1176 | -0.10071 | -122.0627 | 0.15106 | -0.01831 | 0.22888 | 0.11902 | 1.4328 | 1.4282 | 0.17395 | 0.14191 | -0.10071 | 1.4328 | 1.4282 | 0.14191 | 0.11902 | 0.17395 | -120.9595 | -122.3373
714.1094 | 122.3694 | -1.355 | 120.8954 | -0.0076296 | 0.0086239 | 0.010327 | 0.019884 | -0.0047767 | 0.0011193 | 0.026869 | 0.018311 | 0.041199 | -0.14648 | -1.2634 | -1.268 | -1.2451 | -1.3687 | -1.1581 | -1.1902 | -1.4786 | 1.2085 | -120.8542 | 1.3733 | 0.091552 | -122.1634 | -0.1236 | -122.0856 | 0.16479 | -0.013733 | 0.19684 | 0.086975 | 1.3962 | 1.3733 | 0.16479 | 0.10986 | -0.1236 | 1.3962 | 1.3733 | 0.10986 | 0.086975 | 0.16479 | -121.0419 | -122.374
715.0625 | 122.2778 | -1.3687 | 120.932 | -0.27466 | 0.0086239 | 0.0096856 | 0.022447 | -0.0056311 | -0.00080328 | 0.029647 | 0.022888 | 0.073242 | -0.1831 | -1.2634 | -1.2772 | -1.2772 | -1.2131 | -1.1627 | -1.1444 | -1.4832 | 1.1856 | -120.8588 | 1.3916 | 0.10529 | -122.2092 | -0.11444 | -122.0764 | 0.20599 | 0.15564 | 0.20599 | 0.091552 | 1.442 | 1.3916 | 0.2243 | 0.091552 | -0.11444 | 1.442 | 1.3916 | 0.091552 | 0.091552 | 0.2243 | -121.1151 | -122.4152
716.1094 | 122.4518 | -1.3733 | 120.8633 | 0.091553 | 0.0096921 | 0.0060542 | 0.02202 | -0.00093146 | -0.0016577 | 0.026015 | 0.073242 | 0.036621 | -0.15564 | -1.1948 | -1.2177 | -1.1673 | -1.4557 | -1.3824 | -1.1993 | -1.4465 | 1.2177 | -120.8267 | 1.4465 | 0.17853 | -122.081 | -0.073242 | -122.0627 | 0.22888 | -0.082397 | -0.009155 | 0.15564 | 1.4099 | 1.4465 | 0.17395 | 0.20599 | -0.073242 | 1.4099 | 1.4465 | 0.20599 | 0.15564 | 0.17395 | -121.019 | -122.3099
717.0625 | 122.374 | -1.2131 | 121.0052 | 0.030517 | 0.0090511 | 0.0075494 | 0.019243 | -0.0026405 | -0.0010169 | 0.026229 | 0.022888 | 0.050354 | -0.14191 | -1.149 | -1.1353 | -1.1078 | -1.2543 | -1.0437 | -1.062 | -1.3458 | 1.0712 | -120.9549 | 1.236 | 0.064087 | -122.1405 | -0.13275 | -122.0673 | 0.16479 | -0.041198 | 0.16937 | 0.07782 | 1.2634 | 1.236 | 0.15106 | 0.10529 | -0.13275 | 1.2634 | 1.236 | 0.10529 | 0.07782 | 0.15106 | -121.1472 | -122.3511
718.125 | 122.3785 | -1.1627 | 121.0464 | 0.091553 | 0.0088375 | 0.0092584 | 0.021807 | -0.0011451 | -0.00058968 | 0.02986 | 0.054932 | 0.022888 | -0.15564 | -1.0483 | -1.0437 | -1.0117 | -1.2451 | -0.95673 | -1.03 | -1.3092 | 1.0071 | -121.0236 | 1.2177 | 0.11444 | -122.0901 | -0.14648 | -122.0764 | 0.21057 | -0.082397 | 0.20599 | 0.11902 | 1.1856 | 1.2177 | 0.13275 | 0.15106 | -0.14648 | 1.1856 | 1.2177 | 0.15106 | 0.11902 | 0.13275 | -121.2021 | -122.3557
719.0625 | 122.4335 | -1.1627 | 121.0556 | -0.27466 | 0.0084103 | 0.008404 | 0.017534 | -0.0030677 | -0.00037588 | 0.027724 | 0.068665 | 0.041199 | -0.15106 | -1.0071 | -1.0071 | -1.0117 | -1.2222 | -0.89722 | -1.0208 | -1.2955 | 1.0117 | -121.0144 | 1.2314 | 0.15564 | -122.0627 | -0.13275 | -122.0764 | 0.21973 | -0.059509 | 0.2655 | 0.15564 | 1.2039 | 1.2314 | 0.14191 | 0.15106 | -0.13275 | 1.2039 | 1.2314 | 0.15106 | 0.15564 | 0.14191 | -121.2067 | -122.3511
720.125 | 122.4197 | -0.97504 | 121.2341 | 0.16785 | 0.0099057 | 0.011608 | 0.023302 | -0.0028541 | -0.00037588 | 0.029006 | 0.086975 | 0.036621 | -0.13733 | -0.85144 | -0.85602 | -0.82398 | -1.0941 | -0.76446 | -0.8606 | -1.1169 | 0.83771 | -121.1975 | 1.062 | 0.1236 | -122.0901 | -0.14191 | -122.0947 | 0.2243 | -0.11902 | 0.21057 | 0.11902 | 1.0117 | 1.062 | 0.11444 | 0.15106 | -0.14191 | 1.0117 | 1.062 | 0.15106 | 0.11902 | 0.11444 | -121.3715 | -122.3511
721.0625 | 122.3877 | -0.66834 | 121.6095 | -0.083924 | 0.0081967 | 0.010754 | 0.01967 | -0.0041357 | 0.00047852 | 0.026229 | -0.19226 | 0.045776 | -0.27466 | -0.56305 | -0.54474 | -0.52185 | -0.67749 | -0.45319 | -0.51727 | -0.75531 | 0.39368 | -121.5637 | 0.47607 | 0.10529 | -122.1542 | -0.086975 | -122.1268 | 0.082397 | -0.009155 | 0.21515 | 0.1236 | 0.71411 | 0.47607 | 0.15106 | 0.14648 | -0.086975 | 0.71411 | 0.47607 | 0.14648 | 0.1236 | 0.15106 | -121.8842 | -122.3648
722.1094 | 122.2778 | -0.6546 | 121.6736 | -0.022888 | 0.010974 | 0.0098994 | 0.023516 | -0.0028541 | -0.0014441 | 0.028365 | 0.009155 | 0.068665 | -0.21515 | -0.55847 | -0.58136 | -0.57678 | -0.52643 | -0.5127 | -0.44861 | -0.76904 | 0.43945 | -121.6049 | 0.66376 | 0.09613 | -122.2549 | -0.11444 | -122.1222 | 0.2243 | 0.12817 | 0.14191 | 0.073242 | 0.72327 | 0.66376 | 0.20599 | 0.07782 | -0.11444 | 0.72327 | 0.66376 | 0.07782 | 0.073242 | 0.20599 | -121.8887 | -122.4426
723.0625 | 122.3602 | -0.61798 | 121.6141 | 0.061035 | 0.0092649 | 0.0054132 | 0.016466 | -0.0019995 | 0.00047852 | 0.02751 | 0.032043 | 0.050354 | -0.14648 | -0.53558 | -0.53101 | -0.50354 | -0.63629 | -0.45319 | -0.46234 | -0.74158 | 0.4715 | -121.5637 | 0.65002 | 0.082398 | -122.1451 | -0.1236 | -122.0764 | 0.17853 | -0.018311 | 0.1648 | 0.086975 | 0.66834 | 0.65002 | 0.15564 | 0.11444 | -0.1236 | 0.66834 | 0.65002 | 0.11444 | 0.086975 | 0.15564 | -121.7606 | -122.3557
724.1094 | 122.4152 | -0.60425 | 121.6507 | -0.083924 | 0.010333 | 0.008404 | 0.020738 | -0.0032813 | -0.0010169 | 0.029219 | 0.068665 | 0.013733 | -0.15564 | -0.48523 | -0.48523 | -0.46234 | -0.70038 | -0.40283 | -0.47607 | -0.74158 | 0.44861 | -121.637 | 0.67291 | 0.11902 | -122.1359 | -0.13733 | -122.1268 | 0.22431 | -0.09613 | 0.20142 | 0.11902 | 0.61798 | 0.67291 | 0.12817 | 0.14191 | -0.13733 | 0.61798 | 0.67291 | 0.14191 | 0.11902 | 0.12817 | -121.8063 | -122.3923
725.0625 | 122.3099 | -0.65918 | 121.6278 | -0.21362 | 0.01076 | 0.0069086 | 0.02202 | -0.0039221 | -0.00037588 | 0.025801 | 0 | 0.082397 | -0.17395 | -0.55389 | -0.58136 | -0.56763 | -0.48981 | -0.47607 | -0.4303 | -0.7782 | 0.48523 | -121.5454 | 0.65918 | 0.10529 | -122.2092 | -0.11902 | -122.0581 | 0.17395 | 0.16937 | 0.18311 | 0.07782 | 0.74158 | 0.65918 | 0.22888 | 0.091553 | -0.11902 | 0.74158 | 0.65918 | 0.091553 | 0.07782 | 0.22888 | -121.8018 | -122.406
726.125 | 122.3969 | -0.66834 | 121.5637 | 0.022888 | 0.0090511 | 0.012463 | 0.020311 | -0.0041357 | -0.00037588 | 0.027083 | 0.059509 | 0.018311 | -0.16479 | -0.54932 | -0.54474 | -0.51727 | -0.74616 | -0.43488 | -0.54016 | -0.78735 | 0.50354 | -121.5454 | 0.72784 | 0.11902 | -122.1085 | -0.11902 | -122.1039 | 0.2243 | -0.07782 | 0.23346 | 0.1236 | 0.68665 | 0.72784 | 0.12817 | 0.15106 | -0.11902 | 0.68665 | 0.72784 | 0.15106 | 0.1236 | 0.12817 | -121.7285 | -122.3511
727.0625 | 122.4426 | -0.63171 | 121.6232 | -0.11444 | 0.0090511 | 0.0064814 | 0.020311 | -0.0039221 | -0.00058968 | 0.029647 | 0.059509 | 0.064087 | -0.13733 | -0.50812 | -0.48981 | -0.46692 | -0.67291 | -0.39825 | -0.48523 | -0.76446 | 0.49438 | -121.5591 | 0.69122 | 0.1236 | -122.113 | -0.13275 | -122.1085 | 0.19684 | -0.041199 | 0.23346 | 0.14191 | 0.6958 | 0.69122 | 0.14648 | 0.1648 | -0.13275 | 0.6958 | 0.69122 | 0.1648 | 0.14191 | 0.14648 | -121.7606 | -122.3877
728.125 | 122.4243 | -0.58136 | 121.7056 | 0.1297 | 0.0090511 | 0.006695 | 0.021166 | -0.0034949 | 5.1318e-05 | 0.027938 | 0.073242 | 0.045776 | -0.14191 | -0.46234 | -0.45319 | -0.39368 | -0.64087 | -0.32044 | -0.44403 | -0.70953 | 0.43945 | -121.6599 | 0.6546 | 0.11902 | -122.1588 | -0.12817 | -122.1497 | 0.21515 | -0.059509 | 0.26092 | 0.12817 | 0.62714 | 0.6546 | 0.13733 | 0.18768 | -0.12817 | 0.62714 | 0.6546 | 0.18768 | 0.12817 | 0.13733 | -121.8475 | -122.4152
729.0625 | 122.406 | -0.59967 | 121.6553 | 0.015259 | 0.0096921 | 0.0071222 | 0.01668 | -0.0039221 | 0.00026492 | 0.028151 | 0 | 0.045776 | -0.16022 | -0.46234 | -0.46692 | -0.42572 | -0.60883 | -0.45319 | -0.40283 | -0.70038 | 0.43945 | -121.6095 | 0.59967 | 0.13733 | -122.1222 | -0.10071 | -122.0581 | 0.16022 | -0.009156 | 0.14648 | 0.13275 | 0.64545 | 0.59967 | 0.19684 | 0.17395 | -0.10071 | 0.64545 | 0.59967 | 0.17395 | 0.13275 | 0.19684 | -121.8155 | -122.3557
730.1094 | 122.438 | -0.49439 | 121.7789 | -0.068665 | 0.011188 | 0.0079768 | 0.01732 | -0.0043495 | -0.00080328 | 0.029006 | 0.027466 | 0.022888 | -0.086975 | -0.39825 | -0.37994 | -0.34332 | -0.49896 | -0.2655 | -0.33417 | -0.60883 | 0.40741 | -121.756 | 0.52185 | 0.096131 | -122.1588 | -0.11444 | -122.113 | 0.11444 | -0.004577 | 0.22888 | 0.11444 | 0.51727 | 0.52185 | 0.16022 | 0.15106 | -0.11444 | 0.51727 | 0.52185 | 0.15106 | 0.11444 | 0.16022 | -121.8658 | -122.3877
731.0625 | 122.4014 | -0.55389 | 121.7377 | 0.099182 | 0.010547 | 0.0096856 | 0.019457 | -0.0041357 | -0.00080328 | 0.028151 | 0.068665 | 0.054932 | -0.16479 | -0.44403 | -0.46234 | -0.41199 | -0.59509 | -0.3479 | -0.3891 | -0.6546 | 0.3891 | -121.6827 | 0.62256 | 0.10986 | -122.2 | -0.10071 | -122.1268 | 0.23346 | -0.041199 | 0.20599 | 0.091553 | 0.60883 | 0.62256 | 0.1648 | 0.14191 | -0.10071 | 0.60883 | 0.62256 | 0.14191 | 0.091553 | 0.1648 | -121.9025 | -122.3923
732.125 | 122.3969 | -0.49896 | 121.7468 | 0.068664 | 0.011615 | 0.0092584 | 0.022447 | -0.0045631 | -0.00037588 | 0.030074 | 0.050354 | 0.050354 | -0.15564 | -0.39825 | -0.41199 | -0.36163 | -0.54016 | -0.30212 | -0.35706 | -0.62256 | 0.34332 | -121.6965 | 0.54932 | 0.10071 | -122.1588 | -0.1236 | -122.1039 | 0.20599 | -0.041199 | 0.19684 | 0.086975 | 0.54932 | 0.54932 | 0.14191 | 0.13733 | -0.1236 | 0.54932 | 0.54932 | 0.13733 | 0.086975 | 0.14191 | -121.9025 | -122.3694
733.0625 | 122.4197 | -0.54932 | 121.7834 | -0.061035 | 0.0088375 | 0.009472 | 0.020525 | -0.0022131 | -0.00037588 | 0.025588 | 0.009155 | 0.059509 | -0.14191 | -0.56305 | -0.47607 | -0.3891 | -0.59509 | -0.33875 | -0.35706 | -0.62714 | 0.40741 | -121.7239 | 0.55847 | -0.013733 | -122.2595 | -0.07782 | -122.1405 | 0.15106 | -0.045777 | 0.21057 | 0.073242 | 0.60883 | 0.55847 | 0.19226 | 0.16022 | -0.07782 | 0.60883 | 0.55847 | 0.16022 | 0.073242 | 0.19226 | -121.9254 | -122.4106
734.1094 | 122.3236 | -0.56763 | 121.7972 | 0.045776 | 0.013537 | 0.01054 | 0.027574 | -0.0026405 | -0.0014441 | 0.027083 | -0.027466 | 0.091553 | -0.17395 | -0.50354 | -0.53101 | -0.52185 | -0.41657 | -0.45319 | -0.33875 | -0.67749 | 0.39368 | -121.7056 | 0.54016 | 0.064087 | -122.3282 | -0.10986 | -122.1359 | 0.14648 | 0.15106 | 0.11444 | 0.036621 | 0.65918 | 0.54016 | 0.22888 | 0.045776 | -0.10986 | 0.65918 | 0.54016 | 0.045776 | 0.036621 | 0.22888 | -121.9711 | -122.4747
735.0625 | 122.4609 | -0.50812 | 121.7377 | -0.24414 | 0.0081967 | 0.0062678 | 0.015825 | -0.0028541 | 0.00026492 | 0.02516 | 0.064087 | 0.041199 | -0.16022 | -0.34332 | -0.34332 | -0.32501 | -0.54474 | -0.22888 | -0.36163 | -0.64087 | 0.3479 | -121.6965 | 0.5722 | 0.16479 | -122.081 | -0.13275 | -122.0993 | 0.2243 | -0.036621 | 0.27924 | 0.16479 | 0.54932 | 0.5722 | 0.14648 | 0.18311 | -0.13275 | 0.54932 | 0.5722 | 0.18311 | 0.16479 | 0.14648 | -121.8979 | -122.3785
736.1094 | 122.3923 | -0.44861 | 121.843 | 0.091553 | 0.0096921 | 0.011822 | 0.017961 | -0.0026405 | -0.0018713 | 0.026656 | 0.009155 | 0.050354 | -0.15106 | -0.35706 | -0.35248 | -0.3067 | -0.44403 | -0.25177 | -0.27466 | -0.55847 | 0.29755 | -121.7926 | 0.45776 | 0.091552 | -122.1954 | -0.10986 | -122.1176 | 0.16022 | 0.004577 | 0.19684 | 0.09613 | 0.49896 | 0.45776 | 0.17395 | 0.14191 | -0.10986 | 0.49896 | 0.45776 | 0.14191 | 0.09613 | 0.17395 | -121.994 | -122.4014
737.0625 | 122.4152 | -0.39368 | 121.8887 | 0.11444 | 0.0096921 | 0.0062678 | 0.01967 | -0.0024267 | -0.00058968 | 0.028151 | 0.068665 | 0.027466 | -0.15564 | -0.27924 | -0.27008 | -0.23346 | -0.48523 | -0.16937 | -0.2655 | -0.52643 | 0.23804 | -121.8613 | 0.46234 | 0.11444 | -122.1588 | -0.13275 | -122.1542 | 0.22431 | -0.091552 | 0.2243 | 0.1236 | 0.42114 | 0.46234 | 0.12817 | 0.16022 | -0.13275 | 0.42114 | 0.46234 | 0.16022 | 0.1236 | 0.12817 | -122.0444 | -122.4152
738.1094 | 122.3694 | -0.36621 | 121.9345 | 0.19073 | 0.010333 | 0.0062678 | 0.024797 | -0.0032813 | 0.00026492 | 0.024306 | 0 | 0.07782 | -0.20599 | -0.28381 | -0.30212 | -0.25635 | -0.36621 | -0.20599 | -0.19684 | -0.48981 | 0.16022 | -121.8567 | 0.36621 | 0.082398 | -122.2366 | -0.1236 | -122.1313 | 0.20599 | 0 | 0.16022 | 0.064087 | 0.44403 | 0.36621 | 0.16937 | 0.10986 | -0.1236 | 0.44403 | 0.36621 | 0.10986 | 0.064087 | 0.16937 | -122.1405 | -122.4243
739.0625 | 122.4197 | -0.3479 | 121.9025 | -0.1297 | 0.0094785 | 0.0056268 | 0.018175 | -0.0047767 | -0.00058968 | 0.025801 | -0.022888 | 0.004578 | -0.022888 | -0.26093 | -0.23804 | -0.21973 | -0.34332 | -0.14648 | -0.20599 | -0.48065 | 0.32501 | -121.8979 | 0.32501 | 0.086975 | -122.1405 | -0.13275 | -122.1085 | 0 | 0.004577 | 0.20142 | 0.10986 | 0.35248 | 0.32501 | 0.14191 | 0.12817 | -0.13275 | 0.35248 | 0.32501 | 0.12817 | 0.10986 | 0.14191 | -121.9254 | -122.3831
740.125 | 122.4335 | -0.35706 | 121.962 | -1.2131 | 0.0079831 | 0.0086176 | 0.018816 | -0.0056311 | 0.00090572 | 0.028792 | -0.022888 | 0.013733 | -0.013733 | -0.27466 | -0.24261 | -0.19684 | -0.35248 | -0.13733 | -0.18768 | -0.46234 | 0.34332 | -121.9482 | 0.33417 | 0.082398 | -122.2046 | -0.10529 | -122.1497 | -0.009155 | 0.004578 | 0.21973 | 0.11444 | 0.37079 | 0.33417 | 0.16937 | 0.16022 | -0.10529 | 0.37079 | 0.33417 | 0.16022 | 0.11444 | 0.16937 | -121.9757 | -122.4243
741.0625 | 122.4152 | -0.33417 | 121.9849 | -6e-08 | 0.0084103 | 0.0079768 | 0.017748 | -0.0026405 | -0.00016228 | 0.030501 | 0.018311 | 0.045776 | -0.15106 | -0.23346 | -0.24261 | -0.21057 | -0.33417 | -0.12817 | -0.17853 | -0.46234 | 0.1831 | -121.9391 | 0.35248 | 0.10071 | -122.2275 | -0.12817 | -122.1634 | 0.16937 | 0 | 0.20599 | 0.091552 | 0.37994 | 0.35248 | 0.15564 | 0.1236 | -0.12817 | 0.37994 | 0.35248 | 0.1236 | 0.091552 | 0.15564 | -122.1359 | -122.4472
742.1094 | 122.4014 | -0.35706 | 121.9803 | 0.015259 | 0.011828 | 0.013531 | 0.025225 | -0.0034949 | -0.00016228 | 0.027724 | 0.004578 | 0.068665 | -0.19226 | -0.27008 | -0.28839 | -0.25635 | -0.30212 | -0.19684 | -0.15106 | -0.46692 | 0.16479 | -121.9116 | 0.36163 | 0.086975 | -122.2687 | -0.10986 | -122.1313 | 0.19684 | 0.054932 | 0.16022 | 0.068665 | 0.42572 | 0.36163 | 0.20599 | 0.10071 | -0.10986 | 0.42572 | 0.36163 | 0.10071 | 0.068665 | 0.20599 | -122.1725 | -122.4472
743.0625 | 122.4197 | -0.32501 | 121.994 | 0.053406 | 0.010119 | 0.0088312 | 0.017534 | -0.0034949 | -0.0010169 | 0.029219 | 0.036621 | 0.054932 | -0.13733 | -0.23346 | -0.23804 | -0.19226 | -0.32959 | -0.11902 | -0.14648 | -0.43488 | 0.18768 | -121.9391 | 0.36163 | 0.091553 | -122.2321 | -0.10986 | -122.1405 | 0.17395 | -0.004578 | 0.20599 | 0.086975 | 0.37994 | 0.36163 | 0.17853 | 0.13275 | -0.10986 | 0.37994 | 0.36163 | 0.13275 | 0.086975 | 0.17853 | -122.1313 | -122.4289
744.1094 | 122.3877 | -0.33417 | 121.994 | -0.24414 | 0.01076 | 0.0086176 | 0.025011 | -0.0024267 | -0.0012305 | 0.027724 | 0.036621 | 0.07782 | -0.18768 | -0.21057 | -0.2243 | -0.22888 | -0.2655 | -0.13733 | -0.13275 | -0.44861 | 0.14648 | -121.9162 | 0.37079 | 0.1236 | -122.2183 | -0.11444 | -122.1268 | 0.2243 | 0.068664 | 0.19684 | 0.10986 | 0.41199 | 0.37079 | 0.20142 | 0.10528 | -0.11444 | 0.41199 | 0.37079 | 0.10528 | 0.10986 | 0.20142 | -122.1817 | -122.4426
745.0625 | 122.4518 | -0.31586 | 121.9757 | 0.10681 | 0.010333 | 0.009472 | 0.022234 | 0.00013674 | -0.0010169 | 0.026656 | 0.068665 | 0.041199 | -0.13733 | -0.16479 | -0.16937 | -0.13733 | -0.40283 | -0.10071 | -0.16022 | -0.43488 | 0.17853 | -121.9345 | 0.38452 | 0.15106 | -122.1451 | -0.11902 | -122.1359 | 0.20599 | -0.086975 | 0.21515 | 0.14648 | 0.35706 | 0.38452 | 0.15564 | 0.17853 | -0.11902 | 0.35706 | 0.38452 | 0.17853 | 0.14648 | 0.15564 | -122.113 | -122.4106
746.1094 | 122.5113 | -0.32044 | 121.9574 | 0.12207 | 0.0092649 | 0.014385 | 0.021807 | -0.0015723 | -0.0012305 | 0.028578 | 0.068665 | 0.032043 | -0.15564 | -0.15564 | -0.16022 | -0.12817 | -0.62714 | -0.31128 | -0.19226 | -0.41657 | 0.1648 | -121.9254 | 0.3891 | 0.1648 | -122.1176 | -0.09613 | -122.1497 | 0.22431 | -0.3067 | 0.009156 | 0.16022 | 0.35248 | 0.3891 | 0.12817 | 0.19226 | -0.09613 | 0.35248 | 0.3891 | 0.19226 | 0.16022 | 0.12817 | -122.113 | -122.374
747.0625 | 122.4518 | -0.28381 | 121.9894 | 0.0076294 | 0.010974 | 0.010113 | 0.020098 | -0.0019995 | -0.00058968 | 0.029647 | 0.059509 | 0.022888 | -0.15106 | -0.16937 | -0.16479 | -0.12817 | -0.37537 | -0.086975 | -0.15106 | -0.40741 | 0.13275 | -121.9666 | 0.34332 | 0.11444 | -122.1542 | -0.1236 | -122.1405 | 0.21057 | -0.091553 | 0.19684 | 0.11902 | 0.3067 | 0.34332 | 0.13275 | 0.15564 | -0.1236 | 0.3067 | 0.34332 | 0.15564 | 0.11902 | 0.13275 | -122.1405 | -122.3969
748.125 | 122.374 | -0.34332 | 122.0261 | -0.16785 | 0.011188 | 0.014385 | 0.023516 | -0.0026405 | 0.0013329 | 0.026229 | 0.050354 | 0.091553 | -0.19226 | -0.19684 | -0.21973 | -0.21515 | -0.22888 | -0.12817 | -0.10986 | -0.44403 | 0.15106 | -121.9345 | 0.39368 | 0.14648 | -122.2458 | -0.10071 | -122.1359 | 0.24261 | 0.11444 | 0.21515 | 0.1236 | 0.43488 | 0.39368 | 0.23346 | 0.12817 | -0.10071 | 0.43488 | 0.39368 | 0.12817 | 0.1236 | 0.23346 | -122.2183 | -122.4701
749.0625 | 122.4609 | -0.3067 | 121.9986 | 0.12207 | 0.010547 | 0.0090448 | 0.021379 | 0.00013674 | -0.00016228 | 0.027938 | 0.07782 | 0.036621 | -0.14648 | -0.21057 | -0.091553 | -0.050354 | -0.4303 | -0.086975 | -0.19226 | -0.43488 | 0.16022 | -121.962 | 0.38452 | 0.096131 | -122.0901 | -0.12817 | -122.1909 | 0.2243 | -0.1236 | 0.21973 | 0.21515 | 0.34332 | 0.38452 | 0.11444 | 0.25635 | -0.12817 | 0.34332 | 0.38452 | 0.25635 | 0.21515 | 0.11444 | -122.1451 | -122.4335
750.1094 | 122.4426 | -0.3067 | 121.9299 | 0.16785 | 0.0090511 | 0.0073358 | 0.022661 | -0.00050406 | -0.00058968 | 0.027938 | 0.091553 | 0.050354 | -0.15564 | -0.15106 | -0.16479 | -0.12817 | -0.3891 | -0.059509 | -0.14648 | -0.41657 | 0.15106 | -121.8796 | 0.39825 | 0.15564 | -122.0947 | -0.10986 | -122.0764 | 0.24719 | -0.082397 | 0.24719 | 0.14191 | 0.35706 | 0.39825 | 0.16022 | 0.17853 | -0.10986 | 0.35706 | 0.39825 | 0.17853 | 0.14191 | 0.16022 | -122.0856 | -122.3465
751.0625 | 122.4289 | -0.29755 | 122.0215 | 0.16785 | 0.011615 | 0.0092584 | 0.025011 | 0.00013674 | -0.0012305 | 0.029647 | 0.013733 | 0.064087 | -0.17395 | -0.21057 | -0.20142 | -0.16022 | -0.33875 | -0.11902 | -0.1236 | -0.4303 | 0.1236 | -121.9574 | 0.31128 | 0.086975 | -122.2229 | -0.13275 | -122.1451 | 0.18768 | -0.041199 | 0.17853 | 0.09613 | 0.36163 | 0.31128 | 0.17395 | 0.13733 | -0.13275 | 0.36163 | 0.31128 | 0.13733 | 0.09613 | 0.17395 | -122.1954 | -122.4518
752.1094 | 122.374 | -0.33875 | 122.0352 | 0.099182 | 0.014605 | 0.013745 | 0.023729 | -0.00029046 | 0.0036829 | 0.027297 | -0.022888 | 0.07782 | -0.16937 | -0.32501 | -0.16022 | -0.10071 | -0.24719 | -0.23346 | -0.082397 | -0.42572 | 0.16937 | -121.9574 | 0.31586 | 0.013733 | -122.1954 | -0.086975 | -122.1176 | 0.14649 | 0.091553 | 0.10529 | 0.17853 | 0.41657 | 0.31586 | 0.25635 | 0.23804 | -0.086975 | 0.41657 | 0.31586 | 0.23804 | 0.17853 | 0.25635 | -122.2046 | -122.4609
753.0625 | 122.4884 | -0.31128 | 121.9803 | 0.13733 | 0.0094785 | 0.0079768 | 0.019457 | -7.686e-05 | -0.00080328 | 0.030928 | 0.09613 | 0.032043 | -0.14648 | -0.34332 | -0.34332 | -0.1831 | -0.24719 | -0.059509 | -0.17853 | -0.42572 | 0.16479 | -121.9482 | 0.40741 | -0.032044 | -122.3236 | -0.11444 | -122.1588 | 0.24261 | 0.064087 | 0.25177 | -0.032044 | 0.34332 | 0.40741 | 0.13275 | 0.12817 | -0.11444 | 0.34332 | 0.40741 | 0.12817 | -0.032044 | 0.13275 | -122.1268 | -122.406
754.125 | 122.4792 | -0.31586 | 122.0078 | 0.11444 | 0.0092649 | 0.0037042 | 0.019457 | 0.0033411 | 5.1318e-05 | 0.028151 | 0.068665 | 0.045776 | -0.13733 | -0.14648 | -0.082397 | -0.07782 | -0.40741 | -0.032043 | -0.17395 | -0.4303 | 0.17853 | -121.962 | 0.38452 | 0.16937 | -122.0901 | -0.11444 | -122.1817 | 0.20599 | -0.091553 | 0.28381 | 0.23346 | 0.36163 | 0.38452 | 0.14191 | 0.23804 | -0.11444 | 0.36163 | 0.38452 | 0.23804 | 0.23346 | 0.14191 | -122.1451 | -122.438
755.0625 | 122.4518 | -0.27008 | 122.0215 | -0.076294 | 0.0092649 | 0.0037042 | 0.017961 | -0.00093146 | -0.0033667 | 0.029647 | 0.022888 | 0.041199 | -0.15564 | -0.1831 | -0.16022 | -0.13275 | -0.27466 | -0.036621 | -0.11444 | -0.39825 | 0.11444 | -121.9803 | 0.29297 | 0.086976 | -122.1817 | -0.12817 | -122.1359 | 0.17853 | -0.004577 | 0.23346 | 0.10986 | 0.31128 | 0.29297 | 0.15564 | 0.13733 | -0.12817 | 0.31128 | 0.29297 | 0.13733 | 0.10986 | 0.15564 | -122.1771 | -122.4197
756.125 | 122.3419 | -0.33417 | 122.0398 | 0.0076294 | 0.012042 | 0.0058404 | 0.026293 | -0.0022131 | -0.0012305 | 0.028578 | -0.009155 | 0.091553 | -0.19226 | -0.25177 | -0.27008 | -0.25177 | -0.1831 | -0.21057 | -0.09613 | -0.4715 | 0.14191 | -121.9482 | 0.32501 | 0.082397 | -122.3099 | -0.13733 | -122.1359 | 0.18311 | 0.15106 | 0.1236 | 0.064086 | 0.42572 | 0.32501 | 0.23804 | 0.082397 | -0.13733 | 0.42572 | 0.32501 | 0.082397 | 0.064086 | 0.23804 | -122.2321 | -122.5113
757.0625 | 122.4884 | -0.25177 | 122.0352 | 0.099182 | 0.014392 | 0.0079768 | 0.022447 | 0.00035034 | 0.00069212 | 0.028151 | 0.082397 | 0.059509 | -0.17395 | -0.16937 | -0.15564 | -0.10071 | -0.35248 | -0.054932 | -0.12817 | -0.39368 | 0.07782 | -121.9757 | 0.33417 | 0.082397 | -122.1909 | -0.14191 | -122.1634 | 0.25635 | -0.10071 | 0.19684 | 0.09613 | 0.31128 | 0.33417 | 0.1236 | 0.15106 | -0.14191 | 0.31128 | 0.33417 | 0.15106 | 0.09613 | 0.1236 | -122.2092 | -122.4289
758.1094 | 122.4106 | -0.29755 | 122.0764 | -0.47302 | 0.012042 | 0.0073358 | 0.024584 | 0.00035034 | 0.00026492 | 0.028365 | 0.091553 | 0.13733 | 0.23346 | -0.17395 | -0.21057 | -0.19226 | -0.20599 | -0.11444 | -0.082397 | -0.41199 | 0.531 | -121.9391 | 0.3891 | 0.1236 | -122.287 | -0.11444 | -122.1588 | -0.14191 | 0.091552 | 0.1831 | 0.086975 | 0.43488 | 0.3891 | 0.21515 | 0.10528 | -0.11444 | 0.43488 | 0.3891 | 0.10528 | 0.086975 | 0.21515 | -121.843 | -122.4884
759.0625 | 122.4655 | -0.29755 | 121.9528 | -0.045777 | 0.011615 | 0.008404 | 0.01732 | -0.0019995 | 0.00069212 | 0.030501 | 0 | 0.041199 | -0.16937 | -0.19226 | -0.15564 | -0.14648 | -0.26093 | -0.07782 | -0.09613 | -0.40283 | 0.12817 | -121.9116 | 0.29755 | 0.10528 | -122.1085 | -0.10529 | -122.049 | 0.16937 | 0.036621 | 0.21973 | 0.14191 | 0.33874 | 0.29755 | 0.20142 | 0.15106 | -0.10529 | 0.33874 | 0.29755 | 0.15106 | 0.14191 | 0.20142 | -122.1222 | -122.3557
760.1094 | 122.4197 | -0.29755 | 122.049 | 0.14496 | 0.012042 | 0.0079768 | 0.024797 | -0.0015723 | 5.1318e-05 | 0.029433 | 0 | 0.068665 | -0.17853 | -0.21057 | -0.21057 | -0.17853 | -0.28381 | -0.11902 | -0.091553 | -0.40283 | 0.11902 | -121.9803 | 0.29755 | 0.086975 | -122.2595 | -0.10529 | -122.1405 | 0.17853 | 0.013733 | 0.17853 | 0.086975 | 0.36621 | 0.29755 | 0.20599 | 0.11902 | -0.10529 | 0.36621 | 0.29755 | 0.11902 | 0.086975 | 0.20599 | -122.2275 | -122.4518
761.0625 | 122.493 | -0.24261 | 122.0444 | 0.0076294 | 0.01076 | 0.0096856 | 0.020952 | -7.686e-05 | 0.0026147 | 0.02751 | 0.07782 | 0.036621 | -0.16022 | -0.13733 | -0.12817 | -0.091553 | -0.32044 | -0.032043 | -0.1236 | -0.36621 | 0.082398 | -122.0078 | 0.32044 | 0.10529 | -122.1725 | -0.1236 | -122.168 | 0.23804 | -0.07782 | 0.21057 | 0.11444 | 0.27924 | 0.32044 | 0.11902 | 0.15106 | -0.1236 | 0.27924 | 0.32044 | 0.15106 | 0.11444 | 0.11902 | -122.2046 | -122.4106
762.1094 | 122.4609 | -0.25177 | 122.0581 | 0.1297 | 0.0090511 | 0.0056268 | 0.021807 | -0.00050406 | 0.00069212 | 0.026869 | 0.068665 | 0.050354 | -0.15106 | -0.14648 | -0.1236 | -0.082397 | -0.32044 | -0.036621 | -0.10986 | -0.37994 | 0.10071 | -122.0078 | 0.32044 | 0.10529 | -122.1817 | -0.12817 | -122.168 | 0.21973 | -0.068665 | 0.21515 | 0.12817 | 0.30212 | 0.32044 | 0.14191 | 0.16937 | -0.12817 | 0.30212 | 0.32044 | 0.16937 | 0.12817 | 0.14191 | -122.2092 | -122.438
763.0625 | 122.438 | -0.2655 | 122.0535 | 0.15259 | 0.011188 | 0.011181 | 0.025225 | -7.686e-05 | -0.00037588 | 0.027724 | 0.022888 | 0.073242 | -0.17853 | -0.16022 | -0.15564 | -0.1236 | -0.30212 | -0.064087 | -0.10071 | -0.39825 | 0.086975 | -121.9803 | 0.28839 | 0.10529 | -122.2092 | -0.13275 | -122.1542 | 0.20142 | -0.036621 | 0.20142 | 0.10986 | 0.33874 | 0.28839 | 0.16479 | 0.14191 | -0.13275 | 0.33874 | 0.28839 | 0.14191 | 0.10986 | 0.16479 | -122.2321 | -122.4518
764.125 | 122.4701 | -0.25635 | 122.0581 | 0.11444 | 0.0096921 | 0.0075494 | 0.020525 | -0.00071786 | -0.0014441 | 0.028792 | 0.013733 | 0.068665 | -0.17853 | -0.14191 | -0.16022 | -0.12817 | -0.31586 | -0.073242 | -0.10986 | -0.37079 | 0.07782 | -121.9894 | 0.27008 | 0.11444 | -122.2183 | -0.11444 | -122.168 | 0.19226 | -0.059509 | 0.18311 | 0.096131 | 0.32501 | 0.27008 | 0.14649 | 0.12817 | -0.11444 | 0.32501 | 0.27008 | 0.12817 | 0.096131 | 0.14649 | -122.2366 | -122.4289
765.0625 | 122.4792 | -0.24719 | 122.0673 | -0.091553 | 0.010547 | 0.0069086 | 0.017748 | -0.0032813 | -0.00037588 | 0.027297 | 0.013733 | -0.009155 | -0.013733 | -0.16937 | -0.14648 | -0.11902 | -0.25177 | -0.041199 | -0.082397 | -0.36163 | 0.23346 | -122.0764 | 0.26093 | 0.077819 | -122.2137 | -0.11444 | -122.1497 | 0.027466 | -0.004578 | 0.20599 | 0.10071 | 0.23804 | 0.26093 | 0.16479 | 0.12817 | -0.11444 | 0.23804 | 0.26093 | 0.12817 | 0.10071 | 0.16479 | -122.081 | -122.4289
766.1094 | 122.374 | -0.28381 | 122.0993 | -0.045777 | 0.014178 | 0.01524 | 0.025652 | 0.00013674 | -0.0016577 | 0.028578 | 0.036621 | 0.09613 | 0.045776 | -0.16937 | -0.18768 | -0.17395 | -0.19226 | -0.10529 | -0.07782 | -0.39368 | 0.32959 | -122.0032 | 0.32043 | 0.11444 | -122.287 | -0.10986 | -122.1771 | -0.009155 | 0.091552 | 0.17853 | 0.09613 | 0.37994 | 0.32043 | 0.20599 | 0.10986 | -0.10986 | 0.37994 | 0.32043 | 0.10986 | 0.09613 | 0.20599 | -122.0535 | -122.493
767.0625 | 122.4884 | -0.22888 | 122.081 | 0.12207 | 0.012469 | 0.010113 | 0.022234 | 0.00099114 | 0.00026492 | 0.027083 | 0.064087 | 0.064087 | -0.16479 | -0.13733 | -0.13733 | -0.086975 | -0.31586 | -0.041199 | -0.10529 | -0.37079 | 0.064087 | -122.0169 | 0.29297 | 0.091553 | -122.2183 | -0.14191 | -122.1863 | 0.22888 | -0.086975 | 0.18768 | 0.091553 | 0.29297 | 0.29297 | 0.1236 | 0.14191 | -0.14191 | 0.29297 | 0.29297 | 0.14191 | 0.091553 | 0.1236 | -122.2458 | -122.4518
768.125 | 122.3282 | -0.27008 | 122.1313 | 0.091553 | 0.012683 | 0.011608 | 0.025865 | 0.00077754 | -0.0018713 | 0.029219 | -0.027466 | 0.07782 | -0.19226 | -0.23804 | -0.24261 | -0.19684 | -0.16022 | -0.16479 | -0.036621 | -0.39825 | 0.07782 | -122.0535 | 0.24262 | 0.032044 | -122.374 | -0.12817 | -122.168 | 0.16479 | 0.10986 | 0.10529 | 0.027466 | 0.3479 | 0.24262 | 0.23346 | 0.073243 | -0.12817 | 0.3479 | 0.24262 | 0.073243 | 0.027466 | 0.23346 | -122.3236 | -122.5296
769.0625 | 122.3831 | -0.28381 | 122.1222 | -0.28992 | 0.013965 | 0.010327 | 0.017748 | -0.0017859 | -0.00080328 | 0.025588 | 0.013733 | 0.07782 | -0.16479 | -0.17853 | -0.17853 | -0.1831 | -0.11902 | -0.064087 | -0.041199 | -0.40741 | 0.11902 | -122.0444 | 0.29755 | 0.10528 | -122.3007 | -0.1236 | -122.1634 | 0.17853 | 0.16479 | 0.21973 | 0.10528 | 0.36163 | 0.29755 | 0.24261 | 0.10071 | -0.1236 | 0.36163 | 0.29755 | 0.10071 | 0.10528 | 0.24261 | -122.287 | -122.5296
770.125 | 122.374 | -0.27466 | 122.1634 | 0.068664 | 0.012256 | 0.011181 | 0.026079 | -7.686e-05 | 0.0011193 | 0.028151 | -0.027466 | 0.10986 | -0.20599 | -0.24261 | -0.21973 | -0.20142 | -0.13733 | -0.14648 | -0.041199 | -0.39825 | 0.068664 | -122.0535 | 0.24719 | 0.032043 | -122.3831 | -0.1236 | -122.2046 | 0.17853 | 0.13733 | 0.12817 | 0.054931 | 0.38452 | 0.24719 | 0.23346 | 0.073242 | -0.1236 | 0.38452 | 0.24719 | 0.073242 | 0.054931 | 0.23346 | -122.3694 | -122.5616
771.0625 | 122.4335 | -0.25177 | 122.1176 | 0.083923 | 0.011615 | 0.0092584 | 0.023943 | 0.0016321 | -0.00058968 | 0.029647 | 0.013733 | 0.091553 | -0.18768 | -0.18768 | -0.16937 | -0.16022 | -0.2243 | -0.10071 | -0.059509 | -0.37994 | 0.064087 | -122.0261 | 0.2655 | 0.064087 | -122.287 | -0.12817 | -122.1771 | 0.20142 | 0.027466 | 0.15106 | 0.082397 | 0.34332 | 0.2655 | 0.19226 | 0.091553 | -0.12817 | 0.34332 | 0.2655 | 0.091553 | 0.082397 | 0.19226 | -122.3053 | -122.4976
772.125 | 122.4472 | -0.27008 | 122.1222 | 0.14496 | 0.011401 | 0.010754 | 0.021807 | 0.0020593 | -0.0010169 | 0.027938 | 0 | 0.073242 | -0.21057 | -0.19226 | -0.17395 | -0.1236 | -0.24719 | -0.082397 | -0.082397 | -0.37994 | 0.05951 | -122.049 | 0.27008 | 0.07782 | -122.2961 | -0.10986 | -122.2046 | 0.21057 | 0.022889 | 0.18768 | 0.096131 | 0.34332 | 0.27008 | 0.18768 | 0.14649 | -0.10986 | 0.34332 | 0.27008 | 0.14649 | 0.096131 | 0.18768 | -122.3328 | -122.5021
773.0625 | 122.4609 | -0.22888 | 122.1085 | 0.11444 | 0.010974 | 0.0088312 | 0.017107 | 0.00035034 | -0.00037588 | 0.028578 | 0.073242 | 0.054932 | -0.13733 | -0.12817 | -0.10529 | -0.064087 | -0.29297 | 0.013733 | -0.068665 | -0.32501 | 0.091553 | -122.0535 | 0.30212 | 0.10071 | -122.2137 | -0.09613 | -122.1771 | 0.21057 | -0.064087 | 0.24261 | 0.1236 | 0.28381 | 0.30212 | 0.16022 | 0.16479 | -0.09613 | 0.28381 | 0.30212 | 0.16479 | 0.1236 | 0.16022 | -122.2458 | -122.4335
774.1094 | 122.4564 | -0.23346 | 122.0993 | 0.076294 | 0.012897 | 0.008404 | 0.01732 | -0.00050406 | 0.0011193 | 0.031142 | 0.036621 | 0.059509 | -0.14648 | -0.14648 | -0.15106 | -0.09613 | -0.23804 | -0.036621 | -0.073242 | -0.36621 | 0.086975 | -122.0398 | 0.27008 | 0.086975 | -122.2504 | -0.13275 | -122.1725 | 0.18311 | -0.004578 | 0.19684 | 0.082397 | 0.29297 | 0.27008 | 0.16022 | 0.13733 | -0.13275 | 0.29297 | 0.27008 | 0.13733 | 0.082397 | 0.16022 | -122.2458 | -122.4655
775.0625 | 122.4426 | -0.23346 | 122.1268 | 0.038147 | 0.0084103 | 0.0086176 | 0.018175 | -0.0034949 | 0.00026492 | 0.026229 | 0 | 0.054932 | -0.15564 | -0.16022 | -0.14648 | -0.10986 | -0.22888 | -0.032043 | -0.073242 | -0.36621 | 0.077819 | -122.0718 | 0.23346 | 0.073242 | -122.2733 | -0.13275 | -122.2 | 0.15564 | 0.004577 | 0.20142 | 0.086975 | 0.28839 | 0.23346 | 0.16022 | 0.1236 | -0.13275 | 0.28839 | 0.23346 | 0.1236 | 0.086975 | 0.16022 | -122.2824 | -122.493
776.1094 | 122.374 | -0.28381 | 122.168 | -0.28229 | 0.012469 | 0.0075494 | 0.022875 | -0.0034949 | 0.00069212 | 0.027297 | -0.009155 | 0.10986 | -0.21515 | -0.19684 | -0.19684 | -0.1831 | -0.068665 | -0.091553 | -0.022888 | -0.39825 | 0.068664 | -122.0581 | 0.27466 | 0.086975 | -122.3648 | -0.11444 | -122.1909 | 0.20599 | 0.21515 | 0.19226 | 0.086975 | 0.39368 | 0.27466 | 0.26092 | 0.10071 | -0.11444 | 0.39368 | 0.27466 | 0.10071 | 0.086975 | 0.26092 | -122.3831 | -122.5662
777.0625 | 122.5113 | -0.21057 | 122.1313 | 0.22888 | 0.012897 | 0.011395 | 0.023943 | -0.00071786 | -0.00058968 | 0.028792 | 0.07782 | 0.054932 | -0.17853 | -0.10529 | -0.13275 | -0.059509 | -0.30212 | -0.009155 | -0.073242 | -0.3479 | 0.032043 | -122.0764 | 0.28839 | 0.10529 | -122.2641 | -0.13733 | -122.2046 | 0.25635 | -0.091553 | 0.20142 | 0.07782 | 0.2655 | 0.28839 | 0.13733 | 0.15106 | -0.13733 | 0.2655 | 0.28839 | 0.15106 | 0.07782 | 0.13733 | -122.3099 | -122.4792
778.125 | 122.4426 | -0.25177 | 122.1954 | -0.10681 | 0.011615 | 0.0056268 | 0.026079 | 0.0012047 | -0.0020849 | 0.027297 | 0.032043 | 0.073242 | -0.17395 | -0.11902 | -0.15564 | -0.11902 | -0.16479 | -0.041199 | -0.032043 | -0.3479 | 0.07782 | -122.1222 | 0.28381 | 0.13275 | -122.3511 | -0.09613 | -122.2275 | 0.20599 | 0.086975 | 0.21057 | 0.09613 | 0.32501 | 0.28381 | 0.21973 | 0.13275 | -0.09613 | 0.32501 | 0.28381 | 0.13275 | 0.09613 | 0.21973 | -122.3694 | -122.5433
779.0625 | 122.4106 | -0.2655 | 122.1588 | 0.48828 | 0.014605 | 0.010967 | 0.024797 | 0.00013674 | -0.00037588 | 0.027724 | 0.027466 | 0.10986 | -0.17853 | -0.19226 | -0.19684 | -0.18768 | -0.15564 | -0.11444 | -0.036621 | -0.38452 | 0.086975 | -122.0489 | 0.29297 | 0.073242 | -122.3557 | -0.11902 | -122.1954 | 0.20599 | 0.10986 | 0.15106 | 0.068665 | 0.37537 | 0.29297 | 0.22888 | 0.07782 | -0.11902 | 0.37537 | 0.29297 | 0.07782 | 0.068665 | 0.22888 | -122.3373 | -122.5433
780.125 | 122.438 | -0.25177 | 122.1451 | -0.21362 | 0.010547 | 0.012463 | 0.024156 | 0.0014185 | -0.0022987 | 0.02751 | 0.036621 | 0.07782 | -0.17853 | -0.14191 | -0.13733 | -0.12817 | -0.15564 | -0.036621 | -0.036621 | -0.36621 | 0.073242 | -122.0673 | 0.28839 | 0.10986 | -122.2824 | -0.11444 | -122.1817 | 0.21515 | 0.09613 | 0.21515 | 0.11444 | 0.32959 | 0.28839 | 0.21515 | 0.1236 | -0.11444 | 0.32959 | 0.28839 | 0.1236 | 0.11444 | 0.21515 | -122.3236 | -122.5113
781.0625 | 122.4518 | -0.23346 | 122.1405 | 0.12207 | 0.0094785 | 0.010327 | 0.022447 | 0.0029137 | -0.00037588 | 0.027724 | 0.013733 | 0.09613 | -0.19226 | -0.16937 | -0.16022 | -0.12817 | -0.2243 | -0.07782 | -0.054932 | -0.33875 | 0.041198 | -122.0444 | 0.24719 | 0.064086 | -122.3007 | -0.10529 | -122.1954 | 0.20599 | 0.009155 | 0.15564 | 0.073242 | 0.32959 | 0.24719 | 0.17853 | 0.10528 | -0.10529 | 0.32959 | 0.24719 | 0.10528 | 0.073242 | 0.17853 | -122.3328 | -122.4792
782.125 | 122.374 | -0.24261 | 122.1909 | -0.35095 | 0.010547 | 0.0086176 | 0.020098 | 0.0020593 | 0.00047852 | 0.026656 | -0.022888 | 0.10071 | -0.1831 | -0.20142 | -0.16479 | -0.1831 | -0.059509 | -0.064087 | -0.004578 | -0.37079 | 0.05951 | -122.0901 | 0.21973 | 0.041199 | -122.3557 | -0.12817 | -122.1954 | 0.16022 | 0.18311 | 0.17853 | 0.07782 | 0.34332 | 0.21973 | 0.23804 | 0.05951 | -0.12817 | 0.34332 | 0.21973 | 0.05951 | 0.07782 | 0.23804 | -122.374 | -122.5616
783.0625 | 122.4838 | -0.2243 | 122.1497 | -1.1826 | 0.0096921 | 0.0060542 | 0.016039 | -7.686e-05 | -0.00080328 | 0.028792 | -0.022888 | 0.009155 | -0.064087 | -0.15564 | -0.13733 | -0.07782 | -0.21515 | -0.018311 | -0.068665 | -0.32959 | 0.16022 | -122.1405 | 0.20142 | 0.068664 | -122.287 | -0.10529 | -122.2183 | 0.041199 | 0.009155 | 0.20599 | 0.086975 | 0.23346 | 0.20142 | 0.15564 | 0.14648 | -0.10529 | 0.23346 | 0.20142 | 0.14648 | 0.086975 | 0.15564 | -122.2137 | -122.4792
784.1094 | 122.3923 | -0.26093 | 122.1725 | 0.083923 | 0.012469 | 0.0064814 | 0.025438 | -7.686e-05 | 0.00090572 | 0.028365 | -0.009155 | 0.086975 | -0.19226 | -0.20599 | -0.21057 | -0.17395 | -0.13733 | -0.13275 | -0.009155 | -0.37537 | 0.068664 | -122.0856 | 0.25177 | 0.054931 | -122.3831 | -0.11444 | -122.1817 | 0.18311 | 0.1236 | 0.12817 | 0.050354 | 0.3479 | 0.25177 | 0.25177 | 0.086975 | -0.11444 | 0.3479 | 0.25177 | 0.086975 | 0.050354 | 0.25177 | -122.3648 | -122.5479
785.0625 | 122.4747 | -0.2655 | 122.1313 | -0.10681 | 0.0088375 | 0.0069086 | 0.015612 | -0.0017859 | 0.0017603 | 0.02751 | 0.009155 | 0.041199 | -0.14191 | -0.28839 | -0.20142 | -0.12817 | -0.31128 | -0.045776 | -0.09613 | -0.31586 | 0.1236 | -122.0901 | 0.27466 | -0.022888 | -122.3328 | -0.050354 | -122.2275 | 0.15106 | -0.045776 | 0.21973 | 0.064087 | 0.3067 | 0.27466 | 0.16937 | 0.13733 | -0.050354 | 0.3067 | 0.27466 | 0.13733 | 0.064087 | 0.16937 | -122.2733 | -122.4472
786.125 | 122.4564 | -0.24719 | 122.1634 | -0.045777 | 0.011188 | 0.011395 | 0.025225 | -0.00050406 | -0.0010169 | 0.029647 | 0.054932 | 0.12817 | 0.33875 | -0.13275 | -0.16022 | -0.13275 | -0.15106 | -0.050354 | -0.041199 | -0.37994 | 0.58594 | -122.0352 | 0.30212 | 0.11444 | -122.3236 | -0.13275 | -122.2046 | -0.28381 | 0.09613 | 0.19684 | 0.086975 | 0.37537 | 0.30212 | 0.20599 | 0.11444 | -0.13275 | 0.37537 | 0.30212 | 0.11444 | 0.086975 | 0.20599 | -121.8246 | -122.5433
787.0625 | 122.4518 | -0.22888 | 122.1542 | 0.14496 | 0.011615 | 0.010754 | 0.023729 | 0.00099114 | -0.00058968 | 0.030074 | 0.013733 | 0.073242 | -0.18768 | -0.16022 | -0.14648 | -0.11902 | -0.2243 | -0.054932 | -0.027466 | -0.35248 | 0.041199 | -122.081 | 0.24261 | 0.068665 | -122.3007 | -0.1236 | -122.1817 | 0.20142 | 0.004578 | 0.17395 | 0.082398 | 0.30212 | 0.24261 | 0.20142 | 0.10986 | -0.1236 | 0.30212 | 0.24261 | 0.10986 | 0.082398 | 0.20142 | -122.3419 | -122.5067
788.125 | 122.4884 | -0.23804 | 122.1268 | 0.11444 | 0.011401 | 0.011608 | 0.021379 | -7.686e-05 | -0.00080328 | 0.02751 | 0.018311 | 0.064087 | -0.1831 | -0.14191 | -0.14648 | -0.10071 | -0.24719 | -0.032043 | -0.064087 | -0.35248 | 0.054932 | -122.0627 | 0.25635 | 0.09613 | -122.2733 | -0.11444 | -122.1909 | 0.20142 | -0.009155 | 0.20599 | 0.091553 | 0.30212 | 0.25635 | 0.17395 | 0.13733 | -0.11444 | 0.30212 | 0.25635 | 0.13733 | 0.091553 | 0.17395 | -122.3099 | -122.4792
789.0625 | 122.438 | -0.24719 | 122.168 | 0.1297 | 0.012683 | 0.012036 | 0.024156 | 0.00077754 | 0.00047852 | 0.02751 | 0 | 0.073242 | -0.19684 | -0.17395 | -0.18768 | -0.13733 | -0.18768 | -0.09613 | -0.013733 | -0.36621 | 0.050354 | -122.0947 | 0.24719 | 0.073242 | -122.3557 | -0.11902 | -122.1817 | 0.19684 | 0.059509 | 0.15106 | 0.059509 | 0.32043 | 0.24719 | 0.23346 | 0.10986 | -0.11902 | 0.32043 | 0.24719 | 0.10986 | 0.059509 | 0.23346 | -122.3648 | -122.5342
790.125 | 122.4289 | -0.24261 | 122.1954 | -0.053406 | 0.0096921 | 0.007763 | 0.02202 | 0.00035034 | -0.0042213 | 0.029219 | 0.022888 | 0.091553 | -0.022888 | -0.14648 | -0.16479 | -0.13733 | -0.15106 | -0.059509 | -0.018311 | -0.37537 | 0.21973 | -122.1039 | 0.2655 | 0.096131 | -122.3602 | -0.13275 | -122.2137 | 0.045776 | 0.091553 | 0.18311 | 0.07782 | 0.33417 | 0.2655 | 0.2243 | 0.10529 | -0.13275 | 0.33417 | 0.2655 | 0.10529 | 0.07782 | 0.2243 | -122.2183 | -122.5708
791.0625 | 122.5021 | -0.20599 | 122.1542 | 0.11444 | 0.011188 | 0.013958 | 0.020098 | 0.00013674 | 0.0011193 | 0.02751 | 0.013733 | 0.073242 | -0.19226 | -0.14648 | -0.12817 | -0.082397 | -0.25177 | -0.027466 | -0.064087 | -0.34332 | 0.013733 | -122.081 | 0.21973 | 0.05951 | -122.2824 | -0.13733 | -122.2183 | 0.20599 | -0.045776 | 0.17853 | 0.07782 | 0.27924 | 0.21973 | 0.14191 | 0.1236 | -0.13733 | 0.27924 | 0.21973 | 0.1236 | 0.07782 | 0.14191 | -122.3465 | -122.4976
792.1094 | 122.406 | -0.25177 | 122.1771 | -0.25177 | 0.012683 | 0.0092584 | 0.021807 | -0.0011451 | -0.00037588 | 0.026869 | -0.022888 | 0.10071 | -0.19684 | -0.17853 | -0.16022 | -0.16479 | -0.036621 | -0.068665 | -0.009155 | -0.37537 | 0.054932 | -122.0764 | 0.22888 | 0.073242 | -122.3373 | -0.1236 | -122.1863 | 0.17395 | 0.21515 | 0.1831 | 0.091553 | 0.35248 | 0.22888 | 0.24261 | 0.086975 | -0.1236 | 0.35248 | 0.22888 | 0.086975 | 0.091553 | 0.24261 | -122.374 | -122.5525
793.0781 | 122.3785 | -0.25635 | 122.2046 | 0.038147 | 0.012897 | 0.0086176 | 0.023302 | 0.00099114 | -0.00058968 | 0.026229 | -0.022888 | 0.091553 | -0.18768 | -0.21515 | -0.21973 | -0.19684 | -0.10071 | -0.13275 | 0.004578 | -0.37994 | 0.068665 | -122.113 | 0.23346 | 0.041199 | -122.4243 | -0.1236 | -122.2 | 0.16479 | 0.15564 | 0.1236 | 0.036621 | 0.3479 | 0.23346 | 0.26093 | 0.05951 | -0.1236 | 0.3479 | 0.23346 | 0.05951 | 0.036621 | 0.26093 | -122.3923 | -122.5845
794.1094 | 122.3785 | -0.2655 | 122.1954 | -0.045777 | 0.013751 | 0.009472 | 0.023088 | 0.0018457 | -0.0012305 | 0.028151 | 0 | 0.10986 | -0.19226 | -0.19684 | -0.19226 | -0.1831 | -0.11444 | -0.12817 | -0.013733 | -0.36621 | 0.073242 | -122.0856 | 0.2655 | 0.068665 | -122.3877 | -0.10071 | -122.2092 | 0.19226 | 0.15106 | 0.13733 | 0.073242 | 0.37537 | 0.2655 | 0.25177 | 0.082398 | -0.10071 | 0.37537 | 0.2655 | 0.082398 | 0.073242 | 0.25177 | -122.3877 | -122.5616
795.0625 | 122.5113 | -0.21515 | 122.1725 | -0.0076296 | 0.010547 | 0.0096856 | 0.015398 | -0.00093146 | -0.00016228 | 0.027938 | 0.013733 | 0.054932 | -0.13733 | -0.15106 | -0.11444 | -0.064087 | -0.21973 | -0.013733 | -0.022888 | -0.32044 | 0.07782 | -122.1176 | 0.22888 | 0.064087 | -122.287 | -0.10529 | -122.1954 | 0.15106 | -0.004578 | 0.20142 | 0.10071 | 0.27008 | 0.22888 | 0.19226 | 0.15106 | -0.10529 | 0.27008 | 0.22888 | 0.15106 | 0.10071 | 0.19226 | -122.3099 | -122.493
796.125 | 122.4426 | -0.22888 | 122.1954 | -0.59509 | 0.011188 | 0.0060542 | 0.025225 | -7.686e-05 | -0.0018713 | 0.027938 | 0.050354 | 0.13275 | 0.33875 | -0.13275 | -0.16479 | -0.11902 | -0.13733 | -0.050354 | -0.004578 | -0.35248 | 0.56763 | -122.0627 | 0.27924 | 0.096131 | -122.3602 | -0.1236 | -122.2 | -0.28839 | 0.091553 | 0.17853 | 0.064087 | 0.36163 | 0.27924 | 0.2243 | 0.10986 | -0.1236 | 0.36163 | 0.27924 | 0.10986 | 0.064087 | 0.2243 | -121.8567 | -122.5479
797.0625 | 122.4518 | -0.22888 | 122.1954 | 0.099182 | 0.012256 | 0.012036 | 0.022661 | 0.0014185 | -0.0012305 | 0.030928 | -0.013733 | 0.11902 | -0.19226 | -0.2655 | -0.27008 | -0.068665 | -0.045776 | -0.16937 | 0.004578 | -0.33875 | 0.036621 | -122.0764 | 0.21515 | -0.036621 | -122.4655 | -0.10986 | -122.1909 | 0.17853 | 0.18311 | 0.059509 | -0.041199 | 0.3479 | 0.21515 | 0.23346 | 0.16022 | -0.10986 | 0.3479 | 0.21515 | 0.16022 | -0.041199 | 0.23346 | -122.3877 | -122.5342
798.1406 | 122.4197 | -0.24261 | 122.2046 | -0.35858 | 0.0084103 | 0.0079768 | 0.018389 | -0.00029046 | -0.0018713 | 0.029433 | 0 | 0.07782 | -0.1831 | -0.17395 | -0.16479 | -0.13275 | -0.068665 | -0.059509 | 0.013733 | -0.34332 | 0.05951 | -122.1268 | 0.24261 | 0.068665 | -122.3694 | -0.10071 | -122.1909 | 0.1831 | 0.17395 | 0.18311 | 0.07782 | 0.32044 | 0.24261 | 0.25635 | 0.10986 | -0.10071 | 0.32044 | 0.24261 | 0.10986 | 0.07782 | 0.25635 | -122.3877 | -122.5479
799.0625 | 122.4243 | -0.23346 | 122.2 | 0.068664 | 0.010119 | 0.008404 | 0.022447 | 0.00056394 | 0.0017603 | 0.028151 | 0.036621 | 0.10529 | -0.17395 | -0.1831 | -0.18768 | -0.14191 | -0.13275 | -0.10071 | 0 | -0.35248 | 0.059509 | -122.0947 | 0.27008 | 0.050354 | -122.3877 | -0.11902 | -122.2 | 0.21057 | 0.10071 | 0.13275 | 0.045776 | 0.33875 | 0.27008 | 0.23346 | 0.091552 | -0.11902 | 0.33875 | 0.27008 | 0.091552 | 0.045776 | 0.23346 | -122.374 | -122.5525
800.125 | 122.4014 | -0.2243 | 122.2183 | 0.099182 | 0.013324 | 0.010327 | 0.024584 | 0.0014185 | -0.00016228 | 0.028365 | -0.041199 | 0.09613 | -0.19684 | -0.19684 | -0.21057 | -0.16937 | -0.09613 | -0.11444 | -0.004578 | -0.36621 | 0.027466 | -122.1222 | 0.18311 | 0.027466 | -122.4289 | -0.14191 | -122.2229 | 0.15564 | 0.12817 | 0.10986 | 0.013733 | 0.32043 | 0.18311 | 0.21973 | 0.054931 | -0.14191 | 0.32043 | 0.18311 | 0.054931 | 0.013733 | 0.21973 | -122.4152 | -122.5845
801.0625 | 122.4609 | -0.21515 | 122.1634 | 0.091553 | 0.01311 | 0.011822 | 0.020738 | 0.00035034 | 0.00090572 | 0.029647 | 0.018311 | 0.10986 | -0.18768 | -0.16479 | -0.16022 | -0.10529 | -0.1831 | -0.068665 | -0.022888 | -0.35248 | 0.027466 | -122.0535 | 0.23346 | 0.050354 | -122.3236 | -0.13733 | -122.1863 | 0.20599 | 0.032044 | 0.14648 | 0.054932 | 0.32501 | 0.23346 | 0.19226 | 0.10986 | -0.13733 | 0.32501 | 0.23346 | 0.10986 | 0.054932 | 0.19226 | -122.3511 | -122.5159
802.1094 | 122.4792 | -0.22888 | 122.1954 | -0.12207 | 0.01311 | 0.0090448 | 0.023516 | 0.00099114 | 5.1318e-05 | 0.029006 | 0.050354 | 0.091553 | -0.1831 | -0.09613 | -0.11444 | -0.10986 | -0.1236 | -0.013733 | -0.004578 | -0.34332 | 0.045777 | -122.1039 | 0.27924 | 0.13275 | -122.3099 | -0.11444 | -122.2 | 0.23346 | 0.10529 | 0.21515 | 0.11444 | 0.32044 | 0.27924 | 0.2243 | 0.11902 | -0.11444 | 0.32044 | 0.27924 | 0.11902 | 0.11444 | 0.2243 | -122.3785 | -122.5388
803.0781 | 122.406 | -0.25177 | 122.2046 | -0.0076296 | 0.012469 | 0.0086176 | 0.023516 | 0.0016321 | -0.0022987 | 0.029219 | -0.009155 | 0.091553 | -0.17395 | -0.18768 | -0.19684 | -0.16022 | -0.086975 | -0.09613 | -0.013733 | -0.37079 | 0.07782 | -122.113 | 0.24261 | 0.064087 | -122.4014 | -0.11902 | -122.2183 | 0.16479 | 0.16479 | 0.15564 | 0.054932 | 0.34332 | 0.24261 | 0.23804 | 0.091553 | -0.11902 | 0.34332 | 0.24261 | 0.091553 | 0.054932 | 0.23804 | -122.3785 | -122.5754
804.125 | 122.4655 | -0.22888 | 122.2046 | -0.20599 | 0.012042 | 0.011395 | 0.022447 | 0.0012047 | -0.0018713 | 0.027083 | 0.027466 | 0.07782 | -0.17395 | -0.11444 | -0.1236 | -0.10529 | -0.11902 | -0.018311 | -0.009155 | -0.35706 | 0.054932 | -122.1268 | 0.25635 | 0.11444 | -122.3282 | -0.12817 | -122.2137 | 0.20142 | 0.10986 | 0.21057 | 0.10529 | 0.3067 | 0.25635 | 0.21973 | 0.1236 | -0.12817 | 0.3067 | 0.25635 | 0.1236 | 0.10529 | 0.21973 | -122.3785 | -122.5616
805.0625 | 122.5159 | -0.17853 | 122.1909 | 0.076294 | 0.010547 | 0.007763 | 0.01732 | 0.0018457 | -0.0010169 | 0.028151 | 0.050354 | 0.032043 | -0.17395 | -0.10071 | -0.068665 | -0.032043 | -0.26093 | 0.036621 | -0.054932 | -0.32044 | 0.004578 | -122.1588 | 0.22888 | 0.07782 | -122.2595 | -0.14191 | -122.2458 | 0.2243 | -0.082397 | 0.21515 | 0.10986 | 0.21057 | 0.22888 | 0.1236 | 0.14648 | -0.14191 | 0.21057 | 0.22888 | 0.14648 | 0.10986 | 0.1236 | -122.3648 | -122.5113
806.1094 | 122.4518 | -0.23346 | 122.2046 | -0.28229 | 0.012683 | 0.009472 | 0.021807 | 0.00056394 | -0.00016228 | 0.026869 | 0 | 0.10529 | -0.19684 | -0.16937 | -0.16937 | -0.14648 | -0.07782 | -0.045776 | 0.004578 | -0.35706 | 0.036621 | -122.0993 | 0.23346 | 0.064086 | -122.374 | -0.1236 | -122.2 | 0.19684 | 0.15564 | 0.18768 | 0.064086 | 0.33875 | 0.23346 | 0.23804 | 0.086975 | -0.1236 | 0.33875 | 0.23346 | 0.086975 | 0.064086 | 0.23804 | -122.4014 | -122.5616
807.0625 | 122.4426 | -0.22888 | 122.2046 | -0.076294 | 0.01311 | 0.010113 | 0.022875 | 0.00035034 | 0.00090572 | 0.027938 | 0.032043 | 0.10529 | 0.07782 | -0.13275 | -0.13733 | -0.11444 | -0.13275 | -0.059509 | -0.009155 | -0.35248 | 0.3067 | -122.0993 | 0.26093 | 0.096131 | -122.3419 | -0.1236 | -122.2137 | -0.045777 | 0.096131 | 0.16937 | 0.091553 | 0.33417 | 0.26093 | 0.21973 | 0.11444 | -0.1236 | 0.33417 | 0.26093 | 0.11444 | 0.091553 | 0.21973 | -122.1268 | -122.5571
808.1406 | 122.5342 | -0.21515 | 122.1863 | -0.061035 | 0.0094785 | 0.0079768 | 0.013475 | -0.00093146 | -0.0014441 | 0.030501 | -0.23804 | 0.036621 | -0.28839 | -0.13733 | -0.10986 | -0.064087 | -0.20142 | 0.013733 | -0.059509 | -0.3067 | -0.073242 | -122.1497 | -0.022888 | 0.07782 | -122.2961 | -0.091553 | -122.2458 | 0.050354 | 0.013733 | 0.22888 | 0.10529 | 0.25177 | -0.022888 | 0.15564 | 0.15106 | -0.091553 | 0.25177 | -0.022888 | 0.15106 | 0.10529 | 0.15564 | -122.4747 | -122.493
809.0625 | 122.4197 | -0.23804 | 122.2275 | 0.022888 | 0.013537 | 0.0098994 | 0.024156 | -0.00029046 | -0.00058968 | 0.027297 | -0.004578 | 0.086975 | -0.17853 | -0.19684 | -0.1831 | -0.17395 | -0.07782 | -0.1236 | -0.009155 | -0.37079 | 0.059509 | -122.1405 | 0.23346 | 0.041199 | -122.4106 | -0.13275 | -122.2366 | 0.17395 | 0.16022 | 0.11444 | 0.054932 | 0.32501 | 0.23346 | 0.22888 | 0.064087 | -0.13275 | 0.32501 | 0.23346 | 0.064087 | 0.054932 | 0.22888 | -122.406 | -122.5983
810.125 | 122.3969 | -0.2243 | 122.2137 | 0.022888 | 0.0096921 | 0.009472 | 0.023516 | 0.00056394 | -0.0022987 | 0.025588 | -0.022888 | 0.082397 | -0.1831 | -0.17395 | -0.19684 | -0.16479 | -0.073242 | -0.11902 | 0.004578 | -0.36621 | 0.041199 | -122.1313 | 0.20142 | 0.050354 | -122.4106 | -0.14191 | -122.2092 | 0.16022 | 0.15106 | 0.10529 | 0.027466 | 0.3067 | 0.20142 | 0.22888 | 0.059509 | -0.14191 | 0.3067 | 0.20142 | 0.059509 | 0.027466 | 0.22888 | -122.3969 | -122.58

## Thermal Data
Fire Time | South 11 C | Cable 1 | Cable 2
-0.4021 | 25.7637 | 23.4231 | 23.5815
0.5979 | 25.7633 | 23.4217 | 23.5846
1.5979 | 25.7616 | 23.4111 | 23.5822
2.5979 | 25.7658 | 23.4235 | 23.5907
3.5979 | 25.825 | 23.4172 | 23.5872
4.5979 | 26.3813 | 23.406 | 23.5848
5.5979 | 27.697 | 23.4187 | 23.5934
6.5979 | 29.7879 | 23.41 | 23.5928
7.5979 | 32.4779 | 23.4183 | 23.59
8.5979 | 35.7091 | 23.4302 | 23.5903
9.5979 | 39.3457 | 23.428 | 23.607
10.5979 | 43.3427 | 23.4493 | 23.6124
11.5979 | 47.6149 | 23.4601 | 23.6292
12.5979 | 52.0968 | 23.4796 | 23.6482
13.5979 | 56.8019 | 23.5075 | 23.6839
14.5979 | 61.6515 | 23.5399 | 23.7199
15.5979 | 66.6151 | 23.5788 | 23.7592
16.5979 | 71.7583 | 23.62 | 23.8139
17.5979 | 77.0344 | 23.6714 | 23.8719
18.5979 | 82.4892 | 23.7368 | 23.9375
19.5979 | 88.0518 | 23.81 | 24.0176
20.5979 | 93.7155 | 23.8634 | 24.1196
21.5979 | 99.388 | 23.9702 | 24.2189
22.5979 | 105.1396 | 24.0619 | 24.3392
23.5979 | 110.9728 | 24.1745 | 24.4648
24.5979 | 116.7871 | 24.3079 | 24.6166
25.5979 | 122.7028 | 24.4393 | 24.7624
26.5979 | 128.6735 | 24.5896 | 24.9283
27.5979 | 134.6278 | 24.729 | 25.124
28.5979 | 140.6218 | 24.8983 | 25.3226
29.5979 | 146.5833 | 25.096 | 25.5453
30.5979 | 152.4965 | 25.2843 | 25.7751
31.5979 | 158.3736 | 25.5034 | 26.0146
32.5979 | 164.3191 | 25.7334 | 26.2764
33.5979 | 170.227 | 25.9868 | 26.5717
34.5979 | 176.0872 | 26.2568 | 26.8555
35.5979 | 182.0819 | 26.5506 | 27.1638
36.5979 | 188.0341 | 26.8725 | 27.4876
37.5979 | 194.0377 | 27.202 | 27.8307
38.5979 | 200.0569 | 27.5547 | 28.1945
39.5979 | 205.9155 | 27.9067 | 28.5693
40.5979 | 211.7031 | 28.2895 | 28.9786
41.5979 | 217.5837 | 28.6908 | 29.3947
42.5979 | 223.492 | 29.1051 | 29.8344
43.5979 | 229.4537 | 29.5375 | 30.2859
44.5979 | 235.3743 | 29.9899 | 30.7572
45.5979 | 241.2158 | 30.4661 | 31.2659
46.5979 | 247.035 | 30.9603 | 31.7829
47.5979 | 252.8281 | 31.4552 | 32.3272
48.5979 | 258.5489 | 31.9897 | 32.8995
49.5979 | 264.2764 | 32.5337 | 33.4872
50.5979 | 269.8646 | 33.093 | 34.0992
51.5979 | 275.447 | 33.6704 | 34.7453
52.5979 | 280.9754 | 34.2884 | 35.4059
53.5979 | 286.2253 | 34.9173 | 36.088
54.5979 | 291.0945 | 35.5757 | 36.8071
55.5979 | 295.3803 | 36.246 | 37.5219
56.5979 | 299.373 | 36.9377 | 38.2691
57.5979 | 303.1903 | 37.6254 | 39.0316
58.5979 | 306.7636 | 38.3328 | 39.8267
59.5979 | 310.3131 | 39.0507 | 40.6422
60.5979 | 313.6444 | 39.7732 | 41.4462
61.5979 | 316.9584 | 40.4935 | 42.2734
62.5979 | 319.81 | 41.2326 | 43.0986
63.5979 | 322.3702 | 41.9878 | 43.9212
64.5979 | 324.616 | 42.7591 | 44.7478
65.5979 | 326.5372 | 43.526 | 45.581
66.5979 | 328.1463 | 44.3068 | 46.4168
67.5979 | 329.6235 | 45.0847 | 47.2455
68.5979 | 330.8028 | 45.8821 | 48.0841
69.5979 | 331.7244 | 46.6614 | 48.9016
70.5979 | 332.341 | 47.4466 | 49.7436
71.5979 | 332.7363 | 48.2378 | 50.5848
72.5979 | 333.1754 | 49.0282 | 51.4209
73.5979 | 333.4654 | 49.8227 | 52.2688
74.5979 | 333.6269 | 50.5965 | 53.1302
75.5979 | 333.5167 | 51.382 | 53.981
76.5979 | 333.4898 | 52.1606 | 54.8553
77.5979 | 333.4413 | 52.9406 | 55.7389
78.5979 | 333.322 | 53.7235 | 56.6047
79.5979 | 333.1499 | 54.4928 | 57.4832
80.5979 | 332.7783 | 55.2872 | 58.3602
81.5979 | 332.3972 | 56.0461 | 59.2342
82.5979 | 332.2211 | 56.8049 | 60.1172
83.5979 | 332.0533 | 57.5738 | 60.9929
84.5979 | 331.7316 | 58.3307 | 61.8661
85.5979 | 331.3106 | 59.0699 | 62.7252
86.5979 | 331.0094 | 59.7999 | 63.5823
87.5979 | 330.5804 | 60.5469 | 64.4245
88.5979 | 330.1477 | 61.2817 | 65.2686
89.5979 | 329.6827 | 62.0178 | 66.0869
90.5979 | 329.1882 | 62.7311 | 66.9061
91.5979 | 328.7394 | 63.4507 | 67.6938
92.5979 | 328.3096 | 64.1603 | 68.488
93.5979 | 327.9625 | 64.868 | 69.2721
94.5979 | 327.5622 | 65.5659 | 70.0574
95.5979 | 327.1046 | 66.2532 | 70.8313
96.5979 | 326.7289 | 66.9237 | 71.5991
97.5979 | 326.3628 | 67.5977 | 72.367
98.5979 | 325.8987 | 68.2679 | 73.1327
99.5979 | 325.2976 | 68.927 | 73.8957
100.5979 | 324.9061 | 69.5643 | 74.6353
101.5979 | 324.4921 | 70.2105 | 75.3652
102.5979 | 324.2543 | 70.8416 | 76.094
103.5979 | 323.9646 | 71.4758 | 76.7953
104.5979 | 323.7003 | 72.0978 | 77.4995
105.6292 | 323.3907 | 72.7297 | 78.2065
106.5979 | 323.1303 | 73.3177 | 78.8626
107.5979 | 322.9774 | 73.9242 | 79.5314
108.5979 | 322.8814 | 74.5214 | 80.1963
109.5979 | 322.753 | 75.116 | 80.8504
110.5979 | 322.6825 | 75.6943 | 81.5057
111.5979 | 322.6342 | 76.2692 | 82.1653
112.5979 | 322.6176 | 76.854 | 82.82
113.5979 | 322.7076 | 77.4097 | 83.4926
114.5979 | 322.7875 | 78.0024 | 84.1398
115.5979 | 323.0146 | 78.5523 | 84.7889
116.5979 | 323.2088 | 79.1289 | 85.4312
117.5979 | 323.4635 | 79.6732 | 86.0652
118.5979 | 323.6432 | 80.2271 | 86.6959
119.5979 | 323.8146 | 80.7647 | 87.3173
120.5979 | 323.9466 | 81.3333 | 87.9393
121.5979 | 324.1101 | 81.8862 | 88.5493
122.5979 | 324.2951 | 82.4231 | 89.1554
123.5979 | 324.5531 | 82.9713 | 89.7746
124.5979 | 324.797 | 83.5115 | 90.3996
125.5979 | 325.0232 | 84.0567 | 91.0039
126.5979 | 325.2256 | 84.6037 | 91.6193
127.5979 | 325.4561 | 85.1486 | 92.2303
128.5979 | 325.6662 | 85.6928 | 92.858
129.5979 | 325.894 | 86.224 | 93.4719
130.5979 | 326.0431 | 86.7712 | 94.0821
131.5979 | 326.296 | 87.2997 | 94.6929
132.5979 | 326.5647 | 87.8481 | 95.3006
133.5979 | 326.7404 | 88.383 | 95.9109
134.5979 | 326.942 | 88.9248 | 96.5134
135.5979 | 327.1203 | 89.4497 | 97.1032
136.5979 | 327.3868 | 89.9806 | 97.7078
137.5979 | 327.4609 | 90.4956 | 98.3026
138.5979 | 327.6487 | 91.0306 | 98.887
139.5979 | 327.8298 | 91.5515 | 99.4767
140.5979 | 327.8602 | 92.0777 | 100.0712
141.5979 | 327.8937 | 92.6123 | 100.6492
142.5979 | 328.0263 | 93.1438 | 101.2405
143.5979 | 328.2038 | 93.6779 | 101.8329
144.5979 | 328.2338 | 94.2007 | 102.4285
145.5979 | 328.2366 | 94.7103 | 103.0121
146.5979 | 328.2837 | 95.2327 | 103.6059
147.5979 | 328.3971 | 95.7693 | 104.205
148.5979 | 328.496 | 96.2869 | 104.7922
149.5979 | 328.4815 | 96.8068 | 105.3879
150.5979 | 328.4967 | 97.3357 | 105.9743
151.5979 | 328.6945 | 97.8495 | 106.5679
152.5979 | 328.8284 | 98.3772 | 107.1493
153.5979 | 328.9176 | 98.898 | 107.7285
154.5979 | 328.9987 | 99.4119 | 108.3261
155.5979 | 329.0949 | 99.931 | 108.9178
156.5979 | 329.1416 | 100.4734 | 109.5066
157.5979 | 329.1411 | 100.9897 | 110.0966
158.5979 | 329.1142 | 101.5201 | 110.6807
159.5979 | 329.1797 | 102.0385 | 111.2747
160.6135 | 329.1396 | 102.5679 | 111.8642
161.5979 | 329.2276 | 103.0942 | 112.4481
162.5979 | 329.324 | 103.6047 | 113.0373
163.5979 | 329.2749 | 104.1122 | 113.6285
164.5979 | 329.2423 | 104.6319 | 114.2138
165.5979 | 329.235 | 105.1438 | 114.7945
166.5979 | 329.2251 | 105.6631 | 115.3839
167.5979 | 329.2877 | 106.1631 | 115.9664
168.5979 | 329.2105 | 106.6722 | 116.558
169.5979 | 329.215 | 107.1773 | 117.1349
170.5979 | 329.2539 | 107.6804 | 117.7079
171.5979 | 329.3277 | 108.1751 | 118.2887
172.5979 | 329.3203 | 108.6885 | 118.8737
173.5979 | 329.3772 | 109.1779 | 119.4569
174.5979 | 329.4045 | 109.6744 | 120.0394
175.5979 | 329.3576 | 110.1792 | 120.6184
176.5979 | 329.2645 | 110.6596 | 121.21
177.5979 | 329.308 | 111.1536 | 121.7903
178.5979 | 329.4102 | 111.6597 | 122.3588
179.5979 | 329.479 | 112.1409 | 122.9276
180.5979 | 329.5362 | 112.6346 | 123.5016
181.5979 | 329.5796 | 113.1166 | 124.0594
182.5979 | 329.6274 | 113.6012 | 124.6257
183.5979 | 329.7441 | 114.0761 | 125.1851
184.5979 | 329.7167 | 114.5387 | 125.7514
185.5979 | 329.7448 | 115.0018 | 126.3142
186.5979 | 329.7406 | 115.477 | 126.8767
187.5979 | 329.7903 | 115.9374 | 127.439
188.5979 | 329.7958 | 116.3994 | 128.0126
189.5979 | 329.6082 | 116.8595 | 128.5851
190.5979 | 329.5945 | 117.3248 | 129.1406
191.5979 | 329.6177 | 117.7815 | 129.7084
192.5979 | 329.6413 | 118.2427 | 130.2737
193.5979 | 329.5528 | 118.678 | 130.8513
194.5979 | 329.5309 | 119.1311 | 131.4073
195.5979 | 329.521 | 119.5953 | 131.9688
196.5979 | 329.4368 | 120.049 | 132.5366
197.5979 | 329.4091 | 120.498 | 133.0918
198.5979 | 329.3207 | 120.9449 | 133.6569
199.5979 | 329.2737 | 121.402 | 134.2169
200.5979 | 329.297 | 121.8367 | 134.7809
201.5979 | 329.3386 | 122.2674 | 135.3392
202.5979 | 329.2918 | 122.6908 | 135.8824
203.5979 | 329.3854 | 123.1283 | 136.4421
204.5979 | 329.4611 | 123.5573 | 136.9917
205.5979 | 329.4408 | 123.9743 | 137.5388
206.5979 | 329.3189 | 124.4139 | 138.0854
207.5979 | 329.2548 | 124.835 | 138.6339
208.5979 | 329.2298 | 125.2558 | 139.1653
209.5979 | 329.2169 | 125.6991 | 139.7063
210.5979 | 329.1797 | 126.1335 | 140.2394
211.5979 | 329.1558 | 126.5568 | 140.7863
212.5979 | 329.1399 | 126.9935 | 141.318
213.5979 | 329.1957 | 127.4173 | 141.8584
214.5979 | 329.2073 | 127.8372 | 142.401
215.5979 | 329.2003 | 128.2713 | 142.9401
216.5979 | 329.2091 | 128.6578 | 143.4964
217.5979 | 329.2409 | 129.0892 | 144.0378
218.5979 | 329.2996 | 129.493 | 144.5781
219.5979 | 329.2613 | 129.893 | 145.1186
220.5979 | 329.1681 | 130.2932 | 145.6495
221.5979 | 329.1817 | 130.6939 | 146.1809
222.5979 | 329.3237 | 131.1071 | 146.7362
223.5979 | 329.4146 | 131.5126 | 147.2768
224.5979 | 329.3963 | 131.93 | 147.8249
225.5979 | 329.2972 | 132.3411 | 148.3752
226.5979 | 329.2864 | 132.7484 | 148.9065
227.5979 | 329.2595 | 133.1829 | 149.4604
228.5979 | 329.2056 | 133.6005 | 150.0064
229.5979 | 329.217 | 134.0226 | 150.5817
230.5979 | 329.1958 | 134.4466 | 151.1255
231.5979 | 329.1854 | 134.8735 | 151.6852
232.5979 | 329.1736 | 135.295 | 152.2296
233.5979 | 329.1692 | 135.6897 | 152.7669
234.5979 | 329.1514 | 136.0903 | 153.298
235.5979 | 329.1867 | 136.5011 | 153.8307
236.6292 | 329.2413 | 136.9088 | 154.3757
237.5979 | 329.1567 | 137.2667 | 154.8833
238.5979 | 329.1923 | 137.6686 | 155.4093
239.5979 | 329.0574 | 138.0508 | 155.9384
240.5979 | 329.0984 | 138.4393 | 156.4635
241.5979 | 329.0664 | 138.8308 | 156.9838
242.5979 | 329.01 | 139.2151 | 157.5138
243.5979 | 328.9992 | 139.589 | 158.0243
244.5979 | 329.018 | 139.9862 | 158.5271
245.5979 | 328.9483 | 140.3862 | 159.0378
246.5979 | 328.9235 | 140.7728 | 159.5201
247.5979 | 328.8471 | 141.1609 | 160.0064
248.5979 | 328.8652 | 141.5599 | 160.4903
249.5979 | 328.9546 | 141.9373 | 160.9842
250.5979 | 328.9785 | 142.3421 | 161.4625
251.6135 | 328.8995 | 142.7461 | 161.9376
252.5979 | 328.9507 | 143.1285 | 162.4121
253.5979 | 328.933 | 143.523 | 162.8969
254.5979 | 328.9589 | 143.914 | 163.4124
255.5979 | 328.9455 | 144.3088 | 163.932
256.5979 | 328.9326 | 144.7004 | 164.469
257.5979 | 329.0287 | 145.0956 | 164.999
258.5979 | 329.0651 | 145.478 | 165.5335
259.5979 | 329.1017 | 145.8839 | 166.0503
260.5979 | 329.1025 | 146.2727 | 166.5611
261.5979 | 329.0742 | 146.6562 | 167.0787
262.5979 | 328.9838 | 147.0307 | 167.608
263.5979 | 328.9355 | 147.4031 | 168.1367
264.5979 | 328.9111 | 147.7589 | 168.6775
265.5979 | 328.863 | 148.1251 | 169.2254
266.6135 | 328.7764 | 148.4981 | 169.7523
267.6135 | 328.8216 | 148.8575 | 170.2825
268.5979 | 328.8022 | 149.226 | 170.8196
269.5979 | 328.8143 | 149.5918 | 171.3551
270.5979 | 328.8246 | 149.9576 | 171.8965
271.5979 | 328.8894 | 150.3289 | 172.4626
272.5979 | 328.8294 | 150.6994 | 173.0203
273.5979 | 328.7063 | 151.0531 | 173.5589
274.5979 | 328.7848 | 151.4191 | 174.0815
275.5979 | 328.8523 | 151.7804 | 174.583
276.5979 | 328.8686 | 152.1426 | 175.0743
277.6135 | 328.8146 | 152.4844 | 175.5663
278.5979 | 328.7899 | 152.8411 | 176.0698
279.5979 | 328.7301 | 153.1829 | 176.5747
280.5979 | 328.7424 | 153.5111 | 177.0808
281.6135 | 328.8637 | 153.866 | 177.5745
282.5979 | 328.8917 | 154.2055 | 178.0475
283.5979 | 329.0227 | 154.5465 | 178.5283
284.5979 | 329.0693 | 154.8677 | 178.9968
285.5979 | 329.0514 | 155.1928 | 179.4829
286.5979 | 328.9227 | 155.5224 | 179.9518
287.5979 | 328.9426 | 155.86 | 180.4381
288.5979 | 328.9785 | 156.186 | 180.9425
289.5979 | 329.0021 | 156.5108 | 181.4169
290.5979 | 329.0063 | 156.8354 | 181.8844
291.5979 | 328.9827 | 157.1583 | 182.3508
292.5979 | 329.0055 | 157.4827 | 182.8106
293.5979 | 328.9474 | 157.808 | 183.2591
294.5979 | 328.8667 | 158.1176 | 183.6832
295.5979 | 328.8705 | 158.4402 | 184.1101
296.5979 | 328.9776 | 158.7675 | 184.5435
297.6135 | 328.8699 | 159.0971 | 184.986
298.5979 | 328.8804 | 159.417 | 185.4183
299.5979 | 328.8347 | 159.7612 | 185.8485
300.5979 | 328.8805 | 160.0977 | 186.2787
301.5979 | 328.7172 | 160.4232 | 186.7237
302.6135 | 328.7364 | 160.7456 | 187.1362
303.5979 | 328.7721 | 161.0521 | 187.5601
304.6135 | 328.729 | 161.3928 | 187.9741
305.5979 | 328.6379 | 161.71 | 188.3763
306.5979 | 328.664 | 162.0214 | 188.7757
307.6135 | 328.7082 | 162.3437 | 189.1899
308.5979 | 328.6853 | 162.6484 | 189.6042
309.5979 | 328.6958 | 162.9433 | 190.0257
310.5979 | 328.6103 | 163.2386 | 190.4524
311.5979 | 328.4567 | 163.5285 | 190.8807
312.5979 | 328.3885 | 163.7964 | 191.3136
313.5979 | 328.3814 | 164.0772 | 191.7541
314.5979 | 328.4182 | 164.3529 | 192.1886
315.5979 | 328.4753 | 164.6161 | 192.614
316.5979 | 328.6198 | 164.9098 | 193.0406
317.5979 | 328.6039 | 165.1856 | 193.4665
318.6135 | 328.6493 | 165.4805 | 193.8845
319.5979 | 328.6429 | 165.7756 | 194.2969
320.5979 | 328.5845 | 166.0763 | 194.7107
321.5979 | 328.5337 | 166.3722 | 195.1235
322.5979 | 328.4866 | 166.6742 | 195.5585
323.5979 | 328.5204 | 166.9955 | 195.9756
324.5979 | 328.6067 | 167.3099 | 196.3997
325.5979 | 328.5824 | 167.6245 | 196.8143
326.5979 | 328.5233 | 167.9327 | 197.1928
327.5979 | 328.5209 | 168.2522 | 197.5854
328.5979 | 328.5407 | 168.5765 | 197.997
329.5979 | 328.6288 | 168.9105 | 198.4248
330.5979 | 328.699 | 169.253 | 198.8392
331.5979 | 328.7639 | 169.5943 | 199.2363
332.5979 | 328.9025 | 169.9294 | 199.6184
333.5979 | 328.895 | 170.252 | 200.0351
334.5979 | 328.9136 | 170.5944 | 200.467
335.5979 | 328.916 | 170.9361 | 200.9018
336.5979 | 329.0293 | 171.2656 | 201.2776
337.5979 | 329.1191 | 171.588 | 201.6656
338.5979 | 329.1232 | 171.9001 | 202.0508
339.5979 | 329.1726 | 172.229 | 202.4338
340.5979 | 329.1881 | 172.5488 | 202.8048
341.5979 | 329.2754 | 172.8762 | 203.1606
342.5979 | 329.3089 | 173.2001 | 203.5243
343.5979 | 329.3113 | 173.5283 | 203.8807
344.5979 | 329.3337 | 173.8516 | 204.2094
345.5979 | 329.2941 | 174.1878 | 204.5661
346.5979 | 329.3253 | 174.4999 | 204.9382
347.5979 | 329.3724 | 174.8032 | 205.3035
348.5979 | 329.4102 | 175.1101 | 205.658
349.5979 | 329.4191 | 175.4136 | 205.9894
350.5979 | 329.3586 | 175.6996 | 206.3144
351.5979 | 329.3253 | 176.0026 | 206.6339
352.5979 | 329.3418 | 176.3069 | 206.9575
353.5979 | 329.2862 | 176.6139 | 207.3123
354.5979 | 329.309 | 176.9225 | 207.6751
355.5979 | 329.3564 | 177.2301 | 208.0192
356.5979 | 329.3684 | 177.5448 | 208.3332
357.5979 | 329.339 | 177.8584 | 208.6119
358.5979 | 329.4018 | 178.1962 | 208.8589
359.5979 | 329.287 | 178.5076 | 209.0192
360.5979 | 329.2458 | 178.8248 | 209.1878
361.5979 | 329.2434 | 179.1586 | 209.3934
362.5979 | 329.2621 | 179.4997 | 209.6382
363.5979 | 329.2356 | 179.8418 | 209.8508
364.5979 | 329.1463 | 180.1478 | 210.1246
365.5979 | 329.102 | 180.4612 | 210.4289
366.5979 | 329.0367 | 180.7675 | 210.7222
367.5979 | 328.949 | 181.0977 | 210.9884
368.5979 | 328.9645 | 181.4063 | 211.2463
369.5979 | 328.9359 | 181.7008 | 211.4847
370.5979 | 328.932 | 181.9964 | 211.6416
371.5979 | 328.9934 | 182.2786 | 211.8125
372.5979 | 329.0644 | 182.5613 | 211.9427
373.5979 | 329.0508 | 182.8536 | 212.0447
374.5979 | 329.0124 | 183.1589 | 212.1167
375.5979 | 329.0296 | 183.4677 | 212.2011
376.5979 | 329.0133 | 183.759 | 212.3309
377.5979 | 329.0122 | 184.0551 | 212.4323
378.5979 | 328.9085 | 184.3439 | 212.5471
379.5979 | 328.8126 | 184.6242 | 212.7175
380.5979 | 328.6588 | 184.9206 | 212.916
381.5979 | 328.711 | 185.2213 | 213.0582
382.5979 | 328.7954 | 185.5195 | 213.2554
383.5979 | 328.7998 | 185.8149 | 213.4358
384.5979 | 328.8762 | 186.078 | 213.5899
385.5979 | 328.83 | 186.3757 | 213.8004
386.5979 | 328.7891 | 186.6525 | 214.059
387.5979 | 328.8484 | 186.9133 | 214.3102
388.5979 | 328.8171 | 187.1977 | 214.5735
389.5979 | 328.8269 | 187.4455 | 214.7741
390.5979 | 328.8509 | 187.713 | 214.9962
391.5979 | 328.9245 | 187.9776 | 215.2766
392.5979 | 328.9959 | 188.2524 | 215.5664
393.5979 | 328.9793 | 188.5312 | 215.877
394.5979 | 328.9356 | 188.8228 | 216.1461
395.5979 | 328.8551 | 189.1092 | 216.421
396.5979 | 328.818 | 189.4028 | 216.729
397.5979 | 328.7778 | 189.6832 | 217.0066
398.5979 | 328.9027 | 189.9644 | 217.199
399.5979 | 329.0288 | 190.2368 | 217.3532
400.5979 | 329.0882 | 190.4897 | 217.5455
401.5979 | 329.1437 | 190.729 | 217.7378
402.5979 | 329.0956 | 190.9765 | 217.9862
403.5979 | 329.2145 | 191.2195 | 218.1483
404.5979 | 329.2156 | 191.4433 | 218.1539
405.5979 | 329.1612 | 191.687 | 218.337
406.5979 | 329.056 | 191.9288 | 218.5694
407.5979 | 328.9935 | 192.1623 | 218.8466
408.5979 | 328.8794 | 192.4318 | 218.9364
409.5979 | 328.7824 | 192.6795 | 219.1245
410.5979 | 328.7229 | 192.9474 | 219.2931
411.5979 | 328.6242 | 193.2144 | 219.4899
412.5979 | 328.6316 | 193.4736 | 219.6079
413.5979 | 328.54 | 193.7298 | 219.6641
414.5979 | 328.5337 | 193.9763 | 219.751
415.5979 | 328.5159 | 194.1966 | 219.9418
416.5979 | 328.5308 | 194.4502 | 220.1172
417.5979 | 328.4387 | 194.7072 | 220.2046
418.5979 | 328.4483 | 194.9533 | 220.408
419.5979 | 328.4568 | 195.1837 | 220.747
420.5979 | 328.4328 | 195.4363 | 220.9031
421.5979 | 328.503 | 195.6845 | 221.0807
422.5979 | 328.5447 | 195.9288 | 221.3461
423.5979 | 328.4946 | 196.1855 | 221.4012
424.5979 | 328.4885 | 196.4441 | 221.5234
425.5979 | 328.5291 | 196.7129 | 221.6611
426.5979 | 328.5502 | 196.9592 | 221.6957
427.5979 | 328.567 | 197.2144 | 221.6029
428.5979 | 328.5372 | 197.4567 | 221.4235
429.5979 | 328.536 | 197.6934 | 221.156
430.5979 | 328.5208 | 197.9319 | 221.0212
431.5979 | 328.5186 | 198.1805 | 220.8846
432.5979 | 328.4849 | 198.4055 | 220.8816
433.5979 | 328.4267 | 198.6397 | 221.0382
434.5979 | 328.4301 | 198.8667 | 220.9006
435.5979 | 328.4282 | 199.1117 | 221.1766
436.5979 | 328.3902 | 199.3387 | 221.3868
437.5979 | 328.2891 | 199.578 | 221.1461
438.5979 | 328.3183 | 199.8189 | 221.3711
439.5979 | 328.3123 | 200.0505 | 221.3936
440.5979 | 328.3549 | 200.2935 | 221.1593
441.5979 | 328.4508 | 200.5153 | 220.7525
442.5979 | 328.5041 | 200.7649 | 220.3657
443.5979 | 328.5685 | 200.9821 | 220.151
444.5979 | 328.5069 | 201.2105 | 220.3821
445.5979 | 328.5083 | 201.4276 | 220.5061
446.5979 | 328.5406 | 201.6411 | 220.3399
447.5979 | 328.6952 | 201.8508 | 220.3839
448.5979 | 328.7886 | 202.0634 | 220.0942
449.5979 | 328.7983 | 202.2491 | 220.3453
450.5979 | 328.7419 | 202.4618 | 220.3586
451.5979 | 328.7558 | 202.664 | 220.5719
452.5979 | 328.7635 | 202.8546 | 220.9424
453.5979 | 328.761 | 203.0486 | 221.0107
454.5979 | 328.7363 | 203.2529 | 221.4115
455.5979 | 328.6615 | 203.4319 | 221.5642
456.5979 | 328.645 | 203.6226 | 221.6952
457.5979 | 328.6699 | 203.8133 | 222.0399
458.5979 | 328.7046 | 203.9996 | 221.5655
459.5979 | 328.608 | 204.1954 | 221.5627
460.5979 | 328.4521 | 204.3929 | 221.8231
461.5979 | 328.4384 | 204.5856 | 221.9812
462.5979 | 328.457 | 204.7852 | 222.1139
463.5979 | 328.4144 | 204.9749 | 222.3985
464.5979 | 328.4758 | 205.1757 | 222.5268
465.5979 | 328.5241 | 205.3651 | 222.2819
466.5979 | 328.586 | 205.5446 | 221.7304
467.5979 | 328.6961 | 205.7357 | 221.5418
468.5979 | 328.6041 | 205.8944 | 221.6697
469.5979 | 328.5568 | 206.0528 | 221.8557
470.5979 | 328.5889 | 206.2223 | 222.0442
471.5979 | 328.6545 | 206.3814 | 222.187
472.5979 | 328.6839 | 206.5482 | 221.7583
473.5979 | 328.635 | 206.7204 | 221.9167
474.5979 | 328.6221 | 206.8878 | 221.7156
475.5979 | 328.7589 | 207.069 | 221.7618
476.5979 | 328.8321 | 207.2411 | 222.379
477.5979 | 328.9193 | 207.4083 | 222.474
478.5979 | 328.8713 | 207.5887 | 222.3017
479.5979 | 328.7134 | 207.7771 | 222.1619
480.5979 | 328.6453 | 207.9548 | 222.6976
481.5979 | 328.6103 | 208.1314 | 222.8683
482.5979 | 328.5143 | 208.3011 | 223.0465
483.5979 | 328.5072 | 208.4777 | 223.5498
484.5979 | 328.432 | 208.6194 | 223.5144
485.5979 | 328.3503 | 208.8147 | 223.4281
486.5979 | 328.3333 | 208.9761 | 223.7951
487.5979 | 328.3097 | 209.1264 | 224.1633
488.5979 | 328.2621 | 209.3006 | 224.4758
489.5979 | 328.2209 | 209.4467 | 224.6819
490.5979 | 328.2091 | 209.6045 | 224.5026
491.5979 | 328.1805 | 209.7679 | 224.6963
492.5979 | 328.2133 | 209.9316 | 225.015
493.5979 | 328.3231 | 210.1125 | 225.1553
494.5979 | 328.3603 | 210.2858 | 225.1464
495.5979 | 328.4272 | 210.4678 | 224.5956
496.5979 | 328.4712 | 210.6579 | 224.531
497.5979 | 328.5172 | 210.8392 | 224.4032
498.5979 | 328.6081 | 211.0381 | 224.4457
499.5979 | 328.6413 | 211.2334 | 223.9818
500.5979 | 328.7089 | 211.4223 | 223.2323
501.5979 | 328.6906 | 211.6166 | 223.4373
502.5979 | 328.6718 | 211.806 | 223.0291
503.5979 | 328.7432 | 211.9816 | 222.5906
504.5979 | 328.7834 | 212.1484 | 222.8056
505.5979 | 328.869 | 212.3409 | 222.6824
506.5979 | 328.8828 | 212.512 | 222.793
507.5979 | 328.8806 | 212.684 | 222.8548
508.5979 | 328.8395 | 212.8529 | 222.4778
509.5979 | 328.873 | 213.0288 | 222.4189
510.5979 | 328.9065 | 213.2114 | 222.0542
511.5979 | 328.8965 | 213.3908 | 222.2886
512.5979 | 328.9747 | 213.5595 | 221.9693
513.5979 | 328.9144 | 213.729 | 221.5872
514.5979 | 328.8716 | 213.8884 | 221.6764
515.5979 | 328.816 | 214.0559 | 222.1137
516.5979 | 328.8046 | 214.2205 | 222.6082
517.5979 | 328.8083 | 214.3707 | 222.8904
518.5979 | 328.7976 | 214.5292 | 222.9124
519.5979 | 328.7427 | 214.6802 | 223.2103
520.5979 | 328.6325 | 214.8195 | 223.4976
521.5979 | 328.6267 | 214.9684 | 223.675
522.5979 | 328.5984 | 215.0996 | 223.7246
523.5979 | 328.5606 | 215.2502 | 223.743
524.5979 | 328.6126 | 215.3726 | 223.9445
525.5979 | 328.6444 | 215.4965 | 223.8012
526.5979 | 328.6378 | 215.614 | 223.2497
527.5979 | 328.6149 | 215.7499 | 222.5294
528.5979 | 328.5969 | 215.8658 | 222.2447
529.5979 | 328.4711 | 215.9647 | 222.0116
530.5979 | 328.3893 | 216.062 | 221.9712
531.5979 | 328.4529 | 216.1642 | 222.139
532.5979 | 328.479 | 216.2719 | 222.2915
533.5979 | 328.438 | 216.3552 | 222.5477
534.5979 | 328.4275 | 216.4472 | 222.1582
535.5979 | 328.417 | 216.5449 | 222.3135
536.5979 | 328.444 | 216.615 | 222.1009
537.5979 | 328.449 | 216.6815 | 222.1355
538.5979 | 328.3761 | 216.7592 | 221.9534
539.5979 | 328.3729 | 216.8285 | 221.8131
540.5979 | 328.3593 | 216.9216 | 222.0534
541.5979 | 328.3954 | 217.0164 | 221.6378
542.5979 | 328.4137 | 217.0913 | 221.9766
543.5979 | 328.4455 | 217.1783 | 222.4003
544.5979 | 328.3021 | 217.2693 | 222.757
545.5979 | 328.2068 | 217.3452 | 222.9207
546.5979 | 328.1687 | 217.4466 | 223.1326
547.5979 | 328.069 | 217.5314 | 222.8386
548.5979 | 328.1391 | 217.6222 | 222.8053
549.5979 | 328.1758 | 217.7077 | 222.8136
550.5979 | 328.133 | 217.7924 | 222.8022
551.5979 | 328.0829 | 217.88 | 223.2277
552.5979 | 328.0168 | 217.9766 | 223.0333
553.5979 | 327.9552 | 218.0751 | 222.6566
554.5979 | 327.9346 | 218.1683 | 223.0277
555.5979 | 327.8608 | 218.2615 | 222.8601
556.5979 | 327.8077 | 218.3693 | 223.3068
557.5979 | 327.8342 | 218.4962 | 223.4793
558.5979 | 327.8893 | 218.6051 | 223.0686
559.5979 | 327.9953 | 218.7262 | 223.0942
560.5979 | 328.0373 | 218.8764 | 223.4676
561.5979 | 328.0691 | 219.0099 | 223.4888
562.5979 | 328.0313 | 219.1587 | 223.7402
563.5979 | 328.0502 | 219.307 | 223.5258
564.5979 | 328.1005 | 219.4665 | 223.9921
565.5979 | 328.1335 | 219.609 | 223.7936
566.5979 | 328.1556 | 219.7736 | 223.7777
567.5979 | 328.1631 | 219.9177 | 223.695
568.5979 | 328.1998 | 220.0955 | 224.2513
569.5979 | 328.2495 | 220.2803 | 223.8587
570.6135 | 328.3033 | 220.4269 | 223.9711
571.5979 | 328.3022 | 220.5961 | 223.7924
572.5979 | 328.2521 | 220.7702 | 223.9724
573.5979 | 328.2473 | 220.9394 | 224.4553
574.5979 | 328.2194 | 221.102 | 224.7231
575.5979 | 328.2133 | 221.2685 | 224.8017
576.5979 | 328.1752 | 221.4592 | 225.2413
577.5979 | 328.2013 | 221.6365 | 225.1931
578.5979 | 328.1451 | 221.8102 | 225.1747
579.5979 | 328.1374 | 222.0008 | 224.6737
580.6135 | 328.1616 | 222.1788 | 224.5987
581.5979 | 328.0801 | 222.3718 | 224.4108
582.5979 | 327.9871 | 222.5522 | 224.6629
583.5979 | 327.9504 | 222.7359 | 224.3086
584.5979 | 327.98 | 222.8869 | 223.8952
585.5979 | 327.9691 | 223.0511 | 224.1802
586.5979 | 328.0215 | 223.2177 | 224.1669
587.5979 | 328.0255 | 223.369 | 223.9082
588.5979 | 328.0253 | 223.5182 | 223.7855
589.5979 | 328.0981 | 223.6561 | 223.3978
590.5979 | 328.1973 | 223.7789 | 223.0354
591.5979 | 328.2786 | 223.8844 | 223.2303
592.5979 | 328.2327 | 224.0045 | 223.1333
593.5979 | 328.1206 | 224.1206 | 223.051
594.5979 | 328.031 | 224.2321 | 222.5278
595.5979 | 327.9883 | 224.3355 | 223.2949
596.5979 | 328.0084 | 224.4614 | 222.9391
597.5979 | 327.8764 | 224.5629 | 222.9131
598.5979 | 327.8065 | 224.6576 | 222.3897
599.5979 | 327.8479 | 224.7284 | 221.7819
600.5979 | 327.9237 | 224.8261 | 222.6338
601.5979 | 327.9572 | 224.9318 | 222.8088
602.5979 | 327.9455 | 225.0243 | 222.8435
603.5979 | 327.8373 | 225.0851 | 222.231
604.5979 | 327.7029 | 225.1601 | 222.0824
605.5979 | 327.6577 | 225.2356 | 222.4517
606.5979 | 327.6717 | 225.2995 | 223.142
607.5979 | 327.6661 | 225.3902 | 223.5855
608.5979 | 327.6868 | 225.477 | 223.3822
609.5979 | 327.6902 | 225.5606 | 223.1387
610.5979 | 327.6507 | 225.6367 | 223.9331
611.5979 | 327.6752 | 225.7208 | 224.114
612.5979 | 327.7131 | 225.8003 | 224.0341
613.5979 | 327.7088 | 225.8746 | 223.8505
614.5979 | 327.6816 | 225.9661 | 224.2663
615.5979 | 327.7321 | 226.041 | 224.5067
616.5979 | 327.7156 | 226.1391 | 224.4394
617.5979 | 327.7274 | 226.2073 | 223.9972
618.5979 | 327.789 | 226.2664 | 223.642
619.5979 | 327.7665 | 226.3543 | 224.4645
620.5979 | 327.7844 | 226.4168 | 224.273
621.5979 | 327.8583 | 226.4934 | 224.5977
622.5979 | 327.8197 | 226.5957 | 224.7361
623.5979 | 327.798 | 226.6654 | 224.8014
624.5979 | 327.7752 | 226.771 | 225.4875
625.5979 | 327.7201 | 227.1227 | 226.1258
626.5979 | 327.7336 | 227.4426 | 226.4842
627.5979 | 327.686 | 227.6703 | 226.2765
628.5979 | 327.6111 | 227.7959 | 226.1435
629.5979 | 327.4676 | 227.9304 | 226.1104
630.5979 | 327.5291 | 228.0549 | 226.2128
631.5979 | 327.6131 | 228.1572 | 225.509
632.5979 | 327.6303 | 228.298 | 225.9249
633.5979 | 327.6117 | 228.615 | 227.5184
634.5979 | 327.7018 | 228.7959 | 227.2953
635.5979 | 327.6563 | 229.0952 | 227.9117
636.5979 | 327.5715 | 229.1197 | 227.3435
637.5979 | 327.5655 | 229.2644 | 227.1394
638.5979 | 327.5609 | 229.4048 | 227.3535
639.5979 | 327.4957 | 229.5429 | 227.2032
640.5979 | 327.5216 | 229.7342 | 228.0951
641.5979 | 327.4321 | 229.907 | 228.1117
642.5979 | 327.4338 | 230.0911 | 228.2143
643.5979 | 327.4802 | 230.282 | 228.3067
644.5979 | 327.5011 | 230.4512 | 228.163
645.5979 | 327.5976 | 230.6134 | 228.3547
646.5979 | 327.6612 | 230.784 | 228.6468
647.5979 | 327.6962 | 230.9656 | 228.0458
648.5979 | 327.8075 | 231.1124 | 227.5559
649.5979 | 327.7584 | 231.2704 | 227.5225
650.5979 | 327.6817 | 231.4359 | 227.733
651.5979 | 327.6429 | 231.6186 | 228.271
652.5979 | 327.6403 | 231.7932 | 227.896
653.5979 | 327.6758 | 231.9539 | 228.2792
654.5979 | 327.6712 | 232.1124 | 228.5631
655.5979 | 327.6974 | 232.2798 | 228.2483
656.5979 | 327.6862 | 232.4711 | 229.256
657.5979 | 327.6134 | 232.6341 | 229.027
658.5979 | 327.6626 | 232.8089 | 229.5005
659.5979 | 327.6659 | 233.0076 | 229.8698
660.5979 | 327.6182 | 233.1982 | 229.8735
661.5979 | 327.5665 | 233.4521 | 230.7783
662.5979 | 327.4985 | 233.638 | 229.9225
663.5979 | 327.5139 | 233.8319 | 230.5959
664.5979 | 327.5902 | 234.0192 | 230.8714
665.5979 | 327.7273 | 234.2114 | 230.9515
666.5979 | 327.7782 | 234.3732 | 231.0383
667.5979 | 327.824 | 234.5453 | 231.1119
668.5979 | 327.9183 | 234.7284 | 231.425
669.5979 | 327.9617 | 234.9379 | 231.7017
670.5979 | 327.8566 | 235.0978 | 231.1934
671.5979 | 327.7774 | 235.2706 | 231.2579
672.5979 | 327.8524 | 235.4179 | 231.4856
673.5979 | 327.8654 | 235.6015 | 231.491
674.5979 | 327.7956 | 235.7473 | 231.1995
675.5979 | 327.7934 | 235.9212 | 232.3829
676.5979 | 327.7949 | 236.0678 | 231.935
677.5979 | 327.6726 | 236.2063 | 231.6341
678.5979 | 327.5761 | 236.3904 | 232.5273
679.5979 | 327.5405 | 236.5368 | 232.7582
680.5979 | 327.525 | 236.681 | 232.6804
681.5979 | 327.5216 | 236.8436 | 232.6039
682.5979 | 327.4761 | 236.9692 | 232.5371
683.5979 | 327.464 | 237.0984 | 232.3774
684.5979 | 327.4577 | 237.2451 | 232.6945
685.5979 | 327.4813 | 237.394 | 233.0044
686.5979 | 327.53 | 237.5374 | 233.1646
687.5979 | 327.5181 | 237.6497 | 232.9104
688.5979 | 327.494 | 237.7575 | 233.0137
689.5979 | 327.5585 | 237.8838 | 232.8324
690.5979 | 327.6588 | 238.0264 | 233.0769
691.5979 | 327.7116 | 238.1476 | 232.6712
692.5979 | 327.8026 | 238.28 | 232.9828
693.5979 | 327.8551 | 238.4162 | 233.4972
694.5979 | 327.9216 | 238.5472 | 233.5976
695.5979 | 328.0246 | 238.6846 | 233.8142
696.5979 | 328.0637 | 238.8082 | 233.5445
697.5979 | 328.113 | 238.9263 | 233.5005
698.5979 | 328.148 | 239.0491 | 233.7366
699.5979 | 328.1925 | 239.1608 | 233.393
700.5979 | 328.1529 | 239.259 | 233.2819
701.5979 | 328.1219 | 239.3506 | 232.9407
702.5979 | 328.1621 | 239.4181 | 232.1559
703.5979 | 328.1907 | 239.5003 | 231.7003
704.5979 | 328.1206 | 239.5687 | 231.2463
705.5979 | 328.0616 | 239.6463 | 230.7518
706.5979 | 328.0754 | 239.7302 | 230.9346
707.5979 | 328.043 | 239.7823 | 229.9985
708.5979 | 327.9933 | 239.878 | 230.2036
709.5979 | 328.0124 | 239.9524 | 230.8583
710.5979 | 328.1154 | 240.0327 | 230.5403
711.5979 | 328.1756 | 240.0991 | 230.3963
712.5979 | 328.2043 | 240.1507 | 230.1574
713.5979 | 328.1755 | 240.2188 | 230.2868
714.5979 | 328.176 | 240.2826 | 230.2593
715.5979 | 328.1896 | 240.3181 | 230.0665
716.5979 | 328.3331 | 240.3759 | 229.892
717.5979 | 328.3199 | 240.4222 | 229.8322
718.5979 | 328.321 | 240.4665 | 229.8579
719.5979 | 328.3619 | 240.5349 | 230.0655
720.5979 | 328.3965 | 240.5911 | 230.4769
721.5979 | 328.3683 | 240.6468 | 230.8531
722.5979 | 328.4075 | 240.6877 | 230.5081
723.5979 | 328.461 | 240.7256 | 230.5344
724.5979 | 328.4011 | 240.7901 | 230.8081
725.6135 | 328.3649 | 240.8345 | 230.3542
726.5979 | 328.3288 | 240.8643 | 230.0113
727.5979 | 328.2345 | 240.9088 | 230.2295
728.5979 | 328.1553 | 240.9485 | 230.8974
729.5979 | 328.1118 | 241.0025 | 230.9032
730.5979 | 328.0918 | 241.0307 | 230.6839
731.5979 | 328.0993 | 241.0858 | 231.419
732.5979 | 328.0786 | 241.133 | 231.5375
733.5979 | 328.0545 | 241.1832 | 231.7685
734.5979 | 327.941 | 241.2083 | 231.3959
735.5979 | 327.8503 | 241.2529 | 232.0303
736.5979 | 327.8122 | 241.2876 | 231.6523
737.5979 | 327.8659 | 241.3271 | 232.2041
738.5979 | 327.8854 | 241.3365 | 231.4232
739.5979 | 327.8307 | 241.3723 | 231.6114
740.5979 | 327.7708 | 241.4061 | 231.7916
741.5979 | 327.7405 | 241.3918 | 231.8651
742.5979 | 327.7748 | 241.4609 | 232.5601
743.5979 | 327.8413 | 241.4994 | 232.906
744.5979 | 327.8275 | 241.532 | 232.7256
745.5979 | 327.83 | 241.5731 | 232.4829
746.5979 | 327.8271 | 241.5977 | 231.9625
747.5979 | 327.8845 | 241.6338 | 232.2709
748.5979 | 327.8756 | 241.6438 | 232.1543
749.5979 | 327.8103 | 241.6866 | 233.0457
750.5979 | 327.8549 | 241.7145 | 232.5192
751.5979 | 327.8593 | 241.7537 | 232.7839
752.5979 | 327.8211 | 241.7945 | 233.4244
753.5979 | 327.7671 | 241.833 | 233.5838
754.5979 | 327.7453 | 241.8894 | 233.4576
755.5979 | 327.7516 | 241.9417 | 234.2386
756.5979 | 327.7046 | 241.9964 | 234.5053
757.5979 | 327.6105 | 242.0288 | 233.9788
758.5979 | 327.634 | 242.0686 | 233.7956
759.5979 | 327.6012 | 242.0803 | 233.3216
760.5979 | 327.5875 | 242.1186 | 232.8339
761.5979 | 327.5504 | 242.1388 | 232.4403
762.5979 | 327.4889 | 242.1691 | 232.4416
763.5979 | 327.6007 | 242.2079 | 232.0541
764.5979 | 327.6349 | 242.2524 | 232.3345
765.5979 | 327.6773 | 242.2792 | 232.3509
766.5979 | 327.715 | 242.3362 | 233.3431
767.5979 | 327.7638 | 242.3698 | 232.2903
768.5979 | 327.8349 | 242.4104 | 232.3548
769.5979 | 327.8853 | 242.4199 | 231.7373
770.5979 | 327.8148 | 242.4353 | 231.394
771.5979 | 327.7006 | 242.4628 | 231.2055
772.5979 | 327.6695 | 242.4805 | 231.0578
773.5979 | 327.6982 | 242.4984 | 230.9432
774.5979 | 327.6602 | 242.5438 | 231.7363
775.5979 | 327.6251 | 242.5591 | 231.374
776.5979 | 327.6468 | 242.5867 | 231.0792
777.5979 | 327.5616 | 242.6242 | 231.3076
778.5979 | 327.5426 | 242.6534 | 231.2275
779.5979 | 327.5344 | 242.6917 | 230.94
780.5979 | 327.405 | 242.7026 | 230.4043
781.5979 | 327.3801 | 242.7462 | 229.89
782.5979 | 327.3089 | 242.7746 | 229.9602
783.5979 | 327.3183 | 242.8102 | 230.69
784.5979 | 327.2664 | 242.8571 | 231.5705
785.5979 | 327.3424 | 242.9111 | 231.1534
786.5979 | 327.4155 | 242.9479 | 231.2279
787.5979 | 327.4034 | 242.9846 | 231.2504
788.5979 | 327.2915 | 243.0239 | 231.2022
789.5979 | 327.2727 | 243.0664 | 231.9691
790.5979 | 327.2643 | 243.1143 | 232.5489
791.5979 | 327.2672 | 243.157 | 231.7089
792.5979 | 327.1618 | 243.2038 | 232.1703
793.5979 | 327.1734 | 243.2268 | 231.5396
794.5979 | 327.2126 | 243.2468 | 230.8692
795.5979 | 327.243 | 243.2829 | 231.4059
796.5979 | 327.2125 | 243.3072 | 230.7751
797.5979 | 327.2604 | 243.3427 | 230.8306
798.5979 | 327.2553 | 243.3754 | 230.7223
799.5979 | 327.2917 | 243.3906 | 230.5172
800.5979 | 327.3615 | 243.4091 | 230.6335
801.5979 | 327.3101 | 243.4436 | 231.2179
802.5979 | 327.3161 | 243.4684 | 230.9442
803.5979 | 327.2778 | 243.4774 | 231.2963
804.5979 | 327.2427 | 243.5035 | 231.5934
805.5979 | 327.2146 | 243.5255 | 231.5474
806.5979 | 327.2577 | 243.5616 | 232.1218
807.5979 | 327.2353 | 243.6037 | 231.9256
808.5979 | 327.2831 | 243.6355 | 232.8635
809.5979 | 327.3019 | 243.691 | 233.3941
810.5979 | 327.3302 | 243.7137 | 233.1051