## Test Conditions
DESIREE-FIRE Test Number 31 - Circuit Simulator Data Only
Test Date: | 2009-07-17
DCSim DAQ Start Time | 8:36
DCSim Time for Synchronization | 8:35
Heat Source Synchronization | 0:02 | hour:minutes:seconds
Heat Source DAQ Start Time | 8:34
Fire Time | 8:39
Offset | 0:03 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 165 | seconds
Heat Source Offset | 0:05 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 306 | seconds
Heat Source Stop Time | 8:48
Test Duration | 0:10 | hour:minutes:seconds
| 579 | seconds
CT500 turns | 1 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 1 | 1 or 5
Pre-Test Baseline: | Not Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SOV 1 | PVC/PVC, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
SOV 2 | PVC/PVC, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SOV-1_CT500 | SOV-1_CT35_1_P | SOV-1_CT35_2_S1 | SOV-1_CT35_3_G | SOV-1_CT35_4_S2 | SOV-1_CT35_5_N | SOV-2_CT500 | SOV-2_CT35_1_P | SOV-2_CT35_2_S1 | SOV-2_CT35_3_G | SOV-2_CT35_4_S2 | SOV-2_CT35_5_N | SOV-1_VT7_1_R | SOV-1_VT7_2_SP | SOV-1_VT7_3_S | SOV-1_VTU_1_P | SOV-1_VTU_2_S1 | SOV-1_VTU_3_G | SOV-1_VTU_4_N | SOV-2_VT7_1_R | SOV-2_VT7_2_SP | SOV-2_VT7_3_S | SOV-2_VTU_1_P | SOV-2_VTU_2_S1 | SOV-2_VTU_3_G | SOV-2_VTU_4_N | {SOV1} V(N) - V(Batt -) | {SOV1} V(P) - V(Batt +) | {SOV1} V(R) - V(Batt -) | {SOV1} V(S) - V(Batt -) | {SOV1} V(S) - V(N) | {SOV1} V(S1) - V(Batt +) | {SOV1} V(G) - V(Batt +) | {SOV2} V(N) - V(Batt -) | {SOV2} V(P) - V(Batt +) | {SOV2} V(R) - V(Batt -) | {SOV2} V(S) - V(Batt -) | {SOV2} V(S) - V(N) | {SOV2} V(S1) - V(Batt +) | {SOV2} V(G) - V(Batt +) | {SOV1} V(P) - V(Batt -) | {SOV1} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV1} V(SP) - V(Batt -) | {SOV1} V(N) - V(Batt +) | {SOV2} V(P) - V(Batt -) | {SOV2} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV2} V(SP) - V(Batt -) | {SOV2} V(N) - V(Batt +)
-0.09375 | 124.53 | -67.4927 | 56.9046 | 0.033921 | -0.00090066 | 0.00075378 | 0.057764 | 0.00070158 | 0.060288 | 0.064579 | -0.00058685 | 0.0011413 | 0.067408 | -0.0068083 | 0.067251 | -65.0945 | 0.010564 | -67.3549 | 56.76 | 56.4219 | 56.5183 | -67.3504 | -67.4388 | 0.009516 | -67.5603 | 56.693 | 56.7609 | 56.494 | -67.4865 | 0.14232 | -0.14456 | 2.3982 | 0.13776 | -0.004563 | -0.48273 | -0.3863 | 0.006178 | -0.21158 | 0.053906 | -0.067594 | -0.073772 | -0.1437 | -0.41063 | 124.2527 | 123.9145 | 124.011 | 67.5032 | -124.255 | 124.1857 | 124.2536 | 123.9866 | 67.5022 | -124.3911
0.90625 | 124.5026 | -67.4881 | 56.8863 | 0.049183 | -0.0030377 | -0.0013822 | 0.058832 | 0.0017696 | 0.059219 | 0.07984 | 0.0015501 | 0.0032783 | 0.067408 | -0.0078763 | 0.067251 | -65.1494 | 0.010564 | -67.3549 | 56.7463 | 56.4173 | 56.5275 | -67.3916 | -67.4342 | 0.004938 | -67.5511 | 56.7022 | 56.7655 | 56.581 | -67.5002 | 0.096534 | -0.13999 | 2.3387 | 0.13318 | 0.036648 | -0.469 | -0.35884 | -0.012136 | -0.18411 | 0.053907 | -0.063015 | -0.050879 | -0.12081 | -0.30533 | 124.2344 | 123.9054 | 124.0156 | 67.4987 | -124.2779 | 124.1903 | 124.2536 | 124.0691 | 67.493 | -124.3865
1.9062 | 124.5071 | -67.4881 | 56.9 | 0.064445 | 0.0012363 | -0.0013822 | 0.056695 | 0.00070158 | 0.059219 | 0.07984 | 0.0015501 | 0.0011413 | 0.06634 | -0.0057403 | 0.067251 | -65.1403 | 0.015142 | -67.3595 | 56.7555 | 56.4264 | 56.5275 | -67.4007 | -67.4433 | 0.009516 | -67.5465 | 56.7068 | 56.7746 | 56.4344 | -67.4865 | 0.087376 | -0.14456 | 2.3478 | 0.1286 | 0.041228 | -0.47358 | -0.37257 | 0.0016 | -0.19327 | 0.044749 | -0.058436 | -0.060036 | -0.12538 | -0.46558 | 124.2436 | 123.9145 | 124.0156 | 67.5032 | -124.3007 | 124.1949 | 124.2627 | 123.9225 | 67.4976 | -124.3865
2.9062 | 124.5255 | -67.4927 | 56.8954 | 0.079707 | 0.0012363 | -0.00031422 | 0.057764 | -0.00036642 | 0.058151 | 0.049318 | -0.00058685 | 7.3343e-05 | 0.065272 | -0.0089453 | 0.066182 | -65.1403 | 0.015142 | -67.3595 | 56.7509 | 56.4264 | 56.5366 | -67.3641 | -67.4388 | 0.014095 | -67.5511 | 56.7022 | 56.7609 | 56.4802 | -67.4957 | 0.12859 | -0.14456 | 2.3524 | 0.13318 | 0.004596 | -0.469 | -0.35883 | -0.00298 | -0.19327 | 0.053906 | -0.058437 | -0.055457 | -0.13454 | -0.41521 | 124.2436 | 123.9191 | 124.0293 | 67.5078 | -124.2595 | 124.1949 | 124.2536 | 123.9729 | 67.5068 | -124.3911
3.9062 | 124.5026 | -67.4881 | 56.8771 | 0.064445 | 0.00016734 | -0.00031422 | 0.056695 | -0.00036642 | 0.057083 | 0.064579 | 0.0015501 | 0.0011413 | 0.06634 | -0.0078763 | 0.067251 | -65.1403 | 0.015142 | -67.3641 | 56.7509 | 56.431 | 56.5366 | -67.3549 | -67.4433 | 0.009516 | -67.5557 | 56.6976 | 56.7701 | 56.4619 | -67.4911 | 0.13317 | -0.12625 | 2.3478 | 0.12402 | -0.009141 | -0.44611 | -0.34052 | -0.002979 | -0.17954 | 0.044749 | -0.067594 | -0.064615 | -0.10707 | -0.41522 | 124.239 | 123.9191 | 124.0247 | 67.5032 | -124.2321 | 124.1857 | 124.2582 | 123.95 | 67.4976 | -124.3682
4.9062 | 124.4705 | -67.4652 | 56.8909 | 0.064445 | 0.00016734 | 0.00075378 | 0.055627 | 0.0017696 | 0.057083 | 0.07984 | 0.00048215 | 0.0011413 | 0.065272 | -0.0068083 | 0.066182 | -65.154 | 0.019721 | -67.3549 | 56.7509 | 56.4219 | 56.5137 | -67.3687 | -67.4388 | 0.014095 | -67.5465 | 56.6976 | 56.7609 | 56.4665 | -67.4865 | 0.096541 | -0.13999 | 2.3112 | 0.11029 | 0.013753 | -0.469 | -0.37715 | -0.021288 | -0.19327 | 0.02644 | -0.081324 | -0.060036 | -0.12996 | -0.42437 | 124.2161 | 123.8871 | 123.9789 | 67.4849 | -124.2595 | 124.1628 | 124.2261 | 123.9317 | 67.4793 | -124.3774
5.9062 | 124.4934 | -67.4835 | 56.8817 | 0.064445 | -0.00090066 | -0.0013822 | 0.055627 | 0.00070158 | 0.057083 | 0.07984 | -0.00058685 | 0.0022103 | 0.065272 | -0.0046713 | 0.066182 | -65.154 | 0.005985 | -67.3549 | 56.7555 | 56.4264 | 56.5229 | -67.3595 | -67.4342 | 0.014095 | -67.5511 | 56.7022 | 56.7655 | 56.494 | -67.4957 | 0.12401 | -0.12625 | 2.3295 | 0.1286 | 0.004595 | -0.45527 | -0.35884 | -0.012135 | -0.17953 | 0.04933 | -0.067592 | -0.055457 | -0.11623 | -0.38774 | 124.239 | 123.91 | 124.0064 | 67.4895 | -124.2412 | 124.1857 | 124.249 | 123.9775 | 67.4976 | -124.3774
6.9062 | 124.4888 | -67.4927 | 56.9046 | 0.079707 | -0.00090066 | -0.0024512 | 0.058832 | 0.00070158 | 0.058151 | 0.07984 | -0.00058685 | 0.0011413 | 0.065272 | -0.0068083 | 0.067251 | -65.154 | 0.005985 | -67.3458 | 56.7509 | 56.4264 | 56.5275 | -67.3504 | -67.4388 | 0.014095 | -67.5603 | 56.7022 | 56.7655 | 56.4894 | -67.4911 | 0.14232 | -0.15372 | 2.3387 | 0.14692 | 0.004593 | -0.47816 | -0.37715 | 0.001599 | -0.20242 | 0.053906 | -0.067594 | -0.069193 | -0.13912 | -0.41521 | 124.2436 | 123.9191 | 124.0201 | 67.4987 | -124.255 | 124.1949 | 124.2582 | 123.9821 | 67.5068 | -124.3957
7.9062 | 124.5071 | -67.4698 | 56.9046 | 0.079707 | -0.00090066 | -0.0013822 | 0.057764 | 0.00070158 | 0.058151 | 0.064579 | 0.00048215 | 7.3343e-05 | 0.065272 | -0.0057403 | 0.067251 | -65.1586 | 0.010564 | -67.3595 | 56.7555 | 56.4264 | 56.5275 | -67.3687 | -67.4388 | 0.009516 | -67.5557 | 56.6976 | 56.7655 | 56.4848 | -67.4957 | 0.10112 | -0.14914 | 2.3112 | 0.11029 | 0.009175 | -0.47816 | -0.37715 | -0.025868 | -0.207 | 0.031018 | -0.085904 | -0.060036 | -0.13912 | -0.41979 | 124.2252 | 123.8962 | 123.9972 | 67.4804 | -124.2733 | 124.1674 | 124.2353 | 123.9546 | 67.4793 | -124.4003
8.9219 | 124.498 | -67.5293 | 56.8451 | 0.079707 | -0.00090066 | -0.0013822 | 0.058832 | 0.0017696 | 0.057083 | 0.07984 | -0.00058685 | 0.0022103 | 0.06634 | -0.0068083 | 0.067251 | -65.154 | 0.005985 | -67.3595 | 56.7417 | 56.4219 | 56.5275 | -67.3366 | -67.4388 | 0.014095 | -67.5511 | 56.6976 | 56.7655 | 56.4802 | -67.5002 | 0.19268 | -0.10337 | 2.3753 | 0.1698 | -0.022877 | -0.42323 | -0.31764 | 0.029063 | -0.14749 | 0.090527 | -0.021816 | -0.050879 | -0.079608 | -0.36486 | 124.271 | 123.9512 | 124.0568 | 67.5353 | -124.1817 | 124.2269 | 124.2948 | 124.0095 | 67.5434 | -124.3453
9.9688 | 124.5438 | -67.4652 | 56.8405 | 0.049183 | -0.00090066 | -0.0013822 | 0.057764 | -0.00036642 | 0.057083 | 0.049318 | 0.0015501 | 7.3343e-05 | 0.06634 | -0.0068083 | 0.067251 | -65.2364 | 0.015142 | -67.3595 | 56.7417 | 56.4219 | 56.5137 | -67.3366 | -67.4479 | 0.014095 | -67.5557 | 56.7022 | 56.7655 | 56.4482 | -67.4957 | 0.12859 | -0.098789 | 2.2288 | 0.10572 | -0.022877 | -0.41865 | -0.3268 | -0.030446 | -0.13834 | 0.017283 | -0.090482 | -0.060036 | -0.07503 | -0.39233 | 124.2069 | 123.8871 | 123.9789 | 67.4804 | -124.1771 | 124.1674 | 124.2307 | 123.9134 | 67.4793 | -124.3362
10.9062 | 124.4934 | -67.4744 | 56.8954 | 0.064445 | 0.0023043 | 0.00075378 | 0.056695 | 0.0017696 | 0.056015 | 0.049318 | 0.00048215 | -0.00099466 | 0.065272 | -0.0046713 | 0.067251 | -65.154 | 0.005985 | -67.3595 | 56.76 | 56.4264 | 56.5275 | -67.3641 | -67.4342 | 0.014095 | -67.5603 | 56.693 | 56.7655 | 56.4848 | -67.4911 | 0.11028 | -0.13541 | 2.3204 | 0.11487 | 0.004596 | -0.469 | -0.36799 | -0.016712 | -0.20242 | 0.040174 | -0.085905 | -0.069193 | -0.12996 | -0.41063 | 124.2344 | 123.9008 | 124.0018 | 67.4804 | -124.2595 | 124.1674 | 124.2399 | 123.9592 | 67.4885 | -124.3865
11.9062 | 124.5666 | -67.4744 | 56.8817 | 0.049183 | -0.00090066 | -0.00031422 | 0.055627 | 0.0017696 | 0.057083 | 0.095101 | 0.00048215 | 7.3343e-05 | 0.06634 | -0.0046713 | 0.067251 | -65.1631 | 0.015142 | -67.3549 | 56.7509 | 56.4219 | 56.5229 | -67.3091 | -67.4342 | 0.009516 | -67.5511 | 56.6976 | 56.7655 | 56.4848 | -67.4911 | 0.16522 | -0.13083 | 2.3112 | 0.11945 | -0.045773 | -0.45985 | -0.35884 | -0.016712 | -0.18411 | 0.040174 | -0.076748 | -0.060036 | -0.11623 | -0.3969 | 124.2252 | 123.8962 | 123.9972 | 67.4895 | -124.1909 | 124.172 | 124.2399 | 123.9592 | 67.4839 | -124.3728
12.9062 | 124.5987 | -67.4698 | 56.8726 | 0.033921 | -0.00090066 | 0.00075378 | 0.057764 | 0.00070158 | 0.059219 | 0.064579 | 0.0015501 | 0.0022103 | 0.06634 | -0.0046713 | 0.066182 | -65.1769 | 0.015142 | -67.3595 | 56.7463 | 56.4173 | 56.5229 | -67.332 | -67.4388 | 0.004938 | -67.5557 | 56.6976 | 56.7609 | 56.4573 | -67.4911 | 0.13775 | -0.12625 | 2.2929 | 0.11029 | -0.027456 | -0.45527 | -0.34968 | -0.021289 | -0.17496 | 0.031018 | -0.085904 | -0.064615 | -0.11165 | -0.41522 | 124.2161 | 123.8871 | 123.9927 | 67.4849 | -124.2046 | 124.1674 | 124.2307 | 123.9271 | 67.4747 | -124.3636
13.9219 | 124.5346 | -67.4744 | 56.8634 | 0.049183 | 0.00016734 | -0.0013822 | 0.057764 | 0.00070158 | 0.057083 | 0.064579 | -0.00058685 | 7.3343e-05 | 0.064204 | -0.0046713 | 0.065114 | -65.1357 | 0.015142 | -67.3503 | 56.7509 | 56.4264 | 56.5275 | -67.3595 | -67.4342 | 0.009516 | -67.5511 | 56.7068 | 56.7563 | 56.494 | -67.4911 | 0.11485 | -0.11252 | 2.3387 | 0.12403 | 0.009173 | -0.43696 | -0.33595 | -0.016712 | -0.15664 | 0.040174 | -0.076748 | -0.060036 | -0.10707 | -0.36943 | 124.2252 | 123.9008 | 124.0018 | 67.4895 | -124.2229 | 124.1811 | 124.2307 | 123.9683 | 67.4839 | -124.3545
14.9062 | 124.5117 | -67.4835 | 56.8726 | 0.079707 | 0.00016734 | -0.00031422 | 0.056695 | 0.0017696 | 0.057083 | 0.07984 | 0.00048215 | 0.0022103 | 0.06634 | -0.0046713 | 0.066182 | -65.1631 | 0.010564 | -67.3503 | 56.7555 | 56.4264 | 56.5275 | -67.3229 | -67.4342 | 0.014095 | -67.5557 | 56.7068 | 56.7609 | 56.4757 | -67.4957 | 0.16064 | -0.1171 | 2.3204 | 0.13318 | -0.027458 | -0.44611 | -0.3451 | -0.012135 | -0.1658 | 0.04933 | -0.072171 | -0.060036 | -0.11165 | -0.3969 | 124.239 | 123.91 | 124.011 | 67.4941 | -124.1954 | 124.1903 | 124.2444 | 123.9592 | 67.4976 | -124.3682
15.9062 | 124.5804 | -67.4469 | 56.8314 | 0.049183 | 0.0012363 | -0.00031422 | 0.057764 | 0.00070158 | 0.058151 | 0.064579 | 0.00048215 | -0.00099466 | 0.065272 | -0.0046713 | 0.066182 | -65.1677 | 0.005985 | -67.3503 | 56.7463 | 56.4264 | 56.5275 | -67.3412 | -67.4342 | 0.009516 | -67.5557 | 56.6976 | 56.7609 | 56.4528 | -67.4957 | 0.1057 | -0.085055 | 2.2792 | 0.096561 | -0.009142 | -0.40491 | -0.3039 | -0.048757 | -0.13376 | 0.012708 | -0.10879 | -0.060036 | -0.070454 | -0.3786 | 124.1932 | 123.8733 | 123.9744 | 67.4529 | -124.1726 | 124.1445 | 124.2078 | 123.8997 | 67.4564 | -124.327
16.9062 | 124.4888 | -67.4744 | 56.8863 | 0.064445 | -0.00090066 | -0.0013822 | 0.056695 | -0.00036642 | 0.056015 | 0.064579 | 0.00048215 | 0.0011413 | 0.065272 | -0.0036033 | 0.066182 | -65.1631 | 0.015142 | -67.3549 | 56.7555 | 56.4219 | 56.5275 | -67.3412 | -67.4388 | 0.009516 | -67.5557 | 56.7022 | 56.7609 | 56.4528 | -67.5002 | 0.13317 | -0.13083 | 2.3112 | 0.11945 | -0.01372 | -0.46442 | -0.35884 | -0.025869 | -0.18411 | 0.035595 | -0.081327 | -0.055458 | -0.12539 | -0.43353 | 124.2298 | 123.8962 | 124.0018 | 67.4895 | -124.2275 | 124.1765 | 124.2353 | 123.9271 | 67.4839 | -124.3865
17.9062 | 124.5163 | -67.4698 | 56.8726 | 0.049183 | -0.0019697 | 0.00075378 | 0.056695 | 0.00070158 | 0.057083 | 0.07984 | 0.00048215 | 7.3343e-05 | 0.065272 | -0.0036033 | 0.067251 | -65.1586 | 0.010564 | -67.3458 | 56.7463 | 56.4219 | 56.5137 | -67.3458 | -67.4342 | 0.009516 | -67.5465 | 56.7068 | 56.7609 | 56.5123 | -67.4911 | 0.12401 | -0.12625 | 2.3112 | 0.12403 | 1.4e-05 | -0.45069 | -0.35884 | -0.021289 | -0.1658 | 0.035597 | -0.076746 | -0.055457 | -0.11165 | -0.36028 | 124.2161 | 123.8917 | 123.9835 | 67.4804 | -124.2183 | 124.1765 | 124.2307 | 123.9821 | 67.4793 | -124.3636
18.9219 | 124.498 | -67.4789 | 56.8634 | 0.033921 | -0.00090066 | 0.00075378 | 0.055627 | 0.0017696 | 0.059219 | 0.095101 | 0.00048215 | 7.3343e-05 | 0.06634 | -0.0036033 | 0.068319 | -65.1448 | 0.010564 | -67.3549 | 56.7555 | 56.4173 | 56.5229 | -67.3732 | -67.4388 | 0.014095 | -67.5557 | 56.7022 | 56.7609 | 56.5306 | -67.4911 | 0.10569 | -0.10794 | 2.3341 | 0.12403 | 0.018332 | -0.44611 | -0.34053 | -0.012134 | -0.16122 | 0.040173 | -0.076749 | -0.064615 | -0.1025 | -0.3328 | 124.2344 | 123.8962 | 124.0018 | 67.4895 | -124.2367 | 124.1811 | 124.2398 | 124.0095 | 67.493 | -124.3545
19.9062 | 124.5987 | -67.4377 | 56.868 | 0.049183 | 0.00016734 | 0.0018228 | 0.058832 | -0.00036642 | 0.059219 | 0.095101 | -0.00058685 | 0.0011413 | 0.068477 | -0.0025343 | 0.066182 | -65.1952 | 0.005985 | -67.3503 | 56.7463 | 56.4219 | 56.5137 | -67.3366 | -67.4388 | 0.009516 | -67.5511 | 56.7022 | 56.7609 | 56.4482 | -67.4911 | 0.10113 | -0.12168 | 2.2425 | 0.087406 | -0.013721 | -0.44611 | -0.35426 | -0.053333 | -0.1658 | -0.001026 | -0.11337 | -0.060036 | -0.10708 | -0.4198 | 124.184 | 123.8596 | 123.9515 | 67.4437 | -124.2046 | 124.1399 | 124.1986 | 123.8859 | 67.4473 | -124.3591
20.9062 | 124.5758 | -67.4377 | 56.8954 | 0.049183 | 0.00016734 | -0.00031422 | 0.056695 | -0.00036642 | 0.058151 | 0.064579 | 0.00048215 | 0.0022103 | 0.065272 | -0.0025343 | 0.066182 | -65.186 | 0.015142 | -67.3503 | 56.7463 | 56.4264 | 56.5229 | -67.3412 | -67.4342 | 0.014095 | -67.5511 | 56.7022 | 56.7609 | 56.4573 | -67.4911 | 0.096548 | -0.14914 | 2.2517 | 0.087406 | -0.009142 | -0.469 | -0.37257 | -0.053333 | -0.19327 | 0.003553 | -0.11337 | -0.060036 | -0.13454 | -0.43811 | 124.184 | 123.8642 | 123.9606 | 67.4529 | -124.2366 | 124.1399 | 124.1986 | 123.8951 | 67.4518 | -124.3865
21.9062 | 124.585 | -67.4377 | 56.8634 | 0.079707 | -0.00090066 | -0.0013822 | 0.057764 | -0.00036642 | 0.057083 | 0.049318 | 0.00048215 | 0.0022103 | 0.067408 | -0.0046713 | 0.066182 | -65.186 | 0.010564 | -67.3595 | 56.7555 | 56.4264 | 56.532 | -67.3412 | -67.4388 | 0.009516 | -67.5511 | 56.6976 | 56.7609 | 56.4711 | -67.5002 | 0.096548 | -0.10794 | 2.2517 | 0.07825 | -0.018298 | -0.43696 | -0.33137 | -0.06249 | -0.1658 | -0.001026 | -0.11337 | -0.050879 | -0.1025 | -0.39233 | 124.1932 | 123.8642 | 123.9698 | 67.4483 | -124.2046 | 124.1353 | 124.1986 | 123.9088 | 67.4473 | -124.3636
22.9062 | 124.6262 | -67.4149 | 56.8817 | 0.064445 | 0.00016734 | -0.00031422 | 0.057764 | 0.0017696 | 0.058151 | 0.07984 | 0.0015501 | 0.0011413 | 0.06634 | -0.0046713 | 0.067251 | -65.1769 | 0.005985 | -67.3503 | 56.7463 | 56.4264 | 56.5275 | -67.3458 | -67.4388 | 0.009516 | -67.5465 | 56.7022 | 56.7655 | 56.4665 | -67.5002 | 0.069082 | -0.13541 | 2.238 | 0.064518 | -0.004564 | -0.45527 | -0.35426 | -0.085378 | -0.17953 | -0.023914 | -0.13168 | -0.0463 | -0.11623 | -0.41522 | 124.1612 | 123.8413 | 123.9423 | 67.4208 | -124.2275 | 124.117 | 124.1803 | 123.8814 | 67.4244 | -124.3819
23.9219 | 124.5575 | -67.4789 | 56.8771 | 0.064445 | 0.0012363 | -0.00031422 | 0.056695 | -0.00036642 | 0.057083 | 0.07984 | -0.00058685 | 0.0011413 | 0.065272 | -0.0025343 | 0.066182 | -65.1219 | 0.015142 | -67.3595 | 56.7463 | 56.4173 | 56.5275 | -67.3366 | -67.4342 | 0.009516 | -67.5511 | 56.693 | 56.7655 | 56.4619 | -67.5002 | 0.14233 | -0.13083 | 2.357 | 0.11945 | -0.022877 | -0.45985 | -0.34968 | -0.021291 | -0.18411 | 0.044752 | -0.07217 | -0.050879 | -0.11165 | -0.41522 | 124.2252 | 123.8962 | 124.0064 | 67.4941 | -124.2138 | 124.172 | 124.2444 | 123.9409 | 67.4885 | -124.3774
24.9062 | 124.6078 | -67.424 | 56.868 | 0.064445 | 0.00016734 | -0.0013822 | 0.056695 | 0.00070158 | 0.057083 | 0.049318 | 0.00048215 | 0.0011413 | 0.06634 | -0.0025343 | 0.067251 | -65.1677 | 0.015142 | -67.3549 | 56.7509 | 56.4219 | 56.5275 | -67.3366 | -67.4342 | 0.009516 | -67.5511 | 56.6976 | 56.7655 | 56.4711 | -67.4911 | 0.087394 | -0.1171 | 2.2563 | 0.069095 | -0.018299 | -0.44611 | -0.34052 | -0.067066 | -0.17038 | -0.01018 | -0.1271 | -0.060036 | -0.1025 | -0.3969 | 124.1749 | 123.8459 | 123.9515 | 67.4392 | -124.2046 | 124.1216 | 124.1895 | 123.8951 | 67.4335 | -124.3591
25.9062 | 124.6033 | -67.4469 | 56.8405 | 0.064445 | -0.0019697 | -0.00031422 | 0.055627 | 0.00070158 | 0.058151 | 0.064579 | -0.00058685 | 7.3343e-05 | 0.067408 | -0.0014663 | 0.066182 | -65.1952 | 0.015142 | -67.3458 | 56.7509 | 56.4219 | 56.532 | -67.3595 | -67.4296 | 0.009516 | -67.5465 | 56.693 | 56.7609 | 56.4573 | -67.4911 | 0.087388 | -0.089632 | 2.2517 | 0.10114 | 0.013751 | -0.41865 | -0.30848 | -0.044178 | -0.14749 | 0.017287 | -0.099635 | -0.055457 | -0.079609 | -0.38317 | 124.1978 | 123.8688 | 123.9789 | 67.462 | -124.2 | 124.1399 | 124.2078 | 123.9042 | 67.4564 | -124.3316
26.9062 | 124.6353 | -67.4332 | 56.8634 | 0.079707 | 0.00016734 | -0.0013822 | 0.058832 | 0.0028386 | 0.057083 | 0.049318 | 0.00048215 | 7.3343e-05 | 0.06634 | -0.0036033 | 0.066182 | -65.1952 | 0.015142 | -67.3549 | 56.7555 | 56.4219 | 56.532 | -67.3687 | -67.4342 | 0.004938 | -67.542 | 56.6976 | 56.7655 | 56.4894 | -67.4957 | 0.064498 | -0.10794 | 2.238 | 0.078251 | 0.013753 | -0.44154 | -0.33137 | -0.062489 | -0.1658 | -0.001024 | -0.10879 | -0.0463 | -0.097918 | -0.37401 | 124.1886 | 123.855 | 123.9652 | 67.4483 | -124.2321 | 124.1308 | 124.1987 | 123.9226 | 67.4381 | -124.3591
27.9062 | 124.5758 | -67.4377 | 56.8497 | 0.079707 | -0.0019697 | -0.0013822 | 0.057764 | 0.00070158 | 0.057083 | 0.07984 | 0.0015501 | 0.0022103 | 0.06634 | -0.0025343 | 0.066182 | -65.1815 | 0.015142 | -67.3549 | 56.7463 | 56.4219 | 56.5229 | -67.3595 | -67.4296 | 0.004938 | -67.5465 | 56.693 | 56.7655 | 56.4573 | -67.4957 | 0.078233 | -0.10337 | 2.2563 | 0.082828 | 0.004595 | -0.4278 | -0.32679 | -0.057912 | -0.15665 | 0.008132 | -0.10879 | -0.050878 | -0.084185 | -0.39233 | 124.184 | 123.8596 | 123.9606 | 67.4529 | -124.2092 | 124.1308 | 124.2032 | 123.8951 | 67.4427 | -124.3453
28.9219 | 124.4751 | -67.4927 | 56.868 | 0.033921 | 0.00016734 | -0.0013822 | 0.056695 | 0.0017696 | 0.058151 | 0.064579 | 0.00048215 | 7.3343e-05 | 0.06634 | -0.0025343 | 0.066182 | -65.154 | 0.010564 | -67.3458 | 56.7509 | 56.4127 | 56.532 | -67.3549 | -67.4342 | 0.009516 | -67.5465 | 56.7068 | 56.7701 | 56.4848 | -67.4957 | 0.13774 | -0.1171 | 2.3387 | 0.14692 | 0.009172 | -0.45527 | -0.33595 | -0.00298 | -0.16122 | 0.058485 | -0.053858 | -0.050878 | -0.097918 | -0.38317 | 124.2436 | 123.9054 | 124.0247 | 67.5032 | -124.2229 | 124.1994 | 124.2627 | 123.9775 | 67.5022 | -124.3636
29.9062 | 124.6033 | -67.4103 | 56.8451 | 0.049183 | -0.00090066 | -0.0013822 | 0.057764 | 0.00070158 | 0.056015 | 0.095101 | 0.0015501 | 7.3343e-05 | 0.064204 | -0.0025343 | 0.066182 | -65.2044 | 0.010564 | -67.3458 | 56.7463 | 56.4219 | 56.5275 | -67.3412 | -67.4342 | 0.009516 | -67.5465 | 56.6976 | 56.7563 | 56.4482 | -67.4911 | 0.069082 | -0.098788 | 2.2059 | 0.064518 | -0.004564 | -0.42323 | -0.31764 | -0.080799 | -0.14749 | -0.023913 | -0.13626 | -0.055457 | -0.088765 | -0.39691 | 124.1566 | 123.8321 | 123.9377 | 67.4208 | -124.1863 | 124.1079 | 124.1666 | 123.8585 | 67.4198 | -124.3362
30.9062 | 124.617 | -67.4286 | 56.8771 | 0.049183 | 0.00016734 | -0.0013822 | 0.054559 | 0.00070158 | 0.059219 | 0.064579 | -0.00058685 | 7.3343e-05 | 0.065272 | -0.00039829 | 0.065114 | -65.1815 | 0.015142 | -67.3503 | 56.7509 | 56.4127 | 56.5229 | -67.3458 | -67.4342 | 0.009516 | -67.5465 | 56.6976 | 56.7609 | 56.4848 | -67.4911 | 0.082815 | -0.12625 | 2.2471 | 0.078251 | -0.004564 | -0.46443 | -0.35426 | -0.062488 | -0.17954 | -0.005602 | -0.11794 | -0.055457 | -0.11623 | -0.39232 | 124.1795 | 123.8413 | 123.9515 | 67.4437 | -124.2229 | 124.1262 | 124.1895 | 123.9134 | 67.4381 | -124.3682
31.9062 | 124.5895 | -67.4149 | 56.8588 | 0.064445 | -0.00090066 | 0.00075378 | 0.056695 | -0.00036642 | 0.057083 | 0.064579 | 0.0015501 | 0.0011413 | 0.065272 | -0.0036033 | 0.067251 | -65.1815 | 0.005985 | -67.3595 | 56.7509 | 56.4264 | 56.5229 | -67.3458 | -67.4296 | 0.009516 | -67.542 | 56.693 | 56.7655 | 56.4711 | -67.4911 | 0.069082 | -0.10794 | 2.2334 | 0.055362 | -0.01372 | -0.43238 | -0.33595 | -0.076221 | -0.1658 | -0.014756 | -0.1271 | -0.050879 | -0.093341 | -0.38775 | 124.1657 | 123.8413 | 123.9377 | 67.4208 | -124.2046 | 124.1079 | 124.1803 | 123.8859 | 67.4244 | -124.3499
32.9062 | 124.6307 | -67.4332 | 56.8497 | 0.064445 | -0.0019697 | -0.00031422 | 0.057764 | 0.0028386 | 0.058151 | 0.07984 | 0.0015501 | 7.3343e-05 | 0.06634 | -0.0025343 | 0.066182 | -65.2135 | 0.015142 | -67.3503 | 56.7555 | 56.4264 | 56.5229 | -67.3595 | -67.425 | 0.004938 | -67.5465 | 56.7022 | 56.7655 | 56.4802 | -67.4911 | 0.073656 | -0.094209 | 2.2197 | 0.082829 | 0.009173 | -0.42322 | -0.32679 | -0.05791 | -0.14749 | 0.008133 | -0.11337 | -0.055457 | -0.084185 | -0.36944 | 124.1886 | 123.8596 | 123.956 | 67.4483 | -124.2092 | 124.1353 | 124.1987 | 123.9134 | 67.4381 | -124.3407
33.9219 | 124.4705 | -67.4835 | 56.8817 | 0.049183 | -0.00090066 | 0.00075378 | 0.057764 | -0.00036642 | 0.053878 | 0.07984 | -0.00058685 | 0.0011413 | 0.06634 | -0.0025343 | 0.066182 | -65.1357 | 0.010564 | -67.3503 | 56.7555 | 56.4264 | 56.532 | -67.3366 | -67.4296 | 0.014095 | -67.542 | 56.6976 | 56.7609 | 56.4573 | -67.4957 | 0.1469 | -0.12625 | 2.3478 | 0.13318 | -0.013721 | -0.45527 | -0.34968 | -0.012135 | -0.18411 | 0.053909 | -0.058435 | -0.0463 | -0.12081 | -0.42437 | 124.239 | 123.91 | 124.0156 | 67.4941 | -124.2183 | 124.1811 | 124.2444 | 123.9409 | 67.4976 | -124.3774
34.9062 | 124.6262 | -67.424 | 56.8359 | 0.064445 | -0.00090066 | 0.00075378 | 0.056695 | -0.00036642 | 0.057083 | 0.049318 | -0.00058685 | 0.0011413 | 0.06634 | -0.0025343 | 0.067251 | -65.1998 | 0.001407 | -67.3503 | 56.7463 | 56.4264 | 56.532 | -67.3595 | -67.4296 | 0.009516 | -67.542 | 56.6976 | 56.7609 | 56.4436 | -67.4957 | 0.0645 | -0.089632 | 2.2242 | 0.073673 | 0.009173 | -0.40949 | -0.3039 | -0.071645 | -0.13834 | -0.005601 | -0.11795 | -0.0463 | -0.075031 | -0.39233 | 124.1703 | 123.8505 | 123.956 | 67.4254 | -124.1954 | 124.1216 | 124.1849 | 123.8676 | 67.4335 | -124.3316
35.9062 | 124.6307 | -67.4286 | 56.8588 | 0.049183 | 0.00016734 | -0.0013822 | 0.057764 | 0.0017696 | 0.058151 | 0.064579 | 0.00048215 | 0.0011413 | 0.06634 | -0.0014663 | 0.067251 | -65.2089 | 0.001407 | -67.3595 | 56.7417 | 56.4219 | 56.5229 | -67.3687 | -67.425 | 0.018674 | -67.542 | 56.7022 | 56.7655 | 56.4894 | -67.4957 | 0.05992 | -0.1171 | 2.2197 | 0.069095 | 0.009175 | -0.43696 | -0.33595 | -0.067067 | -0.15665 | 0.003555 | -0.11337 | -0.0463 | -0.093341 | -0.36944 | 124.1703 | 123.8505 | 123.9515 | 67.43 | -124.2275 | 124.1308 | 124.1941 | 123.918 | 67.4473 | -124.3545
36.9062 | 124.6307 | -67.424 | 56.8497 | 0.079707 | -0.0019697 | 0.00075378 | 0.055627 | 0.0017696 | 0.057083 | 0.07984 | 0.00048215 | 0.0011413 | 0.065272 | -0.0014663 | 0.065114 | -65.2181 | 0.005985 | -67.3458 | 56.7509 | 56.4127 | 56.5275 | -67.3595 | -67.425 | 0.014095 | -67.5511 | 56.6976 | 56.7701 | 56.4711 | -67.4911 | 0.0645 | -0.098787 | 2.2059 | 0.078251 | 0.013751 | -0.43696 | -0.32221 | -0.067066 | -0.15207 | -0.001023 | -0.1271 | -0.060036 | -0.079607 | -0.37859 | 124.1749 | 123.8367 | 123.9515 | 67.43 | -124.2092 | 124.1216 | 124.1941 | 123.8951 | 67.4381 | -124.3407
37.9062 | 124.5987 | -67.4423 | 56.8863 | 0.049183 | -0.00090066 | -0.00031422 | 0.055627 | 0.00070158 | 0.057083 | 0.07984 | 0.00048215 | 7.3343e-05 | 0.065272 | -0.00039829 | 0.064046 | -65.1906 | 0.010564 | -67.3549 | 56.7509 | 56.4219 | 56.532 | -67.3549 | -67.4296 | 0.009516 | -67.542 | 56.6976 | 56.7655 | 56.4528 | -67.4865 | 0.08739 | -0.13541 | 2.2517 | 0.087406 | 1.6e-05 | -0.46442 | -0.35426 | -0.044176 | -0.18869 | 0.01271 | -0.099634 | -0.055458 | -0.12081 | -0.43353 | 124.1932 | 123.8642 | 123.9744 | 67.4529 | -124.2412 | 124.1399 | 124.2078 | 123.8951 | 67.4518 | -124.3728
38.9062 | 124.6078 | -67.4286 | 56.8542 | 0.079707 | -0.00090066 | 0.00075378 | 0.055627 | -0.00036642 | 0.058151 | 0.064579 | 0.0015501 | 7.3343e-05 | 0.065272 | -0.00039829 | 0.066182 | -65.2044 | 0.005985 | -67.3503 | 56.7463 | 56.4219 | 56.5229 | -67.3091 | -67.4296 | 0.014095 | -67.5465 | 56.693 | 56.7655 | 56.4528 | -67.4911 | 0.11945 | -0.10794 | 2.2242 | 0.078251 | -0.041195 | -0.43238 | -0.33137 | -0.062488 | -0.16123 | -0.001023 | -0.11794 | -0.055457 | -0.088763 | -0.40149 | 124.1749 | 123.8505 | 123.9515 | 67.4346 | -124.1634 | 124.1216 | 124.1941 | 123.8814 | 67.4427 | -124.3453
39.9062 | 124.6078 | -67.4423 | 56.8634 | 0.064445 | -0.00090066 | -0.00031422 | 0.056695 | -0.0014344 | 0.056015 | 0.07984 | 0.00048215 | 0.0011413 | 0.06634 | -0.00039829 | 0.066182 | -65.2364 | 0.005985 | -67.3549 | 56.7417 | 56.4173 | 56.5229 | -67.3458 | -67.4342 | 0.014095 | -67.5465 | 56.6976 | 56.7655 | 56.439 | -67.4957 | 0.096548 | -0.12168 | 2.2059 | 0.087406 | -0.009142 | -0.44611 | -0.34053 | -0.053334 | -0.1658 | 0.008131 | -0.10421 | -0.050878 | -0.097918 | -0.42438 | 124.184 | 123.8596 | 123.9652 | 67.4483 | -124.2092 | 124.1399 | 124.2078 | 123.8813 | 67.4564 | -124.3591
40.9062 | 124.5895 | -67.4286 | 56.8451 | 0.064445 | 0.00016734 | -0.00031422 | 0.055627 | 0.00070158 | 0.057083 | 0.07984 | 0.00048215 | 7.3343e-05 | 0.06634 | -0.00039829 | 0.066182 | -65.2318 | 0.005985 | -67.3549 | 56.7417 | 56.4219 | 56.532 | -67.3275 | -67.4296 | 0.009516 | -67.5465 | 56.693 | 56.7609 | 56.4436 | -67.4911 | 0.10113 | -0.10337 | 2.1968 | 0.073673 | -0.027457 | -0.42323 | -0.31306 | -0.062488 | -0.15207 | -0.001023 | -0.11794 | -0.055457 | -0.084187 | -0.40149 | 124.1703 | 123.8505 | 123.9606 | 67.4346 | -124.1726 | 124.1216 | 124.1895 | 123.8722 | 67.4381 | -124.3362
41.9062 | 124.5804 | -67.4515 | 56.8771 | 0.064445 | -0.00090066 | -0.00031422 | 0.057764 | 0.00070158 | 0.058151 | 0.07984 | 0.0015501 | -0.00099466 | 0.065272 | -0.00039829 | 0.066182 | -65.2227 | 0.005985 | -67.3549 | 56.7463 | 56.4219 | 56.5275 | -67.3961 | -67.4296 | 0.004938 | -67.5511 | 56.7022 | 56.7655 | 56.5031 | -67.4957 | 0.055334 | -0.13083 | 2.2288 | 0.096561 | 0.041227 | -0.45527 | -0.34968 | -0.044179 | -0.17496 | 0.021865 | -0.099636 | -0.055457 | -0.11165 | -0.37401 | 124.1978 | 123.8733 | 123.9789 | 67.4575 | -124.2733 | 124.1537 | 124.217 | 123.9546 | 67.4564 | -124.3728
42.9062 | 124.5895 | -67.4835 | 56.8542 | 0.033921 | 0.0012363 | 0.00075378 | 0.055627 | 0.0028386 | 0.056015 | 0.049318 | 0.00048215 | 0.0011413 | 0.065272 | -0.0025343 | 0.066182 | -65.2272 | 0.015142 | -67.3503 | 56.7417 | 56.4127 | 56.5229 | -67.332 | -67.425 | 0.009516 | -67.5465 | 56.693 | 56.7655 | 56.4344 | -67.4911 | 0.15148 | -0.11252 | 2.2563 | 0.13318 | -0.0183 | -0.44154 | -0.33137 | -0.007556 | -0.16123 | 0.058487 | -0.063013 | -0.055457 | -0.088763 | -0.4198 | 124.2252 | 123.8962 | 124.0064 | 67.4987 | -124.1863 | 124.1765 | 124.249 | 123.918 | 67.493 | -124.3453
43.9062 | 124.5621 | -67.4927 | 56.8588 | 0.033921 | 0.00016734 | -0.00031422 | 0.055627 | -0.00036642 | 0.057083 | 0.07984 | 0.00048215 | 0.0011413 | 0.06634 | 0.00067071 | 0.064046 | -65.2318 | 0.015142 | -67.3503 | 56.7417 | 56.4264 | 56.5275 | -67.3778 | -67.4296 | 0.018674 | -67.542 | 56.6976 | 56.7655 | 56.4848 | -67.4911 | 0.11485 | -0.1171 | 2.2609 | 0.14234 | 0.027489 | -0.43238 | -0.33137 | 0.001599 | -0.16123 | 0.063064 | -0.04928 | -0.050879 | -0.093341 | -0.37401 | 124.2344 | 123.9191 | 124.0201 | 67.5078 | -124.2367 | 124.1903 | 124.2582 | 123.9775 | 67.5114 | -124.3499
44.9062 | 124.5895 | -67.4377 | 56.8405 | 0.064445 | 0.00016734 | -0.0013822 | 0.057764 | 0.0017696 | 0.057083 | 0.064579 | -0.00058685 | 7.3343e-05 | 0.064204 | 0.00067071 | 0.067251 | -65.2318 | 0.010564 | -67.3503 | 56.7463 | 56.4219 | 56.532 | -67.3458 | -67.425 | 0.009516 | -67.5465 | 56.693 | 56.7701 | 56.4619 | -67.4911 | 0.09197 | -0.09421 | 2.2059 | 0.087406 | -0.004564 | -0.41865 | -0.30848 | -0.053333 | -0.14749 | 0.01271 | -0.10879 | -0.055457 | -0.070452 | -0.3786 | 124.184 | 123.8596 | 123.9698 | 67.4483 | -124.1863 | 124.1308 | 124.2078 | 123.8997 | 67.4473 | -124.3316
45.9062 | 124.5392 | -67.4561 | 56.8451 | 0.049183 | -0.00090066 | -0.00031422 | 0.057764 | -0.00036642 | 0.057083 | 0.049318 | -0.00058685 | -0.00099466 | 0.065272 | -0.00039829 | 0.065114 | -65.2364 | 0.005985 | -67.3503 | 56.7509 | 56.4219 | 56.532 | -67.3595 | -67.425 | 0.014095 | -67.5511 | 56.6976 | 56.7609 | 56.439 | -67.4957 | 0.096544 | -0.09421 | 2.2197 | 0.10572 | 0.009173 | -0.42323 | -0.31306 | -0.039601 | -0.14749 | 0.031021 | -0.095058 | -0.055457 | -0.084187 | -0.40607 | 124.2069 | 123.8779 | 123.9881 | 67.462 | -124.2046 | 124.1537 | 124.217 | 123.8951 | 67.4702 | -124.3407
46.9062 | 124.5529 | -67.4561 | 56.8451 | 0.064445 | 0.00016734 | -0.0013822 | 0.055627 | -0.00036642 | 0.057083 | 0.049318 | 0.00048215 | -0.00099466 | 0.065272 | -0.00039829 | 0.066182 | -65.2272 | 0.015142 | -67.3458 | 56.7463 | 56.4127 | 56.532 | -67.3366 | -67.4296 | 0.009516 | -67.5465 | 56.693 | 56.7655 | 56.4482 | -67.5002 | 0.11944 | -0.098788 | 2.2288 | 0.1103 | -0.009143 | -0.43238 | -0.31306 | -0.044179 | -0.15207 | 0.026443 | -0.090479 | -0.0463 | -0.079608 | -0.39691 | 124.2024 | 123.8688 | 123.9881 | 67.4712 | -124.1817 | 124.1491 | 124.2215 | 123.9042 | 67.4656 | -124.3453
47.9062 | 124.5209 | -67.4561 | 56.8497 | 0.064445 | 0.0012363 | -0.00031422 | 0.055627 | -0.00036642 | 0.057083 | 0.064579 | 0.0015501 | 7.3343e-05 | 0.06634 | -0.0014663 | 0.066182 | -65.2227 | 0.010564 | -67.3503 | 56.7463 | 56.4264 | 56.5275 | -67.3549 | -67.4296 | 0.009516 | -67.5511 | 56.6976 | 56.7655 | 56.494 | -67.5002 | 0.10112 | -0.10337 | 2.2334 | 0.10572 | 0.004594 | -0.42322 | -0.32221 | -0.044179 | -0.15207 | 0.026443 | -0.095058 | -0.050879 | -0.084185 | -0.3557 | 124.2024 | 123.8825 | 123.9835 | 67.4666 | -124.2046 | 124.1537 | 124.2215 | 123.95 | 67.4656 | -124.3499
48.9062 | 124.5621 | -67.4515 | 56.8588 | 0.094969 | 0.00016734 | -0.00031422 | 0.056695 | 0.00070158 | 0.054946 | 0.064579 | 0.0026181 | 7.3343e-05 | 0.067408 | 0.00067071 | 0.064046 | -65.2227 | 0.010564 | -67.3366 | 56.7509 | 56.4173 | 56.5229 | -67.3687 | -67.4205 | 0.018674 | -67.542 | 56.693 | 56.7609 | 56.4528 | -67.4957 | 0.082808 | -0.10794 | 2.2288 | 0.11487 | 0.032066 | -0.44154 | -0.33595 | -0.044179 | -0.1658 | 0.031022 | -0.090479 | -0.0463 | -0.09792 | -0.40606 | 124.2024 | 123.8688 | 123.9744 | 67.462 | -124.2275 | 124.1445 | 124.2124 | 123.9042 | 67.4702 | -124.3545
49.9062 | 124.5392 | -67.4744 | 56.8359 | 0.064445 | -0.00090066 | -0.00031422 | 0.055627 | -0.00036642 | 0.057083 | 0.049318 | 0.0015501 | 7.3343e-05 | 0.067408 | 0.0017387 | 0.066182 | -65.2181 | 0.015142 | -67.3503 | 56.7463 | 56.4173 | 56.5275 | -67.332 | -67.425 | 0.004938 | -67.542 | 56.693 | 56.7655 | 56.4665 | -67.4911 | 0.14233 | -0.089632 | 2.2563 | 0.12403 | -0.0183 | -0.41865 | -0.30848 | -0.016712 | -0.14291 | 0.049331 | -0.067591 | -0.050879 | -0.070452 | -0.36944 | 124.2207 | 123.8917 | 124.0018 | 67.4895 | -124.168 | 124.1674 | 124.2399 | 123.9409 | 67.4793 | -124.327
50.9688 | 124.5346 | -67.4423 | 56.9046 | 0.049183 | 0.0012363 | -0.00031422 | 0.056695 | -0.00036642 | 0.056015 | 0.095101 | -0.0016549 | 0.0011413 | 0.065272 | -0.00039829 | 0.064046 | -65.1677 | 0.015142 | -67.3549 | 56.7692 | 56.4585 | 56.5549 | -67.4923 | -67.4296 | 0.014095 | -67.542 | 56.7022 | 56.7609 | 56.6451 | -67.4911 | -0.049978 | -0.1354 | 2.2746 | 0.087406 | 0.13738 | -0.4461 | -0.34967 | -0.048755 | -0.20242 | 0.01271 | -0.099634 | -0.050879 | -0.1437 | -0.25954 | 124.2115 | 123.9008 | 123.9973 | 67.4575 | -124.3969 | 124.1445 | 124.2032 | 124.0874 | 67.4564 | -124.3957
51.9062 | 124.5255 | -67.4469 | 56.8314 | 0.064445 | 0.00016734 | 0.0018228 | 0.056695 | 0.00070158 | 0.057083 | 0.07984 | -0.00058685 | 7.3343e-05 | 0.06634 | -0.00039829 | 0.065114 | -65.273 | 0.015142 | -67.3595 | 56.7692 | 56.4539 | 56.5503 | -67.4831 | -67.4296 | 0.018674 | -67.542 | 56.693 | 56.7609 | 56.6359 | -67.4957 | -0.036243 | -0.062163 | 2.1739 | 0.087405 | 0.12365 | -0.37744 | -0.28101 | -0.048757 | -0.13834 | 0.017287 | -0.095057 | -0.0463 | -0.070454 | -0.19545 | 124.2161 | 123.9008 | 123.9972 | 67.462 | -124.3145 | 124.1399 | 124.2078 | 124.0828 | 67.4656 | -124.327
52.9062 | 124.5804 | -67.4423 | 56.8542 | 0.064445 | -0.00090066 | -0.00031422 | 0.055627 | 0.00070158 | 0.057083 | 0.064579 | 0.00048215 | -0.0020637 | 0.065272 | 0.00067071 | 0.064046 | -65.2685 | 0.019721 | -67.3595 | 56.7646 | 56.4493 | 56.5549 | -67.4969 | -67.4433 | 0.018674 | -67.5374 | 56.7022 | 56.7609 | 56.6771 | -67.4911 | -0.054557 | -0.08963 | 2.1739 | 0.082828 | 0.13739 | -0.40491 | -0.29932 | -0.048755 | -0.15207 | -0.001027 | -0.095055 | -0.0463 | -0.093342 | -0.17713 | 124.2069 | 123.8917 | 123.9973 | 67.462 | -124.3511 | 124.1445 | 124.2032 | 124.1194 | 67.461 | -124.3453
53.9062 | 124.5987 | -67.4194 | 56.8268 | 0.049183 | 0.00016734 | 0.00075378 | 0.055627 | 0.00070158 | 0.054946 | 0.049318 | -0.00058685 | -0.0020637 | 0.064204 | 0.00067071 | 0.066182 | -65.241 | 0.015142 | -67.3458 | 56.7646 | 56.4539 | 56.5549 | -67.4877 | -67.4296 | 0.018674 | -67.5374 | 56.6976 | 56.7609 | 56.5947 | -67.5002 | -0.068287 | -0.062164 | 2.1785 | 0.073674 | 0.14196 | -0.37286 | -0.27185 | -0.0808 | -0.12918 | -0.010178 | -0.11794 | -0.037143 | -0.065876 | -0.23208 | 124.1841 | 123.8734 | 123.9744 | 67.4346 | -124.3145 | 124.117 | 124.1803 | 124.0141 | 67.4381 | -124.327
54.9062 | 124.5941 | -67.4469 | 56.8222 | 0.049183 | 0.00016734 | 0.00075378 | 0.057764 | -0.0014344 | 0.056015 | 0.064579 | 0.00048215 | -0.00099466 | 0.063135 | 0.00067071 | 0.064046 | -65.2364 | 0.019721 | -67.3595 | 56.7646 | 56.4585 | 56.5549 | -67.4786 | -67.4296 | 0.014095 | -67.5374 | 56.693 | 56.7655 | 56.6405 | -67.4957 | -0.031664 | -0.057587 | 2.2105 | 0.087405 | 0.11907 | -0.36371 | -0.26728 | -0.048757 | -0.12918 | 0.017287 | -0.090478 | -0.041721 | -0.05672 | -0.18172 | 124.2115 | 123.9054 | 124.0018 | 67.4666 | -124.3008 | 124.1399 | 124.2124 | 124.0874 | 67.461 | -124.3179
55.9062 | 124.53 | -67.4423 | 56.8268 | 0.064445 | 0.0012363 | 0.00075378 | 0.056695 | 0.00070158 | 0.056015 | 0.064579 | -0.00058685 | -0.00099466 | 0.06634 | -0.00039829 | 0.064046 | -65.2364 | 0.010564 | -67.3503 | 56.7646 | 56.4539 | 56.5595 | -67.4923 | -67.425 | 0.023253 | -67.5374 | 56.693 | 56.7609 | 56.6039 | -67.4911 | -0.049978 | -0.062164 | 2.2059 | 0.091984 | 0.14196 | -0.37286 | -0.26728 | -0.048755 | -0.13376 | 0.017288 | -0.095055 | -0.0463 | -0.065876 | -0.22293 | 124.2069 | 123.8962 | 124.0018 | 67.4529 | -124.3191 | 124.1353 | 124.2032 | 124.0462 | 67.4656 | -124.3179
56.9062 | 124.5804 | -67.4515 | 56.8268 | 0.049183 | 0.00016734 | -0.00031422 | 0.056695 | -0.00036642 | 0.056015 | 0.064579 | -0.00058685 | -0.00099466 | 0.064204 | 0.00067071 | 0.067251 | -65.2501 | 0.019721 | -67.3412 | 56.76 | 56.4585 | 56.5458 | -67.4786 | -67.4205 | 0.018674 | -67.5328 | 56.6976 | 56.7563 | 56.6817 | -67.4911 | -0.027086 | -0.066742 | 2.2013 | 0.1103 | 0.13738 | -0.36828 | -0.28101 | -0.0396 | -0.12918 | 0.031022 | -0.081321 | -0.041721 | -0.070454 | -0.14509 | 124.2115 | 123.91 | 123.9972 | 67.4712 | -124.3053 | 124.1491 | 124.2078 | 124.1332 | 67.4702 | -124.3179
57.9062 | 124.5575 | -67.4469 | 56.8405 | 0.018659 | 0.0012363 | -0.0013822 | 0.056695 | 0.00070158 | 0.058151 | 0.049318 | -0.00058685 | 0.0011413 | 0.064204 | 0.0017387 | 0.061909 | -65.273 | 0.015142 | -67.3412 | 56.7463 | 56.5455 | 56.5275 | -67.4648 | -67.4205 | 0.014095 | -67.542 | 56.6976 | 56.7655 | 56.7687 | -67.4957 | -0.017928 | -0.09421 | 2.1739 | 0.10572 | 0.12365 | -0.29502 | -0.31306 | -0.048757 | -0.14291 | 0.026444 | -0.095057 | -0.0463 | -0.07503 | -0.071829 | 124.1932 | 123.9924 | 123.9744 | 67.462 | -124.3053 | 124.1445 | 124.2124 | 124.2156 | 67.461 | -124.3362
58.9062 | 124.5483 | -67.4423 | 56.8268 | 0.064445 | 0.00016734 | -0.00031422 | 0.056695 | -0.0025034 | 0.057083 | 0.064579 | 0.00048215 | -0.00099466 | 0.065272 | 0.0017387 | 0.065114 | -65.2501 | 0.015142 | -67.3458 | 56.7509 | 56.6188 | 56.5275 | -67.4236 | -67.4296 | 0.009516 | -67.5374 | 56.6976 | 56.7609 | 56.7458 | -67.4911 | 0.018706 | -0.075899 | 2.1922 | 0.096562 | 0.077856 | -0.20802 | -0.29933 | -0.048755 | -0.12918 | 0.01271 | -0.095055 | -0.0463 | -0.065876 | -0.080989 | 124.1932 | 124.0611 | 123.9698 | 67.4575 | -124.2504 | 124.1399 | 124.2032 | 124.1881 | 67.4518 | -124.3179
59.9062 | 124.5758 | -67.4286 | 56.8176 | 0.049183 | 0.0012363 | 0.00075378 | 0.055627 | 0.00070158 | 0.054946 | 0.07984 | 0.00048215 | -0.00099466 | 0.065272 | 0.0028067 | 0.065114 | -65.2181 | 0.005985 | -67.3366 | 56.7509 | 56.5043 | 56.5366 | -67.4419 | -67.4296 | 0.009516 | -67.5328 | 56.7022 | 56.7655 | 56.6359 | -67.4957 | -0.013343 | -0.066744 | 2.2105 | 0.091986 | 0.10533 | -0.31334 | -0.28101 | -0.067067 | -0.11545 | -0.001023 | -0.10421 | -0.037142 | -0.052142 | -0.18172 | 124.1795 | 123.9329 | 123.9652 | 67.4346 | -124.2596 | 124.1308 | 124.1941 | 124.0645 | 67.4381 | -124.3133
60.9062 | 124.5987 | -67.4286 | 56.8222 | 0.064445 | 0.0012363 | 0.0018228 | 0.057764 | 0.0017696 | 0.056015 | 0.064579 | -0.0016549 | 7.3343e-05 | 0.064204 | -0.00039829 | 0.064046 | -65.1723 | 0.015142 | -67.3549 | 56.7371 | 56.4951 | 56.5229 | -67.4374 | -67.4342 | 0.004938 | -67.5374 | 56.6976 | 56.7517 | 56.6313 | -67.5002 | -0.008764 | -0.085057 | 2.2563 | 0.073673 | 0.082437 | -0.32707 | -0.29933 | -0.071645 | -0.1246 | -0.005602 | -0.10879 | -0.037143 | -0.070456 | -0.19088 | 124.1657 | 123.9237 | 123.9515 | 67.4437 | -124.2596 | 124.1262 | 124.1803 | 124.0599 | 67.4335 | -124.3224
61.9062 | 124.6033 | -67.4698 | 56.8176 | 0.064445 | 0.0012363 | -0.0013822 | 0.055627 | -0.0025034 | 0.056015 | 0.07984 | -0.00058685 | -0.00099466 | 0.065272 | 0.0017387 | 0.064046 | -65.154 | 0.015142 | -67.3549 | 56.7371 | 56.486 | 56.532 | -67.4511 | -67.4342 | 0.004938 | -67.5374 | 56.6976 | 56.7701 | 56.668 | -67.4957 | 0.018698 | -0.080479 | 2.3158 | 0.11487 | 0.096174 | -0.33166 | -0.28559 | -0.025868 | -0.12003 | 0.035597 | -0.067589 | -0.041721 | -0.047564 | -0.14967 | 124.2069 | 123.9558 | 124.0018 | 67.4849 | -124.2687 | 124.1674 | 124.2399 | 124.1377 | 67.4747 | -124.3133
62.9062 | 124.617 | -67.4423 | 56.8314 | 0.033921 | 0.0012363 | 0.00075378 | 0.056695 | -0.0014344 | 0.057083 | 0.049318 | -0.00058685 | -0.0020637 | 0.064204 | 0.0017387 | 0.062978 | -65.1586 | 0.010564 | -67.3366 | 56.7463 | 56.4768 | 56.5229 | -67.4282 | -67.4159 | 0.009516 | -67.5374 | 56.6976 | 56.7655 | 56.6084 | -67.4957 | 0.014127 | -0.085055 | 2.2838 | 0.10572 | 0.091592 | -0.35455 | -0.30848 | -0.053334 | -0.13376 | 0.026446 | -0.095055 | -0.041721 | -0.065875 | -0.22292 | 124.1886 | 123.9191 | 123.9652 | 67.4529 | -124.2596 | 124.1399 | 124.2078 | 124.0508 | 67.4518 | -124.327
63.9062 | 124.617 | -67.4286 | 56.813 | 0.033921 | 0.0023043 | -0.00031422 | 0.058832 | -0.0025034 | 0.054946 | 0.07984 | -0.00058685 | 7.3343e-05 | 0.063135 | 0.00067071 | 0.065114 | -65.1769 | 0.019721 | -67.3732 | 56.8058 | 56.4722 | 56.587 | -67.4557 | -67.4525 | 0.018674 | -67.542 | 56.693 | 56.7609 | 56.6451 | -67.5002 | -0.02708 | -0.007225 | 2.2517 | 0.05536 | 0.08244 | -0.34081 | -0.22607 | -0.071645 | -0.12003 | -0.023917 | -0.11337 | -0.041722 | -0.052143 | -0.16799 | 124.2344 | 123.9008 | 124.0156 | 67.4483 | -124.2687 | 124.1216 | 124.1895 | 124.0737 | 67.4473 | -124.3133
64.9062 | 124.5895 | -67.4561 | 56.8268 | 0.033921 | 0.00016734 | 0.00075378 | 0.056695 | -0.00036642 | 0.056015 | 0.049318 | -0.0016549 | 0.0011413 | 0.065272 | 0.0028067 | 0.064046 | -65.1815 | 0.0243 | -67.3687 | 56.7921 | 56.4768 | 56.587 | -67.506 | -67.4342 | 0.023253 | -67.5328 | 56.6976 | 56.7609 | 56.6588 | -67.4957 | -0.049982 | -0.034694 | 2.2746 | 0.087404 | 0.13739 | -0.34997 | -0.2398 | -0.039601 | -0.12918 | 0.021864 | -0.076743 | -0.037142 | -0.065876 | -0.16798 | 124.2481 | 123.9329 | 124.043 | 67.4804 | -124.3328 | 124.1537 | 124.217 | 124.1149 | 67.4793 | -124.3224
65.9062 | 124.6033 | -67.4561 | 56.8268 | 0.064445 | 0.00016734 | 0.00075378 | 0.056695 | 0.00070158 | 0.054946 | 0.07984 | -0.00058685 | -0.00099466 | 0.064204 | 0.0017387 | 0.065114 | -65.1769 | 0.0243 | -67.3549 | 56.7692 | 56.4402 | 56.5687 | -67.4099 | -67.4296 | 0.018674 | -67.5328 | 56.693 | 56.7609 | 56.5947 | -67.4911 | 0.046176 | -0.057585 | 2.2792 | 0.10114 | 0.054963 | -0.3866 | -0.25812 | -0.035022 | -0.13376 | 0.026443 | -0.076743 | -0.041721 | -0.065876 | -0.23208 | 124.2253 | 123.8962 | 124.0247 | 67.4804 | -124.2367 | 124.1491 | 124.217 | 124.0508 | 67.4747 | -124.3179
66.9062 | 124.5987 | -67.4469 | 56.8176 | 0.049183 | 0.0012363 | 0.0018228 | 0.056695 | 0.00070158 | 0.054946 | 0.064579 | -0.00058685 | 0.0011413 | 0.063135 | 0.0028067 | 0.062978 | -65.1723 | 0.019721 | -67.3458 | 56.7555 | 56.4402 | 56.5412 | -67.4099 | -67.425 | 0.014095 | -67.5374 | 56.6976 | 56.7609 | 56.5352 | -67.5002 | 0.03702 | -0.062166 | 2.2746 | 0.10114 | 0.064119 | -0.37744 | -0.27643 | -0.053335 | -0.12003 | 0.021865 | -0.090478 | -0.037143 | -0.056721 | -0.28245 | 124.2024 | 123.8871 | 123.9881 | 67.4666 | -124.2275 | 124.1445 | 124.2078 | 123.9821 | 67.461 | -124.3179
67.9062 | 124.5117 | -67.4652 | 56.8497 | 0.033921 | 0.0012363 | -0.00031422 | 0.057764 | -0.00036642 | 0.056015 | 0.064579 | -0.00058685 | -0.0020637 | 0.065272 | 0.0017387 | 0.064046 | -65.1586 | 0.015142 | -67.3503 | 56.7417 | 56.4264 | 56.532 | -67.3687 | -67.425 | 0.014095 | -67.542 | 56.6884 | 56.7609 | 56.4894 | -67.4957 | 0.096541 | -0.10794 | 2.3066 | 0.11487 | 0.018331 | -0.42322 | -0.31764 | -0.030446 | -0.16123 | 0.040176 | -0.076746 | -0.0463 | -0.088764 | -0.36028 | 124.2069 | 123.8917 | 123.9972 | 67.4804 | -124.2183 | 124.1537 | 124.2261 | 123.9546 | 67.4793 | -124.3453
68.9062 | 124.5941 | -67.4698 | 56.8359 | 0.049183 | 0.0012363 | 0.0018228 | 0.056695 | 0.00070158 | 0.057083 | 0.049318 | -0.00058685 | 7.3343e-05 | 0.063135 | 0.00067071 | 0.065114 | -65.1677 | 0.015142 | -67.3412 | 56.7326 | 56.4127 | 56.5275 | -67.3778 | -67.4205 | 0.014095 | -67.542 | 56.693 | 56.7655 | 56.4207 | -67.5002 | 0.091961 | -0.10337 | 2.3021 | 0.12861 | 0.036646 | -0.42323 | -0.30848 | -0.030446 | -0.14291 | 0.049333 | -0.072168 | -0.041722 | -0.070452 | -0.41522 | 124.2024 | 123.8825 | 123.9972 | 67.4849 | -124.2138 | 124.1628 | 124.2353 | 123.8905 | 67.4839 | -124.3362
69.9062 | 124.5438 | -67.4561 | 56.813 | 0.064445 | 0.0012363 | 0.00075378 | 0.057764 | -0.00036642 | 0.054946 | 0.049318 | -0.00058685 | -0.00099466 | 0.064204 | 0.0028067 | 0.064046 | -65.1677 | 0.010564 | -67.3458 | 56.7371 | 56.4081 | 56.5275 | -67.3275 | -67.425 | 0.014095 | -67.5282 | 56.7022 | 56.7517 | 56.3978 | -67.4957 | 0.1286 | -0.075901 | 2.2883 | 0.1103 | -0.018301 | -0.40492 | -0.28559 | -0.039601 | -0.11087 | 0.031021 | -0.072165 | -0.032564 | -0.0613 | -0.41523 | 124.1932 | 123.8642 | 123.9835 | 67.4666 | -124.1405 | 124.1582 | 124.2078 | 123.8539 | 67.4702 | -124.3087
70.9062 | 124.5712 | -67.4652 | 56.8405 | 0.064445 | 0.0012363 | 0.00075378 | 0.054559 | 0.00070158 | 0.054946 | 0.064579 | -0.00058685 | 7.3343e-05 | 0.064204 | 0.0017387 | 0.064046 | -65.154 | 0.019721 | -67.3458 | 56.7371 | 56.4127 | 56.5229 | -67.3549 | -67.425 | 0.014095 | -67.5374 | 56.6976 | 56.7609 | 56.3795 | -67.4911 | 0.11028 | -0.10337 | 2.3112 | 0.11945 | 0.009172 | -0.42781 | -0.31764 | -0.025867 | -0.14291 | 0.040176 | -0.072167 | -0.0463 | -0.079609 | -0.46101 | 124.2024 | 123.8779 | 123.9881 | 67.4849 | -124.1954 | 124.1628 | 124.2261 | 123.8447 | 67.4793 | -124.3316
71.9062 | 124.5529 | -67.4194 | 56.813 | 0.064445 | 0.00016734 | -0.0013822 | 0.056695 | -0.00036642 | 0.054946 | 0.064579 | -0.0016549 | -0.00099466 | 0.064204 | 0.0038757 | 0.062978 | -65.1631 | 0.005985 | -67.3458 | 56.7326 | 56.4081 | 56.5275 | -67.3641 | -67.425 | 0.014095 | -67.5282 | 56.6884 | 56.7609 | 56.4757 | -67.4957 | 0.055344 | -0.08048 | 2.2563 | 0.073674 | 0.01833 | -0.40492 | -0.28559 | -0.076222 | -0.12461 | -0.0056 | -0.10879 | -0.032564 | -0.052143 | -0.33739 | 124.152 | 123.8276 | 123.9469 | 67.4254 | -124.1771 | 124.1079 | 124.1803 | 123.8951 | 67.4335 | -124.3087
72.9062 | 124.5987 | -67.4561 | 56.8268 | 0.049183 | -0.00090066 | -0.00031422 | 0.056695 | -0.0014344 | 0.056015 | 0.064579 | -0.0016549 | 7.3343e-05 | 0.063135 | 0.0028067 | 0.065114 | -65.154 | 0.015142 | -67.3503 | 56.7371 | 56.4127 | 56.532 | -67.3549 | -67.4205 | 0.014095 | -67.5236 | 56.693 | 56.7655 | 56.4436 | -67.4957 | 0.10112 | -0.089634 | 2.3021 | 0.10572 | 0.004594 | -0.41407 | -0.29475 | -0.039601 | -0.13376 | 0.0356 | -0.067586 | -0.027985 | -0.061297 | -0.38318 | 124.1932 | 123.8688 | 123.9881 | 67.4712 | -124.1817 | 124.1491 | 124.2215 | 123.8997 | 67.4702 | -124.3224
73.9062 | 124.5026 | -67.5018 | 56.8497 | 0.049183 | 0.0023043 | -0.0013822 | 0.056695 | 0.00070158 | 0.054946 | 0.018796 | -0.00058685 | 7.3343e-05 | 0.06634 | 0.0017387 | 0.062978 | -65.1403 | 0.019721 | -67.3503 | 56.7417 | 56.3898 | 56.5229 | -67.3824 | -67.4296 | 0.014095 | -67.5328 | 56.693 | 56.7655 | 56.4207 | -67.4957 | 0.11942 | -0.10794 | 2.3616 | 0.15149 | 0.032068 | -0.45986 | -0.32679 | 0.006175 | -0.15665 | 0.072219 | -0.030967 | -0.037142 | -0.084185 | -0.42896 | 124.2436 | 123.8916 | 124.0247 | 67.5216 | -124.2321 | 124.1949 | 124.2673 | 123.9225 | 67.5159 | -124.3453
74.9062 | 124.4843 | -67.4835 | 56.8451 | 0.064445 | 0.0012363 | 0.00075378 | 0.056695 | -0.0014344 | 0.057083 | 0.034057 | 0.00048215 | 7.3343e-05 | 0.064204 | 0.0028067 | 0.062978 | -65.1403 | 0.015142 | -67.3458 | 56.7371 | 56.4173 | 56.5229 | -67.3366 | -67.4205 | 0.018674 | -67.5282 | 56.6884 | 56.7563 | 56.3566 | -67.5002 | 0.1469 | -0.10795 | 2.3433 | 0.13776 | -0.009143 | -0.4278 | -0.32222 | -0.016713 | -0.15665 | 0.063066 | -0.044699 | -0.027986 | -0.088765 | -0.48848 | 124.2207 | 123.9008 | 124.0064 | 67.4987 | -124.1817 | 124.172 | 124.2398 | 123.8401 | 67.5022 | -124.3453
75.9062 | 124.5209 | -67.4515 | 56.8405 | 0.049183 | 0.00016734 | 0.00075378 | 0.056695 | -0.0025034 | 0.057083 | 0.034057 | 0.00048215 | -0.00099466 | 0.065272 | 0.0028067 | 0.064046 | -65.1448 | 0.010564 | -67.3366 | 56.7463 | 56.4127 | 56.532 | -67.3091 | -67.425 | 0.018674 | -67.5374 | 56.693 | 56.7563 | 56.4299 | -67.5002 | 0.14233 | -0.09421 | 2.3066 | 0.11487 | -0.02746 | -0.42781 | -0.30848 | -0.048757 | -0.14749 | 0.026443 | -0.0859 | -0.037143 | -0.084187 | -0.41065 | 124.1978 | 123.8642 | 123.9835 | 67.462 | -124.1497 | 124.1445 | 124.2078 | 123.8813 | 67.4702 | -124.3407
76.9062 | 124.5209 | -67.4606 | 56.8451 | 0.064445 | 0.00016734 | -0.00031422 | 0.054559 | -0.0014344 | 0.054946 | 0.064579 | -0.00058685 | -0.0020637 | 0.065272 | 0.0038757 | 0.065114 | -65.1494 | 0.010564 | -67.3503 | 56.7326 | 56.4081 | 56.5183 | -67.3732 | -67.4205 | 0.014095 | -67.5328 | 56.6976 | 56.7655 | 56.3658 | -67.4957 | 0.087384 | -0.11252 | 2.3112 | 0.11029 | 0.02291 | -0.43696 | -0.32679 | -0.035024 | -0.14749 | 0.040177 | -0.072166 | -0.037142 | -0.079608 | -0.47932 | 124.1932 | 123.8688 | 123.9789 | 67.4712 | -124.2183 | 124.1582 | 124.2261 | 123.8264 | 67.4747 | -124.3407
77.9688 | 124.4659 | -67.4698 | 56.8863 | 0.049183 | 0.0012363 | 0.0028908 | 0.055627 | -0.0014344 | 0.054946 | 0.049318 | 0.00048215 | 7.3343e-05 | 0.064204 | 0.0038757 | 0.065114 | -65.1219 | 0.015142 | -67.3458 | 56.7417 | 56.4219 | 56.532 | -67.3732 | -67.425 | 0.009516 | -67.5374 | 56.6884 | 56.7609 | 56.4116 | -67.5002 | 0.09654 | -0.14457 | 2.3478 | 0.12403 | 0.027488 | -0.46442 | -0.35426 | -0.030446 | -0.19785 | 0.044754 | -0.067589 | -0.037143 | -0.12539 | -0.47474 | 124.2115 | 123.8917 | 124.0018 | 67.4849 | -124.2595 | 124.1582 | 124.2307 | 123.8813 | 67.4793 | -124.3865
78.9062 | 124.5666 | -67.4469 | 56.8268 | 0.064445 | 0.00016734 | -0.00031422 | 0.055627 | 0.00070158 | 0.054946 | 0.049318 | -0.00058685 | 7.3343e-05 | 0.064204 | 0.0028067 | 0.065114 | -65.1631 | 0.015142 | -67.3458 | 56.7371 | 56.4219 | 56.5275 | -67.3824 | -67.4159 | 0.014095 | -67.5282 | 56.693 | 56.7655 | 56.3932 | -67.4957 | 0.064493 | -0.089634 | 2.2838 | 0.10114 | 0.036646 | -0.40492 | -0.29933 | -0.048757 | -0.13376 | 0.031023 | -0.081321 | -0.032564 | -0.061297 | -0.43354 | 124.184 | 123.8688 | 123.9744 | 67.462 | -124.2092 | 124.1399 | 124.2124 | 123.8401 | 67.461 | -124.3224
79.9062 | 124.5163 | -67.4606 | 56.813 | 0.033921 | -0.00090066 | -0.0013822 | 0.057764 | -0.00036642 | 0.056015 | 0.049318 | -0.00058685 | 7.3343e-05 | 0.063135 | 0.0038757 | 0.062978 | -65.1494 | 0.010564 | -67.3458 | 56.7371 | 56.4219 | 56.5275 | -67.3504 | -67.425 | 0.009516 | -67.5282 | 56.693 | 56.7609 | 56.3932 | -67.4957 | 0.11028 | -0.075901 | 2.3112 | 0.11487 | 0.004593 | -0.39118 | -0.28559 | -0.035024 | -0.12003 | 0.035598 | -0.067588 | -0.032564 | -0.052143 | -0.41981 | 124.1978 | 123.8825 | 123.9881 | 67.4712 | -124.1634 | 124.1537 | 124.2215 | 123.8539 | 67.4701 | -124.3087
80.9531 | 124.4614 | -67.4698 | 56.8817 | 0.064445 | 0.00016734 | 0.00075378 | 0.056695 | 0.00070158 | 0.056015 | 0.064579 | 0.00048215 | -0.0020637 | 0.065272 | 0.0049437 | 0.064046 | -65.1174 | 0.015142 | -67.3366 | 56.7326 | 56.4219 | 56.532 | -67.3595 | -67.425 | 0.009516 | -67.5374 | 56.6884 | 56.7746 | 56.439 | -67.4957 | 0.11028 | -0.14915 | 2.3524 | 0.13318 | 0.022908 | -0.45985 | -0.34968 | -0.025868 | -0.19327 | 0.044754 | -0.067589 | -0.041721 | -0.10707 | -0.44269 | 124.2024 | 123.8917 | 124.0018 | 67.4849 | -124.2412 | 124.1582 | 124.2444 | 123.9088 | 67.4793 | -124.3774
81.9062 | 124.4614 | -67.5018 | 56.8451 | 0.064445 | -0.00090066 | 0.00075378 | 0.055627 | -0.0014344 | 0.053878 | 0.049318 | -0.00058685 | -0.00099466 | 0.063135 | 0.0038757 | 0.062978 | -65.1311 | 0.015142 | -67.3366 | 56.728 | 56.4081 | 56.5275 | -67.3732 | -67.4205 | 0.018674 | -67.5282 | 56.6884 | 56.7701 | 56.4299 | -67.5048 | 0.12858 | -0.1171 | 2.3707 | 0.16523 | 0.036645 | -0.43696 | -0.31764 | -0.002982 | -0.15665 | 0.081376 | -0.026389 | -0.023407 | -0.07503 | -0.41522 | 124.2298 | 123.91 | 124.0293 | 67.517 | -124.2183 | 124.1903 | 124.2719 | 123.9317 | 67.5205 | -124.3499
82.9062 | 124.4614 | -67.4973 | 56.8497 | 0.049183 | -0.00090066 | 0.00075378 | 0.056695 | -0.0014344 | 0.056015 | 0.07984 | -0.0016549 | -0.0020637 | 0.065272 | 0.0028067 | 0.062978 | -65.1403 | 0.015142 | -67.3366 | 56.7417 | 56.4081 | 56.5229 | -67.3549 | -67.4205 | 0.014095 | -67.5374 | 56.693 | 56.7609 | 56.3795 | -67.4957 | 0.14232 | -0.10794 | 2.357 | 0.16065 | 0.018329 | -0.44154 | -0.32679 | 0.001597 | -0.15665 | 0.076798 | -0.040124 | -0.041721 | -0.088764 | -0.47017 | 124.239 | 123.9054 | 124.0201 | 67.5124 | -124.2046 | 124.1903 | 124.2582 | 123.8768 | 67.5113 | -124.3453
83.9062 | 124.4705 | -67.5018 | 56.8359 | 0.064445 | 0.0012363 | -0.00031422 | 0.056695 | -0.0014344 | 0.056015 | 0.049318 | -0.0016549 | 7.3343e-05 | 0.064204 | 0.0028067 | 0.065114 | -65.1403 | 0.015142 | -67.3412 | 56.7326 | 56.4127 | 56.5229 | -67.3412 | -67.4159 | 0.004938 | -67.5328 | 56.693 | 56.7563 | 56.3978 | -67.4911 | 0.16063 | -0.10337 | 2.3616 | 0.16065 | 1.5e-05 | -0.42323 | -0.31306 | 0.010754 | -0.14291 | 0.085955 | -0.030967 | -0.041721 | -0.079609 | -0.43812 | 124.2344 | 123.9145 | 124.0247 | 67.517 | -124.1771 | 124.1949 | 124.2582 | 123.8996 | 67.5068 | -124.327
84.9062 | 124.4751 | -67.5018 | 56.8542 | 0.049183 | -0.00090066 | 0.00075378 | 0.056695 | -0.00036642 | 0.056015 | 0.07984 | 0.0015501 | -0.00099466 | 0.065272 | 0.0038757 | 0.062978 | -65.1311 | 0.005985 | -67.3366 | 56.7371 | 56.4219 | 56.532 | -67.3916 | -67.4159 | 0.009516 | -67.5282 | 56.693 | 56.7609 | 56.3566 | -67.4957 | 0.11027 | -0.1171 | 2.3707 | 0.16523 | 0.054961 | -0.43238 | -0.32221 | 0.006175 | -0.16123 | 0.085955 | -0.026389 | -0.032564 | -0.093342 | -0.49764 | 124.239 | 123.9237 | 124.0339 | 67.5078 | -124.2458 | 124.1949 | 124.2627 | 123.8584 | 67.5113 | -124.3499
85.9062 | 124.5071 | -67.4744 | 56.8405 | 0.049183 | 0.0012363 | -0.00031422 | 0.054559 | -0.0014344 | 0.056015 | 0.064579 | 0.0015501 | -0.0020637 | 0.064204 | 0.0049437 | 0.064046 | -65.1494 | 0.015142 | -67.3366 | 56.728 | 56.4173 | 56.532 | -67.3641 | -67.4205 | 0.009516 | -67.5282 | 56.6884 | 56.7655 | 56.4482 | -67.4957 | 0.11028 | -0.11252 | 2.325 | 0.13776 | 0.027487 | -0.42323 | -0.30848 | -0.021291 | -0.15207 | 0.05391 | -0.053855 | -0.032564 | -0.07503 | -0.39233 | 124.2024 | 123.8917 | 124.0064 | 67.4895 | -124.2046 | 124.1628 | 124.2399 | 123.9225 | 67.4839 | -124.3362
86.9062 | 124.4751 | -67.4835 | 56.8588 | 0.018659 | 0.00016734 | -0.00031422 | 0.056695 | -0.0025034 | 0.054946 | 0.064579 | -0.00058685 | 7.3343e-05 | 0.065272 | 0.0049437 | 0.062978 | -65.1357 | 0.019721 | -67.3412 | 56.7371 | 56.4127 | 56.532 | -67.3961 | -67.4205 | 0.009516 | -67.5282 | 56.6884 | 56.7701 | 56.3566 | -67.5002 | 0.087378 | -0.12168 | 2.3478 | 0.14234 | 0.054962 | -0.44612 | -0.32679 | -0.016713 | -0.17038 | 0.063066 | -0.044699 | -0.027986 | -0.088763 | -0.50221 | 124.2207 | 123.8962 | 124.0156 | 67.5032 | -124.255 | 124.172 | 124.2536 | 123.8401 | 67.493 | -124.3591
87.9062 | 124.4202 | -67.4927 | 56.8542 | 0.049183 | 0.00016734 | 0.0018228 | 0.056695 | -0.0014344 | 0.056015 | 0.064579 | 0.00048215 | 7.3343e-05 | 0.063135 | 0.0049437 | 0.064046 | -65.1219 | 0.019721 | -67.332 | 56.7371 | 56.4173 | 56.532 | -67.3687 | -67.4159 | 0.009516 | -67.5328 | 56.7022 | 56.7609 | 56.3887 | -67.4911 | 0.12401 | -0.1171 | 2.3707 | 0.16065 | 0.036644 | -0.43696 | -0.32221 | 0.001599 | -0.15207 | 0.0768 | -0.040122 | -0.041721 | -0.093342 | -0.46559 | 124.2298 | 123.91 | 124.0247 | 67.5124 | -124.2229 | 124.1949 | 124.2536 | 123.8813 | 67.5022 | -124.3453
88.9062 | 124.4522 | -67.4881 | 56.8542 | 0.064445 | 0.00016734 | -0.00031422 | 0.056695 | -0.0025034 | 0.057083 | 0.049318 | 0.0015501 | -0.0020637 | 0.065272 | 0.0060117 | 0.065114 | -65.1174 | 0.015142 | -67.3458 | 56.7371 | 56.4081 | 56.5275 | -67.3732 | -67.425 | 0.009516 | -67.5282 | 56.693 | 56.7563 | 56.3658 | -67.4957 | 0.11485 | -0.1171 | 2.3707 | 0.14234 | 0.027488 | -0.44612 | -0.32679 | -0.007558 | -0.16123 | 0.063064 | -0.040122 | -0.032564 | -0.09792 | -0.48848 | 124.2252 | 123.8962 | 124.0156 | 67.5032 | -124.2275 | 124.1811 | 124.2444 | 123.8539 | 67.4976 | -124.3499
89.9062 | 124.4431 | -67.4789 | 56.8771 | 0.079707 | 0.00016734 | 0.0018228 | 0.055627 | -0.00036642 | 0.057083 | 0.064579 | 0.00048215 | -0.0020637 | 0.063135 | 0.0049437 | 0.064046 | -65.1265 | 0.010564 | -67.3412 | 56.7417 | 56.4219 | 56.532 | -67.4099 | -67.4159 | 0.018674 | -67.5282 | 56.6884 | 56.7609 | 56.4665 | -67.4957 | 0.069064 | -0.13541 | 2.3524 | 0.13776 | 0.068698 | -0.45527 | -0.3451 | -0.016713 | -0.18869 | 0.063067 | -0.049277 | -0.032564 | -0.11623 | -0.41064 | 124.2207 | 123.9008 | 124.011 | 67.4895 | -124.287 | 124.1674 | 124.2398 | 123.9454 | 67.4976 | -124.3728
90.9062 | 124.4476 | -67.5018 | 56.8314 | 0.033921 | 0.00016734 | 0.00075378 | 0.055627 | -0.0014344 | 0.056015 | 0.064579 | 0.00048215 | -0.00099466 | 0.065272 | 0.0049437 | 0.061909 | -65.1219 | 0.019721 | -67.3458 | 56.7371 | 56.4173 | 56.5183 | -67.3549 | -67.4205 | 0.009516 | -67.5236 | 56.6976 | 56.7609 | 56.3841 | -67.4957 | 0.1469 | -0.094212 | 2.3799 | 0.15607 | 0.009172 | -0.41407 | -0.31306 | 0.006175 | -0.13376 | 0.081376 | -0.02181 | -0.027985 | -0.070454 | -0.44728 | 124.239 | 123.9191 | 124.0201 | 67.5216 | -124.1863 | 124.1994 | 124.2627 | 123.8859 | 67.5113 | -124.327
91.9062 | 124.4339 | -67.4789 | 56.8542 | 0.049183 | -0.00090066 | 0.00075378 | 0.056695 | 0.00070158 | 0.056015 | 0.049318 | -0.0016549 | 7.3343e-05 | 0.064204 | 0.0049437 | 0.062978 | -65.1219 | 0.005985 | -67.3412 | 56.7417 | 56.4173 | 56.532 | -67.3183 | -67.4159 | 0.014095 | -67.5282 | 56.6884 | 56.7517 | 56.4344 | -67.4865 | 0.16064 | -0.11252 | 2.357 | 0.13776 | -0.02288 | -0.43696 | -0.32221 | -0.007555 | -0.1658 | 0.063067 | -0.049277 | -0.041722 | -0.1025 | -0.4198 | 124.2207 | 123.8962 | 124.011 | 67.4849 | -124.1725 | 124.1674 | 124.2307 | 123.9134 | 67.493 | -124.3407
92.9062 | 124.4385 | -67.4881 | 56.8497 | 0.064445 | -0.0019697 | -0.0013822 | 0.056695 | -0.0025034 | 0.056015 | 0.064579 | -0.0027229 | -0.00099466 | 0.064204 | 0.0049437 | 0.064046 | -65.1311 | 0.010564 | -67.332 | 56.7326 | 56.4127 | 56.532 | -67.3595 | -67.4205 | 0.014095 | -67.5282 | 56.693 | 56.7609 | 56.3932 | -67.4865 | 0.12859 | -0.1171 | 2.357 | 0.15607 | 0.027486 | -0.43696 | -0.31764 | 0.0016 | -0.15665 | 0.067643 | -0.040122 | -0.041722 | -0.088764 | -0.45643 | 124.2207 | 123.9008 | 124.0201 | 67.4987 | -124.2092 | 124.1811 | 124.249 | 123.8813 | 67.5022 | -124.3362
93.9062 | 124.4568 | -67.4789 | 56.8726 | 0.049183 | -0.00090066 | 0.00075378 | 0.056695 | -0.00036642 | 0.057083 | 0.064579 | -0.0016549 | 7.3343e-05 | 0.06634 | 0.0060117 | 0.062978 | -65.1265 | 0.015142 | -67.3366 | 56.7371 | 56.4264 | 56.532 | -67.3549 | -67.4067 | 0.014095 | -67.5374 | 56.693 | 56.7655 | 56.4482 | -67.4957 | 0.12401 | -0.13541 | 2.3524 | 0.14234 | 0.018329 | -0.44611 | -0.34052 | -0.016713 | -0.17954 | 0.072224 | -0.058434 | -0.041721 | -0.10707 | -0.42438 | 124.2161 | 123.9054 | 124.011 | 67.4941 | -124.2275 | 124.172 | 124.2444 | 123.9271 | 67.493 | -124.3682
94.9062 | 124.4888 | -67.4606 | 56.8771 | 0.049183 | 0.0012363 | 0.00075378 | 0.056695 | -0.0014344 | 0.054946 | 0.095101 | -0.00058685 | -0.0031317 | 0.063135 | 0.0070807 | 0.062978 | -65.1128 | 0.015142 | -67.3366 | 56.728 | 56.4173 | 56.532 | -67.3229 | -67.4113 | 0.009516 | -67.5282 | 56.6884 | 56.7609 | 56.3291 | -67.4957 | 0.13775 | -0.14914 | 2.3478 | 0.12403 | -0.013723 | -0.45985 | -0.3451 | -0.035024 | -0.18869 | 0.049334 | -0.067588 | -0.032564 | -0.11623 | -0.548 | 124.1886 | 123.8779 | 123.9927 | 67.4758 | -124.2 | 124.1491 | 124.2215 | 123.7898 | 67.4701 | -124.3728
95.9062 | 124.4659 | -67.4606 | 56.8542 | 0.064445 | 0.00016734 | 0.00075378 | 0.057764 | -0.0014344 | 0.056015 | 0.07984 | -0.00058685 | 7.3343e-05 | 0.065272 | 0.0049437 | 0.064046 | -65.1082 | 0.0243 | -67.3412 | 56.7371 | 56.4219 | 56.532 | -67.3778 | -67.4113 | 0.014095 | -67.5236 | 56.6884 | 56.7609 | 56.4207 | -67.4957 | 0.082805 | -0.1171 | 2.3524 | 0.11945 | 0.036646 | -0.43238 | -0.32221 | -0.035024 | -0.1658 | 0.049334 | -0.063009 | -0.027985 | -0.093342 | -0.43354 | 124.1978 | 123.8825 | 123.9927 | 67.4849 | -124.2321 | 124.1491 | 124.2215 | 123.8813 | 67.4747 | -124.3499
96.9062 | 124.4614 | -67.4789 | 56.8451 | 0.064445 | 0.00016734 | 0.0018228 | 0.055627 | -0.00036642 | 0.056015 | 0.049318 | -0.0016549 | 7.3343e-05 | 0.063135 | 0.0060117 | 0.061909 | -65.1174 | 0.010564 | -67.3503 | 56.7371 | 56.4173 | 56.5366 | -67.3641 | -67.4159 | 0.009516 | -67.5236 | 56.7022 | 56.7609 | 56.3749 | -67.5048 | 0.11485 | -0.10795 | 2.3616 | 0.12861 | 0.013752 | -0.4278 | -0.30848 | -0.02587 | -0.14291 | 0.063067 | -0.044698 | -0.018828 | -0.084187 | -0.47017 | 124.2161 | 123.8962 | 124.0156 | 67.4895 | -124.2092 | 124.1811 | 124.2398 | 123.8539 | 67.4885 | -124.3499
97.9062 | 124.4705 | -67.4561 | 56.8497 | 0.064445 | 0.00016734 | -0.00031422 | 0.055627 | -0.00036642 | 0.056015 | 0.049318 | -0.00058685 | 7.3343e-05 | 0.063135 | 0.0070807 | 0.064046 | -65.1128 | 0.005985 | -67.3366 | 56.7371 | 56.4173 | 56.5275 | -67.3824 | -67.425 | 0.000359 | -67.5282 | 56.6884 | 56.7609 | 56.3887 | -67.4911 | 0.073649 | -0.11252 | 2.3433 | 0.11945 | 0.045803 | -0.43238 | -0.32221 | -0.035022 | -0.16123 | 0.031021 | -0.072165 | -0.037143 | -0.088764 | -0.46101 | 124.1932 | 123.8733 | 123.9835 | 67.462 | -124.2321 | 124.1445 | 124.217 | 123.8447 | 67.4564 | -124.3407
98.9062 | 124.4431 | -67.4698 | 56.8405 | 0.049183 | -0.0019697 | 0.0018228 | 0.055627 | -0.0014344 | 0.054946 | 0.049318 | -0.0016549 | -0.0020637 | 0.065272 | 0.0060117 | 0.064046 | -65.1036 | 0.015142 | -67.3412 | 56.7326 | 56.4219 | 56.5366 | -67.3641 | -67.4205 | 0.004938 | -67.5236 | 56.6884 | 56.7655 | 56.3841 | -67.4911 | 0.1057 | -0.10795 | 2.3662 | 0.12861 | 0.022909 | -0.41865 | -0.3039 | -0.021289 | -0.15207 | 0.049333 | -0.053853 | -0.032564 | -0.07503 | -0.45643 | 124.2024 | 123.8917 | 124.0064 | 67.4849 | -124.2046 | 124.1582 | 124.2353 | 123.8539 | 67.4747 | -124.3316
99.9062 | 124.4751 | -67.4744 | 56.8497 | 0.064445 | 0.00016734 | 0.0018228 | 0.054559 | -0.00036642 | 0.057083 | 0.064579 | -0.0016549 | -0.0020637 | 0.062067 | 0.0070807 | 0.062978 | -65.1174 | 0.015142 | -67.3412 | 56.7371 | 56.4127 | 56.532 | -67.3641 | -67.4205 | 0.004938 | -67.5328 | 56.693 | 56.7609 | 56.3978 | -67.4957 | 0.11028 | -0.11252 | 2.357 | 0.13318 | 0.022909 | -0.43696 | -0.31764 | -0.021291 | -0.15665 | 0.05391 | -0.058433 | -0.037142 | -0.088764 | -0.45185 | 124.2115 | 123.8871 | 124.0064 | 67.4895 | -124.2138 | 124.1674 | 124.2353 | 123.8722 | 67.4793 | -124.3453
100.9062 | 124.4293 | -67.4789 | 56.868 | 0.033921 | 0.0012363 | 0.00075378 | 0.054559 | -0.0025034 | 0.053878 | 0.049318 | -0.00058685 | 7.3343e-05 | 0.062067 | 0.0060117 | 0.064046 | -65.1174 | 0.010564 | -67.3458 | 56.7417 | 56.3852 | 56.532 | -67.3595 | -67.425 | 0.018674 | -67.5236 | 56.6839 | 56.7609 | 56.3612 | -67.4911 | 0.11943 | -0.12626 | 2.3616 | 0.13318 | 0.013751 | -0.48275 | -0.33595 | -0.012134 | -0.18411 | 0.053909 | -0.044698 | -0.032564 | -0.10708 | -0.50679 | 124.2207 | 123.8642 | 124.011 | 67.4895 | -124.2275 | 124.1628 | 124.2398 | 123.8401 | 67.4976 | -124.3591
101.9062 | 124.4797 | -67.4423 | 56.8314 | 0.049183 | -0.00090066 | -0.00031422 | 0.055627 | -0.0014344 | 0.057083 | 0.07984 | -0.00058685 | 7.3343e-05 | 0.063135 | 0.0060117 | 0.064046 | -65.1082 | 0.015142 | -67.3366 | 56.7509 | 56.4173 | 56.532 | -67.4099 | -67.4159 | 0.018674 | -67.5191 | 56.6884 | 56.7655 | 56.5626 | -67.4957 | 0.032443 | -0.080477 | 2.3341 | 0.10572 | 0.073276 | -0.41407 | -0.29932 | -0.053334 | -0.14292 | 0.026446 | -0.07674 | -0.023406 | -0.065875 | -0.26871 | 124.1932 | 123.8596 | 123.9744 | 67.4575 | -124.2412 | 124.1308 | 124.2078 | 124.005 | 67.461 | -124.327
102.9062 | 124.5163 | -67.4286 | 56.8634 | 0.049183 | 0.0012363 | 0.0018228 | 0.056695 | -0.0025034 | 0.054946 | 0.07984 | -0.0016549 | -0.0031317 | 0.064204 | 0.0070807 | 0.061909 | -65.099 | 0.019721 | -67.3412 | 56.7692 | 56.4631 | 56.5687 | -67.4877 | -67.4067 | 0.014095 | -67.5236 | 56.6839 | 56.7701 | 56.6634 | -67.4957 | -0.059132 | -0.094206 | 2.3295 | 0.087408 | 0.14654 | -0.40032 | -0.29474 | -0.067067 | -0.17954 | 0.02187 | -0.095052 | -0.027985 | -0.09334 | -0.20002 | 124.1978 | 123.8917 | 123.9973 | 67.4483 | -124.3511 | 124.1125 | 124.1987 | 124.092 | 67.4427 | -124.3591
103.9062 | 124.4934 | -67.4698 | 56.8497 | 0.064445 | -0.00090066 | 0.00075378 | 0.056695 | -0.0025034 | 0.054946 | 0.07984 | -0.0016549 | -0.00099466 | 0.065272 | 0.0092177 | 0.064046 | -65.1036 | 0.019721 | -67.3549 | 56.7738 | 56.486 | 56.5778 | -67.4969 | -67.4205 | 0.023253 | -67.5236 | 56.6839 | 56.7563 | 56.6863 | -67.5002 | -0.027091 | -0.075895 | 2.3662 | 0.11487 | 0.14196 | -0.3637 | -0.27185 | -0.030446 | -0.1658 | 0.049333 | -0.053853 | -0.023407 | -0.093342 | -0.1634 | 124.2436 | 123.9558 | 124.0476 | 67.4895 | -124.3465 | 124.1537 | 124.2261 | 124.1561 | 67.493 | -124.3499
104.9688 | 124.5483 | -67.4332 | 56.8314 | 0.079707 | 0.0033723 | 0.0018228 | 0.055627 | -0.0014344 | 0.053878 | 0.064579 | -0.0016549 | 7.3343e-05 | 0.064204 | 0.0081487 | 0.065114 | -65.2044 | 0.0243 | -67.3687 | 56.7829 | 56.4768 | 56.5824 | -67.5015 | -67.4205 | 0.018674 | -67.5282 | 56.6747 | 56.7563 | 56.7137 | -67.4911 | -0.068291 | -0.048428 | 2.2288 | 0.064516 | 0.13281 | -0.35455 | -0.24896 | -0.05791 | -0.15665 | 0.012712 | -0.095053 | -0.037143 | -0.075032 | -0.11762 | 124.2161 | 123.91 | 124.0156 | 67.4575 | -124.3328 | 124.1079 | 124.1895 | 124.1469 | 67.4518 | -124.3224
105.9062 | 124.4843 | -67.4423 | 56.8359 | 0.049183 | 0.0023043 | 0.0028908 | 0.054559 | -0.00036642 | 0.05281 | 0.07984 | -0.0016549 | -0.0020637 | 0.064204 | 0.0092177 | 0.061909 | -65.1036 | 0.028878 | -67.3687 | 56.7921 | 56.486 | 56.587 | -67.5244 | -67.425 | 0.027831 | -67.5191 | 56.6839 | 56.7563 | 56.7229 | -67.4911 | -0.082031 | -0.043849 | 2.3387 | 0.073671 | 0.1557 | -0.34997 | -0.24896 | -0.048755 | -0.15207 | 0.017288 | -0.07674 | -0.027985 | -0.079609 | -0.11304 | 124.2344 | 123.9283 | 124.0293 | 67.4712 | -124.3603 | 124.1262 | 124.1987 | 124.1652 | 67.4702 | -124.327
106.9688 | 124.5666 | -67.4057 | 56.8359 | 0.049183 | 0.0012363 | 0.0018228 | 0.054559 | -0.0025034 | 0.05281 | 0.064579 | -0.00058685 | -0.0041997 | 0.063135 | 0.0070807 | 0.062978 | -65.186 | 0.033457 | -67.3778 | 56.7967 | 56.4906 | 56.5916 | -67.5244 | -67.4296 | 0.03241 | -67.5328 | 56.6884 | 56.7609 | 56.7321 | -67.4911 | -0.11865 | -0.03927 | 2.2197 | 0.027893 | 0.14655 | -0.34539 | -0.24438 | -0.085376 | -0.14749 | -0.023911 | -0.1271 | -0.041721 | -0.075031 | -0.10388 | 124.2024 | 123.8963 | 123.9973 | 67.4392 | -124.3603 | 124.0941 | 124.1666 | 124.1378 | 67.4381 | -124.327
107.9062 | 124.4934 | -67.4652 | 56.868 | 0.064445 | 0.0023043 | -0.00031422 | 0.057764 | -0.0014344 | 0.053878 | 0.064579 | -0.0027229 | -0.0020637 | 0.062067 | 0.0070807 | 0.061909 | -65.1174 | 0.038035 | -67.3732 | 56.8012 | 56.5089 | 56.6053 | -67.5244 | -67.4342 | 0.023253 | -67.5191 | 56.6884 | 56.7609 | 56.7366 | -67.4957 | -0.059143 | -0.066736 | 2.3478 | 0.091981 | 0.15112 | -0.35911 | -0.26269 | -0.030446 | -0.17954 | 0.031019 | -0.053852 | -0.023406 | -0.10708 | -0.13135 | 124.2665 | 123.9741 | 124.0705 | 67.5032 | -124.3923 | 124.1537 | 124.2261 | 124.2018 | 67.4885 | -124.3636
108.9062 | 124.4614 | -67.4606 | 56.8954 | 0.064445 | 0.0023043 | 0.00075378 | 0.054559 | -0.0035714 | 0.051741 | 0.07984 | -0.0016549 | -0.0031317 | 0.059931 | 0.0060117 | 0.064046 | -65.099 | 0.0243 | -67.387 | 56.8012 | 56.518 | 56.6053 | -67.5289 | -67.4388 | 0.027831 | -67.5236 | 56.6884 | 56.7609 | 56.6634 | -67.4957 | -0.068299 | -0.094202 | 2.3616 | 0.073668 | 0.14197 | -0.37742 | -0.29015 | -0.035024 | -0.207 | 0.021862 | -0.063009 | -0.027985 | -0.13454 | -0.23207 | 124.2619 | 123.9787 | 124.0659 | 67.4849 | -124.4244 | 124.1491 | 124.2215 | 124.124 | 67.4885 | -124.3911
109.9062 | 124.4064 | -67.4469 | 56.868 | 0.064445 | 0.0044413 | 0.00075378 | 0.055627 | -0.0046394 | 0.054946 | 0.07984 | 0.00048215 | -0.0031317 | 0.062067 | 0.0070807 | 0.064046 | -65.099 | 0.010564 | -67.3366 | 56.7371 | 56.4768 | 56.5458 | -67.4465 | -67.4296 | 0.009516 | -67.5236 | 56.693 | 56.7655 | 56.6451 | -67.4957 | 0.000388 | -0.13083 | 2.3479 | 0.1103 | 0.10991 | -0.39117 | -0.32221 | -0.048757 | -0.17496 | 0.017287 | -0.076742 | -0.027985 | -0.1025 | -0.22292 | 124.184 | 123.9237 | 123.9927 | 67.4575 | -124.3145 | 124.1399 | 124.2124 | 124.092 | 67.4564 | -124.3636
110.9688 | 124.53 | -67.4377 | 56.8359 | 0.064445 | 0.00016734 | 0.00075378 | 0.054559 | -0.0014344 | 0.056015 | 0.064579 | -0.00058685 | -0.00099466 | 0.063135 | 0.0081487 | 0.062978 | -65.1815 | 0.005985 | -67.332 | 56.7371 | 56.4768 | 56.5275 | -67.4282 | -67.4021 | 0.009516 | -67.5282 | 56.6839 | 56.7472 | 56.6496 | -67.4957 | 0.009549 | -0.098789 | 2.2563 | 0.10572 | 0.09617 | -0.35912 | -0.30848 | -0.057912 | -0.15207 | 0.035604 | -0.090476 | -0.032564 | -0.088767 | -0.1863 | 124.1749 | 123.9146 | 123.9652 | 67.4437 | -124.2641 | 124.1216 | 124.1849 | 124.0874 | 67.4473 | -124.3316
111.9062 | 124.4339 | -67.4652 | 56.8817 | 0.064445 | 0.0012363 | 0.0018228 | 0.055627 | -0.0014344 | 0.054946 | 0.049318 | -0.00058685 | -0.00099466 | 0.060999 | 0.0070807 | 0.064046 | -65.0945 | 0.015142 | -67.3366 | 56.7463 | 56.4814 | 56.5366 | -67.4419 | -67.4159 | 0.014095 | -67.5236 | 56.693 | 56.7655 | 56.6542 | -67.4957 | 0.023278 | -0.13541 | 2.3707 | 0.12861 | 0.10533 | -0.40032 | -0.3451 | -0.030446 | -0.18869 | 0.049334 | -0.058431 | -0.027985 | -0.11623 | -0.22749 | 124.2115 | 123.9466 | 124.0018 | 67.4804 | -124.3236 | 124.1582 | 124.2307 | 124.1194 | 67.4793 | -124.3774
112.9062 | 124.4202 | -67.4423 | 56.9092 | 0.064445 | 0.0012363 | 0.0018228 | 0.054559 | -0.0014344 | 0.054946 | 0.07984 | -0.00058685 | -0.0020637 | 0.063135 | 0.0070807 | 0.064046 | -65.0945 | 0.010564 | -67.3458 | 56.728 | 56.4814 | 56.5366 | -67.4374 | -67.4159 | 0.004938 | -67.5236 | 56.6884 | 56.7655 | 56.6405 | -67.4865 | 0.004969 | -0.18119 | 2.3479 | 0.096562 | 0.091593 | -0.42779 | -0.37257 | -0.044176 | -0.22074 | 0.026446 | -0.081319 | -0.037143 | -0.1437 | -0.2687 | 124.1703 | 123.9237 | 123.9789 | 67.4529 | -124.3465 | 124.1308 | 124.2078 | 124.0828 | 67.4473 | -124.3957
113.9062 | 124.4568 | -67.4469 | 56.8771 | 0.064445 | 0.0023043 | 0.0018228 | 0.055627 | -0.0014344 | 0.056015 | 0.07984 | -0.00058685 | -0.0020637 | 0.063135 | 0.0081487 | 0.062978 | -65.099 | 0.010564 | -67.3549 | 56.7326 | 56.4906 | 56.5275 | -67.4419 | -67.4159 | 0.014095 | -67.5236 | 56.6884 | 56.7655 | 56.6771 | -67.4957 | 0.004967 | -0.14457 | 2.3479 | 0.091983 | 0.087016 | -0.38658 | -0.34968 | -0.048757 | -0.18869 | 0.031023 | -0.076742 | -0.027985 | -0.11165 | -0.20002 | 124.1795 | 123.9375 | 123.9744 | 67.4575 | -124.3191 | 124.1353 | 124.2124 | 124.124 | 67.461 | -124.3728
114.9219 | 124.411 | -67.4698 | 56.8405 | 0.049183 | 0.0023043 | 0.0018228 | 0.055627 | -0.0025034 | 0.053878 | 0.064579 | 0.00048215 | -0.0031317 | 0.064204 | 0.0070807 | 0.064046 | -65.099 | 0.015142 | -67.3503 | 56.7417 | 56.486 | 56.532 | -67.4419 | -67.4296 | 0.018674 | -67.5282 | 56.6884 | 56.7609 | 56.6588 | -67.4957 | 0.027856 | -0.098789 | 2.3707 | 0.11945 | 0.091594 | -0.35454 | -0.30848 | -0.025868 | -0.15207 | 0.040176 | -0.058432 | -0.032564 | -0.079609 | -0.18172 | 124.2115 | 123.9558 | 124.0018 | 67.4849 | -124.2824 | 124.1582 | 124.2307 | 124.1286 | 67.4885 | -124.3362
115.9688 | 124.5575 | -67.4561 | 56.8268 | 0.033921 | 0.0023043 | 0.00075378 | 0.055627 | -0.0025034 | 0.054946 | 0.064579 | -0.0016549 | -0.0020637 | 0.062067 | 0.0081487 | 0.064046 | -65.1723 | 0.005985 | -67.3412 | 56.7371 | 56.4768 | 56.5275 | -67.419 | -67.4205 | 0.009516 | -67.5282 | 56.6884 | 56.7563 | 56.6405 | -67.5002 | 0.037018 | -0.089634 | 2.2838 | 0.11487 | 0.077856 | -0.34997 | -0.29933 | -0.044179 | -0.13834 | 0.0356 | -0.072165 | -0.027986 | -0.070454 | -0.1863 | 124.1932 | 123.9329 | 123.9835 | 67.462 | -124.2458 | 124.1445 | 124.2124 | 124.0965 | 67.4656 | -124.327
116.9062 | 124.5209 | -67.4103 | 56.8817 | 0.064445 | 0.00016734 | 0.00075378 | 0.05349 | -0.0014344 | 0.054946 | 0.07984 | -0.00058685 | -0.0031317 | 0.063135 | 0.0081487 | 0.062978 | -65.1448 | 0.005985 | -67.3458 | 56.7417 | 56.4906 | 56.532 | -67.4374 | -67.4205 | 0.009516 | -67.5236 | 56.6839 | 56.7517 | 56.6771 | -67.4957 | -0.027075 | -0.13999 | 2.2654 | 0.064518 | 0.091593 | -0.39116 | -0.34968 | -0.085378 | -0.19785 | -0.010177 | -0.11336 | -0.027985 | -0.12997 | -0.2046 | 124.152 | 123.9008 | 123.9423 | 67.4163 | -124.3191 | 124.0941 | 124.162 | 124.0874 | 67.4198 | -124.3774
117.9688 | 124.5666 | -67.424 | 56.8222 | 0.049183 | 0.0012363 | 0.0018228 | 0.056695 | -0.00036642 | 0.054946 | 0.07984 | -0.00058685 | -0.0031317 | 0.063135 | 0.0092177 | 0.061909 | -65.1494 | 0.010564 | -67.3412 | 56.7417 | 56.4997 | 56.532 | -67.4374 | -67.4205 | 0.014095 | -67.5145 | 56.693 | 56.7609 | 56.6542 | -67.4957 | -0.013342 | -0.080479 | 2.2746 | 0.08283 | 0.096172 | -0.3225 | -0.29017 | -0.071645 | -0.12918 | 0.003556 | -0.090472 | -0.018827 | -0.061299 | -0.16798 | 124.1657 | 123.9237 | 123.956 | 67.4346 | -124.2596 | 124.117 | 124.1849 | 124.0782 | 67.4381 | -124.3179
118.9062 | 124.5529 | -67.4194 | 56.8634 | 0.049183 | 0.0012363 | 0.00075378 | 0.056695 | -0.0014344 | 0.056015 | 0.07984 | -0.0016549 | -0.00099466 | 0.063135 | 0.010286 | 0.061909 | -65.154 | 0.015142 | -67.3366 | 56.7417 | 56.5043 | 56.5412 | -67.4374 | -67.425 | 0.004938 | -67.5282 | 56.6884 | 56.7517 | 56.6405 | -67.5002 | -0.017919 | -0.12168 | 2.2654 | 0.082831 | 0.10075 | -0.35911 | -0.32221 | -0.0808 | -0.17496 | -0.0056 | -0.10879 | -0.027986 | -0.11165 | -0.22292 | 124.1612 | 123.9237 | 123.9606 | 67.4346 | -124.3008 | 124.1079 | 124.1712 | 124.0599 | 67.4244 | -124.3636
119.9219 | 124.4339 | -67.4835 | 56.8542 | 0.049183 | 0.0012363 | -0.0013822 | 0.055627 | -0.00036642 | 0.054946 | 0.049318 | -0.00058685 | -0.0020637 | 0.064204 | 0.0092177 | 0.061909 | -65.1311 | 0.019721 | -67.3366 | 56.7371 | 56.4997 | 56.5412 | -67.4374 | -67.4159 | 0.014095 | -67.5328 | 56.6839 | 56.7563 | 56.6176 | -67.4911 | 0.046168 | -0.1171 | 2.3524 | 0.14692 | 0.10075 | -0.35454 | -0.31306 | -0.007556 | -0.17038 | 0.067645 | -0.049277 | -0.041721 | -0.09792 | -0.23666 | 124.2207 | 123.9832 | 124.0247 | 67.5032 | -124.2916 | 124.1674 | 124.2398 | 124.1011 | 67.4976 | -124.3453
120.9688 | 124.5392 | -67.4469 | 56.8542 | 0.064445 | 0.0012363 | 0.0018228 | 0.054559 | -0.0014344 | 0.05281 | 0.095101 | 0.00048215 | -0.0020637 | 0.062067 | 0.0081487 | 0.061909 | -65.2044 | 0.010564 | -67.3274 | 56.7371 | 56.5043 | 56.5366 | -67.4282 | -67.4113 | 0.014095 | -67.5236 | 56.6884 | 56.7563 | 56.6359 | -67.4865 | 0.018704 | -0.1171 | 2.2425 | 0.11945 | 0.10075 | -0.34996 | -0.31763 | -0.039599 | -0.1658 | 0.035601 | -0.076742 | -0.037143 | -0.09792 | -0.21834 | 124.184 | 123.9512 | 123.9835 | 67.4575 | -124.2824 | 124.1353 | 124.2032 | 124.0828 | 67.461 | -124.3407
121.9062 | 124.5666 | -67.3828 | 56.8542 | 0.064445 | 0.00016734 | 0.00075378 | 0.055627 | -0.0035714 | 0.054946 | 0.064579 | -0.0027229 | -0.0020637 | 0.064204 | 0.010286 | 0.060841 | -65.1723 | 0.010564 | -67.332 | 56.7417 | 56.5043 | 56.5366 | -67.4236 | -67.4159 | 0.009516 | -67.5191 | 56.693 | 56.7563 | 56.6634 | -67.4911 | -0.040804 | -0.11252 | 2.2105 | 0.050787 | 0.091591 | -0.34996 | -0.31763 | -0.10827 | -0.16123 | -0.033064 | -0.13625 | -0.027985 | -0.09792 | -0.19087 | 124.1245 | 123.8871 | 123.9194 | 67.3934 | -124.2779 | 124.0758 | 124.1391 | 124.0462 | 67.3923 | -124.3453
122.9688 | 124.4339 | -67.4423 | 56.8405 | 0.049183 | 0.0023043 | 0.0018228 | 0.05349 | -0.0014344 | 0.053878 | 0.049318 | -0.0016549 | 7.3343e-05 | 0.063135 | 0.0092177 | 0.062978 | -65.154 | 0.015142 | -67.3229 | 56.7371 | 56.5043 | 56.5458 | -67.4374 | -67.4067 | 0.009516 | -67.5191 | 56.6884 | 56.7609 | 56.6542 | -67.4865 | 0.004969 | -0.10337 | 2.2883 | 0.11945 | 0.11449 | -0.33623 | -0.29475 | -0.044176 | -0.15207 | 0.035603 | -0.07674 | -0.032564 | -0.079609 | -0.18629 | 124.1795 | 123.9466 | 123.9881 | 67.4575 | -124.2779 | 124.1308 | 124.2032 | 124.0965 | 67.4518 | -124.327
123.9062 | 124.5621 | -67.4469 | 56.8359 | 0.064445 | 0.00016734 | 0.00075378 | 0.05349 | -0.0014344 | 0.054946 | 0.064579 | -0.00058685 | -0.0020637 | 0.063135 | 0.011354 | 0.062978 | -65.2227 | 0.010564 | -67.3274 | 56.7326 | 56.5043 | 56.5366 | -67.4328 | -67.4113 | 0.004938 | -67.5236 | 56.6884 | 56.7609 | 56.6267 | -67.4911 | 0.014125 | -0.10337 | 2.2242 | 0.11945 | 0.10533 | -0.33165 | -0.29932 | -0.044178 | -0.14749 | 0.035601 | -0.076742 | -0.032564 | -0.075031 | -0.20919 | 124.1795 | 123.9512 | 123.9835 | 67.4575 | -124.2687 | 124.1353 | 124.2078 | 124.0736 | 67.4518 | -124.327
124.9219 | 124.4568 | -67.4561 | 56.8817 | 0.049183 | 0.0012363 | 0.0018228 | 0.054559 | -0.00036642 | 0.054946 | 0.07984 | -0.00058685 | -0.0020637 | 0.063135 | 0.011354 | 0.061909 | -65.1311 | 0.010564 | -67.3366 | 56.7417 | 56.518 | 56.5366 | -67.4419 | -67.4113 | 0.018674 | -67.5191 | 56.6839 | 56.7563 | 56.6359 | -67.4957 | 0.014123 | -0.13999 | 2.325 | 0.11945 | 0.10533 | -0.36369 | -0.3451 | -0.039601 | -0.19785 | 0.044757 | -0.063007 | -0.023406 | -0.12539 | -0.24581 | 124.1978 | 123.9741 | 123.9927 | 67.4666 | -124.3236 | 124.1399 | 124.2124 | 124.092 | 67.4747 | -124.3774
125.9688 | 124.4659 | -67.4469 | 56.8222 | 0.064445 | 0.0012363 | 0.0028908 | 0.054559 | -0.0025034 | 0.053878 | 0.049318 | -0.00058685 | -0.0020637 | 0.062067 | 0.010286 | 0.061909 | -65.1677 | 0.010564 | -67.332 | 56.728 | 56.5089 | 56.532 | -67.4419 | -67.4067 | 0.009516 | -67.5145 | 56.6793 | 56.7609 | 56.6542 | -67.4911 | 0.004967 | -0.094214 | 2.2792 | 0.11487 | 0.10991 | -0.31334 | -0.29017 | -0.044178 | -0.14292 | 0.04018 | -0.067584 | -0.023406 | -0.061299 | -0.16798 | 124.1749 | 123.9558 | 123.9789 | 67.4575 | -124.2641 | 124.1262 | 124.2078 | 124.1011 | 67.4564 | -124.3133
126.9062 | 124.5575 | -67.4377 | 56.8314 | 0.079707 | 0.0023043 | 0.0028908 | 0.055627 | -0.0025034 | 0.054946 | 0.07984 | -0.0016549 | -0.00099466 | 0.063135 | 0.0092177 | 0.061909 | -65.2364 | 0.005985 | -67.332 | 56.7371 | 56.5134 | 56.5366 | -67.4328 | -67.4113 | 0.009516 | -67.5236 | 56.693 | 56.7563 | 56.6451 | -67.5002 | 0.00497 | -0.094212 | 2.2013 | 0.10572 | 0.10075 | -0.31791 | -0.29475 | -0.06249 | -0.13834 | 0.026446 | -0.085897 | -0.023407 | -0.075032 | -0.1863 | 124.1749 | 123.9512 | 123.9744 | 67.4437 | -124.2641 | 124.1308 | 124.1941 | 124.0828 | 67.4473 | -124.3316
127.9062 | 124.5346 | -67.4057 | 56.8314 | 0.064445 | 0.0012363 | 0.00075378 | 0.05349 | -0.00036642 | 0.054946 | 0.095101 | 0.00048215 | -0.00099466 | 0.063135 | 0.011354 | 0.062978 | -65.2318 | 0.005985 | -67.3274 | 56.7371 | 56.5089 | 56.5412 | -67.4328 | -67.4021 | 0.009516 | -67.5191 | 56.6839 | 56.7609 | 56.6313 | -67.4911 | -0.027073 | -0.094212 | 2.1739 | 0.078255 | 0.10533 | -0.32249 | -0.29017 | -0.085376 | -0.14749 | 0.003561 | -0.11336 | -0.027985 | -0.070454 | -0.20003 | 124.1428 | 123.9146 | 123.9469 | 67.4117 | -124.2641 | 124.0896 | 124.1666 | 124.037 | 67.4152 | -124.3224
128.9062 | 124.5575 | -67.4103 | 56.8405 | 0.079707 | 0.00016734 | 0.0018228 | 0.05349 | -0.0014344 | 0.054946 | 0.07984 | -0.0016549 | -0.0020637 | 0.060999 | 0.0092177 | 0.062978 | -65.2364 | 0.001407 | -67.3274 | 56.7326 | 56.4997 | 56.532 | -67.4374 | -67.4067 | 0.004938 | -67.5191 | 56.6884 | 56.7517 | 56.6176 | -67.4911 | -0.027075 | -0.10795 | 2.1739 | 0.082832 | 0.10991 | -0.34081 | -0.30848 | -0.080799 | -0.15207 | 0.003559 | -0.10878 | -0.027985 | -0.088766 | -0.22292 | 124.1428 | 123.91 | 123.9423 | 67.4117 | -124.2779 | 124.0987 | 124.162 | 124.0279 | 67.4152 | -124.3316
129.9219 | 124.498 | -67.4423 | 56.8909 | 0.079707 | 0.0012363 | 0.00075378 | 0.054559 | -0.0014344 | 0.053878 | 0.064579 | 0.00048215 | -0.00099466 | 0.060999 | 0.010286 | 0.061909 | -65.1265 | 0.005985 | -67.3366 | 56.7371 | 56.518 | 56.532 | -67.4419 | -67.4067 | 0.014095 | -67.5191 | 56.693 | 56.7563 | 56.6359 | -67.4957 | 0.00039 | -0.15372 | 2.3158 | 0.10572 | 0.10533 | -0.37284 | -0.35883 | -0.053334 | -0.19785 | 0.035603 | -0.07674 | -0.023406 | -0.13454 | -0.25496 | 124.1795 | 123.9603 | 123.9744 | 67.4483 | -124.3328 | 124.1353 | 124.1987 | 124.0782 | 67.4564 | -124.3865
130.9062 | 124.53 | -67.424 | 56.8314 | 0.018659 | 0.00016734 | 0.00075378 | 0.05349 | -0.00036642 | 0.056015 | 0.064579 | -0.0016549 | 0.0011413 | 0.064204 | 0.010286 | 0.064046 | -65.2227 | 0.005985 | -67.3274 | 56.7326 | 56.4997 | 56.532 | -67.4282 | -67.4067 | 0.004938 | -67.5191 | 56.6839 | 56.7655 | 56.6405 | -67.4957 | -0.004184 | -0.098791 | 2.2013 | 0.096565 | 0.10075 | -0.33165 | -0.29932 | -0.071645 | -0.14749 | 0.017292 | -0.095051 | -0.023406 | -0.065875 | -0.19087 | 124.1566 | 123.9237 | 123.956 | 67.43 | -124.2596 | 124.1079 | 124.1895 | 124.0645 | 67.4289 | -124.327
131.9062 | 124.53 | -67.4149 | 56.8268 | 0.049183 | 0.00016734 | 0.0018228 | 0.054559 | -0.0025034 | 0.054946 | 0.049318 | -0.0016549 | -0.0020637 | 0.062067 | 0.0092177 | 0.064046 | -65.2318 | 0.005985 | -67.332 | 56.7371 | 56.4997 | 56.532 | -67.4419 | -67.4113 | 0.014095 | -67.5145 | 56.6884 | 56.7517 | 56.613 | -67.4957 | -0.027076 | -0.089634 | 2.183 | 0.082831 | 0.10991 | -0.32707 | -0.29475 | -0.0808 | -0.13834 | 0.003558 | -0.099627 | -0.018827 | -0.075033 | -0.21377 | 124.152 | 123.9146 | 123.9469 | 67.4208 | -124.2687 | 124.1033 | 124.1666 | 124.0279 | 67.429 | -124.3224
132.9688 | 124.4888 | -67.4332 | 56.8497 | 0.033921 | 0.0012363 | 0.00075378 | 0.055627 | -0.0025034 | 0.053878 | 0.07984 | -0.0016549 | -0.0031317 | 0.064204 | 0.010286 | 0.061909 | -65.1174 | 0.010564 | -67.332 | 56.7371 | 56.5043 | 56.532 | -67.4328 | -67.4205 | 0.009516 | -67.5191 | 56.6839 | 56.7609 | 56.6176 | -67.4957 | 0.000393 | -0.11252 | 2.3158 | 0.10114 | 0.10075 | -0.34538 | -0.31764 | -0.062489 | -0.1658 | 0.012712 | -0.085895 | -0.023406 | -0.088764 | -0.23208 | 124.1703 | 123.9375 | 123.9652 | 67.4437 | -124.2824 | 124.117 | 124.1941 | 124.0508 | 67.4427 | -124.3453
133.9062 | 124.498 | -67.4194 | 56.8451 | 0.049183 | 0.0023043 | 0.0028908 | 0.054559 | -0.0014344 | 0.053878 | 0.07984 | -0.00058685 | -0.0020637 | 0.062067 | 0.011354 | 0.062978 | -65.2272 | 0.010564 | -67.3274 | 56.728 | 56.4997 | 56.5412 | -67.4374 | -67.4113 | 0.009516 | -67.5236 | 56.6839 | 56.7517 | 56.6267 | -67.4911 | -0.017919 | -0.1171 | 2.1922 | 0.091988 | 0.10991 | -0.34538 | -0.3039 | -0.071643 | -0.16123 | 0.008136 | -0.10421 | -0.032564 | -0.093344 | -0.21834 | 124.1474 | 123.9191 | 123.9606 | 67.43 | -124.2824 | 124.1033 | 124.1712 | 124.0462 | 67.429 | -124.3362
134.9219 | 124.4934 | -67.4332 | 56.8588 | 0.064445 | 0.0012363 | -0.00031422 | 0.054559 | -0.0025034 | 0.054946 | 0.064579 | -0.0016549 | -0.0020637 | 0.062067 | 0.012423 | 0.061909 | -65.1082 | 0.005985 | -67.3366 | 56.7371 | 56.4997 | 56.5412 | -67.4419 | -67.4205 | 0.009516 | -67.5236 | 56.6884 | 56.7563 | 56.6084 | -67.4957 | -0.008765 | -0.12168 | 2.325 | 0.096564 | 0.10533 | -0.35912 | -0.31763 | -0.062489 | -0.17038 | 0.012712 | -0.090474 | -0.027985 | -0.1025 | -0.25039 | 124.1703 | 123.9329 | 123.9744 | 67.4392 | -124.3008 | 124.1216 | 124.1895 | 124.0416 | 67.4427 | -124.3545
135.9688 | 124.4385 | -67.4652 | 56.8542 | 0.033921 | 0.0012363 | -0.00031422 | 0.054559 | -0.0014344 | 0.054946 | 0.049318 | -0.0027229 | 7.3343e-05 | 0.064204 | 0.010286 | 0.059773 | -65.1311 | 0.005985 | -67.332 | 56.7326 | 56.4951 | 56.532 | -67.4236 | -67.4159 | 0.009516 | -67.5191 | 56.6839 | 56.7563 | 56.6222 | -67.4957 | 0.041594 | -0.12168 | 2.3341 | 0.13318 | 0.091591 | -0.35912 | -0.32221 | -0.030446 | -0.17038 | 0.049334 | -0.053852 | -0.023406 | -0.09792 | -0.23208 | 124.1978 | 123.9603 | 123.9972 | 67.4712 | -124.2779 | 124.1491 | 124.2215 | 124.0874 | 67.4747 | -124.3499
136.9062 | 124.498 | -67.4286 | 56.8268 | 0.064445 | 0.00016734 | 0.00075378 | 0.054559 | -0.0025034 | 0.056015 | 0.064579 | -0.0016549 | -0.0031317 | 0.064204 | 0.011354 | 0.059773 | -65.1952 | -0.003172 | -67.332 | 56.728 | 56.4997 | 56.5366 | -67.4236 | -67.4067 | 0.004938 | -67.5145 | 56.6884 | 56.7655 | 56.6039 | -67.4957 | 0.004973 | -0.098791 | 2.2334 | 0.096564 | 0.091591 | -0.32707 | -0.29017 | -0.067067 | -0.13834 | 0.02187 | -0.085894 | -0.018827 | -0.061297 | -0.22293 | 124.1566 | 123.9283 | 123.9652 | 67.4254 | -124.2504 | 124.117 | 124.1941 | 124.0324 | 67.4335 | -124.3224
137.9062 | 124.5255 | -67.4469 | 56.8497 | 0.064445 | 0.0012363 | 0.00075378 | 0.05349 | -0.00036642 | 0.054946 | 0.064579 | -0.00058685 | -0.0020637 | 0.063135 | 0.011354 | 0.061909 | -65.1952 | 0.005985 | -67.3274 | 56.7371 | 56.4951 | 56.5366 | -67.4328 | -67.4113 | 0.009516 | -67.5145 | 56.6839 | 56.7517 | 56.6496 | -67.5002 | 0.014125 | -0.11252 | 2.2517 | 0.11945 | 0.10533 | -0.35454 | -0.31306 | -0.053335 | -0.1658 | 0.035601 | -0.067584 | -0.014249 | -0.097921 | -0.20003 | 124.184 | 123.942 | 123.9835 | 67.4529 | -124.2824 | 124.1308 | 124.1986 | 124.0965 | 67.4564 | -124.3499
138.9062 | 124.498 | -67.4011 | 56.8405 | 0.049183 | 0.0033723 | 0.0018228 | 0.054559 | -0.0025034 | 0.053878 | 0.07984 | -0.00058685 | -0.0020637 | 0.063135 | 0.010286 | 0.062978 | -65.1998 | 0.010564 | -67.332 | 56.7326 | 56.4997 | 56.5366 | -67.4374 | -67.4159 | 0.009516 | -67.5191 | 56.6884 | 56.7517 | 56.613 | -67.4957 | -0.03623 | -0.10795 | 2.2013 | 0.069098 | 0.10533 | -0.34081 | -0.3039 | -0.094533 | -0.15207 | -0.014753 | -0.11794 | -0.023406 | -0.088766 | -0.2275 | 124.1337 | 123.9008 | 123.9377 | 67.4117 | -124.2779 | 124.0896 | 124.1529 | 124.0141 | 67.4106 | -124.3362
139.9062 | 124.4888 | -67.4103 | 56.8405 | 0.049183 | 0.0012363 | 0.00075378 | 0.055627 | -0.00036642 | 0.054946 | 0.064579 | -0.0027229 | -0.00099466 | 0.064204 | 0.013491 | 0.062978 | -65.1952 | 0.005985 | -67.3458 | 56.7326 | 56.4997 | 56.5412 | -67.4374 | -67.4113 | 0.000359 | -67.5145 | 56.6793 | 56.7563 | 56.6084 | -67.5002 | -0.027075 | -0.10795 | 2.2151 | 0.064518 | 0.091593 | -0.34081 | -0.29932 | -0.089956 | -0.16123 | -0.00102 | -0.1042 | -0.014249 | -0.084187 | -0.23208 | 124.1428 | 123.91 | 123.9515 | 67.4163 | -124.2779 | 124.0896 | 124.1666 | 124.0187 | 67.4106 | -124.3407
140.9062 | 124.5117 | -67.4149 | 56.8542 | 0.049183 | 0.0023043 | 0.0018228 | 0.055627 | -0.0025034 | 0.054946 | 0.07984 | -0.0016549 | -0.0020637 | 0.062067 | 0.0092177 | 0.060841 | -65.1906 | 0.001407 | -67.332 | 56.7371 | 56.4997 | 56.5366 | -67.4374 | -67.4113 | 0.004938 | -67.5145 | 56.6884 | 56.7609 | 56.6084 | -67.5048 | -0.022497 | -0.1171 | 2.2242 | 0.082831 | 0.10533 | -0.35454 | -0.31763 | -0.089957 | -0.1658 | 0.003558 | -0.099627 | -0.00967 | -0.093342 | -0.24581 | 124.152 | 123.9146 | 123.9515 | 67.4163 | -124.2916 | 124.1033 | 124.1758 | 124.0233 | 67.4198 | -124.3591
141.9062 | 124.5071 | -67.4103 | 56.8405 | 0.049183 | 0.0012363 | 0.0018228 | 0.054559 | -0.0025034 | 0.056015 | 0.064579 | -0.0027229 | -0.0031317 | 0.063135 | 0.010286 | 0.061909 | -65.2044 | 0.005985 | -67.3366 | 56.7371 | 56.4906 | 56.5366 | -67.4419 | -67.4159 | 0.009516 | -67.5191 | 56.693 | 56.7655 | 56.6405 | -67.4911 | -0.031654 | -0.10337 | 2.2059 | 0.073675 | 0.10533 | -0.34996 | -0.3039 | -0.080799 | -0.14749 | -0.005598 | -0.10878 | -0.027985 | -0.07503 | -0.20003 | 124.1474 | 123.9008 | 123.9469 | 67.4163 | -124.2824 | 124.1033 | 124.1758 | 124.0508 | 67.4198 | -124.3316
142.9062 | 124.5255 | -67.4423 | 56.8176 | 0.049183 | 0.0023043 | 0.0018228 | 0.054559 | -0.0035714 | 0.054946 | 0.064579 | -0.0027229 | -0.00099466 | 0.063135 | 0.011354 | 0.062978 | -65.1998 | 0.001407 | -67.332 | 56.7371 | 56.4906 | 56.5366 | -67.4465 | -67.4067 | 0.004938 | -67.5145 | 56.6793 | 56.7655 | 56.6451 | -67.4911 | -0.004189 | -0.080479 | 2.2425 | 0.1103 | 0.11449 | -0.32708 | -0.28101 | -0.048755 | -0.13834 | 0.035603 | -0.072161 | -0.023406 | -0.052142 | -0.17256 | 124.1795 | 123.9329 | 123.9789 | 67.4437 | -124.2641 | 124.1216 | 124.2078 | 124.0874 | 67.4473 | -124.3087
143.9062 | 124.5483 | -67.4515 | 56.8451 | 0.064445 | 0.0012363 | 0.0018228 | 0.05349 | -0.0025034 | 0.053878 | 0.064579 | -0.0027229 | -0.00099466 | 0.062067 | 0.013491 | 0.060841 | -65.186 | 0.010564 | -67.332 | 56.7371 | 56.486 | 56.5412 | -67.4282 | -67.4113 | 0.004938 | -67.5145 | 56.6884 | 56.7609 | 56.6176 | -67.4911 | 0.023282 | -0.10795 | 2.2654 | 0.11945 | 0.09617 | -0.35912 | -0.3039 | -0.0396 | -0.15665 | 0.040179 | -0.063006 | -0.023406 | -0.084187 | -0.2275 | 124.1886 | 123.9374 | 123.9927 | 67.462 | -124.2733 | 124.1399 | 124.2124 | 124.0691 | 67.4564 | -124.3362
144.9062 | 124.5346 | -67.424 | 56.8497 | 0.079707 | 0.0023043 | 0.0018228 | 0.054559 | -0.0014344 | 0.05281 | 0.049318 | -0.00058685 | -0.0031317 | 0.062067 | 0.012423 | 0.059773 | -65.1769 | 0.001407 | -67.3366 | 56.7326 | 56.486 | 56.5412 | -67.4328 | -67.4067 | 0.004938 | -67.5191 | 56.6839 | 56.7563 | 56.613 | -67.5002 | -0.008763 | -0.1171 | 2.2471 | 0.087408 | 0.096171 | -0.3637 | -0.30848 | -0.076223 | -0.1658 | 0.017292 | -0.095051 | -0.018828 | -0.093342 | -0.23666 | 124.1566 | 123.91 | 123.9652 | 67.4254 | -124.2824 | 124.1079 | 124.1803 | 124.037 | 67.4289 | -124.3499
145.9062 | 124.5255 | -67.4286 | 56.8451 | 0.064445 | 0.00016734 | -0.00031422 | 0.054559 | -0.0014344 | 0.054946 | 0.049318 | -0.0016549 | -0.0031317 | 0.062067 | 0.013491 | 0.062978 | -65.1906 | 0.005985 | -67.3412 | 56.728 | 56.4814 | 56.5366 | -67.4236 | -67.4113 | 0.000359 | -67.5099 | 56.6839 | 56.7563 | 56.6039 | -67.4957 | 0.004973 | -0.1171 | 2.238 | 0.087408 | 0.082435 | -0.3637 | -0.30848 | -0.067067 | -0.16123 | 0.017291 | -0.081316 | -0.014249 | -0.088765 | -0.24124 | 124.1566 | 123.91 | 123.9652 | 67.4346 | -124.2687 | 124.1125 | 124.1849 | 124.0324 | 67.4289 | -124.3407
146.9688 | 124.4247 | -67.4652 | 56.8405 | 0.049183 | 0.00016734 | 0.0018228 | 0.056695 | -0.0046394 | 0.053878 | 0.095101 | -0.0016549 | -0.0041997 | 0.062067 | 0.012423 | 0.062978 | -65.099 | 0.005985 | -67.3366 | 56.7371 | 56.486 | 56.5366 | -67.4419 | -67.4159 | 0.014095 | -67.5191 | 56.6839 | 56.7563 | 56.6588 | -67.4957 | 0.023278 | -0.10337 | 2.3662 | 0.12861 | 0.10533 | -0.35454 | -0.3039 | -0.030446 | -0.15665 | 0.049334 | -0.053852 | -0.023406 | -0.084187 | -0.18172 | 124.2024 | 123.9512 | 124.0018 | 67.4712 | -124.2824 | 124.1491 | 124.2215 | 124.124 | 67.4793 | -124.3362
147.9062 | 124.498 | -67.424 | 56.8314 | 0.033921 | 0.0012363 | 0.00075378 | 0.05349 | -0.0025034 | 0.054946 | 0.064579 | -0.00058685 | -0.0020637 | 0.062067 | 0.012423 | 0.060841 | -65.1815 | 0.005985 | -67.3412 | 56.7326 | 56.4768 | 56.5412 | -67.4328 | -67.4113 | 0.014095 | -67.5099 | 56.6884 | 56.7563 | 56.6496 | -67.4957 | -0.008763 | -0.098791 | 2.2426 | 0.08283 | 0.091593 | -0.35455 | -0.29017 | -0.071645 | -0.14292 | 0.012713 | -0.085894 | -0.014249 | -0.075032 | -0.18172 | 124.1566 | 123.9008 | 123.9652 | 67.43 | -124.2641 | 124.1125 | 124.1803 | 124.0737 | 67.4381 | -124.327
148.9062 | 124.5255 | -67.4286 | 56.8451 | 0.049183 | 0.00016734 | 0.00075378 | 0.054559 | -0.0025034 | 0.053878 | 0.034057 | -0.0016549 | -0.0031317 | 0.064204 | 0.010286 | 0.062978 | -65.1815 | -0.003172 | -67.3503 | 56.7371 | 56.4814 | 56.5366 | -67.4511 | -67.4159 | 0.009516 | -67.5236 | 56.6793 | 56.7517 | 56.6496 | -67.4911 | -0.022501 | -0.10795 | 2.2471 | 0.078251 | 0.10075 | -0.3637 | -0.30848 | -0.062488 | -0.16581 | 0.012713 | -0.095052 | -0.032564 | -0.093344 | -0.19545 | 124.1657 | 123.91 | 123.9652 | 67.4254 | -124.2962 | 124.1079 | 124.1803 | 124.0782 | 67.4381 | -124.3362
149.9062 | 124.5346 | -67.424 | 56.8497 | 0.079707 | 0.0023043 | 0.00075378 | 0.054559 | -0.0035714 | 0.05281 | 0.11036 | -0.00058685 | -0.0031317 | 0.063135 | 0.013491 | 0.064046 | -65.1769 | 0.001407 | -67.3412 | 56.7371 | 56.4814 | 56.5366 | -67.4282 | -67.4021 | 0.004938 | -67.5145 | 56.6839 | 56.7609 | 56.6725 | -67.4957 | -0.004184 | -0.11252 | 2.2471 | 0.08283 | 0.087014 | -0.36828 | -0.31306 | -0.071645 | -0.1658 | 0.021871 | -0.090472 | -0.018827 | -0.088764 | -0.17713 | 124.1612 | 123.9054 | 123.9606 | 67.4254 | -124.2779 | 124.1079 | 124.1849 | 124.0965 | 67.4289 | -124.3453
150.9062 | 124.4888 | -67.4194 | 56.8405 | 0.049183 | 0.0012363 | 0.0018228 | 0.054559 | -0.0046394 | 0.053878 | 0.07984 | -0.0016549 | -0.0031317 | 0.063135 | 0.011354 | 0.062978 | -65.1769 | -0.003172 | -67.3412 | 56.7234 | 56.4768 | 56.5412 | -67.4282 | -67.4113 | 0.004938 | -67.5145 | 56.6884 | 56.7517 | 56.6451 | -67.4957 | -0.008761 | -0.1171 | 2.2426 | 0.078253 | 0.087014 | -0.3637 | -0.29932 | -0.076222 | -0.15207 | 0.008136 | -0.095049 | -0.018827 | -0.088766 | -0.19545 | 124.1428 | 123.8962 | 123.9606 | 67.4163 | -124.2687 | 124.1079 | 124.1712 | 124.0645 | 67.4244 | -124.3362
151.9062 | 124.5438 | -67.4194 | 56.8039 | 0.064445 | 0.0023043 | 0.0018228 | 0.054559 | -0.0025034 | 0.056015 | 0.064579 | -0.0016549 | -0.0020637 | 0.060999 | 0.013491 | 0.060841 | -65.1631 | 0.010564 | -67.3412 | 56.7326 | 56.4814 | 56.532 | -67.4236 | -67.4113 | 0.004938 | -67.5099 | 56.6839 | 56.7609 | 56.6359 | -67.4865 | -0.004182 | -0.071325 | 2.2563 | 0.078253 | 0.082435 | -0.3225 | -0.27186 | -0.067064 | -0.12003 | 0.008136 | -0.090471 | -0.023407 | -0.042988 | -0.16799 | 124.152 | 123.9008 | 123.9515 | 67.43 | -124.2275 | 124.1033 | 124.1803 | 124.0553 | 67.4244 | -124.2904
152.9688 | 124.4614 | -67.4377 | 56.8634 | 0.049183 | 0.0012363 | 0.0018228 | 0.055627 | -0.0035714 | 0.053878 | 0.064579 | -0.00058685 | -0.0020637 | 0.060999 | 0.011354 | 0.061909 | -65.0807 | 0.005985 | -67.3503 | 56.7417 | 56.4768 | 56.5412 | -67.4374 | -67.4067 | 0.004938 | -67.5099 | 56.6839 | 56.7609 | 56.6634 | -67.5002 | 0.000391 | -0.12168 | 2.357 | 0.087406 | 0.087015 | -0.38659 | -0.32221 | -0.06249 | -0.17954 | 0.031025 | -0.072161 | -0.009671 | -0.1025 | -0.20002 | 124.1795 | 123.9146 | 123.9789 | 67.4437 | -124.3008 | 124.1216 | 124.1986 | 124.1011 | 67.4427 | -124.3636
153.9062 | 124.498 | -67.4332 | 56.813 | 0.049183 | 0.0023043 | 0.0028908 | 0.055627 | -0.00036642 | 0.054946 | 0.064579 | -0.00058685 | -0.0041997 | 0.062067 | 0.012423 | 0.060841 | -65.1723 | 0.005985 | -67.3458 | 56.7326 | 56.4677 | 56.5366 | -67.4419 | -67.4067 | 0.004938 | -67.5145 | 56.6839 | 56.7563 | 56.6496 | -67.5002 | -0.008765 | -0.08048 | 2.2609 | 0.087407 | 0.096172 | -0.34539 | -0.27644 | -0.067067 | -0.12918 | 0.026448 | -0.081316 | -0.014249 | -0.056721 | -0.16341 | 124.1657 | 123.9008 | 123.9698 | 67.4392 | -124.255 | 124.117 | 124.1895 | 124.0828 | 67.4381 | -124.3133
154.9688 | 124.4843 | -67.4286 | 56.8588 | 0.079707 | 0.0023043 | 0.0028908 | 0.055627 | -0.0035714 | 0.056015 | 0.064579 | -0.0027229 | -0.0041997 | 0.062067 | 0.013491 | 0.061909 | -65.0807 | 0.001407 | -67.3412 | 56.7417 | 56.4722 | 56.5366 | -67.4374 | -67.4021 | 0.009516 | -67.5099 | 56.6884 | 56.7655 | 56.6405 | -67.4911 | -0.008764 | -0.1171 | 2.3479 | 0.087408 | 0.096172 | -0.38659 | -0.32221 | -0.062488 | -0.17038 | 0.026449 | -0.081316 | -0.018828 | -0.093341 | -0.21834 | 124.1703 | 123.9008 | 123.9652 | 67.43 | -124.2962 | 124.117 | 124.1941 | 124.0691 | 67.4381 | -124.3499
155.9062 | 124.4797 | -67.424 | 56.8359 | 0.049183 | 0.0033723 | 0.00075378 | 0.054559 | -0.0014344 | 0.053878 | 0.07984 | -0.0027229 | -0.0041997 | 0.063135 | 0.012423 | 0.061909 | -65.1815 | -0.007751 | -67.3366 | 56.728 | 56.4768 | 56.5412 | -67.4328 | -67.4067 | 0.004938 | -67.5145 | 56.6839 | 56.7609 | 56.6634 | -67.4911 | -0.008763 | -0.10795 | 2.2426 | 0.087408 | 0.096171 | -0.35912 | -0.29474 | -0.067066 | -0.15207 | 0.017292 | -0.090472 | -0.023406 | -0.075031 | -0.17256 | 124.152 | 123.9008 | 123.9652 | 67.4163 | -124.2687 | 124.1079 | 124.1849 | 124.0874 | 67.4289 | -124.327
156.9688 | 124.4293 | -67.4194 | 56.8771 | 0.064445 | 0.0012363 | 0.0018228 | 0.055627 | -0.0035714 | 0.051741 | 0.07984 | -0.00058685 | -0.0041997 | 0.062067 | 0.014559 | 0.060841 | -65.0899 | 0.001407 | -67.3503 | 56.7326 | 56.4814 | 56.5412 | -67.4419 | -67.4067 | 0.000359 | -67.5145 | 56.6793 | 56.7701 | 56.6359 | -67.4957 | -0.022498 | -0.14457 | 2.3295 | 0.069096 | 0.091594 | -0.39574 | -0.33594 | -0.076222 | -0.19785 | 0.012715 | -0.095049 | -0.018827 | -0.10707 | -0.24123 | 124.152 | 123.9008 | 123.9606 | 67.4208 | -124.3191 | 124.0987 | 124.1895 | 124.0553 | 67.4198 | -124.3728
157.9062 | 124.5483 | -67.4011 | 56.8268 | 0.064445 | 0.0012363 | 0.00075378 | 0.054559 | -0.0025034 | 0.05281 | 0.049318 | -0.0016549 | -0.0031317 | 0.063135 | 0.013491 | 0.062978 | -65.1631 | 0.001407 | -67.3503 | 56.728 | 56.4814 | 56.5366 | -67.4328 | -67.4067 | 0.004938 | -67.5099 | 56.6747 | 56.7609 | 56.6267 | -67.5002 | -0.031651 | -0.098791 | 2.238 | 0.050785 | 0.082436 | -0.34539 | -0.29017 | -0.099111 | -0.15207 | -0.005596 | -0.10878 | -0.009671 | -0.065876 | -0.20003 | 124.1291 | 123.8825 | 123.9377 | 67.4025 | -124.2596 | 124.0758 | 124.162 | 124.0279 | 67.4061 | -124.327
158.9688 | 124.4659 | -67.4286 | 56.8542 | 0.064445 | 0.0023043 | 0.0018228 | 0.054559 | -0.0025034 | 0.054946 | 0.049318 | -0.0027229 | -0.0052687 | 0.060999 | 0.013491 | 0.061909 | -65.0853 | -0.007751 | -67.3412 | 56.7371 | 56.4814 | 56.5412 | -67.4374 | -67.4113 | 0.000359 | -67.5099 | 56.6839 | 56.7563 | 56.6634 | -67.5002 | -0.008764 | -0.1171 | 2.3433 | 0.087408 | 0.096172 | -0.37286 | -0.31306 | -0.071645 | -0.17038 | 0.017291 | -0.081316 | -0.009671 | -0.09792 | -0.19087 | 124.1657 | 123.91 | 123.9698 | 67.4208 | -124.2916 | 124.1125 | 124.1849 | 124.092 | 67.4289 | -124.3545
159.9062 | 124.4934 | -67.4286 | 56.8176 | 0.049183 | 0.0023043 | 0.00075378 | 0.056695 | -0.0035714 | 0.056015 | 0.064579 | -0.00058685 | -0.0041997 | 0.062067 | 0.013491 | 0.060841 | -65.1631 | -0.007751 | -67.3458 | 56.7326 | 56.4768 | 56.5366 | -67.4328 | -67.4113 | 0.004938 | -67.5099 | 56.6839 | 56.7563 | 56.6588 | -67.4957 | -0.004185 | -0.085058 | 2.2654 | 0.082829 | 0.087014 | -0.34081 | -0.28101 | -0.067067 | -0.13376 | 0.017291 | -0.081316 | -0.014249 | -0.061299 | -0.15883 | 124.1612 | 123.9054 | 123.9652 | 67.4208 | -124.2504 | 124.1125 | 124.1849 | 124.0874 | 67.4335 | -124.3133
160.9688 | 124.4751 | -67.4469 | 56.8634 | 0.064445 | 0.0012363 | 0.0018228 | 0.055627 | -0.0035714 | 0.05281 | 0.064579 | -0.0016549 | -0.0041997 | 0.062067 | 0.014559 | 0.061909 | -65.0807 | -0.003172 | -67.3503 | 56.7326 | 56.4768 | 56.5412 | -67.4282 | -67.4021 | 0.000359 | -67.5053 | 56.6747 | 56.7517 | 56.6496 | -67.5048 | 0.018704 | -0.13083 | 2.3662 | 0.096561 | 0.077857 | -0.38659 | -0.32221 | -0.057914 | -0.18869 | 0.044759 | -0.058427 | -0.000513 | -0.11165 | -0.21376 | 124.1795 | 123.9237 | 123.9881 | 67.4437 | -124.2916 | 124.1216 | 124.1986 | 124.0965 | 67.4473 | -124.3682
161.9062 | 124.5026 | -67.4194 | 56.813 | 0.049183 | 0.0012363 | 0.0028908 | 0.055627 | -0.0046394 | 0.051741 | 0.07984 | -0.00058685 | -0.0041997 | 0.062067 | 0.014559 | 0.062978 | -65.1631 | -0.003172 | -67.3412 | 56.7326 | 56.4768 | 56.5366 | -67.4419 | -67.4021 | 0.004938 | -67.5145 | 56.6793 | 56.7563 | 56.6359 | -67.5002 | -0.022498 | -0.08048 | 2.2563 | 0.078253 | 0.10075 | -0.33624 | -0.27644 | -0.0808 | -0.13376 | 0.017294 | -0.095049 | -0.014249 | -0.056721 | -0.17714 | 124.152 | 123.8962 | 123.956 | 67.4163 | -124.255 | 124.0987 | 124.1758 | 124.0553 | 67.4244 | -124.3133
162.9062 | 124.5071 | -67.4194 | 56.8222 | 0.018659 | 0.0012363 | 0.0018228 | 0.052422 | -0.0025034 | 0.053878 | 0.064579 | -0.0016549 | -0.0031317 | 0.062067 | 0.014559 | 0.060841 | -65.1769 | 0.001407 | -67.3366 | 56.728 | 56.4722 | 56.5366 | -67.4236 | -67.4113 | -0.00422 | -67.5191 | 56.6839 | 56.7517 | 56.6359 | -67.4911 | -0.004182 | -0.094214 | 2.2426 | 0.082831 | 0.087013 | -0.34997 | -0.28559 | -0.071643 | -0.13834 | 0.008136 | -0.099628 | -0.027985 | -0.070456 | -0.1863 | 124.1474 | 123.8917 | 123.956 | 67.4208 | -124.2458 | 124.1033 | 124.1712 | 124.0553 | 67.4152 | -124.3133
163.9062 | 124.5346 | -67.4377 | 56.8222 | 0.064445 | 0.0012363 | 0.00075378 | 0.05349 | -0.0035714 | 0.05281 | 0.064579 | -0.0027229 | -0.0031317 | 0.062067 | 0.013491 | 0.061909 | -65.1677 | -0.007751 | -67.3458 | 56.7371 | 56.4814 | 56.5366 | -67.4419 | -67.4021 | 0.000359 | -67.5099 | 56.6884 | 56.7563 | 56.6451 | -67.4957 | -0.004188 | -0.085057 | 2.27 | 0.091984 | 0.096172 | -0.34081 | -0.28559 | -0.057912 | -0.13376 | 0.035604 | -0.072161 | -0.014249 | -0.065877 | -0.17714 | 124.1749 | 123.9191 | 123.9744 | 67.43 | -124.2641 | 124.1262 | 124.1941 | 124.0828 | 67.4381 | -124.3179
164.9062 | 124.5392 | -67.4103 | 56.8314 | 0.049183 | 0.0012363 | -0.00031422 | 0.054559 | -0.0046394 | 0.05281 | 0.064579 | -0.0016549 | -0.0041997 | 0.062067 | 0.013491 | 0.059773 | -65.1448 | -0.007751 | -67.3412 | 56.728 | 56.4722 | 56.5412 | -67.4374 | -67.393 | -0.00422 | -67.5099 | 56.6839 | 56.7563 | 56.668 | -67.5002 | -0.027075 | -0.10337 | 2.2654 | 0.069097 | 0.096172 | -0.35912 | -0.29017 | -0.089956 | -0.14749 | 0.017295 | -0.099627 | -0.009671 | -0.075032 | -0.1634 | 124.1383 | 123.8825 | 123.9515 | 67.4025 | -124.2687 | 124.0941 | 124.1666 | 124.0782 | 67.4061 | -124.3316
165.9062 | 124.4934 | -67.4469 | 56.8039 | 0.049183 | 0.0012363 | 0.0018228 | 0.052422 | -0.0046394 | 0.053878 | 0.049318 | -0.0027229 | -0.0031317 | 0.062067 | 0.014559 | 0.060841 | -65.1677 | 0.001407 | -67.3458 | 56.728 | 56.4768 | 56.5366 | -67.4328 | -67.4067 | 0.000359 | -67.5099 | 56.6884 | 56.7517 | 56.6359 | -67.4865 | 0.014125 | -0.075903 | 2.2792 | 0.10114 | 0.087014 | -0.32708 | -0.26728 | -0.039599 | -0.11545 | 0.04018 | -0.063006 | -0.023407 | -0.052145 | -0.16799 | 124.1749 | 123.9237 | 123.9835 | 67.4483 | -124.2367 | 124.1353 | 124.1986 | 124.0828 | 67.4473 | -124.2904
166.9062 | 124.5255 | -67.4011 | 56.813 | 0.064445 | 0.00016734 | -0.00031422 | 0.054559 | -0.0046394 | 0.053878 | 0.049318 | -0.00058685 | -0.0020637 | 0.060999 | 0.014559 | 0.060841 | -65.1586 | -0.003172 | -67.3366 | 56.728 | 56.4722 | 56.532 | -67.4465 | -67.4067 | 0.000359 | -67.5053 | 56.6839 | 56.7563 | 56.6588 | -67.4865 | -0.045388 | -0.085058 | 2.2426 | 0.06452 | 0.10991 | -0.34081 | -0.28101 | -0.085375 | -0.12918 | -0.005596 | -0.1042 | -0.018828 | -0.056721 | -0.15425 | 124.1291 | 123.8734 | 123.9332 | 67.398 | -124.2596 | 124.085 | 124.1575 | 124.0599 | 67.4015 | -124.2995
167.9062 | 124.5346 | -67.4057 | 56.8085 | 0.064445 | 0.0023043 | 0.00075378 | 0.054559 | -0.0025034 | 0.05281 | 0.034057 | -0.0027229 | -0.0031317 | 0.062067 | 0.014559 | 0.062978 | -65.1494 | -0.007751 | -67.3412 | 56.728 | 56.4768 | 56.5458 | -67.4282 | -67.4021 | -0.008798 | -67.5099 | 56.6839 | 56.7563 | 56.6359 | -67.4957 | -0.022494 | -0.080481 | 2.2563 | 0.06452 | 0.087014 | -0.33166 | -0.2627 | -0.089955 | -0.12461 | 0.003561 | -0.1042 | -0.014249 | -0.052144 | -0.17256 | 124.1337 | 123.8825 | 123.9515 | 67.3979 | -124.2367 | 124.0896 | 124.162 | 124.0416 | 67.3969 | -124.3041
168.9062 | 124.5209 | -67.4103 | 56.8268 | 0.064445 | 0.00016734 | 0.00075378 | 0.055627 | -0.0046394 | 0.05281 | 0.064579 | -0.0027229 | -0.0031317 | 0.059931 | 0.014559 | 0.060841 | -65.1036 | -0.007751 | -67.332 | 56.728 | 56.4768 | 56.5275 | -67.4374 | -67.3976 | -0.008798 | -67.5007 | 56.6793 | 56.7563 | 56.6634 | -67.4957 | -0.027075 | -0.098791 | 2.3067 | 0.078253 | 0.10533 | -0.34997 | -0.29933 | -0.085378 | -0.14749 | 0.012717 | -0.090469 | -0.005091 | -0.070454 | -0.1634 | 124.1383 | 123.8871 | 123.9377 | 67.4025 | -124.2641 | 124.0896 | 124.1666 | 124.0737 | 67.4015 | -124.3224
169.9062 | 124.5575 | -67.424 | 56.8085 | 0.049183 | 0.0023043 | 0.0018228 | 0.05349 | -0.0025034 | 0.054946 | 0.049318 | -0.00058685 | -0.0031317 | 0.062067 | 0.014559 | 0.060841 | -65.1128 | -0.012329 | -67.332 | 56.7234 | 56.4814 | 56.532 | -67.4328 | -67.3976 | -0.00422 | -67.5053 | 56.6839 | 56.7517 | 56.6496 | -67.4911 | -0.008763 | -0.085059 | 2.3112 | 0.091986 | 0.10075 | -0.32708 | -0.27644 | -0.067066 | -0.12461 | 0.02645 | -0.081315 | -0.014249 | -0.056723 | -0.15883 | 124.1474 | 123.9054 | 123.956 | 67.4117 | -124.2412 | 124.1079 | 124.1758 | 124.0737 | 67.4198 | -124.2995
170.9062 | 124.5621 | -67.4011 | 56.8039 | 0.049183 | 0.00016734 | 0.0018228 | 0.05349 | -0.0046394 | 0.051741 | 0.064579 | -0.0016549 | -0.0020637 | 0.062067 | 0.015628 | 0.060841 | -65.0899 | -0.007751 | -67.3412 | 56.7326 | 56.4814 | 56.5458 | -67.4328 | -67.393 | 0.004938 | -67.5145 | 56.6793 | 56.7563 | 56.613 | -67.5002 | -0.031651 | -0.071325 | 2.3112 | 0.059942 | 0.091593 | -0.3225 | -0.25812 | -0.099111 | -0.12461 | 0.00814 | -0.11336 | -0.014249 | -0.047566 | -0.19088 | 124.1337 | 123.8825 | 123.9469 | 67.3934 | -124.2367 | 124.0804 | 124.1575 | 124.0141 | 67.4061 | -124.3041
171.9062 | 124.5346 | -67.424 | 56.8085 | 0.079707 | 0.0012363 | 0.0018228 | 0.05349 | -0.0025034 | 0.05281 | 0.034057 | -0.0016549 | -0.0031317 | 0.059931 | 0.014559 | 0.060841 | -65.0853 | -0.007751 | -67.3366 | 56.728 | 56.4722 | 56.5366 | -67.4282 | -67.4067 | -0.008798 | -67.5099 | 56.6839 | 56.7609 | 56.6405 | -67.4911 | -0.004184 | -0.080481 | 2.3387 | 0.087408 | 0.091592 | -0.33624 | -0.27186 | -0.067066 | -0.12461 | 0.017292 | -0.085894 | -0.018828 | -0.047566 | -0.16799 | 124.152 | 123.8962 | 123.9606 | 67.4163 | -124.2367 | 124.1079 | 124.1849 | 124.0645 | 67.4152 | -124.2995
172.9688 | 124.4888 | -67.4423 | 56.8634 | 0.049183 | 0.0023043 | 0.00075378 | 0.054559 | -0.0035714 | 0.053878 | 0.064579 | -0.0027229 | -0.0041997 | 0.062067 | 0.014559 | 0.060841 | -65.0304 | -0.012329 | -67.3412 | 56.7371 | 56.4814 | 56.5366 | -67.4328 | -67.3976 | 0.000359 | -67.5007 | 56.6793 | 56.7472 | 56.6496 | -67.4911 | 0.009548 | -0.12626 | 2.4119 | 0.10114 | 0.091593 | -0.38201 | -0.32679 | -0.048755 | -0.18412 | 0.044761 | -0.058425 | -0.00967 | -0.11623 | -0.21376 | 124.1795 | 123.9237 | 123.9789 | 67.43 | -124.2962 | 124.1216 | 124.1895 | 124.092 | 67.4427 | -124.3545
173.9062 | 124.5438 | -67.4423 | 56.781 | 0.049183 | 0.0012363 | 0.0018228 | 0.055627 | -0.0025034 | 0.053878 | 0.095101 | -0.0027229 | -0.0041997 | 0.060999 | 0.014559 | 0.059773 | -65.0853 | -0.012329 | -67.3366 | 56.728 | 56.4768 | 56.5366 | -67.4328 | -67.4067 | 0.000359 | -67.5145 | 56.6839 | 56.7563 | 56.6313 | -67.4957 | 0.009548 | -0.053015 | 2.357 | 0.10572 | 0.096171 | -0.30419 | -0.24439 | -0.053334 | -0.09714 | 0.035603 | -0.072161 | -0.018827 | -0.024678 | -0.14968 | 124.1703 | 123.9191 | 123.9789 | 67.43 | -124.2138 | 124.1262 | 124.1987 | 124.0737 | 67.4427 | -124.2767
174.9062 | 124.4614 | -67.4423 | 56.7856 | 0.079707 | 0.00016734 | 0.00075378 | 0.05349 | -0.0035714 | 0.054946 | 0.064579 | -0.0027229 | -0.0041997 | 0.059931 | 0.014559 | 0.060841 | -65.0762 | -0.003172 | -67.3366 | 56.7326 | 56.4768 | 56.5275 | -67.4282 | -67.3976 | -0.00422 | -67.5053 | 56.6839 | 56.7472 | 56.6359 | -67.4957 | 0.014127 | -0.053014 | 2.3662 | 0.10572 | 0.091592 | -0.30877 | -0.25813 | -0.053334 | -0.10172 | 0.044761 | -0.063004 | -0.00967 | -0.038413 | -0.14968 | 124.1749 | 123.9191 | 123.9698 | 67.4391 | -124.2138 | 124.1262 | 124.1895 | 124.0782 | 67.4381 | -124.2812
175.9062 | 124.5438 | -67.4194 | 56.7993 | 0.064445 | 0.0012363 | 0.0018228 | 0.05349 | -0.0046394 | 0.05281 | 0.064579 | -0.0027229 | -0.0031317 | 0.060999 | 0.014559 | 0.060841 | -65.0853 | -0.012329 | -67.3458 | 56.7234 | 56.4677 | 56.5412 | -67.4328 | -67.393 | 0.000359 | -67.5145 | 56.6839 | 56.7517 | 56.6405 | -67.4957 | -0.01334 | -0.075903 | 2.3341 | 0.073674 | 0.087014 | -0.33166 | -0.25812 | -0.076222 | -0.11545 | 0.026451 | -0.095049 | -0.018827 | -0.047567 | -0.15883 | 124.1428 | 123.8871 | 123.9606 | 67.4071 | -124.2321 | 124.1033 | 124.1712 | 124.0599 | 67.4198 | -124.295
176.9062 | 124.4705 | -67.4606 | 56.8176 | 0.049183 | 0.00016734 | -0.00031422 | 0.055627 | -0.0025034 | 0.05281 | 0.064579 | -0.0027229 | -0.0031317 | 0.060999 | 0.015628 | 0.061909 | -65.067 | -0.007751 | -67.3366 | 56.728 | 56.4814 | 56.5366 | -67.4328 | -67.3976 | -0.00422 | -67.5053 | 56.6839 | 56.7563 | 56.6725 | -67.4957 | 0.027858 | -0.089636 | 2.3936 | 0.12403 | 0.096171 | -0.33623 | -0.28101 | -0.035024 | -0.13376 | 0.063071 | -0.044694 | -0.00967 | -0.061299 | -0.14509 | 124.1886 | 123.942 | 123.9972 | 67.4529 | -124.2504 | 124.1445 | 124.217 | 124.1332 | 67.4564 | -124.3133
177.9062 | 124.4247 | -67.4561 | 56.8497 | 0.033921 | 0.0012363 | 0.0018228 | 0.054559 | -0.0035714 | 0.05281 | 0.064579 | -0.0037909 | -0.0031317 | 0.059931 | 0.014559 | 0.060841 | -65.0578 | -0.003172 | -67.3412 | 56.728 | 56.4722 | 56.5412 | -67.4282 | -67.4021 | -0.00422 | -67.5053 | 56.6747 | 56.7609 | 56.6359 | -67.5002 | 0.02786 | -0.12168 | 2.3982 | 0.11487 | 0.087014 | -0.37744 | -0.30848 | -0.044179 | -0.17496 | 0.053915 | -0.049271 | -0.005092 | -0.088764 | -0.21376 | 124.184 | 123.9283 | 123.9972 | 67.4529 | -124.2779 | 124.1308 | 124.217 | 124.092 | 67.4518 | -124.3499
178.9062 | 124.379 | -67.4652 | 56.8497 | 0.049183 | 0.00016734 | 0.0018228 | 0.054559 | -0.0035714 | 0.05281 | 0.07984 | -0.0037909 | -0.0020637 | 0.059931 | 0.015628 | 0.058705 | -65.0487 | -0.003172 | -67.3412 | 56.728 | 56.4768 | 56.5458 | -67.4282 | -67.393 | -0.00422 | -67.5099 | 56.6793 | 56.7563 | 56.6451 | -67.5048 | 0.037015 | -0.12168 | 2.4165 | 0.12403 | 0.087014 | -0.37286 | -0.3039 | -0.039603 | -0.17038 | 0.072227 | -0.044695 | -0.005092 | -0.093342 | -0.20461 | 124.1932 | 123.942 | 124.011 | 67.462 | -124.2779 | 124.1445 | 124.2215 | 124.1103 | 67.461 | -124.3545
179.9062 | 124.4202 | -67.4515 | 56.8451 | 0.033921 | -0.0019697 | -0.00031422 | 0.054559 | -0.0046394 | 0.054946 | 0.049318 | -0.0027229 | -0.0041997 | 0.062067 | 0.014559 | 0.060841 | -65.0533 | -0.012329 | -67.3412 | 56.728 | 56.4722 | 56.5458 | -67.4465 | -67.393 | -0.008798 | -67.5053 | 56.6839 | 56.7517 | 56.6588 | -67.4957 | 0.004966 | -0.1171 | 2.3982 | 0.1103 | 0.10533 | -0.37286 | -0.29932 | -0.044179 | -0.16123 | 0.058494 | -0.053849 | -0.00967 | -0.093344 | -0.18629 | 124.1795 | 123.9237 | 123.9972 | 67.4391 | -124.2916 | 124.1353 | 124.2032 | 124.1103 | 67.4427 | -124.3407
180.9688 | 124.4156 | -67.4332 | 56.8634 | 0.079707 | 0.0012363 | 0.0028908 | 0.054559 | -0.0035714 | 0.054946 | 0.064579 | -0.0027229 | -0.0041997 | 0.060999 | 0.014559 | 0.059773 | -65.0624 | -0.016908 | -67.3366 | 56.728 | 56.4814 | 56.5412 | -67.4374 | -67.3976 | -0.008798 | -67.5099 | 56.6793 | 56.7472 | 56.6771 | -67.4865 | -0.004186 | -0.13541 | 2.3707 | 0.096564 | 0.10075 | -0.38201 | -0.32221 | -0.053331 | -0.18412 | 0.035606 | -0.076738 | -0.023407 | -0.11623 | -0.18629 | 124.1612 | 123.9146 | 123.9744 | 67.4163 | -124.3008 | 124.1125 | 124.1803 | 124.1103 | 67.4244 | -124.3499
181.9062 | 124.4476 | -67.4286 | 56.8497 | 0.049183 | 0.0012363 | 0.0018228 | 0.05349 | -0.0046394 | 0.05281 | 0.049318 | -0.0027229 | -0.0041997 | 0.063135 | 0.016696 | 0.060841 | -65.0441 | -0.012329 | -67.3458 | 56.728 | 56.4768 | 56.5412 | -67.4419 | -67.3976 | -0.00422 | -67.5053 | 56.6793 | 56.7472 | 56.6542 | -67.4911 | -0.013343 | -0.12168 | 2.3845 | 0.082829 | 0.096172 | -0.37286 | -0.30848 | -0.062488 | -0.17038 | 0.031028 | -0.076737 | -0.014249 | -0.1025 | -0.19545 | 124.1566 | 123.9054 | 123.9698 | 67.4163 | -124.2916 | 124.1079 | 124.1758 | 124.0828 | 67.4244 | -124.3407
182.9688 | 124.5575 | -67.3874 | 56.8359 | 0.064445 | 0.0012363 | 0.0018228 | 0.055627 | -0.0035714 | 0.053878 | 0.064579 | -0.0016549 | -0.0020637 | 0.060999 | 0.014559 | 0.059773 | -65.0807 | -0.021486 | -67.3366 | 56.728 | 56.4768 | 56.5412 | -67.4419 | -67.3976 | -0.008798 | -67.5053 | 56.6884 | 56.7563 | 56.6771 | -67.4957 | -0.054542 | -0.10795 | 2.3067 | 0.050787 | 0.10533 | -0.35912 | -0.29474 | -0.10827 | -0.14749 | -0.010171 | -0.11794 | -0.00967 | -0.079609 | -0.15882 | 124.1154 | 123.8642 | 123.9286 | 67.3659 | -124.2779 | 124.0758 | 124.1437 | 124.0645 | 67.3786 | -124.3316
183.9062 | 124.4339 | -67.4561 | 56.8497 | 0.079707 | 0.0023043 | 0.0018228 | 0.05349 | -0.0035714 | 0.053878 | 0.049318 | -0.0016549 | -0.0031317 | 0.063135 | 0.016696 | 0.059773 | -65.0441 | -0.012329 | -67.3366 | 56.7326 | 56.4768 | 56.5458 | -67.4465 | -67.4067 | -0.013377 | -67.5053 | 56.6839 | 56.7563 | 56.6588 | -67.5002 | 0.009544 | -0.1171 | 2.4119 | 0.11945 | 0.10991 | -0.37286 | -0.3039 | -0.044179 | -0.1658 | 0.049336 | -0.049271 | -0.005092 | -0.093342 | -0.19087 | 124.1886 | 123.9329 | 124.0018 | 67.4437 | -124.2962 | 124.1399 | 124.2124 | 124.1149 | 67.4427 | -124.3499
184.9062 | 124.4659 | -67.4286 | 56.8359 | 0.079707 | 0.00016734 | 0.00075378 | 0.054559 | -0.0046394 | 0.053878 | 0.064579 | -0.0048589 | -0.0041997 | 0.062067 | 0.016696 | 0.059773 | -65.0395 | -0.012329 | -67.3458 | 56.7371 | 56.4814 | 56.5458 | -67.4419 | -67.3976 | -0.008798 | -67.5053 | 56.6839 | 56.7563 | 56.6496 | -67.4865 | -0.013343 | -0.098789 | 2.3891 | 0.082829 | 0.096172 | -0.35454 | -0.29017 | -0.057909 | -0.15207 | 0.031028 | -0.076737 | -0.018828 | -0.079609 | -0.1863 | 124.1657 | 123.91 | 123.9744 | 67.4163 | -124.2779 | 124.1125 | 124.1849 | 124.0782 | 67.4198 | -124.3224
185.9062 | 124.4522 | -67.4332 | 56.8405 | 0.049183 | 0.0033723 | 0.0018228 | 0.05349 | -0.0035714 | 0.05281 | 0.095101 | -0.0027229 | -0.0041997 | 0.064204 | 0.016696 | 0.059773 | -65.035 | -0.016908 | -67.332 | 56.7234 | 56.4722 | 56.5412 | -67.4282 | -67.3976 | -0.013377 | -67.5007 | 56.6839 | 56.7563 | 56.6405 | -67.4911 | 0.004972 | -0.1171 | 2.3982 | 0.10114 | 0.09617 | -0.36828 | -0.29932 | -0.05791 | -0.15665 | 0.035606 | -0.06758 | -0.00967 | -0.084187 | -0.20003 | 124.1566 | 123.9054 | 123.9744 | 67.4163 | -124.2687 | 124.117 | 124.1895 | 124.0737 | 67.4198 | -124.3316
186.9062 | 124.4705 | -67.4515 | 56.8726 | 0.079707 | 0.0012363 | 0.0018228 | 0.055627 | -0.0046394 | 0.05281 | 0.07984 | -0.0037909 | -0.0031317 | 0.060999 | 0.016696 | 0.059773 | -65.0212 | -0.021486 | -67.3366 | 56.7326 | 56.4768 | 56.5412 | -67.4282 | -67.3976 | -0.00422 | -67.5053 | 56.6793 | 56.7563 | 56.6588 | -67.4865 | 0.023282 | -0.13999 | 2.4303 | 0.11487 | 0.091592 | -0.39575 | -0.33137 | -0.035021 | -0.19327 | 0.053916 | -0.053849 | -0.018828 | -0.11623 | -0.21376 | 124.184 | 123.9283 | 123.9927 | 67.43 | -124.3008 | 124.1308 | 124.2078 | 124.1103 | 67.4473 | -124.3591
187.9688 | 124.4888 | -67.4286 | 56.8039 | 0.049183 | 0.0023043 | 0.00075378 | 0.05349 | -0.0035714 | 0.051741 | 0.064579 | -0.0027229 | -0.0020637 | 0.062067 | 0.014559 | 0.059773 | -65.1265 | -0.016908 | -67.3274 | 56.728 | 56.4722 | 56.5412 | -67.4374 | -67.393 | -0.008798 | -67.5053 | 56.6839 | 56.7517 | 56.668 | -67.4957 | -0.008764 | -0.075903 | 2.3021 | 0.10114 | 0.10991 | -0.33166 | -0.2627 | -0.067067 | -0.12003 | 0.035606 | -0.076737 | -0.00967 | -0.052145 | -0.13594 | 124.1566 | 123.9008 | 123.9698 | 67.4117 | -124.2412 | 124.1125 | 124.1803 | 124.0965 | 67.4198 | -124.2995
188.9062 | 124.4385 | -67.4423 | 56.8771 | 0.064445 | 0.0012363 | -0.00031422 | 0.054559 | -0.0046394 | 0.05281 | 0.064579 | -0.0027229 | -0.0020637 | 0.063135 | 0.017764 | 0.060841 | -65.0304 | -0.021486 | -67.3366 | 56.728 | 56.4677 | 56.5458 | -67.4465 | -67.4021 | -0.017956 | -67.5053 | 56.6793 | 56.7517 | 56.6451 | -67.4957 | -0.004189 | -0.14914 | 2.4119 | 0.10572 | 0.10991 | -0.40948 | -0.33137 | -0.053334 | -0.19785 | 0.040182 | -0.063004 | -0.00967 | -0.12539 | -0.23207 | 124.1703 | 123.91 | 123.9881 | 67.4208 | -124.3236 | 124.1216 | 124.1941 | 124.0874 | 67.4244 | -124.3728
189.9062 | 124.4431 | -67.4194 | 56.8542 | 0.049183 | 0.00016734 | -0.00031422 | 0.052422 | -0.0035714 | 0.053878 | 0.064579 | -0.0037909 | -0.0031317 | 0.060999 | 0.015628 | 0.060841 | -65.035 | -0.021486 | -67.3366 | 56.7234 | 56.4722 | 56.5412 | -67.4236 | -67.4021 | -0.013377 | -67.5053 | 56.6839 | 56.7609 | 56.6267 | -67.5002 | -0.004182 | -0.13083 | 2.3845 | 0.082831 | 0.087013 | -0.38201 | -0.31306 | -0.0808 | -0.17038 | 0.017294 | -0.085892 | -0.005092 | -0.093342 | -0.2275 | 124.1428 | 123.8917 | 123.9606 | 67.3979 | -124.2779 | 124.1033 | 124.1803 | 124.0462 | 67.4061 | -124.3545
190.9062 | 124.4476 | -67.4194 | 56.8588 | 0.064445 | 0.0012363 | 0.0018228 | 0.05349 | -0.0046394 | 0.05281 | 0.049318 | -0.0027229 | -0.0031317 | 0.063135 | 0.016696 | 0.060841 | -65.035 | -0.016908 | -67.332 | 56.7234 | 56.4814 | 56.532 | -67.4236 | -67.3976 | -0.013377 | -67.4962 | 56.6793 | 56.7517 | 56.6542 | -67.4957 | -0.004182 | -0.13541 | 2.3845 | 0.087409 | 0.091591 | -0.37743 | -0.32679 | -0.076222 | -0.17954 | 0.021873 | -0.076735 | -0.000513 | -0.10708 | -0.20461 | 124.1428 | 123.9008 | 123.9515 | 67.4025 | -124.2824 | 124.0987 | 124.1712 | 124.0737 | 67.4061 | -124.3545
191.9062 | 124.4156 | -67.4469 | 56.8726 | 0.064445 | 0.00016734 | 0.0018228 | 0.054559 | -0.0046394 | 0.05281 | 0.064579 | -0.0037909 | -0.0041997 | 0.062067 | 0.018833 | 0.060841 | -65.0533 | -0.016908 | -67.3412 | 56.728 | 56.4722 | 56.5366 | -67.4374 | -67.4021 | -0.008798 | -67.5007 | 56.6839 | 56.7563 | 56.6359 | -67.4957 | 0.009546 | -0.14457 | 2.3936 | 0.10572 | 0.096172 | -0.40032 | -0.33595 | -0.048757 | -0.18869 | 0.044759 | -0.053848 | -0.005091 | -0.11623 | -0.23665 | 124.1749 | 123.9191 | 123.9835 | 67.43 | -124.3099 | 124.1308 | 124.2032 | 124.0828 | 67.4381 | -124.3682
192.9062 | 124.4659 | -67.3965 | 56.8588 | 0.064445 | 0.0012363 | 0.0028908 | 0.05349 | -0.0035714 | 0.051741 | 0.07984 | -0.0016549 | -0.0031317 | 0.062067 | 0.016696 | 0.060841 | -65.0624 | -0.016908 | -67.3458 | 56.7234 | 56.4768 | 56.5412 | -67.4374 | -67.3976 | -0.013377 | -67.5053 | 56.6747 | 56.7517 | 56.6496 | -67.4911 | -0.040808 | -0.13541 | 2.3341 | 0.050785 | 0.091593 | -0.38201 | -0.31763 | -0.094532 | -0.18412 | -0.001016 | -0.10878 | -0.014249 | -0.10708 | -0.20918 | 124.12 | 123.8734 | 123.9377 | 67.3796 | -124.2962 | 124.0713 | 124.1483 | 124.0462 | 67.3832 | -124.3499
193.9062 | 124.4202 | -67.4332 | 56.868 | 0.049183 | 0.00016734 | 0.0018228 | 0.054559 | -0.0046394 | 0.05281 | 0.095101 | -0.0016549 | -0.0031317 | 0.062067 | 0.014559 | 0.059773 | -65.0533 | -0.026065 | -67.3412 | 56.7326 | 56.4814 | 56.5458 | -67.4328 | -67.393 | -0.013377 | -67.4962 | 56.6793 | 56.7563 | 56.6359 | -67.4957 | 0.000393 | -0.13541 | 2.3799 | 0.091986 | 0.091593 | -0.38659 | -0.32221 | -0.062489 | -0.18869 | 0.040184 | -0.063002 | -0.000513 | -0.11165 | -0.23207 | 124.1657 | 123.9146 | 123.9789 | 67.4071 | -124.3008 | 124.1125 | 124.1895 | 124.0691 | 67.4198 | -124.3636
194.9062 | 124.498 | -67.4103 | 56.8405 | 0.049183 | 0.0023043 | 0.0018228 | 0.05349 | -0.0035714 | 0.053878 | 0.064579 | -0.0027229 | -0.0041997 | 0.060999 | 0.017764 | 0.061909 | -65.0716 | -0.016908 | -67.332 | 56.7326 | 56.4768 | 56.5412 | -67.4236 | -67.3976 | -0.017956 | -67.5053 | 56.6793 | 56.7517 | 56.6542 | -67.5002 | -0.013338 | -0.10795 | 2.3387 | 0.078253 | 0.091591 | -0.3637 | -0.29932 | -0.089956 | -0.16123 | 0.012717 | -0.095048 | -0.005092 | -0.088766 | -0.18629 | 124.1428 | 123.8871 | 123.9515 | 67.3934 | -124.2641 | 124.0896 | 124.162 | 124.0645 | 67.3923 | -124.3407
195.9062 | 124.5026 | -67.3965 | 56.8268 | 0.064445 | 0.0012363 | 0.00075378 | 0.05349 | -0.0057084 | 0.053878 | 0.064579 | -0.0027229 | -0.0031317 | 0.063135 | 0.017764 | 0.060841 | -65.0716 | -0.021486 | -67.3366 | 56.7326 | 56.4814 | 56.532 | -67.4282 | -67.3976 | -0.017956 | -67.5053 | 56.6793 | 56.7609 | 56.6451 | -67.5002 | -0.03165 | -0.094213 | 2.325 | 0.059942 | 0.091592 | -0.34539 | -0.29475 | -0.10369 | -0.14749 | -0.001016 | -0.10878 | -0.005092 | -0.065876 | -0.18172 | 124.1291 | 123.8779 | 123.9286 | 67.3751 | -124.255 | 124.0758 | 124.1575 | 124.0416 | 67.3786 | -124.327
196.9062 | 129.2404 | -67.3645 | 56.8451 | 0.079707 | 0.0023043 | 0.0028908 | 0.05349 | -0.0046394 | 0.050673 | 0.07984 | -0.0027229 | -0.0041997 | 0.063135 | 0.017764 | 0.060841 | -64.8015 | 0.19829 | -67.7074 | 56.7188 | 56.486 | 56.532 | -67.4236 | -67.5349 | 2.482 | -67.4824 | 56.6793 | 56.738 | 56.6313 | -67.4773 | -0.059114 | -0.12626 | 2.563 | -0.34294 | -0.28383 | -0.35912 | -0.31306 | -0.11284 | -0.16581 | -0.17042 | -0.11793 | -0.005092 | -0.10708 | -0.21376 | 124.0833 | 123.8505 | 123.8965 | 67.5628 | -124.2687 | 124.0438 | 124.1025 | 123.9958 | 69.8465 | -124.3224
197.9062 | 124.7086 | -67.3965 | 56.8314 | 0.049183 | 0.0033723 | 0.0028908 | 0.054559 | -0.0025034 | 0.05281 | 0.049318 | -0.0037909 | -0.0052687 | 0.063135 | 0.017764 | 0.060841 | -64.6 | 0.083821 | -67.3229 | 56.7234 | 56.4814 | 56.532 | -67.4282 | -67.393 | 0.36208 | -67.4504 | 56.6839 | 56.7472 | 56.6496 | -67.4911 | -0.03165 | -0.10795 | 2.7965 | 0.073677 | 0.10533 | -0.34997 | -0.29932 | -0.094532 | -0.14749 | 0.003562 | -0.053836 | 0.040696 | -0.08419 | -0.18172 | 124.12 | 123.8779 | 123.9286 | 67.4804 | -124.2596 | 124.0804 | 124.1437 | 124.0462 | 67.7586 | -124.3224
198.9062 | 124.5712 | -67.3874 | 56.8314 | 0.064445 | 0.0012363 | 0.0018228 | 0.05349 | -0.0035714 | 0.051741 | 0.064579 | -0.0016549 | -0.0041997 | 0.060999 | 0.017764 | 0.058705 | -65.1128 | -0.026065 | -67.332 | 56.728 | 56.4814 | 56.5366 | -67.4282 | -67.393 | -0.022535 | -67.5007 | 56.6884 | 56.7472 | 56.6451 | -67.4911 | -0.040805 | -0.10337 | 2.2746 | 0.055365 | 0.09617 | -0.34997 | -0.29475 | -0.10369 | -0.14292 | -0.005593 | -0.11336 | -0.00967 | -0.08419 | -0.1863 | 124.1154 | 123.8688 | 123.924 | 67.3613 | -124.2596 | 124.0758 | 124.1346 | 124.0325 | 67.3649 | -124.3224
199.9062 | 124.5346 | -67.3737 | 56.8405 | 0.079707 | 0.0023043 | 0.0028908 | 0.05349 | -0.0035714 | 0.053878 | 0.064579 | -0.0027229 | -0.0041997 | 0.059931 | 0.018833 | 0.060841 | -65.1357 | -0.026065 | -67.3366 | 56.7234 | 56.4814 | 56.532 | -67.4282 | -67.4021 | -0.022535 | -67.5053 | 56.6793 | 56.7609 | 56.6405 | -67.4957 | -0.054538 | -0.1171 | 2.238 | 0.037054 | 0.091592 | -0.35912 | -0.30848 | -0.122 | -0.16123 | -0.028483 | -0.13167 | -0.00967 | -0.079609 | -0.20003 | 124.0971 | 123.855 | 123.9057 | 67.3476 | -124.2687 | 124.0529 | 124.1346 | 124.0141 | 67.3511 | -124.3362
200.9062 | 124.5346 | -67.3828 | 56.8314 | 0.064445 | 0.0012363 | 0.0018228 | 0.054559 | -0.0025034 | 0.051741 | 0.064579 | -0.0037909 | -0.0052687 | 0.060999 | 0.017764 | 0.059773 | -65.1174 | -0.021486 | -67.3366 | 56.728 | 56.4814 | 56.5412 | -67.4374 | -67.393 | -0.017956 | -67.4916 | 56.6839 | 56.7472 | 56.668 | -67.5002 | -0.054541 | -0.10337 | 2.2654 | 0.046209 | 0.10075 | -0.34997 | -0.29017 | -0.11742 | -0.14749 | -0.010171 | -0.10878 | 0.008644 | -0.08419 | -0.1634 | 124.1108 | 123.8642 | 123.924 | 67.3613 | -124.2687 | 124.0667 | 124.13 | 124.0508 | 67.3649 | -124.3316
201.9688 | 124.3744 | -67.4561 | 56.8359 | 0.033921 | 0.0033723 | 0.0028908 | 0.054559 | -0.0035714 | 0.05281 | 0.07984 | -0.0027229 | -0.0041997 | 0.062067 | 0.018833 | 0.060841 | -65.0487 | -0.026065 | -67.3412 | 56.7326 | 56.4814 | 56.5458 | -67.4328 | -67.4021 | -0.017956 | -67.5007 | 56.6793 | 56.7472 | 56.6542 | -67.4957 | 0.023281 | -0.10337 | 2.4074 | 0.11487 | 0.091593 | -0.35454 | -0.29017 | -0.039601 | -0.15665 | 0.053915 | -0.044692 | -0.005091 | -0.088767 | -0.18172 | 124.1886 | 123.9374 | 124.0018 | 67.43 | -124.2687 | 124.1353 | 124.2032 | 124.1103 | 67.4381 | -124.3316
202.9062 | 124.5071 | -67.3965 | 56.8222 | 0.049183 | 0.0012363 | 0.0028908 | 0.054559 | -0.0046394 | 0.053878 | 0.064579 | -0.0048589 | -0.0052687 | 0.060999 | 0.018833 | 0.060841 | -65.1403 | -0.026065 | -67.3274 | 56.7188 | 56.4722 | 56.5412 | -67.419 | -67.4021 | -0.022535 | -67.5007 | 56.6747 | 56.7563 | 56.6359 | -67.5002 | -0.022492 | -0.10337 | 2.2563 | 0.069099 | 0.091591 | -0.34997 | -0.28101 | -0.10369 | -0.1475 | -0.005595 | -0.1042 | -0.000513 | -0.065877 | -0.1863 | 124.1154 | 123.8688 | 123.9377 | 67.3705 | -124.2412 | 124.0713 | 124.1529 | 124.0325 | 67.374 | -124.3224
203.9688 | 124.4797 | -67.3782 | 56.8405 | 0.079707 | 0.0012363 | 0.0018228 | 0.051353 | -0.0046394 | 0.053878 | 0.07984 | -0.0037909 | -0.0041997 | 0.062067 | 0.018833 | 0.060841 | -65.0899 | -0.026065 | -67.332 | 56.7326 | 56.4768 | 56.5503 | -67.4328 | -67.3976 | -0.017956 | -67.4962 | 56.6747 | 56.7563 | 56.6542 | -67.4957 | -0.054539 | -0.10795 | 2.2883 | 0.04621 | 0.10075 | -0.3637 | -0.29017 | -0.11742 | -0.16581 | -0.019326 | -0.11793 | -0.000513 | -0.084187 | -0.18629 | 124.1108 | 123.855 | 123.9286 | 67.3522 | -124.2733 | 124.0529 | 124.1346 | 124.0325 | 67.3603 | -124.3362
204.9062 | 124.5346 | -67.3737 | 56.8314 | 0.064445 | 0.0023043 | 0.0018228 | 0.052422 | -0.0046394 | 0.051741 | 0.064579 | -0.0037909 | -0.0031317 | 0.060999 | 0.018833 | 0.058705 | -65.1219 | -0.030644 | -67.332 | 56.7234 | 56.4768 | 56.5412 | -67.4236 | -67.393 | -0.017956 | -67.4962 | 56.6839 | 56.7563 | 56.6451 | -67.4957 | -0.049959 | -0.10795 | 2.2517 | 0.041632 | 0.091591 | -0.35455 | -0.29017 | -0.122 | -0.14749 | -0.019326 | -0.12251 | -0.000513 | -0.075032 | -0.1863 | 124.0971 | 123.8505 | 123.9148 | 67.343 | -124.255 | 124.0575 | 124.13 | 124.0187 | 67.3557 | -124.327
205.9688 | 124.3835 | -67.4469 | 56.8405 | 0.049183 | 0.0012363 | 0.0028908 | 0.054559 | -0.0035714 | 0.051741 | 0.07984 | -0.0027229 | -0.0052687 | 0.060999 | 0.017764 | 0.061909 | -65.0487 | -0.035222 | -67.3366 | 56.728 | 56.4814 | 56.5503 | -67.4236 | -67.3976 | -0.022535 | -67.5007 | 56.6747 | 56.7517 | 56.6451 | -67.4911 | 0.023283 | -0.11252 | 2.3982 | 0.1103 | 0.087013 | -0.35912 | -0.29017 | -0.044178 | -0.16581 | 0.049338 | -0.053848 | -0.00967 | -0.088766 | -0.19545 | 124.1749 | 123.9283 | 123.9972 | 67.4117 | -124.2641 | 124.1216 | 124.1986 | 124.092 | 67.4244 | -124.3316
206.9062 | 124.4797 | -67.4011 | 56.8176 | 0.064445 | 0.00016734 | -0.00031422 | 0.052422 | -0.0046394 | 0.050673 | 0.064579 | -0.0037909 | -0.0041997 | 0.060999 | 0.018833 | 0.058705 | -65.1357 | -0.035222 | -67.3274 | 56.728 | 56.4768 | 56.5366 | -67.4282 | -67.4021 | -0.022535 | -67.4962 | 56.6747 | 56.7563 | 56.6313 | -67.4957 | -0.027072 | -0.089636 | 2.2654 | 0.073677 | 0.10075 | -0.34081 | -0.28101 | -0.094533 | -0.14292 | -0.001017 | -0.095046 | -0.000513 | -0.061299 | -0.1863 | 124.1291 | 123.8779 | 123.9377 | 67.3659 | -124.2458 | 124.0758 | 124.1575 | 124.0325 | 67.3786 | -124.3133
207.9688 | 124.5255 | -67.4103 | 56.8176 | 0.033921 | 0.00016734 | 0.00075378 | 0.054559 | -0.0046394 | 0.05281 | 0.064579 | -0.0027229 | -0.0052687 | 0.063135 | 0.019901 | 0.059773 | -65.0899 | -0.030644 | -67.3274 | 56.728 | 56.4768 | 56.5366 | -67.4328 | -67.393 | -0.022535 | -67.4962 | 56.6839 | 56.7563 | 56.6634 | -67.4957 | -0.022496 | -0.089636 | 2.3204 | 0.082832 | 0.10533 | -0.34081 | -0.28101 | -0.085378 | -0.13376 | 0.017295 | -0.085891 | -0.000513 | -0.061299 | -0.15425 | 124.1383 | 123.8871 | 123.9469 | 67.3796 | -124.2504 | 124.0941 | 124.1666 | 124.0737 | 67.3877 | -124.3133
208.9062 | 124.4843 | -67.4194 | 56.8085 | 0.064445 | -0.00090066 | 0.0028908 | 0.05349 | -0.0046394 | 0.053878 | 0.064579 | -0.0027229 | -0.0041997 | 0.060999 | 0.018833 | 0.060841 | -65.1357 | -0.035222 | -67.332 | 56.7234 | 56.4722 | 56.5503 | -67.4328 | -67.393 | -0.027113 | -67.4962 | 56.6747 | 56.7517 | 56.6313 | -67.4911 | -0.01334 | -0.085059 | 2.2838 | 0.087409 | 0.10075 | -0.33624 | -0.25812 | -0.071643 | -0.13376 | 0.026451 | -0.076735 | -0.005092 | -0.056723 | -0.17714 | 124.1428 | 123.8917 | 123.9698 | 67.3842 | -124.2412 | 124.0941 | 124.1712 | 124.0508 | 67.3923 | -124.2995
209.9062 | 124.4705 | -67.4057 | 56.8634 | 0.033921 | 0.0023043 | 0.0018228 | 0.05349 | -0.0025034 | 0.05281 | 0.07984 | -0.0027229 | -0.0052687 | 0.059931 | 0.018833 | 0.060841 | -65.1357 | -0.030644 | -67.332 | 56.7234 | 56.4814 | 56.5366 | -67.4328 | -67.3976 | -0.022535 | -67.5007 | 56.6747 | 56.7517 | 56.6359 | -67.4957 | -0.027073 | -0.13999 | 2.27 | 0.073676 | 0.10075 | -0.38201 | -0.32679 | -0.089955 | -0.18869 | 0.00814 | -0.095046 | -0.005091 | -0.11165 | -0.2275 | 124.1291 | 123.8871 | 123.9423 | 67.3751 | -124.2962 | 124.0804 | 124.1574 | 124.0416 | 67.3832 | -124.3591
210.9688 | 124.3881 | -67.4469 | 56.8451 | 0.064445 | 0.00016734 | 0.0018228 | 0.052422 | -0.0046394 | 0.051741 | 0.07984 | -0.0048589 | -0.0041997 | 0.060999 | 0.018833 | 0.059773 | -65.0304 | -0.035222 | -67.3458 | 56.728 | 56.4768 | 56.5458 | -67.4282 | -67.4021 | -0.022535 | -67.5053 | 56.6701 | 56.7517 | 56.6496 | -67.4865 | 0.018704 | -0.1171 | 2.4165 | 0.10114 | 0.082435 | -0.36828 | -0.29932 | -0.039599 | -0.17496 | 0.044759 | -0.058427 | -0.018828 | -0.093344 | -0.19545 | 124.1749 | 123.9237 | 123.9927 | 67.4117 | -124.2733 | 124.117 | 124.1986 | 124.0965 | 67.4244 | -124.3316
211.9062 | 124.5071 | -67.424 | 56.8268 | 0.049183 | 0.0012363 | 0.00075378 | 0.052422 | -0.0025034 | 0.051741 | 0.07984 | -0.0016549 | -0.0041997 | 0.060999 | 0.019901 | 0.060841 | -65.1357 | -0.030644 | -67.332 | 56.7234 | 56.486 | 56.5366 | -67.4282 | -67.393 | -0.031692 | -67.5007 | 56.6793 | 56.7609 | 56.6359 | -67.4957 | -0.004184 | -0.10337 | 2.2883 | 0.091986 | 0.09617 | -0.34081 | -0.29017 | -0.071645 | -0.14749 | 0.031028 | -0.076736 | -0.005091 | -0.065876 | -0.19087 | 124.1474 | 123.91 | 123.9606 | 67.3934 | -124.255 | 124.1033 | 124.1849 | 124.0599 | 67.3923 | -124.3224
212.9688 | 124.4247 | -67.424 | 56.8497 | 0.064445 | -0.00090066 | 0.0028908 | 0.051353 | -0.0046394 | 0.05281 | 0.064579 | -0.0027229 | -0.0031317 | 0.060999 | 0.018833 | 0.060841 | -65.0258 | -0.039801 | -67.332 | 56.7234 | 56.4768 | 56.5412 | -67.4419 | -67.393 | -0.027113 | -67.5053 | 56.6747 | 56.7472 | 56.6771 | -67.4911 | -0.017921 | -0.12626 | 2.3982 | 0.091986 | 0.10991 | -0.37286 | -0.30848 | -0.067066 | -0.17496 | 0.031028 | -0.081315 | -0.014249 | -0.1025 | -0.17256 | 124.1474 | 123.9008 | 123.9652 | 67.3842 | -124.2916 | 124.0987 | 124.1712 | 124.1011 | 67.3969 | -124.3407
213.9062 | 124.4934 | -67.4057 | 56.8222 | 0.033921 | 0.0012363 | 0.0018228 | 0.052422 | -0.0046394 | 0.05281 | 0.07984 | -0.0016549 | -0.0041997 | 0.062067 | 0.022038 | 0.060841 | -65.1082 | -0.035222 | -67.3274 | 56.7234 | 56.4722 | 56.5503 | -67.4328 | -67.393 | -0.027113 | -67.5007 | 56.6747 | 56.7472 | 56.6405 | -67.4957 | -0.027073 | -0.098792 | 2.2975 | 0.078255 | 0.10533 | -0.34997 | -0.27186 | -0.089955 | -0.1475 | 0.012718 | -0.095046 | -0.005091 | -0.075035 | -0.18172 | 124.1291 | 123.8779 | 123.956 | 67.3705 | -124.255 | 124.0804 | 124.1529 | 124.0462 | 67.3786 | -124.3179
214.9062 | 124.4934 | -67.392 | 56.8588 | 0.033921 | 0.0012363 | 0.0018228 | 0.05349 | -0.0025034 | 0.051741 | 0.049318 | -0.0016549 | -0.0031317 | 0.062067 | 0.02097 | 0.058705 | -65.1357 | -0.035222 | -67.332 | 56.7234 | 56.4768 | 56.5458 | -67.4236 | -67.3976 | -0.031692 | -67.5007 | 56.6793 | 56.7472 | 56.6405 | -67.4911 | -0.031648 | -0.13541 | 2.2563 | 0.059943 | 0.091591 | -0.38201 | -0.31306 | -0.099109 | -0.17954 | -0.005593 | -0.10878 | -0.00967 | -0.11166 | -0.21834 | 124.1154 | 123.8688 | 123.9377 | 67.3567 | -124.2824 | 124.0713 | 124.1391 | 124.0325 | 67.3603 | -124.3499
215.9219 | 124.3973 | -67.4149 | 56.8771 | 0.079707 | -0.00090066 | 0.00075378 | 0.052422 | -0.0035714 | 0.051741 | 0.07984 | -0.0027229 | -0.0041997 | 0.060999 | 0.019901 | 0.057636 | -65.035 | -0.039801 | -67.3412 | 56.728 | 56.4768 | 56.5458 | -67.4099 | -67.393 | -0.027113 | -67.4962 | 56.6793 | 56.7563 | 56.6405 | -67.4957 | 0.004977 | -0.14914 | 2.3799 | 0.073675 | 0.068698 | -0.40032 | -0.33137 | -0.0808 | -0.19785 | 0.021873 | -0.081313 | -0.000513 | -0.12081 | -0.23665 | 124.1428 | 123.8917 | 123.9606 | 67.3751 | -124.287 | 124.0941 | 124.1712 | 124.0553 | 67.3877 | -124.3728
216.9062 | 124.4659 | -67.4286 | 56.8039 | 0.064445 | 0.0012363 | 0.00075378 | 0.05349 | -0.0046394 | 0.05281 | 0.07984 | -0.0037909 | -0.0031317 | 0.059931 | 0.017764 | 0.059773 | -65.1128 | -0.030644 | -67.3366 | 56.728 | 56.4814 | 56.5503 | -67.419 | -67.3884 | -0.031692 | -67.5007 | 56.6839 | 56.7472 | 56.613 | -67.4957 | 0.009552 | -0.075903 | 2.3158 | 0.091986 | 0.082434 | -0.3225 | -0.25355 | -0.067067 | -0.12003 | 0.040185 | -0.072158 | -0.005091 | -0.056724 | -0.19088 | 124.1566 | 123.91 | 123.9789 | 67.3979 | -124.2229 | 124.1125 | 124.1758 | 124.0416 | 67.3969 | -124.2995
217.9688 | 124.4934 | -67.424 | 56.8314 | 0.049183 | 0.0023043 | 0.0028908 | 0.055627 | -0.0046394 | 0.05281 | 0.064579 | -0.0016549 | -0.0052687 | 0.059931 | 0.018833 | 0.058705 | -65.0533 | -0.039801 | -67.3366 | 56.728 | 56.4722 | 56.5412 | -67.4236 | -67.393 | -0.022535 | -67.4916 | 56.6747 | 56.7655 | 56.6405 | -67.4957 | 0.000395 | -0.10337 | 2.3707 | 0.087408 | 0.087013 | -0.35912 | -0.29017 | -0.071645 | -0.15665 | 0.031028 | -0.067579 | 0.004066 | -0.065875 | -0.19087 | 124.152 | 123.8962 | 123.9652 | 67.3842 | -124.255 | 124.0987 | 124.1895 | 124.0645 | 67.4015 | -124.327
218.9062 | 124.498 | -67.392 | 56.8359 | 0.064445 | 0.00016734 | 0.00075378 | 0.05349 | -0.0046394 | 0.051741 | 0.064579 | -0.0027229 | -0.0031317 | 0.059931 | 0.018833 | 0.059773 | -65.1265 | -0.039801 | -67.3366 | 56.7188 | 56.4768 | 56.5412 | -67.4145 | -67.393 | -0.027113 | -67.5007 | 56.6747 | 56.7563 | 56.6451 | -67.5002 | -0.02249 | -0.1171 | 2.2654 | 0.055365 | 0.077855 | -0.35912 | -0.29474 | -0.10827 | -0.16123 | -0.001015 | -0.10878 | -0.000513 | -0.079609 | -0.19087 | 124.1108 | 123.8688 | 123.9332 | 67.3522 | -124.2504 | 124.0667 | 124.1483 | 124.037 | 67.3649 | -124.3362
219.9062 | 124.5346 | -67.3874 | 56.7993 | 0.064445 | 0.00016734 | 0.0028908 | 0.05349 | -0.0046394 | 0.051741 | 0.064579 | -0.00058685 | -0.0052687 | 0.059931 | 0.019901 | 0.060841 | -65.1036 | -0.035222 | -67.3229 | 56.7234 | 56.4677 | 56.5366 | -67.419 | -67.3884 | -0.027113 | -67.5007 | 56.6747 | 56.7517 | 56.6176 | -67.4957 | -0.031647 | -0.075903 | 2.2838 | 0.064522 | 0.096169 | -0.33166 | -0.2627 | -0.10827 | -0.12461 | -0.001014 | -0.11336 | -0.005091 | -0.047567 | -0.18172 | 124.1108 | 123.855 | 123.924 | 67.3522 | -124.2184 | 124.0621 | 124.1391 | 124.005 | 67.3603 | -124.295
220.9219 | 125.7431 | -67.3782 | 56.8405 | 0.064445 | 0.0012363 | 0.0018228 | 0.052422 | -0.0025034 | 0.05281 | 0.07984 | -0.0027229 | -0.0041997 | 0.060999 | 0.02097 | 0.059773 | -65.0121 | 0.0243 | -67.2634 | 56.7234 | 56.4677 | 56.5366 | -67.4374 | -67.3747 | -0.036271 | -67.4779 | 56.6747 | 56.7609 | 56.6496 | -67.4957 | -0.059118 | -0.1171 | 2.3662 | 0.11488 | 0.174 | -0.37286 | -0.3039 | -0.11742 | -0.16581 | 0.003567 | -0.099619 | 0.017802 | -0.079609 | -0.19087 | 124.1016 | 123.8459 | 123.9148 | 67.4025 | -124.2779 | 124.0529 | 124.1391 | 124.0279 | 67.342 | -124.3362
221.9062 | 125.061 | -67.3874 | 56.7993 | 0.049183 | 0.00016734 | 0.0028908 | 0.052422 | -0.0046394 | 0.051741 | 0.064579 | -0.0027229 | -0.0041997 | 0.060999 | 0.019901 | 0.060841 | -65.0807 | -0.007751 | -67.2725 | 56.728 | 56.4722 | 56.5412 | -67.4419 | -67.425 | -0.022535 | -67.487 | 56.6747 | 56.7609 | 56.6359 | -67.4911 | -0.054542 | -0.071325 | 2.3067 | 0.11488 | 0.16942 | -0.32708 | -0.25812 | -0.10369 | -0.12461 | -0.037644 | -0.099621 | 0.004066 | -0.03841 | -0.16341 | 124.1154 | 123.8596 | 123.9286 | 67.3796 | -124.2412 | 124.0621 | 124.1483 | 124.0233 | 67.3649 | -124.2904
222.9062 | 125.2441 | -67.4149 | 56.8039 | 0.064445 | 0.00016734 | 0.00075378 | 0.05349 | -0.0046394 | 0.051741 | 0.064579 | -0.0027229 | -0.0020637 | 0.062067 | 0.02097 | 0.057636 | -65.0762 | 0.005985 | -67.2634 | 56.7234 | 56.4722 | 56.5366 | -67.4236 | -67.4067 | -0.031692 | -67.487 | 56.6747 | 56.7609 | 56.6222 | -67.4957 | -0.00876 | -0.080481 | 2.3387 | 0.15151 | 0.16026 | -0.33166 | -0.26728 | -0.0808 | -0.12918 | 0.008137 | -0.072155 | 0.008645 | -0.042988 | -0.18172 | 124.1383 | 123.8871 | 123.9515 | 67.4208 | -124.2275 | 124.0896 | 124.1758 | 124.037 | 67.3832 | -124.2995
223.9062 | 125.3174 | -67.392 | 56.8039 | 0.049183 | 0.00016734 | 0.0018228 | 0.05349 | -0.0035714 | 0.051741 | 0.07984 | -0.0037909 | -0.0041997 | 0.059931 | 0.022038 | 0.059773 | -65.0578 | -0.003172 | -67.2634 | 56.7234 | 56.4768 | 56.5412 | -67.4282 | -67.4067 | -0.036271 | -67.487 | 56.6839 | 56.7563 | 56.6588 | -67.4957 | -0.036227 | -0.080481 | 2.3341 | 0.12862 | 0.16484 | -0.32708 | -0.2627 | -0.10369 | -0.12003 | -0.014751 | -0.095043 | 0.008645 | -0.047566 | -0.14509 | 124.1154 | 123.8688 | 123.9332 | 67.3888 | -124.2321 | 124.0758 | 124.1483 | 124.0508 | 67.3557 | -124.2995
224.9062 | 125.2258 | -67.392 | 56.8085 | 0.064445 | 0.00016734 | 0.00075378 | 0.05349 | -0.0046394 | 0.051741 | 0.07984 | -0.0037909 | -0.0031317 | 0.062067 | 0.019901 | 0.060841 | -65.0853 | -0.003172 | -67.2679 | 56.7188 | 56.4677 | 56.5412 | -67.4236 | -67.4067 | -0.036271 | -67.4779 | 56.6839 | 56.7563 | 56.6359 | -67.4911 | -0.031648 | -0.089638 | 2.3067 | 0.12404 | 0.15569 | -0.34082 | -0.26728 | -0.099109 | -0.12461 | -0.014751 | -0.085886 | 0.013223 | -0.052144 | -0.17256 | 124.1108 | 123.8596 | 123.9332 | 67.3888 | -124.2321 | 124.0758 | 124.1483 | 124.0279 | 67.3557 | -124.2995
225.9844 | 125.2029 | -67.3874 | 56.8268 | 0.049183 | 0.00016734 | 0.0018228 | 0.054559 | -0.0057084 | 0.051741 | 0.064579 | -0.0027229 | -0.0041997 | 0.059931 | 0.02097 | 0.058705 | -65.0807 | -0.003172 | -67.2679 | 56.7234 | 56.4722 | 56.5412 | -67.4236 | -67.4113 | -0.036271 | -67.4824 | 56.6793 | 56.7426 | 56.6496 | -67.4957 | -0.036226 | -0.10337 | 2.3067 | 0.11946 | 0.15569 | -0.35455 | -0.28559 | -0.10827 | -0.14749 | -0.023908 | -0.095042 | 0.013224 | -0.08419 | -0.17714 | 124.1108 | 123.8596 | 123.9286 | 67.3842 | -124.2504 | 124.0667 | 124.13 | 124.037 | 67.3511 | -124.3224
226.9062 | 125.354 | -67.3828 | 56.781 | 0.079707 | -0.00090066 | -0.00031422 | 0.052422 | -0.0057084 | 0.05281 | 0.07984 | -0.0027229 | -0.0031317 | 0.059931 | 0.02097 | 0.058705 | -65.0533 | -0.007751 | -67.2588 | 56.7188 | 56.4722 | 56.5458 | -67.4328 | -67.4113 | -0.040849 | -67.4824 | 56.6747 | 56.7517 | 56.6451 | -67.4911 | -0.049962 | -0.062172 | 2.3295 | 0.12404 | 0.174 | -0.30877 | -0.23524 | -0.10827 | -0.1063 | -0.028486 | -0.09962 | 0.008645 | -0.029257 | -0.13594 | 124.1016 | 123.855 | 123.9286 | 67.3751 | -124.2138 | 124.0575 | 124.1346 | 124.0279 | 67.342 | -124.2721
227.9062 | 125.3723 | -67.3874 | 56.7902 | 0.049183 | -0.00090066 | 0.0018228 | 0.054559 | -0.0046394 | 0.051741 | 0.064579 | -0.0037909 | -0.0031317 | 0.059931 | 0.022038 | 0.060841 | -65.035 | -0.003172 | -67.2542 | 56.7188 | 56.4631 | 56.5412 | -67.4328 | -67.3976 | -0.040849 | -67.4779 | 56.6701 | 56.7517 | 56.6313 | -67.4865 | -0.045384 | -0.071327 | 2.3524 | 0.1332 | 0.17858 | -0.32708 | -0.24897 | -0.099108 | -0.12003 | -0.010171 | -0.090464 | 0.008644 | -0.038412 | -0.15883 | 124.1062 | 123.8505 | 123.9286 | 67.3842 | -124.2229 | 124.0575 | 124.1391 | 124.0187 | 67.3465 | -124.2767
228.9062 | 125.4227 | -67.3874 | 56.8222 | 0.079707 | 0.00016734 | 0.0018228 | 0.052422 | -0.0025034 | 0.051741 | 0.07984 | -0.0027229 | -0.0031317 | 0.060999 | 0.024175 | 0.058705 | -65.0487 | -0.007751 | -67.2634 | 56.7234 | 56.4768 | 56.5412 | -67.4328 | -67.393 | -0.045428 | -67.4824 | 56.6793 | 56.7472 | 56.6405 | -67.4911 | -0.045384 | -0.098792 | 2.3387 | 0.12404 | 0.16942 | -0.34539 | -0.28101 | -0.10369 | -0.14292 | -0.005593 | -0.095042 | 0.008645 | -0.075035 | -0.18172 | 124.1108 | 123.8642 | 123.9286 | 67.3796 | -124.255 | 124.0667 | 124.1346 | 124.0279 | 67.342 | -124.3133
229.9062 | 125.4639 | -67.4103 | 56.813 | 0.033921 | -0.00090066 | 0.00075378 | 0.054559 | -0.0046394 | 0.05281 | 0.049318 | -0.0016549 | -0.0041997 | 0.059931 | 0.022038 | 0.058705 | -65.0304 | -0.007751 | -67.2542 | 56.7188 | 56.4722 | 56.5412 | -67.4236 | -67.3976 | -0.036271 | -67.4687 | 56.6747 | 56.7472 | 56.6176 | -67.5002 | -0.013338 | -0.094215 | 2.3799 | 0.15608 | 0.16942 | -0.34081 | -0.27186 | -0.089956 | -0.13834 | 0.012717 | -0.058418 | 0.031538 | -0.065879 | -0.19546 | 124.1291 | 123.8825 | 123.9515 | 67.4025 | -124.2367 | 124.085 | 124.1574 | 124.0279 | 67.374 | -124.3133
230.9219 | 125.3448 | -67.424 | 56.8817 | 0.064445 | -0.0019697 | 0.0018228 | 0.054559 | -0.0025034 | 0.051741 | 0.095101 | -0.0016549 | -0.0031317 | 0.060999 | 0.022038 | 0.059773 | -65.0075 | -0.026065 | -67.2771 | 56.7234 | 56.4722 | 56.5412 | -67.4236 | -67.3976 | -0.027113 | -67.4733 | 56.6839 | 56.7563 | 56.6267 | -67.4911 | 0.000395 | -0.1583 | 2.4165 | 0.14693 | 0.14653 | -0.40948 | -0.34052 | -0.067066 | -0.19785 | 0.02645 | -0.049264 | 0.017802 | -0.12539 | -0.25497 | 124.1474 | 123.8962 | 123.9652 | 67.3979 | -124.3053 | 124.1079 | 124.1803 | 124.0508 | 67.3969 | -124.3728
231.9062 | 125.3357 | -67.3828 | 56.7902 | 0.033921 | 0.00016734 | 0.0018228 | 0.05349 | -0.0025034 | 0.05281 | 0.049318 | -0.0037909 | -0.0031317 | 0.060999 | 0.02097 | 0.056568 | -65.067 | -0.012329 | -67.2817 | 56.7188 | 56.4722 | 56.5503 | -67.4236 | -67.4021 | -0.045428 | -67.4733 | 56.6839 | 56.7517 | 56.6222 | -67.4957 | -0.040804 | -0.071327 | 2.3158 | 0.10115 | 0.14195 | -0.31793 | -0.23981 | -0.11284 | -0.10629 | -0.019328 | -0.090463 | 0.022381 | -0.038412 | -0.16799 | 124.1016 | 123.855 | 123.9332 | 67.3705 | -124.2138 | 124.0667 | 124.1346 | 124.005 | 67.3374 | -124.2858
232.9062 | 125.267 | -67.3599 | 56.7947 | 0.064445 | 0.0012363 | 0.0018228 | 0.052422 | -0.0046394 | 0.050673 | 0.07984 | -0.0027229 | -0.0041997 | 0.058862 | 0.022038 | 0.059773 | -65.035 | -0.012329 | -67.2771 | 56.7234 | 56.4768 | 56.5458 | -67.4374 | -67.4113 | -0.045428 | -67.4779 | 56.6839 | 56.7563 | 56.6496 | -67.4911 | -0.077429 | -0.071326 | 2.325 | 0.082839 | 0.16027 | -0.31793 | -0.24897 | -0.13115 | -0.11087 | -0.051374 | -0.11793 | 0.013223 | -0.038411 | -0.1451 | 124.0833 | 123.8367 | 123.9057 | 67.3476 | -124.2321 | 124.0438 | 124.1163 | 124.0096 | 67.3145 | -124.2858
233.9062 | 125.3311 | -67.4011 | 56.8222 | 0.033921 | 0.00016734 | 0.0018228 | 0.05349 | -0.0035714 | 0.051741 | 0.064579 | -0.0016549 | -0.0031317 | 0.060999 | 0.02097 | 0.059773 | -65.0304 | -0.007751 | -67.2817 | 56.728 | 56.4814 | 56.5412 | -67.4282 | -67.4067 | -0.036271 | -67.4779 | 56.6793 | 56.7563 | 56.6267 | -67.4957 | -0.027072 | -0.094214 | 2.3707 | 0.11946 | 0.14653 | -0.34081 | -0.28101 | -0.094533 | -0.14292 | -0.005596 | -0.076731 | 0.017802 | -0.065877 | -0.19546 | 124.1291 | 123.8825 | 123.9423 | 67.3934 | -124.2504 | 124.0804 | 124.1575 | 124.0279 | 67.3649 | -124.3179
234.9062 | 124.4339 | -67.4332 | 56.7993 | 0.064445 | 0.0012363 | 0.0028908 | 0.052422 | -0.0057084 | 0.050673 | 0.049318 | -0.0027229 | -0.0031317 | 0.059931 | 0.022038 | 0.056568 | -65.0533 | -0.058115 | -67.332 | 56.7234 | 56.4768 | 56.5458 | -67.419 | -67.3792 | -0.050007 | -67.4962 | 56.6793 | 56.7517 | 56.6405 | -67.4957 | 0.01413 | -0.075903 | 2.3799 | 0.10114 | 0.087012 | -0.3225 | -0.25355 | -0.062489 | -0.12003 | 0.05392 | -0.063002 | -0.000513 | -0.047567 | -0.15883 | 124.1566 | 123.91 | 123.9789 | 67.3751 | -124.2184 | 124.1125 | 124.1849 | 124.0737 | 67.3832 | -124.295
235.9219 | 124.53 | -67.3965 | 56.8314 | 0.049183 | 0.00016734 | 0.0028908 | 0.052422 | -0.0046394 | 0.051741 | 0.07984 | -0.0027229 | -0.0041997 | 0.060999 | 0.02097 | 0.059773 | -65.0945 | -0.058115 | -67.3274 | 56.7188 | 56.4814 | 56.5458 | -67.4374 | -67.393 | -0.050007 | -67.4824 | 56.6793 | 56.7472 | 56.6451 | -67.4865 | -0.040808 | -0.11253 | 2.3021 | 0.069099 | 0.10991 | -0.34997 | -0.28559 | -0.089953 | -0.15207 | 0.003562 | -0.085887 | 0.004066 | -0.08419 | -0.1863 | 124.1154 | 123.8779 | 123.9423 | 67.3384 | -124.2687 | 124.0758 | 124.1437 | 124.0416 | 67.3465 | -124.3179
236.9062 | 124.5117 | -67.4332 | 56.8039 | 0.049183 | -0.00090066 | 0.00075378 | 0.052422 | -0.0046394 | 0.050673 | 0.07984 | -0.0048589 | -0.0052687 | 0.060999 | 0.022038 | 0.057636 | -65.067 | -0.062694 | -67.3274 | 56.728 | 56.4814 | 56.5458 | -67.4282 | -67.3838 | -0.054586 | -67.487 | 56.6701 | 56.7517 | 56.6542 | -67.4865 | 0.004972 | -0.075903 | 2.3662 | 0.10572 | 0.10075 | -0.3225 | -0.25812 | -0.053331 | -0.13376 | 0.049342 | -0.053844 | -0.000513 | -0.052145 | -0.14967 | 124.1612 | 123.9146 | 123.9789 | 67.3705 | -124.2321 | 124.1033 | 124.1849 | 124.0874 | 67.3786 | -124.2904
237.9062 | 124.4339 | -67.424 | 56.8222 | 0.033921 | 0.00016734 | 0.0039598 | 0.05349 | -0.0035714 | 0.051741 | 0.064579 | -0.0037909 | -0.0052687 | 0.060999 | 0.02097 | 0.059773 | -65.0578 | -0.067272 | -67.332 | 56.7188 | 56.4814 | 56.5458 | -67.4419 | -67.3747 | -0.054586 | -67.4916 | 56.6701 | 56.7517 | 56.6542 | -67.4865 | -0.017921 | -0.10337 | 2.3662 | 0.091986 | 0.10991 | -0.34081 | -0.27643 | -0.062487 | -0.15207 | 0.049343 | -0.067579 | -0.005092 | -0.070456 | -0.16798 | 124.1428 | 123.9054 | 123.9698 | 67.3567 | -124.2641 | 124.0941 | 124.1758 | 124.0782 | 67.3694 | -124.3087
238.9062 | 124.5483 | -67.392 | 56.7993 | 0.049183 | 0.0012363 | 0.0018228 | 0.05349 | -0.0057084 | 0.05281 | 0.07984 | -0.0059269 | -0.0041997 | 0.059931 | 0.022038 | 0.059773 | -65.067 | -0.067272 | -67.3274 | 56.7234 | 56.4677 | 56.5458 | -67.4282 | -67.3884 | -0.059164 | -67.487 | 56.6793 | 56.7563 | 56.6267 | -67.4957 | -0.036227 | -0.075903 | 2.325 | 0.064522 | 0.10075 | -0.33166 | -0.25355 | -0.10369 | -0.12003 | 0.003564 | -0.095043 | 0.008645 | -0.042988 | -0.17257 | 124.1154 | 123.8596 | 123.9377 | 67.3247 | -124.2275 | 124.0713 | 124.1483 | 124.0187 | 67.3328 | -124.295
239.9062 | 124.4614 | -67.4149 | 56.8222 | 0.033921 | 0.00016734 | 0.0028908 | 0.05349 | -0.0035714 | 0.050673 | 0.064579 | -0.0027229 | -0.0041997 | 0.060999 | 0.024175 | 0.059773 | -65.0624 | -0.07643 | -67.332 | 56.7234 | 56.4768 | 56.5412 | -67.4282 | -67.3838 | -0.054586 | -67.487 | 56.6747 | 56.7563 | 56.6451 | -67.4911 | -0.013339 | -0.098792 | 2.3524 | 0.082831 | 0.09617 | -0.34539 | -0.28101 | -0.076221 | -0.1475 | 0.031031 | -0.072155 | 0.004066 | -0.065877 | -0.17714 | 124.1383 | 123.8917 | 123.956 | 67.3384 | -124.2504 | 124.0896 | 124.1712 | 124.0599 | 67.3603 | -124.3133
240.9062 | 124.3744 | -67.4515 | 56.8451 | 0.033921 | 0.0012363 | 0.0028908 | 0.05349 | -0.0046394 | 0.051741 | 0.064579 | -0.0037909 | -0.0041997 | 0.060999 | 0.024175 | 0.057636 | -65.0441 | -0.07643 | -67.3274 | 56.728 | 56.4722 | 56.5458 | -67.4328 | -67.3884 | -0.059164 | -67.487 | 56.6747 | 56.7517 | 56.6359 | -67.4865 | 0.018703 | -0.1171 | 2.4074 | 0.12403 | 0.10533 | -0.37286 | -0.29932 | -0.035021 | -0.17038 | 0.063073 | -0.035534 | -0.000513 | -0.093344 | -0.20919 | 124.1795 | 123.9237 | 123.9972 | 67.375 | -124.2779 | 124.1262 | 124.2032 | 124.0874 | 67.3923 | -124.3316
241.9062 | 124.3835 | -67.4561 | 56.8497 | 0.049183 | 0.00016734 | 0.0028908 | 0.052422 | -0.0035714 | 0.051741 | 0.095101 | -0.0037909 | -0.0052687 | 0.060999 | 0.024175 | 0.059773 | -65.0304 | -0.067272 | -67.332 | 56.7234 | 56.4677 | 56.5503 | -67.4328 | -67.3838 | -0.063743 | -67.487 | 56.6701 | 56.7517 | 56.6451 | -67.4865 | 0.023281 | -0.12626 | 2.4257 | 0.12403 | 0.10075 | -0.38201 | -0.29932 | -0.030443 | -0.17954 | 0.07223 | -0.030956 | -0.000513 | -0.097921 | -0.20461 | 124.1795 | 123.9237 | 124.0064 | 67.3888 | -124.2824 | 124.1262 | 124.2078 | 124.1011 | 67.3923 | -124.3362
242.9062 | 124.411 | -67.4515 | 56.8359 | 0.049183 | 0.00016734 | 0.0018228 | 0.05349 | -0.0035714 | 0.05281 | 0.049318 | -0.0027229 | -0.0041997 | 0.058862 | 0.022038 | 0.058705 | -65.0487 | -0.081008 | -67.3229 | 56.728 | 56.4722 | 56.5503 | -67.4328 | -67.3792 | -0.0729 | -67.4824 | 56.6839 | 56.7563 | 56.6451 | -67.4865 | 0.018703 | -0.10795 | 2.4028 | 0.12861 | 0.10991 | -0.3637 | -0.28559 | -0.035021 | -0.15207 | 0.07223 | -0.030955 | 0.004066 | -0.079609 | -0.19087 | 124.1795 | 123.9237 | 124.0018 | 67.3705 | -124.2687 | 124.1353 | 124.2078 | 124.0965 | 67.3786 | -124.3224
243.9062 | 124.4385 | -67.4423 | 56.8268 | 0.064445 | -0.00090066 | 0.0018228 | 0.052422 | -0.0035714 | 0.051741 | 0.064579 | -0.0037909 | -0.0041997 | 0.059931 | 0.025243 | 0.059773 | -65.035 | -0.085587 | -67.3274 | 56.728 | 56.4677 | 56.5458 | -67.4282 | -67.3792 | -0.068322 | -67.4916 | 56.6793 | 56.7517 | 56.6359 | -67.4911 | 0.014127 | -0.098791 | 2.4074 | 0.11488 | 0.10075 | -0.35913 | -0.28101 | -0.048755 | -0.14749 | 0.063075 | -0.049268 | -0.000513 | -0.075033 | -0.19087 | 124.1703 | 123.91 | 123.9881 | 67.3567 | -124.255 | 124.1216 | 124.1941 | 124.0782 | 67.374 | -124.3179
244.9062 | 124.3835 | -67.4469 | 56.8451 | 0.079707 | 0.00016734 | 0.0028908 | 0.054559 | -0.0046394 | 0.051741 | 0.07984 | -0.0027229 | -0.0041997 | 0.062067 | 0.024175 | 0.058705 | -65.0395 | -0.085587 | -67.3183 | 56.7143 | 56.4768 | 56.5503 | -67.419 | -67.3884 | -0.0729 | -67.4824 | 56.6747 | 56.7563 | 56.6313 | -67.4957 | 0.027862 | -0.13084 | 2.4074 | 0.12861 | 0.10075 | -0.36828 | -0.29474 | -0.048757 | -0.17038 | 0.058495 | -0.035533 | 0.013224 | -0.088765 | -0.21376 | 124.1612 | 123.9237 | 123.9972 | 67.3613 | -124.2641 | 124.1216 | 124.2032 | 124.0782 | 67.374 | -124.3407
245.9062 | 124.3927 | -67.4469 | 56.8176 | 0.049183 | 0.00016734 | 0.00075378 | 0.052422 | -0.0057084 | 0.051741 | 0.064579 | -0.0016549 | -0.0052687 | 0.059931 | 0.024175 | 0.058705 | -65.0395 | -0.081008 | -67.3229 | 56.728 | 56.4677 | 56.5458 | -67.4328 | -67.3747 | -0.068322 | -67.4916 | 56.6701 | 56.7609 | 56.6496 | -67.4957 | 0.014125 | -0.089636 | 2.4074 | 0.12403 | 0.10991 | -0.34997 | -0.27186 | -0.048757 | -0.1475 | 0.072231 | -0.044691 | 0.004066 | -0.056721 | -0.16799 | 124.1749 | 123.9146 | 123.9927 | 67.3659 | -124.2504 | 124.117 | 124.2078 | 124.0965 | 67.3786 | -124.3133
246.9062 | 124.4476 | -67.3965 | 56.8542 | 0.064445 | 0.00016734 | 0.0018228 | 0.052422 | -0.0046394 | 0.050673 | 0.064579 | -0.0027229 | -0.0041997 | 0.059931 | 0.023106 | 0.058705 | -65.0395 | -0.090166 | -67.3183 | 56.7234 | 56.4722 | 56.5549 | -67.4236 | -67.3884 | -0.0729 | -67.4824 | 56.6747 | 56.7517 | 56.6359 | -67.4911 | -0.027071 | -0.13083 | 2.357 | 0.078255 | 0.10533 | -0.38201 | -0.29932 | -0.094532 | -0.17954 | 0.008141 | -0.085887 | 0.008645 | -0.1025 | -0.21834 | 124.12 | 123.8688 | 123.9515 | 67.3064 | -124.2779 | 124.0713 | 124.1483 | 124.0325 | 67.3236 | -124.3453
247.9062 | 124.3744 | -67.4377 | 56.8497 | 0.064445 | 0.00016734 | 0.00075378 | 0.05349 | -0.0057084 | 0.051741 | 0.049318 | -0.0037909 | -0.0052687 | 0.058862 | 0.023106 | 0.059773 | -65.0716 | -0.090166 | -67.3274 | 56.7188 | 56.4768 | 56.5503 | -67.4328 | -67.3838 | -0.077479 | -67.4824 | 56.6747 | 56.7563 | 56.6359 | -67.4957 | 0.00497 | -0.13084 | 2.3662 | 0.1103 | 0.10533 | -0.37286 | -0.29932 | -0.057912 | -0.17496 | 0.053919 | -0.044688 | 0.013224 | -0.093342 | -0.21376 | 124.1566 | 123.9146 | 123.9881 | 67.3476 | -124.2824 | 124.1125 | 124.1941 | 124.0737 | 67.3603 | -124.3453
248.9062 | 124.4019 | -67.4377 | 56.8542 | 0.079707 | 0.00016734 | 0.00075378 | 0.05349 | -0.0046394 | 0.050673 | 0.064579 | -0.0027229 | -0.0041997 | 0.059931 | 0.024175 | 0.058705 | -65.067 | -0.090166 | -67.3274 | 56.7326 | 56.4768 | 56.5458 | -67.4236 | -67.3747 | -0.082058 | -67.4916 | 56.6747 | 56.7517 | 56.6588 | -67.4957 | 0.014128 | -0.12168 | 2.3707 | 0.1103 | 0.09617 | -0.37743 | -0.30848 | -0.057912 | -0.17954 | 0.063076 | -0.053846 | 0.004066 | -0.1025 | -0.19545 | 124.1703 | 123.9146 | 123.9835 | 67.3476 | -124.2779 | 124.1125 | 124.1895 | 124.0965 | 67.3557 | -124.3499
249.9062 | 124.3561 | -67.4698 | 56.8359 | 0.064445 | -0.0019697 | 0.0018228 | 0.054559 | -0.0057084 | 0.051741 | 0.07984 | -0.0027229 | -0.0063367 | 0.060999 | 0.026311 | 0.058705 | -65.0716 | -0.094744 | -67.3183 | 56.7188 | 56.4768 | 56.5503 | -67.419 | -67.3747 | -0.086637 | -67.4824 | 56.6701 | 56.7563 | 56.6496 | -67.4865 | 0.050751 | -0.1171 | 2.3982 | 0.1515 | 0.10075 | -0.35912 | -0.28559 | -0.01671 | -0.16581 | 0.09512 | -0.012644 | 0.004066 | -0.079609 | -0.1863 | 124.1886 | 123.9466 | 124.0201 | 67.375 | -124.255 | 124.1399 | 124.2261 | 124.1194 | 67.3832 | -124.3224
250.9062 | 124.3973 | -67.4286 | 56.8222 | 0.079707 | -0.00090066 | -0.00031422 | 0.052422 | -0.0046394 | 0.050673 | 0.049318 | -0.0037909 | -0.0052687 | 0.060999 | 0.023106 | 0.058705 | -65.067 | -0.099323 | -67.3229 | 56.728 | 56.4814 | 56.5412 | -67.4328 | -67.3838 | -0.091215 | -67.4824 | 56.6747 | 56.7655 | 56.6496 | -67.4957 | -0.004185 | -0.094214 | 2.3616 | 0.10572 | 0.10991 | -0.34081 | -0.28101 | -0.067067 | -0.1475 | 0.044764 | -0.053843 | 0.013224 | -0.05672 | -0.17256 | 124.1566 | 123.91 | 123.9698 | 67.3293 | -124.255 | 124.1033 | 124.1941 | 124.0782 | 67.3374 | -124.3179
251.9062 | 124.3561 | -67.4515 | 56.8222 | 0.064445 | 0.00016734 | 0.0028908 | 0.051353 | -0.0046394 | 0.05281 | 0.064579 | -0.0037909 | -0.0041997 | 0.059931 | 0.023106 | 0.057636 | -65.0762 | -0.10848 | -67.3229 | 56.7234 | 56.4768 | 56.5458 | -67.4328 | -67.3792 | -0.086637 | -67.487 | 56.6793 | 56.7517 | 56.6496 | -67.4865 | 0.018703 | -0.098792 | 2.3753 | 0.12861 | 0.10991 | -0.34539 | -0.27643 | -0.035021 | -0.14292 | 0.07223 | -0.035534 | -0.000513 | -0.070456 | -0.17256 | 124.1749 | 123.9283 | 123.9972 | 67.343 | -124.255 | 124.1308 | 124.2032 | 124.1011 | 67.3648 | -124.3087
252.9062 | 124.379 | -67.4561 | 56.8497 | 0.049183 | 0.00016734 | 0.0018228 | 0.051353 | -0.0057084 | 0.05281 | 0.064579 | -0.0037909 | -0.0041997 | 0.060999 | 0.025243 | 0.058705 | -65.0716 | -0.11306 | -67.3183 | 56.7234 | 56.4722 | 56.5458 | -67.4328 | -67.3792 | -0.10037 | -67.4733 | 56.6793 | 56.7563 | 56.6496 | -67.4911 | 0.023281 | -0.12626 | 2.3845 | 0.13777 | 0.11448 | -0.37744 | -0.3039 | -0.035022 | -0.17038 | 0.076808 | -0.01722 | 0.017802 | -0.093342 | -0.20003 | 124.1795 | 123.9283 | 124.0018 | 67.343 | -124.2824 | 124.1353 | 124.2124 | 124.1057 | 67.3557 | -124.3407
253.9062 | 124.3927 | -67.4469 | 56.8497 | 0.018659 | 0.00016734 | 0.0039598 | 0.051353 | -0.0057084 | 0.050673 | 0.095101 | -0.0048589 | -0.0052687 | 0.058862 | 0.023106 | 0.058705 | -65.067 | -0.11306 | -67.3229 | 56.7326 | 56.4768 | 56.5503 | -67.419 | -67.3792 | -0.10495 | -67.4824 | 56.6793 | 56.7563 | 56.6313 | -67.4911 | 0.027862 | -0.1171 | 2.3799 | 0.12403 | 0.096169 | -0.37286 | -0.29932 | -0.044178 | -0.17038 | 0.067652 | -0.035533 | 0.008645 | -0.093342 | -0.21834 | 124.1795 | 123.9237 | 123.9972 | 67.3338 | -124.2687 | 124.1262 | 124.2032 | 124.0782 | 67.3419 | -124.3407
254.9062 | 124.4064 | -67.4103 | 56.8451 | 0.049183 | 0.00016734 | 0.0028908 | 0.05349 | -0.0067764 | 0.050673 | 0.064579 | -0.0027229 | -0.0052687 | 0.060999 | 0.024175 | 0.058705 | -65.0578 | -0.12222 | -67.3183 | 56.728 | 56.4768 | 56.5458 | -67.4328 | -67.3747 | -0.10037 | -67.4824 | 56.6747 | 56.7563 | 56.6405 | -67.4865 | -0.022496 | -0.1171 | 2.3524 | 0.091988 | 0.11448 | -0.36828 | -0.29932 | -0.07622 | -0.17038 | 0.03561 | -0.072154 | 0.004066 | -0.088765 | -0.20461 | 124.1383 | 123.8871 | 123.956 | 67.2881 | -124.2779 | 124.085 | 124.1666 | 124.0508 | 67.3099 | -124.3316
255.9062 | 124.4156 | -67.4286 | 56.8405 | 0.049183 | 0.00016734 | 0.00075378 | 0.052422 | -0.0067764 | 0.050673 | 0.064579 | -0.0037909 | -0.0041997 | 0.059931 | 0.023106 | 0.057636 | -65.0578 | -0.12222 | -67.332 | 56.728 | 56.4814 | 56.5503 | -67.4328 | -67.3747 | -0.10953 | -67.4824 | 56.6793 | 56.7517 | 56.6313 | -67.4865 | -0.004185 | -0.11252 | 2.3707 | 0.096564 | 0.10075 | -0.35912 | -0.29017 | -0.057909 | -0.16123 | 0.053921 | -0.053843 | 0.004066 | -0.088766 | -0.20919 | 124.1566 | 123.91 | 123.9789 | 67.3064 | -124.2733 | 124.1079 | 124.1803 | 124.0599 | 67.3191 | -124.327
256.9062 | 124.4019 | -67.4332 | 56.8451 | 0.049183 | 0.00016734 | 0.0039598 | 0.052422 | -0.0046394 | 0.051741 | 0.064579 | -0.0037909 | -0.0052687 | 0.060999 | 0.025243 | 0.058705 | -65.0716 | -0.13137 | -67.3274 | 56.728 | 56.4814 | 56.5458 | -67.4328 | -67.3792 | -0.10953 | -67.487 | 56.6747 | 56.7563 | 56.6542 | -67.4865 | 0.000393 | -0.1171 | 2.3616 | 0.10572 | 0.10533 | -0.3637 | -0.29932 | -0.053331 | -0.17038 | 0.05392 | -0.053844 | -0.000513 | -0.088765 | -0.19087 | 124.1612 | 123.9146 | 123.9789 | 67.3018 | -124.2779 | 124.1079 | 124.1895 | 124.0874 | 67.3236 | -124.3316
257.9062 | 124.4019 | -67.4377 | 56.8588 | 0.079707 | -0.00090066 | 0.0018228 | 0.05349 | -0.0046394 | 0.050673 | 0.064579 | -0.0037909 | -0.0041997 | 0.058862 | 0.024175 | 0.057636 | -65.0624 | -0.13595 | -67.3229 | 56.728 | 56.4814 | 56.5595 | -67.4328 | -67.3792 | -0.11869 | -67.487 | 56.6793 | 56.7563 | 56.6405 | -67.4865 | 0.00497 | -0.13083 | 2.3753 | 0.11488 | 0.10991 | -0.37743 | -0.29932 | -0.048754 | -0.17954 | 0.058497 | -0.049267 | -0.000513 | -0.1025 | -0.21834 | 124.1657 | 123.9191 | 123.9972 | 67.3018 | -124.2916 | 124.117 | 124.1941 | 124.0782 | 67.3191 | -124.3453
258.9062 | 124.4064 | -67.4377 | 56.8497 | 0.049183 | -0.0019697 | 0.00075378 | 0.050285 | -0.0057084 | 0.051741 | 0.07984 | -0.0037909 | -0.0052687 | 0.060999 | 0.023106 | 0.057636 | -65.0533 | -0.13595 | -67.3229 | 56.7234 | 56.486 | 56.5412 | -67.4282 | -67.3884 | -0.12327 | -67.4824 | 56.6747 | 56.7563 | 56.6451 | -67.4957 | 0.009549 | -0.12626 | 2.3845 | 0.11488 | 0.10533 | -0.3637 | -0.30848 | -0.057912 | -0.17496 | 0.04934 | -0.044688 | 0.013224 | -0.093342 | -0.20461 | 124.1612 | 123.9237 | 123.9789 | 67.3018 | -124.2779 | 124.1125 | 124.1941 | 124.0828 | 67.3145 | -124.3453
259.9062 | 124.3973 | -67.4194 | 56.8405 | 0.049183 | 0.0012363 | 0.0018228 | 0.052422 | -0.0035714 | 0.051741 | 0.049318 | -0.0027229 | -0.0041997 | 0.059931 | 0.025243 | 0.058705 | -65.0578 | -0.14511 | -67.3229 | 56.7234 | 56.4768 | 56.5412 | -67.4236 | -67.3792 | -0.137 | -67.4733 | 56.6793 | 56.7517 | 56.6405 | -67.4957 | -0.004182 | -0.1171 | 2.3616 | 0.096566 | 0.10075 | -0.3637 | -0.29932 | -0.076222 | -0.16123 | 0.040187 | -0.053841 | 0.022381 | -0.088766 | -0.20003 | 124.1428 | 123.8962 | 123.9606 | 67.2743 | -124.2641 | 124.0987 | 124.1712 | 124.0599 | 67.2824 | -124.3362
260.9062 | 124.4156 | -67.4332 | 56.8268 | 0.079707 | 0.00016734 | 0.00075378 | 0.051353 | -0.0046394 | 0.05281 | 0.049318 | -0.0016549 | -0.0041997 | 0.059931 | 0.025243 | 0.057636 | -65.0578 | -0.14511 | -67.3229 | 56.728 | 56.4768 | 56.5595 | -67.4236 | -67.3884 | -0.13242 | -67.4779 | 56.6701 | 56.7517 | 56.6405 | -67.4911 | 0.009551 | -0.098791 | 2.3753 | 0.1103 | 0.10075 | -0.34997 | -0.26728 | -0.05791 | -0.15665 | 0.044763 | -0.044687 | 0.013223 | -0.075033 | -0.1863 | 124.1612 | 123.91 | 123.9927 | 67.2881 | -124.2504 | 124.1033 | 124.1849 | 124.0737 | 67.3007 | -124.3179
261.9062 | 124.4476 | -67.3965 | 56.8405 | 0.049183 | -0.00090066 | 0.0028908 | 0.051353 | -0.0067764 | 0.053878 | 0.049318 | -0.0037909 | -0.0052687 | 0.058862 | 0.026311 | 0.058705 | -65.0578 | -0.15427 | -67.3183 | 56.7326 | 56.4814 | 56.5503 | -67.4374 | -67.3792 | -0.137 | -67.4824 | 56.6747 | 56.7563 | 56.6496 | -67.4911 | -0.040808 | -0.10795 | 2.3387 | 0.078255 | 0.11906 | -0.35912 | -0.29017 | -0.094532 | -0.16581 | 0.017298 | -0.085887 | 0.008645 | -0.084187 | -0.19087 | 124.1291 | 123.8779 | 123.9469 | 67.2423 | -124.2779 | 124.0713 | 124.1529 | 124.0462 | 67.2595 | -124.3316
262.9062 | 124.4614 | -67.4103 | 56.8268 | 0.064445 | -0.00090066 | 0.0018228 | 0.05349 | -0.0035714 | 0.05281 | 0.07984 | -0.0048589 | -0.0041997 | 0.059931 | 0.025243 | 0.058705 | -65.0578 | -0.15884 | -67.3229 | 56.728 | 56.4768 | 56.5458 | -67.4236 | -67.3747 | -0.14158 | -67.4733 | 56.6793 | 56.7563 | 56.6267 | -67.4911 | -0.013338 | -0.098791 | 2.3524 | 0.08741 | 0.10075 | -0.34997 | -0.28101 | -0.080799 | -0.14749 | 0.03561 | -0.062997 | 0.017802 | -0.070454 | -0.20003 | 124.1383 | 123.8871 | 123.956 | 67.2514 | -124.2504 | 124.0896 | 124.1666 | 124.037 | 67.2687 | -124.3179
263.9062 | 124.4385 | -67.4194 | 56.8359 | 0.079707 | 0.00016734 | 0.0039598 | 0.05349 | -0.0046394 | 0.050673 | 0.064579 | -0.0037909 | -0.0031317 | 0.060999 | 0.02738 | 0.057636 | -65.0578 | -0.168 | -67.3229 | 56.7234 | 56.4768 | 56.5549 | -67.4328 | -67.3701 | -0.15074 | -67.4824 | 56.6793 | 56.7517 | 56.6405 | -67.4865 | -0.01334 | -0.11252 | 2.3616 | 0.096566 | 0.10991 | -0.35912 | -0.28101 | -0.067064 | -0.15665 | 0.049345 | -0.062998 | 0.004066 | -0.084188 | -0.19545 | 124.1428 | 123.8962 | 123.9744 | 67.2514 | -124.2687 | 124.0987 | 124.1712 | 124.0599 | 67.2687 | -124.3224
264.9062 | 124.4339 | -67.392 | 56.8314 | 0.064445 | -0.00090066 | 0.0018228 | 0.051353 | -0.0035714 | 0.050673 | 0.07984 | -0.0037909 | -0.0041997 | 0.060999 | 0.02738 | 0.056568 | -65.0578 | -0.17716 | -67.3183 | 56.7326 | 56.4677 | 56.5458 | -67.4145 | -67.3747 | -0.1599 | -67.4733 | 56.6747 | 56.7563 | 56.6359 | -67.4819 | -0.02249 | -0.098791 | 2.3341 | 0.073678 | 0.096168 | -0.3637 | -0.28559 | -0.089951 | -0.15665 | 0.0173 | -0.081307 | 0.008644 | -0.075032 | -0.19545 | 124.1245 | 123.8596 | 123.9377 | 67.2148 | -124.2458 | 124.0667 | 124.1483 | 124.0279 | 67.2321 | -124.3133
265.9062 | 124.4156 | -67.4057 | 56.8314 | 0.064445 | -0.00090066 | 0.0018228 | 0.052422 | -0.0057084 | 0.049605 | 0.064579 | -0.0037909 | -0.0041997 | 0.059931 | 0.026311 | 0.058705 | -65.0578 | -0.18174 | -67.3183 | 56.7326 | 56.4814 | 56.5549 | -67.4099 | -67.3701 | -0.16448 | -67.4687 | 56.6793 | 56.7609 | 56.6405 | -67.4911 | -0.004178 | -0.098791 | 2.3479 | 0.087411 | 0.091589 | -0.34997 | -0.27643 | -0.085376 | -0.15207 | 0.035612 | -0.062995 | 0.022381 | -0.070454 | -0.19087 | 124.1383 | 123.8871 | 123.9606 | 67.224 | -124.2412 | 124.085 | 124.1666 | 124.0462 | 67.2412 | -124.3224
266.9062 | 124.4522 | -67.4057 | 56.8405 | 0.064445 | -0.0019697 | 0.0018228 | 0.05349 | -0.0057084 | 0.051741 | 0.07984 | -0.0037909 | -0.0063367 | 0.059931 | 0.025243 | 0.059773 | -65.0578 | -0.1909 | -67.3091 | 56.728 | 56.4814 | 56.5549 | -67.4145 | -67.3792 | -0.16905 | -67.4779 | 56.6747 | 56.7609 | 56.6222 | -67.4865 | -0.008757 | -0.11252 | 2.3479 | 0.096568 | 0.10532 | -0.35912 | -0.28559 | -0.080797 | -0.16581 | 0.026454 | -0.072153 | 0.008644 | -0.079609 | -0.21834 | 124.1337 | 123.8871 | 123.9606 | 67.2148 | -124.255 | 124.0804 | 124.1666 | 124.0279 | 67.2366 | -124.327
267.9062 | 124.3652 | -67.424 | 56.8085 | 0.064445 | 0.00016734 | 0.0039598 | 0.051353 | -0.0046394 | 0.051741 | 0.064579 | -0.0037909 | -0.0063367 | 0.058862 | 0.026311 | 0.058705 | -65.0807 | -0.19547 | -67.3137 | 56.728 | 56.4768 | 56.5503 | -67.4282 | -67.3701 | -0.17363 | -67.4779 | 56.6747 | 56.7701 | 56.6634 | -67.4911 | -0.004184 | -0.080481 | 2.3433 | 0.1103 | 0.11448 | -0.33166 | -0.25812 | -0.067066 | -0.13376 | 0.053922 | -0.053843 | 0.013223 | -0.038409 | -0.14509 | 124.152 | 123.9008 | 123.9744 | 67.2285 | -124.2367 | 124.0987 | 124.1941 | 124.0874 | 67.2504 | -124.2995
268.9062 | 124.4064 | -67.424 | 56.8726 | 0.064445 | -0.00090066 | 0.00075378 | 0.05349 | -0.0057084 | 0.050673 | 0.07984 | -0.0037909 | -0.0041997 | 0.057794 | 0.026311 | 0.058705 | -65.0624 | -0.21379 | -67.3137 | 56.7234 | 56.4768 | 56.5458 | -67.4053 | -67.3655 | -0.17821 | -67.4733 | 56.6747 | 56.7472 | 56.6267 | -67.4819 | 0.01871 | -0.14915 | 2.3616 | 0.1103 | 0.091589 | -0.39575 | -0.32679 | -0.057908 | -0.19785 | 0.058501 | -0.049264 | 0.008644 | -0.12539 | -0.24581 | 124.1474 | 123.9008 | 123.9698 | 67.2102 | -124.2779 | 124.0987 | 124.1712 | 124.0508 | 67.2458 | -124.3545
269.9062 | 124.4247 | -67.4103 | 56.8222 | 0.064445 | -0.0019697 | 0.0028908 | 0.05349 | -0.0067764 | 0.050673 | 0.064579 | -0.0027229 | -0.0041997 | 0.058862 | 0.025243 | 0.059773 | -65.0533 | -0.21379 | -67.3046 | 56.7188 | 56.4768 | 56.5503 | -67.4236 | -67.3655 | -0.19195 | -67.4779 | 56.6701 | 56.7563 | 56.6451 | -67.4911 | -0.013338 | -0.10337 | 2.357 | 0.10572 | 0.11906 | -0.34539 | -0.27186 | -0.080799 | -0.15207 | 0.044768 | -0.067576 | 0.013223 | -0.065877 | -0.17714 | 124.1291 | 123.8871 | 123.9606 | 67.1965 | -124.2458 | 124.0804 | 124.1666 | 124.0553 | 67.2183 | -124.3133
270.9062 | 124.4156 | -67.4103 | 56.8222 | 0.064445 | 0.00016734 | 0.0018228 | 0.051353 | -0.0046394 | 0.051741 | 0.095101 | -0.0027229 | -0.0052687 | 0.059931 | 0.026311 | 0.058705 | -65.0533 | -0.22295 | -67.3091 | 56.728 | 56.4722 | 56.5503 | -67.4236 | -67.3701 | -0.19653 | -67.4779 | 56.6839 | 56.7563 | 56.6313 | -67.4865 | -0.013338 | -0.094214 | 2.357 | 0.10115 | 0.11448 | -0.34997 | -0.27186 | -0.07622 | -0.13834 | 0.040189 | -0.067576 | 0.008644 | -0.065877 | -0.19088 | 124.1383 | 123.8825 | 123.9606 | 67.1873 | -124.2458 | 124.0941 | 124.1666 | 124.0416 | 67.2138 | -124.3087
271.9062 | 124.4293 | -67.4103 | 56.8268 | 0.049183 | 0.00016734 | 0.00075378 | 0.052422 | -0.0046394 | 0.050673 | 0.07984 | -0.0027229 | -0.0063367 | 0.060999 | 0.026311 | 0.059773 | -65.0578 | -0.23668 | -67.3137 | 56.7188 | 56.4677 | 56.5503 | -67.4282 | -67.3655 | -0.21026 | -67.4733 | 56.6747 | 56.7563 | 56.6359 | -67.4911 | -0.017917 | -0.10795 | 2.3524 | 0.096566 | 0.11448 | -0.35913 | -0.27643 | -0.080799 | -0.15207 | 0.044768 | -0.062997 | 0.017802 | -0.070454 | -0.19087 | 124.1291 | 123.8779 | 123.9606 | 67.1736 | -124.255 | 124.085 | 124.1666 | 124.0462 | 67.2 | -124.3179
272.9219 | 124.3652 | -67.4377 | 56.8314 | 0.064445 | -0.00090066 | 0.0018228 | 0.051353 | -0.0046394 | 0.050673 | 0.064579 | -0.0027229 | -0.0063367 | 0.059931 | 0.026311 | 0.057636 | -65.0762 | -0.24584 | -67.3091 | 56.7234 | 56.4722 | 56.5595 | -67.4282 | -67.3655 | -0.21942 | -67.4779 | 56.6793 | 56.7609 | 56.6313 | -67.4865 | 0.009549 | -0.10795 | 2.3616 | 0.12861 | 0.11906 | -0.35912 | -0.27185 | -0.048754 | -0.15207 | 0.072234 | -0.04011 | 0.008644 | -0.070454 | -0.20003 | 124.1612 | 123.91 | 123.9972 | 67.1919 | -124.2596 | 124.117 | 124.1986 | 124.0691 | 67.2183 | -124.3179
273.9062 | 124.4385 | -67.4103 | 56.8314 | 0.049183 | 0.00016734 | 0.00075378 | 0.05349 | -0.0067764 | 0.049605 | 0.049318 | -0.0037909 | -0.0063367 | 0.058862 | 0.026311 | 0.057636 | -65.0533 | -0.26415 | -67.3091 | 56.728 | 56.4814 | 56.5549 | -67.4374 | -67.3655 | -0.23316 | -67.4733 | 56.6793 | 56.7563 | 56.668 | -67.4865 | -0.027075 | -0.10337 | 2.357 | 0.10115 | 0.12822 | -0.34997 | -0.27643 | -0.07622 | -0.15207 | 0.044768 | -0.062997 | 0.013223 | -0.075032 | -0.1634 | 124.1383 | 123.8917 | 123.9652 | 67.1461 | -124.2687 | 124.0896 | 124.1666 | 124.0782 | 67.1771 | -124.3179
274.9062 | 124.379 | -67.4149 | 56.8771 | 0.064445 | -0.00090066 | 0.0018228 | 0.050285 | -0.0046394 | 0.051741 | 0.064579 | -0.0027229 | -0.0052687 | 0.058862 | 0.025243 | 0.057636 | -65.067 | -0.26873 | -67.3091 | 56.7234 | 56.4722 | 56.5503 | -67.4145 | -67.3701 | -0.23773 | -67.4687 | 56.6793 | 56.7563 | 56.6359 | -67.4865 | 0.000398 | -0.15372 | 2.3479 | 0.10572 | 0.10532 | -0.4049 | -0.32679 | -0.071642 | -0.19785 | 0.044767 | -0.05384 | 0.017802 | -0.12081 | -0.24123 | 124.1383 | 123.8871 | 123.9652 | 67.1461 | -124.2916 | 124.0941 | 124.1712 | 124.0508 | 67.1771 | -124.3636
275.9062 | 124.3744 | -67.424 | 56.8268 | 0.064445 | -0.00090066 | 0.0039598 | 0.052422 | -0.0057084 | 0.050673 | 0.07984 | -0.0027229 | -0.0041997 | 0.059931 | 0.026311 | 0.058705 | -65.0624 | -0.28247 | -67.3137 | 56.7234 | 56.4768 | 56.5503 | -67.419 | -67.3655 | -0.25605 | -67.4733 | 56.6793 | 56.7563 | 56.6313 | -67.4865 | 0.004974 | -0.10337 | 2.3616 | 0.1103 | 0.10533 | -0.34997 | -0.27643 | -0.062487 | -0.14749 | 0.058501 | -0.049264 | 0.013223 | -0.070454 | -0.19545 | 124.1474 | 123.9008 | 123.9744 | 67.1415 | -124.2458 | 124.1033 | 124.1803 | 124.0553 | 67.168 | -124.3133
276.9062 | 124.4064 | -67.3965 | 56.8314 | 0.064445 | -0.00090066 | 0.0018228 | 0.05349 | -0.0057084 | 0.048536 | 0.064579 | -0.0027229 | -0.0063367 | 0.059931 | 0.026311 | 0.058705 | -65.0578 | -0.30078 | -67.3137 | 56.728 | 56.4722 | 56.5458 | -67.4053 | -67.3564 | -0.26978 | -67.4687 | 56.6839 | 56.7609 | 56.6313 | -67.4819 | -0.008756 | -0.10337 | 2.3387 | 0.082833 | 0.091589 | -0.35912 | -0.28559 | -0.085374 | -0.14749 | 0.040192 | -0.072151 | 0.013223 | -0.070454 | -0.20003 | 124.1245 | 123.8688 | 123.9423 | 67.0958 | -124.2367 | 124.0804 | 124.1575 | 124.0279 | 67.1268 | -124.3133
277.9219 | 124.379 | -67.4469 | 56.8451 | 0.049183 | -0.0019697 | 0.0039598 | 0.052422 | -0.0035714 | 0.050673 | 0.07984 | -0.0027229 | -0.0074047 | 0.059931 | 0.026311 | 0.057636 | -65.0624 | -0.31452 | -67.3091 | 56.7234 | 56.4814 | 56.5595 | -67.4236 | -67.3655 | -0.28352 | -67.4779 | 56.6701 | 56.7609 | 56.6634 | -67.4865 | 0.023283 | -0.12168 | 2.3845 | 0.13777 | 0.11448 | -0.3637 | -0.28559 | -0.039599 | -0.17496 | 0.081389 | -0.030955 | 0.008644 | -0.084187 | -0.18171 | 124.1703 | 123.9283 | 124.0064 | 67.1324 | -124.2687 | 124.117 | 124.2078 | 124.1103 | 67.1634 | -124.3316
278.9062 | 124.4247 | -67.4011 | 56.9092 | 0.049183 | 0.0012363 | 0.00075378 | 0.05349 | -0.0057084 | 0.049605 | 0.064579 | -0.0037909 | -0.0041997 | 0.060999 | 0.02738 | 0.058705 | -65.0624 | -0.3191 | -67.3137 | 56.7188 | 56.4814 | 56.5503 | -67.4236 | -67.3655 | -0.29726 | -67.4779 | 56.6793 | 56.7563 | 56.6588 | -67.4911 | -0.022493 | -0.19035 | 2.3387 | 0.087411 | 0.1099 | -0.42779 | -0.35883 | -0.089954 | -0.22989 | 0.035613 | -0.076731 | 0.013223 | -0.15285 | -0.25038 | 124.12 | 123.8825 | 123.9515 | 67.082 | -124.3328 | 124.0804 | 124.1575 | 124.0599 | 67.1039 | -124.4003
279.9688 | 124.4888 | -67.4149 | 56.8039 | 0.049183 | -0.00090066 | 0.0028908 | 0.052422 | -0.0067764 | 0.051741 | 0.064579 | -0.0027229 | -0.0041997 | 0.058862 | 0.02738 | 0.057636 | -65.1586 | -0.33741 | -67.3091 | 56.7234 | 56.4814 | 56.5503 | -67.4145 | -67.3609 | -0.31099 | -67.4779 | 56.6701 | 56.7609 | 56.6496 | -67.4865 | 0.000398 | -0.080481 | 2.2563 | 0.10572 | 0.10532 | -0.3225 | -0.25355 | -0.071642 | -0.13376 | 0.053924 | -0.062998 | 0.008644 | -0.042988 | -0.15425 | 124.1383 | 123.8962 | 123.9652 | 67.0774 | -124.2184 | 124.085 | 124.1758 | 124.0645 | 67.1039 | -124.2904
280.9062 | 124.3286 | -67.4149 | 56.8359 | 0.064445 | -0.00090066 | 0.0018228 | 0.052422 | -0.0057084 | 0.051741 | 0.07984 | -0.0027229 | -0.0052687 | 0.058862 | 0.02738 | 0.057636 | -65.0578 | -0.34657 | -67.3091 | 56.7234 | 56.4906 | 56.5549 | -67.4282 | -67.3655 | -0.32473 | -67.4687 | 56.6747 | 56.7609 | 56.6451 | -67.4957 | -0.013339 | -0.11252 | 2.357 | 0.10572 | 0.11906 | -0.34539 | -0.28101 | -0.0808 | -0.16123 | 0.049346 | -0.05384 | 0.02696 | -0.075031 | -0.19087 | 124.1383 | 123.9054 | 123.9698 | 67.0683 | -124.2641 | 124.0896 | 124.1758 | 124.0599 | 67.0901 | -124.3316
281.9062 | 124.4156 | -67.3965 | 56.8726 | 0.064445 | -0.00090066 | 0.0039598 | 0.052422 | -0.0078444 | 0.050673 | 0.07984 | -0.0027229 | -0.0041997 | 0.060999 | 0.02738 | 0.057636 | -65.0807 | -0.36488 | -67.3046 | 56.7188 | 56.4814 | 56.5503 | -67.4282 | -67.3747 | -0.33847 | -67.4687 | 56.6747 | 56.7655 | 56.6588 | -67.4865 | -0.03165 | -0.15373 | 2.3158 | 0.09199 | 0.12364 | -0.39117 | -0.32221 | -0.089953 | -0.19785 | 0.021877 | -0.072151 | 0.017802 | -0.10707 | -0.21376 | 124.1154 | 123.8779 | 123.9469 | 67.0317 | -124.3008 | 124.0713 | 124.162 | 124.0553 | 67.0581 | -124.3591
282.9219 | 124.3835 | -67.4194 | 56.8451 | 0.033921 | -0.0019697 | 0.0018228 | 0.05349 | -0.0057084 | 0.050673 | 0.064579 | -0.0037909 | -0.0052687 | 0.059931 | 0.026311 | 0.058705 | -65.0578 | -0.38777 | -67.3091 | 56.728 | 56.4814 | 56.5641 | -67.4236 | -67.3655 | -0.36136 | -67.4687 | 56.6747 | 56.7563 | 56.6588 | -67.4865 | -0.004182 | -0.1171 | 2.3616 | 0.1103 | 0.11448 | -0.3637 | -0.28101 | -0.067064 | -0.17038 | 0.053924 | -0.049262 | 0.017802 | -0.088765 | -0.18629 | 124.1474 | 123.9008 | 123.9835 | 67.0317 | -124.2687 | 124.0941 | 124.1758 | 124.0782 | 67.0581 | -124.3316
283.9062 | 124.3835 | -67.3874 | 56.8542 | 0.049183 | -0.00090066 | 0.0028908 | 0.05349 | -0.0057084 | 0.051741 | 0.064579 | -0.0027229 | -0.0074047 | 0.059931 | 0.02738 | 0.057636 | -65.0716 | -0.39235 | -67.3046 | 56.7234 | 56.486 | 56.5549 | -67.4236 | -67.3655 | -0.3751 | -67.4687 | 56.6884 | 56.7517 | 56.6313 | -67.4865 | -0.036226 | -0.13083 | 2.3158 | 0.082835 | 0.11906 | -0.36828 | -0.29932 | -0.099108 | -0.1658 | 0.02188 | -0.081306 | 0.017802 | -0.1025 | -0.22292 | 124.1108 | 123.8734 | 123.9423 | 66.995 | -124.2779 | 124.0758 | 124.1391 | 124.0187 | 67.0123 | -124.3407
284.9062 | 124.3881 | -67.4332 | 56.8405 | 0.079707 | -0.0019697 | 0.0028908 | 0.052422 | -0.0035714 | 0.050673 | 0.064579 | -0.0037909 | -0.0052687 | 0.057794 | 0.026311 | 0.056568 | -65.0533 | -0.41525 | -67.3091 | 56.728 | 56.4768 | 56.5458 | -67.4328 | -67.3655 | -0.39341 | -67.4687 | 56.6747 | 56.7609 | 56.6359 | -67.4911 | 0.000393 | -0.11252 | 2.3799 | 0.12403 | 0.12364 | -0.3637 | -0.29475 | -0.05791 | -0.16581 | 0.067657 | -0.035529 | 0.022381 | -0.079609 | -0.20461 | 124.1612 | 123.91 | 123.9789 | 67.0179 | -124.2733 | 124.1079 | 124.1941 | 124.0691 | 67.0398 | -124.3316
285.9062 | 124.4614 | -67.3737 | 56.8176 | 0.079707 | 0.00016734 | 0.0018228 | 0.052422 | -0.0067764 | 0.049605 | 0.049318 | -0.0027229 | -0.0041997 | 0.058862 | 0.02738 | 0.056568 | -65.0807 | -0.43814 | -67.3046 | 56.7188 | 56.4906 | 56.5595 | -67.419 | -67.3609 | -0.40257 | -67.4733 | 56.6793 | 56.7563 | 56.668 | -67.4865 | -0.04538 | -0.098793 | 2.2929 | 0.069102 | 0.11448 | -0.32708 | -0.25812 | -0.11284 | -0.13834 | 0.012725 | -0.099618 | 0.013223 | -0.061299 | -0.14967 | 124.0925 | 123.8642 | 123.9332 | 66.9355 | -124.2367 | 124.0529 | 124.13 | 124.0416 | 66.9711 | -124.3041
286.9062 | 124.4293 | -67.3965 | 56.8359 | 0.049183 | -0.0019697 | 0.0039598 | 0.052422 | -0.0057084 | 0.049605 | 0.064579 | -0.0037909 | -0.0041997 | 0.058862 | 0.02738 | 0.058705 | -65.0441 | -0.45188 | -67.3046 | 56.7234 | 56.4814 | 56.5595 | -67.4236 | -67.3564 | -0.42088 | -67.4687 | 56.6701 | 56.7563 | 56.6542 | -67.4773 | -0.027071 | -0.11252 | 2.3524 | 0.09199 | 0.11906 | -0.35454 | -0.27643 | -0.080795 | -0.16581 | 0.040192 | -0.072151 | 0.008644 | -0.079609 | -0.18172 | 124.12 | 123.8779 | 123.9561 | 66.9447 | -124.2596 | 124.0667 | 124.1529 | 124.0508 | 66.9757 | -124.3133
287.9219 | 124.4659 | -67.4057 | 56.7947 | 0.064445 | 0.00016734 | 0.0018228 | 0.051353 | -0.0046394 | 0.050673 | 0.049318 | -0.0048589 | -0.0063367 | 0.059931 | 0.028448 | 0.057636 | -65.0945 | -0.47477 | -67.3046 | 56.7371 | 56.4768 | 56.5503 | -67.419 | -67.3564 | -0.43462 | -67.4687 | 56.6793 | 56.7563 | 56.6405 | -67.4911 | -0.013336 | -0.057591 | 2.3112 | 0.10115 | 0.11448 | -0.31793 | -0.24439 | -0.085376 | -0.11545 | 0.049348 | -0.062995 | 0.022381 | -0.038411 | -0.15425 | 124.1428 | 123.8825 | 123.956 | 66.9309 | -124.2138 | 124.085 | 124.162 | 124.0462 | 66.9711 | -124.2858
288.9062 | 124.4888 | -67.3553 | 56.8359 | 0.049183 | -0.0030377 | 0.0028908 | 0.051353 | -0.0067764 | 0.049605 | 0.064579 | -0.0037909 | -0.0063367 | 0.059931 | 0.028448 | 0.057636 | -65.0853 | -0.47935 | -67.3046 | 56.7326 | 56.4814 | 56.5549 | -67.4145 | -67.3609 | -0.45751 | -67.4687 | 56.6793 | 56.7609 | 56.6405 | -67.4865 | -0.059111 | -0.10337 | 2.27 | 0.050792 | 0.1099 | -0.35454 | -0.28101 | -0.13115 | -0.15665 | -0.005585 | -0.11335 | 0.017802 | -0.075031 | -0.19545 | 124.0879 | 123.8367 | 123.9103 | 66.876 | -124.2504 | 124.0346 | 124.1163 | 123.9958 | 66.8978 | -124.3224
289.9062 | 124.379 | -67.3279 | 56.8176 | 0.079707 | 0.00016734 | 0.0018228 | 0.052422 | -0.0057084 | 0.050673 | 0.064579 | -0.0037909 | -0.0041997 | 0.059931 | 0.026311 | 0.056568 | -65.1082 | -0.49766 | -67.2954 | 56.728 | 56.4906 | 56.5503 | -67.4099 | -67.3655 | -0.47125 | -67.4595 | 56.6793 | 56.7563 | 56.6451 | -67.4819 | -0.081998 | -0.089636 | 2.2197 | 0.032483 | 0.11448 | -0.32708 | -0.26728 | -0.15404 | -0.13834 | -0.037629 | -0.13166 | 0.02238 | -0.061299 | -0.17256 | 124.0559 | 123.8184 | 123.8782 | 66.8302 | -124.2275 | 124.0072 | 124.0842 | 123.9729 | 66.8566 | -124.2995
290.9062 | 124.4843 | -67.3508 | 56.8176 | 0.049183 | -0.00090066 | 0.0018228 | 0.050285 | -0.0057084 | 0.050673 | 0.07984 | -0.0027229 | -0.0052687 | 0.057794 | 0.02738 | 0.056568 | -65.099 | -0.52055 | -67.3046 | 56.7326 | 56.4814 | 56.5549 | -67.4099 | -67.3609 | -0.48956 | -67.4687 | 56.6839 | 56.7517 | 56.6588 | -67.4865 | -0.05911 | -0.085058 | 2.2517 | 0.046214 | 0.10532 | -0.33623 | -0.2627 | -0.13573 | -0.13376 | -0.010163 | -0.11793 | 0.017802 | -0.065878 | -0.15883 | 124.0833 | 123.8322 | 123.9057 | 66.8302 | -124.2275 | 124.0346 | 124.1025 | 124.0096 | 66.8612 | -124.3041
291.9062 | 124.4614 | -67.3462 | 56.8497 | 0.049183 | -0.0051747 | -0.00031422 | 0.052422 | -0.0035714 | 0.051741 | 0.064579 | -0.0027229 | -0.0063367 | 0.058862 | 0.028448 | 0.056568 | -65.0807 | -0.53887 | -67.3046 | 56.7326 | 56.4814 | 56.5549 | -67.4145 | -67.3518 | -0.5033 | -67.4595 | 56.6747 | 56.7563 | 56.6405 | -67.4819 | -0.068267 | -0.1171 | 2.2655 | 0.041636 | 0.1099 | -0.36828 | -0.29474 | -0.13573 | -0.17496 | -0.005583 | -0.11335 | 0.02238 | -0.093342 | -0.20919 | 124.0788 | 123.8276 | 123.9011 | 66.8073 | -124.2641 | 124.0209 | 124.1025 | 123.9867 | 66.8429 | -124.3316
292.9219 | 124.4843 | -67.3874 | 56.8222 | 0.049183 | -0.00090066 | 0.00075378 | 0.051353 | -0.0057084 | 0.05281 | 0.07984 | -0.0037909 | -0.0041997 | 0.060999 | 0.029517 | 0.057636 | -65.1403 | -0.5526 | -67.3 | 56.7234 | 56.4814 | 56.5549 | -67.4099 | -67.3564 | -0.52619 | -67.455 | 56.6793 | 56.7609 | 56.6313 | -67.4773 | -0.022489 | -0.098792 | 2.2471 | 0.087413 | 0.1099 | -0.34081 | -0.26728 | -0.08995 | -0.14292 | 0.031037 | -0.06757 | 0.02238 | -0.061299 | -0.19088 | 124.1108 | 123.8688 | 123.9423 | 66.8348 | -124.2321 | 124.0667 | 124.1483 | 124.0187 | 66.8612 | -124.2995
293.9062 | 124.5026 | -67.337 | 56.8176 | 0.064445 | 0.00016734 | 0.00075378 | 0.051353 | -0.0057084 | 0.048536 | 0.064579 | -0.0037909 | -0.0063367 | 0.058862 | 0.028448 | 0.058705 | -65.1128 | -0.57092 | -67.3046 | 56.728 | 56.486 | 56.5549 | -67.4145 | -67.3472 | -0.53077 | -67.4595 | 56.6793 | 56.7609 | 56.6451 | -67.4819 | -0.077422 | -0.089636 | 2.2243 | 0.032481 | 0.1099 | -0.33166 | -0.2627 | -0.14488 | -0.13834 | -0.01016 | -0.1225 | 0.02238 | -0.056721 | -0.17256 | 124.065 | 123.823 | 123.892 | 66.7661 | -124.2321 | 124.0163 | 124.0979 | 123.9821 | 66.8063 | -124.2995
294.9219 | 124.4751 | -67.3691 | 56.8542 | 0.049183 | -0.00090066 | 0.0039598 | 0.051353 | -0.0057084 | 0.050673 | 0.07984 | -0.0048589 | -0.0052687 | 0.059931 | 0.028448 | 0.058705 | -65.0853 | -0.59381 | -67.2908 | 56.7234 | 56.4814 | 56.5595 | -67.4099 | -67.3518 | -0.55824 | -67.4595 | 56.6793 | 56.7563 | 56.6359 | -67.4819 | -0.040799 | -0.13083 | 2.2838 | 0.07826 | 0.11906 | -0.37286 | -0.29474 | -0.11284 | -0.17496 | 0.017306 | -0.090459 | 0.02238 | -0.09792 | -0.21834 | 124.0925 | 123.8505 | 123.9286 | 66.7753 | -124.2641 | 124.0484 | 124.1254 | 124.005 | 66.8108 | -124.3362
295.9062 | 124.4385 | -67.3462 | 56.8726 | 0.079707 | -0.00090066 | 0.0028908 | 0.051353 | -0.0046394 | 0.051741 | 0.07984 | -0.0027229 | -0.0041997 | 0.059931 | 0.028448 | 0.057636 | -65.0716 | -0.6167 | -67.2817 | 56.728 | 56.4768 | 56.5503 | -67.4099 | -67.3472 | -0.5674 | -67.4641 | 56.6793 | 56.7563 | 56.6588 | -67.4728 | -0.063688 | -0.14457 | 2.2746 | 0.064527 | 0.12821 | -0.39575 | -0.32221 | -0.12657 | -0.19327 | -0.001005 | -0.11793 | 0.008644 | -0.11623 | -0.21376 | 124.0742 | 123.823 | 123.8965 | 66.7295 | -124.2824 | 124.0255 | 124.1025 | 124.005 | 66.7788 | -124.3453
296.9219 | 124.3881 | -67.3874 | 56.8817 | 0.064445 | -0.00090066 | 0.0018228 | 0.05349 | -0.0067764 | 0.049605 | 0.064579 | -0.0027229 | -0.0052687 | 0.057794 | 0.02738 | 0.057636 | -65.067 | -0.63044 | -67.2862 | 56.728 | 56.4814 | 56.5641 | -67.419 | -67.3426 | -0.5903 | -67.4595 | 56.6747 | 56.7563 | 56.6542 | -67.4819 | -0.031647 | -0.15372 | 2.3204 | 0.10115 | 0.1328 | -0.40032 | -0.31763 | -0.094529 | -0.20701 | 0.044773 | -0.072149 | 0.02238 | -0.12539 | -0.22749 | 124.1154 | 123.8688 | 123.9515 | 66.7569 | -124.3008 | 124.0621 | 124.1437 | 124.0416 | 66.7971 | -124.3636
297.9375 | 124.5071 | -67.3416 | 56.8359 | 0.064445 | -0.0041057 | 0.0018228 | 0.051353 | -0.0046394 | 0.051741 | 0.064579 | -0.0037909 | -0.0031317 | 0.057794 | 0.030585 | 0.058705 | -65.1128 | -0.64875 | -67.2817 | 56.728 | 56.4768 | 56.5503 | -67.419 | -67.338 | -0.60403 | -67.4595 | 56.6747 | 56.7655 | 56.6634 | -67.4819 | -0.077423 | -0.10795 | 2.2288 | 0.05995 | 0.13737 | -0.35912 | -0.28559 | -0.1403 | -0.16123 | 0.003576 | -0.11792 | 0.02238 | -0.070452 | -0.17256 | 124.0696 | 123.8184 | 123.892 | 66.6929 | -124.255 | 124.0163 | 124.1071 | 124.005 | 66.7376 | -124.3179
298.9219 | 124.3835 | -67.3874 | 56.8588 | 0.064445 | 0.00016734 | 0.0018228 | 0.05349 | -0.0057084 | 0.048536 | 0.07984 | -0.0037909 | -0.0052687 | 0.058862 | 0.029517 | 0.056568 | -65.0533 | -0.68538 | -67.2817 | 56.7371 | 56.4768 | 56.5549 | -67.419 | -67.3426 | -0.63608 | -67.4641 | 56.6747 | 56.7563 | 56.6359 | -67.4819 | -0.031647 | -0.12168 | 2.3341 | 0.10573 | 0.13737 | -0.38201 | -0.3039 | -0.094529 | -0.18412 | 0.044773 | -0.076728 | 0.017801 | -0.1025 | -0.22292 | 124.1245 | 123.8642 | 123.9423 | 66.702 | -124.2779 | 124.0621 | 124.1437 | 124.0233 | 66.7513 | -124.3407
299.9062 | 124.4659 | -67.3782 | 56.7902 | 0.033921 | -0.0019697 | 0.0018228 | 0.050285 | -0.0067764 | 0.050673 | 0.049318 | -0.0016549 | -0.0052687 | 0.057794 | 0.030585 | 0.056568 | -65.0945 | -0.70828 | -67.2817 | 56.728 | 56.4814 | 56.5549 | -67.419 | -67.3426 | -0.6544 | -67.4595 | 56.6839 | 56.7563 | 56.6359 | -67.4773 | -0.040802 | -0.06217 | 2.2838 | 0.096571 | 0.13737 | -0.30877 | -0.23523 | -0.099105 | -0.10629 | 0.035618 | -0.081304 | 0.017801 | -0.033833 | -0.15425 | 124.1062 | 123.8596 | 123.9332 | 66.67 | -124.2092 | 124.0621 | 124.1346 | 124.0141 | 66.7238 | -124.2675
300.9219 | 124.5026 | -67.3737 | 56.8268 | 0.064445 | -0.0019697 | 0.0028908 | 0.05349 | -0.0057084 | 0.051741 | 0.064579 | -0.0027229 | -0.0041997 | 0.059931 | 0.028448 | 0.057636 | -65.1311 | -0.74491 | -67.2908 | 56.7326 | 56.4814 | 56.5641 | -67.4099 | -67.3472 | -0.67729 | -67.4504 | 56.6839 | 56.7517 | 56.6542 | -67.4819 | -0.036222 | -0.094213 | 2.2426 | 0.082837 | 0.11906 | -0.34539 | -0.2627 | -0.10826 | -0.14292 | 0.026461 | -0.076724 | 0.031538 | -0.075033 | -0.17256 | 124.1062 | 123.855 | 123.9377 | 66.6288 | -124.2367 | 124.0575 | 124.1254 | 124.0279 | 66.6964 | -124.3087
301.9062 | 124.4934 | -67.3599 | 56.8451 | 0.049183 | -0.0030377 | 0.0018228 | 0.05349 | -0.0057084 | 0.050673 | 0.064579 | -0.0027229 | -0.0063367 | 0.059931 | 0.028448 | 0.059773 | -65.1265 | -0.76322 | -67.2817 | 56.7326 | 56.486 | 56.5549 | -67.4099 | -67.3426 | -0.70476 | -67.4595 | 56.6839 | 56.7609 | 56.6496 | -67.4728 | -0.049955 | -0.11252 | 2.2334 | 0.07826 | 0.12821 | -0.35912 | -0.29017 | -0.11284 | -0.16123 | 0.017307 | -0.099615 | 0.013223 | -0.084187 | -0.19545 | 124.0925 | 123.8459 | 123.9149 | 66.5967 | -124.255 | 124.0438 | 124.1208 | 124.0096 | 66.6552 | -124.3179
302.9375 | 124.4614 | -67.3462 | 56.8314 | 0.064445 | -0.00090066 | 0.0028908 | 0.051353 | -0.0089134 | 0.051741 | 0.07984 | -0.0048589 | -0.0063367 | 0.057794 | 0.028448 | 0.058705 | -65.0762 | -0.78153 | -67.2954 | 56.728 | 56.4906 | 56.5641 | -67.4053 | -67.3426 | -0.74139 | -67.455 | 56.6884 | 56.7517 | 56.6542 | -67.4819 | -0.05911 | -0.10337 | 2.27 | 0.050793 | 0.1099 | -0.34081 | -0.26727 | -0.13573 | -0.14292 | 0.003574 | -0.10877 | 0.026959 | -0.079611 | -0.17714 | 124.0742 | 123.8367 | 123.9103 | 66.5647 | -124.2367 | 124.0346 | 124.0979 | 124.0004 | 66.6048 | -124.3133
303.9062 | 124.4843 | -67.3553 | 56.813 | 0.079707 | -0.0019697 | 0.0028908 | 0.051353 | -0.0057084 | 0.051741 | 0.07984 | -0.0037909 | -0.0063367 | 0.057794 | 0.029517 | 0.056568 | -65.0762 | -0.81359 | -67.2954 | 56.7234 | 56.4906 | 56.5595 | -67.4099 | -67.338 | -0.75971 | -67.455 | 56.6793 | 56.7655 | 56.6588 | -67.4728 | -0.054532 | -0.089636 | 2.2792 | 0.059949 | 0.11448 | -0.3225 | -0.25354 | -0.11742 | -0.13376 | 0.017309 | -0.099613 | 0.017802 | -0.047564 | -0.15425 | 124.0788 | 123.8459 | 123.9149 | 66.5418 | -124.2229 | 124.0346 | 124.1208 | 124.0141 | 66.5956 | -124.2858
304.9219 | 124.4293 | -67.3599 | 56.8314 | 0.049183 | -0.0019697 | 0.0018228 | 0.051353 | -0.0046394 | 0.051741 | 0.064579 | -0.0048589 | -0.0041997 | 0.057794 | 0.030585 | 0.057636 | -65.1174 | -0.84106 | -67.2954 | 56.728 | 56.4814 | 56.5641 | -67.4145 | -67.3472 | -0.79634 | -67.455 | 56.6884 | 56.7563 | 56.6725 | -67.4773 | -0.054534 | -0.10337 | 2.2426 | 0.064526 | 0.11906 | -0.34997 | -0.26727 | -0.11742 | -0.14292 | 0.012728 | -0.095036 | 0.02238 | -0.075032 | -0.15882 | 124.0879 | 123.8413 | 123.924 | 66.5189 | -124.2458 | 124.0484 | 124.1163 | 124.0325 | 66.5636 | -124.3087
305.9219 | 124.4431 | -67.392 | 56.8176 | 0.064445 | -0.0019697 | 0.0039598 | 0.050285 | -0.0057084 | 0.049605 | 0.064579 | -0.0037909 | -0.0052687 | 0.058862 | 0.028448 | 0.057636 | -65.1311 | -0.86395 | -67.2862 | 56.7326 | 56.4906 | 56.5641 | -67.4099 | -67.3335 | -0.81007 | -67.455 | 56.6747 | 56.7655 | 56.6359 | -67.4773 | -0.017911 | -0.085058 | 2.2609 | 0.10573 | 0.12364 | -0.32708 | -0.25354 | -0.085372 | -0.14292 | 0.058508 | -0.062992 | 0.02238 | -0.052142 | -0.18172 | 124.1245 | 123.8825 | 123.9561 | 66.528 | -124.2275 | 124.0667 | 124.1575 | 124.0279 | 66.5819 | -124.295
306.9062 | 124.5026 | -67.3462 | 56.7993 | 0.064445 | -0.00090066 | 0.0018228 | 0.051353 | -0.0057084 | 0.050673 | 0.049318 | -0.0027229 | -0.0052687 | 0.058862 | 0.029517 | 0.057636 | -65.0853 | -0.88684 | -67.2817 | 56.7326 | 56.486 | 56.5549 | -67.4099 | -67.338 | -0.83754 | -67.455 | 56.6884 | 56.7609 | 56.6771 | -67.4728 | -0.063688 | -0.066747 | 2.2609 | 0.064527 | 0.12821 | -0.31334 | -0.24439 | -0.12657 | -0.11087 | 0.008153 | -0.10877 | 0.017802 | -0.03841 | -0.1222 | 124.0788 | 123.8322 | 123.9011 | 66.4593 | -124.2092 | 124.0346 | 124.1071 | 124.0233 | 66.5086 | -124.2721
307.9219 | 124.3515 | -67.4057 | 56.8451 | 0.049183 | 0.00016734 | 0.0018228 | 0.05349 | -0.0035714 | 0.050673 | 0.064579 | -0.0048589 | -0.0041997 | 0.057794 | 0.031653 | 0.056568 | -65.0304 | -0.92347 | -67.2862 | 56.7326 | 56.4906 | 56.5549 | -67.419 | -67.338 | -0.8696 | -67.455 | 56.6839 | 56.7609 | 56.6405 | -67.4773 | -0.013336 | -0.11252 | 2.3753 | 0.11946 | 0.1328 | -0.35454 | -0.29017 | -0.071639 | -0.16123 | 0.067663 | -0.049259 | 0.02238 | -0.084187 | -0.20461 | 124.1383 | 123.8963 | 123.9606 | 66.4822 | -124.2641 | 124.0896 | 124.1666 | 124.0462 | 66.5361 | -124.3224
308.9219 | 124.4705 | -67.3599 | 56.7993 | 0.049183 | -0.00090066 | 0.0028908 | 0.051353 | -0.0046394 | 0.050673 | 0.049318 | -0.0048589 | -0.0041997 | 0.060999 | 0.029517 | 0.057636 | -65.1036 | -0.94636 | -67.2908 | 56.7326 | 56.486 | 56.5595 | -67.4007 | -67.3289 | -0.89707 | -67.455 | 56.693 | 56.7655 | 56.6771 | -67.4773 | -0.040798 | -0.066747 | 2.2563 | 0.069104 | 0.1099 | -0.31334 | -0.23981 | -0.11742 | -0.10629 | 0.031043 | -0.095036 | 0.02238 | -0.033831 | -0.1222 | 124.0925 | 123.8459 | 123.9194 | 66.4136 | -124.2 | 124.0529 | 124.1254 | 124.037 | 66.4629 | -124.2767
309.9062 | 124.4522 | -67.3874 | 56.813 | 0.064445 | -0.0019697 | 0.0039598 | 0.052422 | -0.0057084 | 0.050673 | 0.064579 | -0.0048589 | -0.0052687 | 0.059931 | 0.028448 | 0.057636 | -65.0624 | -0.96926 | -67.2817 | 56.7371 | 56.4997 | 56.5641 | -67.4145 | -67.338 | -0.92454 | -67.4458 | 56.6747 | 56.7655 | 56.6542 | -67.4682 | -0.027068 | -0.075901 | 2.325 | 0.10573 | 0.13279 | -0.31334 | -0.24896 | -0.080793 | -0.13834 | 0.049352 | -0.058413 | 0.02238 | -0.047564 | -0.15883 | 124.1245 | 123.8871 | 123.9515 | 66.4181 | -124.2275 | 124.0621 | 124.1529 | 124.0416 | 66.4629 | -124.2812
310.9219 | 124.4522 | -67.3645 | 56.8268 | 0.064445 | -0.0019697 | 0.0028908 | 0.052422 | -0.0057084 | 0.051741 | 0.049318 | -0.0027229 | -0.0041997 | 0.057794 | 0.031653 | 0.059773 | -65.1036 | -1.0013 | -67.2862 | 56.7326 | 56.4906 | 56.5549 | -67.4099 | -67.338 | -0.95659 | -67.4504 | 56.6884 | 56.7701 | 56.6771 | -67.4773 | -0.045377 | -0.094213 | 2.2609 | 0.07826 | 0.12364 | -0.33623 | -0.27185 | -0.11284 | -0.13834 | 0.026464 | -0.085879 | 0.026959 | -0.056719 | -0.14967 | 124.0971 | 123.8551 | 123.9194 | 66.3632 | -124.2367 | 124.0529 | 124.1346 | 124.0416 | 66.4079 | -124.3041
311.9062 | 124.4659 | -67.3782 | 56.7993 | 0.064445 | -0.0030377 | 0.00075378 | 0.052422 | -0.0078444 | 0.051741 | 0.049318 | -0.0037909 | -0.0052687 | 0.058862 | 0.031653 | 0.056568 | -65.067 | -1.0379 | -67.2908 | 56.728 | 56.4951 | 56.5549 | -67.4053 | -67.3335 | -0.98406 | -67.4458 | 56.6884 | 56.7701 | 56.6542 | -67.4773 | -0.027066 | -0.071325 | 2.3112 | 0.087415 | 0.11448 | -0.30419 | -0.24439 | -0.099105 | -0.11087 | 0.044775 | -0.067568 | 0.031537 | -0.029253 | -0.14509 | 124.1062 | 123.8734 | 123.9332 | 66.3403 | -124.2046 | 124.0667 | 124.1483 | 124.0325 | 66.3942 | -124.2767
312.9219 | 124.3561 | -67.4103 | 56.8222 | 0.033921 | -0.00090066 | 0.00075378 | 0.052422 | -0.0046394 | 0.050673 | 0.064579 | -0.0048589 | -0.0074047 | 0.058862 | 0.029517 | 0.057636 | -65.035 | -1.07 | -67.2862 | 56.7326 | 56.486 | 56.5732 | -67.4099 | -67.3335 | -1.0161 | -67.4412 | 56.6884 | 56.7609 | 56.6542 | -67.4636 | 0.000399 | -0.089636 | 2.3753 | 0.12404 | 0.12364 | -0.33623 | -0.24896 | -0.053326 | -0.13376 | 0.076818 | -0.030946 | 0.02238 | -0.061299 | -0.16798 | 124.1428 | 123.8963 | 123.9835 | 66.3403 | -124.2321 | 124.0987 | 124.1712 | 124.0645 | 66.3942 | -124.2858
313.9219 | 124.4705 | -67.3279 | 56.7856 | 0.049183 | -0.0019697 | 0.0018228 | 0.051353 | -0.0067764 | 0.050673 | 0.049318 | -0.0048589 | -0.0074047 | 0.058862 | 0.031653 | 0.056568 | -65.0853 | -1.0883 | -67.2862 | 56.7326 | 56.4906 | 56.5595 | -67.4007 | -67.3289 | -1.0436 | -67.4458 | 56.6839 | 56.7701 | 56.6588 | -67.4773 | -0.072841 | -0.053014 | 2.2426 | 0.041639 | 0.11448 | -0.29503 | -0.22608 | -0.14946 | -0.10172 | -0.001 | -0.11792 | 0.031537 | -0.01552 | -0.12678 | 124.0605 | 123.8184 | 123.8874 | 66.2396 | -124.1863 | 124.0117 | 124.0979 | 123.9867 | 66.2843 | -124.2629
314.9219 | 124.5163 | -67.3233 | 56.813 | 0.049183 | -0.00090066 | 0.0018228 | 0.051353 | -0.0046394 | 0.049605 | 0.064579 | -0.0027229 | -0.0052687 | 0.056726 | 0.031653 | 0.058705 | -65.1036 | -1.1204 | -67.2908 | 56.7371 | 56.4951 | 56.5595 | -67.4053 | -67.3335 | -1.0802 | -67.4504 | 56.693 | 56.7563 | 56.6771 | -67.4682 | -0.081998 | -0.075901 | 2.2197 | 0.032483 | 0.11448 | -0.31792 | -0.25354 | -0.14488 | -0.12003 | -0.010157 | -0.12708 | 0.017802 | -0.056721 | -0.13593 | 124.0605 | 123.8184 | 123.8828 | 66.203 | -124.2183 | 124.0163 | 124.0796 | 124.0004 | 66.2431 | -124.2812
315.9062 | 124.3561 | -67.3691 | 56.8588 | 0.049183 | -0.00090066 | 0.0018228 | 0.052422 | -0.0078444 | 0.050673 | 0.049318 | -0.0037909 | -0.0052687 | 0.059931 | 0.030585 | 0.056568 | -65.0304 | -1.1524 | -67.2817 | 56.7326 | 56.4906 | 56.5687 | -67.4053 | -67.3289 | -1.1077 | -67.4412 | 56.6884 | 56.7609 | 56.6634 | -67.4682 | -0.036221 | -0.12626 | 2.3387 | 0.087416 | 0.12364 | -0.36827 | -0.29016 | -0.099103 | -0.17038 | 0.040199 | -0.072144 | 0.026959 | -0.09792 | -0.19545 | 124.1016 | 123.8596 | 123.9377 | 66.2167 | -124.2641 | 124.0575 | 124.13 | 124.0325 | 66.2614 | -124.327
316.9219 | 124.4659 | -67.3462 | 56.8359 | 0.049183 | 0.00016734 | 0.0028908 | 0.051353 | -0.0067764 | 0.049605 | 0.07984 | -0.0027229 | -0.0063367 | 0.058862 | 0.031653 | 0.057636 | -65.0853 | -1.1799 | -67.2771 | 56.7326 | 56.4906 | 56.5595 | -67.4053 | -67.3289 | -1.1306 | -67.455 | 56.6793 | 56.7701 | 56.6771 | -67.4682 | -0.05911 | -0.10337 | 2.2609 | 0.069106 | 0.12822 | -0.34539 | -0.27643 | -0.12199 | -0.15665 | 0.01731 | -0.10877 | 0.013223 | -0.065874 | -0.15882 | 124.0788 | 123.8367 | 123.9057 | 66.1663 | -124.2412 | 124.0255 | 124.1163 | 124.0233 | 66.2156 | -124.3041
317.9219 | 124.5392 | -67.3416 | 56.8268 | 0.033921 | -0.00090066 | 0.0028908 | 0.050285 | -0.0067764 | 0.050673 | 0.064579 | -0.0027229 | -0.0063367 | 0.058862 | 0.031653 | 0.056568 | -65.0762 | -1.2119 | -67.2771 | 56.7463 | 56.4951 | 56.5641 | -67.4099 | -67.3243 | -1.1718 | -67.4412 | 56.6976 | 56.7609 | 56.6405 | -67.4682 | -0.068265 | -0.080477 | 2.2655 | 0.064529 | 0.13279 | -0.33165 | -0.2627 | -0.12657 | -0.12918 | 0.017312 | -0.09961 | 0.026959 | -0.065876 | -0.1863 | 124.0879 | 123.8367 | 123.9057 | 66.1297 | -124.2367 | 124.0392 | 124.1025 | 123.9821 | 66.1698 | -124.295
318.9062 | 124.3607 | -67.4103 | 56.8542 | 0.049183 | 0.00016734 | 0.0028908 | 0.051353 | -0.0057084 | 0.048536 | 0.07984 | -0.0048589 | -0.0041997 | 0.057794 | 0.030585 | 0.056568 | -65.0304 | -1.2394 | -67.2725 | 56.7326 | 56.4906 | 56.5687 | -67.4053 | -67.3197 | -1.1947 | -67.4458 | 56.6839 | 56.7701 | 56.6405 | -67.4682 | 0.004977 | -0.12168 | 2.3799 | 0.13777 | 0.13279 | -0.3637 | -0.28558 | -0.057905 | -0.17038 | 0.090555 | -0.035525 | 0.02238 | -0.084185 | -0.21376 | 124.1428 | 123.9008 | 123.9789 | 66.1709 | -124.2595 | 124.0941 | 124.1803 | 124.0508 | 66.2156 | -124.3224
319.9844 | 124.3195 | -67.3782 | 56.8588 | 0.064445 | -0.0030377 | 0.0028908 | 0.051353 | -0.0057084 | 0.050673 | 0.095101 | -0.0016549 | -0.0041997 | 0.057794 | 0.029517 | 0.057636 | -65.0166 | -1.2806 | -67.2771 | 56.7371 | 56.4951 | 56.5732 | -67.4053 | -67.3335 | -1.2267 | -67.4458 | 56.693 | 56.7655 | 56.6405 | -67.4682 | -0.027066 | -0.12168 | 2.3616 | 0.10115 | 0.12822 | -0.3637 | -0.28558 | -0.089948 | -0.1658 | 0.044775 | -0.067568 | 0.02238 | -0.093341 | -0.21834 | 124.1154 | 123.8734 | 123.9515 | 66.0976 | -124.2641 | 124.0713 | 124.1437 | 124.0187 | 66.1515 | -124.327
320.9219 | 124.4888 | -67.3508 | 56.7993 | 0.049183 | -0.0030377 | 0.0028908 | 0.051353 | -0.0057084 | 0.049605 | 0.049318 | -0.0059269 | -0.0052687 | 0.057794 | 0.030585 | 0.057636 | -65.0716 | -1.3035 | -67.2725 | 56.7326 | 56.4906 | 56.5687 | -67.4007 | -67.3243 | -1.2588 | -67.4366 | 56.693 | 56.7746 | 56.668 | -67.4682 | -0.049953 | -0.066747 | 2.2792 | 0.078262 | 0.12821 | -0.30876 | -0.23065 | -0.11741 | -0.10629 | 0.026467 | -0.085876 | 0.031538 | -0.024674 | -0.13136 | 124.0833 | 123.8413 | 123.9194 | 66.0473 | -124.2 | 124.0438 | 124.1254 | 124.0187 | 66.092 | -124.2675
321.9219 | 124.4797 | -67.3599 | 56.8359 | 0.064445 | -0.0019697 | 0.0039598 | 0.050285 | -0.0078444 | 0.050673 | 0.064579 | -0.0027229 | -0.0052687 | 0.058862 | 0.032722 | 0.058705 | -65.1128 | -1.3355 | -67.2634 | 56.7326 | 56.486 | 56.5687 | -67.3961 | -67.3151 | -1.2817 | -67.4412 | 56.6839 | 56.7655 | 56.6451 | -67.4682 | -0.036219 | -0.10337 | 2.2471 | 0.096573 | 0.13279 | -0.34997 | -0.26727 | -0.10826 | -0.15207 | 0.044779 | -0.0813 | 0.026959 | -0.070452 | -0.19087 | 124.0925 | 123.8459 | 123.9286 | 66.0244 | -124.2321 | 124.0438 | 124.1254 | 124.005 | 66.0782 | -124.3041
322.9219 | 124.4522 | -67.3691 | 56.8314 | 0.049183 | -0.0030377 | 0.00075378 | 0.050285 | -0.0057084 | 0.050673 | 0.018796 | -0.0048589 | -0.0063367 | 0.055658 | 0.03379 | 0.0555 | -65.0899 | -1.3676 | -67.2634 | 56.7371 | 56.486 | 56.5687 | -67.4007 | -67.3151 | -1.3183 | -67.4412 | 56.6884 | 56.7701 | 56.6496 | -67.4636 | -0.031642 | -0.094212 | 2.2792 | 0.10573 | 0.13737 | -0.34539 | -0.2627 | -0.094524 | -0.14292 | 0.053935 | -0.072144 | 0.02238 | -0.061297 | -0.18172 | 124.1062 | 123.8551 | 123.9377 | 66.0015 | -124.2321 | 124.0575 | 124.1391 | 124.0187 | 66.0508 | -124.295
323.9062 | 124.3881 | -67.3599 | 56.8726 | 0.033921 | -0.00090066 | 0.0028908 | 0.052422 | -0.0057084 | 0.050673 | 0.049318 | -0.0037909 | -0.0063367 | 0.057794 | 0.032722 | 0.056568 | -65.0029 | -1.4088 | -67.2679 | 56.7463 | 56.4951 | 56.5687 | -67.4099 | -67.3243 | -1.3595 | -67.4458 | 56.6884 | 56.7655 | 56.6634 | -67.4682 | -0.049955 | -0.12625 | 2.357 | 0.091995 | 0.14195 | -0.37743 | -0.3039 | -0.10826 | -0.18412 | 0.035622 | -0.085879 | 0.02238 | -0.10707 | -0.20918 | 124.1062 | 123.8551 | 123.9286 | 65.9511 | -124.2824 | 124.0484 | 124.1254 | 124.0233 | 66.0004 | -124.3407
324.9219 | 124.3607 | -67.4011 | 56.8359 | 0.033921 | -0.0019697 | 0.0018228 | 0.054559 | -0.0057084 | 0.050673 | 0.049318 | -0.0037909 | -0.0052687 | 0.058862 | 0.031653 | 0.056568 | -65.0304 | -1.4409 | -67.2725 | 56.7371 | 56.4951 | 56.5732 | -67.4053 | -67.3151 | -1.3916 | -67.4321 | 56.6884 | 56.7701 | 56.668 | -67.4544 | -0.004178 | -0.098789 | 2.3707 | 0.12862 | 0.13279 | -0.34081 | -0.2627 | -0.053323 | -0.14749 | 0.085978 | -0.030944 | 0.022379 | -0.065874 | -0.16798 | 124.1383 | 123.8963 | 123.9744 | 65.9603 | -124.2412 | 124.0896 | 124.1712 | 124.0691 | 66.0096 | -124.2904
325.9062 | 124.3469 | -67.3965 | 56.8634 | 0.049183 | -0.0019697 | 0.0028908 | 0.051353 | -0.0078444 | 0.049605 | 0.07984 | -0.0048589 | -0.0031317 | 0.057794 | 0.030585 | 0.058705 | -65.0212 | -1.4775 | -67.2679 | 56.7417 | 56.4906 | 56.5687 | -67.3778 | -67.3197 | -1.4145 | -67.4321 | 56.6976 | 56.7746 | 56.6405 | -67.4682 | 0.018718 | -0.12168 | 2.3753 | 0.12862 | 0.1099 | -0.37285 | -0.29474 | -0.071638 | -0.1658 | 0.076822 | -0.035522 | 0.036116 | -0.088761 | -0.22292 | 124.1383 | 123.8871 | 123.9652 | 65.9191 | -124.2412 | 124.0941 | 124.1712 | 124.037 | 65.9821 | -124.3316
326.9219 | 124.53 | -67.3828 | 56.8176 | 0.049183 | -0.0030377 | 0.0018228 | 0.052422 | -0.0078444 | 0.049605 | 0.049318 | -0.0048589 | -0.0063367 | 0.057794 | 0.030585 | 0.058705 | -65.0624 | -1.5095 | -67.2634 | 56.7371 | 56.4906 | 56.5732 | -67.3961 | -67.3106 | -1.4465 | -67.4366 | 56.6839 | 56.7746 | 56.6725 | -67.459 | -0.013331 | -0.080479 | 2.3204 | 0.11946 | 0.13279 | -0.32708 | -0.24439 | -0.076213 | -0.13376 | 0.072246 | -0.053833 | 0.02238 | -0.042985 | -0.14509 | 124.12 | 123.8734 | 123.9561 | 65.8733 | -124.2138 | 124.0667 | 124.1575 | 124.0553 | 65.9363 | -124.2767
327.9375 | 124.4064 | -67.3828 | 56.8359 | 0.049183 | -0.0019697 | 0.0028908 | 0.05349 | -0.0078444 | 0.050673 | 0.034057 | -0.0037909 | -0.0052687 | 0.055658 | 0.032722 | 0.059773 | -65.0304 | -1.5462 | -67.2588 | 56.7417 | 56.4951 | 56.5778 | -67.3961 | -67.3106 | -1.4786 | -67.4366 | 56.693 | 56.7746 | 56.6542 | -67.4636 | -0.013331 | -0.094211 | 2.3524 | 0.12404 | 0.13737 | -0.34081 | -0.25812 | -0.080792 | -0.14291 | 0.072246 | -0.053833 | 0.026959 | -0.061295 | -0.18172 | 124.1245 | 123.8779 | 123.9606 | 65.8367 | -124.2321 | 124.0758 | 124.1575 | 124.037 | 65.9042 | -124.2995
328.9219 | 124.3927 | -67.4103 | 56.8634 | 0.064445 | -0.00090066 | 0.0018228 | 0.050285 | -0.0078444 | 0.051741 | 0.049318 | -0.0027229 | -0.0052687 | 0.058862 | 0.030585 | 0.058705 | -65.0304 | -1.5828 | -67.2634 | 56.7463 | 56.4906 | 56.5778 | -67.3961 | -67.3106 | -1.5152 | -67.4321 | 56.6976 | 56.7701 | 56.6542 | -67.4636 | 0.014135 | -0.1171 | 2.3799 | 0.14693 | 0.13279 | -0.37285 | -0.28558 | -0.053326 | -0.1658 | 0.099712 | -0.021789 | 0.031537 | -0.09334 | -0.20918 | 124.1566 | 123.9008 | 123.9881 | 65.8275 | -124.2595 | 124.1079 | 124.1803 | 124.0645 | 65.8951 | -124.327
329.9062 | 124.3835 | -67.392 | 56.8405 | 0.033921 | -0.00090066 | 0.0028908 | 0.052422 | -0.0067764 | 0.048536 | 0.049318 | -0.0027229 | -0.0052687 | 0.057794 | 0.031653 | 0.0555 | -65.0258 | -1.6057 | -67.2679 | 56.7417 | 56.4906 | 56.5778 | -67.387 | -67.3106 | -1.5381 | -67.4229 | 56.693 | 56.7792 | 56.668 | -67.4636 | 0.004983 | -0.098789 | 2.3662 | 0.12404 | 0.11906 | -0.34996 | -0.26269 | -0.071636 | -0.14749 | 0.081402 | -0.030941 | 0.040695 | -0.061294 | -0.17256 | 124.1337 | 123.8825 | 123.9698 | 65.7863 | -124.2275 | 124.085 | 124.1712 | 124.0599 | 65.8539 | -124.3041
330.9062 | 124.3927 | -67.3782 | 56.8451 | 0.064445 | -0.0019697 | 0.0018228 | 0.051353 | -0.0067764 | 0.048536 | 0.07984 | -0.0037909 | -0.0041997 | 0.058862 | 0.032722 | 0.058705 | -64.9937 | -1.6515 | -67.2588 | 56.7417 | 56.4951 | 56.5687 | -67.3824 | -67.3014 | -1.5656 | -67.4229 | 56.693 | 56.7701 | 56.6771 | -67.4544 | -0.004171 | -0.10337 | 2.3845 | 0.11946 | 0.12363 | -0.34996 | -0.27643 | -0.076211 | -0.15207 | 0.076826 | -0.044674 | 0.031537 | -0.07503 | -0.16798 | 124.12 | 123.8734 | 123.9469 | 65.7268 | -124.2275 | 124.0713 | 124.1483 | 124.0553 | 65.8127 | -124.2995
331.9219 | 124.4614 | -67.337 | 56.8542 | 0.033921 | -0.0019697 | 0.0018228 | 0.051353 | -0.0057084 | 0.050673 | 0.07984 | -0.0048589 | -0.0052687 | 0.057794 | 0.031653 | 0.056568 | -65.0945 | -1.6835 | -67.2588 | 56.7463 | 56.4951 | 56.5778 | -67.3961 | -67.3014 | -1.5793 | -67.4275 | 56.693 | 56.7792 | 56.6817 | -67.459 | -0.059107 | -0.10794 | 2.2426 | 0.078264 | 0.13737 | -0.35912 | -0.27643 | -0.12199 | -0.16123 | 0.035627 | -0.090452 | 0.031537 | -0.075027 | -0.17255 | 124.0833 | 123.8322 | 123.9149 | 65.6535 | -124.2504 | 124.0301 | 124.1163 | 124.0187 | 65.7577 | -124.3133
332.9219 | 124.4476 | -67.3508 | 56.8405 | 0.049183 | -0.0019697 | 0.0028908 | 0.051353 | -0.0046394 | 0.049605 | 0.049318 | -0.0037909 | -0.0063367 | 0.058862 | 0.031653 | 0.057636 | -64.9846 | -1.711 | -67.245 | 56.7417 | 56.4951 | 56.587 | -67.3824 | -67.2968 | -1.5976 | -67.4229 | 56.7022 | 56.7792 | 56.6496 | -67.4544 | -0.031637 | -0.098789 | 2.3662 | 0.10573 | 0.13737 | -0.34539 | -0.25354 | -0.10368 | -0.13834 | 0.053939 | -0.07214 | 0.031537 | -0.061294 | -0.19087 | 124.0925 | 123.8459 | 123.9377 | 65.6398 | -124.2229 | 124.0529 | 124.13 | 124.0004 | 65.7532 | -124.295
333.9062 | 124.3927 | -67.3874 | 56.8726 | 0.049183 | -0.0019697 | 0.0028908 | 0.051353 | -0.0067764 | 0.050673 | 0.07984 | -0.0037909 | -0.0041997 | 0.057794 | 0.031653 | 0.056568 | -64.9525 | -1.7476 | -67.2496 | 56.7555 | 56.5043 | 56.587 | -67.3961 | -67.2923 | -1.6159 | -67.4229 | 56.693 | 56.7884 | 56.6222 | -67.4544 | -0.008753 | -0.1171 | 2.4348 | 0.13777 | 0.14653 | -0.36827 | -0.28558 | -0.067056 | -0.17954 | 0.095139 | -0.035519 | 0.031537 | -0.084181 | -0.25039 | 124.1429 | 123.8917 | 123.9744 | 65.6398 | -124.2687 | 124.0804 | 124.1758 | 124.0096 | 65.7715 | -124.327
334.9062 | 124.3881 | -67.3828 | 56.8726 | 0.049183 | -0.0019697 | 0.0028908 | 0.052422 | -0.0057084 | 0.050673 | 0.064579 | -0.0016549 | -0.0052687 | 0.056726 | 0.034858 | 0.057636 | -64.9434 | -1.7842 | -67.245 | 56.7555 | 56.4997 | 56.5778 | -67.3961 | -67.2968 | -1.6297 | -67.4183 | 56.693 | 56.7838 | 56.6771 | -67.4499 | -0.013331 | -0.1171 | 2.4394 | 0.13778 | 0.15111 | -0.37285 | -0.29474 | -0.067055 | -0.17954 | 0.085982 | -0.035518 | 0.031537 | -0.08876 | -0.19544 | 124.1383 | 123.8825 | 123.9606 | 65.5986 | -124.2687 | 124.0758 | 124.1666 | 124.0599 | 65.7532 | -124.3224
335.9062 | 124.3607 | -67.3874 | 56.8588 | 0.049183 | -0.00090066 | 0.0039598 | 0.05349 | -0.0067764 | 0.050673 | 0.064579 | -0.0037909 | -0.0041997 | 0.057794 | 0.03379 | 0.058705 | -64.9388 | -1.8163 | -67.2313 | 56.7463 | 56.5043 | 56.5824 | -67.3824 | -67.2877 | -1.648 | -67.4138 | 56.693 | 56.7746 | 56.668 | -67.4499 | 0.004984 | -0.11252 | 2.4486 | 0.15609 | 0.1511 | -0.35454 | -0.27643 | -0.062477 | -0.1658 | 0.099718 | -0.026362 | 0.036115 | -0.084184 | -0.19087 | 124.1337 | 123.8917 | 123.9698 | 65.5711 | -124.2412 | 124.0804 | 124.162 | 124.0553 | 65.7394 | -124.3087
336.9219 | 124.4522 | -67.3325 | 56.8451 | 0.064445 | -0.0030377 | 0.00075378 | 0.052422 | -0.0067764 | 0.049605 | 0.095101 | -0.0027229 | -0.0063367 | 0.059931 | 0.034858 | 0.058705 | -65.035 | -1.8483 | -67.2313 | 56.7463 | 56.4997 | 56.5916 | -67.3778 | -67.2831 | -1.6663 | -67.4138 | 56.6976 | 56.7838 | 56.6771 | -67.459 | -0.045369 | -0.098788 | 2.2975 | 0.10116 | 0.14652 | -0.34538 | -0.25354 | -0.12657 | -0.14749 | 0.049364 | -0.081294 | 0.045273 | -0.061294 | -0.16798 | 124.0788 | 123.8322 | 123.924 | 65.4841 | -124.2229 | 124.0301 | 124.1163 | 124.0096 | 65.6662 | -124.3041
337.9219 | 124.4522 | -67.3325 | 56.8268 | 0.049183 | -0.0030377 | 0.0028908 | 0.050285 | -0.0057084 | 0.050673 | 0.049318 | -0.0027229 | -0.0074047 | 0.057794 | 0.03379 | 0.056568 | -65.0212 | -1.8896 | -67.2221 | 56.76 | 56.5043 | 56.5916 | -67.3824 | -67.2831 | -1.6846 | -67.4138 | 56.7113 | 56.7884 | 56.6542 | -67.4453 | -0.049948 | -0.066742 | 2.3112 | 0.11031 | 0.16026 | -0.32249 | -0.23523 | -0.11283 | -0.11545 | 0.049364 | -0.081294 | 0.031537 | -0.038404 | -0.17256 | 124.0925 | 123.8367 | 123.924 | 65.4429 | -124.2092 | 124.0438 | 124.1208 | 123.9867 | 65.6479 | -124.2721
338.9219 | 124.3515 | -67.3691 | 56.8588 | 0.049183 | -0.0030377 | 0.0028908 | 0.051353 | -0.0078444 | 0.051741 | 0.095101 | -0.0027229 | -0.0052687 | 0.056726 | 0.03379 | 0.056568 | -64.9388 | -1.9216 | -67.2359 | 56.76 | 56.5134 | 56.587 | -67.3778 | -67.2785 | -1.7075 | -67.4138 | 56.7113 | 56.7884 | 56.6954 | -67.4453 | -0.008747 | -0.098786 | 2.4303 | 0.1332 | 0.14195 | -0.34538 | -0.27185 | -0.076209 | -0.14749 | 0.090565 | -0.044672 | 0.031537 | -0.070448 | -0.1634 | 124.1291 | 123.8825 | 123.9561 | 65.4475 | -124.2367 | 124.0804 | 124.1575 | 124.0645 | 65.6616 | -124.3041
339.9062 | 124.411 | -67.3691 | 56.8863 | 0.079707 | -0.0019697 | 0.0028908 | 0.05349 | -0.0078444 | 0.049605 | 0.07984 | -0.0037909 | -0.0052687 | 0.057794 | 0.03379 | 0.059773 | -64.9296 | -1.9491 | -67.2313 | 56.7555 | 56.5089 | 56.5916 | -67.3778 | -67.2785 | -1.735 | -67.4046 | 56.7113 | 56.7975 | 56.6954 | -67.4361 | -0.008747 | -0.13083 | 2.4394 | 0.13778 | 0.14652 | -0.37742 | -0.29474 | -0.067051 | -0.17495 | 0.090565 | -0.035514 | 0.031537 | -0.088757 | -0.19086 | 124.1245 | 123.8779 | 123.9606 | 65.42 | -124.2641 | 124.0804 | 124.1666 | 124.0645 | 65.6341 | -124.3224
340.9219 | 124.3149 | -67.4011 | 56.8359 | 0.018659 | -0.0030377 | 0.0018228 | 0.051353 | -0.0067764 | 0.049605 | 0.049318 | -0.0048589 | -0.0063367 | 0.056726 | 0.03379 | 0.057636 | -64.9342 | -1.9811 | -67.2221 | 56.76 | 56.518 | 56.5916 | -67.3824 | -67.2739 | -1.767 | -67.4092 | 56.7068 | 56.7838 | 56.6863 | -67.4453 | 0.018717 | -0.075897 | 2.4669 | 0.17898 | 0.16026 | -0.31791 | -0.24438 | -0.044166 | -0.12918 | 0.12719 | -0.00805 | 0.036116 | -0.052138 | -0.14967 | 124.1612 | 123.9191 | 123.9927 | 65.42 | -124.2183 | 124.1079 | 124.1849 | 124.0874 | 65.6341 | -124.2812
341.9219 | 124.4751 | -67.337 | 56.813 | 0.049183 | -0.0041057 | 0.0028908 | 0.051353 | -0.0057084 | 0.049605 | 0.07984 | -0.0037909 | -0.0041997 | 0.057794 | 0.032722 | 0.056568 | -65.0029 | -1.9994 | -67.2313 | 56.76 | 56.5089 | 56.5961 | -67.3687 | -67.2739 | -1.7945 | -67.4046 | 56.7159 | 56.793 | 56.668 | -67.4316 | -0.031633 | -0.053009 | 2.3341 | 0.10573 | 0.13737 | -0.30418 | -0.21691 | -0.094516 | -0.097134 | 0.0631 | -0.067558 | 0.026958 | -0.020093 | -0.14509 | 124.0971 | 123.8459 | 123.9332 | 65.3376 | -124.1817 | 124.053 | 124.13 | 124.005 | 65.5425 | -124.2446
342.9219 | 124.4614 | -67.3141 | 56.8268 | 0.064445 | -0.0030377 | 0.0028908 | 0.051353 | -0.0057084 | 0.049605 | 0.064579 | -0.0027229 | -0.0052687 | 0.057794 | 0.034858 | 0.0555 | -64.9983 | -2.0315 | -67.2221 | 56.7555 | 56.5134 | 56.5961 | -67.3778 | -67.2648 | -1.8174 | -67.4046 | 56.7113 | 56.793 | 56.7046 | -67.4407 | -0.063679 | -0.071321 | 2.3158 | 0.092002 | 0.15568 | -0.31334 | -0.23065 | -0.12656 | -0.11545 | 0.049369 | -0.090446 | 0.036116 | -0.033826 | -0.1222 | 124.0696 | 123.8276 | 123.9103 | 65.2827 | -124.2046 | 124.0255 | 124.1071 | 124.0187 | 65.4968 | -124.2675
343.9062 | 124.3469 | -67.3325 | 56.8909 | 0.033921 | -0.0041057 | 0.0028908 | 0.050285 | -0.0067764 | 0.050673 | 0.07984 | -0.0037909 | -0.0063367 | 0.056726 | 0.03379 | 0.056568 | -64.9251 | -2.0498 | -67.2221 | 56.7692 | 56.518 | 56.6053 | -67.3687 | -67.2739 | -1.8586 | -67.4 | 56.7205 | 56.7975 | 56.6725 | -67.4407 | -0.036211 | -0.12167 | 2.4074 | 0.11031 | 0.14652 | -0.37284 | -0.28558 | -0.10825 | -0.17038 | 0.058522 | -0.067558 | 0.040694 | -0.093334 | -0.21833 | 124.1017 | 123.8505 | 123.9377 | 65.2827 | -124.2595 | 124.053 | 124.13 | 124.005 | 65.4739 | -124.3316
344.9219 | 124.3881 | -67.337 | 56.8726 | 0.033921 | -0.0030377 | 0.0028908 | 0.052422 | -0.0078444 | 0.049605 | 0.049318 | -0.0048589 | -0.0074047 | 0.057794 | 0.032722 | 0.057636 | -64.9205 | -2.0544 | -67.2267 | 56.7738 | 56.5272 | 56.6007 | -67.3687 | -67.2694 | -1.8952 | -67.4 | 56.7251 | 56.793 | 56.6954 | -67.4361 | -0.031633 | -0.098784 | 2.4165 | 0.11031 | 0.14194 | -0.34538 | -0.27184 | -0.099095 | -0.14749 | 0.067678 | -0.06298 | 0.036115 | -0.079603 | -0.17713 | 124.1108 | 123.8642 | 123.9377 | 65.2827 | -124.2412 | 124.0621 | 124.13 | 124.0325 | 65.4418 | -124.3087
345.9062 | 124.3927 | -67.3462 | 56.8771 | 0.064445 | -0.0041057 | 0.0050278 | 0.051353 | -0.0046394 | 0.049605 | 0.07984 | -0.0048589 | -0.0052687 | 0.058862 | 0.034858 | 0.057636 | -64.9113 | -2.0819 | -67.213 | 56.7692 | 56.5226 | 56.6007 | -67.3549 | -67.2602 | -1.9181 | -67.4 | 56.7251 | 56.7975 | 56.6725 | -67.4316 | -0.008741 | -0.10794 | 2.4349 | 0.1332 | 0.14194 | -0.35453 | -0.27642 | -0.085361 | -0.15206 | 0.085991 | -0.053825 | 0.031536 | -0.079601 | -0.2046 | 124.1154 | 123.8688 | 123.9469 | 65.2643 | -124.2321 | 124.0713 | 124.1437 | 124.0187 | 65.4281 | -124.3087
346.9219 | 124.5071 | -67.305 | 56.8222 | 0.033921 | -0.0030377 | 0.0018228 | 0.050285 | -0.0057084 | 0.048536 | 0.064579 | -0.0037909 | -0.0063367 | 0.057794 | 0.03379 | 0.056568 | -64.9754 | -2.091 | -67.213 | 56.7692 | 56.5272 | 56.5961 | -67.3595 | -67.251 | -1.9547 | -67.3909 | 56.7205 | 56.8067 | 56.7 | -67.427 | -0.054518 | -0.053008 | 2.3296 | 0.092004 | 0.14652 | -0.29502 | -0.22607 | -0.12198 | -0.10171 | 0.05395 | -0.085865 | 0.036115 | -0.015513 | -0.1222 | 124.0742 | 123.8322 | 123.9011 | 65.214 | -124.1817 | 124.0255 | 124.1117 | 124.005 | 65.3502 | -124.2492
347.9219 | 124.4568 | -67.3141 | 56.8451 | 0.079707 | -0.0030377 | 0.00075378 | 0.052422 | -0.0057084 | 0.048536 | 0.064579 | -0.0027229 | -0.0052687 | 0.056726 | 0.03379 | 0.056568 | -64.948 | -2.1185 | -67.2221 | 56.7738 | 56.5318 | 56.6053 | -67.3504 | -67.2602 | -1.9914 | -67.3863 | 56.7296 | 56.8021 | 56.6771 | -67.427 | -0.036205 | -0.071318 | 2.3662 | 0.092002 | 0.12821 | -0.31333 | -0.2398 | -0.11283 | -0.11544 | 0.053948 | -0.072131 | 0.040694 | -0.042979 | -0.16798 | 124.0879 | 123.8459 | 123.9194 | 65.1957 | -124.1954 | 124.0438 | 124.1163 | 123.9913 | 65.3228 | -124.2721
348.9062 | 124.3286 | -67.3416 | 56.8954 | 0.064445 | -0.0041057 | 0.0028908 | 0.052422 | -0.0057084 | 0.048536 | 0.064579 | -0.0048589 | -0.0052687 | 0.058862 | 0.036995 | 0.056568 | -64.9113 | -2.1414 | -67.2221 | 56.7738 | 56.5318 | 56.6144 | -67.3458 | -67.2556 | -2.0143 | -67.3817 | 56.7251 | 56.8067 | 56.7 | -67.4224 | -0.00416 | -0.12167 | 2.4303 | 0.11947 | 0.12363 | -0.36369 | -0.281 | -0.080781 | -0.17037 | 0.085993 | -0.040087 | 0.040694 | -0.088755 | -0.19544 | 124.1154 | 123.8734 | 123.9561 | 65.2002 | -124.2412 | 124.0667 | 124.1483 | 124.0416 | 65.3273 | -124.3178
349.9062 | 124.3973 | -67.3187 | 56.9046 | 0.064445 | -0.0030377 | 0.0018228 | 0.051353 | -0.0078444 | 0.049605 | 0.064579 | -0.0027229 | -0.0052687 | 0.057794 | 0.034858 | 0.057636 | -64.8976 | -2.1551 | -67.2221 | 56.7784 | 56.5363 | 56.619 | -67.3412 | -67.2602 | -2.0601 | -67.3817 | 56.7251 | 56.8158 | 56.7 | -67.4178 | -0.02247 | -0.12625 | 2.4211 | 0.09658 | 0.11905 | -0.36826 | -0.28557 | -0.09909 | -0.17953 | 0.058526 | -0.062975 | 0.036115 | -0.088753 | -0.20459 | 124.0971 | 123.8551 | 123.9378 | 65.1636 | -124.2458 | 124.0438 | 124.1346 | 124.0187 | 65.2587 | -124.3224
350.9219 | 124.3607 | -67.3325 | 56.8588 | 0.064445 | -0.0030377 | 0.0028908 | 0.051353 | -0.0078444 | 0.049605 | 0.064579 | -0.0048589 | -0.0041997 | 0.056726 | 0.035927 | 0.057636 | -64.893 | -2.1826 | -67.2084 | 56.7829 | 56.5363 | 56.6236 | -67.3458 | -67.2465 | -2.0921 | -67.3863 | 56.7342 | 56.8158 | 56.6908 | -67.4178 | -0.013316 | -0.075894 | 2.4394 | 0.12405 | 0.13736 | -0.32249 | -0.23522 | -0.085358 | -0.1246 | 0.085994 | -0.053821 | 0.031537 | -0.042977 | -0.16798 | 124.1154 | 123.8688 | 123.9561 | 65.1499 | -124.2046 | 124.0667 | 124.1483 | 124.0233 | 65.2403 | -124.2766
351.9062 | 124.3652 | -67.3233 | 56.9092 | 0.049183 | -0.0030377 | 0.0018228 | 0.052422 | -0.0078444 | 0.050673 | 0.07984 | -0.0027229 | -0.0052687 | 0.057794 | 0.034858 | 0.0555 | -64.9068 | -2.2055 | -67.2084 | 56.7875 | 56.5409 | 56.619 | -67.3366 | -67.251 | -2.1287 | -67.3817 | 56.7296 | 56.8204 | 56.6817 | -67.4178 | -0.013314 | -0.12167 | 2.4165 | 0.11489 | 0.12821 | -0.36826 | -0.29015 | -0.094513 | -0.17953 | 0.07226 | -0.058398 | 0.036115 | -0.088752 | -0.22749 | 124.1108 | 123.8642 | 123.9423 | 65.1178 | -124.2458 | 124.053 | 124.1437 | 124.005 | 65.1946 | -124.327
352.9219 | 124.4293 | -67.337 | 56.868 | 0.049183 | -0.0051747 | 0.0050278 | 0.052422 | -0.0067764 | 0.049605 | 0.064579 | -0.0027229 | -0.0063367 | 0.056726 | 0.034858 | 0.0555 | -64.9159 | -2.2192 | -67.1855 | 56.7875 | 56.5409 | 56.6144 | -67.3412 | -67.2327 | -2.1471 | -67.3725 | 56.7251 | 56.8204 | 56.7137 | -67.4178 | -0.00416 | -0.080471 | 2.4211 | 0.15152 | 0.15568 | -0.32706 | -0.25353 | -0.08078 | -0.14291 | 0.10431 | -0.035507 | 0.045273 | -0.047553 | -0.15424 | 124.1245 | 123.878 | 123.9515 | 65.1178 | -124.2092 | 124.0621 | 124.1575 | 124.0508 | 65.19 | -124.2858
353.9062 | 124.3652 | -67.3004 | 56.9412 | 0.064445 | -0.0041057 | 0.0018228 | 0.052422 | -0.0057084 | 0.048536 | 0.07984 | -0.0037909 | -0.0063367 | 0.057794 | 0.034858 | 0.057636 | -64.8884 | -2.1689 | -67.1901 | 56.7967 | 56.5501 | 56.6236 | -67.3366 | -67.2281 | -2.1928 | -67.368 | 56.7434 | 56.8204 | 56.7046 | -67.4041 | -0.036202 | -0.14456 | 2.412 | 0.11032 | 0.14652 | -0.39115 | -0.31762 | -0.10366 | -0.19784 | 0.072266 | -0.06755 | 0.036114 | -0.1208 | -0.23664 | 124.0971 | 123.8505 | 123.924 | 65.1316 | -124.2778 | 124.0438 | 124.1208 | 124.005 | 65.1076 | -124.3453
354.9219 | 124.3973 | -67.3004 | 56.9046 | 0.064445 | -0.00090066 | 0.00075378 | 0.051353 | -0.0078444 | 0.050673 | 0.064579 | -0.0048589 | -0.0052687 | 0.056726 | 0.034858 | 0.057636 | -64.8701 | -2.1185 | -67.1855 | 56.8012 | 56.5547 | 56.6282 | -67.3366 | -67.2236 | -2.2157 | -67.3634 | 56.7525 | 56.825 | 56.7092 | -67.4041 | -0.036202 | -0.10336 | 2.4303 | 0.1149 | 0.1511 | -0.34995 | -0.27642 | -0.10366 | -0.15206 | 0.076845 | -0.062971 | 0.040693 | -0.079595 | -0.19544 | 124.1017 | 123.8551 | 123.9286 | 65.1819 | -124.2412 | 124.053 | 124.1254 | 124.0096 | 65.0847 | -124.3087
355.9062 | 124.3561 | -67.3096 | 56.9366 | 0.079707 | -0.0030377 | 0.0028908 | 0.049217 | -0.0057084 | 0.049605 | 0.07984 | -0.0059269 | -0.0063367 | 0.058862 | 0.03379 | 0.058705 | -64.8793 | -2.1048 | -67.1855 | 56.8012 | 56.5547 | 56.6419 | -67.3229 | -67.2236 | -2.2432 | -67.3451 | 56.748 | 56.8296 | 56.7092 | -67.3995 | -0.01331 | -0.1354 | 2.4303 | 0.12405 | 0.13736 | -0.38199 | -0.29472 | -0.08993 | -0.18868 | 0.086 | -0.035501 | 0.054429 | -0.10706 | -0.22748 | 124.1108 | 123.8642 | 123.9515 | 65.2048 | -124.2595 | 124.0575 | 124.1392 | 124.0187 | 65.0664 | -124.3361
356.9062 | 124.3973 | -67.2638 | 56.9229 | 0.064445 | -0.0030377 | 0.0028908 | 0.052422 | -0.0067764 | 0.048536 | 0.064579 | -0.0048589 | -0.0063367 | 0.057794 | 0.034858 | 0.0555 | -64.8564 | -2.1185 | -67.1947 | 56.8058 | 56.573 | 56.6419 | -67.3183 | -67.219 | -2.2753 | -67.3496 | 56.7525 | 56.8296 | 56.7275 | -67.3903 | -0.054507 | -0.11709 | 2.4074 | 0.069118 | 0.12363 | -0.34994 | -0.28099 | -0.12655 | -0.17037 | 0.044802 | -0.085856 | 0.040693 | -0.093328 | -0.19543 | 124.0696 | 123.8368 | 123.9057 | 65.1453 | -124.2412 | 124.0163 | 124.0934 | 123.9913 | 64.9885 | -124.3133
357.9219 | 124.3195 | -67.3462 | 56.9138 | 0.049183 | -0.0041057 | 0.0028908 | 0.052422 | -0.0078444 | 0.048536 | 0.064579 | -0.0037909 | -0.0052687 | 0.057794 | 0.034858 | 0.056568 | -64.8747 | -2.1368 | -67.1855 | 56.815 | 56.5684 | 56.6511 | -67.3183 | -67.2098 | -2.2707 | -67.3451 | 56.7617 | 56.8479 | 56.7275 | -67.3903 | 0.02789 | -0.098777 | 2.4715 | 0.16067 | 0.13278 | -0.34536 | -0.26268 | -0.044152 | -0.15206 | 0.13636 | 0.00112 | 0.045272 | -0.065857 | -0.18628 | 124.1612 | 123.9146 | 123.9973 | 65.2094 | -124.2321 | 124.1079 | 124.1941 | 124.0737 | 65.0755 | -124.3041
358.9219 | 124.292 | -67.305 | 56.9458 | 0.064445 | -0.0019697 | 0.0018228 | 0.050285 | -0.0057084 | 0.049605 | 0.064579 | -0.0037909 | -0.0063367 | 0.057794 | 0.035927 | 0.057636 | -64.8656 | -2.1689 | -67.1764 | 56.815 | 56.573 | 56.6511 | -67.3137 | -67.2053 | -2.289 | -67.3496 | 56.7571 | 56.8433 | 56.7183 | -67.3766 | -0.008729 | -0.13082 | 2.4394 | 0.12863 | 0.13736 | -0.37283 | -0.29472 | -0.071613 | -0.18868 | 0.099737 | -0.044657 | 0.026956 | -0.10248 | -0.22748 | 124.12 | 123.878 | 123.9561 | 65.1361 | -124.2595 | 124.0621 | 124.1483 | 124.0233 | 65.016 | -124.3224
359.9062 | 124.5117 | -67.2363 | 56.9092 | 0.064445 | -0.0041057 | 0.0018228 | 0.051353 | -0.0067764 | 0.049605 | 0.07984 | -0.0037909 | -0.0074047 | 0.055658 | 0.034858 | 0.056568 | -64.9251 | -2.2101 | -67.1809 | 56.8196 | 56.5776 | 56.6511 | -67.3137 | -67.2007 | -2.289 | -67.3359 | 56.7617 | 56.8479 | 56.7275 | -67.3858 | -0.077394 | -0.089621 | 2.3113 | 0.055387 | 0.13278 | -0.33163 | -0.2581 | -0.14944 | -0.14748 | 0.035651 | -0.099586 | 0.04985 | -0.06128 | -0.1817 | 124.0559 | 123.8139 | 123.8874 | 65.0263 | -124.2229 | 123.998 | 124.0842 | 123.9638 | 64.9473 | -124.2949
360.9219 | 124.3378 | -67.2546 | 56.9366 | 0.049183 | -0.0030377 | 0.0018228 | 0.052422 | -0.0089134 | 0.050673 | 0.049318 | -0.0027229 | -0.0063367 | 0.055658 | 0.035927 | 0.056568 | -64.8747 | -2.233 | -67.1672 | 56.8241 | 56.5776 | 56.6602 | -67.3091 | -67.2007 | -2.2982 | -67.3359 | 56.7663 | 56.8525 | 56.7412 | -67.372 | -0.054504 | -0.11251 | 2.3799 | 0.087432 | 0.14194 | -0.3591 | -0.27641 | -0.11739 | -0.17037 | 0.053962 | -0.081275 | 0.036114 | -0.084168 | -0.19543 | 124.0788 | 123.8322 | 123.9149 | 65.0217 | -124.2458 | 124.0209 | 124.1071 | 123.9959 | 64.9565 | -124.3087
361.9062 | 124.4522 | -67.2592 | 56.9275 | 0.064445 | -0.0041057 | 0.0018228 | 0.050285 | -0.0067764 | 0.050673 | 0.07984 | -0.0048589 | -0.0074047 | 0.056726 | 0.036995 | 0.057636 | -64.8884 | -2.2696 | -67.1535 | 56.815 | 56.5821 | 56.6602 | -67.3091 | -67.1915 | -2.2982 | -67.3313 | 56.7709 | 56.8525 | 56.7458 | -67.3812 | -0.049927 | -0.11251 | 2.3708 | 0.10574 | 0.15567 | -0.34536 | -0.26725 | -0.12197 | -0.15663 | 0.067697 | -0.072119 | 0.04985 | -0.075012 | -0.1817 | 124.0742 | 123.8413 | 123.9195 | 64.9896 | -124.2366 | 124.0301 | 124.1117 | 124.005 | 64.9611 | -124.3087
362.9219 | 124.3652 | -67.2867 | 56.9321 | 0.064445 | -0.0030377 | 0.0039598 | 0.051353 | -0.0057084 | 0.048536 | 0.034057 | -0.0037909 | -0.0074047 | 0.057794 | 0.035927 | 0.056568 | -64.861 | -2.3062 | -67.1626 | 56.8196 | 56.5821 | 56.6602 | -67.2817 | -67.1824 | -2.3256 | -67.3268 | 56.7846 | 56.8616 | 56.7366 | -67.3766 | 0.005012 | -0.11251 | 2.4257 | 0.12405 | 0.11904 | -0.34994 | -0.27183 | -0.089924 | -0.14748 | 0.10432 | -0.040074 | 0.04985 | -0.070433 | -0.19543 | 124.1062 | 123.8688 | 123.9469 | 64.9805 | -124.2137 | 124.0713 | 124.1483 | 124.0233 | 64.9611 | -124.3087
363.9062 | 124.4751 | -67.218 | 56.9183 | 0.049183 | -0.0030377 | 0.0028908 | 0.050285 | -0.0067764 | 0.049605 | 0.064579 | -0.0037909 | -0.0052687 | 0.056726 | 0.035927 | 0.057636 | -64.9022 | -2.3474 | -67.1581 | 56.8287 | 56.5867 | 56.6648 | -67.2954 | -67.1824 | -2.3623 | -67.313 | 56.7754 | 56.8616 | 56.7687 | -67.3766 | -0.077388 | -0.089619 | 2.3158 | 0.059968 | 0.13736 | -0.33163 | -0.25352 | -0.15859 | -0.1429 | 0.035656 | -0.095002 | 0.063586 | -0.0567 | -0.14965 | 124.0467 | 123.8047 | 123.8828 | 64.8706 | -124.2137 | 123.9935 | 124.0797 | 123.9867 | 64.8558 | -124.2949
364.9062 | 124.3561 | -67.2729 | 56.9687 | 0.064445 | -0.0030377 | 0.0028908 | 0.050285 | -0.0078444 | 0.048536 | 0.064579 | -0.0048589 | -0.0074047 | 0.055658 | 0.034858 | 0.056568 | -64.8518 | -2.384 | -67.1626 | 56.8379 | 56.5913 | 56.6694 | -67.2817 | -67.1824 | -2.3943 | -67.313 | 56.7846 | 56.8662 | 56.7412 | -67.3674 | -0.008721 | -0.13082 | 2.4211 | 0.11032 | 0.11904 | -0.3774 | -0.2993 | -0.0945 | -0.1841 | 0.090587 | -0.040071 | 0.054429 | -0.10247 | -0.22747 | 124.1108 | 123.8642 | 123.9423 | 64.8889 | -124.2504 | 124.0575 | 124.1392 | 124.0142 | 64.8786 | -124.3361
365.9062 | 124.4431 | -67.2409 | 56.9138 | 0.049183 | -0.0030377 | 0.0028908 | 0.052422 | -0.0067764 | 0.048536 | 0.07984 | -0.0027229 | -0.0052687 | 0.057794 | 0.036995 | 0.057636 | -64.9251 | -2.4024 | -67.1581 | 56.8333 | 56.5867 | 56.674 | -67.2862 | -67.1778 | -2.4126 | -67.3084 | 56.7892 | 56.8754 | 56.7595 | -67.3629 | -0.045342 | -0.080463 | 2.3158 | 0.082856 | 0.1282 | -0.32705 | -0.23979 | -0.12196 | -0.12459 | 0.063123 | -0.067535 | 0.054429 | -0.038386 | -0.15423 | 124.0742 | 123.8276 | 123.9149 | 64.8385 | -124.2 | 124.0301 | 124.1163 | 124.0004 | 64.8283 | -124.2766
366.9219 | 124.3973 | -67.2592 | 57.0007 | 0.049183 | -0.0030377 | 0.0039598 | 0.050285 | -0.0067764 | 0.048536 | 0.095101 | -0.0048589 | -0.0063367 | 0.057794 | 0.038063 | 0.0555 | -64.8518 | -2.4436 | -67.1443 | 56.8333 | 56.605 | 56.6786 | -67.2908 | -67.1686 | -2.4264 | -67.313 | 56.7892 | 56.8708 | 56.7595 | -67.3629 | -0.031611 | -0.16744 | 2.4074 | 0.1149 | 0.14651 | -0.39571 | -0.32218 | -0.10365 | -0.21156 | 0.09059 | -0.053804 | 0.04985 | -0.12994 | -0.2412 | 124.0925 | 123.8642 | 123.9378 | 64.8156 | -124.2916 | 124.0484 | 124.13 | 124.0187 | 64.8329 | -124.3636
367.9219 | 124.4476 | -67.2501 | 56.9778 | 0.064445 | -0.0019697 | 0.0039598 | 0.052422 | -0.0089134 | 0.049605 | 0.064579 | -0.0037909 | -0.0052687 | 0.057794 | 0.035927 | 0.0555 | -64.8472 | -2.4436 | -67.1443 | 56.8425 | 56.605 | 56.6786 | -67.2908 | -67.164 | -2.4355 | -67.3039 | 56.7937 | 56.88 | 56.7595 | -67.3491 | -0.040766 | -0.13539 | 2.4028 | 0.10575 | 0.14651 | -0.37282 | -0.29929 | -0.099072 | -0.18409 | 0.086014 | -0.053802 | 0.04527 | -0.097894 | -0.21831 | 124.0925 | 123.8551 | 123.9286 | 64.8065 | -124.2687 | 124.0438 | 124.13 | 124.0096 | 64.8145 | -124.327
368.9219 | 124.4843 | -67.186 | 56.9321 | 0.049183 | -0.0030377 | 0.0028908 | 0.051353 | -0.0067764 | 0.049605 | 0.064579 | -0.0037909 | -0.0041997 | 0.057794 | 0.038063 | 0.057636 | -64.8701 | -2.4665 | -67.1397 | 56.8425 | 56.605 | 56.6786 | -67.2817 | -67.1549 | -2.4538 | -67.2993 | 56.8029 | 56.8845 | 56.755 | -67.3491 | -0.095696 | -0.089617 | 2.3158 | 0.046237 | 0.14193 | -0.32704 | -0.25352 | -0.16316 | -0.12916 | 0.031084 | -0.11331 | 0.049849 | -0.04754 | -0.17712 | 124.0284 | 123.791 | 123.8645 | 64.7195 | -124.2137 | 123.9889 | 124.0705 | 123.9409 | 64.7321 | -124.2812
369.9062 | 124.4522 | -67.2043 | 56.9504 | 0.079707 | -0.0030377 | 0.0039598 | 0.050285 | -0.0089134 | 0.048536 | 0.049318 | -0.0037909 | -0.0052687 | 0.057794 | 0.036995 | 0.0555 | -64.8976 | -2.4802 | -67.1306 | 56.8425 | 56.6096 | 56.6877 | -67.2771 | -67.1595 | -2.4813 | -67.2947 | 56.7937 | 56.8845 | 56.7504 | -67.3491 | -0.072806 | -0.10793 | 2.3067 | 0.073705 | 0.14651 | -0.34078 | -0.26267 | -0.14485 | -0.15663 | 0.044816 | -0.09042 | 0.054428 | -0.06585 | -0.20001 | 124.0467 | 123.8139 | 123.892 | 64.7241 | -124.2275 | 123.998 | 124.0888 | 123.9547 | 64.723 | -124.2995
370.9219 | 124.4385 | -67.2043 | 56.9641 | 0.064445 | -0.0051747 | 0.0018228 | 0.049217 | -0.0067764 | 0.048536 | 0.064579 | -0.0048589 | -0.0063367 | 0.056726 | 0.038063 | 0.0555 | -64.8289 | -2.5077 | -67.1214 | 56.8516 | 56.6096 | 56.6923 | -67.2725 | -67.1503 | -2.495 | -67.2947 | 56.8075 | 56.8983 | 56.7778 | -67.3446 | -0.068227 | -0.1125 | 2.3754 | 0.082861 | 0.15109 | -0.35451 | -0.27182 | -0.14027 | -0.15663 | 0.053974 | -0.09042 | 0.04985 | -0.065847 | -0.18627 | 124.0559 | 123.8139 | 123.8966 | 64.6966 | -124.2366 | 124.0118 | 124.1025 | 123.9821 | 64.7092 | -124.3087
371.9219 | 124.4293 | -67.1722 | 56.987 | 0.049183 | -0.0041057 | 0.0028908 | 0.051353 | -0.0067764 | 0.048536 | 0.049318 | -0.0048589 | -0.0063367 | 0.055658 | 0.036995 | 0.056568 | -64.8656 | -2.5214 | -67.1214 | 56.8516 | 56.6142 | 56.6923 | -67.245 | -67.1457 | -2.5317 | -67.2855 | 56.8075 | 56.9028 | 56.7595 | -67.34 | -0.072797 | -0.13539 | 2.3067 | 0.050817 | 0.12361 | -0.37282 | -0.29471 | -0.16773 | -0.17952 | 0.026509 | -0.11331 | 0.054428 | -0.084157 | -0.22747 | 124.0238 | 123.7864 | 123.8645 | 64.6508 | -124.232 | 123.9797 | 124.0751 | 123.9318 | 64.6406 | -124.327
372.9219 | 124.3835 | -67.2501 | 56.9641 | 0.049183 | -0.0041057 | 0.0028908 | 0.052422 | -0.0078444 | 0.048536 | 0.064579 | -0.0048589 | -0.0074047 | 0.056726 | 0.038063 | 0.0555 | -64.7969 | -2.5443 | -67.1214 | 56.8608 | 56.6188 | 56.7014 | -67.2634 | -67.1457 | -2.5546 | -67.2855 | 56.8075 | 56.8983 | 56.7733 | -67.34 | -0.013293 | -0.10335 | 2.4532 | 0.12864 | 0.14193 | -0.34535 | -0.26267 | -0.089915 | -0.15663 | 0.10433 | -0.035487 | 0.054428 | -0.065847 | -0.19085 | 124.1108 | 123.8688 | 123.9515 | 64.7058 | -124.2275 | 124.0575 | 124.1483 | 124.0233 | 64.6955 | -124.3041
373.9062 | 124.4385 | -67.2134 | 56.9687 | 0.064445 | -0.0041057 | 0.0028908 | 0.049217 | -0.0067764 | 0.048536 | 0.064579 | -0.0059269 | -0.0063367 | 0.056726 | 0.036995 | 0.057636 | -64.893 | -2.5855 | -67.1214 | 56.8608 | 56.6142 | 56.7014 | -67.2588 | -67.1412 | -2.582 | -67.2855 | 56.8121 | 56.8937 | 56.787 | -67.3262 | -0.045335 | -0.10792 | 2.3204 | 0.092016 | 0.13735 | -0.35451 | -0.26725 | -0.1128 | -0.15663 | 0.072286 | -0.072108 | 0.040691 | -0.075003 | -0.18169 | 124.0742 | 123.8276 | 123.9149 | 64.6279 | -124.2275 | 124.0255 | 124.1071 | 124.0004 | 64.6314 | -124.2949
374.9219 | 124.4202 | -67.1997 | 56.9687 | 0.064445 | -0.0041057 | 0.0028908 | 0.052422 | -0.0078444 | 0.049605 | 0.07984 | -0.0037909 | -0.0074047 | 0.057794 | 0.038063 | 0.054432 | -64.8381 | -2.613 | -67.1123 | 56.8699 | 56.6188 | 56.7106 | -67.2542 | -67.1412 | -2.6232 | -67.2764 | 56.8212 | 56.9074 | 56.8007 | -67.3308 | -0.054489 | -0.098768 | 2.3616 | 0.08744 | 0.14193 | -0.34993 | -0.25809 | -0.13111 | -0.14747 | 0.058553 | -0.076683 | 0.054428 | -0.061268 | -0.16795 | 124.0696 | 123.8185 | 123.9103 | 64.5867 | -124.2229 | 124.0209 | 124.1071 | 124.0004 | 64.5765 | -124.2995
375.9062 | 124.4156 | -67.2226 | 56.9733 | 0.064445 | -0.0041057 | 0.0018228 | 0.050285 | -0.0089134 | 0.047468 | 0.049318 | -0.0048589 | -0.0074047 | 0.056726 | 0.035927 | 0.057636 | -64.8839 | -2.6496 | -67.1123 | 56.8608 | 56.6279 | 56.7014 | -67.2634 | -67.1274 | -2.6553 | -67.2764 | 56.8166 | 56.9074 | 56.7778 | -67.3308 | -0.040759 | -0.1125 | 2.3387 | 0.11033 | 0.15109 | -0.34535 | -0.27182 | -0.10822 | -0.15662 | 0.095177 | -0.053795 | 0.054428 | -0.065846 | -0.19542 | 124.0834 | 123.8505 | 123.924 | 64.573 | -124.2366 | 124.0392 | 124.13 | 124.0004 | 64.5673 | -124.3041
376.9062 | 124.4431 | -67.1906 | 56.9733 | 0.064445 | -0.0019697 | 0.0039598 | 0.050285 | -0.0089134 | 0.048536 | 0.049318 | -0.0037909 | -0.0074047 | 0.056726 | 0.039132 | 0.056568 | -64.8243 | -2.6817 | -67.1077 | 56.8745 | 56.6279 | 56.7152 | -67.2588 | -67.1366 | -2.6828 | -67.2718 | 56.8166 | 56.912 | 56.8007 | -67.3262 | -0.068223 | -0.098768 | 2.3662 | 0.082863 | 0.15109 | -0.34535 | -0.25809 | -0.13569 | -0.15662 | 0.053977 | -0.08126 | 0.054427 | -0.061267 | -0.17253 | 124.0651 | 123.8185 | 123.9057 | 64.5089 | -124.232 | 124.0072 | 124.1026 | 123.9913 | 64.5078 | -124.2995
377.9062 | 124.5163 | -67.2043 | 56.9687 | 0.049183 | -0.0041057 | 0.0028908 | 0.051353 | -0.0089134 | 0.047468 | 0.064579 | -0.0037909 | -0.0063367 | 0.055658 | 0.038063 | 0.0555 | -64.8243 | -2.7137 | -67.1123 | 56.8699 | 56.6371 | 56.7106 | -67.2496 | -67.1274 | -2.7102 | -67.2627 | 56.8212 | 56.9028 | 56.8007 | -67.3217 | -0.045332 | -0.098768 | 2.3799 | 0.092018 | 0.13735 | -0.33161 | -0.25809 | -0.11738 | -0.14747 | 0.076867 | -0.058369 | 0.059007 | -0.065846 | -0.16795 | 124.0742 | 123.8414 | 123.9149 | 64.4906 | -124.2183 | 124.0255 | 124.1071 | 124.005 | 64.494 | -124.2904
378.9219 | 124.4522 | -67.1722 | 56.9824 | 0.064445 | -0.0041057 | 0.0028908 | 0.051353 | -0.0078444 | 0.0464 | 0.064579 | -0.0048589 | -0.0052687 | 0.057794 | 0.036995 | 0.0555 | -64.8243 | -2.7503 | -67.0985 | 56.8791 | 56.6325 | 56.706 | -67.2588 | -67.1091 | -2.7514 | -67.2627 | 56.8212 | 56.9074 | 56.8007 | -67.3125 | -0.086534 | -0.10334 | 2.3479 | 0.073709 | 0.16024 | -0.34992 | -0.2764 | -0.14026 | -0.1612 | 0.063138 | -0.090413 | 0.049849 | -0.075001 | -0.18169 | 124.0513 | 123.8047 | 123.8783 | 64.4219 | -124.2412 | 123.9935 | 124.0797 | 123.973 | 64.4208 | -124.2949
379.9219 | 124.4385 | -67.1997 | 56.9733 | 0.064445 | -0.0041057 | 0.0028908 | 0.051353 | -0.0099814 | 0.048536 | 0.095101 | -0.0027229 | -0.0063367 | 0.056726 | 0.038063 | 0.056568 | -64.8701 | -2.787 | -67.0985 | 56.8745 | 56.6417 | 56.7198 | -67.2405 | -67.1137 | -2.7789 | -67.2581 | 56.8258 | 56.9166 | 56.787 | -67.3262 | -0.040752 | -0.098768 | 2.3296 | 0.10117 | 0.14193 | -0.33161 | -0.25351 | -0.12653 | -0.14747 | 0.086026 | -0.058369 | 0.068163 | -0.056688 | -0.18627 | 124.0742 | 123.8414 | 123.9195 | 64.4127 | -124.2137 | 124.0255 | 124.1163 | 123.9867 | 64.4208 | -124.2995
380.9219 | 124.4339 | -67.1997 | 56.987 | 0.079707 | -0.0019697 | 0.0039598 | 0.050285 | -0.0078444 | 0.049605 | 0.064579 | -0.0048589 | -0.0063367 | 0.056726 | 0.038063 | 0.056568 | -64.8656 | -2.8282 | -67.094 | 56.8837 | 56.6325 | 56.7198 | -67.2588 | -67.1137 | -2.811 | -67.2627 | 56.8212 | 56.9166 | 56.7962 | -67.3125 | -0.059068 | -0.10334 | 2.3342 | 0.10575 | 0.16482 | -0.3545 | -0.26724 | -0.1128 | -0.16578 | 0.086026 | -0.062947 | 0.049849 | -0.070421 | -0.19084 | 124.0834 | 123.8322 | 123.9195 | 64.3715 | -124.2458 | 124.0209 | 124.1163 | 123.9959 | 64.3887 | -124.2995
381.9062 | 124.411 | -67.1951 | 56.9458 | 0.049183 | -0.0041057 | 0.0018228 | 0.050285 | -0.0057084 | 0.049605 | 0.064579 | -0.0037909 | -0.0074047 | 0.057794 | 0.039132 | 0.056568 | -64.8656 | -2.8602 | -67.1123 | 56.8699 | 56.6279 | 56.706 | -67.2542 | -67.1137 | -2.843 | -67.2581 | 56.8212 | 56.9028 | 56.7916 | -67.3262 | -0.059067 | -0.07588 | 2.3296 | 0.082862 | 0.14193 | -0.31788 | -0.23978 | -0.13111 | -0.12458 | 0.081448 | -0.062947 | 0.068163 | -0.042958 | -0.15422 | 124.065 | 123.823 | 123.9012 | 64.3349 | -124.2 | 124.0163 | 124.098 | 123.9867 | 64.3521 | -124.272
382.9219 | 124.4064 | -67.2409 | 56.9916 | 0.079707 | -0.0051747 | 0.0018228 | 0.051353 | -0.0099814 | 0.0464 | 0.049318 | -0.0037909 | -0.0063367 | 0.057794 | 0.038063 | 0.057636 | -64.7831 | -2.9014 | -67.1077 | 56.8516 | 56.6188 | 56.7014 | -67.2725 | -67.1366 | -2.8751 | -67.2718 | 56.8075 | 56.8891 | 56.7733 | -67.3308 | -0.031606 | -0.13997 | 2.4578 | 0.13322 | 0.16482 | -0.37282 | -0.29013 | -0.089912 | -0.18409 | 0.10433 | -0.030906 | 0.059006 | -0.10247 | -0.21831 | 124.0925 | 123.8597 | 123.9423 | 64.3395 | -124.2641 | 124.0484 | 124.13 | 124.0142 | 64.3658 | -124.3224
383.9062 | 124.4476 | -67.2043 | 56.9183 | 0.049183 | -0.0041057 | 0.0028908 | 0.050285 | -0.0078444 | 0.048536 | 0.07984 | -0.0048589 | -0.0063367 | 0.056726 | 0.039132 | 0.056568 | -64.8793 | -2.9518 | -67.1352 | 56.8379 | 56.6004 | 56.6786 | -67.2862 | -67.1457 | -2.9163 | -67.2901 | 56.7983 | 56.8845 | 56.7595 | -67.3537 | -0.081963 | -0.080463 | 2.325 | 0.069126 | 0.15109 | -0.31789 | -0.23978 | -0.14943 | -0.12001 | 0.058553 | -0.085842 | 0.063585 | -0.033807 | -0.15881 | 124.0422 | 123.8047 | 123.8828 | 64.2525 | -124.2046 | 124.0026 | 124.0888 | 123.9638 | 64.288 | -124.272
384.9062 | 124.5071 | -67.2272 | 56.9366 | 0.064445 | -0.0041057 | 0.0028908 | 0.049217 | -0.0078444 | 0.049605 | 0.049318 | -0.0048589 | -0.0084727 | 0.055658 | 0.038063 | 0.0555 | -64.9022 | -2.993 | -67.1489 | 56.815 | 56.5776 | 56.6648 | -67.3046 | -67.1595 | -2.9438 | -67.3176 | 56.7754 | 56.8616 | 56.7458 | -67.3766 | -0.077391 | -0.12167 | 2.325 | 0.07828 | 0.15567 | -0.3591 | -0.27183 | -0.14943 | -0.16121 | 0.067704 | -0.090426 | 0.059007 | -0.075011 | -0.19085 | 124.0422 | 123.8047 | 123.892 | 64.2342 | -124.2412 | 124.0026 | 124.0888 | 123.973 | 64.2834 | -124.3133
385.9062 | 124.4614 | -67.2867 | 56.868 | 0.064445 | -0.0051747 | 0.0039598 | 0.049217 | -0.0067764 | 0.049605 | 0.049318 | -0.0059269 | -0.0052687 | 0.055658 | 0.039132 | 0.056568 | -64.8976 | -3.0296 | -67.1718 | 56.8058 | 56.5638 | 56.6465 | -67.3183 | -67.1778 | -2.9895 | -67.3268 | 56.7525 | 56.8342 | 56.7366 | -67.3903 | -0.031619 | -0.062157 | 2.3891 | 0.1149 | 0.14652 | -0.30417 | -0.22148 | -0.10366 | -0.11544 | 0.1089 | -0.040074 | 0.063587 | -0.033817 | -0.13135 | 124.0925 | 123.8505 | 123.9332 | 64.2571 | -124.1863 | 124.0392 | 124.1208 | 124.0233 | 64.2971 | -124.2583
386.9219 | 124.4202 | -67.2775 | 56.8726 | 0.049183 | -0.0051747 | 0.0028908 | 0.049217 | -0.0089134 | 0.049605 | 0.049318 | -0.0027229 | -0.0052687 | 0.055658 | 0.038063 | 0.0555 | -64.948 | -3.0617 | -67.1809 | 56.7921 | 56.5501 | 56.619 | -67.3366 | -67.1915 | -3.0307 | -67.3405 | 56.7388 | 56.8204 | 56.6954 | -67.4041 | -0.05909 | -0.080471 | 2.3296 | 0.096586 | 0.15568 | -0.32248 | -0.25353 | -0.12655 | -0.13375 | 0.086008 | -0.062965 | 0.063587 | -0.052131 | -0.17713 | 124.0696 | 123.8276 | 123.8966 | 64.2158 | -124.2092 | 124.0163 | 124.098 | 123.973 | 64.2468 | -124.2766
387.9219 | 124.3835 | -67.3187 | 56.8863 | 0.049183 | -0.0051747 | 0.0018228 | 0.050285 | -0.0089134 | 0.048536 | 0.064579 | -0.0037909 | -0.0063367 | 0.057794 | 0.039132 | 0.0555 | -64.8564 | -3.1166 | -67.2038 | 56.7646 | 56.5318 | 56.6144 | -67.3549 | -67.2098 | -3.0811 | -67.3588 | 56.7159 | 56.8021 | 56.6817 | -67.427 | -0.036206 | -0.12167 | 2.4623 | 0.11489 | 0.1511 | -0.35453 | -0.27184 | -0.10825 | -0.17038 | 0.10889 | -0.040081 | 0.068166 | -0.084178 | -0.2046 | 124.0833 | 123.8505 | 123.9332 | 64.2021 | -124.2412 | 124.0346 | 124.1208 | 124.0004 | 64.2376 | -124.3133
388.9062 | 124.4247 | -67.3141 | 56.8359 | 0.049183 | -0.0041057 | 0.0028908 | 0.050285 | -0.0078444 | 0.049605 | 0.064579 | -0.0059269 | -0.0063367 | 0.055658 | 0.039132 | 0.054432 | -64.9754 | -3.1533 | -67.2176 | 56.7509 | 56.5089 | 56.6007 | -67.3732 | -67.219 | -3.1132 | -67.3771 | 56.7113 | 56.7884 | 56.6771 | -67.4407 | -0.0591 | -0.085054 | 2.3387 | 0.09658 | 0.15568 | -0.32707 | -0.23522 | -0.12656 | -0.1246 | 0.095156 | -0.062974 | 0.063588 | -0.047559 | -0.15882 | 124.065 | 123.823 | 123.9149 | 64.1609 | -124.2092 | 124.0255 | 124.1025 | 123.9913 | 64.201 | -124.2766
389.9062 | 124.4568 | -67.3645 | 56.813 | 0.064445 | -0.0030377 | 0.0018228 | 0.051353 | -0.0057084 | 0.050673 | 0.034057 | -0.0048589 | -0.0063367 | 0.056726 | 0.039132 | 0.057636 | -64.9617 | -3.2036 | -67.2313 | 56.7326 | 56.4951 | 56.5778 | -67.3778 | -67.2327 | -3.1452 | -67.4 | 56.6839 | 56.7701 | 56.6405 | -67.4636 | -0.013325 | -0.08048 | 2.4028 | 0.1332 | 0.14652 | -0.31792 | -0.23523 | -0.099102 | -0.12918 | 0.13177 | -0.035514 | 0.063588 | -0.042986 | -0.17256 | 124.0971 | 123.8596 | 123.9423 | 64.1609 | -124.1909 | 124.0484 | 124.1346 | 124.005 | 64.2193 | -124.2767
390.9219 | 124.4522 | -67.3416 | 56.781 | 0.049183 | -0.0051747 | 0.0028908 | 0.052422 | -0.0089134 | 0.049605 | 0.049318 | -0.0048589 | -0.0052687 | 0.057794 | 0.0402 | 0.0555 | -65.0029 | -3.2631 | -67.2588 | 56.7097 | 56.4722 | 56.5549 | -67.419 | -67.2602 | -3.1956 | -67.4229 | 56.6564 | 56.7426 | 56.6267 | -67.4819 | -0.077423 | -0.071329 | 2.3387 | 0.082842 | 0.16027 | -0.30877 | -0.22608 | -0.1403 | -0.12461 | 0.081414 | -0.081295 | 0.05901 | -0.038414 | -0.15426 | 124.0513 | 123.8138 | 123.8965 | 64.0785 | -124.2 | 123.998 | 124.0842 | 123.9684 | 64.146 | -124.2629
391.9062 | 124.4522 | -67.3691 | 56.7581 | 0.049183 | -0.0041057 | 0.0028908 | 0.051353 | -0.0067764 | 0.0464 | 0.049318 | -0.0037909 | -0.0041997 | 0.056726 | 0.038063 | 0.056568 | -65.035 | -3.3135 | -67.2771 | 56.6731 | 56.4356 | 56.5229 | -67.4419 | -67.2831 | -3.2322 | -67.4458 | 56.6335 | 56.7151 | 56.5718 | -67.514 | -0.072852 | -0.085068 | 2.3341 | 0.091995 | 0.16485 | -0.32251 | -0.23524 | -0.14489 | -0.12462 | 0.085986 | -0.076723 | 0.068168 | -0.042998 | -0.18631 | 124.0421 | 123.8047 | 123.892 | 64.0556 | -124.2001 | 124.0026 | 124.0842 | 123.9409 | 64.1369 | -124.2721
392.9219 | 124.3149 | -67.4377 | 56.7993 | 0.064445 | -0.0062427 | 0.0028908 | 0.050285 | -0.0089134 | 0.047468 | 0.049318 | -0.0037909 | -0.0063367 | 0.055658 | 0.039132 | 0.054432 | -64.9709 | -3.3684 | -67.3 | 56.6639 | 56.4219 | 56.5046 | -67.4648 | -67.306 | -3.278 | -67.4595 | 56.6152 | 56.6968 | 56.5855 | -67.5369 | -0.027083 | -0.13542 | 2.4669 | 0.13777 | 0.16485 | -0.37745 | -0.29475 | -0.099121 | -0.18413 | 0.13176 | -0.021795 | 0.077326 | -0.10251 | -0.21377 | 124.1016 | 123.8596 | 123.9423 | 64.0693 | -124.2641 | 124.0529 | 124.1345 | 124.0233 | 64.1597 | -124.3362
393.9062 | 124.4705 | -67.4149 | 56.7032 | 0.033921 | -0.0041057 | 0.0028908 | 0.051353 | -0.0089134 | 0.049605 | 0.049318 | -0.0037909 | -0.0052687 | 0.055658 | 0.039132 | 0.056568 | -65.0121 | -3.4325 | -67.2954 | 56.6547 | 56.4036 | 56.4954 | -67.4648 | -67.3151 | -3.3009 | -67.4733 | 56.606 | 56.6876 | 56.581 | -67.5369 | -0.049971 | -0.048449 | 2.4028 | 0.11946 | 0.16943 | -0.29964 | -0.20778 | -0.12201 | -0.097155 | 0.099711 | -0.058419 | 0.06359 | -0.015538 | -0.12222 | 124.0696 | 123.8184 | 123.9103 | 63.9823 | -124.168 | 124.0209 | 124.1025 | 123.9958 | 64.114 | -124.2401
394.9219 | 124.3835 | -67.4377 | 56.7398 | 0.049183 | -0.0051747 | 0.0028908 | 0.051353 | -0.0089134 | 0.048536 | 0.049318 | -0.0048589 | -0.0052687 | 0.055658 | 0.0402 | 0.0555 | -65.0853 | -3.5058 | -67.3137 | 56.6364 | 56.3944 | 56.4817 | -67.4877 | -67.3243 | -3.3604 | -67.4916 | 56.5969 | 56.6785 | 56.5718 | -67.5506 | -0.049977 | -0.10338 | 2.3524 | 0.12403 | 0.17401 | -0.34541 | -0.25814 | -0.11286 | -0.14293 | 0.11344 | -0.053846 | 0.059011 | -0.061316 | -0.168 | 124.0742 | 123.8321 | 123.9194 | 63.9319 | -124.2275 | 124.0346 | 124.1162 | 124.0095 | 64.0773 | -124.2904
395.9219 | 124.4476 | -67.4423 | 56.7352 | 0.064445 | -0.0062427 | 0.0028908 | 0.051353 | -0.0067764 | 0.048536 | 0.049318 | -0.0027229 | -0.0063367 | 0.055658 | 0.041269 | 0.0555 | -65.0762 | -3.5653 | -67.3274 | 56.6273 | 56.3944 | 56.4771 | -67.4786 | -67.3335 | -3.4016 | -67.487 | 56.5877 | 56.6693 | 56.5672 | -67.5598 | -0.036241 | -0.10796 | 2.3662 | 0.11488 | 0.15112 | -0.34083 | -0.25814 | -0.11744 | -0.14751 | 0.10886 | -0.044689 | 0.072748 | -0.065895 | -0.168 | 124.0696 | 123.8367 | 123.9194 | 63.877 | -124.2138 | 124.03 | 124.1117 | 124.0096 | 64.0407 | -124.295
396.9062 | 124.4385 | -67.4515 | 56.6895 | 0.064445 | -0.0062427 | 0.0039598 | 0.051353 | -0.0067764 | 0.048536 | 0.049318 | -0.0048589 | -0.0063367 | 0.055658 | 0.039132 | 0.056568 | -65.0533 | -3.6294 | -67.3274 | 56.6227 | 56.3852 | 56.4679 | -67.4923 | -67.3289 | -3.4566 | -67.5007 | 56.574 | 56.6648 | 56.5581 | -67.5689 | -0.040823 | -0.066765 | 2.3982 | 0.12403 | 0.16485 | -0.30422 | -0.22152 | -0.11744 | -0.11547 | 0.1226 | -0.04927 | 0.06817 | -0.024698 | -0.13138 | 124.0742 | 123.8367 | 123.9194 | 63.8221 | -124.1818 | 124.0255 | 124.1162 | 124.0095 | 63.9949 | -124.2584
397.9219 | 124.4202 | -67.4515 | 56.7535 | 0.064445 | -0.0051747 | 0.0018228 | 0.050285 | -0.0089134 | 0.0464 | 0.07984 | -0.0048589 | -0.0084727 | 0.057794 | 0.0402 | 0.0555 | -65.0166 | -3.6981 | -67.3274 | 56.6181 | 56.3807 | 56.4679 | -67.4923 | -67.3472 | -3.4978 | -67.5053 | 56.5786 | 56.6602 | 56.5443 | -67.5735 | -0.040823 | -0.13543 | 2.4348 | 0.12403 | 0.16485 | -0.37288 | -0.28561 | -0.12202 | -0.17498 | 0.10428 | -0.053849 | 0.06817 | -0.093363 | -0.20921 | 124.0696 | 123.8321 | 123.9194 | 63.7534 | -124.2458 | 124.03 | 124.1117 | 123.9958 | 63.9537 | -124.327
398.9219 | 124.4156 | -67.4332 | 56.7352 | 0.064445 | -0.0051747 | 0.0018228 | 0.051353 | -0.0078444 | 0.048536 | 0.064579 | -0.0059269 | -0.0074047 | 0.058862 | 0.042337 | 0.054432 | -65.035 | -3.7668 | -67.3091 | 56.6502 | 56.4081 | 56.4954 | -67.4511 | -67.3197 | -3.5527 | -67.4779 | 56.5969 | 56.6785 | 56.6084 | -67.5323 | -0.017923 | -0.085071 | 2.3982 | 0.12403 | 0.14196 | -0.3271 | -0.23982 | -0.099119 | -0.13835 | 0.11344 | -0.044687 | 0.054432 | -0.056738 | -0.12679 | 124.0833 | 123.8413 | 123.9286 | 63.6664 | -124.1863 | 124.03 | 124.1117 | 124.0416 | 63.8804 | -124.2675
399.9062 | 124.4705 | -21.8536 | 102.388 | 0.064445 | -0.0030377 | 0.0039598 | 0.051353 | -0.0089134 | 0.059219 | 0.07984 | -0.0037909 | -0.0063367 | 0.057794 | 0.0402 | 0.054432 | -0.10426 | 3.4766 | -22.0574 | 102.2601 | 101.9181 | 101.9518 | -21.8267 | -22.0317 | 2.7705 | -22.1669 | 101.9377 | 102.2493 | 102.1701 | -21.9868 | 0.026952 | -0.12794 | 21.7494 | -0.20377 | -0.23072 | -0.46994 | -0.43623 | -0.13315 | -0.45029 | -0.17807 | -0.3133 | -0.18015 | -0.13868 | -0.21789 | 124.1137 | 123.7717 | 123.8054 | 25.3302 | -124.2147 | 123.7914 | 124.103 | 124.0237 | 24.6241 | -124.3748
400.9219 | 124.4247 | -21.8674 | 102.3422 | 0.049183 | -0.0041057 | 0.0039598 | 0.051353 | -0.0078444 | 0.060288 | 0.064579 | -0.0027229 | -0.0084727 | 0.055658 | 0.041269 | 0.054432 | -0.03558 | 3.5178 | -22.0574 | 102.2738 | 101.9318 | 101.9747 | -21.8313 | -22.0363 | 2.8163 | -22.1578 | 101.9606 | 102.2768 | 102.1884 | -21.9776 | 0.036106 | -0.068431 | 21.8318 | -0.19004 | -0.22614 | -0.41043 | -0.36756 | -0.11026 | -0.38162 | -0.16891 | -0.29041 | -0.18015 | -0.06543 | -0.1538 | 124.1412 | 123.7992 | 123.842 | 25.3851 | -124.1735 | 123.828 | 124.1442 | 124.0558 | 24.6836 | -124.3199
401.9062 | 124.4019 | -21.9772 | 102.2461 | 0.033921 | -0.0030377 | 0.0028908 | 0.052422 | -0.0089134 | 0.061356 | 0.07984 | -0.0037909 | -0.0063367 | 0.055658 | 0.039132 | 0.054432 | -0.03558 | 3.5681 | -22.0803 | 102.2463 | 101.9043 | 101.9472 | -21.8633 | -22.0638 | 2.8208 | -22.1898 | 101.9331 | 102.2402 | 102.1564 | -22.0097 | 0.11392 | 0.000229 | 21.9417 | -0.10307 | -0.21698 | -0.34177 | -0.2989 | -0.032452 | -0.31296 | -0.086521 | -0.2126 | -0.18015 | -0.005929 | -0.089721 | 124.2236 | 123.8816 | 123.9244 | 25.5454 | -124.1094 | 123.9104 | 124.2174 | 124.1336 | 24.7981 | -124.2558
402.9219 | 124.4751 | -21.9772 | 102.2324 | 0.079707 | -0.0051747 | 0.0028908 | 0.050285 | -0.0078444 | 0.060288 | 0.049318 | -0.0059269 | -0.0084727 | 0.057794 | 0.0402 | 0.054432 | -0.031001 | 3.6093 | -22.0895 | 102.1914 | 101.854 | 101.9014 | -21.9183 | -22.1187 | 2.8712 | -22.2448 | 101.8782 | 102.1944 | 102.1106 | -22.0555 | 0.05897 | -0.040979 | 21.9462 | -0.11222 | -0.17119 | -0.37841 | -0.33095 | -0.07824 | -0.35417 | -0.14147 | -0.26755 | -0.18931 | -0.037982 | -0.12177 | 124.1686 | 123.8312 | 123.8786 | 25.5866 | -124.1506 | 123.8554 | 124.1716 | 124.0878 | 24.8484 | -124.2878
403.9062 | 124.3927 | -22.0596 | 102.182 | 0.033921 | -0.0041057 | 0.0028908 | 0.050285 | -0.0099814 | 0.059219 | 0.064579 | -0.0048589 | -0.0063367 | 0.058862 | 0.041269 | 0.054432 | -0.03558 | 3.6643 | -22.1444 | 102.1456 | 101.8036 | 101.851 | -21.9732 | -22.1782 | 2.9216 | -22.2906 | 101.8278 | 102.144 | 102.0556 | -22.1058 | 0.08642 | -0.036408 | 22.0241 | -0.084765 | -0.17119 | -0.37842 | -0.33096 | -0.04621 | -0.35418 | -0.11859 | -0.23093 | -0.18472 | -0.037993 | -0.12636 | 124.2052 | 123.8632 | 123.9107 | 25.7239 | -124.1552 | 123.8875 | 124.2036 | 124.1153 | 24.9812 | -124.2878
404.9219 | 124.4522 | -22.0688 | 102.1545 | 0.064445 | -0.0041057 | 0.0018228 | 0.052422 | -0.0089134 | 0.060288 | 0.064579 | -0.0037909 | -0.0052687 | 0.057794 | 0.039132 | 0.0555 | -0.021844 | 3.7055 | -22.1902 | 102.0998 | 101.7532 | 101.8098 | -22.0098 | -22.2103 | 2.9674 | -22.3455 | 101.782 | 102.0982 | 102.019 | -22.1562 | 0.058944 | -0.054726 | 22.0469 | -0.12139 | -0.18034 | -0.40132 | -0.34471 | -0.087421 | -0.3725 | -0.14149 | -0.27672 | -0.1893 | -0.056313 | -0.13553 | 124.1686 | 123.822 | 123.8786 | 25.7743 | -124.1644 | 123.8508 | 124.167 | 124.0878 | 25.0361 | -124.3107
405.9062 | 124.4843 | -22.1283 | 102.095 | 0.033921 | -0.0041057 | 0.0028908 | 0.050285 | -0.0089134 | 0.060288 | 0.064579 | -0.0027229 | -0.0074047 | 0.056726 | 0.039132 | 0.054432 | -0.026423 | 3.7467 | -22.2176 | 102.0586 | 101.7257 | 101.7686 | -22.0373 | -22.2469 | 3.0177 | -22.3638 | 101.7592 | 102.0662 | 101.9824 | -22.1883 | 0.09098 | -0.036423 | 22.1019 | -0.089352 | -0.18033 | -0.36929 | -0.32641 | -0.059963 | -0.33588 | -0.11861 | -0.23553 | -0.17557 | -0.028854 | -0.11265 | 124.1869 | 123.854 | 123.8969 | 25.875 | -124.1323 | 123.8874 | 124.1945 | 124.1107 | 25.146 | -124.2833
406.9219 | 124.411 | -22.1329 | 102.1271 | 0.049183 | -0.0030377 | 0.0039598 | 0.049217 | -0.0089134 | 0.060288 | 0.064579 | -0.0048589 | -0.0052687 | 0.056726 | 0.0402 | 0.0555 | -0.021844 | 3.7559 | -22.236 | 102.054 | 101.7074 | 101.764 | -22.0556 | -22.224 | 3.0773 | -22.3867 | 101.7408 | 102.0524 | 101.9641 | -22.202 | 0.077242 | -0.073044 | 22.111 | -0.10309 | -0.18033 | -0.41964 | -0.36303 | -0.069122 | -0.38624 | -0.091136 | -0.25384 | -0.18472 | -0.074633 | -0.163 | 124.1869 | 123.8403 | 123.8969 | 25.8887 | -124.1827 | 123.8737 | 124.1853 | 124.0969 | 25.2101 | -124.3291
407.9219 | 124.3881 | -22.1191 | 102.1042 | 0.064445 | -0.0041057 | 0.0028908 | 0.050285 | -0.0078444 | 0.060288 | 0.095101 | -0.0048589 | -0.0063367 | 0.055658 | 0.0402 | 0.053363 | -0.026423 | 3.8062 | -22.236 | 102.0449 | 101.7166 | 101.7549 | -22.0602 | -22.224 | 3.1139 | -22.3867 | 101.7408 | 102.0479 | 101.9778 | -22.2112 | 0.05893 | -0.059313 | 22.0927 | -0.11682 | -0.17575 | -0.3876 | -0.34929 | -0.092013 | -0.36335 | -0.10487 | -0.26758 | -0.17556 | -0.056323 | -0.12638 | 124.164 | 123.8357 | 123.874 | 25.9254 | -124.1644 | 123.86 | 124.167 | 124.0969 | 25.233 | -124.3153
408.9062 | 123.6374 | -22.1512 | 102.1133 | 0.033921 | -0.0051747 | 0.0028908 | 0.049217 | -0.0089134 | 0.060288 | 0.049318 | -0.0048589 | -0.0063367 | 0.055658 | 0.041269 | 0.052295 | -0.026423 | 3.8429 | -22.3001 | 101.9808 | 101.6525 | 101.6908 | -22.1152 | -22.2835 | 3.1322 | -22.4554 | 101.6767 | 101.9975 | 101.8954 | -22.2524 | 0.036026 | -0.13256 | 22.1248 | -0.14887 | -0.1849 | -0.46086 | -0.42255 | -0.10118 | -0.4366 | -0.13235 | -0.30422 | -0.20304 | -0.11584 | -0.21795 | 124.132 | 123.8037 | 123.842 | 25.994 | -124.2285 | 123.8279 | 124.1487 | 124.0466 | 25.2834 | -124.3657
409.9062 | 124.5163 | -21.7026 | 93.6768 | 0.049183 | -0.0041057 | 0.0028908 | 0.049217 | -0.0078444 | 0.059219 | 0.049318 | -0.0037909 | -0.0052687 | 0.057794 | 0.042337 | 0.054432 | -0.021844 | 3.8886 | -22.3184 | 102.0037 | 101.6616 | 101.7137 | -22.0968 | -22.3018 | 3.178 | -22.4371 | 101.6859 | 102.0067 | 101.9091 | -22.0509 | -0.39427 | 8.3269 | 21.6807 | -0.61579 | -0.22153 | 7.9849 | 8.0369 | -0.34832 | 8.0091 | -0.59927 | -0.73451 | -0.38619 | 8.3299 | 8.2324 | 123.7062 | 123.3642 | 123.4163 | 25.5912 | -115.7736 | 123.3885 | 123.7092 | 123.6117 | 24.8806 | -115.7277
410.9219 | 98.1949 | -23.7488 | 86.879 | 0.064445 | -0.0051747 | 0.0028908 | 0.051353 | -0.0089134 | 0.061356 | 0.07984 | -0.0027229 | -0.0063367 | 0.058862 | 0.042337 | 0.0555 | -0.017266 | 3.7788 | -23.756 | 100.5844 | 100.2513 | 100.2943 | -23.4293 | -23.7258 | 2.9948 | -23.8611 | 100.2803 | 100.569 | 100.4943 | -23.3467 | 0.31947 | 13.7054 | 23.7315 | -0.007172 | -0.32664 | 13.3724 | 13.4154 | 0.40208 | 13.4013 | 0.022952 | -0.11228 | -0.51436 | 13.69 | 13.6154 | 124.3331 | 124.0001 | 124.0431 | 27.5275 | -110.3083 | 124.0291 | 124.3178 | 124.2431 | 26.7436 | -110.2257
411.9062 | 120.3094 | -32.4875 | 63.5925 | 0.049183 | -0.0062427 | 0.0028908 | 0.050285 | -0.0089134 | 0.063493 | 0.07984 | -0.0037909 | -0.0074047 | 0.062067 | 0.042337 | 0.053363 | -0.021844 | 3.2568 | -27.6521 | 96.7111 | 96.3592 | 96.4346 | -27.2573 | -27.7322 | 2.2943 | -27.8629 | 96.3886 | 96.6131 | 96.5705 | -27.1883 | 5.2302 | 33.1185 | 32.4656 | 4.8354 | -0.39478 | 32.7667 | 32.842 | 5.2992 | 32.796 | 4.7553 | 4.6246 | -0.67453 | 33.0205 | 32.9779 | 129.1985 | 128.8467 | 128.922 | 35.7443 | -90.8498 | 128.8761 | 129.1005 | 129.058 | 34.7818 | -90.7809
412.9219 | 98.703 | -28.7109 | 68.3853 | 0.064445 | -0.0041057 | 0.0028908 | 0.050285 | -0.0089134 | 0.067766 | 0.049318 | -0.0037909 | -0.0052687 | 0.068477 | 0.0402 | 0.054432 | -0.026423 | 2.3502 | -36.0074 | 88.296 | 88.0256 | 88.0466 | -35.2979 | -35.9922 | 1.0855 | -36.1137 | 88.1473 | 88.2617 | 88.2924 | -35.0089 | -6.5869 | 19.9107 | 28.6845 | -7.2965 | -0.70955 | 19.6403 | 19.6612 | -6.298 | 19.762 | -7.2813 | -7.4028 | -1.1047 | 19.8764 | 19.907 | 117.0069 | 116.7365 | 116.7575 | 31.0612 | -103.6832 | 116.8582 | 116.9726 | 117.0033 | 29.7965 | -103.3943
413.9062 | 124.3195 | -123.7747 | -0.004578 | 0.064445 | -0.0051747 | 0.0039598 | 0.050285 | -0.0078444 | 0.11584 | 0.049318 | -0.0048589 | -0.0063367 | 0.14218 | 0.041269 | 0.0555 | -0.067628 | -8.9498 | -120.2798 | 2.9502 | 2.7202 | 3.1043 | -120.7956 | -120.8906 | -14.1387 | -121.1678 | 2.7263 | 2.9303 | 2.6633 | -120.7839 | 2.9792 | 2.9548 | 123.7071 | 3.4949 | 0.51572 | 2.7248 | 3.1089 | 2.9908 | 2.7309 | 2.8841 | 2.6069 | -0.38388 | 2.9349 | 2.6679 | 126.725 | 126.495 | 126.879 | 114.825 | -120.791 | 126.501 | 126.705 | 126.4381 | 109.636 | -120.7794
414.9062 | 123.6603 | -123.3536 | 0.064087 | 0.049183 | -0.0062427 | 0.0018228 | 0.050285 | -0.0067764 | 0.11691 | 0.034057 | -0.0048589 | -0.0074047 | 0.14539 | 0.042337 | 0.0555 | -0.058472 | -9.0276 | -123.5854 | 0.15285 | 0.069043 | 0.17402 | -124.2664 | -123.6058 | -14.0059 | -123.8738 | 0.061616 | 0.14191 | 0.18632 | -124.1997 | -0.91281 | 0.088765 | 123.2951 | -0.23178 | 0.68103 | 0.004956 | 0.10993 | -0.84615 | -0.002471 | -0.25223 | -0.52025 | 0.3259 | 0.07782 | 0.12223 | 123.5064 | 123.4226 | 123.5276 | 114.326 | -124.3305 | 123.4152 | 123.4955 | 123.5399 | 109.3477 | -124.2638
415.9219 | 124.0631 | -123.6786 | 0.11902 | 0.049183 | -0.0073107 | 0.0039598 | 0.050285 | -0.0067764 | 0.11584 | 0.064579 | -0.0059269 | -0.0063367 | 0.14539 | 0.042337 | 0.056568 | -0.06305 | -9.0734 | -123.6037 | 0.12538 | 0.046148 | 0.14197 | -124.2939 | -123.6287 | -13.7403 | -123.9013 | 0.04788 | 0.11444 | 0.15884 | -124.2318 | -0.61527 | 0.006363 | 123.6155 | 0.074918 | 0.69019 | -0.072871 | 0.022947 | -0.55319 | -0.071139 | 0.049892 | -0.22271 | 0.33048 | -0.004583 | 0.039826 | 123.804 | 123.7247 | 123.8206 | 114.6052 | -124.4129 | 123.7265 | 123.793 | 123.8374 | 109.9382 | -124.3508
416.9219 | 124.1089 | -123.6786 | 0.064087 | 0.079707 | -0.0051747 | 0.0018228 | 0.049217 | -0.0089134 | 0.11691 | 0.07984 | -0.0048589 | -0.0063367 | 0.14646 | 0.042337 | 0.0555 | -0.06305 | -9.1512 | -123.622 | 0.11165 | 0.027833 | 0.12823 | -124.3213 | -123.647 | -13.7129 | -123.9242 | 0.015831 | 0.086964 | 0.14511 | -124.2547 | -0.64274 | 0.04756 | 123.6155 | 0.056605 | 0.69935 | -0.036254 | 0.064143 | -0.57608 | -0.048256 | 0.031577 | -0.2456 | 0.33048 | 0.022877 | 0.081022 | 123.7902 | 123.7064 | 123.8068 | 114.5274 | -124.3854 | 123.6944 | 123.7656 | 123.8237 | 109.9657 | -124.3188
417.9219 | 124.1364 | -123.7793 | 0.10986 | 0.079707 | -0.0062427 | 0.00075378 | 0.049217 | -0.0067764 | 0.11691 | 0.064579 | -0.0048589 | -0.0084727 | 0.14646 | 0.042337 | 0.054432 | -0.06305 | -9.2886 | -123.622 | 0.052128 | 0.018675 | 0.11449 | -124.3213 | -123.6333 | -13.6534 | -123.9242 | 0.015831 | 0.086964 | 0.13595 | -124.2547 | -0.54204 | -0.057735 | 123.7162 | 0.15731 | 0.69935 | -0.091188 | 0.004631 | -0.47538 | -0.094032 | 0.14602 | -0.14489 | 0.33048 | -0.022899 | 0.026089 | 123.8314 | 123.798 | 123.8938 | 114.4907 | -124.4312 | 123.7951 | 123.8663 | 123.9152 | 110.1259 | -124.3645
418.9219 | 124.1867 | -123.7427 | 0.10529 | 0.033921 | -0.0073107 | 0.0018228 | 0.050285 | -0.0046394 | 0.11477 | 0.049318 | -0.0048589 | -0.0074047 | 0.14753 | 0.041269 | 0.054432 | -0.058472 | -9.4534 | -123.6128 | 0.047549 | 0.009517 | 0.10992 | -124.3305 | -123.6333 | -13.6442 | -123.9242 | 0.011252 | 0.073228 | 0.13137 | -124.2638 | -0.58781 | -0.057737 | 123.6842 | 0.12985 | 0.71766 | -0.095769 | 0.00463 | -0.52115 | -0.094034 | 0.1094 | -0.18151 | 0.33964 | -0.032058 | 0.026087 | 123.7902 | 123.7522 | 123.8526 | 114.2893 | -124.4358 | 123.7539 | 123.8159 | 123.874 | 110.0985 | -124.3691
419.9062 | 124.1913 | -123.8434 | 0.10071 | 0.064445 | -0.0062427 | 0.0039598 | 0.049217 | -0.0057084 | 0.11584 | 0.07984 | -0.0037909 | -0.0063367 | 0.14539 | 0.041269 | 0.0555 | -0.058472 | -9.6182 | -123.6128 | 0.042971 | 0.014096 | 0.10076 | -124.3259 | -123.6379 | -13.7083 | -123.9242 | 0.002095 | 0.064071 | 0.12222 | -124.2638 | -0.48253 | -0.057737 | 123.7849 | 0.23056 | 0.71308 | -0.086612 | 5.1e-05 | -0.42045 | -0.098613 | 0.20553 | -0.080805 | 0.33964 | -0.036637 | 0.021508 | 123.8864 | 123.8575 | 123.9441 | 114.2251 | -124.4266 | 123.8455 | 123.9075 | 123.9656 | 110.1351 | -124.3645
420.9219 | 123.9807 | -123.3948 | 0.09613 | 0.033921 | -0.0073107 | 0.0039598 | 0.049217 | -0.0089134 | 0.11477 | 0.064579 | -0.0048589 | -0.0063367 | 0.14753 | 0.042337 | 0.0555 | -0.058472 | -9.838 | -123.6128 | 0.038393 | 0.009517 | 0.09618 | -124.3305 | -123.6333 | -13.7816 | -123.9288 | -0.002483 | 0.073228 | 0.12222 | -124.273 | -0.93572 | -0.057737 | 123.3363 | -0.21805 | 0.71766 | -0.086613 | 5e-05 | -0.87821 | -0.098613 | -0.2385 | -0.53399 | 0.34422 | -0.022902 | 0.026086 | 123.4332 | 123.4043 | 123.491 | 113.5568 | -124.4266 | 123.3923 | 123.468 | 123.517 | 109.6132 | -124.3691
421.9062 | 124.4064 | -109.0027 | 0.11902 | 0.064445 | -0.0073107 | 0.0028908 | 0.051353 | -0.0067764 | 0.11477 | 0.07984 | -0.0059269 | -0.0063367 | 0.14646 | 0.041269 | 0.0555 | -0.053893 | -10.0578 | -123.6037 | 0.047549 | -0.00422 | 0.10992 | -124.3351 | -123.6287 | -14.0105 | -123.9196 | -0.002483 | 0.077807 | 0.12679 | -124.273 | -15.3324 | -0.07147 | 108.9488 | -14.601 | 0.7314 | -0.12324 | -0.009103 | -15.2703 | -0.1215 | -14.626 | -14.9169 | 0.35338 | -0.041212 | 0.007775 | 109.0502 | 108.9985 | 109.1126 | 98.9449 | -124.4541 | 109.0002 | 109.0805 | 109.1295 | 94.9922 | -124.392
422.9219 | 124.3149 | -123.9532 | 0.10986 | 0.064445 | -0.0062427 | 0.0039598 | 0.051353 | -0.0078444 | 0.11477 | 0.049318 | -0.0059269 | -0.0063367 | 0.14646 | 0.043405 | 0.0555 | -0.058472 | -10.2547 | -123.6037 | 0.042971 | 0.009517 | 0.09618 | -124.3259 | -123.615 | -14.4363 | -123.915 | -0.002483 | 0.06865 | 0.12222 | -124.2776 | -0.37266 | -0.066892 | 123.8948 | 0.34958 | 0.72224 | -0.10035 | -0.013683 | -0.32432 | -0.11235 | 0.33829 | 0.038216 | 0.36254 | -0.041213 | 0.012353 | 123.9962 | 123.9628 | 124.0494 | 113.6986 | -124.4358 | 123.9508 | 124.0219 | 124.0755 | 109.5169 | -124.3874
423.9062 | 123.9166 | -113.1821 | 0.1236 | 0.033921 | -0.0073107 | 0.00075378 | 0.049217 | -0.0089134 | 0.11477 | 0.064579 | -0.0059269 | -0.0063367 | 0.14753 | 0.043405 | 0.054432 | -0.058472 | -10.6576 | -123.5991 | 0.033814 | -0.036272 | 0.091601 | -124.3305 | -123.615 | -14.853 | -123.9059 | -0.007062 | 0.064071 | 0.12222 | -124.2776 | -11.1484 | -0.089782 | 113.1236 | -10.417 | 0.7314 | -0.15987 | -0.031995 | -11.0955 | -0.13066 | -10.4329 | -10.7238 | 0.37169 | -0.059525 | -0.00138 | 113.2159 | 113.1458 | 113.2737 | 102.5245 | -124.4541 | 113.175 | 113.2461 | 113.3043 | 98.3291 | -124.4012
424.9062 | 123.761 | -123.4085 | 0.10529 | 0.049183 | -0.0083797 | 0.0028908 | 0.051353 | -0.0089134 | 0.11584 | 0.064579 | -0.0037909 | -0.0063367 | 0.14646 | 0.044474 | 0.0555 | -0.058472 | -11.0605 | -123.5991 | 0.038393 | -0.040851 | 0.087023 | -124.3305 | -123.6058 | -15.4436 | -123.915 | -0.007062 | 0.06865 | 0.12222 | -124.273 | -0.92198 | -0.066893 | 123.35 | -0.19058 | 0.7314 | -0.14614 | -0.018263 | -0.86448 | -0.11235 | -0.1973 | -0.50652 | 0.35796 | -0.036636 | 0.01693 | 123.4469 | 123.3677 | 123.4955 | 112.348 | -124.4358 | 123.4014 | 123.4772 | 123.5307 | 107.9649 | -124.3783
425.9062 | 123.468 | -123.4909 | 0.12817 | 0.049183 | -0.0073107 | 0.00075378 | 0.048148 | -0.0089134 | 0.1137 | 0.049318 | -0.0048589 | -0.0084727 | 0.14539 | 0.043405 | 0.056568 | -0.06305 | -11.4909 | -123.5991 | 0.038393 | -0.036272 | 0.091601 | -124.3213 | -123.5921 | -16.1167 | -123.9105 | -0.002483 | 0.06865 | 0.007751 | -124.2776 | -0.83043 | -0.089781 | 123.4279 | -0.10819 | 0.72224 | -0.16445 | -0.036573 | -0.78666 | -0.13066 | -0.10116 | -0.41955 | 0.36711 | -0.059524 | -0.12042 | 123.5293 | 123.4546 | 123.5825 | 112 | -124.4495 | 123.4884 | 123.5596 | 123.4987 | 107.3742 | -124.4057
426.9844 | 123.642 | -123.7747 | 0.10986 | 0.049183 | -0.0073107 | 0.0028908 | 0.050285 | -0.0099814 | 0.11477 | 0.034057 | -0.0069959 | -0.0074047 | 0.14539 | 0.043405 | 0.056568 | -0.06305 | -12.109 | -123.5854 | 0.038393 | -0.036272 | 0.087023 | -124.3259 | -123.5921 | -16.7715 | -123.8921 | -0.007062 | 0.064071 | -0.05635 | -124.2776 | -0.55119 | -0.07147 | 123.7117 | 0.18936 | 0.74055 | -0.14614 | -0.02284 | -0.50285 | -0.11693 | 0.18265 | -0.11742 | 0.38543 | -0.045792 | -0.16621 | 123.8131 | 123.7384 | 123.8617 | 111.6657 | -124.4358 | 123.7677 | 123.8388 | 123.7184 | 107.0033 | -124.3874
427.9219 | 124.3835 | -124.1638 | 0.11444 | 0.064445 | -0.0094477 | 0.0018228 | 0.051353 | -0.0067764 | 0.11691 | 0.07984 | -0.0037909 | -0.0063367 | 0.14646 | 0.044474 | 0.054432 | -0.053893 | -12.8049 | -123.5808 | 0.038393 | -0.04543 | 0.091601 | -124.3259 | -123.5829 | -17.3438 | -123.8921 | -0.007062 | 0.064071 | -0.060928 | -124.2776 | -0.16209 | -0.076048 | 124.1099 | 0.58304 | 0.74513 | -0.15987 | -0.02284 | -0.11375 | -0.1215 | 0.58091 | 0.27168 | 0.38543 | -0.05037 | -0.17537 | 124.2022 | 124.1184 | 124.2554 | 111.3589 | -124.4404 | 124.1568 | 124.2279 | 124.1029 | 106.82 | -124.392
428.9062 | 123.7473 | -123.3261 | 0.12817 | 0.033921 | -0.0083797 | 0.0028908 | 0.049217 | -0.0078444 | 0.11691 | 0.064579 | -0.0037909 | -0.0074047 | 0.14753 | 0.043405 | 0.054432 | -0.06305 | -13.6245 | -123.5716 | 0.042971 | -0.036272 | 0.091601 | -124.3259 | -123.5692 | -17.9985 | -123.8738 | 0.002095 | 0.073228 | -0.05635 | -124.2776 | -0.9998 | -0.085203 | 123.2631 | -0.24551 | 0.75429 | -0.16445 | -0.036573 | -0.95146 | -0.12608 | -0.24306 | -0.54771 | 0.40375 | -0.054946 | -0.18452 | 123.3691 | 123.2898 | 123.4177 | 109.7016 | -124.4541 | 123.3282 | 123.3993 | 123.2698 | 105.3276 | -124.4057
429.9062 | 123.7839 | -123.6832 | 0.11444 | 0.064445 | -0.0073107 | 0.0018228 | 0.049217 | -0.0078444 | 0.1137 | 0.049318 | -0.0048589 | -0.0084727 | 0.14539 | 0.043405 | 0.0555 | -0.053893 | -14.2884 | -123.5625 | 0.047549 | -0.040851 | 0.087023 | -124.3259 | -123.5738 | -18.8181 | -123.8692 | -0.007062 | 0.064071 | -0.051771 | -124.273 | -0.64274 | -0.066892 | 123.6293 | 0.1207 | 0.76345 | -0.15529 | -0.027418 | -0.58982 | -0.1215 | 0.10941 | -0.18608 | 0.40375 | -0.05037 | -0.16621 | 123.7307 | 123.6423 | 123.7702 | 109.3948 | -124.4404 | 123.6761 | 123.7472 | 123.6314 | 104.865 | -124.3874
430.9219 | 124.3927 | -124.0128 | 0.10529 | 0.049183 | -0.0094477 | 0.0039598 | 0.048148 | -0.0078444 | 0.11477 | 0.049318 | -0.0037909 | -0.0063367 | 0.14539 | 0.044474 | 0.0555 | -0.053893 | -15.0301 | -123.5625 | 0.033814 | -0.040851 | 0.091601 | -124.3213 | -123.5646 | -19.6331 | -123.8555 | 0.002095 | 0.059493 | -0.060928 | -124.2684 | -0.30858 | -0.071472 | 123.9589 | 0.45029 | 0.75887 | -0.14614 | -0.013685 | -0.25565 | -0.10319 | 0.44816 | 0.15725 | 0.4129 | -0.045793 | -0.16621 | 124.0466 | 123.9719 | 124.1044 | 108.9826 | -124.4266 | 124.0149 | 124.0722 | 123.9518 | 104.3796 | -124.3737
431.9062 | 110.7971 | -19.3954 | 85.762 | 0.064445 | -0.0062427 | 0.0028908 | 0.051353 | -0.0089134 | 0.064561 | 0.049318 | -0.0048589 | -0.0084727 | 0.27678 | 0.045542 | 0.21467 | -0.021844 | 3.7284 | -35.5542 | 88.6577 | 88.8544 | 87.9046 | -35.0506 | -17.8513 | -2.5683 | -17.9957 | 0.011252 | 0.082386 | 0.10848 | -18.6992 | -15.6552 | 2.8956 | 19.3736 | -16.1587 | -0.50356 | 3.0924 | 2.1426 | 0.69625 | -85.7508 | 1.5441 | 1.3997 | 0.70346 | -85.6796 | -85.6535 | 108.0531 | 108.2498 | 107.3001 | 23.1238 | -120.8126 | 19.4067 | 19.4778 | 19.5039 | 16.8271 | -104.4612
432.9219 | 123.7015 | -18.8141 | 101.7563 | 0.033921 | -0.0073107 | 0.0028908 | 0.050285 | -0.0089134 | 0.059219 | 0.049318 | -0.0059269 | -0.0074047 | 0.10693 | 0.047679 | 0.054432 | -0.017266 | 6.8464 | -19.2326 | 105.0117 | 104.6517 | 104.7081 | -19.0748 | -0.031003 | -0.11411 | -0.079245 | -0.048268 | 0.018285 | 0.07643 | -0.11836 | -0.26066 | 3.2554 | 18.7968 | -0.41852 | -0.15786 | 2.8954 | 2.9518 | 18.6957 | -101.8046 | 18.7831 | 18.7348 | 0.039116 | -101.738 | -101.6799 | 123.8258 | 123.4658 | 123.5222 | 25.6605 | -120.831 | 18.7658 | 18.8324 | 18.8905 | 18.7 | -101.8746
433.9062 | 102.7176 | -15.8936 | 78.3142 | 0.049183 | -0.0073107 | 0.0050278 | 0.050285 | -0.0099814 | 0.059219 | 0.064579 | -0.0027229 | -0.0063367 | 0.1048 | 0.04661 | 0.0555 | -0.008109 | 7.4828 | -19.2051 | 105.0437 | 104.6746 | 104.731 | -19.0519 | -0.00811 | -0.12327 | -0.051772 | -0.048268 | 0.013707 | -0.083821 | -0.10004 | -3.1583 | 26.7295 | 15.8854 | -3.3116 | -0.15328 | 26.3604 | 26.4168 | 15.7935 | -78.3625 | 15.8854 | 15.8418 | 0.048273 | -78.3005 | -78.398 | 120.9373 | 120.5681 | 120.6245 | 23.3764 | -97.3661 | 15.8453 | 15.9073 | 15.8097 | 15.7703 | -78.4143
434.9062 | 109.2178 | -19.5969 | 83.757 | 0.049183 | -0.0073107 | 0.0028908 | 0.049217 | -0.0089134 | 0.057083 | 0.049318 | -0.0048589 | -0.0063367 | 0.10693 | 0.04661 | 0.057636 | -0.008109 | 8.1422 | -19.1868 | 105.0529 | 104.702 | 104.7493 | -19.0473 | 0.001048 | -0.10037 | -0.051772 | -0.048268 | 0.018285 | -0.0884 | -0.08173 | 0.54959 | 21.2959 | 19.5888 | 0.41004 | -0.13955 | 20.945 | 20.9923 | 19.5151 | -83.8053 | 19.5979 | 19.5451 | 0.029958 | -83.7387 | -83.8454 | 124.6497 | 124.2989 | 124.3462 | 27.739 | -102.8043 | 19.5486 | 19.6151 | 19.5085 | 19.4965 | -83.8387
435.9062 | 108.8058 | -19.6289 | 85.4141 | 0.049183 | -0.0083797 | 0.0028908 | 0.050285 | -0.0078444 | 0.057083 | 0.034057 | -0.0059269 | -0.0074047 | 0.108 | 0.047679 | 0.056568 | -0.008109 | 8.5405 | -19.1685 | 105.0575 | 104.702 | 104.7539 | -19.029 | -0.003531 | -0.077479 | -0.047194 | -0.048268 | 0.013707 | -0.079243 | -0.077151 | 0.59994 | 19.6433 | 19.6208 | 0.46039 | -0.13955 | 19.2879 | 19.3398 | 19.5518 | -85.4624 | 19.6254 | 19.5817 | 0.029957 | -85.4004 | -85.4934 | 124.6864 | 124.331 | 124.3828 | 28.1694 | -104.4431 | 19.5806 | 19.6426 | 19.5497 | 19.5514 | -85.4913
436.9062 | 116.4688 | -19.1391 | 89.5981 | 0.064445 | -0.0073107 | 0.0050278 | 0.052422 | -0.0078444 | 0.058151 | 0.049318 | -0.0059269 | -0.0074047 | 0.10586 | 0.047679 | 0.0555 | -0.012688 | 8.6046 | -19.1136 | 105.0529 | 104.702 | 104.763 | -19.0335 | 0.010205 | -0.045428 | -0.038036 | -0.057425 | 0.018285 | -0.079243 | -0.077151 | 0.10556 | 15.4548 | 19.1264 | 0.025525 | -0.080032 | 15.104 | 15.165 | 19.0619 | -89.6555 | 19.1493 | 19.1011 | 0.039115 | -89.5798 | -89.6773 | 124.192 | 123.8411 | 123.9021 | 27.7437 | -108.6316 | 19.0817 | 19.1574 | 19.0599 | 19.0937 | -89.6752
437.9219 | 123.8159 | -19.0704 | 104.3152 | 0.033921 | -0.0083797 | 0.0039598 | 0.049217 | -0.011049 | 0.058151 | 0.049318 | -0.0048589 | -0.0074047 | 0.108 | 0.04661 | 0.0555 | -0.008109 | 8.6367 | -19.1044 | 105.0575 | 104.702 | 104.7539 | -19.0427 | 0.001048 | -0.017956 | -0.042615 | -0.052847 | 0.013707 | -0.079243 | -0.072572 | 0.027735 | 0.74227 | 19.0623 | -0.033983 | -0.061718 | 0.38686 | 0.43869 | 18.9979 | -104.368 | 19.0715 | 19.0278 | 0.029957 | -104.3015 | -104.3944 | 124.1279 | 123.7725 | 123.8243 | 27.7071 | -123.3579 | 19.0176 | 19.0841 | 18.9912 | 19.0525 | -104.3878
438.9062 | 106.3293 | -19.6381 | 94.4183 | 0.064445 | -0.0073107 | 0.0039598 | 0.050285 | -0.0089134 | 0.057083 | 0.07984 | -0.0048589 | -0.0084727 | 0.10586 | 0.045542 | 0.056568 | -0.008109 | 8.6321 | -19.0998 | 105.062 | 104.702 | 104.7447 | -19.0427 | 0.005626 | -0.008798 | -0.042615 | -0.057425 | 0.013707 | -0.074664 | -0.077151 | 0.59536 | 10.6437 | 19.63 | 0.53822 | -0.057139 | 10.2837 | 10.3264 | 19.5609 | -94.4758 | 19.6437 | 19.5954 | 0.034536 | -94.4046 | -94.493 | 124.7001 | 124.3401 | 124.3828 | 28.2701 | -113.461 | 19.5806 | 19.6518 | 19.5634 | 19.6293 | -94.4955
439.9062 | 114.9719 | -19.1025 | 96.666 | 0.049183 | -0.0062427 | 0.0028908 | 0.050285 | -0.0099814 | 0.058151 | 0.049318 | -0.0048589 | -0.0074047 | 0.10586 | 0.047679 | 0.056568 | -0.003531 | 8.6275 | -19.0953 | 105.0529 | 104.6883 | 104.7493 | -19.0519 | -0.003531 | -0.00422 | -0.038036 | -0.052847 | 0.013707 | -0.074664 | -0.072572 | 0.050621 | 8.3869 | 19.0989 | 0.007217 | -0.043404 | 8.0224 | 8.0833 | 19.0299 | -96.7188 | 19.0989 | 19.0644 | 0.034536 | -96.6522 | -96.7406 | 124.1554 | 123.7908 | 123.8518 | 27.73 | -115.7178 | 19.0496 | 19.1162 | 19.0278 | 19.0983 | -96.7385
440.9062 | 114.9765 | -19.0567 | 89.5844 | 0.049183 | -0.0083797 | 0.0028908 | 0.050285 | -0.0089134 | 0.058151 | 0.049318 | -0.0069959 | -0.0084727 | 0.10586 | 0.047679 | 0.054432 | -0.012688 | 8.7099 | -19.0998 | 105.0483 | 104.6837 | 104.7447 | -19.0656 | 0.005626 | -0.00422 | -0.042615 | -0.048268 | 0.018285 | -0.0884 | -0.063415 | -0.008892 | 15.4639 | 19.044 | -0.043137 | -0.034245 | 15.0994 | 15.1604 | 18.9933 | -89.6326 | 19.0623 | 19.0141 | 0.0208 | -89.5661 | -89.6728 | 124.105 | 123.7404 | 123.8014 | 27.7666 | -108.6499 | 19.0084 | 19.075 | 18.9683 | 19.0525 | -89.6478
441.9062 | 100.5157 | -19.725 | 89.7629 | 0.049183 | -0.0073107 | 0.0018228 | 0.049217 | -0.0089134 | 0.057083 | 0.095101 | -0.0059269 | -0.0063367 | 0.10693 | 0.047679 | 0.056568 | -0.026423 | 8.8106 | -19.0998 | 105.0391 | 104.6837 | 104.7447 | -19.0702 | 0.005626 | 0.009516 | -0.038036 | -0.052847 | 0.013707 | -0.083821 | -0.067994 | 0.65486 | 15.2763 | 19.6986 | 0.6252 | -0.029666 | 14.9209 | 14.9818 | 19.657 | -89.8157 | 19.7307 | 19.687 | 0.029958 | -89.7492 | -89.8467 | 124.7642 | 124.4088 | 124.4698 | 28.5357 | -108.8331 | 19.6722 | 19.7387 | 19.6412 | 19.7346 | -89.8309
442.9219 | 113.2462 | -19.2581 | 86.7004 | 0.049183 | -0.0062427 | 0.0028908 | 0.050285 | -0.0089134 | 0.059219 | 0.07984 | -0.0048589 | -0.0084727 | 0.108 | 0.048747 | 0.056568 | -0.012688 | 8.8885 | -19.0998 | 105.0437 | 104.6837 | 104.7401 | -19.0702 | 0.005626 | 0.004938 | -0.042615 | -0.048268 | 0.018285 | -0.0884 | -0.072572 | 0.18794 | 18.3433 | 19.2454 | 0.15828 | -0.029666 | 17.9833 | 18.0397 | 19.1855 | -86.7487 | 19.2637 | 19.2155 | 0.029957 | -86.6822 | -86.7888 | 124.3018 | 123.9419 | 123.9983 | 28.1466 | -105.7706 | 19.2098 | 19.2764 | 19.1697 | 19.2631 | -86.773
443.9219 | 124.1913 | -18.7912 | 98.7946 | 0.049183 | -0.0073107 | 0.0039598 | 0.050285 | -0.0078444 | 0.058151 | 0.064579 | -0.0048589 | -0.0084727 | 0.10907 | 0.047679 | 0.054432 | -0.017266 | 8.98 | -19.109 | 105.03 | 104.6746 | 104.7356 | -19.0702 | 0.005626 | 0.009516 | -0.042615 | -0.052847 | 0.013707 | -0.0884 | -0.058836 | -0.27897 | 6.2354 | 18.7739 | -0.3178 | -0.038823 | 5.88 | 5.941 | 18.7324 | -98.8474 | 18.7968 | 18.7486 | 0.016221 | -98.7808 | -98.883 | 123.8212 | 123.4658 | 123.5268 | 27.7712 | -117.8647 | 18.7384 | 18.8049 | 18.7028 | 18.8007 | -98.8534
444.9219 | 123.6923 | -18.8278 | 104.5395 | 0.064445 | -0.0062427 | 0.0039598 | 0.050285 | -0.0089134 | 0.057083 | 0.034057 | -0.0059269 | -0.0074047 | 0.11014 | 0.04661 | 0.0555 | -0.008109 | 9.0625 | -19.1044 | 105.0254 | 104.6746 | 104.7264 | -19.0839 | 0.010205 | 0.009516 | -0.042615 | -0.048268 | 0.018285 | -0.0884 | -0.067994 | -0.25609 | 0.48592 | 18.8197 | -0.2766 | -0.020508 | 0.13508 | 0.18691 | 18.7598 | -104.5878 | 18.838 | 18.7852 | 0.025379 | -104.5212 | -104.6279 | 123.8532 | 123.5024 | 123.5542 | 27.8903 | -123.6234 | 18.7796 | 18.8461 | 18.7394 | 18.8373 | -104.6075
445.9219 | 123.7793 | -18.9056 | 104.4571 | 0.033921 | -0.0073107 | 0.0050278 | 0.049217 | -0.0099814 | 0.058151 | 0.018796 | -0.0048589 | -0.0084727 | 0.108 | 0.04661 | 0.057636 | -0.012688 | 9.1357 | -19.1182 | 105.0254 | 104.67 | 104.7218 | -19.0839 | 0.010205 | 0.009516 | -0.028879 | -0.048268 | 0.013707 | -0.097557 | -0.063415 | -0.17827 | 0.56831 | 18.893 | -0.21251 | -0.034242 | 0.2129 | 0.26473 | 18.8422 | -104.5054 | 18.9158 | 18.8768 | 0.034536 | -104.4434 | -104.5546 | 123.931 | 123.5756 | 123.6275 | 28.0414 | -123.541 | 18.8574 | 18.9193 | 18.8081 | 18.9152 | -104.5205
446.9688 | 117.2195 | -19.1208 | 104.5395 | 0.064445 | -0.0062427 | 0.0028908 | 0.049217 | -0.0078444 | 0.058151 | 0.064579 | -0.0037909 | -0.0074047 | 0.10907 | 0.047679 | 0.054432 | -0.012688 | 9.2319 | -19.1227 | 105.0208 | 104.6746 | 104.7218 | -19.1068 | 0.001048 | 0.004938 | -0.038036 | -0.052847 | 0.013707 | -0.097557 | -0.063415 | 0.013985 | 0.48134 | 19.1081 | -0.001942 | -0.015927 | 0.13508 | 0.18234 | 19.0574 | -104.5923 | 19.1218 | 19.0828 | 0.025379 | -104.5258 | -104.637 | 124.1416 | 123.7954 | 123.8426 | 28.3527 | -123.6463 | 19.0679 | 19.1345 | 19.0232 | 19.1257 | -104.6029
447.9219 | 124.4934 | -18.8278 | 93.8004 | 0.049183 | -0.0051747 | 0.0028908 | 0.049217 | -0.0078444 | 0.058151 | 0.049318 | -0.0059269 | -0.0084727 | 0.108 | 0.049815 | 0.0555 | -0.017266 | 9.3463 | -19.1136 | 105.0117 | 104.6654 | 104.7127 | -19.1022 | 0.005626 | 0.000359 | -0.038036 | -0.052847 | 0.009128 | -0.092979 | -0.058836 | -0.27441 | 11.2113 | 18.8106 | -0.28575 | -0.011348 | 10.8651 | 10.9123 | 18.769 | -93.8532 | 18.8334 | 18.7898 | 0.0208 | -93.7912 | -93.8933 | 123.8395 | 123.4932 | 123.5405 | 28.1742 | -112.9026 | 18.775 | 18.8369 | 18.7348 | 18.8282 | -93.8592
448.9219 | 124.4431 | -18.7592 | 102.095 | 0.033921 | -0.0062427 | 0.0050278 | 0.051353 | -0.0078444 | 0.057083 | 0.07984 | -0.0048589 | -0.0074047 | 0.108 | 0.047679 | 0.0555 | -0.012688 | 9.4196 | -19.1273 | 104.9979 | 104.6563 | 104.7035 | -19.0976 | 0.001048 | 0.004938 | -0.042615 | -0.048268 | 0.004549 | -0.083821 | -0.063415 | -0.33849 | 2.9029 | 18.7465 | -0.36815 | -0.029662 | 2.5612 | 2.6085 | 18.6957 | -102.1433 | 18.7602 | 18.7165 | 0.0208 | -102.0905 | -102.1789 | 123.7571 | 123.4154 | 123.4627 | 28.1787 | -121.1927 | 18.7109 | 18.7637 | 18.6753 | 18.7641 | -102.1584
449.9062 | 106.572 | -19.4092 | 104.1504 | 0.064445 | -0.0073107 | 0.0028908 | 0.052422 | -0.0089134 | 0.057083 | 0.064579 | -0.0069959 | -0.0074047 | 0.10907 | 0.04661 | 0.054432 | -0.017266 | 9.5112 | -19.1456 | 104.9705 | 104.6334 | 104.676 | -19.1434 | 0.005626 | -0.00422 | -0.033458 | -0.057425 | 0.009128 | -0.083821 | -0.058836 | 0.26574 | 0.82007 | 19.3919 | 0.26356 | -0.002186 | 0.48297 | 0.52565 | 19.3503 | -104.2078 | 19.4148 | 19.3757 | 0.025378 | -104.1413 | -104.2342 | 124.3796 | 124.0425 | 124.0852 | 28.9203 | -123.2938 | 19.3518 | 19.4183 | 19.3254 | 19.405 | -104.2092
450.9219 | 124.3744 | -19.0338 | 103.9764 | 0.033921 | -0.0073107 | 0.0039598 | 0.050285 | -0.011049 | 0.059219 | 0.049318 | -0.0037909 | -0.0084727 | 0.108 | 0.048747 | 0.0555 | -0.008109 | 9.5341 | -19.1502 | 104.9613 | 104.6105 | 104.6623 | -19.1618 | 0.005626 | 0.000359 | -0.033458 | -0.048268 | 0.013707 | -0.079243 | -0.063415 | -0.12794 | 0.98487 | 19.0257 | -0.11639 | 0.011552 | 0.63403 | 0.68586 | 18.9704 | -104.0247 | 19.0394 | 19.0004 | 0.029957 | -103.9627 | -104.0557 | 123.9951 | 123.6443 | 123.6961 | 28.5679 | -123.1382 | 18.9855 | 19.0475 | 18.9546 | 19.0342 | -104.0399
451.9062 | 111.5204 | -19.162 | 104.6997 | 0.049183 | -0.0083797 | 0.0039598 | 0.050285 | -0.0089134 | 0.057083 | 0.064579 | -0.0069959 | -0.0084727 | 0.11014 | 0.049815 | 0.0555 | -0.021844 | 9.5066 | -19.1594 | 104.9476 | 104.6013 | 104.6531 | -19.1709 | 0.005626 | 0.004938 | -0.042615 | -0.052847 | 0.013707 | -0.0884 | -0.058836 | -0.008922 | 0.24786 | 19.1401 | 0.00263 | 0.011552 | -0.098396 | -0.04656 | 19.1032 | -104.7526 | 19.1676 | 19.1194 | 0.016221 | -104.686 | -104.7881 | 124.1096 | 123.7633 | 123.8151 | 28.6686 | -123.8706 | 19.1091 | 19.1757 | 19.0736 | 19.1669 | -104.7585
452.9219 | 94.3222 | -19.1574 | 81.015 | 0.064445 | -0.0073107 | 0.0039598 | 0.052422 | -0.0078444 | 0.059219 | 0.07984 | -0.0059269 | -0.0074047 | 0.10907 | 0.048747 | 0.0555 | -0.026423 | 8.9388 | -20.6793 | 103.455 | 103.1361 | 103.1605 | -20.54 | -0.00811 | 0.000359 | -0.033458 | -0.057425 | 0.013707 | -0.083821 | -0.013048 | -1.3826 | 22.44 | 19.131 | -1.5219 | -0.13934 | 22.121 | 22.1455 | 19.1444 | -81.0724 | 19.1493 | 19.124 | -0.02041 | -81.0013 | -81.0988 | 122.6124 | 122.2935 | 122.3179 | 28.0962 | -101.555 | 19.1 | 19.1711 | 19.0736 | 19.1578 | -81.0281
453.9688 | 107.0618 | -19.6976 | 83.0063 | 0.064445 | -0.0083797 | 0.0039598 | 0.052422 | -0.0089134 | 0.058151 | 0.064579 | -0.0059269 | -0.0063367 | 0.11014 | 0.047679 | 0.053363 | -0.021844 | 9.2136 | -19.3837 | 104.737 | 104.409 | 104.4425 | -19.3632 | -0.017267 | -0.00422 | -0.038036 | -0.052847 | 0.009128 | -0.0884 | -0.058836 | 0.33435 | 21.7307 | 19.6757 | 0.31388 | -0.020469 | 21.4027 | 21.4362 | 19.6387 | -83.0591 | 19.6803 | 19.6595 | 0.0208 | -82.9972 | -83.0947 | 124.4345 | 124.1066 | 124.1401 | 28.9111 | -102.3695 | 19.6447 | 19.7067 | 19.6092 | 19.6934 | -83.0651
454.9062 | 123.8251 | -121.9849 | 1.0803 | 0.033921 | -0.0083797 | 0.0028908 | 0.12401 | -0.0078444 | 0.11477 | 0.07984 | -0.0048589 | -0.0074047 | 0.108 | 0.047679 | 0.0555 | -0.09052 | -32.5982 | -121.2184 | 2.1078 | 1.9876 | 2.1703 | -122.2425 | -0.012689 | 0.000359 | -0.038036 | -0.052847 | 0.018285 | -0.079243 | -0.049678 | -0.25764 | 1.0275 | 121.8943 | 0.76648 | 1.0241 | 0.90729 | 1.09 | 121.9352 | -1.1332 | 121.9722 | 121.9468 | 0.011642 | -1.062 | -1.1596 | 124.0927 | 123.9725 | 124.1552 | 89.3866 | -123.3228 | 121.932 | 122.0031 | 121.9056 | 121.9852 | -1.13
455.9062 | 121.9391 | -104.8508 | 1.2131 | 0.033921 | -0.0083797 | 0.00075378 | 0.12401 | -0.0099814 | 0.11584 | 0.07984 | -0.0069959 | -0.0084727 | 0.10907 | 0.048747 | 0.0555 | -0.12257 | -35.9818 | -122.0745 | 1.3066 | 1.2229 | 1.3095 | -123.1125 | -0.00811 | -0.008798 | -0.038036 | -0.052847 | 0.018285 | -0.079243 | -0.063415 | -18.2617 | 0.093532 | 104.7282 | -17.2238 | 1.038 | 0.009858 | 0.096436 | 104.7874 | -1.2659 | 104.8427 | 104.8127 | 0.025379 | -1.1948 | -1.2923 | 106.1574 | 106.0737 | 106.1603 | 68.8689 | -124.3256 | 104.7979 | 104.8691 | 104.7715 | 104.842 | -1.2765
456.9219 | 123.5733 | -123.1384 | 0.71411 | 0.064445 | -0.0073107 | 0.0018228 | 0.12614 | -0.0089134 | 0.11584 | 0.07984 | -0.0059269 | -0.0084727 | 0.10907 | 0.047679 | 0.0555 | -0.18667 | -37.7858 | -122.3034 | 1.0456 | 0.97109 | 1.0623 | -123.3689 | -0.012689 | 0.000359 | -0.038036 | -0.057425 | 0.013707 | -0.083821 | -0.054257 | -0.23049 | 0.33153 | 122.9518 | 0.83499 | 1.0655 | 0.25698 | 0.34815 | 123.0842 | -0.77154 | 123.1257 | 123.1004 | 0.016221 | -0.7004 | -0.79793 | 124.1841 | 124.1095 | 124.2007 | 85.3526 | -124.083 | 123.081 | 123.1521 | 123.0546 | 123.1388 | -0.76837
457.9219 | 123.5321 | -123.3765 | 0.89264 | 0.064445 | -0.0083797 | 0.0028908 | 0.12401 | -0.0099814 | 0.1137 | 0.049318 | -0.0037909 | -0.0084727 | 0.11014 | 0.049815 | 0.0555 | -0.11341 | -39.1319 | -122.363 | 0.95407 | 0.88409 | 0.97069 | -123.4605 | -0.00811 | -0.008798 | -0.033458 | -0.057425 | 0.018285 | -0.083821 | -0.058836 | -0.08403 | 0.061431 | 123.2631 | 1.0135 | 1.0975 | -0.008548 | 0.078054 | 123.3176 | -0.95006 | 123.3684 | 123.343 | 0.025378 | -0.87435 | -0.97646 | 124.3305 | 124.2606 | 124.3472 | 84.2446 | -124.3531 | 123.319 | 123.3948 | 123.2926 | 123.3677 | -0.95147
458.9219 | 123.5184 | -123.2712 | 0.92468 | 0.049183 | -0.0083797 | 0.0018228 | 0.12507 | -0.0067764 | 0.1137 | 0.064579 | -0.0059269 | -0.0095417 | 0.108 | 0.050884 | 0.054432 | -0.1363 | -40.3956 | -122.3767 | 0.83961 | 0.82456 | 0.92033 | -123.5154 | -0.00811 | -0.00422 | -0.038036 | -0.052847 | 0.022864 | -0.083821 | -0.054257 | -0.24426 | -0.085073 | 123.1349 | 0.89449 | 1.1387 | -0.10012 | -0.004355 | 123.2169 | -0.97753 | 123.2631 | 123.2331 | 0.016221 | -0.90182 | -1.0085 | 124.1108 | 124.0957 | 124.1915 | 82.8756 | -124.4401 | 123.2183 | 123.294 | 123.1874 | 123.267 | -0.97894
459.9062 | 124.1684 | -111.5524 | 0.90179 | 0.064445 | -0.0073107 | 0.00075378 | 0.12507 | -0.0099814 | 0.11477 | 0.064579 | -0.0059269 | -0.0084727 | 0.108 | 0.048747 | 0.054432 | -0.099677 | -41.5677 | -122.3263 | 0.83045 | 0.84288 | 0.93406 | -123.4971 | -0.00811 | -0.013377 | -0.033458 | -0.052847 | 0.009128 | -0.083821 | -0.054257 | -11.9447 | -0.07134 | 111.4528 | -10.7739 | 1.1708 | -0.058913 | 0.03227 | 111.4982 | -0.95464 | 111.5443 | 111.519 | 0.020799 | -0.89267 | -0.98562 | 112.3829 | 112.3953 | 112.4865 | 69.9847 | -124.3989 | 111.4996 | 111.5616 | 111.4686 | 111.5391 | -0.95605
460.9219 | 124.0128 | -122.4426 | 0.95673 | 0.064445 | -0.0073107 | 0.0018228 | 0.12401 | -0.0099814 | 0.11584 | 0.049318 | -0.0048589 | -0.0074047 | 0.10907 | 0.049815 | 0.054432 | -0.1363 | -42.5979 | -122.3172 | 0.8213 | 0.84288 | 0.92949 | -123.4925 | -0.00811 | -0.013377 | -0.038036 | -0.052847 | 0.018285 | -0.083821 | -0.058836 | -1.0499 | -0.13543 | 122.3063 | 0.12545 | 1.1754 | -0.11384 | -0.02724 | 122.3838 | -1.0096 | 122.4345 | 122.4046 | 0.0208 | -0.93844 | -1.0405 | 123.2639 | 123.2855 | 123.3721 | 79.8447 | -124.4493 | 122.3898 | 122.4609 | 122.3588 | 122.4292 | -1.0156
461.9219 | 123.587 | -123.2162 | 1.1444 | 0.049183 | -0.0073107 | 0.0039598 | 0.12507 | -0.0099814 | 0.11477 | 0.049318 | -0.0080639 | -0.0095417 | 0.108 | 0.048747 | 0.0555 | -0.24161 | -43.7563 | -122.4133 | 0.70226 | 0.71925 | 0.80586 | -123.6162 | -0.003531 | -0.00422 | -0.038036 | -0.052847 | 0.013707 | -0.0884 | -0.054257 | -0.39993 | -0.44215 | 122.9746 | 0.80293 | 1.2029 | -0.42516 | -0.33855 | 123.162 | -1.1973 | 123.2127 | 123.1782 | 0.016221 | -1.1307 | -1.2328 | 123.9185 | 123.9355 | 124.0221 | 79.4599 | -124.7606 | 123.1634 | 123.23 | 123.1278 | 123.212 | -1.1987
462.9219 | 123.5825 | -116.2582 | 0.78735 | 0.033921 | -0.0083797 | 0.0028908 | 0.12401 | -0.0099814 | 0.11691 | 0.064579 | -0.0059269 | -0.0084727 | 0.11014 | 0.048747 | 0.0555 | -0.24618 | -45.1482 | -122.3492 | 0.74346 | 0.76046 | 0.83791 | -123.5246 | -0.017267 | 0.000359 | -0.033458 | -0.062004 | 0.022864 | -0.0884 | -0.0451 | -7.2664 | -0.04389 | 116.0121 | -6.091 | 1.1754 | -0.026894 | 0.05056 | 116.2131 | -0.84936 | 116.241 | 116.2248 | 0.011642 | -0.76449 | -0.87575 | 117.0017 | 117.0187 | 117.0962 | 71.11 | -124.312 | 116.1962 | 116.2811 | 116.1698 | 116.2586 | -0.83245
463.9062 | 124.4385 | -106.3705 | 0.96588 | 0.049183 | -0.0094477 | 0.0018228 | 0.12401 | -0.0099814 | 0.1137 | 0.049318 | -0.0059269 | -0.0095417 | 0.11014 | 0.049815 | 0.054432 | -0.22787 | -46.2013 | -122.3263 | 0.73431 | 0.7513 | 0.83791 | -123.5383 | -0.00811 | -0.008798 | -0.038036 | -0.052847 | 0.013707 | -0.0884 | -0.054257 | -17.1678 | -0.23157 | 106.1427 | -15.9558 | 1.212 | -0.21458 | -0.12797 | 106.3163 | -1.0187 | 106.3624 | 106.3325 | 0.016221 | -0.95217 | -1.0543 | 107.1049 | 107.1218 | 107.2085 | 60.1693 | -124.5042 | 106.3177 | 106.3843 | 106.2821 | 106.3617 | -1.0201
464.9219 | 123.7747 | -122.699 | 0.90179 | 0.049183 | -0.0094477 | 0.0050278 | 0.12507 | -0.0089134 | 0.11477 | 0.064579 | -0.0059269 | -0.0084727 | 0.108 | 0.050884 | 0.0555 | -0.1592 | -47.2406 | -122.2485 | 0.78009 | 0.73757 | 0.8837 | -123.5017 | -0.012689 | -0.013377 | -0.038036 | -0.052847 | 0.013707 | -0.0884 | -0.054257 | -0.80273 | -0.1217 | 122.5398 | 0.45047 | 1.2532 | -0.16423 | -0.018094 | 122.6447 | -0.95464 | 122.6863 | 122.6609 | 0.016221 | -0.88809 | -0.99019 | 123.4791 | 123.4365 | 123.5827 | 75.4584 | -124.4035 | 122.6461 | 122.7127 | 122.6106 | 122.6856 | -0.95605
465.9062 | 124.324 | -109.1034 | 0.82855 | 0.049183 | -0.0083797 | 0.0018228 | 0.12401 | -0.0067764 | 0.11584 | 0.07984 | -0.0059269 | -0.0084727 | 0.10693 | 0.049815 | 0.053363 | -0.09052 | -47.9595 | -122.2348 | 0.77094 | 0.72383 | 0.86996 | -123.5154 | -0.00811 | -0.013377 | -0.033458 | -0.052847 | 0.018285 | -0.083821 | -0.054257 | -14.412 | -0.057617 | 109.0129 | -13.1314 | 1.2807 | -0.10472 | 0.041412 | 109.0491 | -0.8814 | 109.0953 | 109.0699 | 0.020799 | -0.81027 | -0.91237 | 109.8743 | 109.8272 | 109.9734 | 61.1439 | -124.344 | 109.0505 | 109.1217 | 109.0196 | 109.09 | -0.88281
466.9062 | 123.9532 | -114.1022 | 0.68207 | 0.079707 | -0.0094477 | 0.0018228 | 0.12507 | -0.0089134 | 0.11584 | 0.049318 | -0.0059269 | -0.0095417 | 0.10693 | 0.049815 | 0.053363 | -0.09052 | -48.3074 | -122.2897 | 0.68852 | 0.62767 | 0.78755 | -123.5841 | -0.00811 | -0.008798 | -0.038036 | -0.048268 | 0.004549 | -0.083821 | -0.049678 | -9.482 | 0.006456 | 114.0117 | -8.1875 | 1.2944 | -0.054396 | 0.10548 | 114.0525 | -0.73034 | 114.0941 | 114.0641 | 0.011642 | -0.67752 | -0.76589 | 114.7907 | 114.7298 | 114.8897 | 65.7947 | -124.2662 | 114.0539 | 114.1067 | 114.0184 | 114.0934 | -0.73175
467.9844 | 124.3698 | -123.2437 | 0.70953 | 0.049183 | -0.010516 | 0.0028908 | 0.12401 | -0.0067764 | 0.11477 | 0.07984 | -0.0059269 | -0.0095417 | 0.108 | 0.048747 | 0.0555 | -0.10426 | -49.0583 | -122.3538 | 0.5878 | 0.54983 | 0.70056 | -123.6711 | -0.003531 | -0.017956 | -0.038036 | -0.062004 | 0.013707 | -0.0884 | -0.0451 | -0.42741 | -0.12174 | 123.1395 | 0.88991 | 1.3173 | -0.1597 | -0.008979 | 123.1986 | -0.77154 | 123.2402 | 123.2057 | 0.007064 | -0.69583 | -0.79793 | 123.8315 | 123.7935 | 123.9443 | 74.1854 | -124.3807 | 123.1817 | 123.2574 | 123.1553 | 123.2258 | -0.75463
468.9219 | 123.4726 | -122.6395 | 0.79651 | 0.064445 | -0.0083797 | 0.0028908 | 0.12507 | -0.0099814 | 0.1137 | 0.049318 | -0.0048589 | -0.0063367 | 0.108 | 0.050884 | 0.054432 | -0.11341 | -49.6032 | -122.2714 | 0.65648 | 0.6002 | 0.76466 | -123.5979 | -0.00811 | -0.013377 | -0.033458 | -0.057425 | 0.013707 | -0.079243 | -0.049678 | -0.9584 | -0.14003 | 122.5261 | 0.36807 | 1.3265 | -0.19631 | -0.031853 | 122.5898 | -0.85393 | 122.6314 | 122.606 | 0.01622 | -0.7828 | -0.87575 | 123.2959 | 123.2397 | 123.4041 | 73.0363 | -124.3944 | 122.582 | 122.6532 | 122.5602 | 122.6261 | -0.84619
469.9219 | 123.8663 | -115.6311 | 0.84686 | 0.049183 | -0.0094477 | 0.0028908 | 0.12507 | -0.0078444 | 0.11584 | 0.07984 | -0.0059269 | -0.0074047 | 0.10693 | 0.050884 | 0.056568 | -0.1363 | -50.3907 | -122.2393 | 0.66105 | 0.62309 | 0.77839 | -123.607 | 0.001048 | -0.017956 | -0.038036 | -0.048268 | 0.013707 | -0.092979 | -0.054257 | -7.9759 | -0.18581 | 115.4948 | -6.6082 | 1.3677 | -0.22377 | -0.068471 | 115.5768 | -0.89513 | 115.6322 | 115.5931 | 0.016221 | -0.83316 | -0.93984 | 116.2922 | 116.2542 | 116.4095 | 65.2404 | -124.4539 | 115.5828 | 115.6448 | 115.5381 | 115.6131 | -0.90112
470.9844 | 123.5275 | -120.282 | 0.70038 | 0.049183 | -0.0083797 | 0.0028908 | 0.12614 | -0.0089134 | 0.11477 | 0.095101 | -0.0048589 | -0.0074047 | 0.10693 | 0.049815 | 0.054432 | -0.13173 | -51.137 | -122.2805 | 0.59238 | 0.53609 | 0.68682 | -123.694 | -0.00811 | -0.008798 | -0.033458 | -0.052847 | 0.013707 | -0.083821 | -0.049678 | -3.412 | -0.108 | 120.1503 | -1.9986 | 1.4135 | -0.16428 | -0.013558 | 120.2323 | -0.75322 | 120.2739 | 120.2485 | 0.01622 | -0.68667 | -0.7842 | 120.8744 | 120.8181 | 120.9688 | 69.145 | -124.3944 | 120.2291 | 120.2957 | 120.1982 | 120.2732 | -0.75006
471.9219 | 124.4431 | -123.3627 | 0.77362 | 0.049183 | -0.0094477 | 0.0028908 | 0.12614 | -0.0099814 | 0.11477 | 0.064579 | -0.0059269 | -0.0074047 | 0.108 | 0.049815 | 0.054432 | -0.16377 | -51.5857 | -122.2073 | 0.60153 | 0.56357 | 0.71429 | -123.6665 | -0.003531 | -0.027113 | -0.028879 | -0.052847 | 0.013707 | -0.092979 | -0.054257 | -0.30381 | -0.17209 | 123.199 | 1.1554 | 1.4593 | -0.21005 | -0.05933 | 123.3085 | -0.82647 | 123.3592 | 123.3339 | 0.025378 | -0.75991 | -0.8666 | 123.9643 | 123.9263 | 124.077 | 71.777 | -124.4402 | 123.3099 | 123.3764 | 123.2698 | 123.3356 | -0.82788
472.9844 | 124.3607 | -123.349 | 0.75989 | 0.049183 | -0.0094477 | 0.0028908 | 0.12614 | -0.0089134 | 0.1137 | 0.07984 | -0.0059269 | -0.0084727 | 0.10907 | 0.049815 | 0.054432 | -0.36064 | -52.6022 | -122.1981 | 0.5878 | 0.53609 | 0.70056 | -123.7123 | -0.003531 | -0.017956 | -0.033458 | -0.052847 | 0.018285 | -0.097557 | -0.049678 | -0.36334 | -0.17209 | 122.9884 | 1.1509 | 1.5142 | -0.22379 | -0.059333 | 123.2993 | -0.81273 | 123.3455 | 123.3155 | 0.01622 | -0.7416 | -0.85745 | 123.9368 | 123.8851 | 124.0496 | 70.7468 | -124.4722 | 123.2962 | 123.3673 | 123.2514 | 123.331 | -0.80957
473.9062 | 123.5413 | -123.2803 | 0.8194 | 0.033921 | -0.010516 | 0.0039598 | 0.12401 | -0.0099814 | 0.1137 | 0.064579 | -0.0059269 | -0.0074047 | 0.10907 | 0.050884 | 0.0555 | -0.37438 | -53.3576 | -122.1752 | 0.58322 | 0.52236 | 0.69598 | -123.7261 | -0.00811 | -0.017956 | -0.028879 | -0.052847 | 0.013707 | -0.092979 | -0.049678 | -0.44574 | -0.23618 | 122.906 | 1.1051 | 1.5508 | -0.29704 | -0.12342 | 123.2307 | -0.87224 | 123.2722 | 123.2515 | 0.020799 | -0.80569 | -0.91238 | 123.8636 | 123.8027 | 123.9763 | 69.9227 | -124.5455 | 123.2275 | 123.294 | 123.1874 | 123.2624 | -0.86908
474.9062 | 123.5733 | -122.7631 | 0.68665 | 0.049183 | -0.010516 | 0.0039598 | 0.12507 | -0.0089134 | 0.1137 | 0.064579 | -0.0048589 | -0.0074047 | 0.10907 | 0.050884 | 0.053363 | -0.31944 | -54.4428 | -122.1112 | 0.60611 | 0.55899 | 0.70513 | -123.6986 | -0.017267 | -0.013377 | -0.033458 | -0.052847 | 0.009128 | -0.0884 | -0.054257 | -0.93554 | -0.080533 | 122.4436 | 0.65191 | 1.5874 | -0.12766 | 0.018488 | 122.7088 | -0.73949 | 122.7458 | 122.7296 | 0.020799 | -0.67752 | -0.77505 | 123.3692 | 123.3221 | 123.4682 | 68.3203 | -124.3852 | 122.7102 | 122.7722 | 122.6747 | 122.7497 | -0.7409
475.9062 | 123.5092 | -122.8134 | 0.71869 | 0.079707 | -0.010516 | 0.0039598 | 0.12507 | -0.0099814 | 0.11477 | 0.064579 | -0.0059269 | -0.0084727 | 0.10907 | 0.053021 | 0.053363 | -0.34233 | -55.5599 | -122.1157 | 0.57406 | 0.51778 | 0.67308 | -123.7307 | -0.003531 | -0.022535 | -0.028879 | -0.057425 | 0.013707 | -0.083821 | -0.0451 | -0.91723 | -0.14463 | 122.4711 | 0.69769 | 1.6149 | -0.20091 | -0.045605 | 122.7683 | -0.77611 | 122.8099 | 122.7845 | 0.016221 | -0.70498 | -0.80251 | 123.3875 | 123.3312 | 123.4865 | 67.2535 | -124.4493 | 122.756 | 122.8271 | 122.7296 | 122.7909 | -0.76379
477 | 124.4019 | -123.5504 | 0.68665 | 0.018659 | -0.011585 | 0.0028908 | 0.12401 | -0.0089134 | 0.1137 | 0.064579 | -0.0059269 | -0.0084727 | 0.10693 | 0.050884 | 0.052295 | -0.3286 | -56.4757 | -122.0791 | 0.55117 | 0.50862 | 0.66851 | -123.7535 | -0.012689 | -0.013377 | -0.038036 | -0.057425 | 0.018285 | -0.092979 | -0.054257 | -0.20313 | -0.13547 | 123.2218 | 1.4713 | 1.6744 | -0.17803 | -0.018141 | 123.4962 | -0.74407 | 123.5377 | 123.5124 | 0.016221 | -0.66836 | -0.77963 | 124.1016 | 124.059 | 124.2189 | 67.0748 | -124.4402 | 123.493 | 123.5687 | 123.4574 | 123.537 | -0.7409
478.2344 | 124.3927 | -123.5641 | 0.65918 | 0.033921 | -0.010516 | 0.0018228 | 0.12401 | -0.0089134 | 0.11264 | 0.049318 | -0.0048589 | -0.0084727 | 0.10907 | 0.053021 | 0.053363 | -0.28739 | -57.4967 | -122.0379 | 0.53744 | 0.49488 | 0.65019 | -123.7627 | -0.00811 | -0.017956 | -0.033458 | -0.062004 | 0.004549 | -0.092979 | -0.0451 | -0.19856 | -0.12174 | 123.2768 | 1.5262 | 1.7248 | -0.1643 | -0.008989 | 123.519 | -0.72118 | 123.556 | 123.5307 | 0.011642 | -0.65463 | -0.75216 | 124.1016 | 124.059 | 124.2143 | 66.0675 | -124.4219 | 123.5021 | 123.5687 | 123.4712 | 123.5462 | -0.70428
478.9219 | 123.4634 | -122.818 | 0.66834 | 0.049183 | -0.011585 | 0.0039598 | 0.12507 | -0.0089134 | 0.1137 | 0.064579 | -0.0059269 | -0.0074047 | 0.10693 | 0.050884 | 0.054432 | -0.25534 | -58.1972 | -122.0059 | 0.55117 | 0.51778 | 0.66393 | -123.7398 | -0.00811 | -0.017956 | -0.038036 | -0.062004 | 0.009128 | -0.0884 | -0.049678 | -0.92182 | -0.11716 | 122.5627 | 0.81214 | 1.734 | -0.15056 | -0.004408 | 122.7683 | -0.73034 | 122.8099 | 122.78 | 0.011642 | -0.65921 | -0.75674 | 123.3692 | 123.3358 | 123.4819 | 64.6208 | -124.4081 | 122.756 | 122.8271 | 122.7296 | 122.8 | -0.71801
479.9062 | 123.8892 | -123.0835 | 0.737 | 0.064445 | -0.0094477 | 0.0028908 | 0.12401 | -0.0089134 | 0.11264 | 0.064579 | -0.0069959 | -0.0084727 | 0.108 | 0.051952 | 0.054432 | -0.25534 | -59.1221 | -121.9463 | 0.57864 | 0.52694 | 0.68224 | -123.7261 | -0.00811 | -0.013377 | -0.033458 | -0.062004 | 0.013707 | -0.083821 | -0.049678 | -0.64258 | -0.15836 | 122.8282 | 1.1372 | 1.7797 | -0.21006 | -0.054759 | 123.0338 | -0.799 | 123.0754 | 123.05 | 0.01622 | -0.72329 | -0.82082 | 123.6621 | 123.6104 | 123.7657 | 63.9614 | -124.4631 | 123.0215 | 123.0972 | 122.9997 | 123.0701 | -0.78668
480.9062 | 123.5413 | -122.8912 | 0.69122 | 0.049183 | -0.010516 | 0.0028908 | 0.12401 | -0.0089134 | 0.1137 | 0.07984 | -0.0048589 | -0.0074047 | 0.108 | 0.051952 | 0.0555 | -0.30113 | -60.0515 | -121.9189 | 0.56491 | 0.50404 | 0.67308 | -123.7398 | -0.00811 | 0.000359 | -0.033458 | -0.057425 | -2.9e-05 | -0.083821 | -0.049678 | -0.84857 | -0.12632 | 122.5901 | 0.97237 | 1.8209 | -0.18718 | -0.018139 | 122.8416 | -0.74865 | 122.8831 | 122.8578 | 0.01622 | -0.69125 | -0.77504 | 123.4561 | 123.3953 | 123.5643 | 62.8397 | -124.431 | 122.8338 | 122.8912 | 122.8074 | 122.8916 | -0.7409
481.9844 | 124.2828 | -123.2529 | 0.70038 | 0.033921 | -0.0094477 | 0.0039598 | 0.12294 | -0.0067764 | 0.11264 | 0.064579 | -0.0037909 | -0.0084727 | 0.108 | 0.051952 | 0.054432 | -0.37896 | -60.8253 | -121.8731 | 0.56949 | 0.50862 | 0.67766 | -123.7398 | -0.00811 | 0.000359 | -0.038036 | -0.057425 | 0.009128 | -0.097557 | -0.049678 | -0.48694 | -0.13089 | 122.8739 | 1.3798 | 1.8667 | -0.19176 | -0.022716 | 123.2032 | -0.7578 | 123.2448 | 123.2148 | 0.011642 | -0.69125 | -0.79793 | 123.8224 | 123.7615 | 123.9305 | 62.4275 | -124.4402 | 123.1954 | 123.262 | 123.1553 | 123.2532 | -0.75006
482.9219 | 123.6649 | -122.9965 | 0.70038 | 0.049183 | -0.010516 | 0.0050278 | 0.12401 | -0.0089134 | 0.1137 | 0.064579 | -0.0048589 | -0.0074047 | 0.10693 | 0.050884 | 0.053363 | -0.41559 | -61.4938 | -121.8548 | 0.55117 | 0.49488 | 0.66393 | -123.749 | -0.00811 | 0.014095 | -0.028879 | -0.057425 | 0.018285 | -0.079243 | -0.049678 | -0.75245 | -0.14921 | 122.5809 | 1.1418 | 1.8942 | -0.20549 | -0.036451 | 122.9468 | -0.7578 | 122.9884 | 122.9676 | 0.020799 | -0.68209 | -0.77962 | 123.5477 | 123.4914 | 123.6604 | 61.5027 | -124.4493 | 122.9391 | 123.0148 | 122.9173 | 123.0106 | -0.75006
483.9062 | 124.1135 | -123.3627 | 0.6958 | 0.049183 | -0.011585 | 0.0018228 | 0.12294 | -0.0089134 | 0.1137 | 0.049318 | -0.0048589 | -0.0084727 | 0.10693 | 0.051952 | 0.052295 | -0.41101 | -62.2355 | -121.8227 | 0.54659 | 0.4903 | 0.65019 | -123.7535 | -0.00811 | 0.004938 | -0.028879 | -0.052847 | 0.004549 | -0.10214 | -0.0451 | -0.39081 | -0.14921 | 122.9517 | 1.54 | 1.9308 | -0.2055 | -0.04561 | 123.3176 | -0.74865 | 123.3546 | 123.3339 | 0.016221 | -0.69125 | -0.79794 | 123.9093 | 123.853 | 124.0129 | 61.1272 | -124.4493 | 123.3099 | 123.3673 | 123.2606 | 123.3677 | -0.7409
484.9062 | 123.9212 | -123.0881 | 0.70953 | 0.064445 | -0.0094477 | 0.0028908 | 0.12401 | -0.0089134 | 0.11264 | 0.064579 | -0.0048589 | -0.0084727 | 0.108 | 0.051952 | 0.052295 | -0.47053 | -63.1284 | -121.7632 | 0.55117 | 0.50404 | 0.66393 | -123.7535 | -0.00811 | 0.023253 | -0.038036 | -0.062004 | 0.013707 | -0.0884 | -0.049678 | -0.66547 | -0.15836 | 122.6175 | 1.3249 | 1.9903 | -0.20549 | -0.045607 | 123.0384 | -0.77154 | 123.08 | 123.05 | 0.011642 | -0.69583 | -0.79793 | 123.6392 | 123.5921 | 123.752 | 59.9597 | -124.4631 | 123.0261 | 123.1018 | 122.9997 | 123.1113 | -0.75921
485.9062 | 123.9029 | -123.1155 | 0.69122 | 0.064445 | -0.012653 | 0.0028908 | 0.12507 | -0.0089134 | 0.11264 | 0.049318 | -0.0048589 | -0.0074047 | 0.108 | 0.049815 | 0.052295 | -0.43848 | -64.5019 | -121.7312 | 0.5237 | 0.46741 | 0.6273 | -123.7764 | -0.003531 | 0.018674 | -0.033458 | -0.052847 | -2.9e-05 | -0.092979 | -0.0451 | -0.6609 | -0.16752 | 122.6771 | 1.3844 | 2.0453 | -0.22381 | -0.063925 | 123.0704 | -0.74407 | 123.112 | 123.0821 | 0.011642 | -0.69125 | -0.7842 | 123.6392 | 123.5829 | 123.7428 | 58.6136 | -124.4677 | 123.0627 | 123.1155 | 123.0226 | 123.1342 | -0.73632
486.9219 | 123.6511 | -122.8592 | 0.6546 | 0.064445 | -0.010516 | 0.0028908 | 0.12401 | -0.0089134 | 0.1137 | 0.07984 | -0.0059269 | -0.0084727 | 0.10693 | 0.051952 | 0.051227 | -0.45679 | -65.4543 | -121.6854 | 0.5237 | 0.46283 | 0.6273 | -123.781 | -0.012689 | 0.023253 | -0.038036 | -0.057425 | 0.009128 | -0.097557 | -0.049678 | -0.92183 | -0.1309 | 122.4024 | 1.1738 | 2.0956 | -0.19177 | -0.027304 | 122.8095 | -0.71203 | 122.8465 | 122.8212 | 0.011642 | -0.64547 | -0.75216 | 123.3829 | 123.322 | 123.4865 | 57.4049 | -124.4356 | 122.8018 | 122.8683 | 122.7616 | 122.8824 | -0.70428
487.9219 | 123.674 | -122.8683 | 0.66376 | 0.049183 | -0.011585 | 0.0028908 | 0.12507 | -0.0078444 | 0.11584 | 0.049318 | -0.0069959 | -0.0074047 | 0.108 | 0.050884 | 0.053363 | -0.42932 | -65.6329 | -121.6213 | 0.5237 | 0.47657 | 0.63188 | -123.7719 | -0.012689 | 0.018674 | -0.033458 | -0.057425 | 0.009128 | -0.0884 | -0.0451 | -0.90351 | -0.14006 | 122.439 | 1.2471 | 2.1506 | -0.18719 | -0.031881 | 122.8232 | -0.72118 | 122.8557 | 122.8349 | 0.011642 | -0.65463 | -0.75216 | 123.392 | 123.3449 | 123.5002 | 57.2355 | -124.4356 | 122.8109 | 122.8775 | 122.7799 | 122.887 | -0.70886
488.9062 | 123.8068 | -122.8729 | 0.59967 | 0.064445 | -0.011585 | 0.0028908 | 0.12614 | -0.0099814 | 0.1137 | 0.07984 | -0.0059269 | -0.0095417 | 0.10693 | 0.051952 | 0.053363 | -0.40185 | -65.7977 | -121.603 | 0.49623 | 0.43536 | 0.58151 | -123.8177 | -0.012689 | 0.014095 | -0.028879 | -0.04369 | 0.004549 | -0.097557 | -0.049678 | -0.94473 | -0.10344 | 122.4711 | 1.27 | 2.2147 | -0.16431 | -0.018158 | 122.8232 | -0.64336 | 122.8602 | 122.844 | 0.020799 | -0.59512 | -0.69723 | 123.3692 | 123.3083 | 123.4544 | 57.0752 | -124.4173 | 122.8292 | 122.8775 | 122.7754 | 122.887 | -0.64935
489.9062 | 123.8159 | -122.8455 | 0.59967 | 0.033921 | -0.010516 | 0.0039598 | 0.12401 | -0.0078444 | 0.11477 | 0.049318 | -0.0059269 | -0.0084727 | 0.108 | 0.053021 | 0.051227 | -0.36522 | -66.0175 | -121.5801 | 0.47334 | 0.41704 | 0.56778 | -123.8268 | 0.001048 | 0.009516 | -0.033458 | -0.062004 | 0.009128 | -0.097557 | -0.049678 | -0.98135 | -0.12633 | 122.4802 | 1.2654 | 2.2467 | -0.18263 | -0.031894 | 122.7958 | -0.66167 | 122.8465 | 122.812 | 0.01622 | -0.59054 | -0.69723 | 123.3188 | 123.2625 | 123.4132 | 56.828 | -124.4265 | 122.7835 | 122.8546 | 122.7479 | 122.855 | -0.64935
490.9844 | 123.8754 | -122.8821 | 0.60883 | 0.064445 | -0.012653 | 0.0050278 | 0.12294 | -0.0078444 | 0.11584 | 0.07984 | -0.0059269 | -0.0074047 | 0.108 | 0.053021 | 0.052295 | -0.25076 | -66.3334 | -121.4931 | 0.47792 | 0.43536 | 0.59067 | -123.8085 | -0.00811 | 0.018674 | -0.038036 | -0.052847 | 0.022864 | -0.092979 | -0.058836 | -0.92641 | -0.13091 | 122.6313 | 1.389 | 2.3154 | -0.17347 | -0.018157 | 122.8232 | -0.66167 | 122.874 | 122.844 | 0.0208 | -0.58596 | -0.70181 | 123.36 | 123.3174 | 123.4727 | 56.5487 | -124.4173 | 122.8292 | 122.9049 | 122.7891 | 122.9008 | -0.66766
491.9219 | 123.7106 | -122.9553 | 0.61798 | 0.033921 | -0.0094477 | 0.0039598 | 0.12507 | -0.0078444 | 0.11157 | 0.049318 | -0.0059269 | -0.0052687 | 0.10693 | 0.051952 | 0.053363 | -0.22329 | -66.4524 | -121.4107 | 0.50997 | 0.45825 | 0.61814 | -123.7856 | -0.00811 | 0.014095 | -0.028879 | -0.062004 | 0.013707 | -0.097557 | -0.0451 | -0.83028 | -0.10801 | 122.732 | 1.5446 | 2.3749 | -0.15973 | 0.00016 | 122.9102 | -0.67998 | 122.9472 | 122.9264 | 0.016221 | -0.60427 | -0.71554 | 123.4653 | 123.4136 | 123.5735 | 56.5029 | -124.4036 | 122.8933 | 122.969 | 122.8578 | 122.9694 | -0.66308
492.9219 | 123.7564 | -122.8226 | 0.65918 | 0.079707 | -0.011585 | 0.0039598 | 0.12401 | -0.0078444 | 0.11264 | 0.064579 | -0.0037909 | -0.0084727 | 0.10693 | 0.051952 | 0.053363 | -0.19582 | -66.5761 | -121.3695 | 0.50539 | 0.45367 | 0.6044 | -123.7993 | -0.003531 | 0.014095 | -0.033458 | -0.048268 | 0.018285 | -0.092979 | -0.049678 | -0.97676 | -0.15379 | 122.6267 | 1.4531 | 2.4299 | -0.20551 | -0.054775 | 122.7729 | -0.70745 | 122.819 | 122.7891 | 0.01622 | -0.64089 | -0.75216 | 123.328 | 123.2762 | 123.427 | 56.2465 | -124.4585 | 122.7743 | 122.8409 | 122.7296 | 122.8367 | -0.70886
493.9062 | 124.4064 | -123.6282 | 0.60883 | 0.079707 | -0.010516 | 0.0028908 | 0.12614 | -0.0089134 | 0.11477 | 0.049318 | -0.0059269 | -0.0084727 | 0.10907 | 0.053021 | 0.0555 | -0.14546 | -67.0293 | -121.3557 | 0.46418 | 0.41704 | 0.57235 | -123.8314 | -0.00811 | 0.014095 | -0.042615 | -0.052847 | 0.009128 | -0.092979 | -0.0451 | -0.20315 | -0.14464 | 123.4828 | 2.2725 | 2.4757 | -0.19178 | -0.036471 | 123.5831 | -0.66167 | 123.6201 | 123.5856 | 0.002485 | -0.5997 | -0.70181 | 124.0924 | 124.0453 | 124.2006 | 56.5989 | -124.4402 | 123.5754 | 123.6374 | 123.5353 | 123.6423 | -0.65393
495.0156 | 123.9944 | -123.2437 | 0.61798 | 0.064445 | -0.010516 | 0.0028908 | 0.12507 | -0.0089134 | 0.11477 | 0.049318 | -0.0069959 | -0.0095417 | 0.10693 | 0.050884 | 0.054432 | -0.16835 | -67.2216 | -121.2642 | 0.4825 | 0.4262 | 0.58151 | -123.8039 | -0.003531 | 0.014095 | -0.033458 | -0.057425 | 0.009128 | -0.0884 | -0.049678 | -0.5602 | -0.13549 | 123.0754 | 1.9795 | 2.5397 | -0.19178 | -0.036469 | 123.194 | -0.67541 | 123.2402 | 123.2103 | 0.01622 | -0.60885 | -0.70638 | 123.7262 | 123.6699 | 123.8252 | 56.0221 | -124.4219 | 123.1863 | 123.2528 | 123.1553 | 123.2578 | -0.66766
495.9219 | 124.054 | -123.4406 | 0.5127 | 0.064445 | -0.011585 | 0.0028908 | 0.12507 | -0.0078444 | 0.11477 | 0.049318 | -0.0059269 | -0.0074047 | 0.10693 | 0.050884 | 0.053363 | -0.18667 | -67.5925 | -121.3328 | 0.35888 | 0.31173 | 0.46247 | -123.9092 | -0.00811 | 0.018674 | -0.038036 | -0.052847 | 0.009128 | -0.092979 | -0.0451 | -0.46868 | -0.15382 | 123.2539 | 2.1077 | 2.5764 | -0.20097 | -0.050227 | 123.3955 | -0.56554 | 123.4324 | 123.4025 | 0.007064 | -0.50357 | -0.60567 | 123.7994 | 123.7523 | 123.903 | 55.8481 | -124.4219 | 123.3877 | 123.4497 | 123.3476 | 123.4592 | -0.5578
496.9062 | 124.4202 | -123.7427 | 0.48523 | 0.064445 | -0.0094477 | 0.0028908 | 0.12507 | -0.0089134 | 0.1137 | 0.064579 | -0.0059269 | -0.0084727 | 0.11014 | 0.053021 | 0.053363 | -0.47968 | -67.8169 | -121.2459 | 0.3543 | 0.32088 | 0.45789 | -123.9047 | -0.00811 | 0.009516 | -0.028879 | -0.052847 | 0.004549 | -0.092979 | -0.054257 | -0.16197 | -0.13093 | 123.263 | 2.4968 | 2.6588 | -0.16435 | -0.027339 | 123.6884 | -0.53808 | 123.7346 | 123.7138 | 0.025378 | -0.48068 | -0.57821 | 124.097 | 124.0636 | 124.2006 | 55.9258 | -124.3899 | 123.6898 | 123.7472 | 123.6497 | 123.7522 | -0.53949
497.9062 | 124.4339 | -123.7473 | 0.48065 | 0.064445 | -0.010516 | 0.00075378 | 0.12507 | -0.0057084 | 0.11477 | 0.064579 | -0.0069959 | -0.0074047 | 0.108 | 0.050884 | 0.053363 | -0.46595 | -67.6978 | -121.1818 | 0.3543 | 0.32088 | 0.45331 | -123.9001 | -0.003531 | 0.018674 | -0.033458 | -0.057425 | 0.004549 | -0.092979 | -0.049678 | -0.15282 | -0.12635 | 123.2813 | 2.5655 | 2.7183 | -0.15977 | -0.027341 | 123.6976 | -0.53808 | 123.7437 | 123.7138 | 0.01622 | -0.4761 | -0.57363 | 124.1016 | 124.0681 | 124.2006 | 56.0494 | -124.3807 | 123.6898 | 123.7518 | 123.6543 | 123.7659 | -0.53033
498.9219 | 123.6237 | -123.1293 | 0.5722 | 0.079707 | -0.010516 | 0.0039598 | 0.12401 | -0.0099814 | 0.11477 | 0.049318 | -0.0069959 | -0.0074047 | 0.10693 | 0.051952 | 0.052295 | -0.45679 | -67.5467 | -121.0124 | 0.46418 | 0.41246 | 0.56778 | -123.7948 | -0.003531 | 0.009516 | -0.033458 | -0.052847 | -2.9e-05 | -0.092979 | -0.049678 | -0.66548 | -0.10802 | 122.6725 | 2.1169 | 2.7824 | -0.15974 | -0.004429 | 123.0796 | -0.62505 | 123.1257 | 123.0958 | 0.01622 | -0.57223 | -0.66518 | 123.5935 | 123.5417 | 123.697 | 55.5826 | -124.367 | 123.0764 | 123.1292 | 123.0363 | 123.1388 | -0.62188
499.9219 | 124.3103 | -123.4726 | 0.59509 | 0.079707 | -0.010516 | 0.0028908 | 0.12507 | -0.0089134 | 0.1137 | 0.11036 | -0.0080639 | -0.0084727 | 0.108 | 0.053021 | 0.054432 | -0.47053 | -67.8306 | -120.9849 | 0.45045 | 0.41246 | 0.54488 | -123.8039 | -0.00811 | 0.009516 | -0.038036 | -0.057425 | 0.009128 | -0.0884 | -0.0451 | -0.33132 | -0.14465 | 123.0021 | 2.4877 | 2.819 | -0.18263 | -0.05021 | 123.4275 | -0.65252 | 123.4645 | 123.4346 | 0.007064 | -0.58596 | -0.68349 | 123.923 | 123.8851 | 124.0175 | 55.642 | -124.399 | 123.4152 | 123.4817 | 123.3842 | 123.4821 | -0.64019
500.9062 | 124.4293 | -123.674 | 0.51727 | 0.064445 | -0.011585 | 0.0050278 | 0.12401 | -0.0099814 | 0.11477 | 0.064579 | -0.0080639 | -0.0074047 | 0.108 | 0.054089 | 0.053363 | -0.19124 | -68.0504 | -121.0169 | 0.38177 | 0.3392 | 0.48994 | -123.8909 | -0.003531 | 0.009516 | -0.038036 | -0.048268 | 0.022864 | -0.083821 | -0.058836 | -0.2169 | -0.1355 | 123.4828 | 2.6571 | 2.874 | -0.17807 | -0.027333 | 123.6152 | -0.56554 | 123.6705 | 123.636 | 0.0208 | -0.49441 | -0.60109 | 124.0558 | 124.0132 | 124.164 | 55.6236 | -124.4082 | 123.6257 | 123.6969 | 123.5902 | 123.6835 | -0.57611
501.9062 | 124.4385 | -123.761 | 0.45319 | 0.064445 | -0.010516 | 0.0028908 | 0.12614 | -0.0099814 | 0.11477 | 0.064579 | -0.0059269 | -0.0084727 | 0.10693 | 0.053021 | 0.053363 | -0.17751 | -68.1648 | -120.9162 | 0.44129 | 0.38499 | 0.52657 | -123.8497 | -0.003531 | 0.009516 | -0.038036 | -0.057425 | 0.009128 | -0.092979 | -0.054257 | -0.088717 | -0.011895 | 123.5835 | 2.8448 | 2.9335 | -0.068197 | 0.073383 | 123.7067 | -0.51061 | 123.7575 | 123.7229 | 0.016221 | -0.44406 | -0.54617 | 124.2023 | 124.146 | 124.2876 | 55.5962 | -124.3029 | 123.7036 | 123.7701 | 123.668 | 123.7705 | -0.50744
502.9219 | 124.0128 | -123.0835 | 0.59967 | 0.049183 | -0.011585 | 0.0018228 | 0.12401 | -0.0089134 | 0.11477 | 0.064579 | -0.0059269 | -0.0095417 | 0.108 | 0.054089 | 0.053363 | -0.16377 | -68.3754 | -120.8338 | 0.46418 | 0.41704 | 0.57235 | -123.7993 | 0.001048 | 0.018674 | -0.038036 | -0.052847 | 0.004549 | -0.0884 | -0.049678 | -0.71584 | -0.13549 | 122.9197 | 2.2497 | 2.9655 | -0.18263 | -0.027315 | 123.0338 | -0.65252 | 123.0845 | 123.0455 | 0.011642 | -0.59512 | -0.68807 | 123.5477 | 123.5005 | 123.6559 | 54.7081 | -124.399 | 123.0306 | 123.088 | 122.9951 | 123.1022 | -0.64935
503.9219 | 123.5596 | -123.1064 | 0.48065 | 0.064445 | -0.010516 | 0.0039598 | 0.12721 | -0.0089134 | 0.11584 | 0.064579 | -0.0059269 | -0.0095417 | 0.108 | 0.054089 | 0.052295 | -0.15462 | -68.7372 | -120.8933 | 0.3543 | 0.31631 | 0.46247 | -123.9001 | 0.001048 | 0.014095 | -0.042615 | -0.057425 | 0.004549 | -0.092979 | -0.049678 | -0.79369 | -0.12635 | 122.9518 | 2.2131 | 3.0067 | -0.16435 | -0.018184 | 123.0567 | -0.53808 | 123.1074 | 123.0638 | 0.007063 | -0.4761 | -0.57363 | 123.4607 | 123.4227 | 123.5689 | 54.3692 | -124.3807 | 123.049 | 123.1109 | 123.0134 | 123.1205 | -0.53033
504.9062 | 124.3927 | -123.7015 | 0.48981 | 0.064445 | -0.011585 | 0.0039598 | 0.12507 | -0.0099814 | 0.11584 | 0.064579 | -0.0048589 | -0.0084727 | 0.10693 | 0.054089 | 0.054432 | -0.17293 | -69.163 | -120.8292 | 0.38635 | 0.33004 | 0.48536 | -123.8772 | -0.012689 | 0.014095 | -0.033458 | -0.057425 | 0.013707 | -0.0884 | -0.054257 | -0.1757 | -0.10346 | 123.5285 | 2.8722 | 3.0479 | -0.15976 | -0.004446 | 123.6472 | -0.54723 | 123.6888 | 123.668 | 0.020799 | -0.4761 | -0.57821 | 124.0878 | 124.0315 | 124.1868 | 54.5385 | -124.367 | 123.6441 | 123.7152 | 123.6131 | 123.7156 | -0.54406
505.9062 | 124.3973 | -123.7015 | 0.51727 | 0.049183 | -0.013722 | 0.0028908 | 0.12401 | -0.0089134 | 0.11584 | 0.064579 | -0.0069959 | -0.0084727 | 0.10693 | 0.055157 | 0.052295 | -0.17293 | -69.6208 | -120.7835 | 0.37719 | 0.3392 | 0.48536 | -123.8634 | -0.00811 | 0.004938 | -0.033458 | -0.052847 | 0.013707 | -0.0884 | -0.049678 | -0.16196 | -0.14008 | 123.5285 | 2.918 | 3.08 | -0.17807 | -0.031912 | 123.6518 | -0.57012 | 123.6934 | 123.668 | 0.01622 | -0.50357 | -0.60567 | 124.0787 | 124.0407 | 124.1868 | 54.0807 | -124.3807 | 123.6486 | 123.7152 | 123.6131 | 123.7064 | -0.56695
506.9219 | 124.4019 | -123.7244 | 0.52185 | 0.049183 | -0.011585 | 0.0028908 | 0.12401 | -0.0089134 | 0.11477 | 0.064579 | -0.0059269 | -0.0084727 | 0.108 | 0.055157 | 0.052295 | -0.1592 | -69.7811 | -120.7468 | 0.36346 | 0.32546 | 0.47163 | -123.8863 | -0.003531 | 0.004938 | -0.033458 | -0.057425 | 0.009128 | -0.083821 | -0.0451 | -0.16197 | -0.15839 | 123.5652 | 2.9775 | 3.1395 | -0.19639 | -0.050226 | 123.6793 | -0.57928 | 123.7208 | 123.6909 | 0.011642 | -0.51272 | -0.60567 | 124.0878 | 124.0498 | 124.196 | 53.9433 | -124.4082 | 123.6669 | 123.7335 | 123.6405 | 123.7293 | -0.56695
507.9062 | 124.3103 | -123.6328 | 0.49896 | 0.064445 | -0.0094477 | 0.0050278 | 0.12507 | -0.0089134 | 0.11691 | 0.064579 | -0.0059269 | -0.0095417 | 0.108 | 0.054089 | 0.053363 | -0.15004 | -70.3488 | -120.701 | 0.36346 | 0.33004 | 0.46705 | -123.9001 | -0.00811 | 0.014095 | -0.038036 | -0.052847 | 0.009128 | -0.092979 | -0.0451 | -0.26726 | -0.1355 | 123.4828 | 2.9318 | 3.199 | -0.16892 | -0.031915 | 123.5877 | -0.55181 | 123.6247 | 123.5948 | 0.007064 | -0.48983 | -0.59194 | 123.9963 | 123.9629 | 124.0999 | 53.284 | -124.399 | 123.58 | 123.6419 | 123.5398 | 123.6469 | -0.54406
508.9844 | 123.9716 | -123.3124 | 0.52185 | 0.049183 | -0.012653 | 0.0039598 | 0.12507 | -0.0078444 | 0.11798 | 0.064579 | -0.0059269 | -0.0074047 | 0.10693 | 0.054089 | 0.050158 | -0.17293 | -70.4953 | -120.6186 | 0.38635 | 0.34836 | 0.48536 | -123.8863 | 0.001048 | 0.009516 | -0.033458 | -0.052847 | 0.009128 | -0.092979 | -0.0451 | -0.57396 | -0.1355 | 123.1394 | 2.6937 | 3.2677 | -0.17349 | -0.03649 | 123.2673 | -0.5747 | 123.3134 | 123.2789 | 0.011642 | -0.51272 | -0.61483 | 123.6987 | 123.6607 | 123.7977 | 52.817 | -124.4082 | 123.2595 | 123.3215 | 123.2194 | 123.3219 | -0.56695
509.9062 | 124.411 | -123.7518 | 0.45776 | 0.049183 | -0.011585 | 0.0018228 | 0.12614 | -0.0057084 | 0.11584 | 0.064579 | -0.0059269 | -0.0074047 | 0.10907 | 0.053021 | 0.052295 | -0.19582 | -70.1474 | -120.5316 | 0.38177 | 0.34378 | 0.4762 | -123.8909 | -0.00811 | 0.009516 | -0.028879 | -0.057425 | 0.013707 | -0.0884 | -0.049678 | -0.13908 | -0.075992 | 123.556 | 3.2202 | 3.3593 | -0.11399 | 0.01844 | 123.7022 | -0.51519 | 123.7437 | 123.723 | 0.020799 | -0.44406 | -0.54616 | 124.1336 | 124.0956 | 124.228 | 53.6045 | -124.3487 | 123.6944 | 123.7655 | 123.6634 | 123.7613 | -0.50744
510.9219 | 124.379 | -123.7152 | 0.51727 | 0.064445 | -0.010516 | 0.0018228 | 0.12614 | -0.0078444 | 0.11584 | 0.07984 | -0.0059269 | -0.0084727 | 0.10907 | 0.054089 | 0.052295 | -0.2004 | -70.2206 | -120.4675 | 0.38177 | 0.3392 | 0.48536 | -123.8909 | -0.00811 | 0.014095 | -0.033458 | -0.04369 | 0.013707 | -0.092979 | -0.049678 | -0.1757 | -0.1355 | 123.5148 | 3.2477 | 3.4234 | -0.17807 | -0.031912 | 123.6655 | -0.56096 | 123.7071 | 123.6818 | 0.01622 | -0.50357 | -0.61025 | 124.097 | 124.0544 | 124.2006 | 53.4946 | -124.4082 | 123.6715 | 123.7289 | 123.6222 | 123.7293 | -0.56695
511.9219 | 124.411 | -123.7061 | 0.5127 | 0.049183 | -0.011585 | 0.0039598 | 0.12401 | -0.0078444 | 0.11691 | 0.064579 | -0.0069959 | -0.0063367 | 0.108 | 0.054089 | 0.051227 | -0.16835 | -70.3305 | -120.4172 | 0.37261 | 0.33004 | 0.48078 | -123.8955 | -0.003531 | 0.004938 | -0.033458 | -0.062004 | 0.004549 | -0.092979 | -0.054257 | -0.18944 | -0.14008 | 123.5377 | 3.2889 | 3.4783 | -0.18265 | -0.031912 | 123.6518 | -0.5747 | 123.7025 | 123.6726 | 0.020799 | -0.50815 | -0.60567 | 124.0787 | 124.0361 | 124.1868 | 53.3755 | -124.4082 | 123.6441 | 123.7106 | 123.6131 | 123.711 | -0.56695
512.9219 | 124.4476 | -123.7152 | 0.45776 | 0.049183 | -0.011585 | 0.0028908 | 0.12401 | -0.0067764 | 0.11477 | 0.049318 | -0.0059269 | -0.0084727 | 0.10586 | 0.054089 | 0.052295 | -0.19124 | -70.2664 | -120.3165 | 0.36804 | 0.32088 | 0.46247 | -123.8863 | -0.012689 | 0.014095 | -0.038036 | -0.052847 | 0.013707 | -0.083821 | -0.049678 | -0.17113 | -0.089728 | 123.524 | 3.3987 | 3.5699 | -0.13688 | 0.004704 | 123.6655 | -0.51061 | 123.7025 | 123.6772 | 0.011642 | -0.44406 | -0.54158 | 124.0832 | 124.0361 | 124.1777 | 53.4488 | -124.3441 | 123.6624 | 123.7289 | 123.6314 | 123.7293 | -0.50744
513.9062 | 124.3011 | -123.5092 | 0.51727 | 0.079707 | -0.011585 | 0.023191 | 0.10798 | -0.0089134 | 0.11691 | 0.07984 | -0.0069959 | -0.0084727 | 0.10693 | 0.055157 | 0.053363 | -0.17293 | -70.0695 | -120.2478 | 0.37719 | 0.32088 | 0.47163 | -123.8909 | -0.003531 | 0.018674 | -0.033458 | -0.062004 | 0.009128 | -0.092979 | -0.049678 | -0.3817 | -0.14008 | 123.3363 | 3.2614 | 3.6431 | -0.19639 | -0.045648 | 123.4595 | -0.57928 | 123.5057 | 123.4758 | 0.01622 | -0.50814 | -0.61025 | 123.8864 | 123.8301 | 123.9808 | 53.4397 | -124.4082 | 123.4472 | 123.5183 | 123.4162 | 123.5279 | -0.56695
514.9062 | 124.3698 | -123.7564 | 0.49439 | 0.079707 | -0.013722 | 0.062721 | 0.07379 | -0.0067764 | 0.11798 | 0.07984 | -0.0069959 | -0.0084727 | 0.10693 | 0.055157 | 0.051227 | -0.1592 | -70.3259 | -120.1654 | 0.35888 | 0.32088 | 0.46705 | -123.9047 | -0.00811 | 0.018674 | -0.033458 | -0.057425 | 0.013707 | -0.092979 | -0.0451 | -0.14824 | -0.13551 | 123.5972 | 3.591 | 3.7393 | -0.1735 | -0.027338 | 123.7113 | -0.55181 | 123.7483 | 123.723 | 0.011642 | -0.48068 | -0.58736 | 124.1153 | 124.0773 | 124.2235 | 53.4305 | -124.399 | 123.699 | 123.7701 | 123.6634 | 123.7751 | -0.53948
515.9062 | 124.4293 | -123.7106 | 0.52185 | 0.064445 | -0.010516 | 0.071268 | 0.065243 | -0.0089134 | 0.11477 | 0.07984 | -0.0048589 | -0.0074047 | 0.10586 | 0.055157 | 0.051227 | -0.19582 | -70.6647 | -120.0784 | 0.37261 | 0.32546 | 0.4762 | -123.8818 | -0.003531 | 0.009516 | -0.028879 | -0.052847 | 0.018285 | -0.092979 | -0.054257 | -0.17112 | -0.14924 | 123.5148 | 3.6322 | 3.8034 | -0.19639 | -0.045647 | 123.6564 | -0.5747 | 123.7071 | 123.6818 | 0.025378 | -0.50357 | -0.61483 | 124.0832 | 124.0361 | 124.1868 | 53.0459 | -124.4036 | 123.6578 | 123.7289 | 123.6177 | 123.7201 | -0.57611
516.9062 | 124.379 | -123.6237 | 0.58594 | 0.064445 | -0.010516 | 0.073405 | 0.063106 | -0.0078444 | 0.11477 | 0.049318 | -0.0048589 | -0.0095417 | 0.10693 | 0.054089 | 0.051227 | -0.20498 | -71.4339 | -119.8678 | 0.38635 | 0.34378 | 0.48994 | -123.8772 | -0.003531 | 0.018674 | -0.038036 | -0.052847 | 0.009128 | -0.0884 | -0.035942 | -0.25352 | -0.19959 | 123.4187 | 3.7559 | 4.0094 | -0.24216 | -0.095997 | 123.5877 | -0.63878 | 123.6201 | 123.5856 | -0.002094 | -0.57681 | -0.67434 | 124.01 | 123.9674 | 124.1136 | 52.1897 | -124.4631 | 123.5708 | 123.6328 | 123.5353 | 123.6423 | -0.62188
517.9062 | 124.3881 | -123.7198 | 0.53101 | 0.079707 | -0.0083797 | 0.11293 | 0.10264 | 0.070143 | 0.11477 | 0.07984 | -0.0059269 | -0.0074047 | 0.10586 | 0.054089 | 0.051227 | 0.11093 | -43.4404 | -14.929 | 0.39551 | 0.28883 | 0.45331 | -123.3643 | -0.003531 | 0.014095 | -0.038036 | -0.048268 | 0.004549 | -0.097557 | 0.055634 | 0.35545 | -0.1355 | 123.8307 | 108.7908 | 108.4353 | -0.24217 | -0.077695 | 123.7754 | -0.57927 | 123.7163 | 123.6818 | -0.09367 | -0.52646 | -0.62856 | 124.1153 | 124.0086 | 124.1731 | 80.2794 | -123.8953 | 123.6715 | 123.7243 | 123.6222 | 123.7339 | -0.47537
518.9062 | 124.411 | -123.7518 | 0.45319 | 0.094969 | -0.013722 | 0.11828 | 0.10157 | 0.084031 | 0.11798 | 0.064579 | -0.0069959 | -0.0084727 | 0.10586 | 0.055157 | 0.051227 | -0.47053 | -43.4129 | 0.34412 | 0.30394 | 0.22015 | 0.40753 | -123.9733 | -0.00811 | 0.018674 | -0.028879 | -0.048268 | -2.9e-05 | -0.092979 | -0.0451 | -0.2215 | -0.14925 | 123.2813 | 124.0959 | 124.3175 | -0.23304 | -0.045661 | 123.7067 | -0.50145 | 123.7437 | 123.723 | 0.016221 | -0.45321 | -0.54617 | 124.0558 | 123.972 | 124.1594 | 80.3389 | -124.4265 | 123.7036 | 123.7518 | 123.6589 | 123.7705 | -0.49829
519.9219 | 124.3698 | -123.8297 | 0.40741 | 0.049183 | -0.01479 | 0.11935 | 0.10157 | 0.081894 | 0.11798 | 0.07984 | -0.0069959 | -0.0095417 | 0.10693 | 0.056226 | 0.052295 | -0.46137 | -44.3149 | 0.32581 | 0.28563 | 0.20641 | 0.38921 | -123.9962 | -0.00811 | 0.014095 | -0.038036 | -0.052847 | 0.013707 | -0.092979 | -0.058836 | -0.16658 | -0.12178 | 123.3683 | 124.1555 | 124.322 | -0.201 | -0.018199 | 123.7708 | -0.46026 | 123.8215 | 123.7916 | 0.0208 | -0.3937 | -0.50039 | 124.1153 | 124.0361 | 124.2189 | 79.5148 | -124.4036 | 123.7768 | 123.8434 | 123.7367 | 123.8437 | -0.46625
520.9062 | 123.7473 | -61.8027 | 61.409 | 0.049183 | -0.01479 | 0.14606 | 0.14431 | -0.020664 | 0.034648 | 0.064579 | -0.0069959 | -0.0084727 | 0.10586 | 0.055157 | 0.052295 | 0.001048 | 0.23949 | 0.000747 | 0.024657 | -0.054588 | 0.041237 | -0.26453 | -0.012689 | 0.014095 | -0.033458 | -0.048268 | 0.013707 | -0.0884 | -0.0451 | 61.5381 | -61.3843 | 61.8037 | 61.8034 | 0.26528 | -61.4636 | -61.3678 | 61.7576 | -61.4573 | 61.79 | 61.7692 | 0.011642 | -61.3953 | -61.4974 | 61.8273 | 61.7481 | 61.8439 | 62.0422 | -61.6735 | 61.7544 | 61.8164 | 61.7143 | 61.8168 | -61.4541
521.9062 | 123.9807 | -61.4868 | 61.5692 | 0.033921 | -0.012653 | 0.14499 | 0.14537 | -0.020664 | 0.032512 | 0.064579 | -0.0059269 | -0.0074047 | 0.10693 | 0.056226 | 0.050158 | -0.008109 | 0.34938 | -0.003831 | -0.025705 | -0.054588 | 0.03208 | -0.035584 | -0.012689 | 0.014095 | -0.033458 | -0.048268 | 0.009128 | -0.0884 | -0.040521 | 61.4512 | -61.5949 | 61.4787 | 61.483 | 0.031753 | -61.6238 | -61.5371 | 61.4463 | -61.6175 | 61.4741 | 61.4534 | 0.007063 | -61.5601 | -61.6576 | 61.4611 | 61.4322 | 61.5189 | 61.8362 | -61.6048 | 61.4385 | 61.4959 | 61.3984 | 61.5009 | -61.6097
522.9062 | 124.1959 | -61.441 | 61.528 | 0.064445 | -0.013722 | 0.14499 | 0.14644 | -0.019596 | 0.031443 | 0.064579 | -0.0069959 | -0.0095417 | 0.10586 | 0.054089 | 0.051227 | -0.003531 | 0.37227 | 0.009904 | -0.01197 | -0.054588 | 0.036658 | -0.031005 | -0.00811 | 0.018674 | -0.033458 | -0.052847 | 0.004549 | -0.0884 | -0.040521 | 61.41 | -61.54 | 61.4375 | 61.4509 | 0.040909 | -61.5826 | -61.4914 | 61.4005 | -61.5809 | 61.4329 | 61.4076 | 0.007063 | -61.5235 | -61.6164 | 61.4291 | 61.3865 | 61.4777 | 61.8133 | -61.559 | 61.3882 | 61.4456 | 61.3526 | 61.4597 | -61.5685
523.9219 | 123.7793 | -61.9125 | 61.4685 | 0.064445 | -0.011585 | 0.14392 | 0.14537 | -0.020664 | 0.03358 | 0.034057 | -0.0069959 | -0.0095417 | 0.10693 | 0.055157 | 0.051227 | -0.008109 | 0.38601 | 0.005325 | -0.007391 | -0.054588 | 0.036658 | -0.031005 | -0.012689 | 0.009516 | -0.033458 | -0.052847 | 0.018285 | -0.097557 | -0.035942 | 61.8815 | -61.4759 | 61.9044 | 61.9179 | 0.03633 | -61.5231 | -61.4318 | 61.8766 | -61.5214 | 61.8998 | 61.8791 | 0.002484 | -61.4502 | -61.5661 | 61.9051 | 61.8579 | 61.9492 | 62.2985 | -61.4995 | 61.8597 | 61.9308 | 61.815 | 61.9221 | -61.5044
524.9062 | 123.7701 | -61.5372 | 61.853 | 0.049183 | -0.013722 | 0.14392 | 0.14431 | -0.020664 | 0.03358 | 0.064579 | -0.0069959 | -0.0074047 | 0.10693 | 0.056226 | 0.052295 | -0.012688 | 0.39059 | 0.005325 | -0.002813 | -0.054588 | 0.03208 | -0.017268 | -0.00811 | 0.009516 | -0.033458 | -0.052847 | 0.009128 | -0.092979 | -0.040521 | 61.5199 | -61.8558 | 61.5245 | 61.5425 | 0.022593 | -61.9076 | -61.8209 | 61.4966 | -61.9059 | 61.5291 | 61.5037 | 0.007063 | -61.8439 | -61.946 | 61.5344 | 61.4826 | 61.5693 | 61.9278 | -61.8703 | 61.4843 | 61.5463 | 61.4442 | 61.5467 | -61.8935
525.9062 | 121.3531 | -61.7935 | 61.6699 | 0.033921 | -0.013722 | 0.14606 | 0.14324 | -0.020664 | 0.032512 | 0.064579 | -0.0069959 | -0.0084727 | 0.108 | 0.055157 | 0.051227 | -0.003531 | 0.39059 | 0.009904 | -0.016548 | -0.050009 | 0.03208 | -0.021847 | -0.003531 | 0.014095 | -0.028879 | -0.052847 | 0.009128 | -0.097557 | -0.035942 | 61.7717 | -61.6865 | 61.79 | 61.8034 | 0.031751 | -61.7199 | -61.6378 | 61.7576 | -61.7228 | 61.79 | 61.7646 | 0.007063 | -61.6608 | -61.7675 | 61.777 | 61.7435 | 61.8256 | 62.1841 | -61.6918 | 61.7407 | 61.8026 | 61.696 | 61.8076 | -61.7059
526.9062 | 123.6877 | -61.6241 | 61.5646 | 0.049183 | -0.012653 | 0.14392 | 0.14537 | -0.019596 | 0.032512 | 0.064579 | -0.0080639 | -0.0074047 | 0.108 | 0.056226 | 0.052295 | -0.008109 | 0.37685 | 0.009904 | -0.021127 | -0.054588 | 0.041237 | -0.021847 | -0.00811 | 0.027831 | -0.033458 | -0.052847 | 0.009128 | -0.092979 | -0.035942 | 61.6023 | -61.5858 | 61.616 | 61.6341 | 0.031751 | -61.6192 | -61.5234 | 61.5882 | -61.6175 | 61.616 | 61.5907 | 0.002484 | -61.5555 | -61.6576 | 61.603 | 61.5696 | 61.6654 | 62.001 | -61.5865 | 61.5713 | 61.6333 | 61.5312 | 61.652 | -61.6006
527.9062 | 124.2599 | -61.4639 | 61.7477 | 0.049183 | -0.013722 | 0.14499 | 0.14431 | -0.020664 | 0.03358 | 0.064579 | -0.0059269 | -0.0074047 | 0.10693 | 0.056226 | 0.051227 | -0.008109 | 0.37685 | 0.005325 | -0.016548 | -0.054588 | 0.03208 | -0.021847 | -0.00811 | 0.018674 | -0.028879 | -0.052847 | 0.018285 | -0.0884 | -0.035942 | 61.4421 | -61.7643 | 61.4558 | 61.4693 | 0.027172 | -61.8023 | -61.7157 | 61.428 | -61.8006 | 61.4558 | 61.435 | 0.007063 | -61.7295 | -61.8361 | 61.4474 | 61.4093 | 61.496 | 61.8408 | -61.7696 | 61.4111 | 61.4822 | 61.3755 | 61.4826 | -61.7837
528.9062 | 123.8205 | -61.9537 | 61.94 | 0.049183 | -0.013722 | 0.14392 | 0.14431 | -0.018528 | 0.03358 | 0.064579 | -0.0059269 | -0.0084727 | 0.108 | 0.056226 | 0.052295 | -0.008109 | 0.038035 | -0.008409 | -0.016548 | -0.054588 | 0.036658 | -0.012689 | -0.00811 | 0.023253 | -0.033458 | -0.057425 | 0.013707 | -0.097557 | -0.035942 | 61.941 | -61.9566 | 61.9456 | 61.9453 | 0.00428 | -61.9946 | -61.9033 | 61.9178 | -61.9974 | 61.9456 | 61.9203 | 0.002484 | -61.9263 | -62.0376 | 61.9372 | 61.8991 | 61.9904 | 61.9918 | -61.9527 | 61.8963 | 61.9674 | 61.8562 | 61.977 | -61.9759
529.9062 | 124.0768 | -61.3907 | 61.3449 | 0.049183 | -0.013722 | 0.14392 | 0.14431 | -0.020664 | 0.032512 | 0.064579 | -0.0080639 | -0.0074047 | 0.108 | 0.056226 | 0.051227 | -0.008109 | 0.047193 | -0.003831 | -0.01197 | -0.050009 | 0.004608 | -0.003531 | -0.003531 | 0.014095 | -0.033458 | -0.057425 | 0.018285 | -0.092979 | -0.035942 | 61.3872 | -61.3569 | 61.3826 | 61.3869 | -0.0003 | -61.3949 | -61.3403 | 61.3547 | -61.4023 | 61.3872 | 61.3572 | 0.002484 | -61.3266 | -61.4379 | 61.3787 | 61.3407 | 61.3953 | 61.4379 | -61.3484 | 61.3333 | 61.409 | 61.2977 | 61.4048 | -61.3809
530.9062 | 124.3607 | -61.3861 | 61.6562 | 0.049183 | -0.01479 | 0.14606 | 0.14431 | -0.020664 | 0.03358 | 0.07984 | -0.0069959 | -0.0084727 | 0.1048 | 0.056226 | 0.052295 | -0.012688 | 0.042614 | -0.003831 | -0.007391 | -0.059167 | 0.009187 | 0.001048 | -0.00811 | 0.018674 | -0.038036 | -0.052847 | 0.013707 | -0.0884 | -0.040521 | 61.3872 | -61.6636 | 61.3734 | 61.3823 | -0.004879 | -61.7154 | -61.647 | 61.3456 | -61.709 | 61.378 | 61.3481 | 0.002485 | -61.6425 | -61.7446 | 61.3787 | 61.3269 | 61.3953 | 61.4287 | -61.6551 | 61.3333 | 61.3998 | 61.2977 | 61.4048 | -61.6967
531.9062 | 124.5026 | -61.3586 | 61.8668 | 0.049183 | -0.013722 | 0.14392 | 0.14324 | -0.020664 | 0.034648 | 0.049318 | -0.0080639 | -0.0063367 | 0.10586 | 0.056226 | 0.051227 | -0.003531 | 0.042614 | -0.008409 | -0.007391 | -0.04543 | -0.013707 | -0.012689 | -0.00811 | 0.023253 | -0.028879 | -0.062004 | 0.004549 | -0.097557 | -0.040521 | 61.346 | -61.8742 | 61.3551 | 61.3502 | 0.00428 | -61.9122 | -61.8805 | 61.3181 | -61.9288 | 61.3505 | 61.3298 | 0.011642 | -61.8622 | -61.9643 | 61.3513 | 61.3132 | 61.3449 | 61.4013 | -61.8794 | 61.2966 | 61.3632 | 61.2611 | 61.3819 | -61.9073
532.9062 | 123.8663 | -61.5784 | 61.853 | 0.049183 | -0.012653 | 0.14499 | 0.14431 | -0.021732 | 0.037853 | 0.049318 | -0.0069959 | -0.0063367 | 0.1048 | 0.057294 | 0.053363 | -0.012688 | 0.042614 | -0.003831 | -0.01197 | -0.059167 | -0.004549 | -0.021847 | -0.00811 | 0.023253 | -0.038036 | -0.052847 | 0.018285 | -0.092979 | -0.040521 | 61.5565 | -61.865 | 61.5657 | 61.5745 | 0.018016 | -61.9122 | -61.8576 | 61.5378 | -61.9059 | 61.5703 | 61.5403 | 0.002485 | -61.8347 | -61.946 | 61.5664 | 61.5192 | 61.5738 | 61.621 | -61.8749 | 61.5255 | 61.5967 | 61.4854 | 61.6016 | -61.8935
533.9062 | 120.9137 | -61.734 | 62.0041 | 0.079707 | -0.012653 | 0.14285 | 0.14431 | -0.020664 | 0.038921 | 0.049318 | -0.0059269 | -0.0084727 | 0.108 | 0.056226 | 0.053363 | -0.008109 | 0.038035 | -0.003831 | -0.01197 | -0.050009 | 2.9e-05 | -0.003531 | -0.003531 | 0.023253 | -0.028879 | -0.052847 | 0.022864 | -0.0884 | -0.031363 | 61.7305 | -62.0161 | 61.7259 | 61.7302 | -0.0003 | -62.0541 | -62.0041 | 61.7026 | -62.0569 | 61.7305 | 61.7051 | 0.002484 | -61.9812 | -62.0925 | 61.722 | 61.684 | 61.734 | 61.772 | -62.0076 | 61.6812 | 61.7569 | 61.6456 | 61.7573 | -62.0355
534.9062 | 118.3594 | -61.821 | 61.8942 | 0.064445 | -0.015858 | 0.14392 | 0.14324 | -0.020664 | 0.035717 | 0.064579 | -0.0069959 | -0.0095417 | 0.10586 | 0.055157 | 0.052295 | -0.012688 | 0.047193 | 0.000747 | -0.025705 | -0.050009 | 2.9e-05 | -0.00811 | -0.012689 | 0.014095 | -0.0243 | -0.066582 | 0.018285 | -0.097557 | -0.040521 | 61.8129 | -61.9199 | 61.8083 | 61.8217 | 0.008857 | -61.9442 | -61.8942 | 61.7805 | -61.9608 | 61.8083 | 61.7967 | 0.016221 | -61.8759 | -61.9918 | 61.7953 | 61.771 | 61.821 | 61.8682 | -61.9023 | 61.7544 | 61.8393 | 61.7234 | 61.8351 | -61.9347
535.9062 | 123.8205 | -61.9949 | 62.1094 | 0.049183 | -0.013722 | 0.14285 | 0.14324 | -0.019596 | 0.038921 | 0.07984 | -0.0069959 | -0.0074047 | 0.10586 | 0.058362 | 0.051227 | -0.003531 | 0.047193 | -0.003831 | -0.007391 | -0.050009 | 0.004608 | -0.00811 | -0.003531 | 0.018674 | -0.028879 | -0.057425 | 0.009128 | -0.092979 | -0.035942 | 61.9868 | -62.1168 | 61.9914 | 61.9911 | 0.004279 | -62.1594 | -62.1048 | 61.959 | -62.1668 | 61.9914 | 61.9661 | 0.007063 | -62.1002 | -62.2024 | 61.9875 | 61.9449 | 61.9995 | 62.0421 | -62.1175 | 61.9375 | 62.0041 | 61.902 | 62.0136 | -62.1453
536.9062 | 123.8617 | -61.9995 | 62.059 | 0.049183 | -0.013722 | 0.14499 | 0.14324 | -0.018528 | 0.038921 | 0.064579 | -0.0059269 | -0.0063367 | 0.10373 | 0.056226 | 0.052295 | -0.012688 | 0.033457 | 0.000747 | -0.007391 | -0.050009 | -0.004549 | 0.001048 | -0.003531 | 0.014095 | -0.033458 | -0.057425 | 0.009128 | -0.0884 | -0.040521 | 62.0006 | -62.0664 | 61.9868 | 62.0003 | -0.000301 | -62.109 | -62.0636 | 61.959 | -62.1164 | 61.996 | 61.9661 | 0.007063 | -62.0499 | -62.1474 | 61.9921 | 61.9495 | 61.995 | 62.033 | -62.058 | 61.9421 | 62.0086 | 61.9111 | 62.0136 | -62.0995
537.9062 | 123.967 | -61.5097 | 62.0819 | 0.049183 | -0.01479 | 0.14178 | 0.14431 | -0.019596 | 0.036785 | 0.07984 | -0.0037909 | -0.0074047 | 0.10693 | 0.058362 | 0.051227 | -0.012688 | 0.042614 | -0.003831 | -0.01197 | -0.059167 | -0.004549 | -0.003531 | -0.00811 | 0.018674 | -0.0243 | -0.052847 | 0.018285 | -0.097557 | -0.040521 | 61.5062 | -62.0939 | 61.497 | 61.5059 | -0.0003 | -62.1411 | -62.0865 | 61.4692 | -62.1348 | 61.5016 | 61.4854 | 0.016221 | -62.0636 | -62.1795 | 61.4977 | 61.4505 | 61.5052 | 61.5523 | -62.0854 | 61.4569 | 61.528 | 61.4121 | 61.5284 | -62.1224
538.9062 | 120.8084 | -61.7386 | 62.0819 | 0.064445 | -0.01479 | 0.14392 | 0.14324 | -0.019596 | 0.037853 | 0.034057 | -0.0048589 | -0.0063367 | 0.10586 | 0.057294 | 0.051227 | -0.008109 | 0.051771 | -0.008409 | -0.01197 | -0.050009 | -0.004549 | -0.003531 | -0.012689 | 0.023253 | -0.038036 | -0.052847 | 0.027442 | -0.0884 | -0.040521 | 61.7351 | -62.0939 | 61.7305 | 61.7302 | -0.004878 | -62.1319 | -62.0865 | 61.6981 | -62.1348 | 61.7259 | 61.7005 | 0.002485 | -62.0545 | -62.1703 | 61.7266 | 61.6886 | 61.734 | 61.7904 | -62.0854 | 61.6857 | 61.766 | 61.6502 | 61.7618 | -62.1224
539.9062 | 109.8495 | -62.0544 | 61.9812 | 0.018659 | -0.01479 | 0.14392 | 0.14324 | -0.018528 | 0.036785 | 0.064579 | -0.0069959 | -0.0084727 | 0.10586 | 0.056226 | 0.051227 | -0.003531 | 0.047193 | -0.003831 | -0.021127 | -0.054588 | -0.004549 | -0.012689 | -0.00811 | 0.023253 | -0.028879 | -0.048268 | 0.009128 | -0.092979 | -0.040521 | 62.0418 | -62.0023 | 62.0509 | 62.0506 | 0.008858 | -62.0358 | -61.9857 | 62.0139 | -62.0295 | 62.0463 | 62.0256 | 0.011642 | -61.9721 | -62.0742 | 62.0333 | 61.9999 | 62.0499 | 62.1016 | -61.9939 | 62.0062 | 62.0636 | 61.9615 | 62.0777 | -62.0217
540.9062 | 119.6136 | -61.7935 | 61.8301 | 0.064445 | -0.01479 | 0.14285 | 0.14324 | -0.020664 | 0.037853 | 0.034057 | -0.0069959 | -0.0063367 | 0.10693 | 0.057294 | 0.050158 | -0.003531 | 0.010564 | -0.003831 | -0.016548 | -0.054588 | -0.004549 | -0.012689 | -0.003531 | 0.014095 | -0.033458 | -0.062004 | 0.022864 | -0.083821 | -0.031363 | 61.7808 | -61.8467 | 61.79 | 61.7897 | 0.008858 | -61.8847 | -61.8347 | 61.7622 | -61.8921 | 61.79 | 61.7601 | -0.002095 | -61.8073 | -61.914 | 61.777 | 61.7389 | 61.789 | 61.8041 | -61.8428 | 61.7315 | 61.8164 | 61.7097 | 61.8076 | -61.8615
541.9062 | 115.9515 | -61.702 | 61.9995 | 0.033921 | -0.013722 | 0.14178 | 0.14324 | -0.019596 | 0.037853 | 0.064579 | -0.0080639 | -0.0084727 | 0.10693 | 0.058362 | 0.051227 | 0.001048 | 0.019721 | -0.003831 | -0.016548 | -0.050009 | 2.9e-05 | -0.00811 | -0.00811 | 0.018674 | -0.028879 | -0.057425 | 0.009128 | -0.0884 | -0.040521 | 61.6939 | -62.0161 | 61.703 | 61.6981 | 0.004279 | -62.0495 | -61.9995 | 61.6614 | -62.0569 | 61.6939 | 61.6731 | 0.011642 | -61.9904 | -62.0879 | 61.6854 | 61.652 | 61.702 | 61.7217 | -62.0076 | 61.6445 | 61.7111 | 61.6136 | 61.7206 | -62.04
542.9062 | 123.7747 | -61.8484 | 61.9125 | 0.064445 | -0.015858 | 0.14392 | 0.14324 | -0.021732 | 0.037853 | 0.07984 | -0.0069959 | -0.0084727 | 0.10586 | 0.058362 | 0.050158 | -0.008109 | 0.0243 | 0.005325 | -0.007391 | -0.054588 | -0.004549 | -0.003531 | -0.00811 | 0.018674 | -0.028879 | -0.048268 | 0.004549 | -0.0884 | -0.035942 | 61.8449 | -61.9199 | 61.8403 | 61.8538 | 0.008856 | -61.9671 | -61.9171 | 61.8125 | -61.9608 | 61.8403 | 61.8196 | 0.007063 | -61.908 | -62.0009 | 61.8411 | 61.7939 | 61.8439 | 61.8727 | -61.9161 | 61.8002 | 61.853 | 61.76 | 61.8671 | -61.9485
543.9062 | 124.5071 | -61.6425 | 62.1094 | 0.018659 | -0.016927 | 0.14392 | 0.14537 | -0.020664 | 0.038921 | 0.049318 | -0.0059269 | -0.0084727 | 0.108 | 0.058362 | 0.052295 | -0.003531 | 0.0243 | 0.000747 | -0.01197 | -0.050009 | 0.004608 | 0.010206 | -0.012689 | 0.014095 | -0.028879 | -0.057425 | 0.018285 | -0.079243 | -0.035942 | 61.6527 | -62.1213 | 61.6389 | 61.6432 | -0.009459 | -62.1594 | -62.1048 | 61.6065 | -62.1668 | 61.6298 | 61.6136 | 0.007063 | -62.0911 | -62.1886 | 61.6305 | 61.5924 | 61.6471 | 61.6668 | -62.0992 | 61.585 | 61.6607 | 61.5632 | 61.6566 | -62.1453
544.9062 | 121.8246 | -61.7889 | 62.0316 | 0.049183 | -0.012653 | 0.14392 | 0.14324 | -0.021732 | 0.035717 | 0.07984 | -0.0069959 | -0.0063367 | 0.10586 | 0.057294 | 0.050158 | -0.003531 | 0.019721 | 0.000747 | -0.01197 | -0.059167 | -0.004549 | 0.001048 | -0.003531 | 0.018674 | -0.028879 | -0.052847 | 0.013707 | -0.083821 | -0.0451 | 61.79 | -62.0435 | 61.7854 | 61.7897 | -0.000301 | -62.0907 | -62.0361 | 61.7438 | -62.0844 | 61.7854 | 61.7601 | 0.016221 | -62.0178 | -62.1154 | 61.777 | 61.7298 | 61.7844 | 61.8087 | -62.0305 | 61.7361 | 61.8026 | 61.7051 | 61.8076 | -62.0767
545.9062 | 124.6445 | -61.6653 | 62.1048 | 0.049183 | -0.01479 | 0.14392 | 0.14217 | -0.020664 | 0.036785 | 0.064579 | -0.0059269 | -0.0074047 | 0.1048 | 0.056226 | 0.050158 | -0.003531 | 0.015142 | 0.000747 | -0.016548 | -0.054588 | -0.004549 | 0.001048 | -0.003531 | 0.018674 | -0.028879 | -0.057425 | 0.022864 | -0.092979 | -0.0451 | 61.6664 | -62.1213 | 61.6618 | 61.6661 | -0.000301 | -62.1594 | -62.1093 | 61.6202 | -62.1622 | 61.6618 | 61.6365 | 0.016221 | -62.0819 | -62.1978 | 61.6488 | 61.6108 | 61.6608 | 61.6805 | -62.1037 | 61.6079 | 61.6882 | 61.5724 | 61.684 | -62.1499
546.9062 | 123.6694 | -61.7523 | 62.0041 | 0.033921 | -0.016927 | 0.14499 | 0.14324 | -0.020664 | 0.035717 | 0.049318 | -0.0048589 | -0.0084727 | 0.1048 | 0.058362 | 0.051227 | -0.008109 | 0.019721 | -0.003831 | -0.01197 | -0.059167 | 2.9e-05 | -0.003531 | 0.001048 | 0.023253 | -0.033458 | -0.057425 | 0.018285 | -0.0884 | -0.040521 | 61.7488 | -62.0161 | 61.7442 | 61.7485 | -0.0003 | -62.0633 | -62.0041 | 61.7118 | -62.0615 | 61.7534 | 61.7189 | 0.007063 | -61.9858 | -62.0925 | 61.7403 | 61.6932 | 61.7523 | 61.772 | -62.0076 | 61.6949 | 61.7706 | 61.6639 | 61.7756 | -62.0446
547.9062 | 119.1193 | -61.8713 | 62.1094 | 0.033921 | -0.013722 | 0.14285 | 0.14217 | -0.020664 | 0.036785 | 0.049318 | -0.0091319 | -0.0063367 | 0.1048 | 0.059431 | 0.04909 | -0.008109 | 0.015142 | -0.003831 | -0.01197 | -0.054588 | 2.9e-05 | 0.001048 | -0.00811 | 0.023253 | -0.028879 | -0.052847 | 0.018285 | -0.092979 | -0.040521 | 61.8724 | -62.1213 | 61.8632 | 61.8675 | -0.004879 | -62.164 | -62.1093 | 61.8308 | -62.1622 | 61.8632 | 61.8425 | 0.011642 | -62.0911 | -62.2024 | 61.8594 | 61.8167 | 61.8714 | 61.8865 | -62.1083 | 61.8185 | 61.8896 | 61.7784 | 61.8946 | -62.1499
548.9062 | 119.6503 | -61.8622 | 62.1002 | 0.049183 | -0.01479 | 0.14392 | 0.14431 | -0.020664 | 0.036785 | 0.049318 | -0.0069959 | -0.0084727 | 0.10586 | 0.059431 | 0.051227 | -0.008109 | 0.0243 | -0.003831 | -0.002813 | -0.054588 | 0.004608 | 0.001048 | -0.00811 | 0.018674 | -0.033458 | -0.057425 | 0.018285 | -0.092979 | -0.040521 | 61.8632 | -62.103 | 61.8541 | 61.8584 | -0.004879 | -62.1548 | -62.0956 | 61.8217 | -62.1576 | 61.8541 | 61.8287 | 0.007063 | -62.0819 | -62.1932 | 61.8594 | 61.8076 | 61.8668 | 61.8865 | -62.0992 | 61.8048 | 61.8805 | 61.7692 | 61.8809 | -62.1407
549.9062 | 123.3673 | -61.7477 | 62.1368 | 0.049183 | -0.01479 | 0.14392 | 0.14324 | -0.020664 | 0.037853 | 0.07984 | -0.0048589 | -0.0095417 | 0.1048 | 0.058362 | 0.050158 | -0.008109 | 0.015142 | 0.000747 | -0.016548 | -0.059167 | 0.009187 | -0.003531 | -0.012689 | 0.023253 | -0.028879 | -0.052847 | 0.009128 | -0.0884 | -0.035942 | 61.7442 | -62.1534 | 61.7396 | 61.7485 | 0.004278 | -62.196 | -62.1277 | 61.7118 | -62.1897 | 61.7351 | 61.7189 | 0.007063 | -62.1277 | -62.2252 | 61.7312 | 61.6886 | 61.7569 | 61.7629 | -62.1404 | 61.6949 | 61.7569 | 61.6593 | 61.771 | -62.1728
550.9688 | 123.4955 | -61.5784 | 61.94 | 0.049183 | -0.015858 | 0.14499 | 0.14324 | -0.020664 | 0.035717 | 0.064579 | -0.0069959 | -0.0084727 | 0.10586 | 0.057294 | 0.051227 | -0.003531 | 0.0243 | -0.003831 | -0.021127 | -0.059167 | -0.004549 | -0.003531 | -0.012689 | 0.023253 | -0.028879 | -0.052847 | 0.018285 | -0.092979 | -0.035942 | 61.5748 | -61.9611 | 61.5748 | 61.5745 | -0.0003 | -61.9992 | -61.9446 | 61.5424 | -61.9928 | 61.5657 | 61.5495 | 0.007063 | -61.9217 | -62.033 | 61.5572 | 61.5192 | 61.5738 | 61.6027 | -61.9435 | 61.5255 | 61.5967 | 61.4854 | 61.6016 | -61.9759
551.9062 | 124.5071 | -61.6837 | 61.6562 | 0.064445 | -0.013722 | 0.14392 | 0.1411 | -0.020664 | 0.035717 | 0.07984 | -0.0048589 | -0.0063367 | 0.1048 | 0.057294 | 0.051227 | -0.003531 | 0.015142 | 0.000747 | -0.007391 | -0.04543 | -0.004549 | 0.001048 | -0.003531 | 0.027831 | -0.028879 | -0.052847 | 0.013707 | -0.092979 | -0.0451 | 61.6847 | -61.6636 | 61.6801 | 61.6844 | -0.000301 | -61.7016 | -61.6607 | 61.6386 | -61.709 | 61.6801 | 61.6548 | 0.016221 | -61.6425 | -61.7492 | 61.6763 | 61.6382 | 61.6791 | 61.6988 | -61.6551 | 61.6308 | 61.6974 | 61.5907 | 61.7115 | -61.7013
552.9062 | 123.6557 | -61.8622 | 61.7981 | 0.033921 | -0.013722 | 0.14392 | 0.14324 | -0.020664 | 0.035717 | 0.064579 | -0.0080639 | -0.0063367 | 0.10586 | 0.058362 | 0.050158 | -0.008109 | 0.028878 | 0.000747 | -0.007391 | -0.050009 | 2.9e-05 | -0.003531 | -0.003531 | 0.018674 | -0.028879 | -0.048268 | 0.009128 | -0.0884 | -0.035942 | 61.8587 | -61.8055 | 61.8541 | 61.8629 | 0.004278 | -61.8481 | -61.7981 | 61.8262 | -61.8464 | 61.8587 | 61.8333 | 0.007063 | -61.789 | -61.8865 | 61.8548 | 61.8122 | 61.8622 | 61.8911 | -61.8016 | 61.8139 | 61.8713 | 61.7738 | 61.8809 | -61.834
553.9062 | 120.1584 | -61.9217 | 62.0956 | 0.064445 | -0.01479 | 0.14392 | 0.14324 | -0.021732 | 0.036785 | 0.064579 | -0.0080639 | -0.0095417 | 0.1048 | 0.057294 | 0.050158 | -0.008109 | 0.015142 | -0.003831 | -0.007391 | -0.050009 | 2.9e-05 | 0.001048 | -0.003531 | 0.014095 | -0.033458 | -0.048268 | 0.013707 | -0.0884 | -0.0451 | 61.9227 | -62.103 | 61.9136 | 61.9179 | -0.004879 | -62.1457 | -62.0956 | 61.8766 | -62.1439 | 61.9182 | 61.8882 | 0.011642 | -62.0819 | -62.184 | 61.9143 | 61.8717 | 61.9217 | 61.9368 | -62.0946 | 61.8734 | 61.9354 | 61.8333 | 61.9358 | -62.1407
554.9062 | 124.1089 | -61.8347 | 61.9858 | 0.033921 | -0.015858 | 0.14285 | 0.14324 | -0.020664 | 0.034648 | 0.07984 | -0.0080639 | -0.0084727 | 0.10586 | 0.059431 | 0.050158 | 0.001048 | 0.015142 | -0.008409 | -0.016548 | -0.059167 | -0.004549 | -0.00811 | -0.003531 | 0.018674 | -0.0243 | -0.057425 | 0.013707 | -0.0884 | -0.040521 | 61.8266 | -62.0023 | 61.8358 | 61.8263 | -0.000299 | -62.0449 | -61.9903 | 61.7942 | -62.0432 | 61.8312 | 61.8104 | 0.016221 | -61.9721 | -62.0742 | 61.8182 | 61.7755 | 61.8302 | 61.8499 | -61.9939 | 61.7773 | 61.8484 | 61.7463 | 61.8534 | -62.0263
555.9219 | 123.9304 | -61.9263 | 62.114 | 0.079707 | -0.015858 | 0.14392 | 0.14217 | -0.022801 | 0.036785 | 0.064579 | -0.0069959 | -0.01061 | 0.1048 | 0.059431 | 0.053363 | -0.003531 | 0.0243 | -0.008409 | -0.007391 | -0.054588 | -0.004549 | 0.001048 | -0.003531 | 0.018674 | -0.038036 | -0.048268 | 0.013707 | -0.0884 | -0.0451 | 61.9273 | -62.1213 | 61.9227 | 61.9179 | -0.009457 | -62.1685 | -62.1185 | 61.8812 | -62.1622 | 61.9227 | 61.8882 | 0.007064 | -62.1002 | -62.2024 | 61.9189 | 61.8717 | 61.9217 | 61.9506 | -62.1129 | 61.878 | 61.94 | 61.8379 | 61.9449 | -62.1591
556.9219 | 123.8617 | -62.0407 | 62.1002 | 0.049183 | -0.01479 | 0.14285 | 0.14324 | -0.021732 | 0.036785 | 0.064579 | -0.0059269 | -0.0084727 | 0.10586 | 0.056226 | 0.051227 | -0.008109 | 0.0243 | 0.000747 | -0.007391 | -0.054588 | 2.9e-05 | 0.001048 | -0.003531 | 0.018674 | -0.028879 | -0.052847 | 0.013707 | -0.092979 | -0.040521 | 62.0418 | -62.1076 | 62.0326 | 62.0415 | -0.000301 | -62.1548 | -62.1002 | 62.0002 | -62.1531 | 62.0372 | 62.0118 | 0.011642 | -62.0865 | -62.1932 | 62.0333 | 61.9861 | 62.0407 | 62.065 | -62.0992 | 61.9879 | 62.0544 | 61.9477 | 62.0594 | -62.1407
557.9062 | 116.4139 | -61.8668 | 62.1735 | 0.018659 | -0.015858 | 0.14392 | 0.14324 | -0.020664 | 0.035717 | 0.064579 | -0.0059269 | -0.0095417 | 0.10586 | 0.059431 | 0.04909 | -0.008109 | 0.019721 | -0.008409 | -0.01197 | -0.054588 | 0.009187 | -0.012689 | -0.003531 | 0.023253 | -0.033458 | -0.052847 | 0.004549 | -0.0884 | -0.040521 | 61.8541 | -62.1854 | 61.8587 | 61.8584 | 0.00428 | -62.2281 | -62.1643 | 61.8262 | -62.2263 | 61.8632 | 61.8333 | 0.007063 | -62.1689 | -62.2619 | 61.8548 | 61.8122 | 61.8759 | 61.8865 | -62.1862 | 61.8139 | 61.8713 | 61.7784 | 61.89 | -62.214
558.9062 | 116.4139 | -61.8896 | 62.1368 | 0.064445 | -0.01479 | 0.14392 | 0.14324 | -0.020664 | 0.035717 | 0.064579 | -0.0080639 | -0.0084727 | 0.10586 | 0.059431 | 0.050158 | -0.008109 | 0.015142 | -0.003831 | -0.01197 | -0.054588 | -0.004549 | -0.003531 | 0.001048 | 0.018674 | -0.033458 | -0.052847 | 0.004549 | -0.0884 | -0.040521 | 61.8861 | -62.1488 | 61.8815 | 61.8858 | -0.0003 | -62.1914 | -62.1414 | 61.8491 | -62.1897 | 61.8907 | 61.8562 | 0.007063 | -62.1323 | -62.2252 | 61.8777 | 61.8351 | 61.8851 | 61.9048 | -62.1404 | 61.8368 | 61.8942 | 61.8012 | 61.9083 | -62.1774
559.9062 | 109.0256 | -61.7752 | 62.1231 | 0.033921 | -0.01479 | 0.14392 | 0.14217 | -0.020664 | 0.036785 | 0.064579 | -0.0059269 | -0.0063367 | 0.1048 | 0.058362 | 0.051227 | -0.008109 | 0.0243 | 0.005325 | -0.007391 | -0.054588 | 0.004608 | 0.001048 | -0.00811 | 0.014095 | -0.033458 | -0.052847 | 0.013707 | -0.092979 | -0.0451 | 61.7763 | -62.1305 | 61.7671 | 61.7805 | 0.004277 | -62.1777 | -62.1185 | 61.7301 | -62.176 | 61.7671 | 61.7417 | 0.011642 | -62.1094 | -62.2161 | 61.7678 | 61.7206 | 61.7798 | 61.7995 | -62.1221 | 61.7224 | 61.7889 | 61.6822 | 61.7893 | -62.1682
560.9062 | 114.3494 | -61.8393 | 61.8118 | 0.049183 | -0.015858 | 0.14392 | 0.14324 | -0.021732 | 0.035717 | 0.064579 | -0.0069959 | -0.0084727 | 0.10693 | 0.057294 | 0.04909 | -0.012688 | 0.033457 | -0.003831 | -0.002813 | -0.050009 | -0.009128 | -0.003531 | -0.003531 | 0.023253 | -0.028879 | -0.062004 | 0.013707 | -0.10214 | -0.035942 | 61.8358 | -61.8146 | 61.8266 | 61.8355 | -0.0003 | -61.8618 | -61.821 | 61.8034 | -61.8738 | 61.8358 | 61.8104 | 0.007063 | -61.7981 | -61.914 | 61.8365 | 61.7893 | 61.8302 | 61.8728 | -61.8154 | 61.7773 | 61.853 | 61.7372 | 61.8625 | -61.8478
561.9375 | 123.7106 | -61.9949 | 61.9034 | 0.018659 | -0.015858 | 0.14285 | 0.14217 | -0.020664 | 0.037853 | 0.049318 | -0.0069959 | -0.0095417 | 0.10693 | 0.059431 | 0.051227 | -0.012688 | 0.028878 | -0.008409 | -0.016548 | -0.054588 | -0.004549 | 0.001048 | -0.00811 | 0.018674 | -0.038036 | -0.057425 | 0.018285 | -0.092979 | -0.0451 | 61.996 | -61.9199 | 61.9822 | 61.9865 | -0.009457 | -61.958 | -61.9079 | 61.9498 | -61.9608 | 61.9868 | 61.9569 | 0.007064 | -61.8851 | -61.9964 | 61.9784 | 61.9403 | 61.9904 | 62.0238 | -61.9023 | 61.9375 | 62.0132 | 61.902 | 62.0136 | -61.9485
562.9062 | 104.8416 | -61.7477 | 62.0132 | 0.064445 | -0.017995 | 0.14285 | 0.14217 | -0.020664 | 0.035717 | 0.095101 | -0.0059269 | -0.0084727 | 0.10373 | 0.058362 | 0.04909 | -0.008109 | 0.028878 | 0.005325 | -0.002813 | -0.050009 | 2.9e-05 | -0.003531 | -0.003531 | 0.018674 | -0.033458 | -0.048268 | 0.009128 | -0.083821 | -0.040521 | 61.7442 | -62.0161 | 61.7396 | 61.7531 | 0.008856 | -62.0633 | -62.0132 | 61.7072 | -62.0615 | 61.7442 | 61.7143 | 0.007063 | -62.0041 | -62.0971 | 61.7449 | 61.6977 | 61.7478 | 61.7766 | -62.0168 | 61.6995 | 61.7569 | 61.6639 | 61.7664 | -62.0538
563.9062 | 111.2274 | -61.821 | 61.8668 | 0.079707 | -0.01479 | 0.14392 | 0.14217 | -0.020664 | 0.034648 | 0.07984 | -0.0059269 | -0.0063367 | 0.10586 | 0.058362 | 0.051227 | -0.003531 | 0.019721 | 0.000747 | -0.007391 | -0.059167 | -0.004549 | 0.001048 | -0.00811 | 0.023253 | -0.033458 | -0.052847 | 0.013707 | -0.0884 | -0.035942 | 61.822 | -61.8742 | 61.8175 | 61.8217 | -0.000301 | -61.9259 | -61.8713 | 61.785 | -61.9196 | 61.8129 | 61.7875 | 0.002484 | -61.8531 | -61.9552 | 61.8136 | 61.7618 | 61.8164 | 61.8407 | -61.8657 | 61.7681 | 61.8347 | 61.7326 | 61.8442 | -61.9027
565 | 118.2083 | -61.8073 | 62.0041 | 0.049183 | -0.016927 | 0.14392 | 0.14217 | -0.020664 | 0.036785 | 0.049318 | -0.0069959 | -0.0095417 | 0.1048 | 0.058362 | 0.050158 | -0.003531 | 0.015142 | 0.005325 | -0.016548 | -0.054588 | -0.004549 | -0.003531 | 0.001048 | 0.014095 | -0.033458 | -0.057425 | 0.018285 | -0.10214 | -0.040521 | 61.8037 | -62.0206 | 61.8037 | 61.8126 | 0.008856 | -62.0587 | -62.0086 | 61.7667 | -62.0615 | 61.8083 | 61.7738 | 0.007063 | -61.9858 | -62.1062 | 61.7907 | 61.7527 | 61.8027 | 61.8224 | -62.0076 | 61.7498 | 61.8255 | 61.7051 | 61.8213 | -62.0446
565.9062 | 122.4472 | -61.7889 | 61.7889 | 0.064445 | -0.015858 | 0.14392 | 0.14431 | -0.020664 | 0.036785 | 0.064579 | -0.0069959 | -0.0084727 | 0.10586 | 0.060499 | 0.050158 | -0.003531 | 0.019721 | -0.003831 | -0.007391 | -0.054588 | 0.004608 | -0.003531 | -0.00811 | 0.014095 | -0.033458 | -0.057425 | 0.018285 | -0.0884 | -0.040521 | 61.7854 | -61.7963 | 61.7854 | 61.7851 | -0.0003 | -61.8435 | -61.7843 | 61.7484 | -61.8464 | 61.7808 | 61.7555 | 0.007063 | -61.7707 | -61.8773 | 61.7815 | 61.7344 | 61.7935 | 61.8087 | -61.7925 | 61.7315 | 61.8072 | 61.7005 | 61.803 | -61.8295
566.9062 | 124.4202 | -61.8118 | 61.6333 | 0.064445 | -0.016927 | 0.14178 | 0.14431 | -0.020664 | 0.036785 | 0.064579 | -0.0069959 | -0.0084727 | 0.10373 | 0.060499 | 0.051227 | -0.012688 | 0.019721 | -0.003831 | -0.002813 | -0.054588 | 2.9e-05 | 0.001048 | -0.00811 | 0.023253 | -0.033458 | -0.052847 | 0.013707 | -0.0884 | -0.040521 | 61.8129 | -61.6361 | 61.7991 | 61.808 | -0.004879 | -61.6879 | -61.6333 | 61.7713 | -61.6861 | 61.8037 | 61.7784 | 0.007063 | -61.6196 | -61.7217 | 61.809 | 61.7572 | 61.8119 | 61.8316 | -61.6323 | 61.759 | 61.8255 | 61.7234 | 61.8351 | -61.6738
567.9062 | 124.2737 | -61.7798 | 61.4914 | 0.079707 | -0.015858 | 0.14178 | 0.14324 | -0.020664 | 0.034648 | 0.064579 | -0.0091319 | -0.0074047 | 0.1048 | 0.061567 | 0.050158 | -0.008109 | 0.019721 | 0.000747 | -0.016548 | -0.04543 | 0.004608 | 0.005627 | -0.003531 | 0.014095 | -0.033458 | -0.057425 | 0.013707 | -0.092979 | -0.0451 | 61.7854 | -61.5079 | 61.7717 | 61.7805 | -0.00488 | -61.5368 | -61.4868 | 61.7347 | -61.5488 | 61.7763 | 61.7463 | 0.011642 | -61.4777 | -61.5844 | 61.7632 | 61.7344 | 61.7844 | 61.7995 | -61.4858 | 61.7224 | 61.7935 | 61.6868 | 61.7939 | -61.5365
569.0938 | 123.8251 | -62.0819 | 61.7844 | 0.079707 | -0.01479 | 0.14071 | 0.14324 | -0.020664 | 0.034648 | 0.07984 | -0.0080639 | -0.0084727 | 0.1048 | 0.059431 | 0.050158 | -0.012688 | 0.015142 | -0.003831 | 0.001765 | -0.059167 | 0.004608 | 0.001048 | -0.003531 | 0.023253 | -0.038036 | -0.057425 | 0.018285 | -0.097557 | -0.040521 | 62.083 | -61.7826 | 62.0692 | 62.0781 | -0.004879 | -61.8435 | -61.7798 | 62.0414 | -61.8418 | 62.0784 | 62.0439 | 0.002485 | -61.7661 | -61.8819 | 62.0837 | 62.0227 | 62.0865 | 62.0971 | -61.7833 | 62.0245 | 62.1002 | 61.9844 | 62.1052 | -61.8249
569.9219 | 123.5367 | -61.7294 | 62.0224 | 0.064445 | -0.01479 | 0.14071 | 0.14324 | -0.021732 | 0.03358 | 0.064579 | -0.0069959 | -0.0084727 | 0.10586 | 0.061567 | 0.050158 | -0.008109 | 0.0243 | 0.000747 | -0.007391 | -0.054588 | 2.9e-05 | -0.00811 | 0.001048 | 0.023253 | -0.033458 | -0.052847 | 0.022864 | -0.092979 | -0.035942 | 61.7213 | -62.0298 | 61.7213 | 61.7302 | 0.008857 | -62.077 | -62.0224 | 61.6935 | -62.0752 | 61.7305 | 61.696 | 0.002484 | -61.9995 | -62.1154 | 61.722 | 61.6748 | 61.7295 | 61.7537 | -62.0305 | 61.6766 | 61.7523 | 61.6365 | 61.7527 | -62.0583
570.9219 | 123.999 | -62.0682 | 61.9263 | 0.049183 | -0.01479 | 0.14071 | 0.14324 | -0.020664 | 0.034648 | 0.07984 | -0.0080639 | -0.0095417 | 0.10693 | 0.060499 | 0.051227 | -0.003531 | 0.015142 | -0.003831 | -0.002813 | -0.050009 | -0.004549 | 0.001048 | -0.00811 | 0.023253 | -0.033458 | -0.057425 | 0.022864 | -0.0884 | -0.035942 | 62.0692 | -61.9291 | 62.0646 | 62.0643 | -0.004879 | -61.9763 | -61.9308 | 62.0322 | -61.9837 | 62.0601 | 62.0347 | 0.002484 | -61.9034 | -62.0147 | 62.0654 | 62.0182 | 62.0636 | 62.0833 | -61.9252 | 62.0108 | 62.091 | 61.9798 | 62.0914 | -61.9622
571.9844 | 123.7839 | -62.0911 | 62.1277 | 0.033921 | -0.015858 | 0.14071 | 0.14217 | -0.020664 | 0.034648 | 0.07984 | -0.0059269 | -0.0084727 | 0.10586 | 0.060499 | 0.050158 | 0.001048 | 0.019721 | 0.005325 | -0.01197 | -0.059167 | 0.004608 | -0.017268 | -0.00811 | 0.023253 | -0.033458 | -0.052847 | 0.022864 | -0.092979 | -0.035942 | 62.0738 | -62.1397 | 62.0921 | 62.0964 | 0.022593 | -62.1869 | -62.1231 | 62.0551 | -62.1805 | 62.083 | 62.0576 | 0.002484 | -62.1048 | -62.2207 | 62.0791 | 62.0319 | 62.0957 | 62.1108 | -62.145 | 62.0382 | 62.1139 | 61.9981 | 62.1143 | -62.1636
572.9062 | 123.9349 | -62.0819 | 62.0453 | 0.064445 | -0.015858 | 0.14071 | 0.14217 | -0.021732 | 0.034648 | 0.095101 | -0.0080639 | -0.0084727 | 0.1048 | 0.061567 | 0.04909 | -0.008109 | 0.028878 | 0.009904 | -0.007391 | -0.054588 | -0.009128 | 0.005627 | 0.001048 | 0.023253 | -0.038036 | -0.057425 | 0.013707 | -0.097557 | -0.040521 | 62.0875 | -62.0527 | 62.0738 | 62.0918 | 0.004277 | -62.0999 | -62.0544 | 62.0414 | -62.1027 | 62.083 | 62.0439 | 0.002485 | -62.0316 | -62.1428 | 62.0745 | 62.0273 | 62.0728 | 62.1108 | -62.0397 | 62.0245 | 62.0956 | 61.9844 | 62.1052 | -62.0858
573.9062 | 124.1409 | -62.0453 | 61.9308 | 0.064445 | -0.015858 | 0.13964 | 0.14431 | -0.020664 | 0.035717 | 0.07984 | -0.0080639 | -0.0084727 | 0.1048 | 0.059431 | 0.04909 | -0.003531 | 0.0243 | 0.000747 | -0.007391 | -0.050009 | -0.004549 | 0.001048 | -0.00811 | 0.018674 | -0.038036 | -0.057425 | 0.018285 | -0.0884 | -0.040521 | 62.0463 | -61.9382 | 62.0418 | 62.046 | -0.000301 | -61.9809 | -61.9354 | 62.0048 | -61.9883 | 62.0372 | 62.0073 | 0.002485 | -61.9126 | -62.0192 | 62.0379 | 61.9953 | 62.0407 | 62.0696 | -61.9298 | 61.9879 | 62.0636 | 61.9569 | 62.064 | -61.9714
574.9219 | 123.7061 | -61.8668 | 62.1048 | 0.049183 | -0.015858 | 0.13858 | 0.14324 | -0.020664 | 0.034648 | 0.07984 | -0.0080639 | -0.0063367 | 0.10373 | 0.060499 | 0.04909 | -0.003531 | 0.0243 | -0.003831 | -0.021127 | -0.050009 | -0.004549 | 0.005627 | -0.003531 | 0.018674 | -0.033458 | -0.052847 | 0.013707 | -0.097557 | -0.035942 | 61.8724 | -62.1259 | 61.8632 | 61.8629 | -0.009458 | -62.1548 | -62.1093 | 61.8308 | -62.1576 | 61.8632 | 61.8333 | 0.002484 | -62.0911 | -62.2024 | 61.8456 | 61.8168 | 61.8622 | 61.8911 | -62.0992 | 61.8139 | 61.8805 | 61.7692 | 61.8854 | -62.1407
575.9062 | 124.2783 | -62.059 | 62.1368 | 0.064445 | -0.015858 | 0.14071 | 0.14217 | -0.021732 | 0.036785 | 0.07984 | -0.0069959 | -0.0084727 | 0.10586 | 0.060499 | 0.04909 | -0.012688 | 0.019721 | 0.000747 | -0.021127 | -0.054588 | 2.9e-05 | 0.005627 | -0.00811 | 0.023253 | -0.038036 | -0.052847 | 0.013707 | -0.092979 | -0.031363 | 62.0646 | -62.158 | 62.0463 | 62.0598 | -0.00488 | -62.1914 | -62.1368 | 62.0277 | -62.1897 | 62.0509 | 62.021 | -0.006673 | -62.1231 | -62.2298 | 62.0379 | 62.0044 | 62.059 | 62.0787 | -62.1312 | 62.0062 | 62.0727 | 61.966 | 62.0823 | -62.1682
576.9062 | 124.0952 | -62.0361 | 62.1735 | 0.079707 | -0.016927 | 0.14071 | 0.14217 | -0.021732 | 0.035717 | 0.064579 | -0.0059269 | -0.0095417 | 0.1048 | 0.063704 | 0.050158 | -0.003531 | 0.028878 | 0.005325 | -0.007391 | -0.04543 | -0.018285 | 0.069732 | -0.003531 | 0.018674 | -0.033458 | -0.052847 | 0.004549 | -0.12045 | -0.049678 | 62.1059 | -62.1809 | 62.0326 | 62.0415 | -0.064407 | -62.2189 | -62.1917 | 61.9865 | -62.2263 | 62.0326 | 62.0027 | 0.01622 | -62.1689 | -62.2939 | 62.0287 | 61.9907 | 62.0178 | 62.065 | -62.1037 | 61.9833 | 62.0407 | 61.9157 | 62.0548 | -62.2231
577.9688 | 124.2416 | -62.0407 | 62.1094 | 0.064445 | -0.016927 | 0.13751 | 0.14324 | -0.020664 | 0.036785 | 0.07984 | -0.0069959 | -0.0095417 | 0.10586 | 0.062636 | 0.050158 | -0.008109 | 0.0243 | -0.008409 | -0.044018 | -0.04543 | -0.013707 | 0.092626 | -0.012689 | 0.014095 | -0.0243 | -0.057425 | 0.013707 | -0.13419 | -0.0451 | 62.1333 | -62.1534 | 62.0326 | 62.0323 | -0.10103 | -62.1548 | -62.1231 | 61.9956 | -62.1668 | 62.028 | 62.0164 | 0.0208 | -62.0957 | -62.2436 | 61.9967 | 61.9953 | 62.027 | 62.065 | -62.0167 | 61.9833 | 62.0544 | 61.9065 | 62.0548 | -62.1545
578.9062 | 124.1318 | -62.0453 | 62.1643 | 0.064445 | -0.016927 | 0.13964 | 0.14431 | -0.018528 | 0.035717 | 0.07984 | -0.0080639 | -0.0084727 | 0.1048 | 0.061567 | 0.04909 | -0.003531 | 0.019721 | -0.003831 | -0.002813 | -0.050009 | -0.045757 | 0.11552 | -0.012689 | 0.023253 | -0.038036 | -0.052847 | 0.013707 | -0.12503 | -0.049678 | 62.1608 | -62.1671 | 62.0418 | 62.0415 | -0.11935 | -62.2143 | -62.2101 | 61.9956 | -62.2172 | 62.0326 | 62.0073 | 0.011642 | -62.1506 | -62.2893 | 62.0425 | 61.9953 | 61.9995 | 62.065 | -62.0488 | 61.9924 | 62.059 | 61.9203 | 62.0685 | -62.214
579.9844 | 124.3378 | -62.0544 | 62.0636 | 0.049183 | -0.016927 | 0.14178 | 0.1411 | -0.020664 | 0.035717 | 0.07984 | -0.0069959 | -0.0095417 | 0.10586 | 0.061567 | 0.051227 | -0.012688 | 0.015142 | -0.003831 | -0.01197 | -0.040851 | -0.041178 | 0.12468 | -0.00811 | 0.023253 | -0.028879 | -0.062004 | 0.022864 | -0.12961 | -0.040521 | 62.1791 | -62.0756 | 62.0418 | 62.0506 | -0.12851 | -62.1045 | -62.1048 | 62.0139 | -62.1256 | 62.0463 | 62.0256 | 0.011642 | -62.0407 | -62.1932 | 62.0425 | 62.0136 | 62.0133 | 62.0696 | -61.9389 | 61.9924 | 62.0773 | 61.9248 | 62.0777 | -62.1041

## Thermal Data
Fire Time | South 11 C | Cable 1 | Cable 2
-0.7615 | 22.1613 | 20.3454 | 20.4493
0.2385 | 22.1604 | 20.3457 | 20.452
1.2385 | 22.162 | 20.349 | 20.4521
2.2385 | 22.1629 | 20.3452 | 20.4524
3.2385 | 22.1702 | 20.3485 | 20.4557
4.2385 | 22.3148 | 20.3468 | 20.4545
5.2385 | 22.9506 | 20.3484 | 20.4555
6.2385 | 24.2131 | 20.3493 | 20.4496
7.2385 | 26.0461 | 20.344 | 20.4564
8.2385 | 28.386 | 20.3575 | 20.4609
9.2385 | 31.1718 | 20.3686 | 20.4642
10.2385 | 34.3035 | 20.3879 | 20.4785
11.2385 | 37.755 | 20.3963 | 20.4838
12.2385 | 41.4935 | 20.4162 | 20.5051
13.2385 | 45.4731 | 20.4425 | 20.5281
14.2385 | 49.6805 | 20.4676 | 20.5529
15.2385 | 54.0324 | 20.5093 | 20.5892
16.2385 | 58.644 | 20.5473 | 20.6298
17.2385 | 63.3744 | 20.605 | 20.6832
18.2385 | 68.2107 | 20.6607 | 20.7326
19.2385 | 73.1451 | 20.7345 | 20.8063
20.2385 | 78.2016 | 20.8207 | 20.8788
21.2385 | 83.4144 | 20.907 | 20.9599
22.2385 | 88.6894 | 21.0099 | 21.06
23.2385 | 94.0505 | 21.1216 | 21.1696
24.2385 | 99.5044 | 21.2297 | 21.2985
25.2385 | 105.0403 | 21.3727 | 21.4304
26.2385 | 110.6517 | 21.5217 | 21.59
27.2385 | 116.3464 | 21.6818 | 21.7459
28.2385 | 122.0909 | 21.8599 | 21.9325
29.2385 | 127.8763 | 22.0564 | 22.1174
30.2385 | 133.6989 | 22.2603 | 22.3206
31.2385 | 139.5807 | 22.494 | 22.5484
32.2385 | 145.5246 | 22.7365 | 22.781
33.2385 | 151.4497 | 22.9935 | 23.0346
34.2385 | 157.4047 | 23.2577 | 23.3048
35.2385 | 163.3743 | 23.554 | 23.5847
36.2385 | 169.327 | 23.8617 | 23.8883
37.2385 | 175.2706 | 24.183 | 24.2124
38.2385 | 181.1711 | 24.531 | 24.5448
39.2385 | 187.0795 | 24.8895 | 24.9159
40.2385 | 193.0515 | 25.2786 | 25.3118
41.2385 | 199.0439 | 25.6754 | 25.7023
42.2385 | 205.0276 | 26.1051 | 26.1235
43.2385 | 210.9164 | 26.5609 | 26.5537
44.2385 | 216.7759 | 27.0499 | 27.0168
45.2385 | 222.7223 | 27.5537 | 27.4971
46.2385 | 228.7016 | 28.0628 | 28.0057
47.2385 | 234.7299 | 28.5913 | 28.524
48.2385 | 240.6207 | 29.1272 | 29.0621
49.2385 | 246.4929 | 29.6748 | 29.6269
50.2385 | 252.3255 | 30.2492 | 30.2261
51.2385 | 258.1047 | 30.8513 | 30.8386
52.2385 | 263.8312 | 31.4912 | 31.476
53.2385 | 269.5264 | 32.1423 | 32.1199
54.2385 | 275.2312 | 32.8034 | 32.7902
55.2385 | 280.9322 | 33.4966 | 33.4713
56.2385 | 286.3658 | 34.2114 | 34.1803
57.2385 | 291.4092 | 34.9468 | 34.9114
58.2385 | 296.144 | 35.6748 | 35.6432
59.2385 | 300.5406 | 36.4209 | 36.3964
60.2385 | 304.7037 | 37.1825 | 37.1801
61.2385 | 308.7335 | 37.9539 | 37.9667
62.2385 | 312.4917 | 38.7315 | 38.7565
63.2385 | 316.095 | 39.5147 | 39.5635
64.2385 | 319.4229 | 40.2934 | 40.3769
65.2385 | 322.3523 | 41.0755 | 41.1877
66.2385 | 324.8937 | 41.8711 | 42.0124
67.2385 | 327.1093 | 42.6754 | 42.845
68.2385 | 329.0445 | 43.4941 | 43.6797
69.2385 | 330.6829 | 44.3222 | 44.5331
70.2385 | 332.1811 | 45.159 | 45.3876
71.2385 | 333.5172 | 45.9882 | 46.248
72.2385 | 334.6674 | 46.823 | 47.0981
73.2385 | 335.6232 | 47.6576 | 47.9557
74.2385 | 336.4025 | 48.499 | 48.8154
75.2385 | 336.919 | 49.3161 | 49.6621
76.2385 | 337.3273 | 50.1299 | 50.5091
77.2385 | 337.6346 | 50.936 | 51.3558
78.2385 | 337.7893 | 51.7286 | 52.2137
79.2385 | 337.9092 | 52.5115 | 53.0577
80.2385 | 337.8264 | 53.3017 | 53.9169
81.2385 | 337.7041 | 54.087 | 54.7635
82.2385 | 337.5957 | 54.8591 | 55.6087
83.2385 | 337.5168 | 55.6301 | 56.4549
84.2385 | 337.345 | 56.3969 | 57.2986
85.2385 | 337.1067 | 57.1525 | 58.1347
86.2385 | 336.8649 | 57.9126 | 58.9583
87.2385 | 336.6059 | 58.6637 | 59.7879
88.2385 | 336.2337 | 59.4003 | 60.6056
89.2385 | 335.7749 | 60.1378 | 61.4306
90.2385 | 335.4097 | 60.878 | 62.2444
91.2385 | 334.9988 | 61.6109 | 63.0549
92.2385 | 334.556 | 62.3456 | 63.8664
93.2385 | 334.2133 | 63.0684 | 64.6592
94.2385 | 333.8441 | 63.8017 | 65.4545
95.2385 | 333.5046 | 64.5187 | 66.2352
96.2385 | 333.1084 | 65.2234 | 66.997
97.2385 | 332.7026 | 65.935 | 67.7687
98.2385 | 332.2247 | 66.6377 | 68.5356
99.2385 | 331.7876 | 67.34 | 69.2852
100.2385 | 331.3296 | 68.0403 | 70.0369
101.2385 | 330.7503 | 68.7333 | 70.7763
102.2385 | 330.1804 | 69.4147 | 71.5057
103.2385 | 329.6351 | 70.0961 | 72.2372
104.2385 | 329.2275 | 70.7763 | 72.9709
105.2385 | 328.6636 | 71.4466 | 73.6774
106.2385 | 328.0059 | 72.1009 | 74.3807
107.2385 | 327.5559 | 72.7636 | 75.0808
108.2385 | 327.0969 | 73.4074 | 75.7592
109.2385 | 326.514 | 74.0429 | 76.4292
110.2385 | 325.9826 | 74.6718 | 77.0941
111.2385 | 325.4384 | 75.2994 | 77.7539
112.2385 | 324.9025 | 75.9171 | 78.4037
113.2385 | 324.3538 | 76.5357 | 79.0427
114.2385 | 323.8389 | 77.1459 | 79.6847
115.2385 | 323.3379 | 77.741 | 80.3129
116.2385 | 322.7631 | 78.329 | 80.9285
117.2385 | 322.2649 | 78.9055 | 81.5222
118.2385 | 321.8035 | 79.4705 | 82.1216
119.2385 | 321.5154 | 80.0377 | 82.7042
120.2385 | 321.2016 | 80.6005 | 83.2808
121.2385 | 320.8196 | 81.149 | 83.8507
122.2385 | 320.5665 | 81.7103 | 84.4166
123.2385 | 320.3687 | 82.2792 | 84.9875
124.2385 | 320.2336 | 82.8225 | 85.5436
125.2385 | 320.1154 | 83.3772 | 86.1078
126.2385 | 320.1309 | 83.9295 | 86.6672
127.2385 | 320.1589 | 84.4814 | 87.2222
128.2385 | 320.1828 | 85.0208 | 87.7632
129.2385 | 320.242 | 85.566 | 88.3159
130.2385 | 320.4894 | 86.1048 | 88.8591
131.2385 | 320.6818 | 86.6253 | 89.3927
132.2385 | 321.0049 | 87.1443 | 89.9216
133.2385 | 321.3516 | 87.6634 | 90.4552
134.2385 | 321.7997 | 88.1885 | 90.9927
135.2385 | 322.1331 | 88.719 | 91.5376
136.2385 | 322.266 | 89.2554 | 92.0777
137.2385 | 322.6578 | 89.7928 | 92.626
138.2385 | 323.1189 | 90.3372 | 93.1722
139.2385 | 323.6254 | 90.8692 | 93.725
140.2385 | 323.9372 | 91.4123 | 94.2736
141.2385 | 324.2447 | 91.9682 | 94.8278
142.2385 | 324.5106 | 92.5091 | 95.3823
143.2385 | 324.8576 | 93.0437 | 95.9449
144.2385 | 325.0989 | 93.5937 | 96.5099
145.2385 | 325.3457 | 94.1294 | 97.0741
146.2385 | 325.6857 | 94.6745 | 97.6324
147.2385 | 326.0195 | 95.2131 | 98.1936
148.2385 | 326.3488 | 95.7722 | 98.7586
149.2385 | 326.5972 | 96.3204 | 99.3228
150.2385 | 326.8054 | 96.8719 | 99.8961
151.2385 | 327.0972 | 97.4119 | 100.462
152.2385 | 327.3953 | 97.9501 | 101.0364
153.2385 | 327.651 | 98.4828 | 101.6077
154.2385 | 327.86 | 99.0273 | 102.1724
155.2385 | 328.1716 | 99.5664 | 102.7408
156.2385 | 328.3341 | 100.0968 | 103.3089
157.2385 | 328.4087 | 100.6265 | 103.8681
158.2385 | 328.4717 | 101.1703 | 104.4285
159.2385 | 328.5913 | 101.6937 | 104.9962
160.2385 | 328.7743 | 102.2343 | 105.5571
161.2385 | 328.8634 | 102.7728 | 106.1211
162.2385 | 328.9644 | 103.3056 | 106.6829
163.2385 | 328.9768 | 103.8436 | 107.2427
164.2385 | 328.9977 | 104.3834 | 107.81
165.2385 | 329.0713 | 104.9184 | 108.388
166.2385 | 329.1233 | 105.4591 | 108.9535
167.2385 | 329.1406 | 105.9913 | 109.5253
168.2385 | 329.1205 | 106.5312 | 110.0952
169.2385 | 329.15 | 107.057 | 110.6759
170.2385 | 329.2614 | 107.6029 | 111.242
171.2385 | 329.3814 | 108.1411 | 111.8141
172.2385 | 329.4339 | 108.6797 | 112.3924
173.2385 | 329.3931 | 109.208 | 112.9667
174.2385 | 329.3964 | 109.7444 | 113.5366
175.2385 | 329.428 | 110.2757 | 114.1121
176.2385 | 329.3701 | 110.8135 | 114.6813
177.2385 | 329.3018 | 111.3419 | 115.2447
178.2385 | 329.2376 | 111.8652 | 115.8048
179.2385 | 329.1467 | 112.4019 | 116.3677
180.2385 | 329.1149 | 112.9133 | 116.9224
181.2385 | 329.1216 | 113.4383 | 117.4832
182.2385 | 329.1733 | 113.9515 | 118.0416
183.2385 | 329.1854 | 114.479 | 118.5951
184.2385 | 329.2095 | 114.9897 | 119.1638
185.2385 | 329.223 | 115.4983 | 119.7179
186.2385 | 329.2076 | 116.014 | 120.3042
187.2385 | 329.2433 | 116.5168 | 120.8676
188.2385 | 329.2262 | 117.0346 | 121.4328
189.2385 | 329.2217 | 117.5428 | 121.9996
190.2385 | 329.2349 | 118.0522 | 122.5596
191.2385 | 329.2422 | 118.5666 | 123.1242
192.2385 | 329.1788 | 119.0689 | 123.6913
193.2385 | 329.0405 | 119.581 | 124.2648
194.2385 | 328.9807 | 120.0971 | 124.8442
195.2385 | 328.8997 | 120.5971 | 125.4123
196.2385 | 328.9047 | 121.0964 | 125.982
197.2385 | 328.8944 | 121.593 | 126.5433
198.2385 | 328.8952 | 122.0848 | 127.112
199.2385 | 328.8749 | 122.58 | 127.6696
200.2385 | 328.8105 | 123.0604 | 128.2328
201.2385 | 328.7422 | 123.5438 | 128.7913
202.2385 | 328.7246 | 124.0254 | 129.3393
203.2385 | 328.7451 | 124.5152 | 129.9067
204.2385 | 328.8393 | 125.0045 | 130.4555
205.2385 | 328.8602 | 125.4796 | 131.0047
206.2385 | 328.8243 | 125.9703 | 131.5469
207.2385 | 328.8366 | 126.4411 | 132.1005
208.2385 | 328.8734 | 126.9235 | 132.6439
209.2385 | 328.8983 | 127.4028 | 133.1904
210.2385 | 329.0108 | 127.8742 | 133.7336
211.2385 | 329.0664 | 128.3481 | 134.2893
212.2385 | 329.1547 | 128.8221 | 134.8148
213.2385 | 329.2617 | 129.2926 | 135.3801
214.2385 | 329.2511 | 129.7747 | 135.9302
215.2385 | 329.2271 | 130.2475 | 136.4821
216.2385 | 329.3052 | 130.713 | 137.0215
217.2385 | 329.3557 | 131.1696 | 137.5676
218.2385 | 329.3298 | 131.6326 | 138.1033
219.2385 | 329.4241 | 132.094 | 138.6441
220.2385 | 329.5807 | 132.5624 | 139.1894
221.2385 | 329.545 | 133.0166 | 139.7259
222.2385 | 329.6272 | 133.4817 | 140.2632
223.2385 | 329.6868 | 133.9243 | 140.7949
224.2385 | 329.6746 | 134.3832 | 141.3327
225.2385 | 329.7825 | 134.8355 | 141.8629
226.2385 | 329.9072 | 135.2943 | 142.3923
227.2385 | 329.8941 | 135.7308 | 142.924
228.2385 | 329.7901 | 136.1782 | 143.45
229.2385 | 329.7863 | 136.6277 | 143.9795
230.2385 | 329.8346 | 137.0686 | 144.4984
231.2385 | 329.7898 | 137.5166 | 145.0168
232.2385 | 329.7502 | 137.9525 | 145.5331
233.2385 | 329.7546 | 138.3995 | 146.0442
234.2385 | 329.7439 | 138.8337 | 146.5473
235.2385 | 329.7395 | 139.2902 | 147.0592
236.2385 | 329.7815 | 139.7182 | 147.5688
237.2385 | 329.742 | 140.15 | 148.0801
238.2385 | 329.7422 | 140.5839 | 148.5831
239.2385 | 329.7519 | 140.9978 | 149.096
240.2385 | 329.7543 | 141.4315 | 149.599
241.2385 | 329.7162 | 141.8591 | 150.0979
242.2385 | 329.7377 | 142.2823 | 150.5917
243.2385 | 329.8125 | 142.7044 | 151.0884
244.2385 | 329.8372 | 143.1327 | 151.5866
245.2385 | 329.7793 | 143.5455 | 152.0782
246.2385 | 329.7236 | 143.9568 | 152.5674
247.2385 | 329.6306 | 144.3723 | 153.0559
248.2385 | 329.5279 | 144.7857 | 153.5433
249.2385 | 329.5895 | 145.1954 | 154.0202
250.2385 | 329.6795 | 145.6045 | 154.5025
251.2385 | 329.6942 | 146.0059 | 154.9783
252.2385 | 329.7262 | 146.4155 | 155.4581
253.2385 | 329.7561 | 146.8261 | 155.9348
254.2385 | 329.7554 | 147.2233 | 156.4168
255.2385 | 329.7587 | 147.6212 | 156.8862
256.2385 | 329.8309 | 148.0272 | 157.3571
257.2385 | 329.8642 | 148.4265 | 157.8238
258.2385 | 329.8466 | 148.839 | 158.2869
259.2385 | 329.8281 | 149.2434 | 158.7625
260.2385 | 329.8189 | 149.6493 | 159.214
261.2385 | 329.7951 | 150.0484 | 159.6731
262.2385 | 329.8443 | 150.4466 | 160.128
263.2385 | 329.8981 | 150.8546 | 160.5751
264.2385 | 329.9515 | 151.2544 | 161.0262
265.2385 | 330.0166 | 151.6556 | 161.4761
266.2385 | 330.0379 | 152.055 | 161.93
267.2385 | 330.0634 | 152.4521 | 162.377
268.2385 | 330.0485 | 152.8539 | 162.8266
269.2385 | 330.0585 | 153.2488 | 163.2808
270.2385 | 330.1296 | 153.6499 | 163.7275
271.2385 | 330.1319 | 154.0453 | 164.1843
272.2385 | 330.1415 | 154.44 | 164.6421
273.2385 | 330.0634 | 154.8263 | 165.104
274.2385 | 330.0383 | 155.2275 | 165.5696
275.2385 | 330.0168 | 155.6205 | 166.0365
276.2385 | 330.0028 | 156.0209 | 166.5081
277.2385 | 329.9811 | 156.4156 | 166.9777
278.2385 | 329.8924 | 156.8154 | 167.4547
279.2385 | 329.6855 | 157.2107 | 167.937
280.2385 | 329.6376 | 157.6015 | 168.4274
281.2385 | 329.6781 | 158.0056 | 168.9137
282.2385 | 329.7222 | 158.3889 | 169.3993
283.2385 | 329.7973 | 158.8031 | 169.8926
284.2385 | 329.8595 | 159.1898 | 170.3876
285.2385 | 329.8111 | 159.5896 | 170.9031
286.2385 | 329.7693 | 159.976 | 171.4236
287.2385 | 329.7157 | 160.3704 | 171.9379
288.2385 | 329.6903 | 160.7666 | 172.473
289.2385 | 329.622 | 161.1642 | 173.0035
290.2385 | 329.5529 | 161.5377 | 173.5348
291.2385 | 329.5627 | 161.9377 | 174.0596
292.2385 | 329.5415 | 162.3299 | 174.5874
293.2385 | 329.5919 | 162.7155 | 175.115
294.2385 | 329.5778 | 163.0928 | 175.6447
295.2385 | 329.6422 | 163.4864 | 176.1722
296.2385 | 329.7249 | 163.8742 | 176.6946
297.2385 | 329.818 | 164.2578 | 177.1938
298.2385 | 329.8083 | 164.6399 | 177.6908
299.2385 | 329.8253 | 165.024 | 178.1993
300.2385 | 329.8686 | 165.3986 | 178.6996
301.2385 | 329.7523 | 165.7852 | 179.1969
302.2385 | 329.6665 | 166.1798 | 179.6931
303.2385 | 329.5906 | 166.5576 | 180.1951
304.2385 | 329.4957 | 166.9391 | 180.6898
305.2385 | 329.4772 | 167.3288 | 181.2003
306.2385 | 329.4238 | 167.7099 | 181.7029
307.2385 | 329.3479 | 168.0877 | 182.2197
308.2385 | 329.2834 | 168.4855 | 182.7425
309.2385 | 329.294 | 168.8643 | 183.2607
310.2385 | 329.2434 | 169.2492 | 183.794
311.2385 | 329.2057 | 169.6257 | 184.3328
312.2385 | 329.2108 | 170.0029 | 184.878
313.2385 | 329.2456 | 170.3789 | 185.4692
314.2385 | 329.2539 | 170.7692 | 186.0434
315.2385 | 329.2751 | 171.1429 | 186.622
316.2385 | 329.3411 | 171.5358 | 187.1825
317.2385 | 329.3462 | 171.9195 | 187.722
318.2385 | 329.3332 | 172.2886 | 188.2737
319.2385 | 329.4168 | 172.6732 | 188.797
320.2385 | 329.5418 | 173.0633 | 189.3171
321.2385 | 329.6708 | 173.4322 | 189.8353
322.2385 | 329.7299 | 173.8122 | 190.336
323.2385 | 329.759 | 174.1998 | 190.8349
324.2385 | 329.8576 | 174.5793 | 191.3199
325.2385 | 329.8401 | 174.9587 | 191.8026
326.2385 | 329.7939 | 175.3268 | 192.2719
327.2385 | 329.7395 | 175.7167 | 192.7228
328.2385 | 329.6835 | 176.0957 | 193.1718
329.2385 | 329.705 | 176.4656 | 193.6089
330.2385 | 329.7144 | 176.8536 | 194.0349
331.2385 | 329.7027 | 177.2184 | 194.4574
332.2385 | 329.6716 | 177.6032 | 194.8614
333.2385 | 329.624 | 177.9766 | 195.2603
334.2385 | 329.5625 | 178.3637 | 195.6532
335.2385 | 329.5086 | 178.7282 | 196.0341
336.2385 | 329.4519 | 179.1091 | 196.4113
337.2385 | 329.3757 | 179.4785 | 196.7818
338.2385 | 329.3939 | 179.8459 | 197.1438
339.2385 | 329.4276 | 180.2151 | 197.4955
340.2385 | 329.3843 | 180.5787 | 197.8565
341.2385 | 329.351 | 180.9479 | 198.1925
342.2385 | 329.3344 | 181.3115 | 198.5288
343.2385 | 329.2914 | 181.6845 | 198.8567
344.2385 | 329.2997 | 182.0512 | 199.1831
345.2385 | 329.2798 | 182.42 | 199.5072
346.2385 | 329.1958 | 182.7803 | 199.8293
347.2385 | 329.1621 | 183.1439 | 200.1522
348.2385 | 329.1096 | 183.5025 | 200.4621
349.2385 | 329.0859 | 183.8657 | 200.7777
350.2385 | 329.0813 | 184.2188 | 201.0801
351.2385 | 329.0577 | 184.5862 | 201.3812
352.2385 | 328.9994 | 184.9418 | 201.6735
353.2385 | 328.8912 | 185.2937 | 201.9647
354.2385 | 328.8646 | 185.6505 | 202.2492
355.2385 | 328.8453 | 186.0045 | 202.5255
356.2385 | 328.9591 | 186.3526 | 202.8149
357.2385 | 329.0382 | 186.7068 | 203.0907
358.2385 | 329.0491 | 187.0581 | 203.3723
359.2385 | 329.0643 | 187.4097 | 203.6478
360.2385 | 329.0089 | 187.7588 | 203.9268
361.2385 | 328.9637 | 188.1129 | 204.2049
362.2385 | 328.9748 | 188.4592 | 204.4735
363.2385 | 328.9884 | 188.8072 | 204.7492
364.2385 | 328.9862 | 189.1457 | 205.0118
365.2385 | 328.9713 | 189.4836 | 205.2755
366.2385 | 328.898 | 189.8303 | 205.5429
367.2385 | 328.8484 | 190.1741 | 205.8036
368.2385 | 328.7565 | 190.5162 | 206.0562
369.2385 | 328.6957 | 190.8574 | 206.317
370.2385 | 328.6585 | 191.1998 | 206.5643
371.2385 | 328.6647 | 191.5317 | 206.8208
372.2385 | 328.6019 | 191.8618 | 207.0799
373.2385 | 328.5367 | 192.192 | 207.3282
374.2385 | 328.6565 | 192.52 | 207.5869
375.2385 | 328.681 | 192.8476 | 207.8354
376.2385 | 328.6505 | 193.1738 | 208.0809
377.2385 | 328.5269 | 193.4903 | 208.3322
378.2385 | 328.456 | 193.8062 | 208.5653
379.2385 | 328.4678 | 194.1292 | 208.8021
380.2385 | 328.4524 | 194.4472 | 209.0432
381.2385 | 328.4294 | 194.77 | 209.2826
382.2385 | 328.5118 | 195.0874 | 209.5103
383.2385 | 328.5031 | 195.4025 | 209.7465
384.2385 | 328.5325 | 195.7155 | 209.9733
385.2385 | 328.5318 | 196.0225 | 210.1946
386.2385 | 328.5353 | 196.3333 | 210.4255
387.2385 | 328.567 | 196.6437 | 210.6543
388.2385 | 328.5755 | 196.9551 | 210.8757
389.2385 | 328.6555 | 197.2617 | 211.0907
390.2385 | 328.7094 | 197.5637 | 211.3141
391.2385 | 328.7897 | 197.8694 | 211.531
392.2385 | 328.8378 | 198.168 | 211.7487
393.2385 | 328.8754 | 198.4695 | 211.9545
394.2385 | 328.9695 | 198.7503 | 212.1694
395.2385 | 329.0362 | 199.0577 | 212.388
396.2385 | 329.0957 | 199.3498 | 212.5845
397.2385 | 329.167 | 199.6446 | 212.7948
398.2385 | 329.1942 | 199.9385 | 212.9972
399.2385 | 329.2552 | 200.1989 | 213.2054
400.2385 | 329.2184 | 200.456 | 213.41
401.2385 | 329.2414 | 200.6966 | 213.6052
402.2385 | 329.2745 | 200.9371 | 213.798
403.2385 | 329.2465 | 201.1879 | 214.0026
404.2385 | 329.2188 | 201.433 | 214.1979
405.2385 | 329.203 | 201.6699 | 214.3911
406.2385 | 329.2426 | 201.9031 | 214.5833
407.2385 | 329.3439 | 202.1336 | 214.7841
408.2385 | 329.419 | 202.3635 | 214.9789
409.2385 | 329.4363 | 202.5898 | 215.1673
410.2385 | 329.4398 | 202.8103 | 215.367
411.2385 | 329.4585 | 203.0316 | 215.5626
412.2385 | 329.525 | 203.2531 | 215.7474
413.2385 | 329.5617 | 203.4717 | 215.9388
414.2385 | 329.5969 | 203.6927 | 216.1289
415.2385 | 329.7207 | 203.9125 | 216.3179
416.2385 | 329.7925 | 204.1333 | 216.5091
417.2385 | 329.8772 | 204.3528 | 216.694
418.2385 | 329.8612 | 204.5814 | 216.8734
419.2385 | 329.9893 | 204.8024 | 217.0644
420.2385 | 330.1511 | 205.0301 | 217.2451
421.2385 | 330.2953 | 205.2611 | 217.4478
422.2385 | 330.4055 | 205.4872 | 217.6298
423.2385 | 330.4139 | 205.7076 | 217.8104
424.2385 | 330.4526 | 205.943 | 217.9933
425.2385 | 330.4876 | 206.1643 | 218.1738
426.2385 | 330.4137 | 206.3865 | 218.3557
427.2385 | 330.4104 | 206.6013 | 218.5401
428.2385 | 330.4348 | 206.8295 | 218.722
429.2385 | 330.3529 | 207.0355 | 218.8897
430.2385 | 330.2276 | 207.2675 | 219.0801
431.2385 | 330.1712 | 207.4873 | 219.2511
432.2385 | 330.1363 | 207.7165 | 219.4328
433.2385 | 330.0853 | 207.9238 | 219.6029
434.2385 | 330.0398 | 208.1466 | 219.7702
435.2385 | 329.9878 | 208.3533 | 219.9309
436.2385 | 329.9202 | 208.5643 | 220.0955
437.2385 | 329.8474 | 208.7831 | 220.2542
438.2385 | 329.6637 | 208.9867 | 220.4129
439.2385 | 329.5598 | 209.1979 | 220.5667
440.2385 | 329.5077 | 209.3946 | 220.7161
441.2385 | 329.3844 | 209.6044 | 220.8643
442.2385 | 329.2616 | 209.8177 | 221.0176
443.2385 | 329.1585 | 210.0171 | 221.1637
444.2385 | 329.1143 | 210.2235 | 221.302
445.2385 | 329.041 | 210.4247 | 221.4453
446.2385 | 328.9538 | 210.6244 | 221.5772
447.2385 | 328.9077 | 210.8149 | 221.7168
448.2385 | 328.8534 | 211.0143 | 221.8447
449.2385 | 328.8418 | 211.1987 | 221.9728
450.2385 | 328.7989 | 211.3818 | 222.0987
451.2385 | 328.7446 | 211.5617 | 222.227
452.2385 | 328.7274 | 211.7405 | 222.3387
453.2385 | 328.7177 | 211.921 | 222.4586
454.2385 | 328.7044 | 212.1099 | 222.5718
455.2385 | 328.6944 | 212.2881 | 222.6837
456.2385 | 328.6876 | 212.4524 | 222.7996
457.2385 | 328.6394 | 212.6067 | 222.9042
458.2385 | 328.5577 | 212.7582 | 223.0078
459.2385 | 328.5262 | 212.9132 | 223.1063
460.2385 | 328.5297 | 213.0688 | 223.2075
461.2385 | 328.5622 | 213.2242 | 223.3003
462.2385 | 328.6328 | 213.3653 | 223.3886
463.2385 | 328.6892 | 213.505 | 223.4716
464.2385 | 328.7661 | 213.6422 | 223.5516
465.2385 | 328.8515 | 213.768 | 223.6291
466.2385 | 328.9299 | 213.8875 | 223.7009
467.2385 | 328.9544 | 214.0168 | 223.7694
468.2385 | 329.0272 | 214.1322 | 223.8332
469.2385 | 329.1095 | 214.2514 | 223.917
470.2385 | 329.1905 | 214.3704 | 223.9816
471.2385 | 329.2794 | 214.4922 | 224.0635
472.2385 | 329.3996 | 214.6102 | 224.1579
473.2385 | 329.3995 | 214.7396 | 224.2483
474.2385 | 329.4409 | 214.8556 | 224.3443
475.2385 | 329.5065 | 214.9771 | 224.445
476.2385 | 329.5667 | 215.0847 | 224.5509
477.2385 | 329.6921 | 215.1992 | 224.658
478.2385 | 329.7375 | 215.3032 | 224.7635
479.2385 | 329.8534 | 215.4087 | 224.8683
480.2385 | 329.9356 | 215.5046 | 224.973
481.2385 | 329.9357 | 215.6146 | 225.0904
482.2385 | 329.9286 | 215.7207 | 225.2078
483.2385 | 329.9377 | 215.8247 | 225.3167
484.2385 | 329.9727 | 215.9236 | 225.4476
485.2385 | 330.0043 | 216.027 | 225.5665
486.2385 | 330.0625 | 216.1212 | 225.691
487.2385 | 330.021 | 216.2148 | 225.8227
488.2385 | 330.0178 | 216.3023 | 225.9488
489.2385 | 329.9724 | 216.3903 | 226.083
490.2385 | 329.8831 | 216.4617 | 226.2213
491.2385 | 329.7914 | 216.5454 | 226.3564
492.2385 | 329.7233 | 216.6297 | 226.4826
493.2385 | 329.6458 | 216.7125 | 226.6144
494.2385 | 329.5632 | 216.7963 | 226.7432
495.2385 | 329.563 | 216.8838 | 226.8763
496.2385 | 329.4784 | 216.9554 | 226.9958
497.2385 | 329.4541 | 217.0449 | 227.1341
498.2385 | 329.4479 | 217.1215 | 227.2563
499.2385 | 329.3495 | 217.2008 | 227.3695
500.2385 | 329.2779 | 217.2837 | 227.4904
501.2385 | 329.1674 | 217.3775 | 227.6109
502.2385 | 329.1923 | 217.439 | 227.7174
503.2385 | 329.2203 | 217.512 | 227.831
504.2385 | 329.2262 | 217.5855 | 227.9384
505.2385 | 329.2817 | 217.6581 | 228.0425
506.2385 | 329.2655 | 217.7238 | 228.1446
507.2385 | 329.2565 | 217.793 | 228.2433
508.2385 | 329.2735 | 217.8571 | 228.3374
509.2385 | 329.3454 | 217.9288 | 228.4207
510.2385 | 329.3728 | 217.9843 | 228.5041
511.2385 | 329.4077 | 218.0682 | 228.5797
512.2385 | 329.4417 | 218.1384 | 228.662
513.2385 | 329.4658 | 218.2254 | 228.7236
514.2385 | 329.4204 | 218.3063 | 228.7909
515.2385 | 329.4244 | 218.3878 | 228.8476
516.2385 | 329.5178 | 218.465 | 228.8999
517.2385 | 329.5809 | 218.5399 | 228.9532
518.2385 | 329.5889 | 218.6175 | 229.0055
519.2385 | 329.5399 | 218.6921 | 229.0569
520.2385 | 329.5003 | 218.7599 | 229.1053
521.2385 | 329.4508 | 218.8346 | 229.1591
522.2385 | 329.4387 | 218.9015 | 229.206
523.2385 | 329.4944 | 218.973 | 229.2363
524.2385 | 329.4738 | 219.018 | 229.2736
525.2385 | 329.5047 | 219.0825 | 229.3059
526.2385 | 329.5413 | 219.1364 | 229.3379
527.2385 | 329.5842 | 219.1812 | 229.3683
528.2385 | 329.676 | 219.1798 | 229.4009
529.2385 | 329.6873 | 218.9821 | 229.4294
530.2385 | 329.6427 | 218.984 | 229.459
531.2385 | 329.6329 | 219.0617 | 229.4896
532.2385 | 329.6385 | 219.1583 | 229.525
533.2385 | 329.6117 | 219.2648 | 229.5576
534.2385 | 329.6136 | 219.3934 | 229.5895
535.2385 | 329.5471 | 219.5369 | 229.6405
536.2385 | 329.5636 | 219.6694 | 229.6872
537.2385 | 329.5638 | 219.8179 | 229.7445
538.2385 | 329.6123 | 219.9521 | 229.8003
539.2385 | 329.623 | 220.1072 | 229.8522
540.2385 | 329.616 | 220.2501 | 229.778
541.2385 | 329.6129 | 220.4002 | 229.8117
542.2385 | 329.5824 | 220.5444 | 229.9524
543.2385 | 329.5412 | 220.6977 | 230.0496
544.2385 | 329.4808 | 220.8575 | 230.1113
545.2385 | 329.4122 | 221.0061 | 230.1986
546.2385 | 329.3629 | 221.1593 | 230.2853
547.2385 | 329.3796 | 221.3189 | 230.3742
548.2385 | 329.2866 | 221.4469 | 230.4727
549.2385 | 329.2181 | 221.5731 | 230.5484
550.2385 | 329.1811 | 221.6938 | 230.6307
551.2385 | 329.135 | 221.8007 | 230.7145
552.2385 | 329.1136 | 221.9006 | 230.7941
553.2385 | 329.1493 | 222.0265 | 230.882
554.2385 | 329.1141 | 222.1361 | 230.9787
555.2385 | 329.0329 | 222.2538 | 231.0672
556.2385 | 328.9375 | 222.3325 | 231.1561
557.2385 | 328.9117 | 222.4164 | 231.2577
558.2385 | 328.8754 | 222.4969 | 231.375
559.2385 | 328.8654 | 222.6185 | 231.5012
560.2385 | 328.8213 | 222.737 | 231.6387
561.2385 | 328.802 | 222.8969 | 231.7861
562.2385 | 328.7676 | 223.0391 | 231.9323
563.2385 | 328.8152 | 223.1963 | 232.0862
564.2385 | 328.824 | 223.369 | 232.2291
565.2385 | 328.7926 | 223.5175 | 232.3937
566.2385 | 328.8733 | 223.6759 | 232.5478
567.2385 | 328.8841 | 223.8677 | 232.6896
568.2385 | 328.936 | 224.0549 | 232.8446
569.2385 | 328.9651 | 224.2398 | 232.9852
570.2385 | 329.011 | 224.3427 | 233.1326
571.2385 | 329.02 | 224.5325 | 233.2798
572.2385 | 329.0048 | 224.7292 | 233.4192
573.2385 | 329.0016 | 224.9322 | 233.5658
574.2385 | 329.0133 | 225.1371 | 233.7161
575.2385 | 329.0503 | 225.3484 | 233.8615
576.2385 | 329.1032 | 225.5305 | 234.0001
577.2385 | 329.1207 | 225.7545 | 234.1412
578.2385 | 329.1317 | 225.947 | 234.2835
579.2385 | 329.149 | 226.1531 | 234.4253
580.2385 | 329.1486 | 226.3477 | 234.5739