## Test Conditions
DESIREE-FIRE Test Number 33 - Circuit Simulator Data Only
Test Date: | 2009-08-12
DCSim DAQ Start Time | 17:02
DCSim Time for Synchronization | 17:39
Heat Source Synchronization | 2:02 | minutes:seconds
Heat Source DAQ Start Time | 17:37
Fire Time | 17:41
Offset | 0:40 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 2370 | seconds
Heat Source Offset | 0:04 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 227 | seconds
Heat Source Stop Time | 17:53
Test Duration | 0:12 | minutes:seconds
| 705 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
MOV 1 | PVC/PVC, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
MOV 2 | PVC/PVC, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | MOV-1_CT500 | MOV-1a_CT35_1_P | MOV-1a_CT35_2_N | MOV-1b_CT35_1_G | MOV-1b_CT35_2_R | MOV-1b_CT35_3_YO | MOV-1b_CT35_4_YC | MOV-2_CT500 | MOV-2a_CT35_1_P | MOV-2a_CT35_2_N | MOV-2b_CT35_1_G | MOV-2b_CT35_2_R | MOV-2b_CT35_3_YO | 2b_CT35_4_YC1 | MOV-1a_VT7_1_SP | MOV-1a_VTU_1_P | MOV-1a_VTU_2_N | MOV-1b_VT7_1_G | MOV-1b_VT7_2_R | MOV-1b_VT7_3_YO1 | MOV-1b_VT7_4_YC1 | MOV-2a_VT7_1_SP | MOV-2a_VTU_1_P | MOV-2a_VTU_2_N | MOV-2b_VT7_1_G | MOV-2b_VT7_2_R | 2b_VT7_3_YO1 | MOV-2b_VT7_4_YC1 | {MOV1} V(N) - V(Batt -) | {MOV1} V(P) - V(Batt +) | {MOV1} V(G) - V(Batt +) | {MOV1} V(R) - V(Batt -) | {MOV1} V(YC1) - V(Batt -) | {MOV1} V(YO1) - V(Batt -) | {MOV1} V(YC1) - V(N) | {MOV1} V(YO1) - V(N) | {MOV2} V(N) - V(Batt -) | {MOV2} V(P) - V(Batt +) | {MOV2} V(G) - V(Batt +) | {MOV2} V(R) - V(Batt -) | {MOV2} V(YC1) - V(Batt -) | {MOV2} V(YO1) - V(Batt -) | {MOV2} V(YC1) - V(N) | {MOV2} V(YO1) - V(N) | {MOV-1} V(R) - V(N) | {MOV-1} V(G) - V(N) | {MOV-2} V(R) - V(N) | {MOV-2} V(G) - V(N) | {MOV-1} V(P) - V(N) | {MOV-2} V(P) - V(N) | {MOV-1} V(P) - V(Batt -) | {MOV-2} V(P) - V(Batt -) | {MOV-1} V(N) - V(Batt +) | {MOV-2} V(N) - V(Batt +) | {MOV-1} V(G) - V(Batt -) | {MOV2} V(G) - V(Batt-) | {MOV1} V(SP) - V(Batt -) | {MOV2} V(SP) - V(Batt -)
-0.015625 | 123.6145 | -61.5417 | 61.7523 | -0.020447 | 0.0023669 | 0.00095711 | -0.00075838 | -0.00030984 | -0.0012838 | -0.0011664 | -0.021668 | 0.00034178 | 0.033259 | 0.030967 | -0.0012923 | -0.00035469 | -0.0027065 | -0.018311 | 61.8256 | -61.7981 | 61.6928 | 61.6837 | -61.7432 | 0.091553 | 0.10529 | 61.8118 | -61.6379 | 61.9263 | -0.65002 | -61.5509 | -61.1755 | -0.25635 | 0.073243 | -0.059509 | 123.2254 | 61.6333 | -0.20142 | 61.8896 | 0.054932 | -0.09613 | 0.05951 | 0.17395 | 60.8917 | 0.36621 | -0.009155 | 0.46234 | 0.086975 | 123.4818 | 123.4909 | 60.9879 | 123.5641 | 123.6237 | 123.4497 | 123.3673 | 123.3536 | -123.5504 | -123.3902 | 123.2346 | 123.468 | 61.5234 | 61.647
0.98438 | 123.5641 | -61.5372 | 61.8164 | -0.020447 | 0.0015125 | 0.00010251 | -0.00011758 | 0.00011756 | 0.00085237 | 0.0011834 | -0.027771 | -0.0015808 | 0.034541 | 0.032889 | -1.0744e-05 | 0.00071351 | 7.0452e-05 | 0.068665 | 61.8347 | -61.7981 | 61.6928 | 61.702 | -61.7294 | 0.1236 | 0.14648 | 61.8484 | -61.6379 | 61.8668 | -0.76904 | -61.6058 | -61.2213 | -0.26093 | 0.018311 | -0.1236 | 123.2391 | 61.6608 | -0.19226 | 61.9217 | 0.068665 | -0.10071 | 0.032044 | 0.050354 | 60.7681 | 0.31586 | -0.068665 | 0.41656 | 0.032043 | 123.5001 | 123.4909 | 60.8688 | 123.5046 | 123.6328 | 123.4863 | 123.3719 | 123.3856 | -123.6145 | -123.4543 | 123.23 | 123.4039 | 61.6058 | 61.6837
1.9844 | 123.6237 | -61.528 | 61.7615 | -0.043335 | 0.0017261 | 0.0013843 | -0.00075838 | 0.00097196 | 0.00021157 | -0.0028754 | -0.030823 | 0.00012818 | 0.034327 | 0.035239 | -0.00022434 | 0.00049991 | -0.0024929 | -0.009155 | 61.8164 | -61.8164 | 61.6882 | 61.6791 | -61.7615 | 0.073242 | 0.10986 | 61.8164 | -61.6287 | 61.9034 | -0.74158 | -61.5509 | -61.1938 | -0.28839 | 0.054931 | -0.073243 | 123.2071 | 61.6013 | -0.23346 | 61.8896 | 0.054931 | -0.10071 | 0.054931 | 0.14191 | 60.7864 | 0.33417 | -0.022888 | 0.43487 | 0.07782 | 123.4955 | 123.5046 | 60.8871 | 123.5321 | 123.6328 | 123.4451 | 123.3444 | 123.3444 | -123.5779 | -123.3902 | 123.2162 | 123.4314 | 61.5189 | 61.6379
2.9844 | 123.555 | -61.5143 | 61.7844 | -0.005188 | -0.0010511 | 0.00095711 | 0.0015914 | 0.00075836 | 0.00021157 | -0.00052556 | -0.033875 | 0.00034178 | 0.0339 | 0.034812 | -0.00086514 | -0.00035469 | 0.0011387 | 0.027466 | 61.8484 | -61.7844 | 61.7111 | 61.702 | -61.7249 | 0.11902 | 0.15564 | 61.821 | -61.6058 | 61.8805 | -0.76446 | -61.5875 | -61.2122 | -0.27008 | 0.064087 | -0.073242 | 123.2162 | 61.6333 | -0.21057 | 61.9034 | 0.059509 | -0.091553 | 0.036621 | 0.09613 | 60.7498 | 0.30212 | -0.073242 | 0.39368 | 0.018311 | 123.4863 | 123.4955 | 60.8414 | 123.4863 | 123.6328 | 123.4268 | 123.3627 | 123.3353 | -123.5687 | -123.3902 | 123.2254 | 123.3948 | 61.5417 | 61.6699
3.9844 | 123.5916 | -61.5692 | 61.7477 | 0.0024415 | 0.00044428 | 0.0011707 | -0.00075838 | 0.00011756 | -0.00085663 | 0.00075624 | -0.0064087 | -0.00051262 | 0.033045 | 0.034598 | 0.00063026 | 0.00071351 | -0.0020657 | -0.054932 | 61.8301 | -61.8027 | 61.6379 | 61.6196 | -61.7981 | 0.004578 | -0.009155 | 61.8118 | -61.6562 | 61.8713 | -0.78735 | -61.6196 | -61.2213 | -0.23346 | 0.082397 | -0.10986 | 123.1888 | 61.5738 | -0.22888 | 61.8073 | 0.004577 | -0.086975 | 0.064087 | 0.1236 | 60.7819 | 0.3479 | -0.050354 | 0.43488 | 0.036621 | 123.4222 | 123.4406 | 60.8688 | 123.5275 | 123.6328 | 123.468 | 123.3994 | 123.381 | -123.5504 | -123.4039 | 123.2071 | 123.4406 | 61.5143 | 61.5601
4.9844 | 123.5504 | -61.5372 | 61.7935 | -0.012817 | -0.0012647 | -0.00011109 | -0.00054478 | 0.00033116 | -0.00064303 | 0.0011834 | -0.024719 | 0.0022644 | 0.0339 | 0.039939 | 0.00041666 | -0.00035469 | 0.0015659 | 0.045776 | 61.8347 | -61.7661 | 61.7111 | 61.702 | -61.7111 | 0.11444 | 0.14191 | 61.8347 | -61.6058 | 61.8988 | -0.75073 | -61.5829 | -61.2076 | -0.22888 | 0.041199 | -0.082397 | 123.2391 | 61.6516 | -0.17395 | 61.8805 | 0.054931 | -0.068665 | 0.041199 | 0.10529 | 60.7864 | 0.32959 | -0.045777 | 0.39825 | 0.022888 | 123.468 | 123.4772 | 60.8551 | 123.5046 | 123.6008 | 123.4406 | 123.3719 | 123.3719 | -123.5596 | -123.3994 | 123.2483 | 123.436 | 61.5829 | 61.6791
5.9844 | 123.6008 | -61.5051 | 61.7569 | -0.012817 | 0.0012989 | -0.0011793 | 0.00030982 | 0.0013992 | 0.00085237 | -0.0033026 | 0.0027465 | -0.00051262 | 0.033259 | 0.031608 | 0.00020286 | 0.0013543 | 0.0011387 | 0.032043 | 61.8118 | -61.7706 | 61.734 | 61.7477 | -61.6882 | 0.11902 | 0.15106 | 61.8301 | -61.6058 | 61.8988 | -0.72784 | -61.5372 | -61.1893 | -0.2655 | 0.054932 | -0.022888 | 123.2529 | 61.6241 | -0.1831 | 61.8896 | 0.082398 | -0.10071 | 0.073242 | 0.14191 | 60.7773 | 0.31586 | -0.032043 | 0.41656 | 0.068665 | 123.5184 | 123.5046 | 60.878 | 123.5046 | 123.5825 | 123.436 | 123.317 | 123.3353 | -123.5275 | -123.3627 | 123.2391 | 123.4039 | 61.5372 | 61.6562
6.9844 | 123.4772 | -61.5509 | 61.8073 | 0.010071 | 0.00087168 | -0.00011109 | 0.00052342 | -0.0022324 | -0.00021583 | 0.00011544 | -0.039978 | -0.0028626 | 0.032405 | 0.033103 | -0.0019333 | 0.00071351 | 0.0024203 | 0.032043 | 61.8439 | -61.8164 | 61.5417 | 61.5646 | -61.5601 | 0.091553 | 0.11902 | 61.853 | -61.6379 | 61.8073 | -0.80566 | -61.6425 | -61.2625 | -0.2655 | 0.036621 | -0.2655 | 123.1155 | 61.6425 | -0.009156 | 61.908 | 0.25635 | -0.086975 | 0.045776 | 0 | 60.7452 | 0.28839 | -0.091553 | 0.37537 | -0.004578 | 123.381 | 123.3582 | 60.8322 | 123.4451 | 123.6603 | 123.4909 | 123.3948 | 123.4039 | -123.6237 | -123.4451 | 123.0927 | 123.3582 | 61.5829 | 61.6699
7.9844 | 123.6053 | -61.5509 | 61.7615 | -0.012817 | -0.0019055 | -0.00011109 | -0.00075838 | 0.0037492 | -0.00085663 | 0.00096984 | 0.0027465 | -0.00029902 | 0.033045 | 0.037376 | -0.0021469 | 0.0017817 | -0.0022793 | 0.036621 | 61.8118 | -61.7844 | 61.7157 | 61.7615 | -61.6974 | 0.14191 | 0.14648 | 61.8118 | -61.615 | 61.9263 | -0.74616 | -61.5463 | -61.1755 | -0.23346 | 0.050354 | -0.045777 | 123.3124 | 61.6928 | -0.14648 | 61.9263 | 0.086975 | -0.064087 | 0.050354 | 0.1648 | 60.8047 | 0.37537 | 0.004577 | 0.43945 | 0.068664 | 123.5458 | 123.5001 | 60.8688 | 123.5413 | 123.5962 | 123.4268 | 123.3627 | 123.3627 | -123.5458 | -123.3765 | 123.2666 | 123.4772 | 61.5875 | 61.6974
8.9844 | 123.4955 | -61.5509 | 61.8164 | -0.050964 | 0.00023068 | 0.00052971 | -0.00033118 | 0.00011756 | -0.0019248 | 0.001397 | -0.030823 | 0.00012818 | 0.032832 | 0.033317 | -0.00065154 | -0.00035469 | -0.0024929 | 0.036621 | 61.853 | -61.7889 | 61.6562 | 61.6425 | -61.7844 | -0.059509 | 0.15106 | 61.8622 | -61.6287 | 61.8484 | -0.82855 | -61.6837 | -61.29 | -0.23804 | 0.036621 | -0.16022 | 123.1934 | 61.4914 | -0.23346 | 61.7294 | 0.004577 | -0.07782 | 0.045777 | 0.032044 | 60.7224 | 0.26093 | -0.13275 | 0.33875 | -0.054932 | 123.4314 | 123.4451 | 60.8002 | 123.4772 | 123.642 | 123.4909 | 123.4039 | 123.4131 | -123.6053 | -123.4451 | 123.2071 | 123.3994 | 61.5875 | 61.702
9.9844 | 123.6008 | -61.528 | 61.7935 | -0.028076 | 0.00044428 | 0.00031611 | -0.0018266 | -0.0060776 | -0.00085663 | -0.00138 | -0.00030511 | 0.00098258 | 0.032618 | 0.027335 | -1.0744e-05 | 7.2706e-05 | 7.0452e-05 | 0.018311 | 61.8301 | -61.8256 | 61.7249 | 61.7477 | -61.702 | 0.11902 | 0.18768 | 61.821 | -61.6196 | 61.9034 | -0.737 | -61.5692 | -61.1618 | -0.29755 | 0.036621 | -0.068664 | 123.2758 | 61.647 | -0.17395 | 61.9446 | 0.1236 | -0.091553 | 0.027466 | 0.10986 | 60.791 | 0.36621 | -0.041199 | 0.45776 | 0.050354 | 123.5733 | 123.5504 | 60.8826 | 123.5229 | 123.6557 | 123.4406 | 123.3582 | 123.349 | -123.6191 | -123.4131 | 123.2529 | 123.4314 | 61.5463 | 61.7157
10.9844 | 123.4909 | -61.5372 | 61.7889 | 0.02533 | 0.0015125 | 0.00074331 | 0.00030982 | 0.0035354 | -0.00064303 | 0.00075624 | -0.027771 | 0.0016236 | 0.034541 | 0.037162 | -0.0012923 | 0.0011407 | -0.00014315 | 0.050354 | 61.8347 | -61.7844 | 61.6699 | 61.6699 | -61.7477 | 0.082397 | 0.10986 | 61.8713 | -61.6333 | 61.8027 | -0.78735 | -61.6287 | -61.2534 | -0.24719 | 0.045777 | -0.11902 | 123.2071 | 61.6196 | -0.21057 | 61.8668 | 0.036621 | -0.096131 | 0.082398 | 0.013733 | 60.7498 | 0.28381 | -0.091553 | 0.37994 | 0.004578 | 123.4543 | 123.4543 | 60.8459 | 123.436 | 123.6191 | 123.5046 | 123.3719 | 123.4085 | -123.5733 | -123.4222 | 123.2071 | 123.3398 | 61.5875 | 61.647
11.9844 | 123.6282 | -61.5234 | 61.7661 | -0.012817 | 0.00065788 | -0.00075189 | -0.0013992 | 0.0024674 | 0.0029886 | 0.00032904 | -0.0094605 | -0.00029902 | 0.0339 | 0.033958 | -0.0015059 | 0.00071351 | -0.0012111 | 0.027466 | 61.8347 | -61.8118 | 61.7157 | 61.7065 | -61.7203 | 0.12817 | 0.13733 | 61.8027 | -61.5921 | 61.9354 | -0.68665 | -61.5234 | -61.1389 | -0.28839 | 0.068665 | -0.050354 | 123.23 | 61.6516 | -0.19684 | 61.94 | 0.091553 | -0.068665 | 0.036621 | 0.16937 | 60.8368 | 0.38452 | 0 | 0.45319 | 0.068665 | 123.5184 | 123.5275 | 60.9055 | 123.5275 | 123.6465 | 123.3948 | 123.3582 | 123.3261 | -123.5779 | -123.3582 | 123.2391 | 123.4589 | 61.5509 | 61.6608
12.9844 | 123.4634 | -61.5692 | 61.8347 | 0.010071 | 0.00044428 | 0.00010251 | 0.00052342 | -0.00052344 | -0.00021583 | 0.0022516 | -0.055237 | 0.00034178 | 0.035609 | 0.034171 | 0.0021255 | -0.00099549 | 0.00092505 | 0.009155 | 61.8942 | -61.8347 | 61.6013 | 61.5829 | -61.821 | 0.045776 | 0.054932 | 61.8622 | -61.6333 | 61.7981 | -0.85144 | -61.6791 | -61.2808 | -0.2655 | 0.059509 | -0.23346 | 123.1522 | 61.615 | -0.25177 | 61.8805 | 0.013733 | -0.064087 | 0.027466 | -0.036621 | 60.7178 | 0.28839 | -0.10986 | 0.35248 | -0.045776 | 123.4177 | 123.436 | 60.7819 | 123.4314 | 123.7289 | 123.4955 | 123.4634 | 123.4314 | -123.6694 | -123.468 | 123.1705 | 123.3673 | 61.5784 | 61.6241
13.9844 | 123.6008 | -61.528 | 61.7844 | -0.028076 | 0.0015125 | -0.00096549 | -0.00011758 | -0.00073704 | 0.0017068 | -0.002021 | -0.04303 | -0.0022216 | 0.032832 | 0.033744 | -0.0015059 | -0.00035469 | 0.00049765 | 0.032043 | 61.8439 | -61.7981 | 61.7111 | 61.7157 | -61.7157 | 0.09613 | 0.17395 | 61.8164 | -61.6104 | 61.9034 | -0.72784 | -61.5555 | -61.1664 | -0.27008 | 0.059509 | -0.073242 | 123.2437 | 61.6241 | -0.18768 | 61.8942 | 0.082398 | -0.082398 | 0.032043 | 0.11902 | 60.8002 | 0.36163 | -0.027466 | 0.44403 | 0.054932 | 123.5138 | 123.5092 | 60.8826 | 123.5138 | 123.642 | 123.4268 | 123.3719 | 123.3444 | -123.5825 | -123.3948 | 123.2391 | 123.4314 | 61.5601 | 61.702
14.9844 | 123.4726 | -61.5692 | 61.821 | -0.005188 | -0.00041012 | 0.00095711 | -0.00075838 | 0.00011756 | -0.00085663 | 0.00011544 | -0.012512 | 0.00034178 | 0.032832 | 0.034171 | -0.00065154 | -0.00099549 | -0.00099755 | 0.086975 | 61.853 | -61.7752 | 61.6379 | 61.5967 | -61.8439 | 0.059509 | 0.064087 | 61.8622 | -61.6379 | 61.7981 | -0.83771 | -61.6791 | -61.29 | -0.20599 | 0.032043 | -0.18311 | 123.1659 | 61.6287 | -0.27466 | 61.8347 | -0.068664 | -0.068664 | 0.041199 | -0.022888 | 60.7315 | 0.27924 | -0.10986 | 0.3479 | -0.041199 | 123.3719 | 123.4131 | 60.8002 | 123.436 | 123.6282 | 123.5001 | 123.4222 | 123.4314 | -123.5962 | -123.4589 | 123.2071 | 123.3673 | 61.6562 | 61.6333
15.9844 | 123.6053 | -61.528 | 61.7798 | 0.010071 | -0.00083732 | 0.0015979 | -0.00054478 | 0.00011756 | -0.00064303 | 0.00075624 | 0.033264 | 0.0016236 | 0.032405 | 0.029044 | -0.0019333 | -0.0016363 | 0.00092505 | 0.045776 | 61.8301 | -61.7615 | 61.7249 | 61.7523 | -61.6653 | 0.10986 | 0.17395 | 61.8301 | -61.615 | 61.9034 | -0.72327 | -61.5646 | -61.1801 | -0.23346 | 0.050354 | -0.054931 | 123.2803 | 61.6379 | -0.13733 | 61.8713 | 0.096131 | -0.086975 | 0.050354 | 0.1236 | 60.8047 | 0.3479 | -0.036621 | 0.43487 | 0.050354 | 123.5138 | 123.4863 | 60.8917 | 123.5184 | 123.5916 | 123.4451 | 123.3582 | 123.3582 | -123.5413 | -123.3948 | 123.2529 | 123.4314 | 61.5738 | 61.702
17.0469 | 123.5779 | -61.5372 | 61.7661 | -0.035705 | -0.00041012 | 0.0024523 | 9.6222e-05 | -0.0026596 | -0.0012838 | 0.00054264 | 0.0057983 | 0.00076898 | 0.031336 | 0.032889 | -0.0021469 | -0.0020637 | 0.0024203 | -0.068665 | 61.8027 | -61.8118 | 61.6241 | 61.615 | -61.821 | 0 | -0.045776 | 61.8118 | -61.647 | 61.8484 | -0.81482 | -61.6608 | -61.235 | -0.27466 | 0.036621 | -0.14191 | 123.1522 | 61.5372 | -0.28381 | 61.8118 | -0.009155 | -0.10986 | 0.045777 | 0.082398 | 60.7224 | 0.30212 | -0.1236 | 0.41199 | -0.013733 | 123.4268 | 123.436 | 60.8322 | 123.4955 | 123.6145 | 123.4589 | 123.3398 | 123.349 | -123.5779 | -123.4131 | 123.1613 | 123.3856 | 61.4685 | 61.4914
17.9844 | 123.6145 | -61.528 | 61.8027 | 0.040589 | 0.00087168 | -0.00011109 | -0.00097198 | 0.00054476 | 0.00021157 | -0.0018072 | 0.0088501 | -0.00029902 | 0.035182 | 0.032462 | -0.0012923 | -0.0022773 | -0.0031339 | 0.027466 | 61.8256 | -61.7981 | 61.7249 | 61.7294 | -61.7157 | 0.12817 | 0.19226 | 61.8347 | -61.6196 | 61.8942 | -0.73242 | -61.5555 | -61.1755 | -0.27008 | 0.022889 | -0.077819 | 123.2574 | 61.6562 | -0.18768 | 61.9263 | 0.082398 | -0.091553 | 0.032044 | 0.091553 | 60.7956 | 0.35248 | -0.027466 | 0.44403 | 0.064087 | 123.5275 | 123.523 | 60.8871 | 123.5138 | 123.6237 | 123.4543 | 123.3536 | 123.3627 | -123.6008 | -123.4222 | 123.2529 | 123.4222 | 61.5555 | 61.7203
18.9844 | 123.5092 | -61.5372 | 61.8118 | -0.012817 | 0.00065788 | 0.00095711 | 0.00030982 | 0.0024674 | -0.00021583 | 0.0018242 | -0.012512 | -8.5416e-05 | 0.034754 | 0.029685 | -0.0027877 | 0.0015679 | -0.0012111 | 0.027466 | 61.8622 | -61.8073 | 61.6882 | 61.6516 | -61.7432 | 0.082397 | 0.1236 | 61.8484 | -61.6287 | 61.8027 | -0.78735 | -61.6379 | -61.2625 | -0.27008 | 0.050354 | -0.1236 | 123.1888 | 61.6196 | -0.20599 | 61.8896 | 0.064087 | -0.091553 | 0.036621 | -0.009156 | 60.7498 | 0.27466 | -0.10071 | 0.36621 | -0.009155 | 123.4589 | 123.4955 | 60.8414 | 123.4314 | 123.6694 | 123.4772 | 123.3994 | 123.3856 | -123.6191 | -123.4406 | 123.2254 | 123.3398 | 61.5646 | 61.6608
19.9844 | 123.6145 | -61.5143 | 61.7935 | 0.032959 | 0.0032215 | 0.0024523 | 0.00052342 | 0.00097196 | -0.0021384 | 0.0039606 | -0.0094605 | -8.5416e-05 | 0.032618 | 0.036521 | -0.00022434 | 0.00092711 | 0.00049765 | 0.036621 | 61.8347 | -61.7661 | 61.7157 | 61.7157 | -61.7111 | 0.10529 | 0.15564 | 61.8347 | -61.615 | 61.8988 | -0.71869 | -61.5646 | -61.1847 | -0.25177 | 0.041199 | -0.07782 | 123.23 | 61.6196 | -0.19684 | 61.8713 | 0.054931 | -0.10071 | 0.041199 | 0.10529 | 60.7956 | 0.32959 | -0.050354 | 0.4303 | 0.050354 | 123.4818 | 123.4818 | 60.8963 | 123.5138 | 123.6008 | 123.4497 | 123.349 | 123.349 | -123.5596 | -123.4085 | 123.23 | 123.4131 | 61.5509 | 61.6699
20.9844 | 123.4863 | -61.5692 | 61.8301 | 0.040589 | 0.00065788 | 0.00010251 | 0.00073702 | 0.00075836 | 0.00042517 | 0.00096984 | -0.052185 | 0.00034178 | 0.032618 | 0.035667 | -0.00065154 | 0.0011407 | 0.00049765 | 0 | 61.8759 | -61.821 | 61.6196 | 61.6013 | -61.8347 | 0.036621 | 0.041199 | 61.8896 | -61.6287 | 61.8073 | -0.84228 | -61.6882 | -61.3037 | -0.25177 | 0.045777 | -0.21057 | 123.1705 | 61.6058 | -0.2655 | 61.8576 | -0.013733 | -0.059509 | 0.059509 | -0.022888 | 60.7269 | 0.2655 | -0.11902 | 0.32501 | -0.059509 | 123.4222 | 123.4406 | 60.7864 | 123.436 | 123.6969 | 123.5184 | 123.4451 | 123.4589 | -123.6511 | -123.4589 | 123.1888 | 123.3765 | 61.5692 | 61.6104
21.9844 | 123.5825 | -61.5326 | 61.7889 | 0.032959 | 1.7082e-05 | 0.0013843 | -0.00097198 | -0.0011642 | 0.00085237 | -0.0026618 | 0.0088501 | 0.00012818 | 0.035609 | 0.033317 | -0.00065154 | 0.00028631 | 0.0017795 | 0.036621 | 61.8393 | -61.7981 | 61.7111 | 61.7294 | -61.7065 | 0.1236 | 0.16937 | 61.8164 | -61.6104 | 61.8896 | -0.72327 | -61.5601 | -61.1664 | -0.2655 | 0.050354 | -0.077819 | 123.262 | 61.6562 | -0.17395 | 61.9217 | 0.091553 | -0.07782 | 0.027466 | 0.10071 | 60.8093 | 0.36621 | -0.027466 | 0.44403 | 0.050354 | 123.5275 | 123.5092 | 60.8871 | 123.5001 | 123.6374 | 123.4268 | 123.3719 | 123.349 | -123.587 | -123.3994 | 123.2437 | 123.4222 | 61.5692 | 61.702
22.9844 | 123.4772 | -61.5646 | 61.8347 | -0.089111 | 0.0036487 | -0.00011109 | 0.0011642 | -0.0013778 | 0.0017068 | -0.0015936 | -0.033875 | 0.00055538 | 0.034113 | 0.033744 | 0.0019119 | 0.0019953 | 0.00028405 | 0.018311 | 61.8439 | -61.8301 | 61.647 | 61.6608 | -61.7935 | 0.050354 | 0.068665 | 61.8622 | -61.6287 | 61.8027 | -0.85144 | -61.6928 | -61.2854 | -0.2655 | 0.009155 | -0.18768 | 123.2254 | 61.615 | -0.22888 | 61.8805 | 0.036621 | -0.064087 | 0.027466 | -0.032044 | 60.7132 | 0.27924 | -0.12817 | 0.34332 | -0.064087 | 123.4909 | 123.4772 | 60.7773 | 123.4314 | 123.674 | 123.4909 | 123.4085 | 123.4268 | -123.6649 | -123.4634 | 123.2117 | 123.3673 | 61.5829 | 61.6333
24.0469 | 123.5596 | -61.5555 | 61.7523 | 0.063477 | 0.0030079 | 0.00095711 | 0.00052342 | -9.604e-05 | 0.0017068 | -0.00138 | -0.0033569 | -0.00094002 | 0.036891 | 0.029899 | -0.00086514 | -0.0012091 | -0.0014249 | -0.086975 | 61.8256 | -61.8027 | 61.6333 | 61.615 | -61.8256 | 0 | -0.050354 | 61.7981 | -61.6837 | 61.8484 | -0.8194 | -61.6379 | -61.2442 | -0.24719 | 0.073243 | -0.11902 | 123.1705 | 61.5555 | -0.27008 | 61.8027 | -0.022889 | -0.12817 | 0.045777 | 0.096131 | 60.7361 | 0.31128 | -0.082397 | 0.43945 | 0.045777 | 123.4177 | 123.436 | 60.8643 | 123.5321 | 123.6282 | 123.4818 | 123.381 | 123.3536 | -123.555 | -123.436 | 123.1888 | 123.4039 | 61.4685 | 61.5051
24.9844 | 123.5046 | -61.5601 | 61.8301 | 0.040589 | -0.00083732 | 0.00052971 | -0.0016128 | -0.00052344 | 0.0021342 | -0.00052556 | -0.030823 | 0.00034178 | 0.033045 | 0.034385 | -1.0744e-05 | -0.00099549 | -0.00078395 | 0.054932 | 61.8484 | -61.7935 | 61.6562 | 61.6516 | -61.7661 | 0.07782 | -0.022888 | 61.8256 | -61.615 | 61.821 | -0.82855 | -61.6653 | -61.2442 | -0.23346 | 0.018311 | -0.17395 | 123.2117 | 61.6379 | -0.20599 | 61.8713 | 0.027466 | -0.054931 | -0.004577 | -0.009155 | 60.7315 | 0.31586 | -0.10528 | 0.37079 | -0.050354 | 123.4451 | 123.4497 | 60.7864 | 123.436 | 123.642 | 123.4406 | 123.4085 | 123.3856 | -123.6237 | -123.4451 | 123.2162 | 123.381 | 61.615 | 61.5372
25.9844 | 123.5733 | -61.5234 | 61.7844 | 0.010071 | 0.00087168 | 0.00095711 | -0.0018266 | -0.0011642 | -0.002352 | -0.00073916 | 0.0088501 | -0.0013672 | 0.034113 | 0.031608 | -0.0010787 | -0.00035469 | 0.0022067 | 0.027466 | 61.8256 | -61.7844 | 61.7249 | 61.702 | -61.702 | 0.11444 | 0.16022 | 61.8301 | -61.6104 | 61.908 | -0.74616 | -61.5555 | -61.1801 | -0.26093 | 0.041199 | -0.059509 | 123.2254 | 61.6379 | -0.17853 | 61.8988 | 0.082398 | -0.086976 | 0.045776 | 0.1236 | 60.7773 | 0.34332 | -0.032044 | 0.4303 | 0.054932 | 123.4863 | 123.5092 | 60.8643 | 123.5184 | 123.6099 | 123.4406 | 123.349 | 123.3536 | -123.5687 | -123.3948 | 123.2483 | 123.4314 | 61.5509 | 61.6837
26.9844 | 123.4818 | -61.5555 | 61.8164 | 0.093994 | 0.0010853 | 0.00095711 | 0.0011642 | 0.0011856 | -0.00042943 | -9.8356e-05 | -0.04303 | 0.0016236 | 0.033259 | 0.029899 | 0.00063026 | -0.00099549 | 0.00049765 | -0.009155 | 61.8713 | -61.8393 | 61.6058 | 61.5646 | -61.8484 | 0.013733 | 0.032043 | 61.8805 | -61.615 | 61.8118 | -0.86517 | -61.6974 | -61.2762 | -0.28381 | 0.054932 | -0.21057 | 123.1201 | 61.5692 | -0.29297 | 61.853 | -0.009156 | -0.059509 | 0.064087 | -0.004577 | 60.6903 | 0.27924 | -0.14191 | 0.33874 | -0.082398 | 123.4039 | 123.4451 | 60.7498 | 123.4268 | 123.7106 | 123.4955 | 123.4268 | 123.436 | -123.6557 | -123.4314 | 123.1613 | 123.3673 | 61.5463 | 61.5875
27.9844 | 123.5367 | -61.5372 | 61.7844 | 0.0177 | 0.0021533 | -0.00011109 | 0.00073702 | -0.00073704 | 0.00021157 | -0.003089 | 0.0088501 | -0.00029902 | 0.033259 | 0.034171 | 0.0014847 | 7.2706e-05 | -0.00078395 | 0.041199 | 61.8301 | -61.7706 | 61.6791 | 61.6882 | -61.7294 | 0.10071 | 0.14648 | 61.821 | -61.6333 | 61.8668 | -0.77362 | -61.6241 | -61.2167 | -0.23346 | 0.045776 | -0.10529 | 123.2254 | 61.6379 | -0.19226 | 61.8713 | 0.041199 | -0.096131 | 0.036621 | 0.082397 | 60.7635 | 0.32043 | -0.086976 | 0.41657 | 0.009155 | 123.4589 | 123.4497 | 60.8597 | 123.5001 | 123.6008 | 123.4543 | 123.3673 | 123.3582 | -123.555 | -123.4177 | 123.2162 | 123.4039 | 61.5784 | 61.6837
28.9844 | 123.4818 | -61.5372 | 61.8164 | 0.010071 | 1.7082e-05 | 0.00095711 | -0.00054478 | -0.0026596 | -0.00085663 | -9.8356e-05 | -0.027771 | 0.00098258 | 0.033473 | 0.035026 | -0.00022434 | 0.00049991 | 0.0039157 | -0.027466 | 61.8896 | -61.8256 | 61.5875 | 61.5738 | -61.8393 | 0.022888 | 0.032043 | 61.8805 | -61.6425 | 61.7981 | -0.85144 | -61.6928 | -61.2671 | -0.28839 | 0.073242 | -0.22888 | 123.111 | 61.5601 | -0.30212 | 61.8484 | -0.013732 | -0.10529 | 0.064087 | -0.01831 | 60.6857 | 0.27008 | -0.15564 | 0.37537 | -0.050354 | 123.3994 | 123.4131 | 60.791 | 123.4406 | 123.7152 | 123.5229 | 123.4268 | 123.4177 | -123.642 | -123.4589 | 123.1247 | 123.3353 | 61.5097 | 61.5692
29.9844 | 123.6099 | -61.5097 | 61.7706 | -0.020447 | 0.0015125 | -0.00053829 | -0.00054478 | -0.0013778 | 0.0021342 | 0.00011544 | 0.027161 | 0.00034178 | 0.034327 | 0.027335 | -0.0017197 | 0.00092711 | -0.0018521 | 0.032043 | 61.821 | -61.7844 | 61.7432 | 61.7615 | -61.6837 | 0.11902 | 0.15564 | 61.8256 | -61.615 | 61.908 | -0.72784 | -61.5692 | -61.171 | -0.27466 | 0.050354 | -0.027466 | 123.2712 | 61.6287 | -0.17395 | 61.9034 | 0.10071 | -0.10529 | 0.054932 | 0.13733 | 60.7819 | 0.33875 | -0.059509 | 0.44403 | 0.045776 | 123.5458 | 123.5275 | 60.8871 | 123.5229 | 123.6053 | 123.4406 | 123.3307 | 123.3353 | -123.555 | -123.3856 | 123.2529 | 123.4177 | 61.5417 | 61.6653
30.9844 | 123.4863 | -61.5509 | 61.821 | -0.012817 | -0.0010511 | 0.00052971 | -0.00033118 | 0.00097196 | -2.232e-06 | 0.0016106 | 0.042419 | 0.0022644 | 0.034968 | 0.036735 | -0.0015059 | -0.0012091 | -0.0022793 | 0.022888 | 61.8622 | -61.7935 | 61.6379 | 61.6608 | -61.8439 | -0.036621 | 0.10071 | 61.8576 | -61.6379 | 61.8301 | -0.86975 | -61.6516 | -61.2442 | -0.24262 | 0.041199 | -0.18311 | 123.2117 | 61.5143 | -0.29297 | 61.7569 | -0.050354 | -0.086975 | 0.036621 | 0.009155 | 60.6812 | 0.3067 | -0.10071 | 0.39368 | -0.013733 | 123.4543 | 123.4314 | 60.7681 | 123.468 | 123.6557 | 123.4955 | 123.4131 | 123.4085 | -123.6145 | -123.4589 | 123.1888 | 123.381 | 61.5738 | 61.6516
31.9844 | 123.6191 | -61.5143 | 61.7706 | 0.0177 | 0.0010853 | -0.0011793 | -0.00054478 | -0.00095064 | -0.00021583 | -0.0018072 | 0.036316 | -0.0011536 | 0.035182 | 0.031394 | -0.0032149 | 7.2706e-05 | -0.00078395 | 0.009155 | 61.8073 | -61.7844 | 61.702 | 61.7386 | -61.7065 | 0.11444 | 0.17853 | 61.821 | -61.6196 | 61.9217 | -0.74158 | -61.5509 | -61.1526 | -0.27008 | 0.036621 | -0.068665 | 123.2529 | 61.6287 | -0.19226 | 61.8988 | 0.07782 | -0.10529 | 0.050354 | 0.15106 | 60.7727 | 0.36163 | -0.036621 | 0.46692 | 0.068665 | 123.5229 | 123.4863 | 60.878 | 123.5413 | 123.5916 | 123.4406 | 123.3215 | 123.3353 | -123.555 | -123.3902 | 123.2162 | 123.436 | 61.5234 | 61.6928
32.9844 | 123.5367 | -61.5372 | 61.8027 | -0.020447 | -0.00041012 | -0.00075189 | -0.0011856 | 0.0024674 | 0.00085237 | 0.001397 | -0.027771 | 0.00076898 | 0.033473 | 0.039512 | 0.0016983 | -0.00099549 | -0.0024929 | 0.041199 | 61.8301 | -61.7844 | 61.6699 | 61.6699 | -61.7477 | 0.10529 | 0.1236 | 61.8484 | -61.6241 | 61.9217 | -0.76446 | -61.6425 | -61.2305 | -0.24719 | 0.027466 | -0.13275 | 123.2071 | 61.6425 | -0.21057 | 61.8896 | 0.036621 | -0.086976 | 0.045777 | 0.11902 | 60.7727 | 0.3067 | -0.10529 | 0.39368 | -0.01831 | 123.4543 | 123.4543 | 60.8597 | 123.5458 | 123.6145 | 123.4726 | 123.3673 | 123.3856 | -123.587 | -123.4268 | 123.2071 | 123.4589 | 61.5784 | 61.6608
33.9844 | 123.5916 | -61.5005 | 61.7798 | -0.005188 | 0.0010853 | 0.00010251 | -0.0016128 | -0.00095064 | 0.0014932 | -0.00073916 | 0.030212 | -0.00072642 | 0.033045 | 0.030326 | 0.0012711 | 0.00028631 | 0.0013523 | 0.036621 | 61.8256 | -61.7889 | 61.6928 | 61.7203 | -61.7249 | 0.10986 | 0.16937 | 61.8118 | -61.6425 | 61.8988 | -0.72327 | -61.5417 | -61.1526 | -0.28839 | 0.045777 | -0.086975 | 123.2208 | 61.6104 | -0.22431 | 61.8988 | 0.064086 | -0.14191 | 0.032044 | 0.11902 | 60.7773 | 0.3479 | -0.041199 | 0.48981 | 0.10071 | 123.5092 | 123.4818 | 60.9192 | 123.5413 | 123.6145 | 123.4543 | 123.3261 | 123.3124 | -123.5687 | -123.4222 | 123.1934 | 123.3994 | 61.5372 | 61.6699
34.9844 | 123.4818 | -61.5646 | 61.8256 | -0.005188 | 0.0012989 | 0.0013843 | 0.00095062 | 0.00075836 | 0.00021157 | -0.00031196 | -0.012512 | -0.00072642 | 0.032618 | 0.033744 | 0.00063026 | -0.0012091 | 0.0011387 | 0.041199 | 61.8805 | -61.7889 | 61.5829 | 61.615 | -61.7477 | 0.045776 | 0.064087 | 61.8668 | -61.6333 | 61.7981 | -0.8606 | -61.7111 | -61.2854 | -0.2243 | 0.054931 | -0.24262 | 123.1796 | 61.6104 | -0.18311 | 61.8347 | 0.041198 | -0.068665 | 0.041198 | -0.027466 | 60.704 | 0.27924 | -0.14648 | 0.3479 | -0.07782 | 123.4039 | 123.3719 | 60.7727 | 123.4314 | 123.6694 | 123.5001 | 123.4451 | 123.4314 | -123.6145 | -123.4589 | 123.1476 | 123.3627 | 61.6058 | 61.6287
35.9844 | 123.6053 | -61.5005 | 61.7844 | -0.028076 | 0.0012989 | 0.00052971 | 0.0011642 | -0.00095064 | 0.001066 | -0.00031196 | 0.018005 | 0.00034178 | 0.034968 | 0.031394 | -0.00043794 | -0.0018499 | 0.0011387 | 0.059509 | 61.8393 | -61.8073 | 61.6974 | 61.7203 | -61.7249 | 0.10986 | 0.16937 | 61.8256 | -61.6379 | 61.9034 | -0.74158 | -61.5692 | -61.1755 | -0.3067 | 0.054931 | -0.086975 | 123.2208 | 61.6104 | -0.22431 | 61.9171 | 0.082397 | -0.13733 | 0.041199 | 0.11902 | 60.759 | 0.32501 | -0.068665 | 0.46234 | 0.068664 | 123.5275 | 123.5046 | 60.8963 | 123.5413 | 123.6465 | 123.4634 | 123.3398 | 123.3261 | -123.5916 | -123.4222 | 123.1979 | 123.4039 | 61.5601 | 61.6699
36.9844 | 123.4772 | -61.5372 | 61.8301 | -0.012817 | 0.0010853 | -0.00032469 | -0.00075838 | -0.0013778 | -0.0029928 | 0.0026788 | -0.0033569 | -0.0013672 | 0.0339 | 0.039512 | 0.00020286 | -0.00056829 | -0.00078395 | 0.027466 | 61.8576 | -61.8118 | 61.6104 | 61.6516 | -61.7615 | 0.050354 | 0.07782 | 61.853 | -61.6653 | 61.7935 | -0.87433 | -61.6882 | -61.2946 | -0.27466 | 0.027466 | -0.21973 | 123.1888 | 61.5875 | -0.2243 | 61.8622 | 0.050354 | -0.12817 | 0.022888 | -0.036621 | 60.6628 | 0.24261 | -0.15106 | 0.37079 | -0.022888 | 123.4634 | 123.4222 | 60.791 | 123.4589 | 123.6694 | 123.5184 | 123.3948 | 123.3902 | -123.642 | -123.4955 | 123.1476 | 123.3307 | 61.5646 | 61.615
37.9844 | 123.5825 | -61.5143 | 61.7615 | -0.035705 | 0.0021533 | 0.00074331 | -0.0013992 | -0.00073704 | -2.232e-06 | 0.00075624 | -0.0064087 | 0.00076898 | 0.033473 | 0.029258 | -0.0010787 | -0.00099549 | -0.00078395 | -0.013733 | 61.8256 | -61.8164 | 61.6699 | 61.6699 | -61.7752 | 0.050354 | 0.07782 | 61.821 | -61.6287 | 61.8896 | -0.75989 | -61.5738 | -61.1893 | -0.30212 | 0.064087 | -0.091553 | 123.1842 | 61.5646 | -0.26093 | 61.8668 | 0.041198 | -0.11444 | 0.059509 | 0.12817 | 60.7544 | 0.32501 | -0.05951 | 0.43945 | 0.054931 | 123.4863 | 123.4863 | 60.8688 | 123.5184 | 123.642 | 123.4497 | 123.3398 | 123.3353 | -123.5779 | -123.3902 | 123.1842 | 123.4039 | 61.5005 | 61.5921
38.9844 | 123.4772 | -61.5601 | 61.8301 | -0.012817 | -0.00083732 | 0.00010251 | 0.00073702 | 0.0013992 | -0.00064303 | 0.00096984 | -0.027771 | 0.0020508 | 0.036463 | 0.032889 | 0.00020286 | -0.00035469 | 0.0049839 | -0.027466 | 61.8759 | -61.8439 | 61.6058 | 61.5738 | -61.8439 | 0.009155 | 0.036621 | 61.8942 | -61.6013 | 61.8073 | -0.85602 | -61.702 | -61.29 | -0.28381 | 0.045777 | -0.2243 | 123.1339 | 61.5692 | -0.28381 | 61.853 | 0 | -0.041198 | 0.064087 | -0.022888 | 60.704 | 0.27008 | -0.14191 | 0.31128 | -0.10071 | 123.4177 | 123.4497 | 60.7452 | 123.4085 | 123.7198 | 123.4955 | 123.436 | 123.4543 | -123.674 | -123.4314 | 123.1659 | 123.3673 | 61.5326 | 61.5967
39.9844 | 123.5046 | -61.5738 | 61.821 | -0.005188 | -0.0014783 | 0.00010251 | 0.00095062 | -0.00052344 | -0.002352 | -0.00373 | -0.0094605 | -0.00094002 | 0.033045 | 0.034385 | 0.0010575 | 0.0011407 | -0.00035675 | 0.045776 | 61.853 | -61.7844 | 61.647 | 61.6516 | -61.7661 | 0.086975 | -0.036621 | 61.8301 | -61.6333 | 61.8256 | -0.86517 | -61.6562 | -61.2534 | -0.21057 | 0.032043 | -0.17395 | 123.2254 | 61.6608 | -0.19226 | 61.8713 | 0.018311 | -0.059509 | 0.009155 | 0.004578 | 60.7086 | 0.32043 | -0.082397 | 0.37994 | -0.022888 | 123.436 | 123.4314 | 60.7681 | 123.4589 | 123.6374 | 123.4634 | 123.4268 | 123.4039 | -123.6053 | -123.4543 | 123.2208 | 123.3994 | 61.6196 | 61.5372
40.9844 | 123.5001 | -61.5738 | 61.8576 | 0.048218 | 0.00065788 | -0.00075189 | 0.0013778 | 0.0013992 | -0.00085663 | 0.00075624 | -0.046082 | 0.00076898 | 0.033259 | 0.040366 | -0.0012923 | -0.00056829 | 0.00071145 | -0.027466 | 61.9034 | -61.8164 | 61.5967 | 61.5784 | -61.8256 | 0.022888 | 0.022888 | 61.853 | -61.6608 | 61.8118 | -0.8606 | -61.702 | -61.2808 | -0.24261 | 0.045776 | -0.26093 | 123.1522 | 61.5967 | -0.25177 | 61.8393 | -0.009156 | -0.086975 | -0.004578 | -0.045776 | 60.7132 | 0.29297 | -0.12817 | 0.37994 | -0.041198 | 123.3948 | 123.4131 | 60.8002 | 123.4726 | 123.7198 | 123.5138 | 123.4772 | 123.4268 | -123.674 | -123.5184 | 123.1705 | 123.3856 | 61.5463 | 61.5967
41.9844 | 123.587 | -61.5143 | 61.7935 | -0.050964 | -0.0016919 | 0.00052971 | -0.0013992 | 0.0028946 | 0.0025614 | -0.002021 | 0.051575 | -8.5416e-05 | 0.034113 | 0.031608 | -0.0012923 | -0.00035469 | 0.0026341 | 0.054932 | 61.8256 | -61.7752 | 61.7203 | 61.6974 | -61.7249 | 0.10986 | 0.14648 | 61.821 | -61.5921 | 61.8805 | -0.75531 | -61.5555 | -61.1847 | -0.26093 | 0.032044 | -0.073242 | 123.2117 | 61.6241 | -0.21057 | 61.8851 | 0.050354 | -0.07782 | 0.027466 | 0.086975 | 60.759 | 0.32959 | -0.041199 | 0.40741 | 0.036621 | 123.4726 | 123.4955 | 60.8368 | 123.4726 | 123.6008 | 123.4131 | 123.3398 | 123.3353 | -123.5687 | -123.3856 | 123.2346 | 123.3948 | 61.5692 | 61.6608
42.9844 | 123.4955 | -61.5692 | 61.8393 | 0.0177 | 1.7082e-05 | -0.0024609 | -0.0011856 | 0.0018266 | -0.0014974 | -0.00095276 | 0.0088501 | 0.0016236 | 0.032832 | 0.036948 | -0.00065154 | -0.00056829 | -0.0020657 | -0.009155 | 61.853 | -61.821 | 61.6013 | 61.5784 | -61.8164 | 0.022888 | 0.050354 | 61.8713 | -61.6516 | 61.7981 | -0.86517 | -61.6745 | -61.2854 | -0.25177 | 0.013733 | -0.23804 | 123.1476 | 61.5921 | -0.24719 | 61.8439 | 0.004578 | -0.082397 | 0.032044 | -0.041198 | 60.704 | 0.28381 | -0.10529 | 0.36621 | -0.022889 | 123.3994 | 123.4222 | 60.7864 | 123.4497 | 123.674 | 123.5229 | 123.4222 | 123.4406 | -123.6603 | -123.4909 | 123.1705 | 123.3673 | 61.5601 | 61.6196
43.9844 | 123.6008 | -61.5463 | 61.7798 | -0.028076 | -0.00019652 | -0.00011109 | -0.00075838 | -0.00030984 | -0.0014974 | 0.0018242 | 0.021057 | -0.0013672 | 0.035609 | 0.034385 | -0.0015059 | 0.0015679 | -0.0020657 | 0.022888 | 61.8347 | -61.7844 | 61.6974 | 61.7065 | -61.7111 | 0.11902 | 0.16022 | 61.821 | -61.6013 | 61.9125 | -0.71869 | -61.5509 | -61.1847 | -0.23804 | 0.054932 | -0.082397 | 123.2529 | 61.6653 | -0.16479 | 61.9034 | 0.073242 | -0.054931 | 0.041199 | 0.13275 | 60.8276 | 0.36163 | -0.004577 | 0.41656 | 0.050354 | 123.4909 | 123.4818 | 60.8826 | 123.5138 | 123.6191 | 123.4222 | 123.381 | 123.3673 | -123.5641 | -123.381 | 123.2437 | 123.4589 | 61.5692 | 61.7065
44.9844 | 123.4955 | -61.5738 | 61.8164 | 0.0177 | 1.7082e-05 | 0.00031611 | 0.00073702 | 0.00097196 | -0.00085663 | 0.0022516 | -0.039978 | 0.0018372 | 0.034113 | 0.030967 | -1.0744e-05 | 0.00071351 | -0.00099755 | -0.022888 | 61.8942 | -61.8347 | 61.5921 | 61.5692 | -61.8347 | 0.032043 | 0.032043 | 61.8759 | -61.6653 | 61.8118 | -0.86975 | -61.702 | -61.2854 | -0.26093 | 0.07782 | -0.2243 | 123.143 | 61.6058 | -0.26093 | 61.8668 | 0 | -0.091552 | 0.05951 | -0.004577 | 60.704 | 0.28839 | -0.12817 | 0.37994 | -0.036621 | 123.4039 | 123.4268 | 60.7956 | 123.4772 | 123.7289 | 123.5413 | 123.468 | 123.4497 | -123.6511 | -123.4818 | 123.1659 | 123.3856 | 61.5509 | 61.6058
45.9844 | 123.5962 | -61.5189 | 61.7798 | -0.020447 | 0.0030079 | 0.0022387 | -0.00054478 | -0.0043686 | 0.0019204 | -0.00095276 | 0.027161 | -0.00051262 | 0.031336 | 0.032462 | -0.00022434 | 0.00028631 | -0.0039883 | 0.032043 | 61.821 | -61.7935 | 61.6928 | 61.7249 | -61.7203 | 0.11902 | 0.15106 | 61.8073 | -61.6287 | 61.9125 | -0.72784 | -61.5646 | -61.1755 | -0.27466 | 0.041199 | -0.086975 | 123.2437 | 61.6379 | -0.20142 | 61.9125 | 0.073242 | -0.10986 | 0.027466 | 0.13275 | 60.791 | 0.34332 | -0.045776 | 0.45319 | 0.064087 | 123.5184 | 123.4863 | 60.9009 | 123.5413 | 123.6145 | 123.436 | 123.3398 | 123.3261 | -123.5733 | -123.4085 | 123.2117 | 123.4314 | 61.5509 | 61.6699
46.9844 | 123.4772 | -61.5646 | 61.821 | 0.0024415 | 0.0021533 | -0.0016065 | 0.0022324 | -0.0015914 | 0.00085237 | 0.00032904 | -0.064392 | -8.5416e-05 | 0.035822 | 0.033744 | -0.0010787 | -0.00056829 | 0.00028405 | -0.027466 | 61.8805 | -61.8164 | 61.5875 | 61.5646 | -61.8347 | 0.022888 | 0.022888 | 61.8576 | -61.6425 | 61.7981 | -0.87433 | -61.6837 | -61.2854 | -0.25177 | 0.059509 | -0.23346 | 123.1293 | 61.5875 | -0.27008 | 61.8393 | -0.018311 | -0.07782 | 0.036621 | -0.022888 | 60.6903 | 0.27924 | -0.11902 | 0.35706 | -0.041199 | 123.381 | 123.4039 | 60.7681 | 123.4406 | 123.6969 | 123.5001 | 123.4451 | 123.4222 | -123.6374 | -123.4634 | 123.1522 | 123.3627 | 61.5372 | 61.5875
47.9844 | 123.4909 | -61.5555 | 61.8164 | 0.055847 | 1.7082e-05 | -0.00096549 | 9.6222e-05 | 0.00011756 | -0.0014974 | -0.0018072 | 0.014954 | 0.0022644 | 0.035609 | 0.03118 | 0.0014847 | 0.0013543 | -0.0024929 | -0.009155 | 61.8576 | -61.7981 | 61.5829 | 61.5829 | -61.8073 | 0.068665 | 0.050354 | 61.8759 | -61.6379 | 61.7935 | -0.86517 | -61.6928 | -61.2854 | -0.24262 | 0.041199 | -0.23346 | 123.1384 | 61.6241 | -0.25177 | 61.8668 | -0.009155 | -0.082397 | 0.05951 | -0.022888 | 60.6903 | 0.27008 | -0.13733 | 0.35248 | -0.054932 | 123.381 | 123.381 | 60.7727 | 123.4314 | 123.6557 | 123.5138 | 123.4131 | 123.4314 | -123.6145 | -123.4543 | 123.1384 | 123.349 | 61.5463 | 61.6058
48.9844 | 123.5138 | -61.5463 | 61.821 | 0.040589 | 0.0017261 | -0.0028881 | -0.00054478 | -0.0026596 | -0.00021583 | 0.00032904 | -0.055237 | 0.00098258 | 0.0339 | 0.032035 | -0.0015059 | 7.2706e-05 | -0.0020657 | -0.013733 | 61.8988 | -61.8073 | 61.5967 | 61.5784 | -61.8118 | 0.013733 | 0.041199 | 61.853 | -61.6608 | 61.8301 | -0.84686 | -61.6653 | -61.2534 | -0.26093 | 0.07782 | -0.2243 | 123.1247 | 61.5601 | -0.2655 | 61.821 | -0.004578 | -0.11444 | 0.032043 | 0.009155 | 60.6995 | 0.29297 | -0.11902 | 0.40741 | -0.004577 | 123.3856 | 123.4039 | 60.8139 | 123.4909 | 123.7061 | 123.5138 | 123.4451 | 123.3994 | -123.6282 | -123.4818 | 123.143 | 123.3765 | 61.5326 | 61.5875
49.9844 | 123.587 | -61.528 | 61.821 | 0.0024415 | 0.0017261 | 0.0024523 | -0.00075838 | 0.0028946 | 0.002775 | -9.8356e-05 | 0.0088501 | 0.00076898 | 0.037318 | 0.034385 | 0.00041666 | -0.00078189 | -0.0012111 | 0.032043 | 61.8256 | -61.7798 | 61.6882 | 61.7157 | -61.734 | 0.10986 | 0.13275 | 61.8301 | -61.6241 | 61.8668 | -0.7782 | -61.6196 | -61.1526 | -0.25177 | 0.004578 | -0.13275 | 123.2437 | 61.6379 | -0.20599 | 61.8896 | 0.045776 | -0.096131 | 0.009155 | 0.045776 | 60.7498 | 0.37537 | -0.091553 | 0.4715 | 0.004578 | 123.4955 | 123.468 | 60.8459 | 123.4909 | 123.6053 | 123.4543 | 123.3536 | 123.3582 | -123.6008 | -123.4451 | 123.2162 | 123.3948 | 61.5601 | 61.6608
50.9844 | 123.5229 | -61.528 | 61.8164 | -0.020447 | 0.0012989 | 0.00010251 | 0.002446 | -0.0011642 | -2.232e-06 | -0.0011664 | -0.052185 | -8.5416e-05 | 0.034968 | 0.034171 | 0.00041666 | -0.0054815 | -0.0054837 | -0.018311 | 61.8942 | -61.8164 | 61.6058 | 61.5555 | -61.8256 | 0.009155 | 0.036621 | 61.8759 | -61.6379 | 62.0682 | -0.9613 | -61.6699 | -61.1984 | -0.28839 | 0.07782 | -0.21057 | 123.0835 | 61.5372 | -0.29755 | 61.8256 | -0.009156 | -0.10986 | 0.05951 | 0.25177 | 60.5667 | 0.32959 | -0.14191 | 0.43945 | -0.032044 | 123.3719 | 123.4222 | 60.6766 | 123.7061 | 123.7106 | 123.5138 | 123.4222 | 123.4039 | -123.6328 | -123.4543 | 123.1338 | 123.5962 | 61.5097 | 61.5646
51.9844 | 123.5138 | -61.528 | 61.7935 | 0.010071 | -0.00062372 | 0.00095711 | -0.00054478 | 0.0031082 | 0.0019204 | 0.0011834 | 0.024109 | -0.00029902 | 0.034327 | 0.029044 | 0.00084386 | -0.00035469 | -0.00057035 | 0.032043 | 61.8484 | -61.8027 | 61.6974 | 61.7111 | -61.7294 | 0.11902 | 0.14648 | 61.8347 | -61.6333 | 61.8622 | -0.77362 | -61.5875 | -61.1938 | -0.27466 | 0.054932 | -0.09613 | 123.2391 | 61.647 | -0.20142 | 61.9217 | 0.073242 | -0.10529 | 0.041199 | 0.068665 | 60.7544 | 0.33417 | -0.059509 | 0.43945 | 0.045777 | 123.5138 | 123.5001 | 60.8597 | 123.4955 | 123.6511 | 123.468 | 123.3765 | 123.3627 | -123.5962 | -123.4268 | 123.2254 | 123.3902 | 61.5601 | 61.6745
52.9844 | 123.4818 | -61.5555 | 61.821 | -0.005188 | 0.00044428 | -0.0018201 | -0.00011758 | -0.002446 | -0.002352 | -0.00095276 | -0.0094605 | 0.0011964 | 0.035182 | 0.029899 | -0.00043794 | -0.0020637 | -0.0020657 | -0.027466 | 61.8851 | -61.8164 | 61.5829 | 61.5829 | -61.8393 | 0.032043 | 0.032043 | 61.8439 | -61.6516 | 61.8027 | -0.86975 | -61.702 | -61.2762 | -0.26093 | 0.064087 | -0.23804 | 123.1384 | 61.5875 | -0.28381 | 61.8484 | -0.022888 | -0.09613 | 0.022888 | -0.018311 | 60.6857 | 0.27924 | -0.14648 | 0.37537 | -0.050354 | 123.3994 | 123.3994 | 60.7819 | 123.4543 | 123.7015 | 123.4955 | 123.4406 | 123.3994 | -123.6374 | -123.4726 | 123.1384 | 123.3582 | 61.528 | 61.5875
53.9844 | 123.4955 | -61.5463 | 61.8256 | 0.055847 | 0.0021533 | -0.00053829 | 0.00073702 | -9.604e-05 | 0.00063877 | 0.00054264 | 0.018005 | 0.0016236 | 0.034754 | 0.034171 | -0.0010787 | -0.0012091 | -0.0016385 | 0.032043 | 61.8622 | -61.8256 | 61.6241 | 61.6287 | -61.7981 | 0.054932 | 0.086975 | 61.8484 | -61.6287 | 61.8073 | -0.85144 | -61.6699 | -61.2717 | -0.27924 | 0.036621 | -0.20142 | 123.175 | 61.6013 | -0.25177 | 61.8805 | 0.027466 | -0.082397 | 0.022888 | -0.018311 | 60.6949 | 0.27466 | -0.1236 | 0.35706 | -0.041199 | 123.4543 | 123.4497 | 60.7773 | 123.436 | 123.6877 | 123.4772 | 123.4085 | 123.3948 | -123.6511 | -123.4543 | 123.1705 | 123.3536 | 61.5784 | 61.6333
54.9844 | 123.4314 | -61.5601 | 61.8484 | 0.040589 | 0.00044428 | -0.00053829 | -0.00075838 | 0.0031082 | -0.00064303 | -0.00031196 | -0.024719 | 0.0016236 | 0.032832 | 0.029471 | -0.00022434 | -0.00056829 | 0.0043431 | -0.013733 | 61.8988 | -61.8256 | 61.5967 | 61.5692 | -61.821 | 0.018311 | 0.027466 | 61.8668 | -61.6608 | 61.6562 | -0.83771 | -61.2442 | -61.1481 | -0.2655 | 0.050354 | -0.25177 | 123.1293 | 61.5784 | -0.26093 | 61.8439 | 0.004578 | -0.10071 | 0.01831 | -0.19226 | 60.7224 | 0.41199 | 0.31586 | 0.5127 | 0.41656 | 123.3948 | 123.4222 | 60.8231 | 123.317 | 123.7244 | 123.5275 | 123.4589 | 123.4268 | -123.674 | -123.5092 | 123.1567 | 123.2162 | 61.5463 | 61.5875
56 | 123.5184 | -61.6013 | 61.7798 | -0.043335 | 1.7082e-05 | 0.00010251 | -0.00097198 | 0.0033218 | 0.00085237 | -0.00095276 | -0.064392 | 0.00076898 | 0.034113 | 0.033103 | -0.00043794 | 0.0015679 | -0.0029201 | -0.10529 | 61.8256 | -61.8713 | 61.5509 | 61.496 | -61.9308 | -0.1236 | -0.16937 | 61.8073 | -61.6837 | 61.7752 | -0.94299 | -61.7661 | -61.2991 | -0.27008 | 0.045777 | -0.22888 | 123.0972 | 61.4777 | -0.32959 | 61.7477 | -0.059509 | -0.082398 | 0.027466 | -0.004577 | 60.6583 | 0.30212 | -0.1648 | 0.38452 | -0.082397 | 123.3673 | 123.4222 | 60.7407 | 123.4589 | 123.6969 | 123.4909 | 123.4268 | 123.4085 | -123.6511 | -123.4634 | 123.1522 | 123.3765 | 61.496 | 61.4319
56.9844 | 123.5001 | -61.5509 | 61.821 | 0.010071 | -0.00019652 | 0.00052971 | 0.0011642 | 0.0024674 | 0.00021157 | 0.00011544 | -0.030823 | 0.0018372 | 0.034541 | 0.029471 | 0.0016983 | -0.00056829 | -0.0024929 | -0.022888 | 61.8576 | -61.8164 | 61.5875 | 61.5601 | -61.8393 | 0.009155 | 0.004578 | 61.8668 | -61.6562 | 61.7981 | -0.86517 | -61.6837 | -61.2625 | -0.2655 | 0.036621 | -0.23346 | 123.111 | 61.5601 | -0.28839 | 61.8256 | -0.022888 | -0.10529 | 0.045776 | -0.022888 | 60.6857 | 0.28839 | -0.13275 | 0.39368 | -0.027466 | 123.3765 | 123.4039 | 60.791 | 123.4543 | 123.674 | 123.5229 | 123.4085 | 123.4177 | -123.6374 | -123.4772 | 123.1384 | 123.349 | 61.528 | 61.5555
57.9844 | 123.4909 | -61.5601 | 61.8164 | 0.032959 | 0.0023669 | 0.0020251 | 0.0015914 | -0.001805 | -0.00042943 | -0.003089 | -0.024719 | 0.0016236 | 0.034754 | 0.033744 | -0.00043794 | -0.00014089 | 0.0019931 | 0 | 61.8851 | -61.8256 | 61.5829 | 61.5601 | -61.8301 | 0.022888 | 0.041199 | 61.8347 | -61.6425 | 61.7981 | -0.87433 | -61.6791 | -61.2717 | -0.2655 | 0.068665 | -0.23346 | 123.1201 | 61.5829 | -0.27008 | 61.8484 | -0.004577 | -0.082397 | 0.018311 | -0.01831 | 60.6857 | 0.28839 | -0.11902 | 0.37079 | -0.036621 | 123.3856 | 123.4085 | 60.7681 | 123.4406 | 123.7106 | 123.4772 | 123.4451 | 123.3948 | -123.642 | -123.4589 | 123.143 | 123.3582 | 61.5601 | 61.6013
58.9844 | 123.5092 | -61.5555 | 61.8027 | 0.0024415 | 0.00023068 | 0.0013843 | 0.002446 | -0.001805 | -0.0010702 | 0.00075624 | -0.036926 | 0.00034178 | 0.033473 | 0.03353 | 0.0012711 | 0.00028631 | 0.0011387 | 0.004578 | 61.8805 | -61.7844 | 61.615 | 61.6287 | -61.821 | 0.013733 | 0.059509 | 61.821 | -61.6653 | 61.8301 | -0.84686 | -61.6837 | -61.235 | -0.22888 | 0.07782 | -0.18768 | 123.1842 | 61.5692 | -0.2655 | 61.7981 | -0.036621 | -0.10986 | 0.018311 | 0.027466 | 60.7086 | 0.32044 | -0.12817 | 0.4303 | -0.018311 | 123.4131 | 123.3994 | 60.8185 | 123.4955 | 123.6649 | 123.4863 | 123.436 | 123.3765 | -123.587 | -123.468 | 123.1705 | 123.3856 | 61.5601 | 61.615
59.9844 | 123.4772 | -61.5509 | 61.8347 | -0.043335 | 0.00065788 | -0.00075189 | -0.00011758 | -0.004155 | 0.00021157 | -0.0011664 | 0.030212 | -0.00072642 | 0.032618 | 0.031394 | 0.0025529 | -0.00056829 | 0.0028477 | 0.027466 | 61.8347 | -61.7981 | 61.647 | 61.647 | -61.7615 | 0.082397 | 0.10986 | 61.8439 | -61.647 | 61.8027 | -0.85144 | -61.6791 | -61.2534 | -0.24719 | 0 | -0.18768 | 123.1979 | 61.6333 | -0.21057 | 61.8805 | 0.036621 | -0.096131 | 0.009155 | -0.032044 | 60.6995 | 0.29755 | -0.12817 | 0.39368 | -0.032043 | 123.4451 | 123.4451 | 60.7956 | 123.4497 | 123.6328 | 123.4909 | 123.3856 | 123.3948 | -123.6328 | -123.4818 | 123.1979 | 123.3536 | 61.5784 | 61.6608
61 | 123.5687 | -61.5372 | 61.7477 | -0.081482 | 0.0030079 | 0.00031611 | 0.00030982 | -0.00073704 | 0.0051248 | -0.0022346 | 0.011902 | 0.00034178 | 0.034327 | 0.032249 | -0.0012923 | 0.00049991 | -0.00057035 | -0.027466 | 61.8118 | -61.8256 | 61.6287 | 61.6562 | -61.7981 | -0.018311 | -0.013733 | 61.7889 | -61.6241 | 61.8805 | -0.82398 | -61.6379 | -61.1984 | -0.28839 | 0.064087 | -0.11902 | 123.1934 | 61.5189 | -0.26093 | 61.8073 | 0.027466 | -0.086976 | 0.041198 | 0.13275 | 60.7132 | 0.33875 | -0.10071 | 0.42572 | -0.013732 | 123.4818 | 123.4543 | 60.8002 | 123.5046 | 123.6374 | 123.4131 | 123.349 | 123.3261 | -123.5733 | -123.3719 | 123.1659 | 123.4177 | 61.5097 | 61.5234
61.9844 | 123.5001 | -61.5646 | 61.8301 | 0.032959 | 0.0017261 | 0.0022387 | 0.0028732 | -0.0028732 | 0.00085237 | -0.00073916 | -0.0064087 | 0.00076898 | 0.033686 | 0.039939 | -0.0025741 | -0.00035469 | -0.0016385 | -0.032043 | 61.8713 | -61.8484 | 61.5738 | 61.5646 | -61.8256 | 0.018311 | 0.032043 | 61.8713 | -61.6653 | 61.7935 | -0.86975 | -61.6791 | -61.2762 | -0.28381 | 0.041199 | -0.25635 | 123.1293 | 61.5829 | -0.26093 | 61.8668 | 0.022888 | -0.10071 | 0.041199 | -0.036621 | 60.6949 | 0.28839 | -0.11444 | 0.3891 | -0.013733 | 123.4131 | 123.4222 | 60.7956 | 123.4589 | 123.7198 | 123.5367 | 123.436 | 123.436 | -123.6786 | -123.4955 | 123.1384 | 123.3582 | 61.5326 | 61.5967
62.9844 | 123.5184 | -61.5646 | 61.8027 | -0.035705 | -0.00083732 | -0.00011109 | 0.0026596 | 0.0024674 | 0.0012796 | 0.0018242 | -0.033875 | 0.0016236 | 0.032832 | 0.033958 | -0.0030013 | 0.0017817 | 0.00092505 | -0.004578 | 61.8851 | -61.853 | 61.6058 | 61.6013 | -61.7981 | 0.036621 | 0.082397 | 61.8484 | -61.6562 | 61.8484 | -0.82855 | -61.6653 | -61.2442 | -0.28839 | 0.082398 | -0.19684 | 123.1659 | 61.6013 | -0.23346 | 61.8896 | 0.054931 | -0.091553 | 0.045777 | 0.045777 | 60.7361 | 0.32043 | -0.10071 | 0.41199 | -0.009155 | 123.4543 | 123.4589 | 60.8276 | 123.5046 | 123.7381 | 123.5046 | 123.4497 | 123.4131 | -123.6557 | -123.4589 | 123.1705 | 123.4131 | 61.5601 | 61.647
63.9844 | 123.4863 | -61.5784 | 61.8118 | 0.040589 | 0.0015125 | 0.0024523 | -0.0011856 | -0.00030984 | 0.0025614 | -0.003089 | 0.014954 | 0.00055538 | 0.035822 | 0.036094 | 0.0010575 | -0.00056829 | 0.0017795 | -0.027466 | 61.9034 | -61.8073 | 61.5829 | 61.5784 | -61.821 | 0.027466 | 0.050354 | 61.8851 | -61.647 | 61.7752 | -0.87891 | -61.6882 | -61.29 | -0.22888 | 0.091552 | -0.22888 | 123.1567 | 61.6058 | -0.24262 | 61.8347 | -0.013733 | -0.068665 | 0.073242 | -0.036621 | 60.6995 | 0.28839 | -0.10986 | 0.35706 | -0.041198 | 123.3856 | 123.3902 | 60.7681 | 123.4222 | 123.7106 | 123.5321 | 123.4818 | 123.4634 | -123.6191 | -123.4589 | 123.1613 | 123.3536 | 61.5509 | 61.6287
64.9844 | 123.5275 | -61.5555 | 61.7935 | -0.020447 | 0.0019397 | 0.00052971 | -0.00097198 | 0.0022538 | -0.00021583 | -0.00052556 | -0.033875 | 0.0016236 | 0.03625 | 0.034812 | 0.00020286 | 0.00028631 | 0.0022067 | -0.009155 | 61.8713 | -61.8301 | 61.6196 | 61.5784 | -61.7798 | 0.036621 | 0.059509 | 61.853 | -61.6425 | 61.8301 | -0.83313 | -61.6745 | -61.2396 | -0.27466 | 0.07782 | -0.17395 | 123.1338 | 61.5921 | -0.2243 | 61.8668 | 0.050354 | -0.086975 | 0.059509 | 0.036621 | 60.7224 | 0.31586 | -0.11902 | 0.40283 | -0.032044 | 123.4085 | 123.4497 | 60.8093 | 123.4726 | 123.7015 | 123.4955 | 123.4268 | 123.4085 | -123.6237 | -123.436 | 123.175 | 123.3856 | 61.5463 | 61.615
66 | 123.5596 | -61.5738 | 61.734 | 0.048218 | 0.00087168 | 0.0011707 | 0.00052342 | -0.0020188 | 0.00085237 | -0.0015936 | 0.039368 | 0.00055538 | 0.033045 | 0.035026 | -0.00022434 | -0.00014089 | 0.0013523 | -0.07782 | 61.7889 | -61.7981 | 61.6241 | 61.6379 | -61.8027 | -0.018311 | -0.027466 | 61.7752 | -61.6425 | 61.8393 | -0.84686 | -61.6699 | -61.2305 | -0.2243 | 0.054931 | -0.10986 | 123.2117 | 61.5555 | -0.22888 | 61.7798 | -0.004577 | -0.068664 | 0.041199 | 0.10529 | 60.7269 | 0.34332 | -0.09613 | 0.41199 | -0.027466 | 123.436 | 123.4222 | 60.7956 | 123.4818 | 123.587 | 123.4177 | 123.3627 | 123.349 | -123.5321 | -123.3765 | 123.1979 | 123.4131 | 61.496 | 61.5463
66.9844 | 123.5092 | -61.5463 | 61.8164 | 0.02533 | 0.00065788 | 0.0022387 | -0.0016128 | 0.00075836 | -0.00021583 | 0.00075624 | -0.04303 | 0.00034178 | 0.034113 | 0.030753 | -0.00065154 | 0.0011407 | 0.0032749 | -0.013733 | 61.8805 | -61.8256 | 61.6104 | 61.5875 | -61.7889 | 0.036621 | 0.054932 | 61.8713 | -61.6425 | 61.8301 | -0.85602 | -61.6745 | -61.2488 | -0.27924 | 0.064087 | -0.20599 | 123.1338 | 61.5829 | -0.24261 | 61.8622 | 0.036622 | -0.09613 | 0.054932 | 0.013733 | 60.6903 | 0.29755 | -0.12817 | 0.39368 | -0.032044 | 123.4131 | 123.436 | 60.7864 | 123.4726 | 123.7061 | 123.5138 | 123.4268 | 123.4177 | -123.642 | -123.4589 | 123.1567 | 123.3765 | 61.5326 | 61.6013
67.9844 | 123.4909 | -61.5738 | 61.8027 | 0.071106 | -0.00019652 | 0.00031611 | 0.00052342 | -0.0011642 | -2.232e-06 | -0.00031196 | -0.033875 | 0.00034178 | 0.034968 | 0.031821 | 0.00041666 | -0.00056829 | 0.0011387 | -0.027466 | 61.8851 | -61.7889 | 61.5829 | 61.5509 | -61.821 | 0.022888 | 0.027466 | 61.8805 | -61.647 | 61.7844 | -0.88348 | -61.6837 | -61.2762 | -0.21515 | 0.082398 | -0.21973 | 123.1247 | 61.5967 | -0.24719 | 61.8118 | -0.032044 | -0.073242 | 0.07782 | -0.01831 | 60.6903 | 0.29755 | -0.10986 | 0.37079 | -0.036621 | 123.3398 | 123.3719 | 60.7635 | 123.4314 | 123.674 | 123.5275 | 123.4589 | 123.4543 | -123.5916 | -123.4497 | 123.1567 | 123.3582 | 61.5463 | 61.6013
68.9844 | 123.4314 | -61.5967 | 61.7798 | 0.0024415 | 0.00044428 | 0.00052971 | 0.0037276 | 0.0050308 | 0.0017068 | 0.0018242 | -0.046082 | 0.0016236 | 0.037745 | 0.038016 | -0.0010787 | 7.2706e-05 | 0.0022067 | -0.018311 | 61.8622 | -61.8027 | 61.5967 | 61.5921 | -61.8393 | -0.013733 | -0.004578 | 61.8484 | -61.6699 | 61.8027 | -0.91095 | -61.7981 | -61.3037 | -0.20599 | 0.082398 | -0.1831 | 123.1888 | 61.5829 | -0.24261 | 61.7889 | -0.036621 | -0.073242 | 0.068665 | 0.022888 | 60.6857 | 0.29297 | -0.20142 | 0.36621 | -0.12817 | 123.3948 | 123.3994 | 60.759 | 123.4726 | 123.6649 | 123.5184 | 123.4589 | 123.4451 | -123.5825 | -123.4497 | 123.1934 | 123.3994 | 61.5784 | 61.5921
69.9844 | 123.5229 | -61.5646 | 61.8164 | -0.005188 | -0.00041012 | -0.00096549 | 0.00073702 | 0.0039628 | 0.0014932 | 0.00032904 | -0.027771 | 0.0018372 | 0.032832 | 0.031608 | 0.00041666 | -0.00078189 | 7.0452e-05 | -0.022888 | 61.8805 | -61.821 | 61.5921 | 61.5921 | -61.8439 | 0.022888 | 0.050354 | 61.8713 | -61.6608 | 61.821 | -0.84228 | -61.6699 | -61.2442 | -0.25635 | 0.064087 | -0.2243 | 123.1567 | 61.5875 | -0.27924 | 61.8439 | -0.022888 | -0.096131 | 0.054932 | 0.004578 | 60.7224 | 0.32043 | -0.10529 | 0.41656 | -0.009155 | 123.4131 | 123.4131 | 60.8185 | 123.4818 | 123.7015 | 123.5321 | 123.4451 | 123.436 | -123.6374 | -123.4772 | 123.1567 | 123.3856 | 61.5417 | 61.615
71 | 123.5596 | -61.5509 | 61.7294 | -0.012817 | 1.7082e-05 | 0.00074331 | 0.00073702 | -0.0011642 | -0.0010702 | -0.0015936 | 0.0088501 | 0.00076898 | 0.034968 | 0.03054 | 0.0019119 | -0.00014089 | -0.0014249 | -0.059509 | 61.821 | -61.7798 | 61.6333 | 61.6425 | -61.7981 | -0.022888 | -0.013733 | 61.7844 | -61.6379 | 61.8622 | -0.82398 | -61.6333 | -61.2396 | -0.22888 | 0.091553 | -0.09613 | 123.1934 | 61.528 | -0.24719 | 61.7569 | -0.018311 | -0.086975 | 0.054932 | 0.13275 | 60.7269 | 0.31128 | -0.082398 | 0.39825 | 0.004577 | 123.4222 | 123.4131 | 60.8139 | 123.5001 | 123.6008 | 123.4222 | 123.3719 | 123.3353 | -123.5092 | -123.3673 | 123.1842 | 123.4131 | 61.4914 | 61.5372
71.9844 | 123.4909 | -61.5463 | 61.8164 | 0.055847 | 0.0021533 | 0.00052971 | -0.0011856 | 0.0022538 | 0.00042517 | 0.0011834 | 0.0088501 | 0.002478 | 0.034113 | 0.034598 | -0.00043794 | -0.00099549 | 0.0026341 | -0.018311 | 61.9034 | -61.8256 | 61.5646 | 61.5646 | -61.8118 | 0.032043 | 0.032043 | 61.8622 | -61.647 | 61.7935 | -0.88348 | -61.6928 | -61.2671 | -0.27924 | 0.086975 | -0.25177 | 123.111 | 61.5784 | -0.2655 | 61.8576 | 0.013733 | -0.10071 | 0.045777 | -0.022888 | 60.6628 | 0.27924 | -0.14648 | 0.37994 | -0.045776 | 123.3902 | 123.3902 | 60.7635 | 123.4406 | 123.7289 | 123.5092 | 123.4497 | 123.4085 | -123.642 | -123.4634 | 123.111 | 123.3398 | 61.528 | 61.5784
72.9844 | 123.5138 | -61.5875 | 61.7935 | -0.005188 | -0.00019652 | -0.00011109 | 9.6222e-05 | 0.0022538 | -2.232e-06 | 0.003106 | -0.058289 | 0.0018372 | 0.032832 | 0.035239 | -0.0023605 | 0.00071351 | 0.00028405 | -0.009155 | 61.8622 | -61.8347 | 61.6241 | 61.6196 | -61.821 | 0.009155 | 0.041199 | 61.8576 | -61.6562 | 61.821 | -0.86517 | -61.6791 | -61.2396 | -0.24719 | 0.068665 | -0.16937 | 123.2071 | 61.5967 | -0.23346 | 61.8439 | 0.013733 | -0.068665 | 0.064087 | 0.027466 | 60.7224 | 0.3479 | -0.091553 | 0.41656 | -0.022888 | 123.4543 | 123.4589 | 60.791 | 123.4772 | 123.6969 | 123.5138 | 123.4497 | 123.4451 | -123.6282 | -123.4497 | 123.2117 | 123.4085 | 61.5784 | 61.6287
73.9844 | 123.4955 | -61.5646 | 61.8027 | 0.071106 | -0.00062372 | -0.00011109 | 0.0020188 | -0.0020188 | -0.00064303 | -0.00031196 | -0.0094605 | 0.00076898 | 0.035395 | 0.029471 | -1.0744e-05 | -0.00014089 | -0.00078395 | -0.022888 | 61.8805 | -61.8027 | 61.5738 | 61.5646 | -61.8347 | 0.032043 | 0.036621 | 61.8851 | -61.6653 | 61.7889 | -0.87433 | -61.702 | -61.2808 | -0.23804 | 0.07782 | -0.22888 | 123.1293 | 61.5967 | -0.27008 | 61.8347 | -0.032044 | -0.10071 | 0.082398 | -0.013733 | 60.6903 | 0.28381 | -0.13733 | 0.38452 | -0.036621 | 123.3673 | 123.3765 | 60.791 | 123.4543 | 123.6832 | 123.5504 | 123.4451 | 123.4497 | -123.6053 | -123.468 | 123.1384 | 123.3536 | 61.5417 | 61.6013
74.9844 | 123.5229 | -61.5601 | 61.7935 | -0.005188 | 0.0012989 | -0.00011109 | 9.6222e-05 | 0.00097196 | 0.00085237 | 0.00032904 | -0.055237 | -0.00051262 | 0.033259 | 0.032889 | -0.00043794 | 7.2706e-05 | -0.00035675 | -0.022888 | 61.8347 | -61.8347 | 61.5967 | 61.6058 | -61.8347 | -0.009155 | 0.018311 | 61.8439 | -61.6562 | 61.7844 | -0.87891 | -61.702 | -61.2717 | -0.27466 | 0.041199 | -0.19684 | 123.1659 | 61.5509 | -0.27466 | 61.8256 | 0 | -0.09613 | 0.050354 | -0.009155 | 60.6812 | 0.28839 | -0.14191 | 0.38452 | -0.045776 | 123.4406 | 123.4314 | 60.7773 | 123.4406 | 123.6694 | 123.5001 | 123.3948 | 123.4039 | -123.6282 | -123.4497 | 123.1567 | 123.3444 | 61.5372 | 61.5784
75.9844 | 123.5504 | -61.5234 | 61.7981 | -0.020447 | -0.0010511 | 0.0011707 | -0.00033118 | 0.0016128 | -0.0014974 | -0.00095276 | 0.069885 | -0.00029902 | 0.035822 | 0.025413 | 0.0023393 | -0.0022773 | 7.0452e-05 | -0.068665 | 61.8118 | -61.8164 | 61.615 | 61.6287 | -61.7935 | 0.022888 | 0 | 61.8073 | -61.647 | 61.8576 | -0.79193 | -61.6058 | -61.1847 | -0.29297 | 0.013733 | -0.18311 | 123.1522 | 61.5463 | -0.27008 | 61.8393 | 0.022888 | -0.1236 | 0.009155 | 0.059509 | 60.7315 | 0.33875 | -0.082398 | 0.46234 | 0.041199 | 123.4451 | 123.4314 | 60.8551 | 123.5046 | 123.6282 | 123.4543 | 123.3353 | 123.3307 | -123.6145 | -123.4451 | 123.1384 | 123.381 | 61.4548 | 61.5234
76.9844 | 123.5092 | -61.5921 | 61.7844 | 0.02533 | 0.00044428 | 0.00074331 | 0.0020188 | 0.0018266 | 0.00021157 | 0.00096984 | -0.064392 | 0.00034178 | 0.033259 | 0.03588 | -0.0012923 | 0.0022089 | -0.0020657 | -0.009155 | 61.8622 | -61.8164 | 61.6104 | 61.6196 | -61.8164 | -0.018311 | 0.032043 | 61.8347 | -61.6562 | 61.8118 | -0.87891 | -61.6974 | -61.2762 | -0.2243 | 0.07782 | -0.17395 | 123.2117 | 61.5738 | -0.2243 | 61.7981 | 0 | -0.064087 | 0.050354 | 0.027466 | 60.7132 | 0.31586 | -0.10529 | 0.37994 | -0.041199 | 123.436 | 123.4268 | 60.7773 | 123.468 | 123.6786 | 123.4909 | 123.4543 | 123.4268 | -123.6008 | -123.4406 | 123.2025 | 123.4039 | 61.5829 | 61.6241
77.9844 | 123.4909 | -61.5646 | 61.8073 | -0.012817 | -0.0010511 | 0.00074331 | 0.0013778 | -0.003514 | -0.00021583 | 0.00032904 | -0.027771 | 0.00098258 | 0.034327 | 0.032249 | -0.0017197 | 7.2706e-05 | -0.00035675 | -0.022888 | 61.8668 | -61.8347 | 61.5784 | 61.5601 | -61.8118 | 0.022888 | 0.027466 | 61.8439 | -61.6516 | 61.8164 | -0.8606 | -61.6745 | -61.2625 | -0.27008 | 0.059509 | -0.22888 | 123.1247 | 61.5875 | -0.24719 | 61.8576 | 0.022888 | -0.086975 | 0.036621 | 0.009155 | 60.704 | 0.30212 | -0.10986 | 0.3891 | -0.022889 | 123.3948 | 123.4131 | 60.791 | 123.468 | 123.7015 | 123.4955 | 123.4314 | 123.4085 | -123.642 | -123.4589 | 123.143 | 123.381 | 61.5417 | 61.5921
78.9844 | 123.5046 | -61.5738 | 61.7889 | 0.010071 | 0.0045031 | 0.00010251 | 0.001805 | 0.00097196 | 0.0012796 | -0.00373 | -0.030823 | 0.00076898 | 0.030696 | 0.034598 | -0.00086514 | -0.00078189 | -0.00099755 | -0.013733 | 61.853 | -61.8073 | 61.6104 | 61.6058 | -61.821 | 0 | 0.054932 | 61.853 | -61.6287 | 61.821 | -0.88348 | -61.6837 | -61.2625 | -0.23346 | 0.064087 | -0.17853 | 123.1796 | 61.5738 | -0.24719 | 61.8073 | -0.013733 | -0.054931 | 0.064087 | 0.032044 | 60.6903 | 0.31128 | -0.10986 | 0.36621 | -0.054932 | 123.4131 | 123.4177 | 60.7452 | 123.4497 | 123.6603 | 123.4818 | 123.4268 | 123.4268 | -123.5962 | -123.4177 | 123.1842 | 123.3948 | 61.5601 | 61.6287
79.9844 | 123.5001 | -61.5692 | 61.821 | 0.040589 | -0.00062372 | 0.00010251 | 0.0015914 | -0.0013778 | -0.001711 | -9.8356e-05 | -0.00030511 | 0.0018372 | 0.035182 | 0.034812 | -0.00022434 | 0.0013543 | 0.0019931 | -0.022888 | 61.8851 | -61.8027 | 61.5692 | 61.5601 | -61.8347 | 0.027466 | 0.013733 | 61.8484 | -61.647 | 61.7889 | -0.86517 | -61.6745 | -61.2579 | -0.23346 | 0.064087 | -0.25177 | 123.1293 | 61.5967 | -0.2655 | 61.8301 | -0.032044 | -0.07782 | 0.027466 | -0.032044 | 60.704 | 0.31128 | -0.10529 | 0.3891 | -0.027466 | 123.3627 | 123.3719 | 60.7819 | 123.436 | 123.6877 | 123.4955 | 123.4543 | 123.4177 | -123.6237 | -123.468 | 123.1384 | 123.3582 | 61.5463 | 61.5829
80.9844 | 123.4909 | -61.5555 | 61.7889 | -0.020447 | 0.0017261 | 0.0013843 | 0.00095062 | 0.00075836 | 0.0012796 | -0.0015936 | -0.033875 | -0.0011536 | 0.032832 | 0.03118 | -0.00065154 | 0.0024225 | 0.0022067 | -0.036621 | 61.8484 | -61.8164 | 61.5967 | 61.5738 | -61.8576 | -0.050354 | -0.022888 | 61.8484 | -61.647 | 61.7981 | -0.93384 | -61.7249 | -61.3037 | -0.26093 | 0.05951 | -0.19226 | 123.1293 | 61.5051 | -0.30212 | 61.7661 | -0.041199 | -0.091553 | 0.05951 | 0.009156 | 60.6216 | 0.25177 | -0.16937 | 0.34332 | -0.07782 | 123.3902 | 123.4131 | 60.7132 | 123.4451 | 123.6649 | 123.4955 | 123.4039 | 123.4039 | -123.6053 | -123.436 | 123.1522 | 123.3536 | 61.5189 | 61.5326
81.9844 | 123.5184 | -61.5646 | 61.7889 | -0.005188 | 0.0010853 | -0.00011109 | -0.00011758 | 0.0041764 | -0.0010702 | -0.0024482 | -0.04303 | -0.0022216 | 0.035822 | 0.032462 | -0.0010787 | -0.00056829 | -0.0012111 | -0.004578 | 61.8759 | -61.821 | 61.6104 | 61.5463 | -61.7111 | 0.068665 | 0.073242 | 61.8668 | -61.647 | 61.8393 | -0.8606 | -61.6699 | -61.2122 | -0.25635 | 0.086976 | -0.17853 | 123.111 | 61.6333 | -0.14648 | 61.8896 | 0.10986 | -0.082398 | 0.07782 | 0.050354 | 60.704 | 0.35248 | -0.10529 | 0.43488 | -0.022888 | 123.3673 | 123.4314 | 60.7864 | 123.4863 | 123.6969 | 123.5138 | 123.4406 | 123.4314 | -123.6099 | -123.436 | 123.175 | 123.4039 | 61.5601 | 61.6379
82.9844 | 123.5092 | -61.5738 | 61.7752 | -0.005188 | 0.00087168 | 0.0015979 | 0.0011642 | -0.00030984 | -0.0021384 | -0.00095276 | -0.058289 | 0.00141 | 0.033259 | 0.032889 | -0.00022434 | -0.00035469 | -0.00035675 | -0.022888 | 61.8622 | -61.8439 | 61.5784 | 61.5875 | -61.8301 | -0.022888 | 0.004578 | 61.8301 | -61.6379 | 61.7981 | -0.89264 | -61.7065 | -61.2946 | -0.27008 | 0.086975 | -0.19684 | 123.1613 | 61.5509 | -0.25635 | 61.821 | 0.013733 | -0.064086 | 0.054931 | 0.022888 | 60.6812 | 0.27924 | -0.13275 | 0.34332 | -0.068665 | 123.4314 | 123.4222 | 60.7452 | 123.436 | 123.7061 | 123.468 | 123.436 | 123.4039 | -123.6191 | -123.4131 | 123.1522 | 123.3719 | 61.5509 | 61.5784
83.9844 | 123.5001 | -61.5738 | 61.7844 | -0.028076 | 0.00044428 | 0.00010251 | -0.00011758 | 0.0011856 | -0.00064303 | 0.00075624 | 0.0057983 | 0.00055538 | 0.033686 | 0.032889 | -1.0744e-05 | -0.00056829 | 7.0452e-05 | -0.018311 | 61.8805 | -61.8301 | 61.5875 | 61.5692 | -61.8393 | 0.013733 | 0.16937 | 61.853 | -61.6333 | 61.821 | -0.86975 | -61.6562 | -61.2534 | -0.25635 | 0.09613 | -0.19684 | 123.143 | 61.5875 | -0.2655 | 61.8439 | -0.009155 | -0.059509 | 0.068664 | 0.036621 | 60.704 | 0.32043 | -0.082397 | 0.37994 | -0.022888 | 123.3994 | 123.4177 | 60.7636 | 123.4543 | 123.7106 | 123.4863 | 123.4543 | 123.4268 | -123.6145 | -123.4177 | 123.1613 | 123.3948 | 61.5555 | 61.7432
84.9844 | 123.4772 | -61.5555 | 61.7844 | -0.012817 | 1.7082e-05 | -0.00011109 | 0.004155 | 0.00054476 | 0.0019204 | 0.001397 | -0.049133 | 0.00141 | 0.033473 | 0.029471 | -0.00043794 | 0.0017817 | 0.0015659 | -0.022888 | 61.853 | -61.8256 | 61.5921 | 61.5967 | -61.8301 | -0.009155 | 0.022888 | 61.821 | -61.6791 | 61.8027 | -0.88806 | -61.7249 | -61.2671 | -0.27008 | 0.068664 | -0.19226 | 123.1522 | 61.5463 | -0.27466 | 61.8164 | -0.004577 | -0.1236 | 0.036621 | 0.01831 | 60.6674 | 0.28839 | -0.16937 | 0.41199 | -0.045777 | 123.4222 | 123.4177 | 60.791 | 123.4818 | 123.6786 | 123.5001 | 123.4085 | 123.3765 | -123.6099 | -123.4634 | 123.1476 | 123.3582 | 61.5326 | 61.5784
85.9844 | 123.4863 | -61.5646 | 61.8164 | 0.040589 | -0.00083732 | -0.0016065 | -0.00075838 | 0.002681 | 0.00042517 | -0.00052556 | 0.0088501 | 0.002478 | 0.035609 | 0.030326 | 0.00063026 | 0.0013543 | 0.0034885 | -0.032043 | 61.9125 | -61.821 | 61.5601 | 61.5509 | -61.8484 | 0.009155 | 0.013733 | 61.8713 | -61.6562 | 61.7752 | -0.89264 | -61.6837 | -61.2671 | -0.25635 | 0.096131 | -0.25635 | 123.1155 | 61.5738 | -0.28381 | 61.8301 | -0.027466 | -0.091553 | 0.054932 | -0.041198 | 60.672 | 0.29755 | -0.11902 | 0.3891 | -0.027466 | 123.3719 | 123.381 | 60.7635 | 123.4314 | 123.7335 | 123.5275 | 123.4772 | 123.436 | -123.6374 | -123.4726 | 123.1247 | 123.3398 | 61.5326 | 61.5784
86.9844 | 123.5321 | -61.5738 | 61.7661 | -0.058594 | -0.00083732 | 0.0024523 | 0.0028732 | -0.00052344 | 0.00021157 | 0.0022516 | -0.030823 | -0.00094002 | 0.033259 | 0.033103 | 0.00041666 | 7.2706e-05 | 0.0011387 | -0.013733 | 61.8759 | -61.8164 | 61.5921 | 61.615 | -61.8164 | -0.013733 | 0.018311 | 61.8301 | -61.6379 | 61.8118 | -0.88348 | -61.6928 | -61.2625 | -0.24261 | 0.10986 | -0.17395 | 123.1888 | 61.5601 | -0.24261 | 61.8027 | 0 | -0.064086 | 0.064087 | 0.045777 | 60.6903 | 0.31128 | -0.11902 | 0.37537 | -0.054932 | 123.4314 | 123.4085 | 60.7544 | 123.4497 | 123.6923 | 123.468 | 123.4497 | 123.4039 | -123.5825 | -123.4039 | 123.1659 | 123.3856 | 61.5601 | 61.5921
87.9844 | 123.5229 | -61.5784 | 61.7706 | -0.066223 | 0.00065788 | 0.00074331 | 0.0013778 | 0.0050308 | -0.0014974 | -0.0011664 | -0.021668 | 0.00055538 | 0.033473 | 0.032889 | 0.00041666 | 0.00028631 | 0.0011387 | -0.009155 | 61.853 | -61.8301 | 61.6013 | 61.6104 | -61.7981 | 0.032043 | 0.041199 | 61.8484 | -61.6379 | 61.8301 | -0.86517 | -61.6745 | -61.2305 | -0.25177 | 0.082397 | -0.16937 | 123.1888 | 61.6104 | -0.21973 | 61.8622 | 0.032043 | -0.059509 | 0.07782 | 0.059509 | 60.7132 | 0.3479 | -0.096131 | 0.40741 | -0.036622 | 123.4406 | 123.4314 | 60.7727 | 123.468 | 123.6832 | 123.4863 | 123.4314 | 123.4268 | -123.6008 | -123.4085 | 123.1796 | 123.4085 | 61.5692 | 61.6196
88.9844 | 123.4955 | -61.5738 | 61.7935 | -0.020447 | -0.00062372 | -0.00032469 | 0.00095062 | 0.0011856 | 0.0023478 | 0.0016106 | -0.012512 | 0.00012818 | 0.0339 | 0.035026 | -0.0012923 | 0.00049991 | -0.00099755 | -0.036621 | 61.8622 | -61.8164 | 61.5875 | 61.5692 | -61.853 | -0.054932 | -0.022888 | 61.8439 | -61.6653 | 61.7615 | -0.91095 | -61.6928 | -61.2625 | -0.24261 | 0.068665 | -0.20599 | 123.143 | 61.5189 | -0.27923 | 61.7615 | -0.036621 | -0.091552 | 0.050354 | -0.032043 | 60.6628 | 0.31128 | -0.11902 | 0.40283 | -0.027466 | 123.3856 | 123.4039 | 60.7544 | 123.4268 | 123.6786 | 123.5092 | 123.436 | 123.4177 | -123.6099 | -123.4589 | 123.1613 | 123.3353 | 61.5372 | 61.5509
89.9844 | 123.5458 | -61.5601 | 61.8073 | 0.071106 | 0.0010853 | 0.00074331 | 9.6222e-05 | 0.0018266 | 0.0036294 | 0.00054264 | 0.0027465 | -0.00051262 | 0.033045 | 0.034812 | 0.00063026 | -0.0016363 | 0.0017795 | -0.036621 | 61.853 | -61.8256 | 61.5921 | 61.5829 | -61.8118 | 0.032043 | 0.068665 | 61.8393 | -61.647 | 61.8164 | -0.85602 | -61.6608 | -61.235 | -0.2655 | 0.045776 | -0.21515 | 123.143 | 61.5921 | -0.25177 | 61.8576 | 0.013733 | -0.086975 | 0.032043 | 0.009155 | 60.704 | 0.32501 | -0.10071 | 0.41199 | -0.013733 | 123.4085 | 123.4177 | 60.791 | 123.4634 | 123.6786 | 123.4863 | 123.4131 | 123.3994 | -123.6328 | -123.4543 | 123.1522 | 123.3765 | 61.5234 | 61.6287
90.9844 | 123.4955 | -61.5555 | 61.7935 | 0.0177 | -0.00062372 | 0.00031611 | 0.00052342 | 0.0013992 | 0.00042517 | -0.0018072 | -0.024719 | 0.00055538 | 0.034327 | 0.03588 | -0.00043794 | 7.2706e-05 | -0.00014315 | -0.032043 | 61.8393 | -61.8439 | 61.5967 | 61.6013 | -61.8256 | -0.050354 | -0.018311 | 61.8256 | -61.647 | 61.8439 | -1.0529 | -61.7386 | -61.1984 | -0.28839 | 0.045776 | -0.19684 | 123.1567 | 61.5051 | -0.27008 | 61.7935 | 0.01831 | -0.091553 | 0.032044 | 0.050354 | 60.5026 | 0.35706 | -0.1831 | 0.44861 | -0.091552 | 123.4451 | 123.4406 | 60.5942 | 123.4909 | 123.6832 | 123.4726 | 123.3948 | 123.381 | -123.6374 | -123.4406 | 123.1522 | 123.3994 | 61.5234 | 61.5372
91.9844 | 123.5092 | -61.5601 | 61.8164 | 0.13214 | -0.00019652 | 0.00010251 | 0.0020188 | -0.0020188 | 0.001066 | -0.0035162 | -0.0064087 | 0.0033326 | 0.034541 | 0.026481 | -0.00043794 | -0.00078189 | -0.0016385 | -0.10986 | 61.8896 | -61.8164 | 61.5921 | 61.5692 | -61.7981 | 0 | 0.032043 | 61.853 | -61.6379 | 61.8027 | -0.86517 | -61.6699 | -61.2259 | -0.25635 | 0.073242 | -0.2243 | 123.1293 | 61.5601 | -0.23804 | 61.8164 | 0.01831 | -0.077819 | 0.036621 | -0.013733 | 60.6949 | 0.33417 | -0.10986 | 0.41199 | -0.032044 | 123.3856 | 123.4085 | 60.7727 | 123.4406 | 123.7061 | 123.4909 | 123.4497 | 123.4131 | -123.6328 | -123.4543 | 123.1522 | 123.3627 | 61.4502 | 61.5921
92.9844 | 123.4589 | -61.5875 | 61.7798 | 0.063477 | 0.00023068 | 0.00095711 | 0.0020188 | 0.002681 | -0.00064303 | 0.00032904 | -0.04303 | 0.0016236 | 0.036463 | 0.04058 | -0.0012923 | 7.2706e-05 | -0.0035611 | -0.068665 | 61.853 | -61.8256 | 61.5738 | 61.5601 | -61.8668 | -0.073242 | -0.059509 | 61.853 | -61.6882 | 61.7661 | -0.92926 | -61.7569 | -61.3083 | -0.23804 | 0.073242 | -0.20599 | 123.1476 | 61.5143 | -0.27924 | 61.7523 | -0.041198 | -0.10071 | 0.073242 | -0.013733 | 60.6583 | 0.27923 | -0.16937 | 0.37994 | -0.068665 | 123.3856 | 123.3994 | 60.759 | 123.4543 | 123.6786 | 123.5413 | 123.4406 | 123.4406 | -123.6053 | -123.468 | 123.1613 | 123.3536 | 61.5189 | 61.528
93.9844 | 123.5367 | -61.5555 | 61.8118 | 0.040589 | 0.00065788 | -0.00053829 | -0.00033118 | 0.0018266 | -0.00042943 | -0.00095276 | -0.0094605 | 0.00098258 | 0.036891 | 0.035239 | -0.0010787 | -0.0012091 | -0.0035611 | -0.032043 | 61.8713 | -61.8027 | 61.5372 | 61.5189 | -61.821 | 0.013733 | 0.018311 | 61.8484 | -61.6608 | 61.7935 | -0.86975 | -61.6699 | -61.2625 | -0.24719 | 0.059509 | -0.27466 | 123.0743 | 61.5692 | -0.2655 | 61.8164 | -0.018311 | -0.10529 | 0.036621 | -0.018311 | 60.6857 | 0.29297 | -0.11444 | 0.39825 | -0.009155 | 123.3215 | 123.3398 | 60.791 | 123.4543 | 123.674 | 123.5092 | 123.4268 | 123.4039 | -123.6145 | -123.4726 | 123.0927 | 123.349 | 61.5234 | 61.5738
94.9844 | 123.4726 | -61.5829 | 61.7889 | -0.028076 | -0.0014783 | -0.00053829 | 0.0011642 | 0.0041764 | -0.0029928 | -0.00073916 | 0.0057983 | 0.0016236 | 0.034541 | 0.034598 | 0.00020286 | -0.00035469 | 0.0015659 | -0.050354 | 61.8484 | -61.8439 | 61.5738 | 61.5692 | -61.853 | -0.054932 | -0.045776 | 61.821 | -61.6608 | 61.7661 | -0.9201 | -61.734 | -61.29 | -0.26093 | 0.05951 | -0.21515 | 123.1522 | 61.528 | -0.27008 | 61.7889 | -0.009155 | -0.07782 | 0.032044 | -0.022888 | 60.6628 | 0.29297 | -0.15106 | 0.37079 | -0.073242 | 123.4131 | 123.4177 | 60.7407 | 123.4268 | 123.6923 | 123.4818 | 123.4314 | 123.4039 | -123.6328 | -123.4497 | 123.1567 | 123.349 | 61.5326 | 61.5372
95.9844 | 123.5367 | -61.5738 | 61.8073 | 0.093994 | 0.0021533 | 0.00074331 | -0.0011856 | -0.0020188 | 0.0012796 | -0.00052556 | 0.0057983 | 0.00098258 | 0.033473 | 0.029258 | -0.0012923 | -0.00099549 | 0.0013523 | -0.004578 | 61.8622 | -61.821 | 61.6104 | 61.5967 | -61.8027 | 0.041199 | 0.064087 | 61.8622 | -61.6196 | 61.8301 | -0.8606 | -61.6653 | -61.2305 | -0.24719 | 0.054932 | -0.19684 | 123.1705 | 61.615 | -0.22888 | 61.8622 | 0.018311 | -0.045776 | 0.054932 | 0.022888 | 60.7132 | 0.34332 | -0.091552 | 0.3891 | -0.045776 | 123.4177 | 123.4314 | 60.759 | 123.4497 | 123.6832 | 123.4818 | 123.436 | 123.436 | -123.6282 | -123.4268 | 123.1842 | 123.4039 | 61.5692 | 61.6379
96.9844 | 123.4863 | -61.5738 | 61.8027 | -0.028076 | 0.0025805 | 0.00052971 | 0.0015914 | -9.604e-05 | 0.00063877 | -0.00031196 | -0.027771 | -0.00029902 | 0.034327 | 0.035026 | -0.0019333 | -0.0012091 | -0.0014249 | 0.013733 | 61.853 | -61.8256 | 61.5829 | 61.5829 | -61.8347 | -0.022888 | -0.004578 | 61.8393 | -61.6562 | 61.7706 | -0.91095 | -61.7294 | -61.2854 | -0.25177 | 0.050354 | -0.21973 | 123.1567 | 61.5509 | -0.26093 | 61.8027 | -0.009155 | -0.082397 | 0.036621 | -0.032043 | 60.6628 | 0.28839 | -0.15564 | 0.37079 | -0.073242 | 123.4085 | 123.4085 | 60.7452 | 123.4268 | 123.6786 | 123.4955 | 123.4268 | 123.4131 | -123.6282 | -123.4589 | 123.1567 | 123.3444 | 61.5875 | 61.5692
97.9844 | 123.5367 | -61.5601 | 61.7844 | -0.012817 | -0.0010511 | -0.0018201 | 0.00073702 | 0.0020402 | -2.232e-06 | -0.00052556 | -0.0064087 | 0.00034178 | 0.034541 | 0.031821 | -0.00065154 | 0.00049991 | -0.0012111 | -0.036621 | 61.8668 | -61.8118 | 61.6104 | 61.5921 | -61.7981 | 0.032043 | 0.059509 | 61.8622 | -61.6196 | 61.821 | -0.84686 | -61.6745 | -61.2259 | -0.25177 | 0.082397 | -0.17395 | 123.1522 | 61.5921 | -0.23804 | 61.8439 | 0.013733 | -0.059509 | 0.07782 | 0.036621 | 60.7132 | 0.33417 | -0.11444 | 0.39368 | -0.054932 | 123.4039 | 123.4222 | 60.7727 | 123.4406 | 123.6786 | 123.4818 | 123.4268 | 123.4222 | -123.5962 | -123.4039 | 123.1705 | 123.381 | 61.5234 | 61.6196
98.9844 | 123.4863 | -61.5646 | 61.7889 | 0.040589 | 0.00087168 | 0.00095711 | 0.0050094 | -0.001805 | 0.0012796 | -0.0022346 | -0.036926 | 0.00076898 | 0.032405 | 0.029471 | -0.00022434 | 0.00071351 | 0.0015659 | -0.022888 | 61.8622 | -61.8393 | 61.5967 | 61.5875 | -61.7981 | -0.027466 | 0.009155 | 61.8393 | -61.647 | 61.7798 | -0.89264 | -61.7157 | -61.2762 | -0.27466 | 0.073243 | -0.19226 | 123.1522 | 61.5372 | -0.23346 | 61.8118 | 0.041198 | -0.082398 | 0.050354 | -0.009155 | 60.672 | 0.28839 | -0.15106 | 0.37079 | -0.068664 | 123.4268 | 123.436 | 60.7544 | 123.4268 | 123.7015 | 123.4863 | 123.4268 | 123.4039 | -123.6282 | -123.436 | 123.1613 | 123.3444 | 61.5417 | 61.5738
99.9844 | 123.5321 | -61.5601 | 61.7981 | 0.040589 | -0.0019055 | 0.00074331 | 0.00030982 | 0.0020402 | 0.001066 | -0.0018072 | 0.024109 | 0.00012818 | 0.033686 | 0.03353 | -0.00043794 | -0.00056829 | -0.00014315 | -0.018311 | 61.8942 | -61.8118 | 61.5829 | 61.5829 | -61.8027 | 0.004578 | 0.027466 | 61.8576 | -61.6287 | 61.821 | -0.85602 | -61.6791 | -61.235 | -0.25177 | 0.09613 | -0.21515 | 123.143 | 61.5646 | -0.24261 | 61.8164 | 0.009156 | -0.068664 | 0.059509 | 0.022888 | 60.704 | 0.32501 | -0.11902 | 0.39368 | -0.050354 | 123.3948 | 123.3948 | 60.7727 | 123.4497 | 123.7061 | 123.4863 | 123.4543 | 123.4177 | -123.6099 | -123.4268 | 123.143 | 123.381 | 61.5417 | 61.5875
100.9844 | 123.5046 | -61.5738 | 61.8027 | 0.0177 | 0.0030079 | -0.00075189 | -0.00033118 | 0.00033116 | -0.0014974 | -0.0022346 | -0.00030511 | -0.00029902 | 0.0339 | 0.039512 | 0.0010575 | -0.00035469 | 0.00071145 | -0.013733 | 61.853 | -61.8484 | 61.6058 | 61.5417 | -61.8988 | -0.073242 | 0.041199 | 61.8301 | -61.6425 | 61.8164 | -0.89722 | -61.6699 | -61.2534 | -0.27466 | 0.050354 | -0.19684 | 123.1155 | 61.5005 | -0.32501 | 61.7752 | -0.050354 | -0.068664 | 0.027466 | 0.013733 | 60.6766 | 0.32043 | -0.09613 | 0.3891 | -0.027466 | 123.3902 | 123.4543 | 60.7452 | 123.4589 | 123.7015 | 123.4726 | 123.4268 | 123.4039 | -123.6511 | -123.4451 | 123.1796 | 123.3902 | 61.5601 | 61.615
101.9844 | 123.5321 | -61.5738 | 61.7935 | -0.005188 | 1.7082e-05 | 0.00010251 | -0.00011758 | 0.00011756 | -0.00021583 | -0.00073916 | 0.0057983 | 0.00034178 | 0.034327 | 0.032889 | -0.00086514 | 0.00049991 | -0.0016385 | -0.004578 | 61.8805 | -61.7981 | 61.615 | 61.5967 | -61.8073 | 0.032043 | 0.054932 | 61.8484 | -61.6425 | 61.821 | -0.8606 | -61.6837 | -61.2534 | -0.2243 | 0.086975 | -0.17853 | 123.1705 | 61.6058 | -0.23346 | 61.8301 | -0.009155 | -0.068664 | 0.054932 | 0.027466 | 60.7132 | 0.32043 | -0.10986 | 0.3891 | -0.041199 | 123.3948 | 123.4131 | 60.7819 | 123.4634 | 123.6786 | 123.4909 | 123.4543 | 123.4222 | -123.5916 | -123.436 | 123.1888 | 123.3948 | 61.5692 | 61.6287
102.9844 | 123.4955 | -61.5921 | 61.7615 | 0.040589 | 0.0027943 | 0.00074331 | 9.6222e-05 | 0.0041764 | 0.001066 | -0.0033026 | -0.024719 | 0.0018372 | 0.034968 | 0.033103 | -0.0021469 | 0.00049991 | 0.00071145 | -0.050354 | 61.8393 | -61.821 | 61.5646 | 61.5646 | -61.8576 | -0.064087 | -0.059509 | 61.8301 | -61.6562 | 61.7569 | -0.93384 | -61.7386 | -61.2854 | -0.22888 | 0.077819 | -0.19684 | 123.1567 | 61.528 | -0.2655 | 61.7569 | -0.036621 | -0.064087 | 0.068664 | -0.004578 | 60.6583 | 0.3067 | -0.14648 | 0.37079 | -0.082397 | 123.3856 | 123.3856 | 60.7224 | 123.4131 | 123.6603 | 123.4863 | 123.4314 | 123.4222 | -123.5825 | -123.4177 | 123.1567 | 123.349 | 61.5417 | 61.5326
103.9844 | 123.5229 | -61.5555 | 61.7981 | -0.043335 | 0.0017261 | 0.00010251 | 0.00073702 | 0.00075836 | 0.0012796 | -0.00095276 | -0.030823 | 0.0016236 | 0.036891 | 0.035453 | -0.0010787 | 7.2706e-05 | 0.00028405 | 0 | 61.8439 | -61.8164 | 61.6013 | 61.6058 | -61.8256 | -0.013733 | 0.041199 | 61.821 | -61.6516 | 61.8073 | -0.88806 | -61.6745 | -61.235 | -0.26093 | 0.045776 | -0.19684 | 123.1613 | 61.5417 | -0.27008 | 61.8027 | -0.009156 | -0.09613 | 0.022888 | 0.009155 | 60.6674 | 0.32044 | -0.11902 | 0.41657 | -0.022889 | 123.4222 | 123.4177 | 60.7635 | 123.4589 | 123.6603 | 123.4726 | 123.3994 | 123.3765 | -123.6145 | -123.4497 | 123.1567 | 123.3627 | 61.5555 | 61.5967
104.9844 | 123.4772 | -61.5784 | 61.7981 | 0.0024415 | 0.00023068 | 0.0026661 | 0.00052342 | -0.00095064 | 0.00085237 | -0.0033026 | -0.021668 | -0.00051262 | 0.034754 | 0.03588 | -0.0027877 | 0.0015679 | -0.0022793 | -0.036621 | 61.853 | -61.821 | 61.5921 | 61.5784 | -61.853 | -0.036621 | -0.027466 | 61.8301 | -61.6425 | 61.7661 | -0.93842 | -61.7249 | -61.29 | -0.24262 | 0.054931 | -0.20599 | 123.1567 | 61.5417 | -0.27466 | 61.7844 | -0.032043 | -0.064087 | 0.032043 | -0.032044 | 60.64 | 0.28839 | -0.14648 | 0.35248 | -0.082398 | 123.3994 | 123.4131 | 60.704 | 123.4085 | 123.674 | 123.4726 | 123.4314 | 123.4085 | -123.6191 | -123.4406 | 123.1705 | 123.3444 | 61.5417 | 61.5509
105.9844 | 123.5046 | -61.5601 | 61.821 | 0.048218 | 0.00044428 | -0.00096549 | 0.0013778 | -0.00052344 | 0.0021342 | -0.0018072 | -0.00030511 | 0.0018372 | 0.037318 | 0.033744 | -0.00022434 | -0.0022773 | 0.00049765 | -0.009155 | 61.8988 | -61.8118 | 61.5829 | 61.5921 | -61.7844 | 0.027466 | 0.054932 | 61.853 | -61.6379 | 61.8164 | -0.85602 | -61.6699 | -61.2442 | -0.25177 | 0.07782 | -0.23804 | 123.1522 | 61.5875 | -0.2243 | 61.8393 | 0.027466 | -0.077819 | 0.032043 | -0.004578 | 60.704 | 0.31586 | -0.10986 | 0.39368 | -0.032044 | 123.4039 | 123.3948 | 60.7819 | 123.4543 | 123.7106 | 123.4909 | 123.4589 | 123.4131 | -123.6328 | -123.4589 | 123.143 | 123.3765 | 61.5509 | 61.615
106.9844 | 123.4863 | -61.5829 | 61.7981 | 0.0024415 | 1.7082e-05 | 0.0011707 | 0.00052342 | 0.00097196 | 0.00063877 | -0.00031196 | -0.039978 | 0.0011964 | 0.035822 | 0.026908 | -1.0744e-05 | 0.0024225 | -0.0020657 | -0.032043 | 61.8484 | -61.8164 | 61.5829 | 61.6196 | -61.8301 | -0.013733 | 0.027466 | 61.853 | -61.6287 | 61.7935 | -0.91095 | -61.7065 | -61.2534 | -0.23346 | 0.050354 | -0.21515 | 123.2025 | 61.5692 | -0.24719 | 61.8027 | -0.013733 | -0.045776 | 0.054931 | -0.004578 | 60.672 | 0.32959 | -0.1236 | 0.37537 | -0.07782 | 123.436 | 123.3994 | 60.7178 | 123.4222 | 123.6649 | 123.4818 | 123.4314 | 123.436 | -123.6145 | -123.4268 | 123.1659 | 123.3765 | 61.5509 | 61.6104
107.9844 | 123.4955 | -61.5692 | 61.8347 | 0.010071 | -0.0010511 | 0.00095711 | -0.00075838 | -0.00095064 | -0.00021583 | 0.00075624 | 0.018005 | -0.0013672 | 0.034754 | 0.032462 | -0.00022434 | -0.0016363 | -0.00078395 | -0.018311 | 61.8851 | -61.8027 | 61.5738 | 61.5738 | -61.8256 | 0.032043 | 0.022888 | 61.8759 | -61.6379 | 61.7981 | -0.86975 | -61.6699 | -61.2396 | -0.23346 | 0.050354 | -0.26093 | 123.143 | 61.6013 | -0.25635 | 61.8347 | -0.022889 | -0.068664 | 0.041199 | -0.036621 | 60.6995 | 0.32959 | -0.10071 | 0.39825 | -0.032044 | 123.3765 | 123.3765 | 60.7681 | 123.436 | 123.6877 | 123.5138 | 123.4543 | 123.4451 | -123.6374 | -123.4726 | 123.143 | 123.3673 | 61.5509 | 61.5921
108.9844 | 123.4909 | -61.5601 | 61.7889 | 0.0024415 | -0.00019652 | -0.00032469 | 0.00095062 | 0.00075836 | -0.00021583 | 0.002038 | -0.024719 | 0.00141 | 0.033045 | 0.033958 | -0.0015059 | -0.00056829 | 0.0013523 | -0.054932 | 61.8622 | -61.8393 | 61.5829 | 61.5601 | -61.8622 | -0.064087 | -0.050354 | 61.8256 | -61.6791 | 61.7569 | -0.92926 | -61.7386 | -61.2808 | -0.27923 | 0.073243 | -0.20599 | 123.1201 | 61.496 | -0.30212 | 61.7752 | -0.022889 | -0.11902 | 0.036622 | -0.032043 | 60.6308 | 0.27924 | -0.17853 | 0.39825 | -0.059509 | 123.3994 | 123.4222 | 60.7498 | 123.436 | 123.7015 | 123.5046 | 123.4222 | 123.3856 | -123.6282 | -123.468 | 123.143 | 123.317 | 61.5051 | 61.5097
109.9844 | 123.4955 | -61.5555 | 61.7935 | 0.02533 | -0.00041012 | 0.00052971 | 0.00095062 | 0.00011756 | 0.00063877 | -0.0026618 | 0.014954 | 0.00076898 | 0.0339 | 0.033958 | -0.0015059 | -0.00014089 | -0.0016385 | -0.009155 | 61.8713 | -61.8256 | 61.615 | 61.6196 | -61.8073 | 0.036621 | 0.07782 | 61.8576 | -61.6516 | 61.8256 | -0.86517 | -61.6745 | -61.235 | -0.27008 | 0.07782 | -0.17853 | 123.175 | 61.5921 | -0.25177 | 61.8622 | 0.018311 | -0.09613 | 0.064087 | 0.032044 | 60.6903 | 0.32044 | -0.11902 | 0.41657 | -0.022889 | 123.4451 | 123.4406 | 60.7864 | 123.4772 | 123.6969 | 123.5092 | 123.4268 | 123.4131 | -123.6191 | -123.4451 | 123.1705 | 123.381 | 61.5463 | 61.6333
110.9844 | 123.5001 | -61.5967 | 61.7798 | 0.0024415 | 0.00087168 | 0.0015979 | 0.001805 | 0.0013992 | 0.001066 | -0.0026618 | -0.027771 | 0.00055538 | 0.031764 | 0.035026 | -0.00065154 | 7.2706e-05 | 0.0024203 | -0.027466 | 61.8759 | -61.8073 | 61.5829 | 61.5829 | -61.8439 | -0.041199 | -0.032043 | 61.8164 | -61.6516 | 61.7889 | -0.9201 | -61.7432 | -61.2854 | -0.21057 | 0.096131 | -0.19684 | 123.1796 | 61.5555 | -0.24719 | 61.7661 | -0.036621 | -0.054931 | 0.036621 | 0.009155 | 60.6766 | 0.31128 | -0.14648 | 0.36621 | -0.091553 | 123.3902 | 123.3902 | 60.7315 | 123.4406 | 123.6832 | 123.468 | 123.4726 | 123.4131 | -123.587 | -123.4314 | 123.1796 | 123.3856 | 61.5692 | 61.5646
111.9844 | 123.5046 | -61.5601 | 61.8027 | 0.093994 | 0.0012989 | 0.00031611 | 0.00052342 | 0.0022538 | 0.002775 | -9.8356e-05 | -0.0033569 | 0.00034178 | 0.036036 | 0.037162 | 0.00063026 | -0.00014089 | 7.0452e-05 | -0.013733 | 61.8576 | -61.8073 | 61.615 | 61.6013 | -61.8118 | 0.009155 | 0.041199 | 61.8622 | -61.6516 | 61.7569 | -1.0071 | -61.5875 | -61.1755 | -0.24719 | 0.054932 | -0.18768 | 123.1613 | 61.5692 | -0.25177 | 61.8164 | -0.004578 | -0.091552 | 0.05951 | -0.045776 | 60.553 | 0.38452 | -0.027465 | 0.47607 | 0.064087 | 123.4085 | 123.4222 | 60.6445 | 123.4085 | 123.6649 | 123.5138 | 123.4177 | 123.4222 | -123.6099 | -123.4543 | 123.175 | 123.317 | 61.5463 | 61.6013
112.9844 | 123.5092 | -61.5738 | 61.7661 | 0.0024415 | 0.00065788 | 0.00010251 | 9.6222e-05 | 0.00011756 | 0.00063877 | 0.00075624 | -0.033875 | 0.00034178 | 0.033259 | 0.032035 | -0.0015059 | 0.0011407 | 0.0017795 | -0.013733 | 61.8576 | -61.8256 | 61.6058 | 61.6013 | -61.8118 | -0.009155 | 0.032043 | 61.8439 | -61.6333 | 61.8164 | -0.88806 | -61.702 | -61.2808 | -0.25177 | 0.091553 | -0.16022 | 123.175 | 61.5646 | -0.23804 | 61.8164 | 0.013733 | -0.059509 | 0.07782 | 0.050354 | 60.6857 | 0.29297 | -0.12817 | 0.35248 | -0.068664 | 123.4268 | 123.4314 | 60.7452 | 123.4497 | 123.6832 | 123.4772 | 123.4314 | 123.4177 | -123.5916 | -123.3994 | 123.1796 | 123.3902 | 61.5601 | 61.6058
113.9844 | 123.5001 | -61.5555 | 61.8393 | -0.035705 | -0.00083732 | 0.0011707 | -0.00054478 | -0.00052344 | -0.00085663 | 0.00096984 | 0.011902 | 0.00034178 | 0.033045 | 0.034171 | -0.0021469 | -0.00099549 | -0.0016385 | -0.032043 | 61.8713 | -61.8118 | 61.5829 | 61.5692 | -61.8256 | 0.027466 | 0.013733 | 61.8622 | -61.6425 | 61.7889 | -0.88348 | -61.6653 | -61.2534 | -0.25635 | 0.032044 | -0.25635 | 123.1247 | 61.5829 | -0.27008 | 61.8393 | -0.013733 | -0.086975 | 0.022889 | -0.050354 | 60.672 | 0.30212 | -0.10986 | 0.3891 | -0.022888 | 123.381 | 123.3948 | 60.759 | 123.4314 | 123.6832 | 123.5046 | 123.4268 | 123.4177 | -123.6511 | -123.4818 | 123.1384 | 123.3444 | 61.5234 | 61.5692
114.9844 | 123.5184 | -61.5646 | 61.7889 | 0.010071 | -0.00019652 | -0.00032469 | 9.6222e-05 | 0.0041764 | -0.0019248 | 0.00075624 | -0.036926 | 0.002478 | 0.033259 | 0.030326 | -0.00022434 | -0.00056829 | 0.0022067 | -0.022888 | 61.853 | -61.8118 | 61.5143 | 61.6745 | -61.7935 | 0.013733 | 0.036621 | 61.8301 | -61.647 | 61.8118 | -0.87433 | -61.6745 | -61.2534 | -0.24719 | 0.064087 | -0.27466 | 123.2391 | 61.5784 | -0.22888 | 61.8256 | 0.018311 | -0.082398 | 0.041199 | 0.022889 | 60.6903 | 0.31128 | -0.10986 | 0.39368 | -0.027466 | 123.4863 | 123.3261 | 60.7727 | 123.4589 | 123.6649 | 123.4772 | 123.4177 | 123.3948 | -123.6008 | -123.436 | 123.0789 | 123.3765 | 61.5417 | 61.6013
115.9844 | 123.5229 | -61.5601 | 61.8027 | -0.035705 | 0.0017261 | 0.0018115 | 0.0015914 | 0.0024674 | 0.0021342 | 0.00011544 | -0.015564 | -0.00072642 | 0.032832 | 0.034385 | -0.0015059 | 0.00028631 | -0.0016385 | 0 | 61.8851 | -61.7981 | 61.5967 | 61.5875 | -61.7981 | 0.018311 | 0.07782 | 61.8668 | -61.6653 | 61.8027 | -0.8606 | -61.6653 | -61.2396 | -0.23804 | 0.082398 | -0.20599 | 123.1476 | 61.5784 | -0.23804 | 61.8164 | 0 | -0.10528 | 0.064087 | 0 | 60.6995 | 0.32044 | -0.10528 | 0.42572 | 0 | 123.3856 | 123.3948 | 60.8047 | 123.468 | 123.6832 | 123.5321 | 123.4451 | 123.4268 | -123.6008 | -123.468 | 123.1567 | 123.3627 | 61.5601 | 61.6379
116.9844 | 123.468 | -61.6013 | 61.8027 | -0.020447 | 0.0010853 | -0.00011109 | -0.00097198 | 0.0011856 | 0.00021157 | 0.0011834 | -0.015564 | 0.00141 | 0.033473 | 0.039084 | -0.0019333 | -0.0027045 | -0.0022793 | -0.068665 | 61.8484 | -61.8439 | 61.5417 | 61.528 | -61.8805 | -0.09613 | -0.11444 | 61.8393 | -61.6562 | 61.7294 | -0.9613 | -61.7981 | -61.3358 | -0.24262 | 0.045777 | -0.26093 | 123.1293 | 61.5051 | -0.27924 | 61.7477 | -0.036621 | -0.054932 | 0.036621 | -0.073242 | 60.64 | 0.2655 | -0.19684 | 0.32043 | -0.14191 | 123.3719 | 123.3856 | 60.6949 | 123.3856 | 123.6923 | 123.4955 | 123.4497 | 123.4406 | -123.6465 | -123.4589 | 123.143 | 123.3307 | 61.5326 | 61.4868
117.9844 | 123.5413 | -61.5646 | 61.8164 | 0.0024415 | -0.00041012 | 0.00074331 | -0.0018266 | 0.0013992 | 0.00063877 | 0.002038 | 0.014954 | -0.0015808 | 0.033259 | 0.027122 | -0.0015059 | -0.00056829 | -0.00078395 | -0.009155 | 61.908 | -61.7889 | 61.5829 | 61.5692 | -61.8118 | 0.022888 | 0.036621 | 61.8576 | -61.6425 | 61.7935 | -0.85144 | -61.6699 | -61.235 | -0.2243 | 0.091553 | -0.23346 | 123.1338 | 61.5875 | -0.24719 | 61.8118 | -0.022889 | -0.07782 | 0.041199 | -0.022888 | 60.7132 | 0.32959 | -0.10529 | 0.40741 | -0.027466 | 123.3582 | 123.3719 | 60.791 | 123.436 | 123.6969 | 123.5001 | 123.4726 | 123.4222 | -123.6053 | -123.4589 | 123.1476 | 123.3582 | 61.5555 | 61.6013
118.9844 | 123.5001 | -61.5784 | 61.7661 | 0.10162 | -0.00083732 | -0.00011109 | -0.00054478 | 0.00011756 | -0.001711 | 0.00054264 | -0.00030511 | 0.00141 | 0.032618 | 0.029899 | -0.0012923 | -0.0020637 | 0.00071145 | -0.013733 | 61.8713 | -61.8164 | 61.615 | 61.6058 | -61.8073 | 0.009155 | 0.022888 | 61.8164 | -61.647 | 61.7981 | -0.89722 | -61.7111 | -61.2717 | -0.23804 | 0.10529 | -0.15106 | 123.1842 | 61.5875 | -0.22888 | 61.8256 | 0.009155 | -0.068665 | 0.050354 | 0.032044 | 60.6812 | 0.3067 | -0.13275 | 0.37537 | -0.064087 | 123.4222 | 123.4314 | 60.7498 | 123.4451 | 123.6877 | 123.4634 | 123.4497 | 123.3948 | -123.5825 | -123.4131 | 123.1934 | 123.3765 | 61.5646 | 61.6013
119.9844 | 123.5413 | -61.5509 | 61.8301 | 0.040589 | -0.00041012 | -0.0031019 | -0.0011856 | -0.0022324 | -0.00021583 | -0.0024482 | 0.021057 | -0.00094002 | 0.0339 | 0.032035 | -0.00022434 | 0.00028631 | 0.00092505 | -0.013733 | 61.8988 | -61.8027 | 61.5646 | 61.5601 | -61.8393 | 0.027466 | 0.027466 | 61.8622 | -61.647 | 61.7844 | -0.88348 | -61.6837 | -61.2671 | -0.25177 | 0.068665 | -0.2655 | 123.111 | 61.5784 | -0.28839 | 61.8301 | -0.036621 | -0.096131 | 0.032044 | -0.045776 | 60.6674 | 0.28381 | -0.13275 | 0.37994 | -0.036621 | 123.3627 | 123.3673 | 60.7635 | 123.4314 | 123.7015 | 123.5092 | 123.4497 | 123.4131 | -123.6328 | -123.4772 | 123.1155 | 123.3353 | 61.5372 | 61.5784
120.9844 | 123.4863 | -61.5555 | 61.7889 | 0.0177 | 0.00065788 | 0.00010251 | 0.0015914 | 0.0058854 | -0.0019248 | 0.0035332 | -0.021668 | 0.00012818 | 0.035609 | 0.033317 | -0.00043794 | -0.0022773 | 0.0013523 | -0.027466 | 61.8668 | -61.8256 | 61.4502 | 61.4868 | -61.6699 | 0.032043 | 0.050354 | 61.8301 | -61.6791 | 61.8164 | -0.88348 | -61.6608 | -61.235 | -0.27008 | 0.07782 | -0.33874 | 123.0423 | 61.5875 | -0.11444 | 61.8576 | 0.15564 | -0.1236 | 0.041199 | 0.027466 | 60.672 | 0.32044 | -0.10529 | 0.44403 | 0.01831 | 123.3124 | 123.2758 | 60.7956 | 123.4955 | 123.6923 | 123.5092 | 123.4222 | 123.3856 | -123.6145 | -123.468 | 123.0057 | 123.3719 | 61.528 | 61.6058
121.9844 | 123.4909 | -61.5646 | 61.7889 | -0.035705 | -0.00041012 | -0.0020337 | -0.0020402 | -0.0015914 | 0.00021157 | -0.00031196 | 0.018005 | 0.0016236 | 0.033686 | 0.030753 | -0.0019333 | -0.00056829 | 0.0028477 | -0.018311 | 61.908 | -61.8256 | 61.5692 | 61.5784 | -61.8256 | 0.027466 | 0.013733 | 61.8759 | -61.6516 | 61.7798 | -0.88806 | -61.6928 | -61.2488 | -0.26093 | 0.11902 | -0.21973 | 123.143 | 61.5921 | -0.26093 | 61.853 | 0 | -0.086975 | 0.086976 | -0.009155 | 60.6766 | 0.31586 | -0.12817 | 0.40283 | -0.041199 | 123.4039 | 123.3948 | 60.7635 | 123.4314 | 123.7335 | 123.5275 | 123.4726 | 123.4406 | -123.6145 | -123.4406 | 123.1338 | 123.3444 | 61.5463 | 61.5784
122.9844 | 123.4726 | -61.5875 | 61.7798 | 0.010071 | 0.00087168 | 0.00031611 | 0.00073702 | 0.0011856 | 0.00042517 | -0.0011664 | -0.027771 | 0.00141 | 0.034754 | 0.035026 | -0.00022434 | -0.00014089 | 7.0452e-05 | -0.013733 | 61.8576 | -61.8301 | 61.5967 | 61.6058 | -61.8393 | -0.032043 | 0.009155 | 61.8484 | -61.6608 | 61.7844 | -0.91095 | -61.7111 | -61.2717 | -0.24262 | 0.07782 | -0.1831 | 123.1934 | 61.5555 | -0.25177 | 61.7981 | -0.009155 | -0.073243 | 0.068665 | 0.004578 | 60.6766 | 0.31586 | -0.1236 | 0.3891 | -0.050354 | 123.436 | 123.4268 | 60.7498 | 123.4451 | 123.6877 | 123.5092 | 123.4451 | 123.436 | -123.6099 | -123.4406 | 123.1842 | 123.3719 | 61.5738 | 61.5967
123.9844 | 123.5275 | -61.5601 | 61.7981 | 0.010071 | -0.00083732 | 0.00095711 | 0.00052342 | -0.0015914 | 0.0012796 | 0.00054264 | -0.00030511 | -0.00051262 | 0.0339 | 0.036094 | 0.00020286 | 0.00071351 | 0.0011387 | -0.013733 | 61.8759 | -61.8073 | 61.5829 | 61.5784 | -61.8164 | 0.013733 | 0.045776 | 61.8851 | -61.6287 | 61.7981 | -0.87891 | -61.6699 | -61.2167 | -0.24719 | 0.07782 | -0.21515 | 123.1384 | 61.5738 | -0.25635 | 61.821 | -0.009155 | -0.068664 | 0.086975 | 0 | 60.6812 | 0.34332 | -0.10986 | 0.41199 | -0.041199 | 123.3856 | 123.3902 | 60.7498 | 123.4268 | 123.6832 | 123.5138 | 123.436 | 123.4451 | -123.6053 | -123.4268 | 123.143 | 123.3582 | 61.5463 | 61.6058
124.9844 | 123.5138 | -61.5738 | 61.7661 | 0.0024415 | 0.00044428 | 0.0011707 | 0.0011642 | 0.00033116 | 0.0019204 | -0.00052556 | -0.018616 | 0.00012818 | 0.034541 | 0.031608 | -0.0027877 | 7.2706e-05 | 0.0011387 | -0.027466 | 61.8439 | -61.8393 | 61.6058 | 61.5921 | -61.8073 | -0.009155 | 0.036621 | 61.8393 | -61.6379 | 61.7981 | -0.88806 | -61.7203 | -61.2579 | -0.2655 | 0.07782 | -0.16022 | 123.1659 | 61.5646 | -0.23346 | 61.8301 | 0.032043 | -0.064086 | 0.073242 | 0.032044 | 60.6857 | 0.31586 | -0.14648 | 0.37994 | -0.082398 | 123.4314 | 123.4451 | 60.7498 | 123.436 | 123.6832 | 123.4772 | 123.4177 | 123.4131 | -123.6053 | -123.4039 | 123.1796 | 123.3719 | 61.5463 | 61.6104
125.9844 | 123.5367 | -61.5417 | 61.7889 | 0.071106 | -0.00083732 | 0.00095711 | -0.00075838 | 0.00054476 | -0.0021384 | -0.0024482 | 0.021057 | 0.0020508 | 0.031764 | 0.026053 | -0.0025741 | 0.00071351 | 0.00028405 | -0.013733 | 61.8713 | -61.8256 | 61.5829 | 61.5738 | -61.821 | 0.022888 | 0.013733 | 61.8805 | -61.6425 | 61.7935 | -0.87891 | -61.6699 | -61.2442 | -0.28381 | 0.082398 | -0.20599 | 123.1155 | 61.5646 | -0.27924 | 61.8484 | 0.004578 | -0.10071 | 0.091553 | 0.004578 | 60.6628 | 0.29755 | -0.12817 | 0.39825 | -0.027466 | 123.3994 | 123.4085 | 60.7636 | 123.436 | 123.6969 | 123.5229 | 123.4131 | 123.4222 | -123.6145 | -123.4314 | 123.1247 | 123.3353 | 61.528 | 61.5555
126.9844 | 123.4863 | -61.5692 | 61.7844 | -0.005188 | 0.0019397 | -0.0011793 | -0.00075838 | 0.0013992 | -0.00042943 | -9.8356e-05 | -0.039978 | 0.0020508 | 0.033686 | 0.028831 | -1.0744e-05 | 0.0011407 | 0.00028405 | -0.14648 | 61.8439 | -61.853 | 61.5967 | 61.6013 | -61.8347 | 0.009155 | 0.050354 | 61.8393 | -61.6333 | 61.821 | -0.88806 | -61.6837 | -61.2534 | -0.28381 | 0.059509 | -0.18768 | 123.1705 | 61.5784 | -0.2655 | 61.8622 | 0.01831 | -0.064087 | 0.054931 | 0.036621 | 60.6812 | 0.31586 | -0.11444 | 0.37994 | -0.050354 | 123.4543 | 123.4497 | 60.7452 | 123.4543 | 123.6969 | 123.4726 | 123.4131 | 123.4085 | -123.6374 | -123.4177 | 123.1659 | 123.3902 | 61.4227 | 61.6196
127.9844 | 123.5184 | -61.5692 | 61.7981 | 0.063477 | 0.00065788 | -0.0013929 | -0.00097198 | -0.002446 | -0.0025656 | 0.0016106 | 0.014954 | 0.00076898 | 0.033473 | 0.029044 | 0.00020286 | -0.00056829 | 0.0022067 | -0.027466 | 61.8759 | -61.8118 | 61.5784 | 61.5555 | -61.8256 | 0.022888 | 0.004578 | 61.8668 | -61.6379 | 61.7981 | -0.88806 | -61.6745 | -61.2488 | -0.24262 | 0.07782 | -0.21973 | 123.1247 | 61.5921 | -0.25635 | 61.8347 | -0.013733 | -0.068664 | 0.068664 | 0 | 60.6812 | 0.32044 | -0.10529 | 0.3891 | -0.036622 | 123.3673 | 123.3902 | 60.7498 | 123.436 | 123.6877 | 123.5046 | 123.4451 | 123.436 | -123.6099 | -123.436 | 123.1476 | 123.3673 | 61.5417 | 61.5738
128.9844 | 123.4863 | -61.5555 | 61.8027 | 0.02533 | -0.00083732 | -0.00032469 | 0.001805 | 0.0011856 | -0.00042943 | 0.0033196 | -0.021668 | 0.002478 | 0.032405 | 0.033744 | -0.00065154 | 0.0022089 | 0.0013523 | 0 | 61.8576 | -61.8256 | 61.5005 | 61.5601 | -61.7203 | 0.004578 | 0.045776 | 61.8668 | -61.6516 | 61.8118 | -0.88348 | -61.6882 | -61.2396 | -0.27008 | 0.054932 | -0.30212 | 123.1155 | 61.5601 | -0.16479 | 61.8301 | 0.10529 | -0.09613 | 0.064087 | 0.009156 | 60.672 | 0.31586 | -0.13275 | 0.41199 | -0.036621 | 123.3856 | 123.3261 | 60.7681 | 123.4634 | 123.6832 | 123.5184 | 123.4131 | 123.4222 | -123.6282 | -123.4543 | 123.056 | 123.3673 | 61.5555 | 61.6013
129.9844 | 123.5046 | -61.5646 | 61.8118 | 0.0024415 | 0.00087168 | -0.00053829 | 0.00030982 | 0.00033116 | 0.00042517 | -0.0011664 | 0.011902 | 0.0037598 | 0.031336 | 0.035667 | 0.00063026 | -0.00078189 | 0.0058383 | -0.004578 | 61.8622 | -61.8301 | 61.6013 | 61.615 | -61.7981 | 0.041199 | 0.07782 | 61.8439 | -61.6379 | 61.8164 | -0.87891 | -61.6745 | -61.235 | -0.2655 | 0.050354 | -0.21057 | 123.1796 | 61.6058 | -0.23346 | 61.8713 | 0.032043 | -0.073242 | 0.032043 | 0.004577 | 60.6857 | 0.32959 | -0.10986 | 0.40283 | -0.036622 | 123.4451 | 123.4314 | 60.759 | 123.4543 | 123.6923 | 123.4818 | 123.4268 | 123.4085 | -123.642 | -123.4497 | 123.1659 | 123.381 | 61.5601 | 61.6425
130.9844 | 123.4955 | -61.5692 | 61.8073 | 0.032959 | 0.0021533 | 0.0018115 | 0.00052342 | 0.0024674 | -0.00085663 | -0.00095276 | -0.021668 | 0.0029052 | 0.034113 | 0.033744 | -0.0025741 | -0.0012091 | -0.0033475 | -0.022888 | 61.8622 | -61.8439 | 61.5692 | 61.5829 | -61.8622 | -0.054932 | -0.036621 | 61.8118 | -61.6516 | 61.7798 | -0.92926 | -61.7157 | -61.2762 | -0.27466 | 0.054932 | -0.23804 | 123.1522 | 61.5143 | -0.29297 | 61.7889 | -0.018311 | -0.082397 | 0.004578 | -0.027466 | 60.64 | 0.29297 | -0.14648 | 0.37537 | -0.064087 | 123.4268 | 123.4131 | 60.7224 | 123.4314 | 123.7061 | 123.4634 | 123.4314 | 123.381 | -123.6511 | -123.4589 | 123.1384 | 123.349 | 61.5463 | 61.5326
131.9844 | 123.5001 | -61.5372 | 61.8164 | 0.071106 | 0.00044428 | 0.00074331 | 0.0011642 | -0.002446 | -0.0019248 | -9.8356e-05 | 0.024109 | -0.0024352 | 0.034113 | 0.031608 | -0.0025741 | -0.00014089 | 0.0011387 | -0.009155 | 61.8668 | -61.8073 | 61.6013 | 61.5967 | -61.7844 | 0.027466 | 0.073242 | 61.8713 | -61.6425 | 61.8118 | -0.86517 | -61.6882 | -61.2442 | -0.27008 | 0.050354 | -0.21515 | 123.1338 | 61.5646 | -0.24719 | 61.8347 | 0.022888 | -0.10529 | 0.054932 | -0.004577 | 60.672 | 0.29297 | -0.15106 | 0.39825 | -0.045776 | 123.4039 | 123.4085 | 60.7773 | 123.4543 | 123.674 | 123.5138 | 123.4039 | 123.4085 | -123.6237 | -123.4589 | 123.1384 | 123.349 | 61.528 | 61.6104
132.9844 | 123.5092 | -61.5738 | 61.7798 | -0.012817 | 0.00023068 | 0.00074331 | 9.6222e-05 | 0.00075836 | 0.00042517 | 0.00054264 | -0.04303 | 0.0020508 | 0.035182 | 0.036094 | -0.00065154 | -0.00056829 | 0.00049765 | -0.027466 | 61.8759 | -61.853 | 61.5829 | 61.5875 | -61.8347 | -0.032043 | -0.018311 | 61.8301 | -61.6562 | 61.7798 | -0.91553 | -61.7203 | -61.2946 | -0.27923 | 0.096131 | -0.19684 | 123.1613 | 61.5417 | -0.26093 | 61.821 | 0.01831 | -0.082397 | 0.050354 | 0 | 60.6583 | 0.27924 | -0.14648 | 0.36163 | -0.064087 | 123.4406 | 123.436 | 60.7407 | 123.436 | 123.7289 | 123.4863 | 123.4497 | 123.4039 | -123.6328 | -123.436 | 123.1567 | 123.3536 | 61.5463 | 61.5555
133.9844 | 123.5229 | -61.5784 | 61.7981 | 0.02533 | -0.0025463 | 0.0013843 | -0.00033118 | 0.0024674 | 0.00021157 | 0.001397 | -0.027771 | 0.00098258 | 0.0339 | 0.032462 | -0.00022434 | -0.00099549 | 0.0019931 | -0.004578 | 61.8668 | -61.8347 | 61.6013 | 61.615 | -61.821 | 0 | 0.054932 | 61.8484 | -61.6425 | 61.7249 | -0.82855 | -61.6516 | -61.235 | -0.25635 | 0.068664 | -0.19684 | 123.1934 | 61.5784 | -0.24262 | 61.8347 | 0.013733 | -0.064087 | 0.050354 | -0.073242 | 60.7498 | 0.34332 | -0.073242 | 0.40741 | -0.009155 | 123.4497 | 123.436 | 60.8139 | 123.3673 | 123.7015 | 123.4909 | 123.4451 | 123.4268 | -123.6328 | -123.4406 | 123.1796 | 123.3032 | 61.5738 | 61.6333
134.9844 | 123.4955 | -61.5784 | 61.7752 | 0.048218 | 1.7082e-05 | 0.0013843 | 0.0011642 | 0.0031082 | -0.0012838 | 0.0035332 | -0.012512 | 0.0037598 | 0.035822 | 0.032676 | -0.0010787 | 0.00049991 | 0.0019931 | -0.018311 | 61.8484 | -61.8347 | 61.5967 | 61.5967 | -61.8256 | -0.027466 | 0.004578 | 61.8439 | -61.6562 | 61.7889 | -0.92468 | -61.7249 | -61.2854 | -0.25635 | 0.073242 | -0.17853 | 123.175 | 61.5509 | -0.24719 | 61.8073 | 0.009155 | -0.07782 | 0.068664 | 0.013732 | 60.6537 | 0.29297 | -0.14648 | 0.37079 | -0.068665 | 123.4314 | 123.4314 | 60.7315 | 123.4451 | 123.6832 | 123.5001 | 123.4268 | 123.4222 | -123.6099 | -123.4314 | 123.175 | 123.3673 | 61.5601 | 61.5829
135.9844 | 123.5275 | -61.5646 | 61.7752 | 0.071106 | 0.0017261 | 0.0033069 | -0.0013992 | 0.0067398 | -0.0029928 | -0.0011664 | -0.033875 | -0.0013672 | 0.034113 | 0.03588 | 0.0010575 | -0.00099549 | -0.00035675 | -0.004578 | 61.8668 | -61.8118 | 61.5921 | 61.6058 | -61.821 | 0 | 0.054932 | 61.8256 | -61.6425 | 61.8118 | -0.88348 | -61.6699 | -61.2396 | -0.24719 | 0.091552 | -0.18311 | 123.1705 | 61.5646 | -0.25635 | 61.8118 | -0.009155 | -0.07782 | 0.050354 | 0.036621 | 60.6812 | 0.32501 | -0.10529 | 0.40283 | -0.027466 | 123.4177 | 123.4039 | 60.759 | 123.4543 | 123.6786 | 123.468 | 123.4314 | 123.3902 | -123.587 | -123.4177 | 123.1567 | 123.3765 | 61.5601 | 61.6196
136.9844 | 123.4818 | -61.5921 | 61.7661 | 0.0177 | 0.0010853 | 0.0030933 | -0.00054478 | 0.0011856 | 0.0012796 | -0.00095276 | -0.030823 | -0.00029902 | 0.035822 | 0.032889 | -0.0017197 | 0.00028631 | -0.0042019 | -0.073242 | 61.8668 | -61.8484 | 61.5463 | 61.5417 | -61.8759 | -0.073242 | -0.086975 | 61.8256 | -61.6882 | 61.7477 | -0.95215 | -61.7844 | -61.3083 | -0.25635 | 0.10071 | -0.21973 | 123.1338 | 61.5189 | -0.28381 | 61.7752 | -0.027466 | -0.09613 | 0.05951 | -0.01831 | 60.64 | 0.28381 | -0.19226 | 0.37994 | -0.096131 | 123.3902 | 123.3948 | 60.7361 | 123.436 | 123.7152 | 123.5138 | 123.4589 | 123.4177 | -123.6145 | -123.4543 | 123.1384 | 123.3398 | 61.5189 | 61.5051
137.9844 | 123.4909 | -61.5829 | 61.7798 | 0.055847 | 0.00087168 | 0.00095711 | 9.6222e-05 | 0.0024674 | 0.0017068 | -0.00073916 | -0.0033569 | 0.00141 | 0.034113 | 0.032035 | 0.00041666 | 0.0019953 | -0.0024929 | -0.004578 | 61.8942 | -61.8347 | 61.6058 | 61.5967 | -61.8164 | 0.022888 | 0.050354 | 61.8393 | -61.647 | 61.8118 | -0.87891 | -61.6653 | -61.235 | -0.25177 | 0.11444 | -0.17395 | 123.1796 | 61.6058 | -0.23346 | 61.8576 | 0.018311 | -0.064087 | 0.059509 | 0.032044 | 60.704 | 0.3479 | -0.082397 | 0.41199 | -0.01831 | 123.4314 | 123.4406 | 60.7681 | 123.4589 | 123.7289 | 123.4863 | 123.4772 | 123.4222 | -123.6145 | -123.4268 | 123.1888 | 123.3948 | 61.5784 | 61.6333
138.9844 | 123.4772 | -61.5921 | 61.7798 | 0.032959 | 0.0012989 | 0.0018115 | -0.0013992 | 0.0013992 | -2.232e-06 | 0.00032904 | -0.021668 | 0.00098258 | 0.032832 | 0.032676 | -0.0012923 | 0.00092711 | -0.00035675 | -0.054932 | 61.853 | -61.853 | 61.5555 | 61.5463 | -61.8851 | -0.073242 | -0.073242 | 61.8301 | -61.6562 | 61.7569 | -0.95215 | -61.7523 | -61.29 | -0.26093 | 0.073242 | -0.2243 | 123.1384 | 61.5189 | -0.29297 | 61.7798 | -0.032044 | -0.064087 | 0.050354 | -0.022888 | 60.64 | 0.30212 | -0.16022 | 0.36621 | -0.09613 | 123.3994 | 123.4085 | 60.704 | 123.4131 | 123.7061 | 123.4863 | 123.4451 | 123.4222 | -123.6328 | -123.436 | 123.1476 | 123.349 | 61.5372 | 61.5189
139.9844 | 123.5367 | -61.5738 | 61.7981 | 0.055847 | 0.00044428 | 0.0020251 | -0.0011856 | -0.0030868 | -0.00042943 | 0.001397 | -0.024719 | -0.00029902 | 0.0339 | 0.035453 | -1.0744e-05 | -0.0014227 | -0.00057035 | -0.004578 | 61.8896 | -61.821 | 61.6058 | 61.5967 | -61.821 | 0.009155 | 0.041199 | 61.8393 | -61.647 | 61.821 | -0.87891 | -61.6837 | -61.2259 | -0.24719 | 0.091552 | -0.19226 | 123.1705 | 61.5829 | -0.24719 | 61.8301 | 0 | -0.073242 | 0.041198 | 0.022888 | 60.6949 | 0.3479 | -0.10986 | 0.42114 | -0.036621 | 123.4177 | 123.4268 | 60.7681 | 123.468 | 123.7106 | 123.4863 | 123.4634 | 123.4131 | -123.6191 | -123.4451 | 123.1796 | 123.3948 | 61.5692 | 61.615
140.9844 | 123.468 | -61.6104 | 61.7798 | -0.035705 | -0.00083732 | 0.00031611 | -0.00075838 | -0.00030984 | 0.0012796 | 0.00032904 | -0.052185 | 0.00141 | 0.033473 | 0.029471 | -0.0023605 | 0.0011407 | 0.0015659 | -0.10071 | 61.8713 | -61.8484 | 61.5005 | 61.4731 | -61.9492 | -0.14648 | -0.16022 | 61.8393 | -61.7111 | 61.7432 | -0.97961 | -61.7752 | -61.2991 | -0.23804 | 0.091553 | -0.27924 | 123.0835 | 61.4639 | -0.33874 | 61.702 | -0.10071 | -0.10071 | 0.059509 | -0.036621 | 60.6308 | 0.31128 | -0.16479 | 0.41199 | -0.064087 | 123.3215 | 123.349 | 60.7315 | 123.4543 | 123.7198 | 123.5504 | 123.4818 | 123.4497 | -123.6282 | -123.4909 | 123.111 | 123.3536 | 61.5097 | 61.4502
141.9844 | 123.5184 | -61.5555 | 61.7981 | 0.010071 | -0.00083732 | 0.0013843 | -0.0011856 | 0.0013992 | -0.0025656 | -0.002021 | -0.024719 | 0.00012818 | 0.033473 | 0.035453 | -1.0744e-05 | -0.00078189 | 0.0015659 | -0.009155 | 61.8851 | -61.8256 | 61.6104 | 61.6104 | -61.8073 | 0.027466 | 0.050354 | 61.8484 | -61.6516 | 61.8256 | -0.8606 | -61.6699 | -61.2396 | -0.27008 | 0.086975 | -0.18768 | 123.1659 | 61.5829 | -0.25177 | 61.853 | 0.018311 | -0.09613 | 0.050354 | 0.027466 | 60.6949 | 0.31586 | -0.11444 | 0.41199 | -0.018311 | 123.436 | 123.436 | 60.791 | 123.4772 | 123.7106 | 123.5001 | 123.4406 | 123.4039 | -123.6237 | -123.4497 | 123.1659 | 123.381 | 61.5463 | 61.6058
142.9844 | 123.4497 | -61.5601 | 61.7844 | -0.005188 | -0.0016919 | 0.00052971 | -0.00033118 | -0.0022324 | -2.232e-06 | -0.00031196 | -0.024719 | 0.0011964 | 0.034327 | 0.03353 | -0.0015059 | -0.0016363 | -0.00099755 | -0.054932 | 61.853 | -61.8484 | 61.5555 | 61.5555 | -61.8713 | -0.059509 | -0.068665 | 61.821 | -61.6791 | 61.7752 | -0.94757 | -61.734 | -61.2808 | -0.28839 | 0.068664 | -0.22888 | 123.1155 | 61.5006 | -0.31128 | 61.7889 | -0.022888 | -0.11902 | 0.036621 | -0.009155 | 60.6125 | 0.27924 | -0.17395 | 0.39825 | -0.054932 | 123.4039 | 123.4039 | 60.7315 | 123.4543 | 123.7015 | 123.5001 | 123.4131 | 123.381 | -123.6328 | -123.4634 | 123.1155 | 123.3353 | 61.5051 | 61.4914
143.9844 | 123.5092 | -61.5601 | 61.7935 | 0.048218 | 0.0021533 | 0.00074331 | -0.00054478 | 0.0013992 | 0.00042517 | -0.002021 | -0.0064087 | 0.00141 | 0.035395 | 0.028403 | -0.0025741 | 0.00071351 | -0.00078395 | -0.027466 | 61.8805 | -61.8393 | 61.6013 | 61.6379 | -61.9766 | -0.045776 | 0.050354 | 61.853 | -61.6653 | 61.8118 | -0.87891 | -61.6653 | -61.235 | -0.27923 | 0.086975 | -0.19226 | 123.1979 | 61.5143 | -0.41656 | 61.7935 | -0.13733 | -0.10528 | 0.059509 | 0.018311 | 60.6812 | 0.32501 | -0.10528 | 0.4303 | 0 | 123.4772 | 123.4406 | 60.7864 | 123.4772 | 123.7198 | 123.5184 | 123.4406 | 123.4131 | -123.6328 | -123.4589 | 123.1613 | 123.3719 | 61.5326 | 61.6104
144.9844 | 123.4909 | -61.5784 | 61.7798 | -0.028076 | 0.0025805 | 0.0011707 | -0.00054478 | 0.0013992 | 0.0012796 | -0.00138 | 0.030212 | 0.00034178 | 0.032191 | 0.033744 | -0.00043794 | -0.00056829 | -0.00014315 | -0.12817 | 61.8622 | -61.8713 | 61.7157 | 61.7065 | -62.0087 | -0.064087 | -0.1831 | 61.8576 | -61.6653 | 61.7661 | -0.96588 | -61.7569 | -61.2991 | -0.29297 | 0.082398 | -0.064087 | 123.2849 | 61.5143 | -0.4303 | 61.8073 | -0.13733 | -0.086975 | 0.07782 | -0.013733 | 60.6125 | 0.27924 | -0.17853 | 0.36621 | -0.091553 | 123.5779 | 123.587 | 60.6995 | 123.4314 | 123.7335 | 123.5229 | 123.4406 | 123.436 | -123.6511 | -123.4451 | 123.2941 | 123.3444 | 61.4502 | 61.3953
145.9844 | 123.5413 | -61.5692 | 61.7935 | -0.012817 | 0.00065788 | 0.00074331 | 0.00030982 | -0.0013778 | -0.0027792 | 0.00096984 | -0.024719 | -0.00072642 | 0.034541 | 0.03054 | -0.0027877 | -0.00099549 | -0.0027065 | -0.018311 | 61.8439 | -61.8256 | 61.615 | 61.6013 | -61.8118 | 0 | 0.050354 | 61.8393 | -61.6791 | 61.8393 | -0.90637 | -61.7065 | -61.2534 | -0.25635 | 0.050354 | -0.17853 | 123.1705 | 61.5692 | -0.24262 | 61.8256 | 0.013733 | -0.10986 | 0.045776 | 0.045776 | 60.6628 | 0.31586 | -0.13733 | 0.42572 | -0.027466 | 123.4268 | 123.4406 | 60.7727 | 123.5184 | 123.6694 | 123.5184 | 123.4131 | 123.4085 | -123.6191 | -123.4726 | 123.1842 | 123.4085 | 61.5509 | 61.6196
146.9844 | 123.436 | -61.5692 | 61.7798 | 0.040589 | 0.00023068 | 0.0024523 | 0.00073702 | 0.00033116 | 0.00063877 | -0.0011664 | -0.021668 | 0.00034178 | 0.032832 | 0.029471 | -0.0012923 | 0.00071351 | -0.0012111 | -0.07782 | 61.853 | -61.8484 | 61.5372 | 61.5326 | -61.9492 | -0.1236 | -0.16937 | 61.8759 | -61.6837 | 61.7203 | -0.99335 | -61.7889 | -61.3174 | -0.27924 | 0.073242 | -0.24261 | 123.1018 | 61.4456 | -0.37994 | 61.7249 | -0.10071 | -0.11444 | 0.096131 | -0.059509 | 60.5759 | 0.25177 | -0.21973 | 0.36621 | -0.10528 | 123.381 | 123.3856 | 60.6903 | 123.4039 | 123.7015 | 123.5596 | 123.4222 | 123.4451 | -123.6282 | -123.4634 | 123.1064 | 123.2895 | 61.4914 | 61.3998
147.9844 | 123.5046 | -61.6013 | 61.7935 | 0.0024415 | 0.0010853 | -0.00032469 | 0.00030982 | 0.0041764 | 0.0029886 | -0.00052556 | -0.0064087 | 0.00076898 | 0.03625 | 0.033103 | -0.0015059 | 0.00028631 | 0.0011387 | -0.022888 | 61.853 | -61.8393 | 61.5967 | 61.6013 | -61.8164 | -0.013733 | 0.022888 | 61.853 | -61.6333 | 61.8073 | -0.99335 | -61.647 | -61.235 | -0.23804 | 0.059509 | -0.19684 | 123.2025 | 61.5875 | -0.21515 | 61.8256 | 0.022888 | -0.032044 | 0.059509 | 0.013733 | 60.6079 | 0.36621 | -0.045777 | 0.39826 | -0.013733 | 123.4406 | 123.436 | 60.64 | 123.4406 | 123.6923 | 123.4863 | 123.4543 | 123.4543 | -123.6328 | -123.4268 | 123.1979 | 123.4085 | 61.5784 | 61.6241
148.9844 | 123.4589 | -61.5921 | 61.7523 | -0.043335 | 0.0032215 | -0.0011793 | 0.00052342 | 0.00075836 | 0.0029886 | -0.00052556 | -0.039978 | -0.0013672 | 0.033686 | 0.036307 | -0.00086514 | 0.0017817 | 0.0024203 | -0.073242 | 61.8484 | -61.8393 | 61.5326 | 61.5234 | -61.8988 | -0.082397 | -0.1831 | 61.8576 | -61.6608 | 61.7157 | -0.96588 | -61.7935 | -61.3174 | -0.24719 | 0.096131 | -0.21973 | 123.1155 | 61.5097 | -0.3067 | 61.7569 | -0.05951 | -0.068665 | 0.10529 | -0.036621 | 60.6262 | 0.27466 | -0.20142 | 0.34332 | -0.13275 | 123.3627 | 123.3719 | 60.6949 | 123.3765 | 123.6877 | 123.5184 | 123.4406 | 123.4497 | -123.5916 | -123.4131 | 123.1247 | 123.3078 | 61.5189 | 61.409
149.9844 | 123.4955 | -61.5921 | 61.7798 | -0.035705 | 0.00023068 | 0.0015979 | 0.0015914 | -0.0026596 | 0.0023478 | 0.002038 | -0.015564 | 0.0011964 | 0.034113 | 0.034171 | -0.00022434 | -0.00078189 | 0.00071145 | -0.027466 | 61.8668 | -61.8439 | 61.5921 | 61.5967 | -61.853 | -0.036621 | 0.004578 | 61.8393 | -61.6562 | 61.7798 | -0.9201 | -61.7249 | -61.2625 | -0.25177 | 0.086975 | -0.18768 | 123.1888 | 61.5555 | -0.26093 | 61.8073 | -0.009155 | -0.064087 | 0.059509 | 0 | 60.672 | 0.32959 | -0.13275 | 0.39368 | -0.068665 | 123.4406 | 123.436 | 60.7361 | 123.436 | 123.7106 | 123.4955 | 123.4589 | 123.4314 | -123.6237 | -123.436 | 123.1842 | 123.3719 | 61.5646 | 61.5967
150.9844 | 123.5138 | -61.5646 | 61.7935 | -0.020447 | 0.0010853 | 0.0011707 | 0.001805 | 0.0011856 | -0.00042943 | 0.0022516 | -0.027771 | -8.5416e-05 | 0.034327 | 0.037162 | 0.00063026 | 0.0037043 | 0.0015659 | -0.14648 | 61.8484 | -61.8622 | 61.5234 | 61.496 | -61.9125 | -0.11444 | -0.17395 | 61.821 | -61.6882 | 61.5829 | -0.63629 | -61.7065 | -61.3358 | -0.29755 | 0.054932 | -0.27008 | 123.0606 | 61.4502 | -0.3479 | 61.7477 | -0.050354 | -0.1236 | 0.027466 | -0.21057 | 60.9283 | 0.22888 | -0.14191 | 0.35248 | -0.018311 | 123.3582 | 123.3856 | 61.0519 | 123.2712 | 123.7106 | 123.5092 | 123.4131 | 123.3856 | -123.6557 | -123.4818 | 123.0881 | 123.1476 | 61.4182 | 61.3907
152 | 123.5413 | -61.5509 | 61.7432 | -0.043335 | 0.0019397 | -0.00032469 | -0.00054478 | 0.00054476 | -0.00064303 | -0.0028754 | 0.075989 | -0.0022216 | 0.034541 | 0.035453 | -0.00022434 | -0.00099549 | 0.0045567 | -0.09613 | 61.8301 | -61.7935 | 61.5921 | 61.5967 | -61.8256 | -0.022888 | -0.086975 | 61.7889 | -61.6653 | 61.8256 | -0.85144 | -61.6562 | -61.235 | -0.24262 | 0.086975 | -0.15106 | 123.1476 | 61.528 | -0.27466 | 61.7706 | -0.032044 | -0.11444 | 0.045776 | 0.082398 | 60.6995 | 0.31586 | -0.10529 | 0.4303 | 0.009155 | 123.3902 | 123.3856 | 60.8139 | 123.4909 | 123.6237 | 123.4543 | 123.381 | 123.3398 | -123.5367 | -123.4085 | 123.143 | 123.3765 | 61.4548 | 61.4639
152.9844 | 123.3902 | -61.6425 | 61.7249 | 0.010071 | -0.00062372 | 0.0018115 | 0.001805 | -9.604e-05 | -0.0027792 | -9.8356e-05 | -0.055237 | -0.0013672 | 0.033045 | 0.027762 | -0.0019333 | 0.0022089 | 0.00049765 | -0.13733 | 61.853 | -61.8759 | 61.5097 | 61.4731 | -61.9446 | -0.11444 | -0.17853 | 61.8439 | -61.6745 | 61.7523 | -0.98419 | -61.7798 | -61.3037 | -0.23346 | 0.12817 | -0.21515 | 123.1155 | 61.528 | -0.30212 | 61.7615 | -0.068664 | -0.032044 | 0.11902 | 0.027465 | 60.6583 | 0.33875 | -0.13733 | 0.37079 | -0.10528 | 123.349 | 123.3856 | 60.6903 | 123.4268 | 123.7289 | 123.5184 | 123.4955 | 123.4863 | -123.6008 | -123.3994 | 123.1522 | 123.3948 | 61.5051 | 61.4639
153.9844 | 123.4955 | -61.5784 | 61.7798 | -0.028076 | 0.0012989 | -0.00096549 | 0.00095062 | 0.0016128 | -0.0014974 | -0.0028754 | -0.033875 | 0.0026916 | 0.034327 | 0.029899 | -0.0015059 | 0.0019953 | 7.0452e-05 | 0.004578 | 61.8484 | -61.8347 | 61.5921 | 61.5875 | -61.8347 | -0.009155 | 0 | 61.8484 | -61.6425 | 61.8073 | -0.91553 | -61.7111 | -61.2625 | -0.25635 | 0.068665 | -0.18768 | 123.1659 | 61.5692 | -0.25635 | 61.8256 | 0 | -0.064087 | 0.068665 | 0.027466 | 60.6628 | 0.31586 | -0.13275 | 0.37994 | -0.068665 | 123.4222 | 123.4268 | 60.7269 | 123.4497 | 123.6832 | 123.4909 | 123.4268 | 123.4268 | -123.6145 | -123.4222 | 123.1705 | 123.3856 | 61.5829 | 61.5784
154.9844 | 123.4818 | -61.6058 | 61.7706 | -0.066223 | 0.00044428 | 0.0011707 | 0.0028732 | 0.0016128 | -0.00064303 | -0.0041572 | -0.024719 | 0.0016236 | 0.034113 | 0.035026 | 0.00020286 | 7.2706e-05 | 0.0030613 | -0.1236 | 61.853 | -61.8439 | 61.4914 | 61.4594 | -61.9583 | -0.13275 | -0.16479 | 61.821 | -61.6699 | 61.7615 | -0.96588 | -61.7798 | -61.3174 | -0.23804 | 0.082397 | -0.27924 | 123.0652 | 61.4731 | -0.35248 | 61.7111 | -0.11444 | -0.064087 | 0.050354 | -0.009155 | 60.64 | 0.28839 | -0.17395 | 0.35248 | -0.10986 | 123.3032 | 123.3353 | 60.704 | 123.4314 | 123.6969 | 123.4909 | 123.4589 | 123.4268 | -123.6145 | -123.4406 | 123.0972 | 123.3673 | 61.4822 | 61.441
155.9844 | 123.4818 | -61.5326 | 61.7798 | 0.032959 | 0.0019397 | -0.00075189 | 0.00095062 | 0.0011856 | -0.001711 | 0.0024652 | -0.04303 | 0.00141 | 0.032405 | 0.035453 | 0.00020286 | -0.0020637 | -0.0029201 | -0.036621 | 61.8622 | -61.8118 | 61.6425 | 61.4685 | -61.8988 | -0.018311 | 0.027466 | 61.8393 | -61.6562 | 61.8073 | -0.90179 | -61.702 | -61.2442 | -0.27924 | 0.082398 | -0.13733 | 123.0011 | 61.5143 | -0.36621 | 61.7935 | -0.086975 | -0.1236 | 0.059509 | 0.027466 | 60.6308 | 0.28839 | -0.16937 | 0.41199 | -0.045776 | 123.2803 | 123.4543 | 60.7544 | 123.4634 | 123.674 | 123.4955 | 123.3948 | 123.3719 | -123.5916 | -123.436 | 123.175 | 123.3398 | 61.496 | 61.5601
157 | 123.6053 | -61.5234 | 61.7706 | 0.02533 | 0.00087168 | 0.00031611 | -0.0016128 | 0.0013992 | 0.001066 | -0.0024482 | 0.072937 | -8.5416e-05 | 0.037318 | 0.030112 | -0.0015059 | -0.0029181 | 0.00092505 | -0.018311 | 61.853 | -61.7935 | 61.6608 | 61.6928 | -61.734 | 0.082397 | 0.14191 | 61.8073 | -61.6196 | 61.908 | -0.75531 | -61.528 | -61.1481 | -0.27008 | 0.082397 | -0.10986 | 123.2162 | 61.6058 | -0.21057 | 61.8759 | 0.059509 | -0.096131 | 0.036621 | 0.13733 | 60.7681 | 0.37537 | -0.004578 | 0.4715 | 0.091553 | 123.4863 | 123.4543 | 60.8643 | 123.5275 | 123.6465 | 123.4268 | 123.3765 | 123.3307 | -123.5641 | -123.3902 | 123.1842 | 123.4314 | 61.5051 | 61.6653
157.9844 | 123.4818 | -61.5875 | 61.7889 | -0.058594 | 1.7082e-05 | 0.00095711 | 0.00073702 | 0.0013992 | -0.00085663 | 0.0018242 | -0.055237 | -0.0013672 | 0.032832 | 0.034812 | -0.00022434 | 0.0011407 | -0.0018521 | -0.041199 | 61.8439 | -61.8439 | 61.5784 | 61.5463 | -61.8713 | -0.059509 | -0.054932 | 61.853 | -61.6837 | 61.7798 | -0.93842 | -61.7249 | -61.2671 | -0.25635 | 0.054932 | -0.21057 | 123.1338 | 61.528 | -0.28381 | 61.7844 | -0.027466 | -0.096131 | 0.064087 | -0.009155 | 60.6491 | 0.32043 | -0.13733 | 0.41656 | -0.041199 | 123.3902 | 123.4222 | 60.7452 | 123.4634 | 123.6877 | 123.5367 | 123.4314 | 123.4406 | -123.6328 | -123.4726 | 123.1659 | 123.3673 | 61.5463 | 61.5326
158.9844 | 123.4863 | -61.6058 | 61.7615 | 0.0024415 | 0.00087168 | 0.00074331 | 0.00095062 | 0.0018266 | -0.0014974 | 0.0011834 | 0.054626 | -8.5416e-05 | 0.033686 | 0.03118 | 0.00041666 | 0.0015679 | 0.0028477 | -0.11902 | 61.853 | -61.8805 | 61.5234 | 61.496 | -62.0773 | -0.36621 | -0.15564 | 61.8668 | -61.6791 | 61.7752 | -0.98419 | -61.7386 | -61.2808 | -0.27466 | 0.091552 | -0.23804 | 123.1018 | 61.2396 | -0.4715 | 61.5143 | -0.19684 | -0.073242 | 0.10529 | 0.013733 | 60.6216 | 0.32501 | -0.13275 | 0.39825 | -0.059509 | 123.3765 | 123.4039 | 60.6949 | 123.4543 | 123.7335 | 123.5458 | 123.4589 | 123.4726 | -123.642 | -123.4406 | 123.1293 | 123.381 | 61.4868 | 61.4502
159.9844 | 123.5046 | -61.5738 | 61.7889 | -0.012817 | 0.00065788 | 0.0020251 | -0.00054478 | -0.0026596 | 0.0012796 | 0.0054558 | -0.039978 | 0.00141 | 0.032618 | 0.040793 | 0.0012711 | -0.00078189 | 0.0041293 | -0.036621 | 61.8484 | -61.821 | 61.5784 | 61.5784 | -61.8393 | -0.032043 | -0.036621 | 61.853 | -61.6608 | 61.7889 | -0.93384 | -61.7111 | -61.2808 | -0.24719 | 0.05951 | -0.21057 | 123.1522 | 61.5417 | -0.2655 | 61.7889 | -0.01831 | -0.086975 | 0.064087 | 0 | 60.64 | 0.29297 | -0.13733 | 0.37994 | -0.050354 | 123.3994 | 123.3994 | 60.7269 | 123.4497 | 123.6694 | 123.5138 | 123.4222 | 123.4268 | -123.6099 | -123.4497 | 123.1522 | 123.3627 | 61.5372 | 61.5372
160.9844 | 123.4726 | -61.5555 | 61.7752 | 0.0024415 | 0.0010853 | 0.0013843 | 0.0013778 | 0.0013992 | -0.0014974 | 0.00096984 | -0.018616 | -0.00029902 | 0.033259 | 0.034598 | -0.0023605 | -0.0014227 | -0.0016385 | -0.11902 | 61.8439 | -61.8622 | 61.528 | 61.4914 | -61.9308 | -0.11444 | -0.17395 | 61.8576 | -61.6882 | 61.7432 | -0.95673 | -61.6882 | -61.2671 | -0.3067 | 0.068664 | -0.24719 | 123.0469 | 61.441 | -0.37537 | 61.7477 | -0.068664 | -0.13275 | 0.082397 | -0.032044 | 60.5988 | 0.28839 | -0.13275 | 0.42114 | 0 | 123.3536 | 123.3902 | 60.7315 | 123.4314 | 123.7061 | 123.5458 | 123.3994 | 123.4131 | -123.6374 | -123.4634 | 123.0835 | 123.2986 | 61.4365 | 61.3815
161.9844 | 123.587 | -61.5417 | 61.7477 | -0.058594 | -0.00019652 | 0.0020251 | -0.002681 | -0.0030868 | -0.00021583 | -0.0026618 | 0.057678 | -0.00094002 | 0.035395 | 0.027762 | 0.00041666 | -0.0018499 | -0.0063381 | -0.064087 | 61.8347 | -61.7935 | 61.6287 | 61.6287 | -61.7661 | 0.059509 | 0.013733 | 61.8118 | -61.6196 | 61.8484 | -0.81024 | -61.5921 | -61.1755 | -0.25177 | 0.086975 | -0.11902 | 123.1705 | 61.6013 | -0.2243 | 61.853 | 0.027466 | -0.07782 | 0.064087 | 0.10071 | 60.7315 | 0.36621 | -0.050354 | 0.44403 | 0.027466 | 123.4222 | 123.4222 | 60.8093 | 123.468 | 123.6282 | 123.4314 | 123.3765 | 123.3536 | -123.5413 | -123.3673 | 123.1705 | 123.3902 | 61.4777 | 61.5555
162.9844 | 123.4177 | -61.6425 | 61.7386 | -0.043335 | 0.00087168 | 0.00052971 | 0.0011642 | 0.0024674 | 0.00021157 | -0.00052556 | -0.055237 | 0.00076898 | 0.033473 | 0.039298 | -0.0015059 | 0.0011407 | 0.00071145 | -0.12817 | 61.8622 | -61.8896 | 61.5051 | 61.4639 | -61.94 | -0.11444 | -0.16022 | 61.8347 | -61.702 | 61.7523 | -0.98419 | -61.7249 | -61.4777 | -0.24719 | 0.1236 | -0.23346 | 123.1064 | 61.528 | -0.29755 | 61.7752 | -0.050354 | -0.059509 | 0.096131 | 0.013733 | 60.6583 | 0.1648 | -0.082398 | 0.2243 | -0.022889 | 123.3536 | 123.3948 | 60.7178 | 123.4543 | 123.7518 | 123.5367 | 123.5046 | 123.4772 | -123.6282 | -123.4406 | 123.1476 | 123.3948 | 61.5143 | 61.4822
163.9844 | 123.4772 | -61.5555 | 61.7981 | -0.020447 | 0.0010853 | 0.0013843 | 0.00095062 | 0.0035354 | 0.0029886 | 0.00011544 | -0.064392 | -0.00051262 | 0.035395 | 0.037376 | -0.00043794 | 0.00071351 | 0.0013523 | -0.07782 | 61.8622 | -61.853 | 61.5646 | 61.528 | -61.8713 | -0.07782 | -0.086975 | 61.8347 | -61.6837 | 61.7615 | -0.96588 | -61.7477 | -61.2946 | -0.29755 | 0.064087 | -0.23346 | 123.0835 | 61.4777 | -0.31586 | 61.7752 | -0.018311 | -0.12817 | 0.036621 | -0.036621 | 60.5896 | 0.26093 | -0.19226 | 0.3891 | -0.064087 | 123.381 | 123.4177 | 60.7178 | 123.4451 | 123.7152 | 123.5184 | 123.4177 | 123.3902 | -123.6511 | -123.4818 | 123.1201 | 123.317 | 61.4777 | 61.4685
164.9844 | 123.4818 | -61.5921 | 61.7294 | -0.012817 | 0.0034351 | 0.00010251 | 0.0011642 | 0.0035354 | 0.00021157 | -0.00095276 | -0.04303 | 0.0016236 | 0.034113 | 0.033744 | -0.00043794 | 7.2706e-05 | -0.0016385 | -0.30212 | 61.8027 | -61.8759 | 61.5051 | 61.5326 | -61.8988 | -0.11444 | -0.16479 | 61.8484 | -61.6928 | 61.7706 | -0.94757 | -61.7523 | -61.2808 | -0.28381 | 0.073242 | -0.2243 | 123.1247 | 61.4777 | -0.3067 | 61.7615 | -0.022888 | -0.10071 | 0.11902 | 0.041199 | 60.6445 | 0.31128 | -0.16022 | 0.41199 | -0.059509 | 123.4085 | 123.381 | 60.7452 | 123.4634 | 123.6786 | 123.5413 | 123.3948 | 123.4406 | -123.6053 | -123.4222 | 123.0972 | 123.3627 | 61.29 | 61.4273
165.9844 | 123.5001 | -61.5692 | 61.7661 | -0.028076 | 0.0017261 | 0.00010251 | 0.0011642 | 0.0020402 | 0.00063877 | 0.00054264 | -0.04303 | 0.0011964 | 0.033045 | 0.035453 | -0.0023605 | 0.0011407 | -0.0014249 | -0.050354 | 61.853 | -61.8439 | 61.5738 | 61.5601 | -61.8759 | -0.064087 | -0.064087 | 61.8393 | -61.6562 | 61.7752 | -0.94299 | -61.734 | -61.2808 | -0.27466 | 0.086975 | -0.19226 | 123.1293 | 61.5051 | -0.3067 | 61.7798 | -0.032044 | -0.086975 | 0.073242 | 0.009156 | 60.6262 | 0.28839 | -0.16479 | 0.37537 | -0.07782 | 123.4039 | 123.4177 | 60.7132 | 123.4314 | 123.6969 | 123.4955 | 123.4222 | 123.4085 | -123.6099 | -123.4222 | 123.143 | 123.3444 | 61.5189 | 61.5051
167 | 123.5733 | -61.5372 | 61.734 | -0.043335 | -0.00062372 | -0.00075189 | -0.002681 | -0.0020188 | -0.0012838 | 0.00032904 | 0.063782 | 0.00055538 | 0.036463 | 0.029258 | 0.00084386 | -0.0022773 | -0.0016385 | -0.068665 | 61.821 | -61.7752 | 61.615 | 61.6241 | -61.8164 | 0.009155 | -0.027466 | 61.7981 | -61.6425 | 61.8439 | -0.81482 | -61.6013 | -61.1984 | -0.23804 | 0.086975 | -0.11902 | 123.1613 | 61.5463 | -0.27924 | 61.7844 | -0.041198 | -0.10529 | 0.064087 | 0.10986 | 60.7224 | 0.33875 | -0.064087 | 0.44403 | 0.041199 | 123.3994 | 123.3902 | 60.8276 | 123.4863 | 123.5962 | 123.4406 | 123.3582 | 123.3353 | -123.5092 | -123.3765 | 123.1522 | 123.381 | 61.4685 | 61.5097
167.9844 | 123.5092 | -61.5967 | 61.7889 | -0.005188 | 0.0025805 | 0.00095711 | 0.00073702 | 0.00033116 | 0.00063877 | 0.001397 | -0.055237 | 0.00141 | 0.033686 | 0.038016 | -0.0025741 | -0.00078189 | -0.0029201 | -0.032043 | 61.8576 | -61.8347 | 61.5829 | 61.5646 | -61.8484 | -0.032043 | -0.036621 | 61.853 | -61.647 | 61.7706 | -0.92926 | -61.7203 | -61.2762 | -0.23804 | 0.068665 | -0.20599 | 123.1613 | 61.5646 | -0.25177 | 61.8027 | -0.013733 | -0.050354 | 0.064087 | -0.01831 | 60.6674 | 0.32043 | -0.1236 | 0.37079 | -0.073242 | 123.3994 | 123.4177 | 60.7178 | 123.4177 | 123.6923 | 123.5001 | 123.4543 | 123.4497 | -123.6237 | -123.436 | 123.1796 | 123.3673 | 61.5646 | 61.5601
168.9844 | 123.4406 | -61.5875 | 61.7935 | -0.058594 | 0.0019397 | 0.00052971 | 0.00030982 | -0.00052344 | 0.0012796 | -0.00095276 | -0.046082 | 0.0022644 | 0.033259 | 0.03353 | -0.0023605 | -0.0024909 | -0.00078395 | -0.11902 | 61.8347 | -61.8622 | 61.5189 | 61.4822 | -61.9171 | -0.11902 | -0.16022 | 61.8256 | -61.6882 | 61.8347 | -1.0345 | -61.6653 | -61.2488 | -0.27466 | 0.041199 | -0.27466 | 123.0698 | 61.4685 | -0.32959 | 61.7432 | -0.054931 | -0.10071 | 0.032044 | 0.041199 | 60.553 | 0.33875 | -0.07782 | 0.43945 | 0.022888 | 123.3444 | 123.381 | 60.6537 | 123.5229 | 123.6969 | 123.5138 | 123.4222 | 123.4131 | -123.6557 | -123.4818 | 123.1064 | 123.4222 | 61.4685 | 61.4273
169.9844 | 123.4909 | -61.5646 | 61.7615 | 0.02533 | -0.0010511 | 0.0020251 | 0.00095062 | 0.00011756 | 0.001066 | -9.8356e-05 | -0.04303 | 0.00034178 | 0.032618 | 0.034812 | -0.0012923 | -0.00056829 | 0.0032749 | -0.032043 | 61.8484 | -61.8256 | 61.615 | 61.6058 | -61.8439 | -0.018311 | -0.013733 | 61.8393 | -61.6425 | 61.7981 | -0.90179 | -61.7065 | -61.2671 | -0.26093 | 0.086975 | -0.14648 | 123.1705 | 61.5463 | -0.27924 | 61.8073 | -0.01831 | -0.07782 | 0.077819 | 0.036621 | 60.6628 | 0.29755 | -0.14191 | 0.37537 | -0.064087 | 123.4314 | 123.4406 | 60.7407 | 123.4406 | 123.674 | 123.4818 | 123.4131 | 123.4039 | -123.587 | -123.4039 | 123.1796 | 123.3627 | 61.5326 | 61.5509
170.9844 | 123.4726 | -61.5967 | 61.7752 | -0.028076 | 0.00087168 | -0.00032469 | -0.00054478 | -0.00030984 | 0.00063877 | -0.0018072 | -0.036926 | 0.0020508 | 0.034754 | 0.032035 | -0.0012923 | 0.00092711 | -0.00078395 | -0.11902 | 61.8576 | -61.8622 | 61.5189 | 61.5143 | -61.9171 | -0.11444 | -0.16479 | 61.8256 | -61.6928 | 61.7844 | -0.9613 | -61.734 | -61.2991 | -0.2655 | 0.082397 | -0.25635 | 123.111 | 61.4822 | -0.32043 | 61.7477 | -0.054931 | -0.09613 | 0.050354 | 0.009155 | 60.6354 | 0.29755 | -0.13733 | 0.39368 | -0.041199 | 123.3765 | 123.381 | 60.7315 | 123.4772 | 123.7198 | 123.5184 | 123.4543 | 123.4222 | -123.6374 | -123.468 | 123.1155 | 123.381 | 61.4777 | 61.4319
171.9844 | 123.4589 | -61.5738 | 61.7844 | -0.081482 | 0.0027943 | -0.00011109 | 0.001805 | -0.00095064 | -2.232e-06 | -0.0033026 | -0.064392 | 0.00055538 | 0.034968 | 0.032889 | 0.0010575 | 0.00028631 | -0.0035611 | -0.07782 | 61.8576 | -61.8439 | 61.5646 | 61.5555 | -61.8576 | -0.064087 | -0.068665 | 61.8576 | -61.647 | 61.7844 | -0.94757 | -61.7523 | -61.2854 | -0.27008 | 0.073242 | -0.21973 | 123.1293 | 61.5097 | -0.28381 | 61.7798 | -0.013733 | -0.073242 | 0.073242 | 0 | 60.6262 | 0.28839 | -0.17853 | 0.36163 | -0.10529 | 123.3994 | 123.4085 | 60.6995 | 123.4314 | 123.7015 | 123.5046 | 123.4314 | 123.4314 | -123.6282 | -123.4314 | 123.1384 | 123.3582 | 61.496 | 61.5051
172.9844 | 123.4863 | -61.5829 | 61.7615 | -0.005188 | 0.0017261 | 0.0011707 | 0.004155 | 0.0016128 | 0.00063877 | 0.00054264 | -0.036926 | 0.00141 | 0.033686 | 0.03054 | -0.00022434 | 0.00049991 | -0.00078395 | -0.10529 | 61.8393 | -61.8713 | 61.7615 | 61.5921 | -61.9675 | -0.059509 | -0.16479 | 61.8439 | -61.6608 | 61.7615 | -0.97046 | -61.7706 | -61.3129 | -0.28839 | 0.077819 | 0 | 123.175 | 61.5234 | -0.38452 | 61.8118 | -0.09613 | -0.07782 | 0.082397 | 0 | 60.6125 | 0.27008 | -0.18768 | 0.3479 | -0.10986 | 123.4634 | 123.6328 | 60.6903 | 123.4222 | 123.7106 | 123.5046 | 123.4222 | 123.4268 | -123.6328 | -123.4222 | 123.3444 | 123.3444 | 61.4777 | 61.4182
173.9844 | 123.4863 | -61.5646 | 61.7661 | -0.012817 | 0.00023068 | 0.0011707 | 0.00030982 | 0.00054476 | 0.00063877 | -0.00073916 | -0.021668 | 0.0018372 | 0.035395 | 0.026267 | 0.00020286 | 0.00092711 | -0.0033475 | -0.045776 | 61.8805 | -61.8393 | 61.5738 | 61.5692 | -61.8484 | -0.036621 | -0.041199 | 61.8393 | -61.6699 | 61.7798 | -0.92468 | -61.7294 | -61.2762 | -0.27466 | 0.11444 | -0.19226 | 123.1338 | 61.528 | -0.28381 | 61.8027 | -0.009156 | -0.10529 | 0.073242 | 0.013733 | 60.64 | 0.28839 | -0.16479 | 0.39368 | -0.059509 | 123.4085 | 123.4131 | 60.7452 | 123.4497 | 123.7198 | 123.5092 | 123.4451 | 123.4039 | -123.6053 | -123.436 | 123.1384 | 123.3444 | 61.5189 | 61.5234
174.9844 | 123.5321 | -61.5738 | 61.7432 | -0.081482 | -0.00041012 | -0.00075189 | 0.00030982 | -0.00095064 | 0.0014932 | -0.00373 | -0.0033569 | 0.0011964 | 0.033045 | 0.031608 | -0.00086514 | -0.00035469 | 0.00049765 | -0.11902 | 61.8393 | -61.8347 | 61.528 | 61.5189 | -61.8988 | -0.10529 | -0.16022 | 61.8027 | -61.6791 | 61.7935 | -0.92926 | -61.7294 | -61.2534 | -0.26093 | 0.09613 | -0.21515 | 123.0927 | 61.4685 | -0.32501 | 61.7294 | -0.064087 | -0.10529 | 0.059509 | 0.050354 | 60.6445 | 0.32043 | -0.15564 | 0.42572 | -0.050354 | 123.3536 | 123.3627 | 60.7498 | 123.4726 | 123.674 | 123.4818 | 123.4131 | 123.3765 | -123.5779 | -123.4222 | 123.1018 | 123.3673 | 61.4548 | 61.4136
175.9844 | 123.4589 | -61.5967 | 61.7844 | -0.035705 | 0.0012989 | 0.0013843 | 0.0013778 | 0.00075836 | -0.00042943 | -0.0015936 | -0.024719 | 0.00034178 | 0.034113 | 0.032249 | 0.00041666 | 0.00092711 | -0.0050565 | -0.064087 | 61.8393 | -61.8439 | 61.5417 | 61.5463 | -61.8851 | -0.064087 | -0.11444 | 61.8484 | -61.6653 | 61.7523 | -0.97961 | -61.7615 | -61.2946 | -0.24719 | 0.054931 | -0.24262 | 123.143 | 61.5326 | -0.28839 | 61.7798 | -0.041199 | -0.068664 | 0.064087 | -0.032044 | 60.6171 | 0.30212 | -0.16479 | 0.37079 | -0.096131 | 123.3902 | 123.3856 | 60.6857 | 123.4177 | 123.6832 | 123.5138 | 123.436 | 123.4451 | -123.6282 | -123.4497 | 123.1384 | 123.349 | 61.5326 | 61.4822
176.9844 | 123.4406 | -61.6104 | 61.7706 | -0.050964 | 0.00065788 | 0.0013843 | 0.00073702 | 0.0028946 | 0.0014932 | -0.0018072 | -0.067444 | 0.00012818 | 0.032191 | 0.034385 | -0.0010787 | -0.00014089 | 0.0026341 | -0.10071 | 61.8668 | -61.8622 | 61.5143 | 61.4594 | -61.9354 | -0.14648 | -0.16937 | 61.8301 | -61.6745 | 61.7523 | -0.96588 | -61.7798 | -61.2991 | -0.25177 | 0.09613 | -0.25635 | 123.0698 | 61.4639 | -0.32501 | 61.7157 | -0.073242 | -0.064087 | 0.059509 | -0.018311 | 60.6445 | 0.31128 | -0.16937 | 0.37537 | -0.10528 | 123.3215 | 123.3765 | 60.7086 | 123.4268 | 123.7289 | 123.5046 | 123.4772 | 123.4406 | -123.6328 | -123.4451 | 123.1247 | 123.3627 | 61.5097 | 61.441
177.9844 | 123.4589 | -61.5784 | 61.8027 | 0.078736 | -0.0014783 | 0.0015979 | 0.001805 | 0.0011856 | 0.00085237 | 0.002038 | -0.046082 | -0.00029902 | 0.032832 | 0.033317 | 0.00020286 | 0.00071351 | -0.0024929 | -0.041199 | 61.8393 | -61.8393 | 61.5555 | 61.5509 | -61.8668 | -0.068665 | -0.059509 | 61.8393 | -61.6699 | 61.7752 | -0.92926 | -61.7249 | -61.2762 | -0.26093 | 0.036621 | -0.24719 | 123.1293 | 61.5097 | -0.28839 | 61.7706 | -0.027466 | -0.091553 | 0.036621 | -0.027465 | 60.6491 | 0.30212 | -0.14648 | 0.39368 | -0.054932 | 123.3902 | 123.3948 | 60.7407 | 123.4451 | 123.6786 | 123.5092 | 123.4177 | 123.4177 | -123.642 | -123.4726 | 123.1338 | 123.3536 | 61.5372 | 61.5189
178.9844 | 123.4818 | -61.5875 | 61.7935 | -0.012817 | -0.0019055 | 0.00031611 | -0.0018266 | 0.0020402 | -2.232e-06 | 0.00054264 | -0.10406 | 0.0026916 | 0.033259 | 0.031821 | 0.0010575 | 0.00028631 | -0.00099755 | -0.11444 | 61.8256 | -61.8576 | 61.5143 | 61.5005 | -61.9171 | -0.11902 | -0.37079 | 61.7752 | -61.7203 | 61.7386 | -0.92926 | -61.7661 | -61.3037 | -0.27008 | 0.032044 | -0.27924 | 123.0881 | 61.4685 | -0.32959 | 61.7386 | -0.059509 | -0.13275 | -0.01831 | -0.054932 | 60.6583 | 0.28381 | -0.17853 | 0.41656 | -0.045776 | 123.3582 | 123.3719 | 60.791 | 123.4589 | 123.6832 | 123.4955 | 123.4131 | 123.3627 | -123.6511 | -123.5138 | 123.1018 | 123.3261 | 61.4731 | 61.2167
179.9844 | 123.4955 | -61.5738 | 61.7752 | 0.040589 | 0.0027943 | 0.00031611 | 0.00030982 | 0.0022538 | 0.0012796 | -0.002021 | -0.039978 | 0.00034178 | 0.036036 | 0.034171 | 0.0010575 | -0.0014227 | -0.0016385 | -0.041199 | 61.8393 | -61.8393 | 61.5967 | 61.5921 | -61.8439 | -0.027466 | -0.004578 | 61.853 | -61.6699 | 61.7752 | -0.94757 | -61.7065 | -61.2762 | -0.2655 | 0.064086 | -0.17853 | 123.1659 | 61.5463 | -0.27008 | 61.8118 | -0.004578 | -0.09613 | 0.077819 | 0 | 60.6262 | 0.29755 | -0.13275 | 0.39368 | -0.036621 | 123.4314 | 123.436 | 60.7224 | 123.4451 | 123.6786 | 123.5229 | 123.4131 | 123.4268 | -123.6145 | -123.4451 | 123.1705 | 123.349 | 61.5326 | 61.5692
180.9844 | 123.3627 | -61.6379 | 61.7111 | 0.0024415 | 1.7082e-05 | -0.00032469 | 0.0015914 | 0.00033116 | -0.00085663 | 0.0024652 | -0.04303 | -0.00029902 | 0.034541 | 0.033744 | -1.0744e-05 | -0.0018499 | -0.00035675 | -0.11444 | 61.8393 | -61.8622 | 61.4914 | 61.4685 | -61.9354 | -0.10986 | -0.17395 | 61.853 | -61.6974 | 61.7706 | -0.97961 | -61.7706 | -61.2305 | -0.22431 | 0.12817 | -0.21973 | 123.1064 | 61.528 | -0.29755 | 61.7523 | -0.073242 | -0.05951 | 0.14191 | 0.059509 | 60.6583 | 0.40741 | -0.13275 | 0.46692 | -0.073242 | 123.3307 | 123.3536 | 60.7178 | 123.468 | 123.7015 | 123.5504 | 123.4772 | 123.4909 | -123.5733 | -123.4085 | 123.1293 | 123.4085 | 61.5234 | 61.4639
181.9844 | 123.4863 | -61.6104 | 61.8027 | -0.043335 | -0.0010511 | 0.0018115 | 0.00073702 | -0.00095064 | -0.00021583 | -0.00095276 | -0.04303 | 0.0026916 | 0.034541 | 0.035453 | 0.0014847 | 0.0011407 | 0.0030613 | -0.073242 | 61.8668 | -61.8256 | 61.5646 | 61.5692 | -61.8622 | -0.064087 | -0.082397 | 61.8439 | -61.6699 | 61.7752 | -0.94299 | -61.7386 | -61.2717 | -0.21515 | 0.064087 | -0.23804 | 123.1796 | 61.5463 | -0.25177 | 61.7615 | -0.036621 | -0.059509 | 0.041199 | -0.027465 | 60.6674 | 0.33875 | -0.12817 | 0.39825 | -0.068664 | 123.3948 | 123.3902 | 60.7269 | 123.4451 | 123.6923 | 123.5138 | 123.4772 | 123.4543 | -123.6282 | -123.4726 | 123.175 | 123.3856 | 61.5372 | 61.528
182.9844 | 123.4406 | -61.6287 | 61.7661 | 0.010071 | 0.0012989 | 0.0013843 | -0.00075838 | 0.0022538 | -0.00085663 | 0.00054264 | -0.027771 | 0.00012818 | 0.035822 | 0.030753 | 0.00041666 | -0.00078189 | -0.0029201 | -0.073242 | 61.8576 | -61.8622 | 61.5097 | 61.4868 | -61.94 | -0.086975 | -0.17395 | 61.8347 | -61.6882 | 61.7249 | -0.97504 | -61.7935 | -61.3312 | -0.23346 | 0.091553 | -0.25635 | 123.1155 | 61.5417 | -0.31128 | 61.7752 | -0.077819 | -0.059509 | 0.068665 | -0.041198 | 60.6537 | 0.29755 | -0.16479 | 0.35706 | -0.10529 | 123.349 | 123.3719 | 60.7132 | 123.4131 | 123.7198 | 123.5229 | 123.4863 | 123.4634 | -123.6282 | -123.4543 | 123.1384 | 123.3536 | 61.5555 | 61.4548
183.9844 | 123.4818 | -61.5738 | 61.8027 | 0.0177 | 0.0010853 | 0.00074331 | 9.6222e-05 | -9.604e-05 | -0.00042943 | 0.0024652 | -0.039978 | 0.002478 | 0.036036 | 0.040366 | -0.0034287 | -0.0022773 | -0.0029201 | -0.027466 | 61.8668 | -61.821 | 61.5692 | 61.5921 | -61.853 | -0.036621 | -0.036621 | 61.8484 | -61.6699 | 61.7706 | -0.94299 | -61.7294 | -61.2808 | -0.24719 | 0.064087 | -0.23346 | 123.1659 | 61.5372 | -0.27923 | 61.7844 | -0.032043 | -0.09613 | 0.045777 | -0.032043 | 60.6308 | 0.29297 | -0.15564 | 0.3891 | -0.059509 | 123.4131 | 123.3902 | 60.7269 | 123.4406 | 123.6877 | 123.5184 | 123.4406 | 123.4222 | -123.6237 | -123.4726 | 123.143 | 123.3444 | 61.5463 | 61.5372
184.9844 | 123.4589 | -61.5646 | 61.7981 | -0.050964 | 0.0017261 | -0.00011109 | 0.0013778 | -9.604e-05 | 0.00021157 | -0.00052556 | -0.024719 | 0.00098258 | 0.034327 | 0.037589 | -0.00022434 | -0.00035469 | -0.00099755 | -0.12817 | 61.8576 | -61.853 | 61.5097 | 61.4914 | -61.9263 | -0.11444 | -0.1831 | 61.821 | -61.6745 | 61.5601 | -0.9201 | -61.5097 | -61.2076 | -0.28839 | 0.059509 | -0.28839 | 123.056 | 61.4502 | -0.36163 | 61.7386 | -0.073243 | -0.10986 | 0.022888 | -0.23804 | 60.6445 | 0.35706 | 0.054931 | 0.46692 | 0.1648 | 123.3444 | 123.3627 | 60.7544 | 123.2346 | 123.7106 | 123.4955 | 123.4222 | 123.3856 | -123.6511 | -123.4726 | 123.0743 | 123.1247 | 61.4365 | 61.3815
185.9844 | 123.5184 | -61.5463 | 61.7844 | -0.005188 | 1.7082e-05 | 0.00052971 | -0.0011856 | -0.001805 | -0.00021583 | 0.0024652 | -0.024719 | 0.00098258 | 0.034113 | 0.036094 | -0.0015059 | -0.0016363 | -0.0022793 | -0.013733 | 61.8439 | -61.8301 | 61.5967 | 61.5875 | -61.821 | -0.004578 | 0.004578 | 61.8484 | -61.6608 | 61.8118 | -0.90179 | -61.7111 | -61.2442 | -0.28381 | 0.059509 | -0.18768 | 123.1338 | 61.5417 | -0.27466 | 61.8256 | 0.009155 | -0.11444 | 0.064087 | 0.027466 | 60.6445 | 0.30212 | -0.16479 | 0.41656 | -0.050354 | 123.4177 | 123.4268 | 60.759 | 123.4726 | 123.674 | 123.5092 | 123.3902 | 123.3948 | -123.6145 | -123.4451 | 123.143 | 123.3582 | 61.5326 | 61.5509
186.9844 | 123.4818 | -61.5921 | 61.7661 | 0.010071 | 0.0019397 | 0.00095711 | 0.0011642 | 0.0028946 | -0.0025656 | 0.0026788 | -0.058289 | 0.0016236 | 0.034541 | 0.029471 | -0.00065154 | 0.00049991 | 0.0056247 | -0.11444 | 61.8668 | -61.8759 | 61.4822 | 61.4685 | -61.9308 | -0.11444 | -0.20142 | 61.853 | -61.7203 | 61.7432 | -0.97961 | -61.7661 | -61.2946 | -0.28381 | 0.10071 | -0.28381 | 123.0606 | 61.4777 | -0.33875 | 61.7615 | -0.054931 | -0.12817 | 0.086975 | -0.022888 | 60.6125 | 0.29755 | -0.17395 | 0.42572 | -0.045776 | 123.3444 | 123.3582 | 60.7407 | 123.4634 | 123.7427 | 123.5733 | 123.4589 | 123.4451 | -123.642 | -123.4863 | 123.0743 | 123.3353 | 61.4777 | 61.3907
187.9844 | 123.5321 | -61.5601 | 61.7844 | -0.035705 | 0.0019397 | 0.00095711 | -0.0016128 | -0.00052344 | -0.0010702 | 0.0011834 | -0.00030511 | 0.00076898 | 0.033259 | 0.031608 | -1.0744e-05 | -0.0018499 | -0.0027065 | -0.004578 | 61.8439 | -61.8256 | 61.5967 | 61.6013 | -61.821 | 0.022888 | 0.10986 | 61.8301 | -61.6562 | 61.8347 | -0.90179 | -61.6882 | -61.2305 | -0.2655 | 0.059509 | -0.18768 | 123.1613 | 61.5829 | -0.26093 | 61.8484 | 0.004578 | -0.09613 | 0.045776 | 0.050354 | 60.6583 | 0.32959 | -0.12817 | 0.42572 | -0.032043 | 123.4268 | 123.4222 | 60.7544 | 123.4909 | 123.6694 | 123.4863 | 123.4039 | 123.3902 | -123.6099 | -123.4406 | 123.1567 | 123.3948 | 61.5555 | 61.6699
188.9844 | 123.4726 | -61.6058 | 61.7798 | -0.005188 | 0.00044428 | -0.00053829 | 0.00030982 | 0.0018266 | -0.00021583 | 0.00096984 | -0.015564 | 0.00055538 | 0.034327 | 0.031394 | 0.0014847 | -0.0018499 | 0.00049765 | -0.091553 | 61.8668 | -61.8713 | 61.5143 | 61.4777 | -61.9354 | -0.091553 | -0.14191 | 61.8027 | -61.7203 | 61.7752 | -0.91553 | -61.8118 | -61.3083 | -0.2655 | 0.086975 | -0.2655 | 123.0835 | 61.5143 | -0.32959 | 61.7798 | -0.064087 | -0.11444 | 0.022888 | -0.004577 | 60.6903 | 0.29755 | -0.20599 | 0.41199 | -0.091553 | 123.349 | 123.3856 | 60.8047 | 123.4955 | 123.7381 | 123.5229 | 123.4726 | 123.4085 | -123.6511 | -123.5001 | 123.1201 | 123.381 | 61.5143 | 61.4639
189.9844 | 123.5138 | -61.5601 | 61.8027 | -0.005188 | 0.0030079 | 0.0026661 | 0.00030982 | -0.0022324 | 0.00063877 | 0.00054264 | -0.00030511 | -8.5416e-05 | 0.033045 | 0.036094 | -0.00043794 | -0.00099549 | -0.00078395 | 0.013733 | 61.8713 | -61.8301 | 61.5921 | 61.6013 | -61.8164 | 0.009155 | 0.036621 | 61.8622 | -61.6287 | 61.8256 | -0.89264 | -61.6653 | -61.2305 | -0.27008 | 0.068665 | -0.21057 | 123.1613 | 61.5692 | -0.25635 | 61.8393 | 0.013733 | -0.068664 | 0.05951 | 0.022889 | 60.6674 | 0.32959 | -0.10528 | 0.39825 | -0.036621 | 123.4314 | 123.4222 | 60.7361 | 123.4543 | 123.7015 | 123.4909 | 123.4314 | 123.4222 | -123.6328 | -123.4314 | 123.1522 | 123.3856 | 61.5738 | 61.5967
190.9844 | 123.5001 | -61.6013 | 61.7523 | -0.035705 | 0.00065788 | 0.0015979 | 0.0011642 | 0.0067398 | 0.00021157 | -9.8356e-05 | -0.036926 | 0.00055538 | 0.035182 | 0.035667 | 0.0016983 | 7.2706e-05 | -0.0012111 | -0.10529 | 61.853 | -61.8622 | 61.5051 | 61.4548 | -61.9354 | -0.11444 | -0.17395 | 61.8073 | -61.6791 | 61.7477 | -0.98877 | -61.7706 | -61.2946 | -0.26093 | 0.10071 | -0.24719 | 123.056 | 61.4868 | -0.33417 | 61.7477 | -0.073242 | -0.07782 | 0.054932 | -0.004577 | 60.6125 | 0.3067 | -0.16937 | 0.38452 | -0.091553 | 123.317 | 123.3673 | 60.6903 | 123.4268 | 123.7152 | 123.4863 | 123.4543 | 123.4085 | -123.6145 | -123.4314 | 123.1064 | 123.349 | 61.496 | 61.4273
191.9844 | 123.4955 | -61.5509 | 61.7615 | 0.0024415 | 0.0012989 | -0.0013929 | -0.00011758 | 0.00097196 | -0.0014974 | -0.0056526 | -0.0064087 | -0.00029902 | 0.035182 | 0.029258 | 0.00041666 | 0.00049991 | 0.00028405 | -0.013733 | 61.8622 | -61.8164 | 61.5051 | 61.5692 | -61.7477 | 0.004578 | 0.009155 | 61.8301 | -61.6608 | 61.8073 | -0.89722 | -61.6837 | -61.2213 | -0.2655 | 0.10071 | -0.25635 | 123.1201 | 61.5555 | -0.19684 | 61.821 | 0.068664 | -0.10986 | 0.068664 | 0.045776 | 60.6537 | 0.32959 | -0.13275 | 0.43945 | -0.022888 | 123.3856 | 123.3215 | 60.7636 | 123.468 | 123.6786 | 123.4909 | 123.4131 | 123.381 | -123.5779 | -123.4222 | 123.056 | 123.3582 | 61.5372 | 61.5601
192.9844 | 123.4863 | -61.5875 | 61.7706 | -0.112 | -0.00019652 | 0.0015979 | -0.00075838 | 0.0011856 | 0.00021157 | -0.00073916 | -0.046082 | 0.0011964 | 0.034541 | 0.03823 | -0.00043794 | -0.00014089 | -0.00057035 | -0.10986 | 61.8301 | -61.8622 | 61.5234 | 61.4685 | -61.7752 | -0.07782 | -0.16022 | 61.8576 | -61.6882 | 61.7569 | -0.97046 | -61.7523 | -61.3129 | -0.27466 | 0.059509 | -0.24719 | 123.056 | 61.5097 | -0.18768 | 61.7844 | 0.086975 | -0.10071 | 0.086975 | -0.013733 | 60.6171 | 0.27466 | -0.16479 | 0.37537 | -0.064087 | 123.3307 | 123.3856 | 60.7178 | 123.4451 | 123.6923 | 123.5458 | 123.4177 | 123.4451 | -123.6328 | -123.4589 | 123.111 | 123.3444 | 61.4777 | 61.4273
193.9844 | 123.4863 | -61.5646 | 61.7844 | -0.035705 | -0.0010511 | 0.0013843 | 9.6222e-05 | -0.00073704 | -0.00085663 | 0.00011544 | -0.021668 | 0.00055538 | 0.032832 | 0.032035 | -0.0019333 | -0.00078189 | 0.0011387 | -0.032043 | 61.8576 | -61.8484 | 61.5601 | 61.5601 | -61.8668 | -0.045776 | -0.068665 | 61.8439 | -61.6653 | 61.7706 | -0.93384 | -61.7386 | -61.2946 | -0.28381 | 0.073242 | -0.2243 | 123.1247 | 61.5189 | -0.30212 | 61.8027 | -0.01831 | -0.10071 | 0.059509 | -0.013733 | 60.6308 | 0.27008 | -0.17395 | 0.37079 | -0.073242 | 123.4085 | 123.4085 | 60.7315 | 123.436 | 123.7061 | 123.5092 | 123.4222 | 123.4085 | -123.6328 | -123.4497 | 123.1247 | 123.3353 | 61.5326 | 61.496
194.9844 | 123.4863 | -61.6058 | 61.7844 | -0.043335 | 0.0010853 | 0.0020251 | 0.0013778 | 0.00097196 | -2.232e-06 | -0.00052556 | 0.088196 | 0.00012818 | 0.034968 | 0.032462 | -1.0744e-05 | -0.0018499 | 0.0019931 | -0.10986 | 61.8439 | -61.8668 | 61.5143 | 61.4777 | -62.1918 | -0.35706 | -0.19226 | 61.8256 | -61.6653 | 61.7615 | -0.98419 | -61.7523 | -61.2762 | -0.26093 | 0.059509 | -0.27008 | 123.0835 | 61.2488 | -0.58594 | 61.5097 | -0.32501 | -0.059509 | 0.041199 | -0.022888 | 60.6216 | 0.32959 | -0.14648 | 0.3891 | -0.086975 | 123.3444 | 123.381 | 60.6812 | 123.4268 | 123.7106 | 123.4909 | 123.4497 | 123.4314 | -123.6511 | -123.4497 | 123.1201 | 123.3673 | 61.496 | 61.4136
195.9844 | 123.4955 | -61.5692 | 61.7889 | 0.02533 | 1.7082e-05 | -0.0011793 | 0.0020188 | -0.00073704 | 0.00021157 | -0.0028754 | -0.04303 | 0.00034178 | 0.034541 | 0.03588 | -0.0012923 | -0.0020637 | -0.00014315 | -0.022888 | 61.8805 | -61.8118 | 61.5829 | 61.5692 | -61.8393 | -0.027466 | -0.041199 | 61.8256 | -61.6562 | 61.7752 | -0.94757 | -61.7249 | -61.2762 | -0.24262 | 0.091553 | -0.20599 | 123.1384 | 61.5417 | -0.27008 | 61.7844 | -0.027465 | -0.086975 | 0.036622 | -0.013732 | 60.6216 | 0.29297 | -0.15564 | 0.37994 | -0.068665 | 123.381 | 123.3948 | 60.7086 | 123.4314 | 123.6923 | 123.4818 | 123.4497 | 123.3948 | -123.6008 | -123.4451 | 123.1522 | 123.3444 | 61.5463 | 61.528
196.9844 | 123.4497 | -61.5921 | 61.7569 | -0.012817 | 1.7082e-05 | -0.00096549 | -0.0016128 | -0.00030984 | 0.0036294 | 0.00054264 | -0.027771 | -0.0017944 | 0.035609 | 0.030326 | -0.0010787 | 0.00071351 | -0.00014315 | -0.059509 | 61.8622 | -61.8256 | 61.5372 | 61.5189 | -61.9034 | -0.068665 | -0.15564 | 61.853 | -61.6791 | 61.7249 | -0.98419 | -61.7661 | -61.3037 | -0.23346 | 0.10529 | -0.21973 | 123.111 | 61.5234 | -0.31128 | 61.7569 | -0.077819 | -0.086975 | 0.09613 | -0.032043 | 60.6079 | 0.28839 | -0.17395 | 0.37537 | -0.086975 | 123.3444 | 123.3627 | 60.6949 | 123.4039 | 123.6877 | 123.5321 | 123.4543 | 123.4451 | -123.5825 | -123.436 | 123.1293 | 123.317 | 61.5326 | 61.4365
197.9844 | 123.4726 | -61.5463 | 61.7889 | 0.0177 | -0.0010511 | -0.00011109 | 0.00052342 | 0.00097196 | -0.0014974 | 0.00011544 | -0.027771 | 0.00034178 | 0.033473 | 0.03588 | 0.0010575 | 7.2706e-05 | 0.00049765 | -0.013733 | 61.8759 | -61.8484 | 61.5921 | 61.5829 | -61.8439 | -0.004578 | -0.027466 | 61.8393 | -61.6608 | 61.7844 | -0.93384 | -61.7249 | -61.2808 | -0.30212 | 0.086976 | -0.19684 | 123.1293 | 61.5417 | -0.29755 | 61.8439 | 0.004578 | -0.11444 | 0.050354 | -0.004577 | 60.6125 | 0.2655 | -0.17853 | 0.37994 | -0.064087 | 123.4314 | 123.4406 | 60.7269 | 123.4451 | 123.7244 | 123.5001 | 123.4222 | 123.3856 | -123.6374 | -123.4497 | 123.1384 | 123.3307 | 61.5326 | 61.5189
198.9844 | 123.4726 | -61.5967 | 61.7844 | -0.043335 | 0.0015125 | 0.00052971 | -0.00011758 | -0.00030984 | -0.0012838 | 0.0022516 | -0.030823 | 0.00012818 | 0.034968 | 0.031821 | -0.00022434 | -0.0031317 | -0.0012111 | -0.10071 | 61.853 | -61.8622 | 61.5143 | 61.496 | -61.9217 | -0.10071 | -0.18768 | 61.8256 | -61.6745 | 61.8805 | -1.0574 | -61.7111 | -61.2259 | -0.2655 | 0.068664 | -0.27008 | 123.0927 | 61.496 | -0.32501 | 61.7615 | -0.059509 | -0.07782 | 0.041199 | 0.09613 | 60.5392 | 0.37079 | -0.11444 | 0.44861 | -0.036621 | 123.3582 | 123.3765 | 60.6171 | 123.555 | 123.7152 | 123.5001 | 123.4497 | 123.4222 | -123.6465 | -123.4589 | 123.111 | 123.4772 | 61.496 | 61.409
199.9844 | 123.4863 | -61.6058 | 61.7935 | 0.0177 | 0.0025805 | 0.00095711 | -0.00011758 | -0.0013778 | -0.0014974 | 0.0016106 | -0.033875 | 0.00098258 | 0.033686 | 0.033958 | -0.00043794 | 0.00049991 | 0.0011387 | -0.022888 | 61.8942 | -61.8256 | 61.5784 | 61.5875 | -61.8347 | -0.004578 | -0.022888 | 61.8484 | -61.647 | 61.7935 | -0.94299 | -61.702 | -61.2762 | -0.21973 | 0.10071 | -0.21515 | 123.1934 | 61.6013 | -0.22888 | 61.821 | -0.009155 | -0.041199 | 0.054932 | 0 | 60.6628 | 0.32959 | -0.09613 | 0.37079 | -0.054931 | 123.4131 | 123.4039 | 60.704 | 123.4406 | 123.7198 | 123.4955 | 123.5001 | 123.4543 | -123.6191 | -123.4406 | 123.1842 | 123.3994 | 61.5829 | 61.5829
200.9844 | 123.4543 | -61.5601 | 61.7889 | -0.035705 | 0.0042895 | 0.00031611 | -0.00011758 | -0.00095064 | -0.00042943 | 0.00075624 | -0.046082 | 0.0020508 | 0.035395 | 0.034598 | -0.0017197 | -0.00078189 | 0.0011387 | -0.11902 | 61.853 | -61.853 | 61.4914 | 61.5005 | -61.94 | -0.09613 | -0.17395 | 61.8393 | -61.7065 | 61.5738 | -0.91553 | -61.5005 | -61.1938 | -0.29297 | 0.064087 | -0.29755 | 123.0606 | 61.4639 | -0.37994 | 61.7569 | -0.086975 | -0.14648 | 0.050354 | -0.21515 | 60.6445 | 0.36621 | 0.05951 | 0.5127 | 0.20599 | 123.3536 | 123.3444 | 60.791 | 123.2803 | 123.7061 | 123.5458 | 123.4131 | 123.3994 | -123.642 | -123.4955 | 123.0515 | 123.1339 | 61.441 | 61.3861
201.9844 | 123.4818 | -61.5646 | 61.7889 | 0.02533 | 0.0017261 | 0.00052971 | 9.6222e-05 | 0.0020402 | 0.001066 | 0.0016106 | -0.030823 | 0.00098258 | 0.032618 | 0.03353 | -0.0010787 | 7.2706e-05 | 0.0032749 | 0.004578 | 61.8484 | -61.8439 | 61.5784 | 61.5829 | -61.8118 | -0.022888 | -0.018311 | 61.8301 | -61.6608 | 61.7889 | -0.92468 | -61.7249 | -61.2762 | -0.27924 | 0.05951 | -0.21057 | 123.1476 | 61.5417 | -0.24719 | 61.821 | 0.032043 | -0.096131 | 0.041199 | 0 | 60.64 | 0.28839 | -0.16022 | 0.38452 | -0.064087 | 123.4268 | 123.4222 | 60.7361 | 123.4497 | 123.6923 | 123.4909 | 123.4131 | 123.3948 | -123.6328 | -123.4497 | 123.143 | 123.3536 | 61.5692 | 61.5463
202.9844 | 123.4955 | -61.5921 | 61.7432 | 0.0177 | 0.00065788 | 0.0013843 | 0.0011642 | 0.00075836 | -0.00021583 | -0.0011664 | -0.0033569 | -0.00051262 | 0.033686 | 0.041434 | 0.0012711 | 0.00071351 | -0.0014249 | -0.10529 | 61.8347 | -61.8668 | 61.528 | 61.5372 | -61.908 | -0.086975 | -0.16937 | 61.7935 | -61.6699 | 61.7889 | -0.95215 | -61.7294 | -61.2762 | -0.27466 | 0.091553 | -0.21515 | 123.1293 | 61.5051 | -0.31586 | 61.7798 | -0.041199 | -0.07782 | 0.050354 | 0.045776 | 60.64 | 0.31586 | -0.13733 | 0.39368 | -0.059509 | 123.4039 | 123.3948 | 60.7178 | 123.4589 | 123.7015 | 123.4634 | 123.4268 | 123.3856 | -123.6099 | -123.4131 | 123.1201 | 123.381 | 61.4868 | 61.4227
203.9844 | 123.5001 | -61.5875 | 61.7798 | 0.0024415 | 0.00044428 | 0.0011707 | -0.00011758 | -0.0013778 | -0.001711 | 0.003747 | -0.0094605 | 0.00098258 | 0.033473 | 0.034812 | -1.0744e-05 | -0.00056829 | 0.0013523 | 0 | 61.8668 | -61.8027 | 61.5921 | 61.5829 | -61.8301 | -0.004578 | -0.022888 | 61.8576 | -61.6608 | 61.7935 | -0.93842 | -61.7203 | -61.2625 | -0.21515 | 0.086975 | -0.18768 | 123.1705 | 61.5829 | -0.24262 | 61.7981 | -0.027466 | -0.073243 | 0.07782 | 0.013733 | 60.6491 | 0.32501 | -0.13275 | 0.39825 | -0.059509 | 123.3856 | 123.3948 | 60.7224 | 123.4543 | 123.6694 | 123.5184 | 123.4543 | 123.4451 | -123.5825 | -123.4406 | 123.1796 | 123.381 | 61.5875 | 61.5646
204.9844 | 123.5092 | -61.5921 | 61.7294 | -0.020447 | -0.00062372 | 0.00031611 | -0.00011758 | -9.604e-05 | 0.0023478 | -0.00138 | -0.018616 | -8.5416e-05 | 0.034327 | 0.042075 | -0.0010787 | -0.00056829 | 0.0049839 | -0.09613 | 61.8484 | -61.8576 | 61.528 | 61.5051 | -61.9171 | -0.082397 | -0.17395 | 61.8347 | -61.6837 | 61.7981 | -0.93842 | -61.7203 | -61.2488 | -0.2655 | 0.11902 | -0.20142 | 123.0972 | 61.5097 | -0.32501 | 61.7752 | -0.059509 | -0.091553 | 0.10529 | 0.068665 | 60.6537 | 0.34332 | -0.12817 | 0.43488 | -0.036621 | 123.3627 | 123.3856 | 60.7452 | 123.4818 | 123.7061 | 123.5184 | 123.4406 | 123.4268 | -123.587 | -123.4131 | 123.1201 | 123.3902 | 61.496 | 61.4182
205.9844 | 123.4497 | -61.5875 | 61.7798 | -0.043335 | 1.7082e-05 | -0.0011793 | 0.00095062 | 0.0031082 | 0.00021157 | -0.00095276 | -0.015564 | 0.00034178 | 0.033686 | 0.029685 | -0.0017197 | 7.2706e-05 | -0.0016385 | -0.045776 | 61.8622 | -61.8393 | 61.5463 | 61.528 | -61.9034 | -0.064087 | -0.13275 | 61.8347 | -61.6837 | 61.7249 | -0.99335 | -61.7844 | -61.3083 | -0.25177 | 0.082398 | -0.23346 | 123.1155 | 61.5234 | -0.31586 | 61.7752 | -0.064087 | -0.096131 | 0.054932 | -0.054931 | 60.5942 | 0.27923 | -0.19684 | 0.37537 | -0.10071 | 123.3673 | 123.3856 | 60.6903 | 123.4085 | 123.7015 | 123.5184 | 123.4497 | 123.4222 | -123.6191 | -123.4634 | 123.1338 | 123.3124 | 61.5417 | 61.4548
206.9844 | 123.5046 | -61.5875 | 61.7477 | 0.02533 | -0.0010511 | -0.00075189 | -0.00054478 | 0.00033116 | 0.001066 | 0.0011834 | -0.00030511 | -0.00029902 | 0.035395 | 0.030753 | 0.00020286 | -0.0012091 | 0.0013523 | -0.086975 | 61.8439 | -61.8622 | 61.5234 | 61.5189 | -61.8942 | -0.07782 | -0.16479 | 61.8256 | -61.6699 | 61.821 | -0.92926 | -61.7249 | -61.2625 | -0.27466 | 0.09613 | -0.22431 | 123.1064 | 61.5097 | -0.3067 | 61.7844 | -0.032043 | -0.082398 | 0.07782 | 0.073242 | 60.6583 | 0.32501 | -0.13733 | 0.40741 | -0.054932 | 123.381 | 123.3856 | 60.7407 | 123.4909 | 123.7061 | 123.4955 | 123.4314 | 123.4131 | -123.6099 | -123.4177 | 123.111 | 123.4085 | 61.5005 | 61.4227
207.9844 | 123.4314 | -61.6013 | 61.7935 | -0.012817 | 0.0010853 | -0.00032469 | -0.00054478 | 0.0048172 | 0.0014932 | -0.00031196 | -0.030823 | 0.0011964 | 0.035822 | 0.046561 | -0.0015059 | 0.0013543 | -0.00078395 | -0.050354 | 61.8668 | -61.8576 | 61.5463 | 61.5097 | -61.9034 | -0.07782 | -0.16479 | 61.8393 | -61.6653 | 61.7249 | -0.99792 | -61.8027 | -61.3174 | -0.25635 | 0.073242 | -0.24719 | 123.111 | 61.5234 | -0.30212 | 61.7798 | -0.045776 | -0.064087 | 0.045776 | -0.068664 | 60.6033 | 0.28381 | -0.20142 | 0.3479 | -0.13733 | 123.3673 | 123.4039 | 60.6674 | 123.3902 | 123.7244 | 123.5046 | 123.468 | 123.4406 | -123.6511 | -123.4589 | 123.1476 | 123.3261 | 61.5509 | 61.4365
208.9844 | 123.5184 | -61.6013 | 61.7249 | -0.043335 | 0.00087168 | 0.0011707 | 0.0013778 | 0.00075836 | 0.00021157 | -0.0015936 | -0.015564 | -0.00051262 | 0.030268 | 0.032462 | -0.0019333 | -0.0016363 | 0.0028477 | -0.09613 | 61.8439 | -61.8484 | 61.528 | 61.5234 | -61.908 | -0.07782 | -0.16022 | 61.8118 | -61.6608 | 61.7981 | -0.93384 | -61.702 | -61.2534 | -0.24719 | 0.11902 | -0.19684 | 123.1247 | 61.5234 | -0.3067 | 61.7706 | -0.059509 | -0.05951 | 0.086975 | 0.073242 | 60.6674 | 0.3479 | -0.10071 | 0.40741 | -0.041198 | 123.3719 | 123.3765 | 60.7269 | 123.4589 | 123.6923 | 123.4726 | 123.4451 | 123.4131 | -123.5733 | -123.3856 | 123.1293 | 123.3994 | 61.5051 | 61.441
209.9844 | 123.436 | -61.5829 | 61.7752 | -0.012817 | 0.0030079 | 0.0011707 | 0.00052342 | 0.0024674 | -0.00042943 | 0.001397 | -0.039978 | 0.0018372 | 0.035395 | 0.034598 | -0.0021469 | 0.00071351 | -0.00014315 | -0.050354 | 61.853 | -61.8347 | 61.5463 | 61.5051 | -61.908 | -0.059509 | -0.16937 | 61.853 | -61.6745 | 61.7386 | -0.99335 | -61.7752 | -61.3266 | -0.25177 | 0.077819 | -0.22888 | 123.0881 | 61.5234 | -0.32501 | 61.7752 | -0.073242 | -0.091553 | 0.077819 | -0.036622 | 60.5896 | 0.25635 | -0.19226 | 0.3479 | -0.10071 | 123.3398 | 123.381 | 60.6812 | 123.4131 | 123.6877 | 123.5275 | 123.436 | 123.436 | -123.6099 | -123.4497 | 123.1293 | 123.3215 | 61.5326 | 61.4136
210.9844 | 123.5229 | -61.5738 | 61.734 | 0.0177 | 0.0027943 | 0.00095711 | 0.00030982 | 0.0018266 | 0.00021157 | -9.8356e-05 | -0.015564 | 0.00012818 | 0.033686 | 0.028617 | -0.0023605 | 0.00028631 | 0.00028405 | -0.10071 | 61.853 | -61.8393 | 61.5326 | 61.5143 | -61.8896 | -0.082397 | -0.16479 | 61.8073 | -61.6608 | 61.7844 | -0.93384 | -61.7111 | -61.2579 | -0.2655 | 0.11902 | -0.20142 | 123.0881 | 61.4914 | -0.31586 | 61.7569 | -0.050354 | -0.086975 | 0.073242 | 0.050354 | 60.64 | 0.31586 | -0.13733 | 0.40283 | -0.050354 | 123.3536 | 123.3719 | 60.7269 | 123.4451 | 123.6923 | 123.468 | 123.4268 | 123.381 | -123.5733 | -123.3948 | 123.1064 | 123.3582 | 61.4731 | 61.409
211.9844 | 123.5229 | -61.6104 | 61.7706 | 0.0024415 | 0.0017261 | 0.00010251 | 0.00073702 | 0.0016128 | 0.00042517 | -0.002021 | -0.04303 | 0.00055538 | 0.033259 | 0.035239 | -0.00086514 | 7.2706e-05 | -0.00078395 | -0.086975 | 61.8713 | -61.8713 | 61.528 | 61.4731 | -61.9217 | -0.086975 | -0.19226 | 61.8393 | -61.6745 | 61.9034 | -0.85602 | -61.7889 | -61.2854 | -0.26093 | 0.10071 | -0.24261 | 123.0835 | 61.5234 | -0.31128 | 61.7844 | -0.050354 | -0.064087 | 0.068664 | 0.13275 | 60.7544 | 0.32501 | -0.17853 | 0.3891 | -0.11444 | 123.3444 | 123.3994 | 60.8185 | 123.5779 | 123.7427 | 123.5138 | 123.4818 | 123.4497 | -123.642 | -123.4451 | 123.1384 | 123.5138 | 61.5234 | 61.4182
212.9844 | 123.6099 | -61.5692 | 61.7157 | -0.096741 | 0.00065788 | -0.00053829 | -0.0016128 | -0.00030984 | 0.00021157 | 0.00032904 | -0.0094605 | -0.00029902 | 0.034327 | 0.037162 | 0.00041666 | -0.00078189 | 0.00049765 | -0.059509 | 61.8164 | -61.8347 | 61.6379 | 61.5784 | -61.8759 | -0.009155 | -0.09613 | 61.7615 | -61.6562 | 61.8439 | -0.86517 | -61.6287 | -61.1801 | -0.2655 | 0.10071 | -0.07782 | 123.1476 | 61.5601 | -0.3067 | 61.8256 | -0.041199 | -0.086975 | 0.045777 | 0.12817 | 60.704 | 0.3891 | -0.059509 | 0.47607 | 0.027466 | 123.4131 | 123.4726 | 60.791 | 123.5001 | 123.6511 | 123.4177 | 123.3856 | 123.3307 | -123.5504 | -123.3719 | 123.2071 | 123.4131 | 61.5097 | 61.4731
213.9844 | 123.4406 | -61.5967 | 61.7844 | -0.020447 | 0.0015125 | 0.00074331 | 0.00073702 | 0.0016128 | 0.00042517 | 0.00096984 | -0.027771 | 0.0016236 | 0.036463 | 0.03588 | -0.00043794 | 0.00092711 | -0.0029201 | -0.091553 | 61.8347 | -61.8713 | 61.5189 | 61.4777 | -61.9308 | -0.086975 | -0.18768 | 61.8347 | -61.6882 | 61.5692 | -0.78278 | -61.5784 | -61.2579 | -0.27466 | 0.050354 | -0.2655 | 123.0743 | 61.5097 | -0.33417 | 61.7844 | -0.059509 | -0.091552 | 0.050354 | -0.21515 | 60.8139 | 0.33874 | 0.018311 | 0.4303 | 0.10986 | 123.349 | 123.3902 | 60.9055 | 123.2574 | 123.7061 | 123.5229 | 123.4314 | 123.4314 | -123.6557 | -123.4726 | 123.1155 | 123.1659 | 61.5051 | 61.409
214.9844 | 123.5825 | -61.5601 | 61.734 | -0.050964 | 0.0019397 | 0.00095711 | 0.0011642 | -0.0013778 | 0.0019204 | -0.002021 | -0.015564 | -0.002008 | 0.033259 | 0.027122 | 0.00020286 | 0.00092711 | -0.00035675 | -0.054932 | 61.8027 | -61.8393 | 61.6104 | 61.5921 | -61.8439 | -0.013733 | -0.082397 | 61.7889 | -61.6745 | 61.8713 | -0.84686 | -61.6425 | -61.1893 | -0.27923 | 0.068664 | -0.1236 | 123.1522 | 61.5463 | -0.28381 | 61.8256 | -0.004578 | -0.11444 | 0.054931 | 0.13733 | 60.7132 | 0.37079 | -0.082397 | 0.48523 | 0.032044 | 123.4314 | 123.4497 | 60.8276 | 123.5458 | 123.642 | 123.4634 | 123.3627 | 123.349 | -123.5733 | -123.4085 | 123.1705 | 123.4314 | 61.5051 | 61.4777
215.9844 | 123.4451 | -61.5921 | 61.7889 | -0.058594 | -0.00019652 | 0.00031611 | -0.00011758 | -0.00030984 | 0.001066 | -0.00031196 | -0.055237 | 0.002478 | 0.033686 | 0.03588 | -1.0744e-05 | 0.00028631 | 0.00028405 | -0.073242 | 61.8347 | -61.853 | 61.5143 | 61.4868 | -61.9308 | -0.073242 | -0.1831 | 61.8301 | -61.6882 | 61.6882 | -1.236 | -61.5372 | -61.0565 | -0.26093 | 0.045777 | -0.27466 | 123.0789 | 61.5189 | -0.33875 | 61.7798 | -0.07782 | -0.09613 | 0.041199 | -0.10071 | 60.3561 | 0.53558 | 0.054932 | 0.63171 | 0.15106 | 123.3398 | 123.3673 | 60.4523 | 123.3765 | 123.6877 | 123.5184 | 123.4268 | 123.4222 | -123.642 | -123.4772 | 123.1064 | 123.2803 | 61.5189 | 61.409
216.9844 | 123.587 | -61.5601 | 61.7432 | 0.0024415 | -0.0010511 | -0.00053829 | 0.002446 | -0.00095064 | -2.232e-06 | -0.00073916 | -0.00030511 | -0.00051262 | 0.030055 | 0.034812 | -0.0017197 | 0.00028631 | 0.00071145 | -0.068665 | 61.8256 | -61.8118 | 61.6013 | 61.6058 | -61.8256 | -0.009155 | -0.10529 | 61.7935 | -61.6608 | 61.8668 | -0.86517 | -61.6379 | -61.1801 | -0.25177 | 0.082398 | -0.14191 | 123.1659 | 61.5509 | -0.2655 | 61.8027 | -0.013733 | -0.10071 | 0.050354 | 0.1236 | 60.6949 | 0.37994 | -0.077819 | 0.48065 | 0.022889 | 123.4177 | 123.4131 | 60.7956 | 123.5275 | 123.6374 | 123.4543 | 123.3856 | 123.3536 | -123.555 | -123.4039 | 123.1613 | 123.4268 | 61.4914 | 61.4548
217.9844 | 123.349 | -61.647 | 61.7249 | -0.005188 | -0.0010511 | 0.0011707 | 0.0011642 | 0.0024674 | -0.0019248 | -0.002021 | -0.052185 | 0.0016236 | 0.033473 | 0.035667 | 0.00063026 | -0.00078189 | 0.0013523 | -0.086975 | 61.8393 | -61.8851 | 61.4914 | 61.4685 | -61.9125 | -0.091553 | -0.19226 | 61.8256 | -61.6928 | 61.7569 | -0.98419 | -61.7752 | -61.2946 | -0.23804 | 0.11444 | -0.23346 | 123.1155 | 61.5555 | -0.2655 | 61.7935 | -0.027466 | -0.045776 | 0.10071 | 0.032043 | 60.6628 | 0.35248 | -0.12817 | 0.39825 | -0.082398 | 123.3536 | 123.3765 | 60.7086 | 123.4497 | 123.7244 | 123.5184 | 123.4863 | 123.4726 | -123.6099 | -123.4177 | 123.1384 | 123.4039 | 61.5601 | 61.4548
218.9844 | 123.6053 | -61.5463 | 61.7523 | -0.058594 | 0.0012989 | 0.00095711 | -0.0013992 | -0.0015914 | 0.0017068 | 0.00054264 | -0.0094605 | -0.0015808 | 0.033259 | 0.035667 | -0.00043794 | -0.0027045 | -0.00078395 | -0.013733 | 61.7981 | -61.8301 | 61.6196 | 61.647 | -61.8027 | 0 | -0.073242 | 61.7889 | -61.6562 | 61.9766 | -0.84228 | -61.5646 | -61.1526 | -0.28381 | 0.045777 | -0.13275 | 123.1934 | 61.5463 | -0.25635 | 61.8301 | 0.027466 | -0.10986 | 0.036621 | 0.22431 | 60.704 | 0.39368 | -0.01831 | 0.50354 | 0.091553 | 123.4772 | 123.4497 | 60.8139 | 123.6328 | 123.6282 | 123.4451 | 123.3444 | 123.3353 | -123.5825 | -123.4085 | 123.1659 | 123.523 | 61.5326 | 61.4731
219.9844 | 123.5229 | -61.5875 | 61.7523 | -0.089111 | -0.0025463 | -0.00011109 | 0.00095062 | 0.0011856 | -0.00064303 | 0.0016106 | -0.046082 | 0.00034178 | 0.033045 | 0.037589 | -0.0025741 | 0.0011407 | 0.00092505 | -0.022888 | 61.8622 | -61.853 | 61.528 | 61.5097 | -61.8942 | -0.086975 | -0.18768 | 61.8118 | -61.6745 | 61.7661 | -0.94299 | -61.734 | -61.2762 | -0.2655 | 0.10986 | -0.2243 | 123.0972 | 61.5005 | -0.3067 | 61.7661 | -0.041199 | -0.086976 | 0.05951 | 0.013733 | 60.6445 | 0.31128 | -0.14648 | 0.39825 | -0.059509 | 123.3627 | 123.381 | 60.7315 | 123.4406 | 123.7152 | 123.4863 | 123.4497 | 123.3994 | -123.6053 | -123.4268 | 123.1155 | 123.3536 | 61.5646 | 61.3998
220.9844 | 123.5733 | -61.5646 | 61.7386 | -0.096741 | 0.0021533 | 0.00031611 | -0.0016128 | -0.00073704 | 0.0012796 | -0.0033026 | 0.014954 | 0.00098258 | 0.0339 | 0.036948 | -0.0017197 | -0.0012091 | 0.0079745 | -0.022888 | 61.8073 | -61.8164 | 61.6333 | 61.6333 | -61.8073 | 0.009155 | -0.064087 | 61.7798 | -61.6516 | 61.8896 | -1.0941 | -61.4182 | -60.997 | -0.25177 | 0.068665 | -0.10528 | 123.1979 | 61.5738 | -0.24262 | 61.8256 | 0.009155 | -0.086975 | 0.041199 | 0.15106 | 60.4706 | 0.56763 | 0.14648 | 0.6546 | 0.23346 | 123.4497 | 123.4497 | 60.5576 | 123.5413 | 123.6237 | 123.4314 | 123.3719 | 123.3444 | -123.555 | -123.3902 | 123.1979 | 123.4543 | 61.5417 | 61.5005
221.9844 | 123.4863 | -61.5967 | 61.7294 | 0.02533 | -0.0036145 | -0.0018201 | 0.00073702 | 0.0016128 | 0.0023478 | 0.0024652 | -0.049133 | 0.00034178 | 0.034113 | 0.037589 | -0.00065154 | -0.00056829 | -0.0018521 | 0.09613 | 61.821 | -61.8484 | 61.5601 | 61.5097 | -61.9263 | -0.086975 | -0.1831 | 61.8164 | -61.6791 | 61.7706 | -0.94757 | -61.7477 | -61.2808 | -0.25177 | 0.091553 | -0.16937 | 123.1064 | 61.5097 | -0.32959 | 61.7615 | -0.07782 | -0.082397 | 0.086975 | 0.041199 | 60.6491 | 0.31586 | -0.15106 | 0.39825 | -0.068665 | 123.3582 | 123.4085 | 60.7315 | 123.4497 | 123.6694 | 123.4955 | 123.4177 | 123.4131 | -123.5779 | -123.4085 | 123.1567 | 123.3673 | 61.6928 | 61.4136
222.9844 | 123.5184 | -61.5601 | 61.7294 | -0.020447 | -0.00019652 | 0.00095711 | -0.00097198 | -0.0013778 | 0.00021157 | -9.8356e-05 | 0.0027465 | -0.0015808 | 0.033473 | 0.030967 | -0.0019333 | -0.00099549 | -0.0042019 | 0.004578 | 61.821 | -61.7935 | 61.6333 | 61.6425 | -61.7981 | 0.018311 | -0.073242 | 61.7706 | -61.647 | 61.8484 | -0.86517 | -61.6425 | -61.1984 | -0.23346 | 0.091553 | -0.09613 | 123.2025 | 61.5784 | -0.23804 | 61.8118 | -0.004578 | -0.086975 | 0.041199 | 0.11902 | 60.6949 | 0.36163 | -0.082397 | 0.44861 | 0.004578 | 123.436 | 123.4268 | 60.7819 | 123.4955 | 123.6145 | 123.4177 | 123.381 | 123.3307 | -123.5229 | -123.3765 | 123.1934 | 123.4085 | 61.5646 | 61.4868
223.9844 | 123.4955 | -61.5921 | 61.734 | -0.24933 | 0.00044428 | -0.00053829 | 0.00030982 | 0.002681 | -0.0010702 | 0.00075624 | -0.06134 | 0.0022644 | 0.033045 | 0.039512 | -0.0012923 | 0.00049991 | 0.00028405 | 0.15564 | 61.8256 | -61.8484 | 61.5463 | 61.5189 | -61.9446 | -0.082397 | -0.1831 | 61.8347 | -61.6791 | 61.7523 | -0.97046 | -61.7386 | -61.29 | -0.25635 | 0.091553 | -0.18768 | 123.111 | 61.5097 | -0.35248 | 61.7661 | -0.09613 | -0.086975 | 0.10071 | 0.01831 | 60.6216 | 0.30212 | -0.14648 | 0.3891 | -0.059509 | 123.3673 | 123.3948 | 60.7086 | 123.4314 | 123.674 | 123.5138 | 123.4177 | 123.4268 | -123.5825 | -123.4131 | 123.1384 | 123.3444 | 61.7477 | 61.409
224.9844 | 123.6511 | -61.5921 | 61.7249 | -0.028076 | 0.0019397 | 0.0018115 | 0.0011642 | -0.00052344 | -0.00021583 | 0.00096984 | 0.011902 | -0.00051262 | 0.031336 | 0.033744 | -0.00022434 | 0.00028631 | 0.00092505 | -0.009155 | 61.7935 | -61.8301 | 61.6562 | 61.6196 | -61.8073 | 0.004578 | -0.091553 | 61.8027 | -61.647 | 61.8622 | -0.84228 | -61.8073 | -61.3861 | -0.23804 | 0.068664 | -0.068665 | 123.2117 | 61.5967 | -0.21515 | 61.8347 | 0.022888 | -0.054932 | 0.077819 | 0.13733 | 60.7498 | 0.20599 | -0.21515 | 0.26093 | -0.16022 | 123.4497 | 123.4863 | 60.8047 | 123.5092 | 123.6237 | 123.4497 | 123.3856 | 123.3948 | -123.555 | -123.3719 | 123.2483 | 123.4543 | 61.5829 | 61.5005
225.9844 | 123.5687 | -61.5555 | 61.7157 | -0.020447 | 0.00087168 | -0.00011109 | 0.0015914 | 0.0018266 | 0.0025614 | -0.00052556 | -0.055237 | 0.002478 | 0.0339 | 0.026267 | -1.0744e-05 | -0.00014089 | 7.0452e-05 | -0.064087 | 61.8393 | -61.8576 | 61.5646 | 61.5555 | -61.8896 | -0.027466 | -0.13733 | 61.8118 | -61.6974 | 61.8439 | -0.87891 | -61.6379 | -61.1755 | -0.30212 | 0.1236 | -0.15106 | 123.111 | 61.528 | -0.33417 | 61.8301 | -0.032043 | -0.14191 | 0.096131 | 0.12817 | 60.6766 | 0.37994 | -0.082397 | 0.52185 | 0.05951 | 123.4131 | 123.4222 | 60.8185 | 123.5413 | 123.6969 | 123.5092 | 123.3948 | 123.3673 | -123.5733 | -123.4131 | 123.1201 | 123.3994 | 61.4914 | 61.4182
226.9844 | 123.5458 | -61.5829 | 61.734 | -0.005188 | 0.00023068 | 0.00095711 | 0.0011642 | -0.0015914 | 0.0038432 | 0.00011544 | 0.0088501 | -0.00094002 | 0.034327 | 0.028617 | -0.00043794 | -0.0029181 | 0.00028405 | 0 | 61.8256 | -61.8073 | 61.6196 | 61.6287 | -61.7889 | 0.032043 | -0.07782 | 61.7935 | -61.6516 | 61.8393 | -0.85602 | -61.6287 | -61.1938 | -0.2243 | 0.091553 | -0.11444 | 123.2117 | 61.615 | -0.20599 | 61.8393 | 0.018311 | -0.068664 | 0.059509 | 0.10529 | 60.7269 | 0.3891 | -0.045776 | 0.45776 | 0.022888 | 123.436 | 123.4268 | 60.7956 | 123.4909 | 123.6328 | 123.4451 | 123.4085 | 123.3765 | -123.5413 | -123.3856 | 123.2025 | 123.4222 | 61.5829 | 61.5051
227.9844 | 123.5596 | -61.5784 | 61.734 | -0.012817 | 0.0012989 | -0.00096549 | 0.001805 | 0.0022538 | 0.0017068 | -0.0026618 | -0.055237 | -0.00029902 | 0.032405 | 0.039084 | -0.00065154 | -0.00014089 | -0.0012111 | -0.041199 | 61.8301 | -61.8439 | 61.5555 | 61.5601 | -61.8805 | -0.045776 | -0.15564 | 61.8073 | -61.6699 | 61.8347 | -0.89264 | -61.6608 | -61.2076 | -0.2655 | 0.09613 | -0.17853 | 123.1384 | 61.5326 | -0.30212 | 61.7981 | -0.036621 | -0.091553 | 0.073242 | 0.10071 | 60.6857 | 0.37079 | -0.082398 | 0.46234 | 0.009155 | 123.4039 | 123.3994 | 60.7773 | 123.5046 | 123.674 | 123.4772 | 123.4085 | 123.3856 | -123.5779 | -123.4039 | 123.1338 | 123.4131 | 61.5372 | 61.4227
228.9844 | 123.5458 | -61.5463 | 61.7065 | 0.063477 | 0.0034351 | 0.00052971 | 0.00030982 | 0.00033116 | 0.0012796 | -0.00073916 | -0.0094605 | 0.0011964 | 0.031123 | 0.039725 | -0.0025741 | -0.0018499 | -0.0031339 | -0.013733 | 61.7981 | -61.8118 | 61.6241 | 61.6196 | -61.7935 | 0.004578 | -0.068665 | 61.8027 | -61.647 | 61.8484 | -0.84686 | -61.6241 | -61.1984 | -0.2655 | 0.091553 | -0.082397 | 123.1659 | 61.5509 | -0.24719 | 61.8164 | 0.018311 | -0.10071 | 0.09613 | 0.14191 | 60.6995 | 0.3479 | -0.07782 | 0.44861 | 0.022888 | 123.4314 | 123.436 | 60.8002 | 123.4955 | 123.6099 | 123.4497 | 123.3444 | 123.349 | -123.5184 | -123.3536 | 123.1705 | 123.3948 | 61.5326 | 61.4777
229.9844 | 123.5733 | -61.5692 | 61.7294 | -0.020447 | 0.00087168 | 0.0018115 | 0.00030982 | 0.00075836 | 0.002775 | -0.00095276 | -0.036926 | 0.00055538 | 0.032832 | 0.032889 | -0.0015059 | 0.00049991 | 0.0017795 | 0.013733 | 61.7889 | -61.8393 | 61.6241 | 61.615 | -61.7935 | 0.018311 | -0.07782 | 61.7844 | -61.6562 | 61.8622 | -0.8606 | -61.6104 | -61.1938 | -0.27008 | 0.059509 | -0.10528 | 123.1842 | 61.5875 | -0.2243 | 61.8576 | 0.045776 | -0.086975 | 0.054932 | 0.13275 | 60.7086 | 0.37537 | -0.041199 | 0.46234 | 0.045776 | 123.4543 | 123.4634 | 60.7956 | 123.5184 | 123.6282 | 123.4406 | 123.3582 | 123.3536 | -123.5687 | -123.3856 | 123.1934 | 123.4314 | 61.5829 | 61.4914
230.9844 | 123.5687 | -61.5326 | 61.7249 | -0.012817 | 0.00065788 | 0.0013843 | 0.0011642 | -0.0020188 | 0.00042517 | 0.00032904 | 0.0027465 | -8.5416e-05 | 0.031977 | 0.037589 | -0.00022434 | -0.00014089 | -0.0016385 | 0.036621 | 61.7889 | -61.7981 | 61.6562 | 61.6196 | -61.8164 | 0.045776 | -0.064087 | 61.7798 | -61.647 | 61.853 | -0.85602 | -61.6287 | -61.1847 | -0.2655 | 0.064086 | -0.068665 | 123.1522 | 61.5784 | -0.28381 | 61.8439 | -0.01831 | -0.11444 | 0.054931 | 0.12817 | 60.6766 | 0.3479 | -0.09613 | 0.46234 | 0.018311 | 123.4177 | 123.4543 | 60.791 | 123.5001 | 123.587 | 123.4268 | 123.3215 | 123.3124 | -123.523 | -123.3719 | 123.1888 | 123.3856 | 61.5692 | 61.4685
231.9844 | 123.5458 | -61.5829 | 61.6882 | -0.005188 | -0.00019652 | 0.0011707 | 0.00095062 | 0.0011856 | -0.00042943 | 0.0016106 | -0.046082 | 0.00141 | 0.030696 | 0.042075 | -0.0010787 | 0.00092711 | -0.00057035 | -0.022888 | 61.8256 | -61.8622 | 61.5784 | 61.5417 | -61.8668 | -0.041199 | -0.13733 | 61.8164 | -61.6425 | 61.821 | -0.90179 | -61.6745 | -61.2259 | -0.27924 | 0.13733 | -0.10986 | 123.1247 | 61.5417 | -0.28381 | 61.821 | -0.004577 | -0.059509 | 0.12817 | 0.13275 | 60.6812 | 0.35706 | -0.091553 | 0.41657 | -0.032044 | 123.4039 | 123.4406 | 60.7407 | 123.4634 | 123.6877 | 123.4589 | 123.4085 | 123.3994 | -123.5504 | -123.3307 | 123.1613 | 123.4039 | 61.5601 | 61.4456
232.9844 | 123.5504 | -61.5555 | 61.7294 | -0.035705 | 0.00087168 | -0.00011109 | 0.00073702 | -0.0037276 | -0.00021583 | -0.00031196 | 0.011902 | -0.00051262 | 0.033473 | 0.03054 | -0.0012923 | 0.0011407 | -0.00078395 | -0.004578 | 61.8164 | -61.8164 | 61.6013 | 61.6058 | -61.8301 | 0.018311 | -0.14191 | 61.8164 | -61.6791 | 61.821 | -0.88348 | -61.6562 | -61.2213 | -0.26093 | 0.086975 | -0.12817 | 123.1613 | 61.5738 | -0.27466 | 61.8347 | -0.013733 | -0.1236 | 0.086975 | 0.091553 | 60.672 | 0.33417 | -0.10071 | 0.45776 | 0.022888 | 123.4222 | 123.4177 | 60.7956 | 123.5001 | 123.6328 | 123.4955 | 123.3719 | 123.3719 | -123.5458 | -123.4085 | 123.1567 | 123.3765 | 61.5509 | 61.4136
233.9844 | 123.5916 | -61.5692 | 61.6745 | -0.005188 | -0.00062372 | 0.0030933 | -0.00011758 | 0.00097196 | -2.232e-06 | 0.0028924 | -0.039978 | 0.00012818 | 0.033259 | 0.029899 | -0.0023605 | 0.0015679 | 7.0452e-05 | 0.022888 | 61.7706 | -61.8347 | 61.6516 | 61.6287 | -61.8027 | 0.022888 | -0.082397 | 61.8027 | -61.6562 | 61.8759 | -0.84228 | -61.6241 | -61.171 | -0.2655 | 0.09613 | -0.022889 | 123.1979 | 61.5921 | -0.23346 | 61.8576 | 0.032044 | -0.086975 | 0.12817 | 0.20142 | 60.7269 | 0.39825 | -0.054932 | 0.48523 | 0.032043 | 123.4634 | 123.4863 | 60.8139 | 123.5321 | 123.6053 | 123.4589 | 123.3398 | 123.3719 | -123.5092 | -123.3307 | 123.2208 | 123.4451 | 61.5921 | 61.4868
234.9844 | 123.5458 | -61.5784 | 61.7432 | 0.010071 | 0.0021533 | 0.00052971 | 0.00095062 | -0.00095064 | 0.00063877 | 0.00032904 | 0.0057983 | -8.5416e-05 | 0.032832 | 0.033317 | -0.0025741 | -0.0014227 | 0.0017795 | 0.009155 | 61.7981 | -61.7981 | 61.5921 | 61.615 | -61.8439 | 0.022888 | -0.14191 | 61.8164 | -61.6379 | 61.8393 | -0.87433 | -61.6608 | -61.2122 | -0.21973 | 0.054932 | -0.15106 | 123.1934 | 61.6013 | -0.2655 | 61.821 | -0.045776 | -0.059509 | 0.073242 | 0.09613 | 60.704 | 0.36621 | -0.082398 | 0.42572 | -0.022889 | 123.4131 | 123.3902 | 60.7635 | 123.4772 | 123.5962 | 123.4543 | 123.3765 | 123.3948 | -123.5413 | -123.381 | 123.1705 | 123.4177 | 61.5875 | 61.4365
235.9844 | 123.5825 | -61.5967 | 61.702 | -0.035705 | 0.0036487 | 0.00074331 | 0.0013778 | 0.0011856 | 0.00042517 | -0.0011664 | -0.04303 | 0.00076898 | 0.031977 | 0.032676 | 0.00020286 | 0.0026361 | 0.0015659 | 0.041199 | 61.7981 | -61.8301 | 61.647 | 61.6196 | -61.7844 | 0.032043 | -0.082397 | 61.7889 | -61.647 | 61.8805 | -0.85602 | -61.8301 | -61.3953 | -0.23346 | 0.096131 | -0.054931 | 123.2162 | 61.6287 | -0.18768 | 61.8622 | 0.045776 | -0.050354 | 0.086975 | 0.17853 | 60.7407 | 0.20142 | -0.23346 | 0.25177 | -0.18311 | 123.4497 | 123.4772 | 60.791 | 123.5275 | 123.6282 | 123.436 | 123.3948 | 123.3856 | -123.5321 | -123.349 | 123.2437 | 123.4772 | 61.6379 | 61.5143
236.9844 | 123.5275 | -61.5692 | 61.7615 | -0.050964 | -0.00019652 | 0.0015979 | -0.00097198 | 0.0016128 | 0.0017068 | 0.00011544 | 0.027161 | -0.0011536 | 0.035182 | 0.027976 | 0.00020286 | 0.0011407 | -0.00014315 | 0.009155 | 61.8301 | -61.8118 | 61.5967 | 61.6058 | -61.8027 | 0.064087 | -0.045776 | 61.8301 | -61.6241 | 61.8347 | -0.8606 | -61.6287 | -61.2305 | -0.24262 | 0.068664 | -0.16479 | 123.175 | 61.6333 | -0.23346 | 61.8759 | 0.009156 | -0.054932 | 0.068664 | 0.073242 | 60.7086 | 0.33875 | -0.059509 | 0.39368 | -0.004577 | 123.4177 | 123.4085 | 60.7636 | 123.4589 | 123.642 | 123.4543 | 123.3994 | 123.3994 | -123.5733 | -123.3856 | 123.1659 | 123.4039 | 61.5784 | 61.5234
237.9844 | 123.5916 | -61.5051 | 61.7661 | -0.020447 | 1.7082e-05 | -0.0011793 | -0.00054478 | -0.0026596 | -0.0012838 | -0.0018072 | 0.021057 | -0.00094002 | 0.035609 | 0.027122 | -0.00022434 | 0.0015679 | -0.0016385 | 0.091553 | 61.8347 | -61.7935 | 61.702 | 61.7386 | -61.7111 | 0.1831 | 0.11444 | 61.8118 | -61.6058 | 61.9171 | -0.78278 | -61.5372 | -61.1343 | -0.28839 | 0.068665 | -0.064087 | 123.2437 | 61.6882 | -0.20599 | 61.9766 | 0.082397 | -0.10071 | 0.045777 | 0.15106 | 60.7224 | 0.37079 | -0.032043 | 0.4715 | 0.068665 | 123.5321 | 123.4955 | 60.8231 | 123.5229 | 123.6282 | 123.4177 | 123.3398 | 123.317 | -123.5596 | -123.3719 | 123.2071 | 123.4222 | 61.5967 | 61.6196
238.9844 | 123.5413 | -61.5555 | 61.7386 | -0.028076 | 0.0010853 | -0.00096549 | 0.00095062 | 0.0020402 | -0.0010702 | -0.00095276 | -0.036926 | 0.00055538 | 0.033259 | 0.035667 | -0.0010787 | -0.00014089 | -0.0016385 | 0.013733 | 61.8164 | -61.8393 | 61.615 | 61.5555 | -61.8347 | 0.041199 | -0.13275 | 61.8347 | -61.6608 | 61.8256 | -0.8606 | -61.647 | -61.2259 | -0.28381 | 0.07782 | -0.1236 | 123.111 | 61.5967 | -0.27924 | 61.8805 | 0.004577 | -0.10529 | 0.096131 | 0.086976 | 60.6949 | 0.32959 | -0.091553 | 0.43488 | 0.013733 | 123.3948 | 123.4543 | 60.8002 | 123.4863 | 123.6557 | 123.4955 | 123.3719 | 123.3902 | -123.5779 | -123.3994 | 123.1705 | 123.381 | 61.5692 | 61.4227
239.9844 | 123.5504 | -61.5646 | 61.7386 | -0.066223 | 0.0019397 | -0.00032469 | -0.0013992 | 0.00075836 | 0.0023478 | 0.0018242 | -0.033875 | 0.00012818 | 0.033045 | 0.032676 | -0.0010787 | 7.2706e-05 | -0.00078395 | 0.045776 | 61.821 | -61.8256 | 61.6425 | 61.6425 | -61.7935 | 0.054932 | -0.082397 | 61.8027 | -61.6562 | 61.853 | -0.86517 | -61.6333 | -61.2167 | -0.26093 | 0.082398 | -0.09613 | 123.2071 | 61.6196 | -0.22888 | 61.8805 | 0.032044 | -0.091553 | 0.064087 | 0.11444 | 60.6995 | 0.3479 | -0.068665 | 0.43945 | 0.022888 | 123.468 | 123.468 | 60.791 | 123.5092 | 123.6465 | 123.4589 | 123.3856 | 123.3673 | -123.5641 | -123.3948 | 123.2071 | 123.4177 | 61.6104 | 61.4822
240.9844 | 123.5779 | -61.5189 | 61.7661 | 0.032959 | 0.0019397 | -0.00053829 | -0.00033118 | -0.0026596 | -0.002352 | -0.00095276 | 0.0088501 | 0.0011964 | 0.032191 | 0.030112 | -0.0019333 | -0.0020637 | -0.0020657 | 0.07782 | 61.853 | -61.8164 | 61.6516 | 61.6516 | -61.7432 | 0.1236 | 0 | 61.8347 | -61.6333 | 61.8988 | -0.78735 | -61.5646 | -61.1526 | -0.29755 | 0.086975 | -0.11444 | 123.1705 | 61.6425 | -0.2243 | 61.94 | 0.073242 | -0.11444 | 0.068665 | 0.13275 | 60.7315 | 0.36621 | -0.045776 | 0.48065 | 0.068665 | 123.468 | 123.468 | 60.8459 | 123.5321 | 123.6694 | 123.468 | 123.3719 | 123.3536 | -123.5825 | -123.3994 | 123.1705 | 123.4177 | 61.5967 | 61.5189
241.9844 | 123.5596 | -61.5646 | 61.7523 | -0.066223 | 0.0023669 | -0.00096549 | -0.0011856 | 0.0024674 | 0.00063877 | 0.00032904 | -0.033875 | 0.00055538 | 0.033686 | 0.034812 | -0.00086514 | -0.0014227 | -0.0012111 | 0.045776 | 61.8027 | -61.8484 | 61.6333 | 61.6196 | -61.8164 | 0.045776 | -0.10071 | 61.821 | -61.6562 | 61.8393 | -0.87891 | -61.647 | -61.2396 | -0.28381 | 0.050354 | -0.11902 | 123.1842 | 61.6104 | -0.25177 | 61.8942 | 0.032044 | -0.091553 | 0.068665 | 0.086975 | 60.6857 | 0.32501 | -0.082398 | 0.41656 | 0.009155 | 123.468 | 123.4818 | 60.7773 | 123.4955 | 123.6511 | 123.4772 | 123.3673 | 123.3856 | -123.6008 | -123.4085 | 123.1979 | 123.4039 | 61.6104 | 61.4639
243 | 123.4955 | -61.5509 | 61.7798 | 0.040589 | 0.0012989 | -0.00011109 | 0.0028732 | 0.0022538 | -0.0021384 | 0.00011544 | -0.10406 | 0.00076898 | 0.033259 | 0.036307 | -0.0023605 | 7.2706e-05 | -0.00057035 | 0.10986 | 61.8484 | -61.8347 | 61.6379 | 61.5967 | -61.8073 | 0.10529 | 0.004578 | 61.8484 | -61.6653 | 61.8439 | -0.90179 | -61.6745 | -61.2442 | -0.28381 | 0.068665 | -0.14191 | 123.1476 | 61.6562 | -0.25635 | 61.94 | 0.027466 | -0.11444 | 0.068665 | 0.064087 | 60.6491 | 0.3067 | -0.1236 | 0.42114 | -0.009156 | 123.4314 | 123.4726 | 60.7635 | 123.5092 | 123.6832 | 123.5138 | 123.3994 | 123.3994 | -123.6145 | -123.4451 | 123.1888 | 123.3948 | 61.6608 | 61.5555
243.9844 | 123.5641 | -61.5921 | 61.734 | -0.020447 | 1.7082e-05 | 0.0013843 | 0.003514 | -0.0020188 | 0.002775 | 0.0016106 | -0.021668 | 0.0011964 | 0.034968 | 0.03353 | 0.00041666 | 0.00028631 | -0.0012111 | 0.054932 | 61.8027 | -61.8256 | 61.6196 | 61.6196 | -61.8027 | 0.045776 | -0.13275 | 61.7844 | -61.647 | 61.8347 | -0.88348 | -61.6562 | -61.2167 | -0.23346 | 0.068664 | -0.11444 | 123.2117 | 61.6379 | -0.21057 | 61.8713 | 0.022889 | -0.054932 | 0.050354 | 0.10071 | 60.7086 | 0.37537 | -0.064087 | 0.4303 | -0.009155 | 123.4451 | 123.4451 | 60.7635 | 123.4818 | 123.6282 | 123.4314 | 123.3948 | 123.3765 | -123.5596 | -123.381 | 123.2117 | 123.4268 | 61.647 | 61.4594
244.9844 | 123.5733 | -61.5326 | 61.7477 | -0.050964 | 1.7082e-05 | 0.0011707 | -0.0013992 | -0.0015914 | 0.00042517 | -0.00095276 | 0.0088501 | -0.00094002 | 0.033473 | 0.029044 | -0.0010787 | -0.00099549 | -0.00035675 | 0.064087 | 61.8256 | -61.8073 | 61.647 | 61.6058 | -61.8027 | 0.09613 | -0.073242 | 61.7981 | -61.6562 | 61.8713 | -0.82855 | -61.5921 | -61.1755 | -0.27466 | 0.07782 | -0.10071 | 123.1384 | 61.6287 | -0.27008 | 61.9034 | 0.004578 | -0.1236 | 0.050354 | 0.1236 | 60.704 | 0.35706 | -0.059509 | 0.48065 | 0.064087 | 123.4131 | 123.4543 | 60.8276 | 123.5275 | 123.6328 | 123.4543 | 123.3582 | 123.3307 | -123.555 | -123.4039 | 123.1796 | 123.4039 | 61.5967 | 61.4594
245.9844 | 123.5916 | -61.5463 | 61.7523 | -0.028076 | -0.00041012 | 0.00010251 | 0.0015914 | -0.003514 | 0.0012796 | -9.8356e-05 | -0.015564 | 0.00034178 | 0.033045 | 0.034385 | -0.0017197 | -0.0022773 | 0.00092505 | 0.059509 | 61.8393 | -61.8164 | 61.6058 | 61.5875 | -61.8073 | 0.07782 | -0.11444 | 61.8164 | -61.6562 | 61.8393 | -0.84686 | -61.7111 | -61.0977 | -0.27008 | 0.086975 | -0.14648 | 123.1338 | 61.6241 | -0.26093 | 61.8942 | 0.009155 | -0.10986 | 0.064087 | 0.086975 | 60.6995 | 0.44861 | -0.16479 | 0.55847 | -0.054932 | 123.4039 | 123.4222 | 60.8093 | 123.4955 | 123.6557 | 123.4726 | 123.3856 | 123.3627 | -123.5687 | -123.4085 | 123.1522 | 123.3856 | 61.6058 | 61.4319
246.9844 | 123.5825 | -61.5234 | 61.7706 | -0.043335 | 0.00087168 | 0.0022387 | -0.00011758 | 0.0016128 | 0.0025614 | 0.00075624 | 0.0027465 | -8.5416e-05 | 0.035182 | 0.028831 | -0.0010787 | -0.0024909 | 0.0030613 | 0.10529 | 61.8301 | -61.8073 | 61.6791 | 61.6837 | -61.734 | 0.1831 | 0.082397 | 61.8393 | -61.6287 | 61.9308 | -0.75531 | -61.5326 | -61.1526 | -0.28381 | 0.059509 | -0.091553 | 123.2071 | 61.7065 | -0.21057 | 61.9904 | 0.073242 | -0.10529 | 0.068664 | 0.16022 | 60.7681 | 0.37079 | -0.009156 | 0.47607 | 0.09613 | 123.4909 | 123.4863 | 60.8734 | 123.5596 | 123.6374 | 123.468 | 123.3536 | 123.3627 | -123.5779 | -123.3994 | 123.2025 | 123.4543 | 61.6287 | 61.6058
247.9844 | 123.4863 | -61.5601 | 61.8073 | 0.040589 | 0.00044428 | 0.00031611 | 0.00095062 | -0.0028732 | -0.00085663 | 0.0033196 | -0.039978 | 0.00076898 | 0.033045 | 0.036735 | -1.0744e-05 | -0.0014227 | -0.0020657 | 0.10986 | 61.8942 | -61.8439 | 61.7432 | 61.7203 | -62.1048 | 0.036621 | -0.10529 | 61.8668 | -61.6379 | 61.7889 | -0.89722 | -61.6882 | -61.2534 | -0.28381 | 0.086975 | -0.064087 | 123.2803 | 61.5967 | -0.54474 | 61.8805 | -0.26093 | -0.077819 | 0.059509 | -0.018311 | 60.6628 | 0.3067 | -0.12817 | 0.38452 | -0.050354 | 123.5641 | 123.587 | 60.7407 | 123.4268 | 123.7381 | 123.5046 | 123.4543 | 123.4268 | -123.6511 | -123.4451 | 123.3032 | 123.349 | 61.6699 | 61.4548
248.9844 | 123.6008 | -61.5372 | 61.7935 | -0.035705 | -0.0010511 | -0.0018201 | -0.00075838 | -0.0013778 | -0.0025656 | -0.00138 | 0.0057983 | 0.00098258 | 0.031977 | 0.036094 | -0.0023605 | -0.0012091 | 0.00049765 | 0.13275 | 61.8301 | -61.7935 | 61.6837 | 61.6745 | -61.7294 | 0.18768 | 0.054932 | 61.8256 | -61.6241 | 61.9217 | -0.76904 | -61.5326 | -61.116 | -0.25635 | 0.036621 | -0.10986 | 123.2117 | 61.7249 | -0.19226 | 61.9812 | 0.064087 | -0.086976 | 0.032044 | 0.12817 | 60.7681 | 0.42114 | 0.004577 | 0.50812 | 0.091553 | 123.468 | 123.4772 | 60.8551 | 123.5458 | 123.6237 | 123.4497 | 123.3673 | 123.3627 | -123.587 | -123.4177 | 123.2208 | 123.4589 | 61.6699 | 61.5921
249.9844 | 123.5367 | -61.5509 | 61.7935 | 0.048218 | -0.0012647 | -0.00096549 | 0.0013778 | -0.002446 | 0.00042517 | -0.0022346 | -0.015564 | -0.00029902 | 0.035609 | 0.033103 | -0.0021469 | -0.00099549 | -0.0027065 | 0.07782 | 61.8164 | -61.8393 | 61.6058 | 61.5967 | -61.8301 | 0.10529 | -0.13733 | 61.8027 | -61.6379 | 61.8622 | -0.7782 | -61.6653 | -61.2259 | -0.28839 | 0.022888 | -0.18768 | 123.1476 | 61.6562 | -0.27924 | 61.9446 | 0.009155 | -0.086975 | 0.009155 | 0.068665 | 60.7727 | 0.32501 | -0.11444 | 0.41199 | -0.027466 | 123.436 | 123.4451 | 60.8597 | 123.5001 | 123.6557 | 123.4406 | 123.3673 | 123.3536 | -123.6328 | -123.4314 | 123.1567 | 123.4131 | 61.6287 | 61.4136
250.9844 | 123.5779 | -61.5372 | 61.7569 | 0.0024415 | 0.0021533 | -0.0022473 | 0.0011642 | -0.0030868 | -0.00085663 | -9.8356e-05 | -0.024719 | -0.0024352 | 0.030268 | 0.035453 | 0.00020286 | 0.00092711 | -0.00014315 | 0.17853 | 61.8576 | -61.7981 | 61.7065 | 61.7111 | -61.7157 | 0.19684 | 0.36163 | 61.8805 | -61.5738 | 61.908 | -0.75531 | -61.5692 | -61.171 | -0.26093 | 0.10071 | -0.050354 | 123.2483 | 61.734 | -0.17853 | 61.9949 | 0.082398 | -0.036622 | 0.1236 | 0.15106 | 60.7819 | 0.36621 | -0.032044 | 0.40283 | 0.004578 | 123.5092 | 123.5046 | 60.8185 | 123.4818 | 123.6557 | 123.4543 | 123.3948 | 123.4177 | -123.555 | -123.3307 | 123.2437 | 123.4451 | 61.7157 | 61.8988
251.9844 | 123.5641 | -61.5463 | 61.7523 | -0.10437 | -0.00062372 | 0.00010251 | -0.00054478 | -0.0015914 | 0.0019204 | -0.00052556 | -0.0094605 | -0.002008 | 0.034754 | 0.033103 | -0.0010787 | -0.00035469 | -0.0020657 | 0.07782 | 61.821 | -61.8073 | 61.6241 | 61.5829 | -61.8073 | 0.09613 | -0.13733 | 61.8073 | -61.6562 | 61.8164 | -0.76904 | -61.702 | -61.2076 | -0.26093 | 0.068665 | -0.12817 | 123.1293 | 61.6425 | -0.26093 | 61.9034 | 0 | -0.10986 | 0.054932 | 0.064087 | 60.7773 | 0.33875 | -0.15564 | 0.44861 | -0.045776 | 123.3902 | 123.4314 | 60.8871 | 123.4726 | 123.6282 | 123.4634 | 123.3673 | 123.3536 | -123.5596 | -123.4085 | 123.1705 | 123.3627 | 61.6241 | 61.409
253 | 123.4818 | -61.5692 | 61.7844 | -0.058594 | -0.0031873 | 0.0018115 | 0.0026596 | -0.0013778 | -0.0012838 | 0.0018242 | -0.12848 | 0.002478 | 0.030482 | 0.035667 | -0.00086514 | 0.00028631 | 0.00049765 | 0.036621 | 61.8027 | -61.8713 | 61.6058 | 61.5921 | -61.8164 | 0.073242 | -0.07782 | 61.8484 | -61.6653 | 61.8256 | -0.9201 | -61.7065 | -61.2534 | -0.30212 | 0.01831 | -0.17853 | 123.1613 | 61.6425 | -0.24719 | 61.9446 | 0.054932 | -0.09613 | 0.064087 | 0.041199 | 60.6491 | 0.31586 | -0.13733 | 0.41199 | -0.041199 | 123.4634 | 123.4772 | 60.7452 | 123.4909 | 123.674 | 123.5138 | 123.3719 | 123.4177 | -123.6557 | -123.4497 | 123.175 | 123.3948 | 61.6058 | 61.4914
253.9844 | 123.5504 | -61.5326 | 61.7569 | -0.10437 | 0.00087168 | -0.00053829 | 0.00030982 | -9.604e-05 | -0.00042943 | -0.0015936 | 0.0057983 | 0.00012818 | 0.034541 | 0.033744 | -0.00022434 | 0.00028631 | 0.00049765 | 0.09613 | 61.8256 | -61.8073 | 61.6516 | 61.647 | -61.7798 | 0.14648 | -0.073242 | 61.8027 | -61.6379 | 61.8805 | -0.81482 | -61.5967 | -61.1755 | -0.27466 | 0.068665 | -0.10529 | 123.1796 | 61.6791 | -0.24719 | 61.9537 | 0.027466 | -0.10529 | 0.045776 | 0.1236 | 60.7178 | 0.35706 | -0.064087 | 0.46234 | 0.041198 | 123.4543 | 123.4589 | 60.8231 | 123.5184 | 123.6328 | 123.4406 | 123.3582 | 123.3353 | -123.5641 | -123.3948 | 123.1842 | 123.4131 | 61.6287 | 61.4594
254.9844 | 123.587 | -61.528 | 61.7661 | 0.071106 | 0.0012989 | 0.0011707 | -0.0020402 | -0.0011642 | -0.0010702 | 0.00096984 | 0.011902 | -8.5416e-05 | 0.030055 | 0.028617 | 0.00041666 | 0.00049991 | -0.0014249 | 0.19684 | 61.853 | -61.7935 | 61.702 | 61.7065 | -61.7157 | 0.21515 | 0.3479 | 61.8713 | -61.5921 | 61.8622 | -0.75989 | -61.5829 | -61.1618 | -0.2655 | 0.086975 | -0.064087 | 123.2346 | 61.7432 | -0.18768 | 62.0087 | 0.07782 | -0.064087 | 0.10529 | 0.096131 | 60.7681 | 0.36621 | -0.054932 | 0.4303 | 0.009155 | 123.5001 | 123.4955 | 60.8322 | 123.4543 | 123.6465 | 123.4634 | 123.381 | 123.3994 | -123.5596 | -123.3582 | 123.23 | 123.3902 | 61.7249 | 61.8759
255.9844 | 123.5641 | -61.5555 | 61.7615 | -0.005188 | 0.0021533 | 0.00010251 | -0.00033118 | -0.00095064 | -0.00021583 | -0.00073916 | 0.018005 | -0.002008 | 0.032832 | 0.030112 | -0.0021469 | -0.00078189 | -0.0027065 | 0.10071 | 61.8301 | -61.8164 | 61.6425 | 61.6241 | -61.7798 | 0.15106 | -0.073242 | 61.8073 | -61.6608 | 61.8759 | -0.8194 | -61.5784 | -61.1664 | -0.26093 | 0.068664 | -0.11902 | 123.1796 | 61.7065 | -0.2243 | 61.9675 | 0.036621 | -0.10529 | 0.045776 | 0.11444 | 60.7361 | 0.3891 | -0.022888 | 0.49439 | 0.082398 | 123.4406 | 123.4589 | 60.8414 | 123.5367 | 123.6465 | 123.468 | 123.3856 | 123.3627 | -123.5779 | -123.4222 | 123.1979 | 123.4314 | 61.6562 | 61.4822
256.9844 | 123.5046 | -61.5326 | 61.7889 | 0.0177 | -0.00041012 | -0.0022473 | 0.0015914 | -0.0011642 | 0.001066 | 0.00054264 | -0.024719 | 0.0016236 | 0.031336 | 0.036521 | -0.00043794 | -0.00056829 | -0.0029201 | 0.20142 | 61.8484 | -61.7889 | 61.6699 | 61.6745 | -61.7432 | 0.21515 | 0.004578 | 61.8576 | -61.6104 | 61.8484 | -0.83771 | -61.6104 | -61.2076 | -0.25635 | 0.05951 | -0.11902 | 123.2071 | 61.7477 | -0.21057 | 62.0041 | 0.045776 | -0.07782 | 0.068665 | 0.05951 | 60.6949 | 0.32501 | -0.07782 | 0.40283 | 0 | 123.4634 | 123.4589 | 60.7727 | 123.4589 | 123.6374 | 123.468 | 123.381 | 123.3902 | -123.5779 | -123.3994 | 123.2025 | 123.381 | 61.734 | 61.5372
258 | 123.5184 | -61.5555 | 61.8118 | 0.010071 | -0.00041012 | 0.0024523 | -0.0020402 | 0.0024674 | -2.232e-06 | -0.00073916 | -0.11627 | 0.00012818 | 0.032832 | 0.033958 | -0.0017197 | 0.0028497 | -0.00078395 | 0.16022 | 61.8347 | -61.8484 | 61.615 | 61.6013 | -61.7935 | 0.11444 | -0.059509 | 61.8713 | -61.647 | 61.8073 | -0.9201 | -61.7157 | -61.2579 | -0.29297 | 0.022888 | -0.19684 | 123.1567 | 61.6699 | -0.23804 | 61.9629 | 0.054932 | -0.091553 | 0.059509 | -0.004578 | 60.6354 | 0.29755 | -0.16022 | 0.3891 | -0.068664 | 123.4497 | 123.4634 | 60.7269 | 123.4543 | 123.6832 | 123.5184 | 123.3902 | 123.4268 | -123.6603 | -123.4589 | 123.1705 | 123.3627 | 61.7157 | 61.496
258.9844 | 123.6191 | -61.5326 | 61.7615 | 0.0177 | -0.00062372 | 0.00010251 | -0.0033218 | -0.0020188 | -2.232e-06 | -0.00095276 | 0.021057 | 0.00141 | 0.035822 | 0.030967 | -0.0025741 | -0.0065497 | 0.0039157 | 0.20142 | 61.8439 | -61.7844 | 61.6791 | 61.702 | -61.7249 | 0.22888 | 0.036621 | 61.8118 | -61.6241 | 62.0956 | -0.90179 | -61.7569 | -61.2213 | -0.25177 | 0.082397 | -0.082398 | 123.2346 | 61.7615 | -0.19226 | 62.0132 | 0.059509 | -0.091553 | 0.050354 | 0.33417 | 60.6308 | 0.31128 | -0.2243 | 0.40283 | -0.13275 | 123.4863 | 123.4634 | 60.7224 | 123.7198 | 123.6282 | 123.436 | 123.3765 | 123.3444 | -123.5458 | -123.3856 | 123.2117 | 123.6282 | 61.734 | 61.5692
259.9844 | 123.6099 | -61.5234 | 61.7477 | -0.035705 | 0.0015125 | -0.00075189 | -0.0013992 | -0.0037276 | 0.0032022 | 0.0011834 | 0.021057 | -0.00029902 | 0.033473 | 0.039512 | -0.00065154 | -0.0014227 | 0.0015659 | 0.1831 | 61.8393 | -61.8027 | 61.6608 | 61.6791 | -61.734 | 0.20142 | -0.009155 | 61.821 | -61.6241 | 61.9125 | -0.7782 | -61.5509 | -61.1343 | -0.27924 | 0.091552 | -0.086975 | 123.2025 | 61.7249 | -0.21057 | 62.0041 | 0.068664 | -0.10071 | 0.073242 | 0.16479 | 60.7452 | 0.3891 | -0.027466 | 0.48981 | 0.073243 | 123.4818 | 123.4634 | 60.8459 | 123.5367 | 123.642 | 123.4451 | 123.3627 | 123.3444 | -123.5504 | -123.3719 | 123.1842 | 123.436 | 61.7065 | 61.5143
260.9844 | 123.5458 | -61.5417 | 61.8027 | 0.010071 | -0.00041012 | -0.00011109 | 0.001805 | -0.0028732 | 0.0021342 | 0.00011544 | 0.0027465 | -0.0013672 | 0.033045 | 0.041221 | 0.0010575 | -0.00099549 | -0.0018521 | 0.20142 | 61.8347 | -61.8301 | 61.6745 | 61.6928 | -61.7294 | 0.23346 | 0.018311 | 61.8393 | -61.6241 | 61.8713 | -0.83313 | -61.5967 | -61.1801 | -0.28839 | 0.032044 | -0.12817 | 123.2346 | 61.7752 | -0.18768 | 62.0636 | 0.10071 | -0.082398 | 0.036621 | 0.068665 | 60.7086 | 0.36163 | -0.054932 | 0.44403 | 0.027466 | 123.5229 | 123.5046 | 60.791 | 123.4955 | 123.6649 | 123.4634 | 123.3765 | 123.381 | -123.6328 | -123.4268 | 123.2162 | 123.4131 | 61.7432 | 61.5601
261.9844 | 123.6099 | -61.5372 | 61.7615 | -0.043335 | 0.0017261 | 0.00074331 | -0.00011758 | 0.0016128 | -0.00085663 | -0.002021 | 0.024109 | -0.00051262 | 0.032618 | 0.037376 | -0.00065154 | -0.0022773 | 0.0017795 | 0.15106 | 61.821 | -61.8118 | 61.6745 | 61.6699 | -61.7386 | 0.19684 | -0.032043 | 61.8256 | -61.6287 | 61.908 | -0.75989 | -61.5738 | -61.1435 | -0.27466 | 0.059509 | -0.086975 | 123.2071 | 61.734 | -0.20142 | 62.0087 | 0.073243 | -0.091553 | 0.064087 | 0.14648 | 60.7773 | 0.39368 | -0.036622 | 0.48523 | 0.054931 | 123.4818 | 123.4863 | 60.8688 | 123.5367 | 123.6328 | 123.4543 | 123.3582 | 123.3627 | -123.5733 | -123.3902 | 123.2117 | 123.4451 | 61.6882 | 61.5051
262.9844 | 123.5321 | -61.5601 | 61.7844 | 0.048218 | 0.0015125 | 0.00052971 | -0.00011758 | -9.604e-05 | 0.0019204 | -0.003089 | -0.0064087 | 0.00012818 | 0.033045 | 0.03588 | -0.0021469 | -0.0020637 | 0.0022067 | 0.14648 | 61.8256 | -61.821 | 61.6974 | 61.6653 | -61.7432 | 0.23804 | 0 | 61.8301 | -61.6333 | 61.8713 | -0.82398 | -61.5921 | -61.1801 | -0.26093 | 0.041199 | -0.086975 | 123.2254 | 61.7981 | -0.1831 | 62.059 | 0.07782 | -0.073242 | 0.045776 | 0.086975 | 60.7361 | 0.37994 | -0.032043 | 0.45319 | 0.041199 | 123.4863 | 123.5184 | 60.8093 | 123.5046 | 123.6465 | 123.4634 | 123.3856 | 123.3902 | -123.6053 | -123.4177 | 123.2574 | 123.4314 | 61.7065 | 61.5601
263.9844 | 123.6053 | -61.528 | 61.7477 | 0.0177 | 1.7082e-05 | 0.0013843 | -0.00033118 | 0.00054476 | 0.0017068 | 0.00032904 | 0.014954 | 0.00012818 | 0.034754 | 0.027976 | -0.00022434 | -0.0029181 | -0.0048427 | 0.21973 | 61.8256 | -61.7752 | 61.7065 | 61.7386 | -61.6791 | 0.25177 | 0.009155 | 61.8164 | -61.6058 | 61.9034 | -0.79651 | -61.5646 | -61.1664 | -0.24719 | 0.07782 | -0.041199 | 123.2666 | 61.7798 | -0.15106 | 62.027 | 0.096131 | -0.07782 | 0.068664 | 0.15564 | 60.7315 | 0.36163 | -0.036621 | 0.43945 | 0.041199 | 123.5138 | 123.4818 | 60.8093 | 123.5092 | 123.6008 | 123.4222 | 123.3536 | 123.3444 | -123.523 | -123.3536 | 123.2346 | 123.4314 | 61.7477 | 61.5372
264.9844 | 123.5458 | -61.5189 | 61.7844 | 0.040589 | 0.0019397 | -0.0033155 | 0.001805 | 0.00054476 | 0.0014932 | 0.0011834 | -0.00030511 | -0.0013672 | 0.033473 | 0.036948 | -0.0023605 | -0.0014227 | 0.00028405 | 0.44861 | 61.8942 | -61.7615 | 61.6928 | 61.702 | -61.7432 | 0.24719 | -0.022888 | 61.8301 | -61.6333 | 61.8805 | -0.79651 | -61.5555 | -61.1618 | -0.24262 | 0.10986 | -0.091553 | 123.2208 | 61.7661 | -0.2243 | 62.0087 | 0.018311 | -0.11444 | 0.045776 | 0.09613 | 60.7224 | 0.35706 | -0.036621 | 0.4715 | 0.07782 | 123.4634 | 123.4543 | 60.8368 | 123.5138 | 123.6557 | 123.4634 | 123.4131 | 123.349 | -123.5458 | -123.4177 | 123.2117 | 123.3994 | 61.9675 | 61.496
265.9844 | 123.6053 | -61.5463 | 61.7661 | -0.035705 | 0.0012989 | -0.0013929 | 0.0015914 | -0.001805 | 0.0012796 | -0.0035162 | 0.0057983 | 0.00141 | 0.034754 | 0.034812 | -0.0025741 | -0.00056829 | -0.00099755 | 0.16937 | 61.8301 | -61.8118 | 61.6745 | 61.6516 | -61.7615 | 0.21057 | -0.10986 | 61.821 | -61.6425 | 61.8759 | -0.80109 | -61.5738 | -61.1572 | -0.2655 | 0.064087 | -0.091552 | 123.1979 | 61.7569 | -0.21515 | 62.0224 | 0.050354 | -0.09613 | 0.054932 | 0.10986 | 60.7452 | 0.3891 | -0.027466 | 0.48523 | 0.068664 | 123.4634 | 123.4863 | 60.8414 | 123.5184 | 123.642 | 123.4634 | 123.3765 | 123.3673 | -123.5779 | -123.4085 | 123.2208 | 123.4222 | 61.7157 | 61.4365
266.9844 | 123.4909 | -61.5463 | 61.8256 | -0.050964 | 0.00023068 | -0.00053829 | 0.00052342 | 0.0013992 | -0.0012838 | -0.00373 | -0.030823 | 0.00034178 | 0.033473 | 0.031821 | -0.0030013 | -0.0020637 | -0.0035611 | 0.23804 | 61.8622 | -61.8164 | 61.6516 | 61.6653 | -61.7386 | 0.23346 | -0.045776 | 61.8805 | -61.6196 | 61.8256 | -0.87433 | -61.6333 | -61.2076 | -0.27008 | 0.036621 | -0.17395 | 123.2117 | 61.7798 | -0.19226 | 62.0499 | 0.07782 | -0.073242 | 0.054931 | 0 | 60.672 | 0.33875 | -0.086975 | 0.41199 | -0.013733 | 123.4818 | 123.468 | 60.7452 | 123.4451 | 123.6786 | 123.5001 | 123.4085 | 123.4268 | -123.642 | -123.4451 | 123.1979 | 123.3719 | 61.7844 | 61.5006
267.9844 | 123.6053 | -61.5189 | 61.7523 | -0.035705 | -0.00062372 | -0.00032469 | 9.6222e-05 | -0.00073704 | -0.001711 | 0.003747 | 0.018005 | 0.00055538 | 0.032405 | 0.034812 | -0.0015059 | -0.00078189 | -0.00099755 | 0.20599 | 61.853 | -61.8027 | 61.6837 | 61.6974 | -61.702 | 0.25177 | -0.027466 | 61.8439 | -61.6104 | 61.9125 | -0.75073 | -61.528 | -61.1343 | -0.28381 | 0.10071 | -0.068664 | 123.2162 | 61.7706 | -0.18311 | 62.0544 | 0.10071 | -0.091553 | 0.091553 | 0.16022 | 60.7681 | 0.38452 | -0.009155 | 0.47608 | 0.082398 | 123.5001 | 123.4863 | 60.8597 | 123.523 | 123.6557 | 123.4543 | 123.3719 | 123.3627 | -123.555 | -123.3627 | 123.2025 | 123.4314 | 61.7249 | 61.4914
268.9844 | 123.5138 | -61.5189 | 61.8256 | -0.058594 | -0.0012647 | 0.00095711 | 0.0013778 | -0.00095064 | -0.0014974 | -0.0035162 | -0.0064087 | 0.00034178 | 0.033473 | 0.035239 | -0.0017197 | -0.00078189 | -0.00078395 | 0.24261 | 61.8393 | -61.7935 | 61.6837 | 61.6699 | -61.7523 | 0.24261 | -0.050354 | 61.8347 | -61.6241 | 61.8439 | -0.85602 | -61.6333 | -61.1938 | -0.27466 | 0.013732 | -0.14191 | 123.1888 | 61.7615 | -0.23346 | 62.0361 | 0.041199 | -0.10529 | 0.009155 | 0.01831 | 60.6628 | 0.32501 | -0.11444 | 0.4303 | -0.009155 | 123.4634 | 123.4772 | 60.7681 | 123.468 | 123.6328 | 123.4589 | 123.3582 | 123.3536 | -123.6191 | -123.4497 | 123.2025 | 123.3627 | 61.7615 | 61.4685
269.9844 | 123.6053 | -61.5051 | 61.7477 | 0.0177 | -0.00062372 | 0.00074331 | 0.00052342 | -0.0013778 | -0.001711 | 0.00011544 | 0.0027465 | 0.00076898 | 0.034113 | 0.032462 | -0.0010787 | -0.0014227 | -0.0014249 | 0.20599 | 61.8393 | -61.8118 | 61.6791 | 61.6653 | -61.7523 | 0.23804 | -0.082397 | 61.8256 | -61.6516 | 61.8805 | -0.80109 | -61.528 | -61.1435 | -0.3067 | 0.091552 | -0.068665 | 123.1705 | 61.7432 | -0.24719 | 62.0499 | 0.05951 | -0.14648 | 0.07782 | 0.13275 | 60.704 | 0.36163 | -0.022888 | 0.50812 | 0.1236 | 123.4772 | 123.4909 | 60.8505 | 123.5321 | 123.6511 | 123.4772 | 123.3444 | 123.3307 | -123.5596 | -123.3994 | 123.1842 | 123.3856 | 61.7111 | 61.4227
270.9844 | 123.468 | -61.5601 | 61.821 | 0.032959 | 0.0010853 | 0.0011707 | 0.00073702 | -0.0013778 | 0.001066 | -0.0028754 | -0.036926 | -8.5416e-05 | 0.034541 | 0.038444 | -1.0744e-05 | -0.00056829 | 0.0022067 | 0.24261 | 61.8439 | -61.8118 | 61.615 | 61.615 | -61.7798 | 0.21973 | -0.12817 | 61.8759 | -61.6379 | 61.8027 | -0.91553 | -61.6745 | -61.2717 | -0.25177 | 0.022888 | -0.20599 | 123.175 | 61.7798 | -0.21973 | 62.0316 | 0.032044 | -0.077819 | 0.054932 | -0.018311 | 60.6445 | 0.28839 | -0.11444 | 0.36621 | -0.036622 | 123.4268 | 123.4268 | 60.7224 | 123.4406 | 123.6557 | 123.5138 | 123.4039 | 123.436 | -123.6328 | -123.4589 | 123.175 | 123.3627 | 61.8027 | 61.4319
271.9844 | 123.587 | -61.5143 | 61.7523 | 0.02533 | 0.0021533 | -0.0011793 | 0.0020188 | -0.0011642 | -0.00042943 | 0.0016106 | 0.030212 | 0.00012818 | 0.036036 | 0.032249 | 0.00063026 | -0.0016363 | -0.00078395 | 0.20142 | 61.8256 | -61.7935 | 61.6837 | 61.6425 | -61.7615 | 0.2243 | -0.12817 | 61.7935 | -61.6425 | 61.908 | -0.79193 | -61.5692 | -61.1526 | -0.27924 | 0.073243 | -0.068664 | 123.1567 | 61.7386 | -0.24719 | 62.0178 | 0.032043 | -0.12817 | 0.041199 | 0.15564 | 60.7224 | 0.36163 | -0.054932 | 0.48981 | 0.073242 | 123.436 | 123.4772 | 60.8505 | 123.5504 | 123.6191 | 123.436 | 123.3398 | 123.3078 | -123.5458 | -123.3948 | 123.1979 | 123.4222 | 61.7157 | 61.3861
272.9844 | 123.555 | -61.5372 | 61.7798 | 0.0024415 | 0.0017261 | -0.00075189 | -0.0022538 | -0.0037276 | 0.00021157 | 0.00075624 | 0.018005 | -0.00029902 | 0.033045 | 0.032035 | -1.0744e-05 | -0.00014089 | -0.00014315 | 0.25635 | 61.8439 | -61.7798 | 61.5784 | 61.7798 | -61.8164 | 0.21973 | -0.091553 | 61.8164 | -61.6333 | 61.8942 | -0.80566 | -61.5601 | -61.1664 | -0.24261 | 0.064087 | -0.20142 | 123.317 | 61.7569 | -0.27924 | 61.9995 | -0.036621 | -0.096131 | 0.036621 | 0.11444 | 60.7315 | 0.37079 | -0.022889 | 0.46692 | 0.073242 | 123.5596 | 123.3582 | 60.8276 | 123.5275 | 123.6237 | 123.4497 | 123.381 | 123.3536 | -123.5596 | -123.4131 | 123.1155 | 123.4314 | 61.7935 | 61.4456
273.9844 | 123.6237 | -61.5189 | 61.7706 | -0.058594 | -0.00041012 | 0.00010251 | 9.6222e-05 | 0.00075836 | -0.00042943 | -0.0028754 | 0.021057 | 0.00055538 | 0.034113 | 0.034385 | -0.0010787 | 0.0011407 | -0.0046291 | 0.23804 | 61.8576 | -61.7981 | 61.6974 | 61.7065 | -61.6974 | 0.27466 | -0.068665 | 61.8256 | -61.6287 | 61.9263 | -0.7782 | -61.5189 | -61.1252 | -0.27924 | 0.086975 | -0.073242 | 123.2254 | 61.7935 | -0.17853 | 62.0728 | 0.10071 | -0.10986 | 0.054932 | 0.15564 | 60.7407 | 0.39368 | 0 | 0.50354 | 0.10986 | 123.5046 | 123.4955 | 60.8505 | 123.555 | 123.6557 | 123.4543 | 123.3765 | 123.3444 | -123.5687 | -123.3994 | 123.2162 | 123.4451 | 61.7569 | 61.4502
274.9844 | 123.5367 | -61.5463 | 61.8073 | -0.028076 | 0.0015125 | 0.00095711 | -0.00054478 | 0.0013992 | -0.0025656 | -0.002021 | 0.0088501 | 0.00055538 | 0.034113 | 0.034812 | -0.0015059 | -0.00078189 | 0.00049765 | 0.25635 | 61.8301 | -61.8027 | 61.6745 | 61.6653 | -61.7432 | 0.2655 | -0.10071 | 61.8668 | -61.6241 | 61.8439 | -0.85144 | -61.6196 | -61.203 | -0.25635 | 0.022888 | -0.13275 | 123.2117 | 61.8118 | -0.19684 | 62.0682 | 0.059509 | -0.07782 | 0.059509 | 0.036621 | 60.6949 | 0.34332 | -0.073242 | 0.42114 | 0.004578 | 123.468 | 123.4772 | 60.7727 | 123.468 | 123.6328 | 123.4909 | 123.3765 | 123.4131 | -123.6099 | -123.4314 | 123.2208 | 123.3902 | 61.8027 | 61.4456
276.0469 | 123.5687 | -61.5417 | 61.7615 | -0.050964 | 0.0021533 | -0.00011109 | 0.0015914 | 0.0016128 | 0.001066 | -0.00073916 | -0.058289 | -0.00094002 | 0.032618 | 0.035667 | -0.0019333 | 0.0017817 | -0.0063381 | 0.20599 | 61.8027 | -61.8301 | 61.6562 | 61.6333 | -61.7798 | 0.15564 | -0.25177 | 61.7889 | -61.6653 | 61.7935 | -0.69122 | -61.4822 | -61.1755 | -0.28839 | 0.041198 | -0.10529 | 123.175 | 61.6974 | -0.23804 | 61.9858 | 0.050354 | -0.1236 | 0.027465 | 0.032043 | 60.8505 | 0.36621 | 0.059509 | 0.48981 | 0.1831 | 123.4634 | 123.4863 | 60.9741 | 123.4589 | 123.6328 | 123.4543 | 123.3444 | 123.3307 | -123.5916 | -123.4268 | 123.1979 | 123.3353 | 61.7477 | 61.29
276.9844 | 123.5733 | -61.5417 | 61.821 | 0.0024415 | 0.0019397 | -0.0020337 | 9.6222e-05 | -0.0028732 | -0.0032064 | 0.00054264 | -0.00030511 | 0.00012818 | 0.034754 | 0.030326 | -0.0015059 | -0.0012091 | -0.0022793 | 0.2655 | 61.821 | -61.7981 | 61.6699 | 61.6928 | -61.7111 | 0.29297 | -0.11444 | 61.8393 | -61.6379 | 61.853 | -0.83771 | -61.615 | -61.1938 | -0.25635 | 0 | -0.15106 | 123.2346 | 61.8347 | -0.16937 | 62.0911 | 0.086975 | -0.09613 | 0.01831 | 0.032043 | 60.704 | 0.3479 | -0.073242 | 0.44403 | 0.022888 | 123.4909 | 123.468 | 60.8002 | 123.4909 | 123.6191 | 123.4772 | 123.3627 | 123.381 | -123.6191 | -123.4589 | 123.2117 | 123.3948 | 61.8073 | 61.4273
277.9844 | 123.4909 | -61.5097 | 61.7569 | -0.012817 | 0.00044428 | -0.00011109 | -0.0022538 | -0.0011642 | 0.00063877 | -0.0024482 | -0.012512 | 0.00012818 | 0.033686 | 0.032035 | -0.00043794 | -0.00099549 | -0.0033475 | 0.27924 | 61.853 | -61.7844 | 61.6928 | 61.7065 | -61.7157 | 0.28839 | -0.09613 | 61.8347 | -61.6333 | 61.8896 | -0.71411 | -61.2579 | -61.0474 | -0.27466 | 0.09613 | -0.064087 | 123.2162 | 61.7981 | -0.20599 | 62.0728 | 0.068665 | -0.1236 | 0.07782 | 0.13275 | 60.7956 | 0.46234 | 0.25177 | 0.58594 | 0.37537 | 123.4909 | 123.4772 | 60.9192 | 123.5229 | 123.6374 | 123.468 | 123.3627 | 123.3444 | -123.5413 | -123.3902 | 123.2025 | 123.3994 | 61.7889 | 61.4136
278.9844 | 123.5504 | -61.5234 | 61.7615 | -0.073852 | 0.0019397 | 0.00010251 | -0.00033118 | -0.0015914 | 0.0012796 | -0.00138 | 0.0088501 | -0.00094002 | 0.032191 | 0.036521 | -0.0015059 | 0.00028631 | -0.00014315 | 0.27008 | 61.8393 | -61.7981 | 61.6974 | 61.6745 | -61.7523 | 0.27466 | -0.13275 | 61.8622 | -61.6104 | 61.8668 | -0.82855 | -61.5738 | -61.171 | -0.27466 | 0.077819 | -0.064087 | 123.1979 | 61.7981 | -0.22888 | 62.0728 | 0.045777 | -0.086976 | 0.10071 | 0.10529 | 60.6949 | 0.35248 | -0.050355 | 0.43945 | 0.036621 | 123.4726 | 123.4955 | 60.7819 | 123.4772 | 123.6374 | 123.4726 | 123.3627 | 123.3856 | -123.5596 | -123.3719 | 123.2208 | 123.3902 | 61.7935 | 61.3907
279.9844 | 123.5962 | -61.5509 | 61.734 | -0.050964 | -0.00019652 | -0.0013929 | 9.6222e-05 | -9.604e-05 | 0.00021157 | -0.0022346 | 0.014954 | -8.5416e-05 | 0.033259 | 0.026908 | -0.0017197 | -0.00099549 | -0.0012111 | 0.22888 | 61.8118 | -61.8256 | 61.6653 | 61.6745 | -61.7523 | 0.25177 | -0.21515 | 61.8256 | -61.647 | 61.8988 | -0.79651 | -61.5784 | -61.1526 | -0.27466 | 0.07782 | -0.068665 | 123.2254 | 61.8027 | -0.20142 | 62.0773 | 0.073243 | -0.096131 | 0.091553 | 0.16479 | 60.7544 | 0.39825 | -0.027466 | 0.49439 | 0.068665 | 123.5001 | 123.4909 | 60.8505 | 123.5458 | 123.6374 | 123.4726 | 123.3627 | 123.3765 | -123.5596 | -123.381 | 123.2162 | 123.4497 | 61.7798 | 61.3358
280.9844 | 123.468 | -61.5692 | 61.8118 | -0.005188 | 0.00087168 | 0.00052971 | -0.00097198 | 0.0018266 | -0.00042943 | -9.8356e-05 | -0.0094605 | 0.0018372 | 0.033259 | 0.041648 | -0.0027877 | -0.00014089 | -0.00078395 | 0.27008 | 61.8576 | -61.7981 | 61.647 | 61.6241 | -61.7889 | 0.24261 | -0.21515 | 61.8713 | -61.6425 | 61.7935 | -0.84686 | -61.6058 | -61.2305 | -0.22888 | 0.045776 | -0.1648 | 123.1934 | 61.8118 | -0.21973 | 62.0407 | 0.009156 | -0.073242 | 0.059509 | -0.018311 | 60.7224 | 0.33875 | -0.036621 | 0.41199 | 0.036621 | 123.4222 | 123.4451 | 60.7956 | 123.436 | 123.6557 | 123.5138 | 123.4268 | 123.4406 | -123.6099 | -123.4543 | 123.2162 | 123.3627 | 61.8393 | 61.3541
281.9844 | 123.5733 | -61.5189 | 61.7706 | -0.035705 | 0.00044428 | -0.0013929 | -0.0020402 | 0.00033116 | 0.0025614 | -0.0015936 | 0.0088501 | 0.0026916 | 0.034968 | 0.03054 | -0.00086514 | -0.00078189 | -0.0029201 | 0.29755 | 61.8347 | -61.7752 | 61.702 | 61.7157 | -61.6974 | 0.32044 | -0.11902 | 61.8073 | -61.6241 | 61.908 | -0.77362 | -61.5463 | -61.1572 | -0.25635 | 0.064087 | -0.068665 | 123.2346 | 61.8393 | -0.17853 | 62.0956 | 0.07782 | -0.10529 | 0.036621 | 0.13733 | 60.7452 | 0.36163 | -0.027466 | 0.46692 | 0.07782 | 123.4909 | 123.4772 | 60.8505 | 123.5321 | 123.6099 | 123.4314 | 123.3536 | 123.3261 | -123.5458 | -123.3948 | 123.2208 | 123.4268 | 61.8164 | 61.3998
282.9844 | 123.4726 | -61.5097 | 61.8073 | -0.005188 | -0.0027599 | 0.00010251 | -0.0011856 | 0.00054476 | 0.00021157 | 0.00011544 | 0.0027465 | 0.003119 | 0.032618 | 0.036521 | -1.0744e-05 | -0.00035469 | -0.00014315 | 0.29297 | 61.8622 | -61.8118 | 61.647 | 61.6562 | -61.7615 | 0.27924 | -0.21057 | 61.8576 | -61.6333 | 61.8347 | -0.87891 | -61.6425 | -61.2259 | -0.30212 | 0.054932 | -0.16022 | 123.1659 | 61.7889 | -0.25177 | 62.0911 | 0.050354 | -0.1236 | 0.050354 | 0.027466 | 60.6308 | 0.28381 | -0.13275 | 0.40741 | -0.009155 | 123.468 | 123.4589 | 60.7544 | 123.468 | 123.674 | 123.4909 | 123.3719 | 123.3673 | -123.6191 | -123.4406 | 123.1567 | 123.3444 | 61.8027 | 61.2991
283.9844 | 123.6328 | -61.5143 | 61.7706 | -0.012817 | -0.0012647 | 0.00010251 | -0.00054478 | -0.0020188 | 0.00063877 | -0.0035162 | 0.024109 | 0.00012818 | 0.033686 | 0.027549 | -0.0010787 | -0.0018499 | 0.0015659 | 0.24261 | 61.8393 | -61.7752 | 61.6791 | 61.7294 | -61.7249 | 0.30212 | -0.17853 | 61.8347 | -61.615 | 61.9354 | -0.76446 | -61.5097 | -61.1298 | -0.26093 | 0.068664 | -0.091553 | 123.2437 | 61.8164 | -0.21057 | 62.0773 | 0.050354 | -0.10071 | 0.064087 | 0.1648 | 60.7498 | 0.38452 | 0.004577 | 0.48523 | 0.10529 | 123.5046 | 123.4543 | 60.8505 | 123.5504 | 123.6145 | 123.4497 | 123.3536 | 123.349 | -123.5458 | -123.3856 | 123.1934 | 123.4497 | 61.7569 | 61.3358
284.9844 | 123.4634 | -61.5417 | 61.8118 | 0.063477 | -0.0019055 | -0.00011109 | -0.00054478 | -0.0037276 | -2.232e-06 | 0.00054264 | -0.04303 | -0.00029902 | 0.034541 | 0.034171 | 0.0014847 | -0.0012091 | 7.0452e-05 | 0.24261 | 61.8759 | -61.7935 | 61.6058 | 61.5601 | -61.7981 | 0.22888 | -0.27466 | 61.8668 | -61.6562 | 61.7981 | -0.9201 | -61.6791 | -61.2579 | -0.25177 | 0.064087 | -0.20599 | 123.1018 | 61.7706 | -0.25635 | 62.0224 | -0.004578 | -0.11444 | 0.054931 | -0.013733 | 60.6216 | 0.28381 | -0.13733 | 0.39825 | -0.022888 | 123.3536 | 123.3994 | 60.7361 | 123.4543 | 123.6694 | 123.5229 | 123.4177 | 123.4085 | -123.6053 | -123.468 | 123.1476 | 123.3398 | 61.7844 | 61.2671
285.9844 | 123.6191 | -61.5143 | 61.7798 | 0.0024415 | 0.0030079 | -0.0020337 | -0.00011758 | -0.0039414 | -0.00021583 | -0.00031196 | 0.0027465 | -0.00029902 | 0.033473 | 0.035239 | -0.00065154 | -0.00078189 | -0.0018521 | 0.25177 | 61.8301 | -61.8027 | 61.6699 | 61.6699 | -61.7294 | 0.28381 | -0.19226 | 61.8256 | -61.6104 | 61.9263 | -0.76446 | -61.5509 | -61.1343 | -0.28839 | 0.050354 | -0.10986 | 123.1842 | 61.7981 | -0.21515 | 62.0865 | 0.073242 | -0.096131 | 0.045777 | 0.14649 | 60.7498 | 0.37994 | -0.036621 | 0.47608 | 0.05951 | 123.4726 | 123.4726 | 60.8459 | 123.5367 | 123.6328 | 123.436 | 123.3444 | 123.3398 | -123.5825 | -123.3902 | 123.1842 | 123.4406 | 61.7661 | 61.322
286.9844 | 123.5092 | -61.5417 | 61.8073 | 0.010071 | 0.0010853 | -0.0013929 | -0.00054478 | 0.00011756 | 0.00021157 | -0.0015936 | -0.00030511 | -0.0015808 | 0.034968 | 0.037376 | -0.0010787 | -0.0012091 | -0.0012111 | 0.30212 | 61.8439 | -61.7844 | 61.702 | 61.6653 | -61.7249 | 0.31586 | -0.23804 | 61.8668 | -61.6241 | 61.8713 | -0.8194 | -61.615 | -61.1984 | -0.24262 | 0.036621 | -0.10529 | 123.2071 | 61.8576 | -0.18311 | 62.1002 | 0.059509 | -0.082398 | 0.059509 | 0.064087 | 60.7224 | 0.34332 | -0.073242 | 0.42572 | 0.009156 | 123.4497 | 123.4863 | 60.8047 | 123.4955 | 123.6282 | 123.4909 | 123.3856 | 123.4085 | -123.5916 | -123.4314 | 123.2437 | 123.4131 | 61.8439 | 61.3037
287.9844 | 123.5458 | -61.5143 | 61.7615 | 0.0177 | 0.00065788 | 0.00095711 | -0.00011758 | 0.0035354 | 0.0012796 | -0.00052556 | 0.018005 | 0.00055538 | 0.034968 | 0.028403 | 0.0010575 | -0.0022773 | -0.0029201 | 0.32959 | 61.8484 | -61.8027 | 61.6928 | 61.702 | -61.6928 | 0.32501 | -0.20142 | 61.8393 | -61.647 | 62.0224 | -1.1032 | -61.5646 | -61.1069 | -0.28839 | 0.086975 | -0.068665 | 123.2162 | 61.8393 | -0.17853 | 62.1277 | 0.10986 | -0.13275 | 0.077819 | 0.26093 | 60.4111 | 0.40741 | -0.050354 | 0.54016 | 0.082398 | 123.5046 | 123.4955 | 60.5438 | 123.6694 | 123.6511 | 123.4863 | 123.3627 | 123.3536 | -123.5641 | -123.4085 | 123.2071 | 123.5367 | 61.8439 | 61.3129
288.9844 | 123.4543 | -61.5509 | 61.8073 | 0.048218 | -0.00062372 | 0.00052971 | 9.6222e-05 | 0.00011756 | 0.00042517 | 0.00032904 | -0.018616 | -0.00072642 | 0.034113 | 0.029044 | 0.00063026 | -0.00056829 | 0.0015659 | 0.28839 | 61.8713 | -61.8164 | 61.6058 | 61.6058 | -61.7981 | 0.25635 | -0.31128 | 61.8851 | -61.6516 | 61.7981 | -0.89722 | -61.6882 | -61.2625 | -0.2655 | 0.064087 | -0.20142 | 123.1567 | 61.8073 | -0.24719 | 62.0728 | 0.01831 | -0.10071 | 0.07782 | -0.009155 | 60.6537 | 0.28839 | -0.13733 | 0.3891 | -0.036621 | 123.4222 | 123.4222 | 60.7544 | 123.4497 | 123.6877 | 123.5367 | 123.4222 | 123.436 | -123.6237 | -123.4589 | 123.1567 | 123.349 | 61.8393 | 61.2396
289.9844 | 123.5962 | -61.4777 | 61.8393 | 0.040589 | 0.0012989 | -0.00096549 | -0.00011758 | -0.002446 | -2.232e-06 | 0.0018242 | 0.0088501 | 0.00034178 | 0.033259 | 0.029044 | -0.0019333 | -0.00014089 | 0.0011387 | 0.3067 | 61.8439 | -61.7752 | 61.7157 | 61.734 | -61.6791 | 0.33417 | -0.24261 | 61.8301 | -61.6287 | 61.8988 | -0.80109 | -61.5417 | -61.1526 | -0.29755 | 0.004578 | -0.1236 | 123.2117 | 61.8118 | -0.20142 | 62.1094 | 0.096131 | -0.15106 | -0.009155 | 0.05951 | 60.6766 | 0.32501 | -0.064087 | 0.47607 | 0.086975 | 123.5092 | 123.4909 | 60.8276 | 123.5275 | 123.6191 | 123.4589 | 123.3215 | 123.3078 | -123.6145 | -123.468 | 123.1934 | 123.3765 | 61.7844 | 61.235
290.9844 | 123.4451 | -61.5692 | 61.821 | -0.012817 | 1.7082e-05 | -0.0018201 | 0.0015914 | 0.00075836 | -0.00021583 | -0.00138 | -0.052185 | 0.0020508 | 0.033686 | 0.034598 | -1.0744e-05 | -0.00035469 | -0.0014249 | 0.24719 | 61.9034 | -61.8393 | 61.5875 | 61.5601 | -61.8164 | 0.23804 | -0.36621 | 61.8988 | -61.647 | 61.8118 | -0.68207 | -61.8668 | -61.4182 | -0.27008 | 0.082397 | -0.23346 | 123.1293 | 61.8073 | -0.24719 | 62.0773 | 0.022888 | -0.07782 | 0.07782 | -0.009155 | 60.8871 | 0.15106 | -0.29755 | 0.22888 | -0.21973 | 123.3994 | 123.4268 | 60.965 | 123.4589 | 123.7427 | 123.5458 | 123.4726 | 123.468 | -123.6603 | -123.468 | 123.1567 | 123.381 | 61.8164 | 61.203
291.9844 | 123.587 | -61.5143 | 61.7661 | -0.020447 | -0.00083732 | -0.00032469 | 9.6222e-05 | -9.604e-05 | 0.00063877 | -0.002021 | 0.054626 | -0.00029902 | 0.034968 | 0.027335 | -0.0025741 | -0.00014089 | -0.0050565 | 0.32044 | 61.8439 | -61.7706 | 61.7203 | 61.7157 | -61.6928 | 0.33875 | -0.26093 | 61.821 | -61.6104 | 61.9125 | -0.77362 | -61.5326 | -61.1435 | -0.25635 | 0.07782 | -0.045776 | 123.23 | 61.853 | -0.17853 | 62.1094 | 0.07782 | -0.096131 | 0.054932 | 0.14648 | 60.7407 | 0.37079 | -0.018311 | 0.46692 | 0.07782 | 123.4863 | 123.4909 | 60.8368 | 123.523 | 123.6145 | 123.4314 | 123.3582 | 123.3353 | -123.5367 | -123.3765 | 123.2346 | 123.4268 | 61.8347 | 61.2534
292.9844 | 123.4543 | -61.5326 | 61.8118 | 0.0024415 | -0.00019652 | -0.00053829 | -0.00097198 | 0.00075836 | 0.0021342 | -0.003089 | 0.0057983 | 0.00055538 | 0.034754 | 0.033317 | -0.00065154 | -0.0020637 | -0.00099755 | 0.29755 | 61.8805 | -61.7935 | 61.647 | 61.6516 | -61.7661 | 0.3067 | -0.32959 | 61.8759 | -61.6562 | 61.821 | -0.88348 | -61.6516 | -61.2213 | -0.26093 | 0.068664 | -0.1648 | 123.1842 | 61.8393 | -0.23346 | 62.1002 | 0.027466 | -0.1236 | 0.064087 | 0.009155 | 60.6491 | 0.31128 | -0.11902 | 0.43488 | 0.004578 | 123.4451 | 123.4406 | 60.7727 | 123.4772 | 123.674 | 123.5321 | 123.4131 | 123.4085 | -123.6053 | -123.468 | 123.1796 | 123.3536 | 61.8301 | 61.203
293.9844 | 123.5779 | -61.5005 | 61.7844 | -0.028076 | 0.0010853 | 0.00031611 | -0.0028946 | 0.0018266 | -0.00021583 | -0.00095276 | 0.0057983 | 0.00034178 | 0.033259 | 0.035667 | -0.0010787 | -0.0014227 | 0.00028405 | 0.31586 | 61.8576 | -61.7981 | 61.5601 | 61.7523 | -61.8027 | 0.23804 | -0.33417 | 61.8073 | -61.6425 | 61.908 | -0.79651 | -61.5509 | -61.1252 | -0.29755 | 0.073242 | -0.2243 | 123.2529 | 61.7386 | -0.30212 | 62.0361 | -0.004577 | -0.14191 | 0.022888 | 0.1236 | 60.704 | 0.37537 | -0.050354 | 0.51727 | 0.091553 | 123.5504 | 123.3582 | 60.8459 | 123.5504 | 123.6557 | 123.4497 | 123.3582 | 123.3078 | -123.5825 | -123.4268 | 123.0606 | 123.4085 | 61.8164 | 61.1664
294.9844 | 123.4818 | -61.5646 | 61.8164 | 0.078736 | -0.00019652 | -0.00011109 | 9.6222e-05 | -0.004155 | -0.0014974 | -0.0026618 | -0.015564 | 0.00012818 | 0.034541 | 0.033103 | -0.00086514 | -0.0012091 | -0.0022793 | 0.2655 | 61.8988 | -61.8256 | 61.5784 | 61.5601 | -61.8164 | 0.26093 | -0.44861 | 61.8759 | -61.647 | 61.7935 | -0.90637 | -61.6837 | -61.2671 | -0.26093 | 0.082398 | -0.23804 | 123.1247 | 61.8256 | -0.25177 | 62.0865 | 0.009156 | -0.082398 | 0.05951 | -0.022888 | 60.6583 | 0.29755 | -0.11902 | 0.37994 | -0.036621 | 123.3856 | 123.4039 | 60.7407 | 123.4406 | 123.7244 | 123.5229 | 123.4634 | 123.4406 | -123.642 | -123.4634 | 123.143 | 123.3582 | 61.8301 | 61.116
295.9844 | 123.5916 | -61.5417 | 61.7844 | -0.043335 | 0.0019397 | -0.00075189 | 0.0011642 | -0.0022324 | 0.0017068 | -0.0050116 | 0.063782 | -0.00029902 | 0.0339 | 0.030753 | -0.0015059 | 0.00071351 | -0.0012111 | 0.31128 | 61.8164 | -61.7981 | 61.8164 | 61.9766 | -61.9675 | 0.16479 | -0.44403 | 61.8073 | -61.6333 | 61.8988 | -0.79651 | -61.5829 | -61.1801 | -0.25635 | 0.032043 | 0.032043 | 123.5184 | 61.7065 | -0.42572 | 61.9629 | -0.16937 | -0.091553 | 0.022888 | 0.11444 | 60.7452 | 0.36163 | -0.041199 | 0.45319 | 0.050354 | 123.7747 | 123.6145 | 60.8368 | 123.5321 | 123.6145 | 123.4406 | 123.3582 | 123.349 | -123.5825 | -123.4177 | 123.3582 | 123.4406 | 61.853 | 61.0977
296.9844 | 123.4634 | -61.5601 | 61.853 | 0.02533 | -0.00019652 | -0.0016065 | 0.0011642 | 0.0013992 | 0.00063877 | -9.8356e-05 | -0.039978 | 0.0022644 | 0.033473 | 0.033744 | 0.00041666 | -0.00078189 | 0.0026341 | 0.27924 | 61.8896 | -61.8301 | 61.5829 | 61.5555 | -61.821 | 0.25177 | -0.45319 | 61.8851 | -61.6379 | 61.7935 | -0.91095 | -61.6791 | -61.2671 | -0.27008 | 0.036621 | -0.27008 | 123.1155 | 61.8118 | -0.26093 | 62.0819 | 0.009155 | -0.077819 | 0.032044 | -0.059509 | 60.6491 | 0.29297 | -0.11902 | 0.37079 | -0.041199 | 123.3856 | 123.4131 | 60.7269 | 123.4314 | 123.7198 | 123.5229 | 123.4497 | 123.4451 | -123.6832 | -123.4909 | 123.143 | 123.3536 | 61.8393 | 61.1069
297.9844 | 123.5275 | -61.5417 | 61.7981 | 0.040589 | 0.00044428 | 0.00010251 | -0.0024674 | 0.0039628 | 0.00042517 | 0.00075624 | -0.00030511 | 0.0011964 | 0.032191 | 0.036735 | -1.0744e-05 | 0.0011407 | 0.0034885 | 0.31586 | 61.8439 | -61.7935 | 61.6653 | 61.647 | -61.734 | 0.31128 | -0.39368 | 61.8484 | -61.6196 | 61.8484 | -0.86975 | -61.6104 | -61.2167 | -0.25177 | 0.045776 | -0.13275 | 123.1888 | 61.853 | -0.19226 | 62.1048 | 0.059509 | -0.07782 | 0.050354 | 0.050354 | 60.672 | 0.32501 | -0.068665 | 0.40283 | 0.009155 | 123.4406 | 123.4589 | 60.7498 | 123.468 | 123.6374 | 123.468 | 123.3856 | 123.3902 | -123.5916 | -123.4177 | 123.2071 | 123.3902 | 61.8576 | 61.1481
298.9844 | 123.468 | -61.5692 | 61.821 | 0.055847 | -0.00041012 | -0.0011793 | 0.002446 | 0.00033116 | -0.0014974 | 0.00075624 | -0.070496 | 0.00034178 | 0.034113 | 0.035667 | 0.0014847 | 0.00092711 | -0.00078395 | 0.27008 | 61.9034 | -61.8301 | 61.5784 | 61.4822 | -61.821 | 0.25177 | -0.48065 | 61.908 | -61.6516 | 61.7935 | -0.90179 | -61.6699 | -61.2442 | -0.26093 | 0.082397 | -0.24262 | 123.0515 | 61.821 | -0.25177 | 62.0819 | 0.009155 | -0.082397 | 0.086975 | -0.027466 | 60.6674 | 0.32501 | -0.10071 | 0.40741 | -0.018311 | 123.3124 | 123.4085 | 60.7498 | 123.4451 | 123.7335 | 123.5596 | 123.4726 | 123.4772 | -123.6511 | -123.4726 | 123.1476 | 123.3627 | 61.8393 | 61.0886
299.9844 | 123.5916 | -61.5463 | 61.7889 | 0.0177 | 0.0019397 | -0.00096549 | 0.00052342 | -0.00052344 | -0.00085663 | 0.00011544 | 0.066833 | 0.0033326 | 0.034113 | 0.030753 | -0.00086514 | -0.00099549 | 0.0028477 | 0.3067 | 61.8301 | -61.8027 | 61.702 | 61.702 | -61.7111 | 0.5722 | -0.62256 | 61.8027 | -61.6196 | 61.8668 | -0.79193 | -61.5372 | -61.1435 | -0.25635 | 0.041199 | -0.086975 | 123.2483 | 62.1185 | -0.16479 | 62.3749 | 0.091552 | -0.073242 | 0.013733 | 0.07782 | 60.7544 | 0.40283 | 0.009156 | 0.47607 | 0.082398 | 123.5046 | 123.5046 | 60.8276 | 123.4863 | 123.6328 | 123.4222 | 123.3765 | 123.349 | -123.5916 | -123.4085 | 123.2483 | 123.4131 | 61.853 | 60.9238
300.9844 | 123.4818 | -61.5555 | 61.821 | 0.02533 | -0.0023327 | -0.00053829 | 0.0011642 | -0.00030984 | -0.00042943 | -0.003089 | -0.049133 | 0.0018372 | 0.034541 | 0.038016 | -0.00022434 | 0.0013543 | 0.0013523 | 0.26093 | 61.8988 | -61.8301 | 61.6241 | 61.4914 | -61.8759 | 0.24261 | -0.51727 | 61.8759 | -61.6653 | 61.7981 | -0.90637 | -61.6745 | -61.2579 | -0.27466 | 0.07782 | -0.19684 | 123.0469 | 61.7981 | -0.32043 | 62.0728 | -0.045777 | -0.10986 | 0.054932 | -0.022888 | 60.6491 | 0.29755 | -0.11902 | 0.40741 | -0.009156 | 123.3215 | 123.4543 | 60.759 | 123.4634 | 123.7289 | 123.5413 | 123.4543 | 123.4314 | -123.6511 | -123.4863 | 123.1796 | 123.3536 | 61.8164 | 61.0382
301.9844 | 123.5092 | -61.5372 | 61.7981 | 0.032959 | 0.00044428 | -0.00011109 | 0.00052342 | 0.00097196 | -0.00021583 | -0.00052556 | 0.027161 | -0.0011536 | 0.0339 | 0.030326 | 0.00084386 | -0.0012091 | 0.00049765 | 0.32044 | 61.8484 | -61.7981 | 61.6562 | 61.6791 | -61.7294 | 0.32044 | -0.47607 | 61.8484 | -61.6333 | 61.8439 | -0.86517 | -61.6104 | -61.2076 | -0.26093 | 0.050354 | -0.14191 | 123.2162 | 61.8576 | -0.19226 | 62.1185 | 0.068665 | -0.096131 | 0.050354 | 0.045776 | 60.672 | 0.32959 | -0.073243 | 0.42572 | 0.022888 | 123.4772 | 123.4543 | 60.7681 | 123.4772 | 123.6465 | 123.4818 | 123.3856 | 123.3856 | -123.5962 | -123.4314 | 123.1934 | 123.381 | 61.8576 | 61.0611
302.9844 | 123.4863 | -61.5784 | 61.8393 | 0.040589 | -0.00019652 | 0.00095711 | 0.0015914 | 0.0011856 | -0.0014974 | -0.00031196 | -0.055237 | 0.0016236 | 0.034541 | 0.03823 | -0.0010787 | -0.0012091 | 0.0026341 | 0.25635 | 61.8942 | -61.8118 | 61.5509 | 61.4868 | -61.821 | 0.23346 | -0.54474 | 61.8759 | -61.6653 | 61.8118 | -0.90637 | -61.6745 | -61.2396 | -0.23346 | 0.054932 | -0.28839 | 123.0652 | 61.8118 | -0.24262 | 62.0453 | -0.009155 | -0.086975 | 0.036622 | -0.027465 | 60.672 | 0.33875 | -0.096131 | 0.42572 | -0.009156 | 123.2986 | 123.3627 | 60.759 | 123.4772 | 123.7061 | 123.5413 | 123.4726 | 123.4543 | -123.6511 | -123.5046 | 123.1293 | 123.3902 | 61.8347 | 61.0336
303.9844 | 123.4955 | -61.5372 | 61.7935 | 0.010071 | 0.0030079 | 0.00031611 | 0.00095062 | 0.0028946 | -0.001711 | -9.8356e-05 | 0.014954 | -8.5416e-05 | 0.032191 | 0.032035 | 0.00020286 | -0.0022773 | -0.0024929 | 0.32501 | 61.853 | -61.7981 | 61.647 | 61.6562 | -61.7432 | 0.33875 | -0.5127 | 61.8668 | -61.6196 | 61.8393 | -0.89264 | -61.6241 | -61.2259 | -0.26093 | 0.059509 | -0.14648 | 123.1934 | 61.8759 | -0.20599 | 62.1368 | 0.054932 | -0.082398 | 0.073242 | 0.045776 | 60.6445 | 0.31128 | -0.086976 | 0.39368 | -0.004578 | 123.4543 | 123.4451 | 60.7269 | 123.4589 | 123.6511 | 123.4863 | 123.3902 | 123.4039 | -123.5916 | -123.4131 | 123.1842 | 123.3765 | 61.8622 | 61.0245
304.9844 | 123.5184 | -61.5463 | 61.8073 | 0.02533 | 0.0019397 | 0.0022387 | -0.00097198 | 0.00054476 | -0.001711 | 0.00011544 | -0.039978 | 0.002478 | 0.035182 | 0.037803 | -0.00022434 | 0.00049991 | -0.0014249 | 0.28381 | 61.9125 | -61.8439 | 61.6196 | 61.5738 | -61.7889 | 0.26093 | -0.5722 | 61.8759 | -61.6287 | 61.8484 | -0.88348 | -61.6425 | -61.2259 | -0.29755 | 0.10529 | -0.18768 | 123.1201 | 61.8073 | -0.24261 | 62.1048 | 0.054932 | -0.082397 | 0.068665 | 0.041199 | 60.6628 | 0.32044 | -0.09613 | 0.40283 | -0.013733 | 123.4177 | 123.4634 | 60.7452 | 123.4772 | 123.7564 | 123.5046 | 123.4589 | 123.4222 | -123.6511 | -123.436 | 123.1659 | 123.3948 | 61.8301 | 60.9741
305.9844 | 123.5138 | -61.5417 | 61.8301 | -0.028076 | -0.00019652 | -0.00011109 | 9.6222e-05 | -0.0013778 | -0.0012838 | 0.00075624 | 0.014954 | 0.00012818 | 0.034327 | 0.033103 | 0.00020286 | -0.0018499 | -0.00078395 | 0.31586 | 61.8439 | -61.8027 | 61.6516 | 61.6516 | -61.734 | 0.31586 | -0.55389 | 61.8439 | -61.6379 | 61.8118 | -0.86975 | -61.6425 | -61.2122 | -0.26093 | 0.013733 | -0.17853 | 123.1934 | 61.8576 | -0.19226 | 62.1185 | 0.068664 | -0.09613 | 0.013733 | -0.01831 | 60.672 | 0.32959 | -0.10071 | 0.42572 | -0.004578 | 123.4543 | 123.4543 | 60.7681 | 123.4497 | 123.6465 | 123.4818 | 123.3856 | 123.3856 | -123.6328 | -123.468 | 123.1934 | 123.3536 | 61.8576 | 60.9879
306.9844 | 123.5092 | -61.5738 | 61.8256 | -0.028076 | 0.0012989 | -0.00011109 | -0.00033118 | 0.00054476 | -0.002352 | 0.00075624 | -0.036926 | 0.00055538 | 0.032618 | 0.031821 | -0.0012923 | 0.00028631 | 0.0019931 | 0.30212 | 61.8805 | -61.8484 | 61.5921 | 61.5555 | -61.821 | 0.2655 | -0.65002 | 61.8713 | -61.647 | 61.7935 | -0.91095 | -61.6791 | -61.2442 | -0.27466 | 0.054931 | -0.23346 | 123.1293 | 61.8393 | -0.24719 | 62.114 | 0.027466 | -0.073242 | 0.045776 | -0.032044 | 60.6628 | 0.32959 | -0.10529 | 0.40283 | -0.032043 | 123.4039 | 123.4406 | 60.7361 | 123.4406 | 123.7289 | 123.5184 | 123.4543 | 123.4451 | -123.674 | -123.4726 | 123.1659 | 123.3673 | 61.8759 | 60.9238
307.9844 | 123.468 | -61.5555 | 61.8347 | 0.0177 | 1.7082e-05 | -0.00096549 | 0.00095062 | -9.604e-05 | -0.0014974 | -0.0043708 | 0.0088501 | 0.0020508 | 0.032832 | 0.036948 | -0.0012923 | 0.00028631 | 0.0043431 | 0.25635 | 61.8942 | -61.8118 | 61.5738 | 61.5601 | -61.8073 | 0.27008 | -0.67291 | 61.9034 | -61.6653 | 61.7844 | -0.91553 | -61.6837 | -61.2579 | -0.25635 | 0.059509 | -0.26093 | 123.1155 | 61.8256 | -0.25177 | 62.0819 | 0.004578 | -0.10986 | 0.068664 | -0.050354 | 60.64 | 0.29755 | -0.12817 | 0.40741 | -0.018311 | 123.3719 | 123.3856 | 60.7498 | 123.4497 | 123.7061 | 123.5687 | 123.4497 | 123.4589 | -123.6465 | -123.5001 | 123.1293 | 123.3398 | 61.8118 | 60.8826
308.9844 | 123.5275 | -61.5463 | 61.7981 | 0.063477 | -0.0010511 | 0.00010251 | 0.0033004 | 0.0028946 | -0.00021583 | 0.00011544 | -0.04303 | 0.0016236 | 0.033686 | 0.036735 | -0.00086514 | 0.0032769 | 0.00049765 | 0.29755 | 61.8668 | -61.8164 | 61.6196 | 61.5967 | -61.8027 | 0.26093 | -0.63171 | 61.853 | -61.6379 | 61.8301 | -0.89264 | -61.6516 | -61.2076 | -0.27008 | 0.068664 | -0.17853 | 123.143 | 61.8073 | -0.25635 | 62.0773 | 0.013733 | -0.091552 | 0.054931 | 0.032043 | 60.6537 | 0.33875 | -0.10529 | 0.4303 | -0.013733 | 123.4131 | 123.436 | 60.7452 | 123.468 | 123.6832 | 123.4909 | 123.4131 | 123.3994 | -123.6145 | -123.436 | 123.1659 | 123.3765 | 61.8439 | 60.9146
309.9844 | 123.4497 | -61.5692 | 61.8393 | 0.0024415 | 0.00023068 | -0.0028881 | 0.0011642 | 0.00033116 | 0.001066 | -0.0028754 | -0.0033569 | 0.0020508 | 0.033473 | 0.026053 | 0.00041666 | 7.2706e-05 | -0.00014315 | 0.25177 | 61.8805 | -61.8347 | 61.5692 | 61.5509 | -61.8347 | 0.26093 | -0.70953 | 61.8622 | -61.615 | 61.7432 | -0.6134 | -61.734 | -61.3861 | -0.2655 | 0.041199 | -0.27008 | 123.1201 | 61.8301 | -0.2655 | 62.0956 | 0 | -0.045776 | 0.022889 | -0.09613 | 60.9558 | 0.18311 | -0.16479 | 0.22888 | -0.11902 | 123.3856 | 123.4039 | 61.0016 | 123.3582 | 123.7152 | 123.4772 | 123.4497 | 123.4314 | -123.674 | -123.4543 | 123.1384 | 123.3124 | 61.821 | 60.8597
310.9844 | 123.5184 | -61.5509 | 61.8073 | 0.0024415 | 0.0019397 | 0.00052971 | 0.0026596 | 0.0018266 | 0.0023478 | 0.00032904 | -0.027771 | 0.00141 | 0.037104 | 0.034598 | -0.00022434 | 0.0022089 | -0.00078395 | 0.27924 | 61.8942 | -61.8393 | 61.615 | 61.5967 | -61.7981 | 0.25635 | -0.67291 | 61.8668 | -61.6379 | 61.8301 | -0.90179 | -61.6653 | -61.2213 | -0.28839 | 0.086975 | -0.19226 | 123.1476 | 61.8073 | -0.24719 | 62.0956 | 0.041198 | -0.086975 | 0.059509 | 0.022888 | 60.6491 | 0.32959 | -0.11444 | 0.41656 | -0.027466 | 123.436 | 123.4543 | 60.7361 | 123.468 | 123.7335 | 123.5046 | 123.4451 | 123.4177 | -123.6465 | -123.4451 | 123.1659 | 123.381 | 61.8301 | 60.878
311.9844 | 123.5092 | -61.5417 | 61.8118 | 0.032959 | -0.00062372 | -0.00032469 | 0.0013778 | -0.0037276 | 0.0017068 | -0.0022346 | -0.036926 | 0.00141 | 0.034968 | 0.034598 | -0.00086514 | -0.00035469 | 0.0015659 | 0.27466 | 61.8988 | -61.8164 | 61.5738 | 61.5463 | -61.8073 | 0.25177 | -0.77362 | 61.8622 | -61.6425 | 61.8164 | -0.89722 | -61.6608 | -61.2167 | -0.27466 | 0.086975 | -0.23804 | 123.0881 | 61.7935 | -0.2655 | 62.0682 | 0.009155 | -0.10071 | 0.050354 | 0.004577 | 60.6445 | 0.32501 | -0.11902 | 0.42572 | -0.018311 | 123.3627 | 123.3902 | 60.7452 | 123.4589 | 123.7152 | 123.5046 | 123.4406 | 123.4039 | -123.6282 | -123.4543 | 123.1155 | 123.3582 | 61.8164 | 60.7681
312.9844 | 123.5367 | -61.5738 | 61.7935 | 0.032959 | -0.0010511 | 0.00031611 | -0.0013992 | -0.00030984 | -2.232e-06 | -0.00095276 | -0.015564 | 0.00076898 | 0.03625 | 0.035239 | -0.0017197 | -0.0024909 | -0.0020657 | 0.27924 | 61.8805 | -61.8164 | 61.6104 | 61.6058 | -61.7752 | 0.27008 | -0.70496 | 61.8576 | -61.6241 | 61.8347 | -0.88806 | -61.6699 | -61.2167 | -0.24261 | 0.086975 | -0.1831 | 123.1796 | 61.8439 | -0.20142 | 62.0865 | 0.041198 | -0.050354 | 0.064087 | 0.041199 | 60.6857 | 0.35706 | -0.09613 | 0.40741 | -0.045776 | 123.4222 | 123.4268 | 60.7361 | 123.4589 | 123.6969 | 123.4818 | 123.4543 | 123.4314 | -123.6099 | -123.4177 | 123.1842 | 123.4085 | 61.853 | 60.8688
313.9844 | 123.4863 | -61.5646 | 61.7935 | 0.055847 | -0.00041012 | -0.0016065 | -0.0013992 | -0.00052344 | -0.0014974 | 0.0018242 | 0.0088501 | 0.00098258 | 0.033473 | 0.027762 | 0.0021255 | -0.0014227 | -0.0018521 | 0.23804 | 61.8988 | -61.8027 | 61.5692 | 61.5463 | -61.8256 | 0.25635 | -0.79193 | 61.8851 | -61.6425 | 61.9446 | -1.0071 | -61.8484 | -61.2808 | -0.23804 | 0.10529 | -0.2243 | 123.111 | 61.821 | -0.26093 | 62.059 | -0.022889 | -0.07782 | 0.091553 | 0.15106 | 60.5576 | 0.28381 | -0.28381 | 0.36163 | -0.20599 | 123.349 | 123.3719 | 60.6354 | 123.587 | 123.7015 | 123.5275 | 123.4634 | 123.4497 | -123.5962 | -123.436 | 123.1338 | 123.5092 | 61.8027 | 60.7727
314.9844 | 123.5092 | -61.5509 | 61.821 | 0.071106 | 0.0023669 | 0.0022387 | 9.6222e-05 | -0.0020188 | 0.002775 | 0.001397 | -0.039978 | 0.00098258 | 0.033045 | 0.034171 | -0.0017197 | 0.0015679 | 0.0030613 | 0.27008 | 61.8622 | -61.8439 | 61.6013 | 61.5967 | -61.8027 | 0.23346 | -0.90637 | 61.8439 | -61.6653 | 61.821 | -0.91095 | -61.6699 | -61.2122 | -0.29297 | 0.041199 | -0.21973 | 123.1476 | 61.7844 | -0.25177 | 62.0773 | 0.041199 | -0.11444 | 0.022888 | 0 | 60.64 | 0.33874 | -0.11902 | 0.45319 | -0.004578 | 123.4406 | 123.4451 | 60.7544 | 123.4863 | 123.7061 | 123.5092 | 123.4131 | 123.3948 | -123.6649 | -123.4863 | 123.1522 | 123.3719 | 61.821 | 60.6445
315.9844 | 123.5001 | -61.5555 | 61.8118 | 0.032959 | 0.0010853 | 0.00031611 | 0.00073702 | 0.00033116 | -0.0021384 | 0.00075624 | -0.0064087 | -0.00029902 | 0.033473 | 0.037162 | 0.00020286 | -0.0018499 | -0.0012111 | 0.22888 | 61.908 | -61.8256 | 61.5784 | 61.5417 | -61.821 | 0.25177 | -0.85144 | 61.8484 | -61.6425 | 61.8027 | -0.91095 | -61.6653 | -61.235 | -0.27008 | 0.09613 | -0.23346 | 123.0972 | 61.8073 | -0.2655 | 62.0773 | 0.004578 | -0.086975 | 0.036621 | -0.009156 | 60.6445 | 0.32044 | -0.10986 | 0.40741 | -0.022888 | 123.3673 | 123.4039 | 60.7315 | 123.4451 | 123.7335 | 123.4909 | 123.4634 | 123.4039 | -123.6374 | -123.4543 | 123.1338 | 123.3582 | 61.7844 | 60.704
316.9844 | 123.4726 | -61.5921 | 61.7981 | 0.0024415 | 0.0010853 | 0.0013843 | 9.6222e-05 | 0.00097196 | -2.232e-06 | -0.0028754 | -0.036926 | 0.002478 | 0.034754 | 0.032249 | -0.00022434 | -0.00056829 | -0.0029201 | 0.25177 | 61.8622 | -61.8439 | 61.5738 | 61.5555 | -61.853 | 0.18768 | -0.92468 | 61.853 | -61.6608 | 61.7844 | -0.94757 | -61.7157 | -61.2488 | -0.25177 | 0.064087 | -0.2243 | 123.1476 | 61.7798 | -0.26093 | 62.0316 | -0.009155 | -0.068665 | 0.054931 | -0.013733 | 60.6445 | 0.34332 | -0.1236 | 0.41199 | -0.054931 | 123.3994 | 123.4177 | 60.7132 | 123.4451 | 123.7061 | 123.5138 | 123.4543 | 123.4451 | -123.642 | -123.4589 | 123.1659 | 123.3765 | 61.8439 | 60.6674
317.9844 | 123.5184 | -61.5509 | 61.8256 | -0.19592 | 0.00023068 | -0.00011109 | -0.00033118 | -0.00030984 | -0.00021583 | 0.00075624 | -0.0033569 | 0.0022644 | 0.036036 | 0.03054 | 0.00041666 | -0.00014089 | 0.0022067 | 0.23804 | 61.8851 | -61.8347 | 61.5829 | 61.5509 | -61.8118 | 0.25635 | -0.88806 | 61.8713 | -61.647 | 61.8073 | -0.91095 | -61.6791 | -61.235 | -0.28381 | 0.059509 | -0.24262 | 123.1018 | 61.8073 | -0.26093 | 62.0911 | 0.022888 | -0.096131 | 0.045776 | -0.018311 | 60.64 | 0.31586 | -0.12817 | 0.41199 | -0.032043 | 123.3856 | 123.4177 | 60.7361 | 123.4543 | 123.7198 | 123.5184 | 123.436 | 123.4222 | -123.6603 | -123.4726 | 123.1338 | 123.3582 | 61.7889 | 60.6628
318.9844 | 123.4818 | -61.5646 | 61.8164 | -0.012817 | 0.00065788 | 0.0011707 | 0.0020188 | -0.00052344 | 0.00021157 | -0.0022346 | -0.030823 | 0.0020508 | 0.034968 | 0.032462 | 0.00063026 | 0.00092711 | 0.0026341 | 0.24261 | 61.8484 | -61.8347 | 61.5875 | 61.5738 | -61.8164 | 0.20599 | -0.92926 | 61.8622 | -61.6653 | 61.7798 | -0.93384 | -61.7249 | -61.2534 | -0.27008 | 0.032044 | -0.22888 | 123.1384 | 61.7706 | -0.25177 | 62.0407 | 0.018311 | -0.10071 | 0.045777 | -0.036621 | 60.6308 | 0.31128 | -0.16022 | 0.41199 | -0.05951 | 123.4085 | 123.4222 | 60.7315 | 123.4451 | 123.6832 | 123.5275 | 123.4131 | 123.4268 | -123.6511 | -123.4818 | 123.1522 | 123.3444 | 61.8073 | 60.6354
319.9844 | 123.5138 | -61.5509 | 61.8301 | 0.032959 | -0.00041012 | -0.00032469 | 0.0011642 | 0.0011856 | -0.0014974 | -0.00073916 | -0.00030511 | 0.0018372 | 0.0339 | 0.030753 | -0.0017197 | -0.00014089 | -0.0012111 | 0.23346 | 61.8851 | -61.8164 | 61.5646 | 61.4868 | -61.8439 | 0.24261 | -0.90637 | 61.8759 | -61.6516 | 61.7706 | -0.9201 | -61.6608 | -61.2259 | -0.2655 | 0.054932 | -0.2655 | 123.0377 | 61.7935 | -0.29297 | 62.059 | -0.027466 | -0.10071 | 0.045777 | -0.059509 | 60.6308 | 0.32501 | -0.10986 | 0.42572 | -0.009156 | 123.3032 | 123.381 | 60.7315 | 123.4222 | 123.7015 | 123.5275 | 123.436 | 123.4268 | -123.6465 | -123.4818 | 123.1155 | 123.3215 | 61.7844 | 60.6445
320.9844 | 123.5138 | -61.5509 | 61.8118 | 0.055847 | 0.00065788 | 0.00074331 | 0.00052342 | 0.002681 | -0.00042943 | -0.0033026 | -0.015564 | 0.00034178 | 0.033686 | 0.03353 | -0.00022434 | 0.00092711 | -0.0020657 | 0.27008 | 61.8622 | -61.821 | 61.5967 | 61.5784 | -61.8073 | 0.23346 | -0.89264 | 61.8484 | -61.6196 | 61.8256 | -0.90637 | -61.6562 | -61.2213 | -0.27008 | 0.050354 | -0.21515 | 123.1293 | 61.7844 | -0.25635 | 62.0544 | 0.013733 | -0.068665 | 0.036621 | 0.013733 | 60.6445 | 0.32959 | -0.10529 | 0.39825 | -0.036621 | 123.3994 | 123.4177 | 60.7132 | 123.4451 | 123.6832 | 123.468 | 123.4131 | 123.3994 | -123.6328 | -123.4314 | 123.1476 | 123.3765 | 61.821 | 60.6583
321.9844 | 123.5138 | -61.5372 | 61.8347 | -0.005188 | 1.7082e-05 | -0.00032469 | 0.0011642 | 0.00011756 | 0.0012796 | 0.0022516 | 0.011902 | 0.0022644 | 0.034113 | 0.030753 | -0.00065154 | -0.00035469 | -0.00078395 | 0.24261 | 61.8851 | -61.8118 | 61.5784 | 61.5646 | -61.8027 | 0.25635 | -0.95673 | 61.8668 | -61.6379 | 61.8118 | -0.88806 | -61.6699 | -61.1984 | -0.27466 | 0.050354 | -0.25635 | 123.1018 | 61.7935 | -0.2655 | 62.0682 | 0.009156 | -0.10071 | 0.032043 | -0.022888 | 60.6491 | 0.33875 | -0.13275 | 0.43945 | -0.032044 | 123.3765 | 123.3902 | 60.7498 | 123.4497 | 123.6969 | 123.5046 | 123.4222 | 123.4039 | -123.6465 | -123.4726 | 123.1155 | 123.349 | 61.7798 | 60.5804
322.9844 | 123.5092 | -61.5601 | 61.7935 | -0.020447 | 0.00044428 | -0.00053829 | 0.0015914 | -0.0022324 | 0.0019204 | -0.0026618 | -0.015564 | 0.00034178 | 0.033473 | 0.036094 | 0.0010575 | 0.00092711 | 7.0452e-05 | 0.24719 | 61.8713 | -61.8484 | 61.5921 | 61.5921 | -61.8164 | 0.20599 | -0.97961 | 61.8576 | -61.6516 | 61.8118 | -0.93842 | -61.6974 | -61.2305 | -0.28839 | 0.07782 | -0.20142 | 123.1522 | 61.7661 | -0.25635 | 62.0544 | 0.032044 | -0.091552 | 0.064087 | 0.018311 | 60.6216 | 0.32959 | -0.13733 | 0.42114 | -0.045777 | 123.4406 | 123.4406 | 60.7132 | 123.4634 | 123.7198 | 123.5092 | 123.4314 | 123.4177 | -123.642 | -123.4451 | 123.1522 | 123.3719 | 61.8073 | 60.5804
323.9844 | 123.5138 | -61.5509 | 61.8347 | 0.055847 | -0.00062372 | -0.00053829 | -0.00011758 | -0.00030984 | -0.0012838 | 0.0016106 | -0.00030511 | 0.00055538 | 0.035609 | 0.030326 | -0.0021469 | -0.00078189 | 7.0452e-05 | 0.23346 | 61.908 | -61.8164 | 61.5829 | 61.528 | -61.8118 | 0.25177 | -1.0117 | 61.8896 | -61.647 | 61.7981 | -0.89722 | -61.6653 | -61.1984 | -0.2655 | 0.073242 | -0.25177 | 123.0789 | 61.8027 | -0.26093 | 62.0682 | 0.004577 | -0.096131 | 0.054931 | -0.036621 | 60.6537 | 0.35248 | -0.11444 | 0.44861 | -0.01831 | 123.3444 | 123.3994 | 60.7498 | 123.4451 | 123.7244 | 123.5367 | 123.4589 | 123.4406 | -123.6511 | -123.4818 | 123.1338 | 123.349 | 61.7844 | 60.5392
324.9844 | 123.4863 | -61.5509 | 61.7981 | 0.0177 | 0.00044428 | 0.00095711 | 0.00030982 | 0.00097196 | 0.0021342 | -0.00138 | -0.030823 | 0.0029052 | 0.033045 | 0.029258 | -0.00065154 | 0.00028631 | 0.0034885 | 0.23346 | 61.8622 | -61.8164 | 61.5921 | 61.5829 | -61.821 | 0.13275 | -1.0345 | 61.8713 | -61.647 | 61.8118 | -0.91553 | -61.6837 | -61.2213 | -0.2655 | 0.064087 | -0.20599 | 123.1338 | 61.6837 | -0.27008 | 61.9492 | -0.004578 | -0.096131 | 0.073242 | 0.013733 | 60.6354 | 0.32959 | -0.13275 | 0.42572 | -0.036621 | 123.3994 | 123.4085 | 60.7315 | 123.4589 | 123.6786 | 123.5184 | 123.4131 | 123.4222 | -123.6145 | -123.4451 | 123.143 | 123.3627 | 61.7844 | 60.5164
325.9844 | 123.5001 | -61.5601 | 61.821 | 0.063477 | 0.0019397 | 0.00010251 | 9.6222e-05 | -0.001805 | -0.0021384 | 0.0011834 | -0.0064087 | 0.00012818 | 0.035609 | 0.030112 | -0.0012923 | 0.00071351 | 0.0013523 | 0.25177 | 61.8942 | -61.8118 | 61.6104 | 61.5829 | -61.7889 | 0.26093 | -0.97961 | 61.8668 | -61.6333 | 61.821 | -0.88348 | -61.6608 | -61.2213 | -0.25177 | 0.073242 | -0.21057 | 123.143 | 61.821 | -0.22888 | 62.0728 | 0.022889 | -0.073242 | 0.045776 | 0 | 60.6766 | 0.33875 | -0.10071 | 0.41199 | -0.027466 | 123.3948 | 123.4222 | 60.7498 | 123.4543 | 123.7061 | 123.5001 | 123.4543 | 123.4268 | -123.6328 | -123.4543 | 123.1705 | 123.381 | 61.8118 | 60.5804
326.9844 | 123.4863 | -61.5555 | 61.8027 | 0.0177 | 0.0015125 | -0.00032469 | 0.0020188 | 0.0013992 | 0.0021342 | -0.00052556 | 0.0027465 | 0.00076898 | 0.033259 | 0.039298 | -0.0012923 | 7.2706e-05 | -0.0012111 | 0.23346 | 61.8988 | -61.8256 | 61.5921 | 61.5967 | -61.8027 | 0.23346 | -1.0483 | 61.8668 | -61.6287 | 61.7798 | -0.99335 | -61.6333 | -61.1984 | -0.27008 | 0.096131 | -0.21057 | 123.1522 | 61.7889 | -0.24719 | 62.059 | 0.022889 | -0.073242 | 0.064087 | -0.022888 | 60.5621 | 0.35706 | -0.07782 | 0.4303 | -0.004578 | 123.4222 | 123.4177 | 60.6354 | 123.4085 | 123.7244 | 123.4955 | 123.4543 | 123.4222 | -123.6282 | -123.4314 | 123.1476 | 123.3353 | 61.7889 | 60.5072
327.9844 | 123.5229 | -61.5829 | 61.8118 | -0.035705 | -0.0021191 | 0.00074331 | -0.00033118 | -0.001805 | -0.00085663 | -0.00031196 | 0.014954 | 0.00076898 | 0.0339 | 0.036735 | 0.00041666 | -0.0024909 | -0.0022793 | 0.15106 | 61.9125 | -61.7432 | 61.5234 | 61.5097 | -61.7981 | 0.24261 | -1.1032 | 61.8851 | -61.647 | 61.7844 | -0.92468 | -61.6608 | -61.235 | -0.16022 | 0.10071 | -0.28839 | 123.0927 | 61.8256 | -0.21515 | 61.9858 | -0.054932 | -0.064087 | 0.073242 | -0.027466 | 60.6583 | 0.3479 | -0.07782 | 0.41199 | -0.013733 | 123.2529 | 123.2666 | 60.7224 | 123.4314 | 123.6557 | 123.5321 | 123.4955 | 123.468 | -123.555 | -123.4589 | 123.1064 | 123.3673 | 61.734 | 60.4797
329 | 123.5596 | -61.5646 | 61.7569 | -0.012817 | -0.00083732 | -0.0018201 | -0.0020402 | 0.0024674 | -0.00021583 | -0.0039436 | 0.069885 | 0.00055538 | 0.036891 | 0.033103 | 0.00020286 | -0.0016363 | 0.00092505 | 0.18768 | 61.8347 | -61.8027 | 61.615 | 61.5875 | -61.7661 | 0.26093 | -1.2268 | 61.7935 | -61.6287 | 61.8118 | -0.87891 | -61.6241 | -61.1755 | -0.23804 | 0.07782 | -0.14191 | 123.1522 | 61.8256 | -0.20142 | 62.0636 | 0.036621 | -0.064087 | 0.036621 | 0.054932 | 60.6857 | 0.3891 | -0.05951 | 0.45319 | 0.004577 | 123.3902 | 123.4177 | 60.7498 | 123.4406 | 123.6374 | 123.4222 | 123.3994 | 123.3582 | -123.5596 | -123.3856 | 123.1796 | 123.3765 | 61.7523 | 60.3378
329.9844 | 123.5001 | -61.5234 | 61.821 | 0.02533 | 0.0010853 | -0.00032469 | 0.004155 | -0.00073704 | -0.00342 | -9.8356e-05 | 0.0057983 | 0.0033326 | 0.037318 | 0.033317 | -0.0012923 | -0.00056829 | -0.0014249 | 0.20599 | 61.8988 | -61.8118 | 61.6013 | 61.5509 | -61.8118 | 0.24719 | -1.1398 | 61.8942 | -61.647 | 61.8301 | -0.90179 | -61.6745 | -61.1984 | -0.28839 | 0.07782 | -0.21973 | 123.0743 | 61.7706 | -0.28839 | 62.059 | 0 | -0.1236 | 0.073242 | 0.009155 | 60.6216 | 0.32501 | -0.15106 | 0.44861 | -0.027466 | 123.3627 | 123.4131 | 60.7452 | 123.4772 | 123.7106 | 123.5413 | 123.4222 | 123.4177 | -123.6328 | -123.468 | 123.1247 | 123.3536 | 61.7294 | 60.3836
330.9844 | 123.4863 | -61.5463 | 61.8073 | -0.035705 | 0.0017261 | 0.0011707 | 0.0020188 | -0.00095064 | -0.0014974 | 0.00054264 | -0.039978 | 0.0016236 | 0.033473 | 0.034171 | -0.0023605 | 0.00028631 | -0.0014249 | 0.21515 | 61.8622 | -61.8393 | 61.6013 | 61.5829 | -61.8027 | 0.21057 | -1.2268 | 61.8301 | -61.6699 | 61.8164 | -0.91095 | -61.6608 | -61.2122 | -0.29297 | 0.054932 | -0.20599 | 123.1293 | 61.7569 | -0.25635 | 62.0499 | 0.036621 | -0.1236 | 0.022888 | 0.009155 | 60.6354 | 0.33417 | -0.11444 | 0.45776 | 0.009155 | 123.4222 | 123.4406 | 60.759 | 123.4863 | 123.7015 | 123.5001 | 123.4085 | 123.3765 | -123.6465 | -123.4772 | 123.1476 | 123.3627 | 61.7615 | 60.3195
331.9844 | 123.4634 | -61.5372 | 61.8256 | 0.078736 | 0.00087168 | 0.00010251 | -0.00011758 | 0.0024674 | 0.00042517 | -0.00052556 | 0.011902 | 0.00012818 | 0.035395 | 0.032676 | -0.0017197 | 0.0011407 | 0.00071145 | 0.16022 | 61.9171 | -61.8256 | 61.5738 | 61.5509 | -61.8164 | 0.23346 | -1.1627 | 61.8713 | -61.6425 | 61.7935 | -0.91553 | -61.6745 | -61.2396 | -0.28839 | 0.091552 | -0.25177 | 123.0881 | 61.7706 | -0.27924 | 62.059 | 0.009156 | -0.10529 | 0.045776 | -0.032044 | 60.6216 | 0.29755 | -0.13733 | 0.40283 | -0.032044 | 123.3765 | 123.3994 | 60.7269 | 123.436 | 123.7427 | 123.5138 | 123.4543 | 123.4085 | -123.6511 | -123.468 | 123.111 | 123.3307 | 61.6974 | 60.3745
332.9844 | 123.4726 | -61.5646 | 61.8073 | 0.02533 | -0.00041012 | 0.0011707 | 0.00095062 | 0.0037492 | 0.001066 | 0.0011834 | -0.033875 | 0.002478 | 0.033045 | 0.036094 | -0.00022434 | -0.00056829 | -0.0046291 | 0.21057 | 61.8484 | -61.8439 | 61.5875 | 61.5784 | -61.8256 | 0.20142 | -1.1902 | 61.8713 | -61.6516 | 61.7981 | -0.96588 | -61.7157 | -61.2396 | -0.27924 | 0.041199 | -0.21973 | 123.143 | 61.7661 | -0.26093 | 62.0453 | 0.01831 | -0.086975 | 0.064087 | -0.009155 | 60.5988 | 0.32501 | -0.15106 | 0.41199 | -0.064087 | 123.4222 | 123.4314 | 60.6857 | 123.4497 | 123.6923 | 123.5229 | 123.4131 | 123.436 | -123.6511 | -123.4589 | 123.1522 | 123.3627 | 61.7752 | 60.3745
333.9844 | 123.5779 | -61.5372 | 61.7569 | -0.21881 | 0.00023068 | 0.00010251 | -0.00075838 | -0.00073704 | 0.0025614 | 0.00032904 | 0.030212 | 0.00098258 | 0.034113 | 0.030753 | -1.0744e-05 | -0.0014227 | 0.0019931 | 0.33417 | 61.7889 | -61.8027 | 61.6699 | 61.647 | -61.821 | 0.20142 | -1.236 | 61.7935 | -61.615 | 61.8759 | -0.84686 | -61.6196 | -61.1755 | -0.2655 | 0.032043 | -0.086975 | 123.1842 | 61.7386 | -0.28381 | 62.0041 | -0.018311 | -0.07782 | 0.036621 | 0.11902 | 60.6903 | 0.36163 | -0.082398 | 0.43945 | -0.004578 | 123.4497 | 123.4726 | 60.7681 | 123.4909 | 123.5916 | 123.4085 | 123.3261 | 123.3307 | -123.5596 | -123.3719 | 123.2071 | 123.4131 | 61.8713 | 60.3012
334.9844 | 123.5367 | -61.5417 | 61.8027 | 0.010071 | 0.00044428 | -0.00053829 | 0.0022324 | 0.0011856 | -0.002352 | -0.00031196 | -0.030823 | 0.00098258 | 0.035395 | 0.034812 | -0.00086514 | 0.00028631 | -0.0029201 | 0.22888 | 61.8942 | -61.8347 | 61.6104 | 61.5875 | -61.7844 | 0.23804 | -1.1398 | 61.8805 | -61.6287 | 61.8439 | -0.90179 | -61.6745 | -61.2076 | -0.29297 | 0.091553 | -0.19226 | 123.1293 | 61.7798 | -0.24262 | 62.0728 | 0.050354 | -0.086975 | 0.07782 | 0.041199 | 60.64 | 0.33417 | -0.13275 | 0.42114 | -0.045777 | 123.4222 | 123.4451 | 60.7269 | 123.4726 | 123.7289 | 123.5092 | 123.436 | 123.4222 | -123.6374 | -123.4314 | 123.1522 | 123.3856 | 61.7706 | 60.4019
335.9844 | 123.4818 | -61.5601 | 61.8576 | 0.010071 | -0.00041012 | -0.00053829 | -0.00033118 | 0.00097196 | -0.0032064 | -0.0015936 | 0.0088501 | 0.0011964 | 0.0386 | 0.026053 | -0.00065154 | -0.00099549 | 0.00092505 | 0.19684 | 61.8988 | -61.8118 | 61.5829 | 61.5417 | -61.8027 | 0.25635 | -1.1993 | 61.908 | -61.6287 | 61.8118 | -0.90179 | -61.6516 | -61.2305 | -0.25177 | 0.041199 | -0.27466 | 123.1018 | 61.8164 | -0.24261 | 62.0682 | 0.009156 | -0.068664 | 0.050354 | -0.045776 | 60.6583 | 0.32959 | -0.091552 | 0.39825 | -0.022888 | 123.3536 | 123.3948 | 60.7269 | 123.4406 | 123.7106 | 123.5367 | 123.4589 | 123.468 | -123.6694 | -123.4863 | 123.143 | 123.3719 | 61.7569 | 60.3607
336.9844 | 123.5184 | -61.5372 | 61.8118 | -0.005188 | 0.0021533 | 0.0015979 | 0.0013778 | -9.604e-05 | 0.0019204 | 0.0011834 | -0.033875 | -8.5416e-05 | 0.033045 | 0.032462 | -0.0015059 | 0.0037043 | -0.0014249 | 0.20599 | 61.8942 | -61.8347 | 61.6058 | 61.5921 | -61.8027 | 0.21515 | -1.1719 | 61.8713 | -61.6562 | 61.8073 | -0.96588 | -61.6379 | -61.235 | -0.29755 | 0.082397 | -0.20599 | 123.1293 | 61.7523 | -0.2655 | 62.0499 | 0.032044 | -0.11902 | 0.059509 | -0.004578 | 60.5713 | 0.30212 | -0.10071 | 0.42114 | 0.018311 | 123.4268 | 123.4406 | 60.6903 | 123.4634 | 123.7289 | 123.5275 | 123.4314 | 123.4085 | -123.6465 | -123.468 | 123.143 | 123.3444 | 61.7432 | 60.3653
337.9844 | 123.4955 | -61.5509 | 61.8256 | 0.010071 | 1.7082e-05 | 0.00074331 | 0.00073702 | 0.00097196 | -0.0027792 | -0.0026618 | 0.030212 | 0.00055538 | 0.031977 | 0.032462 | -0.0017197 | -0.0020637 | -0.0029201 | 0.10986 | 61.9492 | -61.7569 | 61.5372 | 61.5051 | -61.7935 | 0.20599 | -1.2131 | 61.8851 | -61.6516 | 61.7981 | -0.90637 | -61.6653 | -61.2259 | -0.20599 | 0.1236 | -0.28839 | 123.056 | 61.7569 | -0.24262 | 61.9629 | -0.036621 | -0.10071 | 0.059509 | -0.027466 | 60.6445 | 0.32501 | -0.11444 | 0.42572 | -0.013733 | 123.262 | 123.2941 | 60.7452 | 123.4497 | 123.7061 | 123.5367 | 123.5001 | 123.436 | -123.5825 | -123.4772 | 123.0881 | 123.349 | 61.6608 | 60.3378
339 | 123.5504 | -61.5051 | 61.7935 | -0.035705 | 0.00044428 | 0.00031611 | 0.00052342 | -0.00030984 | -0.0010702 | -0.0033026 | 0.10651 | -0.0017944 | 0.035182 | 0.03353 | -0.0012923 | -0.00056829 | -0.0016385 | 0.14648 | 61.8484 | -61.7798 | 61.615 | 61.615 | -61.7981 | 0.27008 | -1.3046 | 61.821 | -61.6196 | 61.8347 | -0.86975 | -61.6104 | -61.171 | -0.27466 | 0.054932 | -0.17853 | 123.1201 | 61.7752 | -0.29297 | 62.0499 | -0.018311 | -0.11444 | 0.027466 | 0.041199 | 60.6354 | 0.33417 | -0.10529 | 0.44861 | 0.009155 | 123.3948 | 123.3948 | 60.7498 | 123.4543 | 123.6282 | 123.4406 | 123.3536 | 123.3261 | -123.5733 | -123.4131 | 123.1201 | 123.3398 | 61.6516 | 60.2005
339.9844 | 123.4543 | -61.5509 | 61.8301 | -0.012817 | 0.00065788 | 0.00010251 | 0.00073702 | -0.00095064 | -2.232e-06 | -0.00095276 | -0.00030511 | 0.00141 | 0.035609 | 0.032249 | -0.0021469 | 0.00092711 | 0.00092505 | 0.18768 | 61.9034 | -61.7981 | 61.5875 | 61.5509 | -61.8073 | 0.24719 | -1.0849 | 61.9492 | -61.5967 | 61.8073 | -0.94299 | -61.6425 | -61.2122 | -0.24719 | 0.073242 | -0.24262 | 123.1018 | 61.7981 | -0.25635 | 62.0453 | -0.009155 | -0.045777 | 0.11902 | -0.022888 | 60.6079 | 0.33874 | -0.091553 | 0.38452 | -0.045776 | 123.349 | 123.3856 | 60.6537 | 123.4039 | 123.7015 | 123.5458 | 123.4543 | 123.5001 | -123.6282 | -123.4268 | 123.1384 | 123.3582 | 61.7386 | 60.466
340.9844 | 123.5367 | -61.5417 | 61.821 | -0.012817 | -0.00062372 | -0.0013929 | 0.0015914 | -0.0011642 | -0.0014974 | -0.00052556 | -0.021668 | 0.00012818 | 0.033259 | 0.039084 | -1.0744e-05 | -0.0020637 | -0.00014315 | 0.20142 | 61.9034 | -61.8073 | 61.6379 | 61.6241 | -61.7889 | 0.24261 | -1.1902 | 61.8942 | -61.6058 | 61.8347 | -0.89264 | -61.6699 | -61.203 | -0.2655 | 0.082397 | -0.18311 | 123.1659 | 61.7844 | -0.24719 | 62.0499 | 0.018311 | -0.064087 | 0.073242 | 0.013733 | 60.6491 | 0.33874 | -0.12817 | 0.40283 | -0.064087 | 123.4314 | 123.4451 | 60.7132 | 123.4406 | 123.7106 | 123.5001 | 123.4451 | 123.436 | -123.6282 | -123.4268 | 123.1796 | 123.3765 | 61.7432 | 60.3516
341.9844 | 123.5138 | -61.528 | 61.8347 | -0.035705 | 0.0010853 | -0.00096549 | 0.00030982 | -0.001805 | -0.00342 | -0.00095276 | -0.0094605 | 0.00076898 | 0.033686 | 0.032035 | -0.00086514 | 0.00071351 | 0.00049765 | 0.1831 | 61.9125 | -61.7935 | 61.5921 | 61.5417 | -61.8073 | 0.2243 | -1.2451 | 61.8942 | -61.615 | 61.8073 | -0.89264 | -61.6425 | -61.203 | -0.2655 | 0.07782 | -0.24262 | 123.0698 | 61.7523 | -0.27924 | 62.0178 | -0.013733 | -0.086975 | 0.059509 | -0.027466 | 60.6354 | 0.32501 | -0.11444 | 0.41199 | -0.027466 | 123.3353 | 123.3856 | 60.7224 | 123.4222 | 123.7061 | 123.5092 | 123.4406 | 123.4222 | -123.6282 | -123.4497 | 123.1201 | 123.3353 | 61.7111 | 60.2829
342.9844 | 123.5138 | -61.5601 | 61.821 | 0.02533 | 0.00087168 | -0.0016065 | 0.00073702 | -0.0026596 | 0.00021157 | -0.00073916 | -0.012512 | 0.0020508 | 0.032832 | 0.035239 | 0.0010575 | 0.00028631 | 0.0013523 | 0.19226 | 61.8713 | -61.8027 | 61.615 | 61.5967 | -61.7889 | 0.2243 | -1.2405 | 61.8622 | -61.6241 | 61.8073 | -0.93842 | -61.7294 | -61.2305 | -0.24261 | 0.050354 | -0.20599 | 123.1567 | 61.7844 | -0.22888 | 62.027 | 0.013733 | -0.064087 | 0.041199 | -0.013733 | 60.6216 | 0.32959 | -0.16937 | 0.39368 | -0.10528 | 123.3994 | 123.4177 | 60.6857 | 123.4314 | 123.674 | 123.4863 | 123.4314 | 123.4222 | -123.6237 | -123.4451 | 123.175 | 123.3673 | 61.7523 | 60.3195
343.9844 | 123.4955 | -61.5509 | 61.8073 | -0.005188 | 0.00065788 | -0.00011109 | 0.0026596 | -0.00095064 | 0.00021157 | 0.002038 | -0.052185 | 0.0011964 | 0.035395 | 0.035453 | -0.00022434 | 0.0032769 | 7.0452e-05 | 0.091553 | 61.8713 | -61.853 | 61.5417 | 61.4822 | -61.8942 | 0.091553 | -1.4511 | 61.8759 | -61.6745 | 61.6608 | -0.64545 | -61.7569 | -61.3129 | -0.30212 | 0.064087 | -0.2655 | 123.0331 | 61.6425 | -0.34332 | 61.9446 | -0.041199 | -0.1236 | 0.068665 | -0.14648 | 60.9055 | 0.23804 | -0.20599 | 0.36163 | -0.082397 | 123.3353 | 123.3948 | 61.0291 | 123.3353 | 123.7244 | 123.5504 | 123.4222 | 123.4268 | -123.6603 | -123.4818 | 123.0927 | 123.2117 | 61.6425 | 60.0998
344.9844 | 123.5229 | -61.5509 | 61.7981 | 0.032959 | 0.0010853 | 0.00074331 | 0.00073702 | 0.00075836 | -0.0012838 | -0.0024482 | -0.027771 | 0.00055538 | 0.034327 | 0.037376 | -0.0027877 | -0.00014089 | -0.00099755 | 0.20142 | 61.9125 | -61.7981 | 61.615 | 61.5784 | -61.7935 | 0.2243 | -1.2634 | 61.8622 | -61.6333 | 61.8439 | -0.88348 | -61.6516 | -61.1984 | -0.24719 | 0.11444 | -0.18311 | 123.1293 | 61.7752 | -0.24262 | 62.0224 | 0.004578 | -0.082398 | 0.064087 | 0.045776 | 60.6674 | 0.35248 | -0.10071 | 0.43488 | -0.01831 | 123.3765 | 123.4131 | 60.7498 | 123.4772 | 123.7106 | 123.4955 | 123.4634 | 123.4131 | -123.5962 | -123.4314 | 123.1659 | 123.3948 | 61.7523 | 60.2875
345.9844 | 123.5321 | -61.5051 | 61.8439 | 0.055847 | 0.0015125 | 0.0013843 | 0.00073702 | 0.0011856 | 0.00085237 | -0.00373 | 0.0088501 | 0.00034178 | 0.035182 | 0.031821 | -0.0025741 | 0.00049991 | -0.0020657 | 0.17853 | 61.9125 | -61.7752 | 61.6013 | 61.5601 | -61.7844 | 0.23346 | -1.3 | 61.9034 | -61.6379 | 61.8393 | -0.84686 | -61.6287 | -61.203 | -0.27008 | 0.068665 | -0.24262 | 123.0652 | 61.7386 | -0.27924 | 62.0087 | -0.009155 | -0.13275 | 0.059509 | -0.004578 | 60.6583 | 0.30212 | -0.1236 | 0.43487 | 0.009155 | 123.3353 | 123.3765 | 60.791 | 123.4772 | 123.6877 | 123.5413 | 123.4177 | 123.4085 | -123.6191 | -123.4818 | 123.1064 | 123.3444 | 61.6837 | 60.2051
346.9844 | 123.4863 | -61.5509 | 61.8301 | -0.066223 | -0.00041012 | 0.0011707 | 0.0026596 | 0.0031082 | 0.00042517 | 0.0024652 | -0.00030511 | 0.00076898 | 0.035822 | 0.034598 | 0.00020286 | 0.00049991 | -0.0016385 | 0.17853 | 61.8988 | -61.8164 | 61.5738 | 61.5189 | -61.7477 | 0.21057 | -1.3367 | 61.8896 | -61.6333 | 61.8347 | -0.90637 | -61.6653 | -61.2167 | -0.2655 | 0.068665 | -0.25635 | 123.0698 | 61.7615 | -0.19684 | 62.027 | 0.068664 | -0.082398 | 0.059509 | 0.004578 | 60.6445 | 0.33417 | -0.11444 | 0.41657 | -0.032043 | 123.3353 | 123.3902 | 60.7269 | 123.468 | 123.7152 | 123.5229 | 123.4497 | 123.4406 | -123.6465 | -123.4634 | 123.1247 | 123.3856 | 61.7294 | 60.2142
347.9844 | 123.4726 | -61.528 | 61.8439 | -0.005188 | 0.0010853 | -0.0022473 | 0.0011642 | -0.0020188 | -0.0025656 | -9.8356e-05 | 0.036316 | 0.0018372 | 0.036891 | 0.030753 | -0.00065154 | 0.0011407 | 0.0024203 | 0.15106 | 61.9217 | -61.8027 | 61.5875 | 61.5601 | -61.821 | 0.23804 | -1.3733 | 61.908 | -61.6241 | 61.6837 | -0.92468 | -61.7111 | -61.2579 | -0.27466 | 0.07782 | -0.25635 | 123.0881 | 61.7661 | -0.29297 | 62.0407 | -0.018311 | -0.096131 | 0.064087 | -0.16022 | 60.6033 | 0.27008 | -0.18311 | 0.36621 | -0.086975 | 123.3627 | 123.3902 | 60.6995 | 123.3078 | 123.7244 | 123.5321 | 123.4497 | 123.436 | -123.6465 | -123.468 | 123.1155 | 123.2117 | 61.6791 | 60.1547
348.9844 | 123.5641 | -61.5372 | 61.7661 | -0.073852 | 1.7082e-05 | -0.00032469 | 0.00030982 | -0.001805 | -0.00021583 | -0.00095276 | 0.036316 | -0.00051262 | 0.034541 | 0.032889 | -0.0010787 | 0.00049991 | 0.0024203 | 0.10986 | 61.8256 | -61.7981 | 61.6425 | 61.6333 | -61.7752 | 0.19226 | -1.4282 | 61.7844 | -61.6287 | 61.8393 | -0.8606 | -61.6196 | -61.1801 | -0.26093 | 0.05951 | -0.1236 | 123.1705 | 61.7294 | -0.23804 | 61.9904 | 0.022888 | -0.091553 | 0.018311 | 0.073242 | 60.6766 | 0.35706 | -0.082398 | 0.44861 | 0.009155 | 123.4314 | 123.4406 | 60.7681 | 123.468 | 123.6237 | 123.4131 | 123.3627 | 123.3215 | -123.5641 | -123.3948 | 123.1796 | 123.3765 | 61.647 | 60.1089
349.9844 | 123.4955 | -61.5143 | 61.7935 | 0.048218 | 0.00087168 | -0.00032469 | 0.0015914 | 0.0020402 | 0.001066 | 0.00032904 | -0.036926 | -0.00072642 | 0.031977 | 0.034171 | -1.0744e-05 | -0.00056829 | 0.0013523 | 0.1831 | 61.9125 | -61.8027 | 61.6287 | 61.6013 | -61.7706 | 0.25635 | -1.3184 | 61.9034 | -61.6013 | 61.8622 | -0.86975 | -61.6379 | -61.1801 | -0.28839 | 0.11902 | -0.16479 | 123.1155 | 61.7706 | -0.25635 | 62.059 | 0.032043 | -0.086975 | 0.10986 | 0.068665 | 60.6445 | 0.33417 | -0.1236 | 0.42114 | -0.036621 | 123.4039 | 123.4314 | 60.7315 | 123.4634 | 123.7152 | 123.5046 | 123.4268 | 123.4177 | -123.5962 | -123.3948 | 123.143 | 123.3765 | 61.6974 | 60.1959
350.9844 | 123.5092 | -61.5051 | 61.8118 | -0.020447 | 0.00087168 | 0.0011707 | 0.00073702 | 0.0020402 | 0.0034158 | 0.002038 | -0.039978 | 0.0011964 | 0.033259 | 0.037162 | -0.0019333 | -0.0018499 | 0.0037021 | 0.16937 | 61.8896 | -61.8027 | 61.6196 | 61.5921 | -61.7798 | 0.21057 | -1.4145 | 61.8896 | -61.6013 | 61.8576 | -0.98419 | -61.5921 | -61.2122 | -0.29755 | 0.077819 | -0.19226 | 123.0972 | 61.7157 | -0.27466 | 62.0132 | 0.022888 | -0.09613 | 0.077819 | 0.045776 | 60.5209 | 0.29297 | -0.086975 | 0.3891 | 0.009155 | 123.3948 | 123.4222 | 60.6171 | 123.4589 | 123.6923 | 123.4909 | 123.3948 | 123.3948 | -123.6145 | -123.4131 | 123.1247 | 123.3627 | 61.6745 | 60.0906
351.9844 | 123.4863 | -61.528 | 61.8393 | 0.15503 | -0.00041012 | -0.00032469 | 0.00052342 | -0.00052344 | 0.00042517 | 0.0024652 | -0.015564 | -0.00094002 | 0.034754 | 0.03118 | 0.00020286 | -0.00099549 | -0.00057035 | 0.054932 | 61.9537 | -61.7844 | 61.5921 | 61.5234 | -61.7752 | 0.24719 | -1.4511 | 61.8896 | -61.6333 | 61.8118 | -0.91553 | -61.647 | -61.2122 | -0.25635 | 0.11444 | -0.24719 | 123.0515 | 61.7752 | -0.24719 | 62.0316 | 0.009155 | -0.10529 | 0.050354 | -0.027465 | 60.6125 | 0.31586 | -0.11902 | 0.42114 | -0.013733 | 123.3078 | 123.3765 | 60.7178 | 123.4451 | 123.7381 | 123.5229 | 123.4818 | 123.4177 | -123.6237 | -123.4726 | 123.1201 | 123.3398 | 61.5829 | 60.0769
352.9844 | 123.4634 | -61.528 | 61.8073 | 0.0177 | 0.0015125 | 0.00031611 | 0.0026596 | 0.0033218 | 0.0021342 | -0.00052556 | -0.055237 | 0.00141 | 0.035182 | 0.029685 | -0.00065154 | -0.0014227 | -0.0029201 | 0.16479 | 61.8805 | -61.8073 | 61.6196 | 61.5784 | -61.7935 | 0.1831 | -1.4832 | 61.8668 | -61.6333 | 61.821 | -0.9201 | -61.6837 | -61.235 | -0.27924 | 0.073242 | -0.18768 | 123.1064 | 61.7111 | -0.2655 | 61.9904 | 0.013733 | -0.10529 | 0.059509 | 0.013733 | 60.6079 | 0.29297 | -0.15564 | 0.39826 | -0.050354 | 123.3856 | 123.4268 | 60.7132 | 123.4543 | 123.6877 | 123.5001 | 123.4085 | 123.3948 | -123.6145 | -123.4406 | 123.1476 | 123.349 | 61.6928 | 60.0449
353.9844 | 123.4726 | -61.5143 | 61.8484 | 0.040589 | 0.00065788 | -0.0018201 | -0.00033118 | -0.0030868 | -0.00085663 | 0.0026788 | -0.033875 | 0.00012818 | 0.034754 | 0.026267 | -1.0744e-05 | -0.0012091 | 0.0024203 | 0.13733 | 61.9217 | -61.8073 | 61.4365 | 61.4273 | -61.7294 | 0.19226 | -1.5106 | 61.8942 | -61.6379 | 61.8073 | -0.91553 | -61.6608 | -61.2167 | -0.29297 | 0.073242 | -0.41199 | 122.9416 | 61.7065 | -0.21515 | 61.9995 | 0.07782 | -0.1236 | 0.045776 | -0.041199 | 60.5988 | 0.29755 | -0.14648 | 0.42114 | -0.022889 | 123.2346 | 123.2437 | 60.7224 | 123.4451 | 123.7289 | 123.5321 | 123.436 | 123.4085 | -123.6557 | -123.4863 | 122.9507 | 123.3215 | 61.6516 | 60.0037
354.9844 | 123.5321 | -61.5555 | 61.8301 | 0.040589 | 0.0019397 | 0.0024523 | 0.00030982 | 0.00097196 | -0.0025656 | 0.0016106 | -0.0094605 | 0.00098258 | 0.034754 | 0.038444 | -0.0015059 | -0.00078189 | 0.00028405 | 0.16937 | 61.9171 | -61.8027 | 61.6379 | 61.5967 | -61.7935 | 0.24719 | -1.4786 | 61.8668 | -61.6333 | 61.8484 | -0.87891 | -61.6379 | -61.1755 | -0.24719 | 0.086975 | -0.19226 | 123.1522 | 61.8027 | -0.23804 | 62.0499 | 0.009155 | -0.07782 | 0.036621 | 0.018311 | 60.6766 | 0.37994 | -0.082397 | 0.45776 | -0.004577 | 123.3994 | 123.4406 | 60.7544 | 123.4818 | 123.7198 | 123.5001 | 123.4726 | 123.4222 | -123.6328 | -123.4634 | 123.1934 | 123.4039 | 61.7249 | 60.0769
355.9844 | 123.5367 | -61.5326 | 61.8393 | 0.0177 | -0.00083732 | -0.0013929 | 0.0013778 | -0.00073704 | 0.0021342 | 0.0033196 | -0.0094605 | 0.0011964 | 0.035822 | 0.034171 | -0.00043794 | 0.00049991 | -0.0016385 | 0.17853 | 61.94 | -61.7752 | 61.5921 | 61.5646 | -61.7752 | 0.24261 | -1.5335 | 61.9308 | -61.6058 | 61.8439 | -0.84686 | -61.6196 | -61.1755 | -0.24262 | 0.10071 | -0.24719 | 123.0972 | 61.7752 | -0.24262 | 62.0178 | 0 | -0.073242 | 0.091553 | 0.004578 | 60.6857 | 0.35706 | -0.086975 | 0.4303 | -0.013733 | 123.3398 | 123.3673 | 60.759 | 123.4497 | 123.7152 | 123.5367 | 123.4726 | 123.4634 | -123.6145 | -123.4451 | 123.1247 | 123.3765 | 61.7111 | 59.9991
356.9844 | 123.4955 | -61.5417 | 61.8164 | -0.012817 | -0.00019652 | -0.0013929 | 0.0013778 | 0.00033116 | -0.0010702 | -0.0028754 | -0.039978 | 0.0011964 | 0.033259 | 0.033744 | -0.0019333 | 0.0011407 | 7.0452e-05 | 0.16937 | 61.8988 | -61.8347 | 61.5601 | 61.528 | -61.7157 | 0.21057 | -1.5472 | 61.9034 | -61.6516 | 61.853 | -0.89722 | -61.6653 | -61.1938 | -0.29297 | 0.082398 | -0.25635 | 123.0698 | 61.7523 | -0.17395 | 62.0453 | 0.11902 | -0.10986 | 0.086975 | 0.036621 | 60.6445 | 0.3479 | -0.1236 | 0.45776 | -0.013733 | 123.3627 | 123.3948 | 60.7544 | 123.5046 | 123.7335 | 123.555 | 123.4406 | 123.4451 | -123.6511 | -123.468 | 123.1018 | 123.3948 | 61.7111 | 59.9945
357.9844 | 123.5001 | -61.5234 | 61.8393 | 0.055847 | 0.00044428 | -0.00032469 | 0.00030982 | -0.002446 | 0.00021157 | -0.0015936 | -0.018616 | 0.00098258 | 0.0339 | 0.032462 | -0.00043794 | 0.0015679 | -0.00078395 | 0.15106 | 61.9125 | -61.7844 | 61.6058 | 61.5646 | -61.7889 | 0.21973 | -1.593 | 61.9263 | -61.615 | 61.8393 | -0.89264 | -61.6287 | -61.2076 | -0.26093 | 0.073243 | -0.23346 | 123.0881 | 61.7432 | -0.2655 | 62.0041 | -0.004577 | -0.091553 | 0.086976 | 0 | 60.6308 | 0.31586 | -0.10529 | 0.40741 | -0.013733 | 123.349 | 123.3902 | 60.7224 | 123.4543 | 123.6969 | 123.5413 | 123.436 | 123.4497 | -123.6237 | -123.4543 | 123.1293 | 123.3627 | 61.6745 | 59.9304
358.9844 | 123.4863 | -61.5326 | 61.853 | -0.020447 | -0.00062372 | 0.00095711 | 0.00052342 | -0.00095064 | -0.00064303 | -0.0018072 | -0.033875 | 0.00012818 | 0.035822 | 0.038871 | -0.0010787 | 0.0013543 | 0.00028405 | 0.15106 | 61.8851 | -61.8027 | 61.6241 | 61.5967 | -61.7752 | 0.21057 | -1.6754 | 61.8759 | -61.647 | 61.8301 | -0.89264 | -61.6241 | -61.1847 | -0.27008 | 0.032044 | -0.22888 | 123.1293 | 61.7432 | -0.24262 | 62.0132 | 0.027465 | -0.11444 | 0.022889 | -0.022888 | 60.64 | 0.3479 | -0.091553 | 0.46234 | 0.022888 | 123.3994 | 123.4268 | 60.7544 | 123.4772 | 123.6877 | 123.5229 | 123.4177 | 123.4085 | -123.6557 | -123.5001 | 123.1567 | 123.3627 | 61.6837 | 59.8572
359.9844 | 123.5046 | -61.5372 | 61.8256 | -0.035705 | 0.00044428 | 0.00010251 | 0.00073702 | 0.0011856 | -0.0047018 | 0.0041742 | -0.012512 | 0.00034178 | 0.034327 | 0.031608 | -0.0012923 | 7.2706e-05 | -0.0018521 | 0.17395 | 61.9217 | -61.7981 | 61.6104 | 61.6013 | -61.7615 | 0.2243 | -1.5747 | 61.8942 | -61.5738 | 61.853 | -0.87891 | -61.6379 | -61.1847 | -0.26093 | 0.09613 | -0.21515 | 123.1384 | 61.7615 | -0.2243 | 62.0224 | 0.036621 | -0.036622 | 0.068664 | 0.027465 | 60.6583 | 0.35248 | -0.10071 | 0.3891 | -0.064086 | 123.3994 | 123.4085 | 60.6949 | 123.4268 | 123.7198 | 123.468 | 123.4589 | 123.4314 | -123.6237 | -123.3994 | 123.1476 | 123.3902 | 61.7111 | 59.9625
360.9844 | 123.5184 | -61.5372 | 61.8118 | -0.073852 | -0.00041012 | -0.00053829 | 0.0028732 | 0.00011756 | 0.00021157 | 0.0033196 | -0.021668 | 0.0039734 | 0.034113 | 0.031394 | 0.0010575 | 7.2706e-05 | -0.0033475 | 0.14191 | 61.908 | -61.7889 | 61.6287 | 61.5967 | -61.7889 | 0.21515 | -1.6205 | 61.8668 | -61.6333 | 61.8622 | -0.89722 | -61.6241 | -61.1755 | -0.25177 | 0.09613 | -0.18311 | 123.1338 | 61.7523 | -0.25177 | 62.0041 | 0 | -0.096131 | 0.054931 | 0.050354 | 60.64 | 0.36163 | -0.086976 | 0.45776 | 0.009155 | 123.3856 | 123.4177 | 60.7361 | 123.4955 | 123.6969 | 123.5001 | 123.4451 | 123.4039 | -123.6008 | -123.4451 | 123.1659 | 123.3994 | 61.6791 | 59.9167
361.9844 | 123.5001 | -61.5326 | 61.8439 | 0.032959 | 0.00044428 | -0.00075189 | -0.0013992 | -0.00052344 | 0.00063877 | -0.0035162 | 0.014954 | 0.0022644 | 0.03625 | 0.031821 | -0.0012923 | -0.0014227 | 0.0019931 | 0.086975 | 61.9263 | -61.8073 | 61.5967 | 61.5601 | -61.7889 | 0.24261 | -1.6571 | 61.908 | -61.615 | 61.821 | -0.90637 | -61.6516 | -61.1847 | -0.27466 | 0.082398 | -0.24719 | 123.0927 | 61.7752 | -0.25635 | 62.0499 | 0.018311 | -0.082397 | 0.064087 | -0.022888 | 60.6262 | 0.3479 | -0.11902 | 0.4303 | -0.036621 | 123.3673 | 123.4039 | 60.7086 | 123.436 | 123.7335 | 123.5229 | 123.4589 | 123.4406 | -123.6511 | -123.4589 | 123.1293 | 123.3536 | 61.6196 | 59.8755
362.9844 | 123.4726 | -61.5417 | 61.8256 | -0.050964 | 0.00065788 | -0.00053829 | 0.0015914 | 0.0033218 | -0.0012838 | -0.00031196 | -0.018616 | -0.00029902 | 0.032618 | 0.036094 | -0.0034287 | 0.0015679 | 0.0022067 | 0.14191 | 61.8942 | -61.7706 | 61.6058 | 61.5738 | -61.8118 | 0.17395 | -1.7303 | 61.8759 | -61.6287 | 61.8118 | -0.93842 | -61.6837 | -61.235 | -0.22888 | 0.068664 | -0.21973 | 123.1155 | 61.7157 | -0.27008 | 61.9446 | -0.041199 | -0.086975 | 0.050354 | -0.013733 | 60.6033 | 0.3067 | -0.14191 | 0.39368 | -0.054932 | 123.3444 | 123.3765 | 60.6903 | 123.4406 | 123.6649 | 123.5046 | 123.436 | 123.4177 | -123.5962 | -123.4543 | 123.1476 | 123.3536 | 61.6837 | 59.8114
363.9844 | 123.5229 | -61.5234 | 61.8576 | 0.0177 | 0.0025805 | -0.00075189 | 0.0011642 | 0.0041764 | 0.001066 | 0.00075624 | -0.0094605 | -0.00029902 | 0.033045 | 0.03823 | -0.0025741 | -0.0029181 | -0.00035675 | 0.14191 | 61.9217 | -61.7706 | 61.6379 | 61.5875 | -61.7569 | 0.25635 | -1.6754 | 61.908 | -61.6241 | 61.8576 | -0.87433 | -61.6241 | -61.1664 | -0.24719 | 0.064087 | -0.21973 | 123.111 | 61.7798 | -0.23346 | 62.027 | 0.013733 | -0.10071 | 0.050354 | 0 | 60.6491 | 0.35706 | -0.10071 | 0.45776 | 0 | 123.3582 | 123.4085 | 60.7498 | 123.4818 | 123.6923 | 123.5321 | 123.4451 | 123.4314 | -123.6282 | -123.4818 | 123.1613 | 123.381 | 61.6653 | 59.848
364.9844 | 123.468 | -61.5234 | 61.8301 | -0.012817 | 0.0012989 | 0.0024523 | -0.00011758 | 0.00054476 | 0.0021342 | 0.002038 | -0.021668 | 0.0029052 | 0.033259 | 0.034385 | -1.0744e-05 | 0.00049991 | 0.0019931 | 0.11902 | 61.908 | -61.7935 | 61.6104 | 61.5875 | -61.8027 | 0.18768 | -1.7532 | 61.8759 | -61.6379 | 61.821 | -0.90637 | -61.6928 | -61.2167 | -0.27008 | 0.07782 | -0.21973 | 123.111 | 61.7111 | -0.27924 | 61.9812 | -0.009155 | -0.11444 | 0.045777 | -0.009155 | 60.6171 | 0.3067 | -0.16937 | 0.42114 | -0.054932 | 123.381 | 123.4039 | 60.7315 | 123.4589 | 123.7015 | 123.5138 | 123.4314 | 123.3994 | -123.6237 | -123.468 | 123.1338 | 123.3444 | 61.6425 | 59.7702
365.9844 | 123.5321 | -61.5234 | 61.8439 | 0.032959 | 0.00044428 | -0.00032469 | -0.0016128 | 0.002681 | 0.0029886 | -0.0022346 | -0.0033569 | 0.0020508 | 0.035395 | 0.031394 | -0.0012923 | 7.2706e-05 | -0.0012111 | 0.14648 | 61.9263 | -61.7706 | 61.6379 | 61.5967 | -61.7615 | 0.24719 | -1.7303 | 61.9171 | -61.6196 | 61.853 | -0.87433 | -61.6013 | -61.1435 | -0.24719 | 0.082398 | -0.20599 | 123.1201 | 61.7706 | -0.23804 | 62.0178 | 0.009155 | -0.096131 | 0.073242 | 0.009155 | 60.6491 | 0.37994 | -0.07782 | 0.47607 | 0.018311 | 123.3673 | 123.4085 | 60.7452 | 123.4726 | 123.6969 | 123.5367 | 123.4497 | 123.4406 | -123.6145 | -123.4634 | 123.1613 | 123.3765 | 61.6699 | 59.7931
366.9844 | 123.4543 | -61.5646 | 61.8576 | -0.028076 | 0.00044428 | 0.00095711 | 0.0013778 | -0.00052344 | -0.00042943 | -9.8356e-05 | -0.052185 | 0.0029052 | 0.032618 | 0.035026 | -0.0015059 | 0.0013543 | 0.0024203 | 0.082397 | 61.8896 | -61.821 | 61.5692 | 61.5326 | -61.8484 | 0.13733 | -1.918 | 61.8713 | -61.6425 | 61.7798 | -0.9613 | -61.734 | -61.2579 | -0.25635 | 0.032043 | -0.28839 | 123.0972 | 61.702 | -0.28381 | 61.9583 | -0.027466 | -0.07782 | 0.013733 | -0.07782 | 60.6033 | 0.3067 | -0.16937 | 0.38452 | -0.091553 | 123.3536 | 123.3902 | 60.6812 | 123.4222 | 123.7106 | 123.5138 | 123.4543 | 123.436 | -123.6786 | -123.5001 | 123.1338 | 123.3444 | 61.647 | 59.6466
367.9844 | 123.5046 | -61.5051 | 61.8393 | -0.035705 | -0.00062372 | 0.00052971 | 0.00030982 | 0.00011756 | -0.001711 | 0.00096984 | -0.0033569 | 0.0020508 | 0.033473 | 0.029258 | -0.0023605 | -0.00014089 | 0.0034885 | 0.11902 | 61.9354 | -61.7889 | 61.6333 | 61.5829 | -61.7615 | 0.21515 | -1.7853 | 61.8851 | -61.6013 | 61.8393 | -0.85602 | -61.5967 | -61.171 | -0.28381 | 0.096131 | -0.20599 | 123.0881 | 61.7203 | -0.25635 | 62.0041 | 0.027465 | -0.09613 | 0.045777 | 0 | 60.6491 | 0.33417 | -0.091553 | 0.4303 | 0.004577 | 123.3719 | 123.4222 | 60.7452 | 123.4406 | 123.7244 | 123.4863 | 123.4406 | 123.3902 | -123.6282 | -123.4406 | 123.1384 | 123.3444 | 61.6241 | 59.7198
368.9844 | 123.4634 | -61.496 | 61.8347 | 0.071106 | 0.00087168 | -0.0016065 | 0.0011642 | 0.0020402 | 0.00063877 | 0.0011834 | -0.027771 | 0.0026916 | 0.035822 | 0.029044 | -0.0017197 | 7.2706e-05 | -0.00035675 | 0.10529 | 61.9217 | -61.7935 | 61.6287 | 61.5829 | -61.7706 | 0.18768 | -1.8402 | 61.8759 | -61.6104 | 61.8301 | -0.91095 | -61.6745 | -61.2076 | -0.29755 | 0.086975 | -0.20599 | 123.0789 | 61.6837 | -0.27466 | 61.9812 | 0.022888 | -0.11444 | 0.041199 | -0.004578 | 60.585 | 0.28839 | -0.17853 | 0.40283 | -0.064087 | 123.3765 | 123.4222 | 60.6995 | 123.4406 | 123.7152 | 123.4863 | 123.4177 | 123.3719 | -123.6282 | -123.4451 | 123.1247 | 123.3261 | 61.6013 | 59.6558
369.9844 | 123.5092 | -61.528 | 61.8164 | -0.012817 | 0.0017261 | 0.00052971 | 0.0011642 | -0.0020188 | -0.0021384 | 0.00075624 | 0.0088501 | -0.00094002 | 0.035182 | 0.032676 | -0.00043794 | -0.00035469 | -0.00035675 | 0.1236 | 61.9263 | -61.7844 | 61.6196 | 61.6013 | -61.7661 | 0.19226 | -1.8173 | 61.8805 | -61.6333 | 61.8668 | -0.86975 | -61.615 | -61.1893 | -0.25635 | 0.10986 | -0.19684 | 123.1293 | 61.7203 | -0.23804 | 61.9766 | 0.018311 | -0.10529 | 0.064087 | 0.050354 | 60.6583 | 0.33875 | -0.086975 | 0.44403 | 0.018311 | 123.3856 | 123.4039 | 60.7636 | 123.5001 | 123.7106 | 123.5138 | 123.4543 | 123.4085 | -123.6008 | -123.4497 | 123.1476 | 123.3948 | 61.6516 | 59.7107
370.9844 | 123.4451 | -61.528 | 61.8439 | 0.010071 | 0.00087168 | 0.00010251 | 0.0037276 | 0.0016128 | 0.001066 | 0.0016106 | -0.046082 | 0.00141 | 0.034754 | 0.036094 | -0.0019333 | 0.00071351 | -0.0024929 | 0.041199 | 61.8896 | -61.8118 | 61.5829 | 61.528 | -61.8256 | 0.10986 | -1.9867 | 61.8805 | -61.6425 | 61.8027 | -0.95673 | -61.7111 | -61.2625 | -0.28381 | 0.045776 | -0.26093 | 123.056 | 61.6379 | -0.29755 | 61.9217 | -0.013733 | -0.11444 | 0.036621 | -0.041199 | 60.5713 | 0.2655 | -0.18311 | 0.37994 | -0.068665 | 123.3398 | 123.3948 | 60.6857 | 123.4451 | 123.7015 | 123.5229 | 123.4177 | 123.4085 | -123.6557 | -123.4863 | 123.111 | 123.3307 | 61.5692 | 59.5413
371.9844 | 123.5046 | -61.528 | 61.8301 | 0.0177 | 0.0017261 | -0.00075189 | 0.00095062 | 0.0031082 | 0.0014932 | 0.00075624 | -0.00030511 | 0.0016236 | 0.0339 | 0.034171 | -1.0744e-05 | 0.0011407 | -0.0016385 | 0.11902 | 61.9263 | -61.7844 | 61.6241 | 61.5967 | -61.7569 | 0.18768 | -1.8677 | 61.8805 | -61.5875 | 61.8668 | -0.87891 | -61.6058 | -61.1755 | -0.25635 | 0.096131 | -0.20599 | 123.1247 | 61.7157 | -0.22888 | 61.972 | 0.027466 | -0.059509 | 0.050354 | 0.036621 | 60.6491 | 0.35248 | -0.07782 | 0.41199 | -0.018311 | 123.381 | 123.4085 | 60.7086 | 123.4543 | 123.7106 | 123.468 | 123.4543 | 123.4085 | -123.6145 | -123.4177 | 123.1522 | 123.3948 | 61.647 | 59.6603
372.9844 | 123.4451 | -61.5509 | 61.8256 | -0.058594 | 0.0017261 | 0.00010251 | 0.00052342 | 0.00075836 | -0.00021583 | -9.8356e-05 | -0.018616 | 0.00055538 | 0.035609 | 0.03054 | -0.00086514 | 0.0011407 | 7.0452e-05 | 0.054932 | 61.9034 | -61.8256 | 61.5875 | 61.5509 | -61.821 | 0.12817 | -2.0096 | 61.8805 | -61.615 | 61.8027 | -0.93842 | -61.6928 | -61.2167 | -0.27466 | 0.077819 | -0.23804 | 123.1018 | 61.6791 | -0.27008 | 61.9537 | 0.004578 | -0.064087 | 0.054931 | -0.022889 | 60.6125 | 0.33417 | -0.14191 | 0.39825 | -0.07782 | 123.3765 | 123.4131 | 60.6766 | 123.4177 | 123.7289 | 123.4955 | 123.4543 | 123.4314 | -123.6511 | -123.4406 | 123.1384 | 123.3536 | 61.6058 | 59.5413
373.9844 | 123.5092 | -61.5051 | 61.821 | 0.0024415 | 0.00044428 | 0.00031611 | -0.00011758 | 0.00097196 | -0.0021384 | 0.00096984 | -0.0094605 | 0.0011964 | 0.033473 | 0.044639 | -0.0025741 | 0.00049991 | -0.0024929 | 0.07782 | 61.9217 | -61.7752 | 61.5601 | 61.6745 | -61.7706 | 0.19226 | -1.9501 | 61.8942 | -61.6058 | 61.8347 | -0.89264 | -61.6379 | -61.1847 | -0.27008 | 0.10071 | -0.26093 | 123.1796 | 61.6974 | -0.2655 | 61.9675 | 0.004578 | -0.10071 | 0.073242 | 0.013733 | 60.6125 | 0.32044 | -0.13275 | 0.42114 | -0.032043 | 123.4497 | 123.3353 | 60.7132 | 123.4406 | 123.6969 | 123.5001 | 123.4268 | 123.3994 | -123.5962 | -123.4268 | 123.0652 | 123.3398 | 61.5829 | 59.5551
374.9844 | 123.4909 | -61.5463 | 61.8484 | 0.010071 | 0.00023068 | 0.00052971 | 0.0022324 | 0.00054476 | -0.0010702 | 0.0024652 | -0.030823 | -0.00029902 | 0.034113 | 0.038871 | -0.0012923 | 0.00049991 | 0.0013523 | 0.036621 | 61.8988 | -61.8073 | 61.5829 | 61.5417 | -61.821 | 0.11444 | -2.0782 | 61.8988 | -61.5921 | 61.8073 | -0.92926 | -61.6745 | -61.2167 | -0.26093 | 0.050354 | -0.2655 | 123.0881 | 61.6608 | -0.27466 | 61.9217 | -0.013733 | -0.045776 | 0.050354 | -0.041199 | 60.6171 | 0.32959 | -0.12817 | 0.37537 | -0.082398 | 123.349 | 123.3902 | 60.6628 | 123.3994 | 123.7061 | 123.4909 | 123.4451 | 123.4451 | -123.6557 | -123.4406 | 123.1293 | 123.3536 | 61.5829 | 59.4681
375.9844 | 123.5001 | -61.5143 | 61.8439 | 0.010071 | -0.00083732 | 0.00010251 | 9.6222e-05 | -0.00073704 | -0.00021583 | -0.0011664 | -0.0033569 | 0.0020508 | 0.035182 | 0.040153 | -0.0012923 | 0.00092711 | 0.0013523 | 0.082397 | 61.9263 | -61.7798 | 61.6333 | 61.6013 | -61.7523 | 0.24261 | -1.9684 | 61.9034 | -61.6058 | 61.8484 | -0.86517 | -61.6196 | -61.1664 | -0.2655 | 0.082398 | -0.21057 | 123.1155 | 61.7569 | -0.23804 | 62.0224 | 0.027466 | -0.091553 | 0.059509 | 0.004578 | 60.6491 | 0.3479 | -0.10529 | 0.43945 | -0.013733 | 123.381 | 123.4131 | 60.7407 | 123.4543 | 123.7061 | 123.5092 | 123.4406 | 123.4177 | -123.6237 | -123.4497 | 123.1476 | 123.3627 | 61.5967 | 59.5459
376.9844 | 123.4589 | -61.5463 | 61.8256 | -0.005188 | -0.0012647 | 0.0015979 | 9.6222e-05 | 0.002681 | 0.00042517 | 0.00096984 | -0.021668 | 0.0026916 | 0.035822 | 0.034385 | 0.00063026 | -0.00099549 | -0.0012111 | -0.009155 | 61.908 | -61.8164 | 61.5601 | 61.4914 | -61.8851 | 0.054932 | -2.2202 | 61.8713 | -61.615 | 61.7706 | -0.97504 | -61.7432 | -61.2625 | -0.27008 | 0.082397 | -0.2655 | 123.0377 | 61.6013 | -0.33875 | 61.8713 | -0.068665 | -0.068664 | 0.045776 | -0.054932 | 60.5713 | 0.28381 | -0.19684 | 0.35248 | -0.12817 | 123.3078 | 123.3765 | 60.64 | 123.3856 | 123.7244 | 123.4863 | 123.4543 | 123.4177 | -123.642 | -123.4406 | 123.1064 | 123.317 | 61.5372 | 59.3262
377.9844 | 123.4863 | -61.4914 | 61.8393 | 0.010071 | 0.0015125 | 0.0020251 | 0.0011642 | 0.0033218 | -0.0010702 | 0.002038 | -0.0064087 | 0.0020508 | 0.034541 | 0.030112 | 0.0021255 | -0.0024909 | 0.0039157 | 0.059509 | 61.9171 | -61.7706 | 61.6241 | 61.6058 | -61.7523 | 0.19684 | -2.0233 | 61.9034 | -61.6058 | 61.7844 | -0.81024 | -61.6379 | -61.1801 | -0.27924 | 0.07782 | -0.21515 | 123.0972 | 61.6882 | -0.26093 | 61.9675 | 0.018311 | -0.11444 | 0.064087 | -0.054931 | 60.6812 | 0.31128 | -0.14648 | 0.42572 | -0.032043 | 123.3765 | 123.3948 | 60.7956 | 123.3902 | 123.6877 | 123.5092 | 123.4085 | 123.3948 | -123.6099 | -123.4451 | 123.1155 | 123.2758 | 61.5509 | 59.4681
378.9844 | 123.4589 | -61.528 | 61.8301 | 0.055847 | -0.00019652 | 0.00095711 | 0.00052342 | 0.00011756 | -0.00085663 | -0.00031196 | -0.027771 | 0.0020508 | 0.0339 | 0.029044 | -0.0023605 | -0.0024909 | 0.00092505 | -0.004578 | 61.9171 | -61.8073 | 61.5784 | 61.5234 | -61.8393 | 0.07782 | -2.211 | 61.8942 | -61.6104 | 61.7798 | -0.96588 | -61.734 | -61.2442 | -0.27924 | 0.086975 | -0.25177 | 123.0515 | 61.6058 | -0.31128 | 61.8851 | -0.032043 | -0.082398 | 0.064087 | -0.050354 | 60.5621 | 0.28381 | -0.20599 | 0.36621 | -0.1236 | 123.3307 | 123.3856 | 60.6445 | 123.3902 | 123.7244 | 123.5046 | 123.4451 | 123.4222 | -123.6374 | -123.4406 | 123.1064 | 123.3078 | 61.5234 | 59.317
379.9844 | 123.4726 | -61.5051 | 61.821 | -0.043335 | 0.0019397 | 0.0011707 | -0.00075838 | -0.0011642 | 0.00085237 | 0.0011834 | 0.024109 | -0.0011536 | 0.034541 | 0.037162 | -0.0015059 | 7.2706e-05 | 0.0017795 | 0.059509 | 61.9217 | -61.7889 | 61.6241 | 61.6058 | -61.7661 | 0.15564 | -2.124 | 61.9034 | -61.6104 | 61.8393 | -0.91095 | -61.6608 | -61.1938 | -0.28381 | 0.10071 | -0.19684 | 123.111 | 61.6608 | -0.26093 | 61.9446 | 0.022888 | -0.10529 | 0.082397 | 0.01831 | 60.5942 | 0.31128 | -0.15564 | 0.41656 | -0.050354 | 123.3948 | 123.4131 | 60.6995 | 123.4497 | 123.7106 | 123.5138 | 123.4268 | 123.4085 | -123.6099 | -123.4314 | 123.1293 | 123.3444 | 61.5646 | 59.3811
380.9844 | 123.3261 | -61.5601 | 61.7615 | -0.058594 | 0.00023068 | -0.00032469 | 0.00030982 | -0.0011642 | -0.00021583 | -0.0018072 | -0.030823 | 0.00034178 | 0.033686 | 0.030112 | 0.00020286 | 0.0026361 | 0.0022067 | -0.032043 | 61.9308 | -61.8073 | 61.5326 | 61.4594 | -61.8896 | 0.059509 | -2.3071 | 61.8942 | -61.6379 | 61.7889 | -0.9613 | -61.7157 | -61.0199 | -0.24719 | 0.16937 | -0.22888 | 123.0194 | 61.6196 | -0.32959 | 61.8668 | -0.082397 | -0.077819 | 0.13275 | 0.027465 | 60.5988 | 0.54016 | -0.15564 | 0.61798 | -0.07782 | 123.2666 | 123.3398 | 60.6766 | 123.4268 | 123.7381 | 123.5321 | 123.4909 | 123.4543 | -123.5687 | -123.3994 | 123.0927 | 123.349 | 61.528 | 59.2529
381.9844 | 123.5092 | -61.5143 | 61.8393 | 0.0024415 | 0.0012989 | 0.00010251 | -0.00033118 | -0.0013778 | -0.0012838 | 0.0041742 | -0.0064087 | -8.5416e-05 | 0.034541 | 0.031821 | -0.0025741 | 0.0011407 | -0.00035675 | 0.032043 | 61.9263 | -61.7706 | 61.6379 | 61.5967 | -61.734 | 0.16022 | -2.1194 | 61.9125 | -61.6013 | 61.8713 | -0.86517 | -61.6287 | -61.171 | -0.25635 | 0.086976 | -0.20142 | 123.111 | 61.6745 | -0.21973 | 61.9308 | 0.036621 | -0.086975 | 0.073243 | 0.032044 | 60.6491 | 0.34332 | -0.11444 | 0.4303 | -0.027466 | 123.3673 | 123.4085 | 60.7361 | 123.4726 | 123.6969 | 123.5138 | 123.4406 | 123.4268 | -123.6099 | -123.4406 | 123.1522 | 123.3856 | 61.5463 | 59.3948
382.9844 | 123.4634 | -61.5509 | 61.8164 | 0.0024415 | 0.00044428 | 0.00095711 | -0.00011758 | 0.0011856 | 0.00085237 | 0.00075624 | -0.018616 | -8.5416e-05 | 0.035609 | 0.033958 | -0.0015059 | -0.00099549 | -0.00078395 | -0.004578 | 61.94 | -61.7798 | 61.5829 | 61.5555 | -61.8118 | 0.09613 | -2.2614 | 61.8942 | -61.6196 | 61.8073 | -0.92468 | -61.6653 | -61.2122 | -0.22888 | 0.1236 | -0.23346 | 123.1064 | 61.647 | -0.26093 | 61.8759 | -0.032044 | -0.068665 | 0.07782 | -0.009155 | 60.6262 | 0.33874 | -0.11444 | 0.40741 | -0.045776 | 123.3353 | 123.3627 | 60.6949 | 123.4268 | 123.7198 | 123.5138 | 123.4909 | 123.4451 | -123.5962 | -123.436 | 123.1338 | 123.3582 | 61.5463 | 59.2895
383.9844 | 123.5046 | -61.5189 | 61.8576 | -0.066223 | 0.0019397 | 0.0020251 | -0.00011758 | 0.0016128 | -0.00085663 | -0.0018072 | -0.0033569 | -0.0017944 | 0.036463 | 0.033744 | -0.0015059 | -0.0020637 | 7.0452e-05 | 0.009155 | 61.9354 | -61.7889 | 61.6379 | 61.615 | -61.7523 | 0.16022 | -2.1973 | 61.8942 | -61.5875 | 61.8805 | -0.87433 | -61.6241 | -61.1481 | -0.27008 | 0.07782 | -0.21973 | 123.1338 | 61.6791 | -0.23346 | 61.9492 | 0.036621 | -0.068664 | 0.036621 | 0.022888 | 60.6445 | 0.37079 | -0.10529 | 0.43945 | -0.036622 | 123.4039 | 123.4268 | 60.7132 | 123.468 | 123.7244 | 123.4818 | 123.4543 | 123.4131 | -123.6465 | -123.4451 | 123.1567 | 123.3994 | 61.528 | 59.3216
384.9844 | 123.4726 | -61.5143 | 61.8301 | -0.020447 | 0.00065788 | 0.0011707 | 0.00030982 | 0.002681 | 0.0014932 | 0.00011544 | -0.027771 | 0.00076898 | 0.033045 | 0.034171 | 0.00063026 | 7.2706e-05 | 0.00092505 | -0.027466 | 61.9308 | -61.7798 | 61.5829 | 61.528 | -61.8301 | 0.073242 | -2.3575 | 61.9034 | -61.6333 | 61.7844 | -0.97961 | -61.7111 | -61.2396 | -0.2655 | 0.10071 | -0.24719 | 123.0423 | 61.5875 | -0.31586 | 61.853 | -0.050354 | -0.11902 | 0.073242 | -0.045776 | 60.5347 | 0.27466 | -0.19684 | 0.39368 | -0.07782 | 123.3078 | 123.3627 | 60.6537 | 123.4177 | 123.7106 | 123.5367 | 123.4451 | 123.4177 | -123.6099 | -123.4634 | 123.0972 | 123.2986 | 61.4868 | 59.1568
385.9844 | 123.5184 | -61.5005 | 61.8576 | 0.0177 | -0.0012647 | -0.00032469 | 0.0030868 | 0.0033218 | 0.001066 | 0.00054264 | -0.015564 | -0.00072642 | 0.035609 | 0.033958 | -0.0010787 | -0.00035469 | 0.0015659 | 0.004578 | 61.9446 | -61.7615 | 61.6425 | 61.6013 | -61.7569 | 0.15106 | -2.2339 | 61.9354 | -61.5967 | 61.8668 | -0.87433 | -61.6058 | -61.1618 | -0.26093 | 0.086975 | -0.21515 | 123.1018 | 61.6516 | -0.25635 | 61.9125 | 0.004578 | -0.096131 | 0.07782 | 0.009155 | 60.6262 | 0.33875 | -0.10529 | 0.43488 | -0.009155 | 123.3627 | 123.4039 | 60.7224 | 123.4634 | 123.7061 | 123.5321 | 123.4451 | 123.436 | -123.6191 | -123.4543 | 123.143 | 123.3673 | 61.5051 | 59.2667
386.9844 | 123.3444 | -61.5738 | 61.7523 | -0.020447 | -0.0010511 | -0.00096549 | 0.001805 | -0.00052344 | -0.00085663 | 0.001397 | -0.030823 | 0.00055538 | 0.033473 | 0.032676 | -0.00043794 | -0.00056829 | 0.0022067 | -0.07782 | 61.8896 | -61.7889 | 61.5509 | 61.4777 | -61.8988 | 0.045776 | -2.4261 | 61.8896 | -61.6425 | 61.7935 | -0.95673 | -61.7111 | -61.1984 | -0.21515 | 0.13733 | -0.20142 | 123.0515 | 61.6196 | -0.32501 | 61.8347 | -0.10986 | -0.068664 | 0.13733 | 0.041199 | 60.6171 | 0.37537 | -0.13733 | 0.44403 | -0.068665 | 123.2666 | 123.3398 | 60.6857 | 123.436 | 123.6786 | 123.5321 | 123.4634 | 123.4634 | -123.5413 | -123.3948 | 123.1247 | 123.3673 | 61.496 | 59.1476
387.9844 | 123.5046 | -61.5051 | 61.8668 | -0.020447 | 0.00044428 | -0.00096549 | 0.0015914 | 0.00033116 | 0.0014932 | -0.00031196 | -0.0094605 | -0.00051262 | 0.033686 | 0.036521 | -0.0021469 | 0.00092711 | 0.0028477 | 0.022888 | 61.9446 | -61.7615 | 61.6562 | 61.6104 | -61.7294 | 0.1831 | -2.2202 | 61.8942 | -61.5738 | 61.8759 | -0.85602 | -61.6196 | -61.1481 | -0.25635 | 0.07782 | -0.21057 | 123.1155 | 61.6882 | -0.2243 | 61.9446 | 0.032044 | -0.068665 | 0.027466 | 0.009156 | 60.6491 | 0.35706 | -0.11444 | 0.42572 | -0.045776 | 123.3719 | 123.4177 | 60.7178 | 123.4497 | 123.7061 | 123.468 | 123.4497 | 123.3994 | -123.6282 | -123.4406 | 123.1613 | 123.381 | 61.528 | 59.285
388.9844 | 123.4863 | -61.5326 | 61.8439 | 0.0177 | -0.00041012 | -0.00032469 | 0.0015914 | -0.00052344 | 0.0012796 | -0.00052556 | -0.036926 | 0.00012818 | 0.032618 | 0.030753 | -0.00086514 | 7.2706e-05 | 0.0013523 | -0.032043 | 61.9492 | -61.7844 | 61.615 | 61.5555 | -61.7935 | 0.086975 | -2.3209 | 61.9354 | -61.5784 | 61.8439 | -0.91553 | -61.6562 | -61.2076 | -0.25177 | 0.10529 | -0.22888 | 123.0881 | 61.6196 | -0.26093 | 61.8713 | -0.009155 | -0.045776 | 0.091553 | 0 | 60.6171 | 0.32501 | -0.1236 | 0.37079 | -0.07782 | 123.3398 | 123.3994 | 60.6628 | 123.4222 | 123.7335 | 123.5138 | 123.4818 | 123.468 | -123.6282 | -123.4222 | 123.1476 | 123.3765 | 61.5005 | 59.2117
389.9844 | 123.5229 | -61.496 | 61.8668 | -0.020447 | -0.00083732 | -0.0018201 | 0.0033004 | -0.00052344 | 0.0017068 | 0.0026788 | -0.021668 | -0.00029902 | 0.032405 | 0.029471 | -0.0017197 | -0.00056829 | -0.00078395 | 0 | 61.9217 | -61.7889 | 61.6425 | 61.6196 | -61.7477 | 0.14191 | -2.2614 | 61.9171 | -61.5875 | 61.8713 | -0.87891 | -61.6104 | -61.1435 | -0.29297 | 0.054932 | -0.2243 | 123.1155 | 61.6379 | -0.25177 | 61.9308 | 0.041198 | -0.091552 | 0.050354 | 0.004578 | 60.6171 | 0.35248 | -0.11444 | 0.44403 | -0.022889 | 123.4085 | 123.4314 | 60.7086 | 123.4589 | 123.7106 | 123.5046 | 123.4177 | 123.4131 | -123.6557 | -123.4543 | 123.1384 | 123.3673 | 61.496 | 59.2346
390.9844 | 123.436 | -61.528 | 61.8942 | -0.005188 | 0.0023669 | 0.00074331 | 0.00073702 | -0.00052344 | 0.001066 | 0.00032904 | -0.036926 | 0.00098258 | 0.033473 | 0.033744 | 0.00041666 | -0.00056829 | -0.0014249 | -0.064087 | 61.9354 | -61.7752 | 61.5967 | 61.5326 | -61.8118 | 0.050354 | -2.4078 | 61.94 | -61.5921 | 61.8027 | -0.95215 | -61.7111 | -61.2442 | -0.24719 | 0.041199 | -0.29755 | 123.0606 | 61.5784 | -0.28381 | 61.8256 | -0.036621 | -0.064087 | 0.045776 | -0.091553 | 60.5759 | 0.28381 | -0.18311 | 0.3479 | -0.11902 | 123.3078 | 123.3719 | 60.64 | 123.3948 | 123.7106 | 123.5321 | 123.4634 | 123.468 | -123.6694 | -123.4863 | 123.1247 | 123.3307 | 61.4639 | 59.1202
391.9844 | 123.555 | -61.4868 | 61.8439 | -0.035705 | 0.0025805 | 0.0015979 | -0.00011758 | 0.00097196 | 0.00042517 | -0.0024482 | -0.015564 | -8.5416e-05 | 0.032618 | 0.033317 | -0.0010787 | -0.00056829 | 0.0011387 | -0.009155 | 61.9492 | -61.7615 | 61.6516 | 61.6241 | -61.7294 | 0.14648 | -2.211 | 61.9217 | -61.5692 | 61.8805 | -0.83771 | -61.5875 | -61.1389 | -0.27466 | 0.10529 | -0.19226 | 123.111 | 61.6333 | -0.24262 | 61.908 | 0.032044 | -0.082398 | 0.07782 | 0.036621 | 60.6491 | 0.3479 | -0.10071 | 0.4303 | -0.01831 | 123.3856 | 123.4131 | 60.7315 | 123.4497 | 123.7106 | 123.4909 | 123.436 | 123.4085 | -123.6053 | -123.4131 | 123.1384 | 123.3673 | 61.4777 | 59.2758
392.9844 | 123.4772 | -61.5097 | 61.8805 | -0.005188 | 0.0012989 | 0.00074331 | 0.001805 | 0.0013992 | 0.00021157 | 0.0011834 | -0.030823 | 0.00055538 | 0.034113 | 0.03588 | -0.0015059 | 0.00028631 | -0.00035675 | -0.091553 | 61.9537 | -61.7889 | 61.615 | 61.5738 | -61.8027 | 0.064087 | -2.3987 | 61.9125 | -61.5692 | 61.8484 | -0.94299 | -61.7111 | -61.2167 | -0.27923 | 0.073242 | -0.2655 | 123.0835 | 61.5738 | -0.29297 | 61.853 | -0.013733 | -0.059509 | 0.032044 | -0.032043 | 60.5667 | 0.29297 | -0.20142 | 0.35248 | -0.14191 | 123.3627 | 123.4039 | 60.6262 | 123.4177 | 123.7427 | 123.4818 | 123.4634 | 123.4222 | -123.6694 | -123.4497 | 123.1247 | 123.3582 | 61.4182 | 59.111
393.9844 | 123.5138 | -61.5051 | 61.8484 | -0.005188 | -0.00019652 | -0.00096549 | -0.00075838 | 0.0031082 | 0.0053384 | -0.0033026 | -0.015564 | 0.0018372 | 0.036677 | 0.032462 | -0.00086514 | 7.2706e-05 | -0.0022793 | -0.036621 | 61.9308 | -61.7432 | 61.5692 | 61.6608 | -61.7294 | 0.1236 | -2.3117 | 61.94 | -61.5738 | 61.8896 | -0.8606 | -61.6058 | -61.1435 | -0.23804 | 0.082397 | -0.27924 | 123.1659 | 61.6287 | -0.2243 | 61.8668 | 0.013733 | -0.068665 | 0.091552 | 0.041198 | 60.6445 | 0.36163 | -0.10071 | 0.4303 | -0.032043 | 123.4039 | 123.3124 | 60.7132 | 123.4634 | 123.674 | 123.5138 | 123.436 | 123.4451 | -123.5916 | -123.4222 | 123.0743 | 123.3948 | 61.4685 | 59.1934
394.9844 | 123.4634 | -61.5097 | 61.853 | -0.020447 | 0.00023068 | 0.00095711 | 0.0020188 | -0.0011642 | 0.00042517 | 0.003106 | -0.039978 | -0.0015808 | 0.035395 | 0.036948 | -0.00022434 | 0.00071351 | 0.00071145 | -0.1236 | 61.9492 | -61.7706 | 61.5738 | 61.496 | -61.853 | 0.018311 | -2.5269 | 61.9308 | -61.615 | 61.7844 | -0.92926 | -61.6837 | -61.1938 | -0.26093 | 0.096131 | -0.27923 | 123.0057 | 61.528 | -0.34332 | 61.7889 | -0.082397 | -0.10529 | 0.07782 | -0.068664 | 60.5804 | 0.31586 | -0.17395 | 0.42114 | -0.068665 | 123.2666 | 123.3444 | 60.6857 | 123.3994 | 123.7198 | 123.5458 | 123.4589 | 123.4406 | -123.6237 | -123.468 | 123.0835 | 123.2941 | 61.3861 | 58.9828
395.9844 | 123.5092 | -61.4639 | 61.8851 | -0.012817 | -0.0012647 | 0.00010251 | -0.00033118 | -0.0020188 | 0.00042517 | -0.0015936 | -0.0094605 | -8.5416e-05 | 0.035609 | 0.039725 | -0.00065154 | -0.00099549 | -0.0018521 | -0.036621 | 61.9629 | -61.734 | 61.6699 | 61.6241 | -61.7065 | 0.14648 | -2.33 | 61.9446 | -61.5738 | 61.8942 | -0.82855 | -61.5784 | -61.1252 | -0.27008 | 0.07782 | -0.21515 | 123.0881 | 61.6104 | -0.24262 | 61.8805 | 0.027466 | -0.10986 | 0.059509 | 0.009155 | 60.6354 | 0.33875 | -0.11444 | 0.44861 | -0.004577 | 123.3582 | 123.4039 | 60.7452 | 123.468 | 123.6969 | 123.5184 | 123.4268 | 123.4085 | -123.6191 | -123.4589 | 123.1338 | 123.3582 | 61.4273 | 59.1339
396.9844 | 123.4451 | -61.5143 | 61.8713 | 0.02533 | 0.00065788 | 0.00095711 | 0.0013778 | 0.0011856 | 0.00063877 | 0.0024652 | -0.012512 | 0.00055538 | 0.034327 | 0.033744 | -0.00086514 | -0.00014089 | 0.0034885 | -0.09613 | 61.9492 | -61.7477 | 61.615 | 61.5601 | -61.8073 | 0.041199 | -2.4994 | 61.9537 | -61.5875 | 61.8301 | -0.92926 | -61.6791 | -61.2076 | -0.23346 | 0.07782 | -0.25635 | 123.0743 | 61.5555 | -0.29297 | 61.7889 | -0.059509 | -0.073242 | 0.082397 | -0.041199 | 60.585 | 0.3067 | -0.16479 | 0.37994 | -0.091553 | 123.3078 | 123.3627 | 60.6583 | 123.4177 | 123.6969 | 123.5413 | 123.4634 | 123.468 | -123.6191 | -123.4589 | 123.1293 | 123.3444 | 61.4182 | 59.0149
397.9844 | 123.5092 | -61.4685 | 61.8668 | 0.0177 | 0.0021533 | 0.0024523 | 0.0022324 | -0.0015914 | -0.00021583 | 0.0039606 | 0.0027465 | 0.0016236 | 0.035609 | 0.030326 | -0.00065154 | -0.00056829 | 0.0017795 | -0.027466 | 61.972 | -61.7203 | 61.6745 | 61.6425 | -61.7203 | 0.12817 | -2.3758 | 61.9354 | -61.5509 | 61.9034 | -0.84228 | -61.5875 | -61.1298 | -0.25177 | 0.10529 | -0.19226 | 123.111 | 61.5967 | -0.25177 | 61.8484 | 0 | -0.082397 | 0.068665 | 0.036621 | 60.6262 | 0.33874 | -0.11902 | 0.42114 | -0.036621 | 123.3627 | 123.3948 | 60.7086 | 123.4543 | 123.6923 | 123.4863 | 123.4406 | 123.4039 | -123.587 | -123.4177 | 123.143 | 123.3719 | 61.441 | 59.0927
398.9844 | 123.4818 | -61.5051 | 61.8713 | -0.050964 | -0.00083732 | 0.0013843 | 0.002446 | 0.00033116 | 0.001066 | 0.0041742 | -0.04303 | 0.002478 | 0.035182 | 0.036307 | -0.0012923 | -0.00014089 | 0.0015659 | -0.082397 | 61.9492 | -61.7477 | 61.6333 | 61.5921 | -61.7798 | 0.064087 | -2.4994 | 61.9583 | -61.5875 | 61.8668 | -0.88806 | -61.6241 | -61.1755 | -0.24262 | 0.07782 | -0.23804 | 123.0972 | 61.5692 | -0.27466 | 61.8118 | -0.032043 | -0.082397 | 0.086975 | -0.004578 | 60.6171 | 0.32959 | -0.11902 | 0.41199 | -0.036622 | 123.3398 | 123.381 | 60.6995 | 123.4543 | 123.6969 | 123.5458 | 123.4543 | 123.4634 | -123.6191 | -123.4589 | 123.1384 | 123.3719 | 61.4227 | 59.0057
399.9844 | 123.5321 | -61.4548 | 61.8896 | 0.040589 | 1.7082e-05 | -0.00075189 | -0.00011758 | 0.0031082 | 0.0021342 | -0.00138 | -0.0033569 | 0.00034178 | 0.033045 | 0.030967 | 0.00020286 | 0.00092711 | -0.00057035 | -0.054932 | 61.9949 | -61.7203 | 61.6974 | 61.6425 | -61.7111 | 0.15564 | -2.4124 | 61.9492 | -61.5097 | 61.9171 | -0.8194 | -61.5738 | -61.1298 | -0.2655 | 0.10529 | -0.19226 | 123.0972 | 61.6104 | -0.25635 | 61.8759 | 0.009155 | -0.054932 | 0.05951 | 0.027466 | 60.6354 | 0.32501 | -0.11902 | 0.37994 | -0.064087 | 123.3627 | 123.4177 | 60.6903 | 123.4268 | 123.7152 | 123.4589 | 123.4497 | 123.4039 | -123.6099 | -123.3994 | 123.1522 | 123.3719 | 61.3998 | 59.0424
400.9844 | 123.587 | -61.4227 | 61.8484 | -0.035705 | 0.00044428 | 0.00095711 | 0.00052342 | 0.00054476 | -0.001711 | 0.0011834 | 0.0088501 | -0.0011536 | 0.035609 | 0.034812 | -0.0021469 | -0.00035469 | -0.0014249 | -0.14191 | 61.9171 | -61.734 | 61.7065 | 61.6425 | -61.6745 | 0.10529 | -2.6001 | 61.8851 | -61.5646 | 61.9446 | -0.76904 | -61.5234 | -61.0657 | -0.31128 | 0.068664 | -0.14191 | 123.0652 | 61.528 | -0.25177 | 61.8393 | 0.059509 | -0.14191 | 0.036621 | 0.09613 | 60.6537 | 0.35705 | -0.10071 | 0.49896 | 0.041199 | 123.3765 | 123.4406 | 60.7956 | 123.5092 | 123.6511 | 123.4497 | 123.3398 | 123.3078 | -123.5825 | -123.4131 | 123.1293 | 123.3673 | 61.2808 | 58.8226
401.9844 | 123.5367 | -61.4548 | 61.9537 | 0.048218 | 0.00087168 | -0.00032469 | 0.00073702 | -0.0020188 | -2.232e-06 | -0.00031196 | 0.014954 | 0.00098258 | 0.034754 | 0.037589 | -0.0010787 | -0.00035469 | -0.0020657 | -0.086975 | 61.9949 | -61.7111 | 61.6974 | 61.6287 | -61.6882 | 0.12817 | -2.5223 | 61.9858 | -61.5326 | 61.9308 | -0.7782 | -61.5372 | -61.0886 | -0.25635 | 0.041199 | -0.25635 | 123.0835 | 61.5829 | -0.23346 | 61.8393 | 0.022889 | -0.07782 | 0.032044 | -0.022888 | 60.6766 | 0.36621 | -0.082397 | 0.44403 | -0.004577 | 123.3398 | 123.4085 | 60.7544 | 123.4634 | 123.7061 | 123.5184 | 123.4497 | 123.4406 | -123.6649 | -123.4863 | 123.1522 | 123.3856 | 61.3678 | 58.9325
403 | 123.6099 | -61.3907 | 61.8668 | -0.020447 | 0.0010853 | 0.0037341 | 9.6222e-05 | 0.0013992 | 0.0023478 | -0.00031196 | 0.0027465 | 0.00098258 | 0.033045 | 0.032035 | -0.00022434 | 0.0011407 | -0.00014315 | -0.091553 | 61.9583 | -61.6837 | 61.7661 | 61.702 | -61.6608 | 0.086975 | -2.5818 | 61.8988 | -61.4868 | 62.0041 | -0.73242 | -61.4822 | -61.0153 | -0.29297 | 0.091553 | -0.10071 | 123.0927 | 61.4777 | -0.27008 | 61.7706 | 0.022888 | -0.09613 | 0.032044 | 0.13733 | 60.6583 | 0.37537 | -0.091553 | 0.4715 | 0.004577 | 123.3856 | 123.4497 | 60.7544 | 123.4909 | 123.642 | 123.3856 | 123.349 | 123.2895 | -123.5504 | -123.3536 | 123.1567 | 123.3948 | 61.2991 | 58.8089
403.9844 | 123.4955 | -61.3998 | 61.9629 | 0.02533 | 0.00044428 | -0.0011793 | 0.00095062 | -0.0026596 | 0.0017068 | 0.002038 | -0.030823 | 0.00034178 | 0.034327 | 0.029685 | -0.0053513 | 0.0017817 | 0.0011387 | -0.059509 | 62.0453 | -61.6608 | 61.7386 | 61.6928 | -61.6516 | 0.12817 | -2.5497 | 62.0087 | -61.4685 | 61.908 | -0.73242 | -61.5372 | -61.0657 | -0.26093 | 0.082397 | -0.22431 | 123.0927 | 61.528 | -0.25177 | 61.7889 | 0.009156 | -0.068665 | 0.045776 | -0.054932 | 60.6674 | 0.33417 | -0.13733 | 0.40283 | -0.068664 | 123.3536 | 123.3994 | 60.7361 | 123.3765 | 123.7061 | 123.4772 | 123.4451 | 123.4085 | -123.6237 | -123.4314 | 123.1384 | 123.3078 | 61.3403 | 58.8501
404.9844 | 123.4543 | -61.4136 | 61.9492 | 0.0177 | 0.0019397 | 0.00074331 | 0.0022324 | 0.0033218 | -0.001711 | -0.00073916 | -0.018616 | 0.0016236 | 0.033259 | 0.033103 | -0.0017197 | 0.00049991 | -0.00057035 | -0.14191 | 62.027 | -61.6837 | 61.7157 | 61.6379 | -61.702 | 0.018311 | -2.774 | 62.0224 | -61.4914 | 61.8988 | -0.85144 | -61.5967 | -61.116 | -0.27008 | 0.07782 | -0.23346 | 123.0515 | 61.4319 | -0.28839 | 61.702 | -0.01831 | -0.07782 | 0.073242 | -0.050354 | 60.5621 | 0.29755 | -0.18311 | 0.37537 | -0.10529 | 123.3215 | 123.3994 | 60.64 | 123.3902 | 123.7106 | 123.5138 | 123.4406 | 123.436 | -123.6328 | -123.4406 | 123.1293 | 123.3124 | 61.2717 | 58.6395
406 | 123.5687 | -61.3129 | 61.9766 | 0.010071 | 0.0017261 | -0.00075189 | 0.00030982 | 0.0037492 | -2.232e-06 | -0.002021 | 0.051575 | 0.0011964 | 0.035395 | 0.029471 | -0.0025741 | -0.0031317 | 0.0015659 | -0.027466 | 62.0773 | -61.5921 | 61.9263 | 61.7889 | -61.6287 | 0.21515 | -2.5269 | 62.0087 | -61.4136 | 62.0636 | -0.63171 | -61.3541 | -60.9558 | -0.27924 | 0.10071 | -0.050354 | 123.1018 | 61.528 | -0.31586 | 61.8073 | -0.036621 | -0.10071 | 0.032043 | 0.086975 | 60.6812 | 0.35706 | -0.041199 | 0.45776 | 0.059509 | 123.381 | 123.5184 | 60.7819 | 123.4772 | 123.6694 | 123.4222 | 123.3902 | 123.3215 | -123.5687 | -123.3902 | 123.2391 | 123.3765 | 61.2854 | 58.786
407.0312 | 123.4589 | -61.3907 | 62.0041 | -0.020447 | 1.7082e-05 | -0.00096549 | 0.0013778 | 0.0024674 | -0.00021583 | 0.0026788 | -0.052185 | -0.00029902 | 0.033045 | 0.039512 | -0.0027877 | 0.0019953 | -0.00057035 | -0.13275 | 62.0682 | -61.6196 | 61.7477 | 61.6882 | -61.6653 | 0.050354 | -2.7695 | 62.0911 | -61.4365 | 61.9812 | -0.77362 | -61.5097 | -61.0519 | -0.22888 | 0.064087 | -0.25635 | 123.0789 | 61.441 | -0.27466 | 61.6699 | -0.045776 | -0.045776 | 0.086975 | -0.022888 | 60.6171 | 0.33875 | -0.11902 | 0.38452 | -0.073243 | 123.3078 | 123.3673 | 60.6628 | 123.4177 | 123.6877 | 123.5275 | 123.4589 | 123.4818 | -123.6237 | -123.4406 | 123.1384 | 123.3719 | 61.2579 | 58.6212
408.0625 | 123.5962 | -61.3678 | 62.0361 | 0.010071 | 0.0030079 | 0.0022387 | 0.0022324 | 0.0033218 | -0.00042943 | -0.00095276 | -0.073547 | -0.0013672 | 0.033259 | 0.035453 | -0.00086514 | -0.0020637 | -0.0022793 | -0.20142 | 62.0865 | -61.6425 | 61.7706 | 61.6608 | -61.6928 | -0.009155 | -2.8564 | 62.0956 | -61.441 | 61.9904 | -0.74616 | -61.8347 | -61.2488 | -0.27466 | 0.050354 | -0.2655 | 123.0286 | 61.3586 | -0.32501 | 61.6333 | -0.050354 | -0.073242 | 0.059509 | -0.045777 | 60.6216 | 0.11902 | -0.46692 | 0.19226 | -0.39368 | 123.3032 | 123.4131 | 60.6949 | 123.4314 | 123.7289 | 123.5367 | 123.4543 | 123.4634 | -123.6786 | -123.4772 | 123.1384 | 123.3582 | 61.1664 | 58.5114
408.9844 | 123.468 | -61.3312 | 62.0132 | 0.02533 | 0.0010853 | 0.0015979 | 0.00095062 | 0.0022538 | 0.0019204 | -0.00095276 | -0.046082 | -8.5416e-05 | 0.0339 | 0.028403 | 0.0012711 | 7.2706e-05 | 0.00049765 | -0.20599 | 62.114 | -61.6196 | 61.7432 | 61.6333 | -61.6791 | 0.004578 | -2.8931 | 62.1002 | -61.4273 | 61.9858 | -0.74158 | -61.5234 | -61.0336 | -0.28839 | 0.10071 | -0.27008 | 122.9645 | 61.3358 | -0.3479 | 61.6241 | -0.059509 | -0.09613 | 0.086975 | -0.027466 | 60.5896 | 0.29755 | -0.19226 | 0.39368 | -0.09613 | 123.2529 | 123.3627 | 60.6857 | 123.4131 | 123.7335 | 123.5275 | 123.4451 | 123.4314 | -123.6328 | -123.4406 | 123.0743 | 123.317 | 61.1252 | 58.4381
410.0469 | 123.4818 | -61.3037 | 62.059 | 0.0024415 | 0.00087168 | -0.00053829 | 0.0013778 | -0.0022324 | 0.0017068 | 0.00011544 | 0.14923 | -0.00029902 | 0.035182 | 0.035026 | -0.00022434 | 0.00049991 | 0.0011387 | -0.13733 | 62.1323 | -61.5509 | 61.8256 | 61.7432 | -61.5646 | 0.11902 | -2.8656 | 62.1643 | -61.3953 | 62.0361 | -0.71869 | -61.3678 | -60.9558 | -0.24719 | 0.073242 | -0.23346 | 123.0469 | 61.4227 | -0.26093 | 61.6699 | -0.013733 | -0.091553 | 0.10529 | -0.022888 | 60.585 | 0.3479 | -0.064087 | 0.43945 | 0.027466 | 123.2941 | 123.3765 | 60.6766 | 123.4314 | 123.6832 | 123.5596 | 123.436 | 123.468 | -123.6099 | -123.4543 | 123.1293 | 123.3398 | 61.1664 | 58.4381
410.9844 | 123.468 | -61.3358 | 62.0407 | -0.058594 | 0.00065788 | 0.00095711 | 0.0013778 | -0.0020188 | -0.00042943 | 0.003106 | -0.23529 | 0.00012818 | 0.032618 | 0.027549 | 0.00020286 | 0.00049991 | 0.0017795 | -0.21515 | 62.146 | -61.5967 | 61.7752 | 61.702 | -61.6333 | -0.004578 | -2.742 | 62.0819 | -61.4182 | 62.0041 | -0.69122 | -61.5234 | -61.0428 | -0.26093 | 0.10529 | -0.2655 | 123.0377 | 61.3312 | -0.29755 | 61.5921 | -0.036621 | -0.082398 | 0.041199 | -0.036621 | 60.6445 | 0.29297 | -0.18768 | 0.37537 | -0.10529 | 123.2986 | 123.3719 | 60.7269 | 123.4222 | 123.7427 | 123.5001 | 123.4818 | 123.4177 | -123.6374 | -123.4589 | 123.111 | 123.3398 | 61.1206 | 58.5938
411.9844 | 123.4818 | -61.2991 | 62.0544 | 0.032959 | 0.0012989 | -0.00053829 | 0.003514 | -0.0011642 | 0.0012796 | 0.0039606 | -0.046082 | 0.00141 | 0.034754 | 0.036948 | -0.0015059 | -0.0020637 | 0.0019931 | -0.13275 | 62.1231 | -61.5509 | 61.8668 | 61.7981 | -61.5372 | 0.10529 | -2.7512 | 62.1185 | -61.3678 | 62.0865 | -0.6958 | -61.4227 | -61.0336 | -0.25177 | 0.068665 | -0.18768 | 123.0972 | 61.4044 | -0.23804 | 61.6562 | 0.013733 | -0.068665 | 0.064087 | 0.032044 | 60.6033 | 0.2655 | -0.1236 | 0.33417 | -0.054931 | 123.349 | 123.4177 | 60.672 | 123.4543 | 123.674 | 123.4863 | 123.4222 | 123.4177 | -123.6053 | -123.4222 | 123.1659 | 123.3856 | 61.1664 | 58.548
413.0469 | 123.4772 | -61.2671 | 62.0865 | 0.0024415 | 0.0021533 | -0.00032469 | 0.0011642 | 0.0024674 | -0.0012838 | -0.00095276 | -0.030823 | -0.00051262 | 0.036036 | 0.029471 | -0.0010787 | 0.00071351 | -0.00099755 | -0.13275 | 62.1552 | -61.5555 | 61.8622 | 61.8164 | -61.5372 | 0.07782 | -2.7924 | 62.1277 | -61.3861 | 62.0819 | -0.63171 | -61.3907 | -60.9375 | -0.28839 | 0.068664 | -0.2243 | 123.0835 | 61.3449 | -0.27008 | 61.6333 | 0.018311 | -0.11902 | 0.041199 | -0.004578 | 60.6354 | 0.32959 | -0.1236 | 0.44861 | -0.004578 | 123.3719 | 123.4177 | 60.7544 | 123.468 | 123.7106 | 123.5138 | 123.4222 | 123.3948 | -123.642 | -123.4726 | 123.1293 | 123.349 | 61.1343 | 58.4747
413.9844 | 123.4818 | -61.2808 | 62.0773 | -0.005188 | -0.00041012 | -0.00075189 | 0.00030982 | 0.00011756 | -2.232e-06 | 0.0026788 | -0.033875 | 0.00141 | 0.03625 | 0.034171 | -0.0027877 | 7.2706e-05 | -0.00035675 | -0.21973 | 62.114 | -61.5646 | 61.8576 | 61.8164 | -61.5372 | 0.082397 | -2.8519 | 62.1414 | -61.3678 | 62.0865 | -0.68665 | -61.4182 | -60.9512 | -0.28381 | 0.036621 | -0.21973 | 123.0972 | 61.3632 | -0.25635 | 61.647 | 0.027466 | -0.086975 | 0.064086 | 0.009155 | 60.5942 | 0.32959 | -0.13733 | 0.41656 | -0.050354 | 123.381 | 123.4222 | 60.6812 | 123.4543 | 123.6786 | 123.5092 | 123.3948 | 123.4222 | -123.642 | -123.4451 | 123.1384 | 123.3673 | 61.0611 | 58.429
414.9844 | 123.5458 | -61.2762 | 62.027 | -0.035705 | 0.0030079 | -0.00075189 | 0.00030982 | -0.003514 | -0.0012838 | 0.0018242 | 0.042419 | 0.00012818 | 0.032405 | 0.028403 | 0.00084386 | -0.0020637 | -0.00099755 | -0.19684 | 62.1231 | -61.5417 | 61.8668 | 61.8118 | -61.5417 | 0.050354 | -2.9526 | 62.0636 | -61.3678 | 62.0956 | -0.62714 | -61.3541 | -60.9146 | -0.2655 | 0.09613 | -0.16022 | 123.0881 | 61.3266 | -0.2655 | 61.5921 | 0 | -0.091553 | 0.036621 | 0.068664 | 60.6491 | 0.36163 | -0.07782 | 0.45319 | 0.013733 | 123.3536 | 123.4085 | 60.7407 | 123.4634 | 123.6649 | 123.4314 | 123.3994 | 123.3398 | -123.5687 | -123.3948 | 123.143 | 123.3719 | 61.0794 | 58.3237
415.9844 | 123.4772 | -61.2488 | 62.0956 | 0.0024415 | 0.00023068 | 0.00095711 | 0.0015914 | -0.00095064 | -0.002352 | 0.0011834 | -0.021668 | -0.00051262 | 0.0339 | 0.030753 | -0.0019333 | 7.2706e-05 | 0.0015659 | -0.16479 | 62.1826 | -61.5601 | 61.8668 | 61.7798 | -61.5189 | 0.10986 | -2.8793 | 62.178 | -61.3541 | 62.0819 | -0.63629 | -61.3495 | -60.91 | -0.31128 | 0.086975 | -0.22888 | 123.0286 | 61.3586 | -0.27008 | 61.6699 | 0.041199 | -0.10529 | 0.082398 | -0.013733 | 60.6125 | 0.33874 | -0.10071 | 0.44403 | 0.004578 | 123.3398 | 123.4268 | 60.7178 | 123.436 | 123.7427 | 123.5321 | 123.4314 | 123.4268 | -123.6557 | -123.4497 | 123.1155 | 123.3307 | 61.084 | 58.3694
416.9844 | 123.5229 | -61.2762 | 62.0911 | -0.020447 | -0.00019652 | -0.00032469 | 0.00095062 | 0.0028946 | -0.00085663 | 0.0022516 | 0.011902 | -0.0015808 | 0.034541 | 0.036735 | -0.00043794 | 0.00071351 | -0.0018521 | -0.15106 | 62.1689 | -61.5326 | 61.8851 | 61.8073 | -61.5189 | 0.082397 | -2.9114 | 62.1368 | -61.377 | 62.1002 | -0.64087 | -61.3815 | -60.9467 | -0.25635 | 0.07782 | -0.20599 | 123.0835 | 61.3586 | -0.24261 | 61.615 | 0.013733 | -0.10071 | 0.045777 | 0.009156 | 60.6354 | 0.32959 | -0.10529 | 0.4303 | -0.004578 | 123.3398 | 123.4177 | 60.7361 | 123.4772 | 123.7015 | 123.5138 | 123.4451 | 123.4131 | -123.6237 | -123.468 | 123.1613 | 123.3765 | 61.1252 | 58.3649
417.9844 | 123.5138 | -61.2762 | 62.0819 | -0.005188 | 0.0036487 | 0.0011707 | 0.0015914 | -0.001805 | -0.0014974 | -0.0026618 | -0.04303 | -0.00094002 | 0.034541 | 0.036521 | -0.0040695 | 0.00092711 | -0.0035611 | -0.16022 | 62.1872 | -61.528 | 61.8759 | 61.8164 | -61.5143 | 0.068665 | -2.9297 | 62.1552 | -61.3495 | 62.1048 | -0.63629 | -61.3815 | -60.9329 | -0.25177 | 0.10529 | -0.20599 | 123.0927 | 61.3449 | -0.23804 | 61.5967 | 0.013733 | -0.073242 | 0.073242 | 0.022888 | 60.64 | 0.34332 | -0.10529 | 0.41657 | -0.032044 | 123.3444 | 123.4039 | 60.7132 | 123.4543 | 123.7152 | 123.5046 | 123.4634 | 123.4314 | -123.6099 | -123.4314 | 123.1522 | 123.381 | 61.116 | 58.3466
419.0156 | 123.5962 | -61.2213 | 62.059 | 0.02533 | 0.0012989 | -0.0016065 | -0.0011856 | -0.00030984 | -2.232e-06 | 0.002038 | 0.097351 | 0.00012818 | 0.0339 | 0.037589 | -0.00043794 | -0.0022773 | 0.00071145 | -0.1831 | 62.1597 | -61.4868 | 61.9492 | 61.908 | -61.4319 | 0.16022 | -2.8885 | 62.114 | -61.3129 | 62.1918 | -0.50812 | -61.2259 | -60.8185 | -0.2655 | 0.10071 | -0.10986 | 123.1293 | 61.3815 | -0.21057 | 61.647 | 0.054931 | -0.091553 | 0.054932 | 0.13275 | 60.7132 | 0.40283 | -0.004578 | 0.49439 | 0.086975 | 123.3948 | 123.436 | 60.8047 | 123.5046 | 123.6465 | 123.4268 | 123.381 | 123.3353 | -123.5458 | -123.3719 | 123.1705 | 123.4131 | 61.0382 | 58.3328
419.9844 | 123.5046 | -61.2442 | 62.1002 | 0.010071 | -0.00062372 | 0.0013843 | -0.00011758 | -0.00095064 | 0.002775 | -0.0015936 | -0.024719 | -0.00051262 | 0.032191 | 0.035667 | -0.0021469 | -0.00078189 | -0.0037747 | -0.1831 | 62.1643 | -61.5326 | 61.8759 | 61.8164 | -61.4868 | 0.10529 | -2.9846 | 62.1826 | -61.3358 | 62.1185 | -0.59509 | -61.3495 | -60.9146 | -0.28839 | 0.064087 | -0.2243 | 123.0606 | 61.3495 | -0.24261 | 61.6379 | 0.045777 | -0.091552 | 0.082397 | 0.01831 | 60.6491 | 0.32959 | -0.10529 | 0.42114 | -0.013733 | 123.349 | 123.4085 | 60.7407 | 123.4543 | 123.6969 | 123.5184 | 123.4085 | 123.4268 | -123.6328 | -123.436 | 123.1201 | 123.3627 | 61.0611 | 58.2596
421.0312 | 123.5138 | -61.2488 | 62.1185 | 0.0177 | -0.00019652 | -0.0016065 | 9.6222e-05 | -0.0011642 | -2.232e-06 | -0.0028754 | 0.048523 | 0.00012818 | 0.035609 | 0.033103 | -0.0017197 | -0.00035469 | -0.0020657 | -0.16479 | 62.1552 | -61.4777 | 61.94 | 61.8942 | -61.4319 | 0.16479 | -2.9526 | 62.1368 | -61.3266 | 62.1277 | -0.57678 | -61.3266 | -60.8826 | -0.22888 | 0.036621 | -0.17853 | 123.143 | 61.4136 | -0.18311 | 61.6425 | 0.045776 | -0.07782 | 0.018311 | 0.009156 | 60.672 | 0.36621 | -0.07782 | 0.44403 | 0 | 123.3719 | 123.4177 | 60.7498 | 123.4543 | 123.6328 | 123.4634 | 123.4039 | 123.3856 | -123.5962 | -123.4451 | 123.1888 | 123.3765 | 61.084 | 58.2962
421.9844 | 123.4863 | -61.2762 | 62.0865 | -0.020447 | 1.7082e-05 | 0.00010251 | 9.6222e-05 | 0.0011856 | 0.0014932 | -0.00073916 | -0.055237 | 0.00012818 | 0.032832 | 0.031394 | -0.00022434 | -0.00099549 | -0.00057035 | -0.20599 | 62.1643 | -61.5189 | 61.8759 | 61.8256 | -61.5051 | 0.045776 | -3.0487 | 62.1597 | -61.3312 | 62.1002 | -0.63629 | -61.3907 | -60.9467 | -0.24261 | 0.07782 | -0.21057 | 123.1018 | 61.322 | -0.22888 | 61.5646 | 0.013733 | -0.054932 | 0.073242 | 0.013733 | 60.64 | 0.32959 | -0.11444 | 0.38452 | -0.059509 | 123.3444 | 123.3948 | 60.6949 | 123.4314 | 123.6832 | 123.4909 | 123.4406 | 123.436 | -123.6053 | -123.4177 | 123.1522 | 123.3765 | 61.0703 | 58.2275
422.9844 | 123.4955 | -61.2625 | 62.1185 | -0.035705 | 0.00023068 | 0.00052971 | 0.0022324 | 0.0016128 | -0.0021384 | 0.00075624 | -0.04303 | -0.00029902 | 0.036677 | 0.041007 | -0.0012923 | -0.0018499 | -0.00078395 | -0.2655 | 62.1597 | -61.5326 | 61.8576 | 61.7752 | -61.5829 | -0.009155 | -3.186 | 62.1643 | -61.3632 | 62.0819 | -0.68665 | -61.441 | -60.9604 | -0.27008 | 0.041199 | -0.26093 | 123.0377 | 61.2534 | -0.32043 | 61.5234 | -0.050354 | -0.10071 | 0.045777 | -0.036621 | 60.5759 | 0.30212 | -0.17853 | 0.40283 | -0.07782 | 123.3078 | 123.3902 | 60.6766 | 123.4451 | 123.6923 | 123.5275 | 123.4222 | 123.4268 | -123.6511 | -123.4818 | 123.1201 | 123.3444 | 60.997 | 58.0765
423.9844 | 123.5001 | -61.2396 | 62.1002 | 0.040589 | -0.00041012 | -0.00011109 | 0.0011642 | 0.0028946 | -0.00042943 | -0.0035162 | -0.058289 | 0.0022644 | 0.035182 | 0.033958 | -0.0012923 | -0.00035469 | -0.0018521 | -0.20142 | 62.1918 | -61.5097 | 61.908 | 61.8393 | -61.4868 | 0.064087 | -3.0991 | 62.146 | -61.3541 | 62.1323 | -0.60883 | -61.3586 | -60.9192 | -0.27008 | 0.091552 | -0.19226 | 123.0789 | 61.3037 | -0.24719 | 61.5738 | 0.022889 | -0.11444 | 0.045776 | 0.032043 | 60.6308 | 0.32043 | -0.11902 | 0.43488 | -0.004578 | 123.349 | 123.4177 | 60.7452 | 123.4863 | 123.7015 | 123.5001 | 123.4314 | 123.3856 | -123.6099 | -123.4543 | 123.1476 | 123.3719 | 61.0382 | 58.1406
425 | 123.5229 | -61.2305 | 62.027 | -0.050964 | 0.0010853 | -0.0013929 | 0.00030982 | -0.00030984 | 0.00063877 | 0.002038 | 0.024109 | 0.00141 | 0.033045 | 0.032462 | -0.00065154 | 0.00028631 | 0.00049765 | -0.16479 | 62.1185 | -61.5143 | 61.9537 | 61.8576 | -61.5097 | 0.027466 | -3.1906 | 62.1231 | -61.3266 | 62.1552 | -0.57678 | -61.322 | -60.8459 | -0.28381 | 0.091552 | -0.073243 | 123.0881 | 61.2579 | -0.27924 | 61.5417 | 0.004577 | -0.09613 | 0.09613 | 0.12817 | 60.6537 | 0.38452 | -0.091552 | 0.48065 | 0.004578 | 123.3719 | 123.468 | 60.7498 | 123.4818 | 123.6328 | 123.4497 | 123.349 | 123.3536 | -123.5413 | -123.3536 | 123.1842 | 123.3856 | 61.0657 | 58.0399
425.9844 | 123.5001 | -61.2442 | 62.0956 | -0.020447 | 0.0012989 | 0.00095711 | 0.00030982 | 0.00054476 | 0.0017068 | -0.00052556 | -0.055237 | -0.00072642 | 0.030482 | 0.030753 | -0.0025741 | -0.0012091 | -0.0027065 | -0.27466 | 62.2055 | -61.5234 | 61.9034 | 61.8256 | -61.5005 | 0.018311 | -3.3005 | 62.1597 | -61.3449 | 62.1231 | -0.64087 | -61.3632 | -60.9055 | -0.27923 | 0.10986 | -0.19226 | 123.0698 | 61.2625 | -0.25635 | 61.5417 | 0.022888 | -0.10071 | 0.064087 | 0.027466 | 60.6033 | 0.33875 | -0.11902 | 0.43945 | -0.01831 | 123.349 | 123.4268 | 60.704 | 123.468 | 123.7289 | 123.5046 | 123.4497 | 123.4039 | -123.6191 | -123.4406 | 123.1476 | 123.3673 | 60.9695 | 57.9437
427 | 123.5321 | -61.2396 | 62.1231 | 0.02533 | 0.0010853 | -0.0011793 | 0.001805 | 0.0011856 | 0.001066 | -9.8356e-05 | -0.04303 | 0.00034178 | 0.033686 | 0.035667 | -0.0015059 | 0.00049991 | -0.00035675 | -0.3067 | 62.2101 | -61.5005 | 61.9125 | 61.8484 | -61.5005 | 0.027466 | -3.2593 | 62.1918 | -61.3174 | 62.1368 | -0.59052 | -61.3403 | -60.9055 | -0.26093 | 0.086975 | -0.21057 | 123.0881 | 61.2671 | -0.26093 | 61.528 | 0 | -0.07782 | 0.068664 | 0.013733 | 60.6491 | 0.33417 | -0.10071 | 0.41199 | -0.022888 | 123.349 | 123.4131 | 60.7269 | 123.4543 | 123.7106 | 123.5092 | 123.4497 | 123.4314 | -123.6237 | -123.4406 | 123.1522 | 123.3765 | 60.9329 | 57.9803
428.0469 | 123.4909 | -61.2076 | 62.1231 | 0.0177 | 0.0012989 | 0.00010251 | 0.001805 | 0.0054582 | -0.001711 | -0.00138 | -0.049133 | 0.0011964 | 0.034968 | 0.038444 | -0.0021469 | 7.2706e-05 | 0.00028405 | -0.34332 | 62.1826 | -61.5005 | 61.8576 | 61.94 | -61.4914 | -0.018311 | -3.3463 | 62.178 | -61.3174 | 62.1323 | -0.62714 | -61.3632 | -60.8917 | -0.29297 | 0.059509 | -0.2655 | 123.1476 | 61.1893 | -0.28381 | 61.4822 | 0.009155 | -0.10986 | 0.054932 | 0.009155 | 60.5804 | 0.31586 | -0.15564 | 0.42572 | -0.045776 | 123.4406 | 123.3582 | 60.6903 | 123.4497 | 123.6832 | 123.4955 | 123.3902 | 123.3856 | -123.6237 | -123.4406 | 123.0652 | 123.3398 | 60.8643 | 57.8613
428.9844 | 123.5321 | -61.235 | 62.0956 | 0.010071 | 0.0034351 | 0.00095711 | 0.0011642 | -0.002446 | 0.0019204 | -0.00138 | -0.033875 | 0.0026916 | 0.0339 | 0.02819 | -0.00065154 | -0.00014089 | 0.00071145 | -0.48981 | 62.178 | -61.5143 | 61.8713 | 61.7661 | -61.5463 | -0.12817 | -3.5248 | 62.178 | -61.3312 | 62.1414 | -0.60883 | -61.3586 | -60.8917 | -0.27924 | 0.082398 | -0.2243 | 123.0011 | 61.1069 | -0.31128 | 61.3861 | -0.032044 | -0.096131 | 0.082398 | 0.045776 | 60.6262 | 0.34332 | -0.1236 | 0.43945 | -0.027466 | 123.2803 | 123.3856 | 60.7224 | 123.4726 | 123.6923 | 123.5092 | 123.4131 | 123.4131 | -123.6099 | -123.4268 | 123.1064 | 123.3765 | 60.7452 | 57.7103
430.0469 | 123.468 | -61.2122 | 62.1277 | -0.005188 | 0.0010853 | 0.00052971 | 0.00095062 | -0.00030984 | -0.001711 | 0.0026788 | -0.04303 | 0.00141 | 0.032618 | 0.03353 | -0.0023605 | -0.00035469 | 7.0452e-05 | -0.4715 | 62.1918 | -61.4822 | 61.8896 | 61.8164 | -61.5143 | -0.12817 | -3.5385 | 62.2284 | -61.3037 | 62.114 | -0.65002 | -61.3815 | -60.91 | -0.27008 | 0.064086 | -0.23804 | 123.0286 | 61.084 | -0.30212 | 61.3541 | -0.032043 | -0.091553 | 0.10071 | -0.013733 | 60.5621 | 0.30212 | -0.16937 | 0.39368 | -0.07782 | 123.2986 | 123.3719 | 60.6537 | 123.4177 | 123.674 | 123.5321 | 123.4039 | 123.4406 | -123.6099 | -123.4314 | 123.1018 | 123.3261 | 60.7407 | 57.6736
430.9844 | 123.4222 | -61.2259 | 62.1597 | -0.050964 | 0.0012989 | 0.00074331 | 0.0011642 | 0.0022538 | 0.0019204 | 0.0033196 | -0.04303 | 0.00012818 | 0.033045 | 0.030326 | -0.0021469 | -0.00035469 | -0.00035675 | -0.53101 | 62.2192 | -61.5143 | 61.8805 | 61.7889 | -61.496 | -0.16937 | -3.6667 | 62.2101 | -61.3129 | 62.1002 | -0.66376 | -61.4273 | -60.9375 | -0.28839 | 0.059509 | -0.27924 | 123.0148 | 61.0565 | -0.27008 | 61.3449 | 0.01831 | -0.086975 | 0.050354 | -0.059509 | 60.5621 | 0.28839 | -0.20142 | 0.37537 | -0.11444 | 123.3032 | 123.3948 | 60.6491 | 123.4131 | 123.7335 | 123.5229 | 123.4451 | 123.436 | -123.674 | -123.4726 | 123.1064 | 123.3261 | 60.6949 | 57.5592
431.9844 | 123.5641 | -61.1526 | 62.1002 | -0.073852 | -0.00019652 | 0.00095711 | 0.00095062 | 0.0016128 | 0.0014932 | -0.00095276 | 0.0027465 | 0.0011964 | 0.033045 | 0.032249 | -0.0010787 | -0.00078189 | 0.0013523 | -0.58136 | 62.178 | -61.4456 | 62.0132 | 61.9034 | -61.4136 | -0.15106 | -3.685 | 62.1918 | -61.2671 | 62.2513 | -0.50354 | -61.2442 | -60.7864 | -0.29297 | 0.07782 | -0.086975 | 123.056 | 61.0016 | -0.26093 | 61.2946 | 0.032044 | -0.11444 | 0.091552 | 0.15106 | 60.6491 | 0.36621 | -0.091553 | 0.48065 | 0.022888 | 123.349 | 123.4589 | 60.7636 | 123.5184 | 123.6237 | 123.4589 | 123.3307 | 123.3444 | -123.5458 | -123.3673 | 123.1659 | 123.4039 | 60.5713 | 57.4677
432.9844 | 123.4772 | -61.1847 | 62.1689 | -0.035705 | -0.00062372 | 0.0028797 | 0.00030982 | -0.00052344 | 0.0021342 | 0.00054264 | -0.052185 | 0.00012818 | 0.037959 | 0.032462 | -0.0021469 | -0.00014089 | 0.0015659 | -0.66376 | 62.265 | -61.4731 | 61.908 | 61.8118 | -61.5234 | -0.23804 | -4.216 | 62.1735 | -61.3312 | 62.2055 | -0.64545 | -61.3495 | -60.8505 | -0.28839 | 0.096131 | -0.26093 | 122.9965 | 60.9467 | -0.33875 | 61.235 | -0.050354 | -0.14648 | 0.004578 | 0.036621 | 60.5392 | 0.33417 | -0.1648 | 0.48065 | -0.01831 | 123.2849 | 123.381 | 60.6857 | 123.5367 | 123.7381 | 123.5046 | 123.4497 | 123.3582 | -123.642 | -123.5001 | 123.0927 | 123.3902 | 60.5209 | 56.9687
433.9844 | 123.5413 | -61.1801 | 62.1597 | -0.035705 | 0.00044428 | -0.00011109 | 0.00073702 | 0.00075836 | 0.001066 | 0.0018242 | 0.021057 | 0.00141 | 0.029841 | 0.035667 | -0.0012923 | -0.0014227 | 0.0022067 | -0.70038 | 62.2604 | -61.4456 | 61.9537 | 61.853 | -61.4822 | -0.25177 | -3.923 | 62.2467 | -61.2579 | 62.2101 | -0.55389 | -61.2762 | -60.8139 | -0.2655 | 0.10071 | -0.20599 | 123.0331 | 60.9283 | -0.30212 | 61.1938 | -0.036621 | -0.07782 | 0.086975 | 0.050354 | 60.6262 | 0.36621 | -0.09613 | 0.44403 | -0.01831 | 123.2986 | 123.3994 | 60.704 | 123.468 | 123.7061 | 123.5046 | 123.4406 | 123.4268 | -123.6053 | -123.4177 | 123.1338 | 123.3902 | 60.4797 | 57.2571
435.0469 | 123.4955 | -61.1252 | 62.233 | 0.010071 | 0.0015125 | -0.00053829 | 0.00030982 | 0.0020402 | -0.0019248 | 0.0016106 | -0.0033569 | 0.00098258 | 0.034541 | 0.029044 | -0.0030013 | -0.00035469 | -0.00014315 | -0.60883 | 62.3383 | -61.3815 | 62.027 | 61.9446 | -61.3678 | -0.13733 | -3.8269 | 62.3016 | -61.1938 | 62.2559 | -0.49896 | -61.2259 | -60.791 | -0.25635 | 0.10529 | -0.20599 | 123.0698 | 60.9879 | -0.24262 | 61.2442 | 0.013733 | -0.068665 | 0.068665 | 0.022888 | 60.6262 | 0.33417 | -0.10071 | 0.40283 | -0.032043 | 123.3261 | 123.4085 | 60.6949 | 123.4497 | 123.7198 | 123.4955 | 123.4634 | 123.4268 | -123.6145 | -123.4268 | 123.1522 | 123.381 | 60.5164 | 57.2983
435.9844 | 123.468 | -61.1526 | 62.2513 | -0.028076 | 0.00023068 | 0.0011707 | 0.00030982 | -0.00052344 | 0.001066 | -0.0011664 | -0.06134 | -0.00072642 | 0.037318 | 0.040153 | -0.0017197 | -0.00035469 | -0.00057035 | -0.72784 | 62.3108 | -61.409 | 61.9812 | 61.8713 | -61.4227 | -0.25177 | -4.0604 | 62.3199 | -61.2076 | 62.1964 | -0.58136 | -61.322 | -60.8276 | -0.25635 | 0.059509 | -0.27008 | 123.024 | 60.9009 | -0.27008 | 61.1572 | -0.013732 | -0.054932 | 0.068664 | -0.054932 | 60.5713 | 0.32501 | -0.16937 | 0.37994 | -0.11444 | 123.2803 | 123.3902 | 60.6262 | 123.4039 | 123.7198 | 123.5275 | 123.4634 | 123.4726 | -123.6603 | -123.4589 | 123.1338 | 123.349 | 60.4248 | 57.0923
437.0625 | 123.5779 | -61.084 | 62.2513 | -0.020447 | 0.0017261 | -0.0026745 | -0.00054478 | -0.0013778 | -0.00085663 | 0.00075624 | 0.072937 | 0.0018372 | 0.035395 | 0.028831 | -0.0010787 | -0.0012091 | 0.0039157 | -0.72784 | 62.3199 | -61.3174 | 62.0682 | 61.972 | -61.3174 | -0.14191 | -4.0375 | 62.2879 | -61.1847 | 62.3108 | -0.40283 | -61.116 | -60.6949 | -0.23346 | 0.068664 | -0.18311 | 123.056 | 60.9421 | -0.23346 | 61.1755 | 0 | -0.10071 | 0.036621 | 0.059509 | 60.6812 | 0.3891 | -0.032044 | 0.48981 | 0.068664 | 123.2895 | 123.3856 | 60.7819 | 123.4955 | 123.6374 | 123.4726 | 123.4039 | 123.3719 | -123.5687 | -123.436 | 123.1522 | 123.3948 | 60.3561 | 57.0465
437.9844 | 123.4818 | -61.084 | 62.2375 | -0.005188 | 0.0015125 | 0.0011707 | 0.0013778 | 0.00033116 | -0.0032064 | -0.0011664 | -0.070496 | 0.0018372 | 0.0339 | 0.031821 | -0.0025741 | -0.0016363 | 0.00049765 | -0.74158 | 62.352 | -61.3586 | 62.0819 | 61.972 | -61.3312 | -0.21515 | -4.0649 | 62.3428 | -61.1938 | 62.2696 | -0.49439 | -61.2213 | -60.759 | -0.27466 | 0.11444 | -0.15564 | 123.056 | 60.8688 | -0.24719 | 61.1435 | 0.027466 | -0.10986 | 0.10529 | 0.032043 | 60.5896 | 0.32501 | -0.13733 | 0.43488 | -0.027465 | 123.3307 | 123.4406 | 60.6995 | 123.4634 | 123.7106 | 123.5367 | 123.436 | 123.4268 | -123.5962 | -123.4314 | 123.1659 | 123.3536 | 60.3424 | 57.019
439.0469 | 123.4451 | -61.084 | 62.2833 | -0.020447 | 0.0019397 | 0.0028797 | 0.00073702 | 0.002681 | 0.00085237 | -0.0011664 | -0.027771 | 0.00076898 | 0.034754 | 0.035239 | -0.00043794 | 0.00092711 | -0.00078395 | -0.87433 | 62.3657 | -61.3358 | 62.0316 | 61.9492 | -61.4227 | -0.3479 | -4.3121 | 62.3703 | -61.1755 | 62.2375 | -0.54474 | -61.2762 | -60.8002 | -0.25177 | 0.082398 | -0.25177 | 123.0331 | 60.7361 | -0.33874 | 60.9879 | -0.086975 | -0.091553 | 0.086975 | -0.045776 | 60.5392 | 0.28381 | -0.19226 | 0.37537 | -0.10071 | 123.2849 | 123.3673 | 60.6308 | 123.4131 | 123.7015 | 123.5458 | 123.4497 | 123.4543 | -123.6191 | -123.4589 | 123.1155 | 123.3215 | 60.2097 | 56.7719
439.9844 | 123.4634 | -61.0565 | 62.3108 | 0.0024415 | 1.7082e-05 | 0.00095711 | 0.001805 | 0.002681 | -0.0025656 | 0.00054264 | -0.04303 | 0.00034178 | 0.032405 | 0.034812 | 0.00041666 | -0.00078189 | -0.0031339 | -0.89264 | 62.384 | -61.3358 | 62.0499 | 61.9537 | -61.3495 | -0.31586 | -4.3671 | 62.3795 | -61.1618 | 62.2833 | -0.5127 | -61.2488 | -60.7681 | -0.27923 | 0.073242 | -0.26093 | 123.0103 | 60.7407 | -0.29297 | 61.0199 | -0.013733 | -0.10528 | 0.068665 | -0.027466 | 60.5438 | 0.28839 | -0.19226 | 0.39368 | -0.086975 | 123.2895 | 123.3856 | 60.6491 | 123.4451 | 123.7198 | 123.5413 | 123.4406 | 123.436 | -123.6465 | -123.4726 | 123.1064 | 123.3398 | 60.1639 | 56.6895
440.9844 | 123.5779 | -61.0153 | 62.2604 | -0.073852 | -0.00062372 | 0.00052971 | 0.0028732 | 0.00097196 | 0.0023478 | -0.0022346 | 0.0057983 | 0.00141 | 0.033045 | 0.036521 | -0.0015059 | -0.0012091 | -0.0024929 | -0.99792 | 62.3795 | -61.3037 | 62.114 | 62.0316 | -61.2946 | -0.29297 | -4.4266 | 62.3428 | -61.1252 | 62.3886 | -0.37994 | -61.0794 | -60.6216 | -0.28839 | 0.11902 | -0.14648 | 123.0469 | 60.7224 | -0.27924 | 61.0107 | 0.009155 | -0.10986 | 0.082397 | 0.12817 | 60.6354 | 0.39368 | -0.064087 | 0.50354 | 0.045776 | 123.3353 | 123.4177 | 60.7452 | 123.5138 | 123.6832 | 123.468 | 123.3948 | 123.3582 | -123.5641 | -123.3856 | 123.1293 | 123.4039 | 60.0174 | 56.5887
442.0625 | 123.6053 | -60.9879 | 62.3337 | -0.005188 | 0.00044428 | -0.00032469 | -0.00075838 | -0.0039414 | 0.00042517 | -0.00373 | 0.085144 | -0.00051262 | 0.034327 | 0.026908 | -0.0015059 | -0.0014227 | 0.0011387 | -0.98877 | 62.4069 | -61.2488 | 62.1735 | 62.0911 | -61.1847 | -0.19226 | -4.4083 | 62.3703 | -61.0886 | 62.4298 | -0.27924 | -61.0107 | -60.5804 | -0.26093 | 0.073242 | -0.16022 | 123.0789 | 60.7956 | -0.19684 | 61.0565 | 0.064087 | -0.10071 | 0.036621 | 0.096131 | 60.7086 | 0.40741 | -0.022888 | 0.50812 | 0.07782 | 123.3398 | 123.4222 | 60.8093 | 123.5184 | 123.6557 | 123.4589 | 123.3948 | 123.3582 | -123.5825 | -123.4222 | 123.1613 | 123.4177 | 59.9991 | 56.5796
442.9844 | 123.5962 | -60.9833 | 62.3062 | 0.0177 | 0.0032215 | 0.0011707 | 0.0037276 | -9.604e-05 | 0.0029886 | -0.0026618 | -0.018616 | -0.00072642 | 0.033686 | 0.037803 | -0.0012923 | -0.00014089 | 0.0024203 | -1.1215 | 62.4161 | -61.2854 | 62.1368 | 62.0407 | -61.2762 | -0.34332 | -4.6371 | 62.3566 | -61.1069 | 62.3703 | -0.35706 | -61.0519 | -60.6033 | -0.30212 | 0.10986 | -0.16937 | 123.024 | 60.64 | -0.29297 | 60.9421 | 0.009155 | -0.1236 | 0.050354 | 0.064087 | 60.6262 | 0.37994 | -0.068665 | 0.50354 | 0.054932 | 123.3261 | 123.4222 | 60.7498 | 123.4772 | 123.7015 | 123.4634 | 123.3994 | 123.3398 | -123.5916 | -123.4131 | 123.1201 | 123.3536 | 59.8618 | 56.3461
444.0469 | 123.5229 | -60.9421 | 62.3795 | -0.012817 | 0.00087168 | 0.00031611 | -0.00033118 | -0.00073704 | -0.00085663 | -0.00095276 | 0.051575 | 0.00012818 | 0.034541 | 0.029685 | -0.00022434 | -0.0016363 | 0.00049765 | -1.0941 | 62.4527 | -61.1938 | 62.2101 | 62.1277 | -61.1481 | -0.24261 | -4.6234 | 62.439 | -61.0703 | 62.4069 | -0.34332 | -61.0199 | -60.64 | -0.25177 | 0.073242 | -0.16937 | 123.0698 | 60.6995 | -0.20599 | 60.9512 | 0.045777 | -0.12817 | 0.059509 | 0.027465 | 60.5988 | 0.30212 | -0.077819 | 0.4303 | 0.050354 | 123.3215 | 123.4039 | 60.7269 | 123.4772 | 123.6465 | 123.5092 | 123.3948 | 123.381 | -123.5733 | -123.4497 | 123.1522 | 123.349 | 59.848 | 56.3187
444.9844 | 123.4863 | -60.9879 | 62.352 | -0.028076 | 0.0015125 | -0.00075189 | 0.0015914 | 0.00033116 | -0.0012838 | -0.0011664 | -0.073547 | 0.0011964 | 0.033686 | 0.037162 | -0.0010787 | -0.00056829 | 0.00028405 | -1.5884 | 62.384 | -61.3541 | 62.1277 | 61.9446 | -61.29 | -0.41657 | -4.9347 | 62.4069 | -61.0977 | 62.3428 | -0.4303 | -61.1572 | -60.6995 | -0.36621 | 0.032043 | -0.2243 | 122.9324 | 60.5713 | -0.30212 | 60.9375 | 0.064087 | -0.10986 | 0.054931 | -0.009156 | 60.5576 | 0.28839 | -0.16937 | 0.39825 | -0.05951 | 123.2986 | 123.4818 | 60.6674 | 123.4406 | 123.7381 | 123.5046 | 123.3719 | 123.3948 | -123.7061 | -123.4497 | 123.1155 | 123.3307 | 59.3994 | 56.0532
445.9844 | 123.5733 | -60.9924 | 62.3428 | -0.012817 | 1.7082e-05 | -0.0020337 | 0.00095062 | 0.0018266 | 0.001066 | -0.00073916 | -0.039978 | 0.00034178 | 0.034754 | 0.032676 | -0.0010787 | 0.0017817 | 0.0030613 | -1.4145 | 62.4115 | -61.2671 | 62.1231 | 62.0407 | -61.2717 | -0.44403 | -5.0308 | 62.3932 | -61.084 | 62.4252 | -0.35248 | -61.0611 | -60.6033 | -0.27466 | 0.068665 | -0.21973 | 123.0331 | 60.5484 | -0.27923 | 60.8231 | -0.004577 | -0.091552 | 0.050354 | 0.082398 | 60.64 | 0.3891 | -0.068664 | 0.48065 | 0.022888 | 123.3078 | 123.3902 | 60.7315 | 123.5092 | 123.6786 | 123.4772 | 123.4039 | 123.3856 | -123.6099 | -123.4268 | 123.1155 | 123.4177 | 59.5779 | 55.9616
447.0781 | 123.4772 | -60.9833 | 62.3703 | -0.066223 | -0.0014783 | -0.00032469 | 0.002446 | 0.0033218 | 0.00021157 | -0.0011664 | -0.036926 | 0.002478 | 0.032191 | 0.033744 | -0.00065154 | 0.0030633 | 0.00092505 | -1.5701 | 62.4344 | -61.2854 | 62.114 | 61.9812 | -61.3174 | -0.52185 | -5.2597 | 62.4756 | -61.0931 | 62.1918 | -0.11444 | -61.116 | -60.7407 | -0.30212 | 0.064087 | -0.25635 | 122.9645 | 60.4614 | -0.33417 | 60.7635 | -0.032044 | -0.10986 | 0.10529 | -0.17853 | 60.8688 | 0.24261 | -0.13275 | 0.35248 | -0.022888 | 123.2666 | 123.3994 | 60.9787 | 123.2849 | 123.7198 | 123.5687 | 123.4177 | 123.4589 | -123.6557 | -123.4634 | 123.0972 | 123.175 | 59.4131 | 55.7236
447.9844 | 123.5321 | -60.9558 | 62.3428 | -0.028076 | -0.00062372 | 0.00031611 | 0.003514 | 0.0022538 | 0.00085237 | -9.8356e-05 | -0.027771 | -0.00029902 | 0.0339 | 0.038016 | -0.0025741 | 7.2706e-05 | 0.0034885 | -1.6388 | 62.4435 | -61.2717 | 62.1506 | 62.0407 | -61.2717 | -0.53101 | -5.3879 | 62.4115 | -61.0931 | 62.4023 | -0.37079 | -61.0886 | -60.6308 | -0.31586 | 0.10071 | -0.19226 | 122.9965 | 60.4248 | -0.31586 | 60.7407 | 0 | -0.13733 | 0.068665 | 0.05951 | 60.585 | 0.32501 | -0.13275 | 0.46234 | 0.004578 | 123.3124 | 123.4222 | 60.7224 | 123.4955 | 123.7152 | 123.5046 | 123.3994 | 123.3673 | -123.6145 | -123.436 | 123.1064 | 123.3582 | 59.317 | 55.5679
449.0469 | 123.4268 | -60.9741 | 62.384 | 0.0024415 | 0.00087168 | 0.00031611 | 0.00073702 | -0.0028732 | -2.232e-06 | 0.002038 | -0.052185 | 0.00098258 | 0.035182 | 0.03823 | -0.00022434 | -0.00014089 | 0.00028405 | -1.7349 | 62.4847 | -61.2534 | 62.1094 | 62.0132 | -61.3083 | -0.5722 | -5.6946 | 62.4802 | -61.0703 | 62.3428 | -0.42114 | -61.1801 | -60.6812 | -0.27924 | 0.10071 | -0.27466 | 122.9874 | 60.4019 | -0.33417 | 60.6812 | -0.054932 | -0.09613 | 0.096131 | -0.041199 | 60.553 | 0.29297 | -0.20599 | 0.3891 | -0.10986 | 123.2666 | 123.3627 | 60.6491 | 123.4131 | 123.7381 | 123.5504 | 123.4589 | 123.4543 | -123.6374 | -123.4543 | 123.0835 | 123.317 | 59.2392 | 55.2795
449.9844 | 123.5733 | -60.9146 | 62.3428 | -0.073852 | -0.00041012 | 0.00095711 | -0.00011758 | -0.00030984 | 0.0023478 | -0.0035162 | 0.0057983 | 0.0016236 | 0.033686 | 0.03588 | -0.0047103 | -0.0020637 | 0.0032749 | -1.7899 | 62.439 | -61.2167 | 62.2513 | 62.1506 | -61.1664 | -0.48523 | -5.8823 | 62.4207 | -61.0474 | 62.471 | -0.27008 | -60.9055 | -60.5301 | -0.30212 | 0.096131 | -0.091552 | 123.0652 | 60.4294 | -0.25177 | 60.7315 | 0.050354 | -0.13275 | 0.07782 | 0.12817 | 60.6445 | 0.38452 | 0.009155 | 0.51727 | 0.14191 | 123.3673 | 123.468 | 60.7773 | 123.5184 | 123.6557 | 123.468 | 123.3536 | 123.3353 | -123.5596 | -123.3902 | 123.1659 | 123.3856 | 59.1248 | 55.0323
451.0625 | 123.4955 | -60.9421 | 62.4207 | -0.028076 | 0.00087168 | -0.00032469 | 0.00052342 | 0.0016128 | -0.00021583 | 0.00032904 | -0.049133 | 0.00141 | 0.035822 | 0.029899 | -0.0030013 | 0.0013543 | -0.00078395 | -2.0142 | 62.4847 | -61.2396 | 62.1506 | 62.0407 | -61.2717 | -0.61798 | -6.3446 | 62.439 | -61.0291 | 62.4161 | -0.35706 | -61.0611 | -60.6125 | -0.29755 | 0.064087 | -0.27008 | 122.9828 | 60.3241 | -0.32959 | 60.6216 | -0.032043 | -0.086975 | 0.018311 | -0.004577 | 60.585 | 0.32959 | -0.11902 | 0.41656 | -0.032043 | 123.2803 | 123.3902 | 60.672 | 123.4451 | 123.7244 | 123.468 | 123.4268 | 123.381 | -123.6603 | -123.4497 | 123.0927 | 123.3582 | 58.9279 | 54.5975
452 | 123.4268 | -60.965 | 62.4207 | -0.050964 | 0.0027943 | -0.0011793 | 0.001805 | -0.00073704 | -0.00021583 | -0.002021 | -0.030823 | 0.00034178 | 0.033686 | 0.037803 | -0.00086514 | 0.00092711 | 0.0013523 | -2.1469 | 62.4985 | -61.2167 | 62.1872 | 62.059 | -61.2259 | -0.65918 | -6.6238 | 62.5031 | -61.0336 | 62.4115 | -0.38452 | -61.0794 | -60.6308 | -0.25177 | 0.07782 | -0.23346 | 123.024 | 60.3058 | -0.26093 | 60.5576 | -0.009155 | -0.068664 | 0.082398 | -0.009155 | 60.5804 | 0.33417 | -0.11444 | 0.40283 | -0.045777 | 123.2758 | 123.4039 | 60.6491 | 123.4451 | 123.7152 | 123.5367 | 123.4634 | 123.468 | -123.6374 | -123.4543 | 123.1522 | 123.3765 | 58.8181 | 54.3411
452.9844 | 123.5733 | -60.9055 | 62.3886 | -0.066223 | 0.0019397 | 0.00031611 | 0.001805 | 0.0039628 | -0.0019248 | -0.0015936 | 0.024109 | -0.00029902 | 0.035182 | 0.036735 | -1.0744e-05 | -0.0041999 | 0.00049765 | -2.3483 | 62.4847 | -61.1664 | 62.233 | 62.2238 | -61.0611 | -0.65002 | -6.9214 | 62.4527 | -61.0107 | 62.5122 | -0.2655 | -60.9467 | -60.5347 | -0.26093 | 0.09613 | -0.15564 | 123.1293 | 60.2554 | -0.15564 | 60.5164 | 0.10529 | -0.10529 | 0.064087 | 0.1236 | 60.64 | 0.37079 | -0.041198 | 0.47607 | 0.064087 | 123.3902 | 123.3994 | 60.7452 | 123.5229 | 123.6511 | 123.4634 | 123.3902 | 123.3582 | -123.555 | -123.3994 | 123.1384 | 123.4177 | 58.5571 | 53.9841
453.9844 | 123.5687 | -60.8963 | 62.3749 | 0.010071 | 0.0010853 | 0.00074331 | -0.00011758 | 0.0020402 | 0.00063877 | -0.00138 | -0.046082 | -0.00094002 | 0.035822 | 0.034171 | -1.0744e-05 | 0.00028631 | 0.0019931 | -2.5452 | 62.4847 | -61.1664 | 62.265 | 62.0865 | -61.1801 | -0.737 | -7.3196 | 62.4756 | -61.0016 | 62.5168 | -0.24719 | -60.9558 | -60.4935 | -0.27008 | 0.10986 | -0.10986 | 122.9828 | 60.1593 | -0.28381 | 60.4294 | -0.013733 | -0.10529 | 0.10071 | 0.14191 | 60.6491 | 0.40283 | -0.05951 | 0.50812 | 0.045776 | 123.2529 | 123.4314 | 60.7544 | 123.5184 | 123.6511 | 123.4772 | 123.381 | 123.3719 | -123.5413 | -123.3765 | 123.1613 | 123.4131 | 58.3511 | 53.5767
455.0469 | 123.5413 | -60.8688 | 62.4435 | 0.055847 | 0.0019397 | 0.00074331 | 0.00030982 | -0.00073704 | 0.00021157 | 0.00011544 | -0.055237 | 0.0020508 | 0.035182 | 0.03118 | -0.0064193 | 0.00071351 | 0.0037021 | -2.7328 | 62.5305 | -61.171 | 62.2513 | 62.1414 | -61.1389 | -0.81024 | -7.6721 | 62.5305 | -60.9695 | 62.4207 | -0.2243 | -61.0107 | -60.5392 | -0.30212 | 0.086976 | -0.19226 | 123.0103 | 60.0586 | -0.27008 | 60.3607 | 0.032043 | -0.10071 | 0.086976 | -0.022888 | 60.6445 | 0.32959 | -0.14191 | 0.4303 | -0.041199 | 123.3124 | 123.4222 | 60.7452 | 123.3902 | 123.7015 | 123.5001 | 123.3994 | 123.3994 | -123.6145 | -123.4131 | 123.1201 | 123.2895 | 58.136 | 53.1967
455.9844 | 123.6649 | -60.878 | 62.3932 | -0.005188 | 0.00044428 | -0.00053829 | 0.00095062 | 0.00054476 | 0.0014932 | -0.00031196 | -0.00030511 | 0.00076898 | 0.031764 | 0.036307 | 0.00020286 | -0.00014089 | 0.0019931 | -2.9022 | 62.4802 | -61.1481 | 62.2833 | 62.1872 | -61.116 | -0.8606 | -7.9697 | 62.4802 | -60.9787 | 62.5717 | -0.27466 | -61.1984 | -60.5804 | -0.27008 | 0.086976 | -0.10986 | 123.0652 | 60.0174 | -0.23804 | 60.2875 | 0.032043 | -0.10071 | 0.086976 | 0.17853 | 60.6033 | 0.29755 | -0.32043 | 0.39825 | -0.21973 | 123.3353 | 123.4314 | 60.704 | 123.5504 | 123.6282 | 123.4589 | 123.3582 | 123.3582 | -123.5413 | -123.3719 | 123.1613 | 123.4497 | 57.9758 | 52.9083
457.0625 | 123.5504 | -60.8597 | 62.4527 | -0.020447 | -0.0010511 | -0.00096549 | -0.0011856 | -0.001805 | 0.0012796 | -0.00052556 | 0.13702 | -0.00029902 | 0.033473 | 0.03118 | -0.0012923 | -0.0012091 | -0.0024929 | -2.9709 | 62.5534 | -61.1114 | 62.2879 | 62.146 | -61.1114 | -0.8194 | -8.2581 | 62.5031 | -60.9283 | 62.5397 | -0.23804 | -60.9283 | -60.4752 | -0.25177 | 0.10071 | -0.16479 | 123.0057 | 60.0403 | -0.25177 | 60.2921 | 0 | -0.068665 | 0.050354 | 0.086975 | 60.6216 | 0.38452 | -0.068665 | 0.45319 | 0 | 123.2574 | 123.3994 | 60.6903 | 123.468 | 123.6649 | 123.4314 | 123.4131 | 123.3627 | -123.5641 | -123.381 | 123.1476 | 123.3994 | 57.8888 | 52.6016
457.9844 | 123.5229 | -60.8643 | 62.471 | -0.035705 | -0.00062372 | 0.0013843 | 0.0028732 | 0.00033116 | -0.0012838 | -9.8356e-05 | -0.052185 | 0.00012818 | 0.036036 | 0.03118 | -0.0027877 | 0.0028497 | -0.00035675 | -3.0945 | 62.558 | -61.1572 | 62.2604 | 62.0956 | -61.1664 | -0.90637 | -8.6655 | 62.5122 | -60.965 | 62.5214 | -0.27466 | -60.9695 | -60.5072 | -0.29297 | 0.086975 | -0.21057 | 122.9599 | 59.9579 | -0.30212 | 60.2509 | -0.009155 | -0.10071 | 0.041199 | 0.050354 | 60.5896 | 0.35706 | -0.10529 | 0.45776 | -0.004577 | 123.2529 | 123.4177 | 60.6903 | 123.4863 | 123.7152 | 123.4772 | 123.4222 | 123.3765 | -123.6282 | -123.436 | 123.1247 | 123.3856 | 57.7698 | 52.1988
459.0469 | 123.5092 | -60.8414 | 62.5031 | -0.005188 | 0.0025805 | 0.00074331 | 0.0028732 | 0.0041764 | 0.00063877 | -0.00031196 | -0.046082 | 0.0022644 | 0.036891 | 0.030112 | -0.0015059 | -0.0022773 | -0.0016385 | -3.1174 | 62.6083 | -61.1114 | 62.3108 | 62.1643 | -61.0657 | -0.7782 | -8.8211 | 62.5809 | -60.9375 | 62.5488 | -0.2243 | -60.9467 | -60.498 | -0.27008 | 0.10529 | -0.19226 | 123.0057 | 60.0632 | -0.2243 | 60.3333 | 0.045776 | -0.09613 | 0.07782 | 0.045776 | 60.6171 | 0.34332 | -0.10529 | 0.43945 | -0.009155 | 123.2758 | 123.4222 | 60.7132 | 123.4863 | 123.7198 | 123.5184 | 123.4497 | 123.4222 | -123.6145 | -123.4406 | 123.1522 | 123.3902 | 57.724 | 52.0203
459.9844 | 123.5779 | -60.8002 | 62.4619 | 0.010071 | 0.00044428 | -0.00011109 | 0.0015914 | 0.0011856 | -0.00021583 | 0.001397 | -0.046082 | -0.00094002 | 0.034113 | 0.034171 | -0.00086514 | 0.00028631 | -0.0012111 | -3.2272 | 62.558 | -61.1206 | 62.3154 | 62.1506 | -61.0886 | -0.76446 | -9.2011 | 62.5305 | -60.9329 | 62.5946 | -0.19684 | -60.8871 | -60.4248 | -0.32043 | 0.09613 | -0.14648 | 122.9507 | 60.0357 | -0.28839 | 60.3561 | 0.032043 | -0.13275 | 0.068665 | 0.13275 | 60.6033 | 0.37537 | -0.086975 | 0.50812 | 0.045776 | 123.2712 | 123.436 | 60.7361 | 123.5275 | 123.6786 | 123.4634 | 123.3582 | 123.3307 | -123.5825 | -123.3948 | 123.1155 | 123.3948 | 57.5729 | 51.5991
461.0625 | 123.587 | -60.7727 | 62.5305 | 0.0024415 | 0.0015125 | -0.00011109 | -0.0013992 | -9.604e-05 | -0.00021583 | -0.0015936 | 0.045471 | 0.00076898 | 0.032618 | 0.03054 | -0.00022434 | -0.00014089 | 0.0011387 | -3.241 | 62.6221 | -61.0291 | 62.4344 | 62.2925 | -60.9283 | -0.50812 | -9.3292 | 62.5626 | -60.8734 | 62.6404 | -0.10071 | -60.7727 | -60.3745 | -0.25635 | 0.091552 | -0.096131 | 123.0652 | 60.2646 | -0.15564 | 60.5209 | 0.10071 | -0.10071 | 0.032043 | 0.10986 | 60.672 | 0.39825 | 0 | 0.49896 | 0.10071 | 123.3215 | 123.4634 | 60.7727 | 123.5138 | 123.6511 | 123.436 | 123.3948 | 123.3353 | -123.5596 | -123.4039 | 123.2071 | 123.4131 | 57.5317 | 51.4435
462 | 123.4909 | -60.8139 | 62.5305 | -0.36377 | 0.00044428 | -0.0028881 | 0.0030868 | 0.0020402 | 0.002775 | -0.00073916 | -0.073547 | 0.0018372 | 0.035395 | 0.034812 | -0.0015059 | -0.00056829 | 0.0022067 | -3.1631 | 62.6038 | -61.116 | 62.3154 | 62.1048 | -61.1893 | -0.68207 | -9.9792 | 62.5992 | -60.9283 | 62.5442 | -0.28381 | -60.9512 | -60.4935 | -0.30212 | 0.073242 | -0.21515 | 122.9187 | 60.1318 | -0.37537 | 60.434 | -0.073242 | -0.11444 | 0.068664 | 0.013732 | 60.5301 | 0.32044 | -0.13733 | 0.43488 | -0.022888 | 123.2208 | 123.4314 | 60.6445 | 123.4726 | 123.7198 | 123.5275 | 123.4177 | 123.4131 | -123.6465 | -123.4589 | 123.1293 | 123.3582 | 57.6508 | 50.8347
463.0469 | 123.4818 | -60.7864 | 62.5488 | 0.010071 | 0.00065788 | 0.00031611 | 0.0022324 | 0.0033218 | -0.00021583 | -0.0026618 | -0.030823 | 0.0011964 | 0.036677 | 0.032889 | 0.00020286 | 7.2706e-05 | -0.0037747 | -3.3737 | 62.6495 | -61.0611 | 62.3291 | 62.1185 | -61.0611 | -0.47607 | -10.3729 | 62.6221 | -60.8826 | 62.5809 | -0.20599 | -60.878 | -60.4568 | -0.27466 | 0.10071 | -0.21973 | 122.905 | 60.3104 | -0.27466 | 60.585 | 0 | -0.09613 | 0.073242 | 0.032044 | 60.5804 | 0.32959 | -0.091553 | 0.42572 | 0.004577 | 123.1796 | 123.3902 | 60.6766 | 123.4634 | 123.7106 | 123.5046 | 123.436 | 123.4085 | -123.6099 | -123.4314 | 123.1155 | 123.3673 | 57.4127 | 50.4135
463.9844 | 123.4589 | -60.8002 | 62.5488 | 0.040589 | 0.0017261 | -0.00053829 | 0.0028732 | -0.0030868 | -2.232e-06 | -0.0011664 | -0.070496 | 0.00141 | 0.033686 | 0.036094 | -0.00022434 | -0.0022773 | 0.00049765 | -3.5248 | 62.6129 | -61.0794 | 62.3474 | 62.1597 | -61.0428 | -0.45776 | -10.7208 | 62.6221 | -60.878 | 62.5809 | -0.24261 | -60.9055 | -60.4568 | -0.27924 | 0.064087 | -0.20142 | 122.9599 | 60.3424 | -0.24262 | 60.6216 | 0.036621 | -0.07782 | 0.073242 | 0.032044 | 60.5576 | 0.34332 | -0.10529 | 0.42114 | -0.027466 | 123.2391 | 123.4268 | 60.6354 | 123.4589 | 123.6923 | 123.5001 | 123.4131 | 123.4222 | -123.6282 | -123.4268 | 123.1476 | 123.381 | 57.2754 | 50.0793
464.9844 | 123.4818 | -60.8002 | 62.5763 | -0.050964 | 0.0012989 | -0.00053829 | -0.00075838 | 0.00011756 | 0.0017068 | 0.0018242 | -0.049133 | 0.00055538 | 0.0339 | 0.03353 | -0.00086514 | 0.00092711 | 0.0017795 | -3.6072 | 62.6358 | -61.0703 | 62.2879 | 62.027 | -61.1618 | -0.52185 | -11.2015 | 62.6404 | -60.9146 | 62.5305 | -0.27466 | -60.9787 | -60.4935 | -0.27008 | 0.059509 | -0.28839 | 122.8271 | 60.2783 | -0.36163 | 60.5484 | -0.091553 | -0.11444 | 0.064087 | -0.045776 | 60.5255 | 0.3067 | -0.17853 | 0.42114 | -0.064087 | 123.0972 | 123.3582 | 60.64 | 123.4451 | 123.7061 | 123.555 | 123.436 | 123.4406 | -123.6465 | -123.4909 | 123.0881 | 123.3307 | 57.193 | 49.5987
466.0469 | 123.468 | -60.7681 | 62.6083 | 0.0177 | 0.0012989 | -0.0016065 | 0.001805 | -0.00073704 | -0.0025656 | -0.00373 | 0.024109 | 0.0011964 | 0.036036 | 0.040153 | -0.00086514 | -0.00056829 | -0.00035675 | -3.6301 | 62.677 | -61.0153 | 62.3611 | 62.1552 | -61.0153 | -0.34332 | -11.3846 | 62.6633 | -60.8643 | 62.5626 | -0.20142 | -60.8597 | -60.4477 | -0.24719 | 0.068665 | -0.24719 | 122.9233 | 60.4248 | -0.24719 | 60.672 | 0 | -0.096131 | 0.054932 | -0.045776 | 60.5667 | 0.32043 | -0.091553 | 0.41656 | 0.004578 | 123.1705 | 123.3765 | 60.6628 | 123.4268 | 123.6923 | 123.5275 | 123.4451 | 123.4314 | -123.6237 | -123.4726 | 123.1293 | 123.3307 | 57.1381 | 49.3835
467 | 123.5641 | -60.7498 | 62.5717 | -0.012817 | 1.7082e-05 | -0.00053829 | 0.0030868 | -0.0026596 | -0.00064303 | -0.00095276 | 0.06073 | -0.00029902 | 0.035395 | 0.028403 | -0.00043794 | -0.0014227 | 0.00049765 | -3.7857 | 62.6678 | -61.0107 | 62.4023 | 62.1826 | -60.9924 | -0.33417 | -11.6867 | 62.6129 | -60.8368 | 62.6495 | -0.1236 | -60.7773 | -60.3699 | -0.26093 | 0.096131 | -0.16937 | 122.9324 | 60.4156 | -0.24262 | 60.6766 | 0.01831 | -0.086975 | 0.041199 | 0.07782 | 60.6262 | 0.37994 | -0.027466 | 0.46692 | 0.059509 | 123.1934 | 123.4131 | 60.7132 | 123.4863 | 123.6786 | 123.4497 | 123.4177 | 123.3627 | -123.5825 | -123.4085 | 123.1522 | 123.3994 | 56.9641 | 49.0631
468.0469 | 123.4863 | -60.759 | 62.6266 | 0.0177 | -0.0023327 | 0.00095711 | -0.00033118 | -0.00095064 | 0.002775 | -0.00138 | 0.0088501 | -0.00029902 | 0.033045 | 0.034598 | -0.0021469 | -0.0012091 | 7.0452e-05 | -3.8635 | 62.6495 | -61.0153 | 62.4252 | 62.1918 | -60.9467 | -0.28839 | -11.9934 | 62.6724 | -60.8139 | 62.6083 | -0.19226 | -60.8459 | -60.4202 | -0.25635 | 0.022888 | -0.20142 | 122.9507 | 60.4706 | -0.18768 | 60.7269 | 0.068665 | -0.054932 | 0.045776 | -0.018311 | 60.5667 | 0.33875 | -0.086975 | 0.39368 | -0.032043 | 123.2071 | 123.4406 | 60.6216 | 123.4222 | 123.6649 | 123.4863 | 123.4085 | 123.4314 | -123.642 | -123.4406 | 123.1842 | 123.3673 | 56.8954 | 48.7656
468.9844 | 123.4497 | -60.7727 | 62.6129 | 0.010071 | 0.0027943 | -0.00096549 | 0.0028732 | 0.00033116 | -0.00021583 | -0.00095276 | -0.06134 | 0.00076898 | 0.034754 | 0.034171 | -0.0012923 | 0.00049991 | 0.00071145 | -4.0924 | 62.6999 | -61.0565 | 62.3199 | 62.0132 | -61.1114 | -0.45776 | -12.4191 | 62.6541 | -60.8688 | 62.5671 | -0.25635 | -60.9283 | -60.466 | -0.28381 | 0.086975 | -0.29297 | 122.7859 | 60.3149 | -0.33874 | 60.5988 | -0.054931 | -0.09613 | 0.041199 | -0.045776 | 60.5164 | 0.3067 | -0.15564 | 0.40283 | -0.05951 | 123.0698 | 123.3765 | 60.6125 | 123.436 | 123.7564 | 123.5229 | 123.4726 | 123.4268 | -123.6694 | -123.4818 | 123.0927 | 123.3398 | 56.6803 | 48.3536
469.9844 | 123.5733 | -60.7407 | 62.5259 | -0.020447 | 0.0010853 | -0.0018201 | 0.00073702 | -0.0015914 | -0.00042943 | -0.00138 | -0.058289 | -0.00029902 | 0.034113 | 0.03588 | -0.00086514 | -0.00056829 | -0.0035611 | -4.2114 | 62.6678 | -61.0474 | 62.3703 | 62.1094 | -61.0291 | -0.40741 | -12.6755 | 62.645 | -60.8414 | 62.645 | -0.14648 | -60.8185 | -60.3607 | -0.3067 | 0.14191 | -0.15564 | 122.85 | 60.3333 | -0.28839 | 60.64 | 0.01831 | -0.10071 | 0.11902 | 0.11902 | 60.5942 | 0.37994 | -0.077819 | 0.48065 | 0.022889 | 123.1567 | 123.4177 | 60.6949 | 123.4863 | 123.7152 | 123.4863 | 123.4085 | 123.3856 | -123.5733 | -123.3673 | 123.111 | 123.3856 | 56.5292 | 48.0652
471.0625 | 123.4314 | -60.791 | 62.59 | -0.035705 | 0.0017261 | -0.00096549 | 0.0015914 | -0.0043686 | -0.0019248 | 0.0039606 | -0.067444 | 0.0026916 | 0.035822 | 0.039725 | -0.00065154 | -0.00035469 | -0.0016385 | -4.3625 | 62.6907 | -61.0519 | 62.3337 | 62.027 | -61.0977 | -0.46234 | -13.0096 | 62.6678 | -60.878 | 62.59 | -0.25177 | -60.9283 | -60.434 | -0.26093 | 0.10071 | -0.25635 | 122.818 | 60.3287 | -0.3067 | 60.5896 | -0.045776 | -0.086975 | 0.07782 | 0 | 60.5392 | 0.35706 | -0.13733 | 0.44403 | -0.050354 | 123.0789 | 123.3856 | 60.6262 | 123.468 | 123.7427 | 123.5458 | 123.4818 | 123.4589 | -123.642 | -123.468 | 123.1247 | 123.381 | 56.4285 | 47.7814
472 | 123.5184 | -60.7452 | 62.558 | -0.012817 | 0.0010853 | -0.00011109 | 0.00095062 | 0.00097196 | 0.00085237 | -0.00095276 | 0.011902 | -8.5416e-05 | 0.035395 | 0.030967 | -0.0015059 | -0.00014089 | -0.00078395 | -4.4174 | 62.6358 | -60.9833 | 62.4619 | 62.1597 | -60.9604 | -0.32959 | -13.0463 | 62.6266 | -60.8322 | 62.6404 | -0.14191 | -60.791 | -60.3516 | -0.23804 | 0.07782 | -0.09613 | 122.905 | 60.4156 | -0.21515 | 60.6537 | 0.022888 | -0.086975 | 0.068665 | 0.082398 | 60.6033 | 0.39368 | -0.045777 | 0.48065 | 0.041198 | 123.143 | 123.4451 | 60.6903 | 123.4726 | 123.6191 | 123.4589 | 123.381 | 123.3719 | -123.5413 | -123.3902 | 123.2071 | 123.3856 | 56.3278 | 47.699
472.9844 | 123.5504 | -60.7819 | 62.5488 | -0.028076 | 0.0032215 | 0.0011707 | 0.0039414 | -0.00052344 | 0.00085237 | 0.00011544 | -0.067444 | -8.5416e-05 | 0.035822 | 0.040793 | -0.0019333 | -0.00056829 | 0.0022067 | -4.6234 | 62.6953 | -61.0519 | 62.3245 | 61.9812 | -61.0748 | -0.43945 | -13.3667 | 62.6678 | -60.8597 | 62.5763 | -0.25177 | -60.8963 | -60.4477 | -0.27008 | 0.14648 | -0.2243 | 122.7631 | 60.3424 | -0.29297 | 60.6125 | -0.022888 | -0.07782 | 0.11902 | 0.027466 | 60.5301 | 0.33417 | -0.11444 | 0.41199 | -0.036621 | 123.0331 | 123.3765 | 60.6079 | 123.436 | 123.7473 | 123.5275 | 123.4772 | 123.4497 | -123.6008 | -123.4085 | 123.1064 | 123.3582 | 56.1584 | 47.4152
474.0469 | 123.5184 | -60.7086 | 62.6129 | 0.010071 | 0.00065788 | 0.00095711 | 0.00073702 | -0.002446 | -0.0032064 | -0.00052556 | 0.018005 | 0.00055538 | 0.034327 | 0.031821 | -0.00065154 | -0.0016363 | 0.0022067 | -4.66 | 62.6816 | -60.9695 | 62.4802 | 62.1872 | -60.91 | -0.2655 | -13.3713 | 62.6678 | -60.791 | 62.6633 | -0.13275 | -60.7636 | -60.3424 | -0.26093 | 0.068665 | -0.13275 | 122.8958 | 60.4431 | -0.20142 | 60.704 | 0.059509 | -0.082398 | 0.054932 | 0.050354 | 60.5759 | 0.36621 | -0.054932 | 0.44861 | 0.027466 | 123.1567 | 123.4497 | 60.6583 | 123.4543 | 123.6511 | 123.4589 | 123.3902 | 123.3765 | -123.5825 | -123.4039 | 123.1888 | 123.3719 | 56.0486 | 47.3373
474.9844 | 123.5916 | -60.7315 | 62.5809 | -0.081482 | 1.7082e-05 | 0.0011707 | 0.00095062 | 0.0022538 | 0.00063877 | -0.00138 | -0.036926 | -0.0013672 | 0.035609 | 0.029685 | -0.0030013 | 0.00028631 | -0.0012111 | -4.9622 | 62.677 | -61.0245 | 62.4115 | 62.0773 | -61.0107 | -0.45319 | -13.6505 | 62.6541 | -60.8276 | 62.6907 | -0.14648 | -60.7956 | -60.3333 | -0.29297 | 0.09613 | -0.16937 | 122.8088 | 60.2783 | -0.27924 | 60.5713 | 0.013733 | -0.096131 | 0.073242 | 0.10986 | 60.585 | 0.39825 | -0.064087 | 0.49439 | 0.032044 | 123.1018 | 123.436 | 60.6812 | 123.5184 | 123.7015 | 123.4818 | 123.4085 | 123.3856 | -123.6053 | -123.4085 | 123.143 | 123.4222 | 55.7693 | 47.081
476.0469 | 123.4589 | -60.704 | 62.645 | 0.02533 | 1.7082e-05 | 0.00010251 | 0.00030982 | 0.00097196 | -2.232e-06 | -0.00073916 | -0.076599 | 0.00055538 | 0.035395 | 0.032035 | 0.00020286 | -0.00056829 | 0.00071145 | -5.127 | 62.7869 | -60.9741 | 62.3932 | 62.0544 | -60.9787 | -0.2655 | -13.9847 | 62.7411 | -60.8276 | 62.6221 | -0.15564 | -60.8002 | -60.4248 | -0.27008 | 0.14191 | -0.25177 | 122.7585 | 60.4385 | -0.27466 | 60.7086 | -0.004578 | -0.1236 | 0.096131 | -0.022888 | 60.5484 | 0.27924 | -0.09613 | 0.40283 | 0.027466 | 123.0286 | 123.3673 | 60.672 | 123.4497 | 123.761 | 123.5687 | 123.4909 | 123.4451 | -123.6191 | -123.4726 | 123.0972 | 123.3261 | 55.5771 | 46.7194
477 | 123.5779 | -60.6628 | 62.6083 | 0.010071 | 0.0025805 | -0.00053829 | 0.00095062 | -0.002446 | -0.00021583 | -0.00052556 | 0.030212 | 0.00055538 | 0.034327 | 0.026694 | 0.00041666 | -0.00056829 | 0.00049765 | -5.2689 | 62.709 | -60.9283 | 62.4939 | 62.1826 | -60.8826 | -0.42114 | -13.8748 | 62.6724 | -60.7956 | 62.7365 | -0.036621 | -60.6766 | -60.2417 | -0.2655 | 0.10071 | -0.11444 | 122.8455 | 60.2417 | -0.21973 | 60.5072 | 0.045777 | -0.13275 | 0.064087 | 0.12817 | 60.6262 | 0.42114 | -0.013733 | 0.55389 | 0.11902 | 123.111 | 123.4222 | 60.759 | 123.5321 | 123.6374 | 123.468 | 123.3719 | 123.3353 | -123.5367 | -123.4039 | 123.1567 | 123.3994 | 55.394 | 46.788
478.0469 | 123.555 | -60.6445 | 62.6541 | 0.010071 | 0.00023068 | -0.0026745 | -0.00011758 | -0.0011642 | -0.00042943 | -0.00052556 | 0.036316 | 0.0016236 | 0.0339 | 0.03588 | -0.00065154 | -0.0012091 | -0.00035675 | -5.4474 | 62.7045 | -60.9558 | 62.5214 | 62.1872 | -60.8597 | -0.48523 | -13.9801 | 62.6999 | -60.7636 | 62.7228 | -0.082397 | -60.6949 | -60.3058 | -0.31128 | 0.050354 | -0.13275 | 122.8317 | 60.1593 | -0.21515 | 60.4706 | 0.096131 | -0.11902 | 0.045776 | 0.068664 | 60.5621 | 0.33875 | -0.050354 | 0.45776 | 0.068665 | 123.143 | 123.4772 | 60.6812 | 123.4863 | 123.6603 | 123.4634 | 123.349 | 123.3444 | -123.6099 | -123.4177 | 123.1659 | 123.3673 | 55.1971 | 46.6644
478.9844 | 123.5687 | -60.6903 | 62.6129 | -0.066223 | 0.00023068 | -0.0016065 | 0.00095062 | -0.00095064 | -0.00042943 | -0.002021 | -0.027771 | 0.00055538 | 0.033686 | 0.032249 | -0.0010787 | 0.0019953 | -0.0029201 | -5.6671 | 62.6953 | -60.965 | 62.4847 | 62.114 | -60.9375 | -0.59967 | -14.1495 | 62.677 | -60.8047 | 62.7182 | -0.10986 | -60.7315 | -60.2921 | -0.27466 | 0.082397 | -0.12817 | 122.8043 | 60.0906 | -0.24719 | 60.3653 | 0.027466 | -0.11444 | 0.064087 | 0.10529 | 60.5804 | 0.39825 | -0.041198 | 0.5127 | 0.073243 | 123.0789 | 123.4497 | 60.6949 | 123.523 | 123.6603 | 123.4818 | 123.3856 | 123.3673 | -123.5779 | -123.4177 | 123.175 | 123.4085 | 55.0232 | 46.5408
480.0469 | 123.4772 | -60.7086 | 62.6495 | 0.0177 | 0.00065788 | -0.00032469 | 0.0015914 | 0.002681 | 0.00085237 | 0.0016106 | -0.073547 | 0.00076898 | 0.032618 | 0.035026 | -0.0025741 | -0.00056829 | -0.0024929 | -5.8731 | 62.7457 | -61.0016 | 62.4252 | 62.027 | -61.0016 | -0.66834 | -14.3417 | 62.7182 | -60.8002 | 62.6358 | -0.19684 | -60.8505 | -60.3928 | -0.29297 | 0.096131 | -0.2243 | 122.7356 | 60.0403 | -0.29297 | 60.3333 | 0 | -0.091553 | 0.068665 | -0.013733 | 60.5118 | 0.31586 | -0.14191 | 0.40741 | -0.050354 | 123.0286 | 123.4268 | 60.6033 | 123.436 | 123.7473 | 123.5184 | 123.4543 | 123.4268 | -123.6511 | -123.4497 | 123.1338 | 123.3444 | 54.8355 | 46.3669
480.9844 | 123.4634 | -60.704 | 62.6266 | -0.028076 | -0.00062372 | 0.0013843 | 0.0028732 | -0.002446 | 0.001066 | 0.0041742 | -0.1651 | -0.0017944 | 0.031977 | 0.034171 | -0.0019333 | 0.0015679 | 0.0024203 | -6.0745 | 62.7228 | -61.0107 | 62.4023 | 61.972 | -61.0336 | -0.70496 | -14.36 | 62.6999 | -60.8322 | 62.6038 | -0.19684 | -60.8917 | -60.4156 | -0.3067 | 0.09613 | -0.2243 | 122.6761 | 59.9991 | -0.32959 | 60.3058 | -0.022888 | -0.12817 | 0.073242 | -0.022888 | 60.5072 | 0.28839 | -0.18768 | 0.41656 | -0.05951 | 122.9828 | 123.4131 | 60.6354 | 123.436 | 123.7335 | 123.5321 | 123.4268 | 123.4039 | -123.6374 | -123.4589 | 123.1064 | 123.3078 | 54.6295 | 46.344
482.0625 | 123.6053 | -60.6583 | 62.6266 | -0.043335 | -0.00062372 | -0.0020337 | 9.6222e-05 | -0.00095064 | -0.001711 | 0.0024652 | 0.057678 | 0.00098258 | 0.034754 | 0.027122 | -0.0012923 | -0.00014089 | -0.0027065 | -6.1111 | 62.7228 | -60.9375 | 62.5168 | 62.1964 | -60.8276 | -0.4303 | -14.3829 | 62.6678 | -60.759 | 62.7731 | -0.022888 | -60.6171 | -60.2371 | -0.27924 | 0.09613 | -0.10986 | 122.8546 | 60.228 | -0.16937 | 60.5072 | 0.10986 | -0.10071 | 0.041199 | 0.14648 | 60.6354 | 0.42114 | 0.041199 | 0.52185 | 0.14191 | 123.1338 | 123.4543 | 60.7361 | 123.5321 | 123.6603 | 123.4268 | 123.381 | 123.3261 | -123.5641 | -123.3856 | 123.175 | 123.4314 | 54.5471 | 46.2753
482.9844 | 123.5825 | -60.6949 | 62.5854 | 0.048218 | 0.00044428 | 0.00074331 | 0.00030982 | -0.001805 | 0.0014932 | 0.00011544 | -0.033875 | 0.00012818 | 0.035822 | 0.035026 | -0.0015059 | -0.00078189 | 0.00049765 | -6.221 | 62.6862 | -60.965 | 62.4893 | 62.0911 | -60.9192 | -0.45776 | -14.6118 | 62.6587 | -60.791 | 62.7319 | -0.11444 | -60.7361 | -60.2783 | -0.27008 | 0.10071 | -0.09613 | 122.7859 | 60.2371 | -0.2243 | 60.5072 | 0.045777 | -0.096131 | 0.073242 | 0.14649 | 60.5804 | 0.41656 | -0.041199 | 0.5127 | 0.054932 | 123.056 | 123.4543 | 60.6766 | 123.523 | 123.6511 | 123.4497 | 123.381 | 123.3536 | -123.5504 | -123.3765 | 123.1842 | 123.4268 | 54.4739 | 46.0831
484.0625 | 123.5733 | -60.6903 | 62.5992 | -0.012817 | -0.00062372 | 0.00074331 | 0.001805 | -0.00052344 | 0.00042517 | -0.0011664 | -0.052185 | 0.00055538 | 0.031336 | 0.032249 | -0.0023605 | 0.00028631 | -0.00078395 | -6.3446 | 62.6907 | -60.9787 | 62.439 | 62.0361 | -60.9787 | -0.37994 | -14.8361 | 62.6541 | -60.7819 | 62.7045 | -0.14648 | -60.7452 | -60.2829 | -0.28839 | 0.091553 | -0.16022 | 122.7264 | 60.3104 | -0.28839 | 60.5988 | 0 | -0.091552 | 0.054932 | 0.10529 | 60.5438 | 0.40741 | -0.054931 | 0.49896 | 0.036621 | 123.0148 | 123.4177 | 60.6354 | 123.4863 | 123.6694 | 123.436 | 123.381 | 123.3444 | -123.5779 | -123.381 | 123.1293 | 123.3948 | 54.3457 | 45.8542
484.9844 | 123.4497 | -60.7224 | 62.6175 | -0.089111 | 0.0015125 | 0.0020251 | 0.002446 | -0.0028732 | 0.00021157 | -0.00052556 | -0.10712 | 0.00098258 | 0.035182 | 0.03588 | -0.0017197 | 0.0013543 | 0.00092505 | -6.3858 | 62.709 | -61.0062 | 62.1552 | 61.7569 | -60.5621 | -0.2243 | -14.978 | 62.7319 | -60.8047 | 62.6404 | -0.23346 | -60.8551 | -60.3745 | -0.28381 | 0.091552 | -0.46234 | 122.4792 | 60.498 | 0.16022 | 60.7819 | 0.44403 | -0.082398 | 0.11444 | 0.022888 | 60.4889 | 0.3479 | -0.13275 | 0.4303 | -0.050354 | 122.7631 | 123.1613 | 60.5713 | 123.4451 | 123.7152 | 123.5367 | 123.4314 | 123.4543 | -123.6237 | -123.4222 | 122.8775 | 123.3627 | 54.3365 | 45.7443
485.9844 | 123.5321 | -60.6995 | 62.6129 | -0.043335 | 0.0017261 | 0.0011707 | 0.00073702 | 0.0024674 | 0.00042517 | 0.00032904 | -0.027771 | 0.00141 | 0.034541 | 0.033958 | -0.0012923 | -0.00035469 | 0.00071145 | -6.4407 | 62.7228 | -61.0062 | 62.4252 | 61.972 | -60.997 | -0.20142 | -15.1291 | 62.6999 | -60.8185 | 62.6953 | -0.16479 | -60.791 | -60.3378 | -0.3067 | 0.10986 | -0.18768 | 122.6715 | 60.498 | -0.29755 | 60.8047 | 0.009156 | -0.11902 | 0.086975 | 0.082397 | 60.5347 | 0.36163 | -0.091553 | 0.48065 | 0.027465 | 122.9782 | 123.4314 | 60.6537 | 123.5138 | 123.7289 | 123.5184 | 123.4222 | 123.3994 | -123.6191 | -123.4314 | 123.1247 | 123.3948 | 54.2587 | 45.5704
487.0625 | 123.6008 | -60.6628 | 62.6038 | -0.020447 | -0.00041012 | -0.00096549 | 0.00030982 | 0.00097196 | 0.00063877 | -0.0011664 | 0.042419 | 0.00076898 | 0.035609 | 0.02819 | -0.0012923 | -0.0033453 | 0.00028405 | -6.4316 | 62.7365 | -60.9604 | 62.5534 | 62.146 | -60.8276 | 0.041199 | -15.0604 | 62.677 | -60.7407 | 62.7823 | -0.050354 | -60.6308 | -60.2417 | -0.29755 | 0.13275 | -0.050354 | 122.8088 | 60.704 | -0.1648 | 61.0016 | 0.13275 | -0.07782 | 0.073242 | 0.17853 | 60.6125 | 0.42114 | 0.032044 | 0.49896 | 0.10986 | 123.1064 | 123.5138 | 60.6903 | 123.523 | 123.6969 | 123.4177 | 123.3994 | 123.3398 | -123.5641 | -123.3444 | 123.2162 | 123.4451 | 54.2313 | 45.6024
487.9844 | 123.4863 | -60.7224 | 62.6221 | 0.0024415 | 0.0017261 | 0.0011707 | 0.0013778 | 0.002681 | 0.0040568 | 0.00011544 | -0.030823 | 0.002478 | 0.033686 | 0.037162 | -0.00065154 | -0.00078189 | -0.0024929 | -6.6513 | 62.7136 | -61.0016 | 62.5946 | 62.0956 | -61.1664 | -0.086975 | -15.4633 | 62.7365 | -60.8002 | 62.6221 | -0.23804 | -60.8505 | -60.4065 | -0.27924 | 0.091553 | -0.027466 | 122.818 | 60.6354 | -0.44403 | 60.9146 | -0.16479 | -0.07782 | 0.11444 | 0 | 60.4843 | 0.31586 | -0.12817 | 0.39368 | -0.050354 | 123.0972 | 123.5962 | 60.5621 | 123.4222 | 123.7152 | 123.5367 | 123.436 | 123.4589 | -123.6237 | -123.4222 | 123.317 | 123.3444 | 54.071 | 45.2591
488.9844 | 123.5504 | -60.7086 | 62.6129 | -0.050964 | -0.00041012 | 0.00095711 | 0.0011642 | 0.0024674 | -2.232e-06 | 0.0022516 | -0.021668 | 0.0026916 | 0.034541 | 0.036307 | -0.0021469 | 0.00028631 | 0.00071145 | -6.7429 | 62.6999 | -61.0016 | 62.4161 | 61.9492 | -61.0107 | 0.004578 | -15.5685 | 62.6816 | -60.8093 | 62.6816 | -0.17853 | -60.7681 | -60.3149 | -0.29297 | 0.086975 | -0.19684 | 122.6578 | 60.7132 | -0.30212 | 61.0062 | -0.009155 | -0.10071 | 0.068665 | 0.068665 | 60.5301 | 0.39368 | -0.059509 | 0.49439 | 0.041199 | 122.9507 | 123.4177 | 60.6308 | 123.4909 | 123.7015 | 123.4909 | 123.4085 | 123.3902 | -123.6145 | -123.4222 | 123.1247 | 123.3902 | 53.9658 | 45.1401
490.0469 | 123.5229 | -60.7361 | 62.6358 | 0.010071 | 0.00023068 | -0.0020337 | 0.0015914 | -0.00095064 | 0.00021157 | 0.00075624 | -0.06134 | 0.00141 | 0.035395 | 0.033317 | -0.0012923 | -0.00078189 | -0.00014315 | -6.7657 | 62.7411 | -60.9741 | 62.4619 | 61.9858 | -60.9238 | 0.15564 | -15.6143 | 62.7228 | -60.7773 | 62.677 | -0.17395 | -60.7773 | -60.3333 | -0.23804 | 0.10529 | -0.17395 | 122.7219 | 60.8917 | -0.18768 | 61.1298 | 0.050354 | -0.041199 | 0.086975 | 0.041199 | 60.5621 | 0.40283 | -0.041199 | 0.44403 | 0 | 122.9599 | 123.436 | 60.6033 | 123.4543 | 123.7152 | 123.5001 | 123.4772 | 123.4589 | -123.6099 | -123.4131 | 123.1979 | 123.4131 | 53.9703 | 45.1218
490.9844 | 123.5458 | -60.6949 | 62.5992 | -0.035705 | -0.0010511 | 0.00052971 | 0.00073702 | -0.0013778 | 0.0040568 | -0.00138 | -0.0033569 | 0.00034178 | 0.034541 | 0.033103 | -0.0010787 | -0.00099549 | 0.0028477 | -7.1182 | 62.6358 | -60.9833 | 62.5214 | 62.0178 | -60.9146 | 0.26093 | -15.683 | 62.6358 | -60.791 | 62.7274 | -0.14648 | -60.7315 | -60.2966 | -0.28839 | 0.036621 | -0.07782 | 122.7127 | 60.9558 | -0.21973 | 61.2442 | 0.068664 | -0.096131 | 0.036621 | 0.12817 | 60.5484 | 0.39825 | -0.036621 | 0.49439 | 0.05951 | 123.0011 | 123.5046 | 60.6445 | 123.5184 | 123.6191 | 123.4268 | 123.3307 | 123.3307 | -123.5825 | -123.3902 | 123.2162 | 123.4222 | 53.5767 | 45.0119
492.0625 | 123.587 | -60.6812 | 62.6175 | 0.0024415 | 0.0017261 | 0.00052971 | 0.00052342 | -0.0013778 | 0.0029886 | -0.002021 | -0.12848 | -0.00051262 | 0.034113 | 0.032249 | -0.00043794 | -0.00078189 | 0.0019931 | -7.0541 | 62.7045 | -60.9283 | 62.5442 | 61.9904 | -60.4111 | 0.53101 | -15.6418 | 62.6816 | -60.7681 | 62.7411 | -0.045776 | -60.6674 | -60.2692 | -0.24719 | 0.086975 | -0.073243 | 122.6715 | 61.2122 | 0.27008 | 61.4594 | 0.51727 | -0.086975 | 0.064087 | 0.1236 | 60.6354 | 0.41199 | 0.013733 | 0.49896 | 0.10071 | 122.9187 | 123.4726 | 60.7224 | 123.5092 | 123.6328 | 123.4497 | 123.3856 | 123.3627 | -123.5458 | -123.3856 | 123.2254 | 123.4222 | 53.627 | 45.0394
492.9844 | 123.5687 | -60.6812 | 62.6038 | 0.0177 | 1.7082e-05 | 0.0013843 | 0.0020188 | 0.0020402 | -2.232e-06 | -9.8356e-05 | -0.024719 | 0.00034178 | 0.0339 | 0.037803 | -0.0034287 | 0.0015679 | 0.0030613 | -7.2372 | 62.6999 | -60.965 | 62.4847 | 62.0041 | -60.9329 | 0.36621 | -15.9576 | 62.6633 | -60.8047 | 62.709 | -0.12817 | -60.7224 | -60.26 | -0.28381 | 0.09613 | -0.11902 | 122.6852 | 61.0474 | -0.25177 | 61.3312 | 0.032044 | -0.1236 | 0.059509 | 0.10529 | 60.553 | 0.42114 | -0.041199 | 0.54474 | 0.082398 | 122.9691 | 123.4497 | 60.6766 | 123.5138 | 123.6649 | 123.468 | 123.381 | 123.3444 | -123.5687 | -123.4085 | 123.1659 | 123.3902 | 53.4439 | 44.7235
494.0469 | 123.4726 | -60.6995 | 62.6312 | -0.020447 | -0.00083732 | 0.00095711 | 0.0026596 | 0.0035354 | 0.0029886 | -9.8356e-05 | -0.055237 | -8.5416e-05 | 0.034754 | 0.039084 | -0.0025741 | 0.0017817 | -0.00014315 | -7.3883 | 62.7274 | -60.965 | 62.4207 | 61.9171 | -60.9924 | 0.3891 | -16.1774 | 62.7182 | -60.7773 | 62.6587 | -0.24261 | -60.8231 | -60.3653 | -0.2655 | 0.09613 | -0.21057 | 122.6166 | 61.0886 | -0.29297 | 61.3541 | -0.027466 | -0.07782 | 0.086975 | 0.027465 | 60.4568 | 0.33417 | -0.1236 | 0.41199 | -0.045776 | 122.8821 | 123.3856 | 60.5347 | 123.436 | 123.6923 | 123.4955 | 123.4268 | 123.4177 | -123.5962 | -123.4085 | 123.1201 | 123.3582 | 53.3112 | 44.5221
494.9844 | 123.5687 | -60.6674 | 62.6175 | -0.073852 | 0.00023068 | -0.0024609 | 0.00073702 | -0.003514 | -0.00085663 | 0.0018242 | 0.033264 | -0.0017944 | 0.034541 | 0.032249 | -0.0023605 | -0.0031317 | 0.0022067 | -7.5302 | 62.6862 | -60.9421 | 62.4619 | 61.9537 | -60.9192 | 0.58594 | -16.3193 | 62.6862 | -60.7681 | 62.6999 | -0.16937 | -60.7269 | -60.3012 | -0.27466 | 0.068664 | -0.15564 | 122.6212 | 61.2534 | -0.25177 | 61.528 | 0.022889 | -0.10071 | 0.068664 | 0.082397 | 60.498 | 0.36621 | -0.05951 | 0.46692 | 0.041198 | 122.8958 | 123.4039 | 60.5988 | 123.468 | 123.6282 | 123.4543 | 123.3536 | 123.3536 | -123.5596 | -123.3856 | 123.1293 | 123.3673 | 53.1372 | 44.3481
496.0469 | 123.5733 | -60.6583 | 62.6541 | -0.16541 | 0.0015125 | -0.00032469 | 0.0011642 | -9.604e-05 | 0.0012796 | -0.0026618 | 0.0088501 | -0.00051262 | 0.031977 | 0.033744 | -0.0025741 | -0.0037725 | -0.00099755 | -7.4936 | 62.7731 | -60.9192 | 62.5534 | 62.0682 | -60.8185 | 0.77362 | -16.3605 | 62.709 | -60.7727 | 62.7319 | -0.10529 | -60.6445 | -60.2509 | -0.26093 | 0.11902 | -0.10071 | 122.7264 | 61.4319 | -0.16022 | 61.6928 | 0.10071 | -0.11444 | 0.054931 | 0.07782 | 60.553 | 0.40741 | 0.013733 | 0.52185 | 0.12817 | 122.9874 | 123.4726 | 60.6674 | 123.5046 | 123.6923 | 123.4818 | 123.4314 | 123.3673 | -123.5733 | -123.4268 | 123.2117 | 123.3902 | 53.1647 | 44.2978
497 | 123.5321 | -60.6583 | 62.7457 | 0.071106 | -0.00062372 | -0.0018201 | 0.001805 | -9.604e-05 | -0.0014974 | -0.002021 | -0.015564 | 0.0022644 | 0.034113 | 0.028617 | -0.0019333 | -0.0027045 | 0.00049765 | -7.6401 | 62.7777 | -60.9146 | 62.4435 | 61.908 | -60.9238 | 0.81024 | -16.713 | 62.7594 | -60.7636 | 62.645 | -0.19226 | -60.7178 | -60.1685 | -0.25635 | 0.032043 | -0.30212 | 122.5662 | 61.4685 | -0.2655 | 61.7249 | -0.009155 | -0.10529 | 0.013732 | -0.10071 | 60.466 | 0.48981 | -0.059509 | 0.59509 | 0.045777 | 122.8226 | 123.3582 | 60.5713 | 123.4085 | 123.6923 | 123.5229 | 123.436 | 123.4177 | -123.6603 | -123.5092 | 123.1018 | 123.3032 | 53.0182 | 43.9453
498.0625 | 123.5916 | -60.6537 | 62.6495 | -0.035705 | 0.0015125 | 0.0013843 | 0.0011642 | 0.00033116 | -0.001711 | -0.00138 | -0.027771 | -8.5416e-05 | 0.033045 | 0.034171 | -0.0012923 | -0.00014089 | 0.0047703 | -7.6675 | 62.709 | -60.9558 | 62.5168 | 61.9583 | -60.9055 | 1.0071 | -16.8823 | 62.6678 | -60.7819 | 62.7548 | -0.13275 | -60.6857 | -60.2325 | -0.30212 | 0.059509 | -0.13275 | 122.612 | 61.6608 | -0.25177 | 61.9629 | 0.050354 | -0.12817 | 0.018311 | 0.10529 | 60.5209 | 0.42114 | -0.032043 | 0.54932 | 0.09613 | 122.9141 | 123.4726 | 60.6491 | 123.5367 | 123.6649 | 123.4497 | 123.3627 | 123.3215 | -123.6053 | -123.4314 | 123.1705 | 123.4085 | 52.9861 | 43.7714
498.9844 | 123.5596 | -60.6674 | 62.6221 | -0.073852 | -0.0016919 | 0.00031611 | 0.00052342 | -0.0013778 | 0.00042517 | 0.00032904 | 0.0088501 | -0.00072642 | 0.032191 | 0.032889 | -0.0025741 | -0.0033453 | 7.0452e-05 | -7.7362 | 62.7457 | -60.9283 | 62.5031 | 61.9354 | -60.9238 | 1.1719 | -17.1295 | 62.7045 | -60.7636 | 62.7274 | -0.15106 | -60.6995 | -60.2554 | -0.26093 | 0.1236 | -0.11902 | 122.6028 | 61.8393 | -0.25635 | 62.1002 | 0.004578 | -0.096131 | 0.082398 | 0.10529 | 60.5164 | 0.41199 | -0.032044 | 0.50812 | 0.064087 | 122.8638 | 123.4314 | 60.6125 | 123.4909 | 123.674 | 123.468 | 123.4131 | 123.3719 | -123.5504 | -123.3856 | 123.1705 | 123.3948 | 52.9312 | 43.5379
500.0625 | 123.5825 | -60.6537 | 62.6358 | -0.058594 | 0.00087168 | -0.00011109 | 0.0020188 | -0.001805 | 0.0017068 | -0.0043708 | -0.06134 | -0.00072642 | 0.032191 | 0.037803 | -0.0021469 | -0.00056829 | 0.00071145 | -7.6904 | 62.6953 | -60.9192 | 62.5397 | 61.9812 | -60.8734 | 1.3733 | -17.1844 | 62.6678 | -60.7681 | 62.7502 | -0.091553 | -60.704 | -60.2646 | -0.2655 | 0.059509 | -0.09613 | 122.6349 | 62.027 | -0.21973 | 62.2925 | 0.045776 | -0.11444 | 0.032044 | 0.11444 | 60.5621 | 0.3891 | -0.050354 | 0.50354 | 0.064086 | 122.9004 | 123.4589 | 60.6766 | 123.5184 | 123.6145 | 123.436 | 123.349 | 123.3215 | -123.555 | -123.4039 | 123.1934 | 123.4039 | 52.9633 | 43.4692
501 | 123.5001 | -60.6308 | 62.6816 | 0.0024415 | 1.7082e-05 | 0.00095711 | 0.0037276 | 0.00097196 | 0.00085237 | -0.00052556 | -0.09491 | 0.00141 | 0.030696 | 0.039939 | -0.0012923 | -0.0022773 | -0.00078395 | -7.7042 | 62.7502 | -60.9238 | 62.5076 | 61.9354 | -60.8734 | 1.4877 | -17.4362 | 62.7457 | -60.7361 | 62.7319 | -0.17853 | -60.7224 | -60.2783 | -0.29297 | 0.068664 | -0.17395 | 122.5662 | 62.1185 | -0.24262 | 62.4115 | 0.050354 | -0.10529 | 0.064087 | 0.050354 | 60.4523 | 0.35248 | -0.091553 | 0.45776 | 0.013733 | 122.8592 | 123.4314 | 60.5576 | 123.468 | 123.674 | 123.4818 | 123.381 | 123.3765 | -123.6053 | -123.4177 | 123.1384 | 123.3627 | 52.9266 | 43.1946
502 | 123.4451 | -60.6628 | 62.7365 | -0.012817 | 0.0023669 | 0.00010251 | 0.001805 | -0.0039414 | 0.0038432 | 0.00032904 | 0.011902 | 0.00098258 | 0.032405 | 0.027549 | 0.00020286 | -0.0014227 | -0.00035675 | -7.7728 | 62.8281 | -60.8871 | 62.5031 | 61.9034 | -60.8688 | 1.6617 | -17.6788 | 62.8326 | -60.7224 | 62.6999 | -0.16479 | -60.7224 | -60.3149 | -0.2243 | 0.091553 | -0.23346 | 122.5662 | 62.3245 | -0.20599 | 62.5488 | 0.018311 | -0.059509 | 0.096131 | -0.036621 | 60.498 | 0.3479 | -0.059509 | 0.40741 | 0 | 122.7905 | 123.3902 | 60.5576 | 123.4222 | 123.7152 | 123.555 | 123.4909 | 123.4955 | -123.6237 | -123.4589 | 123.1659 | 123.3627 | 52.89 | 42.984
502.9844 | 123.5504 | -60.6079 | 62.6953 | -0.050964 | 0.0015125 | 0.00074331 | 0.00030982 | 0.00054476 | 0.0014932 | -9.8356e-05 | -0.015564 | 0.00012818 | 0.032405 | 0.032676 | -0.0012923 | -0.00099549 | 0.0013523 | -7.8644 | 62.6816 | -60.9375 | 62.59 | 61.9766 | -60.8505 | 1.8951 | -17.8253 | 62.7045 | -60.7407 | 62.796 | -0.11902 | -60.6445 | -60.2097 | -0.32959 | -0.013732 | -0.10529 | 122.5845 | 62.5031 | -0.24262 | 62.8326 | 0.086975 | -0.13275 | 0.009156 | 0.10071 | 60.4889 | 0.39825 | -0.036621 | 0.53101 | 0.096131 | 122.9141 | 123.5275 | 60.6216 | 123.5367 | 123.6191 | 123.4451 | 123.2895 | 123.3124 | -123.6328 | -123.436 | 123.1979 | 123.4039 | 52.7435 | 42.7826
504.0625 | 123.5641 | -60.5988 | 62.7045 | -0.020447 | 0.00044428 | -0.0022473 | 0.002446 | -0.0033004 | 0.00021157 | 0.00011544 | 0.018005 | -0.00029902 | 0.032832 | 0.033103 | -0.0017197 | 7.2706e-05 | -0.0012111 | -7.8369 | 62.8006 | -60.8917 | 62.5488 | 61.9354 | -60.8459 | 2.0966 | -18.1595 | 62.7731 | -60.704 | 62.7731 | -0.12817 | -60.6491 | -60.228 | -0.29297 | 0.09613 | -0.15564 | 122.5342 | 62.6953 | -0.24719 | 62.9883 | 0.045777 | -0.10529 | 0.068664 | 0.068664 | 60.4706 | 0.37079 | -0.050354 | 0.47607 | 0.054932 | 122.8271 | 123.4406 | 60.5759 | 123.4772 | 123.6923 | 123.4772 | 123.3994 | 123.3719 | -123.5962 | -123.4085 | 123.1476 | 123.3719 | 52.7618 | 42.4393
504.9844 | 123.5733 | -60.5667 | 62.6999 | -0.112 | 0.00087168 | 0.0011707 | 0.00030982 | -0.0026596 | 0.0042704 | -9.8356e-05 | 0.021057 | 0.0011964 | 0.033473 | 0.036521 | -0.0010787 | -0.00035469 | 0.0026341 | -7.7591 | 62.7411 | -60.8917 | 62.4298 | 62.0865 | -60.5942 | 2.2888 | -18.3701 | 62.7686 | -60.6812 | 62.8326 | -0.11444 | -60.5942 | -60.1776 | -0.32501 | 0.041199 | -0.27008 | 122.6532 | 62.8555 | -0.027466 | 63.1805 | 0.29755 | -0.11444 | 0.068665 | 0.13275 | 60.4523 | 0.3891 | -0.027466 | 0.50354 | 0.086975 | 122.9782 | 123.3215 | 60.5667 | 123.5138 | 123.6328 | 123.4497 | 123.3078 | 123.3353 | -123.5916 | -123.381 | 122.9965 | 123.3994 | 52.8076 | 42.1967
505.9844 | 123.5184 | -60.5713 | 62.6862 | -0.066223 | 0.0010853 | 0.00010251 | 0.00095062 | 0.0013992 | -2.232e-06 | 0.00096984 | -0.015564 | -0.00051262 | 0.033473 | 0.035453 | -0.0036423 | -0.0012091 | 7.0452e-05 | -7.7499 | 62.7823 | -60.8505 | 62.5854 | 61.972 | -60.8139 | 2.536 | -18.631 | 62.764 | -60.672 | 62.8006 | -0.1236 | -60.6354 | -60.2005 | -0.27924 | 0.096131 | -0.10071 | 122.5433 | 63.1073 | -0.24262 | 63.3865 | 0.036621 | -0.10071 | 0.07782 | 0.11444 | 60.4477 | 0.37079 | -0.064087 | 0.4715 | 0.036621 | 122.8226 | 123.436 | 60.5484 | 123.4726 | 123.6328 | 123.436 | 123.3536 | 123.3353 | -123.5367 | -123.3582 | 123.1567 | 123.3719 | 52.8214 | 41.9403
507.0625 | 123.5046 | -60.553 | 62.7823 | 0.0024415 | 0.0015125 | 0.00095711 | 0.004155 | 0.00075836 | -0.0012838 | 0.0033196 | -0.04303 | 0.0018372 | 0.034968 | 0.039939 | -0.0015059 | -0.0022773 | 0.0019931 | -7.695 | 62.8647 | -60.8459 | 62.5809 | 61.9217 | -60.8002 | 2.7603 | -18.8324 | 62.8738 | -60.6354 | 62.8006 | -0.11444 | -60.6262 | -60.1868 | -0.29297 | 0.082397 | -0.20142 | 122.4747 | 63.3133 | -0.24719 | 63.6063 | 0.045776 | -0.082397 | 0.091552 | 0.01831 | 60.4385 | 0.36621 | -0.073242 | 0.44861 | 0.009155 | 122.7676 | 123.4268 | 60.5209 | 123.436 | 123.7106 | 123.5092 | 123.4177 | 123.4268 | -123.6282 | -123.4177 | 123.1339 | 123.3536 | 52.858 | 41.7206
507.9844 | 123.5229 | -60.5759 | 62.7502 | -0.035705 | -0.00041012 | 0.0013843 | 0.00030982 | -0.0037276 | 0.0019204 | 0.00075624 | 0.0057983 | -0.00029902 | 0.033686 | 0.033958 | 0.00020286 | 0.00049991 | -0.0031339 | -7.6904 | 62.8372 | -60.8414 | 62.59 | 61.94 | -60.7681 | 3.035 | -18.9606 | 62.8052 | -60.6766 | 62.8372 | -0.086975 | -60.5988 | -60.1685 | -0.2655 | 0.086975 | -0.16022 | 122.5159 | 63.6108 | -0.19226 | 63.8763 | 0.073243 | -0.10071 | 0.054932 | 0.086975 | 60.4889 | 0.40741 | -0.022888 | 0.50812 | 0.07782 | 122.7814 | 123.4314 | 60.5896 | 123.5138 | 123.6786 | 123.4818 | 123.4131 | 123.381 | -123.5916 | -123.4268 | 123.1659 | 123.4131 | 52.8854 | 41.6153
509.0469 | 123.4818 | -60.5301 | 62.8052 | -0.012817 | -0.0019055 | 0.0011707 | 0.0039414 | 0.0031082 | -0.0025656 | 0.00096984 | -0.024719 | 0.00034178 | 0.032618 | 0.034385 | -0.0010787 | -0.0024909 | 0.00049765 | -7.663 | 62.8784 | -60.8368 | 62.5854 | 61.8759 | -60.7956 | 3.2364 | -19.1483 | 62.8967 | -60.6354 | 62.8143 | -0.1236 | -60.6125 | -60.1776 | -0.3067 | 0.073242 | -0.21973 | 122.406 | 63.7665 | -0.2655 | 64.0732 | 0.041199 | -0.10529 | 0.091553 | 0.009155 | 60.4065 | 0.35248 | -0.082398 | 0.45776 | 0.022888 | 122.7127 | 123.4222 | 60.5118 | 123.4497 | 123.7152 | 123.5321 | 123.4085 | 123.4268 | -123.642 | -123.4406 | 123.1155 | 123.3444 | 52.8671 | 41.3818
509.9844 | 123.587 | -60.5209 | 62.7731 | -0.028076 | 0.0012989 | 0.0015979 | 0.00073702 | 0.0031082 | 0.00063877 | -0.0015936 | -0.015564 | -0.0011536 | 0.034113 | 0.036735 | -0.0017197 | -0.00035469 | -0.0035611 | -7.5989 | 62.8052 | -60.8185 | 62.6678 | 61.9949 | -60.7407 | 3.5248 | -19.313 | 62.8006 | -60.6949 | 62.9059 | -0.068665 | -60.5621 | -60.0952 | -0.29755 | 0.032044 | -0.10528 | 122.5159 | 64.0457 | -0.21973 | 64.3433 | 0.077819 | -0.17395 | 0.027466 | 0.13275 | 60.4523 | 0.42572 | -0.041199 | 0.59967 | 0.13275 | 122.8134 | 123.4863 | 60.6262 | 123.6008 | 123.6237 | 123.4955 | 123.3261 | 123.3215 | -123.5916 | -123.468 | 123.1888 | 123.4268 | 52.9221 | 41.2079
511.0625 | 123.6099 | -60.5164 | 62.8006 | -0.012817 | 0.0010853 | 0.00010251 | 0.0011642 | 0.002681 | -0.00021583 | -0.00052556 | 0.048523 | 0.0020508 | 0.031764 | 0.035026 | -0.0015059 | -0.00099549 | 0.0011387 | -7.5485 | 62.851 | -60.7819 | 62.6724 | 62.0041 | -60.6812 | 3.8223 | -19.4458 | 62.8326 | -60.5988 | 62.9333 | 0.045776 | -60.4843 | -60.0769 | -0.2655 | 0.050354 | -0.12817 | 122.5204 | 64.3387 | -0.16479 | 64.6042 | 0.10071 | -0.082398 | 0.032044 | 0.13275 | 60.5621 | 0.43945 | 0.032043 | 0.52185 | 0.11444 | 122.7859 | 123.4543 | 60.6445 | 123.5321 | 123.6328 | 123.4314 | 123.3673 | 123.349 | -123.5825 | -123.3994 | 123.1888 | 123.4497 | 52.9678 | 41.0706
511.9844 | 123.555 | -60.5438 | 62.764 | -0.058594 | -0.0021191 | -0.00011109 | 9.6222e-05 | -0.0028732 | -0.0014974 | -9.8356e-05 | 0.021057 | 0.00098258 | 0.0339 | 0.035239 | -0.0025741 | -0.0018499 | -0.0014249 | -7.608 | 62.8647 | -60.7636 | 62.6221 | 61.9446 | -60.7269 | 3.9917 | -19.8212 | 62.8693 | -60.6125 | 62.8601 | -0.054932 | -60.553 | -60.1181 | -0.21973 | 0.10071 | -0.14191 | 122.4884 | 64.5355 | -0.18311 | 64.7552 | 0.036621 | -0.068665 | 0.10529 | 0.09613 | 60.4889 | 0.42572 | -0.009156 | 0.49439 | 0.059509 | 122.7081 | 123.3856 | 60.5576 | 123.4726 | 123.6282 | 123.4818 | 123.4085 | 123.4131 | -123.5275 | -123.3765 | 123.1659 | 123.4039 | 52.9358 | 40.7227
512.9844 | 123.6053 | -60.4797 | 62.7869 | -0.050964 | 0.0030079 | 0.0013843 | 0.003514 | -0.00073704 | 0.00085237 | 0.0018242 | -0.036926 | -0.0011536 | 0.034968 | 0.036094 | 0.0010575 | 0.0017817 | -0.00035675 | -7.5897 | 62.8281 | -60.8002 | 62.6816 | 61.9812 | -60.6949 | 4.1382 | -19.899 | 62.8281 | -60.6033 | 62.915 | 0.17395 | -60.5026 | -60.1273 | -0.32043 | 0.041199 | -0.10529 | 122.4609 | 64.6179 | -0.21515 | 64.9384 | 0.10529 | -0.1236 | 0.041199 | 0.12817 | 60.6537 | 0.35248 | -0.022889 | 0.47608 | 0.10071 | 122.7814 | 123.4818 | 60.7773 | 123.5184 | 123.6282 | 123.4314 | 123.3078 | 123.3078 | -123.587 | -123.3902 | 123.1613 | 123.3948 | 52.89 | 40.5807
514.0469 | 123.4955 | -60.5164 | 62.8235 | -0.089111 | 0.00065788 | 0.00052971 | 0.0030868 | 0.002681 | -0.00064303 | 0.00054264 | -0.097962 | 0.0016236 | 0.033259 | 0.035239 | -0.0027877 | 0.00071351 | 7.0452e-05 | -7.695 | 62.9059 | -60.8139 | 62.5854 | 61.821 | -60.8185 | 4.2206 | -20.2194 | 62.9196 | -60.6537 | 62.8189 | -0.07782 | -60.6903 | -60.2097 | -0.29755 | 0.082398 | -0.23804 | 122.3373 | 64.7369 | -0.30212 | 65.0345 | -0.004577 | -0.13733 | 0.096131 | -0.004577 | 60.4385 | 0.3067 | -0.17395 | 0.44403 | -0.036621 | 122.6349 | 123.3994 | 60.5759 | 123.4726 | 123.7198 | 123.5733 | 123.4222 | 123.436 | -123.6374 | -123.4772 | 123.1018 | 123.3353 | 52.8213 | 40.2969
514.9844 | 123.5596 | -60.4935 | 62.7869 | -0.112 | 0.00023068 | 0.0022387 | -0.00054478 | -0.0026596 | 0.00021157 | -0.0026618 | -0.0094605 | 0.00098258 | 0.034541 | 0.03054 | -0.00022434 | -0.00014089 | 0.00071145 | -7.6721 | 62.8647 | -60.759 | 62.6907 | 61.9629 | -60.6903 | 4.5319 | -20.3201 | 62.8601 | -60.5713 | 62.9196 | -0.045776 | -60.5347 | -60.0815 | -0.2655 | 0.07782 | -0.09613 | 122.4564 | 65.0253 | -0.19684 | 65.2908 | 0.068664 | -0.07782 | 0.073242 | 0.13275 | 60.4477 | 0.41199 | -0.041199 | 0.48981 | 0.036621 | 122.7219 | 123.4497 | 60.5255 | 123.4909 | 123.6237 | 123.4314 | 123.3582 | 123.3536 | -123.5458 | -123.3582 | 123.1842 | 123.4131 | 52.8213 | 40.1733
516 | 123.4772 | -60.4889 | 62.8784 | -0.043335 | -0.0010511 | -0.00075189 | 0.0013778 | 0.0020402 | 0.0025614 | 0.001397 | -0.018616 | -0.00051262 | 0.033045 | 0.036307 | -0.00065154 | -0.00056829 | 0.0024203 | -7.6813 | 62.9791 | -60.7178 | 62.6312 | 61.8896 | -60.7224 | 4.7012 | -20.5856 | 62.9654 | -60.5759 | 62.8464 | -0.09613 | -60.5438 | -60.1318 | -0.22888 | 0.10071 | -0.24719 | 122.3785 | 65.1901 | -0.23346 | 65.419 | -0.004578 | -0.086975 | 0.086975 | -0.032043 | 60.3928 | 0.35706 | -0.054931 | 0.44403 | 0.032044 | 122.6074 | 123.349 | 60.4797 | 123.4222 | 123.6969 | 123.5413 | 123.468 | 123.4543 | -123.5962 | -123.4543 | 123.1201 | 123.3353 | 52.8076 | 39.9033
516.9844 | 123.555 | -60.4523 | 62.8418 | -0.050964 | -0.00019652 | -0.0013929 | 0.0011642 | -0.0013778 | -0.00085663 | -0.0024482 | 0.021057 | -0.002649 | 0.034327 | 0.035239 | -0.00065154 | -0.00099549 | 0.0043431 | -7.6035 | 62.9013 | -60.7315 | 62.6999 | 61.9492 | -60.6491 | 5.0171 | -20.6863 | 62.9105 | -60.5667 | 62.9562 | -0.004578 | -60.4568 | -60.0311 | -0.27923 | 0.059509 | -0.14191 | 122.4014 | 65.4694 | -0.19684 | 65.7486 | 0.082397 | -0.11444 | 0.068664 | 0.11444 | 60.4477 | 0.42114 | -0.004577 | 0.53558 | 0.10986 | 122.6807 | 123.4314 | 60.5621 | 123.5229 | 123.6328 | 123.4772 | 123.3536 | 123.3627 | -123.5733 | -123.4085 | 123.1522 | 123.4085 | 52.8488 | 39.7659
518.0625 | 123.5367 | -60.4889 | 62.8189 | -0.028076 | 0.0010853 | -0.00096549 | 0.00052342 | 0.0018266 | 0.002775 | 0.00011544 | -0.033875 | -0.0015808 | 0.034754 | 0.037162 | -0.0021469 | 0.00071351 | 0.0013523 | -7.5394 | 62.9013 | -60.7452 | 62.7045 | 61.9537 | -60.6766 | 5.1819 | -20.9381 | 62.8738 | -60.5621 | 62.9059 | -0.045776 | -60.5072 | -60.0769 | -0.25635 | 0.082397 | -0.11444 | 122.4426 | 65.6708 | -0.18768 | 65.9271 | 0.068664 | -0.073242 | 0.054931 | 0.086975 | 60.4431 | 0.41199 | -0.01831 | 0.48523 | 0.054932 | 122.699 | 123.4497 | 60.5164 | 123.468 | 123.6465 | 123.436 | 123.3902 | 123.3627 | -123.5641 | -123.381 | 123.1934 | 123.3948 | 52.9495 | 39.5508
518.9844 | 123.5596 | -60.4614 | 62.8372 | 0.032959 | 1.7082e-05 | -0.00075189 | 0.0026596 | 0.0011856 | -0.00064303 | -0.0018072 | -0.024719 | -0.00094002 | 0.034327 | 0.039512 | -0.0034287 | -0.00099549 | 7.0452e-05 | -7.4982 | 62.8967 | -60.7132 | 62.7182 | 61.9537 | -60.6491 | 5.3558 | -21.0846 | 62.9059 | -60.5804 | 62.9608 | -0.059509 | -60.4843 | -60.0723 | -0.25177 | 0.05951 | -0.11902 | 122.4152 | 65.8173 | -0.18768 | 66.069 | 0.064087 | -0.11902 | 0.068665 | 0.1236 | 60.4019 | 0.3891 | -0.022888 | 0.50812 | 0.09613 | 122.6669 | 123.4314 | 60.5209 | 123.5413 | 123.6099 | 123.4863 | 123.3582 | 123.3673 | -123.5504 | -123.4177 | 123.1796 | 123.4222 | 52.9633 | 39.3768
519.9844 | 123.5962 | -60.4523 | 62.8326 | -0.112 | 0.0027943 | 0.0013843 | 0.0028732 | 0.00033116 | 0.00085237 | -0.0022346 | -0.055237 | 0.0016236 | 0.032191 | 0.040366 | -0.0023605 | 0.00049991 | -0.0029201 | -7.4615 | 62.8784 | -60.7269 | 62.7319 | 61.908 | -60.6583 | 5.5344 | -21.2814 | 62.883 | -60.5759 | 62.9791 | -0.045776 | -60.466 | -60.0403 | -0.27466 | 0.045776 | -0.10071 | 122.3602 | 65.9866 | -0.20599 | 66.2613 | 0.068665 | -0.1236 | 0.050354 | 0.14648 | 60.4065 | 0.41199 | -0.013732 | 0.53558 | 0.10986 | 122.6349 | 123.4589 | 60.5301 | 123.555 | 123.6053 | 123.4589 | 123.3307 | 123.3353 | -123.5596 | -123.4085 | 123.1842 | 123.4314 | 52.9907 | 39.1708
521.0625 | 123.4497 | -60.4431 | 62.9333 | -0.020447 | -0.00041012 | 0.0015979 | 0.003514 | 0.002681 | 0.0034158 | -0.00031196 | -0.10712 | 0.00076898 | 0.03625 | 0.033317 | -0.0030013 | 0.0022089 | -0.00057035 | -7.5714 | 63.0203 | -60.6995 | 62.7045 | 61.8347 | -60.704 | 5.6213 | -21.579 | 63.0478 | -60.5301 | 62.9059 | -0.15106 | -60.585 | -60.1135 | -0.25635 | 0.086975 | -0.22888 | 122.2778 | 66.0645 | -0.26093 | 66.3208 | -0.004578 | -0.086975 | 0.11444 | -0.027466 | 60.2921 | 0.32959 | -0.14191 | 0.41656 | -0.054932 | 122.5342 | 123.4039 | 60.379 | 123.436 | 123.7198 | 123.5779 | 123.4634 | 123.4909 | -123.6328 | -123.4634 | 123.1476 | 123.349 | 52.8717 | 38.8641
521.9844 | 123.6099 | -60.4294 | 62.8967 | -0.043335 | 0.00023068 | -0.0011793 | 0.00073702 | -0.0015914 | 0.0025614 | 0.00032904 | 0.048523 | -0.0013672 | 0.036036 | 0.033317 | 0.00063026 | -0.0014227 | 7.0452e-05 | -7.6584 | 62.9745 | -60.6583 | 62.7686 | 62.0041 | -60.5438 | 5.9372 | -21.5057 | 62.9471 | -60.4935 | 63.0341 | 0.064087 | -60.347 | -59.9442 | -0.22888 | 0.077819 | -0.12817 | 122.4335 | 66.3666 | -0.11444 | 66.5955 | 0.11444 | -0.064087 | 0.050354 | 0.13733 | 60.4935 | 0.48523 | 0.082397 | 0.54932 | 0.14648 | 122.6624 | 123.4268 | 60.5576 | 123.5275 | 123.6328 | 123.4406 | 123.4039 | 123.3765 | -123.555 | -123.3902 | 123.1979 | 123.4634 | 52.771 | 38.9236
522.9844 | 123.5367 | -60.4477 | 62.883 | -0.073852 | 0.0019397 | 0.00052971 | 0.00052342 | -9.604e-05 | 0.001066 | -0.0024482 | 0.0027465 | -0.00094002 | 0.034968 | 0.031608 | -0.0017197 | -0.0012091 | 0.0026341 | -7.8049 | 62.9379 | -60.7086 | 62.7182 | 61.8805 | -60.6445 | 5.9784 | -21.8674 | 62.9562 | -60.5392 | 62.9562 | -0.045776 | -60.4431 | -60.0174 | -0.26093 | 0.054931 | -0.16479 | 122.3282 | 66.4261 | -0.19684 | 66.687 | 0.064087 | -0.091553 | 0.073242 | 0.073242 | 60.4019 | 0.4303 | 0.004578 | 0.52185 | 0.096131 | 122.5891 | 123.4268 | 60.4935 | 123.4955 | 123.6465 | 123.4955 | 123.3856 | 123.4039 | -123.5916 | -123.4222 | 123.1659 | 123.4039 | 52.6428 | 38.5803
523.9844 | 123.5367 | -60.4431 | 62.8922 | -0.096741 | -0.00083732 | 0.0015979 | -0.00033118 | -0.0033004 | -0.00042943 | -0.0015936 | -0.00030511 | 0.0016236 | 0.034968 | 0.030112 | -0.0017197 | -0.0018499 | -0.00078395 | -7.8781 | 62.9745 | -60.6812 | 62.7411 | 61.8805 | -60.6491 | 6.1066 | -22.1191 | 62.9562 | -60.5209 | 62.9608 | -0.032043 | -60.4706 | -60.0128 | -0.23804 | 0.082397 | -0.15106 | 122.3236 | 66.5497 | -0.20599 | 66.7877 | 0.032043 | -0.07782 | 0.064087 | 0.068664 | 60.4111 | 0.4303 | -0.027466 | 0.50812 | 0.050354 | 122.5616 | 123.4222 | 60.4889 | 123.4818 | 123.6557 | 123.4772 | 123.4177 | 123.3994 | -123.5733 | -123.4131 | 123.1842 | 123.4039 | 52.565 | 38.324
525.0469 | 123.6008 | -60.4248 | 62.8601 | -0.012817 | 0.0015125 | 0.0013843 | 0.002446 | 0.0033218 | 0.00021157 | 0.0022516 | -0.055237 | 0.00076898 | 0.033259 | 0.039512 | -0.0012923 | 0.00028631 | -0.00078395 | -7.9559 | 62.9562 | -60.6857 | 62.7457 | 61.8576 | -60.6491 | 6.2256 | -22.2885 | 62.9379 | -60.5301 | 63.002 | -0.022888 | -60.4294 | -59.9762 | -0.26093 | 0.096131 | -0.11444 | 122.2824 | 66.6504 | -0.2243 | 66.9113 | 0.036621 | -0.10529 | 0.07782 | 0.14191 | 60.4019 | 0.44861 | -0.004577 | 0.55389 | 0.10071 | 122.5433 | 123.4314 | 60.5072 | 123.5321 | 123.642 | 123.468 | 123.381 | 123.3627 | -123.5458 | -123.3902 | 123.1705 | 123.4268 | 52.4689 | 38.1363
525.9844 | 123.5641 | -60.4065 | 62.8922 | -0.058594 | -0.00041012 | 0.00074331 | 0.0020188 | 0.00011756 | 0.001066 | -0.0011664 | 0.0027465 | 0.00034178 | 0.036036 | 0.035667 | -0.0019333 | -0.0016363 | -0.0016385 | -8.0017 | 62.9883 | -60.6766 | 62.764 | 61.8713 | -60.6125 | 6.34 | -22.4167 | 62.9608 | -60.5072 | 62.9837 | 0 | -60.4202 | -60.0128 | -0.27008 | 0.09613 | -0.12817 | 122.2778 | 66.7465 | -0.20599 | 67.0166 | 0.064087 | -0.10071 | 0.068664 | 0.091553 | 60.4065 | 0.39368 | -0.013733 | 0.49439 | 0.086975 | 122.5479 | 123.4406 | 60.5072 | 123.4909 | 123.6649 | 123.468 | 123.3948 | 123.3673 | -123.5687 | -123.3994 | 123.1705 | 123.3902 | 52.4048 | 37.9898
527.0625 | 123.468 | -60.4065 | 62.9745 | -0.020447 | 0.0015125 | -0.00096549 | 0.0013778 | 0.0011856 | -0.0010702 | -0.00073916 | -0.027771 | 0.0016236 | 0.034968 | 0.037589 | -0.0017197 | 0.00028631 | 0.0011387 | -8.0795 | 63.0386 | -60.6262 | 62.764 | 61.8988 | -60.5896 | 6.4362 | -22.5906 | 63.0478 | -60.4706 | 62.9379 | -0.073242 | -60.4385 | -60.0357 | -0.21973 | 0.064087 | -0.21057 | 122.3053 | 66.8427 | -0.18311 | 67.0624 | 0.036621 | -0.064087 | 0.073243 | -0.036621 | 60.3333 | 0.37079 | -0.032044 | 0.43488 | 0.032043 | 122.525 | 123.3902 | 60.3973 | 123.4085 | 123.6649 | 123.5184 | 123.4451 | 123.4543 | -123.6008 | -123.4451 | 123.1705 | 123.3444 | 52.327 | 37.8159
528 | 123.4909 | -60.3973 | 62.9791 | 0.010071 | -0.0023327 | 0.00010251 | 0.0030868 | 0.0024674 | -0.0027792 | 0.00075624 | -0.070496 | 0.0016236 | 0.036036 | 0.035453 | -0.0010787 | 0.0011407 | 0.0013523 | -8.139 | 63.0386 | -60.6812 | 62.7731 | 61.8576 | -60.5896 | 6.5277 | -22.728 | 63.0386 | -60.4752 | 63.0203 | -0.036621 | -60.4294 | -59.9945 | -0.28381 | 0.059509 | -0.20599 | 122.2549 | 66.925 | -0.19226 | 67.2089 | 0.091552 | -0.07782 | 0.059509 | 0.041199 | 60.3607 | 0.40283 | -0.032043 | 0.48065 | 0.045777 | 122.5388 | 123.4543 | 60.4385 | 123.4955 | 123.7198 | 123.5138 | 123.436 | 123.436 | -123.6603 | -123.4543 | 123.1705 | 123.4177 | 52.2583 | 37.6694
528.9844 | 123.587 | -60.3516 | 62.915 | -0.005188 | -0.00041012 | -0.00096549 | 0.00052342 | -0.00095064 | 0.00021157 | -9.8356e-05 | 0.011902 | 0.0016236 | 0.034541 | 0.036735 | -0.00086514 | -0.0012091 | 0.00049765 | -8.226 | 63.0066 | -60.6262 | 62.8143 | 61.9308 | -60.5118 | 6.7062 | -22.9523 | 62.9974 | -60.4568 | 63.0615 | 0.004578 | -60.3195 | -59.9258 | -0.27466 | 0.091553 | -0.10071 | 122.2824 | 67.0578 | -0.16022 | 67.3325 | 0.11444 | -0.10529 | 0.082398 | 0.14648 | 60.3561 | 0.42572 | 0.032043 | 0.53101 | 0.13733 | 122.5571 | 123.4406 | 60.4614 | 123.5184 | 123.6328 | 123.4543 | 123.3582 | 123.349 | -123.5413 | -123.3719 | 123.1659 | 123.4131 | 52.1255 | 37.3993
530.0625 | 123.6191 | -60.4065 | 62.9837 | -0.020447 | 0.0027943 | 0.00010251 | 0.0013778 | 0.0020402 | 0.0038432 | -0.00052556 | -0.012512 | 0.00055538 | 0.034327 | 0.035026 | -0.0025741 | -0.0016363 | 0.0013523 | -8.2626 | 63.002 | -60.6491 | 62.7731 | 61.8393 | -60.585 | 6.752 | -23.259 | 62.9929 | -60.4706 | 62.9883 | -0.082397 | -60.3973 | -59.935 | -0.24262 | 0.01831 | -0.21057 | 122.2458 | 67.1585 | -0.17853 | 67.4011 | 0.064087 | -0.064087 | 0.009155 | 0.004577 | 60.3241 | 0.4715 | 0.009155 | 0.53558 | 0.073242 | 122.4884 | 123.4222 | 60.3882 | 123.4589 | 123.6511 | 123.4634 | 123.4085 | 123.3994 | -123.6328 | -123.4543 | 123.1796 | 123.3948 | 52.1439 | 37.1475
530.9844 | 123.4772 | -60.347 | 62.9837 | 0.048218 | -0.00062372 | 0.00052971 | 0.00095062 | -0.003514 | -0.00085663 | -0.0033026 | 0.011902 | -0.00029902 | 0.0339 | 0.035026 | 0.00020286 | -0.00035469 | -0.00057035 | -8.2306 | 63.0478 | -60.5942 | 62.883 | 61.972 | -60.4523 | 6.9397 | -23.1354 | 63.002 | -60.434 | 63.0707 | -0.013733 | -60.2921 | -59.9121 | -0.24719 | 0.064087 | -0.10071 | 122.319 | 67.2867 | -0.10529 | 67.5339 | 0.14191 | -0.086975 | 0.01831 | 0.086975 | 60.3333 | 0.43488 | 0.054932 | 0.52185 | 0.14191 | 122.5662 | 123.4772 | 60.4202 | 123.5046 | 123.642 | 123.436 | 123.3948 | 123.349 | -123.5779 | -123.4177 | 123.23 | 123.4177 | 52.1164 | 37.2116
532 | 123.4772 | -60.3561 | 62.9974 | 0.040589 | 0.00065788 | -0.00053829 | 0.0013778 | 0.00097196 | -0.001711 | 0.00054264 | -0.088806 | 0.00034178 | 0.033045 | 0.038871 | -0.0015059 | -0.00014089 | -0.0029201 | -8.4457 | 63.0478 | -60.6583 | 62.7548 | 61.7889 | -60.5804 | 6.9489 | -23.2773 | 63.0569 | -60.4568 | 62.9974 | -0.10986 | -60.434 | -59.9762 | -0.30212 | 0.050354 | -0.24262 | 122.1451 | 67.305 | -0.2243 | 67.6071 | 0.07782 | -0.10071 | 0.059509 | 0 | 60.2463 | 0.37994 | -0.07782 | 0.48065 | 0.022888 | 122.4472 | 123.4131 | 60.347 | 123.4543 | 123.7061 | 123.5138 | 123.4039 | 123.4131 | -123.6557 | -123.4543 | 123.111 | 123.3536 | 51.9104 | 37.0789
532.9844 | 123.5275 | -60.3607 | 62.9745 | -0.012817 | 0.00087168 | 0.0011707 | 0.00073702 | -0.0011642 | 0.00021157 | -0.0018072 | -0.0033569 | -0.002008 | 0.034327 | 0.033958 | -0.0019333 | -0.0014227 | -0.0039883 | -8.5922 | 63.0066 | -60.6125 | 62.8418 | 61.8896 | -60.466 | 7.1503 | -22.9889 | 63.0386 | -60.4156 | 63.0341 | -0.050354 | -60.3516 | -59.9533 | -0.25177 | 0.032044 | -0.13275 | 122.2504 | 67.511 | -0.10529 | 67.7628 | 0.14648 | -0.054931 | 0.064087 | 0.05951 | 60.3104 | 0.40741 | 0.009156 | 0.46234 | 0.064087 | 122.5021 | 123.4543 | 60.3653 | 123.4497 | 123.6191 | 123.4543 | 123.3673 | 123.3994 | -123.587 | -123.3902 | 123.2025 | 123.3948 | 51.7685 | 37.3718
533.9844 | 123.5229 | -60.379 | 62.9471 | -0.081482 | 0.0017261 | 0.0026661 | 0.0011642 | 0.0028946 | 0.0014932 | -0.0028754 | -0.00030511 | 0.00055538 | 0.034327 | 0.034598 | -0.00065154 | -0.00056829 | 0.00028405 | -8.931 | 62.9974 | -60.6491 | 62.7731 | 61.8027 | -60.6079 | 7.1503 | -23.053 | 62.9974 | -60.4706 | 62.9837 | -0.1236 | -60.3882 | -59.9533 | -0.27008 | 0.050354 | -0.17395 | 122.1817 | 67.5293 | -0.22888 | 67.7994 | 0.041199 | -0.091553 | 0.050354 | 0.036621 | 60.2554 | 0.42572 | -0.009156 | 0.51727 | 0.082397 | 122.4518 | 123.4222 | 60.347 | 123.4543 | 123.6465 | 123.468 | 123.3765 | 123.3765 | -123.5962 | -123.4177 | 123.1522 | 123.3627 | 51.4481 | 37.326
534.9844 | 123.6053 | -60.3561 | 62.9929 | -0.073852 | -0.00083732 | -0.00075189 | 0.0013778 | -0.003514 | -0.00021583 | 0.00011544 | 0.021057 | 0.00098258 | 0.034754 | 0.038871 | -0.0019333 | -0.00078189 | -0.00057035 | -9.0454 | 63.0432 | -60.6216 | 62.8738 | 61.9171 | -60.4477 | 7.3059 | -22.7005 | 63.0753 | -60.4156 | 63.0981 | -0.041199 | -60.3058 | -59.8892 | -0.2655 | 0.050354 | -0.11902 | 122.2733 | 67.662 | -0.091553 | 67.9276 | 0.17395 | -0.059509 | 0.082397 | 0.10529 | 60.3149 | 0.46692 | 0.050354 | 0.52643 | 0.10986 | 122.5388 | 123.4955 | 60.3745 | 123.5138 | 123.6649 | 123.4909 | 123.3994 | 123.4314 | -123.6145 | -123.4085 | 123.23 | 123.4543 | 51.3107 | 37.6556
536.0625 | 123.6008 | -60.3058 | 62.9883 | -0.020447 | 1.7082e-05 | 0.00074331 | 0.0022324 | 0.00075836 | 0.00021157 | -0.0018072 | 0.030212 | 0.00141 | 0.036463 | 0.033744 | -0.0040695 | -0.00035469 | 0.0024203 | -9.2102 | 63.0707 | -60.5896 | 62.9013 | 61.9034 | -60.4111 | 7.4112 | -23.0896 | 63.0478 | -60.3882 | 63.1027 | -0.022888 | -60.2554 | -59.8618 | -0.28381 | 0.082398 | -0.086975 | 122.2092 | 67.717 | -0.10529 | 68.0008 | 0.17853 | -0.082398 | 0.05951 | 0.11444 | 60.2829 | 0.44403 | 0.050354 | 0.52643 | 0.13275 | 122.493 | 123.4909 | 60.3653 | 123.4909 | 123.6603 | 123.436 | 123.3765 | 123.3536 | -123.5779 | -123.3765 | 123.2071 | 123.4085 | 51.0956 | 37.2162
536.9844 | 123.5413 | -60.2966 | 63.0112 | -0.028076 | -0.0012647 | -0.0013929 | 0.0026596 | 0.00054476 | 0.0014932 | -0.0022346 | 0.0027465 | 0.00034178 | 0.033045 | 0.039725 | -0.0021469 | 0.0013543 | -0.00014315 | -9.3155 | 63.0707 | -60.5759 | 63.121 | 61.9904 | -60.8688 | 7.3929 | -23.3551 | 63.0341 | -60.4156 | 63.0936 | -0.068665 | -60.2737 | -59.8709 | -0.27924 | 0.05951 | 0.10986 | 122.287 | 67.6895 | -0.5722 | 67.9688 | -0.29297 | -0.11902 | 0.022889 | 0.082398 | 60.228 | 0.42572 | 0.022888 | 0.54474 | 0.14191 | 122.5662 | 123.6969 | 60.347 | 123.5092 | 123.6465 | 123.4497 | 123.3673 | 123.3307 | -123.587 | -123.4268 | 123.4177 | 123.3902 | 50.9811 | 36.9415
537.9844 | 123.5001 | -5.7312 | 117.7643 | 0.0177 | -0.00041012 | -0.0022473 | 0.0030868 | -0.0011642 | 0.001066 | -0.00138 | 0.0057983 | 0.00034178 | 0.049922 | 0.030753 | -0.0010787 | -0.0018499 | -0.0042019 | 19.2947 | 117.7185 | -6.0013 | 117.3843 | 115.9927 | -5.7449 | 33.9478 | 22.3892 | 117.778 | -5.8777 | 117.7689 | 54.5517 | -5.5435 | -5.452 | -0.27008 | -0.045776 | -0.37994 | 121.7239 | 39.679 | -0.013733 | 39.949 | 0.25635 | -0.14648 | 0.013733 | 0.004578 | 60.2829 | 0.27924 | 0.18768 | 0.42572 | 0.33417 | 121.994 | 123.3856 | 60.4294 | 123.6465 | 123.7198 | 123.6557 | 123.4497 | 123.5092 | -123.7656 | -123.642 | 123.1155 | 123.5001 | 25.0259 | 28.1204
539.0625 | 123.4818 | -3.0945 | 120.369 | 0.0177 | 0.0032215 | -0.0016065 | 0.0011642 | -0.0022324 | -0.0012838 | -0.00052556 | -0.0033569 | 0.00055538 | 0.05099 | 0.034812 | -0.0027877 | -0.00078189 | -0.00078395 | 18.5211 | 120.4651 | -3.2822 | 120.1218 | 118.7073 | -2.9846 | 36.2549 | 24.7513 | 120.4468 | -3.2227 | 120.4468 | 57.1472 | -2.6733 | -2.7145 | -0.18768 | 0.09613 | -0.24719 | 121.8018 | 39.3494 | 0.10986 | 39.537 | 0.29755 | -0.12817 | 0.077819 | 0.077819 | 60.2417 | 0.37994 | 0.42114 | 0.50812 | 0.54932 | 121.9894 | 123.4039 | 60.3699 | 123.6694 | 123.7473 | 123.6694 | 123.5596 | 123.5413 | -123.6511 | -123.5916 | 123.2162 | 123.5413 | 21.6156 | 27.8458
539.9844 | 123.555 | -2.861 | 120.6162 | 0.032959 | 0.00023068 | -0.0022473 | 0.0013778 | 0.0024674 | 0.001066 | -0.00138 | 0.0027465 | -8.5416e-05 | 0.049708 | 0.032035 | -0.0015059 | -0.0029181 | 0.0041293 | 17.7887 | 120.694 | -3.0991 | 120.2911 | 118.8171 | -2.8381 | 36.8866 | 25.2594 | 120.6528 | -3.0441 | 120.639 | 57.399 | -2.6596 | -2.6138 | -0.23804 | 0.07782 | -0.32501 | 121.6782 | 39.7476 | 0.022888 | 39.9857 | 0.26093 | -0.18311 | 0.036621 | 0.022888 | 60.26 | 0.24719 | 0.20142 | 0.4303 | 0.38452 | 121.9162 | 123.3902 | 60.4431 | 123.6832 | 123.793 | 123.6969 | 123.555 | 123.5138 | -123.7152 | -123.6603 | 123.1522 | 123.5001 | 20.6497 | 28.1204
541.0469 | 123.555 | -2.7695 | 120.7031 | -0.028076 | -0.00019652 | -0.00053829 | 0.0022324 | -0.0028732 | 0.00085237 | 0.0028924 | 0.014954 | 0.0011964 | 0.049708 | 0.033744 | -0.0032149 | -0.0014227 | -0.0020657 | 17.2806 | 120.7809 | -2.9572 | 120.4193 | 118.9636 | -2.6733 | 37.6602 | 25.4471 | 120.7855 | -2.8931 | 120.7764 | 57.5134 | -2.5131 | -2.4536 | -0.18768 | 0.07782 | -0.28381 | 121.7331 | 40.4297 | 0.09613 | 40.6174 | 0.28381 | -0.1236 | 0.082397 | 0.073242 | 60.2829 | 0.31586 | 0.25635 | 0.43945 | 0.37994 | 121.9208 | 123.3765 | 60.4065 | 123.6694 | 123.7381 | 123.6786 | 123.5504 | 123.555 | -123.6603 | -123.5962 | 123.1888 | 123.5458 | 20.05 | 28.2166
542 | 123.4909 | -2.7237 | 120.7901 | 0.048218 | 0.00023068 | -0.0020337 | 0.0037276 | 0.0046036 | 0.00085237 | -0.00031196 | -0.11627 | 0.0033326 | 0.049922 | 0.03588 | -0.0032149 | -0.00099549 | -0.00035675 | 16.8915 | 120.8267 | -2.9617 | 120.4102 | 118.8995 | -2.6871 | 37.9944 | 25.5798 | 120.8771 | -2.8748 | 120.7581 | 57.4402 | -2.5955 | -2.4948 | -0.23804 | 0.036621 | -0.37994 | 121.6232 | 40.7181 | 0.036621 | 40.9561 | 0.27466 | -0.15106 | 0.086975 | -0.032043 | 60.1639 | 0.22888 | 0.12817 | 0.37994 | 0.27924 | 121.8613 | 123.3719 | 60.3149 | 123.6328 | 123.7885 | 123.7518 | 123.5504 | 123.6008 | -123.7518 | -123.6649 | 123.1338 | 123.4818 | 19.6152 | 28.3035
543.0469 | 123.587 | -2.6093 | 120.8908 | 0.032959 | -0.0016919 | -0.00032469 | 0.0013778 | 0.0013992 | -2.232e-06 | 0.00011544 | 0.024109 | 0.00055538 | 0.051417 | 0.032676 | -0.00022434 | -0.0016363 | 0.00071145 | 16.713 | 120.9641 | -2.7786 | 120.607 | 119.101 | -2.504 | 38.6765 | 25.6256 | 120.9412 | -2.7466 | 120.9366 | 57.6462 | -2.3254 | -2.2659 | -0.16937 | 0.073242 | -0.28381 | 121.7102 | 41.2857 | 0.10529 | 41.4551 | 0.27466 | -0.13733 | 0.050354 | 0.045776 | 60.2554 | 0.34332 | 0.28381 | 0.48065 | 0.42114 | 121.8796 | 123.3856 | 60.3928 | 123.6832 | 123.7427 | 123.6877 | 123.5733 | 123.5504 | -123.6694 | -123.6374 | 123.2162 | 123.5458 | 19.3222 | 28.2349
543.9844 | 123.5046 | -2.4673 | 121.0007 | -0.005188 | 0.0017261 | -0.0016065 | 0.0022324 | -0.002446 | 0.0029886 | -0.0026618 | -0.015564 | 0.0020508 | 0.052058 | 0.033744 | -0.0021469 | -0.00099549 | 0.0024203 | 16.7267 | 121.0922 | -2.6642 | 120.7077 | 119.1788 | -2.3804 | 39.1708 | 25.4745 | 121.0922 | -2.6138 | 121.0373 | 57.6874 | -2.243 | -2.1973 | -0.19684 | 0.091553 | -0.29297 | 121.6461 | 41.6382 | 0.086975 | 41.835 | 0.28381 | -0.14648 | 0.091553 | 0.036621 | 60.1547 | 0.27008 | 0.2243 | 0.41656 | 0.37079 | 121.843 | 123.3719 | 60.3012 | 123.6511 | 123.7564 | 123.7061 | 123.5596 | 123.5596 | -123.6649 | -123.6145 | 123.175 | 123.5046 | 19.194 | 27.9419
544.9844 | 123.4772 | -2.4307 | 121.0739 | -0.020447 | 0.0017261 | -0.0020337 | 0.003514 | 0.002681 | 0.0014932 | -9.8356e-05 | -0.070496 | 0.00141 | 0.051417 | 0.035667 | -0.0012923 | 0.00071351 | 0.00049765 | 16.9464 | 121.1929 | -2.6276 | 120.694 | 119.0506 | -2.4078 | 39.7705 | 25.3784 | 121.1975 | -2.5726 | 121.0648 | 57.6828 | -2.2614 | -2.1744 | -0.19684 | 0.11902 | -0.37994 | 121.4813 | 42.2012 | 0.022888 | 42.3981 | 0.21973 | -0.14191 | 0.1236 | -0.009156 | 60.1135 | 0.25635 | 0.16937 | 0.39826 | 0.31128 | 121.6782 | 123.3215 | 60.2554 | 123.6374 | 123.8205 | 123.7701 | 123.6237 | 123.6282 | -123.7015 | -123.6465 | 123.1247 | 123.4955 | 19.3771 | 27.8091
546.0625 | 123.4497 | -2.3254 | 121.1929 | 0.0177 | 0.00065788 | -0.00053829 | 0.0026596 | 0.0048172 | -0.00085663 | -9.8356e-05 | -0.06134 | 0.0011964 | 0.053767 | 0.036307 | -0.0010787 | 7.2706e-05 | 0.0013523 | 17.4545 | 121.3669 | -2.4765 | 120.7993 | 119.0689 | -2.33 | 40.5167 | 25.3189 | 121.3074 | -2.4628 | 121.1243 | 57.7057 | -2.179 | -2.0874 | -0.15106 | 0.17395 | -0.39368 | 121.3943 | 42.8421 | -0.004578 | 42.9932 | 0.14648 | -0.13733 | 0.11444 | -0.068664 | 60.0311 | 0.23804 | 0.14648 | 0.37537 | 0.28381 | 121.5454 | 123.2758 | 60.1685 | 123.587 | 123.8434 | 123.7701 | 123.6923 | 123.6328 | -123.6694 | -123.6557 | 123.1247 | 123.4497 | 19.78 | 27.6443
546.9844 | 123.4268 | -2.3117 | 121.2112 | 0.032959 | 0.0015125 | -0.00032469 | 0.0028732 | -0.0033004 | -0.00085663 | 0.0035332 | -0.018616 | -8.5416e-05 | 0.053553 | 0.034171 | -0.0015059 | -0.00035469 | 0.0013523 | 17.4088 | 121.3028 | -2.4948 | 120.8038 | 119.0506 | -2.3026 | 40.8966 | 25.1404 | 121.2982 | -2.4582 | 121.1426 | 57.7103 | -2.1606 | -2.0737 | -0.1831 | 0.091552 | -0.40741 | 121.3623 | 43.2083 | 0.009156 | 43.3914 | 0.19226 | -0.14648 | 0.086975 | -0.068665 | 60.022 | 0.23804 | 0.15106 | 0.38452 | 0.29755 | 121.5454 | 123.2986 | 60.1685 | 123.6008 | 123.7976 | 123.7564 | 123.6145 | 123.6099 | -123.7061 | -123.6694 | 123.1155 | 123.4543 | 19.7205 | 27.4521
547.9844 | 123.5184 | -2.243 | 121.2479 | 0.02533 | -0.00019652 | 0.00095711 | 0.0026596 | -0.00030984 | 0.00042517 | 0.00032904 | 0.011902 | 0.0011964 | 0.051631 | 0.03353 | 0.00063026 | 0.0011407 | -0.0027065 | 17.5507 | 121.2982 | -2.4399 | 120.9366 | 119.1147 | -2.1561 | 41.2628 | 25.2686 | 121.3257 | -2.4033 | 121.2479 | 57.8018 | -2.0462 | -1.9592 | -0.19684 | 0.050354 | -0.31128 | 121.3577 | 43.5059 | 0.086975 | 43.7027 | 0.28381 | -0.16022 | 0.07782 | 0 | 60.0449 | 0.28381 | 0.19684 | 0.44403 | 0.35705 | 121.5546 | 123.3765 | 60.2051 | 123.6511 | 123.7381 | 123.7289 | 123.5413 | 123.5687 | -123.6877 | -123.6511 | 123.1796 | 123.4909 | 19.7937 | 27.5116
549.0625 | 123.4772 | -2.243 | 121.2936 | -0.035705 | 0.0012989 | 0.00031611 | 0.0045822 | -9.604e-05 | 0.00021157 | 0.001397 | -0.039978 | 0.0018372 | 0.05334 | 0.039084 | -0.0025741 | -0.0018499 | 0.00028405 | 17.5598 | 121.4172 | -2.3941 | 120.8496 | 118.9911 | -2.2018 | 41.4459 | 25.3098 | 121.3715 | -2.3758 | 121.2204 | 57.7377 | -2.0782 | -1.973 | -0.15106 | 0.1236 | -0.44403 | 121.2341 | 43.689 | 0.041199 | 43.84 | 0.19226 | -0.13275 | 0.07782 | -0.073242 | 59.9808 | 0.27008 | 0.16479 | 0.40283 | 0.29755 | 121.3852 | 123.2437 | 60.1135 | 123.5962 | 123.8113 | 123.7473 | 123.6603 | 123.6145 | -123.6877 | -123.6694 | 123.0927 | 123.4634 | 19.8029 | 27.5528
549.9844 | 123.5641 | -2.1103 | 121.3486 | -0.012817 | 0.00044428 | 0.0011707 | 0.0026596 | -0.0028732 | -0.00042943 | -0.003089 | 0.021057 | 0.00055538 | 0.049708 | 0.033744 | -0.00065154 | 0.00092711 | 0.00092505 | 17.7429 | 121.4447 | -2.3026 | 121.0602 | 119.1925 | -2.005 | 41.7847 | 25.621 | 121.4081 | -2.2751 | 121.4035 | 57.9117 | -1.799 | -1.7532 | -0.19226 | 0.09613 | -0.28839 | 121.3028 | 43.895 | 0.10529 | 44.0872 | 0.29755 | -0.16479 | 0.059509 | 0.054931 | 60.022 | 0.35706 | 0.31128 | 0.52185 | 0.47607 | 121.4951 | 123.3627 | 60.1868 | 123.6786 | 123.7473 | 123.6832 | 123.555 | 123.5184 | -123.6511 | -123.6237 | 123.1705 | 123.5138 | 19.8532 | 27.7313
550.9844 | 123.4726 | -2.1011 | 121.4493 | 0.032959 | 0.0015125 | 0.00052971 | 0.002446 | 0.00097196 | -0.0036336 | -0.0026618 | -0.06134 | 0.0039734 | 0.050135 | 0.03588 | 0.00020286 | 0.0013543 | 0.0022067 | 17.7979 | 121.5454 | -2.2797 | 121.1151 | 118.8629 | -2.1286 | 41.7343 | 25.5936 | 121.5637 | -2.1973 | 121.3669 | 57.8247 | -1.9363 | -1.8356 | -0.17853 | 0.09613 | -0.33417 | 120.9641 | 43.8354 | -0.027466 | 44.014 | 0.15106 | -0.096131 | 0.11444 | -0.082398 | 59.9258 | 0.2655 | 0.1648 | 0.36163 | 0.26093 | 121.1426 | 123.3948 | 60.022 | 123.5641 | 123.8251 | 123.761 | 123.6465 | 123.6649 | -123.7289 | -123.6465 | 123.2162 | 123.468 | 19.899 | 27.6947
552.0625 | 123.4634 | -2.0782 | 121.4722 | -0.020447 | 0.0017261 | 0.0013843 | 0.005223 | 0.0031082 | -2.232e-06 | 0.00054264 | -0.22308 | 0.003119 | 0.050349 | 0.034812 | -0.0010787 | 0.00028631 | 0.0017795 | 18.0954 | 121.5317 | -2.2934 | 121.0098 | 118.8675 | -2.1011 | 41.8396 | 25.9003 | 121.5912 | -2.1927 | 121.3898 | 57.8064 | -1.9592 | -1.799 | -0.21515 | 0.059509 | -0.46234 | 120.9457 | 43.9178 | -0.022888 | 44.133 | 0.19226 | -0.11444 | 0.11902 | -0.082397 | 59.8846 | 0.27924 | 0.11902 | 0.39368 | 0.23346 | 121.1609 | 123.3032 | 59.9991 | 123.5825 | 123.8251 | 123.7839 | 123.6099 | 123.6694 | -123.7656 | -123.6649 | 123.0881 | 123.468 | 20.1736 | 27.9785
552.9844 | 123.4863 | -2.0279 | 121.4905 | 0.02533 | -0.00041012 | -0.00032469 | 0.0030868 | 0.0035354 | 0.00021157 | -0.0018072 | -0.024719 | 0.0011964 | 0.052271 | 0.03588 | -0.0023605 | 0.00092711 | 0.0015659 | 18.425 | 121.5958 | -2.2293 | 121.0739 | 118.84 | -1.9867 | 42.0959 | 26.0422 | 121.5637 | -2.1881 | 121.4447 | 57.8384 | -1.8173 | -1.6983 | -0.20142 | 0.10529 | -0.41656 | 120.8679 | 44.1238 | 0.041199 | 44.3253 | 0.24262 | -0.16022 | 0.073242 | -0.045777 | 59.8663 | 0.32959 | 0.21057 | 0.48981 | 0.37079 | 121.0693 | 123.3032 | 60.0266 | 123.6328 | 123.8251 | 123.7518 | 123.6237 | 123.5916 | -123.7198 | -123.6786 | 123.1018 | 123.4726 | 20.4529 | 28.0701
554.0625 | 123.4818 | -1.9592 | 121.5271 | -0.005188 | 1.7082e-05 | 0.0026661 | 0.0028732 | 0.002681 | 0.0038432 | 0.0018242 | -0.030823 | 0.00141 | 0.050776 | 0.036735 | -0.0036423 | -0.00035469 | 0.0039157 | 18.7866 | 121.5866 | -2.1973 | 121.1334 | 118.7439 | -1.9592 | 42.2379 | 26.4999 | 121.637 | -2.1149 | 121.4996 | 57.8567 | -1.7807 | -1.6571 | -0.23804 | 0.059509 | -0.39368 | 120.7031 | 44.1971 | 0 | 44.4351 | 0.23804 | -0.15564 | 0.10986 | -0.027466 | 59.816 | 0.30213 | 0.17853 | 0.45776 | 0.33417 | 120.9412 | 123.3307 | 59.9716 | 123.6145 | 123.7839 | 123.7518 | 123.5458 | 123.5962 | -123.7244 | -123.642 | 123.0927 | 123.4589 | 20.7459 | 28.4592
554.9844 | 123.4818 | -1.9867 | 121.5271 | 0.24658 | -0.00041012 | 0.0052295 | 0.0013778 | -0.0015914 | 0.0025614 | -0.0018072 | -0.0094605 | 0.0026916 | 0.052485 | 0.037589 | -0.0017197 | -0.00035469 | 0.0030613 | 19.0475 | 121.6782 | -2.1378 | 121.106 | 118.6249 | -1.9272 | 42.3889 | 26.3443 | 121.6324 | -2.1286 | 121.4813 | 57.8384 | -1.7761 | -1.6617 | -0.15106 | 0.15106 | -0.42114 | 120.6116 | 44.3756 | 0.059509 | 44.5267 | 0.21057 | -0.14191 | 0.10528 | -0.045777 | 59.8251 | 0.32501 | 0.21057 | 0.46692 | 0.35248 | 120.7626 | 123.2437 | 59.967 | 123.6099 | 123.8159 | 123.761 | 123.6649 | 123.6191 | -123.6649 | -123.6557 | 123.0927 | 123.468 | 21.0342 | 28.331
556.0625 | 123.5001 | -1.9775 | 121.5408 | 0.010071 | 0.0019397 | 0.00074331 | 0.0047958 | -0.0022324 | 0.0023478 | 0.00032904 | -0.039978 | 0.00141 | 0.05099 | 0.036094 | -0.00065154 | 0.00028631 | 0.0032749 | 19.4595 | 121.6415 | -2.1744 | 121.138 | 118.5287 | -1.9135 | 42.4576 | 26.4587 | 121.6415 | -2.092 | 121.5042 | 57.8201 | -1.7441 | -1.6159 | -0.19684 | 0.10071 | -0.40283 | 120.5063 | 44.4351 | 0.064087 | 44.632 | 0.26092 | -0.11444 | 0.10071 | -0.036622 | 59.7977 | 0.36163 | 0.23346 | 0.47607 | 0.3479 | 120.7031 | 123.3124 | 59.9121 | 123.5962 | 123.8159 | 123.7335 | 123.6191 | 123.6191 | -123.7152 | -123.6328 | 123.1155 | 123.4817 | 21.4371 | 28.4363
557 | 123.468 | -1.9455 | 121.5546 | -0.005188 | 0.0017261 | 0.0026661 | 0.0047958 | 0.00075836 | -0.0010702 | 0.0022516 | 0.036316 | 0.0050416 | 0.052699 | 0.03353 | -0.00086514 | 0.0013543 | 0.0013523 | 19.7845 | 121.637 | -2.1469 | 121.106 | 118.4921 | -2.2476 | 42.7139 | 26.4862 | 121.6599 | -2.0782 | 121.4996 | 57.8018 | -1.7807 | -1.6251 | -0.20142 | 0.082398 | -0.44861 | 120.4376 | 44.6594 | -0.30212 | 44.8608 | -0.10071 | -0.13275 | 0.10529 | -0.054931 | 59.7473 | 0.32043 | 0.16479 | 0.45319 | 0.29755 | 120.639 | 123.2529 | 59.8801 | 123.5779 | 123.7839 | 123.7381 | 123.5825 | 123.6053 | -123.7015 | -123.6328 | 123.0515 | 123.4451 | 21.73 | 28.4317
558.0625 | 123.4726 | -1.9363 | 121.582 | 0.0177 | -0.00083732 | 0.00031611 | 0.0030868 | 0.0018266 | 0.00063877 | -0.00052556 | -0.073547 | 0.00098258 | 0.053553 | 0.03823 | -0.00043794 | -0.00035469 | 7.0452e-05 | 20.4941 | 121.6919 | -2.1286 | 121.138 | 118.2999 | -1.5381 | 43.4509 | 26.8021 | 121.701 | -2.0508 | 121.5134 | 57.7789 | -1.7029 | -1.6067 | -0.19226 | 0.10986 | -0.44403 | 120.2362 | 45.3873 | 0.39825 | 45.5795 | 0.59052 | -0.11444 | 0.11902 | -0.068664 | 59.7153 | 0.32959 | 0.23346 | 0.44403 | 0.3479 | 120.4285 | 123.2666 | 59.8297 | 123.5641 | 123.8205 | 123.7518 | 123.6282 | 123.6374 | -123.7106 | -123.6328 | 123.0743 | 123.4497 | 22.4304 | 28.7384
558.9844 | 123.4772 | -1.9135 | 121.5958 | -0.020447 | 0.0010853 | 0.0013843 | 0.004155 | 0.0024674 | 0.0017068 | -0.00095276 | -0.024719 | 0.002478 | 0.051844 | 0.032035 | -0.0010787 | 0.0019953 | 7.0452e-05 | 21.0068 | 121.6553 | -2.1103 | 121.2799 | 118.3502 | -1.7853 | 44.2932 | 27.0355 | 121.7285 | -2.0096 | 121.5775 | 57.8156 | -1.68 | -1.5381 | -0.19684 | 0.059509 | -0.31586 | 120.2637 | 46.2067 | 0.12817 | 46.4035 | 0.32501 | -0.096131 | 0.13275 | -0.01831 | 59.729 | 0.37537 | 0.23346 | 0.4715 | 0.32959 | 120.4605 | 123.3902 | 59.8251 | 123.587 | 123.7656 | 123.7381 | 123.5687 | 123.642 | -123.7061 | -123.6053 | 123.1934 | 123.4909 | 22.9202 | 28.949
559.9844 | 123.4726 | -1.9592 | 121.5408 | -0.012817 | 0.0025805 | 0.00074331 | 0.0030868 | -0.0039414 | -0.00042943 | -9.8356e-05 | 0.039368 | 0.0020508 | 0.052485 | 0.036521 | -0.00065154 | 0.00071351 | 0.0066929 | 21.286 | 121.669 | -2.1378 | 121.1517 | 118.0252 | -1.8997 | 44.989 | 26.9073 | 121.6599 | -2.0737 | 121.4859 | 57.7515 | -1.6983 | -1.6113 | -0.17853 | 0.12817 | -0.3891 | 119.9844 | 46.9482 | 0.05951 | 47.1268 | 0.23804 | -0.11444 | 0.11902 | -0.054932 | 59.7107 | 0.3479 | 0.26093 | 0.46234 | 0.37537 | 120.163 | 123.2895 | 59.8251 | 123.5596 | 123.8068 | 123.7335 | 123.6282 | 123.6191 | -123.6786 | -123.6145 | 123.111 | 123.4451 | 23.2452 | 28.8666
561.0625 | 123.4406 | -1.9455 | 121.5775 | 0.0177 | 0.0015125 | 0.0013843 | 0.0045822 | 0.0028946 | 0.0046976 | 0.00032904 | -0.030823 | 0.0020508 | 0.051631 | 0.037376 | -0.00065154 | 0.00049991 | 0.0013523 | 21.4691 | 121.6599 | -2.1423 | 121.1151 | 117.8375 | -1.9501 | 45.6345 | 26.8341 | 121.6873 | -2.0874 | 121.5088 | 57.692 | -1.7578 | -1.6022 | -0.19684 | 0.082397 | -0.46234 | 119.783 | 47.58 | -0.004577 | 47.7768 | 0.19226 | -0.14191 | 0.10986 | -0.068665 | 59.6375 | 0.34332 | 0.18768 | 0.48523 | 0.32959 | 119.9799 | 123.2574 | 59.7794 | 123.5962 | 123.8022 | 123.7747 | 123.6053 | 123.6328 | -123.7198 | -123.6649 | 123.0606 | 123.4543 | 23.4146 | 28.7796
561.9844 | 123.436 | -1.9501 | 121.5454 | -0.005188 | 0.0015125 | 0.00095711 | 0.005864 | -0.00073704 | -0.001711 | 0.0011834 | -0.039978 | 0.0033326 | 0.050562 | 0.040153 | 0.00063026 | 0.00071351 | -0.00035675 | 21.7484 | 121.669 | -2.1561 | 121.1105 | 117.7368 | -1.9501 | 46.3623 | 26.9302 | 121.6599 | -2.1149 | 121.4859 | 57.6874 | -1.7487 | -1.5884 | -0.20599 | 0.1236 | -0.43488 | 119.6869 | 48.3124 | 0 | 48.5184 | 0.20599 | -0.1648 | 0.11444 | -0.059509 | 59.6375 | 0.36163 | 0.20142 | 0.52643 | 0.36621 | 119.8929 | 123.2666 | 59.8022 | 123.6008 | 123.8251 | 123.7747 | 123.6191 | 123.6099 | -123.7015 | -123.6603 | 123.0606 | 123.436 | 23.6984 | 28.8803
563.0625 | 123.4634 | -1.9684 | 121.5271 | -0.066223 | 0.0012989 | 0.0018115 | 0.0037276 | 0.0018266 | 0.00042517 | 0.0033196 | -0.027771 | 0.0022644 | 0.051631 | 0.037376 | -0.0015059 | 0.0013543 | 0.0045567 | 22.0551 | 121.6507 | -2.1652 | 121.0464 | 117.6224 | -1.6388 | 47.3923 | 26.976 | 121.6507 | -2.0966 | 121.4859 | 57.7469 | -1.7258 | -1.5701 | -0.19684 | 0.1236 | -0.48065 | 119.5908 | 49.3607 | 0.32959 | 49.5575 | 0.52643 | -0.12817 | 0.1236 | -0.041199 | 59.7153 | 0.39825 | 0.24261 | 0.52643 | 0.37079 | 119.7876 | 123.2117 | 59.8434 | 123.5825 | 123.8159 | 123.7473 | 123.6191 | 123.6191 | -123.6923 | -123.6237 | 123.0148 | 123.4543 | 24.0234 | 28.9444
563.9844 | 123.5001 | -1.9135 | 121.5729 | -0.012817 | 0.0021533 | 0.0030933 | 0.0037276 | -0.00052344 | -0.0012838 | -0.00052556 | -0.021668 | 0.0020508 | 0.052912 | 0.042502 | -0.00065154 | -0.0012091 | 0.0034885 | 22.3297 | 121.6507 | -2.1515 | 121.1472 | 117.6224 | -1.8997 | 48.4406 | 27.0859 | 121.6278 | -2.1011 | 121.6095 | 58.0261 | -1.5839 | -1.4923 | -0.23804 | 0.07782 | -0.42572 | 119.5358 | 50.354 | 0.013733 | 50.592 | 0.25177 | -0.18768 | 0.054932 | 0.036621 | 59.9396 | 0.42114 | 0.32959 | 0.60883 | 0.51727 | 119.7739 | 123.2986 | 60.1273 | 123.7106 | 123.8022 | 123.7289 | 123.5641 | 123.5413 | -123.7244 | -123.674 | 123.0606 | 123.5229 | 24.2432 | 28.9993
565.0625 | 123.468 | -1.9547 | 121.5271 | -0.18829 | 0.0036487 | 0.0022387 | 0.0054366 | -0.0011642 | 0.00021157 | 0.00075624 | -0.012512 | 0.0035462 | 0.052271 | 0.036948 | -1.0744e-05 | -0.00035469 | 0.0026341 | 22.5677 | 121.6827 | -2.1378 | 121.0876 | 117.5354 | -1.9501 | 49.4019 | 27.42 | 121.6736 | -2.0966 | 121.5179 | 57.7881 | -1.6754 | -1.5427 | -0.18311 | 0.15564 | -0.43945 | 119.4901 | 51.3565 | 0.004578 | 51.5396 | 0.18768 | -0.14191 | 0.14648 | -0.009156 | 59.7427 | 0.41199 | 0.27924 | 0.55389 | 0.42114 | 119.6732 | 123.2254 | 59.8846 | 123.6145 | 123.8205 | 123.7701 | 123.6374 | 123.6282 | -123.6649 | -123.6237 | 123.0423 | 123.4726 | 24.5224 | 29.3747
565.9844 | 123.468 | -1.9684 | 121.5317 | -0.028076 | 0.0019397 | 0.0011707 | 0.0050094 | 0.00097196 | 0.001066 | 0.0018242 | -0.039978 | 0.0050416 | 0.055476 | 0.042502 | -0.0010787 | 0.00071351 | 0.0077609 | 22.7417 | 121.669 | -2.1469 | 121.1243 | 117.4805 | -1.9363 | 50.235 | 27.7496 | 121.6507 | -2.1011 | 121.4859 | 57.7606 | -1.7029 | -1.5381 | -0.17853 | 0.13733 | -0.40741 | 119.4489 | 52.2034 | 0.032044 | 52.3819 | 0.21057 | -0.13275 | 0.11902 | -0.045776 | 59.729 | 0.4303 | 0.2655 | 0.56305 | 0.39825 | 119.6274 | 123.2712 | 59.8618 | 123.587 | 123.8159 | 123.7518 | 123.6374 | 123.6191 | -123.6786 | -123.6328 | 123.0927 | 123.4543 | 24.7101 | 29.718
567.0625 | 123.5641 | -1.9043 | 121.5363 | 0.010071 | 0.0012989 | 0.0013843 | 0.0039414 | -0.00030984 | 0.0017068 | 0.0011834 | 0.091247 | 0.0018372 | 0.05334 | 0.037162 | -0.0012923 | 0.00092711 | 0.0026341 | 23.1125 | 121.6324 | -2.0691 | 121.2616 | 117.5903 | -1.767 | 51.329 | 28.0838 | 121.6003 | -2.0599 | 121.6232 | 57.9391 | -1.4832 | -1.4008 | -0.1648 | 0.09613 | -0.27466 | 119.4946 | 53.2333 | 0.13733 | 53.3981 | 0.30212 | -0.15564 | 0.064087 | 0.086975 | 59.8434 | 0.50354 | 0.42114 | 0.65918 | 0.57678 | 119.6594 | 123.3307 | 59.9991 | 123.6832 | 123.7015 | 123.6603 | 123.5367 | 123.5046 | -123.6053 | -123.5962 | 123.1659 | 123.5275 | 25.0168 | 29.9881
567.9844 | 123.4955 | -1.9684 | 121.5454 | 0.02533 | 0.00044428 | 0.00095711 | 0.0065048 | -0.0028732 | 0.001066 | -0.00373 | -0.012512 | 0.0037598 | 0.055476 | 0.038016 | -0.0021469 | 0.00092711 | 0.0037021 | 23.4146 | 121.6415 | -2.1606 | 121.0922 | 117.2836 | -1.918 | 52.2766 | 27.8778 | 121.6187 | -2.1103 | 121.4905 | 57.8156 | -1.6342 | -1.506 | -0.19226 | 0.096131 | -0.45319 | 119.252 | 54.245 | 0.050354 | 54.4373 | 0.24262 | -0.14191 | 0.073242 | -0.054931 | 59.7839 | 0.46234 | 0.33417 | 0.60425 | 0.47608 | 119.4443 | 123.2529 | 59.9258 | 123.6008 | 123.8022 | 123.7289 | 123.6099 | 123.587 | -123.7061 | -123.6557 | 123.0606 | 123.4589 | 25.383 | 29.8462
569.0625 | 123.436 | -1.9958 | 121.5408 | -0.035705 | 0.0023669 | 0.0043749 | 0.0067184 | -9.604e-05 | 0.00042517 | -0.0011664 | -0.049133 | 0.0037598 | 0.05398 | 0.036521 | -0.00022434 | 0.0022089 | 0.0030613 | 23.8449 | 121.6278 | -2.1835 | 121.0739 | 117.1875 | -1.973 | 53.5034 | 27.8503 | 121.6232 | -2.1469 | 121.4493 | 57.7286 | -1.7166 | -1.5747 | -0.18768 | 0.086975 | -0.46692 | 119.1834 | 55.4993 | 0.022889 | 55.687 | 0.21057 | -0.15106 | 0.082397 | -0.091553 | 59.7244 | 0.42114 | 0.27924 | 0.5722 | 0.4303 | 119.371 | 123.2574 | 59.8755 | 123.5962 | 123.8113 | 123.7701 | 123.6237 | 123.6191 | -123.7244 | -123.6877 | 123.0698 | 123.4451 | 25.8408 | 29.8462
569.9844 | 123.4634 | -2.0004 | 121.4951 | 0.0024415 | -0.0010511 | 0.00052971 | 0.0043686 | -0.0030868 | -0.00042943 | 0.00054264 | -0.024719 | 0.0046142 | 0.053126 | 0.038016 | -0.0012923 | 0.00092711 | 0.00049765 | 24.1196 | 121.6187 | -2.1835 | 121.1197 | 117.1875 | -1.9226 | 54.538 | 27.9373 | 121.6141 | -2.124 | 121.4859 | 57.7789 | -1.6754 | -1.5518 | -0.18311 | 0.1236 | -0.37537 | 119.1879 | 56.5384 | 0.07782 | 56.7215 | 0.26093 | -0.1236 | 0.11902 | -0.009155 | 59.7794 | 0.44861 | 0.32501 | 0.5722 | 0.44861 | 119.371 | 123.3032 | 59.903 | 123.6099 | 123.8022 | 123.7381 | 123.6191 | 123.6145 | -123.6786 | -123.6191 | 123.1201 | 123.4863 | 26.12 | 29.9377
570.9844 | 123.5321 | -2.037 | 121.5042 | 0.032959 | 0.0030079 | 0.0035205 | 0.0054366 | -0.00052344 | 0.00063877 | 0.00096984 | -0.039978 | 0.0035462 | 0.052699 | 0.042075 | -0.00022434 | 0.0024225 | 0.0041293 | 24.3118 | 121.6187 | -2.2247 | 121.019 | 117.0181 | -2.0187 | 55.3574 | 28.0975 | 121.6003 | -2.179 | 121.431 | 57.724 | -1.712 | -1.5839 | -0.18768 | 0.11444 | -0.48523 | 119.0552 | 57.3944 | 0.01831 | 57.5821 | 0.20599 | -0.14191 | 0.096131 | -0.073242 | 59.761 | 0.45319 | 0.32501 | 0.59509 | 0.46692 | 119.2429 | 123.2437 | 59.903 | 123.6099 | 123.8434 | 123.7793 | 123.6557 | 123.6374 | -123.7289 | -123.6832 | 123.056 | 123.468 | 26.3489 | 30.1346
572.0625 | 123.555 | -2.0554 | 121.3669 | -0.096741 | 0.00087168 | 0.0011707 | 0.0033004 | 0.0031082 | 0.00021157 | -0.003089 | 0.042419 | 0.00076898 | 0.054194 | 0.035453 | -0.00043794 | 0.0015679 | -0.0012111 | 24.733 | 121.4859 | -2.2385 | 121.1334 | 117.0639 | -2.0096 | 56.3919 | -1.9455 | 121.4355 | -2.2476 | 121.4401 | 57.692 | -1.6617 | -1.5747 | -0.1831 | 0.11902 | -0.23346 | 119.1193 | 58.4473 | 0.045776 | 58.6304 | 0.22888 | -0.19226 | 0.068665 | 0.073243 | 59.7473 | 0.48065 | 0.39368 | 0.67291 | 0.58594 | 119.3024 | 123.3719 | 59.9396 | 123.6877 | 123.7244 | 123.6832 | 123.5413 | 123.4909 | -123.6053 | -123.6145 | 123.1888 | 123.4955 | 26.7883 | 0.10986
572.9844 | 123.5641 | -2.0874 | 121.3715 | -0.020447 | 0.00023068 | 0.0020251 | 0.0056504 | -0.0015914 | 0.00063877 | 0.0011834 | -0.015564 | 0.0033326 | 0.05398 | 0.038016 | -0.0034287 | 0.0019953 | 7.0452e-05 | 25.09 | 121.431 | -2.2888 | 121.0144 | 116.9403 | -2.0279 | 57.019 | -1.9913 | 121.4584 | -2.2247 | 121.4355 | 57.6736 | -1.7075 | -1.561 | -0.20142 | 0.059509 | -0.35706 | 119.0277 | 59.1064 | 0.059509 | 59.3079 | 0.26092 | -0.13733 | 0.086975 | 0.064087 | 59.761 | 0.52643 | 0.37994 | 0.66376 | 0.51727 | 119.2291 | 123.3032 | 59.8984 | 123.6603 | 123.7198 | 123.6832 | 123.5184 | 123.5458 | -123.6603 | -123.5962 | 123.1018 | 123.5229 | 27.1774 | 0.09613
573.9844 | 123.4406 | -2.0508 | 121.4355 | -0.012817 | 1.7082e-05 | 0.0024523 | 0.0065048 | -0.00095064 | 0.0025614 | -0.003089 | -0.12238 | 0.10779 | 0.092219 | 0.0034094 | 0.071339 | 0.10261 | 0.0017795 | 25.3876 | 121.5546 | -2.2614 | 120.9824 | 116.7664 | -2.0233 | 57.7652 | -2.0554 | 121.5042 | -2.1973 | 118.4738 | 121.2708 | 121.1243 | 83.0383 | -0.21057 | 0.11902 | -0.45319 | 118.8171 | 59.816 | 0.027466 | 60.0266 | 0.23804 | -0.14648 | 0.068664 | -2.9617 | 123.3215 | 85.0891 | 123.175 | 85.2356 | 123.3215 | 119.0277 | 123.2437 | 123.468 | 120.6711 | 123.8159 | 123.7015 | 123.6053 | 123.555 | -123.6969 | -123.6328 | 123.0331 | 120.5246 | 27.4384 | -0.004578
575.0625 | 123.555 | -3.0808 | 120.2591 | -0.005188 | -0.00041012 | 0.00074331 | 0.0054366 | 0.0016128 | 0.0017068 | -0.0024482 | 0.042419 | 0.012732 | 0.025569 | -0.0019312 | -0.0010787 | -0.00078189 | 0.0032749 | 25.2045 | 120.3598 | -3.3234 | 119.9982 | 115.7684 | -2.9572 | 57.6736 | -2.9846 | -2.742 | -3.1906 | -3.035 | -2.8976 | -3.0441 | -2.916 | -0.24261 | 0.10071 | -0.26093 | 118.8492 | 60.7544 | 0.1236 | 60.997 | 0.36621 | -0.10986 | -123.0011 | -123.2941 | 0.18311 | 0.1648 | 0.036622 | 0.27466 | 0.14648 | 119.0918 | 123.3215 | 0.29297 | 0.15564 | 123.6832 | 0.44861 | 123.4406 | 0.33875 | -123.5825 | -123.4497 | 123.0789 | 0.045777 | 28.2852 | 0.096131
575.9844 | 123.4634 | -1.8036 | 121.6644 | -0.005188 | 0.00087168 | 0.00031611 | 0.005864 | 0.0013992 | 0.0051248 | -0.0011664 | -0.036926 | 0.012732 | 0.024928 | 0.0061866 | -0.0027877 | 0.0013543 | 0.0022067 | 26.2711 | 121.8018 | -1.9684 | 121.2936 | 116.9495 | -1.6846 | 59.166 | -1.7807 | -1.3824 | -1.8997 | -1.767 | -1.6891 | -1.799 | -1.68 | -0.16479 | 0.13733 | -0.37079 | 118.7531 | 60.9695 | 0.11902 | 61.1343 | 0.28381 | -0.09613 | -123.0469 | -123.4314 | 0.11444 | 0.1236 | 0.004578 | 0.21973 | 0.10071 | 118.9178 | 123.262 | 0.21057 | 0.13275 | 123.7701 | 0.51727 | 123.6053 | 0.42114 | -123.6328 | -123.5641 | 123.0972 | 0.036621 | 28.0746 | 0.022888
577 | 123.4955 | -1.7441 | 121.6919 | 0.010071 | 0.00044428 | 0.0033069 | 0.0033004 | -0.00052344 | 0.0021342 | -0.0018072 | 0.057678 | 0.013373 | 0.026637 | -0.0019312 | -0.0012923 | -0.0044135 | 7.0452e-05 | 26.7105 | 121.8246 | -1.9226 | 121.344 | 116.9449 | -1.5793 | 59.8251 | -1.6983 | -1.3779 | -1.8539 | -1.6891 | -1.561 | -1.68 | -1.5839 | -0.17853 | 0.13275 | -0.3479 | 118.689 | 61.5692 | 0.1648 | 61.7477 | 0.34332 | -0.10986 | -123.0698 | -123.381 | 0.18311 | 0.16022 | 0.064087 | 0.27008 | 0.17395 | 118.8675 | 123.2666 | 0.29297 | 0.16479 | 123.7473 | 0.47607 | 123.5687 | 0.36621 | -123.6145 | -123.5458 | 123.0881 | 0.054932 | 28.4546 | 0.045777
578.0469 | 123.4772 | -1.7761 | 121.6827 | -0.012817 | 0.0019397 | 0.00052971 | 0.00052342 | 0.0020402 | 0.001066 | 0.0022516 | -0.030823 | 0.011877 | 0.026637 | 0.0014868 | -0.0030013 | 0.0030633 | -0.0024929 | 27.2919 | 121.8201 | -1.9638 | 121.3211 | 116.8533 | -1.5976 | 60.4889 | -1.7075 | -1.3458 | -1.8585 | -1.7303 | -1.6479 | -1.7487 | -1.6434 | -0.18768 | 0.13733 | -0.36163 | 118.6295 | 62.265 | 0.17853 | 62.4527 | 0.36621 | -0.082398 | -123.0286 | -123.4131 | 0.12817 | 0.13275 | 0.027466 | 0.21515 | 0.10986 | 118.8171 | 123.2849 | 0.21057 | 0.12817 | 123.7839 | 0.5127 | 123.5962 | 0.4303 | -123.6465 | -123.5413 | 123.0972 | 0.045776 | 29.068 | 0.068665
578.9844 | 123.555 | -1.7441 | 121.6415 | -0.073852 | 0.0030079 | 0.00052971 | 0.0056504 | 0.0052444 | -0.0012838 | 0.00032904 | 0.0027465 | 0.01145 | 0.024714 | -0.0036402 | -0.00086514 | 0.00092711 | -0.00035675 | 27.7313 | 121.7743 | -1.9547 | 121.3623 | 116.8625 | -1.5884 | 61.1526 | -1.6525 | -1.4328 | -1.8814 | -1.6571 | -1.5564 | -1.6663 | -1.5472 | -0.21057 | 0.13275 | -0.27924 | 118.6066 | 62.8967 | 0.15564 | 63.1073 | 0.36621 | -0.13733 | -123.0743 | -123.2986 | 0.18768 | 0.19684 | 0.07782 | 0.33417 | 0.21515 | 118.8171 | 123.317 | 0.32501 | 0.22431 | 123.7289 | 0.44861 | 123.5184 | 0.31128 | -123.5962 | -123.523 | 123.1064 | 0.086976 | 29.4754 | 0.091553
580.0625 | 123.5367 | -1.7853 | 121.6461 | -0.058594 | 0.0040759 | 0.0030933 | 0.0054366 | -9.604e-05 | 0.0017068 | 0.0011834 | 0.021057 | 0.013159 | 0.024287 | 0.002555 | -0.0032149 | 0.00028631 | -0.0022793 | 28.2944 | 121.7972 | -1.918 | 121.3943 | 116.8716 | -1.5472 | 61.7981 | -1.6342 | -1.4053 | -1.8402 | -1.8127 | -1.6571 | -1.5015 | -1.4877 | -0.13275 | 0.15106 | -0.25177 | 118.6569 | 63.5834 | 0.23804 | 63.7161 | 0.37079 | -0.054932 | -123.0515 | -123.4589 | 0.12817 | 0.29755 | 0.28381 | 0.35248 | 0.33874 | 118.7897 | 123.3124 | 0.18311 | 0.027466 | 123.7152 | 0.43488 | 123.5825 | 0.37994 | -123.5641 | -123.4863 | 123.1796 | -0.027466 | 30.0797 | 0.15106
581 | 123.5825 | -1.7441 | 121.6736 | -0.043335 | 0.00087168 | 0.0015979 | 0.0028732 | -9.604e-05 | 0.0032022 | -0.0050116 | 0.048523 | 0.010596 | 0.025569 | -0.0021448 | -0.0032149 | -0.0020637 | 0.00049765 | 28.7384 | 121.8338 | -1.9089 | 121.4081 | 116.8579 | -1.4877 | 62.3886 | -1.6388 | -1.3916 | -1.8539 | -1.6296 | -1.4832 | -1.593 | -1.5427 | -0.1648 | 0.16022 | -0.2655 | 118.602 | 64.1327 | 0.25635 | 64.2975 | 0.42114 | -0.10986 | -123.0652 | -123.3032 | 0.26093 | 0.20142 | 0.15106 | 0.31128 | 0.26092 | 118.7668 | 123.317 | 0.37079 | 0.2243 | 123.7427 | 0.46234 | 123.5779 | 0.35248 | -123.5825 | -123.5275 | 123.1522 | 0.11444 | 30.4825 | 0.10529
582.0625 | 123.5321 | -1.7807 | 121.701 | -0.012817 | 0.00023068 | 0.0015979 | 0.0047958 | 0.00054476 | 0.002775 | -0.00373 | 0.063782 | 0.010596 | 0.025569 | -0.0032128 | -0.0019333 | -0.0024909 | -0.00078395 | 29.2557 | 121.8246 | -1.9272 | 121.3394 | 116.7343 | -1.5472 | 62.7274 | -1.886 | -1.4008 | -1.9135 | -1.7303 | -1.5884 | -1.7029 | -1.593 | -0.14648 | 0.1236 | -0.36163 | 118.515 | 64.5081 | 0.23346 | 64.6545 | 0.37994 | -0.13275 | -123.1018 | -123.4314 | 0.19226 | 0.18768 | 0.07782 | 0.32043 | 0.21057 | 118.6615 | 123.2666 | 0.32501 | 0.1831 | 123.7518 | 0.51269 | 123.6053 | 0.37994 | -123.6282 | -123.6145 | 123.1201 | 0.050354 | 31.0364 | -0.10528
582.9844 | 123.555 | -1.7532 | 121.6644 | -0.020447 | -0.0012647 | 0.00052971 | 0.0071456 | 0.0018266 | 0.0038432 | 0.00096984 | -0.015564 | 0.01145 | 0.025355 | -0.00022222 | -0.0047103 | 0.00028631 | -0.0050565 | 29.7501 | 121.7606 | -1.9592 | 121.3806 | 116.7343 | -1.5472 | 63.0432 | -1.6571 | -1.4236 | -1.8539 | -1.6571 | -1.561 | -1.68 | -1.561 | -0.20599 | 0.09613 | -0.28381 | 118.4875 | 64.7964 | 0.20599 | 65.0024 | 0.41199 | -0.10071 | -123.0881 | -123.3215 | 0.19226 | 0.19226 | 0.073242 | 0.29297 | 0.17395 | 118.6935 | 123.3398 | 0.29297 | 0.19684 | 123.7198 | 0.4303 | 123.5138 | 0.32959 | -123.6237 | -123.5184 | 123.1339 | 0.096131 | 31.5033 | 0.096131
583.9844 | 123.4039 | -1.7807 | 121.7102 | 0.010071 | 0.0019397 | 0.0035205 | 0.0071456 | 0.0031082 | 0.00085237 | -0.0028754 | -0.088806 | 0.014441 | 0.023432 | 0.0078956 | -0.00065154 | -0.00056829 | -0.0037747 | 30.13 | 121.8338 | -1.9821 | 121.2708 | 116.5329 | -1.6342 | 63.0844 | -1.8265 | -1.3824 | -1.8951 | -1.799 | -1.7075 | -1.8173 | -1.6846 | -0.20142 | 0.1236 | -0.43945 | 118.3136 | 64.8651 | 0.14649 | 65.0665 | 0.3479 | -0.11444 | -123.0927 | -123.5092 | 0.073243 | 0.096131 | -0.036621 | 0.21057 | 0.07782 | 118.515 | 123.2529 | 0.18768 | 0.096131 | 123.8159 | 0.5127 | 123.6145 | 0.39826 | -123.6923 | -123.6053 | 123.0515 | -0.01831 | 31.9107 | -0.045776
585.0625 | 123.5321 | -1.7578 | 121.701 | -0.066223 | 1.7082e-05 | 0.0026661 | 0.007573 | 0.0033218 | 0.0025614 | 0.0016106 | -0.033875 | 0.014441 | 0.023432 | -0.0023584 | -0.0023605 | -0.0020637 | 0.0011387 | 30.6061 | 121.8338 | -1.973 | 121.3257 | 116.5878 | -1.5793 | 63.1165 | -1.7075 | -1.3779 | -1.8723 | -1.6663 | -1.5656 | -1.6846 | -1.5656 | -0.21515 | 0.13275 | -0.37537 | 118.3456 | 64.8743 | 0.17853 | 65.0894 | 0.39368 | -0.11444 | -123.0789 | -123.3673 | 0.19226 | 0.19226 | 0.073242 | 0.3067 | 0.18768 | 118.5608 | 123.2986 | 0.3067 | 0.20599 | 123.8068 | 0.49438 | 123.5916 | 0.37994 | -123.674 | -123.5733 | 123.0835 | 0.091552 | 32.3639 | 0.050354
585.9844 | 123.4863 | -1.767 | 121.701 | -0.081482 | 0.00044428 | 0.0033069 | 0.006932 | 0.00097196 | 0.0017068 | 0.00075624 | -0.036926 | 0.014868 | 0.024287 | -0.0017176 | -0.0010787 | -0.00056829 | 0.0011387 | 30.9265 | 121.875 | -1.9684 | 121.2982 | 116.5375 | -1.6113 | 63.3728 | -1.7441 | -1.3733 | -1.8723 | -1.712 | -1.6205 | -1.7349 | -1.6067 | -0.20142 | 0.17395 | -0.40283 | 118.3044 | 65.1398 | 0.15564 | 65.3412 | 0.35706 | -0.10528 | -123.0743 | -123.4131 | 0.14649 | 0.16022 | 0.032044 | 0.2655 | 0.13733 | 118.5059 | 123.2666 | 0.25177 | 0.16022 | 123.8434 | 0.49896 | 123.642 | 0.39368 | -123.6694 | -123.5733 | 123.0652 | 0.054932 | 32.6935 | 0.022888
586.9844 | 123.5138 | -1.7395 | 121.7148 | -0.050964 | 0.0021533 | 0.0033069 | 0.008641 | -0.0045822 | 0.0019204 | -0.00052556 | 0.030212 | 0.013586 | 0.026209 | -0.0012902 | -0.00065154 | -0.0022773 | -0.0027065 | 31.3843 | 121.8338 | -1.918 | 121.4035 | 116.6016 | -1.474 | 63.5834 | -1.6342 | -1.3916 | -1.8402 | -1.6479 | -1.5381 | -1.6571 | -1.5472 | -0.17853 | 0.11902 | -0.31128 | 118.3411 | 65.3229 | 0.2655 | 65.5014 | 0.44403 | -0.10071 | -123.1064 | -123.3627 | 0.20142 | 0.19226 | 0.082398 | 0.29297 | 0.18311 | 118.5196 | 123.3215 | 0.30212 | 0.19226 | 123.7518 | 0.44861 | 123.5733 | 0.3479 | -123.6328 | -123.555 | 123.143 | 0.091553 | 33.1238 | 0.10529
588.0625 | 123.5458 | -1.7349 | 121.6873 | -0.081482 | 0.00087168 | 0.0011707 | 0.0071456 | 0.0020402 | 0.001066 | 0.0028924 | 0.0027465 | 0.013159 | 0.0245 | -0.0015038 | -0.0042831 | -0.00056829 | 7.0452e-05 | 31.6772 | 121.8018 | -1.9409 | 121.4127 | 116.5558 | -1.5244 | 64.0228 | -1.6342 | -1.4145 | -1.8539 | -1.6479 | -1.5564 | -1.6663 | -1.5427 | -0.20599 | 0.11444 | -0.27466 | 118.2907 | 65.7578 | 0.21057 | 65.9637 | 0.41656 | -0.11902 | -123.1018 | -123.3353 | 0.17853 | 0.19226 | 0.068664 | 0.31128 | 0.18768 | 118.4967 | 123.3536 | 0.29755 | 0.20599 | 123.7427 | 0.43945 | 123.5367 | 0.32043 | -123.6282 | -123.5413 | 123.1476 | 0.086975 | 33.4122 | 0.10071
588.9844 | 123.642 | -1.7578 | 121.6415 | -0.035705 | 0.00044428 | 0.0039477 | 0.005223 | -0.0020188 | -0.00064303 | -0.00138 | -0.00030511 | 0.012732 | 0.023646 | -0.0051354 | -0.0019333 | 0.00028631 | -0.0031339 | 31.9611 | 121.8292 | -1.9318 | 121.4081 | 116.5375 | -1.4786 | 64.4806 | -1.6388 | -1.4008 | -1.8402 | -1.5884 | -1.8082 | -1.8036 | -1.6205 | -0.17395 | 0.18768 | -0.23346 | 118.2953 | 66.2384 | 0.27923 | 66.4124 | 0.45319 | -0.082398 | -123.0423 | -123.23 | -0.050355 | 0.13733 | -0.045777 | 0.21973 | 0.036621 | 118.4692 | 123.3398 | 0.032043 | 0.25177 | 123.761 | 0.43945 | 123.587 | 0.35705 | -123.5733 | -123.4818 | 123.1659 | 0.16937 | 33.7189 | 0.11902
590.0469 | 123.5001 | -1.7715 | 121.7514 | -0.020447 | 0.0021533 | 0.0013843 | 0.0056504 | 0.0011856 | 0.0014932 | -0.002021 | -0.018616 | 0.014014 | 0.022791 | 0.0044776 | -0.0012923 | 0.00092711 | 0.00028405 | 32.2311 | 121.8933 | -1.9775 | 121.3211 | 116.4047 | -1.5381 | 64.7507 | -1.7349 | -1.3779 | -1.8768 | -1.712 | -1.5884 | -1.7166 | -1.5976 | -0.20599 | 0.14191 | -0.4303 | 118.1763 | 66.5222 | 0.23346 | 66.7282 | 0.43945 | -0.10529 | -123.1293 | -123.4634 | 0.1831 | 0.17395 | 0.054931 | 0.27924 | 0.16022 | 118.3823 | 123.2986 | 0.28839 | 0.1648 | 123.8708 | 0.49896 | 123.6649 | 0.39368 | -123.7289 | -123.6282 | 123.0927 | 0.059509 | 34.0027 | 0.036621
591 | 123.5458 | -1.7532 | 121.7148 | -0.012817 | -0.00019652 | 0.00031611 | 0.0065048 | 0.00054476 | -0.0019248 | -0.0035162 | 0.06073 | 0.013373 | 0.02685 | -0.0040674 | -0.0030013 | -0.00099549 | 0.0024203 | 32.3822 | 121.8155 | -1.9684 | 121.3577 | 116.4413 | -1.4969 | 64.7964 | -1.6891 | -1.3916 | -1.8539 | -1.6754 | -1.5381 | -1.6434 | -1.5472 | -0.21515 | 0.10071 | -0.35706 | 118.1946 | 66.5497 | 0.25635 | 66.7648 | 0.4715 | -0.10071 | -123.1064 | -123.3902 | 0.21515 | 0.20599 | 0.10986 | 0.3067 | 0.21057 | 118.4097 | 123.3261 | 0.31586 | 0.17853 | 123.7839 | 0.46234 | 123.5687 | 0.36163 | -123.6832 | -123.5687 | 123.111 | 0.07782 | 34.1354 | 0.064087
592.0625 | 123.4726 | -1.7807 | 121.6919 | -0.34088 | 0.0015125 | -0.00096549 | 0.005864 | -0.00095064 | 0.0017068 | -0.00073916 | -0.04303 | 0.015509 | 0.022791 | 0.0049048 | -0.00065154 | 0.00092711 | -0.00014315 | 32.4188 | 121.8384 | -1.9547 | 121.2982 | 116.3269 | -1.6296 | 64.3433 | -1.7807 | -1.3824 | -1.8951 | -1.7441 | -1.6525 | -1.7807 | -1.6434 | -0.17395 | 0.14648 | -0.39368 | 118.1076 | 66.124 | 0.15106 | 66.2979 | 0.32501 | -0.11444 | -123.0743 | -123.436 | 0.12817 | 0.13733 | 0 | 0.25177 | 0.11444 | 118.2816 | 123.2529 | 0.24262 | 0.15106 | 123.793 | 0.5127 | 123.6191 | 0.39826 | -123.6465 | -123.587 | 123.0789 | 0.036621 | 34.1995 | 0
592.9844 | 123.5733 | -1.7899 | 121.6553 | -0.020447 | 0.00065788 | 0.0039477 | 0.0060776 | 0.0018266 | 0.0034158 | -0.00052556 | 0.027161 | 0.012091 | 0.023646 | -0.00022222 | -0.0036423 | -0.00014089 | 0.0037021 | 32.3181 | 121.8018 | -1.9363 | 121.2982 | 116.5878 | -1.5244 | 64.119 | -1.6846 | -1.4832 | -1.8951 | -1.7212 | -1.6113 | -1.712 | -1.6067 | -0.14648 | 0.14649 | -0.35705 | 118.3777 | 65.9088 | 0.2655 | 66.0553 | 0.41199 | -0.10529 | -123.1384 | -123.3765 | 0.17853 | 0.18311 | 0.07782 | 0.28839 | 0.18311 | 118.5242 | 123.2346 | 0.28381 | 0.17395 | 123.7381 | 0.41199 | 123.5916 | 0.3067 | -123.5916 | -123.5504 | 123.0881 | 0.068665 | 34.108 | 0.10529
594.0469 | 123.5001 | -1.7807 | 121.7285 | 0.078736 | -0.0014783 | -0.00032469 | 0.0065048 | 0.00097196 | 0.00042517 | 0.001397 | 0.0027465 | 0.012091 | 0.024714 | 0.0023414 | -0.0015059 | -0.0012091 | 0.0013523 | 32.2861 | 121.843 | -2.0279 | 121.2524 | 116.272 | -1.6022 | 63.4094 | -1.8311 | -1.3962 | -1.918 | -1.6617 | -1.5152 | -1.9638 | -1.7395 | -0.24719 | 0.11444 | -0.47607 | 118.0527 | 65.1901 | 0.17853 | 65.4373 | 0.42572 | -0.13733 | -123.1247 | -123.3902 | 0.2655 | 0.041199 | -0.1831 | 0.17853 | -0.045776 | 118.2999 | 123.2803 | 0.40283 | 0.25635 | 123.8709 | 0.52185 | 123.6237 | 0.38452 | -123.7564 | -123.6465 | 123.0331 | 0.11902 | 34.0668 | -0.050354
594.9844 | 123.5596 | -1.7853 | 121.6415 | -0.050964 | 0.0023669 | 0.0013843 | 0.006932 | 0.00075836 | 0.00063877 | -0.00031196 | -0.024719 | 0.013159 | 0.026423 | 0.0055456 | -0.00043794 | 0.00028631 | -0.0033475 | 32.341 | 121.756 | -2.0187 | 121.312 | 116.3223 | -1.5747 | 63.382 | -1.712 | -1.4832 | -1.9318 | -1.712 | -1.6067 | -1.7212 | -1.593 | -0.23346 | 0.11444 | -0.32959 | 118.1076 | 65.1672 | 0.21057 | 65.4007 | 0.44403 | -0.14648 | -123.1247 | -123.3536 | 0.17853 | 0.19226 | 0.064087 | 0.33874 | 0.21057 | 118.3411 | 123.3307 | 0.32501 | 0.21973 | 123.7747 | 0.44861 | 123.5413 | 0.30212 | -123.6603 | -123.5733 | 123.0972 | 0.073242 | 34.1263 | 0.073242
596.0469 | 123.4543 | -1.8311 | 121.669 | -0.035705 | -0.00083732 | 0.0011707 | 0.01035 | 0.0020402 | 0.0014932 | 0.00096984 | -0.064392 | 0.015082 | 0.024287 | 0.0040504 | -1.0744e-05 | 0.0013543 | 0.00071145 | 32.2403 | 121.7789 | -2.0325 | 121.2341 | 116.1896 | -1.6571 | 63.2904 | -1.9592 | -1.4374 | -1.9455 | -1.7944 | -1.7624 | -1.8219 | -1.6891 | -0.20142 | 0.10986 | -0.43487 | 118.0206 | 65.1215 | 0.17395 | 65.3229 | 0.37537 | -0.11444 | -123.1064 | -123.4634 | 0.068665 | 0.14191 | 0.009156 | 0.25635 | 0.1236 | 118.222 | 123.2666 | 0.18311 | 0.15106 | 123.8113 | 0.50812 | 123.6099 | 0.39368 | -123.7015 | -123.6145 | 123.0652 | 0.036621 | 34.0714 | -0.12817
597 | 123.4818 | -1.8539 | 121.6873 | 0.1474 | -0.00083732 | -0.0011793 | 0.0071456 | 0.00033116 | 0.0021342 | 0.00032904 | -0.0094605 | 0.0138 | 0.029414 | 0.0061866 | -0.0010787 | 0.0015679 | 0.00049765 | 31.9794 | 121.8201 | -2.005 | 121.2296 | 116.1804 | -1.593 | 62.9608 | -1.8585 | -1.4374 | -1.9638 | -1.8402 | -1.712 | -1.8173 | -1.7166 | -0.15106 | 0.13275 | -0.45776 | 118.0344 | 64.8148 | 0.26092 | 64.9658 | 0.41199 | -0.10986 | -123.1247 | -123.5275 | 0.14191 | 0.13733 | 0.036621 | 0.24719 | 0.14648 | 118.1854 | 123.2346 | 0.25177 | 0.1236 | 123.8251 | 0.52643 | 123.674 | 0.41656 | -123.6923 | -123.6511 | 123.0835 | 0.013733 | 33.8333 | -0.004578
598.0469 | 123.4589 | -1.8539 | 121.6873 | 0.048218 | -0.0019055 | 0.0013843 | 0.0054366 | 0.0013992 | 0.0012796 | -0.00095276 | 0.0088501 | 0.015082 | 0.027064 | -0.0049218 | -0.0017197 | -0.00035469 | 0.00092505 | 32.0023 | 121.7697 | -2.0279 | 121.2158 | 116.1987 | -1.6067 | 62.6404 | -1.8356 | -1.4328 | -1.9501 | -1.8585 | -1.7212 | -1.8219 | -1.7258 | -0.17395 | 0.082397 | -0.4715 | 118.0527 | 64.4943 | 0.24719 | 64.6683 | 0.42114 | -0.09613 | -123.1201 | -123.5458 | 0.13275 | 0.12817 | 0.032044 | 0.2243 | 0.12817 | 118.2266 | 123.2437 | 0.22888 | 0.091552 | 123.7976 | 0.51727 | 123.6237 | 0.42114 | -123.7152 | -123.6374 | 123.0698 | -0.004578 | 33.8562 | 0.018311
598.9844 | 123.6099 | -1.7761 | 121.6736 | -0.058594 | 0.00065788 | 0.00010251 | 0.0060776 | 0.0020402 | 0.0017068 | 0.0011834 | 0.045471 | 0.011237 | 0.026637 | -0.0040674 | -0.0010787 | 7.2706e-05 | 7.0452e-05 | 32.016 | 121.7972 | -1.9775 | 121.3577 | 116.3544 | -1.474 | 62.6862 | -1.6571 | -1.4465 | -1.8814 | -1.6891 | -1.5427 | -1.6434 | -1.5839 | -0.20142 | 0.1236 | -0.31586 | 118.1305 | 64.4623 | 0.30212 | 64.6637 | 0.50354 | -0.10529 | -123.1201 | -123.3627 | 0.23346 | 0.19226 | 0.13275 | 0.29755 | 0.23804 | 118.3319 | 123.3353 | 0.33875 | 0.19226 | 123.7747 | 0.43488 | 123.5733 | 0.32959 | -123.6511 | -123.555 | 123.1338 | 0.086975 | 33.7921 | 0.11902
600.0469 | 123.4634 | -1.8265 | 121.7194 | -0.035705 | 0.0019397 | 0.0043749 | 0.0067184 | -0.002446 | 0.0032022 | 0.00032904 | 0.014954 | 0.013373 | 0.023219 | -0.00022222 | -0.0017197 | -0.0012091 | -0.0039883 | 31.7734 | 121.8246 | -1.9913 | 121.2708 | 116.2079 | -1.5747 | 62.6312 | -1.8173 | -1.4145 | -1.918 | -1.8127 | -1.6891 | -1.7807 | -1.7029 | -0.1648 | 0.10529 | -0.44861 | 118.0344 | 64.4577 | 0.25177 | 64.6225 | 0.41656 | -0.091553 | -123.1338 | -123.5321 | 0.13733 | 0.1236 | 0.045776 | 0.21515 | 0.13733 | 118.1992 | 123.262 | 0.22888 | 0.10529 | 123.8159 | 0.50354 | 123.6511 | 0.41199 | -123.7106 | -123.6374 | 123.0972 | 0.013733 | 33.5999 | 0.009155
600.9844 | 123.5641 | -1.8723 | 121.5546 | -0.15778 | 0.0027943 | -0.00053829 | 0.0090682 | 0.00033116 | 0.00085237 | 0.00054264 | -0.0033569 | 0.014655 | 0.026209 | -0.00043582 | -1.0744e-05 | 0.00028631 | 0.0015659 | 31.5399 | 121.6187 | -2.0874 | 121.2891 | 116.217 | -1.6251 | 62.3291 | -1.7487 | -1.5518 | -1.9821 | -1.7807 | -1.6708 | -1.7807 | -1.6754 | -0.21515 | 0.064087 | -0.2655 | 118.0893 | 64.2014 | 0.24719 | 64.4165 | 0.46234 | -0.10986 | -123.1064 | -123.3353 | 0.20142 | 0.19684 | 0.091552 | 0.3067 | 0.20142 | 118.3044 | 123.3765 | 0.31128 | 0.20142 | 123.7061 | 0.4303 | 123.4909 | 0.32043 | -123.642 | -123.5367 | 123.1613 | 0.091552 | 33.4122 | 0.1236
602 | 123.4772 | -2.0096 | 121.5271 | 0.0177 | 0.0012989 | 0.00074331 | 0.0094956 | -0.003514 | 0.0017068 | 0.0011834 | -0.085754 | 0.013373 | 0.022791 | 0.0034094 | -0.0012923 | 7.2706e-05 | -0.0046291 | 31.0272 | 121.6461 | -2.1835 | 121.0739 | 115.9653 | -1.4832 | 62.1964 | -1.9455 | -1.5564 | -2.0645 | -1.9867 | -1.8723 | -1.9867 | -1.8631 | -0.17395 | 0.11902 | -0.45319 | 117.9749 | 64.2059 | 0.52643 | 64.3799 | 0.70038 | -0.054931 | -123.0835 | -123.5138 | 0.13733 | 0.14649 | 0.022889 | 0.20142 | 0.07782 | 118.1488 | 123.2574 | 0.19226 | 0.07782 | 123.8297 | 0.50812 | 123.6557 | 0.45319 | -123.7106 | -123.5916 | 123.0835 | 0.022889 | 33.0368 | 0.064087
603.0469 | 123.5504 | -1.886 | 121.5729 | -0.089111 | 0.0027943 | 0.0041613 | 0.0067184 | -0.00073704 | 0.0025614 | 0.00054264 | -0.00030511 | 0.012946 | 0.0245 | -0.0019312 | -0.0025741 | -0.00014089 | -0.0024929 | 30.5923 | 121.5775 | -2.0966 | 121.2479 | 116.0706 | -1.6159 | 61.8713 | -1.7899 | -1.6022 | -2.0187 | -1.8036 | -1.6891 | -1.8036 | -1.7029 | -0.21057 | 0.004578 | -0.32501 | 117.9565 | 63.7573 | 0.27008 | 63.9679 | 0.48065 | -0.13275 | -123.175 | -123.3765 | 0.19684 | 0.1831 | 0.082397 | 0.31586 | 0.21515 | 118.1671 | 123.3444 | 0.32959 | 0.21515 | 123.674 | 0.41656 | 123.4634 | 0.28381 | -123.6694 | -123.5916 | 123.1339 | 0.082397 | 32.4783 | 0.09613
603.9844 | 123.4818 | -2.0096 | 121.5042 | -0.050964 | 0.0027943 | 0.0026661 | 0.0097092 | -0.0022324 | 0.001066 | 0.0018242 | -0.0094605 | 0.013586 | 0.025782 | 0.0074682 | -0.0010787 | 0.0015679 | -0.0016385 | 30.3406 | 121.6095 | -2.2156 | 121.051 | 115.8829 | -1.9455 | 61.8073 | -2.0416 | -1.6067 | -2.1011 | -1.9958 | -1.8951 | -2.0096 | -1.8585 | -0.20599 | 0.10529 | -0.45319 | 117.8925 | 63.8168 | 0.064087 | 64.0228 | 0.27008 | -0.091552 | -123.111 | -123.5001 | 0.11444 | 0.15106 | 0 | 0.24261 | 0.091552 | 118.0984 | 123.2666 | 0.20599 | 0.10529 | 123.8251 | 0.49439 | 123.6191 | 0.40283 | -123.7198 | -123.6053 | 123.0606 | 0.013733 | 32.3502 | -0.032043
604.9844 | 123.5733 | -1.8723 | 121.582 | -0.073852 | 0.0027943 | 0.0022387 | 0.0013778 | -0.0022324 | 0.0040568 | -0.00031196 | -0.0064087 | 0.01145 | 0.024928 | 0.004264 | -0.0023605 | 0.00071351 | -0.00014315 | 30.4276 | 121.6599 | -2.0782 | 121.2616 | 116.0843 | -1.6067 | 61.5601 | -1.7899 | -1.5839 | -1.9913 | -1.799 | -1.68 | -1.7853 | -1.7166 | -0.20599 | 0.07782 | -0.32043 | 117.9565 | 63.4323 | 0.2655 | 63.6383 | 0.4715 | -0.11902 | -123.1659 | -123.381 | 0.19226 | 0.15564 | 0.086975 | 0.27466 | 0.20599 | 118.1625 | 123.3398 | 0.31128 | 0.19226 | 123.7381 | 0.40741 | 123.5321 | 0.28839 | -123.6603 | -123.5733 | 123.1338 | 0.073242 | 32.2998 | 0.082397
606.0469 | 123.5229 | -1.7899 | 121.7102 | 0.0024415 | 0.0019397 | 0.0020251 | 0.0080002 | -0.0020188 | 0.004484 | -9.8356e-05 | -0.027771 | 0.012091 | 0.023432 | -0.0015038 | -0.0019333 | -0.00056829 | -0.0042019 | 30.4276 | 121.8475 | -1.9775 | 121.312 | 116.0522 | -1.4969 | 61.3632 | -1.7944 | -1.3824 | -1.8997 | -1.7578 | -1.6479 | -1.7349 | -1.6342 | -0.18768 | 0.13733 | -0.39825 | 117.8421 | 63.1531 | 0.29297 | 63.3408 | 0.48065 | -0.10986 | -123.0927 | -123.468 | 0.14191 | 0.15564 | 0.054932 | 0.2655 | 0.1648 | 118.0298 | 123.2895 | 0.25177 | 0.14191 | 123.8251 | 0.51727 | 123.6374 | 0.40741 | -123.6877 | -123.6099 | 123.1018 | 0.032044 | 32.2174 | -0.004578
607 | 123.5138 | -1.7715 | 121.7834 | -0.012817 | 0.0017261 | 0.0011707 | 0.0067184 | 0.00011756 | 0.0038432 | -0.0011664 | -0.021668 | 0.012518 | 0.024073 | -0.0066308 | -0.0015059 | 0.0024225 | -0.00014315 | 30.5557 | 121.9208 | -1.9455 | 121.3348 | 116.0477 | -1.4877 | 61.5372 | -1.7532 | -1.3733 | -1.8631 | -1.7303 | -1.6067 | -1.712 | -1.6067 | -0.17395 | 0.13733 | -0.44861 | 117.8192 | 63.3087 | 0.28381 | 63.4827 | 0.45776 | -0.091553 | -123.1567 | -123.5138 | 0.1648 | 0.1648 | 0.059509 | 0.25635 | 0.15106 | 117.9932 | 123.2803 | 0.25635 | 0.13275 | 123.8663 | 0.48981 | 123.6923 | 0.39825 | -123.7289 | -123.6465 | 123.1064 | 0.041198 | 32.3273 | 0.01831
608.0625 | 123.6008 | -1.7532 | 121.6461 | -0.050964 | 0.0019397 | 0.0011707 | 0.0071456 | 0.0013992 | 0.002775 | -0.002021 | -0.00030511 | 0.011664 | 0.02386 | -0.002572 | -0.00086514 | -0.0012091 | -0.00035675 | 30.6427 | 121.8246 | -1.9318 | 121.4035 | 116.1072 | -1.4191 | 61.6241 | -1.6296 | -1.4145 | -1.8402 | -1.6342 | -1.5518 | -1.6296 | -1.5381 | -0.17853 | 0.17853 | -0.24262 | 117.8604 | 63.3774 | 0.33417 | 63.5559 | 0.5127 | -0.086975 | -123.0606 | -123.2803 | 0.20142 | 0.21515 | 0.1236 | 0.30212 | 0.21057 | 118.0389 | 123.3353 | 0.28839 | 0.20599 | 123.7564 | 0.42572 | 123.5779 | 0.33875 | -123.5779 | -123.4863 | 123.1567 | 0.11902 | 32.3959 | 0.1236
608.9844 | 123.5184 | -1.7487 | 121.7285 | -0.073852 | -0.00041012 | 0.0022387 | 0.0062912 | 0.0022538 | 0.0014932 | -0.0035162 | 0.018005 | 0.011877 | 0.023646 | -8.62e-06 | -0.0010787 | 7.2706e-05 | 0.0015659 | 30.6107 | 121.8613 | -1.9318 | 121.3898 | 116.0477 | -1.4282 | 61.2762 | -1.6617 | -1.4053 | -1.8356 | -1.6708 | -1.5656 | -1.68 | -1.5793 | -0.18311 | 0.13275 | -0.33875 | 117.7963 | 63.0249 | 0.32043 | 63.208 | 0.50354 | -0.086975 | -123.1338 | -123.3994 | 0.1831 | 0.16937 | 0.068664 | 0.25635 | 0.15564 | 117.9794 | 123.3215 | 0.27008 | 0.1648 | 123.793 | 0.4303 | 123.6099 | 0.34332 | -123.6603 | -123.5641 | 123.1384 | 0.07782 | 32.3593 | 0.086975
610.0469 | 123.4818 | -1.7761 | 121.7606 | -0.081482 | 0.00023068 | 0.0033069 | 0.012486 | 0.0033218 | 0.0040568 | -0.00073916 | -0.067444 | 0.015082 | 0.023646 | 0.00020498 | -0.00086514 | -0.00014089 | 0.0015659 | 30.7159 | 121.8567 | -1.9638 | 121.4539 | 115.8508 | -1.5793 | 62.2742 | -1.7441 | -1.355 | -1.8677 | -1.7303 | -1.6479 | -1.7487 | -1.6113 | -0.18768 | 0.09613 | -0.3067 | 117.627 | 64.0503 | 0.19684 | 64.238 | 0.38452 | -0.091553 | -123.1155 | -123.4909 | 0.12817 | 0.16479 | 0.027466 | 0.25635 | 0.11902 | 117.8146 | 123.4177 | 0.21973 | 0.13733 | 123.8205 | 0.5127 | 123.6328 | 0.42114 | -123.7244 | -123.6282 | 123.23 | 0.045776 | 32.4921 | 0.032043
610.9844 | 123.5641 | -1.7899 | 121.7056 | -0.005188 | 0.00023068 | 0.0011707 | 0.008641 | -0.00095064 | 0.002775 | 0.00075624 | 0.048523 | 0.012305 | 0.027918 | -0.00043582 | -0.00065154 | -0.00056829 | 0.00028405 | 33.7051 | 121.843 | -1.9409 | 121.3531 | 113.3743 | -1.4191 | 112.262 | -1.7303 | -1.4236 | -1.8768 | -1.7212 | -1.593 | -1.6983 | -1.5976 | -0.15106 | 0.13733 | -0.35248 | 115.1642 | 114.0518 | 0.37079 | 114.2029 | 0.52185 | -0.086975 | -123.1293 | -123.4268 | 0.19684 | 0.19226 | 0.091553 | 0.27924 | 0.17853 | 115.3152 | 123.2941 | 0.28381 | 0.15564 | 123.7839 | 0.45319 | 123.6328 | 0.36621 | -123.6465 | -123.5825 | 123.143 | 0.068665 | 35.495 | 0.059509
612.0625 | 123.5184 | -1.7441 | 121.7972 | -0.050964 | -0.00041012 | 0.0013843 | 0.0065048 | -0.0011642 | -0.00064303 | 0.0011834 | 0.014954 | 0.012305 | 0.027491 | -8.62e-06 | -0.0027877 | -0.00035469 | -0.0029201 | 33.8058 | 121.8842 | -1.9043 | 121.4218 | 113.5117 | -1.3138 | 113.4247 | -1.6479 | -1.3916 | -1.8265 | -1.6846 | -1.5518 | -1.6525 | -1.561 | -0.16022 | 0.086975 | -0.37537 | 115.2557 | 115.1688 | 0.4303 | 115.329 | 0.59051 | -0.082397 | -123.1888 | -123.4817 | 0.19226 | 0.18311 | 0.091553 | 0.2655 | 0.17395 | 115.416 | 123.3261 | 0.27466 | 0.14191 | 123.7885 | 0.43487 | 123.6282 | 0.35248 | -123.7015 | -123.6237 | 123.1659 | 0.05951 | 35.5499 | 0.096131
612.9844 | 123.5504 | -1.7532 | 121.7102 | -0.089111 | 0.00044428 | 0.0011707 | 0.0071456 | -0.00052344 | 0.0040568 | 0.00054264 | 0.024109 | 0.012732 | 0.025782 | -0.0017176 | -0.0025741 | -0.00056829 | -0.0024929 | 33.6868 | 121.8246 | -1.9409 | 121.3486 | 113.3652 | -1.4053 | 113.3743 | -1.7303 | -1.4236 | -1.8723 | -1.7075 | -1.593 | -1.6983 | -1.5747 | -0.18768 | 0.11444 | -0.36163 | 115.1184 | 115.1276 | 0.3479 | 115.3152 | 0.53558 | -0.11902 | -123.1338 | -123.4177 | 0.16022 | 0.17853 | 0.054932 | 0.29755 | 0.17395 | 115.3061 | 123.2895 | 0.27923 | 0.1648 | 123.7656 | 0.44861 | 123.5779 | 0.32959 | -123.6511 | -123.5825 | 123.1018 | 0.045777 | 35.4401 | 0.022888
614.0469 | 123.436 | -3.5156 | 120.0211 | -0.028076 | -0.00041012 | 0.0020251 | 0.01035 | -0.0011642 | 0.001066 | 0.00011544 | 0.011902 | 0.013373 | 0.027491 | -0.00064942 | -0.00065154 | -0.00035469 | -0.0014249 | 32.6294 | 120.1538 | -3.6896 | 119.5953 | 111.6348 | -3.4744 | 111.7996 | -3.566 | -3.0762 | -3.598 | -3.511 | -3.3966 | -3.511 | -3.3554 | -0.17395 | 0.13275 | -0.42572 | 115.1505 | 115.3152 | 0.041199 | 115.4892 | 0.21515 | -0.082397 | -123.0972 | -123.5321 | 0.11902 | 0.16022 | 0.004578 | 0.24261 | 0.086975 | 115.3244 | 123.2849 | 0.20142 | 0.086975 | 123.8434 | 0.52185 | 123.6694 | 0.43945 | -123.7106 | -123.6191 | 123.111 | 0.004578 | 36.145 | -0.050354
614.9844 | 123.5825 | -2.8564 | 120.5978 | -0.028076 | -0.00062372 | 0.00010251 | 0.0065048 | -0.002446 | 0.00021157 | -0.00095276 | -0.033875 | 0.012305 | 0.023005 | -8.62e-06 | -0.0015059 | 0.00028631 | 0.0026341 | 33.4488 | 120.7031 | -3.0441 | 120.2866 | 112.2849 | -2.3804 | 112.3993 | -2.7649 | -2.5589 | -2.9984 | -2.8152 | -2.623 | -2.7649 | -2.6825 | -0.18768 | 0.10529 | -0.31128 | 115.1413 | 115.2557 | 0.47607 | 115.4434 | 0.66376 | -0.14191 | -123.1567 | -123.4131 | 0.23346 | 0.17395 | 0.091552 | 0.31586 | 0.23346 | 115.329 | 123.3307 | 0.37537 | 0.18311 | 123.7473 | 0.43945 | 123.5596 | 0.29755 | -123.642 | -123.5962 | 123.143 | 0.041198 | 36.3052 | 0.091552
616.0469 | 123.468 | -2.7969 | 120.7581 | -0.035705 | 0.0017261 | 0.0035205 | 0.0097092 | 0.00097196 | 0.0017068 | -0.0018072 | 0.036316 | 0.015936 | 0.023646 | 0.0046912 | -0.0027877 | -0.00099549 | 0.0019931 | 33.7326 | 120.8405 | -2.9892 | 120.2911 | 112.1933 | -2.4902 | 112.2528 | -2.8976 | -2.3895 | -2.8976 | -2.8015 | -2.6962 | -2.7924 | -2.6733 | -0.19226 | 0.082397 | -0.46692 | 114.9902 | 115.0497 | 0.3067 | 115.242 | 0.49896 | -0.10071 | -123.1476 | -123.5596 | 0.10071 | 0.1236 | 0.004578 | 0.2243 | 0.10529 | 115.1825 | 123.2803 | 0.20142 | 0.09613 | 123.8297 | 0.50812 | 123.6374 | 0.40741 | -123.7473 | -123.6557 | 123.0881 | -0.004578 | 36.5295 | -0.10071
617 | 123.5733 | -2.2705 | 121.2021 | 0.010071 | 0.0015125 | 0.0018115 | 0.0092818 | -0.0011642 | 0.0029886 | -0.00095276 | 0.057678 | 0.012946 | 0.024287 | 0.00020498 | -0.00022434 | -0.0022773 | -0.0035611 | 34.5245 | 121.3165 | -2.449 | 120.9274 | 112.8296 | -1.8082 | 112.8479 | -2.1378 | -1.9318 | -2.3712 | -2.179 | -2.0416 | -2.1469 | -2.0737 | -0.17853 | 0.11444 | -0.27466 | 115.1001 | 115.1184 | 0.46234 | 115.2969 | 0.64087 | -0.10071 | -123.1339 | -123.381 | 0.22888 | 0.19684 | 0.1236 | 0.29755 | 0.2243 | 115.2786 | 123.3765 | 0.32959 | 0.19226 | 123.7656 | 0.43945 | 123.587 | 0.33875 | -123.6511 | -123.5733 | 123.1979 | 0.091553 | 36.795 | 0.13275
618.0469 | 123.5229 | -2.3071 | 121.2067 | -0.028076 | 0.0021533 | 0.0018115 | 0.0094956 | 0.00097196 | 0.0017068 | -0.0026618 | -0.052185 | 0.010809 | 0.025782 | 0.004264 | -0.0023605 | -0.00014089 | 0.0013523 | 34.6527 | 121.3165 | -2.4948 | 120.7855 | 112.6328 | -1.9547 | 112.6511 | -2.2934 | -1.9501 | -2.4307 | -2.2659 | -2.1606 | -2.2659 | -2.1561 | -0.18768 | 0.10986 | -0.42114 | 114.9399 | 114.9582 | 0.35248 | 115.1459 | 0.54016 | -0.1236 | -123.1567 | -123.4726 | 0.14648 | 0.15106 | 0.041199 | 0.27466 | 0.16479 | 115.1276 | 123.2803 | 0.27008 | 0.16479 | 123.8113 | 0.48065 | 123.6237 | 0.35706 | -123.7015 | -123.6374 | 123.0927 | 0.041199 | 36.9598 | 0.013733
618.9844 | 123.555 | -2.3804 | 121.1517 | -0.020447 | 0.00023068 | 0.0013843 | 0.0084274 | -0.0013778 | 0.0040568 | -0.00138 | 0.048523 | 0.013373 | 0.025996 | -0.00064942 | -0.00022434 | 7.2706e-05 | -0.0037747 | 35.1105 | 121.2799 | -2.5085 | 120.7809 | 112.6053 | -1.9501 | 112.6556 | -2.3483 | -2.0096 | -2.504 | -2.3071 | -2.1515 | -2.2888 | -2.1606 | -0.12817 | 0.12817 | -0.37079 | 114.9857 | 115.036 | 0.4303 | 115.1642 | 0.55847 | -0.1236 | -123.1613 | -123.4589 | 0.22888 | 0.21973 | 0.091553 | 0.34332 | 0.21515 | 115.1138 | 123.2895 | 0.35248 | 0.19684 | 123.7885 | 0.49438 | 123.6603 | 0.37079 | -123.6603 | -123.6557 | 123.1613 | 0.073242 | 37.4908 | 0.032043
620.0469 | 123.5825 | -2.7054 | 120.7489 | -0.066223 | 0.0015125 | 0.00074331 | 0.0080002 | 0.002681 | 0.0038432 | -0.0018072 | -0.055237 | 0.011664 | 0.024287 | -0.0036402 | -0.0023605 | -0.00014089 | 0.00092505 | 36.8042 | 120.8588 | -2.9068 | 120.4193 | 112.2528 | -2.2202 | 112.2345 | -2.6321 | -2.3804 | -2.8198 | -2.6367 | -2.5314 | -2.6184 | -2.4902 | -0.20142 | 0.10986 | -0.32959 | 114.9582 | 114.9399 | 0.48523 | 115.1413 | 0.68664 | -0.11444 | -123.1293 | -123.3856 | 0.17395 | 0.21515 | 0.086975 | 0.32959 | 0.20142 | 115.1596 | 123.3261 | 0.28839 | 0.18311 | 123.7656 | 0.43945 | 123.5641 | 0.32501 | -123.6557 | -123.5687 | 123.1247 | 0.068664 | 39.5096 | 0.073242
620.9844 | 123.5687 | -2.4216 | 121.0739 | -0.035705 | 1.7082e-05 | 0.0013843 | 0.0084274 | 0.00033116 | 0.0038432 | -0.0022346 | 0.039368 | 0.013373 | 0.025355 | -0.00064942 | -0.0010787 | -0.00056829 | 7.0452e-05 | 36.2 | 121.138 | -2.6138 | 120.7077 | 112.4817 | -1.9958 | 112.5229 | -2.3483 | -2.0874 | -2.5223 | -2.3346 | -2.1835 | -2.298 | -2.2156 | -0.19226 | 0.064086 | -0.36621 | 114.9033 | 114.9445 | 0.42572 | 115.1367 | 0.61798 | -0.10071 | -123.1613 | -123.4085 | 0.23804 | 0.20599 | 0.1236 | 0.3067 | 0.2243 | 115.0955 | 123.3215 | 0.33874 | 0.18768 | 123.7518 | 0.43488 | 123.5596 | 0.33417 | -123.6877 | -123.5962 | 123.1293 | 0.086975 | 38.6215 | 0.073242
622.0469 | 123.4726 | -2.4902 | 121.0373 | -0.028076 | 0.0021533 | 0.0018115 | 0.01035 | 0.0013992 | 0.0034158 | 0.00054264 | -0.09491 | 0.013373 | 0.024928 | -0.00043582 | -0.0021469 | 0.0026361 | -0.0042019 | 37.1933 | 121.1884 | -2.6276 | 120.6573 | 112.3306 | -2.1378 | 112.3627 | -2.449 | -2.0782 | -2.5681 | -2.4536 | -2.3621 | -2.4811 | -2.33 | -0.13733 | 0.15106 | -0.37994 | 114.8209 | 114.8529 | 0.35248 | 114.9902 | 0.48981 | -0.07782 | -123.1155 | -123.4909 | 0.12817 | 0.16022 | 0.009155 | 0.23804 | 0.086975 | 114.9582 | 123.2849 | 0.20599 | 0.11444 | 123.8159 | 0.48981 | 123.6786 | 0.41199 | -123.6649 | -123.6053 | 123.1476 | 0.036621 | 39.6835 | 0.041198
622.9844 | 123.5641 | -3.0396 | 120.4605 | -0.028076 | -0.00083732 | 0.00074331 | 0.0073592 | -0.0033004 | 0.0034158 | -0.0018072 | 0.036316 | 0.012091 | 0.023432 | -0.0023584 | -0.00043794 | 0.00028631 | -0.00035675 | 36.7722 | 120.5704 | -3.2181 | 120.1355 | 111.7676 | -2.5955 | 111.8179 | -3.067 | -2.7145 | -3.1952 | -2.9984 | -2.8381 | -2.9297 | -2.8381 | -0.17853 | 0.10986 | -0.32501 | 114.8071 | 114.8575 | 0.44403 | 115.036 | 0.62256 | -0.15564 | -123.175 | -123.4589 | 0.20142 | 0.20142 | 0.10986 | 0.35706 | 0.2655 | 114.9857 | 123.3536 | 0.35706 | 0.19684 | 123.7885 | 0.48065 | 123.6099 | 0.32501 | -123.6786 | -123.6557 | 123.175 | 0.041199 | 39.8117 | -0.027466
624.0469 | 123.5779 | -2.6459 | 120.813 | -0.089111 | 0.0025805 | 0.0028797 | 0.008641 | -0.0013778 | 0.0019204 | 0.0060968 | -0.049133 | 0.010382 | 0.024073 | 0.005332 | -0.0015059 | 0.0028497 | 0.00049765 | 36.8362 | 120.9091 | -2.7969 | 120.282 | 111.9415 | -1.9958 | 112.0834 | -2.5452 | -2.3529 | -2.7878 | -2.5818 | -2.4628 | -2.5589 | -2.4719 | -0.15106 | 0.096131 | -0.53101 | 114.5874 | 114.7293 | 0.65002 | 114.8804 | 0.80109 | -0.14191 | -123.1659 | -123.3948 | 0.1831 | 0.17395 | 0.086975 | 0.31586 | 0.22888 | 114.7385 | 123.0789 | 0.32501 | 0.20599 | 123.7061 | 0.43488 | 123.555 | 0.29297 | -123.6099 | -123.6008 | 122.9279 | 0.064087 | 39.4821 | 0.10071
624.9844 | 123.761 | -1.0208 | 105.2673 | 0.071106 | 0.0032215 | -0.0080151 | 0.0080002 | -0.0013778 | 0.0029886 | 0.00032904 | 0.024109 | 0.014227 | 0.025996 | -0.0029992 | -0.0030013 | -0.0016363 | -0.0020657 | 36.3464 | 120.2316 | -149.9954 | 120.0211 | 103.9673 | -3.8773 | 111.4563 | -3.1586 | -2.9846 | -2.7832 | -3.1998 | -3.1311 | -3.2455 | -3.1952 | -148.9746 | 14.9643 | 14.7537 | 104.9881 | 112.4771 | -2.8564 | 261.4517 | 146.1182 | -1.7624 | -108.252 | -108.4671 | -2.1103 | -2.1744 | -2.2247 | -0.41199 | -0.46234 | 253.9627 | 270.0165 | -0.3479 | -0.41657 | 270.227 | -0.20142 | 121.2524 | -1.9638 | -255.2628 | -108.0505 | 121.0419 | -2.179 | 37.3672 | -2.1378
626.0469 | -150 | 5.9052 | 122.3602 | -0.18066 | 0.0074939 | 0.1129 | 0.0090682 | 0.0067398 | 0.0038432 | -0.006507 | -0.10101 | 0.031104 | 0.030268 | 0.00020498 | -0.0032149 | 0.0037043 | 0.010324 | 39.2944 | 121.6736 | -149.9954 | 121.7102 | 94.0567 | 13.3804 | 95.3156 | -1.8814 | -1.6663 | -0.78278 | -1.8585 | -1.799 | -1.8036 | 1.8036 | -155.9006 | -0.68664 | -0.65002 | 88.1516 | 89.4104 | 7.4753 | 245.311 | 163.3759 | -6.6879 | -124.0265 | -124.2188 | -7.7042 | -4.1016 | -7.7087 | 2.5864 | -1.0208 | 244.0521 | 271.7056 | -1.0162 | -1.0757 | 271.669 | -0.88348 | 115.7684 | -7.5714 | -272.3557 | -123.143 | 115.8051 | -7.7637 | 33.3893 | -7.7866
626.9844 | 123.6374 | -1.3962 | 121.6919 | -0.19592 | -0.00041012 | 0.0065113 | 0.002446 | 0.00054476 | 0.0019204 | -0.00095276 | 0.021057 | 0.011664 | 0.023005 | -0.007058 | -0.00086514 | 0.00071351 | 0.0017795 | -0.12817 | 0.16479 | -0.40283 | -0.24719 | -0.09613 | -0.25177 | -0.10529 | -1.3321 | -1.0712 | -1.4053 | -1.3321 | -1.1902 | -1.2817 | -1.1902 | 0.99335 | -121.5271 | -121.9391 | 1.3 | 1.2909 | 1.1444 | 0.29755 | 0.15106 | -0.009155 | -122.7631 | -123.024 | 0.20599 | 0.20599 | 0.11444 | 0.21515 | 0.1236 | 0.3067 | 0.15564 | 0.21515 | 0.073242 | 0.56763 | 0.33417 | 1.561 | 0.32501 | -122.0947 | -123.0972 | 1.149 | 0.064087 | 1.268 | 0.064087
627.9844 | 123.587 | -1.3 | 122.1497 | -0.20355 | 0.00044428 | 0.0075793 | 0.0026596 | 0.0028946 | -0.0014974 | -9.8356e-05 | -0.00030511 | 0.011023 | 0.021723 | -0.0019312 | -0.0015059 | 0.0011407 | -0.00099755 | -0.19684 | 0.10986 | -0.39368 | -0.23804 | -0.10071 | -0.2655 | -0.13733 | -1.1765 | -0.99792 | -1.387 | -1.2222 | -1.1444 | -1.2314 | -1.1261 | 0.90637 | -122.0398 | -122.3877 | 1.1993 | 1.1627 | 1.0345 | 0.25635 | 0.12817 | -0.086975 | -123.1476 | -123.3719 | 0.15564 | 0.17395 | 0.068665 | 0.26093 | 0.15564 | 0.29297 | 0.15564 | 0.24262 | 0.1648 | 0.50354 | 0.3891 | 1.4099 | 0.30212 | -122.5433 | -123.5367 | 1.062 | 0.07782 | 1.1032 | 0.1236
629.0469 | 123.5367 | -1.3504 | 121.8796 | -0.27985 | -0.0061779 | 0.0015979 | 0.0026596 | -0.0077866 | -0.0036336 | -0.008216 | -0.31158 | 0.007605 | 0.01211 | -0.0079126 | -0.030559 | 0.012676 | -0.013174 | -0.19226 | 0.16937 | -0.39825 | -0.31128 | -0.17853 | -0.33875 | -0.22888 | -1.3 | -0.95673 | -1.3687 | -1.3 | -1.4008 | -1.7441 | -1.442 | 0.95215 | -121.7102 | -122.1909 | 1.1719 | 1.1215 | 1.0117 | 0.16937 | 0.059509 | -0.01831 | -122.8363 | -123.1796 | -0.050354 | -0.091553 | -0.39368 | -0.073243 | -0.37537 | 0.21973 | 0.086975 | -0.032044 | 0.068664 | 0.56763 | 0.41199 | 1.5198 | 0.39368 | -122.2778 | -123.2483 | 1.0391 | 0.050354 | 1.1581 | 0.050354
629.9844 | 123.5641 | -1.2955 | 122.1588 | -0.112 | 0.0034351 | 0.0071521 | 0.0020188 | 0.00054476 | 0.0012796 | 0.00054264 | 0.021057 | 0.01145 | 0.020442 | -0.0049218 | -0.0019333 | 0.0011407 | 0.0017795 | -0.19684 | 0.12817 | -0.37994 | -0.24719 | -0.082397 | -0.27924 | -0.14648 | -1.1993 | -0.94299 | -1.3733 | -1.1993 | -1.1078 | -1.2085 | -1.1169 | 0.91553 | -122.0306 | -122.406 | 1.2131 | 1.149 | 1.0162 | 0.23346 | 0.10071 | -0.07782 | -123.1018 | -123.3582 | 0.18768 | 0.17853 | 0.086975 | 0.25635 | 0.1648 | 0.29755 | 0.13275 | 0.2655 | 0.17395 | 0.50812 | 0.4303 | 1.4236 | 0.35248 | -122.5388 | -123.5321 | 1.0483 | 0.09613 | 1.0986 | 0.09613
631.0469 | 123.4818 | -1.3458 | 122.1863 | -0.18066 | 0.00065788 | 0.0050159 | 0.0033004 | 0.00075836 | -0.0012838 | 0.0026788 | -0.015564 | 0.013373 | 0.023432 | 0.0014868 | -0.0019333 | 0.00071351 | 0.0013523 | -0.2655 | 0.14191 | -0.41657 | -0.47607 | -0.07782 | -0.086975 | -0.33417 | -1.3321 | -0.91095 | -1.4053 | -1.2863 | -1.2268 | -1.3275 | -1.2863 | 0.92926 | -122.0444 | -122.6624 | 1.268 | 1.0117 | 1.2589 | 0.082398 | 0.32959 | -0.059509 | -123.0972 | -123.4726 | 0.11902 | 0.059509 | 0.01831 | 0.11902 | 0.077819 | 0.33875 | -0.059509 | 0.17853 | 0.11902 | 0.55847 | 0.49438 | 1.4877 | 0.43488 | -122.6028 | -123.5916 | 0.86975 | 0.059509 | 1.0803 | 0.013733
631.9844 | 123.6694 | -1.2817 | 122.2046 | -0.14252 | 0.0017261 | 0.0065113 | -0.00075838 | 0.00097196 | 0.00021157 | -0.0033026 | 0.045471 | 0.012732 | 0.023219 | -0.00064942 | -0.0021469 | -0.0016363 | 0.00071145 | -0.16479 | 0.12817 | -0.35706 | -0.21515 | -0.013733 | -0.17395 | -0.082397 | -1.1398 | -0.93842 | -1.3824 | -1.1765 | -1.0483 | -1.1444 | -1.0757 | 0.92468 | -122.0764 | -122.4197 | 1.268 | 1.1993 | 1.1078 | 0.27466 | 0.18311 | -0.10071 | -123.143 | -123.381 | 0.23346 | 0.20599 | 0.13733 | 0.3067 | 0.23804 | 0.34332 | 0.14191 | 0.33417 | 0.20599 | 0.48523 | 0.44403 | 1.4099 | 0.34332 | -122.5616 | -123.587 | 1.0666 | 0.10529 | 1.1169 | 0.14191
633.0469 | 123.1476 | -1.3504 | 122.0169 | -0.15015 | 0.0023669 | 0.013561 | 0.002446 | 0.0024674 | 0.0019204 | -0.0026618 | -0.088806 | 0.0138 | 0.0245 | 0.0014868 | -0.0032149 | 0.00049991 | 7.0452e-05 | -0.31586 | 0.13275 | -0.4303 | -0.26093 | -0.2243 | -0.41657 | -0.23346 | -1.3138 | -0.9201 | -1.4465 | -1.268 | -1.2177 | -1.3184 | -1.1765 | 0.9201 | -121.8842 | -122.2778 | 1.1261 | 1.1169 | 0.93384 | 0.19684 | 0.013733 | -0.09613 | -122.937 | -123.2849 | 0.13275 | 0.17395 | 0.032044 | 0.27008 | 0.12817 | 0.20599 | 0.16937 | 0.22888 | 0.17853 | 0.56305 | 0.52643 | 1.4832 | 0.4303 | -122.4472 | -123.4634 | 1.0895 | 0.082398 | 1.0345 | 0.036621
633.9844 | 123.5641 | -1.3138 | 122.1634 | -0.112 | 0.0032215 | 0.0067249 | -0.0022538 | 0.0028946 | 0.004484 | 0.0016106 | 0.027161 | 0.010596 | 0.022364 | -0.0029992 | -0.0023605 | 0.0019953 | -0.00035675 | -0.24261 | 0.091553 | -0.3891 | -0.28839 | -0.14648 | -0.28839 | -0.16937 | -1.2451 | -0.9613 | -1.4191 | -1.236 | -1.1124 | -1.2314 | -1.1353 | 0.92468 | -122.0718 | -122.4518 | 1.1673 | 1.1444 | 1.0254 | 0.21973 | 0.10071 | -0.10529 | -123.1247 | -123.3994 | 0.20142 | 0.17853 | 0.082398 | 0.28381 | 0.18768 | 0.24261 | 0.10071 | 0.3067 | 0.18311 | 0.48065 | 0.45776 | 1.4053 | 0.35248 | -122.5525 | -123.5825 | 1.0254 | 0.07782 | 1.0712 | 0.068665
635.0469 | 123.555 | -1.3458 | 122.168 | -0.16541 | 0.00087168 | 0.0077929 | -0.00075838 | -0.002446 | 0.0014932 | 0.00011544 | 0.042419 | 0.012946 | 0.028346 | -0.0021448 | -0.0023605 | -0.0016363 | 0.0041293 | -0.22888 | 0.11902 | -0.40283 | -0.28381 | -0.14648 | -0.29297 | -0.18768 | -1.4145 | -0.95673 | -1.442 | -1.2405 | -1.1536 | -1.236 | -1.1215 | 0.94299 | -122.049 | -122.4518 | 1.1993 | 1.1581 | 1.0529 | 0.21515 | 0.10986 | -0.096131 | -123.1247 | -123.4085 | 0.19226 | 0.2243 | 0.10986 | 0.32044 | 0.20599 | 0.25635 | 0.11902 | 0.28839 | 0.20142 | 0.52185 | 0.48523 | 1.4648 | 0.3891 | -122.5708 | -123.6099 | 1.062 | 0.10529 | 1.1169 | -0.068665
635.9844 | 123.5458 | -1.3275 | 122.1405 | -0.12726 | 0.0017261 | 0.0067249 | -0.0016128 | -9.604e-05 | -0.00085663 | -0.003089 | 0.018005 | 0.01145 | 0.020014 | -0.0079126 | -1.0744e-05 | 7.2706e-05 | 0.0013523 | -0.23346 | 0.086975 | -0.41657 | -0.28381 | -0.16479 | -0.28839 | -0.17395 | -1.2405 | -0.94757 | -1.3916 | -1.2314 | -1.1536 | -1.3046 | -1.236 | 0.91095 | -122.0535 | -122.4243 | 1.1627 | 1.1536 | 1.0391 | 0.24262 | 0.12817 | -0.064087 | -123.0881 | -123.3719 | 0.17395 | 0.091553 | 0.022889 | 0.15564 | 0.086976 | 0.25177 | 0.13275 | 0.23804 | 0.16022 | 0.50354 | 0.44403 | 1.4145 | 0.37994 | -122.5571 | -123.5321 | 1.0437 | 0.096131 | 1.0941 | 0.086975
636.9844 | 123.5916 | -1.3138 | 122.1909 | -0.13489 | 0.0021533 | 0.0067249 | -0.00097198 | -0.00073704 | -0.0012838 | -0.0022346 | 0.033264 | 0.011877 | 0.021296 | -0.00043582 | -0.0027877 | 0.0030633 | -0.00099755 | -0.19684 | 0.068665 | -0.3891 | -0.22888 | -0.064087 | -0.20599 | -0.12817 | -1.0712 | -0.97504 | -1.4236 | -1.2314 | -1.0345 | -1.1902 | -1.1124 | 0.92468 | -122.1222 | -122.4197 | 1.2497 | 1.1856 | 1.1078 | 0.26092 | 0.1831 | -0.10986 | -123.1659 | -123.4222 | 0.27924 | 0.20142 | 0.1236 | 0.31128 | 0.23346 | 0.32501 | 0.16022 | 0.3891 | 0.19226 | 0.45776 | 0.44861 | 1.3824 | 0.33874 | -122.58 | -123.6145 | 1.0849 | 0.082398 | 1.1169 | 0.24262
637.9844 | 123.6145 | -1.2863 | 122.2046 | -0.15778 | 0.00044428 | 0.0073657 | 0.0013778 | 0.00033116 | -0.00064303 | 0.00011544 | 0.011902 | 0.012946 | 0.021723 | -0.0034264 | -0.0025741 | -0.00078189 | 0.0019931 | -0.19684 | 0.082397 | -0.37537 | -0.21515 | -0.086975 | -0.21057 | -0.10529 | -1.1078 | -0.94757 | -1.3779 | -1.1673 | -1.0254 | -1.1215 | -1.0757 | 0.91095 | -122.1222 | -122.4197 | 1.1993 | 1.181 | 1.0757 | 0.27008 | 0.16479 | -0.091553 | -123.1522 | -123.3719 | 0.26093 | 0.21057 | 0.1648 | 0.30212 | 0.25635 | 0.28839 | 0.16022 | 0.35248 | 0.21057 | 0.45776 | 0.4303 | 1.3687 | 0.33874 | -122.58 | -123.5825 | 1.0712 | 0.11902 | 1.0895 | 0.17853
639.0469 | 123.5367 | -1.2817 | 122.2366 | -0.17303 | 0.0025805 | 0.0090747 | -0.00011758 | 0.0050308 | -0.00064303 | 0.00075624 | -0.0064087 | 0.011664 | 0.020442 | 0.0029822 | 0.00063026 | -0.00035469 | 0.0024203 | -0.24261 | 0.054932 | -0.42572 | -0.27008 | -0.1236 | -0.31128 | -0.17853 | -1.1719 | -0.9613 | -1.4099 | -1.1902 | -1.0986 | -1.2085 | -1.1215 | 0.85602 | -122.1817 | -122.5067 | 1.1581 | 1.1032 | 0.97046 | 0.24719 | 0.11444 | -0.12817 | -123.1979 | -123.4268 | 0.18311 | 0.16022 | 0.073242 | 0.28839 | 0.20142 | 0.30212 | 0.15564 | 0.31128 | 0.21973 | 0.48065 | 0.44861 | 1.3367 | 0.32043 | -122.6624 | -123.6465 | 1.0117 | 0.091552 | 1.0391 | 0.10986
639.9844 | 123.5962 | -1.2955 | 122.1817 | -0.15778 | 0.0010853 | 0.0086475 | -0.00011758 | 0.00097196 | 0.0012796 | -0.0015936 | 0.011902 | 0.011664 | 0.019373 | -0.0057764 | -1.0744e-05 | 0.0011407 | 0.0039157 | -0.26093 | 0.054932 | -0.42572 | -0.27924 | -0.15564 | -0.27008 | -0.16022 | -1.2222 | -0.95673 | -1.4008 | -1.1993 | -1.0803 | -1.1719 | -1.0941 | 0.86975 | -122.1268 | -122.4609 | 1.1398 | 1.1353 | 1.0254 | 0.2655 | 0.15564 | -0.10529 | -123.1384 | -123.381 | 0.21515 | 0.20142 | 0.1236 | 0.3067 | 0.22888 | 0.27008 | 0.14648 | 0.32044 | 0.20142 | 0.48065 | 0.44403 | 1.3504 | 0.33875 | -122.6074 | -123.5825 | 1.0162 | 0.09613 | 1.0345 | 0.073242
641.0625 | 123.111 | -1.3458 | 122.2366 | -0.12726 | 0.0025805 | 0.0071521 | 0.001805 | 0.0018266 | 0.0021342 | -0.0033026 | -0.070496 | 0.0138 | 0.022791 | 0.0044776 | -0.0015059 | 0.00092711 | 7.0452e-05 | -0.30212 | 0.1236 | -0.42572 | -0.35706 | -0.25635 | -0.36163 | -0.25177 | -1.3184 | -0.91553 | -1.4511 | -1.3046 | -1.1856 | -1.2955 | -1.2039 | 0.92011 | -122.113 | -122.5937 | 1.0895 | 1.0941 | 0.98419 | 0.17395 | 0.064087 | -0.10529 | -123.1522 | -123.5413 | 0.16022 | 0.14191 | 0.050354 | 0.24719 | 0.15564 | 0.16937 | 0.068664 | 0.2655 | 0.14648 | 0.54932 | 0.53558 | 1.4694 | 0.4303 | -122.6624 | -123.6877 | 0.98877 | 0.041199 | 1.0437 | 0.027466
641.9844 | 123.5092 | -1.3321 | 122.1954 | -0.15778 | 0.0017261 | 0.0050159 | -0.00075838 | -0.00095064 | -0.00021583 | 0.00075624 | 0.0088501 | 0.014655 | 0.019587 | -0.0036402 | -0.00065154 | 7.2706e-05 | 0.0022067 | -0.2243 | 0.032043 | -0.44861 | -0.29297 | -0.14648 | -0.27008 | -0.18768 | -1.2314 | -0.9613 | -1.4099 | -1.2726 | -1.149 | -1.2405 | -1.1673 | 0.88348 | -122.1634 | -122.4884 | 1.1856 | 1.1444 | 1.062 | 0.26093 | 0.17853 | -0.07782 | -123.1567 | -123.468 | 0.18311 | 0.1648 | 0.091552 | 0.24262 | 0.16937 | 0.30212 | 0.15564 | 0.26093 | 0.13733 | 0.48065 | 0.44861 | 1.3641 | 0.37079 | -122.644 | -123.6053 | 1.0391 | 0.059509 | 1.1078 | 0.10071
642.9844 | 123.4589 | -1.3596 | 122.2092 | -0.10437 | 0.0021533 | 0.0080065 | 0.0030868 | 0.0022538 | -0.0014974 | -0.00052556 | -0.033875 | 0.014441 | 0.022578 | -0.0066308 | -0.0017197 | -0.0014227 | 0.00092505 | -0.28381 | 0.086975 | -0.46692 | -0.37994 | -0.2243 | -0.36163 | -0.26093 | -1.3275 | -0.94757 | -1.4374 | -1.3138 | -1.2131 | -1.3138 | -1.2131 | 0.89264 | -122.1222 | -122.5891 | 1.1353 | 1.0986 | 0.99793 | 0.20599 | 0.10529 | -0.07782 | -123.1567 | -123.5229 | 0.14648 | 0.14648 | 0.045776 | 0.2243 | 0.1236 | 0.24261 | 0.086975 | 0.2243 | 0.1236 | 0.55389 | 0.48981 | 1.4465 | 0.41199 | -122.6761 | -123.6465 | 0.97961 | 0.045776 | 1.0757 | 0.032043
644.0469 | 123.5275 | -1.3367 | 122.2183 | -0.15778 | 0.00044428 | 0.0069385 | 0.003514 | 0.0020402 | 0.0014932 | 0.00011544 | -0.073547 | 0.013159 | 0.021723 | -0.0040674 | -0.00065154 | 0.0017817 | 0.0034885 | -0.32044 | 0.050354 | -0.48981 | -0.40741 | -0.27008 | -0.44403 | -0.32044 | -1.3 | -0.97046 | -1.4282 | -1.2589 | -1.1765 | -1.2772 | -1.1673 | 0.84686 | -122.168 | -122.6257 | 1.0666 | 1.0162 | 0.89264 | 0.16937 | 0.045776 | -0.091553 | -123.1888 | -123.4772 | 0.16022 | 0.16937 | 0.059509 | 0.26093 | 0.15106 | 0.21973 | 0.082397 | 0.25177 | 0.16937 | 0.54016 | 0.45776 | 1.387 | 0.36621 | -122.7081 | -123.6465 | 0.92926 | 0.07782 | 1.0162 | 0.036621
644.9844 | 123.4634 | -1.3458 | 122.2046 | 0.0177 | 0.0021533 | 0.0077929 | 0.001805 | -0.0030868 | 0.00042517 | 0.00032904 | -0.012512 | 0.012946 | 0.020869 | -0.0023584 | 0.0012711 | 7.2706e-05 | 0.0024203 | -0.34332 | 0.082397 | -0.48065 | -0.39825 | -0.26093 | -0.35248 | -0.27008 | -1.3412 | -0.94299 | -1.4694 | -1.3229 | -1.2039 | -1.3092 | -1.2314 | 0.86517 | -122.1222 | -122.6028 | 1.0849 | 1.0757 | 0.99335 | 0.21057 | 0.12817 | -0.1236 | -123.1476 | -123.5275 | 0.14191 | 0.11444 | 0.036621 | 0.23804 | 0.16022 | 0.21973 | 0.082398 | 0.2655 | 0.14648 | 0.56305 | 0.52643 | 1.4282 | 0.40283 | -122.6852 | -123.674 | 0.94757 | 0.022888 | 1.0025 | 0.004577
645.9844 | 123.5641 | -1.3229 | 122.1725 | -0.15778 | 0.0027943 | 0.0086475 | 0.001805 | 0.00033116 | -0.00064303 | -0.0035162 | -0.021668 | 0.012732 | 0.023005 | -0.0072718 | -0.00022434 | -0.0012091 | -0.00078395 | -0.22888 | 0.009155 | -0.43945 | -0.17395 | -0.31586 | -0.52185 | -0.10986 | -1.1993 | -1.0208 | -1.4191 | -1.2268 | -1.0849 | -1.1902 | -1.1261 | 0.88348 | -122.1634 | -122.3465 | 1.0071 | 1.2131 | 0.80109 | 0.32959 | -0.082398 | -0.09613 | -123.1934 | -123.3994 | 0.23804 | 0.19684 | 0.13275 | 0.29297 | 0.22888 | 0.1236 | 0.2655 | 0.33417 | 0.19226 | 0.44861 | 0.39825 | 1.3321 | 0.30212 | -122.612 | -123.5916 | 1.149 | 0.09613 | 1.0941 | 0.1236
647.0469 | 123.5962 | -1.3046 | 122.1771 | -0.12726 | -0.00041012 | 0.0067249 | 0.00095062 | -0.0033004 | 0.0032022 | -9.8356e-05 | 0.027161 | 0.01145 | 0.022578 | 0.00084598 | -0.0034287 | -0.00056829 | -0.00014315 | -0.27924 | 0.022888 | -0.45776 | -0.3067 | -0.16937 | -0.29297 | -0.1831 | -1.1993 | -0.99335 | -1.4145 | -1.2131 | -1.0757 | -1.1856 | -1.1261 | 0.84686 | -122.1542 | -122.4838 | 1.1353 | 1.1215 | 1.0117 | 0.27466 | 0.1648 | -0.10986 | -123.1705 | -123.3902 | 0.22888 | 0.17853 | 0.11902 | 0.28839 | 0.22888 | 0.28839 | 0.15106 | 0.33875 | 0.20142 | 0.48065 | 0.42114 | 1.3275 | 0.31128 | -122.6349 | -123.5916 | 0.99792 | 0.091552 | 1.0254 | 0.10529
647.9844 | 123.4909 | -1.3962 | 122.2 | -0.17303 | -0.0010511 | 0.0060839 | 0.0033004 | -0.0015914 | 0.00042517 | -0.0011664 | -0.058289 | 0.014441 | 0.021296 | -0.0029992 | -0.0015059 | 0.0011407 | -0.00057035 | -0.23804 | 0.10071 | -0.4715 | -0.39825 | -0.31128 | -0.37079 | -0.27924 | -1.3321 | -0.94299 | -1.4557 | -1.3458 | -1.2131 | -1.3275 | -1.2177 | 0.92468 | -122.0993 | -122.5983 | 1.0849 | 1.1169 | 1.0254 | 0.19226 | 0.10071 | -0.059509 | -123.143 | -123.5458 | 0.18311 | 0.17853 | 0.068664 | 0.23804 | 0.12817 | 0.16022 | 0.073243 | 0.24261 | 0.10986 | 0.5722 | 0.5127 | 1.4969 | 0.45319 | -122.6715 | -123.6557 | 0.99793 | 0.050354 | 1.1581 | 0.064087
649.0469 | 123.6099 | -1.3275 | 122.1542 | -0.15015 | 0.0019397 | 0.0048023 | -0.00054478 | 0.00075836 | -2.232e-06 | -0.00095276 | 0.014954 | 0.013373 | 0.022578 | -0.0023584 | -0.0012923 | 0.00028631 | 0.0017795 | -0.2655 | 0 | -0.45776 | -0.27466 | -0.091553 | -0.25635 | -0.20142 | -1.1902 | -1.0025 | -1.4328 | -1.2177 | -1.0941 | -1.181 | -1.1261 | 0.86975 | -122.1542 | -122.4289 | 1.236 | 1.1261 | 1.0712 | 0.25635 | 0.20142 | -0.10529 | -123.1567 | -123.3719 | 0.23346 | 0.20142 | 0.14648 | 0.3067 | 0.25177 | 0.36621 | 0.18311 | 0.33875 | 0.21515 | 0.45776 | 0.4303 | 1.3275 | 0.32501 | -122.612 | -123.587 | 1.0529 | 0.10986 | 1.062 | 0.13733
649.9844 | 123.5962 | -1.3596 | 122.1588 | -0.13489 | 0.00087168 | 0.0082201 | -0.00011758 | -0.003514 | 0.00042517 | -0.0011664 | 0.039368 | 0.0138 | 0.023432 | -0.0012902 | -0.0036423 | 0.00049991 | -0.0024929 | -0.25177 | 0 | -0.45776 | -0.14648 | 0.018311 | -0.71869 | -0.27924 | -1.2726 | -1.03 | -1.4648 | -1.2497 | -1.1215 | -1.2177 | -1.1627 | 0.90179 | -122.1588 | -122.3053 | 1.3779 | 1.0803 | 0.64087 | 0.17853 | -0.26093 | -0.10529 | -123.1888 | -123.4085 | 0.23804 | 0.19684 | 0.14191 | 0.30212 | 0.24719 | 0.47608 | 0.31128 | 0.34332 | 0.21515 | 0.45776 | 0.43488 | 1.3596 | 0.32959 | -122.6166 | -123.6237 | 1.2131 | 0.10986 | 1.1078 | 0.086975
650.9844 | 123.4634 | -1.3916 | 122.1863 | -0.096741 | 0.0017261 | 0.0054431 | 0.0030868 | -0.00030984 | 0.00021157 | -0.0026618 | -0.0094605 | 0.012091 | 0.023432 | -0.0029992 | -0.00065154 | 0.0011407 | -0.00099755 | -0.35248 | 0.036621 | -0.5127 | -0.42114 | -0.28839 | -0.39825 | -0.29755 | -1.3687 | -0.97504 | -1.4969 | -1.3596 | -1.2405 | -1.3367 | -1.2543 | 0.87891 | -122.1497 | -122.6074 | 1.1032 | 1.0941 | 0.99335 | 0.21515 | 0.11444 | -0.10529 | -123.1613 | -123.5458 | 0.15106 | 0.13733 | 0.054932 | 0.24262 | 0.16022 | 0.2243 | 0.091552 | 0.25635 | 0.13733 | 0.54932 | 0.52185 | 1.4282 | 0.41656 | -122.699 | -123.6832 | 0.97046 | 0.032044 | 1.0391 | 0.022889
652.0625 | 123.3902 | -1.355 | 122.2595 | -0.17303 | 0.00065788 | 0.0030933 | 0.003514 | 0.00033116 | -0.0014974 | -0.00073916 | -0.024719 | 0.013159 | 0.022364 | 0.0049048 | 0.00063026 | -0.0020637 | 0.00092505 | -0.32501 | 0.032043 | -0.5127 | -0.43488 | -0.29755 | -0.39825 | -0.31586 | -1.3641 | -0.97046 | -1.4877 | -1.3824 | -1.0666 | -1.0849 | -1.0757 | 0.84229 | -122.2275 | -122.6944 | 1.0574 | 1.0391 | 0.95673 | 0.19684 | 0.11444 | -0.13275 | -123.23 | -123.642 | 0.28839 | 0.27924 | 0.27008 | 0.41199 | 0.40283 | 0.21515 | 0.07782 | 0.42114 | 0.10529 | 0.54474 | 0.51727 | 1.387 | 0.38452 | -122.7722 | -123.7473 | 0.92011 | -0.027466 | 1.03 | -0.009156
652.9844 | 123.5046 | -1.3824 | 122.1817 | -0.12726 | 0.0021533 | 0.0052295 | 0.0015914 | 0.0041764 | -0.00085663 | -0.00031196 | -0.058289 | 0.014655 | 0.022578 | -0.0038538 | -0.00065154 | 7.2706e-05 | -0.0020657 | -0.3479 | 0.041199 | -0.52643 | -0.38452 | -0.33875 | -0.46234 | -0.29297 | -1.3596 | -0.95215 | -1.4786 | -1.3596 | -1.2177 | -1.3367 | -1.2314 | 0.85602 | -122.1405 | -122.5662 | 1.0437 | 1.0895 | 0.92011 | 0.23346 | 0.064087 | -0.096131 | -123.1338 | -123.5413 | 0.1648 | 0.15106 | 0.045776 | 0.24719 | 0.14191 | 0.18768 | 0.14191 | 0.26093 | 0.11902 | 0.56763 | 0.52643 | 1.4236 | 0.4303 | -122.7081 | -123.6603 | 0.99793 | 0.022888 | 1.0345 | 0.022888
653.9844 | 123.4772 | -1.4008 | 122.1863 | -0.10437 | 0.00065788 | 0.0062975 | 0.0011642 | -0.00030984 | 0.00085237 | -0.0015936 | -0.0094605 | 0.013373 | 0.019587 | -0.0044946 | 0.00020286 | -0.00035469 | 0.00049765 | -0.37994 | 0 | -0.52185 | -0.4303 | -0.28839 | -0.41199 | -0.32044 | -1.3596 | -0.99792 | -1.4832 | -1.3733 | -1.2451 | -1.3275 | -1.2497 | 0.87891 | -122.1863 | -122.6166 | 1.1124 | 1.0803 | 0.98877 | 0.20142 | 0.10986 | -0.082397 | -123.1842 | -123.5596 | 0.15564 | 0.15106 | 0.073242 | 0.23346 | 0.15564 | 0.23346 | 0.091553 | 0.23804 | 0.10986 | 0.52185 | 0.48523 | 1.4008 | 0.40283 | -122.7081 | -123.6694 | 0.97046 | 0.027466 | 1.0208 | 0.041199
655.0469 | 123.5962 | -1.3458 | 122.1497 | -0.089111 | 0.0017261 | 0.0048023 | 0.00095062 | -0.002446 | 0.00063877 | -0.00138 | 0.039368 | 0.012091 | 0.022578 | -0.0012902 | -0.0021469 | 0.00071351 | -0.0031339 | -0.3067 | -0.018311 | -0.4715 | -0.32044 | -0.12817 | -0.28381 | -0.1831 | -1.2131 | -1.0254 | -1.4282 | -1.2405 | -1.0986 | -1.1902 | -1.1353 | 0.87433 | -122.168 | -122.4701 | 1.2177 | 1.1627 | 1.062 | 0.28839 | 0.18768 | -0.082398 | -123.175 | -123.3902 | 0.24719 | 0.21057 | 0.15564 | 0.29297 | 0.23804 | 0.34332 | 0.15106 | 0.32959 | 0.18768 | 0.45319 | 0.40283 | 1.3275 | 0.32043 | -122.6212 | -123.5779 | 1.0254 | 0.10529 | 1.0391 | 0.13275
655.9844 | 123.5321 | -1.3824 | 122.1771 | -0.16541 | 0.00087168 | 0.0069385 | 0.0015914 | 0.00011756 | -0.0012838 | 0.0016106 | -0.039978 | 0.014655 | 0.023005 | 0.00084598 | -0.0036423 | -0.00078189 | -0.0031339 | -0.33875 | 0 | -0.54016 | -0.43488 | -0.31586 | -0.39368 | -0.32959 | -1.3458 | -1.0208 | -1.4786 | -1.3367 | -1.2268 | -1.3321 | -1.2314 | 0.84229 | -122.1771 | -122.612 | 1.0666 | 1.0529 | 0.98877 | 0.21057 | 0.14648 | -0.096131 | -123.1979 | -123.5138 | 0.15564 | 0.15106 | 0.050354 | 0.24719 | 0.14648 | 0.2243 | 0.10529 | 0.25177 | 0.14191 | 0.54016 | 0.45776 | 1.3824 | 0.36163 | -122.7173 | -123.6557 | 0.94757 | 0.045776 | 1.0437 | 0.036621
656.9844 | 123.4772 | -1.4008 | 122.1771 | -0.16541 | 0.0017261 | 0.0022387 | 0.0030868 | -0.005223 | -0.0014974 | -0.009284 | -0.085754 | 0.0138 | 0.022791 | 0.00084598 | -0.00065154 | 0.00049991 | -0.0027065 | -0.37994 | -0.018311 | -0.54016 | -0.49896 | -0.40741 | -0.53101 | -0.4303 | -1.3962 | -0.98877 | -1.506 | -1.3641 | -1.2817 | -1.387 | -1.2497 | 0.8606 | -122.1954 | -122.6761 | 0.99335 | 0.97046 | 0.86975 | 0.10986 | 0.009155 | -0.10529 | -123.1659 | -123.5413 | 0.11902 | 0.15106 | 0.013733 | 0.25635 | 0.11902 | 0.13275 | 0.041199 | 0.2243 | 0.14191 | 0.52185 | 0.51727 | 1.3824 | 0.41199 | -122.7173 | -123.6832 | 0.9018 | 0.036621 | 1.0208 | 0.004578
658.0469 | 123.6099 | -1.355 | 122.1268 | -0.10437 | -0.0010511 | 0.0056567 | -0.0016128 | -0.00052344 | 0.00021157 | 0.00096984 | 0.042419 | 0.012091 | 0.022791 | -0.0051354 | -0.00022434 | 7.2706e-05 | -0.0042019 | -0.29755 | -0.050354 | -0.48065 | -0.33875 | -0.14648 | -0.29755 | -0.20142 | -1.1856 | -1.0208 | -1.4603 | -1.236 | -1.1032 | -1.2039 | -1.1627 | 0.87433 | -122.1771 | -122.4655 | 1.2085 | 1.1536 | 1.0574 | 0.27924 | 0.18311 | -0.10529 | -123.1476 | -123.3627 | 0.25177 | 0.19226 | 0.15106 | 0.29755 | 0.25635 | 0.33417 | 0.14191 | 0.35706 | 0.2243 | 0.4303 | 0.43945 | 1.3046 | 0.33417 | -122.6074 | -123.587 | 1.0162 | 0.11902 | 1.0574 | 0.16937
658.9844 | 123.5229 | -1.4008 | 122.1817 | -0.15778 | 0.0023669 | 0.0075793 | 0.003514 | -0.0030868 | -0.00042943 | -0.011848 | -0.06134 | 0.015509 | 0.021723 | 0.00020498 | -0.00086514 | -0.0044135 | 0.00049765 | -0.33417 | -0.027466 | -0.54474 | -0.43488 | -0.27008 | -0.40741 | -0.34332 | -1.3092 | -1.0208 | -1.4969 | -1.3092 | -1.2131 | -1.3275 | -1.2222 | 0.85602 | -122.2092 | -122.6166 | 1.1307 | 1.0574 | 0.99335 | 0.20142 | 0.13733 | -0.09613 | -123.2025 | -123.4909 | 0.18768 | 0.17853 | 0.073242 | 0.27466 | 0.16937 | 0.27466 | 0.10986 | 0.28381 | 0.18768 | 0.51727 | 0.47607 | 1.3733 | 0.37994 | -122.7264 | -123.6786 | 0.96588 | 0.091553 | 1.0666 | 0.091553
660.0469 | 123.5596 | -1.3504 | 122.1222 | -0.23407 | 0.0021533 | 0.0077929 | 0.0011642 | 0.0018266 | 0.0014932 | 0.001397 | -0.00030511 | 0.013373 | 0.021937 | -0.0029992 | -0.0010787 | 0.00092711 | -0.00014315 | -0.34332 | -0.082397 | -0.52643 | -0.39368 | -0.2243 | -0.39368 | -0.27924 | -1.2497 | -1.0345 | -1.4694 | -1.2497 | -1.1673 | -1.268 | -1.1948 | 0.82398 | -122.2046 | -122.5159 | 1.1261 | 1.0712 | 0.95673 | 0.24719 | 0.13275 | -0.11902 | -123.1567 | -123.3719 | 0.18311 | 0.15564 | 0.082398 | 0.27466 | 0.20142 | 0.30212 | 0.13275 | 0.30212 | 0.21973 | 0.44403 | 0.43488 | 1.268 | 0.31586 | -122.6486 | -123.5916 | 0.95673 | 0.10071 | 1.0071 | 0.10071
660.9844 | 123.5229 | -1.4191 | 122.1222 | -0.15778 | 0.0017261 | 0.0084339 | 0.0022324 | -0.0022324 | 0.0029886 | 0.00054264 | -0.046082 | 0.015295 | 0.023219 | 0.0010596 | -0.0012923 | 0.0024225 | -0.0031339 | -0.37537 | -0.004578 | -0.56305 | -0.46234 | -0.33417 | -0.43945 | -0.3479 | -1.3687 | -1.0071 | -1.506 | -1.3412 | -1.2314 | -1.3275 | -1.2222 | 0.85602 | -122.1268 | -122.5845 | 1.0849 | 1.0712 | 0.97961 | 0.21515 | 0.1236 | -0.086975 | -123.1293 | -123.4634 | 0.18768 | 0.19684 | 0.091552 | 0.28381 | 0.17853 | 0.22888 | 0.10071 | 0.27466 | 0.16479 | 0.55847 | 0.49896 | 1.4145 | 0.41199 | -122.6852 | -123.6282 | 0.95673 | 0.077819 | 1.0437 | 0.050354
662.0469 | 123.5229 | -1.387 | 122.1359 | -0.096741 | 0.00023068 | 0.0077929 | 0.001805 | -9.604e-05 | 0.001066 | 0.00054264 | 0.024109 | 0.013586 | 0.022791 | -0.00043582 | -0.0012923 | 0.0026361 | 0.0011387 | -0.31586 | -0.054932 | -0.52185 | -0.41657 | -0.24261 | -0.35248 | -0.28381 | -1.3229 | -1.03 | -1.5106 | -1.3504 | -1.2314 | -1.3367 | -1.2405 | 0.86517 | -122.1909 | -122.5525 | 1.1444 | 1.1032 | 1.0345 | 0.23804 | 0.16937 | -0.1236 | -123.1659 | -123.4863 | 0.15564 | 0.14648 | 0.050354 | 0.27008 | 0.17395 | 0.27924 | 0.10529 | 0.27924 | 0.16022 | 0.46692 | 0.48065 | 1.3321 | 0.35706 | -122.6578 | -123.6465 | 0.97046 | 0.036621 | 1.0712 | 0.064087
662.9844 | 123.4863 | -1.4328 | 122.1313 | -0.13489 | -0.0016919 | 0.0028797 | 0.0020188 | 0.0024674 | -0.00021583 | 0.0016106 | 0.021057 | 0.013373 | 0.024073 | 0.0021278 | -0.0012923 | -0.00099549 | -0.00078395 | -0.36621 | -0.032043 | -0.54474 | -0.42114 | -0.26093 | -0.48981 | -0.36163 | -1.4053 | -1.0483 | -1.5335 | -1.4145 | -1.2909 | -1.387 | -1.3092 | 0.88806 | -122.1634 | -122.5525 | 1.1719 | 1.0712 | 0.94299 | 0.18311 | 0.054932 | -0.10071 | -123.1796 | -123.5458 | 0.14191 | 0.1236 | 0.045776 | 0.2243 | 0.14648 | 0.28381 | 0.1236 | 0.24261 | 0.11902 | 0.5127 | 0.48523 | 1.4008 | 0.38452 | -122.6761 | -123.6649 | 1.0117 | 0.01831 | 1.0666 | 0.027466
664.0469 | 123.5962 | -1.387 | 122.1405 | -0.17303 | 0.0019397 | 0.0073657 | -0.00011758 | 0.0013992 | -2.232e-06 | 0.00032904 | 0.066833 | 0.013586 | 0.02151 | -0.0036402 | -0.0017197 | -0.0014227 | 0.0011387 | -0.31128 | -0.086975 | -0.52643 | -0.21057 | -0.086975 | -0.78278 | -0.32044 | -1.3 | -1.0712 | -1.5198 | -1.3046 | -1.1765 | -1.2497 | -1.1856 | 0.8606 | -122.2275 | -122.3511 | 1.3 | 1.0666 | 0.60425 | 0.20599 | -0.25635 | -0.13275 | -123.2117 | -123.4451 | 0.21057 | 0.20142 | 0.13733 | 0.33417 | 0.27008 | 0.43945 | 0.31586 | 0.34332 | 0.21515 | 0.43945 | 0.44861 | 1.3 | 0.31586 | -122.6669 | -123.6603 | 1.1765 | 0.082398 | 1.0757 | 0.086975
664.9844 | 123.5275 | -1.4511 | 122.113 | -0.14252 | -0.00083732 | 0.0069385 | 0.0022324 | 0.0013992 | 0.00085237 | -0.00031196 | -0.04303 | 0.013373 | 0.025569 | -0.0029992 | -0.0012923 | 7.2706e-05 | 0.0024203 | -0.37079 | -0.036621 | -0.56305 | -0.4715 | -0.35248 | -0.44403 | -0.37994 | -1.3779 | -1.0391 | -1.5381 | -1.3962 | -1.2817 | -1.3916 | -1.2772 | 0.88806 | -122.1497 | -122.5845 | 1.0986 | 1.0712 | 1.0071 | 0.18311 | 0.11902 | -0.086975 | -123.1522 | -123.5092 | 0.16937 | 0.17395 | 0.059509 | 0.26093 | 0.14648 | 0.21057 | 0.091552 | 0.25635 | 0.14191 | 0.52643 | 0.49896 | 1.4145 | 0.41199 | -122.6761 | -123.6511 | 0.97961 | 0.054932 | 1.0803 | 0.073242
666.0469 | 123.5596 | -1.4053 | 122.1451 | -0.18066 | 0.0023669 | 0.0080065 | 0.00052342 | -0.0015914 | 0.0014932 | -0.00031196 | 0.057678 | 0.012305 | 0.020014 | -0.0047082 | -0.00065154 | 0.00028631 | 0.0026341 | -0.36163 | -0.073242 | -0.55389 | -0.45776 | -0.28381 | -0.45319 | -0.33875 | -1.3367 | -1.0529 | -1.4969 | -1.3184 | -1.2131 | -1.3092 | -1.2131 | 0.85144 | -122.2183 | -122.6028 | 1.1215 | 1.0666 | 0.95215 | 0.21515 | 0.10071 | -0.091553 | -123.1979 | -123.4634 | 0.19226 | 0.19226 | 0.09613 | 0.28381 | 0.18768 | 0.27008 | 0.09613 | 0.28381 | 0.17853 | 0.48065 | 0.44403 | 1.3321 | 0.35248 | -122.699 | -123.642 | 0.94757 | 0.086975 | 1.0437 | 0.068664
666.9844 | 123.5001 | -1.4099 | 122.1313 | -0.20355 | 0.0034351 | 0.0088611 | 0.0026596 | -0.0020188 | 0.007261 | 0.00075624 | -0.0094605 | 0.0138 | 0.022151 | 0.0017004 | -0.00086514 | 0.0013543 | -0.0033475 | -0.41199 | -0.050354 | -0.59967 | -0.6134 | -0.1831 | -0.35706 | -0.50354 | -1.4236 | -1.0254 | -1.5244 | -1.387 | -1.3184 | -1.4191 | -1.2909 | 0.81024 | -122.1817 | -122.7448 | 1.2268 | 0.90637 | 1.0529 | 0.09613 | 0.24261 | -0.11444 | -123.1567 | -123.5184 | 0.091553 | 0.11902 | -0.009155 | 0.23346 | 0.10529 | 0.41657 | -0.013733 | 0.20599 | 0.13733 | 0.54932 | 0.49896 | 1.3596 | 0.38452 | -122.731 | -123.6557 | 0.79651 | 0.022888 | 0.99793 | -0.013733
668.0469 | 123.587 | -1.4008 | 122.0718 | -0.14252 | 0.0025805 | 0.0088611 | 0.0011642 | -0.0022324 | -2.232e-06 | -0.002021 | 0.018005 | 0.013159 | 0.021723 | 0.001914 | 0.00020286 | 0.0039179 | -0.00035675 | -0.35248 | -0.10071 | -0.55847 | -0.39368 | -0.25635 | -0.42572 | -0.31128 | -1.2589 | -1.0574 | -1.4923 | -1.4236 | -1.2039 | -1.1581 | -1.1581 | 0.84229 | -122.1725 | -122.4655 | 1.1444 | 1.0895 | 0.97504 | 0.24719 | 0.13275 | -0.091553 | -123.1293 | -123.4955 | 0.19684 | 0.24262 | 0.24262 | 0.33417 | 0.33417 | 0.30212 | 0.16479 | 0.28839 | 0.068665 | 0.45776 | 0.43488 | 1.3 | 0.34332 | -122.6303 | -123.5641 | 1.0071 | -0.022888 | 1.0483 | 0.14191
668.9844 | 123.5275 | -1.4465 | 122.113 | -0.13489 | 0.0015125 | 0.0065113 | 0.0020188 | 0.00054476 | 0.00021157 | -0.0035162 | -0.021668 | 0.013159 | 0.021723 | 0.0027686 | -0.00086514 | -0.00014089 | -0.0031339 | -0.39825 | -0.041199 | -0.56763 | -0.49439 | -0.35706 | -0.45319 | -0.37079 | -1.3916 | -1.0345 | -1.5244 | -1.3641 | -1.2634 | -1.3687 | -1.2589 | 0.87891 | -122.1542 | -122.6074 | 1.0895 | 1.0757 | 0.99335 | 0.19684 | 0.11444 | -0.07782 | -123.1476 | -123.4772 | 0.18311 | 0.18768 | 0.07782 | 0.2655 | 0.15564 | 0.21057 | 0.073242 | 0.26093 | 0.16022 | 0.52643 | 0.48981 | 1.4053 | 0.41199 | -122.6807 | -123.6374 | 0.95215 | 0.082397 | 1.0483 | 0.054931
670.0469 | 123.5001 | -1.4236 | 122.1359 | -0.112 | 0.0032215 | 0.0080065 | 0.00095062 | -9.604e-05 | 0.00021157 | -0.0011664 | -0.0064087 | 0.013373 | 0.023219 | -0.0064172 | -0.0019333 | -0.0014227 | -0.0037747 | -0.35706 | -0.07782 | -0.54016 | -0.4303 | -0.27924 | -0.39825 | -0.31128 | -1.3367 | -1.0529 | -1.5152 | -1.3962 | -1.2589 | -1.3596 | -1.268 | 0.88348 | -122.2137 | -122.5662 | 1.1444 | 1.1124 | 1.0254 | 0.22888 | 0.14191 | -0.091553 | -123.1888 | -123.5321 | 0.1648 | 0.15564 | 0.064087 | 0.24719 | 0.15564 | 0.26093 | 0.10986 | 0.25635 | 0.11902 | 0.46234 | 0.46234 | 1.3458 | 0.37079 | -122.6761 | -123.6511 | 0.99335 | 0.027466 | 1.0666 | 0.086975
670.9844 | 123.5138 | -1.4465 | 122.1313 | -0.16541 | 0.0012989 | 0.0073657 | 0.0020188 | 0.00011756 | -0.00021583 | 0.00032904 | 0.011902 | 0.012732 | 0.021296 | -0.0012902 | -1.0744e-05 | -0.00035469 | -0.00014315 | -0.43488 | -0.036621 | -0.56763 | -0.4715 | -0.004578 | -0.39825 | -0.55847 | -1.442 | -1.0162 | -1.5152 | -1.4145 | -1.3046 | -1.3962 | -1.2955 | 0.87891 | -122.168 | -122.6028 | 1.442 | 0.88806 | 1.0483 | 0.009155 | 0.16937 | -0.068665 | -123.1476 | -123.5458 | 0.14191 | 0.15106 | 0.050354 | 0.21973 | 0.11902 | 0.56305 | 0.09613 | 0.21057 | 0.10071 | 0.53101 | 0.49896 | 1.4099 | 0.4303 | -122.699 | -123.6465 | 0.97504 | 0.032043 | 1.0117 | 0.004577
672.0469 | 123.5229 | -1.4328 | 122.1405 | -0.15015 | 0.0012989 | 0.0080065 | 0.0030868 | -0.00073704 | 0.00085237 | -0.00031196 | -0.064392 | 0.014227 | 0.022364 | 0.0034094 | -0.0019333 | -0.00056829 | 0.0034885 | -0.36163 | -0.045776 | -0.59052 | -0.45776 | -0.3067 | -0.46234 | -0.36621 | -1.355 | -1.0529 | -1.5198 | -1.3733 | -1.2726 | -1.3687 | -1.2589 | 0.84229 | -122.1863 | -122.5983 | 1.1261 | 1.0666 | 0.97046 | 0.2243 | 0.12817 | -0.086975 | -123.1934 | -123.5138 | 0.16022 | 0.17395 | 0.064087 | 0.26093 | 0.15106 | 0.28381 | 0.13275 | 0.24719 | 0.14648 | 0.54474 | 0.46692 | 1.387 | 0.37994 | -122.731 | -123.6603 | 0.97504 | 0.059509 | 1.0712 | 0.07782
673 | 123.5687 | -1.4008 | 122.1039 | -0.14252 | 1.7082e-05 | 0.0077929 | -0.00033118 | 0.0011856 | -0.002352 | 0.00054264 | 0.063782 | 0.014227 | 0.024073 | -0.0027856 | -0.0023605 | 0.00049991 | 0.0024203 | -0.39825 | -0.09613 | -0.56305 | -0.45776 | -0.3067 | -0.44403 | -0.34332 | -1.3596 | -1.0803 | -1.5289 | -1.3504 | -1.236 | -1.3229 | -1.236 | 0.83771 | -122.2 | -122.5616 | 1.0941 | 1.0574 | 0.95673 | 0.21973 | 0.11902 | -0.12817 | -123.1842 | -123.4543 | 0.1648 | 0.1648 | 0.07782 | 0.29297 | 0.20599 | 0.25635 | 0.10529 | 0.29297 | 0.17853 | 0.46692 | 0.44861 | 1.3046 | 0.32044 | -122.6669 | -123.6328 | 0.94299 | 0.050354 | 1.0025 | 0.041199
674 | 123.4314 | -1.4145 | 122.1542 | -0.15778 | 0.0030079 | 0.0077929 | 0.002446 | 0.0018266 | 0.0023478 | -9.8356e-05 | -0.067444 | 0.013586 | 0.021937 | 0.0029822 | -0.0030013 | 0.0032769 | 0.0019931 | -0.44403 | -0.082397 | -0.61798 | -0.54474 | -0.41657 | -0.56305 | -0.44861 | -1.4465 | -1.0529 | -1.5518 | -1.4099 | -1.3504 | -1.3962 | -1.2451 | 0.79651 | -122.2366 | -122.699 | 0.99792 | 0.96588 | 0.85144 | 0.16937 | 0.054932 | -0.13733 | -123.2071 | -123.5641 | 0.064087 | 0.16937 | 0.018311 | 0.3067 | 0.15564 | 0.20142 | 0.073242 | 0.20142 | 0.14191 | 0.53558 | 0.49896 | 1.3321 | 0.36163 | -122.7722 | -123.7061 | 0.86975 | 0.004578 | 0.97046 | -0.032043
675.0469 | 123.5321 | -1.4557 | 122.1176 | -0.14252 | 0.00065788 | 0.0067249 | -0.00011758 | -0.0011642 | 0.0019204 | -0.0018072 | 0.021057 | 0.015936 | 0.022578 | -0.0017176 | -0.00065154 | -0.00035469 | -0.00099755 | -0.35248 | -0.064087 | -0.54474 | -0.43945 | -0.28381 | -0.41199 | -0.32501 | -1.3596 | -1.0712 | -1.5472 | -1.4053 | -1.2772 | -1.3824 | -1.2863 | 0.91095 | -122.1817 | -122.5571 | 1.1719 | 1.1307 | 1.0437 | 0.21973 | 0.13275 | -0.091553 | -123.1888 | -123.5229 | 0.17853 | 0.16937 | 0.073242 | 0.26093 | 0.1648 | 0.26093 | 0.10529 | 0.27008 | 0.14191 | 0.48065 | 0.47607 | 1.3916 | 0.38452 | -122.6624 | -123.6649 | 1.0162 | 0.050354 | 1.1032 | 0.09613
675.9844 | 123.5733 | -1.4191 | 122.081 | -0.096741 | 0.0034351 | 0.0080065 | 0.0045822 | 0.0016128 | 0.0012796 | 0.00032904 | -0.046082 | 0.0138 | 0.022578 | 0.0014868 | -0.0010787 | 0.0019953 | -0.00078395 | -0.42572 | -0.07782 | -0.60883 | -0.49439 | -0.35706 | -0.50812 | -0.39368 | -1.3504 | -1.0757 | -1.5244 | -1.3321 | -1.236 | -1.3275 | -1.2131 | 0.81024 | -122.1588 | -122.5754 | 1.062 | 1.0254 | 0.91095 | 0.21515 | 0.10071 | -0.10529 | -123.1567 | -123.4131 | 0.18311 | 0.20599 | 0.091552 | 0.31128 | 0.19684 | 0.25177 | 0.11444 | 0.28839 | 0.19226 | 0.53101 | 0.44861 | 1.3412 | 0.34332 | -122.6898 | -123.6053 | 0.92468 | 0.086975 | 0.99335 | 0.068664
677.0625 | 123.5596 | -1.4465 | 122.113 | -0.10437 | 0.0030079 | 0.0054431 | 0.004155 | 0.0016128 | 0.00042517 | 0.00011544 | -0.027771 | 0.012518 | 0.020655 | 0.0023414 | -0.0010787 | -0.00014089 | 0.00071145 | -0.39825 | -0.07782 | -0.59967 | -0.48981 | -0.35248 | -0.45319 | -0.37994 | -1.3962 | -1.0712 | -1.5656 | -1.3779 | -1.2772 | -1.3779 | -1.2726 | 0.84686 | -122.1909 | -122.6028 | 1.0941 | 1.0666 | 0.99335 | 0.21973 | 0.14648 | -0.11902 | -123.1842 | -123.4909 | 0.16937 | 0.17395 | 0.068664 | 0.29297 | 0.18768 | 0.24719 | 0.10986 | 0.28839 | 0.18768 | 0.52185 | 0.49439 | 1.3687 | 0.37537 | -122.7127 | -123.6786 | 0.95673 | 0.068664 | 1.0483 | 0.050354
677.9844 | 123.6237 | -1.4008 | 122.0673 | -0.18829 | 0.0019397 | 0.0073657 | 0.001805 | -0.00030984 | -0.0012838 | -9.8356e-05 | 0.0057983 | 0.011023 | 0.021082 | 0.00063238 | -0.00086514 | -0.00078189 | 0.00071145 | -0.3891 | -0.11902 | -0.58594 | -0.44403 | -0.27924 | -0.43488 | -0.35248 | -1.3092 | -1.1124 | -1.5152 | -1.3138 | -1.2039 | -1.3092 | -1.2131 | 0.81482 | -122.1863 | -122.5113 | 1.1215 | 1.0483 | 0.96588 | 0.23346 | 0.15106 | -0.11444 | -123.1796 | -123.381 | 0.19684 | 0.18768 | 0.091553 | 0.30212 | 0.20599 | 0.3067 | 0.14191 | 0.31128 | 0.20142 | 0.46692 | 0.40283 | 1.2817 | 0.28839 | -122.6532 | -123.5825 | 0.95673 | 0.086975 | 1.0117 | 0.091553
678.9844 | 123.5367 | -1.4557 | 122.1268 | -0.12726 | 0.00065788 | 0.0075793 | 0.00095062 | -0.0037276 | 0.0014932 | 0.0018242 | -0.04303 | 0.014227 | 0.024928 | 0.0014868 | -0.0012923 | 0.00028631 | 0.00028405 | -0.37994 | -0.09613 | -0.59052 | -0.48981 | -0.33417 | -0.45776 | -0.3891 | -1.3733 | -1.0757 | -1.5564 | -1.3824 | -1.2772 | -1.3779 | -1.2817 | 0.86517 | -122.2229 | -122.6166 | 1.1215 | 1.0666 | 0.99792 | 0.20142 | 0.13275 | -0.10071 | -123.2025 | -123.5092 | 0.17853 | 0.17395 | 0.077819 | 0.27466 | 0.17853 | 0.25635 | 0.10071 | 0.27923 | 0.17395 | 0.49439 | 0.48065 | 1.3596 | 0.37994 | -122.7173 | -123.6832 | 0.96588 | 0.073242 | 1.0757 | 0.082397
680.0469 | 123.6465 | -1.4145 | 122.0535 | -0.11963 | 0.0030079 | 0.0060839 | 0.00030982 | -0.0050094 | 0.00085237 | -0.003089 | 0.075989 | 0.012732 | 0.024714 | -8.62e-06 | -0.0032149 | -0.00099549 | -0.00014315 | -0.37994 | -0.10071 | -0.54474 | -0.40283 | -0.19226 | -0.37994 | -0.27008 | -1.268 | -1.1032 | -1.5244 | -1.3092 | -1.1627 | -1.2589 | -1.2039 | 0.86975 | -122.1542 | -122.4564 | 1.2222 | 1.1444 | 1.0345 | 0.27466 | 0.16479 | -0.10986 | -123.1567 | -123.3627 | 0.25177 | 0.21057 | 0.15564 | 0.32044 | 0.2655 | 0.35248 | 0.14191 | 0.36163 | 0.21515 | 0.44403 | 0.42114 | 1.3138 | 0.31128 | -122.5983 | -123.5779 | 1.0117 | 0.10529 | 1.0345 | 0.14648
680.9844 | 123.5275 | -1.4328 | 122.1313 | -0.112 | 0.0025805 | 0.0067249 | 0.00052342 | 0.0018266 | -0.00042943 | 0.0026788 | -0.055237 | 0.013373 | 0.022578 | 0.0061866 | -0.00022434 | 0.0015679 | -0.0050565 | -0.40741 | -0.10071 | -0.59509 | -0.50354 | -0.32959 | -0.4715 | -0.33417 | -1.3504 | -1.0162 | -1.4648 | -1.3687 | -1.2955 | -1.3824 | -1.2772 | 0.83771 | -122.2321 | -122.6349 | 1.1032 | 1.0986 | 0.9613 | 0.26093 | 0.1236 | -0.032044 | -123.1476 | -123.5001 | 0.13733 | 0.15564 | 0.050354 | 0.18768 | 0.082398 | 0.2655 | 0.091553 | 0.16937 | 0.096131 | 0.49438 | 0.44861 | 1.3321 | 0.41657 | -122.7264 | -123.5962 | 0.92926 | 0.064087 | 1.0254 | 0.082397
682.0469 | 123.4863 | -1.4603 | 122.1039 | -0.058594 | 0.0012989 | 0.0045887 | 0.0015914 | -0.0011642 | 0.0032022 | -0.00073916 | 0.027161 | 0.014868 | 0.021937 | 0.0029822 | -0.0015059 | -0.00099549 | 0.00049765 | -0.41199 | -0.07782 | -0.57678 | -0.50354 | -0.36163 | -0.48981 | -0.39825 | -1.4236 | -1.0712 | -1.5701 | -1.442 | -1.3229 | -1.4145 | -1.3229 | 0.88348 | -122.1817 | -122.6074 | 1.0986 | 1.062 | 0.97046 | 0.17853 | 0.086975 | -0.10986 | -123.175 | -123.5458 | 0.13733 | 0.13733 | 0.045776 | 0.24719 | 0.15564 | 0.21515 | 0.073242 | 0.24719 | 0.12817 | 0.49896 | 0.49896 | 1.3824 | 0.3891 | -122.6807 | -123.674 | 0.95673 | 0.01831 | 1.0483 | 0.036621
683 | 123.555 | -1.442 | 122.0993 | -0.24933 | -0.00062372 | 0.0084339 | 0.002446 | 0.0018266 | -0.0010702 | 0.00075624 | 0.024109 | 0.014227 | 0.023432 | -0.0074854 | -0.00065154 | -0.00035469 | 0.0030613 | -0.39825 | -0.1236 | -0.58136 | -0.44403 | -0.28839 | -0.46692 | -0.3479 | -1.3412 | -1.0941 | -1.5335 | -1.355 | -1.2589 | -1.355 | -1.2497 | 0.8606 | -122.2229 | -122.5433 | 1.1536 | 1.0941 | 0.97504 | 0.23346 | 0.11444 | -0.091552 | -123.1934 | -123.4543 | 0.18311 | 0.19226 | 0.086976 | 0.28381 | 0.17853 | 0.29297 | 0.13733 | 0.27466 | 0.17853 | 0.45776 | 0.43945 | 1.3184 | 0.3479 | -122.6807 | -123.6328 | 0.99792 | 0.086976 | 1.0437 | 0.10071
684.0469 | 123.4222 | -1.4099 | 122.0718 | -0.13489 | 0.0032215 | 0.0062975 | -0.00054478 | 0.0011856 | 0.0017068 | -0.00031196 | 0.054626 | 0.012305 | 0.022578 | -0.0040674 | -0.0015059 | 7.2706e-05 | -0.0014249 | -0.3479 | -0.11902 | -0.54016 | -0.42114 | -0.22888 | -0.37994 | -0.29755 | -1.268 | -1.1078 | -1.5472 | -1.3184 | -1.1856 | -1.2863 | -1.2222 | 0.86975 | -122.1909 | -122.493 | 1.181 | 1.1124 | 1.03 | 0.24262 | 0.16022 | -0.13733 | -123.1796 | -123.3902 | 0.2243 | 0.18768 | 0.1236 | 0.32501 | 0.26093 | 0.31128 | 0.11902 | 0.36163 | 0.22888 | 0.42114 | 0.43945 | 1.2909 | 0.30212 | -122.612 | -123.6191 | 0.98877 | 0.091553 | 1.062 | 0.14191
684.9844 | 123.5413 | -1.4511 | 122.1313 | -0.15015 | 0.0015125 | 0.0065113 | 0.0037276 | 0.0011856 | -0.00064303 | 0.0022516 | -0.055237 | 0.014441 | 0.022151 | 0.00020498 | -0.0030013 | 0.0011407 | 0.00028405 | -0.41657 | -0.082397 | -0.6134 | -0.5127 | -0.37994 | -0.47607 | -0.39825 | -1.3824 | -1.0849 | -1.5564 | -1.3824 | -1.2726 | -1.3779 | -1.268 | 0.83771 | -122.2137 | -122.644 | 1.0712 | 1.0529 | 0.97504 | 0.21515 | 0.13733 | -0.10528 | -123.2162 | -123.5138 | 0.17853 | 0.18311 | 0.073242 | 0.28839 | 0.17853 | 0.23346 | 0.10071 | 0.28381 | 0.17395 | 0.53101 | 0.4715 | 1.3687 | 0.36621 | -122.7448 | -123.6877 | 0.93842 | 0.068665 | 1.0345 | 0.068665
686.0469 | 123.4085 | -1.4648 | 122.2092 | -0.096741 | 0.0010853 | 0.0052295 | 0.00030982 | -0.0045822 | -0.00085663 | -0.00138 | 0.0057983 | 0.01145 | 0.023005 | -0.0023584 | -0.00043794 | -0.0014227 | 0.0015659 | -0.44403 | -0.068665 | -0.59509 | -0.54016 | -0.39368 | -0.49896 | -0.40741 | -1.4557 | -1.0529 | -1.5793 | -1.4465 | -1.3184 | -1.4328 | -1.3275 | 0.86975 | -122.2778 | -122.7493 | 1.0712 | 1.0574 | 0.96588 | 0.18768 | 0.096131 | -0.11444 | -123.262 | -123.6557 | 0.14648 | 0.13733 | 0.032044 | 0.25177 | 0.14648 | 0.20142 | 0.054932 | 0.26093 | 0.13275 | 0.52643 | 0.52643 | 1.3962 | 0.41199 | -122.8043 | -123.7885 | 0.92468 | 0.018311 | 1.0208 | 0.009156
686.9844 | 123.6237 | -1.4191 | 122.081 | -0.18066 | 0.0010853 | 0.0073657 | 0.00030982 | 0.0016128 | -0.0021384 | 0.0011834 | -0.018616 | 0.013373 | 0.02386 | -8.62e-06 | -0.0027877 | 0.00049991 | 0.00092505 | -0.38452 | -0.16022 | -0.58136 | -0.42114 | -0.28839 | -0.44861 | -0.35248 | -1.3 | -1.1215 | -1.5244 | -1.3046 | -1.2085 | -1.3321 | -1.2268 | 0.83771 | -122.2412 | -122.5021 | 1.1307 | 1.0666 | 0.97046 | 0.22888 | 0.13275 | -0.10529 | -123.2025 | -123.3856 | 0.21057 | 0.19226 | 0.086975 | 0.29755 | 0.19226 | 0.29297 | 0.16022 | 0.31586 | 0.21973 | 0.42114 | 0.40283 | 1.2589 | 0.29755 | -122.6624 | -123.6053 | 0.99792 | 0.11444 | 1.0345 | 0.11902
688.0625 | 123.4772 | -1.4786 | 122.1085 | -0.14252 | 0.0047169 | 0.0069385 | 0.0045822 | 0.0031082 | 0.00021157 | 0.00032904 | -0.070496 | 0.0138 | 0.021723 | 0.0023414 | -0.00043794 | 0.00071351 | 7.0452e-05 | -0.45319 | -0.11444 | -0.62714 | -0.56305 | -0.4303 | -0.55389 | -0.48065 | -1.4557 | -1.0895 | -1.5839 | -1.4511 | -1.3824 | -1.4877 | -1.3412 | 0.85144 | -122.2229 | -122.6715 | 1.0483 | 0.99792 | 0.92468 | 0.14648 | 0.073242 | -0.10529 | -123.1979 | -123.5596 | 0.096131 | 0.13733 | -0.009155 | 0.24261 | 0.09613 | 0.19684 | 0.064087 | 0.20142 | 0.13275 | 0.5127 | 0.49438 | 1.3641 | 0.3891 | -122.7356 | -123.6923 | 0.91553 | 0.027466 | 1.0254 | 0.022889
688.9844 | 123.5229 | -1.4648 | 122.0856 | -0.14252 | 0.0023669 | 0.0073657 | 0.0020188 | -0.00095064 | -0.00064303 | 0.0022516 | -0.04303 | 0.015295 | 0.022151 | 0.004264 | -0.0019333 | 0.0011407 | 0.0017795 | -0.41657 | -0.10986 | -0.60883 | -0.4303 | -0.28381 | -0.44403 | -0.40741 | -1.3733 | -1.0483 | -1.506 | -1.4053 | -1.3184 | -1.4328 | -1.3092 | 0.85602 | -122.1954 | -122.5159 | 1.181 | 1.0574 | 1.0208 | 0.20142 | 0.16479 | -0.041198 | -123.1338 | -123.4909 | 0.14648 | 0.15564 | 0.032044 | 0.19684 | 0.073242 | 0.32501 | 0.17853 | 0.18768 | 0.10071 | 0.49896 | 0.45776 | 1.355 | 0.41657 | -122.6944 | -123.5916 | 1.0345 | 0.05951 | 1.0483 | 0.091553
690.0469 | 123.5092 | -1.4694 | 122.0993 | -0.096741 | 0.0012989 | 0.0065113 | 0.0011642 | -0.0013778 | -0.0012838 | -0.0018072 | 0.0027465 | 0.014655 | 0.024073 | -0.00086302 | -0.0025741 | 0.00028631 | -0.00078395 | -0.44861 | -0.082397 | -0.62714 | -0.24261 | -0.27466 | -0.79651 | -0.40283 | -1.4694 | -1.0437 | -1.5335 | -1.4557 | -1.3321 | -1.442 | -1.3229 | 0.84229 | -122.1817 | -122.3419 | 1.1948 | 1.0666 | 0.67291 | 0.2243 | -0.16937 | -0.064087 | -123.143 | -123.555 | 0.13733 | 0.14648 | 0.027465 | 0.21057 | 0.091552 | 0.35248 | 0.38452 | 0.20142 | 0.07782 | 0.54474 | 0.48981 | 1.387 | 0.42572 | -122.7264 | -123.6328 | 1.2268 | 0.013733 | 1.0208 | 0
690.9844 | 123.5458 | -1.474 | 122.0947 | -0.13489 | 0.0017261 | 0.0069385 | 0.0022324 | 0.0048172 | 0.0012796 | -0.0024482 | -0.021668 | 0.013159 | 0.021296 | -0.00064942 | -0.00043794 | 0.00028631 | 0.0026341 | -0.40741 | -0.091553 | -0.62256 | -0.49896 | -0.3479 | -0.4715 | -0.40741 | -1.3962 | -1.1124 | -1.5701 | -1.4008 | -1.3046 | -1.3962 | -1.3046 | 0.85144 | -122.1863 | -122.5937 | 1.1261 | 1.0666 | 1.0025 | 0.21515 | 0.15106 | -0.09613 | -123.2071 | -123.4955 | 0.16937 | 0.16937 | 0.07782 | 0.2655 | 0.17395 | 0.27466 | 0.1236 | 0.2655 | 0.16937 | 0.53101 | 0.45776 | 1.3824 | 0.36163 | -122.7173 | -123.6649 | 0.97504 | 0.073242 | 1.0666 | 0.07782
691.9844 | 123.4131 | -1.4557 | 122.1405 | -0.073852 | 0.0017261 | 0.0052295 | -0.00075838 | -0.00052344 | 0.00063877 | -0.00031196 | 0.018005 | 0.014655 | 0.023005 | -0.0029992 | 0.00020286 | -0.00056829 | -0.0042019 | -0.45319 | -0.07782 | -0.6134 | -0.55389 | -0.40741 | -0.50354 | -0.42572 | -1.4832 | -1.0757 | -1.5793 | -1.4603 | -1.3321 | -1.1307 | -1.1032 | 0.84229 | -122.2183 | -122.6944 | 1.0483 | 1.03 | 0.95215 | 0.18768 | 0.10986 | -0.1236 | -123.2162 | -123.6008 | 0.1236 | 0.35248 | 0.32501 | 0.47608 | 0.44861 | 0.20599 | 0.059509 | 0.24719 | 0.11902 | 0.53558 | 0.50354 | 1.3779 | 0.37994 | -122.7539 | -123.7198 | 0.90179 | -0.004578 | 1.0025 | -0.027466
693.0625 | 123.5825 | -1.4145 | 121.9894 | -0.20355 | 0.0010853 | 0.0065113 | 0.0011642 | 0.0028946 | -0.00064303 | -0.00073916 | 0.0027465 | 0.012518 | 0.024073 | -0.00043582 | -0.00086514 | 0.0011407 | 0.0026341 | -0.3891 | -0.13733 | -0.59967 | -0.47607 | -0.28839 | -0.45776 | -0.37537 | -1.3046 | -1.1307 | -1.5427 | -1.3275 | -1.2405 | -1.3321 | -1.2131 | 0.81482 | -122.1268 | -122.4655 | 1.1261 | 1.0391 | 0.95673 | 0.2243 | 0.14191 | -0.12817 | -123.1201 | -123.317 | 0.17395 | 0.20142 | 0.082398 | 0.32959 | 0.21057 | 0.31128 | 0.1236 | 0.30212 | 0.21515 | 0.46234 | 0.41199 | 1.2772 | 0.28381 | -122.5891 | -123.5321 | 0.93842 | 0.086975 | 1.0254 | 0.10986
693.9844 | 123.5275 | -1.4648 | 122.1085 | -0.18829 | 0.0019397 | 0.0056567 | 0.0015914 | 0.0016128 | 0.00021157 | -0.0024482 | -0.027771 | 0.015295 | 0.021937 | 0.00020498 | -0.00022434 | 0.00049991 | -0.0022793 | -0.42114 | -0.09613 | -0.61798 | -0.5127 | -0.36163 | -0.49439 | -0.42572 | -1.3779 | -1.0895 | -1.5747 | -1.3916 | -1.2909 | -1.3962 | -1.2772 | 0.84686 | -122.2046 | -122.6212 | 1.1032 | 1.0391 | 0.97046 | 0.19226 | 0.1236 | -0.10986 | -123.1979 | -123.5001 | 0.17395 | 0.18768 | 0.068665 | 0.29755 | 0.17853 | 0.25635 | 0.10529 | 0.28381 | 0.18311 | 0.52185 | 0.48523 | 1.3687 | 0.37537 | -122.7264 | -123.6832 | 0.95215 | 0.073242 | 1.0437 | 0.086975
695.0469 | 123.5321 | -1.4511 | 122.1222 | -0.089111 | 0.00087168 | 0.0060839 | 0.0011642 | 0.0033218 | 0.00021157 | -0.002021 | -0.00030511 | 0.015509 | 0.024714 | -0.0010766 | -0.00086514 | 0.00071351 | -0.0027065 | -0.44403 | -0.09613 | -0.63171 | -0.54016 | -0.41657 | -0.5127 | -0.41199 | -1.4557 | -1.0849 | -1.5747 | -1.4374 | -1.3 | -1.4053 | -1.3367 | 0.8194 | -122.2183 | -122.6624 | 1.0345 | 1.0391 | 0.93842 | 0.21973 | 0.11902 | -0.1236 | -123.2071 | -123.5596 | 0.15106 | 0.11444 | 0.045777 | 0.23804 | 0.16937 | 0.21515 | 0.091553 | 0.27466 | 0.13733 | 0.53558 | 0.48981 | 1.355 | 0.36621 | -122.7539 | -123.6969 | 0.91095 | 0.013733 | 1.0071 | -0.004577
695.9844 | 123.5184 | -1.4877 | 122.1176 | -0.35614 | 0.00044428 | 0.0073657 | 0.00095062 | 0.00075836 | 0.0019204 | -0.0011664 | 0.0027465 | 0.013373 | 0.023219 | 0.0027686 | -0.0012923 | -0.0027045 | 0.0041293 | -0.37994 | -0.050354 | -0.57678 | -0.53558 | -0.39825 | -0.52185 | -0.42114 | -1.4603 | -1.0757 | -1.5656 | -1.4465 | -1.3275 | -1.4236 | -1.3367 | 0.91095 | -122.168 | -122.6532 | 1.0895 | 1.0666 | 0.96588 | 0.15564 | 0.054931 | -0.07782 | -123.1934 | -123.5641 | 0.16022 | 0.15106 | 0.064087 | 0.22888 | 0.14191 | 0.17853 | 0.041199 | 0.23804 | 0.11902 | 0.52643 | 0.48981 | 1.4374 | 0.41199 | -122.6944 | -123.6832 | 0.95215 | 0.041199 | 1.1078 | 0.027466
697.0469 | 123.5504 | -1.4786 | 122.1222 | -0.12726 | 0.0021533 | 0.0060839 | 0.00030982 | 0.00033116 | -0.0014974 | -0.00095276 | 0.0027465 | 0.013373 | 0.02151 | 0.00041878 | -0.0012923 | 0.00049991 | 0.0032749 | -0.43488 | -0.09613 | -0.63171 | -0.52643 | -0.42114 | -0.50354 | -0.43488 | -1.4511 | -1.0757 | -1.5656 | -1.4191 | -1.3092 | -1.4053 | -1.3138 | 0.84686 | -122.2183 | -122.6486 | 1.0574 | 1.0437 | 0.97504 | 0.19684 | 0.12817 | -0.086975 | -123.1979 | -123.5413 | 0.16937 | 0.1648 | 0.073243 | 0.25177 | 0.16022 | 0.21057 | 0.10529 | 0.25635 | 0.14648 | 0.53558 | 0.48981 | 1.3824 | 0.40283 | -122.7539 | -123.6877 | 0.95215 | 0.05951 | 1.0437 | 0.027466
697.9844 | 123.4863 | -1.4923 | 122.1405 | -0.12726 | 0.0021533 | 0.0045887 | 0.00030982 | 0.00033116 | 0.00063877 | -0.00052556 | 0.0088501 | 0.014014 | 0.020655 | -0.0055628 | -0.0012923 | 0.0017817 | -0.0031339 | -0.45776 | -0.10986 | -0.6134 | -0.5722 | -0.40283 | -0.5127 | -0.42572 | -1.4511 | -1.0803 | -1.5701 | -1.4648 | -1.3275 | -1.4374 | -1.3321 | 0.87891 | -122.2504 | -122.7127 | 1.0895 | 1.0666 | 0.97962 | 0.18768 | 0.10071 | -0.077819 | -123.2208 | -123.6053 | 0.1648 | 0.16022 | 0.054932 | 0.23804 | 0.13275 | 0.21057 | 0.041198 | 0.24261 | 0.10529 | 0.50354 | 0.48981 | 1.3824 | 0.41199 | -122.7539 | -123.7106 | 0.92011 | 0.027466 | 1.0345 | 0.041199
699.0469 | 123.4772 | -1.4648 | 122.1039 | -0.096741 | 0.0025805 | 0.0080065 | 0.002446 | 0.0013992 | 0.0023478 | 0.00075624 | -0.067444 | 0.013373 | 0.022151 | 0.0023414 | -0.0015059 | 0.0015679 | -0.0018521 | -0.48981 | -0.13733 | -0.6546 | -0.55847 | -0.4715 | -0.60883 | -0.48065 | -1.4923 | -1.0803 | -1.5701 | -1.4557 | -1.4008 | -1.4969 | -1.3641 | 0.81024 | -122.2412 | -122.6624 | 0.99335 | 0.98419 | 0.85602 | 0.17395 | 0.045776 | -0.10529 | -123.1842 | -123.5596 | 0.064087 | 0.10071 | -0.032043 | 0.20599 | 0.073242 | 0.18311 | 0.09613 | 0.16937 | 0.11444 | 0.51727 | 0.48981 | 1.3275 | 0.38452 | -122.7585 | -123.674 | 0.90637 | 0.009156 | 0.97504 | -0.027466
699.9844 | 123.5367 | -1.4832 | 122.1085 | -0.112 | 0.0030079 | 0.0069385 | -0.00011758 | 0.0011856 | -0.0010702 | -0.0033026 | -0.0064087 | 0.013373 | 0.023219 | -0.0079126 | -0.00086514 | -0.0014227 | -0.00035675 | -0.42572 | -0.10986 | -0.63171 | -0.54932 | -0.37079 | -0.49896 | -0.4303 | -1.4053 | -1.1215 | -1.5656 | -1.3916 | -1.2955 | -1.4053 | -1.2863 | 0.85144 | -122.2183 | -122.6578 | 1.1124 | 1.0529 | 0.98419 | 0.20142 | 0.13275 | -0.082398 | -123.23 | -123.5001 | 0.18768 | 0.19684 | 0.07782 | 0.27924 | 0.16022 | 0.26093 | 0.082398 | 0.27008 | 0.17395 | 0.52185 | 0.44403 | 1.3733 | 0.36163 | -122.7402 | -123.674 | 0.93384 | 0.091552 | 1.0574 | 0.07782
701.0625 | 123.6008 | -1.442 | 122.0718 | -0.15015 | -0.00062372 | 0.0069385 | 0.0020188 | 0.00054476 | 0.0019204 | -0.0011664 | 0.011902 | 0.013373 | 0.021082 | -0.0023584 | 0.00084386 | 0.00028631 | -0.00014315 | -0.45319 | -0.14648 | -0.63629 | -0.53101 | -0.36621 | -0.53101 | -0.42572 | -1.3779 | -1.1169 | -1.5289 | -1.3229 | -1.2863 | -1.3458 | -1.2222 | 0.80566 | -122.2183 | -122.6028 | 1.0757 | 1.0162 | 0.91095 | 0.21057 | 0.10529 | -0.086975 | -123.1888 | -123.3948 | 0.15564 | 0.21973 | 0.096131 | 0.3067 | 0.18311 | 0.27008 | 0.10529 | 0.24262 | 0.20599 | 0.48981 | 0.41199 | 1.2955 | 0.32501 | -122.7081 | -123.6008 | 0.91095 | 0.11902 | 0.98877 | 0.064087
701.9844 | 123.4955 | -1.474 | 122.081 | -0.10437 | 0.0019397 | 0.0071521 | 0.001805 | -0.001805 | -0.0010702 | 0.00011544 | -0.021668 | 0.014014 | 0.021723 | 0.0027686 | -0.0012923 | 0.0022089 | 0.00049765 | -0.43945 | -0.1236 | -0.63171 | -0.56305 | -0.40741 | -0.55389 | -0.4715 | -1.442 | -1.0941 | -1.5884 | -1.4557 | -1.3641 | -1.4648 | -1.3504 | 0.84229 | -122.2046 | -122.644 | 1.0666 | 1.0025 | 0.92011 | 0.16022 | 0.07782 | -0.11444 | -123.175 | -123.5367 | 0.10986 | 0.1236 | 0.009155 | 0.23804 | 0.1236 | 0.2243 | 0.068665 | 0.2243 | 0.13275 | 0.50812 | 0.49439 | 1.3504 | 0.37994 | -122.7127 | -123.6694 | 0.91095 | 0.018311 | 1.0345 | 0.032043
703.0469 | 123.4818 | -1.4694 | 122.113 | -0.11963 | 0.0021533 | 0.0039477 | 0.00052342 | -0.00095064 | -0.00042943 | 0.001397 | 0.039368 | 0.014014 | 0.021723 | -0.0012902 | 0.00063026 | -0.00078189 | 0.00071145 | -0.45776 | -0.11444 | -0.60883 | -0.54932 | -0.40283 | -0.49439 | -0.41199 | -1.4603 | -1.0986 | -1.5976 | -1.4648 | -1.3412 | -1.4236 | -1.3504 | 0.8606 | -122.2275 | -122.6624 | 1.0666 | 1.0574 | 0.97504 | 0.19684 | 0.11444 | -0.12817 | -123.2117 | -123.5779 | 0.12817 | 0.11902 | 0.045776 | 0.24719 | 0.17395 | 0.20599 | 0.05951 | 0.25635 | 0.13275 | 0.49438 | 0.49896 | 1.355 | 0.37079 | -122.7219 | -123.7106 | 0.92011 | 0.004577 | 1.0117 | 0.009155
703.9844 | 123.5275 | -1.4786 | 122.0947 | -0.096741 | -0.00019652 | 0.0058703 | 0.001805 | -0.0050094 | 0.0012796 | -0.00031196 | -0.0033569 | 0.013586 | 0.021937 | 0.0014868 | -0.0025741 | -0.00014089 | -0.0033475 | -0.46692 | -0.10071 | -0.6134 | -0.54932 | -0.41657 | -0.54932 | -0.43488 | -1.474 | -1.1124 | -1.5793 | -1.4465 | -1.3275 | -1.442 | -1.3321 | 0.86517 | -122.1954 | -122.644 | 1.062 | 1.0437 | 0.92926 | 0.17853 | 0.064087 | -0.10071 | -123.2071 | -123.5413 | 0.15106 | 0.14648 | 0.036621 | 0.24719 | 0.13733 | 0.19684 | 0.064087 | 0.25177 | 0.13275 | 0.5127 | 0.46692 | 1.3779 | 0.36621 | -122.7081 | -123.674 | 0.92926 | 0.032044 | 1.0117 | 0.004578
704.9844 | 123.5321 | -1.4694 | 122.0673 | -0.22644 | 0.0025805 | 0.0067249 | 0.00073702 | 0.0016128 | 0.00063877 | -9.8356e-05 | -0.088806 | 0.013373 | 0.019801 | -0.00086302 | -0.0015059 | -0.00099549 | 0.0017795 | -0.48981 | -0.13275 | -0.64545 | -0.5722 | -0.45319 | -0.57678 | -0.51727 | -1.3458 | -1.0895 | -1.5656 | -1.4282 | -1.3367 | -1.4511 | -1.3275 | 0.82397 | -122.2 | -122.6395 | 1.0162 | 0.95215 | 0.89264 | 0.12817 | 0.068665 | -0.096131 | -123.1567 | -123.4955 | 0.13275 | 0.14191 | 0.01831 | 0.23804 | 0.11444 | 0.19226 | 0.073242 | 0.22888 | 0.13733 | 0.5127 | 0.47607 | 1.3367 | 0.37994 | -122.7127 | -123.6328 | 0.89722 | 0.041198 | 0.97961 | 0.1236
705.9844 | 123.5092 | -1.6617 | 121.9345 | -0.11963 | 0.0015125 | 0.0067249 | 0.0022324 | 0.0020402 | -0.00021583 | -0.003089 | -0.039978 | 0.014227 | 0.022578 | -0.0034264 | -0.0021469 | 0.0013543 | 0.00092505 | -0.43945 | -0.11902 | -0.6134 | -0.53101 | -0.36621 | -0.50812 | -0.44861 | -1.6113 | -1.2909 | -1.767 | -1.6251 | -1.5244 | -1.6479 | -1.5106 | 1.0483 | -122.0535 | -122.4655 | 1.2955 | 1.2131 | 1.1536 | 0.1648 | 0.10529 | -0.10529 | -123.2254 | -123.5596 | 0.13733 | 0.15106 | 0.013733 | 0.25635 | 0.11902 | 0.24719 | 0.082397 | 0.24262 | 0.14191 | 0.49438 | 0.47607 | 1.5427 | 0.37079 | -122.5479 | -123.7015 | 1.1307 | 0.036621 | 1.2222 | 0.050354

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2
-0.0896 | 32.396 | 31.0116 | 31.2237
0.9104 | 32.3847 | 31.0061 | 31.2238
1.9104 | 32.3762 | 31.003 | 31.2162
2.9104 | 32.4795 | 31.0163 | 31.2161
3.9104 | 33.1485 | 31.0026 | 31.212
4.9104 | 34.6197 | 30.9961 | 31.2085
5.9104 | 36.8264 | 30.9961 | 31.2117
6.9104 | 39.6586 | 31.0042 | 31.2185
7.9104 | 42.9793 | 30.9982 | 31.2243
8.9104 | 46.6902 | 31.0098 | 31.2375
9.9104 | 50.721 | 31.0214 | 31.2557
10.9104 | 55.0362 | 31.0369 | 31.2773
11.9104 | 59.6162 | 31.0526 | 31.3073
12.9104 | 64.3189 | 31.0807 | 31.3439
13.9104 | 69.2648 | 31.1206 | 31.3911
14.9104 | 74.3089 | 31.145 | 31.4369
15.9104 | 79.5067 | 31.2013 | 31.5117
16.9104 | 84.8282 | 31.2372 | 31.5782
17.9104 | 90.2903 | 31.3188 | 31.6668
18.9104 | 95.8153 | 31.3933 | 31.7637
19.9104 | 101.4717 | 31.4763 | 31.8716
20.9104 | 107.2106 | 31.5486 | 31.9871
21.9104 | 113.0012 | 31.6415 | 32.1206
22.9104 | 118.8435 | 31.7583 | 32.2676
23.9104 | 124.7972 | 31.8835 | 32.4263
24.9104 | 130.5962 | 32.0281 | 32.6061
25.9104 | 136.4224 | 32.1712 | 32.799
26.9104 | 142.3421 | 32.3391 | 33.0097
27.9104 | 148.2732 | 32.507 | 33.2333
28.9104 | 154.2388 | 32.6835 | 33.4856
29.9104 | 160.2396 | 32.889 | 33.745
30.9104 | 166.091 | 33.0992 | 34.0348
31.9104 | 171.9969 | 33.3297 | 34.342
32.9104 | 177.9961 | 33.5614 | 34.6693
33.9104 | 183.9349 | 33.8248 | 35.0115
34.9104 | 189.7957 | 34.1271 | 35.376
35.9104 | 195.6534 | 34.3948 | 35.7424
36.9104 | 201.4431 | 34.6954 | 36.1354
37.9104 | 207.2425 | 35.0144 | 36.548
38.9104 | 213.1225 | 35.3518 | 36.9812
39.9104 | 218.9956 | 35.6945 | 37.4267
40.9104 | 224.988 | 36.0666 | 37.8991
41.9104 | 230.9118 | 36.4538 | 38.3969
42.9104 | 236.7383 | 36.8716 | 38.8992
43.9104 | 242.5363 | 37.291 | 39.4295
44.9104 | 248.2596 | 37.7335 | 39.9681
45.9104 | 254.0144 | 38.1944 | 40.5435
46.9104 | 259.6761 | 38.669 | 41.144
47.9104 | 265.3204 | 39.1666 | 41.768
48.9104 | 270.9476 | 39.692 | 42.4096
49.9104 | 276.6277 | 40.2464 | 43.0678
50.9104 | 282.214 | 40.822 | 43.7565
51.9104 | 287.3887 | 41.4151 | 44.4579
52.9104 | 292.2633 | 42.0198 | 45.1829
53.9104 | 296.787 | 42.6352 | 45.9239
54.9104 | 300.898 | 43.2773 | 46.6756
55.9104 | 304.7383 | 43.9316 | 47.4487
56.9104 | 308.3995 | 44.582 | 48.2231
57.9104 | 311.8643 | 45.2612 | 49.0064
58.9104 | 315.094 | 45.9445 | 49.8035
59.9104 | 318.0846 | 46.6392 | 50.6071
60.9104 | 320.9712 | 47.3327 | 51.413
61.9104 | 323.6924 | 48.0445 | 52.2379
62.9104 | 325.9117 | 48.7503 | 53.081
63.9104 | 327.64 | 49.4734 | 53.925
64.9104 | 329.1606 | 50.2287 | 54.7723
65.9104 | 330.4974 | 50.954 | 55.6125
66.9104 | 331.5686 | 51.7085 | 56.4535
67.9104 | 332.4586 | 52.4847 | 57.2974
68.9104 | 333.0409 | 53.2889 | 58.1391
69.9104 | 333.3833 | 54.0492 | 58.9728
70.9104 | 333.7979 | 54.8761 | 59.8046
71.9104 | 334.2428 | 55.6881 | 60.6298
72.9104 | 334.4277 | 56.4934 | 61.4645
73.9104 | 334.3309 | 57.2906 | 62.2856
74.9104 | 334.2819 | 58.1107 | 63.1349
75.9104 | 334.0264 | 58.9102 | 63.9478
76.9104 | 333.7759 | 59.7266 | 64.7754
77.9104 | 333.4697 | 60.5433 | 65.5763
78.9104 | 333.1961 | 61.3443 | 66.3903
79.9104 | 333.05 | 62.1521 | 67.1796
80.9104 | 332.765 | 62.9622 | 67.9772
81.9104 | 332.4174 | 63.7712 | 68.763
82.9104 | 332.2207 | 64.5625 | 69.5404
83.9104 | 331.9223 | 65.3416 | 70.3091
84.9104 | 331.5246 | 66.113 | 71.0747
85.9104 | 331.0087 | 66.8633 | 71.8413
86.9104 | 330.594 | 67.6218 | 72.5811
87.9104 | 330.2076 | 68.3684 | 73.3194
88.9104 | 329.6521 | 69.1149 | 74.0462
89.9104 | 329.1433 | 69.8647 | 74.7786
90.9104 | 328.6089 | 70.602 | 75.4985
91.9104 | 328.3037 | 71.3331 | 76.2073
92.9104 | 327.9204 | 72.0433 | 76.9095
93.9104 | 327.3823 | 72.7521 | 77.5867
94.9104 | 326.7412 | 73.4439 | 78.252
95.9104 | 326.244 | 74.1262 | 78.922
96.9104 | 325.972 | 74.8027 | 79.5744
97.9104 | 325.5744 | 75.4656 | 80.2322
98.9104 | 325.153 | 76.1348 | 80.8765
99.9104 | 324.8352 | 76.7925 | 81.5362
100.9104 | 324.3873 | 77.4369 | 82.1665
101.9104 | 324.0526 | 78.0757 | 82.7917
102.9104 | 323.7501 | 78.6955 | 83.4207
103.9104 | 323.5097 | 79.3123 | 84.031
104.9104 | 323.2312 | 79.9303 | 84.6425
105.9104 | 323.0018 | 80.5152 | 85.2449
106.9104 | 322.6402 | 81.1169 | 85.8345
107.9104 | 322.5873 | 81.6936 | 86.4126
108.9104 | 322.4825 | 82.2637 | 86.9823
109.9104 | 322.328 | 82.8279 | 87.5398
110.9104 | 322.2643 | 83.3879 | 88.1116
111.9104 | 322.2825 | 83.933 | 88.6778
112.9104 | 322.3769 | 84.4944 | 89.2383
113.9104 | 322.5075 | 85.0533 | 89.8028
114.9104 | 322.652 | 85.6111 | 90.3558
115.9104 | 322.8281 | 86.1728 | 90.9349
116.9104 | 322.9236 | 86.7198 | 91.4989
117.9104 | 322.8941 | 87.2814 | 92.0616
118.9104 | 323.0272 | 87.8387 | 92.6216
119.9104 | 323.2635 | 88.3965 | 93.1738
120.9104 | 323.458 | 88.9659 | 93.7452
121.9104 | 323.5698 | 89.5188 | 94.3051
122.9104 | 323.7783 | 90.065 | 94.8688
123.9104 | 324.0917 | 90.6413 | 95.4306
124.9104 | 324.5167 | 91.1933 | 95.9954
125.9104 | 324.8504 | 91.7477 | 96.5613
126.9104 | 325.2204 | 92.3024 | 97.1348
127.9104 | 325.4823 | 92.8549 | 97.7108
128.9104 | 325.7817 | 93.4185 | 98.274
129.9104 | 326.0788 | 93.9685 | 98.8525
130.9104 | 326.3513 | 94.5279 | 99.4303
131.9104 | 326.6937 | 95.0773 | 100.0033
132.9104 | 326.9303 | 95.6179 | 100.5862
133.9104 | 327.0599 | 96.1669 | 101.1491
134.9104 | 327.259 | 96.7195 | 101.7148
135.9104 | 327.5521 | 97.2627 | 102.3009
136.9104 | 327.8317 | 97.8168 | 102.8712
137.9104 | 327.9326 | 98.3376 | 103.4476
138.9104 | 328.0311 | 98.8872 | 104.0251
139.9104 | 328.1741 | 99.432 | 104.5999
140.9104 | 328.3052 | 99.9744 | 105.1742
141.9104 | 328.4987 | 100.5327 | 105.7301
142.9104 | 328.647 | 101.0534 | 106.2934
143.9104 | 328.8356 | 101.6025 | 106.869
144.9104 | 328.8593 | 102.1254 | 107.4332
145.9104 | 328.8317 | 102.655 | 107.9989
146.9104 | 328.9388 | 103.1841 | 108.561
147.9104 | 329.0485 | 103.6979 | 109.1199
148.9104 | 329.1135 | 104.2427 | 109.6812
149.9104 | 329.0937 | 104.7829 | 110.2414
150.9104 | 329.111 | 105.2879 | 110.7866
151.9104 | 329.1696 | 105.8116 | 111.3391
152.9104 | 329.2342 | 106.3382 | 111.8908
153.9104 | 329.1468 | 106.8458 | 112.4346
154.9104 | 329.0354 | 107.3567 | 112.9797
155.9104 | 328.9789 | 107.87 | 113.5313
156.9104 | 328.9508 | 108.3987 | 114.0692
157.9104 | 328.9434 | 108.9056 | 114.6115
158.9104 | 328.8117 | 109.416 | 115.1384
159.9104 | 328.7871 | 109.9265 | 115.6728
160.926 | 328.8309 | 110.4657 | 116.2226
161.9104 | 328.8324 | 110.9713 | 116.7592
162.9104 | 328.8214 | 111.4882 | 117.2926
163.9104 | 328.9032 | 111.9929 | 117.8385
164.9104 | 328.9276 | 112.4941 | 118.3677
165.9104 | 328.85 | 113.0067 | 118.9124
166.9104 | 328.7904 | 113.5086 | 119.4613
167.9104 | 328.9022 | 114.0157 | 119.9924
168.9104 | 328.9483 | 114.5175 | 120.5263
169.9104 | 328.9144 | 114.9928 | 121.0618
170.9104 | 328.8402 | 115.4954 | 121.5915
171.9104 | 328.7447 | 115.9966 | 122.1188
172.9104 | 328.6986 | 116.4886 | 122.6458
173.9104 | 328.7147 | 116.9665 | 123.1673
174.9104 | 328.7878 | 117.4642 | 123.6815
175.9104 | 328.7027 | 117.9448 | 124.1941
176.9104 | 328.6922 | 118.4462 | 124.7042
177.9104 | 328.7407 | 118.9239 | 125.2024
178.9104 | 328.809 | 119.4436 | 125.7023
179.9104 | 328.8206 | 119.9261 | 126.195
180.9104 | 328.9013 | 120.4277 | 126.6903
181.9104 | 328.8455 | 120.903 | 127.191
182.9104 | 328.6898 | 121.3867 | 127.6821
183.9104 | 328.7158 | 121.872 | 128.1651
184.9104 | 328.7089 | 122.3353 | 128.6556
185.9104 | 328.7554 | 122.8212 | 129.1494
186.9104 | 328.7528 | 123.298 | 129.6426
187.9104 | 328.698 | 123.7559 | 130.1334
188.9104 | 328.7055 | 124.2293 | 130.6203
189.9104 | 328.7136 | 124.6846 | 131.1146
190.926 | 328.7749 | 125.1571 | 131.6084
191.9104 | 328.7613 | 125.6095 | 132.0893
192.9104 | 328.7459 | 126.0545 | 132.5813
193.9104 | 328.6371 | 126.5087 | 133.0715
194.9104 | 328.6698 | 126.9671 | 133.5657
195.9104 | 328.6466 | 127.4365 | 134.046
196.9104 | 328.7133 | 127.8811 | 134.5241
197.9104 | 328.751 | 128.333 | 135.0052
198.9104 | 328.8142 | 128.7957 | 135.4899
199.9104 | 328.749 | 129.2497 | 135.9621
200.9104 | 328.6886 | 129.7121 | 136.4357
201.9104 | 328.6137 | 130.1458 | 136.9216
202.9104 | 328.6041 | 130.598 | 137.3917
203.9104 | 328.6257 | 131.0342 | 137.8588
204.9104 | 328.6933 | 131.4662 | 138.3285
205.9104 | 328.7453 | 131.873 | 138.7894
206.9104 | 328.8321 | 132.3094 | 139.243
207.9104 | 328.949 | 132.7386 | 139.6971
208.9104 | 328.9445 | 133.1588 | 140.1536
209.9104 | 328.9145 | 133.5898 | 140.6004
210.9104 | 328.9283 | 134.0094 | 141.0511
211.9104 | 328.9766 | 134.4414 | 141.4769
212.9104 | 328.9656 | 134.8488 | 141.9191
213.9104 | 328.9641 | 135.2673 | 142.3531
214.9104 | 328.9166 | 135.6658 | 142.7949
215.9104 | 328.887 | 136.1087 | 143.2254
216.9104 | 328.8449 | 136.4937 | 143.6726
217.9104 | 328.7838 | 136.8966 | 144.1191
218.9104 | 328.6546 | 137.3194 | 144.5526
219.9104 | 328.5225 | 137.7188 | 144.9821
220.926 | 328.5009 | 138.1238 | 145.3919
221.9104 | 328.5195 | 138.536 | 145.7861
222.9104 | 328.4577 | 138.9262 | 146.1796
223.9104 | 328.4411 | 139.3246 | 146.5773
224.9104 | 328.4459 | 139.7249 | 146.9843
225.9104 | 328.4746 | 140.1094 | 147.3927
226.9104 | 328.4206 | 140.4647 | 147.7859
227.9104 | 328.3822 | 140.8549 | 148.1966
228.9104 | 328.4652 | 141.2256 | 148.597
229.9104 | 328.5294 | 141.589 | 148.9981
230.9104 | 328.473 | 141.9204 | 149.4029
231.9104 | 328.4724 | 142.2895 | 149.8181
232.9104 | 328.6371 | 142.6302 | 150.2351
233.9104 | 328.7238 | 142.9778 | 150.6379
234.9104 | 328.6761 | 143.3387 | 151.0259
235.9104 | 328.7599 | 143.6763 | 151.4149
236.9104 | 328.7105 | 144.0245 | 151.7947
237.9104 | 328.7517 | 144.3489 | 152.1752
238.9104 | 328.7601 | 144.6954 | 152.5571
239.9104 | 328.749 | 145.043 | 152.9409
240.9104 | 328.7287 | 145.3774 | 153.3213
241.9104 | 328.6783 | 145.7267 | 153.7051
242.9104 | 328.6804 | 146.0726 | 154.0936
243.9104 | 328.6881 | 146.3978 | 154.4805
244.9104 | 328.7481 | 146.7428 | 154.8789
245.9104 | 328.8086 | 147.0761 | 155.2713
246.9104 | 328.9031 | 147.3968 | 155.6564
247.9104 | 328.9579 | 147.7275 | 156.0303
248.9104 | 328.9388 | 148.0474 | 156.4049
249.9104 | 328.8538 | 148.3678 | 156.7779
250.926 | 328.8847 | 148.6791 | 157.1593
251.9104 | 328.9205 | 149.0153 | 157.5328
252.9104 | 328.9157 | 149.3423 | 157.9094
253.9104 | 328.7798 | 149.6599 | 158.2594
254.9104 | 328.77 | 149.978 | 158.6117
255.9104 | 328.6343 | 150.2867 | 158.9783
256.9104 | 328.492 | 150.598 | 159.3491
257.9104 | 328.4909 | 150.9099 | 159.7252
258.9104 | 328.4612 | 151.2029 | 160.0986
259.9104 | 328.3204 | 151.5218 | 160.4658
260.9104 | 328.241 | 151.834 | 160.8318
261.9104 | 328.1481 | 152.1384 | 161.2076
262.9104 | 328.0718 | 152.4445 | 161.5825
263.9104 | 327.9216 | 152.745 | 161.9355
264.9104 | 327.8232 | 153.0427 | 162.3073
265.9104 | 327.774 | 153.3367 | 162.6669
266.9104 | 327.7775 | 153.6314 | 163.0296
267.9104 | 327.7683 | 153.9105 | 163.4001
268.9104 | 327.7513 | 154.2089 | 163.7758
269.9104 | 327.7707 | 154.5061 | 164.1622
270.9104 | 327.7399 | 154.81 | 164.5266
271.9104 | 327.6076 | 155.1189 | 164.9045
272.9104 | 327.6077 | 155.4317 | 165.2714
273.9104 | 327.6535 | 155.7275 | 165.6442
274.9104 | 327.6137 | 156.0396 | 166.0086
275.9104 | 327.5915 | 156.3501 | 166.3776
276.9104 | 327.5903 | 156.6744 | 166.7398
277.9104 | 327.5929 | 156.9788 | 167.1028
278.9104 | 327.5862 | 157.3064 | 167.489
279.9104 | 327.5596 | 157.6357 | 167.8529
280.926 | 327.6335 | 157.9435 | 168.2065
281.9104 | 327.6626 | 158.2837 | 168.5577
282.9104 | 327.5053 | 158.5956 | 168.9198
283.9104 | 327.2894 | 158.9165 | 169.265
284.9104 | 327.2173 | 159.248 | 169.6121
285.9104 | 327.2445 | 159.5768 | 169.9626
286.9104 | 327.327 | 159.9037 | 170.3163
287.9104 | 327.3608 | 160.2276 | 170.6718
288.9104 | 327.3838 | 160.5617 | 171.0109
289.9104 | 327.3759 | 160.8708 | 171.3494
290.9104 | 327.5014 | 161.2062 | 171.6811
291.9104 | 327.5914 | 161.5303 | 172.0129
292.9104 | 327.654 | 161.8629 | 172.3537
293.9104 | 327.6741 | 162.2003 | 172.6958
294.9104 | 327.7139 | 162.5073 | 173.0536
295.9104 | 327.8287 | 162.8343 | 173.4006
296.9104 | 327.9164 | 163.1672 | 173.7462
297.9104 | 327.9395 | 163.4874 | 174.1036
298.9104 | 327.9789 | 163.8292 | 174.4595
299.9104 | 327.9704 | 164.1457 | 174.8195
300.9104 | 328.02 | 164.4637 | 175.1759
301.9104 | 328.0118 | 164.8005 | 175.5398
302.9104 | 328.0348 | 165.125 | 175.9045
303.9104 | 328.0243 | 165.4593 | 176.2665
304.9104 | 327.9749 | 165.7661 | 176.6204
305.9104 | 327.9059 | 166.087 | 176.9871
306.9104 | 327.8812 | 166.3811 | 177.3602
307.9104 | 327.8615 | 166.6637 | 177.7133
308.9104 | 327.8799 | 166.977 | 178.0771
309.9104 | 327.9609 | 167.2672 | 178.4475
310.926 | 327.9998 | 167.5698 | 178.8236
311.9104 | 328.019 | 167.8891 | 179.1722
312.9104 | 328.0854 | 168.1953 | 179.5069
313.9104 | 328.1677 | 168.5114 | 179.8753
314.9104 | 328.114 | 168.8225 | 180.2439
315.9104 | 327.9874 | 169.1271 | 180.6039
316.9104 | 327.8527 | 169.4377 | 180.9696
317.9104 | 327.7998 | 169.7547 | 181.3356
318.9104 | 327.8785 | 170.071 | 181.6684
319.9104 | 327.9639 | 170.3772 | 182.0053
320.9104 | 327.9538 | 170.7034 | 182.3132
321.9104 | 327.9234 | 171.0093 | 182.6285
322.9104 | 327.8652 | 171.3143 | 182.9303
323.9104 | 327.8448 | 171.6168 | 183.2324
324.9104 | 327.8547 | 171.9319 | 183.5341
325.9104 | 327.8189 | 172.2283 | 183.8342
326.9104 | 327.7811 | 172.5336 | 184.1413
327.9104 | 327.749 | 172.827 | 184.4518
328.9104 | 327.7381 | 173.1099 | 184.766
329.9104 | 327.7257 | 173.4271 | 185.0832
330.9104 | 327.7722 | 173.7205 | 185.4188
331.9104 | 327.7515 | 174.0373 | 185.7356
332.9104 | 327.7328 | 174.3515 | 186.0615
333.9104 | 327.7507 | 174.69 | 186.3798
334.9104 | 327.7252 | 175.012 | 186.6949
335.9104 | 327.7626 | 175.3295 | 187.0198
336.9104 | 327.7441 | 175.6568 | 187.318
337.9104 | 327.7219 | 175.9791 | 187.6257
338.9104 | 327.702 | 176.3041 | 187.916
339.9104 | 327.5934 | 176.6169 | 188.2195
340.926 | 327.5952 | 176.9299 | 188.5112
341.9104 | 327.498 | 177.263 | 188.803
342.9104 | 327.5235 | 177.5695 | 189.0921
343.9104 | 327.5143 | 177.8993 | 189.3854
344.9104 | 327.4469 | 178.1991 | 189.6714
345.9104 | 327.4363 | 178.5223 | 189.9749
346.9104 | 327.3367 | 178.8485 | 190.2694
347.9104 | 327.3372 | 179.164 | 190.5748
348.9104 | 327.2378 | 179.472 | 190.8704
349.9104 | 327.1772 | 179.8054 | 191.1633
350.9104 | 327.2588 | 180.1175 | 191.4561
351.9104 | 327.3684 | 180.4152 | 191.746
352.9104 | 327.46 | 180.7249 | 192.0204
353.9104 | 327.4983 | 181.0296 | 192.2997
354.9104 | 327.483 | 181.3396 | 192.5561
355.9104 | 327.4386 | 181.6259 | 192.8292
356.9104 | 327.4532 | 181.9437 | 193.0948
357.9104 | 327.4371 | 182.2653 | 193.3607
358.9104 | 327.3805 | 182.5692 | 193.6166
359.9104 | 327.3566 | 182.8728 | 193.8767
360.9104 | 327.3171 | 183.1865 | 194.1333
361.9104 | 327.2932 | 183.4734 | 194.381
362.9104 | 327.2525 | 183.8109 | 194.6471
363.9104 | 327.2232 | 184.1072 | 194.8891
364.9104 | 327.2228 | 184.4041 | 195.1396
365.9104 | 327.2343 | 184.7136 | 195.3666
366.9104 | 327.1709 | 185.0013 | 195.5831
367.9104 | 327.2094 | 185.2902 | 195.8092
368.9104 | 327.2609 | 185.5669 | 196.0147
369.9104 | 327.2123 | 185.8497 | 196.2112
370.926 | 327.1265 | 186.1433 | 196.4149
371.9104 | 327.0524 | 186.4241 | 196.6347
372.9104 | 327.0073 | 186.705 | 196.8724
373.9104 | 327.0473 | 187.0093 | 197.0997
374.9104 | 327.1358 | 187.2819 | 197.3428
375.9104 | 327.2001 | 187.5687 | 197.5769
376.9104 | 327.1799 | 187.8485 | 197.7979
377.9104 | 327.2144 | 188.124 | 198.0166
378.9104 | 327.2601 | 188.4105 | 198.2381
379.9104 | 327.283 | 188.6878 | 198.4722
380.9104 | 327.3009 | 188.9632 | 198.7028
381.9104 | 327.3172 | 189.2487 | 198.9237
382.9104 | 327.4129 | 189.5196 | 199.1345
383.9104 | 327.4495 | 189.8002 | 199.333
384.9104 | 327.4774 | 190.0817 | 199.5495
385.9104 | 327.455 | 190.3783 | 199.7626
386.9104 | 327.5031 | 190.6724 | 199.9761
387.9104 | 327.5743 | 190.9616 | 200.1776
388.9104 | 327.557 | 191.2655 | 200.3879
389.9104 | 327.4981 | 191.5572 | 200.589
390.9104 | 327.5279 | 191.833 | 200.799
391.9104 | 327.5649 | 192.1125 | 200.995
392.9104 | 327.6138 | 192.3818 | 201.2119
393.9104 | 327.6879 | 192.6439 | 201.4335
394.9104 | 327.7191 | 192.8767 | 201.6645
395.9104 | 327.7529 | 193.1381 | 201.9028
396.9104 | 327.7425 | 193.3768 | 202.1313
397.9104 | 327.7377 | 193.636 | 202.3341
398.9104 | 327.7362 | 193.8822 | 202.5461
399.9104 | 327.7335 | 194.1237 | 202.7687
400.926 | 327.801 | 194.3778 | 202.9962
401.9104 | 327.8645 | 194.6321 | 203.215
402.9104 | 327.8119 | 194.8879 | 203.3826
403.9104 | 327.7773 | 195.15 | 203.5279
404.9104 | 327.9082 | 195.4014 | 203.7004
405.9104 | 327.9322 | 195.6585 | 203.8902
406.9104 | 327.8825 | 195.9022 | 204.0896
407.9104 | 327.7573 | 196.1664 | 204.2834
408.9104 | 327.6837 | 196.4313 | 204.4832
409.9104 | 327.5925 | 196.6788 | 204.6839
410.9104 | 327.5071 | 196.9321 | 204.8936
411.9104 | 327.4412 | 197.17 | 205.1021
412.9104 | 327.4027 | 197.4146 | 205.3062
413.9104 | 327.2295 | 197.6643 | 205.5082
414.9104 | 327.0735 | 197.9022 | 205.7096
415.9104 | 327.0715 | 198.2283 | 205.869
416.9104 | 327.0457 | 198.7211 | 206.0449
417.9104 | 327.0176 | 199.063 | 206.2334
418.9104 | 326.9559 | 199.347 | 206.412
419.9104 | 326.9303 | 199.6207 | 206.5711
420.9104 | 326.8671 | 199.8779 | 206.7401
421.9104 | 326.8397 | 200.1137 | 206.9114
422.9104 | 326.8914 | 200.3408 | 207.0906
423.9104 | 326.8563 | 200.5496 | 207.2686
424.9104 | 326.8083 | 200.7723 | 207.4392
425.9104 | 326.6527 | 200.9772 | 207.6045
426.9104 | 326.4774 | 201.1886 | 207.7619
427.9104 | 326.4381 | 201.4017 | 207.9343
428.9104 | 326.4431 | 201.6043 | 208.1247
429.9104 | 326.4523 | 201.8161 | 208.2915
430.926 | 326.4521 | 202.0119 | 208.4825
431.9104 | 326.4234 | 202.2066 | 208.6894
432.9104 | 326.3731 | 202.3878 | 208.883
433.9104 | 326.3279 | 202.5779 | 209.0868
434.9104 | 326.4122 | 202.7609 | 209.257
435.9104 | 326.4858 | 202.9576 | 209.4054
436.9104 | 326.4779 | 203.159 | 209.539
437.9104 | 326.4825 | 203.3558 | 209.692
438.9104 | 326.5844 | 203.5661 | 209.8572
439.9104 | 326.5697 | 203.775 | 210.0314
440.9104 | 326.4178 | 203.9847 | 210.1909
441.9104 | 326.1726 | 204.1683 | 210.3583
442.9104 | 326.1888 | 204.3567 | 210.5043
443.9104 | 326.2993 | 204.5327 | 210.6622
444.9104 | 326.4211 | 204.711 | 210.8042
445.9104 | 326.4306 | 204.8797 | 210.946
446.9104 | 326.347 | 205.0786 | 211.088
447.9104 | 326.3301 | 205.2723 | 211.2308
448.9104 | 326.3527 | 205.4447 | 211.3506
449.9104 | 326.47 | 205.6217 | 211.471
450.9104 | 326.5561 | 205.8024 | 211.5849
451.9104 | 326.582 | 205.9885 | 211.6944
452.9104 | 326.5781 | 206.1647 | 211.8286
453.9104 | 326.683 | 206.3381 | 211.9705
454.9104 | 326.7177 | 206.5334 | 212.1
455.9104 | 326.6548 | 206.7033 | 212.2294
456.9104 | 326.6715 | 206.8835 | 212.3333
457.9104 | 326.7469 | 207.0611 | 212.441
458.9104 | 326.8837 | 207.2419 | 212.5497
459.9104 | 326.987 | 207.4343 | 212.6601
460.926 | 326.9373 | 207.6603 | 212.7151
461.9104 | 326.7782 | 207.8822 | 212.7983
462.9104 | 326.7621 | 208.0946 | 212.9058
463.9104 | 326.893 | 208.3131 | 213.0223
464.9104 | 326.9032 | 208.5058 | 213.1368
465.9104 | 326.8776 | 208.6886 | 213.2364
466.9104 | 326.8573 | 208.8724 | 213.3342
467.9104 | 326.8369 | 209.0578 | 213.4291
468.9104 | 326.8421 | 209.2406 | 213.5513
469.9104 | 326.8047 | 209.4116 | 213.6565
470.9104 | 326.7596 | 209.5915 | 213.7573
471.9104 | 326.7249 | 209.7558 | 213.8799
472.9104 | 326.7135 | 209.9452 | 213.9787
473.9104 | 326.6955 | 210.1329 | 214.0744
474.9104 | 326.6777 | 210.2986 | 214.1849
475.9104 | 326.6555 | 210.5002 | 214.2966
476.9104 | 326.6523 | 210.6855 | 214.409
477.9104 | 326.5764 | 210.8544 | 214.5117
478.9104 | 326.5482 | 211.1272 | 214.59
479.9104 | 326.498 | 211.4021 | 214.6664
480.9104 | 326.473 | 211.6132 | 214.7682
481.9104 | 326.3738 | 211.8016 | 214.8484
482.9104 | 326.2596 | 211.9583 | 214.9318
483.9104 | 326.2446 | 212.1245 | 215.014
484.9104 | 326.2161 | 212.2774 | 215.1216
485.9104 | 326.1909 | 212.4393 | 215.2252
486.9104 | 326.1924 | 212.6151 | 215.346
487.9104 | 326.2662 | 212.7852 | 215.4677
488.9104 | 326.2315 | 212.947 | 215.5624
489.9104 | 326.2633 | 213.1415 | 215.6285
490.926 | 326.3225 | 213.3297 | 215.7027
491.9104 | 326.3873 | 213.4874 | 215.7778
492.9104 | 326.5086 | 213.6501 | 215.8832
493.9104 | 326.5564 | 213.7935 | 215.9997
494.9104 | 326.5624 | 213.9492 | 216.1217
495.9104 | 326.5686 | 214.1062 | 216.2536
496.9104 | 326.5889 | 214.2576 | 216.3818
497.9104 | 326.6166 | 214.4249 | 216.4956
498.9104 | 326.604 | 214.5821 | 216.6109
499.9104 | 326.638 | 214.7275 | 216.7222
500.9104 | 326.5162 | 214.8482 | 216.8279
501.9104 | 326.5042 | 214.9867 | 216.9495
502.9104 | 326.5112 | 215.0808 | 217.0649
503.9104 | 326.571 | 215.214 | 217.194
504.9104 | 326.5248 | 215.3084 | 217.3137
505.9104 | 326.5884 | 215.421 | 217.4213
506.9104 | 326.5363 | 215.5289 | 217.519
507.9104 | 326.5061 | 215.6286 | 217.615
508.9104 | 326.5444 | 215.7492 | 217.7147
509.9104 | 326.5653 | 215.8733 | 217.7765
510.9104 | 326.5596 | 216.0008 | 217.8557
511.9104 | 326.4702 | 216.1139 | 217.9236
512.9104 | 326.3702 | 216.212 | 218.0068
513.9104 | 326.3065 | 216.3206 | 218.0927
514.9104 | 326.2077 | 216.4671 | 218.2038
515.9104 | 326.2333 | 216.5788 | 218.3164
516.9104 | 326.249 | 216.7274 | 218.4238
517.9104 | 326.2306 | 216.8221 | 218.5321
518.9104 | 326.2779 | 216.9646 | 218.641
519.9104 | 326.2984 | 217.1089 | 218.7499
520.9104 | 326.3382 | 217.2013 | 218.8582
521.9104 | 326.3922 | 217.2516 | 218.9602
522.9104 | 326.4437 | 217.3083 | 219.0675
523.9104 | 326.4797 | 217.3651 | 219.1448
524.9104 | 326.4102 | 217.4491 | 219.2388
525.9104 | 326.4515 | 217.5453 | 219.2986
526.9104 | 326.454 | 217.6638 | 219.3758
527.9104 | 326.3309 | 217.7657 | 219.4448
528.9104 | 326.2424 | 217.8992 | 219.5216
529.9104 | 326.1917 | 218.0295 | 219.6022
530.9104 | 326.2014 | 218.147 | 219.6902
531.9104 | 326.1935 | 218.2652 | 219.7586
532.9104 | 326.2048 | 218.3782 | 219.8347
533.9104 | 326.1253 | 218.513 | 219.8935
534.9104 | 326.1553 | 218.6621 | 219.9786
535.9104 | 326.1572 | 218.805 | 220.0592
536.9104 | 326.2162 | 218.9412 | 220.1531
537.9104 | 326.2515 | 219.0586 | 220.2491
538.9104 | 326.3071 | 219.1959 | 220.3543
539.9104 | 326.2883 | 219.3403 | 220.457
540.9104 | 326.2963 | 219.486 | 220.5557
541.9104 | 326.2674 | 219.6336 | 220.6621
542.9104 | 326.3614 | 219.7887 | 220.7742
543.9104 | 326.4499 | 219.931 | 220.8807
544.9104 | 326.4247 | 220.0903 | 220.9948
545.9104 | 326.3423 | 220.2508 | 221.1169
546.9104 | 326.3354 | 220.4043 | 221.2353
547.9104 | 326.3719 | 220.5125 | 221.3639
548.9104 | 326.4795 | 220.6602 | 221.47
549.9104 | 326.5167 | 220.7909 | 221.5604
550.9104 | 326.6534 | 220.9189 | 221.6148
551.9104 | 326.7397 | 221.0133 | 221.6968
552.9104 | 326.6656 | 221.0975 | 221.7666
553.9104 | 326.5881 | 221.1427 | 221.8395
554.9104 | 326.6463 | 221.2476 | 221.8944
555.9104 | 326.6738 | 221.3271 | 221.9502
556.9104 | 326.6856 | 221.3933 | 221.995
557.9104 | 326.6666 | 221.5044 | 222.0267
558.9104 | 326.7029 | 221.6028 | 222.088
559.9104 | 326.7118 | 221.6857 | 222.1481
560.9104 | 326.7128 | 221.7684 | 222.224
561.9104 | 326.7612 | 221.8917 | 222.2899
562.9104 | 326.8217 | 222.0374 | 222.3473
563.9104 | 326.8051 | 222.1833 | 222.4226
564.9104 | 326.6865 | 222.35 | 222.4992
565.9104 | 326.6654 | 222.4909 | 222.5774
566.9104 | 326.7002 | 222.6596 | 222.6566
567.9104 | 326.6094 | 222.778 | 222.7387
568.9104 | 326.3508 | 222.8901 | 222.8036
569.9104 | 326.2663 | 223.0204 | 222.8699
570.9104 | 326.1932 | 223.1363 | 222.9305
571.9104 | 326.2037 | 223.2125 | 222.9926
572.9104 | 326.1794 | 223.3185 | 223.0573
573.9104 | 326.2196 | 223.4269 | 223.1098
574.9104 | 326.2887 | 223.4718 | 223.1454
575.9104 | 326.3103 | 223.5587 | 223.1698
576.9104 | 326.2698 | 223.6699 | 223.2
577.9104 | 326.252 | 223.8021 | 223.2096
578.9104 | 326.241 | 223.9302 | 223.2109
579.9104 | 326.2388 | 224.0716 | 223.1995
580.9104 | 326.2165 | 224.2079 | 223.1883
581.9104 | 326.1555 | 224.3192 | 223.1643
582.9104 | 326.101 | 224.3946 | 223.1447
583.9104 | 326.1288 | 224.4817 | 223.1136
584.9104 | 326.1487 | 224.571 | 223.0751
585.9104 | 326.262 | 224.7053 | 222.9918
586.9104 | 326.3727 | 224.9299 | 222.438
587.9104 | 326.4312 | 225.0605 | 222.3766
588.9104 | 326.3794 | 225.1741 | 222.37
589.9104 | 326.2489 | 225.2809 | 222.3949
590.9104 | 326.1846 | 225.4098 | 222.4234
591.9104 | 326.1922 | 225.532 | 222.4798
592.9104 | 326.1057 | 225.6617 | 222.5516
593.9104 | 325.9727 | 225.7761 | 222.6308
594.9104 | 326.0001 | 225.8895 | 222.7024
595.9104 | 326.0531 | 226.0176 | 222.7856
596.9104 | 326.1235 | 226.1309 | 222.8764
597.9104 | 326.2066 | 226.2137 | 222.9819
598.9104 | 326.2087 | 226.3192 | 223.1048
599.9104 | 326.1483 | 226.4274 | 223.2127
600.9104 | 326.0981 | 226.5465 | 223.3288
601.9104 | 326.2314 | 226.6571 | 223.4457
602.9104 | 326.3509 | 226.7436 | 223.5625
603.9104 | 326.426 | 226.7958 | 223.6848
604.9104 | 326.4422 | 226.8842 | 223.8146
605.9104 | 326.4248 | 226.9779 | 223.9385
606.9104 | 326.3327 | 227.086 | 224.0721
607.9104 | 326.2716 | 227.2054 | 224.2002
608.9104 | 326.4 | 227.3074 | 224.331
609.9104 | 326.4319 | 227.4034 | 224.4555
610.9104 | 326.4778 | 227.4978 | 224.5787
611.9104 | 326.5642 | 227.6017 | 224.7027
612.9104 | 326.5417 | 227.6869 | 224.8251
613.9104 | 326.531 | 227.775 | 224.946
614.9104 | 326.4669 | 227.8542 | 225.073
615.9104 | 326.3848 | 227.9227 | 225.1993
616.9104 | 326.3572 | 228.0011 | 225.3194
617.9104 | 326.3545 | 228.1026 | 225.451
618.9104 | 326.3417 | 228.1858 | 225.5728
619.9104 | 326.3093 | 228.2964 | 225.6999
620.9104 | 326.253 | 228.3736 | 225.8279
621.9104 | 326.155 | 228.4626 | 225.9613
622.9104 | 326.0318 | 228.5748 | 226.102
623.9104 | 325.9205 | 228.6593 | 226.2352
624.9104 | 325.8814 | 228.7732 | 226.3619
625.9104 | 325.9433 | 228.8467 | 226.4906
626.9104 | 325.9822 | 228.9134 | 226.6081
627.9104 | 326.0259 | 228.9913 | 226.7347
628.9104 | 326.0299 | 229.0813 | 226.8716
629.9104 | 326.033 | 229.1719 | 227.0144
630.9104 | 326.047 | 229.2529 | 227.1593
631.9104 | 326.0705 | 229.336 | 227.296
632.9104 | 325.9975 | 229.4259 | 227.4346
633.9104 | 325.9926 | 229.5251 | 227.5712
634.9104 | 326.014 | 229.6235 | 227.7115
635.9104 | 326.0384 | 229.6892 | 227.838
636.9104 | 326.0345 | 229.7682 | 227.9624
637.9104 | 326.1598 | 229.8511 | 228.0908
638.9104 | 326.148 | 229.9219 | 228.2144
639.9104 | 326.1022 | 229.9777 | 228.3448
640.9104 | 326.1669 | 230.0659 | 228.4643
641.9104 | 326.2382 | 230.1677 | 228.4742
642.9104 | 326.26 | 230.2462 | 228.4207
643.9104 | 326.312 | 230.3245 | 228.557
644.9104 | 326.3672 | 230.4128 | 228.6641
645.9104 | 326.4443 | 230.4993 | 228.7824
646.9104 | 326.4521 | 230.5836 | 228.9036
647.9104 | 326.3274 | 230.6384 | 229.015
648.9104 | 326.3035 | 230.7555 | 229.1397
649.9104 | 326.3254 | 230.8479 | 229.238
650.9104 | 326.4403 | 230.9384 | 229.355
651.9104 | 326.4753 | 231.0468 | 229.477
652.9104 | 326.4771 | 231.1467 | 229.5979
653.9104 | 326.4253 | 231.2435 | 229.7206
654.9104 | 326.4394 | 231.349 | 229.8346
655.9104 | 326.4911 | 231.4679 | 229.9562
656.9104 | 326.566 | 231.573 | 230.0796
657.9104 | 326.585 | 231.6804 | 230.2001
658.9104 | 326.5594 | 231.778 | 230.3285
659.9104 | 326.5067 | 231.8771 | 230.4488
660.9104 | 326.4384 | 231.961 | 230.5748
661.9104 | 326.3608 | 232.0666 | 230.6956
662.9104 | 326.1711 | 232.1726 | 230.8189
663.9104 | 326.0894 | 232.2709 | 230.9421
664.9104 | 326.0721 | 232.3775 | 231.0627
665.9104 | 326.1085 | 232.4671 | 231.1788
666.9104 | 326.159 | 232.558 | 231.3019
667.9104 | 326.0955 | 232.635 | 231.4269
668.9104 | 326.0237 | 232.7169 | 231.5366
669.9104 | 326.0567 | 232.8245 | 231.6511
670.9104 | 326.0141 | 232.9049 | 231.7594
671.9104 | 325.9608 | 233.0162 | 231.8705
672.9104 | 325.9549 | 233.1201 | 231.9764
673.9104 | 325.9873 | 233.2398 | 232.0987
674.9104 | 325.9272 | 233.3383 | 232.2322
675.9104 | 325.8378 | 233.4537 | 232.348
676.9104 | 325.831 | 233.5733 | 232.4676
677.9104 | 325.8055 | 233.6884 | 232.5774
678.9104 | 325.8354 | 233.7942 | 232.6898
679.9104 | 325.8793 | 233.903 | 232.7878
680.9104 | 325.9791 | 233.9914 | 232.8959
681.9104 | 325.9547 | 234.1291 | 232.9819
682.9104 | 325.9566 | 234.2251 | 233.086
683.9104 | 325.9709 | 234.3316 | 233.1843
684.9104 | 325.9554 | 234.4356 | 233.2817
685.9104 | 325.956 | 234.5572 | 233.384
686.9104 | 325.9263 | 234.6622 | 233.4841
687.9104 | 325.9059 | 234.7609 | 233.5876
688.9104 | 325.9015 | 234.8536 | 233.7049
689.9104 | 325.9329 | 234.9518 | 233.8142
690.9104 | 325.8597 | 235.0377 | 233.9288
691.9104 | 325.9087 | 235.1341 | 234.0394
692.9104 | 325.9439 | 235.2166 | 234.1385
693.9104 | 325.9323 | 235.3162 | 234.2322
694.9104 | 325.7924 | 235.3944 | 234.3333
695.9104 | 325.8174 | 235.4972 | 234.4279
696.9104 | 325.7887 | 235.5879 | 234.5163
697.9104 | 325.8056 | 235.6768 | 234.6124
698.9104 | 325.8572 | 235.7828 | 234.7123
699.9104 | 325.8072 | 235.8854 | 234.8059
700.9104 | 325.7653 | 235.9657 | 234.895
701.9104 | 325.7779 | 236.067 | 234.9805
702.9104 | 325.7513 | 236.1711 | 235.0682
703.9104 | 325.6668 | 236.2705 | 235.1561
704.9104 | 325.7342 | 236.3722 | 235.2567
705.9104 | 325.8169 | 236.4718 | 235.3409