## Test Conditions
DESIREE-FIRE Test Number 36 - Circuit Data Data Only
Test Date: | 2009-08-12
DCSim DAQ Start Time | 7:05
DCSim Time for Synchronization | 8:06
Heat Source Synchronization | 0:29 | hours:minutes:seconds
Heat Source DAQ Start Time | 7:37
Fire Time | 8:07
Offset | 1:02 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 3720 | seconds
Heat Source Offset | 0:31 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 1840 | seconds
Heat Source Stop Time | 9:01
Test Duration | 0:54 | hours:minutes:seconds
| 3230 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
1" Solenoid Valve | XLPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the top and bottom of the conduit, respectively. Channel 5 represents the cable temperature within the conduit. | Channel 4 which represents TC25 in the Temperature Data File
Large Coil | XLPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the top and bottom of the conduit, respectively. Channel 5 represents the cable temperature within the conduit. | Channel 4 which represents TC25 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | 1"Coil_CT500 | 1"Coil_CT35_1_P | 1"Coil_CT35_2_G | 1"Coil_CT35_3_R | 1"Coil_CT35_4_N2 | 1"Coil_CT35_5_S | 1"Coil_CT35_6_N1 | LgCoil_CT500 | LgCoil_CT35_1_P | LgCoil_CT35_2_G | LgCoil_CT35_3_N2 | LgCoil_CT35_4_S | LgCoil_CT35_5_N1 | 1"Coil_VT7_1_G | 1"Coil_VT7_2_R | 1"Coil_VT7_3_SP | 1"Coil_VT7_4_S | 1"Coil_VTU_1_P | 1"Coil_VTU_2_N2 | 1"Coil_VTU_3_N1 | LgCoil_VT7_1_R | LgCoil_VT7_2_SP | LgCoil_VT7_3_S | LgCoil_VTU_1_P | LgCoil_VTU_2_G | LgCoil_VTU_3_N2 | LgCoil_VTU_4_N1 | {1"Valve} V(N2) - V(Batt -) | {1"Valve} V(N1) - V(Batt -) | {1"Valve} V(P) - V(Batt +) | {1"Valve} V(R) - V(Batt -) | {1"Valve} V(S) - V(Batt -) | {1"Valve} V(S) - V(N1) | {1"Valve} V(G) - V(Batt +) | {LgCoil} V(N2) - V(Batt -) | {LgCoil} V(N1) - V(Batt -) | {LgCoil} V(P) - V(Batt +) | {LgCoil} V(R) - V(Batt -) | {LgCoil} V(S) - V(Batt -) | {LgCoil} V(S) - V(N1) | {LgCoil} V(G) - V(Batt +) | {1"Valve} V(P) - V(Batt -) | {1"Valve} V(G) - V(Batt -) | {1"Valve} V(SP) - V(Batt -) | {1"Valve} V(N1) - V(Batt +) | {LgCoil} V(P) - V(Batt -) | {LgCoil} V(G) - V(Batt -) | {LgCoil} V(SP) - V(Batt -) | {LgCoil} V(N1) - V(Batt +)
-0.48438 | 123.1567 | -59.1064 | 63.8947 | -0.1709 | 0.0083997 | 0.065877 | 0.068364 | 0.13169 | 0.0019078 | 0.00063028 | -0.080643 | 0.00036743 | -0.0010318 | 0.000532 | 0.00091437 | -0.0030335 | 63.8535 | 63.9633 | -0.013733 | -59.2712 | 63.8077 | -59.1019 | -59.111 | -59.0607 | 0.082397 | -59.3536 | 63.8992 | 63.7894 | -59.1019 | -59.23 | 0.004577 | -0.004578 | -0.086975 | 123.0698 | -0.16479 | -0.16022 | -0.041198 | 0.004577 | -0.1236 | 0.004578 | 0.045776 | -0.24719 | -0.1236 | -0.10528 | 122.9141 | 122.9599 | 59.0927 | -123.0057 | 123.0057 | 122.8958 | 59.1888 | -123.1247
0.51562 | 123.1201 | -59.0973 | 63.9359 | 0.49286 | 0.0058361 | 0.068013 | 0.068364 | 0.13169 | -0.001083 | -0.0023605 | -0.088272 | 0.00015383 | 0.0004636 | -0.0005362 | -0.0010082 | -0.0011109 | 63.8489 | 63.9359 | -0.032043 | -59.2941 | 63.8443 | -59.1202 | -59.1248 | -59.0881 | 0.054932 | -59.3857 | 63.8947 | 63.8214 | -59.0927 | -59.2209 | -0.022888 | -0.027466 | -0.091553 | 123.0331 | -0.19684 | -0.16937 | -0.086975 | 0.004578 | -0.1236 | -0.041199 | 0.009155 | -0.28839 | -0.16479 | -0.11444 | 122.9416 | 122.9462 | 59.0652 | -123.0606 | 122.9919 | 122.9187 | 59.1522 | -123.1567
1.5156 | 123.1842 | -59.1019 | 63.8992 | -0.094604 | 0.0088269 | 0.065663 | 0.069432 | 0.13255 | 0.00083955 | 0.00084388 | 0.0032804 | 0.0012218 | 0.0004636 | 0.0003182 | 0.0024096 | -0.00089726 | 63.858 | 64.0594 | 0.022888 | -59.2896 | 63.8214 | -59.1248 | -59.1248 | -59.0378 | 0.068665 | -59.3674 | 63.8763 | 63.8123 | -59.0607 | -59.2529 | -0.022888 | -0.022888 | -0.07782 | 123.1613 | -0.18768 | -0.1648 | -0.041199 | 0.041199 | -0.15106 | -0.022888 | 0.064087 | -0.2655 | -0.11444 | -0.086975 | 122.9233 | 122.9599 | 59.1248 | -123.024 | 122.9782 | 122.9141 | 59.1705 | -123.1522
2.5156 | 123.1567 | -59.0881 | 63.9221 | -0.20142 | 0.0075451 | 0.065022 | 0.067936 | 0.13169 | -0.0023648 | -0.00086512 | -0.065384 | -0.00070077 | 0.0021726 | 0.0009592 | -0.0010082 | -4.2662e-05 | 63.8306 | 63.9496 | -0.022888 | -59.2941 | 63.8351 | -59.1156 | -59.1202 | -59.0881 | 0.050354 | -59.3948 | 63.8855 | 63.8397 | -59.0927 | -59.2163 | -0.027466 | -0.032043 | -0.086975 | 123.0377 | -0.20599 | -0.17395 | -0.091553 | -0.004577 | -0.12817 | -0.036621 | 0 | -0.3067 | -0.17853 | -0.082397 | 122.9233 | 122.9187 | 59.0652 | -123.0423 | 122.9736 | 122.9279 | 59.1385 | -123.1384
3.5156 | 123.2071 | -59.1156 | 63.8901 | -0.18616 | 0.0092541 | 0.064595 | 0.067723 | 0.1334 | 0.0019078 | -0.00022432 | -0.027237 | 0.00058103 | 0.0006772 | 0.0007456 | -0.00015383 | -0.0023927 | 63.8809 | 63.9816 | 0.004578 | -59.2575 | 63.8077 | -59.111 | -59.1156 | -59.0378 | 0.07782 | -59.3628 | 63.8397 | 63.7985 | -59.0652 | -59.2529 | 0.004578 | 0 | -0.082398 | 123.0972 | -0.14191 | -0.14191 | -0.009156 | 0.050354 | -0.13733 | -0.050354 | 0.07782 | -0.24719 | -0.10986 | -0.091553 | 122.9233 | 122.9965 | 59.1202 | -123.0057 | 122.9553 | 122.9141 | 59.1934 | -123.143
4.5156 | 123.1476 | -59.0927 | 63.9313 | -1.0406 | 0.0030591 | 0.065022 | 0.067723 | 0.1334 | -0.0032192 | -0.0019333 | -0.011978 | -0.0013416 | -0.001459 | 0.0016 | -0.00015383 | -0.0011109 | 63.8672 | 63.9954 | 0.027466 | -59.2484 | 63.8077 | -59.0927 | -59.1293 | -59.079 | 0.082397 | -59.3811 | 63.8626 | 63.8397 | -59.0836 | -59.2392 | 0 | -0.036621 | -0.1236 | 123.0881 | -0.15564 | -0.11902 | -0.064087 | 0.009155 | -0.14648 | -0.068664 | 0.013733 | -0.28839 | -0.14191 | -0.091552 | 122.9004 | 122.9599 | 59.1202 | -123.0606 | 122.9553 | 122.9324 | 59.1751 | -123.1705
5.5156 | 123.1705 | -59.0836 | 63.8763 | -0.19379 | 0.0073315 | 0.064382 | 0.067936 | 0.13084 | 0.0036166 | -1.0724e-05 | -0.027237 | -0.001128 | 0.0011044 | 0.0001046 | 0.00027337 | -0.0015381 | 63.8718 | 63.9816 | 0.018311 | -59.2667 | 63.8123 | -59.0973 | -59.1156 | -59.0469 | 0.068665 | -59.3628 | 63.858 | 63.8168 | -59.1156 | -59.2438 | -0.013733 | -0.032044 | -0.064087 | 123.0652 | -0.18311 | -0.15106 | -0.004578 | -0.032044 | -0.16022 | -0.018311 | 0.036621 | -0.27924 | -0.11902 | -0.05951 | 122.8958 | 122.9553 | 59.1019 | -122.9919 | 122.9416 | 122.9004 | 59.1522 | -123.1201
6.5156 | 123.175 | -59.0973 | 63.913 | -0.11749 | 0.0079723 | 0.066304 | 0.069645 | 0.13191 | -0.0012966 | -0.0019333 | -0.073013 | -0.001128 | -0.001459 | 0.0009592 | 0.0013416 | -0.0019653 | 63.858 | 63.9267 | -0.032043 | -59.2804 | 63.8214 | -59.1019 | -59.0973 | -59.0561 | -0.091553 | -59.404 | 63.8535 | 63.8168 | -59.0927 | -59.2392 | -0.004578 | 0 | -0.091553 | 123.024 | -0.18311 | -0.18311 | -0.054932 | 0.004578 | -0.14191 | -0.059509 | 0.041199 | -0.3067 | -0.1648 | -0.096131 | 122.9187 | 122.9553 | 59.0652 | -123.0103 | 122.9507 | 122.9141 | 59.0057 | -123.1522
7.5156 | 123.1155 | -59.1385 | 63.8718 | -0.033569 | 0.0075451 | 0.06545 | 0.069218 | 0.13255 | 0.0019078 | 0.0021255 | 0.026169 | -5.9768e-05 | 0.0017454 | 0.0003182 | 0.001128 | -0.00025626 | 63.8855 | 63.9725 | -0.013733 | -59.2896 | 63.7985 | -59.1202 | -59.1293 | -59.0515 | 0.050354 | -59.3857 | 63.8535 | 63.7802 | -59.0973 | -59.2484 | 0.018311 | 0.009156 | -0.073242 | 123.111 | -0.15106 | -0.16022 | 0.013733 | 0.041199 | -0.10986 | -0.01831 | 0.086975 | -0.24719 | -0.13733 | -0.091553 | 122.937 | 123.024 | 59.1248 | -123.0011 | 122.9919 | 122.9187 | 59.1888 | -123.1201
8.5156 | 123.1705 | -59.079 | 63.9084 | -0.14801 | 0.0032727 | 0.067159 | 0.065159 | 0.13212 | -1.505e-05 | -0.00043792 | -0.11879 | 0.00058103 | 0.0008908 | 0.0001046 | 0.00070077 | 0.00017094 | 63.8443 | 63.9404 | -0.018311 | -59.285 | 63.8489 | -59.0973 | -59.1202 | -59.1705 | 0.064087 | -59.3536 | 63.8855 | 63.8306 | -59.0836 | -59.2484 | -0.018311 | -0.041199 | -0.059509 | 123.0194 | -0.20599 | -0.16479 | -0.064087 | -0.004578 | -0.16937 | -0.022888 | -0.091553 | -0.27466 | -0.10529 | -0.07782 | 122.9279 | 122.9233 | 59.0607 | -123.0286 | 122.9645 | 122.9095 | 59.1431 | -123.1567
9.5156 | 123.143 | -59.1202 | 63.8718 | -0.041199 | 0.0071179 | 0.068227 | 0.06815 | 0.1302 | 0.0014804 | -0.00043792 | 0.026169 | 0.00079463 | 0.0004636 | 0.0022408 | 0.00091437 | -0.00089726 | 63.8855 | 63.9587 | -0.032043 | -59.285 | 63.8306 | -59.1248 | -59.1202 | -59.0607 | 0.041199 | -59.3857 | 63.858 | 63.7894 | -59.0927 | -59.2621 | -0.004578 | 0 | -0.041199 | 123.0789 | -0.16479 | -0.16479 | 0.013733 | 0.027466 | -0.14191 | -0.013733 | 0.059509 | -0.2655 | -0.1236 | -0.082397 | 122.9507 | 123.0057 | 59.0881 | -122.9919 | 122.9782 | 122.9095 | 59.1614 | -123.1338
10.5156 | 123.1888 | -59.0927 | 63.8947 | -0.11749 | 0.0071179 | 0.065877 | 0.069432 | 0.13084 | 0.001694 | -0.00043792 | -0.095902 | -0.001128 | 0.0017454 | -0.0013906 | 0.0017688 | 0.00038454 | 63.8397 | 63.9587 | -0.022888 | -59.2758 | 63.8397 | -59.0973 | -59.1248 | -59.0286 | 0.068665 | -59.3445 | 63.9084 | 63.8397 | -59.0652 | -59.2346 | -0.004578 | -0.032044 | -0.054931 | 123.0515 | -0.18311 | -0.15106 | -0.054931 | 0.027465 | -0.14191 | 0.013733 | 0.064087 | -0.25177 | -0.10986 | -0.054931 | 122.9324 | 122.9324 | 59.0698 | -123.0194 | 123.0011 | 122.9324 | 59.1614 | -123.1293
11.5156 | 123.1979 | -59.1019 | 63.8397 | 0.24109 | 0.0051953 | 0.066518 | 0.068791 | 0.13191 | -0.0034328 | -0.00043792 | 0.32372 | -0.002196 | 3.6404e-05 | -0.0007498 | 0.00091437 | -0.00089726 | 63.8718 | 64.0137 | -0.004578 | -59.2667 | 63.7299 | -59.1019 | -59.1248 | -59.0057 | 0.032043 | -59.317 | 63.7894 | 63.7436 | -59.0973 | -59.2438 | 0 | -0.022888 | -0.10986 | 123.1155 | -0.16479 | -0.14191 | 0.032043 | 0.004578 | -0.14191 | -0.050354 | 0.096131 | -0.21515 | -0.073243 | -0.096131 | 122.8317 | 122.9736 | 59.0973 | -122.9645 | 122.8912 | 122.8455 | 59.1339 | -123.0835
12.5156 | 123.1522 | -59.1156 | 63.9221 | -0.094604 | 0.0069043 | 0.069081 | 0.06815 | 0.12934 | 0.0012668 | -0.0036423 | -0.14931 | -0.00091437 | 0.0017454 | -0.001818 | 0.0017688 | -0.0019653 | 63.8397 | 63.9359 | -0.027466 | -59.2804 | 63.8077 | -59.0927 | -59.0973 | -59.0469 | 0.059509 | -59.3353 | 63.8992 | 63.8214 | -59.0927 | -59.2392 | 0.022889 | 0.018311 | -0.11444 | 123.0515 | -0.1648 | -0.18311 | -0.082397 | 0.022889 | -0.1236 | -0.022888 | 0.068665 | -0.21973 | -0.09613 | -0.10071 | 122.9233 | 122.9553 | 59.0881 | -123.0194 | 123.0148 | 122.937 | 59.1751 | -123.1613
13.5156 | 123.111 | -59.1431 | 63.8763 | 0.012207 | 0.0098951 | 0.065236 | 0.067936 | 0.13041 | 0.00041235 | 0.00020288 | 0.079574 | 0.00036743 | 0.0025998 | -0.001818 | 0.00091437 | -0.0032471 | 63.8489 | 63.9267 | -0.045776 | -59.285 | 63.7985 | -59.1019 | -59.1431 | -59.1019 | -0.013733 | -59.4315 | 63.858 | 63.7985 | -59.1156 | -59.2712 | 0.041198 | 0 | -0.07782 | 123.0698 | -0.14191 | -0.14191 | -0.027466 | 0.027465 | -0.12817 | -0.018311 | 0.041198 | -0.28839 | -0.16022 | -0.07782 | 122.9416 | 122.9919 | 59.0973 | -123.0194 | 123.0011 | 122.9416 | 59.1293 | -123.1476
14.5156 | 123.1659 | -59.1064 | 63.858 | -0.064087 | 0.0092541 | 0.0678 | 0.068364 | 0.13276 | 0.00083955 | -1.0724e-05 | 0.0032804 | 0.0014356 | 0.0017454 | -0.000109 | 0.0013416 | -0.00089726 | 63.8809 | 63.9679 | 0.004578 | -59.2575 | 63.8306 | -59.111 | -59.1202 | -59.0515 | 0.073242 | -59.3628 | 63.8626 | 63.7939 | -59.079 | -59.2438 | -0.004578 | -0.013733 | -0.027466 | 123.0743 | -0.15106 | -0.13733 | 0.022888 | 0.027466 | -0.13733 | 0.004578 | 0.054931 | -0.25635 | -0.11902 | -0.064087 | 122.937 | 122.9874 | 59.111 | -122.9782 | 122.9691 | 122.9004 | 59.1797 | -123.1018
15.5156 | 123.0972 | -59.1431 | 63.8809 | 0.057983 | 0.010322 | 0.066945 | 0.06815 | 0.13105 | 0.002335 | -0.00086512 | 0.19402 | 0.00058103 | 0.0011044 | 0.0026682 | 0.0013416 | -0.0013245 | 63.8351 | 63.9267 | -0.059509 | -59.317 | 63.7939 | -59.1248 | -59.1293 | -59.0927 | -0.036621 | -59.4223 | 63.8626 | 63.8031 | -59.0973 | -59.2575 | 0.01831 | 0.013733 | -0.086975 | 123.0698 | -0.17395 | -0.18768 | -0.045776 | 0.045776 | -0.11444 | -0.01831 | 0.050354 | -0.27924 | -0.1648 | -0.077819 | 122.937 | 122.9782 | 59.0836 | -123.0103 | 123.0057 | 122.9462 | 59.1064 | -123.1384
16.5156 | 123.2071 | -59.111 | 63.858 | 0.81329 | 0.0039135 | 0.067372 | 0.069432 | 0.13126 | -0.0053554 | -0.0036423 | 0.27794 | -0.002837 | 0.0006772 | -0.000109 | -0.0029308 | 0.00038454 | 63.8489 | 63.9633 | -0.050354 | -59.3033 | 63.739 | -59.1064 | -59.1202 | -59.0332 | 0.009155 | -59.3445 | 63.8214 | 63.7665 | -59.0927 | -59.2529 | 0.004578 | -0.009155 | -0.11902 | 123.0743 | -0.19226 | -0.18311 | -0.009155 | 0.018311 | -0.14191 | -0.036621 | 0.07782 | -0.23346 | -0.091552 | -0.091553 | 122.85 | 122.9599 | 59.0607 | -122.9782 | 122.9324 | 122.8775 | 59.1202 | -123.111
17.5156 | 123.1338 | -59.1385 | 63.8855 | 0.042725 | 0.0094677 | 0.066304 | 0.068791 | 0.13062 | 0.0027622 | -0.00022432 | 0.071945 | -0.001128 | 0.0017454 | 0.0018136 | 0.002196 | -0.0026063 | 63.8489 | 63.9221 | -0.059509 | -59.3124 | 63.8077 | -59.1385 | -59.1476 | -59.1064 | -0.022888 | -59.4269 | 63.8626 | 63.7848 | -59.111 | -59.2621 | 0 | -0.009155 | -0.07782 | 123.0606 | -0.17395 | -0.16479 | -0.036621 | 0.027466 | -0.1236 | -0.022888 | 0.032044 | -0.28839 | -0.16479 | -0.10071 | 122.9462 | 122.9874 | 59.079 | -123.0331 | 123.0011 | 122.9233 | 59.1156 | -123.1476
18.5156 | 123.1476 | -59.1431 | 63.8947 | -0.15564 | 0.0086133 | 0.066945 | 0.067936 | 0.13148 | -0.0025784 | -0.0030013 | -0.088272 | 0.0012218 | 0.0017454 | 0.0007456 | 0.00091437 | -4.2662e-05 | 63.8443 | 63.9313 | -0.018311 | -59.2896 | 63.8397 | -59.1339 | -59.1248 | -59.0744 | 0.050354 | -59.3765 | 63.8901 | 63.8443 | -59.0927 | -59.2575 | 0.009155 | 0.01831 | -0.054931 | 123.0743 | -0.14649 | -0.1648 | -0.050354 | 0.050354 | -0.11444 | -0.004577 | 0.068664 | -0.23346 | -0.11902 | -0.050354 | 122.9828 | 122.9874 | 59.1248 | -123.0194 | 123.0331 | 122.9874 | 59.1934 | -123.1522
19.5156 | 123.1338 | -59.1248 | 63.8901 | 0.0045777 | 0.012031 | 0.066518 | 0.065373 | 0.13084 | 0.002335 | -0.0010787 | 0.10246 | 0.0012218 | 0.0008908 | -0.0003226 | 0.0026234 | -0.00047006 | 63.8763 | 63.9404 | -0.050354 | -59.3033 | 63.8214 | -59.111 | -59.1385 | -59.0927 | 0.013733 | -59.3948 | 63.8489 | 63.8077 | -59.111 | -59.2712 | 0.013733 | -0.013733 | -0.068665 | 123.0652 | -0.17853 | -0.16479 | -0.013733 | 0.013733 | -0.14648 | -0.041199 | 0.032044 | -0.27008 | -0.1236 | -0.082398 | 122.9462 | 123.0011 | 59.0744 | -123.0286 | 122.9736 | 122.9324 | 59.1385 | -123.1613
20.5156 | 123.1384 | -59.0927 | 63.8763 | -0.056458 | 0.0079723 | 0.066304 | 0.066227 | 0.13084 | 0.0038304 | -0.0012923 | 0.0032804 | 0.0012218 | 0.0025998 | 0.0013864 | 0.0017688 | -0.0028199 | 63.8718 | 63.9816 | -0.013733 | -59.2712 | 63.8123 | -59.111 | -59.1339 | -59.0515 | 0.068665 | -59.3719 | 63.858 | 63.8351 | -59.0836 | -59.2392 | -0.018311 | -0.041199 | -0.064087 | 123.0743 | -0.17853 | -0.13733 | -0.004578 | 0.009155 | -0.14648 | -0.018311 | 0.041198 | -0.27924 | -0.13275 | -0.041199 | 122.905 | 122.9645 | 59.079 | -123.0103 | 122.9507 | 122.9279 | 59.1614 | -123.1155
21.5156 | 123.1979 | -59.0836 | 63.8763 | 0.050354 | 0.0019909 | -0.034312 | 0.069005 | 0.12849 | -0.0074918 | -0.0034287 | 0.20164 | -0.0036914 | -0.0025272 | -0.0041678 | -0.0037854 | 0.00081174 | 63.8306 | 63.9908 | -0.027466 | -59.2667 | 63.7436 | -59.1064 | -59.1019 | -59.0332 | 0.059509 | -59.3033 | 63.826 | 63.7939 | -59.0973 | -59.2438 | -0.022888 | -0.018311 | -0.13275 | 123.0743 | -0.18311 | -0.16479 | -0.045777 | -0.013733 | -0.16022 | -0.050354 | 0.050354 | -0.21973 | -0.05951 | -0.082398 | 122.8271 | 122.9141 | 59.0561 | -122.9782 | 122.9095 | 122.8775 | 59.1431 | -123.1201
22.5156 | 123.175 | -59.111 | 63.858 | -0.094604 | 0.0071179 | 0.066945 | 0.071354 | 0.13191 | 0.0014804 | -0.00022432 | 0.01091 | 0.0018628 | 0.003027 | -0.001177 | 0.002837 | -0.0030335 | 63.8901 | 63.9633 | 0 | -59.2712 | 63.8123 | -59.1064 | -59.1385 | -59.0469 | 0.064087 | -59.3582 | 63.8718 | 63.8123 | -59.0973 | -59.2392 | 0.004578 | -0.027466 | -0.045776 | 123.0743 | -0.16022 | -0.13275 | 0.032044 | 0.013733 | -0.12817 | 0.013733 | 0.064087 | -0.24719 | -0.11902 | -0.045776 | 122.9233 | 123.0011 | 59.111 | -122.9965 | 122.9828 | 122.9233 | 59.1751 | -123.0972
23.5156 | 123.1155 | -59.1339 | 63.8809 | -0.02594 | 0.0077587 | 0.066945 | 0.070073 | 0.13212 | 0.0027622 | 0.00020288 | 0.15587 | -0.001128 | 0.0021726 | -0.000109 | 0.0017688 | -0.0021789 | 63.8443 | 63.9267 | -0.059509 | -59.3216 | 63.8168 | -59.1339 | -59.111 | -59.0973 | -0.041199 | -59.4406 | 63.858 | 63.8214 | -59.1156 | -59.23 | 0 | 0.022888 | -0.064087 | 123.0606 | -0.18768 | -0.21057 | -0.036621 | 0.01831 | -0.096131 | -0.022888 | 0.036621 | -0.3067 | -0.21057 | -0.059509 | 122.9507 | 122.9782 | 59.0744 | -122.9919 | 122.9919 | 122.9553 | 59.0927 | -123.111
24.5156 | 123.1705 | -59.0881 | 63.8809 | -0.16327 | 0.010963 | 0.065877 | 0.068577 | 0.13511 | -0.00022865 | -1.0724e-05 | -0.0043486 | 0.00058103 | 0.0011044 | -0.001177 | 0.00091437 | -0.0021789 | 63.8992 | 63.9725 | 0 | -59.2575 | 63.8123 | -59.0973 | -59.1248 | -59.0378 | 0.082397 | -59.3582 | 63.858 | 63.8123 | -59.0927 | -59.2438 | -0.009155 | -0.036621 | -0.068664 | 123.0606 | -0.16937 | -0.13275 | 0.018311 | -0.004577 | -0.15564 | -0.022888 | 0.050354 | -0.27008 | -0.11444 | -0.068664 | 122.9004 | 122.9874 | 59.0881 | -123.0057 | 122.9462 | 122.9004 | 59.1705 | -123.1247
25.5156 | 123.1613 | -59.1019 | 63.8672 | -0.018311 | 0.01075 | 0.066518 | 0.067723 | 0.13062 | -1.505e-05 | -0.0021469 | 0.049057 | 0.0010082 | 0.001318 | 0.0007456 | -0.00015383 | -0.00089726 | 63.8855 | 63.9542 | 0 | -59.2804 | 63.8306 | -59.1019 | -59.1293 | -59.0515 | 0.050354 | -59.3674 | 63.8535 | 63.8077 | -59.0881 | -59.2438 | 0 | -0.027465 | -0.036621 | 123.056 | -0.17853 | -0.15106 | 0.018311 | 0.013733 | -0.14191 | -0.013732 | 0.050354 | -0.2655 | -0.1236 | -0.059509 | 122.9324 | 122.9874 | 59.1019 | -122.9965 | 122.9553 | 122.9095 | 59.1522 | -123.111
26.5156 | 123.2437 | -59.0698 | 63.8214 | 0.26398 | 0.0041271 | 0.066304 | 0.065159 | 0.13191 | -0.0030056 | -0.0017197 | 0.27031 | -0.0017688 | -0.0012454 | 0.0018136 | -0.0010082 | 0.00059814 | 63.8809 | 63.9999 | -0.050354 | -59.2621 | 63.7665 | -59.1156 | -59.1385 | -59.0012 | 0.032043 | -59.317 | 63.8168 | 63.7344 | -59.0881 | -59.23 | -0.045777 | -0.068665 | -0.054932 | 123.0698 | -0.19226 | -0.1236 | 0.059509 | -0.018311 | -0.16022 | -0.004578 | 0.068664 | -0.24719 | -0.086975 | -0.086975 | 122.8363 | 122.9507 | 59.0195 | -122.9599 | 122.8867 | 122.8043 | 59.1019 | -123.0515
27.5156 | 123.1247 | -59.1339 | 63.8672 | 0.065613 | 0.0079723 | 0.066091 | 0.0705 | 0.13276 | 0.0025486 | -0.00022432 | 0.14061 | 0.00015383 | 0.0028134 | -0.0003226 | 0.0013416 | -0.0021789 | 63.8443 | 63.8947 | -0.086975 | -59.3262 | 63.8077 | -59.1293 | -59.1293 | -59.1248 | -0.050354 | -59.4406 | 63.8626 | 63.7939 | -59.1385 | -59.2392 | 0.004578 | 0.004578 | -0.059509 | 123.0286 | -0.19226 | -0.19684 | -0.022888 | -0.004578 | -0.10529 | -0.004577 | 0.009155 | -0.3067 | -0.20142 | -0.073242 | 122.9416 | 122.9782 | 59.0469 | -122.9965 | 122.9965 | 122.9279 | 59.0836 | -123.1064
28.5156 | 123.1705 | -59.111 | 63.8672 | -0.094604 | 0.010963 | 0.0678 | 0.067509 | 0.13297 | 0.00062595 | -0.00043792 | 0.026169 | 0.0012218 | -0.0012454 | 0.0009592 | 0.00091437 | -0.0023927 | 63.8901 | 63.9542 | 0.009155 | -59.2758 | 63.826 | -59.0973 | -59.1202 | -59.0378 | 0.073242 | -59.3628 | 63.8672 | 63.8031 | -59.0836 | -59.2209 | 0.013733 | -0.009155 | -0.041198 | 123.0652 | -0.16479 | -0.15564 | 0.022889 | 0.027466 | -0.10986 | 0 | 0.073242 | -0.25177 | -0.14191 | -0.064086 | 122.937 | 123.0011 | 59.1202 | -122.9874 | 122.9782 | 122.9141 | 59.1843 | -123.0881
29.5156 | 123.1247 | -59.1202 | 63.8901 | 0.050354 | 0.010322 | 0.06545 | 0.067936 | 0.13191 | 0.0012668 | -0.0012923 | 0.19402 | -0.0024096 | 0.0017454 | -0.0003226 | 0.0017688 | -0.0028199 | 63.8443 | 63.9313 | -0.059509 | -59.3262 | 63.8031 | -59.1293 | -59.1385 | -59.0744 | -0.013733 | -59.4223 | 63.8626 | 63.8214 | -59.0973 | -59.23 | -0.009155 | -0.018311 | -0.086975 | 123.0515 | -0.20599 | -0.18768 | -0.045777 | 0.022888 | -0.10986 | -0.027466 | 0.045776 | -0.30212 | -0.19226 | -0.068665 | 122.9233 | 122.9645 | 59.0607 | -123.0286 | 122.9828 | 122.9416 | 59.1064 | -123.1201
30.5156 | 123.1796 | -59.111 | 63.8718 | -0.33112 | 0.0049817 | 0.064382 | 0.067296 | 0.13169 | 0.0014804 | -1.0724e-05 | 0.018539 | -0.00027337 | 0.0034542 | -0.001177 | -0.00036743 | -0.0013245 | 63.8901 | 63.9633 | 0.009155 | -59.2712 | 63.8397 | -59.0927 | -59.1248 | -59.0424 | 0.086975 | -59.3628 | 63.8535 | 63.8535 | -59.0927 | -59.2575 | 0.018311 | -0.013733 | -0.032043 | 123.0743 | -0.16022 | -0.14648 | 0.018311 | 0.018311 | -0.14648 | -0.01831 | 0.068665 | -0.25177 | -0.10529 | -0.01831 | 122.9507 | 123.0011 | 59.1202 | -122.9965 | 122.9645 | 122.9645 | 59.198 | -123.1293
31.5156 | 123.2483 | -59.0973 | 63.8535 | 0.22583 | 0.0047681 | 0.066091 | 0.065159 | 0.13084 | -0.0030056 | -0.0025741 | 0.38475 | -0.00027337 | -0.0023136 | 0.0013864 | 0.00027337 | -4.2662e-05 | 63.8855 | 64.0137 | 0 | -59.2575 | 63.7436 | -59.0836 | -59.079 | -59.0012 | 0.050354 | -59.3124 | 63.7848 | 63.7344 | -59.079 | -59.2209 | 0.013733 | 0.018311 | -0.10986 | 123.111 | -0.16022 | -0.17853 | 0.032043 | 0.018311 | -0.1236 | -0.068665 | 0.09613 | -0.21515 | -0.091553 | -0.11902 | 122.8409 | 122.9828 | 59.0973 | -122.9324 | 122.8821 | 122.8317 | 59.1476 | -123.0743
32.5156 | 123.1476 | -59.0927 | 63.9175 | -0.1709 | 0.0036999 | 0.067159 | 0.067509 | 0.12849 | -0.00044225 | -0.0012923 | -0.065384 | -0.0017688 | -0.000391 | -0.0003226 | -0.00015383 | -0.0013245 | 63.8397 | 63.9404 | -0.032043 | -59.2987 | 63.8168 | -59.0973 | -59.111 | -59.0881 | 0.045776 | -59.404 | 63.8855 | 63.826 | -59.0927 | -59.2438 | -0.004578 | -0.018311 | -0.10071 | 123.0331 | -0.20599 | -0.18768 | -0.07782 | 0 | -0.15106 | -0.032044 | 0.004577 | -0.31128 | -0.16022 | -0.091553 | 122.9095 | 122.9324 | 59.0607 | -123.0286 | 122.9782 | 122.9187 | 59.1385 | -123.1613
33.5156 | 123.1522 | -59.111 | 63.8901 | 0.035095 | 0.0090405 | 0.065236 | 0.067936 | 0.13212 | 0.001694 | -0.0017197 | 0.087204 | -0.0017688 | -0.0001774 | 0.0003182 | 0.0032642 | -0.0028199 | 63.8947 | 63.9633 | -0.022888 | -59.2758 | 63.8077 | -59.0973 | -59.1202 | -59.0469 | 0.013733 | -59.3857 | 63.8489 | 63.7711 | -59.1064 | -59.2392 | 0.013733 | -0.009155 | -0.082398 | 123.0743 | -0.16479 | -0.15564 | 0.004577 | 0.004578 | -0.12817 | -0.041199 | 0.064087 | -0.27466 | -0.14648 | -0.11902 | 122.9187 | 123.0057 | 59.0881 | -123.0103 | 122.9599 | 122.8821 | 59.1248 | -123.1293
34.5156 | 123.1613 | -59.0744 | 63.8809 | -0.12512 | 0.0075451 | 0.066731 | 0.070927 | 0.13191 | 0.003403 | 0.0016983 | -0.011978 | -0.00091437 | 0.0021726 | 0.0007456 | 0.00070077 | -0.0026063 | 63.8947 | 63.9908 | -0.009155 | -59.2712 | 63.826 | -59.1202 | -59.111 | -59.0332 | 0.07782 | -59.3491 | 63.8672 | 63.8031 | -59.0744 | -59.2529 | -0.045776 | -0.036621 | -0.054931 | 123.0652 | -0.19684 | -0.16022 | 0.013733 | 0 | -0.17853 | -0.013733 | 0.041199 | -0.27466 | -0.09613 | -0.077819 | 122.9004 | 122.9691 | 59.0652 | -122.9919 | 122.9416 | 122.8775 | 59.1522 | -123.1338
35.5156 | 123.0972 | -59.1248 | 63.8809 | 0.065613 | 0.010109 | 0.063527 | 0.069218 | 0.12913 | 0.00083955 | -0.00022432 | 0.11009 | -0.0019824 | 0.0011044 | 0.0024546 | 0.00027337 | -0.0017517 | 63.8397 | 63.9313 | -0.059509 | -59.3124 | 63.7802 | -59.111 | -59.111 | -59.111 | -0.013733 | -59.4223 | 63.8489 | 63.8168 | -59.111 | -59.2621 | 0.013733 | 0.013733 | -0.10071 | 123.056 | -0.18768 | -0.20142 | -0.041198 | 0.013733 | -0.13733 | -0.032043 | 0.013733 | -0.29755 | -0.16022 | -0.064087 | 122.905 | 122.9645 | 59.0652 | -122.9919 | 122.9736 | 122.9416 | 59.111 | -123.143
36.5156 | 123.1659 | -59.0927 | 63.8809 | 0.12665 | 0.0094677 | 0.066304 | 0.068791 | 0.13148 | 0.00062595 | -0.0010787 | -0.027237 | -0.00091437 | 0.0017454 | 0.0003182 | 0.0013416 | -0.0017517 | 63.8626 | 63.9816 | 0.004578 | -59.2621 | 63.8031 | -59.0927 | -59.1385 | -59.0469 | 0.068665 | -59.3491 | 63.8672 | 63.8351 | -59.079 | -59.2209 | 0 | -0.045777 | -0.077819 | 123.0743 | -0.16937 | -0.1236 | -0.01831 | 0.013733 | -0.12817 | -0.013733 | 0.045776 | -0.25635 | -0.12817 | -0.045776 | 122.8958 | 122.9553 | 59.0973 | -123.0194 | 122.9599 | 122.9279 | 59.1614 | -123.1018
37.5156 | 123.1247 | -59.1019 | 63.8763 | 0.012207 | 0.0086133 | 0.066731 | 0.069645 | 0.1302 | 0.001694 | -0.0012923 | 0.087204 | -0.001128 | 0.0023862 | -0.0016044 | 0.0024096 | 0.0010253 | 63.8489 | 63.9404 | -0.054932 | -59.2941 | 63.7802 | -59.1248 | -59.1293 | -59.0927 | 0.009155 | -59.404 | 63.8535 | 63.8031 | -59.1019 | -59.2529 | -0.022888 | -0.027465 | -0.096131 | 123.0423 | -0.19226 | -0.16479 | -0.027466 | 0 | -0.15106 | -0.022888 | 0.009156 | -0.30212 | -0.15106 | -0.073242 | 122.8821 | 122.9507 | 59.0469 | -123.0057 | 122.9553 | 122.905 | 59.111 | -123.1293
38.5156 | 123.1567 | -59.1064 | 63.8718 | -0.16327 | 0.0083997 | 0.065877 | 0.067723 | 0.13084 | -0.0012966 | -0.0015061 | -0.057755 | 0.00058103 | -0.0025272 | 0.0007456 | 0.001128 | -0.00089726 | 63.8397 | 63.9999 | 0.036621 | -59.2621 | 63.8351 | -59.0744 | -59.1156 | -59.0652 | 0.10071 | -59.3628 | 63.8535 | 63.8443 | -59.0836 | -59.198 | 0.032043 | -0.009156 | -0.036621 | 123.1064 | -0.15564 | -0.14648 | -0.032043 | 0.022888 | -0.091553 | -0.01831 | 0.041198 | -0.25635 | -0.1648 | -0.027466 | 122.9416 | 122.9462 | 59.1431 | -122.9874 | 122.9599 | 122.9507 | 59.2072 | -123.0698
39.5156 | 123.1522 | -59.1064 | 63.8992 | -0.064087 | 0.0088269 | 0.065877 | 0.070073 | 0.12998 | 0.00019875 | -0.00065152 | -0.0043486 | -0.00070077 | 0.001318 | 0.0007456 | -0.00015383 | -0.0017517 | 63.8626 | 63.9725 | -0.009155 | -59.2712 | 63.8214 | -59.1019 | -59.1339 | -59.0424 | 0.059509 | -59.3491 | 63.8351 | 63.7756 | -59.0698 | -59.2346 | 0.004577 | -0.027466 | -0.07782 | 123.0789 | -0.16479 | -0.13733 | -0.036621 | 0.036621 | -0.12817 | -0.064087 | 0.064087 | -0.24262 | -0.11444 | -0.1236 | 122.9279 | 122.9691 | 59.0973 | -123.0331 | 122.9416 | 122.8821 | 59.166 | -123.1338
40.5156 | 123.1888 | -59.0744 | 63.8947 | -0.15564 | 0.0075451 | 0.066945 | 0.069859 | 0.12956 | 0.00041235 | 0.00041648 | 0.28557 | -5.9768e-05 | -0.0008182 | -0.0003226 | -0.00036743 | -0.0017517 | 63.8306 | 63.9496 | -0.013733 | -59.2026 | 63.826 | -59.0881 | -59.1339 | -59.0378 | 0.068665 | -59.3582 | 63.8855 | 63.8306 | -59.0607 | -59.2438 | -0.013733 | -0.059509 | -0.068664 | 123.024 | -0.12817 | -0.068665 | -0.064087 | 0.013733 | -0.16937 | -0.009155 | 0.036621 | -0.28381 | -0.11444 | -0.064087 | 122.9004 | 122.905 | 59.0607 | -123.0286 | 122.9599 | 122.905 | 59.1431 | -123.1384
41.5156 | 123.111 | -59.0973 | 63.8718 | 0.042725 | 0.0094677 | 0.065022 | 0.066655 | 0.12742 | 0.0021214 | -0.00043792 | 0.13298 | 0.0010082 | 0.001318 | 0.0016 | 0.0024096 | 0.0023071 | 63.8443 | 63.9175 | -0.050354 | -59.3124 | 63.8123 | -59.1019 | -59.1202 | -59.1202 | -0.018311 | -59.4406 | 63.8718 | 63.8031 | -59.1156 | -59.2667 | -0.004578 | -0.022888 | -0.059509 | 123.0148 | -0.21515 | -0.19226 | -0.027466 | -0.018311 | -0.16937 | 0 | -0.022888 | -0.34332 | -0.17395 | -0.068664 | 122.9095 | 122.9416 | 59.0469 | -122.9919 | 122.9691 | 122.9004 | 59.079 | -123.1384
42.5156 | 123.1613 | -59.0927 | 63.8718 | -0.086975 | 0.0077587 | 0.064168 | 0.06815 | 0.13276 | 0.0010532 | -0.0025741 | 0.0032804 | 0.0012218 | 0.0011044 | 0.0001046 | 0.001128 | -0.0011109 | 63.8718 | 63.9725 | 0.004578 | -59.2758 | 63.8168 | -59.111 | -59.1064 | -59.0469 | 0.073242 | -59.3582 | 63.8535 | 63.7894 | -59.0927 | -59.2346 | -0.018311 | -0.013733 | -0.054932 | 123.0652 | -0.18311 | -0.16937 | 0 | 0 | -0.14191 | -0.01831 | 0.045776 | -0.2655 | -0.1236 | -0.082397 | 122.9095 | 122.9645 | 59.0973 | -122.9782 | 122.9462 | 122.8821 | 59.166 | -123.1064
43.5156 | 123.0972 | -59.1248 | 63.8809 | 0.050354 | 0.010109 | 0.067372 | 0.067296 | 0.13255 | 0.0025486 | -0.00043792 | 0.13298 | -0.00070077 | 0.0011044 | 0.0003182 | 0.00070077 | -0.00089726 | 63.8351 | 63.9221 | -0.082397 | -59.3033 | 63.7985 | -59.1202 | -59.1202 | -59.1064 | -0.032043 | -59.4315 | 63.8489 | 63.8168 | -59.1019 | -59.2804 | 0.004578 | 0.004578 | -0.082397 | 123.0469 | -0.17853 | -0.18311 | -0.045776 | 0.022888 | -0.15564 | -0.032043 | 0.018311 | -0.3067 | -0.15106 | -0.064087 | 122.9233 | 122.9599 | 59.0424 | -123.0011 | 122.9736 | 122.9416 | 59.0927 | -123.1613
44.6094 | 123.2071 | -59.1064 | 63.858 | 0.17242 | 0.0062635 | 0.067586 | 0.067296 | 0.12998 | -0.0042874 | -0.0027877 | 1.018 | -0.00070077 | 0.0008908 | -0.0003226 | -0.0018628 | -0.00068366 | 63.8626 | 63.9862 | -0.013733 | -59.2804 | 63.7207 | -59.0927 | -59.1019 | -59.0195 | 0.004578 | -59.3399 | 63.7939 | 63.7527 | -59.1019 | -59.2163 | 0.013733 | 0.004577 | -0.13733 | 123.0927 | -0.17395 | -0.17853 | 0.004578 | 0.004577 | -0.10986 | -0.064087 | 0.086975 | -0.23346 | -0.1236 | -0.10529 | 122.8271 | 122.9691 | 59.0927 | -122.9599 | 122.9004 | 122.8592 | 59.111 | -123.0743
45.625 | 123.2346 | -59.0881 | 63.8168 | 0.18768 | 0.0051953 | 0.066304 | 0.063664 | 0.13084 | -0.0032192 | -0.0023605 | 0.33134 | -0.00070077 | -0.0018862 | -0.000109 | 0.0015552 | -0.00089726 | 63.8855 | 64.0137 | 0 | -59.2667 | 63.7344 | -59.1019 | -59.111 | -59.0103 | 0.045776 | -59.317 | 63.8077 | 63.739 | -59.0881 | -59.2163 | -0.013733 | -0.022888 | -0.082397 | 123.1018 | -0.17853 | -0.15564 | 0.068665 | 0 | -0.12817 | -0.009155 | 0.07782 | -0.22888 | -0.10071 | -0.077819 | 122.8226 | 122.9736 | 59.0881 | -122.9279 | 122.8958 | 122.8271 | 59.1339 | -123.0331
47.0625 | 123.1384 | -59.0836 | 63.9084 | -0.18616 | 0.0062635 | 0.065877 | 0.067936 | 0.12956 | -0.0015102 | -0.0034287 | -0.15694 | -0.0019824 | 0.0015316 | 0.0007456 | -0.00058103 | -0.0019653 | 63.9496 | 64.0274 | 0.054932 | -59.2438 | 63.8031 | -59.0927 | -59.0927 | -59.0378 | 0.073242 | -59.3582 | 63.8718 | 63.8214 | -59.0927 | -59.2209 | -0.009155 | -0.009155 | -0.10529 | 123.111 | -0.16022 | -0.15106 | 0.041199 | -0.009155 | -0.13733 | -0.036621 | 0.045776 | -0.27466 | -0.13733 | -0.086975 | 122.8867 | 123.0331 | 59.1385 | -123.0011 | 122.9553 | 122.905 | 59.1568 | -123.1293
48.4062 | 123.1476 | -59.0973 | 63.8809 | -0.064087 | 0.0064771 | 0.066731 | 0.066014 | 0.13233 | 0.0012668 | 0.00020288 | -0.019608 | -0.0015552 | -0.0010318 | -0.0007498 | 0.0034778 | -0.0013245 | 63.8947 | 63.9679 | 0.004578 | -59.2575 | 63.826 | -59.1019 | -59.1064 | -59.0378 | 0.050354 | -59.3719 | 63.8489 | 63.7802 | -59.0836 | -59.23 | -0.004578 | -0.009155 | -0.054931 | 123.0652 | -0.16022 | -0.15106 | 0.013733 | 0.013733 | -0.13275 | -0.032043 | 0.059509 | -0.27466 | -0.14191 | -0.10071 | 122.9233 | 122.9919 | 59.1019 | -122.9874 | 122.9462 | 122.8775 | 59.1476 | -123.111
49.1094 | 123.2437 | -59.0744 | 63.8809 | -0.14801 | 0.00049551 | 0.068654 | 0.067082 | 0.13255 | -0.0040738 | -0.0017197 | 0.0032804 | -0.001128 | -0.0018862 | -0.0003226 | -0.00079463 | -0.00068366 | 63.9221 | 64.0823 | 0.082397 | -59.2163 | 63.7802 | -59.0881 | -59.1019 | -58.9874 | 0.17395 | -59.2575 | 63.8351 | 63.7711 | -59.0744 | -59.1934 | -0.013733 | -0.027466 | -0.10071 | 123.1567 | -0.14191 | -0.11444 | 0.041199 | 0 | -0.11902 | -0.045776 | 0.086975 | -0.1831 | -0.064087 | -0.10986 | 122.8546 | 122.9965 | 59.1568 | -122.9828 | 122.9095 | 122.8455 | 59.2484 | -123.0743
51.0625 | 123.143 | -59.0973 | 63.8809 | 0.0045777 | 0.0069043 | 0.064809 | 0.066441 | 0.13297 | 0.0038304 | -1.0724e-05 | 0.026169 | 0.00036743 | -0.000391 | 0.0011728 | 0.0032642 | -0.0019653 | 63.8992 | 63.9771 | -0.027466 | -59.2896 | 63.8168 | -59.1064 | -59.0973 | -59.0607 | 0.022888 | -59.3948 | 63.8443 | 63.7802 | -59.0973 | -59.2529 | -0.009155 | 0 | -0.064087 | 123.0743 | -0.19226 | -0.19226 | 0.018311 | 0 | -0.15564 | -0.036621 | 0.036621 | -0.29755 | -0.14191 | -0.10071 | 122.9141 | 122.9965 | 59.0698 | -122.9782 | 122.9416 | 122.8775 | 59.1202 | -123.1338
52.25 | 123.1934 | -59.0698 | 63.858 | 0.11902 | 0.0054089 | 0.066518 | 0.068791 | 0.12934 | -0.0023648 | -0.0032151 | 0.65178 | -0.00070077 | 0.003668 | 0.0001046 | -0.00058103 | 0.00038454 | 63.8672 | 64.0045 | -0.054932 | -59.1751 | 63.7665 | -59.111 | -59.111 | -59.0424 | 0.013733 | -59.3353 | 63.8031 | 63.7527 | -59.0927 | -59.2392 | -0.041199 | -0.041199 | -0.091553 | 123.0743 | -0.10529 | -0.064087 | 0.009155 | -0.022888 | -0.16937 | -0.054931 | 0.027466 | -0.2655 | -0.09613 | -0.10529 | 122.8363 | 122.937 | 59.0149 | -122.9691 | 122.8729 | 122.8226 | 59.0836 | -123.0972
52.9375 | 123.2712 | -59.0469 | 63.8672 | -0.094604 | 0.0062635 | 0.06844 | 0.067296 | 0.13126 | -0.0015102 | -0.0038559 | 0.049057 | -0.001128 | 0.0021726 | -0.0016044 | -0.0033582 | -0.0026063 | 63.9267 | 64.0915 | 0.091553 | -59.2209 | 63.7894 | -59.0927 | -59.0607 | -58.9417 | 0.16937 | -59.23 | 63.8168 | 63.7711 | -59.0561 | -59.2026 | -0.045776 | -0.013733 | -0.077819 | 123.1384 | -0.17395 | -0.16022 | 0.05951 | -0.009155 | -0.15564 | -0.050354 | 0.10529 | -0.18311 | -0.027466 | -0.09613 | 122.8363 | 122.9736 | 59.1385 | -122.9279 | 122.8638 | 122.818 | 59.2163 | -123.0698
57.4375 | 123.1384 | -59.1064 | 63.8763 | 0.19531 | 0.0096813 | 0.064809 | 0.068791 | 0.13148 | 0.004044 | 0.00041648 | 0.18639 | 0.0016492 | 0.0008908 | -0.001818 | 0.001128 | -0.0034607 | 63.8123 | 63.8855 | -0.13275 | -59.3262 | 63.7985 | -59.1293 | -59.166 | -59.0973 | -0.082397 | -59.4269 | 63.8672 | 63.7711 | -59.1248 | -59.2484 | -0.022888 | -0.05951 | -0.07782 | 122.9919 | -0.21973 | -0.16022 | -0.064087 | -0.018311 | -0.14191 | -0.009156 | 0.009155 | -0.32043 | -0.17853 | -0.10529 | 122.905 | 122.9187 | 58.9737 | -123.0423 | 122.9736 | 122.8775 | 59.024 | -123.1247
58.0938 | 123.2208 | -59.0515 | 63.8535 | 0.17242 | 0.0036999 | 0.065877 | 0.066227 | 0.12913 | -0.0019376 | -0.00065152 | 0.9417 | 0.00015383 | -0.0059452 | -0.0005362 | -0.00015383 | -0.0023927 | 63.8855 | 64.032 | -0.022888 | -59.2758 | 63.7436 | -59.1064 | -59.1248 | -59.0057 | 0.009155 | -59.3536 | 63.7985 | 63.7344 | -59.0744 | -59.2392 | -0.054931 | -0.073242 | -0.10986 | 123.0835 | -0.2243 | -0.15106 | 0.032043 | -0.022888 | -0.18768 | -0.054932 | 0.045777 | -0.30212 | -0.11444 | -0.11902 | 122.7951 | 122.937 | 59.0286 | -122.9782 | 122.85 | 122.7859 | 59.0607 | -123.0927
58.6562 | 123.143 | -59.111 | 63.8397 | 0.15717 | 0.0090405 | 0.066731 | 0.068577 | 0.13297 | 0.00062595 | 0.0016983 | 0.19402 | -5.9768e-05 | 0.0025998 | -0.0005362 | 0.002196 | -0.0043153 | 63.8214 | 63.8809 | -0.13275 | -59.3262 | 63.8123 | -59.1293 | -59.1614 | -59.0973 | -0.086975 | -59.4543 | 63.8535 | 63.7756 | -59.1202 | -59.2392 | -0.01831 | -0.050354 | -0.027466 | 122.9919 | -0.21515 | -0.16479 | -0.018311 | -0.009155 | -0.12817 | 0.013733 | 0.013733 | -0.34332 | -0.21515 | -0.064087 | 122.9233 | 122.9324 | 58.9783 | -123.0011 | 122.9645 | 122.8867 | 59.024 | -123.0789
59.5156 | 123.1705 | -59.1019 | 63.8855 | -0.048828 | 0.0098951 | 0.06545 | 0.069859 | 0.12934 | 0.005112 | 0.00084388 | 0.026169 | 0.0010082 | 0.0025998 | 0.0003182 | 0.002196 | -0.0023927 | 63.9038 | 63.9679 | -0.009155 | -59.2758 | 63.8214 | -59.1064 | -59.1248 | -59.024 | 0.050354 | -59.3674 | 63.8718 | 63.8214 | -59.079 | -59.2209 | -0.004577 | -0.022888 | -0.064087 | 123.0698 | -0.17395 | -0.15106 | 0.018311 | 0.022889 | -0.11902 | -0.013733 | 0.07782 | -0.2655 | -0.14648 | -0.064087 | 122.9233 | 123.0057 | 59.0927 | -123.0103 | 122.9736 | 122.9233 | 59.1522 | -123.1064
60.5156 | 123.111 | -59.1339 | 63.8763 | 0.12665 | 0.0090405 | 0.067372 | 0.069218 | 0.13575 | 0.0014804 | -0.0017197 | 0.18639 | 0.00079463 | 0.0032406 | -0.0013906 | 0.0013416 | -0.0043153 | 63.7939 | 63.8397 | -0.14648 | -59.3491 | 63.7894 | -59.111 | -59.1385 | -59.0973 | -0.082397 | -59.4452 | 63.8443 | 63.8123 | -59.1156 | -59.2438 | 0.022888 | -0.004578 | -0.086975 | 122.9736 | -0.21515 | -0.21057 | -0.082398 | 0.01831 | -0.10986 | -0.032044 | 0.036621 | -0.31128 | -0.20142 | -0.064087 | 122.9233 | 122.9279 | 58.9874 | -123.0148 | 122.9782 | 122.9462 | 59.0515 | -123.1201
61.5156 | 123.1476 | -59.0881 | 63.8992 | -0.16327 | 0.010536 | 0.064809 | 0.066868 | 0.13255 | 0.00083955 | 0.0019119 | -0.065384 | -0.00091437 | 0.0006772 | -0.0013906 | 0.00048697 | -0.0026063 | 63.8809 | 63.9679 | 0 | -59.2529 | 63.8214 | -59.0927 | -59.0927 | -59.0424 | 0.082397 | -59.3674 | 63.8718 | 63.826 | -59.0881 | -59.23 | -0.004577 | -0.004577 | -0.07782 | 123.056 | -0.16479 | -0.16022 | -0.018311 | 0 | -0.14191 | -0.027466 | 0.045777 | -0.27924 | -0.13733 | -0.073242 | 122.9095 | 122.9691 | 59.0881 | -122.9919 | 122.9599 | 122.9141 | 59.1705 | -123.1293
62.5156 | 123.1659 | -59.1202 | 63.8855 | -0.17853 | 0.0049817 | 0.066731 | 0.067936 | 0.13041 | -0.001083 | -0.00086512 | -0.080643 | 0.00079463 | 0.0017454 | 0.000532 | 5.9768e-05 | 0.00081174 | 63.8306 | 63.9359 | -0.022888 | -59.2758 | 63.826 | -59.111 | -59.1202 | -59.0744 | 0.054932 | -59.3765 | 63.9038 | 63.8168 | -59.0927 | -59.2163 | 0.009155 | 0 | -0.059509 | 123.056 | -0.15564 | -0.15564 | -0.054932 | 0.027466 | -0.096131 | 0.018311 | 0.045776 | -0.25635 | -0.16022 | -0.068665 | 122.9462 | 122.9507 | 59.0973 | -123.0057 | 123.024 | 122.937 | 59.1751 | -123.1018
63.5156 | 123.1842 | -59.0973 | 63.8992 | -0.13275 | 0.010322 | 0.066945 | 0.067082 | 0.13062 | 0.0014804 | 0.0021255 | -0.0043486 | -0.001128 | 0.0004636 | -0.0005362 | 0.0015552 | -0.0019653 | 63.8809 | 63.9862 | 0.013733 | -59.2575 | 63.8168 | -59.0927 | -59.111 | -59.0515 | 0.068665 | -59.3674 | 63.8672 | 63.7894 | -59.0881 | -59.23 | 0.004578 | -0.013733 | -0.082398 | 123.0835 | -0.16022 | -0.14648 | -0.018311 | 0.009155 | -0.13275 | -0.032044 | 0.045776 | -0.27008 | -0.13733 | -0.10986 | 122.9141 | 122.9782 | 59.111 | -123.0103 | 122.9645 | 122.8867 | 59.166 | -123.1293
64.5156 | 123.1247 | -59.0881 | 63.8947 | -0.19379 | 0.0049817 | 0.067159 | 0.065159 | 0.13255 | -0.0021512 | -0.0038559 | -0.10353 | 0.00015383 | 0.0015316 | -0.0030996 | 0.001128 | -4.2662e-05 | 63.826 | 63.9496 | -0.013733 | -59.3033 | 63.8306 | -59.1064 | -59.0927 | -59.0927 | 0.064087 | -59.3811 | 63.8763 | 63.8397 | -59.1064 | -59.2163 | -0.01831 | -0.004577 | -0.064087 | 123.0377 | -0.21515 | -0.21057 | -0.068664 | -0.01831 | -0.12817 | -0.01831 | -0.004577 | -0.29297 | -0.16479 | -0.054931 | 122.9187 | 122.9141 | 59.0744 | -122.9874 | 122.9645 | 122.9279 | 59.1522 | -123.111
65.5156 | 123.111 | -59.1156 | 63.8718 | 0.0045777 | 0.0083997 | 0.066091 | 0.069432 | 0.12934 | 0.0010532 | -0.0012923 | 0.056686 | 0.00036743 | 0.0004636 | 0.0016 | 0.00027337 | -0.0034607 | 63.8672 | 63.9679 | -0.032043 | -59.2896 | 63.8077 | -59.0973 | -59.1202 | -59.0607 | 0.032043 | -59.3857 | 63.8443 | 63.7573 | -59.0881 | -59.2392 | 0.018311 | -0.004577 | -0.064087 | 123.0835 | -0.17395 | -0.16937 | -0.004578 | 0.027466 | -0.1236 | -0.027466 | 0.054932 | -0.27008 | -0.14648 | -0.11444 | 122.9233 | 122.9828 | 59.0836 | -122.9919 | 122.9599 | 122.8729 | 59.1476 | -123.111
66.5156 | 123.1018 | -59.0836 | 63.9175 | -0.52948 | 0.0030591 | 0.068654 | 0.066227 | 0.12977 | -0.0047146 | -0.0034287 | -0.019608 | 0.00036743 | -0.000391 | -0.0003226 | -0.00015383 | 0.00038454 | 63.8535 | 63.9862 | 0.041199 | -59.2575 | 63.7848 | -59.0881 | -59.1019 | -59.0607 | 0.091553 | -59.3536 | 63.8763 | 63.8077 | -59.1202 | -59.2117 | -0.004578 | -0.018311 | -0.13275 | 123.0698 | -0.17395 | -0.15564 | -0.064087 | -0.036621 | -0.12817 | -0.041199 | 0.022888 | -0.27008 | -0.14191 | -0.10986 | 122.8683 | 122.937 | 59.1248 | -123.0194 | 122.9599 | 122.8912 | 59.1751 | -123.1293
67.5156 | 123.1201 | -59.111 | 63.8992 | -0.16327 | 0.0060497 | 0.06844 | 0.06815 | 0.13084 | 0.0010532 | -0.00022432 | -0.065384 | 0.0016492 | -0.001459 | 0.0009592 | -0.00036743 | -0.0026063 | 63.8123 | 63.9359 | -0.036621 | -59.2941 | 63.826 | -59.0927 | -59.1248 | -59.0881 | 0.054932 | -59.3857 | 63.8809 | 63.8123 | -59.0927 | -59.2484 | 0.018311 | -0.013733 | -0.073242 | 123.0469 | -0.1831 | -0.16937 | -0.086975 | 0.018311 | -0.13733 | -0.018311 | 0.022888 | -0.27466 | -0.13733 | -0.086975 | 122.937 | 122.9233 | 59.0744 | -123.024 | 122.9919 | 122.9233 | 59.166 | -123.1476
68.5156 | 123.1659 | -59.0561 | 63.9038 | -0.17853 | 0.0032727 | 0.068868 | 0.067509 | 0.13148 | -0.0023648 | -0.0027877 | -0.042496 | -0.002837 | 3.6404e-05 | -0.000109 | -0.0012218 | -0.00025626 | 63.8809 | 64.0549 | 0.073242 | -59.2255 | 63.7894 | -59.0607 | -59.0881 | -59.0149 | 0.14648 | -59.3399 | 63.8351 | 63.7619 | -59.1156 | -59.2163 | -0.004578 | -0.032044 | -0.11444 | 123.111 | -0.16937 | -0.13733 | -0.022889 | -0.05951 | -0.16022 | -0.068665 | 0.041198 | -0.28381 | -0.1236 | -0.14191 | 122.8455 | 122.937 | 59.1293 | -122.9919 | 122.8912 | 122.818 | 59.2026 | -123.1201
69.5156 | 123.111 | -59.1064 | 63.8672 | -0.14038 | 0.0062635 | 0.067372 | 0.069432 | 0.13105 | 0.001694 | -0.0015061 | -0.11116 | -0.0026234 | -0.0006046 | 0.0001046 | 5.9768e-05 | -4.2662e-05 | 63.8306 | 63.9267 | -0.013733 | -59.2804 | 63.8397 | -59.0881 | -59.1248 | -59.0744 | 0.086975 | -59.3674 | 63.8992 | 63.8077 | -59.1064 | -59.2346 | 0.01831 | -0.018311 | -0.027465 | 123.0331 | -0.17395 | -0.15564 | -0.036621 | 0 | -0.12817 | 0.032044 | 0.032043 | -0.26093 | -0.13275 | -0.059509 | 122.9462 | 122.937 | 59.0927 | -122.9919 | 123.0057 | 122.9141 | 59.1934 | -123.1018
70.5156 | 123.1613 | -59.1019 | 63.9175 | -0.20142 | 0.0045545 | 0.067159 | 0.066655 | 0.13126 | -0.0034328 | -0.0030013 | -0.18745 | -0.0013416 | -0.000391 | -0.000109 | -0.00058103 | -0.0011109 | 63.8809 | 64.032 | 0.068665 | -59.3124 | 63.7756 | -59.1019 | -59.111 | -59.0378 | 0.11444 | -59.3216 | 63.8672 | 63.7848 | -59.0744 | -59.2117 | 0 | -0.009155 | -0.14191 | 123.1338 | -0.21057 | -0.20142 | -0.036622 | 0.027466 | -0.10986 | -0.050355 | 0.064087 | -0.21973 | -0.10986 | -0.13275 | 122.8775 | 122.9828 | 59.1705 | -123.0286 | 122.9691 | 122.8867 | 59.2163 | -123.1293
71.5156 | 123.1384 | -59.0927 | 63.913 | -0.17853 | 0.0049817 | 0.067159 | 0.068791 | 0.13212 | 0.00083955 | -0.0012923 | -0.12642 | -0.001128 | 0.0011044 | 0.0003182 | -0.00058103 | -0.0015381 | 63.8397 | 63.9267 | -0.036621 | -59.2896 | 63.8306 | -59.0881 | -59.111 | -59.0836 | 0.045776 | -59.3811 | 63.8901 | 63.7939 | -59.0973 | -59.2438 | 0.004577 | -0.018311 | -0.082398 | 123.0194 | -0.19684 | -0.17853 | -0.073242 | -0.004578 | -0.15106 | -0.022888 | 0.009155 | -0.28839 | -0.13733 | -0.11902 | 122.9233 | 122.9324 | 59.0561 | -123.024 | 122.9828 | 122.8867 | 59.1385 | -123.1567
72.5156 | 123.1888 | -59.0836 | 63.8672 | -0.19379 | 0.0041271 | 0.066731 | 0.069005 | 0.13319 | -0.002792 | -0.0047103 | -0.019608 | -0.0024096 | 3.6404e-05 | 0.0003182 | 0.00027337 | 0.00038454 | 63.9038 | 64.0732 | 0.091553 | -59.2255 | 63.8123 | -59.0744 | -59.0927 | -59.0057 | 0.15564 | -59.2941 | 63.8443 | 63.7573 | -59.0607 | -59.1888 | 0.009155 | -0.009155 | -0.054931 | 123.1567 | -0.14191 | -0.13275 | 0.036622 | 0.022888 | -0.10529 | -0.022888 | 0.07782 | -0.21057 | -0.10529 | -0.10986 | 122.8958 | 122.9874 | 59.1751 | -122.9599 | 122.9279 | 122.8409 | 59.2392 | -123.056
73.5156 | 123.1293 | -59.0927 | 63.9359 | -0.18616 | 0.0045545 | 0.067372 | 0.0658 | 0.13041 | 0.0014804 | -0.0012923 | -0.095902 | -0.00048697 | -0.0006046 | 0.0026682 | 0.00091437 | -0.00068366 | 63.8397 | 63.9679 | -0.022888 | -59.2896 | 63.8397 | -59.0973 | -59.1064 | -59.0652 | 0.059509 | -59.3857 | 63.8855 | 63.8077 | -59.0973 | -59.2392 | -0.004578 | -0.013733 | -0.09613 | 123.0606 | -0.19684 | -0.18311 | -0.09613 | -0.004578 | -0.14648 | -0.050354 | 0.027465 | -0.29297 | -0.14648 | -0.12817 | 122.9324 | 122.9324 | 59.0698 | -123.0423 | 122.9782 | 122.9004 | 59.1522 | -123.175
74.5156 | 123.2162 | -59.0515 | 63.8763 | -0.1709 | 0.0030591 | 0.0678 | 0.066655 | 0.12998 | -0.002792 | -0.00022432 | 0.0032804 | -0.00027337 | -0.001459 | 0.0003182 | -0.00058103 | -0.0021789 | 63.9221 | 64.0778 | 0.09613 | -59.2255 | 63.7894 | -59.0652 | -59.0973 | -58.9874 | 0.1831 | -59.2758 | 63.8443 | 63.7573 | -59.079 | -59.2026 | -0.013733 | -0.045776 | -0.086975 | 123.1293 | -0.17395 | -0.12817 | 0.045776 | -0.027465 | -0.15106 | -0.032044 | 0.064087 | -0.2243 | -0.073242 | -0.11902 | 122.8409 | 122.9736 | 59.1476 | -122.9736 | 122.8958 | 122.8088 | 59.2346 | -123.0789
75.5156 | 123.1155 | -59.079 | 63.9084 | -0.11749 | 0.0051953 | 0.065663 | 0.070714 | 0.13126 | 0.00041235 | -0.0034287 | -0.080643 | -0.0015552 | -0.000391 | -0.0005362 | 0.00048697 | -0.0019653 | 63.8397 | 63.9542 | -0.004578 | -59.2896 | 63.826 | -59.0881 | -59.0973 | -59.0698 | 0.054932 | -59.3719 | 63.8992 | 63.7802 | -59.079 | -59.2255 | -0.009156 | -0.018311 | -0.082397 | 123.0331 | -0.21057 | -0.19226 | -0.068664 | 0 | -0.14649 | -0.009155 | 0.009155 | -0.29297 | -0.14648 | -0.12817 | 122.905 | 122.9187 | 59.0744 | -123.0057 | 122.9782 | 122.8592 | 59.1339 | -123.1338
76.5156 | 123.2208 | -59.0607 | 63.8718 | -0.13275 | 0.0026319 | 0.068868 | 0.066014 | 0.1334 | -0.00044225 | -0.0017197 | -0.050125 | -0.0024096 | 0.0008908 | 0.0003182 | 0.0013416 | -4.2662e-05 | 63.913 | 64.0594 | 0.07782 | -59.2392 | 63.7756 | -59.079 | -59.1019 | -59.0057 | 0.15564 | -59.3079 | 63.8397 | 63.7665 | -59.0836 | -59.23 | -0.01831 | -0.041199 | -0.09613 | 123.1201 | -0.17853 | -0.13733 | 0.041199 | -0.022888 | -0.16937 | -0.032043 | 0.054932 | -0.24719 | -0.077819 | -0.10529 | 122.8363 | 122.9736 | 59.1385 | -122.9736 | 122.9004 | 122.8271 | 59.2163 | -123.1018
77.5156 | 123.143 | -59.1019 | 63.9175 | -0.17853 | 0.0036999 | 0.065236 | 0.067936 | 0.12913 | 0.0021214 | -0.0023605 | -0.13405 | -0.00070077 | 0.0006772 | 0.0011728 | 0.00048697 | -0.0032471 | 63.8351 | 63.9496 | -0.022888 | -59.3124 | 63.858 | -59.1019 | -59.1339 | -59.0836 | 0.036621 | -59.3857 | 63.8855 | 63.8077 | -59.1064 | -59.2438 | 0 | -0.032043 | -0.05951 | 123.0515 | -0.21057 | -0.17853 | -0.082398 | -0.004577 | -0.14191 | -0.032044 | 0.018311 | -0.28381 | -0.14191 | -0.10986 | 122.9599 | 122.937 | 59.079 | -123.0515 | 122.9874 | 122.9095 | 59.1385 | -123.1613
78.5156 | 123.1842 | -59.0607 | 63.8809 | -0.1709 | 0.00070931 | 0.066518 | 0.069005 | 0.13191 | -0.0032192 | -0.0017197 | -0.057755 | -0.002196 | 3.6404e-05 | -0.001177 | 0.001128 | -0.0011109 | 63.913 | 64.0778 | 0.10071 | -59.2255 | 63.7939 | -59.0698 | -59.0652 | -58.9783 | 0.16479 | -59.2941 | 63.8351 | 63.7573 | -59.0652 | -59.1751 | -0.009155 | -0.004578 | -0.086975 | 123.1384 | -0.1648 | -0.16022 | 0.032044 | -0.004578 | -0.11444 | -0.045776 | 0.082398 | -0.23346 | -0.11902 | -0.1236 | 122.8546 | 122.9736 | 59.1614 | -122.9462 | 122.8958 | 122.818 | 59.2255 | -123.056
79.5156 | 123.1293 | -59.0927 | 63.9267 | -0.18616 | 0.0047681 | 0.066304 | 0.069005 | 0.12977 | 0.0012668 | -0.0019333 | -0.11116 | -0.0015552 | 0.0021726 | -0.0007498 | 5.9768e-05 | -0.0030335 | 63.8351 | 63.9587 | -0.009155 | -59.2941 | 63.8535 | -59.111 | -59.1431 | -59.0652 | 0.059509 | -59.3811 | 63.9038 | 63.7894 | -59.0881 | -59.2255 | -0.018311 | -0.050354 | -0.073242 | 123.0515 | -0.20142 | -0.15106 | -0.091553 | 0.004577 | -0.13275 | -0.022888 | 0.027465 | -0.28839 | -0.15564 | -0.13733 | 122.9462 | 122.9279 | 59.0836 | -123.0698 | 122.9965 | 122.8821 | 59.1522 | -123.1522
80.5156 | 123.2162 | -59.0607 | 63.858 | -0.16327 | 0.0019909 | 0.068013 | 0.066655 | 0.13212 | -0.002792 | -0.00043792 | -0.042496 | -0.002837 | -0.0018862 | 0.0011728 | 0.00091437 | -0.0013245 | 63.9038 | 64.0961 | 0.091553 | -59.23 | 63.7802 | -59.0607 | -59.0881 | -58.9828 | 0.18768 | -59.2621 | 63.8489 | 63.7711 | -59.0607 | -59.1934 | 0 | -0.027466 | -0.07782 | 123.1567 | -0.16937 | -0.14191 | 0.045777 | 0 | -0.13275 | -0.009155 | 0.07782 | -0.20142 | -0.068665 | -0.086975 | 122.8409 | 122.9645 | 59.1522 | -122.9462 | 122.9095 | 122.8317 | 59.2484 | -123.0515
81.5156 | 123.1247 | -59.079 | 63.8901 | -0.1709 | 0.0054089 | 0.068013 | 0.069218 | 0.12806 | -1.505e-05 | -0.0015061 | -0.17983 | -0.00027337 | 0.0006772 | -0.0022452 | -0.00058103 | -0.0015381 | 63.8397 | 63.945 | -0.027466 | -59.285 | 63.8214 | -59.0881 | -59.1339 | -59.0744 | 0.068665 | -59.3765 | 63.8855 | 63.7939 | -59.0973 | -59.2026 | -0.009156 | -0.054932 | -0.068665 | 123.024 | -0.20599 | -0.15106 | -0.050354 | -0.018311 | -0.1236 | -0.004578 | 0.004577 | -0.29755 | -0.17395 | -0.096131 | 122.9004 | 122.9187 | 59.0515 | -123.024 | 122.9645 | 122.8729 | 59.1476 | -123.0927
82.5156 | 123.23 | -59.0744 | 63.8901 | -0.15564 | 0.0030591 | 0.066518 | 0.06815 | 0.12977 | -0.004501 | -0.0023605 | -0.019608 | -0.00091437 | 3.6404e-05 | -0.0016044 | 0.0015552 | -0.0026063 | 63.9038 | 64.0915 | 0.09613 | -59.2255 | 63.7985 | -59.0744 | -59.079 | -58.9783 | 0.19684 | -59.2621 | 63.8168 | 63.739 | -59.0561 | -59.1888 | 0 | -0.004577 | -0.091553 | 123.1659 | -0.15106 | -0.14649 | 0.013733 | 0.018311 | -0.11444 | -0.073243 | 0.096131 | -0.18768 | -0.073242 | -0.15106 | 122.8729 | 122.9782 | 59.1705 | -122.9691 | 122.8912 | 122.8134 | 59.2712 | -123.0789
83.5156 | 123.0881 | -59.111 | 63.913 | -0.16327 | 0.0079723 | 0.066518 | 0.069005 | 0.13041 | 0.0019078 | -0.00022432 | -0.1722 | -0.0019824 | 3.6404e-05 | -0.0005362 | 0.00027337 | -0.0038879 | 63.8351 | 63.9542 | -0.036621 | -59.2712 | 63.8351 | -59.1202 | -59.111 | -59.0698 | 0.050354 | -59.3857 | 63.8809 | 63.7985 | -59.0927 | -59.2209 | -0.009155 | 0 | -0.07782 | 123.0652 | -0.16022 | -0.16022 | -0.07782 | 0.018311 | -0.10986 | -0.032044 | 0.041199 | -0.27466 | -0.16479 | -0.11444 | 122.9462 | 122.9462 | 59.0744 | -123.024 | 122.9919 | 122.9095 | 59.1614 | -123.1338
84.5156 | 123.1888 | -59.0515 | 63.9038 | -0.15564 | 0.0047681 | 0.066091 | 0.067509 | 0.12827 | -0.0023648 | -0.0010787 | -0.088272 | -0.00027337 | -0.0016726 | 0.0003182 | 0.0026234 | -0.0023927 | 63.8947 | 64.0594 | 0.07782 | -59.2346 | 63.7939 | -59.0652 | -59.1064 | -59.0652 | 0.23804 | -59.2941 | 63.8718 | 63.7848 | -59.0561 | -59.2026 | -0.013733 | -0.054931 | -0.10986 | 123.111 | -0.18311 | -0.12817 | -0.009156 | -0.004577 | -0.15106 | -0.032044 | -0.013733 | -0.24261 | -0.091552 | -0.11902 | 122.8455 | 122.9462 | 59.1293 | -123.0103 | 122.9233 | 122.8363 | 59.2896 | -123.1064
85.5156 | 123.1293 | -59.1019 | 63.913 | -0.16327 | 0.0086133 | 0.066091 | 0.0705 | 0.12934 | 0.00083955 | -0.00065152 | -0.11116 | -0.00027337 | 0.00025 | -0.0007498 | 0.0017688 | -0.0017517 | 63.858 | 63.9587 | -0.022888 | -59.2896 | 63.8535 | -59.1019 | -59.1248 | -59.0652 | 0.045776 | -59.3903 | 63.8901 | 63.8077 | -59.0973 | -59.2117 | 0 | -0.022888 | -0.059509 | 123.0606 | -0.18768 | -0.1648 | -0.054932 | 0.004578 | -0.10986 | -0.022888 | 0.036621 | -0.28839 | -0.17853 | -0.10529 | 122.9553 | 122.9599 | 59.079 | -123.0377 | 122.9919 | 122.9095 | 59.1476 | -123.1247
86.5156 | 123.1659 | -59.0469 | 63.8901 | -0.16327 | 0.0011365 | 0.066731 | 0.067936 | 0.13062 | -0.0032192 | -0.0021469 | -0.33241 | -0.001128 | -0.0018862 | -0.001818 | 0.00027337 | -0.0015381 | 63.8992 | 64.0869 | 0.07782 | -59.2209 | 63.7985 | -59.0561 | -59.111 | -58.9966 | 0.13275 | -59.2987 | 63.8489 | 63.7527 | -59.0836 | -59.2255 | -0.009155 | -0.064087 | -0.091553 | 123.1338 | -0.17395 | -0.10986 | 0.009155 | -0.036621 | -0.17853 | -0.041199 | 0.050354 | -0.25177 | -0.073242 | -0.13733 | 122.8455 | 122.9462 | 59.1248 | -123.0011 | 122.8958 | 122.7997 | 59.1797 | -123.1155
87.5156 | 123.1247 | -59.0836 | 63.9084 | -0.20142 | 0.0062635 | 0.066731 | 0.06815 | 0.13233 | 0.0019078 | -0.00065152 | -0.11116 | 0.00036743 | -0.001459 | 0.000532 | -0.00015383 | -0.0032471 | 63.826 | 63.9404 | -0.027466 | -59.2804 | 63.858 | -59.0881 | -59.1248 | -59.0698 | 0.054932 | -59.3811 | 63.8901 | 63.8031 | -59.1064 | -59.2163 | -0.004578 | -0.041199 | -0.050354 | 123.024 | -0.19684 | -0.15564 | -0.082397 | -0.022888 | -0.13275 | -0.01831 | 0.013733 | -0.29755 | -0.16479 | -0.10529 | 122.9416 | 122.9095 | 59.0561 | -123.0331 | 122.9736 | 122.8867 | 59.1385 | -123.1247
88.5156 | 123.1201 | -59.1202 | 63.8306 | 0.16479 | 0.0092541 | 0.069081 | 0.069645 | 0.1302 | 0.0027622 | 0.00041648 | 0.20927 | -5.9768e-05 | 0.001959 | 0.0024546 | 0.001128 | -0.0011109 | 63.8123 | 63.8855 | -0.12817 | -59.3308 | 63.8077 | -59.1202 | -59.1385 | -59.0836 | -0.064087 | -59.4131 | 63.826 | 63.7573 | -59.1248 | -59.23 | 0 | -0.018311 | -0.022888 | 123.0057 | -0.21057 | -0.19226 | -0.01831 | -0.004578 | -0.10986 | -0.004577 | 0.036621 | -0.29297 | -0.18311 | -0.073242 | 122.9279 | 122.9324 | 58.992 | -122.9691 | 122.9462 | 122.8775 | 59.0561 | -123.0606
89.5156 | 123.111 | -59.1293 | 63.9175 | -0.18616 | 0.0062635 | 0.066518 | 0.070286 | 0.13276 | -0.00065585 | 0.00020288 | -0.11879 | -0.00027337 | 0.00025 | 0.0003182 | -0.0016492 | 0.00059814 | 63.8306 | 63.9404 | -0.022888 | -59.285 | 63.8168 | -59.1064 | -59.1293 | -59.0836 | 0.073242 | -59.3903 | 63.8809 | 63.8077 | -59.0836 | -59.23 | 0.022888 | 0 | -0.10071 | 123.0698 | -0.15564 | -0.15564 | -0.086976 | 0.045776 | -0.10071 | -0.036622 | 0.045776 | -0.26093 | -0.16022 | -0.10986 | 122.9462 | 122.9599 | 59.1064 | -123.0469 | 123.0103 | 122.937 | 59.2026 | -123.1476
90.5156 | 123.1247 | -59.079 | 63.913 | -0.20905 | 0.0028455 | 0.068654 | 0.067509 | 0.13062 | 0.00019875 | -0.00043792 | -0.073013 | 0.00036743 | -0.0021 | 0.0007456 | -0.0014356 | 0.00038454 | 63.8489 | 63.9862 | 0.013733 | -59.285 | 63.8214 | -59.0927 | -59.1202 | -59.0561 | 0.082397 | -59.3719 | 63.8947 | 63.7985 | -59.0973 | -59.2163 | -0.013733 | -0.041199 | -0.091553 | 123.0652 | -0.20599 | -0.16479 | -0.064087 | -0.018311 | -0.13733 | -0.018311 | 0.022888 | -0.29297 | -0.15564 | -0.11444 | 122.9004 | 122.9279 | 59.0927 | -123.0331 | 122.9736 | 122.8775 | 59.1614 | -123.1293
91.5156 | 123.1522 | -59.0836 | 63.8992 | -0.13275 | 0.0098951 | 0.065663 | 0.067296 | 0.13276 | 0.0031894 | -1.0724e-05 | 0.0032804 | -0.00070077 | 0.0004636 | 0.000532 | 0.0013416 | -0.0028199 | 63.8672 | 63.9816 | 0 | -59.2575 | 63.8168 | -59.1019 | -59.1339 | -59.0286 | 0.068665 | -59.3582 | 63.8718 | 63.7939 | -59.0881 | -59.2209 | -0.018311 | -0.050354 | -0.082398 | 123.0652 | -0.17395 | -0.1236 | -0.032044 | -0.004578 | -0.13733 | -0.027466 | 0.054932 | -0.27466 | -0.13733 | -0.10529 | 122.9004 | 122.9507 | 59.0836 | -123.0331 | 122.9553 | 122.8775 | 59.1522 | -123.1201
92.5156 | 123.1338 | -59.079 | 63.8901 | -0.20905 | 0.0036999 | 0.069295 | 0.070714 | 0.13212 | -0.0036464 | -0.0012923 | -0.042496 | -0.001128 | 3.6404e-05 | 0.0026682 | 0.00027337 | -0.0013245 | 63.8535 | 63.9908 | 0.018311 | -59.285 | 63.8168 | -59.079 | -59.111 | -59.0469 | 0.082397 | -59.3582 | 63.8672 | 63.8168 | -59.0927 | -59.198 | 0 | -0.032044 | -0.073243 | 123.0698 | -0.20599 | -0.17395 | -0.036621 | -0.013733 | -0.11902 | -0.022889 | 0.032043 | -0.27924 | -0.16022 | -0.073243 | 122.8958 | 122.9324 | 59.0973 | -123.0011 | 122.9462 | 122.8958 | 59.1614 | -123.0881
93.5156 | 123.1155 | -59.1431 | 63.8992 | 0.93536 | 0.0083997 | 0.065236 | 0.069645 | 0.12998 | 0.0019078 | -1.0724e-05 | 0.071945 | 0.0014356 | 3.6404e-05 | 0.0003182 | 0.0017688 | -0.0017517 | 63.8306 | 63.9587 | -0.045776 | -59.3033 | 63.8031 | -59.1156 | -59.1248 | -59.0698 | -0.018311 | -59.4269 | 63.8626 | 63.7482 | -59.111 | -59.2575 | 0.027465 | 0.01831 | -0.09613 | 123.1018 | -0.16022 | -0.17853 | -0.068665 | 0.032043 | -0.11444 | -0.036621 | 0.073242 | -0.28381 | -0.16937 | -0.15106 | 122.9462 | 122.9736 | 59.0973 | -123.024 | 123.0057 | 122.8912 | 59.1248 | -123.1567
94.5156 | 123.2208 | -59.0744 | 63.8992 | -0.16327 | 0.0030591 | 0.068227 | 0.067723 | 0.12785 | -0.0036464 | -0.0019333 | -0.019608 | -0.0013416 | -0.0016726 | -0.0007498 | -0.0018628 | -0.0013245 | 63.8947 | 64.0594 | 0.09613 | -59.23 | 63.7894 | -59.0744 | -59.0973 | -59.0378 | 0.13733 | -59.2896 | 63.8168 | 63.7711 | -59.0652 | -59.2072 | 0 | -0.022888 | -0.10986 | 123.1338 | -0.15564 | -0.13275 | -0.004578 | 0.009155 | -0.13275 | -0.082398 | 0.036621 | -0.21515 | -0.082398 | -0.12817 | 122.8638 | 122.9691 | 59.1705 | -122.9965 | 122.8912 | 122.8455 | 59.2117 | -123.1064
95.5156 | 123.1567 | -59.0881 | 63.9084 | -0.14801 | 0.0071179 | 0.066945 | 0.070714 | 0.13084 | 0.0014804 | -0.0012923 | -0.11116 | 0.00058103 | 0.0028134 | -0.0022452 | -0.0010082 | -0.0011109 | 63.8397 | 63.9313 | -0.018311 | -59.2804 | 63.826 | -59.1019 | -59.111 | -59.0195 | 0.004578 | -59.2804 | 63.9084 | 63.8168 | -59.0927 | -59.2072 | -0.013733 | -0.022888 | -0.082397 | 123.0194 | -0.19226 | -0.16937 | -0.068664 | -0.004577 | -0.11902 | 0 | 0.068665 | -0.19226 | -0.073243 | -0.091553 | 122.9141 | 122.9279 | 59.0698 | -123.0194 | 122.9965 | 122.905 | 59.0927 | -123.1155
96.5156 | 123.1384 | -59.0973 | 63.913 | -0.17853 | 0.0047681 | 0.0678 | 0.066441 | 0.13404 | -0.0023648 | -0.00043792 | -0.13405 | -0.00070077 | -0.0006046 | 0.0001046 | -0.00036743 | -0.0021789 | 63.826 | 63.9496 | -0.018311 | -59.2804 | 63.8168 | -59.0973 | -59.1156 | -59.079 | 0.054932 | -59.3857 | 63.8901 | 63.8077 | -59.1019 | -59.2163 | 0 | -0.018311 | -0.096131 | 123.0469 | -0.18311 | -0.1648 | -0.086975 | -0.004578 | -0.11902 | -0.022888 | 0.018311 | -0.28839 | -0.16937 | -0.10529 | 122.9141 | 122.9233 | 59.079 | -123.0286 | 122.9874 | 122.905 | 59.1522 | -123.1293
97.5156 | 123.0927 | -59.1248 | 63.8214 | 0.027466 | 0.0092541 | 0.0678 | 0.06815 | 0.13191 | 0.003403 | -0.00086512 | 0.041427 | -0.0017688 | 3.6404e-05 | -0.0013906 | 0.00027337 | -0.0021789 | 63.8306 | 63.9404 | -0.059509 | -59.2804 | 63.8214 | -59.1019 | -59.1293 | -59.079 | -0.004578 | -59.4223 | 63.858 | 63.7894 | -59.1019 | -59.2575 | 0.022888 | -0.004577 | 0 | 123.0652 | -0.15564 | -0.15106 | 0.009155 | 0.022888 | -0.13275 | 0.036621 | 0.045777 | -0.29755 | -0.1648 | -0.032043 | 122.9462 | 122.9553 | 59.0652 | -122.9507 | 122.9828 | 122.9141 | 59.1202 | -123.0789
98.5156 | 123.2346 | -59.0881 | 63.8168 | 0.073242 | 0.0060497 | 0.066518 | 0.062169 | 0.13255 | -0.0021512 | -0.00065152 | 0.33897 | -0.0013416 | 3.6404e-05 | 0.0011728 | 0.0013416 | -0.00047006 | 63.8855 | 63.9999 | -0.022888 | -59.2392 | 63.7619 | -59.0836 | -59.1293 | -58.9966 | 0.027466 | -59.3079 | 63.7939 | 63.7024 | -59.0973 | -59.23 | 0.004578 | -0.041198 | -0.054931 | 123.0881 | -0.15106 | -0.10986 | 0.068665 | -0.009155 | -0.14191 | -0.022888 | 0.091553 | -0.21973 | -0.077819 | -0.11444 | 122.85 | 122.9736 | 59.0652 | -122.9462 | 122.8821 | 122.7905 | 59.1156 | -123.0469
99.5156 | 123.1522 | -59.0927 | 63.8855 | -0.14038 | 0.0088269 | 0.066945 | 0.070073 | 0.13233 | 0.0021214 | -0.00022432 | -0.057755 | 0.00058103 | 0.001959 | 0.0030954 | -0.0014356 | -0.0015381 | 63.8763 | 63.9496 | -0.009155 | -59.2575 | 63.8306 | -59.1156 | -59.1293 | -58.905 | 0.018311 | -59.2804 | 63.8855 | 63.8168 | -59.0607 | -59.2392 | -0.022889 | -0.036621 | -0.054932 | 123.0423 | -0.16479 | -0.12817 | -0.009155 | 0.032043 | -0.14648 | 0 | 0.18768 | -0.18768 | -0.041199 | -0.068665 | 122.9233 | 122.9691 | 59.0836 | -123.0148 | 122.9782 | 122.9095 | 59.111 | -123.1247
100.5156 | 123.143 | -59.0973 | 63.9038 | 0.95062 | 0.0047681 | 0.066091 | 0.068791 | 0.13169 | -0.0019376 | -0.0021469 | -0.11116 | 0.00015383 | 0.0008908 | 0.0016 | 0.0017688 | -0.0026063 | 63.8168 | 63.9496 | -0.018311 | -59.2941 | 63.8397 | -59.1064 | -59.0881 | -59.0881 | 0.054932 | -59.3674 | 63.8855 | 63.8306 | -59.0881 | -59.23 | -0.009155 | 0.009155 | -0.064087 | 123.0469 | -0.19684 | -0.20599 | -0.086976 | 0.009155 | -0.13275 | -0.018311 | 0.009155 | -0.27008 | -0.13733 | -0.073243 | 122.937 | 122.9141 | 59.079 | -122.9919 | 122.9828 | 122.9279 | 59.1522 | -123.1339
101.5156 | 123.1842 | -59.0973 | 63.8901 | -0.1709 | 0.0090405 | 0.065663 | 0.068577 | 0.13319 | 0.00062595 | -0.00086512 | -0.042496 | 0.00058103 | 0.001318 | 0.0009592 | 0.0015552 | -0.0028199 | 63.858 | 63.9725 | -0.018311 | -59.2529 | 63.8397 | -59.111 | -59.1202 | -59.0378 | 0.091553 | -59.3536 | 63.8901 | 63.8031 | -59.0881 | -59.23 | -0.013733 | -0.022888 | -0.050354 | 123.0698 | -0.15564 | -0.13275 | -0.032044 | 0.009155 | -0.13275 | 0 | 0.059509 | -0.25635 | -0.1236 | -0.086975 | 122.937 | 122.9553 | 59.079 | -123.0103 | 122.9874 | 122.9004 | 59.1888 | -123.1201
102.5156 | 123.1201 | -59.0744 | 63.913 | -0.15564 | 0.0056225 | 0.066731 | 0.069218 | 0.13169 | -0.0012966 | -0.00086512 | -0.088272 | 0.00079463 | 3.6404e-05 | 0.0007456 | -0.00015383 | -0.00047006 | 63.8214 | 63.9404 | -0.082397 | -59.0927 | 63.8763 | -59.0607 | -59.0927 | -59.0881 | 0.050354 | -59.3582 | 63.8809 | 63.8123 | -59.1202 | -59.2163 | 0.013733 | -0.01831 | -0.036621 | 123.0148 | -0.01831 | 0 | -0.091553 | -0.045776 | -0.14191 | -0.032044 | -0.013733 | -0.28381 | -0.14191 | -0.10071 | 122.9507 | 122.8958 | 58.992 | -123.0057 | 122.9553 | 122.8867 | 59.1248 | -123.1293
103.5156 | 123.2483 | -59.0973 | 63.826 | 0.32501 | 0.0075451 | 0.065663 | 0.067296 | 0.13041 | -0.0023648 | -0.0027877 | 0.33897 | -0.0034778 | 0.001318 | -0.0022452 | 0.0015552 | -0.0030335 | 63.8763 | 64.0091 | -0.022888 | -59.2484 | 63.7344 | -59.0744 | -59.1156 | -58.992 | 0.045776 | -59.2987 | 63.8077 | 63.7253 | -59.1019 | -59.2255 | 0.022888 | -0.018311 | -0.091553 | 123.1064 | -0.15106 | -0.13275 | 0.050354 | -0.004578 | -0.12817 | -0.018311 | 0.10529 | -0.20142 | -0.073242 | -0.10071 | 122.8317 | 122.9736 | 59.0744 | -122.9416 | 122.905 | 122.8226 | 59.1431 | -123.0515
104.5156 | 123.1338 | -59.0973 | 63.913 | -0.15564 | 0.0051953 | 0.066945 | 0.068577 | 0.13169 | 0.00041235 | -0.0032151 | -0.065384 | -0.00048697 | 0.0017454 | -0.001818 | -0.0012218 | -0.0038879 | 63.8351 | 63.9267 | -0.018311 | -59.2804 | 63.8672 | -59.0927 | -59.1248 | -59.079 | 0.045776 | -59.3719 | 63.9084 | 63.8214 | -59.1019 | -59.2255 | 0.004578 | -0.027466 | -0.045777 | 123.024 | -0.18311 | -0.15564 | -0.07782 | -0.004578 | -0.12817 | -0.004578 | 0.018311 | -0.27466 | -0.14648 | -0.091553 | 122.9645 | 122.9324 | 59.079 | -123.0377 | 123.0057 | 122.9187 | 59.1431 | -123.1384
105.5156 | 123.1018 | -59.1019 | 63.8626 | -0.018311 | 0.010963 | 0.064809 | 0.0705 | 0.13084 | 0.001694 | -0.0023605 | 0.033798 | -0.0017688 | 0.0004636 | 0.000532 | -0.00015383 | -0.0013245 | 63.8855 | 63.9542 | -0.036621 | -59.285 | 63.8123 | -59.0881 | -59.1248 | -59.0424 | 0.018311 | -59.3857 | 63.8672 | 63.7848 | -59.0973 | -59.2255 | 0.013733 | -0.022888 | -0.050354 | 123.056 | -0.1831 | -0.16022 | 0.022888 | 0.004578 | -0.1236 | 0.004577 | 0.05951 | -0.28381 | -0.16022 | -0.07782 | 122.9141 | 122.9874 | 59.0652 | -122.9874 | 122.9691 | 122.8867 | 59.1202 | -123.0881
106.5156 | 123.1384 | -59.0836 | 63.913 | -0.2243 | 0.0069043 | 0.068227 | 0.06815 | 0.13191 | -0.00044225 | -0.0017197 | -0.095902 | 0.00015383 | -0.000391 | -0.000109 | 0.00027337 | -0.00068366 | 63.8351 | 63.9267 | -0.018311 | -59.2941 | 63.8123 | -59.0973 | -59.1293 | -59.079 | 0.059509 | -59.3719 | 63.9038 | 63.826 | -59.111 | -59.2117 | -0.013733 | -0.045776 | -0.10071 | 123.0103 | -0.21057 | -0.16479 | -0.07782 | -0.027466 | -0.12817 | -0.009155 | 0.004578 | -0.28839 | -0.16022 | -0.086975 | 122.8958 | 122.9187 | 59.0652 | -123.0423 | 122.9874 | 122.9095 | 59.1431 | -123.1247
107.5156 | 123.1522 | -59.111 | 63.9038 | -0.13275 | 0.0092541 | 0.065236 | 0.068577 | 0.13148 | 0.0025486 | -1.0724e-05 | -0.042496 | 0.0029308 | 0.00025 | 0.0001046 | 0.0019824 | -0.0017517 | 63.8626 | 63.9771 | 0 | -59.2575 | 63.8077 | -59.1156 | -59.1202 | -59.0332 | 0.073242 | -59.4543 | 63.8214 | 63.7482 | -59.1202 | -59.2758 | -0.004578 | -0.009155 | -0.096131 | 123.0881 | -0.14648 | -0.13733 | -0.041199 | -0.009155 | -0.16479 | -0.082398 | 0.07782 | -0.34332 | -0.17853 | -0.15564 | 122.9187 | 122.9736 | 59.111 | -123.024 | 122.9324 | 122.8592 | 59.1843 | -123.1796
108.5156 | 123.1293 | -59.1019 | 63.9313 | -0.21667 | 0.0051953 | 0.067586 | 0.066655 | 0.13319 | -0.0012966 | -0.0012923 | 0.0032804 | -0.001128 | -0.0001774 | 0.0009592 | -0.0027172 | 0.00038454 | 63.8306 | 63.9633 | 0.018311 | -59.2758 | 63.8123 | -59.0973 | -59.111 | -59.0836 | 0.073242 | -59.3491 | 63.8901 | 63.8031 | -59.1156 | -59.2072 | 0.004578 | -0.009155 | -0.11902 | 123.0652 | -0.17395 | -0.16479 | -0.10071 | -0.013733 | -0.10528 | -0.041198 | 0.018311 | -0.24719 | -0.14191 | -0.12817 | 122.9141 | 122.9324 | 59.1202 | -123.0423 | 122.9919 | 122.905 | 59.1751 | -123.1384
109.5156 | 123.0652 | -59.1064 | 63.8718 | -0.086975 | 0.0069043 | 0.066945 | 0.069005 | 0.12956 | 0.0014804 | -0.0019333 | -0.019608 | -0.00091437 | 3.6404e-05 | 0.0009592 | 0.0015552 | -0.0017517 | 63.8672 | 63.9771 | -0.009155 | -59.2621 | 63.8397 | -59.1064 | -59.111 | -59.0469 | 0.073242 | -59.3491 | 63.858 | 63.8031 | -59.0744 | -59.2163 | 0 | -0.004578 | -0.032043 | 123.0835 | -0.15564 | -0.15106 | -0.004578 | 0.032043 | -0.10986 | -0.013733 | 0.059509 | -0.24262 | -0.13275 | -0.068664 | 122.9462 | 122.9736 | 59.0973 | -122.9828 | 122.9645 | 122.9095 | 59.1797 | -123.0881
110.5156 | 123.1247 | -59.0881 | 63.9267 | -0.15564 | 0.0060497 | 0.067372 | 0.069432 | 0.13126 | -0.0017238 | -0.0015061 | -0.11879 | 0.0010082 | -0.0006046 | 0.0016 | 0.00048697 | 0.00059814 | 63.8351 | 63.9221 | -0.036621 | -59.2758 | 63.8397 | -59.1064 | -59.1019 | -59.0744 | 0.068665 | -59.3674 | 63.8809 | 63.8397 | -59.0744 | -59.2163 | -0.01831 | -0.013733 | -0.086975 | 123.0103 | -0.18768 | -0.17395 | -0.091553 | 0.013733 | -0.12817 | -0.045777 | 0.013733 | -0.27924 | -0.15106 | -0.086975 | 122.9279 | 122.9233 | 59.0515 | -123.0286 | 122.9691 | 122.9279 | 59.1568 | -123.143
111.5156 | 123.1476 | -59.0836 | 63.8626 | -0.37689 | 0.0079723 | 0.062245 | 0.068577 | 0.1302 | 0.0038304 | -0.00022432 | 0.01091 | -0.00070077 | 0.0011044 | 0.000532 | 0.0015552 | -0.0019653 | 63.8855 | 63.9679 | 0 | -59.2575 | 63.7939 | -59.1156 | -59.1064 | -59.0286 | 0.050354 | -59.3628 | 63.858 | 63.7848 | -59.0744 | -59.2438 | -0.032044 | -0.022888 | -0.068665 | 123.0515 | -0.17395 | -0.15106 | 0.022888 | 0.009155 | -0.16022 | -0.004578 | 0.054932 | -0.27924 | -0.11902 | -0.07782 | 122.8775 | 122.9691 | 59.0836 | -122.9691 | 122.9416 | 122.8683 | 59.1339 | -123.1064
112.5156 | 123.1338 | -59.0927 | 63.8901 | -0.1709 | 0.0096813 | 0.067372 | 0.067509 | 0.13297 | -0.00065585 | -0.0010787 | -0.12642 | -0.00048697 | 0.0008908 | 0.0001046 | 5.9768e-05 | -0.00047006 | 63.8351 | 63.9267 | -0.022888 | -59.2758 | 63.826 | -59.1202 | -59.1431 | -59.079 | 0.073242 | -59.3719 | 63.9038 | 63.8077 | -59.0973 | -59.2255 | -0.027466 | -0.050354 | -0.064087 | 123.0194 | -0.18311 | -0.13275 | -0.054932 | -0.004578 | -0.13275 | 0.013733 | 0.013733 | -0.27924 | -0.14648 | -0.082398 | 122.9187 | 122.9279 | 59.0698 | -123.0331 | 122.9965 | 122.9004 | 59.166 | -123.1155
113.5156 | 123.1659 | -59.111 | 63.8718 | 0.25635 | 0.010322 | 0.063527 | 0.066868 | 0.13148 | 0.0014804 | 0.0014847 | 0.033798 | 0.00058103 | -0.0012454 | -0.000109 | 0.001128 | -0.0015381 | 63.8763 | 63.9542 | 0.004578 | -59.2667 | 63.8031 | -59.1019 | -59.1064 | -59.0424 | 0.045776 | -59.3628 | 63.8351 | 63.7802 | -59.0881 | -59.2346 | 0.009155 | 0.004578 | -0.068664 | 123.0652 | -0.15564 | -0.16022 | 0.004578 | 0.022888 | -0.1236 | -0.036621 | 0.068665 | -0.25177 | -0.12817 | -0.091553 | 122.9141 | 122.9874 | 59.1156 | -122.9782 | 122.9462 | 122.8912 | 59.1568 | -123.1064
114.5156 | 123.1384 | -59.0744 | 63.8947 | -0.12512 | 0.0060497 | 0.068013 | 0.066441 | 0.13169 | -0.00086945 | -0.0019333 | -0.080643 | -5.9768e-05 | -0.0001774 | -0.0016044 | 0.00091437 | -0.0013245 | 63.8443 | 63.9267 | -0.045776 | -59.285 | 63.8443 | -59.1019 | -59.1248 | -59.0744 | 0.059509 | -59.3857 | 63.8763 | 63.858 | -59.0881 | -59.2117 | -0.027466 | -0.050354 | -0.050354 | 123.0011 | -0.21057 | -0.16022 | -0.050354 | -0.013733 | -0.13733 | -0.01831 | 0 | -0.31128 | -0.17395 | -0.036621 | 122.9187 | 122.9187 | 59.0286 | -123.0194 | 122.9507 | 122.9324 | 59.1339 | -123.1064
115.5156 | 123.1476 | -59.0973 | 63.8626 | 0.027466 | 0.010536 | 0.066518 | 0.070286 | 0.13169 | 0.0031894 | -0.00043792 | 0.11009 | -0.00048697 | 0.0004636 | -0.001177 | 0.0030506 | -0.0038879 | 63.8672 | 63.945 | -0.041199 | -59.285 | 63.8168 | -59.0973 | -59.1156 | -59.079 | -0.009155 | -59.3903 | 63.8351 | 63.7939 | -59.1019 | -59.2255 | 0 | -0.018311 | -0.045777 | 123.0423 | -0.18768 | -0.16937 | 0.004577 | -0.004578 | -0.12817 | -0.027466 | 0.018311 | -0.29297 | -0.16479 | -0.068665 | 122.9141 | 122.9645 | 59.0561 | -122.9782 | 122.9324 | 122.8912 | 59.0881 | -123.0881
116.5156 | 123.1567 | -59.1156 | 63.9084 | -0.16327 | 0.0077587 | 0.065236 | 0.069005 | 0.1302 | -0.0017238 | -0.0025741 | -0.088272 | -0.00048697 | 0.0011044 | 0.0009592 | -0.00036743 | -0.0013245 | 63.826 | 63.9175 | -0.036621 | -59.285 | 63.826 | -59.1156 | -59.0973 | -59.079 | 0.064087 | -59.3811 | 63.8992 | 63.8306 | -59.0836 | -59.2163 | 0 | 0.018311 | -0.082397 | 123.0331 | -0.16937 | -0.18768 | -0.082397 | 0.032044 | -0.10071 | -0.009155 | 0.036622 | -0.2655 | -0.16479 | -0.07782 | 122.9416 | 122.9416 | 59.079 | -123.0057 | 123.0148 | 122.9462 | 59.1797 | -123.1247
117.5156 | 123.1522 | -59.1202 | 63.8901 | -0.0030518 | 0.011818 | 0.066945 | 0.0705 | 0.13084 | 0.00083955 | -0.0012923 | 0.11772 | 0.0014356 | 0.0043088 | -0.0007498 | 0.001128 | -0.00089726 | 63.858 | 63.9496 | -0.045776 | -59.2896 | 63.8077 | -59.1019 | -59.1019 | -59.0698 | 0.027466 | -59.3857 | 63.8626 | 63.7939 | -59.1202 | -59.2346 | 0.01831 | 0.01831 | -0.082398 | 123.0698 | -0.16937 | -0.18768 | -0.032044 | 0 | -0.11444 | -0.027466 | 0.050354 | -0.2655 | -0.15106 | -0.096131 | 122.9279 | 122.9782 | 59.0744 | -122.9919 | 122.9828 | 122.9141 | 59.1476 | -123.1247
118.5156 | 123.1567 | -59.0836 | 63.8718 | -0.10986 | 0.0075451 | 0.066304 | 0.06815 | 0.13062 | -0.001083 | -0.0019333 | -0.088272 | -0.00091437 | 0.0017454 | -0.0003226 | 0.00048697 | -0.0019653 | 63.8535 | 63.9587 | 0.004578 | -59.2621 | 63.8443 | -59.1019 | -59.0927 | -59.0469 | 0.082397 | -59.3353 | 63.8626 | 63.8123 | -59.1019 | -59.23 | -0.018311 | -0.009155 | -0.027466 | 123.0423 | -0.17853 | -0.16937 | -0.01831 | -0.018311 | -0.14648 | -0.009155 | 0.036621 | -0.25177 | -0.10529 | -0.059509 | 122.9279 | 122.937 | 59.0881 | -122.9645 | 122.9462 | 122.8958 | 59.166 | -123.1018
119.5156 | 123.1338 | -59.1019 | 63.8947 | 0.027466 | 0.010536 | 0.065236 | 0.067509 | 0.13212 | 0.0012668 | -0.00065152 | 0.079574 | -0.00091437 | 0.0017454 | 0.0003182 | 5.9768e-05 | -0.0036743 | 63.8763 | 63.9359 | -0.036621 | -59.2621 | 63.7939 | -59.111 | -59.1522 | -59.0652 | 0.027466 | -59.3719 | 63.8672 | 63.7985 | -59.1019 | -59.2392 | -0.009155 | -0.050354 | -0.10071 | 123.0377 | -0.16022 | -0.10986 | -0.01831 | 0 | -0.13733 | -0.027466 | 0.036621 | -0.27008 | -0.13275 | -0.09613 | 122.8958 | 122.9782 | 59.0652 | -123.0469 | 122.9691 | 122.9004 | 59.1293 | -123.1338
120.5156 | 123.1522 | -59.0927 | 63.913 | -0.14801 | 0.0054089 | 0.0678 | 0.068364 | 0.13148 | 0.0012668 | -0.0021469 | -0.11879 | 0.0016492 | 0.001318 | 0.0013864 | 0.0026234 | -0.0026063 | 63.8443 | 63.9496 | -0.032043 | -59.2621 | 63.8306 | -59.111 | -59.1156 | -59.0652 | 0.086975 | -59.3491 | 63.8809 | 63.826 | -59.0744 | -59.1843 | -0.018311 | -0.022889 | -0.082398 | 123.0423 | -0.16937 | -0.14648 | -0.068665 | 0.01831 | -0.091553 | -0.032044 | 0.027465 | -0.25635 | -0.16479 | -0.086975 | 122.9233 | 122.937 | 59.0607 | -123.0286 | 122.9736 | 122.9187 | 59.1797 | -123.0972
121.5156 | 123.1338 | -59.0973 | 63.8672 | -0.02594 | 0.0092541 | 0.064809 | 0.068791 | 0.12913 | 0.001694 | -0.0012923 | 0.079574 | -0.00027337 | 0.0011044 | 0.0007456 | 0.00091437 | -4.2662e-05 | 63.8672 | 63.9679 | -0.032043 | -59.285 | 63.7894 | -59.0744 | -59.1202 | -59.0698 | 0.041199 | -59.3811 | 63.858 | 63.7894 | -59.0973 | -59.2667 | 0.022888 | -0.022888 | -0.077819 | 123.0652 | -0.18768 | -0.16479 | 0 | 0 | -0.16937 | -0.009155 | 0.027466 | -0.28381 | -0.11444 | -0.077819 | 122.8867 | 122.9645 | 59.0652 | -122.9874 | 122.9553 | 122.8867 | 59.1385 | -123.1338
122.5156 | 123.1201 | -59.0927 | 63.913 | -0.3006 | 0.0083997 | 0.067159 | 0.066868 | 0.13169 | -0.0015102 | -0.0036423 | -0.042496 | -0.0013416 | -0.0016726 | 0.0003182 | -0.00036743 | -0.0011109 | 63.8168 | 63.9313 | -0.022888 | -59.285 | 63.8351 | -59.0927 | -59.1431 | -59.0836 | 0.041199 | -59.3857 | 63.913 | 63.8397 | -59.0881 | -59.2117 | 0 | -0.050354 | -0.07782 | 123.024 | -0.19226 | -0.14191 | -0.096131 | 0.004577 | -0.11902 | 0 | 0.009155 | -0.29297 | -0.17395 | -0.073242 | 122.9279 | 122.9095 | 59.0698 | -123.056 | 123.0057 | 122.9324 | 59.1339 | -123.1247
123.5156 | 123.175 | -59.0973 | 63.8901 | -0.033569 | 0.0081861 | 0.065877 | 0.069645 | 0.13126 | 0.0019078 | -0.00043792 | 0.079574 | -0.00027337 | 0.0028134 | -0.000109 | 0.00070077 | -0.0032471 | 63.8718 | 63.9679 | -0.018311 | -59.2712 | 63.7894 | -59.0744 | -59.1202 | -59.0286 | 0.054932 | -59.3628 | 63.8397 | 63.8031 | -59.0973 | -59.2529 | 0.022888 | -0.022888 | -0.10071 | 123.0652 | -0.17395 | -0.15106 | -0.018311 | 0 | -0.15564 | -0.050354 | 0.068665 | -0.2655 | -0.10986 | -0.086975 | 122.8867 | 122.9691 | 59.079 | -123.0103 | 122.937 | 122.9004 | 59.1522 | -123.143
124.5156 | 123.1522 | -59.1064 | 63.8947 | -0.20142 | 0.0086133 | 0.0678 | 0.067509 | 0.13255 | -1.505e-05 | -0.00022432 | -0.095902 | -0.001128 | 3.6404e-05 | -0.0016044 | 0.00070077 | -0.0021789 | 63.8535 | 63.945 | -0.013733 | -59.2575 | 63.8306 | -59.111 | -59.1339 | -59.0652 | 0.091553 | -59.3399 | 63.8947 | 63.8077 | -59.0836 | -59.23 | -0.004578 | -0.027466 | -0.064087 | 123.0515 | -0.15106 | -0.1236 | -0.041198 | 0.022888 | -0.1236 | 0 | 0.041198 | -0.23346 | -0.10986 | -0.086975 | 122.937 | 122.9599 | 59.0927 | -123.0286 | 123.0011 | 122.9141 | 59.198 | -123.1247
125.5156 | 123.111 | -59.0927 | 63.8763 | -0.018311 | 0.0092541 | 0.066091 | 0.06815 | 0.13084 | 0.00083955 | 0.00020288 | 0.087204 | -0.00070077 | 0.0006772 | -0.000109 | 0.0017688 | -0.0023927 | 63.8626 | 63.9359 | -0.027466 | -59.2896 | 63.7985 | -59.1019 | -59.1202 | -59.0652 | 0.036621 | -59.3765 | 63.858 | 63.7985 | -59.1202 | -59.23 | -0.009156 | -0.027466 | -0.07782 | 123.0286 | -0.19684 | -0.16937 | -0.013733 | -0.027466 | -0.13733 | -0.018311 | 0.027465 | -0.28381 | -0.14648 | -0.07782 | 122.8912 | 122.9553 | 59.0652 | -122.9965 | 122.9507 | 122.8912 | 59.1293 | -123.1064
126.5156 | 123.175 | -59.1019 | 63.8992 | -0.16327 | 0.0054089 | 0.06545 | 0.069218 | 0.13255 | -0.00086945 | -0.0015061 | -0.080643 | -0.002196 | 0.0008908 | 0.0009592 | 0.00048697 | -0.00047006 | 63.8306 | 63.9404 | -0.027466 | -59.2712 | 63.8306 | -59.0881 | -59.1202 | -59.0652 | 0.068665 | -59.3628 | 63.8947 | 63.8489 | -59.0881 | -59.2209 | 0.013733 | -0.01831 | -0.068665 | 123.0423 | -0.16937 | -0.15106 | -0.068665 | 0.013733 | -0.11902 | -0.004578 | 0.036621 | -0.26093 | -0.14191 | -0.050354 | 122.9324 | 122.9324 | 59.0744 | -123.0194 | 122.9965 | 122.9507 | 59.1705 | -123.1201
127.5156 | 123.1338 | -59.1019 | 63.8672 | -0.018311 | 0.012672 | 0.064809 | 0.068577 | 0.13084 | 0.002335 | -0.00043792 | 0.079574 | 0.0010082 | 0.001959 | -0.0016044 | 0.0015552 | -0.0032471 | 63.8901 | 63.9679 | -0.009155 | -59.2712 | 63.8306 | -59.0973 | -59.1156 | -59.0515 | 0.064087 | -59.3536 | 63.858 | 63.7802 | -59.0881 | -59.2255 | 0.004578 | -0.013733 | -0.036621 | 123.0698 | -0.16937 | -0.15564 | 0.022889 | 0.013733 | -0.1236 | -0.009155 | 0.050354 | -0.25177 | -0.12817 | -0.086975 | 122.9324 | 122.9919 | 59.0927 | -122.9828 | 122.9599 | 122.8821 | 59.166 | -123.0927
128.5156 | 123.1155 | -59.1064 | 63.8992 | -0.17853 | 0.0056225 | 0.066945 | 0.069432 | 0.13148 | -0.00086945 | -0.0040695 | -0.050125 | 0.00079463 | 0.0006772 | -0.0005362 | 0.00048697 | -0.0013245 | 63.8123 | 63.9267 | -0.018311 | -59.285 | 63.8351 | -59.1156 | -59.1156 | -59.0836 | 0.059509 | -59.3719 | 63.8947 | 63.8397 | -59.0973 | -59.2163 | -0.009156 | -0.009156 | -0.064087 | 123.0331 | -0.17853 | -0.16937 | -0.086975 | 0.009155 | -0.10986 | -0.004578 | 0.022888 | -0.2655 | -0.15564 | -0.059509 | 122.9416 | 122.9187 | 59.0881 | -123.0148 | 123.0011 | 122.9462 | 59.166 | -123.1155
129.5156 | 123.1293 | -59.111 | 63.9084 | -0.11749 | 0.0081861 | 0.0678 | 0.071141 | 0.13148 | -0.00086945 | -0.0019333 | -0.095902 | -0.001128 | 0.0040952 | -0.0016044 | -0.0010082 | -0.00068366 | 63.8214 | 63.9359 | -0.036621 | -59.2804 | 63.8214 | -59.1019 | -59.1202 | -59.0744 | 0.068665 | -59.3491 | 63.8809 | 63.8031 | -59.1293 | -59.2255 | 0.009155 | -0.009155 | -0.086975 | 123.0469 | -0.16937 | -0.16022 | -0.086975 | -0.01831 | -0.11444 | -0.027466 | 0.036621 | -0.23804 | -0.1236 | -0.10529 | 122.9324 | 122.9324 | 59.0744 | -123.0286 | 122.9919 | 122.9141 | 59.1797 | -123.1338
130.5156 | 123.1201 | -59.0836 | 63.8992 | -0.20905 | 0.0049817 | 0.066731 | 0.064946 | 0.12977 | -0.0012966 | -0.0025741 | -0.019608 | 0.00015383 | 0.0011044 | -0.0016044 | 0.0017688 | 0.00038454 | 63.826 | 63.9038 | -0.032043 | -59.2987 | 63.826 | -59.0927 | -59.1339 | -59.0744 | 0.054932 | -59.3765 | 63.8809 | 63.8443 | -59.1064 | -59.1934 | -0.009155 | -0.050354 | -0.073242 | 122.9874 | -0.21515 | -0.1648 | -0.073242 | -0.022888 | -0.10986 | -0.018311 | 0.009155 | -0.29297 | -0.18311 | -0.054932 | 122.9095 | 122.9095 | 59.0515 | -123.0331 | 122.9645 | 122.9279 | 59.1385 | -123.0927
131.5156 | 123.1842 | -59.0652 | 63.8947 | -0.033569 | 0.0090405 | 0.066731 | 0.068364 | 0.13319 | 0.0029758 | 0.00020288 | -0.21797 | -0.00070077 | 0.00025 | 0.000532 | 0.00027337 | -0.0055969 | 63.7436 | 63.826 | -0.10986 | -59.1797 | 63.8077 | -59.1202 | -59.1385 | -59.0561 | 0.091553 | -59.3399 | 63.8718 | 63.7985 | -59.111 | -59.2484 | -0.054931 | -0.073242 | -0.086975 | 122.8912 | -0.11444 | -0.041198 | -0.15106 | -0.045776 | -0.1831 | -0.022888 | 0.009156 | -0.27466 | -0.091553 | -0.09613 | 122.8729 | 122.8088 | 58.9554 | -123.0331 | 122.937 | 122.8638 | 59.1568 | -123.143
132.5156 | 123.0835 | -59.0973 | 63.9175 | 0.15717 | 0.0043409 | 0.068013 | 0.069859 | 0.12956 | -0.0019376 | -0.0049239 | -0.050125 | -0.00027337 | 0.0015316 | 0.0009592 | -0.0027172 | -0.0026063 | 63.8168 | 63.9221 | -0.032043 | -59.2941 | 63.8168 | -59.1064 | -59.111 | -59.0927 | 0.045776 | -59.3674 | 63.8901 | 63.8214 | -59.0881 | -59.198 | -0.009155 | -0.013733 | -0.10071 | 123.0194 | -0.19684 | -0.1831 | -0.10071 | 0.009155 | -0.10071 | -0.027466 | 0.004578 | -0.27008 | -0.16937 | -0.096131 | 122.9141 | 122.9141 | 59.0652 | -123.0286 | 122.9874 | 122.9187 | 59.1431 | -123.1155
133.5156 | 123.1293 | -59.0927 | 63.8809 | -0.10986 | 0.0081861 | 0.063741 | 0.068364 | 0.13126 | 0.00019875 | -0.0017197 | -0.050125 | 0.00015383 | -0.0006046 | -0.001177 | 0.0032642 | -0.0017517 | 63.8489 | 63.945 | -0.009155 | -59.2575 | 63.8397 | -59.0973 | -59.1248 | -59.0378 | 0.086975 | -59.3536 | 63.8763 | 63.7894 | -59.0927 | -59.2346 | -0.004578 | -0.032044 | -0.041198 | 123.0377 | -0.16479 | -0.13275 | -0.032043 | 0 | -0.14191 | -0.004577 | 0.054931 | -0.26093 | -0.11902 | -0.091552 | 122.9324 | 122.9416 | 59.0836 | -123.0057 | 122.9691 | 122.8821 | 59.1797 | -123.1155
134.5156 | 123.1155 | -59.0973 | 63.913 | -0.16327 | 0.0064771 | 0.0678 | 0.070073 | 0.13041 | -0.0032192 | -0.0025741 | -0.050125 | -0.0017688 | 0.0021726 | 0.0020272 | -0.0018628 | -0.00068366 | 63.8168 | 63.9862 | 0.027466 | -59.2804 | 63.8306 | -59.0927 | -59.1064 | -59.0744 | 0.07782 | -59.166 | 63.9267 | 63.858 | -59.0836 | -59.2392 | 0.004578 | -0.009155 | -0.082398 | 123.0835 | -0.18311 | -0.17395 | -0.096131 | 0.013733 | -0.14191 | 0.013733 | 0.022888 | -0.068665 | 0.073242 | -0.054932 | 122.9279 | 122.9141 | 59.1248 | -123.0194 | 123.024 | 122.9553 | 59.1751 | -123.1522
135.5156 | 123.1384 | -59.079 | 63.9084 | -0.16327 | 0.0069043 | 0.066091 | 0.071141 | 0.13233 | 0.00019875 | -0.0025741 | -0.088272 | -0.002196 | 0.0015316 | -0.0013906 | 0.0019824 | -0.0013245 | 63.8306 | 63.913 | -0.032043 | -59.2804 | 63.8351 | -59.0881 | -59.1293 | -59.0698 | 0.059509 | -59.3674 | 63.9084 | 63.7985 | -59.0927 | -59.2163 | -0.009156 | -0.050354 | -0.073242 | 122.9919 | -0.20142 | -0.15106 | -0.07782 | -0.013733 | -0.13733 | 0 | 0.009155 | -0.28839 | -0.15106 | -0.10986 | 122.9141 | 122.9095 | 59.0469 | -123.0377 | 122.9874 | 122.8775 | 59.1385 | -123.1247
136.5156 | 123.1567 | -59.0469 | 63.9084 | -0.12512 | 0.0036999 | 0.066304 | 0.0658 | 0.13212 | -0.0034328 | -0.0023605 | -0.050125 | -0.0030506 | 0.00025 | 0.000532 | -0.00058103 | -0.0017517 | 63.8763 | 64.0503 | 0.07782 | -59.2346 | 63.7894 | -59.0698 | -59.079 | -59.0378 | 0.12817 | -59.2941 | 63.8763 | 63.7848 | -59.0836 | -59.2072 | -0.022888 | -0.032043 | -0.11902 | 123.0972 | -0.18768 | -0.15564 | -0.032043 | -0.036621 | -0.16022 | -0.032043 | 0.009155 | -0.24719 | -0.086975 | -0.1236 | 122.8363 | 122.9233 | 59.1248 | -122.9874 | 122.9233 | 122.8317 | 59.1751 | -123.1155
137.5156 | 123.0972 | -59.0973 | 63.9084 | -0.47607 | 0.0066907 | 0.066304 | 0.069645 | 0.13319 | -0.0023648 | -0.0027877 | -0.11879 | -0.0015552 | 0.0015316 | 0.0007456 | 5.9768e-05 | -0.0015381 | 63.7894 | 63.9313 | -0.013733 | -59.2896 | 63.8443 | -59.0973 | -59.1156 | -59.079 | 0.054932 | -59.3765 | 63.8901 | 63.826 | -59.0927 | -59.2209 | 0 | -0.018311 | -0.064087 | 123.0286 | -0.19226 | -0.17395 | -0.11902 | 0.004578 | -0.1236 | -0.01831 | 0.018311 | -0.27924 | -0.15564 | -0.082397 | 122.9416 | 122.8867 | 59.0836 | -123.024 | 122.9874 | 122.9233 | 59.1522 | -123.1293
138.5156 | 123.111 | -59.0836 | 63.8992 | -0.18616 | 0.0047681 | 0.068227 | 0.068577 | 0.13169 | -0.0023648 | -0.0030013 | -0.042496 | -0.002837 | -0.0006046 | -0.0007498 | 0.00091437 | 0.00059814 | 63.8718 | 64.0503 | 0.086975 | -59.2209 | 63.7985 | -59.0744 | -59.0927 | -59.0195 | 0.1236 | -59.3216 | 63.8397 | 63.7802 | -59.0607 | -59.2392 | 0.009155 | -0.009155 | -0.10071 | 123.1338 | -0.13733 | -0.12817 | -0.027466 | 0.022888 | -0.15564 | -0.059509 | 0.064087 | -0.23804 | -0.082397 | -0.11902 | 122.8821 | 122.9553 | 59.1705 | -122.9919 | 122.9233 | 122.8638 | 59.2072 | -123.1384
139.5156 | 123.1064 | -59.0927 | 63.8992 | -0.10986 | 0.0081861 | 0.069295 | 0.06815 | 0.13212 | 0.00019875 | -0.0019333 | -0.088272 | 0.00015383 | -0.000391 | -0.001818 | -0.00079463 | -0.0017517 | 63.8168 | 63.9359 | -0.018311 | -59.2804 | 63.826 | -59.1019 | -59.1019 | -59.0652 | 0.032043 | -59.3811 | 63.8672 | 63.7939 | -59.0836 | -59.2255 | -0.009156 | -0.009156 | -0.073242 | 123.0286 | -0.18768 | -0.17853 | -0.082398 | 0.009155 | -0.13275 | -0.032044 | 0.027465 | -0.28839 | -0.15564 | -0.10529 | 122.9187 | 122.9095 | 59.0744 | -123.0011 | 122.9599 | 122.8867 | 59.1248 | -123.1247
140.5156 | 123.2117 | -59.0469 | 63.8672 | -0.10986 | 0.0034863 | 0.068654 | 0.066227 | 0.13041 | -0.0025784 | -0.0030013 | 0.0032804 | -0.002837 | -0.0001774 | -0.0022452 | -0.0014356 | -0.0028199 | 63.9175 | 64.0549 | 0.10529 | -59.2072 | 63.8123 | -59.0698 | -59.1156 | -58.992 | 0.18768 | -59.2758 | 63.8306 | 63.7985 | -59.0469 | -59.2026 | -0.022888 | -0.068665 | -0.054931 | 123.1018 | -0.16022 | -0.091552 | 0.050355 | 0 | -0.15564 | -0.036621 | 0.054932 | -0.22888 | -0.073242 | -0.068664 | 122.8592 | 122.9645 | 59.1522 | -122.9828 | 122.8775 | 122.8455 | 59.2346 | -123.0698
141.5156 | 123.0927 | -59.1202 | 63.8855 | -0.1709 | 0.0071179 | 0.06844 | 0.068577 | 0.13361 | -0.001083 | -0.0015061 | -0.080643 | -0.0019824 | 0.0011044 | -0.0005362 | 0.0015552 | -0.0021789 | 63.8489 | 63.9725 | 0.018311 | -59.2667 | 63.8306 | -59.0927 | -59.1156 | -59.0881 | 0.050354 | -59.2987 | 63.8809 | 63.826 | -59.0515 | -59.198 | 0.027466 | 0.004577 | -0.054932 | 123.0927 | -0.14648 | -0.15106 | -0.036621 | 0.068664 | -0.07782 | -0.004578 | 0.032043 | -0.17853 | -0.10071 | -0.059509 | 122.9507 | 122.9691 | 59.1385 | -123.0011 | 123.0011 | 122.9462 | 59.1705 | -123.0835
142.5156 | 123.23 | -59.0607 | 63.8351 | -0.16327 | 0.0024181 | 0.068227 | 0.065373 | 0.12977 | -0.0034328 | -0.0023605 | 2.4752 | -0.0024096 | -0.0018862 | 0.0003182 | 0.0017688 | -0.00089726 | 63.9038 | 64.0869 | 0.09613 | -59.2072 | 63.7665 | -59.0836 | -59.0836 | -58.9828 | 0.17853 | -59.2529 | 63.826 | 63.7299 | -59.0607 | -59.2026 | -0.022888 | -0.022888 | -0.068665 | 123.1476 | -0.14648 | -0.1236 | 0.068665 | 0 | -0.14191 | -0.009155 | 0.07782 | -0.19226 | -0.050354 | -0.10529 | 122.8271 | 122.9645 | 59.1568 | -122.9187 | 122.8867 | 122.7905 | 59.2392 | -123.0377
143.5156 | 123.2071 | -59.0561 | 63.8718 | -0.15564 | 0.0030591 | 0.065877 | 0.066227 | 0.13041 | -0.00022865 | -0.0021469 | -0.088272 | -0.0030506 | -0.0016726 | -0.0016044 | -0.00079463 | -0.0041017 | 63.8992 | 64.0457 | 0.07782 | -59.2209 | 63.7802 | -59.079 | -59.0973 | -58.9874 | 0.16022 | -59.2987 | 63.8397 | 63.7619 | -59.0836 | -59.2072 | -0.022888 | -0.041199 | -0.091553 | 123.1018 | -0.16479 | -0.1236 | 0.027466 | -0.027466 | -0.15106 | -0.032043 | 0.068664 | -0.24262 | -0.091553 | -0.10986 | 122.8363 | 122.9553 | 59.1339 | -122.9691 | 122.8958 | 122.818 | 59.2163 | -123.0789
144.5156 | 123.2346 | -59.0515 | 63.8443 | -0.018311 | 0.0039135 | 0.067159 | 0.067723 | 0.12806 | -0.0034328 | -0.0015061 | 0.11009 | -0.0019824 | -0.0029544 | -0.0003226 | -0.00229 | -0.0015381 | 63.8809 | 64.0274 | 0.027466 | -59.2392 | 63.8123 | -59.079 | -59.0973 | -58.9508 | 0.13275 | -59.285 | 63.826 | 63.7527 | -59.0652 | -59.2255 | -0.027465 | -0.045776 | -0.032043 | 123.0789 | -0.18768 | -0.14191 | 0.036621 | -0.013733 | -0.17395 | -0.01831 | 0.10071 | -0.23346 | -0.059509 | -0.091552 | 122.8638 | 122.9324 | 59.079 | -122.9416 | 122.8775 | 122.8043 | 59.1843 | -123.0698
145.5156 | 123.1064 | -59.0881 | 63.8947 | -0.13275 | 0.0045545 | 0.068654 | 0.0705 | 0.13084 | 0.0025486 | -0.0019333 | -0.14168 | -0.0015552 | -0.0001774 | 0.0003182 | 0.0015552 | -0.0026063 | 63.8351 | 63.9587 | 0 | -59.285 | 63.8443 | -59.0881 | -59.1156 | -59.0607 | 0.068665 | -59.3857 | 63.8718 | 63.7802 | -59.1064 | -59.2621 | 0 | -0.027466 | -0.050354 | 123.0469 | -0.19684 | -0.16937 | -0.059509 | -0.01831 | -0.17395 | -0.022888 | 0.027466 | -0.29755 | -0.1236 | -0.11444 | 122.9324 | 122.9233 | 59.0881 | -123.0103 | 122.9599 | 122.8683 | 59.1568 | -123.1567
146.5156 | 123.2162 | -59.0561 | 63.8672 | -0.041199 | 0.0028455 | 0.0678 | 0.066227 | 0.13169 | -0.0032192 | -0.0034287 | -0.011978 | -0.0015552 | -0.001459 | 0.0011728 | -0.0014356 | -0.0013245 | 63.8947 | 64.0411 | 0.022888 | -59.23 | 63.7894 | -59.0836 | -59.0973 | -58.9508 | 0.1236 | -59.2575 | 63.8214 | 63.7253 | -59.0698 | -59.2163 | -0.027466 | -0.041199 | -0.077819 | 123.0972 | -0.17395 | -0.13275 | 0.027466 | -0.013733 | -0.16022 | -0.045776 | 0.10529 | -0.20142 | -0.041198 | -0.14191 | 122.8455 | 122.9507 | 59.079 | -122.9645 | 122.8775 | 122.7814 | 59.1797 | -123.0835
147.5156 | 123.1842 | -59.0469 | 63.8443 | -0.13275 | 0.0022045 | 0.0678 | 0.068791 | 0.13404 | -0.00044225 | -0.0010787 | -0.065384 | -0.002196 | -0.000391 | -0.0003226 | 0.0015552 | -0.0032471 | 63.9175 | 64.0778 | 0.086975 | -59.2346 | 63.7894 | -59.0836 | -59.0973 | -58.9645 | 0.17395 | -59.2621 | 63.8443 | 63.7482 | -59.0744 | -59.2209 | -0.036621 | -0.050354 | -0.054931 | 123.1247 | -0.18768 | -0.13733 | 0.073243 | -0.027466 | -0.17395 | 0 | 0.082397 | -0.21515 | -0.041199 | -0.09613 | 122.8363 | 122.9645 | 59.1339 | -122.9416 | 122.8912 | 122.7951 | 59.2209 | -123.0652
148.5156 | 123.2071 | -59.0652 | 63.8489 | 0.019836 | 0.0022045 | 0.065236 | 0.067082 | 0.13404 | -0.0034328 | -0.00043792 | 0.11009 | -0.0019824 | -0.0021 | 0.0003182 | -0.0010082 | -0.0026063 | 63.8718 | 64.0137 | 0.004578 | -59.2621 | 63.7985 | -59.0927 | -59.111 | -58.9737 | 0.086975 | -59.2941 | 63.8306 | 63.7253 | -59.0698 | -59.2255 | -0.027465 | -0.045776 | -0.050354 | 123.0789 | -0.19684 | -0.15106 | 0.022888 | -0.004577 | -0.16022 | -0.018311 | 0.091553 | -0.22888 | -0.068664 | -0.1236 | 122.8638 | 122.937 | 59.0698 | -122.9599 | 122.8958 | 122.7905 | 59.1522 | -123.0743
149.5156 | 123.2346 | -59.024 | 63.8763 | -0.10986 | 0.0066907 | 0.067372 | 0.066868 | 0.13169 | -0.001083 | -0.00086512 | -0.065384 | -0.0030506 | -0.0027408 | 0.0001046 | 0.00070077 | -0.0017517 | 63.8992 | 64.0823 | 0.068665 | -59.2392 | 63.7665 | -59.0561 | -59.0973 | -58.9462 | 0.17853 | -59.2621 | 63.8351 | 63.7207 | -59.0607 | -59.2072 | -0.032043 | -0.073242 | -0.10986 | 123.1064 | -0.21515 | -0.14191 | 0.022888 | -0.036621 | -0.1831 | -0.041199 | 0.07782 | -0.23804 | -0.054932 | -0.15564 | 122.7905 | 122.9233 | 59.0927 | -122.9736 | 122.8592 | 122.7448 | 59.2026 | -123.0835
150.5156 | 123.2117 | -59.0836 | 63.858 | 0.035095 | 0.0030591 | 0.068013 | 0.066014 | 0.13169 | -0.0019376 | -0.00022432 | 0.12535 | -0.0019824 | -0.0029544 | -0.0013906 | 0.0017688 | -0.0028199 | 63.8443 | 64.0182 | -0.022888 | -59.2575 | 63.7894 | -59.0652 | -59.1202 | -59.0057 | 0.064087 | -59.3124 | 63.8351 | 63.7344 | -59.0836 | -59.2026 | 0.01831 | -0.036621 | -0.068664 | 123.1018 | -0.17395 | -0.13733 | -0.013733 | 0 | -0.11902 | -0.022888 | 0.07782 | -0.22888 | -0.10986 | -0.1236 | 122.8729 | 122.9279 | 59.0607 | -122.9782 | 122.9187 | 122.818 | 59.1476 | -123.0606
151.5156 | 123.2483 | -59.0607 | 63.8306 | -0.033569 | 0.0026319 | 0.067159 | 0.067723 | 0.13126 | -0.0025784 | 0.00063028 | 0.1635 | -0.0013416 | 0.001959 | -0.001818 | -0.00036743 | -0.0034607 | 63.9359 | 64.0778 | 0.09613 | -59.2163 | 63.7711 | -59.0515 | -59.0652 | -58.9737 | 0.13275 | -59.2392 | 63.8397 | 63.7344 | -59.0561 | -59.1888 | 0.009155 | -0.004578 | -0.059509 | 123.1384 | -0.15564 | -0.15106 | 0.10529 | 0.004578 | -0.12817 | 0.009156 | 0.086975 | -0.17853 | -0.050354 | -0.09613 | 122.8317 | 122.9965 | 59.1568 | -122.8958 | 122.9004 | 122.7951 | 59.1934 | -123.0194
152.5156 | 123.2346 | -59.0652 | 63.8351 | 0.019836 | 0.00028191 | 0.068013 | 0.067723 | 0.13105 | -0.0019376 | -0.0030013 | 0.10246 | -0.0030506 | -0.0027408 | 0.0011728 | 0.00091437 | -0.0041017 | 63.8672 | 64.0228 | 0.009155 | -59.2529 | 63.7573 | -59.0744 | -59.1202 | -58.9645 | 0.091553 | -59.2941 | 63.826 | 63.7482 | -59.0881 | -59.198 | -0.009155 | -0.054931 | -0.07782 | 123.0881 | -0.18768 | -0.13275 | 0.032043 | -0.022888 | -0.13275 | -0.009155 | 0.10071 | -0.22888 | -0.09613 | -0.086975 | 122.8226 | 122.9324 | 59.0744 | -122.9553 | 122.8912 | 122.8134 | 59.1568 | -123.0331
153.5156 | 123.2254 | -59.0607 | 63.8626 | -0.32349 | 0.0011365 | 0.067159 | 0.06815 | 0.12956 | 0.00062595 | -0.0027877 | -0.011978 | -0.0032642 | -0.0006046 | 0.0003182 | 0.0019824 | -0.0026063 | 63.9313 | 64.0915 | 0.10529 | -59.2026 | 63.7894 | -59.0515 | -59.079 | -58.9417 | 0.18768 | -59.2575 | 63.8443 | 63.7299 | -59.0561 | -59.1888 | 0.009155 | -0.01831 | -0.073242 | 123.1522 | -0.14191 | -0.1236 | 0.068664 | 0.004578 | -0.12817 | -0.018311 | 0.11902 | -0.19684 | -0.068664 | -0.13275 | 122.85 | 122.9919 | 59.166 | -122.9416 | 122.905 | 122.7905 | 59.2484 | -123.0515
154.5156 | 123.1338 | -59.0927 | 63.8992 | -0.16327 | 0.0094677 | 0.066518 | 0.070073 | 0.1302 | 0.0027622 | 0.00063028 | -0.1722 | -0.0013416 | -0.001459 | 0.0003182 | 0.0017688 | -0.0017517 | 63.8214 | 63.945 | -0.018311 | -59.2758 | 63.826 | -59.1019 | -59.1064 | -59.0607 | 0.054932 | -59.3857 | 63.9038 | 63.7848 | -59.0836 | -59.2209 | -0.009156 | -0.013733 | -0.073242 | 123.0377 | -0.18311 | -0.16937 | -0.07782 | 0.009155 | -0.12817 | 0.004578 | 0.032043 | -0.29297 | -0.16479 | -0.11444 | 122.9187 | 122.9141 | 59.0744 | -123.0057 | 122.9965 | 122.8775 | 59.1476 | -123.1201
155.5156 | 123.2346 | -59.0424 | 63.8718 | -0.064087 | 0.0017773 | 0.066518 | 0.069218 | 0.13169 | 0.0021214 | -0.00086512 | -0.2256 | -0.0024096 | -0.0010318 | 0.0007456 | 0.00048697 | -0.00089726 | 63.6475 | 64.119 | 0.10986 | -59.2758 | 63.7711 | -59.0744 | -59.0744 | -58.9554 | 0.19226 | -59.2529 | 63.8168 | 63.739 | -59.0607 | -59.1797 | -0.032044 | -0.032044 | -0.10071 | 123.1613 | -0.23346 | -0.20142 | -0.2243 | -0.018311 | -0.13733 | -0.054932 | 0.086975 | -0.21057 | -0.073243 | -0.13275 | 122.8134 | 122.6898 | 59.1522 | -122.9462 | 122.8592 | 122.7814 | 59.2346 | -123.0515
156.5156 | 123.2574 | -59.0698 | 63.8672 | -0.018311 | 0.0011365 | 0.06545 | 0.067509 | 0.12956 | -0.00065585 | -1.0724e-05 | 0.041427 | -0.002837 | -0.003168 | -0.0007498 | 0.00027337 | -0.0028199 | 63.8901 | 64.0549 | 0.036621 | -59.2438 | 63.7894 | -59.079 | -59.111 | -58.9462 | 0.1236 | -59.2621 | 63.8123 | 63.739 | -59.1019 | -59.1843 | -0.009155 | -0.041199 | -0.077819 | 123.1247 | -0.17395 | -0.13275 | 0.022889 | -0.032044 | -0.11444 | -0.054931 | 0.1236 | -0.19226 | -0.07782 | -0.12817 | 122.8592 | 122.9599 | 59.1064 | -122.9782 | 122.8821 | 122.8088 | 59.1934 | -123.0515
157.5156 | 123.2391 | -59.0469 | 63.8626 | -0.086975 | 0.00092291 | 0.066304 | 0.067296 | 0.13233 | -0.0019376 | -0.00065152 | 0.23979 | 0.0012218 | -0.0001774 | -0.0022452 | 0.0024096 | -0.0030335 | 63.9359 | 64.1144 | 0.073242 | -59.2117 | 63.7848 | -59.0515 | -59.0744 | -58.9874 | 0.16937 | -59.2529 | 63.8351 | 63.7207 | -59.0561 | -59.2072 | -0.004578 | -0.027466 | -0.07782 | 123.1613 | -0.16479 | -0.13733 | 0.073242 | -0.009155 | -0.16022 | -0.027466 | 0.059509 | -0.20599 | -0.045777 | -0.14191 | 122.8317 | 122.9828 | 59.1202 | -122.937 | 122.8821 | 122.7676 | 59.2163 | -123.0698
158.5156 | 123.2208 | -59.0836 | 63.8397 | 0.31738 | 0.00092291 | 0.0678 | 0.067936 | 0.13041 | -0.00044225 | -0.0019333 | 0.13298 | -0.0024096 | -0.0038088 | 0.0020272 | 0.0015552 | -0.0011109 | 63.8168 | 64.0045 | -0.013733 | -59.2712 | 63.7894 | -59.0927 | -59.1293 | -59.0103 | 0.050354 | -59.3079 | 63.8535 | 63.7207 | -59.0927 | -59.2163 | -0.009155 | -0.045776 | -0.050354 | 123.0881 | -0.18768 | -0.14191 | -0.022889 | -0.009155 | -0.13275 | 0.013733 | 0.073242 | -0.2243 | -0.091552 | -0.11902 | 122.8729 | 122.9004 | 59.0698 | -122.9691 | 122.937 | 122.8043 | 59.1339 | -123.056
159.5156 | 123.1522 | -59.0836 | 63.858 | -0.064087 | 0.0096813 | 0.066518 | 0.07285 | 0.13084 | 0.0053256 | -0.0019333 | 0.14061 | 0.0014356 | 0.001318 | -0.000109 | 0.0017688 | -0.0036743 | 63.9313 | 63.7436 | -0.17395 | -59.2255 | 63.8351 | -59.1339 | -59.1431 | -58.9966 | 0.082397 | -59.3445 | 63.8901 | 63.7527 | -59.0973 | -59.2255 | -0.050354 | -0.059509 | -0.022888 | 122.8271 | -0.14191 | -0.082398 | 0.073242 | -0.013733 | -0.14191 | 0.032044 | 0.086975 | -0.26093 | -0.11902 | -0.10529 | 122.9187 | 123.0148 | 58.9096 | -123.0011 | 122.9736 | 122.8363 | 59.166 | -123.0835
160.5156 | 123.1018 | -59.0424 | 63.9038 | -0.033569 | 6.8308e-05 | 0.065022 | 0.067296 | 0.13169 | -0.0040738 | -0.00065152 | -0.011978 | -0.0024096 | 0.0006772 | 0.000532 | -0.0012218 | -0.00089726 | 63.913 | 64.0823 | 0.068665 | -59.2163 | 63.7985 | -59.0881 | -59.0973 | -58.9188 | 0.15106 | -59.2209 | 63.8031 | 63.7344 | -59.0424 | -59.1797 | -0.045777 | -0.054932 | -0.10529 | 123.1247 | -0.17395 | -0.11902 | 0.009155 | 0 | -0.13733 | -0.10071 | 0.1236 | -0.17853 | -0.041199 | -0.16937 | 122.8409 | 122.9553 | 59.111 | -123.0011 | 122.8455 | 122.7768 | 59.1934 | -123.0835
161.5156 | 123.1659 | -59.0561 | 63.8626 | -0.17853 | 0.0034863 | 0.065877 | 0.068364 | 0.13233 | 0.00083955 | 0.00041648 | -0.073013 | -5.9768e-05 | -0.0008182 | -0.0007498 | -0.0010082 | -0.0030335 | 63.9084 | 64.0686 | 0.07782 | -59.2163 | 63.7985 | -59.0836 | -59.111 | -58.9645 | 0.16937 | -59.285 | 63.8489 | 63.7344 | -59.0652 | -59.2026 | -0.027466 | -0.054932 | -0.064087 | 123.1247 | -0.16022 | -0.10529 | 0.045776 | -0.009156 | -0.14648 | -0.013733 | 0.091552 | -0.22888 | -0.082397 | -0.12817 | 122.8546 | 122.9645 | 59.1339 | -122.9736 | 122.905 | 122.7905 | 59.2255 | -123.0652
162.5156 | 123.1979 | -59.024 | 63.858 | -0.033569 | 0.0015637 | 0.069081 | 0.067082 | 0.13169 | -0.0030056 | -0.0019333 | 0.056686 | 0.00015383 | -0.0018862 | -0.0003226 | -0.00079463 | -0.00047006 | 63.8763 | 64.0366 | 0.050354 | -59.2392 | 63.7848 | -59.0836 | -59.111 | -58.9554 | 0.13733 | -59.2438 | 63.8214 | 63.7253 | -59.0652 | -59.1843 | -0.059509 | -0.086975 | -0.073242 | 123.0606 | -0.21515 | -0.12817 | 0.018311 | -0.041199 | -0.16022 | -0.036621 | 0.068665 | -0.21973 | -0.059509 | -0.13275 | 122.8088 | 122.9004 | 59.0744 | -122.9691 | 122.8455 | 122.7493 | 59.1614 | -123.0423
163.5156 | 123.1934 | -59.0469 | 63.8626 | -0.14038 | 0.0043409 | 0.066945 | 0.067936 | 0.13255 | 0.00019875 | -0.0015061 | -0.065384 | -0.002196 | 0.0004636 | -0.0016044 | -0.00015383 | -0.0034607 | 63.913 | 64.0869 | 0.086975 | -59.2072 | 63.7802 | -59.0744 | -59.0881 | -58.9508 | 0.16937 | -59.2712 | 63.826 | 63.7253 | -59.0561 | -59.1934 | -0.027466 | -0.041199 | -0.082398 | 123.1338 | -0.16022 | -0.11902 | 0.050354 | -0.009155 | -0.14648 | -0.036621 | 0.09613 | -0.2243 | -0.07782 | -0.13733 | 122.8271 | 122.9599 | 59.1339 | -122.9507 | 122.8729 | 122.7722 | 59.2163 | -123.056
164.5156 | 123.1476 | -59.0698 | 63.8992 | -0.13275 | 0.0077587 | 0.065663 | 0.070714 | 0.13212 | 0.0059666 | -0.0012923 | -0.10353 | -0.00091437 | 0.0006772 | 0.0016 | 0.002837 | -0.0043153 | 63.8672 | 63.9771 | 0 | -59.2529 | 63.8168 | -59.0973 | -59.1293 | -59.0057 | 0.091553 | -59.3582 | 63.8809 | 63.7619 | -59.0881 | -59.2117 | -0.027466 | -0.059509 | -0.082398 | 123.0469 | -0.18311 | -0.1236 | -0.032044 | -0.018311 | -0.14191 | -0.018311 | 0.064087 | -0.28839 | -0.14648 | -0.13733 | 122.8867 | 122.937 | 59.0698 | -123.0286 | 122.9507 | 122.8317 | 59.1614 | -123.111
165.5156 | 123.2208 | -59.024 | 63.8763 | -0.079346 | 0.0049817 | 0.065022 | 0.066014 | 0.13361 | -0.0025784 | -0.0017197 | -0.057755 | -0.001128 | 0.0006772 | -0.0013906 | 0.001128 | -0.0015381 | 63.8992 | 64.0778 | 0.10071 | -59.2163 | 63.7711 | -59.0744 | -59.0881 | -58.96 | 0.1831 | -59.2484 | 63.8351 | 63.7482 | -59.0652 | -59.1934 | -0.050354 | -0.064087 | -0.10529 | 123.1018 | -0.19226 | -0.12817 | 0.022888 | -0.041199 | -0.16937 | -0.041199 | 0.064087 | -0.2243 | -0.054932 | -0.12817 | 122.7951 | 122.9233 | 59.1248 | -122.9645 | 122.8592 | 122.7722 | 59.2072 | -123.0698
166.5156 | 123.262 | -59.0103 | 63.8672 | -0.064087 | 0.0019909 | 0.066518 | 0.066227 | 0.12892 | -0.0025784 | -0.00043792 | 0.018539 | -0.0026234 | -0.0023136 | -0.001177 | -0.0014356 | -0.0032471 | 63.9038 | 64.0869 | 0.054932 | -59.2072 | 63.7894 | -59.0698 | -59.079 | -58.9371 | 0.19226 | -59.2209 | 63.8306 | 63.7161 | -59.0698 | -59.1751 | -0.059509 | -0.068664 | -0.077819 | 123.0972 | -0.19684 | -0.12817 | 0.036622 | -0.059509 | -0.16479 | -0.036621 | 0.073242 | -0.21057 | -0.045776 | -0.15106 | 122.7997 | 122.9141 | 59.0652 | -122.9462 | 122.8409 | 122.7264 | 59.2026 | -123.0423
167.5156 | 123.23 | -59.0195 | 63.858 | -1.2466 | 0.0039135 | 0.066091 | 0.066655 | 0.13148 | -0.0012966 | -0.00022432 | -0.042496 | -0.0034778 | -0.0035952 | -0.0003226 | 0.0030506 | -0.0034607 | 63.8809 | 64.1144 | 0.09613 | -59.2209 | 63.7894 | -59.079 | -59.0881 | -58.9508 | 0.19226 | -59.23 | 63.8535 | 63.7344 | -59.0607 | -59.1888 | -0.059509 | -0.068665 | -0.068664 | 123.1338 | -0.20142 | -0.13275 | 0.022888 | -0.041199 | -0.16937 | -0.004577 | 0.068664 | -0.21057 | -0.041199 | -0.1236 | 122.8088 | 122.9004 | 59.1156 | -122.9462 | 122.8729 | 122.7539 | 59.2117 | -123.0469
168.5156 | 123.1934 | -59.0836 | 63.8397 | 0.050354 | 0.0034863 | 0.066091 | 0.067509 | 0.13212 | -0.002792 | -0.0021469 | 0.094833 | -0.002837 | 3.6404e-05 | -0.0003226 | 0.0019824 | -0.0023927 | 63.8397 | 63.9862 | -0.018311 | -59.2667 | 63.8031 | -59.0881 | -59.0973 | -58.9737 | 0.07782 | -59.2941 | 63.8168 | 63.7161 | -59.0652 | -59.2209 | -0.004578 | -0.013733 | -0.036621 | 123.0698 | -0.18311 | -0.16937 | 0 | 0.01831 | -0.13733 | -0.022889 | 0.10986 | -0.21057 | -0.073242 | -0.1236 | 122.8867 | 122.9233 | 59.0652 | -122.937 | 122.9004 | 122.7997 | 59.1614 | -123.0606
169.5156 | 123.262 | -59.0515 | 63.858 | -0.02594 | 0.0026319 | 0.066731 | 0.065587 | 0.13041 | 0.00041235 | -0.0034287 | 0.056686 | -0.0030506 | -0.003168 | -0.000109 | 0.0017688 | -0.0015381 | 63.945 | 64.1098 | -0.059509 | -58.9325 | 63.826 | -59.0515 | -59.0561 | -58.9783 | 0.16937 | -59.23 | 63.8351 | 63.7207 | -59.0744 | -59.2163 | 0 | -0.004577 | -0.032043 | 123.1613 | 0.11902 | 0.1236 | 0.086975 | -0.022888 | -0.1648 | -0.022888 | 0.073243 | -0.17853 | -0.013733 | -0.13733 | 122.8775 | 122.9965 | 58.992 | -122.9141 | 122.8867 | 122.7722 | 59.2209 | -123.0743
170.5156 | 123.1705 | -59.0652 | 63.858 | 0.11902 | 0.0017773 | 0.066518 | 0.064732 | 0.1302 | -0.0019376 | -0.0010787 | 0.10246 | -0.0017688 | -0.0023136 | -0.0007498 | 0.0015552 | -0.00025626 | 63.8535 | 63.9954 | -0.027466 | -59.2758 | 63.7894 | -59.111 | -59.1064 | -59.0103 | 0.059509 | -59.317 | 63.8397 | 63.7253 | -59.0836 | -59.1934 | -0.045776 | -0.041198 | -0.068664 | 123.0606 | -0.21057 | -0.16937 | -0.004577 | -0.01831 | -0.12817 | -0.01831 | 0.054932 | -0.25177 | -0.1236 | -0.13275 | 122.8546 | 122.9187 | 59.0378 | -122.9645 | 122.905 | 122.7905 | 59.1248 | -123.0515
171.5156 | 123.2117 | -59.0652 | 63.8535 | -0.033569 | 0.0024181 | 0.067372 | 0.068577 | 0.12934 | -0.0017238 | -0.0017197 | -0.011978 | -0.0041186 | -0.0006046 | -0.0016044 | -0.0012218 | -0.0038879 | 63.9359 | 64.0823 | 0.082397 | -59.2209 | 63.7848 | -59.0607 | -59.0836 | -58.9279 | 0.17853 | -59.2346 | 63.858 | 63.7894 | -59.0378 | -59.1614 | 0.004578 | -0.01831 | -0.068665 | 123.1476 | -0.15564 | -0.13733 | 0.082397 | 0.027466 | -0.09613 | 0.004577 | 0.13733 | -0.16937 | -0.073242 | -0.064087 | 122.85 | 123.0011 | 59.1476 | -122.937 | 122.9233 | 122.8546 | 59.2438 | -123.0148
172.5156 | 123.1934 | -59.0515 | 63.8214 | 0.11139 | 0.0015637 | 0.064595 | 0.066227 | 0.12913 | -0.00065585 | -0.0019333 | 0.13298 | -0.0047596 | -0.0001774 | -0.0003226 | 0.0024096 | -0.0019653 | 63.7894 | 63.9862 | -0.027466 | -59.3079 | 63.7482 | -59.0973 | -59.1156 | -59.024 | 0.036621 | -59.3124 | 63.8535 | 63.7344 | -59.0927 | -59.2117 | -0.045776 | -0.064087 | -0.073242 | 123.0377 | -0.25635 | -0.19226 | -0.032043 | -0.041198 | -0.16022 | 0.032044 | 0.027466 | -0.26093 | -0.10071 | -0.086975 | 122.7997 | 122.8409 | 59.024 | -122.937 | 122.905 | 122.7859 | 59.0881 | -123.0331
173.5156 | 123.23 | -59.024 | 63.8626 | -0.13275 | 0.0056225 | 0.068013 | 0.067082 | 0.12956 | -0.0017238 | -0.00086512 | 0.17876 | -0.003905 | -0.0018862 | 0.0009592 | 0.0017688 | -0.0041017 | 63.9084 | 63.8992 | 0 | -59.1934 | 63.7848 | -59.0515 | -59.0836 | -58.9417 | 0.17395 | -59.2346 | 63.858 | 63.7253 | -59.0652 | -59.2163 | -0.027466 | -0.059509 | -0.07782 | 122.9233 | -0.16937 | -0.10986 | 0.045776 | -0.041199 | -0.19226 | -0.004578 | 0.082398 | -0.21057 | -0.01831 | -0.13733 | 122.8088 | 122.9324 | 59.024 | -122.9462 | 122.8821 | 122.7493 | 59.198 | -123.0789
174.5156 | 123.2162 | -59.0698 | 63.8397 | 0.042725 | 0.0030591 | 0.066731 | 0.0658 | 0.12913 | -0.0015102 | -0.0021469 | 0.11009 | -0.0043324 | -0.0018862 | -0.0022452 | -0.00036743 | -0.0021789 | 63.8443 | 63.9908 | -0.027466 | -59.2667 | 63.8031 | -59.0927 | -59.111 | -58.9966 | 0.068665 | -59.3033 | 63.8443 | 63.7161 | -59.079 | -59.2072 | -0.022888 | -0.041199 | -0.036621 | 123.0606 | -0.19684 | -0.15564 | 0.004577 | -0.009155 | -0.13733 | 0.004577 | 0.073242 | -0.23346 | -0.096131 | -0.1236 | 122.8729 | 122.9141 | 59.0424 | -122.9507 | 122.9141 | 122.7859 | 59.1385 | -123.0469
175.5156 | 123.23 | -59.0561 | 63.858 | -0.086975 | 0.0036999 | 0.067586 | 0.068791 | 0.12913 | -0.00022865 | -0.0025741 | -0.034867 | -0.002196 | -0.0021 | -0.0009634 | -0.0031446 | -0.0045289 | 63.9359 | 64.0869 | 0.086975 | -59.2026 | 63.8031 | -59.0607 | -59.0744 | -58.7677 | -0.15564 | -59.3765 | 63.8443 | 63.7207 | -59.0744 | -59.2255 | -0.004578 | -0.018311 | -0.054931 | 123.143 | -0.14648 | -0.12817 | 0.07782 | -0.018311 | -0.16937 | -0.013733 | 0.28839 | -0.32043 | -0.15106 | -0.13733 | 122.8592 | 122.9919 | 59.1431 | -122.9324 | 122.9004 | 122.7768 | 58.9005 | -123.0835
176.5156 | 123.175 | -59.0515 | 63.8443 | -0.41504 | 0.0032727 | 0.063741 | 0.068577 | 0.12977 | -0.00044225 | -0.00022432 | 0.15587 | -0.002196 | -0.0040226 | -0.0009634 | 0.0019824 | -0.0032471 | 63.8763 | 63.9679 | -0.045776 | -59.2712 | 63.7848 | -59.1019 | -59.1019 | -59.0057 | 0.050354 | -59.3124 | 63.8351 | 63.7024 | -59.0881 | -59.1934 | -0.050354 | -0.050354 | -0.059509 | 123.0194 | -0.21973 | -0.16937 | 0.032044 | -0.036621 | -0.14191 | -0.009155 | 0.045777 | -0.26093 | -0.11902 | -0.14191 | 122.8363 | 122.9279 | 59.0057 | -122.9462 | 122.8867 | 122.7539 | 59.1019 | -123.0377
177.5156 | 123.2437 | -59.0424 | 63.8672 | -0.048828 | 0.0034863 | 0.068227 | 0.066227 | 0.1302 | -0.0023648 | -0.0025741 | -0.019608 | -0.003905 | -0.0044498 | -0.0030996 | -0.0025036 | -0.0032471 | 63.9038 | 64.064 | 0.050354 | -59.23 | 63.7894 | -59.0881 | -59.1064 | -58.9279 | 0.14191 | -59.2484 | 63.826 | 63.7161 | -59.0515 | -59.2072 | -0.045777 | -0.064087 | -0.077819 | 123.1064 | -0.18768 | -0.1236 | 0.036622 | -0.009156 | -0.16479 | -0.041198 | 0.11444 | -0.20599 | -0.041199 | -0.15106 | 122.8317 | 122.9462 | 59.0927 | -122.9736 | 122.8683 | 122.7585 | 59.1843 | -123.0743
178.5156 | 123.1476 | -59.0836 | 63.8077 | 0.21057 | 0.0047681 | 0.066945 | 0.065587 | 0.12934 | 0.00062595 | 0.00041648 | 0.15587 | -0.0017688 | -0.0042362 | -0.0005362 | 0.0024096 | -0.00047006 | 63.8489 | 63.9999 | -0.018311 | -59.2758 | 63.7939 | -59.0881 | -59.0927 | -59.1156 | 0.068665 | -59.3674 | 63.8077 | 63.707 | -59.0836 | -59.2621 | -0.004578 | -0.009155 | -0.013733 | 123.0835 | -0.19226 | -0.18311 | 0.041199 | 0 | -0.17853 | 0 | -0.032044 | -0.28381 | -0.10529 | -0.10071 | 122.8775 | 122.9324 | 59.0652 | -122.9004 | 122.8912 | 122.7905 | 59.1522 | -123.0698
179.5156 | 123.2071 | -59.024 | 63.8306 | -0.041199 | 0.00028191 | 0.066304 | 0.069645 | 0.13084 | 0.00062595 | -0.0025741 | 0.041427 | -0.001128 | -0.0035952 | 0.0003182 | 5.9768e-05 | -0.0019653 | 63.8947 | 64.0182 | 0.018311 | -59.23 | 63.7802 | -59.0836 | -59.1202 | -58.96 | 0.11444 | -59.2484 | 63.8489 | 63.7344 | -59.0698 | -59.2255 | -0.059509 | -0.09613 | -0.050354 | 123.0423 | -0.20599 | -0.10986 | 0.064087 | -0.045776 | -0.20142 | 0.018311 | 0.064087 | -0.2243 | -0.022888 | -0.09613 | 122.8043 | 122.9187 | 59.0424 | -122.9507 | 122.8729 | 122.7585 | 59.1385 | -123.056
180.5156 | 123.0927 | -59.0973 | 63.9084 | -0.14038 | 0.0079723 | 0.066945 | 0.067723 | 0.13105 | 0.002335 | -0.00043792 | -0.12642 | -0.00027337 | -0.001459 | -0.0003226 | 0.0013416 | -0.0036743 | 63.8626 | 63.9267 | -0.036621 | -59.2758 | 63.8443 | -59.1019 | -59.1064 | -59.0378 | 0.050354 | -59.3903 | 63.9084 | 63.7894 | -59.0744 | -59.2117 | -0.004578 | -0.009155 | -0.064087 | 123.024 | -0.17853 | -0.16937 | -0.045776 | 0.022888 | -0.11444 | 0 | 0.059509 | -0.29297 | -0.17853 | -0.11902 | 122.9416 | 122.9599 | 59.0607 | -123.0148 | 123.0057 | 122.8867 | 59.1476 | -123.1201
181.5156 | 123.262 | -59.0378 | 63.858 | 0.012207 | 0.0030591 | 0.06844 | 0.067509 | 0.1302 | -0.0036464 | -0.0012923 | 0.056686 | -0.002837 | -0.001459 | -0.0013906 | 0.00070077 | -0.0017517 | 63.9038 | 64.0503 | 0.041199 | -59.23 | 63.7756 | -59.0698 | -59.1064 | -58.9279 | 0.16937 | -59.2392 | 63.826 | 63.7161 | -59.0652 | -59.2163 | -0.032043 | -0.068664 | -0.082397 | 123.0881 | -0.19226 | -0.1236 | 0.045777 | -0.027466 | -0.17853 | -0.032043 | 0.10986 | -0.20142 | -0.022888 | -0.14191 | 122.8134 | 122.9416 | 59.079 | -122.9645 | 122.8638 | 122.7539 | 59.2072 | -123.0743
182.5156 | 123.175 | -59.079 | 63.8443 | 0.14954 | 0.0036999 | 0.066091 | 0.070073 | 0.13169 | -0.0023648 | 0.00041648 | 0.19402 | -0.00091437 | -0.0012454 | -0.0005362 | 0.00091437 | -0.0015381 | 63.8489 | 63.9771 | -0.045776 | -59.285 | 63.7848 | -59.0927 | -59.0973 | -59.0012 | 0.21515 | -59.2026 | 63.8672 | 63.7436 | -59.0607 | -59.2026 | -0.013733 | -0.018311 | -0.059509 | 123.056 | -0.20599 | -0.18768 | 0.004578 | 0.01831 | -0.1236 | 0.022888 | 0.077819 | -0.1236 | 0 | -0.10071 | 122.8638 | 122.9279 | 59.0332 | -122.9416 | 122.9462 | 122.8226 | 59.2941 | -123.0469
183.5156 | 123.2071 | -59.0378 | 63.8535 | 0.027466 | 0.0041271 | 0.066731 | 0.067936 | 0.12956 | -0.00086945 | -0.00043792 | 0.094833 | -0.002196 | -0.001459 | -0.0009634 | 0.0024096 | -0.0013245 | 63.8672 | 64.0228 | 0.004578 | -59.2438 | 63.7894 | -59.0973 | -59.1064 | -58.9645 | 0.10529 | -59.2804 | 63.8306 | 63.7207 | -59.0836 | -59.2163 | -0.059509 | -0.068664 | -0.064087 | 123.0606 | -0.20599 | -0.13733 | 0.013732 | -0.045776 | -0.17853 | -0.022889 | 0.073242 | -0.24262 | -0.064087 | -0.13275 | 122.8271 | 122.905 | 59.0424 | -122.9599 | 122.8683 | 122.7585 | 59.1431 | -123.0698
184.5156 | 123.2437 | -59.0744 | 63.8031 | 0.2182 | 0.0071179 | 0.066518 | 0.068577 | 0.13041 | 0.002335 | -0.00022432 | 0.26268 | -0.0024096 | -0.0025272 | -0.0020316 | 0.0017688 | -0.0032471 | 63.8901 | 64.0137 | -0.027466 | -59.2621 | 63.7482 | -59.1248 | -59.1064 | -58.96 | 0.050354 | -59.2896 | 63.7802 | 63.7115 | -59.1156 | -59.2438 | -0.050354 | -0.032043 | -0.054932 | 123.0881 | -0.18768 | -0.15564 | 0.086975 | -0.041199 | -0.16937 | -0.022889 | 0.11444 | -0.21515 | -0.045777 | -0.091553 | 122.8226 | 122.9645 | 59.0469 | -122.9095 | 122.8546 | 122.7859 | 59.1248 | -123.0469
185.5156 | 123.1888 | -59.0515 | 63.8489 | 0.065613 | 0.0017773 | 0.065236 | 0.069218 | 0.13041 | -0.0012966 | -0.0012923 | 0.14824 | -0.0026234 | -0.0029544 | -0.000109 | -0.00036743 | -0.0026063 | 63.858 | 63.9725 | -0.027466 | -59.2667 | 63.7939 | -59.0607 | -59.1019 | -59.0012 | 0.054932 | -59.3124 | 63.8123 | 63.7115 | -59.079 | -59.2026 | -0.009155 | -0.050354 | -0.054932 | 123.024 | -0.21515 | -0.16479 | 0.009155 | -0.027465 | -0.15106 | -0.036621 | 0.050354 | -0.26093 | -0.10986 | -0.13733 | 122.8455 | 122.9095 | 59.024 | -122.9507 | 122.8638 | 122.7631 | 59.1064 | -123.0515
186.5156 | 123.1705 | -59.0652 | 63.826 | 0.20294 | 0.0041271 | 0.066518 | 0.066227 | 0.1302 | -0.0012966 | 0.00041648 | 0.23216 | -0.0017688 | -0.000391 | -0.001177 | -0.00058103 | -0.0028199 | 63.8626 | 63.9862 | -0.050354 | -59.2758 | 63.7665 | -59.0927 | -59.1156 | -59.0012 | 0.027466 | -59.3262 | 63.826 | 63.7161 | -59.1202 | -59.2117 | -0.027465 | -0.050354 | -0.05951 | 123.0515 | -0.21057 | -0.16022 | 0.036621 | -0.054931 | -0.14648 | 0 | 0.064087 | -0.26093 | -0.11444 | -0.10986 | 122.8317 | 122.9279 | 59.0149 | -122.9416 | 122.8912 | 122.7814 | 59.0927 | -123.0377
187.5156 | 123.1842 | -59.0515 | 63.8397 | 0.027466 | 0.00092291 | 0.069509 | 0.065587 | 0.12998 | -0.00065585 | -0.0021469 | 0.094833 | -0.002196 | -0.0033816 | -0.001177 | -0.00079463 | -0.0038879 | 63.8718 | 63.9954 | -0.013733 | -59.2621 | 63.8077 | -59.1019 | -59.0927 | -58.992 | 0.07782 | -59.2941 | 63.8306 | 63.7344 | -59.0927 | -59.2026 | -0.050354 | -0.041198 | -0.032044 | 123.0469 | -0.21057 | -0.16937 | 0.032043 | -0.041198 | -0.15106 | -0.009156 | 0.05951 | -0.24261 | -0.091552 | -0.10529 | 122.8592 | 122.9233 | 59.0378 | -122.9324 | 122.8821 | 122.7859 | 59.1293 | -123.0423
188.5156 | 123.2071 | -59.0652 | 63.8168 | 0.14954 | 0.0049817 | 0.06545 | 0.067082 | 0.13062 | 0.00041235 | -0.0010787 | 0.11772 | -0.002837 | -0.0006046 | -0.0016044 | 0.0024096 | -0.0019653 | 63.8535 | 63.9679 | -0.054932 | -59.2758 | 63.7665 | -59.0698 | -59.1385 | -59.0103 | 0.050354 | -59.166 | 63.8489 | 63.7436 | -59.0698 | -59.23 | -0.004577 | -0.073242 | -0.050354 | 123.0331 | -0.21057 | -0.13733 | 0.036622 | -0.004577 | -0.16479 | 0.032044 | 0.054932 | -0.10071 | 0.064087 | -0.073242 | 122.8317 | 122.9187 | 59.0103 | -122.9553 | 122.9141 | 122.8088 | 59.1156 | -123.0469
189.5156 | 123.1934 | -59.0744 | 63.858 | -0.10986 | 0.0047681 | 0.065663 | 0.0658 | 0.13169 | 0.00062595 | 0.00020288 | 0.13298 | -0.0024096 | -0.0023136 | -0.0022452 | 0.00027337 | -0.0026063 | 63.8718 | 63.9542 | -0.059509 | -59.2804 | 63.7802 | -59.0927 | -59.0927 | -59.0012 | 0.036621 | -59.3079 | 63.826 | 63.7344 | -59.0744 | -59.2163 | -0.01831 | -0.01831 | -0.07782 | 123.0286 | -0.20599 | -0.18768 | 0.013733 | 0 | -0.14191 | -0.032043 | 0.073242 | -0.23346 | -0.091552 | -0.1236 | 122.8546 | 122.9462 | 59.0149 | -122.9507 | 122.9004 | 122.8088 | 59.111 | -123.0743
190.5156 | 123.2254 | -59.0744 | 63.8168 | 0.17242 | 0.0079723 | 0.0678 | 0.066441 | 0.13169 | 0.0019078 | 0.0014847 | 0.2169 | -0.002837 | -0.0027408 | -0.0009634 | 0.00091437 | -0.0047425 | 63.8947 | 64.0228 | 0 | -59.2575 | 63.7344 | -59.0973 | -59.0927 | -58.96 | 0.050354 | -59.3124 | 63.7939 | 63.7024 | -59.1019 | -59.2255 | -0.022888 | -0.01831 | -0.082397 | 123.0972 | -0.1831 | -0.16479 | 0.07782 | -0.027466 | -0.15106 | -0.022888 | 0.11444 | -0.23804 | -0.086975 | -0.11444 | 122.8088 | 122.9691 | 59.0744 | -122.9095 | 122.8683 | 122.7768 | 59.1248 | -123.0423
191.5156 | 123.23 | -59.0515 | 63.8214 | 0.012207 | 0.0015637 | 0.067586 | 0.067936 | 0.13041 | -0.0021512 | -0.0053513 | 0.064316 | -0.0032642 | -0.0035952 | -0.0026724 | 0.00048697 | -0.0026063 | 63.8809 | 64.0366 | 0.022888 | -59.2392 | 63.7848 | -59.0698 | -59.1019 | -58.9554 | 0.11444 | -59.2712 | 63.8306 | 63.7115 | -59.0607 | -59.2072 | -0.01831 | -0.050354 | -0.036621 | 123.0881 | -0.18768 | -0.13733 | 0.059509 | -0.009155 | -0.15564 | 0.009155 | 0.096131 | -0.21973 | -0.064087 | -0.10986 | 122.8363 | 122.9324 | 59.0744 | -122.9233 | 122.8821 | 122.7631 | 59.166 | -123.0286
192.5156 | 123.2437 | -59.0515 | 63.8031 | 0.18005 | 0.0098951 | 0.06545 | 0.067296 | 0.13084 | 0.0036166 | 0.0012711 | 0.23979 | -0.0024096 | -0.001459 | -0.0016044 | 0.0024096 | -0.0038879 | 63.8992 | 64.0045 | -0.050354 | -59.4315 | 63.739 | -59.1202 | -59.1431 | -58.9554 | 0.041199 | -59.3079 | 63.8306 | 63.6932 | -59.1202 | -59.2209 | -0.068664 | -0.091552 | -0.064087 | 123.056 | -0.37994 | -0.28839 | 0.09613 | -0.068664 | -0.16937 | 0.027465 | 0.096131 | -0.25635 | -0.086975 | -0.10986 | 122.7905 | 122.9507 | 59.0012 | -122.9462 | 122.8821 | 122.7448 | 59.0927 | -123.024
193.5156 | 123.175 | -59.0607 | 63.8123 | 0.16479 | 0.0051953 | 0.063954 | 0.064946 | 0.13105 | 0.00041235 | -0.00086512 | 0.27031 | 0.00036743 | 0.0006772 | 0.0011728 | 0.0019824 | -0.0019653 | 63.8947 | 64.0091 | -0.022888 | -59.285 | 63.7573 | -59.111 | -59.1156 | -58.9966 | 0.032043 | -59.3216 | 63.7985 | 63.7024 | -59.0836 | -59.2117 | -0.050354 | -0.054932 | -0.054932 | 123.0698 | -0.2243 | -0.16937 | 0.082397 | -0.022888 | -0.15106 | -0.013733 | 0.064087 | -0.26093 | -0.10986 | -0.10986 | 122.818 | 122.9553 | 59.0378 | -122.9279 | 122.8592 | 122.7631 | 59.0927 | -123.024
194.5156 | 123.1796 | -59.0561 | 63.8123 | 0.27924 | 0.0090405 | 0.06545 | 0.0658 | 0.13062 | 0.0031894 | -1.0724e-05 | 0.26268 | -0.0013416 | -0.0008182 | 0.0007456 | 0.0013416 | -0.0038879 | 63.913 | 64.0091 | -0.009155 | -59.2667 | 63.7482 | -59.0698 | -59.1064 | -58.9691 | 0.050354 | -59.2941 | 63.7894 | 63.6887 | -59.1248 | -59.23 | -0.013733 | -0.050354 | -0.064087 | 123.0652 | -0.21057 | -0.16022 | 0.10071 | -0.068665 | -0.17395 | -0.022888 | 0.086975 | -0.23804 | -0.064086 | -0.1236 | 122.8043 | 122.9691 | 59.0469 | -122.9187 | 122.8455 | 122.7448 | 59.1064 | -123.0423
195.5156 | 123.1613 | -59.0607 | 63.8397 | 0.14954 | 0.0024181 | 0.063954 | 0.067082 | 0.13041 | -0.0019376 | -0.00065152 | 0.23216 | -0.0019824 | -0.0018862 | -0.0020316 | 0.0030506 | 0.00017094 | 63.858 | 63.9954 | -0.022888 | -59.2941 | 63.739 | -59.111 | -59.111 | -59.0195 | 0.013733 | -59.317 | 63.8351 | 63.7115 | -59.1019 | -59.2117 | -0.050354 | -0.050354 | -0.10071 | 123.056 | -0.23346 | -0.1831 | 0.01831 | -0.041199 | -0.15106 | -0.004578 | 0.041199 | -0.25635 | -0.10529 | -0.12817 | 122.7997 | 122.9187 | 59.0378 | -122.9507 | 122.8958 | 122.7722 | 59.0744 | -123.0515
196.5156 | 123.2208 | -59.0744 | 63.8077 | 0.16479 | 0.0073315 | 0.066731 | 0.068577 | 0.13426 | 0.0036166 | 0.0025529 | 0.28557 | -0.0024096 | 3.6404e-05 | 0.0003182 | 0.0034778 | -0.0021789 | 63.8901 | 63.9954 | -0.036621 | -59.2484 | 63.7619 | -59.0973 | -59.0881 | -58.9691 | 0.21515 | -59.3124 | 63.8168 | 63.7115 | -59.079 | -59.23 | -0.022888 | -0.013733 | -0.045776 | 123.0698 | -0.17395 | -0.16022 | 0.082398 | -0.004577 | -0.15564 | 0.009155 | 0.10529 | -0.23804 | -0.082397 | -0.09613 | 122.8363 | 122.9645 | 59.0378 | -122.8958 | 122.8912 | 122.7859 | 59.2896 | -123.0377
197.5156 | 123.2071 | -59.0607 | 63.8123 | 0.17242 | 0.0047681 | 0.065877 | 0.066868 | 0.12827 | -0.00065585 | 0.00041648 | 0.26268 | -0.0017688 | -0.0012454 | -0.0020316 | 0.0013416 | -0.0036743 | 63.8901 | 63.9999 | -0.022888 | -59.2667 | 63.7482 | -59.0927 | -59.111 | -58.9783 | 0.041199 | -59.317 | 63.7894 | 63.6978 | -59.0836 | -59.23 | -0.032043 | -0.050354 | -0.064087 | 123.0606 | -0.20599 | -0.15564 | 0.07782 | -0.022888 | -0.16937 | -0.022888 | 0.082398 | -0.25635 | -0.086975 | -0.11444 | 122.8088 | 122.9507 | 59.0378 | -122.9233 | 122.85 | 122.7585 | 59.1019 | -123.0423
198.5156 | 123.2025 | -59.0744 | 63.826 | 0.24872 | 0.0056225 | 0.065022 | 0.063878 | 0.13169 | -0.00044225 | -0.0010787 | 0.25505 | -0.0017688 | -0.001459 | -0.0003226 | 0.0017688 | -0.0045289 | 64.0182 | 63.9679 | -0.009155 | -59.2255 | 63.7894 | -59.0744 | -59.1156 | -58.9737 | 0.041199 | -59.2987 | 63.826 | 63.6932 | -59.1339 | -59.2255 | 0 | -0.041199 | -0.036621 | 123.0423 | -0.15106 | -0.10986 | 0.19226 | -0.059509 | -0.15106 | 0 | 0.10071 | -0.2243 | -0.073242 | -0.13275 | 122.8638 | 123.0927 | 59.0652 | -122.9416 | 122.9004 | 122.7676 | 59.1156 | -123.0515
199.5156 | 123.1979 | -59.0652 | 63.7848 | 0.14954 | 0.0058361 | 0.066731 | 0.065373 | 0.13126 | 0.00062595 | -1.0724e-05 | 0.2932 | -0.0017688 | -0.0008182 | -0.0013906 | 0.0026234 | -0.0045289 | 63.8992 | 64.0137 | -0.013733 | -59.2621 | 63.7436 | -59.0973 | -59.1293 | -58.9554 | 0.050354 | -59.285 | 63.7802 | 63.739 | -59.0652 | -59.2163 | -0.032043 | -0.064086 | -0.041199 | 123.0789 | -0.19684 | -0.13275 | 0.11444 | 0 | -0.15106 | -0.004578 | 0.10986 | -0.21973 | -0.068664 | -0.045776 | 122.8088 | 122.9645 | 59.0515 | -122.9141 | 122.8455 | 122.8043 | 59.1156 | -123.0011
200.5156 | 123.2391 | -59.0652 | 63.8123 | 0.23346 | 0.0079723 | 0.065236 | 0.068364 | 0.13148 | 0.0014804 | 0.0012711 | 0.26268 | -0.00048697 | 0.0008908 | -0.0016044 | 0.0019824 | -0.0023927 | 63.8763 | 63.9816 | -0.041199 | -59.2438 | 63.7894 | -59.1064 | -59.1064 | -58.9874 | 0.041199 | -59.3536 | 63.8123 | 63.6475 | -59.111 | -59.2758 | -0.041198 | -0.041198 | -0.022888 | 123.0469 | -0.17853 | -0.13733 | 0.064087 | -0.045776 | -0.21057 | 0 | 0.07782 | -0.28839 | -0.07782 | -0.16479 | 122.8546 | 122.9416 | 59.024 | -122.9187 | 122.8775 | 122.7127 | 59.1064 | -123.0881
201.5156 | 123.2117 | -59.079 | 63.8306 | 0.19531 | 0.0062635 | 0.063954 | 0.070073 | 0.12892 | 0.0025486 | -0.00086512 | 0.25505 | -0.0026234 | -0.0027408 | -0.0016044 | 0.0019824 | -0.0019653 | 63.8626 | 64.0137 | -0.013733 | -59.2667 | 63.7573 | -59.1019 | -59.1064 | -58.9828 | 0.041199 | -59.3124 | 63.7939 | 63.6887 | -59.1156 | -59.2575 | -0.022889 | -0.027466 | -0.073242 | 123.0927 | -0.18768 | -0.16022 | 0.032044 | -0.036622 | -0.17853 | -0.036621 | 0.09613 | -0.23346 | -0.054932 | -0.14191 | 122.8363 | 122.9416 | 59.0652 | -122.937 | 122.8729 | 122.7676 | 59.1202 | -123.0881
202.5156 | 123.1705 | -59.0744 | 63.8077 | 0.21057 | 0.0090405 | 0.06545 | 0.067509 | 0.12785 | 0.0038304 | 0.0023391 | 0.22453 | -0.00070077 | -0.0025272 | -0.0003226 | 0.0019824 | -0.0026063 | 63.8397 | 63.9175 | -0.10529 | -59.3033 | 63.8031 | -59.0973 | -59.1339 | -59.0057 | 0 | -59.3399 | 63.8306 | 63.739 | -59.1248 | -59.2346 | -0.022888 | -0.059509 | -0.004577 | 122.9919 | -0.22888 | -0.16937 | 0.032044 | -0.050354 | -0.16022 | 0.022888 | 0.068665 | -0.2655 | -0.10529 | -0.068664 | 122.8775 | 122.9141 | 58.9691 | -122.9416 | 122.905 | 122.8134 | 59.0744 | -123.0423
203.5156 | 123.1842 | -59.0744 | 63.8351 | 0.19531 | 0.0039135 | 0.06545 | 0.068791 | 0.13062 | -0.00022865 | -0.00086512 | 0.2932 | -0.0013416 | -0.0018862 | -0.0013906 | -0.00036743 | -0.0041017 | 63.8763 | 63.9999 | -0.018311 | -59.2667 | 63.7344 | -59.0973 | -59.1064 | -59.0012 | 0.032043 | -59.317 | 63.7802 | 63.7344 | -59.0973 | -59.23 | -0.022888 | -0.032043 | -0.10071 | 123.0743 | -0.19226 | -0.16022 | 0.041199 | -0.022888 | -0.15564 | -0.054932 | 0.073242 | -0.24262 | -0.086975 | -0.10071 | 122.8088 | 122.9507 | 59.0561 | -122.9416 | 122.8546 | 122.8088 | 59.1064 | -123.0652
204.5156 | 123.1338 | -59.0927 | 63.826 | 0.17242 | 0.0088269 | 0.06545 | 0.067723 | 0.13062 | 0.0042576 | -0.00022432 | 0.20164 | -0.001128 | -0.000391 | 0.0007456 | 0.0019824 | -0.0041017 | 63.8214 | 63.858 | -0.12817 | -59.3079 | 63.8077 | -59.1019 | -59.1476 | -59.0378 | -0.064087 | -59.3811 | 63.8672 | 63.7115 | -59.1202 | -59.2621 | -0.009156 | -0.054932 | -0.018311 | 122.9507 | -0.21515 | -0.16022 | -0.004578 | -0.027466 | -0.16937 | 0.041198 | 0.054931 | -0.28839 | -0.11902 | -0.11444 | 122.9004 | 122.9141 | 58.9645 | -122.9736 | 122.9599 | 122.8043 | 59.0286 | -123.0881
205.5156 | 123.23 | -59.0607 | 63.8077 | 0.19531 | 0.0060497 | 0.067372 | 0.064518 | 0.13105 | 0.0031894 | 0.0031937 | 0.28557 | -0.0019824 | -0.0016726 | -0.001818 | 0.004546 | -0.0032471 | 63.8672 | 64.151 | 0.10071 | -59.23 | 63.739 | -59.0836 | -59.111 | -58.9737 | 0.068665 | -59.285 | 63.8031 | 63.7207 | -59.0973 | -59.2163 | -0.022888 | -0.050354 | -0.068664 | 123.2117 | -0.16937 | -0.11902 | 0.059509 | -0.036621 | -0.15564 | -0.004577 | 0.086975 | -0.2243 | -0.068664 | -0.086975 | 122.7997 | 122.9279 | 59.1614 | -122.9187 | 122.8638 | 122.7814 | 59.1293 | -123.024
206.5156 | 123.1064 | -59.111 | 63.8672 | 0.088501 | 0.0090405 | 0.065236 | 0.067509 | 0.13105 | 0.0038304 | 0.0014847 | 0.17876 | -0.00070077 | -0.0012454 | 0.0001046 | 0.0030506 | -0.0045289 | 63.7985 | 63.8718 | -0.13733 | -59.3033 | 63.8123 | -59.1202 | -59.1522 | -59.0744 | -0.073242 | -59.4086 | 63.8535 | 63.7573 | -59.111 | -59.2621 | -0.009155 | -0.041199 | -0.054931 | 122.9828 | -0.19226 | -0.15106 | -0.068664 | 0 | -0.15106 | -0.013732 | 0.036621 | -0.29755 | -0.14648 | -0.10986 | 122.9233 | 122.9095 | 58.9737 | -123.0194 | 122.9645 | 122.8683 | 59.0378 | -123.1293
207.5156 | 123.1888 | -59.0973 | 63.826 | 0.16479 | 0.0041271 | 0.065022 | 0.066868 | 0.13126 | -0.0017238 | -0.0017197 | 0.28557 | -0.0013416 | -0.001459 | -0.000109 | 0.0019824 | -0.0030335 | 63.8809 | 63.9999 | -0.013733 | -59.2438 | 63.7344 | -59.0973 | -59.1202 | -58.9828 | 0.059509 | -59.2941 | 63.8214 | 63.7161 | -59.111 | -59.2346 | 0 | -0.022888 | -0.091553 | 123.0972 | -0.14648 | -0.1236 | 0.054931 | -0.013733 | -0.13733 | -0.004578 | 0.11444 | -0.19684 | -0.059509 | -0.10986 | 122.8317 | 122.9782 | 59.0836 | -122.9462 | 122.9187 | 122.8134 | 59.1568 | -123.0606
208.5156 | 123.1201 | -59.1019 | 63.8443 | 0.18005 | 0.0092541 | 0.0678 | 0.069645 | 0.13105 | 0.002335 | -0.0012923 | 0.2169 | -0.0013416 | 0.001959 | 0.0003182 | 0.002196 | -0.0034607 | 63.7985 | 63.8672 | -0.14191 | -59.3308 | 63.8031 | -59.1156 | -59.1476 | -59.0652 | -0.064087 | -59.3948 | 63.8397 | 63.7802 | -59.1293 | -59.2529 | -0.013733 | -0.045776 | -0.041198 | 122.9691 | -0.22888 | -0.18311 | -0.045776 | -0.027465 | -0.15106 | -0.004577 | 0.036621 | -0.29297 | -0.14191 | -0.064087 | 122.905 | 122.9004 | 58.96 | -122.9919 | 122.9416 | 122.8821 | 59.0378 | -123.0972
209.5156 | 123.2208 | -59.0744 | 63.7939 | 0.23346 | 0.0079723 | 0.06545 | 0.065587 | 0.13062 | -0.0017238 | 0.00063028 | 0.45341 | -0.0017688 | -0.0008182 | -0.0009634 | 0.0024096 | -0.0034607 | 63.8809 | 63.9862 | -0.004578 | -59.4452 | 63.7207 | -59.1385 | -59.1339 | -58.9691 | 0.059509 | -59.317 | 63.7985 | 63.7253 | -59.1019 | -59.2163 | -0.064087 | -0.059509 | -0.073242 | 123.0606 | -0.37079 | -0.31128 | 0.086975 | -0.027466 | -0.14191 | 0.004578 | 0.10529 | -0.24262 | -0.10071 | -0.068664 | 122.7951 | 122.9553 | 59.0698 | -122.9279 | 122.8729 | 122.7997 | 59.1339 | -123.0103
210.5156 | 123.0881 | -59.1019 | 63.8489 | 0.34027 | 0.010322 | 0.067586 | 0.067509 | 0.1287 | 0.0036166 | -0.00086512 | 0.17876 | -0.00070077 | 0.0021726 | 0.0009592 | -0.00036743 | -0.00089726 | 63.7985 | 63.858 | -0.13733 | -59.3353 | 63.8031 | -59.1064 | -59.1522 | -59.0927 | -0.091553 | -59.4131 | 63.8443 | 63.7482 | -59.1476 | -59.2712 | -0.004577 | -0.050354 | -0.045776 | 122.9599 | -0.23346 | -0.1831 | -0.050354 | -0.045776 | -0.16937 | -0.004578 | 0.009156 | -0.31128 | -0.14191 | -0.10071 | 122.905 | 122.9004 | 58.9645 | -123.0011 | 122.9462 | 122.85 | 59.0103 | -123.1201
211.5156 | 123.2346 | -59.0607 | 63.8077 | 0.27161 | 0.010322 | 0.065236 | 0.067723 | 0.13126 | 0.00083955 | -1.0724e-05 | 0.25505 | -0.0019824 | 3.6404e-05 | 0.0003182 | 0.00091437 | -0.00025626 | 63.8489 | 63.9313 | -0.064087 | -59.2804 | 63.7573 | -59.1064 | -59.1339 | -58.992 | 0.036621 | -59.2941 | 63.8168 | 63.7344 | -59.1293 | -59.2117 | -0.045776 | -0.073242 | -0.050354 | 122.9919 | -0.21973 | -0.14649 | 0.041199 | -0.068664 | -0.15106 | 0.009155 | 0.068665 | -0.23346 | -0.082397 | -0.073242 | 122.818 | 122.9095 | 58.9966 | -122.9416 | 122.8775 | 122.7951 | 59.0973 | -123.0194
212.5156 | 123.0835 | -59.1019 | 63.8672 | 0.20294 | 0.010109 | 0.064595 | 0.06815 | 0.13191 | 0.0031894 | -0.0010787 | -0.24849 | -0.002196 | -0.0010318 | -0.001818 | 0.002196 | -0.0030335 | 63.7848 | 63.8351 | -0.13275 | -59.3353 | 63.7848 | -59.1156 | -59.1431 | -59.0744 | -0.07782 | -59.4086 | 63.8763 | 63.7939 | -59.111 | -59.2621 | -0.013733 | -0.041198 | -0.082397 | 122.937 | -0.23346 | -0.19226 | -0.082397 | -0.009155 | -0.16022 | 0.009156 | 0.027466 | -0.3067 | -0.14648 | -0.073242 | 122.8867 | 122.8867 | 58.9691 | -123.0103 | 122.9782 | 122.8958 | 59.024 | -123.1293
213.5156 | 123.1659 | -59.0973 | 63.8214 | 0.17242 | 0.0086133 | 0.065877 | 0.065587 | 0.12806 | 0.00041235 | 0.00063028 | 0.27794 | -0.0024096 | -0.0025272 | 0.0009592 | 0.0013416 | -0.00047006 | 63.7939 | 63.8855 | -0.11444 | -59.3124 | 63.8077 | -59.0973 | -59.1476 | -59.0332 | -0.036621 | -59.3582 | 63.8306 | 63.7436 | -59.1202 | -59.2667 | 0 | -0.050354 | -0.013733 | 122.9828 | -0.21515 | -0.16479 | -0.027466 | -0.022888 | -0.16937 | 0.009155 | 0.064087 | -0.26093 | -0.091552 | -0.07782 | 122.905 | 122.8912 | 58.9828 | -122.9691 | 122.9279 | 122.8409 | 59.0607 | -123.0881
214.5156 | 123.1018 | -59.1293 | 63.8535 | 0.065613 | 0.0069043 | 0.066945 | 0.067509 | 0.13062 | -0.001083 | -0.00022432 | 0.24742 | -0.00070077 | 0.00025 | -0.0005362 | 0.002196 | -0.0032471 | 63.8031 | 63.8626 | -0.091553 | -59.3079 | 63.8168 | -59.1248 | -59.111 | -59.0927 | -0.064087 | -59.404 | 63.8763 | 63.7939 | -59.1339 | -59.2667 | 0.004577 | 0.01831 | -0.036622 | 122.9919 | -0.17853 | -0.19684 | -0.050354 | -0.004578 | -0.13733 | 0.022888 | 0.036621 | -0.27466 | -0.13733 | -0.05951 | 122.9462 | 122.9324 | 59.0378 | -122.9645 | 123.0057 | 122.9233 | 59.0652 | -123.1201
215.5156 | 123.1659 | -59.111 | 63.8123 | 0.21057 | 0.0079723 | 0.065236 | 0.066868 | 0.13191 | -0.0019376 | -0.00065152 | 0.23979 | -0.0013416 | -0.0016726 | -0.001177 | 0.0019824 | -0.0017517 | 63.8306 | 63.9038 | -0.073242 | -59.2941 | 63.7573 | -59.1064 | -59.1476 | -59.0149 | 0.009155 | -59.3124 | 63.8077 | 63.7482 | -59.1064 | -59.2484 | 0.004578 | -0.036621 | -0.054932 | 123.0148 | -0.1831 | -0.14648 | 0.01831 | 0.004578 | -0.13733 | -0.004578 | 0.09613 | -0.20142 | -0.064087 | -0.064087 | 122.8683 | 122.9416 | 59.0378 | -122.9599 | 122.9187 | 122.8592 | 59.1202 | -123.0606
216.5156 | 123.1247 | -59.1248 | 63.8718 | 0.16479 | 0.0090405 | 0.066945 | 0.06815 | 0.13126 | 0.00062595 | 0.00020288 | 0.14824 | 0.0010082 | 0.0017454 | 0.0016 | 0.00091437 | -0.0023927 | 63.7848 | 63.858 | -0.11902 | -59.3033 | 63.7985 | -59.1293 | -59.1476 | -59.0607 | -0.65002 | -59.6008 | 63.8077 | 63.7573 | -59.1431 | -59.2438 | -0.004577 | -0.022888 | -0.073242 | 122.9828 | -0.17853 | -0.15564 | -0.086975 | -0.01831 | -0.11902 | -0.064087 | 0.064087 | -0.47607 | -0.35706 | -0.11444 | 122.9233 | 122.9095 | 59.0057 | -123.0194 | 122.9324 | 122.8821 | 58.4747 | -123.1155
217.5156 | 123.0927 | -59.1064 | 63.8535 | 0.18005 | 0.0081861 | 0.068868 | 0.067723 | 0.12913 | 0.00083955 | 0.00041648 | 0.26268 | -0.00048697 | -0.001459 | -0.000109 | -0.00036743 | -0.00089726 | 63.7939 | 63.8763 | -0.1236 | -59.317 | 63.7894 | -59.1202 | -59.1431 | -59.0652 | -0.041199 | -59.3765 | 63.8351 | 63.7619 | -59.1339 | -59.2621 | -0.013733 | -0.036621 | -0.064087 | 122.9828 | -0.21057 | -0.17395 | -0.05951 | -0.027466 | -0.15564 | -0.018311 | 0.041198 | -0.27008 | -0.11444 | -0.091553 | 122.8958 | 122.9004 | 58.9828 | -122.9965 | 122.9416 | 122.8683 | 59.0652 | -123.1155
218.5156 | 123.0972 | -59.0973 | 63.8672 | 0.012207 | 0.0098951 | 0.066304 | 0.065587 | 0.12977 | 0.001694 | -0.00022432 | 0.094833 | 0.0014356 | 0.003027 | -0.001818 | 0.0026234 | -0.0026063 | 63.8168 | 63.9038 | -0.07782 | -59.2987 | 63.8031 | -59.1019 | -59.166 | -59.1019 | -0.022888 | -59.3948 | 63.858 | 63.7985 | -59.1064 | -59.2575 | -0.004578 | -0.068665 | -0.064086 | 123.0011 | -0.20142 | -0.13275 | -0.050354 | -0.009155 | -0.16022 | -0.009155 | -0.004578 | -0.29755 | -0.13733 | -0.068664 | 122.9004 | 122.9141 | 59.0195 | -123.0331 | 122.9553 | 122.8958 | 59.0744 | -123.1247
219.5156 | 123.1705 | -59.0927 | 63.8031 | 0.17242 | 0.0079723 | 0.063954 | 0.066655 | 0.13169 | -0.001083 | -0.0017197 | 0.27031 | -0.002837 | 3.6404e-05 | 0.0013864 | 0.0026234 | -0.00089726 | 63.7985 | 63.8947 | -0.10986 | -59.3033 | 63.7894 | -59.1156 | -59.1522 | -59.0378 | -0.018311 | -59.3536 | 63.7848 | 63.7756 | -59.1202 | -59.2255 | -0.022889 | -0.05951 | -0.013733 | 122.9874 | -0.21057 | -0.15106 | -0.004578 | -0.027466 | -0.13275 | -0.018311 | 0.054931 | -0.26093 | -0.12817 | -0.027466 | 122.8821 | 122.8912 | 58.9828 | -122.9553 | 122.8775 | 122.8683 | 59.0744 | -123.0286
220.5156 | 123.1796 | -59.0744 | 63.826 | 0.15717 | 0.0056225 | 0.068013 | 0.06345 | 0.13041 | -0.0023648 | -0.0019333 | 0.32372 | -0.0015552 | 0.0015316 | -0.001177 | 0.001128 | -4.2662e-05 | 63.8351 | 63.9862 | -0.013733 | -59.2804 | 63.7115 | -59.111 | -59.1385 | -59.0195 | 0.036621 | -59.3033 | 63.8168 | 63.7299 | -59.1019 | -59.2484 | -0.036621 | -0.064087 | -0.11444 | 123.0606 | -0.20599 | -0.14191 | 0.009155 | -0.027466 | -0.17395 | -0.009156 | 0.054932 | -0.22888 | -0.054932 | -0.096131 | 122.7859 | 122.9095 | 59.0607 | -122.9645 | 122.8912 | 122.8043 | 59.111 | -123.0743
221.5156 | 123.1247 | -59.0973 | 63.8306 | 0.21057 | 0.0090405 | 0.063741 | 0.067082 | 0.12998 | -0.00022865 | -0.0027877 | 0.24742 | -0.0013416 | -0.001459 | -0.001177 | 0.002196 | -0.0043153 | 63.8031 | 63.8626 | -0.14191 | -59.3079 | 63.8077 | -59.1293 | -59.1339 | -59.0698 | -0.059509 | -59.3903 | 63.8443 | 63.7665 | -59.1202 | -59.2621 | -0.032043 | -0.036621 | -0.022888 | 122.9599 | -0.21057 | -0.17395 | -0.027465 | -0.022888 | -0.16479 | 0.013733 | 0.027466 | -0.29297 | -0.12817 | -0.064087 | 122.905 | 122.9004 | 58.9554 | -122.9645 | 122.9416 | 122.8638 | 59.0378 | -123.0927
222.5156 | 123.1155 | -59.1248 | 63.8672 | 0.0045777 | 0.012886 | 0.067586 | 0.069859 | 0.1302 | 0.003403 | -0.0015061 | 0.11772 | -0.00027337 | -0.0006046 | 0.0011728 | 5.9768e-05 | -0.00089726 | 63.8443 | 63.9084 | -0.059509 | -59.2896 | 63.8214 | -59.0927 | -59.1156 | -59.0744 | -0.004578 | -59.3903 | 63.8535 | 63.8077 | -59.1156 | -59.2667 | 0.032044 | 0.009155 | -0.045776 | 123.0331 | -0.1648 | -0.17395 | -0.022888 | 0.009155 | -0.14191 | -0.013732 | 0.050354 | -0.2655 | -0.1236 | -0.059509 | 122.9462 | 122.9691 | 59.0652 | -122.9828 | 122.9782 | 122.9324 | 59.1202 | -123.1338
223.5156 | 123.1338 | -59.1156 | 63.8626 | 1.2405 | 0.0092541 | 0.0678 | 0.069218 | 0.1302 | 0.0014804 | -0.0023605 | 0.23979 | -0.0017688 | 0.0023862 | 0.0003182 | 0.0013416 | -0.0019653 | 63.826 | 63.8351 | -0.14648 | -59.3216 | 63.8123 | -59.1248 | -59.1293 | -59.0927 | -0.082397 | -59.4086 | 63.8626 | 63.7985 | -59.1385 | -59.2575 | -0.009155 | -0.013732 | -0.050354 | 122.9507 | -0.20599 | -0.19226 | -0.036621 | -0.022888 | -0.14191 | 0 | 0.022889 | -0.29297 | -0.15106 | -0.064087 | 122.9279 | 122.9416 | 58.9691 | -122.9919 | 122.9782 | 122.9141 | 59.0332 | -123.1201
224.5156 | 123.0972 | -59.0744 | 63.8718 | -0.0030518 | 0.012672 | 0.066091 | 0.070286 | 0.13062 | 0.0012668 | -0.0021469 | 0.033798 | -5.9768e-05 | -0.000391 | -0.0030996 | 0.0036914 | -0.0017517 | 63.858 | 63.9313 | -0.018311 | -59.2758 | 63.7985 | -59.0881 | -59.1202 | -59.0515 | 0.045776 | -59.3628 | 63.8535 | 63.7894 | -59.1248 | -59.2529 | -0.013733 | -0.045776 | -0.073242 | 123.0057 | -0.20142 | -0.15564 | -0.013733 | -0.050354 | -0.17853 | -0.01831 | 0.022888 | -0.28839 | -0.10986 | -0.082397 | 122.8729 | 122.9324 | 59.0561 | -122.9919 | 122.9279 | 122.8638 | 59.1202 | -123.1247
225.5156 | 123.1934 | -59.0973 | 63.826 | 0.21057 | 0.0032727 | 0.066304 | 0.067082 | 0.12892 | -0.004501 | -1.0724e-05 | 0.3466 | -0.0024096 | -0.0025272 | -0.001177 | 5.9768e-05 | -0.00025626 | 63.8306 | 63.9679 | -0.036621 | -59.2758 | 63.7711 | -59.0744 | -59.1339 | -59.0286 | 0.013733 | -59.3262 | 63.7848 | 63.7665 | -59.0927 | -59.2209 | 0.022888 | -0.036621 | -0.054932 | 123.0652 | -0.17853 | -0.14191 | 0.004577 | 0.004578 | -0.1236 | -0.041199 | 0.068665 | -0.22888 | -0.10529 | -0.05951 | 122.8683 | 122.9279 | 59.0607 | -122.9599 | 122.8821 | 122.8638 | 59.111 | -123.0469
226.5156 | 123.111 | -59.1019 | 63.8397 | -2.3682 | 0.0092541 | 0.066091 | 0.070286 | 0.12977 | 0.0044712 | -0.0017197 | 0.23216 | 0.00058103 | -0.0012454 | 0.000532 | 0.0034778 | -0.0023927 | 63.7939 | 63.8763 | -0.1236 | -59.3216 | 63.8031 | -59.1064 | -59.1339 | -59.0927 | -0.07782 | -59.4086 | 63.858 | 63.7894 | -59.1385 | -59.2438 | -0.004577 | -0.032043 | -0.036621 | 122.9782 | -0.21973 | -0.18768 | -0.045777 | -0.036621 | -0.14191 | 0.01831 | 0.009156 | -0.3067 | -0.16479 | -0.050354 | 122.905 | 122.8958 | 58.9783 | -122.9736 | 122.9599 | 122.8912 | 59.024 | -123.0835
227.5156 | 123.0652 | -59.1156 | 63.858 | 0.042725 | 0.0098951 | 0.065022 | 0.070073 | 0.13084 | 0.001694 | -0.0019333 | 0.11009 | 0.00015383 | 0.00025 | 0.0016 | 0.0015552 | -0.0032471 | 63.8168 | 63.8992 | -0.073242 | -59.2896 | 63.8077 | -59.1202 | -59.1385 | -59.0973 | -0.036621 | -59.4131 | 63.8672 | 63.7985 | -59.1339 | -59.2529 | -0.004577 | -0.022888 | -0.050354 | 123.0148 | -0.17395 | -0.15106 | -0.041199 | -0.01831 | -0.13733 | 0.009155 | 0.018311 | -0.29755 | -0.16022 | -0.059509 | 122.9233 | 122.9324 | 59.0424 | -122.9965 | 122.9828 | 122.9141 | 59.079 | -123.111
228.5156 | 123.1384 | -59.0652 | 63.8672 | 0.050354 | 0.0096813 | 0.064809 | 0.068577 | 0.1302 | 0.0021214 | 0.00020288 | 0.026169 | -0.0013416 | 0.0004636 | -0.0003226 | 0.0017688 | -0.0015381 | 63.8626 | 63.9587 | -0.013733 | -59.2575 | 63.7939 | -59.1019 | -59.1019 | -59.0424 | 0.050354 | -59.3582 | 63.8763 | 63.8168 | -59.1156 | -59.2255 | -0.036621 | -0.036621 | -0.073242 | 123.024 | -0.19226 | -0.15564 | -0.004577 | -0.050354 | -0.16022 | 0.009156 | 0.022889 | -0.29297 | -0.13275 | -0.050354 | 122.8592 | 122.9279 | 59.0515 | -122.9691 | 122.9416 | 122.8821 | 59.1156 | -123.0927
229.5156 | 123.056 | -59.1431 | 63.8306 | 0.080872 | 0.010536 | 0.067159 | 0.068577 | 0.1302 | 0.00062595 | 0.00020288 | 0.14061 | -0.001128 | 0.0006772 | 0.0016 | 0.001128 | -0.0013245 | 63.7848 | 63.8718 | -0.09613 | -59.317 | 63.8077 | -59.0973 | -59.1339 | -59.1293 | -0.082397 | -59.4315 | 63.8672 | 63.8077 | -59.1476 | -59.2667 | 0.045776 | 0.009155 | -0.022888 | 123.0148 | -0.17395 | -0.18311 | -0.045776 | -0.004578 | -0.1236 | 0.036621 | 0.013733 | -0.28839 | -0.16479 | -0.022888 | 122.9507 | 122.9279 | 59.0469 | -122.9645 | 123.0103 | 122.9507 | 59.0607 | -123.0972
230.5156 | 123.1842 | -59.0378 | 63.8214 | 0.18768 | 0.0066907 | 0.066304 | 0.069218 | 0.13062 | -0.0025784 | -0.0032151 | 0.40001 | -0.0017688 | 0.0006772 | 0.0013864 | -0.0025036 | -0.00089726 | 63.8535 | 63.9816 | -0.013733 | -59.2621 | 63.7299 | -59.1064 | -59.111 | -59.0103 | 0.022888 | -59.3079 | 63.8168 | 63.7619 | -59.1019 | -59.2255 | -0.068664 | -0.073242 | -0.091553 | 123.0194 | -0.2243 | -0.15106 | 0.032044 | -0.064087 | -0.18768 | -0.004578 | 0.027466 | -0.27008 | -0.082397 | -0.059509 | 122.7676 | 122.8912 | 59.024 | -122.9324 | 122.8546 | 122.7997 | 59.0607 | -123.0469
231.5156 | 123.111 | -59.1202 | 63.8672 | 0.057983 | 0.0088269 | 0.065663 | 0.069432 | 0.13212 | 0.0025486 | -0.0010787 | 0.11772 | 0.00015383 | -0.0001774 | 0.0013864 | 0.0024096 | -0.0030335 | 63.8351 | 63.8901 | -0.091553 | -59.285 | 63.826 | -59.0836 | -59.1202 | -59.0927 | -0.027466 | -59.3994 | 63.8626 | 63.7848 | -59.1248 | -59.2484 | 0.036621 | 0 | -0.041198 | 123.0103 | -0.16479 | -0.16479 | -0.032043 | -0.004578 | -0.12817 | -0.004577 | 0.027466 | -0.27924 | -0.15106 | -0.082397 | 122.9462 | 122.9553 | 59.0286 | -122.9874 | 122.9828 | 122.905 | 59.0927 | -123.1155
232.5156 | 123.0972 | -59.0836 | 63.8763 | -0.10223 | 0.010322 | 0.066304 | 0.06815 | 0.1302 | 0.00041235 | -0.00043792 | -0.027237 | 0.0012218 | -0.000391 | -0.000109 | 0.0015552 | -0.0013245 | 63.8626 | 63.9542 | -0.004578 | -59.2346 | 63.8351 | -59.0836 | -59.1202 | -59.0332 | 0.064087 | -59.3491 | 63.858 | 63.7939 | -59.111 | -59.23 | 0 | -0.036621 | -0.041199 | 123.0377 | -0.15106 | -0.11444 | -0.013733 | -0.027466 | -0.14648 | -0.018311 | 0.050354 | -0.2655 | -0.11902 | -0.082398 | 122.9187 | 122.9462 | 59.079 | -122.9965 | 122.9416 | 122.8775 | 59.1476 | -123.1064
233.5156 | 123.1338 | -59.1156 | 63.858 | -0.0030518 | 0.011604 | 0.06545 | 0.069432 | 0.13062 | 0.002335 | -0.00022432 | 0.11009 | -0.001128 | 0.00025 | -0.0003226 | 0.002837 | -0.0034607 | 63.8397 | 63.9313 | -0.054932 | -59.2941 | 63.8123 | -59.0973 | -59.1293 | -59.0698 | 0.009155 | -59.3857 | 63.858 | 63.7711 | -59.1248 | -59.23 | 0.018311 | -0.013732 | -0.045776 | 123.0469 | -0.17853 | -0.16479 | -0.01831 | -0.009155 | -0.11444 | 0 | 0.045777 | -0.27008 | -0.15564 | -0.086975 | 122.9279 | 122.9553 | 59.0607 | -122.9874 | 122.9736 | 122.8867 | 59.1248 | -123.0881
234.5156 | 123.1338 | -59.0881 | 63.8809 | -0.14801 | 0.0096813 | 0.067586 | 0.069432 | 0.13447 | -1.505e-05 | 0.00084388 | -0.10353 | -0.001128 | -0.0006046 | 0.0001046 | 0.00091437 | -0.0021789 | 63.8489 | 63.945 | -0.022888 | -59.2484 | 63.8489 | -59.1064 | -59.1339 | -59.0378 | 0.086975 | -59.3308 | 63.8763 | 63.8168 | -59.0927 | -59.2072 | -0.01831 | -0.045776 | -0.032043 | 123.0331 | -0.16022 | -0.11444 | -0.032043 | -0.004577 | -0.11902 | -0.004577 | 0.050354 | -0.24262 | -0.1236 | -0.064087 | 122.937 | 122.937 | 59.0652 | -123.0148 | 122.9645 | 122.905 | 59.1751 | -123.0881
235.5156 | 123.0743 | -59.1202 | 63.858 | 0.035095 | 0.012031 | 0.065877 | 0.068791 | 0.13169 | 0.00019875 | 0.00020288 | 0.11009 | 0.00036743 | 0.0006772 | 0.0013864 | 0.0017688 | -0.00089726 | 63.8031 | 63.8901 | -0.091553 | -59.3033 | 63.826 | -59.1064 | -59.1431 | -59.1202 | -0.045776 | -59.436 | 63.8626 | 63.8123 | -59.1293 | -59.2621 | 0.013733 | -0.022888 | -0.032043 | 123.0103 | -0.18311 | -0.16022 | -0.054931 | -0.009155 | -0.14191 | 0.004578 | 0 | -0.31586 | -0.17395 | -0.045776 | 122.9462 | 122.9233 | 59.0286 | -123.0011 | 122.9828 | 122.9324 | 59.0744 | -123.1201
236.5156 | 123.1293 | -59.0698 | 63.8626 | -0.15564 | 0.0096813 | 0.065877 | 0.066441 | 0.13319 | 0.0012668 | -0.0015061 | -0.019608 | -0.0017688 | 0.0004636 | -0.0026724 | 0.00091437 | -0.00025626 | 63.8443 | 63.9359 | -0.018311 | -59.2392 | 63.826 | -59.0881 | -59.1156 | -59.0378 | 0.14648 | -59.3399 | 63.8718 | 63.8077 | -59.1202 | -59.2255 | -0.018311 | -0.045777 | -0.036621 | 123.0057 | -0.16937 | -0.1236 | -0.018311 | -0.050354 | -0.15564 | 0.009155 | 0.032043 | -0.27008 | -0.11444 | -0.054932 | 122.8958 | 122.9141 | 59.0515 | -122.9782 | 122.9416 | 122.8775 | 59.2163 | -123.0881
237.5156 | 123.0972 | -59.111 | 63.8763 | 0.088501 | 0.010536 | 0.066731 | 0.068577 | 0.1302 | 0.0027622 | -0.00086512 | 0.15587 | -0.00027337 | 0.004736 | 0.0003182 | -0.00015383 | -0.0015381 | 63.7985 | 63.9084 | -0.073242 | -59.3033 | 63.8123 | -59.0927 | -59.1339 | -59.111 | -0.009155 | -59.4086 | 63.8626 | 63.8031 | -59.1248 | -59.2484 | 0.018311 | -0.022888 | -0.064087 | 123.0194 | -0.19226 | -0.16937 | -0.07782 | -0.013733 | -0.13733 | -0.013733 | 0 | -0.29755 | -0.16022 | -0.073242 | 122.9233 | 122.9095 | 59.0378 | -123.0103 | 122.9736 | 122.9141 | 59.1019 | -123.1247
238.5156 | 123.1384 | -59.0744 | 63.9175 | -0.11749 | 0.0079723 | 0.065663 | 0.069645 | 0.13191 | 0.0010532 | -0.00022432 | -0.034867 | -0.0017688 | 0.0004636 | 0.0007456 | 0.0013416 | -0.0021789 | 63.8535 | 63.9496 | 0.018311 | -59.2392 | 63.8214 | -59.0881 | -59.1385 | -59.0286 | 0.082397 | -59.3445 | 63.8718 | 63.7894 | -59.1202 | -59.2529 | -0.013733 | -0.064087 | -0.096131 | 123.024 | -0.16479 | -0.10071 | -0.064087 | -0.045776 | -0.17853 | -0.045777 | 0.045777 | -0.27008 | -0.091552 | -0.12817 | 122.8958 | 122.9279 | 59.0927 | -123.056 | 122.9462 | 122.8638 | 59.1568 | -123.1705
239.5156 | 123.111 | -59.0973 | 63.8809 | 0.035095 | 0.012245 | 0.066731 | 0.0705 | 0.12977 | 0.0025486 | -0.00043792 | 0.12535 | 0.00058103 | -0.0010318 | 0.0009592 | 0.0015552 | -0.00089726 | 63.8123 | 63.9221 | -0.073242 | -59.2896 | 63.8123 | -59.1064 | -59.1476 | -59.079 | -0.013733 | -59.3857 | 63.8672 | 63.8031 | -59.1248 | -59.2529 | -0.009155 | -0.050354 | -0.068664 | 123.0194 | -0.19226 | -0.14191 | -0.068664 | -0.027466 | -0.15564 | -0.013733 | 0.018311 | -0.28839 | -0.13275 | -0.077819 | 122.9095 | 122.9095 | 59.024 | -123.0286 | 122.9645 | 122.9004 | 59.0836 | -123.1338
240.5156 | 123.1522 | -59.0836 | 63.8672 | -0.11749 | 0.0098951 | 0.065877 | 0.066227 | 0.13126 | -0.00065585 | -0.0012923 | -0.10353 | -0.0026234 | 0.001318 | 0.0003182 | 0.0019824 | -0.0013245 | 63.8351 | 63.9496 | -0.004578 | -59.2438 | 63.8168 | -59.1202 | -59.111 | -59.0378 | 0.086975 | -59.3353 | 63.8626 | 63.7848 | -59.1156 | -59.2438 | -0.036621 | -0.027466 | -0.050354 | 123.0331 | -0.16022 | -0.13275 | -0.032043 | -0.032044 | -0.16022 | -0.004577 | 0.045776 | -0.25177 | -0.091553 | -0.082397 | 122.9004 | 122.9187 | 59.079 | -122.9782 | 122.9462 | 122.8683 | 59.1705 | -123.111
241.5156 | 123.1293 | -59.1156 | 63.8489 | -0.048828 | 0.0098951 | 0.064382 | 0.0658 | 0.13191 | 0.0010532 | 0.00020288 | 0.24742 | -0.0017688 | 0.0008908 | 0.0016 | -0.00015383 | -4.2662e-05 | 63.7527 | 63.8443 | -0.14191 | -59.3216 | 63.8077 | -59.1248 | -59.1522 | -59.111 | -0.07782 | -59.4086 | 63.8535 | 63.7573 | -59.1202 | -59.2667 | -0.009155 | -0.036621 | -0.041199 | 122.9599 | -0.20599 | -0.16937 | -0.09613 | -0.004577 | -0.15106 | 0.004578 | 0.004578 | -0.29297 | -0.14191 | -0.091553 | 122.9233 | 122.8683 | 58.9737 | -123.0011 | 122.9691 | 122.8729 | 59.0378 | -123.1155
242.5156 | 123.1293 | -59.0836 | 63.8443 | -0.018311 | 0.010322 | 0.064809 | 0.070714 | 0.13041 | 0.0021214 | -0.0027877 | -0.042496 | -0.00070077 | 0.0004636 | -0.002886 | 0.0019824 | -0.0030335 | 63.9313 | 63.9404 | -0.009155 | -59.2621 | 63.8168 | -59.0881 | -59.1339 | -59.0515 | 0.064087 | -59.3353 | 63.8672 | 63.7985 | -59.1202 | -59.23 | -0.004578 | -0.050354 | -0.027466 | 123.024 | -0.17853 | -0.12817 | 0.086975 | -0.036621 | -0.14648 | 0.022888 | 0.032043 | -0.25177 | -0.10529 | -0.045776 | 122.9004 | 123.0148 | 59.0744 | -122.9782 | 122.9507 | 122.8821 | 59.1476 | -123.0743
243.5156 | 123.0835 | -59.111 | 63.8443 | 0.080872 | 0.012031 | 0.064809 | 0.069005 | 0.13062 | 0.00062595 | -0.0015061 | 0.17113 | 0.00058103 | 3.6404e-05 | -0.0016044 | 0.0015552 | -0.0019653 | 63.7894 | 63.8763 | -0.10071 | -59.3124 | 63.8123 | -59.1019 | -59.1476 | -59.1202 | -0.064087 | -59.4223 | 63.8535 | 63.8214 | -59.1156 | -59.2484 | 0.009155 | -0.036621 | -0.032043 | 122.9874 | -0.20142 | -0.16479 | -0.054931 | -0.004578 | -0.13733 | 0.009156 | -0.009155 | -0.31128 | -0.17395 | -0.022888 | 122.9233 | 122.9004 | 59.0103 | -122.9919 | 122.9645 | 122.9324 | 59.0469 | -123.0927
244.5156 | 123.1567 | -59.0698 | 63.8763 | -0.048828 | 0.0094677 | 0.065022 | 0.069218 | 0.12956 | 0.001694 | -0.00086512 | 0.40001 | 0.0010082 | 0.0021726 | 0.0001046 | 5.9768e-05 | -0.0013245 | 63.8443 | 63.8672 | -0.16022 | -59.3628 | 63.7802 | -59.0973 | -59.1522 | -59.0103 | 0.073242 | -59.3262 | 63.8489 | 63.8123 | -59.0836 | -59.2484 | -0.027466 | -0.082398 | -0.096131 | 122.937 | -0.29297 | -0.21057 | -0.032044 | -0.013733 | -0.17853 | -0.027466 | 0.059509 | -0.25635 | -0.07782 | -0.064087 | 122.85 | 122.9141 | 58.9096 | -123.0286 | 122.9187 | 122.8821 | 59.1431 | -123.1247
245.5156 | 123.0927 | -59.1202 | 63.8535 | 0.042725 | 0.0083997 | 0.067372 | 0.070073 | 0.12892 | 0.0021214 | -0.00086512 | 0.13298 | -5.9768e-05 | 0.0011044 | -0.000109 | 0.0013416 | -0.0015381 | 63.8168 | 63.8992 | -0.086975 | -59.285 | 63.7985 | -59.1156 | -59.1293 | -59.111 | -0.041199 | -59.404 | 63.8763 | 63.8168 | -59.1064 | -59.2346 | 0.004577 | -0.009155 | -0.054932 | 123.0194 | -0.16479 | -0.15564 | -0.036622 | 0.013733 | -0.11444 | 0.022888 | 0.009155 | -0.28381 | -0.16937 | -0.036622 | 122.9187 | 122.937 | 59.0332 | -122.9828 | 122.9965 | 122.937 | 59.079 | -123.0881
246.5156 | 123.1293 | -59.0652 | 63.8718 | -0.13275 | 0.0092541 | 0.065663 | 0.066227 | 0.12977 | 0.001694 | -0.00043792 | -0.027237 | -0.0013416 | 0.0011044 | 0.0024546 | -0.0012218 | -0.0021789 | 63.8535 | 63.9404 | 0 | -59.2392 | 63.8077 | -59.0927 | -59.1339 | -58.9142 | 0.041199 | -59.3262 | 63.8626 | 63.8168 | -59.1019 | -59.2026 | -0.027465 | -0.068664 | -0.064087 | 123.0057 | -0.17395 | -0.10529 | -0.01831 | -0.036621 | -0.13733 | -0.009155 | 0.15106 | -0.26093 | -0.1236 | -0.054932 | 122.8729 | 122.9187 | 59.0652 | -123.0057 | 122.9279 | 122.8821 | 59.1064 | -123.0743
247.5156 | 123.0927 | -59.1064 | 63.8672 | 0.050354 | 0.010963 | 0.065877 | 0.065373 | 0.13041 | 0.00062595 | -0.0017197 | 0.11009 | -5.9768e-05 | 0.001959 | -0.0016044 | 0.00091437 | -0.0011109 | 63.8031 | 63.9221 | -0.068665 | -59.285 | 63.8077 | -59.1019 | -59.1385 | -59.0973 | -0.022888 | -59.3903 | 63.8763 | 63.826 | -59.1156 | -59.2575 | 0.004577 | -0.032044 | -0.059509 | 123.0286 | -0.17853 | -0.14648 | -0.064086 | -0.009156 | -0.15106 | 0.009156 | 0.009155 | -0.28381 | -0.13275 | -0.041198 | 122.9141 | 122.9095 | 59.0378 | -123.0057 | 122.9828 | 122.9324 | 59.0836 | -123.1247
248.5156 | 123.1293 | -59.0973 | 63.8809 | -0.14801 | 0.013954 | 0.064168 | 0.070073 | 0.13062 | 0.00083955 | -0.0017197 | -0.027237 | 0.00015383 | -0.0001774 | 0.0011728 | 0.00091437 | -0.0047425 | 63.8443 | 63.9587 | -0.018311 | -59.2438 | 63.8123 | -59.1156 | -59.111 | -59.0378 | 0.082397 | -59.3124 | 63.8489 | 63.8214 | -59.0836 | -59.23 | -0.018311 | -0.013733 | -0.068664 | 123.056 | -0.14648 | -0.13275 | -0.036621 | 0.013733 | -0.13275 | -0.032043 | 0.059509 | -0.21515 | -0.082397 | -0.059509 | 122.9095 | 122.9416 | 59.079 | -122.9919 | 122.9462 | 122.9187 | 59.1797 | -123.111
249.5156 | 123.0652 | -59.1431 | 63.8992 | 0.050354 | 0.01075 | 0.065236 | 0.067723 | 0.13255 | 0.001694 | -0.00043792 | 0.23979 | 0.0014356 | 3.6404e-05 | -0.0022452 | 0.0026234 | -0.0023927 | 63.7939 | 63.8672 | -0.10529 | -59.2987 | 63.8077 | -59.0836 | -59.1339 | -59.1385 | -0.054932 | -59.4452 | 63.8672 | 63.826 | -59.1202 | -59.2438 | 0.059509 | 0.009155 | -0.091553 | 123.0103 | -0.15564 | -0.1648 | -0.10529 | 0.022888 | -0.10071 | -0.032044 | 0.004577 | -0.30212 | -0.20142 | -0.073242 | 122.9507 | 122.937 | 59.0378 | -123.0331 | 123.0103 | 122.9691 | 59.0881 | -123.143
250.5156 | 123.1384 | -59.0744 | 63.8763 | -0.12512 | 0.010536 | 0.064595 | 0.067082 | 0.13105 | -0.00022865 | -0.00022432 | 0.68993 | 0.00036743 | 0.001318 | 0.0003182 | 0.0019824 | -0.0017517 | 63.8397 | 63.9359 | -0.018311 | -59.2758 | 63.8031 | -59.079 | -59.1202 | -59.0195 | 0.07782 | -59.3216 | 63.8718 | 63.826 | -59.0836 | -59.2209 | -0.004577 | -0.045776 | -0.073242 | 123.0103 | -0.20142 | -0.15564 | -0.036621 | -0.009155 | -0.14648 | -0.004578 | 0.054932 | -0.24719 | -0.10071 | -0.050354 | 122.8775 | 122.9141 | 59.0561 | -122.9965 | 122.9462 | 122.9004 | 59.1522 | -123.0972
251.5156 | 123.1064 | -59.111 | 63.858 | 0.080872 | 0.011604 | 0.063741 | 0.070073 | 0.13191 | 0.001694 | -0.0025741 | 0.14824 | -0.00048697 | 0.003027 | -0.0005362 | -0.00058103 | -0.0021789 | 63.7985 | 63.8947 | -0.082397 | -59.2758 | 63.8077 | -59.111 | -59.1385 | -59.111 | -0.022888 | -59.3903 | 63.8443 | 63.8123 | -59.111 | -59.2438 | 0 | -0.027466 | -0.050354 | 123.0057 | -0.16479 | -0.13733 | -0.059509 | 0 | -0.13275 | -0.013733 | 0 | -0.27924 | -0.14648 | -0.045776 | 122.9187 | 122.9095 | 59.0286 | -122.9965 | 122.9553 | 122.9233 | 59.0881 | -123.1018
252.5156 | 123.056 | -59.1019 | 63.8443 | -0.079346 | 0.012459 | 0.065663 | 0.067936 | 0.13105 | 0.0012668 | -0.00065152 | 0.026169 | -0.0017688 | -0.0006046 | 0.0016 | 0.002837 | -0.0011109 | 63.8489 | 63.9587 | 0 | -59.2484 | 63.8351 | -59.0973 | -59.1064 | -59.0469 | 0.086975 | -59.3262 | 63.8672 | 63.8168 | -59.1019 | -59.23 | 0.004578 | -0.004577 | -0.009155 | 123.0606 | -0.14648 | -0.14191 | 0.004578 | 0 | -0.12817 | 0.022888 | 0.054932 | -0.2243 | -0.09613 | -0.027466 | 122.937 | 122.9507 | 59.1019 | -122.9507 | 122.9691 | 122.9187 | 59.1888 | -123.0743
253.5156 | 123.0972 | -59.1064 | 63.8672 | 0.019836 | 0.0096813 | 0.067586 | 0.071568 | 0.13126 | -0.00022865 | -0.0010787 | 0.10246 | -0.00027337 | 3.6404e-05 | -0.001177 | 0.0032642 | -0.0015381 | 63.8351 | 63.913 | -0.064087 | -59.2896 | 63.7894 | -59.0836 | -59.1385 | -59.0927 | -0.009155 | -59.3857 | 63.858 | 63.8214 | -59.111 | -59.2484 | 0.022888 | -0.032044 | -0.077819 | 123.0194 | -0.18311 | -0.15106 | -0.032043 | -0.004578 | -0.14191 | -0.009155 | 0.013733 | -0.27924 | -0.13733 | -0.045776 | 122.8958 | 122.9416 | 59.0424 | -123.0057 | 122.9645 | 122.9279 | 59.0973 | -123.1155
254.5156 | 123.1476 | -59.0927 | 63.8626 | -0.1709 | 0.010536 | 0.065022 | 0.071141 | 0.13255 | -0.00044225 | -0.00086512 | -0.042496 | -0.00091437 | -0.0023136 | -0.000109 | 0.0019824 | -0.0026063 | 63.8306 | 63.945 | -0.018311 | -59.2346 | 63.8077 | -59.0881 | -59.1293 | -59.0378 | 0.086975 | -59.3308 | 63.858 | 63.858 | -59.0881 | -59.2117 | 0.004577 | -0.036621 | -0.054932 | 123.0377 | -0.14191 | -0.10529 | -0.032044 | 0.004577 | -0.11902 | -0.004578 | 0.054931 | -0.23804 | -0.11902 | -0.004578 | 122.9004 | 122.9233 | 59.0744 | -122.9919 | 122.9507 | 122.9507 | 59.1797 | -123.0743
255.5156 | 123.0743 | -59.1019 | 63.8901 | 0.019836 | 0.011818 | 0.065022 | 0.070073 | 0.13041 | 0.0010532 | -0.0030013 | 0.11009 | -0.002196 | 0.00025 | -0.0007498 | 0.002196 | -0.0030335 | 63.7985 | 63.8763 | -0.091553 | -59.3033 | 63.7894 | -59.1156 | -59.1248 | -59.111 | -0.064087 | -59.4269 | 63.858 | 63.7985 | -59.1339 | -59.2484 | -0.013733 | -0.022888 | -0.10071 | 122.9782 | -0.20142 | -0.17853 | -0.091553 | -0.032043 | -0.14648 | -0.032044 | -0.009155 | -0.32501 | -0.17853 | -0.091553 | 122.8912 | 122.9004 | 59.0103 | -123.0148 | 122.9599 | 122.9004 | 59.0378 | -123.1384
256.5156 | 123.1476 | -59.0927 | 63.8489 | -0.071716 | 0.0064771 | 0.065877 | 0.067082 | 0.13148 | 0.0021214 | -0.0025741 | 0.033798 | -0.00048697 | -0.0012454 | 0.0013864 | 0.00091437 | -0.0021789 | 63.8535 | 63.9404 | -0.004578 | -59.2438 | 63.8214 | -59.0973 | -59.1248 | -59.1888 | 0.1831 | -59.3216 | 63.8672 | 63.826 | -59.0927 | -59.2484 | -0.004578 | -0.032044 | -0.027466 | 123.0331 | -0.15106 | -0.11902 | 0.004578 | 0 | -0.15564 | 0.01831 | -0.096131 | -0.22888 | -0.073242 | -0.022888 | 122.9141 | 122.9462 | 59.0881 | -122.9736 | 122.9599 | 122.9187 | 59.2758 | -123.0972
257.5156 | 123.0789 | -59.0881 | 63.8535 | 0.065613 | 0.01139 | 0.065877 | 0.069005 | 0.12785 | 0.0012668 | -0.0019333 | 0.087204 | -0.00027337 | 0.0011044 | 0.0009592 | 0.002837 | -0.0015381 | 63.8168 | 63.8947 | -0.073242 | -59.2941 | 63.8077 | -59.0927 | -59.1522 | -59.1064 | 0 | -59.3857 | 63.8763 | 63.8168 | -59.1019 | -59.2529 | -0.004577 | -0.064087 | -0.045777 | 122.9828 | -0.20599 | -0.14191 | -0.036622 | -0.013733 | -0.16479 | 0.022888 | -0.01831 | -0.29755 | -0.13275 | -0.036622 | 122.8958 | 122.905 | 59.0149 | -123.0057 | 122.9645 | 122.905 | 59.0881 | -123.1064
258.5156 | 123.1384 | -59.0927 | 63.8535 | -0.12512 | 0.0088269 | 0.066731 | 0.069005 | 0.13062 | 0.0014804 | -0.00065152 | -0.050125 | -0.00070077 | 0.0006772 | 0.0003182 | 0.0019824 | -0.0041017 | 63.8535 | 63.9404 | 0.004578 | -59.2392 | 63.8214 | -59.0836 | -59.111 | -59.0469 | 0.073242 | -59.3445 | 63.8626 | 63.826 | -59.1156 | -59.2209 | 0.009155 | -0.018311 | -0.032044 | 123.0331 | -0.14648 | -0.12817 | 0 | -0.022889 | -0.12817 | 0.009155 | 0.045776 | -0.25177 | -0.1236 | -0.027466 | 122.9141 | 122.9462 | 59.0973 | -122.9645 | 122.9553 | 122.9187 | 59.166 | -123.0743
259.5156 | 123.0789 | -59.1064 | 63.8855 | 0.012207 | 0.012031 | 0.063954 | 0.069005 | 0.12956 | 0.00083955 | -0.00086512 | 0.064316 | -0.0024096 | 0.0015316 | -0.000109 | 0.0015552 | -0.0015381 | 63.8168 | 63.9313 | -0.050354 | -59.285 | 63.8168 | -59.079 | -59.111 | -59.0744 | 0.013733 | -59.3765 | 63.8626 | 63.7985 | -59.1431 | -59.2346 | 0.027466 | -0.004578 | -0.068665 | 123.0377 | -0.17853 | -0.17395 | -0.068665 | -0.036621 | -0.12817 | -0.022888 | 0.032043 | -0.27008 | -0.14191 | -0.086975 | 122.9233 | 122.9233 | 59.0561 | -122.9965 | 122.9691 | 122.905 | 59.1202 | -123.1201
260.5156 | 123.1247 | -59.0973 | 63.8947 | -0.16327 | 0.0092541 | 0.066945 | 0.06815 | 0.12977 | 0.00083955 | -0.0021469 | -0.065384 | -0.0024096 | -0.0008182 | -0.0005362 | 0.00048697 | -0.0028199 | 63.8123 | 63.9359 | -0.022888 | -59.2621 | 63.8489 | -59.0927 | -59.0927 | -59.0607 | 0.059509 | -59.3216 | 63.8763 | 63.8351 | -59.111 | -59.2438 | 0.004578 | 0.004578 | -0.045776 | 123.0331 | -0.16479 | -0.16937 | -0.082397 | -0.013733 | -0.14648 | -0.01831 | 0.036621 | -0.2243 | -0.07782 | -0.059509 | 122.9462 | 122.9095 | 59.0744 | -122.9874 | 122.9736 | 122.9324 | 59.1568 | -123.1384
261.5156 | 123.0835 | -59.0744 | 63.8672 | -0.048828 | 0.010536 | 0.065022 | 0.069859 | 0.13041 | 0.0031894 | -0.0027877 | 0.079574 | -0.0015552 | 0.0004636 | -0.001177 | -0.00015383 | -0.0021789 | 63.858 | 63.9404 | -0.004578 | -59.2621 | 63.8123 | -59.1019 | -59.1156 | -59.0561 | 0.036621 | -59.3582 | 63.858 | 63.7985 | -59.1019 | -59.2438 | -0.027466 | -0.041199 | -0.054931 | 123.0148 | -0.18768 | -0.14648 | -0.009155 | -0.027466 | -0.16937 | -0.009155 | 0.018311 | -0.28381 | -0.11444 | -0.068664 | 122.8867 | 122.9324 | 59.0698 | -122.9828 | 122.9324 | 122.8729 | 59.111 | -123.111
262.5156 | 123.1476 | -59.0744 | 63.9084 | -0.16327 | 0.0088269 | 0.066304 | 0.06815 | 0.13148 | 0.00019875 | -0.0025741 | -0.065384 | -0.00048697 | -0.0008182 | 0.0016 | 0.00070077 | -0.0038879 | 63.8077 | 63.9175 | -0.041199 | -59.2712 | 63.826 | -59.1019 | -59.1156 | -59.0973 | 0.073242 | -59.3445 | 63.8763 | 63.8214 | -59.1156 | -59.2163 | -0.027466 | -0.041199 | -0.082397 | 122.9919 | -0.19684 | -0.15564 | -0.10071 | -0.041199 | -0.14191 | -0.032043 | -0.022888 | -0.27008 | -0.12817 | -0.086975 | 122.9004 | 122.8821 | 59.0332 | -123.024 | 122.9507 | 122.8958 | 59.1476 | -123.1247
263.5156 | 123.111 | -59.0881 | 63.858 | -0.033569 | 0.010963 | 0.064382 | 0.070286 | 0.12998 | 0.0010532 | -0.0021469 | 0.094833 | -0.0013416 | 0.001318 | -0.0009634 | 0.0017688 | -0.0021789 | 63.8168 | 63.913 | -0.050354 | -59.2758 | 63.8168 | -59.0927 | -59.1202 | -59.0836 | -0.009155 | -59.3857 | 63.8397 | 63.7939 | -59.1202 | -59.2484 | -0.004577 | -0.032043 | -0.041199 | 123.0011 | -0.18768 | -0.15564 | -0.041199 | -0.032043 | -0.16022 | -0.01831 | 0.004578 | -0.29755 | -0.13733 | -0.064087 | 122.905 | 122.905 | 59.0378 | -122.9782 | 122.9279 | 122.8821 | 59.079 | -123.1064
264.5156 | 123.1522 | -59.0927 | 63.8855 | -0.14801 | 0.0073315 | 0.065663 | 0.067723 | 0.13126 | 0.00062595 | -0.00086512 | -0.11116 | -0.0017688 | -0.0001774 | -0.0007498 | -0.00036743 | -0.00089726 | 63.8077 | 63.9313 | -0.022888 | -59.2438 | 63.8489 | -59.1019 | -59.1202 | -59.0469 | 0.091553 | -59.3353 | 63.8763 | 63.8351 | -59.1064 | -59.2117 | -0.009156 | -0.027466 | -0.036621 | 123.024 | -0.15106 | -0.1236 | -0.07782 | -0.013733 | -0.11902 | -0.009155 | 0.045776 | -0.24262 | -0.1236 | -0.050354 | 122.9416 | 122.9004 | 59.0698 | -123.0057 | 122.9691 | 122.9279 | 59.1843 | -123.0972
265.5156 | 123.1018 | -59.0973 | 63.8626 | -0.0030518 | 0.012459 | 0.066731 | 0.070286 | 0.13404 | 0.0012668 | -0.00086512 | 0.01091 | -0.002196 | 0.0006772 | 0.000532 | -0.00036743 | -0.0021789 | 63.8443 | 63.9542 | -0.013733 | -59.2621 | 63.7985 | -59.0881 | -59.1019 | -59.0561 | 0.027466 | -59.3399 | 63.858 | 63.8077 | -59.1156 | -59.2255 | 0.009155 | -0.004578 | -0.064087 | 123.0515 | -0.16479 | -0.16022 | -0.018311 | -0.018311 | -0.12817 | -0.004578 | 0.041199 | -0.24262 | -0.11444 | -0.054932 | 122.8958 | 122.9416 | 59.0836 | -122.9645 | 122.9553 | 122.905 | 59.1248 | -123.0881
266.5156 | 123.0743 | -59.0881 | 63.8489 | -0.15564 | 0.010109 | 0.068227 | 0.069859 | 0.13041 | 0.0014804 | -0.00043792 | -0.011978 | -0.0015552 | -0.0010318 | 0.0003182 | -0.00015383 | -0.0021789 | 63.8535 | 63.9542 | -0.004578 | -59.2392 | 63.8077 | -59.0836 | -59.1019 | -59.0424 | 0.082397 | -59.3399 | 63.8306 | 63.8077 | -59.0836 | -59.2392 | 0.004578 | -0.013733 | -0.041199 | 123.0423 | -0.15106 | -0.13733 | 0.004578 | 0.004578 | -0.15106 | -0.018311 | 0.045777 | -0.25177 | -0.10071 | -0.041199 | 122.8958 | 122.9416 | 59.0836 | -122.9507 | 122.9187 | 122.8958 | 59.1705 | -123.0881
267.5156 | 123.1247 | -59.0836 | 63.8763 | 0.89722 | 0.0079723 | 0.067159 | 0.069432 | 0.1302 | 0.002335 | -0.00065152 | 0.026169 | -0.0013416 | -0.0001774 | -0.0003226 | 0.00027337 | -4.2662e-05 | 63.8306 | 63.9633 | 0 | -59.2575 | 63.8168 | -59.0927 | -59.1385 | -59.0424 | 0.068665 | -59.3582 | 63.8535 | 63.8031 | -59.1156 | -59.2209 | -0.009155 | -0.054932 | -0.05951 | 123.0469 | -0.17395 | -0.11902 | -0.045777 | -0.032044 | -0.13733 | -0.022888 | 0.041199 | -0.27466 | -0.13733 | -0.073242 | 122.9004 | 122.9141 | 59.0836 | -123.0148 | 122.937 | 122.8867 | 59.1522 | -123.0972
268.5156 | 123.0972 | -59.0973 | 63.913 | -0.14038 | 0.0069043 | 0.067159 | 0.067509 | 0.12827 | -0.0017238 | -0.0036423 | -0.034867 | 0.00015383 | -0.000391 | -0.0013906 | -0.0016492 | -0.0013245 | 63.7939 | 63.9084 | -0.027466 | -59.2712 | 63.826 | -59.0881 | -59.1339 | -59.0881 | 0.041199 | -59.3674 | 63.8855 | 63.8306 | -59.0836 | -59.2209 | 0.009155 | -0.036621 | -0.086975 | 123.0057 | -0.17395 | -0.13733 | -0.11902 | 0.013733 | -0.1236 | -0.027466 | 0.009155 | -0.27008 | -0.14648 | -0.082398 | 122.9233 | 122.8912 | 59.0698 | -123.0469 | 122.9828 | 122.9279 | 59.1385 | -123.1338
269.5156 | 123.1476 | -59.0881 | 63.8626 | -0.13275 | 0.012031 | 0.06545 | 0.069005 | 0.13212 | 0.002335 | -0.0017197 | -0.51552 | -0.001128 | -0.0029544 | 0.0013864 | 5.9768e-05 | -0.0026063 | 63.8397 | 63.9587 | -0.009155 | -59.2438 | 63.8306 | -59.1202 | -59.1156 | -59.0469 | 0.073242 | -59.3262 | 63.8443 | 63.7985 | -59.1064 | -59.2072 | -0.032043 | -0.027466 | -0.032044 | 123.0469 | -0.15564 | -0.12817 | -0.022888 | -0.01831 | -0.11902 | -0.018311 | 0.041199 | -0.23804 | -0.11902 | -0.064087 | 122.9187 | 122.9279 | 59.079 | -122.9782 | 122.9324 | 122.8867 | 59.1614 | -123.0698
270.5156 | 123.1155 | -59.0927 | 63.8992 | -0.14038 | 0.0064771 | 0.066304 | 0.069005 | 0.12892 | -0.0021512 | -0.00065152 | -0.080643 | -0.001128 | 0.0006772 | -0.001177 | 0.00027337 | -0.00068366 | 63.8123 | 63.9359 | -0.036621 | -59.2621 | 63.8397 | -59.0698 | -59.1064 | -59.0744 | 0.054932 | -59.3308 | 63.8992 | 63.8123 | -59.1019 | -59.2346 | 0.022888 | -0.013733 | -0.059509 | 123.0286 | -0.16937 | -0.15564 | -0.086975 | -0.009156 | -0.14191 | 0 | 0.01831 | -0.23804 | -0.096131 | -0.086975 | 122.9324 | 122.905 | 59.0561 | -123.0057 | 122.9919 | 122.905 | 59.1476 | -123.1338
271.5156 | 123.1293 | -59.0836 | 63.8901 | -0.27771 | 0.01139 | 0.065877 | 0.068364 | 0.13169 | 0.003403 | -0.0010787 | 0.018539 | -0.00070077 | 0.00025 | 0.0007456 | 0.002837 | -0.0019653 | 63.8489 | 63.9816 | -0.013733 | -59.2621 | 63.8123 | -59.0927 | -59.1202 | -59.0469 | 0.045776 | -59.3536 | 63.8672 | 63.7894 | -59.1019 | -59.2392 | -0.009155 | -0.036621 | -0.07782 | 123.0652 | -0.17853 | -0.14191 | -0.041199 | -0.018311 | -0.15564 | -0.022889 | 0.036621 | -0.27008 | -0.11444 | -0.10071 | 122.8958 | 122.9324 | 59.0698 | -123.0103 | 122.9507 | 122.8729 | 59.1293 | -123.1293
272.5156 | 123.1018 | -59.0744 | 63.8992 | -0.17853 | 0.0075451 | 0.064595 | 0.066227 | 0.1302 | -0.00086945 | -0.0010787 | -0.073013 | -0.00091437 | -0.0001774 | -0.0013906 | -0.00036743 | -0.0028199 | 63.8077 | 63.9175 | -0.036621 | -59.2712 | 63.8397 | -59.0973 | -59.1156 | -59.0744 | 0.059509 | -59.3536 | 63.8718 | 63.8489 | -59.1064 | -59.2209 | -0.022888 | -0.041199 | -0.059509 | 122.9919 | -0.19684 | -0.15564 | -0.091553 | -0.032043 | -0.14648 | -0.027466 | 0 | -0.27924 | -0.13275 | -0.050354 | 122.9141 | 122.8821 | 59.0378 | -123.0148 | 122.9462 | 122.9233 | 59.1339 | -123.1201
273.5156 | 123.1384 | -59.1019 | 63.8809 | -0.02594 | 0.011604 | 0.066731 | 0.071568 | 0.12892 | 0.0027622 | -0.00086512 | 0.17876 | 0.00079463 | 0.0015316 | 0.0009592 | 0.0017688 | -0.0041017 | 63.8718 | 63.7894 | -0.17853 | -59.166 | 63.8214 | -59.1019 | -59.1385 | -59.0286 | 0.064087 | -59.3308 | 63.858 | 63.7802 | -59.1019 | -59.2346 | 0 | -0.036621 | -0.059509 | 122.8912 | -0.064087 | -0.027466 | -0.009155 | 0 | -0.13275 | -0.022888 | 0.073243 | -0.22888 | -0.096131 | -0.10071 | 122.9233 | 122.9736 | 58.9233 | -123.0194 | 122.9599 | 122.8821 | 59.166 | -123.1155
274.5156 | 123.1247 | -59.079 | 63.8992 | -0.16327 | 0.0058361 | 0.068227 | 0.067509 | 0.12977 | -0.0015102 | -0.0042831 | -0.027237 | -0.0024096 | 0.0011044 | 0.0016 | -0.0016492 | -0.0013245 | 63.7848 | 63.9313 | -0.027466 | -59.2804 | 63.8351 | -59.1202 | -59.1156 | -59.0744 | 0.041199 | -59.3582 | 63.8855 | 63.8077 | -59.1064 | -59.2255 | -0.041199 | -0.036622 | -0.064087 | 123.0103 | -0.20142 | -0.1648 | -0.11444 | -0.027466 | -0.14649 | -0.013733 | 0.004577 | -0.27924 | -0.13275 | -0.091553 | 122.9141 | 122.8638 | 59.0515 | -123.0148 | 122.9645 | 122.8867 | 59.1202 | -123.1247
275.5156 | 123.1247 | -59.0836 | 63.8626 | -0.10223 | 0.0096813 | 0.06545 | 0.069218 | 0.1302 | 0.0027622 | 0.00020288 | 0.0032804 | -0.001128 | 0.0004636 | 0.0001046 | 0.00091437 | -0.0017517 | 63.8443 | 63.9542 | 0 | -59.2484 | 63.8306 | -59.0836 | -59.1156 | -59.0424 | -0.19226 | -59.404 | 63.8351 | 63.8077 | -59.1019 | -59.2209 | 0 | -0.032044 | -0.032044 | 123.0377 | -0.16479 | -0.13275 | -0.018311 | -0.018311 | -0.13733 | -0.027466 | 0.041199 | -0.32044 | -0.18311 | -0.054932 | 122.9141 | 122.9279 | 59.0836 | -122.9782 | 122.9187 | 122.8912 | 58.8913 | -123.0835
276.5156 | 123.1247 | -59.0652 | 63.913 | -1.9943 | 0.0054089 | 0.065877 | 0.0658 | 0.12977 | -0.00065585 | -0.0030013 | 0.01091 | -0.0032642 | 0.0021726 | 0.0011728 | -0.0018628 | -0.0013245 | 63.7939 | 63.9221 | -0.018311 | -59.2712 | 63.8351 | -59.1202 | -59.1476 | -59.0836 | 0.041199 | -59.3628 | 63.8855 | 63.8077 | -59.1202 | -59.2117 | -0.054931 | -0.082397 | -0.07782 | 122.9874 | -0.20599 | -0.1236 | -0.11902 | -0.054931 | -0.14648 | -0.027466 | -0.01831 | -0.29755 | -0.15106 | -0.10529 | 122.9004 | 122.8592 | 59.0469 | -123.0606 | 122.9507 | 122.8729 | 59.1064 | -123.1247
277.5156 | 123.1522 | -59.0973 | 63.8992 | 0.30975 | 0.0090405 | 0.066945 | 0.067723 | 0.12892 | 0.00041235 | -0.00086512 | 0.018539 | -5.9768e-05 | 0.0032406 | -0.0005362 | 0.0026234 | -0.0030335 | 63.8397 | 63.9908 | -0.004578 | -59.2438 | 63.826 | -59.0836 | -59.1156 | -59.0286 | 0.073242 | -59.3308 | 63.8535 | 63.7985 | -59.1156 | -59.2438 | 0.013733 | -0.018311 | -0.073242 | 123.0881 | -0.14648 | -0.12817 | -0.059509 | -0.018311 | -0.14648 | -0.045776 | 0.068665 | -0.23346 | -0.086976 | -0.10071 | 122.9233 | 122.937 | 59.0927 | -123.0148 | 122.9507 | 122.8958 | 59.1705 | -123.143
278.5156 | 123.0927 | -59.0927 | 63.8855 | -0.14801 | 0.0054089 | 0.066731 | 0.069859 | 0.12913 | -0.00086945 | -0.0021469 | -0.073013 | -0.0017688 | -0.0006046 | -0.0009634 | 0.00091437 | -0.0032471 | 63.7985 | 63.9038 | -0.027466 | -59.2758 | 63.8306 | -59.0881 | -59.1293 | -59.0973 | 0.041199 | -59.3674 | 63.8809 | 63.7939 | -59.0927 | -59.2255 | 0.004577 | -0.036621 | -0.054932 | 122.9965 | -0.18311 | -0.14648 | -0.086975 | 0 | -0.13275 | -0.004578 | -0.004578 | -0.27466 | -0.14191 | -0.091553 | 122.9233 | 122.8912 | 59.0652 | -123.0148 | 122.9736 | 122.8867 | 59.1339 | -123.111
279.5156 | 123.1293 | -59.0836 | 63.8718 | -0.086975 | 0.01075 | 0.065877 | 0.067296 | 0.13041 | 0.00083955 | -0.0015061 | 0.62889 | -0.0017688 | 0.0008908 | 0.0001046 | 0.0015552 | -0.0030335 | 63.8351 | 63.9542 | 0 | -59.2026 | 63.7939 | -59.0973 | -59.1614 | -59.0286 | 0.082397 | -59.3124 | 63.858 | 63.7894 | -59.111 | -59.23 | -0.013733 | -0.07782 | -0.07782 | 123.0377 | -0.11902 | -0.041199 | -0.036621 | -0.027466 | -0.14648 | -0.013733 | 0.054932 | -0.22888 | -0.082397 | -0.082397 | 122.8775 | 122.9187 | 59.0836 | -123.0331 | 122.9416 | 122.8729 | 59.166 | -123.1018
280.5156 | 123.0835 | -59.079 | 63.8718 | -0.17853 | 0.0077587 | 0.06545 | 0.0705 | 0.13062 | -0.0032192 | -0.0036423 | -0.080643 | -0.002196 | -0.0021 | -0.0016044 | 0.0015552 | -0.0017517 | 63.7894 | 63.9175 | -0.013733 | -59.2758 | 63.8443 | -59.1156 | -59.1431 | -59.0652 | 0.032043 | -59.3628 | 63.8855 | 63.8031 | -59.1156 | -59.23 | -0.036622 | -0.064087 | -0.027466 | 122.9965 | -0.19684 | -0.13275 | -0.082397 | -0.036622 | -0.15106 | 0.013733 | 0.013732 | -0.28381 | -0.13275 | -0.068664 | 122.9233 | 122.8683 | 59.0652 | -123.0148 | 122.9645 | 122.8821 | 59.111 | -123.1018
281.5156 | 123.1384 | -59.0744 | 63.8901 | -0.079346 | 0.0092541 | 0.064382 | 0.069218 | 0.12913 | 0.00019875 | -0.00043792 | -0.0043486 | -0.00070077 | 0.0006772 | -0.0020316 | 0.0017688 | -0.00089726 | 63.826 | 63.9496 | 0.004578 | -59.2575 | 63.8168 | -59.0881 | -59.111 | -59.0469 | 0.11444 | -59.5322 | 63.8168 | 63.7573 | -59.1248 | -59.2392 | -0.013733 | -0.036621 | -0.073243 | 123.024 | -0.1831 | -0.14648 | -0.064087 | -0.050354 | -0.16479 | -0.073243 | 0.027466 | -0.45776 | -0.29297 | -0.13275 | 122.8912 | 122.9004 | 59.079 | -123.0011 | 122.8912 | 122.8317 | 59.1888 | -123.1293
282.5156 | 123.0881 | -59.0927 | 63.8855 | -0.15564 | 0.0062635 | 0.069081 | 0.069218 | 0.13041 | -0.0023648 | -0.0034287 | -0.13405 | -0.0013416 | 0.001318 | 0.0020272 | -0.0014356 | -0.0023927 | 63.8214 | 63.8672 | -0.032043 | -59.2987 | 63.8489 | -59.0973 | -59.1431 | -59.0698 | 0.064087 | -59.3582 | 63.8718 | 63.8123 | -59.1202 | -59.2072 | -0.004578 | -0.050354 | -0.036621 | 122.9599 | -0.20599 | -0.15564 | -0.064087 | -0.027466 | -0.11444 | -0.013733 | 0.022888 | -0.2655 | -0.15106 | -0.073242 | 122.9416 | 122.9141 | 59.0607 | -123.0286 | 122.9645 | 122.905 | 59.1568 | -123.0927
283.5156 | 123.1338 | -59.0836 | 63.8718 | -0.1709 | 0.0086133 | 0.066518 | 0.069645 | 0.13126 | 0.00062595 | -0.0030013 | -0.088272 | -0.0024096 | 0.0011044 | -0.0003226 | 0.001128 | -0.0021789 | 63.8351 | 63.9404 | 0 | -59.2484 | 63.8397 | -59.0927 | -59.1064 | -59.0424 | 0.073242 | -59.3216 | 63.8535 | 63.8031 | -59.1156 | -59.23 | -0.009155 | -0.022888 | -0.032043 | 123.024 | -0.16479 | -0.14191 | -0.036621 | -0.032044 | -0.14648 | -0.01831 | 0.041199 | -0.23804 | -0.091552 | -0.068664 | 122.9233 | 122.9187 | 59.0836 | -122.9782 | 122.937 | 122.8867 | 59.1568 | -123.1018
284.5156 | 123.1201 | -59.0607 | 63.8855 | -0.17853 | 0.0060497 | 0.068654 | 0.067936 | 0.13105 | 0.00019875 | -0.0010787 | -0.034867 | -0.0017688 | -0.0016726 | -0.0022452 | 0.00048697 | -0.0011109 | 63.7939 | 63.9221 | -0.036621 | -59.2758 | 63.8489 | -59.079 | -59.1156 | -59.079 | 0.050354 | -59.3582 | 63.8672 | 63.8168 | -59.1019 | -59.2209 | -0.01831 | -0.054932 | -0.036621 | 122.9828 | -0.21515 | -0.16022 | -0.091553 | -0.041199 | -0.16022 | -0.018311 | -0.01831 | -0.29755 | -0.13733 | -0.068665 | 122.9095 | 122.8546 | 59.024 | -123.0011 | 122.9279 | 122.8775 | 59.111 | -123.1064
285.5156 | 123.1247 | -59.1019 | 63.8718 | -0.048828 | 0.0090405 | 0.0678 | 0.068791 | 0.13105 | 0.0010532 | -0.0015061 | 0.40001 | -0.00027337 | 0.0017454 | 0.0001046 | 5.9768e-05 | -0.0017517 | 63.8397 | 63.9725 | 0 | -59.2072 | 63.8168 | -59.0881 | -59.1476 | -59.0149 | 0.091553 | -59.3079 | 63.8626 | 63.8031 | -59.0927 | -59.2392 | 0.013733 | -0.045776 | -0.054932 | 123.0743 | -0.10528 | -0.059509 | -0.032043 | 0.009156 | -0.13733 | -0.009155 | 0.086975 | -0.20599 | -0.068664 | -0.068664 | 122.9187 | 122.9416 | 59.1019 | -123.0194 | 122.9645 | 122.905 | 59.1934 | -123.111
286.5156 | 123.1018 | -59.0973 | 63.8947 | 0.12665 | 0.012031 | 0.065236 | 0.068364 | 0.13126 | -1.505e-05 | -0.0030013 | 0.25505 | -0.00027337 | 0.001318 | 0.0009592 | 0.0015552 | -0.0017517 | 63.6749 | 63.5422 | -0.2655 | -59.1385 | 63.7939 | -59.1248 | -59.111 | -59.1248 | -0.059509 | -59.4223 | 63.8626 | 63.7985 | -59.1202 | -59.2575 | -0.027466 | -0.013733 | -0.10071 | 122.6395 | -0.041199 | -0.027466 | -0.21973 | -0.022888 | -0.16022 | -0.032043 | -0.027466 | -0.32501 | -0.1648 | -0.09613 | 122.8912 | 122.7722 | 58.8318 | -123.0057 | 122.9599 | 122.8958 | 59.0378 | -123.1522
287.5156 | 123.1293 | -59.0652 | 63.8901 | -0.056458 | 0.01075 | 0.065236 | 0.067723 | 0.12892 | 0.0014804 | 0.00041648 | -0.011978 | 0.0012218 | -0.0006046 | 0.000532 | 0.0036914 | -0.0038879 | 63.8397 | 63.9404 | -0.013733 | -59.23 | 63.8123 | -59.1019 | -59.1156 | -59.2255 | 0.2655 | -59.3353 | 63.8443 | 63.7985 | -59.0698 | -59.2117 | -0.036621 | -0.050354 | -0.07782 | 123.0057 | -0.16479 | -0.11444 | -0.050354 | -0.004577 | -0.14648 | -0.045777 | -0.16022 | -0.27008 | -0.1236 | -0.091553 | 122.8775 | 122.905 | 59.0515 | -123.0057 | 122.9095 | 122.8638 | 59.3308 | -123.1018
288.5156 | 123.1293 | -59.0744 | 63.8947 | -0.13275 | 0.0049817 | 0.06545 | 0.067296 | 0.12934 | 0.0027622 | -0.0021469 | -0.073013 | -0.0015552 | 0.001318 | 0.0003182 | 0.00070077 | -0.0032471 | 63.7894 | 63.9221 | -0.036621 | -59.2575 | 63.826 | -59.0744 | -59.1293 | -59.079 | 0.068665 | -59.3353 | 63.8947 | 63.8123 | -59.1064 | -59.2117 | 0 | -0.054931 | -0.068664 | 122.9965 | -0.1831 | -0.12817 | -0.10528 | -0.032043 | -0.13733 | 0 | -0.004577 | -0.26093 | -0.1236 | -0.082397 | 122.9004 | 122.8638 | 59.0378 | -123.024 | 122.9691 | 122.8867 | 59.1431 | -123.1064
289.5156 | 123.0515 | -59.1064 | 63.8718 | -0.11749 | 0.0090405 | 0.063527 | 0.069005 | 0.13041 | 0.00041235 | -0.00043792 | 0.018539 | -0.0017688 | 0.001959 | 0.0009592 | -0.00036743 | -0.0030335 | 63.8351 | 63.9587 | -0.004578 | -59.2484 | 63.8397 | -59.0927 | -59.1385 | -59.0378 | 0.073242 | -59.3262 | 63.8397 | 63.7802 | -59.1064 | -59.2255 | 0.013733 | -0.032044 | -0.032043 | 123.0652 | -0.14191 | -0.10986 | -0.036621 | 0 | -0.11902 | -0.032043 | 0.068664 | -0.21973 | -0.10071 | -0.091553 | 122.9462 | 122.9416 | 59.1019 | -123.0103 | 122.9462 | 122.8867 | 59.1797 | -123.0972
290.5156 | 123.1155 | -59.0698 | 63.9221 | -0.10986 | 0.0086133 | 0.065236 | 0.069218 | 0.13255 | -0.00022865 | -0.0027877 | -0.065384 | -0.001128 | -0.0001774 | 0.000532 | 0.00091437 | 0.0012389 | 63.7985 | 63.9038 | -0.027466 | -59.2758 | 63.8306 | -59.0881 | -59.111 | -59.079 | 0.064087 | -59.3536 | 63.8901 | 63.8077 | -59.0836 | -59.2163 | -0.018311 | -0.041199 | -0.091553 | 122.9736 | -0.20599 | -0.16479 | -0.1236 | -0.013733 | -0.14649 | -0.032043 | -0.009155 | -0.28381 | -0.13733 | -0.11444 | 122.9004 | 122.8683 | 59.0424 | -123.0331 | 122.9599 | 122.8775 | 59.1339 | -123.1384
291.5156 | 123.2117 | -59.0652 | 63.8306 | 0.17242 | 0.0088269 | 0.066091 | 0.061955 | 0.12977 | -0.002792 | -0.0027877 | 0.33134 | -0.0013416 | -0.001459 | -0.0013906 | 0.0024096 | -0.0034607 | 63.8489 | 63.9954 | -0.027466 | -59.2575 | 63.7573 | -59.0744 | -59.1202 | -59.0103 | 0.045776 | -59.2987 | 63.8168 | 63.7207 | -59.1064 | -59.2438 | -0.009155 | -0.054931 | -0.073242 | 123.0606 | -0.19226 | -0.13733 | 0.018311 | -0.041198 | -0.17853 | -0.013733 | 0.054932 | -0.23346 | -0.054932 | -0.10986 | 122.8226 | 122.9141 | 59.0378 | -122.9507 | 122.8821 | 122.7859 | 59.111 | -123.0743
292.5156 | 123.0789 | -59.0973 | 63.8947 | -0.20905 | 0.0069043 | 0.068013 | 0.067296 | 0.12998 | 0.0014804 | -0.0023605 | -0.042496 | -0.00027337 | -0.0016726 | -0.000109 | 0.001128 | -0.0026063 | 63.8077 | 63.9038 | -0.036621 | -59.2621 | 63.8397 | -59.0881 | -59.111 | -59.0744 | 0.050354 | -59.3582 | 63.8947 | 63.8214 | -59.1156 | -59.198 | 0.009155 | -0.013733 | -0.054931 | 123.0011 | -0.16479 | -0.15106 | -0.086975 | -0.018311 | -0.10071 | 0 | 0.022888 | -0.26093 | -0.16022 | -0.073242 | 122.937 | 122.905 | 59.0607 | -123.0057 | 122.9919 | 122.9187 | 59.1476 | -123.0927
293.5156 | 123.1384 | -59.0927 | 63.8489 | -0.056458 | 0.01139 | 0.064382 | 0.071141 | 0.13255 | 0.0010532 | 0.0012711 | -0.18745 | -0.0015552 | 0.0004636 | 0.0007456 | 0.0015552 | -0.0036743 | 63.6887 | 63.8443 | -0.022888 | -59.1934 | 63.8535 | -59.1064 | -59.1293 | -59.0286 | 0.068665 | -59.3262 | 63.8672 | 63.7939 | -59.1019 | -59.2438 | -0.013733 | -0.036621 | 0.004578 | 122.937 | -0.10071 | -0.064087 | -0.16022 | -0.009156 | -0.15106 | 0.01831 | 0.064087 | -0.23346 | -0.082398 | -0.054932 | 122.9462 | 122.7814 | 59.0698 | -122.9782 | 122.9599 | 122.8867 | 59.1614 | -123.0927
294.5156 | 123.1064 | -59.0927 | 63.9038 | -0.15564 | 0.0041271 | 0.066945 | 0.067936 | 0.13233 | -0.0017238 | -0.0015061 | -0.050125 | -0.00091437 | 0.0011044 | -0.0005362 | -0.00079463 | -0.0013245 | 63.7894 | 63.9221 | -0.041199 | -59.2667 | 63.8443 | -59.1019 | -59.1293 | -59.0744 | 0.050354 | -59.3719 | 63.8809 | 63.8351 | -59.0927 | -59.2072 | -0.009156 | -0.036621 | -0.05951 | 123.0148 | -0.17395 | -0.13733 | -0.11444 | 0 | -0.11444 | -0.022889 | 0.01831 | -0.27924 | -0.1648 | -0.068665 | 122.937 | 122.8821 | 59.0515 | -123.0331 | 122.9736 | 122.9279 | 59.1431 | -123.111
295.5156 | 123.0972 | -59.1156 | 63.8718 | 0.035095 | 0.0094677 | 0.065877 | 0.071141 | 0.12742 | 0.0012668 | -0.00043792 | 0.14824 | -0.001128 | 0.0008908 | 0.000532 | -0.00015383 | -0.0026063 | 63.7756 | 63.8992 | -0.064087 | -59.317 | 63.8214 | -59.1019 | -59.1293 | -59.079 | -0.045776 | -59.4086 | 63.8397 | 63.7802 | -59.1202 | -59.2209 | 0.013733 | -0.013732 | -0.050354 | 123.0148 | -0.20142 | -0.18768 | -0.09613 | -0.004577 | -0.10529 | -0.032043 | 0.036622 | -0.29297 | -0.18768 | -0.091553 | 122.937 | 122.8912 | 59.0515 | -123.0011 | 122.9553 | 122.8958 | 59.0698 | -123.0927
296.5156 | 123.2025 | -59.0744 | 63.8123 | 0.18768 | 0.0047681 | 0.067586 | 0.066014 | 0.1302 | -0.002792 | 0.0016983 | 0.31609 | -0.001128 | -0.0025272 | -0.0007498 | -0.00058103 | 0.0010253 | 63.8443 | 63.9954 | -0.018311 | -59.2484 | 63.739 | -59.1019 | -59.079 | -58.992 | 0.036621 | -59.2987 | 63.7848 | 63.7024 | -59.1156 | -59.2255 | -0.027466 | -0.004577 | -0.073242 | 123.0698 | -0.17395 | -0.16937 | 0.032043 | -0.041199 | -0.15106 | -0.027466 | 0.082398 | -0.2243 | -0.073242 | -0.10986 | 122.8134 | 122.9187 | 59.0561 | -122.8912 | 122.8592 | 122.7768 | 59.111 | -123.0377
297.5156 | 123.1155 | -59.1064 | 63.8626 | -0.14038 | 0.011604 | 0.065663 | 0.070714 | 0.13212 | 0.0029758 | -0.0012923 | -0.034867 | -0.0024096 | 0.0006772 | -0.0003226 | 0.0024096 | -0.0047425 | 63.858 | 63.9496 | 0.013733 | -59.2392 | 63.8626 | -59.0927 | -59.1064 | -59.0332 | 0.073242 | -59.3353 | 63.8855 | 63.7665 | -59.111 | -59.2621 | 0.013733 | 0 | 0 | 123.056 | -0.13275 | -0.13275 | -0.004578 | -0.004578 | -0.15564 | 0.022888 | 0.073242 | -0.22888 | -0.073242 | -0.096131 | 122.9691 | 122.9645 | 59.1202 | -122.9691 | 122.9919 | 122.8729 | 59.1797 | -123.1247
298.5156 | 123.1567 | -59.0698 | 63.8992 | -0.16327 | 0.0066907 | 0.068868 | 0.067936 | 0.12998 | 0.00041235 | -0.0030013 | -0.080643 | -0.0015552 | 0.0025998 | -0.0009634 | -0.0018628 | -0.0034607 | 63.8123 | 63.9038 | -0.022888 | -59.2621 | 63.8306 | -59.1064 | -59.1156 | -59.0744 | 0.068665 | -59.3582 | 63.8947 | 63.8123 | -59.0836 | -59.1888 | -0.036621 | -0.045777 | -0.068665 | 122.9736 | -0.19226 | -0.14648 | -0.086975 | -0.013733 | -0.11902 | -0.004578 | -0.004578 | -0.28839 | -0.16937 | -0.086975 | 122.9004 | 122.8821 | 59.0469 | -123.0148 | 122.9645 | 122.8821 | 59.1385 | -123.0881
299.5156 | 123.1476 | -59.0973 | 63.8535 | 1.6983 | 0.0094677 | 0.068227 | 0.069432 | 0.12977 | 0.0010532 | -0.00022432 | 0.071945 | 0.00015383 | 3.6404e-05 | 0.0028818 | 0.002196 | -0.0026063 | 63.8626 | 63.9496 | -0.004578 | -59.2575 | 63.8443 | -59.0652 | -59.1019 | -59.0286 | 0.068665 | -59.3399 | 63.858 | 63.7756 | -59.1385 | -59.2392 | 0.032043 | -0.004578 | -0.009156 | 123.0469 | -0.16022 | -0.15564 | 0.009155 | -0.041199 | -0.14191 | 0.004577 | 0.068665 | -0.24262 | -0.10071 | -0.07782 | 122.9416 | 122.9599 | 59.0927 | -122.9553 | 122.9553 | 122.8729 | 59.166 | -123.0927
300.5156 | 123.0789 | -59.0973 | 63.8947 | -0.14038 | 0.0098951 | 0.067586 | 0.070286 | 0.1287 | -0.0012966 | -0.0021469 | -0.12642 | -0.0026234 | 3.6404e-05 | -0.000109 | -0.00058103 | -0.0011109 | 63.8031 | 63.9267 | -0.045776 | -59.2804 | 63.8351 | -59.1019 | -59.1385 | -59.079 | 0.068665 | -59.3628 | 63.9084 | 63.8123 | -59.1202 | -59.2209 | -0.004578 | -0.041199 | -0.059509 | 123.024 | -0.18311 | -0.14191 | -0.091552 | -0.022888 | -0.1236 | 0.013733 | 0.018311 | -0.2655 | -0.14191 | -0.082397 | 122.9324 | 122.9004 | 59.0515 | -123.0331 | 123.0057 | 122.9095 | 59.166 | -123.1155
301.5156 | 123.2025 | -59.0698 | 63.8214 | -0.6897 | 0.0058361 | 0.0678 | 0.064946 | 0.12998 | -0.0047146 | -0.00086512 | 0.36186 | -0.002196 | 0.00025 | -0.0005362 | 0.0015552 | -0.0021789 | 63.8443 | 64.0045 | 0 | -59.2575 | 63.7344 | -59.0973 | -59.1202 | -58.9783 | 0.032043 | -59.2896 | 63.7894 | 63.7161 | -59.1248 | -59.2392 | -0.027466 | -0.050354 | -0.086975 | 123.0743 | -0.18768 | -0.13733 | 0.022888 | -0.054932 | -0.16937 | -0.032043 | 0.091553 | -0.21973 | -0.050354 | -0.10529 | 122.8043 | 122.9141 | 59.0698 | -122.9416 | 122.8592 | 122.7859 | 59.1019 | -123.0606
302.5156 | 123.0789 | -59.1019 | 63.8763 | -0.079346 | 0.0060497 | 0.067159 | 0.070714 | 0.13233 | -0.00044225 | -0.0025741 | -0.050125 | -0.00048697 | -0.0001774 | -0.001177 | 0.00027337 | -0.0011109 | 63.8214 | 63.9084 | -0.036621 | -59.2804 | 63.8306 | -59.1019 | -59.1293 | -59.0744 | 0.050354 | -59.3719 | 63.8947 | 63.8351 | -59.1019 | -59.2072 | 0 | -0.027465 | -0.045777 | 123.0103 | -0.17853 | -0.15106 | -0.054932 | 0 | -0.10528 | 0.01831 | 0.027466 | -0.27008 | -0.1648 | -0.041199 | 122.9324 | 122.9233 | 59.0652 | -123.0057 | 122.9965 | 122.937 | 59.1522 | -123.0835
303.5156 | 123.0194 | -59.0881 | 63.8535 | -0.10986 | 0.010109 | 0.067159 | 0.070714 | 0.12998 | 0.00062595 | -0.0015061 | -0.027237 | -0.0017688 | 0.00025 | -0.0007498 | 0.0024096 | -0.0021789 | 63.8489 | 63.945 | -0.004578 | -59.2438 | 63.826 | -59.0881 | -59.1339 | -59.0286 | 0.054932 | -59.3491 | 63.8855 | 63.7985 | -59.111 | -59.2621 | 0 | -0.045776 | -0.027466 | 123.0331 | -0.15564 | -0.10986 | -0.004578 | -0.022888 | -0.17395 | 0.032043 | 0.05951 | -0.26093 | -0.086975 | -0.054932 | 122.9141 | 122.937 | 59.0836 | -122.9874 | 122.9736 | 122.8867 | 59.1431 | -123.1155
304.5156 | 123.0927 | -59.0927 | 63.8992 | -0.14801 | 0.0079723 | 0.067159 | 0.068791 | 0.12977 | -0.00086945 | -0.0032151 | -0.027237 | 0.00015383 | 0.0011044 | -0.0005362 | 0.0017688 | -0.0028199 | 63.8077 | 63.913 | -0.027466 | -59.2529 | 63.8626 | -59.0744 | -59.1248 | -59.0652 | 0.068665 | -59.3628 | 63.9038 | 63.8168 | -59.0881 | -59.2209 | 0.01831 | -0.032044 | -0.036621 | 123.0057 | -0.16022 | -0.12817 | -0.091553 | 0.004577 | -0.12817 | 0.004578 | 0.027465 | -0.27008 | -0.14191 | -0.082398 | 122.9553 | 122.9004 | 59.0652 | -123.024 | 122.9965 | 122.9095 | 59.1614 | -123.1201
305.5156 | 123.1338 | -59.0744 | 63.8763 | -0.033569 | 0.01139 | 0.065877 | 0.067936 | 0.13041 | 0.0048984 | -0.00043792 | 0.018539 | -0.00070077 | 0.0004636 | -0.0003226 | -0.00036743 | -0.00089726 | 63.6566 | 64.0869 | -0.009155 | -59.2484 | 63.8168 | -59.0881 | -59.1064 | -59.0149 | 0.059509 | -59.3308 | 63.858 | 63.7894 | -59.1339 | -59.2346 | -0.013733 | -0.032043 | -0.05951 | 123.1613 | -0.17395 | -0.14191 | -0.21973 | -0.059509 | -0.16022 | -0.018311 | 0.059509 | -0.25635 | -0.096131 | -0.086975 | 122.8912 | 122.731 | 59.0652 | -122.9828 | 122.9324 | 122.8638 | 59.1339 | -123.111
306.5156 | 123.0927 | -59.0881 | 63.8901 | -0.14801 | 0.0086133 | 0.066731 | 0.069859 | 0.13126 | -0.0023648 | -0.0025741 | -0.065384 | -0.0015552 | -0.0018862 | -0.0003226 | 0.001128 | -0.0026063 | 63.7756 | 63.9175 | -0.027466 | -59.2667 | 63.8351 | -59.0881 | -59.1202 | -59.0836 | 0.054932 | -59.3674 | 63.8992 | 63.8123 | -59.1064 | -59.2392 | 0 | -0.032043 | -0.054932 | 123.0057 | -0.17853 | -0.14648 | -0.11444 | -0.01831 | -0.15106 | 0.009155 | 0.004578 | -0.27924 | -0.12817 | -0.07782 | 122.9233 | 122.8638 | 59.0607 | -123.0103 | 122.9874 | 122.9004 | 59.1431 | -123.1293
307.5156 | 123.111 | -59.0973 | 63.8672 | -0.12512 | 0.0098951 | 0.066091 | 0.071354 | 0.13105 | 0.0025486 | -0.00022432 | -0.027237 | -0.001128 | 0.0006772 | 0.0018136 | -0.00036743 | -0.0030335 | 63.8351 | 63.9679 | -0.013733 | -59.2529 | 63.826 | -59.0881 | -59.1293 | -58.9554 | 0.059509 | -59.3445 | 63.8535 | 63.8031 | -59.0973 | -59.2072 | 0.009155 | -0.032043 | -0.041198 | 123.0652 | -0.15564 | -0.1236 | -0.032043 | 0 | -0.10986 | -0.013732 | 0.14191 | -0.24719 | -0.13733 | -0.064086 | 122.9233 | 122.9324 | 59.0836 | -122.9965 | 122.9507 | 122.9004 | 59.1568 | -123.0743
308.5156 | 123.0881 | -59.0881 | 63.8855 | -0.34637 | 0.0056225 | 0.06844 | 0.069218 | 0.13041 | -0.0012966 | -0.0027877 | -0.073013 | -0.001128 | -0.0016726 | 0.0001046 | -0.0010082 | -0.0011109 | 63.7802 | 63.9267 | -0.018311 | -59.2712 | 63.8214 | -59.0973 | -59.1248 | -59.0836 | 0.059509 | -59.3491 | 63.8718 | 63.8306 | -59.1019 | -59.2255 | -0.009155 | -0.036621 | -0.064087 | 123.0148 | -0.1831 | -0.14648 | -0.10529 | -0.013733 | -0.13733 | -0.013733 | 0.004578 | -0.26093 | -0.1236 | -0.054932 | 122.9095 | 122.8683 | 59.0698 | -123.0103 | 122.9599 | 122.9187 | 59.1476 | -123.111
309.5156 | 123.1338 | -59.0881 | 63.8855 | -0.56763 | 0.012459 | 0.067159 | 0.06815 | 0.1302 | 0.0046848 | -0.0017197 | 0.026169 | -0.0017688 | 0.0008908 | 0.0009592 | 0.0019824 | -0.0023927 | 63.858 | 63.9679 | -0.013733 | -59.2392 | 63.7985 | -59.0836 | -59.111 | -59.0378 | 0.054932 | -59.3308 | 63.826 | 63.7894 | -59.0973 | -59.2117 | 0.004578 | -0.022888 | -0.086975 | 123.056 | -0.15106 | -0.12817 | -0.027466 | -0.009155 | -0.1236 | -0.059509 | 0.050354 | -0.24262 | -0.11902 | -0.09613 | 122.8867 | 122.9462 | 59.0744 | -122.9965 | 122.9141 | 122.8775 | 59.1431 | -123.0972
310.5156 | 123.0972 | -59.1019 | 63.8992 | -0.18616 | 0.0071179 | 0.068013 | 0.068364 | 0.13105 | -0.0038602 | -0.00043792 | 0.19402 | -0.001128 | -0.000391 | 0.000532 | -0.00079463 | -0.0017517 | 63.7756 | 63.9771 | 0.10986 | -59.1797 | 63.858 | -59.0744 | -59.1385 | -59.0836 | 0.086975 | -59.3582 | 63.8947 | 63.8443 | -59.1202 | -59.2117 | 0.027466 | -0.036621 | -0.041199 | 123.0789 | -0.077819 | -0.041198 | -0.1236 | -0.01831 | -0.10986 | -0.004578 | 0.018311 | -0.25635 | -0.14648 | -0.054932 | 122.9599 | 122.8775 | 59.2117 | -123.0377 | 122.9965 | 122.9462 | 59.1888 | -123.111
311.5156 | 123.1338 | -59.0836 | 63.8992 | -0.086975 | 0.0098951 | 0.066304 | 0.068791 | 0.12913 | 0.00062595 | 0.0012711 | -0.29427 | -0.0013416 | -0.0010318 | -0.001177 | 0.0019824 | -0.0019653 | 63.6566 | 63.8214 | -0.027466 | -59.1934 | 63.8123 | -59.1019 | -59.1293 | -59.0424 | 0.086975 | -59.3262 | 63.8672 | 63.7802 | -59.1064 | -59.2392 | -0.018311 | -0.045776 | -0.086975 | 122.905 | -0.10986 | -0.064087 | -0.24262 | -0.022888 | -0.15564 | -0.032044 | 0.041199 | -0.24262 | -0.086975 | -0.11902 | 122.8958 | 122.7402 | 59.0561 | -123.0286 | 122.9507 | 122.8638 | 59.1705 | -123.1384
312.5156 | 123.0972 | -59.0607 | 63.8992 | -0.10223 | 0.0081861 | 0.066091 | 0.070073 | 0.12956 | 0.00083955 | -0.0010787 | -0.088272 | -0.0017688 | -0.0001774 | -0.0005362 | -0.00015383 | -0.00089726 | 63.7848 | 63.9038 | -0.036621 | -59.2621 | 63.8443 | -59.0927 | -59.1293 | -59.0698 | 0.054932 | -59.3628 | 63.8763 | 63.8306 | -59.1293 | -59.23 | -0.032043 | -0.068664 | -0.054932 | 122.9645 | -0.20142 | -0.13275 | -0.11444 | -0.068664 | -0.16937 | -0.022888 | -0.009155 | -0.30212 | -0.13275 | -0.068665 | 122.905 | 122.8455 | 59.024 | -123.0286 | 122.937 | 122.8912 | 59.1156 | -123.1293
313.5156 | 123.143 | -59.0698 | 63.8809 | -0.071716 | 0.010109 | 0.066945 | 0.068577 | 0.13383 | 0.0012668 | -0.0019333 | -0.057755 | -0.0013416 | 0.0006772 | 0.0013864 | 0.004546 | -0.0017517 | 63.8443 | 63.9587 | 0 | -59.2438 | 63.8168 | -59.0927 | -59.1156 | -59.1843 | 0.20599 | -59.2804 | 63.8443 | 63.8031 | -59.1339 | -59.2209 | -0.022888 | -0.045777 | -0.064087 | 123.0286 | -0.17395 | -0.12817 | -0.036621 | -0.064087 | -0.15106 | -0.036621 | -0.11444 | -0.21057 | -0.05951 | -0.077819 | 122.8867 | 122.9141 | 59.0698 | -122.9965 | 122.9141 | 122.8729 | 59.2758 | -123.1018
314.5156 | 123.0789 | -59.0927 | 63.913 | 0.21057 | 0.0073315 | 0.069509 | 0.06815 | 0.12956 | -0.00086945 | -0.00022432 | -0.050125 | -0.0030506 | 3.6404e-05 | -0.0009634 | 0.00048697 | -0.0030335 | 63.7939 | 63.9359 | -0.036621 | -59.2712 | 63.8535 | -59.0881 | -59.111 | -59.079 | 0.041199 | -59.3582 | 63.9038 | 63.8031 | -59.1064 | -59.2392 | 0.004577 | -0.018311 | -0.059509 | 123.0286 | -0.17853 | -0.16022 | -0.11902 | -0.013733 | -0.14648 | -0.009155 | 0.013733 | -0.2655 | -0.11902 | -0.10986 | 122.9462 | 122.8867 | 59.0561 | -123.024 | 122.9965 | 122.8958 | 59.1339 | -123.1522
315.5156 | 123.1384 | -59.0744 | 63.8855 | -0.14801 | 0.0083997 | 0.067372 | 0.068791 | 0.13361 | 0.0012668 | -0.00086512 | -0.088272 | -0.0015552 | -0.000391 | 0.000532 | 0.0015552 | -0.0021789 | 63.826 | 63.9496 | -0.013733 | -59.2438 | 63.826 | -59.0927 | -59.1339 | -59.0424 | 0.07782 | -59.3216 | 63.8809 | 63.7985 | -59.1019 | -59.2255 | -0.01831 | -0.059509 | -0.059509 | 123.024 | -0.16937 | -0.10986 | -0.059509 | -0.027466 | -0.15106 | -0.004578 | 0.032044 | -0.24719 | -0.09613 | -0.086975 | 122.9004 | 122.9004 | 59.0607 | -123.0194 | 122.9553 | 122.8729 | 59.1522 | -123.111
316.5156 | 123.0927 | -59.0927 | 63.9175 | -0.10223 | 0.0051953 | 0.068013 | 0.068364 | 0.12956 | -0.0030056 | -0.0042831 | 1.0332 | -0.0017688 | -0.0012454 | -0.000109 | 0.00091437 | -0.0038879 | 63.7894 | 63.9313 | -0.018311 | -59.2667 | 63.8168 | -59.0881 | -59.1339 | -59.1019 | 0.073242 | -59.3628 | 63.8901 | 63.8031 | -59.111 | -59.2255 | 0.004577 | -0.041199 | -0.10071 | 123.024 | -0.17395 | -0.13275 | -0.12817 | -0.018311 | -0.13275 | -0.027466 | -0.009156 | -0.27008 | -0.13733 | -0.11444 | 122.9095 | 122.8821 | 59.0744 | -123.0515 | 122.9828 | 122.8958 | 59.166 | -123.143
317.5156 | 123.1155 | -59.1019 | 63.8763 | -0.11749 | 0.010536 | 0.065877 | 0.071354 | 0.12614 | 0.00019875 | -0.00043792 | -0.095902 | -0.00027337 | -0.000391 | 0.0009592 | 0.0013416 | -0.0032471 | 63.8168 | 63.9267 | -0.022888 | -59.2438 | 63.858 | -59.0881 | -59.1248 | -59.0607 | 0.07782 | -59.3308 | 63.8855 | 63.8306 | -59.0652 | -59.198 | 0.013733 | -0.022888 | -0.018311 | 123.0286 | -0.14191 | -0.11902 | -0.05951 | 0.036621 | -0.09613 | 0.009155 | 0.041199 | -0.22888 | -0.13275 | -0.045777 | 122.9599 | 122.9187 | 59.079 | -123.0011 | 122.9874 | 122.9324 | 59.1797 | -123.0743
318.5156 | 123.111 | -59.0881 | 63.8901 | 0.080872 | 0.0073315 | 0.067372 | 0.070073 | 0.12956 | -0.0021512 | -0.00043792 | -0.050125 | -0.0015552 | 0.001318 | 0.0016 | -0.00079463 | -0.0032471 | 63.8168 | 63.9313 | -0.032043 | -59.2941 | 63.8443 | -59.0927 | -59.1019 | -59.0744 | 0.054932 | -59.3628 | 63.8855 | 63.8306 | -59.1064 | -59.2346 | -0.004577 | -0.013733 | -0.045777 | 123.0194 | -0.20599 | -0.19226 | -0.073243 | -0.01831 | -0.14648 | -0.004578 | 0.013733 | -0.27466 | -0.12817 | -0.05951 | 122.9324 | 122.905 | 59.0561 | -122.9919 | 122.9736 | 122.9187 | 59.1431 | -123.1247
319.5156 | 123.1476 | -59.0927 | 63.858 | -0.10986 | 0.0096813 | 0.066304 | 0.067082 | 0.12977 | 0.00083955 | -0.0030013 | -0.019608 | -0.00027337 | 0.0021726 | 0.0011728 | 0.0034778 | -0.0041017 | 63.8397 | 63.9679 | 0 | -59.2392 | 63.8397 | -59.1064 | -59.1248 | -59.0286 | 0.068665 | -59.3308 | 63.8626 | 63.7894 | -59.0973 | -59.2255 | -0.013733 | -0.032044 | -0.01831 | 123.0606 | -0.14648 | -0.11444 | -0.01831 | -0.004578 | -0.13275 | 0.004578 | 0.064087 | -0.23804 | -0.10529 | -0.068664 | 122.9324 | 122.9324 | 59.0927 | -122.9828 | 122.9553 | 122.8821 | 59.1614 | -123.0835
320.5156 | 123.1247 | -59.0607 | 63.8901 | -0.13275 | 0.0079723 | 0.064809 | 0.06815 | 0.13062 | -0.001083 | -0.0019333 | -0.10353 | -0.001128 | 0.0008908 | 0.0016 | 5.9768e-05 | -0.0019653 | 63.7894 | 63.9267 | -0.036621 | -59.2621 | 63.8306 | -59.1019 | -59.1248 | -59.0836 | 0.068665 | -59.3536 | 63.8809 | 63.8214 | -59.0836 | -59.2163 | -0.041199 | -0.064087 | -0.05951 | 122.9874 | -0.20142 | -0.13733 | -0.10071 | -0.022888 | -0.15564 | -0.009156 | -0.022888 | -0.29297 | -0.13733 | -0.068665 | 122.8912 | 122.85 | 59.024 | -123.0148 | 122.9416 | 122.8821 | 59.1293 | -123.1064
321.5156 | 123.1293 | -59.0836 | 63.9084 | -0.14801 | 0.010109 | 0.06545 | 0.068791 | 0.12934 | 0.0029758 | -0.0021469 | -0.050125 | -0.0019824 | 0.0021726 | -0.0007498 | 0.0019824 | -0.0036743 | 63.8168 | 63.9542 | -0.018311 | -59.2621 | 63.8351 | -59.0836 | -59.1339 | -59.0424 | 0.07782 | -59.3308 | 63.8672 | 63.8077 | -59.1064 | -59.2255 | 0 | -0.050354 | -0.073242 | 123.0377 | -0.17853 | -0.12817 | -0.091553 | -0.022888 | -0.14191 | -0.041199 | 0.041199 | -0.24719 | -0.10529 | -0.10071 | 122.9187 | 122.9004 | 59.0652 | -123.0423 | 122.9507 | 122.8912 | 59.1614 | -123.1338
322.5156 | 123.1247 | -59.0927 | 63.8901 | -0.17853 | 0.0054089 | 0.066945 | 0.070073 | 0.12913 | -0.0021512 | -0.0040695 | -0.011978 | -0.0019824 | -0.0012454 | -0.0005362 | 0.0019824 | -0.0011109 | 63.8031 | 63.9175 | -0.027466 | -59.285 | 63.826 | -59.0973 | -59.1339 | -59.0652 | 0.36163 | -59.4406 | 63.9267 | 63.8397 | -59.0973 | -59.2484 | -0.004578 | -0.041199 | -0.064087 | 123.0103 | -0.19226 | -0.15106 | -0.086975 | -0.004578 | -0.15564 | 0.036621 | 0.027465 | -0.3479 | -0.19226 | -0.050354 | 122.9187 | 122.8958 | 59.0652 | -123.024 | 123.0194 | 122.9324 | 59.4543 | -123.1384
323.5156 | 123.1476 | -59.0973 | 63.8855 | -0.086975 | 0.0081861 | 0.067372 | 0.069645 | 0.12892 | 0.002335 | -0.0010787 | -0.0043486 | -0.0015552 | 0.0008908 | -0.0003226 | 0.001128 | -0.00089726 | 63.8535 | 63.9587 | 0.009155 | -59.2621 | 63.8351 | -59.0927 | -59.0973 | -59.198 | 0.26093 | -59.3124 | 63.8672 | 63.8031 | -59.1248 | -59.2621 | 0.004578 | 0 | -0.050354 | 123.056 | -0.16479 | -0.16479 | -0.032043 | -0.027466 | -0.16479 | -0.018311 | -0.10071 | -0.21515 | -0.050354 | -0.082397 | 122.9324 | 122.9507 | 59.1064 | -122.9828 | 122.9645 | 122.9004 | 59.3582 | -123.1476
324.5156 | 123.0835 | -59.0652 | 63.8992 | -0.19379 | 0.0039135 | 0.069509 | 0.067082 | 0.12934 | -0.0021512 | -0.0027877 | -0.13405 | -0.0017688 | -0.0006046 | -0.0003226 | 0.00027337 | -0.0017517 | 63.8168 | 63.9816 | 0.018311 | -59.2529 | 63.8397 | -59.0836 | -59.1019 | -59.0515 | 0.073242 | -59.3353 | 63.8901 | 63.8168 | -59.111 | -59.23 | -0.01831 | -0.036621 | -0.059509 | 123.0469 | -0.18768 | -0.15106 | -0.082398 | -0.045776 | -0.16479 | -0.009155 | 0.013733 | -0.27008 | -0.10529 | -0.082398 | 122.905 | 122.8821 | 59.0836 | -123.0011 | 122.9553 | 122.8821 | 59.1385 | -123.1293
325.5156 | 123.1796 | -59.0927 | 63.8306 | -0.13275 | 0.0058361 | 0.066731 | 0.069218 | 0.13126 | 0.001694 | 0.0019119 | -0.027237 | -0.003905 | 0.0025998 | -0.0009634 | 0.0013416 | -0.0023927 | 63.8443 | 63.9587 | -0.004578 | -59.2575 | 63.8397 | -59.0836 | -59.1476 | -59.0515 | 0.073242 | -59.3353 | 63.8535 | 63.7848 | -59.1293 | -59.2163 | 0.009155 | -0.054932 | 0.009156 | 123.0515 | -0.16479 | -0.10986 | 0.013733 | -0.036621 | -0.1236 | 0.022889 | 0.041198 | -0.24262 | -0.11902 | -0.045776 | 122.9324 | 122.937 | 59.0881 | -122.9782 | 122.9462 | 122.8775 | 59.166 | -123.0469
326.5156 | 123.1018 | -59.0607 | 63.9221 | -0.19379 | 0.0066907 | 0.066945 | 0.066655 | 0.13041 | -0.001083 | -0.00043792 | -0.057755 | -0.002196 | 0.0008908 | -0.0005362 | -0.00058103 | -0.0021789 | 63.7848 | 63.9267 | -0.018311 | -59.2758 | 63.8397 | -59.111 | -59.1385 | -59.0698 | 0.054932 | -59.3491 | 63.8947 | 63.8168 | -59.0927 | -59.2346 | -0.050354 | -0.07782 | -0.082397 | 122.9874 | -0.21515 | -0.13733 | -0.13733 | -0.032043 | -0.17395 | -0.027466 | -0.009155 | -0.28839 | -0.11444 | -0.10529 | 122.9004 | 122.8455 | 59.0424 | -123.0606 | 122.9553 | 122.8775 | 59.1156 | -123.1567
327.5156 | 123.1155 | -59.0744 | 63.8626 | -0.11749 | 0.0083997 | 0.066518 | 0.070073 | 0.13084 | 0.00019875 | -0.0012923 | -0.065384 | -0.0019824 | 0.0006772 | 0.0013864 | 0.001128 | -0.0034607 | 63.8168 | 63.9404 | 0.004578 | -59.2392 | 63.8397 | -59.0973 | -59.1202 | -59.0515 | 0.07782 | -59.317 | 63.8901 | 63.7894 | -59.0973 | -59.2346 | -0.022888 | -0.045776 | -0.022888 | 123.0148 | -0.16479 | -0.11902 | -0.045777 | -0.022888 | -0.16022 | 0.027466 | 0.022888 | -0.24262 | -0.082398 | -0.073242 | 122.9141 | 122.8912 | 59.079 | -122.9828 | 122.9645 | 122.8638 | 59.1522 | -123.0972
328.5156 | 123.0835 | -59.079 | 63.8855 | -0.31586 | 0.0064771 | 0.069722 | 0.067936 | 0.13105 | -0.0023648 | -0.0030013 | -0.034867 | -0.0013416 | -0.0027408 | -0.001818 | 0.00027337 | 0.0014525 | 63.7848 | 63.9313 | -0.022888 | -59.2758 | 63.8443 | -59.079 | -59.1156 | -59.1843 | 0.036621 | -59.3582 | 63.8535 | 63.7756 | -59.1202 | -59.2529 | 0 | -0.036622 | -0.041199 | 123.0103 | -0.19684 | -0.16022 | -0.10071 | -0.041199 | -0.17395 | -0.032043 | -0.10529 | -0.27924 | -0.10529 | -0.10986 | 122.9233 | 122.8638 | 59.0561 | -123.0011 | 122.9324 | 122.8546 | 59.1156 | -123.1384
329.5156 | 123.0927 | -59.0652 | 63.8855 | -0.14801 | 0.0086133 | 0.062673 | 0.067082 | 0.12913 | -1.505e-05 | -0.0027877 | -0.13405 | -0.0019824 | 0.0028134 | -0.0013906 | 0.00091437 | -0.0013245 | 63.8168 | 63.945 | -0.022888 | -59.2621 | 63.8351 | -59.0927 | -59.1156 | -59.0515 | 0.068665 | -59.3353 | 63.8535 | 63.7939 | -59.0836 | -59.2392 | -0.027465 | -0.050354 | -0.050354 | 123.0103 | -0.19684 | -0.14648 | -0.068665 | -0.01831 | -0.17395 | -0.032043 | 0.013733 | -0.27008 | -0.09613 | -0.091553 | 122.9004 | 122.8821 | 59.0424 | -123.0011 | 122.9187 | 122.8592 | 59.1339 | -123.1247
330.5156 | 123.1155 | -59.0286 | 63.9313 | -0.15564 | 0.0060497 | 0.066945 | 0.066014 | 0.13148 | -0.0025784 | -0.0030013 | -0.042496 | -0.0024096 | -0.0006046 | 0.0003182 | -0.00058103 | -0.0015381 | 63.8031 | 63.9542 | 0.009155 | -59.2621 | 63.8168 | -59.0927 | -59.111 | -59.0561 | 0.064087 | -59.3353 | 63.8763 | 63.8168 | -59.1019 | -59.2255 | -0.064087 | -0.082398 | -0.11444 | 122.9828 | -0.23346 | -0.15106 | -0.12817 | -0.073243 | -0.19684 | -0.054931 | -0.027466 | -0.3067 | -0.10986 | -0.11444 | 122.8455 | 122.8317 | 59.0378 | -123.0423 | 122.905 | 122.8455 | 59.0927 | -123.1567
331.5156 | 123.0972 | -59.0881 | 63.9038 | -0.10223 | 0.0081861 | 0.065663 | 0.06815 | 0.13148 | 0.0010532 | -0.0019333 | -0.13405 | -0.00048697 | 3.6404e-05 | -0.000109 | 0.00091437 | -0.0019653 | 63.8031 | 63.9267 | -0.022888 | -59.2484 | 63.8306 | -59.079 | -59.111 | -59.0561 | 0.059509 | -59.3491 | 63.8901 | 63.8031 | -59.1202 | -59.2392 | 0.009156 | -0.022888 | -0.073243 | 123.0148 | -0.16022 | -0.13733 | -0.10071 | -0.032043 | -0.15106 | -0.013733 | 0.032044 | -0.26093 | -0.10986 | -0.10071 | 122.9187 | 122.8912 | 59.0652 | -123.0148 | 122.9782 | 122.8912 | 59.1476 | -123.143
332.5156 | 123.1018 | -59.079 | 63.8901 | -0.23193 | 0.0051953 | 0.069936 | 0.069432 | 0.12892 | 0.0010532 | -0.0019333 | -0.15694 | -0.0015552 | 3.6404e-05 | -0.000109 | -0.00015383 | -0.0015381 | 63.7711 | 63.8809 | -0.036621 | -59.3079 | 63.826 | -59.0973 | -59.1385 | -59.0836 | 0.064087 | -59.3628 | 63.8947 | 63.8031 | -59.111 | -59.2117 | -0.018311 | -0.05951 | -0.064087 | 122.9599 | -0.22888 | -0.16937 | -0.11902 | -0.032044 | -0.13275 | 0.004577 | -0.004578 | -0.28381 | -0.15106 | -0.086975 | 122.905 | 122.85 | 59.0424 | -123.0286 | 122.9736 | 122.8821 | 59.1431 | -123.1018
333.5156 | 123.143 | -59.0698 | 63.858 | -0.14801 | 0.01139 | 0.066304 | 0.069005 | 0.13191 | 0.0014804 | -0.0021469 | -0.13405 | -0.002196 | 3.6404e-05 | -0.0003226 | 0.0017688 | -0.0026063 | 63.8397 | 63.945 | -0.022888 | -59.2346 | 63.8443 | -59.1202 | -59.1156 | -59.0332 | 0.07782 | -59.3262 | 63.8672 | 63.7939 | -59.111 | -59.2392 | -0.050354 | -0.045777 | -0.013733 | 123.0148 | -0.1648 | -0.11902 | -0.01831 | -0.041199 | -0.16937 | 0.009155 | 0.036621 | -0.25635 | -0.086975 | -0.064087 | 122.9141 | 122.9095 | 59.0469 | -122.9736 | 122.937 | 122.8638 | 59.1476 | -123.0972
334.5156 | 123.0789 | -59.0927 | 63.9038 | -0.14801 | 0.0054089 | 0.06545 | 0.06815 | 0.13041 | 0.00019875 | -0.0042831 | -0.41634 | -0.0024096 | -0.0001774 | -0.0003226 | 0.00091437 | -0.0017517 | 63.7894 | 63.9404 | -0.022888 | -59.3399 | 63.8626 | -59.0698 | -59.0744 | -59.0744 | 0.027466 | -59.3628 | 63.8947 | 63.8077 | -59.111 | -59.2163 | 0.022888 | 0.01831 | -0.041199 | 123.0331 | -0.24719 | -0.2655 | -0.11444 | -0.018311 | -0.1236 | -0.009156 | 0.01831 | -0.27008 | -0.14648 | -0.096131 | 122.9553 | 122.8821 | 59.0698 | -122.9782 | 122.9874 | 122.9004 | 59.1202 | -123.1201
335.5156 | 123.1293 | -59.0607 | 63.8855 | -0.1709 | 0.01139 | 0.065877 | 0.069218 | 0.13126 | 0.0010532 | -0.0025741 | -0.057755 | 0.0010082 | 0.0023862 | -0.000109 | -0.00036743 | -0.0028199 | 63.8031 | 63.9359 | -0.009155 | -59.2575 | 63.8535 | -59.1064 | -59.1202 | -59.0378 | 0.091553 | -59.3216 | 63.8763 | 63.7756 | -59.111 | -59.2209 | -0.045776 | -0.059509 | -0.032043 | 122.9965 | -0.19684 | -0.13733 | -0.082397 | -0.050354 | -0.16022 | -0.009155 | 0.022888 | -0.26093 | -0.10071 | -0.10986 | 122.9141 | 122.8638 | 59.0515 | -123.0057 | 122.937 | 122.8363 | 59.1522 | -123.1064
336.5156 | 123.0835 | -59.0836 | 63.9221 | -0.10223 | 0.0077587 | 0.066091 | 0.069859 | 0.12913 | -0.00022865 | -0.0017197 | -0.088272 | -0.001128 | 0.00025 | -0.000109 | -0.00036743 | -0.0015381 | 63.7711 | 63.9221 | -0.032043 | -59.2712 | 63.826 | -59.0927 | -59.1248 | -59.0652 | 0.054932 | -59.3399 | 63.8718 | 63.8168 | -59.1156 | -59.23 | -0.009155 | -0.041199 | -0.09613 | 123.0057 | -0.18768 | -0.14648 | -0.15106 | -0.032044 | -0.14648 | -0.050354 | 0.01831 | -0.25635 | -0.10986 | -0.10529 | 122.9095 | 122.8546 | 59.0515 | -123.0469 | 122.9553 | 122.9004 | 59.1385 | -123.1522
337.5156 | 123.0743 | -59.0973 | 63.8901 | 0.027466 | 0.012245 | 0.064809 | 0.069432 | 0.12998 | 0.004044 | 0.0021255 | 0.14824 | -0.0013416 | 0.001959 | 0.0011728 | 0.0015552 | -0.0038879 | 63.7894 | 63.8901 | -0.091553 | -59.2896 | 63.8306 | -59.0973 | -59.1202 | -59.0973 | -0.041199 | -59.3903 | 63.8535 | 63.7756 | -59.1293 | -59.2392 | 0 | -0.022888 | -0.05951 | 122.9874 | -0.19226 | -0.16937 | -0.10071 | -0.032043 | -0.14191 | -0.036621 | 0 | -0.29297 | -0.15106 | -0.11444 | 122.9279 | 122.8867 | 59.0057 | -123.0103 | 122.9507 | 122.8729 | 59.0561 | -123.1293
338.5156 | 123.0606 | -59.079 | 63.9267 | 0.012207 | 0.0081861 | 0.068227 | 0.067296 | 0.13084 | -0.00065585 | -0.0027877 | -0.080643 | -0.00070077 | 3.6404e-05 | -0.000109 | 0.00070077 | -0.0028199 | 63.8077 | 63.9084 | -0.032043 | -59.2758 | 63.858 | -59.0973 | -59.1339 | -59.0744 | 0.050354 | -59.3445 | 63.9038 | 63.8031 | -59.111 | -59.2255 | -0.018311 | -0.054932 | -0.068665 | 122.9874 | -0.19684 | -0.14191 | -0.11902 | -0.032044 | -0.14649 | -0.022888 | 0.004577 | -0.2655 | -0.11902 | -0.1236 | 122.937 | 122.8867 | 59.0469 | -123.0606 | 122.9828 | 122.8821 | 59.1293 | -123.1522
339.5156 | 123.0972 | -59.0881 | 63.8489 | -0.14801 | 0.012031 | 0.0678 | 0.069218 | 0.12763 | 0.0012668 | -0.0010787 | 0.033798 | 0.0014356 | -0.0001774 | -0.0009634 | 0.0013416 | -0.0038879 | 63.826 | 63.9542 | -0.004578 | -59.2667 | 63.8123 | -59.0652 | -59.111 | -59.0332 | 0.045776 | -59.3536 | 63.8443 | 63.8031 | -59.0881 | -59.2621 | 0.022888 | -0.022888 | -0.036621 | 123.0423 | -0.17853 | -0.15564 | -0.022888 | 0 | -0.17395 | -0.004578 | 0.054932 | -0.2655 | -0.091553 | -0.045776 | 122.9004 | 122.9141 | 59.0836 | -122.9599 | 122.9324 | 122.8912 | 59.1339 | -123.111
340.5156 | 123.1384 | -59.0744 | 63.8947 | -0.11749 | 0.0062635 | 0.067372 | 0.067296 | 0.13126 | 0.00062595 | -0.0017197 | -0.065384 | -0.0019824 | 0.0017454 | -0.0003226 | 0.0026234 | -0.0011109 | 63.7894 | 63.9038 | -0.027466 | -59.2621 | 63.8123 | -59.0973 | -59.111 | -59.0561 | 0.064087 | -59.3445 | 63.8901 | 63.8214 | -59.0927 | -59.2163 | -0.022888 | -0.036621 | -0.082397 | 122.9782 | -0.18768 | -0.15106 | -0.10528 | -0.01831 | -0.14191 | -0.004577 | 0.018311 | -0.27008 | -0.12817 | -0.073242 | 122.8867 | 122.8638 | 59.0469 | -123.0057 | 122.9645 | 122.8958 | 59.1385 | -123.111
341.5156 | 123.1293 | -59.111 | 63.8763 | 0.31738 | 0.010963 | 0.065022 | 0.066868 | 0.13041 | 0.0012668 | -0.00065152 | 0.041427 | -5.9768e-05 | 0.0028134 | -0.000109 | 0.00091437 | -0.0034607 | 63.8535 | 63.9542 | 0.004578 | -59.2484 | 63.826 | -59.0744 | -59.1156 | -59.0469 | 0.054932 | -59.3399 | 63.8351 | 63.7711 | -59.1202 | -59.2484 | 0.036621 | -0.004578 | -0.050354 | 123.0652 | -0.13733 | -0.13275 | -0.022888 | -0.009155 | -0.13733 | -0.041199 | 0.064087 | -0.22888 | -0.091553 | -0.10529 | 122.937 | 122.9645 | 59.1156 | -122.9919 | 122.9462 | 122.8821 | 59.166 | -123.1247
342.5156 | 123.111 | -59.0881 | 63.8992 | -0.16327 | 0.0079723 | 0.066304 | 0.068364 | 0.1302 | -0.0034328 | -0.0015061 | -0.050125 | -0.002837 | -0.0016726 | -0.0007498 | 0.00027337 | -0.0041017 | 63.8031 | 64.0869 | 0 | -59.3674 | 63.8443 | -59.1019 | -59.1339 | -59.0698 | 0.054932 | -59.3399 | 63.8763 | 63.8077 | -59.1431 | -59.2392 | -0.013733 | -0.045776 | -0.054932 | 123.175 | -0.27924 | -0.23346 | -0.09613 | -0.054931 | -0.15106 | -0.022888 | 0.018311 | -0.25177 | -0.10071 | -0.091553 | 122.9324 | 122.8912 | 59.0881 | -123.0331 | 122.9645 | 122.8958 | 59.1431 | -123.1384
343.5156 | 123.1338 | -59.0881 | 63.8626 | -0.14038 | 0.0098951 | 0.068013 | 0.069218 | 0.13148 | 0.00083955 | -0.0012923 | -0.073013 | -0.0019824 | -0.0010318 | 0.0001046 | 0.0013416 | -0.0023927 | 63.8306 | 63.9496 | -0.004578 | -59.2438 | 63.8443 | -59.0881 | -59.1019 | -59.0561 | 0.086975 | -59.3308 | 63.8672 | 63.7894 | -59.0836 | -59.2346 | 0 | -0.013733 | -0.018311 | 123.0377 | -0.15564 | -0.14191 | -0.032044 | 0.004578 | -0.14648 | 0.004577 | 0.032044 | -0.24262 | -0.096131 | -0.073242 | 122.9324 | 122.9187 | 59.0836 | -122.9645 | 122.9553 | 122.8775 | 59.1751 | -123.0972
344.5156 | 123.0743 | -59.0881 | 63.913 | -0.17853 | 0.0064771 | 0.066304 | 0.068364 | 0.12956 | -0.002792 | -0.0023605 | -0.41634 | -0.00070077 | 0.0011044 | -0.0007498 | -0.00058103 | -0.0011109 | 63.7894 | 63.9221 | -0.009155 | -59.2941 | 63.8397 | -59.0927 | -59.0881 | -59.0744 | 0.027466 | -59.3582 | 63.858 | 63.8214 | -59.1293 | -59.2255 | -0.004577 | 0 | -0.073242 | 123.0103 | -0.20599 | -0.20599 | -0.1236 | -0.041198 | -0.13733 | -0.054932 | 0.013733 | -0.27008 | -0.13275 | -0.091553 | 122.9279 | 122.8775 | 59.079 | -123.0011 | 122.9462 | 122.9095 | 59.1156 | -123.1384
345.5156 | 123.1659 | -59.0973 | 63.8535 | -0.018311 | 0.010963 | 0.068227 | 0.070286 | 0.1287 | 0.0029758 | -0.0023605 | -0.027237 | -0.0019824 | 0.0017454 | 0.0011728 | 0.0013416 | -0.0032471 | 63.8901 | 63.945 | -0.032043 | -59.2163 | 63.8306 | -59.0881 | -59.111 | -59.0378 | 0.082397 | -59.3308 | 63.8718 | 63.7939 | -59.1156 | -59.2209 | 0.009155 | -0.013733 | -0.022889 | 123.0423 | -0.11902 | -0.10529 | 0.036621 | -0.018311 | -0.1236 | 0.01831 | 0.059509 | -0.23346 | -0.10986 | -0.05951 | 122.9279 | 122.9874 | 59.0652 | -122.9645 | 122.9691 | 122.8912 | 59.1797 | -123.0743
346.5156 | 123.0835 | -59.0698 | 63.9175 | -0.19379 | 0.0071179 | 0.066731 | 0.069218 | 0.12892 | -0.0025784 | -0.0019333 | -0.088272 | -0.002196 | -0.0001774 | 0.0016 | -0.00036743 | -0.0015381 | 63.7894 | 63.9175 | -0.032043 | -59.2667 | 63.8443 | -59.1019 | -59.0927 | -59.0652 | 0.045776 | -59.3582 | 63.8947 | 63.8214 | -59.0881 | -59.2117 | -0.032044 | -0.022888 | -0.073243 | 122.9874 | -0.19684 | -0.17395 | -0.12817 | -0.018311 | -0.14191 | -0.022889 | 0.004577 | -0.28839 | -0.14648 | -0.096131 | 122.9141 | 122.8592 | 59.0378 | -123.0103 | 122.9645 | 122.8912 | 59.1156 | -123.1293
347.5156 | 123.1247 | -59.079 | 63.8718 | -0.079346 | 0.0092541 | 0.066091 | 0.067296 | 0.12998 | 0.0014804 | -0.0015061 | -0.19508 | -0.00027337 | -0.0008182 | -0.0003226 | 0.0030506 | -0.0026063 | 63.8214 | 63.9542 | -0.041199 | -59.4086 | 63.7802 | -59.1568 | -59.1614 | -59.0103 | 0.10071 | -59.3216 | 63.8443 | 63.7985 | -59.1019 | -59.23 | -0.07782 | -0.082398 | -0.091553 | 123.0331 | -0.32959 | -0.24719 | -0.050354 | -0.022889 | -0.15106 | -0.027466 | 0.068664 | -0.24262 | -0.091552 | -0.073242 | 122.8592 | 122.9004 | 59.0378 | -123.0331 | 122.9233 | 122.8775 | 59.1797 | -123.1018
348.5156 | 123.111 | -59.0561 | 63.8763 | -0.10986 | 0.011177 | 0.069081 | 0.0705 | 0.1302 | 0.001694 | -0.0015061 | -0.13405 | -0.00048697 | -0.0010318 | -0.0013906 | 0.002837 | -0.0015381 | 63.8077 | 63.9359 | -0.027466 | -59.2438 | 63.8306 | -59.079 | -59.1019 | -59.0561 | 0.10071 | -59.3353 | 63.8672 | 63.7985 | -59.1064 | -59.2484 | -0.022888 | -0.045777 | -0.045777 | 122.9919 | -0.18768 | -0.14191 | -0.068665 | -0.050354 | -0.19226 | -0.009156 | 0 | -0.27924 | -0.086975 | -0.07782 | 122.8867 | 122.8638 | 59.0286 | -122.9782 | 122.9233 | 122.8546 | 59.1568 | -123.1247
349.5156 | 123.1247 | -59.0927 | 63.8672 | -0.064087 | 0.012031 | 0.065663 | 0.069218 | 0.13255 | 0.00041235 | -0.0025741 | 0.018539 | -0.0036914 | -0.0006046 | -0.001177 | 0.001128 | -0.0049561 | 63.8077 | 63.9542 | 0.009155 | -59.2346 | 63.8168 | -59.0973 | -59.1339 | -59.0012 | 0.050354 | -59.3353 | 63.8763 | 63.7985 | -59.1064 | -59.2072 | -0.004578 | -0.041199 | -0.050354 | 123.0469 | -0.14191 | -0.10071 | -0.059509 | -0.013733 | -0.11444 | 0.009156 | 0.091552 | -0.24262 | -0.12817 | -0.068664 | 122.9095 | 122.9004 | 59.1019 | -123.0011 | 122.9691 | 122.8912 | 59.1431 | -123.0743
350.5156 | 123.0927 | -59.0698 | 63.9038 | -0.12512 | 0.0064771 | 0.066945 | 0.067509 | 0.12785 | -0.00086945 | -0.0030013 | -0.065384 | -0.0015552 | -0.0006046 | 0.0007456 | 5.9768e-05 | -0.0028199 | 63.7756 | 63.9221 | -0.027466 | -59.2804 | 63.8489 | -59.0927 | -59.1385 | -59.079 | 0.054932 | -59.3582 | 63.8901 | 63.8123 | -59.1156 | -59.2072 | -0.022888 | -0.068665 | -0.054932 | 122.9919 | -0.21057 | -0.14191 | -0.12817 | -0.045777 | -0.13733 | -0.013733 | -0.009155 | -0.28839 | -0.15106 | -0.091553 | 122.9187 | 122.8455 | 59.0424 | -123.0423 | 122.9599 | 122.8821 | 59.1248 | -123.111
351.5156 | 123.1522 | -59.0744 | 63.8947 | -0.13275 | 0.010109 | 0.065877 | 0.068577 | 0.12977 | -0.00044225 | -1.0724e-05 | 0.049057 | -0.0017688 | -0.0008182 | 0.0028818 | -0.00015383 | -0.0028199 | 63.8214 | 63.9496 | -0.009155 | -59.2575 | 63.8397 | -59.1064 | -59.1156 | -59.0195 | 0.15106 | -59.3216 | 63.8535 | 63.7894 | -59.0927 | -59.2529 | -0.032043 | -0.041199 | -0.054931 | 123.024 | -0.1831 | -0.14191 | -0.073242 | -0.01831 | -0.17853 | -0.041198 | 0.054932 | -0.24719 | -0.068664 | -0.10528 | 122.9141 | 122.8958 | 59.0652 | -123.0103 | 122.9279 | 122.8638 | 59.2255 | -123.1476
352.5156 | 123.1018 | -59.0652 | 63.8901 | -0.27771 | 0.0043409 | 0.067372 | 0.068791 | 0.13148 | -0.002792 | -0.00043792 | -0.073013 | -0.0030506 | 0.0017454 | 0.0016 | -0.0010082 | -0.0021789 | 63.7756 | 63.9084 | -0.045776 | -59.2758 | 63.8626 | -59.0836 | -59.1293 | -59.0652 | 0.041199 | -59.3491 | 63.913 | 63.8077 | -59.1019 | -59.2163 | -0.01831 | -0.064086 | -0.027466 | 122.9736 | -0.21057 | -0.14648 | -0.11444 | -0.036621 | -0.15106 | 0.022888 | 0 | -0.28381 | -0.13275 | -0.082398 | 122.9279 | 122.8409 | 59.0195 | -123.0194 | 122.9782 | 122.8729 | 59.1064 | -123.1064
353.5156 | 123.0972 | -59.0973 | 63.8809 | -0.010681 | 0.011818 | 0.065877 | 0.071141 | 0.13062 | 0.0019078 | -0.00022432 | 0.026169 | -0.00048697 | -0.001459 | 0.0003182 | 0.00070077 | -0.0036743 | 63.8397 | 63.9496 | -0.022888 | -59.2529 | 63.8123 | -59.0881 | -59.1156 | -59.0424 | 0.045776 | -59.3445 | 63.8351 | 63.7665 | -59.1019 | -59.2392 | 0.009155 | -0.018311 | -0.068664 | 123.0469 | -0.15564 | -0.13733 | -0.041198 | -0.004578 | -0.14191 | -0.045776 | 0.054932 | -0.24719 | -0.10529 | -0.11444 | 122.9095 | 122.937 | 59.0744 | -122.9965 | 122.9324 | 122.8638 | 59.1431 | -123.1201
354.5156 | 123.1384 | -59.0698 | 63.9221 | -0.14801 | 0.0079723 | 0.065663 | 0.069645 | 0.12849 | 0.00041235 | -1.0724e-05 | -0.080643 | -0.002837 | 0.0011044 | -0.0007498 | 0.0017688 | -0.0032471 | 63.8031 | 63.913 | -0.041199 | -59.2667 | 63.8168 | -59.0927 | -59.111 | -59.079 | 0.068665 | -59.3445 | 63.8809 | 63.8306 | -59.0652 | -59.2163 | -0.022888 | -0.041199 | -0.10529 | 122.9828 | -0.19684 | -0.15564 | -0.11902 | 0.004577 | -0.14649 | -0.041199 | -0.009155 | -0.27466 | -0.12817 | -0.091553 | 122.8867 | 122.8729 | 59.0286 | -123.0331 | 122.9507 | 122.9004 | 59.1385 | -123.1384
355.5156 | 123.1201 | -59.0927 | 63.8718 | -0.12512 | 0.010536 | 0.065663 | 0.068791 | 0.12956 | 0.00083955 | -0.00065152 | 0.071945 | -0.002837 | 0.0038816 | -0.0022452 | 0.001128 | -0.0026063 | 63.8351 | 63.9633 | -0.018311 | -59.2667 | 63.8214 | -59.1019 | -59.1202 | -59.0515 | 0.054932 | -59.3216 | 63.8535 | 63.7802 | -59.1202 | -59.2346 | -0.009156 | -0.027466 | -0.050354 | 123.056 | -0.17395 | -0.14648 | -0.036621 | -0.027466 | -0.14191 | -0.01831 | 0.041198 | -0.22888 | -0.086975 | -0.091553 | 122.9141 | 122.9279 | 59.0744 | -122.9919 | 122.9462 | 122.8729 | 59.1476 | -123.1064
356.5156 | 123.1522 | -59.0836 | 63.9038 | -0.14801 | 0.0086133 | 0.0678 | 0.069218 | 0.12913 | -0.00086945 | -0.00086512 | -0.050125 | -0.0036914 | -0.0008182 | 0.0001046 | -0.00036743 | -0.0032471 | 63.7848 | 63.9084 | -0.022888 | -59.2712 | 63.826 | -59.1064 | -59.1293 | -59.0698 | 0.064087 | -59.3353 | 63.8992 | 63.826 | -59.079 | -59.2346 | -0.022888 | -0.045776 | -0.07782 | 122.9919 | -0.18768 | -0.14191 | -0.11902 | 0.004578 | -0.15106 | -0.004578 | 0.013733 | -0.25177 | -0.10071 | -0.07782 | 122.9095 | 122.8683 | 59.0607 | -123.0331 | 122.9828 | 122.9095 | 59.1476 | -123.1384
357.5156 | 123.1888 | -59.0652 | 63.7985 | 0.14191 | 0.0083997 | 0.066731 | 0.066441 | 0.13126 | -0.0030056 | -0.0036423 | 0.32372 | -0.0034778 | 0.0011044 | -0.0026724 | 0.0015552 | -0.0015381 | 63.826 | 63.9908 | -0.018311 | -59.2392 | 63.7619 | -59.0881 | -59.1202 | -58.9874 | 0.045776 | -59.2758 | 63.8168 | 63.7161 | -59.1064 | -59.2255 | -0.022888 | -0.054931 | -0.036621 | 123.056 | -0.17395 | -0.11902 | 0.027466 | -0.041198 | -0.16022 | 0.01831 | 0.07782 | -0.21057 | -0.050354 | -0.082398 | 122.8271 | 122.8912 | 59.0469 | -122.9187 | 122.8821 | 122.7814 | 59.111 | -123.024
358.5156 | 123.1064 | -59.0607 | 63.9175 | -0.14038 | 0.0081861 | 0.068227 | 0.069859 | 0.12827 | 0.00062595 | -0.00043792 | -0.073013 | -0.00048697 | 0.0011044 | -0.0041678 | 0.0017688 | -0.0017517 | 63.8077 | 63.8992 | -0.036621 | -59.2712 | 63.8397 | -59.0744 | -59.0973 | -59.0881 | 0.045776 | -59.3674 | 63.9038 | 63.8351 | -59.111 | -59.2255 | -0.013733 | -0.036621 | -0.07782 | 122.9599 | -0.21057 | -0.17395 | -0.10986 | -0.050354 | -0.1648 | -0.013733 | -0.027466 | -0.3067 | -0.14191 | -0.082398 | 122.9004 | 122.8683 | 59.024 | -123.0148 | 122.9645 | 122.8958 | 59.1064 | -123.143
359.5156 | 123.1064 | -59.0836 | 63.858 | 0.019836 | 0.010963 | 0.066731 | 0.067296 | 0.12849 | 0.0027622 | -0.00043792 | 0.087204 | -0.00027337 | -0.0027408 | 0.0018136 | 0.0026234 | -0.0023927 | 63.8306 | 63.9221 | -0.045776 | -59.2758 | 63.7985 | -59.1019 | -59.111 | -59.0698 | 0.004578 | -59.3857 | 63.8443 | 63.7619 | -59.1156 | -59.2484 | -0.018311 | -0.027466 | -0.059509 | 123.0057 | -0.19226 | -0.16479 | -0.027466 | -0.032044 | -0.16479 | -0.013733 | 0.013733 | -0.30212 | -0.13733 | -0.09613 | 122.8821 | 122.9141 | 59.0378 | -122.9691 | 122.9279 | 122.8455 | 59.0881 | -123.1064
360.5156 | 123.1338 | -59.0607 | 63.8855 | -0.20142 | 0.0086133 | 0.066731 | 0.066868 | 0.13041 | 0.00019875 | -0.0025741 | -0.080643 | 0.00015383 | -0.0012454 | -0.0013906 | 0.00091437 | -0.0034607 | 63.8123 | 63.9359 | -0.013733 | -59.2438 | 63.8397 | -59.0744 | -59.1293 | -59.0378 | 0.09613 | -59.3308 | 63.8809 | 63.8123 | -59.1248 | -59.2163 | -0.013733 | -0.068664 | -0.045776 | 122.9965 | -0.18311 | -0.11444 | -0.073242 | -0.064087 | -0.15564 | -0.004578 | 0.022888 | -0.27008 | -0.11444 | -0.073242 | 122.9004 | 122.8729 | 59.0469 | -123.0148 | 122.9416 | 122.8729 | 59.1568 | -123.1018
361.5156 | 123.0743 | -59.1156 | 63.8672 | -0.018311 | 0.0086133 | 0.066945 | 0.068791 | 0.12998 | -0.00022865 | -0.00065152 | 0.049057 | 0.00015383 | 0.0038816 | 0.0024546 | 0.0034778 | -0.00025626 | 63.8306 | 63.9175 | -0.032043 | -59.2758 | 63.826 | -59.0836 | -59.1248 | -59.0652 | 0.013733 | -59.3536 | 63.8397 | 63.7848 | -59.1064 | -59.2529 | 0.032044 | -0.009155 | -0.041198 | 123.0331 | -0.16022 | -0.15106 | -0.036621 | 0.009156 | -0.13733 | -0.027465 | 0.050354 | -0.23804 | -0.10071 | -0.082397 | 122.9416 | 122.9462 | 59.0836 | -122.9919 | 122.9553 | 122.9004 | 59.1293 | -123.1201
362.5156 | 123.1659 | -59.0836 | 63.8214 | 0.15717 | 0.0077587 | 0.068868 | 0.067082 | 0.12956 | -0.0040738 | -0.0015061 | 0.35423 | -0.001128 | -0.0010318 | -0.001818 | 0.00091437 | -0.0034607 | 63.8351 | 63.9725 | -0.018311 | -59.2484 | 63.7436 | -59.1019 | -59.111 | -59.0149 | 0.041199 | -59.2941 | 63.7939 | 63.7619 | -59.1293 | -59.2163 | -0.018311 | -0.027466 | -0.07782 | 123.056 | -0.16479 | -0.13733 | 0.013733 | -0.045776 | -0.13275 | -0.027466 | 0.068664 | -0.21057 | -0.077819 | -0.059509 | 122.8271 | 122.9187 | 59.0652 | -122.9324 | 122.8775 | 122.8455 | 59.1248 | -123.0377
363.5156 | 123.0881 | -59.1019 | 63.8718 | 0.027466 | 0.011604 | 0.068227 | 0.071141 | 0.13062 | 0.0036166 | 0.0014847 | 0.018539 | -0.00048697 | -0.0006046 | -0.002886 | 0.0019824 | -0.0030335 | 63.8351 | 63.9175 | -0.027466 | -59.2621 | 63.8214 | -59.1019 | -59.1248 | -59.0515 | 0.032043 | -59.3582 | 63.858 | 63.8077 | -59.1019 | -59.2255 | 0 | -0.022888 | -0.050354 | 123.0194 | -0.16022 | -0.13733 | -0.036621 | 0 | -0.1236 | -0.013733 | 0.050354 | -0.25635 | -0.13275 | -0.064087 | 122.9233 | 122.937 | 59.0744 | -122.9965 | 122.9599 | 122.9095 | 59.1339 | -123.0972
364.5156 | 123.1659 | -59.0744 | 63.8901 | -0.11749 | 0.012031 | 0.066731 | 0.064091 | 0.12934 | 0.002335 | -0.0017197 | -0.042496 | 0.0010082 | -0.0016726 | -0.0007498 | 0.00027337 | -0.0026063 | 63.8535 | 63.9404 | -0.004578 | -59.2529 | 63.8031 | -59.1019 | -59.1385 | -59.0652 | 0.12817 | -59.3308 | 63.8763 | 63.8214 | -59.111 | -59.2484 | -0.027466 | -0.064087 | -0.086975 | 123.0148 | -0.17853 | -0.11444 | -0.036621 | -0.036621 | -0.17395 | -0.013733 | 0.009155 | -0.25635 | -0.082398 | -0.068665 | 122.8775 | 122.9279 | 59.0698 | -123.0286 | 122.9507 | 122.8958 | 59.2026 | -123.1384
365.5156 | 123.111 | -59.0881 | 63.858 | 0.027466 | 0.014168 | 0.065022 | 0.069218 | 0.1287 | 0.0025486 | -0.00043792 | 0.041427 | -0.00070077 | -0.0029544 | 0.000532 | 0.0013416 | -0.0034607 | 63.8535 | 63.945 | -0.027466 | -59.2621 | 63.8077 | -59.0973 | -59.0973 | -59.0332 | 0.041199 | -59.3399 | 63.8535 | 63.7711 | -59.0927 | -59.23 | -0.009155 | -0.009155 | -0.050354 | 123.0331 | -0.17395 | -0.16479 | -0.004577 | -0.004577 | -0.14191 | -0.004577 | 0.054932 | -0.25177 | -0.10986 | -0.086975 | 122.8958 | 122.9416 | 59.0607 | -122.9553 | 122.9416 | 122.8592 | 59.1293 | -123.0881
366.5156 | 123.1293 | -59.0881 | 63.8763 | -0.1709 | 0.012031 | 0.067586 | 0.069432 | 0.12699 | -0.001083 | -0.00086512 | -0.080643 | -0.00070077 | -0.0006046 | 0.0013864 | 0.00048697 | -0.0011109 | 63.8168 | 63.9359 | -0.018311 | -59.2575 | 63.8214 | -59.0698 | -59.1202 | -59.0515 | 0.068665 | -59.3399 | 63.8626 | 63.826 | -59.1202 | -59.23 | 0.018311 | -0.032043 | -0.054932 | 123.024 | -0.16937 | -0.13733 | -0.05951 | -0.032043 | -0.14191 | -0.013733 | 0.036621 | -0.25177 | -0.10986 | -0.050354 | 122.9095 | 122.905 | 59.0698 | -122.9965 | 122.9507 | 122.9141 | 59.1568 | -123.1064
367.5156 | 123.1796 | -59.0424 | 63.8123 | 0.20294 | 0.0083997 | 0.066304 | 0.065373 | 0.13105 | -0.0040738 | -0.0030013 | 0.36186 | -0.0024096 | -0.0012454 | -0.0009634 | 0.00027337 | -0.0023927 | 63.8351 | 63.9954 | -0.013733 | -59.2529 | 63.7436 | -59.0973 | -59.111 | -59.0012 | 0.041199 | -59.2896 | 63.8077 | 63.707 | -59.1202 | -59.2346 | -0.054932 | -0.068665 | -0.068665 | 123.0377 | -0.21057 | -0.14191 | 0.022888 | -0.07782 | -0.19226 | -0.004578 | 0.041198 | -0.24719 | -0.054932 | -0.10529 | 122.7859 | 122.8775 | 59.0286 | -122.9233 | 122.85 | 122.7493 | 59.0836 | -123.0469
368.5156 | 123.0881 | -59.0698 | 63.8489 | -0.11749 | 0.0092541 | 0.067159 | 0.070073 | 0.13062 | 0.0012668 | -0.0034287 | -0.050125 | -0.0041186 | 0.0017454 | -0.0013906 | 0.0032642 | -0.0015381 | 63.858 | 63.9359 | -0.013733 | -59.2575 | 63.8306 | -59.0927 | -59.1202 | -59.0332 | 0.073242 | -59.317 | 63.8901 | 63.7985 | -59.1064 | -59.2529 | -0.022888 | -0.050354 | -0.018311 | 123.0057 | -0.18768 | -0.13733 | 0.009155 | -0.036621 | -0.18311 | 0.041199 | 0.036621 | -0.24719 | -0.064087 | -0.050354 | 122.9004 | 122.9279 | 59.0561 | -122.9691 | 122.9599 | 122.8683 | 59.1431 | -123.1018
369.5156 | 123.0972 | -59.1019 | 63.8763 | 0.0045777 | 0.010963 | 0.064382 | 0.06815 | 0.13041 | 0.00062595 | -0.00043792 | 0.079574 | 0.0010082 | 0.0028134 | -0.0016044 | 0.001128 | -0.0030335 | 63.826 | 63.9038 | -0.068665 | -59.2712 | 63.826 | -59.0652 | -59.1385 | -59.0881 | 0.004578 | -59.3857 | 63.8535 | 63.8077 | -59.1202 | -59.2667 | 0.036621 | -0.036621 | -0.050354 | 123.0057 | -0.16937 | -0.13275 | -0.050354 | -0.01831 | -0.16479 | -0.022888 | 0.013733 | -0.28381 | -0.11902 | -0.068665 | 122.9279 | 122.9279 | 59.0332 | -123.0148 | 122.9553 | 122.9095 | 59.1064 | -123.143
370.5156 | 123.1064 | -59.0744 | 63.8626 | -0.14801 | 0.0092541 | 0.065236 | 0.069432 | 0.12892 | -0.0015102 | -0.0023605 | -0.073013 | -0.0019824 | 0.0004636 | 0.000532 | 0.0015552 | -0.0023927 | 63.8306 | 63.9404 | -0.027466 | -59.2575 | 63.8306 | -59.1019 | -59.1293 | -59.0378 | 0.091553 | -59.317 | 63.8672 | 63.8077 | -59.1019 | -59.2117 | -0.027466 | -0.054931 | -0.032044 | 123.0148 | -0.1831 | -0.12817 | -0.032044 | -0.027466 | -0.13733 | 0.004577 | 0.036621 | -0.24262 | -0.10529 | -0.054932 | 122.905 | 122.905 | 59.0469 | -122.9919 | 122.9416 | 122.8821 | 59.166 | -123.0743
371.5156 | 123.0698 | -59.111 | 63.8443 | 0.10376 | 0.012886 | 0.063314 | 0.068577 | 0.12892 | 0.0021214 | -0.0025741 | 0.25505 | -0.00091437 | -0.0021 | -0.0024588 | 0.0015552 | -0.0021789 | 63.7711 | 63.8489 | -0.09613 | -59.2896 | 63.8077 | -59.1293 | -59.1293 | -59.1202 | -0.059509 | -59.4406 | 63.8763 | 63.8031 | -59.1476 | -59.2392 | -0.01831 | -0.01831 | -0.036621 | 122.9599 | -0.17853 | -0.16022 | -0.073242 | -0.036621 | -0.12817 | 0.032044 | -0.009155 | -0.32959 | -0.20142 | -0.041198 | 122.9187 | 122.8821 | 59.0149 | -122.9736 | 122.9874 | 122.9141 | 59.0515 | -123.0835
372.5156 | 123.1155 | -59.0836 | 63.8535 | -0.15564 | 0.010536 | 0.065877 | 0.066014 | 0.13191 | 0.00083955 | -0.0019333 | -0.057755 | -0.0019824 | 0.00025 | -0.0007498 | 0.00070077 | -0.0019653 | 63.8123 | 63.9084 | -0.027466 | -59.2346 | 63.8489 | -59.0881 | -59.111 | -59.0424 | 0.091553 | -59.3124 | 63.8809 | 63.8397 | -59.1064 | -59.198 | -0.004578 | -0.027466 | -0.004578 | 122.9919 | -0.15106 | -0.1236 | -0.041199 | -0.022888 | -0.11444 | 0.027465 | 0.041199 | -0.22888 | -0.11444 | -0.013733 | 122.9324 | 122.8958 | 59.0561 | -122.9645 | 122.9645 | 122.9233 | 59.1751 | -123.0515
373.5156 | 123.0927 | -59.0881 | 63.8397 | -0.018311 | 0.010963 | 0.068013 | 0.070714 | 0.12892 | 0.0025486 | -0.0019333 | 0.041427 | -0.001128 | -0.0035952 | 0.0007456 | 0.0015552 | -0.0036743 | 63.8443 | 63.9404 | -0.027466 | -59.2621 | 63.8123 | -59.0927 | -59.1064 | -59.0469 | 0.027466 | -59.3536 | 63.8535 | 63.7894 | -59.0973 | -59.2392 | -0.004577 | -0.01831 | -0.027466 | 123.0286 | -0.17395 | -0.15564 | 0.004577 | -0.009155 | -0.15106 | 0.013733 | 0.041199 | -0.2655 | -0.11444 | -0.050354 | 122.9004 | 122.9324 | 59.0607 | -122.9462 | 122.9416 | 122.8775 | 59.1156 | -123.0789
374.5156 | 123.1247 | -59.0881 | 63.8809 | -0.094604 | 0.011177 | 0.065663 | 0.070286 | 0.13062 | -1.505e-05 | -0.00022432 | -0.019608 | -0.0013416 | -0.0027408 | 0.0018136 | 0.0026234 | -0.0019653 | 63.8443 | 63.9496 | 0.004578 | -59.2575 | 63.8489 | -59.111 | -59.1019 | -59.0286 | 0.082397 | -59.3216 | 63.8306 | 63.7711 | -59.1339 | -59.2621 | -0.022888 | -0.013733 | -0.032043 | 123.0377 | -0.16937 | -0.15564 | -0.036621 | -0.045776 | -0.17395 | -0.050354 | 0.05951 | -0.23346 | -0.059509 | -0.10986 | 122.937 | 122.9324 | 59.0927 | -122.9828 | 122.9187 | 122.8592 | 59.1705 | -123.143
375.5156 | 123.0881 | -59.1293 | 63.858 | 0.0045777 | 0.01139 | 0.065663 | 0.068577 | 0.12934 | -0.00022865 | -0.00086512 | 0.11772 | -0.00091437 | 0.0028134 | 0.0007456 | 0.0019824 | -0.0026063 | 63.8031 | 63.9038 | -0.059509 | -59.2712 | 63.8031 | -59.0973 | -59.1522 | -59.0744 | 0.004578 | -59.3811 | 63.8443 | 63.7894 | -59.1202 | -59.2346 | 0.032043 | -0.022889 | -0.054931 | 123.0331 | -0.14191 | -0.11902 | -0.054931 | 0.009155 | -0.10529 | -0.013733 | 0.054931 | -0.25177 | -0.14648 | -0.068664 | 122.9324 | 122.9324 | 59.0698 | -123.0103 | 122.9736 | 122.9187 | 59.1339 | -123.0927
376.5156 | 123.1659 | -59.0744 | 63.8992 | -0.1709 | 0.0073315 | 0.06545 | 0.069218 | 0.13233 | 0.001694 | -0.0021469 | -0.034867 | -5.9768e-05 | 0.0006772 | -0.000109 | -0.00015383 | -0.0019653 | 63.8168 | 63.9313 | -0.009155 | -59.2575 | 63.826 | -59.0836 | -59.1202 | -59.0424 | 0.086975 | -59.317 | 63.8672 | 63.8168 | -59.111 | -59.2392 | -0.009155 | -0.045776 | -0.073242 | 123.0057 | -0.1831 | -0.13733 | -0.082398 | -0.036621 | -0.16479 | -0.032044 | 0.032044 | -0.24262 | -0.07782 | -0.082398 | 122.9004 | 122.8912 | 59.0652 | -123.0194 | 122.9416 | 122.8912 | 59.1614 | -123.1384
377.5156 | 123.111 | -59.0927 | 63.8809 | -0.018311 | 0.010322 | 0.064809 | 0.069432 | 0.13126 | 0.00062595 | -0.0012923 | 0.056686 | -0.0019824 | 0.0011044 | -0.0013906 | 0.0013416 | -0.0032471 | 63.8397 | 63.9313 | -0.032043 | -59.2758 | 63.7939 | -59.111 | -59.0927 | -59.0652 | 0.041199 | -59.3719 | 63.8672 | 63.8077 | -59.1248 | -59.2392 | -0.018311 | 0 | -0.086975 | 123.024 | -0.18311 | -0.18311 | -0.041198 | -0.032044 | -0.14648 | -0.013733 | 0.027465 | -0.27924 | -0.13275 | -0.073242 | 122.8867 | 122.9324 | 59.0607 | -122.9736 | 122.9599 | 122.9004 | 59.1339 | -123.1201
378.5156 | 123.1338 | -59.0836 | 63.8809 | -0.086975 | 0.011818 | 0.067586 | 0.070927 | 0.13383 | 0.003403 | -0.0023605 | 0.049057 | -0.0017688 | 0.0015316 | 0.000532 | 0.002837 | -0.0041017 | 63.8306 | 63.945 | -0.004578 | -59.2438 | 63.8351 | -59.0973 | -59.1156 | -59.0378 | 0.059509 | -59.5139 | 63.8214 | 63.7711 | -59.1476 | -59.2438 | -0.013733 | -0.032044 | -0.045776 | 123.0286 | -0.16022 | -0.12817 | -0.050354 | -0.064087 | -0.16022 | -0.059509 | 0.045776 | -0.4303 | -0.27008 | -0.10986 | 122.9187 | 122.9141 | 59.079 | -122.9965 | 122.905 | 122.8546 | 59.1431 | -123.1247
379.5156 | 123.143 | -59.079 | 63.8763 | 0.035095 | 0.011177 | 0.065022 | 0.068577 | 0.12956 | 0.00083955 | -0.0010787 | 0.01091 | -0.0013416 | 0.0008908 | 0.0007456 | 0.001128 | -0.0015381 | 63.8489 | 63.9633 | 0 | -59.23 | 63.8351 | -59.0927 | -59.1064 | -59.0286 | 0.064087 | -59.3353 | 63.8489 | 63.7711 | -59.1339 | -59.2163 | -0.013733 | -0.027466 | -0.041199 | 123.0423 | -0.15106 | -0.1236 | -0.027466 | -0.054932 | -0.13733 | -0.027466 | 0.050354 | -0.25635 | -0.11902 | -0.10529 | 122.9141 | 122.9279 | 59.079 | -122.9828 | 122.9279 | 122.85 | 59.1431 | -123.0927
380.5156 | 123.0972 | -59.0698 | 63.8901 | -0.14801 | 0.0090405 | 0.067372 | 0.068577 | 0.13062 | -0.0015102 | -0.0027877 | -0.027237 | -0.0019824 | 0.0011044 | 0.0026682 | 0.0030506 | -0.0013245 | 63.8214 | 63.945 | -0.018311 | -59.2392 | 63.858 | -59.0881 | -59.1385 | -59.0424 | 0.082397 | -59.3033 | 63.8718 | 63.8123 | -59.1019 | -59.2255 | -0.018311 | -0.068665 | -0.032044 | 123.0148 | -0.16937 | -0.10071 | -0.068665 | -0.032044 | -0.15564 | -0.018311 | 0.027466 | -0.23346 | -0.07782 | -0.07782 | 122.9279 | 122.8912 | 59.0515 | -123.0286 | 122.9416 | 122.8821 | 59.1522 | -123.1155
381.5156 | 123.0698 | -59.0973 | 63.8672 | 0.17242 | 0.010322 | 0.06545 | 0.067082 | 0.12849 | 0.0046848 | -0.0038559 | 0.033798 | -0.002196 | 0.001959 | 0.0016 | 0.00070077 | -0.0032471 | 63.9771 | 63.9221 | -0.10986 | -59.3124 | 63.826 | -59.1019 | -59.1476 | -59.111 | -0.073242 | -59.4177 | 63.8306 | 63.7939 | -59.1614 | -59.2712 | -0.004578 | -0.050354 | -0.041198 | 123.0194 | -0.21515 | -0.16479 | 0.10986 | -0.064087 | -0.17395 | -0.036621 | -0.013733 | -0.32043 | -0.14648 | -0.073242 | 122.9233 | 123.0743 | 58.9874 | -123.0148 | 122.9279 | 122.8912 | 59.024 | -123.1384
382.5156 | 123.0835 | -59.1064 | 63.8718 | -0.094604 | 0.01075 | 0.066731 | 0.071995 | 0.13041 | 0.001694 | -0.00022432 | 0.01091 | -0.00070077 | 0.001959 | 0.0009592 | 0.0015552 | -4.2662e-05 | 63.8306 | 63.945 | -0.018311 | -59.2529 | 63.8168 | -59.079 | -59.1339 | -59.1064 | -0.19226 | -59.3216 | 63.8443 | 63.7985 | -59.0927 | -59.2255 | 0.027466 | -0.027466 | -0.054932 | 123.0515 | -0.14648 | -0.11902 | -0.041199 | 0.013733 | -0.11902 | -0.027466 | 0 | -0.21515 | -0.09613 | -0.073242 | 122.9233 | 122.937 | 59.0881 | -123.0057 | 122.9507 | 122.905 | 58.9142 | -123.0972
383.5156 | 123.0927 | -59.1019 | 63.8214 | 0.027466 | 0.012672 | 0.065663 | 0.070286 | 0.12956 | 0.0029758 | 0.00020288 | 0.079574 | -5.9768e-05 | -0.0021 | 0.0011728 | 0.0015552 | -0.0030335 | 63.8214 | 63.8992 | -0.059509 | -59.2941 | 63.8306 | -59.0744 | -59.1431 | -59.0836 | 0.009155 | -59.3674 | 63.8489 | 63.8168 | -59.1293 | -59.23 | 0.027466 | -0.041198 | 0.009155 | 123.0011 | -0.19226 | -0.15106 | 0 | -0.027465 | -0.12817 | 0.027466 | 0.018311 | -0.2655 | -0.13733 | -0.004578 | 122.9324 | 122.9233 | 59.0424 | -122.9645 | 122.9507 | 122.9187 | 59.111 | -123.0515
384.5156 | 123.0835 | -59.079 | 63.8763 | -0.14801 | 0.0073315 | 0.066731 | 0.069432 | 0.12934 | -0.0017238 | -0.0040695 | -0.065384 | 0.00058103 | 0.0023862 | 0.000532 | -0.00015383 | -0.00047006 | 63.8031 | 63.9084 | -0.054932 | -59.2621 | 63.8351 | -59.0836 | -59.1248 | -59.079 | 0.068665 | -59.3536 | 63.8901 | 63.8535 | -59.1064 | -59.2163 | -0.004578 | -0.045777 | -0.041199 | 122.9874 | -0.18311 | -0.13733 | -0.073242 | -0.027466 | -0.13733 | 0.013733 | 0 | -0.27466 | -0.13733 | -0.022888 | 122.9141 | 122.8821 | 59.024 | -123.0011 | 122.9691 | 122.9324 | 59.1476 | -123.0927
385.5156 | 123.0652 | -59.111 | 63.8672 | 0.057983 | 0.011818 | 0.066731 | 0.067723 | 0.12977 | 0.001694 | -0.0025741 | 0.11009 | -0.00091437 | 0.001318 | -0.0007498 | 0.0015552 | -0.0026063 | 63.7848 | 63.8763 | -0.086975 | -59.2941 | 63.8168 | -59.0973 | -59.1476 | -59.1019 | -0.059509 | -59.4131 | 63.8535 | 63.8123 | -59.1522 | -59.2575 | 0.013733 | -0.036621 | -0.050354 | 122.9874 | -0.1831 | -0.14648 | -0.082397 | -0.041199 | -0.14648 | -0.013732 | 0.009155 | -0.30212 | -0.15564 | -0.054931 | 122.9279 | 122.8958 | 59.024 | -123.0148 | 122.9645 | 122.9233 | 59.0515 | -123.1247
386.5156 | 123.0927 | -59.1019 | 63.9084 | -0.39978 | 0.0073315 | 0.067372 | 0.06815 | 0.12998 | -0.0030056 | -0.0017197 | -0.042496 | 0.00036743 | 0.001959 | -0.0016044 | 5.9768e-05 | -0.0019653 | 63.7619 | 63.8901 | -0.018311 | -59.2667 | 63.8214 | -59.1156 | -59.1202 | -59.0881 | 0.059509 | -59.3445 | 63.858 | 63.8535 | -59.0973 | -59.2209 | -0.013733 | -0.01831 | -0.086975 | 122.9919 | -0.16479 | -0.14648 | -0.14648 | 0.004578 | -0.11902 | -0.050354 | 0.013733 | -0.24261 | -0.1236 | -0.054931 | 122.9233 | 122.8638 | 59.0836 | -123.0286 | 122.9599 | 122.9553 | 59.1614 | -123.1293
387.5156 | 123.1613 | -59.0698 | 63.8489 | -0.67444 | 0.01075 | 0.067159 | 0.069432 | 0.13062 | 0.002335 | 0.00020288 | 0.071945 | -0.00070077 | 0.0025998 | 0.000532 | 0.002196 | -0.0030335 | 63.8535 | 63.9679 | 0.009155 | -59.2438 | 63.8168 | -59.0881 | -59.1156 | -59.0286 | 0.036621 | -59.3353 | 63.8672 | 63.7894 | -59.1064 | -59.2346 | -0.018311 | -0.045777 | -0.032044 | 123.0377 | -0.17395 | -0.12817 | 0.004578 | -0.036621 | -0.1648 | 0.01831 | 0.041199 | -0.2655 | -0.10071 | -0.059509 | 122.8867 | 122.9233 | 59.079 | -122.9645 | 122.937 | 122.8592 | 59.1064 | -123.0835
388.5156 | 123.111 | -59.0698 | 63.8992 | -0.12512 | 0.0088269 | 0.0678 | 0.069432 | 0.12998 | -0.0019376 | -0.0023605 | -0.11879 | -0.0017688 | 0.0006772 | -0.0003226 | 5.9768e-05 | -0.0019653 | 63.8031 | 63.8992 | -0.045776 | -59.2758 | 63.8397 | -59.0927 | -59.1202 | -59.079 | 0.045776 | -59.3628 | 63.8763 | 63.8168 | -59.1339 | -59.2255 | -0.022888 | -0.050354 | -0.059509 | 122.9691 | -0.20599 | -0.15564 | -0.09613 | -0.064087 | -0.15564 | -0.022888 | -0.009155 | -0.29297 | -0.13733 | -0.082398 | 122.9095 | 122.8729 | 59.024 | -123.0194 | 122.9462 | 122.8867 | 59.1156 | -123.1247
389.5156 | 123.1476 | -59.0698 | 63.8626 | -0.064087 | 0.012245 | 0.063954 | 0.071354 | 0.12977 | 0.00083955 | -0.0021469 | 1.5826 | -0.0013416 | -0.0023136 | -0.0009634 | 0.0024096 | -0.0019653 | 63.8397 | 63.9359 | -0.004578 | -59.2484 | 63.8123 | -59.0836 | -59.1202 | -59.0057 | 0.064087 | -59.3124 | 63.858 | 63.7985 | -59.111 | -59.2392 | -0.013733 | -0.050354 | -0.050354 | 123.0057 | -0.17853 | -0.12817 | -0.022888 | -0.041199 | -0.16937 | -0.004578 | 0.064087 | -0.24262 | -0.073242 | -0.064087 | 122.8821 | 122.9095 | 59.0652 | -122.9828 | 122.9279 | 122.8683 | 59.1339 | -123.1018
390.5156 | 123.0881 | -59.0836 | 63.8901 | -0.45319 | 0.0086133 | 0.066731 | 0.068791 | 0.12849 | -0.001083 | -0.0034287 | -0.065384 | -0.0043324 | 3.6404e-05 | 0.0003182 | 5.9768e-05 | -4.2662e-05 | 63.7711 | 63.9313 | -0.009155 | -59.2758 | 63.8351 | -59.079 | -59.1293 | -59.079 | 0.050354 | -59.3491 | 63.8992 | 63.8351 | -59.1339 | -59.2438 | 0.004578 | -0.045776 | -0.054932 | 123.0148 | -0.19226 | -0.14648 | -0.11902 | -0.050354 | -0.16022 | 0.009155 | 0.004578 | -0.2655 | -0.10529 | -0.054932 | 122.9187 | 122.8546 | 59.0744 | -123.0194 | 122.9828 | 122.9187 | 59.1339 | -123.1338
391.5156 | 123.1155 | -59.079 | 63.8672 | -0.10986 | 0.010109 | 0.065022 | 0.067296 | 0.12998 | 0.0014804 | -0.00065152 | -0.019608 | -0.0013416 | -0.0012454 | -0.0003226 | 0.0013416 | -0.0028199 | 63.8214 | 63.9404 | 0.013733 | -59.2484 | 63.8443 | -59.0698 | -59.1156 | -59.0469 | 0.068665 | -59.3216 | 63.8672 | 63.8168 | -59.1339 | -59.2255 | 0.009155 | -0.036622 | -0.022888 | 123.0194 | -0.16937 | -0.13275 | -0.045776 | -0.054932 | -0.14649 | 0 | 0.032043 | -0.24262 | -0.09613 | -0.050354 | 122.9233 | 122.9004 | 59.0927 | -122.9828 | 122.9462 | 122.8958 | 59.1476 | -123.0927
392.5156 | 123.0652 | -59.0836 | 63.9084 | -0.20142 | 0.0043409 | 0.067586 | 0.066868 | 0.1287 | 0.00041235 | -0.0023605 | -0.23323 | -0.0019824 | 0.00025 | 0.0003182 | 0.00048697 | -0.00025626 | 63.9816 | 63.8763 | -0.045776 | -59.3674 | 63.8351 | -59.1064 | -59.1248 | -59.079 | 0.045776 | -59.3536 | 63.8763 | 63.8123 | -59.1202 | -59.23 | -0.022888 | -0.041199 | -0.073242 | 122.9599 | -0.28381 | -0.24262 | 0.073242 | -0.036621 | -0.14648 | -0.032043 | 0.004578 | -0.27008 | -0.1236 | -0.09613 | 122.9187 | 123.0652 | 59.0378 | -123.0331 | 122.9599 | 122.8958 | 59.1293 | -123.1384
393.5156 | 123.1293 | -59.079 | 63.8718 | -0.1709 | 0.010963 | 0.066518 | 0.069218 | 0.13169 | 0.002335 | -0.0015061 | -0.065384 | -0.002196 | -0.0021 | -0.0009634 | -0.0014356 | -0.0043153 | 63.8535 | 63.9359 | -0.022888 | -59.2392 | 63.8306 | -59.079 | -59.1339 | -59.0332 | 0.086975 | -59.3216 | 63.8763 | 63.8077 | -59.1019 | -59.2209 | 0 | -0.054932 | -0.041199 | 123.0148 | -0.16022 | -0.10529 | -0.01831 | -0.022889 | -0.14191 | 0.004578 | 0.045776 | -0.24262 | -0.10071 | -0.064087 | 122.9095 | 122.9324 | 59.0561 | -123.0057 | 122.9553 | 122.8867 | 59.166 | -123.0927
394.5156 | 123.0972 | -59.0973 | 63.9175 | -0.1709 | 0.0060497 | 0.06844 | 0.06815 | 0.12827 | -0.00065585 | -0.0017197 | -0.042496 | -0.001128 | -0.0018862 | -0.0007498 | 0.0026234 | -4.2662e-05 | 63.7894 | 63.9038 | -0.036621 | -59.2529 | 63.8214 | -59.079 | -59.1156 | -59.0744 | 0.050354 | -59.3582 | 63.9038 | 63.8443 | -59.1019 | -59.2026 | 0.018311 | -0.018311 | -0.096131 | 123.0011 | -0.15564 | -0.13733 | -0.12817 | -0.004578 | -0.10529 | -0.013733 | 0.022888 | -0.26093 | -0.15564 | -0.073243 | 122.9187 | 122.8867 | 59.0607 | -123.0331 | 123.0011 | 122.9416 | 59.1476 | -123.1201
395.5156 | 123.143 | -59.0698 | 63.8535 | -0.14038 | 0.012031 | 0.067159 | 0.066227 | 0.1302 | 0.001694 | 0.00041648 | -1.3853 | -0.00091437 | 3.6404e-05 | -0.0009634 | 0.0034778 | -0.0034607 | 63.8397 | 63.9359 | -0.009155 | -59.2438 | 63.826 | -59.079 | -59.1202 | -59.0469 | 0.086975 | -59.317 | 63.8489 | 63.8123 | -59.1156 | -59.23 | -0.009155 | -0.050354 | -0.027466 | 123.0057 | -0.17395 | -0.1236 | -0.013733 | -0.045777 | -0.16022 | -0.004578 | 0.022888 | -0.24719 | -0.086975 | -0.041199 | 122.8958 | 122.9095 | 59.0607 | -122.9736 | 122.9187 | 122.8821 | 59.1568 | -123.0835
396.5156 | 123.111 | -59.0836 | 63.9221 | -0.19379 | 0.0086133 | 0.068868 | 0.067296 | 0.13233 | -1.505e-05 | -0.0023605 | -0.073013 | -0.0017688 | 0.001318 | -0.0020316 | -0.00058103 | -0.00068366 | 63.7665 | 63.9175 | -0.036621 | -59.2712 | 63.858 | -59.079 | -59.1156 | -59.0744 | 0.045776 | -59.3491 | 63.8901 | 63.8077 | -59.1202 | -59.1934 | 0.004578 | -0.032044 | -0.064087 | 123.0011 | -0.18768 | -0.15564 | -0.15564 | -0.036621 | -0.10986 | -0.032043 | 0.009155 | -0.2655 | -0.15564 | -0.11444 | 122.9416 | 122.85 | 59.0469 | -123.0377 | 122.9736 | 122.8912 | 59.1293 | -123.1155
397.5156 | 123.1476 | -59.0881 | 63.8809 | -0.056458 | 0.012886 | 0.064809 | 0.068791 | 0.13084 | 0.00041235 | -0.00022432 | -0.011978 | -0.0026234 | 0.0034542 | 0.0009592 | -0.0010082 | -0.0021789 | 63.8168 | 63.9496 | 0 | -59.2621 | 63.8443 | -59.1019 | -59.1339 | -59.0698 | 0.082397 | -59.3033 | 63.8809 | 63.7985 | -59.1202 | -59.2255 | -0.013733 | -0.045776 | -0.036621 | 123.0377 | -0.17395 | -0.12817 | -0.064087 | -0.032043 | -0.13733 | 0 | 0.018311 | -0.21515 | -0.07782 | -0.082397 | 122.9324 | 122.905 | 59.0881 | -123.0148 | 122.9691 | 122.8867 | 59.1705 | -123.1064
398.5156 | 123.1018 | -59.0881 | 63.9175 | -0.23956 | 0.0066907 | 0.066091 | 0.070286 | 0.12892 | -0.0017238 | -0.0010787 | -0.095902 | -0.0015552 | -0.0006046 | -0.0016044 | -0.00036743 | -0.0026063 | 63.7939 | 63.8947 | -0.036621 | -59.2758 | 63.8351 | -59.0881 | -59.1431 | -59.0836 | 0.036621 | -59.3491 | 63.8809 | 63.8031 | -59.1339 | -59.2255 | 0 | -0.054931 | -0.082398 | 122.9828 | -0.18768 | -0.13275 | -0.1236 | -0.045776 | -0.13733 | -0.036622 | 0.004578 | -0.26093 | -0.1236 | -0.11444 | 122.9233 | 122.8821 | 59.0515 | -123.0606 | 122.9691 | 122.8912 | 59.1248 | -123.143
399.5156 | 123.1201 | -59.0698 | 63.8397 | -0.033569 | 0.012031 | 0.065663 | 0.070286 | 0.12998 | 0.0038304 | -0.00065152 | 0.049057 | -0.0036914 | 0.0006772 | -0.0026724 | 0.0013416 | -0.0019653 | 63.8351 | 63.9359 | -0.013733 | -59.2621 | 63.8077 | -59.1156 | -59.1019 | -59.0561 | 0.050354 | -59.3536 | 63.858 | 63.7985 | -59.1202 | -59.2392 | -0.045777 | -0.032044 | -0.032044 | 123.0057 | -0.19226 | -0.16022 | -0.004578 | -0.050354 | -0.16937 | 0.01831 | 0.013733 | -0.28381 | -0.11444 | -0.041199 | 122.8775 | 122.905 | 59.0561 | -122.9416 | 122.9279 | 122.8683 | 59.1202 | -123.0789
400.5156 | 123.111 | -59.0927 | 63.8947 | -0.056458 | 0.0075451 | 0.066731 | 0.069645 | 0.12956 | -0.0017238 | -0.0042831 | -0.034867 | -0.00070077 | 0.00025 | -0.000109 | -0.00058103 | -0.0011109 | 63.8031 | 63.8992 | -0.036621 | -59.285 | 63.826 | -59.0927 | -59.1064 | -59.0698 | 0.045776 | -59.3445 | 63.8947 | 63.826 | -59.1293 | -59.2255 | 0 | -0.013733 | -0.068664 | 122.9919 | -0.19226 | -0.17853 | -0.091552 | -0.036621 | -0.13275 | 0 | 0.022888 | -0.25177 | -0.11902 | -0.068664 | 122.9187 | 122.8958 | 59.0561 | -123.0011 | 122.9874 | 122.9187 | 59.1385 | -123.1201
401.5156 | 123.1338 | -59.0652 | 63.8809 | -0.018311 | 0.0098951 | 0.066304 | 0.067509 | 0.12763 | 0.001694 | -0.0017197 | 0.041427 | -0.0015552 | 0.0023862 | 0.0003182 | 0.0030506 | -0.0026063 | 63.8351 | 63.945 | -0.009155 | -59.2621 | 63.8031 | -59.0973 | -59.1293 | -59.0332 | 0.027466 | -59.3536 | 63.8351 | 63.7894 | -59.1385 | -59.2484 | -0.032043 | -0.064086 | -0.077819 | 123.0103 | -0.19684 | -0.13275 | -0.045776 | -0.073242 | -0.1831 | -0.045776 | 0.032044 | -0.28839 | -0.10529 | -0.091552 | 122.8683 | 122.9004 | 59.0561 | -123.0103 | 122.9004 | 122.8546 | 59.0927 | -123.1293
402.5156 | 123.111 | -59.0881 | 63.8809 | -0.15564 | 0.0083997 | 0.068227 | 0.070927 | 0.12998 | 0.00019875 | -0.0017197 | -0.14931 | -0.0017688 | -0.0025272 | -0.0005362 | 0.00091437 | -0.0034607 | 63.7802 | 63.913 | -0.018311 | -59.2392 | 63.8489 | -59.079 | -59.1202 | -59.0469 | 0.07782 | -59.3353 | 63.8947 | 63.826 | -59.1064 | -59.2117 | 0.009156 | -0.032043 | -0.032043 | 123.0011 | -0.15106 | -0.11902 | -0.10071 | -0.01831 | -0.1236 | 0.013733 | 0.041199 | -0.24719 | -0.1236 | -0.054931 | 122.937 | 122.8683 | 59.0698 | -123.0011 | 122.9828 | 122.9141 | 59.166 | -123.0927
403.5156 | 123.0972 | -59.0744 | 63.858 | -0.079346 | 0.01139 | 0.067159 | 0.068791 | 0.12913 | 0.0012668 | -0.0012923 | 0.064316 | -0.001128 | 0.003027 | 0.0009592 | 0.0017688 | -0.0030335 | 63.8351 | 63.9404 | -0.022888 | -59.2484 | 63.8031 | -59.0744 | -59.111 | -59.0515 | 0.027466 | -59.3445 | 63.8626 | 63.7665 | -59.1202 | -59.23 | 0 | -0.036621 | -0.054931 | 123.0148 | -0.17395 | -0.13733 | -0.022888 | -0.045776 | -0.15564 | 0.004578 | 0.022888 | -0.27008 | -0.11444 | -0.091553 | 122.8775 | 122.9095 | 59.0515 | -122.9691 | 122.937 | 122.8409 | 59.1019 | -123.0881
404.5156 | 123.1155 | -59.0607 | 63.8855 | -0.14801 | 0.0090405 | 0.066091 | 0.067296 | 0.12763 | 0.0014804 | -0.0032151 | -0.11879 | -0.002837 | 0.00025 | -0.001177 | 0.00027337 | -0.0032471 | 63.7848 | 63.9267 | -0.032043 | -59.2529 | 63.8397 | -59.079 | -59.1064 | -59.0744 | 0.073242 | -59.3445 | 63.8763 | 63.8306 | -59.1064 | -59.2117 | -0.01831 | -0.045776 | -0.045776 | 122.9874 | -0.19226 | -0.14648 | -0.10071 | -0.045776 | -0.15106 | -0.009155 | -0.013733 | -0.28381 | -0.13275 | -0.054932 | 122.9004 | 122.8455 | 59.0286 | -122.9919 | 122.937 | 122.8912 | 59.1339 | -123.0972
405.5156 | 123.0927 | -59.0698 | 63.8763 | -0.14801 | 0.010322 | 0.065022 | 0.070714 | 0.13383 | 0.0012668 | -0.0027877 | 0.041427 | -0.0015552 | 0.0006772 | -0.0007498 | 0.001128 | -0.0028199 | 63.8397 | 63.9359 | -0.013733 | -59.2392 | 63.8077 | -59.1064 | -59.1385 | -59.0515 | 0.045776 | -59.3445 | 63.8443 | 63.7985 | -59.0973 | -59.2438 | -0.036621 | -0.068665 | -0.068665 | 123.0057 | -0.16937 | -0.10071 | -0.036621 | -0.027466 | -0.17395 | -0.032044 | 0.01831 | -0.27466 | -0.10071 | -0.07782 | 122.8775 | 122.9095 | 59.0561 | -123.0148 | 122.9141 | 122.8683 | 59.1156 | -123.1201
406.5156 | 123.024 | -59.1156 | 63.8855 | -0.094604 | 0.0083997 | 0.067586 | 0.068577 | 0.13169 | 0.0025486 | -0.0015061 | -0.027237 | -0.0026234 | 3.6404e-05 | -0.0007498 | 0.0024096 | -0.0034607 | 63.8306 | 63.9404 | -0.009155 | -59.23 | 63.826 | -59.0836 | -59.1385 | -59.0286 | 0.07782 | -59.3124 | 63.8489 | 63.8168 | -59.1156 | -59.2438 | 0.032044 | -0.022888 | -0.059509 | 123.056 | -0.11444 | -0.091553 | -0.054932 | 0 | -0.12817 | -0.036621 | 0.086976 | -0.19684 | -0.068665 | -0.068665 | 122.9416 | 122.9462 | 59.1064 | -123.024 | 122.9645 | 122.9324 | 59.1934 | -123.1293
407.5156 | 123.1155 | -59.0698 | 63.8718 | -0.1709 | 0.010963 | 0.066731 | 0.068791 | 0.13041 | 0.00062595 | -0.0019333 | 0.064316 | -0.0019824 | 0.0011044 | 0.0007456 | 0.0015552 | -0.0036743 | 63.8535 | 63.9404 | -0.013733 | -59.2575 | 63.7985 | -59.0836 | -59.1293 | -59.0515 | 0.045776 | -59.3445 | 63.8626 | 63.8077 | -59.1202 | -59.23 | -0.013733 | -0.059509 | -0.073242 | 123.0103 | -0.18768 | -0.12817 | -0.01831 | -0.050354 | -0.16022 | -0.009155 | 0.01831 | -0.27466 | -0.11444 | -0.064087 | 122.8683 | 122.9233 | 59.0561 | -123.0011 | 122.9324 | 122.8775 | 59.1156 | -123.1018
408.5156 | 123.1018 | -59.0836 | 63.858 | -0.12512 | 0.0088269 | 0.066304 | 0.070286 | 0.13212 | 0.00083955 | -0.0032151 | 0.01091 | -5.9768e-05 | 0.001318 | -0.0003226 | 0.002196 | -0.0021789 | 63.8351 | 63.9542 | 0 | -59.2484 | 63.8443 | -59.1019 | -59.1293 | -59.0332 | 0.086975 | -59.3308 | 63.858 | 63.8214 | -59.1476 | -59.2255 | -0.018311 | -0.045776 | -0.013733 | 123.0377 | -0.16479 | -0.11902 | -0.022888 | -0.064087 | -0.14191 | 0 | 0.050354 | -0.24719 | -0.10529 | -0.036621 | 122.9279 | 122.9187 | 59.0836 | -122.9874 | 122.9416 | 122.905 | 59.1705 | -123.0835
409.5156 | 123.1064 | -59.0927 | 63.8672 | 0.0045777 | 0.013527 | 0.065877 | 0.066868 | 0.13148 | 0.0029758 | -0.0025741 | 0.094833 | -0.0015552 | 0.0021726 | -0.000109 | 0.002837 | -0.0023927 | 63.7939 | 63.913 | -0.041199 | -59.2667 | 63.8168 | -59.1248 | -59.1385 | -59.0652 | 0.013733 | -59.3719 | 63.8443 | 63.7848 | -59.1202 | -59.2255 | -0.032044 | -0.045777 | -0.050354 | 123.0057 | -0.17395 | -0.12817 | -0.073242 | -0.027466 | -0.13275 | -0.022888 | 0.027465 | -0.27924 | -0.14648 | -0.082397 | 122.9095 | 122.8867 | 59.0515 | -123.0057 | 122.937 | 122.8775 | 59.1064 | -123.0927
410.5156 | 123.1293 | -59.0607 | 63.8947 | -0.16327 | 0.01139 | 0.065663 | 0.069005 | 0.13105 | 0.00041235 | -0.0015061 | -0.050125 | -0.00091437 | 0.001318 | -0.0009634 | 0.0015552 | -0.0021789 | 63.8214 | 63.9359 | 0 | -59.23 | 63.8351 | -59.0836 | -59.1248 | -59.0378 | 0.068665 | -59.3079 | 63.8763 | 63.8168 | -59.0927 | -59.2484 | -0.022888 | -0.064087 | -0.059509 | 122.9965 | -0.16937 | -0.10529 | -0.073242 | -0.032043 | -0.18768 | -0.01831 | 0.022888 | -0.24719 | -0.059509 | -0.07782 | 122.8958 | 122.8821 | 59.0607 | -123.0194 | 122.937 | 122.8775 | 59.1293 | -123.143
411.5156 | 123.0835 | -59.0881 | 63.8306 | 0.0045777 | 0.011604 | 0.064382 | 0.069859 | 0.13105 | 0.0014804 | -0.0040695 | 0.11772 | -0.002196 | 0.0025998 | -0.0003226 | 0.0036914 | -0.0017517 | 63.7985 | 63.913 | -0.050354 | -59.2621 | 63.826 | -59.0973 | -59.1293 | -59.0836 | 0 | -59.3674 | 63.8443 | 63.7894 | -59.1385 | -59.2484 | -0.009155 | -0.041198 | -0.004577 | 123.0011 | -0.17395 | -0.13275 | -0.032043 | -0.050354 | -0.16022 | 0.013733 | 0.004578 | -0.27924 | -0.11902 | -0.041198 | 122.9141 | 122.8867 | 59.0378 | -122.9599 | 122.9324 | 122.8775 | 59.0881 | -123.0789
412.5156 | 123.1293 | -59.0698 | 63.8947 | -0.033569 | 0.01075 | 0.066304 | 0.067723 | 0.12806 | 0.0019078 | -0.0025741 | -0.042496 | -0.00091437 | 0.0006772 | 0.0011728 | 0.0013416 | -0.0011109 | 64.0045 | 63.9359 | -0.009155 | -59.2209 | 63.8535 | -59.0927 | -59.1156 | -59.0195 | 0.050354 | -59.3216 | 63.8672 | 63.8306 | -59.1064 | -59.2209 | -0.022888 | -0.045777 | -0.041198 | 123.0057 | -0.15106 | -0.10529 | 0.10986 | -0.036621 | -0.15106 | -0.027466 | 0.050354 | -0.25177 | -0.10071 | -0.064087 | 122.9233 | 123.0743 | 59.0607 | -123.0103 | 122.937 | 122.9004 | 59.1202 | -123.1155
413.5156 | 123.0331 | -59.1202 | 63.8535 | 0.050354 | 0.013527 | 0.0678 | 0.066868 | 0.1302 | 0.0025486 | -0.0023605 | 0.17113 | -0.0017688 | -0.0006046 | 0.0003182 | 0.00091437 | -0.0030335 | 63.7711 | 63.8626 | -0.091553 | -59.2804 | 63.8123 | -59.1064 | -59.1476 | -59.1202 | -0.07782 | -59.4223 | 63.8672 | 63.8031 | -59.1156 | -59.2392 | 0.013733 | -0.027466 | -0.041199 | 122.9828 | -0.16022 | -0.13275 | -0.082398 | 0.004577 | -0.11902 | 0.013732 | 0 | -0.30212 | -0.18311 | -0.050354 | 122.9324 | 122.8912 | 59.0286 | -123.0011 | 122.9874 | 122.9233 | 59.0424 | -123.0927
414.5156 | 123.1293 | -59.0469 | 63.8809 | -0.11749 | 0.013099 | 0.067372 | 0.069005 | 0.12849 | 0.00019875 | -0.0021469 | -0.050125 | -0.0017688 | 0.0023862 | -0.0013906 | 0.002196 | -0.0034607 | 63.7939 | 63.9084 | -0.027466 | -59.2438 | 63.858 | -59.0881 | -59.1293 | -59.0561 | 0.073242 | -59.3308 | 63.8763 | 63.8168 | -59.0973 | -59.2346 | -0.041199 | -0.082397 | -0.022888 | 122.9553 | -0.19684 | -0.11444 | -0.086975 | -0.050354 | -0.18768 | -0.004577 | -0.009155 | -0.28381 | -0.096131 | -0.064087 | 122.905 | 122.8409 | 59.0195 | -123.0103 | 122.9233 | 122.8638 | 59.1202 | -123.1155
415.5156 | 123.0652 | -59.1064 | 63.8901 | 0.080872 | 0.012459 | 0.065877 | 0.069005 | 0.13105 | 0.002335 | 0.00063028 | 0.12535 | 0.00058103 | 0.0004636 | -0.001818 | 0.0017688 | -0.0036743 | 63.7711 | 63.8626 | -0.10071 | -59.2896 | 63.7939 | -59.0973 | -59.1293 | -59.111 | -0.045776 | -59.4177 | 63.8443 | 63.8077 | -59.1248 | -59.2712 | 0.009155 | -0.022888 | -0.096131 | 122.9691 | -0.18311 | -0.16022 | -0.11902 | -0.018311 | -0.16479 | -0.045777 | -0.004578 | -0.31128 | -0.14648 | -0.082398 | 122.9004 | 122.8775 | 59.0057 | -123.0194 | 122.9507 | 122.9141 | 59.0607 | -123.1613
416.5156 | 123.1293 | -59.0744 | 63.8763 | -0.14038 | 0.011604 | 0.064809 | 0.068364 | 0.13169 | 0.0010532 | -0.0012923 | 0.041427 | 0.0025036 | 0.0015316 | 0.0001046 | 0.00091437 | -0.0038879 | 63.826 | 63.9404 | -0.013733 | -59.2392 | 63.8443 | -59.0973 | -59.1248 | -59.0607 | 0.11444 | -59.3216 | 63.8809 | 63.8031 | -59.1293 | -59.2529 | -0.022888 | -0.050354 | -0.032044 | 123.0148 | -0.16479 | -0.11444 | -0.050354 | -0.054931 | -0.17853 | 0.004577 | 0.013733 | -0.24719 | -0.068664 | -0.073242 | 122.9187 | 122.9004 | 59.0607 | -123.0011 | 122.9553 | 122.8775 | 59.1888 | -123.1293
417.5156 | 123.0652 | -59.111 | 63.8718 | 0.11902 | 0.012459 | 0.065663 | 0.066014 | 0.13062 | -0.00022865 | -0.0015061 | -0.095902 | 0.00015383 | 0.001959 | -0.0030996 | 0.00070077 | -0.0026063 | 63.7344 | 63.8168 | -0.14648 | -59.3124 | 63.826 | -59.111 | -59.1843 | -59.1202 | -0.027466 | -59.3903 | 63.8809 | 63.7985 | -59.1476 | -59.2575 | 0 | -0.073242 | -0.045776 | 122.9279 | -0.20142 | -0.12817 | -0.13733 | -0.036621 | -0.14648 | 0.009155 | -0.009155 | -0.27924 | -0.13275 | -0.073242 | 122.937 | 122.8455 | 58.9645 | -123.056 | 122.9919 | 122.9095 | 59.0836 | -123.1293
418.5156 | 123.2117 | -59.0973 | 63.8763 | -0.14038 | 0.011177 | 0.0631 | 0.067723 | 0.13105 | 0.001694 | -0.00043792 | -0.042496 | -0.0026234 | 0.0004636 | -0.000109 | 0.00070077 | -0.0036743 | 63.8443 | 63.945 | 0.009155 | -59.23 | 63.8306 | -59.0881 | -59.1202 | -59.024 | 0.07782 | -59.3262 | 63.8626 | 63.8214 | -59.111 | -59.2484 | 0.009155 | -0.022888 | -0.045777 | 123.0423 | -0.13275 | -0.10986 | -0.032044 | -0.013733 | -0.15106 | -0.013733 | 0.073242 | -0.22888 | -0.07782 | -0.054932 | 122.9279 | 122.9416 | 59.1064 | -122.9965 | 122.9599 | 122.9187 | 59.1751 | -123.1247
419.5156 | 123.0927 | -59.1064 | 63.8718 | 0.057983 | 0.013313 | 0.067159 | 0.067509 | 0.1287 | 0.0025486 | -0.0017197 | 0.13298 | -0.001128 | 0.00025 | -0.0009634 | 5.9768e-05 | -0.0032471 | 63.8168 | 63.8901 | -0.064087 | -59.2712 | 63.8168 | -59.0927 | -59.1202 | -59.0973 | 0.004578 | -59.3811 | 63.8443 | 63.7939 | -59.1476 | -59.2392 | 0.013733 | -0.013733 | -0.054932 | 122.9965 | -0.16479 | -0.15106 | -0.054932 | -0.041199 | -0.13275 | -0.027466 | 0.009155 | -0.27466 | -0.14191 | -0.07782 | 122.9233 | 122.9233 | 59.0424 | -122.9919 | 122.9507 | 122.9004 | 59.111 | -123.111
420.5156 | 123.1293 | -59.0652 | 63.8626 | -0.16327 | 0.011818 | 0.066731 | 0.069218 | 0.13041 | 0.002335 | -0.0010787 | -0.019608 | -0.0019824 | 0.00025 | 0.000532 | 0.00048697 | -0.0030335 | 63.8351 | 63.9221 | -0.013733 | -59.23 | 63.7985 | -59.111 | -59.1476 | -59.0286 | 0.082397 | -59.317 | 63.8718 | 63.8168 | -59.1202 | -59.2346 | -0.045776 | -0.082397 | -0.064087 | 122.9874 | -0.16479 | -0.082398 | -0.027466 | -0.054931 | -0.16937 | 0.009155 | 0.036622 | -0.25177 | -0.082398 | -0.045777 | 122.8638 | 122.9004 | 59.0515 | -123.0103 | 122.937 | 122.8821 | 59.1476 | -123.0972
421.5156 | 123.1018 | -59.1019 | 63.8947 | 0.027466 | 0.01075 | 0.066731 | 0.067723 | 0.13084 | 0.00062595 | -0.0030013 | 0.11772 | -0.00070077 | 0.001318 | 0.0001046 | 0.0030506 | -0.00068366 | 63.826 | 63.913 | -0.054932 | -59.2758 | 63.8123 | -59.0881 | -59.1248 | -59.0469 | 0.009155 | -59.3674 | 63.8718 | 63.8123 | -59.1202 | -59.2484 | 0.013733 | -0.022888 | -0.082397 | 123.0148 | -0.17395 | -0.15106 | -0.068664 | -0.01831 | -0.14648 | -0.022888 | 0.054932 | -0.2655 | -0.11902 | -0.082397 | 122.9141 | 122.9279 | 59.0469 | -123.0194 | 122.9736 | 122.9141 | 59.111 | -123.143
422.5156 | 123.1384 | -59.0698 | 63.8947 | -0.10223 | 0.011604 | 0.06844 | 0.068577 | 0.12998 | -0.001083 | -0.0019333 | 0.17876 | -0.0013416 | 0.001318 | -0.0003226 | 0.0013416 | -0.0038879 | 63.8214 | 63.913 | -0.018311 | -59.3216 | 63.8031 | -59.079 | -59.1522 | -59.024 | 0.082397 | -59.3033 | 63.8443 | 63.8123 | -59.1019 | -59.2392 | -0.009155 | -0.082398 | -0.091552 | 122.9828 | -0.25177 | -0.16937 | -0.073242 | -0.032044 | -0.16937 | -0.050354 | 0.045776 | -0.23346 | -0.064087 | -0.082397 | 122.8729 | 122.8912 | 59.0515 | -123.0469 | 122.9141 | 122.8821 | 59.1522 | -123.1338
423.5312 | 123.1567 | -59.0652 | 63.8306 | 0.4776 | 0.0060497 | 0.070149 | 0.066868 | 0.12956 | -0.0055692 | 0.012379 | 0.19402 | -0.0030506 | -0.003168 | -0.0007498 | -0.0014356 | -0.0030335 | 63.7848 | 63.945 | -0.045776 | -59.2758 | 63.7573 | -59.1202 | -59.1156 | -59.0286 | 0.036621 | -59.3033 | 63.8306 | 63.7665 | -59.0836 | -59.2346 | -0.054931 | -0.050354 | -0.073242 | 123.0103 | -0.21057 | -0.16022 | -0.045776 | -0.01831 | -0.16937 | 0 | 0.036622 | -0.23804 | -0.068665 | -0.064087 | 122.8226 | 122.85 | 59.0195 | -122.9462 | 122.8958 | 122.8317 | 59.1019 | -123.0652
424.5156 | 123.0927 | -59.0744 | 63.8947 | -0.14801 | 0.010963 | 0.068868 | 0.067723 | 0.13319 | 0.0010532 | -0.0017197 | -0.027237 | -0.001128 | -0.0012454 | 0.0007456 | 0.002837 | -0.0030335 | 63.8535 | 63.9496 | 0.009155 | -59.2438 | 63.8214 | -59.079 | -59.1202 | -59.0286 | 0.068665 | -59.317 | 63.8626 | 63.7756 | -59.1431 | -59.2575 | -0.004577 | -0.045776 | -0.073242 | 123.024 | -0.16937 | -0.1236 | -0.041198 | -0.068664 | -0.1831 | -0.032043 | 0.045777 | -0.24262 | -0.05951 | -0.11902 | 122.8958 | 122.9279 | 59.0836 | -123.0148 | 122.937 | 122.85 | 59.1431 | -123.1522
425.5156 | 123.0881 | -59.0973 | 63.8489 | 0.09613 | 0.0098951 | 0.067372 | 0.068364 | 0.13041 | 0.004044 | -0.0019333 | 0.1635 | 0.00015383 | 0.00025 | -0.0009634 | 0.002196 | -0.0013245 | 63.7619 | 63.8443 | -0.13733 | -59.2987 | 63.7894 | -59.111 | -59.1568 | -59.0744 | -0.62714 | -59.6054 | 63.7894 | 63.7527 | -59.1431 | -59.2346 | -0.013733 | -0.059509 | -0.059509 | 122.9416 | -0.20142 | -0.14191 | -0.086975 | -0.045776 | -0.13733 | -0.059509 | 0.022888 | -0.50812 | -0.37079 | -0.09613 | 122.8867 | 122.8592 | 58.96 | -123.0057 | 122.8867 | 122.85 | 58.4702 | -123.0835
426.5156 | 123.0972 | -59.111 | 63.8535 | -0.0030518 | 0.011818 | 0.066518 | 0.069218 | 0.1287 | 0.0031894 | 0.00063028 | 0.12535 | -0.0013416 | 0.0015316 | 0.0011728 | 0.0013416 | -0.0017517 | 63.8306 | 63.9084 | -0.059509 | -59.2621 | 63.8123 | -59.111 | -59.1293 | -59.0607 | -0.018311 | -59.3536 | 63.8535 | 63.8168 | -59.1385 | -59.2484 | 0 | -0.01831 | -0.041199 | 123.0194 | -0.15106 | -0.13275 | -0.022889 | -0.027466 | -0.13733 | 0 | 0.050354 | -0.24261 | -0.10529 | -0.036622 | 122.9233 | 122.9416 | 59.0515 | -122.9828 | 122.9645 | 122.9279 | 59.0927 | -123.1018
427.5156 | 123.0743 | -59.1019 | 63.8626 | 0.012207 | 0.012672 | 0.065877 | 0.067509 | 0.12785 | 0.00041235 | -0.0017197 | 0.056686 | 0.00079463 | 0.0011044 | -0.0005362 | 0.0026234 | -0.0038879 | 63.8123 | 63.913 | -0.045776 | -59.2621 | 63.8214 | -59.0927 | -59.1019 | -59.0515 | 0.004578 | -59.3903 | 63.858 | 63.7985 | -59.1202 | -59.2484 | 0.009156 | 0 | -0.041199 | 123.0148 | -0.16022 | -0.16022 | -0.050354 | -0.01831 | -0.14648 | -0.004578 | 0.050354 | -0.28839 | -0.14191 | -0.064087 | 122.9233 | 122.9141 | 59.0561 | -122.9645 | 122.9599 | 122.9004 | 59.1064 | -123.111
428.5156 | 123.1018 | -59.0607 | 63.8855 | -0.14038 | 0.0083997 | 0.066731 | 0.068364 | 0.13105 | -0.00022865 | -0.0023605 | -0.034867 | -0.0017688 | -0.0018862 | -0.0005362 | 0.00048697 | -0.0038879 | 63.8077 | 63.913 | -0.018311 | -59.2346 | 63.858 | -59.079 | -59.1202 | -59.0561 | 0.073242 | -59.3353 | 63.8855 | 63.8306 | -59.1156 | -59.2117 | -0.01831 | -0.059509 | -0.027466 | 122.9736 | -0.17395 | -0.11444 | -0.07782 | -0.054932 | -0.15106 | 0 | 0.004578 | -0.27466 | -0.1236 | -0.054932 | 122.9187 | 122.8683 | 59.0424 | -123.0057 | 122.9462 | 122.8912 | 59.1339 | -123.0972
429.5156 | 123.0789 | -59.1064 | 63.8763 | 0.019836 | 0.01075 | 0.066091 | 0.069859 | 0.12977 | 0.002335 | -0.0010787 | 0.11772 | -0.00091437 | 0.003027 | -0.0005362 | 0.0036914 | -0.0034607 | 63.7802 | 63.8763 | -0.091553 | -59.2804 | 63.8214 | -59.1202 | -59.1522 | -59.1064 | -0.036621 | -59.3903 | 63.8535 | 63.7985 | -59.1385 | -59.2621 | -0.013733 | -0.045777 | -0.054932 | 122.9828 | -0.17395 | -0.12817 | -0.096131 | -0.032044 | -0.15564 | -0.022888 | 0 | -0.28381 | -0.12817 | -0.07782 | 122.9279 | 122.8867 | 59.0149 | -123.0286 | 122.9599 | 122.905 | 59.0698 | -123.1384
430.5156 | 123.1247 | -59.0652 | 63.8855 | -0.13275 | 0.012672 | 0.065663 | 0.069218 | 0.12956 | 0.00041235 | -0.0032151 | 0.026169 | 0.0010082 | 0.0028134 | -0.000109 | -0.0014356 | -0.0030335 | 63.8306 | 63.9175 | -0.013733 | -59.23 | 63.8123 | -59.0881 | -59.1202 | -59.0607 | 0.073242 | -59.3033 | 63.8626 | 63.8123 | -59.1156 | -59.23 | -0.022888 | -0.054931 | -0.073242 | 122.9828 | -0.16479 | -0.10986 | -0.054932 | -0.050354 | -0.16479 | -0.022888 | 0.004578 | -0.23804 | -0.073242 | -0.073242 | 122.8775 | 122.8958 | 59.0515 | -123.0057 | 122.9279 | 122.8775 | 59.1385 | -123.1155
431.5156 | 123.0606 | -59.0881 | 63.8992 | 0.050354 | 0.012672 | 0.066091 | 0.069645 | 0.12913 | -0.00044225 | -0.0012923 | 0.094833 | 0.0010082 | -0.001459 | -0.0024588 | 0.0024096 | -0.0021789 | 63.7711 | 63.8992 | -0.07782 | -59.2804 | 63.826 | -59.0836 | -59.1202 | -59.0927 | -0.013733 | -59.3903 | 63.8672 | 63.8123 | -59.1156 | -59.2438 | 0.004578 | -0.032043 | -0.073242 | 122.9874 | -0.19226 | -0.16022 | -0.12817 | -0.027466 | -0.15564 | -0.032044 | -0.004577 | -0.30212 | -0.14648 | -0.086975 | 122.9141 | 122.8592 | 59.0103 | -123.0194 | 122.9553 | 122.9004 | 59.0744 | -123.143
432.5156 | 123.0286 | -59.1019 | 63.8763 | -0.10223 | 0.012459 | 0.066731 | 0.0705 | 0.13105 | 0.002335 | -1.0724e-05 | 0.026169 | -0.00091437 | 0.0008908 | 0.0001046 | 0.0024096 | -0.0019653 | 63.826 | 63.9359 | -0.013733 | -59.23 | 63.8351 | -59.0927 | -59.1156 | -59.0378 | 0.073242 | -59.3216 | 63.8626 | 63.7939 | -59.1293 | -59.2484 | 0.009156 | -0.013733 | -0.041199 | 123.0377 | -0.12817 | -0.11444 | -0.050354 | -0.027465 | -0.14648 | -0.013733 | 0.064087 | -0.21973 | -0.073242 | -0.082398 | 122.937 | 122.9279 | 59.0881 | -122.9919 | 122.9645 | 122.8958 | 59.1751 | -123.1247
433.5156 | 123.1842 | -59.0149 | 63.8351 | -0.033569 | 0.0060497 | 0.067372 | 0.06815 | 0.13041 | -0.0040738 | -0.0032151 | 2.0022 | -0.0068958 | -0.0023136 | 0.0011728 | -0.0010082 | -0.0013245 | 63.8718 | 64.0686 | 0.086975 | -59.1934 | 63.7985 | -59.0195 | -59.0515 | -58.9737 | 0.14648 | -59.2621 | 63.826 | 63.7802 | -59.1064 | -59.2209 | -0.004577 | -0.036621 | -0.036621 | 123.0835 | -0.17853 | -0.14191 | 0.036621 | -0.091552 | -0.20599 | -0.009155 | 0.041199 | -0.24719 | -0.041199 | -0.054932 | 122.8134 | 122.8867 | 59.1019 | -122.8867 | 122.8409 | 122.7951 | 59.1614 | -123.056
434.5156 | 123.1155 | -59.0744 | 63.8626 | -0.17853 | 0.0083997 | 0.066945 | 0.071354 | 0.13062 | 0.0031894 | -0.0015061 | -0.073013 | -0.0017688 | -0.000391 | -0.0013906 | 0.0026234 | -0.0017517 | 63.8306 | 63.945 | -0.009155 | -59.2438 | 63.8443 | -59.0927 | -59.1339 | -59.0378 | 0.086975 | -59.317 | 63.8718 | 63.7848 | -59.1248 | -59.23 | -0.01831 | -0.059509 | -0.018311 | 123.0194 | -0.16937 | -0.10986 | -0.032044 | -0.050354 | -0.15564 | 0.009155 | 0.036621 | -0.24262 | -0.086975 | -0.07782 | 122.9187 | 122.905 | 59.0652 | -122.9965 | 122.9462 | 122.8592 | 59.1614 | -123.0927
435.5156 | 123.1018 | -59.0881 | 63.8672 | -0.0030518 | 0.011177 | 0.066731 | 0.067723 | 0.13126 | 0.0019078 | -0.00065152 | 0.071945 | 0.00015383 | 0.001318 | 0.000532 | 0.0032642 | -0.0053833 | 63.8214 | 63.913 | -0.041199 | -59.2667 | 63.8077 | -59.1019 | -59.1431 | -59.0515 | 0.004578 | -59.3674 | 63.8489 | 63.7985 | -59.1431 | -59.2438 | -0.013733 | -0.054931 | -0.059509 | 123.0011 | -0.17853 | -0.1236 | -0.045776 | -0.054931 | -0.15564 | -0.01831 | 0.036621 | -0.27924 | -0.1236 | -0.068664 | 122.8958 | 122.9095 | 59.0469 | -123.0103 | 122.937 | 122.8867 | 59.0927 | -123.111
436.5156 | 123.1293 | -59.0744 | 63.8763 | -0.10223 | 0.010536 | 0.065022 | 0.066655 | 0.13191 | 0.0019078 | -0.00022432 | 2.048 | -0.002196 | 0.0006772 | -0.0016044 | 0.0024096 | -0.0019653 | 63.8351 | 63.9221 | -0.013733 | -59.2438 | 63.8123 | -59.0973 | -59.1339 | -59.0057 | 0.082397 | -59.317 | 63.8535 | 63.7939 | -59.1156 | -59.2209 | -0.022888 | -0.059509 | -0.064087 | 122.9965 | -0.16937 | -0.10986 | -0.041199 | -0.041199 | -0.14648 | -0.022888 | 0.068665 | -0.24262 | -0.096131 | -0.082398 | 122.8867 | 122.9095 | 59.0607 | -123.0103 | 122.9279 | 122.8683 | 59.1568 | -123.0972
437.5156 | 123.0469 | -59.0927 | 63.8855 | 0.042725 | 0.0098951 | 0.065663 | 0.066868 | 0.12977 | 0.0019078 | -0.0012923 | 0.11772 | -0.002196 | 0.0015316 | 0.0011728 | 0.0015552 | -0.0036743 | 63.7894 | 63.8763 | -0.068665 | -59.2712 | 63.8168 | -59.1019 | -59.1522 | -59.0927 | -0.032043 | -59.3857 | 63.8535 | 63.7802 | -59.1476 | -59.2712 | -0.009156 | -0.05951 | -0.068665 | 122.9691 | -0.17853 | -0.11902 | -0.09613 | -0.054932 | -0.17853 | -0.032043 | 0 | -0.29297 | -0.11444 | -0.10529 | 122.9095 | 122.8821 | 59.024 | -123.0377 | 122.9462 | 122.8729 | 59.0607 | -123.1567
438.5156 | 123.1613 | -59.079 | 63.826 | 0.2182 | 0.010963 | 0.065663 | 0.068577 | 0.13084 | 0.00019875 | -0.0019333 | 0.3466 | -0.0015552 | 0.0004636 | -0.000109 | 0.001128 | -0.0023927 | 63.7711 | 63.8855 | -0.11444 | -59.2987 | 63.7894 | -59.111 | -59.1248 | -59.0424 | -0.013733 | -59.3308 | 63.7939 | 63.7619 | -59.111 | -59.23 | -0.032044 | -0.045777 | -0.036621 | 122.9645 | -0.21973 | -0.17395 | -0.054932 | -0.032044 | -0.15106 | -0.032044 | 0.036621 | -0.25177 | -0.10071 | -0.064087 | 122.8683 | 122.85 | 58.9645 | -122.9507 | 122.8729 | 122.8409 | 59.0652 | -123.056
439.5156 | 123.0606 | -59.0927 | 63.858 | 0.012207 | 0.014168 | 0.064595 | 0.069859 | 0.13276 | 0.0019078 | 0.00020288 | 0.071945 | 0.0012218 | 0.0023862 | -0.0022452 | 0.00070077 | -0.0028199 | 63.826 | 63.9038 | -0.045776 | -59.2712 | 63.8123 | -59.1064 | -59.1202 | -59.0836 | 0.009155 | -59.3674 | 63.8443 | 63.8031 | -59.1156 | -59.2484 | -0.013733 | -0.027466 | -0.045776 | 122.9965 | -0.17853 | -0.15106 | -0.032043 | -0.022889 | -0.15564 | -0.013733 | 0.009155 | -0.27466 | -0.11902 | -0.054931 | 122.905 | 122.9187 | 59.0469 | -122.9782 | 122.937 | 122.8958 | 59.1019 | -123.1064
440.5156 | 123.1384 | -59.0561 | 63.8626 | -0.10986 | 0.011818 | 0.068227 | 0.070073 | 0.12849 | 0.001694 | -0.0021469 | 0.049057 | 0.00015383 | 0.0015316 | 0.0003182 | 0.0024096 | -0.0017517 | 63.8306 | 63.9267 | -0.004578 | -59.2346 | 63.8306 | -59.111 | -59.1293 | -59.0424 | 0.07782 | -59.2987 | 63.8535 | 63.8168 | -59.111 | -59.2346 | -0.054932 | -0.073242 | -0.032044 | 122.9828 | -0.17853 | -0.10529 | -0.032044 | -0.054932 | -0.17853 | -0.009155 | 0.013733 | -0.24262 | -0.064087 | -0.045777 | 122.8867 | 122.8867 | 59.0515 | -122.9919 | 122.9095 | 122.8729 | 59.1339 | -123.0972
441.5156 | 123.1155 | -59.0561 | 63.8626 | -0.033569 | 0.010109 | 0.064809 | 0.068364 | 0.13169 | 0.00062595 | -0.0019333 | 0.064316 | -0.00048697 | 0.0006772 | 0.0009592 | 0.002837 | -0.0017517 | 63.8443 | 63.9175 | -0.022888 | -59.2621 | 63.8168 | -59.0744 | -59.1385 | -59.0561 | 0.036621 | -59.3491 | 63.8489 | 63.8031 | -59.1248 | -59.2575 | -0.018311 | -0.082398 | -0.045777 | 122.9736 | -0.20599 | -0.1236 | -0.018311 | -0.068665 | -0.20142 | -0.013733 | 0 | -0.29297 | -0.091553 | -0.059509 | 122.8729 | 122.9004 | 59.0332 | -123.0011 | 122.905 | 122.8592 | 59.0927 | -123.1201
442.5156 | 123.111 | -59.0744 | 63.8809 | -0.12512 | 0.0094677 | 0.068013 | 0.0705 | 0.12998 | 0.00041235 | -0.0012923 | -0.11116 | -0.00070077 | 0.0004636 | 0.0009592 | 0.00027337 | -0.0030335 | 63.7939 | 63.9084 | -0.022888 | -59.2758 | 63.826 | -59.0836 | -59.1202 | -59.0652 | 0.086975 | -59.317 | 63.9038 | 63.8397 | -59.111 | -59.2072 | -0.009155 | -0.045776 | -0.054931 | 122.9828 | -0.20142 | -0.15564 | -0.086975 | -0.036621 | -0.13275 | 0.022889 | 0.009155 | -0.24262 | -0.10986 | -0.041198 | 122.9004 | 122.8683 | 59.0515 | -123.0011 | 122.9782 | 122.9141 | 59.1614 | -123.0881
443.5156 | 123.1979 | -59.0698 | 63.8306 | 0.14954 | 0.0073315 | 0.066304 | 0.06815 | 0.12934 | -0.0030056 | -0.0012923 | 0.36949 | -0.0019824 | -0.0016726 | -0.0030996 | 0.0024096 | -0.0023927 | 63.8351 | 63.9771 | -0.013733 | -59.23 | 63.7344 | -59.0973 | -59.1248 | -58.9966 | 0.054932 | -59.285 | 63.7802 | 63.739 | -59.1156 | -59.2484 | -0.027466 | -0.054932 | -0.09613 | 123.0469 | -0.16022 | -0.10529 | 0.004578 | -0.045777 | -0.17853 | -0.050354 | 0.073242 | -0.21515 | -0.036621 | -0.091552 | 122.8043 | 122.905 | 59.0561 | -122.9553 | 122.85 | 122.8088 | 59.1248 | -123.0789
444.5156 | 123.0881 | -59.0698 | 63.8672 | -0.12512 | 0.0086133 | 0.069081 | 0.066868 | 0.12998 | 0.0012668 | -0.00022432 | -0.073013 | 0.00036743 | -0.0006046 | -0.0024588 | -0.00036743 | -0.0038879 | 63.8351 | 63.8901 | -0.018311 | -59.2392 | 63.8535 | -59.0744 | -59.1064 | -59.0424 | 0.086975 | -59.3124 | 63.8672 | 63.8214 | -59.1064 | -59.2484 | -0.004578 | -0.036621 | -0.013732 | 122.9599 | -0.16937 | -0.13275 | -0.032043 | -0.036621 | -0.17853 | 0 | 0.027466 | -0.24262 | -0.064087 | -0.045776 | 122.9233 | 122.905 | 59.0515 | -122.9736 | 122.937 | 122.8912 | 59.1568 | -123.1155
445.5156 | 123.111 | -59.0973 | 63.8672 | 0.0045777 | 0.010322 | 0.066518 | 0.068577 | 0.12977 | 0.003403 | -0.00043792 | 0.064316 | -0.0019824 | 0.0021726 | -0.001818 | 0.00048697 | -0.0028199 | 63.8397 | 63.9084 | -0.027466 | -59.2529 | 63.8168 | -59.1019 | -59.1202 | -59.0607 | 0.022888 | -59.3536 | 63.8626 | 63.7939 | -59.1385 | -59.2392 | -0.004578 | -0.022888 | -0.050354 | 123.0057 | -0.15564 | -0.13275 | -0.027465 | -0.041199 | -0.14191 | -0.004577 | 0.036621 | -0.25635 | -0.11444 | -0.073242 | 122.9141 | 122.937 | 59.0698 | -122.9874 | 122.9599 | 122.8912 | 59.1202 | -123.1064
446.5156 | 123.111 | -59.0652 | 63.8901 | -0.17853 | 0.0086133 | 0.065877 | 0.070714 | 0.12849 | 0.00041235 | -0.0019333 | -0.080643 | -0.0019824 | -0.0010318 | -0.000109 | 0.00091437 | -0.0030335 | 63.8077 | 63.9038 | -0.032043 | -59.2529 | 63.8535 | -59.0836 | -59.1156 | -59.0698 | 0.050354 | -59.3308 | 63.8947 | 63.8123 | -59.1293 | -59.2163 | -0.01831 | -0.050354 | -0.036621 | 122.9691 | -0.18768 | -0.13733 | -0.082398 | -0.064086 | -0.15106 | 0.004577 | -0.004577 | -0.2655 | -0.11444 | -0.07782 | 122.9187 | 122.8729 | 59.0332 | -123.0057 | 122.9599 | 122.8775 | 59.1156 | -123.1064
447.5156 | 123.0789 | -59.0744 | 63.8626 | 0.019836 | 0.01139 | 0.065236 | 0.070714 | 0.12892 | 0.0014804 | -0.00065152 | 0.056686 | -0.0024096 | 0.00025 | -0.0013906 | 0.0032642 | -0.0019653 | 63.8031 | 63.8947 | -0.064087 | -59.2804 | 63.7985 | -59.1019 | -59.1339 | -59.0744 | -0.013733 | -59.3811 | 63.858 | 63.7894 | -59.111 | -59.2758 | -0.027466 | -0.059509 | -0.064087 | 122.9691 | -0.20599 | -0.14649 | -0.059509 | -0.036621 | -0.20142 | -0.004578 | 0 | -0.3067 | -0.10529 | -0.073242 | 122.8729 | 122.8775 | 59.0103 | -122.9965 | 122.9324 | 122.8638 | 59.0607 | -123.1384
448.5156 | 123.1659 | -59.0652 | 63.8214 | 0.11902 | 0.0092541 | 0.066091 | 0.064732 | 0.13126 | -0.0015102 | 0.0016983 | 0.35423 | -0.0030506 | 0.0017454 | -0.0024588 | -0.0010082 | -0.0038879 | 63.8168 | 63.9633 | -0.018311 | -59.2346 | 63.7573 | -59.0927 | -59.1156 | -58.9828 | 0.041199 | -59.2712 | 63.7848 | 63.7299 | -59.1202 | -59.2438 | -0.027465 | -0.050354 | -0.064087 | 123.0286 | -0.16937 | -0.11902 | -0.004578 | -0.054931 | -0.17853 | -0.036621 | 0.082398 | -0.20599 | -0.027466 | -0.091553 | 122.8226 | 122.8821 | 59.0469 | -122.937 | 122.85 | 122.7951 | 59.1064 | -123.0652
449.5156 | 123.0835 | -59.0973 | 63.858 | -0.064087 | 0.010963 | 0.06844 | 0.069218 | 0.13041 | 0.0031894 | -0.0010787 | 0.049057 | -0.0030506 | 0.0021726 | 0.0001046 | 0.0058276 | -0.0034607 | 63.8443 | 63.9221 | -0.036621 | -59.2575 | 63.826 | -59.0881 | -59.1339 | -59.0378 | 0.004578 | -59.3674 | 63.8397 | 63.8123 | -59.1339 | -59.23 | 0.009155 | -0.036621 | -0.032043 | 123.0194 | -0.16022 | -0.1236 | -0.013733 | -0.036621 | -0.13275 | -0.01831 | 0.059509 | -0.27008 | -0.13733 | -0.045776 | 122.9233 | 122.9416 | 59.0607 | -122.9919 | 122.937 | 122.9095 | 59.1019 | -123.0881
450.5156 | 123.1476 | -59.0927 | 63.8809 | -0.11749 | 0.0083997 | 0.06844 | 0.067936 | 0.12614 | 0.00062595 | -0.0017197 | -0.10353 | 0.00058103 | -0.0008182 | -0.001177 | 5.9768e-05 | -0.00089726 | 63.8031 | 63.9084 | -0.045776 | -59.2392 | 63.8443 | -59.0744 | -59.0836 | -59.0469 | 0.086975 | -59.3308 | 63.8809 | 63.8489 | -59.1339 | -59.23 | 0.01831 | 0.009155 | -0.036621 | 123.0011 | -0.14648 | -0.15564 | -0.077819 | -0.041199 | -0.13733 | 0 | 0.045776 | -0.23804 | -0.10071 | -0.032043 | 122.937 | 122.8958 | 59.0469 | -122.9645 | 122.9736 | 122.9416 | 59.1797 | -123.111
451.5156 | 123.1338 | -59.0927 | 63.8626 | 0.019836 | 0.011177 | 0.066518 | 0.06815 | 0.12977 | 0.001694 | -1.0724e-05 | 0.056686 | -0.00091437 | -0.000391 | -0.0016044 | 0.00091437 | -0.0023927 | 63.8306 | 63.9359 | 0 | -59.2529 | 63.8168 | -59.0881 | -59.1293 | -59.0424 | 0.027466 | -59.3399 | 63.8535 | 63.7802 | -59.1293 | -59.2163 | 0.004577 | -0.036621 | -0.045777 | 123.0286 | -0.16022 | -0.1236 | -0.032044 | -0.036621 | -0.1236 | -0.009155 | 0.050354 | -0.24719 | -0.1236 | -0.082398 | 122.9095 | 122.9233 | 59.0927 | -122.9919 | 122.9462 | 122.8729 | 59.1202 | -123.0789
452.5156 | 123.1064 | -59.0836 | 63.9038 | -0.16327 | 0.010109 | 0.066304 | 0.066441 | 0.12956 | -0.00065585 | -0.0012923 | -0.10353 | -0.0015552 | -0.0006046 | -0.0030996 | 0.0015552 | -0.0028199 | 63.7894 | 63.8947 | -0.045776 | -59.2484 | 63.8535 | -59.0881 | -59.1248 | -59.0607 | 0.073242 | -59.3262 | 63.8809 | 63.8168 | -59.1202 | -59.2163 | -0.004578 | -0.041199 | -0.050354 | 122.9782 | -0.16479 | -0.1236 | -0.11444 | -0.036621 | -0.13275 | -0.022889 | 0.022888 | -0.24262 | -0.10986 | -0.086976 | 122.937 | 122.8729 | 59.0378 | -123.0286 | 122.9645 | 122.9004 | 59.1568 | -123.1201
453.5156 | 123.0972 | -59.0698 | 63.8489 | 0.012207 | 0.012886 | 0.065236 | 0.069645 | 0.13105 | 0.0014804 | -0.0017197 | 0.10246 | -0.0013416 | 0.0008908 | 0.0003182 | 0.002837 | -0.0021789 | 63.8077 | 63.9221 | -0.054932 | -59.2758 | 63.826 | -59.0836 | -59.1385 | -59.0469 | 0.004578 | -59.3582 | 63.8489 | 63.7894 | -59.1385 | -59.2712 | -0.013733 | -0.068665 | -0.022888 | 122.9919 | -0.20599 | -0.13733 | -0.041199 | -0.068665 | -0.20142 | 0 | 0.022888 | -0.28839 | -0.086975 | -0.059509 | 122.8958 | 122.8775 | 59.0149 | -122.9874 | 122.9187 | 122.8592 | 59.0744 | -123.1201
454.5156 | 123.1018 | -59.0973 | 63.8626 | -0.1709 | 0.0098951 | 0.064595 | 0.070286 | 0.13276 | -1.505e-05 | -0.0034287 | -0.019608 | -0.001128 | 0.00025 | -0.0009634 | 0.002196 | -0.0013245 | 63.8077 | 63.9221 | -0.018311 | -59.2346 | 63.8397 | -59.0927 | -59.1156 | -59.0515 | 0.07782 | -59.3079 | 63.8763 | 63.8214 | -59.0927 | -59.198 | 0.004578 | -0.018311 | -0.022888 | 123.0194 | -0.13733 | -0.11902 | -0.054932 | 0.004578 | -0.10071 | 0.013733 | 0.045776 | -0.21057 | -0.10986 | -0.041199 | 122.937 | 122.905 | 59.079 | -122.9782 | 122.9736 | 122.9187 | 59.1751 | -123.0606
455.5156 | 123.111 | -59.079 | 63.8626 | -0.079346 | 0.011818 | 0.068227 | 0.067296 | 0.12998 | 0.0010532 | 0.00020288 | -0.088272 | -0.0030506 | -0.0010318 | -0.0003226 | 0.0024096 | -0.0023927 | 63.8168 | 63.9587 | 0.009155 | -59.3903 | 63.7711 | -59.1293 | -59.166 | -59.024 | 0.082397 | -59.3079 | 63.8397 | 63.8214 | -59.1202 | -59.2209 | -0.050354 | -0.086976 | -0.091553 | 123.0377 | -0.31128 | -0.2243 | -0.045777 | -0.041199 | -0.14191 | -0.022888 | 0.054931 | -0.22888 | -0.086975 | -0.041199 | 122.85 | 122.8958 | 59.0881 | -123.0286 | 122.9187 | 122.9004 | 59.1614 | -123.0835
456.5156 | 123.1293 | -59.079 | 63.8901 | -0.14801 | 0.010109 | 0.067372 | 0.068791 | 0.13212 | -0.0012966 | -0.0027877 | -0.057755 | 0.00015383 | 0.001318 | -0.000109 | 0.00070077 | -0.0013245 | 63.7894 | 63.9267 | -0.022888 | -59.2529 | 63.8397 | -59.1064 | -59.111 | -59.0561 | 0.068665 | -59.3033 | 63.8763 | 63.8443 | -59.1019 | -59.2209 | -0.027466 | -0.032044 | -0.050354 | 123.0057 | -0.17395 | -0.14191 | -0.10071 | -0.022889 | -0.14191 | -0.013733 | 0.022888 | -0.22431 | -0.082398 | -0.045777 | 122.9187 | 122.8683 | 59.0561 | -123.0011 | 122.9553 | 122.9233 | 59.1476 | -123.111
457.5156 | 123.1064 | -59.1064 | 63.8626 | -0.0030518 | 0.011177 | 0.06545 | 0.069645 | 0.12913 | 0.001694 | -0.0030013 | 0.049057 | -0.001128 | 0.0032406 | 0.0003182 | 0.0030506 | -0.0028199 | 63.8168 | 63.9496 | -0.022888 | -59.2667 | 63.8351 | -59.079 | -59.1293 | -59.0469 | 0.050354 | -59.3399 | 63.858 | 63.7985 | -59.0973 | -59.2392 | 0.027466 | -0.022888 | -0.027466 | 123.056 | -0.16022 | -0.13733 | -0.045777 | 0.009155 | -0.13275 | -0.004578 | 0.059509 | -0.23346 | -0.10071 | -0.064087 | 122.9416 | 122.9233 | 59.0836 | -122.9919 | 122.9645 | 122.905 | 59.1568 | -123.1018
458.5156 | 123.1018 | -59.0561 | 63.9038 | -0.14038 | 0.0092541 | 0.06545 | 0.069859 | 0.13105 | 0.0012668 | -0.0034287 | -0.057755 | -0.0034778 | 3.6404e-05 | -0.0016044 | 0.00091437 | -0.0019653 | 63.7848 | 63.9038 | -0.036621 | -59.2575 | 63.8535 | -59.0927 | -59.1385 | -59.0881 | 0.068665 | -59.3399 | 63.8763 | 63.8214 | -59.1248 | -59.2209 | -0.036621 | -0.082398 | -0.050354 | 122.9599 | -0.20142 | -0.11902 | -0.11902 | -0.068665 | -0.16479 | -0.027466 | -0.032044 | -0.28381 | -0.11902 | -0.082398 | 122.9095 | 122.8409 | 59.0195 | -123.0423 | 122.9324 | 122.8775 | 59.1248 | -123.1247
459.5156 | 123.1155 | -59.0836 | 63.858 | -0.010681 | 0.010963 | 0.062673 | 0.070073 | 0.13169 | 0.002335 | -0.00043792 | 0.079574 | 0.00036743 | -0.0001774 | -0.0005362 | -0.00015383 | -0.0023927 | 63.8306 | 63.9725 | -0.009155 | -59.2575 | 63.8397 | -59.0744 | -59.1202 | -59.0195 | 0.059509 | -59.3216 | 63.8397 | 63.8306 | -59.1293 | -59.23 | 0.009155 | -0.036621 | -0.01831 | 123.056 | -0.17395 | -0.13733 | -0.027466 | -0.045776 | -0.14648 | -0.01831 | 0.064087 | -0.23804 | -0.091552 | -0.027466 | 122.9233 | 122.9141 | 59.0744 | -122.9782 | 122.9233 | 122.9141 | 59.1431 | -123.0881
460.5156 | 123.143 | -59.0927 | 63.8626 | -0.17853 | 0.01075 | 0.066518 | 0.070714 | 0.12956 | 0.00062595 | -0.0025741 | -0.080643 | -0.0024096 | -0.0018862 | -0.0024588 | -0.00058103 | -0.0013245 | 63.8123 | 63.9084 | -0.018311 | -59.2484 | 63.8443 | -59.0607 | -59.1202 | -59.0378 | 0.082397 | -59.3033 | 63.8672 | 63.826 | -59.111 | -59.2346 | 0.032043 | -0.027466 | -0.018311 | 123.0011 | -0.15564 | -0.12817 | -0.050354 | -0.018311 | -0.14191 | 0.004577 | 0.054931 | -0.21057 | -0.068665 | -0.036621 | 122.937 | 122.905 | 59.0744 | -122.9828 | 122.9599 | 122.9187 | 59.1751 | -123.0972
461.5156 | 123.1247 | -59.079 | 63.8809 | -0.02594 | 0.014381 | 0.065663 | 0.069218 | 0.13105 | 0.00083955 | -0.0034287 | 0.041427 | 0.00058103 | 3.6404e-05 | 0.0009592 | -0.00015383 | -0.0023927 | 63.8214 | 63.9267 | -0.032043 | -59.2575 | 63.8123 | -59.0836 | -59.1156 | -59.0424 | 0.018311 | -59.3399 | 63.8397 | 63.8168 | -59.1385 | -59.2438 | -0.004578 | -0.036622 | -0.068664 | 123.0057 | -0.17853 | -0.14191 | -0.059509 | -0.05951 | -0.1648 | -0.041198 | 0.036621 | -0.26093 | -0.096131 | -0.064087 | 122.8912 | 122.9004 | 59.0469 | -122.9965 | 122.9187 | 122.8958 | 59.0973 | -123.1247
462.5156 | 123.0972 | -59.0652 | 63.8855 | -0.20142 | 0.0081861 | 0.068654 | 0.070714 | 0.13276 | 0.00062595 | -0.0025741 | -0.13405 | -0.0013416 | 0.0008908 | 0.0016 | 0.00070077 | -0.00025626 | 63.7711 | 63.8672 | -0.059509 | -59.2987 | 63.8306 | -59.1019 | -59.1385 | -59.079 | 0.050354 | -59.3582 | 63.9038 | 63.8214 | -59.1339 | -59.2163 | -0.036621 | -0.073242 | -0.054932 | 122.9324 | -0.23346 | -0.16022 | -0.11444 | -0.068664 | -0.15106 | 0.018311 | -0.013732 | -0.29297 | -0.14191 | -0.064087 | 122.8958 | 122.8363 | 59.0057 | -123.024 | 122.9691 | 122.8867 | 59.1156 | -123.1018
463.5156 | 123.1338 | -59.0652 | 63.8855 | -0.1709 | 0.012031 | 0.067586 | 0.067936 | 0.1287 | 0.00083955 | -0.0023605 | -0.011978 | -0.0032642 | 0.0011044 | 0.0003182 | 5.9768e-05 | -0.0032471 | 63.8214 | 63.9175 | -0.013733 | -59.23 | 63.8489 | -59.0744 | -59.1064 | -59.0149 | 0.086975 | -59.3124 | 63.8855 | 63.8168 | -59.1156 | -59.2346 | -0.009155 | -0.041198 | -0.036621 | 122.9828 | -0.16479 | -0.1236 | -0.064087 | -0.050354 | -0.16937 | 0 | 0.050354 | -0.24719 | -0.07782 | -0.068665 | 122.9141 | 122.8867 | 59.0515 | -122.9919 | 122.9507 | 122.8821 | 59.1522 | -123.1201
464.5156 | 123.0743 | -59.079 | 63.8672 | -0.10223 | 0.0075451 | 0.068868 | 0.068364 | 0.13041 | -0.0019376 | -0.0015061 | -0.050125 | 0.0010082 | 0.0004636 | -0.0005362 | -0.00015383 | -0.0013245 | 63.7802 | 63.8901 | -0.032043 | -59.2529 | 63.826 | -59.0973 | -59.1431 | -59.0652 | 0.054932 | -59.3491 | 63.8672 | 63.826 | -59.1156 | -59.2163 | -0.018311 | -0.064087 | -0.041198 | 122.9691 | -0.17395 | -0.10986 | -0.086975 | -0.036622 | -0.13733 | 0 | 0.013732 | -0.27008 | -0.13275 | -0.041198 | 122.905 | 122.8592 | 59.0469 | -123.0103 | 122.9462 | 122.905 | 59.1339 | -123.0835
465.5156 | 123.1155 | -59.0698 | 63.8947 | -0.048828 | 0.01139 | 0.067372 | 0.0705 | 0.12785 | -1.505e-05 | -0.00022432 | 0.01091 | 0.00079463 | 0.0023862 | -0.0024588 | 0.0036914 | -0.0015381 | 63.826 | 63.9496 | -0.013733 | -59.2392 | 63.8397 | -59.0973 | -59.1156 | -59.0378 | 0.11902 | -59.4955 | 63.8168 | 63.7482 | -59.1476 | -59.2575 | -0.027466 | -0.045777 | -0.054931 | 123.0194 | -0.16937 | -0.1236 | -0.068664 | -0.07782 | -0.18768 | -0.07782 | 0.032043 | -0.42572 | -0.23804 | -0.14648 | 122.9095 | 122.8958 | 59.0561 | -123.0103 | 122.8867 | 122.818 | 59.1888 | -123.1522
466.5156 | 123.0606 | -59.0698 | 63.8992 | -0.17853 | 0.0066907 | 0.067586 | 0.068577 | 0.13255 | -0.0051418 | -0.0032151 | -0.042496 | -0.0013416 | -0.0012454 | -0.0016044 | 0.00070077 | -0.0026063 | 63.8901 | 63.7253 | -0.14191 | -59.2896 | 63.8443 | -59.1202 | -59.1248 | -59.0652 | 0.032043 | -59.3445 | 63.8809 | 63.8443 | -59.1202 | -59.2163 | -0.050354 | -0.054932 | -0.054932 | 122.7951 | -0.21973 | -0.1648 | -0.009155 | -0.050354 | -0.14649 | -0.018311 | 0.004577 | -0.27466 | -0.12817 | -0.054932 | 122.9141 | 122.9599 | 58.9279 | -123.024 | 122.9507 | 122.9141 | 59.1019 | -123.1155
467.5156 | 123.0743 | -59.0836 | 63.8489 | -0.033569 | 0.011604 | 0.066731 | 0.067296 | 0.13105 | 0.0038304 | 0.0019119 | 0.056686 | -0.002196 | 0.0028134 | -0.0003226 | 0.0032642 | -0.0034607 | 63.8077 | 63.945 | -0.054932 | -59.2667 | 63.8214 | -59.0744 | -59.1431 | -59.0607 | 0.004578 | -59.3491 | 63.8672 | 63.7894 | -59.1064 | -59.2484 | 0.009155 | -0.059509 | -0.027466 | 123.0286 | -0.18311 | -0.1236 | -0.041199 | -0.022888 | -0.16479 | 0.01831 | 0.022888 | -0.2655 | -0.10071 | -0.059509 | 122.905 | 122.8912 | 59.0286 | -122.9919 | 122.9507 | 122.8729 | 59.0881 | -123.0972
468.5156 | 123.1293 | -59.0698 | 63.8947 | -0.14801 | 0.0075451 | 0.06844 | 0.066227 | 0.13169 | 0.0019078 | -0.0012923 | -0.088272 | -0.00091437 | -0.001459 | -0.0005362 | 0.00091437 | -0.0015381 | 63.7894 | 63.9221 | -0.027466 | -59.2575 | 63.8489 | -59.0881 | -59.1064 | -59.0515 | 0.064087 | -59.3262 | 63.9038 | 63.8306 | -59.1385 | -59.2392 | -0.018311 | -0.036621 | -0.045776 | 122.9919 | -0.18768 | -0.15106 | -0.10528 | -0.068665 | -0.16937 | 0.009156 | 0.01831 | -0.25635 | -0.086975 | -0.064087 | 122.9187 | 122.8592 | 59.0424 | -123.0011 | 122.9736 | 122.9004 | 59.1339 | -123.1338
469.5156 | 123.1338 | -59.0927 | 63.8626 | -0.13275 | 0.0094677 | 0.064809 | 0.068577 | 0.12827 | 0.00019875 | -0.0019333 | -0.019608 | -0.002837 | 0.0021726 | -0.0003226 | 5.9768e-05 | -0.0021789 | 63.8123 | 63.945 | -0.013733 | -59.23 | 63.8306 | -59.1064 | -59.1202 | -59.0378 | 0.082397 | -59.3216 | 63.8535 | 63.7894 | -59.1248 | -59.2575 | -0.013733 | -0.027466 | -0.032044 | 123.0377 | -0.13733 | -0.10986 | -0.050354 | -0.032044 | -0.16479 | -0.009155 | 0.054931 | -0.22888 | -0.064087 | -0.073242 | 122.9233 | 122.905 | 59.079 | -122.9828 | 122.9462 | 122.8821 | 59.1751 | -123.1201
470.5156 | 123.1155 | -59.0561 | 63.9175 | -0.14801 | 0.0086133 | 0.066518 | 0.067936 | 0.12806 | -0.0019376 | -0.00065152 | -0.065384 | -0.002196 | 0.0006772 | 0.0007456 | -0.00036743 | -0.0026063 | 63.7711 | 63.9038 | -0.059509 | -59.2621 | 63.8535 | -59.0927 | -59.1248 | -59.0927 | 0.054932 | -59.3399 | 63.8763 | 63.8168 | -59.111 | -59.2209 | -0.036621 | -0.068665 | -0.064087 | 122.9599 | -0.20599 | -0.13733 | -0.14648 | -0.054932 | -0.16479 | -0.041199 | -0.036621 | -0.28381 | -0.11902 | -0.10071 | 122.9095 | 122.8271 | 58.9966 | -123.0423 | 122.9324 | 122.8729 | 59.111 | -123.1384
471.5156 | 123.1338 | -59.0424 | 63.8947 | -0.048828 | 0.012031 | 0.066945 | 0.070714 | 0.13148 | 0.0014804 | -0.0021469 | -0.0043486 | -0.00091437 | -0.0008182 | -0.0037406 | 0.0024096 | -0.0021789 | 63.8168 | 63.945 | -0.018311 | -59.2392 | 63.8443 | -59.0881 | -59.1064 | -59.0561 | 0.12817 | -59.3262 | 63.858 | 63.7939 | -59.1202 | -59.23 | -0.045777 | -0.064087 | -0.050354 | 122.9874 | -0.19684 | -0.13275 | -0.07782 | -0.07782 | -0.18768 | -0.036621 | -0.013733 | -0.28381 | -0.09613 | -0.10071 | 122.8867 | 122.8592 | 59.024 | -123.0011 | 122.9004 | 122.8363 | 59.1705 | -123.1247
472.5156 | 123.056 | -59.0744 | 63.9038 | -1.3077 | 0.0045545 | 0.068868 | 0.065373 | 0.13148 | 0.00019875 | -0.0012923 | -0.065384 | -0.0026234 | -0.0023136 | 0.0009592 | 0.00048697 | -0.0041017 | 63.7482 | 63.9038 | -0.032043 | -59.2758 | 63.8306 | -59.0973 | -59.1293 | -59.0744 | 0.054932 | -59.3445 | 63.8763 | 63.8306 | -59.0836 | -59.23 | -0.022888 | -0.054931 | -0.073243 | 122.9782 | -0.20142 | -0.14648 | -0.15564 | -0.009155 | -0.15564 | -0.027466 | 0 | -0.27008 | -0.11444 | -0.073243 | 122.905 | 122.8226 | 59.0424 | -123.0331 | 122.9507 | 122.905 | 59.1293 | -123.1339
473.5156 | 123.1476 | -59.0515 | 63.8718 | -0.14038 | 0.011177 | 0.066945 | 0.068577 | 0.13062 | -0.0023648 | 0.00041648 | -0.095902 | -0.0019824 | -0.0021 | -0.0005362 | 0.00091437 | -0.0019653 | 63.8123 | 63.9313 | -0.013733 | -59.2392 | 63.858 | -59.0881 | -59.1339 | -59.0424 | 0.09613 | -59.317 | 63.8535 | 63.8123 | -59.0927 | -59.2117 | -0.036621 | -0.082397 | -0.013733 | 122.9828 | -0.18768 | -0.10529 | -0.059509 | -0.041198 | -0.16022 | -0.01831 | 0.009156 | -0.2655 | -0.10529 | -0.059509 | 122.9095 | 122.8638 | 59.0378 | -123.0057 | 122.905 | 122.8638 | 59.1476 | -123.0835
474.5156 | 123.0698 | -59.0698 | 63.8809 | -0.23193 | 0.0066907 | 0.069295 | 0.068364 | 0.13084 | -0.0023648 | -0.0032151 | 0.0032804 | -0.005614 | 0.0004636 | -0.0009634 | -0.00058103 | -0.0041017 | 63.7619 | 63.9587 | 0.018311 | -59.2529 | 63.8351 | -59.079 | -59.1019 | -59.0607 | 0.068665 | -59.3216 | 63.8901 | 63.8443 | -59.1019 | -59.1797 | -0.009155 | -0.032044 | -0.045776 | 123.0286 | -0.18311 | -0.15106 | -0.11902 | -0.032044 | -0.10986 | 0.009156 | 0.009155 | -0.25177 | -0.14191 | -0.036621 | 122.905 | 122.8317 | 59.0881 | -122.9828 | 122.9599 | 122.9141 | 59.1385 | -123.0606
475.5156 | 122.9828 | -59.1019 | 63.8351 | -0.14038 | 0.010109 | 0.067586 | 0.069859 | 0.13319 | 0.00083955 | 0.0010575 | -0.073013 | 0.00015383 | -0.000391 | 0.0003182 | 0.0034778 | -0.0043153 | 63.826 | 63.9587 | 0 | -59.2438 | 63.8351 | -59.0836 | -59.1202 | -59.0424 | 0.086975 | -59.3262 | 63.8672 | 63.7848 | -59.1019 | -59.2712 | 0.018311 | -0.01831 | 0 | 123.0606 | -0.14191 | -0.1236 | -0.009155 | 0 | -0.16937 | 0.032043 | 0.05951 | -0.2243 | -0.054932 | -0.050354 | 122.937 | 122.9279 | 59.1019 | -122.9553 | 122.9691 | 122.8867 | 59.1888 | -123.1064
476.5156 | 123.1247 | -59.0424 | 63.8855 | -0.16327 | 0.0043409 | 0.066304 | 0.068364 | 0.13126 | -0.0049282 | -0.0030013 | 0.01091 | -0.0024096 | -0.0025272 | -0.002886 | 0.00091437 | -0.0028199 | 63.826 | 63.9954 | 0.041199 | -59.2072 | 63.8168 | -59.0744 | -59.0836 | -59.0149 | 0.1236 | -59.2987 | 63.8855 | 63.8214 | -59.1064 | -59.1843 | -0.032044 | -0.041199 | -0.068665 | 123.0377 | -0.16479 | -0.1236 | -0.059509 | -0.064087 | -0.14191 | 0 | 0.027465 | -0.25635 | -0.11444 | -0.064087 | 122.8592 | 122.8683 | 59.0836 | -122.9691 | 122.9279 | 122.8638 | 59.166 | -123.0698
477.5156 | 123.0652 | -59.0744 | 63.8855 | -0.11749 | 0.0079723 | 0.065877 | 0.070286 | 0.1287 | -0.0015102 | -0.0023605 | -0.11116 | -0.0036914 | 0.0028134 | -0.000109 | 0.00091437 | -0.0034607 | 63.7756 | 63.9175 | -0.036621 | -59.285 | 63.8489 | -59.0698 | -59.1156 | -59.079 | 0.050354 | -59.3491 | 63.8901 | 63.8031 | -59.0973 | -59.2163 | 0.004578 | -0.041199 | -0.036621 | 122.9919 | -0.21057 | -0.16937 | -0.10986 | -0.022888 | -0.14191 | 0.004578 | -0.004577 | -0.27466 | -0.13275 | -0.082397 | 122.9233 | 122.85 | 59.0378 | -123.0011 | 122.9645 | 122.8775 | 59.1248 | -123.1018
478.5156 | 123.0927 | -59.0424 | 63.8855 | -0.14801 | 0.0051953 | 0.068227 | 0.068364 | 0.12721 | -0.0023648 | -0.0038559 | -0.065384 | -0.0026234 | -0.0033816 | -0.0020316 | -0.0010082 | -0.0028199 | 63.826 | 63.9999 | 0.036621 | -59.2163 | 63.8123 | -59.0698 | -59.1019 | -59.0424 | 0.10529 | -59.3079 | 63.8855 | 63.8031 | -59.1248 | -59.23 | -0.027466 | -0.05951 | -0.073242 | 123.0423 | -0.17395 | -0.11444 | -0.059509 | -0.082398 | -0.18768 | 0 | 0 | -0.2655 | -0.077819 | -0.082397 | 122.8546 | 122.8683 | 59.079 | -122.9874 | 122.9279 | 122.8455 | 59.1476 | -123.1155
479.5156 | 123.0606 | -59.0698 | 63.9313 | -0.15564 | 0.0081861 | 0.066091 | 0.069432 | 0.13105 | -0.00065585 | -0.0019333 | -0.073013 | -0.0019824 | -0.0008182 | -0.0003226 | 0.00091437 | -0.0013245 | 63.7802 | 63.9221 | -0.036621 | -59.2575 | 63.8626 | -59.0973 | -59.1202 | -59.0652 | 0.050354 | -59.3445 | 63.8626 | 63.8306 | -59.111 | -59.23 | -0.027466 | -0.050354 | -0.068664 | 122.9919 | -0.18768 | -0.13733 | -0.15106 | -0.041199 | -0.16022 | -0.068664 | 0.004577 | -0.27466 | -0.11444 | -0.10071 | 122.9324 | 122.85 | 59.0332 | -123.0515 | 122.9324 | 122.9004 | 59.1202 | -123.1613
480.5156 | 123.175 | -59.0149 | 63.8535 | -0.17853 | 0.0036999 | 0.06844 | 0.066655 | 0.12913 | -0.002792 | -0.00086512 | -0.050125 | -0.004546 | -0.003168 | 0.0009592 | -0.0018628 | -0.0026063 | 63.8351 | 64.0457 | 0.086975 | -59.1934 | 63.826 | -59.0744 | -59.0744 | -59.0012 | 0.16937 | -59.2621 | 63.8489 | 63.7711 | -59.0836 | -59.1888 | -0.059509 | -0.059509 | -0.027466 | 123.0606 | -0.17853 | -0.11902 | -0.018311 | -0.068664 | -0.17395 | -0.004578 | 0.013733 | -0.24719 | -0.073242 | -0.082398 | 122.8409 | 122.85 | 59.1019 | -122.9279 | 122.8638 | 122.7859 | 59.1843 | -123.0423
481.5156 | 123.0927 | -59.0515 | 63.9038 | -0.17853 | 0.0098951 | 0.066091 | 0.0705 | 0.13041 | -0.0017238 | -0.0025741 | 0.18639 | -0.002837 | -0.0021 | -0.0013906 | 0.002837 | -0.0041017 | 63.7756 | 64.0274 | 0.1831 | -59.2255 | 63.9221 | -59.0698 | -59.1202 | -59.0881 | 0.068665 | -59.3216 | 63.8947 | 63.8077 | -59.1202 | -59.2255 | -0.01831 | -0.068664 | 0.01831 | 123.0789 | -0.17395 | -0.10529 | -0.12817 | -0.068664 | -0.17395 | -0.009156 | -0.036621 | -0.27008 | -0.09613 | -0.096131 | 122.9736 | 122.8271 | 59.2346 | -123.024 | 122.9462 | 122.8592 | 59.1202 | -123.1293
482.5156 | 123.1476 | -59.0515 | 63.8626 | -0.14801 | 0.0043409 | 0.068013 | 0.06815 | 0.12892 | -0.0049282 | -0.0019333 | -0.080643 | -0.0043324 | -0.0023136 | -0.000109 | -0.00015383 | -0.0023927 | 63.8351 | 64.0366 | 0.064087 | -59.1934 | 63.7985 | -59.0469 | -59.0973 | -58.9966 | 0.14191 | -59.2712 | 63.8443 | 63.7527 | -59.0836 | -59.2072 | 0.004578 | -0.045776 | -0.064087 | 123.0881 | -0.14191 | -0.09613 | -0.027466 | -0.032043 | -0.15564 | -0.018311 | 0.054932 | -0.21973 | -0.064087 | -0.10986 | 122.85 | 122.8867 | 59.1156 | -122.9599 | 122.8958 | 122.8043 | 59.1934 | -123.0698
483.5156 | 123.0698 | -59.079 | 63.8992 | -0.19379 | 0.0079723 | 0.068013 | 0.067296 | 0.13148 | 0.00083955 | -0.00043792 | -0.065384 | -0.001128 | 0.00025 | 0.000532 | 0.0013416 | -0.0030335 | 63.7894 | 63.8992 | -0.032043 | -59.2667 | 63.8443 | -59.1202 | -59.1248 | -59.0515 | 0.045776 | -59.3582 | 63.8901 | 63.8031 | -59.1156 | -59.23 | -0.041199 | -0.045777 | -0.054932 | 122.9782 | -0.18768 | -0.14191 | -0.10986 | -0.036622 | -0.15106 | -0.009155 | 0.027465 | -0.27924 | -0.12817 | -0.09613 | 122.9233 | 122.8683 | 59.0469 | -123.024 | 122.9691 | 122.8821 | 59.1248 | -123.1293
484.5156 | 123.2162 | -59.0378 | 63.8351 | -0.064087 | 0.0041271 | 0.068868 | 0.067296 | 0.13084 | -0.0049282 | -0.0032151 | 0.064316 | -0.0051868 | -0.0029544 | -0.0013906 | 0.00027337 | -0.0028199 | 63.8672 | 64.0594 | 0.073242 | -59.2026 | 63.8031 | -59.0469 | -59.1064 | -58.9371 | 0.17853 | -59.1522 | 63.8489 | 63.8077 | -59.024 | -59.1888 | -0.009155 | -0.068664 | -0.032043 | 123.0972 | -0.16479 | -0.096131 | 0.032043 | 0.013733 | -0.15106 | 0.013733 | 0.10071 | -0.11444 | 0.036621 | -0.027466 | 122.8409 | 122.905 | 59.111 | -122.9416 | 122.8867 | 122.8455 | 59.2163 | -123.024
485.5156 | 123.1018 | -59.0607 | 63.8947 | -0.14038 | 0.0062635 | 0.065663 | 0.067723 | 0.12827 | 0.00041235 | -0.0025741 | -0.23323 | -0.0024096 | -0.0010318 | -0.0005362 | -0.00015383 | -0.0055969 | 63.826 | 63.9999 | 0.018311 | -59.2346 | 63.826 | -59.0973 | -59.1202 | -59.0515 | 0.059509 | -59.3353 | 63.9175 | 63.7894 | -59.1019 | -59.2163 | -0.036621 | -0.059509 | -0.068664 | 123.0606 | -0.17395 | -0.11444 | -0.068664 | -0.041199 | -0.15564 | 0.022889 | 0.009155 | -0.27466 | -0.11902 | -0.10528 | 122.8867 | 122.8867 | 59.079 | -123.0148 | 122.9782 | 122.85 | 59.1202 | -123.111
486.5156 | 123.2071 | -59.0561 | 63.8489 | -0.10223 | 0.0058361 | 0.06844 | 0.066868 | 0.12806 | -0.0025784 | -0.0027877 | 0.033798 | -0.0019824 | -0.0027408 | -0.0020316 | -0.0048534 | -0.0043153 | 63.8763 | 64.0686 | 0.082397 | -59.1843 | 63.8077 | -59.0698 | -59.0881 | -58.7585 | -0.21973 | -59.3445 | 63.8214 | 63.7527 | -59.0973 | -59.2026 | -0.013733 | -0.032044 | -0.041199 | 123.1247 | -0.12817 | -0.09613 | 0.027466 | -0.041199 | -0.14648 | -0.027466 | 0.29755 | -0.28839 | -0.14191 | -0.09613 | 122.8638 | 122.9324 | 59.1385 | -122.937 | 122.8775 | 122.8088 | 58.8364 | -123.0515
487.5156 | 123.143 | -59.0469 | 63.8672 | -0.14801 | 0.0054089 | 0.066518 | 0.068577 | 0.13404 | -1.505e-05 | -0.0040695 | -0.11879 | -0.0041186 | -0.0027408 | -0.0020316 | -0.00015383 | -0.0055969 | 63.858 | 64.0411 | 0.073242 | -59.2117 | 63.8077 | -59.0561 | -59.0973 | -58.9966 | 0.16022 | -59.2712 | 63.8535 | 63.7802 | -59.0836 | -59.2117 | -0.009155 | -0.050354 | -0.059509 | 123.0881 | -0.16479 | -0.11444 | -0.009155 | -0.036621 | -0.16479 | -0.013732 | 0.050354 | -0.2243 | -0.059509 | -0.086975 | 122.8546 | 122.905 | 59.1202 | -122.9645 | 122.9004 | 122.8271 | 59.2072 | -123.0789
488.5156 | 123.23 | -59.0424 | 63.8489 | -0.010681 | 0.0026319 | 0.068013 | 0.067509 | 0.12721 | -0.0042874 | -0.0040695 | 0.071945 | -0.0024096 | -0.0006046 | -0.001177 | 0.00027337 | -0.0047425 | 63.8351 | 64.0228 | 0.036621 | -59.2117 | 63.8077 | -59.079 | -59.1019 | -58.9691 | 0.13275 | -59.2255 | 63.8306 | 63.739 | -59.0881 | -59.2026 | -0.036621 | -0.05951 | -0.041199 | 123.0652 | -0.16937 | -0.10986 | -0.013733 | -0.045777 | -0.16022 | -0.018311 | 0.073242 | -0.18311 | -0.022888 | -0.10986 | 122.85 | 122.8775 | 59.079 | -122.9507 | 122.8729 | 122.7814 | 59.1751 | -123.0515
489.5156 | 123.1247 | -59.0286 | 63.8672 | -0.18616 | 0.0039135 | 0.06844 | 0.067723 | 0.1334 | -0.00065585 | -0.0023605 | -0.12642 | -0.0041186 | -0.0008182 | -0.0026724 | 0.002196 | -0.0045289 | 63.8535 | 64.032 | 0.073242 | -59.2163 | 63.826 | -59.0881 | -59.0973 | -58.9966 | 0.13275 | -59.2712 | 63.8672 | 63.7756 | -59.1248 | -59.2163 | -0.05951 | -0.068665 | -0.041198 | 123.0606 | -0.18768 | -0.11902 | -0.013732 | -0.096131 | -0.18768 | 0 | 0.032043 | -0.24262 | -0.054931 | -0.091552 | 122.8546 | 122.8821 | 59.1019 | -122.9645 | 122.8958 | 122.8043 | 59.1614 | -123.0835
490.5156 | 123.1888 | -59.0515 | 63.8443 | 0.012207 | 0.0030591 | 0.068013 | 0.06815 | 0.1287 | -0.002792 | -0.0010787 | 0.13298 | -0.0026234 | -0.0025272 | -0.0003226 | 0.00048697 | -0.0023927 | 63.7985 | 63.9725 | -0.022888 | -59.2392 | 63.8123 | -59.0836 | -59.111 | -58.9828 | 0.082397 | -59.2712 | 63.826 | 63.7436 | -59.1019 | -59.2255 | -0.032043 | -0.059509 | -0.032043 | 123.024 | -0.18768 | -0.12817 | -0.045776 | -0.050354 | -0.17395 | -0.01831 | 0.068665 | -0.21973 | -0.045776 | -0.10071 | 122.8638 | 122.85 | 59.0286 | -122.9553 | 122.8775 | 122.7951 | 59.1339 | -123.0698
491.5156 | 123.1064 | -59.0424 | 63.8123 | -0.079346 | 0.0064771 | 0.068013 | 0.067509 | 0.13191 | -0.002792 | -0.0019333 | 0.033798 | -0.002196 | -0.0001774 | -0.001818 | 0.00091437 | -0.0045289 | 63.9084 | 64.0732 | 0.068665 | -59.1888 | 63.8123 | -59.0698 | -59.0881 | -58.9096 | 0.17853 | -59.198 | 63.826 | 63.7665 | -59.0698 | -59.166 | -0.027466 | -0.045777 | 0 | 123.1155 | -0.14648 | -0.10071 | 0.09613 | -0.027466 | -0.1236 | 0.013733 | 0.13275 | -0.15564 | -0.032043 | -0.045777 | 122.8546 | 122.9507 | 59.111 | -122.9004 | 122.8683 | 122.8088 | 59.2209 | -122.9782
492.5156 | 123.175 | -59.0424 | 63.8214 | 0.057983 | 0.0011365 | 0.067586 | 0.066655 | 0.12934 | -0.00044225 | -0.0027877 | 0.10246 | -0.0036914 | -0.0042362 | -0.002886 | 0.0034778 | -0.0030335 | 63.8168 | 63.9771 | -0.013733 | -59.2346 | 63.826 | -59.0973 | -59.111 | -58.9828 | 0.068665 | -59.2804 | 63.8351 | 63.7436 | -59.1248 | -59.2209 | -0.054932 | -0.068665 | 0.004578 | 123.0194 | -0.19226 | -0.1236 | -0.004578 | -0.082398 | -0.17853 | 0.013733 | 0.059509 | -0.23804 | -0.05951 | -0.07782 | 122.8683 | 122.8592 | 59.0286 | -122.9324 | 122.8775 | 122.7859 | 59.111 | -123.0423
493.5156 | 123.1796 | -59.0515 | 63.826 | -0.056458 | 0.0039135 | 0.066731 | 0.069218 | 0.12849 | -0.00086945 | -0.0019333 | -0.027237 | -0.0030506 | -0.0021 | -0.0022452 | 0.00091437 | -0.0045289 | 63.8855 | 64.0503 | 0.086975 | -59.2026 | 63.7711 | -59.0469 | -59.0927 | -58.8867 | 0.63171 | -59.3536 | 63.9084 | 63.7299 | -59.0561 | -59.2026 | 0.004578 | -0.041198 | -0.054932 | 123.1018 | -0.15106 | -0.10986 | 0.059509 | -0.004577 | -0.15106 | 0.082397 | 0.16479 | -0.30212 | -0.15106 | -0.096131 | 122.8226 | 122.937 | 59.1385 | -122.9187 | 122.9599 | 122.7814 | 59.6832 | -123.0286
494.5156 | 123.1338 | -59.0332 | 63.8351 | 0.080872 | 0.0041271 | 0.070363 | 0.06815 | 0.12721 | 0.00083955 | -0.0036423 | 0.33134 | -0.0034778 | -0.0027408 | -0.000109 | 0.001128 | -0.0036743 | 63.8214 | 63.9633 | -0.027466 | -59.111 | 63.8351 | -59.0332 | -59.1064 | -59.0103 | 0.022888 | -59.317 | 63.826 | 63.7115 | -59.1339 | -59.2117 | 0 | -0.073242 | 0 | 122.9965 | -0.07782 | -0.004578 | -0.013733 | -0.10071 | -0.17853 | -0.009155 | 0.022888 | -0.28381 | -0.10529 | -0.1236 | 122.8683 | 122.8546 | 59.0057 | -122.9416 | 122.8592 | 122.7448 | 59.0561 | -123.0469
495.5156 | 123.1796 | -59.0149 | 63.8535 | -0.094604 | 0.0054089 | 0.066304 | 0.069218 | 0.12892 | -1.505e-05 | -0.0010787 | -0.027237 | -0.0013416 | 0.001318 | -0.0039542 | 0.00048697 | -0.0017517 | 63.8947 | 64.0869 | 0.082397 | -59.1797 | 63.8351 | -59.0378 | -59.079 | -59.1064 | 0.16022 | -59.2072 | 63.858 | 63.707 | -59.0836 | -59.2117 | -0.022888 | -0.064086 | -0.018311 | 123.1018 | -0.16479 | -0.10071 | 0.041198 | -0.068664 | -0.19684 | 0.004577 | -0.091552 | -0.19226 | 0.004578 | -0.14648 | 122.85 | 122.9095 | 59.0973 | -122.9324 | 122.8729 | 122.7219 | 59.1751 | -123.0652
496.5156 | 123.143 | -59.0424 | 63.8626 | 0.065613 | 0.0060497 | 0.069509 | 0.067296 | 0.12934 | -0.00044225 | -0.0032151 | 0.31609 | -0.0041186 | -0.0008182 | -0.0007498 | 0.0019824 | -0.0019653 | 63.913 | 64.0915 | 0.09613 | -59.3536 | 63.7848 | -59.0652 | -59.1019 | -59.0057 | 0.013733 | -59.3124 | 63.826 | 63.739 | -59.1156 | -59.2392 | -0.022889 | -0.05951 | -0.07782 | 123.1338 | -0.31128 | -0.25177 | 0.050354 | -0.073243 | -0.19684 | -0.036621 | 0.036621 | -0.27008 | -0.073242 | -0.1236 | 122.8271 | 122.9553 | 59.1385 | -122.9645 | 122.8683 | 122.7814 | 59.0561 | -123.1018
497.5156 | 123.1842 | -59.0561 | 63.8397 | -0.0030518 | 0.0032727 | 0.06844 | 0.067296 | 0.13148 | -0.00086945 | -0.0030013 | 0.071945 | -0.003905 | -0.0006046 | -0.0009634 | 0.00070077 | -0.0023927 | 63.8626 | 64.0045 | 0.032043 | -59.2209 | 63.7848 | -59.0744 | -59.0927 | -58.9279 | 0.13275 | -59.2438 | 63.8351 | 63.739 | -59.079 | -59.2117 | -0.018311 | -0.036621 | -0.054932 | 123.0606 | -0.16479 | -0.12817 | 0.022888 | -0.022888 | -0.15564 | -0.004578 | 0.12817 | -0.18768 | -0.032043 | -0.10071 | 122.8409 | 122.9187 | 59.0881 | -122.9324 | 122.8912 | 122.7951 | 59.1888 | -123.0515
498.5156 | 123.1522 | -59.0652 | 63.8214 | 0.18768 | 0.0064771 | 0.067586 | 0.067936 | 0.13041 | 0.00019875 | -0.0010787 | 0.26268 | -0.0041186 | -0.0018862 | -0.000109 | -0.00036743 | -0.0032471 | 63.826 | 63.9725 | -0.022888 | -59.2575 | 63.7802 | -59.0836 | -59.0927 | -58.9874 | 0.013733 | -59.3124 | 63.8214 | 63.7253 | -59.1202 | -59.23 | -0.01831 | -0.027465 | -0.041199 | 123.0377 | -0.19226 | -0.16479 | 0.004578 | -0.054931 | -0.16479 | 0 | 0.07782 | -0.24719 | -0.082397 | -0.09613 | 122.8455 | 122.8912 | 59.0424 | -122.9141 | 122.8867 | 122.7905 | 59.079 | -123.0515
499.5312 | 123.0698 | -59.0836 | 63.8901 | -0.20905 | 0.0090405 | 0.06844 | 0.069645 | 0.1287 | 0.0048984 | -0.0010787 | -0.1722 | -0.0015552 | 0.0023862 | -0.0003226 | 0.0032642 | -0.0043153 | 63.826 | 63.9359 | -0.027466 | -59.2667 | 63.8443 | -59.1064 | -59.111 | -59.0286 | 0.073242 | -59.3582 | 63.8992 | 63.7848 | -59.0973 | -59.2209 | -0.022888 | -0.027466 | -0.045777 | 123.0194 | -0.18311 | -0.15564 | -0.064087 | -0.013733 | -0.13733 | 0.009155 | 0.054932 | -0.27466 | -0.13733 | -0.10529 | 122.9279 | 122.9095 | 59.0561 | -123.0011 | 122.9828 | 122.8683 | 59.1568 | -123.111
500.5156 | 123.1979 | -59.0515 | 63.8214 | 0.2182 | 0.0066907 | 0.066945 | 0.066655 | 0.13041 | -1.505e-05 | 0.00041648 | 0.26268 | -0.0019824 | 3.6404e-05 | -0.0024588 | 0.0015552 | -0.0017517 | 63.8535 | 64.0091 | -0.009155 | -59.2438 | 63.7573 | -59.0881 | -59.1293 | -58.9645 | 0.064087 | -59.2758 | 63.7802 | 63.6841 | -59.1019 | -59.2163 | -0.036621 | -0.077819 | -0.064087 | 123.0606 | -0.19226 | -0.11444 | 0.032044 | -0.050354 | -0.1648 | -0.041199 | 0.086975 | -0.2243 | -0.059509 | -0.13733 | 122.8088 | 122.905 | 59.0424 | -122.9507 | 122.8317 | 122.7356 | 59.1156 | -123.0377
501.5156 | 123.0881 | -59.0424 | 63.8168 | 0.15717 | 0.0047681 | 0.066304 | 0.066868 | 0.12849 | -0.0021512 | -0.0034287 | 0.19402 | -0.0026234 | -0.003168 | -0.0022452 | -0.0010082 | -4.2662e-05 | 63.8077 | 63.9542 | -0.050354 | -59.2804 | 63.7939 | -59.1019 | -59.1064 | -59.0012 | 0.036621 | -59.2987 | 63.8168 | 63.7253 | -59.1019 | -59.2072 | -0.05951 | -0.064087 | -0.022888 | 122.9965 | -0.23804 | -0.17395 | -0.009155 | -0.05951 | -0.16479 | 0 | 0.041198 | -0.25635 | -0.091553 | -0.091552 | 122.8363 | 122.85 | 58.992 | -122.9233 | 122.8592 | 122.7676 | 59.079 | -123.024
502.5156 | 123.1979 | -59.0607 | 63.8031 | 0.14191 | 0.0090405 | 0.068013 | 0.067936 | 0.13126 | 0.00041235 | -0.0015061 | 0.23979 | -0.0013416 | -0.0023136 | -0.0022452 | 0.0026234 | -0.0028199 | 63.8672 | 63.9816 | -0.022888 | -59.23 | 63.7985 | -59.0927 | -59.1293 | -58.9417 | 0.041199 | -59.2804 | 63.8306 | 63.6887 | -59.111 | -59.2117 | -0.032043 | -0.068664 | -0.004578 | 123.0423 | -0.16937 | -0.10071 | 0.064086 | -0.050354 | -0.15106 | 0.027465 | 0.11902 | -0.21973 | -0.068665 | -0.11444 | 122.8592 | 122.9279 | 59.0378 | -122.9324 | 122.8912 | 122.7493 | 59.1019 | -123.0148
503.5156 | 123.0927 | -59.0515 | 63.8397 | 0.14954 | 0.0066907 | 0.066731 | 0.067082 | 0.12998 | -0.0015102 | -0.00043792 | 0.2169 | -0.0026234 | -0.0018862 | -0.001177 | 0.00027337 | -0.0019653 | 63.826 | 63.9496 | -0.045776 | -59.2529 | 63.7985 | -59.0698 | -59.1248 | -58.9966 | 0.022888 | -59.3033 | 63.826 | 63.739 | -59.1202 | -59.2026 | -0.01831 | -0.073242 | -0.041199 | 123.0011 | -0.20142 | -0.12817 | -0.013733 | -0.068664 | -0.15106 | -0.013733 | 0.054932 | -0.25177 | -0.10071 | -0.10071 | 122.85 | 122.8775 | 59.0057 | -122.9645 | 122.8775 | 122.7905 | 59.0744 | -123.0423
504.5156 | 123.1384 | -59.0378 | 63.8672 | -0.17853 | 0.0069043 | 0.067586 | 0.066868 | 0.12934 | -0.001083 | -0.0015061 | -0.10353 | -0.002196 | -0.001459 | -0.0003226 | 0.0024096 | -0.0041017 | 63.8718 | 64.032 | 0.07782 | -59.1934 | 63.8168 | -59.0652 | -59.0927 | -58.9737 | 0.16022 | -59.2758 | 63.8672 | 63.7711 | -59.111 | -59.23 | -0.027466 | -0.054931 | -0.050354 | 123.0698 | -0.15564 | -0.10071 | 0.004578 | -0.073242 | -0.19226 | 0 | 0.064087 | -0.23804 | -0.045776 | -0.09613 | 122.8546 | 122.9095 | 59.1156 | -122.9599 | 122.905 | 122.8088 | 59.198 | -123.0972
505.5156 | 123.1613 | -59.0515 | 63.8214 | 0.18005 | 0.0058361 | 0.069081 | 0.066655 | 0.1302 | 0.00019875 | -1.0724e-05 | 0.2932 | -0.0030506 | -0.004877 | -0.001818 | 0.0015552 | -0.0032471 | 63.8626 | 63.9954 | -0.022888 | -59.2484 | 63.739 | -59.0881 | -59.1064 | -58.9874 | 0.036621 | -59.2941 | 63.7985 | 63.7161 | -59.1064 | -59.2255 | -0.036621 | -0.054931 | -0.082397 | 123.0469 | -0.19684 | -0.14191 | 0.041199 | -0.054931 | -0.17395 | -0.022888 | 0.064087 | -0.24261 | -0.068664 | -0.10529 | 122.7905 | 122.9141 | 59.0286 | -122.9279 | 122.85 | 122.7676 | 59.0881 | -123.0469
506.5156 | 123.1979 | -59.0652 | 63.8077 | 0.2182 | 0.0098951 | 0.067372 | 0.067723 | 0.1287 | 0.0021214 | -0.00043792 | 0.19402 | -0.0015552 | 0.001959 | -0.001177 | 0.0019824 | -0.0034607 | 63.8168 | 63.9038 | -0.10071 | -59.2758 | 63.7894 | -59.111 | -59.1248 | -58.9737 | 0.004578 | -59.2987 | 63.8031 | 63.7299 | -59.1339 | -59.2392 | -0.045776 | -0.059509 | -0.01831 | 122.9691 | -0.21057 | -0.15106 | 0.009155 | -0.068664 | -0.17395 | -0.004577 | 0.091553 | -0.23346 | -0.059509 | -0.07782 | 122.8546 | 122.8821 | 58.9645 | -122.9324 | 122.8683 | 122.7951 | 59.0698 | -123.0469
507.5156 | 123.1888 | -59.0607 | 63.8306 | 0.18768 | 0.0071179 | 0.066945 | 0.067723 | 0.13126 | 0.0014804 | -0.0019333 | 0.2169 | -0.0036914 | -0.0023136 | -0.0022452 | 0.0034778 | -0.0043153 | 63.8718 | 63.9771 | -0.013733 | -59.2346 | 63.7665 | -59.0927 | -59.1019 | -58.96 | 0.050354 | -59.2941 | 63.8031 | 63.7024 | -59.111 | -59.2117 | -0.032043 | -0.041199 | -0.064087 | 123.0377 | -0.17395 | -0.13275 | 0.041199 | -0.050354 | -0.15106 | -0.027465 | 0.10071 | -0.23346 | -0.082397 | -0.12817 | 122.8271 | 122.9324 | 59.0469 | -122.9324 | 122.8638 | 122.7631 | 59.111 | -123.0423
508.5156 | 123.0927 | -59.0836 | 63.8306 | 0.19531 | 0.011818 | 0.067372 | 0.067296 | 0.1302 | 0.0027622 | -0.00065152 | 0.23216 | -0.0015552 | 0.0006772 | 0.0007456 | 0.0019824 | -0.0043153 | 63.7894 | 63.858 | -0.13733 | -59.2987 | 63.826 | -59.1202 | -59.1293 | -59.0286 | -0.059509 | -59.3582 | 63.8397 | 63.739 | -59.1431 | -59.2346 | -0.036621 | -0.045776 | -0.004577 | 122.9416 | -0.21515 | -0.16937 | -0.041198 | -0.059509 | -0.15106 | 0.009156 | 0.054932 | -0.27466 | -0.1236 | -0.091552 | 122.9095 | 122.8729 | 58.9462 | -122.9599 | 122.9233 | 122.8226 | 59.024 | -123.0652
509.5156 | 123.3902 | -59.0012 | 63.8992 | -0.056458 | 0.0041271 | 0.0034991 | 0.066868 | 0.1302 | -0.0032192 | -0.0010787 | 0.10246 | -0.0036914 | -0.001459 | -0.0016044 | 0.00027337 | -0.0023927 | 63.8763 | 64.0411 | 0.068665 | -59.198 | 63.7939 | -59.0927 | -59.0744 | -58.9096 | 0.19684 | -59.2072 | 63.8123 | 63.7711 | -59.0744 | -59.2026 | -0.091552 | -0.073242 | -0.10529 | 123.0423 | -0.19684 | -0.1236 | -0.022888 | -0.073242 | -0.20142 | -0.086975 | 0.091553 | -0.20599 | -0.004577 | -0.12817 | 122.7951 | 122.8775 | 59.0698 | -122.9736 | 122.8134 | 122.7722 | 59.198 | -123.1018
510.5156 | 123.0927 | -59.1202 | 63.8718 | 0.33264 | 0.012245 | 0.066091 | 0.069005 | 0.13126 | 0.0031894 | -0.0019333 | 0.17876 | -0.002196 | 0.0011044 | -0.0003226 | 0.002837 | -0.0047425 | 63.7985 | 63.8306 | -0.13733 | -59.3216 | 63.826 | -59.111 | -59.166 | -59.0698 | -0.068665 | -59.4086 | 63.8672 | 63.739 | -59.1385 | -59.2392 | 0.009155 | -0.045777 | -0.045776 | 122.9507 | -0.20142 | -0.15564 | -0.073242 | -0.018311 | -0.11902 | -0.004578 | 0.050354 | -0.28839 | -0.16937 | -0.13275 | 122.9462 | 122.9187 | 58.9828 | -123.0377 | 122.9874 | 122.8592 | 59.0515 | -123.111
511.5156 | 123.1842 | -59.0744 | 63.8123 | 0.37079 | 0.0094677 | 0.066304 | 0.066441 | 0.12956 | 0.00083955 | -0.0010787 | 0.26268 | -0.0030506 | -0.0010318 | -0.0007498 | 0.0032642 | -0.0036743 | 63.8489 | 63.9954 | -0.013733 | -59.2484 | 63.7939 | -59.079 | -59.1019 | -58.9783 | 0.059509 | -59.2667 | 63.7939 | 63.707 | -59.1293 | -59.23 | -0.004577 | -0.027466 | -0.018311 | 123.0698 | -0.17395 | -0.14648 | 0.036621 | -0.054931 | -0.15564 | -0.018311 | 0.096131 | -0.19226 | -0.036621 | -0.10529 | 122.8683 | 122.9233 | 59.0607 | -122.9141 | 122.8683 | 122.7814 | 59.1339 | -123.0423
512.5156 | 123.1201 | -59.0973 | 63.8168 | 0.18768 | 0.012031 | 0.065663 | 0.069005 | 0.12977 | 0.0014804 | -0.0010787 | 0.24742 | -0.00070077 | 0.0006772 | 0.0011728 | 0.0024096 | -0.0030335 | 63.7939 | 63.8535 | -0.12817 | -59.3079 | 63.8123 | -59.111 | -59.1568 | -59.0561 | -0.059509 | -59.3582 | 63.8626 | 63.7619 | -59.1522 | -59.2392 | -0.013733 | -0.059509 | -0.004577 | 122.9507 | -0.21057 | -0.15106 | -0.022888 | -0.054932 | -0.14191 | 0.045777 | 0.041199 | -0.26093 | -0.11902 | -0.054931 | 122.9095 | 122.8912 | 58.9691 | -122.9736 | 122.9599 | 122.8592 | 59.0378 | -123.056
513.5156 | 123.1979 | -59.0515 | 63.7939 | 0.19531 | 0.0075451 | 0.066304 | 0.067082 | 0.1302 | 0.00083955 | -0.00022432 | 0.23216 | -0.002196 | -0.001459 | -0.0020316 | 0.0032642 | -0.0062379 | 63.739 | 64.1922 | 0.10071 | -59.2026 | 63.7802 | -59.079 | -59.079 | -58.9691 | 0.059509 | -59.2667 | 63.7985 | 63.7253 | -59.1156 | -59.2255 | -0.027465 | -0.027465 | -0.013733 | 123.2437 | -0.15106 | -0.1236 | -0.054931 | -0.064087 | -0.17395 | 0.004578 | 0.082398 | -0.21515 | -0.041199 | -0.068664 | 122.8317 | 122.7905 | 59.1522 | -122.8729 | 122.85 | 122.7768 | 59.111 | -123.0194
514.5156 | 123.23 | -59.0012 | 63.8351 | -0.048828 | 0.0090405 | 0.0678 | 0.066655 | 0.12913 | -0.0042874 | -0.0027877 | 0.087204 | -0.0047596 | 3.6404e-05 | -0.0022452 | 0.00070077 | -0.0021789 | 63.8809 | 64.0274 | 0.068665 | -59.2117 | 63.7939 | -59.0515 | -59.1156 | -58.9371 | 0.16022 | -59.2117 | 63.826 | 63.7573 | -59.0698 | -59.1934 | -0.050354 | -0.11444 | -0.041199 | 123.0286 | -0.21057 | -0.09613 | 0.045776 | -0.068664 | -0.19226 | -0.009155 | 0.064087 | -0.21057 | -0.018311 | -0.07782 | 122.7951 | 122.8821 | 59.0698 | -122.9507 | 122.8271 | 122.7585 | 59.1614 | -123.0286
515.5156 | 123.2162 | -59.0515 | 63.7939 | 0.26398 | 0.010963 | 0.067159 | 0.066655 | 0.13041 | 0.0025486 | 0.0016983 | 0.26268 | -0.0017688 | -0.0008182 | -0.0030996 | 0.0013416 | -0.0019653 | 63.8535 | 63.9816 | -0.032043 | -59.2255 | 63.7527 | -59.0881 | -59.1248 | -58.9142 | -0.004578 | -59.2484 | 63.7894 | 63.707 | -59.1156 | -59.2209 | -0.036621 | -0.073242 | -0.041198 | 123.0331 | -0.17395 | -0.10071 | 0.05951 | -0.064087 | -0.16937 | -0.004577 | 0.13733 | -0.19684 | -0.027466 | -0.086975 | 122.8043 | 122.905 | 59.0195 | -122.9187 | 122.8409 | 122.7585 | 59.0469 | -123.0148
516.5156 | 123.1201 | -59.079 | 63.8123 | 0.20294 | 0.0083997 | 0.063741 | 0.066868 | 0.12956 | 0.0021214 | -0.0012923 | 0.2169 | -0.002837 | -0.0027408 | -0.0033134 | 0.003905 | -0.0023927 | 63.7985 | 63.8626 | -0.12817 | -59.3033 | 63.8031 | -59.1019 | -59.1614 | -59.0332 | -0.041199 | -59.3536 | 63.8123 | 63.7573 | -59.1202 | -59.2758 | -0.022889 | -0.082398 | -0.009155 | 122.9416 | -0.22431 | -0.14191 | -0.013733 | -0.041199 | -0.19684 | 0 | 0.045776 | -0.27466 | -0.07782 | -0.054932 | 122.8821 | 122.8775 | 58.9508 | -122.9736 | 122.8912 | 122.8363 | 59.0378 | -123.0881
517.5156 | 123.1888 | -59.079 | 63.7985 | -0.14801 | 0.0069043 | 0.06545 | 0.067082 | 0.1302 | 0.00041235 | 0.00084388 | 0.20164 | -0.0019824 | -0.0021 | 0.0003182 | 0.0017688 | -0.0049561 | 63.8351 | 63.9862 | -0.013733 | -59.2255 | 63.7573 | -59.0698 | -59.1064 | -58.9691 | 0.050354 | -59.2804 | 63.7985 | 63.7299 | -59.1156 | -59.23 | 0.009155 | -0.027466 | -0.041199 | 123.0652 | -0.14649 | -0.11902 | 0.036621 | -0.036622 | -0.15106 | 0 | 0.10986 | -0.20142 | -0.050354 | -0.068665 | 122.8363 | 122.9141 | 59.0652 | -122.905 | 122.8775 | 122.8088 | 59.1293 | -123.0286
518.5156 | 123.0423 | -59.111 | 63.8535 | 0.10376 | 0.01374 | 0.065663 | 0.068791 | 0.12977 | 0.004044 | 0.0016983 | -0.21034 | -0.002837 | 0.0032406 | -0.0005362 | 0.0043324 | -0.0011109 | 63.7665 | 63.3865 | -0.40283 | -59.317 | 63.7802 | -59.1293 | -59.1156 | -59.0927 | -0.07782 | -59.4131 | 63.8763 | 63.7848 | -59.1476 | -59.2575 | -0.01831 | -0.004578 | -0.073243 | 122.4976 | -0.20599 | -0.20142 | -0.086976 | -0.036621 | -0.14648 | 0.022888 | 0.018311 | -0.30212 | -0.15564 | -0.068665 | 122.8912 | 122.8775 | 58.7082 | -122.9691 | 122.9874 | 122.8958 | 59.0332 | -123.111
519.5156 | 123.2025 | -59.0652 | 63.7802 | 0.2182 | 0.0090405 | 0.065236 | 0.067296 | 0.12956 | 0.00083955 | 0.0010575 | 0.20164 | -0.0024096 | -0.0018862 | -0.0013906 | 0.002196 | -0.0030335 | 63.9587 | 63.6566 | -0.1236 | -59.166 | 63.739 | -59.1293 | -59.1202 | -58.9783 | 0.045776 | -59.2712 | 63.7985 | 63.7527 | -59.1202 | -59.23 | -0.064086 | -0.054931 | -0.041198 | 122.7219 | -0.10071 | -0.045777 | 0.17853 | -0.054931 | -0.16479 | 0.018311 | 0.086976 | -0.20599 | -0.041198 | -0.027465 | 122.8043 | 123.024 | 58.9417 | -122.9004 | 122.8638 | 122.818 | 59.111 | -123.0103
520.5156 | 123.056 | -59.111 | 63.8489 | 0.13428 | 0.012031 | 0.068654 | 0.070073 | 0.12977 | -0.00044225 | 0.00020288 | 0.20164 | -0.0026234 | -0.0001774 | 0.000532 | 0.0015552 | -0.0032471 | 63.7665 | 63.8535 | -0.11444 | -59.3079 | 63.8168 | -59.0881 | -59.1476 | -59.0744 | -0.050354 | -59.3994 | 63.8489 | 63.7573 | -59.1293 | -59.2575 | 0.022888 | -0.036621 | -0.032044 | 122.9645 | -0.19684 | -0.16022 | -0.082398 | -0.01831 | -0.14648 | 0 | 0.036621 | -0.28839 | -0.14191 | -0.091553 | 122.9279 | 122.8775 | 58.9966 | -122.9965 | 122.9599 | 122.8683 | 59.0607 | -123.1064
521.5156 | 123.2025 | -59.0378 | 63.8077 | 0.21057 | 0.0098951 | 0.069509 | 0.06815 | 0.12956 | -0.0019376 | -0.00022432 | 0.23979 | -0.0017688 | -0.0023136 | -0.0005362 | 0.004546 | -0.0051697 | 63.8626 | 63.9633 | -0.036621 | -59.2392 | 63.7573 | -59.0927 | -59.1202 | -58.9325 | -0.27008 | -59.3124 | 63.7756 | 63.7115 | -59.1248 | -59.2163 | -0.054931 | -0.082397 | -0.050354 | 123.0011 | -0.20142 | -0.11902 | 0.054932 | -0.086975 | -0.17853 | -0.032043 | 0.10529 | -0.27466 | -0.09613 | -0.09613 | 122.7951 | 122.9004 | 59.0012 | -122.9279 | 122.8134 | 122.7493 | 58.7677 | -123.024
522.5156 | 123.0606 | -59.1019 | 63.8397 | 0.18005 | 0.0079723 | 0.0631 | 0.071354 | 0.12892 | 0.0014804 | -0.00022432 | 0.18639 | 0.0016492 | -0.0001774 | -0.0005362 | 0.0036914 | -0.0060243 | 63.6612 | 63.945 | -0.073242 | -59.3079 | 63.826 | -59.111 | -59.1476 | -59.0881 | -0.068665 | -59.3948 | 63.858 | 63.7802 | -59.1385 | -59.2758 | -0.009155 | -0.045776 | -0.013733 | 123.0469 | -0.20599 | -0.16022 | -0.17853 | -0.036621 | -0.17395 | 0.01831 | 0.013733 | -0.29297 | -0.11902 | -0.05951 | 122.9279 | 122.7631 | 59.0286 | -122.9874 | 122.9599 | 122.8821 | 59.0332 | -123.1155
523.5156 | 123.175 | -59.0469 | 63.8306 | 0.21057 | 0.0088269 | 0.066945 | 0.062809 | 0.12806 | -0.0049282 | -0.0017197 | 0.44579 | -0.0041186 | -0.0021 | -0.0005362 | -0.00079463 | -0.0032471 | 63.9587 | 63.9175 | -0.022888 | -59.2026 | 63.7665 | -59.0836 | -59.1156 | -58.9828 | 0.041199 | -59.2621 | 63.7894 | 63.7344 | -59.1156 | -59.2209 | -0.036621 | -0.068665 | -0.064087 | 122.9645 | -0.15564 | -0.086975 | 0.12817 | -0.068665 | -0.17395 | -0.041198 | 0.064087 | -0.21515 | -0.041199 | -0.09613 | 122.8134 | 123.0057 | 59.024 | -122.9462 | 122.8363 | 122.7814 | 59.0881 | -123.0515
524.5156 | 123.0927 | -59.0881 | 63.8626 | 0.019836 | 0.011604 | 0.066091 | 0.070714 | 0.13105 | 0.002335 | -0.0030013 | 0.13298 | -0.0015552 | 0.001318 | 0.0001046 | 0.002196 | 0.0010253 | 63.7711 | 63.8351 | -0.1236 | -59.3079 | 63.8351 | -59.1019 | -59.1476 | -59.2484 | -0.39825 | -59.1751 | 63.826 | 63.8031 | -59.1202 | -59.2575 | -0.013733 | -0.059509 | -0.027466 | 122.9233 | -0.21973 | -0.16022 | -0.091553 | -0.032043 | -0.16937 | -0.036621 | -0.16022 | -0.086975 | 0.082397 | -0.059509 | 122.9233 | 122.8592 | 58.9645 | -123.0103 | 122.9141 | 122.8912 | 58.6899 | -123.1201
525.5156 | 123.1934 | -59.0378 | 63.7985 | 0.25635 | 0.0066907 | 0.066518 | 0.0658 | 0.12998 | -0.00086945 | 0.00063028 | 0.23979 | -0.003905 | -0.0050906 | 0.0001046 | 0.0034778 | -0.0032471 | 63.8351 | 63.9587 | -0.036621 | -59.2392 | 63.7756 | -59.0927 | -59.1248 | -58.9874 | 0.050354 | -59.3216 | 63.7756 | 63.7024 | -59.1614 | -59.2575 | -0.054931 | -0.086975 | -0.022888 | 122.9965 | -0.20142 | -0.11444 | 0.036621 | -0.1236 | -0.21973 | -0.022888 | 0.050354 | -0.28381 | -0.064087 | -0.09613 | 122.8134 | 122.8729 | 59.0012 | -122.9233 | 122.8134 | 122.7402 | 59.0881 | -123.056
526.5156 | 123.0606 | -59.1019 | 63.8672 | 0.15717 | 0.012031 | 0.067372 | 0.068577 | 0.12827 | 0.0025486 | 0.0014847 | 0.52971 | -0.002196 | 3.6404e-05 | -0.0009634 | 0.003905 | -0.0036743 | 63.3499 | 63.8123 | 0.004578 | -59.1339 | 63.8077 | -59.111 | -59.1431 | -59.0881 | -0.068665 | -59.3948 | 63.8535 | 63.7985 | -59.1248 | -59.2758 | -0.009155 | -0.041198 | -0.059509 | 122.9141 | -0.032043 | 0.009155 | -0.51727 | -0.022888 | -0.17395 | -0.013732 | 0.013733 | -0.29297 | -0.11902 | -0.068664 | 122.9095 | 122.4518 | 59.1064 | -123.0103 | 122.9553 | 122.9004 | 59.0332 | -123.143
527.5156 | 123.1979 | -59.1064 | 63.8168 | 0.2182 | 0.01075 | 0.067159 | 0.067509 | 0.1287 | -0.00065585 | -0.0019333 | 0.2932 | -0.00070077 | -0.0025272 | -0.001177 | 0.002837 | -0.0043153 | 63.7985 | 63.8809 | -0.10529 | -59.2896 | 63.7848 | -59.1064 | -59.1248 | -59.024 | -0.009155 | -59.3079 | 63.8077 | 63.7482 | -59.1431 | -59.2438 | 0 | -0.018311 | -0.032043 | 122.9874 | -0.18311 | -0.1648 | -0.01831 | -0.036621 | -0.13733 | -0.009155 | 0.082397 | -0.20142 | -0.064087 | -0.068664 | 122.8912 | 122.905 | 59.0012 | -122.9416 | 122.9141 | 122.8546 | 59.0973 | -123.0606
528.5156 | 123.0423 | -59.0927 | 63.8489 | 0.10376 | 0.010109 | 0.0678 | 0.067723 | 0.13233 | 0.0012668 | -1.0724e-05 | 0.11009 | -0.00070077 | 3.6404e-05 | -0.0009634 | 0.0024096 | -0.0026063 | 63.7756 | 63.8397 | -0.10071 | -59.2896 | 63.826 | -59.0973 | -59.1614 | -59.0973 | -0.054932 | -59.4131 | 63.8809 | 63.7985 | -59.1476 | -59.2667 | -0.004578 | -0.068665 | -0.022888 | 122.9324 | -0.19684 | -0.12817 | -0.073242 | -0.054932 | -0.17395 | 0.032043 | -0.004578 | -0.32044 | -0.14648 | -0.050354 | 122.9187 | 122.8683 | 58.992 | -123.0103 | 122.9736 | 122.8912 | 59.0378 | -123.1155
529.5156 | 123.1018 | -59.111 | 63.8397 | 0.18768 | 0.012886 | 0.065663 | 0.068577 | 0.1287 | 0.0010532 | 0.0010575 | 0.25505 | -0.0024096 | 0.0006772 | -0.0005362 | 0.0026234 | -0.0023927 | 63.7711 | 63.8489 | -0.12817 | -59.3079 | 63.7894 | -59.1156 | -59.1522 | -59.0515 | -0.064087 | -59.3536 | 63.8718 | 63.7894 | -59.1339 | -59.2392 | -0.004578 | -0.041199 | -0.050354 | 122.9599 | -0.19684 | -0.15564 | -0.068665 | -0.022888 | -0.12817 | 0.032043 | 0.059509 | -0.24261 | -0.11444 | -0.050354 | 122.9004 | 122.8821 | 58.9828 | -122.9919 | 122.9828 | 122.9004 | 59.0469 | -123.0789
530.5156 | 123.0789 | -59.0973 | 63.8809 | 0.050354 | 0.01374 | 0.064595 | 0.067296 | 0.13276 | 0.0014804 | 0.00020288 | 0.15587 | -0.0026234 | -0.0001774 | -0.0005362 | 0.002196 | -0.0030335 | 63.7482 | 63.8123 | -0.12817 | -59.3033 | 63.8397 | -59.1019 | -59.1614 | -59.0652 | -0.63171 | -59.4315 | 63.7848 | 63.7619 | -59.166 | -59.2255 | -0.004578 | -0.064087 | -0.041198 | 122.9095 | -0.20599 | -0.14191 | -0.13275 | -0.068665 | -0.12817 | -0.09613 | 0.032043 | -0.33417 | -0.20599 | -0.11902 | 122.937 | 122.8455 | 58.9691 | -123.0423 | 122.8821 | 122.8592 | 58.4656 | -123.1064
531.5156 | 123.1018 | -59.1019 | 63.8443 | 0.019836 | 0.0092541 | 0.064382 | 0.066227 | 0.13084 | 0.00019875 | -0.0030013 | 0.20927 | -0.0017688 | 3.6404e-05 | 0.0001046 | 0.00070077 | -0.0038879 | 63.7939 | 63.8306 | -0.10986 | -59.2941 | 63.8535 | -59.1156 | -59.1522 | -59.079 | -0.059509 | -59.3811 | 63.8535 | 63.7848 | -59.1476 | -59.2712 | -0.013733 | -0.050354 | 0.009156 | 122.9324 | -0.19226 | -0.14191 | -0.050354 | -0.045776 | -0.16937 | 0.009156 | 0.022889 | -0.27924 | -0.10986 | -0.059509 | 122.9553 | 122.8958 | 58.992 | -122.9965 | 122.9553 | 122.8867 | 59.0424 | -123.1155
532.5156 | 123.0652 | -59.0744 | 63.8489 | -0.056458 | 0.0094677 | 0.065877 | 0.067509 | 0.12998 | 0.001694 | -0.0017197 | 0.0032804 | -0.001128 | -0.001459 | -0.001177 | 0.002837 | -0.0028199 | 63.8443 | 63.9221 | -0.022888 | -59.2392 | 63.8123 | -59.0744 | -59.1156 | -59.0332 | 0.027466 | -59.3399 | 63.8626 | 63.7894 | -59.1202 | -59.2392 | 0 | -0.041199 | -0.036621 | 122.9965 | -0.16479 | -0.1236 | -0.004578 | -0.045776 | -0.16479 | 0.013733 | 0.041199 | -0.2655 | -0.10071 | -0.059509 | 122.8867 | 122.9187 | 59.0515 | -122.9645 | 122.937 | 122.8638 | 59.1019 | -123.0881
533.5156 | 123.0652 | -59.1156 | 63.8489 | 0.09613 | 0.011177 | 0.067372 | 0.066868 | 0.13447 | 0.00019875 | -0.00065152 | 0.23979 | -0.002837 | 0.001318 | 0.000532 | 0.00091437 | -0.0013245 | 63.7527 | 63.8351 | -0.14191 | -59.2941 | 63.7985 | -59.111 | -59.1431 | -59.0927 | -0.064087 | -59.3765 | 63.8535 | 63.7848 | -59.1431 | -59.2529 | 0.004578 | -0.027465 | -0.050354 | 122.9507 | -0.17853 | -0.15106 | -0.09613 | -0.027465 | -0.13733 | 0.004578 | 0.022889 | -0.26093 | -0.1236 | -0.064087 | 122.9141 | 122.8683 | 58.9737 | -122.9919 | 122.9691 | 122.9004 | 59.0515 | -123.1018
534.5156 | 123.1155 | -59.079 | 63.8718 | 0.027466 | 0.010322 | 0.064382 | 0.068577 | 0.13148 | 0.001694 | 0.00020288 | 0.079574 | -0.0026234 | -0.0006046 | 0.0003182 | 0.0026234 | -0.0028199 | 63.8351 | 63.913 | -0.050354 | -59.2621 | 63.8168 | -59.0607 | -59.1431 | -59.0515 | 0.018311 | -59.3445 | 63.8718 | 63.7939 | -59.1385 | -59.2209 | 0.01831 | -0.064087 | -0.054932 | 122.9919 | -0.18311 | -0.11902 | -0.036621 | -0.05951 | -0.14191 | 0 | 0.027465 | -0.2655 | -0.1236 | -0.07782 | 122.8958 | 122.9141 | 59.0286 | -123.0148 | 122.9507 | 122.8729 | 59.0973 | -123.0927
535.5156 | 123.0331 | -59.1019 | 63.8306 | 0.073242 | 0.012245 | 0.066945 | 0.069645 | 0.12913 | -1.505e-05 | -0.0032151 | 2.8719 | -0.00091437 | -0.0012454 | -0.001177 | 0.0017688 | -0.0034607 | 63.7436 | 63.8031 | -0.13275 | -59.3079 | 63.8168 | -59.111 | -59.1385 | -59.1064 | 0.045776 | -59.404 | 63.8672 | 63.8031 | -59.1431 | -59.2346 | -0.009155 | -0.036621 | -0.013733 | 122.905 | -0.20599 | -0.16937 | -0.086975 | -0.041198 | -0.13275 | 0.036621 | -0.004577 | -0.30212 | -0.16937 | -0.027465 | 122.9187 | 122.8455 | 58.9691 | -122.9691 | 122.9691 | 122.905 | 59.1476 | -123.0652
536.5156 | 123.1201 | -59.0698 | 63.8672 | 0.42419 | 0.011177 | 0.067159 | 0.067936 | 0.12998 | 0.0019078 | -0.00043792 | 0.018539 | -0.0013416 | -0.0016726 | -0.0016044 | 0.002196 | -0.0032471 | 63.8397 | 63.9496 | 0.009155 | -59.2438 | 63.8443 | -59.0698 | -59.1476 | -59.0378 | 0.050354 | -59.3124 | 63.8672 | 63.8123 | -59.1339 | -59.2529 | 0 | -0.07782 | -0.022888 | 123.0194 | -0.17395 | -0.09613 | -0.027465 | -0.064087 | -0.18311 | 0 | 0.032043 | -0.24262 | -0.059509 | -0.054931 | 122.9141 | 122.9095 | 59.079 | -123.0148 | 122.937 | 122.8821 | 59.1202 | -123.1201
537.5156 | 123.0743 | -59.1202 | 63.858 | 2.8046 | 0.014381 | 0.066731 | 0.076695 | 0.12763 | 0.0010532 | -0.0021469 | 0.14824 | -0.0017688 | -0.0001774 | -0.001177 | 0.0026234 | -0.00047006 | 63.7711 | 63.8763 | -0.11444 | -59.3124 | 63.8351 | -59.111 | -59.1522 | -59.0973 | -0.059509 | -59.3857 | 63.858 | 63.7848 | -59.1568 | -59.2712 | 0.009155 | -0.032044 | -0.022888 | 122.9965 | -0.19226 | -0.16022 | -0.086975 | -0.036621 | -0.15106 | 0 | 0.022888 | -0.2655 | -0.11444 | -0.073242 | 122.9553 | 122.8912 | 59.0057 | -123.0103 | 122.9782 | 122.905 | 59.0607 | -123.1293
538.5156 | 123.1338 | -59.0744 | 63.8992 | -0.14801 | 0.012245 | 0.0678 | 0.071568 | 0.13212 | 0.0021214 | -0.0027877 | 0.018539 | -0.001128 | -0.0010318 | 0.0001046 | 0.0036914 | -0.0034607 | 63.8397 | 63.9404 | -0.013733 | -59.2438 | 63.8397 | -59.0836 | -59.1202 | -59.1248 | -0.10071 | -59.2255 | 63.8626 | 63.7939 | -59.1476 | -59.2209 | -0.009155 | -0.045776 | -0.059509 | 123.0148 | -0.16937 | -0.1236 | -0.059509 | -0.073242 | -0.14648 | -0.036621 | -0.050354 | -0.15106 | -0.004578 | -0.10529 | 122.9141 | 122.9141 | 59.0607 | -123.0194 | 122.937 | 122.8683 | 58.9737 | -123.1201
539.5156 | 123.0698 | -59.0973 | 63.8626 | 0.042725 | 0.013099 | 0.066304 | 0.066441 | 0.12934 | 0.0019078 | -0.0012923 | 0.087204 | -5.9768e-05 | 0.0004636 | 0.0003182 | 0.00027337 | -0.0030335 | 63.7894 | 63.8901 | -0.050354 | -59.285 | 63.8214 | -59.1156 | -59.1293 | -59.0881 | -0.009155 | -59.3674 | 63.8626 | 63.8168 | -59.1568 | -59.2484 | -0.018311 | -0.032043 | -0.041199 | 122.9874 | -0.18768 | -0.15564 | -0.073242 | -0.059509 | -0.15106 | 0 | 0.009155 | -0.27008 | -0.11902 | -0.045777 | 122.9187 | 122.8867 | 59.0469 | -122.9919 | 122.9599 | 122.9141 | 59.0881 | -123.111
540.5156 | 123.1064 | -59.0744 | 63.8672 | -0.064087 | 0.01374 | 0.064382 | 0.0705 | 0.12785 | 0.0019078 | 0.00063028 | -0.11116 | -0.003905 | 0.00025 | -0.001177 | 0.0017688 | -0.0026063 | 63.6429 | 63.9908 | 0.086975 | -59.2529 | 63.826 | -59.0973 | -59.1431 | -59.0286 | 0.073242 | -59.3033 | 63.8535 | 63.826 | -59.1156 | -59.2438 | -0.022888 | -0.068664 | -0.041198 | 123.0652 | -0.17853 | -0.10986 | -0.2243 | -0.041199 | -0.16937 | -0.013732 | 0.045777 | -0.22888 | -0.05951 | -0.041198 | 122.9004 | 122.7173 | 59.1614 | -123.0103 | 122.9279 | 122.9004 | 59.1476 | -123.111
541.5156 | 123.056 | -59.1019 | 63.8809 | 0.057983 | 0.015877 | 0.065877 | 0.069859 | 0.12977 | 0.0027622 | -0.0021469 | 0.17113 | -0.00070077 | 0.00025 | 0.0009592 | 0.0032642 | -0.0026063 | 63.7802 | 63.8626 | -0.07782 | -59.2941 | 63.8168 | -59.1019 | -59.1339 | -59.1019 | -0.027466 | -59.3765 | 63.8626 | 63.7894 | -59.166 | -59.2758 | 0 | -0.032043 | -0.064087 | 122.9645 | -0.19226 | -0.16022 | -0.10071 | -0.064087 | -0.17395 | -0.01831 | 0 | -0.27466 | -0.10071 | -0.091552 | 122.9187 | 122.8821 | 59.024 | -123.0148 | 122.9645 | 122.8912 | 59.0744 | -123.1567
542.5156 | 123.0057 | -59.0973 | 63.8535 | -0.12512 | 0.011818 | 0.065877 | 0.067509 | 0.13191 | 0.0012668 | -0.0019333 | -0.027237 | -0.0026234 | -0.000391 | -0.0024588 | 0.001128 | -0.0019653 | 63.826 | 63.9221 | 0.013733 | -59.2255 | 63.8443 | -59.0836 | -59.1339 | -59.0424 | 0.073242 | -59.317 | 63.858 | 63.7756 | -59.1156 | -59.2346 | 0.013733 | -0.036621 | -0.009156 | 123.0194 | -0.12817 | -0.091553 | -0.027466 | -0.018311 | -0.13733 | 0.004577 | 0.054932 | -0.21973 | -0.082398 | -0.07782 | 122.9416 | 122.9233 | 59.111 | -122.9874 | 122.9553 | 122.8729 | 59.1705 | -123.0881
543.5156 | 123.0652 | -59.0973 | 63.8809 | 0.0045777 | 0.012459 | 0.065022 | 0.066441 | 0.12849 | 0.0021214 | -0.00022432 | 0.087204 | -0.0026234 | -0.000391 | 0.000532 | 0.002196 | -0.0043153 | 63.8077 | 63.9038 | -0.064087 | -59.2484 | 63.8168 | -59.0973 | -59.1751 | -59.0652 | -0.004578 | -59.3582 | 63.8626 | 63.7939 | -59.1385 | -59.2438 | 0 | -0.07782 | -0.064087 | 123.0011 | -0.15106 | -0.073242 | -0.073242 | -0.041199 | -0.14648 | -0.01831 | 0.032043 | -0.26093 | -0.11444 | -0.086975 | 122.9141 | 122.905 | 59.0332 | -123.056 | 122.9599 | 122.8912 | 59.0927 | -123.1247
544.5156 | 123.1338 | -59.0698 | 63.8718 | -0.079346 | 0.01139 | 0.066731 | 0.069005 | 0.12913 | 0.003403 | -0.0030013 | -1.0648 | -0.0019824 | -0.0012454 | -0.001177 | 0.0013416 | -0.0011109 | 63.826 | 63.913 | -0.013733 | -59.2575 | 63.8168 | -59.1202 | -59.1202 | -59.0424 | 0.091553 | -59.285 | 63.8626 | 63.7985 | -59.111 | -59.2529 | -0.050354 | -0.050354 | -0.054932 | 122.9828 | -0.18768 | -0.13733 | -0.045776 | -0.041199 | -0.18311 | -0.009155 | 0.027466 | -0.21515 | -0.032043 | -0.073242 | 122.8867 | 122.8958 | 59.0561 | -122.9919 | 122.9324 | 122.8683 | 59.1614 | -123.1247
545.5156 | 123.0881 | -59.0836 | 63.8809 | 0.057983 | 0.013099 | 0.064168 | 0.070927 | 0.12742 | 0.001694 | -0.00022432 | 0.049057 | -0.002196 | -0.0016726 | 0.000532 | 0.00048697 | -0.0034607 | 63.8397 | 63.9313 | -0.018311 | -59.2575 | 63.7894 | -59.0744 | -59.1202 | -59.0332 | 0.054932 | -59.3308 | 63.8535 | 63.8168 | -59.1019 | -59.2209 | 0.009155 | -0.036621 | -0.091552 | 123.0148 | -0.17395 | -0.13733 | -0.041198 | -0.018311 | -0.13733 | -0.027465 | 0.050354 | -0.24719 | -0.10986 | -0.064087 | 122.8729 | 122.9233 | 59.0652 | -123.0011 | 122.937 | 122.9004 | 59.1385 | -123.1018
546.5156 | 123.0652 | -59.0927 | 63.8809 | -0.13275 | 0.01075 | 0.066731 | 0.069432 | 0.12998 | -0.0040738 | -0.00086512 | -0.13405 | -0.0019824 | 0.0023862 | 0.0003182 | 0.00070077 | -0.0019653 | 63.7848 | 63.8855 | -0.041199 | -59.2484 | 63.8214 | -59.1019 | -59.1202 | -59.0607 | 0.059509 | -59.3399 | 63.8901 | 63.8351 | -59.1064 | -59.2255 | -0.009156 | -0.027466 | -0.059509 | 122.9782 | -0.15564 | -0.12817 | -0.09613 | -0.013733 | -0.13275 | 0.009156 | 0.032043 | -0.24719 | -0.11444 | -0.045776 | 122.9141 | 122.8775 | 59.0515 | -123.0011 | 122.9828 | 122.9279 | 59.1522 | -123.1064
547.5156 | 123.0515 | -59.079 | 63.8763 | 0.035095 | 0.011177 | 0.067586 | 0.069218 | 0.13126 | 0.0029758 | -0.00022432 | 0.079574 | -0.001128 | 0.001318 | 0.0001046 | 0.0019824 | -0.0017517 | 63.8031 | 63.9175 | -0.045776 | -59.2438 | 63.826 | -59.1064 | -59.1293 | -59.0515 | 0.018311 | -59.3399 | 63.858 | 63.7802 | -59.1248 | -59.23 | -0.027466 | -0.050354 | -0.050354 | 122.9965 | -0.1648 | -0.11444 | -0.073242 | -0.045777 | -0.15106 | -0.018311 | 0.027465 | -0.26093 | -0.10986 | -0.096131 | 122.905 | 122.8821 | 59.0332 | -123.0057 | 122.937 | 122.8592 | 59.0973 | -123.1064
548.5156 | 123.1155 | -59.0698 | 63.8901 | -0.14038 | 0.01075 | 0.066945 | 0.068791 | 0.12998 | 0.00083955 | -0.0023605 | -0.095902 | -0.001128 | -0.0027408 | -0.0009634 | 0.0017688 | -0.0021789 | 63.7756 | 63.8992 | -0.022888 | -59.2529 | 63.8489 | -59.079 | -59.1293 | -59.0561 | 0.068665 | -59.3216 | 63.8763 | 63.8214 | -59.1385 | -59.23 | -0.009155 | -0.059509 | -0.041199 | 122.9691 | -0.18311 | -0.1236 | -0.11444 | -0.068665 | -0.16022 | -0.013733 | 0.013733 | -0.25177 | -0.091552 | -0.068665 | 122.9187 | 122.8455 | 59.0469 | -123.0194 | 122.9462 | 122.8912 | 59.1385 | -123.1201
549.5156 | 123.1476 | -59.079 | 63.8763 | -1.3916 | 0.01139 | 0.06545 | 0.06815 | 0.13361 | 0.002335 | -0.00043792 | 0.056686 | -0.0024096 | -0.000391 | -0.0009634 | 0.00070077 | -0.0021789 | 63.8306 | 63.9633 | 0.027466 | -59.23 | 63.8306 | -59.0973 | -59.1202 | -59.0332 | 0.045776 | -59.3308 | 63.8489 | 63.7711 | -59.111 | -59.2484 | -0.018311 | -0.041199 | -0.045777 | 123.0423 | -0.15106 | -0.10986 | -0.045777 | -0.032044 | -0.16937 | -0.027466 | 0.045776 | -0.25177 | -0.082398 | -0.10529 | 122.9095 | 122.9095 | 59.1064 | -122.9965 | 122.9279 | 122.85 | 59.1248 | -123.1247
550.5156 | 123.0652 | -59.0698 | 63.913 | -0.19379 | 0.0090405 | 0.067586 | 0.070927 | 0.12785 | -0.00086945 | -0.0012923 | -0.027237 | -0.002837 | 0.0015316 | -0.000109 | 0.0024096 | -0.0021789 | 63.7756 | 63.8947 | -0.045776 | -59.2621 | 63.8123 | -59.0836 | -59.1293 | -59.0607 | 0.050354 | -59.3399 | 63.8901 | 63.8214 | -59.1156 | -59.2117 | -0.013733 | -0.059509 | -0.10071 | 122.9645 | -0.19226 | -0.13275 | -0.13733 | -0.045777 | -0.14191 | -0.022888 | 0.009155 | -0.27008 | -0.12817 | -0.091553 | 122.8821 | 122.8455 | 59.024 | -123.0423 | 122.9599 | 122.8912 | 59.1202 | -123.1247
551.5156 | 123.0972 | -59.0744 | 63.8626 | -0.018311 | 0.012886 | 0.066518 | 0.06815 | 0.13191 | 0.0044712 | -0.0027877 | 0.071945 | -0.0019824 | 0.0034542 | -0.0005362 | 0.0024096 | -0.00068366 | 63.8077 | 63.9404 | -0.022888 | -59.2621 | 63.8168 | -59.0744 | -59.1385 | -59.0561 | 0.032043 | -59.3491 | 63.8626 | 63.8168 | -59.1431 | -59.2529 | 0 | -0.064087 | -0.045777 | 123.0148 | -0.18768 | -0.1236 | -0.054932 | -0.068664 | -0.17853 | 0 | 0.018311 | -0.27466 | -0.09613 | -0.045777 | 122.8912 | 122.8821 | 59.0515 | -123.0011 | 122.937 | 122.8912 | 59.1064 | -123.1155
552.5156 | 123.0789 | -59.1019 | 63.9038 | -0.1709 | 0.0079723 | 0.066945 | 0.073918 | 0.12934 | 0.0019078 | 0.0021255 | 0.0032804 | -0.0013416 | -0.0016726 | -0.000109 | 5.9768e-05 | -0.0026063 | 63.5925 | 63.913 | -0.018311 | -59.2987 | 63.8306 | -59.1064 | -59.1293 | -59.079 | 0.045776 | -59.3445 | 63.8626 | 63.826 | -59.1339 | -59.2209 | -0.004577 | -0.027465 | -0.073243 | 123.0148 | -0.19684 | -0.16937 | -0.31128 | -0.032043 | -0.11902 | -0.041199 | 0.022889 | -0.24261 | -0.1236 | -0.07782 | 122.9324 | 122.6944 | 59.0836 | -123.0331 | 122.9645 | 122.9279 | 59.1476 | -123.1247
553.5156 | 123.111 | -59.0973 | 63.858 | -0.0030518 | 0.013313 | 0.065663 | 0.071995 | 0.12849 | 0.0029758 | -0.0010787 | 0.056686 | -0.0013416 | 0.0011044 | -0.0030996 | 0.0030506 | -0.0043153 | 63.8077 | 63.7527 | -0.1831 | -59.1476 | 63.8077 | -59.111 | -59.1385 | -59.024 | 0.068665 | -59.3124 | 63.8489 | 63.7848 | -59.1248 | -59.2438 | -0.013733 | -0.041199 | -0.050354 | 122.85 | -0.050354 | -0.009155 | -0.050354 | -0.027466 | -0.14648 | -0.009155 | 0.073242 | -0.21515 | -0.068665 | -0.073242 | 122.905 | 122.905 | 58.9142 | -122.9965 | 122.9462 | 122.8821 | 59.166 | -123.1018
554.5156 | 123.0698 | -59.079 | 63.8901 | -0.34637 | 0.0069043 | 0.0678 | 0.068364 | 0.1302 | -0.0017238 | -0.0021469 | -0.080643 | -0.00027337 | -0.0023136 | -0.0016044 | 0.001128 | -0.0030335 | 63.7711 | 63.9084 | -0.036621 | -59.2621 | 63.8397 | -59.0881 | -59.1156 | -59.0607 | 0.045776 | -59.3353 | 63.8809 | 63.8306 | -59.1339 | -59.2163 | -0.009156 | -0.036622 | -0.050354 | 122.9874 | -0.18311 | -0.14648 | -0.11902 | -0.054932 | -0.13733 | -0.009156 | 0.01831 | -0.25635 | -0.11902 | -0.05951 | 122.9187 | 122.85 | 59.0424 | -123.0057 | 122.9599 | 122.9095 | 59.1248 | -123.1064
555.5156 | 123.0972 | -59.0698 | 63.8992 | -0.13275 | 0.012031 | 0.066304 | 0.070286 | 0.12913 | 0.001694 | -0.0025741 | 0.0032804 | -0.0026234 | 0.0015316 | -0.0007498 | 0.00048697 | -0.0034607 | 63.8123 | 63.9359 | -0.018311 | -59.23 | 63.8397 | -59.0836 | -59.1064 | -59.0515 | 0.082397 | -59.317 | 63.8489 | 63.7848 | -59.1156 | -59.2484 | -0.013733 | -0.036621 | -0.059509 | 123.0057 | -0.16022 | -0.1236 | -0.086975 | -0.045777 | -0.17853 | -0.050354 | 0.01831 | -0.24719 | -0.068665 | -0.11444 | 122.9095 | 122.8821 | 59.0515 | -123.0057 | 122.9187 | 122.8546 | 59.1522 | -123.1476
556.5156 | 123.0469 | -59.0698 | 63.8992 | -0.21667 | 0.0069043 | 0.06545 | 0.066014 | 0.12977 | -0.0036464 | -0.0017197 | -0.057755 | -0.0015552 | -0.0038088 | -0.0016044 | -0.00036743 | -0.0023927 | 63.7711 | 63.913 | -0.018311 | -59.2621 | 63.8489 | -59.1019 | -59.1293 | -59.1751 | 0 | -59.3399 | 63.8672 | 63.8306 | -59.1293 | -59.2072 | -0.032044 | -0.059509 | -0.050354 | 122.9828 | -0.19226 | -0.13275 | -0.12817 | -0.059509 | -0.13733 | -0.032044 | -0.10529 | -0.27008 | -0.13275 | -0.068665 | 122.9187 | 122.8409 | 59.0515 | -123.0286 | 122.937 | 122.9004 | 59.0698 | -123.1064
557.5156 | 123.0972 | -59.0607 | 63.9084 | -0.11749 | 0.010322 | 0.065022 | 0.069859 | 0.13084 | 0.002335 | -0.0017197 | -0.10353 | -0.0024096 | 0.001959 | -0.0009634 | 0.002196 | -0.0053833 | 63.7619 | 63.9038 | -0.027466 | -59.2484 | 63.8489 | -59.0973 | -59.1202 | -59.0652 | 0.07782 | -59.3262 | 63.8992 | 63.8031 | -59.1339 | -59.2255 | -0.036621 | -0.059509 | -0.059509 | 122.9645 | -0.18768 | -0.12817 | -0.14648 | -0.073242 | -0.1648 | -0.009155 | -0.004578 | -0.2655 | -0.10071 | -0.10529 | 122.9095 | 122.8226 | 59.0332 | -123.0286 | 122.9599 | 122.8638 | 59.1385 | -123.1338
558.5156 | 123.0881 | -59.079 | 63.9221 | -0.18616 | 0.0075451 | 0.0678 | 0.069218 | 0.12721 | -0.0032192 | -0.0044967 | 0.026169 | -0.0026234 | 0.0004636 | -0.0007498 | -0.00015383 | -0.00047006 | 63.7253 | 64.1602 | 0.004578 | -59.3399 | 63.8809 | -59.0744 | -59.1339 | -59.0607 | 0.059509 | -59.3262 | 63.8901 | 63.8031 | -59.1293 | -59.1888 | 0.004577 | -0.054932 | -0.041199 | 123.2391 | -0.26093 | -0.20599 | -0.19684 | -0.050354 | -0.10986 | -0.032043 | 0.01831 | -0.24719 | -0.13733 | -0.11902 | 122.9599 | 122.8043 | 59.0836 | -123.056 | 122.9691 | 122.8821 | 59.1385 | -123.111
559.5156 | 123.1018 | -59.0744 | 63.8992 | -0.11749 | 0.0069043 | 0.067586 | 0.071354 | 0.12785 | -0.00065585 | -0.00086512 | -0.080643 | -0.002196 | -0.0012454 | -0.0009634 | 0.0013416 | -0.0023927 | 63.7665 | 63.9038 | -0.036621 | -59.2667 | 63.8535 | -59.0744 | -59.1156 | -59.0652 | 0.041199 | -59.3582 | 63.8855 | 63.8214 | -59.1248 | -59.2529 | 0 | -0.041199 | -0.045776 | 122.9782 | -0.19226 | -0.15106 | -0.13275 | -0.050354 | -0.17853 | -0.013733 | 0.009155 | -0.28381 | -0.10529 | -0.07782 | 122.9279 | 122.8409 | 59.0378 | -123.0148 | 122.9599 | 122.8958 | 59.1156 | -123.1522
560.5156 | 123.1659 | -59.0424 | 63.8763 | -0.16327 | 0.0062635 | 0.068654 | 0.069432 | 0.12998 | -0.0051418 | -0.0030013 | 0.0032804 | -0.0013416 | -0.0027408 | -0.0016044 | 0.00027337 | -0.0026063 | 63.8397 | 64.0503 | 0.086975 | -59.198 | 63.8031 | -59.0652 | -59.0973 | -58.992 | 0.15106 | -59.2438 | 63.8672 | 63.7939 | -59.0744 | -59.2255 | -0.022889 | -0.054932 | -0.073242 | 123.0927 | -0.15564 | -0.10071 | -0.036621 | -0.032044 | -0.18311 | -0.009156 | 0.050354 | -0.20142 | -0.01831 | -0.082398 | 122.8455 | 122.8821 | 59.1293 | -122.9736 | 122.9095 | 122.8363 | 59.1934 | -123.1018
561.5156 | 123.0972 | -59.0881 | 63.8901 | -0.1709 | 0.0090405 | 0.067586 | 0.069218 | 0.1287 | -0.00065585 | -0.0019333 | -0.080643 | -0.002196 | -0.0016726 | -0.0030996 | 0.0013416 | -0.0030335 | 63.7802 | 63.9084 | -0.032043 | -59.2484 | 63.8535 | -59.0973 | -59.1248 | -59.0607 | 0.054932 | -59.3445 | 63.913 | 63.7985 | -59.1156 | -59.2255 | -0.009155 | -0.036621 | -0.036621 | 122.9965 | -0.16022 | -0.1236 | -0.10986 | -0.027466 | -0.13733 | 0.022888 | 0.027466 | -0.25635 | -0.11902 | -0.091553 | 122.9416 | 122.8683 | 59.0561 | -123.0148 | 123.0011 | 122.8867 | 59.1431 | -123.1155
562.5156 | 123.143 | -59.0286 | 63.8763 | -0.16327 | 0.0051953 | 0.068868 | 0.067723 | 0.1302 | -0.004501 | -0.0034287 | 0.0032804 | -0.0013416 | -0.0027408 | -0.0024588 | 0.00048697 | -0.0026063 | 63.8351 | 64.0274 | 0.068665 | -59.198 | 63.7894 | -59.0607 | -59.0927 | -59.0103 | 0.14191 | -59.2575 | 63.858 | 63.7939 | -59.0927 | -59.2117 | -0.032044 | -0.064087 | -0.086975 | 123.056 | -0.16937 | -0.10529 | -0.041199 | -0.064087 | -0.18311 | -0.018311 | 0.01831 | -0.22888 | -0.045776 | -0.082398 | 122.818 | 122.8638 | 59.0973 | -122.9691 | 122.8867 | 122.8226 | 59.1705 | -123.0881
563.5156 | 123.0789 | -59.0698 | 63.9084 | -0.20142 | 0.0081861 | 0.069936 | 0.0705 | 0.13041 | 0.00062595 | -0.0032151 | -0.17983 | -0.0043324 | -0.000391 | 0.0009592 | 0.001128 | -0.0051697 | 63.8077 | 63.8626 | -0.045776 | -59.285 | 63.8901 | -59.1202 | -59.1476 | -59.0607 | 0.032043 | -59.3445 | 63.8763 | 63.826 | -59.1248 | -59.2255 | -0.050354 | -0.07782 | -0.01831 | 122.9324 | -0.21515 | -0.13733 | -0.10071 | -0.054932 | -0.15564 | -0.032043 | 0.009155 | -0.27466 | -0.11902 | -0.082397 | 122.9599 | 122.8775 | 59.024 | -123.056 | 122.9462 | 122.8958 | 59.1019 | -123.1338
564.5156 | 123.1476 | -59.0424 | 63.8626 | -0.13275 | 0.0045545 | 0.06844 | 0.068364 | 0.12678 | -0.0057828 | -0.0032151 | -0.019608 | -0.0041186 | -0.0029544 | -0.0024588 | 0.00027337 | -0.0019653 | 63.8535 | 64.032 | 0.073242 | -59.1888 | 63.7939 | -59.0378 | -59.0973 | -58.9737 | 0.16937 | -59.23 | 63.8306 | 63.7711 | -59.0698 | -59.2163 | 0.004577 | -0.054932 | -0.068665 | 123.0743 | -0.14648 | -0.091553 | -0.009155 | -0.027466 | -0.17395 | -0.032044 | 0.068664 | -0.18768 | -0.013733 | -0.091553 | 122.8363 | 122.8958 | 59.1156 | -122.9599 | 122.8729 | 122.8134 | 59.2117 | -123.0789
565.5156 | 123.0606 | -59.111 | 63.8397 | 0.12665 | 0.012459 | 0.069081 | 0.070286 | 0.12657 | 0.004044 | -0.0010787 | -0.83595 | -0.0026234 | 0.0021726 | -0.0007498 | 0.0047596 | -0.0026063 | 63.7344 | 63.8306 | -0.33417 | -59.5779 | 63.7573 | -59.1385 | -59.1614 | -59.0698 | -0.10071 | -59.404 | 63.8672 | 63.7756 | -59.1339 | -59.2621 | -0.027466 | -0.050354 | -0.082398 | 122.9416 | -0.46692 | -0.41656 | -0.10529 | -0.022888 | -0.15106 | 0.027465 | 0.041199 | -0.29297 | -0.14191 | -0.064087 | 122.8683 | 122.8455 | 58.7769 | -123.0011 | 122.9782 | 122.8867 | 59.0103 | -123.1018
566.5156 | 123.1888 | -58.9966 | 63.858 | -0.086975 | 6.8308e-05 | 0.069295 | 0.067082 | 0.12934 | -0.0042874 | -0.0036423 | 0.62126 | -0.0036914 | -0.0038088 | -0.0026724 | 0.001128 | -0.0023927 | 63.8809 | 64.476 | 0.36621 | -59.1385 | 63.858 | -59.0378 | -59.079 | -58.9554 | 0.19226 | -59.2255 | 63.8031 | 63.7619 | -59.0744 | -59.198 | -0.041199 | -0.082397 | 0 | 123.4726 | -0.14191 | -0.05951 | 0.022888 | -0.07782 | -0.20142 | -0.054931 | 0.041199 | -0.22888 | -0.027466 | -0.09613 | 122.8546 | 122.8775 | 59.3628 | -122.937 | 122.7997 | 122.7585 | 59.1888 | -123.056
567.5156 | 123.111 | -59.0286 | 63.8809 | -0.19379 | 0.01075 | 0.068227 | 0.068364 | 0.13105 | -0.00044225 | -0.0019333 | -0.080643 | -0.0032642 | 0.00025 | -0.0024588 | 0.00027337 | -0.0043153 | 63.8351 | 63.9954 | 0.059509 | -59.2209 | 63.8306 | -59.0927 | -59.1064 | -59.024 | 0.10986 | -59.2896 | 63.8809 | 63.8123 | -59.1064 | -59.2163 | -0.064087 | -0.07782 | -0.050354 | 123.024 | -0.19226 | -0.11444 | -0.045776 | -0.07782 | -0.18768 | 0 | 0.004577 | -0.26093 | -0.073242 | -0.068664 | 122.8592 | 122.8638 | 59.0881 | -122.9874 | 122.9095 | 122.8409 | 59.1385 | -123.0972
568.5156 | 123.1796 | -59.0378 | 63.8397 | 0.065613 | 0.0030591 | 0.065877 | 0.066655 | 0.13212 | -0.0019376 | -0.0030013 | -0.0043486 | -0.004546 | -0.004877 | -0.0007498 | 0.0013416 | -0.0034607 | 63.8809 | 64.0411 | 0.086975 | -59.198 | 63.826 | -59.0744 | -59.0744 | -58.9554 | 0.17395 | -59.2163 | 63.8168 | 63.7299 | -59.0881 | -59.198 | -0.036621 | -0.036621 | -0.013733 | 123.0789 | -0.16022 | -0.1236 | 0.041198 | -0.050354 | -0.16022 | -0.022889 | 0.082398 | -0.17853 | -0.018311 | -0.10986 | 122.8638 | 122.9187 | 59.1248 | -122.9141 | 122.8546 | 122.7676 | 59.2117 | -123.0377
569.5156 | 123.0606 | -59.079 | 63.9175 | -0.17853 | 0.0066907 | 0.068654 | 0.068791 | 0.12977 | 0.0014804 | 0.00041648 | -0.11879 | -0.0032642 | -0.0010318 | -0.0013906 | 0.00027337 | -0.0026063 | 63.8077 | 63.9679 | 0.013733 | -59.23 | 63.8718 | -59.0744 | -59.1156 | -59.0378 | 0.073242 | -59.3308 | 63.8947 | 63.8031 | -59.1385 | -59.2255 | 0.004577 | -0.036622 | -0.045777 | 123.0469 | -0.15106 | -0.11444 | -0.10986 | -0.05951 | -0.14649 | -0.022889 | 0.041198 | -0.25177 | -0.10529 | -0.11444 | 122.9507 | 122.8867 | 59.0927 | -123.0331 | 122.9736 | 122.8821 | 59.1522 | -123.143
570.5156 | 123.1155 | -59.0378 | 63.8992 | -0.16327 | 0.0079723 | 0.065236 | 0.070714 | 0.12956 | 0.0021214 | -0.0017197 | -0.13405 | -0.00091437 | 0.0015316 | 0.0007456 | 0.0026234 | -0.0038879 | 63.7848 | 63.8992 | -0.022888 | -59.2575 | 63.8672 | -59.0652 | -59.1339 | -59.0515 | 0.050354 | -59.3399 | 63.9084 | 63.7985 | -59.1339 | -59.2438 | -0.027466 | -0.09613 | -0.032044 | 122.937 | -0.21973 | -0.1236 | -0.11444 | -0.09613 | -0.20599 | 0.009155 | -0.013733 | -0.30212 | -0.096131 | -0.10071 | 122.905 | 122.8226 | 59.0149 | -123.0331 | 122.9462 | 122.8363 | 59.0881 | -123.143
571.5156 | 123.0972 | -59.0424 | 63.8901 | -0.16327 | 0.0060497 | 0.067372 | 0.065159 | 0.13105 | -0.00065585 | 0.00020288 | -0.065384 | -0.0026234 | 3.6404e-05 | 0.0001046 | 5.9768e-05 | -0.0028199 | 63.8443 | 64.0228 | 0.050354 | -59.2117 | 63.8351 | -59.0561 | -59.1019 | -59.024 | 0.11902 | -59.3033 | 63.8672 | 63.7802 | -59.1064 | -59.2117 | -0.013733 | -0.05951 | -0.054932 | 123.0652 | -0.16937 | -0.10986 | -0.045777 | -0.064087 | -0.16937 | -0.022889 | 0.01831 | -0.26093 | -0.091553 | -0.10986 | 122.8775 | 122.8867 | 59.0927 | -122.9919 | 122.9095 | 122.8226 | 59.1614 | -123.1018
572.5156 | 123.2117 | -59.024 | 63.8443 | -0.29297 | 0.0054089 | 0.068227 | 0.06815 | 0.12956 | -0.0030056 | -0.0025741 | 0.0032804 | -0.0041186 | -0.000391 | -0.001818 | 0.0019824 | -0.0030335 | 63.8809 | 64.0732 | 0.09613 | -59.2026 | 63.7939 | -59.0561 | -59.1156 | -58.9645 | 0.17853 | -59.2209 | 63.8626 | 63.7436 | -59.0744 | -59.23 | -0.032043 | -0.091553 | -0.050354 | 123.0972 | -0.17853 | -0.086975 | 0.036621 | -0.050354 | -0.20599 | 0.018311 | 0.059509 | -0.19684 | 0.009156 | -0.10071 | 122.818 | 122.905 | 59.1202 | -122.9599 | 122.8867 | 122.7676 | 59.2026 | -123.0743
573.5156 | 123.1567 | -59.0515 | 63.8855 | -0.16327 | 0.0049817 | 0.066945 | 0.068577 | 0.13062 | -0.0012966 | -0.0027877 | -0.080643 | -0.0019824 | -0.0001774 | 0.0001046 | 0.00048697 | -0.0038879 | 63.8489 | 64.0457 | 0.059509 | -59.198 | 63.8077 | -59.0607 | -59.111 | -58.9783 | 0.15564 | -59.2438 | 63.858 | 63.7665 | -59.0836 | -59.2117 | -0.009155 | -0.059509 | -0.07782 | 123.0972 | -0.14648 | -0.086975 | -0.036621 | -0.032043 | -0.16022 | -0.027466 | 0.073243 | -0.19226 | -0.032043 | -0.11902 | 122.8592 | 122.9004 | 59.111 | -122.9965 | 122.9095 | 122.818 | 59.2072 | -123.0972
574.5156 | 123.1842 | -59.0469 | 63.8397 | -0.0030518 | 0.00092291 | 0.069722 | 0.067936 | 0.12956 | -0.0032192 | -0.00086512 | 0.071945 | -0.003905 | -0.0044498 | -0.0009634 | 0.0019824 | -0.0028199 | 63.8351 | 64.0182 | 0.027466 | -59.2117 | 63.8168 | -59.0607 | -59.1248 | -58.9554 | 0.11902 | -59.2529 | 63.8306 | 63.7253 | -59.0836 | -59.2346 | -0.013733 | -0.07782 | -0.022889 | 123.0652 | -0.16479 | -0.086975 | -0.004578 | -0.036621 | -0.18768 | -0.009156 | 0.091553 | -0.20599 | -0.018311 | -0.11444 | 122.8638 | 122.8821 | 59.0744 | -122.9645 | 122.8775 | 122.7722 | 59.166 | -123.0743
575.5156 | 123.1064 | -59.079 | 63.8489 | -0.0030518 | 0.011177 | 0.066945 | 0.070714 | 0.12849 | 0.0042576 | 0.00063028 | 0.049057 | -0.00091437 | 0.0015316 | -0.0007498 | 0.002837 | -0.0066651 | 63.826 | 63.9038 | -0.041199 | -59.2667 | 63.826 | -59.1202 | -59.1431 | -59.0286 | 0.009155 | -59.3628 | 63.8901 | 63.7527 | -59.1202 | -59.2621 | -0.041199 | -0.064087 | -0.022888 | 122.9828 | -0.18768 | -0.1236 | -0.022888 | -0.041199 | -0.18311 | 0.041199 | 0.050354 | -0.28381 | -0.10071 | -0.09613 | 122.905 | 122.905 | 59.0378 | -122.9919 | 122.9691 | 122.8317 | 59.0881 | -123.111
576.5156 | 123.2208 | -59.0332 | 63.858 | -0.079346 | 0.0036999 | 0.066945 | 0.067509 | 0.1302 | -0.002792 | -0.0025741 | 0.079574 | -0.002837 | -0.0040226 | 0.0003182 | -0.0012218 | -0.0017517 | 63.8626 | 64.0411 | 0.059509 | -59.1934 | 63.7665 | -59.0836 | -59.1156 | -58.9279 | 0.17395 | -59.2117 | 63.826 | 63.7436 | -59.0881 | -59.2072 | -0.050354 | -0.082398 | -0.091553 | 123.0743 | -0.16022 | -0.077819 | 0.004578 | -0.054932 | -0.17395 | -0.032043 | 0.10529 | -0.17853 | -0.004578 | -0.11444 | 122.7997 | 122.8958 | 59.0927 | -122.9736 | 122.8592 | 122.7768 | 59.2072 | -123.0652
577.5156 | 123.1476 | -59.0607 | 63.8763 | -0.14801 | 0.0075451 | 0.065877 | 0.066441 | 0.13041 | -1.505e-05 | -0.0017197 | -0.019608 | -0.0034778 | -0.0035952 | -0.0048086 | 0.00048697 | -0.0041017 | 63.8489 | 64.032 | 0.082397 | -59.1888 | 63.8123 | -59.0515 | -59.1064 | -58.9828 | 0.16937 | -59.2575 | 63.8535 | 63.7482 | -59.1019 | -59.2072 | 0.009155 | -0.045776 | -0.064087 | 123.0927 | -0.12817 | -0.082398 | -0.027466 | -0.041199 | -0.14648 | -0.022888 | 0.07782 | -0.19684 | -0.050354 | -0.12817 | 122.8729 | 122.9095 | 59.1431 | -122.9828 | 122.9141 | 122.8088 | 59.23 | -123.0835
578.5156 | 123.1979 | -59.0195 | 63.8489 | -0.048828 | 0.0060497 | 0.069722 | 0.066014 | 0.12913 | -0.0042874 | -0.0034287 | 0.087204 | -0.0030506 | 0.00025 | -0.003527 | 0.0013416 | -0.0030335 | 63.826 | 64.0045 | 0.045776 | -59.2255 | 63.8031 | -59.079 | -59.0973 | -58.9417 | 0.14191 | -59.2255 | 63.8214 | 63.739 | -59.0927 | -59.2117 | -0.059509 | -0.07782 | -0.045776 | 123.024 | -0.20599 | -0.12817 | -0.022888 | -0.073242 | -0.19226 | -0.027466 | 0.07782 | -0.20599 | -0.013733 | -0.10986 | 122.8226 | 122.8455 | 59.0652 | -122.9462 | 122.8409 | 122.7585 | 59.1614 | -123.0606
579.5156 | 123.0835 | -59.0515 | 63.9038 | -0.19379 | 0.0045545 | 0.066091 | 0.067509 | 0.12977 | -0.001083 | -0.0012923 | -0.11116 | -0.0015552 | -0.0008182 | -0.0022452 | 0.002196 | -0.0053833 | 63.8443 | 64.0182 | 0.050354 | -59.2026 | 63.8077 | -59.0469 | -59.1293 | -59.0103 | 0.10986 | -59.2896 | 63.8763 | 63.7527 | -59.1064 | -59.2392 | 0.004578 | -0.077819 | -0.096131 | 123.0698 | -0.15106 | -0.073243 | -0.05951 | -0.054931 | -0.18768 | -0.027466 | 0.041199 | -0.23804 | -0.050354 | -0.15106 | 122.8592 | 122.8958 | 59.1019 | -123.0331 | 122.9279 | 122.8043 | 59.1614 | -123.143
580.5156 | 123.0698 | -59.079 | 63.9084 | -0.17853 | 0.0090405 | 0.066518 | 0.0705 | 0.12892 | 0.001694 | -0.0019333 | -0.13405 | -0.002837 | 0.0006772 | -0.0013906 | 0.0015552 | -0.0045289 | 63.7985 | 63.8992 | -0.036621 | -59.2804 | 63.8535 | -59.1019 | -59.1202 | -59.024 | 0.036621 | -59.3445 | 63.8992 | 63.7939 | -59.1202 | -59.2484 | -0.022889 | -0.041199 | -0.054931 | 122.9782 | -0.20142 | -0.16022 | -0.10986 | -0.041199 | -0.16937 | -0.009155 | 0.054931 | -0.2655 | -0.09613 | -0.11444 | 122.9324 | 122.8775 | 59.0424 | -123.0286 | 122.9782 | 122.8729 | 59.1156 | -123.1567
581.5156 | 123.1842 | -59.0012 | 63.8718 | -0.11749 | 0.0077587 | 0.068654 | 0.068577 | 0.13148 | -0.002792 | -0.0047103 | -0.20271 | -0.0043324 | -0.0021 | -0.0003226 | 0.00027337 | -0.0013245 | 64.119 | 64.2151 | 0.032043 | -59.3719 | 63.7985 | -59.0744 | -59.1248 | -58.9508 | 0.17395 | -59.2163 | 63.8443 | 63.7344 | -59.0836 | -59.2117 | -0.073242 | -0.1236 | -0.073242 | 123.2162 | -0.37079 | -0.24719 | 0.24719 | -0.082397 | -0.21057 | -0.027466 | 0.050354 | -0.21515 | -0.004578 | -0.13733 | 122.7997 | 123.1201 | 59.0332 | -122.9965 | 122.8455 | 122.7356 | 59.1751 | -123.0835
582.5156 | 123.1796 | -59.0012 | 63.8626 | -0.010681 | 0.0045545 | 0.067586 | 0.066441 | 0.12892 | -0.0015102 | -0.0023605 | 0.056686 | -0.0043324 | -0.0012454 | -0.0033134 | 0.0019824 | -0.0034607 | 63.8306 | 64.0137 | 0.022888 | -59.2209 | 63.8123 | -59.079 | -59.1156 | -58.9691 | 0.11902 | -59.2346 | 63.8306 | 63.7161 | -59.0881 | -59.23 | -0.077819 | -0.11444 | -0.050354 | 123.0148 | -0.21973 | -0.10529 | -0.032044 | -0.086975 | -0.22888 | -0.032044 | 0.032044 | -0.23346 | -0.004577 | -0.14648 | 122.8134 | 122.8317 | 59.024 | -122.9782 | 122.8317 | 122.7173 | 59.1202 | -123.0927
583.5156 | 123.1293 | -59.0286 | 63.9084 | -0.19379 | 0.0066907 | 0.067372 | 0.068791 | 0.1302 | -0.00065585 | -0.0017197 | -0.11116 | -0.0026234 | -0.0016726 | -0.001818 | 0.002196 | -0.0030335 | 63.8535 | 64.0091 | 0.059509 | -59.2117 | 63.8443 | -59.0469 | -59.0973 | -58.992 | 0.12817 | -59.285 | 63.8718 | 63.7848 | -59.1064 | -59.2392 | -0.018311 | -0.068665 | -0.064087 | 123.0377 | -0.18311 | -0.11444 | -0.054931 | -0.07782 | -0.21057 | -0.036621 | 0.036621 | -0.25635 | -0.045776 | -0.1236 | 122.8729 | 122.8821 | 59.0881 | -123.0057 | 122.9004 | 122.8134 | 59.1568 | -123.1476
584.5156 | 123.2208 | -59.0469 | 63.8489 | 0.027466 | 0.0051953 | 0.066731 | 0.069005 | 0.12977 | -0.0021512 | -0.0019333 | 0.064316 | -0.0049732 | -0.0038088 | -0.0013906 | -0.00015383 | -0.0045289 | 63.7985 | 63.9862 | -0.013733 | -59.2255 | 63.8123 | -59.0836 | -59.0973 | -58.992 | 0.10071 | -59.2575 | 63.826 | 63.7161 | -59.1064 | -59.2438 | -0.036621 | -0.050354 | -0.036621 | 123.0331 | -0.17853 | -0.12817 | -0.050354 | -0.059509 | -0.19684 | -0.022888 | 0.054932 | -0.21057 | -0.013733 | -0.13275 | 122.8592 | 122.8455 | 59.0332 | -122.9462 | 122.8729 | 122.7631 | 59.1476 | -123.0927
585.5156 | 123.2208 | -59.0195 | 63.858 | -0.064087 | 0.0028455 | 0.065236 | 0.066655 | 0.1302 | -0.0015102 | -0.00043792 | 0.78911 | -0.004546 | -0.0018862 | -0.0022452 | 0.0017688 | -0.0038879 | 63.8992 | 63.858 | 0.23804 | -58.9417 | 63.8855 | -59.0195 | -59.0561 | -58.9462 | 0.20142 | -59.2346 | 63.8306 | 63.7482 | -59.0927 | -59.23 | 0 | -0.036621 | 0.027466 | 122.8775 | 0.07782 | 0.11444 | 0.041199 | -0.073242 | -0.21057 | -0.027466 | 0.073242 | -0.21515 | -0.004577 | -0.10986 | 122.905 | 122.9187 | 59.2575 | -122.9141 | 122.85 | 122.7676 | 59.2209 | -123.0881
586.5156 | 123.2071 | -59.0149 | 63.8351 | -0.086975 | 0.0058361 | 0.066518 | 0.069645 | 0.12977 | -0.0019376 | -0.0021469 | -0.050125 | -0.0041186 | -0.0025272 | -0.0039542 | -0.00036743 | -0.0041017 | 63.913 | 64.0686 | 0.091553 | -59.1934 | 63.7985 | -59.0561 | -59.0927 | -59.0744 | -0.022888 | -59.1934 | 63.826 | 63.707 | -59.079 | -59.2163 | -0.041198 | -0.077819 | -0.036621 | 123.0835 | -0.17853 | -0.10071 | 0.07782 | -0.064086 | -0.20142 | -0.009155 | -0.059509 | -0.17853 | 0.022889 | -0.12817 | 122.8134 | 122.9279 | 59.1064 | -122.9279 | 122.8409 | 122.7219 | 58.992 | -123.0515
587.5156 | 123.1979 | -59.0378 | 63.8351 | -0.40741 | 0.0058361 | 0.066304 | 0.068364 | 0.13105 | -0.0023648 | -0.0017197 | -0.027237 | -0.0047596 | -0.0025272 | -0.0013906 | 0.002196 | -0.0051697 | 63.8718 | 64.0549 | 0.086975 | -59.1751 | 63.7848 | -59.0561 | -59.0744 | -58.9325 | 0.18768 | -59.2209 | 63.8306 | 63.7344 | -59.1202 | -59.2072 | -0.01831 | -0.036621 | -0.050354 | 123.0927 | -0.13733 | -0.10071 | 0.036621 | -0.082397 | -0.16937 | -0.004578 | 0.10529 | -0.1831 | -0.013733 | -0.10071 | 122.8226 | 122.9095 | 59.1248 | -122.9095 | 122.8683 | 122.7722 | 59.2255 | -123.0423
588.5156 | 123.1613 | -59.0515 | 63.8443 | 0.057983 | 0.0039135 | 0.067586 | 0.069859 | 0.12785 | -1.505e-05 | -0.00086512 | 0.11772 | -0.004546 | -0.0018862 | -0.0024588 | 0.00027337 | -0.0043153 | 63.8168 | 63.9771 | -0.004578 | -59.2346 | 63.8031 | -59.0744 | -59.1156 | -58.9691 | 0.068665 | -59.2621 | 63.8351 | 63.7115 | -59.0973 | -59.2209 | -0.022888 | -0.064087 | -0.041198 | 123.0286 | -0.18311 | -0.11902 | -0.027466 | -0.045776 | -0.16937 | -0.009155 | 0.082398 | -0.21057 | -0.041199 | -0.13275 | 122.8546 | 122.8683 | 59.0469 | -122.9599 | 122.8867 | 122.7631 | 59.1202 | -123.0652
589.5156 | 123.175 | -59.0378 | 63.858 | -0.10223 | 0.0066907 | 0.070149 | 0.069432 | 0.12977 | -0.0012966 | -0.0034287 | -0.24849 | -0.003905 | -0.0023136 | -0.0009634 | 0.0013416 | -0.0058105 | 63.913 | 64.0823 | 0.068665 | -58.9828 | 63.8672 | -59.0332 | -59.0469 | -58.9645 | 0.16937 | -59.1888 | 63.8168 | 63.7115 | -59.0927 | -59.2072 | 0.004578 | -0.009155 | 0.009155 | 123.1201 | 0.054932 | 0.064087 | 0.054932 | -0.054931 | -0.16937 | -0.041199 | 0.073242 | -0.15106 | 0.01831 | -0.14648 | 122.905 | 122.9507 | 59.1064 | -122.905 | 122.8546 | 122.7493 | 59.2072 | -123.0652
590.5156 | 123.175 | -59.0424 | 63.8397 | 0.34027 | 0.0026319 | 0.068227 | 0.06815 | 0.12998 | -0.0019376 | -0.0017197 | 0.11772 | -0.0032642 | -0.0012454 | -0.0024588 | 0.0019824 | -0.0051697 | 63.7848 | 63.9404 | -0.032043 | -59.2484 | 63.7939 | -59.0973 | -59.1156 | -59.0057 | 0.050354 | -59.2941 | 63.8306 | 63.7253 | -59.1202 | -59.2209 | -0.054932 | -0.073243 | -0.045777 | 122.9828 | -0.20599 | -0.13275 | -0.054932 | -0.07782 | -0.17853 | -0.009156 | 0.036621 | -0.25177 | -0.073242 | -0.11444 | 122.8363 | 122.8271 | 59.0103 | -122.9553 | 122.8729 | 122.7676 | 59.0927 | -123.0606
591.5156 | 123.1293 | -59.0149 | 63.8947 | -0.056458 | 0.0058361 | 0.0678 | 0.066655 | 0.13212 | 0.0010532 | -0.0019333 | 0.064316 | -0.0054004 | -0.0018862 | 0.0018136 | 0.00070077 | -0.0062379 | 63.8718 | 64.064 | 0.050354 | -59.1888 | 63.8214 | -59.0652 | -59.1248 | -58.9188 | 0.1831 | -59.1888 | 63.8214 | 63.7161 | -59.0881 | -59.198 | -0.050354 | -0.10986 | -0.073242 | 123.0789 | -0.17395 | -0.064087 | -0.022888 | -0.073242 | -0.1831 | -0.073242 | 0.096131 | -0.17395 | 0.009155 | -0.17853 | 122.8363 | 122.8867 | 59.0652 | -123.0194 | 122.8363 | 122.731 | 59.198 | -123.0927
592.5156 | 123.1567 | -59.0515 | 63.8397 | 0.073242 | 0.0049817 | 0.066304 | 0.069218 | 0.12678 | -0.00044225 | -0.0017197 | 0.19402 | -0.0060412 | -0.0038088 | 0.0003182 | 0.001128 | -0.0032471 | 63.8168 | 63.945 | -0.036621 | -59.2484 | 63.7985 | -59.0698 | -59.079 | -58.992 | 0.018311 | -59.3033 | 63.826 | 63.7253 | -59.1339 | -59.2484 | -0.01831 | -0.027465 | -0.041199 | 122.9965 | -0.19684 | -0.16937 | -0.022889 | -0.082397 | -0.19684 | -0.013733 | 0.05951 | -0.25177 | -0.054932 | -0.11444 | 122.85 | 122.8683 | 59.0149 | -122.9187 | 122.8775 | 122.7768 | 59.0698 | -123.0881
593.5156 | 123.2117 | -59.0103 | 63.8214 | -0.11749 | 0.0022045 | 0.067372 | 0.06815 | 0.12892 | -0.0019376 | -0.0036423 | 0.15587 | -0.0013416 | -0.0029544 | -0.0043814 | 0.001128 | -0.0015381 | 63.913 | 64.0778 | 0.07782 | -59.1888 | 63.7985 | -59.0881 | -59.0881 | -58.9783 | 0.14648 | -59.2163 | 63.8351 | 63.7253 | -59.0744 | -59.2026 | -0.07782 | -0.07782 | -0.022888 | 123.0881 | -0.17853 | -0.10071 | 0.091553 | -0.064087 | -0.19226 | 0.013733 | 0.032044 | -0.20599 | -0.013733 | -0.09613 | 122.8088 | 122.9233 | 59.0881 | -122.9095 | 122.8455 | 122.7356 | 59.1568 | -123.024
594.5156 | 123.1842 | -59.0652 | 63.8397 | 0.17242 | 0.0069043 | 0.066304 | 0.065587 | 0.12977 | 0.00041235 | -0.0057785 | 0.1635 | -0.0032642 | -0.0029544 | -0.0007498 | 0.0019824 | -0.0028199 | 63.8168 | 63.9633 | -0.050354 | -59.2529 | 63.7711 | -59.0881 | -59.1293 | -58.9966 | 0.022888 | -59.3033 | 63.8168 | 63.7207 | -59.1293 | -59.2346 | -0.022888 | -0.064086 | -0.068665 | 123.0286 | -0.18768 | -0.1236 | -0.022889 | -0.064086 | -0.16937 | -0.022889 | 0.068665 | -0.23804 | -0.068665 | -0.11902 | 122.8363 | 122.8821 | 59.0149 | -122.9691 | 122.8821 | 122.7859 | 59.0881 | -123.0743
595.5156 | 123.2071 | -59.0332 | 63.8168 | 0.042725 | 0.0026319 | 0.066091 | 0.066441 | 0.12892 | 0.00019875 | -0.0012923 | 0.087204 | -0.0030506 | -0.0035952 | -0.0009634 | 0.0024096 | -0.0053833 | 63.8306 | 63.9771 | -0.004578 | -59.2346 | 63.7894 | -59.0836 | -59.1248 | -58.9645 | 0.10071 | -59.2575 | 63.8214 | 63.7344 | -59.0973 | -59.2529 | -0.050354 | -0.091553 | -0.027465 | 123.0103 | -0.20142 | -0.10986 | 0.013733 | -0.064087 | -0.21973 | 0.004578 | 0.068664 | -0.2243 | -0.004577 | -0.082397 | 122.8226 | 122.8638 | 59.0286 | -122.9416 | 122.8546 | 122.7676 | 59.1339 | -123.0698
596.5156 | 123.1201 | -59.0652 | 63.8397 | 0.15717 | 0.0073315 | 0.0678 | 0.067296 | 0.12827 | 0.0012668 | -0.0040695 | 0.12535 | -0.002837 | -0.0044498 | -0.0024588 | 0.0032642 | -0.0049561 | 63.826 | 63.9633 | -0.045776 | -59.2621 | 63.7894 | -59.0881 | -59.1476 | -59.0698 | 0.050354 | -59.2987 | 63.8351 | 63.739 | -59.1293 | -59.2392 | -0.022888 | -0.082397 | -0.050354 | 123.0286 | -0.19684 | -0.11444 | -0.013733 | -0.064086 | -0.17395 | -0.004578 | -0.004577 | -0.23346 | -0.059509 | -0.10071 | 122.8546 | 122.8912 | 59.0195 | -122.9874 | 122.9004 | 122.8043 | 59.1156 | -123.0789
597.5156 | 123.1979 | -59.0195 | 63.8306 | -0.0030518 | 0.0036999 | 0.065877 | 0.066014 | 0.12763 | -0.0042874 | -0.00043792 | 0.033798 | -0.0026234 | 3.6404e-05 | -0.0016044 | 0.0017688 | -0.0021789 | 63.858 | 63.9816 | 0.018311 | -59.2163 | 63.8077 | -59.0652 | -59.1064 | -58.9508 | 0.10071 | -59.2392 | 63.8535 | 63.7436 | -59.0698 | -59.2209 | -0.045777 | -0.086975 | -0.022888 | 123.0011 | -0.19684 | -0.10986 | 0.027466 | -0.050354 | -0.20142 | 0.022889 | 0.068664 | -0.21973 | -0.018311 | -0.086975 | 122.8271 | 122.8775 | 59.0378 | -122.937 | 122.8729 | 122.7631 | 59.1202 | -123.0515
598.5156 | 123.1384 | -59.0515 | 63.8168 | 0.22583 | 0.0047681 | 0.06545 | 0.069005 | 0.12827 | 0.00019875 | -0.0021469 | 0.23216 | -5.9768e-05 | -0.0021 | -0.001818 | 0.0013416 | -0.0045289 | 63.8351 | 63.9771 | -0.032043 | -59.2529 | 63.7527 | -59.1019 | -59.0973 | -58.9966 | 0.018311 | -59.3124 | 63.8031 | 63.707 | -59.1202 | -59.2529 | -0.050354 | -0.045776 | -0.064086 | 123.0286 | -0.20142 | -0.15564 | 0.018311 | -0.068664 | -0.20142 | -0.013732 | 0.054932 | -0.26093 | -0.059509 | -0.10986 | 122.8043 | 122.8867 | 59.0195 | -122.9141 | 122.8546 | 122.7585 | 59.0698 | -123.0698
599.5156 | 123.2025 | -59.0332 | 63.8168 | -0.018311 | 0.0060497 | 0.066945 | 0.069218 | 0.12892 | -0.00022865 | -0.0019333 | 0.041427 | -0.0036914 | -0.0025272 | 0.000532 | 0.00027337 | -0.0043153 | 63.8535 | 64.0045 | 0.054932 | -59.2163 | 63.8168 | -59.0836 | -59.0973 | -58.9462 | 0.13733 | -59.2346 | 63.8214 | 63.739 | -59.0927 | -59.2346 | -0.050354 | -0.064087 | 0 | 123.0377 | -0.18311 | -0.11902 | 0.036622 | -0.059509 | -0.20142 | 0.004578 | 0.086975 | -0.20142 | 0 | -0.077819 | 122.85 | 122.8867 | 59.0881 | -122.9141 | 122.8546 | 122.7722 | 59.1705 | -123.0515
600.5156 | 123.1522 | -59.0515 | 63.8031 | 0.14954 | 0.0081861 | 0.066731 | 0.066014 | 0.12635 | 0.0010532 | -0.0025741 | 0.23979 | -0.003905 | -0.0006046 | -0.0022452 | 0.00091437 | -0.0038879 | 63.8489 | 63.9862 | -0.018311 | -59.23 | 63.7711 | -59.0881 | -59.1202 | -58.96 | 0.041199 | -59.2804 | 63.7985 | 63.6932 | -59.1156 | -59.2667 | -0.036621 | -0.068664 | -0.032044 | 123.0377 | -0.17853 | -0.10986 | 0.045776 | -0.064087 | -0.21515 | -0.004578 | 0.091553 | -0.22888 | -0.013733 | -0.10986 | 122.8226 | 122.9004 | 59.0332 | -122.9233 | 122.85 | 122.7448 | 59.0927 | -123.0698
601.5156 | 123.1567 | -59.0698 | 63.8397 | 0.065613 | 0.0066907 | 0.069081 | 0.066655 | 0.12892 | -0.0030056 | -0.0021469 | 0.087204 | -0.0051868 | -0.003168 | 0.000532 | 0.0013416 | -0.0021789 | 63.8031 | 63.9862 | -0.009155 | -59.2438 | 63.7665 | -59.079 | -59.0973 | -58.9691 | 0.10071 | -59.2712 | 63.8397 | 63.7207 | -59.111 | -59.2392 | -0.009155 | -0.027466 | -0.073243 | 123.056 | -0.17395 | -0.14648 | -0.036621 | -0.041199 | -0.16937 | 0 | 0.10071 | -0.20142 | -0.032043 | -0.11902 | 122.8363 | 122.8729 | 59.0607 | -122.937 | 122.9095 | 122.7905 | 59.1705 | -123.0789
602.5156 | 123.1522 | -59.0652 | 63.8031 | 0.19531 | 0.0077587 | 0.066945 | 0.068791 | 0.1302 | 0.0012668 | -1.0724e-05 | 0.22453 | -0.0019824 | -0.0001774 | -0.001177 | 0.002196 | -0.0051697 | 63.8535 | 63.9908 | -0.027466 | -59.2392 | 63.7527 | -59.0652 | -59.1248 | -58.9691 | 0.032043 | -59.2804 | 63.8031 | 63.6887 | -59.111 | -59.2346 | 0 | -0.059509 | -0.050354 | 123.056 | -0.17395 | -0.11444 | 0.050354 | -0.045776 | -0.16937 | 0 | 0.096131 | -0.21515 | -0.045777 | -0.11444 | 122.818 | 122.9187 | 59.0378 | -122.9279 | 122.8683 | 122.7539 | 59.0973 | -123.0377
603.5156 | 123.1613 | -59.0515 | 63.8351 | 0.12665 | 0.0039135 | 0.067586 | 0.063023 | 0.12678 | -0.00086945 | -0.0057785 | 0.25505 | -0.004546 | -0.0023136 | -0.001818 | 0.0026234 | -0.0038879 | 64.0045 | 63.858 | -0.14648 | -59.2438 | 63.7894 | -59.0744 | -59.1156 | -59.0195 | 0.041199 | -59.2896 | 63.826 | 63.7161 | -59.1064 | -59.2484 | -0.022888 | -0.064087 | -0.045776 | 122.9095 | -0.19226 | -0.12817 | 0.16937 | -0.054931 | -0.19684 | -0.009155 | 0.032044 | -0.23804 | -0.041199 | -0.11902 | 122.8409 | 123.056 | 58.905 | -122.9507 | 122.8775 | 122.7676 | 59.0927 | -123.0835
604.5156 | 123.1934 | -59.0332 | 63.7848 | 0.38605 | 0.010322 | 0.066731 | 0.069005 | 0.13297 | 0.002335 | -0.0010787 | 0.20927 | -0.002196 | -0.0012454 | 0.0001046 | 0.0032642 | -0.0032471 | 63.8535 | 63.9908 | -0.009155 | -59.2346 | 63.7527 | -59.0927 | -59.1568 | -58.96 | 0.050354 | -59.2712 | 63.8123 | 63.6703 | -59.1064 | -59.2712 | -0.059509 | -0.1236 | -0.032043 | 123.024 | -0.20142 | -0.07782 | 0.068665 | -0.073242 | -0.23804 | 0.027466 | 0.073242 | -0.23804 | 0 | -0.11444 | 122.7859 | 122.8867 | 59.024 | -122.9416 | 122.8455 | 122.7036 | 59.0836 | -123.056
605.5156 | 123.1613 | -59.0286 | 63.826 | 1.5762 | 0.0051953 | 0.069295 | 0.0658 | 0.1287 | -0.0017238 | -0.0012923 | 0.087204 | -0.002196 | -0.0018862 | -0.0009634 | 0.0026234 | -0.0055969 | 63.8077 | 63.9496 | -0.054932 | -59.2621 | 63.8123 | -59.1019 | -59.1202 | -58.9874 | 0.059509 | -59.2804 | 63.8351 | 63.7482 | -59.1156 | -59.2484 | -0.073243 | -0.091553 | -0.013733 | 122.9782 | -0.23346 | -0.14191 | -0.018311 | -0.086976 | -0.21973 | 0.009155 | 0.041198 | -0.25177 | -0.032044 | -0.07782 | 122.8409 | 122.8363 | 58.9737 | -122.9462 | 122.8638 | 122.7768 | 59.0881 | -123.0743
606.5156 | 123.1796 | -59.0515 | 63.8031 | 0.17242 | 0.0083997 | 0.065022 | 0.069645 | 0.12934 | 0.0014804 | -0.00022432 | 0.27031 | -0.0034778 | -0.0021 | -0.0009634 | 0.002837 | -0.0030335 | 63.8763 | 63.9725 | -0.013733 | -59.23 | 63.7527 | -59.1064 | -59.1202 | -58.9645 | 0.041199 | -59.2621 | 63.8031 | 63.6841 | -59.1248 | -59.2392 | -0.054931 | -0.068664 | -0.050354 | 123.024 | -0.17853 | -0.10986 | 0.073242 | -0.073242 | -0.18768 | 0 | 0.086975 | -0.21057 | -0.022888 | -0.11902 | 122.8043 | 122.9279 | 59.0378 | -122.9233 | 122.8546 | 122.7356 | 59.0927 | -123.0423
607.5156 | 123.0789 | -59.0652 | 63.8168 | 0.14191 | 0.0054089 | 0.07079 | 0.068364 | 0.12892 | 0.00083955 | -1.0724e-05 | 0.17876 | -0.0032642 | -0.004877 | -0.0022452 | 0.0015552 | -0.0034607 | 63.826 | 63.9542 | -0.050354 | -59.2575 | 63.7894 | -59.0698 | -59.1248 | -58.992 | 0.045776 | -59.2941 | 63.8351 | 63.7482 | -59.0927 | -59.2209 | -0.004577 | -0.059509 | -0.027465 | 123.0194 | -0.19226 | -0.13275 | 0.009156 | -0.027465 | -0.15564 | 0.018311 | 0.073243 | -0.22888 | -0.073242 | -0.068664 | 122.8546 | 122.8912 | 59.0149 | -122.9416 | 122.9004 | 122.8134 | 59.111 | -123.0377
608.5156 | 123.1567 | -59.0561 | 63.8077 | 0.21057 | 0.010322 | 0.065663 | 0.069218 | 0.12892 | 0.0044712 | 0.00041648 | 0.20164 | -0.0015552 | -0.0006046 | -0.000109 | 0.0030506 | -0.0049561 | 63.826 | 63.9038 | -0.11444 | -59.285 | 63.8031 | -59.1293 | -59.166 | -58.992 | 0.004578 | -59.3079 | 63.8168 | 63.7115 | -59.1431 | -59.2346 | -0.073242 | -0.10986 | -0.004577 | 122.9599 | -0.22888 | -0.11902 | 0.018311 | -0.086975 | -0.17853 | 0.009155 | 0.064087 | -0.25177 | -0.073242 | -0.09613 | 122.8592 | 122.8821 | 58.9417 | -122.9736 | 122.8729 | 122.7676 | 59.0607 | -123.0423
609.5156 | 123.1613 | -59.0469 | 63.8443 | 0.16479 | 0.0071179 | 0.066091 | 0.0658 | 0.12678 | -0.001083 | -0.0021469 | 0.28557 | -0.001128 | -0.001459 | -0.0016044 | 5.9768e-05 | -0.0034607 | 63.8489 | 63.9633 | -0.032043 | -59.2575 | 63.7436 | -59.0881 | -59.1156 | -58.9828 | 0.022888 | -59.2896 | 63.7985 | 63.7299 | -59.1202 | -59.2392 | -0.041199 | -0.068665 | -0.10071 | 123.0103 | -0.21057 | -0.14191 | 0.004578 | -0.073242 | -0.19226 | -0.045776 | 0.064087 | -0.24262 | -0.050354 | -0.11444 | 122.7905 | 122.8958 | 59.0149 | -122.9599 | 122.8455 | 122.7768 | 59.0698 | -123.0835
610.5156 | 123.1522 | -59.0469 | 63.8077 | 0.23346 | 0.0079723 | 0.066518 | 0.070073 | 0.13148 | 0.0046848 | -0.0012923 | 0.30083 | -0.0032642 | -0.0023136 | -0.0007498 | 0.0041186 | -0.0030335 | 63.8351 | 63.913 | -0.068665 | -59.2484 | 63.8123 | -59.079 | -59.1476 | -58.9691 | 0.022888 | -59.285 | 63.8443 | 63.739 | -59.1339 | -59.2529 | -0.032043 | -0.10071 | 0.004578 | 122.9599 | -0.20142 | -0.10071 | 0.027466 | -0.086975 | -0.20599 | 0.036621 | 0.07782 | -0.23804 | -0.032043 | -0.068664 | 122.8592 | 122.8821 | 58.9783 | -122.9553 | 122.8912 | 122.7859 | 59.0698 | -123.0606
611.5156 | 123.1384 | -59.079 | 63.7985 | 0.19531 | 0.0094677 | 0.066518 | 0.068364 | 0.1302 | -0.0023648 | -0.0010787 | 0.22453 | -0.003905 | -0.0025272 | -0.0026724 | 0.0032642 | -0.0030335 | 63.8535 | 63.9862 | -0.018311 | -59.2438 | 63.7527 | -59.0973 | -59.1064 | -58.9462 | 0.045776 | -59.2621 | 63.8031 | 63.707 | -59.1385 | -59.2392 | -0.018311 | -0.027466 | -0.045776 | 123.0652 | -0.1648 | -0.13733 | 0.054932 | -0.05951 | -0.16022 | 0.004578 | 0.13275 | -0.18311 | -0.022888 | -0.091553 | 122.8317 | 122.9324 | 59.0607 | -122.905 | 122.8821 | 122.7859 | 59.1248 | -123.0377
612.5156 | 123.1247 | -59.079 | 63.8123 | 0.21057 | 0.01139 | 0.068227 | 0.069859 | 0.12934 | 0.0042576 | 0.0012711 | 0.22453 | -0.00070077 | 0.00025 | -0.0030996 | 0.002196 | -0.0064515 | 63.8077 | 63.8672 | -0.11902 | -59.2941 | 63.826 | -59.1064 | -59.1385 | -59.0378 | -0.027466 | -59.3491 | 63.826 | 63.7436 | -59.1339 | -59.2529 | -0.027466 | -0.05951 | 0.013733 | 122.9462 | -0.21515 | -0.15564 | -0.004578 | -0.054932 | -0.17395 | 0.013733 | 0.041198 | -0.27008 | -0.09613 | -0.068665 | 122.905 | 122.8867 | 58.96 | -122.9507 | 122.905 | 122.8226 | 59.0515 | -123.0652
613.5156 | 123.1705 | -59.0469 | 63.8214 | 0.17242 | 0.0062635 | 0.068227 | 0.066868 | 0.12827 | -0.0038602 | -1.0724e-05 | 0.2169 | -0.0015552 | -0.0044498 | -0.0016044 | -0.0010082 | -0.0026063 | 63.8168 | 63.9313 | -0.059509 | -59.2804 | 63.7894 | -59.0469 | -59.1156 | -58.9966 | 0.032043 | -59.2896 | 63.8077 | 63.7665 | -59.1156 | -59.2484 | 0 | -0.068665 | -0.032043 | 122.9782 | -0.23346 | -0.1648 | -0.004578 | -0.068665 | -0.20142 | -0.013733 | 0.050354 | -0.24262 | -0.041199 | -0.054932 | 122.8363 | 122.8638 | 58.9874 | -122.937 | 122.8546 | 122.8134 | 59.079 | -123.0698
614.5156 | 123.0835 | -59.079 | 63.8443 | 0.32501 | 0.010963 | 0.066091 | 0.069218 | 0.13062 | 0.003403 | -0.0015061 | 0.18639 | -0.0024096 | -0.0006046 | 0.0003182 | 0.003905 | -0.0028199 | 63.7848 | 63.8351 | -0.12817 | -59.3033 | 63.8214 | -59.1339 | -59.1568 | -59.0607 | -0.073242 | -59.3674 | 63.8626 | 63.7665 | -59.1568 | -59.2529 | -0.054932 | -0.07782 | -0.022888 | 122.9141 | -0.22431 | -0.14648 | -0.059509 | -0.07782 | -0.17395 | 0.018311 | 0.01831 | -0.28839 | -0.11444 | -0.07782 | 122.9004 | 122.8638 | 58.9508 | -123.0011 | 122.9416 | 122.8455 | 59.0057 | -123.0972
615.5156 | 123.1796 | -59.0378 | 63.7985 | -0.033569 | 0.0092541 | 0.066091 | 0.064946 | 0.12977 | -0.00065585 | 0.0016983 | 0.20164 | -0.0017688 | -0.0027408 | -0.001818 | 0.0051868 | -0.0034607 | 63.8397 | 63.9679 | -0.018311 | -59.2255 | 63.7665 | -59.0836 | -59.1339 | -58.9645 | 0.041199 | -59.2575 | 63.7939 | 63.7115 | -59.1385 | -59.2392 | -0.045776 | -0.09613 | -0.032044 | 123.0057 | -0.18768 | -0.091553 | 0.041199 | -0.10071 | -0.20142 | -0.004578 | 0.073242 | -0.21973 | -0.01831 | -0.086975 | 122.8043 | 122.8775 | 59.0195 | -122.9324 | 122.8317 | 122.7493 | 59.079 | -123.0377
616.5156 | 123.0835 | -59.0836 | 63.8489 | 0.13428 | 0.0096813 | 0.067372 | 0.068577 | 0.13084 | 0.0014804 | 0.0012711 | 0.2169 | -0.002196 | -0.0012454 | -0.000109 | 0.002196 | -0.0041017 | 63.7848 | 63.8306 | -0.14191 | -59.3079 | 63.8168 | -59.1293 | -59.1568 | -59.0607 | -0.064087 | -59.3582 | 63.8763 | 63.7665 | -59.1568 | -59.2621 | -0.045776 | -0.073242 | -0.032044 | 122.9141 | -0.2243 | -0.15106 | -0.064087 | -0.073242 | -0.17853 | 0.027466 | 0.022888 | -0.27466 | -0.09613 | -0.082398 | 122.9004 | 122.8683 | 58.9416 | -123.0057 | 122.9599 | 122.85 | 59.0195 | -123.111
617.5156 | 123.2117 | -59.024 | 63.8123 | 0.16479 | 0.010536 | 0.066731 | 0.068577 | 0.13105 | -0.00022865 | -0.0021469 | 0.27031 | -0.0015552 | -0.0027408 | -0.001177 | 0.0030506 | -0.0034607 | 63.8443 | 63.9542 | -0.036621 | -59.23 | 63.7665 | -59.1019 | -59.1293 | -58.9874 | -0.21973 | -59.1797 | 63.7665 | 63.7207 | -59.111 | -59.2392 | -0.07782 | -0.10529 | -0.045777 | 122.9782 | -0.20599 | -0.10071 | 0.032043 | -0.086975 | -0.21515 | -0.045777 | 0.036621 | -0.15564 | 0.05951 | -0.091553 | 122.7905 | 122.8683 | 58.9874 | -122.9416 | 122.7905 | 122.7448 | 58.8043 | -123.0515
618.5156 | 123.0606 | -59.0927 | 63.8351 | 0.073242 | 0.0098951 | 0.0631 | 0.069859 | 0.1302 | 0.0048984 | 0.0057571 | 0.46867 | 0.00079463 | -0.0008182 | -0.002886 | 0.0024096 | -0.0043153 | 63.3774 | 63.7619 | -0.018311 | -59.1293 | 63.826 | -59.0881 | -59.1568 | -59.079 | -0.068665 | -59.404 | 63.8489 | 63.7894 | -59.1385 | -59.2896 | 0.004577 | -0.064087 | -0.009155 | 122.8546 | -0.036621 | 0.027466 | -0.45776 | -0.045777 | -0.19684 | 0.013733 | 0.013733 | -0.31128 | -0.11444 | -0.045776 | 122.9187 | 122.4701 | 59.0744 | -122.9919 | 122.9416 | 122.8821 | 59.024 | -123.1247
619.5156 | 123.143 | -59.0744 | 63.7985 | 0.21057 | 0.0096813 | 0.066304 | 0.067509 | 0.13319 | 0.00062595 | -1.0724e-05 | 0.26268 | -0.0019824 | -0.0023136 | -0.0016044 | 0.0015552 | -0.0021789 | 63.7848 | 63.8718 | -0.10071 | -59.2804 | 63.8031 | -59.1064 | -59.1476 | -59.0103 | -0.013733 | -59.3079 | 63.8489 | 63.7482 | -59.166 | -59.2712 | -0.032043 | -0.073242 | 0.004578 | 122.9462 | -0.20599 | -0.13275 | -0.013733 | -0.091553 | -0.19684 | 0.050354 | 0.064087 | -0.23346 | -0.036621 | -0.050354 | 122.8775 | 122.8592 | 58.9737 | -122.9462 | 122.9233 | 122.8226 | 59.0607 | -123.0698
620.5156 | 123.0698 | -59.1156 | 63.8306 | -1.9638 | 0.012886 | 0.066091 | 0.070073 | 0.12721 | 0.002335 | 0.0010575 | 0.17876 | -0.00070077 | -0.0006046 | 0.0001046 | 0.0034778 | -0.0028199 | 63.7482 | 63.8535 | -0.11902 | -59.3308 | 63.826 | -59.1293 | -59.1339 | -59.0515 | -0.073242 | -59.3857 | 63.8397 | 63.7985 | -59.1568 | -59.2896 | -0.013732 | -0.01831 | -0.004577 | 122.9691 | -0.21515 | -0.19684 | -0.082397 | -0.041198 | -0.17395 | 0.009156 | 0.064087 | -0.27008 | -0.09613 | -0.032043 | 122.9416 | 122.8638 | 58.9966 | -122.9645 | 122.9553 | 122.9141 | 59.0424 | -123.1201
621.5156 | 123.0972 | -59.0881 | 63.8535 | 0.14191 | 0.011177 | 0.0631 | 0.06815 | 0.12827 | 0.0027622 | -0.00043792 | 0.23979 | -0.0026234 | -0.001459 | -0.0009634 | 0.0015552 | -0.0023927 | 63.7756 | 63.826 | -0.14648 | -59.2941 | 63.8306 | -59.1156 | -59.1431 | -59.0561 | -0.068665 | -59.3674 | 63.8535 | 63.7939 | -59.1797 | -59.285 | -0.027466 | -0.054931 | -0.022889 | 122.9141 | -0.20599 | -0.15106 | -0.07782 | -0.091552 | -0.19684 | 0 | 0.032044 | -0.27924 | -0.082398 | -0.05951 | 122.9187 | 122.8638 | 58.9417 | -122.9965 | 122.9416 | 122.8821 | 59.0195 | -123.1384
622.5156 | 123.0698 | -59.079 | 63.858 | -0.0030518 | 0.014808 | 0.06545 | 0.067723 | 0.13084 | 0.0021214 | 0.0010575 | 0.049057 | -0.0032642 | -0.0001774 | -0.0005362 | 0.004546 | -0.0021789 | 63.8077 | 63.8855 | -0.064087 | -59.2712 | 63.8168 | -59.1019 | -59.1202 | -59.0515 | 0.013733 | -59.3582 | 63.858 | 63.7939 | -59.1385 | -59.285 | -0.022889 | -0.041199 | -0.041199 | 122.9645 | -0.19226 | -0.15106 | -0.050354 | -0.05951 | -0.20599 | 0 | 0.027465 | -0.27924 | -0.073242 | -0.064087 | 122.8958 | 122.8867 | 59.0149 | -122.9782 | 122.937 | 122.8729 | 59.0927 | -123.143
623.5156 | 123.1201 | -59.0744 | 63.8077 | 0.15717 | 0.0096813 | 0.067586 | 0.067509 | 0.12827 | -0.00044225 | -0.00086512 | 0.27031 | -0.0034778 | -0.0008182 | -0.0013906 | 0.002837 | -0.0021789 | 63.7573 | 63.826 | -0.13275 | -59.3033 | 63.8351 | -59.1064 | -59.111 | -59.0561 | -0.045776 | -59.3399 | 63.8626 | 63.7527 | -59.1385 | -59.2529 | -0.032043 | -0.036621 | 0.027466 | 122.9004 | -0.22888 | -0.19226 | -0.050354 | -0.064087 | -0.17853 | 0.054932 | 0.018311 | -0.2655 | -0.086975 | -0.054931 | 122.9095 | 122.8317 | 58.9417 | -122.9187 | 122.937 | 122.8271 | 59.0286 | -123.0606
624.5156 | 123.0652 | -59.0881 | 63.8809 | 0.035095 | 0.013954 | 0.066731 | 0.068791 | 0.1287 | 0.003403 | 0.00041648 | 0.064316 | -5.9768e-05 | -0.0001774 | -0.0016044 | 0.002196 | -0.0053833 | 63.7939 | 63.8809 | -0.068665 | -59.2621 | 63.8214 | -59.0698 | -59.1614 | -59.0881 | -0.018311 | -59.3628 | 63.8535 | 63.8031 | -59.1476 | -59.2758 | 0.018311 | -0.073242 | -0.059509 | 122.9691 | -0.17395 | -0.10071 | -0.086975 | -0.059509 | -0.18768 | -0.027465 | 0 | -0.27466 | -0.086975 | -0.077819 | 122.9095 | 122.8821 | 59.0195 | -123.0423 | 122.9416 | 122.8912 | 59.0698 | -123.1567
625.5312 | 123.0698 | -59.0698 | 63.8992 | 1.1719 | 0.0079723 | 0.068013 | 0.070073 | 0.12977 | -0.0017238 | -0.0040695 | -0.050125 | -0.00091437 | 0.00025 | 0.000532 | -0.00058103 | -0.0041017 | 63.7894 | 63.8535 | -0.032043 | -59.2712 | 63.8489 | -59.0927 | -59.111 | -59.0652 | 0.054932 | -59.3124 | 63.8855 | 63.8397 | -59.1431 | -59.2392 | -0.022888 | -0.041199 | -0.050354 | 122.9233 | -0.20142 | -0.16022 | -0.10986 | -0.073242 | -0.16937 | -0.013733 | 0.004577 | -0.24262 | -0.073242 | -0.059509 | 122.9187 | 122.8592 | 59.0378 | -123.0103 | 122.9553 | 122.9095 | 59.1248 | -123.1384
626.5156 | 123.111 | -59.079 | 63.858 | -0.02594 | 0.014595 | 0.066945 | 0.069645 | 0.12806 | 0.0025486 | 0.00084388 | 0.041427 | -0.001128 | 0.0008908 | -0.0007498 | 0.002837 | -0.0055969 | 63.8123 | 63.9221 | -0.036621 | -59.2438 | 63.8031 | -59.0927 | -59.1156 | -59.0424 | 0.045776 | -59.3445 | 63.8809 | 63.7894 | -59.1568 | -59.2667 | -0.013733 | -0.036622 | -0.054931 | 123.0011 | -0.1648 | -0.12817 | -0.045776 | -0.07782 | -0.18768 | 0.022888 | 0.036621 | -0.2655 | -0.077819 | -0.068664 | 122.8821 | 122.8912 | 59.0424 | -122.9736 | 122.9599 | 122.8683 | 59.1248 | -123.1247
627.5156 | 123.0743 | -59.0927 | 63.858 | 0.24109 | 0.013527 | 0.066518 | 0.067936 | 0.13041 | 0.001694 | -0.00086512 | 0.23979 | -0.0013416 | -0.0012454 | -0.000109 | 0.00091437 | -0.0026063 | 63.7344 | 63.8397 | -0.13275 | -59.2896 | 63.8306 | -59.1293 | -59.1431 | -59.0881 | -0.068665 | -59.3674 | 63.858 | 63.7802 | -59.1431 | -59.2758 | -0.036621 | -0.050354 | -0.027466 | 122.9324 | -0.19684 | -0.14649 | -0.1236 | -0.050354 | -0.18311 | 0 | 0.004577 | -0.27466 | -0.091553 | -0.07782 | 122.9233 | 122.8271 | 58.96 | -123.0011 | 122.9507 | 122.8729 | 59.024 | -123.1338
628.5156 | 123.1293 | -59.0607 | 63.8718 | -0.033569 | 0.011818 | 0.066731 | 0.070073 | 0.12913 | 0.00083955 | -0.0027877 | -0.027237 | -0.00091437 | 0.0021726 | 0.0001046 | 0.0032642 | -0.0026063 | 63.9038 | 63.8992 | -0.041199 | -59.2026 | 63.8397 | -59.079 | -59.1431 | -59.0149 | 0.07782 | -59.317 | 63.8672 | 63.7802 | -59.1431 | -59.2621 | -0.01831 | -0.082397 | -0.032043 | 122.9599 | -0.14191 | -0.05951 | 0.032044 | -0.082397 | -0.20142 | -0.004578 | 0.045776 | -0.25635 | -0.054932 | -0.091553 | 122.9004 | 122.9645 | 59.0195 | -123.0148 | 122.9279 | 122.8409 | 59.1385 | -123.1338
629.5156 | 123.0698 | -59.1019 | 63.8397 | 0.080872 | 0.013099 | 0.064809 | 0.067936 | 0.1302 | 0.0014804 | -0.00022432 | 0.10246 | -0.0047596 | 0.0006772 | 0.0016 | 0.0034778 | -0.0032471 | 63.7848 | 63.8763 | -0.09613 | -59.2667 | 63.826 | -59.0973 | -59.1293 | -59.0836 | -0.045776 | -59.3719 | 63.8718 | 63.7985 | -59.1614 | -59.285 | 0.004578 | -0.027465 | -0.013733 | 122.9782 | -0.16479 | -0.13733 | -0.054932 | -0.059509 | -0.1831 | 0.032043 | 0.018311 | -0.27008 | -0.086975 | -0.041199 | 122.9279 | 122.8867 | 59.0057 | -122.9691 | 122.9736 | 122.9004 | 59.0561 | -123.1247
630.5156 | 123.0835 | -59.0927 | 63.8672 | 0.027466 | 0.012672 | 0.068868 | 0.068577 | 0.1287 | 0.00041235 | -0.0021469 | 0.01091 | -0.001128 | 0.00025 | 0.000532 | 0.0041186 | -0.0019653 | 63.8397 | 63.9313 | -0.013733 | -59.2255 | 63.8397 | -59.0973 | -59.1248 | -59.024 | 0.054932 | -59.3124 | 63.8489 | 63.7802 | -59.1339 | -59.2392 | -0.004578 | -0.032044 | -0.027465 | 123.024 | -0.13275 | -0.10071 | -0.027465 | -0.041199 | -0.14648 | -0.01831 | 0.068664 | -0.21973 | -0.073242 | -0.086975 | 122.9324 | 122.9324 | 59.079 | -122.9919 | 122.9416 | 122.8729 | 59.1476 | -123.1064
631.5156 | 123.1476 | -59.0881 | 63.7573 | 0.18768 | 0.010963 | 0.066091 | 0.066655 | 0.12998 | -0.0025784 | -0.0010787 | 0.31609 | -0.001128 | -0.0018862 | -0.0007498 | 0.00091437 | -0.0036743 | 63.7985 | 63.9313 | -0.054932 | -59.2484 | 63.7619 | -59.1019 | -59.1339 | -59.0057 | 0.022888 | -59.2804 | 63.8077 | 63.7436 | -59.1431 | -59.2529 | -0.013733 | -0.045776 | 0.004578 | 123.0194 | -0.16022 | -0.11444 | 0.041199 | -0.054931 | -0.16479 | 0.050354 | 0.082398 | -0.19226 | -0.027466 | -0.013733 | 122.85 | 122.8867 | 59.0332 | -122.8912 | 122.8958 | 122.8317 | 59.111 | -123.0103
632.5156 | 123.0881 | -59.0424 | 63.8763 | -0.094604 | 0.012459 | 0.064595 | 0.068791 | 0.1302 | 0.0012668 | -0.0010787 | -0.0043486 | -0.0036914 | 3.6404e-05 | -0.0005362 | 0.0024096 | -0.0015381 | 63.8077 | 63.9496 | 0 | -59.2438 | 63.8443 | -59.0698 | -59.1248 | -59.111 | -0.059509 | -59.2072 | 63.8626 | 63.8077 | -59.1339 | -59.2529 | -0.027466 | -0.082398 | -0.032044 | 122.9919 | -0.20142 | -0.11902 | -0.068665 | -0.091553 | -0.21057 | -0.013733 | -0.068665 | -0.16479 | 0.045777 | -0.068665 | 122.8867 | 122.85 | 59.0424 | -123.0011 | 122.905 | 122.85 | 58.9828 | -123.1293
633.5156 | 123.056 | -59.1019 | 63.8443 | 0.057983 | 0.014808 | 0.066945 | 0.065373 | 0.12892 | 0.0021214 | -0.0027877 | 0.094833 | -0.002196 | 0.0025998 | 0.0001046 | 0.0017688 | -0.0030335 | 63.7802 | 63.8763 | -0.068665 | -59.2758 | 63.8031 | -59.1019 | -59.1248 | -59.0744 | -0.009155 | -59.3582 | 63.858 | 63.8168 | -59.166 | -59.2758 | 0 | -0.022888 | -0.041198 | 122.9782 | -0.17395 | -0.15106 | -0.064087 | -0.064087 | -0.17395 | 0.013733 | 0.027466 | -0.25635 | -0.082397 | -0.027466 | 122.905 | 122.8821 | 59.0332 | -122.9691 | 122.9599 | 122.9187 | 59.0927 | -123.1201
634.5156 | 123.1201 | -59.0836 | 63.858 | -0.048828 | 0.012031 | 0.066518 | 0.070073 | 0.12956 | 0.0038304 | 0.0029801 | -0.3019 | -5.9768e-05 | -0.0006046 | 0.0003182 | -0.00036743 | -0.0055969 | 63.7161 | 63.7802 | -0.091553 | -59.166 | 63.8168 | -59.0881 | -59.1202 | -59.0332 | 0.082397 | -59.3124 | 63.858 | 63.8031 | -59.1431 | -59.2667 | -0.004578 | -0.036621 | -0.041199 | 122.8638 | -0.082398 | -0.045777 | -0.14191 | -0.059509 | -0.18311 | 0 | 0.050354 | -0.22888 | -0.045776 | -0.054931 | 122.9004 | 122.7997 | 58.992 | -122.9782 | 122.9416 | 122.8867 | 59.166 | -123.1247
635.5156 | 123.0469 | -59.1019 | 63.8672 | -0.033569 | 0.013954 | 0.064809 | 0.069645 | 0.13319 | 0.0012668 | -0.0021469 | 0.064316 | -0.0032642 | -0.0001774 | 0.000532 | 0.002837 | -0.0026063 | 63.8123 | 63.9175 | -0.032043 | -59.2392 | 63.7894 | -59.0836 | -59.1339 | -59.0195 | 0.027466 | -59.3399 | 63.8763 | 63.7939 | -59.1385 | -59.2621 | 0.018311 | -0.032043 | -0.077819 | 123.0194 | -0.13733 | -0.10529 | -0.054931 | -0.036621 | -0.16022 | 0.009156 | 0.082398 | -0.23804 | -0.07782 | -0.073242 | 122.8912 | 122.9141 | 59.0698 | -123.0011 | 122.9782 | 122.8958 | 59.1293 | -123.1293
636.5156 | 123.1979 | -59.0652 | 63.7894 | 0.18768 | 0.012886 | 0.069936 | 0.067723 | 0.12934 | -0.0012966 | -0.0019333 | -0.69862 | -0.0017688 | -0.0027408 | -0.0013906 | 0.0013416 | -0.0030335 | 63.8214 | 63.9587 | -0.050354 | -59.2117 | 63.7527 | -59.079 | -59.1522 | -58.9737 | 0.022888 | -59.2438 | 63.8031 | 63.739 | -59.1064 | -59.2484 | -0.013732 | -0.086975 | -0.036621 | 123.024 | -0.14648 | -0.059509 | 0.032043 | -0.041198 | -0.1831 | 0.013733 | 0.091553 | -0.17853 | 0.004578 | -0.050354 | 122.818 | 122.8867 | 59.0149 | -122.9416 | 122.8683 | 122.8043 | 59.0881 | -123.0377
637.5156 | 123.0286 | -59.0698 | 63.858 | 0.0045777 | 0.015022 | 0.066518 | 0.068791 | 0.12892 | 0.0031894 | -0.0027877 | 0.11009 | -0.0019824 | 0.0006772 | -0.0026724 | 0.0015552 | -0.0053833 | 63.7756 | 63.8351 | -0.11444 | -59.285 | 63.8214 | -59.1019 | -59.1476 | -59.1293 | -0.068665 | -59.404 | 63.8626 | 63.8214 | -59.1522 | -59.2621 | -0.032044 | -0.07782 | -0.036621 | 122.905 | -0.21515 | -0.13733 | -0.082397 | -0.082398 | -0.19226 | 0.004578 | -0.059509 | -0.33417 | -0.14191 | -0.036621 | 122.8912 | 122.8455 | 58.9554 | -123.0057 | 122.9324 | 122.8912 | 59.0012 | -123.1201
638.5156 | 123.1979 | -59.0561 | 63.8031 | 0.51575 | 0.0094677 | 0.064809 | 0.068791 | 0.12892 | -0.0030056 | -0.0010787 | 0.33134 | -0.0036914 | 3.6404e-05 | -0.002886 | 0.001128 | -0.0030335 | 63.8672 | 63.9496 | -0.041199 | -59.2392 | 63.7756 | -59.079 | -59.1476 | -58.9966 | 0.045776 | -59.2667 | 63.8168 | 63.7436 | -59.1019 | -59.2484 | -0.022888 | -0.091553 | -0.027466 | 123.0057 | -0.18311 | -0.091553 | 0.064086 | -0.045777 | -0.19226 | 0.013732 | 0.059509 | -0.21057 | -0.018311 | -0.05951 | 122.8317 | 122.9233 | 59.0149 | -122.9507 | 122.8729 | 122.7997 | 59.1019 | -123.0515
639.5156 | 123.1155 | -59.0973 | 63.8535 | -0.056458 | 0.013313 | 0.068654 | 0.06815 | 0.12956 | 0.0019078 | -0.0019333 | 0.033798 | -0.001128 | 0.0015316 | -0.0003226 | 0.0030506 | -0.0038879 | 63.8397 | 63.913 | -0.032043 | -59.2392 | 63.8031 | -59.0744 | -59.1248 | -59.0515 | 0.032043 | -59.3308 | 63.8535 | 63.7985 | -59.1568 | -59.2484 | 0.022888 | -0.027466 | -0.050354 | 123.0103 | -0.14191 | -0.11444 | -0.013733 | -0.059509 | -0.15106 | 0 | 0.045776 | -0.23346 | -0.082398 | -0.054932 | 122.9004 | 122.937 | 59.0652 | -122.9782 | 122.9507 | 122.8958 | 59.1293 | -123.1018
640.5312 | 123.0927 | -59.0744 | 63.8718 | -0.094604 | 0.012459 | 0.064809 | 0.069005 | 0.13191 | 0.0014804 | 0.00063028 | 0.056686 | -0.002196 | 0.0023862 | -0.002886 | 0.0013416 | -0.0019653 | 63.8306 | 63.913 | -0.018311 | -59.2438 | 63.8351 | -59.111 | -59.1293 | -59.0378 | 0.14191 | -59.3216 | 63.8626 | 63.7894 | -59.1202 | -59.2438 | -0.036621 | -0.054931 | -0.036621 | 122.9874 | -0.16937 | -0.11444 | -0.041199 | -0.045776 | -0.16937 | -0.009155 | 0.036621 | -0.24719 | -0.07782 | -0.082397 | 122.9095 | 122.905 | 59.0561 | -123.0011 | 122.937 | 122.8638 | 59.2163 | -123.1155
641.5156 | 123.1796 | -59.0332 | 63.8397 | 0.019836 | 0.0073315 | -0.034312 | 0.065587 | 0.1287 | -0.0036464 | -0.0034287 | 0.23979 | -0.0030506 | -0.0023136 | -0.0003226 | -0.00036743 | -0.0019653 | 63.7573 | 63.9496 | -0.022888 | -59.2575 | 63.7939 | -59.0744 | -59.1202 | -59.0286 | 0.054932 | -59.2804 | 63.8397 | 63.7894 | -59.1248 | -59.2438 | -0.041199 | -0.086975 | -0.045777 | 122.9828 | -0.2243 | -0.13733 | -0.082398 | -0.091553 | -0.21057 | 0 | 0.004578 | -0.24719 | -0.036622 | -0.050354 | 122.8271 | 122.7905 | 59.0103 | -122.9599 | 122.8729 | 122.8226 | 59.0881 | -123.0835
642.5156 | 123.0743 | -59.0561 | 63.8855 | -0.15564 | 0.0092541 | 0.067159 | 0.069005 | 0.12934 | -0.0012966 | -0.0023605 | -0.13405 | -0.0032642 | 0.0011044 | -0.0022452 | 0.0017688 | -0.0047425 | 63.7894 | 63.8809 | -0.054932 | -59.2575 | 63.8672 | -59.1019 | -59.1202 | -59.0607 | 0.050354 | -59.3491 | 63.9084 | 63.8214 | -59.1431 | -59.2392 | -0.045777 | -0.064087 | -0.018311 | 122.937 | -0.20142 | -0.13733 | -0.09613 | -0.086975 | -0.18311 | 0.022888 | -0.004578 | -0.29297 | -0.10986 | -0.064087 | 122.9233 | 122.8455 | 59.0012 | -123.0057 | 122.9645 | 122.8775 | 59.1064 | -123.1247
643.5156 | 123.0423 | -59.1202 | 63.8672 | 0.065613 | 0.011818 | 0.066731 | 0.069432 | 0.12913 | 0.0031894 | -0.0012923 | 0.11009 | -0.003905 | 0.0008908 | -0.001177 | 0.0032642 | -0.0034607 | 63.7802 | 63.8626 | -0.10071 | -59.2712 | 63.8306 | -59.0927 | -59.1431 | -59.0836 | -0.036621 | -59.3857 | 63.8626 | 63.7619 | -59.166 | -59.2667 | 0.027466 | -0.022888 | -0.036621 | 122.9828 | -0.15106 | -0.12817 | -0.086975 | -0.045777 | -0.14648 | -0.004577 | 0.036621 | -0.2655 | -0.11902 | -0.10529 | 122.9507 | 122.9004 | 59.0195 | -123.0103 | 122.9828 | 122.8821 | 59.0836 | -123.1338
644.5156 | 123.0881 | -59.0607 | 63.8901 | -0.14801 | 0.0066907 | 0.071004 | 0.067936 | 0.13255 | -0.00044225 | -0.0025741 | -0.088272 | -0.0024096 | -0.001459 | -0.0009634 | 0.00070077 | -0.0030335 | 63.7848 | 63.8947 | -0.036621 | -59.2529 | 63.858 | -59.0698 | -59.1202 | -59.0515 | 0.054932 | -59.317 | 63.8809 | 63.8351 | -59.1156 | -59.23 | -0.009155 | -0.059509 | -0.032044 | 122.9553 | -0.19226 | -0.13275 | -0.10529 | -0.054932 | -0.16937 | -0.009156 | 0.009155 | -0.25635 | -0.086975 | -0.054932 | 122.9187 | 122.8455 | 59.024 | -123.0103 | 122.9416 | 122.8958 | 59.1156 | -123.1201
645.5156 | 123.0606 | -59.0698 | 63.858 | -0.20142 | 0.014808 | 0.069081 | 0.06815 | 0.13041 | 0.0019078 | -0.0010787 | 0.087204 | -0.0017688 | 0.0034542 | -0.0009634 | 0.0015552 | -0.0015381 | 63.8351 | 63.9175 | -0.018311 | -59.2346 | 63.8168 | -59.0927 | -59.1202 | -59.0195 | 0.041199 | -59.3216 | 63.8443 | 63.8077 | -59.1431 | -59.2621 | -0.022888 | -0.050354 | -0.041199 | 122.9874 | -0.1648 | -0.11444 | -0.022888 | -0.073242 | -0.19226 | -0.013733 | 0.050354 | -0.25177 | -0.059509 | -0.050354 | 122.8867 | 122.905 | 59.0515 | -122.9782 | 122.9141 | 122.8775 | 59.111 | -123.1201
646.5312 | 123.1522 | -59.0744 | 63.8397 | 0.15717 | 0.0056225 | 0.025289 | 0.066441 | 0.12956 | -0.0032192 | -0.0023605 | 0.24742 | -0.0043324 | -0.0033816 | -0.002886 | -0.0046398 | -0.0011109 | 63.7711 | 64.151 | 0.11902 | -59.1202 | 63.826 | -59.0607 | -59.1019 | -59.0378 | 0.032043 | -59.285 | 63.8077 | 63.7527 | -59.1385 | -59.2346 | 0.013733 | -0.027466 | -0.013733 | 123.2254 | -0.045776 | -0.01831 | -0.068665 | -0.064087 | -0.16022 | -0.032044 | 0.036621 | -0.21057 | -0.050354 | -0.086975 | 122.9004 | 122.8455 | 59.1934 | -122.9416 | 122.8821 | 122.8271 | 59.1064 | -123.0743
647.5156 | 123.0743 | -59.079 | 63.8718 | 0.012207 | 0.013527 | 0.066945 | 0.071141 | 0.13126 | 0.0025486 | -0.0010787 | 0.087204 | -0.0024096 | 0.0011044 | -0.001818 | 0.0041186 | -0.0036743 | 63.8214 | 63.8992 | -0.036621 | -59.2575 | 63.8535 | -59.0973 | -59.1202 | -59.0607 | -0.004578 | -59.3536 | 63.8672 | 63.8123 | -59.1156 | -59.2667 | -0.018311 | -0.041199 | -0.01831 | 122.9782 | -0.17853 | -0.13733 | -0.050354 | -0.036622 | -0.18768 | -0.004578 | 0.01831 | -0.27466 | -0.086975 | -0.059509 | 122.9324 | 122.9004 | 59.0424 | -122.9919 | 122.9462 | 122.8912 | 59.0744 | -123.1384
648.5156 | 123.0423 | -59.0652 | 63.858 | 2.9953 | 0.010536 | 0.069936 | 0.069218 | 0.13041 | 0.0031894 | -0.0030013 | 0.20927 | -5.9768e-05 | 0.001959 | -0.0003226 | 0.0017688 | -0.0028199 | 63.826 | 63.7894 | -0.16022 | -59.2941 | 63.8351 | -59.1019 | -59.1522 | -59.0927 | -0.064087 | -59.3811 | 63.8535 | 63.8077 | -59.1293 | -59.2621 | -0.036621 | -0.086975 | -0.022888 | 122.8546 | -0.22888 | -0.14191 | -0.032043 | -0.064086 | -0.19684 | -0.004577 | -0.027465 | -0.31586 | -0.11902 | -0.050354 | 122.9004 | 122.8912 | 58.905 | -123.0103 | 122.9187 | 122.8729 | 59.0012 | -123.1201
649.5156 | 123.1247 | -59.0424 | 63.8626 | -0.15564 | 0.014381 | 0.066304 | 0.068791 | 0.13105 | 0.001694 | -0.0023605 | -1.6065 | -0.0032642 | -0.0001774 | -0.001177 | 0.0024096 | -0.0043153 | 63.8168 | 63.9404 | -0.013733 | -59.2484 | 63.8214 | -59.0927 | -59.1476 | -59.024 | 0.086975 | -59.2941 | 63.8809 | 63.8214 | -59.1248 | -59.2392 | -0.050354 | -0.10529 | -0.041199 | 122.9828 | -0.20599 | -0.10071 | -0.045777 | -0.082398 | -0.19684 | 0.01831 | 0.01831 | -0.25177 | -0.054931 | -0.041199 | 122.8638 | 122.8592 | 59.0286 | -123.0103 | 122.9233 | 122.8638 | 59.1293 | -123.1018
650.5312 | 123.1293 | -59.0698 | 63.8763 | -0.033569 | 0.013313 | 0.065022 | 0.070286 | 0.12934 | 0.0014804 | 0.0014847 | -0.10353 | -0.002837 | 0.0004636 | 0.0013864 | 0.00027337 | -0.0066651 | 63.6475 | 63.8672 | 0.004578 | -59.198 | 63.8443 | -59.1019 | -59.1385 | -59.0057 | 0.091553 | -59.3033 | 63.8489 | 63.7848 | -59.1385 | -59.2621 | -0.032044 | -0.068665 | -0.032044 | 122.937 | -0.12817 | -0.059509 | -0.22888 | -0.068665 | -0.19226 | -0.027466 | 0.064087 | -0.23346 | -0.041199 | -0.091553 | 122.9141 | 122.7173 | 59.0744 | -123.0148 | 122.9187 | 122.8546 | 59.1614 | -123.1384
651.5156 | 123.1155 | -59.0744 | 63.8535 | -0.02594 | 0.014595 | 0.064382 | 0.069859 | 0.13041 | -1.505e-05 | -0.0021469 | 0.064316 | -0.0015552 | -0.0006046 | -0.0007498 | 0.00070077 | -0.0028199 | 63.8168 | 63.9175 | -0.013733 | -59.2621 | 63.8077 | -59.0973 | -59.1202 | -59.0378 | 0.036621 | -59.3353 | 63.8397 | 63.8077 | -59.1385 | -59.2209 | -0.022888 | -0.045776 | -0.045777 | 122.9919 | -0.18768 | -0.14191 | -0.036622 | -0.064087 | -0.14648 | -0.013733 | 0.036621 | -0.26093 | -0.11444 | -0.045777 | 122.8821 | 122.8912 | 59.0607 | -122.9736 | 122.9141 | 122.8821 | 59.111 | -123.0743
652.5156 | 123.0927 | -59.0836 | 63.8763 | -0.12512 | 0.0092541 | 0.065877 | 0.067936 | 0.13041 | 0.0014804 | -0.0030013 | -0.050125 | -0.0030506 | -0.001459 | -0.0009634 | 0.002837 | -0.0036743 | 63.7756 | 63.8947 | -0.022888 | -59.2575 | 63.858 | -59.1019 | -59.0973 | -59.0469 | 0.073242 | -59.3262 | 63.8901 | 63.8443 | -59.1202 | -59.2712 | -0.018311 | -0.013733 | -0.018311 | 122.9782 | -0.17395 | -0.16022 | -0.10071 | -0.036621 | -0.18768 | 0.013733 | 0.036621 | -0.24262 | -0.054932 | -0.032044 | 122.9416 | 122.8592 | 59.0607 | -122.9736 | 122.9736 | 122.9279 | 59.1568 | -123.1476
653.5156 | 123.1796 | -59.0698 | 63.8077 | 0.18768 | 0.0071179 | 0.06545 | 0.065587 | 0.12742 | -0.0036464 | -0.0044967 | 0.32372 | -0.0032642 | -0.001459 | -0.0009634 | 0.0019824 | -0.0015381 | 63.7894 | 63.9725 | -0.036621 | -59.2392 | 63.7527 | -59.0973 | -59.1248 | -58.9783 | 0.050354 | -59.2529 | 63.7939 | 63.739 | -59.1431 | -59.2392 | -0.027466 | -0.054932 | -0.054931 | 123.0423 | -0.16937 | -0.11444 | -0.01831 | -0.073242 | -0.16937 | -0.013733 | 0.091553 | -0.18311 | -0.013733 | -0.068664 | 122.8226 | 122.8592 | 59.0332 | -122.9324 | 122.8638 | 122.8088 | 59.1202 | -123.0469
654.5156 | 123.0515 | -59.0973 | 63.8123 | 0.065613 | 0.013527 | 0.067159 | 0.069005 | 0.12998 | 0.0014804 | -0.0012923 | 0.1635 | -0.0017688 | 0.0015316 | -0.0003226 | 0.002837 | -0.0034607 | 63.7573 | 63.826 | -0.12817 | -59.2896 | 63.8489 | -59.1156 | -59.1476 | -59.1293 | -0.086975 | -59.4131 | 63.858 | 63.7985 | -59.1522 | -59.2667 | -0.018311 | -0.050354 | 0.036621 | 122.9233 | -0.19226 | -0.14191 | -0.054932 | -0.054932 | -0.16937 | 0.045776 | -0.032043 | -0.31586 | -0.14648 | -0.013733 | 122.9462 | 122.8546 | 58.9691 | -122.9599 | 122.9553 | 122.8958 | 59.0103 | -123.0789
655.5156 | 123.0835 | -59.079 | 63.858 | 0.035095 | 0.012459 | 0.067372 | 0.070073 | 0.13062 | 0.0010532 | -0.0010787 | 0.056686 | -0.0013416 | 0.0008908 | -0.000109 | 0.0026234 | -0.0041017 | 63.8214 | 63.9084 | -0.054932 | -59.2712 | 63.8214 | -59.0927 | -59.1156 | -59.0515 | -0.009155 | -59.3491 | 63.8489 | 63.8123 | -59.1385 | -59.2621 | -0.013733 | -0.036622 | -0.036621 | 122.9874 | -0.19226 | -0.15564 | -0.036621 | -0.05951 | -0.18311 | -0.009155 | 0.027465 | -0.27008 | -0.086975 | -0.045776 | 122.9004 | 122.9004 | 59.024 | -122.9736 | 122.9279 | 122.8912 | 59.0698 | -123.1201
656.5156 | 123.0698 | -59.079 | 63.8901 | -0.13275 | 0.010536 | 0.068654 | 0.068577 | 0.13062 | -0.0021512 | -0.0038559 | -0.042496 | -0.0013416 | -0.0023136 | 0.000532 | 0.0026234 | -0.0045289 | 63.7711 | 63.8901 | -0.027466 | -59.2575 | 63.8489 | -59.0744 | -59.111 | -59.0607 | 0.050354 | -59.3262 | 63.8763 | 63.8214 | -59.1522 | -59.2392 | 0.004577 | -0.032044 | -0.041199 | 122.9691 | -0.17853 | -0.14648 | -0.11902 | -0.073243 | -0.16022 | -0.013733 | 0.01831 | -0.24719 | -0.086975 | -0.068665 | 122.9279 | 122.85 | 59.0515 | -123.0011 | 122.9553 | 122.9004 | 59.1293 | -123.1293
657.5156 | 123.1293 | -59.0744 | 63.8992 | -0.13275 | 0.013954 | 0.06844 | 0.071141 | 0.12977 | 0.001694 | -0.0034287 | -0.019608 | -0.0024096 | 0.001318 | -0.000109 | -0.00079463 | -0.0034607 | 63.8214 | 63.9267 | 0.004578 | -59.2346 | 63.8351 | -59.0836 | -59.1202 | -58.992 | 0.07782 | -59.2758 | 63.8535 | 63.826 | -59.1385 | -59.2621 | -0.009155 | -0.045776 | -0.064087 | 123.0011 | -0.16022 | -0.11444 | -0.07782 | -0.064087 | -0.18768 | -0.045776 | 0.082398 | -0.20142 | -0.013733 | -0.073242 | 122.9095 | 122.8958 | 59.079 | -123.0194 | 122.9279 | 122.9004 | 59.1522 | -123.1613
658.5156 | 123.1247 | -59.0698 | 63.8992 | -0.086975 | 0.013313 | 0.069295 | 0.069005 | 0.13041 | -0.0012966 | -1.0724e-05 | -0.0043486 | -0.0019824 | -0.0006046 | -0.000109 | 0.0024096 | -0.0028199 | 63.8168 | 63.913 | -0.009155 | -59.2392 | 63.8535 | -59.0836 | -59.1431 | -59.0057 | -0.16022 | -59.4223 | 63.8077 | 63.7665 | -59.166 | -59.2484 | -0.013733 | -0.073242 | -0.045776 | 122.9828 | -0.16937 | -0.096131 | -0.082398 | -0.096131 | -0.17853 | -0.091553 | 0.064087 | -0.35248 | -0.17395 | -0.13275 | 122.9233 | 122.8867 | 59.0607 | -123.0423 | 122.8775 | 122.8363 | 58.9096 | -123.1476
659.5156 | 123.0835 | -59.0698 | 63.858 | -0.056458 | 0.013099 | 0.069081 | 0.069432 | 0.12934 | 0.0010532 | -0.0015061 | 0.049057 | -0.002196 | 0.00025 | -0.0026724 | 0.0030506 | -0.0034607 | 63.8214 | 63.945 | -0.032043 | -59.2438 | 63.826 | -59.0881 | -59.1293 | -59.024 | 0.041199 | -59.317 | 63.8672 | 63.7939 | -59.1431 | -59.2346 | -0.018311 | -0.059509 | -0.032043 | 123.0148 | -0.17395 | -0.11444 | -0.036621 | -0.073242 | -0.1648 | 0.009155 | 0.045776 | -0.24719 | -0.082398 | -0.064087 | 122.8958 | 122.8912 | 59.0378 | -122.9874 | 122.937 | 122.8638 | 59.111 | -123.0927
660.5312 | 123.111 | -59.0561 | 63.8855 | -0.13275 | 0.014168 | 0.06545 | 0.071568 | 0.12998 | 0.0019078 | -0.00065152 | 0.026169 | -0.00048697 | 3.6404e-05 | 0.0022408 | 0.0013416 | -0.0032471 | 63.8077 | 63.9404 | -0.009155 | -59.2255 | 63.858 | -59.0836 | -59.1064 | -59.0698 | -0.1831 | -59.3445 | 63.8351 | 63.7894 | -59.1614 | -59.2529 | -0.027466 | -0.050354 | -0.027466 | 122.9965 | -0.16937 | -0.11902 | -0.07782 | -0.10529 | -0.19684 | -0.050354 | -0.013733 | -0.28839 | -0.091552 | -0.09613 | 122.9141 | 122.8638 | 59.0469 | -122.9919 | 122.8912 | 122.8455 | 58.873 | -123.1384
661.5156 | 123.0927 | -59.1019 | 63.8992 | 0.019836 | 0.014168 | 0.067159 | 0.068364 | 0.12827 | 0.0042576 | -0.0017197 | 0.10246 | -0.0036914 | 3.6404e-05 | -0.001177 | 0.0041186 | -0.0036743 | 63.7848 | 63.9038 | -0.041199 | -59.2621 | 63.826 | -59.0973 | -59.1385 | -59.0607 | 0.013733 | -59.3399 | 63.8397 | 63.8123 | -59.1202 | -59.2575 | 0.004578 | -0.036621 | -0.073242 | 123.0057 | -0.16022 | -0.1236 | -0.11444 | -0.01831 | -0.15564 | -0.059509 | 0.041199 | -0.23804 | -0.082398 | -0.086975 | 122.9279 | 122.8867 | 59.0607 | -123.0377 | 122.9416 | 122.9141 | 59.1156 | -123.1567
662.5156 | 123.111 | -59.0652 | 63.858 | -0.071716 | 0.010322 | 0.067159 | 0.069432 | 0.12934 | 0.001694 | -0.0012923 | -0.095902 | -0.0034778 | 0.001318 | -0.0009634 | 0.00048697 | -0.0036743 | 63.7939 | 63.9221 | -0.022888 | -59.23 | 63.8214 | -59.0698 | -59.1019 | -59.0424 | 0.073242 | -59.3079 | 63.858 | 63.8031 | -59.1339 | -59.2346 | -0.004577 | -0.036621 | -0.036621 | 122.9874 | -0.16479 | -0.12817 | -0.064087 | -0.068664 | -0.16937 | 0 | 0.022889 | -0.24261 | -0.073242 | -0.054931 | 122.8867 | 122.8592 | 59.0424 | -122.9599 | 122.9233 | 122.8683 | 59.1385 | -123.0927
663.5156 | 123.0927 | -59.0424 | 63.8626 | -0.10223 | 0.012672 | 0.067372 | 0.069645 | 0.12806 | 0.0010532 | -0.0012923 | -0.0043486 | -0.001128 | -0.0001774 | -0.000109 | 0.00091437 | -0.0030335 | 63.8077 | 63.9496 | -0.013733 | -59.2346 | 63.8351 | -59.0836 | -59.1248 | -59.0469 | 0.15564 | -59.3308 | 63.8626 | 63.7802 | -59.1293 | -59.2575 | -0.041199 | -0.082398 | -0.027466 | 122.9919 | -0.19226 | -0.10986 | -0.054932 | -0.086975 | -0.21515 | 0 | -0.004578 | -0.28839 | -0.073243 | -0.082398 | 122.8775 | 122.85 | 59.0286 | -122.9874 | 122.905 | 122.8226 | 59.198 | -123.1201
664.5156 | 123.1201 | -59.0561 | 63.9038 | -0.094604 | 0.012672 | 0.066731 | 0.070073 | 0.12956 | 0.0012668 | -0.0036423 | -0.011978 | -0.002837 | -0.0021 | -0.000109 | 0.0026234 | -0.0021789 | 63.8123 | 63.9404 | -0.009155 | -59.2255 | 63.8397 | -59.1019 | -59.1293 | -59.0469 | 0.068665 | -59.3811 | 63.858 | 63.7619 | -59.1431 | -59.2712 | -0.045777 | -0.073242 | -0.064087 | 122.9965 | -0.16937 | -0.096131 | -0.091553 | -0.086975 | -0.21515 | -0.045777 | 0.009155 | -0.32501 | -0.10986 | -0.14191 | 122.8958 | 122.8683 | 59.0469 | -123.0331 | 122.9141 | 122.818 | 59.1248 | -123.175
665.5156 | 123.111 | -59.0469 | 63.8763 | 0.45471 | 0.012459 | 0.066091 | 0.067936 | 0.12998 | 0.0014804 | 0.00041648 | 0.10246 | 0.00036743 | -0.001459 | -0.000109 | 0.002196 | -0.0030335 | 63.8214 | 63.945 | -0.018311 | -59.2255 | 63.8535 | -59.0927 | -59.1064 | -59.0469 | 0.050354 | -59.317 | 63.8397 | 63.8031 | -59.1568 | -59.2575 | -0.045776 | -0.059509 | -0.022888 | 122.9919 | -0.17853 | -0.11902 | -0.054932 | -0.10986 | -0.21057 | -0.036621 | 0 | -0.27008 | -0.05951 | -0.073242 | 122.9004 | 122.8683 | 59.0286 | -122.9828 | 122.8867 | 122.85 | 59.0973 | -123.1338
666.5156 | 123.0743 | -59.079 | 63.8992 | -0.20142 | 0.0069043 | 0.066518 | 0.067936 | 0.12827 | -0.00086945 | -0.0023605 | -0.057755 | -0.0043324 | -0.000391 | 0.0003182 | 0.0024096 | -0.0017517 | 63.7573 | 63.8809 | -0.036621 | -59.2667 | 63.8351 | -59.0698 | -59.1431 | -59.0927 | 0.059509 | -59.3353 | 63.8901 | 63.8168 | -59.1202 | -59.2529 | 0.009155 | -0.064087 | -0.064087 | 122.9599 | -0.18768 | -0.1236 | -0.14191 | -0.041199 | -0.17395 | -0.009155 | -0.013733 | -0.25635 | -0.082397 | -0.082398 | 122.9141 | 122.8363 | 59.0424 | -123.0423 | 122.9691 | 122.8958 | 59.1385 | -123.1522
667.5156 | 123.1247 | -59.0698 | 63.8443 | -0.079346 | 0.013527 | 0.065663 | 0.070073 | 0.1287 | 0.00083955 | -0.0015061 | -1.1945 | -0.002196 | 0.0015316 | -0.000109 | 0.0017688 | -0.0036743 | 63.8031 | 63.9267 | -0.022888 | -59.2346 | 63.8626 | -59.0881 | -59.1248 | -59.0378 | 0.091553 | -59.3033 | 63.8763 | 63.8168 | -59.1019 | -59.2575 | -0.018311 | -0.054932 | 0.018311 | 122.9965 | -0.1648 | -0.10986 | -0.041198 | -0.032044 | -0.18768 | 0.032044 | 0.032043 | -0.23346 | -0.045777 | -0.027466 | 122.9324 | 122.8729 | 59.0469 | -122.9691 | 122.9462 | 122.8867 | 59.1614 | -123.1018
668.5156 | 123.1064 | -59.0927 | 63.8992 | -0.18616 | 0.01075 | 0.063527 | 0.0705 | 0.12742 | -0.0017238 | -0.0030013 | -0.088272 | -0.002196 | -0.0006046 | -0.000109 | 0.00048697 | -0.0047425 | 63.7802 | 63.8855 | -0.032043 | -59.2529 | 63.8535 | -59.1064 | -59.1248 | -59.0652 | 0.07782 | -59.3079 | 63.8626 | 63.8397 | -59.1293 | -59.2621 | -0.013733 | -0.032044 | -0.045776 | 122.9782 | -0.16022 | -0.12817 | -0.11902 | -0.036621 | -0.16937 | -0.036621 | 0.027465 | -0.21515 | -0.045776 | -0.059509 | 122.9462 | 122.8729 | 59.0607 | -123.024 | 122.9553 | 122.9324 | 59.1705 | -123.1613
669.5156 | 123.0972 | -59.079 | 63.8489 | -0.14801 | 0.011818 | 0.066518 | 0.070714 | 0.12849 | -1.505e-05 | 0.00020288 | 0.064316 | -0.0013416 | -0.0025272 | 0.000532 | 0.00091437 | -0.0038879 | 63.8535 | 63.9404 | -0.018311 | -59.2392 | 63.8443 | -59.0881 | -59.1385 | -59.0332 | 0.050354 | -59.3399 | 63.8672 | 63.8077 | -59.1339 | -59.2667 | -0.009156 | -0.05951 | -0.004578 | 123.0194 | -0.16022 | -0.10071 | 0.004578 | -0.054932 | -0.18768 | 0.01831 | 0.045776 | -0.26093 | -0.073242 | -0.041199 | 122.9233 | 122.9324 | 59.0607 | -122.9874 | 122.9462 | 122.8867 | 59.1293 | -123.1155
670.5312 | 123.1155 | -59.0515 | 63.8626 | -0.071716 | 0.014381 | 0.065022 | 0.069005 | 0.12934 | 0.0038304 | -0.0027877 | 0.026169 | 0.00036743 | 3.6404e-05 | 0.0016 | 0.0017688 | -0.0021789 | 63.8168 | 63.9267 | -0.018311 | -59.2438 | 63.8306 | -59.0927 | -59.1293 | -59.0424 | 0.050354 | -59.3399 | 63.8306 | 63.8123 | -59.1385 | -59.2621 | -0.041198 | -0.077819 | -0.032044 | 122.9782 | -0.19226 | -0.11444 | -0.045777 | -0.086975 | -0.21057 | -0.032044 | 0.009156 | -0.28839 | -0.07782 | -0.050354 | 122.8821 | 122.8683 | 59.0332 | -122.9919 | 122.8821 | 122.8638 | 59.1019 | -123.1247
671.5156 | 123.0652 | -59.1019 | 63.8718 | -0.033569 | 0.01139 | 0.066731 | 0.070714 | 0.12763 | 0.0029758 | -0.0023605 | 0.094833 | -0.0013416 | 0.0004636 | 0.000532 | 0.002196 | -0.0023927 | 63.7848 | 63.9175 | -0.041199 | -59.2575 | 63.8397 | -59.0927 | -59.1431 | -59.0607 | 0.013733 | -59.3491 | 63.8672 | 63.8123 | -59.1385 | -59.2712 | 0.009156 | -0.041198 | -0.032043 | 123.0194 | -0.15564 | -0.11444 | -0.086975 | -0.036621 | -0.16937 | -0.004578 | 0.041199 | -0.24719 | -0.07782 | -0.059509 | 122.9416 | 122.8867 | 59.0607 | -123.0148 | 122.9691 | 122.9141 | 59.1156 | -123.143
672.5156 | 123.111 | -59.079 | 63.8306 | 0.027466 | 0.012886 | 0.06545 | 0.069218 | 0.12827 | 0.0038304 | -0.0015061 | 0.049057 | -0.00027337 | 0.0004636 | 0.0001046 | 0.002837 | -0.0028199 | 63.8214 | 63.9267 | -0.041199 | -59.2529 | 63.826 | -59.0652 | -59.1431 | -59.0424 | 0.032043 | -59.3445 | 63.8718 | 63.8168 | -59.1293 | -59.2529 | 0.013732 | -0.064087 | -0.004577 | 123.0057 | -0.17395 | -0.10986 | -0.009155 | -0.050354 | -0.17395 | 0.041199 | 0.036621 | -0.2655 | -0.091552 | -0.013733 | 122.905 | 122.9004 | 59.0378 | -122.9736 | 122.9507 | 122.8958 | 59.111 | -123.0835
673.5156 | 123.111 | -59.0698 | 63.8763 | -0.11749 | 0.013954 | 0.067159 | 0.069859 | 0.13084 | 0.002335 | -0.00065152 | 0.041427 | -0.0013416 | -0.0012454 | -0.0003226 | 0.0017688 | -0.0021789 | 63.8397 | 63.945 | -0.018311 | -59.2346 | 63.8077 | -59.0973 | -59.1202 | -59.0378 | 0.054932 | -59.3216 | 63.8626 | 63.7894 | -59.1522 | -59.2529 | -0.027466 | -0.050354 | -0.068665 | 123.0148 | -0.1648 | -0.11444 | -0.036621 | -0.082398 | -0.18311 | -0.013733 | 0.032043 | -0.25177 | -0.068664 | -0.086975 | 122.8775 | 122.9095 | 59.0515 | -122.9965 | 122.9324 | 122.8592 | 59.1248 | -123.1293
674.5156 | 123.111 | -59.0744 | 63.8718 | -0.0030518 | 0.01374 | 0.06545 | 0.068364 | 0.13041 | 0.0029758 | -0.0019333 | 0.0032804 | -0.00091437 | -0.0016726 | 0.0001046 | 0.0036914 | -0.0011109 | 63.8123 | 63.945 | -0.036621 | -59.1888 | 63.8626 | -59.0973 | -59.1339 | -59.0195 | 0.064087 | -59.317 | 63.858 | 63.7939 | -59.1156 | -59.2667 | -0.022888 | -0.059509 | -0.009155 | 123.0194 | -0.11444 | -0.054932 | -0.059509 | -0.041199 | -0.19226 | -0.013733 | 0.054932 | -0.24262 | -0.050354 | -0.07782 | 122.937 | 122.8867 | 59.0378 | -123.0057 | 122.9324 | 122.8683 | 59.1385 | -123.1384
675.5156 | 123.1247 | -59.0561 | 63.8718 | -0.071716 | 0.01139 | 0.065236 | 0.068364 | 0.12806 | 0.0029758 | -0.0021469 | -1.3166 | -0.002837 | -0.0001774 | 0.0009592 | 0.0024096 | -0.0045289 | 63.8123 | 63.945 | -0.018311 | -59.2392 | 63.8168 | -59.0973 | -59.1431 | -59.0332 | 0.09613 | -59.2987 | 63.8489 | 63.8214 | -59.1293 | -59.23 | -0.041199 | -0.086975 | -0.054932 | 123.0011 | -0.18311 | -0.096131 | -0.059509 | -0.073242 | -0.17395 | -0.022888 | 0.022888 | -0.24262 | -0.068664 | -0.050354 | 122.8729 | 122.8683 | 59.0378 | -123.0148 | 122.905 | 122.8775 | 59.1522 | -123.1018
676.5156 | 123.1018 | -59.0561 | 63.8718 | -0.064087 | 0.0098951 | 0.065663 | 0.067296 | 0.13041 | 0.001694 | -0.00065152 | -0.050125 | -0.0013416 | 0.0025998 | -0.000109 | 0.0032642 | -0.0036743 | 63.8168 | 63.9313 | -0.009155 | -59.2484 | 63.8489 | -59.111 | -59.1202 | -59.0378 | -0.17395 | -59.3674 | 63.8397 | 63.7985 | -59.1705 | -59.2621 | -0.054932 | -0.064087 | -0.022888 | 122.9874 | -0.19226 | -0.12817 | -0.054932 | -0.11444 | -0.20599 | -0.032043 | 0.01831 | -0.31128 | -0.10529 | -0.073242 | 122.905 | 122.8729 | 59.0469 | -122.9919 | 122.8958 | 122.8546 | 58.8821 | -123.1338
677.5156 | 123.0652 | -59.0698 | 63.8535 | -0.11749 | 0.010963 | 0.065022 | 0.070286 | 0.13105 | -0.00044225 | -0.0030013 | 0.018539 | -0.0015552 | -0.0001774 | -0.0007498 | 0.0013416 | -0.0041017 | 63.8123 | 63.9267 | 0 | -59.2117 | 63.8397 | -59.0744 | -59.1431 | -59.0469 | 0.07782 | -59.2987 | 63.858 | 63.8123 | -59.1248 | -59.2712 | -0.004578 | -0.073242 | -0.013733 | 122.9965 | -0.14191 | -0.068665 | -0.041199 | -0.054932 | -0.20142 | 0.004577 | 0.022888 | -0.22888 | -0.027466 | -0.041199 | 122.9095 | 122.8821 | 59.0698 | -122.9965 | 122.9279 | 122.8821 | 59.1476 | -123.1247
678.5156 | 123.0881 | -59.0744 | 63.8901 | -0.18616 | 0.0090405 | 0.066731 | 0.071141 | 0.1302 | -0.00065585 | -0.00086512 | -0.050125 | -0.0024096 | -0.000391 | -0.0009634 | 0.0015552 | -0.0030335 | 63.7573 | 63.8763 | -0.027466 | -59.2484 | 63.8489 | -59.0927 | -59.1156 | -59.0698 | 0.07782 | -59.3353 | 63.8901 | 63.8489 | -59.1431 | -59.2392 | -0.01831 | -0.041199 | -0.041199 | 122.9507 | -0.17395 | -0.13275 | -0.13275 | -0.068664 | -0.16479 | 0 | 0.004578 | -0.26093 | -0.09613 | -0.041199 | 122.9233 | 122.8317 | 59.0469 | -123.0057 | 122.9645 | 122.9233 | 59.1522 | -123.1293
679.5156 | 123.1064 | -59.0698 | 63.8672 | -0.13275 | 0.0094677 | 0.065022 | 0.069218 | 0.12763 | -1.505e-05 | -0.00086512 | -0.027237 | -0.0024096 | -0.0001774 | -0.001818 | 0.00091437 | -0.0060243 | 63.7848 | 63.9313 | -0.032043 | -59.2163 | 63.8535 | -59.0836 | -59.1156 | -59.0515 | 0.091553 | -59.3124 | 63.8763 | 63.8214 | -59.1339 | -59.2529 | -0.013733 | -0.045777 | -0.013732 | 123.0011 | -0.14649 | -0.10071 | -0.082397 | -0.064087 | -0.18311 | 0.009156 | 0.01831 | -0.24262 | -0.059509 | -0.045776 | 122.9233 | 122.8546 | 59.0378 | -122.9828 | 122.9462 | 122.8912 | 59.1614 | -123.1201
680.5312 | 123.0606 | -59.0607 | 63.8901 | -0.18616 | 0.0081861 | 0.069295 | 0.068791 | 0.13276 | -0.0017238 | -0.0019333 | -0.042496 | -0.0017688 | -0.0016726 | -0.0009634 | -0.00036743 | -0.0026063 | 63.7985 | 63.9816 | 0.059509 | -59.2209 | 63.8123 | -59.0698 | -59.0927 | -59.0378 | 0.10071 | -59.285 | 63.8763 | 63.8351 | -59.1019 | -59.2712 | -0.009155 | -0.032043 | -0.07782 | 123.0423 | -0.16022 | -0.12817 | -0.091553 | -0.041199 | -0.21057 | -0.013733 | 0.022888 | -0.2243 | -0.013733 | -0.054932 | 122.8729 | 122.8592 | 59.1202 | -122.9828 | 122.937 | 122.8958 | 59.1614 | -123.1613
681.5156 | 123.056 | -59.0698 | 63.8901 | -0.14801 | 0.0098951 | 0.067586 | 0.071568 | 0.13297 | -1.505e-05 | 0.00020288 | -0.088272 | -0.0032642 | 0.0006772 | -0.0022452 | 0.003905 | -0.0062379 | 63.7711 | 63.8947 | -0.022888 | -59.2575 | 63.8626 | -59.0836 | -59.1156 | -59.0515 | 0.073242 | -59.3079 | 63.8855 | 63.7939 | -59.1202 | -59.2621 | -0.013733 | -0.045777 | -0.027466 | 122.9645 | -0.18768 | -0.14191 | -0.11902 | -0.050354 | -0.19226 | -0.004578 | 0.01831 | -0.23804 | -0.045776 | -0.096131 | 122.9324 | 122.8409 | 59.0469 | -123.0057 | 122.9553 | 122.8638 | 59.1431 | -123.1522
682.5156 | 123.0698 | -59.1019 | 63.8947 | 0.012207 | 0.012886 | 0.064809 | 0.069859 | 0.13212 | 0.0029758 | -0.00043792 | 0.079574 | -0.0017688 | 0.0021726 | -0.0003226 | 0.0047596 | -0.0032471 | 63.7848 | 63.8763 | -0.068665 | -59.2758 | 63.8214 | -59.0881 | -59.1248 | -59.0698 | -0.009155 | -59.3674 | 63.8718 | 63.7756 | -59.1385 | -59.285 | 0.013733 | -0.022888 | -0.073242 | 122.9782 | -0.17395 | -0.15106 | -0.10986 | -0.036621 | -0.1831 | -0.022888 | 0.032044 | -0.2655 | -0.082398 | -0.11902 | 122.9233 | 122.8867 | 59.0332 | -123.0194 | 122.9736 | 122.8775 | 59.0927 | -123.1796
683.5156 | 123.0789 | -59.0652 | 63.858 | -0.15564 | 0.012672 | 0.065877 | 0.071568 | 0.13233 | 0.00041235 | -0.0025741 | 0.0032804 | -0.002196 | -0.0001774 | -0.001177 | 0.0013416 | -0.0036743 | 63.8077 | 63.9359 | -0.009155 | -59.23 | 63.8626 | -59.079 | -59.1248 | -59.0286 | 0.086975 | -59.2987 | 63.858 | 63.8077 | -59.1156 | -59.23 | -0.013732 | -0.059509 | 0.004578 | 123.0011 | -0.16479 | -0.10529 | -0.050354 | -0.050354 | -0.16479 | 0 | 0.036622 | -0.23346 | -0.068664 | -0.050354 | 122.9279 | 122.8729 | 59.0561 | -122.9828 | 122.9233 | 122.8729 | 59.1522 | -123.0881
684.5156 | 123.0835 | -59.0881 | 63.8855 | -0.14801 | 0.0081861 | 0.065022 | 0.066227 | 0.12827 | -0.0017238 | -0.00022432 | -0.33241 | -0.0034778 | 0.00025 | -0.0007498 | -0.00058103 | -0.0041017 | 63.7436 | 63.913 | -0.013733 | -59.2804 | 63.8489 | -59.0698 | -59.0927 | -59.0836 | 0.013733 | -59.3353 | 63.8947 | 63.8077 | -59.1431 | -59.23 | 0.018311 | -0.004577 | -0.036621 | 123.0011 | -0.19226 | -0.18768 | -0.14191 | -0.054931 | -0.14191 | 0.009155 | 0.004578 | -0.24719 | -0.10529 | -0.07782 | 122.937 | 122.8317 | 59.0744 | -122.9782 | 122.9828 | 122.8958 | 59.1019 | -123.1155
685.5156 | 123.0743 | -59.0652 | 63.8855 | -0.15564 | 0.010109 | 0.067159 | 0.0705 | 0.12956 | -0.00065585 | -0.0017197 | -0.073013 | -0.0017688 | -0.0001774 | -0.0013906 | 0.00027337 | -0.0032471 | 63.7665 | 63.8901 | -0.041199 | -59.2392 | 63.8397 | -59.0881 | -59.1339 | -59.0561 | 0.059509 | -59.3491 | 63.8763 | 63.826 | -59.1476 | -59.2346 | -0.022888 | -0.068664 | -0.045776 | 122.9553 | -0.17395 | -0.10529 | -0.11902 | -0.082397 | -0.16937 | -0.009155 | 0.009156 | -0.28381 | -0.11444 | -0.059509 | 122.905 | 122.8317 | 59.024 | -123.0194 | 122.9416 | 122.8912 | 59.1248 | -123.1201
686.5156 | 123.0743 | -59.0469 | 63.8809 | -0.17853 | 0.010109 | 0.069295 | 0.069005 | 0.12913 | -0.0019376 | -0.00065152 | -0.034867 | -0.0019824 | -0.001459 | -0.0043814 | 0.00091437 | -0.0019653 | 63.7619 | 63.9175 | -0.018311 | -59.2575 | 63.8443 | -59.0836 | -59.1385 | -59.1202 | -0.064087 | -59.3079 | 63.8672 | 63.8077 | -59.1476 | -59.2438 | -0.036621 | -0.091553 | -0.036621 | 122.9645 | -0.21057 | -0.11902 | -0.11902 | -0.10071 | -0.19684 | -0.013733 | -0.073242 | -0.26093 | -0.064087 | -0.073242 | 122.8912 | 122.8088 | 59.0286 | -123.0194 | 122.9141 | 122.8546 | 58.9828 | -123.1247
687.5156 | 123.1155 | -59.0698 | 63.8992 | -0.16327 | 0.010322 | 0.065663 | 0.068791 | 0.1287 | 0.00041235 | -0.0025741 | -0.065384 | -0.0015552 | -0.0025272 | 0.000532 | 0.002196 | -0.0051697 | 63.7848 | 63.9221 | -0.022888 | -59.2255 | 63.8855 | -59.111 | -59.1156 | -59.0195 | 0.073242 | -59.3124 | 63.858 | 63.8123 | -59.0973 | -59.2529 | -0.041199 | -0.045777 | -0.013733 | 122.9919 | -0.15564 | -0.10986 | -0.11444 | -0.027466 | -0.18311 | -0.041199 | 0.050354 | -0.24262 | -0.059509 | -0.086975 | 122.9553 | 122.8546 | 59.0469 | -123.0148 | 122.9279 | 122.8821 | 59.1431 | -123.1522
688.5156 | 123.0606 | -59.0515 | 63.8855 | -0.23956 | 0.010963 | 0.066091 | 0.06815 | 0.12913 | -0.0025784 | -0.00086512 | -0.11879 | -0.0024096 | -0.0012454 | -0.0003226 | 0.0017688 | -0.0032471 | 63.7482 | 63.8992 | -0.041199 | -59.2575 | 63.8443 | -59.0836 | -59.111 | -59.0652 | 0.041199 | -59.3262 | 63.8809 | 63.8123 | -59.1293 | -59.2346 | -0.032043 | -0.059509 | -0.041199 | 122.9507 | -0.20599 | -0.14648 | -0.13733 | -0.077819 | -0.18311 | -0.004578 | -0.013733 | -0.27466 | -0.091553 | -0.073242 | 122.8958 | 122.7997 | 59.0103 | -122.9965 | 122.9324 | 122.8638 | 59.0927 | -123.1201
689.5156 | 123.1384 | -59.0561 | 63.8992 | -0.071716 | 0.013099 | 0.066091 | 0.068364 | 0.12956 | 0.0027622 | -0.0025741 | -0.011978 | -0.0034778 | 3.6404e-05 | 0.0003182 | 0.0032642 | -0.0045289 | 63.8031 | 63.9587 | 0 | -59.2255 | 63.8535 | -59.0973 | -59.111 | -59.0286 | 0.082397 | -59.4864 | 63.8306 | 63.739 | -59.1568 | -59.2484 | -0.041199 | -0.054932 | -0.045776 | 123.0148 | -0.16937 | -0.11444 | -0.09613 | -0.10071 | -0.19226 | -0.068665 | 0.027466 | -0.4303 | -0.23804 | -0.16022 | 122.9095 | 122.8592 | 59.0561 | -123.0103 | 122.8867 | 122.7951 | 59.1385 | -123.1476
690.5312 | 123.1476 | -59.0469 | 63.8626 | -0.1709 | 0.0047681 | 0.067159 | 0.066227 | 0.12742 | -0.002792 | -0.0027877 | -0.073013 | -0.0049732 | -0.0010318 | -0.001818 | -0.0018628 | -0.0026063 | 63.8214 | 64.0182 | 0.082397 | -59.1934 | 63.8031 | -59.0652 | -59.0881 | -59.0012 | 0.15106 | -59.2575 | 63.8626 | 63.7802 | -59.1019 | -59.2484 | -0.018311 | -0.041199 | -0.059509 | 123.0652 | -0.14648 | -0.10529 | -0.041199 | -0.054932 | -0.20142 | 0 | 0.045776 | -0.21057 | -0.009155 | -0.082398 | 122.85 | 122.8683 | 59.1293 | -122.9507 | 122.9095 | 122.8271 | 59.198 | -123.111
691.5156 | 123.0881 | -59.0469 | 63.8809 | -0.1709 | 0.011604 | 0.0678 | 0.071141 | 0.13191 | 0.0042576 | -0.0030013 | -0.073013 | -0.003905 | 0.0004636 | -0.0009634 | 0.00027337 | -0.0053833 | 63.7939 | 63.9313 | 0 | -59.2163 | 63.8718 | -59.0698 | -59.0973 | -59.0286 | 0.07782 | -59.3124 | 63.8855 | 63.7985 | -59.1202 | -59.2529 | -0.022888 | -0.050354 | -0.009155 | 122.9782 | -0.16937 | -0.11902 | -0.086975 | -0.073242 | -0.20599 | 0.004578 | 0.018311 | -0.2655 | -0.059509 | -0.082397 | 122.9187 | 122.8409 | 59.0469 | -122.9782 | 122.9324 | 122.8455 | 59.1248 | -123.1338
692.5156 | 123.143 | -59.0698 | 63.858 | -0.15564 | 0.011818 | 0.066518 | 0.066868 | 0.12913 | 0.0010532 | -0.0038559 | -0.12642 | -0.0032642 | -0.0010318 | -0.001818 | 0.0026234 | -0.0047425 | 63.7848 | 63.9313 | -0.009155 | -59.2392 | 63.858 | -59.1019 | -59.1522 | -59.0332 | 0.059509 | -59.2987 | 63.8763 | 63.8077 | -59.1385 | -59.2438 | -0.032044 | -0.082398 | 0 | 123.0011 | -0.16937 | -0.086975 | -0.073242 | -0.068665 | -0.17395 | 0.018311 | 0.036621 | -0.22888 | -0.054932 | -0.050354 | 122.9279 | 122.8546 | 59.0607 | -123.0103 | 122.9462 | 122.8775 | 59.1293 | -123.1018
693.5156 | 123.0927 | -59.0698 | 63.8626 | -0.13275 | 0.010109 | 0.066945 | 0.069645 | 0.12827 | -1.505e-05 | -0.0023605 | -0.10353 | -0.002196 | -0.0027408 | -0.0009634 | 0.002196 | -0.0055969 | 63.7756 | 63.9084 | -0.027466 | -59.2392 | 63.8397 | -59.1019 | -59.1248 | -59.0515 | 0.086975 | -59.3124 | 63.8855 | 63.8214 | -59.1064 | -59.2529 | -0.032044 | -0.054932 | -0.022888 | 122.9782 | -0.16937 | -0.11444 | -0.086975 | -0.036621 | -0.18311 | 0.022888 | 0.01831 | -0.24262 | -0.059509 | -0.041199 | 122.9095 | 122.8455 | 59.0424 | -122.9874 | 122.9553 | 122.8912 | 59.1568 | -123.1155
694.5156 | 123.0606 | -59.0515 | 63.8901 | -0.18616 | 0.0077587 | 0.067159 | 0.0705 | 0.12934 | -0.0040738 | -0.0023605 | 0.0032804 | -0.0030506 | -0.0033816 | -0.0013906 | -0.00079463 | -0.0043153 | 63.7939 | 63.9816 | 0.013733 | -59.2209 | 63.8443 | -59.0515 | -59.0927 | -59.0561 | 0.059509 | -59.3216 | 63.8855 | 63.8214 | -59.1248 | -59.2346 | 0 | -0.041198 | -0.045777 | 123.0331 | -0.16937 | -0.12817 | -0.096131 | -0.073242 | -0.18311 | -0.004578 | -0.004577 | -0.27008 | -0.086975 | -0.068665 | 122.8958 | 122.8455 | 59.0652 | -122.9828 | 122.937 | 122.8729 | 59.111 | -123.1247
695.5312 | 123.1018 | -59.0561 | 63.8443 | 0.17242 | 0.0060497 | 0.06844 | 0.065159 | 0.12892 | -0.0023648 | -0.0025741 | 0.32372 | -0.002837 | -0.0025272 | -0.0020316 | 0.002196 | -0.00068366 | 63.7711 | 63.9587 | -0.045776 | -59.2484 | 63.7802 | -59.0744 | -59.1385 | -59.0103 | 0.018311 | -59.285 | 63.8031 | 63.7436 | -59.1293 | -59.2392 | -0.018311 | -0.082398 | -0.064087 | 123.0148 | -0.19226 | -0.10986 | -0.073242 | -0.073242 | -0.18311 | -0.041198 | 0.045776 | -0.22888 | -0.045776 | -0.10071 | 122.8363 | 122.8271 | 59.0103 | -122.9828 | 122.8592 | 122.7997 | 59.0744 | -123.0835
696.5156 | 123.0652 | -59.079 | 63.8901 | -0.15564 | 0.011177 | 0.0678 | 0.06815 | 0.12892 | -0.00044225 | -0.0030013 | -0.034867 | -0.0030506 | -0.0012454 | 0.0001046 | 0.00091437 | -0.0015381 | 63.7894 | 63.8992 | -0.027466 | -59.2529 | 63.8718 | -59.079 | -59.1248 | -59.1476 | -0.004578 | -59.317 | 63.8901 | 63.8168 | -59.1339 | -59.2529 | 0 | -0.045777 | -0.018311 | 122.9782 | -0.17395 | -0.12817 | -0.10071 | -0.054932 | -0.17395 | 0 | -0.068665 | -0.23804 | -0.064087 | -0.073243 | 122.9507 | 122.8683 | 59.0515 | -123.0148 | 122.9691 | 122.8958 | 59.0744 | -123.143
697.5156 | 123.1705 | -59.0469 | 63.8077 | 0.12665 | 0.0069043 | 0.066945 | 0.068791 | 0.12956 | 0.00019875 | -0.00086512 | 0.3466 | -0.005614 | -0.0001774 | -0.0009634 | 0.002196 | -0.0015381 | 63.826 | 63.9908 | -0.013733 | -59.2392 | 63.7619 | -59.0836 | -59.1339 | -58.9783 | 0.036621 | -59.2667 | 63.8168 | 63.7482 | -59.1431 | -59.2667 | -0.036621 | -0.086975 | -0.045776 | 123.0377 | -0.19226 | -0.10529 | 0.018311 | -0.09613 | -0.21973 | 0.009155 | 0.068665 | -0.21973 | 0 | -0.059509 | 122.8088 | 122.8729 | 59.0332 | -122.9416 | 122.8638 | 122.7951 | 59.0836 | -123.0743
698.5156 | 123.1247 | -59.0836 | 63.8855 | -0.14801 | 0.012459 | 0.064168 | 0.069005 | 0.1287 | 0.0042576 | -0.0025741 | -0.019608 | -0.0015552 | -0.0016726 | 0.0009592 | 0.001128 | -0.0049561 | 63.8535 | 63.9359 | -0.009155 | -59.2346 | 63.8489 | -59.079 | -59.1339 | -59.0149 | 0.073242 | -59.3033 | 63.8763 | 63.7894 | -59.1293 | -59.2575 | 0.004578 | -0.050354 | -0.036621 | 123.0194 | -0.15106 | -0.10071 | -0.032043 | -0.045776 | -0.17395 | -0.009155 | 0.068664 | -0.21973 | -0.045777 | -0.09613 | 122.9324 | 122.937 | 59.0744 | -123.0194 | 122.9599 | 122.8729 | 59.1568 | -123.143
699.5156 | 123.1064 | -59.0836 | 63.8626 | -0.14038 | 0.010536 | 0.068227 | 0.069432 | 0.1302 | -0.00086945 | -0.0015061 | -0.12642 | -0.0024096 | -0.0027408 | 0.0009592 | -0.0010082 | -0.0038879 | 63.7802 | 63.8947 | -0.027466 | -59.2575 | 63.8489 | -59.0927 | -59.1248 | -59.0607 | 0.068665 | -59.3445 | 63.8947 | 63.8214 | -59.1339 | -59.2163 | -0.009155 | -0.041199 | -0.013733 | 122.9782 | -0.17395 | -0.13275 | -0.082398 | -0.050354 | -0.13275 | 0.032043 | 0.022888 | -0.26093 | -0.12817 | -0.041199 | 122.9324 | 122.8638 | 59.0561 | -122.9874 | 122.9782 | 122.905 | 59.1522 | -123.0789
700.5312 | 123.111 | -59.0469 | 63.8214 | 0.16479 | 0.0058361 | 0.066731 | 0.066868 | 0.13212 | -0.0032192 | -0.0027877 | 0.3466 | -0.004546 | -0.000391 | -0.0009634 | -0.0010082 | -0.0023927 | 63.7985 | 63.9908 | -0.027466 | -59.23 | 63.7573 | -59.0881 | -59.1293 | -59.0103 | 0.027466 | -59.3079 | 63.7802 | 63.7573 | -59.1202 | -59.2621 | -0.041199 | -0.082397 | -0.064087 | 123.0377 | -0.18311 | -0.10071 | -0.022888 | -0.073242 | -0.21515 | -0.041199 | 0.036621 | -0.26093 | -0.045776 | -0.064087 | 122.8043 | 122.8455 | 59.0195 | -122.9507 | 122.8271 | 122.8043 | 59.0744 | -123.0835
701.5156 | 123.1201 | -59.0607 | 63.8763 | -0.17853 | 0.01139 | 0.070149 | 0.069005 | 0.12849 | 0.0029758 | -0.00065152 | -0.095902 | 0.00036743 | -0.0010318 | -0.0020316 | 0.00027337 | -0.0049561 | 63.7985 | 63.8809 | -0.022888 | -59.2346 | 63.8535 | -59.079 | -59.1385 | -59.0424 | 0.073242 | -59.317 | 63.9038 | 63.8123 | -59.1202 | -59.2575 | -0.01831 | -0.07782 | -0.022888 | 122.9416 | -0.17395 | -0.09613 | -0.07782 | -0.059509 | -0.19684 | 0.027466 | 0.018311 | -0.25635 | -0.05951 | -0.064087 | 122.9141 | 122.8592 | 59.0378 | -123.0148 | 122.9645 | 122.8729 | 59.1339 | -123.1338
702.5156 | 123.0469 | -59.0927 | 63.8901 | 0.14191 | 0.013313 | 0.066518 | 0.071141 | 0.13169 | 0.0019078 | -1.0724e-05 | 0.14824 | -0.001128 | 0.001318 | -0.0005362 | 0.0024096 | -0.0064515 | 63.7344 | 63.8306 | -0.11902 | -59.2804 | 63.8397 | -59.111 | -59.1614 | -59.1248 | -0.38452 | -59.6878 | 63.7894 | 63.7299 | -59.1568 | -59.2712 | -0.018311 | -0.068665 | -0.050354 | 122.9233 | -0.18768 | -0.11902 | -0.15564 | -0.064087 | -0.17853 | -0.10071 | -0.032044 | -0.59509 | -0.41656 | -0.16022 | 122.9324 | 122.8271 | 58.9737 | -123.0515 | 122.8821 | 122.8226 | 58.7082 | -123.1613
703.5156 | 123.0789 | -59.0607 | 63.8947 | -0.1709 | 0.010536 | 0.067372 | 0.070714 | 0.13148 | -0.0012966 | -0.0027877 | -0.080643 | -0.0019824 | -0.0008182 | -0.0003226 | 0.0013416 | -0.0058105 | 63.7848 | 63.8809 | -0.050354 | -59.2529 | 63.8489 | -59.0973 | -59.1476 | -59.0561 | 0.054932 | -59.3353 | 63.8947 | 63.8168 | -59.1385 | -59.2529 | -0.036621 | -0.086975 | -0.045776 | 122.9416 | -0.19226 | -0.10529 | -0.10986 | -0.07782 | -0.19226 | 0 | 0.004578 | -0.27466 | -0.082397 | -0.07782 | 122.9095 | 122.8455 | 59.0103 | -123.0423 | 122.9553 | 122.8775 | 59.1156 | -123.1476
704.5156 | 123.1293 | -59.0378 | 63.8535 | -0.1709 | 0.0066907 | 0.065663 | 0.0658 | 0.12785 | -0.0040738 | -0.0025741 | -0.027237 | -0.0049732 | -0.0023136 | -0.0005362 | 0.00048697 | -0.0011109 | 63.8214 | 64.0182 | 0.073242 | -59.2026 | 63.7985 | -59.0469 | -59.1248 | -58.9966 | 0.16479 | -59.2575 | 63.8489 | 63.7894 | -59.1064 | -59.2026 | -0.009155 | -0.086975 | -0.054932 | 123.056 | -0.16479 | -0.07782 | -0.032044 | -0.068664 | -0.16479 | -0.004578 | 0.041199 | -0.21973 | -0.054931 | -0.064087 | 122.8363 | 122.8592 | 59.111 | -122.9782 | 122.8867 | 122.8271 | 59.2026 | -123.056
705.5156 | 123.0469 | -59.0881 | 63.858 | 0.035095 | 0.012886 | 0.065877 | 0.069645 | 0.12785 | 0.0046848 | 0.00063028 | 0.10246 | -0.0030506 | 0.0004636 | -0.0022452 | 0.0047596 | -0.0041017 | 63.7939 | 63.8947 | -0.050354 | -59.2712 | 63.8351 | -59.079 | -59.1248 | -59.0652 | -0.009155 | -59.3628 | 63.858 | 63.7756 | -59.1431 | -59.2758 | 0.009156 | -0.036621 | -0.022888 | 122.9828 | -0.1831 | -0.14648 | -0.064087 | -0.054931 | -0.18768 | 0 | 0.022888 | -0.27466 | -0.086975 | -0.082397 | 122.9233 | 122.8821 | 59.0378 | -122.9828 | 122.9462 | 122.8638 | 59.079 | -123.1338
706.5156 | 123.0743 | -59.0652 | 63.8992 | -0.21667 | 0.010109 | 0.067159 | 0.069432 | 0.13105 | -0.001083 | -0.0047103 | -0.080643 | -0.0041186 | -0.0008182 | -0.0016044 | 0.0017688 | -0.0023927 | 63.7802 | 63.8947 | -0.032043 | -59.2529 | 63.8626 | -59.1019 | -59.1476 | -59.0652 | 0.064087 | -59.3308 | 63.8809 | 63.8123 | -59.1339 | -59.2621 | -0.036621 | -0.082397 | -0.036621 | 122.9599 | -0.18768 | -0.10529 | -0.11902 | -0.068664 | -0.19684 | -0.018311 | 0 | -0.2655 | -0.068665 | -0.086975 | 122.9279 | 122.8455 | 59.0332 | -123.0469 | 122.9462 | 122.8775 | 59.1293 | -123.1613
707.5156 | 123.0515 | -59.1385 | 63.8718 | 0.14954 | 0.013954 | 0.066091 | 0.069432 | 0.12827 | 0.0036166 | -0.00043792 | 0.094833 | -0.0030506 | 0.001959 | 0.0013864 | 0.0030506 | -0.0053833 | 63.6932 | 63.7985 | -0.17853 | -59.6237 | 63.7619 | -59.1248 | -59.1797 | -59.0698 | -0.10071 | -59.4086 | 63.858 | 63.7619 | -59.1476 | -59.2896 | 0.013733 | -0.041198 | -0.10986 | 122.937 | -0.48523 | -0.44403 | -0.17853 | -0.009155 | -0.15106 | -0.013733 | 0.068665 | -0.27008 | -0.11902 | -0.10986 | 122.9004 | 122.8317 | 58.96 | -123.0515 | 122.9965 | 122.9004 | 59.0378 | -123.1613
708.5156 | 123.0423 | -59.0881 | 63.913 | -0.15564 | 0.0069043 | 0.069295 | 0.066868 | 0.1287 | -0.00044225 | -0.0017197 | -0.057755 | -0.0013416 | -0.0008182 | -0.0016044 | -0.00058103 | -0.0019653 | 63.7619 | 63.8718 | -0.050354 | -59.2575 | 63.8718 | -59.0744 | -59.1202 | -59.0744 | 0.064087 | -59.3399 | 63.8763 | 63.8306 | -59.1156 | -59.2392 | 0.013733 | -0.032043 | -0.041199 | 122.9599 | -0.16937 | -0.13733 | -0.15106 | -0.027466 | -0.15106 | -0.036621 | 0.013733 | -0.25177 | -0.10071 | -0.082398 | 122.9599 | 122.85 | 59.0378 | -123.0331 | 122.9645 | 122.9187 | 59.1522 | -123.1522
709.5156 | 123.0698 | -59.079 | 63.8901 | -0.1709 | 0.0069043 | 0.066945 | 0.0705 | 0.12977 | 0.00041235 | -0.0015061 | 1.0027 | -0.0013416 | 0.0004636 | -0.0007498 | 0.0013416 | -0.0021789 | 63.7619 | 63.9084 | -0.022888 | -59.2621 | 63.8397 | -59.1156 | -59.1339 | -59.0836 | 0.073242 | -59.3582 | 63.8947 | 63.8351 | -59.1476 | -59.2484 | -0.036622 | -0.054932 | -0.050354 | 122.9874 | -0.18311 | -0.12817 | -0.12817 | -0.068665 | -0.16937 | 0.004577 | -0.004578 | -0.27924 | -0.10986 | -0.054932 | 122.9187 | 122.8409 | 59.0561 | -123.024 | 122.9736 | 122.9141 | 59.1522 | -123.1384
710.5312 | 123.1613 | -59.0652 | 63.7939 | 0.62256 | 0.0092541 | 0.070577 | 0.066868 | 0.12956 | -0.00022865 | -0.0023605 | 0.30846 | -0.0049732 | 0.0006772 | 0.0003182 | 0.0024096 | -0.0017517 | 63.826 | 63.9725 | -0.018311 | -59.2117 | 63.7802 | -59.0836 | -59.111 | -58.9783 | 0.050354 | -59.2758 | 63.8031 | 63.7344 | -59.1431 | -59.2575 | -0.01831 | -0.045776 | -0.013733 | 123.0377 | -0.14648 | -0.10071 | 0.032044 | -0.077819 | -0.19226 | 0.009156 | 0.086976 | -0.21057 | -0.018311 | -0.059509 | 122.8455 | 122.8912 | 59.0469 | -122.905 | 122.8683 | 122.7997 | 59.1156 | -123.0515
711.5156 | 123.1476 | -59.0515 | 63.858 | -0.13275 | 0.0079723 | 0.069722 | 0.070073 | 0.13126 | -0.0023648 | -0.0042831 | -0.034867 | -0.0041186 | -0.0016726 | -0.0020316 | -0.0012218 | -0.0021789 | 63.8397 | 64.0228 | 0.07782 | -59.1888 | 63.826 | -59.0652 | -59.079 | -58.9828 | 0.15564 | -59.2438 | 63.8718 | 63.7939 | -59.1202 | -59.2392 | -0.013733 | -0.027465 | -0.032043 | 123.0743 | -0.13733 | -0.10986 | -0.01831 | -0.068664 | -0.18768 | 0.013733 | 0.068665 | -0.19226 | -0.004577 | -0.064087 | 122.8775 | 122.8912 | 59.1293 | -122.937 | 122.9233 | 122.8455 | 59.2072 | -123.0972
712.5156 | 123.0698 | -59.0836 | 63.8672 | 0.0045777 | 0.011177 | 0.068227 | 0.0705 | 0.13105 | 0.0031894 | -0.00043792 | 0.041427 | -0.0036914 | 0.0008908 | 0.0001046 | 0.002196 | -0.0038879 | 63.7894 | 63.8947 | -0.045776 | -59.2621 | 63.8443 | -59.0836 | -59.1339 | -59.0698 | -0.004578 | -59.3628 | 63.8672 | 63.7665 | -59.1431 | -59.2804 | 0 | -0.050354 | -0.022888 | 122.9782 | -0.17853 | -0.12817 | -0.077819 | -0.059509 | -0.19684 | 0 | 0.013733 | -0.27924 | -0.082397 | -0.10071 | 122.9279 | 122.8729 | 59.0378 | -123.0011 | 122.9507 | 122.85 | 59.079 | -123.1476
713.5156 | 123.111 | -59.0836 | 63.8672 | -0.041199 | 0.012672 | 0.064595 | 0.067936 | 0.12806 | 0.0012668 | -0.0019333 | 0.33897 | -0.002196 | 0.001318 | 0.0011728 | 0.0030506 | -0.0047425 | 63.826 | 63.7436 | -0.14191 | -59.2758 | 63.8123 | -59.1293 | -59.1431 | -58.9966 | 0.07782 | -59.317 | 63.858 | 63.7985 | -59.111 | -59.2484 | -0.045776 | -0.059509 | -0.054931 | 122.8271 | -0.19226 | -0.13275 | -0.041198 | -0.027466 | -0.16479 | -0.009155 | 0.086975 | -0.23346 | -0.068665 | -0.068664 | 122.8958 | 122.9095 | 58.9416 | -123.0103 | 122.9416 | 122.8821 | 59.1614 | -123.1155
714.5156 | 123.1796 | -59.024 | 63.8489 | -0.11749 | 0.0054089 | 0.066518 | 0.071141 | 0.12785 | -0.0068508 | -0.0027877 | 0.094833 | -0.0047596 | -0.0033816 | 0.000532 | -0.00015383 | -0.0023927 | 63.826 | 64.0274 | 0.054932 | -59.2117 | 63.8123 | -59.0744 | -59.111 | -58.9417 | 0.1831 | -59.1934 | 63.826 | 63.7527 | -59.0881 | -59.2026 | -0.050354 | -0.086975 | -0.036621 | 123.0515 | -0.18768 | -0.10071 | -0.022888 | -0.064087 | -0.17853 | -0.022888 | 0.082398 | -0.16937 | 0.009156 | -0.09613 | 122.8363 | 122.85 | 59.079 | -122.9599 | 122.85 | 122.7768 | 59.2072 | -123.0515
715.5312 | 123.1659 | -59.0607 | 63.8077 | 0.19531 | 0.0088269 | 0.067586 | 0.063878 | 0.13212 | -0.0036464 | -0.0019333 | 0.2932 | -0.003905 | -0.0012454 | -0.0050222 | 0.0017688 | -0.0011109 | 63.8168 | 63.9725 | -0.018311 | -59.2484 | 63.7527 | -59.0698 | -59.1431 | -58.992 | 0.036621 | -59.2712 | 63.8031 | 63.7207 | -59.1385 | -59.2392 | -0.009155 | -0.082397 | -0.054931 | 123.0331 | -0.18768 | -0.10529 | 0.009155 | -0.07782 | -0.17853 | -0.004577 | 0.068665 | -0.21057 | -0.032043 | -0.086975 | 122.8134 | 122.8775 | 59.0424 | -122.9507 | 122.8638 | 122.7814 | 59.0973 | -123.0469
716.5156 | 123.1659 | -59.0469 | 63.8443 | -0.056458 | 0.0049817 | 0.067159 | 0.065159 | 0.12806 | -0.0040738 | -0.0047103 | -2.606 | -0.0043324 | 0.0008908 | -0.0013906 | -0.0016492 | -0.0038879 | 63.8855 | 64.0549 | 0.086975 | -59.1751 | 63.8031 | -59.0378 | -59.1019 | -58.9005 | 0.041199 | -59.2072 | 63.8351 | 63.7665 | -59.1019 | -59.2163 | 0.009155 | -0.054932 | -0.041198 | 123.1018 | -0.12817 | -0.073242 | 0.041199 | -0.054932 | -0.16937 | -0.009155 | 0.14648 | -0.16022 | 0.009156 | -0.07782 | 122.85 | 122.9324 | 59.1339 | -122.9462 | 122.8821 | 122.8134 | 59.0881 | -123.0606
717.5156 | 123.0789 | -59.0378 | 63.8718 | -0.15564 | 0.0047681 | 0.066304 | 0.069432 | 0.1302 | -0.0021512 | -0.0049239 | -0.10353 | -0.0060412 | -0.0016726 | -0.0016044 | 5.9768e-05 | -0.0026063 | 63.8397 | 64.0045 | 0.054932 | -59.198 | 63.8306 | -59.0744 | -59.1202 | -59.0149 | 0.13733 | -59.285 | 63.8947 | 63.7711 | -59.111 | -59.23 | -0.036621 | -0.082397 | -0.041199 | 123.0423 | -0.16022 | -0.07782 | -0.032043 | -0.073242 | -0.19226 | 0.022888 | 0.022888 | -0.24719 | -0.054931 | -0.10071 | 122.8683 | 122.8775 | 59.0927 | -122.9919 | 122.9324 | 122.8088 | 59.1751 | -123.1018
718.5156 | 123.1293 | -59.0286 | 63.9038 | -0.010681 | 0.0043409 | 0.068654 | 0.068364 | 0.12806 | -0.0038602 | -0.0036423 | 0.026169 | -0.0060412 | -0.0016726 | -0.0013906 | 0.00048697 | -0.0041017 | 63.8489 | 64.0091 | 0.050354 | -59.1934 | 63.7848 | -59.0652 | -59.111 | -58.9417 | 0.17853 | -59.1843 | 63.8763 | 63.739 | -59.0744 | -59.2117 | -0.036622 | -0.082398 | -0.11902 | 123.0377 | -0.1648 | -0.082397 | -0.054932 | -0.045777 | -0.18311 | -0.027466 | 0.086975 | -0.15564 | 0.027466 | -0.1648 | 122.8134 | 122.8775 | 59.079 | -123.0148 | 122.905 | 122.7676 | 59.2072 | -123.1155
719.5156 | 123.0011 | -59.0561 | 63.9175 | -0.20905 | 0.0088269 | 0.068227 | 0.070927 | 0.13169 | -0.0012966 | -0.0025741 | -0.019608 | -0.0049732 | -0.0001774 | -0.001177 | 0.002196 | -0.0030335 | 63.826 | 63.9359 | 0.018311 | -59.2392 | 63.8535 | -59.0927 | -59.1202 | -59.0332 | 0.059509 | -59.3262 | 63.9084 | 63.7985 | -59.1293 | -59.2484 | -0.036621 | -0.064087 | -0.064087 | 122.9919 | -0.18311 | -0.11902 | -0.091553 | -0.073242 | -0.19226 | -0.009156 | 0.022888 | -0.27008 | -0.07782 | -0.11902 | 122.9095 | 122.8821 | 59.0744 | -123.0377 | 122.9645 | 122.8546 | 59.1156 | -123.1659
720.5312 | 123.1888 | -59.0652 | 63.8626 | 0.012207 | 0.0066907 | -0.034312 | 0.064305 | 0.12785 | -0.0019376 | -0.0027877 | 0.11009 | -0.005614 | -0.0023136 | 0.000532 | 0.002837 | -0.0030335 | 63.7802 | 63.9633 | -0.013733 | -59.23 | 63.8123 | -59.0607 | -59.111 | -58.992 | 0.091553 | -59.2529 | 63.8397 | 63.7482 | -59.1202 | -59.2438 | 0.004578 | -0.045776 | -0.050354 | 123.0286 | -0.16479 | -0.11902 | -0.082398 | -0.054931 | -0.17853 | -0.022888 | 0.073243 | -0.18768 | -0.009156 | -0.11444 | 122.8775 | 122.8455 | 59.0515 | -122.9736 | 122.905 | 122.8134 | 59.1568 | -123.1064
721.5156 | 123.0743 | -59.0607 | 63.8855 | -0.15564 | 0.0086133 | 0.067159 | 0.070714 | 0.13148 | 0.0027622 | -0.00086512 | -0.14931 | -0.003905 | -0.000391 | 0.0003182 | 0.002196 | -0.0045289 | 63.7939 | 63.8992 | -0.027466 | -59.2575 | 63.8763 | -59.0744 | -59.1476 | -59.0515 | 0.050354 | -59.3353 | 63.913 | 63.8123 | -59.1156 | -59.2484 | -0.013733 | -0.086975 | -0.009155 | 122.9599 | -0.19684 | -0.10986 | -0.091553 | -0.054932 | -0.18768 | 0.027466 | 0.009155 | -0.27466 | -0.086975 | -0.073242 | 122.937 | 122.8546 | 59.0332 | -123.0331 | 122.9736 | 122.8729 | 59.111 | -123.1338
722.5156 | 123.2071 | -59.0469 | 63.8763 | -0.018311 | 0.0036999 | 0.0678 | 0.066868 | 0.12913 | -0.0030056 | -0.0021469 | 0.079574 | -0.0041186 | -0.0053042 | 0.0001046 | -0.0016492 | -0.0013245 | 63.8031 | 63.9771 | -0.004578 | -59.2209 | 63.8077 | -59.0881 | -59.111 | -58.9645 | 0.091553 | -59.2346 | 63.8168 | 63.7207 | -59.1568 | -59.2438 | -0.041199 | -0.064087 | -0.068665 | 123.024 | -0.17395 | -0.10986 | -0.073242 | -0.10986 | -0.19684 | -0.05951 | 0.082397 | -0.18768 | 0.009155 | -0.15564 | 122.8546 | 122.85 | 59.0424 | -122.9874 | 122.8638 | 122.7676 | 59.1385 | -123.1201
723.5156 | 123.1842 | -59.0515 | 63.8718 | -0.12512 | 0.0069043 | 0.066518 | 0.067296 | 0.12763 | -0.00065585 | -0.0017197 | -0.073013 | -0.0032642 | -0.0040226 | -0.0026724 | -0.00015383 | -0.0068787 | 63.8626 | 64.0366 | 0.064087 | -59.1888 | 63.8351 | -59.0836 | -59.0836 | -58.992 | 0.15106 | -59.2621 | 63.8718 | 63.7665 | -59.1293 | -59.23 | -0.032043 | -0.032043 | -0.036621 | 123.0881 | -0.13733 | -0.10529 | -0.009155 | -0.077819 | -0.17853 | 0 | 0.05951 | -0.21057 | -0.032043 | -0.10529 | 122.8867 | 122.9141 | 59.1156 | -122.9553 | 122.9233 | 122.818 | 59.2026 | -123.1018
724.5156 | 123.1888 | -59.0286 | 63.8397 | -0.13275 | 0.0054089 | 0.070577 | 0.069432 | 0.12892 | -0.0017238 | -0.0021469 | 0.064316 | -0.0047596 | -0.0012454 | -0.0005362 | 0.002196 | -0.0034607 | 63.8718 | 64.0778 | -0.082397 | -58.9096 | 63.8809 | -59.024 | -59.0881 | -58.9828 | 0.16937 | -59.2163 | 63.8397 | 63.7436 | -59.0973 | -59.2346 | 0.004577 | -0.05951 | 0.041198 | 123.1064 | 0.11902 | 0.17853 | 0.032043 | -0.068665 | -0.20599 | 0 | 0.045776 | -0.18768 | 0.01831 | -0.096131 | 122.9095 | 122.9004 | 58.9462 | -122.9279 | 122.8683 | 122.7722 | 59.198 | -123.0743
725.5312 | 123.1567 | -59.0286 | 63.8672 | -0.15564 | 0.0062635 | 0.066091 | 0.06815 | 0.12827 | -0.00065585 | -0.0012923 | -0.050125 | -0.007323 | -0.0021 | -0.0030996 | 0.0019824 | -0.0064515 | 63.8535 | 64.0228 | 0.068665 | -59.1934 | 63.8168 | -59.0652 | -59.1202 | -58.9645 | 0.15564 | -59.2484 | 63.8535 | 63.7665 | -59.111 | -59.23 | -0.036622 | -0.091553 | -0.050354 | 123.0515 | -0.1648 | -0.073242 | -0.013732 | -0.082398 | -0.20142 | -0.013732 | 0.064086 | -0.21973 | -0.01831 | -0.10071 | 122.8455 | 122.8821 | 59.0973 | -122.9874 | 122.8821 | 122.7951 | 59.1843 | -123.0972
726.5156 | 123.1293 | -59.0607 | 63.8397 | 0.09613 | 0.0041271 | 0.069081 | 0.065373 | 0.12849 | -0.00065585 | -0.0017197 | 0.1635 | -0.004546 | -0.0023136 | -0.0020316 | 0.00027337 | -0.0038879 | 63.7115 | 63.9542 | -0.032043 | -59.2484 | 63.8077 | -59.0698 | -59.1156 | -59.0103 | 0.041199 | -59.2758 | 63.8031 | 63.7299 | -59.1064 | -59.2529 | -0.009155 | -0.054932 | -0.032044 | 123.0148 | -0.18768 | -0.13275 | -0.12817 | -0.045776 | -0.19226 | -0.036621 | 0.050354 | -0.21515 | -0.022888 | -0.10986 | 122.8683 | 122.7722 | 59.0286 | -122.9553 | 122.8638 | 122.7905 | 59.1019 | -123.0927
727.5156 | 123.1338 | -59.0378 | 63.8809 | -0.14801 | 0.0058361 | 0.06844 | 0.070073 | 0.12849 | -0.0015102 | -0.0034287 | -0.11116 | -0.0036914 | -0.0025272 | -0.0022452 | -0.00058103 | -0.0060243 | 63.8626 | 64.0274 | 0.07782 | -59.1843 | 63.8214 | -59.0698 | -59.0927 | -58.9737 | 0.15564 | -59.2484 | 63.8718 | 63.7573 | -59.0973 | -59.2117 | -0.032043 | -0.054931 | -0.059509 | 123.0652 | -0.14648 | -0.091553 | -0.01831 | -0.059509 | -0.17395 | -0.009155 | 0.064087 | -0.21057 | -0.036621 | -0.1236 | 122.8592 | 122.9004 | 59.1156 | -122.9736 | 122.9095 | 122.7951 | 59.1934 | -123.0927
728.5156 | 123.1888 | -59.0515 | 63.8763 | -0.14038 | 0.0069043 | 0.066945 | 0.067296 | 0.1287 | -0.00086945 | -0.0019333 | -0.080643 | -0.002837 | -0.0025272 | -0.0013906 | 0.0013416 | -0.0060243 | 63.8718 | 64.0228 | 0.09613 | -59.1888 | 63.8031 | -59.0652 | -59.111 | -58.9462 | 0.17395 | -59.2392 | 63.8397 | 63.7756 | -59.0881 | -59.2163 | -0.013733 | -0.059509 | -0.073242 | 123.0743 | -0.13733 | -0.07782 | -0.004578 | -0.036621 | -0.1648 | -0.036621 | 0.10529 | -0.18768 | -0.022888 | -0.10071 | 122.8546 | 122.9233 | 59.1476 | -122.9874 | 122.8912 | 122.8271 | 59.2255 | -123.0927
729.5156 | 123.0789 | -59.0378 | 63.8031 | 0.0045777 | 0.0043409 | 0.067586 | 0.067082 | 0.13126 | -0.0030056 | -0.0034287 | 0.056686 | -0.0026234 | -0.0027408 | 0.000532 | 0.00070077 | -0.0038879 | 63.8809 | 64.0594 | 0.07782 | -59.1888 | 63.8031 | -59.0515 | -59.1019 | -58.905 | 0.17395 | -59.1797 | 63.8306 | 63.7436 | -59.0515 | -59.1934 | -0.013733 | -0.064087 | 0 | 123.0972 | -0.15106 | -0.086975 | 0.077819 | -0.013733 | -0.15564 | 0.027465 | 0.13275 | -0.14191 | 0.013733 | -0.05951 | 122.8409 | 122.9187 | 59.1156 | -122.905 | 122.8683 | 122.7814 | 59.2117 | -122.9965
730.5312 | 123.1705 | -59.0515 | 63.826 | 0.2182 | 0.011604 | 0.065663 | 0.069218 | 0.12956 | 0.0027622 | 0.00063028 | 0.17876 | -0.0032642 | 0.0006772 | -0.0022452 | 0.0026234 | -0.0049561 | 63.7894 | 63.9084 | -0.086975 | -59.2667 | 63.8168 | -59.0881 | -59.1614 | -58.9828 | 0.004578 | -59.3216 | 63.8443 | 63.7299 | -59.1385 | -59.2346 | -0.036621 | -0.10986 | -0.009156 | 122.9599 | -0.21515 | -0.10529 | -0.036621 | -0.086975 | -0.18311 | 0.01831 | 0.068665 | -0.27008 | -0.086975 | -0.096131 | 122.8683 | 122.8409 | 58.9645 | -122.9874 | 122.8958 | 122.7814 | 59.0561 | -123.0606
731.5156 | 123.1705 | -59.024 | 63.826 | -0.12512 | 0.0043409 | 0.068868 | 0.066227 | 0.13062 | -0.004501 | -0.0021469 | 0.2932 | -0.0036914 | -0.0046634 | -0.0016044 | 0.00048697 | -0.0038879 | 63.8855 | 64.0778 | 0.091553 | -59.1843 | 63.826 | -59.0515 | -59.0515 | -58.9096 | 0.10529 | -59.2163 | 63.8397 | 63.739 | -59.0973 | -59.2163 | -0.027466 | -0.027466 | 0 | 123.1018 | -0.16022 | -0.13275 | 0.059509 | -0.073242 | -0.19226 | 0.013733 | 0.11444 | -0.19226 | 0 | -0.086975 | 122.85 | 122.9095 | 59.1156 | -122.8775 | 122.8638 | 122.7631 | 59.1293 | -123.0423
732.5156 | 123.1522 | -59.0698 | 63.8306 | -0.25482 | 0.0056225 | 0.065022 | 0.067936 | 0.13169 | 0.00019875 | -0.0019333 | 0.14824 | -0.0041186 | -0.0027408 | -0.0003226 | 0.001128 | -0.0041017 | 63.7848 | 63.9542 | -0.027466 | -59.2438 | 63.7985 | -59.0881 | -59.1156 | -58.992 | 0.054932 | -59.2712 | 63.8351 | 63.7665 | -59.1156 | -59.2484 | -0.018311 | -0.045777 | -0.032043 | 123.024 | -0.17395 | -0.12817 | -0.045776 | -0.045777 | -0.17853 | 0.004578 | 0.07782 | -0.20142 | -0.022888 | -0.064087 | 122.8683 | 122.8546 | 59.0424 | -122.9462 | 122.905 | 122.8363 | 59.1248 | -123.0789
733.5156 | 123.1934 | -59.0378 | 63.8351 | 0.24109 | 0.0058361 | 0.066945 | 0.067296 | 0.12934 | -0.0025784 | -0.0032151 | -0.027237 | -0.0058276 | -0.0038088 | -0.0009634 | 0.00070077 | -0.0049561 | 63.8809 | 64.0411 | 0.091553 | -59.1797 | 63.8168 | -59.0561 | -59.111 | -58.9371 | 0.1831 | -59.2346 | 63.8626 | 63.7299 | -59.0836 | -59.2163 | -0.01831 | -0.073242 | -0.018311 | 123.0789 | -0.14191 | -0.068664 | 0.045776 | -0.045776 | -0.17853 | 0.027466 | 0.10071 | -0.19684 | -0.01831 | -0.10529 | 122.8546 | 122.9187 | 59.1293 | -122.9462 | 122.9004 | 122.7676 | 59.2209 | -123.0515
734.5156 | 123.1293 | -59.0378 | 63.8443 | 0.10376 | 0.0049817 | 0.067159 | 0.066227 | 0.12892 | -0.0023648 | -0.0038559 | 0.33897 | -0.0036914 | -0.0029544 | -0.0020316 | 0.0030506 | -0.0028199 | 63.7894 | 63.9679 | 0 | -59.0836 | 63.8626 | -59.0469 | -59.1019 | -59.0057 | 0.013733 | -59.2941 | 63.8351 | 63.7344 | -59.1431 | -59.2667 | -0.009155 | -0.064087 | 0.018311 | 123.0057 | -0.045776 | 0.018311 | -0.054931 | -0.10528 | -0.22888 | -0.009155 | 0.032044 | -0.25635 | -0.027465 | -0.10986 | 122.9004 | 122.8271 | 59.0378 | -122.9462 | 122.8729 | 122.7722 | 59.0515 | -123.111
735.5312 | 123.1247 | -59.0744 | 63.826 | 0.21057 | 0.010963 | 0.066091 | 0.070714 | 0.12678 | 0.0038304 | 0.00041648 | 0.23979 | -0.002837 | -0.0006046 | -0.001177 | 0.0026234 | -0.0053833 | 63.7985 | 63.8901 | -0.09613 | -59.2987 | 63.8397 | -59.1064 | -59.1614 | -59.0057 | -0.018311 | -59.3308 | 63.8214 | 63.7253 | -59.1431 | -59.2712 | -0.032043 | -0.086975 | 0.013733 | 122.9645 | -0.2243 | -0.13733 | -0.027466 | -0.068664 | -0.19684 | -0.004578 | 0.068665 | -0.25635 | -0.05951 | -0.10071 | 122.9141 | 122.8729 | 58.9783 | -122.9874 | 122.8958 | 122.7997 | 59.0561 | -123.0972
736.5156 | 123.2162 | -59.024 | 63.8397 | -0.20142 | 0.0043409 | 0.068227 | 0.066868 | 0.12892 | -0.00065585 | -0.0010787 | -0.042496 | -0.0047596 | -0.0040226 | -0.0013906 | -0.00079463 | -0.0043153 | 63.8718 | 64.0457 | 0.082397 | -59.1888 | 63.7985 | -59.0652 | -59.0836 | -58.7585 | -0.22888 | -59.3262 | 63.8031 | 63.7161 | -59.111 | -59.2072 | -0.041199 | -0.059509 | -0.041199 | 123.0698 | -0.16479 | -0.10529 | 0.032043 | -0.086975 | -0.1831 | -0.036621 | 0.2655 | -0.30212 | -0.11902 | -0.1236 | 122.8226 | 122.8958 | 59.1064 | -122.9233 | 122.8271 | 122.7402 | 58.7952 | -123.0469
737.5156 | 123.175 | -59.0378 | 63.8535 | -0.018311 | 0.0041271 | 0.0678 | 0.0658 | 0.12614 | -0.0034328 | -0.0030013 | 0.079574 | -0.0054004 | -0.0046634 | -0.0033134 | 0.00048697 | -0.0045289 | 63.8214 | 63.9954 | 0 | -59.2255 | 63.8306 | -59.0607 | -59.1202 | -58.96 | 0.10986 | -59.2575 | 63.8168 | 63.7527 | -59.0973 | -59.23 | -0.022888 | -0.082397 | -0.022889 | 123.0331 | -0.18768 | -0.10529 | -0.032044 | -0.059509 | -0.19226 | -0.036622 | 0.07782 | -0.21973 | -0.027465 | -0.10071 | 122.8683 | 122.8592 | 59.0378 | -122.9736 | 122.8546 | 122.7905 | 59.1476 | -123.0835
738.5156 | 123.1476 | -59.0469 | 63.8535 | 0.073242 | 0.0062635 | 0.069295 | 0.069645 | 0.12742 | -0.0012966 | -0.0032151 | 0.38475 | -0.0032642 | 0.0004636 | -0.001177 | 0.001128 | -0.0023927 | 63.8077 | 64.0732 | 0.11444 | -59.1293 | 63.8397 | -59.0424 | -59.0973 | -59.0195 | 0.045776 | -59.3079 | 63.8626 | 63.7344 | -59.1339 | -59.2575 | 0.004578 | -0.050354 | -0.013733 | 123.1201 | -0.082397 | -0.032043 | -0.045777 | -0.086975 | -0.21057 | 0.009155 | 0.027466 | -0.26093 | -0.050354 | -0.11902 | 122.8867 | 122.8546 | 59.1614 | -122.9507 | 122.9095 | 122.7814 | 59.0927 | -123.111
739.5156 | 123.143 | -59.0378 | 63.8397 | 0.012207 | 0.0062635 | 0.068654 | 0.066014 | 0.12892 | -0.0015102 | -0.0019333 | 0.10246 | -0.0051868 | -0.004877 | -0.0024588 | 0.00070077 | -0.0038879 | 63.7985 | 63.945 | -0.036621 | -59.2163 | 63.7894 | -59.0744 | -59.1248 | -58.9737 | 0.068665 | -59.2712 | 63.8077 | 63.7299 | -59.1156 | -59.2484 | -0.036621 | -0.086975 | -0.050354 | 122.9828 | -0.17853 | -0.091553 | -0.041199 | -0.07782 | -0.21057 | -0.032044 | 0.064087 | -0.23346 | -0.022888 | -0.10986 | 122.8271 | 122.8363 | 59.0012 | -122.9645 | 122.8455 | 122.7676 | 59.1064 | -123.0881
740.5156 | 123.0881 | -59.0607 | 63.8718 | -0.17853 | 0.010109 | 0.066518 | 0.070073 | 0.12785 | 0.0031894 | -0.00086512 | -0.16457 | -0.0024096 | 0.0017454 | -0.000109 | 0.003905 | -0.0051697 | 63.8168 | 63.9084 | -0.018311 | -59.2484 | 63.8535 | -59.0973 | -59.1202 | -59.024 | 0.073242 | -59.3353 | 63.8992 | 63.7939 | -59.1385 | -59.2392 | -0.036621 | -0.059509 | -0.01831 | 122.9691 | -0.18768 | -0.12817 | -0.054932 | -0.07782 | -0.17853 | 0.027466 | 0.036621 | -0.27466 | -0.09613 | -0.07782 | 122.9141 | 122.8775 | 59.0424 | -122.9919 | 122.9599 | 122.8546 | 59.1339 | -123.111
741.5156 | 123.2025 | -59.0012 | 63.8718 | -0.1709 | 0.0054089 | 0.069936 | 0.063878 | 0.12849 | -0.0021512 | -0.00043792 | -0.011978 | -0.0041186 | -0.0027408 | -0.002886 | 0.0019824 | -0.0051697 | 63.8535 | 64.032 | 0.09613 | -59.1934 | 63.8077 | -59.0515 | -59.0836 | -58.9279 | 0.17395 | -59.2026 | 63.826 | 63.7527 | -59.1248 | -59.2117 | -0.050354 | -0.082397 | -0.064087 | 123.0331 | -0.19226 | -0.10986 | -0.01831 | -0.1236 | -0.21057 | -0.045776 | 0.073243 | -0.20142 | 0.009155 | -0.11902 | 122.8088 | 122.8546 | 59.0973 | -122.9553 | 122.8271 | 122.7539 | 59.1751 | -123.0835
742.5156 | 123.1476 | -59.0652 | 63.8443 | 0.20294 | 0.0069043 | 0.066304 | 0.066655 | 0.12913 | -0.0015102 | -0.00086512 | 0.27031 | -0.0036914 | -0.0018862 | -0.0016044 | 0.002196 | -0.0036743 | 63.7939 | 63.9633 | -0.036621 | -59.2438 | 63.7802 | -59.1019 | -59.1431 | -58.9783 | 0.032043 | -59.2987 | 63.8123 | 63.707 | -59.1385 | -59.2667 | -0.036621 | -0.077819 | -0.064087 | 123.0286 | -0.17853 | -0.10071 | -0.050354 | -0.073242 | -0.20142 | -0.032043 | 0.086976 | -0.23346 | -0.032043 | -0.13733 | 122.8455 | 122.8592 | 59.0286 | -122.9874 | 122.8775 | 122.7722 | 59.0973 | -123.111
743.5156 | 123.1705 | -59.0515 | 63.8168 | 0.012207 | 0.0077587 | 0.070149 | 0.069859 | 0.12998 | -0.0032192 | -0.0038559 | 0.14061 | -0.0036914 | -0.0018862 | -0.0013906 | 0.0015552 | -0.0032471 | 63.7939 | 63.945 | -0.013733 | -59.23 | 63.8031 | -59.0927 | -59.111 | -58.9966 | 0.07782 | -59.2712 | 63.8443 | 63.7344 | -59.1248 | -59.2621 | -0.041198 | -0.059509 | -0.013732 | 122.9965 | -0.17853 | -0.11902 | -0.022888 | -0.073242 | -0.21057 | 0.027466 | 0.054932 | -0.21973 | -0.009155 | -0.082397 | 122.8546 | 122.8455 | 59.0378 | -122.9279 | 122.8958 | 122.7859 | 59.1293 | -123.0789
744.5156 | 123.1842 | -59.024 | 63.826 | -0.02594 | 0.0054089 | 0.068868 | 0.065587 | 0.12892 | -0.0017238 | -0.0040695 | 0.064316 | -0.003905 | -0.0027408 | -0.0026724 | 0.0030506 | -0.0026063 | 63.8306 | 63.9771 | 0.009155 | -59.2163 | 63.8214 | -59.0744 | -59.1019 | -58.9645 | 0.09613 | -59.2392 | 63.8214 | 63.7299 | -59.1156 | -59.2163 | -0.050354 | -0.07782 | -0.004578 | 123.0011 | -0.19226 | -0.11444 | 0.004577 | -0.091553 | -0.19226 | -0.004578 | 0.059509 | -0.21515 | -0.022888 | -0.096131 | 122.8455 | 122.8546 | 59.0332 | -122.9279 | 122.8455 | 122.7539 | 59.1202 | -123.0423
745.5156 | 123.1201 | -59.0652 | 63.8489 | -0.26245 | 0.015663 | 0.065663 | 0.070714 | 0.12977 | 0.0063938 | 0.0036209 | -0.042496 | -0.00048697 | -0.000391 | -0.001177 | 0.0041186 | -0.0068787 | 63.8672 | 63.9359 | -0.004578 | -59.2346 | 63.8535 | -59.1064 | -59.1248 | -58.9874 | 0.059509 | -59.3353 | 63.8809 | 63.7665 | -59.1522 | -59.2484 | -0.041198 | -0.059509 | 0.004578 | 123.0011 | -0.16937 | -0.10986 | 0.01831 | -0.086975 | -0.1831 | 0.032043 | 0.07782 | -0.27008 | -0.086975 | -0.082398 | 122.9187 | 122.9324 | 59.0607 | -122.9736 | 122.9462 | 122.8317 | 59.1248 | -123.0972
746.5156 | 123.1842 | -59.0469 | 63.8031 | 0.14191 | 0.0083997 | 0.06545 | 0.0658 | 0.12977 | -1.505e-05 | -0.00086512 | 0.27031 | -0.0019824 | -0.0029544 | -0.0009634 | 0.0024096 | -0.0041017 | 63.8397 | 63.9725 | -0.018311 | -59.23 | 63.7665 | -59.1064 | -59.1248 | -58.9417 | 0.050354 | -59.2621 | 63.8214 | 63.7024 | -59.1293 | -59.2438 | -0.059509 | -0.07782 | -0.036622 | 123.0194 | -0.18311 | -0.10529 | 0.036621 | -0.082397 | -0.19684 | 0.01831 | 0.10529 | -0.21515 | -0.018311 | -0.10071 | 122.8134 | 122.8867 | 59.0286 | -122.9279 | 122.8683 | 122.7493 | 59.0973 | -123.0469
747.5156 | 123.1522 | -59.0378 | 63.826 | 0.14954 | 0.0051953 | 0.066945 | 0.069005 | 0.13105 | -0.001083 | -0.0019333 | 0.15587 | -0.0030506 | -0.0040226 | -0.0003226 | 5.9768e-05 | -0.0034607 | 63.7939 | 63.9404 | -0.050354 | -59.2667 | 63.8031 | -59.0836 | -59.1248 | -58.9966 | 0.027466 | -59.3033 | 63.7985 | 63.7207 | -59.1293 | -59.2346 | -0.045776 | -0.086975 | -0.022888 | 122.9782 | -0.22888 | -0.14191 | -0.032044 | -0.091552 | -0.19684 | -0.027466 | 0.041199 | -0.2655 | -0.068665 | -0.10529 | 122.8409 | 122.8317 | 58.9874 | -122.9507 | 122.8363 | 122.7585 | 59.0652 | -123.0606
748.5156 | 123.1338 | -59.0378 | 63.8306 | 0.2182 | 0.0077587 | 0.067586 | 0.067509 | 0.12742 | -1.505e-05 | -0.0027877 | 0.22453 | -0.0030506 | -0.0012454 | -0.0013906 | 0.002196 | -0.0030335 | 63.826 | 63.9404 | -0.050354 | -59.2575 | 63.7848 | -59.0973 | -59.1248 | -58.9966 | 0.018311 | -59.2941 | 63.8351 | 63.7344 | -59.1248 | -59.2484 | -0.059509 | -0.086975 | -0.045776 | 122.9782 | -0.21973 | -0.13275 | -0.004577 | -0.086975 | -0.21057 | 0.004578 | 0.041199 | -0.25635 | -0.045776 | -0.09613 | 122.8226 | 122.8638 | 58.9874 | -122.9553 | 122.8729 | 122.7722 | 59.0561 | -123.0789
749.5156 | 123.1934 | -59.0286 | 63.8443 | -0.033569 | 0.0043409 | 0.067586 | 0.066441 | 0.13212 | -0.00086945 | -0.0047103 | 0.026169 | -0.003905 | -0.0044498 | -0.0003226 | 0.0019824 | -0.0036743 | 63.8535 | 64.0091 | 0.050354 | -59.2163 | 63.826 | -59.079 | -59.111 | -58.9417 | 0.16022 | -59.1888 | 63.8214 | 63.7436 | -59.0927 | -59.2163 | -0.050354 | -0.082398 | -0.01831 | 123.0377 | -0.18768 | -0.10529 | 0.009156 | -0.064087 | -0.18768 | -0.022888 | 0.086975 | -0.16022 | 0.027466 | -0.10071 | 122.8546 | 122.8821 | 59.079 | -122.9553 | 122.85 | 122.7722 | 59.1888 | -123.0606
750.5156 | 123.1842 | -59.0332 | 63.826 | 0.0045777 | 0.0047681 | 0.071858 | 0.066655 | 0.12998 | -0.0017238 | -0.0023605 | 0.064316 | -0.003905 | -0.0042362 | -0.0007498 | 0.0013416 | -0.0041017 | 63.8535 | 64.0091 | 0.027466 | -59.2117 | 63.8123 | -59.0744 | -59.1202 | -58.9554 | 0.13275 | -59.2346 | 63.8306 | 63.7299 | -59.1202 | -59.23 | -0.041199 | -0.086975 | -0.013733 | 123.0423 | -0.17853 | -0.091553 | 0.027466 | -0.086975 | -0.19684 | 0.004577 | 0.07782 | -0.20142 | -0.004577 | -0.096131 | 122.8455 | 122.8867 | 59.0607 | -122.9462 | 122.8638 | 122.7631 | 59.166 | -123.056
751.5156 | 123.1476 | -59.0149 | 63.8306 | 1.3779 | 0.0073315 | 0.068654 | 0.067296 | 0.12507 | -0.0025784 | -0.0030013 | 0.11009 | -0.0054004 | -0.0006046 | -0.0003226 | 0.0049732 | -0.0034607 | 63.7848 | 63.9175 | -0.050354 | -59.2621 | 63.7894 | -59.0698 | -59.1156 | -59.0057 | 0.036621 | -59.2758 | 63.8535 | 63.7344 | -59.1476 | -59.2255 | -0.054931 | -0.10071 | -0.041198 | 122.9324 | -0.24719 | -0.14648 | -0.045776 | -0.13275 | -0.21057 | 0.022889 | 0.009156 | -0.26093 | -0.050354 | -0.09613 | 122.8043 | 122.7997 | 58.9645 | -122.9462 | 122.8683 | 122.7493 | 59.0515 | -123.056
752.5156 | 123.1979 | -59.0652 | 63.7802 | 0.19531 | 0.011604 | 0.067372 | 0.067509 | 0.12913 | 0.0021214 | -0.0010787 | 0.26268 | -0.0026234 | -0.0012454 | -0.0020316 | 0.0015552 | -0.0070923 | 63.8626 | 63.9816 | -0.022888 | -59.2438 | 63.7527 | -59.0927 | -59.1019 | -58.9371 | 0.041199 | -59.2758 | 63.7985 | 63.6887 | -59.1431 | -59.2575 | -0.027465 | -0.036621 | -0.027465 | 123.0469 | -0.17853 | -0.14191 | 0.082398 | -0.077819 | -0.19226 | 0.018311 | 0.12817 | -0.21057 | -0.018311 | -0.091552 | 122.818 | 122.9279 | 59.0424 | -122.8821 | 122.8638 | 122.7539 | 59.1064 | -123.0377
753.5156 | 123.1338 | -59.0378 | 63.8168 | 0.057983 | 0.0062635 | 0.070577 | 0.067082 | 0.12806 | -0.0023648 | -0.0017197 | 0.15587 | -0.006255 | -0.0055178 | -0.0016044 | -0.0014356 | -0.0036743 | 63.8214 | 63.9542 | -0.050354 | -59.2529 | 63.8214 | -59.0927 | -59.111 | -58.8226 | -0.16022 | -59.2758 | 63.8168 | 63.7482 | -59.1064 | -59.2209 | -0.054931 | -0.073242 | 0.004578 | 122.9919 | -0.21515 | -0.14191 | 0.004578 | -0.068664 | -0.1831 | 0 | 0.21515 | -0.23804 | -0.054932 | -0.068664 | 122.8592 | 122.8592 | 58.9874 | -122.9279 | 122.8546 | 122.7859 | 58.8776 | -123.0377
754.5156 | 123.1842 | -59.0561 | 63.7985 | 0.19531 | 0.012459 | 0.064809 | 0.069005 | 0.12956 | 0.0021214 | -0.00043792 | 0.24742 | -0.004546 | -0.0001774 | -0.0009634 | 0.0034778 | -0.0038879 | 63.8489 | 63.9954 | 0 | -59.2346 | 63.7665 | -59.0561 | -59.1248 | -58.9462 | 0.045776 | -59.2484 | 63.8214 | 63.707 | -59.1202 | -59.2484 | 0 | -0.068665 | -0.032044 | 123.0515 | -0.17853 | -0.10986 | 0.050354 | -0.064087 | -0.19226 | 0.022888 | 0.10986 | -0.19226 | 0 | -0.091553 | 122.8226 | 122.905 | 59.0561 | -122.9233 | 122.8775 | 122.7631 | 59.1019 | -123.0469
755.5312 | 123.056 | -59.0744 | 63.8947 | -0.18616 | 0.0083997 | 0.069295 | 0.071141 | 0.12998 | 0.00062595 | -0.00086512 | -0.095902 | -0.00027337 | -0.0018862 | -0.0005362 | 0.00091437 | -0.0068787 | 63.8214 | 63.9084 | 0 | -59.2484 | 63.8672 | -59.0836 | -59.1339 | -59.0332 | 0.07782 | -59.3079 | 63.9359 | 63.8535 | -59.0927 | -59.2255 | -0.009155 | -0.059509 | -0.027466 | 122.9828 | -0.17395 | -0.11444 | -0.073242 | -0.01831 | -0.15106 | 0.041199 | 0.041199 | -0.23346 | -0.082397 | -0.041198 | 122.9416 | 122.8958 | 59.0744 | -123.0286 | 123.0103 | 122.9279 | 59.1522 | -123.1201
756.5156 | 123.175 | -59.0561 | 63.7985 | 0.18005 | 0.010536 | 0.0678 | 0.065587 | 0.12742 | 0.00083955 | -0.0015061 | 0.23979 | -0.0049732 | -0.0029544 | -0.0026724 | 0.001128 | -0.0051697 | 63.8489 | 63.9862 | -0.009155 | -59.2346 | 63.7894 | -59.0973 | -59.1019 | -58.96 | 0.045776 | -59.2712 | 63.8168 | 63.707 | -59.1293 | -59.2621 | -0.041199 | -0.045777 | -0.009155 | 123.0423 | -0.17853 | -0.13275 | 0.050354 | -0.073242 | -0.20599 | 0.01831 | 0.09613 | -0.21515 | -0.009155 | -0.091553 | 122.8455 | 122.905 | 59.0469 | -122.9004 | 122.8729 | 122.7631 | 59.1019 | -123.0606
757.5156 | 123.1567 | -59.0469 | 63.8489 | -0.041199 | 0.0024181 | 0.069936 | 0.06815 | 0.12934 | -0.0023648 | -0.0010787 | 0.12535 | -0.0041186 | -0.0027408 | -0.0005362 | 0.00070077 | -0.0043153 | 63.7985 | 63.945 | -0.027466 | -59.23 | 63.8123 | -59.0698 | -59.1156 | -59.0057 | 0.064087 | -59.2667 | 63.8168 | 63.7527 | -59.1522 | -59.2529 | -0.022888 | -0.068665 | -0.036621 | 122.9919 | -0.18311 | -0.11444 | -0.050354 | -0.10529 | -0.20599 | -0.032044 | 0.041199 | -0.21973 | -0.013733 | -0.09613 | 122.8592 | 122.8455 | 59.0195 | -122.9645 | 122.8638 | 122.7997 | 59.111 | -123.1018
758.5156 | 123.1522 | -59.079 | 63.826 | 0.17242 | 0.0064771 | 0.069081 | 0.067509 | 0.1287 | -0.0021512 | -0.0010787 | 0.1635 | -0.0041186 | -0.0044498 | -0.0022452 | 0.0013416 | -0.0047425 | 63.8077 | 63.945 | -0.050354 | -59.2667 | 63.7985 | -59.0698 | -59.111 | -59.0012 | 0.036621 | -59.285 | 63.826 | 63.7344 | -59.1522 | -59.2346 | 0.009155 | -0.032044 | -0.027466 | 123.024 | -0.18768 | -0.15564 | -0.018311 | -0.073243 | -0.15564 | 0 | 0.077819 | -0.20599 | -0.050354 | -0.091553 | 122.8775 | 122.8867 | 59.0286 | -122.937 | 122.905 | 122.8134 | 59.1156 | -123.0606
759.5156 | 123.0972 | -59.0469 | 63.8031 | 0.19531 | 0.0047681 | 0.069722 | 0.066655 | 0.12977 | -0.001083 | -0.00065152 | 0.26268 | -0.0047596 | -0.003168 | -0.001177 | 0.0024096 | -0.0049561 | 63.826 | 63.9542 | -0.036621 | -59.2575 | 63.7985 | -59.0881 | -59.0973 | -59.0057 | 0.013733 | -59.2941 | 63.8168 | 63.7161 | -59.111 | -59.23 | -0.041199 | -0.050354 | -0.004578 | 123.0011 | -0.21057 | -0.16022 | 0.022888 | -0.064087 | -0.18311 | 0.013732 | 0.041199 | -0.24719 | -0.064086 | -0.086976 | 122.8455 | 122.8729 | 59.0103 | -122.9004 | 122.8638 | 122.7631 | 59.0607 | -123.0331
760.5156 | 123.1384 | -59.0103 | 63.8535 | -0.14801 | 0.0054089 | 0.067159 | 0.065373 | 0.13062 | -0.00044225 | -0.0025741 | -0.095902 | -0.003905 | -0.0038088 | -0.0033134 | 0.002837 | -0.0062379 | 63.8855 | 64.0228 | 0.07782 | -59.1751 | 63.8214 | -59.0515 | -59.0927 | -58.9691 | 0.16937 | -59.2346 | 63.8626 | 63.7939 | -59.1202 | -59.2438 | -0.041199 | -0.082397 | -0.032044 | 123.0331 | -0.16479 | -0.082398 | 0.032043 | -0.10986 | -0.23346 | 0.009155 | 0.041199 | -0.2243 | 0.009155 | -0.05951 | 122.8317 | 122.8958 | 59.0881 | -122.9462 | 122.8729 | 122.8043 | 59.1797 | -123.0972
761.5156 | 123.1201 | -59.0652 | 63.8168 | 0.15717 | 0.0060497 | 0.066304 | 0.065587 | 0.12934 | -0.00065585 | -0.00065152 | 0.28557 | -0.004546 | -0.0027408 | 0.0011728 | 0.0047596 | -0.0041017 | 63.826 | 63.9816 | -0.027466 | -59.2438 | 63.7573 | -59.111 | -59.111 | -58.9783 | 0.050354 | -59.2987 | 63.7894 | 63.7161 | -59.1339 | -59.2392 | -0.045776 | -0.045776 | -0.059509 | 123.0469 | -0.17853 | -0.13275 | 0.009156 | -0.068664 | -0.17395 | -0.027465 | 0.086976 | -0.23346 | -0.059509 | -0.10071 | 122.8226 | 122.8912 | 59.0378 | -122.9279 | 122.8546 | 122.7814 | 59.1156 | -123.056
762.5156 | 123.1796 | -59.0836 | 63.7939 | 0.20294 | 0.01139 | 0.067586 | 0.070286 | 0.13169 | 0.0046848 | -0.00022432 | 0.23216 | -0.0030506 | -0.0010318 | -0.0007498 | 0.0032642 | -0.0045289 | 63.8168 | 63.913 | -0.082397 | -59.2529 | 63.8123 | -59.1019 | -59.1431 | -58.9737 | 0 | -59.285 | 63.8306 | 63.7253 | -59.1431 | -59.2667 | -0.018311 | -0.059509 | 0.018311 | 122.9965 | -0.16937 | -0.10986 | 0.022888 | -0.059509 | -0.18311 | 0.036621 | 0.10986 | -0.20142 | -0.01831 | -0.068664 | 122.8958 | 122.9004 | 59.0012 | -122.937 | 122.9141 | 122.8088 | 59.0836 | -123.0606
763.5156 | 123.1659 | -59.0332 | 63.8031 | 0.17242 | 0.0075451 | 0.067586 | 0.066441 | 0.12592 | 0.00019875 | 0.00041648 | 0.26268 | -0.002196 | -0.0029544 | -0.0024588 | 5.9768e-05 | -0.0021789 | 63.8535 | 63.9725 | -0.013733 | -59.23 | 63.7711 | -59.0881 | -59.1202 | -58.9554 | 0.045776 | -59.2712 | 63.8214 | 63.7207 | -59.1476 | -59.2575 | -0.054932 | -0.086975 | -0.032044 | 123.0057 | -0.19684 | -0.10986 | 0.050354 | -0.11444 | -0.2243 | 0.01831 | 0.07782 | -0.23804 | -0.013733 | -0.082398 | 122.8043 | 122.8867 | 59.0195 | -122.9233 | 122.8546 | 122.7539 | 59.079 | -123.0606
764.5156 | 123.175 | -59.0332 | 63.7985 | 0.31738 | 0.0092541 | 0.068227 | 0.067509 | 0.13084 | 0.0014804 | -0.00043792 | 0.26268 | -0.0043324 | -0.001459 | -0.0013906 | 0.0026234 | -0.0045289 | 63.8763 | 63.9587 | -0.013733 | -59.2209 | 63.7711 | -59.0652 | -59.1248 | -58.9645 | 0.064087 | -59.2712 | 63.8031 | 63.7207 | -59.1431 | -59.2529 | -0.032044 | -0.091553 | -0.027466 | 122.9919 | -0.18768 | -0.09613 | 0.07782 | -0.10986 | -0.21973 | 0.004578 | 0.068664 | -0.23804 | -0.01831 | -0.07782 | 122.8043 | 122.9095 | 59.0195 | -122.9233 | 122.8363 | 122.7539 | 59.0973 | -123.0515
765.5156 | 123.0835 | -59.0698 | 63.8855 | -0.14801 | 0.0077587 | 0.06844 | 0.067936 | 0.12827 | 0.0031894 | -1.0724e-05 | -0.12642 | -0.002196 | -0.0042362 | -0.000109 | 0.0024096 | -0.0043153 | 63.8031 | 63.8901 | -0.032043 | -59.2575 | 63.8672 | -59.079 | -59.1293 | -59.0286 | 0.064087 | -59.3353 | 63.913 | 63.826 | -59.1522 | -59.2484 | -0.009155 | -0.059509 | -0.018311 | 122.9599 | -0.18768 | -0.12817 | -0.082397 | -0.082398 | -0.17853 | 0.027466 | 0.041199 | -0.2655 | -0.086975 | -0.059509 | 122.937 | 122.8729 | 59.0378 | -123.0148 | 122.9828 | 122.8958 | 59.1339 | -123.1338
766.5156 | 123.1384 | -59.0561 | 63.8214 | 0.13428 | 0.0043409 | 0.069509 | 0.065587 | 0.12913 | -0.0025784 | -0.0025741 | 0.23979 | -0.0049732 | -0.0035952 | -0.0013906 | 0.0017688 | -0.0023927 | 63.7985 | 63.9404 | -0.036621 | -59.2529 | 63.7985 | -59.0561 | -59.1339 | -59.0012 | 0.032043 | -59.2987 | 63.8351 | 63.7299 | -59.1293 | -59.2392 | 0 | -0.07782 | -0.022888 | 122.9965 | -0.19684 | -0.11902 | -0.022888 | -0.073242 | -0.18311 | 0.013733 | 0.054931 | -0.24262 | -0.059509 | -0.091553 | 122.8546 | 122.8546 | 59.0195 | -122.9553 | 122.8912 | 122.7859 | 59.0881 | -123.0606
767.5156 | 123.1522 | -59.0469 | 63.7985 | 0.17242 | 0.0056225 | 0.06545 | 0.067296 | 0.12913 | 0.0019078 | -0.0010787 | 0.22453 | -0.0026234 | -0.0029544 | -0.0026724 | 0.0017688 | -0.0060243 | 63.8443 | 63.9771 | -0.009155 | -59.2392 | 63.7527 | -59.0698 | -59.1293 | -58.9691 | 0.050354 | -59.2667 | 63.7939 | 63.6978 | -59.1339 | -59.2392 | -0.022888 | -0.082397 | -0.045776 | 123.024 | -0.19226 | -0.10986 | 0.045776 | -0.086975 | -0.19226 | -0.004578 | 0.07782 | -0.21973 | -0.027466 | -0.10071 | 122.7997 | 122.8912 | 59.0378 | -122.9279 | 122.8409 | 122.7448 | 59.0973 | -123.0377
768.5156 | 123.143 | -59.0515 | 63.8397 | 0.073242 | 0.0060497 | 0.066518 | 0.069432 | 0.13062 | -0.0019376 | -0.0051377 | 0.18639 | -0.0058276 | -0.006586 | -0.0007498 | 0.0015552 | -0.0047425 | 63.8168 | 63.9084 | -0.045776 | -59.2621 | 63.826 | -59.0836 | -59.1248 | -58.9691 | -0.009155 | -59.2941 | 63.8443 | 63.7711 | -59.1248 | -59.2392 | -0.032043 | -0.073242 | -0.013733 | 122.9599 | -0.21057 | -0.13733 | -0.022889 | -0.073242 | -0.18768 | 0.004577 | 0.082398 | -0.24261 | -0.054931 | -0.068665 | 122.8775 | 122.8683 | 59.0057 | -122.9645 | 122.8958 | 122.8226 | 59.0424 | -123.0789
769.5156 | 123.1064 | -59.0652 | 63.7985 | 0.16479 | 0.0083997 | 0.066304 | 0.071568 | 0.12849 | -0.001083 | -0.0025741 | 0.31609 | -0.002837 | -0.0033816 | -0.0022452 | 0.0019824 | -0.0055969 | 63.858 | 63.9679 | -0.027466 | -59.2392 | 63.7756 | -59.0881 | -59.1064 | -58.9691 | 0.027466 | -59.2758 | 63.8123 | 63.7207 | -59.1248 | -59.2575 | -0.022888 | -0.041198 | -0.022888 | 123.0331 | -0.17395 | -0.13275 | 0.059509 | -0.059509 | -0.19226 | 0.013733 | 0.096131 | -0.21057 | -0.018311 | -0.07782 | 122.8409 | 122.9233 | 59.0378 | -122.905 | 122.8775 | 122.7859 | 59.0927 | -123.056
770.5156 | 123.1613 | -59.0378 | 63.8214 | 0.14954 | 0.0069043 | 0.069295 | 0.065159 | 0.1287 | -0.0015102 | -0.0025741 | 0.24742 | -0.0030506 | -0.0021 | -0.001177 | 0.0019824 | -0.0045289 | 63.8168 | 63.9404 | -0.041199 | -59.2529 | 63.7848 | -59.0836 | -59.1156 | -59.0012 | 0.032043 | -59.3033 | 63.826 | 63.7344 | -59.1431 | -59.2438 | -0.045776 | -0.07782 | -0.036621 | 122.9782 | -0.21515 | -0.13733 | -0.004578 | -0.10528 | -0.20599 | 0.004578 | 0.036621 | -0.2655 | -0.05951 | -0.086975 | 122.8226 | 122.8546 | 58.9966 | -122.937 | 122.8638 | 122.7722 | 59.0698 | -123.0652
771.5156 | 123.1796 | -59.0378 | 63.8123 | 0.15717 | 0.010536 | 0.064809 | 0.066441 | 0.12998 | 0.002335 | -0.0012923 | 0.22453 | -0.0036914 | -0.0021 | -0.0030996 | 0.0049732 | -0.0064515 | 63.8672 | 63.9587 | -0.045776 | -59.2346 | 63.7848 | -59.0927 | -59.1156 | -59.0057 | -0.2243 | -59.166 | 63.8031 | 63.7299 | -59.1385 | -59.2117 | -0.054931 | -0.07782 | -0.027466 | 122.9965 | -0.19684 | -0.11902 | 0.054931 | -0.10071 | -0.17395 | -0.009155 | 0.032044 | -0.12817 | 0.045776 | -0.082398 | 122.8226 | 122.905 | 58.992 | -122.9279 | 122.8409 | 122.7676 | 58.8135 | -123.024
772.5156 | 123.111 | -59.079 | 63.8214 | 0.17242 | 0.014808 | 0.066945 | 0.06815 | 0.12934 | 0.0031894 | -0.0010787 | 0.20164 | -0.001128 | -0.0006046 | 0.0001046 | 0.002837 | -0.0060243 | 63.7939 | 63.8489 | -0.13733 | -59.3033 | 63.8443 | -59.1019 | -59.1614 | -59.0195 | -0.059509 | -59.3582 | 63.858 | 63.7573 | -59.1522 | -59.2621 | -0.022889 | -0.082398 | 0.022888 | 122.9279 | -0.22431 | -0.14191 | -0.027466 | -0.073243 | -0.18311 | 0.036621 | 0.059509 | -0.27924 | -0.09613 | -0.064087 | 122.9233 | 122.8729 | 58.9416 | -122.9828 | 122.937 | 122.8363 | 59.0195 | -123.0835
773.5312 | 123.1201 | -59.0836 | 63.8489 | -0.048828 | 0.013954 | 0.068868 | 0.069645 | 0.13319 | 0.0053256 | -0.00043792 | -0.52315 | -0.0024096 | 0.0008908 | -0.0013906 | 0.0034778 | -0.0038879 | 63.8535 | 63.9221 | -0.013733 | -59.23 | 63.858 | -59.1019 | -59.1431 | -58.992 | 0.086975 | -59.3033 | 63.858 | 63.8123 | -59.1248 | -59.2529 | -0.018311 | -0.059509 | 0.009155 | 123.0057 | -0.14648 | -0.086976 | 0.004578 | -0.041199 | -0.16937 | 0.009155 | 0.091553 | -0.21973 | -0.050354 | -0.036621 | 122.9416 | 122.937 | 59.0698 | -122.9919 | 122.9416 | 122.8958 | 59.1705 | -123.1018
774.5156 | 123.1384 | -59.0973 | 63.8306 | 0.20294 | 0.012459 | 0.066304 | 0.069005 | 0.12934 | 0.001694 | 0.00084388 | 0.26268 | -0.0036914 | -0.0021 | 0.0009592 | 0.0026234 | -0.0026063 | 63.7802 | 63.8672 | -0.11444 | -59.2896 | 63.8077 | -59.1019 | -59.1476 | -59.0195 | -0.009155 | -59.3308 | 63.8397 | 63.7527 | -59.1522 | -59.2804 | -0.004578 | -0.050354 | -0.022888 | 122.9645 | -0.19226 | -0.14191 | -0.050354 | -0.054932 | -0.18311 | 0.009156 | 0.07782 | -0.23346 | -0.050354 | -0.077819 | 122.905 | 122.8775 | 58.9828 | -122.9782 | 122.937 | 122.85 | 59.0881 | -123.111
775.5156 | 123.1293 | -59.0469 | 63.8168 | 0.18768 | 0.0058361 | -0.034099 | 0.0658 | 0.12699 | -0.0055692 | -0.0021469 | 0.1635 | -0.004546 | -0.0053042 | -0.0016044 | 0.00048697 | -0.0034607 | 63.7665 | 63.9221 | -0.032043 | -59.2255 | 63.8168 | -59.0652 | -59.1293 | -59.0103 | 0.064087 | -59.2804 | 63.8306 | 63.7527 | -59.1202 | -59.2621 | -0.018311 | -0.082397 | 0 | 122.9691 | -0.17853 | -0.096131 | -0.050354 | -0.073242 | -0.21515 | 0.013733 | 0.036621 | -0.23346 | -0.018311 | -0.064086 | 122.8638 | 122.8134 | 59.0149 | -122.9462 | 122.8775 | 122.7997 | 59.111 | -123.0789
776.5156 | 123.0515 | -59.0652 | 63.8535 | 0.073242 | 0.014595 | 0.06844 | 0.069005 | 0.13191 | 0.003403 | -0.0012923 | 0.13298 | -0.00091437 | -0.0027408 | 0.0052316 | 0.0060412 | -0.0073059 | 63.7619 | 63.7985 | -0.11902 | -59.3033 | 63.8214 | -59.1202 | -59.1385 | -59.0332 | 0.29297 | -59.3811 | 63.8901 | 63.7711 | -59.1522 | -59.2758 | -0.054931 | -0.073242 | -0.032044 | 122.8638 | -0.23804 | -0.16479 | -0.091553 | -0.086975 | -0.21057 | 0.036621 | 0.032044 | -0.31586 | -0.10529 | -0.082398 | 122.8867 | 122.8271 | 58.9462 | -122.9919 | 122.9553 | 122.8363 | 59.3582 | -123.1293
777.5156 | 123.1522 | -59.0515 | 63.8123 | 0.23346 | 0.010963 | 0.067372 | 0.067936 | 0.12785 | -1.505e-05 | -1.0724e-05 | 0.2932 | -0.003905 | -0.0044498 | -0.0039542 | 0.0030506 | -0.0049561 | 63.826 | 63.9175 | -0.041199 | -59.2255 | 63.7665 | -59.1019 | -59.111 | -58.9645 | 0.064087 | -59.4269 | 63.7848 | 63.7115 | -59.1614 | -59.2438 | -0.050354 | -0.059509 | -0.045777 | 122.9691 | -0.17395 | -0.11444 | 0.013733 | -0.10986 | -0.19226 | -0.027466 | 0.086975 | -0.37537 | -0.18311 | -0.10071 | 122.818 | 122.8775 | 59.0103 | -122.9233 | 122.8363 | 122.7631 | 59.1156 | -123.056
778.5156 | 123.2849 | -59.0424 | 63.8626 | 0.17242 | 0.0086133 | 0.069509 | 0.067723 | 0.12763 | -0.0053554 | -0.0032151 | 0.27794 | -0.004546 | -0.0033816 | -0.001818 | 0.0015552 | -0.0030335 | 63.7802 | 63.9267 | -0.054932 | -59.2484 | 63.7756 | -59.079 | -59.1248 | -59.0103 | 0.036621 | -59.285 | 63.8306 | 63.7619 | -59.1156 | -59.23 | -0.036621 | -0.082398 | -0.086975 | 122.9691 | -0.20599 | -0.1236 | -0.082398 | -0.073243 | -0.18768 | -0.032044 | 0.032043 | -0.24262 | -0.054931 | -0.10071 | 122.818 | 122.8226 | 58.9874 | -122.9874 | 122.8729 | 122.8043 | 59.079 | -123.0927
779.5156 | 123.1338 | -59.0744 | 63.8168 | 0.18768 | 0.012031 | 0.067586 | 0.067723 | 0.12635 | 0.0010532 | -0.0019333 | 0.27031 | -0.0041186 | -0.0008182 | -0.0022452 | 0.0043324 | -0.0053833 | 63.8123 | 63.8626 | -0.10071 | -59.2758 | 63.826 | -59.0836 | -59.1614 | -59.0332 | -0.027466 | -59.3353 | 63.8351 | 63.7436 | -59.1614 | -59.2575 | -0.009155 | -0.086975 | 0.009156 | 122.937 | -0.20142 | -0.11444 | -0.004577 | -0.086975 | -0.1831 | 0.018311 | 0.041199 | -0.26093 | -0.07782 | -0.073242 | 122.9004 | 122.8867 | 58.9737 | -122.9782 | 122.9095 | 122.818 | 59.0469 | -123.0743
780.5156 | 123.1247 | -59.0652 | 63.8535 | 0.088501 | 0.0056225 | 0.069081 | 0.066227 | 0.12721 | -0.0012966 | -0.0025741 | 0.28557 | -0.002837 | -0.0035952 | -0.0024588 | -0.00058103 | -0.0015381 | 63.7939 | 63.913 | -0.036621 | -59.2621 | 63.8077 | -59.0927 | -59.1293 | -58.9554 | -0.13275 | -59.2712 | 63.8351 | 63.7619 | -59.1339 | -59.2712 | -0.027465 | -0.064086 | -0.045777 | 122.9782 | -0.19684 | -0.13275 | -0.05951 | -0.068664 | -0.20599 | -0.018311 | 0.10986 | -0.20599 | 0 | -0.091553 | 122.8729 | 122.8592 | 59.0286 | -122.9828 | 122.9004 | 122.8271 | 58.9325 | -123.1247
781.5156 | 123.0743 | -59.0698 | 63.8397 | 0.11902 | 0.01075 | 0.068013 | 0.070927 | 0.12998 | 0.0038304 | -0.0017197 | 0.20164 | -0.0019824 | 0.0004636 | -0.0022452 | 0.003905 | -0.0058105 | 63.7802 | 63.8077 | -0.11902 | -59.3033 | 63.8626 | -59.1019 | -59.1522 | -59.0561 | -0.068665 | -59.3674 | 63.8763 | 63.7802 | -59.1614 | -59.2621 | -0.032044 | -0.082398 | 0.022888 | 122.8775 | -0.23346 | -0.15106 | -0.05951 | -0.091553 | -0.19226 | 0.036621 | 0.013733 | -0.29755 | -0.10529 | -0.05951 | 122.9324 | 122.85 | 58.9508 | -122.9919 | 122.9462 | 122.85 | 59.0012 | -123.1018
782.5156 | 123.0881 | -59.0973 | 63.8397 | -0.048828 | 0.012031 | 0.066518 | 0.068577 | 0.13041 | 0.0029758 | -0.00022432 | 0.15587 | -0.0015552 | -0.000391 | -0.0016044 | 0.0013416 | -0.0045289 | 63.7756 | 63.8077 | -0.1236 | -59.2987 | 63.8397 | -59.111 | -59.1705 | -59.0652 | -0.086975 | -59.3811 | 63.8626 | 63.7848 | -59.1705 | -59.2896 | -0.013733 | -0.073242 | 0 | 122.905 | -0.20142 | -0.12817 | -0.064087 | -0.073242 | -0.19226 | 0.022888 | 0.032043 | -0.28381 | -0.091553 | -0.054932 | 122.937 | 122.8729 | 58.9737 | -123.0103 | 122.9599 | 122.8821 | 59.0103 | -123.1293
783.5156 | 123.2391 | -59.0424 | 63.8306 | 0.18005 | 0.0075451 | 0.067372 | 0.064091 | 0.12806 | -0.0053554 | -0.0015061 | 0.25505 | -0.0058276 | -0.0057316 | -0.0005362 | 0.00091437 | -0.0045289 | 63.7802 | 63.9084 | -0.050354 | -59.2575 | 63.7802 | -59.1064 | -59.1202 | -59.0103 | 0.036621 | -59.2804 | 63.8489 | 63.7802 | -59.1202 | -59.2163 | -0.064087 | -0.07782 | -0.050354 | 122.9507 | -0.21515 | -0.13733 | -0.050354 | -0.07782 | -0.17395 | 0.018311 | 0.032043 | -0.23804 | -0.064087 | -0.050354 | 122.8226 | 122.8226 | 58.992 | -122.9507 | 122.8912 | 122.8226 | 59.079 | -123.0469
784.5156 | 123.0972 | -59.0698 | 63.8672 | -0.36926 | 0.013099 | 0.067159 | 0.068791 | 0.13084 | 0.0046848 | -0.0015061 | 0.026169 | -0.0036914 | 0.001959 | -0.0007498 | 0.0026234 | -0.0049561 | 63.858 | 63.9359 | 0.004578 | -59.23 | 63.8672 | -59.0744 | -59.1339 | -59.0057 | 0.054932 | -59.317 | 63.8763 | 63.7985 | -59.1339 | -59.2621 | -0.004578 | -0.064087 | 0 | 123.0057 | -0.16022 | -0.096131 | -0.009155 | -0.064087 | -0.19226 | 0.009156 | 0.064087 | -0.24719 | -0.054932 | -0.068664 | 122.937 | 122.9279 | 59.0744 | -123.0011 | 122.9462 | 122.8683 | 59.1248 | -123.1293
785.5156 | 123.111 | -59.0973 | 63.826 | 0.16479 | 0.010322 | 0.067586 | 0.069645 | 0.12956 | 0.001694 | 0.00020288 | 0.23216 | -0.0043324 | 0.0004636 | 0.000532 | 0.0032642 | -0.0053833 | 63.7711 | 63.8306 | -0.1236 | -59.2987 | 63.8168 | -59.1156 | -59.1614 | -59.0469 | -0.050354 | -59.3628 | 63.8535 | 63.7436 | -59.1705 | -59.2621 | -0.018311 | -0.064087 | -0.009156 | 122.9279 | -0.20142 | -0.13733 | -0.054932 | -0.073242 | -0.16479 | 0.027466 | 0.050354 | -0.2655 | -0.10071 | -0.082398 | 122.9141 | 122.8683 | 58.9737 | -122.9874 | 122.9507 | 122.8409 | 59.0469 | -123.0881
786.5156 | 123.0377 | -59.0836 | 63.8763 | 0.065613 | 0.013527 | 0.066304 | 0.070714 | 0.12934 | 0.0029758 | -0.0017197 | 0.064316 | 0.00015383 | -0.0012454 | 0.0007456 | 0.0041186 | -0.0034607 | 63.7939 | 63.8672 | -0.073242 | -59.2804 | 63.8351 | -59.0927 | -59.1431 | -59.0744 | -0.018311 | -59.3628 | 63.8992 | 63.7848 | -59.1522 | -59.285 | -0.009155 | -0.059509 | -0.041199 | 122.9507 | -0.19684 | -0.13733 | -0.082398 | -0.068665 | -0.20142 | 0.022888 | 0.009155 | -0.27924 | -0.07782 | -0.091553 | 122.9187 | 122.8775 | 59.0103 | -123.0194 | 122.9828 | 122.8683 | 59.0652 | -123.1613
787.5156 | 123.0331 | -59.0836 | 63.8901 | 0.080872 | 0.012031 | 0.068227 | 0.067509 | 0.12998 | 0.002335 | -1.0724e-05 | 0.087204 | -0.001128 | 3.6404e-05 | -0.0016044 | 0.0015552 | -0.0062379 | 63.7573 | 63.8123 | -0.10071 | -59.2941 | 63.826 | -59.1019 | -59.1339 | -59.1064 | -0.064087 | -59.3948 | 63.8855 | 63.8123 | -59.1751 | -59.285 | -0.018311 | -0.050354 | -0.064087 | 122.8958 | -0.21057 | -0.16022 | -0.13275 | -0.091553 | -0.20142 | -0.004578 | -0.022888 | -0.31128 | -0.10986 | -0.07782 | 122.9095 | 122.8409 | 58.9828 | -123.024 | 122.9691 | 122.8958 | 59.0195 | -123.175
788.5156 | 123.111 | -59.0607 | 63.8763 | -0.079346 | 0.014381 | 0.066945 | 0.06815 | 0.12934 | 0.0014804 | -0.00065152 | -0.019608 | -0.0019824 | -0.0006046 | -0.002886 | 0.0019824 | -0.0041017 | 63.8306 | 63.913 | 0.009155 | -59.23 | 63.8351 | -59.079 | -59.1522 | -59.1843 | 0.26093 | -59.2987 | 63.8672 | 63.8123 | -59.1339 | -59.2621 | -0.01831 | -0.091553 | -0.041199 | 122.9736 | -0.16937 | -0.07782 | -0.045777 | -0.073242 | -0.20142 | -0.009156 | -0.1236 | -0.23804 | -0.036621 | -0.064087 | 122.8958 | 122.8912 | 59.0698 | -123.0286 | 122.9279 | 122.8729 | 59.3216 | -123.1384
789.5156 | 123.0927 | -59.0744 | 63.858 | 0.0045777 | 0.013954 | 0.068868 | 0.070286 | 0.12763 | 0.00062595 | -0.0027877 | 0.087204 | -0.001128 | 3.6404e-05 | -0.003527 | 0.0019824 | -0.0034607 | 63.8031 | 63.8763 | -0.054932 | -59.2667 | 63.8123 | -59.079 | -59.1339 | -59.0515 | 0.004578 | -59.3674 | 63.8535 | 63.7939 | -59.1293 | -59.2804 | -0.004577 | -0.059509 | -0.045776 | 122.9507 | -0.19226 | -0.13275 | -0.054931 | -0.054931 | -0.20599 | -0.004577 | 0.022888 | -0.29297 | -0.086975 | -0.064087 | 122.8867 | 122.8775 | 59.0195 | -122.9919 | 122.9279 | 122.8683 | 59.079 | -123.1384
790.5156 | 123.1338 | -59.0561 | 63.826 | 0.13428 | 0.0069043 | 0.068868 | 0.064732 | 0.12827 | -0.0040738 | -0.0015061 | 0.37712 | -0.0041186 | -0.0027408 | 0.0007456 | 0.0019824 | -0.0013245 | 63.7939 | 63.9633 | -0.018311 | -59.23 | 63.7619 | -59.0698 | -59.1064 | -58.9966 | 0.045776 | -59.2804 | 63.8123 | 63.7299 | -59.1431 | -59.2575 | -0.013733 | -0.050354 | -0.064087 | 123.0194 | -0.17395 | -0.1236 | -0.032044 | -0.086975 | -0.20142 | -0.013733 | 0.059509 | -0.22431 | -0.022889 | -0.096131 | 122.818 | 122.85 | 59.0378 | -122.9324 | 122.8683 | 122.7859 | 59.1019 | -123.0835
791.5156 | 123.0743 | -59.0698 | 63.8489 | 0.20294 | 0.011818 | 0.066518 | 0.072636 | 0.13084 | 0.004044 | -0.0025741 | 0.026169 | -0.001128 | -0.0008182 | -0.0007498 | 0.0041186 | -0.0051697 | 63.8397 | 63.9175 | -0.004578 | -59.2484 | 63.8443 | -59.0836 | -59.1522 | -59.0332 | 0.041199 | -59.317 | 63.8626 | 63.7756 | -59.1248 | -59.2529 | -0.013733 | -0.082398 | -0.004578 | 122.9874 | -0.17853 | -0.09613 | -0.009155 | -0.054932 | -0.18311 | 0.013733 | 0.036621 | -0.24719 | -0.064087 | -0.073242 | 122.9141 | 122.9095 | 59.0652 | -123.0011 | 122.9324 | 122.8455 | 59.111 | -123.1018
792.5156 | 123.1384 | -59.0424 | 63.8672 | -0.1709 | 0.0096813 | 0.069722 | 0.070073 | 0.12763 | -1.505e-05 | -0.0027877 | -0.065384 | -0.001128 | 0.0006772 | -0.0026724 | 0.00091437 | -0.0030335 | 63.8077 | 63.913 | 0.004578 | -59.2209 | 63.8626 | -59.0744 | -59.1248 | -59.0286 | 0.091553 | -59.2941 | 63.9084 | 63.8214 | -59.1293 | -59.2484 | -0.032044 | -0.082398 | -0.004577 | 122.9553 | -0.17853 | -0.09613 | -0.059509 | -0.086975 | -0.20599 | 0.041199 | 0.013733 | -0.25177 | -0.045776 | -0.045776 | 122.905 | 122.85 | 59.0469 | -122.9919 | 122.9507 | 122.8638 | 59.1339 | -123.1155
793.5156 | 123.0606 | -59.0973 | 63.8672 | 0.065613 | 0.012886 | 0.065663 | 0.069432 | 0.12977 | 0.0012668 | -0.0010787 | 0.11772 | -0.00091437 | 0.00025 | -0.0009634 | 0.0034778 | -0.0047425 | 63.7527 | 63.8947 | -0.091553 | -59.2667 | 63.8489 | -59.1064 | -59.1476 | -59.0881 | -0.027466 | -59.3674 | 63.8855 | 63.7848 | -59.1476 | -59.2941 | -0.009155 | -0.050354 | -0.01831 | 122.9919 | -0.16937 | -0.11902 | -0.11444 | -0.050354 | -0.19684 | 0.018311 | 0.009155 | -0.27008 | -0.073243 | -0.082397 | 122.9462 | 122.85 | 59.0057 | -123.0148 | 122.9828 | 122.8821 | 59.0698 | -123.1613
794.5156 | 123.0881 | -59.0652 | 63.8901 | -0.15564 | 0.0090405 | 0.069081 | 0.0705 | 0.12956 | -0.00044225 | -0.0034287 | -0.095902 | -0.0030506 | -0.0001774 | -0.0003226 | 0.00048697 | -0.0047425 | 63.7573 | 63.8763 | -0.041199 | -59.2346 | 63.8351 | -59.0836 | -59.1431 | -59.0698 | 0.07782 | -59.3308 | 63.8992 | 63.8306 | -59.1476 | -59.2255 | -0.01831 | -0.077819 | -0.054932 | 122.9416 | -0.16937 | -0.091553 | -0.13275 | -0.082397 | -0.16022 | 0.009155 | -0.004577 | -0.2655 | -0.10529 | -0.05951 | 122.9004 | 122.8226 | 59.024 | -123.0331 | 122.9645 | 122.8958 | 59.1431 | -123.1155
795.5156 | 123.1064 | -59.0836 | 63.8397 | 0.15717 | 0.012672 | 0.066091 | 0.069432 | 0.12827 | 0.002335 | -0.0012923 | 0.25505 | -0.003905 | -0.0008182 | -0.0005362 | 0.0026234 | -0.0043153 | 63.7482 | 63.8443 | -0.1236 | -59.2896 | 63.8168 | -59.1248 | -59.1522 | -59.0332 | -0.041199 | -59.3445 | 63.8535 | 63.7756 | -59.166 | -59.2896 | -0.041199 | -0.068665 | -0.022889 | 122.9279 | -0.20599 | -0.13733 | -0.091553 | -0.082398 | -0.20599 | 0.013733 | 0.050354 | -0.26093 | -0.054931 | -0.064087 | 122.9004 | 122.8317 | 58.96 | -122.9919 | 122.937 | 122.8592 | 59.0424 | -123.1293
796.5156 | 123.1064 | -59.0881 | 63.8901 | -0.13275 | 0.01075 | 0.066304 | 0.069645 | 0.13191 | -0.0021512 | -0.0021469 | -0.088272 | -0.004546 | -0.0006046 | -0.0009634 | 0.0015552 | -0.0041017 | 63.7711 | 63.8855 | -0.032043 | -59.2392 | 63.8718 | -59.1064 | -59.1248 | -59.0561 | 0.068665 | -59.3033 | 63.8947 | 63.8306 | -59.1431 | -59.2575 | -0.01831 | -0.036621 | -0.018311 | 122.9736 | -0.15106 | -0.11444 | -0.11902 | -0.054931 | -0.16937 | 0.004577 | 0.032044 | -0.21515 | -0.045777 | -0.05951 | 122.9599 | 122.8592 | 59.0561 | -123.0148 | 122.9828 | 122.9187 | 59.1568 | -123.1476
797.5156 | 123.1338 | -59.0836 | 63.858 | -0.086975 | 0.013313 | 0.068654 | 0.069645 | 0.12892 | 0.0038304 | 0.00041648 | -0.43922 | -0.002837 | -0.001459 | -0.001818 | 0.001128 | -0.0041017 | 63.8077 | 64.0961 | -0.07782 | -59.3765 | 63.7985 | -59.1064 | -59.1431 | -58.9966 | 0.068665 | -59.3079 | 63.8855 | 63.7894 | -59.1339 | -59.2575 | -0.022888 | -0.059509 | -0.059509 | 123.1796 | -0.29297 | -0.23346 | -0.050354 | -0.050354 | -0.17395 | 0.027466 | 0.086975 | -0.2243 | -0.050354 | -0.068664 | 122.8821 | 122.8912 | 59.0057 | -123.0011 | 122.9691 | 122.8729 | 59.1522 | -123.1155
798.5156 | 123.0881 | -59.0652 | 63.8489 | -0.018311 | 0.012672 | 0.066304 | 0.070927 | 0.12827 | 0.001694 | -1.0724e-05 | 0.049057 | -0.0026234 | 0.0025998 | -0.0003226 | 0.00048697 | -0.0041017 | 63.7985 | 63.9221 | -0.022888 | -59.2484 | 63.826 | -59.111 | -59.1385 | -59.0332 | 0.068665 | -59.3399 | 63.858 | 63.8077 | -59.1202 | -59.2667 | -0.045776 | -0.073242 | -0.022888 | 122.9874 | -0.1831 | -0.10986 | -0.050354 | -0.054931 | -0.20142 | 0.009155 | 0.032044 | -0.27466 | -0.073242 | -0.041199 | 122.8912 | 122.8638 | 59.0424 | -122.9874 | 122.9233 | 122.8729 | 59.1339 | -123.1155
799.5156 | 123.0835 | -59.024 | 63.8672 | -0.17853 | 0.010963 | 0.067159 | 0.069218 | 0.12849 | -0.0015102 | -0.0010787 | -0.057755 | -0.0026234 | 0.0008908 | -0.0013906 | 0.0015552 | -0.0021789 | 63.7711 | 63.8855 | -0.041199 | -59.2438 | 63.8763 | -59.1019 | -59.1293 | -59.0515 | 0.073242 | -59.3216 | 63.9038 | 63.8351 | -59.1705 | -59.2438 | -0.07782 | -0.10529 | 0.009156 | 122.9095 | -0.21973 | -0.11444 | -0.09613 | -0.14648 | -0.21973 | 0.036622 | -0.027466 | -0.29755 | -0.07782 | -0.032043 | 122.9004 | 122.7951 | 58.9828 | -122.9965 | 122.9279 | 122.8592 | 59.0973 | -123.111
800.5156 | 123.0652 | -59.0927 | 63.826 | 0.18005 | 0.010963 | 0.069936 | 0.070714 | 0.12956 | 0.00041235 | -0.00065152 | 0.2932 | -0.0019824 | -0.001459 | 0.0003182 | 0.0024096 | -0.0034607 | 63.739 | 63.858 | -0.1236 | -59.3033 | 63.826 | -59.1248 | -59.1568 | -59.0698 | -0.064087 | -59.3719 | 63.8535 | 63.7756 | -59.166 | -59.285 | -0.032044 | -0.064087 | 0 | 122.9507 | -0.21057 | -0.14648 | -0.086975 | -0.073243 | -0.19226 | 0.027466 | 0.022888 | -0.27924 | -0.086975 | -0.050354 | 122.9187 | 122.8317 | 58.9691 | -122.9828 | 122.9462 | 122.8683 | 59.0286 | -123.111
801.5156 | 123.0881 | -59.0607 | 63.8947 | -0.2243 | 0.010322 | 0.069081 | 0.067509 | 0.12913 | -0.0021512 | -0.0070603 | -0.24086 | -0.00070077 | 0.0004636 | -0.0009634 | 5.9768e-05 | -0.0034607 | 63.9999 | 63.8351 | -0.068665 | -59.3628 | 63.8489 | -59.1156 | -59.1293 | -59.0469 | 0.050354 | -59.3353 | 63.8947 | 63.8351 | -59.1522 | -59.2621 | -0.054932 | -0.068664 | -0.045776 | 122.8958 | -0.30212 | -0.23346 | 0.10529 | -0.091553 | -0.20142 | 0 | 0.013733 | -0.27466 | -0.073242 | -0.059509 | 122.9095 | 123.0606 | 58.992 | -123.024 | 122.9553 | 122.8958 | 59.111 | -123.1567
802.5156 | 123.1201 | -59.079 | 63.8947 | -0.18616 | 0.011604 | 0.067586 | 0.069645 | 0.1302 | 0.00083955 | -0.0021469 | -0.057755 | -0.002837 | 0.003027 | -0.001818 | 0.003905 | -0.0060243 | 63.7802 | 63.9221 | -0.013733 | -59.2438 | 63.8672 | -59.0836 | -59.1293 | -59.0195 | 0.073242 | -59.2987 | 63.8718 | 63.8168 | -59.1431 | -59.2529 | -0.004578 | -0.050354 | -0.027466 | 123.0011 | -0.1648 | -0.11444 | -0.11444 | -0.064087 | -0.17395 | -0.022888 | 0.059509 | -0.21973 | -0.045776 | -0.07782 | 122.9462 | 122.8592 | 59.0652 | -123.024 | 122.9507 | 122.8958 | 59.1522 | -123.1476
803.5156 | 123.0743 | -59.0652 | 63.913 | -0.90332 | 0.0073315 | 0.066518 | 0.066227 | 0.13041 | -0.001083 | -0.0027877 | -0.027237 | -0.0026234 | 0.0006772 | -0.0003226 | 0.00048697 | -0.0047425 | 63.7253 | 63.8763 | -0.036621 | -59.2529 | 63.8489 | -59.0927 | -59.1431 | -59.0469 | 0.059509 | -59.3353 | 63.9038 | 63.8123 | -59.1385 | -59.2575 | -0.027465 | -0.077819 | -0.064087 | 122.9416 | -0.18768 | -0.10986 | -0.18768 | -0.073242 | -0.19226 | -0.009155 | 0.018311 | -0.27008 | -0.07782 | -0.10071 | 122.9141 | 122.7905 | 59.0286 | -123.056 | 122.9691 | 122.8775 | 59.1248 | -123.1705
804.5156 | 123.0881 | -59.0424 | 63.913 | -0.17853 | 0.0077587 | 0.065236 | 0.068364 | 0.12956 | -0.00065585 | -0.0059921 | -0.065384 | -0.0026234 | -0.0023136 | 0.000532 | 0.00070077 | -0.0028199 | 63.7482 | 63.9084 | -0.013733 | -59.2667 | 63.8397 | -59.0881 | -59.1293 | -59.166 | 0.10529 | -59.3582 | 63.8809 | 63.7894 | -59.1843 | -59.2667 | -0.045777 | -0.086975 | -0.073242 | 122.9507 | -0.22431 | -0.13733 | -0.1648 | -0.14191 | -0.22431 | -0.032044 | -0.1236 | -0.31586 | -0.091552 | -0.1236 | 122.8821 | 122.7905 | 59.0286 | -123.0423 | 122.9233 | 122.8317 | 59.1476 | -123.1796
805.5156 | 123.0835 | -59.0973 | 63.8626 | 0.088501 | 0.01374 | 0.066091 | 0.0705 | 0.12849 | 0.003403 | -0.0023605 | 0.20927 | -0.0013416 | 0.0011044 | -0.0024588 | 0.00048697 | -0.0034607 | 63.6887 | 63.826 | -0.12817 | -59.2987 | 63.8351 | -59.0973 | -59.1751 | -59.0607 | -0.10986 | -59.3399 | 63.8809 | 63.7848 | -59.1476 | -59.2804 | 0 | -0.07782 | -0.027466 | 122.9233 | -0.20142 | -0.1236 | -0.17395 | -0.050354 | -0.18311 | 0.01831 | 0.036621 | -0.24262 | -0.059509 | -0.07782 | 122.9324 | 122.7859 | 58.9691 | -123.0377 | 122.9782 | 122.8821 | 58.9874 | -123.143
806.5156 | 123.0789 | -59.0652 | 63.8855 | -0.18616 | 0.010109 | 0.066304 | 0.0705 | 0.12678 | -0.0025784 | -0.0032151 | -0.073013 | -0.002196 | 0.00025 | 0.000532 | 0.00027337 | -0.0064515 | 63.7665 | 63.8947 | -0.036621 | -59.2575 | 63.8718 | -59.079 | -59.1339 | -59.0561 | 0.064087 | -59.3353 | 63.8763 | 63.826 | -59.1293 | -59.2484 | -0.013732 | -0.068664 | -0.013733 | 122.9599 | -0.19226 | -0.1236 | -0.11902 | -0.064086 | -0.1831 | -0.009155 | 0.009156 | -0.27008 | -0.086975 | -0.059509 | 122.937 | 122.8317 | 59.0286 | -123.0194 | 122.9416 | 122.8912 | 59.1293 | -123.1338
807.5156 | 123.1064 | -59.0561 | 63.8992 | -0.10223 | 0.013099 | 0.068013 | 0.070073 | 0.13126 | 0.00083955 | 0.00041648 | -0.11879 | -0.0019824 | 0.0017454 | 0.0003182 | 0.0017688 | -0.0043153 | 63.7711 | 63.8992 | -0.013733 | -59.2392 | 63.8672 | -59.0698 | -59.1202 | -59.024 | 0.091553 | -59.317 | 63.8809 | 63.8214 | -59.1293 | -59.2575 | -0.013733 | -0.064087 | -0.032044 | 122.9553 | -0.18311 | -0.11902 | -0.12817 | -0.073242 | -0.20142 | -0.018311 | 0.032043 | -0.26093 | -0.05951 | -0.07782 | 122.9233 | 122.8271 | 59.0424 | -123.0194 | 122.937 | 122.8775 | 59.1476 | -123.1567
808.5156 | 123.143 | -59.0515 | 63.8763 | -0.11749 | 0.0060497 | 0.066304 | 0.06815 | 0.12977 | -0.0051418 | -0.0019333 | 0.01091 | -0.005614 | 0.0008908 | 0.0018136 | -0.00036743 | -0.0028199 | 63.8168 | 64.0274 | 0.091553 | -59.198 | 63.7894 | -59.0561 | -59.1019 | -58.9737 | 0.17853 | -59.2255 | 63.8397 | 63.7527 | -59.1064 | -59.2392 | -0.004577 | -0.050354 | -0.086975 | 123.0789 | -0.14648 | -0.09613 | -0.05951 | -0.054931 | -0.18768 | -0.036621 | 0.07782 | -0.17395 | 0.013733 | -0.1236 | 122.8409 | 122.8683 | 59.1431 | -122.9782 | 122.8912 | 122.8043 | 59.23 | -123.1155
809.5156 | 123.1018 | -59.0607 | 63.8992 | -0.17853 | 0.0081861 | 0.067159 | 0.068577 | 0.12785 | -0.0023648 | -0.0055649 | -0.057755 | -0.0047596 | -0.0008182 | -0.0013906 | 0.00027337 | -0.0019653 | 63.8031 | 63.9999 | 0.050354 | -59.1934 | 63.8306 | -59.0744 | -59.111 | -59.0195 | 0.12817 | -59.2712 | 63.8901 | 63.7802 | -59.111 | -59.2255 | -0.013733 | -0.050354 | -0.068665 | 123.0606 | -0.13275 | -0.082397 | -0.09613 | -0.050354 | -0.1648 | -0.009155 | 0.041199 | -0.21057 | -0.045776 | -0.11902 | 122.8912 | 122.8638 | 59.111 | -123.0103 | 122.9507 | 122.8409 | 59.1888 | -123.1247
810.5156 | 123.1201 | -59.0698 | 63.8809 | -0.10986 | 0.014595 | 0.066091 | 0.073704 | 0.1287 | 0.0010532 | -0.0017197 | -0.050125 | -0.0024096 | 0.0011044 | 0.0011728 | 0.0032642 | -0.0060243 | 63.8031 | 63.9359 | 0.004578 | -59.2072 | 63.8718 | -59.079 | -59.1431 | -58.9874 | -0.18768 | -59.4177 | 63.8397 | 63.7619 | -59.1797 | -59.285 | -0.009155 | -0.073242 | -0.009155 | 123.0057 | -0.13733 | -0.064087 | -0.077819 | -0.10986 | -0.21515 | -0.041198 | 0.082397 | -0.3479 | -0.13275 | -0.11902 | 122.9416 | 122.8729 | 59.0744 | -123.024 | 122.9095 | 122.8317 | 58.8821 | -123.1659
811.5156 | 123.1705 | -59.0332 | 63.8672 | -0.10223 | 0.0069043 | 0.067586 | 0.068364 | 0.13233 | -0.0040738 | -0.0040695 | -0.027237 | -0.005614 | -0.0008182 | -0.0005362 | -0.00015383 | -0.0023927 | 63.8306 | 64.0411 | 0.09613 | -59.1934 | 63.8168 | -59.0561 | -59.0836 | -58.9691 | 0.1831 | -59.2163 | 63.8306 | 63.7848 | -59.1248 | -59.2255 | -0.022888 | -0.050354 | -0.050354 | 123.0743 | -0.16022 | -0.10986 | -0.036621 | -0.091553 | -0.19226 | -0.036621 | 0.064087 | -0.18311 | 0.009155 | -0.082397 | 122.85 | 122.8638 | 59.1293 | -122.9507 | 122.8638 | 122.818 | 59.2163 | -123.0927
812.5156 | 123.1705 | -59.0149 | 63.8535 | 0.19531 | 0.0088269 | 0.067159 | 0.067723 | 0.12998 | -0.0025784 | -0.0030013 | -0.019608 | -0.0026234 | -0.0001774 | 0.0003182 | 0.0019824 | -0.0047425 | 63.8351 | 64.0503 | 0.09613 | -59.1888 | 63.7939 | -59.0607 | -59.0881 | -58.9554 | 0.1831 | -59.2117 | 63.8535 | 63.7527 | -59.1064 | -59.2484 | -0.045776 | -0.073242 | -0.05951 | 123.0652 | -0.17395 | -0.10071 | -0.018311 | -0.091552 | -0.23346 | 0 | 0.05951 | -0.19684 | 0.036621 | -0.10071 | 122.8088 | 122.85 | 59.111 | -122.9416 | 122.8683 | 122.7676 | 59.198 | -123.1018
813.5156 | 123.1384 | -59.024 | 63.8535 | -0.14801 | 0.0071179 | 0.06844 | 0.067509 | 0.13191 | -0.001083 | -0.0025741 | -0.034867 | -0.003905 | -0.0023136 | -0.0005362 | 0.00070077 | -0.0034607 | 63.8214 | 64.0274 | 0.086975 | -59.2026 | 63.8077 | -59.0561 | -59.0973 | -58.9737 | 0.16022 | -59.2575 | 63.8626 | 63.7848 | -59.111 | -59.2163 | -0.032043 | -0.073242 | -0.045777 | 123.0515 | -0.17853 | -0.10529 | -0.032044 | -0.086975 | -0.19226 | 0.009155 | 0.050354 | -0.23346 | -0.041198 | -0.068665 | 122.8317 | 122.8455 | 59.111 | -122.9507 | 122.8867 | 122.8088 | 59.1843 | -123.0698
814.5156 | 123.0972 | -59.0515 | 63.8672 | -0.21667 | 0.0066907 | 0.067372 | 0.06815 | 0.12892 | -0.00044225 | -0.0038559 | -0.12642 | -0.004546 | -0.0006046 | 0.0013864 | 0.002196 | -0.0051697 | 63.8123 | 63.9771 | 0.050354 | -59.2026 | 63.8397 | -59.0652 | -59.1064 | -59.024 | 0.091553 | -59.3079 | 63.8947 | 63.7894 | -59.1156 | -59.2484 | -0.013733 | -0.054931 | -0.027465 | 123.0286 | -0.15106 | -0.096131 | -0.054931 | -0.064087 | -0.19684 | 0.027466 | 0.027466 | -0.25635 | -0.059509 | -0.077819 | 122.8912 | 122.8638 | 59.1019 | -122.9736 | 122.9462 | 122.8409 | 59.1431 | -123.1155
815.5156 | 123.1247 | -59.0607 | 63.8809 | -0.18616 | 0.01139 | 0.066518 | 0.070927 | 0.13276 | 0.0027622 | -0.0015061 | -0.065384 | -0.00048697 | 3.6404e-05 | -0.0003226 | 0.0017688 | -0.0070923 | 63.7894 | 63.9313 | -0.018311 | -59.2209 | 63.8855 | -59.0744 | -59.1293 | -59.0103 | 0.09613 | -59.317 | 63.8763 | 63.7894 | -59.1385 | -59.2392 | -0.013733 | -0.068664 | 0.004578 | 122.9919 | -0.16022 | -0.091553 | -0.091552 | -0.07782 | -0.17853 | -0.004577 | 0.050354 | -0.25635 | -0.07782 | -0.091552 | 122.9462 | 122.85 | 59.0424 | -123.0103 | 122.937 | 122.85 | 59.1568 | -123.1201
816.5156 | 123.1796 | -59.0378 | 63.858 | 0.012207 | 0.0043409 | 0.066945 | 0.068364 | 0.12721 | -0.0034328 | -0.0015061 | 0.14061 | -0.0032642 | -0.0029544 | -0.000109 | -0.00058103 | -0.0030335 | 63.7527 | 63.9771 | 0 | -59.2255 | 63.8123 | -59.079 | -59.1293 | -58.9828 | 0.09613 | -59.2529 | 63.8077 | 63.7619 | -59.111 | -59.2346 | -0.041198 | -0.091552 | -0.045776 | 123.0148 | -0.18768 | -0.096131 | -0.10529 | -0.073242 | -0.19684 | -0.050354 | 0.054932 | -0.21515 | -0.018311 | -0.09613 | 122.85 | 122.7905 | 59.0378 | -122.9874 | 122.8455 | 122.7997 | 59.1339 | -123.0927
817.5156 | 123.1796 | -59.0103 | 63.8626 | -0.14038 | 0.0064771 | 0.066945 | 0.069859 | 0.12785 | -0.0038602 | -0.0030013 | 1.552 | -0.002837 | -0.0025272 | -0.0039542 | 0.0024096 | -0.0045289 | 63.8626 | 64.0686 | 0.10986 | -59.166 | 63.7985 | -59.0286 | -59.1064 | -58.9783 | 0.21515 | -59.2209 | 63.8443 | 63.7253 | -59.1202 | -59.2072 | -0.01831 | -0.09613 | -0.064087 | 123.0789 | -0.15564 | -0.05951 | 0 | -0.10986 | -0.19684 | -0.018311 | 0.032044 | -0.21057 | -0.013733 | -0.13733 | 122.8088 | 122.8729 | 59.1202 | -122.9691 | 122.8546 | 122.7356 | 59.2255 | -123.0698
818.5156 | 123.111 | -59.0469 | 63.8535 | -0.048828 | 0.01374 | 0.065663 | 0.070927 | 0.12849 | 0.0046848 | -0.0017197 | 0.2932 | -0.001128 | -0.0001774 | -0.0016044 | 0.0047596 | -0.0075195 | 63.8397 | 63.6429 | -0.15564 | -59.3033 | 63.826 | -59.1293 | -59.1431 | -58.9783 | 0.068665 | -59.3124 | 63.8992 | 63.8031 | -59.1293 | -59.2667 | -0.082397 | -0.09613 | -0.027466 | 122.6898 | -0.25635 | -0.16022 | -0.013733 | -0.082397 | -0.21973 | 0.045776 | 0.068665 | -0.2655 | -0.045776 | -0.050354 | 122.8729 | 122.8867 | 58.8913 | -122.9965 | 122.9462 | 122.85 | 59.1156 | -123.1201
819.5156 | 123.175 | -59.0012 | 63.8351 | -0.033569 | 0.0032727 | 0.068227 | 0.06815 | 0.12956 | -0.00621 | -0.0010787 | 0.10246 | -0.0068958 | -0.004877 | -0.001818 | -0.0010082 | -0.0030335 | 63.826 | 64.032 | 0.059509 | -59.1934 | 63.8123 | -59.0515 | -59.0836 | -58.9279 | 0.15106 | -59.2026 | 63.8214 | 63.7619 | -59.0973 | -59.2163 | -0.050354 | -0.082397 | -0.022888 | 123.0331 | -0.19226 | -0.10986 | -0.009155 | -0.09613 | -0.21515 | -0.013733 | 0.073243 | -0.20142 | 0.013733 | -0.073242 | 122.8134 | 122.8271 | 59.0607 | -122.9187 | 122.8226 | 122.7631 | 59.1522 | -123.0515
820.5156 | 123.0652 | -59.0515 | 63.8763 | -0.1709 | 0.0094677 | 0.068868 | 0.067723 | 0.12785 | 0.0010532 | -0.0047103 | -0.16457 | -0.0030506 | -0.0018862 | -0.0009634 | 0.0013416 | -0.0068787 | 63.9633 | 63.7253 | -0.1236 | -59.3079 | 63.8351 | -59.0927 | -59.1248 | -59.0378 | 0.041199 | -59.3445 | 63.9221 | 63.8123 | -59.1339 | -59.2392 | -0.041198 | -0.073242 | -0.041199 | 122.7768 | -0.25635 | -0.18311 | 0.086975 | -0.082397 | -0.18768 | 0.045776 | 0.013733 | -0.29297 | -0.10529 | -0.064087 | 122.8867 | 123.0148 | 58.9279 | -123.0011 | 122.9736 | 122.8638 | 59.0927 | -123.1155
821.5156 | 123.0972 | -59.0195 | 63.8168 | -0.071716 | 0.0060497 | 0.066091 | 0.065159 | 0.12849 | -0.0047146 | -0.00043792 | 0.026169 | -0.003905 | -0.0063724 | 0.0001046 | 5.9768e-05 | -0.0030335 | 63.8443 | 64.0549 | 0.07782 | -59.2026 | 63.8168 | -59.0561 | -59.0744 | -58.9142 | 0.20599 | -59.1888 | 63.8214 | 63.7299 | -59.0836 | -59.198 | -0.036621 | -0.054932 | 0 | 123.0743 | -0.18311 | -0.12817 | 0.027466 | -0.064087 | -0.17853 | 0.004578 | 0.10528 | -0.16937 | 0.009155 | -0.086975 | 122.8363 | 122.8638 | 59.0973 | -122.8912 | 122.8409 | 122.7493 | 59.2255 | -123.0148
822.5156 | 123.2071 | -59.0332 | 63.8123 | -0.10223 | 0.0049817 | 0.066945 | 0.068364 | 0.13126 | -0.0015102 | -0.0047103 | -0.011978 | -0.0036914 | -0.0016726 | -0.0013906 | 0.0024096 | -0.0038879 | 63.8443 | 64.032 | 0.059509 | -59.2072 | 63.8214 | -59.0424 | -59.0836 | -58.9233 | 0.16479 | -59.1797 | 63.8214 | 63.7436 | -59.1064 | -59.2117 | -0.009155 | -0.050354 | 0.009155 | 123.0652 | -0.17395 | -0.1236 | 0.032043 | -0.073242 | -0.17853 | 0.009155 | 0.10986 | -0.14648 | 0.032044 | -0.068665 | 122.8546 | 122.8775 | 59.0927 | -122.8958 | 122.8546 | 122.7768 | 59.198 | -123.024
823.5156 | 123.1613 | -59.024 | 63.8351 | -0.064087 | 0.0062635 | 0.066731 | 0.068364 | 0.12934 | 0.00062595 | -0.0017197 | 0.0032804 | -0.0030506 | -0.0021 | -0.0007498 | 0.0026234 | -0.0047425 | 63.8901 | 64.0732 | 0.027466 | -58.8776 | 63.8626 | -59.0378 | -59.1019 | -58.9737 | 0.17395 | -59.2026 | 63.826 | 63.7482 | -59.111 | -59.2117 | -0.013733 | -0.07782 | 0.027466 | 123.0972 | 0.14648 | 0.22431 | 0.054932 | -0.086975 | -0.18768 | -0.009155 | 0.050354 | -0.17853 | 0.009155 | -0.086975 | 122.8867 | 122.9141 | 59.0515 | -122.937 | 122.85 | 122.7722 | 59.198 | -123.0469
824.5156 | 123.1384 | -59.0469 | 63.8489 | 0.37842 | 0.0060497 | 0.066731 | 0.067296 | 0.12998 | -0.0019376 | -0.0027877 | 0.11772 | -0.0051868 | -0.0018862 | -0.0007498 | 0.0013416 | -0.0038879 | 63.7665 | 63.9359 | -0.022888 | -59.2392 | 63.8351 | -59.0881 | -59.1156 | -58.9874 | 0.050354 | -59.2896 | 63.8535 | 63.7482 | -59.111 | -59.2255 | -0.041199 | -0.068665 | -0.013733 | 122.9828 | -0.19226 | -0.1236 | -0.082398 | -0.064087 | -0.17853 | 0.004578 | 0.059509 | -0.24262 | -0.064087 | -0.10071 | 122.8821 | 122.8134 | 59.024 | -122.9645 | 122.9004 | 122.7951 | 59.0973 | -123.0743
825.5156 | 123.1201 | -59.0469 | 63.858 | -0.17853 | 0.0064771 | 0.067159 | 0.067509 | 0.12806 | 0.001694 | -0.0034287 | -0.13405 | -0.004546 | -0.0035952 | -0.0016044 | 0.0017688 | -0.0055969 | 63.8535 | 64.0137 | 0.059509 | -59.1888 | 63.8397 | -59.0652 | -59.1248 | -58.9874 | 0.1236 | -59.2758 | 63.8535 | 63.7848 | -59.1064 | -59.2209 | -0.018311 | -0.07782 | -0.01831 | 123.0606 | -0.14191 | -0.064087 | -0.004577 | -0.059509 | -0.17395 | -0.004577 | 0.059509 | -0.22888 | -0.054932 | -0.073242 | 122.8867 | 122.9004 | 59.1064 | -122.9828 | 122.9004 | 122.8317 | 59.1705 | -123.0789
826.5156 | 123.1934 | -59.0103 | 63.8397 | -0.064087 | 0.0049817 | 0.068654 | 0.067082 | 0.12721 | -0.0025784 | -0.0015061 | 0.10246 | -0.0051868 | -0.003168 | -0.0007498 | 0.0017688 | -0.0049561 | 63.8351 | 64.0182 | 0.054932 | -59.1934 | 63.8306 | -59.0561 | -59.111 | -58.9325 | 0.16022 | -59.2117 | 63.8397 | 63.7344 | -59.1064 | -59.2209 | -0.045776 | -0.10071 | -0.009156 | 123.0286 | -0.18311 | -0.082397 | -0.004578 | -0.09613 | -0.21057 | 0 | 0.07782 | -0.20142 | 0.009155 | -0.10529 | 122.8409 | 122.8455 | 59.0652 | -122.9507 | 122.85 | 122.7448 | 59.1705 | -123.0606
827.5156 | 123.175 | -59.0149 | 63.8443 | -0.086975 | 0.0028455 | 0.067586 | 0.069218 | 0.12592 | 0.0010532 | -0.0023605 | -0.47737 | -0.006255 | -0.0023136 | 0.0011728 | 0.0013416 | -0.0053833 | 63.8718 | 64.0961 | 0.09613 | -59.1385 | 63.8397 | -59.0515 | -59.079 | -58.9233 | 0.1236 | -59.1843 | 63.8397 | 63.7253 | -59.111 | -59.198 | -0.036621 | -0.064086 | -0.004577 | 123.111 | -0.1236 | -0.05951 | 0.027466 | -0.09613 | -0.1831 | -0.004577 | 0.091553 | -0.16937 | 0.013733 | -0.11902 | 122.8546 | 122.8867 | 59.111 | -122.9233 | 122.8546 | 122.7402 | 59.1385 | -123.0423
828.5156 | 123.1796 | -59.0515 | 63.8443 | 0.22583 | 0.0047681 | 0.06844 | 0.067296 | 0.12763 | -0.0012966 | -0.0036423 | 0.13298 | -0.0043324 | 3.6404e-05 | -0.001177 | 0.00027337 | -0.0053833 | 63.7711 | 63.945 | -0.009155 | -59.2484 | 63.8351 | -59.0836 | -59.111 | -58.9966 | 0.054932 | -59.2712 | 63.8306 | 63.7436 | -59.1156 | -59.2575 | -0.032043 | -0.059509 | -0.009155 | 122.9965 | -0.19684 | -0.13733 | -0.073242 | -0.064087 | -0.20599 | -0.013733 | 0.054932 | -0.21973 | -0.013733 | -0.10071 | 122.8867 | 122.8226 | 59.0424 | -122.9553 | 122.8821 | 122.7951 | 59.1064 | -123.1018
829.5156 | 123.1201 | -59.0378 | 63.8351 | -1.1475 | 0.0090405 | 0.065663 | 0.066655 | 0.12635 | -0.0019376 | -0.0049239 | 0.17876 | -0.0047596 | -0.0023136 | -0.0033134 | 0.0036914 | -0.0036743 | 63.8123 | 63.945 | -0.045776 | -59.2621 | 63.8214 | -59.0744 | -59.1156 | -58.9966 | 0.045776 | -59.285 | 63.8626 | 63.7436 | -59.111 | -59.2438 | -0.036621 | -0.07782 | -0.013733 | 122.9828 | -0.2243 | -0.14648 | -0.022888 | -0.073242 | -0.20599 | 0.027466 | 0.041199 | -0.24719 | -0.041199 | -0.091553 | 122.8592 | 122.85 | 58.992 | -122.9507 | 122.9004 | 122.7814 | 59.0836 | -123.0789
830.5156 | 123.0881 | -59.0332 | 63.9221 | -0.23956 | 0.010963 | 0.06545 | 0.069432 | 0.13062 | 0.0031894 | -0.0025741 | -0.088272 | -0.0030506 | 0.0004636 | -0.0003226 | 0.0019824 | -0.0045289 | 63.7802 | 63.9862 | 0.036621 | -59.2484 | 63.8855 | -59.0881 | -59.1248 | -59.0195 | 0.073242 | -59.3308 | 63.9267 | 63.8168 | -59.1293 | -59.2392 | -0.054932 | -0.091553 | -0.036621 | 123.0194 | -0.21515 | -0.1236 | -0.14191 | -0.09613 | -0.20599 | 0.004578 | 0.013733 | -0.29755 | -0.091553 | -0.10529 | 122.9187 | 122.8134 | 59.0698 | -123.0469 | 122.9599 | 122.85 | 59.1064 | -123.1613
831.5156 | 123.1888 | -59.0012 | 63.8718 | -0.1709 | 0.0062635 | 0.069081 | 0.064946 | 0.12721 | -0.0017238 | -0.0081283 | -0.33241 | -0.0054004 | -0.0021 | 0.0001046 | -0.00015383 | -0.0041017 | 64.2563 | 64.0411 | -0.054932 | -59.3216 | 63.7939 | -59.0652 | -59.0973 | -58.9233 | 0.17395 | -59.1934 | 63.8306 | 63.739 | -59.1202 | -59.2117 | -0.064087 | -0.09613 | -0.07782 | 123.0423 | -0.32043 | -0.2243 | 0.38452 | -0.11902 | -0.21057 | -0.041199 | 0.07782 | -0.19226 | 0.018311 | -0.13275 | 122.7951 | 123.2574 | 58.9462 | -122.9691 | 122.8317 | 122.7402 | 59.1751 | -123.0835
832.5156 | 123.1476 | -59.0286 | 63.8397 | 0.035095 | 0.0047681 | 0.067372 | 0.067296 | 0.12827 | -0.002792 | -0.0036423 | 0.11772 | -0.0041186 | -0.0027408 | -0.0009634 | 0.0013416 | -0.0055969 | 63.7848 | 63.9679 | -0.022888 | -59.2209 | 63.8214 | -59.0836 | -59.1156 | -58.9783 | 0.054932 | -59.2712 | 63.8397 | 63.7619 | -59.1431 | -59.2438 | -0.054932 | -0.086976 | -0.018311 | 122.9965 | -0.19226 | -0.10529 | -0.054932 | -0.11444 | -0.21515 | 0 | 0.050354 | -0.24262 | -0.027466 | -0.07782 | 122.85 | 122.8134 | 59.0057 | -122.9553 | 122.8683 | 122.7905 | 59.0836 | -123.0835
833.5312 | 123.1155 | -59.0881 | 63.8626 | -0.02594 | 0.012459 | 0.066304 | 0.072636 | 0.12977 | 0.00853 | -0.0027877 | -0.14931 | -0.00048697 | -0.0012454 | -0.0024588 | 0.0043324 | -0.0060243 | 63.9359 | 63.9404 | -0.004578 | -59.1843 | 63.8901 | -59.0881 | -59.1385 | -58.9828 | 0.073242 | -59.3124 | 63.8672 | 63.7756 | -59.1522 | -59.2438 | 0 | -0.050354 | 0.027466 | 123.0286 | -0.09613 | -0.045776 | 0.073242 | -0.064087 | -0.15564 | 0.004577 | 0.10529 | -0.2243 | -0.068665 | -0.086975 | 122.9782 | 123.024 | 59.0836 | -123.0011 | 122.9553 | 122.8638 | 59.1614 | -123.1064
834.5312 | 123.0835 | -59.0744 | 63.8718 | -0.033569 | 0.01075 | 0.065663 | 0.071782 | 0.12892 | 0.0048984 | -0.00065152 | 0.049057 | -0.0024096 | 0.001318 | -0.0003226 | 0.0032642 | -0.0041017 | 63.8123 | 63.9175 | -0.022888 | -59.2484 | 63.826 | -59.0881 | -59.1339 | -59.024 | 0.018311 | -59.3536 | 63.8763 | 63.7848 | -59.1339 | -59.2484 | -0.013733 | -0.059509 | -0.045776 | 122.9919 | -0.17395 | -0.11444 | -0.059509 | -0.059509 | -0.17395 | 0.004578 | 0.050354 | -0.27924 | -0.10529 | -0.086975 | 122.9004 | 122.8867 | 59.0515 | -123.0057 | 122.9507 | 122.8592 | 59.0927 | -123.1201
835.5312 | 123.0606 | -59.0881 | 63.858 | 0.0045777 | 0.01609 | 0.067159 | 0.067936 | 0.12913 | 0.001694 | 0.00063028 | -0.019608 | -0.0030506 | 0.0021726 | 0.0011728 | 0.002837 | -0.0049561 | 63.8168 | 63.9267 | -0.018311 | -59.2484 | 63.858 | -59.0927 | -59.1156 | -59.0103 | 0.027466 | -59.3308 | 63.8855 | 63.7848 | -59.1248 | -59.2621 | -0.004577 | -0.027466 | 0 | 123.0148 | -0.16022 | -0.13275 | -0.041199 | -0.036621 | -0.17395 | 0.027466 | 0.07782 | -0.24262 | -0.068665 | -0.073242 | 122.9462 | 122.905 | 59.0698 | -122.9736 | 122.9736 | 122.8729 | 59.1156 | -123.1201
836.5156 | 123.1293 | -59.0515 | 63.8306 | 0.12665 | 0.0054089 | 0.0678 | 0.066655 | 0.12785 | -0.0055692 | -0.0021469 | 0.23216 | -0.0030506 | -0.0040226 | -0.0005362 | 0.001128 | -0.0032471 | 63.7619 | 63.9587 | -0.032043 | -59.2484 | 63.7848 | -59.0927 | -59.1202 | -58.9966 | 0.045776 | -59.2758 | 63.8351 | 63.7527 | -59.1156 | -59.23 | -0.041198 | -0.068664 | -0.045776 | 123.0103 | -0.19684 | -0.12817 | -0.068664 | -0.064087 | -0.17853 | 0.004578 | 0.054932 | -0.2243 | -0.045776 | -0.077819 | 122.8363 | 122.8134 | 59.0195 | -122.9507 | 122.8867 | 122.8043 | 59.0973 | -123.0606
837.5156 | 123.1293 | -59.0469 | 63.8306 | 1.0956 | 0.0051953 | 0.068868 | 0.067296 | 0.12806 | -0.0032192 | -0.0047103 | 0.14061 | -0.0043324 | -0.0025272 | -0.0022452 | -0.0016492 | -0.0041017 | 63.7619 | 63.9221 | -0.050354 | -59.2575 | 63.8031 | -59.0607 | -59.1064 | -59.0195 | 0.054932 | -59.2804 | 63.858 | 63.7436 | -59.1248 | -59.2117 | -0.013733 | -0.059509 | -0.027465 | 122.9691 | -0.21057 | -0.15106 | -0.068664 | -0.07782 | -0.16479 | 0.027466 | 0.027466 | -0.23346 | -0.068665 | -0.086975 | 122.85 | 122.8088 | 58.9966 | -122.937 | 122.905 | 122.7905 | 59.1019 | -123.0423
838.5156 | 123.2117 | -59.0195 | 63.8168 | 0.012207 | 0.0066907 | 0.068013 | 0.067936 | 0.12892 | -0.0012966 | -0.0027877 | 0.087204 | -0.006255 | -0.0018862 | -0.0009634 | 0.0013416 | -0.0028199 | 63.8077 | 63.9771 | 0.022888 | -59.2255 | 63.7985 | -59.0881 | -59.1248 | -58.9645 | 0.11902 | -59.2392 | 63.8397 | 63.7619 | -59.1156 | -59.2392 | -0.068665 | -0.10529 | -0.01831 | 122.9965 | -0.20599 | -0.10071 | -0.009155 | -0.096131 | -0.21973 | 0.022889 | 0.054931 | -0.21973 | 0 | -0.054931 | 122.818 | 122.8271 | 59.0424 | -122.9416 | 122.8592 | 122.7814 | 59.1385 | -123.056
839.5312 | 123.0835 | -59.0698 | 63.858 | -0.056458 | 0.013527 | 0.065663 | 0.069859 | 0.12892 | 0.0072482 | -0.00043792 | -0.011978 | -0.001128 | 0.0008908 | 0.0007456 | 0.0015552 | -0.0062379 | 63.6475 | 64.0732 | 0.009155 | -59.2255 | 63.8672 | -59.0927 | -59.1156 | -58.9737 | 0.086975 | -59.3124 | 63.8992 | 63.7711 | -59.1339 | -59.2712 | -0.022888 | -0.045777 | 0.009155 | 123.143 | -0.15564 | -0.10986 | -0.21057 | -0.064087 | -0.20142 | 0.041199 | 0.09613 | -0.24262 | -0.041199 | -0.086975 | 122.937 | 122.7173 | 59.079 | -122.9736 | 122.9691 | 122.8409 | 59.1568 | -123.1293
840.5156 | 123.0698 | -59.0652 | 63.8992 | -0.17853 | 0.0047681 | 0.065236 | 0.069005 | 0.1302 | -0.0015102 | -0.0012923 | -0.10353 | -0.0047596 | -0.004877 | -0.0007498 | 0.0015552 | -0.0030335 | 63.8214 | 63.9908 | 0.059509 | -59.2026 | 63.8351 | -59.0744 | -59.1248 | -58.9966 | 0.1236 | -59.285 | 63.8855 | 63.8123 | -59.1293 | -59.2484 | -0.009155 | -0.059509 | -0.064087 | 123.056 | -0.13733 | -0.07782 | -0.07782 | -0.064086 | -0.1831 | -0.013733 | 0.068665 | -0.21973 | -0.036621 | -0.086975 | 122.9004 | 122.8867 | 59.1248 | -123.024 | 122.9507 | 122.8775 | 59.1888 | -123.1476
841.5156 | 123.1613 | -59.024 | 63.8397 | -0.064087 | 0.0041271 | 0.070149 | 0.069218 | 0.12977 | -0.002792 | -0.0019333 | 0.0032804 | -0.0060412 | -0.004877 | -0.004595 | 0.0051868 | -0.0021789 | 63.8672 | 64.0686 | 0.09613 | -59.1751 | 63.826 | -59.0378 | -59.1019 | -59.1385 | 0.21515 | -59.2209 | 63.8306 | 63.7436 | -59.1019 | -59.2529 | -0.013733 | -0.07782 | -0.013733 | 123.0927 | -0.15106 | -0.073242 | 0.027465 | -0.07782 | -0.22888 | -0.009156 | -0.11444 | -0.19684 | 0.032044 | -0.096131 | 122.85 | 122.8912 | 59.1202 | -122.9416 | 122.8546 | 122.7676 | 59.2392 | -123.0927
842.5156 | 123.2025 | -59.0332 | 63.8489 | -0.048828 | 0.0028455 | 0.069081 | 0.0658 | 0.12956 | -0.0019376 | -0.0036423 | -2.0643 | -0.007323 | -0.0010318 | -0.0005362 | 0.0017688 | -0.0043153 | 63.858 | 64.0778 | 0.10529 | -59.166 | 63.8306 | -59.0469 | -59.079 | -58.8455 | 0.073242 | -59.2346 | 63.8397 | 63.7253 | -59.1019 | -59.2438 | -0.013733 | -0.045776 | -0.018311 | 123.111 | -0.13275 | -0.086976 | 0.009155 | -0.068665 | -0.21057 | -0.009155 | 0.18768 | -0.20142 | 0.009155 | -0.1236 | 122.8638 | 122.8912 | 59.1385 | -122.9279 | 122.8729 | 122.7585 | 59.1064 | -123.0927
843.5156 | 123.1613 | -59.0103 | 63.8489 | -0.018311 | 0.0077587 | 0.066304 | 0.071141 | 0.12956 | -0.0019376 | -0.0015061 | 0.43816 | -0.0019824 | -0.000391 | -0.0020316 | 0.0030506 | -0.0049561 | 63.8763 | 64.0823 | 0.10986 | -59.166 | 63.8123 | -59.0652 | -59.0927 | -58.9645 | 0.20599 | -59.2209 | 63.8351 | 63.7161 | -59.111 | -59.2072 | -0.054932 | -0.082397 | -0.036621 | 123.0927 | -0.15564 | -0.073243 | 0.027466 | -0.10071 | -0.19684 | -0.013733 | 0.045776 | -0.21057 | -0.013733 | -0.13275 | 122.8226 | 122.8867 | 59.1202 | -122.9416 | 122.8455 | 122.7264 | 59.2163 | -123.056
844.5156 | 123.0606 | -59.0607 | 63.8947 | -0.18616 | 0.0094677 | 0.066304 | 0.069218 | 0.13148 | -1.505e-05 | -0.0027877 | -0.088272 | -0.0043324 | -0.0016726 | -0.0016044 | 0.00070077 | -0.0036743 | 63.8168 | 63.9862 | 0.054932 | -59.2117 | 63.8489 | -59.0744 | -59.1156 | -59.0195 | 0.12817 | -59.3124 | 63.9267 | 63.8077 | -59.111 | -59.2438 | -0.013733 | -0.054932 | -0.045776 | 123.0469 | -0.15106 | -0.09613 | -0.07782 | -0.050354 | -0.18311 | 0.032044 | 0.041199 | -0.25177 | -0.068665 | -0.086975 | 122.9095 | 122.8775 | 59.1156 | -123.0103 | 122.9874 | 122.8683 | 59.1888 | -123.1384
845.5156 | 123.0606 | -59.0515 | 63.8992 | -0.19379 | 0.010322 | 0.068227 | 0.074986 | 0.12913 | 0.0029758 | -0.0017197 | -0.29427 | -0.0036914 | 0.0011044 | -0.0016044 | 0.0026234 | -0.0058105 | 63.6841 | 63.9175 | -0.027466 | -59.2712 | 63.8443 | -59.111 | -59.1568 | -59.0469 | 0.068665 | -59.3308 | 63.9038 | 63.7985 | -59.1293 | -59.2438 | -0.059509 | -0.10529 | -0.054932 | 122.9691 | -0.21973 | -0.11444 | -0.21515 | -0.077819 | -0.19226 | 0.004578 | 0.004578 | -0.27924 | -0.086976 | -0.10071 | 122.8958 | 122.7356 | 59.024 | -123.056 | 122.9553 | 122.85 | 59.1202 | -123.143
846.5156 | 123.1567 | -59.0057 | 63.8535 | -0.079346 | 0.0058361 | 0.068013 | 0.068364 | 0.12806 | -0.0025784 | -0.0032151 | 0.17876 | -0.0036914 | -0.0001774 | 0.0003182 | 0.0015552 | -0.0041017 | 63.8809 | 64.0778 | 0.16937 | -58.8913 | 63.9084 | -59.0149 | -59.0424 | -58.9645 | 0.23346 | -59.2026 | 63.8489 | 63.7527 | -59.1156 | -59.2484 | -0.009156 | -0.036621 | 0.054931 | 123.0835 | 0.11444 | 0.15106 | 0.027465 | -0.10986 | -0.24261 | -0.004578 | 0.041198 | -0.19684 | 0.045776 | -0.10071 | 122.9141 | 122.8867 | 59.1751 | -122.8958 | 122.8546 | 122.7585 | 59.2392 | -123.1018
847.5156 | 123.0698 | -59.0469 | 63.8855 | -0.18616 | 0.0073315 | 0.071218 | 0.067723 | 0.12849 | -0.00065585 | -0.00043792 | -0.057755 | -0.0043324 | -0.0029544 | -0.0024588 | 0.001128 | -0.0066651 | 63.7985 | 63.9725 | 0.027466 | -59.2072 | 63.858 | -59.0927 | -59.1064 | -59.0515 | 0.091553 | -59.3216 | 63.9038 | 63.8031 | -59.1293 | -59.2346 | -0.045776 | -0.059509 | -0.027466 | 123.0194 | -0.16022 | -0.10071 | -0.086975 | -0.082397 | -0.18768 | 0.018311 | -0.004578 | -0.27466 | -0.086975 | -0.082397 | 122.905 | 122.8455 | 59.0744 | -122.9919 | 122.9507 | 122.85 | 59.1385 | -123.1201
848.5156 | 123.0835 | -59.079 | 63.9084 | -1.1627 | 0.0094677 | 0.065022 | 0.070286 | 0.12934 | 0.0019078 | -0.0019333 | -0.12642 | -0.0036914 | -0.0033816 | 0.0001046 | 0.002837 | -0.0049561 | 63.7299 | 63.913 | 0.004578 | -59.2575 | 63.8626 | -59.0927 | -59.1339 | -59.0469 | 0.068665 | -59.3308 | 63.8992 | 63.8123 | -59.1476 | -59.2529 | -0.013733 | -0.054932 | -0.045776 | 122.9919 | -0.17853 | -0.1236 | -0.17853 | -0.068665 | -0.17395 | -0.009155 | 0.032043 | -0.25177 | -0.07782 | -0.09613 | 122.9416 | 122.8088 | 59.0836 | -123.0423 | 122.9782 | 122.8912 | 59.1476 | -123.1613
849.5156 | 123.1476 | -59.0286 | 63.8626 | -0.14801 | 0.0064771 | 0.067586 | 0.06815 | 0.13062 | -0.0023648 | -0.0040695 | -0.11879 | -0.0043324 | -0.0018862 | -0.001818 | 0.0019824 | -0.0060243 | 63.8397 | 64.0366 | 0.10071 | -59.1843 | 63.8077 | -59.0469 | -59.0652 | -58.9783 | 0.18768 | -59.2392 | 63.8672 | 63.7756 | -59.1064 | -59.2392 | -0.018311 | -0.036622 | -0.054932 | 123.0652 | -0.15564 | -0.11902 | -0.022888 | -0.07782 | -0.21057 | 0.004577 | 0.050354 | -0.21057 | 0 | -0.086975 | 122.8363 | 122.8683 | 59.1293 | -122.9279 | 122.8958 | 122.8043 | 59.2163 | -123.1018
850.5156 | 123.0698 | -59.0515 | 63.8855 | -0.15564 | 0.0092541 | 0.066518 | 0.0705 | 0.13084 | 0.00062595 | -0.00065152 | -0.20271 | -0.002837 | -0.0018862 | -0.0003226 | 0.00048697 | -0.0051697 | 63.8077 | 63.9725 | 0.027466 | -59.2255 | 63.8718 | -59.0881 | -59.1293 | -59.0332 | 0.09613 | -59.317 | 63.8947 | 63.8077 | -59.1476 | -59.2438 | -0.036621 | -0.077819 | -0.013733 | 123.024 | -0.17395 | -0.096131 | -0.07782 | -0.09613 | -0.19226 | 0.009155 | 0.018311 | -0.2655 | -0.073243 | -0.07782 | 122.9233 | 122.8592 | 59.079 | -123.0148 | 122.9462 | 122.8592 | 59.1476 | -123.1293
851.5156 | 123.1247 | -59.0286 | 63.8901 | -0.13275 | 0.0098951 | 0.067586 | 0.067082 | 0.12934 | -0.0023648 | -0.0012923 | -0.088272 | -0.0043324 | -0.0025272 | -0.0016044 | 0.0013416 | -0.0043153 | 63.8443 | 64.032 | 0.086975 | -59.1843 | 63.8443 | -59.0744 | -59.1156 | -58.9691 | 0.17395 | -59.23 | 63.8672 | 63.7573 | -59.111 | -59.2438 | -0.045777 | -0.086976 | -0.045777 | 123.0606 | -0.15564 | -0.068664 | -0.045777 | -0.082398 | -0.21515 | -0.022889 | 0.059509 | -0.20142 | 0.013732 | -0.13275 | 122.8729 | 122.8729 | 59.1156 | -123.0057 | 122.8958 | 122.7859 | 59.2026 | -123.1338
852.5156 | 123.1979 | -59.0378 | 63.858 | -0.13275 | 0.0032727 | 0.068868 | 0.0752 | 0.12592 | -0.00044225 | 0.0010575 | -0.26375 | -0.0036914 | -0.0055178 | -0.0022452 | 0.0030506 | -0.0038879 | 63.6017 | 64.1144 | 0.10071 | -59.2346 | 63.8168 | -59.0652 | -59.111 | -58.9462 | 0.19226 | -59.2026 | 63.8535 | 63.7299 | -59.0927 | -59.2392 | -0.027466 | -0.073242 | -0.041199 | 123.1522 | -0.19684 | -0.1236 | -0.25635 | -0.054931 | -0.20142 | -0.004577 | 0.091553 | -0.16479 | 0.036621 | -0.12817 | 122.8546 | 122.6395 | 59.1385 | -122.9691 | 122.8912 | 122.7676 | 59.23 | -123.0972
853.5156 | 123.0515 | -59.0607 | 63.9084 | -0.23193 | 0.0092541 | 0.066945 | 0.0705 | 0.12849 | -0.00044225 | -0.0032151 | -0.19508 | -0.003905 | 0.0004636 | -0.0024588 | 0.002837 | -0.0045289 | 63.7894 | 63.9587 | 0 | -59.23 | 63.8718 | -59.079 | -59.1293 | -59.0286 | 0.07782 | -59.3079 | 63.9038 | 63.7711 | -59.1431 | -59.23 | -0.01831 | -0.068664 | -0.036621 | 123.0194 | -0.16937 | -0.10071 | -0.11902 | -0.082397 | -0.16937 | -0.004577 | 0.032044 | -0.24719 | -0.077819 | -0.13733 | 122.9324 | 122.85 | 59.0607 | -123.0377 | 122.9645 | 122.8317 | 59.1385 | -123.1384
854.5156 | 123.0515 | -59.0332 | 63.9587 | -0.21667 | 0.0083997 | 0.068654 | 0.068577 | 0.12913 | 0.00041235 | -0.0021469 | -0.13405 | -0.002837 | -0.0033816 | 0.000532 | 0.0024096 | -0.0041017 | 63.7939 | 63.9496 | 0.027466 | -59.2392 | 63.8672 | -59.0744 | -59.1293 | -59.0332 | 0.064087 | -59.3216 | 63.9084 | 63.8077 | -59.1385 | -59.2529 | -0.041199 | -0.09613 | -0.091553 | 122.9828 | -0.20599 | -0.10986 | -0.16479 | -0.10529 | -0.21973 | -0.050354 | 0 | -0.28839 | -0.068664 | -0.15106 | 122.9004 | 122.8271 | 59.0607 | -123.0881 | 122.9416 | 122.8409 | 59.0973 | -123.2117
855.5156 | 123.1247 | -59.0744 | 63.826 | 0.2182 | 0.012672 | 0.068654 | 0.071141 | 0.12657 | 0.0019078 | -0.0015061 | 0.25505 | -5.9768e-05 | -0.001459 | -0.0003226 | 0.002837 | -0.0038879 | 63.7756 | 63.8809 | -0.09613 | -59.2758 | 63.8443 | -59.1064 | -59.1431 | -59.0149 | 0 | -59.3124 | 63.8306 | 63.7482 | -59.1339 | -59.2575 | -0.032043 | -0.068664 | 0.01831 | 122.9553 | -0.20142 | -0.13275 | -0.050354 | -0.059509 | -0.1831 | 0.004577 | 0.059509 | -0.23804 | -0.054932 | -0.07782 | 122.9187 | 122.85 | 58.9783 | -122.9691 | 122.905 | 122.8226 | 59.0744 | -123.0835
856.5156 | 123.0927 | -59.0424 | 63.8763 | -0.15564 | 0.01139 | 0.066945 | 0.069859 | 0.12998 | 0.003403 | -0.0017197 | -0.12642 | -0.002837 | -0.0027408 | -0.0022452 | 0.0019824 | -0.0043153 | 63.7894 | 63.9084 | -0.013733 | -59.23 | 63.8763 | -59.0927 | -59.1248 | -59.024 | 0.091553 | -59.2941 | 63.8947 | 63.8168 | -59.1202 | -59.2575 | -0.050354 | -0.082398 | 0 | 122.9507 | -0.18768 | -0.10529 | -0.086975 | -0.07782 | -0.21515 | 0.01831 | 0.01831 | -0.25177 | -0.036621 | -0.05951 | 122.9187 | 122.8317 | 59.0286 | -123.0011 | 122.937 | 122.8592 | 59.1339 | -123.1338
857.5156 | 123.056 | -59.0744 | 63.9084 | -0.17853 | 0.011177 | 0.068013 | 0.067936 | 0.13041 | -0.0017238 | -0.0027877 | -0.12642 | -0.0041186 | -0.0038088 | -0.0016044 | 0.001128 | -0.0034607 | 63.7802 | 63.9542 | 0.009155 | -59.23 | 63.8718 | -59.0607 | -59.1385 | -59.0332 | 0.086975 | -59.317 | 63.9084 | 63.8123 | -59.1293 | -59.2392 | 0.013733 | -0.064087 | -0.036621 | 123.0286 | -0.15564 | -0.091553 | -0.12817 | -0.054931 | -0.16479 | 0 | 0.041199 | -0.24262 | -0.07782 | -0.09613 | 122.9462 | 122.8546 | 59.0836 | -123.0469 | 122.9828 | 122.8867 | 59.1614 | -123.1476
858.5156 | 123.1613 | -59.0286 | 63.858 | -0.15564 | 0.0079723 | 0.066304 | 0.068791 | 0.12742 | -0.0030056 | -0.00086512 | -0.080643 | -0.0026234 | -0.0018862 | -0.0022452 | -0.00015383 | -0.0055969 | 63.8351 | 64.0411 | 0.086975 | -59.1797 | 63.826 | -59.0469 | -59.1019 | -58.9828 | 0.16937 | -59.23 | 63.8672 | 63.7802 | -59.1385 | -59.23 | -0.018311 | -0.073243 | -0.032043 | 123.0698 | -0.15106 | -0.077819 | -0.022888 | -0.10986 | -0.20142 | 0.009155 | 0.045776 | -0.20142 | 0 | -0.07782 | 122.8546 | 122.8638 | 59.1156 | -122.9599 | 122.8958 | 122.8088 | 59.198 | -123.0881
859.5156 | 123.111 | -59.0698 | 63.8947 | -0.13275 | 0.01139 | 0.064595 | 0.071354 | 0.13191 | 0.003403 | -0.0023605 | -0.14168 | -0.0034778 | 0.0006772 | 0.000532 | 0.0013416 | -0.0045289 | 63.7711 | 63.9221 | -0.009155 | -59.2529 | 63.8626 | -59.0836 | -59.1385 | -59.0103 | 0.082397 | -59.2987 | 63.9038 | 63.7848 | -59.1293 | -59.2346 | -0.013733 | -0.068665 | -0.032043 | 122.9919 | -0.18311 | -0.11444 | -0.1236 | -0.059509 | -0.1648 | 0.009156 | 0.059509 | -0.22888 | -0.064087 | -0.10986 | 122.9324 | 122.8409 | 59.0607 | -123.0331 | 122.9736 | 122.8546 | 59.1522 | -123.1293
860.5156 | 123.0652 | -59.0607 | 63.8855 | -0.19379 | 0.0081861 | 0.067159 | 0.070073 | 0.12977 | -0.0019376 | -0.0019333 | -0.12642 | -0.002837 | -0.0016726 | -0.0020316 | -0.00058103 | -0.0023927 | 63.8123 | 63.9771 | 0.045776 | -59.2026 | 63.8351 | -59.0607 | -59.1202 | -59.0378 | 0.10071 | -59.2804 | 63.8901 | 63.8077 | -59.111 | -59.23 | 0 | -0.059509 | -0.050354 | 123.0377 | -0.14191 | -0.082398 | -0.073242 | -0.050354 | -0.16937 | 0.004578 | 0.022888 | -0.21973 | -0.050354 | -0.07782 | 122.8958 | 122.8729 | 59.1064 | -123.0057 | 122.9507 | 122.8683 | 59.1614 | -123.1155
861.5156 | 123.1064 | -59.024 | 63.8809 | -0.18616 | 0.0088269 | 0.066304 | 0.067723 | 0.12934 | -0.0032192 | -0.0023605 | -0.080643 | -0.0036914 | -0.0042362 | -0.0030996 | 5.9768e-05 | -0.0053833 | 63.8168 | 63.9908 | 0.050354 | -59.1934 | 63.826 | -59.0469 | -59.1064 | -59.0012 | 0.11902 | -59.2621 | 63.8901 | 63.8031 | -59.1385 | -59.2346 | -0.022888 | -0.082397 | -0.054931 | 123.0148 | -0.16937 | -0.086975 | -0.064087 | -0.11444 | -0.21057 | 0.009156 | 0.022888 | -0.23804 | -0.027466 | -0.077819 | 122.85 | 122.8409 | 59.0744 | -122.9874 | 122.9141 | 122.8271 | 59.1431 | -123.1155
862.5156 | 123.1155 | -59.0286 | 63.8992 | -0.1709 | 0.0079723 | 0.067586 | 0.067509 | 0.12849 | -0.0019376 | -0.0038559 | -0.11879 | -0.003905 | -0.001459 | -0.0009634 | 0.0024096 | -0.0028199 | 63.8214 | 64.0182 | 0.073242 | -59.2072 | 63.826 | -59.0607 | -59.0973 | -59.0012 | 0.14648 | -59.2621 | 63.8809 | 63.7756 | -59.1019 | -59.2346 | -0.032044 | -0.068665 | -0.073242 | 123.0469 | -0.17853 | -0.10986 | -0.07782 | -0.073243 | -0.20599 | -0.018311 | 0.027465 | -0.23346 | -0.027466 | -0.1236 | 122.8546 | 122.85 | 59.1019 | -122.9965 | 122.9095 | 122.8043 | 59.1751 | -123.1338
863.5156 | 123.111 | -59.0607 | 63.8809 | -0.14038 | 0.012459 | 0.066945 | 0.069218 | 0.13062 | 0.0042576 | -0.0010787 | -0.11116 | -0.0043324 | 0.0004636 | 0.0007456 | 0.0026234 | -0.0051697 | 63.7848 | 63.9359 | -0.013733 | -59.2117 | 63.8992 | -59.0881 | -59.1339 | -59.0103 | 0.091553 | -59.3033 | 63.9084 | 63.7894 | -59.1339 | -59.2255 | -0.027466 | -0.073242 | 0.018311 | 122.9965 | -0.15106 | -0.07782 | -0.09613 | -0.073242 | -0.1648 | 0.027466 | 0.050354 | -0.24262 | -0.07782 | -0.091552 | 122.9599 | 122.8455 | 59.0469 | -123.0148 | 122.9691 | 122.85 | 59.1522 | -123.1064
864.5156 | 123.1018 | -59.0561 | 63.9175 | -0.31586 | 0.0098951 | 0.067586 | 0.069645 | 0.1287 | -0.00065585 | -0.0027877 | -0.14168 | -0.0034778 | -0.0025272 | -0.001818 | 0.0026234 | -0.0026063 | 63.7436 | 63.913 | 0.009155 | -59.2484 | 63.8855 | -59.0927 | -59.1293 | -59.0378 | 0.064087 | -59.3216 | 63.9084 | 63.7848 | -59.1431 | -59.2529 | -0.036621 | -0.073242 | -0.032044 | 122.9691 | -0.19226 | -0.11902 | -0.17395 | -0.086975 | -0.19684 | -0.009156 | 0.01831 | -0.2655 | -0.068664 | -0.13275 | 122.9416 | 122.7997 | 59.0652 | -123.0469 | 122.9645 | 122.8409 | 59.1202 | -123.1705
865.5156 | 123.0698 | -59.0652 | 63.8901 | -0.17853 | 0.0075451 | 0.069081 | 0.06815 | 0.12785 | -0.0030056 | -0.0015061 | -0.11879 | -0.003905 | -0.0001774 | 0.0001046 | 0.00048697 | -0.0049561 | 63.8123 | 63.9679 | 0.054932 | -59.2026 | 63.8672 | -59.0744 | -59.0927 | -59.0332 | 0.13733 | -59.2987 | 63.9267 | 63.8397 | -59.111 | -59.2529 | -0.009155 | -0.027465 | -0.022889 | 123.0331 | -0.13733 | -0.10986 | -0.07782 | -0.045776 | -0.18768 | 0.036621 | 0.032044 | -0.23346 | -0.045776 | -0.050354 | 122.9324 | 122.8775 | 59.1202 | -122.9828 | 122.9919 | 122.905 | 59.2026 | -123.143
866.5156 | 123.0972 | -59.0469 | 63.8855 | -0.1709 | 0.0086133 | 0.069509 | 0.067082 | 0.1334 | -0.0023648 | -0.0040695 | -0.080643 | -0.0036914 | -0.0023136 | -0.0016044 | 0.002837 | -0.0043153 | 63.8123 | 63.9908 | 0.068665 | -59.1843 | 63.8306 | -59.0515 | -59.0836 | -59.0103 | 0.13275 | -59.2667 | 63.8809 | 63.8077 | -59.111 | -59.2438 | -0.004578 | -0.036621 | -0.054932 | 123.0377 | -0.13733 | -0.10071 | -0.073242 | -0.064087 | -0.19684 | -0.004578 | 0.036621 | -0.21973 | -0.022889 | -0.07782 | 122.8775 | 122.8592 | 59.1156 | -122.9691 | 122.9279 | 122.8546 | 59.1797 | -123.1293
867.5156 | 123.0606 | -59.079 | 63.9038 | -0.20142 | 0.0047681 | 0.067159 | 0.069005 | 0.1287 | -0.00044225 | -0.00086512 | -0.080643 | -0.0032642 | 0.0006772 | -0.0013906 | 0.001128 | -0.0051697 | 63.7848 | 63.9267 | -0.009155 | -59.2392 | 63.8763 | -59.0744 | -59.1202 | -59.0469 | 0.086975 | -59.2392 | 63.9175 | 63.8351 | -59.0927 | -59.2255 | 0.004577 | -0.041199 | -0.027466 | 123.0057 | -0.16022 | -0.11902 | -0.11902 | -0.013733 | -0.14649 | 0.013733 | 0.032043 | -0.16022 | -0.013733 | -0.068665 | 122.9553 | 122.8638 | 59.0698 | -123.024 | 122.9965 | 122.9141 | 59.166 | -123.1293
868.5156 | 123.175 | -59.024 | 63.8626 | -0.10223 | 0.0056225 | 0.066731 | 0.066655 | 0.12934 | -0.0030056 | -0.0053513 | -0.2256 | -0.0032642 | -0.0029544 | -0.0009634 | 0.001128 | -0.0038879 | 64.2654 | 63.7939 | -0.086975 | -59.2987 | 63.8123 | -59.0561 | -59.1019 | -58.9508 | 0.17395 | -59.1843 | 63.8351 | 63.7619 | -59.0973 | -59.2438 | -0.032043 | -0.07782 | -0.050354 | 122.818 | -0.27466 | -0.19684 | 0.40283 | -0.073242 | -0.21973 | -0.027466 | 0.073242 | -0.16022 | 0.059509 | -0.10071 | 122.8363 | 123.2895 | 58.9371 | -122.9645 | 122.8592 | 122.7859 | 59.198 | -123.1064
869.5312 | 123.1888 | -59.0607 | 63.8123 | 0.18768 | 0.0096813 | 0.066304 | 0.067936 | 0.13148 | 0.002335 | -0.00065152 | 0.23216 | -0.0054004 | -0.0008182 | -0.0009634 | 0.0034778 | -0.0070923 | 63.8306 | 63.9633 | -0.018311 | -59.2072 | 63.7939 | -59.0698 | -59.1248 | -58.9188 | -0.30212 | -59.23 | 63.7802 | 63.6841 | -59.1614 | -59.2392 | -0.009155 | -0.064087 | -0.018311 | 123.024 | -0.14648 | -0.082397 | 0.01831 | -0.10071 | -0.17853 | -0.032044 | 0.14191 | -0.16937 | 0.009155 | -0.12817 | 122.8546 | 122.8912 | 59.0424 | -122.937 | 122.8409 | 122.7448 | 58.7585 | -123.0515
870.5156 | 123.056 | -59.0561 | 63.913 | -0.17853 | 0.0096813 | 0.067586 | 0.070714 | 0.12892 | -0.001083 | -0.00022432 | -0.095902 | -0.0043324 | 3.6404e-05 | -0.0003226 | 0.002196 | -0.0045289 | 63.7665 | 63.9084 | -0.027466 | -59.2438 | 63.8718 | -59.0927 | -59.1339 | -59.0469 | 0.054932 | -59.3353 | 63.9221 | 63.7894 | -59.1522 | -59.2346 | -0.036621 | -0.07782 | -0.041199 | 122.9645 | -0.18768 | -0.10986 | -0.14649 | -0.096131 | -0.17853 | 0.009155 | 0.009155 | -0.27924 | -0.10071 | -0.1236 | 122.9279 | 122.8226 | 59.0286 | -123.0469 | 122.9782 | 122.8455 | 59.111 | -123.1476
871.5156 | 123.1567 | -59.024 | 63.8763 | -0.15564 | 0.0092541 | 0.068868 | 0.06815 | 0.13041 | -0.002792 | -0.00086512 | -0.042496 | -0.004546 | -0.0027408 | -0.0013906 | 0.00070077 | -0.0053833 | 63.8077 | 64.0503 | 0.091553 | -59.1751 | 63.8443 | -59.0195 | -59.111 | -58.9828 | 0.17853 | -59.2255 | 63.8489 | 63.7894 | -59.1019 | -59.2346 | 0.004578 | -0.086975 | -0.032044 | 123.0743 | -0.15106 | -0.064087 | -0.068665 | -0.07782 | -0.21057 | -0.027466 | 0.041199 | -0.20142 | 0.009155 | -0.086975 | 122.8683 | 122.8317 | 59.1156 | -122.9874 | 122.8729 | 122.8134 | 59.2026 | -123.111
872.5156 | 123.1659 | -59.0332 | 63.8489 | -0.041199 | 0.0051953 | 0.067586 | 0.064946 | 0.12635 | -0.004501 | -0.0034287 | -0.011978 | -0.0036914 | -0.0018862 | -0.0005362 | -0.00015383 | -0.0064515 | 63.8443 | 64.0411 | 0.10529 | -59.1751 | 63.8306 | -59.0515 | -59.1064 | -58.7402 | 0.32044 | -59.4086 | 63.8763 | 63.739 | -59.1339 | -59.2392 | -0.018311 | -0.073242 | -0.018311 | 123.0743 | -0.14191 | -0.068665 | -0.004578 | -0.10071 | -0.20599 | 0.027466 | 0.29297 | -0.37537 | -0.16937 | -0.10986 | 122.8638 | 122.8775 | 59.1385 | -122.9553 | 122.9095 | 122.7722 | 59.3536 | -123.0881
873.5156 | 123.0743 | -59.0515 | 63.8992 | -0.10986 | 0.012245 | 0.066945 | 0.068577 | 0.12956 | 0.0025486 | -0.0032151 | -0.15694 | -0.0032642 | -0.0006046 | 0.0016 | 0.0034778 | -0.0075195 | 63.7711 | 63.9038 | -0.013733 | -59.2575 | 63.8763 | -59.1064 | -59.1156 | -59.0424 | 0.064087 | -59.3216 | 63.9084 | 63.8031 | -59.1339 | -59.2255 | -0.054931 | -0.064087 | -0.022888 | 122.9553 | -0.20599 | -0.14191 | -0.12817 | -0.082397 | -0.17395 | 0.009155 | 0.009156 | -0.27008 | -0.09613 | -0.09613 | 122.9279 | 122.8226 | 59.0378 | -123.0148 | 122.9599 | 122.8546 | 59.1156 | -123.1247
874.5156 | 123.175 | -59.0149 | 63.8535 | -0.10223 | 0.0049817 | 0.066518 | 0.067723 | 0.12785 | -0.0040738 | -0.00086512 | 0.40001 | -0.0049732 | -0.0027408 | 0.0009592 | 5.9768e-05 | -0.0060243 | 63.858 | 64.0823 | 0.11902 | -59.1843 | 63.826 | -59.0652 | -59.0881 | -58.9188 | 0.15106 | -59.2346 | 63.826 | 63.7436 | -59.1156 | -59.2072 | -0.050354 | -0.073242 | -0.027466 | 123.0972 | -0.16937 | -0.09613 | 0.004577 | -0.10071 | -0.19226 | -0.027466 | 0.096131 | -0.21973 | -0.027466 | -0.10986 | 122.8409 | 122.8729 | 59.1339 | -122.9416 | 122.8409 | 122.7585 | 59.166 | -123.0606
875.5156 | 123.0835 | -59.0607 | 63.8947 | -0.19379 | 0.010109 | 0.0678 | 0.070714 | 0.12892 | 0.004044 | -0.0019333 | -0.10353 | -0.002196 | 0.0017454 | -0.001818 | 0.0043324 | -0.0062379 | 63.7711 | 63.9084 | -0.009155 | -59.2529 | 63.8763 | -59.0881 | -59.1202 | -59.024 | 0.064087 | -59.3216 | 63.9175 | 63.8031 | -59.1202 | -59.2667 | -0.027466 | -0.059509 | -0.01831 | 122.9691 | -0.19226 | -0.13275 | -0.1236 | -0.059509 | -0.20599 | 0.022889 | 0.036621 | -0.26093 | -0.054931 | -0.091552 | 122.937 | 122.8317 | 59.0515 | -123.0148 | 122.9782 | 122.8638 | 59.1248 | -123.1613
876.5156 | 123.1476 | -59.0286 | 63.8763 | -0.11749 | 0.0071179 | 0.067586 | 0.067296 | 0.13041 | -0.0036464 | -0.0027877 | -0.080643 | -0.0049732 | -0.0018862 | -0.003527 | 0.0024096 | -0.0030335 | 63.8443 | 64.032 | 0.082397 | -59.166 | 63.8397 | -59.0561 | -59.1156 | -58.9691 | 0.17395 | -59.2209 | 63.8626 | 63.7848 | -59.111 | -59.2163 | -0.027466 | -0.086976 | -0.036621 | 123.0606 | -0.13733 | -0.050354 | -0.032044 | -0.082398 | -0.18768 | -0.013733 | 0.059509 | -0.19226 | -0.004577 | -0.091553 | 122.8683 | 122.8729 | 59.111 | -122.9919 | 122.8912 | 122.8134 | 59.2026 | -123.0927
877.5156 | 123.1201 | -59.0149 | 63.8535 | -0.071716 | 0.0073315 | 0.067586 | 0.069859 | 0.12806 | -0.0042874 | -0.0019333 | -0.019608 | -0.004546 | -0.003168 | -0.0016044 | 0.0024096 | -0.0047425 | 63.8535 | 64.0594 | 0.07782 | -59.2072 | 63.8214 | -59.0881 | -59.1156 | -58.9279 | 0.70953 | -59.23 | 63.9038 | 63.7756 | -59.1019 | -59.2484 | -0.073242 | -0.10071 | -0.032044 | 123.0743 | -0.19226 | -0.091552 | 0 | -0.086975 | -0.23346 | 0.050354 | 0.086976 | -0.21515 | 0.01831 | -0.07782 | 122.8363 | 122.8683 | 59.0927 | -122.9691 | 122.9187 | 122.7905 | 59.7244 | -123.1018
878.5156 | 123.1842 | -59.0424 | 63.8351 | 0.035095 | 0.0066907 | 0.067586 | 0.0658 | 0.12827 | -0.0023648 | -0.0036423 | 0.064316 | -0.002837 | -0.003168 | -0.0033134 | 0.0024096 | -0.0043153 | 63.7802 | 63.9679 | 0.009155 | -59.2163 | 63.8123 | -59.0561 | -59.1202 | -58.9645 | 0.10071 | -59.2621 | 63.8168 | 63.7527 | -59.1248 | -59.2346 | -0.013733 | -0.07782 | -0.022888 | 123.0103 | -0.17395 | -0.096131 | -0.054932 | -0.082398 | -0.19226 | -0.018311 | 0.077819 | -0.21973 | -0.027466 | -0.082397 | 122.8546 | 122.8226 | 59.0515 | -122.9553 | 122.8592 | 122.7951 | 59.1431 | -123.0698
879.5156 | 123.1888 | -59.024 | 63.8306 | 0.019836 | 0.0047681 | 0.066945 | 0.069645 | 0.12956 | -0.00044225 | -0.0021469 | 0.056686 | -0.0060412 | -0.0029544 | -0.0016044 | 0.00070077 | -0.0055969 | 63.8168 | 63.9999 | 0.045776 | -59.2072 | 63.8351 | -59.0836 | -59.1202 | -58.9554 | 0.1236 | -59.23 | 63.8397 | 63.7436 | -59.1019 | -59.2026 | -0.059509 | -0.09613 | 0.004578 | 123.024 | -0.1831 | -0.086975 | -0.013733 | -0.07782 | -0.17853 | 0.009156 | 0.068665 | -0.20599 | -0.027466 | -0.086975 | 122.8592 | 122.8409 | 59.0698 | -122.9507 | 122.8638 | 122.7676 | 59.1476 | -123.0331
880.5156 | 123.0789 | -59.0698 | 63.8947 | -0.19379 | 0.010322 | 0.068654 | 0.069432 | 0.12956 | -0.00044225 | -0.0049239 | -0.088272 | -0.0030506 | -0.0027408 | -0.001818 | 0.0024096 | -0.0058105 | 63.8214 | 63.9038 | -0.009155 | -59.2529 | 63.8626 | -59.0744 | -59.1064 | -59.0286 | 0 | -59.1797 | 63.9633 | 63.8535 | -59.1156 | -59.2255 | -0.004578 | -0.036621 | -0.032043 | 122.9736 | -0.18311 | -0.14648 | -0.073242 | -0.045777 | -0.15564 | 0.068665 | 0.041199 | -0.10986 | 0.045777 | -0.041198 | 122.9324 | 122.8912 | 59.0607 | -123.0011 | 123.0331 | 122.9233 | 59.0698 | -123.1201
881.5156 | 123.1613 | -59.0515 | 63.8443 | -0.0030518 | 0.0058361 | 0.06844 | 0.06815 | 0.12977 | -0.0036464 | -0.0025741 | 0.11772 | -0.0032642 | -0.0046634 | -0.001177 | 0.00070077 | -0.0049561 | 63.7848 | 63.9633 | -0.009155 | -59.2255 | 63.8168 | -59.0927 | -59.1156 | -58.9737 | 0.082397 | -59.2667 | 63.8306 | 63.7436 | -59.1248 | -59.2392 | -0.041198 | -0.064087 | -0.027466 | 123.0148 | -0.17395 | -0.10986 | -0.059509 | -0.073242 | -0.18768 | -0.013733 | 0.07782 | -0.21515 | -0.027466 | -0.10071 | 122.8683 | 122.8363 | 59.0424 | -122.9599 | 122.8821 | 122.7951 | 59.1339 | -123.0835
882.5156 | 123.1293 | -59.0652 | 63.8031 | 0.16479 | 0.0056225 | 0.066945 | 0.067296 | 0.12934 | -0.001083 | -0.0015061 | 0.20164 | -0.0032642 | -0.0040226 | -0.001818 | -0.00015383 | -0.0038879 | 63.8077 | 63.9587 | -0.018311 | -59.2575 | 63.8123 | -59.111 | -59.1248 | -58.9966 | 0.036621 | -59.2758 | 63.826 | 63.7619 | -59.111 | -59.2438 | -0.045776 | -0.059509 | 0.009155 | 123.024 | -0.19226 | -0.13275 | 0.004577 | -0.045776 | -0.17853 | 0.022888 | 0.068665 | -0.21057 | -0.032044 | -0.041199 | 122.8775 | 122.8729 | 59.0469 | -122.9279 | 122.8912 | 122.8271 | 59.1019 | -123.0469
883.5156 | 123.2254 | -59.0103 | 63.8535 | 0.0045777 | 0.0036999 | 0.066091 | 0.066227 | 0.12892 | 0.00019875 | -0.00086512 | 0.064316 | -0.005614 | -0.0038088 | -0.0033134 | 0.00027337 | -0.0038879 | 63.8535 | 64.0091 | 0.059509 | -59.1934 | 63.8168 | -59.079 | -59.0927 | -58.905 | 0.16022 | -59.2026 | 63.8443 | 63.7436 | -59.0927 | -59.2117 | -0.068664 | -0.082397 | -0.036622 | 123.0194 | -0.18311 | -0.10071 | 0 | -0.082397 | -0.20142 | -0.009156 | 0.10529 | -0.19226 | 0.009155 | -0.10986 | 122.8271 | 122.8638 | 59.0698 | -122.9462 | 122.8546 | 122.7539 | 59.1705 | -123.0652
884.5156 | 123.1293 | -59.0286 | 63.8123 | 0.17242 | 0.0047681 | 0.067159 | 0.067723 | 0.12806 | 0.0027622 | -0.0025741 | 0.25505 | -0.0047596 | -0.0023136 | -0.001177 | 0.0015552 | -0.0032471 | 63.8397 | 63.9908 | -0.018311 | -59.2346 | 63.7894 | -59.1019 | -59.1248 | -58.9691 | 0.032043 | -59.2667 | 63.7985 | 63.7299 | -59.1431 | -59.2209 | -0.073243 | -0.096131 | -0.022888 | 123.0194 | -0.20599 | -0.10986 | 0.027466 | -0.11444 | -0.19226 | -0.013733 | 0.059509 | -0.23804 | -0.045777 | -0.082398 | 122.818 | 122.8683 | 59.0103 | -122.937 | 122.8271 | 122.7585 | 59.0607 | -123.0331
885.5156 | 123.1567 | -59.024 | 63.8489 | -0.0030518 | 0.0077587 | 0.066945 | 0.066655 | 0.12742 | -0.0034328 | -0.0025741 | 0.071945 | -0.0049732 | -0.0035952 | -0.001177 | 0.00027337 | -0.0043153 | 63.8123 | 63.9587 | 0.032043 | -59.2209 | 63.8351 | -59.079 | -59.1064 | -58.9508 | 0.086975 | -59.2392 | 63.8443 | 63.7711 | -59.0836 | -59.23 | -0.054931 | -0.082397 | -0.013733 | 122.9828 | -0.19684 | -0.11444 | -0.036621 | -0.059509 | -0.20599 | -0.004578 | 0.073242 | -0.21515 | -0.009155 | -0.07782 | 122.8592 | 122.8363 | 59.0561 | -122.9553 | 122.8683 | 122.7951 | 59.111 | -123.0789
886.5156 | 123.1659 | -59.0378 | 63.8031 | 0.14954 | 0.0083997 | 0.068013 | 0.067936 | 0.13062 | 0.00083955 | -0.0021469 | 0.2932 | -0.0034778 | -0.0021 | -0.0003226 | 0.0036914 | -0.0051697 | 63.8351 | 63.9633 | -0.004578 | -59.2438 | 63.8031 | -59.1019 | -59.1385 | -58.9783 | 0.022888 | -59.2941 | 63.8168 | 63.7024 | -59.1339 | -59.2392 | -0.064087 | -0.10071 | 0 | 123.0011 | -0.20599 | -0.10529 | 0.032043 | -0.09613 | -0.20142 | 0.013732 | 0.05951 | -0.25635 | -0.054931 | -0.10071 | 122.8409 | 122.8729 | 59.0332 | -122.9416 | 122.8546 | 122.7402 | 59.0607 | -123.0423
887.5156 | 123.1293 | -59.0195 | 63.8397 | 0.09613 | 0.0086133 | 0.068227 | 0.066441 | 0.12956 | -0.00086945 | -0.00086512 | 0.14061 | -0.003905 | -0.003168 | -0.0033134 | 0.0019824 | -0.0051697 | 63.8168 | 63.9542 | -0.027466 | -59.2484 | 63.8351 | -59.079 | -59.1248 | -58.9874 | 0.059509 | -59.2712 | 63.8489 | 63.7436 | -59.111 | -59.2484 | -0.059509 | -0.10529 | -0.004578 | 122.9736 | -0.22888 | -0.1236 | -0.022889 | -0.091553 | -0.22888 | 0.009155 | 0.032043 | -0.25177 | -0.022888 | -0.096131 | 122.8546 | 122.8363 | 58.992 | -122.9645 | 122.8683 | 122.7631 | 59.079 | -123.0881
888.5156 | 123.1705 | -59.0424 | 63.8397 | 0.035095 | 0.0077587 | 0.071431 | 0.067509 | 0.12892 | -0.00022865 | -0.0012923 | 0.087204 | -0.0024096 | -0.0046634 | -0.0020316 | 0.0026234 | -0.0041017 | 63.8123 | 63.9725 | 0.013733 | -59.2209 | 63.826 | -59.079 | -59.1293 | -58.9554 | 0.10529 | -59.2575 | 63.8626 | 63.7482 | -59.1339 | -59.2529 | -0.036621 | -0.086975 | -0.013733 | 123.0148 | -0.17853 | -0.091553 | -0.027466 | -0.091553 | -0.21057 | 0.022888 | 0.086975 | -0.21515 | -0.004577 | -0.091553 | 122.8683 | 122.8546 | 59.0561 | -122.9691 | 122.905 | 122.7905 | 59.1476 | -123.0927
889.5156 | 123.1842 | -59.024 | 63.8306 | -0.17853 | 0.0064771 | 0.068013 | 0.06815 | 0.12785 | -1.505e-05 | -0.0023605 | -0.073013 | -0.006255 | -0.0040226 | -0.0022452 | 0.002196 | -0.0026063 | 63.8901 | 64.0594 | 0.10529 | -59.1843 | 63.8214 | -59.0515 | -59.0927 | -58.9096 | 0.45776 | -59.0057 | 63.9221 | 63.7894 | -59.0698 | -59.2392 | -0.027466 | -0.068664 | -0.009155 | 123.0835 | -0.16022 | -0.091553 | 0.05951 | -0.045776 | -0.21515 | 0.091553 | 0.11444 | 0.018311 | 0.23346 | -0.041198 | 122.8455 | 122.9141 | 59.1293 | -122.9233 | 122.9462 | 122.8134 | 59.4818 | -123.0698
890.5156 | 123.1567 | -59.0378 | 63.8077 | 0.12665 | 0.01075 | 0.067372 | 0.067082 | 0.12849 | 0.0021214 | -0.0019333 | 0.23979 | -0.005614 | -0.0025272 | -0.0009634 | 0.0034778 | -0.0060243 | 63.8535 | 63.9725 | -0.013733 | -59.2392 | 63.8031 | -59.0698 | -59.1385 | -58.9371 | 0.064087 | -59.2667 | 63.8214 | 63.7024 | -59.1385 | -59.2712 | -0.032043 | -0.10071 | -0.004577 | 123.0103 | -0.20142 | -0.10071 | 0.045777 | -0.10071 | -0.23346 | 0.013733 | 0.10071 | -0.22888 | 0.004577 | -0.10529 | 122.8409 | 122.8912 | 59.024 | -122.9462 | 122.8592 | 122.7402 | 59.1019 | -123.0789
891.5156 | 123.0789 | -59.0378 | 63.8489 | 0.14954 | 0.0075451 | 0.068654 | 0.065159 | 0.12913 | 0.00041235 | -0.0023605 | 0.18639 | -0.0026234 | -0.003168 | -0.0003226 | 0.0017688 | -0.0047425 | 63.8214 | 63.9359 | -0.041199 | -59.2575 | 63.8077 | -59.0652 | -59.1019 | -58.9737 | 0.036621 | -59.2941 | 63.8306 | 63.7436 | -59.111 | -59.23 | -0.027466 | -0.064087 | -0.041199 | 122.9736 | -0.21973 | -0.15564 | -0.027466 | -0.073242 | -0.19226 | -0.018311 | 0.064087 | -0.25635 | -0.064086 | -0.10529 | 122.8455 | 122.8592 | 58.9966 | -122.9507 | 122.8683 | 122.7814 | 59.0744 | -123.0789
892.5156 | 123.1567 | -59.0607 | 63.7894 | 0.16479 | 0.0092541 | 0.066518 | 0.067296 | 0.12827 | -0.0017238 | 0.00041648 | 0.20927 | -0.0043324 | -0.0042362 | -0.0007498 | 0.0017688 | -0.0047425 | 63.8535 | 63.9908 | -0.013733 | -59.2163 | 63.7756 | -59.079 | -59.1156 | -58.96 | 0.064087 | -59.2712 | 63.8123 | 63.6978 | -59.1522 | -59.2575 | -0.01831 | -0.054932 | -0.013733 | 123.0515 | -0.15564 | -0.10071 | 0.064087 | -0.091553 | -0.19684 | 0.022888 | 0.10071 | -0.21057 | -0.013733 | -0.091553 | 122.8363 | 122.9141 | 59.0469 | -122.905 | 122.8729 | 122.7585 | 59.1248 | -123.0469
893.5156 | 123.2529 | -59.0286 | 63.8443 | 0.09613 | 0.0086133 | 0.068654 | 0.064732 | 0.12934 | 0.00019875 | -0.0030013 | 0.20927 | -0.0024096 | -0.0038088 | 0.0001046 | -0.00079463 | -0.0055969 | 63.8077 | 63.9267 | -0.036621 | -59.2575 | 63.8077 | -59.079 | -59.0927 | -58.9874 | 0.050354 | -59.2896 | 63.8489 | 63.7482 | -59.1156 | -59.2163 | -0.050354 | -0.064087 | -0.036621 | 122.9553 | -0.22888 | -0.16479 | -0.036621 | -0.086976 | -0.18768 | 0.004578 | 0.041198 | -0.26093 | -0.073242 | -0.09613 | 122.8363 | 122.8363 | 58.992 | -122.937 | 122.8775 | 122.7768 | 59.079 | -123.0606
894.5156 | 123.1476 | -59.0561 | 63.8306 | 0.2182 | 0.013099 | 0.06844 | 0.070714 | 0.13105 | 0.0036166 | -0.0019333 | 0.2169 | -0.002837 | -0.0006046 | -0.0030996 | 0.0036914 | -0.0041017 | 63.8123 | 63.8809 | -0.082397 | -59.2667 | 63.8214 | -59.1064 | -59.1568 | -58.9874 | -0.018311 | -59.3079 | 63.8351 | 63.7527 | -59.1751 | -59.2529 | -0.050354 | -0.10071 | -0.009155 | 122.937 | -0.21057 | -0.10986 | -0.01831 | -0.11902 | -0.19684 | 0.004578 | 0.068664 | -0.25177 | -0.054931 | -0.077819 | 122.8775 | 122.8683 | 58.9737 | -122.9874 | 122.8912 | 122.8088 | 59.0378 | -123.0835
895.5156 | 123.143 | -59.0469 | 63.8535 | 0.035095 | 0.0060497 | -0.033885 | 0.067082 | 0.1287 | -0.0036464 | -0.0012923 | 0.11772 | -0.0051868 | -0.004877 | -0.0020316 | 0.00070077 | -0.0043153 | 63.8077 | 63.9313 | -0.027466 | -59.23 | 63.8077 | -59.079 | -59.1248 | -58.9737 | 0.082397 | -59.2667 | 63.8626 | 63.7573 | -59.1339 | -59.2255 | -0.032043 | -0.07782 | -0.045777 | 122.9782 | -0.18311 | -0.10529 | -0.045777 | -0.086975 | -0.17853 | 0.009155 | 0.073242 | -0.21973 | -0.041199 | -0.096131 | 122.8546 | 122.8546 | 59.0195 | -122.9782 | 122.9095 | 122.8043 | 59.1293 | -123.0789
896.5156 | 123.1888 | -59.0378 | 63.8214 | 0.21057 | 0.010109 | 0.067159 | 0.067509 | 0.1287 | 0.0027622 | -0.0017197 | 0.17113 | -0.004546 | -0.0018862 | -0.003527 | 0.006255 | -0.0049561 | 63.8718 | 63.9542 | -0.018311 | -59.2163 | 63.8214 | -59.0836 | -59.1156 | -58.9554 | 0.086975 | -59.2758 | 63.8306 | 63.739 | -59.1293 | -59.2209 | -0.045776 | -0.07782 | 0 | 122.9919 | -0.17853 | -0.10071 | 0.050354 | -0.091552 | -0.1831 | 0.009155 | 0.082398 | -0.23804 | -0.054932 | -0.082397 | 122.8592 | 122.9095 | 59.0195 | -122.937 | 122.8683 | 122.7768 | 59.1248 | -123.0423
897.5156 | 123.1888 | -59.0652 | 63.8214 | 0.22583 | 0.012459 | 0.067372 | 0.066868 | 0.12934 | 0.0025486 | 0.00020288 | 0.20927 | -0.002837 | 0.0004636 | -0.002886 | 0.002837 | -0.0041017 | 63.8397 | 63.9496 | -0.041199 | -59.23 | 63.7985 | -59.0973 | -59.1293 | -58.9691 | 0.054932 | -59.285 | 63.826 | 63.7115 | -59.1431 | -59.2438 | -0.032043 | -0.064086 | -0.022888 | 123.0148 | -0.16479 | -0.10071 | 0.018311 | -0.077819 | -0.17853 | 0.004578 | 0.096131 | -0.21973 | -0.041199 | -0.10986 | 122.8638 | 122.905 | 59.024 | -122.9507 | 122.8912 | 122.7768 | 59.1202 | -123.0652
898.5156 | 123.0469 | -59.0652 | 63.8672 | 0.11902 | 0.013954 | 0.065236 | 0.069218 | 0.13126 | 0.0046848 | -0.00022432 | 0.14824 | -0.0030506 | -0.0012454 | 0.0003182 | 0.0026234 | -0.0023927 | 63.7665 | 63.8168 | -0.10986 | -59.285 | 63.8672 | -59.111 | -59.1476 | -59.2026 | -0.32501 | -59.1522 | 63.8443 | 63.7665 | -59.1385 | -59.2667 | -0.045776 | -0.082397 | 0 | 122.8821 | -0.21973 | -0.13733 | -0.10071 | -0.073242 | -0.20142 | -0.022888 | -0.13733 | -0.086975 | 0.11444 | -0.10071 | 122.9324 | 122.8317 | 58.9554 | -123.0148 | 122.9095 | 122.8317 | 58.7402 | -123.1338
899.5156 | 123.0606 | -59.0836 | 63.8535 | 0.19531 | 0.019508 | 0.06545 | 0.0705 | 0.12892 | 0.003403 | -0.00022432 | 0.1635 | -0.001128 | 0.0011044 | 0.0001046 | 0.0026234 | -0.0053833 | 63.6658 | 63.9221 | -0.068665 | -59.2987 | 63.858 | -59.111 | -59.1476 | -59.0424 | -0.041199 | -59.3719 | 63.8763 | 63.8214 | -59.1431 | -59.285 | -0.027466 | -0.064087 | 0.004577 | 123.0057 | -0.21515 | -0.15106 | -0.18768 | -0.059509 | -0.20142 | 0.022888 | 0.041199 | -0.28839 | -0.086975 | -0.032044 | 122.9416 | 122.7493 | 59.0149 | -123.0011 | 122.9599 | 122.905 | 59.0424 | -123.1384
900.5156 | 123.1888 | -59.0607 | 63.8214 | 0.18768 | 0.012459 | 0.06844 | 0.0658 | 0.12699 | -0.0017238 | -0.0010787 | 0.2932 | -0.0036914 | -0.0008182 | -0.0026724 | 0.002837 | -0.0041017 | 63.7848 | 63.8992 | -0.091553 | -59.2575 | 63.8214 | -59.111 | -59.1568 | -58.9828 | 0.036621 | -59.285 | 63.8306 | 63.7436 | -59.1568 | -59.23 | -0.050354 | -0.09613 | 0 | 122.9599 | -0.19684 | -0.10071 | -0.036621 | -0.09613 | -0.16937 | 0.009155 | 0.07782 | -0.2243 | -0.054931 | -0.07782 | 122.8821 | 122.8455 | 58.9691 | -122.9782 | 122.8912 | 122.8043 | 59.0973 | -123.0515
901.5156 | 123.0469 | -59.1202 | 63.8626 | -3.0777 | 0.010109 | 0.064382 | 0.069859 | 0.12785 | 0.0014804 | -0.00022432 | 0.22453 | -0.002196 | 0.0011044 | -0.0013906 | 0.0032642 | -0.0047425 | 63.7344 | 63.858 | -0.09613 | -59.2896 | 63.8443 | -59.0836 | -59.1385 | -59.0561 | -0.041199 | -59.3536 | 63.8809 | 63.7619 | -59.1385 | -59.2896 | 0.036621 | -0.018311 | -0.018311 | 122.9782 | -0.16937 | -0.15106 | -0.12817 | -0.018311 | -0.16937 | 0.01831 | 0.064087 | -0.23346 | -0.064087 | -0.10071 | 122.9645 | 122.8546 | 59.024 | -123.0011 | 123.0011 | 122.8821 | 59.079 | -123.1522
902.5156 | 123.056 | -59.0881 | 63.858 | 0.019836 | 0.013313 | 0.065236 | 0.06815 | 0.12635 | 0.0031894 | 0.00020288 | 0.087204 | -0.0026234 | -0.000391 | -0.0005362 | 0.0026234 | -0.0043153 | 63.7985 | 63.8672 | -0.054932 | -59.2484 | 63.8535 | -59.079 | -59.1476 | -59.0744 | -0.009155 | -59.3628 | 63.8763 | 63.7894 | -59.1522 | -59.2758 | 0.009156 | -0.059509 | -0.004577 | 122.9553 | -0.16022 | -0.10071 | -0.059509 | -0.064087 | -0.18768 | 0.018311 | 0.013733 | -0.27466 | -0.086975 | -0.068664 | 122.9416 | 122.8867 | 59.0332 | -123.0057 | 122.9645 | 122.8775 | 59.079 | -123.1338
903.5156 | 123.1384 | -59.079 | 63.8214 | 0.18005 | 0.010536 | 0.065877 | 0.066868 | 0.13105 | -1.505e-05 | 0.00084388 | 0.26268 | -0.0019824 | -0.0027408 | -0.000109 | 0.002837 | -0.0041017 | 63.7711 | 63.8672 | -0.10529 | -59.2758 | 63.8351 | -59.111 | -59.1522 | -58.9874 | -0.004578 | -59.317 | 63.8168 | 63.7619 | -59.1705 | -59.2575 | -0.032044 | -0.073243 | 0.013733 | 122.9462 | -0.19684 | -0.1236 | -0.050354 | -0.091553 | -0.17853 | -0.004578 | 0.091552 | -0.23804 | -0.05951 | -0.059509 | 122.9141 | 122.85 | 58.9737 | -122.9736 | 122.8958 | 122.8409 | 59.0744 | -123.0789
904.5156 | 123.111 | -59.079 | 63.858 | 0.16479 | 0.013313 | 0.065877 | 0.070714 | 0.12998 | 0.0010532 | -0.0021469 | 0.26268 | -0.00048697 | -0.0001774 | -0.0013906 | 0.002837 | -0.0038879 | 63.7665 | 63.8397 | -0.11444 | -59.2804 | 63.8397 | -59.0927 | -59.1339 | -59.0424 | -0.036621 | -59.3353 | 63.8397 | 63.7711 | -59.1476 | -59.2758 | -0.013733 | -0.054932 | -0.01831 | 122.9187 | -0.20142 | -0.14649 | -0.091553 | -0.068665 | -0.19684 | -0.01831 | 0.036621 | -0.25635 | -0.059509 | -0.086975 | 122.9187 | 122.8455 | 58.9645 | -122.9919 | 122.9187 | 122.85 | 59.0424 | -123.1338
905.5312 | 123.1384 | -59.024 | 63.8855 | -0.14801 | 0.0090405 | 0.06844 | 0.069432 | 0.12849 | -0.0047146 | -0.0034287 | -0.027237 | -0.0034778 | -0.003168 | -0.003527 | -0.00036743 | -0.0041017 | 63.8397 | 63.9999 | 0.086975 | -59.1797 | 63.8351 | -59.0469 | -59.0836 | -58.9783 | 0.16937 | -59.2575 | 63.8855 | 63.8168 | -59.1019 | -59.2438 | -0.022888 | -0.059509 | -0.050354 | 123.024 | -0.15564 | -0.09613 | -0.045776 | -0.07782 | -0.21973 | 0 | 0.045777 | -0.23346 | -0.013733 | -0.068665 | 122.8592 | 122.8638 | 59.111 | -122.9691 | 122.9095 | 122.8409 | 59.1934 | -123.1293
906.5156 | 123.1018 | -59.0698 | 63.8397 | -0.033569 | 0.013527 | 0.06545 | 0.066227 | 0.1302 | 0.0010532 | 0.00020288 | -0.0043486 | -0.002196 | -0.0006046 | -0.0026724 | 0.0043324 | -0.0047425 | 63.8123 | 63.945 | 0.050354 | -59.23 | 63.8672 | -59.0698 | -59.1339 | -59.0012 | 0.082397 | -59.3033 | 63.8535 | 63.7619 | -59.1248 | -59.2575 | 0 | -0.064087 | 0.027465 | 123.0148 | -0.16022 | -0.096131 | -0.027466 | -0.054932 | -0.18768 | 0.013733 | 0.068664 | -0.23346 | -0.045777 | -0.07782 | 122.937 | 122.8821 | 59.1202 | -122.9736 | 122.9233 | 122.8317 | 59.1522 | -123.0972
907.5156 | 123.0743 | -59.1064 | 63.8718 | 0.14191 | 0.015663 | 0.065236 | 0.067082 | 0.1255 | 0.0010532 | -0.0051377 | 0.018539 | -0.002837 | 3.6404e-05 | -0.0022452 | 0.0024096 | -0.0038879 | 64.0182 | 63.8718 | -0.10986 | -59.2667 | 63.858 | -59.0927 | -59.1248 | -59.0881 | -0.041199 | -59.3674 | 63.8763 | 63.7802 | -59.1476 | -59.2941 | 0.013733 | -0.018311 | -0.013733 | 122.9782 | -0.16022 | -0.14191 | 0.14648 | -0.041199 | -0.18768 | 0.004578 | 0.01831 | -0.26093 | -0.073243 | -0.091553 | 122.9645 | 123.1247 | 58.9966 | -122.9965 | 122.9828 | 122.8867 | 59.0652 | -123.1659
908.5156 | 123.0148 | -59.1156 | 63.8535 | 0.11902 | 0.013527 | 0.067586 | 0.070714 | 0.12721 | 0.0010532 | -0.0015061 | -2.2932 | -0.0019824 | 3.6404e-05 | -0.0022452 | 0.00070077 | -0.0036743 | 63.7253 | 63.8077 | -0.13733 | -59.3033 | 63.8443 | -59.1156 | -59.1751 | -59.0652 | -0.045776 | -59.3399 | 63.913 | 63.8168 | -59.1568 | -59.285 | 0 | -0.059509 | -0.009156 | 122.9233 | -0.18768 | -0.12817 | -0.12817 | -0.041198 | -0.16937 | 0.059509 | 0.050354 | -0.2243 | -0.054932 | -0.036622 | 122.9599 | 122.8409 | 58.9783 | -123.0286 | 123.0286 | 122.9324 | 59.0698 | -123.1384
909.5156 | 123.0515 | -59.0836 | 63.8763 | 0.20294 | 0.012886 | 0.063527 | 0.070286 | 0.12721 | 0.002335 | -0.0015061 | 0.19402 | -0.0013416 | 0.0004636 | 0.0065134 | 0.0064686 | -0.0053833 | 63.7482 | 63.8123 | -0.11444 | -59.2896 | 63.8535 | -59.1156 | -59.166 | -59.0744 | 0.31586 | -59.3491 | 63.8855 | 63.8123 | -59.1431 | -59.2804 | -0.032044 | -0.082398 | -0.022888 | 122.8958 | -0.20599 | -0.1236 | -0.12817 | -0.059509 | -0.19684 | 0.009155 | 0.009155 | -0.2655 | -0.068664 | -0.064087 | 122.937 | 122.8317 | 58.9691 | -123.0423 | 122.9691 | 122.8958 | 59.3994 | -123.1567
910.5312 | 123.0835 | -59.024 | 63.9359 | -0.23193 | 0.0096813 | 0.0678 | 0.067509 | 0.13169 | -0.0047146 | -0.00022432 | -0.027237 | -0.0041186 | -0.0021 | 0.0011728 | 0.00027337 | -0.0049561 | 63.7756 | 63.9496 | 0.018311 | -59.23 | 63.858 | -59.0698 | -59.1248 | -59.0469 | 0.091553 | -59.2987 | 63.9038 | 63.8306 | -59.1385 | -59.2346 | -0.045776 | -0.10071 | -0.07782 | 122.9736 | -0.20599 | -0.10529 | -0.16022 | -0.11444 | -0.21057 | -0.032043 | -0.022888 | -0.27466 | -0.064087 | -0.10529 | 122.8821 | 122.7997 | 59.0424 | -123.0606 | 122.9279 | 122.8546 | 59.1156 | -123.1705
911.5156 | 123.0698 | -59.1019 | 63.858 | 0.14191 | 0.014595 | 0.065022 | 0.065587 | 0.12827 | 0.00083955 | -0.0012923 | 0.20927 | -0.0032642 | 0.0006772 | -0.0024588 | 0.0017688 | -0.0036743 | 63.7299 | 63.826 | -0.1236 | -59.285 | 63.8535 | -59.111 | -59.1751 | -59.0607 | -0.054932 | -59.3719 | 63.8809 | 63.7985 | -59.1751 | -59.2941 | -0.009155 | -0.073242 | -0.004577 | 122.9279 | -0.1831 | -0.10986 | -0.12817 | -0.073242 | -0.19226 | 0.022888 | 0.041199 | -0.27008 | -0.07782 | -0.059509 | 122.9553 | 122.8317 | 58.9783 | -123.0331 | 122.9828 | 122.9004 | 59.0469 | -123.1522
912.5156 | 123.0743 | -59.0515 | 63.8855 | -0.018311 | 0.011604 | 0.065877 | 0.069645 | 0.12956 | 0.0010532 | -0.00043792 | 0.079574 | -0.0026234 | 0.0004636 | -0.0016044 | 0.0032642 | -0.0034607 | 63.8031 | 63.8901 | -0.032043 | -59.2529 | 63.8489 | -59.079 | -59.1431 | -59.0515 | 0.018311 | -59.3262 | 63.8809 | 63.826 | -59.1293 | -59.2575 | -0.027465 | -0.091552 | -0.036621 | 122.9416 | -0.20142 | -0.10986 | -0.082397 | -0.077819 | -0.20599 | -0.004578 | 0 | -0.27466 | -0.068665 | -0.059509 | 122.9004 | 122.8546 | 59.0195 | -123.0286 | 122.9324 | 122.8775 | 59.0698 | -123.143
913.5156 | 123.0377 | -59.0927 | 63.8947 | 0.057983 | 0.016304 | 0.067586 | 0.071141 | 0.12614 | 0.0021214 | -0.0019333 | 0.1635 | -0.0026234 | 0.001318 | -0.001177 | 0.0030506 | -0.0045289 | 63.739 | 63.8443 | -0.082397 | -59.2621 | 63.8351 | -59.0836 | -59.1614 | -59.079 | -0.054932 | -59.3903 | 63.8855 | 63.8077 | -59.1614 | -59.2941 | 0.009155 | -0.068665 | -0.059509 | 122.937 | -0.16937 | -0.10071 | -0.15564 | -0.068665 | -0.20142 | -0.009155 | 0.013733 | -0.29755 | -0.096131 | -0.086975 | 122.9279 | 122.8317 | 59.0103 | -123.056 | 122.9782 | 122.9004 | 59.0378 | -123.1888
914.5156 | 123.0789 | -59.079 | 63.8718 | -0.018311 | 0.014595 | 0.065022 | 0.070714 | 0.12934 | 0.0010532 | -0.0019333 | 0.056686 | -0.00027337 | -0.0033816 | -0.0009634 | 0.002837 | -0.0041017 | 63.7894 | 63.8901 | -0.027466 | -59.2484 | 63.858 | -59.079 | -59.1431 | -59.0424 | 0.027466 | -59.317 | 63.8901 | 63.8031 | -59.1522 | -59.2667 | 0 | -0.064087 | -0.013733 | 122.9691 | -0.16937 | -0.10529 | -0.082397 | -0.073243 | -0.18768 | 0.018311 | 0.036621 | -0.23804 | -0.050354 | -0.068664 | 122.937 | 122.8683 | 59.0515 | -123.0148 | 122.9691 | 122.8821 | 59.1064 | -123.1384
915.5312 | 123.1659 | -59.0561 | 63.8672 | 0.057983 | 0.0077587 | -0.033885 | 0.064305 | 0.12592 | -0.0074918 | -0.0044967 | 0.20927 | -0.0049732 | -0.0025272 | -0.0022452 | 0.0068958 | -0.0015381 | 63.7619 | 63.9496 | 0.009155 | -59.2163 | 63.7939 | -59.0607 | -59.1248 | -59.0103 | 0.091553 | -59.2346 | 63.8489 | 63.7848 | -59.1202 | -59.2346 | -0.004578 | -0.068665 | -0.073242 | 123.0057 | -0.16022 | -0.091553 | -0.10529 | -0.064087 | -0.17853 | -0.01831 | 0.045776 | -0.17853 | 0 | -0.082397 | 122.85 | 122.818 | 59.0652 | -122.9919 | 122.905 | 122.8409 | 59.1476 | -123.1018
916.5156 | 123.056 | -59.0836 | 63.858 | 0.080872 | 0.012886 | 0.066945 | 0.069432 | 0.12827 | 0.0031894 | -0.0015061 | 0.19402 | -0.0015552 | 0.0004636 | -0.0024588 | 0.0019824 | -0.0047425 | 63.7756 | 63.7894 | -0.13733 | -59.2804 | 63.8626 | -59.111 | -59.1431 | -59.0836 | -0.073242 | -59.3765 | 63.8672 | 63.8077 | -59.1751 | -59.2712 | -0.027466 | -0.059509 | 0.004578 | 122.8729 | -0.19684 | -0.13733 | -0.082397 | -0.091553 | -0.18768 | 0.009155 | 0 | -0.29297 | -0.10529 | -0.050354 | 122.9462 | 122.8592 | 58.9462 | -123.0011 | 122.9507 | 122.8912 | 59.0103 | -123.1293
917.5156 | 123.0743 | -59.0836 | 63.8626 | -0.27771 | 0.012245 | 0.065663 | 0.071354 | 0.13126 | 0.0038304 | -0.0012923 | 0.22453 | -0.0017688 | -0.0027408 | -0.0005362 | 0.0024096 | -0.0041017 | 63.7344 | 63.8351 | -0.11444 | -59.2896 | 63.8306 | -59.111 | -59.1431 | -59.0836 | -0.064087 | -59.3536 | 63.8626 | 63.7985 | -59.166 | -59.2758 | -0.027466 | -0.059509 | -0.032044 | 122.9187 | -0.20599 | -0.14649 | -0.12817 | -0.082398 | -0.19226 | 0 | 0 | -0.27008 | -0.07782 | -0.064087 | 122.9141 | 122.818 | 58.9691 | -123.0057 | 122.9462 | 122.8821 | 59.0195 | -123.1384
918.5156 | 123.1064 | -59.1019 | 63.8443 | 0.080872 | 0.015449 | 0.066091 | 0.069432 | 0.12934 | 0.0021214 | -0.00065152 | 0.079574 | -0.0032642 | -0.0006046 | -0.0039542 | 0.002837 | -0.0051697 | 63.7573 | 63.8123 | -0.086975 | -59.2712 | 63.8214 | -59.1202 | -59.1476 | -59.0973 | -0.059509 | -59.3948 | 63.8763 | 63.8077 | -59.1476 | -59.2987 | -0.01831 | -0.045776 | -0.022888 | 122.9141 | -0.16937 | -0.1236 | -0.086975 | -0.045776 | -0.19684 | 0.032044 | 0.004578 | -0.29297 | -0.09613 | -0.036621 | 122.9233 | 122.8592 | 59.0149 | -122.9919 | 122.9782 | 122.9095 | 59.0424 | -123.143
919.5156 | 123.0606 | -59.1064 | 63.8351 | 0.39368 | 0.012245 | 0.065236 | 0.068364 | 0.12827 | 0.001694 | -0.0015061 | 0.23979 | -0.0024096 | -0.0008182 | -0.000109 | 0.0017688 | -0.0028199 | 63.7436 | 63.8214 | -0.1236 | -59.285 | 63.858 | -59.1019 | -59.1568 | -59.0698 | -0.054932 | -59.3674 | 63.8672 | 63.826 | -59.1614 | -59.2896 | 0.004577 | -0.050354 | 0.022888 | 122.9279 | -0.17853 | -0.12817 | -0.091553 | -0.054932 | -0.18311 | 0.032043 | 0.036621 | -0.26093 | -0.07782 | -0.009155 | 122.9645 | 122.85 | 58.9828 | -122.9919 | 122.9736 | 122.9324 | 59.0515 | -123.1247
920.5312 | 123.0652 | -59.0286 | 63.8855 | -0.10223 | 0.012459 | 0.068013 | 0.067296 | 0.12934 | -0.00086945 | -0.0021469 | -0.095902 | -0.0043324 | -0.0001774 | -0.001177 | 0.0024096 | -0.0041017 | 63.7665 | 63.8718 | -0.018311 | -59.2529 | 63.8626 | -59.0836 | -59.1293 | -59.0561 | 0.064087 | -59.317 | 63.9084 | 63.8489 | -59.1522 | -59.23 | -0.054932 | -0.10071 | -0.022888 | 122.9004 | -0.22431 | -0.1236 | -0.11902 | -0.1236 | -0.20142 | 0.022888 | -0.027466 | -0.28839 | -0.086975 | -0.036621 | 122.8912 | 122.7951 | 59.0103 | -123.0148 | 122.937 | 122.8775 | 59.0927 | -123.1155
921.5156 | 123.1842 | -59.0515 | 63.8306 | 0.18005 | 0.012031 | 0.064809 | 0.066227 | 0.12699 | 0.0014804 | -0.0012923 | 0.2932 | -0.0060412 | 0.0006772 | -0.0007498 | 0.0017688 | -0.0049561 | 63.7665 | 63.8809 | -0.07782 | -59.2484 | 63.826 | -59.1019 | -59.1385 | -58.9874 | 0.013733 | -59.2896 | 63.8123 | 63.7573 | -59.166 | -59.2392 | -0.050354 | -0.086975 | -0.004577 | 122.9324 | -0.19684 | -0.10986 | -0.064087 | -0.11444 | -0.18768 | -0.01831 | 0.064087 | -0.23804 | -0.050354 | -0.073242 | 122.8775 | 122.818 | 58.9737 | -122.9691 | 122.8638 | 122.8088 | 59.0652 | -123.0698
922.5156 | 123.0515 | -59.079 | 63.8672 | 0.12665 | 0.015449 | 0.066731 | 0.069859 | 0.12827 | 0.0021214 | 0.00084388 | -1.9651 | -0.0043324 | 0.0011044 | 0.0007456 | 0.00027337 | -0.0058105 | 63.7527 | 63.8031 | -0.11902 | -59.2941 | 63.8489 | -59.0881 | -59.1522 | -59.0515 | -0.09613 | -59.3674 | 63.8947 | 63.826 | -59.166 | -59.2712 | -0.009156 | -0.073243 | -0.01831 | 122.8821 | -0.21515 | -0.14191 | -0.11444 | -0.086976 | -0.19226 | 0.027466 | 0.027465 | -0.28839 | -0.096131 | -0.041198 | 122.9279 | 122.8317 | 58.96 | -123.0194 | 122.9736 | 122.905 | 58.9828 | -123.1384
923.5156 | 123.1979 | -59.0469 | 63.8168 | 1.6602 | 0.0086133 | 0.069509 | 0.068791 | 0.12913 | -0.0038602 | -0.0027877 | 0.2932 | -0.0036914 | -0.0021 | -0.0020316 | 0.001128 | -0.0053833 | 63.826 | 63.9587 | -0.013733 | -59.198 | 63.7894 | -59.0652 | -59.0973 | -58.9783 | 0.091553 | -59.2484 | 63.7985 | 63.7711 | -59.1339 | -59.2438 | -0.018311 | -0.050354 | -0.027465 | 123.0057 | -0.15106 | -0.10071 | 0.009156 | -0.086975 | -0.19684 | -0.01831 | 0.068665 | -0.20142 | -0.004578 | -0.045776 | 122.8363 | 122.8729 | 59.0332 | -122.9141 | 122.8455 | 122.818 | 59.1385 | -123.0606
924.5156 | 123.2025 | -59.0469 | 63.8123 | 0.44708 | 0.0083997 | 0.0678 | 0.065587 | 0.12699 | -0.001083 | -0.00065152 | 0.30846 | -0.003905 | -0.0021 | -0.0016044 | 0.0015552 | -0.0038879 | 63.8535 | 63.9221 | -0.018311 | -59.23 | 63.7756 | -59.0652 | -59.1248 | -58.9874 | 0.045776 | -59.2529 | 63.8123 | 63.7527 | -59.1293 | -59.2529 | -0.018311 | -0.07782 | -0.036621 | 122.9691 | -0.18311 | -0.10529 | 0.041199 | -0.082397 | -0.20599 | 0 | 0.059509 | -0.20599 | 0 | -0.059509 | 122.8226 | 122.9004 | 59.0286 | -122.937 | 122.8592 | 122.7997 | 59.0927 | -123.0652
925.5156 | 123.1842 | -59.0424 | 63.8168 | 0.073242 | 0.010322 | 0.068654 | 0.065159 | 0.12742 | -0.0032192 | -0.0023605 | 0.33134 | -0.0019824 | 0.0008908 | -0.001818 | 0.001128 | -0.0026063 | 63.8351 | 63.9496 | 0.009155 | -59.2163 | 63.7894 | -59.0515 | -59.1293 | -58.9691 | 0.059509 | -59.2484 | 63.8031 | 63.7619 | -59.1385 | -59.23 | -0.009156 | -0.086975 | -0.027465 | 122.9919 | -0.17395 | -0.086976 | 0.018311 | -0.096131 | -0.18768 | -0.013732 | 0.073242 | -0.20599 | -0.01831 | -0.054931 | 122.8317 | 122.8775 | 59.0515 | -122.9462 | 122.8455 | 122.8043 | 59.1019 | -123.0469
926.5156 | 122.8775 | -59.0927 | 63.7756 | 0.11139 | 0.012031 | 0.068868 | 0.069218 | 0.12785 | 0.0021214 | -0.00086512 | 0.11772 | -0.0032642 | -0.0006046 | -0.002886 | 0.0041186 | -0.0047425 | 63.7665 | 63.8123 | -0.10986 | -59.2804 | 63.8626 | -59.0927 | -59.1431 | -59.0836 | -0.059509 | -59.4223 | 63.8809 | 63.8031 | -59.1568 | -59.2621 | 0 | -0.050354 | 0.086975 | 122.905 | -0.18768 | -0.13733 | -0.009156 | -0.064087 | -0.16937 | 0.10529 | 0.009155 | -0.32959 | -0.16022 | 0.027466 | 122.9553 | 122.8592 | 58.9828 | -122.9187 | 122.9736 | 122.8958 | 59.0332 | -123.0377
927.5156 | 123.1476 | -59.0286 | 63.826 | 0.23346 | 0.010536 | 0.066091 | 0.065373 | 0.12806 | -0.00065585 | -0.0015061 | 0.88829 | -0.0051868 | -0.0033816 | 0.0003182 | 0.0047596 | -0.0041017 | 63.8397 | 63.9496 | -0.018311 | -59.2117 | 63.7939 | -59.0652 | -59.1248 | -58.96 | 0.086975 | -59.2575 | 63.8489 | 63.7299 | -59.1202 | -59.2255 | -0.036622 | -0.096131 | -0.032044 | 122.9782 | -0.18311 | -0.086975 | 0.013733 | -0.091553 | -0.19684 | 0.022888 | 0.068664 | -0.22888 | -0.032043 | -0.096131 | 122.8226 | 122.8683 | 59.0103 | -122.9507 | 122.8775 | 122.7585 | 59.1156 | -123.0515
928.5156 | 123.1705 | -59.0515 | 63.8031 | 0.21057 | 0.0090405 | 0.069081 | 0.066441 | 0.12998 | -0.0049282 | -0.00043792 | 0.26268 | -0.0026234 | -0.0021 | -0.0030996 | 0.0019824 | -0.0043153 | 63.826 | 63.9496 | 0.013733 | -59.2392 | 63.7985 | -59.079 | -59.1248 | -58.9691 | 0.054932 | -59.2667 | 63.7894 | 63.7894 | -59.1431 | -59.2712 | -0.027465 | -0.073242 | -0.004578 | 123.0011 | -0.18768 | -0.11444 | 0.022888 | -0.091552 | -0.21973 | -0.013733 | 0.082398 | -0.21515 | 0.004577 | -0.013733 | 122.85 | 122.8775 | 59.0652 | -122.9279 | 122.8409 | 122.8409 | 59.1064 | -123.0743
929.5156 | 123.1705 | -59.0607 | 63.8077 | 0.19531 | 0.01139 | 0.066945 | 0.0658 | 0.12827 | -0.00086945 | -0.0025741 | 0.19402 | -0.0034778 | -0.0018862 | -0.002886 | 0.0024096 | -0.0073059 | 64.0366 | 63.9862 | -0.022888 | -59.1797 | 63.7665 | -59.079 | -59.111 | -58.9554 | 0.068665 | -59.2667 | 63.8489 | 63.7482 | -59.1522 | -59.2255 | -0.01831 | -0.050354 | -0.041199 | 123.0469 | -0.11902 | -0.068664 | 0.22888 | -0.091553 | -0.1648 | 0.041199 | 0.10529 | -0.20599 | -0.041199 | -0.059509 | 122.8271 | 123.0972 | 59.0378 | -122.9187 | 122.9095 | 122.8088 | 59.1293 | -123.0331
930.5156 | 123.0972 | -59.024 | 63.8306 | 0.16479 | 0.0081861 | 0.066731 | 0.066655 | 0.12998 | -0.0025784 | -0.0040695 | 0.2169 | -0.0043324 | -0.0021 | -0.0026724 | -0.00036743 | -0.0043153 | 63.7939 | 63.9084 | -0.022888 | -59.2392 | 63.8123 | -59.0424 | -59.1339 | -58.992 | 0.036621 | -59.2804 | 63.8168 | 63.8031 | -59.1248 | -59.23 | -0.01831 | -0.10986 | -0.01831 | 122.9324 | -0.21515 | -0.10529 | -0.036621 | -0.10071 | -0.20599 | -0.013733 | 0.032044 | -0.25635 | -0.050354 | -0.027465 | 122.8363 | 122.818 | 59.0012 | -122.9645 | 122.8409 | 122.8271 | 59.0607 | -123.0606
931.5156 | 123.1522 | -59.0744 | 63.8535 | 0.14191 | 0.0081861 | 0.069722 | 0.069218 | 0.12849 | -0.0021512 | -0.0042831 | 0.1635 | -0.0064686 | -0.0006046 | -0.0022452 | 0.0017688 | -0.0058105 | 63.8031 | 63.9175 | -0.018311 | -59.2346 | 63.8168 | -59.0561 | -59.1156 | -58.9096 | 0.20599 | -59.3582 | 63.858 | 63.7802 | -59.1202 | -59.2438 | 0.018311 | -0.041199 | -0.036622 | 122.9919 | -0.16022 | -0.11902 | -0.050354 | -0.045776 | -0.16937 | 0.004577 | 0.16479 | -0.28381 | -0.11444 | -0.073243 | 122.8912 | 122.8775 | 59.0561 | -122.9691 | 122.9324 | 122.8546 | 59.2804 | -123.0972
932.5156 | 123.1384 | -59.0332 | 63.8168 | 0.19531 | 0.0098951 | 0.065663 | 0.06815 | 0.12785 | -1.505e-05 | -0.0017197 | 0.25505 | -0.0054004 | -0.0023136 | -0.0026724 | 0.0026234 | -0.0066651 | 63.8168 | 63.9404 | -0.018311 | -59.23 | 63.7985 | -59.0744 | -59.0881 | -58.9737 | 0.022888 | -59.2804 | 63.8351 | 63.7482 | -59.1522 | -59.2209 | -0.041199 | -0.054932 | -0.01831 | 122.9736 | -0.19684 | -0.14191 | 0 | -0.11902 | -0.18768 | 0.018311 | 0.059509 | -0.24719 | -0.05951 | -0.068664 | 122.8317 | 122.85 | 59.0149 | -122.905 | 122.8683 | 122.7814 | 59.0561 | -123.0377
933.5156 | 123.175 | -59.0378 | 63.8443 | 0.20294 | 0.0071179 | 0.067372 | 0.068577 | 0.12785 | 0.00041235 | 0.00020288 | 0.2169 | -0.0019824 | -0.0035952 | 0.000532 | 0.002196 | -0.0043153 | 63.858 | 63.9404 | -0.004578 | -59.2209 | 63.8077 | -59.0744 | -59.1385 | -58.9508 | 0.059509 | -59.2712 | 63.8351 | 63.7482 | -59.1431 | -59.2255 | -0.036621 | -0.10071 | -0.036621 | 122.9782 | -0.1831 | -0.082397 | 0.013733 | -0.10528 | -0.18768 | -0.009155 | 0.086975 | -0.23346 | -0.045776 | -0.09613 | 122.8455 | 122.8958 | 59.0332 | -122.9828 | 122.8729 | 122.7859 | 59.0973 | -123.0698
934.5156 | 123.1613 | -59.0561 | 63.826 | 0.2182 | 0.010322 | 0.066945 | 0.069218 | 0.12592 | 0.0038304 | -0.0025741 | 0.22453 | -0.0019824 | -0.0016726 | 0.0009592 | 0.0049732 | -0.0051697 | 63.8031 | 63.8763 | -0.07782 | -59.2712 | 63.8351 | -59.0927 | -59.1476 | -58.992 | 0.009155 | -59.3216 | 63.8306 | 63.7756 | -59.1522 | -59.2484 | -0.036621 | -0.091553 | 0.009155 | 122.9324 | -0.21515 | -0.1236 | -0.022888 | -0.096131 | -0.19226 | 0.004577 | 0.064087 | -0.2655 | -0.073242 | -0.050354 | 122.8912 | 122.8592 | 58.9783 | -122.9736 | 122.8867 | 122.8317 | 59.0652 | -123.0743
935.5156 | 123.1064 | -58.992 | 63.8855 | -0.1709 | 0.0051953 | 0.070149 | 0.067509 | 0.12785 | -0.00065585 | -0.0025741 | -0.11879 | -0.003905 | -0.0046634 | -0.0013906 | 0.00091437 | -0.0055969 | 63.8763 | 63.9954 | 0.082397 | -59.1843 | 63.858 | -59.0424 | -59.1293 | -58.9828 | 0.16937 | -59.2758 | 63.8901 | 63.826 | -59.111 | -59.2072 | -0.050354 | -0.13733 | -0.027466 | 122.9874 | -0.19226 | -0.054932 | -0.009155 | -0.11902 | -0.21515 | 0.004578 | 0.009155 | -0.28381 | -0.068665 | -0.059509 | 122.85 | 122.8683 | 59.0744 | -123.0148 | 122.8821 | 122.818 | 59.1614 | -123.0927
936.5156 | 123.1338 | -59.0332 | 63.8626 | 0.12665 | 0.0066907 | 0.068013 | 0.066014 | 0.12913 | -0.0034328 | -0.0023605 | 0.22453 | -0.0049732 | -0.0053042 | -0.0003226 | 0.0017688 | -0.0051697 | 63.7985 | 63.9496 | -0.013733 | -59.2575 | 63.7985 | -59.0698 | -59.0973 | -58.9828 | 0.027466 | -59.2941 | 63.8443 | 63.7619 | -59.1019 | -59.2346 | -0.036621 | -0.064087 | -0.064087 | 122.9828 | -0.2243 | -0.16022 | -0.064087 | -0.068665 | -0.20142 | -0.018311 | 0.050354 | -0.26093 | -0.059509 | -0.10071 | 122.8317 | 122.8317 | 59.0195 | -122.9599 | 122.8775 | 122.7951 | 59.0607 | -123.0972
937.5156 | 123.2162 | -59.0332 | 63.858 | 0.16479 | 0.0086133 | 0.069722 | 0.068791 | 0.12934 | 0.00062595 | -0.0019333 | 0.18639 | -0.005614 | -0.003168 | -0.0013906 | 0.0034778 | -0.0049561 | 63.826 | 63.9221 | -0.013733 | -59.2438 | 63.8077 | -59.0744 | -59.1202 | -59.0012 | 0.045776 | -59.2804 | 63.8535 | 63.7848 | -59.1385 | -59.2667 | -0.041199 | -0.086975 | -0.050354 | 122.9553 | -0.21057 | -0.1236 | -0.032043 | -0.10529 | -0.23346 | -0.004577 | 0.032043 | -0.24719 | -0.013733 | -0.073242 | 122.8409 | 122.8592 | 59.0195 | -122.9782 | 122.8867 | 122.818 | 59.079 | -123.1247
938.5156 | 123.1796 | -59.0012 | 63.8489 | -0.1709 | 0.0079723 | 0.069936 | 0.068364 | 0.12763 | -0.0032192 | -0.0034287 | -0.019608 | -0.0060412 | -0.004877 | -0.0056632 | -0.00079463 | -0.0043153 | 63.8855 | 64.0274 | 0.09613 | -59.166 | 63.8489 | -59.0469 | -59.0881 | -59.0744 | -0.018311 | -59.1888 | 63.8351 | 63.7527 | -59.1156 | -59.2438 | -0.045776 | -0.086975 | 0 | 123.0286 | -0.16479 | -0.07782 | 0.036621 | -0.11444 | -0.24261 | -0.013733 | -0.073242 | -0.18768 | 0.054931 | -0.09613 | 122.85 | 122.8867 | 59.0973 | -122.937 | 122.8363 | 122.7539 | 58.9828 | -123.0927
939.5156 | 123.1979 | -58.9966 | 63.826 | -0.033569 | 0.0051953 | 0.069081 | 0.069005 | 0.12699 | 0.00062595 | -0.0040695 | -0.065384 | -0.009032 | -0.0006046 | 0.0007456 | 0.003905 | -0.0070923 | 63.8947 | 64.0549 | 0.11902 | -59.1705 | 63.8306 | -59.0378 | -59.0881 | -58.9417 | 0.18768 | -59.2392 | 63.8443 | 63.7527 | -59.1202 | -59.2209 | -0.041199 | -0.091553 | 0.004577 | 123.0515 | -0.17395 | -0.082397 | 0.068664 | -0.1236 | -0.2243 | 0.01831 | 0.054932 | -0.24262 | -0.018311 | -0.073242 | 122.8271 | 122.8912 | 59.1156 | -122.9141 | 122.8409 | 122.7493 | 59.1843 | -123.0469
940.5156 | 123.1567 | -58.9828 | 63.8809 | -0.13275 | 0.0075451 | 0.067372 | 0.067936 | 0.12913 | -0.001083 | -0.0021469 | -0.10353 | -0.0081776 | -0.0006046 | 0.0007456 | 0.0041186 | -0.0055969 | 63.8763 | 64.0366 | 0.10529 | -59.1797 | 63.8397 | -59.0424 | -59.1156 | -58.9325 | 0.20142 | -59.23 | 63.8809 | 63.7619 | -59.1293 | -59.2163 | -0.059509 | -0.13275 | -0.041198 | 123.0194 | -0.19684 | -0.064086 | -0.004577 | -0.14648 | -0.23346 | 0 | 0.050354 | -0.24719 | -0.013733 | -0.11902 | 122.8226 | 122.8592 | 59.0881 | -122.9965 | 122.8638 | 122.7448 | 59.1843 | -123.0972
941.5156 | 123.1247 | -59.0332 | 63.8077 | 0.073242 | 0.0060497 | 0.068013 | 0.067509 | 0.12849 | -0.0021512 | -0.0021469 | 0.14061 | -0.0043324 | -0.0038088 | -0.0030996 | 0.00070077 | -0.0049561 | 63.8168 | 63.945 | -0.013733 | -59.2438 | 63.8214 | -59.1064 | -59.1019 | -58.8638 | -0.004578 | -59.3353 | 63.858 | 63.7756 | -59.1019 | -59.2529 | -0.073242 | -0.068665 | 0.013733 | 122.9782 | -0.21057 | -0.14191 | 0.009155 | -0.068665 | -0.21973 | 0.050354 | 0.16937 | -0.30212 | -0.082397 | -0.032043 | 122.8546 | 122.85 | 59.0195 | -122.9095 | 122.8912 | 122.8088 | 59.0286 | -123.0606
942.5156 | 123.143 | -59.0515 | 63.8123 | 0.18768 | 0.0069043 | 0.067372 | 0.06815 | 0.12956 | 0.00019875 | -0.0019333 | 0.25505 | -0.003905 | 3.6404e-05 | -0.0022452 | 0.0024096 | -0.0062379 | 63.8397 | 63.9633 | 0 | -59.2209 | 63.7985 | -59.0973 | -59.1293 | -58.9645 | 0.045776 | -59.2896 | 63.826 | 63.7299 | -59.1522 | -59.2392 | -0.045776 | -0.077819 | -0.013733 | 123.0148 | -0.16937 | -0.091553 | 0.027466 | -0.10071 | -0.18768 | 0.013733 | 0.086975 | -0.23804 | -0.050354 | -0.082398 | 122.85 | 122.8912 | 59.0515 | -122.9416 | 122.8775 | 122.7814 | 59.0973 | -123.0515
943.5156 | 123.1659 | -59.0012 | 63.8672 | -0.10986 | 0.0064771 | 0.0678 | 0.067723 | 0.12592 | -0.0023648 | -0.0047103 | -0.23323 | -0.003905 | -0.003168 | -0.0022452 | 0.0015552 | -0.0038879 | 63.9038 | 64.0869 | 0.064087 | -58.8501 | 63.8947 | -59.0012 | -59.0607 | -58.9645 | 0.21973 | -59.1751 | 63.8809 | 63.7527 | -59.1019 | -59.1934 | 0 | -0.059509 | 0.027466 | 123.0881 | 0.15106 | 0.21057 | 0.036622 | -0.10071 | -0.19226 | 0.013733 | 0.036621 | -0.17395 | 0.01831 | -0.11444 | 122.8958 | 122.905 | 59.0652 | -122.9279 | 122.8821 | 122.7539 | 59.2209 | -123.0606
944.5156 | 123.1705 | -59.0286 | 63.8306 | 0.019836 | 0.0064771 | 0.067586 | 0.066014 | 0.12934 | -0.00086945 | -0.0032151 | 0.11772 | -0.0041186 | -0.0040226 | -0.0039542 | 0.00048697 | -0.0066651 | 63.8031 | 63.9633 | -0.004578 | -59.2255 | 63.8306 | -59.079 | -59.111 | -58.9691 | 0.10071 | -59.2346 | 63.8535 | 63.7436 | -59.1202 | -59.23 | -0.050354 | -0.082398 | 0 | 122.9919 | -0.19684 | -0.11444 | -0.027465 | -0.091553 | -0.20142 | 0.022889 | 0.059509 | -0.20599 | -0.004577 | -0.086975 | 122.8592 | 122.8317 | 59.024 | -122.9416 | 122.8821 | 122.7722 | 59.1293 | -123.0606
945.5156 | 123.1018 | -59.0515 | 63.8992 | -1.9943 | 0.0069043 | 0.066731 | 0.066868 | 0.12849 | 0.004044 | -0.00043792 | -0.11116 | -0.0026234 | -0.0018862 | -0.0013906 | 0.0041186 | -0.0055969 | 63.7894 | 63.8947 | -0.013733 | -59.2621 | 63.913 | -59.0836 | -59.1339 | -59.0057 | 0.064087 | -59.3262 | 63.9175 | 63.8031 | -59.111 | -59.2255 | -0.032043 | -0.082397 | 0.013733 | 122.9462 | -0.21057 | -0.12817 | -0.10986 | -0.059509 | -0.17395 | 0.018311 | 0.045777 | -0.27466 | -0.10071 | -0.09613 | 122.9645 | 122.8409 | 59.0378 | -123.0331 | 122.9691 | 122.8546 | 59.1156 | -123.1247
946.5156 | 123.2117 | -59.024 | 63.8672 | -0.11749 | 0.0034863 | 0.065236 | 0.068791 | 0.12827 | -0.00022865 | -0.0027877 | 0.9951 | -0.0034778 | -0.0021 | -0.000109 | 0.001128 | -0.0049561 | 63.9084 | 64.2059 | 0.31586 | -58.9508 | 63.9084 | -59.0057 | -59.0836 | -58.9233 | 0.21973 | -59.2026 | 63.826 | 63.7756 | -59.1064 | -59.1751 | 0.018311 | -0.059509 | 0.041199 | 123.23 | 0.073242 | 0.13275 | 0.041199 | -0.082397 | -0.15106 | -0.041198 | 0.10071 | -0.17853 | -0.027466 | -0.091552 | 122.9324 | 122.9324 | 59.3399 | -122.9507 | 122.85 | 122.7997 | 59.2438 | -123.0423
947.5156 | 123.1842 | -59.0286 | 63.8397 | 0.0045777 | 0.0049817 | 0.069081 | 0.067082 | 0.12827 | -0.0017238 | -0.0010787 | 0.064316 | -0.0049732 | -0.0021 | -0.003527 | 0.00091437 | -0.0047425 | 63.8489 | 64.0274 | 0.068665 | -59.1934 | 63.8214 | -59.0561 | -59.1019 | -58.9233 | 0.16022 | -59.2026 | 63.858 | 63.7573 | -59.1202 | -59.1888 | -0.027466 | -0.073243 | -0.018311 | 123.056 | -0.1648 | -0.091552 | 0.009155 | -0.091553 | -0.16022 | 0.01831 | 0.10528 | -0.17395 | -0.013733 | -0.082398 | 122.85 | 122.8775 | 59.0973 | -122.9416 | 122.8867 | 122.7859 | 59.1888 | -123.0286
948.5156 | 123.1934 | -59.0286 | 63.8397 | -0.02594 | 0.0043409 | 0.067586 | 0.067509 | 0.1287 | 0.00019875 | -0.0019333 | 0.026169 | -0.005614 | -0.0033816 | -0.0007498 | 0.00070077 | -0.0043153 | 63.8535 | 64.0182 | 0.064087 | -59.1888 | 63.826 | -59.0286 | -59.111 | -58.9417 | 0.16022 | -59.2209 | 63.858 | 63.7527 | -59.1202 | -59.2072 | 0 | -0.082398 | -0.013733 | 123.0469 | -0.16022 | -0.07782 | 0.013733 | -0.091553 | -0.17853 | 0.01831 | 0.086975 | -0.19226 | -0.013733 | -0.086975 | 122.8546 | 122.8821 | 59.0927 | -122.9507 | 122.8867 | 122.7814 | 59.1888 | -123.0469
949.5156 | 123.1979 | -59.0195 | 63.8306 | -0.02594 | 0.0054089 | 0.067586 | 0.070714 | 0.12657 | -0.0023648 | -0.0027877 | 0.056686 | -0.0060412 | -0.0038088 | -0.0041678 | 0.0024096 | -0.0055969 | 63.8351 | 64.0091 | 0.073242 | -59.198 | 63.8397 | -59.0469 | -59.1293 | -58.9279 | 0.15564 | -59.2255 | 63.8489 | 63.7482 | -59.1156 | -59.2117 | -0.027466 | -0.10986 | 0.009156 | 123.0286 | -0.17853 | -0.068665 | 0.004578 | -0.096131 | -0.19226 | 0.018311 | 0.091553 | -0.20599 | -0.013733 | -0.082397 | 122.8592 | 122.8546 | 59.0927 | -122.9599 | 122.8683 | 122.7676 | 59.1751 | -123.0423
950.5156 | 123.0789 | -59.0378 | 63.9221 | -0.19379 | 0.0077587 | 0.068013 | 0.067296 | 0.12785 | 0.0014804 | -0.0021469 | -0.18745 | -0.0054004 | -0.0012454 | -0.0016044 | 0.0032642 | -0.0058105 | 63.8535 | 63.9999 | 0.068665 | -59.2026 | 63.8718 | -59.0698 | -59.1202 | -59.0057 | 0.11444 | -59.2896 | 63.9267 | 63.8031 | -59.1156 | -59.2346 | -0.032043 | -0.082397 | -0.050354 | 123.0377 | -0.16479 | -0.082398 | -0.068664 | -0.07782 | -0.19684 | 0.004578 | 0.032044 | -0.25177 | -0.054932 | -0.11902 | 122.9095 | 122.8912 | 59.1064 | -123.0423 | 122.9645 | 122.8409 | 59.1522 | -123.1567
951.5156 | 123.1888 | -58.9966 | 63.8397 | -0.086975 | 0.0066907 | 0.069081 | 0.068577 | 0.12849 | -0.0021512 | -0.0025741 | -0.019608 | -0.0068958 | -0.0038088 | -0.0033134 | 0.0013416 | -0.0083741 | 63.8718 | 64.064 | 0.10529 | -59.166 | 63.8168 | -59.0515 | -59.1019 | -58.8409 | 0.5722 | -59.4131 | 63.8992 | 63.7482 | -59.1293 | -59.2346 | -0.054932 | -0.10529 | -0.022889 | 123.0606 | -0.16937 | -0.064087 | 0.032043 | -0.13275 | -0.23804 | 0.059509 | 0.15564 | -0.41657 | -0.17853 | -0.091553 | 122.8134 | 122.8683 | 59.1019 | -122.9416 | 122.8958 | 122.7448 | 59.5688 | -123.0743
952.5156 | 123.143 | -58.992 | 63.8489 | -0.010681 | 0.0071179 | 0.067159 | 0.066868 | 0.12721 | -0.0019376 | -0.0017197 | -0.0043486 | -0.003905 | -0.0016726 | -0.0020316 | 0.002196 | -0.0055969 | 63.8718 | 64.0549 | 0.09613 | -59.166 | 63.8123 | -59.0607 | -59.1019 | -58.8913 | 0.21515 | -59.1751 | 63.8397 | 63.739 | -59.1156 | -59.1934 | -0.068665 | -0.10986 | -0.036621 | 123.0469 | -0.17395 | -0.064087 | 0.022888 | -0.1236 | -0.20142 | -0.009155 | 0.10071 | -0.18311 | 0.01831 | -0.10986 | 122.8043 | 122.8638 | 59.0881 | -122.9507 | 122.8317 | 122.731 | 59.2072 | -123.0423
953.5312 | 123.1018 | -59.0469 | 63.8351 | 0.019836 | 0.013099 | 0.065663 | 0.068791 | 0.12806 | 0.005112 | 0.0012711 | -0.019608 | -0.001128 | -0.001459 | 0.000532 | 0.003905 | -0.0081605 | 63.8535 | 63.9542 | -0.009155 | -59.23 | 63.8397 | -59.1019 | -59.1156 | -58.992 | 0.045776 | -59.3216 | 63.8855 | 63.7436 | -59.1568 | -59.2392 | -0.054932 | -0.068665 | 0.004578 | 123.0011 | -0.18311 | -0.11444 | 0.018311 | -0.10986 | -0.19226 | 0.050354 | 0.054932 | -0.27466 | -0.082397 | -0.091553 | 122.8867 | 122.9004 | 59.0378 | -122.9507 | 122.9324 | 122.7905 | 59.0927 | -123.0743
954.5156 | 123.2025 | -58.9783 | 63.8397 | -0.010681 | 0.0079723 | 0.066731 | 0.06815 | 0.12806 | -0.001083 | -0.0032151 | 0.079574 | -0.0060412 | -0.0038088 | -0.0009634 | -0.00036743 | -0.0030335 | 63.8351 | 64.032 | 0.082397 | -59.1888 | 63.8443 | -59.0469 | -59.0973 | -58.8959 | 0.18768 | -59.1705 | 63.8351 | 63.7482 | -59.1156 | -59.1843 | -0.068665 | -0.11902 | 0.004577 | 123.0103 | -0.21057 | -0.091553 | -0.004578 | -0.13733 | -0.20599 | -0.004578 | 0.082397 | -0.19226 | 0.013733 | -0.091553 | 122.8226 | 122.8134 | 59.0607 | -122.937 | 122.8134 | 122.7264 | 59.166 | -123.024
955.5156 | 123.0698 | -59.0286 | 63.8992 | -0.1709 | 0.0066907 | 0.068868 | 0.067082 | 0.12956 | 0.0012668 | -0.0034287 | -0.19508 | -0.002837 | -0.0018862 | -0.001818 | 0.0034778 | -0.0062379 | 63.826 | 63.8718 | -0.027466 | -59.2255 | 63.8809 | -59.1019 | -59.1751 | -59.0286 | 0.091553 | -59.3216 | 63.913 | 63.8123 | -59.1476 | -59.2575 | -0.073243 | -0.14648 | -0.018311 | 122.9004 | -0.19684 | -0.050354 | -0.073242 | -0.11902 | -0.22888 | 0.013733 | 0 | -0.29297 | -0.064087 | -0.086975 | 122.9095 | 122.8546 | 59.0012 | -123.0743 | 122.9416 | 122.8409 | 59.1202 | -123.1567
956.5156 | 123.1705 | -59.0103 | 63.8397 | -0.02594 | 0.0069043 | 0.066945 | 0.067936 | 0.12806 | -0.0038602 | -0.00065152 | 0.087204 | -0.0051868 | -0.0061588 | -0.000109 | 0.00070077 | -0.0041017 | 63.8168 | 63.9999 | 0.054932 | -59.2117 | 63.8168 | -59.0561 | -59.0927 | -58.9233 | 0.16479 | -59.1843 | 63.8306 | 63.7619 | -59.1202 | -59.2163 | -0.045776 | -0.082397 | -0.022889 | 123.0103 | -0.20142 | -0.11902 | -0.022889 | -0.10986 | -0.20599 | -0.009156 | 0.086975 | -0.17395 | 0.032044 | -0.07782 | 122.8271 | 122.8271 | 59.0652 | -122.9324 | 122.8409 | 122.7722 | 59.1751 | -123.056
957.5156 | 123.1613 | -59.0195 | 63.8535 | -0.018311 | 0.0079723 | 0.068013 | 0.069005 | 0.12742 | -0.002792 | -0.0021469 | 0.049057 | -0.0049732 | -0.0029544 | -0.001818 | 0.0019824 | -0.0032471 | 63.8123 | 64.0137 | 0.045776 | -59.2026 | 63.8351 | -59.0836 | -59.0881 | -58.9417 | 0.16937 | -59.2163 | 63.8626 | 63.7299 | -59.1156 | -59.2209 | -0.064087 | -0.068665 | -0.018311 | 123.0331 | -0.18311 | -0.11444 | -0.041199 | -0.096131 | -0.20142 | 0.009155 | 0.07782 | -0.19684 | 0.004577 | -0.1236 | 122.8546 | 122.8317 | 59.0652 | -122.9416 | 122.8821 | 122.7493 | 59.1888 | -123.0743
958.5156 | 123.175 | -59.0057 | 63.8626 | 0.77515 | 0.0073315 | 0.067586 | 0.069645 | 0.13041 | -0.0019376 | -0.0027877 | 0.0032804 | -0.0049732 | -0.0040226 | -0.0022452 | 0.002837 | -0.0068787 | 63.8901 | 64.0457 | 0.10986 | -59.1843 | 63.8351 | -59.0698 | -59.111 | -58.9371 | 0.20142 | -59.2072 | 63.8626 | 63.7344 | -59.1064 | -59.2072 | -0.064087 | -0.10529 | -0.027466 | 123.0515 | -0.17853 | -0.073242 | 0.027466 | -0.10071 | -0.20142 | 0 | 0.068664 | -0.20142 | 0 | -0.12817 | 122.8409 | 122.8958 | 59.1156 | -122.9736 | 122.8683 | 122.7402 | 59.2072 | -123.0698
959.5156 | 123.1659 | -59.0012 | 63.8351 | -0.10986 | 0.0045545 | 0.069722 | 0.07584 | 0.13084 | 0.004044 | -0.0023605 | -0.24086 | -0.0036914 | -0.001459 | -0.0026724 | 0.0024096 | -0.0060243 | 63.6749 | 64.1006 | 0.09613 | -59.2346 | 63.8214 | -59.0881 | -59.0698 | -58.9371 | 0.2243 | -59.198 | 63.8397 | 63.7482 | -59.1156 | -59.1934 | -0.086975 | -0.068664 | -0.013733 | 123.1018 | -0.23346 | -0.1648 | -0.16022 | -0.11444 | -0.19226 | 0.004578 | 0.064087 | -0.19684 | -0.004578 | -0.086975 | 122.8226 | 122.6761 | 59.0973 | -122.905 | 122.8409 | 122.7493 | 59.2255 | -123.0286
960.5156 | 123.0331 | -59.0469 | 63.8855 | -0.20142 | 0.0086133 | 0.0678 | 0.067723 | 0.12806 | 0.0019078 | -0.0034287 | -0.16457 | -0.0043324 | -0.0023136 | 0.0001046 | 0.0034778 | -0.0053833 | 63.8168 | 63.9679 | 0.050354 | -59.2117 | 63.8763 | -59.0378 | -59.1248 | -59.0103 | 0.10529 | -59.3124 | 63.8992 | 63.7894 | -59.1431 | -59.2117 | 0.009155 | -0.07782 | -0.009155 | 123.0148 | -0.16479 | -0.086975 | -0.068665 | -0.09613 | -0.16479 | 0.013733 | 0.036621 | -0.2655 | -0.10071 | -0.09613 | 122.9233 | 122.8638 | 59.0973 | -123.0103 | 122.9462 | 122.8363 | 59.1522 | -123.0972
961.5156 | 123.175 | -59.0149 | 63.8947 | -0.1709 | 0.0073315 | 0.069936 | 0.066227 | 0.12721 | -0.0012966 | -0.0010787 | -0.073013 | -0.003905 | -0.0055178 | -0.0003226 | 0.0030506 | -0.0049561 | 63.8626 | 64.064 | 0.11444 | -59.1751 | 63.8351 | -59.0607 | -59.1202 | -58.9325 | 0.20599 | -59.2255 | 63.8718 | 63.7344 | -59.0973 | -59.23 | -0.045776 | -0.10529 | -0.059509 | 123.0789 | -0.16022 | -0.054932 | -0.032043 | -0.082397 | -0.21515 | -0.022888 | 0.082398 | -0.21057 | 0.004578 | -0.16022 | 122.85 | 122.8775 | 59.1293 | -123.0148 | 122.8867 | 122.7493 | 59.2209 | -123.1247
962.5156 | 123.175 | -59.0103 | 63.8763 | -0.033569 | 0.0060497 | 0.068868 | 0.068364 | 0.12678 | -0.00065585 | -0.0012923 | 0.056686 | -0.0036914 | -0.0023136 | -0.001818 | 0.00091437 | -0.0055969 | 63.8214 | 63.9954 | 0.032043 | -59.2026 | 63.8351 | -59.0561 | -59.1019 | -58.96 | 0.13733 | -59.2255 | 63.8397 | 63.7436 | -59.1293 | -59.2117 | -0.045776 | -0.091553 | -0.041199 | 123.0057 | -0.19226 | -0.10071 | -0.054932 | -0.11902 | -0.20142 | -0.036621 | 0.050354 | -0.21515 | -0.013733 | -0.13275 | 122.8455 | 122.8317 | 59.0424 | -122.9782 | 122.85 | 122.7539 | 59.1476 | -123.0881
963.5156 | 123.2162 | -59.0057 | 63.8306 | -0.041199 | 0.0062635 | 0.067159 | 0.065587 | 0.12678 | -0.0023648 | -0.0032151 | 0.041427 | -0.003905 | -0.0044498 | -0.0007498 | 0.0026234 | -0.0045289 | 63.8718 | 64.0411 | 0.07782 | -59.1888 | 63.826 | -59.0607 | -59.1202 | -58.905 | 0.21057 | -59.198 | 63.8626 | 63.739 | -59.1019 | -59.2163 | -0.054932 | -0.11444 | -0.004577 | 123.0469 | -0.18311 | -0.068665 | 0.041199 | -0.096131 | -0.21057 | 0.032044 | 0.10071 | -0.19226 | 0.018311 | -0.091552 | 122.8317 | 122.8775 | 59.0836 | -122.9507 | 122.8683 | 122.7448 | 59.2163 | -123.0469
964.5156 | 123.1567 | -59.0378 | 63.8535 | 0.10376 | 0.0079723 | 0.068868 | 0.067082 | 0.12742 | -0.0025784 | -0.0021469 | 0.079574 | -0.0079638 | -0.0044498 | -0.0037406 | 0.0013416 | -0.0045289 | 63.7939 | 63.9633 | 0.013733 | -59.2209 | 63.8214 | -59.0836 | -59.111 | -58.96 | 0.11444 | -59.23 | 63.8443 | 63.7482 | -59.1202 | -59.2255 | -0.045776 | -0.073242 | -0.032044 | 123.0011 | -0.1831 | -0.10986 | -0.05951 | -0.082397 | -0.18768 | -0.009156 | 0.07782 | -0.19226 | -0.004578 | -0.10529 | 122.8592 | 122.8317 | 59.0515 | -122.9645 | 122.8821 | 122.7859 | 59.1522 | -123.0789
965.5156 | 123.1522 | -58.9828 | 63.8672 | -0.13275 | 0.0062635 | 0.068654 | 0.069859 | 0.12806 | -0.00065585 | -0.0030013 | -0.10353 | -0.0024096 | -0.003168 | -0.0007498 | 0.002196 | -0.0066651 | 63.858 | 64.032 | 0.10986 | -59.166 | 63.8443 | -59.0607 | -59.0927 | -58.9417 | 0.19684 | -59.2209 | 63.8947 | 63.7619 | -59.1064 | -59.1888 | -0.07782 | -0.10986 | -0.022888 | 123.0148 | -0.18311 | -0.073243 | -0.009155 | -0.1236 | -0.20599 | 0.027466 | 0.041199 | -0.23804 | -0.032043 | -0.10529 | 122.8271 | 122.8409 | 59.0927 | -122.9599 | 122.8775 | 122.7448 | 59.1797 | -123.056
966.5156 | 123.1338 | -59.0149 | 63.8397 | 0.29449 | 0.0069043 | 0.068227 | 0.065373 | 0.12699 | -0.0012966 | -0.0040695 | 0.10246 | -0.0047596 | -0.0018862 | -0.0022452 | 0.0019824 | -0.0049561 | 63.7756 | 63.9496 | -0.009155 | -59.23 | 63.8123 | -59.0652 | -59.1385 | -58.9737 | 0.086975 | -59.2758 | 63.8489 | 63.7436 | -59.111 | -59.2255 | -0.050354 | -0.1236 | -0.027466 | 122.9645 | -0.21515 | -0.091553 | -0.064087 | -0.09613 | -0.21057 | 0.009155 | 0.041199 | -0.26093 | -0.050354 | -0.096131 | 122.8271 | 122.7905 | 59.0057 | -122.9782 | 122.8638 | 122.7585 | 59.1019 | -123.0652
967.5156 | 123.1796 | -59.0103 | 63.858 | 0.035095 | 0.0062635 | 0.069722 | 0.066868 | 0.12721 | -0.0021512 | -0.0019333 | 0.071945 | -0.0058276 | -0.0023136 | -0.0009634 | 0.0015552 | -0.0058105 | 63.8214 | 64.0091 | 0.027466 | -59.2163 | 63.858 | -59.0607 | -59.1248 | -58.9462 | 0.15564 | -59.2163 | 63.8718 | 63.7436 | -59.1156 | -59.2072 | -0.050354 | -0.11444 | 0 | 123.0194 | -0.20599 | -0.091553 | -0.036621 | -0.10529 | -0.19684 | 0.013733 | 0.064087 | -0.20599 | -0.009156 | -0.11444 | 122.8683 | 122.8317 | 59.0378 | -122.9828 | 122.8821 | 122.7539 | 59.166 | -123.0652
968.5156 | 123.111 | -59.0286 | 63.8535 | 0.057983 | 0.0066907 | 0.068013 | 0.067296 | 0.12742 | -0.0017238 | -0.0034287 | 0.72807 | -0.0043324 | -0.0010318 | -0.0030996 | 0.0015552 | -0.0053833 | 63.8077 | 63.9496 | -0.013733 | -59.1339 | 63.8443 | -59.0561 | -59.0927 | -58.992 | 0.041199 | -59.285 | 63.8351 | 63.7253 | -59.1248 | -59.2346 | -0.027466 | -0.064087 | -0.009156 | 122.9782 | -0.10529 | -0.041199 | -0.045777 | -0.096131 | -0.20599 | -0.018311 | 0.036621 | -0.25635 | -0.050354 | -0.12817 | 122.8729 | 122.8363 | 59.0149 | -122.9462 | 122.8638 | 122.7539 | 59.0698 | -123.0881
969.5156 | 123.1247 | -59.0149 | 63.8077 | 0.09613 | 0.0062635 | 0.069295 | 0.068364 | 0.12785 | -0.0019376 | -0.0044967 | 0.087204 | -0.0034778 | -0.0018862 | -0.0026724 | -0.00015383 | -0.0047425 | 63.8077 | 63.9542 | 0.009155 | -59.2255 | 63.8168 | -59.0561 | -59.1248 | -58.9554 | 0.10071 | -59.2438 | 63.858 | 63.7253 | -59.0973 | -59.2117 | -0.041198 | -0.10986 | 0.009155 | 122.9691 | -0.21057 | -0.10071 | 0 | -0.082397 | -0.19684 | 0.050354 | 0.05951 | -0.22888 | -0.032043 | -0.082397 | 122.8317 | 122.8226 | 59.024 | -122.9324 | 122.8729 | 122.7402 | 59.1156 | -123.0194
970.5156 | 123.1613 | -59.0149 | 63.8763 | -0.27771 | 0.0058361 | 0.067159 | 0.069432 | 0.12956 | 0.0029758 | -0.0021469 | -0.10353 | -0.0060412 | -0.0018862 | -0.0013906 | 0.0043324 | -0.0053833 | 63.8901 | 64.0503 | 0.10986 | -59.1705 | 63.8168 | -59.0424 | -59.1019 | -58.9325 | 0.20142 | -59.2117 | 63.8489 | 63.7482 | -59.0927 | -59.1934 | -0.027465 | -0.086975 | -0.05951 | 123.0652 | -0.15564 | -0.068664 | 0.013733 | -0.077819 | -0.17853 | -0.027466 | 0.082398 | -0.19684 | -0.018311 | -0.12817 | 122.8317 | 122.905 | 59.1248 | -122.9782 | 122.8638 | 122.7631 | 59.2163 | -123.0698
971.5156 | 123.1705 | -59.0286 | 63.8397 | 0.012207 | 0.0045545 | 0.069509 | 0.066014 | 0.12592 | -0.002792 | -0.0015061 | 0.094833 | -0.004546 | -0.0046634 | -0.0016044 | 0.0015552 | -0.0062379 | 63.8123 | 63.9862 | 0.036621 | -59.2163 | 63.8351 | -59.0652 | -59.1385 | -58.9554 | 0.1236 | -59.2346 | 63.8718 | 63.7299 | -59.1339 | -59.23 | -0.036622 | -0.10986 | -0.004578 | 123.0148 | -0.18768 | -0.07782 | -0.027466 | -0.10529 | -0.20142 | 0.032043 | 0.073242 | -0.20599 | -0.004577 | -0.10986 | 122.8638 | 122.8409 | 59.0652 | -122.9782 | 122.9004 | 122.7585 | 59.1522 | -123.0698
972.5156 | 123.1567 | -59.0332 | 63.8168 | 0.18768 | 0.010536 | 0.069081 | 0.06815 | 0.12998 | -0.001083 | -0.0019333 | 0.27794 | -0.0024096 | -0.0012454 | -0.0037406 | 0.0043324 | -0.0060243 | 63.8168 | 63.9725 | 0.013733 | -59.2346 | 63.8077 | -59.0836 | -59.1339 | -58.9828 | 0.054932 | -59.2804 | 63.8214 | 63.7207 | -59.111 | -59.2438 | -0.050354 | -0.10071 | -0.009155 | 123.0057 | -0.20142 | -0.10071 | 0 | -0.07782 | -0.21057 | 0.004578 | 0.050354 | -0.24719 | -0.036622 | -0.09613 | 122.8409 | 122.85 | 59.0469 | -122.9507 | 122.8546 | 122.7539 | 59.0881 | -123.0606
973.5156 | 123.1613 | -59.0424 | 63.8077 | -0.20905 | 0.0015637 | 0.06844 | 0.068577 | 0.1255 | -0.0015102 | -0.0015061 | -0.065384 | -0.0058276 | -0.0059452 | -0.0005362 | 0.00048697 | -0.0051697 | 63.8763 | 64.064 | 0.09613 | -59.1522 | 63.8489 | -59.0469 | -59.0836 | -58.9462 | 0.60883 | -59.0469 | 63.9313 | 63.8031 | -59.1019 | -59.198 | -0.004578 | -0.041199 | 0.041199 | 123.1064 | -0.10986 | -0.068665 | 0.068665 | -0.05951 | -0.15564 | 0.1236 | 0.09613 | -0.004578 | 0.15106 | -0.004577 | 122.8912 | 122.9187 | 59.1385 | -122.8912 | 122.9736 | 122.8455 | 59.6512 | -123.0057
974.5156 | 123.2025 | -59.0332 | 63.8168 | 0.2182 | 0.012459 | 0.066518 | 0.066441 | 0.12956 | 0.003403 | -0.00022432 | -0.69099 | -0.0032642 | -0.0044498 | -0.0016044 | 0.0030506 | -0.0079469 | 63.8489 | 63.9679 | -0.004578 | -59.2209 | 63.7985 | -59.079 | -59.1202 | -58.9233 | 0.068665 | -59.2346 | 63.8672 | 63.7253 | -59.1202 | -59.2255 | -0.045776 | -0.086975 | -0.01831 | 123.0011 | -0.18768 | -0.10071 | 0.032044 | -0.086975 | -0.19226 | 0.050354 | 0.10986 | -0.20142 | -0.009155 | -0.091552 | 122.8317 | 122.8821 | 59.0286 | -122.937 | 122.9004 | 122.7585 | 59.1019 | -123.0423
975.5156 | 123.1888 | -59.0149 | 63.858 | 0.019836 | 0.0088269 | 0.069295 | 0.067509 | 0.12849 | -0.0034328 | -0.0021469 | 0.14061 | -0.004546 | -0.0042362 | -0.001818 | 0.00070077 | -0.0051697 | 63.826 | 63.9496 | 0.018311 | -59.2117 | 63.858 | -59.079 | -59.0973 | -58.9462 | 0.10986 | -59.2438 | 63.8855 | 63.7482 | -59.1248 | -59.2209 | -0.064086 | -0.082397 | 0 | 122.9645 | -0.19684 | -0.11444 | -0.032043 | -0.10986 | -0.20599 | 0.027466 | 0.068665 | -0.22888 | -0.022888 | -0.10986 | 122.8729 | 122.8409 | 59.0332 | -122.9553 | 122.9004 | 122.7631 | 59.1248 | -123.0789
976.5156 | 123.1247 | -59.0195 | 63.8123 | 0.019836 | 0.0062635 | 0.068654 | 0.066014 | 0.12934 | -0.001083 | -0.0017197 | 0.11009 | -0.0032642 | -0.001459 | -0.0039542 | 0.00070077 | -0.0060243 | 63.7939 | 63.945 | 0.004578 | -59.2117 | 63.8351 | -59.0836 | -59.1156 | -58.9783 | 0.10071 | -59.2575 | 63.8626 | 63.7527 | -59.1202 | -59.2255 | -0.064087 | -0.096131 | 0.022888 | 122.9645 | -0.19226 | -0.09613 | -0.018311 | -0.10071 | -0.20599 | 0.050354 | 0.041199 | -0.23804 | -0.032043 | -0.059509 | 122.8546 | 122.8134 | 59.024 | -122.9279 | 122.8821 | 122.7722 | 59.1202 | -123.0377
977.5156 | 123.1567 | -59.0424 | 63.8535 | 0.09613 | 0.0051953 | 0.068868 | 0.067936 | 0.12849 | -0.00022865 | -0.0032151 | 0.17876 | -0.003905 | -0.0023136 | -0.0020316 | 0.0026234 | -0.0066651 | 63.8031 | 63.9542 | -0.004578 | -59.2392 | 63.8077 | -59.0652 | -59.1202 | -58.9966 | 0.064087 | -59.2804 | 63.8443 | 63.7573 | -59.1614 | -59.2209 | -0.022889 | -0.07782 | -0.045777 | 122.9965 | -0.19684 | -0.11902 | -0.050354 | -0.11902 | -0.17853 | -0.009156 | 0.045776 | -0.23804 | -0.05951 | -0.096131 | 122.85 | 122.8455 | 59.0378 | -122.9736 | 122.8867 | 122.7997 | 59.1064 | -123.0743
978.5156 | 123.1796 | -59.0378 | 63.8077 | 0.16479 | 0.013527 | 0.068868 | 0.067936 | 0.13041 | 0.0021214 | -0.00086512 | 0.23216 | -0.001128 | -0.0023136 | -0.0043814 | 0.0019824 | -0.0060243 | 63.8672 | 63.9679 | 0.009155 | -59.2072 | 63.7756 | -59.0744 | -59.1293 | -58.9142 | 0.054932 | -59.2438 | 63.8397 | 63.707 | -59.1385 | -59.2163 | -0.036621 | -0.091552 | -0.032043 | 123.0057 | -0.16937 | -0.07782 | 0.059509 | -0.10071 | -0.17853 | 0.032044 | 0.1236 | -0.20599 | -0.027465 | -0.10071 | 122.8134 | 122.905 | 59.0469 | -122.937 | 122.8775 | 122.7448 | 59.0927 | -123.024
979.5156 | 123.1155 | -59.0469 | 63.8351 | 0.057983 | 0.0062635 | 0.067586 | 0.067082 | 0.12892 | -0.0017238 | -0.0015061 | 0.18639 | -0.0047596 | -0.0029544 | -0.0039542 | 0.0013416 | -0.0032471 | 63.8168 | 63.9404 | 0 | -59.23 | 63.8306 | -59.0515 | -59.111 | -59.0652 | 0.07782 | -59.3124 | 63.858 | 63.7619 | -59.1339 | -59.2072 | -0.004578 | -0.064087 | -0.004578 | 122.9874 | -0.18311 | -0.11902 | -0.018311 | -0.086975 | -0.16022 | 0.022888 | -0.018311 | -0.2655 | -0.10529 | -0.073242 | 122.8775 | 122.8638 | 59.0469 | -122.9462 | 122.905 | 122.8088 | 59.1248 | -123.0423
980.5156 | 123.23 | -59.0286 | 63.826 | 0.10376 | 0.0075451 | 0.067159 | 0.068364 | 0.12934 | 0.0012668 | -0.0021469 | 0.14061 | -0.0041186 | -0.0038088 | -0.003527 | 0.00027337 | -0.0038879 | 63.8168 | 63.9221 | 0.009155 | -59.2438 | 63.826 | -59.0973 | -59.1202 | -58.9737 | 0.054932 | -59.285 | 63.8626 | 63.7344 | -59.1248 | -59.2117 | -0.068665 | -0.091553 | 0 | 122.9507 | -0.21515 | -0.1236 | -0.009156 | -0.096131 | -0.18311 | 0.036621 | 0.054931 | -0.25635 | -0.073242 | -0.091553 | 122.8546 | 122.8455 | 59.0378 | -122.9462 | 122.8912 | 122.7631 | 59.0836 | -123.0377
981.5156 | 123.1201 | -59.0424 | 63.8901 | -0.1709 | 0.0079723 | 0.0678 | 0.066441 | 0.13062 | 0.0014804 | -0.0017197 | -0.16457 | -0.004546 | -0.0050906 | -0.002886 | 0.003905 | -0.0036743 | 63.8672 | 64.0274 | 0.10529 | -59.1843 | 63.8489 | -59.0652 | -59.1019 | -58.9737 | 0.18768 | -59.2712 | 63.8855 | 63.7985 | -59.1156 | -59.2163 | -0.022889 | -0.05951 | -0.041199 | 123.0698 | -0.14191 | -0.082397 | -0.022889 | -0.073243 | -0.17395 | -0.004578 | 0.068664 | -0.22888 | -0.054931 | -0.091553 | 122.8912 | 122.9095 | 59.1476 | -122.9919 | 122.9279 | 122.8409 | 59.23 | -123.1064
982.5156 | 123.1796 | -59.0332 | 63.8031 | 0.18768 | 0.012886 | 0.067372 | 0.067296 | 0.12763 | 0.0021214 | -0.0019333 | 0.24742 | -0.0043324 | -0.0040226 | -0.0007498 | 0.004546 | -0.0068787 | 63.8397 | 63.9862 | 0.050354 | -59.2117 | 63.7756 | -59.079 | -59.111 | -58.9325 | 0.082397 | -59.2438 | 63.8351 | 63.707 | -59.1202 | -59.2255 | -0.045776 | -0.07782 | -0.027466 | 123.0194 | -0.17853 | -0.10071 | 0.036621 | -0.086975 | -0.19226 | 0.032043 | 0.10071 | -0.21057 | -0.01831 | -0.096131 | 122.8088 | 122.8729 | 59.0836 | -122.9141 | 122.8683 | 122.7402 | 59.1156 | -123.0286
983.5156 | 123.1293 | -59.0469 | 63.8535 | 0.19531 | 0.0073315 | 0.068654 | 0.065587 | 0.12849 | 0.00041235 | -0.00086512 | 0.30083 | -0.004546 | -0.0023136 | -0.001818 | 0.002837 | -0.0055969 | 63.8123 | 63.9633 | 0.041199 | -59.2438 | 63.7848 | -59.0744 | -59.1202 | -58.992 | 0.059509 | -59.2667 | 63.8077 | 63.7253 | -59.1156 | -59.2392 | -0.027466 | -0.073242 | -0.068665 | 123.0103 | -0.19684 | -0.1236 | -0.041199 | -0.068665 | -0.19226 | -0.045777 | 0.054932 | -0.21973 | -0.027466 | -0.12817 | 122.8317 | 122.8592 | 59.0881 | -122.9736 | 122.8546 | 122.7722 | 59.1064 | -123.0927
984.5156 | 123.1155 | -59.0652 | 63.7985 | 0.15717 | 0.0090405 | 0.069509 | 0.067082 | 0.12592 | -0.0015102 | -0.0021469 | 0.19402 | -0.0043324 | -0.0025272 | -0.001818 | 0.0013416 | -0.0038879 | 63.7985 | 63.945 | 0.041199 | -59.23 | 63.8168 | -59.0927 | -59.1431 | -58.9828 | 0.064087 | -59.1202 | 63.8763 | 63.7894 | -59.0927 | -59.2163 | -0.027465 | -0.077819 | 0.01831 | 123.0103 | -0.16479 | -0.086976 | 0 | -0.027465 | -0.15106 | 0.07782 | 0.082398 | -0.054931 | 0.096131 | -0.009155 | 122.8821 | 122.8638 | 59.1064 | -122.9416 | 122.9416 | 122.8546 | 59.1293 | -123.0148
985.5156 | 123.1613 | -59.0424 | 63.8123 | 0.38605 | 0.0030591 | 0.068227 | 0.066014 | 0.12721 | -0.0036464 | -0.00022432 | 0.11009 | -0.006255 | -0.0035952 | -0.0022452 | 0.0024096 | -0.0043153 | 63.7894 | 63.9221 | 0.059509 | -59.2438 | 63.8031 | -59.0607 | -59.1293 | -58.9737 | 0.086975 | -59.2758 | 63.8672 | 63.7573 | -59.1339 | -59.2346 | -0.018311 | -0.086975 | -0.009155 | 122.9645 | -0.20142 | -0.11444 | -0.022888 | -0.091553 | -0.19226 | 0.054931 | 0.068664 | -0.23346 | -0.041199 | -0.054932 | 122.8455 | 122.8317 | 59.1019 | -122.9416 | 122.9095 | 122.7997 | 59.1293 | -123.0469
986.5156 | 123.1979 | -59.0103 | 63.8489 | 0.24872 | 0.0086133 | 0.070577 | 0.06815 | 0.12635 | 0.00062595 | -0.0025741 | -0.034867 | -0.0049732 | -0.0046634 | -0.0022452 | 0.0026234 | -0.0038879 | 63.8992 | 64.0228 | 0.16937 | -59.1888 | 63.8351 | -59.0607 | -59.0927 | -58.9233 | 0.20599 | -59.2072 | 63.8672 | 63.7436 | -59.1431 | -59.2026 | -0.050354 | -0.082397 | -0.013733 | 123.0331 | -0.17853 | -0.096131 | 0.050354 | -0.13275 | -0.19226 | 0.01831 | 0.086975 | -0.19684 | -0.004577 | -0.10529 | 122.8455 | 122.9095 | 59.1797 | -122.9416 | 122.8775 | 122.7539 | 59.2163 | -123.0515
987.5156 | 123.1201 | -59.0698 | 63.8443 | 0.042725 | 0.0047681 | 0.069295 | 0.067082 | 0.12657 | -0.001083 | -0.0017197 | 0.7357 | -0.004546 | -0.0044498 | -0.0020316 | 0.0026234 | -0.0053833 | 63.7894 | 63.9587 | 0.07782 | -59.1156 | 63.8397 | -59.0652 | -59.0927 | -58.9966 | 0.036621 | -59.2941 | 63.8489 | 63.6978 | -59.1568 | -59.2484 | 0.004577 | -0.022888 | -0.004577 | 123.0286 | -0.045777 | -0.022889 | -0.054931 | -0.086975 | -0.17853 | 0.004578 | 0.073242 | -0.2243 | -0.045776 | -0.14648 | 122.9095 | 122.8592 | 59.1476 | -122.937 | 122.9187 | 122.7676 | 59.1064 | -123.0927
988.5156 | 123.1018 | -59.0698 | 63.8077 | 0.18005 | 0.012459 | 0.066518 | 0.069859 | 0.12913 | 0.0066074 | -0.0030013 | 0.17876 | -0.002837 | -0.001459 | -0.0009634 | 0.0036914 | -0.0068787 | 63.7619 | 63.8672 | 0.013733 | -59.285 | 63.858 | -59.111 | -59.1568 | -58.9874 | -0.009155 | -59.3308 | 63.8306 | 63.7161 | -59.1705 | -59.2438 | -0.041199 | -0.086975 | 0.050354 | 122.937 | -0.21515 | -0.12817 | -0.045776 | -0.10071 | -0.17395 | 0.022888 | 0.082397 | -0.26093 | -0.086976 | -0.091553 | 122.9279 | 122.8317 | 59.0836 | -122.9645 | 122.9004 | 122.7859 | 59.0607 | -123.0515
989.5156 | 123.1705 | -59.0607 | 63.7985 | -0.19379 | 0.0090405 | 0.068868 | 0.067082 | 0.1287 | -0.00022865 | 0.00063028 | 0.19402 | -0.0041186 | -0.0044498 | -0.002886 | 0.003905 | -0.0047425 | 63.8443 | 63.9862 | 0.16022 | -59.2072 | 63.8077 | -59.0927 | -59.1156 | -58.9462 | 0.068665 | -59.2712 | 63.8306 | 63.7024 | -59.1614 | -59.23 | -0.032043 | -0.054932 | 0.009155 | 123.0469 | -0.14648 | -0.091552 | 0.045776 | -0.10071 | -0.16937 | 0.032043 | 0.11444 | -0.21057 | -0.041198 | -0.09613 | 122.8683 | 122.905 | 59.2209 | -122.9141 | 122.8912 | 122.7631 | 59.1293 | -123.0286
990.5156 | 123.1613 | -59.0698 | 63.826 | 0.21057 | 0.0098951 | 0.068654 | 0.069859 | 0.1287 | 0.0012668 | 0.0010575 | 0.27031 | -0.0036914 | -0.0001774 | -0.0033134 | 0.0049732 | -0.0038879 | 63.7985 | 63.9175 | 0.10071 | -59.2575 | 63.8306 | -59.1202 | -59.1568 | -58.9783 | 0.050354 | -59.2758 | 63.8214 | 63.7253 | -59.1568 | -59.2392 | -0.050354 | -0.086975 | 0.004577 | 122.9874 | -0.18768 | -0.10071 | -0.027466 | -0.086975 | -0.16937 | -0.004578 | 0.091553 | -0.20599 | -0.036621 | -0.10071 | 122.9004 | 122.8683 | 59.1705 | -122.9828 | 122.8912 | 122.7951 | 59.1202 | -123.0652
991.5156 | 123.1384 | -59.0286 | 63.8763 | -0.15564 | 0.0071179 | 0.067372 | 0.067296 | 0.13255 | -0.0040738 | -0.0027877 | -0.14168 | -0.0030506 | -0.003168 | -0.0048086 | 0.001128 | -0.0051697 | 63.8489 | 64.0137 | 0.24719 | -59.1934 | 63.8306 | -59.0378 | -59.1248 | -58.96 | 0.19226 | -59.2438 | 63.8672 | 63.7848 | -59.1248 | -59.2392 | -0.009156 | -0.096131 | -0.045777 | 123.0423 | -0.1648 | -0.068664 | -0.027466 | -0.096131 | -0.21057 | -0.009156 | 0.068664 | -0.21515 | -0.004577 | -0.091553 | 122.8592 | 122.8775 | 59.2758 | -123.0011 | 122.8958 | 122.8134 | 59.2209 | -123.1155
992.5156 | 123.1796 | -59.0286 | 63.858 | 0.019836 | 0.0081861 | 0.067586 | 0.067723 | 0.12892 | -0.0032192 | -0.0012923 | 0.14824 | -0.0049732 | -0.0027408 | -0.0009634 | -0.0020764 | -0.0026063 | 63.7848 | 63.9496 | 0.1831 | -59.23 | 63.826 | -59.0836 | -59.0927 | -58.9828 | 0.10529 | -59.2346 | 63.8397 | 63.7482 | -59.1293 | -59.2438 | -0.054932 | -0.064087 | -0.032043 | 122.9782 | -0.20142 | -0.13733 | -0.073242 | -0.10071 | -0.21515 | -0.01831 | 0.045776 | -0.20599 | 0.009155 | -0.10986 | 122.8546 | 122.8134 | 59.2117 | -122.9507 | 122.8683 | 122.7768 | 59.1339 | -123.1018
993.5156 | 123.1338 | -59.0652 | 63.826 | 0.17242 | 0.0083997 | 0.068013 | 0.066441 | 0.13126 | -0.0012966 | 0.00084388 | 0.27031 | -0.0034778 | -0.0042362 | -0.0013906 | 0.0015552 | -0.0036743 | 63.8123 | 63.9679 | 0.20599 | -59.23 | 63.7802 | -59.0973 | -59.1156 | -58.9737 | 0.073242 | -59.2621 | 63.826 | 63.7115 | -59.1522 | -59.2346 | -0.032043 | -0.050354 | -0.045777 | 123.0331 | -0.16479 | -0.11444 | -0.013733 | -0.086975 | -0.16937 | 0 | 0.091553 | -0.19684 | -0.027466 | -0.11444 | 122.8455 | 122.8775 | 59.2712 | -122.9416 | 122.8912 | 122.7768 | 59.1385 | -123.0606
994.5156 | 123.1888 | -59.0378 | 63.8031 | 0.24109 | 0.012459 | 0.067159 | 0.069218 | 0.12956 | 0.0019078 | -0.0017197 | 0.23979 | -0.0034778 | 0.0011044 | 0.000532 | 0.0036914 | -0.0045289 | 63.7985 | 63.913 | 0.14191 | -59.2667 | 63.8397 | -59.0973 | -59.166 | -58.9828 | 0.059509 | -59.2941 | 63.8351 | 63.7253 | -59.1568 | -59.2209 | -0.059509 | -0.12817 | 0.036621 | 122.9507 | -0.22888 | -0.10071 | -0.004578 | -0.11902 | -0.1831 | 0.032043 | 0.054932 | -0.25635 | -0.073242 | -0.07782 | 122.8775 | 122.8363 | 59.1797 | -122.9691 | 122.8729 | 122.7631 | 59.0973 | -123.024
995.5156 | 123.1659 | -59.0103 | 63.8168 | 0.23346 | 0.0098951 | 0.066091 | 0.066868 | 0.12721 | 0.0029758 | -0.00043792 | 0.24742 | -0.0034778 | -0.0035952 | 0.0024546 | 0.0051868 | -0.0064515 | 63.8214 | 63.9587 | 0.22888 | -59.2026 | 63.7802 | -59.079 | -59.1476 | -58.9233 | 0.20599 | -59.2758 | 63.8123 | 63.7482 | -59.0927 | -59.2209 | -0.068664 | -0.13733 | -0.036621 | 122.9691 | -0.19226 | -0.054932 | 0.004578 | -0.082397 | -0.21057 | -0.004577 | 0.086975 | -0.2655 | -0.054932 | -0.068664 | 122.7905 | 122.8317 | 59.2392 | -122.9645 | 122.8226 | 122.7585 | 59.2163 | -123.0377
996.5156 | 123.0423 | -59.0927 | 63.8214 | 0.15717 | 0.021431 | 0.068654 | 0.071568 | 0.12785 | 0.005753 | -0.0012923 | 0.094833 | -0.0017688 | -0.0008182 | -0.0013906 | 0.0030506 | -0.0030335 | 63.6887 | 63.8901 | 0.1831 | -59.3033 | 63.8763 | -59.1156 | -59.1705 | -59.0652 | -0.045776 | -59.3811 | 63.8672 | 63.7482 | -59.1431 | -59.2667 | -0.022889 | -0.07782 | 0.054932 | 122.9828 | -0.21057 | -0.13275 | -0.13275 | -0.050354 | -0.17395 | 0.045776 | 0.027465 | -0.28839 | -0.11444 | -0.073242 | 122.9691 | 122.7814 | 59.2758 | -122.9919 | 122.9599 | 122.8409 | 59.0469 | -123.0881
997.5156 | 123.1522 | -59.0652 | 63.8077 | 0.18768 | 0.013313 | 0.069081 | 0.065159 | 0.12827 | 0.0019078 | -0.00022432 | 0.12535 | -0.0032642 | -0.0018862 | -0.000109 | 0.0049732 | -0.0038879 | 63.8397 | 64.0961 | 0.36163 | -59.2163 | 63.7848 | -59.0698 | -59.1156 | -58.9462 | 0.086975 | -59.2484 | 63.8031 | 63.7024 | -59.1248 | -59.2438 | -0.004577 | -0.050354 | -0.022888 | 123.1613 | -0.15106 | -0.10071 | 0.032044 | -0.059509 | -0.17853 | -0.004577 | 0.11902 | -0.1831 | -0.004578 | -0.10529 | 122.85 | 122.905 | 59.4269 | -122.9233 | 122.8683 | 122.7676 | 59.1522 | -123.0515
998.5156 | 123.0972 | -59.0973 | 63.8397 | 0.15717 | 0.014595 | 0.066091 | 0.070073 | 0.12592 | 0.0042576 | -0.0012923 | 0.17876 | -0.0019824 | -0.0010318 | 0.0001046 | 0.0041186 | -0.0077331 | 63.7344 | 63.8306 | 0.19226 | -59.2896 | 63.8535 | -59.1248 | -59.166 | -59.0561 | -0.036621 | -59.3536 | 63.8809 | 63.7573 | -59.1751 | -59.2667 | -0.027466 | -0.068665 | 0.013733 | 122.9279 | -0.19226 | -0.1236 | -0.10529 | -0.07782 | -0.16937 | 0.041198 | 0.041199 | -0.25635 | -0.086975 | -0.082398 | 122.9507 | 122.8317 | 59.2896 | -123.0057 | 122.9782 | 122.8546 | 59.0607 | -123.1064
999.5156 | 123.1705 | -59.0652 | 63.8077 | 0.19531 | 0.011177 | 0.066304 | 0.067296 | 0.12892 | 0.00019875 | -1.0724e-05 | 0.19402 | -0.002196 | -0.0029544 | -0.0013906 | 0.003905 | -0.0051697 | 63.7939 | 63.9267 | 0.28381 | -59.23 | 63.8123 | -59.1019 | -59.1476 | -58.9737 | 0.073242 | -59.2621 | 63.8168 | 63.7115 | -59.1522 | -59.2255 | -0.036621 | -0.082397 | 0.004578 | 122.9919 | -0.16479 | -0.082398 | -0.013733 | -0.086975 | -0.16022 | 0.009155 | 0.091553 | -0.19684 | -0.036621 | -0.09613 | 122.8775 | 122.8592 | 59.3491 | -122.9553 | 122.8821 | 122.7768 | 59.1385 | -123.0331
1000.5156 | 123.0835 | -59.0927 | 63.8397 | 0.18005 | 0.013313 | 0.066304 | 0.071354 | 0.12699 | 0.0012668 | -0.0012923 | 0.20164 | -0.0024096 | -0.0010318 | -0.001818 | 0.0013416 | -0.0049561 | 63.7527 | 63.8214 | 0.21515 | -59.285 | 63.8397 | -59.1156 | -59.1797 | -59.0744 | -0.022888 | -59.3536 | 63.858 | 63.7756 | -59.1568 | -59.2758 | -0.022889 | -0.086975 | 0 | 122.9141 | -0.19226 | -0.10529 | -0.086975 | -0.064087 | -0.18311 | 0.01831 | 0.01831 | -0.26093 | -0.07782 | -0.064087 | 122.9324 | 122.8455 | 59.3079 | -123.0194 | 122.9507 | 122.8683 | 59.0698 | -123.1155
1001.5156 | 123.2483 | -59.0927 | 63.8077 | 0.21057 | 0.010963 | 0.066518 | 0.065373 | 0.12806 | 0.00041235 | -0.0010787 | 0.23979 | -0.0036914 | -0.0021 | -0.001177 | 0.0032642 | -0.0049561 | 63.8214 | 63.9359 | 0.32959 | -59.2209 | 63.7894 | -59.079 | -59.1293 | -58.9783 | 0.082397 | -59.2621 | 63.8123 | 63.7344 | -59.1751 | -59.2667 | 0.013733 | -0.036621 | -0.01831 | 123.0286 | -0.12817 | -0.091553 | 0.013733 | -0.082398 | -0.17395 | 0.004578 | 0.11444 | -0.16937 | 0.004578 | -0.073242 | 122.8821 | 122.9141 | 59.4223 | -122.937 | 122.905 | 122.8271 | 59.1751 | -123.0743
1002.5156 | 123.024 | -59.0973 | 63.8901 | 0.065613 | 0.014808 | 0.067159 | 0.069218 | 0.12742 | 0.0038304 | 0.00020288 | 0.079574 | -0.0015552 | -0.0006046 | -0.001177 | 0.0058276 | -0.0038879 | 63.7711 | 63.8672 | 0.32501 | -59.2712 | 63.8626 | -59.0881 | -59.1431 | -59.0561 | 0.004578 | -59.3719 | 63.858 | 63.7894 | -59.1614 | -59.2667 | 0.009155 | -0.045776 | -0.027466 | 122.9645 | -0.17395 | -0.12817 | -0.11902 | -0.064087 | -0.16937 | -0.032044 | 0.041199 | -0.27466 | -0.10529 | -0.10071 | 122.9599 | 122.8683 | 59.4223 | -123.0331 | 122.9553 | 122.8867 | 59.1019 | -123.1567
1003.5156 | 123.1384 | -59.0698 | 63.8168 | 0.16479 | 0.013099 | 0.067586 | 0.067936 | 0.12827 | 0.0027622 | -0.0021469 | 0.24742 | -0.002837 | -0.0018862 | -0.0022452 | 0.0032642 | -0.0021789 | 63.7573 | 63.8672 | 0.3067 | -59.2621 | 63.8351 | -59.1064 | -59.1522 | -59.0149 | 0.022888 | -59.317 | 63.8489 | 63.7711 | -59.166 | -59.2712 | -0.036621 | -0.082398 | 0.018311 | 122.937 | -0.19226 | -0.10986 | -0.059509 | -0.096131 | -0.20142 | 0.032044 | 0.054931 | -0.24719 | -0.045777 | -0.045776 | 122.905 | 122.8271 | 59.3765 | -122.9691 | 122.9187 | 122.8409 | 59.0927 | -123.0881
1004.5156 | 123.0286 | -59.0881 | 63.858 | 0.057983 | 0.013313 | 0.0678 | 0.069218 | 0.12806 | 0.0012668 | 0.0012711 | 0.049057 | -0.00048697 | 0.00025 | -0.0013906 | 0.0043324 | -0.0053833 | 63.7573 | 63.8489 | 0.34332 | -59.2621 | 63.8626 | -59.1156 | -59.1476 | -59.0973 | -0.004578 | -59.3857 | 63.8809 | 63.8123 | -59.1751 | -59.2621 | -0.027466 | -0.059509 | 0.004578 | 122.937 | -0.17395 | -0.11444 | -0.10071 | -0.086975 | -0.17395 | 0.022888 | -0.009155 | -0.29755 | -0.1236 | -0.045776 | 122.9507 | 122.8455 | 59.4315 | -123.0057 | 122.9691 | 122.9004 | 59.0836 | -123.1201
1005.5156 | 123.0698 | -59.0698 | 63.8306 | 0.20294 | 0.012886 | 0.066731 | 0.068791 | 0.12934 | 0.0010532 | -0.0023605 | 0.22453 | -0.002837 | -0.0033816 | 0.0011728 | 0.0024096 | -0.0038879 | 63.7482 | 63.826 | 0.32959 | -59.285 | 63.8443 | -59.1202 | -59.1568 | -59.0698 | -0.022888 | -59.3536 | 63.858 | 63.7802 | -59.1614 | -59.2896 | -0.050354 | -0.086975 | 0.013733 | 122.8958 | -0.21515 | -0.12817 | -0.082397 | -0.091553 | -0.21973 | 0.027466 | 0 | -0.28381 | -0.064087 | -0.050354 | 122.9141 | 122.818 | 59.3994 | -122.9874 | 122.9279 | 122.85 | 59.0469 | -123.1201
1006.5156 | 123.0881 | -59.0927 | 63.8535 | 0.027466 | 0.014595 | 0.065877 | 0.069859 | 0.12977 | 0.0019078 | -0.0021469 | 0.10246 | -0.002837 | 3.6404e-05 | -0.0003226 | 0.002196 | -0.0032471 | 63.7985 | 63.8855 | 0.42114 | -59.2438 | 63.8672 | -59.0836 | -59.1476 | -59.0378 | 0.050354 | -59.3308 | 63.8855 | 63.7985 | -59.166 | -59.2529 | 0.009155 | -0.054932 | 0.013732 | 122.9782 | -0.15106 | -0.09613 | -0.054932 | -0.073243 | -0.16022 | 0.032043 | 0.054931 | -0.23804 | -0.07782 | -0.054932 | 122.9599 | 122.8912 | 59.5139 | -123.0011 | 122.9782 | 122.8912 | 59.1431 | -123.1064
1007.5156 | 123.0515 | -59.0836 | 63.8397 | 0.15717 | 0.014808 | 0.066518 | 0.066868 | 0.12657 | 0.0010532 | -0.00022432 | 0.23979 | -0.0030506 | 3.6404e-05 | -0.0020316 | 0.001128 | -0.0034607 | 63.7527 | 63.826 | 0.32959 | -59.2941 | 63.858 | -59.1248 | -59.1614 | -59.0607 | -0.027466 | -59.3674 | 63.8626 | 63.7711 | -59.1476 | -59.2575 | -0.041199 | -0.07782 | 0.01831 | 122.9095 | -0.21057 | -0.13275 | -0.086975 | -0.064087 | -0.17395 | 0.022888 | 0.022888 | -0.28381 | -0.10986 | -0.068665 | 122.9416 | 122.8363 | 59.4131 | -123.0011 | 122.9462 | 122.8546 | 59.0561 | -123.0972
1008.5156 | 123.0927 | -59.0652 | 63.8489 | 0.050354 | 0.012459 | 0.069295 | 0.069432 | 0.12977 | 0.0019078 | 0.00020288 | 0.11009 | -0.0030506 | 0.0021726 | -0.0016044 | 0.002196 | -0.0047425 | 63.7894 | 63.8809 | 0.39368 | -59.2484 | 63.8489 | -59.0836 | -59.1522 | -59.0652 | 0.032043 | -59.3491 | 63.8672 | 63.8123 | -59.1568 | -59.2758 | -0.01831 | -0.086975 | 0 | 122.9462 | -0.1831 | -0.09613 | -0.059509 | -0.091552 | -0.21057 | 0.01831 | 0 | -0.28381 | -0.073242 | -0.036621 | 122.9141 | 122.8546 | 59.4589 | -123.0011 | 122.9324 | 122.8775 | 59.0973 | -123.1247
1009.5156 | 123.056 | -59.0744 | 63.8718 | 0.0045777 | 0.013313 | 0.066518 | 0.072209 | 0.12977 | 0.0012668 | -0.00065152 | 0.071945 | -0.0019824 | -0.0008182 | -0.0007498 | 0.0019824 | -0.0032471 | 63.739 | 63.8535 | 0.37994 | -59.2758 | 63.8306 | -59.0927 | -59.1476 | -59.0973 | -0.018311 | -59.3903 | 63.8763 | 63.8077 | -59.1751 | -59.2667 | -0.01831 | -0.073242 | -0.041199 | 122.9279 | -0.20142 | -0.12817 | -0.13275 | -0.10071 | -0.19226 | 0.004578 | -0.022888 | -0.31586 | -0.1236 | -0.064087 | 122.905 | 122.8134 | 59.4543 | -123.0194 | 122.9507 | 122.8821 | 59.0561 | -123.1384
1010.5156 | 123.0927 | -59.0973 | 63.8351 | -0.15564 | 0.012886 | 0.066945 | 0.067082 | 0.13126 | 0.0031894 | -0.0019333 | -0.027237 | -0.002837 | -0.0038088 | -0.0013906 | 0.0026234 | -0.0060243 | 63.7985 | 63.9221 | 0.49896 | -59.2163 | 63.8718 | -59.0881 | -59.1293 | -59.0332 | 0.10529 | -59.3124 | 63.8992 | 63.8214 | -59.1476 | -59.2575 | 0.009155 | -0.032043 | 0.036621 | 123.0194 | -0.11902 | -0.086976 | -0.036621 | -0.050354 | -0.16022 | 0.064087 | 0.064087 | -0.21515 | -0.054932 | -0.013733 | 122.9691 | 122.8958 | 59.5963 | -122.9645 | 122.9965 | 122.9187 | 59.2026 | -123.0927
1011.5156 | 123.0515 | -59.0927 | 63.8718 | 0.050354 | 0.014595 | 0.066945 | 0.069859 | 0.12977 | 0.002335 | -0.0012923 | 0.1635 | -0.0030506 | 0.003027 | -0.0007498 | 0.0017688 | -0.0021789 | 63.7344 | 63.8306 | 0.42114 | -59.2712 | 63.8397 | -59.1019 | -59.1522 | -59.1064 | -0.032043 | -59.3994 | 63.8809 | 63.7985 | -59.1888 | -59.2712 | -0.009156 | -0.05951 | -0.032043 | 122.9233 | -0.17853 | -0.11902 | -0.13733 | -0.096131 | -0.17853 | 0.009155 | -0.013733 | -0.3067 | -0.12817 | -0.073242 | 122.9324 | 122.8271 | 59.5139 | -123.024 | 122.9736 | 122.8912 | 59.0607 | -123.143
1012.5156 | 123.0835 | -59.0698 | 63.9038 | -0.10223 | 0.016945 | 0.066518 | 0.070927 | 0.12806 | 0.00062595 | -0.0034287 | 0.026169 | -0.0049732 | -0.0001774 | -0.0022452 | 0.0030506 | -0.0055969 | 63.8077 | 63.9038 | 0.51727 | -59.2163 | 63.8489 | -59.0744 | -59.1568 | -59.0195 | 0.10529 | -59.2987 | 63.8992 | 63.7711 | -59.1614 | -59.2804 | -0.004578 | -0.086975 | -0.054932 | 122.9736 | -0.14649 | -0.05951 | -0.096131 | -0.091553 | -0.21057 | -0.004578 | 0.050354 | -0.22888 | -0.01831 | -0.13275 | 122.9187 | 122.8775 | 59.5871 | -123.0606 | 122.9691 | 122.8409 | 59.1751 | -123.1842
1013.5156 | 123.0835 | -59.0836 | 63.8489 | -0.010681 | 0.015236 | 0.066731 | 0.069218 | 0.12763 | 0.002335 | -0.0036423 | 0.11009 | -0.0017688 | 3.6404e-05 | -0.0007498 | 0.003905 | -0.0047425 | 63.7756 | 63.8855 | 0.49896 | -59.2484 | 63.8397 | -59.0881 | -59.1248 | -59.0652 | 0.054932 | -59.3536 | 63.8535 | 63.8214 | -59.1705 | -59.2667 | -0.004578 | -0.041199 | -0.009155 | 122.9691 | -0.16479 | -0.1236 | -0.073242 | -0.086975 | -0.18311 | 0.004578 | 0.01831 | -0.27008 | -0.086975 | -0.027466 | 122.9233 | 122.8592 | 59.5825 | -122.9736 | 122.937 | 122.905 | 59.1385 | -123.1155
1014.5156 | 123.0835 | -59.0424 | 63.8489 | -0.13275 | 0.013527 | 0.066091 | 0.069645 | 0.13041 | 0.00041235 | -0.00022432 | -0.0043486 | -0.0034778 | -0.0016726 | -0.001177 | 0.0041186 | -0.0053833 | 63.8031 | 63.9175 | 0.52643 | -59.2117 | 63.8626 | -59.0652 | -59.1156 | -59.024 | -0.16479 | -59.3811 | 63.858 | 63.8214 | -59.1568 | -59.2575 | -0.022889 | -0.073243 | 0.013733 | 122.9599 | -0.16937 | -0.09613 | -0.045776 | -0.11444 | -0.21515 | 0.009155 | 0.01831 | -0.33875 | -0.1236 | -0.027466 | 122.905 | 122.8455 | 59.5688 | -122.9645 | 122.9004 | 122.8638 | 58.8776 | -123.1064
1015.5156 | 123.0698 | -59.0836 | 63.8626 | 0.019836 | 0.016304 | 0.066304 | 0.0705 | 0.1287 | 0.0046848 | 0.00084388 | 0.094833 | -0.0032642 | -0.000391 | -0.0020316 | 0.0030506 | -0.0028199 | 63.7985 | 63.8672 | 0.53101 | -59.2575 | 63.826 | -59.0881 | -59.1385 | -59.0515 | 0.045776 | -59.3353 | 63.8535 | 63.8168 | -59.1705 | -59.2392 | -0.004578 | -0.054932 | -0.036621 | 122.9507 | -0.17395 | -0.11902 | -0.064087 | -0.086975 | -0.15564 | -0.009155 | 0.032043 | -0.25177 | -0.09613 | -0.045777 | 122.9095 | 122.8821 | 59.6146 | -123.0011 | 122.937 | 122.9004 | 59.1293 | -123.1018
1016.5156 | 123.0606 | -59.0698 | 63.9038 | 0.12665 | 0.0092541 | 0.066731 | 0.069432 | 0.12977 | -0.00044225 | -0.0047103 | -0.034867 | -0.0026234 | 0.0006772 | -0.0020316 | 5.9768e-05 | -0.0038879 | 63.7985 | 63.8718 | 0.54474 | -59.2621 | 63.8397 | -59.0927 | -59.1522 | -59.0744 | 0.07782 | -59.3124 | 63.9221 | 63.8901 | -59.1385 | -59.2346 | -0.022888 | -0.082398 | -0.064087 | 122.9416 | -0.19226 | -0.10986 | -0.10529 | -0.068665 | -0.1648 | 0.01831 | -0.004578 | -0.24262 | -0.07782 | -0.013733 | 122.9095 | 122.8683 | 59.6146 | -123.056 | 122.9919 | 122.9599 | 59.1476 | -123.1384
1017.5156 | 123.1018 | -59.0652 | 63.8489 | -0.16327 | 0.013954 | 0.064382 | 0.0705 | 0.12806 | 0.001694 | -0.0017197 | -0.050125 | -0.004546 | -0.0001774 | 0.0011728 | 0.0019824 | -0.0034607 | 63.8123 | 63.9038 | 0.58594 | -59.2255 | 63.8763 | -59.0561 | -59.1202 | -59.0378 | 0.10986 | -59.2941 | 63.9038 | 63.826 | -59.1339 | -59.2438 | 0.009156 | -0.054931 | 0.027466 | 122.9691 | -0.16022 | -0.10529 | -0.036621 | -0.068664 | -0.17853 | 0.054932 | 0.027466 | -0.22888 | -0.050354 | -0.022888 | 122.9416 | 122.8775 | 59.6512 | -122.9691 | 122.9691 | 122.8912 | 59.1751 | -123.0927
1018.5156 | 123.0881 | -59.0698 | 63.8809 | -0.20905 | 0.01374 | 0.066518 | 0.068577 | 0.12998 | -0.0019376 | -0.0040695 | -0.080643 | -0.004546 | -0.0018862 | -0.002886 | 0.0013416 | -0.0045289 | 63.7527 | 63.8855 | 0.58594 | -59.2346 | 63.8718 | -59.1019 | -59.1385 | -59.0698 | 0.10071 | -59.317 | 63.8901 | 63.826 | -59.1339 | -59.23 | -0.032044 | -0.068665 | -0.009155 | 122.9553 | -0.1648 | -0.09613 | -0.12817 | -0.064087 | -0.16022 | 0.009156 | 0 | -0.24719 | -0.086975 | -0.054931 | 122.9416 | 122.8226 | 59.6558 | -123.0194 | 122.9599 | 122.8958 | 59.1705 | -123.111
1019.5156 | 123.0652 | -59.079 | 63.8718 | -0.10986 | 0.012031 | 0.066945 | 0.070714 | 0.13191 | 0.0027622 | -0.00043792 | -0.088272 | -0.0032642 | -0.0025272 | 0.0009592 | 0.001128 | -0.0043153 | 63.8031 | 63.9221 | 0.65002 | -59.2026 | 63.8855 | -59.0698 | -59.1522 | -59.024 | 0.11444 | -59.2804 | 63.8947 | 63.7939 | -59.1293 | -59.2438 | 0.009155 | -0.073243 | 0.013733 | 123.0011 | -0.1236 | -0.050354 | -0.068664 | -0.050354 | -0.1648 | 0.022888 | 0.054931 | -0.20142 | -0.036622 | -0.07782 | 122.9645 | 122.8821 | 59.729 | -123.024 | 122.9736 | 122.8729 | 59.1934 | -123.1155
1020.5156 | 123.0835 | -59.0744 | 63.913 | -0.18616 | 0.0094677 | 0.066518 | 0.069645 | 0.13084 | -0.0032192 | -0.0030013 | 0.0032804 | -5.9768e-05 | -0.001459 | -0.0022452 | 0.00048697 | -0.0036743 | 63.7436 | 63.9084 | 0.69122 | -59.2438 | 63.8672 | -59.0607 | -59.1293 | -59.0652 | 0.082397 | -59.2026 | 63.9404 | 63.8809 | -59.1385 | -59.2163 | 0.013733 | -0.054931 | -0.045777 | 122.9828 | -0.16937 | -0.11444 | -0.16937 | -0.064087 | -0.14191 | 0.027466 | 0.009155 | -0.12817 | 0.013733 | -0.032044 | 122.9416 | 122.818 | 59.7656 | -123.0423 | 123.0148 | 122.9553 | 59.1568 | -123.1293
1021.5156 | 123.111 | -59.0652 | 63.858 | -0.14038 | 0.013527 | 0.06545 | 0.069859 | 0.12571 | 0.00062595 | -0.0036423 | -0.034867 | -0.002837 | -0.0010318 | 0.0011728 | 0.0030506 | -0.0032471 | 63.8077 | 63.9084 | 0.737 | -59.2072 | 63.8626 | -59.079 | -59.1293 | -59.0103 | 0.10071 | -59.2941 | 63.8626 | 63.826 | -59.1156 | -59.2346 | -0.013732 | -0.064086 | 0.004578 | 122.9736 | -0.14191 | -0.07782 | -0.050354 | -0.050354 | -0.16937 | 0.004578 | 0.054932 | -0.22888 | -0.059509 | -0.032043 | 122.9279 | 122.8729 | 59.8022 | -122.9874 | 122.9279 | 122.8912 | 59.166 | -123.0927
1022.5156 | 123.056 | -59.0607 | 63.913 | -0.21667 | 0.0083997 | 0.069295 | 0.069432 | 0.13062 | -0.0032192 | -0.0044967 | -0.11116 | -0.0047596 | -0.0029544 | -0.0007498 | 0.0024096 | -0.0021789 | 63.7573 | 63.8947 | 0.72784 | -59.2529 | 63.8626 | -59.1156 | -59.1202 | -59.1614 | 0.14191 | -59.3445 | 63.8992 | 63.8535 | -59.1568 | -59.2438 | -0.054932 | -0.059509 | -0.050354 | 122.9553 | -0.19226 | -0.13275 | -0.15564 | -0.09613 | -0.18311 | -0.013733 | -0.10071 | -0.28381 | -0.10071 | -0.059509 | 122.9233 | 122.818 | 59.7885 | -123.0331 | 122.9599 | 122.9141 | 59.2026 | -123.1567
1023.5156 | 123.0698 | -59.0332 | 63.9175 | -0.24719 | 0.0092541 | 0.066945 | 0.070073 | 0.12892 | 0.00019875 | -0.0030013 | -0.073013 | -0.0051868 | -0.0023136 | -0.0020316 | 0.002196 | -0.0055969 | 63.7665 | 63.8992 | 0.78278 | -59.2346 | 63.8672 | -59.0698 | -59.1202 | -59.0561 | 0.086975 | -59.3353 | 63.9084 | 63.8351 | -59.1293 | -59.2346 | -0.036621 | -0.086975 | -0.050355 | 122.9324 | -0.20142 | -0.11444 | -0.15106 | -0.09613 | -0.20142 | -0.009156 | -0.022888 | -0.30212 | -0.10071 | -0.082398 | 122.9004 | 122.7997 | 59.816 | -123.0377 | 122.9416 | 122.8683 | 59.1202 | -123.1522
1024.5156 | 123.175 | -59.0286 | 63.8626 | -0.16327 | 0.0056225 | 0.066304 | 0.067723 | 0.12721 | -0.00621 | -0.0027877 | -0.0043486 | -0.006255 | -0.0033816 | 0.0001046 | 0.00027337 | -0.0028199 | 63.8443 | 64.0137 | 0.92926 | -59.1843 | 63.8489 | -59.0515 | -59.0927 | -58.9691 | 0.20599 | -59.198 | 63.8535 | 63.8214 | -59.1064 | -59.2163 | -0.022889 | -0.064087 | -0.013733 | 123.0423 | -0.15564 | -0.091553 | -0.018311 | -0.07782 | -0.18768 | -0.009155 | 0.059509 | -0.16937 | 0.018311 | -0.041199 | 122.8775 | 122.8729 | 59.9579 | -122.9553 | 122.8821 | 122.85 | 59.2346 | -123.0789
1025.5156 | 123.0698 | -59.0515 | 63.8901 | -0.21667 | 0.0094677 | 0.067586 | 0.071568 | 0.1255 | 0.0012668 | -0.0040695 | -0.13405 | -0.0017688 | 0.0008908 | -0.0016044 | 0.0034778 | -0.0047425 | 63.7665 | 63.8901 | 0.85144 | -59.2438 | 63.8901 | -59.0607 | -59.1385 | -59.0561 | 0.091553 | -59.3216 | 63.8901 | 63.8443 | -59.1522 | -59.2438 | -0.009155 | -0.086975 | 0 | 122.9416 | -0.19226 | -0.10529 | -0.1236 | -0.10071 | -0.19226 | 0 | -0.004577 | -0.27008 | -0.07782 | -0.045777 | 122.9416 | 122.818 | 59.903 | -123.0286 | 122.9416 | 122.8958 | 59.1431 | -123.1338
1026.5156 | 123.1338 | -59.0286 | 63.8809 | -0.16327 | 0.0096813 | 0.0678 | 0.069218 | 0.12998 | -0.0032192 | -0.0032151 | -0.088272 | -0.004546 | -0.001459 | -0.0009634 | 0.00070077 | -0.0049561 | 63.826 | 64.0137 | 1.03 | -59.1751 | 63.8626 | -59.0469 | -59.0881 | -58.9645 | 0.16937 | -59.2255 | 63.8718 | 63.8077 | -59.1064 | -59.2255 | -0.018311 | -0.05951 | -0.01831 | 123.0423 | -0.14648 | -0.086975 | -0.054931 | -0.07782 | -0.19684 | -0.009155 | 0.064086 | -0.19684 | 0 | -0.073242 | 122.8912 | 122.8546 | 60.0586 | -122.9691 | 122.9004 | 122.8363 | 59.198 | -123.1064
1027.5156 | 123.056 | -59.0469 | 63.8809 | -0.21667 | 0.011604 | 0.06844 | 0.070714 | 0.12742 | 0.00062595 | -0.0021469 | -0.45448 | -0.003905 | -0.0033816 | -0.000109 | 0.002837 | -0.0053833 | 63.7665 | 63.9175 | 0.94757 | -59.3353 | 63.8809 | -59.0652 | -59.0927 | -59.0424 | 0.054932 | -59.3262 | 63.9267 | 63.8077 | -59.1431 | -59.2255 | -0.018311 | -0.045776 | 0 | 122.9645 | -0.28839 | -0.24262 | -0.11444 | -0.09613 | -0.17853 | 0.045777 | 0.004578 | -0.27924 | -0.10071 | -0.073242 | 122.9279 | 122.8134 | 59.9945 | -122.9736 | 122.9736 | 122.8546 | 59.1019 | -123.1064
1028.5156 | 123.111 | -58.9966 | 63.8763 | -0.1709 | 0.0081861 | 0.068227 | 0.070286 | 0.12934 | -0.0021512 | -0.0036423 | -0.050125 | -0.0051868 | -0.0012454 | -0.001818 | 0.0019824 | -0.0045289 | 63.8214 | 63.9908 | 1.0849 | -59.166 | 63.8443 | -59.0698 | -59.111 | -58.992 | 0.15564 | -59.2758 | 63.8809 | 63.7985 | -59.111 | -59.2117 | -0.073242 | -0.11444 | -0.032044 | 122.9874 | -0.16937 | -0.054932 | -0.054932 | -0.11444 | -0.21515 | 0.004577 | 0.004578 | -0.27924 | -0.064087 | -0.07782 | 122.8409 | 122.818 | 60.0815 | -122.9874 | 122.8775 | 122.7951 | 59.1522 | -123.0881
1029.5156 | 123.0194 | -59.0424 | 63.8855 | -0.20905 | 0.011604 | 0.065236 | 0.068791 | 0.12956 | 0.00062595 | -0.0032151 | -0.10353 | -0.003905 | -0.000391 | -0.0022452 | 0.00027337 | -0.0047425 | 63.7527 | 63.9221 | 1.0345 | -59.2575 | 63.8763 | -59.079 | -59.1568 | -59.0469 | 0.07782 | -59.3124 | 63.9359 | 63.8351 | -59.1431 | -59.2255 | -0.036621 | -0.11444 | -0.009155 | 122.9645 | -0.21515 | -0.10071 | -0.13275 | -0.10071 | -0.18311 | 0.050354 | -0.004578 | -0.27008 | -0.086975 | -0.050354 | 122.9187 | 122.7951 | 60.0769 | -123.0423 | 122.9782 | 122.8775 | 59.1202 | -123.111
1030.5156 | 123.1842 | -58.9966 | 63.8626 | -0.02594 | 0.0073315 | 0.067586 | 0.069432 | 0.12742 | -0.0036464 | -0.0040695 | 0.01091 | -0.005614 | -0.0053042 | -0.0043814 | -0.00036743 | -0.00089726 | 63.8535 | 64.0503 | 1.1902 | -59.1568 | 63.858 | -59.0652 | -59.0927 | -59.1019 | 0.14648 | -59.1843 | 63.8443 | 63.7665 | -59.1202 | -59.2484 | -0.068665 | -0.09613 | -0.004578 | 123.0469 | -0.16022 | -0.064087 | -0.009155 | -0.1236 | -0.25177 | -0.018311 | -0.10529 | -0.18768 | 0.064087 | -0.096131 | 122.8546 | 122.85 | 60.1868 | -122.9553 | 122.8409 | 122.7631 | 59.1431 | -123.111
1031.5156 | 123.0835 | -59.0607 | 63.8947 | -0.1709 | 0.0090405 | 0.066945 | 0.069432 | 0.12849 | -0.0017238 | -0.0040695 | -0.13405 | -0.0047596 | -0.0029544 | -0.0020316 | 0.00070077 | -0.0049561 | 63.8351 | 64.0045 | 1.2222 | -59.166 | 63.8443 | -59.0607 | -59.111 | -58.9828 | 0.16022 | -59.2575 | 63.8672 | 63.7939 | -59.1248 | -59.2255 | 0 | -0.050354 | -0.050354 | 123.0652 | -0.10529 | -0.054932 | -0.059509 | -0.064087 | -0.1648 | -0.027466 | 0.07782 | -0.19684 | -0.032043 | -0.10071 | 122.905 | 122.8958 | 60.2829 | -123.0057 | 122.9279 | 122.8546 | 59.2209 | -123.1201
1032.5156 | 123.175 | -59.024 | 63.8626 | -0.10986 | 0.0062635 | 0.066945 | 0.071141 | 0.12678 | -0.0032192 | -0.0068465 | -0.14931 | -0.003905 | -0.0023136 | -0.0022452 | -0.00079463 | -0.0064515 | 64.2288 | 63.7848 | 1.0803 | -59.2667 | 63.8351 | -59.0698 | -59.1156 | -58.9325 | 0.20142 | -59.2117 | 63.858 | 63.7985 | -59.0927 | -59.1934 | -0.045776 | -0.091553 | -0.027466 | 122.8088 | -0.24262 | -0.15106 | 0.36621 | -0.068664 | -0.16937 | -0.004578 | 0.091553 | -0.18768 | -0.018311 | -0.064087 | 122.8592 | 123.2529 | 60.1044 | -122.9782 | 122.8821 | 122.8226 | 59.2255 | -123.056
1033.5156 | 123.0743 | -59.0652 | 63.9084 | -0.21667 | 0.0066907 | 0.066731 | 0.068791 | 0.12806 | -0.001083 | -0.0023605 | -0.10353 | -0.0049732 | -0.0025272 | -0.0005362 | 0.0017688 | -0.0068787 | 63.8077 | 63.9908 | 1.2955 | -59.1888 | 63.8306 | -59.0652 | -59.111 | -59.0012 | 0.11444 | -59.2987 | 63.9084 | 63.826 | -59.1293 | -59.2026 | 0 | -0.045776 | -0.07782 | 123.056 | -0.1236 | -0.07782 | -0.10071 | -0.064086 | -0.13733 | 0 | 0.064087 | -0.23346 | -0.09613 | -0.082397 | 122.8958 | 122.8729 | 60.3607 | -123.0194 | 122.9736 | 122.8912 | 59.1797 | -123.111
1034.5156 | 123.175 | -59.0012 | 63.8626 | -0.27771 | 0.0056225 | 0.068227 | 0.068791 | 0.12721 | -0.0021512 | -0.0017197 | -0.027237 | -0.0054004 | -0.0029544 | -0.002886 | 5.9768e-05 | -0.0030335 | 63.8489 | 64.0457 | 1.3779 | -59.1614 | 63.826 | -59.0652 | -59.0973 | -58.9554 | 0.20599 | -59.2117 | 63.8443 | 63.7711 | -59.1156 | -59.2163 | -0.064087 | -0.09613 | -0.036621 | 123.0469 | -0.16022 | -0.064087 | -0.013733 | -0.11444 | -0.21515 | -0.018311 | 0.045777 | -0.21057 | 0.004578 | -0.091553 | 122.8271 | 122.85 | 60.379 | -122.9599 | 122.8455 | 122.7722 | 59.2072 | -123.0789
1035.5156 | 123.0698 | -59.0561 | 63.9542 | -0.19379 | 0.0098951 | 0.0678 | 0.068577 | 0.12592 | -0.00022865 | -0.0030013 | -0.10353 | -0.0054004 | -0.003168 | -0.0016044 | 0.002196 | -0.0051697 | 63.8031 | 63.9359 | 1.3229 | -59.198 | 63.8809 | -59.0744 | -59.1202 | -59.0332 | 0.086975 | -59.2941 | 63.9221 | 63.8031 | -59.1293 | -59.2438 | -0.018311 | -0.064087 | -0.073243 | 122.9919 | -0.14191 | -0.07782 | -0.15106 | -0.073242 | -0.18768 | -0.032044 | 0.022888 | -0.23804 | -0.050354 | -0.15106 | 122.937 | 122.8592 | 60.379 | -123.0743 | 122.9782 | 122.8592 | 59.1431 | -123.1979
1036.5156 | 123.1659 | -58.9828 | 63.8397 | -0.02594 | 0.0079723 | 0.065663 | 0.066227 | 0.12742 | -0.002792 | -0.0042831 | 0.18639 | -0.002196 | -0.0012454 | -0.0016044 | 5.9768e-05 | -0.0045289 | 63.8718 | 64.0778 | 1.442 | -59.1522 | 63.8397 | -59.0515 | -59.0836 | -58.9737 | 0.16022 | -59.198 | 63.8626 | 63.7711 | -59.0881 | -59.1843 | -0.068665 | -0.10071 | 0 | 123.0606 | -0.16937 | -0.068665 | 0.032043 | -0.10529 | -0.20142 | 0.022888 | 0.009155 | -0.21515 | -0.013733 | -0.068665 | 122.8226 | 122.8546 | 60.4248 | -122.9233 | 122.8455 | 122.7539 | 59.1431 | -123.024
1037.5156 | 123.1247 | -59.024 | 63.8992 | -0.18616 | 0.0077587 | 0.06844 | 0.068577 | 0.13126 | 0.00019875 | -0.0044967 | -0.12642 | -0.0049732 | -0.0021 | -0.0024588 | 5.9768e-05 | -0.0045289 | 63.8306 | 64.0228 | 1.4694 | -59.166 | 63.8351 | -59.0698 | -59.1156 | -58.9874 | 0.16022 | -59.2621 | 63.8901 | 63.7756 | -59.1202 | -59.2163 | -0.045776 | -0.091553 | -0.064087 | 123.0469 | -0.14191 | -0.050354 | -0.068665 | -0.09613 | -0.19226 | -0.009155 | 0.036621 | -0.23804 | -0.045776 | -0.1236 | 122.8592 | 122.8546 | 60.4935 | -123.0148 | 122.9141 | 122.7997 | 59.1843 | -123.1155
1038.5156 | 123.2025 | -58.992 | 63.858 | -0.018311 | 0.0060497 | 0.066304 | 0.066014 | 0.12913 | -0.00065585 | -0.0012923 | 0.071945 | -0.0043324 | -0.001459 | -0.0026724 | 0.00091437 | -0.0060243 | 63.8489 | 64.0274 | 1.5381 | -59.1751 | 63.8351 | -59.0561 | -59.1019 | -58.8913 | 0.16479 | -59.1934 | 63.826 | 63.7436 | -59.1248 | -59.2163 | -0.064087 | -0.10986 | -0.022888 | 123.0194 | -0.18311 | -0.073242 | -0.009155 | -0.13275 | -0.22431 | -0.032043 | 0.10071 | -0.20142 | 0.022889 | -0.11444 | 122.8271 | 122.8409 | 60.5301 | -122.9599 | 122.818 | 122.7356 | 59.1568 | -123.0743
1039.5156 | 123.1476 | -59.0057 | 63.8809 | -0.15564 | 0.0060497 | 0.069722 | 0.06815 | 0.12592 | -0.00022865 | -0.0023605 | -0.073013 | -0.0047596 | -0.0021 | -0.0005362 | 0.002837 | -0.0049561 | 63.8443 | 64.0411 | 1.5839 | -59.166 | 63.8306 | -59.0469 | -59.1248 | -58.9554 | 0.1831 | -59.23 | 63.8718 | 63.7573 | -59.1248 | -59.198 | -0.041199 | -0.11902 | -0.050354 | 123.0469 | -0.16022 | -0.041199 | -0.036621 | -0.11902 | -0.19226 | -0.009155 | 0.050354 | -0.2243 | -0.032044 | -0.1236 | 122.8363 | 122.85 | 60.5896 | -123.0057 | 122.8775 | 122.7631 | 59.1888 | -123.0789
1040.5156 | 123.1705 | -58.9966 | 63.8626 | 0.012207 | 0.0069043 | 0.069295 | 0.067723 | 0.12956 | -0.0021512 | -0.0030013 | 0.064316 | -0.0049732 | -0.0023136 | -0.001818 | 0.0026234 | -0.0043153 | 63.7939 | 63.9954 | 1.5793 | -59.1888 | 63.8306 | -59.0515 | -59.1522 | -58.9371 | 0.12817 | -59.2392 | 63.8397 | 63.739 | -59.1156 | -59.2163 | -0.054932 | -0.15564 | -0.032044 | 122.9919 | -0.19226 | -0.036621 | -0.068665 | -0.11902 | -0.21973 | -0.022888 | 0.059509 | -0.24262 | -0.022888 | -0.1236 | 122.8271 | 122.7905 | 60.5759 | -123.0148 | 122.8363 | 122.7356 | 59.1248 | -123.0789
1041.5156 | 123.1338 | -59.0515 | 63.8855 | -0.15564 | 0.0073315 | 0.069722 | 0.0705 | 0.13105 | 0.00083955 | -0.0027877 | -0.11879 | -0.0047596 | -0.0029544 | -0.001177 | 0.001128 | -0.0051697 | 63.8535 | 64.0274 | 1.6479 | -59.1751 | 63.8397 | -59.0561 | -59.111 | -58.96 | 0.17395 | -59.2529 | 63.8809 | 63.7527 | -59.1248 | -59.2026 | -0.004577 | -0.059509 | -0.045776 | 123.0789 | -0.1236 | -0.064087 | -0.032043 | -0.073242 | -0.15106 | -0.004578 | 0.091553 | -0.20142 | -0.050354 | -0.13275 | 122.8912 | 122.905 | 60.6995 | -122.9965 | 122.9324 | 122.8043 | 59.2255 | -123.0881
1042.5156 | 123.175 | -58.9874 | 63.858 | -0.048828 | 0.0081861 | 0.067586 | 0.069005 | 0.12956 | -0.0025784 | -0.0019333 | 0.0032804 | -0.006255 | -0.0042362 | -0.0007498 | 0.001128 | -0.0030335 | 63.8351 | 64.032 | 1.6891 | -59.1751 | 63.8489 | -59.0744 | -59.1202 | -58.9188 | 0.16937 | -59.1934 | 63.8489 | 63.7482 | -59.1202 | -59.2255 | -0.086975 | -0.13275 | -0.009155 | 123.0194 | -0.18768 | -0.054932 | -0.022888 | -0.13275 | -0.23804 | -0.009155 | 0.068665 | -0.20599 | 0.032044 | -0.10986 | 122.8363 | 122.8226 | 60.6766 | -122.9782 | 122.8363 | 122.7356 | 59.1568 | -123.0835
1043.5156 | 123.1476 | -59.024 | 63.858 | -0.14038 | 0.0062635 | 0.069081 | 0.068364 | 0.12998 | 0.0019078 | -0.0042831 | -0.095902 | -0.0054004 | -0.0025272 | -0.001177 | 0.0030506 | -0.0060243 | 63.8763 | 64.0411 | 1.7258 | -59.1614 | 63.8443 | -59.0424 | -59.0927 | -58.9508 | 0.19226 | -59.2209 | 63.8901 | 63.7756 | -59.1064 | -59.2209 | -0.01831 | -0.068664 | -0.013733 | 123.0652 | -0.13733 | -0.068665 | 0.018311 | -0.082397 | -0.19684 | 0.032044 | 0.073242 | -0.19684 | 0 | -0.082397 | 122.8683 | 122.9004 | 60.7498 | -122.9507 | 122.9141 | 122.7997 | 59.2163 | -123.0789
1044.5156 | 123.143 | -59.0149 | 63.8718 | 1.3016 | 0.0062635 | 0.068227 | 0.067296 | 0.12806 | -0.0030056 | -0.0040695 | 0.10246 | -0.0049732 | -0.0035952 | -0.0020316 | 0.0015552 | -0.0026063 | 63.7619 | 63.9359 | 1.6891 | -59.2209 | 63.8351 | -59.0927 | -59.1156 | -59.0012 | 0.059509 | -59.2667 | 63.8626 | 63.7344 | -59.1339 | -59.2117 | -0.077819 | -0.10071 | -0.036621 | 122.9507 | -0.20599 | -0.10529 | -0.10986 | -0.11902 | -0.19684 | -0.009155 | 0.013733 | -0.25177 | -0.054932 | -0.13733 | 122.85 | 122.7768 | 60.704 | -122.9874 | 122.8775 | 122.7493 | 59.0744 | -123.0835
1045.5156 | 123.1796 | -59.024 | 63.858 | -0.033569 | 0.0049817 | 0.06844 | 0.067936 | 0.12678 | -0.001083 | -0.0025741 | 0.01091 | -0.0049732 | -0.0010318 | -0.0016044 | 0.00027337 | -0.0058105 | 63.858 | 64.0366 | 1.8356 | -59.166 | 63.8123 | -59.0561 | -59.1293 | -58.905 | 0.16937 | -59.2026 | 63.858 | 63.7711 | -59.1064 | -59.1797 | -0.032043 | -0.10529 | -0.045776 | 123.0606 | -0.14191 | -0.036622 | 0 | -0.082397 | -0.15564 | 0 | 0.11902 | -0.17853 | -0.022889 | -0.086975 | 122.8363 | 122.8821 | 60.8597 | -122.9874 | 122.8821 | 122.7951 | 59.1934 | -123.0377
1046.5156 | 123.1842 | -59.0286 | 63.8443 | 0.035095 | 0.0047681 | 0.06844 | 0.070073 | 0.12678 | -0.0012966 | -0.0021469 | 0.13298 | -0.0054004 | -0.0012454 | -0.0007498 | 0.00091437 | -0.0034607 | 63.7802 | 63.9862 | 1.799 | -59.2117 | 63.826 | -59.0698 | -59.1339 | -58.9645 | 0.10529 | -59.2346 | 63.8535 | 63.7344 | -59.1476 | -59.2209 | -0.041199 | -0.10529 | -0.01831 | 123.0148 | -0.18311 | -0.07782 | -0.064087 | -0.11902 | -0.19226 | 0.009156 | 0.064086 | -0.20599 | -0.013733 | -0.10986 | 122.8546 | 122.8088 | 60.8276 | -122.9782 | 122.8821 | 122.7631 | 59.1339 | -123.0652
1047.5156 | 123.0972 | -59.0332 | 63.8718 | -0.13275 | 0.014595 | 0.067586 | 0.072636 | 0.1287 | 0.0044712 | -1.0724e-05 | -0.1722 | -0.003905 | -0.001459 | -0.001818 | 0.002196 | -0.0077331 | 63.8351 | 63.9267 | 1.8448 | -59.1934 | 63.8809 | -59.0698 | -59.1339 | -58.9737 | 0.10529 | -59.2987 | 63.8992 | 63.8031 | -59.1339 | -59.2346 | -0.036621 | -0.10071 | 0.009155 | 122.9599 | -0.16022 | -0.059509 | -0.036621 | -0.10071 | -0.20142 | 0.027466 | 0.059509 | -0.2655 | -0.064087 | -0.068664 | 122.9141 | 122.8683 | 60.878 | -123.0057 | 122.9324 | 122.8363 | 59.1385 | -123.1064
1048.5156 | 123.1705 | -59.0149 | 63.8489 | -0.010681 | 0.0062635 | 0.066731 | 0.067509 | 0.12956 | -0.0025784 | -0.0034287 | 0.094833 | -0.004546 | -0.0035952 | 0.000532 | -0.00079463 | -0.0047425 | 63.7985 | 63.9954 | 1.9226 | -59.1843 | 63.8443 | -59.0744 | -59.1202 | -58.96 | 0.1236 | -59.2072 | 63.8489 | 63.7619 | -59.111 | -59.1934 | -0.059509 | -0.10529 | -0.004578 | 123.0103 | -0.16937 | -0.064087 | -0.050354 | -0.09613 | -0.17853 | 0 | 0.054932 | -0.19226 | -0.013733 | -0.086975 | 122.8592 | 122.8134 | 60.9375 | -122.9691 | 122.8638 | 122.7768 | 59.1385 | -123.0423
1049.5156 | 123.1934 | -59.0286 | 63.8672 | -0.094604 | 0.0036999 | 0.068013 | 0.062596 | 0.12785 | -0.002792 | -0.0036423 | 0.041427 | -0.0030506 | -0.0023136 | -0.0013906 | 0.0017688 | -0.0053833 | 63.8763 | 63.9816 | 2.0096 | -59.1385 | 63.8031 | -59.0607 | -59.1019 | -58.9188 | 0.19684 | -59.198 | 63.8626 | 63.7482 | -59.1064 | -59.2117 | -0.032044 | -0.073243 | -0.064086 | 123.0103 | -0.10986 | -0.036621 | 0.009156 | -0.07782 | -0.18311 | -0.004577 | 0.10986 | -0.16937 | 0.013733 | -0.11902 | 122.8317 | 122.905 | 61.0382 | -122.9691 | 122.8912 | 122.7768 | 59.2255 | -123.0789
1050.5156 | 123.175 | -59.0286 | 63.8489 | 0.13428 | 0.0060497 | 0.066945 | 0.067296 | 0.12913 | -0.0015102 | -0.0021469 | 0.1635 | -0.0043324 | -0.0016726 | -0.0041678 | 0.0043324 | -0.0045289 | 63.7802 | 63.9771 | 1.9638 | -59.2255 | 63.8397 | -59.0515 | -59.1248 | -59.0607 | 0.050354 | -59.3033 | 63.8214 | 63.7253 | -59.1248 | -59.2209 | -0.022889 | -0.096131 | -0.009155 | 123.0057 | -0.19684 | -0.10071 | -0.068665 | -0.096131 | -0.19226 | -0.027466 | -0.032044 | -0.27466 | -0.082398 | -0.1236 | 122.8683 | 122.8088 | 60.9924 | -122.9736 | 122.85 | 122.7539 | 59.079 | -123.0698
1051.5156 | 123.1979 | -59.0195 | 63.8443 | -0.02594 | 0.0049817 | 0.066731 | 0.068791 | 0.12678 | -0.00065585 | -0.0021469 | -0.019608 | -0.0036914 | -0.0057316 | -0.0024588 | 0.00091437 | -0.0098695 | 63.858 | 64.064 | 2.1332 | -59.1522 | 63.8489 | -59.0332 | -59.0836 | -58.7357 | 0.2243 | -59.4131 | 63.8855 | 63.7482 | -59.1293 | -59.2163 | -0.013733 | -0.064087 | 0.004578 | 123.0835 | -0.13275 | -0.068665 | 0.013733 | -0.10986 | -0.19684 | 0.041199 | 0.28381 | -0.39368 | -0.19684 | -0.09613 | 122.8683 | 122.8775 | 61.1526 | -122.9279 | 122.905 | 122.7676 | 59.2438 | -123.0606
1052.5156 | 123.1155 | -59.0149 | 63.8947 | -0.18616 | 0.0094677 | 0.0678 | 0.069432 | 0.12956 | 0.001694 | -0.0032151 | -0.095902 | -0.0051868 | -0.0042362 | -0.0003226 | 0.00091437 | -0.0060243 | 63.8626 | 64.032 | 2.1286 | -59.1614 | 63.858 | -59.0515 | -59.0836 | -58.96 | 0.15106 | -59.2575 | 63.8947 | 63.7665 | -59.1293 | -59.2026 | -0.036621 | -0.068664 | -0.036621 | 123.0469 | -0.14648 | -0.07782 | -0.032043 | -0.11444 | -0.18768 | 0 | 0.054932 | -0.24261 | -0.054931 | -0.12817 | 122.8729 | 122.8775 | 61.1435 | -122.9782 | 122.9095 | 122.7814 | 59.166 | -123.0972
1053.5156 | 123.1888 | -59.0012 | 63.8489 | -0.0030518 | 0.0056225 | 0.071645 | 0.067936 | 0.12998 | -0.00086945 | -0.0034287 | 0.01091 | -0.005614 | -0.0042362 | -0.0005362 | 0.0034778 | -0.0058105 | 63.8443 | 64.032 | 2.1927 | -59.1797 | 63.8443 | -59.0561 | -59.1156 | -58.8913 | 0.16479 | -59.1888 | 63.8718 | 63.7299 | -59.0973 | -59.2026 | -0.054931 | -0.11444 | -0.004578 | 123.0331 | -0.17853 | -0.064086 | -0.004578 | -0.09613 | -0.20142 | 0.022888 | 0.10986 | -0.18768 | 0.013733 | -0.11902 | 122.8455 | 122.8455 | 61.1938 | -122.9645 | 122.8729 | 122.731 | 59.166 | -123.0515
1054.5156 | 123.1155 | -59.0195 | 63.858 | 0.17242 | 0.0083997 | 0.069081 | 0.066014 | 0.12763 | -0.0012966 | -0.0034287 | 0.15587 | -0.0036914 | -0.0046634 | -0.0024588 | -0.00079463 | -0.0075195 | 63.7939 | 63.9771 | 2.1515 | -59.2117 | 63.8306 | -59.0652 | -59.1385 | -58.8867 | 0.054932 | -59.3399 | 63.8626 | 63.7436 | -59.1248 | -59.2072 | -0.045777 | -0.11902 | -0.027466 | 122.9965 | -0.19226 | -0.073242 | -0.064087 | -0.10529 | -0.18768 | 0.004578 | 0.13275 | -0.32044 | -0.13275 | -0.11444 | 122.85 | 122.8134 | 61.171 | -122.9965 | 122.8821 | 122.7631 | 59.0744 | -123.0652
1055.5156 | 123.1842 | -58.9966 | 63.8351 | -0.13275 | 0.0056225 | 0.068227 | 0.070286 | 0.12678 | -0.0021512 | -0.0019333 | -0.019608 | -0.0043324 | -0.0042362 | -0.0030996 | 0.0019824 | -0.0053833 | 63.8809 | 64.0823 | 2.2934 | -59.1476 | 63.8351 | -59.0424 | -59.0927 | -58.7448 | 0.032043 | -59.3857 | 63.8855 | 63.7299 | -59.1064 | -59.23 | -0.045776 | -0.09613 | 0 | 123.0789 | -0.15106 | -0.054932 | 0.045776 | -0.10986 | -0.23346 | 0.050354 | 0.25177 | -0.3891 | -0.15564 | -0.10529 | 122.8317 | 122.8775 | 61.29 | -122.9279 | 122.8821 | 122.7264 | 59.0286 | -123.0652
1056.5156 | 123.1247 | -59.024 | 63.858 | 0.073242 | 0.0058361 | 0.066304 | 0.069005 | 0.12785 | 0.0010532 | -0.00065152 | 0.12535 | -0.005614 | -0.0033816 | -0.0026724 | 0.00048697 | -0.0064515 | 63.8168 | 63.9084 | 2.1973 | -59.2072 | 63.8306 | -59.0607 | -59.1293 | -58.9691 | 0.041199 | -59.2712 | 63.8489 | 63.7299 | -59.1522 | -59.2255 | -0.036621 | -0.10529 | -0.027466 | 122.9324 | -0.1831 | -0.07782 | -0.041199 | -0.12817 | -0.20142 | -0.009155 | 0.054932 | -0.24719 | -0.045776 | -0.12817 | 122.8546 | 122.8409 | 61.2213 | -122.9874 | 122.8729 | 122.7539 | 59.0652 | -123.0835
1057.5156 | 123.0606 | -59.0424 | 63.8672 | 0.042725 | 0.017158 | 0.065236 | 0.071995 | 0.1302 | 0.0055392 | 0.00020288 | -0.011978 | -0.0036914 | 0.00025 | -0.001818 | 0.003905 | -0.0092285 | 63.8397 | 63.9175 | 2.243 | -59.23 | 63.8626 | -59.0744 | -59.1476 | -59.0103 | 0.022888 | -59.3491 | 63.913 | 63.7665 | -59.1385 | -59.2529 | -0.032044 | -0.10529 | -0.004577 | 122.9599 | -0.18768 | -0.082398 | -0.027465 | -0.096131 | -0.21057 | 0.045777 | 0.032043 | -0.3067 | -0.09613 | -0.10071 | 122.905 | 122.8821 | 61.2854 | -123.0148 | 122.9553 | 122.8088 | 59.0652 | -123.1201
1058.5156 | 123.1247 | -59.0286 | 63.8306 | 0.14954 | 0.010322 | 0.067586 | 0.068364 | 0.12806 | -0.00086945 | -0.0019333 | 0.26268 | -0.0036914 | 0.0004636 | -0.0020316 | 0.001128 | -0.0055969 | 63.8123 | 63.9999 | 2.3575 | -59.2163 | 63.7985 | -59.0744 | -59.1385 | -58.9508 | 0.054932 | -59.2667 | 63.8397 | 63.7482 | -59.1156 | -59.23 | -0.045777 | -0.10986 | -0.032043 | 123.0286 | -0.18768 | -0.07782 | -0.01831 | -0.086976 | -0.20142 | 0.009156 | 0.077819 | -0.23804 | -0.036621 | -0.082397 | 122.8271 | 122.8409 | 61.3861 | -122.9691 | 122.8683 | 122.7768 | 59.0836 | -123.0606
1059.5156 | 123.1476 | -59.0012 | 63.8763 | -0.02594 | 0.0045545 | 0.066518 | 0.069005 | 0.12657 | -0.0036464 | -0.00086512 | 0.11009 | -0.0030506 | -0.0029544 | -0.002886 | 0.0019824 | -0.0053833 | 63.826 | 63.9862 | 2.3712 | -59.1888 | 63.8443 | -59.0836 | -59.0881 | -58.9325 | 0.11902 | -59.2117 | 63.858 | 63.7711 | -59.0973 | -59.2026 | -0.082397 | -0.086975 | -0.032044 | 122.9874 | -0.18768 | -0.10071 | -0.050354 | -0.09613 | -0.20142 | -0.018311 | 0.068665 | -0.21057 | -0.009155 | -0.10529 | 122.8455 | 122.8271 | 61.3724 | -122.9645 | 122.8592 | 122.7722 | 59.1202 | -123.0789
1060.5156 | 123.1476 | -58.992 | 63.8443 | 0.20294 | 0.0092541 | 0.067586 | 0.066868 | 0.12699 | 0.00019875 | -0.0027877 | 0.22453 | -0.0024096 | -0.0025272 | -0.0013906 | 0.0024096 | -0.0019653 | 63.8077 | 63.9816 | 2.417 | -59.23 | 63.8031 | -59.0652 | -59.1202 | -58.9645 | 0.022888 | -59.2575 | 63.8535 | 63.7253 | -59.1202 | -59.2255 | -0.073243 | -0.12817 | -0.041198 | 122.9736 | -0.23804 | -0.10986 | -0.036621 | -0.12817 | -0.23346 | 0.009156 | 0.027465 | -0.2655 | -0.032043 | -0.11902 | 122.7951 | 122.7997 | 61.409 | -122.9645 | 122.8455 | 122.7173 | 59.0149 | -123.0698
1061.5156 | 123.1522 | -59.0149 | 63.8489 | 0.042725 | 0.0064771 | 0.070577 | 0.067082 | 0.12614 | -0.0023648 | -0.0030013 | 0.10246 | -0.0054004 | -0.0044498 | -0.0003226 | 0.0015552 | -0.0055969 | 63.7985 | 63.9679 | 2.4445 | -59.198 | 63.8351 | -59.0469 | -59.111 | -58.9508 | 0.064087 | -59.2484 | 63.8489 | 63.7573 | -59.1248 | -59.198 | -0.032043 | -0.09613 | -0.013733 | 122.9828 | -0.1831 | -0.086975 | -0.050354 | -0.10986 | -0.1831 | 0 | 0.064087 | -0.23346 | -0.050354 | -0.091553 | 122.85 | 122.8134 | 61.4594 | -122.9599 | 122.8638 | 122.7722 | 59.079 | -123.0469
1062.5156 | 123.056 | -59.0515 | 63.913 | -0.19379 | 0.0098951 | 0.066304 | 0.071141 | 0.12849 | 0.0012668 | 0.00084388 | -0.19508 | -0.0049732 | 0.0004636 | 0.0003182 | 0.0058276 | -0.0066651 | 63.7985 | 63.9313 | 2.4399 | -59.2255 | 63.8992 | -59.0744 | -59.1248 | -59.0561 | 0.10529 | -59.3353 | 63.9175 | 63.8077 | -59.1522 | -59.2072 | -0.022888 | -0.073242 | -0.013733 | 122.9828 | -0.17395 | -0.10071 | -0.11444 | -0.10071 | -0.15564 | 0.004578 | -0.004577 | -0.28381 | -0.12817 | -0.10529 | 122.9507 | 122.85 | 61.4914 | -123.0377 | 122.9691 | 122.8592 | 59.1568 | -123.1201
1063.5156 | 123.175 | -59.0149 | 63.8672 | 0.050354 | 0.0058361 | 0.069509 | 0.066441 | 0.12806 | -0.001083 | -0.0017197 | 0.064316 | -0.0071094 | -0.0055178 | -0.0020316 | 0.0019824 | -0.0036743 | 63.7985 | 64.0091 | 2.5085 | -59.1888 | 63.858 | -59.0836 | -59.111 | -58.9371 | 0.09613 | -59.2346 | 63.8718 | 63.7573 | -59.1202 | -59.2072 | -0.068664 | -0.09613 | -0.009155 | 123.024 | -0.17395 | -0.07782 | -0.068664 | -0.10529 | -0.19226 | 0.004578 | 0.07782 | -0.21973 | -0.027466 | -0.10986 | 122.8729 | 122.8134 | 61.5234 | -122.9782 | 122.8867 | 122.7722 | 59.111 | -123.0743
1064.5156 | 123.175 | -59.024 | 63.8123 | 0.22583 | 0.011818 | 0.066731 | 0.068577 | 0.12785 | 0.00041235 | -0.0015061 | 0.28557 | -0.005614 | -0.0008182 | -0.0026724 | 0.0026234 | -0.0058105 | 63.8489 | 63.9954 | 2.5497 | -59.1934 | 63.8031 | -59.0698 | -59.1248 | -58.9279 | 0.045776 | -59.2255 | 63.8397 | 63.739 | -59.1339 | -59.2163 | -0.045776 | -0.10071 | -0.009155 | 123.0194 | -0.16937 | -0.068664 | 0.036621 | -0.10986 | -0.19226 | 0.027466 | 0.096131 | -0.20142 | -0.009155 | -0.073242 | 122.8271 | 122.8729 | 61.5738 | -122.937 | 122.8638 | 122.7631 | 59.0698 | -123.0286
1065.5156 | 123.1338 | -59.0332 | 63.8672 | -0.38452 | 0.0094677 | 0.069081 | 0.065587 | 0.12934 | -0.0012966 | -0.0034287 | 0.13298 | -0.0054004 | -0.0038088 | -0.003527 | 0.0015552 | -0.0045289 | 63.7939 | 63.9496 | 2.5314 | -59.1934 | 63.858 | -59.0607 | -59.1202 | -58.9691 | 0.022888 | -59.2346 | 63.8809 | 63.7665 | -59.1156 | -59.2117 | -0.027466 | -0.086975 | -0.009155 | 122.9828 | -0.16022 | -0.073242 | -0.073242 | -0.082398 | -0.17853 | 0.013733 | 0.064087 | -0.20142 | -0.022888 | -0.10071 | 122.8912 | 122.8271 | 61.5646 | -122.9874 | 122.9141 | 122.7997 | 59.0561 | -123.0789
1066.5156 | 123.1796 | -59.0378 | 63.8214 | 0.17242 | 0.0098951 | 0.065663 | 0.067509 | 0.1287 | 0.0025486 | -0.0019333 | 0.25505 | -0.003905 | -0.0021 | -0.0024588 | 0.0041186 | -0.0049561 | 63.8214 | 63.9954 | 2.5818 | -59.1843 | 63.8031 | -59.0698 | -59.1156 | -58.9371 | 0.027466 | -59.23 | 63.8351 | 63.7253 | -59.1339 | -59.2026 | -0.032043 | -0.07782 | -0.01831 | 123.0331 | -0.14648 | -0.068664 | 0 | -0.09613 | -0.16479 | 0.013733 | 0.10071 | -0.19226 | -0.027466 | -0.09613 | 122.8409 | 122.8592 | 61.6196 | -122.937 | 122.8729 | 122.7631 | 59.0652 | -123.024
1067.5156 | 123.1522 | -59.0286 | 63.8535 | 0.11902 | 0.0079723 | 0.069509 | 0.065587 | 0.12934 | -0.00086945 | -0.0019333 | 0.14824 | -0.0041186 | -0.001459 | -0.001818 | 0.00027337 | -0.0047425 | 63.8123 | 63.9542 | 2.5909 | -59.2209 | 63.8123 | -59.0469 | -59.0927 | -58.9691 | 0.013733 | -59.2484 | 63.8626 | 63.7802 | -59.0881 | -59.1797 | -0.018311 | -0.064087 | -0.041199 | 122.9828 | -0.19226 | -0.12817 | -0.041199 | -0.05951 | -0.15106 | 0.009155 | 0.059509 | -0.21973 | -0.068665 | -0.073243 | 122.8409 | 122.8409 | 61.6196 | -122.9462 | 122.8912 | 122.8088 | 59.0424 | -123.0331
1068.5156 | 123.1842 | -59.024 | 63.8443 | 0.18768 | 0.013527 | 0.066091 | 0.069645 | 0.12977 | 0.001694 | -0.0010787 | 0.46104 | -0.004546 | -0.0006046 | -0.0007498 | 0.0049732 | -0.0066651 | 63.8626 | 63.9954 | 2.6138 | -59.2117 | 63.8031 | -59.1064 | -59.1522 | -58.9188 | 0.064087 | -59.2484 | 63.8397 | 63.7253 | -59.1522 | -59.23 | -0.082397 | -0.12817 | -0.041198 | 123.0194 | -0.18768 | -0.059509 | 0.018311 | -0.12817 | -0.20599 | -0.004577 | 0.10529 | -0.2243 | -0.01831 | -0.11902 | 122.8271 | 122.8867 | 61.6379 | -122.9965 | 122.8638 | 122.7493 | 59.0881 | -123.0743
1069.5156 | 123.1338 | -59.0012 | 63.8489 | 0.13428 | 0.0069043 | 0.068654 | 0.067509 | 0.12699 | -0.0025784 | -0.00043792 | 0.1635 | -0.004546 | -0.0063724 | -0.0009634 | 0.0032642 | -0.0051697 | 63.7985 | 63.9587 | 2.6184 | -59.1888 | 63.8626 | -59.0561 | -59.1202 | -58.9783 | -0.022888 | -59.2941 | 63.858 | 63.7665 | -59.1293 | -59.23 | -0.054931 | -0.11902 | 0.013733 | 122.9599 | -0.18768 | -0.068665 | -0.050354 | -0.12817 | -0.22888 | 0.009155 | 0.022889 | -0.29297 | -0.064086 | -0.082398 | 122.8638 | 122.7997 | 61.6196 | -122.9691 | 122.8592 | 122.7676 | 58.9783 | -123.0789
1070.5156 | 123.1659 | -59.024 | 63.8306 | 0.21057 | 0.0098951 | 0.067372 | 0.070073 | 0.13084 | 0.0014804 | -1.0724e-05 | 0.094833 | -0.004546 | -0.0008182 | -0.0024588 | 0.003905 | -0.0062379 | 63.9679 | 64.0594 | 2.7008 | -59.1614 | 63.826 | -59.0607 | -59.0927 | -58.9233 | 0.032043 | -59.2392 | 63.8535 | 63.707 | -59.1248 | -59.1888 | -0.036621 | -0.068664 | -0.004577 | 123.0835 | -0.13733 | -0.068665 | 0.13733 | -0.10071 | -0.16479 | 0.022889 | 0.10071 | -0.21515 | -0.050354 | -0.1236 | 122.85 | 122.9919 | 61.7249 | -122.9233 | 122.8775 | 122.731 | 59.0561 | -123.0194
1071.5156 | 123.1934 | -59.024 | 63.8306 | 0.20294 | 0.0092541 | 0.065236 | 0.06815 | 0.12742 | -0.001083 | -0.0023605 | 0.20164 | -0.0058276 | -0.0040226 | -0.0005362 | 0.0024096 | -0.0043153 | 63.8397 | 63.9908 | 2.7283 | -59.1934 | 63.8214 | -59.0652 | -59.0973 | -58.9142 | 0 | -59.23 | 63.8306 | 63.7299 | -59.1385 | -59.23 | -0.041199 | -0.073242 | -0.009155 | 123.0148 | -0.16937 | -0.09613 | 0.009156 | -0.11444 | -0.20599 | 0 | 0.10986 | -0.20599 | 0 | -0.10071 | 122.8455 | 122.8638 | 61.7523 | -122.9279 | 122.8546 | 122.7539 | 59.024 | -123.0606
1072.5156 | 123.1018 | -59.0469 | 63.858 | 0.14954 | 0.014168 | 0.067586 | 0.069859 | 0.13126 | 0.0027622 | -0.0010787 | 0.18639 | -0.0015552 | -0.0010318 | 0.000532 | 0.0064686 | -0.0049561 | 63.7985 | 63.8718 | 2.6093 | -59.23 | 63.8718 | -59.0698 | -59.1248 | -59.0012 | -0.082397 | -59.3124 | 63.8763 | 63.7756 | -59.1248 | -59.23 | -0.022888 | -0.07782 | 0.013733 | 122.9187 | -0.18311 | -0.10529 | -0.059509 | -0.07782 | -0.18311 | 0.018311 | 0.045776 | -0.2655 | -0.082397 | -0.082397 | 122.9187 | 122.8455 | 61.6562 | -122.9828 | 122.9233 | 122.8226 | 58.9645 | -123.0881
1073.5156 | 123.1293 | -59.0057 | 63.8443 | 0.15717 | 0.0075451 | 0.067586 | 0.066014 | 0.12956 | -1.505e-05 | -0.00065152 | 0.25505 | -0.0049732 | -0.0018862 | 0.0003182 | 0.0024096 | -0.0034607 | 63.8443 | 64.0091 | 2.7969 | -59.1797 | 63.8306 | -59.0515 | -59.1064 | -58.9417 | 0.004578 | -59.2484 | 63.8535 | 63.7299 | -59.1293 | -59.2026 | -0.045777 | -0.10071 | -0.013733 | 123.0148 | -0.17395 | -0.073242 | 0 | -0.1236 | -0.19684 | 0.009156 | 0.064087 | -0.24261 | -0.045776 | -0.11444 | 122.8363 | 122.85 | 61.8027 | -122.9507 | 122.8592 | 122.7356 | 59.0103 | -123.0469
1074.5156 | 123.1293 | -59.0515 | 63.8351 | 0.17242 | 0.012031 | 0.068227 | 0.067509 | 0.13084 | 0.0019078 | -0.0019333 | 0.20164 | -0.002196 | -0.0018862 | -0.0022452 | 0.0032642 | -0.0053833 | 63.7802 | 63.8992 | 2.7008 | -59.2392 | 63.9038 | -59.0561 | -59.1293 | -58.9783 | -0.068665 | -59.2804 | 63.8763 | 63.739 | -59.1522 | -59.23 | -0.004577 | -0.077819 | 0.068665 | 122.9507 | -0.18768 | -0.10986 | -0.054932 | -0.10071 | -0.17853 | 0.041199 | 0.073243 | -0.22888 | -0.050354 | -0.09613 | 122.9553 | 122.8317 | 61.7523 | -122.9645 | 122.9279 | 122.7905 | 58.9828 | -123.0652
1075.5156 | 123.1476 | -59.024 | 63.8214 | 0.10376 | 0.011604 | 0.066518 | 0.069432 | 0.12635 | -0.0015102 | -0.0030013 | 0.27031 | -0.004546 | -0.0033816 | -0.0016044 | 0.003905 | -0.0051697 | 63.8306 | 64.0091 | 2.8427 | -59.1705 | 63.8077 | -59.0561 | -59.1019 | -58.9325 | 0 | -59.2072 | 63.8489 | 63.739 | -59.1202 | -59.1934 | -0.032043 | -0.07782 | -0.013733 | 123.0331 | -0.14648 | -0.068664 | 0.009155 | -0.09613 | -0.16937 | 0.027466 | 0.091553 | -0.1831 | -0.013733 | -0.082397 | 122.8317 | 122.8546 | 61.8668 | -122.9233 | 122.8729 | 122.7631 | 59.024 | -123.0148
1076.5156 | 123.175 | -59.0103 | 63.8351 | 0.22583 | 0.013099 | 0.066731 | 0.069432 | 0.12699 | 0.00062595 | -0.0015061 | 0.20164 | -0.0030506 | -0.0029544 | -0.0030996 | 0.0019824 | -0.0045289 | 63.8168 | 63.9313 | 2.7695 | -59.2209 | 63.8351 | -59.0698 | -59.1019 | -58.9508 | -0.004578 | -59.2438 | 63.8763 | 63.7527 | -59.1339 | -59.2163 | -0.059509 | -0.091553 | 0 | 122.9416 | -0.21057 | -0.11902 | -0.018311 | -0.1236 | -0.20599 | 0.041199 | 0.059509 | -0.23346 | -0.027465 | -0.082397 | 122.8455 | 122.8271 | 61.7798 | -122.937 | 122.8867 | 122.7631 | 59.0057 | -123.0515
1077.5156 | 123.1293 | -59.024 | 63.8214 | 0.18005 | 0.0077587 | 0.066518 | 0.069645 | 0.12849 | -0.00022865 | -0.0012923 | 0.30083 | -0.0019824 | -0.0033816 | -0.0009634 | 0.002837 | -0.0032471 | 63.8397 | 63.9954 | 2.8748 | -59.1843 | 63.826 | -59.0698 | -59.1019 | -58.9325 | -0.022888 | -59.2255 | 63.8351 | 63.7619 | -59.1156 | -59.2255 | -0.045776 | -0.07782 | 0.004578 | 123.0194 | -0.16022 | -0.082397 | 0.018311 | -0.091553 | -0.20142 | 0.013733 | 0.091553 | -0.20142 | 0 | -0.059509 | 122.85 | 122.8638 | 61.8988 | -122.9233 | 122.8592 | 122.7859 | 59.0012 | -123.0469
1078.5156 | 123.0789 | -59.079 | 63.8809 | 0.11902 | 0.014381 | 0.0678 | 0.070286 | 0.12785 | 0.0044712 | -0.00043792 | 0.15587 | -0.0049732 | -0.001459 | -0.0013906 | 0.0036914 | -0.0043153 | 63.7619 | 63.8672 | 2.7557 | -59.2392 | 63.9084 | -59.0607 | -59.1339 | -59.024 | -0.1236 | -59.3353 | 63.913 | 63.8031 | -59.1431 | -59.2163 | 0.01831 | -0.054932 | 0.027466 | 122.9462 | -0.16022 | -0.10529 | -0.11902 | -0.064087 | -0.13733 | 0.032044 | 0.054931 | -0.25635 | -0.11902 | -0.077819 | 122.9874 | 122.8409 | 61.8347 | -123.0148 | 122.9919 | 122.8821 | 58.9554 | -123.0972
1079.5156 | 123.1567 | -59.0103 | 63.8306 | 0.19531 | 0.011818 | 0.065022 | 0.071568 | 0.13148 | -1.505e-05 | -0.0012923 | 0.24742 | -0.0030506 | -0.0012454 | -0.003527 | 0.0034778 | -0.0058105 | 63.8168 | 63.9999 | 2.861 | -59.1705 | 63.8123 | -59.0881 | -59.1064 | -58.9233 | -0.027466 | -59.3262 | 63.7985 | 63.7527 | -59.1751 | -59.23 | -0.07782 | -0.09613 | -0.01831 | 123.0103 | -0.16022 | -0.064087 | -0.013733 | -0.16479 | -0.21973 | -0.032043 | 0.086975 | -0.31586 | -0.09613 | -0.077819 | 122.8226 | 122.8271 | 61.8713 | -122.937 | 122.8088 | 122.7631 | 58.9828 | -123.0606
1080.5156 | 123.0972 | -59.0424 | 63.858 | 0.16479 | 0.014595 | 0.068868 | 0.071141 | 0.12678 | 0.0027622 | -0.00043792 | 0.23979 | -0.001128 | 0.00025 | -0.0026724 | 0.0032642 | -0.0038879 | 63.7848 | 63.8763 | 2.8152 | -59.23 | 63.8626 | -59.079 | -59.1476 | -59.0012 | -0.1236 | -59.2987 | 63.858 | 63.7894 | -59.1293 | -59.2209 | -0.036621 | -0.10529 | 0.004578 | 122.9187 | -0.18768 | -0.082398 | -0.073242 | -0.086975 | -0.17853 | 0 | 0.041198 | -0.25635 | -0.07782 | -0.068664 | 122.905 | 122.8271 | 61.8576 | -123.0057 | 122.9004 | 122.8317 | 58.9188 | -123.0789
1081.5156 | 123.1705 | -58.992 | 63.8397 | 0.21057 | 0.012672 | 0.067159 | 0.064518 | 0.12763 | -0.0019376 | 0.00020288 | 0.43053 | -0.0041186 | -0.0021 | -0.0009634 | 0.0041186 | -0.0055969 | 63.9084 | 63.9816 | 2.9251 | -59.1476 | 63.826 | -59.0378 | -59.1064 | -58.9142 | -0.032043 | -59.2163 | 63.8443 | 63.7527 | -59.1248 | -59.1888 | -0.045777 | -0.11444 | -0.013733 | 122.9736 | -0.15564 | -0.041199 | 0.068664 | -0.13275 | -0.19684 | 0.004577 | 0.077819 | -0.22431 | -0.027466 | -0.086975 | 122.818 | 122.9004 | 61.9171 | -122.9462 | 122.8363 | 122.7448 | 58.96 | -123.0286
1082.5156 | 123.0881 | -59.0332 | 63.8535 | 0.18768 | 0.015877 | 0.0678 | 0.070073 | 0.12592 | 0.001694 | -0.0017197 | 0.2169 | -0.0034778 | -0.0008182 | 0.0009592 | 0.0026234 | -0.0066651 | 63.7848 | 63.858 | 2.8107 | -59.2392 | 63.8992 | -59.0378 | -59.1202 | -59.0103 | -0.16022 | -59.3033 | 63.9084 | 63.8214 | -59.1431 | -59.2346 | -0.004578 | -0.086975 | 0.045776 | 122.8912 | -0.20599 | -0.11902 | -0.068665 | -0.10986 | -0.20142 | 0.054931 | 0.022888 | -0.27008 | -0.068665 | -0.032044 | 122.9324 | 122.818 | 61.8439 | -122.9736 | 122.9416 | 122.8546 | 58.873 | -123.0881
1083.5156 | 123.1842 | -58.9966 | 63.8351 | 0.15717 | 0.010322 | 0.068227 | 0.068364 | 0.12934 | -0.0017238 | -0.0027877 | 0.30846 | -0.0054004 | -0.0033816 | -0.0033134 | 0.002196 | -0.0036743 | 63.8351 | 63.9954 | 2.9617 | -59.1705 | 63.8306 | -59.0652 | -59.0836 | -58.9233 | -0.022888 | -59.2163 | 63.8672 | 63.7573 | -59.1202 | -59.2072 | -0.068665 | -0.086975 | -0.004578 | 122.9919 | -0.17395 | -0.086975 | 0 | -0.1236 | -0.21057 | 0.032043 | 0.073242 | -0.21973 | -0.009156 | -0.07782 | 122.8271 | 122.8317 | 61.9583 | -122.9187 | 122.8638 | 122.7539 | 58.9737 | -123.0423
1084.5156 | 123.1155 | -59.0424 | 63.858 | 0.21057 | 0.013099 | 0.067159 | 0.072423 | 0.12806 | 0.0014804 | -0.0047103 | 0.25505 | -0.0036914 | 0.0004636 | -0.0024588 | 0.001128 | -0.0051697 | 63.7985 | 63.8809 | 2.8793 | -59.2255 | 63.8763 | -59.079 | -59.1202 | -58.992 | -0.14191 | -59.2804 | 63.8763 | 63.8031 | -59.1156 | -59.198 | -0.036621 | -0.07782 | 0.018311 | 122.9233 | -0.18311 | -0.10529 | -0.059509 | -0.073243 | -0.15564 | 0.018311 | 0.050354 | -0.23804 | -0.082398 | -0.054931 | 122.9187 | 122.8409 | 61.9217 | -122.9782 | 122.9187 | 122.8455 | 58.9005 | -123.056
1085.5156 | 123.1796 | -59.0012 | 63.8535 | 0.19531 | 0.011818 | 0.068868 | 0.067082 | 0.12678 | 0.0019078 | -0.00043792 | 0.25505 | -0.0024096 | -0.0040226 | -0.0009634 | 0.0017688 | -0.0055969 | 63.8214 | 63.9496 | 2.9388 | -59.1843 | 63.8626 | -59.0515 | -59.1293 | -58.9233 | -0.068665 | -59.23 | 63.858 | 63.7894 | -59.1202 | -59.2163 | -0.050354 | -0.12817 | 0.009155 | 122.9507 | -0.18311 | -0.054932 | -0.032044 | -0.11902 | -0.21515 | 0.004577 | 0.07782 | -0.22888 | -0.013733 | -0.064087 | 122.8638 | 122.8226 | 61.94 | -122.9828 | 122.8592 | 122.7905 | 58.9325 | -123.0698
1086.5156 | 123.0331 | -59.0515 | 63.8855 | 0.065613 | 0.015877 | 0.068013 | 0.069859 | 0.12892 | 0.0010532 | -1.0724e-05 | -3.079 | -0.0026234 | 3.6404e-05 | -0.0009634 | 0.0019824 | -0.0038879 | 63.7756 | 63.8489 | 2.8656 | -59.2163 | 63.913 | -59.0607 | -59.1156 | -59.0149 | -0.1831 | -59.3124 | 63.9084 | 63.858 | -59.111 | -59.2255 | -0.009155 | -0.064087 | 0.027466 | 122.9004 | -0.1648 | -0.10071 | -0.10986 | -0.059509 | -0.17395 | 0.022888 | 0.036621 | -0.26093 | -0.086975 | -0.027466 | 122.9645 | 122.8271 | 61.9171 | -123.0011 | 122.9599 | 122.9095 | 58.8684 | -123.111
1087.5156 | 123.1659 | -59.0057 | 63.8626 | 0.13428 | 0.011177 | 0.0678 | 0.0658 | 0.1287 | -0.0021512 | -1.0724e-05 | -0.18745 | -0.005614 | -0.0018862 | -0.0037406 | 0.002196 | -0.0064515 | 63.8763 | 63.9816 | 3.0487 | -59.1431 | 63.858 | -59.0378 | -59.0836 | -58.9233 | -0.064087 | -59.2072 | 63.8901 | 63.7939 | -59.079 | -59.1751 | -0.032044 | -0.07782 | -0.004578 | 122.9874 | -0.13733 | -0.059509 | 0.013733 | -0.073242 | -0.16937 | 0.027466 | 0.082397 | -0.20142 | -0.032043 | -0.068665 | 122.8638 | 122.8821 | 62.0544 | -122.9462 | 122.8958 | 122.7997 | 58.9417 | -123.0377
1088.5156 | 123.056 | -59.0698 | 63.8947 | -0.6897 | 0.012672 | 0.066091 | 0.068364 | 0.1302 | 0.0010532 | -0.0032151 | 0.14061 | -0.0024096 | -0.0018862 | -0.0030996 | 0.003905 | -0.0060243 | 63.7665 | 63.8672 | 2.9297 | -59.198 | 63.8947 | -59.0607 | -59.1019 | -59.0103 | -0.19226 | -59.3353 | 63.9313 | 63.826 | -59.1248 | -59.2484 | 0.009155 | -0.032044 | 0 | 122.937 | -0.12817 | -0.09613 | -0.12817 | -0.054932 | -0.17853 | 0.036621 | 0.059509 | -0.2655 | -0.086975 | -0.068664 | 122.9645 | 122.8363 | 61.9995 | -122.9965 | 123.0011 | 122.8958 | 58.8776 | -123.143
1089.5156 | 123.1613 | -58.992 | 63.8443 | 0.37842 | 0.0062635 | 0.065877 | 0.067082 | 0.12956 | -0.0030056 | -0.00086512 | 0.33134 | -0.0034778 | -0.003168 | -0.001818 | 0.0034778 | -0.0038879 | 63.8763 | 63.9954 | 3.0396 | -59.1339 | 63.8351 | -59.0195 | -59.0698 | -58.9279 | -0.082397 | -59.1934 | 63.8718 | 63.7939 | -59.111 | -59.198 | -0.027466 | -0.07782 | -0.009155 | 122.9874 | -0.14191 | -0.064087 | 0.032044 | -0.11902 | -0.20599 | 0.027466 | 0.064087 | -0.20142 | 0.004578 | -0.050354 | 122.8271 | 122.8683 | 62.0316 | -122.9141 | 122.8638 | 122.7859 | 58.9096 | -123.0423
1090.5156 | 123.1064 | -59.0195 | 63.8809 | 0.16479 | 0.013099 | 0.068654 | 0.0705 | 0.12699 | 0.0031894 | -0.0025741 | 0.26268 | -0.0024096 | 0.00025 | -0.0024588 | 0.003905 | -0.0043153 | 63.8031 | 63.8901 | 2.9526 | -59.2072 | 63.8992 | -59.0607 | -59.1064 | -58.9783 | -0.21057 | -59.2804 | 63.9084 | 63.858 | -59.1156 | -59.2026 | -0.041199 | -0.086975 | 0.018311 | 122.9095 | -0.18768 | -0.10071 | -0.077819 | -0.096131 | -0.18311 | 0.027466 | 0.041199 | -0.26093 | -0.07782 | -0.022888 | 122.9187 | 122.8226 | 61.972 | -122.9874 | 122.9279 | 122.8775 | 58.8089 | -123.0835
1091.5156 | 123.1705 | -58.992 | 63.8947 | 0.22583 | 0.012031 | 0.065663 | 0.066655 | 0.12785 | 0.00019875 | -0.00065152 | -0.95039 | -0.0047596 | -0.0010318 | -0.0009634 | 0.0030506 | -0.0062379 | 63.8763 | 63.9908 | 3.0762 | -59.1385 | 63.8672 | -59.0424 | -59.0836 | -58.8959 | -0.10529 | -59.1705 | 63.8809 | 63.8123 | -59.0652 | -59.1797 | -0.050354 | -0.091553 | -0.027466 | 122.9828 | -0.14648 | -0.054932 | -0.01831 | -0.073243 | -0.18768 | -0.013733 | 0.09613 | -0.17853 | 0.009155 | -0.082397 | 122.8592 | 122.8683 | 62.0682 | -122.9782 | 122.8729 | 122.8043 | 58.8867 | -123.0743
1092.5156 | 122.8683 | -59.0698 | 63.8901 | 0.09613 | 0.014381 | 0.068013 | 0.066655 | 0.12763 | 0.002335 | -0.0012923 | 0.087204 | -0.002837 | -0.0042362 | -0.002886 | 0.0036914 | -0.0051697 | 63.8077 | 63.8992 | 2.9663 | -59.2026 | 63.9038 | -59.0652 | -59.0836 | -59.0332 | -0.2243 | -59.3308 | 63.9587 | 63.8763 | -59.1156 | -59.2255 | 0.004577 | -0.013733 | 0.013733 | 122.9691 | -0.13275 | -0.11902 | -0.082398 | -0.045777 | -0.15564 | 0.068664 | 0.036621 | -0.26093 | -0.10529 | -0.013733 | 122.9736 | 122.8775 | 62.0361 | -122.9736 | 123.0286 | 122.9462 | 58.8455 | -123.1155
1093.5156 | 123.175 | -59.0012 | 63.8306 | 0.25635 | 0.012031 | 0.069081 | 0.068577 | 0.13105 | -0.0012966 | -0.0023605 | 0.28557 | -0.0047596 | -0.0044498 | -0.0022452 | 0.0041186 | -0.0034607 | 63.8855 | 63.9725 | 3.0487 | -59.1476 | 63.8672 | -59.0286 | -59.079 | -58.9096 | -0.14648 | -59.2026 | 63.8901 | 63.8031 | -59.1064 | -59.1888 | -0.027465 | -0.077819 | 0.036621 | 122.9736 | -0.14648 | -0.068665 | 0.054932 | -0.10529 | -0.18768 | 0.05951 | 0.091553 | -0.20142 | -0.013733 | -0.027465 | 122.8683 | 122.8867 | 62.0499 | -122.9095 | 122.8912 | 122.8043 | 58.8547 | -123.0194
1094.5156 | 123.0789 | -59.024 | 63.9359 | 0.11902 | 0.013527 | 0.066731 | 0.071568 | 0.12913 | 0.0031894 | 0.00020288 | 1.2087 | -0.002837 | -0.0008182 | -0.001818 | 0.004546 | -0.0062379 | 63.7985 | 63.8626 | 2.9984 | -59.3308 | 63.8855 | -59.0607 | -59.1156 | -58.9783 | -0.2243 | -59.3216 | 63.9496 | 63.8901 | -59.1064 | -59.1797 | -0.036621 | -0.091553 | -0.050354 | 122.8867 | -0.3067 | -0.21515 | -0.13733 | -0.082397 | -0.15564 | 0.013733 | 0.045777 | -0.29755 | -0.14191 | -0.045776 | 122.9095 | 122.8226 | 62.0224 | -123.0515 | 122.9736 | 122.9141 | 58.7997 | -123.1155
1095.5156 | 123.1384 | -59.0012 | 63.8718 | 0.20294 | 0.011604 | 0.066731 | 0.069432 | 0.12635 | -0.0032192 | -0.0023605 | 0.30083 | -0.0030506 | -0.0006046 | -0.0024588 | 0.0041186 | -0.0036743 | 63.8306 | 63.9359 | 3.0579 | -59.1797 | 63.913 | -59.0378 | -59.0927 | -58.9142 | -0.19684 | -59.2117 | 63.913 | 63.858 | -59.0744 | -59.1888 | -0.036621 | -0.091552 | 0.041199 | 122.937 | -0.17853 | -0.086975 | -0.041199 | -0.073242 | -0.18768 | 0.041199 | 0.086975 | -0.21057 | -0.022888 | -0.013733 | 122.9141 | 122.8317 | 62.059 | -122.9645 | 122.9141 | 122.8592 | 58.8043 | -123.0606
1096.5156 | 123.0881 | -58.9966 | 63.9221 | -0.048828 | 0.015449 | 0.065877 | 0.070286 | 0.1287 | 0.00019875 | -0.00086512 | 0.14824 | -0.001128 | -0.0008182 | -0.0022452 | 0.0026234 | -0.0064515 | 63.8123 | 63.9038 | 3.0212 | -59.1843 | 63.9038 | -59.024 | -59.0927 | -58.9828 | -0.27466 | -59.2941 | 63.9542 | 63.8901 | -59.0836 | -59.1888 | -0.027466 | -0.09613 | -0.01831 | 122.9004 | -0.18768 | -0.091553 | -0.10986 | -0.086975 | -0.19226 | 0.032044 | 0.013733 | -0.29755 | -0.10529 | -0.032043 | 122.9004 | 122.8088 | 62.0178 | -123.0148 | 122.9507 | 122.8867 | 58.7219 | -123.111
1097.5156 | 123.1796 | -59.0103 | 63.8718 | 0.24109 | 0.012245 | 0.065877 | 0.069432 | 0.12998 | -0.0015102 | -0.0019333 | 0.25505 | -0.0071094 | -0.0006046 | -0.0026724 | 0.002196 | -0.0043153 | 63.8992 | 64.0274 | 3.1403 | -59.1202 | 63.8763 | -59.0469 | -59.0561 | -58.8684 | -0.19684 | -59.1705 | 63.9038 | 63.8626 | -59.0836 | -59.1843 | -0.036621 | -0.045776 | 0.004578 | 123.0377 | -0.10986 | -0.064087 | 0.027466 | -0.073242 | -0.17395 | 0.032044 | 0.14191 | -0.16022 | 0.013733 | -0.009155 | 122.8867 | 122.9095 | 62.1506 | -122.9279 | 122.9141 | 122.8729 | 58.8135 | -123.056
1098.5156 | 123.0881 | -59.0012 | 63.9313 | 0.16479 | 0.01374 | 0.0678 | 0.071141 | 0.12721 | 0.003403 | 0.0023391 | 0.38475 | -0.0036914 | -0.0008182 | -0.001818 | 0.0043324 | -0.0028199 | 63.4689 | 64.1785 | 3.2135 | -59.0744 | 63.9267 | -58.9874 | -59.0561 | -58.9783 | -0.31586 | -59.3033 | 63.945 | 63.8901 | -59.0927 | -59.1843 | 0.013733 | -0.054931 | -0.004577 | 123.1796 | -0.073242 | -0.018311 | -0.46234 | -0.091552 | -0.18311 | 0.013733 | 0.022889 | -0.30212 | -0.11902 | -0.041198 | 122.9279 | 122.4701 | 62.2147 | -122.9874 | 122.9462 | 122.8912 | 58.6853 | -123.1155
1099.5156 | 123.0835 | -59.0057 | 63.9313 | 0.14954 | 0.012886 | 0.0678 | 0.066655 | 0.12721 | -0.0017238 | -0.0023605 | 0.25505 | -0.004546 | -0.0010318 | -0.0033134 | 0.0043324 | -0.0043153 | 63.8397 | 63.9221 | 3.0533 | -59.166 | 63.9496 | -59.0424 | -59.0652 | -58.9508 | -0.32959 | -59.2575 | 63.9542 | 63.8809 | -59.0973 | -59.1797 | -0.036621 | -0.05951 | 0.018311 | 122.9279 | -0.16022 | -0.10071 | -0.091552 | -0.091553 | -0.17395 | 0.022889 | 0.054931 | -0.25177 | -0.07782 | -0.050354 | 122.9553 | 122.8455 | 62.059 | -122.9965 | 122.9599 | 122.8867 | 58.6761 | -123.111
1100.5156 | 123.1018 | -58.9783 | 63.9633 | 0.16479 | 0.015877 | 0.066731 | 0.069645 | 0.12678 | 0.0021214 | -0.0017197 | 0.22453 | -0.0030506 | -0.0006046 | -0.0013906 | 0.002837 | -0.0038879 | 63.8306 | 63.8855 | 3.0487 | -59.1751 | 63.9542 | -59.0103 | -59.0836 | -58.9417 | -0.87891 | -59.3719 | 63.9084 | 63.8763 | -59.0698 | -59.1751 | -0.032044 | -0.10529 | -0.009155 | 122.8638 | -0.19684 | -0.091553 | -0.13275 | -0.091553 | -0.19684 | -0.054932 | 0.036621 | -0.39368 | -0.19684 | -0.086975 | 122.9324 | 122.8088 | 62.027 | -123.0469 | 122.8867 | 122.8546 | 58.0994 | -123.1384
1101.5156 | 123.1522 | -58.9691 | 63.9038 | 0.2182 | 0.014808 | 0.066518 | 0.069218 | 0.12934 | 0.00083955 | -0.0027877 | 0.28557 | -0.0019824 | -0.0021 | -0.002886 | 0.0026234 | -0.0047425 | 63.8351 | 63.9404 | 3.0624 | -59.1568 | 63.913 | -59.0195 | -59.0561 | -58.9325 | -0.35248 | -59.2163 | 63.9404 | 63.8809 | -59.079 | -59.166 | -0.050354 | -0.086975 | 0.009155 | 122.9095 | -0.18768 | -0.10071 | -0.068665 | -0.10986 | -0.19684 | 0.036621 | 0.036621 | -0.24719 | -0.050354 | -0.022889 | 122.8821 | 122.8043 | 62.0316 | -122.9599 | 122.9095 | 122.85 | 58.6166 | -123.0698
1102.5156 | 123.0377 | -59.0103 | 63.945 | 0.09613 | 0.015449 | 0.068868 | 0.0705 | 0.12956 | 0.001694 | -0.00065152 | 0.25505 | -0.003905 | -0.001459 | -0.0016044 | 0.0032642 | -0.0041017 | 63.8397 | 63.9175 | 3.0991 | -59.1614 | 63.9587 | -59.0057 | -59.0515 | -58.9691 | -0.40283 | -59.2941 | 63.9908 | 63.913 | -59.0927 | -59.1751 | 0.004578 | -0.041199 | 0.013733 | 122.9279 | -0.15106 | -0.10986 | -0.10528 | -0.082397 | -0.16479 | 0.045777 | 0.041199 | -0.28381 | -0.11902 | -0.032043 | 122.9691 | 122.85 | 62.1094 | -122.9965 | 123.0011 | 122.9233 | 58.6075 | -123.1201
1103.5156 | 123.143 | -58.9828 | 63.9175 | 0.17242 | 0.011818 | 0.066518 | 0.06815 | 0.12849 | 0.00062595 | -0.0017197 | 0.28557 | -0.002196 | 0.0006772 | -0.0007498 | 0.003905 | -0.0030335 | 63.8901 | 63.9954 | 3.1723 | -59.1293 | 63.8763 | -58.9874 | -59.0424 | -58.8638 | -0.32959 | -59.1705 | 63.9221 | 63.8809 | -59.0744 | -59.1339 | -0.004578 | -0.059509 | -0.041199 | 122.9782 | -0.14648 | -0.086975 | -0.027466 | -0.091553 | -0.15106 | 0.004577 | 0.11902 | -0.18768 | -0.036621 | -0.036622 | 122.8592 | 122.8729 | 62.1552 | -122.9599 | 122.905 | 122.8638 | 58.6533 | -123.0515
1104.5156 | 123.0652 | -58.9737 | 63.9862 | 0.14191 | 0.016304 | 0.067372 | 0.071782 | 0.12849 | -0.00044225 | -0.0012923 | 0.20927 | -0.0019824 | -0.0012454 | 0.0039498 | 0.0019824 | -0.0070923 | 63.8214 | 63.8901 | 3.0991 | -59.1568 | 63.9542 | -59.0149 | -59.0515 | -58.9096 | -0.09613 | -59.2712 | 63.9771 | 63.945 | -59.0332 | -59.166 | -0.041199 | -0.07782 | -0.032043 | 122.8638 | -0.1831 | -0.10529 | -0.1648 | -0.059509 | -0.19226 | -0.009155 | 0.064087 | -0.29755 | -0.10529 | -0.041199 | 122.9279 | 122.7951 | 62.0728 | -123.0377 | 122.9507 | 122.9187 | 58.8776 | -123.1522
1105.5156 | 123.1293 | -58.9691 | 63.8947 | 0.2182 | 0.014168 | 0.067586 | 0.067936 | 0.12742 | 0.0014804 | -0.00086512 | 0.26268 | -0.0032642 | -0.0029544 | -0.0020316 | 0.0019824 | -0.0045289 | 63.858 | 63.9679 | 3.2043 | -59.1522 | 63.9679 | -58.992 | -59.0469 | -58.8867 | -0.43488 | -59.198 | 63.9771 | 63.8809 | -59.0469 | -59.1431 | -0.022888 | -0.07782 | 0.073243 | 122.937 | -0.18311 | -0.10529 | -0.036621 | -0.07782 | -0.17395 | 0.082398 | 0.082397 | -0.22888 | -0.054932 | -0.013733 | 122.937 | 122.8271 | 62.1735 | -122.9416 | 122.9462 | 122.85 | 58.5342 | -123.0377
1106.5156 | 123.0789 | -58.9737 | 63.9771 | -0.0030518 | 0.01139 | 0.068654 | 0.070073 | 0.12785 | 0.001694 | -0.0019333 | 0.094833 | -0.002196 | -0.0001774 | -0.0007498 | 0.0032642 | -0.0034607 | 63.9175 | 64.0091 | 3.2135 | -59.1064 | 63.945 | -58.9828 | -59.0103 | -58.9096 | -0.43945 | -59.23 | 64.0182 | 63.9496 | -59.0286 | -59.1476 | -0.009155 | -0.036621 | -0.032044 | 122.9828 | -0.13275 | -0.09613 | -0.059509 | -0.054931 | -0.17395 | 0.041199 | 0.064087 | -0.25635 | -0.082398 | -0.027466 | 122.9187 | 122.8912 | 62.1872 | -122.9874 | 122.9919 | 122.9233 | 58.5342 | -123.1247
1107.5156 | 123.0606 | -58.9645 | 63.9542 | 0.19531 | 0.012031 | 0.068227 | 0.068364 | 0.12592 | 0.0029758 | -0.0023605 | -0.27901 | -0.0026234 | -0.0025272 | -0.0009634 | 0.0024096 | -0.0043153 | 63.8214 | 63.9404 | 3.0579 | -59.4315 | 63.8855 | -59.0332 | -59.0744 | -58.9096 | -0.56305 | -59.2575 | 64.0045 | 63.9404 | -59.0652 | -59.1476 | -0.068664 | -0.10986 | -0.068665 | 122.905 | -0.46692 | -0.35706 | -0.13275 | -0.10071 | -0.1831 | 0.050354 | 0.054932 | -0.29297 | -0.10986 | -0.013733 | 122.85 | 122.7859 | 62.0224 | -123.0286 | 122.9691 | 122.905 | 58.4015 | -123.1018
1108.5156 | 123.0789 | -58.96 | 63.9908 | 0.019836 | 0.016731 | 0.066945 | 0.068364 | 0.12934 | 0.0021214 | 0.00041648 | 0.087204 | -0.0024096 | 0.0004636 | -0.001818 | 0.0030506 | -0.0053833 | 63.8901 | 63.9816 | 3.2684 | -59.1248 | 63.9816 | -58.9783 | -59.0424 | -58.9188 | -0.52185 | -59.2484 | 63.9999 | 63.945 | -59.0698 | -59.1614 | -0.01831 | -0.082397 | -0.009156 | 122.9416 | -0.16479 | -0.082398 | -0.10071 | -0.10986 | -0.20142 | 0.009155 | 0.041199 | -0.28839 | -0.086975 | -0.045777 | 122.9416 | 122.85 | 62.2284 | -123.0331 | 122.9599 | 122.905 | 58.4381 | -123.1522
1109.5156 | 123.0423 | -58.9417 | 63.9587 | -0.23956 | 0.014381 | 0.064168 | 0.06815 | 0.12913 | -0.00065585 | -0.0034287 | 0.20927 | -0.0017688 | -0.000391 | -0.0024588 | 0.0032642 | -0.0019653 | 63.8397 | 63.945 | 3.241 | -59.1385 | 63.9771 | -59.0103 | -59.0378 | -58.9233 | -0.56305 | -59.2529 | 63.9908 | 63.945 | -59.0561 | -59.1156 | -0.068665 | -0.096131 | 0.018311 | 122.8867 | -0.19684 | -0.10071 | -0.11902 | -0.11444 | -0.17395 | 0.032044 | 0.01831 | -0.31128 | -0.13733 | -0.013733 | 122.9187 | 122.7814 | 62.1826 | -122.9965 | 122.9324 | 122.8867 | 58.3786 | -123.0743
1110.5156 | 123.0469 | -58.9417 | 63.9771 | 0.042725 | 0.014381 | 0.06844 | 0.069218 | 0.12849 | 0.0021214 | 0.00063028 | 0.10246 | -0.0013416 | 0.0006772 | 0.0001046 | 0.0036914 | -0.0045289 | 63.8672 | 63.9725 | 3.3142 | -59.1293 | 63.9862 | -58.9783 | -59.0149 | -58.9645 | -0.59509 | -59.2712 | 64.0045 | 63.9542 | -59.0424 | -59.1293 | -0.036621 | -0.073243 | 0.009155 | 122.9141 | -0.18768 | -0.11444 | -0.10986 | -0.10071 | -0.18768 | 0.027466 | -0.022889 | -0.32959 | -0.14191 | -0.022888 | 122.9279 | 122.8088 | 62.2559 | -122.9919 | 122.9462 | 122.8958 | 58.3466 | -123.1064
1111.5156 | 123.0652 | -58.96 | 63.9816 | 0.14191 | 0.012672 | 0.066518 | 0.070073 | 0.13084 | -0.00065585 | -0.0032151 | 0.27031 | -0.0034778 | -0.0001774 | -0.0009634 | 0.001128 | -0.0021789 | 63.8763 | 63.945 | 3.2867 | -59.1248 | 63.9725 | -58.9783 | -59.0378 | -58.905 | -0.64087 | -59.2026 | 63.9816 | 63.9313 | -59.0561 | -59.1339 | -0.01831 | -0.07782 | -0.009155 | 122.905 | -0.16479 | -0.086975 | -0.10529 | -0.09613 | -0.17395 | 0 | 0.054932 | -0.24262 | -0.068665 | -0.050354 | 122.9324 | 122.8363 | 62.2467 | -123.0194 | 122.9416 | 122.8912 | 58.3191 | -123.1155
1112.5156 | 123.0743 | -58.992 | 63.9999 | 0.16479 | 0.017586 | 0.068013 | 0.069645 | 0.12956 | 0.0019078 | -0.00086512 | 0.14824 | -0.0017688 | 0.0015316 | 0.0001046 | 0.0034778 | -0.0043153 | 63.8626 | 63.9359 | 3.3417 | -59.1156 | 63.9908 | -58.9645 | -59.0286 | -58.9462 | -0.65918 | -59.2804 | 64.0091 | 63.9771 | -59.0378 | -59.1476 | 0.027465 | -0.036621 | -0.009155 | 122.9279 | -0.1236 | -0.086976 | -0.13733 | -0.045777 | -0.15564 | 0.009155 | 0.045776 | -0.28839 | -0.13275 | -0.022888 | 122.9828 | 122.8546 | 62.3337 | -123.0286 | 123.0011 | 122.9691 | 58.3328 | -123.1476
1113.5156 | 123.0743 | -58.9554 | 63.9954 | 0.088501 | 0.016517 | 0.067372 | 0.070714 | 0.12742 | 0.0038304 | -0.0025741 | 0.1635 | -0.0015552 | 0.001318 | -0.0009634 | 0.003905 | -0.0045289 | 63.8855 | 63.9587 | 3.3875 | -59.111 | 63.9999 | -58.96 | -59.0103 | -58.9325 | -0.67749 | -59.2575 | 63.9862 | 63.9771 | -59.0332 | -59.111 | -0.004578 | -0.054932 | 0.004578 | 122.9141 | -0.15564 | -0.10071 | -0.10986 | -0.07782 | -0.15564 | -0.009155 | 0.022888 | -0.30212 | -0.14648 | -0.01831 | 122.9553 | 122.8409 | 62.3428 | -123.0057 | 122.9416 | 122.9324 | 58.2779 | -123.1064
1114.5156 | 123.1476 | -58.8959 | 64.0411 | -0.14801 | 0.015877 | 0.0678 | 0.070714 | 0.12785 | 0.0019078 | -0.00043792 | -0.011978 | -0.0030506 | 0.0004636 | -0.0024588 | 0.0024096 | -0.0060243 | 63.9542 | 64.0503 | 3.4378 | -59.0607 | 64.0366 | -58.9417 | -59.0057 | -58.8501 | -0.5722 | -59.3353 | 63.9908 | 63.9359 | -59.0286 | -59.111 | -0.045776 | -0.10986 | -0.004578 | 122.9462 | -0.16479 | -0.054932 | -0.086975 | -0.13275 | -0.21515 | -0.050354 | 0.045776 | -0.43945 | -0.2243 | -0.10529 | 122.9324 | 122.85 | 62.3337 | -123.0469 | 122.8867 | 122.8317 | 58.3237 | -123.1522
1115.5156 | 122.9187 | -58.9691 | 63.9908 | 0.09613 | 0.017372 | 0.067159 | 0.068791 | 0.13084 | 0.0038304 | -0.0015061 | 0.15587 | -0.002196 | 0.0021726 | -0.0020316 | 0.003905 | -0.0043153 | 63.8718 | 63.9587 | 3.3646 | -59.111 | 63.9862 | -58.96 | -59.0149 | -58.9188 | -0.75073 | -59.2529 | 64.0274 | 63.9679 | -59.0286 | -59.1248 | 0.009155 | -0.045777 | -0.004578 | 122.9279 | -0.14191 | -0.09613 | -0.11902 | -0.059509 | -0.15564 | 0.036621 | 0.050354 | -0.28381 | -0.12817 | -0.022888 | 122.9553 | 122.8409 | 62.3337 | -123.0057 | 122.9965 | 122.937 | 58.2184 | -123.1155
1116.5156 | 123.0698 | -58.9005 | 64.0091 | -0.041199 | 0.014595 | 0.066945 | 0.071141 | 0.12956 | 0.00083955 | -0.0015061 | 0.25505 | -0.0017688 | 3.6404e-05 | -0.0003226 | 0.002837 | -0.0053833 | 63.9496 | 64.0503 | 3.479 | -59.0561 | 64.0137 | -58.9417 | -58.9874 | -58.8181 | -0.59967 | -59.1385 | 64.032 | 63.9816 | -59.0149 | -59.0927 | -0.041198 | -0.086975 | 0.004578 | 122.9507 | -0.15564 | -0.068664 | -0.059509 | -0.11444 | -0.19226 | 0.022888 | 0.082398 | -0.23804 | -0.045777 | -0.027466 | 122.9141 | 122.85 | 62.3795 | -122.9965 | 122.9324 | 122.8821 | 58.3008 | -123.1018
1117.5156 | 123.0881 | -58.9462 | 64.0091 | 0.088501 | 0.013954 | 0.064809 | 0.069005 | 0.12785 | -0.00022865 | -0.0012923 | 2.8262 | -0.0036914 | -0.0029544 | -0.001177 | 0.0032642 | -0.0049561 | 63.8626 | 63.9221 | 3.3966 | -59.111 | 63.9954 | -58.9554 | -59.0286 | -58.9142 | -0.6546 | -59.2346 | 64.0549 | 63.9679 | -59.0149 | -59.1293 | -0.009155 | -0.082397 | -0.013733 | 122.8683 | -0.1648 | -0.082398 | -0.14648 | -0.068665 | -0.18311 | 0.045777 | 0.032043 | -0.28839 | -0.10529 | -0.041198 | 122.9416 | 122.8088 | 62.3428 | -123.0377 | 123.0011 | 122.9141 | 58.2916 | -123.1384
1118.5156 | 123.0698 | -58.9096 | 63.9999 | -0.90332 | 0.01609 | 0.0678 | 0.070073 | 0.12657 | -0.00044225 | -0.0019333 | 0.064316 | -0.0034778 | 0.0008908 | -0.0013906 | 0.0043324 | -0.0028199 | 63.9954 | 64.0961 | 3.5248 | -59.0561 | 63.9908 | -58.9279 | -58.9691 | -58.8272 | -0.6546 | -59.1614 | 64.0411 | 63.9908 | -58.9828 | -59.0927 | -0.01831 | -0.059509 | -0.009155 | 123.0057 | -0.14648 | -0.086975 | -0.004578 | -0.073242 | -0.1831 | 0.041199 | 0.082398 | -0.25177 | -0.068665 | -0.009155 | 122.9004 | 122.905 | 62.4344 | -122.9691 | 122.9507 | 122.9004 | 58.255 | -123.0927
1119.5156 | 123.0331 | -58.9188 | 64.0182 | 0.10376 | 0.016304 | 0.067372 | 0.071354 | 0.12763 | 0.00019875 | -0.0017197 | 0.17876 | -0.0034778 | -0.0012454 | -0.000109 | 0.0030506 | -0.0066651 | 63.913 | 63.9954 | 3.4424 | -59.079 | 64.0091 | -58.9188 | -58.9828 | -58.9142 | -0.79193 | -59.2209 | 64.0182 | 63.9999 | -59.024 | -59.0744 | 0 | -0.064087 | -0.009156 | 122.9141 | -0.16022 | -0.09613 | -0.10529 | -0.10529 | -0.15564 | 0 | 0.004577 | -0.30212 | -0.14648 | -0.018311 | 122.9279 | 122.8317 | 62.3611 | -123.0011 | 122.937 | 122.9187 | 58.1268 | -123.0927
1120.5156 | 123.111 | -58.9005 | 64.0411 | -0.14038 | 0.012672 | 0.0678 | 0.069432 | 0.12699 | 0.0021214 | -0.0010787 | -0.14931 | -0.0036914 | -0.0033816 | -0.001177 | 0.0032642 | -0.0064515 | 63.9359 | 64.032 | 3.4698 | -59.0424 | 64.0411 | -58.9142 | -58.9966 | -58.8409 | -0.67291 | -59.1339 | 64.0686 | 64.0411 | -58.9966 | -59.0836 | -0.013733 | -0.09613 | 0 | 122.9324 | -0.14191 | -0.045776 | -0.10529 | -0.09613 | -0.1831 | 0.027466 | 0.05951 | -0.23346 | -0.050354 | 0 | 122.9416 | 122.8363 | 62.3703 | -123.0377 | 122.9691 | 122.9416 | 58.2275 | -123.1247
1121.5156 | 123.0881 | -58.9096 | 64.0274 | 0.52338 | 0.016945 | 0.066945 | 0.072209 | 0.12763 | 0.00083955 | -0.0032151 | 0.01091 | -0.003905 | 3.6404e-05 | -0.001177 | 0.0026234 | -0.0064515 | 63.9908 | 64.0823 | 3.5431 | -59.0195 | 64.0274 | -58.8959 | -58.992 | -58.8135 | -0.70496 | -59.1431 | 64.0366 | 63.9954 | -58.9783 | -59.0652 | 0.013733 | -0.082397 | 0 | 122.9919 | -0.10986 | -0.027466 | -0.036621 | -0.068664 | -0.15564 | 0.009155 | 0.09613 | -0.23346 | -0.077819 | -0.032044 | 122.937 | 122.9004 | 62.4527 | -123.0194 | 122.9462 | 122.905 | 58.2047 | -123.0927
1122.5156 | 123.0972 | -58.8913 | 64.0457 | -0.12512 | 0.013099 | 0.068868 | 0.0705 | 0.12806 | -0.00044225 | -0.0019333 | -0.065384 | -0.0049732 | -0.0046634 | -0.0024588 | 0.00048697 | -0.0045289 | 63.9633 | 64.0732 | 3.5202 | -59.0057 | 64.0411 | -58.905 | -58.9645 | -58.8043 | -0.69122 | -59.1156 | 64.064 | 64.0091 | -58.9737 | -59.0607 | -0.013733 | -0.073243 | -0.004577 | 122.9645 | -0.11444 | -0.041198 | -0.082397 | -0.082398 | -0.16937 | 0.018311 | 0.086975 | -0.22431 | -0.054932 | -0.036621 | 122.9324 | 122.8546 | 62.4115 | -123.0103 | 122.9553 | 122.9004 | 58.2001 | -123.1064
1123.5312 | 123.1155 | -58.8409 | 64.0091 | -0.071716 | 0.0081861 | 0.068227 | 0.069432 | 0.12721 | -0.004501 | -0.0064193 | 0.049057 | -0.0043324 | -0.004877 | -0.001177 | 0.00048697 | -0.0032471 | 64.0045 | 64.1922 | 3.6346 | -58.9783 | 64.032 | -58.8867 | -58.9508 | -58.7128 | -0.60425 | -58.9828 | 64.0274 | 63.9999 | -58.9188 | -59.0195 | -0.045777 | -0.10986 | 0.022888 | 123.0331 | -0.13733 | -0.027465 | -0.004577 | -0.07782 | -0.17853 | 0.018311 | 0.12817 | -0.14191 | 0.036621 | -0.009155 | 122.8729 | 122.8455 | 62.4756 | -122.9599 | 122.8683 | 122.8409 | 58.2367 | -123.0286
1124.5156 | 123.1018 | -58.905 | 64.0503 | -0.11749 | 0.015449 | 0.068868 | 0.071568 | 0.12614 | 0.001694 | -0.0036423 | -0.034867 | -0.0032642 | -0.0012454 | -0.0022452 | 0.002837 | -0.0073059 | 63.9816 | 64.0869 | 3.5385 | -59.0012 | 64.0549 | -58.9142 | -58.9508 | -58.786 | -0.71411 | -59.1202 | 64.0366 | 63.9816 | -58.9691 | -59.0652 | -0.009156 | -0.045777 | 0.004578 | 122.9919 | -0.096131 | -0.050354 | -0.068665 | -0.064087 | -0.16022 | -0.013733 | 0.11902 | -0.21515 | -0.054931 | -0.068665 | 122.9599 | 122.8867 | 62.4435 | -123.0011 | 122.9416 | 122.8867 | 58.1909 | -123.1155
1125.5156 | 123.0972 | -58.8776 | 64.0411 | 0.0045777 | 0.014168 | 0.064595 | 0.069218 | 0.12763 | 0.0010532 | -0.0027877 | 0.11009 | -0.0036914 | 0.0006772 | 0.0003182 | 0.0026234 | -0.0066651 | 63.9725 | 64.0778 | 3.5294 | -59.0378 | 64.0182 | -58.9233 | -58.9417 | -58.8181 | -0.79651 | -59.1705 | 64.0732 | 63.9908 | -58.992 | -59.079 | -0.045777 | -0.064087 | -0.022888 | 122.9553 | -0.16022 | -0.096131 | -0.068665 | -0.11444 | -0.20142 | 0.032043 | 0.059509 | -0.29297 | -0.091553 | -0.050354 | 122.8958 | 122.85 | 62.4069 | -122.9828 | 122.9507 | 122.8683 | 58.0811 | -123.1201
1126.5156 | 123.1018 | -58.8409 | 64.0457 | -0.15564 | 0.012031 | 0.068013 | 0.06815 | 0.1255 | 0.0012668 | -0.0019333 | -0.065384 | -0.0036914 | -0.0021 | 0.0007456 | 0.002196 | -0.0049561 | 63.9725 | 64.064 | 3.5568 | -58.9966 | 64.064 | -58.9142 | -58.9279 | -58.7952 | -0.74616 | -59.111 | 64.0961 | 64.0091 | -58.9691 | -59.0561 | -0.073243 | -0.086975 | 0.018311 | 122.905 | -0.15564 | -0.068665 | -0.073242 | -0.12817 | -0.21515 | 0.050354 | 0.045776 | -0.27008 | -0.054932 | -0.036621 | 122.905 | 122.8134 | 62.3978 | -122.9736 | 122.937 | 122.85 | 58.0948 | -123.1018
1127.5156 | 123.1338 | -58.873 | 64.064 | -0.28534 | 0.015663 | 0.067372 | 0.070073 | 0.12592 | 0.0036166 | -0.00043792 | 0.041427 | -0.0024096 | -0.000391 | -0.0013906 | 0.0043324 | -0.0038879 | 64.0228 | 64.1052 | 3.6072 | -59.0103 | 64.0549 | -58.8867 | -58.9508 | -58.7906 | -0.76446 | -59.1202 | 64.0503 | 64.0045 | -58.9691 | -59.0561 | -0.013733 | -0.07782 | -0.009155 | 122.9782 | -0.13733 | -0.059509 | -0.041199 | -0.09613 | -0.18311 | -0.013733 | 0.082398 | -0.24719 | -0.064087 | -0.059509 | 122.9279 | 122.8958 | 62.4802 | -123.0148 | 122.9233 | 122.8775 | 58.1085 | -123.1201
1128.5156 | 123.1384 | -58.8913 | 64.0274 | 0.23346 | 0.013099 | 0.068013 | 0.070286 | 0.12785 | 0.0012668 | -0.0027877 | 0.27794 | -0.0013416 | 0.0017454 | -0.0020316 | 0.0019824 | -0.0041017 | 63.9267 | 64.0182 | 3.5019 | -59.0469 | 64.0366 | -58.9005 | -58.9554 | -58.7952 | -0.86517 | -59.1476 | 64.0594 | 63.9771 | -58.992 | -59.0652 | -0.009156 | -0.064087 | 0.009155 | 122.9095 | -0.15564 | -0.091553 | -0.10071 | -0.10071 | -0.17395 | 0.032043 | 0.09613 | -0.25635 | -0.082397 | -0.050354 | 122.9279 | 122.818 | 62.3932 | -122.9828 | 122.9507 | 122.8683 | 58.0261 | -123.0927
1129.5156 | 123.0881 | -58.8638 | 64.0823 | -0.071716 | 0.015449 | 0.065877 | 0.070927 | 0.1287 | 0.0025486 | -0.00043792 | -0.011978 | -0.003905 | -0.0008182 | 0.0013864 | 0.0034778 | -0.0047425 | 63.9954 | 64.1006 | 3.5843 | -58.9966 | 64.0594 | -58.8821 | -58.9325 | -58.7769 | -0.66376 | -59.1019 | 64.0594 | 64.0594 | -58.9417 | -59.0378 | -0.01831 | -0.068664 | -0.022888 | 122.9645 | -0.13275 | -0.064087 | -0.086975 | -0.077819 | -0.17395 | -0.022888 | 0.086976 | -0.23804 | -0.064087 | -0.022888 | 122.9233 | 122.8592 | 62.4481 | -123.0148 | 122.9233 | 122.9233 | 58.2001 | -123.1201
1130.5156 | 123.0469 | -58.8547 | 64.1144 | -0.17853 | 0.010963 | 0.071218 | 0.069005 | 0.12763 | 0.00083955 | -0.0021469 | -0.14168 | -0.0013416 | 0.00025 | -0.0005362 | 0.002196 | -0.0036743 | 63.9816 | 64.032 | 3.5156 | -59.0332 | 64.0686 | -58.9096 | -58.9554 | -58.8226 | -0.77362 | -59.1385 | 64.1052 | 64.0686 | -58.9325 | -59.024 | -0.054932 | -0.10071 | -0.045776 | 122.8867 | -0.17853 | -0.07782 | -0.13275 | -0.07782 | -0.16937 | -0.009155 | 0.032043 | -0.28381 | -0.11444 | -0.045776 | 122.9233 | 122.8363 | 62.3703 | -123.0698 | 122.9599 | 122.9233 | 58.0811 | -123.1384
1131.5156 | 123.0881 | -58.8593 | 64.0594 | -0.079346 | 0.014808 | 0.067159 | 0.069645 | 0.12678 | 0.0012668 | 0.0036209 | -0.29427 | -0.0017688 | -0.0016726 | -0.0007498 | 0.0024096 | -0.0060243 | 63.9221 | 64.0137 | 3.5751 | -58.905 | 64.064 | -58.8867 | -58.9417 | -58.7402 | -0.75989 | -59.0836 | 64.0686 | 64.0228 | -58.9462 | -59.0332 | -0.027466 | -0.082397 | 0.004578 | 122.8729 | -0.045776 | 0.036621 | -0.13733 | -0.086975 | -0.17395 | 0.009156 | 0.11902 | -0.2243 | -0.050354 | -0.036621 | 122.9233 | 122.7814 | 62.4344 | -123.0011 | 122.9279 | 122.8821 | 58.0994 | -123.0927
1132.5156 | 123.0469 | -58.8455 | 64.0961 | -0.23956 | 0.010536 | 0.068868 | 0.068577 | 0.12785 | -0.0017238 | -0.0038559 | -0.095902 | -0.0034778 | -0.001459 | -0.0024588 | 0.00091437 | -0.0041017 | 63.9496 | 64.0915 | 3.5889 | -59.0012 | 64.0915 | -58.8684 | -58.9279 | -58.7952 | -0.84228 | -59.111 | 64.1281 | 64.0411 | -58.9508 | -59.0149 | -0.022888 | -0.082397 | -0.004577 | 122.937 | -0.15564 | -0.073243 | -0.14648 | -0.10529 | -0.16937 | 0.032044 | 0.050354 | -0.2655 | -0.09613 | -0.054931 | 122.937 | 122.7951 | 62.4344 | -123.024 | 122.9736 | 122.8867 | 58.0032 | -123.111
1133.5156 | 123.111 | -58.8364 | 64.0686 | 0.18005 | 0.0090405 | 0.066304 | 0.067509 | 0.12721 | -0.0019376 | -0.0025741 | 0.36186 | -0.0030506 | -0.0021 | -0.0022452 | 0.00027337 | -0.0038879 | 63.9816 | 64.1556 | 3.6758 | -58.992 | 64.0182 | -58.8638 | -58.9096 | -58.7311 | -0.83313 | -59.0561 | 64.032 | 63.9771 | -58.9233 | -59.0286 | -0.027466 | -0.073242 | -0.050354 | 122.9919 | -0.15564 | -0.082397 | -0.086976 | -0.086975 | -0.19226 | -0.036622 | 0.10529 | -0.21973 | -0.027466 | -0.091553 | 122.8546 | 122.818 | 62.5122 | -122.9782 | 122.8683 | 122.8134 | 58.0032 | -123.0972
1134.5156 | 123.111 | -58.8181 | 64.1098 | -0.14038 | 0.0090405 | 0.066304 | 0.069218 | 0.1302 | -0.0015102 | -0.0032151 | -0.080643 | -0.0047596 | -0.003168 | -0.0033134 | 0.00070077 | -0.0053833 | 64.0228 | 64.1922 | 3.7125 | -58.9554 | 64.0778 | -58.8455 | -58.905 | -58.7265 | -0.78735 | -59.0698 | 64.1144 | 64.0457 | -58.9279 | -59.0103 | -0.027466 | -0.086975 | -0.032043 | 123.0103 | -0.13733 | -0.050354 | -0.086975 | -0.10986 | -0.19226 | 0.004578 | 0.091553 | -0.25177 | -0.059509 | -0.064087 | 122.8958 | 122.8409 | 62.5305 | -123.0148 | 122.9324 | 122.8638 | 58.0307 | -123.1201
1135.5156 | 123.0881 | -58.8226 | 64.0961 | -0.15564 | 0.012672 | 0.0678 | 0.071995 | 0.12827 | 0.0029758 | -0.0025741 | -0.073013 | -0.0034778 | 0.0004636 | -0.0024588 | 0.002196 | -0.0073059 | 63.9999 | 64.1281 | 3.6942 | -58.9508 | 64.1098 | -58.8501 | -58.9142 | -58.7311 | -0.83771 | -59.0836 | 64.119 | 64.032 | -58.9188 | -59.024 | -0.027466 | -0.091553 | 0.013733 | 122.9507 | -0.12817 | -0.036621 | -0.09613 | -0.09613 | -0.20142 | 0.022889 | 0.091553 | -0.26093 | -0.059509 | -0.064087 | 122.9324 | 122.8226 | 62.5168 | -123.0103 | 122.9416 | 122.8546 | 57.9849 | -123.1201
1136.5156 | 123.0972 | -58.8364 | 64.1327 | -0.21667 | 0.0075451 | 0.067586 | 0.067936 | 0.12721 | -0.0017238 | -0.0032151 | 0.041427 | -0.0047596 | -0.0012454 | -0.0009634 | -0.00036743 | -0.0038879 | 64.0045 | 64.1785 | 3.7216 | -58.9371 | 64.1144 | -58.8547 | -58.8913 | -58.7494 | -0.83313 | -59.0881 | 64.119 | 64.0686 | -58.9142 | -59.0012 | -0.01831 | -0.054931 | -0.01831 | 123.0148 | -0.10071 | -0.045777 | -0.12817 | -0.07782 | -0.16479 | -0.013732 | 0.086975 | -0.25177 | -0.086975 | -0.064086 | 122.9507 | 122.8409 | 62.558 | -123.024 | 122.9553 | 122.905 | 58.0032 | -123.1338
1137.5156 | 123.0927 | -58.8043 | 64.1418 | -0.19379 | 0.01139 | 0.067586 | 0.070714 | 0.13062 | 0.00062595 | -0.0019333 | -0.10353 | -0.0032642 | 0.0015316 | -0.000109 | 0.0019824 | -0.0051697 | 63.9908 | 64.1235 | 3.6667 | -58.96 | 64.1144 | -58.8409 | -58.905 | -58.7265 | -0.87433 | -59.0927 | 64.1464 | 64.0686 | -58.905 | -59.0149 | -0.036621 | -0.10071 | -0.027466 | 122.9279 | -0.15564 | -0.054932 | -0.15106 | -0.10071 | -0.21057 | 0.004577 | 0.07782 | -0.28839 | -0.077819 | -0.073242 | 122.9187 | 122.7951 | 62.471 | -123.0469 | 122.9507 | 122.8729 | 57.93 | -123.1567
1138.5156 | 123.0881 | -58.8409 | 64.1006 | -0.010681 | 0.015663 | 0.065236 | 0.0705 | 0.12892 | 0.004044 | -1.0724e-05 | 0.056686 | -0.0058276 | 0.0017454 | -0.000109 | 0.0026234 | -0.0038879 | 64.0457 | 64.1602 | 3.6621 | -58.96 | 64.1235 | -58.8318 | -58.8821 | -58.7265 | -0.88806 | -59.0973 | 64.1144 | 64.0503 | -58.9279 | -58.992 | 0.009155 | -0.041199 | 0.022888 | 123.0011 | -0.11902 | -0.07782 | -0.054932 | -0.086975 | -0.15106 | 0.013733 | 0.11444 | -0.25635 | -0.10529 | -0.050354 | 122.9645 | 122.8867 | 62.5031 | -122.9828 | 122.9553 | 122.8912 | 57.9529 | -123.0927
1139.5156 | 123.0881 | -58.8043 | 64.1418 | -0.14038 | 0.013954 | 0.068013 | 0.069859 | 0.12913 | -0.00065585 | -0.00022432 | -0.12642 | -0.0017688 | 0.0021726 | -0.0016044 | 0.0024096 | -0.0049561 | 63.9999 | 64.151 | 3.6758 | -58.9462 | 64.1281 | -58.8409 | -58.8913 | -58.7036 | -0.84228 | -59.0515 | 64.1281 | 64.1006 | -58.905 | -59.0103 | -0.036621 | -0.086975 | -0.013733 | 122.9553 | -0.14191 | -0.054932 | -0.14191 | -0.10071 | -0.20599 | -0.013733 | 0.10071 | -0.24719 | -0.041199 | -0.041199 | 122.9324 | 122.8043 | 62.4802 | -123.0331 | 122.9324 | 122.905 | 57.962 | -123.1522
1140.5156 | 123.1613 | -58.7677 | 64.1235 | -0.12512 | 0.0058361 | 0.06844 | 0.066014 | 0.12934 | -0.0053554 | -0.0040695 | -0.0043486 | -0.004546 | -0.0021 | 0.0001046 | 5.9768e-05 | -0.0041017 | 64.0732 | 64.2609 | 3.8086 | -58.8913 | 64.0778 | -58.8043 | -58.8501 | -58.6441 | -0.74158 | -58.9645 | 64.119 | 64.0274 | -58.8776 | -58.9554 | -0.036621 | -0.082398 | -0.045776 | 123.0286 | -0.1236 | -0.041198 | -0.050354 | -0.10986 | -0.18768 | -0.004577 | 0.1236 | -0.19684 | -0.009156 | -0.09613 | 122.8455 | 122.8409 | 62.5763 | -122.9736 | 122.8867 | 122.7951 | 58.0261 | -123.0789
1141.5156 | 123.0835 | -58.8226 | 64.1556 | 0.027466 | 0.010963 | 0.067586 | 0.070286 | 0.12977 | -0.001083 | -0.0019333 | -0.073013 | -0.0013416 | -0.0008182 | -0.0009634 | 0.0026234 | -0.0041017 | 64.0411 | 64.1418 | 3.7216 | -58.9554 | 64.151 | -58.8318 | -58.8547 | -58.7128 | -0.85602 | -59.0698 | 64.1739 | 64.0869 | -58.8913 | -58.9828 | -0.009155 | -0.032043 | -0.004578 | 122.9645 | -0.13275 | -0.10071 | -0.11444 | -0.068664 | -0.16022 | 0.01831 | 0.10986 | -0.24719 | -0.086975 | -0.068665 | 122.9736 | 122.8638 | 62.5443 | -123.0103 | 122.9965 | 122.9095 | 57.9666 | -123.1384
1142.5156 | 123.1384 | -58.7769 | 64.1281 | -0.12512 | 0.0077587 | 0.069936 | 0.06815 | 0.1287 | -0.0034328 | -0.0049239 | -0.042496 | -0.0047596 | -0.0042362 | -0.0030996 | -0.00015383 | -0.0043153 | 64.0823 | 64.2838 | 3.8681 | -58.8959 | 64.0915 | -58.7906 | -58.8455 | -58.6578 | -0.70953 | -58.9737 | 64.1144 | 64.0594 | -58.8593 | -58.9508 | -0.013733 | -0.068665 | -0.036621 | 123.0606 | -0.11902 | -0.050354 | -0.045777 | -0.082398 | -0.17395 | -0.013733 | 0.11902 | -0.19684 | -0.022888 | -0.068665 | 122.8683 | 122.8592 | 62.645 | -122.9736 | 122.8912 | 122.8363 | 58.0673 | -123.0789
1143.5156 | 123.0972 | -58.7997 | 64.1602 | -0.2243 | 0.01139 | 0.068654 | 0.073704 | 0.12742 | -0.0012966 | -0.0025741 | -0.11879 | -0.0030506 | 0.0011044 | -0.001818 | 0.001128 | -0.0041017 | 64.0228 | 64.183 | 3.772 | -58.9508 | 64.1556 | -58.8364 | -58.8684 | -58.6899 | -1.0529 | -59.1202 | 64.1785 | 64.0823 | -58.8821 | -59.0012 | -0.036621 | -0.068664 | -0.004577 | 122.9828 | -0.15106 | -0.082398 | -0.13733 | -0.082397 | -0.20142 | 0.018311 | 0.10986 | -0.32043 | -0.11902 | -0.07782 | 122.9553 | 122.8226 | 62.5717 | -123.0286 | 122.9782 | 122.8821 | 57.7469 | -123.1613
1144.5156 | 123.1247 | -58.7402 | 64.1373 | -0.15564 | 0.0088269 | 0.067372 | 0.067723 | 0.12806 | -0.00086945 | -0.0034287 | -0.065384 | -0.0054004 | -0.0035952 | -0.0007498 | -0.00015383 | -0.0045289 | 64.1098 | 64.2654 | 3.8773 | -58.8821 | 64.1235 | -58.7952 | -58.8501 | -58.6441 | -0.75531 | -58.9645 | 64.1464 | 64.0778 | -58.8638 | -58.9462 | -0.054932 | -0.10986 | -0.013733 | 123.0057 | -0.14191 | -0.032043 | -0.027466 | -0.1236 | -0.20599 | 0.009155 | 0.09613 | -0.22431 | -0.018311 | -0.059509 | 122.8638 | 122.85 | 62.6175 | -122.9874 | 122.8867 | 122.818 | 57.9849 | -123.0835
1145.5156 | 123.056 | -58.7769 | 64.183 | -0.18616 | 0.0092541 | 0.066091 | 0.069645 | 0.12763 | -0.00065585 | -0.0023605 | 0.056686 | -0.0026234 | 0.0006772 | -0.0020316 | 0.0019824 | -0.0060243 | 64.0457 | 64.032 | 3.8956 | -58.786 | 64.2105 | -58.7677 | -58.8684 | -58.7173 | -0.86517 | -59.0332 | 64.1922 | 64.1235 | -58.8959 | -58.9737 | 0.009155 | -0.091553 | 0.027466 | 122.8088 | -0.009156 | 0.082397 | -0.13733 | -0.11902 | -0.19684 | 0.009156 | 0.059509 | -0.25635 | -0.059509 | -0.059509 | 122.9874 | 122.8226 | 62.6724 | -123.0515 | 122.9691 | 122.9004 | 57.9117 | -123.1567
1146.5156 | 123.1247 | -58.7585 | 64.1785 | -0.16327 | 0.0079723 | 0.0678 | 0.069218 | 0.12998 | -0.0030056 | -0.0023605 | -0.095902 | -0.0047596 | -0.0021 | -0.0024588 | 0.0013416 | -0.0043153 | 64.1006 | 64.2792 | 3.9322 | -58.873 | 64.151 | -58.8043 | -58.8455 | -58.6349 | -0.79651 | -58.9691 | 64.1464 | 64.0823 | -58.8638 | -58.9233 | -0.045776 | -0.086975 | -0.027466 | 123.0377 | -0.11444 | -0.027466 | -0.07782 | -0.10529 | -0.1648 | -0.032044 | 0.1236 | -0.21057 | -0.045776 | -0.096131 | 122.9095 | 122.8592 | 62.6907 | -123.024 | 122.905 | 122.8409 | 57.962 | -123.1018
1147.5156 | 123.0469 | -58.7677 | 64.1968 | -0.18616 | 0.010536 | 0.068868 | 0.068791 | 0.13041 | -0.0012966 | -0.0027877 | -0.13405 | -0.003905 | -0.001459 | -0.0024588 | 0.002196 | -0.0049561 | 64.064 | 64.2242 | 3.9001 | -58.9188 | 64.1602 | -58.7677 | -58.8501 | -58.6716 | -0.90179 | -59.0424 | 64.2105 | 64.0915 | -58.8684 | -58.9462 | 0 | -0.082398 | -0.036621 | 122.9919 | -0.15106 | -0.068664 | -0.13275 | -0.10071 | -0.17853 | 0.013733 | 0.09613 | -0.27466 | -0.09613 | -0.10528 | 122.9279 | 122.8317 | 62.6678 | -123.0469 | 122.9782 | 122.8592 | 57.8659 | -123.143
1148.5156 | 123.1934 | -58.7265 | 64.1327 | -0.018311 | 0.0073315 | 0.068654 | 0.067296 | 0.12913 | -0.002792 | -0.0032151 | 0.11009 | -0.007323 | -0.0021 | -0.0009634 | -0.00036743 | -0.0055969 | 64.0778 | 64.2975 | 3.923 | -58.8776 | 64.1373 | -58.8043 | -58.8135 | -58.5846 | -0.8194 | -58.9279 | 64.1144 | 64.0594 | -58.873 | -58.9462 | -0.07782 | -0.086976 | 0.004578 | 123.024 | -0.15106 | -0.064086 | -0.054931 | -0.14648 | -0.21973 | -0.01831 | 0.14191 | -0.20142 | 0.018311 | -0.073242 | 122.8638 | 122.8043 | 62.6495 | -122.9462 | 122.8409 | 122.7859 | 57.9071 | -123.0789
1149.5156 | 123.0972 | -58.7311 | 64.1785 | -0.17853 | 0.010536 | 0.0678 | 0.070286 | 0.12699 | -0.00086945 | -0.0034287 | -0.12642 | -0.005614 | -0.0027408 | -0.0005362 | 0.0019824 | -0.0053833 | 64.1281 | 64.27 | 3.9093 | -58.8684 | 64.1464 | -58.7723 | -58.8364 | -58.6121 | -0.83771 | -58.9783 | 64.1647 | 64.119 | -58.8455 | -58.9096 | -0.041199 | -0.10529 | -0.032044 | 123.0011 | -0.13733 | -0.032043 | -0.050354 | -0.11444 | -0.17853 | -0.013733 | 0.11902 | -0.24719 | -0.068664 | -0.059509 | 122.8775 | 122.8592 | 62.6404 | -123.0148 | 122.8958 | 122.85 | 57.8934 | -123.0881
1150.5156 | 123.2071 | -58.7585 | 64.1418 | -0.064087 | 0.0071179 | 0.068227 | 0.067296 | 0.12763 | -0.0040738 | -0.0027877 | -0.011978 | -0.004546 | -0.0042362 | -0.0026724 | 0.0019824 | -0.0053833 | 64.119 | 64.3158 | 3.9688 | -58.8409 | 64.1098 | -58.7631 | -58.8318 | -58.5663 | -0.81024 | -58.8913 | 64.1052 | 64.0549 | -58.8181 | -58.9188 | -0.004578 | -0.073242 | -0.032044 | 123.0743 | -0.082397 | -0.009155 | -0.022888 | -0.059509 | -0.16022 | -0.036621 | 0.19226 | -0.13275 | 0.027466 | -0.086975 | 122.8683 | 122.8775 | 62.7274 | -122.9736 | 122.8638 | 122.8134 | 57.9483 | -123.0606
1151.5156 | 123.143 | -58.7357 | 64.1647 | -0.14038 | 0.0098951 | 0.068868 | 0.069859 | 0.12849 | -0.001083 | -0.0025741 | -0.073013 | -0.005614 | -0.0018862 | -0.0039542 | 0.003905 | -0.0070923 | 64.1327 | 64.3158 | 3.9917 | -58.8409 | 64.1235 | -58.7906 | -58.8181 | -58.5754 | -0.7782 | -58.9371 | 64.1647 | 64.0549 | -58.8181 | -58.9142 | -0.054931 | -0.082397 | -0.041199 | 123.0515 | -0.10528 | -0.022888 | -0.032044 | -0.082397 | -0.17853 | 0 | 0.16022 | -0.20142 | -0.022888 | -0.10986 | 122.8592 | 122.8683 | 62.7274 | -122.9828 | 122.9004 | 122.7905 | 57.9575 | -123.0789
1152.5156 | 123.2025 | -58.7357 | 64.1235 | -0.11749 | 0.0051953 | 0.06844 | 0.069005 | 0.12635 | -0.0019376 | -0.0036423 | -0.011978 | -0.0049732 | -0.0053042 | -0.001177 | -0.0029308 | -0.0070923 | 64.1556 | 64.357 | 4.0512 | -58.8409 | 64.151 | -58.7585 | -58.8135 | -58.3649 | -1.1948 | -59.0012 | 64.1373 | 64.0503 | -58.8409 | -58.9371 | -0.022888 | -0.07782 | 0.027466 | 123.0927 | -0.10528 | -0.027465 | 0.032044 | -0.10528 | -0.20142 | 0.013733 | 0.37079 | -0.2655 | -0.064087 | -0.073242 | 122.8867 | 122.8912 | 62.7869 | -122.937 | 122.8729 | 122.7859 | 57.5409 | -123.0606
1153.5156 | 123.1293 | -58.7402 | 64.183 | -0.15564 | 0.01075 | 0.070149 | 0.071354 | 0.12977 | 0.001694 | -0.0015061 | -0.12642 | -0.0051868 | -0.0044498 | -0.0003226 | -0.00015383 | -0.0058105 | 64.1373 | 64.3066 | 3.9917 | -58.8409 | 64.1327 | -58.7585 | -58.8272 | -58.5846 | -0.78278 | -58.96 | 64.2014 | 64.1006 | -58.8226 | -58.9142 | -0.018311 | -0.086975 | -0.050354 | 123.0469 | -0.10071 | -0.013733 | -0.045776 | -0.082398 | -0.17395 | 0.018311 | 0.15564 | -0.21973 | -0.045776 | -0.082397 | 122.8729 | 122.8775 | 62.7319 | -123.0103 | 122.9416 | 122.8409 | 57.9575 | -123.0972
1154.5156 | 123.1522 | -58.7402 | 64.1602 | 0.027466 | 0.0062635 | 0.069081 | 0.066014 | 0.12614 | -0.0036464 | -0.0027877 | 0.094833 | -0.0036914 | -0.0023136 | -0.0013906 | 0.00070077 | -0.0049561 | 64.0915 | 64.2288 | 3.9688 | -58.8593 | 64.1556 | -58.754 | -58.8135 | -58.5754 | -0.82855 | -58.9417 | 64.1418 | 64.0915 | -58.8135 | -58.9188 | -0.013733 | -0.073243 | -0.004577 | 122.9691 | -0.11902 | -0.045776 | -0.068664 | -0.073243 | -0.17853 | -0.01831 | 0.16479 | -0.20142 | -0.022888 | -0.068664 | 122.8958 | 122.8317 | 62.709 | -122.9736 | 122.8821 | 122.8317 | 57.9117 | -123.0789
1155.5156 | 123.1293 | -58.7265 | 64.2014 | -0.14801 | 0.0092541 | 0.068013 | 0.068364 | 0.12742 | -0.0015102 | -0.0030013 | -0.10353 | -0.005614 | -0.0033816 | -0.0024588 | 0.00048697 | -0.0064515 | 64.1739 | 64.3066 | 4.0512 | -58.8181 | 64.1464 | -58.7402 | -58.8181 | -58.5388 | -0.76446 | -58.9233 | 64.1876 | 64.064 | -58.8089 | -58.8913 | -0.013733 | -0.091553 | -0.054932 | 123.0331 | -0.091553 | 0 | -0.027466 | -0.082398 | -0.16479 | -0.013733 | 0.18768 | -0.19684 | -0.032044 | -0.13733 | 122.8729 | 122.9004 | 62.7777 | -123.0194 | 122.9141 | 122.7905 | 57.962 | -123.0927
1156.5156 | 123.1796 | -58.699 | 64.1647 | -0.02594 | 0.0064771 | 0.068227 | 0.067723 | 0.12678 | -0.0015102 | -0.0034287 | 0.10246 | -0.0064686 | -0.0021 | -0.001818 | 0.00048697 | -0.0060243 | 64.1144 | 64.3112 | 4.0421 | -58.8455 | 64.1418 | -58.754 | -58.8089 | -58.5434 | -0.80566 | -58.9188 | 64.1647 | 64.0457 | -58.8364 | -58.9371 | -0.054931 | -0.10986 | -0.022888 | 123.0103 | -0.14648 | -0.036621 | -0.050354 | -0.13733 | -0.23804 | 0 | 0.15564 | -0.21973 | 0.018311 | -0.11902 | 122.8409 | 122.8134 | 62.7411 | -122.9736 | 122.8638 | 122.7448 | 57.8934 | -123.1018
1157.5156 | 123.1705 | -58.7082 | 64.1693 | 0.18768 | 0.0098951 | 0.069081 | 0.066868 | 0.12763 | 0.0014804 | -0.0027877 | -0.050125 | -0.0026234 | -0.001459 | -0.001177 | 0.0036914 | -0.0060243 | 64.1922 | 64.3478 | 4.097 | -58.8272 | 64.1602 | -58.7585 | -58.786 | -58.5205 | -0.74616 | -58.9005 | 64.1785 | 64.0686 | -58.7906 | -58.905 | -0.050354 | -0.07782 | -0.009156 | 123.056 | -0.11902 | -0.041198 | 0.022888 | -0.082397 | -0.19684 | 0.009155 | 0.18768 | -0.19226 | 0.004577 | -0.10071 | 122.8683 | 122.9004 | 62.8052 | -122.9553 | 122.8867 | 122.7768 | 57.962 | -123.0743
1158.5156 | 123.1522 | -58.7311 | 64.1556 | 0.050354 | 0.0073315 | 0.068654 | 0.069859 | 0.12827 | -0.00044225 | -0.0012923 | 0.094833 | -0.0066822 | -0.001459 | -0.000109 | 0.0030506 | -0.0070923 | 64.1098 | 64.2838 | 4.0283 | -58.8364 | 64.1647 | -58.7631 | -58.8089 | -58.548 | -0.85144 | -58.9233 | 64.1693 | 64.0686 | -58.8089 | -58.9096 | -0.032044 | -0.07782 | 0.009155 | 123.0148 | -0.10529 | -0.027466 | -0.045777 | -0.07782 | -0.17853 | 0.013733 | 0.1831 | -0.19226 | -0.013733 | -0.086975 | 122.8958 | 122.8409 | 62.7594 | -122.9645 | 122.9004 | 122.7997 | 57.8796 | -123.0652
1159.5156 | 123.1567 | -58.699 | 64.2105 | -0.11749 | 0.0051953 | 0.069295 | 0.068364 | 0.12977 | -0.0017238 | -0.0027877 | -0.13405 | -0.0043324 | -0.0044498 | -0.0003226 | 0.0019824 | -0.0068787 | 64.1693 | 64.3478 | 4.0283 | -58.8135 | 64.1693 | -58.7082 | -58.7952 | -58.5114 | -0.80109 | -58.9005 | 64.1968 | 64.1006 | -58.8135 | -58.8776 | -0.009155 | -0.09613 | -0.041198 | 123.0469 | -0.11444 | -0.018311 | -0.041198 | -0.11444 | -0.17853 | -0.013733 | 0.18768 | -0.20142 | -0.022889 | -0.10986 | 122.8683 | 122.8683 | 62.7274 | -123.0057 | 122.8958 | 122.7997 | 57.898 | -123.0881
1160.5156 | 123.1934 | -58.6853 | 64.1602 | -0.071716 | 0.0058361 | 0.0678 | 0.067723 | 0.12785 | -0.00065585 | -0.0040695 | -0.080643 | -0.0066822 | -0.0046634 | -0.0005362 | 0.0051868 | -0.0038879 | 64.2197 | 64.4119 | 4.0741 | -58.7814 | 64.1647 | -58.7402 | -58.7677 | -58.548 | -0.6958 | -58.9508 | 64.1739 | 64.0686 | -58.786 | -58.9005 | -0.054931 | -0.082397 | 0.004578 | 123.0972 | -0.09613 | -0.013733 | 0.05951 | -0.10071 | -0.21515 | 0.013733 | 0.13733 | -0.2655 | -0.050354 | -0.091552 | 122.85 | 122.905 | 62.7594 | -122.9279 | 122.8592 | 122.7539 | 57.9895 | -123.0606
1161.5156 | 123.2162 | -58.6899 | 64.183 | -0.1709 | 0.0075451 | 0.06844 | 0.068577 | 0.12892 | -0.0012966 | -0.0038559 | 0.033798 | -0.0068958 | -0.0035952 | -0.002886 | 0.00070077 | -0.0058105 | 64.1922 | 64.3753 | 4.0466 | -58.7952 | 64.1602 | -58.7219 | -58.7769 | -58.4427 | -0.72784 | -58.6761 | 64.2242 | 64.151 | -58.7494 | -58.8684 | -0.032044 | -0.086975 | -0.022888 | 123.0652 | -0.10529 | -0.018311 | 0.009156 | -0.05951 | -0.17853 | 0.041199 | 0.24719 | 0.013733 | 0.19226 | -0.032043 | 122.85 | 122.8821 | 62.7365 | -122.9599 | 122.9141 | 122.8409 | 57.962 | -123.0515
1162.5156 | 123.1522 | -58.7128 | 64.1785 | 0.027466 | 0.0056225 | 0.072713 | 0.067723 | 0.12934 | -0.001083 | -0.0023605 | 0.071945 | -0.0098866 | -0.0038088 | -0.0016044 | 0.00048697 | -0.0049561 | 64.1235 | 64.2288 | 3.9551 | -58.8272 | 64.1647 | -58.754 | -58.8135 | -58.5388 | -0.86975 | -58.9325 | 64.1922 | 64.0778 | -58.8089 | -58.9005 | -0.041198 | -0.10071 | -0.013733 | 122.9416 | -0.11444 | -0.013732 | -0.054932 | -0.09613 | -0.18768 | 0.013733 | 0.17395 | -0.21973 | -0.032043 | -0.10071 | 122.8775 | 122.8363 | 62.6678 | -122.9919 | 122.905 | 122.7905 | 57.843 | -123.0789
1163.5156 | 123.1155 | -58.699 | 64.2059 | -0.1709 | 0.0086133 | 0.069295 | 0.069218 | 0.12657 | 0.0010532 | -0.0032151 | -0.11116 | -0.003905 | -0.0018862 | -0.0020316 | 0.002837 | -0.0062379 | 64.1739 | 64.3433 | 4.0833 | -58.8135 | 64.1876 | -58.7173 | -58.7814 | -58.5205 | -0.76446 | -58.9096 | 64.2105 | 64.1052 | -58.786 | -58.8821 | -0.01831 | -0.082397 | -0.018311 | 123.0423 | -0.11444 | -0.032044 | -0.032044 | -0.086975 | -0.1831 | 0.004577 | 0.17853 | -0.21057 | -0.027466 | -0.10071 | 122.8867 | 122.8729 | 62.7823 | -122.9874 | 122.9095 | 122.8043 | 57.9346 | -123.0881
1164.5156 | 123.2208 | -58.6807 | 64.1739 | -0.018311 | 0.0062635 | 0.069081 | 0.066014 | 0.12785 | -0.0023648 | -0.0047103 | -0.011978 | -0.0051868 | -0.0025272 | -0.0009634 | 0.0036914 | -0.0068787 | 64.1785 | 64.3478 | 4.0695 | -58.8318 | 64.183 | -58.7357 | -58.7814 | -58.461 | -0.75989 | -58.8638 | 64.1739 | 64.1006 | -58.7631 | -58.8821 | -0.054932 | -0.10071 | 0.009155 | 123.0286 | -0.15106 | -0.050354 | 0.004578 | -0.082398 | -0.20142 | 0 | 0.21973 | -0.18311 | 0.01831 | -0.073242 | 122.8638 | 122.8592 | 62.7502 | -122.9553 | 122.8546 | 122.7814 | 57.9208 | -123.056
1165.5156 | 123.1522 | -58.699 | 64.1968 | -0.13275 | 0.0079723 | 0.068013 | 0.069218 | 0.12827 | 0.00041235 | -0.0030013 | -0.088272 | -0.003905 | -0.0050906 | -0.0033134 | 0.0036914 | -0.0068787 | 64.1922 | 64.3707 | 4.1473 | -58.786 | 64.183 | -58.7311 | -58.7769 | -58.4885 | -0.76446 | -58.8821 | 64.1968 | 64.0869 | -58.786 | -58.8593 | -0.032043 | -0.077819 | -0.013733 | 123.0698 | -0.086975 | -0.009156 | -0.004577 | -0.086975 | -0.16022 | 0 | 0.21057 | -0.1831 | -0.022888 | -0.10986 | 122.8821 | 122.8912 | 62.8464 | -122.9736 | 122.8958 | 122.7859 | 57.9346 | -123.056
1166.5156 | 123.1842 | -58.6853 | 64.1968 | 0.0045777 | 0.0069043 | 0.068227 | 0.067296 | 0.12571 | -0.00065585 | -0.0017197 | 0.094833 | -0.0058276 | -0.0055178 | 0.0003182 | 0.002196 | -0.0045289 | 64.1418 | 64.3433 | 4.184 | -58.8135 | 64.1922 | -58.7265 | -58.7677 | -58.4702 | -0.80566 | -58.8913 | 64.1922 | 64.0869 | -58.786 | -58.8913 | -0.041198 | -0.082397 | -0.004577 | 123.0286 | -0.12817 | -0.045777 | -0.054931 | -0.10071 | -0.20599 | -0.004577 | 0.21515 | -0.20599 | 0 | -0.10986 | 122.8775 | 122.8271 | 62.8693 | -122.9645 | 122.8775 | 122.7722 | 57.8796 | -123.0881
1167.5156 | 123.1796 | -58.6945 | 64.2059 | -0.26245 | 0.0083997 | 0.065663 | 0.069859 | 0.13084 | 0.00019875 | -0.0019333 | -0.080643 | -0.0058276 | -0.0044498 | -0.0020316 | 0.001128 | -0.0055969 | 64.2014 | 64.3707 | 4.2297 | -58.7906 | 64.1876 | -58.7357 | -58.754 | -58.4885 | -0.75073 | -58.873 | 64.1968 | 64.0823 | -58.7906 | -58.8593 | -0.041199 | -0.059509 | -0.018311 | 123.0652 | -0.09613 | -0.036621 | -0.004578 | -0.09613 | -0.1648 | -0.009156 | 0.20599 | -0.17853 | -0.013733 | -0.1236 | 122.8821 | 122.8958 | 62.9242 | -122.9599 | 122.8912 | 122.7768 | 57.9437 | -123.0652
1168.5156 | 123.1705 | -58.6624 | 64.2288 | -0.064087 | 0.0071179 | 0.067586 | 0.067936 | 0.1255 | 0.00062595 | -0.0023605 | -0.042496 | -0.0075366 | -0.0016726 | -0.0022452 | 0.0036914 | -0.0053833 | 64.1922 | 64.3936 | 4.2252 | -58.7906 | 64.2014 | -58.7219 | -58.7585 | -58.429 | -0.74616 | -58.8364 | 64.1968 | 64.0778 | -58.7952 | -58.8547 | -0.059509 | -0.09613 | -0.027466 | 123.056 | -0.12817 | -0.032043 | -0.036621 | -0.13275 | -0.19226 | -0.032044 | 0.23346 | -0.17395 | 0.01831 | -0.15106 | 122.8638 | 122.8546 | 62.8876 | -122.9874 | 122.8592 | 122.7402 | 57.9163 | -123.0835
1169.5156 | 123.1888 | -58.6624 | 64.2105 | -0.018311 | 0.0073315 | 0.069509 | 0.066655 | 0.12806 | -0.00065585 | -0.0021469 | -0.019608 | -0.006255 | -0.0025272 | -0.0030996 | 0.00048697 | -0.0051697 | 64.183 | 64.3753 | 4.2114 | -58.7769 | 64.2014 | -58.7082 | -58.7631 | -58.429 | -0.79193 | -58.8409 | 64.2151 | 64.0778 | -58.7906 | -58.8547 | -0.045776 | -0.10071 | -0.009155 | 123.0377 | -0.11444 | -0.013732 | -0.027466 | -0.12817 | -0.19226 | 0.004578 | 0.23346 | -0.17853 | 0.013733 | -0.13275 | 122.8638 | 122.8455 | 62.8738 | -122.9736 | 122.8775 | 122.7402 | 57.8705 | -123.0652
1170.5156 | 123.1247 | -58.7036 | 64.2059 | 0.035095 | 0.0083997 | 0.071004 | 0.0705 | 0.12571 | -0.00044225 | -0.00086512 | 0.11009 | -0.0047596 | -0.003168 | -0.000109 | 0.0019824 | -0.0062379 | 64.1281 | 64.3066 | 4.1519 | -58.8318 | 64.2014 | -58.7219 | -58.786 | -58.493 | -0.85144 | -58.9005 | 64.1922 | 64.0961 | -58.7677 | -58.873 | -0.018311 | -0.082398 | -0.004578 | 123.0103 | -0.12817 | -0.045776 | -0.07782 | -0.064087 | -0.16937 | -0.013733 | 0.21057 | -0.19684 | -0.027466 | -0.10986 | 122.905 | 122.8317 | 62.8555 | -122.9919 | 122.8958 | 122.7997 | 57.8522 | -123.0789
1171.5156 | 123.1979 | -58.6761 | 64.1922 | -0.1709 | 0.0043409 | 0.066518 | 0.06815 | 0.12977 | -0.00086945 | -0.0042831 | -0.0043486 | -0.0041186 | -0.0044498 | -0.0026724 | 0.0026234 | -0.0055969 | 64.2197 | 64.4073 | 4.2572 | -58.7723 | 64.2151 | -58.699 | -58.754 | -58.5892 | -0.97961 | -58.8318 | 64.1922 | 64.0732 | -58.7769 | -58.8867 | -0.022889 | -0.07782 | 0.022888 | 123.0835 | -0.096131 | -0.018311 | 0.027466 | -0.10071 | -0.21057 | 0 | 0.086975 | -0.15564 | 0.054932 | -0.11902 | 122.8912 | 122.8958 | 62.9333 | -122.9462 | 122.8683 | 122.7493 | 57.6965 | -123.0789
1172.5156 | 123.1796 | -58.6578 | 64.1785 | -0.010681 | 0.0096813 | 0.069295 | 0.068791 | 0.12678 | 0.00041235 | -0.0042831 | 0.079574 | -0.005614 | -0.0016726 | -0.0009634 | 0.002837 | -0.0075195 | 64.1556 | 64.3478 | 4.1794 | -58.7906 | 64.2059 | -58.7173 | -58.7814 | -58.4793 | -0.84228 | -58.8776 | 64.2288 | 64.0778 | -58.7997 | -58.8684 | -0.059509 | -0.1236 | 0.027466 | 123.0057 | -0.13275 | -0.009155 | -0.022888 | -0.14191 | -0.21057 | 0.050354 | 0.17853 | -0.21973 | -0.009155 | -0.10071 | 122.8638 | 122.8134 | 62.8372 | -122.9599 | 122.8867 | 122.7356 | 57.8156 | -123.0469
1173.5156 | 123.2025 | -58.6395 | 64.2151 | -0.11749 | 0.0030591 | 0.069081 | 0.062596 | 0.12913 | -0.00065585 | -0.0019333 | 0.0032804 | -0.0058276 | -0.0040226 | -0.001818 | 0.0026234 | -0.0047425 | 64.238 | 64.3341 | 4.216 | -58.7585 | 64.1968 | -58.7357 | -58.7311 | -58.4335 | -0.75531 | -58.8501 | 64.2288 | 64.0915 | -58.7585 | -58.8501 | -0.096131 | -0.091553 | -0.018311 | 122.9736 | -0.11902 | -0.027466 | 0.022888 | -0.11902 | -0.21057 | 0.013733 | 0.20599 | -0.21057 | 0 | -0.1236 | 122.8363 | 122.8775 | 62.8555 | -122.9462 | 122.8683 | 122.731 | 57.8842 | -123.0652
1174.5156 | 123.1888 | -58.6349 | 64.2014 | -0.010681 | 0.0062635 | 0.0678 | 0.067936 | 0.12678 | 0.00019875 | -0.0030013 | 0.071945 | -0.0058276 | -0.0050906 | -0.0009634 | 0.00091437 | -0.0060243 | 64.1785 | 64.3616 | 4.1977 | -58.786 | 64.2197 | -58.7219 | -58.7677 | -58.429 | -0.80566 | -58.8501 | 64.2242 | 64.0823 | -58.7585 | -58.8638 | -0.086975 | -0.13275 | 0.018311 | 122.9965 | -0.15106 | -0.018311 | -0.022888 | -0.1236 | -0.22888 | 0.022888 | 0.20599 | -0.21515 | 0.013733 | -0.11902 | 122.8546 | 122.8134 | 62.8326 | -122.9691 | 122.8592 | 122.7173 | 57.8293 | -123.0652
1175.5156 | 123.1888 | -58.6716 | 64.1922 | 0.019836 | 0.0064771 | 0.071004 | 0.069859 | 0.12614 | -0.001083 | -0.0019333 | 0.049057 | -0.005614 | -0.0012454 | -0.0026724 | 0.0024096 | -0.0047425 | 64.1739 | 64.3478 | 4.216 | -58.7769 | 64.2014 | -58.6853 | -58.7494 | -58.4518 | -0.83771 | -58.8593 | 64.1968 | 64.0915 | -58.7723 | -58.8638 | -0.013733 | -0.07782 | 0.009155 | 123.0194 | -0.10528 | -0.027465 | -0.018311 | -0.10071 | -0.19226 | 0.004577 | 0.21973 | -0.18768 | 0.004578 | -0.10071 | 122.8729 | 122.8455 | 62.8876 | -122.9416 | 122.8683 | 122.7631 | 57.8339 | -123.056
1176.5156 | 123.1155 | -58.6807 | 64.2014 | 0.18768 | 0.0090405 | 0.069509 | 0.066014 | 0.1287 | 0.0012668 | -0.0023605 | 0.26268 | -0.0054004 | -0.0050906 | -0.0013906 | 0.0019824 | -0.0038879 | 64.1693 | 64.3112 | 4.1611 | -58.8181 | 64.1647 | -58.7173 | -58.7769 | -58.4747 | -0.91095 | -58.9279 | 64.2151 | 64.1006 | -58.7677 | -58.8684 | -0.036621 | -0.09613 | -0.036621 | 122.9919 | -0.13733 | -0.041199 | -0.032043 | -0.086975 | -0.18768 | 0.013733 | 0.20599 | -0.24719 | -0.059509 | -0.10071 | 122.8455 | 122.85 | 62.8418 | -122.9782 | 122.8958 | 122.7814 | 57.7698 | -123.0698
1177.5156 | 123.1613 | -58.6258 | 64.1968 | -0.018311 | 0.0064771 | 0.071431 | 0.070714 | 0.13126 | -0.0017238 | -0.0010787 | 0.041427 | -0.005614 | -0.0042362 | -0.0009634 | 0.0030506 | -0.0068787 | 64.2197 | 64.357 | 4.2297 | -58.7585 | 64.1922 | -58.6899 | -58.7677 | -58.4015 | -0.81482 | -58.8455 | 64.2288 | 64.1052 | -58.7357 | -58.8638 | -0.064087 | -0.14191 | -0.004577 | 122.9828 | -0.13275 | 0.009155 | 0.022889 | -0.10986 | -0.23804 | 0.032044 | 0.2243 | -0.21973 | 0.018311 | -0.091552 | 122.818 | 122.8455 | 62.8555 | -122.9645 | 122.8546 | 122.731 | 57.811 | -123.0606
1178.5156 | 123.1476 | -58.6533 | 64.2197 | 0.15717 | 0.0066907 | 0.069081 | 0.067936 | 0.12956 | 0.0014804 | -0.0030013 | 0.20164 | -0.0034778 | -0.0025272 | -0.0013906 | 0.001128 | -0.0083741 | 64.1647 | 64.3112 | 4.2023 | -58.8181 | 64.1785 | -58.7173 | -58.7585 | -58.4656 | -0.89722 | -58.9005 | 64.2105 | 64.1098 | -58.7952 | -58.8364 | -0.064087 | -0.10529 | -0.041199 | 122.9645 | -0.16479 | -0.059509 | -0.054932 | -0.14191 | -0.18311 | -0.009156 | 0.18768 | -0.24719 | -0.064087 | -0.10986 | 122.8317 | 122.818 | 62.8555 | -122.9782 | 122.8638 | 122.7631 | 57.756 | -123.056
1179.5156 | 123.1842 | -58.6578 | 64.2105 | -0.033569 | 0.0062635 | 0.069936 | 0.068364 | 0.12785 | -0.0012966 | -0.0021469 | 0.049057 | -0.0071094 | -0.0033816 | -0.0024588 | 0.0032642 | -0.0055969 | 64.2197 | 64.3845 | 4.2801 | -58.754 | 64.2105 | -58.6807 | -58.7494 | -58.3786 | -0.75531 | -58.8043 | 64.2105 | 64.1098 | -58.7448 | -58.8318 | -0.022888 | -0.091553 | 0 | 123.0423 | -0.09613 | -0.004577 | 0.009156 | -0.086975 | -0.17395 | 0 | 0.27924 | -0.14648 | 0.027466 | -0.10071 | 122.8683 | 122.8775 | 62.9379 | -122.9599 | 122.8683 | 122.7676 | 57.9025 | -123.0423
1180.5156 | 123.143 | -58.6899 | 64.2014 | 0.14954 | 0.0077587 | 0.069295 | 0.067723 | 0.12913 | -0.0019376 | -0.0032151 | 0.14824 | -0.0049732 | -0.0025272 | -0.0043814 | 0.0026234 | -0.0055969 | 64.1556 | 64.3204 | 4.1885 | -58.8043 | 64.1922 | -58.6945 | -58.7448 | -58.5388 | -0.90637 | -58.9005 | 64.2014 | 64.0823 | -58.7906 | -58.873 | -0.004578 | -0.054932 | -0.009155 | 123.0103 | -0.11444 | -0.059509 | -0.045776 | -0.10071 | -0.18311 | 0 | 0.15106 | -0.21057 | -0.027466 | -0.11902 | 122.8821 | 122.8455 | 62.8784 | -122.9462 | 122.8912 | 122.7722 | 57.7835 | -123.0743
1181.5156 | 123.1842 | -58.6487 | 64.2334 | 0.0045777 | 0.0079723 | 0.06844 | 0.067296 | 0.1302 | 0.00083955 | -0.0012923 | 0.056686 | -0.0058276 | -0.0029544 | -0.0009634 | -0.00036743 | -0.0077331 | 64.2014 | 64.3753 | 4.2206 | -58.7494 | 64.2105 | -58.6899 | -58.7677 | -58.4152 | -0.83313 | -58.8318 | 64.2471 | 64.1144 | -58.7448 | -58.8409 | -0.041198 | -0.11902 | -0.022888 | 123.024 | -0.10071 | 0.01831 | -0.032043 | -0.09613 | -0.19226 | 0.013733 | 0.23346 | -0.1831 | 0.009155 | -0.11902 | 122.8592 | 122.85 | 62.8693 | -123.0011 | 122.8958 | 122.7631 | 57.8156 | -123.0743
1182.5156 | 123.1567 | -58.6853 | 64.2014 | 0.21057 | 0.010963 | 0.067372 | 0.065587 | 0.12849 | 0.0031894 | -0.0012923 | 0.24742 | -0.0043324 | -0.001459 | 0.0001046 | 0.0032642 | -0.0079469 | 64.183 | 64.3616 | 4.2114 | -58.7814 | 64.1876 | -58.7402 | -58.7494 | -58.4152 | -0.85144 | -58.8821 | 64.2059 | 64.0915 | -58.7814 | -58.873 | -0.054931 | -0.064087 | -0.013733 | 123.0469 | -0.09613 | -0.032043 | -0.018311 | -0.09613 | -0.18768 | 0.004578 | 0.27008 | -0.19684 | -0.009155 | -0.10986 | 122.8729 | 122.8683 | 62.8967 | -122.9507 | 122.8912 | 122.7768 | 57.8339 | -123.0743
1183.5156 | 123.1842 | -58.6395 | 64.2242 | 0.09613 | 0.0077587 | 0.0678 | 0.067936 | 0.12721 | -1.505e-05 | -0.0027877 | 0.11009 | -0.0047596 | -0.003168 | -0.002886 | 5.9768e-05 | -0.0066651 | 64.1647 | 64.325 | 4.184 | -58.7814 | 64.2014 | -58.6807 | -58.754 | -58.4381 | -0.82398 | -58.8638 | 64.2288 | 64.119 | -58.7631 | -58.8455 | -0.041199 | -0.11444 | -0.022888 | 122.9645 | -0.14191 | -0.027466 | -0.059509 | -0.1236 | -0.20599 | 0.004578 | 0.20142 | -0.22431 | -0.018311 | -0.10528 | 122.8409 | 122.8043 | 62.8235 | -122.9782 | 122.8683 | 122.7585 | 57.8156 | -123.0698
1184.5156 | 123.1567 | -58.6807 | 64.1647 | 0.14954 | 0.011604 | 0.066091 | 0.069005 | 0.12977 | 0.00041235 | -0.0012923 | 0.26268 | -0.0041186 | -0.0021 | -0.001177 | 0.0036914 | -0.0081605 | 64.2105 | 64.357 | 4.2114 | -58.7814 | 64.1647 | -58.699 | -58.7585 | -58.4198 | -0.83771 | -58.8776 | 64.238 | 64.0915 | -58.7769 | -58.8638 | -0.018311 | -0.07782 | 0 | 123.0377 | -0.10071 | -0.022888 | 0.045776 | -0.09613 | -0.18311 | 0.073242 | 0.26093 | -0.19684 | -0.013732 | -0.073242 | 122.8455 | 122.8912 | 62.8922 | -122.9233 | 122.9187 | 122.7722 | 57.843 | -123.0286
1185.5156 | 123.1247 | -58.6533 | 64.2105 | 0.035095 | 0.0071179 | 0.066945 | 0.068364 | 0.12657 | -0.00065585 | -0.0010787 | -0.34004 | -0.0036914 | -0.0025272 | -0.0024588 | 0.0013416 | -0.0055969 | 64.1602 | 64.325 | 4.1885 | -58.7631 | 64.2334 | -58.6853 | -58.7402 | -58.4656 | -0.88806 | -58.8959 | 64.2334 | 64.1144 | -58.7769 | -58.8318 | -0.032044 | -0.086975 | 0.022888 | 122.9782 | -0.10986 | -0.022889 | -0.050354 | -0.1236 | -0.17853 | 0.022888 | 0.18768 | -0.24262 | -0.064087 | -0.09613 | 122.8867 | 122.8134 | 62.8418 | -122.9507 | 122.8867 | 122.7676 | 57.7652 | -123.0423
1186.5156 | 123.1064 | -58.6441 | 64.1785 | 0.17242 | 0.010322 | 0.069295 | 0.066014 | 0.1287 | 0.00062595 | -0.0010787 | 0.28557 | -0.0026234 | -0.001459 | -0.0030996 | 0.0032642 | -0.0055969 | 64.2059 | 64.3616 | 4.1885 | -58.7585 | 64.1968 | -58.7036 | -58.7585 | -58.4198 | -0.85144 | -58.8959 | 64.2242 | 64.1052 | -58.7631 | -58.8547 | -0.059509 | -0.11444 | 0.01831 | 123.0057 | -0.11444 | 0 | 0.027466 | -0.11902 | -0.21057 | 0.045776 | 0.2243 | -0.25177 | -0.041199 | -0.073242 | 122.8409 | 122.85 | 62.8326 | -122.937 | 122.8683 | 122.7493 | 57.7927 | -123.0331
1187.5156 | 123.143 | -58.6487 | 64.2288 | -0.42267 | 0.0064771 | 0.068868 | 0.069645 | 0.12699 | -0.00044225 | -0.0036423 | 0.12535 | -0.0047596 | -0.0033816 | -0.0024588 | 0.0015552 | -0.0049561 | 64.1418 | 64.3158 | 4.1931 | -58.7769 | 64.2059 | -58.699 | -58.754 | -58.429 | -0.84686 | -58.8776 | 64.2426 | 64.1098 | -58.7723 | -58.8409 | -0.050354 | -0.10529 | -0.022888 | 122.9645 | -0.12817 | -0.022888 | -0.086975 | -0.1236 | -0.19226 | 0.013733 | 0.21973 | -0.22888 | -0.036621 | -0.11902 | 122.8546 | 122.7905 | 62.8418 | -122.9828 | 122.8912 | 122.7585 | 57.8018 | -123.0698
1188.5156 | 123.1384 | -58.6624 | 64.1922 | 0.15717 | 0.012672 | 0.063527 | 0.068791 | 0.12614 | 0.002335 | -1.0724e-05 | 0.23979 | -0.0036914 | -0.003168 | 0.0001046 | 0.0030506 | -0.0066651 | 64.2151 | 64.357 | 4.2572 | -58.7677 | 64.1876 | -58.7265 | -58.7357 | -58.3969 | -0.81024 | -58.873 | 64.2288 | 64.1052 | -58.7723 | -58.8684 | -0.064086 | -0.073242 | -0.004578 | 123.0194 | -0.10528 | -0.032043 | 0.022888 | -0.10986 | -0.20599 | 0.036621 | 0.2655 | -0.21057 | -0.004578 | -0.086975 | 122.85 | 122.8775 | 62.9196 | -122.9279 | 122.8912 | 122.7676 | 57.8522 | -123.0606
1189.5156 | 123.1247 | -58.6487 | 64.2014 | 0.17242 | 0.0096813 | 0.067159 | 0.067509 | 0.12849 | 0.00083955 | -0.0012923 | 0.23979 | -0.0043324 | -0.0035952 | -0.0003226 | 0.0054004 | -0.0034607 | 64.1922 | 64.357 | 4.2572 | -58.7723 | 64.1922 | -58.6853 | -58.7311 | -58.3969 | -0.84228 | -58.8821 | 64.2197 | 64.1006 | -58.7814 | -58.8593 | -0.036621 | -0.082397 | -0.009155 | 123.0057 | -0.1236 | -0.041199 | -0.009155 | -0.13275 | -0.21057 | 0.018311 | 0.25177 | -0.23346 | -0.022888 | -0.10071 | 122.8409 | 122.8409 | 62.9059 | -122.9324 | 122.8683 | 122.7493 | 57.8064 | -123.0606
1190.5156 | 123.1888 | -58.6395 | 64.1968 | 0.24109 | 0.013313 | 0.071004 | 0.069859 | 0.12614 | 0.0025486 | 0.00063028 | 0.28557 | -0.0054004 | -0.0029544 | -0.0003226 | 0.005614 | -0.0079469 | 64.2197 | 64.3295 | 4.2801 | -58.7585 | 64.2151 | -58.7036 | -58.7631 | -58.3878 | -0.80109 | -58.873 | 64.2242 | 64.119 | -58.7677 | -58.8455 | -0.064087 | -0.1236 | 0.018311 | 122.9691 | -0.11902 | 0.004578 | 0.022889 | -0.12817 | -0.20599 | 0.027466 | 0.25177 | -0.23346 | -0.027466 | -0.077819 | 122.8546 | 122.8592 | 62.9196 | -122.9599 | 122.8638 | 122.7585 | 57.8384 | -123.0423
1191.5156 | 123.1613 | -58.6441 | 64.2197 | 0.14191 | 0.0075451 | 0.071004 | 0.067082 | 0.1287 | -0.0025784 | -0.0012923 | 0.1635 | -0.003905 | -0.0025272 | -0.0039542 | 0.0013416 | -0.0047425 | 64.1785 | 64.3341 | 4.3304 | -58.7997 | 64.2059 | -58.699 | -58.7402 | -58.4198 | -0.80109 | -58.8821 | 64.2517 | 64.151 | -58.7585 | -58.8226 | -0.054932 | -0.09613 | -0.013733 | 122.9782 | -0.15564 | -0.05951 | -0.041199 | -0.11444 | -0.17853 | 0.032043 | 0.2243 | -0.23804 | -0.059509 | -0.068665 | 122.85 | 122.8226 | 62.9745 | -122.9599 | 122.8958 | 122.7951 | 57.843 | -123.0423
1192.5156 | 123.175 | -58.6487 | 64.2014 | 0.17242 | 0.010536 | 0.068227 | 0.071568 | 0.12849 | 0.0012668 | -0.0021469 | 0.22453 | -0.0041186 | -0.0029544 | -0.0026724 | 0.0047596 | -0.0079469 | 64.2151 | 64.3936 | 4.3396 | -58.9142 | 64.151 | -58.7173 | -58.786 | -58.3511 | -0.79193 | -58.8638 | 64.2151 | 64.1052 | -58.7631 | -58.8318 | -0.068664 | -0.13733 | -0.050354 | 123.0423 | -0.2655 | -0.12817 | 0.013733 | -0.11444 | -0.1831 | 0.013733 | 0.29755 | -0.21515 | -0.032044 | -0.09613 | 122.7997 | 122.8638 | 62.9883 | -122.9874 | 122.8638 | 122.7539 | 57.8568 | -123.0331
1193.5156 | 123.1155 | -58.6533 | 64.238 | 0.088501 | 0.0060497 | 0.068654 | 0.066227 | 0.12763 | -0.0017238 | -0.0025741 | -0.24849 | -0.0030506 | -0.0023136 | -0.001818 | 0.00091437 | -0.0036743 | 64.0778 | 64.6408 | 4.5685 | -58.7723 | 64.238 | -58.6761 | -58.7265 | -58.4335 | -0.78735 | -58.8913 | 64.238 | 64.1373 | -58.7494 | -58.8547 | -0.022888 | -0.073242 | 0 | 123.2941 | -0.11902 | -0.045777 | -0.16022 | -0.096131 | -0.20142 | 0 | 0.21973 | -0.23804 | -0.036621 | -0.10071 | 122.8912 | 122.731 | 63.2217 | -122.9645 | 122.8912 | 122.7905 | 57.8659 | -123.0927
1194.5156 | 123.1384 | -58.6441 | 64.2746 | -0.17853 | 0.0098951 | 0.068227 | 0.067936 | 0.12849 | 0.0010532 | -0.0015061 | -0.095902 | -0.0043324 | -0.003168 | -0.0024588 | 0.0034778 | -0.0064515 | 64.2471 | 64.4165 | 4.5319 | -58.6945 | 64.238 | -58.6578 | -58.7265 | -58.3603 | -0.68207 | -58.8318 | 64.2883 | 64.1556 | -58.7402 | -58.7997 | -0.013733 | -0.082397 | -0.036621 | 123.0606 | -0.050354 | 0.032043 | -0.027466 | -0.09613 | -0.15564 | 0.013733 | 0.28381 | -0.18768 | -0.032043 | -0.11902 | 122.8821 | 122.8912 | 63.176 | -123.0011 | 122.9324 | 122.7997 | 57.962 | -123.0743
1195.5156 | 123.1293 | -58.667 | 64.238 | 0.11902 | 0.0079723 | 0.070363 | 0.06815 | 0.12827 | -0.00065585 | -0.0036423 | 0.14061 | -0.0064686 | -0.0046634 | -0.0022452 | 0.0019824 | -0.0053833 | 64.1693 | 64.325 | 4.5181 | -58.7631 | 64.2242 | -58.6807 | -58.7402 | -58.4198 | -0.75531 | -58.7997 | 64.2883 | 64.1556 | -58.7128 | -58.8409 | -0.013733 | -0.073242 | -0.013733 | 122.9919 | -0.096131 | -0.022889 | -0.068664 | -0.045777 | -0.17395 | 0.050354 | 0.24719 | -0.13275 | 0.041198 | -0.082397 | 122.8912 | 122.8363 | 63.1851 | -122.9782 | 122.9553 | 122.8226 | 57.9117 | -123.0789
1196.5156 | 123.1979 | -58.6487 | 64.2197 | 0.22583 | 0.012245 | 0.066945 | 0.071782 | 0.12892 | 0.0036166 | 0.00063028 | 0.25505 | -0.0032642 | -0.0008182 | -0.0037406 | 0.003905 | -0.0077331 | 64.1968 | 64.3158 | 4.5593 | -58.7631 | 64.2151 | -58.7128 | -58.7723 | -58.3878 | -0.79651 | -58.8776 | 64.2517 | 64.0961 | -58.754 | -58.8226 | -0.064087 | -0.1236 | -0.004578 | 122.9645 | -0.11444 | 0.009155 | -0.022889 | -0.10529 | -0.17395 | 0.032043 | 0.26093 | -0.22888 | -0.054931 | -0.1236 | 122.8638 | 122.8455 | 63.208 | -122.9919 | 122.9004 | 122.7448 | 57.8522 | -123.0423
1197.5156 | 123.1522 | -58.6487 | 64.2059 | 0.24109 | 0.010322 | 0.068227 | 0.069859 | 0.12934 | 0.001694 | -0.00043792 | 0.26268 | -0.0032642 | -0.0040226 | -0.0024588 | 0.0036914 | -0.0064515 | 64.2288 | 64.3799 | 4.6509 | -58.7402 | 64.1922 | -58.7036 | -58.7219 | -58.3511 | -0.70038 | -58.8501 | 64.2242 | 64.1098 | -58.7494 | -58.8547 | -0.054931 | -0.073242 | -0.013733 | 123.0286 | -0.091552 | -0.01831 | 0.022888 | -0.10071 | -0.20599 | 0.01831 | 0.29755 | -0.20142 | 0.004577 | -0.096131 | 122.8409 | 122.8775 | 63.2996 | -122.9279 | 122.8729 | 122.7585 | 57.9483 | -123.0606
1198.5156 | 123.1796 | -58.6395 | 64.2288 | 0.29449 | 0.013099 | 0.066945 | 0.069432 | 0.12977 | 0.00041235 | -1.0724e-05 | 0.24742 | -0.0032642 | -0.0025272 | -0.001177 | 0.005614 | -0.0055969 | 64.2471 | 64.3662 | 4.6738 | -58.7311 | 64.2471 | -58.699 | -58.7219 | -58.3878 | -0.47607 | -58.7952 | 64.2288 | 64.1373 | -58.7402 | -58.8135 | -0.05951 | -0.082398 | 0.01831 | 123.0057 | -0.091553 | -0.009155 | 0.01831 | -0.10071 | -0.17395 | 0 | 0.25177 | -0.15564 | 0.018311 | -0.091553 | 122.8867 | 122.8867 | 63.3133 | -122.9507 | 122.8683 | 122.7768 | 58.1635 | -123.0423
1199.5156 | 123.0789 | -58.6487 | 64.2792 | -0.21667 | 0.011177 | 0.067372 | 0.066655 | 0.12977 | 0.0010532 | -0.0010787 | -0.095902 | -0.00070077 | -0.0010318 | -0.0003226 | 0.0026234 | -0.0064515 | 64.2242 | 64.3753 | 4.7012 | -58.7173 | 64.2883 | -58.6533 | -58.7357 | -58.4061 | -0.67749 | -58.8959 | 64.3021 | 64.2014 | -58.7173 | -58.8181 | -0.004577 | -0.086975 | 0.009155 | 123.024 | -0.068664 | 0.018311 | -0.054932 | -0.068664 | -0.16937 | 0.022888 | 0.24262 | -0.24719 | -0.07782 | -0.07782 | 122.937 | 122.8729 | 63.3499 | -123.0148 | 122.9507 | 122.85 | 57.9712 | -123.0972
1200.5156 | 123.1522 | -58.6578 | 64.2151 | 0.56915 | 0.010322 | 0.069081 | 0.069859 | 0.12827 | 0.001694 | -0.00065152 | 0.30083 | -0.0032642 | -0.0027408 | -0.0016044 | 0.0041186 | -0.0066651 | 64.2517 | 64.3799 | 4.7699 | -58.7265 | 64.2014 | -58.6807 | -58.7128 | -58.3511 | -0.66834 | -58.8318 | 64.2334 | 64.1281 | -58.7448 | -58.8272 | -0.022888 | -0.054932 | -0.013733 | 123.0377 | -0.068664 | -0.013732 | 0.036621 | -0.086975 | -0.16937 | 0.01831 | 0.3067 | -0.17395 | -0.004578 | -0.086975 | 122.8592 | 122.9095 | 63.4277 | -122.9279 | 122.8912 | 122.7859 | 57.9895 | -123.0423
1201.5156 | 123.1567 | -58.6258 | 64.2609 | 0.14191 | 0.0077587 | 0.066945 | 0.066868 | 0.1287 | -0.0021512 | -0.0021469 | 0.1635 | -0.004546 | -0.0035952 | -0.003527 | 0.00091437 | -0.0058105 | 64.1922 | 64.3524 | 4.7562 | -58.7357 | 64.2288 | -58.6624 | -58.7265 | -58.3878 | -0.66376 | -58.873 | 64.2654 | 64.1602 | -58.7265 | -58.8135 | -0.036622 | -0.10071 | -0.032043 | 122.9782 | -0.10986 | -0.009156 | -0.068664 | -0.10071 | -0.18768 | 0.004578 | 0.23804 | -0.24719 | -0.059509 | -0.10071 | 122.8546 | 122.818 | 63.382 | -122.9874 | 122.8912 | 122.7859 | 57.962 | -123.0743
1202.5156 | 123.1384 | -58.6121 | 64.2197 | 0.24109 | 0.012672 | 0.068654 | 0.07285 | 0.13041 | 0.002335 | 0.0010575 | 0.36949 | -0.0036914 | -0.0035952 | -0.0003226 | 0.0043324 | -0.0047425 | 64.2426 | 64.3845 | 4.8523 | -58.7997 | 64.2151 | -58.6945 | -58.7357 | -58.3099 | -0.60425 | -58.8409 | 64.2563 | 64.119 | -58.7448 | -58.7952 | -0.082397 | -0.1236 | -0.004578 | 122.9965 | -0.18768 | -0.064087 | 0.022888 | -0.13275 | -0.18311 | 0.036621 | 0.30212 | -0.22888 | -0.045776 | -0.10071 | 122.8271 | 122.8546 | 63.4644 | -122.9553 | 122.8683 | 122.731 | 58.0078 | -123.0148
1203.5156 | 123.1522 | -58.5388 | 64.2883 | 0.14954 | 0.0077587 | 0.069081 | 0.066655 | 0.12742 | -0.00044225 | -0.0012923 | 0.23216 | -0.0041186 | -0.0021 | 0.0018136 | 0.0019824 | -0.0051697 | 64.2929 | 64.4257 | 5.0446 | -58.6624 | 64.2654 | -58.5983 | -58.6487 | -58.3008 | -0.47607 | -58.7952 | 64.325 | 64.238 | -58.6578 | -58.7723 | -0.05951 | -0.10986 | -0.022888 | 122.9645 | -0.1236 | -0.013733 | 0.004578 | -0.11902 | -0.23346 | 0.036621 | 0.23804 | -0.25635 | -0.022888 | -0.050354 | 122.8043 | 122.8317 | 63.5834 | -122.937 | 122.8638 | 122.7768 | 58.0627 | -123.0606
1204.5156 | 123.1934 | -58.5159 | 64.3478 | -0.15564 | 0.0071179 | 0.068227 | 0.068791 | 0.12956 | -0.0015102 | -0.0010787 | 0.30846 | -0.0049732 | -0.0035952 | -0.0007498 | 0.003905 | -0.0045289 | 64.3112 | 64.9796 | 5.452 | -58.6533 | 64.3616 | -58.548 | -58.6212 | -58.2413 | -0.32501 | -58.7082 | 64.357 | 64.2609 | -58.6258 | -58.7357 | -0.032044 | -0.10529 | 0.013733 | 123.4955 | -0.13733 | -0.032043 | -0.036621 | -0.10986 | -0.21973 | 0.009156 | 0.27466 | -0.19226 | 0.027466 | -0.086975 | 122.8775 | 122.8271 | 63.9679 | -122.9691 | 122.8729 | 122.7768 | 58.1909 | -123.0835
1205.5156 | 123.1338 | -58.5571 | 64.2838 | 0.21057 | 0.0073315 | 0.069509 | 0.067509 | 0.12977 | 0.001694 | -0.0017197 | 0.26268 | -0.0064686 | -0.003168 | -0.001177 | 0.0030506 | -0.0036743 | 64.2975 | 64.444 | 5.2048 | -58.6624 | 64.27 | -58.6166 | -58.6304 | -58.2733 | -0.41199 | -58.7952 | 64.3066 | 64.2014 | -58.6853 | -58.7723 | -0.059509 | -0.073242 | -0.013732 | 123.0011 | -0.10529 | -0.032044 | 0.013733 | -0.12817 | -0.21515 | 0.022889 | 0.28381 | -0.23804 | -0.022888 | -0.082397 | 122.8271 | 122.8546 | 63.7619 | -122.9141 | 122.8638 | 122.7585 | 58.1451 | -123.056
1206.5156 | 123.1796 | -58.5709 | 64.2792 | 0.24872 | 0.014168 | 0.068227 | 0.069218 | 0.12592 | 0.0025486 | 0.0012711 | 0.19402 | -0.0047596 | -0.0023136 | -0.0039542 | 0.003905 | -0.0079469 | 64.2838 | 64.3936 | 5.2231 | -58.667 | 64.2975 | -58.6212 | -58.6624 | -58.287 | -0.40283 | -58.7997 | 64.3295 | 64.1876 | -58.6853 | -58.7585 | -0.050354 | -0.091553 | 0.01831 | 122.9645 | -0.09613 | -0.004577 | 0.004577 | -0.11444 | -0.18768 | 0.050354 | 0.28381 | -0.22888 | -0.041199 | -0.091553 | 122.8683 | 122.8546 | 63.7939 | -122.9416 | 122.9004 | 122.7585 | 58.168 | -123.0377
1207.5156 | 123.1155 | -58.5754 | 64.2929 | 0.17242 | 0.0071179 | 0.067586 | 0.066655 | 0.1287 | -0.002792 | -0.0019333 | 0.23216 | -0.0041186 | -0.0018862 | -0.002886 | 0.0013416 | -0.0041017 | 64.27 | 64.4119 | 5.3696 | -58.6853 | 64.3021 | -58.6121 | -58.667 | -58.2916 | -0.41657 | -58.7952 | 64.325 | 64.238 | -58.6578 | -58.7814 | -0.036622 | -0.091553 | 0.009155 | 122.9874 | -0.10986 | -0.018311 | -0.022888 | -0.082398 | -0.20599 | 0.032043 | 0.28381 | -0.21973 | -0.013733 | -0.054932 | 122.8775 | 122.8455 | 63.945 | -122.9599 | 122.9004 | 122.8134 | 58.1589 | -123.0743
1208.5156 | 123.1613 | -58.5754 | 64.2792 | 0.14954 | 0.012031 | 0.065877 | 0.069432 | 0.12892 | 0.0027622 | -0.00065152 | 0.27031 | -0.0036914 | -0.003168 | -0.0026724 | 0.0026234 | -0.0098695 | 64.3295 | 64.4211 | 5.5069 | -58.6304 | 64.2746 | -58.6212 | -58.6624 | -58.2275 | -0.42114 | -58.7585 | 64.3158 | 64.2059 | -58.667 | -58.7402 | -0.045777 | -0.086976 | -0.004578 | 122.9965 | -0.054932 | 0.032044 | 0.050354 | -0.091553 | -0.16479 | 0.036621 | 0.3479 | -0.18311 | -0.018311 | -0.073242 | 122.85 | 122.905 | 64.0823 | -122.9416 | 122.8912 | 122.7814 | 58.1543 | -123.0194
1209.5156 | 123.1613 | -58.5617 | 64.3387 | -0.16327 | 0.0092541 | 0.066945 | 0.065587 | 0.12956 | 0.0010532 | -0.00043792 | -0.095902 | -0.0036914 | -0.0050906 | -0.0020316 | 0.002196 | -0.0045289 | 64.3066 | 64.4897 | 5.777 | -58.6212 | 64.3158 | -58.5709 | -58.6304 | -58.2642 | -0.3479 | -58.7585 | 64.3341 | 64.2517 | -58.667 | -58.7311 | -0.009155 | -0.068664 | -0.022888 | 123.0515 | -0.059509 | 0.009155 | -0.032043 | -0.10529 | -0.16937 | -0.004578 | 0.29755 | -0.19684 | -0.027466 | -0.086975 | 122.8775 | 122.8683 | 64.3387 | -122.9691 | 122.8958 | 122.8134 | 58.2138 | -123.0698
1210.5156 | 123.1018 | -58.6166 | 64.2883 | 0.18005 | 0.014381 | 0.066518 | 0.069432 | 0.1287 | 0.0029758 | -0.0010787 | 0.17113 | -0.0043324 | -0.0012454 | -0.0022452 | 0.0058276 | -0.0068787 | 64.2105 | 64.3341 | 5.7724 | -58.7265 | 64.3341 | -58.667 | -58.699 | -58.342 | -0.50812 | -58.8684 | 64.3112 | 64.2105 | -58.7357 | -58.7952 | -0.050354 | -0.082398 | 0.045776 | 122.9507 | -0.10986 | -0.027465 | -0.07782 | -0.11902 | -0.17853 | 0.022888 | 0.27466 | -0.25177 | -0.073242 | -0.07782 | 122.9507 | 122.8271 | 64.389 | -122.9874 | 122.9279 | 122.8271 | 58.1085 | -123.0835
1211.5156 | 123.1247 | -58.5663 | 64.2654 | 0.19531 | 0.0090405 | 0.069081 | 0.0705 | 0.12934 | -0.0012966 | -0.0015061 | 0.32372 | -0.002196 | -0.0025272 | -0.0043814 | 0.001128 | -0.0030335 | 64.2563 | 64.4165 | 6.0654 | -58.6716 | 64.2563 | -58.6304 | -58.6945 | -58.2916 | -0.45776 | -58.8043 | 64.2654 | 64.1739 | -58.7082 | -58.8043 | -0.064087 | -0.12817 | -0.009155 | 122.9828 | -0.10529 | 0.022888 | -0.009155 | -0.14191 | -0.23804 | 0 | 0.27466 | -0.23804 | 0 | -0.091553 | 122.8226 | 122.8226 | 64.6317 | -122.9599 | 122.8317 | 122.7402 | 58.1085 | -123.0698
1212.5156 | 123.1934 | -58.6212 | 64.2426 | 0.23346 | 0.013313 | 0.066304 | 0.069645 | 0.12806 | 0.0031894 | -0.0010787 | 0.23979 | -0.0041186 | -0.0027408 | -0.0009634 | 0.0019824 | -0.0060243 | 64.2105 | 64.3021 | 6.0837 | -58.7357 | 64.2838 | -58.667 | -58.7082 | -58.3374 | -0.44861 | -58.8593 | 64.2929 | 64.1602 | -58.7357 | -58.8043 | -0.045776 | -0.086975 | 0.041198 | 122.9233 | -0.11444 | -0.027466 | -0.032044 | -0.11444 | -0.18311 | 0.050354 | 0.28381 | -0.23804 | -0.054932 | -0.082398 | 122.905 | 122.8317 | 64.7049 | -122.9507 | 122.9141 | 122.7814 | 58.1726 | -123.0469
1213.5156 | 123.1659 | -58.5983 | 64.2334 | 0.15717 | 0.010536 | 0.067586 | 0.067296 | 0.12934 | 0.001694 | 0.00041648 | 0.25505 | -0.003905 | -0.0044498 | -0.0016044 | 0.0017688 | -0.0038879 | 64.2609 | 64.3982 | 6.2622 | -58.6899 | 64.2288 | -58.6716 | -58.6945 | -58.287 | -0.42572 | -58.8089 | 64.2746 | 64.1876 | -58.7311 | -58.8181 | -0.073242 | -0.09613 | -0.004577 | 122.9965 | -0.091552 | 0.004578 | 0.027466 | -0.13275 | -0.21973 | 0.041199 | 0.31128 | -0.21057 | 0.009155 | -0.045776 | 122.8271 | 122.8592 | 64.8605 | -122.9279 | 122.8729 | 122.786 | 58.1726 | -123.0515
1214.5156 | 123.1293 | -58.6304 | 64.1968 | 0.20294 | 0.013313 | 0.0678 | 0.069432 | 0.12763 | 0.0027622 | -0.00065152 | 0.23216 | -0.0032642 | -0.0012454 | -0.001818 | 0.0036914 | -0.0055969 | 64.2517 | 64.3387 | 6.3492 | -58.7082 | 64.2426 | -58.6807 | -58.7219 | -58.3054 | -0.46234 | -58.8318 | 64.2609 | 64.1693 | -58.7357 | -58.8043 | -0.050354 | -0.091553 | 0.045777 | 122.9691 | -0.07782 | 0.013733 | 0.054932 | -0.10529 | -0.17395 | 0.064087 | 0.32501 | -0.20142 | -0.027466 | -0.027465 | 122.8729 | 122.8821 | 64.9796 | -122.9187 | 122.8912 | 122.7997 | 58.168 | -123.0011
1215.5156 | 123.1659 | -58.6349 | 64.2334 | 0.17242 | 0.0096813 | 0.068013 | 0.066014 | 0.12849 | -0.0021512 | -0.00086512 | 0.24742 | -0.0036914 | -0.0033816 | -0.0016044 | 0.0024096 | -0.0038879 | 64.2288 | 64.4028 | 6.4453 | -58.6945 | 64.2242 | -58.6487 | -58.6945 | -58.3008 | -0.40283 | -58.8409 | 64.2517 | 64.1373 | -58.7402 | -58.8226 | -0.013733 | -0.059509 | -0.009155 | 123.0377 | -0.059509 | 0 | -0.004577 | -0.10529 | -0.18768 | 0.018311 | 0.33417 | -0.20599 | -0.01831 | -0.09613 | 122.8592 | 122.8638 | 65.0803 | -122.9279 | 122.8867 | 122.7722 | 58.2321 | -123.056
1216.5156 | 123.1476 | -58.6304 | 64.2654 | 0.18005 | 0.016304 | 0.065663 | 0.068364 | 0.12763 | 0.0014804 | -0.0025741 | 0.25505 | -0.0024096 | -0.0027408 | -0.0024588 | 0.0024096 | -0.0073059 | 64.2014 | 64.3112 | 6.4911 | -58.7265 | 64.2563 | -58.667 | -58.7219 | -58.3191 | -0.44403 | -58.873 | 64.2792 | 64.1602 | -58.7357 | -58.8272 | -0.036621 | -0.091553 | -0.009155 | 122.9416 | -0.09613 | -0.004577 | -0.064087 | -0.10529 | -0.19684 | 0.013733 | 0.31128 | -0.24262 | -0.045777 | -0.10529 | 122.8867 | 122.8317 | 65.1215 | -122.9874 | 122.9095 | 122.7905 | 58.1863 | -123.0927
1217.5156 | 123.1522 | -58.6349 | 64.2288 | 0.20294 | 0.0098951 | 0.066945 | 0.068577 | 0.12934 | -0.00065585 | 0.00041648 | 0.24742 | -0.0041186 | -0.0012454 | -0.0050222 | 0.0036914 | -0.0058105 | 64.2471 | 64.3982 | 6.6559 | -58.6899 | 64.2059 | -58.6807 | -58.7128 | -58.2916 | -0.37079 | -58.8181 | 64.2334 | 64.1464 | -58.754 | -58.8409 | -0.045776 | -0.07782 | -0.022888 | 123.0331 | -0.054931 | 0.022889 | 0.01831 | -0.11902 | -0.20599 | 0.004577 | 0.34332 | -0.1831 | 0.022888 | -0.082398 | 122.8409 | 122.8821 | 65.2908 | -122.9416 | 122.8683 | 122.7814 | 58.2642 | -123.0698
1218.5156 | 123.1522 | -58.6212 | 64.2197 | 0.21057 | 0.013313 | 0.066518 | 0.070927 | 0.12913 | 0.0027622 | -0.0012923 | 0.2932 | -0.0041186 | -0.0027408 | -0.0026724 | 0.002837 | -0.0034607 | 64.2059 | 64.3295 | 6.8161 | -58.7128 | 64.2426 | -58.7036 | -58.7173 | -58.287 | -0.40283 | -58.8318 | 64.2563 | 64.1693 | -58.7448 | -58.8089 | -0.082397 | -0.09613 | 0.022888 | 122.9507 | -0.091553 | 0.004577 | -0.013733 | -0.1236 | -0.18768 | 0.036621 | 0.33417 | -0.21057 | -0.022888 | -0.050354 | 122.8638 | 122.8271 | 65.4373 | -122.937 | 122.8775 | 122.7905 | 58.2184 | -123.0286
1219.5156 | 123.2117 | -58.6487 | 64.2151 | 0.18768 | 0.012459 | 0.067586 | 0.069005 | 0.13148 | 0.0010532 | -0.0025741 | 0.65941 | -0.0047596 | -0.0033816 | -0.001818 | 0.0030506 | -0.0055969 | 64.2288 | 64.3478 | 7.0175 | -58.6716 | 64.2197 | -58.7173 | -58.7723 | -58.2733 | -0.35248 | -58.8409 | 64.2426 | 64.1464 | -58.7402 | -58.8181 | -0.068664 | -0.1236 | 0.004578 | 122.9965 | -0.022888 | 0.10071 | 0.013733 | -0.091552 | -0.16937 | 0.027466 | 0.37537 | -0.19226 | -0.022888 | -0.068665 | 122.8683 | 122.8775 | 65.6662 | -122.9874 | 122.8912 | 122.7951 | 58.2962 | -123.0331
1220.5156 | 123.0606 | -58.6853 | 64.238 | 1.1566 | 0.015663 | 0.069722 | 0.070286 | 0.12785 | 0.0038304 | -0.00043792 | 0.2169 | -0.0041186 | -0.0012454 | -0.0013906 | 0.003905 | -0.0062379 | 64.1968 | 64.2151 | 7.077 | -58.7631 | 64.2792 | -58.7265 | -58.7585 | -58.3832 | -0.50354 | -58.9783 | 64.2929 | 64.1968 | -58.786 | -58.8867 | -0.041198 | -0.073242 | 0.041199 | 122.9004 | -0.07782 | -0.004578 | -0.041199 | -0.10071 | -0.20142 | 0.054932 | 0.30212 | -0.29297 | -0.091552 | -0.041199 | 122.9645 | 122.8821 | 65.7623 | -122.9965 | 122.9782 | 122.8821 | 58.1818 | -123.1247
1221.5156 | 123.1338 | -58.6578 | 64.1785 | 0.24872 | 0.014595 | 0.065877 | 0.069432 | 0.12913 | 0.00062595 | -0.0010787 | 0.30846 | -0.005614 | -0.0027408 | -0.001818 | 0.0017688 | -0.0051697 | 64.183 | 64.3707 | 7.3654 | -58.7265 | 64.1968 | -58.699 | -58.7311 | -58.3191 | -0.40283 | -58.8638 | 64.1968 | 64.119 | -58.7906 | -58.8821 | -0.041199 | -0.073242 | 0.01831 | 123.0286 | -0.068664 | 0.004578 | 0.004577 | -0.13275 | -0.2243 | 0.01831 | 0.33875 | -0.20599 | 0.01831 | -0.059509 | 122.8546 | 122.8409 | 66.0233 | -122.9095 | 122.8546 | 122.7768 | 58.255 | -123.0606
1222.5156 | 123.0789 | -58.7219 | 64.2059 | 0.18768 | 0.014595 | 0.068013 | 0.070286 | 0.12913 | 0.0014804 | 0.0012711 | 0.20164 | -0.0024096 | -0.0001774 | -0.0009634 | 0.0036914 | -0.0064515 | 64.1144 | 64.1876 | 7.4387 | -58.7677 | 64.2197 | -58.7448 | -58.786 | -58.4015 | -0.54474 | -58.9874 | 64.2242 | 64.1693 | -58.7997 | -58.9096 | -0.022888 | -0.064087 | 0.013733 | 122.9095 | -0.045776 | 0.018311 | -0.091553 | -0.07782 | -0.18768 | 0.01831 | 0.32044 | -0.2655 | -0.07782 | -0.036621 | 122.9416 | 122.8363 | 66.1606 | -122.9919 | 122.9462 | 122.8912 | 58.1772 | -123.1155
1223.5156 | 123.1522 | -58.6899 | 64.1876 | 0.20294 | 0.013954 | 0.068013 | 0.068577 | 0.12934 | 0.00019875 | -0.00065152 | 0.087204 | -0.002196 | -0.0018862 | -0.0022452 | 0.0036914 | -0.0060243 | 64.151 | 64.3021 | 7.6492 | -58.7402 | 64.1922 | -58.7173 | -58.7677 | -58.3282 | -0.38452 | -58.8821 | 64.2014 | 64.1327 | -58.7723 | -58.8593 | -0.027466 | -0.07782 | 0.004578 | 122.9919 | -0.050354 | 0.027466 | -0.036621 | -0.082398 | -0.16937 | 0.013733 | 0.36163 | -0.19226 | -0.022888 | -0.054932 | 122.8821 | 122.8409 | 66.3391 | -122.9553 | 122.8912 | 122.8226 | 58.3054 | -123.0469
1224.5156 | 123.0423 | -58.7173 | 64.2242 | 0.050354 | 0.014168 | 0.068654 | 0.072423 | 0.12742 | 0.0031894 | 0.00041648 | 0.071945 | -0.001128 | -0.0010318 | -0.0020316 | 0.0034778 | -0.0073059 | 64.1464 | 64.2242 | 7.7545 | -58.7585 | 64.2197 | -58.7448 | -58.7952 | -58.4106 | -0.45319 | -58.9828 | 64.2563 | 64.1785 | -58.7814 | -58.8684 | -0.027466 | -0.07782 | -0.004577 | 122.9416 | -0.041199 | 0.036621 | -0.07782 | -0.064087 | -0.15106 | 0.032044 | 0.3067 | -0.2655 | -0.11444 | -0.045776 | 122.937 | 122.8638 | 66.4719 | -123.0194 | 122.9736 | 122.8958 | 58.2642 | -123.0927
1225.5156 | 123.0972 | -58.6807 | 64.2059 | 0.17242 | 0.014381 | 0.067159 | 0.067936 | 0.12956 | 0.00041235 | -0.0023605 | 0.24742 | -0.0032642 | -0.0008182 | -0.002886 | 0.0026234 | -0.0034607 | 64.1098 | 64.2059 | 7.8781 | -58.7723 | 64.2014 | -58.7494 | -58.8135 | -58.3878 | -0.44861 | -58.96 | 64.2242 | 64.1281 | -58.8089 | -58.8821 | -0.068665 | -0.13275 | -0.004578 | 122.8867 | -0.091553 | 0.041199 | -0.096131 | -0.12817 | -0.20142 | 0.01831 | 0.29297 | -0.27924 | -0.07782 | -0.07782 | 122.8821 | 122.7905 | 66.5588 | -123.0194 | 122.905 | 122.8088 | 58.2321 | -123.0881
1226.5156 | 123.0469 | -58.6945 | 64.2197 | 0.050354 | 0.017586 | 0.066091 | 0.070927 | 0.12892 | 0.0021214 | -0.00022432 | 0.087204 | -0.0024096 | 3.6404e-05 | -0.0009634 | 0.0034778 | -0.0060243 | 64.1327 | 64.238 | 8.0658 | -58.754 | 64.2426 | -58.7311 | -58.7814 | -58.4152 | -0.4715 | -59.0057 | 64.27 | 64.1418 | -58.8135 | -58.9005 | -0.036621 | -0.086975 | 0.022888 | 122.9324 | -0.059509 | 0.027466 | -0.086976 | -0.11902 | -0.20599 | 0.050354 | 0.27924 | -0.31128 | -0.10529 | -0.07782 | 122.937 | 122.8271 | 66.7603 | -123.0011 | 122.9645 | 122.8363 | 58.223 | -123.1201
1227.5156 | 123.111 | -58.7128 | 64.1876 | 0.14954 | 0.014168 | 0.066945 | 0.066868 | 0.12699 | -1.505e-05 | 0.00020288 | 0.31609 | -0.0036914 | -0.0001774 | -0.0003226 | 0.0030506 | -0.0038879 | 64.1052 | 64.2242 | 8.2123 | -58.7677 | 64.2059 | -58.7265 | -58.7952 | -58.3878 | -0.46692 | -58.9417 | 64.2151 | 64.1418 | -58.8135 | -58.8776 | -0.013732 | -0.082397 | 0.018311 | 122.937 | -0.054931 | 0.027466 | -0.082397 | -0.10071 | -0.16479 | 0.027466 | 0.32501 | -0.22888 | -0.064087 | -0.045776 | 122.9187 | 122.818 | 66.925 | -122.9828 | 122.9279 | 122.8546 | 58.2459 | -123.0652
1228.5156 | 123.0515 | -58.7219 | 64.2151 | 0.073242 | 0.016517 | 0.067586 | 0.069432 | 0.12742 | 0.0048984 | -0.00086512 | 0.087204 | -0.0019824 | 0.001959 | -0.002886 | 0.0015552 | -0.0053833 | 64.1098 | 64.2288 | 8.4091 | -58.7814 | 64.2334 | -58.754 | -58.7997 | -58.4198 | -0.43488 | -59.0057 | 64.2242 | 64.1693 | -58.8226 | -58.8913 | -0.032043 | -0.07782 | 0.01831 | 122.9507 | -0.059509 | 0.018311 | -0.10529 | -0.10071 | -0.16937 | 0.009155 | 0.30212 | -0.28381 | -0.11444 | -0.045776 | 122.9553 | 122.8317 | 67.131 | -123.0148 | 122.9462 | 122.8912 | 58.287 | -123.1064
1229.5156 | 123.0743 | -58.7402 | 64.1922 | 0.40894 | 0.017372 | 0.068013 | 0.067082 | 0.12785 | -0.00022865 | -0.00065152 | 0.20164 | -0.0034778 | 0.00025 | -0.0003226 | 0.0017688 | -0.0030335 | 64.0915 | 64.1418 | 8.6197 | -58.8043 | 64.2105 | -58.7677 | -58.8043 | -58.4198 | -0.45319 | -58.9966 | 64.2517 | 64.1373 | -58.8181 | -58.8959 | -0.027466 | -0.064087 | 0.01831 | 122.8821 | -0.064087 | 0 | -0.10071 | -0.07782 | -0.15564 | 0.059509 | 0.32043 | -0.25635 | -0.10071 | -0.054932 | 122.9507 | 122.8317 | 67.3599 | -122.9965 | 122.9919 | 122.8775 | 58.287 | -123.0881
1230.5156 | 123.143 | -58.699 | 64.2151 | -0.018311 | 0.016304 | 0.068013 | 0.071354 | 0.1287 | 0.002335 | 0.00041648 | 1.0256 | -0.0015552 | -0.0016726 | -0.0030996 | 0.004546 | -0.0058105 | 64.1373 | 64.2654 | 8.8028 | -58.7311 | 64.2242 | -58.7311 | -58.7677 | -58.3557 | -0.25635 | -58.9554 | 64.2288 | 64.1556 | -58.8089 | -58.9142 | -0.032043 | -0.068664 | 0.009155 | 122.9645 | -0.032043 | 0.036621 | -0.07782 | -0.10986 | -0.21515 | 0.013733 | 0.34332 | -0.25635 | -0.041198 | -0.059509 | 122.9233 | 122.8363 | 67.5018 | -122.9828 | 122.9279 | 122.8546 | 58.4427 | -123.1293
1231.5156 | 123.0377 | -58.7311 | 64.2059 | 0.09613 | 0.015663 | 0.066945 | 0.070714 | 0.1255 | 0.0025486 | -0.00065152 | 0.14061 | -0.0015552 | -0.0010318 | -0.0030996 | 0.0041186 | -0.0034607 | 64.0549 | 64.1785 | 8.9127 | -58.7952 | 64.2426 | -58.7814 | -58.8226 | -58.4656 | -0.40741 | -59.111 | 64.2105 | 64.1006 | -58.8821 | -58.9554 | -0.050354 | -0.091553 | 0.036621 | 122.9095 | -0.064087 | 0.027466 | -0.15106 | -0.15106 | -0.2243 | 0.004577 | 0.2655 | -0.37994 | -0.15564 | -0.10529 | 122.9736 | 122.786 | 67.6437 | -123.0286 | 122.9416 | 122.8317 | 58.3237 | -123.1613
1232.5156 | 123.1064 | -58.6945 | 64.2105 | -0.064087 | 0.016945 | 0.068868 | 0.0705 | 0.12934 | 0.0012668 | -0.00086512 | 0.14061 | -0.0032642 | -0.0010318 | -0.0033134 | 0.0034778 | -0.0062379 | 64.1556 | 64.2609 | 9.1461 | -58.7494 | 64.2197 | -58.754 | -58.786 | -58.3694 | -0.25177 | -58.9371 | 64.238 | 64.1876 | -58.8089 | -58.9005 | -0.059509 | -0.091553 | 0.009156 | 122.9553 | -0.054932 | 0.036621 | -0.054931 | -0.11444 | -0.20599 | 0.027466 | 0.32501 | -0.24262 | -0.036621 | -0.022888 | 122.9141 | 122.85 | 67.8406 | -122.9965 | 122.9324 | 122.8821 | 58.4427 | -123.111
1233.5156 | 123.0377 | -58.7128 | 64.2059 | 0.012207 | 0.017799 | 0.066518 | 0.070714 | 0.12678 | 0.0036166 | -0.0019333 | 0.11772 | -0.0019824 | -0.001459 | -0.001177 | 0.002196 | -0.0036743 | 64.1052 | 64.2151 | 9.2606 | -58.7631 | 64.2242 | -58.754 | -58.7906 | -58.4152 | -0.30212 | -59.0012 | 64.2242 | 64.1785 | -58.8135 | -58.9233 | -0.041198 | -0.077819 | 0.01831 | 122.9279 | -0.050354 | 0.027465 | -0.10071 | -0.10071 | -0.21057 | 0.01831 | 0.29755 | -0.28839 | -0.07782 | -0.027466 | 122.937 | 122.818 | 67.9733 | -122.9965 | 122.937 | 122.8912 | 58.4106 | -123.1293
1234.5156 | 123.1155 | -58.7036 | 64.2197 | -0.13275 | 0.012245 | 0.069295 | 0.068791 | 0.12934 | 0.0019078 | -0.0010787 | -0.050125 | -0.003905 | -0.0010318 | -0.001177 | 0.0013416 | -0.0051697 | 64.1144 | 64.2334 | 9.4894 | -58.7173 | 64.2426 | -58.7448 | -58.7814 | -58.3603 | -0.18768 | -58.9325 | 64.238 | 64.1693 | -58.8135 | -58.905 | -0.041199 | -0.07782 | 0.022888 | 122.937 | -0.013733 | 0.064087 | -0.10529 | -0.10986 | -0.20142 | 0.01831 | 0.34332 | -0.22888 | -0.027466 | -0.050354 | 122.9462 | 122.818 | 68.1931 | -123.0011 | 122.9416 | 122.8729 | 58.5159 | -123.1247
1235.5156 | 123.0515 | -58.7585 | 64.2105 | 0.073242 | 0.01844 | 0.066304 | 0.068364 | 0.12913 | 0.0048984 | -0.00065152 | 0.14061 | -0.0051868 | 0.0011044 | -0.0013906 | 0.0049732 | -0.0038879 | 64.1098 | 64.1968 | 9.6954 | -58.7677 | 64.1968 | -58.7723 | -58.7997 | -58.4198 | -0.23804 | -59.0057 | 64.2334 | 64.1739 | -58.8501 | -58.9233 | -0.013733 | -0.041199 | -0.013733 | 122.9553 | -0.009155 | 0.032044 | -0.10071 | -0.091553 | -0.1648 | 0.022888 | 0.33874 | -0.24719 | -0.082397 | -0.036621 | 122.9553 | 122.8683 | 68.454 | -123.0103 | 122.9919 | 122.9324 | 58.5205 | -123.1338
1236.5156 | 123.0743 | -58.7357 | 64.2059 | -0.15564 | 0.013527 | 0.069936 | 0.071354 | 0.13297 | 0.0029758 | 0.00020288 | -0.065384 | -0.004546 | 0.00025 | -0.001818 | 0.0026234 | -0.0038879 | 64.119 | 64.238 | 9.9289 | -58.7173 | 64.2151 | -58.7585 | -58.7952 | -58.3557 | -0.14191 | -58.9279 | 64.2334 | 64.1739 | -58.8364 | -58.9142 | -0.022888 | -0.059509 | 0.009155 | 122.9736 | 0.018311 | 0.07782 | -0.086975 | -0.10071 | -0.17853 | 0.027465 | 0.37994 | -0.19226 | -0.013732 | -0.032044 | 122.9507 | 122.8546 | 68.6646 | -123.0011 | 122.9691 | 122.9095 | 58.5938 | -123.1201
1237.5156 | 123.0881 | -58.7494 | 64.1968 | 0.027466 | 0.018226 | 0.068013 | 0.069218 | 0.13126 | 0.0019078 | -0.00065152 | 0.033798 | -0.0024096 | -0.0006046 | 0.0020272 | 0.0019824 | -0.0058105 | 64.1418 | 64.2426 | 10.0937 | -58.7585 | 64.1968 | -58.7677 | -58.8135 | -58.3694 | -0.16479 | -58.9874 | 64.2105 | 64.151 | -58.8455 | -58.905 | -0.01831 | -0.064087 | 0 | 122.9919 | -0.009155 | 0.054932 | -0.054931 | -0.09613 | -0.15564 | 0.013733 | 0.37994 | -0.23804 | -0.082398 | -0.045776 | 122.9462 | 122.8912 | 68.8431 | -123.0103 | 122.9599 | 122.9004 | 58.5846 | -123.1018
1238.5156 | 123.0377 | -58.7128 | 64.2471 | -0.15564 | 0.011818 | 0.068227 | 0.069645 | 0.12977 | -0.0017238 | -0.0027877 | 0.049057 | -0.002837 | -0.0029544 | -0.0013906 | 0.001128 | -0.0023927 | 64.0732 | 64.1968 | 10.2951 | -58.754 | 64.238 | -58.7723 | -58.7814 | -58.3969 | -0.15564 | -58.9783 | 64.2563 | 64.2014 | -58.8501 | -58.9142 | -0.059509 | -0.068664 | -0.009155 | 122.9095 | -0.041198 | 0.027466 | -0.17395 | -0.13733 | -0.20142 | 0.009156 | 0.31586 | -0.2655 | -0.064086 | -0.045776 | 122.9507 | 122.786 | 69.0079 | -123.0286 | 122.9691 | 122.9141 | 58.5571 | -123.1613
1239.5156 | 123.1247 | -58.7128 | 64.2105 | -0.064087 | 0.018226 | 0.066731 | 0.068364 | 0.12892 | 0.0044712 | -0.0012923 | -0.034867 | -0.0030506 | -0.0010318 | -0.001818 | 0.0041186 | -0.0045289 | 64.1281 | 64.2426 | 10.5423 | -58.7357 | 64.2014 | -58.7585 | -58.8181 | -58.342 | -0.32044 | -59.0195 | 64.1968 | 64.1235 | -58.8684 | -58.9508 | -0.045776 | -0.10528 | -0.009155 | 122.9553 | -0.022888 | 0.082397 | -0.082397 | -0.15564 | -0.23804 | -0.013733 | 0.37079 | -0.3067 | -0.068664 | -0.086975 | 122.9141 | 122.8409 | 69.2551 | -123.0286 | 122.9095 | 122.8363 | 58.3923 | -123.1613
1240.5156 | 123.0469 | -58.7494 | 64.2426 | -0.18616 | 0.013954 | 0.072072 | 0.069218 | 0.12892 | -1.505e-05 | -0.0032151 | -0.28664 | -0.0034778 | -0.0023136 | -0.0016044 | 0.00027337 | -0.0034607 | 64.0686 | 64.2059 | 10.7849 | -58.6945 | 64.2471 | -58.7357 | -58.7631 | -58.3969 | -0.12817 | -58.9874 | 64.2654 | 64.1464 | -58.8501 | -58.9233 | 0.013733 | -0.013733 | 0.004577 | 122.9553 | 0.054932 | 0.068665 | -0.17395 | -0.10071 | -0.17395 | 0.022888 | 0.35248 | -0.23804 | -0.064087 | -0.096131 | 122.9965 | 122.818 | 69.5343 | -123.0057 | 123.0148 | 122.8958 | 58.6212 | -123.1659
1241.5156 | 123.0789 | -58.7585 | 64.2151 | 0.019836 | 0.017586 | 0.066518 | 0.070927 | 0.12892 | 0.0038304 | 0.00020288 | 0.087204 | -0.0019824 | 0.00025 | -0.0020316 | 0.004546 | -0.0058105 | 64.1373 | 64.2151 | 11.1511 | -58.7357 | 64.1876 | -58.754 | -58.8226 | -58.3786 | -0.050354 | -58.9966 | 64.1922 | 64.1373 | -58.8318 | -58.9279 | 0.004578 | -0.064087 | -0.027466 | 122.9736 | 0.022888 | 0.086975 | -0.07782 | -0.073242 | -0.16937 | -0.022888 | 0.37994 | -0.23804 | -0.068665 | -0.07782 | 122.9462 | 122.8958 | 69.9097 | -123.0377 | 122.9507 | 122.8958 | 58.7082 | -123.143
1242.5156 | 123.056 | -58.7311 | 64.238 | -0.23956 | 0.01139 | 0.069509 | 0.070073 | 0.1287 | -0.001083 | -0.0030013 | -0.17983 | -0.0054004 | -0.0021 | -0.0005362 | 0.0019824 | -0.0047425 | 64.1922 | 64.2609 | 11.4258 | -58.8547 | 64.2151 | -58.7677 | -58.8455 | -58.3786 | 0.022888 | -58.9966 | 64.2426 | 64.1785 | -58.8455 | -58.9233 | -0.036621 | -0.11444 | -0.022888 | 122.9919 | -0.1236 | -0.009155 | -0.045776 | -0.11444 | -0.19226 | 0.004578 | 0.35248 | -0.2655 | -0.073242 | -0.059509 | 122.9462 | 122.9233 | 70.1569 | -123.0835 | 122.9736 | 122.9095 | 58.754 | -123.1613
1243.5156 | 123.0698 | -58.7402 | 64.2014 | -0.15564 | 0.013954 | 0.067159 | 0.071141 | 0.12998 | 0.0014804 | -0.00043792 | -0.11116 | -0.0041186 | 0.0004636 | -0.000109 | 0.00091437 | -0.0047425 | 64.0961 | 64.2014 | 11.7691 | -58.7219 | 64.2105 | -58.7723 | -58.8181 | -58.3649 | 0.10529 | -58.9828 | 64.2014 | 64.1464 | -58.8455 | -58.9371 | -0.032044 | -0.07782 | 0.009155 | 122.9416 | 0.01831 | 0.09613 | -0.10529 | -0.10529 | -0.19684 | 0 | 0.37537 | -0.24262 | -0.045776 | -0.054932 | 122.9507 | 122.8363 | 70.5093 | -123.0194 | 122.9416 | 122.8867 | 58.8455 | -123.1384
1244.5156 | 123.1384 | -58.7128 | 64.2014 | -0.14801 | 0.0098951 | 0.068227 | 0.068577 | 0.13126 | -0.0023648 | -0.0032151 | -0.034867 | -0.0030506 | -0.0001774 | -0.0016044 | 0.001128 | -0.0051697 | 64.1235 | 64.3021 | 12.0438 | -58.6853 | 64.1464 | -58.7357 | -58.7952 | -58.3145 | 0.17853 | -58.9142 | 64.1785 | 64.1052 | -58.8135 | -58.905 | -0.022888 | -0.082397 | -0.054932 | 123.0148 | 0.027466 | 0.10986 | -0.07782 | -0.10071 | -0.19226 | -0.022888 | 0.39825 | -0.20142 | -0.009156 | -0.09613 | 122.8592 | 122.8363 | 70.7565 | -122.9965 | 122.8912 | 122.818 | 58.8913 | -123.1064
1245.5156 | 123.0469 | -58.7311 | 64.2059 | -0.13275 | 0.01374 | 0.065663 | 0.0705 | 0.12827 | 0.0036166 | -0.0034287 | -0.065384 | -0.0034778 | -0.0016726 | -0.0016044 | 0.0024096 | -0.0055969 | 64.0732 | 64.1785 | 12.0255 | -58.7357 | 64.2059 | -58.7677 | -58.8455 | -58.3786 | 0.11902 | -59.024 | 64.2197 | 64.1373 | -58.8364 | -58.9417 | -0.036621 | -0.11444 | 0 | 122.9095 | -0.004578 | 0.10986 | -0.13275 | -0.10529 | -0.21057 | 0.013733 | 0.35248 | -0.29297 | -0.082398 | -0.068665 | 122.937 | 122.8043 | 70.7565 | -123.0515 | 122.9507 | 122.8683 | 58.8501 | -123.1476
1246.5156 | 123.1476 | -58.7357 | 64.2014 | -0.1709 | 0.01075 | 0.069081 | 0.069218 | 0.12977 | -0.0038602 | -0.0030013 | -0.019608 | -0.0043324 | -0.0012454 | -0.0016044 | 0.0015552 | -0.0068787 | 64.1281 | 64.2838 | 12.3138 | -58.6807 | 64.1464 | -58.7585 | -58.7952 | -58.3191 | 0.2655 | -58.9371 | 64.1785 | 64.1464 | -58.8409 | -58.8959 | -0.022888 | -0.059509 | -0.054932 | 123.0194 | 0.054932 | 0.11444 | -0.073242 | -0.10528 | -0.16022 | -0.022888 | 0.41657 | -0.20142 | -0.041199 | -0.054932 | 122.8821 | 122.8638 | 71.0495 | -122.9965 | 122.9141 | 122.8821 | 59.0012 | -123.0972
1247.5156 | 123.0698 | -58.7723 | 64.1968 | -0.18616 | 0.012245 | 0.070577 | 0.070714 | 0.1287 | 0.00083955 | -0.0049239 | -0.19508 | -0.0024096 | -0.0016726 | -0.0016044 | 0.002837 | -0.0041017 | 64.1006 | 64.1098 | 12.5244 | -58.7631 | 64.1785 | -58.8043 | -58.8409 | -58.3832 | 0.1831 | -59.0424 | 64.2105 | 64.1418 | -58.8776 | -58.9462 | -0.032043 | -0.068664 | -0.01831 | 122.8821 | 0.009155 | 0.077819 | -0.09613 | -0.10529 | -0.17395 | 0.013733 | 0.3891 | -0.27008 | -0.09613 | -0.054931 | 122.9507 | 122.8729 | 71.2967 | -123.0377 | 122.9828 | 122.9141 | 58.9554 | -123.143
1248.5156 | 123.0835 | -58.7677 | 64.1968 | -0.19379 | 0.01075 | 0.069722 | 0.070073 | 0.12721 | -0.0023648 | -0.0040695 | -0.095902 | -0.0071094 | -0.0029544 | -0.001177 | 0.0017688 | -0.0049561 | 64.0961 | 64.2609 | 12.8677 | -58.7219 | 64.1464 | -58.7814 | -58.8364 | -58.3557 | 0.2655 | -58.992 | 64.1968 | 64.1098 | -58.8776 | -58.9691 | -0.013733 | -0.068665 | -0.050354 | 123.0286 | 0.045776 | 0.11444 | -0.10071 | -0.10986 | -0.20142 | 0 | 0.41199 | -0.2243 | -0.022888 | -0.086975 | 122.9141 | 122.8638 | 71.6354 | -123.0331 | 122.9645 | 122.8775 | 59.0332 | -123.1659
1249.5156 | 123.0743 | -58.7814 | 64.1922 | -0.25482 | 0.015449 | 0.06844 | 0.072636 | 0.13105 | 0.0027622 | -0.0030013 | -0.073013 | -0.0036914 | -0.0027408 | -0.0022452 | 0.0017688 | -0.0064515 | 64.0503 | 64.1647 | 13.0417 | -58.7723 | 64.1739 | -58.8043 | -58.8547 | -58.3694 | 0.26093 | -59.0469 | 64.2014 | 64.1052 | -58.8638 | -58.9554 | -0.022888 | -0.073242 | -0.018311 | 122.9462 | 0.009155 | 0.082397 | -0.14191 | -0.082398 | -0.17395 | 0.009155 | 0.41199 | -0.2655 | -0.091553 | -0.086975 | 122.9553 | 122.8317 | 71.8231 | -123.0469 | 122.9828 | 122.8867 | 59.0424 | -123.1476
1250.5156 | 123.1064 | -58.7402 | 64.1556 | -0.14038 | 0.012886 | 0.070577 | 0.066655 | 0.12849 | -0.002792 | -0.0017197 | -0.057755 | -0.0058276 | -0.0027408 | -0.000109 | 0.0017688 | -0.0041017 | 64.0869 | 64.27 | 13.4583 | -58.7036 | 64.1235 | -58.7952 | -58.8593 | -58.3099 | 0.3891 | -58.9554 | 64.1647 | 64.0594 | -58.8776 | -58.9645 | -0.054932 | -0.11902 | -0.032044 | 123.0103 | 0.036621 | 0.15564 | -0.068665 | -0.13733 | -0.22431 | 0.009155 | 0.4303 | -0.21515 | 0.009156 | -0.096131 | 122.8638 | 122.8271 | 72.1985 | -123.0148 | 122.905 | 122.7997 | 59.1293 | -123.1201
1251.5156 | 123.056 | -58.7814 | 64.1739 | -0.23956 | 0.013099 | 0.066945 | 0.070927 | 0.12977 | 0.001694 | -0.0027877 | -0.027237 | -0.005614 | -0.0029544 | -0.0005362 | -0.00036743 | -0.0041017 | 64.0732 | 64.2059 | 13.6688 | -58.7448 | 64.1281 | -58.8181 | -58.8638 | -58.3694 | 0.32959 | -59.0424 | 64.1785 | 64.1052 | -58.8959 | -58.9691 | -0.036621 | -0.082398 | -0.045776 | 122.9874 | 0.036621 | 0.11902 | -0.10071 | -0.11444 | -0.18768 | 0.004578 | 0.41199 | -0.26093 | -0.073242 | -0.068664 | 122.9095 | 122.8546 | 72.4503 | -123.0377 | 122.9599 | 122.8867 | 59.111 | -123.143
1252.5156 | 123.1796 | -58.7585 | 64.1235 | -0.10223 | 0.0094677 | 0.071218 | 0.0705 | 0.1287 | -0.001083 | -0.0040695 | -0.019608 | -0.0054004 | -0.0057316 | -0.0054496 | 0.0017688 | -0.0034607 | 64.1006 | 64.2975 | 14.035 | -58.699 | 64.1144 | -58.8089 | -58.8455 | -58.4335 | 0.4715 | -58.9188 | 64.119 | 64.0182 | -58.873 | -58.96 | -0.050354 | -0.086975 | -0.009155 | 123.056 | 0.059509 | 0.14648 | -0.022888 | -0.11444 | -0.20142 | -0.004577 | 0.32501 | -0.16022 | 0.041199 | -0.10529 | 122.8729 | 122.8592 | 72.7936 | -122.9691 | 122.8775 | 122.7768 | 59.23 | -123.0835
1253.5156 | 123.0835 | -58.8089 | 64.1602 | -0.1709 | 0.012245 | 0.070149 | 0.068577 | 0.12977 | 0.001694 | -0.0015061 | -0.97328 | -0.0079638 | -0.0006046 | 0.0001046 | 0.002837 | -0.0058105 | 64.0182 | 64.1418 | 14.1815 | -58.7769 | 64.1373 | -58.8455 | -58.9096 | -58.3557 | 0.33875 | -59.0881 | 64.1647 | 64.0686 | -58.9142 | -58.9874 | -0.036621 | -0.10071 | -0.022888 | 122.9507 | 0.032044 | 0.13275 | -0.14191 | -0.10529 | -0.17853 | 0.004578 | 0.45319 | -0.27924 | -0.10071 | -0.091552 | 122.9462 | 122.8271 | 72.9904 | -123.0698 | 122.9736 | 122.8775 | 59.1476 | -123.1476
1254.5156 | 123.1384 | -58.7494 | 64.0686 | 0.59967 | 0.01139 | 0.0678 | 0.071782 | 0.12806 | -0.0015102 | -0.0015061 | 0.041427 | -0.0043324 | -0.0042362 | -0.002886 | 0.00091437 | -0.0062379 | 64.1006 | 64.2609 | 14.621 | -58.699 | 64.0869 | -58.7997 | -58.8684 | -58.2687 | 0.53101 | -58.9645 | 64.1098 | 64.0549 | -58.873 | -58.9554 | -0.050354 | -0.11902 | 0.01831 | 123.0103 | 0.050354 | 0.16937 | 0.032043 | -0.1236 | -0.20599 | 0.041198 | 0.48065 | -0.21515 | -0.009156 | -0.013733 | 122.8363 | 122.85 | 73.3704 | -122.937 | 122.8592 | 122.8043 | 59.2804 | -123.024
1255.5156 | 123.0423 | -58.8226 | 64.1373 | -0.20905 | 0.013954 | 0.069936 | 0.073704 | 0.12934 | 0.0029758 | -0.00065152 | -0.14168 | -0.002837 | -0.0027408 | -0.0016044 | 0.0041186 | -0.0045289 | 64.0182 | 64.1327 | 14.7537 | -58.7585 | 64.1602 | -58.8455 | -58.8959 | -58.3557 | 0.39825 | -59.0607 | 64.1693 | 64.0732 | -58.9096 | -58.9737 | -0.022888 | -0.073242 | 0.022888 | 122.9553 | 0.064087 | 0.13733 | -0.11902 | -0.086975 | -0.15106 | 0.032044 | 0.46692 | -0.23804 | -0.086975 | -0.064087 | 122.9828 | 122.8409 | 73.5764 | -123.0331 | 122.9919 | 122.8958 | 59.2209 | -123.111
1256.5156 | 123.1201 | -58.7997 | 64.1418 | -0.14038 | 0.0096813 | 0.068013 | 0.069005 | 0.1287 | -0.001083 | -0.0023605 | -0.057755 | -0.006255 | -0.0008182 | -0.001177 | 0.0041186 | -0.0055969 | 64.0915 | 64.2563 | 15.1611 | -58.7082 | 64.0823 | -58.8043 | -58.8776 | -58.2916 | 0.54932 | -58.9828 | 64.1052 | 64.0732 | -58.8959 | -58.9554 | -0.004577 | -0.077819 | -0.05951 | 123.056 | 0.091553 | 0.16937 | -0.050354 | -0.09613 | -0.15564 | -0.036621 | 0.50812 | -0.18311 | -0.027466 | -0.068665 | 122.8821 | 122.8912 | 73.9609 | -123.0194 | 122.905 | 122.8729 | 59.3491 | -123.0972
1257.5156 | 123.0606 | -58.8135 | 64.151 | -1.9562 | 0.011818 | 0.068013 | 0.071141 | 0.12956 | 0.0012668 | -0.0010787 | -0.11116 | -0.0043324 | -0.001459 | -0.001177 | 0.0026234 | -0.0034607 | 63.9954 | 64.1327 | 15.3717 | -58.7631 | 64.1556 | -58.8455 | -58.905 | -58.342 | 0.52185 | -59.0881 | 64.1464 | 64.0869 | -58.9279 | -58.9828 | -0.032043 | -0.091552 | 0.004578 | 122.9462 | 0.050354 | 0.14191 | -0.15564 | -0.11444 | -0.16937 | -0.004578 | 0.4715 | -0.27466 | -0.10529 | -0.064087 | 122.9691 | 122.8088 | 74.1852 | -123.056 | 122.9599 | 122.9004 | 59.3353 | -123.1338
1258.5156 | 123.1705 | -58.7448 | 64.119 | -0.086975 | 0.01075 | 0.068654 | 0.06815 | 0.12913 | -0.0023648 | -0.0015061 | 0.27031 | -0.0047596 | -0.0027408 | -0.001818 | 0.0015552 | -0.0032471 | 64.1006 | 64.3112 | 15.7928 | -58.6578 | 64.1052 | -58.8043 | -58.8593 | -58.287 | 0.60883 | -58.9233 | 64.0961 | 64.0228 | -58.8867 | -58.9737 | -0.059509 | -0.11444 | -0.013733 | 123.056 | 0.086975 | 0.20142 | -0.018311 | -0.14191 | -0.22888 | -0.022889 | 0.45776 | -0.17853 | 0.050354 | -0.096131 | 122.85 | 122.8455 | 74.5377 | -122.9782 | 122.8409 | 122.7676 | 59.3536 | -123.0927
1259.5156 | 123.0652 | -58.7906 | 64.1647 | -0.19379 | 0.015663 | 0.069081 | 0.069859 | 0.12977 | 0.00083955 | -0.0021469 | -0.11879 | -0.0066822 | -0.0029544 | -0.002886 | 0.001128 | -0.0068787 | 64.0457 | 64.2151 | 16.008 | -58.7036 | 64.1235 | -58.7997 | -58.8821 | -58.3008 | 0.58594 | -59.0561 | 64.151 | 64.0686 | -58.8913 | -58.9737 | -0.009156 | -0.091553 | -0.041199 | 123.0057 | 0.086975 | 0.17853 | -0.11902 | -0.10071 | -0.18311 | -0.013733 | 0.48981 | -0.2655 | -0.082397 | -0.09613 | 122.9141 | 122.8363 | 74.7986 | -123.0469 | 122.9416 | 122.8592 | 59.3765 | -123.1384
1260.5156 | 123.175 | -58.7585 | 64.0915 | -0.23956 | 0.011818 | 0.069936 | 0.069645 | 0.12977 | -0.00086945 | -0.0034287 | -0.027237 | -0.0058276 | -0.0023136 | -0.0026724 | 5.9768e-05 | -0.0053833 | 64.0778 | 64.2746 | 16.3055 | -58.6807 | 64.0869 | -58.8089 | -58.8638 | -58.2413 | 0.70038 | -58.9691 | 64.0915 | 64.0137 | -58.8684 | -58.96 | -0.050354 | -0.10529 | -0.004578 | 123.0331 | 0.07782 | 0.18311 | -0.013733 | -0.10986 | -0.20142 | 0 | 0.51727 | -0.21057 | -0.009155 | -0.07782 | 122.8455 | 122.8363 | 75.0641 | -122.9553 | 122.85 | 122.7722 | 59.4589 | -123.0515
1261.5156 | 123.0606 | -58.8135 | 64.1602 | -0.23956 | 0.010963 | 0.069295 | 0.068364 | 0.12849 | 0.0021214 | -0.0017197 | -0.15694 | -0.0043324 | -0.001459 | -0.0024588 | 0.001128 | -0.0055969 | 64.0045 | 64.151 | 16.4474 | -58.754 | 64.1602 | -58.8272 | -58.9142 | -58.3054 | 0.74616 | -58.905 | 64.2014 | 64.1052 | -58.8913 | -59.0012 | -0.013732 | -0.10071 | 0 | 122.9645 | 0.05951 | 0.16022 | -0.15564 | -0.077819 | -0.18768 | 0.041199 | 0.50812 | -0.091552 | 0.096131 | -0.054931 | 122.9736 | 122.818 | 75.2609 | -123.0743 | 123.0148 | 122.9187 | 59.5596 | -123.1613
1262.5156 | 123.1659 | -58.786 | 64.1098 | -0.14038 | 0.012031 | 0.069081 | 0.070927 | 0.12699 | 0.00041235 | -0.0012923 | -0.11116 | -0.007323 | -0.0025272 | -0.001177 | 0.0017688 | -0.0049561 | 64.0594 | 64.2654 | 16.8549 | -58.6807 | 64.1052 | -58.8089 | -58.8638 | -58.2504 | 0.74616 | -59.0012 | 64.119 | 64.0274 | -58.873 | -58.992 | -0.022888 | -0.07782 | -0.004577 | 123.0515 | 0.10529 | 0.18311 | -0.050354 | -0.086975 | -0.20599 | 0.009156 | 0.53558 | -0.21515 | -0.009156 | -0.082397 | 122.8912 | 122.8455 | 75.6409 | -122.9736 | 122.905 | 122.8134 | 59.5322 | -123.1018
1263.5156 | 123.0652 | -58.8318 | 64.1373 | -0.19379 | 0.012459 | 0.070149 | 0.071995 | 0.12849 | 0.0038304 | -0.0012923 | -0.19508 | -0.002837 | -0.001459 | 0.0007456 | 0.0026234 | -0.0051697 | 64.032 | 64.0961 | 16.9464 | -58.7494 | 64.1281 | -58.8638 | -58.9279 | -58.3237 | 0.6546 | -59.0836 | 64.1602 | 64.0366 | -58.9142 | -59.0149 | -0.032044 | -0.09613 | -0.009155 | 122.9279 | 0.082397 | 0.17853 | -0.10529 | -0.082398 | -0.18311 | 0.022888 | 0.50812 | -0.25177 | -0.068664 | -0.10071 | 122.9599 | 122.8638 | 75.7782 | -123.0652 | 122.9919 | 122.8683 | 59.4864 | -123.1522
1264.5156 | 123.1567 | -58.7997 | 64.0915 | -0.17853 | 0.014595 | 0.068227 | 0.069218 | 0.13062 | 0.00041235 | -0.0034287 | -0.042496 | -0.0066822 | -0.0025272 | 0.0007456 | 0.0015552 | -0.0079469 | 64.0686 | 64.27 | 17.3126 | -58.667 | 64.0823 | -58.7952 | -58.8867 | -58.223 | 0.80109 | -58.9645 | 64.0915 | 64.0091 | -58.8684 | -58.9554 | 0.004578 | -0.086975 | -0.009156 | 123.0698 | 0.13275 | 0.21973 | -0.022888 | -0.068664 | -0.15564 | 0 | 0.57678 | -0.1648 | -0.009156 | -0.082398 | 122.8821 | 122.8683 | 76.1124 | -122.9782 | 122.8912 | 122.8088 | 59.6008 | -123.0469
1265.5312 | 123.1659 | -58.8135 | 64.0594 | -0.056458 | 0.014168 | 0.067372 | 0.067936 | 0.1287 | 0.002335 | 0.0010575 | 0.24742 | -0.0041186 | -0.0023136 | -0.001818 | 0.0032642 | -0.0051697 | 64.032 | 64.2197 | 17.4454 | -58.7082 | 64.0549 | -58.8364 | -58.8776 | -58.2001 | 0.74616 | -59.0057 | 64.0732 | 63.9542 | -58.9096 | -58.9966 | -0.022888 | -0.064086 | -0.004577 | 123.0331 | 0.10529 | 0.16937 | -0.027466 | -0.09613 | -0.1831 | 0.013733 | 0.6134 | -0.19226 | -0.009155 | -0.10529 | 122.8683 | 122.8455 | 76.2589 | -122.937 | 122.8867 | 122.7676 | 59.5596 | -123.056
1266.5156 | 123.2254 | -58.786 | 64.1006 | -0.048828 | 0.01075 | 0.072072 | 0.069432 | 0.12571 | -0.00065585 | -0.00065152 | 0.079574 | -0.0049732 | -0.0035952 | -0.0024588 | 0.00027337 | -0.0055969 | 64.0594 | 64.2792 | 17.6926 | -58.667 | 64.0961 | -58.8043 | -58.8593 | -58.1497 | 0.84686 | -58.9371 | 64.0778 | 63.9954 | -58.8867 | -58.96 | -0.01831 | -0.073242 | -0.004578 | 123.0652 | 0.11902 | 0.19226 | -0.041199 | -0.10071 | -0.17395 | -0.022888 | 0.63629 | -0.15106 | 0.022888 | -0.10529 | 122.8821 | 122.8455 | 76.4786 | -122.9599 | 122.8638 | 122.7814 | 59.6329 | -123.0606
1267.5156 | 123.0652 | -58.7997 | 64.1144 | -0.18616 | 0.011604 | 0.068868 | 0.073277 | 0.13084 | 0.0036166 | -0.0025741 | -0.14168 | -0.0041186 | -0.0016726 | -0.0022452 | 0.0013416 | -0.0058105 | 64.0091 | 64.1647 | 17.7246 | -58.7036 | 64.1235 | -58.8409 | -58.8821 | -58.2687 | 0.77362 | -59.0607 | 64.1464 | 64.0594 | -58.9233 | -59.0149 | -0.041198 | -0.082397 | 0.009155 | 122.9645 | 0.096131 | 0.17853 | -0.10529 | -0.1236 | -0.21515 | 0.032043 | 0.53101 | -0.26093 | -0.045776 | -0.054932 | 122.9233 | 122.8088 | 76.5244 | -122.9965 | 122.9462 | 122.8592 | 59.5734 | -123.1293
1268.5156 | 123.1934 | -58.7677 | 64.0915 | -0.094604 | 0.0098951 | 0.071431 | 0.068791 | 0.12998 | -0.001083 | -0.0038559 | 0.2932 | -0.0043324 | -0.0033816 | -0.001177 | 0.002837 | -0.0043153 | 64.1006 | 64.3066 | 18.0084 | -58.6487 | 64.0778 | -58.8226 | -58.8776 | -58.1314 | 0.84686 | -58.9462 | 64.0778 | 63.9771 | -58.8684 | -58.9828 | -0.054932 | -0.10986 | -0.013733 | 123.0743 | 0.11902 | 0.22888 | 0.009155 | -0.10071 | -0.21515 | -0.013733 | 0.63629 | -0.17853 | 0.036621 | -0.11444 | 122.8455 | 122.8683 | 76.7761 | -122.9691 | 122.8455 | 122.7448 | 59.6146 | -123.0743
1269.5156 | 123.0789 | -58.8135 | 64.1281 | -0.18616 | 0.015022 | 0.068654 | 0.072636 | 0.1287 | 0.0053256 | -0.0017197 | -0.32478 | -0.0026234 | -0.0012454 | 0.000532 | 0.0024096 | -0.0060243 | 63.9954 | 64.1418 | 18.0038 | -58.5251 | 64.1922 | -58.7997 | -58.873 | -58.2504 | 0.80109 | -59.0744 | 64.151 | 64.0274 | -58.9325 | -59.0057 | 0.013733 | -0.059509 | 0.064087 | 122.9553 | 0.28839 | 0.3479 | -0.13275 | -0.11902 | -0.19226 | 0.022888 | 0.56305 | -0.26093 | -0.068665 | -0.10071 | 123.0057 | 122.8088 | 76.8173 | -123.0011 | 122.9645 | 122.8409 | 59.6146 | -123.1338
1270.5156 | 123.0789 | -58.8409 | 64.1098 | -0.15564 | 0.015449 | 0.065663 | 0.071568 | 0.12892 | 0.005753 | 0.0010575 | -0.11879 | -0.002837 | -0.0008182 | 0.0007456 | 0.0030506 | -0.0070923 | 64.0366 | 64.183 | 18.1961 | -58.6945 | 64.1418 | -58.8593 | -58.905 | -58.2092 | 0.8606 | -59.0561 | 64.1464 | 64.0045 | -58.9188 | -58.9874 | -0.018311 | -0.064087 | 0.032044 | 123.024 | 0.14648 | 0.21057 | -0.073242 | -0.07782 | -0.14648 | 0.036621 | 0.63171 | -0.21515 | -0.068664 | -0.10528 | 122.9828 | 122.8775 | 77.037 | -123.0148 | 122.9874 | 122.8455 | 59.7015 | -123.0972
1271.5156 | 123.0743 | -58.8409 | 64.1602 | -0.10986 | 0.01139 | 0.068227 | 0.070286 | 0.12977 | 0.0021214 | -0.00086512 | -0.11116 | -0.0058276 | -0.0027408 | -0.0009634 | 0.0024096 | -0.0045289 | 63.9816 | 64.1556 | 18.306 | -58.7128 | 64.1281 | -58.8593 | -58.8959 | -58.223 | 0.87433 | -59.0057 | 64.1556 | 64.1098 | -58.8684 | -58.9783 | -0.018311 | -0.054932 | -0.032043 | 122.9965 | 0.12817 | 0.1831 | -0.17853 | -0.027466 | -0.13733 | -0.004577 | 0.61798 | -0.1648 | -0.027466 | -0.050354 | 122.9691 | 122.8226 | 77.1469 | -123.056 | 122.9965 | 122.9507 | 59.7153 | -123.1384
1272.5156 | 123.1613 | -58.7585 | 64.0823 | -0.064087 | 0.0096813 | 0.07079 | 0.068577 | 0.1287 | -0.002792 | -0.0032151 | 0.12535 | -0.005614 | -0.0042362 | -0.002886 | -0.0010082 | -0.0045289 | 64.0366 | 64.2883 | 18.5303 | -58.6487 | 64.0732 | -58.8272 | -58.8776 | -58.1177 | 0.99335 | -58.9325 | 64.0686 | 63.9954 | -58.8867 | -58.9737 | -0.068664 | -0.11902 | -0.009155 | 123.0469 | 0.10986 | 0.22888 | -0.045776 | -0.12817 | -0.21515 | -0.013732 | 0.64087 | -0.17395 | 0.041199 | -0.086975 | 122.8317 | 122.7951 | 77.2888 | -122.9599 | 122.8271 | 122.7539 | 59.7519 | -123.056
1273.5156 | 123.0606 | -58.8043 | 64.1235 | -0.19379 | 0.014808 | 0.067159 | 0.071141 | 0.12913 | 0.0012668 | 0.00041648 | -0.065384 | -0.0041186 | -0.0016726 | -0.0007498 | 0.0032642 | -0.0062379 | 64.0274 | 64.2151 | 18.6035 | -58.6761 | 64.1327 | -58.8226 | -58.8776 | -58.2138 | 0.94299 | -59.0561 | 64.1235 | 64.0411 | -58.9142 | -59.0012 | -0.018311 | -0.073242 | 0.009155 | 123.0194 | 0.12817 | 0.20142 | -0.09613 | -0.10986 | -0.19684 | 0 | 0.59052 | -0.25177 | -0.054931 | -0.082397 | 122.937 | 122.8317 | 77.4078 | -123.0011 | 122.9279 | 122.8455 | 59.7473 | -123.1247
1274.5156 | 123.1705 | -58.7585 | 64.0549 | -0.079346 | 0.010322 | 0.069722 | 0.067509 | 0.13062 | -0.0012966 | 0.00084388 | 0.0032804 | -0.0077502 | -0.0061588 | -0.0030996 | 0.0024096 | -0.0043153 | 64.0915 | 64.3112 | 18.7958 | -58.6258 | 64.0961 | -58.8272 | -58.873 | -58.2779 | 1.1307 | -58.9462 | 64.119 | 63.9633 | -58.905 | -58.9691 | -0.068664 | -0.11444 | 0.041198 | 123.0698 | 0.13275 | 0.24719 | 0.036621 | -0.14648 | -0.21057 | 0.064087 | 0.48065 | -0.18768 | 0.022888 | -0.091553 | 122.8546 | 122.85 | 77.5543 | -122.9279 | 122.8775 | 122.7219 | 59.8892 | -123.024
1275.5156 | 123.056 | -58.8455 | 64.1052 | 0.073242 | 0.019081 | 0.067586 | 0.073918 | 0.12892 | 0.0066074 | 0.0012711 | 0.064316 | -0.0026234 | 0.0017454 | -0.0005362 | 0.0047596 | -0.0075195 | 63.9862 | 64.1006 | 18.7408 | -58.699 | 64.1464 | -58.8638 | -58.9096 | -58.2275 | 0.9201 | -59.1522 | 64.1327 | 64.0091 | -58.9417 | -59.0286 | -0.018311 | -0.064087 | 0.041198 | 122.9462 | 0.14648 | 0.21057 | -0.11902 | -0.09613 | -0.1831 | 0.027465 | 0.61798 | -0.3067 | -0.1236 | -0.096131 | 122.9919 | 122.8317 | 77.5864 | -123.0148 | 122.9782 | 122.8546 | 59.7656 | -123.1338
1276.5156 | 123.1842 | -58.7494 | 64.1006 | -0.18616 | 0.014381 | 0.067586 | 0.067509 | 0.12977 | 0.00062595 | -0.00065152 | -0.0043486 | -0.0054004 | -0.0040226 | -0.0007498 | 0.00070077 | -0.0036743 | 64.0411 | 64.2792 | 18.9697 | -58.6487 | 64.0732 | -58.8318 | -58.8776 | -58.0719 | 1.1765 | -58.9508 | 64.1098 | 64.032 | -58.8867 | -58.9554 | -0.082397 | -0.12817 | -0.027466 | 123.0286 | 0.10071 | 0.22888 | -0.059509 | -0.13733 | -0.20599 | 0.009155 | 0.67749 | -0.20142 | 0.004577 | -0.068665 | 122.8226 | 122.7905 | 77.7191 | -122.9782 | 122.8592 | 122.7814 | 59.9258 | -123.056
1277.5156 | 123.0652 | -58.8089 | 64.1418 | -0.20905 | 0.011818 | 0.069295 | 0.070714 | 0.12913 | 0.0027622 | 0.0010575 | -0.1722 | -0.002837 | -0.0008182 | -0.0007498 | 0.002837 | -0.0062379 | 64.0366 | 64.1876 | 18.9468 | -58.6716 | 64.1373 | -58.8318 | -58.873 | -58.1726 | 1.0941 | -59.0424 | 64.1647 | 64.0411 | -58.9096 | -59.0057 | -0.022888 | -0.064087 | -0.004578 | 122.9965 | 0.13733 | 0.20142 | -0.10529 | -0.10071 | -0.19684 | 0.022888 | 0.63629 | -0.23346 | -0.036621 | -0.10071 | 122.9462 | 122.8455 | 77.7557 | -123.0148 | 122.9736 | 122.85 | 59.903 | -123.1476
1278.5156 | 123.1659 | -58.7723 | 64.1144 | -0.041199 | 0.0073315 | 0.068654 | 0.066227 | 0.12913 | -1.505e-05 | -0.0017197 | 0.087204 | -0.0051868 | -0.0023136 | -0.0030996 | 0.00070077 | -0.0043153 | 64.032 | 64.238 | 19.1666 | -58.6304 | 64.1006 | -58.8226 | -58.9005 | -58.0627 | 1.1948 | -58.9462 | 64.1052 | 63.9816 | -58.8821 | -58.9645 | -0.050354 | -0.12817 | -0.013733 | 123.0103 | 0.14191 | 0.27008 | -0.082398 | -0.10986 | -0.19226 | -0.009155 | 0.70953 | -0.17395 | 0.018311 | -0.13275 | 122.8729 | 122.8043 | 77.9388 | -123.0148 | 122.8775 | 122.7539 | 59.967 | -123.0789
1279.5156 | 123.1064 | -58.7769 | 64.1464 | -0.02594 | 0.01075 | 0.068654 | 0.072209 | 0.12892 | -0.0019376 | -0.0030013 | 0.071945 | -0.0054004 | -0.0035952 | -0.0016044 | 0.0013416 | -0.0064515 | 64.064 | 64.2838 | 19.2673 | -58.6212 | 64.0732 | -58.7997 | -58.8638 | -58.0078 | 1.3 | -58.9233 | 64.1052 | 63.9771 | -58.8684 | -58.9508 | -0.022889 | -0.086976 | -0.073242 | 123.0606 | 0.15564 | 0.24262 | -0.082397 | -0.091553 | -0.17395 | -0.041198 | 0.76904 | -0.14649 | 0.027466 | -0.16937 | 122.85 | 122.8409 | 78.0441 | -123.0103 | 122.8821 | 122.7539 | 60.0769 | -123.0972
1280.5156 | 123.0927 | -58.7906 | 64.1464 | -0.14801 | 0.014381 | 0.070149 | 0.069005 | 0.13148 | 0.0063938 | -0.00022432 | -0.073013 | -0.0024096 | -0.0025272 | -0.0022452 | 0.0071094 | -0.0081605 | 64.0366 | 64.151 | 19.1803 | -58.6487 | 64.1602 | -58.8318 | -58.8821 | -58.0994 | 1.2039 | -59.0515 | 64.1739 | 64.0411 | -58.905 | -58.9966 | -0.041199 | -0.091553 | 0.013733 | 122.9416 | 0.14191 | 0.23346 | -0.10986 | -0.11444 | -0.20599 | 0.027466 | 0.69122 | -0.26093 | -0.054932 | -0.10528 | 122.9507 | 122.8271 | 77.9709 | -123.0286 | 122.9645 | 122.8317 | 59.9945 | -123.143
1281.5156 | 123.1842 | -58.7402 | 64.1144 | -0.094604 | 0.010109 | 0.072499 | 0.070286 | 0.12977 | -0.001083 | -0.0010787 | 0.2169 | -0.0036914 | -0.0021 | -0.003527 | 0.0030506 | -0.0026063 | 64.119 | 64.3204 | 19.3771 | -58.5754 | 64.0961 | -58.8089 | -58.8547 | -58.0444 | 1.3458 | -58.9096 | 64.1006 | 64.0228 | -58.8867 | -58.9737 | -0.068665 | -0.11444 | -0.018311 | 123.0606 | 0.16479 | 0.27924 | 0.004578 | -0.14648 | -0.23346 | -0.013733 | 0.6958 | -0.16937 | 0.064087 | -0.091553 | 122.8363 | 122.8592 | 78.1174 | -122.9691 | 122.8409 | 122.7631 | 60.0861 | -123.0881
1282.5156 | 123.1888 | -58.7631 | 64.1052 | -0.018311 | 0.012031 | 0.068868 | 0.069645 | 0.13126 | 0.00062595 | -0.0017197 | 0.064316 | -0.0049732 | -0.0025272 | -0.0024588 | 0.0026234 | -0.0053833 | 64.0594 | 64.2288 | 19.3542 | -58.5938 | 64.1098 | -58.7997 | -58.873 | -57.9941 | 1.4191 | -58.9508 | 64.1464 | 64.0045 | -58.8821 | -58.9828 | -0.036621 | -0.10986 | 0.004577 | 122.9919 | 0.16937 | 0.27924 | -0.045777 | -0.11902 | -0.21973 | 0.041198 | 0.76904 | -0.18768 | 0.032043 | -0.10071 | 122.8729 | 122.8226 | 78.1174 | -122.9782 | 122.9095 | 122.7676 | 60.1822 | -123.0881
1283.5156 | 123.1522 | -58.7585 | 64.1281 | 3.125 | 0.01374 | 0.071004 | 0.070714 | 0.12763 | 0.00062595 | -1.0724e-05 | -0.073013 | -0.005614 | -0.0033816 | -0.0016044 | 0.0041186 | -0.0064515 | 64.1418 | 64.2609 | 19.4138 | -58.58 | 64.1144 | -58.7952 | -58.8409 | -57.9758 | 1.5106 | -58.9508 | 64.1373 | 64.0137 | -58.8638 | -58.9462 | -0.036621 | -0.082397 | -0.013733 | 123.0194 | 0.17853 | 0.26093 | 0.013733 | -0.10529 | -0.18768 | 0.009155 | 0.78278 | -0.19226 | -0.004578 | -0.11444 | 122.8729 | 122.9004 | 78.1723 | -122.9691 | 122.8958 | 122.7722 | 60.2692 | -123.0743
1284.5156 | 123.1705 | -58.7494 | 64.1052 | 0.065613 | 0.012672 | 0.069081 | 0.069859 | 0.12785 | 0.00041235 | -0.0015061 | 0.11772 | -0.0051868 | -0.0035952 | -0.0013906 | 0.0032642 | -0.0049561 | 64.0228 | 64.2288 | 19.4183 | -58.6121 | 64.1052 | -58.8043 | -58.8684 | -57.9941 | 1.5015 | -58.9554 | 64.1281 | 64.0091 | -58.8821 | -58.9691 | -0.054931 | -0.11902 | 0 | 122.9782 | 0.13733 | 0.25635 | -0.082398 | -0.13275 | -0.21973 | 0.022888 | 0.75531 | -0.20599 | 0.013733 | -0.096131 | 122.8546 | 122.7722 | 78.1677 | -122.9736 | 122.8775 | 122.7585 | 60.2509 | -123.0743
1285.5156 | 123.1522 | -58.7585 | 64.0915 | -0.13275 | 0.010536 | 0.071218 | 0.069218 | 0.12763 | -1.505e-05 | -0.0025741 | -0.073013 | -0.0049732 | -0.0038088 | -0.006304 | 0.0015552 | -0.0041017 | 64.1281 | 64.3158 | 19.5557 | -58.548 | 64.1144 | -58.7677 | -58.8409 | -58.0719 | 1.5564 | -58.9096 | 64.1006 | 64.0045 | -58.8776 | -58.9645 | -0.009155 | -0.082397 | 0.022888 | 123.0743 | 0.21057 | 0.29297 | 0.036621 | -0.11902 | -0.20599 | 0.009155 | 0.68665 | -0.15106 | 0.054932 | -0.086975 | 122.8729 | 122.8867 | 78.3142 | -122.9324 | 122.8592 | 122.7631 | 60.3149 | -123.056
1286.5156 | 123.1567 | -58.754 | 64.1052 | 0.16479 | 0.01374 | 0.067159 | 0.068577 | 0.12913 | 0.0021214 | -0.0027877 | 0.22453 | -0.003905 | -0.004877 | -0.001818 | 0.0026234 | -0.0060243 | 64.032 | 64.2059 | 19.4687 | -58.6349 | 64.0732 | -58.8318 | -58.8409 | -57.9758 | 1.5656 | -59.0149 | 64.1098 | 64.0182 | -58.8684 | -58.96 | -0.07782 | -0.086975 | -0.032044 | 122.9599 | 0.11902 | 0.20599 | -0.073243 | -0.11444 | -0.20599 | 0.004577 | 0.7782 | -0.26093 | -0.054932 | -0.086975 | 122.8271 | 122.7859 | 78.2227 | -122.9462 | 122.8638 | 122.7722 | 60.3195 | -123.0652
1287.5156 | 123.1705 | -58.7631 | 64.1098 | 0.027466 | 0.01139 | 0.069081 | 0.069432 | 0.12913 | 0.00083955 | -0.0019333 | 0.094833 | -0.0043324 | -0.0044498 | -0.0022452 | 0.00091437 | -0.0026063 | 64.064 | 64.2151 | 19.519 | -58.5938 | 64.119 | -58.8181 | -58.8455 | -57.9391 | 1.6571 | -58.9554 | 64.1281 | 64.0274 | -58.8638 | -58.9508 | -0.054931 | -0.082397 | 0.009156 | 122.9782 | 0.16937 | 0.25177 | -0.045776 | -0.10071 | -0.18768 | 0.018311 | 0.82397 | -0.19226 | -0.004577 | -0.082397 | 122.8821 | 122.8271 | 78.2822 | -122.9553 | 122.8912 | 122.7905 | 60.4202 | -123.0606
1288.5156 | 123.1201 | -58.7997 | 64.0869 | 0.13428 | 0.0098951 | 0.069295 | 0.069432 | 0.12892 | 0.0014804 | -0.00043792 | 0.17876 | -0.0051868 | -0.0027408 | -0.0013906 | 0.0019824 | -0.0055969 | 64.0732 | 64.183 | 19.5236 | -58.6212 | 64.0915 | -58.7952 | -58.8638 | -57.9666 | 1.9455 | -58.9233 | 64.1602 | 64.0274 | -58.8913 | -58.9508 | 0.004578 | -0.064087 | 0.004578 | 122.9828 | 0.17853 | 0.24262 | -0.013733 | -0.091552 | -0.15106 | 0.073242 | 0.83313 | -0.1236 | 0.027466 | -0.059509 | 122.8912 | 122.8729 | 78.3234 | -122.9507 | 122.9599 | 122.8271 | 60.7452 | -123.0377
1289.5156 | 123.0881 | -58.7357 | 64.0961 | 0.012207 | 0.01075 | 0.070577 | 0.067936 | 0.12913 | 0.0010532 | -0.00065152 | 0.041427 | -0.0036914 | -0.0038088 | -0.002886 | 0.0034778 | -0.0064515 | 64.1464 | 64.2929 | 19.6152 | -58.5617 | 64.1281 | -58.7906 | -58.8501 | -57.8476 | 1.918 | -58.9005 | 64.1144 | 64.0503 | -58.8501 | -58.9005 | -0.054931 | -0.11444 | 0.032044 | 123.0286 | 0.17395 | 0.28839 | 0.050354 | -0.11444 | -0.16479 | 0.018311 | 0.88806 | -0.16479 | 0 | -0.045776 | 122.8638 | 122.8821 | 78.3508 | -122.9462 | 122.85 | 122.7859 | 60.6537 | -122.9965
1290.5156 | 123.1613 | -58.7677 | 64.1098 | 0.042725 | 0.010322 | 0.069081 | 0.070073 | 0.12977 | 0.0021214 | 0.00020288 | 0.071945 | -0.0043324 | -0.0029544 | -0.0009634 | 0.0026234 | -0.0068787 | 64.0549 | 64.2288 | 19.5831 | -58.58 | 64.119 | -58.786 | -58.8776 | -57.8888 | 1.9775 | -58.9554 | 64.1373 | 64.0182 | -58.8318 | -58.9691 | -0.018311 | -0.10986 | 0.009156 | 122.9965 | 0.18768 | 0.29755 | -0.054931 | -0.064087 | -0.20142 | 0.027466 | 0.87891 | -0.18768 | 0.013733 | -0.091552 | 122.8867 | 122.8226 | 78.3508 | -122.9874 | 122.905 | 122.7859 | 60.7452 | -123.0789
1291.5156 | 123.1934 | -58.754 | 64.119 | -0.02594 | 0.010963 | 0.06844 | 0.0705 | 0.12892 | 0.002335 | -0.0042831 | -0.080643 | -0.0096728 | -0.0063724 | 0.0009592 | 0.0049732 | -0.0070923 | 64.1464 | 64.3433 | 19.6564 | -58.5251 | 64.1144 | -58.7952 | -58.8226 | -57.843 | 2.3163 | -58.9737 | 64.1006 | 63.9908 | -58.8501 | -58.9279 | -0.041199 | -0.068665 | -0.004578 | 123.0972 | 0.22888 | 0.29755 | 0.027465 | -0.096131 | -0.17395 | -0.018311 | 0.91095 | -0.21973 | -0.045777 | -0.12817 | 122.8683 | 122.9004 | 78.4103 | -122.9416 | 122.8546 | 122.7448 | 61.0703 | -123.0469
1292.5156 | 123.1201 | -58.7448 | 64.119 | 0.088501 | 0.0060497 | 0.071431 | 0.069432 | 0.12443 | 0.0014804 | -0.0023605 | 0.094833 | -0.0043324 | -0.0010318 | -0.003527 | 0.0030506 | -0.0034607 | 64.0457 | 64.2197 | 19.5969 | -58.6029 | 64.0915 | -58.8043 | -58.8547 | -57.9025 | 2.3392 | -58.9966 | 64.1144 | 64.0457 | -58.8821 | -58.9645 | -0.059509 | -0.10986 | -0.027466 | 122.9645 | 0.14191 | 0.25177 | -0.073243 | -0.13733 | -0.21973 | -0.004578 | 0.84229 | -0.25177 | -0.032043 | -0.073243 | 122.8363 | 122.7905 | 78.3417 | -122.9736 | 122.8592 | 122.7905 | 61.084 | -123.0835
1293.5156 | 123.1338 | -58.7723 | 64.119 | 0.10376 | 0.0098951 | 0.0678 | 0.069432 | 0.12977 | 0.00041235 | -0.0021469 | 0.11772 | -0.0051868 | -0.0040226 | 0.0007456 | 0.0043324 | -0.0051697 | 64.0686 | 64.238 | 19.6014 | -58.5892 | 64.1098 | -58.7952 | -58.8455 | -57.8476 | 2.3621 | -58.9783 | 64.1144 | 64.0228 | -58.873 | -58.9417 | -0.022888 | -0.073242 | -0.009156 | 123.0103 | 0.18311 | 0.25635 | -0.050354 | -0.10071 | -0.16937 | -0.004578 | 0.92468 | -0.20599 | -0.036621 | -0.096131 | 122.8821 | 122.8409 | 78.3737 | -122.9645 | 122.8867 | 122.7951 | 61.1343 | -123.0606
1294.5156 | 123.1613 | -58.7631 | 64.0961 | 0.19531 | 0.013527 | 0.069509 | 0.072209 | 0.13191 | 0.0042576 | 0.0014847 | 0.22453 | -0.002837 | -0.0021 | -0.0007498 | 0.006255 | -0.0053833 | 64.1098 | 64.2426 | 19.6335 | -58.5709 | 64.0594 | -58.7997 | -58.873 | -57.8339 | 2.5314 | -58.9828 | 64.1052 | 64.0137 | -58.873 | -58.9645 | -0.036621 | -0.10986 | -0.036621 | 123.0057 | 0.19226 | 0.30212 | 0.013733 | -0.10986 | -0.20142 | 0.009156 | 0.92926 | -0.21973 | -0.01831 | -0.082397 | 122.8226 | 122.8729 | 78.3966 | -122.9691 | 122.8683 | 122.7768 | 61.2946 | -123.0606
1295.5156 | 123.1705 | -58.7585 | 64.1235 | 0.088501 | 0.010109 | 0.068013 | 0.070286 | 0.12827 | 0.0021214 | -0.0012923 | 0.40001 | -0.0043324 | -0.004877 | -0.0022452 | 0.00070077 | -0.0064515 | 64.0778 | 64.2197 | 19.6518 | -58.4335 | 64.1739 | -58.7769 | -58.8226 | -57.8476 | 2.5864 | -58.9691 | 64.1418 | 64.0274 | -58.8638 | -58.9645 | -0.01831 | -0.064087 | 0.050354 | 122.9782 | 0.32501 | 0.3891 | -0.045776 | -0.10529 | -0.20599 | 0.018311 | 0.91095 | -0.21057 | -0.004577 | -0.09613 | 122.9324 | 122.8363 | 78.4103 | -122.9462 | 122.9004 | 122.7859 | 61.3449 | -123.0881
1296.5156 | 123.0927 | -58.7997 | 64.1098 | 0.19531 | 0.014808 | 0.066518 | 0.067936 | 0.12827 | 0.0021214 | 0.00041648 | 0.27031 | -0.0036914 | -0.0027408 | -0.0043814 | 0.0032642 | -0.0068787 | 64.119 | 64.2792 | 19.6335 | -58.5617 | 64.1144 | -58.7906 | -58.8455 | -57.8064 | 2.6917 | -58.9828 | 64.119 | 64.0182 | -58.8593 | -58.9874 | 0.009156 | -0.045776 | 0.004578 | 123.0789 | 0.23804 | 0.28381 | 0.009156 | -0.059509 | -0.18768 | 0.009156 | 0.99335 | -0.18311 | 0.004578 | -0.091552 | 122.9141 | 122.9187 | 78.4332 | -122.9553 | 122.9187 | 122.818 | 61.4914 | -123.0972
1297.5156 | 123.1155 | -58.754 | 64.1052 | 0.050354 | 0.0090405 | 0.069722 | 0.07285 | 0.12849 | 0.00019875 | -1.0724e-05 | 0.087204 | -0.0043324 | -0.001459 | -0.0016044 | 0.0019824 | -0.0045289 | 64.0961 | 64.1602 | 19.5786 | -58.5526 | 64.119 | -58.7952 | -58.8547 | -57.8064 | 2.7786 | -58.9783 | 64.1418 | 64.0503 | -58.8547 | -58.9325 | -0.041199 | -0.10071 | 0.013733 | 122.9141 | 0.20142 | 0.30212 | -0.009156 | -0.10071 | -0.17853 | 0.036621 | 0.94757 | -0.2243 | -0.045776 | -0.054932 | 122.8729 | 122.85 | 78.3325 | -122.9599 | 122.8958 | 122.8043 | 61.5326 | -123.0377
1298.5156 | 123.1842 | -58.7723 | 64.0915 | 0.073242 | 0.017158 | 0.068013 | 0.070927 | 0.13041 | 0.0046848 | -0.00043792 | 0.24742 | -0.0049732 | -0.0025272 | -0.0020316 | 0.0034778 | -0.0079469 | 64.1327 | 64.2609 | 19.6106 | -58.5388 | 64.0823 | -58.7952 | -58.8226 | -57.7377 | 2.8519 | -58.9508 | 64.1098 | 64.0274 | -58.8638 | -58.9554 | -0.022888 | -0.050354 | -0.009156 | 123.0331 | 0.23346 | 0.28381 | 0.041198 | -0.091553 | -0.1831 | 0.01831 | 1.0345 | -0.17853 | 0.004577 | -0.064087 | 122.8546 | 122.905 | 78.3829 | -122.9141 | 122.8821 | 122.7997 | 61.6241 | -123.0469
1299.5156 | 123.1155 | -58.7311 | 64.1281 | 0.12665 | 0.012886 | 0.06844 | 0.071568 | 0.12998 | 0.003403 | -0.0012923 | 0.13298 | -0.004546 | -0.003168 | -0.0003226 | 0.0030506 | -0.0053833 | 64.0732 | 64.2105 | 19.5786 | -58.5754 | 64.1006 | -58.7997 | -58.8593 | -57.7652 | 2.8519 | -58.9828 | 64.1144 | 64.0411 | -58.8684 | -58.9417 | -0.068665 | -0.12817 | -0.027466 | 122.9416 | 0.15564 | 0.28381 | -0.054932 | -0.13733 | -0.21057 | -0.013733 | 0.96588 | -0.25177 | -0.041199 | -0.086975 | 122.8317 | 122.8043 | 78.3096 | -122.9874 | 122.8455 | 122.7722 | 61.5829 | -123.0698
1300.5156 | 123.1338 | -58.786 | 64.1235 | 0.22583 | 0.018013 | 0.066945 | 0.07285 | 0.13041 | 0.0061802 | 0.0027665 | 0.2169 | -0.002837 | -0.001459 | -0.000109 | 0.0060412 | -0.0060243 | 64.0869 | 64.1373 | 19.5236 | -58.6075 | 64.1144 | -58.8272 | -58.9005 | -57.7698 | 2.8519 | -59.0332 | 64.1464 | 64.0228 | -58.8867 | -58.9554 | -0.041198 | -0.11444 | -0.009155 | 122.9233 | 0.17853 | 0.29297 | -0.036621 | -0.10071 | -0.16937 | 0.022888 | 1.0162 | -0.24719 | -0.07782 | -0.10071 | 122.9004 | 122.8729 | 78.3096 | -123.024 | 122.9324 | 122.8088 | 61.6379 | -123.0789
1301.5156 | 123.1293 | -58.754 | 64.0686 | 0.2182 | 0.013099 | 0.070577 | 0.068577 | 0.12956 | -0.00022865 | 0.00041648 | 0.27031 | -0.0043324 | 0.0011044 | -0.0007498 | 0.0013416 | -0.0041017 | 64.1144 | 64.2654 | 19.6152 | -58.5342 | 64.0686 | -58.7906 | -58.8272 | -57.7286 | 3.0212 | -58.9691 | 64.0961 | 64.0228 | -58.8913 | -58.9737 | -0.036621 | -0.073242 | 0 | 123.0194 | 0.21973 | 0.29297 | 0.045776 | -0.13733 | -0.21973 | 0.027465 | 1.0254 | -0.21515 | 0.004578 | -0.045777 | 122.8226 | 122.8683 | 78.3691 | -122.8958 | 122.85 | 122.7768 | 61.7752 | -123.0423
1302.5156 | 123.1888 | -58.754 | 64.0778 | 0.18768 | 0.01609 | 0.066945 | 0.0705 | 0.12913 | 0.0044712 | 0.00041648 | 0.28557 | -0.0049732 | 0.001959 | -0.001177 | 0.0032642 | -0.0064515 | 64.1373 | 64.238 | 19.6152 | -58.5251 | 64.0915 | -58.8043 | -58.8318 | -57.5912 | 3.035 | -58.9279 | 64.1281 | 64.0228 | -58.8593 | -58.9325 | -0.050354 | -0.07782 | 0.013733 | 122.9919 | 0.22888 | 0.3067 | 0.059509 | -0.10529 | -0.17853 | 0.050354 | 1.1627 | -0.17395 | 0.004578 | -0.054932 | 122.8455 | 122.8912 | 78.3691 | -122.9095 | 122.8821 | 122.7768 | 61.7889 | -123.0103
1303.5156 | 123.1293 | -58.7585 | 64.119 | 0.15717 | 0.012459 | 0.069722 | 0.069218 | 0.12849 | 0.002335 | -0.00022432 | 0.27031 | -0.0030506 | -0.0027408 | -0.0013906 | 0.0032642 | -0.0036743 | 64.1052 | 64.238 | 19.6152 | -58.5342 | 64.0869 | -58.7814 | -58.8638 | -57.7011 | 3.1448 | -58.9691 | 64.119 | 64.0274 | -58.8776 | -58.9462 | -0.022888 | -0.10529 | -0.032044 | 122.9965 | 0.2243 | 0.32959 | -0.013733 | -0.11902 | -0.18768 | 0 | 1.0574 | -0.21057 | -0.022888 | -0.091553 | 122.8455 | 122.8638 | 78.3737 | -122.9828 | 122.8775 | 122.7859 | 61.9034 | -123.0652
1304.5156 | 123.1842 | -58.7814 | 64.1006 | 0.20294 | 0.020149 | 0.070363 | 0.072636 | 0.13084 | 0.0046848 | 0.0029801 | 0.20927 | -0.0034778 | -0.0006046 | -0.0009634 | 0.0047596 | -0.0062379 | 64.064 | 64.1556 | 19.5557 | -58.5938 | 64.1235 | -58.8272 | -58.905 | -57.6828 | 3.1311 | -58.992 | 64.1373 | 64.0228 | -58.905 | -58.9783 | -0.045776 | -0.1236 | 0.022888 | 122.937 | 0.18768 | 0.31128 | -0.036621 | -0.1236 | -0.19684 | 0.036621 | 1.0986 | -0.21057 | -0.013733 | -0.07782 | 122.905 | 122.8455 | 78.3371 | -123.0057 | 122.9187 | 122.8043 | 61.9125 | -123.0789
1305.5156 | 123.1659 | -58.7769 | 64.1006 | 0.28687 | 0.015663 | 0.069936 | 0.068791 | 0.13062 | 0.001694 | 0.0014847 | 0.28557 | -0.0036914 | -0.0023136 | -0.0022452 | 0.0047596 | -0.0055969 | 64.1052 | 64.2517 | 19.6014 | -58.5251 | 64.0686 | -58.7997 | -58.8364 | -57.637 | 3.2227 | -58.9554 | 64.1281 | 64.0274 | -58.873 | -58.9508 | -0.022889 | -0.05951 | -0.032043 | 123.0286 | 0.25177 | 0.31128 | 0.004578 | -0.096131 | -0.17395 | 0.027466 | 1.1398 | -0.17853 | -0.004577 | -0.073242 | 122.8455 | 122.8821 | 78.3783 | -122.937 | 122.905 | 122.8043 | 61.9995 | -123.0515
1306.5156 | 123.0927 | -58.7677 | 64.1327 | 0.11902 | 0.019508 | 0.068654 | 0.072423 | 0.12849 | 0.0063938 | -1.0724e-05 | 0.17876 | -0.0030506 | -0.0029544 | 0.0009592 | 0.0047596 | -0.0049561 | 64.0686 | 64.1098 | 19.5511 | -58.5846 | 64.1647 | -58.8181 | -58.8638 | -57.692 | 3.1769 | -59.0607 | 64.1968 | 64.0961 | -58.8547 | -58.96 | -0.050354 | -0.096131 | 0.032044 | 122.8775 | 0.1831 | 0.27924 | -0.064086 | -0.086975 | -0.19226 | 0.064087 | 1.0757 | -0.29297 | -0.10071 | -0.036621 | 122.9324 | 122.8363 | 78.3188 | -122.9965 | 122.9645 | 122.8638 | 61.9446 | -123.0927
1307.5156 | 123.1384 | -58.7631 | 64.1144 | 0.20294 | 0.019508 | 0.069081 | 0.069005 | 0.13084 | 0.0038304 | 0.0012711 | 0.27031 | -0.001128 | -0.0001774 | -0.0003226 | 0.0041186 | -0.0043153 | 64.0823 | 64.151 | 19.6014 | -58.5663 | 64.1556 | -58.8089 | -58.8547 | -57.6324 | 3.2959 | -59.0012 | 64.1556 | 64.0411 | -58.8501 | -58.9371 | -0.045776 | -0.091552 | 0.041199 | 122.9141 | 0.19684 | 0.28839 | -0.032044 | -0.086975 | -0.17395 | 0.041199 | 1.1307 | -0.23804 | -0.064087 | -0.073242 | 122.9187 | 122.8455 | 78.3646 | -122.9691 | 122.9187 | 122.8043 | 62.059 | -123.0515
1308.5156 | 123.0652 | -58.8089 | 64.151 | 0.19531 | 0.019295 | 0.068654 | 0.070714 | 0.12934 | 0.007462 | 0.0025529 | -0.034867 | -0.001128 | 0.00025 | 0.000532 | 0.0030506 | -0.0053833 | 64.0137 | 64.3295 | 19.6106 | -58.5983 | 64.1785 | -58.8135 | -58.8684 | -57.6828 | 3.2913 | -59.0607 | 64.1647 | 64.1144 | -58.8867 | -58.9691 | -0.004578 | -0.059509 | 0.027466 | 123.1384 | 0.21057 | 0.27008 | -0.13733 | -0.07782 | -0.16022 | 0.013733 | 1.1261 | -0.25177 | -0.091553 | -0.036621 | 122.9874 | 122.8226 | 78.4195 | -123.0194 | 122.9736 | 122.9233 | 62.1002 | -123.1201
1309.5156 | 123.143 | -58.7357 | 64.1052 | 0.23346 | 0.018867 | 0.067586 | 0.069432 | 0.13126 | 0.0036166 | 0.00041648 | 0.28557 | -0.002837 | -0.0006046 | -0.0013906 | 0.0026234 | -0.0032471 | 64.0686 | 64.183 | 19.5877 | -58.5388 | 64.1418 | -58.8043 | -58.8409 | -57.5958 | 3.4927 | -58.9737 | 64.151 | 64.0594 | -58.8501 | -58.9417 | -0.068664 | -0.10528 | 0.036621 | 122.9187 | 0.19684 | 0.30212 | -0.036621 | -0.11444 | -0.20599 | 0.045776 | 1.1398 | -0.23804 | -0.032044 | -0.045777 | 122.8775 | 122.8043 | 78.3234 | -122.9462 | 122.8867 | 122.7951 | 62.2284 | -123.0469
1310.5156 | 123.0698 | -58.7906 | 64.1418 | 1.4084 | 0.021217 | 0.069509 | 0.073704 | 0.1302 | 0.0046848 | 0.00041648 | 0.1635 | -0.003905 | 0.00025 | -0.0005362 | 0.0017688 | -0.0045289 | 64.1006 | 64.0823 | 19.4916 | -58.5526 | 64.1785 | -58.7906 | -58.8455 | -57.6416 | 3.4515 | -59.0515 | 64.1785 | 64.1235 | -58.8867 | -58.9554 | 0 | -0.054932 | 0.036621 | 122.8729 | 0.23804 | 0.29297 | -0.041199 | -0.096131 | -0.16479 | 0.036621 | 1.149 | -0.26093 | -0.096131 | -0.018311 | 122.9691 | 122.8912 | 78.2822 | -122.9874 | 122.9691 | 122.9141 | 62.2421 | -123.0972
1311.5156 | 123.2162 | -58.7311 | 64.119 | 0.21057 | 0.018013 | 0.06844 | 0.069432 | 0.12849 | 0.0019078 | 0.00020288 | 0.38475 | -0.0019824 | -0.0018862 | -0.0024588 | 0.0015552 | -0.0047425 | 64.1006 | 64.2059 | 19.5831 | -58.4976 | 64.1281 | -58.7952 | -58.8409 | -57.5409 | 3.6758 | -58.9554 | 64.1464 | 64.0686 | -58.873 | -58.9508 | -0.064087 | -0.10986 | 0.009155 | 122.937 | 0.23346 | 0.34332 | -0.018311 | -0.14191 | -0.21973 | 0.027465 | 1.1902 | -0.2243 | -0.004577 | -0.050354 | 122.8592 | 122.8317 | 78.3142 | -122.9599 | 122.8775 | 122.7997 | 62.4069 | -123.0698
1312.5156 | 123.0286 | -58.754 | 64.183 | 0.11139 | 0.020149 | 0.0678 | 0.071568 | 0.1302 | 0.0031894 | 0.0025529 | 0.2169 | -0.0017688 | 0.0008908 | -0.0016044 | 0.0032642 | -0.0038879 | 64.0594 | 64.1006 | 19.455 | -58.5526 | 64.1602 | -58.8226 | -58.8638 | -57.6141 | 3.3691 | -59.2621 | 64.1144 | 64.0686 | -58.8913 | -58.9874 | -0.068665 | -0.10986 | -0.022888 | 122.8546 | 0.20142 | 0.31128 | -0.1236 | -0.13733 | -0.23346 | -0.068664 | 1.1398 | -0.50812 | -0.27466 | -0.11444 | 122.9141 | 122.8134 | 78.2089 | -123.0469 | 122.8683 | 122.8226 | 62.1231 | -123.1705
1313.5156 | 123.1018 | -58.754 | 64.1464 | 0.19531 | 0.019722 | 0.068654 | 0.071995 | 0.12977 | 0.001694 | -1.0724e-05 | 0.2932 | -0.00070077 | 0.0017454 | -0.0005362 | 0.0024096 | -0.0043153 | 64.0549 | 64.1602 | 19.4687 | -58.5388 | 64.1693 | -58.7997 | -58.8501 | -57.5546 | 3.6896 | -58.9966 | 64.1693 | 64.1006 | -58.8821 | -58.9417 | -0.045777 | -0.096131 | 0.022889 | 122.9141 | 0.21515 | 0.31128 | -0.091552 | -0.12817 | -0.18768 | 0.022889 | 1.1993 | -0.24261 | -0.054932 | -0.045776 | 122.9233 | 122.8088 | 78.2227 | -122.9965 | 122.9233 | 122.8546 | 62.4435 | -123.0881
1314.5156 | 123.0698 | -58.7677 | 64.1876 | -0.0030518 | 0.020576 | 0.070363 | 0.07285 | 0.13191 | 0.005112 | 0.0021255 | -0.0043486 | -0.0026234 | 3.6404e-05 | -0.0009634 | 0.0026234 | -0.0053833 | 64.119 | 64.1922 | 19.5236 | -58.4793 | 64.1693 | -58.7814 | -58.8409 | -57.5226 | 3.7628 | -59.0012 | 64.1968 | 64.119 | -58.873 | -58.9371 | -0.013733 | -0.073242 | -0.01831 | 122.9599 | 0.28839 | 0.36163 | -0.068664 | -0.10529 | -0.16937 | 0.009155 | 1.2451 | -0.23346 | -0.064087 | -0.068664 | 122.937 | 122.8867 | 78.2913 | -123.0286 | 122.9645 | 122.8867 | 62.5305 | -123.1247
1315.5156 | 123.0377 | -58.7769 | 64.1602 | 0.40131 | 0.019295 | 0.068013 | 0.072423 | 0.12977 | 0.0042576 | 0.0014847 | 0.19402 | -0.0030506 | 0.0015316 | 0.000532 | 0.0041186 | -0.0041017 | 64.0182 | 64.1144 | 19.3909 | -58.5434 | 64.1647 | -58.8226 | -58.8821 | -57.55 | 3.7216 | -59.0607 | 64.1739 | 64.1052 | -58.8867 | -58.9737 | -0.045777 | -0.10529 | 0.004578 | 122.8912 | 0.23346 | 0.33874 | -0.14191 | -0.10986 | -0.19684 | 0.013733 | 1.2268 | -0.28381 | -0.086975 | -0.054931 | 122.9416 | 122.7951 | 78.1677 | -123.0423 | 122.9507 | 122.8821 | 62.4985 | -123.1338
1316.5156 | 123.0789 | -58.7494 | 64.1785 | -0.033569 | 0.020576 | 0.067372 | 0.068577 | 0.13105 | 0.0055392 | 0.0014847 | 0.056686 | -0.0024096 | 0.0008908 | -0.0013906 | 0.0024096 | -0.0043153 | 64.0915 | 64.183 | 19.4229 | -58.4976 | 64.1418 | -58.7631 | -58.8409 | -57.4997 | 3.8223 | -59.0195 | 64.1876 | 64.119 | -58.8684 | -58.9508 | -0.013733 | -0.091552 | -0.036621 | 122.9324 | 0.25177 | 0.34332 | -0.086975 | -0.11902 | -0.20142 | 0.009155 | 1.2497 | -0.27008 | -0.068664 | -0.059509 | 122.8912 | 122.8409 | 78.1723 | -123.0194 | 122.937 | 122.8683 | 62.5717 | -123.1293
1317.5156 | 123.0972 | -58.7677 | 64.1693 | 0.2182 | 0.019935 | 0.06844 | 0.07285 | 0.12742 | 0.003403 | -0.0017197 | 0.23216 | -0.002837 | 0.0011044 | -0.0013906 | 0.0030506 | -0.0047425 | 64.0274 | 64.1373 | 19.3359 | -58.5297 | 64.1739 | -58.7769 | -58.8455 | -57.4997 | 3.7903 | -59.0378 | 64.1785 | 64.0961 | -58.8867 | -58.9737 | -0.009155 | -0.07782 | 0.004577 | 122.905 | 0.23804 | 0.31586 | -0.14191 | -0.11902 | -0.20599 | 0.009155 | 1.268 | -0.27008 | -0.064087 | -0.073243 | 122.9416 | 122.7951 | 78.1036 | -123.0148 | 122.9462 | 122.8638 | 62.558 | -123.143
1318.5156 | 123.056 | -58.7723 | 64.1968 | 0.012207 | 0.021858 | 0.067586 | 0.071995 | 0.13212 | 0.004044 | 0.0021255 | 0.13298 | -0.0024096 | -0.000391 | 0.0009592 | 0.0051868 | -0.0053833 | 64.1006 | 64.1739 | 19.3726 | -58.4976 | 64.1693 | -58.7585 | -58.8455 | -57.4677 | 3.9505 | -59.024 | 64.1968 | 64.1327 | -58.8776 | -58.9462 | 0.013733 | -0.073242 | -0.027465 | 122.9462 | 0.27466 | 0.3479 | -0.09613 | -0.10529 | -0.17395 | 0 | 1.3046 | -0.25177 | -0.07782 | -0.064087 | 122.9416 | 122.8729 | 78.1448 | -123.0423 | 122.9691 | 122.905 | 62.7228 | -123.143
1319.5156 | 123.0377 | -58.7677 | 64.1739 | 0.12665 | 0.021004 | 0.068227 | 0.073063 | 0.13276 | 0.012162 | -0.0012923 | 0.041427 | -0.0032642 | 0.001318 | 0.0003182 | 0.003905 | -0.0045289 | 63.7299 | 64.5035 | 19.4595 | -58.5068 | 64.183 | -58.7677 | -58.8501 | -57.4768 | 4.0192 | -59.0561 | 64.1876 | 64.1373 | -58.8593 | -58.9554 | 0 | -0.082398 | 0.009155 | 123.2712 | 0.26093 | 0.34332 | -0.44403 | -0.091553 | -0.18768 | 0.013733 | 1.2909 | -0.28839 | -0.10071 | -0.036621 | 122.9507 | 122.4976 | 78.2272 | -123.024 | 122.9553 | 122.905 | 62.7869 | -123.1293
1320.5156 | 123.0652 | -58.7357 | 64.1876 | -0.12512 | 0.022926 | 0.068654 | 0.073063 | 0.12998 | 0.0066074 | -0.00022432 | 0.071945 | -0.0030506 | -0.0010318 | -0.0003226 | 0.00091437 | -0.0049561 | 64.119 | 64.2151 | 19.3039 | -58.4656 | 64.1922 | -58.7814 | -58.8455 | -57.399 | 4.1702 | -58.9874 | 64.1785 | 64.1373 | -58.8409 | -58.9371 | -0.045776 | -0.10986 | 0.004578 | 122.9507 | 0.27008 | 0.37994 | -0.068664 | -0.10528 | -0.20142 | -0.009155 | 1.3367 | -0.25177 | -0.050354 | -0.050354 | 122.9279 | 122.8546 | 78.0396 | -123.0331 | 122.9141 | 122.8729 | 62.9059 | -123.1247
1321.5156 | 123.0515 | -58.7677 | 64.1968 | 0.027466 | 0.021644 | 0.067372 | 0.074345 | 0.13041 | 0.0036166 | 0.0012711 | 0.087204 | -0.00070077 | 0.0004636 | -0.0005362 | 0.0030506 | -0.0034607 | 64.0915 | 64.1739 | 19.2673 | -58.493 | 64.1739 | -58.8043 | -58.8455 | -57.4127 | 4.2206 | -59.024 | 64.1968 | 64.1464 | -58.8364 | -58.9691 | -0.036621 | -0.07782 | -0.022888 | 122.9416 | 0.27466 | 0.35248 | -0.10528 | -0.068665 | -0.20142 | 0 | 1.355 | -0.25635 | -0.054932 | -0.050354 | 122.9416 | 122.8592 | 78.035 | -123.0423 | 122.9645 | 122.9141 | 62.9883 | -123.1659
1322.5156 | 123.111 | -58.7311 | 64.2059 | -0.033569 | 0.02079 | 0.066518 | 0.072209 | 0.13041 | 0.005112 | 0.00063028 | -0.41634 | -0.001128 | 0.0004636 | -0.000109 | 0.0026234 | -0.0045289 | 64.1144 | 64.1373 | 19.1483 | -58.5388 | 64.151 | -58.7631 | -58.8181 | -57.3029 | 4.3396 | -58.9508 | 64.2105 | 64.1464 | -58.8501 | -58.9142 | -0.032044 | -0.086975 | -0.054932 | 122.8683 | 0.19226 | 0.27924 | -0.091553 | -0.11902 | -0.18311 | 0.004577 | 1.4282 | -0.21973 | -0.036621 | -0.05951 | 122.8821 | 122.8455 | 77.8793 | -123.024 | 122.9416 | 122.8775 | 63.0707 | -123.1201
1323.5156 | 123.0148 | -58.7494 | 64.2014 | 0.050354 | 0.021858 | 0.066731 | 0.069432 | 0.13062 | 0.0066074 | -1.0724e-05 | 0.11772 | -0.001128 | -0.0001774 | -0.0026724 | 0.0036914 | -0.0055969 | 64.064 | 64.1647 | 19.1666 | -58.4747 | 64.1922 | -58.7402 | -58.8501 | -57.3807 | 4.3304 | -59.0149 | 64.1922 | 64.1327 | -58.8593 | -58.9783 | 0.009156 | -0.10071 | -0.009155 | 122.9141 | 0.27466 | 0.37537 | -0.13733 | -0.10986 | -0.22888 | -0.009155 | 1.3687 | -0.2655 | -0.036622 | -0.068665 | 122.9416 | 122.8134 | 77.916 | -123.0515 | 122.9416 | 122.8821 | 63.0798 | -123.1796
1324.5156 | 123.0881 | -58.7311 | 64.2151 | -0.4303 | 0.022072 | 0.067586 | 0.073704 | 0.1302 | 0.0038304 | 0.0010575 | 0.033798 | -0.0019824 | -0.0001774 | -0.0024588 | 0.0041186 | -0.0060243 | 64.1373 | 64.2334 | 19.1757 | -58.429 | 64.2105 | -58.7631 | -58.8135 | -57.2754 | 4.4724 | -58.9645 | 64.2014 | 64.1418 | -58.8455 | -58.9508 | -0.032044 | -0.082398 | -0.004578 | 122.9645 | 0.30212 | 0.38452 | -0.07782 | -0.11444 | -0.21973 | -0.013733 | 1.4557 | -0.23346 | -0.013733 | -0.073242 | 122.9416 | 122.8683 | 77.9068 | -123.0286 | 122.9324 | 122.8729 | 63.2034 | -123.1659
1325.5156 | 123.056 | -58.7494 | 64.2105 | 0.10376 | 0.021858 | 0.068013 | 0.073918 | 0.1287 | 0.003403 | 0.0016983 | 0.17113 | -0.0015552 | -0.0006046 | -0.0009634 | 0.0034778 | -0.0030335 | 64.0549 | 64.1373 | 19.0475 | -58.4885 | 64.1922 | -58.7723 | -58.8364 | -57.3669 | 4.4357 | -59.0332 | 64.2242 | 64.1373 | -58.8821 | -58.96 | -0.022888 | -0.086975 | -0.01831 | 122.8867 | 0.26093 | 0.3479 | -0.15564 | -0.13275 | -0.21057 | 0.013733 | 1.3824 | -0.28381 | -0.073242 | -0.073242 | 122.9416 | 122.8043 | 77.7969 | -123.0469 | 122.9736 | 122.8867 | 63.1851 | -123.1705
1326.5156 | 123.1155 | -58.7265 | 64.2059 | -0.086975 | 0.021004 | 0.069509 | 0.074345 | 0.13191 | 0.0044712 | 0.00041648 | 0.54497 | -0.0030506 | -0.0008182 | 0.0001046 | 0.0036914 | -0.0043153 | 64.1144 | 64.2517 | 19.0796 | -58.4152 | 64.1785 | -58.7402 | -58.8043 | -57.1884 | 4.5593 | -58.9417 | 64.2517 | 64.151 | -58.8318 | -58.8913 | -0.013733 | -0.07782 | -0.027466 | 122.9782 | 0.31128 | 0.3891 | -0.091553 | -0.10529 | -0.16479 | 0.045776 | 1.5381 | -0.21515 | -0.050354 | -0.054932 | 122.905 | 122.8409 | 77.8061 | -123.0103 | 122.9782 | 122.8775 | 63.2858 | -123.0972
1327.5156 | 123.0927 | -58.7311 | 64.1876 | -0.1709 | 0.020576 | 0.068227 | 0.073063 | 0.12977 | 0.0053256 | -1.0724e-05 | 0.064316 | -0.0032642 | 0.0017454 | -0.0003226 | 0.0032642 | -0.0026063 | 64.1464 | 64.238 | 19.0247 | -58.4061 | 64.1922 | -58.7494 | -58.8181 | -57.225 | 4.6509 | -58.9737 | 64.2014 | 64.151 | -58.8364 | -58.9417 | -0.018311 | -0.086975 | 0.004578 | 122.9691 | 0.32501 | 0.41199 | -0.041199 | -0.10529 | -0.21057 | 0.013733 | 1.506 | -0.24262 | -0.032044 | -0.036621 | 122.9233 | 122.8775 | 77.7557 | -123.0057 | 122.9324 | 122.8821 | 63.382 | -123.1293
1328.5156 | 123.0743 | -58.7128 | 64.2288 | -0.14038 | 0.018867 | 0.0678 | 0.071782 | 0.13169 | 0.0027622 | -0.0010787 | -0.088272 | -0.002196 | 0.001318 | -0.0007498 | 0.0024096 | -0.0023927 | 64.0915 | 64.2242 | 18.9697 | -58.4015 | 64.2288 | -58.7585 | -58.8043 | -57.2159 | 4.6692 | -58.9554 | 64.2517 | 64.2059 | -58.7952 | -58.905 | -0.045776 | -0.091552 | 0 | 122.937 | 0.31128 | 0.40283 | -0.13733 | -0.082397 | -0.19226 | 0.022888 | 1.4969 | -0.24261 | -0.050354 | -0.022888 | 122.9416 | 122.8043 | 77.6825 | -123.0331 | 122.9645 | 122.9187 | 63.382 | -123.1338
1329.5156 | 123.0927 | -58.7128 | 64.1968 | -0.02594 | 0.020363 | 0.068868 | 0.071995 | 0.13126 | 0.003403 | 0.00020288 | 0.087204 | -0.0034778 | 0.0032406 | -0.0007498 | 0.0030506 | -0.0055969 | 64.1144 | 64.2288 | 18.9468 | -58.4152 | 64.1876 | -58.7402 | -58.8089 | -57.1655 | 4.6783 | -58.9874 | 64.2334 | 64.1647 | -58.8501 | -58.905 | -0.027465 | -0.09613 | -0.009155 | 122.9416 | 0.29755 | 0.39368 | -0.082397 | -0.13733 | -0.19226 | 0.036621 | 1.5472 | -0.27466 | -0.082398 | -0.032043 | 122.9004 | 122.8271 | 77.6596 | -123.0057 | 122.9462 | 122.8775 | 63.3911 | -123.1018
1330.5156 | 123.0972 | -58.7082 | 64.2242 | -0.094604 | 0.019935 | 0.068868 | 0.072423 | 0.1287 | 0.004044 | -0.00043792 | -0.080643 | -0.0017688 | -0.0012454 | 0.0003182 | 0.0032642 | -0.0053833 | 64.1144 | 64.2242 | 18.9148 | -58.4015 | 64.2334 | -58.7402 | -58.786 | -57.1152 | 4.6783 | -58.9233 | 64.27 | 64.1785 | -58.7952 | -58.8776 | -0.032043 | -0.07782 | 0.009155 | 122.9324 | 0.3067 | 0.38452 | -0.10986 | -0.086975 | -0.16937 | 0.045777 | 1.593 | -0.21515 | -0.045777 | -0.045776 | 122.9416 | 122.8226 | 77.623 | -123.0103 | 122.9782 | 122.8867 | 63.3865 | -123.1018
1331.5156 | 123.0469 | -58.7128 | 64.2517 | 0.080872 | 0.022285 | 0.067586 | 0.072209 | 0.13319 | 0.004044 | 0.00063028 | 0.11009 | -0.0019824 | 0.0006772 | 0.0013864 | 0.004546 | -0.0051697 | 64.1052 | 64.2242 | 18.869 | -58.4152 | 64.2059 | -58.7631 | -58.8135 | -57.1426 | 4.8111 | -58.992 | 64.2471 | 64.1739 | -58.8364 | -58.9188 | -0.050354 | -0.10071 | -0.045776 | 122.937 | 0.29755 | 0.39825 | -0.14648 | -0.1236 | -0.20599 | -0.004578 | 1.5701 | -0.27923 | -0.073242 | -0.07782 | 122.9187 | 122.818 | 77.5818 | -123.0652 | 122.9599 | 122.8867 | 63.5239 | -123.1705
1332.5156 | 123.111 | -58.6945 | 64.238 | -0.14038 | 0.02079 | 0.068868 | 0.073491 | 0.13191 | 0.004044 | -0.0012923 | -0.0043486 | -0.0030506 | 0.0028134 | 0.0009592 | 0.0026234 | -0.0049561 | 64.1418 | 64.2517 | 18.8736 | -58.374 | 64.238 | -58.7265 | -58.786 | -57.0602 | 4.9164 | -58.9371 | 64.2563 | 64.1922 | -58.8043 | -58.8821 | -0.032043 | -0.091553 | 0 | 122.9462 | 0.32043 | 0.41199 | -0.09613 | -0.10986 | -0.18768 | 0.018311 | 1.6342 | -0.24262 | -0.054932 | -0.045776 | 122.9324 | 122.8363 | 77.5681 | -123.024 | 122.9507 | 122.8867 | 63.6108 | -123.1201
1333.5156 | 123.024 | -58.7219 | 64.2288 | 0.073242 | 0.023353 | 0.0678 | 0.073063 | 0.12827 | 0.0044712 | -0.00043792 | 0.2169 | -0.003905 | 0.0015316 | -0.0007498 | 0.002837 | -0.0064515 | 64.0686 | 64.1739 | 18.7729 | -58.4152 | 64.2288 | -58.7494 | -58.8135 | -57.1152 | 4.9301 | -59.0286 | 64.2242 | 64.1647 | -58.8455 | -58.9096 | -0.027466 | -0.091553 | 0 | 122.8958 | 0.3067 | 0.39825 | -0.16022 | -0.1236 | -0.18768 | -0.004578 | 1.6068 | -0.3067 | -0.11902 | -0.064087 | 122.9507 | 122.7905 | 77.4948 | -123.0423 | 122.9462 | 122.8867 | 63.652 | -123.1384
1334.5156 | 123.0515 | -58.7128 | 64.2609 | -0.14801 | 0.019935 | 0.069722 | 0.073277 | 0.13084 | 0.0019078 | -0.0010787 | -0.019608 | -0.0026234 | 0.0015316 | 0.0001046 | 0.001128 | -0.0038879 | 64.0869 | 64.2426 | 18.7546 | -58.374 | 64.2471 | -58.7357 | -58.7814 | -57.0328 | 5.1407 | -58.9554 | 64.2792 | 64.2242 | -58.786 | -58.8593 | -0.022888 | -0.068664 | -0.013733 | 122.9553 | 0.33875 | 0.40741 | -0.17395 | -0.073242 | -0.14648 | 0.018311 | 1.68 | -0.24261 | -0.09613 | -0.036621 | 122.9599 | 122.7997 | 77.4673 | -123.0423 | 122.9919 | 122.937 | 63.8535 | -123.1201
1335.5156 | 123.1018 | -58.6761 | 64.2288 | -0.094604 | 0.019722 | 0.0678 | 0.074131 | 0.13041 | 0.0027622 | 0.0012711 | 0.041427 | -0.0024096 | 0.00025 | -0.001177 | 0.0041186 | -0.0032471 | 64.151 | 64.2838 | 18.7592 | -58.3557 | 64.2105 | -58.7082 | -58.786 | -57.019 | 5.1178 | -58.8409 | 64.238 | 64.2014 | -58.8181 | -58.8776 | -0.032044 | -0.10986 | -0.018311 | 122.9599 | 0.32043 | 0.4303 | -0.07782 | -0.14191 | -0.20142 | 0.009155 | 1.6571 | -0.16479 | 0.036621 | -0.027466 | 122.8867 | 122.8271 | 77.4353 | -123.0148 | 122.9141 | 122.8775 | 63.7939 | -123.1064
1336.5156 | 123.143 | -58.6761 | 64.1876 | 0.25635 | 0.019508 | 0.068013 | 0.070286 | 0.12892 | 0.0019078 | -0.0017197 | 0.30846 | -0.0032642 | 0.0004636 | 0.0003182 | 0.0034778 | -0.0038879 | 64.0915 | 64.2151 | 18.6996 | -58.3969 | 64.1785 | -58.7357 | -58.7952 | -56.9229 | 5.2872 | -58.9233 | 64.1922 | 64.1235 | -58.8181 | -58.8959 | -0.05951 | -0.11902 | -0.009155 | 122.8912 | 0.27923 | 0.39825 | -0.09613 | -0.14191 | -0.21973 | 0.004578 | 1.7532 | -0.24719 | -0.027466 | -0.064087 | 122.8546 | 122.7676 | 77.3758 | -122.9828 | 122.8683 | 122.7997 | 63.9633 | -123.0835
1337.5156 | 123.0148 | -58.7082 | 64.2059 | 0.019836 | 0.02314 | 0.067372 | 0.073704 | 0.13319 | 0.0072482 | -0.00065152 | 0.11772 | -0.002837 | 0.0004636 | -0.0003226 | 0.0041186 | -0.0038879 | 64.1327 | 64.2197 | 18.6768 | -58.3832 | 64.2151 | -58.7311 | -58.786 | -56.9687 | 5.3696 | -58.9874 | 64.2563 | 64.2197 | -58.7906 | -58.9233 | -0.022888 | -0.07782 | 0.009155 | 122.9279 | 0.32501 | 0.40283 | -0.073243 | -0.082397 | -0.21515 | 0.050354 | 1.7395 | -0.27924 | -0.064087 | 0.013733 | 122.9233 | 122.8409 | 77.3849 | -122.9919 | 122.9645 | 122.9279 | 64.0778 | -123.1293
1338.5156 | 123.0972 | -58.7082 | 64.2334 | -0.15564 | 0.017372 | 0.067159 | 0.074345 | 0.13126 | 0.0055392 | 0.00084388 | -0.042496 | -0.0030506 | -0.0008182 | 0.000532 | 0.0024096 | -0.0049561 | 64.1418 | 64.2609 | 18.6676 | -58.3466 | 64.2151 | -58.7219 | -58.8089 | -56.8726 | 5.5389 | -58.9142 | 64.2517 | 64.2059 | -58.7769 | -58.873 | -0.013733 | -0.10071 | -0.01831 | 122.9691 | 0.36163 | 0.46234 | -0.091552 | -0.068664 | -0.16479 | 0.018311 | 1.8356 | -0.20599 | -0.041199 | -0.027465 | 122.9233 | 122.85 | 77.3758 | -123.0423 | 122.9599 | 122.9141 | 64.2471 | -123.1064
1339.5156 | 123.0423 | -58.7173 | 64.2197 | -0.0030518 | 0.019508 | 0.065663 | 0.074131 | 0.13233 | 0.0036166 | -0.0010787 | 0.087204 | -0.002196 | 0.0015316 | 0.0001046 | 0.0036914 | -0.0036743 | 64.1418 | 64.2609 | 18.6447 | -58.3603 | 64.1968 | -58.7448 | -58.7952 | -56.8954 | 5.7404 | -58.9737 | 64.2197 | 64.1693 | -58.8043 | -58.9371 | -0.027466 | -0.07782 | -0.022889 | 122.9782 | 0.35706 | 0.43488 | -0.07782 | -0.086975 | -0.21973 | 0 | 1.8219 | -0.25635 | -0.036621 | -0.050354 | 122.9141 | 122.8592 | 77.3621 | -123.0148 | 122.937 | 122.8867 | 64.4577 | -123.1567
1340.5156 | 123.0972 | -58.699 | 64.2197 | -0.16327 | 0.021004 | 0.06844 | 0.0705 | 0.12934 | 0.0046848 | -0.0012923 | -0.10353 | -0.0026234 | -0.000391 | 0.0001046 | 0.003905 | -0.0034607 | 64.1052 | 64.2426 | 18.6035 | -58.3374 | 64.238 | -58.7357 | -58.7906 | -56.8771 | 5.9921 | -58.9371 | 64.2426 | 64.2059 | -58.8135 | -58.8913 | -0.036621 | -0.091552 | 0.01831 | 122.9416 | 0.36163 | 0.45319 | -0.11444 | -0.11444 | -0.19226 | 0.022888 | 1.8219 | -0.23804 | -0.045777 | -0.013733 | 122.937 | 122.8043 | 77.3026 | -123.0103 | 122.9416 | 122.905 | 64.6912 | -123.111
1341.5156 | 123.143 | -58.7128 | 64.1693 | 0.23346 | 0.019722 | 0.0678 | 0.072636 | 0.13233 | 0.0027622 | 0.0014847 | 0.30846 | -0.003905 | 0.0006772 | 0.000532 | 0.0034778 | -0.0028199 | 64.1006 | 64.2242 | 18.5623 | -58.3786 | 64.1968 | -58.7448 | -58.7952 | -56.8039 | 6.0791 | -58.9096 | 64.1876 | 64.1556 | -58.8318 | -58.9279 | -0.032043 | -0.082397 | 0.027465 | 122.937 | 0.33417 | 0.41656 | -0.068665 | -0.11902 | -0.21515 | 0.01831 | 1.9089 | -0.19684 | 0.01831 | -0.013733 | 122.9095 | 122.8134 | 77.2751 | -122.9645 | 122.9004 | 122.8683 | 64.7919 | -123.0972
1342.5156 | 123.0606 | -58.7265 | 64.2517 | -0.18616 | 0.017586 | 0.069936 | 0.068791 | 0.13084 | 0.00019875 | -0.0051377 | -0.095902 | 0.00036743 | -0.0012454 | 0.0001046 | 0.001128 | -0.0047425 | 64.1922 | 64.3753 | 18.4845 | -58.4747 | 64.2609 | -58.7219 | -58.8043 | -56.8222 | 6.1432 | -58.9462 | 64.2929 | 64.2059 | -58.8181 | -58.9142 | 0.004577 | -0.07782 | 0.009155 | 123.1018 | 0.25177 | 0.32959 | -0.059509 | -0.091553 | -0.18768 | 0.041199 | 1.9043 | -0.21973 | -0.032043 | -0.045776 | 122.9874 | 122.9187 | 77.211 | -123.056 | 123.0194 | 122.9324 | 64.8697 | -123.1659
1343.5156 | 123.1018 | -58.699 | 64.2105 | -0.079346 | 0.020576 | 0.071645 | 0.071141 | 0.13255 | 0.005753 | 0.00084388 | 0.40001 | -0.0041186 | -0.0006046 | -0.0016044 | 0.0054004 | -0.0075195 | 64.2288 | 63.9908 | 18.4113 | -58.3237 | 64.2151 | -58.7265 | -58.7952 | -56.7719 | 6.3721 | -58.9417 | 64.2471 | 64.1556 | -58.8181 | -58.8913 | -0.027465 | -0.09613 | 0.004578 | 122.6898 | 0.37537 | 0.4715 | 0.018311 | -0.11902 | -0.19226 | 0.036621 | 1.9272 | -0.24261 | -0.050354 | -0.054931 | 122.9141 | 122.9279 | 77.1103 | -123.0057 | 122.9462 | 122.8546 | 65.0711 | -123.1018
1344.5156 | 123.0789 | -58.699 | 64.2471 | -0.086975 | 0.015877 | 0.069509 | 0.071141 | 0.1287 | 0.0036166 | -0.0010787 | -0.080643 | -0.0032642 | -0.000391 | 0.0013864 | 0.003905 | -0.0062379 | 64.0732 | 64.2059 | 18.4433 | -58.3603 | 64.2242 | -58.754 | -58.7814 | -56.8039 | 6.5598 | -58.9462 | 64.2471 | 64.2151 | -58.8043 | -58.9279 | -0.054931 | -0.082397 | -0.022888 | 122.905 | 0.33875 | 0.42114 | -0.17395 | -0.10529 | -0.22888 | 0 | 1.8951 | -0.24719 | -0.018311 | -0.032043 | 122.9233 | 122.7722 | 77.1423 | -123.0286 | 122.9462 | 122.9141 | 65.2588 | -123.175
1345.5156 | 123.0972 | -58.7082 | 64.2334 | -0.086975 | 0.019935 | 0.067372 | 0.072209 | 0.12934 | 0.0091708 | 0.00020288 | 0.071945 | -0.0024096 | 0.0011044 | 0.0001046 | 0.0041186 | -0.0053833 | 64.1327 | 64.2517 | 18.425 | -58.3466 | 64.2242 | -58.754 | -58.7814 | -56.7169 | 6.6788 | -58.9645 | 64.2334 | 64.1556 | -58.8043 | -58.9188 | -0.045776 | -0.073242 | -0.009155 | 122.9599 | 0.36163 | 0.43487 | -0.10071 | -0.09613 | -0.21057 | 0 | 1.9913 | -0.25635 | -0.045777 | -0.077819 | 122.9324 | 122.8409 | 77.1332 | -123.0148 | 122.9416 | 122.8638 | 65.387 | -123.1522
1346.5156 | 123.1796 | -58.7128 | 64.1556 | 0.17242 | 0.017158 | 0.068227 | 0.071995 | 0.13105 | 0.0025486 | 0.00020288 | 0.36186 | -0.002837 | 0.0021726 | -0.0013906 | -0.00015383 | -0.0030335 | 64.1235 | 64.2883 | 18.4387 | -58.3145 | 64.151 | -58.7494 | -58.8089 | -56.5613 | 6.8161 | -58.8638 | 64.1739 | 64.1144 | -58.8089 | -58.8867 | -0.036621 | -0.09613 | -0.004578 | 123.0011 | 0.39825 | 0.49438 | -0.032044 | -0.09613 | -0.17395 | 0.01831 | 2.1515 | -0.15106 | 0.022888 | -0.041199 | 122.8638 | 122.8363 | 77.1515 | -122.9645 | 122.8867 | 122.8271 | 65.5289 | -123.0423
1347.5156 | 123.1293 | -58.7036 | 64.2334 | -0.071716 | 0.021217 | 0.069295 | 0.073704 | 0.13126 | 0.0095982 | -0.00022432 | -0.0043486 | -0.0026234 | 0.0006772 | -0.000109 | 0.0017688 | -0.0058105 | 63.9816 | 64.4119 | 18.4113 | -58.3282 | 64.2197 | -58.754 | -58.7769 | -56.6437 | 7.0038 | -58.9371 | 64.2334 | 64.1922 | -58.786 | -58.8959 | -0.050354 | -0.073242 | -0.013732 | 123.1155 | 0.37537 | 0.44861 | -0.25177 | -0.082398 | -0.19226 | 0 | 2.0599 | -0.23346 | -0.041199 | -0.041198 | 122.9233 | 122.6852 | 77.1149 | -123.0103 | 122.937 | 122.8958 | 65.7074 | -123.1293
1348.5156 | 123.0057 | -58.7036 | 64.2426 | -0.29297 | 0.017799 | 0.068868 | 0.071141 | 0.12849 | -0.00044225 | -1.0724e-05 | -0.065384 | -0.002196 | -0.0006046 | -0.0003226 | -0.0010082 | -0.0070923 | 64.0961 | 64.2334 | 18.3472 | -58.3374 | 64.2471 | -58.7128 | -58.786 | -56.6162 | 7.3837 | -59.0561 | 64.2883 | 64.2563 | -58.7997 | -58.8867 | -0.009156 | -0.082398 | 0.004577 | 122.937 | 0.36621 | 0.44861 | -0.14648 | -0.096131 | -0.18311 | 0.045776 | 2.0874 | -0.35248 | -0.16937 | 0.013733 | 122.9507 | 122.7997 | 77.0508 | -123.0286 | 122.9919 | 122.9599 | 66.0873 | -123.1293
1349.5156 | 123.1064 | -58.7311 | 64.2288 | -0.10986 | 0.021431 | 0.067586 | 0.072209 | 0.12827 | 0.0066074 | -0.00043792 | 0.049057 | -0.00070077 | 0.0025998 | 0.0009592 | 0.0083912 | -0.0047425 | 64.1464 | 64.2654 | 18.3334 | -58.3145 | 64.2197 | -58.7219 | -58.7769 | -56.6391 | 7.338 | -58.8547 | 64.2426 | 64.1922 | -58.7906 | -58.8959 | 0.009155 | -0.045776 | -0.009155 | 122.9965 | 0.41656 | 0.46234 | -0.082398 | -0.059509 | -0.16479 | 0.013733 | 2.092 | -0.1236 | 0.041199 | -0.036621 | 122.9507 | 122.8775 | 77.0645 | -123.0057 | 122.9736 | 122.9233 | 66.069 | -123.1247
1350.5156 | 123.0423 | -58.7173 | 64.2792 | -0.57526 | 0.019295 | 0.067372 | 0.071995 | 0.1287 | 0.0025486 | -0.0012923 | -0.065384 | -0.0036914 | -0.0006046 | 0.0011728 | 0.0019824 | -0.0015381 | 64.0503 | 64.2288 | 18.2785 | -58.3466 | 64.2609 | -58.7631 | -58.8089 | -56.575 | 7.4249 | -58.9691 | 64.2517 | 64.2105 | -58.8089 | -58.9096 | -0.045777 | -0.091553 | -0.018311 | 122.9462 | 0.37079 | 0.46234 | -0.22888 | -0.091553 | -0.19226 | -0.027466 | 2.1423 | -0.25177 | -0.059509 | -0.068665 | 122.9782 | 122.7676 | 76.9958 | -123.0881 | 122.9691 | 122.9279 | 66.1423 | -123.1888
1351.5156 | 123.1293 | -58.7265 | 64.1922 | 0.19531 | 0.018654 | 0.069509 | 0.072209 | 0.13062 | 0.0025486 | -0.00086512 | 0.30083 | -0.0030506 | 0.0011044 | -0.0005362 | 0.0017688 | -0.0049561 | 64.0823 | 64.2105 | 18.2465 | -58.342 | 64.2105 | -58.754 | -58.7997 | -56.5018 | 7.4249 | -58.9417 | 64.1968 | 64.1373 | -58.8226 | -58.9142 | -0.027466 | -0.073243 | 0.01831 | 122.937 | 0.38452 | 0.45776 | -0.10986 | -0.096131 | -0.18768 | 0.004577 | 2.2247 | -0.21515 | -0.027465 | -0.054932 | 122.937 | 122.8088 | 76.973 | -122.9919 | 122.9233 | 122.8638 | 66.1514 | -123.1064
1352.5156 | 123.056 | -58.6945 | 64.2334 | -0.14801 | 0.014595 | 0.068868 | 0.07285 | 0.12956 | 0.0025486 | -0.00086512 | -0.073013 | -0.0032642 | -0.000391 | 0.0018136 | 0.002196 | -0.0032471 | 64.0869 | 64.2242 | 18.2007 | -58.3145 | 64.2517 | -58.7128 | -58.7952 | -56.5063 | 7.5439 | -58.9462 | 64.2517 | 64.2197 | -58.7814 | -58.8959 | -0.018311 | -0.10071 | 0.018311 | 122.9187 | 0.37994 | 0.48065 | -0.14648 | -0.086975 | -0.20142 | 0.018311 | 2.1881 | -0.25177 | -0.050354 | -0.013732 | 122.9462 | 122.7814 | 76.8951 | -123.0286 | 122.9462 | 122.9141 | 66.2384 | -123.1293
1353.5156 | 123.0835 | -58.7036 | 64.2288 | -0.12512 | 0.02079 | 0.069722 | 0.075627 | 0.13276 | 0.004044 | -0.0023605 | -0.0043486 | 0.0010082 | 0.0023862 | -0.0007498 | 0.002196 | -0.0058105 | 64.1602 | 64.2654 | 18.1961 | -58.3054 | 64.2197 | -58.7265 | -58.7814 | -56.4331 | 7.7957 | -58.9279 | 64.238 | 64.2059 | -58.7997 | -58.8638 | -0.022888 | -0.07782 | -0.009155 | 122.9691 | 0.39825 | 0.47607 | -0.068665 | -0.096131 | -0.16022 | 0.009155 | 2.2705 | -0.2243 | -0.064086 | -0.022888 | 122.9233 | 122.8638 | 76.8997 | -123.0103 | 122.9416 | 122.9095 | 66.4993 | -123.0927
1354.5156 | 123.0515 | -58.6853 | 64.2792 | 0.8667 | 0.016304 | 0.071858 | 0.072423 | 0.12934 | 0.0012668 | -0.00022432 | -0.050125 | -0.002837 | 0.0008908 | 0.000532 | 0.0024096 | -0.0034607 | 64.119 | 64.1968 | 18.1137 | -58.287 | 64.2517 | -58.7357 | -58.8043 | -56.4239 | 7.8918 | -58.9462 | 64.2792 | 64.2014 | -58.7997 | -58.905 | -0.050354 | -0.11902 | -0.027466 | 122.8821 | 0.39825 | 0.51727 | -0.16022 | -0.11444 | -0.21973 | 0 | 2.2614 | -0.26093 | -0.041199 | -0.07782 | 122.937 | 122.8043 | 76.799 | -123.0835 | 122.9645 | 122.8867 | 66.5771 | -123.1842
1355.5156 | 123.0743 | -58.7036 | 64.2517 | -0.13275 | 0.021431 | 0.069936 | 0.074345 | 0.13169 | 0.001694 | 0.00084388 | -0.095902 | -0.0019824 | 0.0008908 | 0.0003182 | 0.0030506 | -0.0038879 | 64.1052 | 64.2334 | 18.1046 | -58.2916 | 64.2609 | -58.7082 | -58.8089 | -56.3644 | 8.02 | -58.9508 | 64.2654 | 64.1785 | -58.7997 | -58.905 | -0.004578 | -0.10529 | 0.009155 | 122.937 | 0.41199 | 0.51727 | -0.14648 | -0.096131 | -0.20142 | 0.013733 | 2.3392 | -0.24719 | -0.045777 | -0.073242 | 122.9645 | 122.8088 | 76.8082 | -123.0606 | 122.9691 | 122.8821 | 66.7236 | -123.1567
1356.5156 | 123.0469 | -58.7173 | 64.2609 | -0.14801 | 0.016304 | 0.069722 | 0.071141 | 0.13105 | -1.505e-05 | -0.00022432 | 0.37712 | -0.0013416 | -0.0018862 | -0.000109 | 0.0026234 | -0.0041017 | 64.064 | 64.2426 | 18.0817 | -58.3008 | 64.2746 | -58.7311 | -58.7814 | -56.3507 | 8.1024 | -58.9462 | 64.2471 | 64.1876 | -58.8272 | -58.9142 | -0.013733 | -0.064087 | 0.013733 | 122.9599 | 0.41656 | 0.48065 | -0.19684 | -0.10986 | -0.19684 | -0.013733 | 2.3666 | -0.22888 | -0.032043 | -0.073242 | 122.9919 | 122.7814 | 76.799 | -123.0423 | 122.9645 | 122.905 | 66.8198 | -123.175
1357.5156 | 123.0835 | -58.7082 | 64.2426 | -0.1709 | 0.021431 | 0.069295 | 0.074345 | 0.13062 | 0.0042576 | 0.00020288 | -0.10353 | -0.0034778 | 0.0011044 | -0.001818 | 0.002196 | -0.0073059 | 64.1144 | 64.238 | 18.0496 | -58.2642 | 64.2517 | -58.7402 | -58.7997 | -56.2729 | 8.3038 | -58.9142 | 64.2197 | 64.2105 | -58.8318 | -58.8913 | -0.032043 | -0.091553 | 0.009155 | 122.9462 | 0.44403 | 0.53558 | -0.12817 | -0.1236 | -0.1831 | -0.022888 | 2.4353 | -0.20599 | -0.022889 | -0.032044 | 122.9599 | 122.8226 | 76.7578 | -123.0423 | 122.9279 | 122.9187 | 67.012 | -123.1338
1358.5156 | 123.0835 | -58.6533 | 64.2838 | -0.1709 | 0.015022 | 0.070149 | 0.071354 | 0.13148 | 0.001694 | -0.0017197 | -0.065384 | -0.0034778 | -0.0008182 | 0.0013864 | 0.0013416 | -0.0019653 | 64.1006 | 64.238 | 17.9993 | -58.2962 | 64.2334 | -58.7311 | -58.7997 | -56.2683 | 8.4915 | -58.9554 | 64.2838 | 64.2105 | -58.7997 | -58.8913 | -0.07782 | -0.14648 | -0.050354 | 122.8912 | 0.35705 | 0.50354 | -0.18311 | -0.14648 | -0.23804 | 0 | 2.3849 | -0.30212 | -0.064087 | -0.073242 | 122.8867 | 122.7539 | 76.6525 | -123.0835 | 122.937 | 122.8638 | 67.1448 | -123.175
1359.5156 | 123.1064 | -58.6945 | 64.2288 | -0.14801 | 0.018867 | 0.068868 | 0.068364 | 0.13169 | 0.0055392 | 0.0021255 | -0.0043486 | -0.003905 | -0.000391 | 0.000532 | 0.0036914 | -0.0047425 | 64.1373 | 64.2609 | 17.9947 | -58.2504 | 64.2426 | -58.7128 | -58.7952 | -56.1859 | 8.7341 | -58.9233 | 64.238 | 64.1373 | -58.8181 | -58.9508 | -0.018311 | -0.10071 | 0.013733 | 122.9553 | 0.44403 | 0.54474 | -0.091553 | -0.1236 | -0.25635 | 0.009155 | 2.5085 | -0.22888 | 0.027466 | -0.091553 | 122.937 | 122.8317 | 76.6891 | -123.024 | 122.9324 | 122.8317 | 67.4286 | -123.1796
1360.5156 | 123.056 | -58.699 | 64.2563 | -0.18616 | 0.016304 | 0.07079 | 0.072209 | 0.13084 | 0.0038304 | 0.00020288 | -0.20271 | -0.002196 | -0.0018862 | -0.0005362 | 0.00070077 | -0.0030335 | 64.0732 | 64.1922 | 17.8986 | -58.3008 | 64.238 | -58.7448 | -58.8135 | -56.1905 | 8.8943 | -58.9554 | 64.2563 | 64.1922 | -58.7997 | -58.9096 | -0.045776 | -0.11444 | -0.018311 | 122.8912 | 0.39825 | 0.5127 | -0.18311 | -0.10071 | -0.21057 | 0 | 2.5085 | -0.25635 | -0.045776 | -0.064087 | 122.937 | 122.7722 | 76.5976 | -123.0698 | 122.9553 | 122.8912 | 67.5934 | -123.1659
1361.5156 | 123.0743 | -58.7082 | 64.2242 | -0.19379 | 0.021858 | 0.068227 | 0.073704 | 0.13276 | 0.005112 | -0.00022432 | -0.034867 | -0.0032642 | 0.001959 | 0.000532 | 0.002837 | -0.0049561 | 64.1373 | 64.2563 | 17.9077 | -58.2367 | 64.238 | -58.7448 | -58.8135 | -56.1172 | 9.1232 | -58.9233 | 64.238 | 64.1418 | -58.8043 | -58.9142 | -0.036621 | -0.10529 | 0.013733 | 122.9645 | 0.4715 | 0.57678 | -0.086975 | -0.09613 | -0.20599 | 0.013733 | 2.5909 | -0.21515 | -0.009155 | -0.082397 | 122.9462 | 122.8455 | 76.6159 | -123.0377 | 122.9462 | 122.85 | 67.8314 | -123.1384
1362.5156 | 123.0652 | -58.6899 | 64.2471 | -0.19379 | 0.016304 | 0.071004 | 0.070714 | 0.12849 | 0.0012668 | 0.0010575 | -0.042496 | -0.003905 | -0.0016726 | 0.0001046 | 0.001128 | -0.0041017 | 64.1281 | 64.3066 | 17.9535 | -58.2413 | 64.2059 | -58.7265 | -58.7814 | -56.0898 | 9.4162 | -58.9233 | 64.2197 | 64.1693 | -58.7906 | -58.905 | -0.036621 | -0.091553 | -0.041198 | 122.9965 | 0.44861 | 0.54016 | -0.11902 | -0.10071 | -0.21515 | -0.027465 | 2.6001 | -0.23346 | -0.018311 | -0.077819 | 122.8958 | 122.818 | 76.6434 | -123.0286 | 122.9095 | 122.8592 | 68.1061 | -123.1522
1363.5156 | 123.0972 | -58.7128 | 64.2014 | -0.056458 | 0.022712 | 0.069081 | 0.073063 | 0.13148 | 0.0046848 | 0.0010575 | -0.47737 | -0.0015552 | 0.0023862 | 0.000532 | 0.0041186 | -0.0055969 | 64.1144 | 64.2609 | 17.894 | -58.3282 | 64.2059 | -58.7769 | -58.8135 | -55.9891 | 9.6634 | -58.9371 | 64.2242 | 64.1281 | -58.7906 | -58.9325 | -0.064086 | -0.10071 | 0.004578 | 122.9736 | 0.38452 | 0.48523 | -0.086975 | -0.077819 | -0.21973 | 0.022888 | 2.7237 | -0.2243 | -0.004578 | -0.073242 | 122.9187 | 122.8271 | 76.6068 | -123.0148 | 122.937 | 122.8409 | 68.3762 | -123.1339
1364.5156 | 123.0606 | -58.7311 | 64.2288 | -0.1709 | 0.015663 | 0.070149 | 0.071354 | 0.12998 | 0.0014804 | 0.0012711 | -0.088272 | -0.001128 | -0.000391 | 0.003309 | 0.0019824 | -0.0043153 | 64.0594 | 64.2334 | 17.8299 | -58.2825 | 64.2334 | -58.7357 | -58.8043 | -56.0165 | 9.938 | -58.8364 | 64.2746 | 64.2517 | -58.7952 | -58.8959 | -0.004578 | -0.073242 | 0.004577 | 122.9645 | 0.44861 | 0.52185 | -0.16937 | -0.064087 | -0.16479 | 0.045776 | 2.7145 | -0.10529 | 0.059509 | 0.022888 | 122.9645 | 122.7905 | 76.561 | -123.0331 | 123.0057 | 122.9828 | 68.6691 | -123.1247
1365.5156 | 123.0972 | -58.7265 | 64.2288 | -0.19379 | 0.022712 | 0.06844 | 0.071995 | 0.12934 | 0.0059666 | 0.0019119 | -0.027237 | -0.003905 | 0.0008908 | 0.0001046 | 0.004546 | -0.0068787 | 64.1281 | 64.2517 | 17.8162 | -58.2413 | 64.2334 | -58.7677 | -58.8226 | -56.0028 | 10.0067 | -58.8867 | 64.2151 | 64.1556 | -58.8181 | -58.9325 | -0.041199 | -0.096131 | 0.004577 | 122.9782 | 0.48523 | 0.58136 | -0.10071 | -0.091553 | -0.20599 | -0.013733 | 2.7237 | -0.16022 | 0.045776 | -0.073242 | 122.9599 | 122.8546 | 76.5427 | -123.0515 | 122.9416 | 122.8821 | 68.7332 | -123.1613
1366.5156 | 123.0148 | -58.7082 | 64.2517 | -2.2232 | 0.015236 | 0.0678 | 0.068577 | 0.13191 | 0.0012668 | -0.00043792 | -0.027237 | -0.0019824 | -0.0012454 | 0.0022408 | 0.0024096 | -0.0028199 | 64.0549 | 64.2288 | 17.7383 | -58.287 | 64.2334 | -58.7494 | -58.8135 | -55.9387 | 10.3729 | -58.9645 | 64.2563 | 64.1876 | -58.8226 | -58.9142 | -0.041199 | -0.10529 | -0.018311 | 122.937 | 0.42114 | 0.52643 | -0.19684 | -0.11444 | -0.20599 | 0.004578 | 2.7695 | -0.25635 | -0.050354 | -0.064087 | 122.9416 | 122.7631 | 76.4465 | -123.0652 | 122.9645 | 122.8958 | 69.0811 | -123.1659
1367.5156 | 123.0743 | -58.7311 | 64.2334 | -0.15564 | 0.02314 | 0.069722 | 0.076481 | 0.13105 | 0.005112 | -0.0019333 | -0.095902 | 0.00058103 | 0.001959 | 0.0018136 | 0.0034778 | -0.0053833 | 64.1235 | 64.238 | 17.7063 | -58.223 | 64.2105 | -58.754 | -58.7952 | -55.8517 | 10.7208 | -58.9279 | 64.238 | 64.1647 | -58.7997 | -58.9096 | -0.022888 | -0.064087 | -0.022888 | 122.9691 | 0.50812 | 0.57221 | -0.10986 | -0.068665 | -0.17853 | 0.004578 | 2.8793 | -0.19684 | -0.01831 | -0.068664 | 122.9416 | 122.8546 | 76.4374 | -123.0286 | 122.9691 | 122.8958 | 69.4519 | -123.143
1368.5156 | 123.0515 | -58.7357 | 64.2151 | -0.27771 | 0.016945 | 0.06844 | 0.072209 | 0.13041 | 0.0010532 | -0.00086512 | -0.095902 | -0.0013416 | -0.0016726 | -0.0016044 | -0.00058103 | -0.0032471 | 64.0778 | 64.2563 | 17.6331 | -58.2779 | 64.2242 | -58.7585 | -58.8043 | -55.8243 | 10.6934 | -58.9828 | 64.2471 | 64.183 | -58.8364 | -58.9142 | -0.022888 | -0.068664 | 0.009155 | 122.9919 | 0.45776 | 0.52643 | -0.13733 | -0.10071 | -0.17853 | 0.032043 | 2.9114 | -0.24719 | -0.068664 | -0.032044 | 122.9599 | 122.8134 | 76.3687 | -123.0194 | 122.9828 | 122.9187 | 69.429 | -123.1293
1369.5156 | 123.0515 | -58.7311 | 64.2426 | 0.11139 | 0.018654 | 0.072927 | 0.072209 | 0.13126 | 0.0063938 | 0.00020288 | -0.057755 | -0.0026234 | 0.0017454 | -0.0003226 | 0.002196 | -0.0032471 | 64.0823 | 64.2197 | 17.5598 | -58.2596 | 64.2151 | -58.7402 | -58.8089 | -55.7877 | 11.1923 | -58.9645 | 64.2334 | 64.1556 | -58.8181 | -58.9233 | -0.009155 | -0.07782 | -0.027466 | 122.9507 | 0.4715 | 0.54932 | -0.16022 | -0.086975 | -0.19226 | -0.009156 | 2.9434 | -0.23346 | -0.041199 | -0.086975 | 122.9462 | 122.8134 | 76.2909 | -123.0515 | 122.9645 | 122.8867 | 69.9234 | -123.1659
1370.5156 | 123.0698 | -58.7128 | 64.2197 | -0.20905 | 0.016304 | 0.071004 | 0.072636 | 0.12892 | 0.00083955 | -0.00022432 | -0.065384 | -0.0034778 | 3.6404e-05 | -0.000109 | -0.00036743 | -0.0032471 | 64.1098 | 64.2975 | 17.5919 | -58.2092 | 64.1922 | -58.7173 | -58.7723 | -55.7327 | 11.4853 | -58.9096 | 64.2334 | 64.183 | -58.8089 | -58.8867 | -0.004577 | -0.059509 | -0.027466 | 123.0103 | 0.50354 | 0.56305 | -0.10986 | -0.09613 | -0.17395 | 0.013732 | 2.98 | -0.19684 | -0.022888 | -0.036622 | 122.905 | 122.8226 | 76.3046 | -122.9919 | 122.9462 | 122.8958 | 70.1981 | -123.1064
1371.5156 | 123.0469 | -58.7128 | 64.2471 | -0.15564 | 0.01844 | 0.070577 | 0.073277 | 0.12934 | 0.0038304 | -0.0012923 | -0.11116 | -0.003905 | 0.0021726 | 0.0026682 | 0.00027337 | -0.0043153 | 64.0869 | 64.2197 | 17.5003 | -58.2458 | 64.2426 | -58.7585 | -58.8409 | -55.7144 | 11.6821 | -58.9371 | 64.2517 | 64.1785 | -58.8043 | -58.9142 | -0.045776 | -0.12817 | -0.004577 | 122.9324 | 0.46692 | 0.59509 | -0.16022 | -0.091552 | -0.20142 | 0.004578 | 2.9984 | -0.2243 | -0.022888 | -0.068664 | 122.9553 | 122.7997 | 76.2131 | -123.0881 | 122.9645 | 122.8912 | 70.3949 | -123.1613
1372.5156 | 123.1018 | -58.7311 | 64.2517 | -0.19379 | 0.016304 | 0.071004 | 0.073704 | 0.1302 | 0.00083955 | -0.00043792 | -0.11116 | -0.0017688 | 0.0015316 | 0.0020272 | 0.00048697 | -0.0047425 | 64.0732 | 64.2517 | 17.4545 | -58.2184 | 64.2151 | -58.7357 | -58.786 | -55.6732 | 11.8973 | -58.9645 | 64.238 | 64.183 | -58.8272 | -58.9325 | -0.004578 | -0.054932 | -0.036621 | 122.9828 | 0.5127 | 0.56763 | -0.17853 | -0.09613 | -0.20142 | -0.013733 | 3.0579 | -0.23346 | -0.032044 | -0.068665 | 122.9462 | 122.8043 | 76.1856 | -123.0377 | 122.9691 | 122.9141 | 70.6284 | -123.1842
1373.5156 | 123.0881 | -58.7585 | 64.2151 | -0.14038 | 0.018654 | 0.069295 | 0.073918 | 0.13191 | 0.0046848 | -0.00043792 | -0.095902 | 0.00036743 | 3.6404e-05 | 0.0009592 | 0.0036914 | -0.0043153 | 64.0778 | 64.2014 | 17.4042 | -58.2504 | 64.2197 | -58.7677 | -58.8226 | -55.6183 | 12.1353 | -58.9554 | 64.238 | 64.1785 | -58.8272 | -58.9417 | -0.009155 | -0.064087 | 0.004578 | 122.9599 | 0.50812 | 0.5722 | -0.13733 | -0.068664 | -0.18311 | 0.022888 | 3.1403 | -0.19684 | -0.013733 | -0.036621 | 122.9782 | 122.8363 | 76.1627 | -123.0377 | 122.9965 | 122.937 | 70.8939 | -123.1567
1374.5156 | 123.1201 | -58.7128 | 64.238 | -0.18616 | 0.015449 | 0.072499 | 0.068364 | 0.13191 | 0.0014804 | -0.00086512 | -0.088272 | -0.0036914 | -0.0025272 | 0.0011728 | 0.0030506 | -0.0043153 | 64.119 | 64.2975 | 17.4408 | -58.1818 | 64.1647 | -58.754 | -58.7997 | -55.5359 | 12.41 | -58.905 | 64.2059 | 64.1281 | -58.8226 | -58.8959 | -0.041198 | -0.086975 | -0.073242 | 123.0103 | 0.53101 | 0.61798 | -0.11902 | -0.10986 | -0.1831 | -0.032043 | 3.1769 | -0.19226 | -0.009155 | -0.10986 | 122.8775 | 122.8317 | 76.1536 | -123.0377 | 122.9187 | 122.8409 | 71.1227 | -123.1338
1375.5156 | 123.111 | -58.754 | 64.2059 | -0.12512 | 0.022285 | 0.068227 | 0.073704 | 0.13404 | 0.0070346 | 0.00020288 | -0.11879 | -0.00091437 | 0.0006772 | 0.0030954 | 0.0019824 | -0.0038879 | 64.0549 | 64.1876 | 17.2852 | -58.2275 | 64.2288 | -58.7585 | -58.8318 | -55.5313 | 12.5107 | -58.9645 | 64.2426 | 64.1464 | -58.8364 | -58.9508 | -0.004578 | -0.07782 | 0.022888 | 122.9416 | 0.52643 | 0.60425 | -0.15106 | -0.082398 | -0.19684 | 0.036621 | 3.2227 | -0.21057 | -0.013733 | -0.05951 | 122.9828 | 122.8088 | 76.0391 | -123.0377 | 122.9965 | 122.9004 | 71.2646 | -123.1567
1376.5156 | 123.175 | -58.699 | 64.1464 | -0.1709 | 0.015236 | 0.070577 | 0.072209 | 0.13126 | -0.00022865 | 0.00041648 | 0.026169 | -0.004546 | -0.0023136 | -0.0003226 | 0.001128 | -0.0034607 | 64.1006 | 64.357 | 17.3859 | -58.1635 | 64.1281 | -58.7448 | -58.8089 | -55.3482 | 12.7945 | -58.8272 | 64.151 | 64.1464 | -58.7723 | -58.8867 | -0.045776 | -0.10986 | -0.01831 | 123.056 | 0.53558 | 0.64545 | -0.045776 | -0.073242 | -0.18768 | 0.004578 | 3.3508 | -0.12817 | 0.05951 | 0 | 122.8271 | 122.7997 | 76.0849 | -122.9553 | 122.85 | 122.8455 | 71.4935 | -123.0331
1377.5156 | 123.0652 | -58.754 | 64.1876 | -0.52948 | 0.019081 | 0.068013 | 0.074772 | 0.13426 | 0.0044712 | 0.00041648 | -0.088272 | -5.9768e-05 | 0.0006772 | 0.0024546 | 0.0019824 | -0.0043153 | 64.0137 | 64.1876 | 17.1661 | -58.2458 | 64.2151 | -58.7997 | -58.8684 | -55.4443 | 12.8769 | -59.0012 | 64.2426 | 64.1327 | -58.8226 | -58.9554 | -0.045777 | -0.11444 | 0.027466 | 122.9416 | 0.50812 | 0.62256 | -0.17395 | -0.068665 | -0.20142 | 0.054932 | 3.3096 | -0.24719 | -0.045777 | -0.054932 | 122.9691 | 122.7676 | 75.9201 | -123.056 | 122.9965 | 122.8867 | 71.6309 | -123.143
1378.5156 | 123.1705 | -58.7036 | 64.151 | -0.071716 | 0.015236 | 0.071004 | 0.071354 | 0.12849 | -0.001083 | 0.00084388 | 0.033798 | -0.002837 | -0.0010318 | 0.0018136 | -0.00079463 | -0.0066651 | 64.1281 | 64.3478 | 17.244 | -58.1451 | 64.1693 | -58.7265 | -58.7906 | -55.1239 | 13.0966 | -59.0424 | 64.1693 | 64.0411 | -58.7997 | -58.9325 | -0.022888 | -0.086975 | 0.018311 | 123.0515 | 0.55847 | 0.64545 | -0.022888 | -0.096131 | -0.22888 | 0.018311 | 3.5797 | -0.33875 | -0.10986 | -0.10986 | 122.8729 | 122.8317 | 75.9476 | -122.9416 | 122.8729 | 122.7448 | 71.8002 | -123.0835
1379.5156 | 123.0606 | -58.7631 | 64.2059 | -0.086975 | 0.019508 | 0.071858 | 0.072209 | 0.12956 | 0.0063938 | -0.0010787 | -0.11879 | -5.9768e-05 | -0.0012454 | 0.0009592 | 0.0024096 | -0.0047425 | 64.0457 | 64.1922 | 17.038 | -58.2184 | 64.2151 | -58.7997 | -58.8364 | -55.3528 | 13.2431 | -58.9828 | 64.2334 | 64.1464 | -58.8455 | -58.9462 | -0.036621 | -0.073242 | 0.009155 | 122.9553 | 0.54474 | 0.61798 | -0.16022 | -0.082397 | -0.1831 | 0.027465 | 3.4103 | -0.21973 | -0.036621 | -0.05951 | 122.9782 | 122.8088 | 75.8011 | -123.0423 | 122.9965 | 122.9095 | 72.0062 | -123.1522
1380.5156 | 123.1659 | -58.6807 | 64.1647 | -0.10986 | 0.015877 | 0.071218 | 0.072423 | 0.12956 | -1.505e-05 | 0.00041648 | -0.011978 | -0.0098866 | -0.0027408 | 0.0024546 | 0.004546 | -0.0036743 | 64.1327 | 64.3845 | 17.1799 | -58.1451 | 64.1785 | -58.7311 | -58.7723 | -55.22 | 13.6139 | -58.8913 | 64.1418 | 64.0961 | -58.8089 | -58.9005 | -0.050354 | -0.091553 | 0.013733 | 123.0652 | 0.53558 | 0.62714 | -0.032044 | -0.12817 | -0.21973 | -0.022888 | 3.4607 | -0.21057 | 0.009156 | -0.068665 | 122.8592 | 122.8134 | 75.8606 | -122.937 | 122.8226 | 122.7768 | 72.2946 | -123.0652
1381.5156 | 122.9828 | -58.7219 | 64.2288 | -0.19379 | 0.017586 | 0.06844 | 0.07285 | 0.13041 | 0.0048984 | -1.0724e-05 | -0.080643 | -0.0013416 | -0.001459 | 0.0013864 | 0.0024096 | -0.0049561 | 64.0457 | 64.2197 | 16.9739 | -58.2138 | 64.2059 | -58.7723 | -58.8272 | -55.2475 | 13.5727 | -58.9645 | 64.2288 | 64.1464 | -58.8043 | -58.9005 | -0.050354 | -0.10529 | -0.022888 | 122.9416 | 0.50812 | 0.6134 | -0.18311 | -0.082397 | -0.17853 | 0 | 3.4744 | -0.24262 | -0.064087 | -0.082398 | 122.9279 | 122.7676 | 75.6958 | -123.056 | 122.9507 | 122.8683 | 72.2946 | -123.1293
1382.5156 | 123.1293 | -58.7082 | 64.1647 | 0.065613 | 0.015663 | 0.069936 | 0.072209 | 0.13126 | -1.505e-05 | 0.00041648 | 0.1635 | -0.0032642 | 0.0006772 | 0.0020272 | 0.0034778 | -0.0038879 | 64.0411 | 64.2517 | 16.9601 | -58.1863 | 64.1418 | -58.7814 | -58.8455 | -55.1559 | 13.7604 | -58.9096 | 64.1464 | 64.0732 | -58.8364 | -58.9462 | -0.073242 | -0.13733 | -0.022888 | 122.9599 | 0.52185 | 0.65918 | -0.1236 | -0.12817 | -0.23804 | -0.018311 | 3.5522 | -0.20142 | 0.036621 | -0.091553 | 122.85 | 122.7493 | 75.6683 | -123.0103 | 122.8546 | 122.7814 | 72.4686 | -123.111
1383.5156 | 123.1842 | -58.7036 | 64.1876 | -0.02594 | 0.014381 | 0.072286 | 0.072209 | 0.13062 | 0.0029758 | 0.00020288 | 0.064316 | -0.002837 | -0.0006046 | 0.000532 | 0.0019824 | -0.0023927 | 64.1373 | 64.3387 | 16.9922 | -58.1223 | 64.1418 | -58.7494 | -58.7997 | -55.0461 | 13.9847 | -58.8455 | 64.1602 | 64.0915 | -58.8135 | -58.9233 | -0.045777 | -0.096131 | -0.045776 | 123.0423 | 0.58136 | 0.67749 | -0.050354 | -0.10986 | -0.21973 | -0.027466 | 3.6575 | -0.14191 | 0.07782 | -0.09613 | 122.8455 | 122.8409 | 75.6958 | -122.9874 | 122.8638 | 122.7951 | 72.6883 | -123.111
1384.5156 | 123.1842 | -58.7128 | 64.119 | -0.048828 | 0.014381 | 0.069722 | 0.070714 | 0.13126 | 0.0019078 | 0.00084388 | 0.079574 | -0.0051868 | -0.0042362 | 0.0022408 | 0.0017688 | -0.0053833 | 64.1098 | 64.3066 | 16.9327 | -58.1543 | 64.1464 | -58.7677 | -58.8226 | -55.0186 | 14.1769 | -58.8501 | 64.1418 | 64.0549 | -58.8272 | -58.905 | -0.054931 | -0.10986 | 0.027465 | 123.0194 | 0.55847 | 0.66833 | -0.009156 | -0.11444 | -0.19226 | 0.022888 | 3.6942 | -0.13733 | 0.054931 | -0.064087 | 122.8592 | 122.8226 | 75.6454 | -122.9416 | 122.8546 | 122.7676 | 72.8897 | -123.024
1385.5156 | 123.1155 | -58.7128 | 64.1281 | -0.33875 | 0.015022 | 0.070363 | 0.073491 | 0.12998 | 0.0046848 | -0.0010787 | -0.050125 | -0.002196 | 0.0006772 | 0.0018136 | 0.002837 | -0.0047425 | 64.119 | 64.3158 | 16.8961 | -58.1406 | 64.119 | -58.7906 | -58.8409 | -55.0003 | 14.2868 | -58.8913 | 64.151 | 64.0457 | -58.8501 | -58.9233 | -0.077819 | -0.12817 | -0.009155 | 123.0286 | 0.57221 | 0.70038 | -0.009155 | -0.13733 | -0.21057 | 0.022888 | 3.7125 | -0.17853 | 0.032044 | -0.082398 | 122.8317 | 122.8317 | 75.6088 | -122.9691 | 122.8638 | 122.7585 | 72.9996 | -123.0515
1386.5156 | 123.2025 | -58.7311 | 64.1602 | -0.071716 | 0.015022 | 0.072499 | 0.07285 | 0.13041 | 0.00083955 | 0.00063028 | -0.027237 | -0.0026234 | -0.0010318 | 0.0009592 | 0.0015552 | -0.0045289 | 64.1144 | 64.3295 | 16.8686 | -58.1223 | 64.151 | -58.7585 | -58.8226 | -54.9316 | 14.447 | -58.8593 | 64.1327 | 64.0457 | -58.8135 | -58.9188 | -0.027466 | -0.091553 | -0.009155 | 123.0606 | 0.60883 | 0.70038 | -0.045776 | -0.082398 | -0.18768 | -0.027466 | 3.7994 | -0.12817 | 0.059509 | -0.11444 | 122.8821 | 122.8455 | 75.5997 | -122.9828 | 122.8638 | 122.7768 | 73.1781 | -123.0789
1387.5156 | 123.1476 | -58.7128 | 64.1647 | -0.19379 | 0.014808 | 0.069509 | 0.073704 | 0.1302 | 0.0048984 | 0.0012711 | -0.057755 | -0.002196 | -0.0008182 | -0.0007498 | 0.0024096 | -0.0036743 | 64.1327 | 64.3066 | 16.864 | -58.1131 | 64.1464 | -58.7494 | -58.7997 | -54.895 | 14.6347 | -58.8776 | 64.1693 | 64.0274 | -58.8135 | -58.9188 | -0.036621 | -0.086975 | -0.018311 | 123.0194 | 0.59967 | 0.68665 | -0.032044 | -0.10071 | -0.20599 | 0.004578 | 3.8177 | -0.16479 | 0.041199 | -0.13733 | 122.8592 | 122.8455 | 75.5768 | -122.9645 | 122.8821 | 122.7402 | 73.3475 | -123.0835
1388.5156 | 123.1659 | -58.7173 | 64.1281 | 0.019836 | 0.014595 | 0.071858 | 0.069859 | 0.12934 | 0.0012668 | -0.0010787 | 0.026169 | -0.0026234 | -0.0029544 | 0.000532 | 0.00091437 | -0.0036743 | 64.0732 | 64.2563 | 16.7953 | -58.1451 | 64.151 | -58.7585 | -58.8547 | -54.8767 | 14.74 | -58.905 | 64.1052 | 64.0457 | -58.8501 | -58.9554 | -0.041199 | -0.13733 | 0.022888 | 122.9736 | 0.5722 | 0.70953 | -0.054932 | -0.13275 | -0.23804 | -0.022888 | 3.8406 | -0.18768 | 0.050354 | -0.082398 | 122.8683 | 122.7905 | 75.5127 | -122.9828 | 122.8226 | 122.7631 | 73.4573 | -123.0835
1389.5156 | 123.1659 | -58.7311 | 64.1235 | -0.10986 | 0.016731 | 0.069081 | 0.073063 | 0.13062 | 0.0042576 | 0.0010575 | -0.12642 | -0.00091437 | 0.00025 | 0.0013864 | 0.0024096 | -0.0047425 | 64.1785 | 64.5401 | 16.8549 | -58.3191 | 64.1418 | -58.7906 | -58.8455 | -54.8218 | 14.8499 | -58.8776 | 64.1052 | 64.0366 | -58.8455 | -58.9417 | -0.059509 | -0.11444 | 0.018311 | 123.2712 | 0.41199 | 0.52643 | 0.054932 | -0.11444 | -0.21057 | -0.01831 | 3.9093 | -0.14648 | 0.064087 | -0.086975 | 122.8729 | 122.9095 | 75.5859 | -122.9691 | 122.8363 | 122.7676 | 73.5809 | -123.0652
1390.5156 | 123.2437 | -58.7769 | 64.1281 | 0.12665 | 0.014168 | 0.068654 | 0.0705 | 0.13169 | 0.0046848 | 0.0010575 | 0.14061 | -0.0013416 | -0.0021 | 0.0020272 | 0.0032642 | -0.0043153 | 64.0274 | 64.2059 | 16.6901 | -58.1863 | 64.1373 | -58.7906 | -58.8547 | -54.8584 | 14.8727 | -58.9645 | 64.119 | 64.0228 | -58.8821 | -58.9737 | -0.013733 | -0.07782 | 0.009155 | 122.9828 | 0.59051 | 0.66833 | -0.10071 | -0.10529 | -0.19684 | -0.009155 | 3.9185 | -0.18768 | 0.009155 | -0.10529 | 122.9141 | 122.8043 | 75.4669 | -122.9828 | 122.8958 | 122.7997 | 73.6496 | -123.1018
1391.5156 | 123.1705 | -58.7448 | 64.1144 | 0.035095 | 0.016517 | 0.069295 | 0.074986 | 0.13041 | 0.0048984 | -0.0017197 | 0.033798 | -0.0015552 | -0.0010318 | 0.0013864 | 0.0024096 | -0.0041017 | 64.0732 | 64.238 | 16.6397 | -58.1268 | 64.1281 | -58.8318 | -58.8547 | -54.7668 | 15.0055 | -58.9142 | 64.1144 | 64.032 | -58.8318 | -58.9417 | -0.086975 | -0.10986 | 0.013733 | 122.9828 | 0.61798 | 0.72784 | -0.041199 | -0.086975 | -0.19684 | 0 | 3.978 | -0.16937 | 0.027465 | -0.082398 | 122.8729 | 122.818 | 75.3845 | -122.9691 | 122.8592 | 122.7768 | 73.7503 | -123.056
1392.5156 | 123.111 | -58.7585 | 64.0915 | 0.10376 | 0.012672 | 0.069722 | 0.071141 | 0.12892 | 0.0046848 | 0.0014847 | 0.17113 | -0.002196 | 0.0006772 | 0.0018136 | 0.004546 | -0.0043153 | 64.0549 | 64.2151 | 16.6031 | -58.1772 | 64.119 | -58.8043 | -58.8593 | -54.895 | 15.0238 | -58.9966 | 64.1373 | 64.0411 | -58.8821 | -58.96 | -0.045776 | -0.10071 | 0.027466 | 122.9736 | 0.58136 | 0.68207 | -0.036621 | -0.1236 | -0.20142 | 0.045776 | 3.8635 | -0.23804 | -0.036621 | -0.050354 | 122.8775 | 122.8134 | 75.3616 | -122.9507 | 122.8958 | 122.7997 | 73.7823 | -123.0515
1393.5156 | 123.175 | -58.754 | 64.0915 | -0.041199 | 0.016731 | 0.070577 | 0.071782 | 0.13105 | 0.004044 | 0.00084388 | -0.080643 | -0.0017688 | -0.0029544 | -0.0005362 | 0.0013416 | -0.01051 | 64.1281 | 64.2838 | 16.6534 | -58.1223 | 64.1006 | -58.786 | -58.8684 | -54.6844 | 15.6006 | -59.0607 | 64.151 | 64.0411 | -58.8684 | -58.9737 | -0.032044 | -0.11444 | 0.009155 | 123.0377 | 0.63171 | 0.74616 | 0.036621 | -0.11444 | -0.21973 | 0.059509 | 4.0695 | -0.3067 | -0.086975 | -0.050354 | 122.8546 | 122.8821 | 75.4074 | -122.9599 | 122.905 | 122.7951 | 74.3546 | -123.0652
1394.5156 | 123.1064 | -58.7402 | 64.0961 | 0.050354 | 0.013527 | 0.069936 | 0.071354 | 0.13361 | 0.0053256 | -0.00022432 | 0.25505 | 0.0014356 | 3.6404e-05 | 0.0018136 | 0.0024096 | -0.0055969 | 64.2105 | 64.0869 | 16.4658 | -58.1177 | 64.119 | -58.7906 | -58.8501 | -54.7073 | 15.1566 | -58.9508 | 64.1373 | 64.0366 | -58.8593 | -58.9737 | -0.050354 | -0.10986 | 0.022889 | 122.8271 | 0.62256 | 0.73242 | 0.11444 | -0.11902 | -0.23346 | 0.041199 | 4.0329 | -0.21057 | 0.022888 | -0.059509 | 122.8592 | 122.9507 | 75.206 | -122.9462 | 122.8775 | 122.7768 | 73.8968 | -123.0698
1395.5156 | 123.1888 | -58.7494 | 64.0961 | -0.02594 | 0.015663 | 0.068013 | 0.072636 | 0.13126 | 0.0021214 | 0.0029801 | -0.011978 | -0.00027337 | -0.0008182 | 0.0020272 | 0.0019824 | -0.0043153 | 64.1052 | 64.2609 | 16.571 | -58.1131 | 64.1281 | -58.8043 | -58.873 | -54.5975 | 15.2893 | -58.873 | 64.119 | 64.0228 | -58.8593 | -58.9645 | -0.054931 | -0.1236 | 0.032044 | 123.0103 | 0.63629 | 0.75989 | 0.009156 | -0.10986 | -0.21515 | 0.022889 | 4.1519 | -0.1236 | 0.091553 | -0.073242 | 122.8775 | 122.8546 | 75.3204 | -122.9691 | 122.8683 | 122.7722 | 74.0387 | -123.0606
1396.5156 | 123.1018 | -58.7814 | 64.0778 | 0.20294 | 0.016945 | 0.070149 | 0.070286 | 0.13212 | 0.0053256 | 0.0025529 | 0.24742 | -0.00027337 | -0.0029544 | 0.003309 | 0.0049732 | -0.0051697 | 64.0778 | 64.2242 | 16.5298 | -58.1497 | 64.064 | -58.8043 | -58.8821 | -54.6249 | 15.2161 | -58.9783 | 64.0915 | 63.9679 | -58.9096 | -59.0057 | -0.022888 | -0.10071 | -0.013733 | 123.0057 | 0.63171 | 0.73242 | 0 | -0.12817 | -0.2243 | 0.013733 | 4.1565 | -0.19684 | 0.027466 | -0.10986 | 122.8455 | 122.8592 | 75.3113 | -122.9599 | 122.8729 | 122.7493 | 73.9975 | -123.0835
1397.5156 | 123.1384 | -58.7585 | 64.0823 | 0.027466 | 0.015022 | 0.069081 | 0.071568 | 0.13105 | 0.0031894 | 0.0016983 | 0.049057 | -5.9768e-05 | -0.0012454 | 0.0026682 | 0.0030506 | -0.0036743 | 64.0686 | 64.2288 | 16.5161 | -58.1223 | 64.1144 | -58.8089 | -58.8684 | -54.5563 | 15.3122 | -58.9005 | 64.1327 | 64.0228 | -58.8776 | -58.9508 | -0.050354 | -0.10986 | 0.032044 | 122.9874 | 0.63629 | 0.74616 | -0.013732 | -0.11902 | -0.19226 | 0.050354 | 4.2023 | -0.14191 | 0.050354 | -0.059509 | 122.8729 | 122.8271 | 75.2747 | -122.9507 | 122.8912 | 122.7814 | 74.0707 | -123.0331
1398.5156 | 123.2071 | -58.7448 | 64.0915 | -0.056458 | 0.013527 | 0.071431 | 0.071568 | 0.13062 | 0.0046848 | 0.00020288 | 0.056686 | -0.00048697 | -0.0046634 | 0.0011728 | 0.0036914 | -0.0049561 | 64.0778 | 64.2517 | 16.5665 | -58.0948 | 64.1144 | -58.8089 | -58.8684 | -54.5013 | 15.3168 | -58.9005 | 64.1006 | 63.9908 | -58.8867 | -58.9691 | -0.064087 | -0.1236 | 0.022888 | 122.9965 | 0.65002 | 0.77362 | -0.013733 | -0.14191 | -0.2243 | 0.009155 | 4.2435 | -0.15564 | 0.068664 | -0.10071 | 122.8592 | 122.8226 | 75.3113 | -122.9599 | 122.8455 | 122.7356 | 74.0616 | -123.0606
1399.5156 | 123.1476 | -58.8272 | 64.064 | 0.035095 | 0.016517 | 0.07079 | 0.072209 | 0.13319 | 0.0038304 | 0.0023391 | 0.11009 | -0.00091437 | -0.0027408 | 0.0007456 | 0.0047596 | -0.0055969 | 63.9908 | 64.1602 | 16.4703 | -58.1818 | 64.0686 | -58.8684 | -58.9142 | -54.5837 | 15.2435 | -59.0057 | 64.0778 | 63.9633 | -58.9325 | -59.0286 | -0.041199 | -0.086976 | 0.004578 | 122.9874 | 0.64545 | 0.73242 | -0.073242 | -0.10529 | -0.20142 | 0.013733 | 4.2435 | -0.17853 | 0.022888 | -0.10071 | 122.8958 | 122.818 | 75.2975 | -122.9782 | 122.905 | 122.7905 | 74.0707 | -123.0927
1400.5156 | 123.0972 | -58.8455 | 64.0366 | 0.20294 | 0.018226 | 0.069936 | 0.074345 | 0.12998 | 0.005112 | 0.0019119 | 0.1635 | -0.0017688 | 3.6404e-05 | 0.0020272 | 0.0032642 | -0.0013245 | 63.9771 | 64.1281 | 16.4291 | -58.1955 | 64.0182 | -58.8867 | -58.9142 | -54.57 | 15.271 | -59.0195 | 64.064 | 63.9267 | -58.96 | -59.0561 | -0.041199 | -0.068665 | -0.01831 | 122.9736 | 0.65002 | 0.71869 | -0.059509 | -0.11444 | -0.21057 | 0.027466 | 4.2755 | -0.17395 | 0.036621 | -0.10986 | 122.8638 | 122.8226 | 75.2747 | -122.9507 | 122.9095 | 122.7722 | 74.1165 | -123.0927
1401.5156 | 123.1293 | -58.8272 | 64.0411 | 0.057983 | 0.015877 | 0.070363 | 0.071141 | 0.13062 | 0.004044 | 0.00041648 | 0.056686 | 0.0010082 | -0.0035952 | 0.0018136 | 0.002196 | -0.0045289 | 63.9908 | 64.1602 | 16.4108 | -58.1589 | 64.0457 | -58.8501 | -58.9279 | -54.5013 | 15.3214 | -58.9691 | 64.064 | 63.9633 | -58.9279 | -59.0195 | -0.022889 | -0.10071 | 0.004577 | 122.9874 | 0.66833 | 0.76904 | -0.050354 | -0.10071 | -0.19226 | 0.022888 | 4.3259 | -0.14191 | 0.050354 | -0.07782 | 122.8729 | 122.818 | 75.238 | -122.9691 | 122.8912 | 122.7905 | 74.1486 | -123.0606
1402.5156 | 123.111 | -58.8455 | 64.0457 | -0.056458 | 0.02314 | 0.068654 | 0.0752 | 0.13297 | 0.0098118 | 0.0029801 | 0.27031 | 0.00079463 | 0.001959 | 0.0001046 | 0.0066822 | -0.0073059 | 64.0503 | 63.9542 | 16.2506 | -58.1268 | 64.0594 | -58.9188 | -58.9737 | -54.4556 | 15.3809 | -59.0744 | 64.1052 | 63.9633 | -58.9554 | -59.0561 | -0.073242 | -0.12817 | 0.013733 | 122.7997 | 0.71869 | 0.84686 | 0.004578 | -0.10986 | -0.21057 | 0.05951 | 4.39 | -0.22888 | -0.018311 | -0.082397 | 122.905 | 122.8958 | 75.0961 | -123.0194 | 122.9507 | 122.8088 | 74.2264 | -123.1018
1403.5156 | 123.1247 | -58.8272 | 64.0366 | 0.13428 | 0.015663 | 0.068868 | 0.072209 | 0.12892 | 0.0012668 | 0.0012711 | 0.11009 | 0.00058103 | -0.0010318 | 0.0016 | 0.002196 | -0.0030335 | 63.9542 | 64.1235 | 16.3559 | -58.1451 | 64.0594 | -58.873 | -58.9371 | -54.4464 | 15.4495 | -59.024 | 64.0457 | 63.9725 | -58.9417 | -59.0424 | -0.045777 | -0.10986 | 0.022888 | 122.9507 | 0.68207 | 0.79193 | -0.082397 | -0.11444 | -0.21515 | 0.009155 | 4.3808 | -0.19684 | 0.01831 | -0.064087 | 122.8867 | 122.7814 | 75.1831 | -122.9736 | 122.8729 | 122.7997 | 74.2767 | -123.0789
1404.5156 | 123.175 | -58.8272 | 64.0091 | 0.18768 | 0.020363 | 0.069936 | 0.073277 | 0.13212 | 0.0083164 | 0.0025529 | 0.43053 | -0.00091437 | -0.0012454 | 0.0011728 | 0.0041186 | -0.0058105 | 64.0091 | 64.1556 | 16.4795 | -58.2687 | 63.9954 | -58.9325 | -58.96 | -54.3549 | 15.5045 | -59.0149 | 64.0182 | 63.913 | -58.96 | -59.0469 | -0.10529 | -0.13275 | -0.013733 | 122.9828 | 0.55847 | 0.69122 | 0 | -0.13275 | -0.21973 | 0.009156 | 4.4724 | -0.18768 | 0.032043 | -0.09613 | 122.8226 | 122.8363 | 75.3067 | -122.9691 | 122.8455 | 122.7402 | 74.3317 | -123.056
1405.5156 | 123.1476 | -58.8135 | 64.0503 | 0.088501 | 0.018867 | 0.070577 | 0.071995 | 0.13126 | 0.0029758 | -0.00022432 | 0.46104 | -0.001128 | 3.6404e-05 | 0.0022408 | 0.0032642 | -0.0030335 | 63.9633 | 64.1281 | 16.3605 | -58.0124 | 64.0869 | -58.8455 | -58.8913 | -54.3915 | 15.5045 | -59.0057 | 64.064 | 63.9862 | -58.9371 | -59.0424 | -0.032043 | -0.077819 | 0.036621 | 122.9416 | 0.80109 | 0.87891 | -0.086975 | -0.1236 | -0.22888 | 0.013733 | 4.422 | -0.19226 | 0.036621 | -0.064087 | 122.9004 | 122.7768 | 75.174 | -122.9416 | 122.8775 | 122.7997 | 74.3179 | -123.0927
1406.5156 | 123.1567 | -58.8409 | 64.0137 | 0.17242 | 0.022285 | 0.066731 | 0.073918 | 0.13062 | 0.0061802 | 0.0016983 | 0.27031 | -5.9768e-05 | -0.0012454 | 0.0016 | 0.0054004 | -0.0043153 | 64.0182 | 64.1602 | 16.3651 | -58.1085 | 64.0182 | -58.8684 | -58.9554 | -54.2999 | 15.564 | -58.992 | 64.0182 | 63.913 | -58.9508 | -59.0515 | -0.027466 | -0.11444 | 0.004578 | 123.0011 | 0.73242 | 0.84686 | 0.004578 | -0.10986 | -0.21057 | 0.004578 | 4.541 | -0.15106 | 0.05951 | -0.10071 | 122.8592 | 122.8592 | 75.206 | -122.9691 | 122.8592 | 122.7539 | 74.4049 | -123.0652
1407.5156 | 123.0286 | -58.8318 | 64.1006 | -0.18616 | 0.019935 | 0.069295 | 0.074772 | 0.12998 | 0.006821 | -0.0017197 | -0.36293 | 0.00036743 | 0.0004636 | 0.003309 | 0.0036914 | -0.0019653 | 64.238 | 64.0091 | 16.2003 | -58.2321 | 64.1281 | -58.873 | -58.9417 | -54.3228 | 15.5136 | -59.0607 | 64.1281 | 64.0045 | -58.96 | -59.0332 | -0.041199 | -0.10986 | 0.027466 | 122.8409 | 0.59967 | 0.70953 | 0.13733 | -0.12817 | -0.20142 | 0.027466 | 4.509 | -0.22888 | -0.027466 | -0.09613 | 122.9599 | 123.0698 | 75.032 | -123.0423 | 122.9599 | 122.8363 | 74.3454 | -123.1338
1408.5156 | 123.143 | -58.8181 | 64.0366 | 0.18005 | 0.017372 | 0.069509 | 0.07285 | 0.13084 | 0.0042576 | 0.0010575 | 0.26268 | 0.0018628 | 0.0004636 | -0.000109 | 0.0049732 | -0.0032471 | 64.0182 | 64.183 | 16.3239 | -58.0948 | 64.0503 | -58.8409 | -58.9279 | -54.2221 | 15.5823 | -58.9783 | 64.0503 | 63.945 | -58.9325 | -59.0607 | -0.022888 | -0.10986 | 0.013733 | 123.0011 | 0.72327 | 0.83313 | -0.01831 | -0.11444 | -0.24262 | 0.013733 | 4.5959 | -0.16022 | 0.082398 | -0.091553 | 122.8683 | 122.8363 | 75.1419 | -122.9645 | 122.8683 | 122.7631 | 74.4003 | -123.0972
1409.5156 | 123.1247 | -58.8364 | 64.0045 | 1.0193 | 0.015877 | 0.072499 | 0.068577 | 0.12977 | 0.0031894 | -0.00022432 | 0.094833 | 0.00036743 | -0.003168 | 0.0007456 | 0.0036914 | -0.0030335 | 63.9359 | 64.1052 | 16.2323 | -58.1039 | 64.0274 | -58.8684 | -58.9233 | -54.245 | 15.564 | -59.0012 | 64.064 | 63.945 | -58.96 | -59.079 | -0.032043 | -0.086975 | 0.022888 | 122.9416 | 0.73242 | 0.8194 | -0.068665 | -0.1236 | -0.24261 | 0.059509 | 4.5914 | -0.16479 | 0.077819 | -0.05951 | 122.8638 | 122.7722 | 75.0687 | -122.9279 | 122.9004 | 122.7814 | 74.4003 | -123.0835
1410.5156 | 123.1522 | -58.8043 | 64.0457 | 0.18768 | 0.020576 | 0.068868 | 0.073277 | 0.13233 | 0.0081028 | 0.0012711 | 0.50682 | 0.0025036 | -0.0010318 | 0.0007456 | 0.0058276 | -0.0068787 | 64.0503 | 64.1785 | 16.333 | -58.049 | 64.0182 | -58.905 | -58.9417 | -54.1489 | 15.715 | -58.9554 | 64.0503 | 63.9496 | -58.9462 | -59.0195 | -0.10071 | -0.13733 | -0.027465 | 122.9828 | 0.75531 | 0.89264 | 0.004578 | -0.14191 | -0.21515 | 0.004578 | 4.6555 | -0.15106 | 0.064087 | -0.09613 | 122.8226 | 122.8546 | 75.1373 | -122.9874 | 122.8546 | 122.7539 | 74.5193 | -123.0652
1411.5156 | 123.1384 | -58.8135 | 64.0503 | 0.12665 | 0.015877 | 0.071645 | 0.071568 | 0.13084 | 0.0044712 | 0.0012711 | 0.36186 | 0.0010082 | 0.0004636 | 0.0013864 | 0.002196 | -0.0047425 | 64.0915 | 64.2609 | 16.333 | -58.1772 | 64.0732 | -58.8501 | -58.9096 | -54.158 | 15.6372 | -58.9783 | 64.0961 | 64.0091 | -58.9279 | -59.0561 | -0.036621 | -0.09613 | 0.022888 | 123.0743 | 0.63629 | 0.73242 | 0.041199 | -0.11444 | -0.24261 | 0.045776 | 4.6555 | -0.16479 | 0.07782 | -0.041199 | 122.8867 | 122.905 | 75.1465 | -122.9599 | 122.9095 | 122.8226 | 74.4507 | -123.1064
1412.5156 | 123.2025 | -58.7769 | 64.0686 | -0.15564 | 0.018226 | 0.067586 | 0.073491 | 0.12913 | 0.0025486 | 0.0010575 | 0.2169 | 0.00015383 | -0.0008182 | 0.0018136 | 0.0041186 | -0.0053833 | 64.1006 | 64.0274 | 16.2598 | -57.9712 | 64.0869 | -58.8135 | -58.8867 | -54.039 | 15.7837 | -58.9005 | 64.0823 | 63.9999 | -58.8867 | -58.9737 | -0.036622 | -0.10986 | 0.01831 | 122.8043 | 0.80566 | 0.91553 | 0.032043 | -0.10986 | -0.19684 | 0.013732 | 4.7379 | -0.1236 | 0.073242 | -0.068665 | 122.8638 | 122.8775 | 75.0366 | -122.9553 | 122.8592 | 122.7768 | 74.5605 | -123.0423
1413.5156 | 123.0972 | -58.7494 | 64.1098 | 0.12665 | 0.016304 | 0.07079 | 0.071568 | 0.13084 | 0.0019078 | 0.0019119 | 0.13298 | -0.0019824 | -0.0027408 | -0.0013906 | 0.0047596 | -0.0013245 | 64.0503 | 64.2014 | 16.2643 | -57.9895 | 64.119 | -58.7814 | -58.8272 | -54.1534 | 15.7654 | -58.9554 | 64.1144 | 64.0411 | -58.8913 | -58.9645 | -0.032043 | -0.077819 | 0.009156 | 122.9507 | 0.75989 | 0.83771 | -0.059509 | -0.14191 | -0.21515 | 0.004578 | 4.5959 | -0.20599 | 0.009156 | -0.068664 | 122.8683 | 122.7997 | 75.0137 | -122.937 | 122.8638 | 122.7905 | 74.5148 | -123.0743
1414.5156 | 123.1155 | -58.7631 | 64.0915 | 0.057983 | 0.014808 | 0.069081 | 0.0752 | 0.12614 | 0.003403 | 0.0023391 | 0.14824 | 0.00015383 | -0.0001774 | 0.0013864 | 0.002837 | -0.0032471 | 64.0457 | 64.1876 | 16.2369 | -58.0124 | 64.1006 | -58.7769 | -58.8638 | -54.007 | 15.683 | -58.7814 | 64.1556 | 64.0594 | -58.8867 | -58.9737 | -0.013732 | -0.10071 | 0.009155 | 122.9507 | 0.75073 | 0.85144 | -0.045777 | -0.1236 | -0.21057 | 0.064087 | 4.7562 | -0.01831 | 0.19226 | -0.032044 | 122.8638 | 122.8088 | 75 | -122.9553 | 122.9187 | 122.8226 | 74.4461 | -123.0652
1415.5156 | 123.1659 | -58.7402 | 64.1144 | 0.0045777 | 0.018226 | 0.072927 | 0.072209 | 0.13212 | 0.004044 | 0.0029801 | 0.079574 | 0.0010082 | -0.0021 | 0.000532 | 0.0047596 | -0.0049561 | 64.1006 | 64.2517 | 16.2506 | -57.962 | 64.1098 | -58.7906 | -58.8455 | -53.9154 | 15.7837 | -58.8638 | 64.151 | 64.0457 | -58.8821 | -58.9508 | -0.050354 | -0.10529 | -0.004578 | 122.9919 | 0.7782 | 0.88348 | -0.013733 | -0.14191 | -0.21057 | 0.036621 | 4.8248 | -0.1236 | 0.086975 | -0.068665 | 122.85 | 122.8409 | 74.9908 | -122.9599 | 122.8912 | 122.7859 | 74.5239 | -123.0652
1416.5156 | 123.111 | -58.754 | 64.0961 | 0.19531 | 0.014808 | 0.072499 | 0.073063 | 0.1287 | 0.0048984 | 0.0044755 | 0.17113 | -0.00091437 | -0.0016726 | 0.0028818 | 0.0049732 | -0.0055969 | 64.0549 | 64.1968 | 16.2048 | -58.017 | 64.1006 | -58.8043 | -58.8455 | -53.9337 | 15.6921 | -58.9508 | 64.1327 | 64.0457 | -58.8821 | -58.9828 | -0.050354 | -0.091553 | 0.004578 | 122.9507 | 0.737 | 0.82855 | -0.041198 | -0.12817 | -0.22888 | 0.036621 | 4.8203 | -0.19684 | 0.032043 | -0.050354 | 122.8546 | 122.8088 | 74.9588 | -122.9416 | 122.8867 | 122.7997 | 74.4461 | -123.0789
1417.5156 | 123.0835 | -58.7585 | 64.1602 | -0.10986 | 0.024208 | 0.068227 | 0.073491 | 0.12998 | 0.012375 | 0.0021255 | -0.057755 | 0.0029308 | 0.0008908 | 0.0018136 | 0.0060412 | -0.0066651 | 64.1098 | 64.1876 | 16.246 | -57.9758 | 64.1922 | -58.7769 | -58.8501 | -53.8879 | 15.7379 | -58.9554 | 64.1556 | 64.0732 | -58.905 | -59.0012 | -0.01831 | -0.091553 | 0.032044 | 122.9462 | 0.78278 | 0.87433 | -0.050354 | -0.14648 | -0.24262 | -0.004577 | 4.8706 | -0.19684 | 0.045777 | -0.086975 | 122.9507 | 122.8683 | 75.0046 | -123.0103 | 122.9141 | 122.8317 | 74.4965 | -123.1613
1418.5156 | 123.1476 | -58.7357 | 64.1052 | 0.18768 | 0.021644 | 0.068654 | 0.071141 | 0.12763 | 0.005753 | 0.0042619 | 0.24742 | -0.00027337 | -0.0006046 | 0.0039498 | 0.0041186 | -0.0055969 | 64.0915 | 64.2517 | 16.301 | -57.9483 | 64.0961 | -58.7952 | -58.8455 | -53.8101 | 15.7837 | -58.8821 | 64.1098 | 64.0137 | -58.8821 | -58.96 | -0.059509 | -0.10986 | -0.009156 | 122.9874 | 0.78735 | 0.89722 | -0.013733 | -0.14648 | -0.2243 | 0.004577 | 4.9255 | -0.14648 | 0.07782 | -0.091553 | 122.8317 | 122.8271 | 75.0366 | -122.9507 | 122.8455 | 122.7493 | 74.5193 | -123.0652
1419.5156 | 123.0927 | -58.7311 | 64.0961 | 0.10376 | 0.020363 | 0.071645 | 0.071782 | 0.13169 | 0.0038304 | 0.0027665 | -0.31715 | -0.0019824 | -0.0016726 | 0.0035226 | 0.003905 | -0.0036743 | 64.0594 | 64.2334 | 16.2872 | -57.9666 | 64.1418 | -58.786 | -58.8684 | -53.8193 | 15.7104 | -58.9142 | 64.1327 | 64.032 | -58.8593 | -58.9737 | -0.054932 | -0.13733 | 0.045777 | 122.9645 | 0.76447 | 0.90179 | -0.036621 | -0.12817 | -0.24262 | 0.036621 | 4.9118 | -0.18311 | 0.059509 | -0.064087 | 122.8729 | 122.7905 | 75.0183 | -122.9645 | 122.8638 | 122.7631 | 74.4415 | -123.0698
1420.5156 | 123.1705 | -58.7402 | 64.119 | 0.37842 | 0.020149 | 0.071431 | 0.074986 | 0.13041 | 0.0072482 | 0.0025529 | 0.23979 | 0.0014356 | -0.0010318 | 0.0016 | 0.0051868 | -0.0058105 | 64.1647 | 64.2563 | 16.3422 | -57.9208 | 64.1144 | -58.7814 | -58.8135 | -53.746 | 15.8432 | -58.873 | 64.1235 | 64.0457 | -58.8501 | -58.9554 | -0.041199 | -0.073243 | -0.004578 | 122.9965 | 0.8194 | 0.89264 | 0.045776 | -0.10986 | -0.21515 | 0.004577 | 4.9942 | -0.13275 | 0.082397 | -0.073243 | 122.8546 | 122.905 | 75.0824 | -122.9324 | 122.8638 | 122.7859 | 74.5834 | -123.0743
1421.5156 | 123.1476 | -58.7311 | 64.1281 | 0.24109 | 0.018226 | 0.071004 | 0.074131 | 0.12956 | 0.005112 | 0.0027665 | 0.12535 | -5.9768e-05 | -0.0008182 | 0.0018136 | 0.0024096 | -0.0032471 | 64.0594 | 64.2288 | 16.3284 | -57.9346 | 64.1098 | -58.7494 | -58.8501 | -53.7506 | 15.8066 | -58.905 | 64.151 | 64.0274 | -58.8409 | -58.9462 | -0.018311 | -0.11902 | -0.018311 | 122.9599 | 0.79651 | 0.91553 | -0.068665 | -0.10986 | -0.21515 | 0.022888 | 4.9805 | -0.17395 | 0.041199 | -0.10071 | 122.8409 | 122.7905 | 75.0595 | -122.9782 | 122.8821 | 122.7585 | 74.5377 | -123.0743
1422.5156 | 123.1293 | -58.7402 | 64.0915 | 0.22583 | 0.020363 | 0.069295 | 0.073491 | 0.13319 | 0.0061802 | 0.0029801 | 0.20927 | -0.00027337 | 0.0015316 | 0.0041634 | 0.0051868 | -0.0038879 | 64.1281 | 64.2471 | 16.4017 | -57.9163 | 64.0915 | -58.7906 | -58.8501 | -53.6819 | 15.834 | -58.9005 | 64.1098 | 64.032 | -58.8867 | -58.9554 | -0.050354 | -0.10986 | 0 | 122.9874 | 0.82397 | 0.93384 | 0.036621 | -0.14648 | -0.21515 | 0.01831 | 5.0583 | -0.16022 | 0.054931 | -0.05951 | 122.8317 | 122.8683 | 75.1419 | -122.9416 | 122.85 | 122.7722 | 74.5743 | -123.0469
1423.5156 | 123.143 | -58.7723 | 64.1052 | 0.042725 | 0.016945 | 0.071004 | 0.072636 | 0.12956 | 0.004044 | 0.0021255 | 0.40764 | 0.00079463 | -0.000391 | 0.0011728 | 0.002837 | -0.0041017 | 64.0274 | 64.1876 | 16.3788 | -57.8476 | 64.1373 | -58.7677 | -58.8364 | -53.7369 | 15.7837 | -58.9417 | 64.1281 | 64.0045 | -58.8913 | -58.9737 | 0.004578 | -0.064087 | 0.032043 | 122.9599 | 0.92468 | 0.98877 | -0.07782 | -0.11902 | -0.20142 | 0.022888 | 5.0354 | -0.16937 | 0.032044 | -0.10071 | 122.9095 | 122.7997 | 75.1511 | -122.9416 | 122.9004 | 122.7768 | 74.556 | -123.0789
1424.5156 | 123.1842 | -58.7723 | 64.0411 | 0.19531 | 0.021644 | 0.069509 | 0.073704 | 0.13148 | 0.010025 | 0.0034073 | 0.22453 | 0.0020764 | 3.6404e-05 | 0.0018136 | 0.007323 | -0.0064515 | 64.0915 | 64.183 | 16.3605 | -57.93 | 64.0686 | -58.8318 | -58.8913 | -53.6591 | 15.7791 | -58.9279 | 64.1052 | 63.945 | -58.96 | -59.0424 | -0.059509 | -0.11902 | 0.027466 | 122.9553 | 0.84228 | 0.9613 | 0.050354 | -0.18768 | -0.27008 | 0.064087 | 5.1132 | -0.15564 | 0.11444 | -0.096131 | 122.8409 | 122.8638 | 75.1328 | -122.9324 | 122.8775 | 122.7173 | 74.5514 | -123.0835
1425.5156 | 123.1338 | -58.7769 | 64.0594 | 0.19531 | 0.020363 | 0.070577 | 0.0705 | 0.1302 | 0.005753 | 0.0031937 | 0.27031 | 0.00058103 | -0.0010318 | 0.0011728 | 0.003905 | -0.0032471 | 64.0732 | 64.1922 | 16.3422 | -57.9437 | 64.0869 | -58.8364 | -58.8821 | -53.6362 | 15.7654 | -58.9508 | 64.064 | 64.0045 | -58.8638 | -58.9966 | -0.05951 | -0.10529 | 0.027466 | 122.9691 | 0.83313 | 0.93841 | 0.013733 | -0.086976 | -0.21973 | 0.004578 | 5.1407 | -0.17395 | 0.045776 | -0.054931 | 122.8638 | 122.85 | 75.119 | -122.9416 | 122.8409 | 122.7814 | 74.5422 | -123.056
1426.5156 | 123.1705 | -58.7585 | 64.0686 | 0.20294 | 0.02079 | 0.068013 | 0.074345 | 0.13554 | 0.01088 | 0.0016983 | 0.15587 | 0.0014356 | -0.0008182 | 0.0003182 | 0.0051868 | -0.0041017 | 64.1098 | 64.3707 | 16.4886 | -57.9208 | 64.0823 | -58.8089 | -58.8272 | -53.5538 | 15.8112 | -58.905 | 64.1098 | 64.0182 | -58.8684 | -58.96 | -0.050354 | -0.068664 | 0.013732 | 123.1293 | 0.83771 | 0.90637 | 0.041198 | -0.10986 | -0.20142 | 0.041198 | 5.2048 | -0.14648 | 0.054932 | -0.050354 | 122.8409 | 122.8683 | 75.2472 | -122.8958 | 122.8683 | 122.7768 | 74.5697 | -123.0286
1427.5156 | 123.1476 | -58.7402 | 64.1418 | 0.18768 | 0.016731 | 0.069509 | 0.072209 | 0.13191 | 0.0031894 | 0.0031937 | 0.22453 | 0.00058103 | 0.001959 | 0.0028818 | 0.0030506 | -0.0049561 | 64.0823 | 64.2197 | 16.3925 | -57.9071 | 64.0869 | -58.7769 | -58.8409 | -53.5538 | 15.7425 | -58.9325 | 64.1373 | 64.0594 | -58.8547 | -58.9737 | -0.036621 | -0.10071 | -0.054932 | 122.9599 | 0.83313 | 0.93384 | -0.05951 | -0.11444 | -0.23346 | -0.004578 | 5.1865 | -0.19226 | 0.041199 | -0.082398 | 122.8271 | 122.8226 | 75.1328 | -122.9828 | 122.8775 | 122.7997 | 74.4827 | -123.1155
1428.5156 | 123.143 | -58.7265 | 64.1144 | 0.11902 | 0.021858 | 0.07079 | 0.071354 | 0.13062 | 0.0063938 | 0.0034073 | 0.2169 | 0.0027172 | 0.0023862 | 0.0035226 | 0.0036914 | -0.0049561 | 64.1327 | 64.27 | 16.4566 | -57.8613 | 64.1373 | -58.7769 | -58.8318 | -53.4668 | 15.8066 | -58.8821 | 64.1327 | 64.0503 | -58.8547 | -58.9417 | -0.050354 | -0.10529 | 0.022888 | 122.9965 | 0.86517 | 0.97046 | 0.01831 | -0.12817 | -0.21515 | 0.01831 | 5.2597 | -0.15564 | 0.059509 | -0.064087 | 122.8638 | 122.8592 | 75.1831 | -122.9462 | 122.8592 | 122.7768 | 74.5331 | -123.056
1429.5156 | 123.111 | -58.7631 | 64.1052 | 0.15717 | 0.017586 | 0.072072 | 0.070714 | 0.12998 | 0.0036166 | 0.0019119 | 0.11772 | -0.00070077 | -0.0010318 | 0.0030954 | 0.0026234 | -0.0070923 | 64.0411 | 64.1876 | 16.3742 | -57.8934 | 64.1235 | -58.786 | -58.8547 | -53.4393 | 15.7104 | -59.0286 | 64.1281 | 64.0457 | -58.8821 | -58.9737 | -0.022888 | -0.091552 | 0.01831 | 122.9507 | 0.86975 | 0.9613 | -0.064087 | -0.11902 | -0.21057 | 0.022888 | 5.3238 | -0.2655 | -0.054931 | -0.05951 | 122.8867 | 122.8043 | 75.1373 | -122.9599 | 122.8912 | 122.8088 | 74.4736 | -123.0789
1430.5156 | 123.1567 | -58.754 | 64.0961 | 1.1566 | 0.021217 | 0.069722 | 0.071995 | 0.13319 | 0.0066074 | 0.0019119 | 0.2169 | 0.0027172 | 0.00025 | 0.0016 | 0.0054004 | -0.0047425 | 64.1281 | 64.238 | 16.4566 | -57.8156 | 64.1052 | -58.7631 | -58.8272 | -53.4119 | 15.77 | -58.8913 | 64.119 | 64.0274 | -58.8684 | -58.96 | -0.009156 | -0.073242 | 0.009156 | 122.9919 | 0.93842 | 1.0117 | 0.032044 | -0.11444 | -0.20599 | 0.022889 | 5.3421 | -0.13733 | 0.068665 | -0.068664 | 122.8592 | 122.8821 | 75.2106 | -122.9233 | 122.8729 | 122.7814 | 74.5239 | -123.056
1431.5156 | 123.1155 | -58.699 | 64.1281 | 0.15717 | 0.020363 | 0.068868 | 0.073277 | 0.12977 | 0.0070346 | 0.0034073 | 0.26268 | 0.00229 | -0.0006046 | 0.0018136 | 0.0049732 | -0.0023927 | 64.1418 | 64.2792 | 16.5115 | -57.8567 | 64.1144 | -58.7494 | -58.8135 | -53.334 | 15.7745 | -58.8821 | 64.1418 | 64.0549 | -58.8364 | -58.9371 | -0.050354 | -0.11444 | -0.013733 | 122.9782 | 0.84229 | 0.95673 | 0.013733 | -0.13733 | -0.23804 | 0.013733 | 5.365 | -0.1831 | 0.054932 | -0.073242 | 122.8134 | 122.8409 | 75.2106 | -122.9416 | 122.8409 | 122.7539 | 74.4736 | -123.0652
1432.5156 | 123.1201 | -58.6761 | 64.1647 | 0.2182 | 0.024421 | 0.0678 | 0.073063 | 0.12934 | 0.0095982 | 0.0023391 | 0.23216 | 0.0035718 | 0.0006772 | 0.0022408 | 0.0054004 | -0.0038879 | 64.1235 | 64.183 | 16.452 | -57.843 | 64.2014 | -58.7494 | -58.8135 | -53.3386 | 15.7425 | -58.8867 | 64.183 | 64.0915 | -58.8364 | -58.9188 | -0.073243 | -0.13733 | 0.036621 | 122.8592 | 0.83313 | 0.97046 | -0.041199 | -0.16022 | -0.24262 | 0.01831 | 5.3375 | -0.21057 | 0.032043 | -0.073242 | 122.8775 | 122.7997 | 75.1282 | -122.9782 | 122.8592 | 122.7676 | 74.4186 | -123.0835
1433.5156 | 123.1155 | -58.7265 | 64.0961 | 0.15717 | 0.019081 | 0.071004 | 0.070073 | 0.13276 | 0.0046848 | 0.0023391 | 0.27794 | -0.00048697 | -0.0008182 | 0.0018136 | 0.0047596 | -0.0032471 | 64.0778 | 64.2426 | 16.4658 | -57.8659 | 64.0915 | -58.7814 | -58.8455 | -53.3478 | 15.715 | -58.9188 | 64.1235 | 64.0228 | -58.8593 | -58.9828 | -0.054932 | -0.11902 | -0.004577 | 122.9691 | 0.86059 | 0.97961 | -0.01831 | -0.13275 | -0.25635 | 0.027466 | 5.3787 | -0.19226 | 0.064087 | -0.073242 | 122.818 | 122.8043 | 75.1923 | -122.9416 | 122.85 | 122.7493 | 74.4415 | -123.0789
1434.5156 | 123.143 | -58.699 | 64.1647 | 0.19531 | 0.023781 | 0.071858 | 0.073491 | 0.13255 | 0.0087436 | 0.0055435 | 0.23979 | 0.0010082 | -0.0001774 | 0.0043772 | 0.0051868 | -0.0036743 | 64.151 | 64.2563 | 16.4932 | -57.7881 | 64.1739 | -58.7631 | -58.8089 | -53.2425 | 15.8249 | -58.8638 | 64.1602 | 64.064 | -58.8181 | -58.905 | -0.064087 | -0.10986 | 0.009155 | 122.9553 | 0.91095 | 1.0208 | -0.013733 | -0.11902 | -0.20599 | -0.004578 | 5.4565 | -0.16479 | 0.041198 | -0.10071 | 122.8729 | 122.85 | 75.1923 | -122.9736 | 122.8592 | 122.7631 | 74.5239 | -123.0698
1435.5156 | 123.111 | -58.7036 | 64.1327 | 0.14954 | 0.020149 | 0.071858 | 0.071354 | 0.13126 | 0.005753 | 0.0014847 | 0.20164 | 0.0018628 | 0.001959 | 0.0016 | 0.0034778 | -0.0036743 | 64.0961 | 64.2334 | 16.4932 | -57.8201 | 64.1418 | -58.7265 | -58.7952 | -53.2379 | 15.8295 | -58.873 | 64.1922 | 64.1098 | -58.8181 | -58.9142 | -0.022888 | -0.091553 | 0.009156 | 122.937 | 0.88348 | 0.97504 | -0.036621 | -0.11444 | -0.21057 | 0.05951 | 5.4657 | -0.16937 | 0.041199 | -0.022888 | 122.8455 | 122.7997 | 75.1968 | -122.9279 | 122.8958 | 122.8134 | 74.5331 | -123.0469
1436.5156 | 123.1979 | -58.6624 | 64.1785 | 0.19531 | 0.021858 | 0.067372 | 0.070927 | 0.12998 | 0.00853 | 0.0042619 | 0.63652 | 0.0014356 | -0.0001774 | 0.0022408 | 0.005614 | -0.0053833 | 64.183 | 64.3066 | 16.5619 | -57.6965 | 64.1647 | -58.7265 | -58.8226 | -53.1418 | 15.9348 | -58.8089 | 64.1968 | 64.1098 | -58.8043 | -58.8867 | -0.064086 | -0.16022 | -0.013733 | 122.9691 | 0.96588 | 1.1261 | 0.004577 | -0.14191 | -0.2243 | 0.01831 | 5.5206 | -0.14648 | 0.07782 | -0.068665 | 122.8271 | 122.8455 | 75.2243 | -123.0011 | 122.8592 | 122.7722 | 74.5972 | -123.0652
1437.5156 | 123.1338 | -58.7082 | 64.1464 | 0.16479 | 0.020149 | 0.071004 | 0.071354 | 0.13255 | 0.006821 | 0.0044755 | 0.27031 | 0.00058103 | -0.0010318 | 0.0011728 | 0.003905 | -0.0026063 | 64.1281 | 64.2517 | 16.5207 | -57.8064 | 64.1464 | -58.7311 | -58.7997 | -53.1738 | 15.8432 | -58.8684 | 64.1785 | 64.0915 | -58.8089 | -58.9188 | -0.022888 | -0.091553 | 0 | 122.9599 | 0.90179 | 0.99335 | -0.01831 | -0.10071 | -0.21057 | 0.032044 | 5.5344 | -0.16022 | 0.050354 | -0.054931 | 122.8546 | 122.8363 | 75.2289 | -122.9462 | 122.8867 | 122.7997 | 74.5514 | -123.0652
1438.5156 | 123.1201 | -58.7265 | 64.1693 | 0.21057 | 0.022926 | 0.071431 | 0.074772 | 0.13105 | 0.011948 | 0.0040481 | 0.17113 | 0.0046398 | 0.0008908 | 0.0035226 | 0.0068958 | -0.0045289 | 64.0869 | 64.1876 | 16.452 | -57.7927 | 64.1876 | -58.7769 | -58.8089 | -53.1509 | 15.77 | -58.9142 | 64.2151 | 64.1006 | -58.8272 | -58.9188 | -0.050354 | -0.082398 | 0.01831 | 122.9141 | 0.93384 | 1.0162 | -0.082398 | -0.10071 | -0.19226 | 0.045776 | 5.5756 | -0.18768 | 0.004577 | -0.068665 | 122.9141 | 122.8134 | 75.1785 | -122.9782 | 122.9416 | 122.8271 | 74.4965 | -123.0881
1439.5156 | 123.175 | -58.6761 | 64.1693 | 0.19531 | 0.023781 | 0.070363 | 0.073491 | 0.13276 | 0.0083164 | 0.0036209 | 0.23979 | 0.0020764 | -0.0040226 | 0.0020272 | 0.0066822 | -0.0041017 | 64.1693 | 64.3295 | 16.5756 | -57.7103 | 64.1647 | -58.7219 | -58.7677 | -53.0548 | 15.8936 | -58.8226 | 64.1922 | 64.0778 | -58.7906 | -58.8959 | -0.045777 | -0.091553 | -0.004578 | 123.0057 | 0.96588 | 1.0574 | 0 | -0.11444 | -0.21973 | 0.022888 | 5.6213 | -0.14648 | 0.073242 | -0.091553 | 122.8409 | 122.8455 | 75.2518 | -122.937 | 122.8683 | 122.7539 | 74.5697 | -123.0652
1440.5156 | 123.1247 | -58.6945 | 64.1693 | 0.19531 | 0.025917 | 0.070363 | 0.074986 | 0.13105 | 0.0095982 | 0.0034073 | 0.24742 | 0.0025036 | -0.0006046 | 0.0030954 | 0.0058276 | -0.0028199 | 64.1373 | 64.2151 | 16.4886 | -57.7515 | 64.183 | -58.7402 | -58.7906 | -53.0319 | 15.8295 | -58.8547 | 64.1968 | 64.1006 | -58.8226 | -58.9325 | -0.045776 | -0.09613 | 0.013732 | 122.9095 | 0.94299 | 1.0391 | -0.032044 | -0.12817 | -0.23804 | 0.027465 | 5.6625 | -0.16022 | 0.07782 | -0.068665 | 122.8775 | 122.8317 | 75.1831 | -122.9599 | 122.8912 | 122.7951 | 74.5239 | -123.1018
1441.5156 | 123.1201 | -58.7036 | 64.1556 | 0.14191 | 0.019935 | 0.070577 | 0.073918 | 0.13041 | 0.0038304 | 0.00084388 | 0.28557 | 0.0029308 | -0.001459 | 0.0030954 | 0.0036914 | -0.0041017 | 64.119 | 64.2609 | 16.5115 | -57.7515 | 64.1556 | -58.7631 | -58.8089 | -53.0182 | 15.8203 | -58.873 | 64.1693 | 64.1006 | -58.7997 | -58.9233 | -0.05951 | -0.10529 | 0 | 122.9645 | 0.95215 | 1.0574 | -0.036621 | -0.096131 | -0.21973 | 0.013733 | 5.6854 | -0.16937 | 0.050354 | -0.054932 | 122.8592 | 122.8226 | 75.2151 | -122.9645 | 122.8729 | 122.8043 | 74.5239 | -123.0789
1442.5156 | 123.1842 | -58.7082 | 64.1327 | -0.84229 | 0.022712 | 0.069509 | 0.072423 | 0.13148 | 0.0083164 | 0.0042619 | 0.27794 | 0.0012218 | 0.0008908 | 0.0037362 | 0.0060412 | -0.0032471 | 64.1327 | 64.2975 | 16.5848 | -57.7103 | 64.1373 | -58.7677 | -58.786 | -52.9633 | 15.8478 | -58.8547 | 64.1739 | 64.0457 | -58.8364 | -58.9096 | -0.059509 | -0.07782 | 0.004578 | 123.0057 | 0.99793 | 1.0757 | 0 | -0.12817 | -0.20142 | 0.041199 | 5.7449 | -0.14648 | 0.054932 | -0.086975 | 122.8455 | 122.8409 | 75.293 | -122.9187 | 122.8821 | 122.7539 | 74.556 | -123.0423
1443.5156 | 123.1064 | -58.699 | 64.1785 | 0.19531 | 0.021004 | 0.070149 | 0.071782 | 0.12934 | 0.0063938 | 0.0042619 | 0.20927 | 0.0012218 | -0.003168 | 0.0013864 | 0.0036914 | -0.0034607 | 64.1693 | 64.2929 | 16.5985 | -57.7103 | 64.151 | -58.7265 | -58.7814 | -52.8992 | 15.8524 | -58.8318 | 64.1876 | 64.1098 | -58.8089 | -58.9142 | -0.027465 | -0.082397 | -0.027466 | 122.9919 | 0.98877 | 1.0712 | -0.009155 | -0.10986 | -0.21515 | 0.009155 | 5.7999 | -0.13275 | 0.082398 | -0.068665 | 122.85 | 122.8683 | 75.2975 | -122.9599 | 122.8867 | 122.8088 | 74.5514 | -123.0927
1444.5156 | 123.1018 | -58.6761 | 64.1602 | 0.23346 | 0.025062 | 0.071858 | 0.073918 | 0.13212 | 0.0083164 | 0.0055435 | 0.25505 | 0.0014356 | 0.0032406 | 0.0009592 | 0.0066822 | -0.0049561 | 64.1327 | 64.1876 | 16.5161 | -57.724 | 64.2151 | -58.7357 | -58.8043 | -52.9129 | 15.7883 | -58.8959 | 64.2288 | 64.1327 | -58.8043 | -58.9005 | -0.05951 | -0.12817 | 0.054932 | 122.8638 | 0.95215 | 1.0803 | -0.027466 | -0.12817 | -0.22431 | 0.068665 | 5.7632 | -0.21973 | 0.004578 | -0.027466 | 122.8912 | 122.8088 | 75.1923 | -122.9645 | 122.905 | 122.8088 | 74.4644 | -123.0606
1445.5156 | 123.1842 | -58.6533 | 64.183 | 0.24109 | 0.022499 | 0.069722 | 0.072423 | 0.13191 | 0.0072482 | 0.0061845 | 0.2169 | 0.00229 | -0.001459 | 0.0016 | 0.0051868 | -0.0045289 | 64.1647 | 64.2792 | 16.5939 | -57.6736 | 64.1922 | -58.7082 | -58.7677 | -52.8305 | 15.8615 | -58.8272 | 64.2014 | 64.1144 | -58.7952 | -58.9142 | -0.054932 | -0.11444 | 0.009156 | 122.9324 | 0.97961 | 1.0941 | -0.01831 | -0.14191 | -0.26093 | 0.018311 | 5.8228 | -0.17395 | 0.086976 | -0.068664 | 122.8455 | 122.818 | 75.2472 | -122.9507 | 122.8546 | 122.7676 | 74.5148 | -123.0972
1446.5156 | 123.0286 | -58.667 | 64.2334 | 0.042725 | 0.026985 | 0.067586 | 0.075413 | 0.13276 | 0.010025 | 0.0034073 | 0.041427 | 0.0016492 | 0.0017454 | 0.0041634 | 0.0051868 | -0.0032471 | 64.1052 | 64.1739 | 16.4795 | -57.7377 | 64.27 | -58.7082 | -58.7677 | -52.8168 | 15.7791 | -58.9371 | 64.2975 | 64.2014 | -58.7769 | -58.8821 | -0.041199 | -0.10071 | 0.036622 | 122.8409 | 0.92926 | 1.03 | -0.12817 | -0.10986 | -0.21515 | 0.064087 | 5.8502 | -0.27008 | -0.054932 | -0.032043 | 122.937 | 122.7722 | 75.1465 | -123.0011 | 122.9645 | 122.8683 | 74.4461 | -123.1155
1447.5156 | 123.1659 | -58.6212 | 64.2014 | 0.13428 | 0.023994 | 0.068227 | 0.074772 | 0.13062 | 0.0078892 | 0.0042619 | 0.27794 | 0.00079463 | -0.0025272 | 0.0058724 | 0.0054004 | -0.0051697 | 64.1922 | 64.3387 | 16.626 | -57.6233 | 64.183 | -58.6945 | -58.7311 | -52.6382 | 15.9393 | -58.7906 | 64.2426 | 64.1785 | -58.7494 | -58.8593 | -0.073242 | -0.10986 | -0.018311 | 122.9599 | 0.99792 | 1.1078 | -0.009155 | -0.12817 | -0.23804 | 0.041199 | 5.983 | -0.16937 | 0.068665 | -0.022888 | 122.8043 | 122.8134 | 75.2472 | -122.9324 | 122.8638 | 122.7997 | 74.5605 | -123.0606
1448.5156 | 123.0606 | -58.6853 | 64.2014 | 3.3386 | 0.027839 | 0.073995 | 0.078831 | 0.13191 | 0.010239 | 0.0027665 | 0.17113 | 0.0050672 | 0.0015316 | 0.003309 | 0.0051868 | -0.0026063 | 64.2105 | 64.1876 | 16.4658 | -57.6645 | 64.2609 | -58.6945 | -58.7769 | -52.7756 | 15.7425 | -58.8959 | 64.2838 | 64.1968 | -58.7997 | -58.8776 | -0.009155 | -0.091552 | 0.059509 | 122.8729 | 1.0208 | 1.1124 | 0.009155 | -0.11444 | -0.19226 | 0.082397 | 5.9097 | -0.21057 | -0.018311 | -0.004578 | 122.9462 | 122.8958 | 75.1511 | -122.9782 | 122.9691 | 122.8821 | 74.4278 | -123.0789
1449.5156 | 123.1659 | -58.6853 | 64.1968 | 0.22583 | 0.022285 | 0.065236 | 0.067296 | 0.13319 | 0.0055392 | 0.0040481 | 0.41527 | 0.0025036 | -0.0010318 | 0.003309 | 0.0049732 | -0.0030335 | 64.2746 | 64.2838 | 16.6214 | -57.5958 | 64.1785 | -58.6807 | -58.754 | -52.6611 | 15.8569 | -58.7906 | 64.2151 | 64.1327 | -58.7814 | -58.8684 | 0.004578 | -0.068664 | -0.01831 | 122.9691 | 1.0895 | 1.1581 | 0.07782 | -0.09613 | -0.18311 | 0.018311 | 6.0242 | -0.10529 | 0.07782 | -0.064087 | 122.8638 | 122.9599 | 75.3067 | -122.9507 | 122.9004 | 122.818 | 74.5422 | -123.0652
1450.5156 | 123.0652 | -58.6578 | 64.2471 | 0.15717 | 0.025703 | 0.069295 | 0.076909 | 0.13148 | 0.010025 | 0.0038345 | 0.19402 | 0.0037854 | 0.0040952 | 0.0043772 | 0.0054004 | -0.0030335 | 64.1464 | 64.2151 | 16.4795 | -57.6691 | 64.2654 | -58.6853 | -58.7265 | -52.6794 | 15.7791 | -58.8638 | 64.2883 | 64.2014 | -58.7814 | -58.8501 | -0.027466 | -0.068664 | 0.018311 | 122.8729 | 0.98877 | 1.0574 | -0.10071 | -0.1236 | -0.19226 | 0.041199 | 5.9784 | -0.20599 | -0.013733 | -0.045776 | 122.9233 | 122.8043 | 75.1373 | -122.9736 | 122.9462 | 122.8592 | 74.437 | -123.0972
1451.5156 | 123.1796 | -58.6029 | 64.2151 | 0.28687 | 0.025703 | 0.070149 | 0.072636 | 0.13212 | 0.005753 | 0.0063981 | 0.30846 | 0.00229 | -0.0010318 | 0.0011728 | 0.0043324 | -0.0030335 | 64.2197 | 64.3524 | 16.6397 | -57.5592 | 64.2288 | -58.6487 | -58.699 | -52.5055 | 15.5457 | -58.8272 | 64.1785 | 64.1373 | -58.754 | -58.8181 | -0.045777 | -0.096131 | 0.013733 | 122.9553 | 1.0437 | 1.1398 | 0.004578 | -0.15106 | -0.21515 | -0.036621 | 6.0974 | -0.2243 | -0.009155 | -0.07782 | 122.8317 | 122.8226 | 75.2426 | -122.9141 | 122.7814 | 122.7402 | 74.1486 | -123.0331
1452.5156 | 123.024 | -58.6533 | 64.27 | 0.080872 | 0.030189 | 0.070149 | 0.076268 | 0.13404 | 0.010666 | 0.0059707 | 0.094833 | 0.0027172 | 0.0023862 | 0.0039498 | 0.0066822 | -0.0047425 | 64.1602 | 64.2334 | 16.5161 | -57.6187 | 64.3021 | -58.667 | -58.7585 | -52.6108 | 15.7196 | -58.8959 | 64.2838 | 64.2517 | -58.786 | -58.8638 | -0.013733 | -0.10529 | 0.032043 | 122.8867 | 1.0345 | 1.1398 | -0.10986 | -0.13275 | -0.21057 | 0.013732 | 6.0425 | -0.24262 | -0.032043 | -0.018311 | 122.9553 | 122.8134 | 75.1694 | -123.0286 | 122.937 | 122.905 | 74.3729 | -123.1339
1453.5156 | 123.1522 | -58.6029 | 64.2426 | 0.2182 | 0.02549 | 0.070577 | 0.073277 | 0.13169 | 0.0078892 | 0.0027665 | 0.27794 | 0.0010082 | 0.0032406 | 0.0052316 | 0.0049732 | -0.0038879 | 64.1922 | 64.3158 | 16.6168 | -57.5592 | 64.27 | -58.6487 | -58.7128 | -52.4597 | 15.834 | -58.7494 | 64.2792 | 64.2242 | -58.7402 | -58.7997 | -0.045777 | -0.10986 | 0.027466 | 122.9187 | 1.0437 | 1.1536 | -0.050354 | -0.13733 | -0.19684 | 0.036621 | 6.1432 | -0.14648 | 0.050354 | -0.018311 | 122.8729 | 122.7951 | 75.2197 | -122.9553 | 122.8821 | 122.8271 | 74.4369 | -123.0423
1454.5156 | 122.9691 | -58.6578 | 64.2563 | 0.24872 | 0.028267 | 0.07079 | 0.0752 | 0.13426 | 0.011307 | 0.0057571 | 0.17876 | 0.0037854 | 0.0011044 | 0.0026682 | 0.003905 | -0.0032471 | 64.1144 | 64.183 | 16.507 | -57.6279 | 64.2838 | -58.6945 | -58.7631 | -52.5467 | 15.6921 | -59.1293 | 64.2471 | 64.151 | -58.786 | -58.8959 | -0.036621 | -0.10529 | 0.027465 | 122.8409 | 1.03 | 1.1353 | -0.14191 | -0.12817 | -0.23804 | -0.009156 | 6.1111 | -0.4715 | -0.23346 | -0.10529 | 122.9416 | 122.7722 | 75.1648 | -123.0194 | 122.905 | 122.8088 | 74.35 | -123.1522
1455.5156 | 123.2208 | -58.6533 | 64.1968 | 0.18005 | 0.02549 | 0.069081 | 0.074345 | 0.13297 | 0.0072482 | 0.0051163 | 0.30846 | 0.0031446 | 0.00025 | 0.0026682 | 0.0047596 | -0.0036743 | 64.2197 | 64.3295 | 16.6626 | -57.5272 | 64.2242 | -58.667 | -58.7036 | -52.3956 | 15.8249 | -58.7631 | 64.2426 | 64.1693 | -58.7769 | -58.8638 | -0.013733 | -0.050354 | 0.027466 | 122.9828 | 1.1261 | 1.1765 | 0.022889 | -0.1236 | -0.21057 | 0.045777 | 6.2576 | -0.10986 | 0.10071 | -0.027465 | 122.8775 | 122.8729 | 75.3159 | -122.9004 | 122.8958 | 122.8226 | 74.4781 | -123.0606
1456.5156 | 123.0377 | -58.7494 | 64.2105 | 0.15717 | 0.027626 | 0.071218 | 0.076909 | 0.13276 | 0.0098118 | 0.0055435 | -0.37819 | 0.0046398 | 0.003027 | 0.0009592 | 0.0041186 | -0.0028199 | 64.0686 | 63.7299 | 16.246 | -57.6874 | 64.1739 | -58.7677 | -58.8226 | -52.5375 | 15.6006 | -58.9417 | 64.2654 | 64.1647 | -58.8593 | -58.9233 | -0.01831 | -0.073242 | -0.036621 | 122.4792 | 1.062 | 1.1353 | -0.14191 | -0.10986 | -0.17395 | 0.054932 | 6.2119 | -0.19226 | -0.01831 | -0.045776 | 122.9233 | 122.818 | 74.9954 | -123.0331 | 123.0148 | 122.9141 | 74.35 | -123.1338
1457.5156 | 123.1384 | -58.6578 | 64.1785 | 0.24872 | 0.02613 | 0.068654 | 0.073918 | 0.13468 | 0.0089572 | 0.0010575 | 0.27031 | 0.0046398 | 0.0034542 | 0.0041634 | 0.0051868 | -0.0011109 | 64.1235 | 64.2059 | 16.5115 | -57.605 | 64.2105 | -58.7219 | -58.7723 | -52.3636 | 15.7425 | -58.8181 | 64.2105 | 64.1464 | -58.8043 | -58.8593 | -0.064087 | -0.11444 | 0.032043 | 122.8638 | 1.0529 | 1.1673 | -0.054932 | -0.14648 | -0.20142 | 0.032043 | 6.2943 | -0.16022 | 0.041199 | -0.032044 | 122.8683 | 122.7814 | 75.1694 | -122.9507 | 122.8683 | 122.8043 | 74.4003 | -123.0377
1458.5156 | 123.1201 | -58.6578 | 64.2242 | 0.11902 | 0.028053 | 0.068654 | 0.075627 | 0.13212 | 0.010666 | 0.0044755 | 0.1635 | 0.0042126 | 0.0004636 | 0.0028818 | 0.0054004 | -0.0034607 | 64.1144 | 64.2059 | 16.5253 | -57.5912 | 64.27 | -58.6533 | -58.7585 | -52.4048 | 15.6326 | -58.9096 | 64.2746 | 64.238 | -58.7631 | -58.8821 | 0.004578 | -0.10071 | 0.045777 | 122.8638 | 1.0666 | 1.1673 | -0.10986 | -0.10529 | -0.2243 | 0.050354 | 6.2531 | -0.25177 | -0.027466 | 0.013733 | 122.9279 | 122.7722 | 75.1831 | -122.9828 | 122.9324 | 122.8958 | 74.2905 | -123.1064
1459.5156 | 123.0194 | -58.667 | 64.2517 | 0.11902 | 0.024849 | 0.06844 | 0.077122 | 0.13255 | 0.012589 | 0.0027665 | 0.018539 | 0.0046398 | 0.0025998 | 0.0041634 | 0.0066822 | -0.0028199 | 64.1373 | 64.3845 | 16.507 | -57.637 | 64.2609 | -58.7082 | -58.7906 | -52.3407 | 15.6281 | -58.9096 | 64.2929 | 64.2059 | -58.8089 | -58.9188 | -0.041199 | -0.1236 | 0.009155 | 123.0515 | 1.03 | 1.1536 | -0.11444 | -0.14191 | -0.25177 | 0.041199 | 6.3263 | -0.24262 | 0.009155 | -0.045776 | 122.9279 | 122.8043 | 75.174 | -123.0423 | 122.9599 | 122.8729 | 74.295 | -123.1705
1460.5156 | 123.024 | -58.7082 | 64.2151 | 0.035095 | 0.029762 | 0.070149 | 0.074772 | 0.13191 | 0.010025 | 0.0031937 | 0.10246 | 0.0042126 | 0.00025 | 0.0024546 | 0.0060412 | -0.0032471 | 64.1052 | 64.1876 | 16.4612 | -57.6096 | 64.238 | -58.7402 | -58.786 | -52.3361 | 15.6143 | -58.9233 | 64.2609 | 64.183 | -58.8409 | -58.905 | -0.032043 | -0.07782 | 0.022888 | 122.8958 | 1.0986 | 1.1765 | -0.10986 | -0.13275 | -0.19684 | 0.045776 | 6.3721 | -0.21515 | -0.018311 | -0.032044 | 122.9462 | 122.8134 | 75.1694 | -123.0011 | 122.9691 | 122.8912 | 74.3225 | -123.1201
1461.5156 | 123.0469 | -58.6716 | 64.2334 | -0.056458 | 0.027199 | 0.073354 | 0.079258 | 0.13148 | 0.01088 | 0.0016983 | 0.19402 | 0.0059216 | 0.0023862 | 0.0035226 | 0.0051868 | 0.00081174 | 64.1373 | 64.183 | 16.4566 | -57.5867 | 64.2838 | -58.699 | -58.7677 | -52.272 | 15.6052 | -58.8821 | 64.2929 | 64.238 | -58.786 | -58.8821 | -0.027466 | -0.09613 | 0.050354 | 122.8546 | 1.0849 | 1.181 | -0.09613 | -0.11444 | -0.21057 | 0.05951 | 6.3995 | -0.21057 | 0 | 0.004578 | 122.9553 | 122.8088 | 75.1282 | -123.0011 | 122.9645 | 122.9095 | 74.2767 | -123.1155
1462.5156 | 123.0331 | -58.7036 | 64.2517 | 0.0045777 | 0.027626 | 0.070577 | 0.075413 | 0.13233 | 0.011307 | 0.0034073 | 0.10246 | 0.0031446 | 0.0025998 | 0.0037362 | 0.0041186 | -4.2662e-05 | 64.1052 | 64.1922 | 16.4749 | -57.5867 | 64.2426 | -58.7265 | -58.786 | -52.2491 | 15.596 | -58.9279 | 64.2563 | 64.2014 | -58.7997 | -58.8959 | -0.022888 | -0.082398 | -0.009155 | 122.8958 | 1.1169 | 1.1993 | -0.14648 | -0.096131 | -0.19226 | 0.004578 | 6.4545 | -0.2243 | -0.032043 | -0.050354 | 122.9462 | 122.8088 | 75.1785 | -123.0377 | 122.9599 | 122.905 | 74.2996 | -123.1476
1463.5156 | 123.0652 | -58.6578 | 64.2426 | 0.09613 | 0.026558 | 0.07079 | 0.076054 | 0.13105 | 0.0089572 | 0.0031937 | 0.22453 | 0.0042126 | 0.001318 | 0.005018 | 0.0043324 | -4.2662e-05 | 64.1052 | 64.2105 | 16.4474 | -57.5775 | 64.2563 | -58.6945 | -58.7814 | -52.1759 | 15.596 | -58.8593 | 64.2929 | 64.2288 | -58.786 | -58.873 | -0.036621 | -0.1236 | 0.013733 | 122.8683 | 1.0803 | 1.2039 | -0.13733 | -0.12817 | -0.21515 | 0.050354 | 6.4819 | -0.20142 | 0.013733 | -0.013733 | 122.9141 | 122.7631 | 75.1053 | -123.024 | 122.9507 | 122.8867 | 74.2538 | -123.1155
1464.5156 | 123.0423 | -58.667 | 64.27 | 0.057983 | 0.027199 | 0.068868 | 0.07584 | 0.1334 | 0.012162 | 0.0055435 | 0.15587 | 0.0029308 | 0.003027 | 0.0035226 | 0.004546 | -0.00089726 | 64.1373 | 64.2197 | 16.4978 | -57.5363 | 64.2746 | -58.6761 | -58.7357 | -52.1439 | 15.5731 | -58.9005 | 64.2929 | 64.2334 | -58.7769 | -58.8821 | -0.009155 | -0.068665 | 0.004577 | 122.8867 | 1.1307 | 1.1993 | -0.13275 | -0.10986 | -0.21515 | 0.022888 | 6.5231 | -0.23346 | -0.018311 | -0.036622 | 122.9416 | 122.8043 | 75.1648 | -123.0057 | 122.9599 | 122.9004 | 74.2401 | -123.1522
1465.5156 | 123.0103 | -58.6853 | 64.2883 | 0.042725 | 0.028267 | 0.069081 | 0.07819 | 0.13212 | 0.0091708 | 0.0036209 | 0.2169 | 0.0031446 | 0.003027 | 0.0028818 | 0.0101 | -0.0013245 | 64.1235 | 64.2105 | 16.5115 | -57.5043 | 64.3204 | -58.6487 | -58.7357 | -52.2308 | 16.04 | -58.7723 | 64.3295 | 64.2929 | -58.754 | -58.8409 | 0.036621 | -0.050354 | 0.032044 | 122.8958 | 1.181 | 1.2314 | -0.16479 | -0.068664 | -0.15564 | 0.041199 | 6.4545 | -0.086975 | 0.068664 | 0.004578 | 123.0057 | 122.8088 | 75.1968 | -123.024 | 123.0148 | 122.9782 | 74.7253 | -123.1293
1466.5156 | 123.0835 | -58.6578 | 64.2838 | -0.15564 | 0.027839 | 0.072713 | 0.075413 | 0.13169 | 0.010025 | 0.0031937 | 0.0032804 | 0.0029308 | 0.0021726 | 0.0022408 | 0.0041186 | -0.0023927 | 64.1876 | 64.2975 | 16.5939 | -57.486 | 64.2838 | -58.6853 | -58.7311 | -51.9836 | 15.6555 | -58.8043 | 64.3158 | 64.2288 | -58.754 | -58.8593 | -0.027466 | -0.073242 | 0 | 122.9553 | 1.1719 | 1.2451 | -0.09613 | -0.09613 | -0.20142 | 0.032044 | 6.6742 | -0.14648 | 0.054932 | -0.054931 | 122.9416 | 122.8455 | 75.2518 | -123.0148 | 122.9736 | 122.8867 | 74.3134 | -123.143
1467.5156 | 123.0469 | -58.7082 | 64.2471 | 0.088501 | 0.029548 | 0.071645 | 0.073704 | 0.13105 | 0.010025 | 0.0070389 | 0.15587 | 0.0027172 | 0.0015316 | 0.0043772 | 0.0051868 | 0.00059814 | 64.1235 | 64.2288 | 16.5436 | -57.5363 | 64.2517 | -58.7128 | -58.7631 | -52.0065 | 15.5228 | -58.8959 | 64.2609 | 64.2014 | -58.7952 | -58.9005 | -0.004578 | -0.054932 | 0.004578 | 122.937 | 1.1719 | 1.2268 | -0.1236 | -0.086975 | -0.19226 | 0.013733 | 6.7017 | -0.18768 | 0.004578 | -0.045776 | 122.9599 | 122.8317 | 75.2518 | -123.0103 | 122.9691 | 122.9095 | 74.231 | -123.1476
1468.5312 | 123.0835 | -58.699 | 64.1785 | 0.10376 | 0.021858 | 0.071645 | 0.073918 | 0.13191 | 0.0027622 | 0.0025529 | 0.25505 | -0.00027337 | -0.0025272 | 0.0026682 | 0.0041186 | 0.0016663 | 64.064 | 64.2654 | 16.5756 | -57.5363 | 64.1647 | -58.7173 | -58.7677 | -51.9836 | 15.6006 | -58.8638 | 64.1739 | 64.1327 | -58.7997 | -58.8913 | -0.01831 | -0.068664 | -0.013733 | 122.9645 | 1.1627 | 1.2314 | -0.11444 | -0.10071 | -0.19226 | -0.004578 | 6.7154 | -0.16479 | 0.027465 | -0.045777 | 122.8638 | 122.7631 | 75.2747 | -122.9462 | 122.8729 | 122.8317 | 74.2996 | -123.0698
1469.5156 | 123.0423 | -58.7448 | 64.183 | 0.035095 | 0.029335 | 0.072713 | 0.076481 | 0.13233 | 0.012802 | 0.0042619 | 0.094833 | 0.003999 | 0.0049496 | 0.005018 | 0.0047596 | -0.0032471 | 64.0686 | 64.1418 | 16.3971 | -57.5684 | 64.183 | -58.786 | -58.8318 | -51.9882 | 15.4404 | -58.9828 | 64.2197 | 64.1281 | -58.8776 | -58.9737 | -0.041199 | -0.086975 | 0 | 122.8867 | 1.1765 | 1.2634 | -0.11444 | -0.13275 | -0.22888 | 0.036622 | 6.7566 | -0.23804 | -0.009155 | -0.054931 | 122.9279 | 122.8134 | 75.1419 | -123.0148 | 122.9645 | 122.8729 | 74.1852 | -123.1567
1470.5156 | 123.0698 | -58.7585 | 64.151 | -0.15564 | 0.02848 | 0.069936 | 0.076481 | 0.13276 | 0.01088 | 0.0038345 | -0.11879 | 0.0014356 | 0.003027 | 0.0058724 | 0.004546 | -0.0032471 | 64.0686 | 64.1693 | 16.3742 | -57.5455 | 64.2014 | -58.8043 | -58.8593 | -51.9058 | 15.477 | -58.9279 | 64.1922 | 64.1235 | -58.8501 | -58.9508 | -0.045776 | -0.10071 | 0.050354 | 122.9279 | 1.2131 | 1.3138 | -0.082397 | -0.091553 | -0.19226 | 0.041199 | 6.8527 | -0.16937 | 0.022889 | -0.027466 | 122.9599 | 122.8271 | 75.1328 | -123.0103 | 122.9507 | 122.8821 | 74.2355 | -123.1018
1471.5156 | 123.0377 | -58.6945 | 64.2059 | -0.010681 | 0.029121 | 0.071431 | 0.076054 | 0.13426 | 0.0087436 | 0.0059707 | 0.049057 | 0.0044262 | 0.0015316 | 0.0052316 | 0.005614 | -0.0017517 | 64.1464 | 64.2517 | 16.5482 | -57.4905 | 64.2197 | -58.7219 | -58.786 | -51.8097 | 15.4907 | -58.8867 | 64.2563 | 64.1876 | -58.7906 | -58.9096 | -0.027466 | -0.091553 | 0.013733 | 122.9462 | 1.2039 | 1.2955 | -0.05951 | -0.09613 | -0.21515 | 0.050354 | 6.8848 | -0.19226 | 0.022888 | -0.018311 | 122.9141 | 122.8409 | 75.2426 | -122.9919 | 122.9507 | 122.8821 | 74.1852 | -123.1155
1472.5156 | 123.0606 | -58.7311 | 64.2059 | -0.13275 | 0.024849 | 0.072499 | 0.076481 | 0.13233 | 0.007462 | 0.0042619 | -0.073013 | 0.0018628 | 0.0025998 | 0.0041634 | 0.0030506 | -0.00068366 | 64.0411 | 64.1647 | 16.4703 | -57.518 | 64.1968 | -58.7402 | -58.8043 | -51.8005 | 15.4404 | -58.9096 | 64.2426 | 64.1464 | -58.8226 | -58.9279 | -0.009155 | -0.073242 | -0.009156 | 122.8958 | 1.2131 | 1.2863 | -0.16479 | -0.091553 | -0.19684 | 0.036621 | 6.9305 | -0.17853 | 0.01831 | -0.05951 | 122.9279 | 122.7722 | 75.2014 | -123.0103 | 122.9736 | 122.8775 | 74.1714 | -123.1338
1473.5156 | 123.1613 | -58.7723 | 64.0594 | 0.2182 | 0.023994 | 0.07079 | 0.075627 | 0.13276 | 0.0081028 | 0.0055435 | 0.27794 | 0.00229 | 0.0015316 | 0.0020272 | 0.003905 | -0.0023927 | 63.9862 | 64.1647 | 16.3239 | -57.5729 | 64.064 | -58.8226 | -58.8959 | -51.741 | 15.4175 | -58.9233 | 64.0732 | 64.0091 | -58.9142 | -59.0149 | -0.050354 | -0.1236 | 0.004578 | 122.937 | 1.1993 | 1.3229 | -0.073242 | -0.14191 | -0.24262 | 0.013733 | 7.0312 | -0.15106 | 0.091553 | -0.050354 | 122.8363 | 122.7585 | 75.0961 | -122.9553 | 122.8455 | 122.7814 | 74.1898 | -123.0743
1474.5156 | 123.056 | -58.7311 | 64.1876 | -1.2619 | 0.021004 | 0.071004 | 0.073491 | 0.1334 | 0.007462 | 0.0038345 | -0.042496 | 0.0046398 | 0.001318 | 0.0045908 | 0.0036914 | -0.0028199 | 64.032 | 64.1327 | 16.3239 | -57.5317 | 64.183 | -58.786 | -58.8409 | -51.7273 | 15.3946 | -58.9279 | 64.2471 | 64.1464 | -58.8638 | -58.9371 | -0.054932 | -0.10986 | -0.004578 | 122.8638 | 1.1993 | 1.3092 | -0.15564 | -0.13275 | -0.20599 | 0.059509 | 7.0038 | -0.19684 | 0.009156 | -0.041199 | 122.9141 | 122.7631 | 75.0549 | -123.0286 | 122.9782 | 122.8775 | 74.1257 | -123.1247
1475.5156 | 123.0835 | -58.7585 | 64.1602 | -0.18616 | 0.028053 | 0.069295 | 0.076695 | 0.13212 | 0.011093 | 0.0059707 | -0.073013 | 0.0052808 | 0.0017454 | 0.0020272 | 0.006255 | -0.0036743 | 64.0549 | 64.183 | 16.4108 | -57.5043 | 64.183 | -58.7769 | -58.8364 | -51.6495 | 15.4541 | -58.905 | 64.2014 | 64.1281 | -58.8593 | -58.9554 | -0.01831 | -0.07782 | 0.022888 | 122.9416 | 1.2543 | 1.3321 | -0.10528 | -0.10071 | -0.19684 | 0.041199 | 7.1091 | -0.14648 | 0.050354 | -0.032043 | 122.9416 | 122.8134 | 75.1694 | -122.9965 | 122.9599 | 122.8867 | 74.2126 | -123.1155
1476.5156 | 123.0377 | -58.7173 | 64.238 | 0.30975 | 0.02613 | 0.074208 | 0.076695 | 0.1334 | 0.007462 | 0.0034073 | -0.073013 | 0.0044262 | 0.0015316 | 0.0045908 | 0.0032642 | -0.0017517 | 64.064 | 64.1968 | 16.4246 | -57.4493 | 64.2517 | -58.7311 | -58.7997 | -51.5808 | 15.4037 | -58.8867 | 64.2517 | 64.1968 | -58.8089 | -58.9188 | -0.013733 | -0.082398 | 0.013733 | 122.9141 | 1.268 | 1.3504 | -0.17395 | -0.091553 | -0.20142 | 0.013733 | 7.1365 | -0.16937 | 0.032043 | -0.041199 | 122.9691 | 122.7814 | 75.1419 | -123.0377 | 122.9691 | 122.9141 | 74.1211 | -123.1567
1477.5156 | 123.0698 | -58.7311 | 64.183 | -0.11749 | 0.028267 | 0.071645 | 0.077549 | 0.13404 | 0.0098118 | 0.0061845 | -0.050125 | 0.0046398 | 0.0040952 | 0.003309 | 0.002837 | -0.0045289 | 64.0778 | 64.2242 | 16.4108 | -57.4722 | 64.2288 | -58.7357 | -58.8226 | -51.5121 | 15.3946 | -58.9005 | 64.2197 | 64.1235 | -58.8226 | -58.9233 | -0.004578 | -0.091553 | 0.045777 | 122.9553 | 1.2589 | 1.3504 | -0.10528 | -0.091553 | -0.19226 | 0.036622 | 7.2189 | -0.16937 | 0.022888 | -0.059509 | 122.9599 | 122.8088 | 75.1419 | -123.0057 | 122.9507 | 122.8546 | 74.1257 | -123.1064
1478.5156 | 123.0194 | -58.8364 | 64.0961 | 0.11902 | 0.026771 | 0.07079 | 0.078618 | 0.13062 | 0.010453 | 0.0040481 | -0.019608 | 0.0054944 | 0.0032406 | 0.0037362 | 0.0047596 | -0.0021789 | 63.9084 | 64.0091 | 16.2506 | -57.6141 | 64.1281 | -58.8455 | -58.9417 | -51.6266 | 15.2527 | -59.0378 | 64.1052 | 64.0686 | -58.9417 | -59.0332 | -0.009155 | -0.10529 | 0.032044 | 122.8455 | 1.2222 | 1.3275 | -0.18768 | -0.10529 | -0.19684 | 0.009156 | 7.2098 | -0.20142 | -0.004578 | -0.027465 | 122.9645 | 122.7448 | 75.087 | -123.0377 | 122.9416 | 122.905 | 74.0891 | -123.1293
1479.5156 | 123.0881 | -58.7357 | 64.2014 | -0.14801 | 0.02613 | 0.071858 | 0.076909 | 0.13126 | 0.0089572 | 0.0046891 | -0.088272 | 0.0044262 | 0.0015316 | 0.0056588 | 0.0034778 | -0.0015381 | 64.0457 | 64.1693 | 16.3879 | -57.4768 | 64.1647 | -58.7631 | -58.8272 | -51.4618 | 15.3671 | -58.9188 | 64.2151 | 64.1418 | -58.8776 | -58.9508 | -0.027466 | -0.091552 | -0.036621 | 122.905 | 1.2589 | 1.3504 | -0.15564 | -0.14191 | -0.21515 | 0.013733 | 7.2739 | -0.1831 | 0.032044 | -0.059509 | 122.9004 | 122.7814 | 75.1236 | -123.0286 | 122.9507 | 122.8775 | 74.1028 | -123.1522
1480.5156 | 123.1613 | -58.7219 | 64.1418 | -0.42267 | 0.020149 | 0.072072 | 0.07584 | 0.13255 | 0.0046848 | 0.0027665 | 0.033798 | 0.0020764 | 0.003668 | 0.0030954 | 0.0013416 | -0.00089726 | 64.0594 | 64.2975 | 16.3971 | -57.4493 | 64.1144 | -58.7814 | -58.8318 | -51.3565 | 15.4495 | -58.8272 | 64.1098 | 64.0686 | -58.8501 | -58.9279 | -0.059509 | -0.10986 | -0.027466 | 123.0194 | 1.2726 | 1.3824 | -0.082398 | -0.12817 | -0.20599 | -0.032044 | 7.3654 | -0.10529 | 0.10071 | -0.073242 | 122.8363 | 122.7814 | 75.119 | -122.9736 | 122.8317 | 122.7905 | 74.1714 | -123.0698
1481.5156 | 123.024 | -58.7402 | 64.2059 | -0.23956 | 0.025703 | 0.07314 | 0.075627 | 0.1334 | 0.0078892 | 0.0044755 | -0.065384 | 0.0042126 | 0.0015316 | 0.003309 | 0.0024096 | -0.0017517 | 64.0457 | 64.2242 | 16.3559 | -57.4631 | 64.1968 | -58.7769 | -58.8043 | -51.3565 | 15.3397 | -58.9279 | 64.2197 | 64.1281 | -58.8593 | -58.9417 | -0.036621 | -0.064087 | -0.009156 | 122.9645 | 1.2772 | 1.3412 | -0.16022 | -0.11902 | -0.20142 | 0.013733 | 7.3837 | -0.18768 | 0.013733 | -0.07782 | 122.937 | 122.7859 | 75.0961 | -123.0103 | 122.9599 | 122.8683 | 74.0799 | -123.1476
1482.5156 | 123.1522 | -58.7128 | 64.1602 | -0.13275 | 0.022285 | 0.072713 | 0.075627 | 0.13126 | 0.0072482 | 0.0038345 | -0.019608 | -0.00027337 | 0.0011044 | 0.0035226 | 0.0041186 | -0.0017517 | 64.0961 | 64.3204 | 16.4703 | -57.4173 | 64.1556 | -58.7402 | -58.8135 | -51.2329 | 15.4266 | -58.8364 | 64.1693 | 64.1006 | -58.8181 | -58.905 | -0.027465 | -0.10071 | -0.004577 | 123.0331 | 1.2955 | 1.3962 | -0.064087 | -0.10528 | -0.19226 | 0.009156 | 7.4799 | -0.1236 | 0.068664 | -0.059509 | 122.8683 | 122.8088 | 75.1831 | -122.9736 | 122.8821 | 122.8134 | 74.1394 | -123.0652
1483.5156 | 123.1247 | -58.7631 | 64.1144 | 0.18768 | 0.024208 | 0.069722 | 0.076268 | 0.13319 | 0.0089572 | 0.0019119 | 0.28557 | 0.0033582 | 0.0028134 | 0.0035226 | 0.0049732 | -0.00047006 | 64.0274 | 64.2426 | 16.4337 | -57.4539 | 64.0961 | -58.786 | -58.8547 | -51.21 | 15.3122 | -58.8867 | 64.1006 | 64.0228 | -58.8547 | -58.9691 | -0.022888 | -0.091552 | -0.018311 | 123.0057 | 1.3092 | 1.4008 | -0.086975 | -0.091552 | -0.20599 | -0.013733 | 7.5531 | -0.1236 | 0.082397 | -0.091553 | 122.8592 | 122.7905 | 75.1968 | -122.9691 | 122.8638 | 122.786 | 74.0753 | -123.0835
1484.5156 | 123.0927 | -58.6395 | 64.2517 | -0.15564 | 0.021858 | 0.070149 | 0.077336 | 0.13426 | 0.0061802 | 0.0049027 | -0.088272 | 0.0027172 | 0.0006772 | 0.0041634 | 0.0032642 | -0.0028199 | 64.1739 | 64.3524 | 16.4886 | -57.3166 | 64.2105 | -58.6899 | -58.7357 | -51.0727 | 15.4358 | -58.7906 | 64.238 | 64.183 | -58.7311 | -58.8364 | -0.050354 | -0.096131 | -0.041199 | 122.9919 | 1.3229 | 1.4191 | -0.07782 | -0.091553 | -0.19684 | -0.013733 | 7.5668 | -0.15106 | 0.045777 | -0.068665 | 122.85 | 122.8134 | 75.1282 | -122.9874 | 122.8775 | 122.8226 | 74.0753 | -123.0881
1485.5156 | 123.0377 | -58.7082 | 64.2242 | -0.20142 | 0.023353 | 0.068868 | 0.077122 | 0.13618 | 0.0063938 | 0.0025529 | -0.0043486 | 0.0035718 | 0.0006772 | 0.005018 | 0.002837 | -0.0023927 | 64.0594 | 64.1098 | 16.2964 | -57.3898 | 64.2334 | -58.7585 | -58.8181 | -51.1093 | 15.2939 | -58.8913 | 64.2563 | 64.1418 | -58.8181 | -58.9096 | -0.050354 | -0.10986 | 0.009155 | 122.818 | 1.3184 | 1.4282 | -0.16479 | -0.10986 | -0.20142 | 0.032044 | 7.5989 | -0.1831 | 0.018311 | -0.082397 | 122.9416 | 122.7676 | 75.0046 | -123.0423 | 122.9645 | 122.85 | 74.0021 | -123.1338
1486.5156 | 123.0606 | -58.7494 | 64.1876 | -0.17853 | 0.022499 | 0.072072 | 0.076909 | 0.1334 | 0.006821 | 0.0038345 | -0.14168 | 0.0027172 | 0.0023862 | 0.0048044 | 0.0036914 | -0.0017517 | 64.0549 | 64.2426 | 16.4749 | -57.4265 | 64.151 | -58.786 | -58.8135 | -51.091 | 15.303 | -58.9142 | 64.1785 | 64.1006 | -58.8776 | -58.96 | -0.036621 | -0.064087 | -0.036621 | 122.9919 | 1.3229 | 1.387 | -0.13275 | -0.12817 | -0.21057 | -0.009155 | 7.6584 | -0.1648 | 0.045776 | -0.086975 | 122.9004 | 122.8043 | 75.2243 | -123.0011 | 122.9279 | 122.85 | 74.0524 | -123.1476
1487.5156 | 122.9691 | -58.7494 | 64.1876 | -0.1709 | 0.025917 | 0.071645 | 0.07819 | 0.12913 | 0.0081028 | 0.0053299 | -0.13405 | 0.0048534 | 0.0008908 | 0.0054452 | 0.0030506 | -0.0034607 | 63.9954 | 64.1739 | 16.3376 | -57.4539 | 64.1876 | -58.7814 | -58.8547 | -51.0223 | 15.2435 | -58.9554 | 64.2059 | 64.119 | -58.8409 | -58.96 | -0.032043 | -0.10529 | 0 | 122.9233 | 1.2955 | 1.4008 | -0.19226 | -0.091552 | -0.21057 | 0.018311 | 7.7271 | -0.20599 | 0.004578 | -0.068664 | 122.937 | 122.7448 | 75.087 | -123.0423 | 122.9553 | 122.8683 | 73.9929 | -123.1476
1488.5156 | 123.1338 | -58.667 | 64.2105 | -0.14038 | 0.022499 | 0.073354 | 0.071568 | 0.1349 | 0.0059666 | 0.0029801 | 0.14061 | 0.0018628 | 0.0017454 | 0.0039498 | 0.0034778 | -0.0019653 | 64.0549 | 64.8102 | 16.658 | -57.4493 | 64.2288 | -58.699 | -58.7219 | -50.8072 | 15.4495 | -58.7585 | 64.1968 | 64.1464 | -58.7631 | -58.8638 | -0.032044 | -0.054932 | 0.018311 | 123.4772 | 1.2177 | 1.2726 | -0.15564 | -0.096131 | -0.19684 | -0.013733 | 7.8598 | -0.091553 | 0.10529 | -0.064087 | 122.8958 | 122.7219 | 75.325 | -122.9324 | 122.8638 | 122.8134 | 74.1165 | -123.0743
1489.5156 | 123.0103 | -58.7311 | 64.1968 | -0.15564 | 0.025062 | 0.070577 | 0.078404 | 0.1334 | 0.010025 | 0.0031937 | -0.28664 | 0.0033582 | 0.004736 | 0.0030954 | 0.003905 | -0.0026063 | 64.0228 | 64.1785 | 16.4108 | -57.3807 | 64.2242 | -58.754 | -58.7952 | -50.9445 | 15.1886 | -58.9371 | 64.2105 | 64.1144 | -58.8638 | -58.9417 | -0.022888 | -0.064087 | 0.027466 | 122.9095 | 1.3504 | 1.4145 | -0.17395 | -0.13275 | -0.21057 | 0.013733 | 7.7866 | -0.20599 | 0.004577 | -0.082397 | 122.9553 | 122.7539 | 75.1419 | -122.9919 | 122.9416 | 122.8455 | 73.9197 | -123.1384
1490.5156 | 123.1567 | -58.5617 | 64.3204 | -0.24719 | 0.023567 | 0.072927 | 0.071141 | 0.13126 | 0.0081028 | 0.0044755 | -0.027237 | 0.00229 | 0.001959 | 0.0045908 | 0.0034778 | -0.0038879 | 64.2517 | 64.4531 | 16.7038 | -57.1793 | 64.2838 | -58.58 | -58.6258 | -50.6195 | 15.4953 | -58.6533 | 64.3021 | 64.2334 | -58.6716 | -58.7723 | -0.01831 | -0.064086 | -0.036622 | 123.0148 | 1.3824 | 1.4465 | -0.068665 | -0.10986 | -0.21057 | -0.018311 | 7.9422 | -0.091552 | 0.11902 | -0.086976 | 122.8455 | 122.8134 | 75.2655 | -122.9462 | 122.8638 | 122.7951 | 74.057 | -123.0927
1491.5156 | 123.0789 | -58.6166 | 64.3478 | -0.2243 | 0.024635 | 0.072499 | 0.076268 | 0.13383 | 0.010025 | 0.0049027 | -0.088272 | 0.0046398 | 0.0017454 | 0.0056588 | 0.0043324 | -0.0066651 | 64.1327 | 64.2929 | 16.5756 | -57.3166 | 64.2883 | -58.6899 | -58.7311 | -50.7294 | 15.2985 | -58.8226 | 64.2838 | 64.2105 | -58.7723 | -58.8409 | -0.073242 | -0.11444 | -0.059509 | 122.9095 | 1.3 | 1.4145 | -0.21515 | -0.15564 | -0.2243 | -0.064087 | 7.8873 | -0.20599 | 0.01831 | -0.13733 | 122.905 | 122.7493 | 75.1923 | -123.0789 | 122.9004 | 122.8271 | 73.9151 | -123.1888
1492.5156 | 123.143 | -58.6121 | 64.2288 | -0.16327 | 0.020576 | 0.073354 | 0.075627 | 0.13511 | 0.0012668 | 0.0012711 | 0.28557 | 0.0035718 | -0.0010318 | 0.0045908 | 0.0047596 | -0.0034607 | 64.4394 | 64.0182 | 16.4246 | -57.2433 | 64.2288 | -58.6853 | -58.754 | -50.5829 | 15.4221 | -58.7219 | 64.2105 | 64.1373 | -58.7769 | -58.8638 | -0.073242 | -0.14191 | 0 | 122.6303 | 1.3687 | 1.5106 | 0.21057 | -0.16479 | -0.25177 | -0.018311 | 8.0292 | -0.10986 | 0.14191 | -0.091553 | 122.8409 | 123.0515 | 75.0366 | -122.9828 | 122.8226 | 122.7493 | 74.0341 | -123.0927
1493.5156 | 123.0789 | -58.5754 | 64.3616 | -0.19379 | 0.025062 | 0.070363 | 0.076268 | 0.13639 | 0.0095982 | 0.0023391 | -0.095902 | 0.0035718 | 0.003027 | 0.0026682 | 0.0043324 | -0.0017517 | 64.2288 | 64.4165 | 16.6992 | -57.1701 | 64.3524 | -58.6029 | -58.6716 | -50.5096 | 15.4037 | -58.7631 | 64.3662 | 64.2563 | -58.6853 | -58.7769 | -0.027466 | -0.096131 | -0.009155 | 122.9919 | 1.4053 | 1.5015 | -0.13275 | -0.10986 | -0.20142 | 0.004578 | 8.0658 | -0.18768 | 0.013732 | -0.10528 | 122.9279 | 122.8043 | 75.2747 | -123.0331 | 122.9416 | 122.8317 | 73.9792 | -123.1384
1494.5156 | 123.1613 | -58.58 | 64.2654 | -0.018311 | 0.020576 | 0.074636 | 0.076268 | 0.13084 | 0.00853 | 0.0029801 | 0.079574 | 0.003999 | 3.6404e-05 | 0.0045908 | 0.00048697 | -0.0021789 | 64.2059 | 64.3936 | 16.6809 | -57.193 | 64.2838 | -58.6349 | -58.699 | -50.4318 | 15.4404 | -58.6853 | 64.2929 | 64.1556 | -58.6899 | -58.7997 | -0.054932 | -0.11902 | 0.01831 | 122.9736 | 1.387 | 1.506 | -0.059509 | -0.10986 | -0.21973 | 0.027466 | 8.1482 | -0.10529 | 0.11444 | -0.10986 | 122.8638 | 122.7859 | 75.2609 | -122.9645 | 122.8729 | 122.7356 | 74.0204 | -123.0652
1495.5156 | 123.0377 | -58.6533 | 64.2563 | -0.18616 | 0.02549 | 0.072286 | 0.078831 | 0.13212 | 0.011307 | 0.0029801 | -0.11879 | 0.0025036 | 0.0017454 | 0.0054452 | 0.0047596 | -0.0028199 | 64.1876 | 64.3341 | 16.6351 | -57.2571 | 64.2426 | -58.6807 | -58.7219 | -50.4639 | 15.3534 | -58.8043 | 64.2792 | 64.1876 | -58.754 | -58.8547 | -0.027466 | -0.068665 | -0.013733 | 122.9874 | 1.3962 | 1.4648 | -0.068665 | -0.10071 | -0.20142 | 0.022888 | 8.1894 | -0.15106 | 0.050354 | -0.068665 | 122.8958 | 122.8409 | 75.2884 | -122.9782 | 122.9324 | 122.8409 | 74.0067 | -123.111
1496.5156 | 123.1476 | -58.6578 | 64.1373 | -0.02594 | 0.021004 | 0.071645 | 0.075413 | 0.13041 | 0.0076756 | 0.0029801 | 0.01091 | 0.0012218 | 0.0004636 | 0.0058724 | 0.0051868 | -0.0030335 | 64.151 | 64.357 | 16.6077 | -57.2708 | 64.1647 | -58.7265 | -58.7494 | -50.3815 | 15.4312 | -58.754 | 64.1693 | 64.0823 | -58.7723 | -58.8913 | -0.068664 | -0.091553 | 0.027466 | 123.0148 | 1.387 | 1.4786 | 0.013733 | -0.11444 | -0.23346 | 0.032044 | 8.2764 | -0.09613 | 0.13733 | -0.054932 | 122.8226 | 122.8088 | 75.2655 | -122.8867 | 122.8271 | 122.7402 | 74.0891 | -123.0286
1497.5156 | 123.0469 | -58.667 | 64.27 | -0.1709 | 0.024421 | 0.073781 | 0.075627 | 0.13297 | 0.010666 | 0.0053299 | -0.11879 | 0.0052808 | 0.0045224 | 0.005018 | 0.0024096 | -0.0049561 | 64.1098 | 64.2792 | 16.5482 | -57.2754 | 64.3204 | -58.699 | -58.7402 | -50.386 | 15.5273 | -58.6853 | 64.3478 | 64.2242 | -58.7494 | -58.9005 | -0.032044 | -0.073242 | 0.050354 | 122.9462 | 1.3916 | 1.4648 | -0.16022 | -0.082398 | -0.23346 | 0.077819 | 8.2809 | -0.018311 | 0.21515 | -0.045777 | 122.9874 | 122.7768 | 75.2151 | -123.0103 | 123.0148 | 122.8912 | 74.1943 | -123.1705
1498.5156 | 123.1522 | -58.6029 | 64.2609 | 0.50812 | 0.022712 | 0.072713 | 0.0752 | 0.13319 | 0.0081028 | 0.0055435 | -0.11879 | 0.0029308 | -0.0018862 | 0.0052316 | 0.0054004 | -0.00068366 | 64.2059 | 64.4028 | 16.6946 | -57.1655 | 64.2517 | -58.6441 | -58.6899 | -50.1984 | 15.477 | -58.6853 | 64.2426 | 64.151 | -58.7173 | -58.8181 | -0.041199 | -0.086975 | -0.009155 | 123.0057 | 1.4374 | 1.5244 | -0.054931 | -0.11444 | -0.21515 | -0.01831 | 8.4045 | -0.082398 | 0.13275 | -0.10986 | 122.8546 | 122.8088 | 75.2975 | -122.9507 | 122.8455 | 122.7539 | 74.0799 | -123.0789
1499.5156 | 123.1201 | -58.5342 | 64.4257 | -0.19379 | 0.025917 | 0.070149 | 0.078404 | 0.13233 | 0.0081028 | 0.0046891 | -0.13405 | 0.0044262 | 0.001959 | 0.0062998 | 0.0051868 | -0.0021789 | 64.2288 | 64.4028 | 16.6672 | -57.1289 | 64.3799 | -58.5983 | -58.6349 | -50.1526 | 15.4083 | -58.7448 | 64.3845 | 64.2975 | -58.6807 | -58.7723 | -0.064087 | -0.10071 | -0.045776 | 122.937 | 1.4053 | 1.506 | -0.19684 | -0.14648 | -0.23804 | -0.041199 | 8.3817 | -0.21057 | 0.027466 | -0.12817 | 122.9141 | 122.7631 | 75.2014 | -123.0606 | 122.9187 | 122.8317 | 73.9426 | -123.1979
1500.5156 | 123.1522 | -58.5342 | 64.3021 | -0.041199 | 0.022926 | 0.072499 | 0.075413 | 0.13361 | 0.0072482 | 0.0042619 | 0.064316 | 0.0031446 | -0.0008182 | 0.005018 | 0.0032642 | -0.0026063 | 64.2654 | 64.4531 | 16.7084 | -57.1106 | 64.2929 | -58.6029 | -58.6441 | -50.0015 | 15.5045 | -58.6487 | 64.3112 | 64.2242 | -58.6533 | -58.7631 | -0.068664 | -0.10986 | -0.009155 | 122.9874 | 1.4236 | 1.5335 | -0.036621 | -0.11902 | -0.22888 | 0.009155 | 8.5327 | -0.11444 | 0.11444 | -0.07782 | 122.8271 | 122.7997 | 75.2426 | -122.9462 | 122.8455 | 122.7585 | 74.0387 | -123.0652
1501.5156 | 123.0331 | -58.548 | 64.3799 | -0.20905 | 0.02848 | 0.071858 | 0.077763 | 0.13297 | 0.010453 | 0.0053299 | -0.065384 | 0.0050672 | 0.0015316 | 0.0045908 | 0.0041186 | -0.0023927 | 64.2517 | 64.4073 | 16.7084 | -57.1426 | 64.3616 | -58.5938 | -58.6624 | -50.0336 | 15.4037 | -58.7357 | 64.3936 | 64.2746 | -58.6899 | -58.7631 | -0.045776 | -0.11444 | -0.018311 | 122.9553 | 1.4053 | 1.5198 | -0.12817 | -0.14191 | -0.21515 | 0.013733 | 8.5144 | -0.18768 | 0.027466 | -0.10529 | 122.9095 | 122.7997 | 75.2563 | -123.0423 | 122.9416 | 122.8226 | 73.9517 | -123.143
1502.5156 | 123.1247 | -58.4747 | 64.3707 | -0.14038 | 0.02314 | 0.071431 | 0.081181 | 0.13575 | 0.011521 | 0.0053299 | -0.27138 | 0.0027172 | 0.0025998 | 0.0060862 | 0.0034778 | -0.0038879 | 64.1052 | 64.5996 | 16.8503 | -57.074 | 64.3524 | -58.5388 | -58.5846 | -49.8322 | 15.5777 | -58.5754 | 64.3753 | 64.27 | -58.6212 | -58.6945 | -0.064087 | -0.10986 | -0.018311 | 123.0743 | 1.4008 | 1.5106 | -0.2655 | -0.14648 | -0.21973 | 0.004577 | 8.6426 | -0.10071 | 0.11902 | -0.10071 | 122.8271 | 122.58 | 75.325 | -122.9553 | 122.85 | 122.7448 | 74.0524 | -123.0652
1503.5156 | 123.0286 | -58.6121 | 64.325 | -0.1709 | 0.02613 | 0.071858 | 0.076695 | 0.13511 | 0.011521 | 0.0061845 | -0.10353 | 0.0063488 | 0.0023862 | 0.0060862 | 0.0041186 | -0.00025626 | 64.2059 | 64.3707 | 16.6534 | -57.1838 | 64.3387 | -58.6304 | -58.6853 | -49.9329 | 15.3625 | -58.7585 | 64.3478 | 64.238 | -58.7311 | -58.8089 | -0.01831 | -0.073242 | 0.013733 | 122.9828 | 1.4282 | 1.5015 | -0.11902 | -0.11902 | -0.19684 | 0.022888 | 8.6792 | -0.14648 | 0.050354 | -0.086975 | 122.9507 | 122.818 | 75.2655 | -123.0103 | 122.9599 | 122.85 | 73.9746 | -123.1338
1504.5156 | 123.1018 | -58.4839 | 64.3845 | -0.16327 | 0.022499 | 0.07079 | 0.077977 | 0.13361 | 0.0095982 | 0.0055435 | -0.095902 | 0.0012218 | 0.0017454 | 0.0071542 | 0.0060412 | -0.0023927 | 64.325 | 64.5309 | 16.7725 | -57.0099 | 64.3707 | -58.5251 | -58.6166 | -49.7406 | 15.5365 | -58.5938 | 64.4257 | 64.2883 | -58.5892 | -58.7082 | -0.041198 | -0.13275 | -0.013732 | 123.0148 | 1.474 | 1.6068 | -0.059509 | -0.10528 | -0.2243 | 0.041199 | 8.7433 | -0.10986 | 0.11444 | -0.09613 | 122.8546 | 122.8088 | 75.2563 | -123.0011 | 122.9095 | 122.7722 | 74.0204 | -123.0927
1505.5156 | 123.0103 | -58.5022 | 64.444 | 0.073242 | 0.029121 | 0.070577 | 0.077763 | 0.13575 | 0.013016 | 0.0038345 | -0.10353 | 0.0059216 | 0.004736 | 0.0045908 | 0.0051868 | -0.00068366 | 64.3021 | 64.4394 | 16.713 | -57.0557 | 64.444 | -58.5342 | -58.6029 | -49.7086 | 15.4633 | -58.6761 | 64.4714 | 64.3433 | -58.5892 | -58.6945 | -0.032044 | -0.10071 | 0 | 122.9416 | 1.4465 | 1.5472 | -0.14191 | -0.086975 | -0.19226 | 0.027466 | 8.7936 | -0.17395 | 0.018311 | -0.10071 | 122.9462 | 122.8043 | 75.2151 | -123.0469 | 122.9736 | 122.8455 | 73.9655 | -123.1384
1506.5156 | 123.0972 | -58.5068 | 64.3982 | -0.15564 | 0.024421 | 0.074422 | 0.0752 | 0.1334 | 0.0072482 | 0.0053299 | -0.11116 | 0.0033582 | 0.0017454 | 0.0056588 | 0.004546 | -0.0013245 | 64.2883 | 64.5218 | 16.745 | -57.019 | 64.3753 | -58.5388 | -58.6166 | -49.6399 | 15.4907 | -58.6258 | 64.3936 | 64.2883 | -58.6304 | -58.7265 | -0.032043 | -0.10986 | -0.022888 | 123.0286 | 1.4877 | 1.5976 | -0.10986 | -0.1236 | -0.21973 | -0.004577 | 8.8669 | -0.11902 | 0.10071 | -0.10986 | 122.8821 | 122.7951 | 75.2518 | -123.0148 | 122.9004 | 122.7951 | 73.9975 | -123.1247
1507.5156 | 122.9919 | -58.4839 | 64.4302 | -0.19379 | 0.029976 | 0.071004 | 0.079045 | 0.13297 | 0.011307 | 0.0031937 | -0.088272 | 0.0052808 | 0.0025998 | 0.0054452 | 0.006255 | -0.0028199 | 64.2609 | 64.4302 | 16.6901 | -57.074 | 64.4165 | -58.548 | -58.6075 | -49.617 | 15.4404 | -58.6624 | 64.4394 | 64.3387 | -58.6304 | -58.7173 | -0.064087 | -0.1236 | -0.013733 | 122.9141 | 1.4099 | 1.5335 | -0.16937 | -0.14648 | -0.23346 | 0.009155 | 8.8669 | -0.17853 | 0.054931 | -0.091553 | 122.9004 | 122.7448 | 75.174 | -123.0377 | 122.9233 | 122.8226 | 73.9243 | -123.1476
1508.5156 | 123.1567 | -58.4152 | 64.4531 | 0.2182 | 0.021858 | 0.073354 | 0.074131 | 0.13105 | 0.0070346 | 0.0070389 | -0.11879 | 0.003999 | 0.0017454 | 0.0052316 | 0.0032642 | -0.00025626 | 64.3616 | 64.6133 | 16.864 | -56.9092 | 64.4257 | -58.4473 | -58.5159 | -49.3973 | 15.6326 | -58.5068 | 64.4257 | 64.3158 | -58.5159 | -58.6258 | -0.032044 | -0.10071 | -0.027466 | 123.0286 | 1.506 | 1.6067 | -0.091553 | -0.10071 | -0.21057 | -0.027466 | 9.0179 | -0.091553 | 0.11902 | -0.13733 | 122.8409 | 122.7768 | 75.2792 | -122.9691 | 122.8409 | 122.731 | 74.0479 | -123.0789
1509.5156 | 123.024 | -58.493 | 64.4257 | -0.23193 | 0.02613 | 0.072072 | 0.077336 | 0.13319 | 0.013016 | 0.0055435 | -0.11879 | 0.0048534 | 0.0023862 | 0.0060862 | 0.006255 | -0.0030335 | 64.27 | 64.4119 | 16.7358 | -57.0145 | 64.4302 | -58.5297 | -58.5938 | -49.4659 | 15.4312 | -58.6807 | 64.4669 | 64.3433 | -58.6121 | -58.6899 | -0.036621 | -0.10071 | 0.004578 | 122.905 | 1.4786 | 1.5793 | -0.15564 | -0.11902 | -0.19684 | 0.041199 | 9.0271 | -0.18768 | 0.009155 | -0.082397 | 122.9233 | 122.7631 | 75.2289 | -123.0194 | 122.9599 | 122.8363 | 73.9243 | -123.1155
1510.5156 | 123.0331 | -58.4885 | 64.4623 | -0.10986 | 0.025276 | 0.072713 | 0.077549 | 0.13511 | 0.0095982 | 0.0061845 | -0.14168 | 0.003999 | 0.0043088 | 0.0054452 | 0.0041186 | -0.0015381 | 64.2792 | 64.4714 | 16.8137 | -57.0053 | 64.476 | -58.5159 | -58.5663 | -49.2554 | 15.564 | -58.7631 | 64.5035 | 64.3616 | -58.6075 | -58.6853 | -0.027466 | -0.07782 | 0.013733 | 122.9599 | 1.4832 | 1.561 | -0.18311 | -0.11902 | -0.19684 | 0.041199 | 9.2331 | -0.27466 | -0.07782 | -0.10071 | 122.9645 | 122.7676 | 75.3021 | -123.0286 | 122.9919 | 122.85 | 74.0524 | -123.1476
1511.5156 | 123.0835 | -58.4885 | 64.4211 | -0.14038 | 0.029121 | 0.068654 | 0.077977 | 0.13297 | 0.012162 | 0.0081071 | -0.10353 | 0.0069898 | 0.003027 | 0.0060862 | 0.0068958 | -0.0023927 | 64.3066 | 64.4577 | 16.7725 | -56.9778 | 64.4714 | -58.5159 | -58.5938 | -49.324 | 15.4678 | -58.6304 | 64.4669 | 64.3433 | -58.5938 | -58.7082 | -0.027466 | -0.10529 | 0.050354 | 122.9462 | 1.5106 | 1.6159 | -0.11444 | -0.10529 | -0.21973 | 0.045776 | 9.1644 | -0.14191 | 0.07782 | -0.07782 | 122.9599 | 122.7951 | 75.2609 | -123.0148 | 122.9553 | 122.8317 | 73.9563 | -123.1293
1512.5156 | 123.0423 | -58.4976 | 64.4302 | -0.11749 | 0.025276 | 0.07079 | 0.075413 | 0.13447 | 0.0087436 | 0.0051163 | -0.12642 | 0.0063488 | 0.0015316 | 0.0082224 | 0.006255 | -0.0011109 | 64.2426 | 64.4485 | 16.6855 | -57.0007 | 64.4348 | -58.5114 | -58.5663 | -49.3423 | 15.4495 | -58.6853 | 64.4806 | 64.3524 | -58.6212 | -58.699 | -0.013733 | -0.068664 | 0.004577 | 122.9462 | 1.4969 | 1.5656 | -0.18768 | -0.1236 | -0.20142 | 0.050354 | 9.1553 | -0.18768 | 0.013733 | -0.07782 | 122.9324 | 122.7402 | 75.1831 | -122.9965 | 122.9782 | 122.85 | 73.9471 | -123.1293
1513.5156 | 123.0698 | -58.3969 | 64.5035 | -0.16327 | 0.030403 | 0.070363 | 0.074772 | 0.1334 | 0.013657 | 0.0061845 | -0.088272 | 0.0054944 | 0.0040952 | 0.006727 | 0.0064686 | -0.0026063 | 64.3799 | 64.5584 | 16.8137 | -56.8817 | 64.5355 | -58.4427 | -58.4976 | -49.1226 | 15.5365 | -58.5251 | 64.5264 | 64.4485 | -58.5205 | -58.6212 | -0.045776 | -0.10071 | 0.032043 | 122.9553 | 1.5152 | 1.6159 | -0.1236 | -0.1236 | -0.2243 | 0.022888 | 9.2743 | -0.12817 | 0.096131 | -0.054932 | 122.9324 | 122.7768 | 75.2106 | -123.0011 | 122.9233 | 122.8455 | 73.9334 | -123.1247
1514.5156 | 123.0652 | -58.4793 | 64.4485 | -0.18616 | 0.027412 | 0.07079 | 0.074559 | 0.13212 | 0.0089572 | 0.0063981 | -0.073013 | 0.0033582 | -0.000391 | 0.0062998 | 0.0032642 | -0.00047006 | 64.3112 | 64.5355 | 16.8777 | -56.9458 | 64.4073 | -58.5114 | -58.5617 | -49.1272 | 15.509 | -58.5892 | 64.4577 | 64.357 | -58.58 | -58.6761 | -0.032044 | -0.082398 | -0.041198 | 123.0148 | 1.5335 | 1.6159 | -0.13733 | -0.10071 | -0.19684 | 0.009156 | 9.3521 | -0.10986 | 0.086975 | -0.091552 | 122.8867 | 122.7905 | 75.3571 | -123.0103 | 122.937 | 122.8363 | 73.9883 | -123.1247
1515.5156 | 123.0606 | -58.5663 | 64.3524 | -0.20142 | 0.031257 | 0.072499 | 0.079899 | 0.13191 | 0.011948 | 0.0063981 | -0.095902 | 0.0052808 | 0.0038816 | 0.0069406 | 0.0047596 | -0.00068366 | 64.1968 | 64.3524 | 16.7862 | -57.0236 | 64.3845 | -58.6029 | -58.6716 | -49.173 | 15.3854 | -58.7357 | 64.3982 | 64.2883 | -58.6899 | -58.7814 | -0.036621 | -0.10529 | 0.032043 | 122.9187 | 1.5427 | 1.6479 | -0.15564 | -0.1236 | -0.21515 | 0.045776 | 9.3933 | -0.16937 | 0.045776 | -0.064087 | 122.9507 | 122.7631 | 75.3525 | -123.024 | 122.9645 | 122.8546 | 73.9517 | -123.1338
1516.5156 | 123.0377 | -58.5617 | 64.3524 | -0.14038 | 0.026771 | 0.071645 | 0.077977 | 0.13361 | 0.0081028 | 0.0061845 | 0.094833 | 0.0069898 | 0.003668 | 0.0060862 | 0.0047596 | -0.0011109 | 64.1785 | 64.5309 | 17.0654 | -57.0831 | 64.4073 | -58.5617 | -58.6395 | -49.1455 | 15.4037 | -58.7219 | 64.389 | 64.27 | -58.6853 | -58.7677 | 0 | -0.077819 | 0.054932 | 123.0927 | 1.4786 | 1.5564 | -0.17395 | -0.1236 | -0.20599 | 0.036621 | 9.4162 | -0.16022 | 0.045776 | -0.082397 | 122.9691 | 122.7402 | 75.6271 | -122.9919 | 122.9507 | 122.8317 | 73.9655 | -123.1201
1517.5156 | 123.0835 | -58.5434 | 64.3707 | 0.81329 | 0.031471 | 0.072072 | 0.078618 | 0.13404 | 0.014298 | 0.0068253 | 0.033798 | 0.0065624 | 0.0040952 | 0.0041634 | 0.0060412 | -0.0013245 | 64.2746 | 64.4165 | 16.7816 | -56.9778 | 64.4119 | -58.5709 | -58.6258 | -49.0082 | 15.3809 | -58.6716 | 64.4119 | 64.2792 | -58.6533 | -58.7402 | -0.027466 | -0.082397 | 0.041198 | 122.9599 | 1.5656 | 1.6479 | -0.096131 | -0.10986 | -0.19684 | 0.041198 | 9.5352 | -0.12817 | 0.068664 | -0.091553 | 122.9553 | 122.818 | 75.325 | -122.9965 | 122.9553 | 122.8226 | 73.9243 | -123.111
1518.5156 | 123.0423 | -58.493 | 64.4531 | -0.17853 | 0.027839 | 0.072499 | 0.075627 | 0.13191 | 0.0093846 | 0.0051163 | -0.12642 | 0.0063488 | 0.001318 | 0.0071542 | 0.0043324 | -0.0013245 | 64.2563 | 64.4119 | 16.7679 | -56.9641 | 64.444 | -58.5342 | -58.5846 | -48.9532 | 15.3763 | -58.6533 | 64.444 | 64.3524 | -58.6075 | -58.699 | -0.041199 | -0.091553 | -0.009155 | 122.905 | 1.5289 | 1.6205 | -0.19684 | -0.11444 | -0.20599 | -0.009155 | 9.5398 | -0.16022 | 0.045777 | -0.10071 | 122.937 | 122.7493 | 75.2609 | -123.0377 | 122.937 | 122.8455 | 73.8693 | -123.1522
1519.5156 | 123.0423 | -58.4747 | 64.4073 | -0.079346 | 0.032112 | 0.070363 | 0.074772 | 0.13532 | 0.012162 | 0.0049027 | -0.073013 | 0.0052808 | 0.0008908 | 0.0069406 | 0.0066822 | -0.00089726 | 64.4989 | 64.4531 | 16.7953 | -56.9046 | 64.4348 | -58.5114 | -58.5754 | -48.8342 | 15.39 | -58.6395 | 64.3936 | 64.3524 | -58.5983 | -58.7036 | -0.036622 | -0.10071 | 0.027465 | 122.9279 | 1.5701 | 1.6708 | 0.091552 | -0.1236 | -0.22888 | -0.013733 | 9.6405 | -0.16479 | 0.064087 | -0.054932 | 122.9095 | 122.9736 | 75.2701 | -122.9828 | 122.8683 | 122.8271 | 73.8647 | -123.111
1520.5156 | 123.056 | -58.5297 | 64.3982 | -0.14801 | 0.02848 | 0.071218 | 0.074345 | 0.13191 | 0.010453 | 0.0061845 | -0.095902 | 0.0042126 | 0.001318 | 0.0056588 | 0.0054004 | 0.00059814 | 64.238 | 64.3799 | 16.6763 | -56.9824 | 64.4073 | -58.58 | -58.6166 | -48.8708 | 15.3397 | -58.6807 | 64.4302 | 64.3204 | -58.6441 | -58.7128 | -0.050354 | -0.086975 | 0.009156 | 122.9095 | 1.5472 | 1.6342 | -0.16022 | -0.11444 | -0.18311 | 0.032044 | 9.6588 | -0.15106 | 0.032044 | -0.077819 | 122.937 | 122.7676 | 75.206 | -123.0148 | 122.9599 | 122.85 | 73.8693 | -123.111
1521.5156 | 123.0881 | -58.4381 | 64.444 | -0.17853 | 0.032326 | 0.072072 | 0.079686 | 0.13212 | 0.011093 | 0.0053299 | -0.065384 | 0.0048534 | 0.0032406 | 0.0054452 | 0.0036914 | -0.0023927 | 64.3158 | 64.4714 | 16.8869 | -56.8954 | 64.4669 | -58.4885 | -58.5526 | -48.7015 | 15.4495 | -58.5846 | 64.4806 | 64.3845 | -58.5526 | -58.6945 | -0.050354 | -0.11444 | 0.022888 | 122.9095 | 1.5427 | 1.6571 | -0.12817 | -0.11444 | -0.25635 | 0.036621 | 9.7366 | -0.14648 | 0.10986 | -0.05951 | 122.905 | 122.7539 | 75.325 | -122.9965 | 122.9187 | 122.8226 | 73.8876 | -123.1384
1522.5156 | 122.9874 | -58.4061 | 64.4897 | -0.28534 | 0.027412 | 0.072927 | 0.076054 | 0.13596 | 0.0095982 | 0.0066117 | -0.073013 | 0.0063488 | 0.003668 | 0.0058724 | 0.002837 | -0.0026063 | 64.325 | 64.5218 | 16.7999 | -56.8726 | 64.5172 | -58.4473 | -58.5159 | -48.6145 | 15.7379 | -58.6487 | 64.5676 | 64.4485 | -58.548 | -58.6212 | -0.041199 | -0.10986 | 0.027466 | 122.9279 | 1.5335 | 1.6434 | -0.16479 | -0.14191 | -0.21515 | 0.07782 | 9.7916 | -0.24262 | -0.027466 | -0.041199 | 122.9233 | 122.731 | 75.206 | -123.0057 | 122.9736 | 122.8546 | 74.144 | -123.111
1523.5156 | 123.0515 | -58.4564 | 64.4302 | -0.086975 | 0.032539 | 0.070577 | 0.079686 | 0.13361 | 0.014084 | 0.0051163 | 0.064316 | 0.0097668 | 0.0053768 | 0.0054452 | 0.0060412 | -0.0017517 | 64.3433 | 64.4897 | 16.745 | -56.8726 | 64.444 | -58.4976 | -58.5388 | -48.5733 | 15.5365 | -58.5892 | 64.4714 | 64.357 | -58.5663 | -58.6441 | -0.041199 | -0.082397 | 0.013733 | 122.9462 | 1.5839 | 1.6663 | -0.086975 | -0.10986 | -0.18768 | 0.041199 | 9.8831 | -0.13275 | 0.054932 | -0.073242 | 122.9004 | 122.7997 | 75.2014 | -122.9691 | 122.9279 | 122.8134 | 73.9929 | -123.0743
1524.5156 | 123.0789 | -58.4427 | 64.4623 | -0.12512 | 0.031685 | 0.071431 | 0.077977 | 0.13383 | 0.011307 | 0.0068253 | -0.11116 | 0.0063488 | 0.003027 | 0.0058724 | 0.0064686 | -0.0011109 | 64.3295 | 64.4943 | 16.8228 | -56.8405 | 64.5081 | -58.4747 | -58.5114 | -48.5138 | 15.509 | -58.5617 | 64.5035 | 64.4531 | -58.548 | -58.6166 | -0.032043 | -0.068665 | 0.045777 | 122.937 | 1.6022 | 1.6708 | -0.13275 | -0.10529 | -0.17395 | 0.041199 | 9.9289 | -0.11902 | 0.054931 | -0.009155 | 122.9507 | 122.7722 | 75.2655 | -122.9736 | 122.9462 | 122.8958 | 73.9517 | -123.0789
1525.5156 | 123.024 | -58.4244 | 64.4714 | -0.010681 | 0.032326 | 0.070363 | 0.080327 | 0.13532 | 0.011734 | 0.0074661 | 0.033798 | 0.0063488 | 0.0038816 | 0.0060862 | 0.0071094 | -0.0021789 | 64.3707 | 64.5309 | 16.8457 | -56.8222 | 64.4806 | -58.4656 | -58.5159 | -48.4406 | 15.5319 | -58.5754 | 64.5126 | 64.4028 | -58.5342 | -58.6441 | -0.041199 | -0.091553 | 0.009155 | 122.9553 | 1.6022 | 1.6937 | -0.10071 | -0.10986 | -0.21973 | 0.041198 | 9.9838 | -0.15106 | 0.068665 | -0.068665 | 122.905 | 122.7951 | 75.2701 | -122.9874 | 122.937 | 122.8271 | 73.9563 | -123.1155
1526.5156 | 123.0835 | -58.4198 | 64.4897 | -0.14801 | 0.030403 | 0.072499 | 0.079686 | 0.13596 | 0.010666 | 0.0063981 | -0.095902 | 0.0076306 | 0.0017454 | 0.0082224 | 0.0030506 | 0.00038454 | 64.3433 | 64.5035 | 16.8182 | -56.8222 | 64.4897 | -58.4564 | -58.5251 | -48.3719 | 15.5594 | -58.548 | 64.5218 | 64.4257 | -58.5205 | -58.6349 | -0.036621 | -0.10528 | 0 | 122.9233 | 1.5976 | 1.7029 | -0.14648 | -0.10071 | -0.21515 | 0.032044 | 10.0479 | -0.12817 | 0.086975 | -0.064087 | 122.9095 | 122.7631 | 75.238 | -123.0148 | 122.9416 | 122.8455 | 73.9792 | -123.1247
1527.5156 | 123.0515 | -58.4473 | 64.4714 | -0.048828 | 0.034035 | 0.069081 | 0.077977 | 0.1334 | 0.013871 | 0.0063981 | 0.01091 | 0.0089124 | 0.003668 | 0.0073678 | 0.006255 | -0.0021789 | 64.3707 | 64.4989 | 16.8182 | -56.8405 | 64.4531 | -58.4702 | -58.5251 | -48.3215 | 15.5182 | -58.58 | 64.476 | 64.3982 | -58.548 | -58.6441 | -0.022888 | -0.077819 | -0.018311 | 122.9462 | 1.6068 | 1.6846 | -0.10071 | -0.10071 | -0.19684 | 0.004577 | 10.1257 | -0.13275 | 0.064087 | -0.073243 | 122.9004 | 122.818 | 75.2655 | -122.9965 | 122.9233 | 122.8455 | 73.9655 | -123.1155
1528.5156 | 123.0469 | -58.3969 | 64.5401 | -0.24719 | 0.02848 | 0.072713 | 0.07584 | 0.13511 | 0.00853 | 0.0029801 | -0.050125 | 0.0061352 | 0.003668 | 0.0058724 | 0.0036914 | 0.0012389 | 64.3707 | 64.5035 | 16.8411 | -56.7993 | 64.5355 | -58.4152 | -58.4885 | -48.2346 | 15.564 | -58.5388 | 64.563 | 64.4943 | -58.5159 | -58.58 | -0.01831 | -0.091552 | -0.004578 | 122.9004 | 1.5976 | 1.6891 | -0.16937 | -0.11902 | -0.1831 | 0.022888 | 10.1624 | -0.14191 | 0.041199 | -0.045776 | 122.9324 | 122.7676 | 75.238 | -123.0286 | 122.9599 | 122.8912 | 73.9609 | -123.1201
1529.5156 | 123.0972 | -58.3191 | 64.5996 | -0.11749 | 0.032966 | 0.07079 | 0.079045 | 0.13532 | 0.013871 | 0.0091751 | -0.080643 | 0.0061352 | 0.004736 | 0.0062998 | 0.0051868 | -0.0023927 | 64.4669 | 64.6179 | 16.9235 | -56.6895 | 64.6088 | -58.3374 | -58.4015 | -48.0835 | 15.6647 | -58.4518 | 64.595 | 64.5355 | -58.461 | -58.5388 | -0.01831 | -0.082397 | 0.009156 | 122.937 | 1.6296 | 1.712 | -0.13275 | -0.14191 | -0.21973 | -0.004577 | 10.2356 | -0.13275 | 0.086975 | -0.064087 | 122.9279 | 122.7859 | 75.2426 | -123.0011 | 122.9141 | 122.8546 | 73.9838 | -123.1384
1530.5156 | 123.0652 | -58.4015 | 64.5676 | -0.12512 | 0.030617 | 0.071858 | 0.07584 | 0.13703 | 0.010025 | 0.0055435 | -0.057755 | 0.0061352 | 0.003027 | 0.008436 | 0.0054004 | -4.2662e-05 | 64.3845 | 64.5264 | 16.8961 | -56.7902 | 64.5401 | -58.4015 | -58.4747 | -48.1155 | 15.6235 | -58.5068 | 64.563 | 64.4852 | -58.5251 | -58.5938 | 0 | -0.073242 | -0.027466 | 122.9279 | 1.6113 | 1.6846 | -0.18311 | -0.1236 | -0.19226 | -0.004578 | 10.2859 | -0.10529 | 0.086975 | -0.082398 | 122.9416 | 122.7859 | 75.2975 | -123.0423 | 122.9645 | 122.8867 | 74.025 | -123.1613
1531.5156 | 123.0515 | -58.3878 | 64.5309 | -0.0030518 | 0.033394 | 0.070363 | 0.078404 | 0.13319 | 0.01323 | 0.0091751 | 0.14824 | 0.0089124 | 0.0028134 | 0.0080088 | 0.0064686 | -4.2662e-05 | 64.4073 | 64.5401 | 16.9281 | -56.7764 | 64.5172 | -58.4061 | -58.4839 | -48.0423 | 15.5594 | -58.5434 | 64.563 | 64.4577 | -58.4839 | -58.5892 | -0.018311 | -0.096131 | -0.013733 | 122.9279 | 1.6113 | 1.7075 | -0.1236 | -0.096131 | -0.20142 | 0.032043 | 10.3455 | -0.15564 | 0.045776 | -0.073242 | 122.905 | 122.7951 | 75.3159 | -123.0148 | 122.9507 | 122.8455 | 73.9471 | -123.1201
1532.5156 | 123.0606 | -58.3923 | 64.4989 | -0.14801 | 0.032326 | 0.071858 | 0.07819 | 0.1334 | 0.011093 | 0.0046891 | -0.080643 | 0.0059216 | 0.0038816 | 0.005018 | 0.0041186 | 0.00059814 | 64.3799 | 64.5309 | 16.9327 | -56.7902 | 64.5218 | -58.4244 | -58.4885 | -47.9691 | 15.6189 | -58.5205 | 64.5493 | 64.4577 | -58.5022 | -58.5892 | -0.032043 | -0.09613 | 0.022889 | 122.9233 | 1.6022 | 1.6983 | -0.11902 | -0.10986 | -0.19684 | 0.050354 | 10.4233 | -0.12817 | 0.068664 | -0.041198 | 122.9141 | 122.7722 | 75.325 | -122.9874 | 122.9416 | 122.85 | 74.0112 | -123.0881
1533.5156 | 123.0377 | -58.4198 | 64.4714 | 0.0045777 | 0.033821 | 0.070149 | 0.079686 | 0.13404 | 0.014298 | 0.0061845 | 0.071945 | 0.0093396 | 0.004736 | 0.0071542 | 0.0079638 | 0.00017094 | 64.389 | 64.4989 | 16.8961 | -56.8085 | 64.4806 | -58.4564 | -58.5068 | -47.9279 | 15.5457 | -58.5663 | 64.5035 | 64.444 | -58.5342 | -58.6487 | -0.036621 | -0.086975 | 0.009155 | 122.9187 | 1.6113 | 1.6983 | -0.082398 | -0.11444 | -0.22888 | 0.032043 | 10.4919 | -0.14648 | 0.082398 | -0.027466 | 122.9004 | 122.8088 | 75.3159 | -122.9782 | 122.9233 | 122.8638 | 73.9655 | -123.1201
1534.5156 | 123.0377 | -58.461 | 64.4577 | -0.064087 | 0.034675 | 0.07079 | 0.076481 | 0.13511 | 0.013657 | 0.0055435 | 0.056686 | 0.0069898 | 0.0045224 | 0.005018 | 0.0060412 | -0.0011109 | 64.3524 | 64.476 | 16.8549 | -56.8497 | 64.4394 | -58.4839 | -58.5617 | -47.9279 | 15.5273 | -58.6075 | 64.4714 | 64.3936 | -58.5892 | -58.6761 | -0.022888 | -0.10071 | -0.018311 | 122.937 | 1.6113 | 1.712 | -0.10529 | -0.12817 | -0.21515 | 0.013733 | 10.5331 | -0.14648 | 0.068664 | -0.064087 | 122.9004 | 122.8134 | 75.3159 | -123.0194 | 122.9324 | 122.8546 | 73.9883 | -123.1338
1535.5156 | 123.0698 | -58.5434 | 64.3524 | -0.094604 | 0.033821 | 0.069081 | 0.079899 | 0.13361 | 0.012589 | 0.0070389 | -0.027237 | 0.0086988 | 0.0051632 | 0.006727 | 0.0047596 | -0.0013245 | 64.238 | 64.3662 | 16.658 | -56.9321 | 64.3433 | -58.5983 | -58.6533 | -47.9233 | 15.2527 | -58.7036 | 64.3341 | 64.3204 | -58.667 | -58.754 | -0.054932 | -0.10986 | -0.009155 | 122.9095 | 1.6113 | 1.7212 | -0.11444 | -0.1236 | -0.21057 | -0.018311 | 10.6201 | -0.16022 | 0.050354 | -0.032043 | 122.8867 | 122.7814 | 75.2014 | -123.0057 | 122.8775 | 122.8638 | 73.7961 | -123.1064
1536.5156 | 123.0057 | -58.6349 | 64.3112 | -0.25482 | 0.026558 | 0.071218 | 0.075413 | 0.13297 | 0.0095982 | 0.0040481 | -0.050125 | 0.0065624 | 0.0025998 | 0.0082224 | 0.0034778 | 0.0016663 | 64.1144 | 64.2517 | 16.6855 | -57.0145 | 64.2792 | -58.6853 | -58.7494 | -48.0148 | 15.3854 | -58.7814 | 64.3295 | 64.2426 | -58.7448 | -58.8135 | -0.050354 | -0.11444 | -0.032043 | 122.8867 | 1.6205 | 1.7349 | -0.19684 | -0.10986 | -0.17853 | 0.018311 | 10.6201 | -0.14648 | 0.032044 | -0.068664 | 122.9141 | 122.7493 | 75.3204 | -123.0606 | 122.9645 | 122.8775 | 74.0204 | -123.1247
1537.5156 | 123.0606 | -58.5846 | 64.3112 | -0.52948 | 0.032966 | 0.069509 | 0.077549 | 0.13297 | 0.014084 | 0.0070389 | 0.094833 | 0.0080578 | 0.0038816 | 0.0082224 | 0.006255 | -0.0028199 | 64.2105 | 64.3662 | 16.8411 | -56.9366 | 64.3433 | -58.5846 | -58.6624 | -47.8455 | 15.4358 | -58.7036 | 64.3433 | 64.2792 | -58.6945 | -58.8089 | 0 | -0.07782 | 0.032044 | 122.9507 | 1.6479 | 1.7258 | -0.10071 | -0.10986 | -0.2243 | 0.032044 | 10.7391 | -0.11902 | 0.10529 | -0.032043 | 122.9279 | 122.7951 | 75.4257 | -122.9736 | 122.9279 | 122.8638 | 74.0204 | -123.1201
1538.5156 | 123.0743 | -58.5938 | 64.3387 | -0.14801 | 0.031044 | 0.071645 | 0.07819 | 0.1349 | 0.012375 | 0.0049027 | -0.065384 | 0.0082714 | 0.003668 | 0.0062998 | 0.005614 | 0.0016663 | 64.2105 | 64.3478 | 16.8045 | -56.9321 | 64.3158 | -58.6258 | -58.6899 | -47.7997 | 15.477 | -58.7082 | 64.3433 | 64.2517 | -58.699 | -58.7997 | -0.032043 | -0.09613 | -0.022888 | 122.9416 | 1.6617 | 1.7578 | -0.12817 | -0.10529 | -0.20599 | 0.004578 | 10.7941 | -0.11444 | 0.091553 | -0.086975 | 122.9095 | 122.8043 | 75.3983 | -123.0286 | 122.937 | 122.8455 | 74.0707 | -123.1384
1539.5312 | 123.0927 | -58.5297 | 64.2838 | 0.13428 | 0.02848 | 0.073995 | 0.076268 | 0.13084 | 0.007462 | 0.0040481 | 0.25505 | 0.0054944 | 0.0028134 | 0.0056588 | 0.0032642 | 0.0010253 | 64.183 | 64.3845 | 16.8457 | -56.9138 | 64.3066 | -58.5754 | -58.6166 | -47.7081 | 15.509 | -58.5434 | 64.3478 | 64.3158 | -58.6624 | -58.7631 | -0.045776 | -0.086975 | 0.022889 | 122.9141 | 1.6159 | 1.7029 | -0.10071 | -0.13275 | -0.23346 | 0.064087 | 10.8215 | -0.013733 | 0.21973 | 0.032044 | 122.8363 | 122.7127 | 75.3754 | -122.9004 | 122.8775 | 122.8455 | 74.0387 | -123.0469
1540.5156 | 123.0652 | -58.5983 | 64.3158 | -0.14038 | 0.031257 | 0.071645 | 0.076909 | 0.13361 | 0.013871 | 0.0051163 | -0.13405 | 0.0076306 | 0.0032406 | 0.0090768 | 0.0079638 | -0.0019653 | 64.1785 | 64.2883 | 16.7175 | -56.9641 | 64.3158 | -58.6395 | -58.699 | -47.6944 | 15.4312 | -58.7265 | 64.3204 | 64.238 | -58.7357 | -58.8226 | -0.041198 | -0.10071 | 0 | 122.8867 | 1.6342 | 1.7349 | -0.13733 | -0.13733 | -0.2243 | 0.004578 | 10.9039 | -0.12817 | 0.096131 | -0.07782 | 122.9141 | 122.7768 | 75.3159 | -123.0148 | 122.9187 | 122.8363 | 74.0295 | -123.1384
1541.5156 | 123.0286 | -58.5983 | 64.2929 | -0.094604 | 0.033607 | 0.069509 | 0.07819 | 0.13404 | 0.013871 | 0.0061845 | 0.11009 | 0.011049 | 0.0043088 | 0.0080088 | 0.0071094 | -0.0013245 | 64.2334 | 64.3478 | 16.7496 | -56.9504 | 64.2975 | -58.5938 | -58.6761 | -47.6028 | 15.4404 | -58.7357 | 64.3387 | 64.2563 | -58.7082 | -58.8089 | 0.004578 | -0.077819 | 0.004577 | 122.9462 | 1.648 | 1.7258 | -0.05951 | -0.10986 | -0.21057 | 0.045776 | 10.9955 | -0.13733 | 0.073242 | -0.036621 | 122.8958 | 122.8317 | 75.3479 | -122.9691 | 122.937 | 122.8546 | 74.0387 | -123.1018
1542.5156 | 123.0469 | -58.4885 | 64.4257 | -0.20142 | 0.029121 | 0.07079 | 0.083317 | 0.13319 | 0.012589 | 0.0068253 | -0.19508 | 0.0076306 | 0.0053768 | 0.0075814 | 0.003905 | 0.0012389 | 64.151 | 64.4394 | 16.7541 | -56.8771 | 64.4485 | -58.5526 | -58.6075 | -47.5021 | 15.5182 | -58.6487 | 64.4806 | 64.3799 | -58.6441 | -58.7173 | -0.064087 | -0.11902 | 0.022888 | 122.9279 | 1.6113 | 1.7303 | -0.27466 | -0.15564 | -0.22888 | 0.054932 | 10.9863 | -0.16022 | 0.068664 | -0.045776 | 122.937 | 122.6395 | 75.2426 | -123.0331 | 122.9691 | 122.8683 | 74.0067 | -123.143
1543.5156 | 123.0515 | -58.5434 | 64.3799 | -0.14801 | 0.033394 | 0.073781 | 0.081181 | 0.13426 | 0.014298 | 0.0072525 | -0.095902 | 0.0086988 | 0.0051632 | 0.007795 | 0.0064686 | -0.00089726 | 64.2609 | 64.4028 | 16.7313 | -56.8954 | 64.3845 | -58.548 | -58.6395 | -47.4289 | 15.5228 | -58.6578 | 64.4119 | 64.3112 | -58.667 | -58.7402 | -0.004578 | -0.09613 | 0.004577 | 122.9462 | 1.6479 | 1.7441 | -0.11902 | -0.1236 | -0.19684 | 0.032043 | 11.1145 | -0.11444 | 0.082397 | -0.068665 | 122.9279 | 122.8043 | 75.2747 | -123.0194 | 122.9553 | 122.8546 | 74.0662 | -123.1201
1544.5156 | 122.9828 | -58.4839 | 64.4577 | 0.09613 | 0.035743 | 0.070577 | 0.079258 | 0.13319 | 0.014511 | 0.0066117 | 0.18639 | 0.010408 | 0.0058042 | 0.0097176 | 0.0081776 | -0.0011109 | 64.3066 | 64.3982 | 16.7541 | -56.8314 | 64.4623 | -58.4839 | -58.5526 | -47.3419 | 15.5319 | -58.6487 | 64.476 | 64.4257 | -58.5846 | -58.6945 | 0 | -0.068664 | 0.004577 | 122.8821 | 1.6525 | 1.7212 | -0.15106 | -0.10071 | -0.21057 | 0.01831 | 11.142 | -0.16479 | 0.045776 | -0.032044 | 122.9462 | 122.7905 | 75.238 | -123.0103 | 122.9599 | 122.9095 | 74.0158 | -123.1522
1545.5156 | 123.056 | -58.5205 | 64.3799 | 0.0045777 | 0.032966 | 0.071004 | 0.078404 | 0.13062 | 0.014084 | 0.0070389 | 0.094833 | 0.010621 | 0.0060178 | 0.0075814 | 0.0064686 | -4.2662e-05 | 64.2746 | 64.3799 | 16.7404 | -56.8634 | 64.3753 | -58.5526 | -58.58 | -47.3007 | 15.5228 | -58.6761 | 64.389 | 64.3387 | -58.6258 | -58.7631 | -0.032043 | -0.059509 | -0.004578 | 122.9004 | 1.6571 | 1.7166 | -0.10529 | -0.10529 | -0.24262 | 0.009155 | 11.2198 | -0.15564 | 0.086976 | -0.041199 | 122.8958 | 122.7951 | 75.2609 | -122.9599 | 122.9095 | 122.8592 | 74.0433 | -123.143
1546.5156 | 123.056 | -58.5571 | 64.3433 | -0.14038 | 0.033394 | 0.071218 | 0.074772 | 0.13468 | 0.012802 | 0.0070389 | -0.11116 | 0.008485 | 0.0028134 | 0.006727 | 0.006255 | -0.0017517 | 64.2105 | 64.3524 | 16.7084 | -56.8909 | 64.3845 | -58.5892 | -58.6304 | -47.287 | 15.5411 | -58.6716 | 64.3799 | 64.3112 | -58.667 | -58.7585 | -0.032043 | -0.073242 | 0.041198 | 122.9095 | 1.6663 | 1.7395 | -0.13275 | -0.10986 | -0.20142 | 0.036621 | 11.2701 | -0.11444 | 0.086975 | -0.032044 | 122.9416 | 122.7676 | 75.2655 | -122.9736 | 122.937 | 122.8683 | 74.0982 | -123.1018
1547.5156 | 123.0515 | -58.5663 | 64.3021 | -0.23956 | 0.034675 | 0.071645 | 0.075413 | 0.13426 | 0.012802 | 0.0053299 | 0.033798 | 0.0089124 | 0.003027 | 0.008436 | 0.0058276 | -0.00025626 | 64.2151 | 64.3524 | 16.7679 | -56.9321 | 64.3021 | -58.6349 | -58.6716 | -47.2458 | 15.4816 | -58.7219 | 64.3341 | 64.2563 | -58.7173 | -58.8043 | -0.068665 | -0.10529 | 0 | 122.9187 | 1.6342 | 1.7395 | -0.086975 | -0.15106 | -0.23804 | 0.032043 | 11.3205 | -0.15564 | 0.082397 | -0.045776 | 122.8683 | 122.7814 | 75.3342 | -122.9736 | 122.9004 | 122.8226 | 74.0479 | -123.1064
1548.5156 | 123.0469 | -58.4976 | 64.4165 | -0.15564 | 0.032539 | 0.072286 | 0.076481 | 0.13447 | 0.011948 | 0.0070389 | -0.073013 | 0.0076306 | 0.0028134 | 0.0060862 | 0.0047596 | 0.0016663 | 64.2563 | 64.4028 | 16.8137 | -56.8497 | 64.4302 | -58.5388 | -58.6029 | -47.1313 | 15.6097 | -58.6212 | 64.4531 | 64.3707 | -58.6212 | -58.6853 | -0.041198 | -0.10529 | 0.013733 | 122.9004 | 1.6479 | 1.7532 | -0.16022 | -0.1236 | -0.18768 | 0.036621 | 11.3663 | -0.1236 | 0.064087 | -0.045776 | 122.9279 | 122.7539 | 75.3113 | -123.0194 | 122.9507 | 122.8683 | 74.1074 | -123.1018
1549.5156 | 123.1384 | -58.4793 | 64.4073 | 0.18768 | 0.028267 | 0.070149 | 0.076054 | 0.13554 | 0.0055392 | 0.0040481 | 0.25505 | 0.006776 | 0.001959 | 0.0075814 | 0.0034778 | 0.00081174 | 64.2654 | 64.4623 | 16.8457 | -56.8359 | 64.3707 | -58.4976 | -58.5571 | -46.9986 | 15.6464 | -58.5526 | 64.3936 | 64.325 | -58.5938 | -58.6624 | -0.018311 | -0.07782 | -0.036621 | 122.9416 | 1.6434 | 1.7212 | -0.14191 | -0.11444 | -0.18311 | -0.013733 | 11.4807 | -0.073242 | 0.10986 | -0.082398 | 122.85 | 122.7448 | 75.325 | -122.9645 | 122.8729 | 122.8043 | 74.1257 | -123.0698
1550.5156 | 123.0103 | -58.5068 | 64.444 | -0.21667 | 0.027626 | 0.073567 | 0.079472 | 0.13618 | 0.012375 | 0.0068253 | -0.095902 | 0.0069898 | 0.003027 | 0.0071542 | 0.0043324 | -0.00047006 | 64.2746 | 64.4257 | 16.8594 | -56.8497 | 64.4028 | -58.5342 | -58.58 | -46.9849 | 15.6143 | -58.6258 | 64.4531 | 64.3845 | -58.6121 | -58.699 | -0.027466 | -0.073242 | -0.041199 | 122.9324 | 1.6571 | 1.7303 | -0.16937 | -0.10529 | -0.19226 | 0.009155 | 11.5219 | -0.11902 | 0.073243 | -0.05951 | 122.9095 | 122.7814 | 75.3662 | -123.024 | 122.9599 | 122.8912 | 74.1211 | -123.143
1551.5156 | 123.0743 | -58.5297 | 64.3707 | -0.10986 | 0.032753 | 0.072286 | 0.078831 | 0.13447 | 0.012802 | 0.0068253 | -0.027237 | 0.0093396 | 0.0040952 | 0.0071542 | 0.0068958 | -0.0041017 | 64.2838 | 64.3982 | 16.6626 | -56.8542 | 64.4165 | -58.5617 | -58.6349 | -46.9116 | 15.5685 | -58.6487 | 64.3982 | 64.3295 | -58.6578 | -58.7585 | -0.032044 | -0.10529 | 0.045776 | 122.9279 | 1.6754 | 1.7807 | -0.086976 | -0.12817 | -0.22888 | 0.027465 | 11.618 | -0.11902 | 0.10986 | -0.041199 | 122.9462 | 122.8134 | 75.1923 | -123.0057 | 122.9279 | 122.8592 | 74.0982 | -123.1293
1552.5156 | 123.0011 | -58.5617 | 64.3433 | -0.15564 | 0.03318 | 0.071858 | 0.07819 | 0.13191 | 0.011734 | 0.0063981 | -0.088272 | 0.009126 | 0.0040952 | 0.006727 | 0.0068958 | 0.00017094 | 64.1922 | 64.3341 | 16.6489 | -56.8909 | 64.3616 | -58.5938 | -58.6624 | -46.9208 | 15.5365 | -58.7036 | 64.3616 | 64.3021 | -58.6761 | -58.786 | -0.032043 | -0.10071 | 0.01831 | 122.8958 | 1.6708 | 1.7715 | -0.15106 | -0.11444 | -0.2243 | 0.01831 | 11.6409 | -0.14191 | 0.082398 | -0.041199 | 122.9233 | 122.7539 | 75.2106 | -123.0057 | 122.9233 | 122.8638 | 74.0982 | -123.1293
1553.5156 | 123.0972 | -58.4976 | 64.389 | -0.1709 | 0.032539 | 0.071858 | 0.077977 | 0.13682 | 0.011734 | 0.0089615 | -0.057755 | 0.0078442 | 0.0049496 | 0.0086496 | 0.006255 | -0.0011109 | 64.2563 | 64.4119 | 16.745 | -56.8588 | 64.3982 | -58.5571 | -58.6304 | -46.7789 | 15.5502 | -58.7128 | 64.3707 | 64.2929 | -58.6395 | -58.7494 | -0.059509 | -0.13275 | 0.009155 | 122.9095 | 1.6388 | 1.7715 | -0.13275 | -0.14191 | -0.25177 | -0.01831 | 11.7188 | -0.21515 | 0.036621 | -0.09613 | 122.8958 | 122.7539 | 75.2426 | -123.0194 | 122.8683 | 122.7905 | 74.0479 | -123.1384
1554.5156 | 123.0286 | -58.6029 | 64.3433 | -0.17853 | 0.028908 | 0.074208 | 0.07819 | 0.13297 | 0.007462 | 0.0051163 | 0.19402 | 0.0069898 | 0.0017454 | 0.0086496 | 0.0064686 | 0.0014525 | 64.1327 | 64.3982 | 16.8182 | -56.8222 | 64.3662 | -58.5938 | -58.6578 | -46.8521 | 15.5777 | -58.7128 | 64.3616 | 64.2838 | -58.7265 | -58.8043 | 0.009155 | -0.054932 | 0.022888 | 123.0011 | 1.7807 | 1.8356 | -0.21057 | -0.1236 | -0.20142 | 0.01831 | 11.7508 | -0.10986 | 0.091552 | -0.05951 | 122.9691 | 122.7356 | 75.4211 | -123.0011 | 122.9645 | 122.8867 | 74.1806 | -123.1476
1555.5156 | 123.0972 | -58.4793 | 64.4165 | -0.14038 | 0.031044 | 0.072499 | 0.079472 | 0.13618 | 0.013871 | 0.0061845 | -0.050125 | 0.0078442 | 0.0043088 | 0.0088632 | 0.007323 | -0.0013245 | 64.2975 | 64.4211 | 16.8365 | -56.8039 | 64.4257 | -58.5205 | -58.5938 | -46.6095 | 15.6876 | -58.5983 | 64.4394 | 64.4028 | -58.5663 | -58.6899 | -0.041199 | -0.11444 | 0.009155 | 122.9004 | 1.6754 | 1.7899 | -0.11902 | -0.086975 | -0.21057 | 0.022888 | 11.8698 | -0.11902 | 0.091552 | -0.013733 | 122.905 | 122.7768 | 75.3159 | -123.0103 | 122.9187 | 122.8821 | 74.1669 | -123.1064
1556.5156 | 123.1155 | -58.5114 | 64.3478 | -0.15564 | 0.027626 | 0.07314 | 0.07584 | 0.1334 | 0.0078892 | 0.0044755 | -0.027237 | 0.0069898 | 0.001959 | 0.0092904 | 0.0047596 | 0.0010253 | 64.2792 | 64.4806 | 16.9006 | -56.8039 | 64.3387 | -58.5342 | -58.6121 | -46.55 | 15.7379 | -58.58 | 64.3662 | 64.2883 | -58.6258 | -58.7311 | -0.022888 | -0.10071 | -0.009155 | 122.9919 | 1.7075 | 1.8082 | -0.068664 | -0.11444 | -0.21973 | 0.018311 | 11.9614 | -0.068664 | 0.15106 | -0.059509 | 122.85 | 122.7905 | 75.412 | -122.9599 | 122.8775 | 122.7997 | 74.2493 | -123.0789
1557.5156 | 123.0331 | -58.5205 | 64.4028 | -0.10986 | 0.031257 | 0.072927 | 0.078404 | 0.13596 | 0.01088 | 0.0057571 | -0.13405 | 0.0086988 | 0.0070858 | 0.006727 | 0.0064686 | -0.0015381 | 64.2426 | 64.3845 | 16.7725 | -56.8405 | 64.4165 | -58.5571 | -58.6121 | -46.5546 | 15.6738 | -58.6441 | 64.4394 | 64.3341 | -58.6304 | -58.7128 | -0.036621 | -0.091553 | 0.013733 | 122.905 | 1.68 | 1.7715 | -0.16022 | -0.10986 | -0.19226 | 0.036621 | 11.9659 | -0.1236 | 0.068665 | -0.068665 | 122.937 | 122.7631 | 75.293 | -123.0148 | 122.9599 | 122.8546 | 74.1943 | -123.1155
1558.5156 | 123.111 | -58.5022 | 64.3707 | -0.14801 | 0.02848 | 0.07314 | 0.07584 | 0.13169 | 0.0066074 | 0.0049027 | -0.050125 | 0.0089124 | 0.0034542 | 0.0092904 | 0.0036914 | -0.00089726 | 64.2746 | 64.4897 | 16.8915 | -56.7856 | 64.3524 | -58.5342 | -58.5754 | -46.4355 | 15.7608 | -58.5617 | 64.389 | 64.2929 | -58.6075 | -58.7173 | -0.032044 | -0.073242 | -0.018311 | 122.9919 | 1.7166 | 1.7899 | -0.096131 | -0.10529 | -0.21515 | 0.01831 | 12.0667 | -0.05951 | 0.15564 | -0.07782 | 122.8546 | 122.7768 | 75.3937 | -122.9462 | 122.8912 | 122.7951 | 74.263 | -123.0881
1559.5156 | 123.0469 | -58.58 | 64.3295 | -0.13275 | 0.031471 | 0.072072 | 0.080113 | 0.13276 | 0.014084 | 0.0055435 | -0.11116 | 0.010194 | 0.0055906 | 0.0086496 | 0.007323 | -4.2662e-05 | 64.183 | 64.3204 | 16.777 | -56.9321 | 64.3524 | -58.6166 | -58.6899 | -46.4447 | 15.6692 | -58.7265 | 64.3616 | 64.2609 | -58.7219 | -58.7952 | -0.036621 | -0.10986 | 0.022888 | 122.9004 | 1.6479 | 1.7578 | -0.14648 | -0.14191 | -0.21515 | 0.032043 | 12.1353 | -0.14648 | 0.068665 | -0.068665 | 122.9324 | 122.7631 | 75.3571 | -123.0194 | 122.9416 | 122.8409 | 74.2493 | -123.1247
1560.5156 | 123.0927 | -58.4656 | 64.3982 | -0.15564 | 0.028267 | 0.07079 | 0.074131 | 0.13639 | 0.0081028 | 0.0044755 | -0.073013 | 0.008485 | 0.0032406 | 0.0073678 | 0.0066822 | -4.2662e-05 | 64.3204 | 64.5035 | 16.745 | -56.781 | 64.3936 | -58.5159 | -58.5571 | -46.257 | 15.8249 | -58.5709 | 64.3982 | 64.3616 | -58.5846 | -58.6945 | -0.050354 | -0.091553 | -0.004577 | 122.9691 | 1.6846 | 1.7761 | -0.077819 | -0.11902 | -0.22888 | 0 | 12.2086 | -0.10529 | 0.1236 | -0.036621 | 122.8592 | 122.7859 | 75.2106 | -122.9553 | 122.8638 | 122.8271 | 74.2905 | -123.0927
1561.5156 | 123.0423 | -58.5938 | 64.325 | -0.18616 | 0.029335 | 0.072713 | 0.078404 | 0.13511 | 0.0078892 | 0.0068253 | -0.0043486 | 0.009126 | 0.004736 | 0.008436 | 0.005614 | 0.00038454 | 64.1739 | 64.2059 | 16.5298 | -56.8817 | 64.3616 | -58.6166 | -58.6807 | -46.3211 | 15.683 | -58.7128 | 64.3433 | 64.3112 | -58.7036 | -58.7723 | -0.022888 | -0.086975 | 0.036621 | 122.7997 | 1.712 | 1.799 | -0.15106 | -0.10986 | -0.17853 | 0.018311 | 12.2726 | -0.11902 | 0.059509 | -0.013733 | 122.9553 | 122.7676 | 75.1236 | -123.0057 | 122.937 | 122.905 | 74.2767 | -123.0972
1562.5156 | 123.1201 | -58.4518 | 64.3936 | 0.057983 | 0.025917 | 0.07314 | 0.076481 | 0.13084 | 0.0061802 | 0.0053299 | 0.041427 | 0.0080578 | 0.0038816 | 0.0075814 | 0.004546 | 0.00059814 | 64.357 | 64.5538 | 16.8732 | -56.7627 | 64.3982 | -58.493 | -58.5434 | -46.0922 | 15.9302 | -58.5114 | 64.3982 | 64.3112 | -58.5617 | -58.6533 | -0.041199 | -0.091553 | 0.004577 | 123.0057 | 1.6891 | 1.7807 | -0.036621 | -0.10986 | -0.20142 | 0.004577 | 12.3596 | -0.05951 | 0.14191 | -0.082398 | 122.85 | 122.8088 | 75.325 | -122.937 | 122.85 | 122.7631 | 74.382 | -123.0469
1563.5156 | 123.0606 | -58.4793 | 64.4669 | -0.20905 | 0.028908 | 0.070577 | 0.078618 | 0.13447 | 0.012375 | 0.0053299 | -0.065384 | 0.010194 | 0.0038816 | 0.0086496 | 0.0036914 | -0.00068366 | 64.3433 | 64.5035 | 16.8045 | -56.7398 | 64.476 | -58.4702 | -58.5434 | -46.0785 | 15.8386 | -58.5571 | 64.4852 | 64.3982 | -58.5663 | -58.6716 | 0.009155 | -0.064087 | 0.009155 | 122.9828 | 1.7395 | 1.8036 | -0.1236 | -0.086975 | -0.19226 | 0.01831 | 12.4008 | -0.07782 | 0.11444 | -0.068665 | 122.9553 | 122.8226 | 75.2838 | -123.0103 | 122.9645 | 122.8775 | 74.3179 | -123.1384
1564.5156 | 123.0194 | -58.3191 | 64.5218 | -0.056458 | 0.026344 | 0.07314 | 0.073277 | 0.13383 | 0.0089572 | 0.0042619 | -0.011978 | 0.0086988 | 0.003027 | 0.0090768 | 0.0066822 | 0.00059814 | 64.4897 | 64.7003 | 16.9693 | -56.6391 | 64.5401 | -58.3832 | -58.4061 | -45.7718 | 16.1316 | -58.3282 | 64.5355 | 64.4669 | -58.461 | -58.5022 | -0.064087 | -0.086975 | 0.01831 | 123.0194 | 1.68 | 1.767 | -0.032044 | -0.14191 | -0.18311 | 0.013732 | 12.5473 | -0.009155 | 0.17395 | -0.054932 | 122.8592 | 122.8088 | 75.2884 | -122.9279 | 122.8546 | 122.7859 | 74.4507 | -123.024
1565.5156 | 123.0148 | -58.4335 | 64.4669 | -0.2243 | 0.029121 | 0.072072 | 0.076268 | 0.13361 | 0.0095982 | 0.0072525 | -0.10353 | 0.010408 | 0.0025998 | 0.0099314 | 0.007323 | -0.0017517 | 64.357 | 64.4852 | 16.6351 | -56.7627 | 64.476 | -58.461 | -58.5114 | -45.9457 | 15.9027 | -58.5571 | 64.4989 | 64.4073 | -58.5754 | -58.6395 | -0.027466 | -0.07782 | 0.009155 | 122.9187 | 1.6708 | 1.7487 | -0.10986 | -0.14191 | -0.20599 | 0.032043 | 12.4878 | -0.1236 | 0.082397 | -0.059509 | 122.9095 | 122.7905 | 75.0687 | -122.9782 | 122.9324 | 122.8409 | 74.3362 | -123.1064
1566.5156 | 123.1567 | -58.4473 | 64.4211 | -0.11749 | 0.02549 | 0.071218 | 0.073918 | 0.13361 | 0.0070346 | 0.0053299 | 0.0032804 | 0.0093396 | 0.0025998 | 0.0052316 | 0.0043324 | 0.00081174 | 64.3753 | 64.5859 | 16.7541 | -56.7123 | 64.4211 | -58.4381 | -58.5205 | -45.8496 | 15.6738 | -58.4747 | 64.4211 | 64.3204 | -58.5342 | -58.6578 | 0.009156 | -0.073242 | 0 | 123.0331 | 1.7349 | 1.8082 | -0.045777 | -0.086975 | -0.21057 | 0 | 12.5977 | -0.027465 | 0.18311 | -0.10071 | 122.8683 | 122.8226 | 75.2014 | -122.9416 | 122.8683 | 122.7676 | 74.1211 | -123.0789
1567.5156 | 123.0377 | -58.3557 | 64.4989 | -0.16327 | 0.026985 | 0.071645 | 0.077763 | 0.13233 | 0.011093 | 0.0053299 | -0.073013 | 0.0076306 | 0.0049496 | 0.0069406 | 0.0060412 | 0.00017094 | 64.4485 | 64.6362 | 16.864 | -56.6391 | 64.5218 | -58.4061 | -58.429 | -45.6848 | 16.0355 | -58.4427 | 64.5264 | 64.444 | -58.4885 | -58.58 | -0.050354 | -0.073242 | 0.022889 | 122.9919 | 1.7166 | 1.7899 | -0.050354 | -0.13275 | -0.2243 | 0.027466 | 12.6709 | -0.086975 | 0.13733 | -0.054931 | 122.8775 | 122.8043 | 75.2197 | -122.9279 | 122.8821 | 122.7997 | 74.3912 | -123.0789
1568.5156 | 123.1201 | -58.3603 | 64.4897 | -0.10986 | 0.024208 | 0.073995 | 0.077336 | 0.1349 | 0.010453 | 0.0046891 | -0.095902 | 0.0078442 | 0.0023862 | 0.0088632 | 0.0071094 | -0.00089726 | 64.444 | 64.65 | 16.8457 | -56.6574 | 64.4943 | -58.4061 | -58.4518 | -45.6161 | 16.0812 | -58.4152 | 64.4989 | 64.4211 | -58.4839 | -58.5892 | -0.045776 | -0.091552 | 0.004578 | 123.0103 | 1.7029 | 1.7944 | -0.045776 | -0.1236 | -0.22888 | 0.009155 | 12.7441 | -0.054931 | 0.17395 | -0.068664 | 122.8546 | 122.8043 | 75.206 | -122.9416 | 122.8592 | 122.7814 | 74.4415 | -123.0789
1569.5156 | 123.143 | -58.342 | 64.4806 | -0.14038 | 0.026771 | 0.071218 | 0.077549 | 0.13084 | 0.00853 | 0.0029801 | -0.027237 | 0.008485 | 0.0038816 | 0.0088632 | 0.0058276 | -0.00047006 | 64.4257 | 64.6271 | 16.9373 | -56.6666 | 64.4623 | -58.3923 | -58.4839 | -45.5338 | 16.0995 | -58.4152 | 64.476 | 64.3845 | -58.4656 | -58.6029 | -0.050354 | -0.14191 | -0.018311 | 122.9691 | 1.6754 | 1.8173 | -0.054932 | -0.1236 | -0.26093 | -0.004578 | 12.8082 | -0.073242 | 0.18768 | -0.096131 | 122.8043 | 122.7676 | 75.2792 | -122.9645 | 122.818 | 122.7264 | 74.4415 | -123.0835
1570.5156 | 123.0881 | -58.3969 | 64.4165 | 0.088501 | 0.027412 | 0.07079 | 0.076481 | 0.13255 | 0.011948 | 0.0055435 | 0.14061 | 0.007417 | 0.0006772 | 0.012281 | 0.0071094 | -0.00025626 | 64.357 | 64.5035 | 16.7999 | -56.749 | 64.444 | -58.4564 | -58.4885 | -45.52 | 15.9119 | -58.493 | 64.444 | 64.357 | -58.493 | -58.6441 | -0.059509 | -0.091552 | 0.027466 | 122.9004 | 1.648 | 1.7395 | -0.059509 | -0.09613 | -0.24719 | 0.027466 | 12.8769 | -0.09613 | 0.15106 | -0.059509 | 122.8409 | 122.7539 | 75.1968 | -122.905 | 122.8409 | 122.7539 | 74.3088 | -123.0606
1571.5156 | 123.111 | -58.461 | 64.3799 | 0.012207 | 0.025276 | 0.073354 | 0.076054 | 0.13255 | 0.0098118 | 0.0068253 | 0.064316 | 0.0061352 | 0.0051632 | 0.010359 | 0.0047596 | -0.0019653 | 64.3021 | 64.4806 | 16.7358 | -56.7902 | 64.3845 | -58.5342 | -58.5846 | -45.4971 | 15.9714 | -58.5388 | 64.3707 | 64.2838 | -58.5892 | -58.6899 | -0.073242 | -0.1236 | 0.004577 | 122.9416 | 1.6708 | 1.7944 | -0.07782 | -0.12817 | -0.22888 | -0.009155 | 12.9639 | -0.077819 | 0.15106 | -0.096131 | 122.8455 | 122.7631 | 75.1968 | -122.9645 | 122.8317 | 122.7448 | 74.4324 | -123.0698
1572.5156 | 123.1247 | -58.3282 | 64.4852 | 0.14191 | 0.025062 | 0.075063 | 0.077336 | 0.13426 | 0.0093846 | 0.0061845 | 0.2932 | 0.0089124 | 0.0077268 | 0.007795 | 0.006255 | 0.00017094 | 64.4119 | 64.563 | 16.9556 | -56.662 | 64.4806 | -58.4015 | -58.4427 | -45.3506 | 16.0629 | -58.4518 | 64.5309 | 64.4028 | -58.4702 | -58.5434 | -0.073242 | -0.11444 | -0.004577 | 122.8912 | 1.6663 | 1.7807 | -0.073242 | -0.14191 | -0.21515 | 0.045777 | 12.9776 | -0.1236 | 0.091553 | -0.082397 | 122.8088 | 122.7402 | 75.2838 | -122.9279 | 122.8592 | 122.731 | 74.3912 | -123.0286
1573.5156 | 123.1979 | -58.2642 | 64.5401 | -0.086975 | 0.025276 | 0.072927 | 0.074772 | 0.13639 | 0.011093 | 0.0053299 | 0.018539 | 0.0080578 | 0.0006772 | 0.0082224 | 0.0066822 | -0.00047006 | 64.5767 | 64.7598 | 17.0059 | -56.543 | 64.5905 | -58.2779 | -58.3557 | -45.0897 | 16.214 | -58.017 | 64.6545 | 64.5676 | -58.3603 | -58.4564 | -0.013733 | -0.091553 | 0.050354 | 123.024 | 1.7212 | 1.8127 | 0.036621 | -0.096131 | -0.19226 | 0.11444 | 13.1744 | 0.24719 | 0.43945 | 0.027466 | 122.8546 | 122.8409 | 75.2701 | -122.8958 | 122.9187 | 122.8317 | 74.4781 | -122.9965
1574.5156 | 123.0972 | -58.4564 | 64.389 | 0.09613 | 0.027199 | 0.072499 | 0.074772 | 0.13297 | 0.0095982 | 0.0081071 | -0.12642 | 0.0097668 | 0.0032406 | 0.008436 | 0.0077502 | -0.00089726 | 64.3341 | 64.4623 | 16.8686 | -56.7719 | 64.3936 | -58.4885 | -58.5251 | -45.3323 | 15.9485 | -58.5526 | 64.4257 | 64.2929 | -58.5617 | -58.6624 | -0.032043 | -0.068664 | 0.004578 | 122.9187 | 1.6846 | 1.7532 | -0.054932 | -0.10529 | -0.20599 | 0.036621 | 13.1241 | -0.09613 | 0.10986 | -0.09613 | 122.85 | 122.7905 | 75.325 | -122.9141 | 122.8821 | 122.7493 | 74.4049 | -123.0515
1575.5156 | 123.1613 | -58.3008 | 64.5172 | 0.0045777 | 0.02613 | 0.073781 | 0.07584 | 0.13319 | 0.010239 | 0.0061845 | 0.033798 | 0.008485 | 0.0038816 | 0.0062998 | 0.007323 | 0.00017094 | 64.4531 | 64.6271 | 16.9418 | -56.6345 | 64.5309 | -58.374 | -58.4244 | -45.076 | 16.1133 | -58.374 | 64.5355 | 64.4211 | -58.4518 | -58.548 | -0.073242 | -0.1236 | 0.013733 | 122.9279 | 1.6663 | 1.7899 | -0.064087 | -0.15106 | -0.24719 | 0.01831 | 13.2248 | -0.073242 | 0.17395 | -0.09613 | 122.8317 | 122.7539 | 75.2426 | -122.9416 | 122.8363 | 122.7219 | 74.4141 | -123.0652
1576.5156 | 123.1201 | -58.3054 | 64.4989 | 0.14191 | 0.030403 | 0.075063 | 0.076695 | 0.13297 | 0.013871 | 0.0061845 | 0.22453 | 0.0089124 | 0.003668 | 0.0088632 | 0.0083912 | -0.00047006 | 64.4943 | 64.6408 | 17.0151 | -56.6162 | 64.4897 | -58.3694 | -58.4427 | -44.9982 | 16.127 | -58.3923 | 64.5309 | 64.3799 | -58.4518 | -58.5526 | -0.064087 | -0.13733 | -0.009155 | 122.9462 | 1.6891 | 1.8265 | -0.004577 | -0.14648 | -0.24719 | 0.032044 | 13.3072 | -0.086975 | 0.16022 | -0.11902 | 122.7951 | 122.7997 | 75.3204 | -122.9416 | 122.8363 | 122.6852 | 74.4324 | -123.0515
1577.5156 | 123.1064 | -58.3237 | 64.5264 | 1.5686 | 0.024421 | 0.071645 | 0.075627 | 0.13426 | 0.0078892 | 0.0083207 | 0.11772 | 0.0086988 | 0.0006772 | 0.010359 | 0.0049732 | -0.0015381 | 64.4394 | 64.5859 | 17.038 | -56.6254 | 64.5172 | -58.3694 | -58.4335 | -44.9753 | 16.1087 | -58.3832 | 64.5493 | 64.4348 | -58.4198 | -58.5251 | -0.045777 | -0.10986 | -0.009155 | 122.9095 | 1.6983 | 1.8082 | -0.086975 | -0.096131 | -0.20142 | 0.022888 | 13.3484 | -0.05951 | 0.14191 | -0.091553 | 122.8409 | 122.7631 | 75.3616 | -122.9599 | 122.8729 | 122.7585 | 74.4324 | -123.0515
1578.5156 | 123.1018 | -58.6166 | 64.2288 | 0.027466 | 0.032966 | 0.072499 | 0.076054 | 0.13618 | 0.014298 | 0.0072525 | 0.24742 | 0.0095532 | 0.0038816 | 0.009504 | 0.0068958 | -0.00068366 | 64.2151 | 64.3433 | 16.7999 | -56.9183 | 64.2105 | -58.6533 | -58.699 | -45.1584 | 15.8249 | -58.6899 | 64.2288 | 64.1052 | -58.7585 | -58.8455 | -0.036621 | -0.082398 | -0.018311 | 122.9599 | 1.6983 | 1.7807 | -0.013733 | -0.14191 | -0.22888 | 0 | 13.4583 | -0.073242 | 0.15564 | -0.1236 | 122.8271 | 122.8317 | 75.4166 | -122.9279 | 122.8455 | 122.7219 | 74.4415 | -123.0743
1579.5156 | 123.0972 | -58.4427 | 64.3845 | 0.14954 | 0.024635 | 0.07079 | 0.074772 | 0.13276 | 0.010025 | 0.0076797 | 0.2169 | 0.0089124 | 0.0017454 | 0.0092904 | 0.0079638 | 0.0014525 | 64.3158 | 64.4852 | 17.0288 | -56.7535 | 64.4165 | -58.4793 | -58.5159 | -44.9524 | 16.008 | -58.5205 | 64.3936 | 64.3158 | -58.5663 | -58.6807 | -0.036621 | -0.073242 | 0.032044 | 122.9279 | 1.6891 | 1.7624 | -0.068664 | -0.1236 | -0.23804 | 0.009156 | 13.4903 | -0.07782 | 0.16022 | -0.068664 | 122.8592 | 122.7585 | 75.4715 | -122.9004 | 122.8363 | 122.7585 | 74.4507 | -123.0652
1580.5156 | 123.1064 | -58.3786 | 64.4073 | 0.065613 | 0.029335 | 0.071218 | 0.077763 | 0.13618 | 0.014725 | 0.0063981 | 0.28557 | 0.010621 | 0.004736 | 0.007795 | 0.0079638 | 0.00038454 | 64.4531 | 64.5676 | 17.189 | -56.6711 | 64.4348 | -58.4335 | -58.4793 | -44.7739 | 16.0812 | -58.4473 | 64.4531 | 64.3753 | -58.5297 | -58.6121 | -0.054932 | -0.10071 | 0.027465 | 122.9462 | 1.7075 | 1.8082 | 0.045776 | -0.15106 | -0.23346 | 0.045776 | 13.6047 | -0.068665 | 0.16479 | -0.032044 | 122.8134 | 122.8317 | 75.5676 | -122.8867 | 122.8317 | 122.7539 | 74.4598 | -123.0194
1581.5156 | 123.0652 | -58.3649 | 64.476 | 0.14191 | 0.025703 | 0.070363 | 0.074772 | 0.13383 | 0.010025 | 0.0063981 | 0.25505 | 0.0086988 | 0.004736 | 0.0099314 | 0.0077502 | 0.00081174 | 64.4257 | 64.563 | 17.0242 | -56.6666 | 64.4852 | -58.4061 | -58.4427 | -44.7281 | 16.0812 | -58.4427 | 64.4852 | 64.4302 | -58.4656 | -58.58 | -0.041199 | -0.07782 | 0.009155 | 122.9279 | 1.6983 | 1.7761 | -0.050354 | -0.10071 | -0.21515 | 0.009155 | 13.6368 | -0.07782 | 0.13733 | -0.045776 | 122.85 | 122.7905 | 75.3891 | -122.9187 | 122.85 | 122.7951 | 74.4461 | -123.056
1582.5156 | 123.111 | -58.3374 | 64.4806 | 0.25635 | 0.031044 | 0.071218 | 0.076268 | 0.13532 | 0.014511 | 0.0091751 | 0.26268 | 0.011049 | 0.0066586 | 0.0092904 | 0.0071094 | -0.00089726 | 64.5035 | 64.6271 | 16.9876 | -56.5933 | 64.5081 | -58.3878 | -58.4427 | -44.5862 | 15.7791 | -58.342 | 64.4806 | 64.3845 | -58.461 | -58.5388 | -0.050354 | -0.10529 | 0.027466 | 122.9645 | 1.7441 | 1.8494 | 0.022888 | -0.1236 | -0.20142 | 0 | 13.7512 | -0.004578 | 0.19684 | -0.096131 | 122.8455 | 122.8409 | 75.325 | -122.9233 | 122.818 | 122.7219 | 74.1165 | -123.0194
1583.5156 | 123.0789 | -58.4381 | 64.4073 | 0.17242 | 0.027412 | 0.072927 | 0.075627 | 0.13212 | 0.011521 | 0.0061845 | 0.18639 | 0.008485 | 0.003027 | 0.0090768 | 0.0066822 | 0.00081174 | 64.3204 | 64.4623 | 16.7908 | -56.781 | 64.4073 | -58.4885 | -58.5342 | -44.7006 | 15.9668 | -58.5205 | 64.3936 | 64.3066 | -58.5983 | -58.6899 | -0.050354 | -0.096131 | 0 | 122.9004 | 1.6571 | 1.7532 | -0.086975 | -0.16022 | -0.25177 | -0.013733 | 13.7375 | -0.082398 | 0.16937 | -0.10071 | 122.8455 | 122.7585 | 75.2289 | -122.9416 | 122.8317 | 122.7448 | 74.4049 | -123.0972
1584.5156 | 123.1613 | -58.4198 | 64.3982 | 0.18005 | 0.032539 | 0.071004 | 0.074986 | 0.13297 | 0.015152 | 0.0076797 | 0.2932 | 0.010621 | 0.0083676 | 0.011213 | 0.0071094 | -0.0017517 | 64.4302 | 64.5493 | 16.9052 | -56.6711 | 64.4485 | -58.4564 | -58.5068 | -44.4351 | 16.0217 | -58.4473 | 64.4348 | 64.3433 | -58.5342 | -58.6304 | -0.036621 | -0.086975 | 0.050354 | 122.9691 | 1.7487 | 1.8356 | 0.032044 | -0.11444 | -0.21057 | 0.036621 | 13.9847 | -0.027466 | 0.1831 | -0.054931 | 122.8683 | 122.85 | 75.325 | -122.905 | 122.8546 | 122.7631 | 74.4415 | -123.0286
1585.5156 | 123.1293 | -58.4198 | 64.4073 | 0.46997 | 0.028694 | 0.073567 | 0.074772 | 0.13319 | 0.010239 | 0.0070389 | 0.25505 | 0.0099804 | 0.0038816 | 0.0088632 | 0.0098866 | 0.00017094 | 64.4165 | 64.5309 | 16.8777 | -56.7078 | 64.3982 | -58.4839 | -58.5114 | -44.4901 | 16.0812 | -58.4656 | 64.4119 | 64.3295 | -58.5342 | -58.6441 | -0.064087 | -0.091553 | -0.009156 | 122.9507 | 1.712 | 1.8036 | 0.009155 | -0.11444 | -0.2243 | 0.004577 | 13.9297 | -0.045776 | 0.17853 | -0.07782 | 122.818 | 122.8363 | 75.2975 | -122.9187 | 122.8317 | 122.7493 | 74.501 | -123.0515
1586.5156 | 123.0286 | -58.4518 | 64.3982 | 0.20294 | 0.032539 | 0.072286 | 0.077336 | 0.13255 | 0.016861 | 0.01003 | 0.14061 | 0.013185 | 0.006445 | 0.0088632 | 0.0083912 | -0.00089726 | 64.3204 | 64.3753 | 16.7725 | -56.7627 | 64.4531 | -58.5114 | -58.5617 | -44.5084 | 15.9531 | -58.5846 | 64.4485 | 64.3845 | -58.5983 | -58.6761 | -0.05951 | -0.10986 | 0.054932 | 122.8271 | 1.6891 | 1.799 | -0.077819 | -0.14649 | -0.2243 | 0.050354 | 13.9435 | -0.13275 | 0.091552 | -0.013733 | 122.905 | 122.7722 | 75.2243 | -122.9599 | 122.9004 | 122.8363 | 74.4049 | -123.0743
1587.5156 | 123.0881 | -58.3832 | 64.444 | 0.29449 | 0.028908 | 0.072072 | 0.071354 | 0.13426 | 0.012589 | 0.0072525 | 0.26268 | 0.010621 | 0.004736 | 0.008436 | 0.0083912 | 0.00059814 | 64.4531 | 64.5721 | 16.777 | -56.6803 | 64.4302 | -58.4427 | -58.5159 | -44.3115 | 16.1224 | -58.4381 | 64.476 | 64.3753 | -58.5205 | -58.6212 | -0.059509 | -0.13275 | -0.013733 | 122.9553 | 1.7029 | 1.8356 | 0.009155 | -0.13733 | -0.23804 | 0.032043 | 14.0717 | -0.054931 | 0.18311 | -0.068665 | 122.8134 | 122.8363 | 75.1602 | -122.9599 | 122.8592 | 122.7585 | 74.5056 | -123.0652
1588.5156 | 123.0698 | -58.4656 | 64.4348 | 0.20294 | 0.033394 | 0.071218 | 0.076909 | 0.13233 | 0.013443 | 0.0081071 | 0.25505 | 0.012544 | 0.008154 | 0.0097176 | 0.0071094 | -0.00068366 | 64.3433 | 64.4394 | 16.6214 | -56.749 | 64.4623 | -58.461 | -58.5114 | -44.339 | 15.9897 | -58.5297 | 64.4714 | 64.4119 | -58.5617 | -58.6395 | 0.004577 | -0.045777 | 0.027466 | 122.905 | 1.7166 | 1.7624 | -0.091552 | -0.096131 | -0.17395 | 0.036622 | 14.1266 | -0.064087 | 0.10986 | -0.022888 | 122.9279 | 122.8088 | 75.087 | -122.9462 | 122.937 | 122.8775 | 74.4553 | -123.0743
1589.5156 | 123.111 | -58.3832 | 64.4531 | 0.23346 | 0.032539 | 0.070363 | 0.074986 | 0.13383 | 0.012375 | 0.0066117 | 0.12535 | 0.010408 | 0.0023862 | 0.010999 | 0.0079638 | 0.0014525 | 64.444 | 64.5813 | 16.7313 | -56.6528 | 64.4485 | -58.429 | -58.5068 | -44.1925 | 16.2003 | -58.4152 | 64.4623 | 64.3936 | -58.4976 | -58.5846 | -0.045776 | -0.1236 | -0.004578 | 122.9645 | 1.7303 | 1.8539 | -0.009155 | -0.11444 | -0.20142 | 0.009155 | 14.1907 | -0.032043 | 0.16937 | -0.059509 | 122.8317 | 122.8271 | 75.1144 | -122.9599 | 122.8455 | 122.7768 | 74.5834 | -123.0377
1590.5156 | 123.0148 | -58.461 | 64.4531 | 0.088501 | 0.034035 | 0.070577 | 0.076268 | 0.13361 | 0.015793 | 0.0085343 | 0.12535 | 0.012971 | 0.0087948 | 0.010359 | 0.0098866 | -0.00047006 | 64.357 | 64.4119 | 16.4795 | -56.7215 | 64.4806 | -58.4656 | -58.5159 | -44.2795 | 16.0126 | -58.5754 | 64.4852 | 64.4165 | -58.5617 | -58.667 | -0.004577 | -0.054931 | 0.027466 | 122.8729 | 1.7395 | 1.7944 | -0.09613 | -0.10071 | -0.20599 | 0.032043 | 14.1815 | -0.11444 | 0.091553 | -0.036621 | 122.9416 | 122.818 | 74.9405 | -122.9691 | 122.9462 | 122.8775 | 74.4736 | -123.1201
1591.5156 | 123.1247 | -58.3603 | 64.4577 | 0.24109 | 0.032112 | 0.071645 | 0.079899 | 0.1302 | 0.010666 | 0.0085343 | 0.30846 | 0.012544 | 0.003668 | 0.0069406 | 0.0092456 | 0.00017094 | 64.4165 | 64.5264 | 16.5161 | -56.662 | 64.4577 | -58.4061 | -58.4839 | -44.0781 | 16.2048 | -58.4015 | 64.4714 | 64.4028 | -58.4793 | -58.5709 | -0.045776 | -0.1236 | 0 | 122.8867 | 1.6983 | 1.8219 | -0.041199 | -0.11902 | -0.21057 | 0.013733 | 14.2822 | -0.041198 | 0.16937 | -0.054932 | 122.818 | 122.7768 | 74.8764 | -122.9416 | 122.8317 | 122.7631 | 74.5651 | -123.0286
1592.5156 | 122.9919 | -58.4976 | 64.3753 | 0.13428 | 0.037666 | 0.071431 | 0.076909 | 0.13276 | 0.014939 | 0.0072525 | 0.14061 | 0.014039 | 0.0045224 | 0.0086496 | 0.0094592 | 0.0018799 | 64.238 | 64.3066 | 16.1545 | -56.8405 | 64.4211 | -58.5663 | -58.6212 | -44.2474 | 15.8844 | -58.9096 | 64.3433 | 64.2883 | -58.6716 | -58.7494 | -0.068664 | -0.1236 | 0.045777 | 122.8043 | 1.6571 | 1.7807 | -0.13733 | -0.17395 | -0.25177 | -0.032043 | 14.2502 | -0.41199 | -0.16022 | -0.086975 | 122.9187 | 122.7356 | 74.6521 | -122.9965 | 122.8409 | 122.7859 | 74.382 | -123.1247
1593.5156 | 123.0927 | -58.4198 | 64.4348 | 0.17242 | 0.034889 | 0.070363 | 0.07819 | 0.1349 | 0.01088 | 0.0068253 | 0.27794 | 0.014253 | 0.0070858 | 0.009504 | 0.0092456 | 0.0035889 | 64.325 | 64.4073 | 16.0675 | -56.7398 | 64.4623 | -58.4976 | -58.5159 | -44.0231 | 16.0858 | -58.5159 | 64.4806 | 64.3662 | -58.548 | -58.6533 | -0.07782 | -0.09613 | 0.027466 | 122.8271 | 1.68 | 1.7761 | -0.10986 | -0.12817 | -0.23346 | 0.045777 | 14.3967 | -0.09613 | 0.13733 | -0.068664 | 122.8821 | 122.7448 | 74.4873 | -122.9507 | 122.9004 | 122.786 | 74.5056 | -123.0881
1594.5156 | 122.9874 | -58.4198 | 64.5172 | 0.09613 | 0.035957 | 0.07079 | 0.079045 | 0.13297 | 0.014084 | 0.0096023 | 0.14824 | 0.013398 | 0.0066586 | 0.01164 | 0.009032 | 0.00081174 | 64.3524 | 64.4302 | 16.0355 | -56.9412 | 64.4669 | -58.4473 | -58.4976 | -43.927 | 16.0767 | -58.5114 | 64.5401 | 64.476 | -58.493 | -58.6029 | -0.027466 | -0.07782 | -0.050354 | 122.85 | 1.4786 | 1.5564 | -0.16479 | -0.073242 | -0.1831 | 0.022888 | 14.4928 | -0.091553 | 0.091552 | -0.041199 | 122.8867 | 122.7722 | 74.4553 | -123.0148 | 122.9599 | 122.8958 | 74.4965 | -123.1201
1595.5156 | 123.0972 | -58.374 | 64.4806 | 0.2182 | 0.031685 | 0.071004 | 0.077977 | 0.13062 | 0.010453 | 0.0068253 | 0.30846 | 0.013398 | 0.0045224 | 0.010786 | 0.0071094 | 0.0010253 | 64.4119 | 64.5218 | 15.8981 | -56.6483 | 64.5126 | -58.3786 | -58.4564 | -43.7988 | 16.1865 | -58.3923 | 64.5355 | 64.4485 | -58.4885 | -58.5571 | -0.004578 | -0.082398 | 0.032043 | 122.8958 | 1.7258 | 1.8082 | -0.068665 | -0.11444 | -0.18311 | 0.054931 | 14.5752 | -0.018311 | 0.1648 | -0.032044 | 122.8867 | 122.7859 | 74.2722 | -122.937 | 122.9095 | 122.8226 | 74.5605 | -123.0377
1596.5156 | 122.9782 | -58.3008 | 64.6271 | 0.09613 | 0.033607 | 0.069081 | 0.076054 | 0.13297 | 0.013443 | 0.0091751 | 0.10246 | 0.014039 | 0.010077 | 0.010145 | 0.010314 | 0.00038454 | 64.4852 | 64.5676 | 15.9027 | -56.5384 | 64.6591 | -58.3008 | -58.3878 | -43.7027 | 16.1957 | -58.4106 | 64.6683 | 64.6088 | -58.4015 | -58.493 | 0 | -0.086975 | 0.032044 | 122.8683 | 1.7624 | 1.8494 | -0.14191 | -0.10071 | -0.19226 | 0.041199 | 14.5981 | -0.10986 | 0.082397 | -0.01831 | 122.9599 | 122.7859 | 74.2035 | -123.0148 | 122.9691 | 122.9095 | 74.4965 | -123.1201
1597.5156 | 123.0377 | -58.3649 | 64.5584 | 0.11139 | 0.03318 | 0.071004 | 0.075627 | 0.13255 | 0.014725 | 0.011525 | 0.25505 | 0.012544 | 0.0058042 | 0.011854 | 0.0094592 | -0.00068366 | 64.2563 | 64.3433 | 15.6921 | -56.4056 | 64.5767 | -58.3694 | -58.4335 | -43.7119 | 16.1499 | -58.461 | 64.5859 | 64.5081 | -58.4747 | -58.5754 | -0.004578 | -0.068665 | 0.01831 | 122.7081 | 1.9592 | 2.0279 | -0.30212 | -0.10986 | -0.21057 | 0.027465 | 14.653 | -0.096131 | 0.11444 | -0.050354 | 122.9416 | 122.6212 | 74.057 | -122.9919 | 122.9507 | 122.8729 | 74.5148 | -123.1339
1598.5156 | 123.024 | -58.3466 | 64.5584 | -0.071716 | 0.035103 | 0.071431 | 0.079258 | 0.13511 | 0.014511 | 0.0081071 | 0.026169 | 0.013185 | 0.0090084 | 0.010145 | 0.0068958 | 0.0010253 | 64.4669 | 64.5538 | 15.5731 | -56.5521 | 64.5676 | -58.4015 | -58.4473 | -43.5974 | 16.2048 | -58.4198 | 64.563 | 64.5035 | -58.4473 | -58.5526 | -0.054931 | -0.10071 | 0.009155 | 122.9004 | 1.7944 | 1.8951 | -0.091553 | -0.10071 | -0.20599 | 0.004577 | 14.7491 | -0.073242 | 0.13275 | -0.054932 | 122.9141 | 122.8134 | 73.9197 | -123.0057 | 122.9095 | 122.85 | 74.5514 | -123.111
1599.5156 | 123.0835 | -58.4198 | 64.4577 | 0.2182 | 0.032539 | 0.071645 | 0.076909 | 0.13554 | 0.010453 | 0.0083207 | 0.2932 | 0.012117 | 0.0060178 | 0.0097176 | 0.0077502 | 0.0014525 | 64.3204 | 64.4485 | 15.39 | -56.6483 | 64.4394 | -58.4793 | -58.5251 | -43.6066 | 16.1499 | -58.4747 | 64.4531 | 64.3753 | -58.5526 | -58.6258 | -0.059509 | -0.10528 | -0.018311 | 122.8683 | 1.7715 | 1.8768 | -0.13733 | -0.13275 | -0.20599 | -0.004578 | 14.8132 | -0.054931 | 0.15106 | -0.082398 | 122.8592 | 122.7402 | 73.8098 | -122.9828 | 122.8729 | 122.7951 | 74.5697 | -123.0835
1600.5156 | 122.9965 | -58.461 | 64.4211 | -0.010681 | 0.035103 | 0.071858 | 0.079686 | 0.13191 | 0.014939 | 0.0081071 | 0.087204 | 0.012971 | 0.0079404 | 0.01164 | 0.009032 | 0.0029479 | 64.3295 | 64.4348 | 15.3259 | -56.6345 | 64.4485 | -58.4793 | -58.5617 | -43.5974 | 16.0995 | -58.5526 | 64.4577 | 64.4028 | -58.5754 | -58.699 | -0.01831 | -0.10071 | 0.027465 | 122.8958 | 1.8265 | 1.9272 | -0.091553 | -0.11444 | -0.23804 | 0.036621 | 14.8636 | -0.091552 | 0.14648 | -0.018311 | 122.9095 | 122.7905 | 73.7869 | -122.9828 | 122.9187 | 122.8638 | 74.5605 | -123.1201
1601.5312 | 123.1476 | -58.3282 | 64.5126 | -0.018311 | 0.029121 | -0.034099 | 0.076481 | 0.13426 | 0.0059666 | 0.0042619 | 0.1635 | 0.010621 | 0.0038816 | 0.010999 | 0.0049732 | 0.0046569 | 64.4073 | 64.5905 | 15.3351 | -56.543 | 64.5264 | -58.3694 | -58.4244 | -43.4052 | 16.2781 | -58.3282 | 64.5126 | 64.4623 | -58.4564 | -58.5617 | -0.041199 | -0.09613 | 0.013733 | 122.9187 | 1.7853 | 1.8814 | -0.10529 | -0.12817 | -0.23346 | 0 | 14.9231 | 0 | 0.23346 | -0.050354 | 122.8546 | 122.7356 | 73.6633 | -122.937 | 122.8409 | 122.7905 | 74.6063 | -123.0743
1602.5156 | 123.0148 | -58.3511 | 64.5584 | 0.035095 | 0.037452 | 0.071004 | 0.076695 | 0.13383 | 0.014939 | 0.0078933 | 0.071945 | 0.015535 | 0.0079404 | 0.0097176 | 0.0079638 | 0.00017094 | 64.4669 | 64.5355 | 15.1108 | -56.5109 | 64.5676 | -58.3466 | -58.4152 | -43.3685 | 16.2048 | -58.4335 | 64.5813 | 64.4943 | -58.4518 | -58.5434 | 0.004577 | -0.064087 | 0.009155 | 122.8867 | 1.8402 | 1.9043 | -0.091553 | -0.10071 | -0.19226 | 0.022888 | 14.9826 | -0.082398 | 0.10986 | -0.064087 | 122.9187 | 122.818 | 73.4619 | -122.9736 | 122.9324 | 122.8455 | 74.556 | -123.1018
1603.5156 | 123.0011 | -58.3374 | 64.5721 | 0.12665 | 0.035957 | 0.071858 | 0.076909 | 0.13041 | 0.01622 | 0.011525 | 0.46867 | 0.014894 | 0.0038816 | 0.010786 | 0.0079638 | 0.00081174 | 64.0869 | 64.7461 | 15.3442 | -56.4331 | 64.6225 | -58.3374 | -58.4198 | -43.3273 | 16.1911 | -58.4381 | 64.5859 | 64.5447 | -58.461 | -58.5709 | 0 | -0.082398 | 0.050354 | 123.0835 | 1.9043 | 1.9867 | -0.48523 | -0.1236 | -0.23346 | 0.013732 | 15.0101 | -0.10071 | 0.13275 | -0.027466 | 122.9599 | 122.4243 | 73.6816 | -122.9919 | 122.9233 | 122.8821 | 74.5285 | -123.143
1604.5156 | 122.9736 | -58.2184 | 64.682 | -0.10986 | 0.034035 | 0.070363 | 0.077977 | 0.13511 | 0.014511 | 0.0076797 | -0.011978 | 0.014253 | 0.0070858 | 0.0092904 | 0.0058276 | 0.0025207 | 64.5767 | 64.7141 | 15.2435 | -56.3828 | 64.6591 | -58.2687 | -58.3328 | -43.1442 | 16.3742 | -58.2825 | 64.6957 | 64.6271 | -58.3466 | -58.4702 | -0.050354 | -0.11444 | -0.022888 | 122.9324 | 1.8356 | 1.9501 | -0.10529 | -0.12817 | -0.25177 | 0.013733 | 15.0742 | -0.064087 | 0.18768 | -0.054932 | 122.8775 | 122.7951 | 73.4619 | -123.0148 | 122.9141 | 122.8455 | 74.5926 | -123.1522
1605.5156 | 123.111 | -58.2092 | 64.6133 | 0.09613 | 0.031257 | 0.070363 | 0.07584 | 0.13468 | 0.010666 | 0.0059707 | 0.36186 | 0.010621 | 0.0055906 | 0.0092904 | 0.007323 | 0.0035889 | 64.5584 | 64.7003 | 15.1749 | -56.3599 | 64.5859 | -58.2596 | -58.342 | -43.0252 | 16.3742 | -58.2458 | 64.5996 | 64.5493 | -58.3878 | -58.4518 | -0.050354 | -0.13275 | -0.027466 | 122.9095 | 1.8494 | 1.9821 | -0.054931 | -0.17853 | -0.24261 | -0.013733 | 15.184 | -0.036621 | 0.20599 | -0.064087 | 122.7951 | 122.7676 | 73.3841 | -122.9553 | 122.8088 | 122.7585 | 74.5834 | -123.0652
1606.5156 | 123.0515 | -58.2138 | 64.6957 | -0.079346 | 0.035103 | 0.071218 | 0.078618 | 0.13703 | 0.01622 | 0.0068253 | 0.033798 | 0.013398 | 0.0085812 | 0.010359 | 0.0088184 | -0.00047006 | 64.5905 | 64.7095 | 14.8041 | -56.3141 | 64.6866 | -58.2413 | -58.3191 | -43.0389 | 16.5344 | -58.2779 | 64.7232 | 64.6408 | -58.3282 | -58.4106 | -0.027466 | -0.10529 | -0.009156 | 122.9233 | 1.8997 | 2.005 | -0.10529 | -0.11444 | -0.19684 | 0.027466 | 15.1749 | -0.064087 | 0.13275 | -0.054932 | 122.9004 | 122.8043 | 73.0179 | -123.0148 | 122.937 | 122.8546 | 74.7482 | -123.1064
1607.5156 | 122.9782 | -58.2504 | 64.682 | 0.050354 | 0.038307 | 0.072072 | 0.077122 | 0.13447 | 0.016007 | 0.0091751 | 0.17876 | 0.014894 | 0.0085812 | 0.01164 | 0.0075366 | 0.0014525 | 64.4897 | 64.5905 | 14.7217 | -56.3416 | 64.6774 | -58.2779 | -58.3374 | -43.0252 | 16.2689 | -58.3832 | 64.682 | 64.563 | -58.4015 | -58.4747 | -0.027466 | -0.086975 | -0.004578 | 122.8409 | 1.9089 | 1.9958 | -0.19226 | -0.15106 | -0.2243 | 0 | 15.2252 | -0.13275 | 0.091552 | -0.11902 | 122.9279 | 122.7402 | 72.9721 | -123.0194 | 122.9324 | 122.8134 | 74.5193 | -123.1567
1608.5156 | 123.056 | -58.1909 | 64.7095 | -0.033569 | 0.038093 | 0.072927 | 0.07819 | 0.13532 | 0.013016 | 0.0066117 | 0.2169 | 0.013185 | 0.006445 | 0.010999 | 0.0088184 | 0.0012389 | 64.5996 | 64.5355 | 14.4058 | -56.2637 | 64.7141 | -58.2001 | -58.2687 | -42.8055 | 16.3559 | -58.2367 | 64.7141 | 64.6683 | -58.3008 | -58.4106 | -0.009155 | -0.07782 | 0.004577 | 122.7264 | 1.9272 | 2.005 | -0.10986 | -0.10986 | -0.21973 | 0.004577 | 15.3854 | -0.045776 | 0.17395 | -0.041199 | 122.905 | 122.7905 | 72.5967 | -122.9782 | 122.905 | 122.8592 | 74.5468 | -123.1201
1609.5312 | 123.1201 | -58.2642 | 64.6042 | -0.11749 | 0.036598 | 0.073781 | 0.074986 | 0.13319 | 0.014298 | 0.0061845 | -0.027237 | 0.013612 | 0.0045224 | 0.012068 | 0.0068958 | 0.00081174 | 64.5218 | 64.8514 | 14.3784 | -59.3308 | 64.7003 | -58.1863 | -58.2962 | -43.3731 | 16.3055 | -58.0444 | 64.595 | 64.6225 | -58.2825 | -58.4473 | 0.07782 | -0.032044 | 0.09613 | 123.1155 | -1.0666 | -1.0345 | -0.082397 | -0.018311 | -0.18311 | -0.009155 | 14.8911 | 0.21973 | 0.40283 | 0.018311 | 122.9645 | 122.7859 | 72.6425 | -122.9004 | 122.8592 | 122.8867 | 74.5697 | -123.0515
1610.5156 | 123.0972 | -56.3004 | 66.5314 | 0.18768 | 0.79774 | 0.0030719 | 0.074131 | 0.084482 | 0.75557 | 0.0051163 | -0.3553 | 0.01233 | 0.006445 | 0.014204 | 0.0086048 | 0.0020935 | -35.3027 | 66.5634 | -14.4012 | 64.5355 | 66.4536 | -56.2683 | -56.3187 | -40.7684 | 18.132 | -56.3095 | 66.5039 | 66.4261 | -56.4102 | -56.5063 | 0.032043 | -0.018311 | -0.07782 | 122.8638 | 120.8359 | 120.8542 | -101.8341 | -0.10986 | -0.20599 | -0.027466 | 15.5319 | -0.009155 | 0.19684 | -0.10529 | 122.7539 | 20.9976 | 41.8991 | -122.85 | 122.8043 | 122.7264 | 74.4324 | -123.0377
1611.5156 | 123.0194 | -56.3049 | 66.5176 | -0.10986 | 0.80201 | 0.0028583 | 0.077977 | 0.084695 | 0.75941 | 0.0046891 | 0.026169 | 0.013826 | 0.0075132 | 0.012068 | 0.0083912 | 0.00059814 | -34.7031 | 66.4673 | -14.4196 | 64.7507 | 66.5085 | -56.3004 | -56.3324 | -40.7135 | 18.0267 | -56.3965 | 66.5451 | 66.4764 | -56.4148 | -56.5247 | 0.004578 | -0.027465 | -0.009155 | 122.7722 | 121.0556 | 121.0831 | -101.2207 | -0.10986 | -0.21973 | 0.027466 | 15.5914 | -0.091552 | 0.12817 | -0.041199 | 122.8134 | 21.6019 | 41.8854 | -122.85 | 122.85 | 122.7814 | 74.3317 | -123.0423
1612.5156 | 122.9599 | -56.2637 | 66.568 | -0.23956 | 0.79945 | 0.0026447 | 0.078618 | 0.084695 | 0.75899 | 0.0049027 | -0.073013 | 0.014253 | 0.0075132 | 0.012708 | 0.0075366 | 0.0020935 | -35.6735 | 66.4627 | -14.8132 | 65.0391 | 66.5085 | -56.2317 | -56.3004 | -40.7227 | 18.1091 | -56.3553 | 66.5955 | 66.5268 | -56.3553 | -56.4835 | 0.032044 | -0.036621 | -0.059509 | 122.7264 | 121.3028 | 121.3394 | -102.2415 | -0.091553 | -0.21973 | 0.027466 | 15.5411 | -0.091553 | 0.12817 | -0.041199 | 122.7722 | 20.5902 | 41.4505 | -122.8683 | 122.8592 | 122.7905 | 74.3729 | -123.0515
1613.5156 | 122.9187 | -56.2546 | 66.5497 | 0.042725 | 0.80222 | 0.00029489 | 0.077336 | 0.088754 | 0.76262 | 0.0049027 | 0.049057 | 0.012544 | 0.01029 | 0.012708 | 0.0086048 | 0.0044433 | -34.6893 | 66.5131 | -14.7537 | 65.2679 | 66.4902 | -56.2225 | -56.282 | -40.5945 | 18.1641 | -56.3324 | 66.5634 | 66.4719 | -56.3644 | -56.4423 | 0.032044 | -0.027465 | -0.05951 | 122.7676 | 121.5225 | 121.55 | -101.239 | -0.10986 | -0.18768 | 0.013733 | 15.6601 | -0.077819 | 0.10986 | -0.07782 | 122.7448 | 21.5652 | 41.5009 | -122.8317 | 122.818 | 122.7264 | 74.4186 | -122.9919
1614.5156 | 122.9324 | -56.1127 | 66.6779 | -0.079346 | 0.80051 | 0.00093569 | 0.076695 | 0.085977 | 0.76155 | 0.0074661 | -0.042496 | 0.014039 | 0.0043088 | 0.010359 | 0.011168 | 0.0010253 | -35.6873 | 66.6321 | -15.1474 | 65.4785 | 66.6367 | -56.0669 | -56.1768 | -40.3976 | 18.306 | -56.1584 | 66.6824 | 66.6321 | -56.2225 | -56.3095 | 0.045776 | -0.064087 | -0.041198 | 122.7448 | 121.5912 | 121.6553 | -102.3651 | -0.10986 | -0.19684 | 0.004578 | 15.715 | -0.045776 | 0.15106 | -0.045776 | 122.7493 | 20.4254 | 40.9653 | -122.8546 | 122.7951 | 122.7448 | 74.4186 | -122.9874
1615.5156 | 122.9919 | -55.9433 | 66.7603 | 0.30975 | 0.80628 | 0.0017901 | 0.075413 | 0.084268 | 0.76134 | 0.0063981 | 0.33897 | 0.01233 | 0.0040952 | 0.011854 | 0.0071094 | 0.0025207 | -35.994 | 66.8289 | -15.2481 | 66.4536 | 66.6824 | -55.925 | -55.9937 | -40.1825 | 18.4891 | -55.9525 | 66.7465 | 66.6916 | -56.0898 | -56.1676 | 0.01831 | -0.050354 | -0.07782 | 122.7722 | 122.3969 | 122.4472 | -102.7542 | -0.14648 | -0.22431 | -0.013733 | 15.7608 | -0.009156 | 0.21515 | -0.068665 | 122.6257 | 19.9493 | 40.6952 | -122.7539 | 122.6898 | 122.6349 | 74.4324 | -122.9279
1616.5156 | 122.9462 | -56.1722 | 66.5863 | -0.16327 | 0.80415 | 0.0011493 | 0.077549 | 0.084054 | 0.76625 | 0.0063981 | -0.11116 | 0.013185 | 0.0068722 | 0.010572 | 0.0060412 | 0.0025207 | -35.8795 | 66.5222 | -15.5823 | 66.2521 | 66.5726 | -56.1447 | -56.2317 | -40.3839 | 18.2373 | -56.2225 | 66.5955 | 66.5543 | -56.2729 | -56.3828 | 0.027466 | -0.059509 | -0.013733 | 122.6944 | 122.4243 | 122.4838 | -102.4658 | -0.10071 | -0.21057 | 0.009155 | 15.7883 | -0.050354 | 0.16022 | -0.032044 | 122.7448 | 20.2927 | 40.5899 | -122.818 | 122.7676 | 122.7264 | 74.4095 | -122.9691
1617.5156 | 122.9279 | -55.9708 | 66.774 | -0.048828 | 0.80714 | 0.0028583 | 0.079258 | 0.085763 | 0.76689 | 0.0055435 | 0.026169 | 0.015107 | 0.0083676 | 0.014631 | 0.010527 | 0.0016663 | -36.1404 | 66.7374 | -15.6784 | 66.5085 | 66.7374 | -55.957 | -55.9891 | -40.1047 | 18.4341 | -56.044 | 66.7923 | 66.7282 | -56.0852 | -56.1996 | 0.013733 | -0.018311 | -0.036621 | 122.7081 | 122.4792 | 122.4976 | -102.9144 | -0.11444 | -0.22888 | 0.01831 | 15.8661 | -0.073242 | 0.15564 | -0.045777 | 122.7081 | 19.8303 | 40.2924 | -122.7631 | 122.7631 | 122.699 | 74.4049 | -122.9736
1618.5156 | 122.8455 | -55.8563 | 66.9113 | -0.1709 | 0.78471 | 8.1086e-05 | 0.09528 | 0.087259 | 0.76198 | 0.0038345 | -0.31715 | 0.012544 | 0.0077268 | 0.011427 | 0.0054004 | 0.0023071 | -36.1633 | 66.8152 | -15.8981 | 66.7465 | 66.893 | -55.7922 | -55.8701 | -39.9994 | 18.5074 | -55.9158 | 66.9296 | 66.8427 | -56.0028 | -56.0623 | 0.064087 | -0.013733 | -0.018311 | 122.6715 | 122.6028 | 122.6166 | -103.0746 | -0.14648 | -0.20599 | 0.01831 | 15.8569 | -0.05951 | 0.14648 | -0.068665 | 122.7493 | 19.693 | 39.9582 | -122.7814 | 122.7859 | 122.699 | 74.3637 | -122.9736
1619.5312 | 122.9874 | -55.8563 | 66.7877 | -0.84991 | 0.7674 | 0.0032855 | 0.10874 | 0.085336 | 0.76219 | 0.0051163 | 0.3466 | 0.013185 | 0.0049496 | 0.01164 | 0.0077502 | 0.0018799 | -36.2 | 66.861 | -15.921 | 66.6229 | 66.7145 | -55.8517 | -55.9158 | -39.8895 | 18.5349 | -55.8975 | 66.8015 | 66.7099 | -56.0211 | -56.1218 | 0.004577 | -0.05951 | -0.073242 | 122.7173 | 122.4792 | 122.5388 | -102.9877 | -0.16479 | -0.2655 | 0.013733 | 15.9668 | -0.041199 | 0.2243 | -0.07782 | 122.5708 | 19.6564 | 39.9353 | -122.7036 | 122.6578 | 122.5662 | 74.3912 | -122.9095
1620.5156 | 122.8683 | -55.8609 | 66.8564 | 0.027466 | 0.75181 | 0.0015765 | 0.1363 | 0.087045 | 0.76604 | 0.0072525 | 0.064316 | 0.017244 | 0.0096494 | 0.012922 | 0.010955 | 0.0012389 | -36.2045 | 66.7648 | -16.1179 | 66.6275 | 66.8152 | -55.8563 | -55.9113 | -39.8758 | 18.4937 | -55.9799 | 66.9022 | 66.8381 | -55.9937 | -56.0852 | 0.004578 | -0.050354 | -0.041198 | 122.6257 | 122.4884 | 122.5388 | -103.0609 | -0.13275 | -0.2243 | 0.045777 | 15.9851 | -0.11902 | 0.10529 | -0.01831 | 122.6761 | 19.6564 | 39.743 | -122.7676 | 122.7631 | 122.699 | 74.3546 | -122.9416
1621.5156 | 122.8775 | -55.9479 | 66.7648 | 0.057983 | 0.81654 | 0.0022175 | 0.15937 | 0.11631 | 0.76561 | 0.0051163 | 0.087204 | 0.015535 | 0.0083676 | 0.012922 | 0.0086048 | 0.0014525 | -36.2503 | 66.7053 | -16.1819 | 66.5817 | 66.7374 | -55.7053 | -55.925 | -39.8712 | 18.4937 | -56.044 | 66.7969 | 66.7511 | -56.0577 | -56.1401 | 0.24262 | 0.022888 | -0.027466 | 122.6532 | 122.5296 | 122.5067 | -103.0151 | -0.10986 | -0.19226 | 0.032043 | 16.0767 | -0.09613 | 0.096131 | -0.013733 | 122.6852 | 19.6976 | 39.7659 | -122.6898 | 122.7448 | 122.699 | 74.4415 | -122.905
1622.5156 | 122.7997 | -55.838 | 66.8427 | -0.13275 | 0.8473 | 0.0015765 | 0.2305 | 0.098367 | 0.76454 | 0.0044755 | -0.065384 | 0.015962 | 0.0075132 | 0.011213 | 0.0081776 | 0.00017094 | -36.2045 | 66.7557 | -16.1865 | 66.6595 | 66.7969 | -55.7785 | -55.8975 | -39.7247 | 18.576 | -55.9158 | 66.8655 | 66.8152 | -55.9433 | -56.044 | 0.05951 | -0.059509 | -0.045776 | 122.5937 | 122.4976 | 122.5571 | -103.0472 | -0.10529 | -0.20599 | 0.022889 | 16.1133 | -0.07782 | 0.12817 | -0.027465 | 122.6349 | 19.6335 | 39.6515 | -122.7402 | 122.7036 | 122.6532 | 74.4141 | -122.8867
1623.5156 | 122.8867 | -55.9845 | 66.7374 | -0.17853 | 0.70737 | -0.00034611 | 0.20551 | 0.11738 | 0.76454 | 0.0051163 | 0.01091 | 0.015321 | 0.0072994 | 0.010145 | 0.010314 | 0.00081174 | -36.2411 | 66.6641 | -15.9164 | 66.5451 | 66.6595 | -55.9616 | -56.0028 | -39.8071 | 18.5165 | -56.1447 | 66.7099 | 66.6412 | -56.1264 | -56.2088 | 0.022888 | -0.018311 | -0.07782 | 122.6486 | 122.5296 | 122.5479 | -102.9785 | -0.14191 | -0.2243 | -0.027466 | 16.1774 | -0.16022 | 0.064087 | -0.096131 | 122.644 | 19.7433 | 40.0681 | -122.7402 | 122.6944 | 122.6257 | 74.501 | -122.9462
1624.5156 | 122.8226 | -58.3374 | 64.4714 | -0.16327 | 0.0094677 | 0.0022175 | 0.014531 | -0.03002 | 0.010666 | -0.00022432 | -0.14168 | 0.012971 | 0.0055906 | 0.012068 | 0.0079638 | 0.0042297 | -2.2018 | -2.2705 | -2.6001 | -2.5681 | -2.1561 | -2.4353 | -2.5818 | -41.9907 | 16.6351 | -58.3694 | 64.476 | 64.3982 | -58.4152 | -58.5114 | 55.9021 | 55.7556 | -66.6275 | 56.0669 | 55.7693 | 0.013733 | -66.6733 | -0.07782 | -0.17395 | 0.004577 | 16.3467 | -0.032044 | 0.14191 | -0.073243 | 56.1813 | 56.1356 | 55.7373 | -67.0532 | 122.8134 | 122.7356 | 74.9725 | -122.9828
1625.5156 | 122.8775 | -58.3191 | 64.4897 | -0.16327 | 0.013527 | 0.0032855 | 0.014103 | -0.018057 | 0.002335 | 0.00084388 | -0.0043486 | 0.013612 | 0.0070858 | 0.011854 | 0.0096728 | 0.0020935 | -2.3987 | -2.3529 | -2.5085 | -2.3438 | -2.0874 | -2.3712 | -2.5406 | -41.9586 | 16.713 | -58.3649 | 64.4806 | 64.4073 | -58.4198 | -58.493 | 55.9479 | 55.7785 | -66.5771 | 55.9662 | 55.9753 | 0.19684 | -66.8884 | -0.10071 | -0.17395 | -0.009155 | 16.3605 | -0.045776 | 0.12817 | -0.082397 | 56.2317 | 55.9204 | 55.8105 | -67.0303 | 122.7997 | 122.7264 | 75.032 | -122.9828
1626.5156 | 122.9599 | -58.2733 | 64.4485 | -0.14038 | 0.0086133 | 0.0026447 | 0.01389 | -0.01763 | -0.002792 | 0.0023391 | -0.095902 | 0.013826 | 0.0058042 | 0.010572 | 0.0060412 | 0.0027343 | -2.2705 | -2.1835 | -2.3483 | -2.1973 | -2.0554 | -2.3026 | -2.4353 | -41.8121 | 16.8411 | -58.2687 | 64.4623 | 64.4119 | -58.4244 | -58.493 | 55.9708 | 55.838 | -66.5039 | 56.0898 | 56.076 | 0.23804 | -66.7191 | -0.15106 | -0.21973 | 0.013733 | 16.4612 | 0.004577 | 0.2243 | -0.036621 | 56.218 | 56.0028 | 55.925 | -66.8839 | 122.7356 | 122.6852 | 75.1144 | -122.9416
1627.5156 | 122.9324 | -58.2687 | 64.5264 | -0.14038 | 0.014595 | 0.0030719 | 0.01389 | -0.018485 | 0.004044 | 0.0031937 | -0.10353 | 0.01468 | 0.0083676 | 0.014204 | 0.0083912 | 0.0016663 | -2.2705 | -2.2522 | -2.417 | -2.2476 | -2.037 | -2.3163 | -2.4445 | -41.835 | 16.7908 | -58.3099 | 64.5538 | 64.4485 | -58.3969 | -58.4747 | 55.9525 | 55.8243 | -66.5634 | 56.0165 | 56.0211 | 0.19684 | -66.7969 | -0.12817 | -0.20599 | 0.027466 | 16.4337 | -0.041199 | 0.16479 | -0.07782 | 56.2317 | 55.9982 | 55.8517 | -66.9708 | 122.8226 | 122.7173 | 75.0595 | -123.0011
1628.5156 | 122.9233 | -58.2596 | 64.5538 | -0.18616 | 0.0083997 | 0.0060627 | 0.014103 | -0.016135 | -0.00022865 | 0.0046891 | -0.14931 | 0.012758 | 0.0070858 | 0.0097176 | 0.0064686 | 0.0031615 | -2.2751 | -2.2339 | -2.3758 | -2.243 | -1.9775 | -2.2797 | -2.4353 | -41.7389 | 16.6168 | -58.3008 | 64.5493 | 64.4852 | -58.4198 | -58.493 | 55.9799 | 55.8243 | -66.5314 | 56.0257 | 56.0165 | 0.19226 | -66.8289 | -0.16022 | -0.23346 | -0.004578 | 16.5207 | -0.041198 | 0.19226 | -0.068665 | 56.282 | 55.9845 | 55.8838 | -66.9891 | 122.8088 | 122.7448 | 74.8764 | -123.0469
1629.5312 | 122.9462 | -58.255 | 64.5493 | -0.1709 | 0.0094677 | 0.0034991 | 0.013035 | -0.019553 | -0.0032192 | 0.0012711 | -0.14931 | 0.013826 | 0.006445 | 0.012281 | 0.0054004 | 0.0012389 | -2.1927 | -2.092 | -2.2659 | -2.1378 | -1.973 | -2.2064 | -2.3483 | -41.684 | 16.9052 | -58.2779 | 64.563 | 64.4714 | -58.374 | -58.4473 | 56.0486 | 55.9067 | -66.5222 | 56.163 | 56.1172 | 0.21057 | -66.7419 | -0.11902 | -0.19226 | 0.013733 | 16.571 | -0.022888 | 0.16937 | -0.077819 | 56.282 | 56.0623 | 55.9891 | -66.8976 | 122.818 | 122.7264 | 75.1602 | -122.9965
1630.5156 | 122.9645 | -58.2321 | 64.5859 | -0.20142 | 0.010322 | 0.0034991 | 0.013249 | -0.020407 | -0.0012966 | 0.0016983 | -0.18745 | 0.013612 | 0.0070858 | 0.011213 | 0.0101 | 0.0023071 | -2.1835 | -2.092 | -2.2614 | -2.1194 | -1.9547 | -2.1881 | -2.3438 | -41.6519 | 16.8961 | -58.2596 | 64.595 | 64.5218 | -58.3649 | -58.4381 | 56.044 | 55.8884 | -66.5405 | 56.1401 | 56.1127 | 0.2243 | -66.7694 | -0.13275 | -0.20599 | 0.009156 | 16.5802 | -0.027466 | 0.17853 | -0.064086 | 56.2775 | 56.0486 | 55.9708 | -66.9296 | 122.8271 | 122.7539 | 75.1282 | -123.024
1631.5156 | 122.9416 | -58.2321 | 64.5996 | -0.018311 | 0.016304 | 0.00093569 | 0.012394 | -0.020407 | 0.0046848 | 0.0049027 | -0.057755 | 0.015962 | 0.0087948 | 0.012708 | 0.0101 | 0.0010253 | -2.1744 | -2.1744 | -2.298 | -2.1744 | -1.9592 | -2.2202 | -2.3758 | -41.597 | 16.8686 | -58.2962 | 64.6179 | 64.5401 | -58.3466 | -58.4656 | 56.012 | 55.8563 | -66.5588 | 56.0577 | 56.0577 | 0.20142 | -66.774 | -0.11444 | -0.23346 | 0.018311 | 16.6351 | -0.064087 | 0.16937 | -0.059509 | 56.2729 | 56.0577 | 55.9341 | -66.9754 | 122.85 | 122.7722 | 75.1007 | -123.0652
1632.5156 | 123.0835 | -58.1543 | 64.6225 | -0.16327 | 0.0062635 | 0.0032855 | 0.013676 | -0.017417 | -0.0030056 | 0.0068253 | 0.079574 | 0.011903 | 0.0062314 | 0.013136 | 0.0079638 | 0.0038025 | -2.4445 | -2.0554 | -2.1378 | -2.0828 | -1.9501 | -2.1606 | -2.3254 | -41.4459 | 17.0425 | -58.1451 | 64.6225 | 64.5401 | -58.2687 | -58.3786 | 55.9937 | 55.8289 | -66.5726 | 56.0989 | 56.0715 | 0.24261 | -67.067 | -0.11444 | -0.2243 | 0 | 16.7084 | 0.009155 | 0.23346 | -0.082398 | 56.2042 | 55.7098 | 56.0165 | -66.9479 | 122.7768 | 122.6944 | 75.1968 | -123.0011
1633.5156 | 122.9599 | -58.2001 | 64.6408 | -0.16327 | 0.0086133 | 0.0039263 | 0.012822 | -0.018912 | -0.0023648 | 0.0023391 | -0.1722 | 0.014467 | 0.0072994 | 0.012495 | 0.0075366 | 0.0016663 | -2.1286 | -2.0691 | -2.2293 | -2.0874 | -1.9226 | -2.1652 | -2.3071 | -41.4734 | 16.9464 | -58.2367 | 64.65 | 64.563 | -58.3282 | -58.4015 | 56.0349 | 55.8929 | -66.5634 | 56.131 | 56.1127 | 0.21973 | -66.7694 | -0.12817 | -0.20142 | 0.009155 | 16.7267 | -0.036621 | 0.16479 | -0.07782 | 56.2775 | 56.0715 | 55.9708 | -66.9479 | 122.85 | 122.7631 | 75.1465 | -123.0423
1634.5156 | 123.0698 | -58.1589 | 64.6271 | -0.1709 | 0.0079723 | 0.0032855 | 0.013463 | -0.020194 | -0.00044225 | 0.0021255 | -0.095902 | 0.01468 | 0.006445 | 0.01399 | 0.0083912 | 0.0018799 | -2.1561 | -2.0187 | -2.1744 | -2.1011 | -1.9913 | -2.179 | -2.33 | -41.3544 | 17.0288 | -58.1268 | 64.6088 | 64.5767 | -58.287 | -58.3969 | 55.9799 | 55.8289 | -66.6183 | 56.1401 | 56.0577 | 0.22888 | -66.7831 | -0.12817 | -0.23804 | -0.01831 | 16.8045 | 0.032044 | 0.27008 | -0.050354 | 56.1676 | 56.0028 | 55.9845 | -66.9571 | 122.7676 | 122.7356 | 75.1877 | -123.024
1635.5156 | 122.9416 | -58.2138 | 64.6362 | 0.09613 | 0.017158 | 0.0022175 | 0.015599 | -0.020835 | 0.0053256 | 0.0057571 | 0.079574 | 0.016816 | 0.0087948 | 0.015486 | 0.012877 | 0.00059814 | -2.2568 | -2.2705 | -2.3849 | -2.2247 | -1.9592 | -2.2293 | -2.4078 | -41.3589 | 17.1707 | -58.3145 | 64.6637 | 64.563 | -58.3466 | -58.429 | 55.9845 | 55.806 | -66.5955 | 55.9433 | 55.9891 | 0.18311 | -66.893 | -0.13275 | -0.21515 | 0.027466 | 16.8549 | -0.10071 | 0.11444 | -0.073242 | 56.2546 | 55.957 | 55.8289 | -67.0441 | 122.8775 | 122.7768 | 75.3845 | -123.0652
1636.5156 | 123.0606 | -58.1543 | 64.6408 | -0.18616 | 0.0081861 | 0.0045673 | 0.012181 | -0.019766 | -0.00065585 | 0.0040481 | -0.088272 | 0.012971 | 0.0049496 | 0.011427 | 0.0071094 | 0.0020935 | -2.1149 | -2.0325 | -2.1744 | -2.0874 | -1.9638 | -2.1698 | -2.3026 | -41.2537 | 17.0517 | -58.1268 | 64.6545 | 64.5905 | -58.2779 | -58.374 | 55.9845 | 55.8517 | -66.6046 | 56.1218 | 56.0669 | 0.21515 | -66.7557 | -0.1236 | -0.21973 | 0.013733 | 16.9006 | 0.027466 | 0.24719 | -0.050354 | 56.1905 | 56.0394 | 55.9799 | -66.9434 | 122.8088 | 122.7448 | 75.206 | -123.0148
1637.5156 | 122.9919 | -58.2001 | 64.6729 | -0.18616 | 0.015663 | 0.0011493 | 0.011113 | -0.017203 | 0.0019078 | 0.0044755 | -0.20271 | 0.015321 | 0.0085812 | 0.01164 | 0.0101 | 0.0018799 | -2.2568 | -2.2385 | -2.3895 | -2.2293 | -2.0142 | -2.2934 | -2.4628 | -41.272 | 16.9601 | -58.223 | 64.7049 | 64.5996 | -58.3054 | -58.4198 | 55.9067 | 55.7373 | -66.687 | 55.9616 | 55.9708 | 0.23346 | -66.9296 | -0.10529 | -0.21973 | 0.032043 | 16.9281 | -0.022888 | 0.19684 | -0.073243 | 56.1859 | 55.9433 | 55.8105 | -67.1356 | 122.905 | 122.7997 | 75.1602 | -123.0927
1638.5312 | 123.0972 | -58.168 | 64.6225 | 0.18768 | 0.013527 | 0.0041401 | 0.012608 | -0.020835 | 0.0019078 | 0.0042619 | -0.027237 | 0.013185 | 0.0075132 | 0.012495 | 0.0096728 | 0.0052979 | -2.1652 | -2.2202 | -2.4765 | -2.3575 | -2.0462 | -2.2339 | -2.3712 | -41.1438 | 16.9876 | -58.1863 | 64.6133 | 64.5355 | -58.2962 | -58.4061 | 55.9341 | 55.7968 | -66.6687 | 55.9479 | 55.8105 | 0.013733 | -66.7877 | -0.12817 | -0.23804 | -0.009156 | 17.0242 | -0.01831 | 0.21973 | -0.086976 | 56.1218 | 56.0028 | 55.6915 | -66.9937 | 122.7814 | 122.7036 | 75.1556 | -123.0286
1639.5312 | 123.143 | -58.1314 | 64.6454 | -0.033569 | 0.0051953 | -0.034099 | 0.010472 | -0.020194 | -0.0038602 | 0.0029801 | 0.0032804 | 0.012117 | 0.0058042 | 0.011213 | 0.0077502 | 0.0031615 | -2.2064 | -2.1378 | -2.2888 | -2.179 | -2.0599 | -2.2568 | -2.4124 | -41.0797 | 17.0883 | -58.0948 | 64.6545 | 64.6225 | -58.2367 | -58.3603 | 55.8746 | 55.719 | -66.7053 | 55.9937 | 55.9525 | 0.23346 | -66.8518 | -0.10529 | -0.22888 | 0.009155 | 17.0517 | 0.036621 | 0.2655 | -0.022888 | 56.0715 | 55.925 | 55.8426 | -67.0578 | 122.7859 | 122.7539 | 75.2197 | -123.0057
1640.5156 | 123.2895 | -58.1131 | 64.7049 | -0.14038 | 0.0071179 | 0.0037127 | 0.013463 | -0.019766 | -0.002792 | 0.0023391 | -0.0043486 | 0.013826 | 0.0066586 | 0.010145 | 0.006255 | 0.0014525 | -2.179 | -2.1057 | -2.2476 | -2.1835 | -2.0554 | -2.2522 | -2.3849 | -41.0294 | 17.1387 | -58.0811 | 64.6408 | 64.6271 | -58.2596 | -58.3328 | 55.8609 | 55.7281 | -66.7603 | 56.0074 | 55.9296 | 0.20142 | -66.8838 | -0.14648 | -0.21973 | -0.064087 | 17.0837 | 0.032043 | 0.25177 | -0.07782 | 56.0577 | 55.9341 | 55.8655 | -67.0898 | 122.7539 | 122.7402 | 75.2518 | -123.0377
1641.5156 | 123.056 | -58.1726 | 64.7186 | -0.14038 | 0.0096813 | 0.0024311 | 0.014103 | -0.013999 | 0.00019875 | 0.0021255 | -0.11879 | 0.014894 | 0.0079404 | 0.011427 | 0.0079638 | 0.0020935 | -2.2522 | -2.1881 | -2.3209 | -2.2202 | -2.092 | -2.3071 | -2.4399 | -41.0522 | 17.0746 | -58.1497 | 64.6729 | 64.6088 | -58.2733 | -58.3786 | 55.8655 | 55.7327 | -66.8106 | 55.9845 | 55.9525 | 0.21973 | -66.9708 | -0.10071 | -0.20599 | -0.045776 | 17.1204 | 0.022888 | 0.22888 | -0.10986 | 56.0806 | 55.9204 | 55.8517 | -67.1585 | 122.8455 | 122.7814 | 75.2472 | -123.0972
1642.5156 | 123.1201 | -58.1451 | 64.6637 | -0.086975 | 0.0051953 | 0.0058491 | 0.012181 | -0.020621 | -1.505e-05 | 0.0025529 | -0.0043486 | 0.015748 | 0.0072994 | 0.010145 | 0.007323 | 0.0052979 | -2.2156 | -2.1103 | -2.2797 | -2.1973 | -2.0782 | -2.2934 | -2.4353 | -40.9973 | 17.1341 | -58.0856 | 64.6774 | 64.5813 | -58.2504 | -58.3466 | 55.8517 | 55.7098 | -66.7419 | 56.0349 | 55.9479 | 0.23804 | -66.8793 | -0.10529 | -0.20142 | 0.013733 | 17.1478 | 0.05951 | 0.26093 | -0.082397 | 56.0669 | 55.9296 | 55.8655 | -67.099 | 122.8226 | 122.7264 | 75.2792 | -123.0103
1643.5156 | 123.0057 | -58.1543 | 64.7507 | -0.18616 | 0.0077587 | 0.0013629 | 0.01154 | -0.018057 | 0.0019078 | 0.0034073 | -0.21797 | 0.014894 | 0.0085812 | 0.012708 | 0.0071094 | 0.0020935 | -2.2888 | -2.2018 | -2.3849 | -2.2568 | -2.0874 | -2.3254 | -2.4811 | -40.979 | 17.0746 | -58.1497 | 64.7598 | 64.6545 | -58.2825 | -58.374 | 55.8289 | 55.6732 | -66.8381 | 55.9525 | 55.8975 | 0.2243 | -67.0395 | -0.12817 | -0.21973 | 0.009156 | 17.1753 | 0.004578 | 0.2243 | -0.09613 | 56.0669 | 55.8655 | 55.7693 | -67.2317 | 122.9141 | 122.8088 | 75.2289 | -123.1247
1644.5156 | 123.1613 | -58.1314 | 64.6912 | -0.056458 | 0.0069043 | 0.0034991 | 0.013463 | -0.021689 | -1.505e-05 | 0.0044755 | -0.050125 | 0.012971 | 0.0045224 | 0.012068 | 0.007323 | 0.0029479 | -2.2659 | -2.179 | -2.3666 | -2.2659 | -2.1378 | -2.3392 | -2.4902 | -40.8829 | 17.1982 | -58.0765 | 64.682 | 64.6088 | -58.2504 | -58.3969 | 55.7922 | 55.6412 | -66.8289 | 55.9525 | 55.8655 | 0.2243 | -66.9571 | -0.11902 | -0.2655 | -0.009155 | 17.2485 | 0.054932 | 0.32044 | -0.082397 | 55.9937 | 55.8655 | 55.7648 | -67.1814 | 122.8134 | 122.7402 | 75.3296 | -123.0881
1645.5156 | 123.0469 | -58.1589 | 64.7049 | -0.14038 | 0.0083997 | 0.0047809 | 0.014744 | -0.019766 | 0.00062595 | 0.0019119 | -0.14931 | 0.01468 | 0.0051632 | 0.012068 | 0.0071094 | 0.0020935 | -2.2156 | -2.1194 | -2.3071 | -2.1744 | -2.0737 | -2.2614 | -2.4124 | -40.892 | 17.1341 | -58.136 | 64.7049 | 64.6088 | -58.287 | -58.374 | 55.8975 | 55.7465 | -66.7786 | 56.0394 | 55.9845 | 0.23804 | -66.9205 | -0.12817 | -0.21515 | 0 | 17.2668 | 0.022889 | 0.23804 | -0.09613 | 56.0852 | 55.9433 | 55.8517 | -67.1173 | 122.8638 | 122.7676 | 75.293 | -123.0789
1646.5156 | 123.0835 | -58.168 | 64.6729 | 0.18768 | 0.0056225 | 0.0041401 | 0.011326 | -0.018271 | -0.0012966 | 0.0031937 | 0.018539 | 0.012758 | 0.0058042 | 0.014845 | 0.0083912 | 0.0025207 | -2.3575 | -2.2888 | -2.4536 | -2.3071 | -2.1332 | -2.3575 | -2.4857 | -40.8783 | 17.1478 | -58.168 | 64.6912 | 64.5538 | -58.3008 | -58.3878 | 55.8105 | 55.6824 | -66.806 | 55.8792 | 55.8609 | 0.17853 | -67.0303 | -0.13275 | -0.21973 | 0.01831 | 17.2897 | 0 | 0.21973 | -0.11902 | 56.0349 | 55.8105 | 55.7144 | -67.1585 | 122.8592 | 122.7219 | 75.3159 | -123.0606
1647.5156 | 123.0789 | -58.1726 | 64.7095 | -0.20905 | 0.0090405 | 0.0028583 | 0.010899 | -0.018057 | 0.0010532 | 0.0023391 | -0.19508 | 0.015535 | 0.0053768 | 0.010572 | 0.0098866 | 0.00081174 | -2.3209 | -2.2659 | -2.4582 | -2.3071 | -2.1561 | -2.3849 | -2.5314 | -40.8325 | 17.1387 | -58.1726 | 64.7049 | 64.6042 | -58.2916 | -58.3694 | 55.7877 | 55.6412 | -66.8655 | 55.9067 | 55.8655 | 0.2243 | -67.0303 | -0.11902 | -0.19684 | -0.004578 | 17.3401 | 0 | 0.19684 | -0.10529 | 56.0165 | 55.8517 | 55.7144 | -67.2409 | 122.8775 | 122.7768 | 75.3113 | -123.0789
1648.5156 | 123.1293 | -58.1818 | 64.6591 | 0.0045777 | 0.0058361 | 0.0054217 | 0.013035 | -0.020621 | -0.001083 | 0.0021255 | 0.0032804 | 0.014253 | 0.006445 | 0.01164 | 0.0101 | 0.0018799 | -2.3163 | -2.243 | -2.4078 | -2.2705 | -2.1194 | -2.3254 | -2.4948 | -40.8096 | 17.1204 | -58.1635 | 64.6637 | 64.5538 | -58.3282 | -58.4244 | 55.8563 | 55.687 | -66.7786 | 55.9387 | 55.9113 | 0.2243 | -66.9754 | -0.14648 | -0.24261 | 0.004577 | 17.3721 | 0.018311 | 0.26093 | -0.10529 | 56.0623 | 55.8655 | 55.7739 | -67.1539 | 122.8455 | 122.7356 | 75.3021 | -123.0835
1649.5156 | 123.1155 | -58.1635 | 64.6729 | -0.10986 | 0.0092541 | 0.0039263 | 0.01389 | -0.019339 | 0.0014804 | 0.0040481 | -0.15694 | 0.015107 | 0.0058042 | 0.012495 | 0.009032 | 0.00017094 | -2.2385 | -2.1606 | -2.3621 | -2.211 | -2.1149 | -2.3026 | -2.4445 | -40.7593 | 17.1707 | -58.1451 | 64.682 | 64.563 | -58.3099 | -58.4015 | 55.8609 | 55.719 | -66.7877 | 56.0028 | 55.9525 | 0.23346 | -66.9113 | -0.14648 | -0.23804 | 0.009155 | 17.4042 | 0.01831 | 0.25635 | -0.10986 | 56.0486 | 55.925 | 55.8014 | -67.1173 | 122.8455 | 122.7264 | 75.3342 | -123.0743
1650.5156 | 123.143 | -58.1223 | 64.6957 | -0.018311 | 0.0069043 | 0.0037127 | 0.010685 | -0.01998 | -0.00086945 | 0.0016983 | -0.057755 | 0.015748 | 0.0045224 | 0.013349 | 0.0075366 | 0.0020935 | -2.3071 | -2.2385 | -2.4261 | -2.2751 | -2.1286 | -2.3346 | -2.4857 | -40.6494 | 17.2394 | -58.0902 | 64.7232 | 64.6179 | -58.2413 | -58.3237 | 55.7877 | 55.6366 | -66.8243 | 55.8838 | 55.8472 | 0.21057 | -67.0029 | -0.11902 | -0.20142 | 0.027466 | 17.4728 | 0.032043 | 0.23346 | -0.07782 | 55.9937 | 55.8151 | 55.6961 | -67.1814 | 122.8455 | 122.7402 | 75.3616 | -123.0194
1651.5156 | 123.1567 | -58.1543 | 64.6591 | -0.14801 | 0.0062635 | 0.0026447 | 0.012608 | -0.016989 | -0.0070644 | 0.0027665 | 0.1635 | 0.015321 | 0.003668 | 0.013349 | 0.0083912 | 0.0031615 | -1.9592 | -2.5177 | -2.5589 | -2.2202 | -2.092 | -2.3071 | -2.4719 | -40.6311 | 17.189 | -58.1177 | 64.6866 | 64.5905 | -58.2733 | -58.3511 | 55.8472 | 55.6824 | -66.7511 | 55.6366 | 55.9341 | 0.25177 | -66.6183 | -0.11902 | -0.19684 | 0.027465 | 17.5232 | 0.036621 | 0.23346 | -0.068665 | 56.0623 | 56.1951 | 55.5954 | -67.131 | 122.8409 | 122.7448 | 75.3433 | -123.0103
1652.5156 | 123.1064 | -58.1635 | 64.6774 | 0.11139 | 0.0077587 | 0.0030719 | 0.014317 | -0.017203 | 0.001694 | 0.0016983 | 0.041427 | 0.014467 | 0.0055906 | 0.014204 | 0.0096728 | 0.0029479 | -2.3346 | -2.2659 | -2.4399 | -2.2934 | -2.1286 | -2.3346 | -2.5085 | -40.6128 | 17.1295 | -58.1635 | 64.6774 | 64.5721 | -58.2916 | -58.3969 | 55.8289 | 55.6549 | -66.806 | 55.8975 | 55.8701 | 0.21515 | -67.012 | -0.12817 | -0.23346 | 0 | 17.5507 | 0 | 0.23346 | -0.10529 | 56.0349 | 55.8289 | 55.7236 | -67.186 | 122.8409 | 122.7356 | 75.293 | -123.0743
1653.5156 | 123.175 | -58.1543 | 64.6683 | 0.88959 | 0.0060497 | 0.0043537 | 0.012822 | -0.01763 | 0.00041235 | 0.0031937 | -0.12642 | 0.014894 | 0.0060178 | 0.012922 | 0.0098866 | 0.0012389 | -2.3163 | -2.2751 | -2.4673 | -2.3071 | -2.2202 | -2.4033 | -2.5635 | -40.5579 | 17.276 | -58.1223 | 64.6774 | 64.5676 | -58.2825 | -58.4061 | 55.751 | 55.5908 | -66.8884 | 55.8792 | 55.8472 | 0.25635 | -66.9846 | -0.12817 | -0.25177 | 0.009155 | 17.5964 | 0.032044 | 0.28381 | -0.10071 | 55.9341 | 55.838 | 55.687 | -67.2318 | 122.8317 | 122.7219 | 75.4303 | -123.0743
1654.5312 | 123.1293 | -58.1772 | 64.6454 | 0.16479 | 0.012031 | 0.0013629 | 0.011967 | -0.021048 | 0.0029758 | 0.0031937 | 0.19402 | 0.015748 | 0.0060178 | 0.011854 | 0.0094592 | 0.0029479 | -2.3254 | -2.2614 | -2.4673 | -2.3346 | -2.1973 | -2.3712 | -2.5223 | -40.5396 | 17.1295 | -58.1726 | 64.65 | 64.5401 | -58.3282 | -58.4244 | 55.806 | 55.6549 | -66.8427 | 55.9158 | 55.8426 | 0.18768 | -66.9708 | -0.15106 | -0.24719 | 0.004577 | 17.6376 | 0.004578 | 0.25177 | -0.10529 | 55.9799 | 55.8517 | 55.7098 | -67.1677 | 122.8271 | 122.7173 | 75.3067 | -123.0698
1655.5156 | 123.143 | -58.1635 | 64.7095 | -0.033569 | 0.0073315 | 0.0024311 | 0.012181 | -0.021689 | -0.0019376 | 0.0031937 | -0.034867 | 0.015107 | 0.0062314 | 0.012495 | 0.0075366 | 0.0035889 | -2.3163 | -2.2705 | -2.4765 | -2.3026 | -2.1515 | -2.3621 | -2.5314 | -40.4572 | 17.2028 | -58.1177 | 64.7095 | 64.6088 | -58.2733 | -58.374 | 55.8014 | 55.632 | -66.861 | 55.8929 | 55.8609 | 0.22888 | -67.0258 | -0.10986 | -0.21057 | 0 | 17.7063 | 0.045776 | 0.25635 | -0.10071 | 56.012 | 55.8472 | 55.687 | -67.2409 | 122.8729 | 122.7722 | 75.3662 | -123.0835
1656.5156 | 123.1659 | -58.1635 | 64.6957 | -0.18616 | 0.0062635 | 0.0039263 | 0.013676 | -0.018485 | 0.0036166 | -0.00086512 | -0.073013 | 0.016603 | 0.0034542 | 0.012068 | 0.0092456 | 0.0031615 | -2.0325 | -2.6184 | -2.7008 | -2.3666 | -2.1973 | -2.3987 | -2.5772 | -40.4388 | 17.2623 | -58.0994 | 64.6957 | 64.5905 | -58.2916 | -58.3694 | 55.7648 | 55.5862 | -66.893 | 55.545 | 55.7968 | 0.21057 | -66.7282 | -0.12817 | -0.20599 | 0 | 17.7246 | 0.064087 | 0.27008 | -0.10529 | 55.9662 | 56.131 | 55.4626 | -67.2729 | 122.8592 | 122.7539 | 75.4257 | -123.0652
1657.5156 | 123.1293 | -58.1818 | 64.682 | -0.056458 | 0.0096813 | 0.0026447 | 0.013035 | -0.019339 | 0.00062595 | 0.0044755 | 0.033798 | 0.014467 | 0.0060178 | 0.013349 | 0.0086048 | 0.0038025 | -2.2888 | -2.2247 | -2.4216 | -2.2842 | -2.1194 | -2.3254 | -2.4902 | -40.4114 | 17.157 | -58.1177 | 64.7141 | 64.6088 | -58.2825 | -58.3557 | 55.8563 | 55.6915 | -66.8015 | 55.957 | 55.8975 | 0.20599 | -66.9708 | -0.10071 | -0.17395 | 0.032043 | 17.7704 | 0.064087 | 0.23804 | -0.073242 | 56.0623 | 55.8929 | 55.7602 | -67.1722 | 122.8958 | 122.7905 | 75.3387 | -123.0377
1658.5156 | 123.1384 | -58.1772 | 64.6591 | 0.16479 | 0.0066907 | 0.00093569 | 0.01389 | -0.018057 | 0.00062595 | 0.0046891 | 0.14061 | 0.016389 | 0.0055906 | 0.013136 | 0.0081776 | 0.0023071 | -2.3438 | -2.3117 | -2.5223 | -2.3621 | -2.2018 | -2.4078 | -2.536 | -40.4022 | 17.0929 | -58.1818 | 64.7232 | 64.5767 | -58.3191 | -58.4015 | 55.7693 | 55.6412 | -66.861 | 55.8655 | 55.8151 | 0.17395 | -67.0029 | -0.14191 | -0.2243 | 0.064087 | 17.775 | -0.004578 | 0.21973 | -0.082398 | 55.9753 | 55.8334 | 55.6549 | -67.1951 | 122.9004 | 122.7539 | 75.2701 | -123.0606
1659.5156 | 123.1338 | -58.1589 | 64.6912 | 0.073242 | 0.0060497 | 0.0024311 | 0.011326 | -0.01998 | 0.00019875 | 0.0031937 | 0.064316 | 0.014253 | 0.004736 | 0.01399 | 0.0098866 | 0.0025207 | -2.3529 | -2.3117 | -2.4902 | -2.3254 | -2.179 | -2.3758 | -2.536 | -40.3748 | 17.1204 | -58.1406 | 64.6957 | 64.6179 | -58.2962 | -58.374 | 55.7831 | 55.6229 | -66.8701 | 55.8472 | 55.8334 | 0.21057 | -67.0441 | -0.13733 | -0.21515 | 0.004578 | 17.7841 | 0.018311 | 0.23346 | -0.073242 | 55.9799 | 55.806 | 55.6686 | -67.2272 | 122.8546 | 122.7768 | 75.2792 | -123.0652
1660.5156 | 123.1384 | -58.2092 | 64.6408 | 0.2182 | 0.012459 | -0.00034611 | 0.013249 | -0.016562 | 0.0038304 | 0.0049027 | -0.0043486 | 0.017457 | 0.0068722 | 0.013777 | 0.010955 | 0.0018799 | -2.2293 | -2.6917 | -2.6962 | -2.2888 | -2.2522 | -2.4582 | -2.5909 | -40.3107 | 17.07 | -58.168 | 64.6637 | 64.5584 | -58.3466 | -58.4198 | 55.751 | 55.6183 | -66.893 | 55.5176 | 55.9204 | 0.30212 | -66.8701 | -0.13733 | -0.21057 | 0.022888 | 17.8986 | 0.041199 | 0.25177 | -0.082397 | 55.957 | 55.9799 | 55.513 | -67.2318 | 122.8729 | 122.7676 | 75.2792 | -123.0606
1661.5156 | 123.0881 | -58.1772 | 64.6454 | 0.09613 | 0.0079723 | 0.0015765 | 0.011326 | -0.019766 | -0.00022865 | 0.0023391 | 0.44579 | 0.018312 | 0.0040952 | 0.012922 | 0.0075366 | 0.0010253 | -2.3758 | -2.33 | -2.5223 | -2.3575 | -2.179 | -2.3941 | -2.5452 | -40.2924 | 17.0654 | -58.1543 | 64.7049 | 64.6362 | -58.2916 | -58.3694 | 55.7831 | 55.632 | -66.8243 | 55.8472 | 55.8197 | 0.18768 | -67.0212 | -0.11444 | -0.19226 | 0.059509 | 17.8848 | 0.022888 | 0.21515 | -0.009156 | 55.9982 | 55.8014 | 55.6549 | -67.1906 | 122.8821 | 122.8134 | 75.2426 | -123.0148
1662.5156 | 123.1705 | -58.1314 | 64.6912 | 2.095 | 0.01609 | 0.0037127 | 0.015812 | -0.016776 | 0.0027622 | 0.0042619 | 0.14061 | 0.016176 | 0.0051632 | 0.012281 | 0.011809 | 0.0020935 | -2.3438 | -2.3117 | -2.5314 | -2.3758 | -2.2888 | -2.4261 | -2.5955 | -40.1779 | 17.157 | -58.1223 | 64.7278 | 64.6088 | -58.2825 | -58.3557 | 55.7053 | 55.5359 | -66.98 | 55.8197 | 55.7556 | 0.21973 | -67.0349 | -0.15106 | -0.2243 | 0.036621 | 17.9535 | 0.009156 | 0.23346 | -0.082397 | 55.8426 | 55.7877 | 55.6 | -67.2867 | 122.8592 | 122.7402 | 75.2884 | -123.0469
1663.5156 | 123.1338 | -58.1314 | 64.7232 | 0.088501 | 0.0069043 | 0.0022175 | 0.014958 | -0.019126 | -0.0012966 | -0.0012923 | 0.27031 | 0.018312 | 0.0058042 | 0.01164 | 0.0083912 | 0.0044433 | -2.417 | -2.4307 | -2.6825 | -2.4765 | -2.243 | -2.4857 | -2.6321 | -40.2191 | 17.1341 | -58.1314 | 64.7415 | 64.6683 | -58.287 | -58.3649 | 55.6458 | 55.4993 | -66.9662 | 55.7007 | 55.6549 | 0.15564 | -67.1402 | -0.15564 | -0.23346 | 0.01831 | 17.9123 | 0 | 0.23346 | -0.054932 | 55.8884 | 55.7144 | 55.4489 | -67.3553 | 122.8729 | 122.7997 | 75.2655 | -123.0881
1664.5312 | 123.056 | -58.1955 | 64.7415 | 0.042725 | 0.018013 | 0.0015765 | 0.013676 | -0.020835 | 0.0083164 | 0.0049027 | -0.011978 | 0.018312 | 0.009863 | 0.013777 | 0.012023 | 0.00017094 | -2.3804 | -2.4261 | -2.6459 | -2.4261 | -2.2018 | -2.4536 | -2.6001 | -40.242 | 17.07 | -58.2321 | 64.7873 | 64.6591 | -58.3099 | -58.3832 | 55.7419 | 55.5954 | -66.9434 | 55.7693 | 55.7693 | 0.17395 | -67.1219 | -0.11444 | -0.18768 | 0.045776 | 17.9535 | -0.036621 | 0.15106 | -0.082397 | 55.9937 | 55.8151 | 55.5496 | -67.3416 | 122.9828 | 122.8546 | 75.2655 | -123.1247
1665.5156 | 123.1384 | -58.1177 | 64.7781 | 0.14191 | 0.0079723 | 0.0026447 | 0.011113 | -0.020194 | -0.0019376 | 0.0040481 | 0.17113 | 0.015748 | 0.0045224 | 0.015486 | 0.009032 | 0.0031615 | -2.4582 | -2.3849 | -2.6321 | -2.4399 | -2.2751 | -2.4719 | -2.6276 | -40.1321 | 17.1707 | -58.0994 | 64.7873 | 64.7003 | -58.2413 | -58.3466 | 55.6458 | 55.4901 | -67.0532 | 55.7327 | 55.6778 | 0.18768 | -67.2363 | -0.1236 | -0.22888 | 0.009155 | 17.9855 | 0.018311 | 0.24719 | -0.07782 | 55.8426 | 55.6595 | 55.4855 | -67.4057 | 122.905 | 122.818 | 75.2884 | -123.1247
1666.5156 | 123.111 | -58.1039 | 64.7644 | 0.14954 | 0.0073315 | 0.0015765 | 0.014103 | -0.018485 | -0.00065585 | 0.0042619 | 0.17113 | 0.016603 | 0.008154 | 0.012068 | 0.0092456 | 0.0031615 | -2.4445 | -2.4033 | -2.6276 | -2.4582 | -2.3071 | -2.5177 | -2.6459 | -40.123 | 17.1432 | -58.0948 | 64.7873 | 64.682 | -58.2413 | -58.3328 | 55.5862 | 55.4581 | -67.0715 | 55.7007 | 55.6458 | 0.18768 | -67.2089 | -0.13733 | -0.22888 | 0.022888 | 17.981 | 0.009155 | 0.23804 | -0.082397 | 55.7968 | 55.6595 | 55.4764 | -67.4103 | 122.8912 | 122.7859 | 75.2472 | -123.0972
1667.5156 | 123.1659 | -58.0765 | 64.7598 | 0.13428 | 0.0079723 | 0.0037127 | 0.013035 | -0.017417 | 0.00041235 | 0.0049027 | 0.18639 | 0.017884 | 0.006445 | 0.013777 | 0.0092456 | 0.0031615 | -2.4261 | -2.4033 | -2.6001 | -2.4399 | -2.3163 | -2.4948 | -2.6596 | -40.0314 | 17.2348 | -58.0811 | 64.7644 | 64.682 | -58.2184 | -58.3099 | 55.5817 | 55.4169 | -67.0761 | 55.6732 | 55.6366 | 0.21973 | -67.186 | -0.14191 | -0.23346 | 0.004577 | 18.045 | -0.004578 | 0.22888 | -0.07782 | 55.7602 | 55.6503 | 55.4764 | -67.4194 | 122.8409 | 122.7585 | 75.3113 | -123.0698
1668.5156 | 123.1659 | -58.0948 | 64.7507 | 0.18005 | 0.011177 | -0.0024823 | 0.013035 | -0.017417 | 0.0053256 | 0.0040481 | 0.19402 | 0.018098 | 0.0058042 | 0.013349 | 0.013091 | 0.0027343 | -2.4353 | -2.4536 | -2.6596 | -2.4582 | -2.3575 | -2.5269 | -2.6733 | -40.004 | 17.5232 | -57.9941 | 64.8056 | 64.6637 | -58.2275 | -58.3099 | 55.5679 | 55.4214 | -67.1082 | 55.6412 | 55.6366 | 0.21515 | -67.186 | -0.13275 | -0.21515 | 0.054932 | 18.0908 | 0.10071 | 0.31586 | -0.086975 | 55.7373 | 55.6595 | 55.4352 | -67.424 | 122.9004 | 122.7585 | 75.618 | -123.0606
1669.5156 | 123.1522 | -58.1039 | 64.7644 | 0.16479 | 0.01075 | 0.00072209 | 0.011113 | -0.019339 | 0.00041235 | 0.0027665 | 0.23979 | 0.016389 | 0.0060178 | 0.013563 | 0.010741 | 0.0016663 | -2.4307 | -2.4033 | -2.6321 | -2.4445 | -2.3117 | -2.4811 | -2.6505 | -40.0177 | 17.2714 | -58.0902 | 64.7827 | 64.6957 | -58.2275 | -58.3191 | 55.6229 | 55.4535 | -67.0761 | 55.7007 | 55.6595 | 0.20599 | -67.1951 | -0.1236 | -0.21515 | 0.018311 | 18.0862 | 0.013733 | 0.22888 | -0.068664 | 55.7922 | 55.6732 | 55.4718 | -67.4149 | 122.8867 | 122.7997 | 75.3754 | -123.0835
1670.5156 | 123.1247 | -58.1085 | 64.7598 | 0.20294 | 0.014381 | 0.0020037 | 0.014744 | -0.020835 | 0.0038304 | 0.0034073 | 0.15587 | 0.019593 | 0.0066586 | 0.014417 | 0.010741 | 0.0029479 | -2.4719 | -2.504 | -2.7237 | -2.5085 | -2.298 | -2.5406 | -2.6779 | -39.9719 | 17.2943 | -58.0948 | 64.8239 | 64.7095 | -58.2184 | -58.3008 | 55.5679 | 55.4306 | -67.0578 | 55.6046 | 55.6 | 0.16937 | -67.2318 | -0.10986 | -0.19226 | 0.064087 | 18.1366 | 0.013733 | 0.20599 | -0.050354 | 55.8105 | 55.6366 | 55.3848 | -67.4377 | 122.9324 | 122.818 | 75.4028 | -123.0606
1671.5312 | 123.1613 | -58.1406 | 64.7507 | 0.057983 | 0.017799 | 0.0020037 | 0.013035 | -0.017417 | 0.0061802 | 0.0053299 | 0.049057 | 0.021302 | 0.0072994 | 0.015272 | 0.011382 | 0.0020935 | -2.4765 | -2.536 | -2.7557 | -2.4857 | -2.2476 | -2.5223 | -2.6642 | -40.0452 | 17.189 | -58.2092 | 64.8422 | 64.7781 | -58.2596 | -58.3511 | 55.6183 | 55.4764 | -66.9983 | 55.6046 | 55.6549 | 0.17853 | -67.2272 | -0.11902 | -0.21057 | 0.091553 | 18.0954 | -0.068665 | 0.14191 | 0.027466 | 55.8929 | 55.6641 | 55.3848 | -67.4149 | 122.9828 | 122.9187 | 75.3296 | -123.1018
1672.5156 | 123.0606 | -58.0856 | 64.8376 | 0.16479 | 0.015022 | 0.00093569 | 0.011326 | -0.019553 | 0.0038304 | 0.0055435 | 0.12535 | 0.018953 | 0.0096494 | 0.015486 | 0.010955 | 0.0042297 | -2.536 | -2.5681 | -2.7786 | -2.5406 | -2.3026 | -2.5497 | -2.7237 | -39.9307 | 17.2165 | -58.1406 | 64.8834 | 64.801 | -58.2367 | -58.3054 | 55.5359 | 55.3619 | -67.1402 | 55.5176 | 55.545 | 0.18311 | -67.3737 | -0.15106 | -0.21973 | 0.045777 | 18.1549 | -0.054932 | 0.1648 | -0.036621 | 55.7831 | 55.5496 | 55.307 | -67.5613 | 122.9691 | 122.8867 | 75.3021 | -123.143
1673.5156 | 123.1567 | -58.0719 | 64.7827 | 0.23346 | 0.013099 | 0.0011493 | 0.012181 | -0.016562 | 0.0021214 | 0.0061845 | 0.23216 | 0.017671 | 0.008154 | 0.013777 | 0.011168 | 0.0025207 | -2.4582 | -2.4399 | -2.6917 | -2.4582 | -2.3254 | -2.5085 | -2.6733 | -39.83 | 17.4362 | -57.9941 | 64.8468 | 64.769 | -58.2092 | -58.3008 | 55.5634 | 55.3986 | -67.1082 | 55.632 | 55.6137 | 0.21515 | -67.2409 | -0.13733 | -0.22888 | 0.064087 | 18.2419 | 0.077819 | 0.3067 | -0.013733 | 55.7465 | 55.6137 | 55.3802 | -67.4561 | 122.9187 | 122.8409 | 75.5081 | -123.0835
1674.5156 | 123.0515 | -58.0765 | 64.856 | 0.057983 | 0.016945 | 0.0011493 | 0.015599 | -0.018912 | 0.0038304 | 0.0063981 | 0.041427 | 0.020448 | 0.0062314 | 0.013349 | 0.011595 | 0.0023071 | -2.5269 | -2.5406 | -2.7924 | -2.5131 | -2.3071 | -2.5681 | -2.7145 | -39.9124 | 17.3401 | -58.1406 | 64.9109 | 64.8285 | -58.2047 | -58.287 | 55.5084 | 55.3619 | -67.1631 | 55.5359 | 55.5634 | 0.20142 | -67.3828 | -0.12817 | -0.21057 | 0.054932 | 18.1641 | -0.064087 | 0.14648 | -0.027466 | 55.7693 | 55.5496 | 55.2841 | -67.5705 | 122.9874 | 122.905 | 75.4166 | -123.143
1675.5156 | 123.1201 | -58.1039 | 64.8331 | 0.18768 | 0.016945 | 0.00029489 | 0.012181 | -0.018057 | 0.0019078 | 0.0063981 | 0.20927 | 0.019166 | 0.0066586 | 0.015486 | 0.009032 | 0.0046569 | -2.6001 | -2.6093 | -2.8473 | -2.5955 | -2.3483 | -2.5864 | -2.7603 | -39.8575 | 17.3904 | -58.0856 | 64.8376 | 64.7827 | -58.2184 | -58.3145 | 55.5176 | 55.3436 | -67.1814 | 55.4947 | 55.5084 | 0.16479 | -67.4332 | -0.11444 | -0.21057 | 0.004577 | 18.2465 | 0.018311 | 0.22888 | -0.050354 | 55.7556 | 55.5038 | 55.2567 | -67.5934 | 122.9416 | 122.8867 | 75.4944 | -123.1476
1676.5312 | 123.0698 | -58.1268 | 64.856 | 0.10376 | 0.019081 | -0.0024823 | 0.014531 | -0.019766 | 0.0019078 | 0.0070389 | 0.12535 | 0.020662 | 0.0075132 | 0.016981 | 0.0075366 | 0.0038025 | -2.5772 | -2.6093 | -2.6917 | -2.71 | -2.3346 | -2.5497 | -2.7054 | -39.8621 | 17.3035 | -58.168 | 64.8788 | 64.7964 | -58.2092 | -58.3282 | 55.5771 | 55.4214 | -67.1906 | 55.5176 | 55.4169 | -0.004578 | -67.4332 | -0.082398 | -0.20142 | 0.022888 | 18.2648 | -0.041199 | 0.16022 | -0.059509 | 55.7922 | 55.5496 | 55.4352 | -67.5613 | 123.0057 | 122.9233 | 75.4303 | -123.1842
1677.5156 | 123.1064 | -58.0765 | 64.8239 | 0.15717 | 0.014381 | 0.0028583 | 0.014103 | -0.020621 | 0.0025486 | 0.0053299 | 0.23216 | 0.019593 | 0.008154 | 0.011854 | 0.010955 | 0.0014525 | -2.5223 | -2.5406 | -2.7557 | -2.5177 | -2.2934 | -2.536 | -2.6871 | -39.8346 | 17.4225 | -58.1131 | 64.8743 | 64.7964 | -58.2184 | -58.3145 | 55.5405 | 55.3894 | -67.1173 | 55.5359 | 55.5588 | 0.16937 | -67.3462 | -0.14191 | -0.23804 | 0.050354 | 18.2419 | -0.036621 | 0.20142 | -0.027466 | 55.7831 | 55.5542 | 55.3207 | -67.511 | 122.9507 | 122.8729 | 75.499 | -123.1384
1678.5156 | 123.0835 | -58.0994 | 64.856 | 0.042725 | 0.017158 | -0.00034611 | 0.015812 | -0.019126 | 0.0036166 | 0.0049027 | 0.056686 | 0.017244 | 0.009863 | 0.014204 | 0.011168 | 0.0027343 | -2.5085 | -2.5177 | -2.7237 | -2.4857 | -2.2934 | -2.5314 | -2.6733 | -39.8254 | 17.4454 | -58.1085 | 64.8926 | 64.8193 | -58.2047 | -58.3099 | 55.5679 | 55.426 | -67.1494 | 55.5817 | 55.6137 | 0.18768 | -67.3645 | -0.10529 | -0.21057 | 0.036621 | 18.2739 | -0.009156 | 0.20142 | -0.036621 | 55.806 | 55.5908 | 55.3757 | -67.5293 | 122.9919 | 122.9187 | 75.5447 | -123.1659
1679.5156 | 123.0515 | -58.0902 | 64.8834 | 0.09613 | 0.015663 | 0.0022175 | 0.014744 | -0.021262 | 0.0029758 | 0.0072525 | 0.45341 | 0.019807 | 0.0072994 | 0.014631 | 0.0101 | 0.0055115 | -2.8381 | -2.5085 | -2.5314 | -2.3483 | -2.2842 | -2.504 | -2.6779 | -39.8392 | 17.4545 | -58.1268 | 64.8972 | 64.8376 | -58.2001 | -58.287 | 55.5862 | 55.4123 | -67.1677 | 55.5817 | 55.7419 | 0.32959 | -67.7216 | -0.10986 | -0.19684 | 0.013733 | 18.251 | -0.036621 | 0.16022 | -0.045777 | 55.806 | 55.2521 | 55.5588 | -67.5613 | 122.9874 | 122.9279 | 75.5447 | -123.1705
1680.5156 | 123.1384 | -58.0582 | 64.8926 | -0.14801 | 0.012672 | 0.0017901 | 0.010685 | -0.016776 | 0.0027622 | 0.0031937 | -0.14168 | 0.018953 | 0.0068722 | 0.012068 | 0.0098866 | 0.0029479 | -2.504 | -2.4994 | -2.7191 | -2.4719 | -2.2842 | -2.5497 | -2.6733 | -39.7568 | 17.5827 | -58.0215 | 64.9338 | 64.8651 | -58.1726 | -58.2642 | 55.5084 | 55.3848 | -67.1768 | 55.5588 | 55.5862 | 0.20142 | -67.3965 | -0.11444 | -0.20599 | 0.041199 | 18.3014 | 0.036622 | 0.24261 | -0.027466 | 55.7739 | 55.5542 | 55.3391 | -67.5659 | 122.9919 | 122.9233 | 75.6409 | -123.1567
1681.5469 | 123.111 | -58.0673 | 64.92 | 0.035095 | 0.016517 | 0.00072209 | 0.015172 | -0.020407 | 0.00083955 | 0.0049027 | 0.14061 | 0.018739 | 0.01029 | 0.016554 | 0.010314 | 0.0050841 | -2.6001 | -2.6321 | -2.8519 | -2.5726 | -2.3117 | -2.5909 | -2.7374 | -39.7751 | 17.1753 | -58.2504 | 64.8605 | 64.8148 | -58.223 | -58.2916 | 55.4764 | 55.3299 | -67.2318 | 55.4352 | 55.4947 | 0.16479 | -67.5201 | -0.15564 | -0.2243 | -0.059509 | 18.2922 | -0.18311 | 0.041199 | -0.10529 | 55.7556 | 55.4672 | 55.2155 | -67.6575 | 122.9279 | 122.8821 | 75.2426 | -123.2117
1682.5156 | 123.1201 | -58.0719 | 64.8834 | -0.1709 | 0.012459 | 8.1086e-05 | 0.014531 | -0.018698 | 0.0036166 | 0.0029801 | -0.16457 | 0.020234 | 0.0083676 | 0.015058 | 0.012236 | 0.0048705 | -2.504 | -2.504 | -2.7832 | -2.4765 | -2.2888 | -2.5452 | -2.7054 | -39.7202 | 17.6331 | -58.0307 | 64.888 | 64.8285 | -58.2047 | -58.2779 | 55.5267 | 55.3665 | -67.1722 | 55.5679 | 55.5954 | 0.22888 | -67.3874 | -0.13275 | -0.20599 | 0.004577 | 18.3517 | 0.041198 | 0.24719 | -0.054932 | 55.7831 | 55.5679 | 55.2887 | -67.5888 | 122.9599 | 122.9004 | 75.705 | -123.1613
1683.5156 | 123.0789 | -58.1039 | 64.8788 | 0.11139 | 0.017799 | 0.0017901 | 0.013035 | -0.017417 | 0.0029758 | 0.0034073 | 0.11009 | 0.021302 | 0.0092222 | 0.016554 | 0.012023 | 0.0031615 | -2.5726 | -2.5864 | -2.8381 | -2.5406 | -2.3392 | -2.5543 | -2.7054 | -39.7842 | 17.5598 | -58.1451 | 64.9063 | 64.8193 | -58.2138 | -58.3008 | 55.5496 | 55.3986 | -67.218 | 55.5176 | 55.5634 | 0.16479 | -67.4515 | -0.10986 | -0.19684 | 0.027466 | 18.3197 | -0.041199 | 0.15564 | -0.059509 | 55.7648 | 55.5313 | 55.2658 | -67.5842 | 123.0103 | 122.9233 | 75.6638 | -123.1796
1684.5156 | 123.111 | -58.0582 | 64.8743 | -0.59814 | 0.012672 | 0.0022175 | 0.015172 | -0.018271 | 0.0019078 | 0.0046891 | -0.027237 | 0.020448 | 0.0075132 | 0.014417 | 0.0098866 | 0.0033753 | -2.4902 | -2.4673 | -2.7374 | -2.4765 | -2.2751 | -2.5269 | -2.7008 | -39.6744 | 17.6147 | -58.0582 | 64.9155 | 64.856 | -58.1863 | -58.3008 | 55.5313 | 55.3574 | -67.1494 | 55.5908 | 55.5817 | 0.22431 | -67.3645 | -0.12817 | -0.24261 | 0.041198 | 18.3838 | 0 | 0.24261 | -0.018311 | 55.7831 | 55.5679 | 55.3207 | -67.5751 | 122.9736 | 122.9141 | 75.6729 | -123.175
1685.5156 | 123.0743 | -58.0856 | 64.8834 | 0.0045777 | 0.015877 | 0.0015765 | 0.015812 | -0.019766 | 0.003403 | 0.0038345 | 0.0032804 | 0.018739 | 0.0096494 | 0.015058 | 0.010314 | 0.0048705 | -2.4765 | -2.4628 | -2.7054 | -2.4582 | -2.2705 | -2.504 | -2.6642 | -39.7156 | 17.5323 | -58.1039 | 64.9246 | 64.8468 | -58.2047 | -58.2825 | 55.5817 | 55.4214 | -67.1539 | 55.6229 | 55.6274 | 0.20599 | -67.3599 | -0.11902 | -0.19684 | 0.041199 | 18.3701 | -0.018311 | 0.17853 | -0.036621 | 55.8151 | 55.6091 | 55.3802 | -67.5476 | 123.0103 | 122.9324 | 75.618 | -123.1659
1686.5312 | 123.0835 | -58.0902 | 64.9017 | 0.12665 | 0.014381 | 0.00072209 | 0.014744 | -0.01998 | 0.0029758 | 0.0051163 | -0.057755 | 0.021089 | 0.0070858 | 0.01399 | 0.0092456 | 0.0046569 | -2.5864 | -2.6001 | -2.7878 | -2.536 | -2.2888 | -2.5406 | -2.7008 | -39.7751 | 17.5827 | -58.0856 | 64.9475 | 64.8605 | -58.1909 | -58.2687 | 55.5496 | 55.3894 | -67.1906 | 55.4901 | 55.5542 | 0.1648 | -67.4881 | -0.10071 | -0.17853 | 0.045777 | 18.3151 | 0.004578 | 0.18311 | -0.041198 | 55.8014 | 55.5038 | 55.3024 | -67.6025 | 123.0377 | 122.9507 | 75.6729 | -123.1705
1687.5156 | 123.1338 | -58.0856 | 64.9109 | -0.1709 | 0.01609 | 0.0017901 | 0.014103 | -0.01763 | 0.0025486 | 0.0074661 | -0.17983 | 0.018739 | 0.0085812 | 0.016126 | 0.01245 | 0.0031615 | -2.4994 | -2.4719 | -2.7054 | -2.4307 | -2.2522 | -2.4811 | -2.6367 | -39.7156 | 17.6468 | -58.0353 | 64.9338 | 64.888 | -58.1818 | -58.2642 | 55.6046 | 55.4489 | -67.1631 | 55.6137 | 55.6549 | 0.20599 | -67.4103 | -0.096131 | -0.17853 | 0.022888 | 18.3701 | 0.050354 | 0.22888 | -0.022889 | 55.8334 | 55.5862 | 55.3802 | -67.5476 | 123.0194 | 122.9736 | 75.7324 | -123.175
1688.5156 | 123.0789 | -58.0719 | 64.9521 | -0.21667 | 0.011604 | 0.0064899 | 0.016667 | -0.018271 | 0.0014804 | 0.0014847 | -0.20271 | 0.020875 | 0.008154 | 0.014845 | 0.0077502 | 0.0065795 | -2.5497 | -2.5452 | -2.8061 | -2.5314 | -2.2568 | -2.5269 | -2.6917 | -39.7247 | 17.6743 | -58.0353 | 64.9841 | 64.8788 | -58.1589 | -58.223 | 55.545 | 55.3802 | -67.2089 | 55.5267 | 55.5405 | 0.16022 | -67.5018 | -0.086976 | -0.15106 | 0.032044 | 18.3472 | 0.036621 | 0.18768 | -0.073242 | 55.8151 | 55.5222 | 55.2658 | -67.6437 | 123.056 | 122.9507 | 75.7462 | -123.175
1689.5156 | 123.1064 | -58.0261 | 64.9246 | -0.086975 | 0.015236 | 0.00093569 | 0.013035 | -0.018912 | 0.001694 | 0.0038345 | -0.44685 | 0.019593 | 0.0092222 | 0.015913 | 0.0094592 | 0.0031615 | -2.5269 | -2.5131 | -2.7924 | -2.4536 | -2.3254 | -2.5497 | -2.6871 | -39.7018 | 17.6697 | -58.0307 | 64.9292 | 64.888 | -58.1543 | -58.2458 | 55.4764 | 55.3391 | -67.2501 | 55.513 | 55.5725 | 0.23346 | -67.4515 | -0.12817 | -0.21973 | 0.004577 | 18.3243 | -0.004578 | 0.21515 | -0.036622 | 55.7007 | 55.4993 | 55.2338 | -67.6117 | 122.9553 | 122.9141 | 75.6958 | -123.1705
1690.5156 | 123.1247 | -58.049 | 64.9338 | -0.14801 | 0.013099 | 0.0041401 | 0.01154 | -0.017203 | 0.002335 | 0.0046891 | -0.12642 | 0.020448 | 0.0092222 | 0.012922 | 0.010955 | 0.0033753 | -2.5543 | -2.4994 | -2.7786 | -2.4857 | -2.2842 | -2.5497 | -2.7054 | -39.7568 | 17.5781 | -58.0261 | 64.9979 | 64.9017 | -58.1589 | -58.2504 | 55.4993 | 55.3436 | -67.218 | 55.5496 | 55.5634 | 0.21973 | -67.4881 | -0.10986 | -0.20142 | 0.064087 | 18.2922 | 0.022888 | 0.2243 | -0.032044 | 55.7648 | 55.4947 | 55.2704 | -67.6392 | 123.0469 | 122.9507 | 75.6271 | -123.1842
1691.5312 | 123.0927 | -58.0444 | 64.9658 | -0.16327 | 0.0079723 | 0.0024311 | 0.012181 | -0.019553 | -0.0038602 | 0.0034073 | -0.11116 | 0.017884 | 0.006445 | 0.011213 | 0.0075366 | 0.0052979 | -2.5452 | -2.4811 | -2.7283 | -2.4994 | -2.3163 | -2.5635 | -2.6917 | -39.7385 | 17.6147 | -58.017 | 64.9475 | 64.8926 | -58.168 | -58.2596 | 55.481 | 55.3528 | -67.2821 | 55.5634 | 55.545 | 0.19226 | -67.511 | -0.1236 | -0.21515 | -0.01831 | 18.306 | 0.027466 | 0.24262 | -0.073242 | 55.7281 | 55.4993 | 55.3162 | -67.6575 | 122.9919 | 122.937 | 75.6592 | -123.2254
1692.5156 | 123.1018 | -58.0124 | 64.9796 | -0.19379 | 0.010536 | 0.0026447 | 0.013676 | -0.018057 | -0.0012966 | 0.0023391 | -0.050125 | 0.01938 | 0.0062314 | 0.015699 | 0.0066822 | 0.0033753 | -2.5452 | -2.5085 | -2.7512 | -2.5223 | -2.3026 | -2.5406 | -2.6962 | -39.7064 | 17.7017 | -58.0215 | 65.0162 | 64.9338 | -58.1223 | -58.223 | 55.4718 | 55.3162 | -67.2821 | 55.5038 | 55.4901 | 0.17395 | -67.5247 | -0.10986 | -0.21057 | 0.036621 | 18.306 | -0.009155 | 0.20142 | -0.045776 | 55.7098 | 55.4672 | 55.2612 | -67.6758 | 123.0286 | 122.9462 | 75.7141 | -123.2025
1693.5156 | 123.1522 | -58.0353 | 64.9384 | -0.064087 | 0.015236 | 0.00072209 | 0.016026 | -0.01763 | 0.0048984 | 0.0021255 | -0.3019 | 0.018312 | 0.0060178 | 0.012922 | 0.0094592 | 0.0035889 | -2.4857 | -2.6047 | -2.6917 | -2.4582 | -2.2934 | -2.4948 | -2.6642 | -39.6606 | 17.688 | -58.0215 | 64.9658 | 64.9109 | -58.1451 | -58.2413 | 55.5405 | 55.3711 | -67.2318 | 55.4306 | 55.5771 | 0.20599 | -67.424 | -0.10986 | -0.20599 | 0.027466 | 18.3746 | 0.013733 | 0.21973 | -0.027465 | 55.7419 | 55.5496 | 55.3436 | -67.6025 | 123.0011 | 122.9462 | 75.7233 | -123.1796
1694.5156 | 123.0927 | -58.0399 | 64.9841 | -0.20142 | 0.010536 | 0.0034991 | 0.013463 | -0.018271 | -0.00086945 | 0.0019119 | -0.034867 | 0.017244 | 0.0083676 | 0.012708 | 0.0066822 | 0.0040161 | -2.504 | -2.4719 | -2.6871 | -2.4811 | -2.2659 | -2.504 | -2.6642 | -39.7018 | 17.6422 | -58.017 | 64.9979 | 64.9429 | -58.1497 | -58.2321 | 55.5359 | 55.3757 | -67.2501 | 55.5679 | 55.5588 | 0.18311 | -67.4881 | -0.10986 | -0.19226 | 0.013733 | 18.338 | 0.022888 | 0.21515 | -0.041199 | 55.7739 | 55.5359 | 55.3528 | -67.6483 | 123.0377 | 122.9828 | 75.6821 | -123.2162
1695.5156 | 123.1247 | -58.0078 | 64.9887 | -0.20142 | 0.01075 | 0.00072209 | 0.012181 | -0.018271 | -0.0034328 | 0.0040481 | -0.13405 | 0.018953 | 0.0055906 | 0.013563 | 0.0081776 | 0.0061523 | -2.4719 | -2.3987 | -2.6367 | -2.4399 | -2.2934 | -2.504 | -2.6596 | -39.7156 | 17.6971 | -57.9987 | 64.975 | 64.9155 | -58.1451 | -58.223 | 55.5038 | 55.3482 | -67.2821 | 55.6091 | 55.5679 | 0.21973 | -67.4606 | -0.13733 | -0.21515 | -0.013732 | 18.2922 | 0.009155 | 0.2243 | -0.073242 | 55.7144 | 55.5359 | 55.3711 | -67.6483 | 122.9828 | 122.9233 | 75.705 | -123.2117
1696.5312 | 123.2071 | -57.962 | 64.9521 | -1.3992 | 0.0066907 | 0.0034991 | 0.012608 | -0.016989 | -0.0021512 | 0.0014847 | -0.080643 | 0.013826 | 0.006445 | 0.012708 | 0.0092456 | 0.0044433 | -2.4719 | -2.3026 | -2.5589 | -2.3849 | -2.2842 | -2.4673 | -2.623 | -39.6423 | 17.8299 | -57.9025 | 64.9658 | 64.888 | -58.0811 | -58.1863 | 55.4947 | 55.3391 | -67.2363 | 55.6595 | 55.5771 | 0.23804 | -67.424 | -0.11902 | -0.2243 | 0.013733 | 18.3197 | 0.059509 | 0.28381 | -0.064087 | 55.6778 | 55.4901 | 55.4031 | -67.5751 | 122.9279 | 122.85 | 75.7919 | -123.1384
1697.5156 | 123.1293 | -58.0353 | 64.9841 | -0.15564 | 0.012245 | 0.0032855 | 0.014317 | -0.019339 | 0.0027622 | 0.00084388 | -0.15694 | 0.018098 | 0.0058042 | 0.014631 | 0.011382 | 0.0016663 | -2.4902 | -2.4948 | -2.6871 | -2.4582 | -2.2339 | -2.4948 | -2.6505 | -39.7934 | 17.6147 | -58.0536 | 65.0024 | 64.9109 | -58.1543 | -58.2367 | 55.5405 | 55.3848 | -67.218 | 55.5405 | 55.5771 | 0.19226 | -67.4744 | -0.11902 | -0.20142 | 0.01831 | 18.2419 | -0.018311 | 0.1831 | -0.073242 | 55.8014 | 55.545 | 55.3482 | -67.6346 | 123.0377 | 122.9462 | 75.65 | -123.2208
1698.5156 | 123.0698 | -58.017 | 64.9658 | -0.20905 | 0.0088269 | 0.0037127 | 0.012181 | -0.019766 | -0.00022865 | 0.0025529 | -0.17983 | 0.015962 | 0.0075132 | 0.012068 | 0.0075366 | 0.0031615 | -2.4902 | -2.4307 | -2.6779 | -2.4582 | -2.2476 | -2.4948 | -2.6413 | -39.8026 | 17.5781 | -58.0261 | 64.9887 | 64.9384 | -58.136 | -58.2321 | 55.5222 | 55.3757 | -67.2134 | 55.5862 | 55.5588 | 0.18311 | -67.4561 | -0.11902 | -0.21515 | 0.022888 | 18.2144 | -0.009155 | 0.20599 | -0.027466 | 55.7693 | 55.5267 | 55.3391 | -67.6071 | 123.0057 | 122.9553 | 75.5951 | -123.1979
1699.5156 | 123.1247 | -58.0444 | 64.975 | -0.18616 | 0.0083997 | 0.0015765 | 0.013463 | -0.016135 | -0.0019376 | 0.0025529 | -0.12642 | 0.016816 | 0.0075132 | 0.015699 | 0.010741 | 0.0016663 | -2.4216 | -2.3438 | -2.5726 | -2.3804 | -2.2339 | -2.4399 | -2.5909 | -39.83 | 17.6147 | -58.0124 | 64.9796 | 64.8788 | -58.1451 | -58.2321 | 55.6046 | 55.4535 | -67.2089 | 55.7007 | 55.6641 | 0.21057 | -67.3965 | -0.10071 | -0.18768 | 0.004577 | 18.2144 | 0.032044 | 0.21973 | -0.096131 | 55.8105 | 55.6229 | 55.4718 | -67.5659 | 123.024 | 122.9233 | 75.6592 | -123.2071
1700.5156 | 123.2529 | -57.9803 | 64.92 | -0.033569 | 0.0066907 | 0.0039263 | 0.012394 | -0.016562 | -0.0034328 | 0.0016983 | 0.026169 | 0.01703 | 0.0055906 | 0.013563 | 0.0098866 | 0.0033753 | -2.3895 | -2.2934 | -2.4994 | -2.3438 | -2.2247 | -2.4033 | -2.5772 | -39.6835 | 17.7933 | -57.9071 | 64.9246 | 64.8468 | -58.1039 | -58.2138 | 55.5771 | 55.4031 | -67.1448 | 55.687 | 55.6366 | 0.23346 | -67.3096 | -0.1236 | -0.23346 | 0.004578 | 18.2968 | 0.073243 | 0.3067 | -0.073242 | 55.7556 | 55.5908 | 55.481 | -67.4973 | 122.905 | 122.8271 | 75.7736 | -123.1338
1701.5312 | 123.1613 | -58.0124 | 64.9384 | 0.073242 | 0.0075451 | 0.0026447 | 0.012608 | -0.021262 | -0.004501 | 0.0014847 | 1.018 | 0.016389 | 0.0066586 | 0.016981 | 0.0081776 | 0.00017094 | -2.4719 | -2.4078 | -2.6138 | -2.4261 | -2.2797 | -2.4765 | -2.6276 | -39.7797 | 17.6147 | -58.0078 | 64.9429 | 64.8285 | -58.1406 | -58.2413 | 55.5359 | 55.3848 | -67.218 | 55.6046 | 55.5862 | 0.20142 | -67.4103 | -0.12817 | -0.22888 | 0.004578 | 18.2327 | 0.004578 | 0.23346 | -0.10986 | 55.7327 | 55.5405 | 55.3986 | -67.5659 | 122.9553 | 122.8409 | 75.6271 | -123.1796
1702.5156 | 123.2483 | -57.9803 | 64.9475 | -0.056458 | 0.0062635 | 0.0022175 | 0.013249 | -0.018698 | -0.0017238 | -0.00022432 | -0.057755 | 0.017244 | 0.006445 | 0.013777 | 0.0077502 | 0.0038025 | -2.3941 | -2.3117 | -2.5269 | -2.3575 | -2.2568 | -2.4353 | -2.5909 | -39.7247 | 17.7521 | -57.8979 | 64.9155 | 64.8651 | -58.1039 | -58.1909 | 55.545 | 55.3894 | -67.2043 | 55.6686 | 55.6229 | 0.23346 | -67.3416 | -0.1236 | -0.21057 | -0.032044 | 18.2556 | 0.082398 | 0.29297 | -0.082398 | 55.7236 | 55.5862 | 55.4535 | -67.5385 | 122.8958 | 122.8455 | 75.7324 | -123.1384
1703.5156 | 123.2254 | -57.9758 | 64.9109 | -0.11749 | 0.0058361 | 0.0026447 | 0.015172 | -0.021903 | -0.0012966 | 0.0031937 | -1.4387 | 0.016176 | 0.0070858 | 0.013777 | 0.0098866 | 0.0012389 | -2.3483 | -2.2751 | -2.5131 | -2.3621 | -2.2568 | -2.449 | -2.5955 | -39.8346 | 17.6376 | -57.9208 | 64.9338 | 64.8422 | -58.1131 | -58.2275 | 55.5267 | 55.3802 | -67.1677 | 55.7007 | 55.6137 | 0.23346 | -67.2592 | -0.13733 | -0.25177 | 0.022888 | 18.1412 | 0.054932 | 0.3067 | -0.068665 | 55.719 | 55.6274 | 55.4626 | -67.5064 | 122.9095 | 122.818 | 75.6134 | -123.1384
1704.5156 | 123.2162 | -57.9849 | 64.9155 | -0.018311 | 0.0043409 | 0.0030719 | 0.013035 | -0.018485 | -0.0017238 | 0.0019119 | 0.01091 | 0.016176 | 0.0051632 | 0.01164 | 0.0096728 | 0.0025207 | -2.3941 | -2.3071 | -2.5131 | -2.3483 | -2.211 | -2.4353 | -2.5681 | -39.8346 | 17.6285 | -57.9437 | 64.9521 | 64.8285 | -58.1177 | -58.2001 | 55.5496 | 55.4169 | -67.1265 | 55.6778 | 55.6366 | 0.21973 | -67.3096 | -0.13275 | -0.21515 | 0.036621 | 18.1503 | 0.041198 | 0.25635 | -0.086975 | 55.7739 | 55.5908 | 55.4718 | -67.4835 | 122.937 | 122.8134 | 75.6134 | -123.1155
1705.5156 | 123.1842 | -57.9849 | 64.9521 | -0.16327 | 0.0077587 | 0.0013629 | 0.011754 | -0.01763 | -0.00044225 | 0.0034073 | -0.21797 | 0.017671 | 0.004736 | 0.012281 | 0.009032 | 0.0031615 | -2.3712 | -2.2934 | -2.504 | -2.3483 | -2.243 | -2.4307 | -2.5726 | -39.917 | 17.7475 | -57.962 | 64.9796 | 64.888 | -58.1085 | -58.2092 | 55.5542 | 55.4123 | -67.1951 | 55.6915 | 55.6366 | 0.2243 | -67.3233 | -0.1236 | -0.22431 | 0.027466 | 18.0679 | 0.022888 | 0.24719 | -0.064087 | 55.7419 | 55.6137 | 55.481 | -67.5247 | 122.9645 | 122.8729 | 75.7324 | -123.1613
1706.5312 | 123.1842 | -58.0673 | 64.8376 | 0.20294 | 0.013527 | 8.1086e-05 | 0.015385 | -0.019766 | 0.0055392 | 0.0036209 | 0.14061 | 0.018525 | 0.008154 | 0.012281 | 0.010955 | 0.0016663 | -2.3575 | -2.3209 | -2.504 | -2.3346 | -2.2293 | -2.4078 | -2.5543 | -39.9582 | 17.5781 | -58.0124 | 64.8788 | 64.7873 | -58.1726 | -58.2825 | 55.6595 | 55.513 | -67.067 | 55.7465 | 55.7327 | 0.21973 | -67.1951 | -0.10529 | -0.21515 | 0.041199 | 18.1091 | 0.054932 | 0.27008 | -0.050354 | 55.838 | 55.7098 | 55.5634 | -67.392 | 122.9462 | 122.8546 | 75.6454 | -123.1201
1707.5156 | 123.2117 | -57.9987 | 64.9017 | 0.0045777 | 0.0073315 | 0.0011493 | 0.0087628 | -0.022116 | -0.0023648 | 0.0027665 | 0.033798 | 0.018098 | 0.0055906 | 0.014417 | 0.007323 | 0.0027343 | -2.2751 | -2.2156 | -2.4261 | -2.2568 | -2.1378 | -2.3346 | -2.4628 | -39.8849 | 17.6743 | -57.9483 | 64.9017 | 64.8468 | -58.1268 | -58.1818 | 55.6641 | 55.5359 | -67.0395 | 55.7831 | 55.7419 | 0.20599 | -67.1768 | -0.12817 | -0.18311 | 0 | 18.1137 | 0.050354 | 0.23346 | -0.054931 | 55.8609 | 55.7236 | 55.5725 | -67.3645 | 122.9004 | 122.8455 | 75.6729 | -123.0835
1708.5156 | 123.1659 | -58.0261 | 64.888 | 0.16479 | 0.011177 | 0.00093569 | 0.010472 | -0.020407 | 0.001694 | 0.0021255 | 0.20164 | 0.015535 | 0.0068722 | 0.01399 | 0.011382 | 0.0033753 | -2.3117 | -2.2476 | -2.4857 | -2.3254 | -2.2018 | -2.3483 | -2.5177 | -39.9994 | 17.6468 | -58.0078 | 64.9063 | 64.8193 | -58.1497 | -58.2413 | 55.6778 | 55.5084 | -67.0898 | 55.7785 | 55.7007 | 0.19226 | -67.1997 | -0.1236 | -0.21515 | 0.018311 | 18.0267 | 0.018311 | 0.23346 | -0.068664 | 55.8243 | 55.7144 | 55.5405 | -67.4057 | 122.9324 | 122.8455 | 75.6729 | -123.1293
1709.5156 | 123.23 | -57.9987 | 64.9017 | -0.033569 | 0.0081861 | 0.0020037 | 0.012608 | -0.018698 | -0.0047146 | 0.0023391 | -0.019608 | 0.015535 | 0.0053768 | 0.013136 | 0.010527 | 0.0044433 | -2.2934 | -2.2247 | -2.4536 | -2.2934 | -2.1652 | -2.3575 | -2.504 | -40.004 | 17.7246 | -57.9437 | 64.9292 | 64.8331 | -58.136 | -58.1955 | 55.6412 | 55.4947 | -67.067 | 55.7739 | 55.7053 | 0.21057 | -67.1951 | -0.13733 | -0.19684 | 0.027466 | 17.9947 | 0.054931 | 0.25177 | -0.068664 | 55.8334 | 55.7053 | 55.545 | -67.4057 | 122.9279 | 122.8317 | 75.7233 | -123.0972
1710.5156 | 123.1934 | -58.0215 | 64.9155 | 0.09613 | 0.0066907 | 0.0037127 | 0.014103 | -0.020835 | -0.00022865 | 0.00020288 | 0.071945 | 0.016603 | 0.0049496 | 0.012708 | 0.0101 | 0.0048705 | -2.3666 | -2.3163 | -2.5177 | -2.33 | -2.1973 | -2.3666 | -2.5452 | -40.0864 | 17.6376 | -57.9895 | 64.9567 | 64.8422 | -58.1451 | -58.2184 | 55.6549 | 55.4764 | -67.1127 | 55.7053 | 55.6915 | 0.21515 | -67.2821 | -0.1236 | -0.19684 | 0.041199 | 17.9352 | 0.032043 | 0.22888 | -0.073242 | 55.8243 | 55.6549 | 55.5038 | -67.4606 | 122.9782 | 122.8638 | 75.6592 | -123.1338
1711.5312 | 123.1613 | -58.0032 | 64.9841 | -0.10223 | 0.016304 | 0.00093569 | 0.016667 | -0.019553 | 0.0070346 | 0.0044755 | -0.18745 | 0.018739 | 0.0087948 | 0.015058 | 0.011595 | 0.00059814 | -2.2934 | -2.298 | -2.4994 | -2.2888 | -2.1194 | -2.3575 | -2.5223 | -40.1001 | 17.6605 | -58.1863 | 64.9612 | 64.8697 | -58.168 | -58.2504 | 55.6458 | 55.481 | -67.1036 | 55.7053 | 55.7144 | 0.23346 | -67.2775 | -0.1648 | -0.24719 | -0.022888 | 17.9031 | -0.18311 | 0.064087 | -0.11444 | 55.8838 | 55.7098 | 55.5038 | -67.5064 | 122.9645 | 122.8729 | 75.6638 | -123.2346
1712.5156 | 123.1842 | -58.0124 | 64.92 | 0.18768 | 0.010322 | 0.00093569 | 0.012181 | -0.019766 | 0.00083955 | 0.0057571 | 0.2169 | 0.016389 | 0.0090084 | 0.015058 | 0.010527 | 0.0044433 | -2.3026 | -2.2339 | -2.4399 | -2.3071 | -2.179 | -2.3666 | -2.4994 | -40.0909 | 17.775 | -57.9941 | 64.92 | 64.8285 | -58.1406 | -58.2184 | 55.6458 | 55.513 | -67.099 | 55.7785 | 55.7053 | 0.19226 | -67.2226 | -0.12817 | -0.20599 | 0 | 17.9214 | 0.01831 | 0.2243 | -0.091553 | 55.8334 | 55.7098 | 55.5725 | -67.4194 | 122.9324 | 122.8409 | 75.7874 | -123.1384
1713.5156 | 123.2025 | -58.017 | 64.9429 | 0.14191 | 0.0051953 | 0.0032855 | 0.013035 | -0.019126 | -0.0021512 | 0.0023391 | 0.23216 | 0.016603 | 0.0043088 | 0.013777 | 0.0088184 | 0.0033753 | -2.3438 | -2.2842 | -2.6001 | -2.33 | -2.1515 | -2.3712 | -2.5177 | -40.1871 | 17.775 | -57.9803 | 64.9612 | 64.8743 | -58.1314 | -58.2047 | 55.6458 | 55.4993 | -67.0944 | 55.7327 | 55.687 | 0.18768 | -67.2867 | -0.11444 | -0.18768 | 0.018311 | 17.8299 | 0.036621 | 0.2243 | -0.068664 | 55.8655 | 55.6732 | 55.4169 | -67.4606 | 122.9782 | 122.8912 | 75.7919 | -123.1476
1714.5156 | 123.1934 | -58.049 | 64.8972 | 0.21057 | 0.010536 | -0.00034611 | 0.011326 | -0.017203 | 0.0014804 | 0.0040481 | 0.18639 | 0.019166 | 0.0055906 | 0.012922 | 0.010314 | 0.0042297 | -2.2568 | -2.2339 | -2.4307 | -2.2751 | -2.1469 | -2.3254 | -2.4719 | -40.2008 | 17.8436 | -57.9987 | 64.9109 | 64.801 | -58.1589 | -58.2596 | 55.7236 | 55.5771 | -67.0441 | 55.8151 | 55.7739 | 0.19684 | -67.1539 | -0.10986 | -0.21057 | 0.013733 | 17.8482 | 0.050354 | 0.26093 | -0.096131 | 55.9021 | 55.7922 | 55.6183 | -67.3691 | 122.9599 | 122.85 | 75.8926 | -123.1567
1715.5156 | 123.2071 | -58.0353 | 64.92 | 0.14191 | 0.0094677 | 0.0028583 | 0.012822 | -0.021262 | 0.0031894 | 0.0038345 | 0.20927 | 0.017884 | 0.004736 | 0.012495 | 0.0098866 | 0.0035889 | -2.2659 | -2.2293 | -2.4399 | -2.2842 | -2.1835 | -2.3529 | -2.504 | -40.2328 | 17.8574 | -57.9803 | 64.9155 | 64.8514 | -58.1406 | -58.2413 | 55.6824 | 55.5313 | -67.1036 | 55.806 | 55.751 | 0.21973 | -67.186 | -0.10529 | -0.20599 | -0.004578 | 17.8024 | 0.054931 | 0.26093 | -0.068665 | 55.8517 | 55.7693 | 55.5954 | -67.424 | 122.9507 | 122.8867 | 75.8926 | -123.1613
1716.5156 | 123.2208 | -58.0032 | 64.92 | -0.048828 | 0.0064771 | 0.0045673 | 0.013249 | -0.019339 | -0.0021512 | 0.0025529 | 0.018539 | 0.019593 | 0.0053768 | 0.012708 | 0.009032 | 0.0040161 | -2.2568 | -2.1881 | -2.3941 | -2.2247 | -2.1103 | -2.2888 | -2.4399 | -40.274 | 17.8482 | -57.9346 | 64.9475 | 64.8468 | -58.1451 | -58.2001 | 55.7144 | 55.5634 | -67.0303 | 55.8151 | 55.7785 | 0.21515 | -67.1768 | -0.14191 | -0.19684 | 0.027466 | 17.7292 | 0.068665 | 0.2655 | -0.073242 | 55.8929 | 55.7465 | 55.6091 | -67.3599 | 122.9507 | 122.85 | 75.8514 | -123.1201
1717.5156 | 123.2117 | -58.0124 | 64.9109 | 0.18005 | 0.0045545 | 0.0043537 | 0.011754 | -0.020194 | -1.505e-05 | 0.0012711 | 0.12535 | 0.018098 | 0.0040952 | 0.013136 | 0.009032 | 0.0029479 | -2.2293 | -2.1973 | -2.3758 | -2.2293 | -2.0782 | -2.2659 | -2.4124 | -40.2969 | 17.8986 | -57.9895 | 64.9521 | 64.8788 | -58.1497 | -58.2275 | 55.7465 | 55.6 | -66.9891 | 55.8151 | 55.7831 | 0.18311 | -67.1402 | -0.13733 | -0.21515 | 0.041198 | 17.7155 | 0.022888 | 0.23804 | -0.032044 | 55.9341 | 55.7831 | 55.6366 | -67.3233 | 122.9645 | 122.8912 | 75.9109 | -123.1384
1718.5156 | 123.2117 | -57.9987 | 64.92 | 0.30212 | 0.01374 | 0.0024311 | 0.011967 | -0.016989 | 0.0025486 | 0.0014847 | 0.18639 | 0.019166 | 0.0038816 | 0.013563 | 0.012023 | 0.0012389 | -2.2247 | -2.2064 | -2.3666 | -2.2476 | -2.1378 | -2.3071 | -2.4445 | -40.2924 | 17.9169 | -57.9666 | 64.9567 | 64.8651 | -58.1497 | -58.223 | 55.6915 | 55.5542 | -67.0578 | 55.7922 | 55.751 | 0.19684 | -67.1448 | -0.15106 | -0.2243 | 0.036621 | 17.7063 | 0.032043 | 0.25635 | -0.054932 | 55.8609 | 55.7739 | 55.632 | -67.3645 | 122.9553 | 122.8638 | 75.9155 | -123.143
1719.5156 | 123.1979 | -57.9849 | 64.9429 | -0.23193 | 0.0064771 | 0.0028583 | 0.009831 | -0.019766 | -0.00022865 | 0.0014847 | 0.064316 | 0.016176 | 0.0058042 | 0.015486 | 0.010527 | 0.0040161 | -2.2614 | -2.243 | -2.4078 | -2.2614 | -2.1057 | -2.2842 | -2.4261 | -40.3839 | 17.8665 | -57.9666 | 64.9658 | 64.8697 | -58.1223 | -58.2184 | 55.7007 | 55.5588 | -67.0486 | 55.7419 | 55.7236 | 0.16479 | -67.2043 | -0.13733 | -0.23346 | 0.022888 | 17.601 | 0.01831 | 0.25177 | -0.073242 | 55.8792 | 55.7236 | 55.5771 | -67.3691 | 122.9507 | 122.8546 | 75.8514 | -123.1613
1720.5156 | 123.1934 | -58.0124 | 64.9155 | 0.20294 | 0.015877 | 0.0028583 | 0.012822 | -0.021262 | 0.0044712 | 0.0049027 | 0.15587 | 0.019593 | 0.0079404 | 0.013349 | 0.010527 | 0.0020935 | -2.2522 | -2.298 | -2.4811 | -2.2797 | -2.0782 | -2.3071 | -2.4719 | -40.4297 | 17.8894 | -58.0215 | 64.9612 | 64.856 | -58.1268 | -58.2413 | 55.7053 | 55.5405 | -66.9937 | 55.7144 | 55.7327 | 0.19226 | -67.1677 | -0.11444 | -0.22888 | 0.045777 | 17.5827 | -0.009155 | 0.21973 | -0.059509 | 55.9341 | 55.7602 | 55.5313 | -67.3874 | 122.9736 | 122.8683 | 75.9018 | -123.1567
1721.5156 | 123.1064 | -58.017 | 64.9887 | -0.3006 | 0.0096813 | 0.0037127 | 0.011113 | -0.019766 | 0.0014804 | 0.0049027 | -0.18745 | 0.017671 | 0.0040952 | 0.011854 | 0.010314 | 0.0018799 | -2.243 | -2.2339 | -2.4399 | -2.2614 | -2.005 | -2.2797 | -2.4078 | -40.3702 | 17.9901 | -58.1497 | 65.0299 | 64.9338 | -58.1543 | -58.2504 | 55.7373 | 55.6091 | -66.9937 | 55.7831 | 55.7556 | 0.14648 | -67.2318 | -0.13733 | -0.23346 | 0.041199 | 17.6468 | -0.13275 | 0.10071 | -0.054931 | 56.012 | 55.7739 | 55.5771 | -67.3965 | 123.0469 | 122.9507 | 76.0071 | -123.2391
1722.5156 | 123.1293 | -58.0444 | 64.9384 | 0.16479 | 0.016731 | 0.0034991 | 0.013035 | -0.021048 | 0.004044 | 0.0053299 | 0.071945 | 0.018098 | 0.0062314 | 0.014845 | 0.012664 | 0.0035889 | -2.2842 | -2.3026 | -2.4811 | -2.2842 | -2.0325 | -2.2888 | -2.4353 | -40.5212 | 17.8528 | -58.0948 | 64.9658 | 64.8788 | -58.1818 | -58.2687 | 55.7556 | 55.6091 | -66.9708 | 55.7419 | 55.7602 | 0.15106 | -67.2226 | -0.13733 | -0.2243 | 0.027466 | 17.5232 | -0.050354 | 0.17395 | -0.059509 | 56.012 | 55.7602 | 55.5634 | -67.3737 | 123.0103 | 122.9233 | 75.8972 | -123.2071
1723.5156 | 123.1934 | -58.0307 | 64.9612 | 0.18005 | 0.015022 | 0.0017901 | 0.012394 | -0.020194 | 0.003403 | 0.0044755 | 0.18639 | 0.020021 | 0.0072994 | 0.01399 | 0.011809 | 0.0046569 | -2.2705 | -2.2934 | -2.4536 | -2.2705 | -2.0508 | -2.2934 | -2.417 | -40.5212 | 18.013 | -58.0353 | 64.9979 | 64.888 | -58.1497 | -58.255 | 55.7373 | 55.6137 | -67.012 | 55.7373 | 55.7602 | 0.14648 | -67.2318 | -0.11902 | -0.2243 | 0.036621 | 17.5095 | -0.004577 | 0.21973 | -0.073243 | 55.9799 | 55.7602 | 55.5771 | -67.3782 | 123.0286 | 122.9187 | 76.0437 | -123.2162
1724.5156 | 123.0927 | -58.0307 | 64.9704 | 0.13428 | 0.016731 | 0.0028583 | 0.015599 | -0.018271 | 0.0042576 | 0.0049027 | 0.11009 | 0.02173 | 0.0096494 | 0.010786 | 0.010527 | 0.0044433 | -2.3026 | -2.3254 | -2.5131 | -2.2797 | -2.0416 | -2.2797 | -2.4399 | -40.567 | 18.0313 | -58.0215 | 65.0253 | 64.9338 | -58.1635 | -58.2367 | 55.751 | 55.5908 | -67.012 | 55.7053 | 55.751 | 0.16022 | -67.2729 | -0.13275 | -0.20599 | 0.054932 | 17.4637 | 0.009156 | 0.21515 | -0.036621 | 55.9891 | 55.7281 | 55.5176 | -67.4103 | 123.056 | 122.9645 | 76.062 | -123.2071
1725.5156 | 123.3078 | -58.0261 | 64.9063 | 0.2182 | 0.013313 | 0.0015765 | 0.011967 | -0.018271 | -0.00065585 | 0.0063981 | 0.20164 | 0.018525 | 0.0096494 | 0.01399 | 0.0088184 | 0.0040161 | -2.1927 | -2.1652 | -2.3575 | -2.1835 | -2.0737 | -2.2705 | -2.3941 | -40.48 | 18.1641 | -57.9803 | 64.9567 | 64.8743 | -58.1635 | -58.2733 | 55.7556 | 55.632 | -66.98 | 55.8609 | 55.8426 | 0.21057 | -67.099 | -0.13733 | -0.24719 | 0.050354 | 17.5461 | 0.045776 | 0.29297 | -0.032043 | 55.9525 | 55.8334 | 55.6686 | -67.3004 | 122.9828 | 122.9004 | 76.1902 | -123.1796
1726.5156 | 123.175 | -57.9941 | 64.9338 | -0.52185 | 0.010322 | 0.0032855 | 0.009831 | -0.019339 | -0.0025784 | 0.0021255 | 0.15587 | 0.017457 | 0.0053768 | 0.013563 | 0.009032 | 0.0063659 | -2.2202 | -2.2202 | -2.4078 | -2.2156 | -2.0737 | -2.2614 | -2.3987 | -40.5029 | 18.0405 | -57.9483 | 64.9658 | 64.888 | -58.1406 | -58.2184 | 55.7327 | 55.5954 | -67.0074 | 55.7739 | 55.7785 | 0.18311 | -67.1539 | -0.14648 | -0.2243 | 0.032043 | 17.4911 | 0.045777 | 0.27008 | -0.045777 | 55.9204 | 55.7739 | 55.5862 | -67.3325 | 122.9599 | 122.8821 | 76.0345 | -123.1522
1727.5156 | 123.2437 | -57.9758 | 64.9521 | 0.2182 | 0.012459 | 0.0043537 | 0.012394 | -0.019766 | -0.00044225 | 0.0029801 | 0.20927 | 0.017884 | 0.0053768 | 0.012281 | 0.0101 | 0.0040161 | -2.1423 | -2.1332 | -2.3163 | -2.1515 | -2.0554 | -2.2156 | -2.3666 | -40.3885 | 18.1503 | -57.9346 | 64.9704 | 64.8788 | -58.1085 | -58.1955 | 55.7602 | 55.6091 | -67.0074 | 55.8426 | 55.8243 | 0.21515 | -67.0944 | -0.13275 | -0.21973 | 0.018311 | 17.5873 | 0.041199 | 0.26093 | -0.073242 | 55.9204 | 55.8334 | 55.6595 | -67.3187 | 122.9462 | 122.8546 | 76.1261 | -123.1476
1728.5156 | 123.1338 | -58.017 | 65.0208 | 0.057983 | 0.016517 | 0.00093569 | 0.011113 | -0.018057 | 0.0031894 | 0.0027665 | 0.026169 | 0.018739 | 0.008154 | 0.01399 | 0.012023 | 0.0044433 | -2.2476 | -2.2934 | -2.3712 | -2.2659 | -2.0645 | -2.2888 | -2.4582 | -40.4709 | 17.9993 | -58.0399 | 65.0482 | 64.9475 | -58.1314 | -58.2275 | 55.7281 | 55.5588 | -67.0853 | 55.7236 | 55.751 | 0.19226 | -67.2684 | -0.11444 | -0.21057 | 0.027466 | 17.5461 | -0.022888 | 0.18768 | -0.073242 | 55.9525 | 55.7693 | 55.6458 | -67.4789 | 123.0652 | 122.9645 | 76.0162 | -123.2483
1729.5156 | 123.1247 | -58.017 | 65.0024 | -0.30823 | 0.012886 | 0.0020037 | 0.012394 | -0.019553 | 0.001694 | 0.0029801 | 0.17113 | 0.018953 | 0.0062314 | 0.014845 | 0.011809 | 0.0044433 | -2.2385 | -2.2659 | -2.3163 | -2.2202 | -1.9913 | -2.2339 | -2.3895 | -40.4709 | 18.0359 | -58.049 | 65.0208 | 64.9475 | -58.1451 | -58.2001 | 55.7831 | 55.6274 | -66.9937 | 55.751 | 55.7968 | 0.16937 | -67.2409 | -0.12817 | -0.18311 | 0.018311 | 17.5461 | -0.032043 | 0.15106 | -0.054931 | 56.0257 | 55.7785 | 55.7007 | -67.392 | 123.0377 | 122.9645 | 76.0529 | -123.2025
1730.5156 | 123.1476 | -58.0353 | 64.9796 | -0.094604 | 0.015877 | 0.0015765 | 0.013676 | -0.016776 | 0.005112 | 0.0053299 | -0.088272 | 0.019166 | 0.0079404 | 0.012922 | 0.010527 | 0.0020935 | -2.1835 | -2.1973 | -2.2705 | -2.1973 | -1.9958 | -2.2385 | -2.4216 | -40.4022 | 18.1503 | -58.0124 | 64.9933 | 64.9475 | -58.1543 | -58.2413 | 55.7968 | 55.6137 | -66.9754 | 55.838 | 55.838 | 0.2243 | -67.1631 | -0.11902 | -0.20599 | 0.013733 | 17.6331 | 0.022888 | 0.22888 | -0.032043 | 56.0394 | 55.8517 | 55.7648 | -67.4011 | 123.0286 | 122.9828 | 76.1856 | -123.2208
1731.5156 | 123.23 | -58.017 | 64.9109 | 0.29449 | 0.012459 | 0.0045673 | 0.0087628 | -0.021048 | -0.00086945 | 0.0057571 | 0.26268 | 0.017457 | 0.0053768 | 0.01164 | 0.01245 | 0.0059387 | -2.1194 | -2.0782 | -2.1469 | -2.1103 | -2.0233 | -2.1744 | -2.3209 | -40.361 | 18.3105 | -57.9483 | 64.9338 | 64.8514 | -58.1406 | -58.2458 | 55.8426 | 55.6961 | -66.9342 | 55.9387 | 55.9067 | 0.21057 | -67.0303 | -0.1236 | -0.22888 | 0.022888 | 17.6559 | 0.068665 | 0.29755 | -0.05951 | 55.9937 | 55.8975 | 55.8701 | -67.2318 | 122.9507 | 122.8683 | 76.3275 | -123.1567
1732.5156 | 123.1613 | -57.9987 | 64.9612 | -0.086975 | 0.015022 | 0.00050849 | 0.012181 | -0.020407 | 0.0029758 | 0.0042619 | -0.042496 | 0.019807 | 0.0072994 | 0.014845 | 0.010314 | 0.0031615 | -2.124 | -2.1423 | -2.2385 | -2.1561 | -1.9638 | -2.2202 | -2.3621 | -40.361 | 18.1595 | -58.0032 | 65.007 | 64.9292 | -58.1497 | -58.2367 | 55.7785 | 55.6366 | -66.925 | 55.8563 | 55.8426 | 0.20599 | -67.0853 | -0.15106 | -0.23804 | 0.045776 | 17.6376 | -0.004578 | 0.23346 | -0.032044 | 56.0349 | 55.8746 | 55.7602 | -67.3233 | 123.0057 | 122.9279 | 76.1581 | -123.1979
1733.5156 | 123.0927 | -58.0536 | 64.9567 | 0.13428 | 0.015449 | 0.0028583 | 0.012181 | -0.020194 | 0.0055392 | 0.0029801 | 0.056686 | 0.020662 | 0.008154 | 0.014417 | 0.012877 | 0.0063659 | -2.211 | -2.2202 | -2.2797 | -2.179 | -1.9684 | -2.2018 | -2.3529 | -40.416 | 18.1778 | -58.0856 | 64.9979 | 64.9063 | -58.1863 | -58.2825 | 55.8517 | 55.7007 | -66.925 | 55.8334 | 55.8746 | 0.17395 | -67.1677 | -0.13275 | -0.22888 | 0.041199 | 17.6376 | -0.032043 | 0.19684 | -0.050354 | 56.0852 | 55.8426 | 55.7739 | -67.3096 | 123.0515 | 122.9599 | 76.2314 | -123.2391
1734.5156 | 123.1705 | -58.0444 | 64.975 | -0.048828 | 0.015022 | 0.0034991 | 0.014958 | -0.01763 | 0.0019078 | 0.0053299 | 0.018539 | 0.017884 | 0.008154 | 0.013136 | 0.011382 | 0.0046569 | -2.1057 | -2.0966 | -2.1973 | -2.1103 | -1.9272 | -2.1652 | -2.3209 | -40.2969 | 18.2739 | -58.0399 | 64.9933 | 64.9338 | -58.168 | -58.2413 | 55.8792 | 55.7236 | -66.9022 | 55.9479 | 55.9341 | 0.21057 | -67.0807 | -0.1236 | -0.19684 | 0.01831 | 17.7475 | 0.004578 | 0.20142 | -0.041199 | 56.1172 | 55.9387 | 55.8472 | -67.2958 | 123.0377 | 122.9782 | 76.3184 | -123.2162
1735.5156 | 123.1384 | -58.0719 | 64.9475 | -3.0701 | 0.015449 | -0.00013251 | 0.013249 | -0.022544 | -0.001083 | 0.0042619 | 0.17113 | 0.020875 | 0.0075132 | 0.015058 | 0.0098866 | 0.0052979 | -2.2247 | -2.1698 | -2.2568 | -2.1744 | -1.918 | -2.179 | -2.33 | -40.2695 | 18.187 | -58.0902 | 64.9841 | 64.9292 | -58.2001 | -58.2962 | 55.8929 | 55.7419 | -66.8655 | 55.9021 | 55.8975 | 0.15564 | -67.1722 | -0.12817 | -0.22431 | 0.036621 | 17.8024 | -0.018311 | 0.20599 | -0.018311 | 56.1539 | 55.8472 | 55.8151 | -67.2775 | 123.056 | 123.0011 | 76.2588 | -123.2437
1736.5156 | 123.0972 | -58.0673 | 64.9796 | 0.035095 | 0.015236 | 0.0011493 | 0.013249 | -0.016135 | -1.505e-05 | 0.0044755 | 0.041427 | 0.022371 | 0.0068722 | 0.015699 | 0.011168 | 0.0065795 | -2.1881 | -2.1927 | -2.2705 | -2.1561 | -1.9501 | -2.1973 | -2.3483 | -40.2054 | 18.2281 | -58.0673 | 65.0162 | 64.9338 | -58.1772 | -58.2367 | 55.8701 | 55.719 | -66.9296 | 55.8746 | 55.9113 | 0.19226 | -67.1677 | -0.10986 | -0.16937 | 0.036621 | 17.8619 | 0 | 0.16937 | -0.045776 | 56.1172 | 55.8792 | 55.7968 | -67.3279 | 123.0835 | 123.0011 | 76.2955 | -123.2162
1737.5156 | 123.1247 | -58.049 | 64.9658 | -0.33112 | 0.016304 | 0.0032855 | 0.014103 | -0.018912 | 0.0012668 | 0.0057571 | 0.1635 | 0.021516 | 0.0092222 | 0.01634 | 0.010955 | 0.0061523 | -2.2202 | -2.2385 | -2.2888 | -2.179 | -1.9547 | -2.179 | -2.3804 | -40.1413 | 18.3563 | -58.0444 | 65.0208 | 64.9658 | -58.1772 | -58.2504 | 55.8701 | 55.6686 | -66.9205 | 55.8105 | 55.8701 | 0.20142 | -67.186 | -0.12817 | -0.20142 | 0.054932 | 17.9077 | 0.004577 | 0.20599 | 0 | 56.0944 | 55.8289 | 55.7602 | -67.3462 | 123.0698 | 123.0148 | 76.4053 | -123.2162
1738.5156 | 123.1659 | -58.0307 | 64.975 | -0.16327 | 0.012886 | 0.0020037 | 0.014103 | -0.017417 | 0.00083955 | 0.0021255 | -0.12642 | 0.020662 | 0.0066586 | 0.012281 | 0.010955 | 0.0046569 | -2.1149 | -2.0966 | -2.179 | -2.0874 | -1.8951 | -2.124 | -2.3026 | -40.1047 | 18.457 | -57.9941 | 65.0208 | 64.9567 | -58.1589 | -58.2642 | 55.9067 | 55.7281 | -66.8701 | 55.9341 | 55.9433 | 0.21515 | -67.0898 | -0.12817 | -0.23346 | 0.045776 | 17.926 | 0.036621 | 0.27008 | -0.018311 | 56.1356 | 55.9158 | 55.8517 | -67.2775 | 123.0515 | 122.9874 | 76.4877 | -123.2391
1739.5156 | 123.1384 | -58.0582 | 64.9658 | 0.042725 | 0.014381 | 0.0011493 | 0.014958 | -0.018912 | 0.0044712 | 0.0038345 | 0.087204 | 0.021516 | 0.0090084 | 0.015913 | 0.0096728 | 0.0035889 | -2.0966 | -2.0828 | -2.1698 | -2.0645 | -1.8768 | -2.1149 | -2.2522 | -40.0589 | 18.5074 | -58.0719 | 64.9841 | 64.9246 | -58.1772 | -58.2779 | 55.9433 | 55.806 | -66.8427 | 55.9753 | 55.9937 | 0.18768 | -67.0624 | -0.11902 | -0.21973 | 0.018311 | 17.9993 | -0.013732 | 0.20599 | -0.041198 | 56.1813 | 55.9616 | 55.8884 | -67.218 | 123.0423 | 122.9828 | 76.5656 | -123.2437
1740.5156 | 123.1705 | -58.0856 | 64.9567 | -0.18616 | 0.011177 | 0.0026447 | 0.014103 | -0.016989 | -0.00086945 | 0.0019119 | -0.10353 | 0.031984 | 0.008154 | 0.02638 | 0.0098866 | 0.0055115 | -2.1378 | -2.124 | -2.1927 | -2.0874 | -1.886 | -2.1423 | -2.3026 | -40.0635 | 18.6218 | -58.0399 | 64.9933 | 64.92 | -58.2092 | -58.2733 | 55.9433 | 55.7831 | -66.8427 | 55.9616 | 55.9982 | 0.21515 | -67.0944 | -0.1236 | -0.18768 | 0.036621 | 18.0222 | 0.045776 | 0.23346 | -0.036621 | 56.1996 | 55.9479 | 55.8929 | -67.2592 | 123.0789 | 123.0057 | 76.7075 | -123.23
1741.5312 | 123.2529 | -58.049 | 64.8972 | 0.15717 | 0.01139 | 0.0032855 | 0.011326 | -0.016562 | -0.0021512 | 0.0029801 | 0.28557 | 0.025789 | 0.0087948 | 0.022321 | 0.0096728 | 0.0059387 | -2.0599 | -1.9913 | -2.0782 | -2.0325 | -1.9272 | -2.092 | -2.2247 | -39.9628 | 18.6676 | -57.9758 | 64.8972 | 64.8331 | -58.1955 | -58.2687 | 55.957 | 55.8243 | -66.8243 | 56.0577 | 56.0165 | 0.19226 | -66.9571 | -0.14648 | -0.21973 | 0 | 18.0862 | 0.073242 | 0.29297 | -0.064087 | 56.1218 | 55.9891 | 55.9708 | -67.1219 | 122.9462 | 122.8821 | 76.7166 | -123.1659
1742.5312 | 123.0515 | -78.1311 | 44.6548 | 0.15717 | 0.0096813 | 0.0026447 | 0.011967 | -0.020835 | -0.0042874 | 0.00041648 | 0.30846 | 0.01703 | -0.011713 | 0.014417 | -0.0072034 | 0.014697 | 5.0308 | 5.0674 | 4.9805 | 5.0354 | 5.1178 | 4.9255 | 4.7516 | 43.8812 | 41.8304 | 44.5587 | 44.6869 | 44.6182 | 8.7158 | 8.6288 | 83.0566 | 82.8827 | -39.537 | 83.1985 | 83.1665 | 0.28381 | -39.624 | 86.8469 | 86.7599 | 0.032044 | 122.0123 | 122.6898 | 35.9299 | -0.036621 | 83.2489 | 83.1619 | 83.1116 | -39.9033 | 122.818 | 122.7493 | 119.9615 | -36.026
1743.5156 | 123.0652 | -78.241 | 44.6457 | -0.079346 | 0.015022 | 0.00072209 | 0.019871 | -0.018485 | 0.0053256 | 0.0034073 | -0.095902 | 0.020021 | -0.0078678 | 0.017408 | -0.003999 | 0.0093567 | 5.0217 | 5.0217 | 4.9393 | 5.0308 | 5.1407 | 4.8798 | 4.7104 | 43.9499 | 41.8716 | 44.6823 | 44.7098 | 44.6228 | 8.725 | 8.6288 | 83.1207 | 82.9514 | -39.505 | 83.2626 | 83.2718 | 0.32043 | -39.624 | 86.9659 | 86.8698 | 0.064087 | 122.1909 | 122.9233 | 36.0535 | -0.022888 | 83.3817 | 83.2626 | 83.1802 | -39.9353 | 122.9507 | 122.8638 | 120.1126 | -36.0168
1744.5156 | 123.0377 | -78.3096 | 44.632 | -0.18616 | 0.010322 | 0.0030719 | 0.010685 | -0.018698 | -1.505e-05 | 0.0027665 | -0.14168 | 0.019807 | -0.010645 | 0.017195 | -0.0054944 | 0.012134 | 5.0308 | 5.0629 | 4.953 | 5.0491 | 5.1727 | 4.9026 | 4.7333 | 43.8858 | 41.7892 | 44.5999 | 44.6777 | 44.5999 | 8.7387 | 8.6426 | 83.2123 | 83.0429 | -39.4592 | 83.3725 | 83.3588 | 0.31586 | -39.6011 | 87.0483 | 86.9522 | 0.045776 | 122.1954 | 122.9095 | 35.9573 | -0.032043 | 83.4824 | 83.3405 | 83.2626 | -39.8987 | 122.9874 | 122.9095 | 120.0989 | -35.9894
1745.5156 | 123.056 | -78.4241 | 44.5541 | -0.15564 | 0.01374 | 0.0064899 | 0.014317 | -0.018912 | 0.00041235 | 0.0023391 | -0.10353 | 0.018739 | -0.010004 | 0.015486 | -0.0037854 | 0.010852 | 5.0537 | 5.04 | 4.9667 | 5.0766 | 5.2414 | 4.953 | 4.7791 | 43.84 | 41.7252 | 44.5953 | 44.5862 | 44.4946 | 8.7387 | 8.638 | 83.3771 | 83.2031 | -39.3127 | 83.4641 | 83.5007 | 0.29755 | -39.5004 | 87.1628 | 87.0621 | 0.032044 | 122.2641 | 123.0194 | 35.9573 | -0.059509 | 83.6655 | 83.4778 | 83.3908 | -39.7751 | 123.0103 | 122.9187 | 120.1492 | -35.9161
1746.5156 | 123.056 | -78.4698 | 44.5175 | -0.14801 | 0.010536 | 0.0030719 | 0.013463 | -0.018485 | -0.00065585 | 0.0038345 | -0.21797 | 0.019593 | -0.011499 | 0.016554 | -0.0037854 | 0.012347 | 5.04 | 5.072 | 4.985 | 5.04 | 5.1956 | 4.9301 | 4.7607 | 43.8171 | 41.6885 | 44.5724 | 44.5175 | 44.4489 | 8.7387 | 8.6334 | 83.4 | 83.2306 | -39.3219 | 83.5419 | 83.5098 | 0.27924 | -39.4775 | 87.2086 | 87.1033 | 0 | 122.287 | 123.0423 | 35.939 | -0.068664 | 83.6655 | 83.5098 | 83.4549 | -39.7568 | 122.9874 | 122.9187 | 120.1584 | -35.8841
1747.5312 | 123.111 | -78.4882 | 44.4305 | 0.16479 | 0.014595 | 0.0013629 | 0.013035 | -0.019766 | 0.002335 | 0.0046891 | 0.19402 | 0.01938 | -0.012567 | 0.01634 | -0.0048534 | 0.010211 | 5.0262 | 5.0079 | 4.9393 | 5.0262 | 5.1819 | 4.9255 | 4.7653 | 43.808 | 41.6061 | 44.5312 | 44.4489 | 44.3619 | 8.7387 | 8.638 | 83.4137 | 83.2535 | -39.2487 | 83.4961 | 83.5144 | 0.26093 | -39.4043 | 87.2269 | 87.1262 | 0.018311 | 122.2961 | 123.0194 | 35.8933 | -0.068665 | 83.67 | 83.5144 | 83.4274 | -39.6652 | 122.937 | 122.85 | 120.0943 | -35.7925
1748.5156 | 123.1476 | -78.5339 | 44.4214 | -0.16327 | 0.0077587 | 0.00072209 | 0.013676 | -0.019126 | -0.0032192 | 0.0012711 | -0.12642 | 0.01703 | -0.010858 | 0.017408 | -0.005708 | 0.01427 | 5.1315 | 5.1956 | 5.1041 | 5.1636 | 5.2048 | 4.9988 | 4.8065 | 43.8217 | 41.6794 | 44.5587 | 44.3893 | 44.3481 | 8.7341 | 8.6334 | 83.5327 | 83.3405 | -39.2166 | 83.7296 | 83.6975 | 0.35705 | -39.2899 | 87.2681 | 87.1674 | -0.032044 | 122.3557 | 123.0927 | 35.9253 | -0.073242 | 83.7387 | 83.6655 | 83.638 | -39.6149 | 122.9233 | 122.8821 | 120.2133 | -35.788
1749.5156 | 123.0652 | -78.5477 | 44.4305 | -0.18616 | 0.013099 | 0.0043537 | 0.01389 | -0.01998 | -0.001083 | -1.0724e-05 | -2.0948 | 0.020662 | -0.010858 | 0.015486 | -0.0052808 | 0.010425 | 5.1178 | 5.1453 | 5.0537 | 5.1407 | 5.3146 | 5.0446 | 4.8477 | 43.7531 | 41.5604 | 44.4855 | 44.4214 | 44.3756 | 8.7479 | 8.638 | 83.5922 | 83.3954 | -39.1159 | 83.6929 | 83.6884 | 0.29297 | -39.3127 | 87.2955 | 87.1857 | -0.009155 | 122.3007 | 123.0331 | 35.8475 | -0.054932 | 83.8623 | 83.6655 | 83.6014 | -39.5828 | 122.9691 | 122.9233 | 120.108 | -35.7925
1750.5156 | 123.1888 | -78.5385 | 44.3527 | -0.10986 | 0.0083997 | 0.0026447 | 0.01389 | -0.019553 | -0.004501 | 0.0019119 | -0.073013 | 0.017884 | -0.012567 | 0.013563 | -0.003999 | 0.012347 | 4.9896 | 5.5389 | 5.2048 | 4.9255 | 5.2277 | 4.9988 | 4.8203 | 43.8217 | 41.6519 | 44.5816 | 44.3665 | 44.2703 | 8.7387 | 8.6472 | 83.5373 | 83.3588 | -39.1251 | 84.0775 | 83.4641 | 0.10529 | -39.3631 | 87.2772 | 87.1857 | 0.013733 | 122.3602 | 123.1201 | 35.9344 | -0.082397 | 83.7662 | 83.5281 | 83.7433 | -39.5325 | 122.905 | 122.8088 | 120.1904 | -35.7056
1751.5312 | 123.0698 | -78.6621 | 44.3344 | 0.065613 | 0.015663 | 0.00072209 | 0.016026 | -0.01998 | 0.0046848 | 0.0046891 | 0.033798 | 0.020234 | -0.011713 | 0.014631 | -0.0016492 | 0.0091431 | 5.0446 | 5.0354 | 4.953 | 5.0491 | 5.2231 | 4.953 | 4.7882 | 43.6615 | 41.4322 | 44.3665 | 44.3619 | 44.2657 | 8.7479 | 8.638 | 83.6151 | 83.4503 | -39.1113 | 83.6975 | 83.7112 | 0.26093 | -39.2899 | 87.41 | 87.3001 | 0.027465 | 122.3236 | 123.0286 | 35.7285 | -0.068665 | 83.8852 | 83.7067 | 83.6151 | -39.5462 | 123.024 | 122.9279 | 120.0943 | -35.6964
1752.5156 | 123.0927 | -78.6804 | 44.3161 | 0.10376 | 0.017586 | 0.00072209 | 0.014958 | -0.018485 | 0.0063938 | 0.0057571 | -0.0043486 | 0.022798 | -0.0078678 | 0.017622 | -0.0037854 | 0.0097839 | 5.072 | 5.0491 | 4.985 | 5.0674 | 5.2094 | 4.9576 | 4.7745 | 43.6569 | 41.4734 | 44.3573 | 44.3253 | 44.2703 | 8.7387 | 8.638 | 83.638 | 83.4549 | -39.1068 | 83.7296 | 83.7479 | 0.29297 | -39.2441 | 87.4191 | 87.3184 | 0.009155 | 122.3373 | 123.0377 | 35.7193 | -0.045776 | 83.8898 | 83.7524 | 83.6655 | -39.5416 | 123.0057 | 122.9507 | 120.1538 | -35.6781
1753.5156 | 123.1155 | -78.5797 | 44.3573 | -0.17853 | 0.01139 | 0.00093569 | 0.012608 | -0.01998 | -0.0036464 | 0.0010575 | -0.17983 | 0.020448 | -0.013422 | 0.017195 | -0.0044262 | 0.012561 | 5.0903 | 5.1544 | 5.0537 | 5.1178 | 5.2002 | 4.9713 | 4.7974 | 43.721 | 41.6336 | 44.4763 | 44.3436 | 44.2841 | 8.7387 | 8.6426 | 83.551 | 83.3771 | -39.1571 | 83.7341 | 83.6975 | 0.32043 | -39.267 | 87.3184 | 87.2223 | -0.013733 | 122.3007 | 123.056 | 35.8337 | -0.073242 | 83.7799 | 83.67 | 83.6334 | -39.5599 | 122.9233 | 122.8638 | 120.2133 | -35.7147
1754.5156 | 123.2208 | -78.5843 | 44.2978 | -0.048828 | 0.0073315 | 0.0047809 | 0.013035 | -0.021903 | -0.0057828 | 0.00084388 | 0.026169 | 0.016816 | -0.0097904 | 0.015486 | -0.0029308 | 0.012775 | 5.0537 | 5.1498 | 5.0491 | 5.0949 | 5.1636 | 4.9576 | 4.7653 | 43.7851 | 41.6748 | 44.5312 | 44.3344 | 44.2291 | 8.7433 | 8.638 | 83.5419 | 83.3496 | -39.1342 | 83.7341 | 83.6792 | 0.32959 | -39.2441 | 87.3276 | 87.2223 | 0.036621 | 122.3694 | 123.1155 | 35.8933 | -0.068665 | 83.7479 | 83.638 | 83.6334 | -39.5325 | 122.9187 | 122.8134 | 120.2591 | -35.6598
1755.5156 | 123.1247 | -78.7354 | 44.2291 | -0.20142 | 0.0096813 | 0.0024311 | 0.015599 | -0.017844 | 0.00041235 | 0.0029801 | -0.16457 | 0.019593 | -0.012567 | 0.015058 | -0.0035718 | 0.010425 | 5.1315 | 5.1865 | 5.0674 | 5.1544 | 5.2322 | 5.0034 | 4.8157 | 43.6203 | 44.3573 | 44.3573 | 44.2337 | 44.1605 | 8.7433 | 8.638 | 83.7387 | 83.551 | -38.9969 | 83.9218 | 83.8898 | 0.33875 | -39.0976 | 87.4786 | 87.3734 | 0.004578 | 122.3557 | 123.0927 | 35.7193 | -0.068665 | 83.9676 | 83.8669 | 83.8028 | -39.4135 | 122.9691 | 122.8958 | 123.0927 | -35.5911
1756.5156 | 123.1293 | -78.7766 | 44.2062 | -0.086975 | 0.015449 | 0.0073443 | 0.014103 | -0.019766 | 0.0014804 | 0.0046891 | -0.21797 | 0.018098 | -0.011286 | 0.015486 | -0.0016492 | 0.010211 | 5.0674 | 5.0766 | 4.985 | 5.1041 | 5.2414 | 4.9667 | 4.7882 | 43.5608 | 44.2978 | 44.3024 | 44.2337 | 44.1467 | 8.7433 | 8.6472 | 83.7433 | 83.5648 | -38.9648 | 83.8531 | 83.8806 | 0.31586 | -39.1388 | 87.5198 | 87.4237 | 0.027466 | 122.3373 | 123.0789 | 35.6552 | -0.059509 | 84.0179 | 83.844 | 83.7616 | -39.418 | 123.0103 | 122.9233 | 123.0743 | -35.5591
1757.5156 | 123.1247 | -78.7857 | 44.22 | -0.15564 | 0.0096813 | 0.0026447 | 0.014317 | -0.019553 | 0.0021214 | 0.0038345 | -0.2256 | 0.019807 | -0.011499 | 0.016767 | -0.0035718 | 0.010425 | 5.0354 | 5.0674 | 4.9667 | 5.072 | 5.2643 | 4.9484 | 4.7607 | 43.5699 | 44.2795 | 44.2795 | 44.2566 | 44.1513 | 8.7433 | 8.638 | 83.7341 | 83.5464 | -38.9557 | 83.8531 | 83.8577 | 0.31128 | -39.1846 | 87.529 | 87.4237 | 0.036621 | 122.3557 | 123.0652 | 35.6415 | -0.068665 | 84.05 | 83.8211 | 83.7524 | -39.4592 | 123.0423 | 122.937 | 123.0652 | -35.582
1758.5156 | 123.1796 | -78.7766 | 44.133 | 0.073242 | 0.0090405 | 0.0047809 | 0.013463 | -0.01998 | -0.00621 | 0.00041648 | 0.59074 | 0.01938 | -0.014276 | 0.015058 | -0.0042126 | 0.015125 | 5.0446 | 5.1544 | 5.0262 | 5.04 | 5.2139 | 4.9896 | 4.8065 | 44.1742 | 44.2657 | 44.3069 | 44.133 | 44.0643 | 8.7433 | 8.638 | 83.7662 | 83.5831 | -38.9191 | 83.931 | 83.8165 | 0.23346 | -39.0884 | 87.5198 | 87.4146 | 0 | 122.9507 | 123.0835 | 35.6689 | -0.068665 | 83.9905 | 83.8211 | 83.8028 | -39.3265 | 122.9095 | 122.8409 | 123.0423 | -35.495
1759.5156 | 123.1888 | -78.8269 | 44.1055 | -0.094604 | 0.010109 | 0.0045673 | 0.012181 | -0.01998 | -0.001083 | 0.0040481 | -0.088272 | 0.01938 | -0.011927 | 0.013349 | -0.0048534 | 0.011707 | 5.0858 | 5.1453 | 5.0491 | 5.0949 | 5.1727 | 4.953 | 4.7607 | 44.1696 | 44.3207 | 44.3115 | 44.1284 | 44.046 | 8.7524 | 8.6472 | 83.7799 | 83.5876 | -38.9328 | 83.9722 | 83.9218 | 0.33417 | -39.0198 | 87.5793 | 87.4741 | 0.022888 | 122.9965 | 123.1384 | 35.6644 | -0.059509 | 83.9996 | 83.9127 | 83.876 | -39.3448 | 122.9553 | 122.8729 | 123.1476 | -35.4584
1760.5156 | 123.1384 | -78.8361 | 44.0964 | -0.14038 | 0.0060497 | 0.0049945 | 0.013035 | -0.016776 | -0.0040738 | -0.00086512 | -0.0043486 | 0.01703 | -0.017694 | 0.01634 | -0.0046398 | 0.013843 | 5.0903 | 5.1865 | 5.0537 | 5.0949 | 5.1132 | 4.9393 | 4.7699 | 44.2245 | 44.3573 | 44.3344 | 44.101 | 44.0048 | 8.7479 | 8.6472 | 83.7753 | 83.606 | -38.9832 | 84.0225 | 83.931 | 0.32501 | -39.006 | 87.5839 | 87.4832 | 0.004577 | 123.0606 | 123.1705 | 35.6873 | -0.091553 | 83.9493 | 83.9264 | 83.8898 | -39.3265 | 122.937 | 122.8409 | 123.1934 | -35.4492
1761.5312 | 123.1201 | -78.9139 | 44.0506 | -0.0030518 | 0.018226 | -0.00013251 | 0.016453 | -0.018485 | 0.0066074 | 0.0051163 | -0.065384 | 0.018739 | -0.010431 | 0.014845 | -0.0014356 | 0.011493 | 4.9988 | 4.985 | 4.8798 | 4.953 | 5.1041 | 4.8386 | 4.6783 | 44.1055 | 44.1513 | 44.1605 | 44.1238 | 43.9728 | 8.7433 | 8.6334 | 83.7524 | 83.5922 | -38.9465 | 83.8989 | 83.8669 | 0.27466 | -39.0518 | 87.6572 | 87.5473 | 0.073242 | 123.0194 | 123.0743 | 35.527 | -0.07782 | 84.0179 | 83.9127 | 83.7936 | -39.3723 | 123.0377 | 122.8867 | 123.0652 | -35.4172
1762.5156 | 123.1934 | -78.8956 | 44.0414 | 0.14954 | 0.0058361 | 0.0054217 | 0.010685 | -0.020194 | -0.002792 | 0.0016983 | -0.30952 | 0.018525 | -0.011499 | 0.015272 | -0.0035718 | 0.014484 | 4.921 | 4.9942 | 4.8981 | 4.9667 | 5.0858 | 4.8523 | 4.6783 | 44.0735 | 44.1559 | 44.1879 | 44.0643 | 43.9682 | 8.7479 | 8.6472 | 83.7479 | 83.5739 | -38.9557 | 83.8898 | 83.8623 | 0.28839 | -39.1205 | 87.6434 | 87.5427 | 0.022888 | 122.9691 | 123.0835 | 35.5408 | -0.073242 | 83.9813 | 83.8165 | 83.7936 | -39.3631 | 122.9599 | 122.8638 | 123.0515 | -35.3943
1763.5156 | 123.2346 | -78.8681 | 44.0781 | -0.10223 | 0.0073315 | 0.0030719 | 0.013463 | -0.019339 | -0.0019376 | 0.0023391 | 0.23216 | 0.01703 | -0.014917 | 0.014845 | -0.003999 | 0.0095703 | 4.8752 | 5.5939 | 5.2048 | 4.9667 | 5.1407 | 4.921 | 4.747 | 44.1833 | 44.2978 | 44.2932 | 44.0689 | 44.0002 | 8.7433 | 8.638 | 83.7891 | 83.6151 | -38.9374 | 84.462 | 83.8348 | 0.21973 | -39.2029 | 87.6114 | 87.5061 | -0.009155 | 123.0515 | 123.1613 | 35.6552 | -0.07782 | 84.0088 | 83.7433 | 84.0729 | -39.3311 | 122.937 | 122.8683 | 123.1659 | -35.4401
1764.5156 | 123.1979 | -78.923 | 44.0094 | 0.16479 | 0.0069043 | 0.0024311 | 0.011754 | -0.019766 | -0.00022865 | 0.0034073 | 0.17876 | 0.018312 | -0.013636 | 0.015699 | -0.0027172 | 0.012134 | 5.0537 | 5.0858 | 4.9759 | 5.0262 | 5.1086 | 4.9026 | 4.7287 | 44.0918 | 44.133 | 44.1788 | 44.0323 | 43.9224 | 8.7433 | 8.6426 | 83.8257 | 83.6517 | -38.9008 | 84.0088 | 83.9493 | 0.29755 | -38.9557 | 87.6663 | 87.5656 | 0.022889 | 123.0148 | 123.1018 | 35.5362 | -0.086975 | 84.0317 | 83.9767 | 83.8989 | -39.2807 | 122.9553 | 122.8455 | 123.056 | -35.3668
1765.5156 | 123.23 | -78.9322 | 44.0277 | -0.041199 | 0.0066907 | 0.0030719 | 0.012608 | -0.01998 | -0.0021512 | 0.0010575 | -0.019608 | 0.016176 | -0.014276 | 0.015913 | -0.0052808 | 0.011279 | 4.9713 | 5.0262 | 4.9164 | 4.9667 | 5.0583 | 4.8294 | 4.6738 | 44.133 | 44.2291 | 44.2337 | 44.0186 | 43.9362 | 8.7387 | 8.6472 | 83.7616 | 83.606 | -38.9694 | 83.9584 | 83.8989 | 0.29297 | -39.0564 | 87.6709 | 87.5793 | -0.009155 | 123.0652 | 123.1659 | 35.5865 | -0.091553 | 83.9905 | 83.9035 | 83.8486 | -39.3539 | 122.9507 | 122.8683 | 123.1613 | -35.3806
1766.5156 | 123.111 | -78.9642 | 44.0598 | -0.17853 | 0.010536 | 0.0069171 | 0.014744 | -0.020194 | 0.0010532 | 0.0036209 | -0.46974 | 0.017244 | -0.010218 | 0.016554 | -0.0020764 | 0.0095703 | 4.9942 | 5.0034 | 4.9026 | 5.0629 | 5.1956 | 4.8981 | 4.7287 | 44.0277 | 44.0826 | 44.1147 | 44.0826 | 44.0094 | 8.7479 | 8.6472 | 83.8623 | 83.6929 | -38.8641 | 83.9676 | 84.0271 | 0.33417 | -39.0656 | 87.7121 | 87.6114 | 0.022889 | 122.9919 | 123.0789 | 35.4675 | -0.050354 | 84.1599 | 83.9584 | 83.8669 | -39.3311 | 123.0469 | 122.9736 | 123.0469 | -35.4126
1767.5156 | 123.2025 | -78.923 | 44.0231 | -0.17853 | 0.0088269 | 0.0026447 | 0.0089764 | -0.017844 | -0.0019376 | 0.0021255 | -0.12642 | 0.017671 | -0.011286 | 0.012495 | -0.0044262 | 0.012988 | 5.0034 | 5.0858 | 4.9667 | 5.0079 | 5.0583 | 4.8569 | 4.6783 | 44.1101 | 44.22 | 44.2245 | 44.0186 | 43.9407 | 8.7524 | 8.6517 | 83.7799 | 83.6014 | -38.9648 | 84.0088 | 83.931 | 0.32959 | -39.0198 | 87.6755 | 87.5748 | -0.004577 | 123.0331 | 123.1476 | 35.5728 | -0.082397 | 83.9813 | 83.9264 | 83.8898 | -39.3448 | 122.9416 | 122.8638 | 123.143 | -35.3714
1768.5156 | 123.2437 | -78.9459 | 44.0002 | -0.056458 | 0.0062635 | 0.0034991 | 0.012822 | -0.016776 | -0.0017238 | 0.0031937 | -0.065384 | 0.016389 | -0.014276 | 0.012922 | -0.0046398 | 0.010638 | 5.072 | 5.1453 | 5.0308 | 5.0629 | 5.1224 | 4.921 | 4.7516 | 44.0918 | 44.577 | 44.3893 | 44.0689 | 43.9636 | 8.757 | 8.6426 | 83.8669 | 83.6975 | -38.8779 | 84.0912 | 84.0088 | 0.31128 | -38.9282 | 87.7029 | 87.5885 | 0.068665 | 123.0377 | 123.3353 | 35.7468 | -0.036621 | 84.0683 | 84.0179 | 83.9767 | -39.2487 | 123.0148 | 122.9095 | 123.5229 | -35.3577
1769.5156 | 123.23 | -78.9551 | 43.9728 | -0.30823 | 0.010536 | 0.0032855 | 0.012394 | -0.019553 | 0.0010532 | 0.0042619 | -0.11879 | 0.018525 | -0.01449 | 0.014204 | -0.0031446 | 0.012561 | 5.0354 | 5.1041 | 4.985 | 5.0079 | 5.0812 | 4.8569 | 4.6967 | 44.0506 | 44.2108 | 44.1925 | 43.9911 | 43.8904 | 8.757 | 8.6472 | 83.812 | 83.6517 | -38.8916 | 84.0591 | 83.963 | 0.31128 | -38.9374 | 87.7121 | 87.6022 | 0.018311 | 123.0057 | 123.1476 | 35.5453 | -0.082397 | 84.0363 | 83.9905 | 83.9401 | -39.2761 | 122.9462 | 122.8455 | 123.1659 | -35.3256
1770.5156 | 123.1934 | -78.9963 | 43.9407 | 0.15717 | 0.0073315 | 0.0026447 | 0.012394 | -0.019126 | 0.0012668 | 0.0034073 | 0.12535 | 0.018525 | -0.012995 | 0.011854 | -0.0025036 | 0.013416 | 4.9255 | 4.9667 | 4.8843 | 4.9164 | 5.0354 | 4.8294 | 4.6555 | 43.9362 | 44.0872 | 44.1147 | 43.9545 | 43.8995 | 8.7479 | 8.6426 | 83.8257 | 83.6517 | -38.9053 | 83.963 | 83.9127 | 0.26092 | -39.0152 | 87.7441 | 87.6389 | 0.013733 | 122.9324 | 123.111 | 35.4721 | -0.041199 | 84.0317 | 83.9218 | 83.8806 | -39.2853 | 122.9507 | 122.8958 | 123.0835 | -35.2982
1771.5312 | 123.1522 | -79.0192 | 44.0048 | -0.010681 | 0.017799 | 0.0017901 | 0.016881 | -0.020194 | 0.0072482 | 0.0057571 | -0.10353 | 0.019593 | -0.0095768 | 0.017408 | -0.0010082 | 0.011066 | 4.9576 | 4.9118 | 4.8111 | 4.9255 | 5.0583 | 4.7836 | 4.628 | 43.4006 | 44.0689 | 44.0598 | 44.014 | 43.9407 | 8.7479 | 8.638 | 83.8028 | 83.6472 | -38.9465 | 83.931 | 83.9447 | 0.29755 | -39.0472 | 87.767 | 87.6572 | 0.009155 | 122.4197 | 123.0789 | 35.4218 | -0.064087 | 84.0775 | 83.9767 | 83.8303 | -39.3768 | 123.0331 | 122.9599 | 123.0881 | -35.3668
1772.5156 | 123.2025 | -79.01 | 43.9728 | 0.11139 | 0.0079723 | 0.0062763 | 0.0083356 | -0.020194 | -0.0021512 | 0.0034073 | 0.049057 | 0.01938 | -0.013849 | 0.015272 | -0.0044262 | 0.012347 | 4.8981 | 4.9667 | 4.8889 | 4.9255 | 5.0171 | 4.7974 | 4.6417 | 43.9682 | 44.1101 | 44.1238 | 43.9545 | 43.8812 | 8.7524 | 8.6472 | 83.8074 | 83.6517 | -38.9557 | 83.9767 | 83.9355 | 0.28381 | -39.0747 | 87.7625 | 87.6572 | -0.01831 | 122.9782 | 123.1338 | 35.4767 | -0.091552 | 84.0271 | 83.9081 | 83.8989 | -39.3311 | 122.9645 | 122.8912 | 123.1201 | -35.3256
1773.5156 | 123.2437 | -78.9825 | 43.9682 | 0.20294 | 0.0066907 | 0.0034991 | 0.0096174 | -0.020621 | -0.00022865 | 0.0053299 | -0.10353 | 0.020448 | -0.012995 | 0.016126 | -0.0035718 | 0.01192 | 4.9896 | 5.072 | 4.9713 | 5.0217 | 5.0674 | 4.8477 | 4.6692 | 43.8995 | 44.2017 | 44.1742 | 43.9774 | 43.8858 | 8.7524 | 8.638 | 83.8303 | 83.6517 | -38.9008 | 84.0546 | 84.0042 | 0.35248 | -38.9786 | 87.735 | 87.6205 | 0.009155 | 122.8821 | 123.1567 | 35.5362 | -0.082398 | 84.05 | 83.9722 | 83.9539 | -39.299 | 122.9599 | 122.8683 | 123.1842 | -35.3302
1774.5156 | 123.2391 | -78.9871 | 43.9499 | 0.012207 | 0.0064771 | 0.0020037 | 0.014103 | -0.017417 | -0.0019376 | 0.0012711 | 0.018539 | 0.01703 | -0.012995 | 0.014845 | -0.0042126 | 0.012134 | 4.9164 | 4.9805 | 4.8798 | 4.9438 | 5.04 | 4.8019 | 4.6371 | 43.4143 | 44.1284 | 44.1559 | 43.9545 | 43.8629 | 8.7524 | 8.6472 | 83.7891 | 83.6243 | -38.9099 | 83.9676 | 83.931 | 0.3067 | -39.0335 | 87.7396 | 87.6343 | 0.004578 | 122.4014 | 123.143 | 35.5087 | -0.086975 | 84.0271 | 83.9035 | 83.8669 | -39.3127 | 122.9416 | 122.85 | 123.1155 | -35.3027
1775.5156 | 123.1842 | -78.9917 | 44.0048 | -0.19379 | 0.0092541 | 0.0028583 | 0.011754 | -0.019553 | 0.0021214 | 0.0036209 | -0.16457 | 0.018953 | -0.012354 | 0.013563 | -0.0037854 | 0.01192 | 4.9896 | 5.0308 | 4.9484 | 4.9942 | 5.0537 | 4.8294 | 4.6783 | 43.4097 | 44.165 | 44.1513 | 44.0186 | 43.895 | 8.7479 | 8.6517 | 83.8211 | 83.67 | -38.9511 | 84.0225 | 83.9859 | 0.31586 | -39.0152 | 87.7396 | 87.6434 | 0.013733 | 122.4014 | 123.143 | 35.4996 | -0.10986 | 84.0454 | 83.9813 | 83.9401 | -39.3265 | 123.0103 | 122.8867 | 123.1567 | -35.3531
1776.5156 | 123.175 | -79.0283 | 43.9865 | -0.056458 | 0.015877 | 0.00072209 | 0.014531 | -0.018698 | 0.0072482 | 0.0055435 | -0.14168 | 0.019593 | -0.01214 | 0.015913 | -0.0020764 | 0.0087157 | 4.9438 | 4.9484 | 4.8386 | 4.9347 | 5.0812 | 4.8019 | 4.6234 | 43.4006 | 44.1147 | 43.927 | 43.9682 | 43.8721 | 8.7479 | 8.6472 | 83.8303 | 83.6517 | -38.9053 | 83.9767 | 83.963 | 0.31128 | -39.0427 | 87.7762 | 87.6755 | -0.01831 | 122.4289 | 122.9553 | 35.2798 | -0.11444 | 84.1095 | 83.9722 | 83.8669 | -39.3631 | 122.9965 | 122.9004 | 123.143 | -35.3394
1777.5156 | 123.2574 | -79.0192 | 43.9133 | -0.071716 | 0.0049817 | 0.0028583 | 0.010685 | -0.020194 | -0.0036464 | 0.0049027 | -0.027237 | 0.020234 | -0.01449 | 0.016126 | -0.0044262 | 0.015125 | 4.9393 | 5.0308 | 4.8981 | 4.9576 | 5.0262 | 4.7928 | 4.6417 | 43.4097 | 44.165 | 44.1696 | 43.9499 | 43.8583 | 8.7479 | 8.6426 | 83.812 | 83.6609 | -38.887 | 84.05 | 83.9767 | 0.31586 | -38.974 | 87.767 | 87.6617 | 0.036621 | 122.4289 | 123.1888 | 35.527 | -0.054932 | 84.0454 | 83.9584 | 83.9172 | -39.2715 | 122.9691 | 122.8775 | 123.1842 | -35.2707
1778.5156 | 123.2208 | -79.0466 | 43.9133 | 0.088501 | 0.0094677 | 0.0032855 | 0.014744 | -0.020407 | -0.0030056 | 0.0023391 | 0.15587 | 0.017457 | -0.013849 | 0.013563 | -0.0020764 | 0.015552 | 4.9026 | 4.9622 | 4.866 | 4.9255 | 5.0308 | 4.8157 | 4.6463 | 43.2495 | 44.0826 | 44.0506 | 43.9316 | 43.8354 | 8.7479 | 8.6472 | 83.8623 | 83.6929 | -38.8824 | 84.0088 | 83.9722 | 0.27924 | -39.0106 | 87.7945 | 87.6938 | 0.018311 | 122.2961 | 123.0972 | 35.4034 | -0.07782 | 84.0775 | 83.9493 | 83.9127 | -39.267 | 122.9782 | 122.8821 | 123.1293 | -35.2661
1779.5156 | 123.2391 | -79.0512 | 43.9087 | -0.13275 | 0.0088269 | 8.1086e-05 | 0.015172 | -0.016776 | 0.00083955 | 0.0016983 | -0.088272 | 0.020021 | -0.013422 | 0.014417 | -0.0037854 | 0.01192 | 4.9622 | 5.0125 | 4.9026 | 4.9576 | 5.0079 | 4.8019 | 4.6188 | 43.364 | 44.1422 | 44.1055 | 43.9178 | 43.8263 | 8.7479 | 8.6472 | 83.8531 | 83.67 | -38.9008 | 84.0637 | 84.0088 | 0.33875 | -38.9465 | 87.7991 | 87.6984 | 0.009156 | 122.4152 | 123.1567 | 35.4584 | -0.082397 | 84.0591 | 84.0134 | 83.9539 | -39.2899 | 122.9691 | 122.8775 | 123.1934 | -35.2615
1780.5156 | 123.2941 | -79.0695 | 43.9041 | -0.094604 | 0.0060497 | 0.00093569 | 0.01154 | -0.019339 | -0.00065585 | 0.0025529 | -3.0943 | 0.015107 | -0.013422 | 0.01634 | -0.007417 | 0.011493 | 5.0034 | 5.0766 | 4.9484 | 5.0125 | 5.0308 | 4.8431 | 4.66 | 43.4372 | 43.9957 | 44.1284 | 43.8904 | 43.7851 | 8.7479 | 8.6472 | 83.9127 | 83.7296 | -38.8733 | 84.1461 | 84.082 | 0.35248 | -38.9008 | 87.8174 | 87.7167 | -0.013733 | 122.5067 | 123.1979 | 35.4813 | -0.11902 | 84.1003 | 84.0729 | 84.0179 | -39.2441 | 122.9599 | 122.8546 | 123.0652 | -35.257
1781.5312 | 123.1338 | -79.0787 | 43.9224 | -0.0030518 | 0.015877 | 0.0020037 | 0.017949 | -0.019126 | 0.0038304 | 0.0042619 | 0.11009 | 0.022371 | -0.012567 | 0.01634 | -0.0016492 | 0.0093567 | 4.8614 | 4.8523 | 4.7699 | 4.866 | 5.04 | 4.7699 | 4.5914 | 43.3044 | 43.9636 | 43.9865 | 43.9865 | 43.84 | 8.7479 | 8.6472 | 83.8486 | 83.67 | -38.8824 | 83.931 | 83.9447 | 0.27466 | -39.061 | 87.8265 | 87.7258 | 0.064087 | 122.3831 | 123.0652 | 35.3394 | -0.082397 | 84.1187 | 83.9401 | 83.8486 | -39.3311 | 123.0652 | 122.9187 | 123.0423 | -35.2753
1782.5156 | 123.2712 | -79.0421 | 43.895 | -0.02594 | 0.0077587 | 0.0017901 | 0.012608 | -0.019339 | -0.0030056 | 0.00084388 | 0.01091 | 0.015535 | -0.012567 | 0.015058 | -0.0042126 | 0.011493 | 4.8843 | 4.9484 | 4.8569 | 4.9164 | 4.9896 | 4.7653 | 4.6051 | 43.3731 | 44.1101 | 44.1376 | 43.927 | 43.8309 | 8.7479 | 8.6517 | 83.8074 | 83.6472 | -38.9053 | 83.9905 | 83.9584 | 0.31128 | -39.0106 | 87.7899 | 87.6938 | 0.032044 | 122.4152 | 123.1796 | 35.4858 | -0.064086 | 84.0317 | 83.9264 | 83.8989 | -39.2899 | 122.9691 | 122.8729 | 123.1522 | -35.2432
1783.5156 | 123.1705 | -79.1153 | 43.9362 | -0.19379 | 0.010322 | 0.0037127 | 0.01389 | -0.01998 | 0.00062595 | 0.0046891 | -0.26375 | 0.018525 | -0.012567 | 0.01399 | -0.00229 | 0.01192 | 4.9072 | 4.9484 | 4.8431 | 4.9072 | 5.0262 | 4.7607 | 4.5914 | 43.2999 | 44.0231 | 44.0186 | 43.9499 | 43.84 | 8.7524 | 8.6517 | 83.876 | 83.7067 | -38.9099 | 84.0637 | 84.0225 | 0.31586 | -39.0289 | 87.8677 | 87.767 | 0.013733 | 122.4152 | 123.1338 | 35.3668 | -0.09613 | 84.1415 | 84.0225 | 83.9584 | -39.3448 | 123.0652 | 122.9553 | 123.1384 | -35.2844
1784.5156 | 123.2666 | -79.097 | 43.8721 | -0.079346 | 0.0047681 | 0.0024311 | 0.010685 | -0.018271 | -0.001083 | 0.0027665 | -0.027237 | 0.017671 | -0.018335 | 0.012068 | 0.00027337 | 0.013629 | 4.9759 | 5.04 | 4.9255 | 4.9713 | 5.04 | 4.8248 | 4.6326 | 43.1717 | 44.2062 | 44.0826 | 43.8721 | 43.7897 | 8.7524 | 8.6472 | 83.9218 | 83.7296 | -38.8321 | 84.137 | 84.0683 | 0.33875 | -38.8962 | 87.8494 | 87.7441 | 0 | 122.2687 | 123.1796 | 35.4355 | -0.082397 | 84.137 | 84.0729 | 84.0225 | -39.2395 | 122.9691 | 122.8867 | 123.3032 | -35.2249
1785.5156 | 123.2574 | -79.097 | 43.84 | -0.071716 | 0.0092541 | 0.0026447 | 0.0089764 | -0.019339 | 0.00041235 | 0.00041648 | -0.088272 | 0.018525 | -0.014063 | 0.013777 | -0.0010082 | 0.011493 | 4.9805 | 5.0674 | 4.9347 | 4.9805 | 5.0125 | 4.8203 | 4.6555 | 43.1717 | 44.165 | 44.0689 | 43.8538 | 43.7485 | 8.7524 | 8.6426 | 83.9172 | 83.7524 | -38.8275 | 84.1644 | 84.0775 | 0.32501 | -38.8596 | 87.8494 | 87.7396 | 0.013733 | 122.2687 | 123.1659 | 35.4263 | -0.091553 | 84.1095 | 84.0775 | 84.0317 | -39.1846 | 122.9507 | 122.8455 | 123.262 | -35.1974
1786.5156 | 123.1522 | -79.1748 | 43.8721 | -0.20142 | 0.0075451 | 0.0024311 | 0.016026 | -0.022757 | 0.0019078 | 0.0025529 | -0.39345 | 0.020875 | -0.0078678 | 0.016981 | -0.0048534 | 0.011066 | 4.8523 | 4.866 | 4.7653 | 5.0766 | 5.0491 | 4.7699 | 4.5959 | 43.222 | 43.9316 | 43.9545 | 43.927 | 43.808 | 8.7524 | 8.6472 | 83.9447 | 83.7708 | -38.8229 | 84.0408 | 84.2514 | 0.48065 | -39.0198 | 87.9272 | 87.822 | 0.054932 | 122.3969 | 123.1293 | 35.3073 | -0.064087 | 84.2239 | 84.0271 | 83.9401 | -39.2761 | 123.1018 | 122.9828 | 123.1064 | -35.2249
1787.5156 | 123.1705 | -79.1428 | 43.9041 | -0.1709 | 0.0086133 | 0.00072209 | 0.01389 | -0.019766 | 0.00019875 | 0.0025529 | -0.16457 | 0.018525 | -0.013422 | 0.015272 | -0.0061352 | 0.012775 | 4.8981 | 4.9713 | 4.8477 | 4.9118 | 5.0125 | 4.7836 | 4.6051 | 43.2266 | 43.9957 | 43.959 | 43.8904 | 43.7714 | 8.7524 | 8.6517 | 83.9264 | 83.7479 | -38.8916 | 84.1141 | 84.0546 | 0.3067 | -39.006 | 87.8952 | 87.7945 | -0.013733 | 122.3694 | 123.1018 | 35.3073 | -0.13275 | 84.1553 | 84.0408 | 83.9905 | -39.299 | 123.0331 | 122.9141 | 123.1384 | -35.2524
1788.5156 | 123.2483 | -79.1519 | 43.8583 | -0.15564 | 0.0081861 | 0.0049945 | 0.013676 | -0.018698 | 0.00041235 | 0.0040481 | -0.10353 | 0.016603 | -0.012995 | 0.014204 | -0.0031446 | 0.012561 | 4.866 | 4.9713 | 4.8477 | 4.8843 | 4.953 | 4.7241 | 4.5639 | 43.2907 | 44.0689 | 44.0323 | 43.8446 | 43.7439 | 8.757 | 8.6472 | 83.876 | 83.7158 | -38.9053 | 84.1232 | 84.0363 | 0.32043 | -38.9923 | 87.9089 | 87.7991 | -0.013733 | 122.4426 | 123.1842 | 35.3851 | -0.11444 | 84.1049 | 84.0179 | 83.9996 | -39.2944 | 122.9965 | 122.8958 | 123.2208 | -35.2112
1789.5156 | 123.1888 | -79.1748 | 43.8812 | -0.19379 | 0.0092541 | 0.0043537 | 0.014103 | -0.016135 | 0.002335 | 0.0027665 | -0.17983 | 0.01938 | -0.012781 | 0.014631 | -0.0035718 | 0.01192 | 4.8431 | 4.9438 | 4.8019 | 4.8798 | 4.9667 | 4.7195 | 4.5593 | 43.2175 | 43.9682 | 43.959 | 43.8766 | 43.7485 | 8.7524 | 8.6563 | 83.8943 | 83.7341 | -38.9145 | 84.1187 | 84.0546 | 0.32043 | -39.0381 | 87.9272 | 87.8311 | -0.004578 | 122.3923 | 123.1339 | 35.3027 | -0.13275 | 84.1415 | 84.0179 | 83.9767 | -39.3219 | 123.0515 | 122.9233 | 123.143 | -35.2249
1790.5156 | 123.2574 | -79.1336 | 43.8126 | -0.14038 | 0.0090405 | 0.0026447 | 0.014317 | -0.019339 | -0.0021512 | 0.0046891 | -0.10353 | 0.017244 | -0.014917 | 0.015913 | -0.003999 | 0.01427 | 4.8889 | 4.9896 | 4.8614 | 4.9026 | 4.9576 | 4.7653 | 4.5685 | 43.309 | 44.4214 | 44.2154 | 43.8675 | 43.7576 | 8.7524 | 8.6517 | 83.8989 | 83.7021 | -38.855 | 84.1232 | 84.0363 | 0.33417 | -38.9236 | 87.886 | 87.7853 | 0.054932 | 122.4426 | 123.349 | 35.5637 | -0.054932 | 84.0912 | 84.0225 | 83.9951 | -39.2441 | 123.0011 | 122.8912 | 123.555 | -35.1608
1791.5312 | 123.2071 | -79.216 | 43.8263 | 0.20294 | 0.015877 | 0.0030719 | 0.016881 | -0.021475 | 0.0063938 | 0.0042619 | 0.15587 | 0.019166 | -0.0097904 | 0.016126 | -0.0016492 | 0.0099975 | 4.7287 | 4.7333 | 4.6417 | 4.7195 | 4.8889 | 4.6188 | 4.4632 | 43.2495 | 43.9041 | 43.9362 | 43.8583 | 43.7256 | 8.7524 | 8.6472 | 83.8348 | 83.6792 | -38.9374 | 83.9493 | 83.9355 | 0.25635 | -39.0976 | 87.9684 | 87.8632 | 0.032043 | 122.4655 | 123.1522 | 35.289 | -0.10071 | 84.1049 | 83.9447 | 83.8577 | -39.3631 | 123.0743 | 122.9416 | 123.1201 | -35.1791
1792.5156 | 123.1842 | -79.1519 | 43.8766 | -0.19379 | 0.010536 | 0.0017901 | 0.011754 | -0.017844 | 0.0019078 | 0.0034073 | -0.1722 | 0.018953 | -0.011499 | 0.015699 | -0.0042126 | 0.010852 | 4.8706 | 4.9255 | 4.8157 | 4.8798 | 4.9667 | 4.7379 | 4.5456 | 43.2541 | 44.014 | 44.0002 | 43.8675 | 43.8034 | 8.7524 | 8.6563 | 83.8898 | 83.6975 | -38.9099 | 84.0775 | 84.0317 | 0.33417 | -39.006 | 87.9044 | 87.8082 | -0.009155 | 122.406 | 123.1522 | 35.3439 | -0.073242 | 84.1187 | 84.0225 | 83.9676 | -39.3311 | 123.0194 | 122.9553 | 123.1659 | -35.2203
1793.5156 | 123.1659 | -79.2252 | 43.84 | -0.15564 | 0.012459 | 8.1086e-05 | 0.014531 | -0.019126 | 0.003403 | 0.0046891 | -0.18745 | 0.01938 | -0.010858 | 0.016554 | -0.0037854 | 0.011066 | 4.7516 | 4.7607 | 4.6692 | 4.7699 | 4.953 | 4.66 | 4.4907 | 43.19 | 43.9133 | 43.8995 | 43.8766 | 43.7622 | 8.7524 | 8.6472 | 83.8852 | 83.7158 | -38.887 | 83.9859 | 83.9951 | 0.27923 | -39.0884 | 87.9776 | 87.8723 | 0.036621 | 122.4152 | 123.1247 | 35.2524 | -0.07782 | 84.1782 | 83.9767 | 83.8943 | -39.3494 | 123.1018 | 122.9874 | 123.1384 | -35.1929
1794.5156 | 123.4406 | -79.1702 | 43.8492 | -0.10223 | 0.0075451 | 0.0011493 | 0.011326 | -0.019126 | -0.0021512 | 0.0044755 | -0.027237 | 0.017884 | -0.018122 | 0.015272 | -0.0031446 | 0.01192 | 4.8157 | 4.9301 | 4.8019 | 4.8431 | 4.8798 | 4.6875 | 4.5136 | 43.2861 | 44.0231 | 44.0414 | 43.7759 | 43.6981 | 8.757 | 8.6517 | 83.8577 | 83.6838 | -38.9694 | 84.1003 | 84.0134 | 0.32959 | -39.0335 | 87.9272 | 87.822 | -0.073242 | 122.4564 | 123.2117 | 35.3897 | -0.15106 | 84.05 | 83.9859 | 83.9722 | -39.3356 | 122.9462 | 122.8683 | 123.1934 | -35.1974
1795.5156 | 123.1888 | -79.2252 | 43.8354 | -0.16327 | 0.010963 | 0.0032855 | 0.011967 | -0.018698 | 0.0025486 | 0.0029801 | -0.20271 | 0.018953 | -0.011072 | 0.015913 | -0.0042126 | 0.0093567 | 4.7562 | 4.8019 | 4.6967 | 4.7882 | 4.9484 | 4.6738 | 4.5136 | 43.1808 | 43.8446 | 44.0643 | 43.9133 | 43.7714 | 8.757 | 8.6563 | 83.8989 | 83.7387 | -38.887 | 84.0271 | 84.0134 | 0.27466 | -39.0793 | 87.9822 | 87.8815 | 0.07782 | 122.406 | 123.2895 | 35.408 | -0.064087 | 84.1736 | 83.9813 | 83.9218 | -39.3219 | 123.1384 | 122.9965 | 123.0698 | -35.1791
1796.5156 | 123.2208 | -79.2572 | 43.8171 | -0.048828 | 0.01374 | 0.0024311 | 0.015812 | -0.017417 | 0.0044712 | 0.0046891 | -0.15694 | 0.017884 | -0.008295 | 0.015913 | -0.0031446 | 0.0080749 | 4.7974 | 4.8203 | 4.7012 | 4.8065 | 4.921 | 4.6509 | 4.4952 | 43.1351 | 43.927 | 43.9178 | 43.84 | 43.6844 | 8.7524 | 8.6517 | 83.9081 | 83.7524 | -38.8962 | 84.0775 | 84.0637 | 0.31128 | -39.0198 | 88.0096 | 87.9089 | 0.022888 | 122.3923 | 123.175 | 35.2661 | -0.13275 | 84.1782 | 84.0546 | 83.9584 | -39.3219 | 123.0972 | 122.9416 | 123.1842 | -35.1654
1797.5156 | 123.2254 | -79.2389 | 43.7851 | -0.19379 | 0.01075 | 0.0030719 | 0.013463 | -0.018698 | -0.0023648 | 0.0029801 | -0.14931 | 0.018525 | -0.014917 | 0.017622 | -0.0044262 | 0.012775 | 4.7974 | 4.8981 | 4.7653 | 4.8248 | 4.8843 | 4.6921 | 4.4952 | 43.158 | 43.9316 | 43.9316 | 43.7531 | 43.6615 | 8.757 | 8.6472 | 83.931 | 83.7341 | -38.9008 | 84.137 | 84.0637 | 0.32959 | -38.9877 | 87.9959 | 87.886 | -0.032043 | 122.3969 | 123.1705 | 35.2844 | -0.1236 | 84.1232 | 84.0363 | 84.0042 | -39.2899 | 122.9919 | 122.9004 | 123.1705 | -35.1379
1798.5156 | 123.3032 | -79.2435 | 43.7256 | -0.048828 | 0.0060497 | 0.0020037 | 0.010258 | -0.019126 | -0.0032192 | 0.0019119 | -0.057755 | 0.016603 | -0.011927 | 0.016767 | -0.0050672 | 0.011493 | 4.834 | 4.9255 | 4.8065 | 4.8523 | 4.9393 | 4.715 | 4.541 | 43.2312 | 43.959 | 43.9911 | 43.7256 | 43.6478 | 8.757 | 8.6563 | 83.9584 | 83.7845 | -38.7863 | 84.169 | 84.0958 | 0.31128 | -38.8916 | 88.0005 | 87.8998 | 0 | 122.4747 | 123.2346 | 35.3348 | -0.07782 | 84.1827 | 84.0775 | 84.05 | -39.1846 | 122.9691 | 122.8912 | 123.2025 | -35.0693
1799.5156 | 123.1476 | -79.2984 | 43.7988 | 0.36316 | 0.011604 | 0.0032855 | 0.01624 | -0.016562 | 0.004044 | 0.0027665 | -0.2256 | 0.018739 | -0.010645 | 0.016554 | -0.0025036 | 0.010425 | 4.7195 | 4.7287 | 4.6417 | 4.747 | 4.921 | 4.66 | 4.4769 | 43.0893 | 43.8492 | 43.8354 | 43.8171 | 43.6844 | 8.7616 | 8.6517 | 83.9584 | 83.7753 | -38.8779 | 84.0271 | 84.0454 | 0.27008 | -39.0793 | 88.06 | 87.9501 | 0.018311 | 122.3877 | 123.1338 | 35.1837 | -0.11444 | 84.2194 | 84.0179 | 83.9401 | -39.3219 | 123.1155 | 122.9828 | 123.1476 | -35.1471
1800.5156 | 123.1705 | -79.3167 | 43.7485 | 0.37079 | 0.014168 | 0.0015765 | 0.014317 | -0.02233 | 0.0025486 | 0.0042619 | -0.17983 | 0.019593 | -0.010858 | 0.015486 | -0.0035718 | 0.010425 | 4.6875 | 4.7195 | 4.5959 | 4.7058 | 4.9026 | 4.6326 | 4.4632 | 43.0847 | 43.8034 | 43.8263 | 43.7805 | 43.689 | 8.7616 | 8.6563 | 83.9493 | 83.7799 | -38.8458 | 84.0363 | 84.0225 | 0.24261 | -39.061 | 88.0783 | 87.973 | 0.032044 | 122.4014 | 123.143 | 35.17 | -0.059509 | 84.2194 | 84.0042 | 83.9127 | -39.2853 | 123.0972 | 123.0057 | 123.1201 | -35.0922
1801.5312 | 123.2483 | -79.1977 | 43.8126 | 0.24109 | 0.013527 | 0.0017901 | 0.012394 | -0.017844 | 0.0029758 | 0.0055435 | 0.20927 | 0.018739 | -0.014276 | 0.017622 | -0.0016492 | 0.011066 | 4.6005 | 4.6234 | 4.5273 | 4.6005 | 4.7379 | 4.5044 | 4.3304 | 43.222 | 40.979 | 43.9774 | 43.8217 | 43.7164 | 8.7616 | 8.6517 | 83.7021 | 83.5281 | -39.0747 | 83.8211 | 83.7982 | 0.27008 | -39.212 | 87.9593 | 87.8494 | 0.009155 | 122.4197 | 123.175 | 35.3256 | -0.09613 | 83.9355 | 83.7982 | 83.725 | -39.4821 | 123.0194 | 122.9141 | 120.1767 | -35.1608
1802.5156 | 123.317 | -79.1977 | 43.7988 | -0.14801 | 0.0073315 | 0.0013629 | 0.01154 | -0.018057 | -0.0040738 | 0.0027665 | 0.10246 | 0.022371 | -0.012354 | 0.013563 | -0.0054944 | 0.012775 | 4.6967 | 4.8111 | 4.66 | 4.7104 | 4.7424 | 4.5593 | 4.3762 | 43.2037 | 41.6153 | 44.0369 | 43.8034 | 43.7073 | 8.757 | 8.6517 | 83.757 | 83.5739 | -39.0564 | 84.0088 | 83.9081 | 0.33417 | -39.1022 | 87.9547 | 87.8494 | 0.004578 | 122.4014 | 123.2346 | 35.3851 | -0.091553 | 83.9401 | 83.8943 | 83.8577 | -39.4226 | 123.0011 | 122.905 | 120.813 | -35.1471
1803.5156 | 123.1567 | -79.3121 | 43.7622 | -0.17853 | 0.010536 | 0.0034991 | 0.014531 | -0.019766 | 0.0012668 | 0.0016983 | -0.3553 | 0.019166 | -0.010431 | 0.013349 | -0.0035718 | 0.011707 | 4.6371 | 4.6509 | 4.5502 | 4.8752 | 4.8386 | 4.5502 | 4.3671 | 43.0756 | 43.6707 | 43.8263 | 43.7897 | 43.6981 | 8.7616 | 8.6563 | 83.8623 | 83.6792 | -38.9236 | 83.963 | 84.1873 | 0.50812 | -39.1251 | 88.0737 | 87.9684 | 0.027466 | 122.3877 | 123.1384 | 35.17 | -0.064087 | 84.1507 | 83.9493 | 83.8623 | -39.3951 | 123.1018 | 123.0103 | 122.9828 | -35.1059
1804.5156 | 123.3353 | -79.3213 | 43.6661 | -0.14038 | 0.0075451 | 0.0037127 | 0.012822 | -0.018698 | -0.0021512 | 0.0010575 | -0.065384 | 0.018098 | -0.014917 | 0.012708 | -0.0044262 | 0.013629 | 4.7241 | 4.8386 | 4.7058 | 4.7424 | 4.7836 | 4.5868 | 4.4403 | 43.158 | 43.7256 | 44.1879 | 43.7302 | 43.6478 | 8.757 | 8.6609 | 83.9081 | 83.7616 | -38.8824 | 84.1599 | 84.0637 | 0.30212 | -38.942 | 88.0783 | 87.9822 | 0.064087 | 122.4792 | 123.5092 | 35.527 | -0.018311 | 84.1049 | 84.0454 | 84.0271 | -39.2258 | 123.0515 | 122.9691 | 123.0469 | -35.0052
1805.5156 | 123.2025 | -79.3396 | 43.7302 | -0.21667 | 0.0075451 | 0.0032855 | 0.015599 | -0.021048 | 0.00062595 | 0.0023391 | -0.13405 | 0.018953 | -0.010431 | 0.015913 | -0.0035718 | 0.010638 | 4.6875 | 4.7379 | 4.6371 | 4.7012 | 4.7928 | 4.5685 | 4.3991 | 43.1122 | 43.5104 | 43.8583 | 43.7439 | 43.6478 | 8.757 | 8.6609 | 83.9081 | 83.7387 | -38.9374 | 84.0775 | 84.0408 | 0.30212 | -39.0427 | 88.0966 | 88.0005 | 0.013732 | 122.4518 | 123.1979 | 35.1974 | -0.082398 | 84.1324 | 84.0271 | 83.9767 | -39.3311 | 123.0835 | 122.9874 | 122.85 | -35.0693
1806.5156 | 123.1888 | -79.3442 | 43.7119 | -0.056458 | 0.015236 | 0.00093569 | 0.016881 | -0.017844 | 0.0031894 | 0.0025529 | -0.20271 | 0.01938 | -0.0089358 | 0.018263 | -0.0035718 | 0.0076477 | 4.6143 | 4.6326 | 4.5273 | 4.6371 | 4.8203 | 4.5319 | 4.3488 | 43.0161 | 43.6935 | 43.7759 | 43.7485 | 43.6386 | 8.7616 | 8.6563 | 83.876 | 83.6929 | -38.8916 | 83.9767 | 83.9813 | 0.28839 | -39.0976 | 88.1058 | 88.0005 | 0.036621 | 122.3602 | 123.1201 | 35.1196 | -0.073242 | 84.1644 | 83.9584 | 83.8715 | -39.3631 | 123.0927 | 122.9828 | 123.0377 | -35.0555
1807.5156 | 123.1659 | -79.3579 | 43.7027 | -0.23956 | 0.011818 | 0.0041401 | 0.013676 | -0.019766 | -1.505e-05 | 0.0061845 | -0.1722 | 0.019166 | -0.0095768 | 0.018049 | -0.0037854 | 0.01192 | 4.6417 | 4.7012 | 4.5593 | 4.6738 | 4.8294 | 4.5776 | 4.3945 | 43.0344 | 43.3685 | 43.7759 | 43.7439 | 43.634 | 8.7524 | 8.6517 | 83.9355 | 83.7524 | -38.8733 | 84.0591 | 84.0317 | 0.27924 | -39.061 | 88.1104 | 88.0096 | 0.041198 | 122.3923 | 123.1338 | 35.1242 | -0.068665 | 84.1873 | 83.9996 | 83.9172 | -39.3082 | 123.1018 | 122.9919 | 122.7264 | -35.051
1808.5312 | 123.2666 | -79.3625 | 43.6523 | 0.21057 | 0.01374 | 0.00093569 | 0.012822 | -0.018698 | 0.0036166 | 0.0040481 | 0.23979 | 0.018098 | -0.0091494 | 0.016126 | -0.0012218 | 0.012347 | 4.5914 | 4.6371 | 4.5319 | 4.6097 | 4.7333 | 4.509 | 4.3442 | 43.0847 | 43.7073 | 43.8034 | 43.6478 | 43.5333 | 8.7662 | 8.6472 | 83.8715 | 83.7067 | -38.9191 | 83.9996 | 83.9722 | 0.2655 | -39.061 | 88.1287 | 88.0096 | -0.004578 | 122.4472 | 123.1659 | 35.1562 | -0.11902 | 84.0958 | 83.9539 | 83.8943 | -39.3082 | 123.0103 | 122.8958 | 123.0698 | -35.0052
1809.5156 | 123.175 | -79.4083 | 43.6798 | -0.2243 | 0.012459 | 0.0060627 | 0.016453 | -0.018057 | 0.0021214 | 0.0046891 | -0.27138 | 0.01938 | -0.010858 | 0.015058 | -0.0031446 | 0.011707 | 4.6051 | 4.628 | 4.5319 | 4.628 | 4.8248 | 4.5639 | 4.3808 | 42.9886 | 43.5883 | 43.7439 | 43.721 | 43.6295 | 8.7616 | 8.6517 | 83.9722 | 83.7891 | -38.855 | 84.0363 | 84.0363 | 0.24719 | -39.0747 | 88.1699 | 88.06 | 0.041198 | 122.3969 | 123.1522 | 35.0922 | -0.050354 | 84.2331 | 84.0134 | 83.9401 | -39.299 | 123.1293 | 123.0377 | 122.9965 | -35.0281
1810.5156 | 123.2758 | -79.2572 | 43.7531 | -0.12512 | 0.0077587 | 0.0026447 | 0.013249 | -0.020194 | -0.0040738 | 0.00041648 | -0.12642 | 0.016603 | -0.011927 | 0.015058 | -0.0033582 | 0.010852 | 4.6143 | 4.6829 | 4.5776 | 4.6371 | 4.6875 | 4.4907 | 4.3213 | 43.1488 | 40.8417 | 43.9316 | 43.7393 | 43.6523 | 8.7616 | 8.6609 | 83.7479 | 83.5785 | -39.0656 | 83.9401 | 83.8943 | 0.31586 | -39.1388 | 88.0188 | 87.9181 | -0.013733 | 122.406 | 123.1888 | 35.2707 | -0.10071 | 83.9447 | 83.8715 | 83.8348 | -39.4318 | 122.9965 | 122.9095 | 120.0989 | -35.0922
1811.5156 | 123.1842 | -79.4266 | 43.6386 | -0.018311 | 0.01844 | -0.00098691 | 0.013676 | -0.019126 | 0.0029758 | 0.0051163 | -0.027237 | 0.02173 | -0.011713 | 0.017195 | -0.00058103 | 0.0099975 | 4.6188 | 4.6143 | 4.5044 | 4.6097 | 4.7379 | 4.4952 | 4.3167 | 42.9794 | 43.5837 | 43.7073 | 43.6707 | 43.5745 | 8.7524 | 8.6517 | 83.9218 | 83.7433 | -38.9008 | 84.0408 | 84.0363 | 0.29297 | -39.0198 | 88.179 | 88.0783 | 0.032043 | 122.406 | 123.1338 | 35.0555 | -0.064087 | 84.1644 | 84.0454 | 83.931 | -39.3219 | 123.0972 | 123.0011 | 123.0103 | -34.9869
1812.5156 | 123.3078 | -79.2618 | 43.7073 | 0.035095 | 0.0062635 | 0.0045673 | 0.012181 | -0.018698 | -0.0036464 | 0.0021255 | 0.01091 | 0.016176 | -0.011927 | 0.015699 | -0.0050672 | 0.012347 | 4.5319 | 4.6417 | 4.5181 | 4.5685 | 4.6738 | 4.4632 | 4.2847 | 43.1488 | 40.8234 | 43.9362 | 43.7256 | 43.6569 | 8.7616 | 8.6655 | 83.725 | 83.5464 | -39.0335 | 83.9035 | 83.8303 | 0.28381 | -39.1754 | 88.0234 | 87.9272 | 0.018311 | 122.4106 | 123.1979 | 35.2707 | -0.050354 | 83.9355 | 83.7936 | 83.7799 | -39.4226 | 122.9874 | 122.9187 | 120.0851 | -35.0418
1813.5156 | 123.1842 | -79.3854 | 43.6935 | -0.064087 | 0.016731 | 0.0026447 | 0.01624 | -0.020621 | 0.0063938 | 0.0046891 | -0.080643 | 0.018739 | -0.010645 | 0.016767 | -0.0031446 | 0.0091431 | 4.5547 | 4.5364 | 4.4403 | 4.541 | 4.6875 | 4.4312 | 4.2664 | 43.0573 | 41.7847 | 43.7805 | 43.6844 | 43.6432 | 8.757 | 8.6563 | 83.8165 | 83.6517 | -39.006 | 83.9218 | 83.9264 | 0.27466 | -39.1388 | 88.1424 | 88.0417 | -0.009155 | 122.4426 | 123.1659 | 35.1242 | -0.050354 | 84.0729 | 83.9401 | 83.8257 | -39.4272 | 123.0698 | 123.0286 | 121.17 | -35.0372
1814.5156 | 123.2986 | -79.2572 | 43.721 | -0.13275 | 0.0077587 | 0.0079853 | 0.015385 | -0.019766 | -0.001083 | 0.0025529 | -0.088272 | 0.01938 | -0.016626 | 0.016554 | -0.0052808 | 0.010211 | 4.5776 | 4.6005 | 4.454 | 4.5547 | 4.628 | 4.4128 | 4.248 | 43.1763 | 40.8371 | 43.9636 | 43.7531 | 43.6569 | 8.7662 | 8.6517 | 83.67 | 83.5052 | -39.093 | 83.8577 | 83.812 | 0.3067 | -39.1434 | 88.0234 | 87.9089 | 0.032044 | 122.4335 | 123.2208 | 35.3119 | -0.064087 | 83.8852 | 83.8348 | 83.7112 | -39.473 | 123.0103 | 122.9141 | 120.0943 | -35.0693
1815.5156 | 123.1705 | -79.2801 | 43.7897 | -0.19379 | 0.010536 | 0.0015765 | 0.009831 | -0.01763 | 0.0014804 | 0.0029801 | -0.19508 | 0.019166 | -0.010004 | 0.018476 | -0.0035718 | 0.012561 | 4.4357 | 4.3991 | 4.3076 | 4.4357 | 4.6326 | 4.3488 | 4.1885 | 43.0984 | 40.7501 | 43.8583 | 43.8492 | 43.7439 | 8.7662 | 8.6563 | 83.6288 | 83.4686 | -39.1571 | 83.6792 | 83.7158 | 0.24719 | -39.3539 | 88.0463 | 87.9364 | 0.059509 | 122.3785 | 123.1384 | 35.202 | -0.045777 | 83.9127 | 83.7158 | 83.5876 | -39.6011 | 123.1293 | 123.024 | 120.0302 | -35.1334
1816.5156 | 123.23 | -79.2755 | 43.7576 | -0.0030518 | 0.021644 | -0.00055971 | 0.017094 | -0.019766 | 0.003403 | 0.0042619 | -0.11879 | 0.018098 | -0.010858 | 0.015913 | -0.00058103 | 0.010425 | 4.4815 | 4.4586 | 4.3488 | 4.454 | 4.6005 | 4.3488 | 4.1748 | 43.1396 | 40.741 | 43.8675 | 43.7942 | 43.6707 | 8.7616 | 8.6563 | 83.6243 | 83.4503 | -39.1571 | 83.7341 | 83.7296 | 0.27924 | -39.2761 | 88.0371 | 87.9318 | 0.036621 | 122.4152 | 123.143 | 35.2112 | -0.086975 | 83.876 | 83.757 | 83.6243 | -39.5828 | 123.0698 | 122.9462 | 120.0165 | -35.1013
1817.5156 | 123.2254 | -79.3167 | 43.7393 | -0.16327 | 0.0096813 | 0.0030719 | 0.011967 | -0.016776 | -0.0017238 | 0.0023391 | -0.11879 | 0.020234 | -0.012354 | 0.016554 | -0.0063488 | 0.012988 | 4.4266 | 4.5273 | 4.4037 | 4.4769 | 4.5547 | 4.3442 | 4.1656 | 43.0801 | 40.6906 | 43.8675 | 43.7302 | 43.6432 | 8.7662 | 8.6563 | 83.6609 | 83.4824 | -39.1846 | 83.844 | 83.7936 | 0.31128 | -39.3127 | 88.0829 | 87.973 | -0.009155 | 122.3969 | 123.1842 | 35.2112 | -0.096131 | 83.8715 | 83.7433 | 83.7204 | -39.5737 | 123.0469 | 122.9599 | 120.0073 | -35.083
1818.5156 | 123.2712 | -79.3259 | 43.6844 | 0.20294 | 0.015663 | 0.0022175 | 0.015172 | -0.01998 | 0.001694 | 0.0021255 | 0.19402 | 0.018098 | -0.0085086 | 0.015699 | -0.0027172 | 0.010425 | 4.4037 | 4.422 | 4.3304 | 4.4266 | 4.5685 | 4.3259 | 4.1565 | 43.1076 | 40.5808 | 43.8629 | 43.7027 | 43.6249 | 8.7662 | 8.6563 | 83.6517 | 83.4824 | -39.1159 | 83.7479 | 83.7524 | 0.27008 | -39.2807 | 88.092 | 87.9822 | 0.018311 | 122.4335 | 123.1888 | 35.2066 | -0.059509 | 83.8943 | 83.7296 | 83.6563 | -39.5279 | 123.0286 | 122.9507 | 119.9066 | -35.0281
1819.5156 | 123.1934 | -79.3259 | 43.7531 | -0.20142 | 0.0098951 | 0.0032855 | 0.013676 | -0.018057 | 0.00062595 | 0.0019119 | -0.11116 | 0.021516 | -0.011927 | 0.015913 | -0.0052808 | 0.013202 | 4.4083 | 4.454 | 4.3396 | 4.4312 | 4.5776 | 4.2984 | 4.1565 | 43.0801 | 40.5762 | 43.8446 | 43.8126 | 43.7027 | 8.7662 | 8.6563 | 83.6243 | 83.4824 | -39.1754 | 83.7799 | 83.757 | 0.27466 | -39.3448 | 88.092 | 87.9822 | 0.059509 | 122.406 | 123.1705 | 35.1883 | -0.050354 | 83.9035 | 83.7341 | 83.6655 | -39.5966 | 123.1384 | 123.0286 | 119.902 | -35.0967
1820.5156 | 123.317 | -79.2938 | 43.721 | -0.010681 | 0.0079723 | 0.0030719 | 0.013035 | -0.020194 | -0.0040738 | 0.0010575 | 0.018539 | 0.018739 | -0.012995 | 0.015058 | -0.0048534 | 0.011066 | 4.3533 | 4.4495 | 4.3442 | 4.3945 | 4.454 | 4.2664 | 4.0924 | 43.1534 | 40.686 | 43.9453 | 43.7439 | 43.6295 | 8.7616 | 8.6517 | 83.5602 | 83.3862 | -39.267 | 83.7433 | 83.6884 | 0.30212 | -39.3677 | 88.0554 | 87.9456 | 0.022888 | 122.4472 | 123.2391 | 35.2936 | -0.091552 | 83.7479 | 83.6472 | 83.638 | -39.6286 | 123.0377 | 122.9233 | 119.9799 | -35.0693
1821.5156 | 123.2208 | -79.3396 | 43.6935 | -0.056458 | 0.016517 | -0.00098691 | 0.015385 | -0.015708 | 0.0038304 | 0.0070389 | -0.21034 | 0.020021 | -0.011072 | 0.016767 | -0.0014356 | 0.0089295 | 4.4357 | 4.4815 | 4.4083 | 4.4357 | 4.5731 | 4.3076 | 4.129 | 43.1076 | 40.5945 | 43.8171 | 43.7439 | 43.6752 | 8.757 | 8.6609 | 83.6472 | 83.4686 | -39.1205 | 83.8211 | 83.7753 | 0.3067 | -39.2578 | 88.0966 | 88.0005 | 0.050354 | 122.4472 | 123.1567 | 35.1562 | -0.01831 | 83.9127 | 83.7753 | 83.7479 | -39.5645 | 123.0835 | 123.0148 | 119.9341 | -35.0327
1822.5156 | 123.3078 | -79.2984 | 43.721 | -1.4755 | 0.0058361 | 0.0028583 | 0.0096174 | -0.018698 | -0.0036464 | 0.0025529 | -0.11116 | 0.018312 | -0.012567 | 0.016126 | -0.005708 | 0.012561 | 4.3671 | 4.5044 | 4.3991 | 4.422 | 4.4632 | 4.2709 | 4.1153 | 43.1488 | 40.654 | 43.927 | 43.7256 | 43.6249 | 8.7616 | 8.6609 | 83.5693 | 83.4137 | -39.2578 | 83.8028 | 83.7204 | 0.3067 | -39.3539 | 88.06 | 87.9593 | 0.004578 | 122.4472 | 123.2254 | 35.2661 | -0.09613 | 83.7616 | 83.6655 | 83.6975 | -39.6057 | 123.024 | 122.9233 | 119.9524 | -35.0601
1823.5312 | 123.1888 | -79.3762 | 43.6844 | 0.16479 | 0.015449 | 8.1086e-05 | 0.016453 | -0.019766 | 0.002335 | 0.0044755 | 0.13298 | 0.020234 | -0.011927 | 0.019331 | -0.0029308 | 0.011066 | 4.2526 | 4.2618 | 4.1656 | 4.2709 | 4.4632 | 4.1931 | 4.0146 | 43.0389 | 40.416 | 43.7759 | 43.7073 | 43.6386 | 8.7616 | 8.6563 | 83.5693 | 83.3908 | -39.2212 | 83.638 | 83.6472 | 0.25635 | -39.4318 | 88.1378 | 88.0325 | 0.022888 | 122.4152 | 123.1522 | 35.1196 | -0.045776 | 83.8394 | 83.6288 | 83.5419 | -39.6698 | 123.0835 | 123.0148 | 119.7922 | -35.0281
1824.5156 | 123.2895 | -79.335 | 43.689 | -0.10986 | 0.0062635 | 0.0039263 | 0.011113 | -0.016989 | -0.004501 | 0.0034073 | -0.10353 | 0.017457 | -0.014704 | 0.014845 | -0.0027172 | 0.011707 | 4.3533 | 4.4495 | 4.3213 | 4.3762 | 4.4403 | 4.2526 | 4.0695 | 43.1076 | 40.5899 | 43.8675 | 43.6935 | 43.6295 | 8.7616 | 8.6517 | 83.5876 | 83.4045 | -39.2487 | 83.7845 | 83.7112 | 0.3067 | -39.3356 | 88.0966 | 87.9868 | 0.004577 | 122.4426 | 123.2025 | 35.2158 | -0.059509 | 83.7753 | 83.6884 | 83.6563 | -39.6194 | 123.0286 | 122.9645 | 119.9249 | -35.0372
1825.5156 | 123.2803 | -79.3259 | 43.6798 | -0.31586 | 0.0094677 | 0.0013629 | 0.010472 | -0.019339 | -0.0019376 | 0.0040481 | -0.11116 | 0.018739 | -0.010431 | 0.014204 | -0.0044262 | 0.010852 | 4.3121 | 4.3991 | 4.2755 | 4.3259 | 4.3716 | 4.1977 | 4.0237 | 43.1259 | 40.5808 | 43.9041 | 43.6798 | 43.602 | 8.7616 | 8.6517 | 83.5236 | 83.3496 | -39.3082 | 83.725 | 83.6517 | 0.30212 | -39.3677 | 88.0875 | 87.9776 | 0 | 122.4518 | 123.23 | 35.2524 | -0.07782 | 83.6975 | 83.638 | 83.6014 | -39.6561 | 123.0057 | 122.9279 | 119.9066 | -35.0281
1826.5156 | 123.2849 | -79.3121 | 43.6981 | 0.042725 | 0.0041271 | 0.0032855 | 0.0089764 | -0.020407 | -0.0047146 | 0.0012711 | 0.018539 | 0.016603 | -0.013422 | 0.014631 | -0.0033582 | 0.012347 | 4.3076 | 4.3854 | 4.2847 | 4.3579 | 4.4403 | 4.2435 | 4.0649 | 43.1488 | 40.5945 | 43.927 | 43.7256 | 43.6203 | 8.7616 | 8.6563 | 83.5556 | 83.3771 | -39.2578 | 83.6975 | 83.67 | 0.29297 | -39.3906 | 88.0737 | 87.9684 | 0.027466 | 122.4609 | 123.2391 | 35.2707 | -0.07782 | 83.7524 | 83.6197 | 83.5968 | -39.6332 | 123.0377 | 122.9324 | 119.9066 | -35.0418
1827.5156 | 123.2712 | -79.3625 | 43.689 | -0.15564 | 0.0090405 | 0.00050849 | 0.016453 | -0.018698 | -0.00022865 | -0.00022432 | -0.1722 | 0.016603 | -0.012995 | 0.014631 | -0.003999 | 0.010211 | 4.3854 | 4.4357 | 4.3304 | 4.39 | 4.4632 | 4.2664 | 4.097 | 43.103 | 40.5533 | 43.8538 | 43.7119 | 43.6249 | 8.7616 | 8.6609 | 83.6288 | 83.4595 | -39.2258 | 83.7982 | 83.7524 | 0.29297 | -39.3036 | 88.1241 | 88.0234 | 0.022888 | 122.4655 | 123.2162 | 35.1929 | -0.064087 | 83.8257 | 83.7479 | 83.6929 | -39.592 | 123.0743 | 122.9874 | 119.9158 | -35.0281
1828.5156 | 123.2712 | -79.3442 | 43.6935 | -0.13275 | 0.0079723 | 0.0043537 | 0.013676 | -0.021689 | -0.0017238 | 0.0036209 | -0.14168 | 0.016816 | -0.012567 | 0.013136 | -0.0044262 | 0.0085021 | 4.3442 | 4.4128 | 4.2892 | 4.3442 | 4.39 | 4.2206 | 4.0375 | 43.1351 | 40.567 | 43.8721 | 43.7073 | 43.6157 | 8.7662 | 8.6609 | 83.5648 | 83.3817 | -39.3036 | 83.757 | 83.6884 | 0.3067 | -39.3494 | 88.1104 | 88.0051 | 0.013733 | 122.4792 | 123.2162 | 35.2112 | -0.077819 | 83.7341 | 83.6884 | 83.6334 | -39.6561 | 123.0515 | 122.9599 | 119.9112 | -35.0327
1829.5156 | 123.2071 | -79.3991 | 43.6661 | -0.19379 | 0.010536 | 0.0028583 | 0.012608 | -0.016562 | -1.505e-05 | 0.0044755 | -0.16457 | 0.017671 | -0.015345 | 0.015272 | -0.0033582 | 0.011066 | 4.2938 | 4.3259 | 4.2297 | 4.303 | 4.4083 | 4.184 | 4.0146 | 43.2724 | 41.4963 | 43.7439 | 43.6707 | 43.5928 | 8.7433 | 8.6563 | 83.5831 | 83.4137 | -39.2578 | 83.725 | 83.7021 | 0.28839 | -39.3723 | 88.1424 | 88.0554 | 0.004577 | 122.6715 | 123.143 | 35.0876 | -0.073243 | 83.8074 | 83.6929 | 83.6288 | -39.6515 | 123.0698 | 122.9919 | 120.8954 | -35.0098
1830.5156 | 123.2986 | -79.3488 | 43.6752 | -0.010681 | 0.0060497 | 0.0037127 | 0.011754 | -0.021903 | -0.0017238 | -0.00065152 | 0.0032804 | 0.018098 | -0.013208 | 0.014845 | -0.0048534 | 0.011279 | 4.3121 | 4.3808 | 4.2755 | 4.3442 | 4.4174 | 4.2206 | 4.0512 | 43.1168 | 40.5533 | 43.8812 | 43.6569 | 43.5745 | 8.7524 | 8.6563 | 83.5693 | 83.4 | -39.2578 | 83.7296 | 83.6929 | 0.29297 | -39.3631 | 88.1012 | 88.0051 | -0.018311 | 122.4655 | 123.23 | 35.2249 | -0.10071 | 83.7662 | 83.6609 | 83.6243 | -39.624 | 123.0057 | 122.9233 | 119.902 | -35.0189
1831.5156 | 123.2117 | -79.3533 | 43.6981 | -0.14801 | 0.015663 | 0.0032855 | 0.016881 | -0.018057 | 0.005753 | 0.0046891 | -0.24086 | 0.018953 | -0.010858 | 0.017622 | -0.003999 | 0.0095703 | 4.2343 | 4.2297 | 4.1245 | 4.2343 | 4.39 | 4.1428 | 3.9459 | 43.0893 | 40.5304 | 43.7805 | 43.7485 | 43.6478 | 8.757 | 8.6563 | 83.4961 | 83.2993 | -39.3082 | 83.5831 | 83.5876 | 0.28839 | -39.4638 | 88.1104 | 88.0096 | 0.050354 | 122.4426 | 123.1339 | 35.1242 | -0.050354 | 83.7433 | 83.5876 | 83.4778 | -39.7522 | 123.1018 | 123.0011 | 119.8837 | -35.0418
1832.5156 | 123.2986 | -79.335 | 43.6798 | -0.16327 | 0.0069043 | 0.0039263 | 0.017521 | -0.018271 | 0.0029758 | 0.0029801 | -0.31715 | 0.016603 | -0.014704 | 0.01634 | -0.0048534 | 0.011066 | 4.0604 | 4.4128 | 4.216 | 4.2206 | 4.3076 | 4.129 | 3.9642 | 43.1259 | 40.6082 | 43.8858 | 43.6752 | 43.5928 | 8.757 | 8.6609 | 83.4641 | 83.2993 | -39.3723 | 83.7479 | 83.5556 | 0.25635 | -39.6194 | 88.092 | 87.9959 | -0.004578 | 122.4609 | 123.2208 | 35.2249 | -0.086976 | 83.6426 | 83.3954 | 83.551 | -39.7156 | 123.0103 | 122.9279 | 119.9432 | -35.0189
1833.5156 | 123.1934 | -79.5181 | 43.602 | -0.67444 | 0.013954 | -0.00013251 | 0.015385 | -0.018057 | 0.0027622 | 0.0036209 | -0.16457 | 0.019166 | -0.010218 | 0.014845 | -0.003999 | 0.010425 | 4.1931 | 4.2755 | 4.1519 | 4.2343 | 4.4357 | 4.1794 | 3.9963 | 42.9153 | 43.5379 | 43.6203 | 43.634 | 43.4967 | 8.7662 | 8.6563 | 83.6975 | 83.5144 | -39.1663 | 83.7936 | 83.7524 | 0.23804 | -39.4089 | 88.2843 | 88.1744 | 0.032043 | 122.4335 | 123.1384 | 34.964 | -0.10529 | 83.9539 | 83.7112 | 83.67 | -39.6057 | 123.1522 | 123.0148 | 123.056 | -34.9457
1834.5156 | 123.2895 | -79.4907 | 43.5379 | 0.027466 | 0.0060497 | 0.0028583 | 0.014317 | -0.019553 | -0.0032192 | 0.0023391 | 0.071945 | 0.018098 | -0.01214 | 0.013349 | -0.0059216 | 0.011493 | 4.2572 | 4.3213 | 4.2206 | 4.2892 | 4.3991 | 4.1794 | 4.01 | 42.9794 | 43.634 | 43.721 | 43.5379 | 43.4921 | 8.7662 | 8.6609 | 83.67 | 83.5007 | -39.1388 | 83.812 | 83.7799 | 0.27924 | -39.2807 | 88.2568 | 88.1516 | 0 | 122.4701 | 123.2117 | 35.0601 | -0.045777 | 83.8898 | 83.7479 | 83.7112 | -39.5279 | 123.0286 | 122.9828 | 123.1247 | -34.877
1835.5156 | 123.2025 | -79.5364 | 43.5333 | -0.18616 | 0.010536 | 0.0017901 | 0.014103 | -0.018485 | -0.00044225 | 0.0036209 | -0.16457 | 0.020234 | -0.012354 | 0.015913 | -0.0031446 | 0.011066 | 4.2984 | 4.335 | 4.2252 | 4.2984 | 4.4037 | 4.1794 | 4.0283 | 42.8787 | 43.5745 | 43.6111 | 43.5516 | 43.4875 | 8.7616 | 8.6655 | 83.7158 | 83.5648 | -39.1296 | 83.8715 | 83.8348 | 0.27008 | -39.2349 | 88.298 | 88.2019 | 0.018311 | 122.4152 | 123.1476 | 34.9457 | -0.045776 | 83.9401 | 83.8348 | 83.7616 | -39.505 | 123.0881 | 123.024 | 123.111 | -34.8679
1836.5156 | 123.2162 | -79.5547 | 43.5516 | -0.20142 | 0.011604 | 0.0037127 | 0.013463 | -0.015708 | 0.004044 | 0.0027665 | -0.1722 | 0.020875 | -0.013636 | 0.01634 | -0.0037854 | 0.0080749 | 4.2206 | 4.2572 | 4.1382 | 4.2343 | 4.4266 | 4.129 | 3.9551 | 42.8925 | 43.5608 | 43.602 | 43.5654 | 43.4784 | 8.7662 | 8.6563 | 83.6838 | 83.5098 | -39.1251 | 83.812 | 83.7891 | 0.27924 | -39.3311 | 88.3209 | 88.2111 | 0.013733 | 122.4472 | 123.1567 | 34.9457 | -0.073242 | 83.9813 | 83.7753 | 83.6929 | -39.5966 | 123.1201 | 123.0331 | 123.1155 | -34.8953
1837.5156 | 123.2895 | -79.3945 | 43.6295 | -0.048828 | 0.0096813 | 0.0024311 | 0.010685 | -0.01464 | -0.00065585 | 0.0027665 | -0.11116 | 0.019807 | -0.013208 | 0.016126 | -0.0029308 | 0.012134 | 4.1977 | 4.2801 | 4.184 | 4.2206 | 4.2709 | 4.0833 | 3.9276 | 43.5287 | 40.4892 | 43.8171 | 43.6203 | 43.5333 | 8.7662 | 8.67 | 83.4778 | 83.3221 | -39.3585 | 83.6746 | 83.6151 | 0.29297 | -39.4318 | 88.1607 | 88.0646 | -0.009156 | 122.9233 | 123.2117 | 35.1471 | -0.096131 | 83.6655 | 83.5922 | 83.5785 | -39.7018 | 123.0148 | 122.9279 | 119.8837 | -34.9594
1838.5156 | 123.2895 | -79.4266 | 43.5699 | -0.10986 | 0.0092541 | 0.0026447 | 0.014317 | -0.019339 | -0.0047146 | 0.0014847 | -0.088272 | 0.016389 | -0.012995 | 0.016554 | -0.0044262 | 0.010425 | 4.2023 | 4.3121 | 4.1885 | 4.2206 | 4.2709 | 4.0924 | 3.923 | 43.6157 | 40.3976 | 43.7759 | 43.5516 | 43.5104 | 8.7616 | 8.6746 | 83.519 | 83.3496 | -39.299 | 83.7387 | 83.6472 | 0.29755 | -39.3677 | 88.1882 | 88.1012 | -0.01831 | 123.0423 | 123.2025 | 35.1013 | -0.059509 | 83.6975 | 83.6288 | 83.6151 | -39.6469 | 122.9782 | 122.937 | 119.8242 | -34.8953
1839.5156 | 123.3765 | -79.4083 | 43.5791 | -0.071716 | 0.0092541 | 0.0030719 | 0.012608 | -0.019339 | -0.0030056 | 0.0025529 | -0.11879 | 0.017244 | -0.015772 | 0.013777 | -0.0033582 | 0.010211 | 4.1977 | 4.2801 | 4.1565 | 4.1885 | 4.2435 | 4.0695 | 3.8956 | 43.0298 | 40.4068 | 43.7531 | 43.5974 | 43.515 | 8.7616 | 8.6609 | 83.4778 | 83.3038 | -39.3356 | 83.6884 | 83.5968 | 0.29297 | -39.3814 | 88.1699 | 88.0692 | 0.01831 | 122.438 | 123.1613 | 35.0922 | -0.064087 | 83.6517 | 83.606 | 83.5648 | -39.6835 | 123.0057 | 122.9233 | 119.8151 | -34.9182
1840.5156 | 123.5092 | -79.4037 | 43.6432 | -0.10223 | 0.0077587 | 0.0022175 | 0.014744 | -0.020407 | -0.00065585 | 0.0036209 | -0.027237 | 0.018312 | -0.013422 | 0.012281 | -0.0065624 | 0.010211 | 4.2114 | 4.2984 | 4.1794 | 4.2297 | 4.2755 | 4.0833 | 3.9185 | 42.9794 | 40.4205 | 43.6752 | 43.6111 | 43.5104 | 8.7616 | 8.67 | 83.4869 | 83.3221 | -39.3677 | 83.7021 | 83.6334 | 0.31128 | -39.4318 | 88.1653 | 88.0737 | -0.032043 | 122.3831 | 123.0789 | 35.0052 | -0.13275 | 83.6792 | 83.6151 | 83.5831 | -39.7247 | 123.0148 | 122.9141 | 119.8242 | -34.9731
1841.5156 | 123.175 | -79.216 | 43.895 | -0.32349 | 0.012031 | 0.0039263 | 0.012608 | -0.019553 | 0.001694 | 0.0031937 | -0.19508 | 0.018739 | -0.011927 | 0.014845 | -0.0061352 | 0.0072205 | 4.0833 | 4.097 | 3.9871 | 4.0604 | 4.2664 | 3.9963 | 3.8086 | 42.485 | 40.0772 | 41.7572 | 43.9407 | 43.8171 | 8.7616 | 8.6655 | 83.2123 | 83.0246 | -39.6286 | 83.313 | 83.2764 | 0.25177 | -39.8117 | 87.9776 | 87.8815 | 0.045777 | 121.701 | 120.9732 | 33.0917 | -0.077819 | 83.4824 | 83.2993 | 83.2031 | -40.0864 | 123.1567 | 123.0331 | 119.2932 | -35.2295
1842.5156 | 123.3215 | -79.4495 | 43.6249 | -0.086975 | 0.0069043 | 0.00050849 | 0.013249 | -0.016776 | -0.0023648 | 0.0027665 | 0.0032804 | 0.018525 | -0.012995 | 0.014204 | -0.0035718 | 0.013629 | 4.2526 | 4.3213 | 4.1931 | 4.2572 | 4.3121 | 4.1153 | 3.9322 | 43.6523 | 40.3198 | 43.5562 | 43.5516 | 43.483 | 8.7662 | 8.6655 | 83.5648 | 83.3817 | -39.3127 | 83.7708 | 83.7067 | 0.32501 | -39.3723 | 88.2156 | 88.1149 | -0.073242 | 123.1018 | 123.0057 | 34.8907 | -0.14191 | 83.7616 | 83.7021 | 83.6426 | -39.6927 | 123.0011 | 122.9324 | 119.7693 | -34.9594
1843.5156 | 123.2117 | -79.4998 | 43.5974 | -0.20905 | 0.011604 | 0.0034991 | 0.016026 | -0.016776 | -1.505e-05 | 0.0038345 | -0.2256 | 0.017671 | -0.013208 | 0.013777 | -0.0031446 | 0.011066 | 4.1153 | 4.184 | 4.0421 | 4.1428 | 4.3167 | 4.0649 | 3.8864 | 43.515 | 40.1596 | 43.2495 | 43.6295 | 43.5425 | 8.7616 | 8.6655 | 83.5648 | 83.3862 | -39.2807 | 83.6838 | 83.6426 | 0.25635 | -39.4821 | 88.2614 | 88.1653 | 0.032044 | 123.0148 | 122.7493 | 34.584 | -0.054932 | 83.8165 | 83.6151 | 83.5419 | -39.711 | 123.1293 | 123.0423 | 119.6594 | -34.9319
1844.5156 | 123.2529 | -79.5959 | 43.4235 | -0.16327 | 0.0060497 | 0.0022175 | 0.011326 | -0.018057 | 0.0014804 | 0.0042619 | -0.14168 | 0.020448 | -0.011927 | 0.012281 | -0.0046398 | 0.014056 | 4.2801 | 4.335 | 4.2206 | 4.3076 | 4.3625 | 4.1611 | 3.9917 | 42.6727 | 43.3548 | 43.3411 | 43.4372 | 43.3594 | 8.7662 | 8.6655 | 83.757 | 83.5876 | -39.061 | 83.931 | 83.9035 | 0.31586 | -39.1434 | 88.3621 | 88.2614 | 0.013733 | 122.2687 | 122.937 | 34.6756 | -0.064087 | 83.9584 | 83.876 | 83.8165 | -39.4318 | 123.0331 | 122.9553 | 122.9507 | -34.758
1845.5156 | 123.2574 | -79.4861 | 43.5562 | -0.19379 | 0.0094677 | 0.0028583 | 0.014317 | -0.019553 | 0.0010532 | 0.0031937 | -0.17983 | 0.016603 | -0.013849 | 0.013777 | -0.0025036 | 0.012775 | 4.1428 | 4.2114 | 4.1061 | 4.1702 | 4.2664 | 4.0329 | 3.8727 | 42.8146 | 40.2512 | 43.5196 | 43.5608 | 43.4509 | 8.7753 | 8.6563 | 83.519 | 83.3588 | -39.2899 | 83.6975 | 83.6563 | 0.29755 | -39.4135 | 88.2614 | 88.1424 | 0.004578 | 122.3007 | 123.0057 | 34.8633 | -0.10529 | 83.7524 | 83.6288 | 83.5922 | -39.6835 | 123.0469 | 122.937 | 119.7372 | -34.8999
1846.5156 | 123.262 | -79.6509 | 43.4235 | -0.16327 | 0.016945 | -0.00034611 | 0.016453 | -0.018485 | 0.0048984 | 0.0059707 | -0.17983 | 0.01938 | -0.0095768 | 0.015486 | -0.0025036 | 0.011066 | 4.1611 | 4.2023 | 4.0787 | 4.1702 | 4.303 | 4.0421 | 3.8956 | 43.428 | 42.9565 | 43.2724 | 43.4189 | 43.3182 | 8.7708 | 8.6609 | 83.6929 | 83.5464 | -39.1205 | 83.8531 | 83.8211 | 0.27466 | -39.2624 | 88.4216 | 88.3118 | -0.004578 | 123.0789 | 122.9233 | 34.6115 | -0.10529 | 83.9539 | 83.812 | 83.7296 | -39.5279 | 123.0698 | 122.9691 | 122.6074 | -34.7626
1847.5156 | 123.2071 | -79.4403 | 43.6523 | -0.20905 | 0.010536 | 0.0039263 | 0.012181 | -0.01998 | -0.0015102 | 0.0034073 | -0.12642 | 0.019807 | -0.010004 | 0.015486 | -0.0048534 | 0.013202 | 4.0283 | 4.097 | 3.9825 | 4.0604 | 4.2252 | 3.9505 | 3.7994 | 43.4784 | 43.222 | 41.5604 | 43.6295 | 43.5516 | 8.7708 | 8.6609 | 83.3908 | 83.2397 | -39.4272 | 83.5373 | 83.5007 | 0.26093 | -39.624 | 88.2111 | 88.1012 | -0.022888 | 122.9187 | 121.0007 | 32.8995 | -0.10071 | 83.6655 | 83.4686 | 83.4229 | -39.8529 | 123.0698 | 122.9919 | 122.6624 | -34.9915
1848.5156 | 123.317 | -79.5776 | 43.4464 | -0.048828 | 0.0073315 | 0.0015765 | 0.011326 | -0.020407 | -0.0053554 | 0.0029801 | 0.01091 | 0.014039 | -0.011499 | 0.015272 | -0.0063488 | 0.015125 | 4.1519 | 4.248 | 4.1199 | 4.1565 | 4.248 | 4.0466 | 3.8818 | 43.4921 | 43.5104 | 42.3386 | 43.4555 | 43.3594 | 8.7662 | 8.6609 | 83.6243 | 83.4595 | -39.1983 | 83.8257 | 83.7341 | 0.27466 | -39.2944 | 88.3438 | 88.2385 | 0.009155 | 123.0698 | 121.9162 | 33.6777 | -0.086975 | 83.8257 | 83.7296 | 83.6975 | -39.5645 | 123.0331 | 122.937 | 123.0881 | -34.7855
1849.5156 | 123.2162 | -79.7241 | 43.3777 | -0.20905 | 0.0098951 | 0.0034991 | 0.014531 | -0.019766 | -0.00044225 | -1.0724e-05 | -0.13405 | 0.020234 | -0.01214 | 0.014417 | -0.0046398 | 0.011279 | 4.1199 | 4.1977 | 4.0604 | 4.1565 | 4.2847 | 4.0329 | 3.8589 | 43.2907 | 43.2449 | 43.0984 | 43.3914 | 43.2907 | 8.7616 | 8.6609 | 83.757 | 83.5831 | -39.093 | 83.9218 | 83.8806 | 0.29755 | -39.2578 | 88.4857 | 88.385 | 0.013732 | 123.0148 | 122.8226 | 34.4376 | -0.086976 | 84.0088 | 83.844 | 83.7845 | -39.5187 | 123.1155 | 123.0148 | 122.9691 | -34.7168
1850.5156 | 123.3444 | -79.3076 | 43.7393 | -0.064087 | 0.0075451 | 0.0022175 | 0.011113 | -0.01998 | -0.0021512 | 0.0031937 | -3.0485 | 0.015962 | -0.011713 | 0.015272 | -0.0044262 | 0.011493 | 4.0604 | 4.1611 | 4.0421 | 4.0695 | 4.1473 | 3.9276 | 3.772 | 43.7714 | 39.9536 | 42.0181 | 43.7073 | 43.6249 | 8.7708 | 8.6655 | 83.2352 | 83.0795 | -39.592 | 83.4686 | 83.3771 | 0.29755 | -39.679 | 88.0783 | 87.973 | -0.032044 | 123.0789 | 121.3257 | 33.3527 | -0.11444 | 83.4549 | 83.3679 | 83.3496 | -39.9673 | 123.0148 | 122.9324 | 119.2612 | -35.0739
1851.5156 | 123.2117 | -79.5273 | 43.5516 | -0.0030518 | 0.01609 | 0.0020037 | 0.015599 | -0.019553 | 0.005753 | 0.0038345 | -0.019608 | 0.021516 | -0.0095768 | 0.018049 | -0.0018628 | 0.0087157 | 4.0237 | 4.0329 | 3.923 | 4.0192 | 4.1702 | 3.9093 | 3.7582 | 43.4418 | 42.7322 | 42.0044 | 43.5654 | 43.4784 | 8.7616 | 8.6517 | 83.4366 | 83.2855 | -39.3814 | 83.5602 | 83.5464 | 0.26093 | -39.5279 | 88.2889 | 88.179 | 0.013733 | 122.9691 | 121.5317 | 33.3527 | -0.073242 | 83.6975 | 83.551 | 83.4503 | -39.7934 | 123.0927 | 123.0057 | 122.2595 | -34.8999
1852.5156 | 123.2254 | -79.422 | 43.6523 | -0.20905 | 0.010322 | 0.0032855 | 0.012394 | -0.018271 | 0.00019875 | 0.0040481 | -0.16457 | 0.017457 | -0.012995 | 0.016981 | -0.0052808 | 0.011707 | 4.0009 | 4.0787 | 3.9642 | 4.0283 | 4.1336 | 3.9185 | 3.7399 | 43.5471 | 39.9628 | 42.1417 | 43.689 | 43.602 | 8.7708 | 8.67 | 83.3405 | 83.1619 | -39.5187 | 83.5007 | 83.4503 | 0.28839 | -39.6515 | 88.1927 | 88.092 | 0.036621 | 122.9691 | 121.5637 | 33.4717 | -0.050354 | 83.5556 | 83.4229 | 83.3862 | -39.9124 | 123.111 | 123.024 | 119.3848 | -34.9823
1853.5156 | 123.1796 | -79.5044 | 43.5883 | -0.13275 | 0.011818 | 0.0013629 | 0.015172 | -0.019126 | 0.00062595 | 0.0014847 | -0.17983 | 0.018525 | -0.011499 | 0.015058 | -0.0054944 | 0.0099975 | 3.9825 | 4.0421 | 3.923 | 4.0237 | 4.1931 | 3.9322 | 3.7628 | 43.5516 | 42.659 | 41.2628 | 43.6249 | 43.5425 | 8.7708 | 8.6609 | 83.4366 | 83.2672 | -39.3951 | 83.5464 | 83.5281 | 0.26093 | -39.6057 | 88.2751 | 88.1653 | 0.036621 | 123.056 | 120.7672 | 32.6019 | -0.045777 | 83.6975 | 83.4869 | 83.4274 | -39.8254 | 123.1293 | 123.0469 | 122.1634 | -34.9274
1854.5156 | 123.3261 | -79.4403 | 43.6066 | 0.035095 | 0.0077587 | 0.0024311 | 0.011967 | -0.019553 | -0.0047146 | 0.0042619 | 0.041427 | 0.017671 | -0.01214 | 0.014631 | -0.0031446 | 0.012561 | 3.978 | 4.0833 | 3.9688 | 4.0329 | 4.1061 | 3.9276 | 3.7491 | 42.9932 | 42.9337 | 41.1713 | 43.6066 | 43.5196 | 8.7662 | 8.6655 | 83.3679 | 83.1894 | -39.5004 | 83.5236 | 83.4732 | 0.28381 | -39.6286 | 88.2065 | 88.1058 | 0 | 122.4335 | 120.6116 | 32.5058 | -0.086975 | 83.5464 | 83.4183 | 83.4091 | -39.8575 | 123.0469 | 122.9599 | 122.374 | -34.9411
1855.5156 | 123.2071 | -79.5227 | 43.6203 | -0.20142 | 0.011818 | 0.0034991 | 0.012394 | -0.01998 | 0.0044712 | 0.00084388 | -0.20271 | 0.018525 | -0.013636 | 0.015272 | -0.003999 | 0.010211 | 4.0054 | 4.0604 | 3.9597 | 4.0375 | 4.1931 | 3.9459 | 3.7765 | 43.4006 | 40.0543 | 42.4438 | 43.6066 | 43.5059 | 8.7753 | 8.6472 | 83.4686 | 83.2993 | -39.4272 | 83.5831 | 83.5602 | 0.26093 | -39.6149 | 88.298 | 88.1699 | -0.013733 | 122.9233 | 121.9666 | 33.7967 | -0.11444 | 83.7158 | 83.5281 | 83.4824 | -39.8438 | 123.1293 | 123.0286 | 119.577 | -34.9731
1856.5156 | 123.2346 | -79.4907 | 43.5654 | -0.17853 | 0.014168 | 0.0028583 | 0.013676 | -0.019766 | 0.0036166 | 0.0029801 | -0.17983 | 0.019166 | -0.010004 | 0.017622 | -0.0035718 | 0.0080749 | 3.9963 | 4.0192 | 3.9185 | 4.0192 | 4.1977 | 3.923 | 3.7582 | 43.4601 | 39.9719 | 42.5308 | 43.602 | 43.4875 | 8.7662 | 8.6655 | 83.4137 | 83.2489 | -39.3677 | 83.5098 | 83.5098 | 0.26093 | -39.5691 | 88.2568 | 88.1561 | 0.036621 | 122.9507 | 122.0215 | 33.8654 | -0.07782 | 83.6884 | 83.4869 | 83.4091 | -39.8071 | 123.0927 | 122.9782 | 119.4626 | -34.8999
1857.5156 | 123.1979 | -79.6234 | 43.5059 | -0.1709 | 0.010322 | 0.00029489 | 0.014317 | -0.018485 | 0.00083955 | -0.0027877 | -0.33241 | 0.018739 | -0.011072 | 0.019117 | -0.0025036 | 0.011493 | 4.3076 | 4.0466 | 3.8406 | 3.9001 | 4.2343 | 3.9413 | 3.7537 | 43.396 | 39.8758 | 42.7139 | 43.515 | 43.4052 | 8.7616 | 8.6609 | 83.5648 | 83.3771 | -39.2715 | 83.67 | 83.5236 | 0.14648 | -39.1983 | 88.385 | 88.2843 | 0.009156 | 123.0194 | 122.3373 | 34.053 | -0.10071 | 83.8577 | 83.931 | 83.4641 | -39.7522 | 123.1384 | 123.0286 | 119.4992 | -34.845
1858.5156 | 123.3078 | -79.5319 | 43.5059 | -0.079346 | 0.0092541 | 0.0045673 | 0.013463 | -0.019126 | -0.0023648 | 0.0040481 | -0.080643 | 0.016603 | -0.015772 | 0.016126 | -0.0029308 | 0.011279 | 4.0009 | 4.1199 | 4.0054 | 4.0558 | 4.1061 | 3.9276 | 3.7765 | 43.4372 | 40.0635 | 42.8238 | 43.5104 | 43.428 | 8.7662 | 8.6655 | 83.4595 | 83.3084 | -39.3997 | 83.6517 | 83.5876 | 0.27924 | -39.505 | 88.298 | 88.1973 | 0.004578 | 122.9691 | 122.3557 | 34.1583 | -0.077819 | 83.638 | 83.5327 | 83.5373 | -39.7293 | 123.0423 | 122.9599 | 119.5953 | -34.8404
1859.5156 | 123.2117 | -79.541 | 43.5516 | -0.15564 | 0.013527 | 0.0030719 | 0.014317 | -0.019126 | 0.004044 | 0.0025529 | -0.21034 | 0.01938 | -0.011713 | 0.017195 | -0.0035718 | 0.010211 | 3.9276 | 3.9917 | 3.8727 | 3.9642 | 4.1656 | 3.8864 | 3.6987 | 43.2587 | 39.8026 | 42.2974 | 43.5791 | 43.4921 | 8.7662 | 8.6655 | 83.4274 | 83.2397 | -39.386 | 83.5327 | 83.5052 | 0.2655 | -39.624 | 88.3072 | 88.2065 | 0.027466 | 122.7997 | 121.8384 | 33.6319 | -0.05951 | 83.7067 | 83.4686 | 83.4137 | -39.8529 | 123.1201 | 123.0331 | 119.3436 | -34.8862
1860.5156 | 123.262 | -79.6234 | 43.4555 | -0.16327 | 0.010322 | 0.0045673 | 0.013676 | -0.018057 | -0.0023648 | 0.0021255 | -0.12642 | 0.019593 | -0.012995 | 0.01634 | -0.0063488 | 0.011707 | 4.0192 | 4.1061 | 3.978 | 4.0466 | 4.1336 | 3.9368 | 3.7811 | 43.222 | 41.7389 | 42.1188 | 43.4372 | 43.3456 | 8.757 | 8.67 | 83.5602 | 83.4045 | -39.3219 | 83.7296 | 83.67 | 0.2655 | -39.4363 | 88.3804 | 88.2935 | -0.01831 | 122.8455 | 121.7422 | 33.4488 | -0.10986 | 83.757 | 83.6426 | 83.6014 | -39.6744 | 123.0606 | 122.9691 | 121.3623 | -34.7855
1861.5156 | 123.2529 | -79.7287 | 43.3777 | -0.13275 | 0.015236 | 0.0022175 | 0.015812 | -0.018485 | 0.0042576 | 0.0042619 | -0.17983 | 0.020021 | -0.011286 | 0.015913 | -0.0033582 | 0.0097839 | 3.9734 | 4.01 | 3.9093 | 4.0146 | 4.1473 | 3.9093 | 3.7308 | 43.1534 | 41.3773 | 42.4713 | 43.3823 | 43.2953 | 8.7662 | 8.6609 | 83.638 | 83.4595 | -39.2303 | 83.7387 | 83.7433 | 0.28381 | -39.4043 | 88.4949 | 88.3896 | 0.004577 | 122.8821 | 122.2 | 33.8104 | -0.082398 | 83.876 | 83.7021 | 83.638 | -39.6469 | 123.111 | 123.024 | 121.106 | -34.7168
1862.5156 | 123.3398 | -79.541 | 43.4921 | -0.071716 | 0.0051953 | 0.0032855 | 0.010472 | -0.019339 | -0.0030056 | 0.0019119 | 0.0032804 | 0.019593 | -0.01449 | 0.013563 | -0.0035718 | 0.011493 | 4.0375 | 4.1382 | 4.0283 | 4.0833 | 4.1565 | 3.9505 | 3.7949 | 43.3228 | 41.2262 | 42.1555 | 43.515 | 43.4006 | 8.7662 | 8.6609 | 83.4915 | 83.3359 | -39.3356 | 83.6792 | 83.6243 | 0.28839 | -39.4547 | 88.3072 | 88.2019 | 0.022889 | 122.8638 | 121.6965 | 33.4946 | -0.091552 | 83.6975 | 83.5785 | 83.5693 | -39.6973 | 123.056 | 122.9416 | 120.7672 | -34.8312
1863.5156 | 123.2254 | -79.6829 | 43.4189 | -0.15564 | 0.013527 | 0.0030719 | 0.013676 | -0.021262 | 0.0053256 | 0.0021255 | -0.1722 | 0.020234 | -0.011499 | 0.015058 | -0.0033582 | 0.010211 | 4.0146 | 4.0466 | 3.9276 | 4.0375 | 4.1977 | 3.9505 | 3.7628 | 43.1351 | 40.9149 | 42.4118 | 43.4509 | 43.3365 | 8.7616 | 8.67 | 83.6334 | 83.4457 | -39.2212 | 83.7296 | 83.7204 | 0.27466 | -39.4043 | 88.4445 | 88.353 | 0.032044 | 122.818 | 122.0947 | 33.7418 | -0.082397 | 83.8806 | 83.6975 | 83.6105 | -39.6561 | 123.1338 | 123.0194 | 120.5978 | -34.7488
1864.5156 | 123.2437 | -79.4449 | 43.6569 | -0.20142 | 0.01075 | 0.0028583 | 0.011754 | -0.018485 | -0.00022865 | 0.0012711 | -0.14931 | 0.020021 | -0.010858 | 0.01634 | -0.0042126 | 0.0093567 | 3.9688 | 4.0741 | 3.9368 | 4.0192 | 4.1245 | 3.9093 | 3.7445 | 43.1717 | 41.0522 | 41.066 | 43.634 | 43.5425 | 8.7662 | 8.67 | 83.3542 | 83.1894 | -39.5325 | 83.519 | 83.4641 | 0.27466 | -39.6881 | 88.2111 | 88.1149 | -0.022888 | 122.6166 | 120.5109 | 32.3959 | -0.11444 | 83.5693 | 83.4137 | 83.3817 | -39.9124 | 123.0789 | 122.9874 | 120.4971 | -34.9869
1865.5156 | 123.23 | -79.7333 | 43.3594 | -0.15564 | 0.012459 | 0.0026447 | 0.012608 | -0.021262 | 0.00083955 | 0.0034073 | -0.14931 | 0.021089 | -0.011286 | 0.017195 | -0.00229 | 0.012347 | 4.0283 | 4.0604 | 3.9413 | 4.0329 | 4.2297 | 3.9551 | 3.7903 | 43.1534 | 39.9536 | 42.9932 | 43.4097 | 43.309 | 8.7662 | 8.6655 | 83.6884 | 83.5236 | -39.1296 | 83.7936 | 83.7662 | 0.24262 | -39.3311 | 88.4994 | 88.3987 | 0.050354 | 122.8867 | 122.7264 | 34.3277 | -0.050354 | 83.963 | 83.7616 | 83.6746 | -39.5691 | 123.143 | 123.0423 | 119.6869 | -34.6939
1866.5156 | 123.175 | -79.7287 | 43.3548 | -0.20905 | 0.012672 | 0.0037127 | 0.0096174 | -0.017844 | -0.0023648 | 0.0012711 | -0.16457 | 0.018953 | -0.011927 | 0.017622 | -0.0050672 | 0.011493 | 4.0146 | 4.129 | 3.9825 | 4.0695 | 4.2389 | 3.978 | 3.8315 | 43.0984 | 39.8621 | 43.1122 | 43.3502 | 43.2358 | 8.7662 | 8.6517 | 83.7067 | 83.5602 | -39.1159 | 83.8577 | 83.7982 | 0.23804 | -39.3402 | 88.4949 | 88.3804 | -0.004577 | 122.8271 | 122.8409 | 34.4605 | -0.11902 | 83.9676 | 83.7433 | 83.7112 | -39.5233 | 123.0789 | 122.9645 | 119.5908 | -34.7031
1867.5156 | 123.3215 | -79.7653 | 43.2816 | -0.14038 | 0.0079723 | 0.0039263 | 0.013463 | -0.018271 | -0.002792 | 0.0031937 | -0.10353 | 0.017671 | -0.011927 | 0.014417 | -0.0050672 | 0.012561 | 3.7994 | 4.2526 | 4.1473 | 4.0741 | 4.1931 | 3.9917 | 3.8132 | 43.277 | 40.0223 | 43.2587 | 43.2816 | 43.1808 | 8.7662 | 8.67 | 83.757 | 83.5785 | -39.0884 | 84.0179 | 83.8394 | 0.26093 | -39.4821 | 88.5315 | 88.4354 | 0 | 123.0423 | 123.024 | 34.5886 | -0.10071 | 83.9584 | 83.5648 | 83.9127 | -39.4684 | 123.0469 | 122.9462 | 119.7876 | -34.6115
1868.5156 | 123.3444 | -79.747 | 43.3044 | -0.10223 | 0.0086133 | 0.0024311 | 0.011113 | -0.019553 | -0.0012966 | 0.0016983 | 0.78911 | 0.017457 | -0.013208 | 0.017408 | -0.0046398 | 0.011493 | 4.0787 | 4.3762 | 4.2435 | 4.1656 | 4.1565 | 3.9551 | 3.7857 | 43.3594 | 40.1093 | 43.2999 | 43.2953 | 43.19 | 8.7616 | 8.6609 | 83.7021 | 83.5327 | -39.1479 | 84.1232 | 83.9127 | 0.37994 | -39.2258 | 88.5086 | 88.4079 | -0.009155 | 123.1064 | 123.0469 | 34.639 | -0.11444 | 83.9035 | 83.8257 | 83.9905 | -39.5187 | 123.0423 | 122.937 | 119.8563 | -34.6436
1869.5156 | 123.1979 | -79.7745 | 43.3365 | -0.18616 | 0.012245 | 0.0017901 | 0.017308 | -0.017844 | 0.0025486 | 0.0049027 | -0.065384 | 0.018525 | -0.013636 | 0.014631 | -0.00079463 | 0.010211 | 3.8544 | 4.0558 | 3.9871 | 4.0375 | 4.2938 | 3.9871 | 3.8086 | 43.2312 | 39.9902 | 43.1351 | 43.3594 | 43.2632 | 8.7708 | 8.6609 | 83.7616 | 83.5831 | -39.0427 | 83.8303 | 83.812 | 0.22888 | -39.4821 | 88.5452 | 88.4354 | 0.022888 | 123.0057 | 122.9095 | 34.4742 | -0.073242 | 84.0683 | 83.6288 | 83.7616 | -39.5279 | 123.1338 | 123.0377 | 119.7647 | -34.6756
1870.5156 | 123.349 | -79.7653 | 43.2724 | -0.041199 | 0.0075451 | 0.0056353 | 0.014958 | -0.017844 | -0.0040738 | 0.0034073 | -0.088272 | 0.017244 | -0.01684 | 0.018263 | -0.0018628 | 0.011707 | 4.0649 | 4.1794 | 4.0421 | 4.0741 | 4.1428 | 3.9505 | 3.7674 | 43.3182 | 40.1367 | 43.2175 | 43.2541 | 43.1763 | 8.7753 | 8.6655 | 83.7158 | 83.5327 | -39.1296 | 83.9447 | 83.8394 | 0.3067 | -39.2075 | 88.5406 | 88.4308 | -0.018311 | 123.0835 | 122.9828 | 34.552 | -0.09613 | 83.9081 | 83.8303 | 83.8074 | -39.505 | 123.0194 | 122.9416 | 119.902 | -34.6069
1871.5156 | 123.2483 | -79.9622 | 43.1351 | -0.16327 | 0.015663 | 0.0015765 | 0.013676 | -0.018912 | 0.0048984 | 0.0034073 | -0.18745 | 0.01938 | -0.011072 | 0.015272 | -0.0037854 | 0.0082885 | 4.0054 | 4.0375 | 3.9413 | 4.0421 | 4.184 | 3.9185 | 3.7354 | 43.0801 | 41.8716 | 43.071 | 43.1808 | 43.071 | 8.7662 | 8.6655 | 83.8806 | 83.6975 | -38.9511 | 83.9996 | 84.0042 | 0.3067 | -39.1296 | 88.7283 | 88.6276 | 0.045776 | 123.0423 | 123.0331 | 34.4055 | -0.064087 | 84.1461 | 83.9676 | 83.9035 | -39.3997 | 123.143 | 123.0331 | 121.8338 | -34.4696
1872.5156 | 123.2483 | -79.8569 | 43.2266 | -0.1709 | 0.0098951 | 0.0011493 | 0.011326 | -0.019339 | -0.0015102 | 0.0036209 | -0.1722 | 0.017884 | -0.0095768 | 0.015699 | -0.0063488 | 0.012347 | 4.0466 | 4.1153 | 4.0054 | 4.0741 | 4.1519 | 3.9597 | 3.7765 | 43.1488 | 40.004 | 43.1717 | 43.2266 | 43.1488 | 8.757 | 8.6609 | 83.8165 | 83.6334 | -39.0747 | 83.9722 | 83.931 | 0.29755 | -39.18 | 88.6139 | 88.5178 | 0 | 123.0057 | 123.0286 | 34.5108 | -0.07782 | 84.0088 | 83.9035 | 83.8623 | -39.4501 | 123.0835 | 123.0057 | 119.8608 | -34.5657
1873.5156 | 123.2254 | -79.8157 | 43.2724 | -0.1709 | 0.012672 | 0.0026447 | 0.014958 | -0.018698 | 0.0029758 | 0.0044755 | -0.16457 | 0.020448 | -0.010431 | 0.01634 | -0.0027172 | 0.0099975 | 3.9551 | 4.0146 | 3.9047 | 3.9963 | 4.1885 | 3.9139 | 3.7537 | 43.1488 | 39.9307 | 43.1168 | 43.3136 | 43.1992 | 8.7708 | 8.6655 | 83.7296 | 83.5693 | -39.0839 | 83.8303 | 83.812 | 0.24262 | -39.3173 | 88.5864 | 88.4811 | 0.041199 | 122.9645 | 122.9324 | 34.4513 | -0.073242 | 84.0042 | 83.7708 | 83.7204 | -39.5187 | 123.1293 | 123.0148 | 119.7464 | -34.6069
1874.5156 | 123.3536 | -79.8019 | 43.2816 | -0.064087 | 0.010536 | 0.0024311 | 0.012608 | -0.019553 | -0.0017238 | 0.0042619 | 0.041427 | 0.017244 | -0.013849 | 0.015272 | -0.0063488 | 0.012775 | 4.0329 | 4.1656 | 4.0421 | 4.0833 | 4.1382 | 3.9597 | 3.7857 | 43.2816 | 40.0772 | 43.2404 | 43.222 | 43.1625 | 8.7662 | 8.6746 | 83.7616 | 83.5876 | -39.1434 | 83.9676 | 83.8852 | 0.29755 | -39.2487 | 88.5681 | 88.4766 | -0.059509 | 123.0835 | 123.0423 | 34.5657 | -0.11902 | 83.9401 | 83.8348 | 83.844 | -39.4958 | 123.024 | 122.9645 | 119.8792 | -34.6069
1875.5156 | 123.3398 | -79.8523 | 43.1992 | 2.919 | 0.011818 | 0.0032855 | 0.013249 | -0.020621 | -0.00065585 | 0.0029801 | -0.11116 | 0.017884 | -0.01449 | 0.016554 | -0.0059216 | 0.010425 | 4.0741 | 4.1153 | 4.01 | 4.0787 | 4.1107 | 3.923 | 3.7811 | 43.1992 | 40.0452 | 43.2495 | 43.1625 | 43.0984 | 8.7708 | 8.6609 | 83.7753 | 83.6334 | -39.0884 | 83.9676 | 83.931 | 0.29755 | -39.1251 | 88.623 | 88.5132 | -0.036621 | 123.0515 | 123.1018 | 34.5886 | -0.10071 | 83.963 | 83.9264 | 83.8623 | -39.418 | 123.0148 | 122.9507 | 119.8975 | -34.5383
1876.5156 | 123.262 | -79.8981 | 43.1808 | -0.12512 | 0.015877 | 0.0020037 | 0.014317 | -0.018271 | 0.004044 | 0.0036209 | -0.21797 | 0.020448 | -0.0085086 | 0.017408 | -0.0027172 | 0.0095703 | 3.9597 | 3.9871 | 3.8864 | 3.9871 | 4.1611 | 3.9001 | 3.717 | 43.1122 | 39.9902 | 43.1259 | 43.2266 | 43.1213 | 8.7753 | 8.6655 | 83.7982 | 83.6151 | -39.0198 | 83.8852 | 83.8852 | 0.27008 | -39.2212 | 88.6734 | 88.5635 | 0.045777 | 123.0103 | 123.024 | 34.4604 | -0.059509 | 84.0591 | 83.8577 | 83.7845 | -39.4638 | 123.1247 | 123.0194 | 119.8883 | -34.5154
1877.5156 | 123.2162 | -79.9347 | 43.1992 | -0.1709 | 0.010322 | 0.0013629 | 0.012822 | -0.019126 | -0.0015102 | 0.0031937 | -0.20271 | 0.019593 | -0.011286 | 0.01869 | -0.003999 | 0.012561 | 3.9505 | 4.0146 | 3.8864 | 3.9825 | 4.1199 | 3.8589 | 3.7125 | 43.1259 | 39.9628 | 43.1122 | 43.2266 | 43.1396 | 8.7708 | 8.6655 | 83.7936 | 83.6472 | -39.0793 | 83.9493 | 83.9172 | 0.27008 | -39.2487 | 88.7054 | 88.6002 | 0.027466 | 123.0606 | 123.0469 | 34.4467 | -0.05951 | 84.0546 | 83.8852 | 83.8211 | -39.4867 | 123.1613 | 123.0743 | 119.8975 | -34.5337
1878.5156 | 123.3032 | -79.9026 | 43.158 | -0.15564 | 0.0077587 | 0.0022175 | 0.013463 | -0.016135 | -0.0015102 | 0.0027665 | -0.15694 | 0.017671 | -0.011499 | 0.015486 | -0.0033582 | 0.010425 | 4.0054 | 4.1199 | 3.9963 | 4.0421 | 4.1199 | 3.923 | 3.7628 | 43.1717 | 39.9902 | 43.1992 | 43.1625 | 43.0893 | 8.7662 | 8.67 | 83.8257 | 83.6655 | -39.0381 | 84.0225 | 83.9447 | 0.27924 | -39.1525 | 88.6688 | 88.5727 | 0.004578 | 123.0743 | 123.1018 | 34.5291 | -0.068665 | 84.0225 | 83.9081 | 83.8989 | -39.3951 | 123.0652 | 122.9919 | 119.8929 | -34.4879
1879.5156 | 123.1842 | -79.9622 | 43.1442 | 0.065613 | 0.016517 | 0.0011493 | 0.015385 | -0.018485 | 0.0046848 | 0.0044755 | -0.019608 | 0.021089 | -0.0095768 | 0.017622 | -0.0010082 | 0.0093567 | 3.9139 | 3.8818 | 3.8177 | 3.9185 | 4.1016 | 3.8498 | 3.6896 | 43.0618 | 39.7797 | 42.746 | 43.1076 | 43.0023 | 8.7708 | 8.6655 | 83.8119 | 83.6517 | -39.0427 | 83.844 | 83.8806 | 0.22888 | -39.2303 | 88.7329 | 88.6276 | -0.036621 | 123.024 | 122.7081 | 34.0805 | -0.14191 | 84.0637 | 83.876 | 83.7799 | -39.4547 | 123.0698 | 122.9645 | 119.7418 | -34.4788
1880.5156 | 123.3032 | -79.9164 | 43.1534 | -0.13275 | 0.0090405 | 0.0026447 | 0.013249 | -0.01763 | -0.0049282 | 0.0010575 | -0.10353 | 0.017671 | -0.012995 | 0.014845 | -0.0059216 | 0.012775 | 3.9825 | 4.0604 | 3.9597 | 4.0146 | 4.0649 | 3.8864 | 3.7262 | 43.1854 | 39.9628 | 43.1625 | 43.1625 | 43.0984 | 8.7708 | 8.6609 | 83.8028 | 83.6426 | -39.0884 | 83.9767 | 83.931 | 0.28839 | -39.1708 | 88.6871 | 88.5773 | 0.009156 | 123.1018 | 123.0789 | 34.5016 | -0.054931 | 83.9813 | 83.8989 | 83.876 | -39.4272 | 123.0789 | 123.0148 | 119.8792 | -34.4925
1881.5156 | 123.2162 | -79.953 | 43.1717 | -0.14801 | 0.012886 | 0.0026447 | 0.014531 | -0.017844 | 0.004044 | 0.0021255 | -0.485 | 0.019593 | -0.011713 | 0.015913 | -0.0042126 | 0.012775 | 3.9001 | 3.9597 | 3.8223 | 4.2252 | 4.1519 | 3.8544 | 3.6942 | 43.1076 | 39.8621 | 43.0939 | 43.2083 | 43.1076 | 8.7662 | 8.67 | 83.8074 | 83.6472 | -39.0198 | 83.9127 | 84.1782 | 0.53101 | -39.2715 | 88.7192 | 88.623 | 0.036621 | 123.0606 | 123.0469 | 34.4238 | -0.064087 | 84.1049 | 83.8531 | 83.7753 | -39.4775 | 123.1613 | 123.0606 | 119.8151 | -34.5016
1882.5156 | 123.3398 | -79.9667 | 43.071 | -0.11749 | 0.0069043 | 0.0039263 | 0.012822 | -0.01998 | -0.0036464 | 0.0019119 | -0.065384 | 0.01703 | -0.013636 | 0.01634 | -0.0031446 | 0.012988 | 4.0009 | 4.1245 | 3.9917 | 4.0466 | 4.097 | 3.923 | 3.7308 | 43.1808 | 40.2328 | 43.3594 | 43.1488 | 43.0527 | 8.7753 | 8.6655 | 83.8898 | 83.6975 | -38.974 | 84.0912 | 84.0134 | 0.31586 | -39.0701 | 88.7421 | 88.6322 | 0.07782 | 123.1476 | 123.3261 | 34.6939 | -0.018311 | 84.0637 | 83.9676 | 83.9584 | -39.3402 | 123.1155 | 123.0194 | 120.1996 | -34.4055
1883.5156 | 123.262 | -80.0262 | 43.0939 | -0.13275 | 0.015449 | 8.1086e-05 | 0.018376 | -0.017844 | 0.0042576 | 0.0059707 | -0.21034 | 0.018312 | -0.0095768 | 0.014417 | -0.0016492 | 0.0087157 | 3.9276 | 3.9322 | 3.8406 | 3.9459 | 4.0741 | 3.8223 | 3.6758 | 43.0618 | 39.8026 | 43.071 | 43.1076 | 42.9977 | 8.7708 | 8.6655 | 83.8486 | 83.7021 | -39.0198 | 83.9584 | 83.9722 | 0.27008 | -39.1663 | 88.797 | 88.6917 | 0.013733 | 123.0881 | 123.0972 | 34.4055 | -0.09613 | 84.1003 | 83.9539 | 83.8669 | -39.418 | 123.1338 | 123.024 | 119.8288 | -34.4284
1884.5312 | 123.349 | -79.9805 | 43.071 | -0.56763 | 0.010963 | 0.0022175 | 0.01154 | -0.016989 | -0.001083 | 0.0016983 | 0.20927 | 0.018953 | -0.014276 | 0.015913 | -0.0029308 | 0.010638 | 3.9047 | 4.0009 | 3.891 | 3.9185 | 4.0009 | 3.8086 | 3.6392 | 43.1396 | 39.9124 | 43.1396 | 43.0664 | 42.9794 | 8.7753 | 8.67 | 83.7891 | 83.6197 | -39.0701 | 83.9813 | 83.8989 | 0.27924 | -39.1663 | 88.7558 | 88.6505 | -0.004578 | 123.1201 | 123.1201 | 34.4696 | -0.091553 | 83.9813 | 83.8852 | 83.8715 | -39.4318 | 123.0469 | 122.9599 | 119.8929 | -34.4009
1885.5156 | 123.2346 | -80.0125 | 43.0984 | -0.16327 | 0.01075 | 0.0030719 | 0.015172 | -0.020194 | -1.505e-05 | 0.0025529 | -0.18745 | 0.020448 | -0.014704 | 0.015486 | -0.0031446 | 0.012347 | 3.8727 | 3.9322 | 3.8177 | 3.9139 | 4.0787 | 3.8269 | 3.6621 | 43.0298 | 39.798 | 43.2266 | 43.1534 | 43.0756 | 8.7753 | 8.6655 | 83.8394 | 83.6746 | -39.0198 | 83.9447 | 83.9264 | 0.25177 | -39.2258 | 88.7878 | 88.678 | 0.054931 | 123.0423 | 123.2391 | 34.5612 | -0.022888 | 84.0912 | 83.8852 | 83.8303 | -39.4363 | 123.1659 | 123.0881 | 119.8105 | -34.433
1886.5156 | 123.1567 | -80.0629 | 43.0618 | -0.1709 | 0.010322 | 0.0022175 | 0.013249 | -0.019339 | 0.00041235 | 0.0042619 | -0.17983 | 0.018098 | -0.01214 | 0.015486 | -0.0031446 | 0.010211 | 3.8498 | 3.8956 | 3.772 | 3.8635 | 4.0558 | 3.7949 | 3.6255 | 42.9977 | 39.7522 | 42.9977 | 43.0847 | 42.984 | 8.7708 | 8.6609 | 83.8577 | 83.6884 | -39.006 | 83.9584 | 83.9264 | 0.23804 | -39.212 | 88.8336 | 88.7238 | 0.022888 | 123.0606 | 123.0606 | 34.3369 | -0.07782 | 84.1187 | 83.9127 | 83.8348 | -39.4363 | 123.1476 | 123.0469 | 119.8151 | -34.4009
1887.5156 | 123.2346 | -80.1819 | 42.9611 | -0.18616 | 0.010109 | 0.0030719 | 0.010258 | -0.018698 | -0.0012966 | 0.00041648 | -0.16457 | 0.019166 | -0.010431 | 0.015913 | -0.0037854 | 0.013202 | 3.8498 | 3.9001 | 3.804 | 3.8956 | 4.0421 | 3.7994 | 3.6301 | 42.8925 | 42.8879 | 42.9153 | 42.984 | 42.8879 | 8.7662 | 8.6655 | 83.9813 | 83.812 | -38.9191 | 84.082 | 84.0775 | 0.2655 | -39.1113 | 88.9481 | 88.8474 | 0.022888 | 123.0743 | 123.0972 | 34.2499 | -0.073243 | 84.2239 | 84.0317 | 83.9859 | -39.3311 | 123.1659 | 123.0698 | 123.0698 | -34.2957
1888.5156 | 123.3444 | -79.9576 | 43.0893 | -0.14038 | 0.0088269 | 0.0013629 | 0.012394 | -0.022116 | -0.0023648 | -0.0010787 | -0.38582 | 0.019593 | -0.014063 | 0.01399 | -0.0044262 | 0.011707 | 4.1977 | 3.7811 | 3.6301 | 3.7857 | 3.9825 | 3.8086 | 3.6301 | 43.1534 | 40.0452 | 43.1854 | 43.0801 | 42.9932 | 8.7662 | 8.6655 | 83.7662 | 83.5876 | -39.1068 | 83.7387 | 83.7433 | 0.15564 | -38.8916 | 88.7238 | 88.623 | -0.009155 | 123.111 | 123.143 | 34.52 | -0.09613 | 83.9401 | 84.1553 | 83.5876 | -39.4592 | 123.0377 | 122.9507 | 120.0027 | -34.4238
1889.5312 | 123.3124 | -80.1407 | 42.9291 | 0.25635 | 0.015022 | 0.0013629 | 0.012181 | -0.015708 | 0.001694 | 0.0042619 | 0.17113 | 0.018525 | -0.0087222 | 0.016981 | -0.0018628 | 0.012347 | 3.8177 | 3.8452 | 3.7399 | 3.8269 | 3.9734 | 3.7354 | 3.5797 | 42.9565 | 42.9428 | 42.9245 | 42.9474 | 42.8375 | 8.7753 | 8.6609 | 83.876 | 83.7204 | -38.9557 | 83.9859 | 83.9676 | 0.24719 | -39.1113 | 88.916 | 88.8016 | 0.018311 | 123.0972 | 123.0652 | 34.2636 | -0.091553 | 84.1141 | 83.9584 | 83.8806 | -39.3494 | 123.0881 | 122.9782 | 123.0835 | -34.2682
1890.5156 | 123.3261 | -80.1178 | 42.952 | -0.10223 | 0.0075451 | 0.0034991 | 0.012608 | -0.020835 | -0.001083 | 0.0029801 | -0.11879 | 0.018525 | -0.013636 | 0.015913 | -0.0050672 | 0.01192 | 3.8544 | 3.9368 | 3.8269 | 3.8818 | 3.9322 | 3.7491 | 3.598 | 42.984 | 43.0527 | 42.9932 | 42.9565 | 42.8879 | 8.7662 | 8.6655 | 83.8669 | 83.7158 | -39.0198 | 84.0546 | 83.9996 | 0.28381 | -39.0976 | 88.884 | 88.7833 | 0.004578 | 123.1018 | 123.111 | 34.3277 | -0.064087 | 84.05 | 83.9722 | 83.9447 | -39.3539 | 123.0743 | 123.0057 | 123.1705 | -34.2865
1891.5156 | 123.2117 | -80.2139 | 42.9153 | 0.073242 | 0.01609 | 0.0013629 | 0.012181 | -0.01998 | 0.004044 | 0.0051163 | -0.0043486 | 0.020021 | -0.0078678 | 0.013777 | -0.0012218 | 0.0093567 | 3.7949 | 3.7811 | 3.7125 | 3.7949 | 3.978 | 3.7399 | 3.5614 | 42.8375 | 42.9382 | 42.6773 | 42.9428 | 42.8421 | 8.7753 | 8.6655 | 83.9539 | 83.7753 | -38.9374 | 83.9951 | 84.0088 | 0.23346 | -39.1205 | 88.9893 | 88.8794 | 0.027466 | 123.0515 | 122.8912 | 34.0118 | -0.073242 | 84.1919 | 84.0088 | 83.9264 | -39.3539 | 123.1567 | 123.056 | 123.1522 | -34.2499
1892.5156 | 123.2666 | -80.1453 | 42.8879 | -0.18616 | 0.0086133 | 0.0045673 | 0.013676 | -0.018485 | -0.0032192 | 0.0044755 | -0.10353 | 0.018312 | -0.01449 | 0.016126 | -0.0050672 | 0.012134 | 3.8589 | 3.9368 | 3.8223 | 3.8956 | 3.9734 | 3.7857 | 3.6026 | 42.9199 | 42.4622 | 42.8513 | 42.9062 | 42.8604 | 8.7662 | 8.6655 | 83.931 | 83.7479 | -38.9145 | 84.082 | 84.0408 | 0.29297 | -39.0289 | 88.9114 | 88.8107 | 0.018311 | 123.0652 | 122.9965 | 34.1858 | -0.027465 | 84.1187 | 84.0042 | 83.9676 | -39.2853 | 123.0515 | 123.0057 | 122.6074 | -34.2224
1893.5156 | 123.2346 | -80.2505 | 42.8696 | -0.18616 | 0.01075 | 0.00072209 | 0.013249 | -0.016562 | -0.00065585 | 0.0021255 | -0.11116 | 0.020875 | -0.010858 | 0.015486 | -0.0054944 | 0.010211 | 3.804 | 3.8635 | 3.7445 | 3.8315 | 3.9963 | 3.7491 | 3.566 | 42.8238 | 42.7917 | 42.778 | 42.8741 | 42.7826 | 8.7708 | 8.6655 | 83.9996 | 83.8165 | -38.8733 | 84.1141 | 84.082 | 0.2655 | -39.0656 | 89.0213 | 88.916 | 0.004578 | 123.0743 | 123.0286 | 34.1125 | -0.086975 | 84.2468 | 84.0546 | 83.9951 | -39.3036 | 123.1247 | 123.0331 | 123.0423 | -34.2041
1894.5312 | 123.3124 | -80.1682 | 42.8741 | 0.19531 | 0.0073315 | 0.0022175 | 0.012181 | -0.018485 | -0.001083 | 0.0021255 | 0.23979 | 0.020021 | -0.012995 | 0.016981 | -0.0025036 | 0.01192 | 3.7857 | 3.8681 | 3.7537 | 3.8086 | 3.8956 | 3.7079 | 3.5614 | 42.9108 | 41.5558 | 42.8833 | 42.8741 | 42.8009 | 8.7616 | 8.6655 | 83.876 | 83.7296 | -38.9786 | 84.0363 | 83.9767 | 0.24719 | -39.0884 | 88.9297 | 88.8336 | 0 | 123.0789 | 123.0515 | 34.2178 | -0.073243 | 84.0637 | 83.9539 | 83.9218 | -39.3127 | 123.0423 | 122.9691 | 121.7239 | -34.2087
1895.5156 | 123.3261 | -80.159 | 42.9245 | 0.065613 | 0.0071179 | 0.0020037 | 0.01154 | -0.019339 | -0.0017238 | 0.0031937 | -0.11879 | 0.015748 | -0.011713 | 0.014631 | -0.0042126 | 0.010852 | 3.8315 | 3.9551 | 3.8223 | 3.8635 | 3.9368 | 3.7399 | 3.5706 | 42.9611 | 41.2445 | 42.9932 | 42.9245 | 42.8375 | 8.7662 | 8.67 | 83.8989 | 83.7296 | -38.9877 | 84.1141 | 84.0225 | 0.29297 | -39.093 | 88.9252 | 88.829 | 0 | 123.1201 | 123.1522 | 34.3231 | -0.086976 | 84.0958 | 83.9905 | 83.9813 | -39.3539 | 123.0835 | 122.9965 | 121.4035 | -34.2545
1896.5312 | 123.349 | -80.2643 | 42.8284 | -0.071716 | 0.0083997 | 0.0015765 | 0.012608 | -0.017844 | -0.0032192 | 0.00084388 | -0.11116 | 0.018525 | -0.015772 | 0.01399 | -0.0037854 | 0.010211 | 3.8818 | 3.9734 | 3.8452 | 3.891 | 3.9413 | 3.772 | 3.5889 | 42.8741 | 42.8558 | 42.8787 | 42.8101 | 42.7322 | 8.7662 | 8.6655 | 84.0363 | 83.8531 | -38.887 | 84.2377 | 84.1553 | 0.30212 | -38.9465 | 89.0305 | 88.9297 | -0.01831 | 123.1384 | 123.143 | 34.2133 | -0.09613 | 84.2056 | 84.1461 | 84.1095 | -39.2395 | 123.0743 | 122.9965 | 123.1201 | -34.1629
1897.5156 | 123.23 | -80.2231 | 42.8741 | -0.19379 | 0.0088269 | 0.0056353 | 0.015599 | -0.020194 | 0.0025486 | 0.0027665 | -0.11116 | 0.017244 | -0.010218 | 0.015272 | -0.00229 | 0.010211 | 3.8589 | 3.9001 | 3.772 | 3.8635 | 3.9917 | 3.7582 | 3.6118 | 42.8055 | 42.9565 | 42.5812 | 42.9153 | 42.8009 | 8.7753 | 8.67 | 83.9813 | 83.8348 | -38.8824 | 84.1232 | 84.0866 | 0.25177 | -39.0152 | 88.9984 | 88.8931 | 0.041198 | 123.0286 | 122.8043 | 33.9111 | -0.073243 | 84.2148 | 84.082 | 83.9951 | -39.2624 | 123.1384 | 123.024 | 123.1796 | -34.2041
1898.5156 | 123.3673 | -79.9301 | 43.1305 | -0.064087 | 0.0069043 | 0.0030719 | 0.010685 | -0.019126 | -0.00065585 | 0.0025529 | -0.019608 | 0.01703 | -0.011072 | 0.014631 | -0.0069898 | 0.01192 | 3.7262 | 3.8361 | 3.6942 | 3.7399 | 3.804 | 3.6209 | 3.4378 | 43.3044 | 42.8284 | 40.9744 | 43.1396 | 43.0252 | 8.7708 | 8.6655 | 83.551 | 83.3679 | -39.3265 | 83.7662 | 83.67 | 0.30212 | -39.4043 | 88.7009 | 88.5956 | 0.009155 | 123.2346 | 120.9045 | 32.309 | -0.10529 | 83.7341 | 83.6563 | 83.6243 | -39.6927 | 123.0698 | 122.9553 | 122.7585 | -34.465
1899.5156 | 123.2803 | -80.0217 | 43.103 | -0.1709 | 0.0094677 | 0.0026447 | 0.014531 | -0.01998 | -0.00044225 | 0.0029801 | -0.21034 | 0.019166 | -0.015772 | 0.016126 | -0.0050672 | 0.010211 | 3.6987 | 3.7857 | 3.6484 | 3.7125 | 3.8361 | 3.6163 | 3.447 | 43.0298 | 43.2312 | 40.9286 | 43.103 | 43.0023 | 8.7753 | 8.6655 | 83.638 | 83.4686 | -39.267 | 83.8074 | 83.7341 | 0.2655 | -39.4043 | 88.797 | 88.6871 | 0 | 123.0515 | 120.9503 | 32.2632 | -0.10071 | 83.8577 | 83.7204 | 83.67 | -39.6561 | 123.1247 | 123.024 | 123.2529 | -34.4376
1900.5156 | 123.3124 | -79.9896 | 43.0847 | -0.13275 | 0.0075451 | 0.0043537 | 0.012608 | -0.019553 | 0.00019875 | 0.0027665 | -0.15694 | 0.017884 | -0.01449 | 0.015699 | -0.0035718 | 0.010425 | 3.6987 | 3.7765 | 3.6667 | 3.7262 | 3.7811 | 3.6026 | 3.4378 | 43.0389 | 43.2449 | 40.9058 | 43.0756 | 42.9932 | 8.7799 | 8.6792 | 83.5922 | 83.4274 | -39.3036 | 83.7662 | 83.7158 | 0.28839 | -39.386 | 88.7695 | 88.6688 | -0.009155 | 123.0286 | 120.8954 | 32.2266 | -0.091553 | 83.7708 | 83.6884 | 83.6563 | -39.6469 | 123.0652 | 122.9828 | 123.2346 | -34.4055
1901.5156 | 123.2758 | -80.2826 | 42.8055 | 0.17242 | 0.014168 | 0.0020037 | 0.014744 | -0.019766 | 0.0036166 | 0.0036209 | 0.15587 | 0.021089 | -0.010004 | 0.014845 | -0.0014356 | 0.0089295 | 3.7079 | 3.6942 | 3.6026 | 3.6804 | 3.8727 | 3.6163 | 3.4424 | 42.746 | 42.8925 | 42.3065 | 42.8375 | 42.7643 | 8.7662 | 8.6655 | 83.8989 | 83.725 | -38.9328 | 83.9767 | 83.963 | 0.23804 | -39.0976 | 89.0488 | 88.9481 | 0.032043 | 123.0286 | 122.5891 | 33.6411 | -0.041199 | 84.1553 | 83.9905 | 83.8852 | -39.3631 | 123.1201 | 123.0469 | 123.175 | -34.14
1902.5156 | 123.317 | -80.2414 | 42.8238 | 0.75226 | 0.0058361 | 0.0017901 | 0.012181 | -0.018485 | -0.00086945 | 0.0014847 | 0.033798 | 0.017671 | -0.014917 | 0.014417 | -0.005708 | 0.013629 | 3.6713 | 3.7354 | 3.6484 | 3.7216 | 3.8132 | 3.6255 | 3.4607 | 42.7689 | 42.9657 | 42.0227 | 42.8329 | 42.7505 | 8.7753 | 8.67 | 83.8669 | 83.7021 | -39.0106 | 83.9767 | 83.963 | 0.26093 | -39.1525 | 89.0167 | 88.9114 | 0.009155 | 123.0103 | 122.2641 | 33.3527 | -0.073243 | 84.0546 | 83.9127 | 83.8898 | -39.3631 | 123.0743 | 122.9919 | 123.2071 | -34.1537
1903.5156 | 123.2071 | -80.2963 | 42.865 | -0.20142 | 0.012886 | 0.0039263 | 0.017949 | -0.015921 | 0.00083955 | 0.0046891 | -0.14931 | 0.020234 | -0.012354 | 0.014631 | -0.0027172 | 0.010852 | 3.7125 | 3.7262 | 3.6255 | 3.7308 | 3.8727 | 3.6346 | 3.4607 | 42.7185 | 42.9016 | 42.0181 | 42.8558 | 42.8009 | 8.7753 | 8.67 | 83.931 | 83.757 | -38.9923 | 84.0225 | 84.0271 | 0.27008 | -39.1525 | 89.0717 | 88.9664 | -0.009155 | 123.0148 | 122.3145 | 33.3481 | -0.064087 | 84.169 | 84.0088 | 83.9218 | -39.4043 | 123.1522 | 123.0972 | 123.1979 | -34.1949
1904.5156 | 123.3627 | -80.3192 | 42.7094 | -0.071716 | 0.0062635 | 0.0020037 | 0.010685 | -0.018485 | -0.0015102 | 0.0023391 | -1.3319 | 0.020662 | -0.011072 | 0.01399 | -0.0012218 | 0.01192 | 3.8132 | 3.891 | 3.7628 | 3.8086 | 3.8589 | 3.6621 | 3.5156 | 42.7002 | 42.8879 | 42.453 | 42.6865 | 42.6315 | 8.7662 | 8.67 | 83.9813 | 83.8348 | -38.8504 | 84.2102 | 84.1278 | 0.29297 | -38.8962 | 89.0854 | 88.9893 | -0.022889 | 123.0194 | 122.7722 | 33.783 | -0.07782 | 84.1782 | 84.1324 | 84.082 | -39.1937 | 123.0057 | 122.9507 | 123.2071 | -34.0393
1905.5156 | 123.349 | -80.3741 | 42.659 | -0.34637 | 0.0058361 | 0.0043537 | 0.013035 | -0.019126 | -0.00065585 | 0.0014847 | -0.11116 | 0.018953 | -0.014704 | 0.014845 | -0.0033582 | 0.011066 | 3.7765 | 3.8406 | 3.7354 | 3.7903 | 3.8498 | 3.6621 | 3.4653 | 42.7368 | 42.8879 | 42.7597 | 42.6773 | 42.5812 | 8.7753 | 8.6655 | 84.0363 | 83.8394 | -38.8092 | 84.2148 | 84.1644 | 0.32501 | -38.8824 | 89.1495 | 89.0396 | 0.01831 | 123.111 | 123.1339 | 34.0942 | -0.07782 | 84.2239 | 84.1507 | 84.1095 | -39.1937 | 123.0515 | 122.9553 | 123.262 | -33.9935
1906.5156 | 123.2895 | -80.365 | 42.7277 | -0.14038 | 0.0081861 | 0.0032855 | 0.013676 | -0.019553 | 0.00062595 | 0.0019119 | -0.16457 | 0.016176 | -0.013849 | 0.014845 | -0.0014356 | 0.011493 | 3.7445 | 3.8223 | 3.6987 | 3.7537 | 3.8223 | 3.6346 | 3.4698 | 42.7277 | 42.8879 | 42.7826 | 42.7414 | 42.6132 | 8.7662 | 8.6746 | 83.9996 | 83.8348 | -38.9053 | 84.1873 | 84.1187 | 0.28381 | -38.9832 | 89.1312 | 89.0396 | 0.013733 | 123.0927 | 123.1476 | 34.108 | -0.11444 | 84.1873 | 84.1095 | 84.0637 | -39.2578 | 123.1064 | 122.9782 | 123.2529 | -34.053
1907.5156 | 123.3536 | -80.365 | 42.6956 | -0.086975 | 0.0083997 | 0.0037127 | 0.013035 | -0.018271 | -0.00065585 | 0.0023391 | -3.4147 | 0.01468 | -0.013636 | 0.017835 | -0.0010082 | 0.011707 | 3.7537 | 3.8406 | 3.6942 | 3.7491 | 3.7949 | 3.6163 | 3.4607 | 42.778 | 42.8238 | 42.5674 | 42.691 | 42.5949 | 8.7708 | 8.6655 | 83.9813 | 83.8257 | -38.9008 | 84.2056 | 84.1141 | 0.28839 | -38.942 | 89.1357 | 89.0305 | -0.004578 | 123.143 | 122.9324 | 33.902 | -0.10071 | 84.1599 | 84.1187 | 84.0591 | -39.2349 | 123.056 | 122.9599 | 123.1888 | -34.0302
1908.5156 | 123.4222 | -80.3421 | 42.6636 | -0.079346 | 0.0054089 | 0.0041401 | 0.011754 | -0.019766 | -0.001083 | 0.0014847 | -0.17983 | 0.018098 | -0.014276 | 0.013777 | -0.0031446 | 0.011066 | 3.7354 | 3.8315 | 3.6987 | 3.7308 | 3.7994 | 3.6392 | 3.4698 | 42.7048 | 42.9199 | 42.5674 | 42.6865 | 42.5812 | 8.7753 | 8.6746 | 83.9813 | 83.812 | -38.8641 | 84.1736 | 84.0729 | 0.26092 | -38.9282 | 89.1174 | 89.0167 | 0.022888 | 123.0469 | 122.9095 | 33.8928 | -0.082397 | 84.1415 | 84.0775 | 84.0408 | -39.1937 | 123.0286 | 122.9233 | 123.262 | -33.989
1909.5156 | 123.3765 | -80.3467 | 42.6544 | -0.064087 | 0.0049817 | 0.0026447 | 0.011326 | -0.018698 | -0.00022865 | 0.0010575 | 0.026169 | 0.016603 | -0.014063 | 0.015486 | -0.0048534 | 0.0097839 | 3.717 | 3.7903 | 3.6575 | 3.717 | 3.8086 | 3.6072 | 3.4287 | 42.6727 | 42.8787 | 42.5674 | 42.6727 | 42.5629 | 8.7708 | 8.67 | 83.9539 | 83.7753 | -38.8458 | 84.137 | 84.0637 | 0.28839 | -38.9374 | 89.1174 | 89.0167 | 0.01831 | 123.0194 | 122.9141 | 33.8974 | -0.091553 | 84.1553 | 84.0637 | 84.0042 | -39.2258 | 123.0194 | 122.9095 | 123.2254 | -33.9844
1910.5156 | 123.2941 | -80.3741 | 42.659 | 0.15717 | 0.0086133 | 0.0026447 | 0.013463 | -0.018698 | 0.00041235 | 0.0016983 | 0.11772 | 0.018953 | -0.013422 | 0.014845 | -0.0018628 | 0.0057251 | 3.653 | 3.7033 | 3.6163 | 3.6621 | 3.772 | 3.5934 | 3.4287 | 42.6315 | 42.7917 | 42.4072 | 42.6727 | 42.5629 | 8.7662 | 8.6609 | 83.9676 | 83.8028 | -38.887 | 84.0775 | 84.0363 | 0.23346 | -39.006 | 89.1403 | 89.035 | 0.013732 | 123.0057 | 122.7814 | 33.7463 | -0.096131 | 84.1461 | 84.0271 | 83.9905 | -39.2303 | 123.0469 | 122.937 | 123.1659 | -33.9981
1911.5156 | 123.2391 | -80.4474 | 42.6498 | -0.14038 | 0.010109 | 0.00072209 | 0.013463 | -0.017844 | 0.0038304 | 0.0038345 | -0.2256 | 0.021943 | -0.012995 | 0.015486 | -0.00079463 | 0.0089295 | 3.6346 | 3.6255 | 3.5294 | 3.6392 | 3.8361 | 3.5431 | 3.392 | 42.5766 | 42.7368 | 42.5995 | 42.7322 | 42.5949 | 8.7753 | 8.67 | 83.9905 | 83.8394 | -38.8138 | 84.0729 | 84.0866 | 0.24719 | -39.0152 | 89.2227 | 89.1174 | 0.082398 | 123.024 | 123.0469 | 33.9294 | -0.054931 | 84.2834 | 84.082 | 83.9767 | -39.2578 | 123.1796 | 123.0423 | 123.1842 | -33.9798
1912.5156 | 123.349 | -80.484 | 42.5674 | -0.0030518 | 0.0081861 | 0.0037127 | 0.013676 | -0.021475 | -0.0019376 | 0.0012711 | 0.026169 | 0.018098 | -0.013208 | 0.014631 | -0.0031446 | 0.010638 | 3.6484 | 3.7216 | 3.6255 | 3.6713 | 3.7765 | 3.5934 | 3.4012 | 42.6041 | 42.7597 | 42.6361 | 42.5949 | 42.4896 | 8.7708 | 8.67 | 84.0775 | 83.8852 | -38.7909 | 84.2056 | 84.1553 | 0.27008 | -38.9191 | 89.2548 | 89.1541 | 0.027466 | 123.0881 | 123.1201 | 33.9661 | -0.07782 | 84.2606 | 84.1324 | 84.1095 | -39.1663 | 123.0789 | 122.9736 | 123.2437 | -33.8974
1913.5156 | 123.3536 | -80.4291 | 42.6315 | -0.10223 | 0.010109 | 0.0034991 | 0.015385 | -0.019553 | -0.00086945 | 0.0036209 | 0.071945 | 0.017884 | -0.010858 | 0.014417 | -0.0035718 | 0.0093567 | 3.7079 | 3.7857 | 3.653 | 3.6758 | 3.7537 | 3.5614 | 3.3966 | 42.6865 | 42.8055 | 42.6498 | 42.6178 | 42.5262 | 8.7662 | 8.67 | 83.9905 | 83.8257 | -38.8779 | 84.2148 | 84.1049 | 0.27924 | -38.9236 | 89.1953 | 89.0991 | -0.013733 | 123.1155 | 123.0789 | 33.9798 | -0.10529 | 84.1827 | 84.137 | 84.082 | -39.2349 | 123.0469 | 122.9553 | 123.2346 | -33.9615
1914.5156 | 123.3032 | -80.5115 | 42.5537 | 0.13428 | 0.0060497 | 0.0020037 | 0.013035 | -0.019553 | -0.0019376 | 0.0040481 | 0.17876 | 0.018312 | -0.012995 | 0.014845 | -0.0016492 | 0.01192 | 3.6392 | 3.6942 | 3.5843 | 3.6346 | 3.7628 | 3.566 | 3.4058 | 42.4759 | 42.6865 | 42.4255 | 42.5629 | 42.4576 | 8.7708 | 8.67 | 84.0775 | 83.9172 | -38.7909 | 84.2056 | 84.1461 | 0.22888 | -38.9145 | 89.2822 | 89.1815 | 0.009155 | 122.9874 | 122.937 | 33.7555 | -0.09613 | 84.2743 | 84.1507 | 84.0958 | -39.1479 | 123.0743 | 122.9691 | 123.1979 | -33.8837
1915.5156 | 123.3582 | -80.4977 | 42.5354 | 0.0045777 | 0.0073315 | 0.0028583 | 0.011113 | -0.017203 | -1.505e-05 | -0.00022432 | -0.0043486 | 0.017457 | -0.01449 | 0.010145 | -0.0018628 | 0.0082885 | 3.6392 | 3.6942 | 3.598 | 3.6438 | 3.7491 | 3.566 | 3.3875 | 42.5034 | 42.7551 | 42.453 | 42.5949 | 42.485 | 8.7753 | 8.67 | 84.0637 | 83.8852 | -38.7863 | 84.1919 | 84.1415 | 0.25635 | -38.8962 | 89.2731 | 89.1678 | 0.05951 | 123.0011 | 122.9507 | 33.783 | -0.050354 | 84.2468 | 84.137 | 84.0958 | -39.1479 | 123.0927 | 122.9828 | 123.2529 | -33.8654
1916.5156 | 123.3673 | -80.4794 | 42.5583 | -0.056458 | 0.0077587 | 0.0032855 | 0.012394 | -0.021262 | -0.00086945 | 0.0023391 | -0.019608 | 0.017671 | -0.011713 | 0.015058 | -0.0031446 | 0.0099975 | 3.6987 | 3.7674 | 3.6438 | 3.685 | 3.7537 | 3.5843 | 3.4195 | 42.5858 | 42.778 | 42.5858 | 42.572 | 42.4713 | 8.7753 | 8.6655 | 84.0637 | 83.8989 | -38.8046 | 84.2468 | 84.1644 | 0.2655 | -38.8596 | 89.2548 | 89.1449 | 0.013732 | 123.0652 | 123.0652 | 33.9203 | -0.086976 | 84.2331 | 84.1782 | 84.1232 | -39.1388 | 123.0515 | 122.9507 | 123.2574 | -33.8928
1917.5156 | 123.3536 | -80.5252 | 42.5171 | -0.033569 | 0.0069043 | 0.0030719 | 0.012394 | -0.018057 | -0.001083 | 0.0029801 | 0.026169 | 0.01703 | -0.011499 | 0.013349 | -0.0042126 | 0.01192 | 3.6667 | 3.7033 | 3.5934 | 3.6667 | 3.7354 | 3.5339 | 3.392 | 42.5629 | 42.7368 | 42.485 | 42.5491 | 42.4438 | 8.7753 | 8.6746 | 84.0591 | 83.9172 | -38.7817 | 84.2285 | 84.1919 | 0.27466 | -38.8504 | 89.3005 | 89.1998 | 0.032043 | 123.0881 | 123.0103 | 33.8104 | -0.073242 | 84.2606 | 84.1919 | 84.1187 | -39.1251 | 123.0743 | 122.9691 | 123.262 | -33.8425
1918.5156 | 123.2986 | -80.5893 | 42.4759 | 0.17242 | 0.0090405 | 0.0028583 | 0.013463 | -0.018271 | -0.00065585 | 0.0042619 | 0.1635 | 0.018098 | -0.011072 | 0.011854 | -0.00036743 | 0.011279 | 3.6026 | 3.6621 | 3.5431 | 3.598 | 3.717 | 3.5202 | 3.3554 | 42.4988 | 42.6315 | 42.485 | 42.4805 | 42.3935 | 8.7753 | 8.67 | 84.1095 | 83.9447 | -38.7588 | 84.2514 | 84.1873 | 0.24261 | -38.8733 | 89.3646 | 89.2593 | 0.004578 | 123.0881 | 123.0743 | 33.815 | -0.082397 | 84.3063 | 84.1919 | 84.1324 | -39.1205 | 123.0698 | 122.9828 | 123.2208 | -33.8058
1919.5156 | 123.3307 | -80.5115 | 42.5171 | 0.027466 | 0.0071179 | 0.0028583 | 0.01154 | -0.020194 | -0.00086945 | 0.0034073 | -0.019608 | 0.01938 | -0.013849 | 0.01164 | -0.0018628 | 0.012134 | 3.6255 | 3.6758 | 3.5614 | 3.6255 | 3.7216 | 3.5568 | 3.3783 | 42.5262 | 42.6773 | 42.5537 | 42.5354 | 42.4393 | 8.7845 | 8.6655 | 84.0683 | 83.8898 | -38.7955 | 84.1873 | 84.137 | 0.24719 | -38.8916 | 89.296 | 89.1769 | 0.01831 | 123.0377 | 123.0652 | 33.8882 | -0.07782 | 84.2331 | 84.137 | 84.0729 | -39.1388 | 123.0469 | 122.9507 | 123.1888 | -33.8516
1920.5156 | 123.3398 | -80.6122 | 42.4576 | 0.088501 | 0.01139 | 0.0041401 | 0.011967 | -0.01998 | -1.505e-05 | 0.0012711 | 0.071945 | 0.018312 | -0.014704 | 0.01399 | -0.0027172 | 0.010425 | 3.6118 | 3.6438 | 3.5568 | 3.6118 | 3.7125 | 3.5202 | 3.3508 | 42.4484 | 42.6178 | 42.4759 | 42.5079 | 42.4072 | 8.7662 | 8.67 | 84.1324 | 83.963 | -38.7451 | 84.256 | 84.2239 | 0.26092 | -38.8458 | 89.3784 | 89.2822 | 0.050354 | 123.0606 | 123.0881 | 33.8058 | -0.050354 | 84.3246 | 84.2239 | 84.169 | -39.1068 | 123.1201 | 123.0194 | 123.23 | -33.7875
1921.5156 | 123.3536 | -80.603 | 42.4347 | -0.43793 | 0.0071179 | 0.0032855 | 0.012181 | -0.018057 | 0.0010532 | 0.0023391 | -0.13405 | 0.017671 | -0.013422 | 0.014204 | -0.00229 | 0.010425 | 3.6484 | 3.7216 | 3.598 | 3.6621 | 3.7079 | 3.5294 | 3.3508 | 42.5217 | 42.6865 | 42.5537 | 42.4713 | 42.3706 | 8.7708 | 8.67 | 84.1324 | 83.9539 | -38.7268 | 84.3246 | 84.2651 | 0.31128 | -38.7863 | 89.3738 | 89.2731 | 0.036621 | 123.1247 | 123.1567 | 33.8837 | -0.064087 | 84.3109 | 84.2514 | 84.201 | -39.0839 | 123.0743 | 122.9736 | 123.2895 | -33.7646
1922.5156 | 123.3536 | -80.6213 | 42.4576 | 0.16479 | 0.011604 | 0.0030719 | 0.011754 | -0.018271 | 0.0059666 | 0.0057571 | 0.17876 | 0.019593 | -0.015558 | 0.015699 | 0.0013416 | 0.0085021 | 3.6438 | 3.6438 | 3.5385 | 3.6118 | 3.6758 | 3.5202 | 3.3325 | 42.5125 | 42.8192 | 42.5491 | 42.4622 | 42.3614 | 8.7753 | 8.6746 | 84.1415 | 83.9539 | -38.7817 | 84.2651 | 84.2331 | 0.27923 | -38.8138 | 89.3967 | 89.296 | 0.004577 | 123.1338 | 123.1705 | 33.8745 | -0.096131 | 84.2972 | 84.2651 | 84.1599 | -39.1251 | 123.0835 | 122.9828 | 123.4406 | -33.783
1923.5156 | 123.3307 | -80.6442 | 42.4164 | 0.14954 | 0.010322 | 0.0028583 | 0.01154 | -0.022116 | -1.505e-05 | 0.0038345 | 0.20164 | 0.018953 | -0.012354 | 0.015272 | -0.0042126 | 0.011707 | 3.6072 | 3.6438 | 3.5156 | 3.5706 | 3.6484 | 3.4836 | 3.3325 | 42.4713 | 42.5537 | 42.4988 | 42.4118 | 42.3248 | 8.7753 | 8.6655 | 84.1278 | 83.9767 | -38.768 | 84.288 | 84.2148 | 0.23804 | -38.8092 | 89.4196 | 89.3097 | -0.004578 | 123.1155 | 123.143 | 33.8333 | -0.091553 | 84.2926 | 84.2514 | 84.1599 | -39.0839 | 123.056 | 122.9691 | 123.1979 | -33.7509
1924.5156 | 123.317 | -80.6763 | 42.3706 | 0.14191 | 0.0062635 | 0.0022175 | 0.01154 | -0.020407 | -0.00044225 | 0.0036209 | 0.094833 | 0.019807 | -0.01214 | 0.014204 | -0.0029308 | 0.012988 | 3.5385 | 3.5843 | 3.511 | 3.5477 | 3.6621 | 3.4698 | 3.2867 | 42.4164 | 42.5446 | 42.4988 | 42.4164 | 42.334 | 8.7753 | 8.6746 | 84.1461 | 83.963 | -38.7085 | 84.2606 | 84.2239 | 0.26092 | -38.8321 | 89.4516 | 89.3509 | 0.045777 | 123.0927 | 123.175 | 33.8242 | -0.036621 | 84.3384 | 84.2148 | 84.1873 | -39.0839 | 123.0927 | 123.0103 | 123.2208 | -33.696
1925.5156 | 123.317 | -80.603 | 42.4438 | 0.09613 | 0.0058361 | 0.0028583 | 0.012822 | -0.021048 | -0.001083 | 0.0021255 | 0.17113 | 0.01938 | -0.013849 | 0.01399 | -0.0025036 | 0.012988 | 3.5065 | 3.4607 | 3.3554 | 3.4973 | 3.6026 | 3.4149 | 3.2547 | 42.4622 | 42.572 | 42.5537 | 42.4576 | 42.3843 | 8.7708 | 8.6655 | 84.0179 | 83.8577 | -38.8412 | 84.0637 | 84.1003 | 0.24261 | -38.9374 | 89.3738 | 89.2685 | 0.013733 | 123.0652 | 123.1567 | 33.8882 | -0.05951 | 84.2056 | 84.1095 | 83.9584 | -39.1891 | 123.0606 | 122.9874 | 123.175 | -33.7784
1926.5156 | 123.3398 | -80.7175 | 42.3386 | 0.027466 | 0.0096813 | 0.0022175 | 0.013463 | -0.020835 | 0.0012668 | 0.0012711 | 0.049057 | 0.018953 | -0.01449 | 0.01399 | -0.0050672 | 0.010638 | 3.511 | 3.5522 | 3.4561 | 3.5339 | 3.6346 | 3.4332 | 3.2822 | 42.3889 | 42.4759 | 42.4713 | 42.366 | 42.2882 | 8.7708 | 8.67 | 84.1507 | 83.9996 | -38.7039 | 84.2697 | 84.2514 | 0.25177 | -38.8275 | 89.4882 | 89.3875 | 0.027466 | 123.1064 | 123.1888 | 33.8013 | -0.050354 | 84.3521 | 84.2285 | 84.1736 | -39.0564 | 123.0835 | 123.0057 | 123.1934 | -33.6685
1927.5156 | 123.3215 | -80.6396 | 42.3431 | -0.056458 | 0.0086133 | 0.0039263 | 0.0096174 | -0.019126 | -0.00044225 | 0.0010575 | -0.11116 | 0.018739 | -0.013422 | 0.012922 | -0.0037854 | 0.010638 | 3.5934 | 3.6484 | 3.5248 | 3.566 | 3.6072 | 3.447 | 3.2913 | 42.421 | 43.0664 | 42.6407 | 42.4622 | 42.3614 | 8.7753 | 8.6792 | 84.0866 | 83.931 | -38.736 | 84.288 | 84.2056 | 0.27466 | -38.7497 | 89.415 | 89.3188 | 0.11902 | 123.0606 | 123.2803 | 33.9615 | 0.01831 | 84.2468 | 84.2331 | 84.1644 | -39.0518 | 123.1018 | 123.0011 | 123.7061 | -33.6639
1928.5156 | 123.3261 | -80.7495 | 42.2653 | 0.21057 | 0.014381 | 0.0032855 | 0.013676 | -0.019339 | 0.0048984 | 0.0034073 | 0.17876 | 0.018098 | -0.012781 | 0.012922 | -0.0016492 | 0.013629 | 3.5431 | 3.598 | 3.4698 | 3.5248 | 3.5934 | 3.4287 | 3.2593 | 42.3752 | 42.4667 | 42.4255 | 42.3065 | 42.1921 | 8.7753 | 8.6655 | 84.1782 | 84.0088 | -38.6719 | 84.3475 | 84.2743 | 0.2655 | -38.7222 | 89.5248 | 89.415 | 0.041199 | 123.1247 | 123.175 | 33.7601 | -0.073242 | 84.343 | 84.2926 | 84.2194 | -39.006 | 123.056 | 122.9416 | 123.2162 | -33.5999
1929.5156 | 123.3398 | -80.7724 | 42.2607 | 0.18768 | 0.010536 | 0.0026447 | 0.010685 | -0.016135 | 0.0027622 | 0.0061845 | 0.1635 | 0.017884 | -0.013849 | 0.012495 | -0.0020764 | 0.011707 | 3.5339 | 3.5568 | 3.4653 | 3.5156 | 3.566 | 3.4012 | 3.241 | 42.4118 | 42.4942 | 42.4576 | 42.3248 | 42.2012 | 8.7799 | 8.6792 | 84.1736 | 84.0134 | -38.6948 | 84.3292 | 84.288 | 0.27466 | -38.7268 | 89.5523 | 89.4516 | 0.064087 | 123.1842 | 123.23 | 33.7784 | -0.059509 | 84.3384 | 84.3063 | 84.2377 | -39.0198 | 123.0972 | 122.9736 | 123.2666 | -33.5815
1930.5156 | 123.3627 | -80.7449 | 42.2836 | 0.26398 | 0.014168 | 0.0020037 | 0.012181 | -0.018271 | 0.0036166 | 0.0049027 | 0.11772 | 0.021516 | -0.011072 | 0.014845 | -0.0018628 | 0.012561 | 3.5339 | 3.5248 | 3.4149 | 3.4973 | 3.5843 | 3.4012 | 3.241 | 42.3935 | 42.485 | 42.4438 | 42.3294 | 42.2287 | 8.7753 | 8.67 | 84.1461 | 83.9859 | -38.6993 | 84.2697 | 84.2422 | 0.25635 | -38.7497 | 89.5203 | 89.415 | 0.045777 | 123.1384 | 123.1888 | 33.7738 | -0.054931 | 84.3292 | 84.2789 | 84.1599 | -39.0427 | 123.0743 | 122.9736 | 123.23 | -33.6136
1931.5156 | 123.3261 | -80.7404 | 42.3477 | 0.18768 | 0.0086133 | 0.0032855 | 0.013463 | -0.018271 | -0.0021512 | 0.0031937 | 0.17113 | 0.018098 | -0.015558 | 0.014417 | -0.0020764 | 0.01192 | 3.5019 | 3.5339 | 3.4332 | 3.4882 | 3.5889 | 3.4332 | 3.2547 | 42.3706 | 42.453 | 42.4438 | 42.334 | 42.2607 | 8.7708 | 8.6655 | 84.1736 | 83.9951 | -38.7589 | 84.2743 | 84.2285 | 0.23346 | -38.8458 | 89.5111 | 89.4058 | -0.013733 | 123.111 | 123.1842 | 33.7784 | -0.086975 | 84.3292 | 84.2422 | 84.1736 | -39.093 | 123.0743 | 123.0011 | 123.1934 | -33.6823
1932.5156 | 123.3536 | -80.7861 | 42.2424 | 0.14191 | 0.012886 | 0.0017901 | 0.012608 | -0.018698 | 0.00019875 | 0.0051163 | 0.1635 | 0.017457 | -0.012567 | 0.012922 | -0.003999 | 0.010852 | 3.5202 | 3.5385 | 3.4378 | 3.4882 | 3.5522 | 3.4058 | 3.2272 | 42.3706 | 42.4667 | 42.4255 | 42.3065 | 42.1921 | 8.7753 | 8.6746 | 84.1919 | 84.0134 | -38.6902 | 84.3246 | 84.2743 | 0.26092 | -38.7222 | 89.5615 | 89.4608 | 0.064087 | 123.1567 | 123.2117 | 33.7509 | -0.050354 | 84.3384 | 84.3063 | 84.2239 | -39.0152 | 123.0927 | 122.9782 | 123.2529 | -33.5678
1933.5156 | 123.3215 | -80.7678 | 42.3203 | 0.13428 | 0.010963 | 0.0052081 | 0.011967 | -0.019553 | 0.002335 | 0.0031937 | 0.20164 | 0.018098 | -0.012354 | 0.01399 | -0.0031446 | 0.013843 | 3.4882 | 3.511 | 3.4241 | 3.4515 | 3.5339 | 3.36 | 3.1952 | 42.3889 | 42.4438 | 42.4759 | 42.3203 | 42.2333 | 8.7708 | 8.6746 | 84.1278 | 83.963 | -38.7863 | 84.2789 | 84.2194 | 0.25635 | -38.8321 | 89.5386 | 89.4424 | 0 | 123.1567 | 123.2437 | 33.8013 | -0.086975 | 84.3018 | 84.256 | 84.1919 | -39.1251 | 123.0881 | 123.0011 | 123.2117 | -33.6456
1934.5156 | 123.3398 | -80.809 | 42.2607 | 0.22583 | 0.014381 | 0.00093569 | 0.014531 | -0.020621 | 0.004044 | 0.0038345 | 0.18639 | 0.021089 | -0.011927 | 0.01399 | -0.0018628 | 0.011066 | 3.4378 | 3.4287 | 3.3325 | 3.4241 | 3.566 | 3.3463 | 3.1769 | 42.3752 | 42.4347 | 42.4072 | 42.3065 | 42.2012 | 8.7708 | 8.6838 | 84.1553 | 83.9859 | -38.6948 | 84.2377 | 84.2331 | 0.24719 | -38.8229 | 89.5798 | 89.4928 | 0.045777 | 123.1842 | 123.2162 | 33.7234 | -0.059509 | 84.375 | 84.2468 | 84.1415 | -39.0839 | 123.1155 | 123.0103 | 123.2437 | -33.577
1935.5156 | 123.3124 | -80.8456 | 42.2699 | 0.12665 | 0.0077587 | 0.0020037 | 0.013676 | -0.020835 | -0.0019376 | 0.0053299 | -1.7973 | 0.017671 | -0.014063 | 0.01164 | -0.0046398 | 0.015552 | 3.4332 | 3.447 | 3.3783 | 3.4424 | 3.5522 | 3.3646 | 3.1998 | 42.2699 | 42.4255 | 42.4118 | 42.2791 | 42.2058 | 8.7662 | 8.6746 | 84.2102 | 84.0454 | -38.7177 | 84.2926 | 84.288 | 0.24261 | -38.8367 | 89.6118 | 89.5203 | 0.009156 | 123.1155 | 123.2574 | 33.7372 | -0.064086 | 84.3979 | 84.2789 | 84.2239 | -39.0701 | 123.1247 | 123.0515 | 123.2712 | -33.5953
1936.5156 | 123.3536 | -80.7907 | 42.2607 | 1.9806 | 0.014381 | 0.0024311 | 0.016881 | -0.019339 | 0.0025486 | 0.0051163 | 0.12535 | 0.018525 | -0.011499 | 0.012708 | -0.0025036 | 0.013416 | 3.5156 | 3.5019 | 3.4149 | 3.4653 | 3.5019 | 3.3279 | 3.1815 | 42.366 | 42.4576 | 42.453 | 42.2836 | 42.2058 | 8.7708 | 8.6746 | 84.1187 | 83.9722 | -38.7589 | 84.2926 | 84.256 | 0.28381 | -38.7451 | 89.5615 | 89.4653 | 0.022888 | 123.1567 | 123.2437 | 33.7784 | -0.054931 | 84.2926 | 84.3063 | 84.2056 | -39.0793 | 123.0743 | 122.9965 | 123.2483 | -33.5861
1937.5156 | 123.3673 | -80.8136 | 42.247 | 0.23346 | 0.012245 | 0.00029489 | 0.010685 | -0.017417 | 0.001694 | 0.0038345 | -0.18745 | 0.016389 | -0.012995 | 0.010359 | -0.0025036 | 0.012988 | 3.5019 | 3.4927 | 3.4149 | 3.4698 | 3.5248 | 3.3783 | 3.186 | 42.3431 | 42.4393 | 42.4393 | 42.2607 | 42.1692 | 8.7845 | 8.67 | 84.1919 | 83.9996 | -38.7222 | 84.3063 | 84.2834 | 0.28381 | -38.7451 | 89.5981 | 89.4836 | 0.013733 | 123.1567 | 123.2529 | 33.7692 | -0.07782 | 84.3384 | 84.3155 | 84.2285 | -39.061 | 123.0743 | 122.9828 | 123.2529 | -33.577
1938.5156 | 123.2391 | -80.9418 | 42.1921 | -2.7802 | 0.016517 | -0.00077331 | 0.012608 | -0.020407 | 0.0038304 | 0.0055435 | 0.14824 | 0.020234 | -0.010645 | 0.01399 | -0.00079463 | 0.011066 | 3.3646 | 3.3875 | 3.3051 | 3.3737 | 3.598 | 3.3325 | 3.1723 | 42.1875 | 42.247 | 42.2424 | 42.2424 | 42.1738 | 8.7753 | 8.67 | 84.2743 | 84.1141 | -38.5941 | 84.3292 | 84.3155 | 0.20142 | -38.8275 | 89.7171 | 89.6118 | 0.050354 | 123.1293 | 123.1842 | 33.5724 | -0.018311 | 84.5398 | 84.3063 | 84.2468 | -39.0198 | 123.1842 | 123.1155 | 123.1888 | -33.522
1939.5156 | 123.317 | -80.864 | 42.1875 | 0.18005 | 0.010109 | 0.0026447 | 0.011967 | -0.020407 | -0.002792 | 0.0031937 | 0.17113 | 0.017671 | -0.014704 | 0.013349 | -0.0050672 | 0.013629 | 3.4149 | 3.4103 | 3.3508 | 3.4287 | 3.5019 | 3.3371 | 3.154 | 42.2379 | 42.3477 | 42.3523 | 42.2104 | 42.128 | 8.7753 | 8.67 | 84.201 | 84.0179 | -38.6856 | 84.2743 | 84.2926 | 0.27466 | -38.7726 | 89.6393 | 89.534 | 0.022888 | 123.1018 | 123.2162 | 33.6823 | -0.059509 | 84.3658 | 84.2789 | 84.2148 | -39.0335 | 123.0743 | 122.9919 | 123.2117 | -33.5175
1940.5156 | 123.2529 | -80.896 | 42.2287 | -0.12512 | 0.016304 | 0.0022175 | 0.01389 | -0.018057 | 0.0036166 | 0.0044755 | 0.11772 | 0.021089 | -0.010645 | 0.013136 | -0.0010082 | 0.011066 | 3.3554 | 3.3051 | 3.2089 | 3.3371 | 3.5294 | 3.2776 | 3.1036 | 42.2058 | 42.2882 | 42.2974 | 42.2836 | 42.1646 | 8.7616 | 8.67 | 84.1736 | 83.9996 | -38.6993 | 84.201 | 84.2331 | 0.23346 | -38.8733 | 89.6576 | 89.566 | 0.054931 | 123.1018 | 123.1934 | 33.6273 | -0.064087 | 84.4254 | 84.2514 | 84.1049 | -39.1251 | 123.1796 | 123.0606 | 123.1842 | -33.5587
1941.5156 | 123.3582 | -80.8502 | 42.1875 | 0.36316 | 0.01139 | 0.0041401 | 0.01154 | -0.016135 | -0.00022865 | 0.0057571 | 0.23216 | 0.020234 | -0.012567 | 0.012068 | -0.0035718 | 0.012988 | 3.4378 | 3.4241 | 3.3325 | 3.4149 | 3.4698 | 3.2959 | 3.1311 | 42.3019 | 42.3981 | 42.4164 | 42.1829 | 42.1646 | 8.7753 | 8.6746 | 84.1461 | 83.9813 | -38.7177 | 84.2743 | 84.2651 | 0.28381 | -38.7497 | 89.6255 | 89.5248 | -0.004578 | 123.1522 | 123.2666 | 33.7418 | -0.022888 | 84.3201 | 84.288 | 84.1827 | -39.0564 | 123.0331 | 123.0148 | 123.2483 | -33.5129
1942.5156 | 123.2346 | -80.9647 | 42.1692 | 0.10376 | 0.016945 | 0.0039263 | 0.014531 | -0.016776 | 0.0059666 | 0.0055435 | 0.018539 | 0.02173 | -0.0095768 | 0.01634 | -0.0029308 | 0.0097839 | 3.3051 | 3.2547 | 3.186 | 3.3279 | 3.511 | 3.2639 | 3.0762 | 42.3203 | 42.1326 | 42.2424 | 42.215 | 42.1326 | 8.7753 | 8.6746 | 84.2285 | 84.0408 | -38.6581 | 84.2194 | 84.2926 | 0.25177 | -38.8641 | 89.74 | 89.6393 | 0.045777 | 123.2849 | 123.2071 | 33.5678 | -0.036621 | 84.4757 | 84.2697 | 84.1507 | -39.093 | 123.1796 | 123.0972 | 123.0972 | -33.4946
1943.5156 | 123.23 | -80.9463 | 42.1921 | -0.15564 | 0.019295 | 0.00050849 | 0.014317 | -0.020621 | 0.0061802 | 0.0040481 | 0.13298 | 0.020021 | -0.010218 | 0.013349 | -0.0033582 | 0.012988 | 3.3325 | 3.2639 | 3.1815 | 3.3051 | 3.5065 | 3.273 | 3.0716 | 42.1463 | 42.2104 | 42.2241 | 42.2058 | 42.1371 | 8.7708 | 8.6746 | 84.2194 | 84.0179 | -38.6856 | 84.2102 | 84.2514 | 0.23346 | -38.8596 | 89.7171 | 89.621 | 0.013733 | 123.0927 | 123.1705 | 33.5495 | -0.054932 | 84.4528 | 84.2789 | 84.1278 | -39.1205 | 123.1522 | 123.0835 | 123.1567 | -33.5175
1944.5156 | 123.2483 | -80.9967 | 42.1417 | 0.088501 | 0.016517 | 0.0034991 | 0.010258 | -0.01763 | 0.0031894 | 0.0059707 | 0.049057 | 0.020021 | -0.010645 | 0.013777 | -0.0029308 | 0.012775 | 3.3188 | 3.2913 | 3.2089 | 3.3188 | 3.4836 | 3.2455 | 3.0945 | 42.1005 | 42.2104 | 42.1875 | 42.1738 | 42.1005 | 8.7753 | 8.6838 | 84.2422 | 84.0912 | -38.6581 | 84.288 | 84.3155 | 0.2243 | -38.8229 | 89.772 | 89.6805 | 0.032043 | 123.0972 | 123.1842 | 33.5037 | -0.041199 | 84.4803 | 84.3155 | 84.2056 | -39.0472 | 123.1705 | 123.0972 | 123.2071 | -33.4579
1945.5312 | 123.3627 | -80.9235 | 42.1463 | -0.14801 | 0.01139 | 0.011617 | 0.016453 | -0.019766 | -0.00086945 | 0.0034073 | -0.1722 | 0.017457 | -0.01214 | 0.013563 | -0.0042126 | 0.013202 | 3.3737 | 3.447 | 3.2822 | 3.3508 | 3.4332 | 3.2547 | 3.0899 | 42.2058 | 42.3798 | 42.3431 | 42.128 | 42.0731 | 8.7753 | 8.67 | 84.1782 | 84.0134 | -38.7131 | 84.3704 | 84.2743 | 0.26093 | -38.7726 | 89.6988 | 89.5935 | -0.01831 | 123.1293 | 123.2666 | 33.6731 | -0.073242 | 84.3567 | 84.2972 | 84.2056 | -39.0564 | 123.0515 | 122.9965 | 123.3032 | -33.4763
1946.5156 | 123.2529 | -81.0104 | 42.1188 | 0.17242 | 0.016731 | 0.00072209 | 0.014103 | -0.014426 | 0.0027622 | 0.0061845 | 0.36186 | 0.020234 | -0.010645 | 0.015058 | -0.00229 | 0.012775 | 2.9846 | 3.5019 | 3.4149 | 3.3875 | 3.4653 | 3.2364 | 3.0624 | 42.0502 | 42.1509 | 42.1371 | 42.1371 | 42.0456 | 8.7708 | 8.6655 | 84.2468 | 84.0729 | -38.6536 | 84.5123 | 84.3979 | 0.32501 | -39.1342 | 89.7812 | 89.6759 | 0.018311 | 123.0606 | 123.1476 | 33.4717 | -0.073242 | 84.4757 | 83.9951 | 84.4254 | -39.0564 | 123.1476 | 123.056 | 123.1613 | -33.4534
1947.5156 | 123.2758 | -81.0287 | 42.1005 | 0.18768 | 0.015877 | 0.0043537 | 0.01389 | -0.020407 | 0.0021214 | 0.0042619 | 0.14061 | 0.018953 | -0.0097904 | 0.014417 | -0.0020764 | 0.013843 | 3.2547 | 3.2501 | 3.1631 | 3.2776 | 3.479 | 3.2318 | 3.0396 | 42.0731 | 42.1417 | 42.1692 | 42.1509 | 42.0456 | 8.7662 | 8.6746 | 84.2606 | 84.0683 | -38.6215 | 84.2789 | 84.3063 | 0.23804 | -38.8458 | 89.7949 | 89.7034 | 0.050354 | 123.1018 | 123.1979 | 33.4946 | -0.054932 | 84.5078 | 84.2834 | 84.1919 | -39.061 | 123.1796 | 123.0743 | 123.1705 | -33.4259
1948.5156 | 123.2254 | -81.0425 | 42.128 | 0.080872 | 0.017372 | 0.0017901 | 0.014744 | -0.018698 | 0.0038304 | 0.0066117 | 0.033798 | 0.020021 | -0.011713 | 0.015913 | -0.0025036 | 0.012988 | 3.2684 | 3.2318 | 3.1815 | 3.273 | 3.4515 | 3.2227 | 3.0533 | 42.0319 | 42.1555 | 42.1417 | 42.1555 | 42.0776 | 8.7799 | 8.6746 | 84.2651 | 84.0958 | -38.6765 | 84.2743 | 84.3155 | 0.21973 | -38.8596 | 89.8224 | 89.7171 | 0.027466 | 123.0743 | 123.1842 | 33.4671 | -0.050354 | 84.494 | 84.3109 | 84.2239 | -39.0747 | 123.1979 | 123.1201 | 123.1979 | -33.4534
1949.5156 | 123.2529 | -81.0562 | 42.1188 | 0.11902 | 0.017158 | 0.0030719 | 0.013463 | -0.016989 | 0.0027622 | 0.0051163 | 0.041427 | 0.021943 | -0.0070132 | 0.013349 | -0.0048534 | 0.015765 | 3.2501 | 3.2227 | 3.1494 | 3.2547 | 3.4424 | 3.2043 | 3.0487 | 41.8945 | 42.128 | 42.3431 | 42.1097 | 42.0731 | 8.7753 | 8.6655 | 84.2606 | 84.1049 | -38.6765 | 84.2789 | 84.3109 | 0.20599 | -38.8687 | 89.8315 | 89.7217 | -0.009155 | 122.9507 | 123.3994 | 33.6777 | -0.045776 | 84.4986 | 84.3063 | 84.2056 | -39.0701 | 123.1659 | 123.1293 | 123.1842 | -33.4534
1950.5156 | 123.2895 | -81.0104 | 42.1051 | 0.18768 | 0.014808 | 0.0028583 | 0.01389 | -0.019339 | 0.00041235 | 0.0055435 | 0.2169 | 0.020234 | -0.014704 | 0.015058 | -0.003999 | 0.01427 | 3.241 | 3.2135 | 3.1403 | 3.2501 | 3.4195 | 3.1769 | 3.0258 | 42.0822 | 42.1692 | 42.2058 | 42.1555 | 42.0456 | 8.7753 | 8.67 | 84.1873 | 84.0363 | -38.6856 | 84.2239 | 84.2606 | 0.2243 | -38.8641 | 89.7858 | 89.6805 | 0.050354 | 123.0927 | 123.2162 | 33.5358 | -0.05951 | 84.4299 | 84.2514 | 84.1507 | -39.0793 | 123.1659 | 123.056 | 123.1796 | -33.4351
1951.5156 | 123.3353 | -81.015 | 42.0639 | 0.20294 | 0.01609 | 0.0017901 | 0.015812 | -0.020621 | -0.001083 | 0.0025529 | 0.23216 | 0.019166 | -0.010218 | 0.014417 | -0.0025036 | 0.014056 | 3.2776 | 3.2547 | 3.1952 | 3.2639 | 3.4103 | 3.2227 | 3.035 | 42.1143 | 42.2058 | 42.2241 | 42.0731 | 42.009 | 8.7708 | 8.67 | 84.2377 | 84.05 | -38.6536 | 84.2697 | 84.2789 | 0.22888 | -38.7863 | 89.7858 | 89.6851 | 0.009155 | 123.1293 | 123.2391 | 33.5541 | -0.054932 | 84.4254 | 84.2926 | 84.2102 | -39.0289 | 123.0881 | 123.024 | 123.2208 | -33.3939
1952.5156 | 123.2574 | -81.0287 | 42.1005 | 0.019836 | 0.016945 | 0.0011493 | 0.011967 | -0.017417 | 0.0031894 | 0.0051163 | 0.049057 | 0.021302 | -0.010645 | 0.013136 | -0.0020764 | 0.012988 | 3.3142 | 3.2822 | 3.1906 | 3.2913 | 3.4287 | 3.2089 | 3.0258 | 42.0547 | 42.1738 | 42.16 | 42.1188 | 42.0685 | 8.7753 | 8.6609 | 84.2377 | 84.0546 | -38.6719 | 84.3109 | 84.3201 | 0.2655 | -38.7863 | 89.8041 | 89.6896 | 0.01831 | 123.0835 | 123.1888 | 33.4991 | -0.032044 | 84.4574 | 84.343 | 84.2194 | -39.0747 | 123.1476 | 123.0972 | 123.2025 | -33.4396
1953.5156 | 123.2529 | -81.1111 | 42.0639 | 0.035095 | 0.01609 | 0.0015765 | 0.015172 | -0.017844 | 0.0029758 | 0.0051163 | 0.049057 | 0.021089 | -0.0087222 | 0.013136 | -0.0033582 | 0.014484 | 3.2501 | 3.2593 | 3.154 | 3.2501 | 3.4195 | 3.1952 | 3.0304 | 41.9998 | 42.1371 | 42.1051 | 42.0776 | 42.0044 | 8.7753 | 8.6746 | 84.3063 | 84.1415 | -38.6444 | 84.3704 | 84.3613 | 0.21973 | -38.8138 | 89.8865 | 89.7858 | 0.013733 | 123.111 | 123.2162 | 33.4305 | -0.059509 | 84.5306 | 84.3613 | 84.2651 | -39.0335 | 123.1888 | 123.1155 | 123.2483 | -33.3893
1954.5156 | 123.2941 | -81.102 | 42.0319 | -0.15564 | 0.015236 | 0.0028583 | 0.012394 | -0.019553 | -0.00044225 | 0.0027665 | -0.10353 | 0.020448 | -0.0095768 | 0.013777 | -0.0025036 | 0.010852 | 3.2547 | 3.2684 | 3.1815 | 3.2867 | 3.4149 | 3.1998 | 3.0212 | 42.0227 | 42.1646 | 42.1326 | 42.0547 | 41.9861 | 8.7753 | 8.67 | 84.3018 | 84.1232 | -38.6169 | 84.3704 | 84.3887 | 0.2655 | -38.7772 | 89.8773 | 89.772 | 0.022889 | 123.1247 | 123.2346 | 33.4625 | -0.045776 | 84.5169 | 84.3567 | 84.2834 | -39.0106 | 123.1567 | 123.0881 | 123.2666 | -33.3618
1955.5312 | 123.3353 | -81.0837 | 42.0364 | -0.44556 | 0.0094677 | 0.0030719 | 0.012608 | -0.018912 | -0.0057828 | -0.00043792 | 0.13298 | 0.018953 | -0.014276 | 0.015058 | -0.0050672 | 0.015552 | 3.2318 | 3.2455 | 3.1815 | 3.2547 | 3.3417 | 3.154 | 2.9984 | 42.041 | 42.1738 | 42.215 | 42.0502 | 41.9998 | 8.7708 | 8.6746 | 84.2377 | 84.082 | -38.6948 | 84.3292 | 84.3384 | 0.25635 | -38.8046 | 89.8544 | 89.7583 | 0.013733 | 123.1247 | 123.2986 | 33.5403 | -0.036621 | 84.4254 | 84.3155 | 84.2651 | -39.0381 | 123.1338 | 123.0835 | 123.2574 | -33.3618
1956.5156 | 123.2712 | -81.0608 | 42.1051 | -0.20142 | 0.013527 | 0.0049945 | 0.015172 | -0.018912 | 0.0027622 | -0.00043792 | -0.15694 | 0.021516 | -0.010004 | 0.012495 | -0.0012218 | 0.011707 | 3.2227 | 3.2181 | 3.1311 | 3.2364 | 3.4287 | 3.1769 | 3.0029 | 42.0273 | 42.1692 | 42.1326 | 42.1463 | 42.0364 | 8.7708 | 8.6792 | 84.2377 | 84.0637 | -38.6765 | 84.2789 | 84.2972 | 0.23346 | -38.8824 | 89.8315 | 89.74 | 0.041198 | 123.0881 | 123.1934 | 33.4534 | -0.068665 | 84.4894 | 84.2834 | 84.1919 | -39.1022 | 123.2071 | 123.0972 | 123.23 | -33.4259
1957.5156 | 123.2986 | -81.0745 | 42.0639 | -0.13275 | 0.014808 | 0.0011493 | 0.014103 | -0.017844 | 0.0019078 | 0.0016983 | -0.18745 | 0.020234 | -0.0078678 | 0.014204 | -0.0031446 | 0.011493 | 3.2181 | 3.2272 | 3.1448 | 3.2501 | 3.4241 | 3.1723 | 2.9938 | 41.9998 | 42.16 | 42.1371 | 42.0731 | 42.0044 | 8.7799 | 8.6746 | 84.2468 | 84.0683 | -38.6398 | 84.3018 | 84.3246 | 0.25635 | -38.8458 | 89.8544 | 89.7491 | 0.009155 | 123.0743 | 123.2117 | 33.4625 | -0.059509 | 84.4986 | 84.2926 | 84.2194 | -39.0701 | 123.1476 | 123.0789 | 123.2346 | -33.3893
1958.5156 | 123.2574 | -81.0883 | 42.0456 | -0.21667 | 0.011177 | 0.0020037 | 0.016453 | -0.016776 | -0.0023648 | 0.0014847 | -0.11879 | 0.019593 | -0.011499 | 0.015486 | -0.006776 | 0.01427 | 3.2272 | 3.2822 | 3.1769 | 3.241 | 3.3829 | 3.1677 | 2.9846 | 41.9861 | 42.1326 | 42.1005 | 42.0685 | 42.0273 | 8.7753 | 8.6792 | 84.256 | 84.0729 | -38.6627 | 84.3704 | 84.3292 | 0.25635 | -38.8184 | 89.8636 | 89.7675 | 0.022888 | 123.0743 | 123.1888 | 33.4213 | -0.01831 | 84.4711 | 84.3155 | 84.2651 | -39.061 | 123.1567 | 123.1155 | 123.2208 | -33.3664
1959.5156 | 123.3124 | -81.102 | 42.0319 | -0.13275 | 0.017799 | 0.0015765 | 0.016026 | -0.018485 | 0.0031894 | -1.0724e-05 | -0.1722 | 0.018525 | -0.0076542 | 0.015058 | -0.0033582 | 0.012347 | 3.2227 | 3.2501 | 3.2593 | 3.3051 | 3.3783 | 3.1357 | 2.9755 | 42.0273 | 42.1371 | 42.1234 | 42.0731 | 41.9815 | 8.7753 | 8.67 | 84.2377 | 84.0775 | -38.6536 | 84.3521 | 84.407 | 0.32959 | -38.8092 | 89.8773 | 89.772 | 0.041199 | 123.1293 | 123.2254 | 33.4534 | -0.050354 | 84.4803 | 84.3246 | 84.3613 | -39.0564 | 123.175 | 123.0835 | 123.2391 | -33.3618
1960.5156 | 123.2529 | -81.1249 | 42.0731 | -0.12512 | 0.012245 | 0.0037127 | 0.014317 | -0.019766 | -0.0025784 | 0.0038345 | -0.14931 | 0.017244 | -0.012567 | 0.014204 | -0.0042126 | 0.013629 | 3.1631 | 3.1906 | 3.1082 | 3.2043 | 3.392 | 3.1586 | 2.9663 | 41.9769 | 42.1051 | 42.1097 | 42.0822 | 42.0044 | 8.7708 | 8.6746 | 84.2834 | 84.0912 | -38.681 | 84.3155 | 84.3292 | 0.23804 | -38.9099 | 89.8956 | 89.7995 | 0.009155 | 123.1018 | 123.2346 | 33.4351 | -0.068664 | 84.5169 | 84.288 | 84.2331 | -39.1067 | 123.2071 | 123.1293 | 123.23 | -33.3984
1961.5156 | 123.2941 | -81.1249 | 42.0136 | -0.18616 | 0.015663 | 0.0015765 | 0.014958 | -0.018271 | 0.0027622 | 0.0014847 | -0.14168 | 0.020875 | -0.010431 | 0.015058 | -0.0018628 | 0.012775 | 3.1906 | 3.1998 | 3.0991 | 3.2181 | 3.3737 | 3.1128 | 2.9617 | 41.9815 | 42.1188 | 42.0776 | 42.0227 | 41.9266 | 8.7799 | 8.6746 | 84.2377 | 84.0866 | -38.6398 | 84.3246 | 84.343 | 0.25635 | -38.8229 | 89.9048 | 89.7995 | 0.009155 | 123.1064 | 123.2025 | 33.403 | -0.086975 | 84.4986 | 84.3155 | 84.2239 | -39.0518 | 123.1476 | 123.0515 | 123.2437 | -33.3389
1962.5156 | 123.2117 | -81.1066 | 42.0456 | -0.2243 | 0.0094677 | 0.0030719 | 0.010685 | -0.019126 | -0.00022865 | 0.0019119 | -0.095902 | 0.018525 | -0.011499 | 0.01634 | -0.0054944 | 0.013629 | 3.186 | 3.1723 | 3.0899 | 3.1769 | 3.36 | 3.1219 | 2.9572 | 41.9312 | 42.0776 | 42.0639 | 42.0456 | 41.9678 | 8.7753 | 8.67 | 84.2285 | 84.0637 | -38.6856 | 84.2789 | 84.2834 | 0.21973 | -38.8596 | 89.8819 | 89.7766 | 0 | 123.0377 | 123.1705 | 33.3939 | -0.07782 | 84.4666 | 84.2926 | 84.1965 | -39.0884 | 123.1522 | 123.0743 | 123.1842 | -33.3755
1963.5156 | 123.2849 | -81.1661 | 41.9861 | -0.10986 | 0.012672 | 0.0011493 | 0.014317 | -0.018057 | 0.0029758 | 0.0044755 | -0.14168 | 0.018525 | -0.011072 | 0.015058 | -0.0033582 | 0.011493 | 3.1631 | 3.1677 | 3.0762 | 3.1952 | 3.36 | 3.1082 | 2.9343 | 41.8762 | 42.0547 | 42.0364 | 42.0136 | 41.9128 | 8.7753 | 8.6746 | 84.2743 | 84.1003 | -38.6261 | 84.3338 | 84.3613 | 0.26093 | -38.8229 | 89.9414 | 89.8407 | 0.027466 | 123.0423 | 123.2025 | 33.3618 | -0.073242 | 84.5261 | 84.3292 | 84.2422 | -39.0518 | 123.1796 | 123.0789 | 123.2208 | -33.3115
1964.5156 | 123.3719 | -81.1157 | 41.9724 | -0.24719 | 0.0094677 | 0.0020037 | 0.010899 | -0.018485 | -0.0051418 | 0.0031937 | -0.0043486 | 0.016603 | -0.011927 | 0.013136 | -0.0031446 | 0.012775 | 3.2089 | 3.3096 | 3.1998 | 3.2547 | 3.2959 | 3.1219 | 2.9709 | 42.0181 | 42.1967 | 42.1692 | 41.9952 | 41.8991 | 8.7799 | 8.67 | 84.2377 | 84.0866 | -38.6765 | 84.4254 | 84.3704 | 0.28381 | -38.7634 | 89.8956 | 89.7858 | 0.022888 | 123.1338 | 123.2849 | 33.4991 | -0.073242 | 84.4116 | 84.3246 | 84.3155 | -39.0015 | 123.111 | 123.0148 | 123.3124 | -33.3023
1965.5156 | 123.262 | -81.1386 | 41.9998 | -0.20142 | 0.0096813 | 0.0047809 | 0.012181 | -0.021689 | -0.0034328 | 0.0021255 | -0.11879 | 0.017884 | -0.014063 | 0.012495 | -0.0044262 | 0.013843 | 3.1586 | 3.1952 | 3.0991 | 3.1723 | 3.3325 | 3.1036 | 2.9343 | 41.9403 | 42.0731 | 42.0639 | 42.041 | 41.9586 | 8.7845 | 8.6746 | 84.2422 | 84.0729 | -38.6673 | 84.3338 | 84.3109 | 0.23804 | -38.8412 | 89.9231 | 89.8132 | 0.041199 | 123.0789 | 123.2025 | 33.3893 | -0.041199 | 84.4711 | 84.2972 | 84.2377 | -39.0656 | 123.1796 | 123.0972 | 123.2117 | -33.3252
1966.5156 | 123.2529 | -81.1111 | 42.0136 | -0.1709 | 0.0077587 | 0.0011493 | 0.012822 | -0.01763 | -0.0019376 | 0.0016983 | -0.15694 | 0.017671 | -0.011072 | 0.013777 | -0.0052808 | 0.012134 | 3.1815 | 3.2227 | 3.1128 | 3.1952 | 3.3188 | 3.0991 | 2.9297 | 41.9724 | 42.0959 | 42.0959 | 42.0227 | 41.9632 | 8.7708 | 8.6746 | 84.2102 | 84.0408 | -38.6948 | 84.3338 | 84.3063 | 0.2655 | -38.8321 | 89.8819 | 89.7858 | 0.009155 | 123.0835 | 123.2071 | 33.4213 | -0.050354 | 84.4299 | 84.2926 | 84.2239 | -39.0839 | 123.1338 | 123.0743 | 123.2071 | -33.3389
1967.5156 | 123.2574 | -81.1478 | 41.9769 | -0.27771 | 0.010322 | 0.0039263 | 0.015172 | -0.022757 | -0.00044225 | 0.00063028 | -0.19508 | 0.01938 | -0.010004 | 0.015272 | -0.0025036 | 0.012134 | 3.1494 | 3.1494 | 3.0441 | 3.1448 | 3.36 | 3.0945 | 2.9251 | 41.9174 | 42.041 | 42.0181 | 42.009 | 41.9357 | 8.7753 | 8.6746 | 84.2422 | 84.0729 | -38.6169 | 84.2972 | 84.2926 | 0.21973 | -38.8275 | 89.9231 | 89.8224 | 0.032043 | 123.0652 | 123.1659 | 33.3435 | -0.041199 | 84.5078 | 84.2972 | 84.1919 | -39.0518 | 123.1567 | 123.0835 | 123.1888 | -33.3023
1968.5156 | 123.3398 | -81.1661 | 41.9449 | -0.14801 | 0.0079723 | 0.0041401 | 0.014744 | -0.018057 | -0.0017238 | 0.0014847 | -0.11116 | 0.015748 | -0.012781 | 0.014204 | -0.0059216 | 0.012561 | 3.2043 | 3.2822 | 3.1815 | 3.2227 | 3.3096 | 3.1174 | 2.9617 | 41.9449 | 42.128 | 42.0822 | 41.9174 | 41.8488 | 8.7753 | 8.6792 | 84.2834 | 84.1278 | -38.6353 | 84.4482 | 84.3887 | 0.26093 | -38.7405 | 89.9414 | 89.8453 | -0.027466 | 123.111 | 123.2483 | 33.403 | -0.09613 | 84.4757 | 84.3704 | 84.3475 | -38.9832 | 123.0835 | 123.0148 | 123.2941 | -33.2657
1969.5156 | 123.2346 | -81.2073 | 41.9769 | -0.1709 | 0.011604 | 0.0024311 | 0.012394 | -0.019339 | 0.00041235 | 0.0014847 | -0.24086 | 0.018525 | -0.013422 | 0.017622 | -0.0018628 | 0.010638 | 3.1082 | 3.1448 | 3.0396 | 3.1265 | 3.3096 | 3.0716 | 2.9068 | 41.8396 | 42.0639 | 41.9861 | 41.9769 | 41.8945 | 8.7753 | 8.67 | 84.2789 | 84.1141 | -38.6673 | 84.3521 | 84.3338 | 0.21973 | -38.8687 | 89.9826 | 89.8773 | 0 | 123.0469 | 123.1934 | 33.316 | -0.082398 | 84.5169 | 84.3155 | 84.2468 | -39.0701 | 123.1842 | 123.1018 | 123.2712 | -33.3069
1970.5156 | 123.3582 | -81.1752 | 41.9128 | -1.5823 | 0.0041271 | 0.0030719 | 0.0072674 | -0.018057 | -0.0055692 | 0.0014847 | -0.073013 | 0.018739 | -0.015131 | 0.013777 | -0.0050672 | 0.013843 | 3.1448 | 3.2501 | 3.1631 | 3.1998 | 3.2639 | 3.0716 | 2.9297 | 41.9678 | 42.1234 | 42.1051 | 41.8991 | 41.8396 | 8.7753 | 8.6746 | 84.2468 | 84.1049 | -38.649 | 84.4254 | 84.375 | 0.27008 | -38.768 | 89.9506 | 89.8499 | -0.013733 | 123.143 | 123.2803 | 33.4305 | -0.073242 | 84.4391 | 84.3201 | 84.3384 | -38.9832 | 123.0743 | 123.0148 | 123.2986 | -33.2382
1971.5156 | 123.3444 | -81.2073 | 41.9037 | -0.14038 | 0.0098951 | 0.0030719 | 0.011754 | -0.020194 | -0.0015102 | 0.0021255 | -0.15694 | 0.017457 | -0.013636 | 0.012068 | -0.0046398 | 0.012775 | 3.1906 | 3.2547 | 3.1448 | 3.1952 | 3.273 | 3.0762 | 2.9388 | 41.9449 | 42.0822 | 42.0502 | 41.9037 | 41.8213 | 8.7753 | 8.6838 | 84.2834 | 84.1461 | -38.6307 | 84.462 | 84.4025 | 0.25635 | -38.7131 | 89.9826 | 89.8911 | 0 | 123.1522 | 123.2574 | 33.3664 | -0.082398 | 84.4803 | 84.3979 | 84.3521 | -38.9648 | 123.111 | 123.0286 | 123.2895 | -33.2199
1972.5156 | 123.4268 | -81.2302 | 41.8671 | -0.071716 | 0.0090405 | 0.0049945 | 0.011967 | -0.021262 | -0.0030056 | 0.0012711 | -0.065384 | 0.016603 | -0.015558 | 0.011854 | -0.0059216 | 0.011279 | 3.2089 | 3.2776 | 3.1448 | 3.2089 | 3.2684 | 3.0991 | 2.9343 | 41.954 | 42.0914 | 42.3248 | 41.9037 | 41.8533 | 8.7708 | 8.67 | 84.3292 | 84.1644 | -38.5986 | 84.5078 | 84.4391 | 0.27466 | -38.6581 | 90.0009 | 89.9002 | 0.036622 | 123.1842 | 123.555 | 33.6548 | -0.013732 | 84.4986 | 84.4391 | 84.375 | -38.9328 | 123.1339 | 123.0835 | 123.3215 | -33.197
1973.5156 | 123.2025 | -81.2302 | 41.9266 | -0.17853 | 0.012245 | 0.0034991 | 0.014531 | -0.019339 | 0.001694 | 0.0021255 | -0.17983 | 0.019807 | -0.012995 | 0.015272 | -0.0025036 | 0.012134 | 3.1219 | 3.1403 | 3.0304 | 3.1128 | 3.3096 | 3.0487 | 2.8839 | 41.8121 | 41.9449 | 41.9312 | 41.9128 | 41.8076 | 8.7799 | 8.67 | 84.2789 | 84.1141 | -38.6169 | 84.3704 | 84.343 | 0.22888 | -38.8046 | 90.0101 | 89.9002 | -0.013733 | 123.0423 | 123.1613 | 33.2611 | -0.11902 | 84.5398 | 84.3521 | 84.2606 | -39.0427 | 123.143 | 123.0377 | 123.175 | -33.2565
1974.5156 | 123.3765 | -81.2531 | 41.8167 | -0.12512 | 0.0086133 | 0.0041401 | 0.010685 | -0.019766 | -0.0019376 | 0.0029801 | 0.049057 | 0.01938 | -0.013849 | 0.01399 | -0.00229 | 0.010425 | 3.1677 | 3.2593 | 3.0853 | 2.98 | 3.2135 | 3.0212 | 2.8473 | 41.922 | 41.9907 | 42.0273 | 41.8213 | 41.7618 | 8.7753 | 8.67 | 84.2743 | 84.1003 | -38.6032 | 84.5123 | 84.2331 | 0.13275 | -38.649 | 90.0284 | 89.9231 | 0.004578 | 123.175 | 123.2803 | 33.3572 | -0.054931 | 84.4666 | 84.4208 | 84.3384 | -38.9694 | 123.0743 | 123.0148 | 123.2437 | -33.1467
1975.5156 | 123.2758 | -81.2851 | 41.8533 | -0.20905 | 0.0090405 | 0.0020037 | 0.013035 | -0.020194 | 0.0019078 | 0.0012711 | -0.18745 | 0.020448 | -0.011286 | 0.014631 | -0.0027172 | 0.013202 | 3.1082 | 3.1906 | 3.0624 | 3.1219 | 3.2318 | 3.0167 | 2.8748 | 41.8533 | 41.9861 | 41.9449 | 41.8762 | 41.7755 | 8.7753 | 8.6792 | 84.3018 | 84.1599 | -38.6215 | 84.4757 | 84.407 | 0.24719 | -38.7451 | 90.0604 | 89.9643 | 0.022888 | 123.1384 | 123.23 | 33.2657 | -0.07782 | 84.5169 | 84.3933 | 84.3475 | -38.9786 | 123.1613 | 123.0606 | 123.2712 | -33.1741
1976.5156 | 123.4131 | -81.2164 | 41.8442 | -0.048828 | 0.0064771 | 0.0041401 | 0.012181 | -0.021689 | -0.0023648 | 0.0021255 | -0.042496 | 0.018312 | -0.011072 | 0.015486 | -0.0048534 | 0.011066 | 3.1631 | 3.2272 | 3.0991 | 3.154 | 3.2272 | 3.0533 | 2.8793 | 41.9632 | 42.0685 | 42.0593 | 41.835 | 41.7709 | 8.7708 | 8.6746 | 84.2697 | 84.0958 | -38.6169 | 84.4437 | 84.3704 | 0.27466 | -38.681 | 89.9872 | 89.8911 | -0.009155 | 123.1796 | 123.2758 | 33.3847 | -0.073242 | 84.4437 | 84.3796 | 84.3155 | -38.9648 | 123.0515 | 122.9874 | 123.2849 | -33.1696
1977.5156 | 123.3536 | -81.2668 | 41.835 | -0.12512 | 0.0098951 | 0.0034991 | 0.011967 | -0.019553 | -0.0034328 | 0.00041648 | -0.18745 | 0.019807 | -0.011499 | 0.013777 | -0.003999 | 0.011279 | 3.1494 | 3.2089 | 3.1036 | 3.1586 | 3.2135 | 3.0258 | 2.8839 | 41.8991 | 42.0319 | 42.0044 | 41.8396 | 41.7526 | 8.7708 | 8.67 | 84.2926 | 84.1507 | -38.6215 | 84.4757 | 84.4254 | 0.27466 | -38.6856 | 90.0375 | 89.9368 | 0.004578 | 123.1659 | 123.2712 | 33.3344 | -0.082397 | 84.4803 | 84.4162 | 84.3704 | -38.9511 | 123.1064 | 123.0194 | 123.2986 | -33.165
1978.5156 | 123.3307 | -81.2943 | 41.7892 | -0.49896 | 0.0083997 | 0.0039263 | 0.012608 | -0.020621 | -0.00086945 | 0.0025529 | 0.041427 | 0.01938 | -0.014063 | 0.014417 | -0.0042126 | 0.012988 | 3.0808 | 3.0899 | 2.9984 | 3.0716 | 3.1723 | 2.9892 | 2.8107 | 41.8304 | 41.9312 | 41.954 | 41.8259 | 41.7389 | 8.7708 | 8.67 | 84.2834 | 84.1049 | -38.6169 | 84.3842 | 84.3658 | 0.26093 | -38.7085 | 90.065 | 89.9643 | 0.036621 | 123.1247 | 123.2483 | 33.284 | -0.050354 | 84.4666 | 84.375 | 84.2926 | -38.9786 | 123.1201 | 123.0331 | 123.2254 | -33.1192
1979.5156 | 123.3902 | -81.2805 | 41.7755 | -0.086975 | 0.0079723 | 0.0043537 | 0.014103 | -0.01763 | -0.0015102 | -1.0724e-05 | -0.38582 | 0.017457 | -0.01449 | 0.013349 | -0.0044262 | 0.012561 | 3.3966 | 3.1128 | 2.861 | 2.98 | 3.186 | 3.0167 | 2.8381 | 41.9174 | 42.0319 | 42.0044 | 41.803 | 41.716 | 8.7891 | 8.6746 | 84.2972 | 84.1187 | -38.5895 | 84.3933 | 84.2606 | 0.14191 | -38.3789 | 90.0696 | 89.9551 | 0.027466 | 123.1979 | 123.2849 | 33.3298 | -0.05951 | 84.4666 | 84.6771 | 84.1415 | -38.9374 | 123.0835 | 122.9965 | 123.3124 | -33.1009
1980.5156 | 123.381 | -81.2897 | 41.7938 | 0.042725 | 0.0075451 | 0.0024311 | 0.011754 | -0.019766 | -0.00086945 | 0.0021255 | -0.019608 | 0.016176 | -0.0095768 | 0.013563 | -0.0046398 | 0.011279 | 3.0945 | 3.154 | 3.0579 | 3.1311 | 3.1952 | 3.0304 | 2.8381 | 41.9083 | 41.9861 | 41.9952 | 41.8121 | 41.7252 | 8.7799 | 8.6746 | 84.3201 | 84.1278 | -38.5986 | 84.4437 | 84.4208 | 0.29297 | -38.6993 | 90.0696 | 89.9643 | 0.018311 | 123.1979 | 123.2849 | 33.3206 | -0.068664 | 84.4849 | 84.3842 | 84.3475 | -38.9557 | 123.1018 | 123.0148 | 123.2758 | -33.1192
1981.5156 | 123.3902 | -81.3263 | 41.7709 | -0.15564 | 0.0047681 | 0.0067035 | 0.015172 | -0.022116 | 0.0025486 | 0.0031937 | -0.2256 | 0.017884 | -0.012781 | 0.013136 | -0.0033582 | 0.010852 | 3.1494 | 3.1723 | 3.0121 | 3.0853 | 3.1723 | 3.0075 | 2.8336 | 41.8579 | 41.9861 | 41.954 | 41.7664 | 41.629 | 8.7753 | 8.6746 | 84.3338 | 84.1599 | -38.5986 | 84.4986 | 84.4116 | 0.25177 | -38.6215 | 90.1016 | 90.0009 | -0.004578 | 123.1842 | 123.2803 | 33.2794 | -0.14191 | 84.4986 | 84.4757 | 84.3384 | -38.9374 | 123.0927 | 122.9553 | 123.3124 | -33.0963
1982.5156 | 123.3536 | -81.3721 | 41.748 | 0.31738 | 0.0090405 | 0.0028583 | 0.01154 | -0.022757 | -1.505e-05 | 0.0014847 | 0.079574 | 0.015748 | -0.014063 | 0.013349 | -0.0037854 | 0.012347 | 3.0258 | 3.0899 | 2.9984 | 3.0533 | 3.1723 | 2.9617 | 2.8244 | 41.7938 | 41.8854 | 41.89 | 41.748 | 41.6565 | 8.7799 | 8.6746 | 84.3338 | 84.1965 | -38.5757 | 84.462 | 84.4254 | 0.22888 | -38.7222 | 90.152 | 90.0467 | 0 | 123.1659 | 123.262 | 33.2153 | -0.091553 | 84.5444 | 84.3979 | 84.3704 | -38.9236 | 123.1201 | 123.0286 | 123.2574 | -33.0734
1983.5156 | 123.3948 | -81.4133 | 41.6931 | -0.071716 | 0.0086133 | 0.0032855 | 0.013035 | -0.019766 | 0.00062595 | 0.00041648 | -0.057755 | 0.017671 | -0.014917 | 0.013349 | -0.003999 | 0.010638 | 3.1128 | 3.1723 | 3.0396 | 3.0945 | 3.1815 | 3.0075 | 2.8336 | 41.8167 | 41.8945 | 41.8991 | 41.6702 | 41.5833 | 8.7753 | 8.6792 | 84.4208 | 84.2468 | -38.5117 | 84.5856 | 84.5078 | 0.26093 | -38.5803 | 90.1886 | 90.0925 | -0.022888 | 123.23 | 123.3124 | 33.2199 | -0.10986 | 84.5947 | 84.5261 | 84.4528 | -38.8596 | 123.0835 | 122.9965 | 123.3078 | -33.0139
1984.5156 | 123.3536 | -81.3583 | 41.7068 | 0.14191 | 0.01139 | 0.0039263 | 0.010045 | -0.01998 | 0.0012668 | 0.0034073 | 0.19402 | 0.017671 | -0.013422 | 0.013136 | -0.0031446 | 0.0099975 | 3.0762 | 3.1219 | 3.0075 | 3.0441 | 3.1265 | 2.9755 | 2.7969 | 41.8076 | 41.8625 | 41.8671 | 41.7206 | 41.597 | 8.7753 | 8.6746 | 84.3338 | 84.1553 | -38.5803 | 84.4803 | 84.4025 | 0.24719 | -38.6307 | 90.1337 | 90.033 | 0.013733 | 123.1659 | 123.2254 | 33.1924 | -0.10986 | 84.4849 | 84.4345 | 84.3658 | -38.9099 | 123.0789 | 122.9553 | 123.2208 | -33.0322
1985.5156 | 123.3444 | -81.3858 | 41.7252 | 0.09613 | 0.0062635 | 0.0026447 | 0.011967 | -0.019766 | 0.0012668 | 0.0036209 | -0.29427 | 0.017244 | -0.01449 | 0.012922 | -0.0042126 | 0.012347 | 2.9205 | 3.1128 | 2.9526 | 2.9343 | 3.1128 | 2.9388 | 2.7649 | 41.7664 | 41.8488 | 41.8533 | 41.6931 | 41.6428 | 8.7753 | 8.67 | 84.3246 | 84.1507 | -38.6124 | 84.4986 | 84.3201 | 0.16937 | -38.8046 | 90.1611 | 90.0558 | -0.032044 | 123.1522 | 123.2391 | 33.1833 | -0.082398 | 84.4986 | 84.3063 | 84.3384 | -38.9603 | 123.0789 | 123.0286 | 123.2346 | -33.0551
1986.5156 | 123.3582 | -81.3812 | 41.6794 | 0.14954 | 0.01139 | 0.0032855 | 0.013035 | -0.019553 | 0.001694 | 0.0019119 | 0.20164 | 0.019166 | -0.012995 | 0.015272 | -0.0031446 | 0.012347 | 3.0762 | 3.1174 | 3.0121 | 3.067 | 3.1357 | 2.9663 | 2.8015 | 41.7984 | 41.8304 | 41.8533 | 41.6748 | 41.6061 | 8.7799 | 8.6746 | 84.3475 | 84.1827 | -38.5437 | 84.4986 | 84.4482 | 0.2655 | -38.6032 | 90.1611 | 90.0558 | -0.004577 | 123.1796 | 123.2346 | 33.1787 | -0.073242 | 84.5169 | 84.4574 | 84.3933 | -38.8779 | 123.056 | 122.9874 | 123.2117 | -33.0048
1987.5156 | 123.3719 | -81.3766 | 41.6977 | 0.050354 | 0.0047681 | 0.0032855 | 0.011967 | -0.019126 | -0.0034328 | 0.0036209 | 0.0032804 | 0.020875 | -0.012995 | 0.013136 | -0.0042126 | 0.011493 | 3.0304 | 3.0945 | 2.9984 | 3.0579 | 3.1631 | 2.9572 | 2.8015 | 41.7709 | 41.8762 | 41.89 | 41.7068 | 41.6245 | 8.7753 | 8.67 | 84.3338 | 84.1782 | -38.5345 | 84.4711 | 84.4345 | 0.25635 | -38.6673 | 90.152 | 90.0467 | 0.009155 | 123.1476 | 123.2666 | 33.2199 | -0.073242 | 84.5398 | 84.407 | 84.375 | -38.8962 | 123.0835 | 123.0011 | 123.2529 | -33.0276
1988.5156 | 123.3353 | -81.4865 | 41.5924 | 0.14954 | 0.01139 | 0.0041401 | 0.01154 | -0.018485 | 0.0021214 | 0.0034073 | 0.19402 | 0.01938 | -0.013636 | 0.012495 | -0.0027172 | 0.01192 | 3.0487 | 3.0945 | 2.9617 | 3.0258 | 3.1036 | 2.9388 | 2.7649 | 41.716 | 41.7526 | 41.7847 | 41.6199 | 41.5375 | 8.7799 | 8.6746 | 84.4254 | 84.2514 | -38.4888 | 84.581 | 84.5123 | 0.26093 | -38.5437 | 90.2664 | 90.1611 | 0.027466 | 123.2025 | 123.2712 | 33.11 | -0.054931 | 84.5901 | 84.5352 | 84.4482 | -38.8275 | 123.1064 | 123.024 | 123.2391 | -32.9178
1989.5156 | 123.3398 | -81.4407 | 41.684 | 0.10376 | 0.0056225 | 0.0020037 | 0.011754 | -0.023184 | 0.00062595 | 0.0040481 | 0.2169 | 0.018953 | -0.010431 | 0.013777 | -0.0031446 | 0.011707 | 2.9938 | 3.0624 | 2.8931 | 2.948 | 3.1128 | 2.9297 | 2.7557 | 41.7343 | 41.8076 | 41.835 | 41.6931 | 41.6199 | 8.7753 | 8.6746 | 84.3704 | 84.1965 | -38.5712 | 84.5032 | 84.3887 | 0.19226 | -38.6902 | 90.2161 | 90.1154 | 0.009155 | 123.175 | 123.2758 | 33.1604 | -0.064087 | 84.5535 | 84.4345 | 84.3338 | -38.9282 | 123.1338 | 123.0606 | 123.2483 | -33.0093
1990.5156 | 123.3765 | -81.4133 | 41.6702 | 0.24872 | 0.013099 | 0.0020037 | 0.0096174 | -0.017417 | -0.00022865 | 0.0025529 | 0.22453 | 0.018739 | -0.011927 | 0.012708 | -0.0012218 | 0.011066 | 3.1769 | 3.035 | 2.9526 | 3.0258 | 3.0396 | 2.8885 | 2.7237 | 41.8259 | 41.8671 | 41.8762 | 41.6702 | 41.5741 | 8.7845 | 8.67 | 84.3018 | 84.137 | -38.6307 | 84.4482 | 84.4391 | 0.30212 | -38.4933 | 90.1978 | 90.0833 | 0 | 123.2391 | 123.2895 | 33.2062 | -0.09613 | 84.4528 | 84.5901 | 84.3658 | -38.9465 | 123.0835 | 122.9874 | 123.2803 | -33.0002
1991.5156 | 123.349 | -81.4545 | 41.6107 | 0.14954 | 0.010109 | 0.0034991 | 0.011967 | -0.022757 | 0.0010532 | 0.0049027 | 0.18639 | 0.018739 | -0.013636 | 0.014845 | -0.0020764 | 0.013843 | 3.0167 | 3.0533 | 2.9388 | 3.0075 | 3.0853 | 2.9022 | 2.7557 | 41.7206 | 41.7618 | 41.7709 | 41.6153 | 41.5558 | 8.7799 | 8.6792 | 84.3567 | 84.2102 | -38.5254 | 84.5078 | 84.462 | 0.25177 | -38.5941 | 90.2344 | 90.1337 | 0.004577 | 123.175 | 123.2254 | 33.0917 | -0.054932 | 84.5398 | 84.4711 | 84.3933 | -38.855 | 123.0698 | 123.0103 | 123.2162 | -32.9315
1992.5156 | 123.2803 | -81.4728 | 41.6199 | 0.15717 | 0.015449 | 0.0037127 | 0.014317 | -0.018698 | 0.0055392 | 0.0029801 | 0.094833 | 0.018953 | -0.011499 | 0.014631 | 5.9768e-05 | 0.011279 | 2.9343 | 2.8976 | 2.7924 | 2.8931 | 3.0853 | 2.8564 | 2.6779 | 41.6611 | 41.6977 | 41.7068 | 41.6656 | 41.5512 | 8.7753 | 8.6746 | 84.3292 | 84.1507 | -38.5345 | 84.3704 | 84.3658 | 0.21515 | -38.6856 | 90.2481 | 90.1474 | 0.045776 | 123.1338 | 123.1796 | 33.0322 | -0.068665 | 84.5581 | 84.407 | 84.2651 | -38.942 | 123.1384 | 123.024 | 123.1705 | -32.9453
1993.5156 | 123.349 | -81.4682 | 41.597 | 0.13428 | 0.011818 | 0.0022175 | 0.011326 | -0.021689 | -0.00086945 | 0.0025529 | 0.19402 | 0.018739 | -0.012781 | 0.013563 | -0.003999 | 0.014697 | 2.9617 | 3.0075 | 2.9068 | 2.9297 | 3.035 | 2.8473 | 2.6917 | 41.6931 | 41.748 | 41.7572 | 41.6107 | 41.5329 | 8.7799 | 8.67 | 84.3155 | 84.1599 | -38.562 | 84.4757 | 84.3979 | 0.23804 | -38.6353 | 90.2481 | 90.1382 | 0.013733 | 123.1613 | 123.2254 | 33.0872 | -0.064087 | 84.5032 | 84.4299 | 84.375 | -38.9053 | 123.0789 | 123.0011 | 123.2162 | -32.9269
1994.5156 | 123.3582 | -81.5048 | 41.5833 | 0.24872 | 0.01374 | 0.0022175 | 0.012822 | -0.020835 | 0.002335 | 0.0023391 | 0.14061 | 0.019593 | -0.014063 | 0.01399 | -0.0027172 | 0.010852 | 2.9114 | 2.8931 | 2.8107 | 2.8793 | 3.0441 | 2.8198 | 2.6459 | 41.6748 | 41.7252 | 41.7343 | 41.6153 | 41.5054 | 8.7708 | 8.6792 | 84.3246 | 84.1507 | -38.5391 | 84.3979 | 84.3842 | 0.23346 | -38.6719 | 90.2756 | 90.184 | 0.032043 | 123.1796 | 123.2391 | 33.0551 | -0.07782 | 84.549 | 84.4162 | 84.3155 | -38.9374 | 123.1201 | 123.0103 | 123.23 | -32.9041
1995.5156 | 123.3719 | -81.4819 | 41.5741 | -0.78125 | 0.010536 | 0.0022175 | 0.010685 | -0.019339 | -0.0012966 | 0.0051163 | 0.19402 | 0.019593 | -0.011713 | 0.012708 | -0.0016492 | 0.012134 | 2.9297 | 2.9846 | 2.8748 | 2.9297 | 2.9755 | 2.8152 | 2.655 | 41.7068 | 41.7801 | 41.8121 | 41.6016 | 41.5192 | 8.7845 | 8.67 | 84.2972 | 84.137 | -38.5986 | 84.4666 | 84.4116 | 0.27466 | -38.6444 | 90.2664 | 90.152 | 0.027465 | 123.1888 | 123.2941 | 33.1421 | -0.054932 | 84.4574 | 84.4116 | 84.3567 | -38.9191 | 123.0835 | 123.0011 | 123.262 | -32.9041
1996.5156 | 123.2895 | -81.5369 | 41.6199 | 0.27924 | 0.015877 | 0.0028583 | 0.014103 | -0.018912 | 0.003403 | 0.0038345 | 0.12535 | 0.021516 | -0.0097904 | 0.015699 | -0.00015383 | 0.0097839 | 2.8748 | 2.829 | 2.7466 | 2.861 | 3.035 | 2.8015 | 2.6276 | 41.6199 | 41.6702 | 41.6748 | 41.6611 | 41.5787 | 8.7753 | 8.6792 | 84.3384 | 84.1644 | -38.5849 | 84.3658 | 84.3979 | 0.23346 | -38.7451 | 90.3122 | 90.2161 | 0.041199 | 123.1567 | 123.2117 | 32.9956 | -0.041199 | 84.5718 | 84.4116 | 84.2834 | -38.9923 | 123.1979 | 123.1155 | 123.2071 | -32.9407
1997.5156 | 123.3719 | -81.4774 | 41.5833 | 0.21057 | 0.01609 | 0.0020037 | 0.013249 | -0.018912 | 0.0014804 | 0.0066117 | 0.18639 | 0.019593 | -0.011713 | 0.015272 | -0.00079463 | 0.012347 | 2.9022 | 2.9114 | 2.8336 | 2.8931 | 2.9755 | 2.8198 | 2.655 | 41.716 | 41.7709 | 41.7938 | 41.6153 | 41.51 | 8.7708 | 8.67 | 84.2972 | 84.1324 | -38.6078 | 84.3887 | 84.3704 | 0.23804 | -38.681 | 90.2481 | 90.1474 | 0.032043 | 123.1934 | 123.2712 | 33.1238 | -0.073242 | 84.4528 | 84.3796 | 84.3109 | -38.9282 | 123.0927 | 122.9874 | 123.2483 | -32.9132
1998.5156 | 123.262 | -81.5735 | 41.5695 | 0.027466 | 0.018654 | 0.0026447 | 0.011326 | -0.018912 | 0.005112 | 0.0051163 | -0.027237 | 0.021943 | -0.0085086 | 0.013136 | -0.0016492 | 0.011707 | 2.8839 | 2.8519 | 2.7466 | 2.8656 | 3.0304 | 2.7924 | 2.6413 | 41.5649 | 41.6473 | 41.6107 | 41.5924 | 41.51 | 8.7753 | 8.67 | 84.3658 | 84.2148 | -38.5391 | 84.4254 | 84.4391 | 0.2243 | -38.6856 | 90.3488 | 90.2435 | 0.022888 | 123.1384 | 123.1842 | 32.9407 | -0.059509 | 84.6039 | 84.4574 | 84.3201 | -38.9282 | 123.1659 | 123.0835 | 123.2208 | -32.8995
1999.5156 | 123.3856 | -81.5643 | 41.5375 | 0.24872 | 0.015877 | 0.00050849 | 0.0096174 | -0.018485 | 0.0010532 | 0.0055435 | 0.17113 | 0.020021 | -0.012567 | 0.014631 | -0.0016492 | 0.012561 | 2.8656 | 2.8885 | 2.7969 | 2.8931 | 2.9617 | 2.7878 | 2.6093 | 41.6428 | 41.7206 | 41.7297 | 41.5558 | 41.4505 | 8.7753 | 8.6746 | 84.3521 | 84.1736 | -38.5757 | 84.4528 | 84.4574 | 0.28381 | -38.6719 | 90.3397 | 90.239 | 0.01831 | 123.2071 | 123.2941 | 33.0551 | -0.086976 | 84.5261 | 84.4299 | 84.3613 | -38.9282 | 123.1201 | 123.0148 | 123.2849 | -32.8629
2000.5156 | 123.2758 | -81.5598 | 41.5741 | 0.088501 | 0.015877 | 0.0024311 | 0.014958 | -0.018271 | 0.0010532 | 0.0036209 | 0.1635 | 0.020021 | -0.010218 | 0.013349 | -0.00015383 | 0.01192 | 2.8198 | 2.7924 | 2.7054 | 2.8061 | 2.9938 | 2.774 | 2.5681 | 41.5833 | 41.629 | 41.6382 | 41.597 | 41.5283 | 8.7753 | 8.6746 | 84.3338 | 84.1278 | -38.5803 | 84.3521 | 84.3658 | 0.23804 | -38.7543 | 90.3351 | 90.2344 | 0.022888 | 123.143 | 123.1979 | 32.9636 | -0.045777 | 84.5535 | 84.3796 | 84.2651 | -39.006 | 123.1567 | 123.0881 | 123.1888 | -32.8995
2001.5156 | 123.3215 | -81.5552 | 41.5695 | 0.18768 | 0.014595 | 0.0026447 | 0.011967 | -0.01998 | 0.0038304 | 0.0034073 | 0.18639 | 0.019166 | -0.011072 | 0.013136 | -0.0027172 | 0.013202 | 2.7969 | 2.8061 | 2.7008 | 2.8107 | 2.9846 | 2.7649 | 2.5909 | 41.5878 | 41.6702 | 41.6702 | 41.5878 | 41.5146 | 8.7753 | 8.6746 | 84.3201 | 84.1461 | -38.5849 | 84.3613 | 84.3658 | 0.21973 | -38.7726 | 90.3305 | 90.2298 | 0.018311 | 123.143 | 123.2254 | 32.9956 | -0.054932 | 84.5398 | 84.3521 | 84.256 | -38.9786 | 123.143 | 123.0698 | 123.2254 | -32.8949
2002.5156 | 123.2666 | -81.5781 | 41.5466 | 0.050354 | 0.016945 | 0.00093569 | 0.015385 | -0.019766 | 0.003403 | 0.0053299 | 0.026169 | 0.022371 | -0.013636 | 0.012495 | -0.00079463 | 0.014697 | 2.8061 | 2.7969 | 2.71 | 2.7924 | 2.9709 | 2.742 | 2.5864 | 41.5329 | 41.6107 | 41.5924 | 41.5741 | 41.5192 | 8.7753 | 8.67 | 84.3201 | 84.1644 | -38.5757 | 84.375 | 84.3704 | 0.20599 | -38.7405 | 90.3534 | 90.2481 | 0.027466 | 123.111 | 123.1705 | 32.9224 | -0.027466 | 84.5489 | 84.3842 | 84.288 | -38.9603 | 123.1522 | 123.0972 | 123.1888 | -32.8766
2003.5156 | 123.2803 | -81.5598 | 41.5787 | 3.6285 | 0.017799 | 0.0026447 | 0.015812 | -0.017844 | 0.0014804 | 0.0025529 | 0.11772 | 0.020448 | -0.0085086 | 0.01399 | -0.00079463 | 0.012134 | 2.8107 | 2.742 | 2.6367 | 2.7786 | 2.98 | 2.7328 | 2.5635 | 41.5604 | 41.6153 | 41.629 | 41.6061 | 41.5466 | 8.7753 | 8.6746 | 84.2926 | 84.1232 | -38.5986 | 84.3018 | 84.3384 | 0.21515 | -38.768 | 90.3351 | 90.2344 | 0.027466 | 123.1201 | 123.1888 | 32.9544 | -0.032043 | 84.5398 | 84.3704 | 84.1965 | -39.0152 | 123.1659 | 123.1064 | 123.175 | -32.9041
2004.5156 | 123.2895 | -81.6147 | 41.5512 | -0.14038 | 0.016945 | 0.00093569 | 0.014103 | -0.017203 | 0.0042576 | 0.0051163 | -0.042496 | 0.020234 | -0.0087222 | 0.014845 | -0.0029308 | 0.012775 | 2.8381 | 2.8061 | 2.7145 | 2.8061 | 2.9251 | 2.7374 | 2.5726 | 41.5466 | 41.6428 | 41.629 | 41.5604 | 41.4917 | 8.7753 | 8.67 | 84.3521 | 84.1873 | -38.6261 | 84.4208 | 84.4208 | 0.23346 | -38.7131 | 90.39 | 90.2847 | 0.009156 | 123.1613 | 123.2437 | 32.959 | -0.059509 | 84.5398 | 84.4528 | 84.3292 | -38.9786 | 123.175 | 123.1064 | 123.2574 | -32.8812
2005.5156 | 123.2437 | -81.6788 | 41.5192 | 0.09613 | 0.017799 | 0.0026447 | 0.014531 | -0.019766 | 0.0025486 | 0.0031937 | 0.11009 | 0.022584 | -0.011072 | 0.013136 | -0.0029308 | 0.013202 | 2.7374 | 2.7054 | 2.6459 | 2.774 | 2.9434 | 2.71 | 2.5497 | 41.4322 | 41.5192 | 41.5237 | 41.5283 | 41.478 | 8.7753 | 8.6655 | 84.3887 | 84.2285 | -38.5757 | 84.3842 | 84.4528 | 0.2243 | -38.7817 | 90.4541 | 90.3442 | 0.009155 | 123.111 | 123.2025 | 32.8583 | -0.041199 | 84.6222 | 84.4162 | 84.3246 | -38.9694 | 123.2071 | 123.1567 | 123.1979 | -32.8537
2006.5156 | 123.317 | -81.6605 | 41.5283 | -0.15564 | 0.014808 | 0.0017901 | 0.010685 | -0.018485 | -1.505e-05 | 0.0034073 | -0.17983 | 0.020021 | -0.010858 | 0.014631 | -0.0031446 | 0.011707 | 2.742 | 2.7512 | 2.6642 | 2.7786 | 2.9434 | 2.7145 | 2.5314 | 41.5009 | 41.6199 | 41.6061 | 41.5146 | 41.4963 | 8.7799 | 8.6746 | 84.375 | 84.1919 | -38.5849 | 84.4116 | 84.4391 | 0.24719 | -38.7863 | 90.4404 | 90.3351 | -0.013733 | 123.1613 | 123.2666 | 32.9315 | -0.032043 | 84.6039 | 84.4025 | 84.3246 | -38.9969 | 123.175 | 123.1567 | 123.2803 | -32.8537
2007.5156 | 123.2346 | -81.6925 | 41.4963 | 0.057983 | 0.016731 | 0.0037127 | 0.013676 | -0.020407 | 0.003403 | 0.0038345 | 0.056686 | 0.019807 | -0.012567 | 0.014631 | -0.0020764 | 0.012347 | 2.6962 | 2.6779 | 2.6093 | 2.7237 | 2.916 | 2.6733 | 2.5131 | 41.4139 | 41.5054 | 41.4871 | 41.5192 | 41.4413 | 8.7753 | 8.6792 | 84.3658 | 84.2056 | -38.5803 | 84.3704 | 84.4162 | 0.21057 | -38.8 | 90.4678 | 90.3717 | 0.022888 | 123.1064 | 123.1796 | 32.8079 | -0.054932 | 84.6085 | 84.3887 | 84.3018 | -38.9832 | 123.2117 | 123.1338 | 123.1979 | -32.8171
2008.5156 | 123.3078 | -81.6055 | 41.5649 | -0.15564 | 0.016945 | 8.1086e-05 | 0.015812 | -0.01998 | 0.00083955 | 0.0044755 | -0.11116 | 0.020662 | -0.011286 | 0.016554 | -0.00229 | 0.0093567 | 2.7878 | 2.774 | 2.6871 | 2.7878 | 2.9343 | 2.6871 | 2.5223 | 41.5375 | 41.6519 | 41.5375 | 41.5466 | 41.4734 | 8.7708 | 8.67 | 84.2926 | 84.1278 | -38.6307 | 84.3796 | 84.3933 | 0.2655 | -38.7772 | 90.3763 | 90.2756 | -0.01831 | 123.143 | 123.143 | 32.8674 | -0.091552 | 84.5398 | 84.3933 | 84.2926 | -39.0427 | 123.1522 | 123.0789 | 123.2574 | -32.8949
2009.5156 | 123.2666 | -81.6422 | 41.5375 | -0.056458 | 0.016517 | 0.0041401 | 0.012822 | -0.019766 | 0.0012668 | 0.0046891 | 0.079574 | 0.021089 | -0.010431 | 0.012495 | -0.0010082 | 0.012134 | 2.7466 | 2.7466 | 2.6505 | 2.7328 | 2.9114 | 2.6688 | 2.5085 | 41.51 | 41.5833 | 41.5924 | 41.5604 | 41.4734 | 8.7799 | 8.67 | 84.3109 | 84.1507 | -38.6261 | 84.3887 | 84.375 | 0.2243 | -38.7909 | 90.4221 | 90.3122 | 0.022888 | 123.1522 | 123.2346 | 32.9224 | -0.064087 | 84.5535 | 84.3887 | 84.2926 | -39.0289 | 123.2025 | 123.1155 | 123.2254 | -32.8674
2010.5156 | 123.3032 | -81.6834 | 41.4963 | -0.12512 | 0.013099 | 0.0020037 | 0.012608 | -0.019339 | 0.0012668 | 0.00063028 | -0.12642 | 0.019593 | -0.011286 | 0.014845 | -0.0042126 | 0.012988 | 2.71 | 2.6962 | 2.623 | 2.7283 | 2.8931 | 2.6413 | 2.4857 | 41.4459 | 41.5878 | 41.5604 | 41.5054 | 41.4413 | 8.7799 | 8.6792 | 84.3246 | 84.169 | -38.6032 | 84.3796 | 84.4116 | 0.24261 | -38.7863 | 90.4633 | 90.3625 | 0.009155 | 123.1293 | 123.2437 | 32.8812 | -0.054932 | 84.5764 | 84.3933 | 84.3063 | -39.0106 | 123.1888 | 123.1247 | 123.2712 | -32.8171
2011.5156 | 123.3078 | -81.6788 | 41.4871 | -0.064087 | 0.015449 | 0.0015765 | 0.014317 | -0.018057 | 0.0025486 | 0.0046891 | 0.094833 | 0.018525 | -0.0091494 | 0.014417 | -0.0029308 | 0.013416 | 2.861 | 2.742 | 2.6825 | 2.8564 | 2.9205 | 2.7145 | 2.5269 | 41.5146 | 41.597 | 41.5878 | 41.5329 | 41.4551 | 8.7753 | 8.67 | 84.3933 | 84.2056 | -38.5666 | 84.4208 | 84.5352 | 0.32959 | -38.6261 | 90.4541 | 90.3488 | 0.045776 | 123.1934 | 123.2666 | 32.9178 | -0.032044 | 84.5993 | 84.5398 | 84.3613 | -38.9603 | 123.2117 | 123.1338 | 123.2758 | -32.8171
2012.5156 | 123.262 | -81.7383 | 41.4917 | -0.17853 | 0.01075 | 0.00050849 | 0.011967 | -0.019766 | -0.0030056 | 0.0019119 | -0.20271 | 0.017884 | -0.013849 | 0.013563 | -0.0054944 | 0.012561 | 2.71 | 2.7649 | 2.6688 | 2.7512 | 2.8885 | 2.6733 | 2.504 | 41.4093 | 41.5421 | 41.5375 | 41.4871 | 41.4093 | 8.7799 | 8.6746 | 84.4116 | 84.2422 | -38.6032 | 84.5032 | 84.4894 | 0.24719 | -38.7817 | 90.5182 | 90.4129 | -0.004577 | 123.1476 | 123.2758 | 32.8629 | -0.082397 | 84.6268 | 84.4482 | 84.407 | -38.9877 | 123.2254 | 123.1476 | 123.2803 | -32.8171
2013.5156 | 123.2803 | -81.7017 | 41.4597 | -0.14801 | 0.012031 | 0.0039263 | 0.015172 | -0.015921 | -0.00086945 | 0.0025529 | -0.095902 | 0.021516 | -0.0091494 | 0.01399 | -0.0046398 | 0.012988 | 2.6917 | 2.7191 | 2.6276 | 2.7237 | 2.9068 | 2.6505 | 2.4765 | 41.4001 | 41.5375 | 41.5192 | 41.4871 | 41.423 | 8.7845 | 8.6838 | 84.3521 | 84.1782 | -38.5529 | 84.4208 | 84.4254 | 0.24719 | -38.768 | 90.4861 | 90.3854 | 0.027466 | 123.1018 | 123.2208 | 32.8354 | -0.036621 | 84.6085 | 84.3933 | 84.3292 | -38.9832 | 123.1888 | 123.1247 | 123.2391 | -32.7759
2014.5156 | 123.2712 | -81.7429 | 41.4963 | -0.23956 | 0.0098951 | 0.0022175 | 0.012822 | -0.01763 | -0.0030056 | 0.00041648 | -0.19508 | 0.020448 | -0.010218 | 0.012068 | -0.0037854 | 0.013416 | 2.9022 | 2.5452 | 2.5131 | 2.7008 | 2.9617 | 2.6917 | 2.5131 | 41.4093 | 41.51 | 41.5237 | 41.4688 | 41.4185 | 8.7799 | 8.67 | 84.4345 | 84.256 | -38.5345 | 84.288 | 84.4437 | 0.18768 | -38.5941 | 90.5228 | 90.4129 | -0.027466 | 123.1522 | 123.2666 | 32.8537 | -0.07782 | 84.7046 | 84.6451 | 84.256 | -38.9832 | 123.2117 | 123.1613 | 123.2529 | -32.8262
2015.5156 | 123.3078 | -81.6879 | 41.4551 | -0.13275 | 0.014381 | 0.00072209 | 0.014744 | -0.019766 | 0.0027622 | 0.0023391 | -0.14931 | 0.016816 | -0.011499 | 0.012281 | -0.0025036 | 0.010425 | 2.655 | 2.6871 | 2.5818 | 2.7054 | 2.8656 | 2.6413 | 2.4445 | 41.4413 | 41.5649 | 41.5558 | 41.4917 | 41.3864 | 8.7753 | 8.6792 | 84.3292 | 84.1324 | -38.5895 | 84.375 | 84.3933 | 0.26092 | -38.8 | 90.4633 | 90.3671 | 0.036621 | 123.1293 | 123.2437 | 32.8766 | -0.068664 | 84.5535 | 84.343 | 84.2697 | -39.0106 | 123.1796 | 123.0743 | 123.2529 | -32.7759
2016.5156 | 123.3536 | -81.7108 | 41.4001 | 0.20294 | 0.015022 | 0.00029489 | 0.013249 | -0.020621 | 0.0010532 | 0.0046891 | 0.20164 | 0.018953 | -0.011286 | 0.015699 | -0.003999 | 0.01427 | 2.6505 | 2.6688 | 2.5681 | 2.6459 | 2.8198 | 2.6138 | 2.4307 | 41.4459 | 41.5054 | 41.5375 | 41.4413 | 41.3498 | 8.7708 | 8.6792 | 84.3246 | 84.1415 | -38.5803 | 84.3796 | 84.3567 | 0.21515 | -38.7497 | 90.4816 | 90.39 | 0.041199 | 123.1567 | 123.2483 | 32.8583 | -0.050354 | 84.5306 | 84.3613 | 84.2789 | -38.9694 | 123.1522 | 123.0606 | 123.2162 | -32.7209
2017.5156 | 123.262 | -81.7291 | 41.423 | -0.010681 | 0.013313 | 0.0020037 | 0.01624 | -0.021048 | -0.00065585 | 0.0038345 | -0.14168 | 0.018739 | -0.010431 | 0.014417 | -0.0042126 | 0.012134 | 2.6733 | 2.6596 | 2.5726 | 2.6871 | 2.8748 | 2.6138 | 2.4445 | 41.3818 | 41.5009 | 41.4825 | 41.4688 | 41.391 | 8.7799 | 8.6746 | 84.343 | 84.1736 | -38.5483 | 84.3887 | 84.4162 | 0.24261 | -38.7497 | 90.509 | 90.4037 | 0.045776 | 123.111 | 123.2117 | 32.8079 | -0.032044 | 84.6039 | 84.4025 | 84.3018 | -38.9786 | 123.1979 | 123.1201 | 123.23 | -32.7484
2018.5156 | 123.3719 | -81.7337 | 41.3635 | -0.1709 | 0.010109 | 0.0049945 | 0.012394 | -0.017203 | -0.0051418 | 0.0012711 | -0.065384 | 0.017244 | -0.013208 | 0.013777 | -0.0037854 | 0.012134 | 2.7008 | 2.7878 | 2.6825 | 2.7374 | 2.7969 | 2.6413 | 2.4582 | 41.4185 | 41.5695 | 41.5604 | 41.3589 | 41.2994 | 8.7799 | 8.6838 | 84.375 | 84.1919 | -38.5666 | 84.5215 | 84.4711 | 0.27924 | -38.6627 | 90.5136 | 90.4175 | -0.004577 | 123.1522 | 123.2941 | 32.8766 | -0.064087 | 84.5306 | 84.4345 | 84.4162 | -38.9053 | 123.0927 | 123.0331 | 123.3032 | -32.6797
2019.5156 | 123.3398 | -81.7657 | 41.3589 | -0.16327 | 0.010963 | 0.0030719 | 0.010899 | -0.018912 | -0.002792 | 0.0019119 | -0.13405 | 0.01703 | -0.012354 | 0.013136 | -0.0050672 | 0.011279 | 2.6871 | 2.7695 | 2.6596 | 2.71 | 2.8061 | 2.6184 | 2.4536 | 41.391 | 41.5237 | 41.5009 | 41.3818 | 41.2994 | 8.7708 | 8.6792 | 84.3842 | 84.2194 | -38.5529 | 84.5352 | 84.4757 | 0.25635 | -38.6719 | 90.5365 | 90.4449 | 0.022888 | 123.1567 | 123.2666 | 32.8217 | -0.05951 | 84.5718 | 84.4528 | 84.4254 | -38.9053 | 123.1476 | 123.0652 | 123.2895 | -32.6797
2020.5156 | 123.4177 | -81.7978 | 41.2994 | -0.018311 | 0.0086133 | 0.0043537 | 0.011754 | -0.020407 | -0.0038602 | -0.00043792 | 0.01091 | 0.015962 | -0.011072 | 0.013136 | -0.0046398 | 0.013202 | 2.6917 | 2.774 | 2.6688 | 2.71 | 2.8061 | 2.623 | 2.4628 | 41.4001 | 41.4963 | 41.51 | 41.304 | 41.2399 | 8.7708 | 8.6838 | 84.4208 | 84.2606 | -38.4933 | 84.5718 | 84.5078 | 0.24719 | -38.6078 | 90.5685 | 90.4816 | 0.004578 | 123.1979 | 123.3078 | 32.8262 | -0.059509 | 84.6039 | 84.4894 | 84.4666 | -38.8367 | 123.1018 | 123.0377 | 123.2941 | -32.6157
2021.5312 | 123.2803 | -81.8344 | 41.3544 | 0.15717 | 0.016517 | -0.00013251 | 0.01624 | -0.018698 | 0.00853 | 0.0061845 | -0.14168 | 0.018953 | -0.010431 | 0.01399 | -0.0016492 | 0.0093567 | 2.3758 | 2.9022 | 2.6596 | 2.5818 | 2.8107 | 2.5681 | 2.417 | 41.3177 | 41.3452 | 41.3727 | 41.3544 | 41.2857 | 8.7753 | 8.6792 | 84.4025 | 84.2514 | -38.5437 | 84.7366 | 84.4162 | 0.16479 | -38.9786 | 90.6097 | 90.5136 | 0 | 123.1522 | 123.2071 | 32.6935 | -0.068664 | 84.6451 | 84.2102 | 84.494 | -38.9374 | 123.1888 | 123.1201 | 123.1796 | -32.6752
2022.5156 | 123.4039 | -81.7108 | 41.3544 | -0.13275 | 0.0062635 | 0.00072209 | 0.011113 | -0.019339 | -0.0036464 | 0.00041648 | 0.67467 | 0.019166 | -0.014704 | 0.015272 | -0.0035718 | 0.01192 | 2.71 | 2.7557 | 2.7512 | 2.8061 | 2.7878 | 2.5864 | 2.4307 | 41.4459 | 41.6107 | 41.5558 | 41.3544 | 41.2949 | 8.7753 | 8.6838 | 84.2972 | 84.1415 | -38.5666 | 84.4666 | 84.5169 | 0.37537 | -38.6444 | 90.4861 | 90.3946 | 0 | 123.1567 | 123.2666 | 32.872 | -0.059509 | 84.4986 | 84.4208 | 84.462 | -38.9236 | 123.0652 | 123.0057 | 123.3215 | -32.6706
2023.5156 | 123.2986 | -81.7932 | 41.3315 | -0.19379 | 0.012031 | 0.0032855 | 0.012608 | -0.018485 | -0.00065585 | 0.0019119 | -0.17983 | 0.018525 | -0.011286 | 0.012068 | -0.0029308 | 0.011493 | 2.6688 | 2.7145 | 2.6184 | 2.6733 | 2.7878 | 2.5909 | 2.4307 | 41.3406 | 41.4597 | 41.4322 | 41.3544 | 41.272 | 8.7753 | 8.6746 | 84.3842 | 84.2239 | -38.5437 | 84.5078 | 84.4666 | 0.24262 | -38.6627 | 90.5685 | 90.4678 | 0.022888 | 123.1338 | 123.2254 | 32.7576 | -0.059509 | 84.581 | 84.462 | 84.4116 | -38.9008 | 123.1476 | 123.0652 | 123.2529 | -32.6569
2024.5156 | 123.381 | -81.8024 | 41.2674 | -0.14038 | 0.0094677 | 0.00050849 | 0.012608 | -0.019553 | -0.0098416 | -0.0023605 | 0.15587 | 0.017457 | -0.015772 | 0.014631 | -0.0029308 | 0.012988 | 2.9068 | 2.417 | 2.4765 | 2.6871 | 2.7649 | 2.5635 | 2.4033 | 41.3773 | 41.5009 | 41.5054 | 41.2994 | 41.1987 | 8.7799 | 8.6792 | 84.3658 | 84.2056 | -38.5025 | 84.2194 | 84.4894 | 0.28381 | -38.3606 | 90.5823 | 90.4816 | 0.032043 | 123.1796 | 123.3078 | 32.8262 | -0.068665 | 84.5673 | 84.7092 | 84.2789 | -38.8641 | 123.1018 | 123.0011 | 123.3032 | -32.5882
2025.5156 | 123.3765 | -81.7886 | 41.3269 | -0.048828 | 0.0069043 | 0.0043537 | 0.013035 | -0.018485 | 0.00019875 | 0.0025529 | -0.11116 | 0.01703 | -0.013208 | 0.013136 | -0.0027172 | 0.012988 | 2.6688 | 2.7512 | 2.6413 | 2.6779 | 2.7512 | 2.5818 | 2.4078 | 41.4001 | 41.5466 | 41.5283 | 41.3589 | 41.2354 | 8.7799 | 8.6746 | 84.3704 | 84.1965 | -38.5757 | 84.5398 | 84.4666 | 0.27008 | -38.6581 | 90.5685 | 90.4633 | 0.032044 | 123.1888 | 123.317 | 32.8537 | -0.091552 | 84.5398 | 84.4574 | 84.4299 | -38.9191 | 123.1476 | 123.024 | 123.3353 | -32.6523
2026.5156 | 123.3078 | -81.8161 | 41.3269 | -0.12512 | 0.014808 | 0.0024311 | 0.016453 | -0.018912 | 0.004044 | 0.0036209 | -0.2256 | 0.019593 | -0.01214 | 0.013349 | -0.0029308 | 0.0093567 | 2.5818 | 2.6001 | 2.504 | 2.6047 | 2.7969 | 2.536 | 2.3758 | 41.3589 | 41.4322 | 41.423 | 41.3498 | 41.272 | 8.7753 | 8.6746 | 84.3521 | 84.1919 | -38.53 | 84.4162 | 84.4208 | 0.22888 | -38.7451 | 90.5914 | 90.4907 | 0.022888 | 123.175 | 123.2391 | 32.7484 | -0.054931 | 84.613 | 84.3979 | 84.3201 | -38.9511 | 123.1659 | 123.0881 | 123.2483 | -32.6523
2027.5156 | 123.3948 | -81.8069 | 41.2994 | -0.018311 | 0.0073315 | 0.0028583 | 0.012181 | -0.01763 | -0.0034328 | 0.0038345 | 0.041427 | 0.018098 | -0.012995 | 0.014204 | -0.0063488 | 0.012561 | 2.6321 | 2.7145 | 2.6047 | 2.6505 | 2.7603 | 2.5772 | 2.3987 | 41.4001 | 41.4825 | 41.5009 | 41.3361 | 41.2354 | 8.7845 | 8.6746 | 84.3842 | 84.2056 | -38.5391 | 84.5215 | 84.4574 | 0.25177 | -38.6673 | 90.5914 | 90.4816 | 0.036622 | 123.2071 | 123.3078 | 32.8262 | -0.064086 | 84.5673 | 84.4391 | 84.4116 | -38.9008 | 123.143 | 123.0423 | 123.2895 | -32.6248
2028.5156 | 123.3948 | -81.8207 | 41.2994 | 0.035095 | 0.0056225 | 0.0022175 | 0.01154 | -0.018912 | -0.0017238 | 0.0021255 | 0.026169 | 0.017244 | -0.012995 | 0.013349 | -0.0033582 | 0.010852 | 2.6001 | 2.6733 | 2.5635 | 2.6413 | 2.742 | 2.5589 | 2.4033 | 41.3589 | 41.478 | 41.478 | 41.2857 | 41.2079 | 8.7753 | 8.6746 | 84.3796 | 84.2239 | -38.5574 | 84.494 | 84.462 | 0.23804 | -38.6993 | 90.596 | 90.4953 | -0.013732 | 123.1796 | 123.2986 | 32.8033 | -0.091552 | 84.5627 | 84.4208 | 84.3842 | -38.8962 | 123.1064 | 123.0286 | 123.2986 | -32.6248
2029.5156 | 123.4131 | -81.8344 | 41.2399 | -0.010681 | 0.010109 | 0.0024311 | 0.013249 | -0.018057 | -0.0017238 | 0.0019119 | -0.095902 | 0.010194 | -0.01449 | 0.014631 | -0.00079463 | 0.0089295 | 2.6917 | 2.7649 | 2.6321 | 2.6733 | 2.7466 | 2.5818 | 2.3987 | 41.3452 | 41.5466 | 41.4001 | 41.2582 | 41.153 | 8.7708 | 8.67 | 84.4162 | 84.2331 | -38.4933 | 84.5993 | 84.5078 | 0.27466 | -38.5483 | 90.6052 | 90.5045 | 0.018311 | 123.1796 | 123.2346 | 32.7301 | -0.086975 | 84.581 | 84.5261 | 84.4666 | -38.8412 | 123.0927 | 122.9874 | 123.381 | -32.5699
2030.5156 | 123.3627 | -81.8207 | 41.2766 | 0.088501 | 0.0077587 | 0.0030719 | 0.01154 | -0.021262 | -0.0025784 | 0.0023391 | 0.18639 | 0.017244 | -0.011713 | 0.015058 | -0.0027172 | 0.012347 | 2.6001 | 2.4536 | 2.449 | 2.6047 | 2.6688 | 2.5177 | 2.3346 | 41.3086 | 41.4047 | 41.4459 | 41.2994 | 41.1896 | 8.7753 | 8.6746 | 84.3384 | 84.1553 | -38.6078 | 84.2743 | 84.4254 | 0.27008 | -38.6765 | 90.596 | 90.4953 | 0.022888 | 123.1293 | 123.2666 | 32.7713 | -0.086975 | 84.4894 | 84.4208 | 84.2697 | -38.942 | 123.1201 | 123.0103 | 123.2254 | -32.6019
2031.5312 | 123.2895 | -81.8893 | 41.3086 | 0.0045777 | 0.017799 | -0.00013251 | 0.011967 | -0.020621 | 0.0059666 | 0.0025529 | -0.034867 | 0.020448 | -0.0087222 | 0.013777 | -0.00058103 | 0.0089295 | 2.6001 | 2.5818 | 2.4719 | 2.5726 | 2.7466 | 2.5131 | 2.3666 | 41.3086 | 41.3315 | 41.3452 | 41.3269 | 41.2354 | 8.7799 | 8.6792 | 84.4025 | 84.256 | -38.562 | 84.4711 | 84.462 | 0.20599 | -38.7085 | 90.6692 | 90.5685 | 0.01831 | 123.1979 | 123.2346 | 32.666 | -0.073242 | 84.6359 | 84.4894 | 84.3613 | -38.942 | 123.2162 | 123.1247 | 123.2208 | -32.6294
2032.5156 | 123.3398 | -81.9031 | 41.1896 | 0.17242 | 0.0098951 | 0.0032855 | 0.011113 | -0.01763 | -0.0019376 | 0.0040481 | 0.17876 | 0.018525 | -0.013208 | 0.014631 | -0.003999 | 0.013416 | 2.623 | 2.6596 | 2.5681 | 2.6093 | 2.71 | 2.5497 | 2.3941 | 41.2445 | 41.3177 | 41.3498 | 41.1942 | 41.1255 | 8.7845 | 8.6838 | 84.4528 | 84.2972 | -38.4796 | 84.5627 | 84.5123 | 0.21515 | -38.5666 | 90.6876 | 90.5869 | 0.004578 | 123.1476 | 123.2529 | 32.666 | -0.064087 | 84.613 | 84.5261 | 84.4711 | -38.7955 | 123.0972 | 123.0286 | 123.2208 | -32.5058
2033.5156 | 123.3582 | -81.8939 | 41.2308 | 0.019836 | 0.0047681 | 0.0032855 | 0.010685 | -0.018698 | -0.0023648 | 0.0036209 | 0.049057 | 0.018739 | -0.015772 | 0.014631 | -0.0031446 | 0.01192 | 2.5772 | 2.6367 | 2.5406 | 2.5955 | 2.7283 | 2.5177 | 2.3758 | 41.2811 | 41.3773 | 41.3818 | 41.2216 | 41.1484 | 8.7753 | 8.6838 | 84.4116 | 84.2697 | -38.5025 | 84.5306 | 84.4894 | 0.21973 | -38.6536 | 90.6693 | 90.5777 | -0.009155 | 123.175 | 123.2758 | 32.6981 | -0.082398 | 84.6222 | 84.4711 | 84.4345 | -38.855 | 123.1155 | 123.0423 | 123.2712 | -32.547
2034.5156 | 123.3902 | -81.8939 | 41.1392 | 0.17242 | 0.014808 | 0.00093569 | 0.011967 | -0.019766 | 0.001694 | 0.0055435 | 0.49156 | 0.018525 | -0.012781 | 0.012708 | -0.0010082 | 0.010425 | 2.6459 | 2.655 | 2.5635 | 2.5864 | 2.6917 | 2.5269 | 2.3529 | 41.2949 | 41.3681 | 41.3681 | 41.1758 | 41.0797 | 8.7845 | 8.6746 | 84.4208 | 84.2468 | -38.4476 | 84.549 | 84.4803 | 0.23346 | -38.4933 | 90.6784 | 90.5685 | 0.036621 | 123.1888 | 123.262 | 32.6935 | -0.059509 | 84.5856 | 84.5398 | 84.4574 | -38.7863 | 123.0698 | 122.9736 | 123.262 | -32.4646
2035.5156 | 123.3627 | -81.8802 | 41.2628 | 0.080872 | 0.0075451 | 0.0026447 | 0.01154 | -0.017417 | -0.002792 | 0.0034073 | 0.094833 | 0.01703 | -0.011713 | 0.013777 | -0.0035718 | 0.012988 | 2.5818 | 2.6321 | 2.5406 | 2.6047 | 2.7191 | 2.5269 | 2.3712 | 41.3086 | 41.4093 | 41.4047 | 41.2811 | 41.1621 | 8.7799 | 8.6792 | 84.407 | 84.2514 | -38.5437 | 84.5123 | 84.4849 | 0.23346 | -38.681 | 90.6601 | 90.5594 | 0.018311 | 123.1888 | 123.2849 | 32.7255 | -0.10071 | 84.5993 | 84.462 | 84.4208 | -38.8916 | 123.1613 | 123.0423 | 123.2895 | -32.5836
2036.5156 | 123.349 | -81.9443 | 41.1301 | 0.21057 | 0.013313 | 0.0020037 | 0.009831 | -0.020835 | 0.001694 | 0.0031937 | 0.14061 | 0.018739 | -0.012354 | 0.012922 | -0.0029308 | 0.010425 | 2.6367 | 2.6596 | 2.5589 | 2.5909 | 2.6733 | 2.5177 | 2.3621 | 41.2674 | 41.3086 | 41.3406 | 41.153 | 41.0706 | 8.7891 | 8.6792 | 84.462 | 84.3063 | -38.4567 | 84.6039 | 84.5352 | 0.22888 | -38.4933 | 90.7333 | 90.6235 | 0.022888 | 123.2117 | 123.2849 | 32.6614 | -0.059509 | 84.6176 | 84.581 | 84.5032 | -38.768 | 123.0972 | 123.0148 | 123.2529 | -32.4509
2037.5156 | 123.3582 | -81.926 | 41.153 | 0.13428 | 0.0088269 | 0.0026447 | 0.010899 | -0.01763 | -0.001083 | 0.0019119 | 0.11009 | 0.01703 | -0.015985 | 0.013136 | -0.0044262 | 0.0093567 | 2.5726 | 2.6184 | 2.5177 | 2.5909 | 2.7191 | 2.5177 | 2.3621 | 41.2628 | 41.3818 | 41.2308 | 41.1942 | 41.1118 | 8.7799 | 8.6838 | 84.4437 | 84.288 | -38.4338 | 84.5444 | 84.5169 | 0.22888 | -38.5803 | 90.7059 | 90.6097 | 0.041199 | 123.1888 | 123.1567 | 32.547 | -0.041199 | 84.6451 | 84.4986 | 84.4437 | -38.7909 | 123.1201 | 123.0377 | 123.3078 | -32.4692
2038.5156 | 123.3902 | -81.9305 | 41.1484 | 0.24872 | 0.01609 | 0.0013629 | 0.010472 | -0.01998 | 0.0027622 | 0.0029801 | 0.27794 | 0.01938 | -0.013208 | 0.015058 | -0.00015383 | 0.010425 | 2.6413 | 2.6367 | 2.536 | 2.4353 | 2.655 | 2.5177 | 2.3392 | 41.2994 | 41.3681 | 41.3361 | 41.1621 | 41.0522 | 8.7753 | 8.6792 | 84.4482 | 84.2697 | -38.4933 | 84.5673 | 84.3658 | 0.096131 | -38.5071 | 90.7059 | 90.6097 | 0.013733 | 123.23 | 123.2666 | 32.6569 | -0.09613 | 84.5856 | 84.5718 | 84.4666 | -38.8092 | 123.0927 | 122.9828 | 123.2986 | -32.4692
2039.5156 | 123.349 | -81.9901 | 41.1346 | 0.13428 | 0.0081861 | 0.00093569 | 0.010685 | -0.020407 | -0.0012966 | 0.0031937 | 0.20927 | 0.016603 | -0.01449 | 0.014204 | -0.0027172 | 0.01192 | 2.5955 | 2.6184 | 2.5131 | 2.5589 | 2.6688 | 2.504 | 2.33 | 41.2354 | 41.2628 | 41.2811 | 41.1301 | 41.0751 | 8.7799 | 8.6746 | 84.494 | 84.3201 | -38.4659 | 84.6085 | 84.5489 | 0.22888 | -38.5391 | 90.77 | 90.6647 | -0.004578 | 123.2254 | 123.2712 | 32.6065 | -0.05951 | 84.6588 | 84.5856 | 84.5032 | -38.8046 | 123.1201 | 123.0652 | 123.2529 | -32.46
2040.5156 | 123.3078 | -82.0267 | 41.1392 | 0.14954 | 0.015236 | 0.0028583 | 0.012822 | -0.018698 | 0.0048984 | 0.0042619 | 0.11009 | 0.020662 | -0.012354 | 0.013136 | -0.00079463 | 0.011279 | 2.5131 | 2.4857 | 2.3895 | 2.4902 | 2.7008 | 2.4445 | 2.2842 | 41.1713 | 41.1896 | 41.2079 | 41.1484 | 41.0797 | 8.7753 | 8.6792 | 84.4711 | 84.3109 | -38.4384 | 84.5123 | 84.5169 | 0.20599 | -38.6261 | 90.802 | 90.7059 | 0.009155 | 123.1979 | 123.2346 | 32.5287 | -0.059509 | 84.7275 | 84.5398 | 84.4162 | -38.855 | 123.175 | 123.1064 | 123.2162 | -32.46
2041.5156 | 123.3994 | -81.9763 | 41.1072 | 0.14191 | 0.011177 | 0.00093569 | 0.013463 | -0.018912 | -0.001083 | 0.0027665 | 0.18639 | 0.019593 | -0.011072 | 0.011213 | -0.0014356 | 0.011707 | 2.5864 | 2.6138 | 2.5269 | 2.5589 | 2.6413 | 2.4857 | 2.3392 | 41.2216 | 41.304 | 41.2903 | 41.1392 | 41.066 | 8.7845 | 8.6792 | 84.462 | 84.3155 | -38.4659 | 84.5901 | 84.5352 | 0.21973 | -38.5208 | 90.7608 | 90.6555 | 0.032043 | 123.1979 | 123.2666 | 32.6111 | -0.041199 | 84.6176 | 84.5627 | 84.5032 | -38.768 | 123.1155 | 123.0423 | 123.2803 | -32.428
2042.5156 | 123.4039 | -81.9992 | 41.0934 | 0.19531 | 0.015877 | 0.0015765 | 0.014958 | -0.01763 | 0.0029758 | 0.0027665 | 0.14824 | 0.019593 | -0.010858 | 0.015058 | -0.0010082 | 0.012988 | 2.5314 | 2.5497 | 2.4673 | 2.5177 | 2.655 | 2.4536 | 2.298 | 41.217 | 41.2674 | 41.2766 | 41.1301 | 41.0385 | 8.7799 | 8.6792 | 84.4528 | 84.2972 | -38.4384 | 84.549 | 84.5169 | 0.21973 | -38.562 | 90.7791 | 90.6784 | 0.036621 | 123.2162 | 123.2758 | 32.5974 | -0.054932 | 84.6542 | 84.5306 | 84.4666 | -38.7955 | 123.1293 | 123.0377 | 123.2666 | -32.4142
2043.5156 | 123.3582 | -82.045 | 41.0797 | 0.19531 | 0.010963 | 0.0020037 | 0.012822 | -0.020194 | -0.002792 | 0.0023391 | 0.2169 | 0.017457 | -0.011499 | 0.013563 | -0.0054944 | 0.01192 | 2.5497 | 2.6001 | 2.4902 | 2.536 | 2.6413 | 2.4719 | 2.3209 | 41.1438 | 41.2125 | 41.2491 | 41.066 | 40.9973 | 8.7799 | 8.6746 | 84.5169 | 84.3658 | -38.4384 | 84.6451 | 84.581 | 0.21515 | -38.53 | 90.8249 | 90.7196 | -0.013733 | 123.1888 | 123.2941 | 32.5745 | -0.082398 | 84.6863 | 84.5947 | 84.5352 | -38.7589 | 123.111 | 123.0423 | 123.2574 | -32.4051
2044.5156 | 123.3307 | -82.0953 | 41.0614 | 0.17242 | 0.016304 | 0.0020037 | 0.014103 | -0.016989 | 0.0061802 | 0.0049027 | 0.17113 | 0.021302 | -0.010645 | 0.014204 | -0.0016492 | 0.010211 | 2.5085 | 2.4902 | 2.3849 | 2.4811 | 2.6733 | 2.449 | 2.2751 | 41.0934 | 41.1392 | 41.1346 | 41.1163 | 41.0065 | 8.7799 | 8.6746 | 84.5444 | 84.3704 | -38.3881 | 84.5856 | 84.5764 | 0.20599 | -38.5529 | 90.8752 | 90.77 | 0.054932 | 123.1888 | 123.23 | 32.46 | -0.054931 | 84.7687 | 84.6039 | 84.4803 | -38.7863 | 123.2117 | 123.1018 | 123.2346 | -32.3868
2045.5156 | 123.4085 | -82.0267 | 41.0477 | 0.25635 | 0.012459 | 0.0034991 | 0.012394 | -0.019339 | 0.00083955 | 0.0051163 | -0.68337 | 0.018525 | -0.012567 | 0.012068 | -0.0020764 | 0.011066 | 2.5864 | 2.5909 | 2.504 | 2.5589 | 2.6321 | 2.4719 | 2.3117 | 41.1758 | 41.2354 | 41.2674 | 41.0614 | 40.9927 | 8.7753 | 8.6792 | 84.4986 | 84.3384 | -38.4155 | 84.6176 | 84.5856 | 0.24719 | -38.4613 | 90.802 | 90.7059 | 0.013733 | 123.2025 | 123.2941 | 32.5882 | -0.054931 | 84.6588 | 84.613 | 84.5306 | -38.736 | 123.0881 | 123.0194 | 123.262 | -32.3685
2046.5156 | 123.2758 | -82.1091 | 41.0385 | 0.15717 | 0.020576 | 0.00072209 | 0.017949 | -0.020621 | 0.0061802 | 0.0042619 | 0.071945 | 0.02173 | -0.012567 | 0.014417 | -0.0016492 | 0.012561 | 2.4307 | 2.4994 | 2.3575 | 2.4582 | 2.6688 | 2.417 | 2.2797 | 41.0294 | 41.0889 | 41.066 | 41.0614 | 40.9973 | 8.7799 | 8.6838 | 84.5261 | 84.3887 | -38.3698 | 84.6085 | 84.5673 | 0.17853 | -38.6078 | 90.889 | 90.7928 | 0.022888 | 123.1384 | 123.175 | 32.3822 | -0.041199 | 84.7778 | 84.5398 | 84.4666 | -38.7589 | 123.1705 | 123.1064 | 123.1979 | -32.3547
2047.5156 | 123.3078 | -82.1182 | 41.0339 | 0.13428 | 0.014381 | 0.0022175 | 0.012608 | -0.01998 | 0.0031894 | 0.0031937 | 0.14824 | 0.021302 | -0.012567 | 0.013349 | 0.0015552 | 0.013629 | 2.4719 | 2.4673 | 2.3712 | 2.4673 | 2.6688 | 2.4353 | 2.2614 | 41.0568 | 41.098 | 41.1026 | 41.0934 | 40.9607 | 8.7708 | 8.67 | 84.5535 | 84.3796 | -38.3652 | 84.5856 | 84.5856 | 0.20599 | -38.562 | 90.889 | 90.7883 | 0.059509 | 123.175 | 123.2208 | 32.4326 | -0.073243 | 84.787 | 84.5901 | 84.4894 | -38.7726 | 123.2117 | 123.0789 | 123.2162 | -32.3639
2048.5156 | 123.2849 | -82.1457 | 41.0385 | 0.0045777 | 0.015877 | 0.0041401 | 0.014958 | -0.018912 | 0.0061802 | 0.0031937 | 0.01091 | 0.02173 | -0.0097904 | 0.012708 | -0.0025036 | 0.012561 | 2.5223 | 2.4994 | 2.3941 | 2.504 | 2.6733 | 2.4399 | 2.2659 | 41.0248 | 41.1072 | 41.0843 | 41.0477 | 41.0019 | 8.7753 | 8.6746 | 84.5856 | 84.4116 | -38.3652 | 84.6451 | 84.6497 | 0.23804 | -38.5162 | 90.921 | 90.8203 | 0.009155 | 123.1705 | 123.23 | 32.4097 | -0.036621 | 84.819 | 84.668 | 84.5398 | -38.7726 | 123.1934 | 123.1476 | 123.2529 | -32.3639
2049.5156 | 123.3948 | -82.0816 | 40.9973 | 0.20294 | 0.013954 | 0.0022175 | 0.010045 | -0.018485 | 0.00019875 | 0.0053299 | 0.27794 | 0.019593 | -0.011286 | 0.012068 | -0.0020764 | 0.012561 | 2.4994 | 2.536 | 2.4399 | 2.5223 | 2.6321 | 2.4307 | 2.2705 | 41.1118 | 41.1987 | 41.2033 | 41.0156 | 40.9744 | 8.7799 | 8.6746 | 84.5123 | 84.3521 | -38.3652 | 84.6176 | 84.6039 | 0.25177 | -38.4979 | 90.8615 | 90.7562 | 0.018311 | 123.1934 | 123.2849 | 32.5287 | -0.022888 | 84.7137 | 84.581 | 84.5215 | -38.7268 | 123.0972 | 123.056 | 123.2803 | -32.3227
2050.5156 | 123.2529 | -82.132 | 41.0751 | 0.080872 | 0.018226 | 0.0034991 | 0.011754 | -0.016776 | 0.002335 | 0.0046891 | 0.10246 | 0.020021 | -0.011072 | 0.014631 | 0.0019824 | 0.013629 | 2.4582 | 2.4124 | 2.3346 | 2.4582 | 2.6505 | 2.4124 | 2.2385 | 40.892 | 41.4505 | 41.2262 | 41.0568 | 41.0156 | 8.7799 | 8.6746 | 84.5444 | 84.3704 | -38.4247 | 84.5444 | 84.5901 | 0.21973 | -38.6169 | 90.9119 | 90.8066 | -0.01831 | 123.024 | 123.3582 | 32.5516 | -0.059509 | 84.7824 | 84.5901 | 84.4666 | -38.8367 | 123.1888 | 123.1476 | 123.5825 | -32.4005
2051.5156 | 123.3261 | -82.132 | 40.9927 | 0.18768 | 0.016731 | 0.00093569 | 0.012608 | -0.018057 | 0.002335 | 0.0040481 | 0.2169 | 0.020662 | -0.012781 | 0.011854 | -0.0029308 | 0.013843 | 2.4628 | 2.4399 | 2.3758 | 2.4536 | 2.6413 | 2.417 | 2.2385 | 41.0294 | 41.0934 | 41.1026 | 41.0339 | 40.9607 | 8.7753 | 8.6746 | 84.5489 | 84.3704 | -38.3514 | 84.5718 | 84.5856 | 0.21515 | -38.53 | 90.9073 | 90.8066 | 0.041199 | 123.1613 | 123.2346 | 32.428 | -0.032044 | 84.7733 | 84.5947 | 84.5078 | -38.7543 | 123.1659 | 123.0927 | 123.2254 | -32.3181
2052.5156 | 123.2574 | -82.1732 | 41.0156 | 0.042725 | 0.017158 | 0.0041401 | 0.013249 | -0.016776 | 0.0036166 | 0.0038345 | 0.064316 | 0.01938 | -0.009363 | 0.010359 | -0.0016492 | 0.012561 | 2.449 | 2.4582 | 2.3804 | 2.4673 | 2.6413 | 2.417 | 2.2614 | 40.9698 | 41.0477 | 41.0339 | 41.0156 | 40.9515 | 8.7799 | 8.6838 | 84.5901 | 84.4345 | -38.3743 | 84.6313 | 84.6405 | 0.20599 | -38.5666 | 90.9531 | 90.8569 | 0 | 123.143 | 123.2071 | 32.3502 | -0.064087 | 84.8145 | 84.6222 | 84.5535 | -38.7543 | 123.1888 | 123.1247 | 123.2208 | -32.3318
2053.5156 | 123.2849 | -82.1503 | 41.0248 | 0.33264 | 0.017158 | 0.0020037 | 0.012822 | -0.019126 | 0.00062595 | 0.0044755 | 0.15587 | 0.020448 | -0.011286 | 0.012922 | -0.0033582 | 0.013202 | 2.4353 | 2.4399 | 2.3438 | 2.4628 | 2.6413 | 2.4078 | 2.2247 | 41.0065 | 41.0706 | 41.0843 | 41.0706 | 40.9927 | 8.7708 | 8.6746 | 84.5581 | 84.375 | -38.3835 | 84.5901 | 84.613 | 0.23804 | -38.5895 | 90.921 | 90.8249 | 0.045777 | 123.1567 | 123.2346 | 32.4097 | -0.032043 | 84.7916 | 84.5856 | 84.494 | -38.8 | 123.2208 | 123.143 | 123.2208 | -32.3502
2054.5156 | 123.3307 | -82.2052 | 40.9561 | -0.041199 | 0.018654 | 0.0020037 | 0.014317 | -0.016349 | 0.0014804 | 0.0049027 | -0.46211 | 0.022798 | -0.0095768 | 0.012922 | -0.0018628 | 0.01192 | 2.4994 | 2.5223 | 2.4628 | 2.6184 | 2.6505 | 2.4445 | 2.2751 | 40.9882 | 41.098 | 41.0614 | 40.9927 | 40.9378 | 8.7799 | 8.6746 | 84.6497 | 84.4803 | -38.3057 | 84.7275 | 84.8236 | 0.34332 | -38.4567 | 90.9851 | 90.8798 | 0.036621 | 123.1934 | 123.2666 | 32.3868 | -0.018311 | 84.8557 | 84.7046 | 84.668 | -38.681 | 123.1979 | 123.143 | 123.3032 | -32.2815
2055.5156 | 123.2895 | -82.196 | 40.9836 | 0.042725 | 0.015022 | 8.1086e-05 | 0.013463 | -0.019126 | 0.0029758 | 0.0040481 | 0.056686 | 0.021089 | -0.012995 | 0.013563 | -0.0025036 | 0.012988 | 2.4536 | 2.449 | 2.3712 | 2.4582 | 2.6276 | 2.4078 | 2.2522 | 40.9286 | 41.0339 | 41.0156 | 41.0019 | 40.9378 | 8.7753 | 8.6746 | 84.6039 | 84.4482 | -38.356 | 84.6451 | 84.6542 | 0.20599 | -38.53 | 90.9714 | 90.8707 | 0.01831 | 123.1247 | 123.2117 | 32.341 | -0.045777 | 84.8236 | 84.6497 | 84.5673 | -38.7314 | 123.1979 | 123.1338 | 123.23 | -32.309
2056.5156 | 123.2849 | -82.2098 | 40.9653 | 0.012207 | 0.017158 | 0.0020037 | 0.015172 | -0.019126 | 0.00041235 | 0.0051163 | 0.026169 | 0.021089 | -0.0089358 | 0.015486 | -0.0044262 | 0.011493 | 2.4811 | 2.4673 | 2.3895 | 2.4673 | 2.6367 | 2.4124 | 2.243 | 40.9286 | 41.0156 | 41.0019 | 40.9744 | 40.892 | 8.7708 | 8.6746 | 84.6222 | 84.4528 | -38.3286 | 84.6771 | 84.6771 | 0.2243 | -38.4842 | 90.9805 | 90.8844 | 0.009155 | 123.1384 | 123.2117 | 32.3273 | -0.073242 | 84.8465 | 84.6909 | 84.5993 | -38.7222 | 123.1842 | 123.1018 | 123.2254 | -32.2906
2057.5156 | 123.2895 | -82.2739 | 40.9378 | 0.17242 | 0.017586 | 0.0015765 | 0.014103 | -0.01998 | 0.002335 | 0.0036209 | 0.20164 | 0.020021 | -0.0091494 | 0.014417 | -0.0031446 | 0.016193 | 2.3941 | 2.33 | 2.4033 | 2.6093 | 2.6276 | 2.4124 | 2.2476 | 40.8737 | 40.9698 | 40.9698 | 40.979 | 40.8966 | 8.7753 | 8.6746 | 84.6863 | 84.5215 | -38.3102 | 84.6039 | 84.8831 | 0.36163 | -38.5437 | 91.0492 | 90.9485 | 0.041199 | 123.1476 | 123.2437 | 32.2952 | -0.041199 | 84.9014 | 84.668 | 84.6771 | -38.6902 | 123.2529 | 123.1705 | 123.2437 | -32.2632
2058.5156 | 123.3261 | -82.2189 | 40.9653 | 0.19531 | 0.016304 | 0.0013629 | 0.014744 | -0.021689 | 0.0031894 | 0.0038345 | -0.019608 | 0.020662 | -0.010431 | 0.013777 | -0.0029308 | 0.012775 | 2.4902 | 2.4902 | 2.3849 | 2.4673 | 2.6276 | 2.417 | 2.243 | 40.9607 | 41.0614 | 41.0385 | 40.9515 | 40.9332 | 8.7799 | 8.6792 | 84.6359 | 84.462 | -38.3377 | 84.7092 | 84.6863 | 0.2243 | -38.475 | 90.9988 | 90.8981 | -0.013733 | 123.1796 | 123.2574 | 32.3593 | -0.032043 | 84.8465 | 84.7092 | 84.6039 | -38.7222 | 123.1705 | 123.1522 | 123.2803 | -32.2861
2059.5156 | 123.2391 | -82.2693 | 40.9332 | 0.035095 | 0.017799 | 0.0011493 | 0.01624 | -0.018912 | 0.0014804 | 0.0042619 | 0.10246 | 0.020448 | -0.0085086 | 0.014631 | -0.0016492 | 0.012561 | 2.3895 | 2.3895 | 2.3209 | 2.4261 | 2.623 | 2.3529 | 2.2064 | 40.86 | 40.979 | 40.9515 | 40.9653 | 40.9149 | 8.7753 | 8.6746 | 84.6222 | 84.4757 | -38.3102 | 84.6588 | 84.6954 | 0.21973 | -38.5437 | 91.0446 | 90.9439 | 0.032043 | 123.1293 | 123.2208 | 32.2769 | -0.018311 | 84.8923 | 84.6588 | 84.5901 | -38.7268 | 123.2346 | 123.1842 | 123.2483 | -32.2586
2060.5156 | 123.3124 | -82.2189 | 40.9607 | -0.0030518 | 0.015877 | 0.0030719 | 0.014103 | -0.019126 | 0.003403 | 0.0040481 | -0.019608 | 0.020448 | -0.011286 | 0.012922 | -0.0042126 | 0.012134 | 2.4673 | 2.4445 | 2.3529 | 2.4445 | 2.6047 | 2.3895 | 2.2064 | 40.9515 | 41.0431 | 41.0156 | 40.9653 | 40.9378 | 8.7845 | 8.6746 | 84.6085 | 84.4254 | -38.356 | 84.6634 | 84.6634 | 0.23804 | -38.4933 | 91.0034 | 90.8936 | 0.004578 | 123.1705 | 123.2346 | 32.341 | -0.022888 | 84.8236 | 84.6863 | 84.5718 | -38.7543 | 123.1842 | 123.1567 | 123.262 | -32.2861
2061.5156 | 123.2986 | -82.2189 | 40.9561 | -0.10223 | 0.018226 | 0.0030719 | 0.014531 | -0.019339 | 0.0031894 | 0.0016983 | -0.011978 | 0.02173 | -0.010431 | 0.013136 | -0.0018628 | 0.012775 | 2.4673 | 2.4673 | 2.3575 | 2.4582 | 2.6047 | 2.3849 | 2.2202 | 40.9515 | 41.0431 | 41.0248 | 40.9561 | 40.9149 | 8.7753 | 8.6838 | 84.6039 | 84.4391 | -38.3514 | 84.6863 | 84.6771 | 0.23804 | -38.4888 | 90.9943 | 90.9027 | 0 | 123.1705 | 123.2437 | 32.341 | -0.041199 | 84.8236 | 84.6863 | 84.5764 | -38.736 | 123.175 | 123.1339 | 123.262 | -32.2723
2062.5156 | 123.3261 | -82.2556 | 40.9515 | -0.14038 | 0.015022 | 0.0026447 | 0.01624 | -0.01763 | 0.00019875 | 0.0042619 | -0.19508 | 0.018953 | -0.014063 | 0.015058 | -0.0027172 | 0.010425 | 2.4307 | 2.4399 | 2.3483 | 2.4399 | 2.5864 | 2.3666 | 2.1881 | 40.9241 | 41.0477 | 41.0339 | 40.9286 | 40.9012 | 8.7845 | 8.6884 | 84.6222 | 84.4437 | -38.3652 | 84.6954 | 84.6954 | 0.25177 | -38.5208 | 91.04 | 90.9439 | -0.022888 | 123.1796 | 123.2895 | 32.3456 | -0.050354 | 84.8419 | 84.6863 | 84.6039 | -38.7634 | 123.1842 | 123.1567 | 123.3032 | -32.2632
2063.5156 | 123.2849 | -82.2556 | 40.9058 | 1.973 | 0.016304 | 0.0064899 | 0.015172 | -0.020621 | 0.0010532 | 0.0014847 | 0.14824 | 0.018525 | -0.0074404 | 0.014631 | -0.0016492 | 0.013416 | 2.4307 | 2.3483 | 2.2842 | 2.4033 | 2.6001 | 2.3575 | 2.1698 | 40.86 | 40.9286 | 40.9698 | 40.9378 | 40.8829 | 8.7799 | 8.6746 | 84.613 | 84.4254 | -38.3057 | 84.6039 | 84.6588 | 0.23346 | -38.475 | 91.0355 | 90.9302 | 0.032043 | 123.1155 | 123.2254 | 32.2952 | -0.022888 | 84.8557 | 84.6863 | 84.5398 | -38.736 | 123.1934 | 123.1384 | 123.1842 | -32.2311
2064.5156 | 123.3353 | -82.2601 | 40.8875 | -0.10223 | 0.017158 | 0.0054217 | 0.012608 | -0.01998 | 0.0019078 | 0.0031937 | 1.2926 | 0.021089 | -0.010431 | 0.014204 | -0.0014356 | 0.012134 | 2.4399 | 2.4445 | 2.3438 | 2.4353 | 2.5955 | 2.3575 | 2.1973 | 40.9058 | 40.979 | 40.9836 | 40.8966 | 40.8646 | 8.7845 | 8.6746 | 84.6176 | 84.4574 | -38.2919 | 84.7046 | 84.6954 | 0.23804 | -38.4476 | 91.0446 | 90.9348 | 0.009155 | 123.1659 | 123.2437 | 32.309 | -0.022888 | 84.8557 | 84.7 | 84.6039 | -38.6902 | 123.1567 | 123.1247 | 123.2391 | -32.2128
2065.5156 | 123.2803 | -82.3288 | 40.8737 | 0.057983 | 0.017586 | 0.0017901 | 0.016026 | -0.019766 | 0.0027622 | 0.0036209 | 0.094833 | 0.020662 | -0.0089358 | 0.013136 | -0.00058103 | 0.011707 | 2.3987 | 2.3804 | 2.2842 | 2.3987 | 2.5772 | 2.3621 | 2.1881 | 40.7959 | 40.8875 | 40.8783 | 40.8875 | 40.8279 | 8.7708 | 8.6746 | 84.6909 | 84.5169 | -38.2965 | 84.7092 | 84.7275 | 0.21057 | -38.475 | 91.0995 | 91.0034 | 0.013733 | 123.1247 | 123.2071 | 32.2037 | -0.045776 | 84.906 | 84.7275 | 84.613 | -38.6856 | 123.2162 | 123.1567 | 123.2162 | -32.1991
2066.5156 | 123.2254 | -82.3105 | 40.8463 | -0.094604 | 0.016945 | 0.0030719 | 0.014531 | -0.019126 | 0.002335 | 0.0046891 | -0.10353 | 0.02173 | -0.011072 | 0.015058 | -0.0029308 | 0.013416 | 2.4261 | 2.4399 | 2.3529 | 2.4353 | 2.5909 | 2.3392 | 2.179 | 40.8371 | 40.9378 | 40.9332 | 40.8508 | 40.8005 | 8.7753 | 8.6792 | 84.6497 | 84.4894 | -38.2553 | 84.7504 | 84.7458 | 0.25635 | -38.4201 | 91.0858 | 90.9897 | 0.004578 | 123.1476 | 123.2437 | 32.254 | -0.045776 | 84.9014 | 84.7366 | 84.6634 | -38.6673 | 123.1613 | 123.111 | 123.2483 | -32.1671
2067.5156 | 123.2895 | -82.3288 | 40.86 | 0.027466 | 0.018226 | 0.00029489 | 0.013463 | -0.018271 | 0.0031894 | 0.0025529 | 0.064316 | 0.019593 | -0.012354 | 0.014631 | -0.0012218 | 0.01427 | 2.3895 | 2.3849 | 2.2934 | 2.3895 | 2.5543 | 2.3346 | 2.1698 | 40.8142 | 40.892 | 40.8966 | 40.8737 | 40.8142 | 8.7753 | 8.6746 | 84.6634 | 84.4986 | -38.3057 | 84.7137 | 84.7183 | 0.21973 | -38.4705 | 91.1041 | 91.0034 | 0.013733 | 123.143 | 123.2254 | 32.222 | -0.045776 | 84.8831 | 84.7183 | 84.6222 | -38.6902 | 123.2025 | 123.143 | 123.2208 | -32.1854
2068.5156 | 123.3078 | -82.3196 | 40.8783 | -0.15564 | 0.014381 | 0.0034991 | 0.013463 | -0.017203 | -0.00086945 | 0.0012711 | -0.11116 | 0.020021 | -0.012995 | 0.014204 | -0.0037854 | 0.012347 | 2.3529 | 2.3712 | 2.2842 | 2.3987 | 2.5635 | 2.3209 | 2.1606 | 40.8188 | 40.9378 | 40.9378 | 40.9149 | 40.8508 | 8.7799 | 8.6838 | 84.6405 | 84.4803 | -38.3148 | 84.6909 | 84.7183 | 0.23804 | -38.5254 | 91.0995 | 91.0034 | 0.036621 | 123.1384 | 123.2574 | 32.254 | -0.027466 | 84.8831 | 84.6725 | 84.6039 | -38.7177 | 123.2346 | 123.1705 | 123.2574 | -32.1945
2069.5156 | 123.3261 | -82.283 | 40.8646 | -0.079346 | 0.016731 | 0.0022175 | 0.012608 | -0.018698 | 0.001694 | 0.00063028 | 0.15587 | 0.018953 | -0.012995 | 0.013563 | -0.0027172 | 0.012561 | 2.4216 | 2.4216 | 2.33 | 2.4078 | 2.5726 | 2.33 | 2.1698 | 40.8966 | 40.9653 | 40.9515 | 40.8875 | 40.8463 | 8.7753 | 8.6792 | 84.613 | 84.4528 | -38.2919 | 84.7046 | 84.6909 | 0.23804 | -38.443 | 91.0583 | 90.9622 | 0.022888 | 123.1796 | 123.2346 | 32.2723 | -0.018311 | 84.8557 | 84.7046 | 84.613 | -38.6948 | 123.1705 | 123.1293 | 123.2483 | -32.1854
2070.5156 | 123.3078 | -82.3425 | 40.8371 | -0.13275 | 0.015877 | 0.00093569 | 0.013249 | -0.021903 | 0.0025486 | 0.0034073 | -0.034867 | 0.019166 | -0.011713 | 0.01399 | -0.0012218 | 0.011707 | 2.4033 | 2.4307 | 2.3209 | 2.417 | 2.5497 | 2.3392 | 2.1606 | 40.8325 | 40.7639 | 40.892 | 40.8417 | 40.7776 | 8.7753 | 8.6792 | 84.6817 | 84.5032 | -38.2874 | 84.7733 | 84.7595 | 0.25635 | -38.4338 | 91.1179 | 91.0217 | 0.004578 | 123.175 | 123.2346 | 32.2128 | -0.059509 | 84.8923 | 84.7458 | 84.6634 | -38.6765 | 123.1842 | 123.1201 | 123.1064 | -32.1579
2071.5156 | 123.3078 | -82.3837 | 40.8417 | 0.088501 | 0.01844 | 0.0015765 | 0.013249 | -0.019339 | 0.0027622 | 0.0025529 | 0.13298 | 0.021516 | -0.0078678 | 0.012922 | -0.00058103 | 0.011279 | 2.3209 | 2.298 | 2.2339 | 2.3529 | 2.5726 | 2.3026 | 2.1515 | 40.8005 | 40.3427 | 40.7822 | 40.773 | 40.7455 | 8.7708 | 8.6746 | 84.6863 | 84.5352 | -38.269 | 84.6817 | 84.7366 | 0.20142 | -38.5208 | 91.1545 | 91.0584 | -0.068665 | 123.1842 | 123.1659 | 32.1075 | -0.096131 | 84.9564 | 84.7046 | 84.6176 | -38.6902 | 123.1567 | 123.1293 | 122.7264 | -32.1671
2072.5156 | 123.3307 | -82.3608 | 40.8005 | -0.16327 | 0.016731 | 0.0034991 | 0.01389 | -0.020407 | 0.0038304 | 0.0042619 | -0.13405 | 0.021943 | -0.01214 | 0.012281 | -0.0029308 | 0.010852 | 2.3804 | 2.3895 | 2.2888 | 2.3987 | 2.5314 | 2.3254 | 2.1515 | 40.8051 | 40.9332 | 40.9058 | 40.8417 | 40.7913 | 8.7799 | 8.6838 | 84.6863 | 84.5123 | -38.269 | 84.7504 | 84.7595 | 0.24719 | -38.4201 | 91.1407 | 91.0446 | 0.041199 | 123.1659 | 123.2666 | 32.222 | -0.009155 | 84.8923 | 84.7412 | 84.6497 | -38.649 | 123.2025 | 123.1522 | 123.2941 | -32.1167
2073.5156 | 123.2986 | -82.3517 | 40.8051 | 0.012207 | 0.017586 | 0.0022175 | 0.013676 | -0.018271 | 0.0019078 | 0.0012711 | 0.049057 | 0.020662 | -0.012354 | 0.013563 | -0.0029308 | 0.013202 | 2.3987 | 2.3941 | 2.3026 | 2.3849 | 2.5269 | 2.3117 | 2.1423 | 40.8005 | 40.8737 | 40.8875 | 40.8279 | 40.8005 | 8.7799 | 8.6792 | 84.6634 | 84.494 | -38.2782 | 84.7458 | 84.7366 | 0.24262 | -38.4064 | 91.1316 | 91.0309 | 0.022888 | 123.1522 | 123.2391 | 32.2083 | -0.004578 | 84.8785 | 84.7504 | 84.6542 | -38.6627 | 123.1796 | 123.1522 | 123.2254 | -32.1259
2074.5156 | 123.262 | -82.3837 | 40.8371 | -0.32349 | 0.012672 | 0.0028583 | 0.010899 | -0.02233 | -0.00044225 | 0.0023391 | -0.095902 | 0.018525 | -0.0097904 | 0.011854 | -0.0054944 | 0.013629 | 2.3209 | 2.3712 | 2.2797 | 2.3804 | 2.5772 | 2.3483 | 2.1515 | 40.7593 | 40.8646 | 40.8737 | 40.8463 | 40.8142 | 8.7753 | 8.6838 | 84.7321 | 84.5352 | -38.2599 | 84.7549 | 84.7641 | 0.22888 | -38.5162 | 91.1591 | 91.0675 | 0.009155 | 123.143 | 123.2574 | 32.1899 | -0.022888 | 84.9609 | 84.7046 | 84.6634 | -38.6856 | 123.23 | 123.1979 | 123.2483 | -32.1533
2075.5156 | 123.3215 | -82.3654 | 40.7822 | -0.15564 | 0.016517 | -0.00055971 | 0.01624 | -0.019126 | 0.001694 | 0.00041648 | -0.12642 | 0.01938 | -0.0078678 | 0.013777 | -0.0048534 | 0.012561 | 2.3712 | 2.3941 | 2.2751 | 2.3987 | 2.5681 | 2.3209 | 2.1423 | 40.8096 | 40.9241 | 40.9012 | 40.8371 | 40.7639 | 8.7753 | 8.6746 | 84.6863 | 84.5078 | -38.2141 | 84.7595 | 84.7641 | 0.25635 | -38.4109 | 91.1407 | 91.04 | 0.054931 | 123.175 | 123.2666 | 32.2266 | -0.018311 | 84.9335 | 84.7366 | 84.6405 | -38.6398 | 123.2025 | 123.1293 | 123.2895 | -32.1075
2076.5156 | 123.2941 | -82.402 | 40.7776 | -0.18616 | 0.013313 | 0.0017901 | 0.01624 | -0.019339 | 0.00062595 | 0.0031937 | -0.17983 | 0.020234 | -0.01214 | 0.014204 | -0.0044262 | 0.012347 | 2.3438 | 2.3529 | 2.243 | 2.3712 | 2.5406 | 2.298 | 2.1378 | 40.7089 | 40.8371 | 40.8463 | 40.8005 | 40.7455 | 8.7799 | 8.6746 | 84.7 | 84.5398 | -38.237 | 84.7549 | 84.7733 | 0.23346 | -38.4338 | 91.1819 | 91.0767 | 0.022888 | 123.111 | 123.2483 | 32.1716 | -0.032044 | 84.9426 | 84.7458 | 84.6451 | -38.6398 | 123.2025 | 123.1476 | 123.2391 | -32.103
2077.5156 | 123.2986 | -82.4203 | 40.773 | -0.010681 | 0.01609 | 0.0026447 | 0.015385 | -0.019553 | 0.0027622 | 0.0014847 | 0.0032804 | 0.021089 | -0.0080814 | 0.013349 | -0.0014356 | 0.012347 | 2.3895 | 2.3804 | 2.2842 | 2.3849 | 2.5406 | 2.3026 | 2.1332 | 40.7547 | 40.8463 | 40.8234 | 40.7684 | 40.7227 | 8.7845 | 8.6746 | 84.7229 | 84.5535 | -38.2324 | 84.8007 | 84.8053 | 0.25177 | -38.3835 | 91.2048 | 91.095 | -0.004577 | 123.175 | 123.2437 | 32.1487 | -0.050354 | 84.9609 | 84.8099 | 84.7046 | -38.6398 | 123.1888 | 123.143 | 123.2666 | -32.0984
2078.5156 | 123.3353 | -82.4112 | 40.7593 | -0.13275 | 0.014381 | 0.0022175 | 0.014317 | -0.018698 | 0.00083955 | 0.0027665 | -0.14168 | 0.018098 | -0.011286 | 0.012922 | -0.0025036 | 0.011493 | 2.3117 | 2.3529 | 2.2568 | 2.3483 | 2.5269 | 2.298 | 2.1011 | 40.7181 | 40.8508 | 40.8188 | 40.8051 | 40.7455 | 8.7753 | 8.67 | 84.7092 | 84.5123 | -38.2324 | 84.7641 | 84.7595 | 0.24719 | -38.4476 | 91.1865 | 91.0812 | 0.045777 | 123.1293 | 123.23 | 32.1487 | -0.013733 | 84.938 | 84.7229 | 84.668 | -38.6581 | 123.2162 | 123.1567 | 123.262 | -32.0892
2079.5156 | 123.2895 | -82.3975 | 40.7639 | -0.0030518 | 0.016517 | 0.0024311 | 0.01624 | -0.019553 | -1.505e-05 | 0.0044755 | 0.049057 | 0.020448 | -0.011927 | 0.015272 | -0.00058103 | 0.011066 | 2.3483 | 2.3575 | 2.2476 | 2.3529 | 2.5131 | 2.2934 | 2.1194 | 40.7455 | 40.8325 | 40.8279 | 40.7822 | 40.7455 | 8.7799 | 8.6838 | 84.6909 | 84.5169 | -38.2507 | 84.7549 | 84.7504 | 0.23346 | -38.4155 | 91.1774 | 91.0812 | 0.018311 | 123.143 | 123.2254 | 32.1442 | -0.018311 | 84.9106 | 84.7458 | 84.6451 | -38.6444 | 123.1796 | 123.143 | 123.23 | -32.0801
2080.5156 | 123.2849 | -82.4707 | 40.7501 | -0.10986 | 0.01374 | 0.0028583 | 0.010899 | -0.019339 | -0.0019376 | 0.0021255 | -0.11879 | 0.020234 | -0.013208 | 0.014845 | -0.003999 | 0.01427 | 2.2797 | 2.3163 | 2.2156 | 2.3254 | 2.5085 | 2.2659 | 2.0782 | 40.6677 | 40.7913 | 40.7959 | 40.773 | 40.7089 | 8.7753 | 8.6884 | 84.7366 | 84.549 | -38.2416 | 84.787 | 84.7961 | 0.24719 | -38.4705 | 91.246 | 91.1591 | 0.022888 | 123.1384 | 123.2666 | 32.1075 | -0.041199 | 84.9792 | 84.7504 | 84.6863 | -38.6719 | 123.2437 | 123.1796 | 123.262 | -32.0618
2081.5156 | 123.23 | -82.4203 | 40.773 | -0.13275 | 0.013527 | 0.0024311 | 0.011967 | -0.020194 | 0.0019078 | 0.0016983 | -0.0043486 | 0.01938 | -0.010218 | 0.013563 | -0.003999 | 0.010852 | 2.3026 | 2.3621 | 2.2522 | 2.3529 | 2.4948 | 2.2614 | 2.0691 | 40.7501 | 40.8417 | 40.8417 | 40.7455 | 40.7043 | 8.7845 | 8.6792 | 84.6817 | 84.4894 | -38.2782 | 84.7824 | 84.7733 | 0.28381 | -38.4705 | 91.2048 | 91.0995 | -0.027466 | 123.1705 | 123.262 | 32.1625 | -0.068664 | 84.9152 | 84.7229 | 84.6725 | -38.7039 | 123.1659 | 123.1247 | 123.262 | -32.0938
2082.5156 | 123.262 | -82.4478 | 40.7181 | 0.09613 | 0.018226 | 0.0030719 | 0.012394 | -0.017844 | 0.0021214 | 0.0036209 | 0.11009 | 0.018953 | -0.0091494 | 0.014845 | -0.0016492 | 0.012347 | 2.2293 | 2.243 | 2.1515 | 2.2842 | 2.4536 | 2.2247 | 2.0645 | 40.6677 | 40.7501 | 40.7501 | 40.773 | 40.7181 | 8.7845 | 8.67 | 84.6725 | 84.5123 | -38.2645 | 84.6909 | 84.7321 | 0.21973 | -38.4888 | 91.2323 | 91.1179 | 0.054931 | 123.1155 | 123.1979 | 32.0801 | 0 | 84.9014 | 84.6771 | 84.5993 | -38.6536 | 123.2208 | 123.1659 | 123.1979 | -32.048
2083.5156 | 123.3261 | -82.4478 | 40.7913 | -0.14801 | 0.015877 | 0.00072209 | 0.015172 | -0.019339 | 0.00041235 | 0.0040481 | -0.16457 | 0.017457 | -0.011499 | 0.013136 | -0.0029308 | 0.011066 | 2.2751 | 2.3117 | 2.211 | 2.3209 | 2.4536 | 2.243 | 2.0599 | 40.7135 | 40.86 | 40.8463 | 40.7776 | 40.7272 | 8.7845 | 8.6792 | 84.6909 | 84.5078 | -38.3377 | 84.7595 | 84.7687 | 0.26092 | -38.5162 | 91.2323 | 91.127 | -0.013733 | 123.1613 | 123.2941 | 32.1671 | -0.064087 | 84.9014 | 84.7229 | 84.6588 | -38.7314 | 123.2254 | 123.175 | 123.3078 | -32.1121
2084.5156 | 123.2941 | -82.457 | 40.7501 | -0.33112 | 0.013954 | 0.0032855 | 0.013463 | -0.018485 | -0.00022865 | 0.0016983 | -0.088272 | 0.01938 | -0.011499 | 0.013563 | -0.0037854 | 0.013843 | 2.2614 | 2.3026 | 2.2018 | 2.298 | 2.4902 | 2.2614 | 2.0874 | 40.6723 | 40.8051 | 40.7959 | 40.7501 | 40.7089 | 8.7753 | 8.6792 | 84.7183 | 84.5444 | -38.2599 | 84.7595 | 84.7549 | 0.21057 | -38.4888 | 91.2323 | 91.1362 | 0 | 123.1293 | 123.2529 | 32.1167 | -0.041199 | 84.9472 | 84.7183 | 84.6588 | -38.6627 | 123.2071 | 123.1659 | 123.262 | -32.0709
2085.5156 | 123.3215 | -82.4661 | 40.7135 | -0.11749 | 0.015663 | 0.0028583 | 0.013035 | -0.018698 | 0.0021214 | 0.0012711 | -0.095902 | 0.019166 | -0.0087222 | 0.014204 | -0.0033582 | 0.012347 | 2.2842 | 2.3209 | 2.2064 | 2.3117 | 2.4628 | 2.2293 | 2.0416 | 40.7043 | 40.8005 | 40.7867 | 40.7089 | 40.654 | 8.7708 | 8.6838 | 84.6954 | 84.5078 | -38.2507 | 84.787 | 84.7778 | 0.27008 | -38.4293 | 91.2369 | 91.1499 | -0.004578 | 123.1705 | 123.2529 | 32.103 | -0.059509 | 84.9289 | 84.7504 | 84.6725 | -38.6719 | 123.175 | 123.1201 | 123.2666 | -32.0297
2086.5156 | 123.2986 | -82.4982 | 40.7364 | -0.20142 | 0.012245 | 0.0026447 | 0.011326 | -0.017417 | -0.001083 | 0.00063028 | -1.5607 | 0.018312 | -0.0095768 | 0.015272 | -0.003999 | 0.013202 | 2.2339 | 2.3163 | 2.2018 | 2.2751 | 2.4719 | 2.2247 | 2.0737 | 40.6815 | 40.7455 | 40.7455 | 40.7318 | 40.6723 | 8.7799 | 8.6838 | 84.7229 | 84.5718 | -38.2645 | 84.8145 | 84.7733 | 0.20142 | -38.5025 | 91.2781 | 91.1819 | -0.004577 | 123.1796 | 123.2437 | 32.0618 | -0.064087 | 84.9701 | 84.7321 | 84.7 | -38.6627 | 123.23 | 123.1705 | 123.2437 | -32.0526
2087.5312 | 123.3719 | -82.5027 | 40.6631 | 0.18005 | 0.0094677 | 0.0041401 | 0.010899 | -0.018271 | -0.0081326 | 0.00084388 | 0.26268 | 0.018739 | -0.013422 | 0.011854 | -0.006776 | 0.013629 | 2.2797 | 2.3483 | 2.2476 | 2.3071 | 2.4445 | 2.2797 | 2.1057 | 40.6677 | 40.7455 | 40.7913 | 40.6494 | 40.6128 | 8.7753 | 8.6746 | 84.7824 | 84.6085 | -38.2187 | 84.8511 | 84.8099 | 0.20142 | -38.3835 | 91.2781 | 91.1774 | -0.013733 | 123.1705 | 123.2941 | 32.1167 | -0.050354 | 84.9472 | 84.7824 | 84.7504 | -38.5574 | 123.1522 | 123.1155 | 123.2483 | -31.9885
2088.5156 | 123.3765 | -82.4844 | 40.654 | -0.18616 | 0.0098951 | 0.0030719 | 0.014531 | -0.018271 | -0.0017238 | 0.0016983 | -0.11879 | 0.020021 | -0.012781 | 0.012281 | -0.0029308 | 0.01192 | 2.3209 | 2.3987 | 2.2888 | 2.3621 | 2.4536 | 2.2476 | 2.0874 | 40.6952 | 40.8279 | 40.8188 | 40.6677 | 40.6036 | 8.7891 | 8.6792 | 84.7321 | 84.5718 | -38.2004 | 84.8831 | 84.8465 | 0.27466 | -38.3331 | 91.2735 | 91.1636 | 0.013733 | 123.1796 | 123.3032 | 32.1396 | -0.050354 | 84.938 | 84.8053 | 84.7733 | -38.5666 | 123.1522 | 123.0881 | 123.3124 | -31.9748
2089.5156 | 123.2941 | -82.5394 | 40.6448 | -0.18616 | 0.013527 | 0.0020037 | 0.015599 | -0.021048 | 0.0012668 | 0.0021255 | -0.45448 | 0.019593 | -0.013208 | 0.013563 | -0.003999 | 0.011066 | 2.2614 | 2.298 | 2.1973 | 2.3163 | 2.4994 | 2.2522 | 2.0828 | 40.5945 | 40.6723 | 40.6906 | 40.686 | 40.6128 | 8.7845 | 8.6838 | 84.7916 | 84.6222 | -38.1454 | 84.8373 | 84.8557 | 0.23346 | -38.3835 | 91.3239 | 91.2231 | 0.041199 | 123.1338 | 123.23 | 32.0068 | -0.032043 | 85.0388 | 84.8007 | 84.7366 | -38.562 | 123.2254 | 123.1522 | 123.2117 | -31.9611
2090.5156 | 123.262 | -82.5439 | 40.6769 | -0.25482 | 0.013099 | 0.0043537 | 0.012822 | -0.019553 | 0.00041235 | 0.00063028 | -0.19508 | 0.01938 | -0.011072 | 0.014204 | -0.0020764 | 0.010638 | 2.2614 | 2.3071 | 2.1927 | 2.2797 | 2.4719 | 2.2476 | 2.0691 | 40.7318 | 40.8005 | 40.5991 | 40.6998 | 40.6403 | 8.7845 | 8.6792 | 84.7916 | 84.613 | -38.205 | 84.8511 | 84.8236 | 0.21057 | -38.4155 | 91.3284 | 91.2231 | 0.022888 | 123.2758 | 123.143 | 31.9199 | -0.036621 | 85.0159 | 84.8053 | 84.7366 | -38.6078 | 123.2437 | 123.1842 | 123.3444 | -31.9977
2091.5156 | 123.3444 | -82.5348 | 40.6403 | -0.10986 | 0.016304 | 0.0034991 | 0.014531 | -0.018485 | 0.0036166 | 0.00041648 | -0.21797 | 0.019166 | -0.010858 | 0.013777 | -0.0033582 | 0.0095703 | 2.2522 | 2.2797 | 2.1744 | 2.2797 | 2.4536 | 2.211 | 2.0508 | 40.6128 | 40.7501 | 40.7181 | 40.6677 | 40.5853 | 8.7799 | 8.67 | 84.7458 | 84.5856 | -38.1866 | 84.8145 | 84.8145 | 0.22888 | -38.3881 | 91.3147 | 91.2048 | 0.027466 | 123.1476 | 123.2529 | 32.048 | -0.054932 | 84.9884 | 84.787 | 84.7092 | -38.5895 | 123.2025 | 123.1201 | 123.2849 | -31.9702
2092.5156 | 123.3078 | -82.5394 | 40.6586 | 0.012207 | 0.016517 | 0.0020037 | 0.014317 | -0.018485 | 0.0029758 | 0.0038345 | 0.14061 | 0.01938 | -0.01214 | 0.016554 | -0.0025036 | 0.011066 | 2.2339 | 2.2247 | 2.1332 | 2.2385 | 2.4445 | 2.2018 | 2.0233 | 40.6082 | 40.654 | 40.686 | 40.6769 | 40.6082 | 8.7753 | 8.6792 | 84.7412 | 84.5627 | -38.2141 | 84.7641 | 84.7778 | 0.21515 | -38.4247 | 91.3147 | 91.2186 | 0.018311 | 123.1476 | 123.2254 | 32.0068 | -0.050354 | 84.9838 | 84.7733 | 84.6725 | -38.6353 | 123.2162 | 123.1476 | 123.1934 | -31.9794
2093.5156 | 123.3124 | -82.5348 | 40.6906 | -0.17853 | 0.016517 | 0.0037127 | 0.014103 | -0.018912 | 0.0010532 | 0.0023391 | -0.17983 | 0.021302 | -0.012567 | 0.013136 | -0.0031446 | 0.010638 | 2.2522 | 2.2614 | 2.1698 | 2.2842 | 2.449 | 2.2064 | 2.0279 | 40.6174 | 40.7181 | 40.7227 | 40.6998 | 40.6494 | 8.7845 | 8.6838 | 84.7412 | 84.5627 | -38.2416 | 84.7961 | 84.819 | 0.25635 | -38.4384 | 91.3193 | 91.2186 | 0.009155 | 123.1522 | 123.2574 | 32.0389 | -0.041199 | 84.9838 | 84.787 | 84.7046 | -38.6627 | 123.2346 | 123.1842 | 123.2529 | -32.0068
2094.5156 | 123.3353 | -82.5211 | 40.654 | -0.20142 | 0.010536 | 0.0054217 | 0.01154 | -0.021262 | -0.0025784 | 0.0034073 | -0.12642 | 0.018953 | -0.016199 | 0.013563 | -0.0050672 | 0.011707 | 2.2934 | 2.3758 | 2.2614 | 2.33 | 2.417 | 2.2568 | 2.0828 | 40.6494 | 40.7776 | 40.7684 | 40.6219 | 40.5899 | 8.7845 | 8.6792 | 84.7778 | 84.6039 | -38.237 | 84.8969 | 84.8511 | 0.24719 | -38.3606 | 91.3055 | 91.2003 | -0.032044 | 123.1705 | 123.2895 | 32.0892 | -0.064087 | 84.938 | 84.8145 | 84.7824 | -38.5712 | 123.143 | 123.111 | 123.2986 | -31.9748
2095.5156 | 123.3307 | -82.5943 | 40.5762 | -0.16327 | 0.015877 | 0.0030719 | 0.015385 | -0.019553 | 0.00041235 | 0.0025529 | -0.19508 | 0.018525 | -0.0095768 | 0.015486 | -0.0020764 | 0.0089295 | 2.2293 | 2.2705 | 2.1835 | 2.2842 | 2.4399 | 2.1881 | 2.0325 | 40.5716 | 40.6906 | 40.6631 | 40.6128 | 40.5212 | 8.7845 | 8.6746 | 84.7824 | 84.6268 | -38.1363 | 84.8648 | 84.8785 | 0.25177 | -38.3469 | 91.3788 | 91.2689 | 0.036621 | 123.1659 | 123.2574 | 31.9885 | -0.054932 | 85.0342 | 84.8236 | 84.7778 | -38.5437 | 123.2071 | 123.1155 | 123.2849 | -31.9016
2096.5156 | 123.3902 | -82.5714 | 40.5716 | -0.14038 | 0.0088269 | 0.0058491 | 0.011326 | -0.021689 | -0.0049282 | 0.0027665 | -0.13405 | 0.017884 | -0.015558 | 0.015058 | -0.0061352 | 0.0095703 | 2.298 | 2.4033 | 2.2659 | 2.3483 | 2.4078 | 2.2247 | 2.0691 | 40.6082 | 40.7593 | 40.7455 | 40.535 | 40.4846 | 8.7845 | 8.6884 | 84.7961 | 84.6405 | -38.1638 | 84.9747 | 84.9197 | 0.27924 | -38.2736 | 91.3559 | 91.2598 | -0.036621 | 123.1796 | 123.317 | 32.0572 | -0.086975 | 84.9792 | 84.8694 | 84.8373 | -38.5025 | 123.1064 | 123.056 | 123.3307 | -31.8832
2097.5156 | 123.3124 | -82.5806 | 40.5991 | -0.20905 | 0.014595 | 0.00029489 | 0.017521 | -0.020194 | 0.0029758 | 0.0031937 | -0.13405 | 0.018953 | -0.0089358 | 0.013136 | -0.0044262 | 0.0091431 | 2.2156 | 2.2659 | 2.1515 | 2.2797 | 2.4399 | 2.2018 | 2.0233 | 40.5304 | 40.6586 | 40.6403 | 40.6082 | 40.5167 | 8.7799 | 8.6792 | 84.7824 | 84.6039 | -38.1592 | 84.8465 | 84.8602 | 0.25635 | -38.3835 | 91.3605 | 91.2598 | 0.009155 | 123.111 | 123.2208 | 31.9611 | -0.082397 | 85.0204 | 84.7961 | 84.7321 | -38.5757 | 123.1888 | 123.0972 | 123.2391 | -31.9199
2098.5156 | 123.3398 | -82.576 | 40.5945 | -0.19379 | 0.011818 | 0.0037127 | 0.013035 | -0.017417 | -0.00086945 | 0.0010575 | -0.13405 | 0.019166 | -0.013208 | 0.013349 | -0.0037854 | 0.011707 | 2.2934 | 2.3575 | 2.2385 | 2.3163 | 2.4124 | 2.211 | 2.0462 | 40.6082 | 40.7455 | 40.7181 | 40.6219 | 40.5441 | 8.7845 | 8.6792 | 84.787 | 84.6222 | -38.1821 | 84.9335 | 84.8923 | 0.27008 | -38.3011 | 91.3605 | 91.2552 | 0.027466 | 123.1842 | 123.2941 | 32.0389 | -0.050354 | 84.9884 | 84.8694 | 84.8145 | -38.5483 | 123.1979 | 123.1201 | 123.3215 | -31.9153
2099.5156 | 123.2758 | -82.6126 | 40.6036 | -0.10223 | 0.014808 | 0.0028583 | 0.017521 | -0.018912 | 0.0014804 | 0.00041648 | -0.1722 | 0.018739 | -0.009363 | 0.013136 | -0.0025036 | 0.0095703 | 2.243 | 2.2568 | 2.1515 | 2.2659 | 2.4536 | 2.211 | 2.0325 | 40.535 | 40.6448 | 40.6265 | 40.6082 | 40.5029 | 8.7845 | 8.6792 | 84.8236 | 84.6451 | -38.15 | 84.8694 | 84.8785 | 0.23346 | -38.3606 | 91.3971 | 91.2918 | 0.004577 | 123.1476 | 123.2391 | 31.9473 | -0.10071 | 85.0662 | 84.8557 | 84.7641 | -38.5712 | 123.2208 | 123.1155 | 123.2574 | -31.9244
2100.5156 | 123.381 | -82.5806 | 40.567 | -0.14038 | 0.0096813 | 0.0017901 | 0.013035 | -0.020407 | -0.0040738 | 0.0021255 | -0.11116 | 0.018525 | -0.010645 | 0.011854 | -0.0018628 | 0.013416 | 2.2751 | 2.3758 | 2.2614 | 2.3254 | 2.4124 | 2.2293 | 2.0645 | 40.5853 | 40.7364 | 40.7364 | 40.5258 | 40.4892 | 8.7753 | 8.6792 | 84.8099 | 84.6451 | -38.1546 | 84.9564 | 84.906 | 0.26092 | -38.2919 | 91.3559 | 91.2598 | -0.041199 | 123.1659 | 123.317 | 32.0572 | -0.07782 | 84.993 | 84.8557 | 84.8419 | -38.5025 | 123.1064 | 123.0698 | 123.317 | -31.8878
2101.5156 | 123.3536 | -82.6263 | 40.5808 | -0.14801 | 0.015663 | 0.0032855 | 0.015385 | -0.016776 | 0.003403 | 0.0016983 | -0.13405 | 0.020021 | -0.012567 | 0.013777 | -0.0012218 | 0.010638 | 2.243 | 2.2705 | 2.1698 | 2.2705 | 2.4078 | 2.1744 | 2.0142 | 40.5762 | 40.6769 | 40.6403 | 40.5808 | 40.4938 | 8.7845 | 8.6838 | 84.8007 | 84.6405 | -38.1729 | 84.8969 | 84.8969 | 0.25635 | -38.3377 | 91.4108 | 91.3101 | 0 | 123.2025 | 123.2666 | 31.9565 | -0.086976 | 85.0342 | 84.8694 | 84.7961 | -38.5666 | 123.2071 | 123.1201 | 123.3032 | -31.897
2102.5156 | 123.4039 | -82.6263 | 40.5212 | -0.29297 | 0.0077587 | 0.0024311 | 0.011754 | -0.019339 | -0.0030056 | 0.00084388 | -0.057755 | 0.016816 | -0.011286 | 0.014845 | -0.0054944 | 0.012775 | 2.2888 | 2.3804 | 2.2659 | 2.3071 | 2.3621 | 2.2064 | 2.037 | 40.5899 | 40.7364 | 40.7272 | 40.535 | 40.448 | 8.7891 | 8.6746 | 84.8328 | 84.6634 | -38.1592 | 85.0067 | 84.9335 | 0.27008 | -38.2324 | 91.4154 | 91.301 | 0.013733 | 123.2162 | 123.3536 | 32.0526 | -0.073242 | 84.9884 | 84.9152 | 84.8923 | -38.4842 | 123.1613 | 123.0743 | 123.3627 | -31.8466
2103.5156 | 123.2941 | -82.6538 | 40.5487 | -0.086975 | 0.013099 | 0.00050849 | 0.016667 | -0.016562 | -1.505e-05 | 0.0029801 | -0.17983 | 0.019807 | -0.012995 | 0.012708 | -0.0044262 | 0.011493 | 2.243 | 2.2247 | 2.1286 | 2.2476 | 2.4307 | 2.179 | 2.005 | 40.4846 | 40.5945 | 40.5808 | 40.5808 | 40.5121 | 8.7845 | 8.6746 | 84.8328 | 84.6588 | -38.118 | 84.8785 | 84.9014 | 0.24261 | -38.3057 | 91.4383 | 91.3284 | 0.032044 | 123.1384 | 123.2346 | 31.9061 | -0.036621 | 85.0845 | 84.8969 | 84.7824 | -38.5437 | 123.2346 | 123.1659 | 123.2483 | -31.8741
2104.5156 | 123.3765 | -82.6675 | 40.5212 | -0.12512 | 0.01075 | 0.0028583 | 0.012394 | -0.018698 | -0.0021512 | 0.00063028 | -0.11879 | 0.017244 | -0.014063 | 0.013136 | -0.0035718 | 0.012988 | 2.2934 | 2.3758 | 2.2568 | 2.3254 | 2.3895 | 2.2247 | 2.0782 | 40.5624 | 40.6952 | 40.6586 | 40.5121 | 40.4572 | 8.7891 | 8.6792 | 84.8923 | 84.7458 | -38.1317 | 85.0433 | 84.993 | 0.24719 | -38.2278 | 91.4566 | 91.3467 | -0.009155 | 123.23 | 123.3261 | 31.9794 | -0.064087 | 85.0571 | 84.9609 | 84.9243 | -38.443 | 123.1796 | 123.1247 | 123.3627 | -31.842
2105.5156 | 123.3307 | -82.6859 | 40.5441 | -0.17853 | 0.013527 | 0.0056353 | 0.013463 | -0.01763 | 0.0025486 | 0.0027665 | -0.17983 | 0.020448 | -0.010858 | 0.013349 | -0.00229 | 0.010638 | 2.2202 | 2.2339 | 2.1378 | 2.2247 | 2.4216 | 2.1698 | 2.0096 | 40.4892 | 40.6174 | 40.5899 | 40.567 | 40.4892 | 8.7845 | 8.6746 | 84.8557 | 84.6954 | -38.1226 | 84.9197 | 84.9106 | 0.21515 | -38.324 | 91.4703 | 91.3605 | 0.022889 | 123.175 | 123.2758 | 31.9153 | -0.054931 | 85.1074 | 84.906 | 84.8236 | -38.5345 | 123.2529 | 123.175 | 123.3032 | -31.8695
2106.5156 | 123.3994 | -82.6263 | 40.5029 | 0.09613 | 0.010536 | 0.0043537 | 0.01389 | -0.01528 | -0.0030056 | 0.0027665 | -0.073013 | 0.016816 | -0.014704 | 0.012922 | -0.0035718 | 0.010852 | 2.2797 | 2.3758 | 2.2614 | 2.3117 | 2.3758 | 2.2156 | 2.0279 | 40.567 | 40.7272 | 40.6998 | 40.4938 | 40.4526 | 8.7799 | 8.6838 | 84.8419 | 84.6542 | -38.1271 | 85.0021 | 84.9381 | 0.28381 | -38.2233 | 91.4062 | 91.3101 | -0.009156 | 123.1934 | 123.3261 | 32.016 | -0.050354 | 85.0021 | 84.906 | 84.8877 | -38.475 | 123.1201 | 123.0789 | 123.3536 | -31.8192
2107.5156 | 123.2391 | -82.6492 | 40.5533 | -0.1709 | 0.011177 | 0.0020037 | 0.014531 | -0.020194 | 0.00062595 | 0.0019119 | -0.14931 | 0.018312 | -0.012781 | 0.01399 | -0.0050672 | 0.013416 | 2.1973 | 2.243 | 2.1606 | 2.243 | 2.4261 | 2.1835 | 2.0142 | 40.4938 | 40.5853 | 40.5716 | 40.5487 | 40.48 | 8.7753 | 8.6792 | 84.8328 | 84.6634 | -38.1271 | 84.8923 | 84.8923 | 0.22888 | -38.356 | 91.4246 | 91.3284 | -0.004578 | 123.143 | 123.2208 | 31.8924 | -0.073242 | 85.0754 | 84.8465 | 84.8099 | -38.5391 | 123.1979 | 123.1293 | 123.2346 | -31.8741
2108.5156 | 123.4222 | -82.6767 | 40.4663 | -0.11749 | 0.0098951 | 0.0026447 | 0.011326 | -0.020194 | -0.0015102 | -0.0012923 | -0.21797 | 0.018953 | -0.013636 | 0.011854 | -0.0059216 | 0.012347 | 2.4857 | 2.3392 | 2.0691 | 2.1652 | 2.3666 | 2.1881 | 2.037 | 40.5624 | 40.6815 | 40.6494 | 40.4617 | 40.4205 | 8.7845 | 8.6792 | 84.8648 | 84.7137 | -38.0997 | 85.0159 | 84.8419 | 0.12817 | -37.9807 | 91.4612 | 91.3559 | -0.004578 | 123.2391 | 123.3261 | 31.9702 | -0.045777 | 85.0433 | 85.1624 | 84.7458 | -38.4293 | 123.1384 | 123.0972 | 123.3582 | -31.7871
2109.5156 | 123.3948 | -82.6309 | 40.5258 | -0.11749 | 0.010322 | 0.0037127 | 0.013463 | -0.02233 | 0.0012668 | 0.0014847 | -0.14168 | 0.018312 | -0.012781 | 0.014631 | -0.0029308 | 0.010211 | 2.298 | 2.3712 | 2.2476 | 2.3071 | 2.3804 | 2.211 | 2.0416 | 40.5762 | 40.7043 | 40.7043 | 40.5258 | 40.4251 | 8.7799 | 8.6792 | 84.8419 | 84.6725 | -38.1454 | 85.0021 | 84.938 | 0.2655 | -38.2278 | 91.4108 | 91.3101 | 0 | 123.2071 | 123.3353 | 32.0251 | -0.10071 | 85.0113 | 84.9289 | 84.8785 | -38.4842 | 123.1567 | 123.056 | 123.3353 | -31.8466
2110.5156 | 123.436 | -82.6859 | 40.4434 | -0.02594 | 0.0077587 | 0.0030719 | 0.012394 | -0.020194 | -0.0021512 | -0.00022432 | 0.033798 | 0.017884 | -0.013849 | 0.011854 | -0.0050672 | 0.012561 | 2.2797 | 2.3346 | 2.2339 | 2.2842 | 2.3849 | 2.2064 | 2.0599 | 40.5533 | 40.6448 | 40.6586 | 40.4663 | 40.361 | 8.7799 | 8.6746 | 84.8923 | 84.7458 | -38.0585 | 85.0204 | 84.9701 | 0.2243 | -38.1638 | 91.4658 | 91.3605 | 0.022889 | 123.2391 | 123.3444 | 31.9839 | -0.082397 | 85.0708 | 84.9655 | 84.9197 | -38.3835 | 123.1522 | 123.0469 | 123.3307 | -31.7688
2111.5156 | 123.3032 | -82.7499 | 40.4572 | -0.12512 | 0.013313 | 0.0037127 | 0.01624 | -0.017844 | 0.0012668 | 0.0012711 | -0.18745 | 0.018312 | -0.013422 | 0.014204 | -0.0048534 | 0.0097839 | 2.243 | 2.2476 | 2.1378 | 2.243 | 2.4353 | 2.179 | 2.0142 | 40.4343 | 40.5212 | 40.5075 | 40.4938 | 40.4022 | 8.7799 | 8.6792 | 84.9289 | 84.7641 | -38.0219 | 84.9976 | 84.993 | 0.22888 | -38.2141 | 91.5298 | 91.4291 | 0.036621 | 123.1842 | 123.2574 | 31.8283 | -0.054931 | 85.1852 | 84.993 | 84.8877 | -38.443 | 123.2437 | 123.1522 | 123.2712 | -31.778
2112.5156 | 123.3353 | -82.7408 | 40.4251 | -0.18616 | 0.0098951 | 0.0054217 | 0.010258 | -0.018485 | -0.0017238 | 0.0021255 | -0.13405 | 0.01938 | -0.013849 | 0.012495 | -0.0044262 | 0.0099975 | 2.2888 | 2.3666 | 2.2385 | 2.3026 | 2.3895 | 2.2018 | 2.0279 | 40.4572 | 40.5762 | 40.5579 | 40.416 | 40.3473 | 8.7845 | 8.6884 | 84.9426 | 84.7687 | -38.0356 | 85.1074 | 85.0433 | 0.27466 | -38.1363 | 91.5253 | 91.4291 | -0.009155 | 123.1979 | 123.2986 | 31.8695 | -0.07782 | 85.1303 | 85.0296 | 84.9792 | -38.3972 | 123.1567 | 123.0881 | 123.317 | -31.7368
2113.5156 | 123.2849 | -82.7866 | 40.4205 | -0.20905 | 0.011604 | 0.0041401 | 0.011967 | -0.020407 | 0.00083955 | 0.0027665 | -0.24849 | 0.019166 | -0.014063 | 0.013563 | -0.0042126 | 0.012988 | 2.2385 | 2.2751 | 2.1561 | 2.2614 | 2.3941 | 2.1881 | 2.0187 | 40.4068 | 40.5167 | 40.4892 | 40.448 | 40.3931 | 8.7799 | 8.6838 | 84.9747 | 84.8053 | -38.0264 | 85.0616 | 85.0479 | 0.24262 | -38.1821 | 91.5665 | 91.4703 | 0.027466 | 123.1934 | 123.2758 | 31.8054 | -0.027466 | 85.1807 | 85.025 | 84.9426 | -38.4018 | 123.2346 | 123.1796 | 123.3032 | -31.7368
2114.5156 | 123.4085 | -82.7225 | 40.4205 | -0.071716 | 0.0092541 | 0.0037127 | 0.012822 | -0.018057 | -0.0012966 | 0.00041648 | -0.065384 | 0.017244 | -0.015131 | 0.014204 | -0.00058103 | 0.013202 | 2.2888 | 2.4216 | 2.2568 | 2.3071 | 2.3621 | 2.1927 | 2.0233 | 40.361 | 40.7181 | 40.567 | 40.3976 | 40.3107 | 8.7799 | 8.6792 | 84.9152 | 84.7458 | -38.0585 | 85.144 | 85.0296 | 0.28381 | -38.1317 | 91.5024 | 91.4017 | -0.022888 | 123.0835 | 123.2895 | 31.8878 | -0.10986 | 85.0845 | 85.0113 | 84.9792 | -38.3972 | 123.1201 | 123.0331 | 123.4406 | -31.7413
2115.5156 | 123.3353 | -82.7499 | 40.4251 | -0.20142 | 0.010536 | 0.0058491 | 0.013463 | -0.019126 | 0.003403 | 0.0034073 | -0.1722 | 0.018739 | -0.01214 | 0.013136 | -0.003999 | 0.010638 | 2.2522 | 2.33 | 2.2156 | 2.2797 | 2.3987 | 2.179 | 2.0233 | 40.4297 | 40.567 | 40.5304 | 40.4251 | 40.3519 | 8.7845 | 8.6884 | 84.9289 | 84.7733 | -38.0264 | 85.08 | 85.0296 | 0.25635 | -38.1729 | 91.5344 | 91.4383 | 0 | 123.1796 | 123.2803 | 31.842 | -0.073242 | 85.1486 | 85.0021 | 84.9655 | -38.4018 | 123.175 | 123.1018 | 123.317 | -31.7368
2116.5156 | 123.3994 | -82.7682 | 40.361 | 0.012207 | 0.0096813 | 0.0034991 | 0.014744 | -0.018698 | -0.0023648 | 0.0021255 | -0.0043486 | 0.016603 | -0.015772 | 0.013136 | -0.003999 | 0.010852 | 2.2247 | 2.3117 | 2.1973 | 2.2751 | 2.3849 | 2.2064 | 2.037 | 40.4526 | 40.5533 | 40.5762 | 40.3656 | 40.2832 | 8.7799 | 8.67 | 84.9747 | 84.8053 | -37.9761 | 85.08 | 85.0433 | 0.23804 | -38.1363 | 91.5482 | 91.4383 | 0.004578 | 123.2208 | 123.3444 | 31.9061 | -0.07782 | 85.1532 | 84.993 | 84.9655 | -38.324 | 123.1339 | 123.0515 | 123.3215 | -31.691
2117.5156 | 123.4177 | -82.7133 | 40.3839 | -0.094604 | 0.0077587 | 0.0041401 | 0.010899 | -0.019126 | 0.00083955 | 0.0034073 | 0.48393 | 0.018525 | -0.013208 | 0.015913 | -0.0052808 | 0.0097839 | 2.3071 | 2.5452 | 2.4033 | 2.3163 | 2.3621 | 2.1881 | 2.0142 | 40.4938 | 40.6311 | 40.5945 | 40.3976 | 40.2969 | 8.7845 | 8.6884 | 84.9014 | 84.7275 | -38.0219 | 85.2585 | 85.0296 | 0.30212 | -38.0768 | 91.4978 | 91.4017 | 0.013733 | 123.2071 | 123.3078 | 31.9061 | -0.086975 | 85.0754 | 85.0204 | 85.1166 | -38.3698 | 123.111 | 123.0103 | 123.3444 | -31.6956
2118.5156 | 123.4085 | -82.7637 | 40.3656 | -0.086975 | 0.0060497 | 0.0032855 | 0.011326 | -0.016562 | 0.00019875 | 0.0019119 | -0.11116 | 0.016816 | -0.015345 | 0.010359 | -0.0010082 | 0.01192 | 2.298 | 2.3712 | 2.2339 | 2.2797 | 2.3529 | 2.1881 | 2.0279 | 40.329 | 40.654 | 40.567 | 40.3839 | 40.2695 | 8.7891 | 8.6792 | 84.9518 | 84.7916 | -38.0127 | 85.1349 | 85.0433 | 0.25177 | -38.0676 | 91.5527 | 91.4429 | 0.01831 | 123.0927 | 123.3307 | 31.8878 | -0.096131 | 85.1166 | 85.0616 | 84.9976 | -38.3377 | 123.1476 | 123.0331 | 123.4177 | -31.6864
2119.5156 | 123.2849 | -82.7728 | 40.416 | -0.10986 | 0.011604 | 0.0032855 | 0.014531 | -0.017844 | 0.002335 | 0.00041648 | -0.21034 | 0.021089 | -0.012354 | 0.013136 | -0.0048534 | 0.012561 | 2.2064 | 2.2156 | 2.1194 | 2.211 | 2.3987 | 2.1744 | 1.9867 | 40.3473 | 40.3885 | 40.4755 | 40.4343 | 40.3519 | 8.7753 | 8.6792 | 84.9472 | 84.7595 | -38.0173 | 84.9884 | 84.9838 | 0.22431 | -38.2095 | 91.5482 | 91.452 | 0.01831 | 123.1201 | 123.2483 | 31.7963 | -0.064087 | 85.1715 | 84.9792 | 84.8923 | -38.4293 | 123.2071 | 123.1247 | 123.1613 | -31.7368
2120.5156 | 123.4451 | -82.7866 | 40.3381 | -0.056458 | 0.0098951 | 0.0017901 | 0.011113 | -0.021262 | -0.0012966 | 0.00063028 | -0.11116 | 0.019807 | -0.01449 | 0.01399 | -0.0050672 | 0.013202 | 2.3026 | 2.3621 | 2.2247 | 2.2934 | 2.3712 | 2.2018 | 2.0325 | 40.4709 | 40.5991 | 40.5762 | 40.3473 | 40.2557 | 8.7845 | 8.6838 | 84.9884 | 84.819 | -37.9669 | 85.1486 | 85.08 | 0.26092 | -38.0356 | 91.571 | 91.4703 | 0.009155 | 123.2574 | 123.3627 | 31.8924 | -0.082398 | 85.1578 | 85.0891 | 85.0113 | -38.3057 | 123.1338 | 123.0423 | 123.3856 | -31.6544
2121.5156 | 123.3994 | -82.8003 | 40.3473 | -0.16327 | 0.010109 | 0.0028583 | 0.014317 | -0.019339 | -0.00022865 | 0.0044755 | -0.17983 | 0.019166 | -0.013636 | 0.012922 | -0.0035718 | 0.0095703 | 2.2797 | 2.3621 | 2.2385 | 2.3071 | 2.3758 | 2.1881 | 2.0233 | 40.4388 | 40.5487 | 40.5258 | 40.3702 | 40.2695 | 8.7845 | 8.6792 | 84.9884 | 84.8236 | -37.9715 | 85.1624 | 85.1074 | 0.28381 | -38.0676 | 91.5848 | 91.4795 | 0.022888 | 123.2391 | 123.3261 | 31.8466 | -0.07782 | 85.1761 | 85.08 | 85.0388 | -38.324 | 123.1705 | 123.0698 | 123.349 | -31.6681
2122.5156 | 123.4222 | -82.782 | 40.3427 | -0.018311 | 0.0064771 | 0.0041401 | 0.011754 | -0.019126 | -0.001083 | 0.0012711 | -0.019608 | 0.018312 | -0.014704 | 0.012281 | -0.0042126 | 0.010425 | 2.2568 | 2.3346 | 2.2202 | 2.2751 | 2.3483 | 2.1881 | 2.0187 | 40.4434 | 40.5533 | 40.5487 | 40.3427 | 40.2603 | 8.7753 | 8.6838 | 84.9701 | 84.8007 | -37.9944 | 85.1166 | 85.0571 | 0.25635 | -38.0859 | 91.5573 | 91.4658 | 0 | 123.2254 | 123.3307 | 31.8649 | -0.082397 | 85.1303 | 85.0388 | 85.0021 | -38.324 | 123.1247 | 123.0423 | 123.3353 | -31.6589
2123.5156 | 123.5367 | -82.7911 | 40.3152 | -0.079346 | 0.0073315 | 0.0043537 | 0.013463 | -0.019766 | -0.001083 | 0.0021255 | -0.080643 | 0.018525 | -0.012995 | 0.012495 | -0.0050672 | 0.010852 | 2.2842 | 2.3758 | 2.243 | 2.2888 | 2.3712 | 2.1881 | 2.0187 | 40.4709 | 40.5624 | 40.567 | 40.3244 | 40.2374 | 8.7799 | 8.6838 | 84.9792 | 84.8099 | -37.944 | 85.1669 | 85.08 | 0.27008 | -38.031 | 91.571 | 91.4749 | 0.009155 | 123.262 | 123.3582 | 31.8832 | -0.07782 | 85.1624 | 85.0754 | 85.0342 | -38.2965 | 123.1155 | 123.0286 | 123.3536 | -31.6315
2124.5156 | 123.381 | -82.8232 | 40.3015 | 0.057983 | 0.0079723 | 0.0039263 | 0.01389 | -0.020194 | -0.0019376 | 0.0025529 | -0.27901 | 0.01703 | -0.012567 | 0.013136 | -0.0037854 | 0.011066 | 2.1515 | 2.2705 | 2.0966 | 2.1561 | 2.3209 | 2.1378 | 1.9684 | 40.361 | 40.4388 | 40.448 | 40.3152 | 40.2237 | 8.7753 | 8.6792 | 84.9609 | 84.7916 | -37.9807 | 85.0937 | 84.9792 | 0.18768 | -38.15 | 91.5985 | 91.5024 | 0.013733 | 123.1842 | 123.2712 | 31.7688 | -0.07782 | 85.144 | 84.9747 | 84.9197 | -38.3331 | 123.1384 | 123.0469 | 123.262 | -31.6223
2125.5156 | 123.3856 | -82.8232 | 40.3198 | -0.13275 | 0.010109 | 0.0024311 | 0.013249 | -0.020407 | 0.0010532 | 0.0016983 | -0.12642 | 0.017671 | -0.013208 | 0.012068 | -0.0044262 | 0.01192 | 2.2751 | 2.3621 | 2.2339 | 2.2797 | 2.3529 | 2.1652 | 2.0096 | 40.3885 | 40.5029 | 40.4846 | 40.3336 | 40.2283 | 8.7799 | 8.6838 | 84.9884 | 84.8328 | -37.9669 | 85.1852 | 85.1028 | 0.27008 | -38.0447 | 91.6031 | 91.507 | 0.013733 | 123.2117 | 123.3078 | 31.8008 | -0.091553 | 85.1761 | 85.0983 | 85.0571 | -38.3102 | 123.1567 | 123.0515 | 123.3261 | -31.636
2126.5156 | 123.4497 | -82.8278 | 40.3061 | -0.033569 | 0.0069043 | 0.0030719 | 0.01154 | -0.01763 | -0.0015102 | 0.00041648 | 0.01091 | 0.017457 | -0.015558 | 0.01399 | -0.0037854 | 0.012561 | 2.243 | 2.3163 | 2.2018 | 2.2614 | 2.3483 | 2.1606 | 2.0233 | 40.3839 | 40.4892 | 40.5075 | 40.2924 | 40.2237 | 8.7845 | 8.6838 | 84.9884 | 84.8511 | -37.9578 | 85.144 | 85.0891 | 0.23804 | -38.063 | 91.6122 | 91.5115 | -0.013733 | 123.2117 | 123.3353 | 31.8237 | -0.082397 | 85.1761 | 85.0708 | 85.0296 | -38.2828 | 123.1201 | 123.0515 | 123.317 | -31.6223
2127.5156 | 123.2895 | -82.8964 | 40.3244 | -0.1709 | 0.012886 | 0.0058491 | 0.01389 | -0.016989 | 0.0038304 | 0.0031937 | -0.19508 | 0.019166 | -0.011713 | 0.012495 | -0.0031446 | 0.0087157 | 2.1698 | 2.2339 | 2.0874 | 2.1973 | 2.3849 | 2.1194 | 1.9821 | 40.448 | 40.3976 | 40.274 | 40.3702 | 40.2466 | 8.7799 | 8.6792 | 85.0159 | 84.8785 | -37.9395 | 85.1303 | 85.0937 | 0.21515 | -38.1546 | 91.6763 | 91.5756 | 0.045776 | 123.3444 | 123.1705 | 31.5948 | -0.07782 | 85.2814 | 85.0662 | 84.9838 | -38.3423 | 123.2666 | 123.143 | 123.2941 | -31.6452
2128.5156 | 123.4085 | -82.8552 | 40.2603 | 0.035095 | 0.012245 | 0.0043537 | 0.012822 | -0.021475 | -0.0019376 | 0.0031937 | -0.011978 | 0.016389 | -0.013422 | 0.012922 | -0.0037854 | 0.01192 | 2.1835 | 2.2705 | 2.1561 | 2.2247 | 2.3071 | 2.1652 | 1.9867 | 40.3519 | 40.4343 | 40.4572 | 40.2557 | 40.1779 | 8.7799 | 8.6838 | 85.0204 | 84.8419 | -37.9532 | 85.1257 | 85.08 | 0.23804 | -38.0768 | 91.6351 | 91.539 | -0.004578 | 123.2071 | 123.3124 | 31.7734 | -0.082398 | 85.1624 | 85.0388 | 85.0113 | -38.2736 | 123.111 | 123.0331 | 123.2895 | -31.5765
2129.5156 | 123.4314 | -82.8781 | 40.2374 | -0.018311 | 0.0060497 | 0.0022175 | 0.014744 | -0.019553 | -0.00086945 | 0.0025529 | -0.011978 | 0.018953 | -0.010645 | 0.011213 | -0.0031446 | 0.011279 | 2.2888 | 2.3621 | 2.2293 | 2.2842 | 2.3438 | 2.1561 | 1.9958 | 40.329 | 40.4572 | 40.4572 | 40.2328 | 40.1505 | 8.7799 | 8.6884 | 85.0342 | 84.874 | -37.8937 | 85.2402 | 85.1624 | 0.28839 | -37.9486 | 91.658 | 91.5665 | -0.004578 | 123.2071 | 123.3353 | 31.7688 | -0.086975 | 85.2219 | 85.1669 | 85.1074 | -38.2416 | 123.111 | 123.0286 | 123.3353 | -31.5491
2130.5156 | 123.3902 | -82.8873 | 40.21 | 0.10376 | 0.012031 | 0.0060627 | 0.013676 | -0.018271 | 0.0014804 | 0.0044755 | 0.15587 | 0.016603 | -0.015131 | 0.01399 | -0.0025036 | 0.01192 | 2.211 | 2.2705 | 2.1561 | 2.211 | 2.33 | 2.1606 | 1.9821 | 40.2924 | 40.3519 | 40.3656 | 40.2191 | 40.1321 | 8.7799 | 8.6792 | 85.0479 | 84.8694 | -37.8799 | 85.1578 | 85.0983 | 0.22888 | -37.999 | 91.6672 | 91.5665 | 0.009155 | 123.1796 | 123.2529 | 31.6864 | -0.07782 | 85.2173 | 85.0983 | 85.0433 | -38.2278 | 123.1064 | 123.0194 | 123.2391 | -31.5308
2131.5156 | 123.3902 | -82.8964 | 40.2466 | 0.042725 | 0.0083997 | 0.0049945 | 0.012608 | -0.020194 | -0.00022865 | 0.0038345 | 0.018539 | 0.015962 | -0.014276 | 0.012495 | -0.0052808 | 0.011707 | 2.2156 | 2.2705 | 2.1561 | 2.2339 | 2.3346 | 2.1561 | 2.0004 | 40.3381 | 40.4114 | 40.4251 | 40.2695 | 40.1459 | 8.7891 | 8.6838 | 85.0525 | 84.8969 | -37.912 | 85.1669 | 85.1303 | 0.23346 | -38.031 | 91.6855 | 91.5802 | 0.022888 | 123.2346 | 123.3215 | 31.7413 | -0.10071 | 85.231 | 85.112 | 85.0525 | -38.2462 | 123.1659 | 123.0423 | 123.3078 | -31.5628
2132.5156 | 123.4131 | -82.9193 | 40.2054 | 0.10376 | 0.0083997 | 0.0034991 | 0.014317 | -0.01998 | -0.0015102 | 0.00084388 | 0.056686 | 0.017244 | -0.014276 | 0.012922 | -0.003999 | 0.010852 | 2.1973 | 2.2659 | 2.1515 | 2.211 | 2.3346 | 2.1561 | 1.9867 | 40.2924 | 40.3656 | 40.3702 | 40.2191 | 40.1001 | 8.7845 | 8.6746 | 85.0754 | 84.906 | -37.8708 | 85.1852 | 85.1303 | 0.22431 | -38.0081 | 91.7038 | 91.5939 | 0.013733 | 123.2117 | 123.2895 | 31.6956 | -0.10528 | 85.2539 | 85.1166 | 85.0708 | -38.2187 | 123.1384 | 123.0194 | 123.2849 | -31.5308
2133.5156 | 123.4589 | -82.9147 | 40.1871 | -0.033569 | 0.0079723 | 0.0039263 | 0.014958 | -0.019766 | 0.0019078 | 0.0012711 | -0.088272 | 0.016176 | -0.012781 | 0.014204 | -0.0027172 | 0.0076477 | 2.2705 | 2.3621 | 2.2064 | 2.2751 | 2.33 | 2.1744 | 2.0004 | 40.3748 | 40.4709 | 40.4755 | 40.2054 | 40.1276 | 8.7891 | 8.6838 | 85.0891 | 84.9152 | -37.8571 | 85.2768 | 85.1898 | 0.27466 | -37.9166 | 91.7038 | 91.5985 | 0.01831 | 123.2895 | 123.3902 | 31.7917 | -0.05951 | 85.2448 | 85.1852 | 85.1212 | -38.1866 | 123.1201 | 123.0423 | 123.3856 | -31.5033
2134.5156 | 123.3902 | -82.9788 | 40.155 | 0.088501 | 0.0064771 | 0.0030719 | 0.012822 | -0.021048 | -0.0012966 | 0.0023391 | 0.041427 | 0.018098 | -0.013422 | 0.012068 | -0.0035718 | 0.012347 | 2.1927 | 2.2797 | 2.037 | 2.1561 | 2.3117 | 2.1149 | 1.9455 | 40.2008 | 40.3061 | 40.3061 | 40.1779 | 40.0864 | 8.7845 | 8.6746 | 85.0937 | 84.9243 | -37.8433 | 85.2585 | 85.1349 | 0.21057 | -37.9623 | 91.7633 | 91.6534 | 0.022888 | 123.1796 | 123.2849 | 31.6315 | -0.068664 | 85.2905 | 85.1715 | 85.0159 | -38.2095 | 123.1567 | 123.0652 | 123.2849 | -31.4804
2135.5156 | 123.4131 | -82.8964 | 40.2054 | -0.02594 | 0.0083997 | 0.0064899 | 0.010045 | -0.020835 | 0.0010532 | 0.0025529 | -0.027237 | 0.017671 | -0.013849 | 0.012495 | -0.0052808 | 0.010425 | 2.2705 | 2.3209 | 2.2156 | 2.2522 | 2.3529 | 2.1698 | 2.005 | 40.3198 | 40.4114 | 40.4205 | 40.2191 | 40.1138 | 8.7845 | 8.6792 | 85.0662 | 84.9014 | -37.8525 | 85.2173 | 85.1486 | 0.24719 | -37.9349 | 91.6809 | 91.5756 | 0.013733 | 123.2162 | 123.317 | 31.7413 | -0.091552 | 85.2493 | 85.1669 | 85.112 | -38.2004 | 123.1155 | 123.0103 | 123.3078 | -31.5262
2136.5156 | 123.3582 | -82.9468 | 40.1779 | 0.18768 | 0.0090405 | 0.0037127 | 0.010899 | -0.020194 | -0.00044225 | 0.0051163 | 0.12535 | 0.017671 | -0.013422 | 0.013777 | -0.00229 | 0.013629 | 2.2247 | 2.2705 | 2.1423 | 2.2156 | 2.3254 | 2.1606 | 1.9913 | 40.2649 | 40.3061 | 40.329 | 40.1917 | 40.0864 | 8.7753 | 8.6792 | 85.1074 | 84.938 | -37.8525 | 85.2173 | 85.1624 | 0.2243 | -37.9532 | 91.7221 | 91.626 | 0.013733 | 123.2117 | 123.2758 | 31.6498 | -0.091552 | 85.2722 | 85.1715 | 85.0891 | -38.1866 | 123.1384 | 123.0331 | 123.2529 | -31.4987
2137.5156 | 123.3582 | -82.988 | 40.1505 | 0.088501 | 0.0075451 | 0.0020037 | 0.010899 | -0.018698 | 0.00041235 | 0.0036209 | 0.10246 | 0.01703 | -0.013208 | 0.014417 | -0.0025036 | 0.011493 | 2.1927 | 2.1652 | 2.0325 | 2.1561 | 2.2888 | 2.1103 | 1.9592 | 40.1779 | 40.2786 | 40.3015 | 40.1459 | 40.0589 | 8.7753 | 8.6792 | 85.0983 | 84.9472 | -37.8616 | 85.1532 | 85.144 | 0.19684 | -37.9578 | 91.7633 | 91.6672 | -0.004578 | 123.1659 | 123.2895 | 31.6223 | -0.091553 | 85.2768 | 85.1807 | 85.0204 | -38.1912 | 123.1338 | 123.0469 | 123.2666 | -31.4713
2138.5156 | 123.4177 | -83.02 | 40.0909 | 0.35553 | 0.010963 | 0.0022175 | 0.011754 | -0.01998 | 0.002335 | 0.0029801 | 0.15587 | 0.018525 | -0.01214 | 0.015272 | -0.0031446 | 0.010852 | 2.2797 | 2.2842 | 2.1698 | 2.2202 | 2.2888 | 2.1286 | 1.973 | 40.2466 | 40.2969 | 40.3061 | 40.123 | 40.036 | 8.7891 | 8.6838 | 85.1486 | 84.993 | -37.8021 | 85.3043 | 85.2402 | 0.24719 | -37.8113 | 91.8091 | 91.7038 | 0.032044 | 123.2666 | 123.3261 | 31.6223 | -0.054931 | 85.3088 | 85.2997 | 85.1898 | -38.118 | 123.143 | 123.056 | 123.317 | -31.4072
2139.5156 | 123.4085 | -83.0246 | 40.1459 | -0.0030518 | 0.0092541 | 0.0058491 | 0.012822 | -0.019766 | -0.001083 | 0.0014847 | -0.034867 | 0.018098 | -0.012567 | 0.012068 | -0.0033582 | 0.012988 | 2.2293 | 2.2934 | 2.1835 | 2.2522 | 2.3529 | 2.1561 | 1.9867 | 40.2649 | 40.3381 | 40.3381 | 40.1642 | 40.0589 | 8.7799 | 8.6838 | 85.1807 | 85.0113 | -37.793 | 85.318 | 85.2768 | 0.2655 | -37.9166 | 91.8045 | 91.7084 | 0.018311 | 123.2895 | 123.3627 | 31.6544 | -0.086975 | 85.3775 | 85.2539 | 85.2081 | -38.1592 | 123.1888 | 123.0835 | 123.3627 | -31.4621
2140.5156 | 123.3902 | -82.988 | 40.1413 | 0.17242 | 0.010536 | 0.0032855 | 0.014103 | -0.021048 | 0.00083955 | 0.0049027 | 0.17876 | 0.018739 | -0.010004 | 0.014417 | -0.0029308 | 0.010852 | 2.2568 | 2.3026 | 2.179 | 2.2293 | 2.3346 | 2.1744 | 2.0004 | 40.242 | 40.2878 | 40.3152 | 40.1321 | 40.0681 | 8.7799 | 8.6792 | 85.1624 | 84.9884 | -37.8067 | 85.2905 | 85.2173 | 0.22888 | -37.8845 | 91.7679 | 91.6672 | -0.009155 | 123.23 | 123.3032 | 31.636 | -0.073242 | 85.3226 | 85.2448 | 85.1669 | -38.1409 | 123.1201 | 123.056 | 123.2758 | -31.4621
2141.5156 | 123.3856 | -83.0704 | 40.0726 | -0.37689 | 0.0075451 | 0.0034991 | 0.010258 | -0.020407 | -0.001083 | 0.0021255 | 0.041427 | 0.018525 | -0.013422 | 0.012068 | -0.0031446 | 0.010852 | 2.1973 | 2.2476 | 2.1561 | 2.2247 | 2.3254 | 2.1423 | 1.9638 | 40.1413 | 40.2328 | 40.2466 | 40.0955 | 39.9902 | 8.7799 | 8.6838 | 85.2127 | 85.0342 | -37.7472 | 85.318 | 85.2951 | 0.26092 | -37.8754 | 91.8503 | 91.7542 | 0.022888 | 123.2117 | 123.317 | 31.5628 | -0.082398 | 85.3958 | 85.2676 | 85.2264 | -38.1088 | 123.1659 | 123.0606 | 123.3032 | -31.3889
2142.5156 | 123.4039 | -83.0429 | 40.0452 | 0.14954 | 0.015663 | 0.0028583 | 0.011113 | -0.018057 | 0.002335 | 0.0040481 | 0.17876 | 0.018953 | -0.011713 | 0.012922 | -0.00079463 | 0.012134 | 2.2705 | 2.2934 | 2.1835 | 2.2202 | 2.3026 | 2.1561 | 1.9867 | 40.2054 | 40.2649 | 40.274 | 40.0818 | 39.9673 | 8.7936 | 8.6838 | 85.199 | 85.0296 | -37.7426 | 85.3363 | 85.2631 | 0.23346 | -37.7747 | 91.8365 | 91.7267 | 0.036621 | 123.2483 | 123.317 | 31.5903 | -0.07782 | 85.3455 | 85.3134 | 85.2264 | -38.0585 | 123.1247 | 123.0103 | 123.3078 | -31.3614
2143.5156 | 123.4497 | -83.0566 | 40.036 | 0.14191 | 0.0092541 | 0.0024311 | 0.010045 | -0.019766 | 0.00041235 | -1.0724e-05 | 0.079574 | 0.018312 | -0.014063 | 0.011854 | -0.0035718 | 0.012134 | 2.1927 | 2.2476 | 2.1286 | 2.1881 | 2.3209 | 2.1423 | 1.9913 | 40.1459 | 40.2054 | 40.242 | 40.0955 | 40.004 | 8.7799 | 8.6792 | 85.199 | 85.0479 | -37.7151 | 85.3043 | 85.2448 | 0.19684 | -37.8433 | 91.8365 | 91.7358 | 0.059509 | 123.2025 | 123.2986 | 31.5628 | -0.032044 | 85.3775 | 85.2493 | 85.1852 | -38.0447 | 123.1522 | 123.0606 | 123.262 | -31.3568
2144.5156 | 123.4039 | -83.075 | 40.0543 | 0.2182 | 0.014168 | 0.0024311 | 0.011967 | -0.018912 | 0.005112 | 0.0059707 | 0.15587 | 0.021516 | -0.01449 | 0.012922 | -0.0010082 | 0.010638 | 2.211 | 2.1835 | 2.092 | 2.1744 | 2.3254 | 2.1194 | 1.9409 | 40.1596 | 40.1825 | 40.2145 | 40.1001 | 39.9857 | 8.7753 | 8.6838 | 85.1944 | 85.0159 | -37.7289 | 85.2585 | 85.2493 | 0.23346 | -37.8433 | 91.8503 | 91.7587 | 0.045777 | 123.2346 | 123.2895 | 31.5308 | -0.068664 | 85.4004 | 85.2859 | 85.1669 | -38.1134 | 123.175 | 123.0606 | 123.2574 | -31.3705
2145.5156 | 123.3673 | -83.1116 | 40.0223 | 0.13428 | 0.01139 | 0.0017901 | 0.009831 | -0.018485 | -0.0019376 | 0.0027665 | 0.094833 | 0.017244 | -0.014276 | 0.01399 | -0.0020764 | 0.013843 | 2.1835 | 2.2522 | 2.1423 | 2.1927 | 2.3163 | 2.1423 | 1.9913 | 40.123 | 40.2008 | 40.2466 | 40.0772 | 39.9948 | 8.7799 | 8.6838 | 85.2539 | 85.1028 | -37.706 | 85.3638 | 85.3043 | 0.20142 | -37.8387 | 91.8915 | 91.7953 | 0.054931 | 123.2346 | 123.3582 | 31.5628 | -0.027466 | 85.4279 | 85.2951 | 85.2539 | -38.031 | 123.1888 | 123.1064 | 123.3124 | -31.3385
2146.5156 | 123.4222 | -83.1024 | 39.9902 | 0.21057 | 0.012886 | 0.0013629 | 0.012181 | -0.018912 | 0.0029758 | 0.0031937 | -0.62996 | 0.017884 | -0.012354 | 0.01164 | -0.0012218 | 0.010425 | 2.2522 | 2.2659 | 2.1606 | 2.2293 | 2.3026 | 2.124 | 1.9638 | 40.1276 | 40.1825 | 40.2145 | 40.0131 | 39.9261 | 8.7845 | 8.6884 | 85.2264 | 85.0662 | -37.6877 | 85.3683 | 85.3317 | 0.2655 | -37.738 | 91.8869 | 91.7908 | 0.022889 | 123.23 | 123.317 | 31.5262 | -0.064087 | 85.405 | 85.3546 | 85.2631 | -38.0264 | 123.1155 | 123.0286 | 123.2849 | -31.3019
2147.5156 | 123.381 | -83.1436 | 40.0131 | 0.14954 | 0.011818 | 0.0041401 | 0.011113 | -0.018271 | -0.00086945 | 0.0029801 | 0.2169 | 0.020021 | -0.01449 | 0.013777 | -0.0027172 | 0.013629 | 2.2293 | 2.2659 | 2.1561 | 2.2064 | 2.2888 | 2.124 | 1.973 | 40.123 | 40.1596 | 40.1871 | 40.0085 | 39.949 | 8.7799 | 8.6746 | 85.2676 | 85.1166 | -37.7243 | 85.4095 | 85.35 | 0.23346 | -37.7838 | 91.9235 | 91.8182 | -0.004578 | 123.2666 | 123.3307 | 31.5125 | -0.064087 | 85.4324 | 85.3729 | 85.2997 | -38.0402 | 123.1522 | 123.0927 | 123.3032 | -31.3385
2148.5156 | 123.4085 | -83.0841 | 40.0452 | -0.010681 | 0.01075 | 0.0017901 | 0.011967 | -0.020194 | -0.001083 | 0.0016983 | 0.01091 | 0.018312 | -0.014276 | 0.013349 | -0.0063488 | 0.010638 | 2.2064 | 2.2522 | 2.1652 | 2.2064 | 2.3163 | 2.1286 | 1.973 | 40.1459 | 40.2328 | 40.2557 | 40.0681 | 39.9673 | 8.7845 | 8.6746 | 85.2127 | 85.0571 | -37.7289 | 85.3363 | 85.2905 | 0.23346 | -37.8387 | 91.8686 | 91.7587 | 0.022888 | 123.23 | 123.3398 | 31.5811 | -0.07782 | 85.4004 | 85.2905 | 85.2493 | -38.0722 | 123.1522 | 123.0515 | 123.317 | -31.3705
2149.5156 | 123.4222 | -83.1573 | 39.9628 | 0.088501 | 0.012672 | 0.0026447 | 0.010899 | -0.021689 | 0.0012668 | 0.0012711 | 0.20164 | 0.017244 | -0.014063 | 0.011427 | -0.00036743 | 0.010852 | 2.2339 | 2.2614 | 2.1606 | 2.2064 | 2.2797 | 2.1103 | 1.9684 | 40.1047 | 40.1779 | 40.1779 | 40.0269 | 39.8712 | 8.7891 | 8.6838 | 85.2676 | 85.1257 | -37.6831 | 85.4187 | 85.3638 | 0.23804 | -37.7289 | 91.9464 | 91.8411 | 0.064086 | 123.262 | 123.3353 | 31.4941 | -0.091553 | 85.437 | 85.3912 | 85.318 | -37.9944 | 123.1842 | 123.0286 | 123.3353 | -31.279
2150.5156 | 123.317 | -83.1894 | 39.9765 | 0.17242 | 0.016731 | 0.0026447 | 0.013676 | -0.020407 | 0.0053256 | 0.0036209 | 0.087204 | 0.020021 | -0.010431 | 0.012708 | -0.00036743 | 0.011707 | 2.1561 | 2.1194 | 2.0187 | 2.1149 | 2.3209 | 2.0737 | 1.918 | 39.9948 | 40.0131 | 40.0497 | 40.0314 | 39.9261 | 8.7753 | 8.6838 | 85.2631 | 85.1074 | -37.6556 | 85.3088 | 85.3043 | 0.19684 | -37.8204 | 91.9647 | 91.8732 | 0.054932 | 123.1842 | 123.2391 | 31.366 | -0.050354 | 85.5103 | 85.3455 | 85.2081 | -38.0585 | 123.2208 | 123.1155 | 123.2025 | -31.2927
2151.5156 | 123.3719 | -83.2077 | 39.9582 | 0.17242 | 0.015022 | 0.0024311 | 0.010045 | -0.018057 | 0.0036166 | 0.0055435 | 0.1635 | 0.019593 | -0.01214 | 0.011854 | -0.00058103 | 0.013416 | 2.1515 | 2.1423 | 2.0462 | 2.1332 | 2.3117 | 2.092 | 1.9318 | 40.0452 | 40.0726 | 40.1093 | 40.036 | 39.9261 | 8.7799 | 8.6746 | 85.2997 | 85.1395 | -37.6465 | 85.35 | 85.3409 | 0.20142 | -37.8067 | 91.9876 | 91.8823 | 0.07782 | 123.2529 | 123.317 | 31.4346 | -0.032044 | 85.5194 | 85.3592 | 85.2539 | -38.0264 | 123.2437 | 123.1338 | 123.2803 | -31.2836
2152.5156 | 123.2941 | -83.2581 | 39.9261 | 0.088501 | 0.01609 | 8.1086e-05 | 0.013035 | -0.017203 | 0.004044 | 0.0055435 | 0.82726 | 0.020021 | -0.011072 | 0.012495 | -0.0010082 | 0.010638 | 2.1011 | 2.0691 | 2.0142 | 2.0828 | 2.3117 | 2.0828 | 1.9043 | 39.9399 | 40.004 | 39.9765 | 39.9994 | 39.8987 | 8.7753 | 8.6838 | 85.3409 | 85.1624 | -37.6144 | 85.3271 | 85.3409 | 0.17853 | -37.825 | 92.0334 | 91.9418 | 0.073243 | 123.1979 | 123.2346 | 31.2927 | -0.027465 | 85.5698 | 85.3592 | 85.2722 | -38.0219 | 123.2574 | 123.1567 | 123.262 | -31.2424
2153.5312 | 123.4314 | -83.2123 | 39.9307 | -0.11749 | 0.011818 | 0.0060627 | 0.015385 | -0.019553 | -0.00086945 | 0.0036209 | -0.20271 | 0.01938 | -0.01449 | 0.012495 | -0.0050672 | 0.01427 | 2.1927 | 2.3026 | 2.1286 | 2.1927 | 2.2888 | 2.1194 | 1.9455 | 40.0177 | 40.1871 | 40.1505 | 39.9399 | 39.8346 | 8.7845 | 8.6838 | 85.3317 | 85.1578 | -37.6419 | 85.5148 | 85.405 | 0.24719 | -37.738 | 91.9968 | 91.8961 | 0.009155 | 123.23 | 123.3627 | 31.4667 | -0.09613 | 85.5011 | 85.405 | 85.3409 | -37.9852 | 123.1522 | 123.0469 | 123.3994 | -31.2469
2154.5156 | 123.4268 | -83.2352 | 39.8666 | 0.18768 | 0.016731 | 0.00093569 | 0.013463 | -0.021048 | 0.00041235 | 0.0027665 | 0.22453 | 0.019807 | -0.01214 | 0.010786 | -0.0018628 | 0.0093567 | 2.1744 | 2.1973 | 2.1011 | 2.1835 | 2.2751 | 2.092 | 1.9272 | 39.9994 | 40.0589 | 40.0772 | 39.9124 | 39.8026 | 8.7891 | 8.6838 | 85.3271 | 85.1624 | -37.5916 | 85.4324 | 85.4187 | 0.25635 | -37.6923 | 92.0242 | 91.9189 | 0.045777 | 123.2346 | 123.3124 | 31.3934 | -0.064087 | 85.5103 | 85.4095 | 85.3363 | -37.9395 | 123.1476 | 123.0377 | 123.2941 | -31.1829
2155.5156 | 123.4085 | -83.2489 | 39.8529 | 0.22583 | 0.014381 | 0.00050849 | 0.01154 | -0.018485 | 0.0031894 | 0.0038345 | 0.14061 | 0.019593 | -0.011713 | 0.013136 | -0.0033582 | 0.011279 | 2.1606 | 2.1561 | 2.0554 | 2.1423 | 2.298 | 2.092 | 1.9272 | 39.9582 | 40.0223 | 40.0406 | 39.9033 | 39.8346 | 8.7845 | 8.6884 | 85.3409 | 85.1761 | -37.5549 | 85.405 | 85.3912 | 0.21515 | -37.6923 | 92.0334 | 91.9373 | 0.050354 | 123.2071 | 123.2895 | 31.3522 | -0.01831 | 85.5469 | 85.4095 | 85.3043 | -37.9257 | 123.1522 | 123.0835 | 123.2712 | -31.1646
2156.5156 | 123.2803 | -83.3038 | 39.9078 | 0.09613 | 0.018867 | 0.0028583 | 0.013463 | -0.019553 | 0.005753 | 0.0042619 | 0.018539 | 0.021089 | -0.010645 | 0.01399 | -0.0033582 | 0.0089295 | 2.1194 | 2.0782 | 2.0096 | 2.1286 | 2.3026 | 2.0645 | 1.9089 | 39.83 | 39.9307 | 39.9353 | 39.9445 | 39.8712 | 8.7753 | 8.6838 | 85.3683 | 85.2127 | -37.6053 | 85.3821 | 85.4324 | 0.21973 | -37.7884 | 92.0792 | 91.9876 | 0.036621 | 123.1338 | 123.2391 | 31.2515 | -0.036621 | 85.6064 | 85.4233 | 85.3134 | -37.999 | 123.2483 | 123.175 | 123.2346 | -31.2241
2157.5156 | 123.3398 | -83.3359 | 39.8712 | 0.12665 | 0.018654 | 0.0011493 | 0.010685 | -0.021262 | 0.00062595 | 0.0040481 | 0.17113 | 0.018739 | -0.010858 | 0.013777 | -0.0025036 | 0.010425 | 2.1194 | 2.0874 | 2.005 | 2.1103 | 2.3209 | 2.0554 | 1.8997 | 39.8712 | 39.8987 | 39.949 | 39.8804 | 39.8071 | 8.7753 | 8.6746 | 85.3912 | 85.2356 | -37.5504 | 85.4233 | 85.4462 | 0.21057 | -37.7518 | 92.1112 | 92.0105 | 0.009155 | 123.2071 | 123.2849 | 31.2744 | -0.064087 | 85.6567 | 85.4553 | 85.3409 | -37.9715 | 123.2162 | 123.143 | 123.2346 | -31.1966
2158.5312 | 123.3673 | -83.2901 | 39.8621 | -0.15564 | 0.012031 | 0.0047809 | 0.012181 | -0.018485 | -0.0023648 | 0.0019119 | -0.14931 | 0.019807 | -0.014704 | 0.012495 | -0.0042126 | 0.01427 | 2.1927 | 2.2522 | 2.1515 | 2.211 | 2.2888 | 2.1149 | 1.9409 | 39.9033 | 40.0589 | 40.036 | 39.8804 | 39.8163 | 8.7845 | 8.6838 | 85.405 | 85.231 | -37.5732 | 85.5423 | 85.5011 | 0.27008 | -37.6694 | 92.0746 | 91.9739 | 0.01831 | 123.1934 | 123.3261 | 31.3522 | -0.045777 | 85.5789 | 85.4828 | 85.4416 | -37.9211 | 123.1705 | 123.1064 | 123.349 | -31.1783
2159.5156 | 123.317 | -83.345 | 39.8483 | 0.15717 | 0.015236 | 0.0015765 | 0.013463 | -0.017844 | 0.002335 | 0.0038345 | 0.11009 | 0.01938 | -0.011286 | 0.014631 | -0.0014356 | 0.0087157 | 2.211 | 1.9821 | 1.9958 | 2.2888 | 2.3026 | 2.0874 | 1.9135 | 39.8209 | 39.8941 | 39.8987 | 39.8941 | 39.7888 | 8.7753 | 8.6838 | 85.4324 | 85.2585 | -37.5458 | 85.3271 | 85.6339 | 0.37537 | -37.6373 | 92.1204 | 92.0288 | 0.045776 | 123.1659 | 123.2437 | 31.2149 | -0.05951 | 85.6476 | 85.556 | 85.3409 | -37.9349 | 123.2391 | 123.1338 | 123.2391 | -31.1646
2160.5156 | 123.2986 | -83.3359 | 39.8621 | 0.088501 | 0.018013 | 0.0026447 | 0.013463 | -0.019553 | 0.0029758 | 0.0025529 | -0.0043486 | 0.020021 | -0.010431 | 0.013777 | -0.0025036 | 0.011279 | 2.124 | 2.1011 | 2.0233 | 2.124 | 2.2888 | 2.0554 | 1.8997 | 39.83 | 39.9216 | 39.917 | 39.9307 | 39.8163 | 8.7799 | 8.6746 | 85.3912 | 85.2356 | -37.5732 | 85.437 | 85.4599 | 0.2243 | -37.738 | 92.1158 | 92.0105 | 0.068664 | 123.1659 | 123.2529 | 31.2424 | -0.045777 | 85.6247 | 85.4599 | 85.3592 | -37.9623 | 123.2666 | 123.1522 | 123.2574 | -31.1874
2161.5156 | 123.381 | -83.3405 | 39.7934 | 0.2182 | 0.015877 | 0.0024311 | 0.015172 | -0.021048 | 0.0010532 | 0.0044755 | 0.2169 | 0.019807 | -0.0095768 | 0.015486 | -0.0048534 | 0.012347 | 2.1011 | 2.1194 | 2.0187 | 2.1286 | 2.2842 | 2.0599 | 1.8906 | 39.8666 | 39.917 | 39.949 | 39.8438 | 39.7797 | 8.7799 | 8.6838 | 85.4004 | 85.231 | -37.5092 | 85.4599 | 85.4691 | 0.23804 | -37.6923 | 92.1204 | 92.0242 | 0.050354 | 123.2071 | 123.2895 | 31.2653 | -0.013733 | 85.6247 | 85.4416 | 85.3592 | -37.9028 | 123.1842 | 123.1201 | 123.2574 | -31.1096
2162.5156 | 123.2941 | -83.3771 | 39.8163 | -0.02594 | 0.017158 | 0.0024311 | 0.014531 | -0.019766 | 0.0038304 | 0.0042619 | 0.018539 | 0.020234 | -0.009363 | 0.013563 | -0.00036743 | 0.011066 | 2.1561 | 2.1378 | 2.0325 | 2.1423 | 2.2934 | 2.0874 | 1.8906 | 39.8071 | 39.9078 | 39.8712 | 39.8346 | 39.7934 | 8.7799 | 8.6838 | 85.4645 | 85.2676 | -37.5229 | 85.5148 | 85.5194 | 0.25177 | -37.6602 | 92.157 | 92.0609 | 0.018311 | 123.1842 | 123.2483 | 31.1874 | -0.022888 | 85.6705 | 85.5331 | 85.4095 | -37.9257 | 123.2117 | 123.1705 | 123.2849 | -31.1325
2163.5156 | 123.3948 | -83.345 | 39.8163 | 0.065613 | 0.0096813 | -0.033885 | 0.0096174 | -0.019553 | -0.0070644 | 0.0016983 | 0.15587 | 0.016389 | -0.015131 | 0.012708 | -0.0052808 | 0.015125 | 2.1194 | 2.0737 | 2.0966 | 2.1194 | 2.2247 | 2.0554 | 1.8906 | 39.8209 | 39.9261 | 39.9857 | 39.8209 | 39.7339 | 8.7708 | 8.6792 | 85.4004 | 85.2356 | -37.5916 | 85.4187 | 85.4645 | 0.22888 | -37.6968 | 92.1158 | 92.0242 | 0.004578 | 123.1659 | 123.3307 | 31.3065 | -0.082397 | 85.5698 | 85.4645 | 85.4416 | -37.9257 | 123.1659 | 123.0789 | 123.2712 | -31.1371
2164.5156 | 123.3398 | -83.4 | 39.798 | -0.10986 | 0.017158 | 0.0043537 | 0.013249 | -0.016562 | 0.0027622 | 0.0025529 | -0.1722 | 0.020234 | -0.011286 | 0.010786 | -0.0018628 | 0.01192 | 2.1561 | 2.1469 | 2.0462 | 2.1515 | 2.3026 | 2.0737 | 1.9089 | 39.8163 | 39.9124 | 39.9033 | 39.8483 | 39.7476 | 8.7845 | 8.6838 | 85.4736 | 85.3088 | -37.4954 | 85.5469 | 85.5515 | 0.24261 | -37.6419 | 92.1844 | 92.0837 | 0.050354 | 123.2162 | 123.3032 | 31.2195 | -0.050354 | 85.7025 | 85.556 | 85.4462 | -37.8891 | 123.2483 | 123.1476 | 123.3124 | -31.1142
2165.5156 | 123.3215 | -83.4045 | 39.8163 | -0.018311 | 0.017586 | 0.0028583 | 0.012822 | -0.018912 | 0.0027622 | 0.0029801 | -0.027237 | 0.020021 | -0.010645 | 0.01399 | 5.9768e-05 | 0.012347 | 2.1423 | 2.1469 | 2.037 | 2.1423 | 2.2888 | 2.0508 | 1.8951 | 39.7934 | 39.8666 | 39.8575 | 39.83 | 39.7522 | 8.7753 | 8.6792 | 85.4553 | 85.2997 | -37.5275 | 85.5515 | 85.5469 | 0.24719 | -37.674 | 92.1799 | 92.0837 | 0.013733 | 123.1979 | 123.262 | 31.1783 | -0.064087 | 85.6934 | 85.5469 | 85.4416 | -37.9211 | 123.2346 | 123.1567 | 123.2712 | -31.1371
2166.5156 | 123.349 | -83.4091 | 39.7934 | 0.17242 | 0.017586 | 0.0015765 | 0.018589 | -0.022116 | 0.00083955 | 0.0036209 | -0.050125 | 0.02173 | -0.011072 | 0.013349 | -0.0020764 | 0.01192 | 2.1515 | 2.1515 | 2.0554 | 2.1423 | 2.2797 | 2.0966 | 1.8997 | 39.7888 | 39.8804 | 39.8621 | 39.7934 | 39.7247 | 8.7845 | 8.6792 | 85.5057 | 85.3088 | -37.5137 | 85.5606 | 85.5515 | 0.24262 | -37.6419 | 92.1936 | 92.0883 | 0 | 123.1979 | 123.2712 | 31.1829 | -0.068665 | 85.6888 | 85.5606 | 85.4645 | -37.8937 | 123.2025 | 123.1338 | 123.2895 | -31.1142
2167.5156 | 123.3078 | -83.4274 | 39.7705 | -2.536 | 0.016517 | 0.00050849 | 0.013463 | -0.017844 | 0.002335 | 0.0049027 | 0.17876 | 0.018739 | -0.010858 | 0.014204 | -0.0031446 | 0.012347 | 2.0325 | 2.0828 | 1.973 | 2.0782 | 2.298 | 2.0599 | 1.8723 | 39.7385 | 39.7934 | 39.8117 | 39.7888 | 39.711 | 8.7753 | 8.6838 | 85.4874 | 85.2997 | -37.4725 | 85.5103 | 85.5057 | 0.20599 | -37.738 | 92.2028 | 92.1112 | 0.01831 | 123.1659 | 123.2391 | 31.1279 | -0.059509 | 85.7254 | 85.4599 | 85.4004 | -37.8983 | 123.2162 | 123.1384 | 123.2208 | -31.0867
2168.5156 | 123.3765 | -83.4183 | 39.7659 | -0.094604 | 0.016517 | 0.00029489 | 0.012181 | -0.020407 | 0.002335 | 0.0019119 | -0.057755 | 0.019807 | -0.010004 | 0.014204 | -0.0031446 | 0.012561 | 2.1286 | 2.1332 | 2.0279 | 2.1194 | 2.2614 | 2.0416 | 1.8768 | 39.7247 | 39.917 | 39.8575 | 39.7934 | 39.7293 | 8.7845 | 8.6838 | 85.4599 | 85.2951 | -37.5046 | 85.5515 | 85.5377 | 0.24262 | -37.6373 | 92.2028 | 92.1021 | 0.027466 | 123.143 | 123.2758 | 31.1737 | -0.036621 | 85.6796 | 85.5469 | 85.4462 | -37.8891 | 123.2117 | 123.1476 | 123.3353 | -31.0822
2169.5156 | 123.3261 | -83.4503 | 39.7293 | 0.11902 | 0.018226 | 0.0022175 | 0.014531 | -0.021262 | 0.00062595 | 0.0053299 | 0.15587 | 0.020448 | -0.010004 | 0.015699 | -0.0031446 | 0.018543 | 2.037 | 2.0187 | 1.9547 | 2.0645 | 2.2659 | 2.0462 | 1.8631 | 39.679 | 39.4226 | 39.949 | 39.7247 | 39.679 | 8.7799 | 8.6792 | 85.4965 | 85.3134 | -37.4634 | 85.4691 | 85.5148 | 0.20142 | -37.6923 | 92.2302 | 92.1295 | -0.004578 | 123.1293 | 123.3994 | 31.2698 | -0.050354 | 85.7162 | 85.4874 | 85.405 | -37.8662 | 123.175 | 123.1293 | 122.8729 | -31.0501
2170.5156 | 123.3719 | -83.4503 | 39.7293 | -0.12512 | 0.015663 | 0.0032855 | 0.013249 | -0.018698 | 0.0019078 | 0.0044755 | -0.12642 | 0.020234 | -0.01214 | 0.013563 | -0.0027172 | 0.011279 | 2.0874 | 2.1011 | 1.9958 | 2.1194 | 2.2568 | 2.037 | 1.8539 | 39.7568 | 39.8758 | 39.8163 | 39.7751 | 39.7247 | 8.7845 | 8.6838 | 85.4874 | 85.3043 | -37.4725 | 85.5515 | 85.5698 | 0.2655 | -37.6419 | 92.2348 | 92.1341 | 0.045776 | 123.2071 | 123.2666 | 31.1325 | -0.004578 | 85.7071 | 85.5377 | 85.4462 | -37.8754 | 123.2254 | 123.175 | 123.3261 | -31.0455
2171.5156 | 123.2986 | -83.5052 | 39.743 | 0.057983 | 0.019508 | 0.0011493 | 0.012608 | -0.020194 | 0.001694 | 0.0038345 | 0.10246 | 0.02173 | -0.013849 | 0.014204 | -0.0042126 | 0.011707 | 2.0599 | 2.0554 | 1.973 | 2.0691 | 2.2522 | 2.0233 | 1.8539 | 39.6515 | 39.7751 | 39.7385 | 39.7385 | 39.679 | 8.7799 | 8.6792 | 85.5286 | 85.3592 | -37.4908 | 85.5606 | 85.5743 | 0.21515 | -37.6831 | 92.2852 | 92.1844 | -0.004578 | 123.1567 | 123.2437 | 31.0593 | -0.064087 | 85.7574 | 85.5652 | 85.4782 | -37.8891 | 123.2437 | 123.1842 | 123.2803 | -31.0638
2172.5156 | 123.2986 | -83.4824 | 39.7476 | -0.18616 | 0.013313 | 0.0041401 | 0.013249 | -0.019126 | -0.00086945 | -0.0017197 | -0.18745 | 0.019166 | -0.011927 | 0.014204 | -0.0050672 | 0.014056 | 2.3254 | 1.9363 | 1.8951 | 2.0599 | 2.3346 | 2.0691 | 1.8997 | 39.6515 | 39.7659 | 39.7705 | 39.7614 | 39.7202 | 8.7845 | 8.6792 | 85.5515 | 85.3821 | -37.413 | 85.4187 | 85.5423 | 0.16022 | -37.4222 | 92.2668 | 92.1616 | 0.013733 | 123.1338 | 123.2529 | 31.0913 | -0.027466 | 85.817 | 85.8078 | 85.3775 | -37.8479 | 123.2437 | 123.2025 | 123.2483 | -31.0684
2173.5156 | 123.3627 | -83.4915 | 39.6927 | -0.064087 | 0.016304 | 0.0032855 | 0.014103 | -0.020621 | 0.00083955 | 0.0029801 | -1.0572 | 0.019807 | -0.011286 | 0.013777 | -0.0014356 | 0.011493 | 2.1103 | 2.1378 | 2.0325 | 2.1194 | 2.2659 | 2.0325 | 1.9043 | 39.7064 | 39.8346 | 39.798 | 39.711 | 39.6469 | 8.7845 | 8.6838 | 85.524 | 85.3958 | -37.4268 | 85.6293 | 85.611 | 0.21515 | -37.5824 | 92.276 | 92.1753 | 0.018311 | 123.1979 | 123.2895 | 31.1142 | -0.045776 | 85.7574 | 85.6018 | 85.524 | -37.7884 | 123.2025 | 123.1384 | 123.3261 | -31.0089
2174.5156 | 123.3444 | -83.5236 | 39.6835 | -0.14801 | 0.014381 | 0.0037127 | 0.013463 | -0.018912 | 0.0014804 | 0.0012711 | -0.11116 | 0.020234 | -0.012995 | 0.014631 | -0.0048534 | 0.012134 | 2.0554 | 2.0828 | 1.973 | 2.1057 | 2.2659 | 2.037 | 1.8539 | 39.6378 | 39.7797 | 39.7522 | 39.6881 | 39.6378 | 8.7845 | 8.6838 | 85.5606 | 85.3775 | -37.4176 | 85.6064 | 85.6293 | 0.25177 | -37.6282 | 92.308 | 92.2073 | 0.004577 | 123.1613 | 123.2758 | 31.0684 | -0.045777 | 85.7895 | 85.5789 | 85.4965 | -37.8296 | 123.2117 | 123.1613 | 123.3032 | -30.9998
2175.5156 | 123.3398 | -83.5464 | 39.6835 | -0.0030518 | 0.018867 | 0.00050849 | 0.014531 | -0.018485 | 0.0031894 | 0.0034073 | 0.041427 | 0.021089 | -0.010431 | 0.01399 | -0.0014356 | 0.01427 | 2.0782 | 2.0828 | 1.9958 | 2.0782 | 2.2522 | 2.0096 | 1.8494 | 39.6378 | 39.7385 | 39.7156 | 39.6698 | 39.6149 | 8.7799 | 8.6884 | 85.556 | 85.3958 | -37.4313 | 85.6293 | 85.6247 | 0.22888 | -37.6053 | 92.3264 | 92.2348 | -0.013733 | 123.1842 | 123.262 | 31.0272 | -0.068665 | 85.7986 | 85.6247 | 85.5423 | -37.8342 | 123.2162 | 123.1613 | 123.2849 | -30.9952
2176.5156 | 123.3353 | -83.5464 | 39.6561 | -0.28534 | 0.012245 | 0.0049945 | 0.014317 | -0.019339 | -0.0021512 | 0.0027665 | -0.13405 | 0.019166 | -0.012995 | 0.014204 | -0.0054944 | 0.0099975 | 2.0233 | 2.0828 | 1.9867 | 2.0737 | 2.2705 | 2.037 | 1.8631 | 39.5828 | 39.711 | 39.6927 | 39.6515 | 39.6194 | 8.7799 | 8.6838 | 85.5835 | 85.4095 | -37.3856 | 85.6293 | 85.6201 | 0.21057 | -37.6328 | 92.3264 | 92.2302 | -0.004578 | 123.1293 | 123.2391 | 31.0089 | -0.036621 | 85.817 | 85.5698 | 85.5331 | -37.793 | 123.1979 | 123.1659 | 123.2574 | -30.9723
2177.5156 | 123.3536 | -83.6014 | 39.6332 | -0.048828 | 0.018013 | -0.0054731 | 0.01624 | -0.017203 | 0.0066074 | 0.0027665 | -0.019608 | 0.019807 | -0.010218 | 0.013777 | -0.0035718 | 0.0099975 | 2.0966 | 2.1194 | 2.005 | 2.124 | 2.3071 | 2.0828 | 1.8951 | 39.6057 | 39.6881 | 39.6835 | 39.6103 | 39.5599 | 8.7799 | 8.6838 | 85.6842 | 85.4965 | -37.326 | 85.7208 | 85.7254 | 0.22888 | -37.5366 | 92.3813 | 92.2852 | -0.022888 | 123.2071 | 123.2849 | 30.9998 | -0.073242 | 85.9085 | 85.6979 | 85.6064 | -37.738 | 123.2117 | 123.1613 | 123.2895 | -30.9494
2178.5156 | 123.3719 | -83.5831 | 39.5966 | -0.20142 | 0.0092541 | 0.0011493 | 0.012394 | -0.019339 | -0.0038602 | 0.0016983 | -0.10353 | 0.017671 | -0.013422 | 0.012922 | -0.003999 | 0.014484 | 2.1057 | 2.2064 | 2.0828 | 2.1698 | 2.2522 | 2.0462 | 1.8906 | 39.6011 | 39.7476 | 39.7156 | 39.5828 | 39.5462 | 8.7799 | 8.6792 | 85.6293 | 85.4736 | -37.3444 | 85.7895 | 85.7529 | 0.27924 | -37.4908 | 92.363 | 92.2623 | -0.013733 | 123.1842 | 123.2986 | 31.0364 | -0.050354 | 85.8353 | 85.6888 | 85.6659 | -37.706 | 123.1659 | 123.1293 | 123.3307 | -30.9174
2179.5156 | 123.3627 | -83.6426 | 39.5782 | -0.11749 | 0.016731 | 0.0024311 | 0.016453 | -0.01998 | 0.0027622 | 0.0012711 | -0.21797 | 0.020021 | -0.010645 | 0.012708 | -0.00229 | 0.011066 | 2.1011 | 2.1194 | 2.0142 | 2.1194 | 2.2614 | 2.037 | 1.8539 | 39.5508 | 39.679 | 39.6378 | 39.5782 | 39.5096 | 8.7753 | 8.6792 | 85.6796 | 85.4965 | -37.3169 | 85.762 | 85.762 | 0.2655 | -37.4771 | 92.4179 | 92.3218 | 0 | 123.1934 | 123.2803 | 30.9586 | -0.068664 | 85.9039 | 85.7437 | 85.6567 | -37.7243 | 123.2208 | 123.1522 | 123.3215 | -30.899
2180.5156 | 123.317 | -83.638 | 39.6057 | -0.17853 | 0.01075 | 0.0022175 | 0.014103 | -0.018271 | -0.0019376 | 0.0042619 | -0.15694 | 0.018525 | -0.012781 | 0.011427 | -0.006776 | 0.0095703 | 2.0462 | 2.092 | 1.9913 | 2.092 | 2.2751 | 2.0279 | 1.8631 | 39.5233 | 39.6652 | 39.6606 | 39.6149 | 39.592 | 8.7799 | 8.6838 | 85.6659 | 85.5011 | -37.3306 | 85.73 | 85.73 | 0.22888 | -37.5595 | 92.4179 | 92.3218 | 0.009155 | 123.1613 | 123.2986 | 30.9769 | -0.013733 | 85.9131 | 85.6842 | 85.6293 | -37.7426 | 123.2529 | 123.23 | 123.3032 | -30.9219
2181.5156 | 123.3673 | -83.6563 | 39.5691 | -0.19379 | 0.012886 | 0.00072209 | 0.012394 | -0.018271 | -0.00065585 | 0.0025529 | -0.11116 | 0.018525 | -0.011927 | 0.013777 | -0.0033582 | 0.013202 | 2.0599 | 2.092 | 1.9913 | 2.1011 | 2.2705 | 2.0279 | 1.8585 | 39.505 | 39.624 | 39.6011 | 39.6103 | 39.5004 | 8.7845 | 8.6838 | 85.6842 | 85.5148 | -37.2986 | 85.7483 | 85.7574 | 0.24261 | -37.5092 | 92.4408 | 92.3401 | 0.041199 | 123.1613 | 123.2574 | 30.9174 | -0.068665 | 85.9268 | 85.7162 | 85.6476 | -37.7106 | 123.2666 | 123.1567 | 123.2803 | -30.8853
2182.5156 | 123.3719 | -83.6197 | 39.5782 | -0.20905 | 0.0090405 | 0.0022175 | 0.011326 | -0.018698 | -0.0012966 | -0.00043792 | -0.10353 | 0.019166 | -0.013208 | 0.016126 | -0.0052808 | 0.01192 | 2.1149 | 2.2064 | 2.0691 | 2.1606 | 2.2522 | 2.0554 | 1.8906 | 39.5554 | 39.6973 | 39.6835 | 39.5737 | 39.5004 | 8.7799 | 8.6838 | 85.675 | 85.5103 | -37.326 | 85.8261 | 85.7803 | 0.27008 | -37.4634 | 92.3996 | 92.3035 | -0.004578 | 123.175 | 123.3032 | 30.9998 | -0.07782 | 85.8719 | 85.7346 | 85.6888 | -37.6877 | 123.1934 | 123.1201 | 123.317 | -30.8945
2183.5156 | 123.3353 | -83.6014 | 39.6011 | -0.21667 | 0.012672 | 0.0047809 | 0.014531 | -0.019553 | 0.00062595 | 0.0027665 | -0.21797 | 0.018739 | -0.01214 | 0.01399 | -0.0048534 | 0.012347 | 2.0691 | 2.0966 | 1.9913 | 2.0828 | 2.3254 | 2.0691 | 1.8951 | 39.5325 | 39.6103 | 39.6057 | 39.5828 | 39.5279 | 8.7799 | 8.6792 | 85.6705 | 85.4965 | -37.2757 | 85.6979 | 85.6842 | 0.18768 | -37.532 | 92.3813 | 92.2806 | -0.01831 | 123.1338 | 123.2071 | 30.9265 | -0.073242 | 85.9268 | 85.6705 | 85.5927 | -37.706 | 123.1842 | 123.1293 | 123.2117 | -30.9219
2184.5156 | 123.4177 | -83.6014 | 39.5416 | -0.30823 | 0.010109 | 0.0030719 | 0.012608 | -0.019126 | -0.004501 | 0.0016983 | -0.073013 | 0.01703 | -0.011713 | 0.011213 | -0.005708 | 0.012775 | 2.1332 | 2.2476 | 2.1332 | 2.1744 | 2.2293 | 2.0645 | 1.8997 | 39.6057 | 39.7522 | 39.7064 | 39.537 | 39.473 | 8.7891 | 8.6792 | 85.6659 | 85.5011 | -37.3123 | 85.849 | 85.7758 | 0.27466 | -37.4084 | 92.3904 | 92.2806 | -0.004578 | 123.2071 | 123.3078 | 31.0272 | -0.068665 | 85.8307 | 85.7346 | 85.7346 | -37.6419 | 123.1384 | 123.0743 | 123.3536 | -30.8624
2185.5156 | 123.3124 | -83.7341 | 39.5233 | -0.19379 | 0.011604 | 0.0054217 | 0.014958 | -0.018698 | 0.0021214 | -1.0724e-05 | -0.23323 | 0.017884 | -0.010645 | 0.013136 | -0.0069898 | 0.010211 | 2.0828 | 2.092 | 1.973 | 2.0874 | 2.3254 | 2.0691 | 1.8723 | 39.4501 | 39.537 | 39.5462 | 39.5325 | 39.4592 | 8.7753 | 8.67 | 85.8032 | 85.6064 | -37.1979 | 85.8261 | 85.8215 | 0.21515 | -37.4405 | 92.5095 | 92.4042 | 0.009156 | 123.1842 | 123.2803 | 30.8762 | -0.064086 | 86.0596 | 85.817 | 85.7071 | -37.6511 | 123.2666 | 123.1934 | 123.2712 | -30.8533
2186.5156 | 123.3719 | -83.6929 | 39.4913 | -0.086975 | 0.0079723 | 0.0024311 | 0.011326 | -0.020835 | -0.0017238 | 0.00063028 | 0.018539 | 0.017244 | -0.011713 | 0.012068 | -0.0052808 | 0.010852 | 2.1469 | 2.2614 | 2.124 | 2.1881 | 2.2522 | 2.0691 | 1.9272 | 39.5416 | 39.6744 | 39.6835 | 39.4592 | 39.3768 | 8.7799 | 8.6746 | 85.762 | 85.6201 | -37.2391 | 85.9543 | 85.881 | 0.26093 | -37.3444 | 92.4728 | 92.3676 | -0.032043 | 123.2346 | 123.3765 | 31.0089 | -0.11444 | 85.9451 | 85.8398 | 85.817 | -37.5641 | 123.1522 | 123.0698 | 123.3673 | -30.8167
2187.5156 | 123.317 | -83.7067 | 39.5004 | -0.1709 | 0.012672 | 0.0028583 | 0.015172 | -0.019553 | 0.0012668 | 0.0019119 | -0.14168 | 0.019166 | -0.013636 | 0.013349 | -0.0035718 | 0.010425 | 2.0966 | 2.179 | 2.037 | 2.1286 | 2.2568 | 2.0416 | 1.8631 | 39.4547 | 39.5737 | 39.5279 | 39.4913 | 39.4272 | 8.7753 | 8.6838 | 85.7483 | 85.5698 | -37.2437 | 85.8856 | 85.8353 | 0.2655 | -37.4039 | 92.482 | 92.3904 | -0.009155 | 123.1613 | 123.2346 | 30.8441 | -0.073242 | 85.9634 | 85.8032 | 85.7437 | -37.6373 | 123.1979 | 123.1338 | 123.2803 | -30.8167
2188.5156 | 123.4222 | -83.6884 | 39.4547 | -0.1709 | 0.0077587 | 0.0037127 | 0.01389 | -0.019766 | -0.0017238 | 0.0021255 | -0.057755 | 0.017457 | -0.011927 | 0.012495 | -0.0046398 | 0.012561 | 2.1652 | 2.2568 | 2.1194 | 2.1744 | 2.2293 | 2.0554 | 1.8951 | 39.537 | 39.6698 | 39.624 | 39.4409 | 39.3814 | 8.7845 | 8.6838 | 85.7437 | 85.5835 | -37.2253 | 85.9451 | 85.8627 | 0.27923 | -37.2894 | 92.4728 | 92.3721 | -0.013733 | 123.2254 | 123.3124 | 30.9402 | -0.073242 | 85.9177 | 85.8536 | 85.8078 | -37.5595 | 123.1293 | 123.0698 | 123.3582 | -30.7709
2189.5156 | 123.4131 | -83.6746 | 39.4547 | -0.10223 | 0.0092541 | 0.0017901 | 0.0094038 | -0.019766 | -0.00022865 | 0.0016983 | -0.14168 | 0.017884 | -0.009363 | 0.012281 | -0.0035718 | 0.0099975 | 2.1423 | 2.2385 | 2.1057 | 2.1652 | 2.2202 | 2.0416 | 1.886 | 39.5279 | 39.6561 | 39.6194 | 39.4821 | 39.4043 | 8.7799 | 8.6792 | 85.7162 | 85.5606 | -37.2345 | 85.9131 | 85.8398 | 0.27924 | -37.3123 | 92.4545 | 92.3538 | 0.027466 | 123.2025 | 123.2941 | 30.9402 | -0.050354 | 85.8948 | 85.817 | 85.7803 | -37.5687 | 123.1567 | 123.0789 | 123.3307 | -30.7755
2190.5156 | 123.4177 | -83.7204 | 39.4318 | -0.018311 | 0.0071179 | 0.0045673 | 0.009831 | -0.018698 | -0.0019376 | 0.0019119 | 0.01091 | 0.015748 | -0.011927 | 0.014204 | -0.003999 | 0.011493 | 2.1057 | 2.1881 | 2.0737 | 2.1561 | 2.2339 | 2.0645 | 1.9043 | 39.505 | 39.6057 | 39.6149 | 39.4638 | 39.3585 | 8.7799 | 8.6838 | 85.7849 | 85.6247 | -37.1979 | 85.9085 | 85.8765 | 0.25177 | -37.326 | 92.5003 | 92.4042 | 0.032043 | 123.2254 | 123.3353 | 30.9311 | -0.073242 | 85.9543 | 85.8261 | 85.7941 | -37.5275 | 123.1842 | 123.0789 | 123.3261 | -30.748
2191.5156 | 123.436 | -83.725 | 39.4089 | -0.10986 | 0.0069043 | 0.0017901 | 0.012394 | -0.019553 | -0.0015102 | -0.00086512 | -0.33241 | 0.017457 | -0.009363 | 0.012281 | -0.0027172 | 0.011493 | 2.179 | 2.2842 | 2.1149 | 2.1835 | 2.2064 | 2.0645 | 1.9089 | 39.4913 | 39.592 | 39.6194 | 39.3951 | 39.3356 | 8.7799 | 8.6792 | 85.7895 | 85.6339 | -37.2025 | 86.0092 | 85.9085 | 0.27466 | -37.2299 | 92.5049 | 92.4042 | -0.013733 | 123.2162 | 123.3444 | 30.9402 | -0.073243 | 85.9314 | 85.9039 | 85.8398 | -37.5 | 123.1201 | 123.0606 | 123.317 | -30.7297
2192.5156 | 123.4222 | -83.7112 | 39.4135 | 0.0045777 | 0.0081861 | 0.0017901 | 0.0096174 | -0.01998 | -0.0023648 | 0.00063028 | 0.018539 | 0.014467 | -0.011499 | 0.015272 | -0.0042126 | 0.010211 | 2.1286 | 2.2064 | 2.0782 | 2.1515 | 2.243 | 2.0828 | 1.8951 | 39.505 | 39.5828 | 39.592 | 39.4226 | 39.3356 | 8.7891 | 8.6792 | 85.7941 | 85.6064 | -37.1704 | 85.9177 | 85.8627 | 0.25635 | -37.2849 | 92.5003 | 92.3904 | 0.009155 | 123.2162 | 123.3032 | 30.9128 | -0.07782 | 85.9543 | 85.8398 | 85.7895 | -37.5183 | 123.1338 | 123.0469 | 123.2941 | -30.7343
2193.5156 | 123.4451 | -83.7158 | 39.3997 | -0.13275 | 0.010322 | 0.0037127 | 0.013676 | -0.020835 | -0.0023648 | 0.0016983 | -1.0267 | 0.01703 | -0.01214 | 0.013563 | -0.0042126 | 0.01192 | 2.1652 | 2.2522 | 2.1378 | 2.037 | 2.2293 | 2.0462 | 1.9089 | 39.5279 | 39.5874 | 39.6103 | 39.3951 | 39.3356 | 8.7799 | 8.6884 | 85.762 | 85.6247 | -37.1704 | 85.968 | 85.7529 | 0.12817 | -37.2345 | 92.4957 | 92.4042 | -0.004577 | 123.2437 | 123.3261 | 30.9219 | -0.064087 | 85.9451 | 85.881 | 85.8536 | -37.4908 | 123.111 | 123.0515 | 123.3032 | -30.7114
2194.5156 | 123.4268 | -83.7616 | 39.3768 | -0.010681 | 0.0094677 | 0.0037127 | 0.013035 | -0.019766 | -0.00044225 | 0.0010575 | -0.0043486 | 0.018953 | -0.01449 | 0.011427 | -0.0044262 | 0.010852 | 2.1423 | 2.2018 | 2.0782 | 2.1606 | 2.2659 | 2.0599 | 1.8997 | 39.5004 | 39.5828 | 39.5737 | 39.4135 | 39.3127 | 8.7845 | 8.6838 | 85.8215 | 85.6613 | -37.1109 | 85.9634 | 85.9222 | 0.26093 | -37.2345 | 92.5461 | 92.4454 | 0.036621 | 123.262 | 123.3353 | 30.8899 | -0.064087 | 86.0275 | 85.9039 | 85.8398 | -37.4771 | 123.175 | 123.0743 | 123.3444 | -30.6931
2195.5156 | 123.3856 | -83.7845 | 39.3951 | -0.16327 | 0.0081861 | 0.0030719 | 0.012608 | -0.020194 | 0.0029758 | 0.0029801 | -0.14931 | 0.017884 | -0.011286 | 0.012708 | -0.0037854 | 0.010211 | 2.1606 | 2.2385 | 2.1011 | 2.1606 | 2.2568 | 2.0691 | 1.9089 | 39.4547 | 39.5874 | 39.5325 | 39.386 | 39.3127 | 8.7845 | 8.6838 | 85.8536 | 85.6934 | -37.1384 | 86.0229 | 85.9451 | 0.25177 | -37.2345 | 92.569 | 92.4683 | -0.009156 | 123.2391 | 123.317 | 30.8487 | -0.082398 | 86.0413 | 85.9451 | 85.8856 | -37.4863 | 123.1705 | 123.0972 | 123.3719 | -30.7114
2196.5156 | 123.3765 | -83.7982 | 39.3723 | 0.14954 | 0.0088269 | 0.00072209 | 0.010472 | -0.020194 | 0.0012668 | 0.0016983 | 0.14061 | 0.020021 | -0.01449 | 0.012495 | -0.0014356 | 0.012134 | 2.124 | 2.179 | 2.0782 | 2.1194 | 2.2202 | 2.0599 | 1.8906 | 39.4135 | 39.4821 | 39.4958 | 39.3585 | 39.2761 | 8.7753 | 8.6792 | 85.8582 | 85.6888 | -37.1521 | 85.9772 | 85.9177 | 0.22888 | -37.2482 | 92.5735 | 92.4774 | -0.013732 | 123.2117 | 123.2941 | 30.8167 | -0.09613 | 86.0184 | 85.9222 | 85.8765 | -37.4817 | 123.1567 | 123.0743 | 123.2803 | -30.6931
2197.5156 | 123.4131 | -83.7799 | 39.3356 | 0.050354 | 0.0092541 | 0.0037127 | 0.013035 | -0.020835 | 0.00019875 | 0.0021255 | 0.041427 | 0.015535 | -0.012354 | 0.012922 | -0.0033582 | 0.01192 | 2.0828 | 2.1652 | 2.0462 | 2.124 | 2.2385 | 2.0645 | 1.886 | 39.418 | 39.4867 | 39.5004 | 39.3448 | 39.267 | 8.7845 | 8.6792 | 85.8444 | 85.6659 | -37.0972 | 85.9451 | 85.9039 | 0.23804 | -37.2528 | 92.5644 | 92.4591 | 0.009156 | 123.1979 | 123.2803 | 30.8212 | -0.068664 | 86.0184 | 85.8627 | 85.8261 | -37.4496 | 123.1247 | 123.0469 | 123.2666 | -30.6564
2198.5156 | 123.3994 | -83.8257 | 39.2944 | 0.2182 | 0.012459 | 0.0041401 | 0.01389 | -0.019766 | 0.004044 | 0.0036209 | 0.1635 | 0.018739 | -0.012781 | 0.012068 | -0.0031446 | 0.011707 | 2.1332 | 2.179 | 2.0645 | 2.1149 | 2.1744 | 2.0325 | 1.8768 | 39.4409 | 39.4775 | 39.4775 | 39.3356 | 39.2166 | 8.7936 | 8.6884 | 85.8582 | 85.7025 | -37.1201 | 86.0046 | 85.9406 | 0.23804 | -37.1613 | 92.6193 | 92.514 | 0.041198 | 123.2666 | 123.3032 | 30.7892 | -0.07782 | 86.0001 | 85.9589 | 85.8902 | -37.4176 | 123.1613 | 123.0423 | 123.3032 | -30.6061
2199.5156 | 123.3948 | -83.844 | 39.2715 | 0.17242 | 0.01139 | 0.0024311 | 0.010685 | -0.020621 | 0.001694 | 0.0038345 | 0.17876 | 0.018739 | -0.011713 | 0.012922 | -0.0046398 | 0.01192 | 2.1378 | 2.1698 | 2.0645 | 2.1103 | 2.1881 | 2.037 | 1.8677 | 39.386 | 39.418 | 39.4226 | 39.267 | 39.2212 | 8.7891 | 8.6838 | 85.881 | 85.7117 | -37.0834 | 86.0138 | 85.9543 | 0.24262 | -37.1338 | 92.6331 | 92.5278 | -0.004577 | 123.23 | 123.2666 | 30.7388 | -0.050354 | 86.0321 | 85.9817 | 85.9085 | -37.4039 | 123.111 | 123.0652 | 123.262 | -30.5878
2200.5156 | 123.4039 | -83.8852 | 39.2624 | 0.23346 | 0.015449 | 8.1086e-05 | 0.013463 | -0.019126 | 0.0025486 | 0.0049027 | 0.14061 | 0.020021 | -0.011286 | 0.015272 | -0.00036743 | 0.012561 | 2.0737 | 2.0645 | 1.9684 | 2.0737 | 2.2018 | 1.9958 | 1.8402 | 39.3677 | 39.3906 | 39.3951 | 39.2761 | 39.2075 | 8.7753 | 8.6792 | 85.881 | 85.7254 | -37.0605 | 85.9497 | 85.9589 | 0.23346 | -37.1887 | 92.6605 | 92.5644 | 0.013733 | 123.2529 | 123.2803 | 30.7159 | -0.054932 | 86.087 | 85.9589 | 85.8536 | -37.4222 | 123.1613 | 123.0927 | 123.2758 | -30.5832
2201.5156 | 123.3353 | -83.8943 | 39.2258 | 0.088501 | 0.0075451 | 0.0015765 | 0.0094038 | -0.018057 | -0.0015102 | 0.0012711 | 0.10246 | 0.017244 | -0.013422 | 0.013563 | -0.0029308 | 0.012134 | 2.0508 | 2.1194 | 2.0233 | 2.0782 | 2.1973 | 2.0233 | 1.8539 | 39.3265 | 39.3723 | 39.3997 | 39.2715 | 39.1708 | 8.7799 | 8.6792 | 85.9177 | 85.7483 | -37.0285 | 86.0138 | 85.9726 | 0.2243 | -37.175 | 92.6743 | 92.5735 | 0.045776 | 123.2208 | 123.2941 | 30.7205 | -0.054932 | 86.0916 | 85.9451 | 85.9177 | -37.3718 | 123.1659 | 123.0652 | 123.2666 | -30.5466
2202.5156 | 123.4268 | -83.931 | 39.1891 | 0.18768 | 0.013313 | 0.0020037 | 0.013035 | -0.018057 | 0.00062595 | 0.0038345 | 0.20164 | 0.017884 | -0.011713 | 0.013136 | -0.0025036 | 0.010425 | 2.1103 | 2.1515 | 2.0508 | 2.1057 | 2.1927 | 2.0279 | 1.8402 | 39.3173 | 39.3723 | 39.3585 | 39.212 | 39.1113 | 8.7891 | 8.6792 | 85.9589 | 85.7712 | -36.9965 | 86.0825 | 86.0367 | 0.2655 | -37.0789 | 92.72 | 92.6102 | 0.022888 | 123.2483 | 123.2895 | 30.6793 | -0.07782 | 86.1237 | 86.0413 | 85.9818 | -37.3489 | 123.143 | 123.0423 | 123.3032 | -30.5099
2203.5156 | 123.3902 | -83.9584 | 39.1708 | 0.14954 | 0.010322 | 0.0022175 | 0.011326 | -0.018912 | -0.0023648 | 0.0014847 | 0.12535 | 0.018312 | -0.012995 | 0.014845 | -0.0037854 | 0.012347 | 2.0599 | 2.124 | 2.0187 | 2.0691 | 2.1927 | 2.0325 | 1.8311 | 39.2487 | 39.3127 | 39.3127 | 39.1891 | 39.0976 | 8.7799 | 8.6792 | 85.9909 | 85.7895 | -36.9781 | 86.0825 | 86.0275 | 0.23804 | -37.1109 | 92.7383 | 92.6376 | 0.018311 | 123.2071 | 123.2712 | 30.6335 | -0.073242 | 86.1511 | 86.0184 | 85.9772 | -37.3398 | 123.1476 | 123.056 | 123.2712 | -30.4916
2204.5156 | 123.468 | -83.9951 | 39.1159 | 0.18768 | 0.013954 | -0.0012005 | 0.015385 | -0.021475 | 0.004044 | 0.0021255 | 0.2169 | 0.018953 | -0.011499 | 0.012495 | -0.0027172 | 0.0097839 | 2.1286 | 2.1149 | 2.0142 | 2.1011 | 2.1881 | 2.0279 | 1.8311 | 39.267 | 39.3265 | 39.3219 | 39.1434 | 39.0564 | 8.7891 | 8.6838 | 86.0229 | 85.8261 | -36.9278 | 86.1099 | 86.0962 | 0.27008 | -36.9873 | 92.7841 | 92.6788 | 0.027466 | 123.262 | 123.317 | 30.6381 | -0.05951 | 86.1832 | 86.1237 | 86.0092 | -37.2849 | 123.1384 | 123.0515 | 123.3215 | -30.4321
2205.5156 | 123.436 | -83.963 | 39.1571 | 0.2182 | 0.014168 | 0.0020037 | 0.011113 | -0.019553 | 0.002335 | 0.0031937 | 0.31609 | 0.019593 | -0.01214 | 0.012281 | -0.00229 | 0.012775 | 2.1194 | 2.1286 | 1.8997 | 1.8173 | 2.1149 | 1.9638 | 1.8173 | 39.2899 | 39.3402 | 39.3219 | 39.1937 | 39.093 | 8.7845 | 8.6884 | 85.9268 | 85.7803 | -37.0422 | 86.0916 | 85.7803 | 0 | -37.0377 | 92.7475 | 92.6514 | 0.036622 | 123.2529 | 123.2849 | 30.6335 | -0.064086 | 86.0779 | 86.0825 | 85.8627 | -37.3398 | 123.1567 | 123.056 | 123.3032 | -30.4687
2206.5156 | 123.2986 | -84.0363 | 39.1937 | 0.11902 | 0.018226 | 0.0028583 | 0.014317 | -0.019339 | 0.0044712 | 0.0034073 | 0.0032804 | 0.023011 | -0.0097904 | 0.013136 | -0.0018628 | 0.010211 | 2.0279 | 1.9913 | 1.8997 | 2.0233 | 2.1881 | 1.9638 | 1.799 | 39.1571 | 39.2029 | 39.18 | 39.212 | 39.1388 | 8.7845 | 8.6838 | 86.0001 | 85.8353 | -37.0056 | 86.0275 | 86.0596 | 0.2243 | -37.1658 | 92.8207 | 92.72 | 0.01831 | 123.1934 | 123.2162 | 30.4962 | -0.054932 | 86.2244 | 86.0641 | 85.936 | -37.3947 | 123.2483 | 123.175 | 123.2391 | -30.5099
2207.5156 | 123.4222 | -84.0408 | 39.0884 | 0.18768 | 0.016517 | 0.0013629 | 0.01154 | -0.019339 | 0.0031894 | 0.0049027 | 0.20927 | 0.019166 | -0.011713 | 0.01399 | -0.00058103 | 0.012988 | 2.0508 | 2.0508 | 1.9547 | 2.0508 | 2.179 | 1.9913 | 1.8219 | 39.212 | 39.2441 | 39.2532 | 39.1205 | 39.0335 | 8.7799 | 8.6838 | 86.0321 | 85.8627 | -36.9095 | 86.0916 | 86.0916 | 0.22888 | -37.0377 | 92.8207 | 92.7246 | 0.032043 | 123.2529 | 123.2941 | 30.5695 | -0.054932 | 86.2198 | 86.0916 | 85.9955 | -37.2665 | 123.1613 | 123.0743 | 123.2849 | -30.4047
2208.5156 | 123.3124 | -84.082 | 39.1022 | 0.19531 | 0.018867 | 0.0013629 | 0.013463 | -0.019126 | 0.005753 | 0.0051163 | -0.1722 | 0.020875 | -0.010645 | 0.012708 | -0.0012218 | 0.010638 | 1.8127 | 2.2568 | 1.9821 | 1.9821 | 2.2247 | 1.9821 | 1.8082 | 39.1067 | 39.1571 | 39.1571 | 39.1617 | 39.0884 | 8.7891 | 8.6838 | 86.0641 | 85.8902 | -36.8774 | 86.3388 | 86.0641 | 0.17395 | -37.2894 | 92.8711 | 92.7658 | 0.059509 | 123.1888 | 123.2391 | 30.4733 | -0.013733 | 86.3068 | 85.8948 | 86.0641 | -37.294 | 123.2437 | 123.1705 | 123.2391 | -30.4184
2209.5312 | 123.3902 | -84.0775 | 39.0976 | -0.1709 | 0.01075 | 0.0030719 | 0.012394 | -0.018057 | -0.0030056 | 0.0027665 | -0.11879 | 0.01938 | -0.012354 | 0.01399 | -0.005708 | 0.012347 | 2.092 | 2.1423 | 2.0599 | 2.1011 | 2.1973 | 2.0233 | 1.8402 | 39.1617 | 39.2853 | 39.2624 | 39.1113 | 39.061 | 8.7753 | 8.6838 | 86.1008 | 85.9177 | -36.9003 | 86.2198 | 86.1786 | 0.26093 | -37.0056 | 92.8528 | 92.7612 | 0.013733 | 123.2391 | 123.3398 | 30.5786 | -0.036621 | 86.2747 | 86.1694 | 86.1374 | -37.2574 | 123.1888 | 123.1384 | 123.3627 | -30.4138
2210.5156 | 123.3902 | -84.0637 | 39.0656 | 0.14954 | 0.010963 | 0.0020037 | 0.012822 | -0.016349 | -0.00086945 | 0.0029801 | 0.2169 | 0.018312 | -0.011499 | 0.013563 | -0.0044262 | 0.011707 | 2.0874 | 2.1378 | 2.0279 | 2.0691 | 2.1561 | 2.0233 | 1.8494 | 39.1571 | 39.2303 | 39.2303 | 39.0839 | 38.9969 | 8.7845 | 8.6792 | 86.087 | 85.9131 | -36.9095 | 86.2015 | 86.1328 | 0.21973 | -36.9781 | 92.8482 | 92.7429 | 0.01831 | 123.2208 | 123.2941 | 30.5511 | -0.068665 | 86.2198 | 86.1511 | 86.0916 | -37.2162 | 123.1476 | 123.0606 | 123.2941 | -30.3864
2211.5156 | 123.3719 | -84.1232 | 39.0289 | 0.22583 | 0.018226 | 0.0015765 | 0.014958 | -0.018271 | 0.0019078 | 0.0034073 | 0.18639 | 0.018953 | -0.010431 | 0.010359 | -0.0014356 | 0.01192 | 2.0279 | 2.0233 | 1.9272 | 2.0187 | 2.1927 | 1.9821 | 1.8173 | 39.0976 | 39.1388 | 39.1571 | 39.0701 | 38.9603 | 8.7753 | 8.6838 | 86.1053 | 85.9406 | -36.8362 | 86.1465 | 86.142 | 0.20142 | -37.001 | 92.8986 | 92.807 | 0.041198 | 123.2208 | 123.2803 | 30.4733 | -0.068665 | 86.3159 | 86.1511 | 86.0504 | -37.2116 | 123.1934 | 123.0835 | 123.262 | -30.3452
2212.5156 | 123.3353 | -84.169 | 38.9923 | 0.042725 | 0.018867 | 0.0032855 | 0.013463 | -0.018912 | 0.0021214 | 0.0046891 | -0.065384 | 0.02173 | -0.0091494 | 0.014204 | -0.00015383 | 0.0095703 | 2.0828 | 2.0737 | 1.9592 | 2.0508 | 2.179 | 1.973 | 1.8173 | 39.0335 | 39.1296 | 39.093 | 39.0381 | 38.974 | 8.7799 | 8.6838 | 86.142 | 85.9863 | -36.8134 | 86.2427 | 86.2198 | 0.23346 | -36.9095 | 92.9489 | 92.8528 | 0.045776 | 123.2025 | 123.262 | 30.4092 | -0.018311 | 86.348 | 86.2518 | 86.1282 | -37.175 | 123.2071 | 123.143 | 123.2986 | -30.3085
2213.5156 | 123.3353 | -84.1827 | 39.0289 | 0.012207 | 0.019508 | 0.0013629 | 0.014958 | -0.01763 | 0.0014804 | 0.0055435 | -0.019608 | 0.022157 | -0.010645 | 0.013136 | -0.0014356 | 0.011066 | 2.0462 | 2.037 | 1.9363 | 2.0279 | 2.1927 | 1.9501 | 1.799 | 39.0198 | 39.093 | 39.0701 | 39.0335 | 38.9557 | 8.7936 | 8.6838 | 86.1328 | 85.9817 | -36.8362 | 86.2198 | 86.2106 | 0.22888 | -36.9827 | 92.9764 | 92.8665 | 0.004577 | 123.2025 | 123.2529 | 30.3864 | -0.073243 | 86.3754 | 86.2289 | 86.1191 | -37.2299 | 123.2162 | 123.1384 | 123.2758 | -30.3452
2214.5156 | 123.4222 | -84.1324 | 38.9923 | 0.2182 | 0.01374 | 0.0045673 | 0.0089764 | -0.01998 | -0.0023648 | 0.0038345 | 0.24742 | 0.018525 | -0.012354 | 0.012922 | -0.0035718 | 0.015125 | 2.0508 | 2.1194 | 2.0096 | 2.0554 | 2.1378 | 1.9867 | 1.8173 | 39.1022 | 39.1846 | 39.1846 | 38.974 | 38.9374 | 8.7845 | 8.6838 | 86.1191 | 85.9497 | -36.8546 | 86.2518 | 86.1877 | 0.23804 | -36.9415 | 92.9169 | 92.8162 | -0.018311 | 123.2346 | 123.317 | 30.5008 | -0.054932 | 86.2701 | 86.1832 | 86.142 | -37.175 | 123.1064 | 123.0698 | 123.317 | -30.3085
2215.5156 | 123.3124 | -84.1965 | 39.0015 | 0.080872 | 0.018013 | 0.0028583 | 0.016881 | -0.019553 | 0.0029758 | 0.0053299 | 0.026169 | 0.01938 | -0.012354 | 0.015058 | -0.0012218 | 0.0099975 | 2.0142 | 1.9913 | 1.8814 | 2.005 | 2.1835 | 1.9501 | 1.7807 | 38.9648 | 39.0427 | 39.0244 | 39.0472 | 38.974 | 8.7753 | 8.6792 | 86.1465 | 85.9772 | -36.8179 | 86.1877 | 86.2015 | 0.2243 | -36.9873 | 92.9718 | 92.8757 | 0.045776 | 123.1613 | 123.2208 | 30.3452 | -0.027466 | 86.38 | 86.2106 | 86.0779 | -37.2208 | 123.2437 | 123.1705 | 123.2391 | -30.3223
2216.5156 | 123.3582 | -84.201 | 39.0152 | -0.14801 | 0.016304 | 0.0015765 | 0.014103 | -0.018698 | 0.0021214 | 0.0046891 | -0.18745 | 0.021943 | -0.0080814 | 0.013349 | -0.0037854 | 0.010638 | 2.037 | 2.037 | 1.9409 | 2.0508 | 2.1881 | 1.9547 | 1.7944 | 39.006 | 39.1296 | 39.093 | 39.0381 | 38.9648 | 8.7799 | 8.6792 | 86.1557 | 85.9955 | -36.8271 | 86.2381 | 86.2518 | 0.25635 | -36.9781 | 92.981 | 92.8802 | 0.022888 | 123.2071 | 123.2941 | 30.4138 | -0.050354 | 86.3892 | 86.2381 | 86.142 | -37.2208 | 123.2391 | 123.1659 | 123.3307 | -30.336
2217.5156 | 123.3536 | -84.2422 | 38.9694 | -0.018311 | 0.018867 | 0.0011493 | 0.014744 | -0.016349 | 0.002335 | 0.0051163 | -0.042496 | 0.020662 | -0.0085086 | 0.012708 | -0.0029308 | 0.0099975 | 2.0508 | 2.0508 | 1.9455 | 2.0462 | 2.179 | 1.9684 | 1.8036 | 38.974 | 39.0564 | 39.061 | 38.974 | 38.9191 | 8.7799 | 8.6838 | 86.2106 | 86.0458 | -36.7905 | 86.293 | 86.2885 | 0.24261 | -36.9186 | 93.0222 | 92.926 | 0.004578 | 123.2162 | 123.3032 | 30.3772 | -0.050354 | 86.4212 | 86.293 | 86.1877 | -37.1658 | 123.2162 | 123.1613 | 123.2986 | -30.2856
2218.5156 | 123.3444 | -84.3018 | 38.9557 | -0.14038 | 0.013099 | 0.0017901 | 0.011967 | -0.01998 | 0.0014804 | 0.0023391 | -0.12642 | 0.020021 | -0.011499 | 0.012708 | -0.0050672 | 0.012775 | 1.9821 | 2.0142 | 1.9089 | 2.0325 | 2.2064 | 1.9638 | 1.7807 | 38.8824 | 39.0244 | 38.974 | 38.9648 | 38.8962 | 8.7845 | 8.6838 | 86.2656 | 86.0825 | -36.7493 | 86.3159 | 86.3342 | 0.25177 | -36.9736 | 93.0862 | 92.9855 | 0.009156 | 123.1842 | 123.2758 | 30.2902 | -0.059509 | 86.5082 | 86.2839 | 86.2106 | -37.175 | 123.2666 | 123.1979 | 123.3261 | -30.2719
2219.5312 | 123.4039 | -84.2789 | 38.9008 | 0.065613 | 0.012031 | 0.0079853 | 0.01154 | -0.021048 | -0.0049282 | -0.00022432 | 0.1635 | 0.016603 | -0.012567 | 0.015058 | -0.0052808 | 0.012988 | 1.7807 | 2.0416 | 1.9547 | 1.9501 | 2.1469 | 1.9501 | 1.7853 | 38.9191 | 39.0152 | 39.0656 | 38.9008 | 38.8412 | 8.7753 | 8.6792 | 86.2289 | 86.0641 | -36.7538 | 86.3205 | 86.2289 | 0.1648 | -37.1201 | 93.0542 | 92.9581 | 0 | 123.1979 | 123.3444 | 30.3864 | -0.059509 | 86.4258 | 86.0596 | 86.2335 | -37.1155 | 123.1796 | 123.1201 | 123.2941 | -30.2216
2220.5156 | 123.3582 | -84.2743 | 38.8962 | -0.19379 | 0.011818 | 0.0039263 | 0.011967 | -0.017417 | -0.0017238 | 0.0023391 | -0.14168 | 0.017244 | -0.01214 | 0.010786 | -0.003999 | 0.01192 | 2.0737 | 2.1378 | 2.0187 | 2.0966 | 2.1835 | 1.9913 | 1.8265 | 38.9145 | 39.061 | 39.0244 | 38.9328 | 38.8367 | 8.7799 | 8.6884 | 86.2656 | 86.1008 | -36.7126 | 86.412 | 86.3709 | 0.27008 | -36.8225 | 93.0542 | 92.9626 | 0.036621 | 123.1888 | 123.2986 | 30.336 | -0.059509 | 86.4578 | 86.348 | 86.293 | -37.0697 | 123.2071 | 123.111 | 123.3353 | -30.2078
2221.5156 | 123.3627 | -84.3384 | 38.8641 | -0.10986 | 0.015663 | 0.0011493 | 0.01389 | -0.01998 | 0.0061802 | 0.0036209 | -0.13405 | 0.018312 | -0.012354 | 0.011854 | -0.003999 | 0.011707 | 2.0279 | 2.037 | 1.9318 | 2.0462 | 2.2018 | 1.9547 | 1.8127 | 38.8733 | 38.974 | 38.9328 | 38.8779 | 38.8184 | 8.7799 | 8.6838 | 86.293 | 86.1511 | -36.6623 | 86.3754 | 86.3846 | 0.23346 | -36.8362 | 93.1183 | 93.0222 | 0.013733 | 123.2117 | 123.2712 | 30.249 | -0.045777 | 86.5402 | 86.3663 | 86.2701 | -37.0514 | 123.2162 | 123.1567 | 123.3124 | -30.1804
2222.5156 | 123.3307 | -84.3246 | 38.9282 | -0.21667 | 0.011604 | 0.0026447 | 0.011326 | -0.021048 | -0.001083 | 0.0021255 | -0.14931 | 0.01938 | -0.0097904 | 0.013563 | -0.0050672 | 0.011707 | 2.0004 | 2.0325 | 1.918 | 2.0187 | 2.211 | 1.9638 | 1.7899 | 38.8229 | 38.9557 | 38.9236 | 38.8916 | 38.8229 | 8.7891 | 8.6884 | 86.2885 | 86.1145 | -36.7172 | 86.3571 | 86.3434 | 0.22888 | -36.9278 | 93.1137 | 93.013 | -0.036621 | 123.1476 | 123.2483 | 30.2353 | -0.10529 | 86.5356 | 86.3251 | 86.2427 | -37.1384 | 123.2162 | 123.1476 | 123.2803 | -30.2399
2223.5156 | 123.3398 | -84.3567 | 38.8733 | -0.1709 | 0.013313 | 0.0032855 | 0.011754 | -0.017417 | 0.0027622 | 0.0012711 | -0.17983 | 0.019807 | -0.012354 | 0.012281 | -0.0044262 | 0.012561 | 1.9821 | 2.0142 | 1.8906 | 2.0325 | 2.2018 | 1.9592 | 1.7761 | 38.8229 | 38.9328 | 38.9236 | 38.8916 | 38.8138 | 8.7845 | 8.6838 | 86.3159 | 86.1328 | -36.6714 | 86.3708 | 86.3892 | 0.25635 | -36.8912 | 93.1412 | 93.0405 | 0.018311 | 123.1796 | 123.2803 | 30.2399 | -0.059509 | 86.5585 | 86.3388 | 86.2473 | -37.0972 | 123.2483 | 123.1705 | 123.2895 | -30.1895
2224.5156 | 123.3627 | -84.3475 | 38.855 | -0.094604 | 0.01844 | -0.00013251 | 0.014531 | -0.018912 | 0.0042576 | 0.0025529 | -0.050125 | 0.020234 | -0.011713 | 0.015058 | -0.0010082 | 0.0093567 | 2.0508 | 2.0462 | 1.9409 | 2.0325 | 2.1698 | 1.9547 | 1.7899 | 38.8779 | 38.942 | 38.9099 | 38.8824 | 38.7863 | 8.7891 | 8.6792 | 86.3022 | 86.1374 | -36.6852 | 86.3937 | 86.38 | 0.24262 | -36.8042 | 93.1366 | 93.0267 | 0.027466 | 123.2254 | 123.2574 | 30.2307 | -0.068664 | 86.5173 | 86.3983 | 86.2885 | -37.0651 | 123.23 | 123.1338 | 123.2895 | -30.1758
2225.5156 | 123.3444 | -84.3979 | 38.8458 | -0.13275 | 0.013527 | 0.00050849 | 0.012608 | -0.016776 | 0.00083955 | 0.0034073 | -0.17983 | 0.02173 | -0.012567 | 0.012708 | -0.0029308 | 0.011279 | 1.9821 | 2.005 | 1.8997 | 2.0096 | 2.179 | 1.9592 | 1.7807 | 38.7726 | 38.8824 | 38.8641 | 38.8779 | 38.7726 | 8.7845 | 8.6884 | 86.3571 | 86.1786 | -36.6669 | 86.4029 | 86.4075 | 0.22888 | -36.8637 | 93.1824 | 93.0862 | 0.032044 | 123.1705 | 123.262 | 30.1758 | -0.073242 | 86.5768 | 86.38 | 86.2976 | -37.0651 | 123.2758 | 123.1705 | 123.2803 | -30.1575
2226.5156 | 123.4406 | -84.343 | 38.8092 | -0.14038 | 0.0071179 | 0.0039263 | 0.011754 | -0.018485 | -0.00621 | -1.0724e-05 | -0.66811 | 0.017671 | -0.011286 | 0.013136 | -0.006776 | 0.01427 | 2.037 | 2.1561 | 2.0233 | 2.1103 | 2.1698 | 1.9638 | 1.7944 | 38.855 | 39.0015 | 39.006 | 38.7497 | 38.7039 | 8.7891 | 8.6884 | 86.3068 | 86.1374 | -36.6394 | 86.499 | 86.4532 | 0.31586 | -36.7722 | 93.132 | 93.0313 | -0.059509 | 123.1979 | 123.349 | 30.3177 | -0.10529 | 86.5128 | 86.38 | 86.3663 | -37.0148 | 123.0927 | 123.0469 | 123.3444 | -30.1209
2227.5156 | 123.4451 | -84.4025 | 38.7497 | 2.8961 | 0.0098951 | 0.0030719 | 0.012822 | -0.018485 | -0.004501 | 0.0021255 | -0.12642 | 0.017244 | -0.013422 | 0.012495 | -0.0025036 | 0.012347 | 2.0691 | 2.1149 | 2.0142 | 2.0828 | 2.124 | 1.9821 | 1.8036 | 38.8367 | 38.9786 | 38.9511 | 38.7589 | 38.681 | 8.7845 | 8.6929 | 86.3846 | 86.2061 | -36.6257 | 86.5173 | 86.4853 | 0.27924 | -36.6806 | 93.187 | 93.0954 | 0.009155 | 123.2391 | 123.3536 | 30.2582 | -0.068665 | 86.5265 | 86.4716 | 86.4166 | -36.9461 | 123.1613 | 123.0835 | 123.381 | -30.0568
2228.5156 | 123.4314 | -84.3842 | 38.736 | -0.033569 | 0.0058361 | 0.0039263 | 0.010472 | -0.020194 | -0.0036464 | 0.0021255 | -0.0043486 | 0.018312 | -0.014276 | 0.012068 | -0.0044262 | 0.010638 | 2.0233 | 2.124 | 2.005 | 2.0691 | 2.1515 | 1.9913 | 1.8127 | 38.8275 | 38.9374 | 38.9374 | 38.7405 | 38.6627 | 8.7845 | 8.6838 | 86.3754 | 86.1969 | -36.5845 | 86.5082 | 86.4532 | 0.25635 | -36.7126 | 93.1686 | 93.0679 | 0.004578 | 123.2117 | 123.3215 | 30.2536 | -0.073242 | 86.5356 | 86.4075 | 86.3892 | -36.9232 | 123.1247 | 123.0469 | 123.3215 | -30.0522
2229.5156 | 123.4177 | -84.4528 | 38.7405 | -0.16327 | 0.012672 | 0.0032855 | 0.01154 | -0.019766 | -0.00065585 | 0.0023391 | -0.15694 | 0.017671 | -0.011713 | 0.013136 | -0.003999 | 0.011707 | 2.0599 | 2.1423 | 2.037 | 2.092 | 2.1698 | 1.9867 | 1.8127 | 38.7909 | 38.9236 | 38.8916 | 38.7497 | 38.6536 | 8.7753 | 8.6838 | 86.4395 | 86.2656 | -36.5707 | 86.5952 | 86.5448 | 0.27924 | -36.6806 | 93.2281 | 93.1366 | 0.009155 | 123.2437 | 123.3444 | 30.2078 | -0.086976 | 86.6226 | 86.5128 | 86.4899 | -36.9278 | 123.2025 | 123.1064 | 123.3765 | -30.0568
2230.5156 | 123.4177 | -84.4528 | 38.6719 | 0.0045777 | 0.0073315 | 0.0030719 | 0.013035 | -0.021048 | -0.00065585 | 0.0023391 | -0.0043486 | 0.015748 | -0.013849 | 0.012068 | -0.0037854 | 0.0089295 | 2.0279 | 2.1011 | 2.0004 | 2.0599 | 2.1652 | 1.9913 | 1.8356 | 38.7543 | 38.855 | 38.8596 | 38.6948 | 38.6169 | 8.7845 | 8.6884 | 86.4441 | 86.2885 | -36.5067 | 86.554 | 86.5128 | 0.22431 | -36.644 | 93.2373 | 93.1412 | 0.022888 | 123.2071 | 123.3124 | 30.1712 | -0.054932 | 86.618 | 86.4807 | 86.4532 | -36.8362 | 123.1476 | 123.0698 | 123.3078 | -29.9835
2231.5156 | 123.4268 | -84.4711 | 38.6581 | -0.11749 | 0.0069043 | 0.0047809 | 0.01154 | -0.01763 | -0.001083 | 0.00063028 | -0.080643 | 0.016389 | -0.013636 | 0.013349 | -0.0059216 | 0.0082885 | 2.0966 | 2.1698 | 2.0416 | 2.092 | 2.1423 | 1.9867 | 1.8173 | 38.855 | 39.0335 | 38.6444 | 38.6719 | 38.5849 | 8.7799 | 8.6838 | 86.4578 | 86.2885 | -36.5158 | 86.6409 | 86.5631 | 0.27466 | -36.5616 | 93.251 | 93.1549 | 0.013733 | 123.3261 | 123.1155 | 29.9606 | -0.073242 | 86.6135 | 86.5677 | 86.5128 | -36.8408 | 123.143 | 123.056 | 123.5046 | -29.9744
2232.5156 | 123.3765 | -84.5306 | 38.6444 | 0.080872 | 0.0081861 | 0.00093569 | 0.012394 | -0.016349 | -0.00044225 | 0.0025529 | 0.12535 | 0.015321 | -0.014704 | 0.012068 | -0.003999 | 0.01192 | 2.0096 | 2.0462 | 1.9455 | 2.0142 | 2.1378 | 1.9592 | 1.7944 | 38.5941 | 38.7817 | 38.7314 | 38.6215 | 38.53 | 8.7753 | 8.6838 | 86.4899 | 86.3251 | -36.5067 | 86.5768 | 86.5448 | 0.21973 | -36.6348 | 93.306 | 93.2144 | -0.022888 | 123.1247 | 123.262 | 30.0476 | -0.11444 | 86.6684 | 86.5402 | 86.4761 | -36.85 | 123.1522 | 123.0606 | 123.3124 | -29.9606
2233.5156 | 123.4222 | -84.5215 | 38.6307 | 0.012207 | 0.0071179 | 0.0026447 | 0.013676 | -0.018271 | -0.0015102 | 0.0019119 | -0.034867 | 0.01938 | -0.01214 | 0.014417 | -0.0025036 | 0.010211 | 2.0279 | 2.0874 | 1.9958 | 2.0599 | 2.1561 | 1.9775 | 1.8036 | 38.7085 | 38.7817 | 38.8 | 38.6353 | 38.5437 | 8.7845 | 8.6746 | 86.499 | 86.3251 | -36.4746 | 86.6089 | 86.5814 | 0.25635 | -36.6028 | 93.306 | 93.1961 | 0.004578 | 123.23 | 123.3215 | 30.1254 | -0.086975 | 86.6776 | 86.5494 | 86.5173 | -36.8271 | 123.1567 | 123.0652 | 123.3032 | -29.9561
2234.5156 | 123.4406 | -84.5398 | 38.5757 | 0.24109 | 0.012031 | 0.0028583 | 0.013463 | -0.019766 | 0.0029758 | 0.00063028 | 0.033798 | 0.018525 | -0.011713 | 0.012068 | -0.0012218 | 0.01192 | 2.1835 | 2.1423 | 1.9821 | 2.0554 | 2.0691 | 1.9226 | 1.7578 | 38.7177 | 38.7863 | 38.7589 | 38.5895 | 38.5391 | 8.7845 | 8.6792 | 86.4624 | 86.2976 | -36.5067 | 86.6821 | 86.5952 | 0.29755 | -36.3922 | 93.3243 | 93.219 | 0.013733 | 123.2574 | 123.2986 | 30.0797 | -0.036621 | 86.6089 | 86.7233 | 86.5219 | -36.8179 | 123.1293 | 123.0789 | 123.3261 | -29.8965
2235.5156 | 123.4222 | -84.613 | 38.5483 | 0.16479 | 0.0098951 | 0.0017901 | 0.011326 | -0.01998 | -0.001083 | 0.00084388 | 0.14061 | 0.017884 | -0.012781 | 0.012281 | -0.0046398 | 0.0093567 | 2.0233 | 2.0691 | 1.9501 | 2.0233 | 2.1515 | 1.973 | 1.799 | 38.6169 | 38.7817 | 38.6215 | 38.5712 | 38.4659 | 8.7753 | 8.6746 | 86.586 | 86.412 | -36.3968 | 86.6821 | 86.6364 | 0.2243 | -36.525 | 93.3884 | 93.2877 | 0.022888 | 123.23 | 123.2346 | 29.9469 | -0.082398 | 86.7645 | 86.6364 | 86.5631 | -36.7493 | 123.1842 | 123.0789 | 123.3948 | -29.8737
2236.5156 | 123.436 | -84.6176 | 38.5345 | 0.18768 | 0.014168 | 0.0026447 | 0.009831 | -0.018485 | 0.00041235 | 0.0027665 | 0.2169 | 0.01703 | -0.011286 | 0.012495 | -0.003999 | 0.0097839 | 2.0782 | 2.1103 | 1.9867 | 2.037 | 2.1332 | 1.9592 | 1.7944 | 38.681 | 38.6993 | 38.7085 | 38.5574 | 38.4567 | 8.7936 | 8.6884 | 86.5768 | 86.412 | -36.4014 | 86.7279 | 86.6547 | 0.24261 | -36.4563 | 93.4113 | 93.306 | 0.022888 | 123.2986 | 123.3261 | 30.0201 | -0.07782 | 86.7508 | 86.6959 | 86.6043 | -36.7401 | 123.175 | 123.0743 | 123.317 | -29.8462
2237.5156 | 123.3856 | -84.613 | 38.5254 | 0.14191 | 0.0090405 | 0.0028583 | 0.009831 | -0.020194 | 0.0019078 | 0.0036209 | 0.071945 | 0.016603 | -0.012781 | 0.01399 | -0.0054944 | 0.012134 | 2.0233 | 2.0737 | 1.9547 | 2.0096 | 2.1515 | 1.9775 | 1.7944 | 38.5986 | 38.6581 | 38.6673 | 38.5391 | 38.4613 | 8.7708 | 8.6792 | 86.5906 | 86.4075 | -36.3739 | 86.6867 | 86.6226 | 0.21515 | -36.5021 | 93.3838 | 93.2922 | 0.013733 | 123.2117 | 123.2803 | 29.9881 | -0.064087 | 86.7645 | 86.6364 | 86.5677 | -36.731 | 123.1522 | 123.0743 | 123.2712 | -29.8462
2238.5156 | 123.3765 | -84.6771 | 38.3972 | 0.18005 | 0.013313 | 0.0030719 | 0.013035 | -0.020621 | 0.004044 | 0.0046891 | 0.1635 | 0.01938 | -0.013636 | 0.013777 | -0.00058103 | 0.010211 | 2.0645 | 2.0782 | 1.9684 | 2.0508 | 2.1103 | 1.9547 | 1.799 | 38.5895 | 38.6353 | 38.6261 | 38.4842 | 38.3698 | 8.7753 | 8.6884 | 86.6318 | 86.4761 | -36.2869 | 86.7554 | 86.7279 | 0.25177 | -36.3327 | 93.4525 | 93.3655 | 0.086975 | 123.2666 | 123.3032 | 29.9377 | -0.027466 | 86.7874 | 86.7416 | 86.6455 | -36.5982 | 123.1613 | 123.0469 | 123.3124 | -29.7089
2239.5156 | 123.4818 | -84.6497 | 38.5117 | -0.086975 | 0.0069043 | 0.0041401 | 0.011967 | -0.018271 | -0.0025784 | 0.0046891 | -0.073013 | 0.017884 | -0.012995 | 0.013136 | -0.0037854 | 0.01192 | 2.0645 | 2.1469 | 2.0233 | 2.0782 | 2.1515 | 1.9867 | 1.8173 | 38.6398 | 38.7451 | 38.7268 | 38.5117 | 38.4567 | 8.7891 | 8.6884 | 86.6364 | 86.467 | -36.3602 | 86.7966 | 86.7279 | 0.26093 | -36.4471 | 93.4387 | 93.338 | 0 | 123.2895 | 123.3765 | 30.0385 | -0.054932 | 86.8011 | 86.7142 | 86.673 | -36.6943 | 123.1613 | 123.1064 | 123.3948 | -29.8233
2240.5156 | 123.3719 | -84.6588 | 38.5391 | 0.19531 | 0.016731 | 0.0017901 | 0.013035 | -0.01998 | 0.0048984 | 0.0042619 | 0.17876 | 0.020448 | -0.011286 | 0.015486 | -0.00058103 | 0.0093567 | 2.005 | 1.9455 | 1.8539 | 1.9638 | 2.1652 | 1.9272 | 1.7441 | 38.5849 | 38.5941 | 38.5986 | 38.562 | 38.4613 | 8.7845 | 8.6838 | 86.586 | 86.4029 | -36.3739 | 86.6043 | 86.6226 | 0.21973 | -36.5341 | 93.4433 | 93.3426 | 0.022888 | 123.2437 | 123.2574 | 29.9149 | -0.07782 | 86.824 | 86.6638 | 86.5128 | -36.795 | 123.2208 | 123.1201 | 123.2529 | -29.8553
2241.5156 | 123.4039 | -84.6634 | 38.5162 | 0.24109 | 0.014595 | 0.0015765 | 0.011113 | -0.019126 | 0.0042576 | 0.0031937 | 0.15587 | 0.018739 | -0.011286 | 0.014845 | 0.00048697 | 0.010425 | 2.005 | 1.9775 | 1.8906 | 1.9684 | 2.124 | 1.9135 | 1.7578 | 38.5941 | 38.6444 | 38.6124 | 38.5117 | 38.4613 | 8.7799 | 8.6838 | 86.5768 | 86.4212 | -36.3922 | 86.6409 | 86.6318 | 0.21057 | -36.5112 | 93.4433 | 93.3472 | -0.004577 | 123.2574 | 123.2758 | 29.9286 | -0.054931 | 86.7874 | 86.6684 | 86.554 | -36.7584 | 123.175 | 123.1247 | 123.3078 | -29.8325
2242.5156 | 123.317 | -84.7092 | 38.5025 | 0.18005 | 0.015449 | 0.00072209 | 0.016026 | -0.02233 | 0.0046848 | -0.00065152 | -0.034867 | 0.02173 | -0.010004 | 0.013777 | -0.0025036 | 0.012134 | 2.2293 | 1.8997 | 1.8082 | 1.9775 | 2.1561 | 1.9226 | 1.767 | 38.4705 | 38.5117 | 38.5025 | 38.5071 | 38.475 | 8.7799 | 8.6792 | 86.6318 | 86.4761 | -36.3464 | 86.6089 | 86.6867 | 0.21057 | -36.2732 | 93.4891 | 93.3884 | 0.004578 | 123.1796 | 123.2117 | 29.8233 | -0.027465 | 86.8652 | 86.9385 | 86.5173 | -36.7355 | 123.2162 | 123.1842 | 123.2208 | -29.8233
2243.5156 | 123.436 | -84.6909 | 38.4384 | 0.18768 | 0.014595 | 0.0034991 | 0.010258 | -0.01763 | 0.001694 | 0.0036209 | 0.19402 | 0.01703 | -0.012567 | 0.013777 | -0.0020764 | 0.0099975 | 2.0554 | 2.0737 | 1.9638 | 2.0462 | 2.0966 | 1.9501 | 1.7715 | 38.5849 | 38.6581 | 38.6307 | 38.4384 | 38.3698 | 8.7799 | 8.6884 | 86.6409 | 86.4624 | -36.3419 | 86.7645 | 86.7371 | 0.27466 | -36.3831 | 93.4708 | 93.3792 | 0 | 123.2758 | 123.3215 | 29.9423 | -0.068665 | 86.7874 | 86.7462 | 86.6547 | -36.6669 | 123.1293 | 123.0606 | 123.349 | -29.7501
2244.5156 | 123.3215 | -84.7549 | 38.4476 | 0.18768 | 0.017799 | 0.00072209 | 0.007481 | -0.01998 | -0.00086945 | 0.0031937 | 0.31609 | 0.021516 | -0.011499 | 0.014845 | -0.0012218 | 0.011066 | 2.1011 | 1.8631 | 1.8539 | 1.9913 | 2.1332 | 1.9135 | 1.7487 | 38.4384 | 38.4842 | 38.4659 | 38.4979 | 38.443 | 8.7753 | 8.6792 | 86.6684 | 86.5036 | -36.3144 | 86.618 | 86.7462 | 0.24262 | -36.3464 | 93.5303 | 93.4341 | 0.050354 | 123.1934 | 123.2208 | 29.7867 | -0.004578 | 86.8881 | 86.8561 | 86.6089 | -36.6989 | 123.2529 | 123.1979 | 123.2391 | -29.7684
2245.5156 | 123.4177 | -84.7321 | 38.4064 | 0.21057 | 0.017586 | 8.1086e-05 | 0.011326 | -0.018912 | 0.002335 | 0.0044755 | 0.18639 | 0.019807 | -0.012354 | 0.012708 | -0.0018628 | 0.010852 | 1.973 | 1.9684 | 1.8997 | 1.9821 | 2.1194 | 1.9226 | 1.7212 | 38.5162 | 38.5574 | 38.5895 | 38.4521 | 38.3514 | 8.7753 | 8.6746 | 86.6547 | 86.4532 | -36.2869 | 86.7004 | 86.7142 | 0.26093 | -36.4334 | 93.5074 | 93.4067 | 0.045776 | 123.2483 | 123.3215 | 29.9149 | -0.054932 | 86.8515 | 86.705 | 86.6318 | -36.6852 | 123.1842 | 123.0835 | 123.2895 | -29.7317
2246.5156 | 123.3078 | -84.8236 | 38.4018 | 0.088501 | 0.016517 | 0.0032855 | 0.015172 | -0.018698 | 0.003403 | 0.0061845 | 0.23216 | 0.022584 | -0.0095768 | 0.013136 | -0.0018628 | 0.010852 | 1.9409 | 1.8997 | 1.8448 | 1.9547 | 2.1149 | 1.8997 | 1.7166 | 38.3652 | 38.4201 | 38.4109 | 38.4109 | 38.3926 | 8.7799 | 8.6838 | 86.7233 | 86.5402 | -36.2869 | 86.7233 | 86.7783 | 0.23804 | -36.4609 | 93.6035 | 93.5074 | 0.009156 | 123.1888 | 123.2346 | 29.7272 | -0.009155 | 86.9385 | 86.7645 | 86.6684 | -36.6852 | 123.2346 | 123.2162 | 123.2437 | -29.718
2247.5156 | 123.3582 | -84.8419 | 38.3881 | 0.19531 | 0.014808 | 0.0024311 | 0.013463 | -0.016776 | 0.00062595 | 0.0029801 | 0.15587 | 0.019807 | -0.012354 | 0.012708 | -0.0033582 | 0.011279 | 1.9547 | 1.8951 | 1.8219 | 1.9363 | 2.124 | 1.886 | 1.7166 | 38.3743 | 38.4247 | 38.4338 | 38.4018 | 38.3514 | 8.7799 | 8.6838 | 86.7279 | 86.5585 | -36.264 | 86.7371 | 86.7783 | 0.21973 | -36.4334 | 93.6218 | 93.5257 | 0.013732 | 123.2162 | 123.2758 | 29.7501 | -0.036622 | 86.9659 | 86.7966 | 86.6638 | -36.6714 | 123.2437 | 123.1934 | 123.2666 | -29.7043
2248.5156 | 123.3719 | -84.7916 | 38.4109 | -0.064087 | 0.016517 | 0.0041401 | 0.013035 | -0.019126 | 0.0072482 | 0.0044755 | -0.18745 | 0.021302 | -0.014276 | 0.012708 | -0.0016492 | 0.011493 | 2.0233 | 2.2018 | 1.9775 | 1.9821 | 2.1927 | 1.9455 | 1.799 | 38.443 | 38.5391 | 38.4842 | 38.4384 | 38.3789 | 8.7891 | 8.6838 | 86.7371 | 86.5906 | -36.2183 | 86.9934 | 86.7737 | 0.18311 | -36.3876 | 93.5806 | 93.4753 | 0.027466 | 123.2346 | 123.2758 | 29.8004 | -0.032044 | 86.9843 | 86.8149 | 86.7691 | -36.6119 | 123.23 | 123.1705 | 123.3307 | -29.7272
2249.5156 | 123.2895 | -84.8282 | 38.3835 | 0.057983 | 0.017799 | 8.1086e-05 | 0.012608 | -0.019553 | 0.00062595 | 0.0027665 | 0.17113 | 0.020875 | -0.0091494 | 0.010359 | -0.003999 | 0.011707 | 1.9089 | 1.8768 | 1.799 | 1.9272 | 2.124 | 1.8768 | 1.7166 | 38.356 | 38.3743 | 38.4567 | 38.3926 | 38.3423 | 8.7753 | 8.6884 | 86.705 | 86.5448 | -36.2595 | 86.705 | 86.7554 | 0.21057 | -36.4746 | 93.6035 | 93.5165 | 0.009155 | 123.1842 | 123.2849 | 29.7684 | -0.041199 | 86.9522 | 86.7371 | 86.6272 | -36.6669 | 123.2208 | 123.1705 | 123.2025 | -29.6951
2250.5156 | 123.3398 | -84.8602 | 38.3789 | 0.035095 | 0.016517 | -0.00098691 | 0.013249 | -0.019339 | 0.004044 | 0.0046891 | -0.0043486 | 0.021516 | -0.0089358 | 0.013349 | -0.0027172 | 0.0093567 | 1.973 | 1.9501 | 1.8677 | 1.9684 | 2.1286 | 1.8906 | 1.7258 | 38.356 | 38.4338 | 38.4247 | 38.4247 | 38.3331 | 8.7845 | 8.6838 | 86.7508 | 86.586 | -36.2503 | 86.8103 | 86.8286 | 0.24261 | -36.4059 | 93.6447 | 93.544 | 0.045777 | 123.2162 | 123.2849 | 29.7409 | -0.045776 | 86.9888 | 86.8332 | 86.7279 | -36.6531 | 123.2849 | 123.1934 | 123.2941 | -29.6951
2251.5156 | 123.3215 | -84.8877 | 38.3514 | 0.09613 | 0.018867 | 0.00050849 | 0.014103 | -0.019339 | 0.0038304 | 0.0016983 | 0.17876 | 0.020662 | -0.0072268 | 0.012922 | -0.0089124 | 0.0093567 | 1.8997 | 1.8906 | 1.8127 | 1.9318 | 2.1378 | 1.886 | 1.7075 | 38.4155 | 38.269 | 38.4155 | 38.3743 | 38.3057 | 8.7845 | 8.6792 | 86.7737 | 86.5952 | -36.2137 | 86.7783 | 86.8195 | 0.2243 | -36.4517 | 93.6722 | 93.5669 | 0.022889 | 123.3032 | 123.3032 | 29.7363 | -0.045776 | 87.0255 | 86.7874 | 86.7004 | -36.644 | 123.262 | 123.1934 | 123.1567 | -29.6722
2252.5156 | 123.3765 | -84.8877 | 38.2965 | -0.064087 | 0.017372 | 0.0017901 | 0.01389 | -0.019126 | 0.0014804 | 0.0029801 | 0.36949 | 0.020234 | -0.0097904 | 0.013563 | -0.0044262 | 0.011493 | 2.1057 | 1.9638 | 1.9501 | 2.0782 | 2.1561 | 1.9409 | 1.7532 | 38.324 | 38.4247 | 38.3972 | 38.3331 | 38.2645 | 8.7845 | 8.6746 | 86.8286 | 86.6409 | -36.1404 | 86.8515 | 86.9659 | 0.32501 | -36.1908 | 93.6722 | 93.5623 | 0.036621 | 123.2117 | 123.2849 | 29.7226 | -0.032044 | 87.0438 | 86.9934 | 86.8378 | -36.5433 | 123.2208 | 123.1522 | 123.3124 | -29.6219
2253.5156 | 123.3124 | -84.9426 | 38.3011 | 0.012207 | 0.017372 | -0.00034611 | 0.014958 | -0.01998 | -1.505e-05 | 0.0027665 | 0.087204 | 0.01938 | -0.0091494 | 0.015486 | -0.0035718 | 0.011493 | 1.9318 | 1.9363 | 1.8356 | 1.9547 | 2.1194 | 1.8768 | 1.7166 | 38.2462 | 38.3331 | 38.3148 | 38.3148 | 38.237 | 8.7799 | 8.6746 | 86.8195 | 86.6592 | -36.1816 | 86.879 | 86.8973 | 0.23804 | -36.3693 | 93.7225 | 93.6172 | 0.013733 | 123.1888 | 123.2574 | 29.6402 | -0.064086 | 87.0621 | 86.8744 | 86.7783 | -36.5845 | 123.2574 | 123.1796 | 123.2758 | -29.6265
2254.5156 | 123.3398 | -84.9426 | 38.2965 | -0.14801 | 0.017158 | 0.0022175 | 0.015172 | -0.020835 | 0.0012668 | 0.00020288 | -0.14931 | 0.021302 | -0.011286 | 0.013349 | -0.003999 | 0.011279 | 1.9089 | 1.9363 | 1.8402 | 1.9592 | 2.1378 | 1.8906 | 1.6937 | 38.237 | 38.356 | 38.3423 | 38.3148 | 38.2507 | 8.7799 | 8.6838 | 86.8332 | 86.6364 | -36.1588 | 86.879 | 86.9019 | 0.2655 | -36.3876 | 93.7225 | 93.6264 | 0.01831 | 123.1796 | 123.2849 | 29.6585 | -0.045777 | 87.0804 | 86.8515 | 86.7828 | -36.6028 | 123.2574 | 123.1934 | 123.2986 | -29.6127
2255.5156 | 123.4039 | -84.9792 | 38.2828 | -0.079346 | 0.016304 | 0.0020037 | 0.01389 | -0.019339 | 0.0019078 | 0.0029801 | -0.088272 | 0.018739 | -0.010645 | 0.012495 | -0.0033582 | 0.011493 | 1.9501 | 1.9821 | 1.8768 | 1.9913 | 2.1286 | 1.8906 | 1.7075 | 38.237 | 38.3423 | 38.3057 | 38.2553 | 38.1821 | 8.7799 | 8.6746 | 86.8698 | 86.6867 | -36.1542 | 86.9614 | 86.9705 | 0.28381 | -36.3327 | 93.7592 | 93.6539 | -0.027466 | 123.2162 | 123.2849 | 29.631 | -0.10071 | 87.1078 | 86.9293 | 86.8561 | -36.5753 | 123.2346 | 123.1613 | 123.3215 | -29.6082
2256.5156 | 123.3719 | -84.9747 | 38.2233 | -0.14038 | 0.015022 | 0.0013629 | 0.014531 | -0.018912 | 0.0029758 | 0.0038345 | -0.12642 | 0.01938 | -0.012567 | 0.012495 | -0.0033582 | 0.01192 | 1.9318 | 1.9775 | 1.8539 | 1.973 | 2.124 | 1.886 | 1.712 | 38.2187 | 38.3514 | 38.3102 | 38.269 | 38.1866 | 8.7845 | 8.6838 | 86.8607 | 86.6867 | -36.0992 | 86.9522 | 86.9476 | 0.26093 | -36.2915 | 93.7592 | 93.6584 | 0.045776 | 123.1934 | 123.2849 | 29.6265 | -0.036621 | 87.0987 | 86.9064 | 86.8286 | -36.5112 | 123.2437 | 123.1613 | 123.3261 | -29.5395
2257.5156 | 123.3398 | -84.9976 | 38.2233 | -0.11749 | 0.018654 | 0.0022175 | 0.016667 | -0.018485 | 0.0014804 | 0.0031937 | -0.019608 | 0.020021 | -0.010858 | 0.013136 | -0.0029308 | 0.0097839 | 1.9592 | 1.9867 | 1.8768 | 1.9867 | 2.0966 | 1.8906 | 1.7212 | 38.205 | 38.3011 | 38.2599 | 38.2187 | 38.15 | 8.7799 | 8.6792 | 86.8881 | 86.7188 | -36.1267 | 86.9843 | 86.9843 | 0.2655 | -36.264 | 93.7775 | 93.6768 | -0.004578 | 123.2025 | 123.2574 | 29.5807 | -0.073243 | 87.0941 | 86.9568 | 86.8744 | -36.5021 | 123.2162 | 123.1476 | 123.2986 | -29.5441
2258.5156 | 123.349 | -85.0021 | 38.2553 | -0.15564 | 0.013954 | 0.0041401 | 0.011967 | -0.018485 | -1.505e-05 | 0.0019119 | -0.14168 | 0.018312 | -0.011713 | 0.014631 | -0.0048534 | 0.011707 | 1.8951 | 1.9455 | 1.8265 | 1.9592 | 2.124 | 1.8768 | 1.7075 | 38.1729 | 38.269 | 38.2599 | 38.2462 | 38.1683 | 8.7845 | 8.6792 | 86.879 | 86.7096 | -36.1313 | 86.9476 | 86.9614 | 0.25177 | -36.3602 | 93.7866 | 93.6813 | -0.009155 | 123.175 | 123.262 | 29.5807 | -0.086975 | 87.1262 | 86.8973 | 86.8286 | -36.5479 | 123.2483 | 123.1705 | 123.2712 | -29.5761
2259.5156 | 123.3536 | -85.0342 | 38.1821 | 0.027466 | 0.017799 | 0.0032855 | 0.014317 | -0.01763 | 0.004044 | 0.0021255 | -0.0043486 | 0.01938 | -0.0091494 | 0.012068 | -0.0020764 | 0.012347 | 1.9684 | 1.9775 | 1.8677 | 1.9638 | 2.1149 | 1.8768 | 1.6983 | 38.1958 | 38.269 | 38.2324 | 38.2095 | 38.118 | 8.7799 | 8.6838 | 86.911 | 86.7325 | -36.0672 | 87.0117 | 86.998 | 0.2655 | -36.2137 | 93.8141 | 93.718 | 0.027466 | 123.23 | 123.2666 | 29.5486 | -0.064087 | 87.149 | 87.0026 | 86.9019 | -36.4838 | 123.2437 | 123.1522 | 123.3032 | -29.4983
2260.5156 | 123.317 | -85.0616 | 38.1729 | -0.19379 | 0.01139 | -0.00034611 | 0.013249 | -0.019126 | -0.0023648 | 0.0019119 | -0.31715 | 0.01938 | -0.009363 | 0.013563 | -0.0042126 | 0.011066 | 1.8768 | 1.9409 | 1.9043 | 2.211 | 2.1652 | 1.8814 | 1.7258 | 38.0814 | 38.2278 | 38.2187 | 38.1912 | 38.1271 | 8.7799 | 8.6838 | 86.9431 | 86.7874 | -36.0077 | 87.0026 | 87.2726 | 0.48523 | -36.2961 | 93.8416 | 93.7454 | 0.01831 | 123.143 | 123.2803 | 29.5349 | -0.045777 | 87.2269 | 86.9385 | 86.9659 | -36.4471 | 123.2529 | 123.1888 | 123.2895 | -29.4891
2261.5156 | 123.3536 | -85.0296 | 38.1775 | -0.15564 | 0.016304 | 0.0020037 | 0.015812 | -0.020835 | 0.00083955 | 0.0021255 | -0.14168 | 0.018525 | -0.009363 | 0.013136 | -0.0033582 | 0.011493 | 1.8906 | 1.918 | 1.8219 | 1.9409 | 2.1057 | 1.8768 | 1.7075 | 38.1363 | 38.269 | 38.2324 | 38.1866 | 38.118 | 8.7799 | 8.6746 | 86.9064 | 86.7371 | -36.0718 | 86.9476 | 86.9705 | 0.23346 | -36.2869 | 93.8095 | 93.7042 | 0.009156 | 123.1659 | 123.262 | 29.5578 | -0.059509 | 87.1353 | 86.9202 | 86.8515 | -36.47 | 123.2162 | 123.1476 | 123.2986 | -29.5029
2262.5156 | 123.4039 | -85.0067 | 38.1683 | -0.14038 | 0.0092541 | 0.0013629 | 0.012608 | -0.018912 | -0.004501 | 0.0010575 | -0.088272 | 0.017457 | -0.012354 | 0.012708 | -0.0063488 | 0.011279 | 1.9409 | 2.0462 | 1.9455 | 2.005 | 2.0691 | 1.886 | 1.7303 | 38.1821 | 38.356 | 38.324 | 38.15 | 38.0997 | 8.7845 | 8.6792 | 86.8927 | 86.7371 | -36.0992 | 87.0529 | 87.0117 | 0.27466 | -36.2274 | 93.7912 | 93.6859 | -0.018311 | 123.1888 | 123.3307 | 29.6448 | -0.068665 | 87.0758 | 86.9476 | 86.9522 | -36.438 | 123.1567 | 123.1064 | 123.3627 | -29.4891
2263.5156 | 123.381 | -85.1074 | 38.1363 | -0.10986 | 0.015236 | 0.0015765 | 0.01624 | -0.019553 | 0.0010532 | 0.0029801 | -0.1722 | 0.020021 | -0.0091494 | 0.012708 | -0.003999 | 0.011279 | 1.9089 | 1.9363 | 1.8265 | 1.9455 | 2.0874 | 1.8494 | 1.6937 | 38.1271 | 38.2462 | 38.1958 | 38.1683 | 38.0676 | 8.7799 | 8.6838 | 86.9568 | 86.8011 | -36.0489 | 87.0438 | 87.0529 | 0.25177 | -36.2274 | 93.8873 | 93.7912 | 0.032043 | 123.2346 | 123.3032 | 29.512 | -0.068665 | 87.1948 | 87.0163 | 86.9339 | -36.4426 | 123.2758 | 123.175 | 123.3536 | -29.4525
2264.5156 | 123.3398 | -85.0891 | 38.1271 | -0.15564 | 0.011604 | 0.0037127 | 0.013249 | -0.019766 | -0.0025784 | -0.00065152 | -0.12642 | 0.017884 | -0.010858 | 0.012281 | -0.0044262 | 0.011707 | 1.8906 | 1.9501 | 1.8448 | 1.9455 | 2.1194 | 1.8906 | 1.7075 | 38.0585 | 38.1821 | 38.1638 | 38.1363 | 38.0539 | 8.7891 | 8.67 | 86.9797 | 86.7966 | -36.0077 | 87.0392 | 87.0346 | 0.23804 | -36.2366 | 93.8782 | 93.7592 | 0.009156 | 123.1476 | 123.2529 | 29.4937 | -0.073242 | 87.2086 | 86.9797 | 86.9339 | -36.4197 | 123.2254 | 123.143 | 123.2712 | -29.4571
2265.5156 | 123.3398 | -85.1624 | 38.0859 | -0.018311 | 0.021217 | -0.0026959 | 0.015172 | -0.018698 | 0.0036166 | 0.0021255 | -0.080643 | 0.019166 | -0.0091494 | 0.014204 | -0.0035718 | 0.0095703 | 1.9592 | 1.9775 | 1.8585 | 1.9638 | 2.1561 | 1.9089 | 1.7395 | 38.0722 | 38.1638 | 38.1271 | 38.0585 | 38.0081 | 8.7799 | 8.6792 | 87.0712 | 86.9019 | -35.9299 | 87.1399 | 87.1262 | 0.2243 | -36.1267 | 93.9423 | 93.8416 | -0.027465 | 123.2346 | 123.2895 | 29.4479 | -0.077819 | 87.3184 | 87.1216 | 87.0209 | -36.3464 | 123.2208 | 123.1705 | 123.3261 | -29.4067
2266.5156 | 123.3902 | -85.1303 | 38.0768 | -0.16327 | 0.0083997 | 0.0034991 | 0.013463 | -0.018698 | -0.00086945 | 0.00063028 | -0.10353 | 0.018312 | -0.011499 | 0.015486 | -0.0052808 | 0.011493 | 1.9455 | 2.0416 | 1.9318 | 2.005 | 2.0828 | 1.8997 | 1.7166 | 38.0676 | 38.205 | 38.1866 | 38.0722 | 37.9944 | 8.7845 | 8.6838 | 87.03 | 86.8469 | -35.994 | 87.1719 | 87.1353 | 0.28839 | -36.1313 | 93.9148 | 93.8141 | -0.004577 | 123.1979 | 123.317 | 29.5029 | -0.082397 | 87.2131 | 87.0758 | 87.0621 | -36.3602 | 123.2025 | 123.1247 | 123.3353 | -29.393
2267.5156 | 123.3673 | -85.1532 | 38.0447 | -0.1709 | 0.013099 | 0.0011493 | 0.01389 | -0.019766 | 0.0025486 | 0.0010575 | -0.18745 | 0.018525 | -0.011927 | 0.015486 | -0.0016492 | 0.0097839 | 1.886 | 1.9318 | 1.8173 | 1.9318 | 2.1149 | 1.8631 | 1.7029 | 37.999 | 38.118 | 38.0905 | 38.0859 | 37.999 | 8.7799 | 8.6838 | 87.0163 | 86.8561 | -35.9299 | 87.085 | 87.085 | 0.22888 | -36.1588 | 93.9331 | 93.837 | 0.041198 | 123.1522 | 123.2437 | 29.4067 | -0.045777 | 87.2681 | 87.0392 | 86.9705 | -36.3419 | 123.2391 | 123.1522 | 123.2712 | -29.361
2268.5156 | 123.5641 | -85.1303 | 38.0493 | -0.041199 | 0.0096813 | 0.0052081 | 0.013463 | -0.018912 | -0.0055692 | 0.0023391 | -0.011978 | 0.018953 | -0.013636 | 0.013563 | -0.0054944 | 0.012775 | 1.9638 | 2.0874 | 1.9455 | 2.0142 | 2.0691 | 1.9226 | 1.7349 | 38.1409 | 38.2553 | 38.2416 | 38.0081 | 37.9623 | 8.7845 | 8.6838 | 87.0529 | 86.8652 | -35.9802 | 87.2177 | 87.1445 | 0.27924 | -36.0855 | 93.9148 | 93.8141 | -0.041198 | 123.2712 | 123.3719 | 29.5578 | -0.086975 | 87.1994 | 87.0941 | 87.0758 | -36.3144 | 123.1384 | 123.0927 | 123.3856 | -29.3655
2269.5156 | 123.4177 | -85.1715 | 38.0035 | -0.14038 | 0.010109 | 0.0043537 | 0.012181 | -0.017417 | -0.0015102 | 0.0016983 | -0.14931 | 0.017671 | -0.010004 | 0.012708 | -0.0033582 | 0.011493 | 1.9684 | 2.0462 | 1.9409 | 1.9867 | 2.0828 | 1.8906 | 1.7258 | 38.063 | 38.1775 | 38.15 | 38.0173 | 37.9211 | 8.7845 | 8.6792 | 87.0621 | 86.8973 | -35.9207 | 87.2177 | 87.1582 | 0.26092 | -36.0352 | 93.956 | 93.8507 | 0.013733 | 123.2346 | 123.3215 | 29.4708 | -0.082397 | 87.2543 | 87.1399 | 87.1124 | -36.2778 | 123.1888 | 123.0927 | 123.349 | -29.3243
2270.5156 | 123.4451 | -85.1807 | 37.9761 | 0.11902 | 0.0098951 | 0.0043537 | 0.010045 | -0.021262 | -0.0040738 | -0.00065152 | -0.065384 | 0.015962 | -0.012567 | 0.012281 | -0.0031446 | 0.011279 | 1.9775 | 2.0737 | 1.9409 | 2.005 | 2.0691 | 1.8906 | 1.7258 | 38.0539 | 38.1912 | 38.1454 | 37.9715 | 37.9257 | 8.7799 | 8.6838 | 87.0712 | 86.9064 | -35.907 | 87.2543 | 87.1857 | 0.27924 | -35.9985 | 93.9606 | 93.8644 | -0.004577 | 123.2346 | 123.3261 | 29.4617 | -0.050354 | 87.2498 | 87.1582 | 87.1216 | -36.2503 | 123.1522 | 123.1064 | 123.3719 | -29.2923
2271.5156 | 123.3215 | -85.2631 | 37.9578 | -0.18616 | 0.011177 | 0.0034991 | 0.01389 | -0.020621 | 0.00019875 | -0.00022432 | -0.2256 | 0.018098 | -0.011927 | 0.012281 | -0.0035718 | 0.0095703 | 1.9089 | 1.9775 | 1.8539 | 1.9363 | 2.1011 | 1.8631 | 1.712 | 37.9028 | 38.0127 | 37.9715 | 37.9944 | 37.9074 | 8.7799 | 8.6792 | 87.1262 | 86.9751 | -35.8566 | 87.2406 | 87.1994 | 0.2243 | -36.0489 | 94.043 | 93.9423 | 0.036621 | 123.1659 | 123.2346 | 29.2923 | -0.050354 | 87.3642 | 87.1719 | 87.117 | -36.2457 | 123.2574 | 123.1705 | 123.2758 | -29.2786
2272.5156 | 123.4726 | -85.2539 | 37.9257 | -0.010681 | 0.0090405 | 0.0034991 | 0.011967 | -0.017844 | -0.0025784 | -0.00086512 | -0.073013 | 0.017884 | -0.01449 | 0.013563 | -0.0037854 | 0.010852 | 1.9958 | 2.0828 | 1.9501 | 2.0096 | 2.0691 | 1.8906 | 1.7487 | 38.0219 | 38.1592 | 38.1042 | 37.9303 | 37.8708 | 8.7845 | 8.6792 | 87.1445 | 87.0026 | -35.8566 | 87.3367 | 87.2635 | 0.26093 | -35.9299 | 94.0384 | 93.9331 | 0.004578 | 123.2758 | 123.3582 | 29.425 | -0.054931 | 87.323 | 87.2498 | 87.204 | -36.1771 | 123.1842 | 123.1247 | 123.4131 | -29.2465
2273.5156 | 123.3902 | -85.2402 | 37.944 | -0.15564 | 0.012031 | 0.0056353 | 0.016026 | -0.020407 | -0.00044225 | -1.0724e-05 | -0.20271 | 0.016603 | -0.010431 | 0.013349 | -0.0035718 | 0.011066 | 1.9547 | 2.0691 | 1.9272 | 2.0004 | 2.0874 | 1.8906 | 1.712 | 37.9898 | 38.0905 | 38.0585 | 37.9486 | 37.8799 | 8.7845 | 8.6838 | 87.1307 | 86.9522 | -35.8566 | 87.3093 | 87.2406 | 0.28839 | -35.9894 | 94.0247 | 93.9239 | 0.004577 | 123.23 | 123.2986 | 29.3747 | -0.064087 | 87.3276 | 87.1948 | 87.1674 | -36.232 | 123.1888 | 123.1201 | 123.3307 | -29.2603
2274.5156 | 123.3673 | -85.3043 | 37.8937 | -0.071716 | 0.018867 | 0.0022175 | 0.017735 | -0.016562 | 0.0044712 | 0.0025529 | -0.11879 | 0.018953 | -0.0095768 | 0.015058 | -0.00079463 | 0.0087157 | 2.1606 | 2.0737 | 1.886 | 2.0508 | 2.1103 | 1.9089 | 1.7532 | 37.9532 | 38.0081 | 37.9578 | 37.9211 | 37.8433 | 8.7753 | 8.6792 | 87.2131 | 87.0575 | -35.7834 | 87.3779 | 87.355 | 0.29755 | -35.733 | 94.0796 | 93.9835 | 0.027466 | 123.2574 | 123.262 | 29.2786 | -0.050354 | 87.4146 | 87.4649 | 87.1902 | -36.1404 | 123.2254 | 123.1476 | 123.3124 | -29.2145
2275.5156 | 123.3627 | -85.318 | 37.8845 | -0.010681 | 0.016731 | 0.0028583 | 0.014103 | -0.021262 | 0.0044712 | 0.0040481 | -0.050125 | 0.018312 | -0.011286 | 0.013349 | -0.0018628 | 0.011707 | 1.9318 | 1.9821 | 1.8539 | 1.9363 | 2.0691 | 1.8585 | 1.6983 | 37.9074 | 37.9532 | 37.9211 | 37.8891 | 37.793 | 8.7799 | 8.6929 | 87.1765 | 87.0163 | -35.8154 | 87.3001 | 87.2543 | 0.23804 | -35.9528 | 94.0979 | 94.0109 | 0.004578 | 123.2254 | 123.2391 | 29.2282 | -0.091552 | 87.3871 | 87.2498 | 87.1719 | -36.1862 | 123.2071 | 123.111 | 123.2712 | -29.1916
2276.5156 | 123.3948 | -85.3088 | 37.8387 | 0.15717 | 0.01075 | 0.0026447 | 0.010045 | -0.018485 | -0.0042874 | 0.0031937 | 0.18639 | 0.017457 | -0.011499 | 0.016126 | -0.0061352 | 0.012561 | 1.8951 | 1.9913 | 1.886 | 1.9318 | 2.0554 | 1.9135 | 1.7303 | 37.8891 | 37.9761 | 37.9761 | 37.8387 | 37.7655 | 8.7845 | 8.6884 | 87.2223 | 87.0392 | -35.7834 | 87.3001 | 87.2406 | 0.20142 | -35.9436 | 94.0933 | 93.9972 | 0 | 123.1979 | 123.2849 | 29.2877 | -0.073242 | 87.3642 | 87.204 | 87.1948 | -36.1084 | 123.1476 | 123.0743 | 123.2849 | -29.1504
2277.5156 | 123.4451 | -85.3271 | 37.8159 | -0.094604 | 0.0094677 | 0.0028583 | 0.01624 | -0.017203 | 0.0012668 | 0.0036209 | -0.14931 | 0.018739 | -0.01214 | 0.01164 | -0.0054944 | 0.0095703 | 1.7303 | 2.1378 | 1.9821 | 1.9501 | 2.037 | 1.8768 | 1.7075 | 37.9211 | 38.0585 | 38.0219 | 37.8296 | 37.7701 | 8.7845 | 8.6884 | 87.204 | 87.0346 | -35.7788 | 87.4649 | 87.2772 | 0.24262 | -36.0855 | 94.1116 | 94.0155 | 0.013733 | 123.2483 | 123.349 | 29.3335 | -0.045776 | 87.3642 | 87.0575 | 87.3093 | -36.1084 | 123.1567 | 123.0972 | 123.3856 | -29.1275
2278.5156 | 123.4177 | -85.3409 | 37.8113 | 0.29449 | 0.0088269 | 0.0032855 | 0.011967 | -0.018912 | -0.0030056 | 0.0029801 | 0.087204 | 0.016603 | -0.013422 | 0.012922 | -0.005708 | 0.012561 | 1.8814 | 1.973 | 1.8723 | 1.9363 | 2.0508 | 1.8631 | 1.68 | 37.8845 | 37.9715 | 37.9486 | 37.8204 | 37.7335 | 8.7799 | 8.6792 | 87.204 | 87.0209 | -35.7605 | 87.3138 | 87.2772 | 0.25635 | -35.9299 | 94.1208 | 94.0201 | 0.009156 | 123.2254 | 123.2895 | 29.2694 | -0.07782 | 87.3917 | 87.2223 | 87.2131 | -36.1313 | 123.1613 | 123.0743 | 123.3124 | -29.1321
2279.5156 | 123.4589 | -85.3729 | 37.7426 | -0.041199 | 0.0088269 | 0.0030719 | 0.0094038 | -0.018271 | -0.0036464 | -0.00065152 | -0.11879 | 0.017884 | -0.01214 | 0.012281 | -0.0044262 | 0.010638 | 1.9775 | 2.0462 | 1.9272 | 1.9821 | 2.0737 | 1.8768 | 1.7212 | 37.8983 | 37.9761 | 37.9715 | 37.7563 | 37.7106 | 8.7845 | 8.6838 | 87.2498 | 87.0941 | -35.6689 | 87.4191 | 87.355 | 0.26093 | -35.7651 | 94.1574 | 94.0567 | 0.013733 | 123.2712 | 123.3444 | 29.2877 | -0.032044 | 87.4466 | 87.3505 | 87.3001 | -36.0214 | 123.1293 | 123.0835 | 123.349 | -29.0588
2280.5156 | 123.3719 | -85.4553 | 37.738 | -0.16327 | 0.015663 | 0.0020037 | 0.017949 | -0.021475 | 0.0059666 | 0.0016983 | -0.28664 | 0.019593 | -0.010645 | 0.01399 | -0.0033582 | 0.0076477 | 1.9363 | 1.9318 | 1.8219 | 1.9226 | 2.092 | 1.8539 | 1.6754 | 37.7884 | 37.8525 | 37.7975 | 37.7609 | 37.6648 | 8.7845 | 8.6746 | 87.3093 | 87.1307 | -35.6461 | 87.3871 | 87.3779 | 0.24719 | -35.8017 | 94.2398 | 94.1299 | 0.022888 | 123.2437 | 123.2529 | 29.1229 | -0.073242 | 87.5473 | 87.3917 | 87.2772 | -36.0626 | 123.2162 | 123.1201 | 123.3078 | -29.0634
2281.5156 | 123.4268 | -85.4691 | 37.6831 | 0.0045777 | 0.01139 | 0.0041401 | 0.011967 | -0.021262 | -0.0051418 | 0.00063028 | 0.026169 | 0.017671 | -0.013422 | 0.015272 | -0.0052808 | 0.011493 | 1.9089 | 2.005 | 1.8814 | 1.9547 | 2.0691 | 1.8677 | 1.712 | 37.7884 | 37.8799 | 37.8662 | 37.7151 | 37.6328 | 8.7799 | 8.6792 | 87.3367 | 87.1811 | -35.614 | 87.4741 | 87.4237 | 0.24262 | -35.7742 | 94.249 | 94.1483 | 0.032044 | 123.2574 | 123.3353 | 29.187 | -0.050354 | 87.5381 | 87.3779 | 87.3505 | -35.9711 | 123.1842 | 123.1018 | 123.349 | -29.0039
2282.5156 | 123.4268 | -85.4599 | 37.6648 | -0.93384 | 0.011818 | 0.0034991 | 0.012181 | -0.018698 | 0.0036166 | 0.0027665 | 0.17876 | 0.017884 | -0.010645 | 0.014417 | -0.0020764 | 0.011066 | 1.9363 | 2.0325 | 1.918 | 1.9501 | 2.0142 | 1.8539 | 1.6983 | 37.7838 | 37.8525 | 37.8342 | 37.6739 | 37.5732 | 8.7845 | 8.6746 | 87.3138 | 87.1582 | -35.6506 | 87.4924 | 87.41 | 0.25177 | -35.7285 | 94.2444 | 94.1345 | 0.009155 | 123.2437 | 123.2941 | 29.1595 | -0.091553 | 87.4741 | 87.3962 | 87.3779 | -35.9665 | 123.1338 | 123.0331 | 123.3124 | -28.9902
2283.5156 | 123.4451 | -85.4874 | 37.6739 | 0.027466 | 0.0079723 | 0.0049945 | 0.012181 | -0.021903 | -0.0030056 | 0.0044755 | 0.01091 | 0.017244 | -0.014063 | 0.012922 | -0.003999 | 0.013202 | 1.918 | 1.9913 | 1.8951 | 1.9455 | 2.0279 | 1.8631 | 1.7075 | 37.7609 | 37.8479 | 37.825 | 37.6556 | 37.6053 | 8.7845 | 8.6838 | 87.3505 | 87.1948 | -35.6461 | 87.4786 | 87.4329 | 0.23804 | -35.7559 | 94.2719 | 94.1711 | -0.01831 | 123.2483 | 123.3124 | 29.1412 | -0.068664 | 87.5153 | 87.4054 | 87.3825 | -35.9665 | 123.143 | 123.0927 | 123.3353 | -28.9902
2284.5156 | 123.4177 | -85.5286 | 37.6144 | 0.17242 | 0.0092541 | 0.0011493 | 0.0083356 | -0.018912 | -0.00022865 | 0.0012711 | 0.15587 | 0.018525 | -0.011927 | 0.013136 | -0.0044262 | 0.011066 | 1.9547 | 2.0004 | 1.886 | 1.9455 | 2.0233 | 1.8585 | 1.7029 | 37.7243 | 37.7609 | 37.7563 | 37.619 | 37.5641 | 8.7845 | 8.6884 | 87.3871 | 87.2314 | -35.5911 | 87.529 | 87.4741 | 0.24261 | -35.6598 | 94.313 | 94.2169 | 0.004578 | 123.2529 | 123.2849 | 29.068 | -0.050354 | 87.5519 | 87.4832 | 87.4146 | -35.9116 | 123.1476 | 123.0927 | 123.2895 | -28.9261
2285.5312 | 123.3353 | -85.5515 | 37.6694 | 0.10376 | 0.014381 | 0.0045673 | 0.015812 | -0.018057 | 0.002335 | 0.0038345 | -0.20271 | 0.021516 | -0.0087222 | 0.015486 | -0.0037854 | 0.010425 | 1.8997 | 1.8814 | 1.7578 | 1.886 | 2.0737 | 1.8265 | 1.6525 | 37.6373 | 37.7151 | 37.6968 | 37.7197 | 37.6328 | 8.7753 | 8.6838 | 87.3779 | 87.204 | -35.5957 | 87.4329 | 87.4374 | 0.23346 | -35.7697 | 94.3268 | 94.2352 | 0.050354 | 123.1888 | 123.2483 | 29.0131 | -0.036622 | 87.6251 | 87.4512 | 87.3093 | -36.0168 | 123.2712 | 123.1842 | 123.2666 | -28.9856
2286.5156 | 123.4451 | -85.5652 | 37.5824 | 1.6068 | 0.015449 | 0.0030719 | 0.013463 | -0.017844 | 0.00083955 | 0.0010575 | 0.20164 | 0.017884 | -0.010645 | 0.014204 | -0.0012218 | 0.011279 | 1.973 | 1.9867 | 1.8631 | 1.9501 | 1.9867 | 1.8219 | 1.6708 | 37.7197 | 37.7838 | 37.7655 | 37.5916 | 37.5 | 8.7845 | 8.6884 | 87.3871 | 87.236 | -35.5957 | 87.5519 | 87.5153 | 0.27924 | -35.6094 | 94.3497 | 94.2535 | 0.009156 | 123.2849 | 123.3307 | 29.0771 | -0.082397 | 87.5519 | 87.5381 | 87.4283 | -35.9116 | 123.1567 | 123.0652 | 123.349 | -28.894
2287.5156 | 123.4177 | -85.6018 | 37.5732 | 0.18005 | 0.011604 | 0.00050849 | 0.010472 | -0.018912 | -0.00022865 | 0.0012711 | 0.19402 | 0.017884 | -0.015558 | 0.012068 | -0.0033582 | 0.011707 | 1.9272 | 1.9821 | 1.8631 | 1.918 | 2.0187 | 1.8539 | 1.6937 | 37.6328 | 37.6968 | 37.7014 | 37.5778 | 37.4954 | 8.7799 | 8.6792 | 87.4557 | 87.2955 | -35.5545 | 87.5839 | 87.5198 | 0.2243 | -35.6461 | 94.3817 | 94.281 | 0.004578 | 123.2346 | 123.3032 | 29.0222 | -0.07782 | 87.6205 | 87.529 | 87.4649 | -35.8795 | 123.1796 | 123.0972 | 123.2986 | -28.894
2288.5156 | 123.4314 | -85.6155 | 37.5183 | 0.20294 | 0.016304 | 0.0022175 | 0.010899 | -0.019553 | 0.0048984 | 0.0027665 | 0.15587 | 0.020234 | -0.010431 | 0.01164 | 0.00091437 | 0.0089295 | 1.9409 | 1.9409 | 1.8494 | 1.9272 | 2.005 | 1.8311 | 1.6891 | 37.6328 | 37.706 | 37.6968 | 37.5458 | 37.4725 | 8.7799 | 8.6838 | 87.4466 | 87.3047 | -35.5133 | 87.5565 | 87.5427 | 0.23804 | -35.5774 | 94.3954 | 94.2993 | 0.027465 | 123.2483 | 123.3124 | 29.0131 | -0.045777 | 87.6205 | 87.5565 | 87.4649 | -35.8292 | 123.1613 | 123.0881 | 123.3215 | -28.8345
2289.5156 | 123.4451 | -85.643 | 37.5 | 0.26398 | 0.01374 | 0.0024311 | 0.012394 | -0.019339 | 0.0031894 | 0.0025529 | 0.17876 | 0.019807 | -0.012781 | 0.011213 | -0.0012218 | 0.0082885 | 1.9592 | 1.9638 | 1.8539 | 1.9409 | 2.0004 | 1.8539 | 1.68 | 37.619 | 37.7243 | 37.706 | 37.5137 | 37.4634 | 8.7845 | 8.6838 | 87.4969 | 87.323 | -35.4996 | 87.6068 | 87.5839 | 0.26092 | -35.5408 | 94.4275 | 94.3268 | 0.013733 | 123.262 | 123.349 | 29.0222 | -0.036621 | 87.6434 | 87.6022 | 87.4969 | -35.82 | 123.1567 | 123.1064 | 123.3673 | -28.8162
2290.5156 | 123.4222 | -85.6338 | 37.5504 | 0.11139 | 0.0081861 | 0.0049945 | 0.011967 | -0.021475 | -0.0032192 | 0.0014847 | 0.10246 | 0.017244 | -0.015985 | 0.012922 | -0.0031446 | 0.011279 | 1.8906 | 1.918 | 1.8265 | 1.9135 | 2.0233 | 1.8448 | 1.6754 | 37.5687 | 37.6739 | 37.6694 | 37.5275 | 37.4725 | 8.7753 | 8.6838 | 87.4786 | 87.3093 | -35.527 | 87.5519 | 87.5473 | 0.23804 | -35.6598 | 94.4092 | 94.3176 | -0.022888 | 123.2025 | 123.3032 | 28.9856 | -0.07782 | 87.6572 | 87.5244 | 87.4603 | -35.8749 | 123.1613 | 123.1064 | 123.3078 | -28.8666
2291.5156 | 123.4268 | -85.6979 | 37.4359 | 0.15717 | 0.011604 | 0.0041401 | 0.010899 | -0.019126 | 0.0021214 | 0.0023391 | 0.20927 | 0.019166 | -0.015345 | 0.012068 | -0.0014356 | 0.011279 | 1.9455 | 1.9775 | 1.8631 | 1.9089 | 1.9867 | 1.8265 | 1.6663 | 37.5641 | 37.619 | 37.6144 | 37.4588 | 37.3718 | 8.7936 | 8.6884 | 87.5244 | 87.3642 | -35.4492 | 87.6755 | 87.6068 | 0.24262 | -35.4904 | 94.4916 | 94.3863 | 0.022888 | 123.262 | 123.3124 | 28.9261 | -0.064087 | 87.6846 | 87.6434 | 87.561 | -35.7697 | 123.1567 | 123.0698 | 123.317 | -28.7476
2292.5156 | 123.3719 | -85.73 | 37.4817 | 0.18005 | 0.015449 | 0.0013629 | 0.013463 | -0.019766 | 0.0053256 | -1.0724e-05 | 0.17113 | 0.021302 | -0.011072 | 0.01164 | -0.00229 | 0.0093567 | 1.8723 | 1.8356 | 1.7349 | 1.8402 | 2.0645 | 1.8082 | 1.6205 | 37.5092 | 37.5641 | 37.5549 | 37.5183 | 37.4313 | 8.7799 | 8.6838 | 87.5381 | 87.3505 | -35.4172 | 87.5656 | 87.5702 | 0.21973 | -35.6094 | 94.5099 | 94.4138 | 0.036622 | 123.2391 | 123.2849 | 28.8712 | -0.050354 | 87.7945 | 87.6022 | 87.4649 | -35.8612 | 123.2483 | 123.1613 | 123.2941 | -28.7979
2293.5156 | 123.4268 | -85.7208 | 37.413 | 0.16479 | 0.01075 | -0.00055971 | 0.010258 | -0.018057 | 0.00041235 | 0.0034073 | 0.23979 | 0.019807 | -0.013422 | 0.013777 | -0.003999 | 0.011707 | 1.9363 | 1.9684 | 1.8539 | 1.9226 | 1.973 | 1.8356 | 1.6754 | 37.5595 | 37.6053 | 37.6099 | 37.4359 | 37.3535 | 8.7936 | 8.6838 | 87.5565 | 87.3962 | -35.4401 | 87.6892 | 87.6434 | 0.24719 | -35.4767 | 94.5145 | 94.4046 | 0.022888 | 123.2803 | 123.3307 | 28.9261 | -0.059509 | 87.6938 | 87.6572 | 87.5748 | -35.7376 | 123.1567 | 123.0743 | 123.3261 | -28.7292
2294.5156 | 123.349 | -85.7849 | 37.4451 | 0.14191 | 0.017158 | 0.00050849 | 0.014531 | -0.018485 | 0.0042576 | 0.00063028 | -0.12642 | 0.022371 | -0.010431 | 0.014204 | -0.00079463 | 0.0089295 | 2.0737 | 1.8356 | 1.7029 | 1.8219 | 2.0554 | 1.8356 | 1.6617 | 37.4313 | 37.468 | 37.4588 | 37.4725 | 37.4222 | 8.7845 | 8.6792 | 87.6205 | 87.4466 | -35.3897 | 87.6205 | 87.6068 | 0.16022 | -35.3714 | 94.5694 | 94.4641 | 0.027466 | 123.2162 | 123.2437 | 28.7796 | -0.022888 | 87.8403 | 87.8586 | 87.4878 | -35.7834 | 123.2574 | 123.2071 | 123.2529 | -28.7659
2295.5156 | 123.4039 | -85.7666 | 37.3901 | 0.027466 | 0.011177 | 0.0037127 | 0.011326 | -0.020621 | -0.0038602 | 0.0010575 | 0.11009 | 0.017244 | -0.01214 | 0.012068 | -0.0033582 | 0.012775 | 1.9226 | 1.7303 | 1.799 | 1.8585 | 1.9501 | 1.7807 | 1.6159 | 37.3993 | 37.5 | 37.5183 | 37.3718 | 37.3444 | 8.7753 | 8.6746 | 87.5473 | 87.3825 | -35.4401 | 87.4969 | 87.6251 | 0.24262 | -35.4675 | 94.5419 | 94.4412 | -0.018311 | 123.1659 | 123.2849 | 28.8437 | -0.045777 | 87.7167 | 87.6892 | 87.5656 | -35.7742 | 123.1384 | 123.111 | 123.2666 | -28.7155
2296.5156 | 123.317 | -85.8307 | 37.413 | 0.10376 | 0.017372 | 0.0017901 | 0.015812 | -0.018057 | 0.005753 | 0.0042619 | 0.087204 | 0.020662 | -0.010218 | 0.012708 | -0.0025036 | 0.0097839 | 1.8539 | 1.7944 | 1.7258 | 1.8265 | 2.0142 | 1.7761 | 1.6205 | 37.3718 | 37.4359 | 37.4039 | 37.4359 | 37.3764 | 8.7799 | 8.6792 | 87.6068 | 87.4512 | -35.3989 | 87.6251 | 87.6572 | 0.20599 | -35.5591 | 94.6106 | 94.5099 | 0.022888 | 123.2025 | 123.2346 | 28.7247 | -0.036621 | 87.8448 | 87.6846 | 87.5565 | -35.7925 | 123.2666 | 123.2071 | 123.2666 | -28.7338
2297.5156 | 123.3536 | -85.8215 | 37.381 | 0.12665 | 0.016304 | 0.0024311 | 0.010685 | -0.017844 | 0.0031894 | 0.0055435 | 0.17113 | 0.020448 | -0.0089358 | 0.015058 | -0.0010082 | 0.012134 | 1.8356 | 1.8219 | 1.7258 | 1.8265 | 2.0187 | 1.7899 | 1.6067 | 37.3993 | 37.4405 | 37.4268 | 37.4496 | 37.3489 | 8.7799 | 8.6838 | 87.6114 | 87.4283 | -35.3622 | 87.6434 | 87.648 | 0.21973 | -35.5453 | 94.6014 | 94.5053 | 0.068665 | 123.2208 | 123.2483 | 28.743 | -0.032043 | 87.8403 | 87.6572 | 87.5473 | -35.7742 | 123.2712 | 123.1705 | 123.262 | -28.6972
2298.5156 | 123.1384 | -85.8948 | 37.2986 | 0.09613 | 0.01844 | 0.0015765 | 0.013676 | -0.017203 | 0.0031894 | 0.0057571 | -0.011978 | 0.021516 | -0.011499 | 0.012708 | -0.0027172 | 0.012134 | 1.8219 | 1.7944 | 1.712 | 1.8265 | 2.005 | 1.7853 | 1.6067 | 37.2849 | 37.3581 | 37.3352 | 37.3672 | 37.3077 | 8.7753 | 8.6792 | 87.6801 | 87.5015 | -35.2936 | 87.6892 | 87.7213 | 0.21973 | -35.4767 | 94.6701 | 94.574 | 0.068665 | 123.1796 | 123.23 | 28.656 | 0.009155 | 87.8998 | 87.7167 | 87.6068 | -35.6918 | 123.262 | 123.2025 | 123.2529 | -28.6194
2299.5156 | 123.468 | -85.8627 | 37.2986 | -0.49896 | 0.011818 | 0.0030719 | 0.011754 | -0.018698 | -0.0023648 | 0.0053299 | 0.26268 | 0.018525 | -0.012354 | 0.013349 | -0.0033582 | 0.012347 | 1.8951 | 1.9592 | 1.8631 | 1.9135 | 1.9409 | 1.7853 | 1.6388 | 37.4176 | 37.4908 | 37.4771 | 37.3215 | 37.2391 | 8.7936 | 8.6929 | 87.648 | 87.5015 | -35.3577 | 87.822 | 87.7762 | 0.27466 | -35.4034 | 94.6564 | 94.5557 | 0.022888 | 123.2803 | 123.3398 | 28.7842 | -0.059509 | 87.8036 | 87.7579 | 87.7258 | -35.6598 | 123.1842 | 123.1018 | 123.3536 | -28.6057
2300.5156 | 123.2941 | -85.8902 | 37.3215 | 0.057983 | 0.017372 | 0.0026447 | 0.015172 | -0.01998 | 0.0036166 | 0.0036209 | -0.0043486 | 0.020021 | -0.0091494 | 0.010359 | -0.0052808 | 0.011279 | 1.8219 | 1.7715 | 1.6937 | 1.8219 | 2.0233 | 1.767 | 1.6159 | 37.294 | 37.294 | 37.3901 | 37.3398 | 37.294 | 8.7799 | 8.6792 | 87.6572 | 87.5061 | -35.2982 | 87.6617 | 87.7121 | 0.20599 | -35.4996 | 94.6701 | 94.5694 | 0.018311 | 123.1842 | 123.2803 | 28.7109 | -0.027466 | 87.9135 | 87.7121 | 87.5839 | -35.7056 | 123.23 | 123.1842 | 123.1842 | -28.6423
2301.5156 | 123.4726 | -85.8765 | 37.2299 | 0.18768 | 0.013099 | 0.00050849 | 0.011754 | -0.018698 | -0.00086945 | 0.0023391 | 0.22453 | 0.018098 | -0.011072 | 0.010359 | -0.0025036 | 0.0097839 | 1.886 | 1.9135 | 1.8219 | 1.8906 | 1.9684 | 1.799 | 1.6205 | 37.2757 | 37.2528 | 37.5137 | 37.2299 | 37.1796 | 8.7891 | 8.6792 | 87.6755 | 87.4969 | -35.2615 | 87.7899 | 87.767 | 0.27008 | -35.3439 | 94.6655 | 94.5557 | 0 | 123.1522 | 123.3902 | 28.8345 | -0.050354 | 87.8448 | 87.7625 | 87.6984 | -35.6094 | 123.1064 | 123.056 | 123.1293 | -28.5507
2302.5156 | 123.3536 | -85.9726 | 37.2299 | -0.048828 | 0.019081 | 0.0043537 | 0.014317 | -0.018057 | 0.002335 | 0.0034073 | -0.019608 | 0.021302 | -0.010858 | 0.014845 | -0.0018628 | 0.011493 | 1.8631 | 1.8402 | 1.7395 | 1.8356 | 1.9958 | 1.7853 | 1.5976 | 37.2345 | 37.3077 | 37.2757 | 37.2391 | 37.1933 | 8.7753 | 8.6838 | 87.7579 | 87.5702 | -35.2341 | 87.8128 | 87.8082 | 0.23804 | -35.3668 | 94.7479 | 94.6564 | 0.009156 | 123.2071 | 123.2483 | 28.5919 | -0.036621 | 87.9684 | 87.8357 | 87.7121 | -35.6323 | 123.2117 | 123.1659 | 123.2803 | -28.5461
2303.5156 | 123.3307 | -86.0092 | 37.2208 | 0.042725 | 0.019081 | 0.0015765 | 0.012181 | -0.018057 | 0.0027622 | 0.0040481 | 0.049057 | 0.020662 | -0.0089358 | 0.013136 | -0.00058103 | 0.0085021 | 1.8036 | 1.7944 | 1.7075 | 1.8127 | 1.9913 | 1.7578 | 1.593 | 37.1796 | 37.2665 | 37.2482 | 37.2345 | 37.1933 | 8.7845 | 8.6792 | 87.767 | 87.6022 | -35.2295 | 87.8036 | 87.822 | 0.21973 | -35.4172 | 94.7937 | 94.6884 | 0.013733 | 123.1888 | 123.2574 | 28.569 | -0.027466 | 88.0005 | 87.8128 | 87.7167 | -35.6277 | 123.2437 | 123.2025 | 123.2758 | -28.5416
2304.5156 | 123.3719 | -86.0367 | 37.175 | 1.889 | 0.019935 | 0.0022175 | 0.014531 | -0.020194 | 0.00019875 | 0.0042619 | -0.057755 | 0.021089 | -0.009363 | 0.01399 | -0.0033582 | 0.011279 | 1.8951 | 1.8677 | 1.7624 | 1.8631 | 2.0325 | 1.8082 | 1.6479 | 37.2162 | 37.3123 | 37.2574 | 37.2253 | 37.1567 | 8.7799 | 8.6838 | 87.8448 | 87.6846 | -35.1425 | 87.9044 | 87.8998 | 0.21515 | -35.2798 | 94.8166 | 94.7205 | 0.050354 | 123.2529 | 123.2941 | 28.5736 | -0.018311 | 88.0692 | 87.9318 | 87.7991 | -35.527 | 123.262 | 123.1934 | 123.349 | -28.4912
2305.5156 | 123.3765 | -86.0321 | 37.2025 | 0.16479 | 0.017586 | 0.0028583 | 0.01389 | -0.018698 | -1.505e-05 | 0.0036209 | 0.22453 | 0.021516 | -0.011713 | 0.013777 | -0.0025036 | 0.011066 | 1.7761 | 1.7761 | 1.6983 | 1.7899 | 1.9867 | 1.7395 | 1.5793 | 37.1841 | 37.262 | 37.2665 | 37.2162 | 37.1475 | 8.7799 | 8.67 | 87.7716 | 87.6114 | -35.2158 | 87.8082 | 87.822 | 0.21057 | -35.4263 | 94.812 | 94.7021 | 0.013733 | 123.2162 | 123.2986 | 28.5965 | -0.054932 | 88.0188 | 87.8082 | 87.7304 | -35.6232 | 123.2483 | 123.1796 | 123.2941 | -28.5324
2306.5156 | 123.3536 | -86.0229 | 37.207 | -0.064087 | 0.017158 | 0.0011493 | 0.012608 | -0.019339 | 0.003403 | 0.0021255 | -0.034867 | 0.01938 | -0.011713 | 0.011213 | -0.0016492 | 0.010425 | 1.8265 | 1.8585 | 1.7578 | 1.8265 | 1.973 | 1.7624 | 1.593 | 37.207 | 37.294 | 37.2482 | 37.1887 | 37.1567 | 8.7799 | 8.6929 | 87.7853 | 87.616 | -35.2341 | 87.8815 | 87.8494 | 0.23346 | -35.3806 | 94.8029 | 94.7159 | -0.01831 | 123.23 | 123.2712 | 28.5553 | -0.050354 | 87.9959 | 87.8494 | 87.7808 | -35.614 | 123.2117 | 123.1796 | 123.317 | -28.5141
2307.5156 | 123.349 | -86.0184 | 37.2162 | -0.14038 | 0.016517 | -0.0012005 | 0.013676 | -0.018485 | 0.0021214 | 0.0021255 | 0.15587 | 0.021302 | -0.0091494 | 0.013563 | -0.0016492 | 0.011707 | 1.7441 | 1.7624 | 1.6617 | 1.7899 | 1.9821 | 1.7395 | 1.5518 | 37.1521 | 37.2116 | 37.2162 | 37.2025 | 37.1292 | 8.7799 | 8.6838 | 87.7579 | 87.5702 | -35.2341 | 87.7808 | 87.8082 | 0.23804 | -35.4721 | 94.7983 | 94.7021 | -0.013733 | 123.1705 | 123.2346 | 28.5324 | -0.086976 | 88.0005 | 87.7625 | 87.6801 | -35.6644 | 123.2208 | 123.1476 | 123.23 | -28.5324
2308.5156 | 123.3765 | -86.0779 | 37.1658 | -0.071716 | 0.019295 | 0.0030719 | 0.014744 | -0.019126 | 0.0021214 | 0.0055435 | -0.33241 | 0.018739 | -0.010645 | 0.013563 | -0.0020764 | 0.010638 | 2.0554 | 1.9272 | 1.7899 | 1.8997 | 2.0279 | 1.8082 | 1.6342 | 37.175 | 37.2894 | 37.2437 | 37.1979 | 37.1521 | 8.7799 | 8.6792 | 87.886 | 87.7121 | -35.1379 | 88.0051 | 87.9776 | 0.2655 | -35.1105 | 94.8578 | 94.7571 | 0.032043 | 123.2529 | 123.3215 | 28.5645 | -0.013733 | 88.1058 | 88.1332 | 87.8677 | -35.5316 | 123.2758 | 123.23 | 123.3673 | -28.4866
2309.5156 | 123.3261 | -86.1328 | 37.1292 | 0.11139 | 0.016731 | 0.0041401 | 0.013463 | -0.018271 | 0.0025486 | 0.0025529 | -0.59944 | 0.020875 | -0.011286 | 0.012708 | -0.00229 | 0.011066 | 1.7349 | 1.5381 | 1.5289 | 1.7487 | 1.9775 | 1.7349 | 1.5839 | 37.0697 | 37.1063 | 37.1475 | 37.1613 | 37.0834 | 8.7799 | 8.6792 | 87.8677 | 87.7167 | -35.1517 | 87.6709 | 87.8815 | 0.16479 | -35.3943 | 94.9127 | 94.812 | 0.032044 | 123.2025 | 123.2803 | 28.4683 | -0.045776 | 88.1104 | 87.8677 | 87.6617 | -35.5453 | 123.2941 | 123.2162 | 123.2391 | -28.45
2310.5156 | 123.3673 | -86.1145 | 37.1201 | -0.16327 | 0.018867 | 0.00072209 | 0.013249 | -0.018912 | -0.0019376 | 0.0025529 | -0.12642 | 0.019807 | -0.012567 | 0.01399 | -0.0059216 | 0.01192 | 1.767 | 1.7853 | 1.6846 | 1.8036 | 1.9638 | 1.7349 | 1.5564 | 37.0651 | 37.1887 | 37.1613 | 37.1292 | 37.088 | 8.7799 | 8.6838 | 87.8494 | 87.6709 | -35.1562 | 87.8998 | 87.9181 | 0.24719 | -35.3531 | 94.8944 | 94.7983 | 0.009155 | 123.1796 | 123.2758 | 28.4775 | -0.032043 | 88.0783 | 87.8815 | 87.7991 | -35.5637 | 123.2437 | 123.2025 | 123.3032 | -28.4363
2311.5156 | 123.2391 | -86.1649 | 37.0605 | 0.11139 | 0.015663 | 0.0026447 | 0.014103 | -0.020194 | 0.0029758 | 0.0025529 | 0.17113 | 0.020021 | -0.009363 | 0.012708 | -0.0014356 | 0.014056 | 1.7578 | 1.7303 | 1.6388 | 1.7761 | 1.9638 | 1.712 | 1.561 | 37.001 | 37.0972 | 37.0743 | 37.1063 | 37.056 | 8.7799 | 8.67 | 87.8769 | 87.7258 | -35.0967 | 87.8952 | 87.941 | 0.21515 | -35.3027 | 94.9448 | 94.8349 | 0.045776 | 123.1659 | 123.2391 | 28.4042 | -0.004578 | 88.1287 | 87.9227 | 87.8037 | -35.4996 | 123.2712 | 123.2208 | 123.262 | -28.3905
2312.5156 | 123.3627 | -86.1237 | 37.1017 | -0.079346 | 0.017799 | 0.00072209 | 0.01389 | -0.016989 | 0.0010532 | 0.0044755 | -0.59181 | 0.018739 | -0.012567 | 0.015058 | -0.0050672 | 0.012561 | 1.8127 | 1.8173 | 1.7029 | 1.973 | 1.9775 | 1.7578 | 1.6022 | 37.1063 | 37.2482 | 37.1567 | 37.1063 | 37.056 | 8.7845 | 8.6746 | 87.8815 | 87.7258 | -35.1242 | 87.941 | 88.0966 | 0.37079 | -35.289 | 94.9081 | 94.7983 | 0.004577 | 123.23 | 123.2803 | 28.4821 | -0.045777 | 88.1012 | 87.9364 | 87.8265 | -35.4996 | 123.23 | 123.1796 | 123.3719 | -28.4271
2313.5156 | 123.3261 | -86.1923 | 37.0422 | 0.073242 | 0.018654 | 0.0022175 | 0.012394 | -0.018485 | 0.0036166 | 0.0014847 | 0.064316 | 0.018953 | -0.0095768 | 0.013563 | -0.0018628 | 0.0093567 | 1.7532 | 1.7624 | 1.6663 | 1.7715 | 1.9409 | 1.7212 | 1.5427 | 36.9873 | 37.1017 | 37.0697 | 37.0789 | 37.0193 | 8.7799 | 8.6746 | 87.9135 | 87.735 | -35.1013 | 87.9547 | 87.9639 | 0.22888 | -35.289 | 94.9722 | 94.8669 | 0.036621 | 123.1796 | 123.262 | 28.3951 | -0.022888 | 88.1332 | 87.9456 | 87.8586 | -35.4996 | 123.2712 | 123.2117 | 123.2941 | -28.3676
2314.5156 | 123.3719 | -86.1832 | 37.0514 | -0.13275 | 0.017158 | 0.0022175 | 0.015385 | -0.018698 | 0.00062595 | 0.0021255 | -0.042496 | 0.020448 | -0.011927 | 0.013777 | -0.0025036 | 0.010638 | 1.7853 | 1.8082 | 1.7029 | 1.8082 | 1.9455 | 1.7258 | 1.5427 | 37.0651 | 37.1475 | 37.1292 | 37.0789 | 37.0102 | 8.7708 | 8.6792 | 87.9089 | 87.7258 | -35.1059 | 87.9913 | 87.9913 | 0.2655 | -35.2661 | 94.9539 | 94.8624 | 0.027465 | 123.2483 | 123.3124 | 28.45 | -0.041199 | 88.1287 | 87.9684 | 87.886 | -35.5087 | 123.262 | 123.1934 | 123.3307 | -28.3722
2315.5156 | 123.3536 | -86.2198 | 37.0148 | 0.012207 | 0.017799 | 0.0017901 | 0.014103 | -0.018485 | 0.0019078 | 0.0040481 | 0.079574 | 0.018953 | -0.0091494 | 0.012708 | -0.0018628 | 0.0093567 | 1.7944 | 1.7944 | 1.6891 | 1.7944 | 1.9455 | 1.7258 | 1.5472 | 36.9919 | 37.0834 | 37.0468 | 37.0331 | 36.9598 | 8.7753 | 8.6746 | 87.9456 | 87.767 | -35.0693 | 88.0142 | 88.0142 | 0.24719 | -35.2203 | 94.9951 | 94.8944 | 0.01831 | 123.2117 | 123.2666 | 28.3722 | -0.054932 | 88.1653 | 88.0142 | 87.9089 | -35.4675 | 123.2529 | 123.1796 | 123.3032 | -28.3401
2316.5156 | 123.3673 | -86.2198 | 37.0422 | -0.1709 | 0.014168 | 0.0030719 | 0.014958 | -0.018912 | 0.0029758 | 0.0012711 | -0.11116 | 0.018098 | -0.011713 | 0.013563 | -0.0052808 | 0.0093567 | 1.7395 | 1.7624 | 1.68 | 1.7807 | 1.9501 | 1.7029 | 1.5427 | 36.9644 | 37.1109 | 37.0697 | 37.0239 | 36.9781 | 8.7799 | 8.6838 | 87.9227 | 87.7625 | -35.0922 | 87.9822 | 88.0005 | 0.23804 | -35.3027 | 94.9997 | 94.9036 | -0.01831 | 123.1842 | 123.2895 | 28.3859 | -0.064087 | 88.1699 | 87.9593 | 87.8998 | -35.4996 | 123.2437 | 123.1979 | 123.3307 | -28.3585
2317.5156 | 123.3765 | -86.2518 | 36.969 | -0.17853 | 0.017799 | 0.00072209 | 0.013035 | -0.020194 | 0.004044 | 0.0036209 | -0.17983 | 0.018098 | -0.0089358 | 0.013777 | -0.00229 | 0.012134 | 1.7624 | 1.7853 | 1.6937 | 1.8082 | 1.9455 | 1.6983 | 1.5564 | 36.9553 | 37.0743 | 37.0422 | 36.9965 | 36.9003 | 8.7753 | 8.6746 | 87.9501 | 87.8082 | -35.0235 | 88.0371 | 88.06 | 0.25177 | -35.2066 | 95.0272 | 94.9265 | 0.027466 | 123.2071 | 123.2941 | 28.3676 | -0.068664 | 88.1973 | 88.0142 | 87.9456 | -35.4126 | 123.2483 | 123.1522 | 123.3261 | -28.2944
2318.5156 | 123.3398 | -86.2701 | 36.969 | -0.094604 | 0.014381 | 0.00072209 | 0.013035 | -0.017844 | 0.0010532 | 0.0019119 | -0.14168 | 0.018312 | -0.0097904 | 0.012708 | -0.003999 | 0.011707 | 1.7212 | 1.7807 | 1.6525 | 1.7715 | 1.9638 | 1.6937 | 1.5381 | 36.8774 | 37.0239 | 36.9965 | 36.9781 | 36.9049 | 8.7845 | 8.6838 | 87.9639 | 87.8082 | -35.0052 | 88.0508 | 88.0417 | 0.23346 | -35.2478 | 95.0546 | 94.9539 | 0.009155 | 123.1476 | 123.2666 | 28.3127 | -0.064087 | 88.2339 | 87.9913 | 87.9227 | -35.4309 | 123.2483 | 123.175 | 123.2941 | -28.2852
2319.5156 | 123.3627 | -86.2839 | 36.9049 | -0.4837 | 0.016945 | 0.0011493 | 0.015385 | -0.019553 | 0.0038304 | 0.0038345 | -0.042496 | 0.020234 | -0.010645 | 0.012708 | -0.0025036 | 0.010211 | 1.799 | 1.8036 | 1.6983 | 1.7944 | 1.9547 | 1.7349 | 1.5747 | 36.9095 | 37.0193 | 36.9644 | 36.9003 | 36.8866 | 8.7799 | 8.6746 | 88.0188 | 87.8586 | -34.9503 | 88.0875 | 88.0783 | 0.21973 | -35.1059 | 95.0638 | 94.9585 | -0.004577 | 123.1934 | 123.2483 | 28.2898 | -0.01831 | 88.2385 | 88.0829 | 87.9822 | -35.3302 | 123.1842 | 123.1705 | 123.3032 | -28.2303
2320.5156 | 123.3536 | -86.3342 | 36.9141 | -0.15564 | 0.014381 | 0.0056353 | 0.010899 | -0.018485 | 0.00041235 | 0.00084388 | -0.11879 | 0.018739 | -0.012995 | 0.012922 | -0.0031446 | 0.01192 | 1.712 | 1.7624 | 1.6708 | 1.7715 | 1.9501 | 1.7166 | 1.5472 | 36.8546 | 36.9736 | 36.9461 | 36.9141 | 36.8591 | 8.7753 | 8.6746 | 88.0508 | 87.8815 | -34.964 | 88.0966 | 88.1058 | 0.2243 | -35.202 | 95.1096 | 95.0089 | 0 | 123.1888 | 123.2803 | 28.2715 | -0.054931 | 88.2843 | 88.0463 | 88.0051 | -35.3668 | 123.2483 | 123.1934 | 123.3078 | -28.2394
2321.5156 | 123.3856 | -86.3571 | 36.8866 | -0.14038 | 0.019508 | 0.0015765 | 0.013249 | -0.018057 | 0.0031894 | 0.0021255 | -0.034867 | 0.019593 | -0.011927 | 0.014204 | -0.00229 | 0.010638 | 1.7853 | 1.8219 | 1.68 | 1.8036 | 1.9318 | 1.6937 | 1.5289 | 36.8637 | 36.9598 | 36.9095 | 36.882 | 36.7996 | 8.7799 | 8.6838 | 88.0508 | 87.886 | -34.9548 | 88.179 | 88.1607 | 0.27466 | -35.1013 | 95.137 | 95.0409 | -0.004578 | 123.2208 | 123.2666 | 28.2257 | -0.086975 | 88.2889 | 88.1424 | 88.0371 | -35.3577 | 123.2391 | 123.1567 | 123.317 | -28.2028
2322.5156 | 123.3398 | -86.3617 | 36.8729 | -0.20142 | 0.011604 | 0.0041401 | 0.011326 | -0.019766 | -0.00065585 | -0.00022432 | -0.34004 | 0.016816 | -0.0095768 | 0.013777 | -0.005708 | 0.011707 | 1.7075 | 1.767 | 1.6434 | 1.8768 | 1.9638 | 1.7166 | 1.5427 | 36.7859 | 36.8729 | 36.9141 | 36.8774 | 36.8134 | 8.7891 | 8.6792 | 88.0783 | 87.9044 | -34.9091 | 88.1287 | 88.2385 | 0.33417 | -35.1654 | 95.1508 | 95.0409 | 0.004577 | 123.1476 | 123.2758 | 28.2349 | -0.05951 | 88.3255 | 88.0692 | 88.0051 | -35.3302 | 123.2391 | 123.175 | 123.2346 | -28.1937
2323.5156 | 123.3673 | -86.3983 | 36.8042 | -0.13275 | 0.01609 | 0.0011493 | 0.012822 | -0.020835 | 0.002335 | 0.0027665 | -0.16457 | 0.019593 | -0.0097904 | 0.012068 | -0.0033582 | 0.011707 | 1.712 | 1.767 | 1.6571 | 1.767 | 1.9409 | 1.7029 | 1.5289 | 36.7722 | 36.8912 | 36.8637 | 36.85 | 36.7493 | 8.7845 | 8.6792 | 88.1012 | 87.9272 | -34.8633 | 88.1653 | 88.1653 | 0.23804 | -35.0922 | 95.1828 | 95.0775 | 0.045777 | 123.1705 | 123.262 | 28.1845 | -0.054931 | 88.3392 | 88.1104 | 88.0554 | -35.2753 | 123.2483 | 123.1476 | 123.2895 | -28.125
2324.5156 | 123.4177 | -86.3937 | 36.7859 | -0.15564 | 0.01139 | 0.0039263 | 0.0089764 | -0.019339 | -0.0036464 | 0.0031937 | -0.12642 | 0.016176 | -0.012567 | 0.014631 | -0.0054944 | 0.010425 | 1.7761 | 1.8951 | 1.7715 | 1.8219 | 1.886 | 1.7349 | 1.5701 | 36.8134 | 36.9736 | 36.9095 | 36.7859 | 36.7538 | 8.7799 | 8.6792 | 88.1287 | 87.9639 | -34.8999 | 88.2889 | 88.2156 | 0.25177 | -35.0098 | 95.1736 | 95.0729 | 0 | 123.2071 | 123.3032 | 28.2303 | -0.032044 | 88.2797 | 88.1699 | 88.1653 | -35.2158 | 123.1796 | 123.1476 | 123.3673 | -28.1067
2325.5156 | 123.381 | -86.4304 | 36.7676 | -0.14801 | 0.014595 | 0.0041401 | 0.015599 | -0.01998 | 0.002335 | 0.0010575 | -0.13405 | 0.019166 | -0.0085086 | 0.013349 | -0.0027172 | 0.0095703 | 1.7212 | 1.7899 | 1.6663 | 1.7807 | 1.9318 | 1.6891 | 1.5289 | 36.763 | 36.9003 | 36.8454 | 36.795 | 36.7264 | 8.7845 | 8.6746 | 88.1195 | 87.9593 | -34.8358 | 88.2202 | 88.2111 | 0.25177 | -35.0464 | 95.2148 | 95.105 | 0.027466 | 123.1934 | 123.2758 | 28.1708 | -0.041199 | 88.3621 | 88.1516 | 88.0966 | -35.2386 | 123.2254 | 123.1567 | 123.3307 | -28.093
2326.5156 | 123.3902 | -86.4716 | 36.8088 | -0.23193 | 0.01139 | 0.0030719 | 0.012181 | -0.018057 | -1.505e-05 | -0.0027877 | -0.080643 | 0.018525 | -0.0087222 | 0.013349 | -0.0050672 | 0.012134 | 1.7166 | 1.7761 | 1.6434 | 1.7487 | 1.9272 | 1.6891 | 1.5289 | 36.6989 | 36.8042 | 36.7722 | 36.763 | 36.6989 | 8.7845 | 8.6838 | 88.1607 | 88.0005 | -34.8816 | 88.2477 | 88.2202 | 0.21973 | -35.0922 | 95.256 | 95.1553 | -0.045777 | 123.1705 | 123.2437 | 28.0884 | -0.10986 | 88.3987 | 88.1882 | 88.1149 | -35.2798 | 123.2346 | 123.1705 | 123.2758 | -28.125
2327.5156 | 123.3627 | -86.5082 | 36.7401 | -0.10223 | 0.016517 | 0.0067035 | 0.015599 | -0.019126 | 0.001694 | 0.0023391 | -0.18745 | 0.020021 | -0.010645 | 0.013563 | -0.0048534 | 0.010425 | 1.7212 | 1.7578 | 1.6342 | 1.7578 | 1.9318 | 1.6983 | 1.506 | 36.6852 | 36.795 | 36.7767 | 36.7538 | 36.6806 | 8.7799 | 8.6838 | 88.2065 | 88.0142 | -34.8083 | 88.266 | 88.266 | 0.25177 | -35.0189 | 95.2881 | 95.192 | 0.013733 | 123.1934 | 123.2849 | 28.093 | -0.059509 | 88.4399 | 88.2294 | 88.1424 | -35.2341 | 123.262 | 123.1888 | 123.3032 | -28.0563
2328.5156 | 123.3673 | -86.5494 | 36.6943 | -0.19379 | 0.0083997 | 0.0026447 | 0.013249 | -0.022544 | -0.0017238 | -0.00022432 | -0.11116 | 0.019166 | -0.011499 | 0.012281 | -0.003999 | 0.011707 | 1.7532 | 1.8585 | 1.7258 | 1.799 | 1.918 | 1.712 | 1.5472 | 36.6806 | 36.7996 | 36.7584 | 36.676 | 36.6165 | 8.7753 | 8.6792 | 88.2614 | 88.0966 | -34.7763 | 88.4079 | 88.3484 | 0.25177 | -34.9411 | 95.3247 | 95.2286 | -0.018311 | 123.23 | 123.3078 | 28.0792 | -0.07782 | 88.4674 | 88.3026 | 88.2751 | -35.1471 | 123.2254 | 123.1659 | 123.349 | -28.0151
2329.5156 | 123.3353 | -86.5402 | 36.6943 | -0.46844 | 0.014168 | 0.0034991 | 0.014317 | -0.01763 | 0.00083955 | 0.0029801 | -0.15694 | 0.018312 | -0.011927 | 0.012708 | -0.0050672 | 0.010638 | 1.6891 | 1.7532 | 1.6434 | 1.7532 | 1.9455 | 1.6983 | 1.5152 | 36.6394 | 36.731 | 36.7218 | 36.7081 | 36.6394 | 8.7845 | 8.6838 | 88.2385 | 88.0554 | -34.7488 | 88.2935 | 88.2935 | 0.23804 | -35.0052 | 95.3247 | 95.224 | 0.013733 | 123.1796 | 123.262 | 28.038 | -0.054932 | 88.4857 | 88.2294 | 88.1836 | -35.1791 | 123.2483 | 123.1796 | 123.2712 | -28.0106
2330.5156 | 123.3627 | -86.554 | 36.6943 | -0.15564 | 0.013099 | 0.0037127 | 0.014744 | -0.018698 | 0.0010532 | 0.0029801 | -0.13405 | 0.020021 | -0.010431 | 0.014631 | -0.0029308 | 0.0095703 | 1.712 | 1.7532 | 1.6342 | 1.7395 | 1.9226 | 1.6846 | 1.506 | 36.6394 | 36.7401 | 36.7081 | 36.7218 | 36.6348 | 8.7891 | 8.6746 | 88.2385 | 88.06 | -34.7717 | 88.3072 | 88.2935 | 0.23346 | -34.9823 | 95.343 | 95.2286 | 0.027466 | 123.1934 | 123.262 | 28.0334 | -0.059509 | 88.4766 | 88.266 | 88.1882 | -35.1883 | 123.2758 | 123.1888 | 123.2941 | -28.0197
2331.5156 | 123.3673 | -86.5448 | 36.6669 | -0.21667 | 0.011818 | 0.0037127 | 0.011967 | -0.018698 | -0.0023648 | 0.0031937 | -0.11879 | 0.017884 | -0.013208 | 0.01399 | -0.0048534 | 0.010211 | 1.7487 | 1.8494 | 1.7212 | 1.8036 | 1.9043 | 1.6983 | 1.5335 | 36.6531 | 36.7813 | 36.7355 | 36.6714 | 36.5845 | 8.7845 | 8.6792 | 88.2431 | 88.0783 | -34.7626 | 88.3942 | 88.3484 | 0.27008 | -34.9182 | 95.3293 | 95.224 | 0.004578 | 123.1979 | 123.2803 | 28.0563 | -0.082397 | 88.4491 | 88.2935 | 88.266 | -35.1334 | 123.2162 | 123.1293 | 123.3261 | -27.9877
2332.5156 | 123.4085 | -86.5677 | 36.6119 | -0.16327 | 0.0096813 | 0.0045673 | 0.013035 | -0.019766 | -0.0012966 | 0.0023391 | -0.11116 | 0.01703 | -0.012567 | 0.011854 | -0.0035718 | 0.0099975 | 1.7532 | 1.8906 | 1.7532 | 1.8036 | 1.8814 | 1.7166 | 1.5335 | 36.6623 | 36.7813 | 36.7584 | 36.6394 | 36.5753 | 8.7845 | 8.6838 | 88.2843 | 88.1012 | -34.7305 | 88.4583 | 88.3713 | 0.27008 | -34.8587 | 95.3522 | 95.2515 | 0.027466 | 123.23 | 123.3261 | 28.0746 | -0.036621 | 88.4491 | 88.3209 | 88.3209 | -35.0784 | 123.2071 | 123.143 | 123.349 | -27.9282
2333.5156 | 123.3307 | -86.6455 | 36.6028 | -0.19379 | 0.0098951 | 0.0020037 | 0.013249 | -0.017844 | 0.00062595 | -0.00022432 | -0.40108 | 0.020234 | -0.0091494 | 0.014204 | -0.0052808 | 0.011493 | 1.6891 | 1.7303 | 1.6251 | 2.005 | 1.9501 | 1.6983 | 1.5289 | 36.525 | 36.6394 | 36.6394 | 36.6211 | 36.5387 | 8.7845 | 8.6792 | 88.3438 | 88.1744 | -34.6527 | 88.3759 | 88.6505 | 0.47607 | -34.9136 | 95.43 | 95.3247 | 0.018311 | 123.1705 | 123.2849 | 27.9602 | -0.064087 | 88.5956 | 88.3347 | 88.2706 | -35.0739 | 123.2666 | 123.1842 | 123.2849 | -27.9236
2334.5156 | 123.3673 | -86.6867 | 36.5707 | -0.086975 | 0.017586 | 0.0045673 | 0.014531 | -0.018057 | 0.004044 | 0.0029801 | -0.27138 | 0.017244 | -0.010858 | 0.013136 | -0.0035718 | 0.0091431 | 1.7303 | 1.7761 | 1.6571 | 1.7578 | 1.886 | 1.6617 | 1.5152 | 36.5753 | 36.6302 | 36.5891 | 36.5524 | 36.4792 | 8.7891 | 8.6884 | 88.3484 | 88.2019 | -34.6848 | 88.4628 | 88.4445 | 0.24261 | -34.8404 | 95.4758 | 95.3751 | -0.018311 | 123.262 | 123.2758 | 27.9007 | -0.091553 | 88.5727 | 88.4171 | 88.3438 | -35.0555 | 123.2391 | 123.1659 | 123.317 | -27.8824
2335.5156 | 123.3261 | -86.6959 | 36.5479 | -0.21667 | 0.010963 | 0.0037127 | 0.015172 | -0.018912 | -1.505e-05 | 0.0023391 | -0.073013 | 0.017457 | -0.012781 | 0.014845 | -0.0063488 | 0.013202 | 1.6891 | 1.767 | 1.6479 | 1.7258 | 1.9043 | 1.6708 | 1.4969 | 36.4883 | 36.6119 | 36.557 | 36.5433 | 36.4929 | 8.7891 | 8.6792 | 88.3667 | 88.1927 | -34.6436 | 88.4628 | 88.4216 | 0.22888 | -34.8587 | 95.4849 | 95.3751 | -0.004578 | 123.1842 | 123.2529 | 27.8778 | -0.054932 | 88.6002 | 88.385 | 88.3438 | -35.051 | 123.2391 | 123.1888 | 123.3078 | -27.8687
2336.5156 | 123.4863 | -86.6913 | 36.4746 | -0.079346 | 0.0075451 | 0.0039263 | 0.010472 | -0.022971 | -0.0057828 | 0.0014847 | -0.095902 | 0.017884 | -0.012995 | 0.013563 | -0.0086988 | 0.0078613 | 1.7715 | 1.9089 | 1.7532 | 1.8082 | 1.8723 | 1.6937 | 1.5244 | 36.676 | 36.2549 | 36.5707 | 36.4609 | 36.3785 | 8.7845 | 8.6838 | 88.385 | 88.2156 | -34.6024 | 88.6002 | 88.4995 | 0.28381 | -34.7031 | 95.4758 | 95.3751 | -0.013733 | 123.3673 | 123.262 | 27.887 | -0.09613 | 88.5635 | 88.4628 | 88.4445 | -34.9503 | 123.1522 | 123.0698 | 122.9462 | -27.7908
2337.5156 | 123.3994 | -86.6959 | 36.5204 | -0.23193 | 0.010322 | 0.0020037 | 0.01389 | -0.01763 | -0.0023648 | 0.0021255 | -0.13405 | 0.017884 | -0.013636 | 0.015272 | -0.0046398 | 0.0085021 | 1.7441 | 1.8494 | 1.7258 | 1.7807 | 1.8906 | 1.6891 | 1.5289 | 36.5067 | 36.6348 | 36.5662 | 36.4929 | 36.4197 | 8.7845 | 8.6884 | 88.385 | 88.2248 | -34.6298 | 88.5452 | 88.4766 | 0.25177 | -34.7763 | 95.4803 | 95.3842 | -0.027466 | 123.2025 | 123.262 | 27.8778 | -0.10071 | 88.5864 | 88.4399 | 88.4216 | -34.9915 | 123.1888 | 123.1155 | 123.3307 | -27.832
2338.5156 | 123.4451 | -86.7371 | 36.4563 | 0.035095 | 0.0079723 | 0.0054217 | 0.014317 | -0.018485 | -0.0038602 | 0.0014847 | 0.079574 | 0.017457 | -0.01214 | 0.013136 | -0.003999 | 0.012347 | 1.7029 | 1.7899 | 1.68 | 1.7578 | 1.8723 | 1.6983 | 1.506 | 36.5021 | 36.5982 | 36.5891 | 36.4563 | 36.3602 | 8.7799 | 8.6838 | 88.4354 | 88.2431 | -34.584 | 88.5269 | 88.4949 | 0.25177 | -34.7534 | 95.517 | 95.4208 | 0 | 123.2391 | 123.3261 | 27.9053 | -0.096131 | 88.6093 | 88.4399 | 88.4171 | -34.9503 | 123.1934 | 123.0972 | 123.3353 | -27.7725
2339.5156 | 123.4406 | -86.7508 | 36.4243 | -0.33875 | 0.010322 | 0.0015765 | 0.012608 | -0.019126 | -0.00065585 | -0.00022432 | -0.088272 | 0.017671 | -0.013208 | 0.012068 | -0.0044262 | 0.0099975 | 1.7761 | 1.8494 | 1.7303 | 1.7761 | 1.8677 | 1.6846 | 1.5198 | 36.4975 | 36.6257 | 36.5799 | 36.4151 | 36.3327 | 8.7799 | 8.6884 | 88.4354 | 88.2706 | -34.5566 | 88.6002 | 88.5269 | 0.25635 | -34.6481 | 95.5307 | 95.4391 | -0.009155 | 123.2483 | 123.3307 | 27.8915 | -0.091552 | 88.6185 | 88.5269 | 88.4811 | -34.9045 | 123.1659 | 123.0835 | 123.3765 | -27.7359
2340.5156 | 123.4726 | -86.7691 | 36.4105 | -0.094604 | 0.0088269 | 0.0028583 | 0.010899 | -0.020407 | -0.001083 | 0.00084388 | 0.026169 | 0.017884 | -0.012781 | 0.014845 | -0.0027172 | 0.010852 | 1.7853 | 1.8677 | 1.7395 | 1.7944 | 1.8677 | 1.6937 | 1.5335 | 36.5112 | 36.6074 | 36.5799 | 36.4014 | 36.3007 | 8.7799 | 8.6792 | 88.4628 | 88.3026 | -34.5428 | 88.6368 | 88.5635 | 0.26093 | -34.6252 | 95.549 | 95.4483 | -0.009155 | 123.2803 | 123.349 | 27.9007 | -0.10986 | 88.6368 | 88.5544 | 88.5086 | -34.877 | 123.1705 | 123.0698 | 123.3765 | -27.7313
2341.5156 | 123.4406 | -86.7691 | 36.4105 | -0.1709 | 0.0083997 | 0.0043537 | 0.010685 | -0.018057 | 0.00019875 | 0.0012711 | -0.14931 | 0.016176 | -0.013208 | 0.010359 | -0.0042126 | 0.010638 | 1.7715 | 1.8539 | 1.7349 | 1.7853 | 1.8539 | 1.6983 | 1.5244 | 36.4929 | 36.6211 | 36.557 | 36.438 | 36.319 | 8.7845 | 8.6884 | 88.4674 | 88.2935 | -34.5566 | 88.623 | 88.5544 | 0.26092 | -34.639 | 95.5536 | 95.4575 | 0.027466 | 123.262 | 123.3261 | 27.8687 | -0.091552 | 88.623 | 88.5406 | 88.504 | -34.8862 | 123.2071 | 123.0881 | 123.3902 | -27.7222
2342.5156 | 123.4497 | -86.7737 | 36.3464 | 0.027466 | 0.0086133 | 0.0054217 | 0.011754 | -0.015921 | -0.0019376 | 0.00020288 | -0.011978 | 0.016816 | -0.013208 | 0.013777 | -0.0050672 | 0.010211 | 1.7349 | 1.8219 | 1.6937 | 1.767 | 1.8814 | 1.6891 | 1.5244 | 36.4609 | 36.5479 | 36.5295 | 36.3876 | 36.2778 | 8.7753 | 8.6838 | 88.4628 | 88.298 | -34.465 | 88.5956 | 88.5406 | 0.24262 | -34.6115 | 95.549 | 95.4575 | 0.041198 | 123.2346 | 123.3032 | 27.8458 | -0.068665 | 88.6551 | 88.5086 | 88.4674 | -34.8221 | 123.1613 | 123.0515 | 123.3215 | -27.6627
2343.5156 | 123.468 | -86.8423 | 36.3098 | -0.10986 | 0.0081861 | 0.0043537 | 0.010045 | -0.021262 | 0.00041235 | 0.0021255 | 0.23979 | 0.015748 | -0.013849 | 0.012708 | -0.0042126 | 0.011066 | 1.7899 | 1.8768 | 1.7303 | 1.7715 | 1.8402 | 1.6663 | 1.506 | 36.438 | 36.4838 | 36.4929 | 36.3281 | 36.2366 | 8.7799 | 8.6838 | 88.5086 | 88.3484 | -34.4696 | 88.7192 | 88.6139 | 0.2655 | -34.52 | 95.6223 | 95.5261 | 0.018311 | 123.2803 | 123.3353 | 27.8091 | -0.073242 | 88.6826 | 88.6322 | 88.5727 | -34.8038 | 123.1705 | 123.0789 | 123.3261 | -27.626
2344.5156 | 123.4085 | -86.8515 | 36.319 | 0.17242 | 0.010109 | 0.0022175 | 0.011967 | -0.020835 | -0.0012966 | -0.00065152 | 0.15587 | 0.018312 | -0.011286 | 0.014845 | -0.0031446 | 0.011066 | 1.7303 | 1.799 | 1.6891 | 1.7441 | 1.8677 | 1.6754 | 1.5289 | 36.3693 | 36.4288 | 36.4243 | 36.2915 | 36.2228 | 8.7799 | 8.6792 | 88.5269 | 88.3804 | -34.4513 | 88.6505 | 88.5956 | 0.21515 | -34.5886 | 95.6314 | 95.5307 | -0.027466 | 123.2208 | 123.2758 | 27.7451 | -0.096131 | 88.7192 | 88.5818 | 88.5406 | -34.79 | 123.143 | 123.0743 | 123.2803 | -27.6398
2345.5156 | 123.4818 | -86.8698 | 36.2732 | -0.12512 | 0.0092541 | 0.0024311 | 0.011754 | -0.017417 | -1.505e-05 | 0.0042619 | 0.11772 | 0.016389 | -0.013208 | 0.011427 | -0.0042126 | 0.0099975 | 1.6159 | 1.8173 | 1.7487 | 1.8036 | 1.8311 | 1.6479 | 1.5015 | 36.3785 | 36.4883 | 36.4655 | 36.2686 | 36.1954 | 8.7799 | 8.6838 | 88.5178 | 88.3713 | -34.4421 | 88.6871 | 88.6734 | 0.30212 | -34.6573 | 95.6497 | 95.5536 | -0.004577 | 123.2483 | 123.3353 | 27.7817 | -0.077819 | 88.7009 | 88.4857 | 88.6185 | -34.7717 | 123.1384 | 123.0652 | 123.3582 | -27.5894
2346.5156 | 123.4589 | -86.9293 | 36.2503 | -0.033569 | 0.0083997 | 0.0028583 | 0.012394 | -0.018698 | -0.0012966 | 0.0027665 | -0.027237 | 0.017457 | -0.014063 | 0.01164 | -0.0042126 | 0.0099975 | 1.7624 | 1.8402 | 1.7029 | 1.7807 | 1.8906 | 1.6846 | 1.5244 | 36.3464 | 36.4334 | 36.4014 | 36.2183 | 36.1542 | 8.7845 | 8.6838 | 88.6139 | 88.4537 | -34.3597 | 88.7695 | 88.71 | 0.25635 | -34.4879 | 95.7138 | 95.6131 | -0.032043 | 123.2758 | 123.3307 | 27.7176 | -0.09613 | 88.8199 | 88.6917 | 88.6322 | -34.726 | 123.1476 | 123.0835 | 123.3627 | -27.5665
2347.5156 | 123.4955 | -86.9202 | 36.2366 | -0.02594 | 0.0079723 | 0.0032855 | 0.011967 | -0.018485 | -0.001083 | 0.0025529 | -0.050125 | 0.017244 | -0.012781 | 0.012922 | -0.0025036 | 0.0085021 | 1.7899 | 1.8631 | 1.7395 | 1.7715 | 1.8402 | 1.6937 | 1.5244 | 36.3739 | 36.4655 | 36.4151 | 36.2457 | 36.145 | 8.7845 | 8.6884 | 88.6139 | 88.4445 | -34.3964 | 88.7833 | 88.6917 | 0.24719 | -34.4467 | 95.7047 | 95.6085 | 0.009156 | 123.2941 | 123.3353 | 27.7267 | -0.091552 | 88.7604 | 88.71 | 88.6597 | -34.7122 | 123.1659 | 123.0652 | 123.3856 | -27.5482
2348.5156 | 123.4085 | -86.9705 | 36.2 | 0.15717 | 0.010322 | 0.0028583 | 0.012822 | -0.018485 | 0.0012668 | -1.0724e-05 | 0.087204 | 0.017671 | -0.012781 | 0.012922 | -0.0046398 | 0.012775 | 1.6846 | 1.767 | 1.6434 | 1.7075 | 1.8265 | 1.6388 | 1.4832 | 36.1725 | 36.3876 | 36.2915 | 36.2274 | 36.113 | 8.7845 | 8.6746 | 88.6093 | 88.4537 | -34.3735 | 88.7375 | 88.678 | 0.2243 | -34.5154 | 95.755 | 95.6451 | 0.027466 | 123.143 | 123.262 | 27.6169 | -0.086975 | 88.797 | 88.6551 | 88.6139 | -34.7168 | 123.1979 | 123.0835 | 123.3582 | -27.5253
2349.5156 | 123.5092 | -86.9888 | 36.1496 | -0.10986 | 0.0075451 | 0.0022175 | 0.012181 | -0.01998 | -0.0021512 | 0.0023391 | -0.12642 | 0.018312 | -0.015131 | 0.012281 | -0.0035718 | 0.010638 | 1.7807 | 1.8539 | 1.7075 | 1.767 | 1.799 | 1.6617 | 1.4877 | 36.2915 | 36.4151 | 36.4151 | 36.2 | 36.1038 | 8.7799 | 8.6838 | 88.6505 | 88.4766 | -34.3506 | 88.8428 | 88.7558 | 0.27924 | -34.3689 | 95.7687 | 95.6726 | 0.050354 | 123.2803 | 123.4039 | 27.7313 | -0.045776 | 88.7878 | 88.7695 | 88.6963 | -34.6619 | 123.1888 | 123.0927 | 123.4039 | -27.4658
2350.5156 | 123.4177 | -87.0392 | 36.145 | 0.15717 | 0.0098951 | 0.0049945 | 0.014958 | -0.01998 | 0.00083955 | 0.0016983 | 0.14824 | 0.017244 | -0.01214 | 0.011427 | -0.0029308 | 0.011707 | 1.7258 | 1.7807 | 1.6663 | 1.7075 | 1.8311 | 1.6434 | 1.4923 | 36.2228 | 36.264 | 36.2549 | 36.1496 | 36.0306 | 8.7799 | 8.6792 | 88.6826 | 88.5315 | -34.314 | 88.8199 | 88.7466 | 0.21515 | -34.4193 | 95.8191 | 95.7184 | 0.004577 | 123.262 | 123.2941 | 27.5757 | -0.11444 | 88.8702 | 88.765 | 88.7054 | -34.6527 | 123.1888 | 123.0698 | 123.3032 | -27.4658
2351.5156 | 123.3627 | -87.0895 | 36.1313 | -0.10223 | 0.014595 | 0.0020037 | 0.014531 | -0.018271 | 0.0038304 | 0.0025529 | -0.23323 | 0.021089 | -0.011499 | 0.012068 | -0.0029308 | 0.0074341 | 1.6937 | 1.68 | 1.561 | 1.7029 | 1.8677 | 1.5976 | 1.4374 | 36.1176 | 36.2 | 36.1588 | 36.1679 | 36.0718 | 8.7845 | 8.6792 | 88.6871 | 88.5269 | -34.2636 | 88.7695 | 88.7924 | 0.2655 | -34.4376 | 95.874 | 95.7687 | 0.036621 | 123.2071 | 123.2483 | 27.4796 | -0.05951 | 88.9572 | 88.7833 | 88.6505 | -34.6939 | 123.2574 | 123.1613 | 123.2895 | -27.4521
2352.5156 | 123.3994 | -87.1078 | 36.0809 | 0.15717 | 0.0094677 | 0.0028583 | 0.010685 | -0.020194 | -0.0017238 | 0.0036209 | 0.17113 | 0.018739 | -0.014704 | 0.014204 | -0.00229 | 0.013843 | 1.6891 | 1.7624 | 1.6388 | 1.7029 | 1.8311 | 1.6388 | 1.4832 | 36.1359 | 36.2183 | 36.2045 | 36.0901 | 35.9985 | 8.7891 | 8.6746 | 88.7466 | 88.591 | -34.2499 | 88.8702 | 88.8107 | 0.21973 | -34.3918 | 95.8969 | 95.7825 | 0.009155 | 123.2437 | 123.3124 | 27.5299 | -0.082398 | 88.9389 | 88.797 | 88.7466 | -34.5978 | 123.1979 | 123.1064 | 123.3261 | -27.4063
2353.5156 | 123.4497 | -87.1124 | 36.0397 | 0.012207 | 0.0079723 | 0.0028583 | 0.01154 | -0.020621 | -0.0038602 | 0.0046891 | 0.018539 | 0.017457 | -0.012781 | 0.011213 | -0.0033582 | 0.0097839 | 1.6937 | 1.767 | 1.6525 | 1.7258 | 1.8494 | 1.6525 | 1.474 | 36.1359 | 36.2228 | 36.2 | 36.0672 | 35.9848 | 8.7845 | 8.6792 | 88.765 | 88.5864 | -34.1904 | 88.8794 | 88.8382 | 0.25177 | -34.346 | 95.8969 | 95.7916 | 0.027466 | 123.2483 | 123.3124 | 27.5208 | -0.054932 | 88.9618 | 88.8062 | 88.765 | -34.5657 | 123.1796 | 123.0972 | 123.3353 | -27.3605
2354.5156 | 123.4131 | -87.1399 | 36.0168 | 0.18005 | 0.013313 | 0.0026447 | 0.014744 | -0.020194 | 0.0012668 | 0.0027665 | 0.17113 | 0.018098 | -0.011072 | 0.012495 | -0.003999 | 0.011066 | 1.7303 | 1.7944 | 1.6663 | 1.7166 | 1.8036 | 1.6434 | 1.4603 | 36.1084 | 36.1633 | 36.1633 | 36.0352 | 35.9573 | 8.7845 | 8.6838 | 88.7833 | 88.6002 | -34.2133 | 88.9343 | 88.8565 | 0.25635 | -34.2865 | 95.9244 | 95.8237 | 0.01831 | 123.2483 | 123.3032 | 27.4796 | -0.05951 | 88.9435 | 88.8702 | 88.8062 | -34.5566 | 123.175 | 123.0972 | 123.3032 | -27.3331
2355.5156 | 123.4177 | -87.1765 | 36.0214 | -0.80414 | 0.0090405 | 0.0041401 | 0.011326 | -0.018912 | 0.0014804 | 0.0019119 | 0.018539 | 0.017671 | -0.011499 | 0.014845 | -0.0035718 | 0.010425 | 1.7029 | 1.6983 | 1.6022 | 1.68 | 1.7807 | 1.5976 | 1.4282 | 36.0764 | 36.1679 | 36.1679 | 36.0443 | 35.9528 | 8.7936 | 8.6792 | 88.7741 | 88.6047 | -34.2407 | 88.8748 | 88.8565 | 0.25177 | -34.3185 | 95.9702 | 95.8557 | 0.022889 | 123.2529 | 123.3444 | 27.4887 | -0.068664 | 88.9572 | 88.8794 | 88.7787 | -34.5932 | 123.2208 | 123.1293 | 123.3444 | -27.3422
2356.5156 | 123.3353 | -87.1857 | 36.058 | -0.17853 | 0.010109 | 0.0039263 | 0.014744 | -0.020194 | 0.0021214 | 0.00063028 | -0.14168 | 0.019807 | -0.013636 | 0.013777 | -0.0033582 | 0.011279 | 1.6846 | 1.7029 | 1.593 | 1.6708 | 1.8448 | 1.5976 | 1.4465 | 36.0489 | 36.1313 | 36.0855 | 36.0809 | 35.9848 | 8.7891 | 8.6838 | 88.7833 | 88.6322 | -34.2133 | 88.8886 | 88.8565 | 0.2243 | -34.3735 | 95.9747 | 95.8694 | 0.022889 | 123.2346 | 123.2712 | 27.4017 | -0.073242 | 89.0305 | 88.8702 | 88.7787 | -34.6115 | 123.2666 | 123.1705 | 123.317 | -27.3743
2357.5156 | 123.4451 | -87.1811 | 35.9573 | 0.16479 | 0.01075 | 0.0047809 | 0.011113 | -0.022544 | -1.505e-05 | 0.0010575 | 0.1635 | 0.01703 | -0.014276 | 0.011427 | -0.0014356 | 0.012134 | 1.6754 | 1.7349 | 1.6434 | 1.6937 | 1.8219 | 1.6571 | 1.4786 | 36.0443 | 36.1221 | 36.1404 | 36.0123 | 35.9253 | 8.7891 | 8.6838 | 88.8382 | 88.6597 | -34.1354 | 88.916 | 88.8748 | 0.21515 | -34.2819 | 95.9702 | 95.8649 | 0.054932 | 123.2254 | 123.3215 | 27.4567 | -0.032043 | 89.003 | 88.8565 | 88.8245 | -34.4788 | 123.1934 | 123.1064 | 123.3032 | -27.2736
2358.5156 | 123.4177 | -87.1536 | 35.9802 | 0.23346 | 0.016731 | 0.00093569 | 0.01389 | -0.018057 | 0.005112 | 0.0016983 | 0.11772 | 0.020662 | -0.012995 | 0.015486 | -0.0012218 | 0.010852 | 1.6937 | 1.7029 | 1.5884 | 1.6891 | 1.8356 | 1.6113 | 1.4557 | 36.0672 | 36.1313 | 36.1267 | 35.9985 | 35.9207 | 8.7799 | 8.67 | 88.765 | 88.6093 | -34.1446 | 88.8565 | 88.8428 | 0.23346 | -34.2865 | 95.9335 | 95.8237 | 0.01831 | 123.2208 | 123.2803 | 27.4567 | -0.05951 | 88.9893 | 88.8474 | 88.7421 | -34.5245 | 123.1522 | 123.0743 | 123.2849 | -27.3102
2359.5156 | 123.4222 | -87.1994 | 35.9711 | 0.14954 | 0.0088269 | 0.0045673 | 0.011754 | -0.021475 | -0.00065585 | 0.0034073 | 0.10246 | 0.019807 | -0.014917 | 0.012495 | -0.00229 | 0.0095703 | 1.6754 | 1.7258 | 1.6342 | 1.7075 | 1.8127 | 1.6251 | 1.4786 | 36.0397 | 36.1954 | 36.0214 | 35.9573 | 35.8978 | 8.7753 | 8.67 | 88.8245 | 88.678 | -34.1583 | 88.9252 | 88.9069 | 0.22888 | -34.2957 | 95.9747 | 95.8694 | -0.013733 | 123.2391 | 123.2208 | 27.3514 | -0.073242 | 89.0121 | 88.8748 | 88.8336 | -34.4925 | 123.1567 | 123.0972 | 123.3948 | -27.301
2360.5156 | 123.4589 | -87.1994 | 35.9573 | 0.21057 | 0.015663 | 0.0015765 | 0.013035 | -0.01998 | 0.0014804 | 0.0016983 | -0.12642 | 0.019593 | -0.010858 | 0.01164 | -0.00229 | 0.0076477 | 1.7532 | 1.593 | 1.3779 | 1.6388 | 1.7532 | 1.6159 | 1.4282 | 36.0626 | 36.0992 | 36.0992 | 35.9528 | 35.8612 | 8.7845 | 8.6838 | 88.8153 | 88.6276 | -34.2041 | 88.7924 | 88.8382 | 0.21057 | -34.2041 | 95.9839 | 95.8832 | -0.004577 | 123.262 | 123.2986 | 27.4155 | -0.09613 | 88.9526 | 88.9526 | 88.5773 | -34.5291 | 123.1522 | 123.0606 | 123.2986 | -27.2736
2361.5312 | 123.3719 | -87.2864 | 35.9528 | -0.10223 | 0.015663 | 0.0013629 | 0.015599 | -0.016349 | 0.0053256 | 0.0038345 | -0.17983 | 0.020021 | -0.0087222 | 0.013136 | -0.0014356 | 0.0082885 | 1.7075 | 1.6891 | 1.5976 | 1.7212 | 1.8402 | 1.6067 | 1.442 | 35.9894 | 36.0626 | 36.0077 | 35.9848 | 35.8841 | 8.7799 | 8.6746 | 88.8931 | 88.7283 | -34.1125 | 88.9755 | 89.0076 | 0.27923 | -34.2453 | 96.0663 | 95.961 | 0.032043 | 123.2758 | 123.2941 | 27.3331 | -0.068665 | 89.1266 | 88.9938 | 88.884 | -34.5108 | 123.2712 | 123.1705 | 123.349 | -27.2781
2362.5156 | 123.4314 | -87.3367 | 35.8383 | 0.24872 | 0.015877 | 0.0022175 | 0.013463 | -0.020194 | 0.0021214 | 0.0051163 | 0.18639 | 0.018312 | -0.010431 | 0.012281 | -0.0016492 | 0.011707 | 1.6708 | 1.6846 | 1.5747 | 1.6846 | 1.8127 | 1.6067 | 1.442 | 35.9436 | 36.0077 | 35.9985 | 35.8749 | 35.7697 | 8.7845 | 8.6884 | 88.9435 | 88.7787 | -34.0256 | 89.0213 | 89.0213 | 0.24261 | -34.1675 | 96.1212 | 96.0251 | 0.036621 | 123.2803 | 123.3353 | 27.3102 | -0.068665 | 89.1495 | 89.0076 | 88.9114 | -34.3964 | 123.2117 | 123.1064 | 123.3444 | -27.15
2363.5156 | 123.436 | -87.355 | 35.8292 | 0.09613 | 0.01139 | -0.00013251 | 0.010685 | -0.019126 | -0.00065585 | 0.0031937 | 0.24742 | 0.017457 | -0.012781 | 0.01399 | -0.0042126 | 0.011279 | 1.7166 | 1.7624 | 1.6434 | 1.7258 | 1.7853 | 1.6205 | 1.442 | 35.9299 | 35.9985 | 35.9802 | 35.8063 | 35.7422 | 8.7891 | 8.6838 | 88.9755 | 88.797 | -34.0439 | 89.1174 | 89.0808 | 0.28381 | -34.1125 | 96.1441 | 96.0388 | -0.022889 | 123.2849 | 123.3353 | 27.2964 | -0.086976 | 89.1403 | 89.0717 | 88.9984 | -34.3872 | 123.1613 | 123.0972 | 123.3536 | -27.1454
2364.5156 | 123.3627 | -87.442 | 35.7742 | 0.09613 | 0.016517 | 0.0026447 | 0.013676 | -0.01763 | 0.0031894 | 0.0044755 | 0.17113 | 0.021516 | -0.012567 | 0.012495 | -0.00015383 | 0.011493 | 1.6479 | 1.6067 | 1.5244 | 1.6342 | 1.8311 | 1.5839 | 1.4053 | 35.788 | 35.8246 | 35.8292 | 35.8383 | 35.7422 | 8.7799 | 8.6884 | 89.0259 | 88.8474 | -33.9432 | 89.0488 | 89.0762 | 0.22888 | -34.1263 | 96.2219 | 96.1304 | 0.064087 | 123.23 | 123.2712 | 27.1408 | -0.032044 | 89.2731 | 89.09 | 88.9664 | -34.3689 | 123.2803 | 123.1842 | 123.2666 | -27.0859
2365.5156 | 123.4451 | -87.4329 | 35.7193 | 0.057983 | 0.011604 | 0.0037127 | 0.012181 | -0.020621 | -0.0021512 | 0.0031937 | 0.22453 | 0.019807 | -0.013208 | 0.012281 | -0.0037854 | 0.011279 | 1.7075 | 1.7487 | 1.6434 | 1.712 | 1.7899 | 1.6067 | 1.474 | 35.8383 | 35.9161 | 35.8795 | 35.7422 | 35.6415 | 8.7891 | 8.6838 | 89.0396 | 88.9069 | -33.9294 | 89.1815 | 89.1449 | 0.23804 | -34.0118 | 96.2219 | 96.1166 | 0.022888 | 123.2712 | 123.3124 | 27.1957 | -0.07782 | 89.2227 | 89.1403 | 89.0762 | -34.2453 | 123.175 | 123.0743 | 123.349 | -27.0355
2366.5156 | 123.4497 | -87.4283 | 35.733 | -0.0030518 | 0.0090405 | -0.033885 | 0.01154 | -0.022116 | -0.0034328 | 0.00020288 | 0.026169 | 0.019593 | -0.013208 | 0.012708 | -0.0029308 | 0.013202 | 1.6846 | 1.7395 | 1.6388 | 1.7075 | 1.8082 | 1.6159 | 1.4648 | 35.8429 | 35.9436 | 35.9344 | 35.7697 | 35.7101 | 8.7891 | 8.6838 | 89.0442 | 88.8931 | -33.9249 | 89.1678 | 89.1357 | 0.24261 | -34.0485 | 96.2173 | 96.1121 | 0.036621 | 123.2712 | 123.3627 | 27.2507 | -0.022888 | 89.2365 | 89.1129 | 89.0671 | -34.2682 | 123.1979 | 123.1384 | 123.3719 | -27.0493
2367.5156 | 123.4497 | -87.4924 | 35.6186 | 0.2182 | 0.015449 | 0.0020037 | 0.010899 | -0.01998 | 0.0029758 | 0.0029801 | 0.19402 | 0.020662 | -0.012567 | 0.01164 | -0.00058103 | 0.0095703 | 1.7303 | 1.6983 | 1.6159 | 1.7166 | 1.7853 | 1.6022 | 1.4557 | 35.8063 | 35.8704 | 35.8566 | 35.7101 | 35.6186 | 8.7799 | 8.6746 | 89.0945 | 88.9481 | -33.8333 | 89.1907 | 89.209 | 0.26093 | -33.8882 | 96.2723 | 96.167 | 0.091553 | 123.2986 | 123.349 | 27.182 | 0 | 89.2776 | 89.2227 | 89.1083 | -34.1629 | 123.2025 | 123.111 | 123.3627 | -26.944
2368.5156 | 123.3582 | -87.5336 | 35.6964 | 0.073242 | 0.019081 | 0.0028583 | 0.014103 | -0.019126 | 0.006821 | 0.0027665 | 0.15587 | 0.020875 | -0.011927 | 0.015486 | -0.0035718 | 0.0080749 | 1.6342 | 1.5656 | 1.5015 | 1.6296 | 1.8127 | 1.5656 | 1.4099 | 35.7925 | 35.6689 | 35.6689 | 35.7193 | 35.6644 | 8.7799 | 8.6838 | 89.0991 | 88.9435 | -33.8837 | 89.0991 | 89.1632 | 0.21973 | -34.0622 | 96.3135 | 96.2173 | 0.022888 | 123.3261 | 123.2025 | 26.9852 | -0.032043 | 89.3463 | 89.1678 | 89.035 | -34.2865 | 123.2529 | 123.1979 | 123.2025 | -27.0126
2369.5156 | 123.3856 | -87.5702 | 35.6735 | 0.18768 | 0.015663 | 0.00072209 | 0.012181 | -0.016135 | 0.0029758 | 0.0021255 | 0.20927 | 0.020021 | -0.010218 | 0.012708 | -0.0029308 | 0.011279 | 1.6251 | 1.6159 | 1.5198 | 1.6434 | 1.8265 | 1.5976 | 1.4145 | 35.6644 | 35.7101 | 35.7101 | 35.6552 | 35.5911 | 8.7799 | 8.6884 | 89.1678 | 88.9847 | -33.847 | 89.1861 | 89.2136 | 0.22888 | -34.0485 | 96.3501 | 96.2585 | -0.018311 | 123.2346 | 123.2803 | 27.0218 | -0.082398 | 89.3967 | 89.1953 | 89.09 | -34.259 | 123.2254 | 123.1613 | 123.2803 | -26.9852
2370.5156 | 123.3444 | -87.6251 | 35.6277 | 0.019836 | 0.017372 | 0.0037127 | 0.012608 | -0.020194 | 0.0042576 | 0.0038345 | 0.026169 | 0.022798 | -0.0097904 | 0.014204 | -0.0029308 | 0.0087157 | 1.6617 | 1.6251 | 1.5152 | 1.6388 | 1.799 | 1.5747 | 1.4191 | 35.6003 | 35.6781 | 35.6415 | 35.6461 | 35.582 | 8.7845 | 8.6884 | 89.1998 | 89.0442 | -33.8287 | 89.2502 | 89.2639 | 0.21973 | -33.9661 | 96.4096 | 96.3135 | 0.01831 | 123.2254 | 123.2666 | 26.9531 | -0.045777 | 89.4241 | 89.2868 | 89.1403 | -34.2087 | 123.2712 | 123.2071 | 123.3032 | -26.9394
2371.5156 | 123.3398 | -87.6526 | 35.5911 | 0.13428 | 0.021004 | 0.0037127 | 0.01389 | -0.018271 | 0.0083164 | 0.0042619 | -0.065384 | 0.018739 | -0.011713 | 0.013777 | -0.0027172 | 0.012134 | 1.4099 | 1.9501 | 1.6663 | 1.5976 | 1.8082 | 1.593 | 1.4236 | 35.5408 | 35.6049 | 35.5957 | 35.6003 | 35.5316 | 8.7845 | 8.6792 | 89.2456 | 89.0762 | -33.783 | 89.6027 | 89.2502 | 0.17395 | -34.1812 | 96.4371 | 96.3318 | 0.009156 | 123.1934 | 123.2483 | 26.9165 | -0.059509 | 89.4608 | 89.0625 | 89.3188 | -34.1675 | 123.2529 | 123.1842 | 123.2574 | -26.9119
2372.5156 | 123.3994 | -87.6755 | 35.5682 | -0.1709 | 0.016731 | 0.0024311 | 0.013249 | -0.019126 | 0.002335 | 0.0034073 | -0.050125 | 0.019593 | -0.008295 | 0.014845 | 5.9768e-05 | 0.011279 | 1.6479 | 1.6663 | 1.5564 | 1.6754 | 1.8036 | 1.5793 | 1.3779 | 35.5682 | 35.6735 | 35.614 | 35.5728 | 35.5042 | 8.7799 | 8.6792 | 89.2548 | 89.0533 | -33.7646 | 89.3417 | 89.3509 | 0.29755 | -33.9203 | 96.4554 | 96.3547 | 0.004578 | 123.2437 | 123.2895 | 26.9348 | -0.064087 | 89.4791 | 89.3234 | 89.2319 | -34.1904 | 123.2483 | 123.1796 | 123.349 | -26.889
2373.5156 | 123.317 | -87.7396 | 35.527 | 0.050354 | 0.017586 | -0.00013251 | 0.011754 | -0.018057 | -0.00022865 | 0.0036209 | 0.01091 | 0.019593 | -0.010645 | 0.014631 | -0.0020764 | 0.011279 | 1.5976 | 1.6205 | 1.5015 | 1.6113 | 1.7853 | 1.5564 | 1.3962 | 35.4492 | 35.5682 | 35.5225 | 35.5316 | 35.4492 | 8.7845 | 8.6746 | 89.296 | 89.1357 | -33.7418 | 89.36 | 89.3509 | 0.21515 | -33.9294 | 96.524 | 96.4142 | 0.004577 | 123.1888 | 123.262 | 26.8478 | -0.07782 | 89.5248 | 89.3372 | 89.241 | -34.1309 | 123.2712 | 123.1888 | 123.3078 | -26.8524
2374.5156 | 123.3765 | -87.735 | 35.5408 | -0.10223 | 0.020576 | -0.0016279 | 0.014317 | -0.018271 | 0.0019078 | 0.0040481 | -0.011978 | 0.018525 | -0.011072 | 0.012281 | -0.00058103 | 0.012134 | 1.68 | 1.6663 | 1.5747 | 1.6983 | 1.8585 | 1.6434 | 1.4557 | 35.5362 | 35.6369 | 35.5774 | 35.5545 | 35.4492 | 8.7799 | 8.6746 | 89.3784 | 89.1907 | -33.6822 | 89.4012 | 89.4333 | 0.24261 | -33.8608 | 96.5149 | 96.4096 | 0.013733 | 123.2712 | 123.3124 | 26.9028 | -0.091552 | 89.5935 | 89.415 | 89.3097 | -34.0851 | 123.2895 | 123.1842 | 123.3719 | -26.8661
2375.5156 | 123.3353 | -87.7579 | 35.4858 | 0.14191 | 0.019508 | 0.0039263 | 0.014103 | -0.019339 | 0.003403 | 0.0014847 | -0.25612 | 0.022798 | -0.008295 | 0.012495 | -0.0031446 | 0.011493 | 1.5656 | 1.5656 | 1.4877 | 1.6067 | 1.8173 | 1.5656 | 1.4282 | 35.4309 | 35.5591 | 35.5225 | 35.5316 | 35.4584 | 8.7753 | 8.67 | 89.3234 | 89.1861 | -33.6685 | 89.3234 | 89.3646 | 0.17853 | -33.9203 | 96.5332 | 96.4279 | 0.045776 | 123.1888 | 123.2803 | 26.8524 | -0.027466 | 89.5752 | 89.3234 | 89.2456 | -34.0576 | 123.2895 | 123.2162 | 123.317 | -26.8158
2376.5156 | 123.3948 | -87.7579 | 35.5133 | -0.12512 | 0.016517 | 0.0020037 | 0.014744 | -0.017203 | 0.0029758 | 0.0029801 | -0.1722 | 0.020448 | -0.011927 | 0.012708 | -0.0029308 | 0.011279 | 1.6251 | 1.6296 | 1.5472 | 1.6663 | 1.8173 | 1.561 | 1.3962 | 35.495 | 35.6003 | 35.5774 | 35.5133 | 35.4355 | 8.7799 | 8.6838 | 89.3188 | 89.1541 | -33.696 | 89.3875 | 89.4241 | 0.27008 | -33.8882 | 96.5378 | 96.4417 | 0 | 123.2529 | 123.3353 | 26.8936 | -0.07782 | 89.5752 | 89.3829 | 89.3051 | -34.1171 | 123.2712 | 123.1934 | 123.3582 | -26.8295
2377.5156 | 123.349 | -87.8174 | 35.4263 | 0.11902 | 0.01844 | 0.0030719 | 0.01389 | -0.016135 | 0.0025486 | 0.0031937 | 0.6823 | 0.021302 | -0.0089358 | 0.013777 | -0.0033582 | 0.011066 | 1.5884 | 1.5701 | 1.5015 | 1.6022 | 1.799 | 1.5884 | 1.4053 | 35.3989 | 35.4721 | 35.4446 | 35.4492 | 35.3897 | 8.7799 | 8.6838 | 89.4058 | 89.2227 | -33.6273 | 89.3875 | 89.4196 | 0.19684 | -33.8379 | 96.5973 | 96.5012 | 0.022888 | 123.2162 | 123.262 | 26.7609 | -0.036622 | 89.6164 | 89.4058 | 89.3188 | -34.021 | 123.2666 | 123.2071 | 123.2895 | -26.7426
2378.5156 | 123.3948 | -87.7945 | 35.408 | -0.11749 | 0.016517 | 0.0022175 | 0.012394 | -0.015921 | 0.001694 | 0.0029801 | -0.088272 | 0.020021 | -0.010858 | 0.013777 | -0.0029308 | 0.010852 | 1.6342 | 1.6388 | 1.5427 | 1.6479 | 1.799 | 1.5701 | 1.4236 | 35.4034 | 35.527 | 35.495 | 35.4584 | 35.3851 | 8.7799 | 8.6792 | 89.3646 | 89.2181 | -33.609 | 89.4333 | 89.4424 | 0.2243 | -33.7738 | 96.5744 | 96.4737 | 0.050354 | 123.1979 | 123.2895 | 26.8158 | -0.022888 | 89.5935 | 89.4287 | 89.3372 | -33.9844 | 123.2529 | 123.1796 | 123.3215 | -26.7288
2379.5156 | 123.3994 | -87.8632 | 35.3989 | -0.14801 | 0.017586 | 0.0049945 | 0.01389 | -0.019126 | 0.0010532 | 0.00020288 | -0.15694 | 0.020234 | -0.01214 | 0.014631 | -0.0031446 | 0.010425 | 1.6022 | 1.6205 | 1.5152 | 1.6479 | 1.7944 | 1.5656 | 1.3733 | 35.3439 | 35.4767 | 35.4355 | 35.3989 | 35.3348 | 8.7845 | 8.6838 | 89.4287 | 89.2364 | -33.6044 | 89.4836 | 89.5111 | 0.27466 | -33.7967 | 96.6476 | 96.5469 | 0 | 123.2071 | 123.2986 | 26.7517 | -0.064087 | 89.6576 | 89.4653 | 89.3784 | -34.0256 | 123.262 | 123.1979 | 123.3398 | -26.7151
2380.5156 | 123.3261 | -87.8815 | 35.376 | -0.20142 | 0.013313 | 0.0037127 | 0.01624 | -0.01464 | 0.0012668 | 0.0034073 | 0.041427 | 0.018098 | -0.012354 | 0.015058 | -0.0037854 | 0.012775 | 1.4282 | 1.6342 | 1.5335 | 1.6251 | 1.8585 | 1.5976 | 1.4236 | 35.2936 | 35.4126 | 35.3943 | 35.408 | 35.3348 | 8.7753 | 8.6792 | 89.4791 | 89.3051 | -33.5175 | 89.5157 | 89.5065 | 0.20142 | -33.9478 | 96.6568 | 96.5607 | 0.032043 | 123.175 | 123.2758 | 26.7151 | -0.041199 | 89.74 | 89.3097 | 89.415 | -33.9523 | 123.2895 | 123.2162 | 123.2941 | -26.6968
2381.5156 | 123.381 | -87.9318 | 35.3439 | -0.0030518 | 0.01844 | 0.0011493 | 0.015172 | -0.020407 | 0.002335 | 0.0029801 | -0.0043486 | 0.020021 | -0.011713 | 0.013563 | -0.0014356 | 0.0095703 | 1.6479 | 1.6708 | 1.5564 | 1.6479 | 1.799 | 1.5564 | 1.4236 | 35.321 | 35.4355 | 35.3897 | 35.3256 | 35.2615 | 8.7799 | 8.6792 | 89.4882 | 89.3555 | -33.5449 | 89.6027 | 89.5798 | 0.2243 | -33.696 | 96.7117 | 96.611 | -0.01831 | 123.2529 | 123.3215 | 26.7105 | -0.082397 | 89.7308 | 89.5798 | 89.4882 | -33.9203 | 123.2574 | 123.1934 | 123.3673 | -26.6647
2382.5156 | 123.349 | -87.9593 | 35.3119 | -1.9485 | 0.011818 | 0.0028583 | 0.012394 | -0.020621 | 0.00083955 | 0.00041648 | -0.095902 | 0.019593 | -0.011286 | 0.013136 | -0.006776 | 0.012775 | 1.5839 | 1.6067 | 1.5106 | 1.6296 | 1.8311 | 1.5793 | 1.4145 | 35.2249 | 35.3485 | 35.3394 | 35.321 | 35.2524 | 8.7799 | 8.6838 | 89.5386 | 89.3738 | -33.4808 | 89.566 | 89.5889 | 0.21515 | -33.728 | 96.7392 | 96.6431 | 0.009155 | 123.1842 | 123.2986 | 26.6556 | -0.05951 | 89.7903 | 89.5432 | 89.4699 | -33.8974 | 123.2803 | 123.2117 | 123.3078 | -26.6281
2383.5156 | 123.3948 | -87.9318 | 35.2844 | -0.033569 | 0.017158 | 0.0020037 | 0.015812 | -0.018271 | 0.0021214 | 0.0029801 | 0.32372 | 0.018312 | -0.010858 | 0.013136 | -0.0037854 | 0.010638 | 1.7166 | 1.8082 | 1.6251 | 1.7487 | 1.8311 | 1.6067 | 1.4603 | 35.2798 | 35.3897 | 35.3394 | 35.2982 | 35.2295 | 8.7845 | 8.6838 | 89.5386 | 89.3921 | -33.4534 | 89.74 | 89.6805 | 0.28839 | -33.5678 | 96.7163 | 96.6156 | 0.013733 | 123.2117 | 123.2712 | 26.6556 | -0.054932 | 89.7629 | 89.6484 | 89.5569 | -33.8242 | 123.23 | 123.1613 | 123.3215 | -26.6006
2384.5156 | 123.3353 | -88.0096 | 35.2295 | -0.1709 | 0.010963 | 0.0026447 | 0.013463 | -0.018698 | -0.002792 | 0.0016983 | -0.20271 | 0.019166 | -0.013422 | 0.012708 | -0.0063488 | 0.013202 | 1.593 | 1.6617 | 1.5472 | 1.6296 | 1.7899 | 1.5793 | 1.4145 | 35.1746 | 35.321 | 35.2844 | 35.2707 | 35.2295 | 8.7891 | 8.6884 | 89.5889 | 89.4241 | -33.4396 | 89.6713 | 89.6393 | 0.21515 | -33.6365 | 96.7987 | 96.698 | 0.041199 | 123.1842 | 123.2941 | 26.5961 | 0 | 89.7995 | 89.6027 | 89.5569 | -33.815 | 123.2803 | 123.2391 | 123.3307 | -26.5411
2385.5156 | 123.3582 | -88.0142 | 35.2341 | -0.14801 | 0.01374 | 0.0032855 | 0.015172 | -0.016989 | 0.0019078 | 0.0019119 | -0.10353 | 0.021302 | -0.0085086 | 0.013777 | -0.0033582 | 0.011707 | 1.5793 | 1.6067 | 1.506 | 1.6205 | 1.799 | 1.5472 | 1.3824 | 35.1517 | 35.2753 | 35.2661 | 35.2707 | 35.17 | 8.7799 | 8.6838 | 89.5615 | 89.3967 | -33.4351 | 89.621 | 89.6347 | 0.23804 | -33.6548 | 96.7941 | 96.698 | 0.036621 | 123.1659 | 123.2803 | 26.5823 | -0.064087 | 89.8132 | 89.5935 | 89.5203 | -33.8516 | 123.2849 | 123.1842 | 123.2895 | -26.5503
2386.5156 | 123.468 | -88.028 | 35.1517 | -0.17853 | 0.010536 | 0.0032855 | 0.01624 | -0.021475 | -1.505e-05 | 0.0019119 | -0.21034 | 0.015321 | -0.015345 | 0.012922 | -0.0061352 | 0.010852 | 1.6067 | 1.767 | 1.6159 | 1.6708 | 1.7624 | 1.5839 | 1.4191 | 35.2432 | 35.3989 | 35.3394 | 35.1379 | 35.1013 | 8.7799 | 8.6838 | 89.6118 | 89.447 | -33.3893 | 89.7949 | 89.6988 | 0.25177 | -33.5449 | 96.8079 | 96.7117 | -0.013733 | 123.2712 | 123.3673 | 26.6556 | -0.050354 | 89.7903 | 89.6347 | 89.6439 | -33.7326 | 123.1659 | 123.1293 | 123.4268 | -26.4679
2387.5156 | 123.3627 | -88.1287 | 35.17 | -0.20142 | 0.015663 | 0.0028583 | 0.015172 | -0.018485 | -1.505e-05 | 0.0012711 | -0.40108 | 0.019807 | -0.011499 | 0.014845 | -0.0052808 | 0.01192 | 1.5793 | 1.6251 | 1.4832 | 1.8906 | 1.8219 | 1.5656 | 1.4145 | 35.0647 | 35.1654 | 35.17 | 35.1746 | 35.0922 | 8.7845 | 8.6838 | 89.6942 | 89.5432 | -33.3481 | 89.7537 | 90.0192 | 0.47607 | -33.5907 | 96.9131 | 96.8124 | 0.004578 | 123.1934 | 123.2986 | 26.4862 | -0.07782 | 89.9506 | 89.7079 | 89.6118 | -33.7555 | 123.3032 | 123.2208 | 123.2941 | -26.4862
2388.5156 | 123.381 | -88.0646 | 35.1562 | -0.17853 | 0.0094677 | 0.0032855 | 0.011326 | -0.018698 | -0.0042874 | 0.0016983 | -0.14168 | 0.018953 | -0.011286 | 0.011213 | -0.0052808 | 0.010638 | 1.6479 | 1.7441 | 1.6022 | 1.6846 | 1.7624 | 1.5793 | 1.4145 | 35.1334 | 35.2798 | 35.2295 | 35.1379 | 35.0784 | 8.7753 | 8.6792 | 89.6439 | 89.4791 | -33.3939 | 89.8087 | 89.7491 | 0.27008 | -33.5083 | 96.8399 | 96.7438 | -0.018311 | 123.1979 | 123.2941 | 26.5503 | -0.07782 | 89.827 | 89.7125 | 89.6667 | -33.7418 | 123.2025 | 123.143 | 123.3444 | -26.4771
2389.5156 | 123.3765 | -88.1241 | 35.1288 | -0.16327 | 0.015663 | 0.0034991 | 0.013035 | -0.020194 | 0.0027622 | 0.00020288 | -0.21034 | 0.019166 | -0.012354 | 0.012495 | -0.0033582 | 0.011066 | 1.5839 | 1.6113 | 1.5106 | 1.6159 | 1.7853 | 1.5472 | 1.3824 | 35.0601 | 35.1791 | 35.1334 | 35.1334 | 35.0693 | 8.7845 | 8.6746 | 89.6713 | 89.5065 | -33.3435 | 89.7354 | 89.74 | 0.23346 | -33.5449 | 96.9086 | 96.7987 | 0.004578 | 123.1842 | 123.2574 | 26.4587 | -0.059509 | 89.9094 | 89.7079 | 89.6347 | -33.7463 | 123.2574 | 123.1934 | 123.3032 | -26.4542
2390.5156 | 123.4406 | -88.1058 | 35.0647 | -1.3229 | 0.0086133 | 0.0024311 | 0.014103 | -0.020621 | -0.0023648 | 0.00020288 | -0.073013 | 0.016176 | -0.01214 | 0.012922 | -0.0033582 | 0.011707 | 1.6205 | 1.7899 | 1.6479 | 1.6846 | 1.7441 | 1.5747 | 1.4236 | 35.1425 | 35.2753 | 35.2524 | 35.0693 | 35.0281 | 8.7799 | 8.6838 | 89.6805 | 89.5294 | -33.3206 | 89.8956 | 89.7903 | 0.26092 | -33.4442 | 96.8857 | 96.7896 | 0.004578 | 123.2483 | 123.3582 | 26.5686 | -0.036621 | 89.8499 | 89.7263 | 89.7537 | -33.6411 | 123.175 | 123.1338 | 123.381 | -26.3809
2391.5156 | 123.3261 | -88.2019 | 35.0555 | -0.1709 | 0.014808 | 0.0026447 | 0.016453 | -0.020194 | 0.0010532 | 0.0019119 | -0.034867 | 0.018525 | -0.0097904 | 0.012281 | -0.0029308 | 0.010211 | 1.5015 | 1.6022 | 1.5152 | 1.6205 | 1.8539 | 1.5793 | 1.4099 | 34.9915 | 35.0784 | 35.0601 | 35.0555 | 34.9915 | 8.7799 | 8.6792 | 89.7812 | 89.6118 | -33.2016 | 89.8041 | 89.8224 | 0.21057 | -33.5541 | 96.9818 | 96.8811 | 0 | 123.1934 | 123.262 | 26.3809 | -0.064087 | 90.0558 | 89.7034 | 89.7171 | -33.6456 | 123.2574 | 123.1934 | 123.2803 | -26.3763
2392.5156 | 123.4497 | -88.1927 | 35.0098 | -0.02594 | 0.0090405 | 0.0039263 | 0.011967 | -0.022971 | -0.0034328 | 0.00084388 | 0.0032804 | 0.018098 | -0.013849 | 0.010572 | -0.005708 | 0.010638 | 1.6708 | 1.7715 | 1.6342 | 1.6754 | 1.7578 | 1.5839 | 1.4191 | 35.0967 | 35.2158 | 35.1929 | 34.9823 | 34.9182 | 8.7845 | 8.6838 | 89.7766 | 89.6118 | -33.252 | 89.9643 | 89.8682 | 0.25635 | -33.3389 | 96.9772 | 96.8765 | -0.027466 | 123.2895 | 123.3856 | 26.5091 | -0.091553 | 89.9506 | 89.8636 | 89.827 | -33.5907 | 123.175 | 123.111 | 123.4085 | -26.326
2393.5156 | 123.4818 | -88.2019 | 34.9503 | -0.10986 | 0.0062635 | 0.0047809 | 0.013463 | -0.019766 | -0.00065585 | 0.0019119 | 0.17876 | 0.017244 | -0.010645 | 0.013777 | -0.0042126 | 0.010638 | 1.68 | 1.7578 | 1.6388 | 1.6983 | 1.7624 | 1.5747 | 1.4053 | 35.0601 | 35.1242 | 35.1334 | 34.9548 | 34.8816 | 8.7799 | 8.6838 | 89.7766 | 89.6072 | -33.1879 | 89.9597 | 89.9002 | 0.29297 | -33.2703 | 96.9818 | 96.8857 | 0.004578 | 123.262 | 123.3353 | 26.4496 | -0.068664 | 89.9643 | 89.8819 | 89.8407 | -33.5449 | 123.1567 | 123.0835 | 123.3261 | -26.2665
2394.5156 | 123.3856 | -88.2751 | 34.9503 | -0.15564 | 0.01609 | 0.0028583 | 0.016026 | -0.018271 | 0.0059666 | 0.0021255 | -0.21034 | 0.021089 | -0.0087222 | 0.01399 | -0.0031446 | 0.0072205 | 1.6022 | 1.6159 | 1.5106 | 1.6205 | 1.7853 | 1.5427 | 1.3733 | 34.9548 | 35.051 | 35.0143 | 34.9731 | 34.877 | 8.7936 | 8.6792 | 89.8178 | 89.6484 | -33.165 | 89.8911 | 89.8956 | 0.24719 | -33.3481 | 97.0688 | 96.9543 | 0.022889 | 123.23 | 123.2895 | 26.3351 | -0.073242 | 90.0604 | 89.8773 | 89.7858 | -33.577 | 123.2483 | 123.1522 | 123.3261 | -26.2711
2395.5156 | 123.349 | -88.2843 | 34.9503 | -0.19379 | 0.011177 | 0.0034991 | 0.011754 | -0.014853 | -0.00065585 | 0.00041648 | -0.12642 | 0.018739 | -0.011286 | 0.012281 | -0.0052808 | 0.0097839 | 1.6159 | 1.712 | 1.5564 | 1.6479 | 1.8036 | 1.5656 | 1.4008 | 34.9136 | 35.0372 | 34.9869 | 34.9869 | 34.877 | 8.7799 | 8.6884 | 89.8499 | 89.6851 | -33.1467 | 89.9963 | 89.9323 | 0.24719 | -33.3344 | 97.0642 | 96.9727 | 0.036621 | 123.1979 | 123.2712 | 26.2985 | -0.073242 | 90.0879 | 89.9002 | 89.8407 | -33.5495 | 123.2712 | 123.1613 | 123.3215 | -26.2619
2396.5156 | 123.4634 | -88.298 | 34.8816 | 0.050354 | 0.011604 | 0.0045673 | 0.012394 | -0.019766 | -0.004501 | 0.00084388 | 0.0032804 | 0.017884 | -0.013208 | 0.012922 | -0.0046398 | 0.011707 | 1.593 | 1.7075 | 1.593 | 1.6617 | 1.7532 | 1.5884 | 1.4236 | 34.964 | 35.0372 | 35.0327 | 34.8724 | 34.7992 | 8.7891 | 8.6838 | 89.8865 | 89.7217 | -33.1284 | 90.0055 | 89.9597 | 0.23804 | -33.2886 | 97.0871 | 96.9818 | -0.009155 | 123.262 | 123.3307 | 26.3489 | -0.082398 | 90.0513 | 89.8911 | 89.8911 | -33.4579 | 123.1705 | 123.0972 | 123.3353 | -26.1978
2397.5156 | 123.4497 | -88.3255 | 34.877 | -0.17853 | 0.01075 | 0.0032855 | 0.012608 | -0.018271 | -0.0017238 | 0.0023391 | -0.12642 | 0.017457 | -0.012354 | 0.013777 | -0.0061352 | 0.010852 | 1.6708 | 1.767 | 1.6296 | 1.6937 | 1.7807 | 1.5793 | 1.4191 | 34.9228 | 35.0555 | 35.0098 | 34.8587 | 34.7946 | 8.7936 | 8.6884 | 89.9048 | 89.7446 | -33.0963 | 90.0925 | 90.0192 | 0.27466 | -33.2062 | 97.1191 | 97.0139 | -0.01831 | 123.2483 | 123.3353 | 26.3214 | -0.082397 | 90.1062 | 89.9963 | 89.9551 | -33.4579 | 123.1842 | 123.1201 | 123.381 | -26.1887
2398.5156 | 123.4314 | -88.3575 | 34.8404 | 0.09613 | 0.0096813 | 0.0022175 | 0.012608 | -0.019339 | -0.001083 | 0.00063028 | -0.14931 | 0.018098 | -0.014063 | 0.01164 | -0.0052808 | 0.014056 | 1.5976 | 1.5884 | 1.4374 | 1.5656 | 1.7212 | 1.5381 | 1.3596 | 34.845 | 34.9686 | 34.9365 | 34.8267 | 34.7443 | 8.7845 | 8.6746 | 89.8956 | 89.7171 | -33.1192 | 89.946 | 89.9231 | 0.20599 | -33.2428 | 97.142 | 97.0322 | -0.013733 | 123.2025 | 123.2941 | 26.2619 | -0.09613 | 90.0787 | 89.9551 | 89.7949 | -33.4808 | 123.1842 | 123.1018 | 123.3261 | -26.1658
2399.5156 | 123.468 | -88.3987 | 34.758 | -0.056458 | 0.0088269 | 0.0030719 | 0.011967 | -0.019339 | -0.00086945 | 0.00041648 | -0.0043486 | 0.017671 | -0.012781 | 0.013563 | -0.0020764 | 0.011066 | 1.6571 | 1.712 | 1.6113 | 1.6617 | 1.7624 | 1.5793 | 1.4191 | 34.8633 | 34.9548 | 34.9594 | 34.7855 | 34.7031 | 8.7845 | 8.6838 | 89.978 | 89.8178 | -32.9956 | 90.1108 | 90.0604 | 0.24262 | -33.1009 | 97.1832 | 97.0825 | 0.027465 | 123.262 | 123.3582 | 26.2756 | -0.054932 | 90.1611 | 90.0558 | 90.0101 | -33.3389 | 123.1842 | 123.1018 | 123.3536 | -26.0742
2400.5156 | 123.4268 | -88.4308 | 34.7305 | 0.17242 | 0.010109 | 0.0032855 | 0.012608 | -0.021262 | -0.00065585 | 0.0025529 | 0.1635 | 0.018525 | -0.013636 | 0.011213 | -0.0037854 | 0.010638 | 1.6388 | 1.712 | 1.6022 | 1.6296 | 1.7441 | 1.5747 | 1.4236 | 34.8038 | 34.8404 | 34.8541 | 34.7305 | 34.671 | 8.7799 | 8.6792 | 90.0055 | 89.8544 | -32.9865 | 90.1428 | 90.0604 | 0.20599 | -33.0917 | 97.2107 | 97.11 | 0 | 123.2346 | 123.2849 | 26.1749 | -0.059509 | 90.1749 | 90.0696 | 90.033 | -33.3069 | 123.1613 | 123.1018 | 123.2712 | -26.0513
2401.5156 | 123.4314 | -88.5086 | 34.6756 | 0.50812 | 0.0075451 | 0.0028583 | 0.013249 | -0.016562 | -0.0021512 | 0.0012711 | 0.056686 | 0.016816 | -0.012781 | 0.014631 | -0.0044262 | 0.012134 | 1.5884 | 1.6663 | 1.5793 | 1.6525 | 1.7395 | 1.561 | 1.3824 | 34.7351 | 34.8267 | 34.7992 | 34.6939 | 34.6298 | 8.7799 | 8.6838 | 90.0696 | 89.8911 | -32.9361 | 90.1749 | 90.1611 | 0.27008 | -33.0872 | 97.2885 | 97.1924 | 0.018311 | 123.2437 | 123.3078 | 26.1154 | -0.045776 | 90.2481 | 90.097 | 90.0879 | -33.2932 | 123.2025 | 123.1384 | 123.3353 | -25.9918
2402.5156 | 123.3994 | -88.559 | 34.6436 | 0.18768 | 0.0098951 | 0.0039263 | 0.013035 | -0.020194 | 0.00062595 | 0.0012711 | 0.17876 | 0.017671 | -0.0095768 | 0.012281 | -0.0016492 | 0.010211 | 1.68 | 1.7029 | 1.5793 | 1.6479 | 1.7441 | 1.5747 | 1.4008 | 34.7214 | 34.7672 | 34.7534 | 34.6756 | 34.5749 | 8.7753 | 8.6838 | 90.1337 | 89.9597 | -32.8995 | 90.2618 | 90.2069 | 0.24719 | -32.9636 | 97.3343 | 97.2427 | 0.032043 | 123.2803 | 123.3124 | 26.0696 | -0.068665 | 90.303 | 90.239 | 90.1382 | -33.2428 | 123.2346 | 123.1338 | 123.3261 | -25.9598
2403.5156 | 123.4634 | -88.559 | 34.6344 | 0.012207 | 0.0086133 | 0.0039263 | 0.011967 | -0.020407 | -0.0025784 | 0.00063028 | -0.0043486 | 0.018312 | -0.014063 | 0.011854 | -0.0033582 | 0.011493 | 1.6663 | 1.7029 | 1.5976 | 1.6571 | 1.7624 | 1.5793 | 1.4053 | 34.726 | 34.8129 | 34.8038 | 34.6527 | 34.5566 | 8.7845 | 8.6792 | 90.1382 | 89.9643 | -32.872 | 90.2618 | 90.2161 | 0.25177 | -32.9681 | 97.3434 | 97.2382 | 0.018311 | 123.2849 | 123.3627 | 26.1246 | -0.077819 | 90.3213 | 90.2252 | 90.1566 | -33.2291 | 123.2117 | 123.1155 | 123.3719 | -25.9552
2404.5156 | 123.4634 | -88.6002 | 34.5657 | 0.29449 | 0.011604 | 0.0037127 | 0.013035 | -0.018057 | 0.002335 | 0.0021255 | 0.15587 | 0.018739 | -0.010645 | 0.012495 | -0.0012218 | 0.011066 | 1.68 | 1.6983 | 1.5884 | 1.6571 | 1.7303 | 1.5701 | 1.4145 | 34.6756 | 34.7351 | 34.7122 | 34.5566 | 34.465 | 8.7845 | 8.6838 | 90.1703 | 90.0146 | -32.8354 | 90.2985 | 90.2573 | 0.24261 | -32.8857 | 97.3846 | 97.2839 | -0.009155 | 123.2758 | 123.3124 | 26.0284 | -0.10071 | 90.3305 | 90.2802 | 90.1886 | -33.1512 | 123.1567 | 123.0652 | 123.3353 | -25.882
2405.5156 | 123.4268 | -88.6414 | 34.552 | 0.15717 | 0.0088269 | 0.0034991 | 0.013249 | -0.018912 | -0.00065585 | 0.0029801 | 0.19402 | 0.015748 | -0.014704 | 0.01164 | -0.0050672 | 0.011493 | 1.6159 | 1.6571 | 1.5656 | 1.6388 | 1.7441 | 1.5839 | 1.4008 | 34.6024 | 34.6756 | 34.6756 | 34.552 | 34.5062 | 8.7753 | 8.6792 | 90.2252 | 90.0421 | -32.8079 | 90.2985 | 90.2802 | 0.23804 | -32.9361 | 97.4167 | 97.3206 | 0 | 123.2437 | 123.317 | 25.9964 | -0.045776 | 90.3854 | 90.2573 | 90.2069 | -33.1512 | 123.1934 | 123.1476 | 123.317 | -25.8728
2406.5156 | 123.468 | -88.6368 | 34.5016 | 0.14954 | 0.01609 | 0.0013629 | 0.01154 | -0.019339 | 0.0031894 | 0.0031937 | 0.17876 | 0.019593 | -0.012781 | 0.011854 | -0.0010082 | 0.0091431 | 1.6891 | 1.6891 | 1.5793 | 1.6525 | 1.7303 | 1.5564 | 1.4008 | 34.6298 | 34.6573 | 34.639 | 34.4925 | 34.4009 | 8.7936 | 8.6838 | 90.1932 | 90.0375 | -32.7713 | 90.3259 | 90.2893 | 0.25177 | -32.8125 | 97.4304 | 97.3206 | -0.009155 | 123.2666 | 123.2758 | 25.9552 | -0.10071 | 90.3671 | 90.3259 | 90.2161 | -33.1009 | 123.1293 | 123.0377 | 123.2941 | -25.8179
2407.5156 | 123.4314 | -88.71 | 34.465 | 0.13428 | 0.011177 | 0.0028583 | 0.012181 | -0.018698 | 0.002335 | 0.0034073 | 0.20927 | 0.01938 | -0.013849 | 0.012708 | -0.0018628 | 0.010425 | 1.6617 | 1.712 | 1.5976 | 1.6388 | 1.7303 | 1.5656 | 1.4099 | 34.5795 | 34.6436 | 34.6298 | 34.4742 | 34.4009 | 8.7845 | 8.6838 | 90.2756 | 90.1199 | -32.7347 | 90.4221 | 90.3488 | 0.22888 | -32.8033 | 97.4945 | 97.3938 | 0.009155 | 123.2895 | 123.3398 | 25.946 | -0.064087 | 90.4404 | 90.3717 | 90.3076 | -33.0551 | 123.1842 | 123.111 | 123.3536 | -25.7812
2408.5156 | 123.468 | -88.7695 | 34.3826 | 0.18768 | 0.01609 | -0.0018415 | 0.013035 | -0.020194 | 0.0014804 | 0.0036209 | 0.17876 | 0.020662 | -0.010431 | 0.014204 | -0.0020764 | 0.0087157 | 1.6708 | 1.6663 | 1.5701 | 1.6525 | 1.7303 | 1.5564 | 1.3824 | 34.5062 | 34.5016 | 34.3369 | 34.3872 | 34.3002 | 8.7891 | 8.6838 | 90.3259 | 90.152 | -32.6523 | 90.4358 | 90.4221 | 0.27008 | -32.7118 | 97.5586 | 97.4533 | 0.004578 | 123.2758 | 123.1064 | 25.6531 | -0.082397 | 90.4999 | 90.4404 | 90.3397 | -33.0002 | 123.1567 | 123.0698 | 123.2712 | -25.6989
2409.5156 | 123.436 | -88.765 | 34.4009 | 0.15717 | 0.012459 | 0.0041401 | 0.011967 | -0.01998 | -0.00022865 | 0.0046891 | 0.2169 | 0.018312 | -0.013422 | 0.012068 | -0.0037854 | 0.010852 | 1.6754 | 1.6891 | 1.6067 | 1.6388 | 1.7166 | 1.5564 | 1.3962 | 34.5337 | 34.5657 | 34.5657 | 34.4192 | 34.346 | 8.7891 | 8.6929 | 90.3214 | 90.1611 | -32.6843 | 90.4541 | 90.4037 | 0.24262 | -32.7255 | 97.554 | 97.4579 | 0.01831 | 123.2986 | 123.3307 | 25.8728 | -0.054932 | 90.4816 | 90.4404 | 90.3717 | -33.0048 | 123.1842 | 123.111 | 123.3307 | -25.708
2410.5156 | 123.4039 | -88.8428 | 34.3826 | 0.18005 | 0.016517 | -0.00013251 | 0.013249 | -0.021048 | 0.004044 | 0.0053299 | 0.14824 | 0.021089 | -0.0091494 | 0.014204 | -0.0025036 | 0.0080749 | 1.6067 | 1.5839 | 1.474 | 1.5839 | 1.7166 | 1.5289 | 1.3504 | 34.4376 | 34.4559 | 34.465 | 34.3826 | 34.3094 | 8.7753 | 8.6746 | 90.3717 | 90.1932 | -32.666 | 90.4266 | 90.4266 | 0.23346 | -32.7759 | 97.6181 | 97.5174 | 0 | 123.2803 | 123.3078 | 25.7904 | -0.073242 | 90.5594 | 90.4495 | 90.3168 | -33.0322 | 123.2254 | 123.1522 | 123.2986 | -25.708
2411.5156 | 123.4543 | -88.8245 | 34.3231 | 0.18005 | 0.0086133 | 0.0039263 | 0.010899 | -0.021689 | -0.00022865 | 0.0025529 | 0.19402 | 0.020021 | -0.012995 | 0.011427 | -0.0027172 | 0.01192 | 1.6571 | 1.6846 | 1.593 | 1.6479 | 1.7303 | 1.561 | 1.4008 | 34.4513 | 34.5062 | 34.5062 | 34.3323 | 34.2819 | 8.7891 | 8.6838 | 90.3854 | 90.2252 | -32.5928 | 90.509 | 90.4724 | 0.24719 | -32.666 | 97.6135 | 97.5082 | 0.009155 | 123.2758 | 123.3307 | 25.8224 | -0.041199 | 90.5548 | 90.4816 | 90.4175 | -32.9224 | 123.1567 | 123.1064 | 123.3307 | -25.6393
2412.5156 | 123.3398 | -88.8931 | 34.346 | 0.27924 | 0.020363 | 0.00029489 | 0.013249 | -0.021048 | 0.0021214 | 0.0029801 | 0.071945 | 0.020448 | -0.01214 | 0.011854 | -0.0042126 | 0.010638 | 1.6067 | 1.5381 | 1.4557 | 1.5564 | 1.7715 | 1.5152 | 1.3504 | 34.3323 | 34.3689 | 34.3506 | 34.3597 | 34.3002 | 8.7799 | 8.6884 | 90.4083 | 90.2435 | -32.5745 | 90.4312 | 90.4495 | 0.20599 | -32.7393 | 97.673 | 97.5815 | 0.013733 | 123.2254 | 123.2437 | 25.6622 | -0.045776 | 90.6647 | 90.4999 | 90.3488 | -32.9956 | 123.2529 | 123.1934 | 123.262 | -25.6577
2413.5156 | 123.468 | -88.8977 | 34.2773 | 0.24109 | 0.016517 | 0.0017901 | 0.011326 | -0.021262 | 0.0029758 | 0.0034073 | 0.15587 | 0.020021 | -0.0097904 | 0.014204 | -0.0033582 | 0.01192 | 1.6251 | 1.6296 | 1.5381 | 1.6022 | 1.7166 | 1.5518 | 1.3779 | 34.3964 | 34.465 | 34.4421 | 34.3094 | 34.2316 | 8.7708 | 8.6838 | 90.4495 | 90.2756 | -32.5607 | 90.5273 | 90.4999 | 0.2243 | -32.6523 | 97.6685 | 97.5815 | 0.032043 | 123.2941 | 123.3398 | 25.7584 | -0.045777 | 90.6143 | 90.5228 | 90.4358 | -32.8995 | 123.2071 | 123.1293 | 123.3627 | -25.5936
2414.5156 | 123.2758 | -88.9572 | 34.259 | 0.073242 | 0.016304 | 0.0017901 | 0.014317 | -0.019766 | 0.0038304 | 0.0034073 | 0.049057 | 0.020662 | -0.006586 | 0.012281 | -0.00036743 | 0.0089295 | 1.5427 | 1.5244 | 1.4511 | 1.5656 | 1.767 | 1.5198 | 1.3458 | 34.227 | 34.3094 | 34.2728 | 34.3552 | 34.2499 | 8.7753 | 8.6838 | 90.477 | 90.303 | -32.4921 | 90.4816 | 90.5228 | 0.21973 | -32.7164 | 97.7325 | 97.641 | 0.096131 | 123.1842 | 123.23 | 25.589 | -0.009155 | 90.7242 | 90.4999 | 90.4083 | -32.9132 | 123.3124 | 123.2071 | 123.2666 | -25.5753
2415.5156 | 123.3719 | -88.9847 | 34.2728 | 0.15717 | 0.018013 | 0.0026447 | 0.011113 | -0.017203 | 0.0029758 | 0.00084388 | 0.15587 | 0.022157 | -0.010004 | 0.017195 | -0.0010082 | 0.011066 | 1.561 | 1.5518 | 1.4465 | 1.5656 | 1.7624 | 1.5152 | 1.355 | 34.259 | 34.314 | 34.3094 | 34.2636 | 34.2087 | 8.7753 | 8.6792 | 90.4999 | 90.3397 | -32.5104 | 90.5365 | 90.5502 | 0.21057 | -32.7118 | 97.76 | 97.6639 | -0.009155 | 123.2437 | 123.2941 | 25.6302 | -0.064087 | 90.7471 | 90.5457 | 90.4312 | -32.9178 | 123.2483 | 123.1934 | 123.2986 | -25.5936
2416.5156 | 123.2986 | -89.0442 | 34.1812 | 0.073242 | 0.019508 | 0.0020037 | 0.014317 | -0.019553 | 0.0042576 | 0.0044755 | 0.071945 | 0.020234 | -0.0097904 | 0.013777 | -0.0033582 | 0.012134 | 1.5472 | 1.5244 | 1.4557 | 1.5701 | 1.7578 | 1.5015 | 1.3367 | 34.14 | 34.2041 | 34.1812 | 34.2224 | 34.1721 | 8.7891 | 8.6746 | 90.5457 | 90.3809 | -32.4234 | 90.5685 | 90.6143 | 0.23346 | -32.634 | 97.8333 | 97.7188 | 0.041199 | 123.1842 | 123.2254 | 25.5066 | -0.009155 | 90.802 | 90.5914 | 90.4999 | -32.8445 | 123.2666 | 123.2162 | 123.2483 | -25.5066
2417.5156 | 123.3948 | -89.003 | 34.259 | 0.14191 | 0.01844 | 0.0030719 | 0.01389 | -0.018912 | 0.0025486 | 0.0042619 | 0.19402 | 0.021089 | -0.011499 | 0.010145 | -0.0031446 | 0.010852 | 1.5793 | 1.5564 | 1.4557 | 1.5793 | 1.7532 | 1.5289 | 1.3504 | 34.2407 | 34.3002 | 34.2957 | 34.2819 | 34.2087 | 8.7845 | 8.6792 | 90.5319 | 90.3534 | -32.5058 | 90.5594 | 90.5823 | 0.22888 | -32.6797 | 97.7875 | 97.6822 | 0.022888 | 123.2437 | 123.2986 | 25.6165 | -0.050354 | 90.7562 | 90.5823 | 90.4587 | -32.9086 | 123.2849 | 123.2117 | 123.3032 | -25.5798
2418.5156 | 123.3536 | -89.0259 | 34.2087 | 0.019836 | 0.018013 | 0.00072209 | 0.014958 | -0.020194 | 0.0029758 | 0.0027665 | 0.026169 | 0.020875 | -0.0087222 | 0.011854 | -0.0018628 | 0.012988 | 1.6067 | 1.593 | 1.4969 | 1.593 | 1.7624 | 1.5335 | 1.355 | 34.1858 | 34.2728 | 34.2407 | 34.2361 | 34.1858 | 8.7845 | 8.6746 | 90.5594 | 90.3809 | -32.4463 | 90.6189 | 90.6189 | 0.23804 | -32.6019 | 97.8104 | 97.7005 | 0.027466 | 123.2117 | 123.2666 | 25.5661 | -0.022888 | 90.7883 | 90.6326 | 90.5228 | -32.8537 | 123.262 | 123.2117 | 123.2986 | -25.5341
2419.5156 | 123.3627 | -89.0625 | 34.1537 | 0.13428 | 0.022285 | 0.0028583 | 0.011754 | -0.020194 | 0.0014804 | 0.0016983 | 0.22453 | 0.020875 | -0.0089358 | 0.012922 | -0.0046398 | 0.010425 | 1.5656 | 1.5564 | 1.4603 | 1.5747 | 1.7715 | 1.5289 | 1.3687 | 34.1354 | 34.2133 | 34.2224 | 34.1949 | 34.1217 | 8.7753 | 8.6884 | 90.5914 | 90.4312 | -32.3822 | 90.6189 | 90.6372 | 0.20599 | -32.5882 | 97.8378 | 97.7509 | 0.041198 | 123.1979 | 123.2849 | 25.5341 | -0.032044 | 90.834 | 90.6281 | 90.5228 | -32.785 | 123.2574 | 123.1842 | 123.2758 | -25.4654
2420.5156 | 123.3444 | -89.1678 | 34.1171 | 0.065613 | 0.017799 | 0.0020037 | 0.013676 | -0.018698 | 0.0019078 | 0.0025529 | 0.11009 | 0.023011 | -0.011286 | 0.01399 | -0.0037854 | 0.0099975 | 1.5335 | 1.5289 | 1.4557 | 1.5656 | 1.7487 | 1.5198 | 1.3504 | 34.0439 | 34.1125 | 34.0851 | 34.1492 | 34.0714 | 8.7799 | 8.6792 | 90.6876 | 90.5182 | -32.3685 | 90.6967 | 90.7333 | 0.21515 | -32.5836 | 97.9477 | 97.847 | 0.032044 | 123.2117 | 123.2529 | 25.4059 | -0.045776 | 90.9164 | 90.7013 | 90.6235 | -32.7667 | 123.317 | 123.2391 | 123.2803 | -25.4379
2421.5156 | 123.3627 | -89.1769 | 34.0851 | 0.0045777 | 0.015236 | 8.1086e-05 | 0.014744 | -0.020407 | 0.0019078 | 0.0040481 | -0.019608 | 0.020234 | -0.0087222 | 0.013563 | -0.0035718 | 0.0099975 | 1.6205 | 1.6205 | 1.4969 | 1.6067 | 1.7487 | 1.5198 | 1.3412 | 34.0576 | 34.1583 | 34.1309 | 34.0714 | 34.0302 | 8.7753 | 8.6838 | 90.6967 | 90.5182 | -32.3364 | 90.7974 | 90.7837 | 0.2655 | -32.4646 | 97.9523 | 97.8607 | -0.013733 | 123.2346 | 123.3078 | 25.4471 | -0.054932 | 90.9256 | 90.7974 | 90.6738 | -32.7438 | 123.2483 | 123.2071 | 123.3353 | -25.4013
2422.5156 | 123.4177 | -89.1678 | 34.0439 | 0.15717 | 0.010963 | 0.0032855 | 0.013249 | -0.01998 | -0.0049282 | 0.0012711 | 0.27794 | 0.018525 | -0.013208 | 0.014204 | -0.0052808 | 0.012561 | 1.6205 | 1.6754 | 1.5747 | 1.6251 | 1.7166 | 1.561 | 1.4008 | 34.0576 | 34.1766 | 34.1721 | 34.0027 | 33.9615 | 8.7799 | 8.6746 | 90.7288 | 90.5685 | -32.3273 | 90.8432 | 90.7928 | 0.2243 | -32.4234 | 97.9477 | 97.8424 | -0.041198 | 123.2254 | 123.3398 | 25.4974 | -0.082397 | 90.8844 | 90.7883 | 90.7425 | -32.6431 | 123.1705 | 123.1293 | 123.3444 | -25.3693
2423.5156 | 123.317 | -89.2639 | 34.0118 | 0.073242 | 0.015663 | 0.00093569 | 0.014317 | -0.018912 | 0.004044 | 0.0027665 | 0.033798 | 0.021516 | -0.009363 | 0.012281 | 0.00070077 | 0.010425 | 1.5656 | 1.5472 | 1.4557 | 1.5701 | 1.7578 | 1.5152 | 1.3275 | 33.9432 | 34.0302 | 34.0027 | 34.0302 | 33.9661 | 8.7799 | 8.6746 | 90.7791 | 90.5914 | -32.254 | 90.8112 | 90.834 | 0.24261 | -32.4463 | 98.0438 | 97.9385 | 0.01831 | 123.2071 | 123.2666 | 25.3281 | -0.045777 | 91.0217 | 90.8295 | 90.7196 | -32.6843 | 123.2941 | 123.23 | 123.2941 | -25.3372
2424.5156 | 123.3856 | -89.2685 | 33.9798 | -0.13275 | 0.019722 | 0.0024311 | 0.013249 | -0.018912 | 0.0029758 | 0.0031937 | -0.13405 | 0.020234 | -0.010431 | 0.013563 | -0.0025036 | 0.010852 | 1.5793 | 1.593 | 1.4923 | 1.6067 | 1.7578 | 1.5152 | 1.3412 | 33.9752 | 34.0805 | 34.0485 | 33.9935 | 33.9294 | 8.7799 | 8.6838 | 90.7837 | 90.6097 | -32.222 | 90.8615 | 90.8752 | 0.2655 | -32.4005 | 98.0484 | 97.9523 | 0.013733 | 123.2437 | 123.317 | 25.3647 | -0.050354 | 91.0263 | 90.8478 | 90.7608 | -32.6385 | 123.262 | 123.1979 | 123.349 | -25.296
2425.5156 | 123.3719 | -89.2822 | 33.9432 | 0.0045777 | 0.01844 | 0.0024311 | 0.012181 | -0.019766 | 0.0038304 | 0.0021255 | -0.027237 | 0.020875 | -0.010645 | 0.012281 | -0.0027172 | 0.010425 | 1.593 | 1.5976 | 1.4969 | 1.593 | 1.7395 | 1.5289 | 1.3367 | 33.934 | 34.0256 | 33.9798 | 33.9661 | 33.9157 | 8.7799 | 8.6792 | 90.8112 | 90.6189 | -32.2037 | 90.8798 | 90.8752 | 0.25635 | -32.3502 | 98.0621 | 97.9614 | 0.022888 | 123.2162 | 123.262 | 25.3006 | -0.027466 | 91.0217 | 90.8752 | 90.7791 | -32.6065 | 123.2483 | 123.1979 | 123.3078 | -25.264
2426.5156 | 123.3856 | -89.3097 | 33.8882 | -0.11749 | 0.01609 | 0.00072209 | 0.012822 | -0.018271 | 0.0014804 | 0.0031937 | -0.10353 | 0.019593 | -0.01214 | 0.014417 | -0.0018628 | 0.0097839 | 1.5884 | 1.5976 | 1.4877 | 1.6159 | 1.7532 | 1.5152 | 1.3458 | 33.8974 | 34.0118 | 33.9752 | 33.9249 | 33.8699 | 8.7753 | 8.6792 | 90.8249 | 90.6555 | -32.135 | 90.9073 | 90.9256 | 0.27008 | -32.2998 | 98.085 | 97.9889 | 0.036621 | 123.2071 | 123.2849 | 25.296 | -0.018311 | 91.0629 | 90.8981 | 90.7974 | -32.5424 | 123.2346 | 123.1796 | 123.3215 | -25.209
2427.5156 | 123.4314 | -89.3143 | 33.8974 | 0.87433 | 0.010109 | 0.0077717 | 0.009831 | -0.019339 | -0.0066372 | -0.00043792 | 0.1635 | 0.018953 | -0.014063 | 0.015699 | -0.0059216 | 0.014056 | 1.5198 | 1.6159 | 1.5244 | 1.5976 | 1.6891 | 1.4923 | 1.3367 | 33.8791 | 34.0118 | 34.0302 | 33.8928 | 33.8379 | 8.7799 | 8.6838 | 90.8066 | 90.6509 | -32.2083 | 90.9302 | 90.9119 | 0.26093 | -32.3776 | 98.0942 | 97.998 | -0.004578 | 123.1934 | 123.3444 | 25.3464 | -0.059509 | 91.0034 | 90.834 | 90.8386 | -32.5607 | 123.2071 | 123.1522 | 123.3261 | -25.2136
2428.5156 | 123.381 | -89.3692 | 33.8745 | -0.14038 | 0.014381 | 0.00093569 | 0.013035 | -0.019553 | 0.002335 | 0.0025529 | -0.14931 | 0.021089 | -0.011499 | 0.012068 | -0.0012218 | 0.0097839 | 1.5701 | 1.561 | 1.4648 | 1.5884 | 1.767 | 1.4923 | 1.3367 | 33.847 | 33.9432 | 33.9157 | 33.9111 | 33.847 | 8.7799 | 8.67 | 90.8615 | 90.7059 | -32.1075 | 90.9302 | 90.9576 | 0.25177 | -32.3044 | 98.1491 | 98.0392 | 0.036621 | 123.2162 | 123.2849 | 25.2457 | -0.027466 | 91.1362 | 90.9393 | 90.834 | -32.5378 | 123.2803 | 123.2162 | 123.3124 | -25.2045
2429.5156 | 123.4039 | -89.4058 | 33.8333 | -0.056458 | 0.017799 | 0.00093569 | 0.013249 | -0.018271 | 0.0044712 | 0.0027665 | -0.24086 | 0.020448 | -0.0089358 | 0.013563 | -0.0012218 | 0.0078613 | 1.8448 | 1.7532 | 1.5472 | 1.6846 | 1.8127 | 1.5564 | 1.3962 | 33.8379 | 33.934 | 33.8791 | 33.847 | 33.7875 | 8.7845 | 8.6792 | 90.9622 | 90.802 | -32.0206 | 91.1591 | 91.0904 | 0.28839 | -31.9885 | 98.1903 | 98.085 | 0.013733 | 123.2437 | 123.2849 | 25.1999 | -0.045776 | 91.2186 | 91.2506 | 90.9531 | -32.4371 | 123.2529 | 123.1934 | 123.3398 | -25.1541
2430.5156 | 123.3994 | -89.4608 | 33.8104 | -0.15564 | 0.014168 | 0.0026447 | 0.015385 | -0.017203 | 0.00062595 | 0.0044755 | -0.17983 | 0.01703 | -0.011927 | 0.015058 | -0.0014356 | 0.011066 | 1.5381 | 1.5793 | 1.4603 | 1.5793 | 1.7715 | 1.5015 | 1.3321 | 33.7418 | 33.8745 | 33.847 | 33.847 | 33.7372 | 8.7845 | 8.6792 | 90.9622 | 90.7928 | -32.0389 | 91.04 | 91.04 | 0.24719 | -32.2723 | 98.2452 | 98.14 | 0.036621 | 123.2025 | 123.3078 | 25.1678 | -0.073242 | 91.2323 | 90.9988 | 90.921 | -32.4783 | 123.3078 | 123.1979 | 123.3353 | -25.1312
2431.5156 | 123.3765 | -89.502 | 33.7555 | -0.041199 | 0.018867 | 0.0020037 | 0.014744 | -0.018912 | 0.003403 | 0.0061845 | -0.10353 | 0.020448 | -0.0074404 | 0.013777 | -0.0016492 | 0.011066 | 1.6571 | 1.767 | 1.5976 | 1.6113 | 1.8082 | 1.5884 | 1.4145 | 33.7738 | 33.847 | 33.8058 | 33.7692 | 33.6777 | 8.7799 | 8.6838 | 91.0904 | 90.9164 | -31.9473 | 91.2689 | 91.1133 | 0.19684 | -32.0984 | 98.2819 | 98.1857 | 0.013733 | 123.2758 | 123.3078 | 25.1221 | -0.07782 | 91.3101 | 91.1591 | 91.0995 | -32.341 | 123.2712 | 123.1796 | 123.349 | -25.0717
2432.5156 | 123.3261 | -89.5111 | 33.7372 | 0.042725 | 0.017158 | 0.0022175 | 0.016881 | -0.018912 | 0.0042576 | 0.0038345 | 0.064316 | 0.022371 | -0.0095768 | 0.01399 | -0.0042126 | 0.01192 | 1.5427 | 1.5656 | 1.4694 | 1.5518 | 1.7441 | 1.5198 | 1.3504 | 33.6914 | 33.7875 | 33.7463 | 33.7601 | 33.7143 | 8.7799 | 8.6746 | 91.0309 | 90.8615 | -31.9931 | 91.0767 | 91.0629 | 0.20142 | -32.1945 | 98.291 | 98.1857 | 0.022888 | 123.2025 | 123.2574 | 25.0717 | -0.022889 | 91.2552 | 91.0538 | 90.9805 | -32.3868 | 123.2712 | 123.2254 | 123.2986 | -25.0626
2433.5156 | 123.3673 | -89.502 | 33.7646 | -0.15564 | 0.015022 | 0.0034991 | 0.014317 | -0.018912 | 0.0010532 | 0.0019119 | -0.12642 | 0.021516 | -0.010004 | 0.013777 | -0.0054944 | 0.012347 | 1.5427 | 1.561 | 1.474 | 1.5976 | 1.7899 | 1.5152 | 1.3458 | 33.6823 | 33.8013 | 33.783 | 33.7692 | 33.7006 | 8.7845 | 8.6838 | 91.0172 | 90.8478 | -31.9748 | 91.0629 | 91.0995 | 0.25177 | -32.222 | 98.2864 | 98.1857 | 0.004578 | 123.1842 | 123.2849 | 25.0992 | -0.064086 | 91.2918 | 91.0446 | 90.976 | -32.4188 | 123.2712 | 123.2025 | 123.3032 | -25.0809
2434.5156 | 123.4634 | -89.5065 | 33.6914 | -0.15564 | 0.010109 | 0.0043537 | 0.010899 | -0.019126 | -0.0066372 | -1.0724e-05 | 0.31609 | 0.018312 | -0.013422 | 0.010999 | -0.0063488 | 0.012347 | 1.8036 | 1.3962 | 1.4648 | 1.68 | 1.7212 | 1.5289 | 1.3687 | 33.7418 | 33.8928 | 33.8608 | 33.6685 | 33.6319 | 8.7799 | 8.6838 | 91.0355 | 90.8752 | -31.9702 | 90.9027 | 91.1865 | 0.31128 | -31.8878 | 98.2864 | 98.1903 | -0.022888 | 123.2483 | 123.3673 | 25.177 | -0.059509 | 91.2277 | 91.3101 | 90.9714 | -32.3227 | 123.175 | 123.1384 | 123.3994 | -25.0076
2435.5156 | 123.3673 | -89.5935 | 33.6548 | -0.13275 | 0.016304 | 0.0013629 | 0.016881 | -0.017417 | 0.00083955 | -0.00022432 | -0.14931 | 0.022584 | -0.0095768 | 0.01164 | -0.0033582 | 0.010425 | 1.5427 | 1.5747 | 1.4603 | 1.5839 | 1.7761 | 1.5106 | 1.3412 | 33.609 | 33.7051 | 33.696 | 33.6685 | 33.6273 | 8.7845 | 8.6838 | 91.1041 | 90.9348 | -31.8787 | 91.1682 | 91.1774 | 0.24261 | -32.1121 | 98.378 | 98.2773 | 0.013733 | 123.2025 | 123.2895 | 25.0122 | -0.027466 | 91.3696 | 91.1362 | 91.0538 | -32.3135 | 123.262 | 123.2208 | 123.2986 | -24.971
2436.5156 | 123.4314 | -89.5798 | 33.6365 | -0.16327 | 0.010109 | 0.0058491 | 0.011754 | -0.016135 | -0.0015102 | -0.00086512 | -0.11116 | 0.018525 | -0.014276 | 0.013349 | -0.0046398 | 0.010211 | 1.5839 | 1.7029 | 1.5839 | 1.6342 | 1.7349 | 1.5381 | 1.387 | 33.6639 | 33.8013 | 33.7509 | 33.6136 | 33.5632 | 8.7799 | 8.6838 | 91.1179 | 90.9668 | -31.9016 | 91.2827 | 91.214 | 0.24719 | -32.0526 | 98.3597 | 98.2636 | -0.022889 | 123.2437 | 123.3307 | 25.0671 | -0.073243 | 91.3147 | 91.1636 | 91.1636 | -32.2495 | 123.1934 | 123.143 | 123.381 | -24.9527
2437.5156 | 123.349 | -89.6576 | 33.6136 | 0.027466 | 0.021431 | 0.0022175 | 0.014317 | -0.020621 | 0.0046848 | 0.0025529 | 0.071945 | 0.021089 | -0.0091494 | 0.015272 | -0.0012218 | 0.0099975 | 1.5289 | 1.5427 | 1.4282 | 1.5472 | 1.7395 | 1.4969 | 1.3367 | 33.5083 | 33.5907 | 33.577 | 33.6182 | 33.5495 | 8.7799 | 8.6838 | 91.1545 | 90.9943 | -31.8741 | 91.2003 | 91.2048 | 0.21057 | -32.0847 | 98.4375 | 98.3414 | 0.004578 | 123.1659 | 123.2346 | 24.8932 | -0.064086 | 91.3971 | 91.1865 | 91.0858 | -32.2769 | 123.2758 | 123.2071 | 123.2483 | -24.9298
2438.5156 | 123.4818 | -89.6393 | 33.5312 | -0.14801 | 0.0077587 | 0.0028583 | 0.010472 | -0.017844 | -0.0047146 | 0.00041648 | -0.10353 | 0.018098 | -0.0097904 | 0.014204 | -0.006776 | 0.011707 | 1.6067 | 1.7258 | 1.4374 | 1.7532 | 1.7166 | 1.5289 | 1.3596 | 33.5632 | 33.7738 | 33.7189 | 33.5266 | 33.4854 | 8.7845 | 8.6838 | 91.1682 | 90.9988 | -31.8146 | 91.3651 | 91.3925 | 0.39368 | -31.9244 | 98.4238 | 98.3231 | -0.004578 | 123.2025 | 123.3582 | 25.0351 | -0.045776 | 91.3559 | 91.246 | 91.0767 | -32.1716 | 123.1659 | 123.1247 | 123.4131 | -24.8474
2439.5156 | 123.349 | -89.7079 | 33.5449 | -0.27771 | 0.011177 | 0.0037127 | 0.013676 | -0.018485 | 0.00062595 | 0.0023391 | -0.15694 | 0.018953 | -0.0097904 | 0.012281 | -0.003999 | 0.010211 | 1.5198 | 1.5839 | 1.4832 | 1.5472 | 1.7441 | 1.5106 | 1.3367 | 33.4396 | 33.9386 | 33.5129 | 33.5632 | 33.5037 | 8.7753 | 8.6746 | 91.2186 | 91.0446 | -31.8008 | 91.2918 | 91.2552 | 0.21057 | -32.0251 | 98.4833 | 98.3826 | 0.01831 | 123.1476 | 123.2208 | 24.8383 | -0.041199 | 91.452 | 91.2277 | 91.1911 | -32.2083 | 123.2712 | 123.2117 | 123.6465 | -24.8703
2440.5156 | 123.4726 | -89.7354 | 33.4534 | -0.02594 | 0.0090405 | 0.0037127 | 0.012181 | -0.023612 | -0.0051418 | 0.00041648 | 0.041427 | 0.016176 | -0.010645 | 0.012708 | -0.0044262 | 0.013416 | 1.5884 | 1.6983 | 1.5884 | 1.6434 | 1.7395 | 1.5472 | 1.3779 | 33.5449 | 33.6502 | 33.6319 | 33.4579 | 33.3893 | 8.7799 | 8.6838 | 91.2827 | 91.1133 | -31.7139 | 91.4337 | 91.3788 | 0.2655 | -31.8649 | 98.5153 | 98.4192 | 0.004578 | 123.2803 | 123.3673 | 24.9481 | -0.064087 | 91.4749 | 91.3239 | 91.3239 | -32.0755 | 123.1934 | 123.1247 | 123.3856 | -24.7696
2441.5156 | 123.5184 | -89.7629 | 33.4076 | -0.071716 | 0.0081861 | 0.0049945 | 0.011754 | -0.018485 | -0.0038602 | 0.00020288 | -0.042496 | 0.016603 | -0.01449 | 0.010786 | -0.0054944 | 0.011066 | 1.6113 | 1.7258 | 1.5884 | 1.6479 | 1.7349 | 1.5564 | 1.3779 | 33.522 | 33.6136 | 33.5907 | 33.3755 | 33.3527 | 8.7845 | 8.6792 | 91.3193 | 91.1407 | -31.6727 | 91.4886 | 91.4108 | 0.27008 | -31.7963 | 98.5474 | 98.4421 | -0.032044 | 123.2849 | 123.3536 | 24.9115 | -0.054932 | 91.4978 | 91.3742 | 91.3513 | -32.0297 | 123.1384 | 123.1155 | 123.3765 | -24.7284
2442.5156 | 123.4314 | -89.859 | 33.3069 | 0.11139 | 0.0092541 | 0.0056353 | 0.013035 | -0.01998 | -0.0021512 | 0.0016983 | 0.087204 | 0.015321 | -0.0095768 | 0.01164 | -0.0031446 | 0.012561 | 1.5381 | 1.6159 | 1.5244 | 1.5839 | 1.7212 | 1.5289 | 1.3641 | 33.3572 | 33.4671 | 33.4534 | 33.3527 | 33.2336 | 8.7845 | 8.6792 | 91.3879 | 91.2231 | -31.5857 | 91.4749 | 91.4429 | 0.21973 | -31.7688 | 98.6435 | 98.5382 | 0.045776 | 123.2162 | 123.3124 | 24.7742 | -0.073242 | 91.5802 | 91.3971 | 91.3834 | -31.9427 | 123.2117 | 123.0927 | 123.3261 | -24.6277
2443.5156 | 123.4818 | -89.8636 | 33.3069 | -0.12512 | 0.0088269 | 0.0073443 | 0.010045 | -0.018485 | -0.0032192 | 0.00020288 | -0.11116 | 0.018098 | -0.012781 | 0.012495 | -0.0037854 | 0.010638 | 1.7258 | 1.6388 | 1.5518 | 1.6479 | 1.6937 | 1.5152 | 1.3687 | 33.3847 | 33.5037 | 33.4579 | 33.3252 | 33.2474 | 8.7845 | 8.6838 | 91.3788 | 91.2323 | -31.6132 | 91.5024 | 91.5115 | 0.27924 | -31.5811 | 98.6481 | 98.5474 | 0.01831 | 123.2483 | 123.3215 | 24.7742 | -0.05951 | 91.5573 | 91.5894 | 91.4154 | -31.9382 | 123.1888 | 123.111 | 123.3673 | -24.6231
2444.5156 | 123.4268 | -89.9094 | 33.2703 | 0.012207 | 0.011177 | 0.0045673 | 0.014958 | -0.018698 | -0.0025784 | 0.00020288 | 0.079574 | 0.017457 | -0.011927 | 0.012281 | -0.0046398 | 0.0095703 | 1.5427 | 1.6205 | 1.5335 | 1.5884 | 1.7029 | 1.5015 | 1.3321 | 33.3115 | 33.403 | 33.3893 | 33.2977 | 33.2016 | 8.7753 | 8.6792 | 91.4108 | 91.2415 | -31.5674 | 91.5298 | 91.4978 | 0.25635 | -31.7276 | 98.6847 | 98.5886 | 0.027465 | 123.2208 | 123.2986 | 24.7101 | -0.068665 | 91.6122 | 91.452 | 91.4429 | -31.9382 | 123.2071 | 123.111 | 123.3124 | -24.5911
2445.5156 | 123.4634 | -89.9414 | 33.2565 | -0.21667 | 0.0073315 | 0.0028583 | 0.01154 | -0.020621 | -0.0023648 | 0.00041648 | -0.073013 | 0.019166 | -0.012781 | 0.010145 | -0.0029308 | 0.0095703 | 1.6479 | 1.7075 | 1.5198 | 1.7075 | 1.7258 | 1.5106 | 1.3458 | 33.316 | 33.4854 | 33.403 | 33.2428 | 33.1604 | 8.7845 | 8.6838 | 91.452 | 91.2872 | -31.5308 | 91.6489 | 91.6489 | 0.36163 | -31.6086 | 98.7259 | 98.6252 | -0.013733 | 123.2574 | 123.3444 | 24.7192 | -0.096131 | 91.6672 | 91.5894 | 91.4612 | -31.9107 | 123.1842 | 123.1018 | 123.4268 | -24.5728
2446.5156 | 123.436 | -89.9872 | 33.2016 | 0.14954 | 0.011177 | 0.0030719 | 0.013463 | -0.020835 | 0.00019875 | -0.00022432 | 0.1635 | 0.018739 | -0.012995 | 0.01164 | -0.0029308 | 0.012134 | 1.6067 | 1.6479 | 1.5335 | 1.5884 | 1.6937 | 1.5335 | 1.3596 | 33.2748 | 33.3298 | 33.3298 | 33.2062 | 33.1329 | 8.7845 | 8.6838 | 91.5207 | 91.3467 | -31.5079 | 91.6351 | 91.5756 | 0.22888 | -31.5948 | 98.7717 | 98.671 | 0.004578 | 123.262 | 123.317 | 24.646 | -0.068664 | 91.6809 | 91.5939 | 91.5207 | -31.842 | 123.1934 | 123.1201 | 123.317 | -24.5178
2447.5156 | 123.468 | -90.0284 | 33.1787 | -0.056458 | 0.0083997 | 0.0032855 | 0.01389 | -0.01998 | -1.505e-05 | 0.0014847 | 0.01091 | 0.015962 | -0.014063 | 0.013777 | -0.0042126 | 0.011066 | 1.6113 | 1.6708 | 1.561 | 1.6296 | 1.7212 | 1.5518 | 1.355 | 33.2703 | 33.3389 | 33.3252 | 33.1787 | 33.1146 | 8.7799 | 8.6746 | 91.5802 | 91.3834 | -31.4575 | 91.6992 | 91.658 | 0.27466 | -31.5674 | 98.8083 | 98.703 | 0 | 123.2986 | 123.3536 | 24.6506 | -0.064087 | 91.7496 | 91.6397 | 91.5894 | -31.8237 | 123.2071 | 123.143 | 123.3673 | -24.5041
2448.5156 | 123.5275 | -90.0558 | 33.11 | 0.18768 | 0.013527 | 0.0028583 | 0.011967 | -0.018485 | 0.0025486 | 0.0021255 | 0.1635 | 0.020448 | -0.010218 | 0.013349 | -0.0016492 | 0.0091431 | 1.6342 | 1.6342 | 1.5289 | 1.6067 | 1.6891 | 1.5289 | 1.355 | 33.2565 | 33.2886 | 33.2748 | 33.1375 | 33.078 | 8.7982 | 8.6838 | 91.5848 | 91.4108 | -31.4209 | 91.6901 | 91.6626 | 0.25177 | -31.4758 | 98.8541 | 98.7396 | 0.027466 | 123.3124 | 123.3307 | 24.5911 | -0.032043 | 91.745 | 91.6901 | 91.5848 | -31.7551 | 123.1934 | 123.1338 | 123.3444 | -24.4263
2449.5156 | 123.4314 | -90.0696 | 33.1375 | 0.057983 | 0.0086133 | 0.0026447 | 0.01154 | -0.01998 | -0.002792 | 0.0016983 | 0.3466 | 0.018098 | -0.013636 | 0.01164 | -0.003999 | 0.012347 | 1.5656 | 1.7166 | 1.3275 | 1.4694 | 1.68 | 1.474 | 1.3229 | 33.1558 | 33.2611 | 33.2428 | 33.1329 | 33.0643 | 8.7799 | 8.6792 | 91.5436 | 91.3925 | -31.4575 | 91.7862 | 91.539 | 0.14648 | -31.572 | 98.8495 | 98.7488 | -0.004577 | 123.2254 | 123.3124 | 24.5636 | -0.073242 | 91.7496 | 91.6351 | 91.3971 | -31.8146 | 123.2025 | 123.1338 | 123.3307 | -24.4583
2450.5156 | 123.4634 | -90.0879 | 33.0505 | 0.2182 | 0.016731 | 0.00093569 | 0.011967 | -0.019339 | 0.001694 | 0.0038345 | -0.065384 | 0.020448 | -0.011713 | 0.012068 | -0.00229 | 0.0095703 | 1.6434 | 1.4008 | 1.3229 | 1.5884 | 1.6342 | 1.4832 | 1.3138 | 33.2062 | 33.2428 | 33.2336 | 33.0688 | 32.9956 | 8.7799 | 8.6838 | 91.571 | 91.4017 | -31.4163 | 91.4886 | 91.6763 | 0.27466 | -31.4072 | 98.8678 | 98.7717 | 0.018311 | 123.2941 | 123.3215 | 24.5499 | -0.054932 | 91.7221 | 91.7313 | 91.4108 | -31.7368 | 123.1567 | 123.0835 | 123.3307 | -24.3668
2451.5156 | 123.4222 | -90.1291 | 33.0597 | 0.19531 | 0.011604 | 0.0039263 | 0.012608 | -0.021048 | 0.0010532 | 0.0014847 | 0.17876 | 0.019593 | -0.014704 | 0.012495 | -0.0025036 | 0.0099975 | 1.6296 | 1.6525 | 1.5427 | 1.6022 | 1.6708 | 1.5335 | 1.3504 | 33.1467 | 33.1879 | 33.1833 | 33.0551 | 32.991 | 8.7753 | 8.6792 | 91.6626 | 91.4795 | -31.3889 | 91.7816 | 91.7313 | 0.25177 | -31.4301 | 98.9044 | 98.8083 | -0.004577 | 123.2758 | 123.3124 | 24.5041 | -0.068664 | 91.7999 | 91.7587 | 91.6718 | -31.7093 | 123.1842 | 123.1201 | 123.317 | -24.3805
2452.5156 | 123.4177 | -90.1657 | 33.0276 | 0.23346 | 0.01844 | 0.0020037 | 0.014317 | -0.020835 | 0.005753 | 0.0021255 | 0.15587 | 0.01938 | -0.010645 | 0.012068 | 0.00070077 | 0.0095703 | 1.5656 | 1.5244 | 1.4374 | 1.5335 | 1.712 | 1.4832 | 1.3184 | 33.0872 | 33.1238 | 33.11 | 33.0643 | 32.9773 | 8.7799 | 8.6746 | 91.6489 | 91.4841 | -31.3156 | 91.6901 | 91.6992 | 0.21515 | -31.4621 | 98.9456 | 98.8403 | 0.036621 | 123.2529 | 123.2758 | 24.4354 | -0.050354 | 91.8777 | 91.7313 | 91.6031 | -31.7093 | 123.23 | 123.143 | 123.2895 | -24.353
2453.5156 | 123.4314 | -90.2206 | 32.9727 | 0.20294 | 0.014168 | 0.0022175 | 0.011754 | -0.017203 | -0.00086945 | 0.0031937 | 0.19402 | 0.017457 | -0.01214 | 0.01399 | -0.0018628 | 0.011707 | 1.5793 | 1.6434 | 1.5381 | 1.5747 | 1.6617 | 1.5106 | 1.3229 | 33.0872 | 33.1512 | 33.1284 | 32.9819 | 32.8995 | 8.7845 | 8.6884 | 91.7313 | 91.5436 | -31.311 | 91.864 | 91.7953 | 0.25177 | -31.3934 | 99.0051 | 98.909 | 0.009156 | 123.3078 | 123.349 | 24.44 | -0.073242 | 91.8823 | 91.7999 | 91.7587 | -31.6498 | 123.2025 | 123.1201 | 123.3719 | -24.2844
2454.5156 | 123.4222 | -90.2756 | 32.9361 | 0.17242 | 0.014168 | 0.0045673 | 0.012822 | -0.01998 | -0.0023648 | 0.0027665 | 0.11772 | 0.018098 | -0.010004 | 0.012922 | -0.0050672 | 0.010638 | 1.561 | 1.5884 | 1.5106 | 1.5518 | 1.68 | 1.5106 | 1.3412 | 32.9956 | 33.0597 | 33.0551 | 32.8995 | 32.872 | 8.7753 | 8.6792 | 91.7862 | 91.6168 | -31.2561 | 91.864 | 91.8274 | 0.21057 | -31.3751 | 99.0509 | 98.9548 | -0.036621 | 123.2712 | 123.3307 | 24.3759 | -0.064087 | 91.9556 | 91.8365 | 91.7862 | -31.5948 | 123.175 | 123.1476 | 123.3353 | -24.2569
2455.5156 | 123.349 | -90.2985 | 32.9544 | 0.10376 | 0.016945 | 0.0026447 | 0.011113 | -0.019126 | 0.0055392 | 0.0053299 | 0.36186 | 0.020662 | -0.010431 | 0.012708 | 0.001128 | 0.0089295 | 1.3229 | 1.7578 | 1.5656 | 1.5656 | 1.712 | 1.4786 | 1.3092 | 32.9269 | 32.9681 | 32.9269 | 32.9636 | 32.8537 | 8.7753 | 8.6838 | 91.777 | 91.6077 | -31.2424 | 92.0563 | 91.864 | 0.25635 | -31.6315 | 99.0738 | 98.9822 | 0.009155 | 123.2254 | 123.2254 | 24.2432 | -0.10071 | 92.0105 | 91.6214 | 91.864 | -31.6452 | 123.262 | 123.1522 | 123.2666 | -24.2706
2456.5156 | 123.3582 | -90.3259 | 32.8995 | -0.010681 | 0.018867 | 0.0037127 | 0.011326 | -0.018271 | 0.0059666 | 0.0053299 | 0.026169 | 0.01938 | -0.010858 | 0.013563 | 0.00091437 | 0.011279 | 1.5518 | 1.5198 | 1.4282 | 1.5289 | 1.6846 | 1.4557 | 1.3092 | 32.8949 | 32.959 | 32.9269 | 32.9224 | 32.8308 | 8.7799 | 8.6792 | 91.7816 | 91.6351 | -31.2149 | 91.8457 | 91.8549 | 0.21973 | -31.3477 | 99.1058 | 99.0051 | 0.022888 | 123.2208 | 123.2529 | 24.2477 | -0.068664 | 92.0105 | 91.8777 | 91.7542 | -31.5903 | 123.2483 | 123.1567 | 123.2849 | -24.2203
2457.5156 | 123.3902 | -90.3946 | 32.8766 | 0.13428 | 0.017799 | 0.0026447 | 0.013035 | -0.015494 | 0.0042576 | 0.0040481 | 0.13298 | 0.021302 | -0.010858 | 0.012708 | -0.00058103 | 0.011279 | 1.4969 | 1.4832 | 1.3779 | 1.4923 | 1.6891 | 1.4603 | 1.2863 | 32.8491 | 32.8857 | 32.8766 | 32.8903 | 32.8125 | 8.7753 | 8.6838 | 91.8549 | 91.6809 | -31.1874 | 91.8777 | 91.8869 | 0.20599 | -31.3797 | 99.1699 | 99.0784 | 0.013733 | 123.2437 | 123.2712 | 24.1928 | -0.064087 | 92.0837 | 91.8915 | 91.7725 | -31.5903 | 123.2849 | 123.2071 | 123.2803 | -24.1928
2458.5156 | 123.3765 | -90.39 | 32.8583 | 0.019836 | 0.017372 | 0.0020037 | 0.012394 | -0.018057 | 0.002335 | 0.0042619 | -0.011978 | 0.02173 | -0.0085086 | 0.012922 | -0.00079463 | 0.010425 | 1.5518 | 1.5427 | 1.4465 | 1.5427 | 1.6708 | 1.4511 | 1.2863 | 32.8583 | 32.9498 | 32.8857 | 32.8583 | 32.8125 | 8.7799 | 8.6792 | 91.8411 | 91.6763 | -31.1874 | 91.9327 | 91.9327 | 0.25635 | -31.3065 | 99.1699 | 99.0692 | 0 | 123.2483 | 123.2758 | 24.2065 | -0.045776 | 92.0609 | 91.9418 | 91.8365 | -31.572 | 123.2483 | 123.2025 | 123.3398 | -24.1791
2459.5156 | 123.317 | -90.4678 | 32.8125 | 0.057983 | 0.019935 | 0.0030719 | 0.013463 | -0.021689 | -1.505e-05 | 0.0038345 | 0.049057 | 0.020234 | -0.010858 | 0.010786 | -0.0018628 | 0.011707 | 1.4648 | 1.4923 | 1.3962 | 1.4969 | 1.6937 | 1.4557 | 1.2772 | 32.7347 | 32.8262 | 32.7942 | 32.8171 | 32.7576 | 8.7845 | 8.6746 | 91.9235 | 91.745 | -31.1188 | 91.9601 | 91.9647 | 0.21973 | -31.3477 | 99.2523 | 99.1425 | 0.004578 | 123.2025 | 123.262 | 24.1196 | -0.054932 | 92.1616 | 91.9327 | 91.864 | -31.5353 | 123.2849 | 123.2254 | 123.2941 | -24.1379
2460.5156 | 123.3948 | -90.4861 | 32.7621 | -0.10986 | 0.015663 | 0.0017901 | 0.012394 | -0.018485 | 0.0010532 | 0.0046891 | -0.15694 | 0.02173 | -0.010645 | 0.013777 | -0.0031446 | 0.011066 | 1.5152 | 1.5472 | 1.442 | 1.5656 | 1.68 | 1.4603 | 1.2863 | 32.7438 | 32.8583 | 32.8125 | 32.753 | 32.7072 | 8.7845 | 8.6792 | 91.9464 | 91.7725 | -31.0822 | 92.0334 | 92.0517 | 0.27924 | -31.2469 | 99.2706 | 99.1653 | -0.009155 | 123.23 | 123.2986 | 24.1333 | -0.054932 | 92.1661 | 92.0013 | 91.9281 | -31.4758 | 123.2391 | 123.1934 | 123.3444 | -24.0829
2461.5156 | 123.3719 | -90.5365 | 32.7301 | 0.042725 | 0.01844 | 0.0039263 | 0.01389 | -0.016989 | 0.002335 | 0.0042619 | -0.011978 | 0.021089 | -0.010645 | 0.013349 | -0.0014356 | 0.012134 | 1.5244 | 1.5472 | 1.4374 | 1.5381 | 1.6708 | 1.4603 | 1.2817 | 32.7118 | 32.8125 | 32.753 | 32.7438 | 32.6706 | 8.7708 | 8.6792 | 91.9968 | 91.8182 | -31.0593 | 92.0837 | 92.0746 | 0.25635 | -31.2057 | 99.3073 | 99.2157 | 0.013732 | 123.2483 | 123.2895 | 24.0738 | -0.05951 | 92.2073 | 92.0609 | 91.9739 | -31.4484 | 123.2803 | 123.2071 | 123.349 | -24.0509
2462.5156 | 123.3444 | -90.5869 | 32.6935 | -0.1709 | 0.013527 | 0.0032855 | 0.013676 | -0.020194 | -0.0036464 | 0.00041648 | 0.96458 | 0.019593 | -0.011072 | 0.01164 | -0.0054944 | 0.013629 | 1.4511 | 1.5106 | 1.3916 | 1.5015 | 1.7075 | 1.4511 | 1.2817 | 32.6019 | 32.7576 | 32.6889 | 32.6981 | 32.6202 | 8.7845 | 8.6746 | 92.038 | 91.8686 | -30.986 | 92.0975 | 92.0883 | 0.21973 | -31.2424 | 99.3713 | 99.2615 | 0.004578 | 123.1888 | 123.2758 | 24.0143 | -0.073242 | 92.2943 | 92.038 | 91.9785 | -31.4117 | 123.2849 | 123.2071 | 123.3444 | -24.0189
2463.5156 | 123.3444 | -90.596 | 32.666 | -0.14038 | 0.018013 | 0.0022175 | 0.014103 | -0.019553 | 0.0038304 | 0.0019119 | -0.011978 | 0.01938 | -0.010858 | 0.013136 | -0.0027172 | 0.01192 | 1.5198 | 1.5564 | 1.442 | 1.5472 | 1.6846 | 1.4465 | 1.2726 | 32.6202 | 32.7484 | 32.6797 | 32.634 | 32.579 | 8.7753 | 8.6838 | 92.0425 | 91.8686 | -30.9814 | 92.1524 | 92.1432 | 0.27466 | -31.1462 | 99.3713 | 99.2798 | -0.032044 | 123.2162 | 123.2758 | 23.996 | -0.086975 | 92.2806 | 92.1158 | 92.038 | -31.3934 | 123.23 | 123.175 | 123.3444 | -23.9822
2464.5156 | 123.3719 | -90.6647 | 32.6019 | -0.12512 | 0.014381 | 0.0047809 | 0.011113 | -0.018057 | 0.0010532 | 0.00041648 | -0.10353 | 0.018953 | -0.01214 | 0.015272 | -0.0025036 | 0.011707 | 1.4511 | 1.5244 | 1.4145 | 1.5198 | 1.7075 | 1.442 | 1.2726 | 32.515 | 32.6523 | 32.6294 | 32.6248 | 32.5287 | 8.7799 | 8.6838 | 92.1066 | 91.9373 | -30.8945 | 92.189 | 92.1844 | 0.24719 | -31.1508 | 99.4446 | 99.3484 | 0.022888 | 123.1796 | 123.2941 | 23.9456 | -0.073242 | 92.3721 | 92.1158 | 92.0792 | -31.3293 | 123.2895 | 123.1934 | 123.317 | -23.9182
2465.5156 | 123.4085 | -90.7288 | 32.5333 | -0.17853 | 0.019722 | 0.0017901 | 0.011326 | -0.018485 | 0.0014804 | 0.0019119 | -0.095902 | 0.017884 | -0.0097904 | 0.012495 | -0.0035718 | 0.011707 | 1.4877 | 1.5472 | 1.4236 | 1.5472 | 1.6846 | 1.4511 | 1.2772 | 32.5104 | 32.6386 | 32.5928 | 32.5333 | 32.4738 | 8.7753 | 8.6838 | 92.1799 | 92.0059 | -30.8487 | 92.276 | 92.276 | 0.27008 | -31.0455 | 99.5041 | 99.4125 | 0 | 123.2391 | 123.3215 | 23.909 | -0.059509 | 92.4133 | 92.2165 | 92.1524 | -31.2561 | 123.262 | 123.2025 | 123.3673 | -23.8495
2466.5156 | 123.2849 | -90.715 | 32.5745 | -0.1709 | 0.011177 | 0.0037127 | 0.013035 | -0.018271 | -0.0036464 | 0.0016983 | -0.15694 | 0.018312 | -0.011286 | 0.01399 | -0.0054944 | 0.012561 | 1.4374 | 1.5427 | 1.4099 | 1.5289 | 1.6891 | 1.4511 | 1.2863 | 32.4463 | 32.5699 | 32.5378 | 32.5424 | 32.4646 | 8.7845 | 8.6746 | 92.1661 | 92.0013 | -30.8853 | 92.2577 | 92.244 | 0.24262 | -31.1371 | 99.4995 | 99.3896 | -0.032044 | 123.1613 | 123.2529 | 23.8632 | -0.10986 | 92.4042 | 92.1524 | 92.1249 | -31.2881 | 123.2574 | 123.1796 | 123.2849 | -23.8998
2467.5156 | 123.381 | -90.8112 | 32.4463 | -0.18616 | 0.014381 | 0.0026447 | 0.014958 | -0.01998 | 0.00019875 | 0.0021255 | -0.14931 | 0.020448 | -0.0078678 | 0.012708 | -0.0027172 | 0.0095703 | 1.4648 | 1.5106 | 1.3962 | 1.5106 | 1.6846 | 1.442 | 1.2817 | 32.3959 | 32.5287 | 32.4829 | 32.4783 | 32.3959 | 8.7799 | 8.6792 | 92.2531 | 92.0929 | -30.7617 | 92.3218 | 92.3218 | 0.22888 | -30.9814 | 99.5911 | 99.4904 | 0.032044 | 123.2071 | 123.2941 | 23.8037 | -0.050354 | 92.4957 | 92.276 | 92.2073 | -31.1646 | 123.2895 | 123.2071 | 123.3398 | -23.7671
2468.5156 | 123.4406 | -90.8203 | 32.4097 | -0.15564 | 0.010109 | 0.0039263 | 0.012394 | -0.01998 | -0.0034328 | 0.00041648 | -0.10353 | 0.016816 | -0.012354 | 0.012922 | -0.0035718 | 0.010852 | 1.5198 | 1.6296 | 1.506 | 1.593 | 1.68 | 1.4648 | 1.2955 | 32.3822 | 32.5378 | 32.4921 | 32.3822 | 32.3273 | 8.7799 | 8.6838 | 92.2852 | 92.1158 | -30.7297 | 92.45 | 92.4133 | 0.29755 | -30.8899 | 99.6002 | 99.5041 | -0.027466 | 123.2025 | 123.3124 | 23.8083 | -0.082397 | 92.5003 | 92.3401 | 92.3264 | -31.1142 | 123.2025 | 123.1476 | 123.3582 | -23.7259
2469.5156 | 123.3673 | -90.8569 | 32.4188 | -0.20905 | 0.013527 | 0.0062763 | 0.013035 | -0.018057 | -0.0023648 | -0.00043792 | -0.12642 | 0.018312 | -0.0091494 | 0.015272 | -0.006776 | 0.010211 | 1.5015 | 1.5884 | 1.4648 | 1.5656 | 1.6663 | 1.4648 | 1.2909 | 32.341 | 32.4783 | 32.4509 | 32.4142 | 32.3318 | 8.7799 | 8.6792 | 92.3218 | 92.1478 | -30.7526 | 92.4454 | 92.4225 | 0.27466 | -30.9174 | 99.6368 | 99.5361 | -0.004577 | 123.1979 | 123.3078 | 23.7717 | -0.086975 | 92.5232 | 92.3584 | 92.3218 | -31.1279 | 123.2712 | 123.1888 | 123.3353 | -23.7396
2470.5156 | 123.4222 | -90.8798 | 32.3181 | -0.12512 | 0.0090405 | 0.0037127 | 0.010258 | -0.019339 | -0.0021512 | 0.00084388 | -0.15694 | 0.017457 | -0.012995 | 0.013136 | -0.0050672 | 0.013202 | 1.5381 | 1.6434 | 1.5106 | 1.5656 | 1.6708 | 1.4786 | 1.3046 | 32.3273 | 32.4738 | 32.4371 | 32.3364 | 32.2403 | 8.7799 | 8.6838 | 92.3584 | 92.1844 | -30.6473 | 92.5232 | 92.4454 | 0.26093 | -30.78 | 99.6597 | 99.5636 | 0.018311 | 123.2071 | 123.317 | 23.7534 | -0.07782 | 92.5507 | 92.4179 | 92.3904 | -31.0135 | 123.2162 | 123.1201 | 123.3536 | -23.6343
2471.5156 | 123.3719 | -90.9714 | 32.2815 | -0.18616 | 0.014381 | 0.0047809 | 0.015599 | -0.021689 | 0.00083955 | -0.00022432 | -1.6065 | 0.020234 | -0.01214 | 0.012922 | -0.0027172 | 0.011279 | 1.4557 | 1.5106 | 1.3916 | 1.506 | 1.6846 | 1.4328 | 1.2543 | 32.2266 | 32.3135 | 32.2998 | 32.3364 | 32.2037 | 8.7891 | 8.6792 | 92.4042 | 92.2256 | -30.5969 | 92.482 | 92.4774 | 0.25177 | -30.8258 | 99.7604 | 99.6506 | 0.054932 | 123.1979 | 123.2712 | 23.6206 | -0.07782 | 92.6559 | 92.4271 | 92.363 | -31.0272 | 123.3078 | 123.175 | 123.2849 | -23.6023
2472.5156 | 123.4863 | -90.9576 | 32.2266 | -0.12512 | 0.011177 | 0.0041401 | 0.01154 | -0.01998 | -0.0034328 | 0.0016983 | 0.18639 | 0.018098 | -0.014276 | 0.011854 | -0.0044262 | 0.011066 | 1.3962 | 1.6022 | 1.5427 | 1.6067 | 1.6296 | 1.442 | 1.3 | 32.2952 | 32.4326 | 32.4051 | 32.2128 | 32.1487 | 8.7799 | 8.6838 | 92.3996 | 92.2577 | -30.5969 | 92.5598 | 92.5644 | 0.3067 | -30.8304 | 99.7375 | 99.6414 | -0.013732 | 123.2529 | 123.3627 | 23.7213 | -0.077819 | 92.5873 | 92.3538 | 92.5003 | -30.9265 | 123.1705 | 123.1064 | 123.3902 | -23.5428
2473.5156 | 123.3673 | -91.0584 | 32.2037 | -0.17853 | 0.01139 | 0.0011493 | 0.01154 | -0.020407 | -0.0023648 | 0.0036209 | -0.14168 | 0.017244 | -0.012995 | 0.012708 | -0.0031446 | 0.011493 | 1.5198 | 1.5976 | 1.4603 | 1.5518 | 1.68 | 1.474 | 1.2863 | 32.1762 | 32.2769 | 32.2495 | 32.1991 | 32.1213 | 8.7891 | 8.6838 | 92.5323 | 92.3447 | -30.5237 | 92.6559 | 92.6102 | 0.2655 | -30.6839 | 99.8474 | 99.7421 | -0.004577 | 123.2346 | 123.3078 | 23.5657 | -0.082397 | 92.7383 | 92.5781 | 92.5186 | -30.9174 | 123.2574 | 123.1796 | 123.3353 | -23.5199
2474.5156 | 123.5138 | -91.0629 | 32.1121 | 0.012207 | 0.0096813 | 0.0039263 | 0.013035 | -0.019126 | -0.0019376 | -0.00086512 | -0.080643 | 0.015748 | -0.013422 | 0.013349 | -0.0052808 | 0.011066 | 1.5427 | 1.6342 | 1.5244 | 1.5747 | 1.6663 | 1.4603 | 1.3184 | 32.2311 | 32.3502 | 32.3181 | 32.1304 | 32.0435 | 8.7708 | 8.6838 | 92.5232 | 92.3813 | -30.4459 | 92.6971 | 92.6376 | 0.25635 | -30.5695 | 99.8337 | 99.7467 | 0.01831 | 123.2941 | 123.381 | 23.6343 | -0.068665 | 92.7292 | 92.6056 | 92.5873 | -30.7938 | 123.1934 | 123.1064 | 123.4131 | -23.4283
2475.5156 | 123.4406 | -91.0767 | 32.1167 | -0.16327 | 0.010322 | 0.0037127 | 0.013463 | -0.019126 | -0.00065585 | 0.0021255 | -0.14931 | 0.015962 | -0.012781 | 0.012068 | -0.0035718 | 0.010638 | 1.5564 | 1.6571 | 1.5244 | 1.5747 | 1.6708 | 1.474 | 1.3184 | 32.1991 | 32.3135 | 32.2723 | 32.1167 | 32.048 | 8.7845 | 8.6884 | 92.5507 | 92.395 | -30.4459 | 92.7338 | 92.6514 | 0.25635 | -30.5603 | 99.8611 | 99.765 | 0 | 123.2758 | 123.349 | 23.584 | -0.068664 | 92.7475 | 92.6331 | 92.601 | -30.7983 | 123.1934 | 123.1247 | 123.3902 | -23.4283
2476.5156 | 123.4268 | -91.0492 | 32.1259 | 0.088501 | 0.0079723 | 0.0017901 | 0.01154 | -0.01998 | -0.0034328 | -0.0012923 | -0.27901 | 0.017457 | -0.010858 | 0.012922 | -0.0029308 | 0.0097839 | 1.4008 | 1.442 | 1.3916 | 1.4557 | 1.6067 | 1.4191 | 1.268 | 32.1625 | 32.254 | 32.2678 | 32.1442 | 32.0435 | 8.7799 | 8.6746 | 92.4683 | 92.3172 | -30.5191 | 92.4912 | 92.5049 | 0.18768 | -30.7251 | 99.8291 | 99.7238 | 0.018311 | 123.2117 | 123.317 | 23.5931 | -0.082397 | 92.6559 | 92.45 | 92.4408 | -30.8578 | 123.1934 | 123.0927 | 123.3032 | -23.4512
2477.5156 | 123.436 | -91.0492 | 32.1396 | -0.16327 | 0.010536 | 0.0039263 | 0.012608 | -0.019766 | -0.00022865 | -0.00065152 | -0.15694 | 0.017884 | -0.011499 | 0.012708 | -0.0054944 | 0.0099975 | 1.5793 | 1.6479 | 1.5244 | 1.5839 | 1.6571 | 1.4832 | 1.3138 | 32.1945 | 32.3181 | 32.2769 | 32.1396 | 32.0572 | 8.7799 | 8.6838 | 92.5323 | 92.363 | -30.4825 | 92.6971 | 92.6331 | 0.27008 | -30.5603 | 99.8291 | 99.733 | 0 | 123.2437 | 123.3261 | 23.5931 | -0.082397 | 92.7063 | 92.6285 | 92.5735 | -30.8258 | 123.1888 | 123.1064 | 123.3673 | -23.4558
2478.5156 | 123.4543 | -91.1407 | 32.0526 | 0.042725 | 0.0081861 | 0.0026447 | 0.012181 | -0.018698 | -0.00086945 | 0.00041648 | -0.0043486 | 0.016389 | -0.013208 | 0.012708 | -0.0033582 | 0.0099975 | 1.5152 | 1.593 | 1.4786 | 1.561 | 1.6663 | 1.4694 | 1.3092 | 32.1213 | 32.2037 | 32.1991 | 32.0663 | 31.9839 | 8.7845 | 8.6792 | 92.6102 | 92.45 | -30.3864 | 92.7338 | 92.7017 | 0.25177 | -30.5374 | 99.9252 | 99.8199 | 0.013733 | 123.262 | 123.3398 | 23.5199 | -0.068664 | 92.807 | 92.6559 | 92.6193 | -30.7434 | 123.2071 | 123.1247 | 123.3444 | -23.3734
2479.5156 | 123.4772 | -91.1774 | 32.0068 | -0.033569 | 0.0096813 | 0.0062763 | 0.012608 | -0.021689 | 0.00062595 | -0.00022432 | -0.12642 | 0.017671 | -0.013422 | 0.011427 | -0.0078442 | 0.010211 | 1.5884 | 1.6891 | 1.5427 | 1.5839 | 1.6434 | 1.4832 | 1.2909 | 32.2266 | 31.8008 | 32.1808 | 32.0068 | 31.9336 | 8.7799 | 8.6838 | 92.6605 | 92.4683 | -30.3635 | 92.8665 | 92.7612 | 0.29297 | -30.4184 | 99.9573 | 99.8611 | 0 | 123.4039 | 123.3582 | 23.497 | -0.073242 | 92.8207 | 92.7658 | 92.72 | -30.7159 | 123.1842 | 123.111 | 122.9782 | -23.3231
2480.5156 | 123.436 | -91.214 | 31.9611 | 0.14954 | 0.0098951 | 0.0043537 | 0.012822 | -0.021475 | 0.0010532 | 0.0021255 | -0.23323 | 0.018312 | -0.013422 | 0.012708 | -0.0027172 | 0.01192 | 1.4969 | 1.5747 | 1.4603 | 1.4008 | 1.6205 | 1.4465 | 1.2451 | 31.9977 | 32.0709 | 32.0755 | 31.9977 | 31.9016 | 8.7799 | 8.6792 | 92.6605 | 92.4591 | -30.3406 | 92.7887 | 92.6147 | 0.15564 | -30.4642 | 99.9939 | 99.8932 | 0.036621 | 123.2117 | 123.2895 | 23.3963 | -0.05951 | 92.8345 | 92.7109 | 92.6743 | -30.7159 | 123.2117 | 123.1155 | 123.2849 | -23.2819
2481.5156 | 123.4772 | -91.2506 | 31.9382 | 0.027466 | 0.0092541 | 0.0030719 | 0.014317 | -0.020835 | 0.00019875 | 0.00041648 | -0.027237 | 0.019166 | -0.013849 | 0.011213 | -0.0052808 | 0.0089295 | 1.5427 | 1.6159 | 1.4969 | 1.5701 | 1.6525 | 1.4923 | 1.3 | 32.0343 | 32.135 | 32.1075 | 31.9427 | 31.8787 | 8.7799 | 8.6746 | 92.7429 | 92.5507 | -30.2856 | 92.8665 | 92.8207 | 0.27008 | -30.3955 | 100.0305 | 99.9252 | 0.004578 | 123.2849 | 123.3582 | 23.4329 | -0.059509 | 92.9031 | 92.7933 | 92.7475 | -30.6381 | 123.1934 | 123.1293 | 123.3856 | -23.2635
2482.5156 | 123.4085 | -91.2964 | 31.8832 | 0.17242 | 0.012459 | 0.0032855 | 0.012608 | -0.019339 | -0.00044225 | 0.00084388 | 0.18639 | 0.017457 | -0.009363 | 0.010359 | -0.0054944 | 0.0097839 | 1.5472 | 1.6067 | 1.4694 | 1.5198 | 1.6296 | 1.4694 | 1.3046 | 31.9611 | 32.0251 | 32.0023 | 31.9016 | 31.8054 | 8.7799 | 8.6838 | 92.7658 | 92.601 | -30.2536 | 92.9031 | 92.8162 | 0.21515 | -30.336 | 100.0763 | 99.9802 | 0.01831 | 123.2574 | 123.2986 | 23.3185 | -0.07782 | 92.926 | 92.8436 | 92.7658 | -30.5786 | 123.1979 | 123.1018 | 123.3215 | -23.1995
2483.5156 | 123.4406 | -91.333 | 31.8329 | -0.28534 | 0.0094677 | 0.0024311 | 0.013249 | -0.020835 | -1.505e-05 | 0.0021255 | 0.018539 | 0.018739 | -0.015345 | 0.011427 | -0.0033582 | 0.0099975 | 1.4923 | 1.5381 | 1.4557 | 1.5152 | 1.6434 | 1.4328 | 1.2589 | 31.9107 | 31.9885 | 31.9931 | 31.8878 | 31.7871 | 8.7799 | 8.6838 | 92.7658 | 92.5919 | -30.1895 | 92.8711 | 92.8482 | 0.25635 | -30.3406 | 100.1129 | 100.0168 | 0.054931 | 123.2437 | 123.3261 | 23.3093 | -0.045777 | 92.9764 | 92.8253 | 92.7887 | -30.574 | 123.2208 | 123.1201 | 123.3215 | -23.1491
2484.5156 | 123.4177 | -91.3925 | 31.8237 | 0.16479 | 0.01374 | 0.0030719 | 0.013035 | -0.022757 | 0.002335 | 0.0016983 | 0.1635 | 0.019166 | -0.013849 | 0.011213 | -0.0020764 | 0.010852 | 1.561 | 1.5976 | 1.4832 | 1.5335 | 1.6342 | 1.4603 | 1.2817 | 31.8878 | 31.9427 | 31.9336 | 31.81 | 31.7459 | 8.7891 | 8.6746 | 92.8528 | 92.6743 | -30.1895 | 92.9901 | 92.926 | 0.25177 | -30.2628 | 100.1816 | 100.0671 | -0.013732 | 123.2803 | 123.3261 | 23.259 | -0.077819 | 93.0267 | 92.9535 | 92.8757 | -30.542 | 123.2025 | 123.1384 | 123.3353 | -23.1491
2485.5156 | 123.4085 | -91.4108 | 31.778 | -0.41504 | 0.0079723 | 0.0022175 | 0.014317 | -0.020621 | -0.00022865 | 0.00041648 | 0.033798 | 0.018312 | -0.012781 | 0.01164 | -0.0010082 | 0.0099975 | 1.4923 | 1.5427 | 1.4328 | 1.5106 | 1.6113 | 1.4282 | 1.2589 | 31.8283 | 31.9199 | 31.9244 | 31.81 | 31.6956 | 8.7799 | 8.6838 | 92.8391 | 92.6697 | -30.1666 | 92.9535 | 92.9214 | 0.25177 | -30.2856 | 100.1907 | 100.0946 | 0.032044 | 123.2391 | 123.3353 | 23.2407 | -0.082397 | 93.0222 | 92.9031 | 92.8436 | -30.5191 | 123.2208 | 123.1064 | 123.3307 | -23.0942
2486.5156 | 123.4543 | -91.5024 | 31.6818 | 0.18768 | 0.014381 | 0.0039263 | 0.01154 | -0.022116 | 0.004044 | 0.0044755 | 0.14061 | 0.019807 | -0.010645 | 0.010786 | -0.0014356 | 0.0091431 | 1.561 | 1.593 | 1.474 | 1.5335 | 1.5976 | 1.442 | 1.2909 | 31.8329 | 31.8512 | 31.8695 | 31.7047 | 31.6177 | 8.7845 | 8.6746 | 92.9443 | 92.7933 | -30.0842 | 93.0954 | 93.0359 | 0.24261 | -30.1208 | 100.2869 | 100.177 | 0.022888 | 123.3353 | 123.3719 | 23.1949 | -0.064087 | 93.1 | 93.0634 | 92.9764 | -30.3909 | 123.2071 | 123.1201 | 123.3536 | -23.0072
2487.5156 | 123.4314 | -91.5024 | 31.691 | 0.15717 | 0.0096813 | 0.0041401 | 0.011967 | -0.019126 | 0.00062595 | 0.0025529 | 0.14824 | 0.01938 | -0.011713 | 0.012068 | -0.0048534 | 0.0076477 | 1.5198 | 1.561 | 1.4603 | 1.4969 | 1.6296 | 1.4511 | 1.2772 | 31.7688 | 31.8054 | 31.8237 | 31.7093 | 31.6315 | 8.7845 | 8.6792 | 92.9535 | 92.7795 | -30.0613 | 93.0634 | 92.9993 | 0.21973 | -30.1712 | 100.2869 | 100.1816 | 0.018311 | 123.2712 | 123.3261 | 23.1445 | -0.059509 | 93.132 | 93.0222 | 92.9626 | -30.4138 | 123.2117 | 123.1338 | 123.3078 | -23.0118
2488.5156 | 123.4634 | -91.5207 | 31.6223 | 0.042725 | 0.014808 | 0.00093569 | 0.012394 | -0.019766 | 0.0014804 | 0.0014847 | 0.20927 | 0.01938 | -0.012567 | 0.012495 | -0.0025036 | 0.0089295 | 1.5701 | 1.5747 | 1.474 | 1.5289 | 1.6067 | 1.442 | 1.2863 | 31.7688 | 31.8283 | 31.8008 | 31.6589 | 31.5811 | 8.7845 | 8.6792 | 92.9626 | 92.807 | -30.0156 | 93.0954 | 93.0496 | 0.24262 | -30.0522 | 100.3052 | 100.1999 | 0.036622 | 123.2895 | 123.3215 | 23.1216 | -0.041198 | 93.1274 | 93.0908 | 92.9947 | -30.336 | 123.1796 | 123.1018 | 123.349 | -22.9431
2489.5156 | 123.4497 | -91.5344 | 31.636 | 0.18005 | 0.012672 | 0.0037127 | 0.012608 | -0.019339 | 0.0019078 | 0.0034073 | 0.15587 | 0.020234 | -0.012354 | 0.01164 | -0.0037854 | 0.011493 | 1.5472 | 1.5839 | 1.4786 | 1.5289 | 1.6159 | 1.4465 | 1.2863 | 31.7505 | 31.7963 | 31.7825 | 31.6132 | 31.5674 | 8.7891 | 8.6792 | 92.981 | 92.8207 | -30.0201 | 93.1183 | 93.0634 | 0.24262 | -30.0888 | 100.3235 | 100.2136 | -0.022888 | 123.2849 | 123.317 | 23.1033 | -0.068664 | 93.1503 | 93.0817 | 93.013 | -30.3497 | 123.1476 | 123.1018 | 123.3307 | -22.9568
2490.5156 | 123.4085 | -91.6351 | 31.5628 | 0.19531 | 0.017158 | 0.0020037 | 0.013249 | -0.019766 | 0.0048984 | 0.0042619 | 0.14824 | 0.022798 | -0.011927 | 0.010786 | -0.0020764 | 0.0089295 | 1.4877 | 1.442 | 1.3458 | 1.4557 | 1.6434 | 1.4145 | 1.2405 | 31.6132 | 31.6498 | 31.6406 | 31.6177 | 31.517 | 8.7753 | 8.6884 | 93.0496 | 92.8757 | -29.9194 | 93.0771 | 93.0908 | 0.21515 | -30.0751 | 100.4105 | 100.3235 | 0.054932 | 123.2483 | 123.2758 | 22.9523 | -0.045776 | 93.2785 | 93.1229 | 92.981 | -30.3223 | 123.2529 | 123.1522 | 123.2849 | -22.8745
2491.5156 | 123.4772 | -91.6122 | 31.5537 | 0.20294 | 0.015022 | 0.0026447 | 0.010472 | -0.020407 | 0.002335 | 0.0044755 | 0.56023 | 0.018525 | -0.012354 | 0.012495 | -0.0014356 | 0.010211 | 1.561 | 1.5884 | 1.4557 | 1.4832 | 1.6022 | 1.4374 | 1.2589 | 31.6589 | 31.7688 | 31.7093 | 31.5308 | 31.4987 | 8.7799 | 8.6838 | 93.0496 | 92.8711 | -29.9515 | 93.2007 | 93.0954 | 0.2243 | -29.9927 | 100.3922 | 100.296 | -0.022888 | 123.2712 | 123.3215 | 23.0255 | -0.054932 | 93.2144 | 93.1732 | 93.0679 | -30.2948 | 123.143 | 123.111 | 123.381 | -22.8699
2492.5156 | 123.4039 | -91.7496 | 31.485 | 0.18768 | 0.016731 | 0.0034991 | 0.012822 | -0.019339 | 0.0042576 | 0.0042619 | 0.15587 | 0.02173 | -0.010004 | 0.012068 | -0.00058103 | 0.010425 | 1.4832 | 1.4465 | 1.355 | 1.4557 | 1.6342 | 1.4099 | 1.2222 | 31.5125 | 31.5537 | 31.5445 | 31.485 | 31.4209 | 8.7753 | 8.6746 | 93.1595 | 92.9718 | -29.8508 | 93.1961 | 93.2053 | 0.23346 | -30.0018 | 100.5249 | 100.4242 | 0 | 123.262 | 123.2941 | 22.8699 | -0.064087 | 93.3838 | 93.2327 | 93.1046 | -30.2628 | 123.2346 | 123.1705 | 123.3032 | -22.8104
2493.5156 | 123.4406 | -91.777 | 31.4438 | 0.088501 | 0.0081861 | 0.0064899 | 0.0085492 | -0.020407 | -0.0030056 | 0.0031937 | 0.11772 | 0.020234 | -0.011927 | 0.015058 | -0.0037854 | 0.011707 | 1.4191 | 1.5198 | 1.4145 | 1.4786 | 1.561 | 1.387 | 1.2314 | 31.4758 | 31.5811 | 31.572 | 31.4484 | 31.3705 | 8.7753 | 8.6792 | 93.1641 | 93.0084 | -29.8828 | 93.2968 | 93.2556 | 0.24719 | -30.0247 | 100.5524 | 100.4562 | 0.004577 | 123.2529 | 123.349 | 22.8928 | -0.073243 | 93.338 | 93.1961 | 93.1915 | -30.2124 | 123.2254 | 123.1476 | 123.3582 | -22.7646
2494.5156 | 123.3673 | -91.8961 | 31.3202 | -2.4673 | 0.016517 | 0.00072209 | 0.016026 | -0.019339 | 0.005753 | 0.0051163 | 0.12535 | 0.019593 | -0.011072 | 0.013777 | -0.00036743 | 0.0085021 | 1.442 | 1.442 | 1.3229 | 1.4374 | 1.6388 | 1.3962 | 1.236 | 31.3339 | 31.366 | 31.366 | 31.4026 | 31.3019 | 8.7753 | 8.6838 | 93.2922 | 93.132 | -29.6814 | 93.338 | 93.3334 | 0.20142 | -29.8782 | 100.6714 | 100.5798 | 0.082398 | 123.23 | 123.262 | 22.6822 | -0.01831 | 93.5349 | 93.338 | 93.219 | -30.0842 | 123.2986 | 123.1979 | 123.262 | -22.6364
2495.5156 | 123.4451 | -91.8732 | 31.3156 | 0.22583 | 0.017372 | 0.0028583 | 0.011326 | -0.017417 | 0.0025486 | 0.0038345 | 0.20927 | 0.02173 | -0.010218 | 0.012281 | -0.0020764 | 0.012347 | 1.4969 | 1.4877 | 1.387 | 1.4786 | 1.6159 | 1.4053 | 1.236 | 31.3843 | 31.4529 | 31.4575 | 31.3202 | 31.2653 | 8.7799 | 8.6792 | 93.2785 | 93.1091 | -29.6997 | 93.3609 | 93.3517 | 0.24262 | -29.8187 | 100.6531 | 100.5524 | 0.004577 | 123.2574 | 123.3307 | 22.7783 | -0.050354 | 93.4891 | 93.3701 | 93.2602 | -30.0797 | 123.1934 | 123.1384 | 123.3261 | -22.6364
2496.5156 | 123.3444 | -91.9373 | 31.3156 | 0.027466 | 0.019508 | 0.0039263 | 0.014103 | -0.017844 | 0.004044 | 0.0029801 | -0.0043486 | 0.02173 | -0.012567 | 0.015058 | -0.0012218 | 0.0076477 | 1.4694 | 1.442 | 1.3641 | 1.4557 | 1.6159 | 1.3916 | 1.2268 | 31.2836 | 31.3614 | 31.3385 | 31.3156 | 31.2561 | 8.7845 | 8.6838 | 93.3289 | 93.1641 | -29.6997 | 93.3792 | 93.3929 | 0.22888 | -29.8462 | 100.7217 | 100.621 | 0 | 123.2208 | 123.2758 | 22.6547 | -0.059509 | 93.5532 | 93.4067 | 93.3014 | -30.0888 | 123.2529 | 123.1934 | 123.2986 | -22.6318
2497.5156 | 123.468 | -91.951 | 31.2286 | 0.23346 | 0.014808 | 0.0020037 | 0.00919 | -0.019553 | -0.00022865 | 0.0038345 | 0.15587 | 0.020875 | -0.010645 | 0.013349 | -0.0010082 | 0.011279 | 1.4877 | 1.5106 | 1.4099 | 1.5152 | 1.6067 | 1.4191 | 1.2451 | 31.3202 | 31.4026 | 31.4026 | 31.2332 | 31.1783 | 8.7845 | 8.6838 | 93.3701 | 93.1961 | -29.6219 | 93.4616 | 93.4662 | 0.27008 | -29.7409 | 100.7355 | 100.6348 | 0.004577 | 123.2712 | 123.3536 | 22.7188 | -0.050354 | 93.5577 | 93.4387 | 93.3609 | -29.9835 | 123.1842 | 123.1293 | 123.3536 | -22.5449
2498.5156 | 123.4268 | -91.9968 | 31.2057 | 0.22583 | 0.011177 | 0.0032855 | 0.01154 | -0.020835 | -0.001083 | 0.0038345 | 0.27794 | 0.018525 | -0.014063 | 0.012281 | -0.0046398 | 0.012134 | 1.5152 | 1.5564 | 1.4557 | 1.5106 | 1.5793 | 1.4374 | 1.2589 | 31.2927 | 31.366 | 31.3705 | 31.2057 | 31.16 | 8.7845 | 8.6792 | 93.4341 | 93.2556 | -29.6265 | 93.5532 | 93.5074 | 0.25177 | -29.6906 | 100.7812 | 100.676 | 0 | 123.2895 | 123.3673 | 22.6913 | -0.045777 | 93.576 | 93.512 | 93.4525 | -29.9469 | 123.2025 | 123.1567 | 123.3627 | -22.5266
2499.5156 | 123.4222 | -92.0563 | 31.1508 | 0.20294 | 0.016945 | 0.0037127 | 0.012181 | -0.01998 | 0.0029758 | 0.0044755 | 0.17876 | 0.020448 | -0.0097904 | 0.012068 | -0.0025036 | 0.010425 | 1.4557 | 1.4236 | 1.355 | 1.4557 | 1.6388 | 1.4008 | 1.236 | 31.192 | 31.2424 | 31.2607 | 31.2012 | 31.1096 | 8.7799 | 8.6838 | 93.457 | 93.2922 | -29.512 | 93.4799 | 93.512 | 0.21973 | -29.6951 | 100.8362 | 100.7401 | 0.050354 | 123.2483 | 123.317 | 22.5769 | -0.041199 | 93.6951 | 93.512 | 93.4113 | -29.9149 | 123.2574 | 123.1659 | 123.2986 | -22.467
2500.5156 | 123.349 | -92.0975 | 31.1691 | 0.057983 | 0.020149 | 0.0020037 | 0.016453 | -0.019339 | 0.003403 | 0.0038345 | 0.026169 | 0.02173 | -0.0089358 | 0.012495 | -0.00079463 | 0.0085021 | 1.4282 | 1.4053 | 1.3184 | 1.4511 | 1.6022 | 1.3824 | 1.2222 | 31.0959 | 31.1874 | 31.16 | 31.1737 | 31.1234 | 8.7799 | 8.6838 | 93.4799 | 93.3197 | -29.567 | 93.5028 | 93.5486 | 0.22888 | -29.7409 | 100.8774 | 100.7812 | 0.004578 | 123.1934 | 123.2574 | 22.4762 | -0.045776 | 93.6996 | 93.5257 | 93.4158 | -29.9469 | 123.2712 | 123.2208 | 123.2849 | -22.4854
2501.5156 | 123.3765 | -92.1616 | 31.0913 | 0.18768 | 0.016945 | 0.0017901 | 0.013676 | -0.018485 | 0.0025486 | 0.0025529 | 0.1635 | 0.021516 | -0.010645 | 0.013563 | -0.0035718 | 0.012988 | 1.4282 | 1.4145 | 1.3367 | 1.4328 | 1.6388 | 1.3824 | 1.2268 | 31.073 | 31.1234 | 31.1417 | 31.1279 | 31.0455 | 8.7753 | 8.6792 | 93.544 | 93.3884 | -29.4525 | 93.576 | 93.5944 | 0.20599 | -29.6631 | 100.9369 | 100.8408 | 0.036621 | 123.2346 | 123.3032 | 22.4625 | -0.045777 | 93.8004 | 93.5898 | 93.4982 | -29.8645 | 123.2895 | 123.2071 | 123.2849 | -22.4121
2502.5156 | 123.3719 | -92.1936 | 31.0913 | 0.019836 | 0.019508 | 0.0037127 | 0.013463 | -0.019553 | 0.0036166 | 0.0040481 | -0.0043486 | 0.020875 | -0.0091494 | 0.013349 | -0.0025036 | 0.010638 | 1.4603 | 1.4374 | 1.3412 | 1.4557 | 1.6113 | 1.3779 | 1.2268 | 31.041 | 31.1234 | 31.1005 | 31.0867 | 31.0226 | 8.7753 | 8.6746 | 93.5715 | 93.4204 | -29.48 | 93.631 | 93.6493 | 0.22888 | -29.631 | 100.9689 | 100.8682 | -0.004578 | 123.2346 | 123.2941 | 22.4258 | -0.068665 | 93.8049 | 93.6539 | 93.5349 | -29.8645 | 123.2803 | 123.2162 | 123.317 | -22.4167
2503.5312 | 123.468 | -92.1753 | 31.0043 | -0.048828 | 0.0092541 | 0.0058491 | 0.008122 | -0.020621 | -0.008987 | 0.0014847 | -0.042496 | 0.018098 | -0.01449 | 0.0069406 | -0.0050672 | 0.014484 | 1.5198 | 1.6113 | 1.4969 | 1.5381 | 1.6159 | 1.4099 | 1.2543 | 30.9906 | 31.0364 | 31.2469 | 31.0043 | 30.9402 | 8.7799 | 8.6792 | 93.5852 | 93.4296 | -29.3884 | 93.7866 | 93.7134 | 0.28381 | -29.4846 | 100.9552 | 100.8545 | 0 | 123.1659 | 123.4222 | 22.5677 | -0.064086 | 93.7912 | 93.6951 | 93.6722 | -29.7501 | 123.1796 | 123.1155 | 123.2117 | -22.3251
2504.5156 | 123.3765 | -92.2806 | 30.9952 | -0.079346 | 0.017799 | 0.0011493 | 0.013676 | -0.018698 | 0.0031894 | 0.0021255 | -0.050125 | 0.021089 | -0.010004 | 0.013777 | -0.0016492 | 0.0099975 | 1.5015 | 1.4832 | 1.3779 | 1.4786 | 1.6205 | 1.3916 | 1.2451 | 30.9769 | 31.073 | 31.0226 | 31.0089 | 30.9402 | 8.7753 | 8.6746 | 93.6722 | 93.5257 | -29.3747 | 93.7637 | 93.7592 | 0.23346 | -29.4937 | 101.0559 | 100.9552 | 0.013733 | 123.2574 | 123.3032 | 22.348 | -0.054931 | 93.9011 | 93.782 | 93.6584 | -29.7501 | 123.2895 | 123.2208 | 123.3536 | -22.3206
2505.5156 | 123.381 | -92.3126 | 30.9631 | 0.28687 | 0.014381 | 0.0028583 | 0.013035 | -0.018912 | 0.0025486 | 0.0027665 | 0.13298 | 0.022798 | -0.010004 | 0.015058 | -0.0044262 | 0.012988 | 1.4099 | 1.387 | 1.3275 | 1.4374 | 1.6296 | 1.3779 | 1.2131 | 30.9036 | 30.9586 | 30.9631 | 30.9586 | 30.8945 | 8.7753 | 8.6792 | 93.6905 | 93.5257 | -29.3335 | 93.6996 | 93.75 | 0.2243 | -29.5532 | 101.088 | 100.9918 | -0.004578 | 123.2162 | 123.2758 | 22.2839 | -0.068665 | 93.9423 | 93.7225 | 93.6401 | -29.7501 | 123.2712 | 123.2071 | 123.2712 | -22.2839
2506.5156 | 123.3673 | -92.3813 | 30.8807 | -0.02594 | 0.017799 | 0.0043537 | 0.015172 | -0.019766 | 0.0036166 | 0.0027665 | -0.011978 | 0.018739 | -0.010645 | 0.012495 | -0.0012218 | 0.0080749 | 1.4832 | 1.4648 | 1.3412 | 1.4557 | 1.6067 | 1.387 | 1.2131 | 30.867 | 30.9631 | 30.9128 | 30.9082 | 30.8395 | 8.7799 | 8.6792 | 93.7683 | 93.5944 | -29.274 | 93.8461 | 93.837 | 0.24261 | -29.3976 | 101.1612 | 101.0605 | 0.027466 | 123.2483 | 123.2941 | 22.2336 | -0.041198 | 93.988 | 93.8644 | 93.7225 | -29.6677 | 123.2895 | 123.2208 | 123.3444 | -22.2015
2507.5156 | 123.3673 | -92.4179 | 30.8716 | 0.088501 | 0.019722 | 0.0026447 | 0.015172 | -0.022544 | 0.00041235 | 0.0034073 | 0.18639 | 0.021089 | -0.010431 | 0.011213 | -0.003999 | 0.010638 | 1.4145 | 1.4099 | 1.3138 | 1.4282 | 1.6159 | 1.3824 | 1.2177 | 30.8166 | 30.8762 | 30.8945 | 30.8716 | 30.7983 | 8.7753 | 8.6746 | 93.8004 | 93.6356 | -29.2557 | 93.8278 | 93.8461 | 0.21057 | -29.4571 | 101.1932 | 101.0925 | 0 | 123.2346 | 123.3124 | 22.2198 | -0.073242 | 94.0338 | 93.8324 | 93.7317 | -29.6539 | 123.2895 | 123.2162 | 123.2941 | -22.197
2508.5156 | 123.4726 | -92.4133 | 30.7571 | 0.2182 | 0.013313 | 0.0054217 | 0.0076948 | -0.017844 | -0.0019376 | 0.0025529 | 0.23979 | 0.020234 | -0.012995 | 0.012281 | -0.005708 | 0.012347 | 1.4832 | 1.5472 | 1.4511 | 1.5152 | 1.5793 | 1.4099 | 1.2634 | 30.8624 | 30.954 | 30.9494 | 30.7983 | 30.7251 | 8.7799 | 8.6792 | 93.8232 | 93.6768 | -29.1779 | 93.9606 | 93.9285 | 0.25177 | -29.274 | 101.1932 | 101.0925 | 0.041199 | 123.2758 | 123.3627 | 22.2702 | -0.032043 | 93.9926 | 93.8965 | 93.8644 | -29.4937 | 123.2117 | 123.1384 | 123.3673 | -22.0779
2509.5156 | 123.468 | -92.482 | 30.7251 | 0.21057 | 0.016517 | 0.0013629 | 0.01154 | -0.019339 | 0.00019875 | 0.0027665 | 0.25505 | 0.021302 | -0.010431 | 0.012708 | -0.0027172 | 0.0099975 | 1.4786 | 1.4832 | 1.4008 | 1.4648 | 1.5884 | 1.4191 | 1.2268 | 30.8121 | 30.8945 | 30.8853 | 30.7388 | 30.6976 | 8.7708 | 8.6884 | 93.9011 | 93.7088 | -29.1367 | 93.9651 | 93.9468 | 0.23804 | -29.2465 | 101.2527 | 101.1703 | 0.013733 | 123.2941 | 123.3673 | 22.197 | -0.027466 | 94.0704 | 93.9606 | 93.8828 | -29.4983 | 123.2208 | 123.1796 | 123.3765 | -22.0367
2510.5156 | 123.3994 | -92.5415 | 30.6885 | -0.14038 | 0.018013 | 0.0017901 | 0.012394 | -0.019766 | 0.003403 | 0.0021255 | -0.11879 | 0.020662 | -0.0072268 | 0.014417 | -0.0014356 | 0.0078613 | 1.4694 | 1.4557 | 1.3458 | 1.4832 | 1.6296 | 1.3779 | 1.1902 | 30.7159 | 30.8166 | 30.7846 | 30.7434 | 30.6702 | 8.7845 | 8.6838 | 93.9194 | 93.7317 | -29.0588 | 93.9972 | 94.0247 | 0.29297 | -29.2191 | 101.326 | 101.2253 | 0.054931 | 123.2574 | 123.3261 | 22.1008 | -0.018311 | 94.1711 | 94.0109 | 93.8873 | -29.4983 | 123.2849 | 123.2117 | 123.3582 | -22.0047
2511.5156 | 123.3536 | -92.5964 | 30.6885 | 0.035095 | 0.01844 | -0.00013251 | 0.012822 | -0.020194 | 0.002335 | 0.0029801 | 0.15587 | 0.020234 | -0.011499 | 0.01164 | -0.0033582 | 0.011279 | 1.4099 | 1.3916 | 1.3046 | 1.4282 | 1.5976 | 1.387 | 1.2131 | 30.6061 | 30.6839 | 30.6656 | 30.6931 | 30.6702 | 8.7753 | 8.67 | 93.9835 | 93.8095 | -29.0909 | 93.988 | 94.0247 | 0.21515 | -29.2786 | 101.3718 | 101.2665 | 0.004577 | 123.2025 | 123.262 | 21.9955 | -0.018311 | 94.194 | 94.0063 | 93.9011 | -29.4754 | 123.2895 | 123.2666 | 123.2803 | -22.0184
2512.5156 | 123.3627 | -92.601 | 30.6519 | -0.10986 | 0.02079 | 0.0020037 | 0.014103 | -0.019126 | 0.0027622 | 0.0021255 | -0.019608 | 0.02173 | -0.010645 | 0.011427 | -0.0010082 | 0.010638 | 1.4694 | 1.4877 | 1.3641 | 1.4603 | 1.6159 | 1.3824 | 1.2222 | 30.6107 | 30.7022 | 30.6793 | 30.6564 | 30.5923 | 8.7845 | 8.6792 | 93.9835 | 93.8232 | -29.0359 | 94.0887 | 94.0613 | 0.23804 | -29.1824 | 101.3855 | 101.2802 | 0.004578 | 123.2117 | 123.2803 | 22.0001 | -0.059509 | 94.2169 | 94.0704 | 93.9651 | -29.4296 | 123.2574 | 123.1934 | 123.3032 | -21.9727
2513.5312 | 123.4406 | -92.6239 | 30.5786 | 0.13428 | 0.015022 | 0.0028583 | 0.0087628 | -0.020407 | -0.0049282 | 0.0012711 | 0.27031 | 0.017884 | -0.013849 | 0.012068 | -0.0052808 | 0.01192 | 1.4694 | 1.5289 | 1.4374 | 1.4969 | 1.5976 | 1.4145 | 1.2543 | 30.6198 | 30.6931 | 30.7114 | 30.5786 | 30.5283 | 8.7753 | 8.6792 | 94.0384 | 93.8782 | -28.981 | 94.1528 | 94.1208 | 0.24262 | -29.1092 | 101.3992 | 101.3031 | 0 | 123.2437 | 123.3353 | 22.0322 | -0.050354 | 94.2215 | 94.0933 | 94.0613 | -29.3243 | 123.2025 | 123.1522 | 123.317 | -21.8994
2514.5156 | 123.3627 | -92.7155 | 30.542 | 0.027466 | 0.018867 | 0.0013629 | 0.014103 | -0.016776 | 0.0044712 | 0.0014847 | -0.042496 | 0.020662 | -0.0089358 | 0.013349 | -0.00079463 | 0.0089295 | 1.4923 | 1.4557 | 1.3412 | 1.4648 | 1.6022 | 1.3779 | 1.2222 | 30.5466 | 30.629 | 30.574 | 30.5832 | 30.5145 | 8.7799 | 8.6838 | 94.0933 | 93.9377 | -28.9398 | 94.1711 | 94.1803 | 0.24262 | -29.0497 | 101.4954 | 101.3992 | 0.041199 | 123.262 | 123.2895 | 21.8903 | -0.027466 | 94.3176 | 94.2078 | 94.0567 | -29.3198 | 123.2986 | 123.23 | 123.3444 | -21.8582
2515.5156 | 123.4085 | -92.775 | 30.4916 | -0.28534 | 0.018654 | 0.0024311 | 0.015172 | -0.018485 | 0.0029758 | 0.0012711 | -0.088272 | 0.020448 | -0.0080814 | 0.013563 | -0.0035718 | 0.0099975 | 1.4877 | 1.4877 | 1.3641 | 1.4694 | 1.6571 | 1.4008 | 1.2405 | 30.4779 | 30.5832 | 30.5328 | 30.5099 | 30.4459 | 8.7753 | 8.6792 | 94.1757 | 94.0155 | -28.8345 | 94.2627 | 94.2444 | 0.22888 | -29.0039 | 101.5503 | 101.4542 | 0.018311 | 123.2529 | 123.3078 | 21.8536 | -0.045776 | 94.4321 | 94.2627 | 94.1391 | -29.2511 | 123.2849 | 123.2208 | 123.3582 | -21.8124
2516.5156 | 123.3582 | -92.7017 | 30.6244 | -0.18616 | 0.012672 | 0.0034991 | 0.012181 | -0.018912 | -0.00065585 | -0.00086512 | -0.14168 | 0.01938 | -0.01214 | 0.010999 | -0.0033582 | 0.012347 | 1.4236 | 1.4236 | 1.3229 | 1.4465 | 1.6479 | 1.3779 | 1.1993 | 30.5054 | 30.629 | 30.6107 | 30.5969 | 30.5283 | 8.7753 | 8.6746 | 94.0796 | 93.9011 | -28.9764 | 94.1254 | 94.1483 | 0.24719 | -29.2007 | 101.4771 | 101.3763 | -0.027466 | 123.2071 | 123.3124 | 21.936 | -0.096131 | 94.3497 | 94.1254 | 94.0247 | -29.425 | 123.2986 | 123.23 | 123.3307 | -21.9498
2517.5156 | 123.2849 | -92.6331 | 30.629 | -0.14801 | 0.019081 | 0.0011493 | 0.015385 | -0.016135 | 0.0010532 | 0.0019119 | -0.15694 | 0.020021 | -0.0091494 | 0.014845 | -0.0020764 | 0.0097839 | 1.4557 | 1.5015 | 1.387 | 1.5015 | 1.6205 | 1.3824 | 1.2268 | 30.5923 | 30.6793 | 30.6381 | 30.6015 | 30.5283 | 8.7753 | 8.6746 | 94.0155 | 93.8599 | -29.0085 | 94.1345 | 94.1345 | 0.27466 | -29.1733 | 101.4084 | 101.3077 | -0.027466 | 123.2254 | 123.2712 | 21.9635 | -0.10071 | 94.2535 | 94.0887 | 94.0201 | -29.4022 | 123.2346 | 123.1613 | 123.3124 | -21.9543
2518.5156 | 123.3627 | -92.6697 | 30.6335 | -0.14801 | 0.015236 | 0.0022175 | 0.014103 | -0.01998 | -0.0040738 | 0.0025529 | -0.080643 | 0.017884 | -0.010858 | 0.013349 | -0.0042126 | 0.012775 | 1.3962 | 1.4877 | 1.355 | 1.4465 | 1.6434 | 1.3824 | 1.2268 | 30.5511 | 30.6381 | 30.661 | 30.6427 | 30.574 | 8.7845 | 8.6746 | 94.0521 | 93.8965 | -28.9902 | 94.1574 | 94.1162 | 0.21973 | -29.2374 | 101.4542 | 101.3443 | 0.009155 | 123.2208 | 123.3307 | 21.9864 | -0.059509 | 94.3131 | 94.0659 | 94.0247 | -29.4067 | 123.3124 | 123.2437 | 123.3078 | -21.9589
2519.5156 | 123.3948 | -92.6468 | 30.6015 | -0.14038 | 0.01844 | 0.00093569 | 0.014103 | -0.019766 | 0.0025486 | 0.0014847 | -0.088272 | 0.019807 | -0.0085086 | 0.013349 | -0.0018628 | 0.010425 | 1.4923 | 1.4877 | 1.387 | 1.506 | 1.6205 | 1.4053 | 1.2222 | 30.5969 | 30.7343 | 30.7159 | 30.6152 | 30.5557 | 8.7753 | 8.6838 | 94.0521 | 93.869 | -28.981 | 94.1345 | 94.1528 | 0.28381 | -29.1092 | 101.4221 | 101.3306 | 0.013733 | 123.2437 | 123.3627 | 22.0322 | -0.045776 | 94.2673 | 94.1391 | 94.0338 | -29.3793 | 123.262 | 123.2025 | 123.381 | -21.9177
2520.5156 | 123.3673 | -92.6743 | 30.6015 | -0.20142 | 0.015022 | 0.0032855 | 0.011326 | -0.020621 | -0.0025784 | 0.00041648 | -0.19508 | 0.017671 | -0.010858 | 0.013777 | -0.003999 | 0.0099975 | 1.6571 | 1.3184 | 1.2726 | 1.4557 | 1.7029 | 1.4328 | 1.2589 | 30.5191 | 30.6244 | 30.6198 | 30.6152 | 30.5603 | 8.7845 | 8.6838 | 94.1071 | 93.9331 | -28.8986 | 93.9926 | 94.1299 | 0.19684 | -28.9444 | 101.4587 | 101.358 | 0.013733 | 123.1934 | 123.2941 | 21.936 | -0.041198 | 94.3771 | 94.3314 | 93.9468 | -29.3427 | 123.2895 | 123.2346 | 123.2986 | -21.9177
2521.5156 | 123.4131 | -92.6559 | 30.5923 | -0.15564 | 0.016304 | 0.0030719 | 0.010899 | -0.018485 | -1.505e-05 | 0.0016983 | -0.1722 | 0.02173 | -0.011713 | 0.013349 | -0.0018628 | 0.011279 | 1.442 | 1.4648 | 1.355 | 1.4786 | 1.6251 | 1.3962 | 1.2131 | 30.5649 | 30.6656 | 30.6427 | 30.5969 | 30.5328 | 8.7799 | 8.6792 | 94.0521 | 93.869 | -28.9673 | 94.1208 | 94.1345 | 0.2655 | -29.1504 | 101.4359 | 101.3351 | 0.004578 | 123.2208 | 123.2986 | 21.9635 | -0.059509 | 94.281 | 94.0979 | 94.0109 | -29.3793 | 123.2529 | 123.1888 | 123.3215 | -21.9131
2522.5156 | 123.3536 | -92.7155 | 30.6015 | -0.16327 | 0.012245 | 0.0049945 | 0.012181 | -0.020194 | -0.0034328 | 0.0012711 | -0.14931 | 0.018953 | -0.012354 | 0.013563 | -0.0054944 | 0.010852 | 1.4236 | 1.4923 | 1.3824 | 1.474 | 1.6525 | 1.387 | 1.2268 | 30.4916 | 30.629 | 30.6107 | 30.5878 | 30.5191 | 8.7799 | 8.6792 | 94.1025 | 93.9423 | -28.949 | 94.2078 | 94.1895 | 0.24719 | -29.1779 | 101.4954 | 101.3947 | -0.013732 | 123.2071 | 123.3261 | 21.9315 | -0.082397 | 94.368 | 94.1391 | 94.0979 | -29.3747 | 123.3032 | 123.2346 | 123.3444 | -21.9223
2523.5156 | 123.3948 | -92.6926 | 30.5557 | -0.14801 | 0.015236 | 0.0041401 | 0.013035 | -0.01763 | 0.00019875 | 0.00063028 | -0.19508 | 0.021089 | -0.0091494 | 0.011427 | -0.0037854 | 0.0099975 | 1.4099 | 1.474 | 1.3504 | 1.474 | 1.6479 | 1.4008 | 1.2268 | 30.5054 | 30.6244 | 30.6015 | 30.6061 | 30.5237 | 8.7799 | 8.6746 | 94.0933 | 93.9194 | -28.9078 | 94.1666 | 94.1666 | 0.24719 | -29.1458 | 101.4725 | 101.3672 | 0.050354 | 123.1979 | 123.2941 | 21.9269 | -0.032043 | 94.3405 | 94.1025 | 94.043 | -29.3289 | 123.2986 | 123.2162 | 123.317 | -21.8811
2524.5156 | 123.4909 | -92.6743 | 30.5145 | -0.14038 | 0.013313 | 0.0032855 | 0.015385 | -0.018485 | -0.0051418 | 0.00084388 | -0.050125 | 0.017457 | -0.013208 | 0.012708 | -0.0061352 | 0.011493 | 1.506 | 1.6022 | 1.4877 | 1.5381 | 1.6022 | 1.4465 | 1.2589 | 30.5923 | 30.7434 | 30.7114 | 30.5283 | 30.4688 | 8.7799 | 8.6746 | 94.1208 | 93.9331 | -28.9124 | 94.2764 | 94.2123 | 0.27924 | -29.0085 | 101.4542 | 101.3489 | 0.013733 | 123.2666 | 123.3856 | 22.0367 | -0.045776 | 94.2764 | 94.1803 | 94.162 | -29.2557 | 123.2025 | 123.143 | 123.4177 | -21.8399
2525.5156 | 123.3856 | -92.7292 | 30.5283 | -0.20905 | 0.015449 | 0.0034991 | 0.018162 | -0.017417 | 0.0036166 | 0.0012711 | -0.16457 | 0.017671 | -0.0080814 | 0.014631 | -0.0029308 | 0.010425 | 1.4374 | 1.4557 | 1.3687 | 1.4694 | 1.6342 | 1.3916 | 1.2314 | 30.4825 | 30.6061 | 30.574 | 30.5603 | 30.4779 | 8.7845 | 8.6838 | 94.1208 | 93.9606 | -28.894 | 94.1849 | 94.1986 | 0.23804 | -29.0909 | 101.5137 | 101.413 | 0.032044 | 123.2117 | 123.3032 | 21.8903 | -0.050354 | 94.3634 | 94.1666 | 94.0979 | -29.2969 | 123.2895 | 123.2071 | 123.3353 | -21.8445
2526.5156 | 123.3719 | -92.72 | 30.542 | -0.20142 | 0.011177 | 0.0043537 | 0.012181 | -0.017844 | -0.00022865 | 0.0014847 | -0.15694 | 0.017457 | -0.01449 | 0.015272 | -0.0044262 | 0.010425 | 1.4603 | 1.5427 | 1.4099 | 1.5198 | 1.6571 | 1.4328 | 1.2222 | 30.4779 | 30.6015 | 30.574 | 30.5374 | 30.4642 | 8.7753 | 8.6838 | 94.1528 | 93.9423 | -28.8849 | 94.2627 | 94.2398 | 0.29755 | -29.0817 | 101.4954 | 101.4038 | -0.004577 | 123.1979 | 123.2941 | 21.8903 | -0.07782 | 94.3771 | 94.1803 | 94.1299 | -29.3198 | 123.2574 | 123.1842 | 123.3215 | -21.8582
2527.5156 | 123.3673 | -92.8116 | 30.4825 | -0.16327 | 0.015236 | 0.0037127 | 0.013676 | -0.018912 | 0.002335 | -0.00043792 | -0.12642 | 0.01938 | -0.010431 | 0.013136 | -0.0020764 | 0.0076477 | 1.4236 | 1.4603 | 1.3412 | 1.4648 | 1.6708 | 1.4008 | 1.2177 | 30.3818 | 30.5145 | 30.4688 | 30.4733 | 30.423 | 8.7799 | 8.6838 | 94.2123 | 94.0292 | -28.8116 | 94.2719 | 94.2764 | 0.24719 | -29.0588 | 101.5915 | 101.4954 | -0.009155 | 123.1934 | 123.2803 | 21.785 | -0.059509 | 94.4824 | 94.2352 | 94.1528 | -29.2648 | 123.2849 | 123.2346 | 123.3261 | -21.7987
2528.5156 | 123.4222 | -92.807 | 30.4276 | -0.16327 | 0.0092541 | 0.0030719 | 0.011754 | -0.01998 | -0.0040738 | -0.00022432 | -0.11879 | 0.017671 | -0.010858 | 0.013563 | -0.0048534 | 0.010211 | 1.4969 | 1.5976 | 1.4557 | 1.5244 | 1.6296 | 1.4236 | 1.2634 | 30.4092 | 30.5603 | 30.5191 | 30.4184 | 30.3452 | 8.7891 | 8.6838 | 94.2307 | 94.0704 | -28.7979 | 94.4046 | 94.3314 | 0.26093 | -28.9307 | 101.5961 | 101.4908 | -0.009155 | 123.2162 | 123.3261 | 21.8353 | -0.082397 | 94.4366 | 94.3039 | 94.2627 | -29.1641 | 123.2254 | 123.1522 | 123.3673 | -21.7438
2529.5156 | 123.381 | -92.8665 | 30.4184 | -0.17853 | 0.016304 | 8.1086e-05 | 0.013676 | -0.016989 | 0.00062595 | 0.00041648 | -0.16457 | 0.020448 | -0.010645 | 0.012708 | -0.0035718 | 0.0097839 | 1.4557 | 1.4465 | 1.3458 | 1.4648 | 1.6571 | 1.3916 | 1.2222 | 30.3497 | 30.4642 | 30.455 | 30.423 | 30.3543 | 8.7799 | 8.6792 | 94.2581 | 94.0887 | -28.7613 | 94.313 | 94.3314 | 0.24262 | -28.9627 | 101.6464 | 101.5457 | 0.004578 | 123.2162 | 123.3215 | 21.7758 | -0.064087 | 94.5236 | 94.3222 | 94.2123 | -29.1962 | 123.2895 | 123.2208 | 123.3307 | -21.7392
2530.5156 | 123.4726 | -92.8253 | 30.368 | -0.14038 | 0.011818 | 0.0041401 | 0.011967 | -0.020407 | -0.0036464 | -0.00022432 | -0.10353 | 0.015748 | -0.012354 | 0.012495 | -0.0044262 | 0.0097839 | 1.4969 | 1.593 | 1.4877 | 1.5335 | 1.6251 | 1.4511 | 1.268 | 30.4092 | 30.5603 | 30.5283 | 30.3589 | 30.2856 | 8.7799 | 8.6746 | 94.2764 | 94.0933 | -28.743 | 94.4183 | 94.3588 | 0.2655 | -28.8712 | 101.6052 | 101.4999 | -0.009155 | 123.2346 | 123.3536 | 21.8536 | -0.082397 | 94.4504 | 94.3222 | 94.313 | -29.1 | 123.1842 | 123.111 | 123.3856 | -21.6934
2531.5156 | 123.4131 | -92.8848 | 30.3543 | -0.20142 | 0.01374 | 0.0020037 | 0.013035 | -0.021903 | -0.0021512 | 0.0012711 | -0.15694 | 0.019807 | -0.012354 | 0.013136 | -0.005708 | 0.0099975 | 1.4877 | 1.5701 | 1.4511 | 1.5289 | 1.6296 | 1.4282 | 1.2589 | 30.3268 | 30.4779 | 30.423 | 30.3406 | 30.2628 | 8.7799 | 8.6792 | 94.3131 | 94.1437 | -28.7247 | 94.455 | 94.4138 | 0.27008 | -28.8666 | 101.6647 | 101.564 | -0.013733 | 123.2117 | 123.3078 | 21.7438 | -0.091553 | 94.5145 | 94.3726 | 94.3359 | -29.0955 | 123.2254 | 123.1476 | 123.3627 | -21.6751
2532.5156 | 123.4772 | -92.9031 | 30.2948 | -0.14801 | 0.0079723 | 0.0099079 | 0.014744 | -0.017417 | 0.00041235 | -0.00022432 | -0.1722 | 0.016816 | -0.013636 | 0.010359 | -0.0042126 | 0.0097839 | 1.5289 | 1.5839 | 1.4603 | 1.5289 | 1.593 | 1.4236 | 1.2451 | 30.3726 | 30.5054 | 30.4688 | 30.2902 | 30.2216 | 8.7799 | 8.6792 | 94.3268 | 94.1483 | -28.7018 | 94.487 | 94.4321 | 0.28381 | -28.7659 | 101.683 | 101.5823 | -0.004578 | 123.2758 | 123.3719 | 21.7896 | -0.073242 | 94.4962 | 94.4321 | 94.3634 | -29.0497 | 123.1934 | 123.1247 | 123.4085 | -21.6156
2533.5156 | 123.3765 | -92.9489 | 30.336 | -0.20905 | 0.016731 | 0.0043537 | 0.014744 | -0.021475 | 0.00062595 | 0.0010575 | -0.073013 | 0.018525 | -0.011072 | 0.013777 | -0.0033582 | 0.0091431 | 1.4099 | 1.4328 | 1.3641 | 1.474 | 1.7075 | 1.4511 | 1.2634 | 30.2628 | 30.3635 | 30.3452 | 30.3726 | 30.249 | 8.7753 | 8.6838 | 94.4 | 94.2123 | -28.6285 | 94.3817 | 94.4229 | 0.21057 | -28.9261 | 101.7242 | 101.6327 | 0.036621 | 123.2117 | 123.2941 | 21.6614 | -0.086976 | 94.6564 | 94.3588 | 94.3131 | -29.0726 | 123.3215 | 123.1979 | 123.3124 | -21.6522
2534.5156 | 123.4726 | -92.9352 | 30.2536 | -0.12512 | 0.011177 | 0.0026447 | 0.011113 | -0.01998 | -0.0025784 | 0.00020288 | -0.11879 | 0.017244 | -0.011927 | 0.0092904 | -0.0020764 | 0.011493 | 1.5152 | 1.5839 | 1.4877 | 1.5289 | 1.6342 | 1.4374 | 1.2634 | 30.3268 | 30.4504 | 30.423 | 30.249 | 30.2078 | 8.7845 | 8.6884 | 94.3726 | 94.1986 | -28.6194 | 94.519 | 94.4641 | 0.2655 | -28.7384 | 101.7197 | 101.6235 | -0.004578 | 123.262 | 123.3582 | 21.7346 | -0.045776 | 94.5694 | 94.4504 | 94.4229 | -28.9902 | 123.1842 | 123.143 | 123.3856 | -21.5652
2535.5156 | 123.3398 | -92.9672 | 30.304 | -0.20905 | 0.012886 | 0.0045673 | 0.01389 | -0.018057 | -0.00044225 | 0.0014847 | -0.21797 | 0.018312 | -0.011499 | 0.013349 | -0.0025036 | 0.0082885 | 1.4374 | 1.4648 | 1.3641 | 1.4648 | 1.6388 | 1.3962 | 1.2268 | 30.2765 | 30.5328 | 30.1758 | 30.3223 | 30.2216 | 8.7799 | 8.6792 | 94.3634 | 94.194 | -28.6652 | 94.4321 | 94.4321 | 0.23804 | -28.8666 | 101.7471 | 101.6464 | 0.018311 | 123.2437 | 123.143 | 21.4966 | -0.082397 | 94.606 | 94.4046 | 94.3314 | -29.0771 | 123.2895 | 123.1888 | 123.5001 | -21.6248
2536.5156 | 123.4818 | -93.013 | 30.2216 | -3.1082 | 0.01075 | 0.0020037 | 0.0089764 | -0.018698 | -0.0042874 | -1.0724e-05 | -0.10353 | 0.016816 | -0.012354 | 0.011427 | -0.0029308 | 0.0097839 | 1.474 | 1.6159 | 1.4923 | 1.5152 | 1.5976 | 1.4145 | 1.2589 | 30.2948 | 30.4047 | 30.3772 | 30.2078 | 30.1346 | 8.7799 | 8.6838 | 94.4275 | 94.2719 | -28.624 | 94.6289 | 94.5282 | 0.25635 | -28.7476 | 101.7929 | 101.6968 | -0.013733 | 123.3078 | 123.3902 | 21.6934 | -0.086975 | 94.6106 | 94.487 | 94.5053 | -28.9627 | 123.2208 | 123.1476 | 123.4177 | -21.5378
2537.5156 | 123.3627 | -93.0634 | 30.2216 | -0.20142 | 0.012459 | 0.0052081 | 0.014103 | -0.01763 | 0.0031894 | -0.0015061 | -0.23323 | 0.018525 | -0.012781 | 0.012922 | -0.0035718 | 0.0099975 | 1.4603 | 1.5244 | 1.3916 | 1.4786 | 1.6434 | 1.3962 | 1.2405 | 30.1666 | 30.2628 | 30.2261 | 30.2353 | 30.1437 | 8.7845 | 8.6792 | 94.4595 | 94.3039 | -28.5782 | 94.5877 | 94.5419 | 0.23804 | -28.7613 | 101.8478 | 101.7426 | 0.013733 | 123.23 | 123.2895 | 21.5469 | -0.07782 | 94.7067 | 94.5236 | 94.455 | -28.981 | 123.2986 | 123.2071 | 123.3261 | -21.5424
2538.5156 | 123.5001 | -93.0542 | 30.13 | -0.033569 | 0.0092541 | 0.0028583 | 0.010899 | -0.018271 | -0.0036464 | 0.00020288 | -0.027237 | 0.017457 | -0.011072 | 0.010999 | -0.0048534 | 0.011707 | 1.4877 | 1.6067 | 1.4694 | 1.5335 | 1.6251 | 1.4511 | 1.2726 | 30.2261 | 30.3131 | 30.3223 | 30.1346 | 30.0659 | 8.7799 | 8.6838 | 94.5053 | 94.3268 | -28.5049 | 94.6609 | 94.5877 | 0.26093 | -28.6423 | 101.8341 | 101.738 | 0.004578 | 123.2803 | 123.3765 | 21.6385 | -0.064087 | 94.6793 | 94.5419 | 94.5236 | -28.8574 | 123.1888 | 123.1201 | 123.3673 | -21.4462
2539.5156 | 123.3582 | -93.1229 | 30.1575 | -0.15564 | 0.013099 | 0.0028583 | 0.014317 | -0.021262 | 0.0010532 | 0.0019119 | -0.1722 | 0.016603 | -0.012354 | 0.012922 | -0.00229 | 0.010425 | 1.4786 | 1.561 | 1.442 | 1.5289 | 1.6296 | 1.4099 | 1.2772 | 30.13 | 30.2353 | 30.1987 | 30.1575 | 30.0705 | 8.7753 | 8.6884 | 94.5328 | 94.4 | -28.5278 | 94.6838 | 94.6518 | 0.25177 | -28.6789 | 101.8982 | 101.8112 | 0 | 123.2529 | 123.3215 | 21.5103 | -0.086975 | 94.7525 | 94.6014 | 94.5648 | -28.8803 | 123.2803 | 123.1934 | 123.3582 | -21.4691
2540.5156 | 123.4818 | -93.1137 | 30.0842 | 0.69122 | 0.010963 | 0.0056353 | 0.010045 | -0.018912 | -0.0012966 | 0.0019119 | -0.050125 | 0.017244 | -0.011286 | 0.0099314 | -0.0044262 | 0.0093567 | 1.5289 | 1.6251 | 1.474 | 1.5244 | 1.6113 | 1.4236 | 1.2543 | 30.1712 | 30.2902 | 30.2536 | 30.0934 | 30.0201 | 8.7799 | 8.6838 | 94.5374 | 94.368 | -28.4729 | 94.7388 | 94.6381 | 0.27008 | -28.5553 | 101.8936 | 101.7975 | 0.009155 | 123.2849 | 123.3673 | 21.5698 | -0.064087 | 94.725 | 94.6426 | 94.5877 | -28.83 | 123.2071 | 123.1338 | 123.4039 | -21.4005
2541.5156 | 123.4131 | -93.1503 | 30.13 | -0.21667 | 0.013099 | 0.0026447 | 0.014317 | -0.016776 | -0.00065585 | 0.00041648 | -0.1722 | 0.019166 | -0.011499 | 0.012495 | -0.0020764 | 0.0093567 | 1.442 | 1.4786 | 1.3596 | 1.4557 | 1.6342 | 1.387 | 1.2177 | 30.0476 | 30.1346 | 30.1025 | 30.1209 | 30.0339 | 8.7845 | 8.67 | 94.5374 | 94.368 | -28.4958 | 94.6289 | 94.606 | 0.23804 | -28.688 | 101.9348 | 101.8204 | -0.009155 | 123.1979 | 123.2529 | 21.4325 | -0.09613 | 94.7845 | 94.5923 | 94.5099 | -28.9124 | 123.2712 | 123.1842 | 123.2849 | -21.46
2542.5156 | 123.4818 | -93.1412 | 30.0522 | -0.14801 | 0.0083997 | 0.0037127 | 0.0085492 | -0.019339 | -0.0074918 | -0.00065152 | -0.20271 | 0.01703 | -0.011927 | 0.011213 | -0.0027172 | 0.010638 | 1.6891 | 1.2405 | 1.3458 | 1.5106 | 1.6113 | 1.4053 | 1.2405 | 30.1437 | 30.2673 | 30.2307 | 30.0613 | 29.9835 | 8.7753 | 8.6838 | 94.5465 | 94.3817 | -28.4409 | 94.3817 | 94.6518 | 0.27008 | -28.363 | 101.9165 | 101.825 | 0.009155 | 123.2849 | 123.3719 | 21.5469 | -0.068664 | 94.7525 | 94.8303 | 94.487 | -28.8116 | 123.2025 | 123.1247 | 123.4085 | -21.3684
2543.5156 | 123.3719 | -93.2007 | 30.0476 | -0.1709 | 0.013527 | 0.0041401 | 0.010899 | -0.019766 | 0.00062595 | 0.00020288 | -0.14168 | 0.018953 | -0.011927 | 0.011854 | -0.0046398 | 0.0095703 | 1.474 | 1.5427 | 1.4145 | 1.5015 | 1.6342 | 1.3779 | 1.236 | 30.011 | 30.1025 | 30.0797 | 30.0797 | 29.9744 | 8.7753 | 8.6792 | 94.5786 | 94.4366 | -28.4134 | 94.7433 | 94.7021 | 0.2655 | -28.5736 | 101.976 | 101.8799 | 0.032044 | 123.2117 | 123.2803 | 21.4005 | -0.073242 | 94.8349 | 94.6747 | 94.6152 | -28.8116 | 123.2803 | 123.175 | 123.3032 | -21.3684
2544.5156 | 123.5092 | -93.1961 | 29.9881 | -0.056458 | 0.0098951 | 0.0013629 | 0.011754 | -0.020407 | -0.0019376 | 0.0012711 | -0.11879 | 0.016389 | -0.012995 | 0.011427 | -0.0086988 | 0.0095703 | 1.5152 | 1.6342 | 1.5015 | 1.5518 | 1.6113 | 1.4328 | 1.268 | 30.2124 | 29.7318 | 30.1346 | 29.9744 | 29.8874 | 8.7799 | 8.6838 | 94.6289 | 94.4641 | -28.3768 | 94.8303 | 94.7479 | 0.28381 | -28.4729 | 101.976 | 101.8799 | -0.013733 | 123.4085 | 123.3307 | 21.4508 | -0.10071 | 94.8074 | 94.7113 | 94.6976 | -28.7201 | 123.1705 | 123.0835 | 122.9279 | -21.3043
2545.5156 | 123.4863 | -93.2693 | 29.9835 | 0.10376 | 0.011818 | 0.0032855 | 0.014103 | -0.021048 | -1.505e-05 | 0.00063028 | -0.095902 | 0.018098 | -0.012567 | 0.01164 | -0.0031446 | 0.0093567 | 1.5106 | 1.6159 | 1.4877 | 1.5335 | 1.6022 | 1.4282 | 1.2543 | 30.0247 | 30.1483 | 30.1117 | 29.9515 | 29.8737 | 8.7845 | 8.6838 | 94.6976 | 94.5236 | -28.3813 | 94.8853 | 94.8029 | 0.27924 | -28.4729 | 102.0538 | 101.9531 | -0.032044 | 123.2941 | 123.381 | 21.4279 | -0.10986 | 94.8715 | 94.78 | 94.7571 | -28.7292 | 123.2208 | 123.143 | 123.4177 | -21.2997
2546.5156 | 123.5138 | -93.2831 | 29.9011 | -0.071716 | 0.0079723 | 0.0058491 | 0.010685 | -0.021048 | -0.0034328 | 0.0010575 | -0.057755 | 0.01938 | -0.013422 | 0.010786 | -0.0044262 | 0.0080749 | 1.5106 | 1.6067 | 1.4786 | 1.5198 | 1.6342 | 1.4328 | 1.2726 | 30.0018 | 30.1209 | 30.1025 | 29.9194 | 29.8141 | 8.7799 | 8.6792 | 94.7159 | 94.5557 | -28.2669 | 94.8898 | 94.8029 | 0.24719 | -28.3905 | 102.063 | 101.9623 | 0.018311 | 123.2849 | 123.3856 | 21.4233 | -0.086975 | 94.9173 | 94.7937 | 94.7617 | -28.6285 | 123.2025 | 123.0972 | 123.4039 | -21.2219
2547.5156 | 123.3719 | -93.3792 | 29.9057 | -0.18616 | 0.013099 | 0.0022175 | 0.014744 | -0.019126 | 0.0019078 | 0.0016983 | -0.21034 | 0.018525 | -0.0089358 | 0.010999 | -0.0035718 | 0.0095703 | 1.4557 | 1.5152 | 1.3733 | 1.4694 | 1.6479 | 1.4053 | 1.236 | 29.8599 | 29.9332 | 29.924 | 29.9057 | 29.8141 | 8.7845 | 8.6792 | 94.7845 | 94.6152 | -28.2578 | 94.8944 | 94.8486 | 0.23346 | -28.45 | 102.1637 | 102.0584 | 0 | 123.2391 | 123.3032 | 21.2448 | -0.091553 | 95.0272 | 94.8349 | 94.7525 | -28.6697 | 123.2849 | 123.1934 | 123.3124 | -21.2265
2548.5156 | 123.4726 | -93.3426 | 29.8416 | -0.17853 | 0.0098951 | 0.0049945 | 0.0089764 | -0.017203 | -0.00022865 | 0.00084388 | 1.8038 | 0.019166 | -0.012995 | 0.012922 | -0.0020764 | 0.010852 | 1.5289 | 1.6434 | 1.5015 | 1.5381 | 1.6113 | 1.4374 | 1.2543 | 29.9103 | 30.098 | 29.9927 | 29.8325 | 29.7409 | 8.7799 | 8.6792 | 94.78 | 94.5969 | -28.2303 | 94.986 | 94.8807 | 0.28381 | -28.3127 | 102.1225 | 102.0218 | -0.009156 | 123.2529 | 123.3353 | 21.3135 | -0.10071 | 94.9539 | 94.8715 | 94.8441 | -28.5873 | 123.175 | 123.0835 | 123.4406 | -21.1624
2549.5156 | 123.3719 | -93.4158 | 29.8279 | -0.20142 | 0.011818 | 0.0041401 | 0.01389 | -0.018912 | 0.001694 | 0.0023391 | -0.18745 | 0.017244 | -0.01214 | 0.013136 | -0.0035718 | 0.0072205 | 1.5152 | 1.5701 | 1.4374 | 1.506 | 1.6296 | 1.4145 | 1.2497 | 29.8187 | 29.924 | 29.8828 | 29.8599 | 29.7272 | 8.7708 | 8.6792 | 94.8303 | 94.6655 | -28.1982 | 94.986 | 94.9219 | 0.25635 | -28.3127 | 102.1866 | 102.095 | 0.032043 | 123.2346 | 123.2986 | 21.2036 | -0.10071 | 95.0455 | 94.931 | 94.8532 | -28.5782 | 123.2758 | 123.143 | 123.3398 | -21.1487
2550.5156 | 123.5229 | -93.4204 | 29.7775 | -0.094604 | 0.0090405 | 0.0039263 | 0.010472 | -0.018912 | -0.00044225 | 0.00084388 | 0.0032804 | 0.018953 | -0.012781 | 0.011854 | -0.0037854 | 0.011493 | 1.5015 | 1.6296 | 1.4786 | 1.5289 | 1.6022 | 1.4328 | 1.2772 | 29.8691 | 29.9973 | 29.9606 | 29.7684 | 29.6768 | 8.7799 | 8.6838 | 94.8532 | 94.6976 | -28.1754 | 95.05 | 94.9493 | 0.25177 | -28.2761 | 102.2003 | 102.1042 | -0.009155 | 123.2895 | 123.381 | 21.2769 | -0.10071 | 95.0226 | 94.9219 | 94.899 | -28.5004 | 123.1888 | 123.0972 | 123.4177 | -21.0938
2551.5156 | 123.4406 | -93.4799 | 29.7455 | -0.15564 | 0.01075 | 0.0026447 | 0.011967 | -0.019126 | 0.00019875 | 0.0014847 | -0.17983 | 0.019593 | -0.011713 | 0.012495 | 0.00048697 | 0.0097839 | 1.5198 | 1.6022 | 1.4648 | 1.5427 | 1.6296 | 1.4145 | 1.268 | 29.7821 | 29.9057 | 29.8737 | 29.7455 | 29.6402 | 8.7799 | 8.6792 | 94.8944 | 94.7479 | -28.1158 | 95.0821 | 95.0226 | 0.27466 | -28.2257 | 102.2598 | 102.1591 | 0 | 123.262 | 123.3536 | 21.1945 | -0.10528 | 95.1096 | 94.9997 | 94.9448 | -28.4775 | 123.2254 | 123.1201 | 123.3856 | -21.0663
2552.5156 | 123.4863 | -93.4982 | 29.6814 | -0.064087 | 0.0094677 | 0.0047809 | 0.010258 | -0.020621 | -0.00086945 | 0.0021255 | -0.042496 | 0.017457 | -0.014917 | 0.011213 | -0.0035718 | 0.011279 | 1.5015 | 1.5976 | 1.4557 | 1.5244 | 1.6251 | 1.4328 | 1.2589 | 29.7775 | 29.8691 | 29.8691 | 29.6722 | 29.5898 | 8.7799 | 8.6746 | 94.931 | 94.7571 | -28.0563 | 95.0958 | 95.0226 | 0.2655 | -28.1799 | 102.2781 | 102.1729 | -0.009155 | 123.2758 | 123.3673 | 21.1945 | -0.091552 | 95.1233 | 94.9997 | 94.9539 | -28.4225 | 123.1705 | 123.0881 | 123.3673 | -21.0068
2553.5156 | 123.4772 | -93.5806 | 29.6539 | 0.19531 | 0.012031 | 0.0056353 | 0.013463 | -0.021689 | 0.00041235 | 0.0038345 | -0.14168 | 0.016176 | -0.011713 | 0.012922 | -0.0033582 | 0.0095703 | 1.5152 | 1.6067 | 1.4648 | 1.5289 | 1.593 | 1.4236 | 1.2497 | 29.7134 | 29.8462 | 29.8004 | 29.631 | 29.5486 | 8.7799 | 8.6792 | 95.0043 | 94.8303 | -28.0609 | 95.1874 | 95.1096 | 0.27924 | -28.1387 | 102.3605 | 102.2598 | -0.022889 | 123.2941 | 123.381 | 21.1212 | -0.10529 | 95.1736 | 95.0958 | 95.0455 | -28.4042 | 123.2117 | 123.1293 | 123.4268 | -20.9747
2554.5156 | 123.5001 | -93.6081 | 29.5624 | -0.02594 | 0.0094677 | 0.0060627 | 0.010045 | -0.021262 | -0.0019376 | 0.00063028 | -0.11116 | 0.017884 | -0.01449 | 0.0099314 | -0.0044262 | 0.010211 | 1.506 | 1.6022 | 1.474 | 1.5335 | 1.5976 | 1.4236 | 1.2497 | 29.7043 | 29.7913 | 29.7684 | 29.5898 | 29.4846 | 8.7799 | 8.6792 | 95.0317 | 94.8578 | -27.9648 | 95.2103 | 95.1416 | 0.28381 | -28.0563 | 102.388 | 102.2873 | 0.027466 | 123.3124 | 123.3765 | 21.0892 | -0.07782 | 95.2057 | 95.1141 | 95.0821 | -28.3127 | 123.1979 | 123.0927 | 123.3994 | -20.8832
2555.5156 | 123.468 | -93.6584 | 29.5532 | -0.071716 | 0.012245 | 0.0030719 | 0.013035 | -0.021048 | 0.00062595 | 0.0012711 | -0.1722 | 0.020021 | -0.013849 | 0.01164 | -0.0016492 | 0.0078613 | 1.5106 | 1.6205 | 1.4648 | 1.5244 | 1.5884 | 1.4236 | 1.2634 | 29.631 | 29.7409 | 29.686 | 29.5807 | 29.4754 | 8.7753 | 8.6929 | 95.0821 | 94.9219 | -27.9648 | 95.2789 | 95.1828 | 0.26093 | -28.0426 | 102.4338 | 102.3514 | 0.027465 | 123.2895 | 123.3444 | 20.993 | -0.07782 | 95.2469 | 95.1691 | 95.1233 | -28.2898 | 123.2391 | 123.1338 | 123.3994 | -20.8603
2556.5156 | 123.4955 | -93.7088 | 29.4937 | 0.0045777 | 0.0079723 | 0.0032855 | 0.0096174 | -0.021903 | -0.001083 | 0.0019119 | -0.0043486 | 0.018098 | -0.011499 | 0.013136 | -0.00229 | 0.010638 | 1.4648 | 1.5564 | 1.4282 | 1.5152 | 1.6113 | 1.4191 | 1.2634 | 29.5761 | 29.6677 | 29.6585 | 29.5029 | 29.393 | 8.7799 | 8.6792 | 95.1279 | 94.9722 | -27.8824 | 95.2652 | 95.224 | 0.25177 | -28.0289 | 102.4887 | 102.388 | 0.009156 | 123.2849 | 123.3673 | 20.9793 | -0.10071 | 95.3201 | 95.1736 | 95.137 | -28.2303 | 123.2117 | 123.1018 | 123.3765 | -20.8145
2557.5156 | 123.4955 | -93.7042 | 29.4617 | -0.14038 | 0.0096813 | 0.0030719 | 0.010685 | -0.018698 | -0.00022865 | -0.0019333 | -0.27138 | 0.018525 | -0.014276 | 0.010786 | -0.0042126 | 0.0091431 | 1.7029 | 1.2589 | 1.3184 | 1.4877 | 1.593 | 1.3779 | 1.2268 | 29.5715 | 29.6997 | 29.6402 | 29.4891 | 29.3793 | 8.7845 | 8.6838 | 95.0821 | 94.931 | -27.8687 | 94.9631 | 95.192 | 0.26093 | -27.7588 | 102.4887 | 102.388 | 0.027466 | 123.2758 | 123.3444 | 20.9564 | -0.082398 | 95.2972 | 95.4071 | 95.0226 | -28.2349 | 123.1934 | 123.0835 | 123.4039 | -20.7779
2558.5156 | 123.436 | -93.7775 | 29.4342 | 0.11139 | 0.0069043 | 0.0037127 | 0.011754 | -0.020407 | -1.505e-05 | -1.0724e-05 | 0.049057 | 0.017457 | -0.012354 | 0.012281 | -0.0035718 | 0.011279 | 1.442 | 1.5381 | 1.4008 | 1.474 | 1.5884 | 1.4053 | 1.2177 | 29.4937 | 29.5578 | 29.5578 | 29.4662 | 29.3198 | 8.7799 | 8.6746 | 95.1828 | 94.9951 | -27.8458 | 95.3156 | 95.2515 | 0.25635 | -27.9922 | 102.5574 | 102.4521 | 0.032044 | 123.2712 | 123.3353 | 20.8832 | -0.11444 | 95.3659 | 95.2194 | 95.1782 | -28.2166 | 123.2437 | 123.0972 | 123.3353 | -20.7596
2559.5156 | 123.5046 | -93.8232 | 29.3564 | -0.071716 | 0.0081861 | 0.0026447 | 0.013035 | -0.018485 | 0.0010532 | 0.0023391 | -0.042496 | 0.016816 | -0.015131 | 0.0090768 | -0.003999 | 0.010425 | 1.5198 | 1.6067 | 1.4648 | 1.5198 | 1.6159 | 1.4191 | 1.2589 | 29.4891 | 29.567 | 29.5532 | 29.3518 | 29.2648 | 8.7845 | 8.6838 | 95.2423 | 95.0821 | -27.7405 | 95.43 | 95.343 | 0.26093 | -27.8366 | 102.6077 | 102.507 | -0.004577 | 123.3124 | 123.3765 | 20.8694 | -0.091552 | 95.4391 | 95.343 | 95.2881 | -28.0975 | 123.175 | 123.0881 | 123.3902 | -20.6726
2560.5156 | 123.4314 | -93.8644 | 29.3289 | 0.10376 | 0.010322 | 0.0030719 | 0.010685 | -0.020194 | 0.00062595 | 0.0023391 | 0.079574 | 0.01938 | -0.013208 | 0.010786 | -0.0033582 | 0.010638 | 1.4511 | 1.5244 | 1.4145 | 1.4648 | 1.5884 | 1.4145 | 1.2451 | 29.3564 | 29.4067 | 29.4525 | 29.3518 | 29.2236 | 8.7708 | 8.6792 | 95.2789 | 95.1096 | -27.7405 | 95.3888 | 95.3293 | 0.21973 | -27.8778 | 102.6352 | 102.5436 | 0.022889 | 123.2208 | 123.317 | 20.7733 | -0.10529 | 95.4529 | 95.3156 | 95.2789 | -28.0838 | 123.2162 | 123.0881 | 123.2712 | -20.6497
2561.5156 | 123.3856 | -93.9011 | 29.2694 | 0.012207 | 0.011177 | 0.0047809 | 0.01389 | -0.018912 | -0.001083 | 0.0014847 | -0.073013 | 0.018098 | -0.01449 | 0.013777 | -0.0050672 | 0.0080749 | 1.5335 | 1.6113 | 1.4877 | 1.5289 | 1.6067 | 1.3962 | 1.2497 | 29.4205 | 29.5303 | 29.4846 | 29.2969 | 29.1962 | 8.7799 | 8.6838 | 95.2972 | 95.1508 | -27.6627 | 95.5124 | 95.43 | 0.27924 | -27.7359 | 102.681 | 102.5848 | 0.027466 | 123.3215 | 123.3856 | 20.8008 | -0.073242 | 95.5078 | 95.4346 | 95.3888 | -28.0197 | 123.1979 | 123.0972 | 123.4314 | -20.5856
2562.5156 | 123.4497 | -93.9651 | 29.2648 | 0.09613 | 0.011177 | 0.0024311 | 0.011967 | -0.020407 | 0.001694 | 0.00084388 | 1.3842 | 0.020875 | -0.011927 | 0.010359 | -0.0037854 | 0.0085021 | 1.4603 | 1.5198 | 1.4008 | 1.4786 | 1.5839 | 1.4053 | 1.2314 | 29.3198 | 29.3472 | 29.3701 | 29.2786 | 29.1824 | 8.7753 | 8.6792 | 95.3705 | 95.1965 | -27.681 | 95.4849 | 95.4437 | 0.24719 | -27.8046 | 102.7405 | 102.6443 | 0.013732 | 123.2849 | 123.3353 | 20.6909 | -0.082398 | 95.549 | 95.4254 | 95.3659 | -28.0334 | 123.2437 | 123.1476 | 123.3124 | -20.5856
2563.5156 | 123.4863 | -93.988 | 29.187 | -0.071716 | 0.0071179 | 0.0030719 | 0.01154 | -0.019766 | -0.0012966 | 0.00084388 | 0.0032804 | 0.01938 | -0.012354 | 0.011854 | -0.003999 | 0.010425 | 1.5015 | 1.5701 | 1.4511 | 1.506 | 1.6022 | 1.4236 | 1.2543 | 29.3152 | 29.3793 | 29.3747 | 29.2099 | 29.1321 | 8.7799 | 8.6792 | 95.4117 | 95.2423 | -27.5848 | 95.5582 | 95.4941 | 0.25177 | -27.6855 | 102.7679 | 102.6672 | 0.022888 | 123.3032 | 123.3627 | 20.6955 | -0.054932 | 95.5902 | 95.4895 | 95.4391 | -27.9327 | 123.1979 | 123.1201 | 123.3673 | -20.5078
2564.5156 | 123.4039 | -94.0567 | 29.2419 | -0.1709 | 0.015877 | 0.0024311 | 0.013249 | -0.018912 | 0.004044 | 0.0029801 | -0.31715 | 0.019807 | -0.011713 | 0.011427 | 0.00091437 | 0.0063659 | 1.4328 | 1.4328 | 1.3046 | 1.4328 | 1.5976 | 1.3596 | 1.181 | 29.2236 | 29.3152 | 29.2694 | 29.2465 | 29.1641 | 8.7753 | 8.6746 | 95.4163 | 95.2377 | -27.6443 | 95.4895 | 95.4895 | 0.25177 | -27.8091 | 102.832 | 102.7313 | 0.004578 | 123.2803 | 123.3261 | 20.5948 | -0.077819 | 95.6543 | 95.4895 | 95.3613 | -28.0609 | 123.3032 | 123.2208 | 123.3719 | -20.5673
2565.5156 | 123.4497 | -94.043 | 29.155 | 0.10376 | 0.01075 | 0.0043537 | 0.00919 | -0.021048 | -0.0019376 | 0.0021255 | 0.033798 | 0.017884 | -0.013849 | 0.011854 | -0.0033582 | 0.011279 | 1.4236 | 1.5015 | 1.387 | 1.4374 | 1.593 | 1.3779 | 1.2222 | 29.2007 | 29.2831 | 29.3015 | 29.155 | 29.0588 | 8.7753 | 8.6746 | 95.4208 | 95.2652 | -27.5619 | 95.5444 | 95.4803 | 0.21515 | -27.7313 | 102.8183 | 102.7176 | 0 | 123.2437 | 123.3444 | 20.6268 | -0.09613 | 95.636 | 95.4666 | 95.43 | -27.9327 | 123.1979 | 123.1018 | 123.3261 | -20.4803
2566.5156 | 123.4726 | -94.0475 | 29.1504 | 0.20294 | 0.012886 | 0.0011493 | 0.012394 | -0.018698 | 0.0021214 | 0.0031937 | 0.18639 | 0.021516 | -0.012567 | 0.013136 | -0.0014356 | 0.012347 | 1.4969 | 1.561 | 1.4328 | 1.4832 | 1.5564 | 1.4053 | 1.2268 | 29.2374 | 29.306 | 29.3015 | 29.155 | 29.0405 | 8.7845 | 8.6746 | 95.4529 | 95.2744 | -27.594 | 95.6085 | 95.5307 | 0.25635 | -27.6535 | 102.832 | 102.7222 | 0.004577 | 123.2849 | 123.349 | 20.6268 | -0.10986 | 95.6039 | 95.5444 | 95.4803 | -27.9236 | 123.2025 | 123.0881 | 123.3536 | -20.4758
2567.5156 | 123.4451 | -94.1116 | 29.0817 | 0.13428 | 0.0079723 | 0.0032855 | 0.014317 | -0.01998 | 0.00062595 | 0.0034073 | 0.12535 | 0.019593 | -0.015131 | 0.012068 | -0.0033582 | 0.0085021 | 1.4236 | 1.4877 | 1.3824 | 1.4511 | 1.5793 | 1.387 | 1.2451 | 29.1367 | 29.3289 | 29.2236 | 29.1092 | 29.0085 | 8.7753 | 8.6838 | 95.4987 | 95.3567 | -27.5024 | 95.5994 | 95.5627 | 0.20599 | -27.6581 | 102.887 | 102.7954 | 0.027466 | 123.2483 | 123.3353 | 20.5399 | -0.073242 | 95.6909 | 95.5353 | 95.4941 | -27.8366 | 123.2208 | 123.1201 | 123.4406 | -20.3979
2568.5156 | 123.4406 | -94.1116 | 29.0451 | 0.2182 | 0.013099 | 0.0049945 | 0.011967 | -0.018698 | 0.0029758 | 0.0034073 | 0.17113 | 0.019166 | -0.013849 | 0.013136 | -0.0025036 | 0.0093567 | 1.4923 | 1.5564 | 1.4282 | 1.4877 | 1.5747 | 1.3962 | 1.2222 | 29.1595 | 29.2145 | 29.2191 | 29.068 | 28.9948 | 8.7845 | 8.6838 | 95.5078 | 95.3339 | -27.4704 | 95.668 | 95.5994 | 0.2655 | -27.5528 | 102.8961 | 102.7954 | 0.022888 | 123.2712 | 123.3307 | 20.5353 | -0.050354 | 95.6863 | 95.6039 | 95.5399 | -27.8229 | 123.1796 | 123.1064 | 123.3261 | -20.3613
2569.5312 | 123.4085 | -94.2261 | 29.0359 | -0.14801 | 0.01844 | 0.0022175 | 0.015599 | -0.019766 | 0.0042576 | 0.0046891 | -0.21034 | 0.020662 | -0.011072 | 0.013349 | -0.0012218 | 0.0050841 | 1.4648 | 1.4603 | 1.3504 | 1.4557 | 1.6113 | 1.3504 | 1.1902 | 29.0588 | 29.1458 | 29.0955 | 29.0771 | 28.981 | 8.7799 | 8.6838 | 95.5765 | 95.4163 | -27.4246 | 95.6863 | 95.6818 | 0.2655 | -27.5711 | 103.006 | 102.9099 | 0.041198 | 123.2849 | 123.3215 | 20.4117 | -0.054932 | 95.8374 | 95.6909 | 95.5765 | -27.8458 | 123.3032 | 123.2071 | 123.3719 | -20.3522
2570.5156 | 123.4909 | -94.2123 | 28.9352 | 0.20294 | 0.015236 | 8.1086e-05 | 0.01154 | -0.018057 | 0.001694 | 0.0057571 | -0.94276 | 0.021302 | -0.013636 | 0.013777 | -0.0029308 | 0.0097839 | 1.4969 | 1.5152 | 1.4191 | 1.4923 | 1.5518 | 1.3779 | 1.2177 | 29.0771 | 29.155 | 29.1367 | 28.9352 | 28.9032 | 8.7845 | 8.6838 | 95.5902 | 95.43 | -27.3834 | 95.7275 | 95.7047 | 0.27466 | -27.4384 | 102.9968 | 102.8961 | 0 | 123.2895 | 123.349 | 20.4529 | -0.032044 | 95.7642 | 95.7092 | 95.6314 | -27.7176 | 123.1476 | 123.1155 | 123.3673 | -20.2515
2571.5156 | 123.4406 | -94.2444 | 28.9581 | 0.21057 | 0.010536 | 0.0030719 | 0.010899 | -0.021048 | -0.0019376 | 0.0042619 | 0.2169 | 0.018953 | -0.013636 | 0.013777 | -0.0020764 | 0.0099975 | 1.4832 | 1.5335 | 1.4099 | 1.4786 | 1.5793 | 1.4008 | 1.2268 | 29.0314 | 29.0771 | 29.1 | 28.9719 | 28.8803 | 8.7799 | 8.6884 | 95.6451 | 95.4712 | -27.3788 | 95.7779 | 95.723 | 0.25177 | -27.475 | 103.0243 | 102.9327 | 0.013733 | 123.2758 | 123.3444 | 20.4117 | -0.07782 | 95.8237 | 95.7275 | 95.6543 | -27.7313 | 123.2162 | 123.1247 | 123.3215 | -20.2698
2572.5156 | 123.4497 | -94.2719 | 28.9124 | 0.22583 | 0.015022 | 0.0020037 | 0.01389 | -0.01998 | 0.0027622 | 0.0010575 | 0.1635 | 0.021302 | -0.012567 | 0.010786 | 5.9768e-05 | 0.0097839 | 1.4465 | 1.4557 | 1.3412 | 1.4374 | 1.5839 | 1.3779 | 1.1948 | 28.9948 | 29.0588 | 29.0405 | 28.9398 | 28.8574 | 8.7753 | 8.6838 | 95.6497 | 95.4666 | -27.3285 | 95.7275 | 95.7092 | 0.24262 | -27.4658 | 103.0472 | 102.9556 | 0.027465 | 123.2666 | 123.3124 | 20.3568 | -0.054932 | 95.8557 | 95.7184 | 95.6131 | -27.7176 | 123.2117 | 123.1293 | 123.3307 | -20.2286
2573.5156 | 123.4863 | -94.3314 | 28.8666 | 0.080872 | 0.013313 | 0.0020037 | 0.011754 | -0.01763 | -0.00044225 | 0.0029801 | 0.25505 | 0.020875 | -0.012995 | 0.012708 | -0.0016492 | 0.011066 | 1.4786 | 1.5335 | 1.4282 | 1.4786 | 1.5335 | 1.3779 | 1.2131 | 28.9719 | 29.0451 | 29.0543 | 28.8849 | 28.8071 | 8.7845 | 8.6792 | 95.7092 | 95.5444 | -27.3331 | 95.8649 | 95.8099 | 0.2655 | -27.388 | 103.1158 | 103.0106 | 0.018311 | 123.3032 | 123.3856 | 20.3751 | -0.059509 | 95.8649 | 95.8099 | 95.7596 | -27.6535 | 123.2162 | 123.1384 | 123.3765 | -20.1874
2574.5156 | 123.4085 | -94.3771 | 28.8391 | -0.20905 | 0.012459 | 0.0060627 | 0.00919 | -0.019553 | -0.0021512 | 0.0036209 | -0.20271 | 0.020234 | -0.014704 | 0.012922 | -0.0018628 | 0.010638 | 1.474 | 1.5198 | 1.387 | 1.4557 | 1.5793 | 1.3733 | 1.2222 | 28.8528 | 28.9948 | 28.949 | 28.8528 | 28.7796 | 8.7799 | 8.6746 | 95.7504 | 95.5994 | -27.2598 | 95.8969 | 95.8328 | 0.23346 | -27.3651 | 103.157 | 103.0518 | 0.013733 | 123.23 | 123.3261 | 20.2744 | -0.059509 | 95.9564 | 95.8511 | 95.7642 | -27.6169 | 123.23 | 123.1567 | 123.3719 | -20.1645
2575.5156 | 123.468 | -94.519 | 28.6743 | 0.16479 | 0.01609 | 0.0049945 | 0.00919 | -0.018485 | 0.0031894 | 0.0019119 | 0.19402 | 0.020021 | -0.013422 | 0.011213 | -0.0020764 | 0.0089295 | 1.4603 | 1.5244 | 1.4053 | 1.4648 | 1.5335 | 1.3733 | 1.2039 | 28.7888 | 28.8528 | 28.8574 | 28.688 | 28.624 | 8.7753 | 8.67 | 95.8923 | 95.723 | -27.1408 | 96.0434 | 95.9839 | 0.26093 | -27.2141 | 103.2944 | 103.1891 | 0.013733 | 123.3078 | 123.3765 | 20.1874 | -0.050354 | 96.0526 | 95.9793 | 95.9244 | -27.4704 | 123.2071 | 123.143 | 123.3719 | -20.0043
2576.5156 | 123.4772 | -94.4595 | 28.7613 | 0.042725 | 0.0094677 | 0.0049945 | 0.012822 | -0.019766 | -0.0032192 | 0.00041648 | -0.14168 | 0.019593 | -0.013208 | 0.0097176 | -0.0042126 | 0.0097839 | 1.4786 | 1.5427 | 1.4374 | 1.4923 | 1.5518 | 1.387 | 1.2177 | 28.8025 | 28.9352 | 28.9169 | 28.7338 | 28.6469 | 8.7799 | 8.6838 | 95.8466 | 95.6772 | -27.2095 | 96.0022 | 95.9518 | 0.27466 | -27.2827 | 103.2394 | 103.1433 | -0.027466 | 123.262 | 123.3765 | 20.2332 | -0.11444 | 96.0114 | 95.9381 | 95.8969 | -27.5436 | 123.1934 | 123.1064 | 123.3948 | -20.0775
2577.5156 | 123.468 | -94.693 | 28.4775 | 0.25635 | 0.016304 | 0.0030719 | 0.010685 | -0.018271 | 0.0019078 | 0.0040481 | 0.20164 | 0.018525 | -0.012354 | 0.013563 | -0.00015383 | 0.0095703 | 1.4694 | 1.4969 | 1.3779 | 1.474 | 1.5427 | 1.3824 | 1.2222 | 28.6057 | 28.6514 | 28.5416 | 28.5187 | 28.3813 | 8.7891 | 8.6792 | 96.0754 | 95.9152 | -26.9348 | 96.1899 | 96.167 | 0.25177 | -27.0081 | 103.4821 | 103.3722 | 0.041199 | 123.2986 | 123.2346 | 19.8624 | -0.09613 | 96.2357 | 96.1624 | 96.0709 | -27.2552 | 123.2117 | 123.0743 | 123.3444 | -19.7983
2578.5156 | 123.349 | -94.6838 | 28.5873 | 0.16479 | 0.018867 | 0.0026447 | 0.015812 | -0.019126 | 0.003403 | 0.0046891 | -0.23323 | 0.021516 | -0.011713 | 0.0097176 | 0.00070077 | 0.0091431 | 1.3962 | 1.3504 | 1.2726 | 1.3962 | 1.6159 | 1.3458 | 1.1856 | 28.5416 | 28.6514 | 28.6102 | 28.624 | 28.537 | 8.7845 | 8.6792 | 96.0297 | 95.8694 | -26.9714 | 96.0342 | 96.08 | 0.21057 | -27.1912 | 103.4683 | 103.363 | 0.036621 | 123.2254 | 123.2941 | 19.931 | -0.050354 | 96.2997 | 96.08 | 95.9564 | -27.4017 | 123.3078 | 123.2208 | 123.3353 | -19.9081
2579.5156 | 123.436 | -94.5236 | 28.6926 | 0.20294 | 0.01609 | 0.0039263 | 0.011326 | -0.018912 | 0.002335 | 0.0049027 | 0.20927 | 0.021302 | -0.011713 | 0.012281 | -0.0033582 | 0.0099975 | 1.4145 | 1.4191 | 1.3184 | 1.4191 | 1.5839 | 1.3504 | 1.1993 | 28.7476 | 28.775 | 28.7888 | 28.7201 | 28.6469 | 8.7708 | 8.6838 | 95.874 | 95.723 | -27.1088 | 95.9427 | 95.9427 | 0.21973 | -27.2781 | 103.2944 | 103.2074 | 0.027466 | 123.2712 | 123.3124 | 20.105 | -0.045776 | 96.1075 | 95.9381 | 95.842 | -27.4933 | 123.2437 | 123.1705 | 123.2986 | -20.0089
2580.5156 | 123.3673 | -94.6106 | 28.6469 | 0.12665 | 0.015663 | 8.1086e-05 | 0.01389 | -0.019339 | 0.003403 | 0.0031937 | -0.027237 | 0.021089 | -0.010431 | 0.010999 | -0.0031446 | 0.0099975 | 1.3779 | 1.3916 | 1.2909 | 1.5747 | 1.6022 | 1.355 | 1.181 | 28.5873 | 28.7018 | 28.6606 | 28.6972 | 28.6102 | 8.7753 | 8.6746 | 95.9656 | 95.7916 | -27.0447 | 96.0022 | 96.1853 | 0.39368 | -27.269 | 103.3859 | 103.2852 | 0.050354 | 123.1979 | 123.2712 | 19.986 | -0.036622 | 96.2128 | 95.9885 | 95.9015 | -27.4658 | 123.3078 | 123.2208 | 123.3124 | -19.9722
2581.5312 | 123.3673 | -94.7708 | 28.5278 | 0.29449 | 0.012459 | 0.0028583 | 0.013249 | -0.021475 | -0.0019376 | 0.0044755 | -0.12642 | 0.019807 | -0.010645 | 0.014204 | -0.0048534 | 0.0087157 | 1.3824 | 1.4008 | 1.2726 | 1.3916 | 1.6113 | 1.3504 | 1.181 | 28.4729 | 28.5782 | 28.537 | 28.537 | 28.4683 | 8.7845 | 8.6792 | 96.1212 | 95.9518 | -26.9165 | 96.1716 | 96.1624 | 0.21057 | -27.1454 | 103.5553 | 103.45 | 0.009155 | 123.2437 | 123.3078 | 19.8578 | -0.059509 | 96.3821 | 96.1533 | 96.0434 | -27.3468 | 123.3078 | 123.2391 | 123.349 | -19.8486
2582.5156 | 123.3582 | -94.7067 | 28.5873 | 0.11139 | 0.021217 | 8.1086e-05 | 0.014531 | -0.01763 | 0.0038304 | 0.0055435 | 0.026169 | 0.020234 | -0.010431 | 0.010999 | -0.0016492 | 0.010425 | 1.3596 | 1.387 | 1.2772 | 1.387 | 1.5747 | 1.3367 | 1.1536 | 28.4958 | 28.5828 | 28.5553 | 28.6011 | 28.4866 | 8.7799 | 8.6792 | 96.0434 | 95.8603 | -27.0126 | 96.0938 | 96.0938 | 0.23346 | -27.2278 | 103.4866 | 103.3859 | 0.013733 | 123.2025 | 123.262 | 19.8761 | -0.10071 | 96.2814 | 96.0663 | 95.9839 | -27.4338 | 123.3078 | 123.1934 | 123.2895 | -19.9081
2583.5156 | 123.3719 | -94.78 | 28.4958 | -0.17853 | 0.016731 | 0.00072209 | 0.013463 | -0.020621 | 0.00019875 | 0.0040481 | 0.15587 | 0.02173 | -0.010645 | 0.013777 | -0.0029308 | 0.010211 | 1.3687 | 1.3641 | 1.268 | 1.387 | 1.5839 | 1.3367 | 1.1856 | 28.4454 | 28.537 | 28.5233 | 28.537 | 28.4271 | 8.7753 | 8.6746 | 96.1166 | 95.9656 | -26.9119 | 96.1441 | 96.167 | 0.20142 | -27.1271 | 103.5553 | 103.4546 | 0.041198 | 123.2254 | 123.3032 | 19.8486 | -0.068665 | 96.3638 | 96.1487 | 96.048 | -27.3102 | 123.317 | 123.2071 | 123.317 | -19.8212
2584.5156 | 123.3765 | -94.7205 | 28.537 | 0.012207 | 0.018867 | 0.0020037 | 0.012608 | -0.019126 | 0.0036166 | 0.0046891 | 0.0032804 | 0.020448 | -0.008295 | 0.013563 | -0.00058103 | 0.0099975 | 1.4282 | 1.442 | 1.3229 | 1.4145 | 1.5747 | 1.3504 | 1.181 | 28.5141 | 28.5965 | 28.569 | 28.5461 | 28.4958 | 8.7799 | 8.6746 | 96.0709 | 95.9015 | -26.9623 | 96.1624 | 96.1349 | 0.23346 | -27.1088 | 103.5004 | 103.3951 | 0.009156 | 123.2346 | 123.2895 | 19.8944 | -0.041198 | 96.2952 | 96.1487 | 96.0434 | -27.356 | 123.2666 | 123.2162 | 123.317 | -19.8624
2585.5156 | 123.3124 | -94.8395 | 28.4317 | 0.065613 | 0.019295 | 0.00029489 | 0.014103 | -0.018485 | 0.0010532 | 0.0040481 | 0.10246 | 0.021943 | -0.0080814 | 0.012495 | -0.0020764 | 0.010852 | 1.355 | 1.3504 | 1.2314 | 1.387 | 1.5839 | 1.3275 | 1.1719 | 28.3447 | 28.4134 | 28.1937 | 28.3905 | 28.3218 | 8.7799 | 8.6838 | 96.167 | 96.0114 | -26.8478 | 96.1899 | 96.2265 | 0.21515 | -27.0767 | 103.6194 | 103.5233 | -0.041199 | 123.1842 | 123.0331 | 19.5099 | -0.10986 | 96.4233 | 96.1945 | 96.0709 | -27.2598 | 123.23 | 123.1613 | 123.2529 | -19.7479
2586.5156 | 123.4222 | -94.8944 | 28.3676 | -0.11749 | 0.017799 | 0.0037127 | 0.013249 | -0.017417 | -0.00044225 | 0.0025529 | -0.12642 | 0.021943 | -0.010004 | 0.010786 | -0.0033582 | 0.0089295 | 1.3824 | 1.4053 | 1.3046 | 1.4236 | 1.593 | 1.3321 | 1.1719 | 28.3539 | 28.4775 | 28.45 | 28.3951 | 28.3264 | 8.7891 | 8.6792 | 96.2265 | 96.0663 | -26.7746 | 96.2997 | 96.3181 | 0.25177 | -26.9852 | 103.6835 | 103.5736 | 0.027466 | 123.2483 | 123.3444 | 19.7708 | -0.041199 | 96.4874 | 96.2769 | 96.199 | -27.1957 | 123.2895 | 123.2208 | 123.3719 | -19.6884
2587.5156 | 123.3582 | -94.8395 | 28.45 | 0.14954 | 0.01609 | 0.0032855 | 0.013676 | -0.019126 | 0.0031894 | 0.0044755 | 0.12535 | 0.020234 | -0.0087222 | 0.014417 | -0.0010082 | 0.013843 | 1.3412 | 1.355 | 1.2497 | 1.3733 | 1.593 | 1.3275 | 1.1627 | 28.2669 | 28.4958 | 28.6331 | 28.4592 | 28.3813 | 8.7799 | 8.6792 | 96.167 | 96.0022 | -26.857 | 96.1945 | 96.2128 | 0.21057 | -27.1088 | 103.6194 | 103.5187 | 0.009155 | 123.1064 | 123.4726 | 19.9539 | -0.068664 | 96.4325 | 96.1807 | 96.0892 | -27.2873 | 123.2986 | 123.2208 | 123.3353 | -19.7708
2588.5156 | 123.3719 | -95.0409 | 28.2028 | -0.02594 | 0.017799 | 0.0024311 | 0.012608 | -0.018057 | 0.0014804 | 0.0021255 | 0.026169 | 0.019807 | -0.0095768 | 0.014631 | -0.00229 | 0.010425 | 1.4008 | 1.4191 | 1.3092 | 1.4053 | 1.5747 | 1.3367 | 1.1627 | 28.1662 | 28.2669 | 28.2532 | 28.2303 | 28.1662 | 8.7799 | 8.6792 | 96.3776 | 96.2036 | -26.6281 | 96.46 | 96.4462 | 0.24261 | -26.8021 | 103.8208 | 103.7201 | 0.027466 | 123.2071 | 123.2941 | 19.574 | -0.036621 | 96.6156 | 96.4417 | 96.3501 | -27.0401 | 123.2712 | 123.2071 | 123.3078 | -19.5236
2589.5156 | 123.3719 | -94.986 | 28.2806 | 0.065613 | 0.018226 | 0.0022175 | 0.014531 | -0.017844 | 0.0025486 | 0.0025529 | 0.056686 | 0.021089 | -0.009363 | 0.014204 | -0.0014356 | 0.010425 | 1.3779 | 1.3779 | 1.2772 | 1.3962 | 1.5518 | 1.3412 | 1.1581 | 28.2074 | 28.331 | 28.3035 | 28.3218 | 28.2578 | 8.7708 | 8.67 | 96.3272 | 96.1441 | -26.7288 | 96.3638 | 96.3821 | 0.23804 | -26.9028 | 103.7567 | 103.656 | 0.041198 | 123.1934 | 123.2895 | 19.6335 | -0.022889 | 96.5378 | 96.3638 | 96.2631 | -27.1225 | 123.3078 | 123.2437 | 123.317 | -19.6106
2590.5156 | 123.4039 | -94.931 | 28.3264 | -0.17853 | 0.016945 | 0.0013629 | 0.015385 | -0.019766 | 0.0010532 | 0.0034073 | -0.10353 | 0.020662 | -0.010645 | 0.009504 | -0.0033582 | 0.011279 | 1.3824 | 1.4008 | 1.3046 | 1.4236 | 1.5701 | 1.3275 | 1.181 | 28.2944 | 28.4271 | 28.3905 | 28.3401 | 28.2898 | 8.7845 | 8.6838 | 96.2585 | 96.1121 | -26.7563 | 96.3318 | 96.3547 | 0.24262 | -26.944 | 103.7155 | 103.6148 | 0.013733 | 123.2254 | 123.3215 | 19.7067 | -0.036621 | 96.5012 | 96.3135 | 96.2357 | -27.1454 | 123.2712 | 123.2208 | 123.3582 | -19.6426
2591.5312 | 123.3856 | -94.9905 | 28.2898 | -0.17853 | 0.012031 | 0.0013629 | 0.014317 | -0.018271 | -0.004501 | 0.0010575 | -0.073013 | 0.018312 | -0.0097904 | 0.012922 | -0.007417 | 0.0091431 | 1.4008 | 1.5015 | 1.387 | 1.4557 | 1.5564 | 1.3504 | 1.1993 | 28.2394 | 28.3951 | 28.363 | 28.2898 | 28.2303 | 8.7799 | 8.6792 | 96.3409 | 96.1899 | -26.7334 | 96.492 | 96.4462 | 0.25635 | -26.889 | 103.7704 | 103.6697 | 0 | 123.23 | 123.3536 | 19.6838 | -0.059509 | 96.5469 | 96.3913 | 96.3776 | -27.0905 | 123.2803 | 123.2208 | 123.3856 | -19.6106
2592.5156 | 123.3948 | -95.0638 | 28.2394 | -0.16327 | 0.015449 | 0.0043537 | 0.013463 | -0.019126 | 0.00041235 | -0.00065152 | -0.1722 | 0.020021 | -0.011713 | 0.012495 | -0.0027172 | 0.0095703 | 1.355 | 1.3962 | 1.2817 | 1.4053 | 1.5839 | 1.3275 | 1.1673 | 28.1433 | 28.2852 | 28.2532 | 28.2669 | 28.1845 | 8.7799 | 8.6792 | 96.3913 | 96.2311 | -26.6556 | 96.46 | 96.4691 | 0.23804 | -26.8845 | 103.8437 | 103.743 | 0.027466 | 123.2071 | 123.317 | 19.574 | -0.054932 | 96.6476 | 96.4188 | 96.3455 | -27.0721 | 123.3307 | 123.2483 | 123.349 | -19.5602
2593.5156 | 123.3902 | -95.1096 | 28.1754 | -0.02594 | 0.017586 | 0.0022175 | 0.01389 | -0.019126 | 0.0021214 | 0.0019119 | -0.027237 | 0.020448 | -0.008295 | 0.014204 | -0.0016492 | 0.010211 | 1.4099 | 1.442 | 1.3184 | 1.4145 | 1.561 | 1.3275 | 1.1536 | 28.1342 | 28.2166 | 28.1891 | 28.1616 | 28.1204 | 8.7845 | 8.6792 | 96.4371 | 96.2631 | -26.6144 | 96.5515 | 96.524 | 0.26093 | -26.7654 | 103.894 | 103.7888 | -0.013733 | 123.2437 | 123.2986 | 19.5099 | -0.054932 | 96.6705 | 96.5195 | 96.4279 | -27.0218 | 123.2712 | 123.23 | 123.3261 | -19.4962
2594.5156 | 123.3948 | -95.0867 | 28.1799 | -0.14038 | 0.01609 | 0.0026447 | 0.016453 | -0.015067 | 0.00062595 | 0.0021255 | -0.12642 | 0.01938 | -0.010218 | 0.011427 | -0.0025036 | 0.010638 | 1.3412 | 1.3824 | 1.2772 | 1.4008 | 1.5701 | 1.3184 | 1.1627 | 28.1113 | 28.2211 | 28.2074 | 28.2028 | 28.1433 | 8.7845 | 8.6792 | 96.405 | 96.2494 | -26.6098 | 96.4691 | 96.4874 | 0.23804 | -26.8387 | 103.8712 | 103.7659 | 0.022888 | 123.1979 | 123.2941 | 19.5282 | -0.036621 | 96.6568 | 96.4279 | 96.3638 | -27.0172 | 123.2895 | 123.23 | 123.3078 | -19.5007
2595.5156 | 123.3627 | -95.1736 | 28.1342 | 0.057983 | 0.018867 | 0.0015765 | 0.017521 | -0.018271 | 0.0031894 | 0.0029801 | 0.087204 | 0.021943 | -0.011713 | 0.011854 | -0.00015383 | 0.0089295 | 1.3641 | 1.3458 | 1.2634 | 1.3687 | 1.5747 | 1.3229 | 1.1536 | 28.0243 | 28.1113 | 28.1204 | 28.1113 | 28.0746 | 8.7799 | 8.6746 | 96.4966 | 96.3272 | -26.5594 | 96.5195 | 96.5424 | 0.21515 | -26.77 | 103.9536 | 103.8483 | -0.022888 | 123.1979 | 123.2941 | 19.4458 | -0.059509 | 96.7484 | 96.5378 | 96.4371 | -26.9806 | 123.2849 | 123.2483 | 123.2849 | -19.4595
2596.5156 | 123.3902 | -95.1782 | 28.1021 | -0.18616 | 0.01609 | 0.0043537 | 0.01389 | -0.01998 | 0.0012668 | -0.00022432 | -0.12642 | 0.019593 | -0.011286 | 0.011427 | -0.0025036 | 0.0093567 | 1.3504 | 1.387 | 1.2909 | 1.3824 | 1.5793 | 1.3138 | 1.1398 | 28.0106 | 28.1479 | 28.1113 | 28.0975 | 28.0563 | 8.7799 | 8.6746 | 96.492 | 96.3181 | -26.5228 | 96.5652 | 96.5607 | 0.24261 | -26.7517 | 103.9581 | 103.8528 | -0.004578 | 123.1888 | 123.2895 | 19.4366 | -0.045777 | 96.7575 | 96.5286 | 96.4691 | -26.9623 | 123.2758 | 123.2346 | 123.3261 | -19.4275
2597.5156 | 123.4268 | -95.1645 | 28.0792 | -0.15564 | 0.017372 | 0.0024311 | 0.013463 | -0.020407 | 0.0021214 | 0.0023391 | -0.14931 | 0.020662 | -0.010004 | 0.013777 | -0.0027172 | 0.010211 | 1.3641 | 1.4008 | 1.2955 | 1.4099 | 1.5518 | 1.3184 | 1.1536 | 28.0334 | 28.1616 | 28.1158 | 28.0884 | 28.0289 | 8.7799 | 8.6746 | 96.4828 | 96.3181 | -26.5274 | 96.5652 | 96.5744 | 0.25635 | -26.7151 | 103.9444 | 103.8391 | 0.009155 | 123.1979 | 123.2803 | 19.4412 | -0.050354 | 96.7163 | 96.5286 | 96.46 | -26.9257 | 123.2529 | 123.1934 | 123.3261 | -19.4046
2598.5156 | 123.349 | -95.2835 | 28.0334 | -0.1709 | 0.012672 | 0.0041401 | 0.013035 | -0.019126 | -0.0019376 | 0.00041648 | -0.24849 | 0.017671 | -0.013422 | 0.012068 | -0.0035718 | 0.011279 | 1.3458 | 1.4465 | 1.3275 | 1.4053 | 1.561 | 1.3275 | 1.1581 | 27.9282 | 28.0655 | 28.0472 | 28.0151 | 27.9556 | 8.7845 | 8.6746 | 96.611 | 96.4416 | -26.4725 | 96.73 | 96.6888 | 0.24719 | -26.6876 | 104.068 | 103.9581 | -0.01831 | 123.2117 | 123.3307 | 19.3726 | -0.07782 | 96.8445 | 96.6293 | 96.611 | -26.8753 | 123.2986 | 123.2391 | 123.349 | -19.3588
2599.5156 | 123.3673 | -95.3247 | 27.9785 | 0.12665 | 0.022926 | 0.0020037 | 0.020085 | -0.020194 | 0.002335 | 0.0034073 | 0.094833 | 0.018953 | -0.009363 | 0.014845 | -0.00058103 | 0.0091431 | 1.2909 | 1.3916 | 1.2634 | 1.3641 | 1.5884 | 1.3321 | 1.1673 | 27.919 | 27.9739 | 27.9922 | 27.9877 | 27.9419 | 8.7799 | 8.6746 | 96.6568 | 96.492 | -26.3901 | 96.7163 | 96.6888 | 0.19684 | -26.6876 | 104.1046 | 103.9993 | 0.009155 | 123.2437 | 123.317 | 19.3176 | -0.036621 | 96.9131 | 96.6156 | 96.5881 | -26.8112 | 123.3124 | 123.2666 | 123.2986 | -19.3039
2600.5156 | 123.3536 | -95.2698 | 28.006 | 0.6073 | 0.017158 | 0.0017901 | 0.016453 | -0.019553 | 0.00019875 | 0.0016983 | -0.14168 | 0.020662 | -0.011286 | 0.015913 | -0.0037854 | 0.010211 | 1.3321 | 1.3641 | 1.2817 | 1.3824 | 1.6113 | 1.3321 | 1.1673 | 27.9007 | 28.0197 | 27.9968 | 28.0014 | 27.951 | 8.7799 | 8.6838 | 96.6019 | 96.4371 | -26.3947 | 96.6339 | 96.6522 | 0.21515 | -26.6739 | 104.0497 | 103.9536 | -0.004577 | 123.1705 | 123.2666 | 19.313 | -0.054931 | 96.8811 | 96.6019 | 96.5515 | -26.8387 | 123.2712 | 123.2208 | 123.2895 | -19.3222
2601.5312 | 123.381 | -95.3979 | 27.9053 | -0.18616 | 0.012672 | 0.0041401 | 0.012181 | -0.018485 | -0.001083 | 0.0016983 | -0.073013 | 0.01703 | -0.01214 | 0.012495 | -0.0048534 | 0.0097839 | 1.3687 | 1.4465 | 1.3046 | 1.4053 | 1.5747 | 1.3275 | 1.1765 | 27.8183 | 27.951 | 27.9282 | 27.9144 | 27.8366 | 8.7753 | 8.6838 | 96.7255 | 96.5744 | -26.3306 | 96.8445 | 96.8033 | 0.22888 | -26.5366 | 104.1733 | 104.0817 | 0.009156 | 123.2162 | 123.3261 | 19.2444 | -0.068664 | 96.9727 | 96.7667 | 96.7026 | -26.7288 | 123.3124 | 123.2346 | 123.349 | -19.2215
2602.5156 | 123.3673 | -95.4987 | 27.8137 | -0.27771 | 0.01374 | 0.0034991 | 0.01389 | -0.019126 | 0.00019875 | -1.0724e-05 | -0.14931 | 0.01938 | -0.010218 | 0.013136 | -0.0050672 | 0.0089295 | 1.3412 | 1.3824 | 1.2726 | 1.3779 | 1.5839 | 1.3275 | 1.1536 | 27.6947 | 27.8046 | 27.7908 | 27.8137 | 27.713 | 8.7799 | 8.6792 | 96.8262 | 96.6522 | -26.2299 | 96.8811 | 96.8765 | 0.2243 | -26.4725 | 104.2786 | 104.1779 | 0 | 123.1934 | 123.2895 | 19.1116 | -0.10071 | 97.0825 | 96.8399 | 96.7712 | -26.6602 | 123.3124 | 123.2117 | 123.3032 | -19.1345
2603.5156 | 123.4085 | -95.5215 | 27.7863 | -0.13275 | 0.014381 | 0.0034991 | 0.015599 | -0.020194 | 0.00083955 | 0.0014847 | -0.15694 | 0.019807 | -0.0095768 | 0.012281 | -0.0042126 | 0.0093567 | 1.3367 | 1.3733 | 1.2589 | 1.387 | 1.5747 | 1.3 | 1.1536 | 27.7039 | 27.832 | 27.8046 | 27.8183 | 27.713 | 8.7753 | 8.6792 | 96.8216 | 96.6751 | -26.2115 | 96.8948 | 96.9086 | 0.23346 | -26.4496 | 104.2969 | 104.2007 | 0.032043 | 123.2254 | 123.3261 | 19.1254 | -0.073242 | 97.0963 | 96.8582 | 96.7804 | -26.6327 | 123.3398 | 123.2346 | 123.3536 | -19.1071
2604.5156 | 123.3627 | -95.5582 | 27.7679 | -0.20905 | 0.012672 | 0.0039263 | 0.012822 | -0.021475 | -0.0023648 | 0.0021255 | -0.19508 | 0.021089 | -0.011072 | 0.012922 | -0.0031446 | 0.011279 | 1.3367 | 1.4236 | 1.2863 | 1.3824 | 1.5701 | 1.3092 | 1.1581 | 27.6764 | 27.7863 | 27.7817 | 27.7679 | 27.7313 | 8.7845 | 8.6838 | 96.8674 | 96.7163 | -26.1978 | 96.9818 | 96.9406 | 0.2243 | -26.4313 | 104.3427 | 104.2419 | 0 | 123.2346 | 123.3398 | 19.0979 | -0.036621 | 97.1283 | 96.8948 | 96.8445 | -26.6098 | 123.3261 | 123.2895 | 123.3444 | -19.0842
2605.5156 | 123.381 | -95.5765 | 27.6947 | -0.0030518 | 0.021217 | 0.00093569 | 0.014958 | -0.020835 | 0.0029758 | -0.00086512 | 0.018539 | 0.020021 | -0.010645 | 0.012708 | -0.0029308 | 0.0078613 | 1.3824 | 1.3962 | 1.2726 | 1.3779 | 1.5427 | 1.3092 | 1.1444 | 27.6306 | 27.7313 | 27.6901 | 27.7222 | 27.6352 | 8.7799 | 8.6746 | 96.8857 | 96.7209 | -26.152 | 96.9727 | 96.9543 | 0.23346 | -26.3123 | 104.3564 | 104.2511 | 0.027466 | 123.2071 | 123.2666 | 19.0155 | -0.059509 | 97.1191 | 96.9589 | 96.8491 | -26.5503 | 123.2986 | 123.2117 | 123.3078 | -19.0201
2606.5156 | 123.4818 | -95.5353 | 27.6535 | -0.056458 | 0.0088269 | 0.0045673 | 0.010258 | -0.018698 | -0.0070644 | -0.0012923 | 0.049057 | 0.018953 | -0.012995 | 0.012495 | -0.0059216 | 0.011707 | 1.4145 | 1.5198 | 1.4145 | 1.4557 | 1.5427 | 1.355 | 1.1902 | 27.7451 | 27.8595 | 27.8458 | 27.6718 | 27.6123 | 8.7753 | 8.6792 | 96.8903 | 96.7255 | -26.1108 | 97.0551 | 96.991 | 0.2655 | -26.239 | 104.3106 | 104.2145 | 0.018311 | 123.2803 | 123.381 | 19.1666 | -0.041198 | 97.0779 | 96.9498 | 96.9498 | -26.4633 | 123.2071 | 123.1476 | 123.3948 | -18.9743
2607.5156 | 123.3765 | -95.6039 | 27.6718 | -0.19379 | 0.012886 | 0.0024311 | 0.013035 | -0.021475 | -0.0017238 | -0.00043792 | -0.11879 | 0.020448 | -0.0091494 | 0.012922 | -0.0020764 | 0.0099975 | 1.3916 | 1.4694 | 1.3367 | 1.4191 | 1.5289 | 1.3092 | 1.1627 | 27.6306 | 27.7451 | 27.6993 | 27.6627 | 27.6031 | 8.7845 | 8.6792 | 96.9131 | 96.7667 | -26.1429 | 97.0734 | 97.023 | 0.25635 | -26.2802 | 104.3884 | 104.2831 | -0.009155 | 123.2346 | 123.3032 | 19.0201 | -0.068665 | 97.1329 | 96.9955 | 96.9406 | -26.5091 | 123.2666 | 123.2071 | 123.349 | -18.9926
2608.5156 | 123.468 | -95.6223 | 27.5848 | 0.019836 | 0.0096813 | 0.0015765 | 0.010472 | -0.021048 | -0.0040738 | 0.0012711 | 0.064316 | 0.015962 | -0.010645 | 0.011427 | -0.0050672 | 0.0099975 | 1.3596 | 1.4465 | 1.3412 | 1.4282 | 1.561 | 1.3733 | 1.1856 | 27.6352 | 27.7451 | 27.7588 | 27.5894 | 27.5528 | 8.7708 | 8.6792 | 96.9955 | 96.8079 | -26.0239 | 97.0688 | 97.0505 | 0.24262 | -26.2253 | 104.393 | 104.3015 | 0.004578 | 123.2574 | 123.381 | 19.0796 | -0.032044 | 97.1832 | 96.9818 | 96.9635 | -26.3992 | 123.2117 | 123.175 | 123.3673 | -18.9056
2609.5156 | 123.4589 | -95.6451 | 27.5848 | -0.16327 | 0.012031 | 0.0022175 | 0.01389 | -0.019766 | -0.0019376 | -0.00022432 | -0.088272 | 0.018312 | -0.011072 | 0.013777 | -0.0044262 | 0.0097839 | 1.4328 | 1.5015 | 1.387 | 1.4511 | 1.5427 | 1.3504 | 1.1948 | 27.6535 | 27.7817 | 27.7451 | 27.5894 | 27.5162 | 8.7845 | 8.6838 | 96.9955 | 96.8399 | -26.0422 | 97.1466 | 97.0963 | 0.25635 | -26.152 | 104.4296 | 104.3289 | 0.004578 | 123.2986 | 123.3902 | 19.0613 | -0.068665 | 97.1878 | 97.0779 | 97.0322 | -26.3901 | 123.2346 | 123.1613 | 123.4268 | -18.9011
2610.5156 | 123.4909 | -95.6818 | 27.5345 | 0.019836 | 0.0092541 | 0.0024311 | 0.012822 | -0.021048 | -0.0032192 | 0.0012711 | 0.033798 | 0.016603 | -0.011286 | 0.011213 | -0.005708 | 0.010211 | 1.3733 | 1.4557 | 1.3458 | 1.4328 | 1.5427 | 1.3504 | 1.1765 | 27.5757 | 27.6672 | 27.6718 | 27.5299 | 27.4658 | 8.7708 | 8.67 | 97.0322 | 96.8582 | -25.9918 | 97.1375 | 97.1146 | 0.25635 | -26.1612 | 104.4525 | 104.3518 | -0.004578 | 123.2574 | 123.3536 | 19.0018 | -0.068665 | 97.2244 | 97.0551 | 97.0276 | -26.358 | 123.2117 | 123.1476 | 123.349 | -18.8644
2611.5312 | 123.4543 | -95.7275 | 27.4841 | 0.15717 | 0.012031 | 0.0028583 | 0.010899 | -0.022544 | 0.00041235 | -0.00086512 | 0.20164 | 0.020448 | -0.014704 | 0.011427 | -0.00079463 | 0.0085021 | 1.4282 | 1.4786 | 1.3687 | 1.4282 | 1.5244 | 1.3412 | 1.1765 | 27.5345 | 27.5803 | 27.5986 | 27.475 | 27.388 | 8.7799 | 8.6746 | 97.0688 | 96.904 | -25.9598 | 97.2061 | 97.1558 | 0.25177 | -26.0559 | 104.5074 | 104.4022 | -0.009155 | 123.262 | 123.3261 | 18.924 | -0.096131 | 97.2519 | 97.1558 | 97.0963 | -26.3077 | 123.2025 | 123.1155 | 123.3078 | -18.8095
2612.5156 | 123.4543 | -95.7733 | 27.4338 | 0.088501 | 0.0094677 | 0.0041401 | 0.013249 | -0.019126 | -0.00022865 | 0.00084388 | -0.85121 | 0.018525 | -0.012354 | 0.012922 | -0.0031446 | 0.0095703 | 1.3779 | 1.4236 | 1.3321 | 1.4008 | 1.5381 | 1.3321 | 1.1627 | 27.4384 | 27.5848 | 27.5711 | 27.4384 | 27.3605 | 8.7845 | 8.6792 | 97.1054 | 96.936 | -25.8957 | 97.197 | 97.1741 | 0.23804 | -26.0559 | 104.5578 | 104.4525 | 0.004577 | 123.2117 | 123.3444 | 18.8919 | -0.073242 | 97.3114 | 97.1512 | 97.1054 | -26.2711 | 123.2117 | 123.1338 | 123.3582 | -18.7546
2613.5156 | 123.4818 | -95.8099 | 27.4109 | 0.012207 | 0.0088269 | 0.0037127 | 0.013249 | -0.01998 | -0.0019376 | 0.00041648 | 0.0032804 | 0.018953 | -0.013636 | 0.014631 | -0.0035718 | 0.0097839 | 1.4282 | 1.4923 | 1.3641 | 1.4374 | 1.5381 | 1.3504 | 1.181 | 27.5024 | 27.5894 | 27.5848 | 27.4475 | 27.3605 | 8.7753 | 8.6792 | 97.1603 | 96.991 | -25.8728 | 97.3022 | 97.2473 | 0.25635 | -25.9827 | 104.5853 | 104.4891 | 0.036621 | 123.3124 | 123.3948 | 18.9056 | -0.050354 | 97.348 | 97.2382 | 97.1741 | -26.2299 | 123.2574 | 123.1705 | 123.3994 | -18.7317
2614.5156 | 123.4589 | -95.8282 | 27.3972 | 0.088501 | 0.010963 | 0.0052081 | 0.014531 | -0.018271 | -0.0017238 | 0.00084388 | -0.15694 | 0.020234 | -0.012567 | 0.011427 | -0.0031446 | 0.0082885 | 1.4008 | 1.4236 | 1.3275 | 1.387 | 1.5244 | 1.3412 | 1.1765 | 27.4063 | 27.5024 | 27.5024 | 27.3834 | 27.301 | 8.7753 | 8.6838 | 97.1695 | 97.0047 | -25.8728 | 97.2519 | 97.2153 | 0.21057 | -25.9964 | 104.6036 | 104.512 | -0.013733 | 123.2346 | 123.3307 | 18.8187 | -0.096131 | 97.3526 | 97.229 | 97.1558 | -26.2207 | 123.2117 | 123.1293 | 123.3307 | -18.7134
2615.5156 | 123.4726 | -95.8603 | 27.3514 | -0.0030518 | 0.0098951 | 0.0032855 | 0.011754 | -0.021048 | -0.0023648 | 0.0014847 | -0.011978 | 0.018525 | -0.011927 | 0.011427 | -0.0031446 | 0.0099975 | 1.4328 | 1.4923 | 1.3641 | 1.4328 | 1.5472 | 1.3458 | 1.1719 | 27.4429 | 27.5116 | 27.4887 | 27.3331 | 27.2736 | 8.7799 | 8.6792 | 97.2061 | 97.0322 | -25.8041 | 97.3526 | 97.2931 | 0.26093 | -25.9186 | 104.6402 | 104.5395 | -0.01831 | 123.3032 | 123.349 | 18.8095 | -0.077819 | 97.4075 | 97.2931 | 97.2244 | -26.1795 | 123.1934 | 123.1339 | 123.3719 | -18.6722
2616.5156 | 123.4634 | -95.9152 | 27.3193 | 0.15717 | 0.010963 | 0.0032855 | 0.014958 | -0.019553 | 0.001694 | 0.00041648 | 0.20164 | 0.018953 | -0.0085086 | 0.011427 | -0.0025036 | 0.0080749 | 1.4374 | 1.4648 | 1.3687 | 1.4191 | 1.5152 | 1.3321 | 1.1719 | 27.3788 | 27.4246 | 27.4384 | 27.3285 | 27.2781 | 8.7753 | 8.6746 | 97.2473 | 97.0871 | -25.8041 | 97.3801 | 97.3343 | 0.24719 | -25.882 | 104.6906 | 104.5898 | 0.009155 | 123.2941 | 123.3536 | 18.7637 | -0.041199 | 97.4304 | 97.3526 | 97.2839 | -26.1475 | 123.2437 | 123.1934 | 123.3398 | -18.6447
2617.5156 | 123.4497 | -95.929 | 27.2873 | 0.46997 | 0.0094677 | 0.0041401 | 0.011967 | -0.021475 | 0.00062595 | 0.0010575 | 0.064316 | 0.017457 | -0.010645 | 0.011427 | -0.0016492 | 0.0099975 | 1.3779 | 1.4236 | 1.3275 | 1.3962 | 1.5106 | 1.3184 | 1.149 | 27.3422 | 27.4109 | 27.4246 | 27.301 | 27.2369 | 8.7799 | 8.6838 | 97.2473 | 97.0779 | -25.7767 | 97.3526 | 97.3251 | 0.24719 | -25.9094 | 104.7089 | 104.6127 | 0.013733 | 123.2712 | 123.3536 | 18.7408 | -0.050354 | 97.4396 | 97.3068 | 97.2565 | -26.1383 | 123.23 | 123.1659 | 123.3398 | -18.6035
2618.5156 | 123.4909 | -95.9427 | 27.2369 | 0.14191 | 0.013954 | 0.0017901 | 0.012394 | -0.019553 | 0.0036166 | 0.0016983 | 0.14824 | 0.020448 | -0.011499 | 0.0099314 | -0.0012218 | 0.0059387 | 1.4603 | 1.4832 | 1.3641 | 1.4236 | 1.506 | 1.3367 | 1.181 | 27.3697 | 27.4017 | 27.4109 | 27.2461 | 27.182 | 8.7845 | 8.6746 | 97.2794 | 97.1237 | -25.7309 | 97.4258 | 97.3663 | 0.24262 | -25.7767 | 104.7272 | 104.6173 | 0.009156 | 123.3124 | 123.3536 | 18.7363 | -0.054931 | 97.4487 | 97.403 | 97.3068 | -26.0559 | 123.1888 | 123.1247 | 123.3444 | -18.5623
2619.5156 | 123.4634 | -96.0022 | 27.2141 | 0.19531 | 0.0098951 | 0.0030719 | 0.0085492 | -0.019126 | -0.0023648 | 0.00020288 | 0.033798 | 0.019166 | -0.012995 | 0.01399 | -0.0018628 | 0.012347 | 1.3824 | 1.4145 | 1.3184 | 1.3962 | 1.5015 | 1.3229 | 1.1536 | 27.2507 | 27.3376 | 27.3514 | 27.2186 | 27.1637 | 8.7753 | 8.6792 | 97.3251 | 97.1558 | -25.7126 | 97.4167 | 97.3984 | 0.24262 | -25.8316 | 104.7775 | 104.6814 | 0.004578 | 123.2529 | 123.3536 | 18.6722 | -0.050354 | 97.5037 | 97.3846 | 97.3206 | -26.0605 | 123.2208 | 123.1659 | 123.3398 | -18.5349
2620.5156 | 123.4726 | -96.0709 | 27.1317 | 0.24872 | 0.015022 | 0.0034991 | 0.013249 | -0.01763 | 0.0038304 | 0.0025529 | 0.17113 | 0.018098 | -0.011927 | 0.0099314 | -0.0012218 | 0.0099975 | 1.4374 | 1.474 | 1.3733 | 1.4236 | 1.5106 | 1.3321 | 1.1673 | 27.2598 | 27.3239 | 27.301 | 27.1545 | 27.0905 | 8.7799 | 8.6792 | 97.403 | 97.2382 | -25.621 | 97.5449 | 97.4945 | 0.25635 | -25.6943 | 104.8508 | 104.7501 | 0.022888 | 123.3307 | 123.3719 | 18.6218 | -0.041199 | 97.5815 | 97.5082 | 97.4442 | -25.9644 | 123.2254 | 123.1613 | 123.3948 | -18.4525
2621.5312 | 123.4726 | -96.0846 | 27.1317 | 0.035095 | 0.0088269 | 0.0026447 | 0.012394 | -0.020407 | -0.0023648 | 0.0014847 | 0.056686 | 0.018098 | -0.014704 | 0.010999 | -0.0029308 | 0.01192 | 1.3916 | 1.4557 | 1.3275 | 1.4191 | 1.5152 | 1.3275 | 1.1627 | 27.1912 | 27.2736 | 27.2736 | 27.1545 | 27.0721 | 8.7708 | 8.6792 | 97.4121 | 97.2473 | -25.6165 | 97.5403 | 97.5037 | 0.25635 | -25.7401 | 104.8553 | 104.7638 | 0.022888 | 123.2758 | 123.3582 | 18.5944 | -0.059509 | 97.5998 | 97.4762 | 97.4121 | -25.9689 | 123.2391 | 123.1567 | 123.3582 | -18.4525
2622.5156 | 123.4314 | -96.1487 | 27.0584 | 0.21057 | 0.017158 | 0.00093569 | 0.011967 | -0.01998 | 0.0042576 | 0.0036209 | 0.11772 | 0.020021 | -0.0078678 | 0.01399 | -0.00058103 | 0.0087157 | 1.387 | 1.3641 | 1.2589 | 1.3641 | 1.5564 | 1.3184 | 1.1353 | 27.1317 | 27.1408 | 27.1408 | 27.1042 | 27.0172 | 8.7799 | 8.6746 | 97.467 | 97.2839 | -25.502 | 97.5128 | 97.5128 | 0.22888 | -25.6714 | 104.9286 | 104.8233 | 0.045776 | 123.2803 | 123.2895 | 18.4662 | -0.041199 | 97.7051 | 97.5357 | 97.4075 | -25.9232 | 123.2529 | 123.1659 | 123.2895 | -18.3838
2623.5156 | 123.4589 | -96.2036 | 27.0081 | 0.11139 | 0.013099 | 0.0043537 | 0.014317 | -0.01998 | -0.00065585 | 0.0025529 | 0.2169 | 0.019807 | -0.013208 | 0.01164 | 5.9768e-05 | 0.0097839 | 1.4236 | 1.4557 | 1.3504 | 1.3962 | 1.5198 | 1.3321 | 1.1948 | 27.0538 | 27.1271 | 27.1179 | 26.9989 | 26.9485 | 8.7753 | 8.6838 | 97.5357 | 97.3984 | -25.4883 | 97.6593 | 97.5998 | 0.20142 | -25.5844 | 104.9789 | 104.8874 | -0.009156 | 123.2574 | 123.3215 | 18.4341 | -0.05951 | 97.7234 | 97.6273 | 97.554 | -25.8133 | 123.2025 | 123.1522 | 123.3307 | -18.3243
2624.5156 | 123.468 | -96.2265 | 26.9577 | 0.26398 | 0.015022 | 0.0015765 | 0.015385 | -0.016989 | 0.001694 | 0.0034073 | 0.14824 | 0.020021 | -0.010645 | 0.013136 | -0.0010082 | 0.0070067 | 1.4465 | 1.4328 | 1.3412 | 1.4008 | 1.5244 | 1.3184 | 1.1627 | 27.0721 | 27.1133 | 27.1133 | 26.9989 | 26.8936 | 8.7753 | 8.6746 | 97.5449 | 97.3892 | -25.4333 | 97.6593 | 97.6273 | 0.23804 | -25.5112 | 105.0018 | 104.9011 | 0.041198 | 123.2986 | 123.3398 | 18.4387 | -0.064087 | 97.7509 | 97.673 | 97.5677 | -25.795 | 123.2254 | 123.1201 | 123.3398 | -18.2831
2625.5156 | 123.4772 | -96.1945 | 27.0035 | -0.13275 | 0.0081861 | 0.0041401 | 0.014744 | -0.019553 | -0.0049282 | 0.0021255 | 0.17113 | 0.020448 | -0.013208 | 0.012922 | -0.0052808 | 0.0095703 | 1.5472 | 1.3275 | 1.3687 | 1.4648 | 1.5106 | 1.3138 | 1.149 | 27.0905 | 27.2324 | 27.1866 | 27.0035 | 26.9485 | 8.7753 | 8.6838 | 97.5082 | 97.3434 | -25.4929 | 97.522 | 97.6593 | 0.31586 | -25.4562 | 104.9698 | 104.8782 | 0 | 123.2849 | 123.381 | 18.5028 | -0.054932 | 97.7051 | 97.7417 | 97.5632 | -25.8545 | 123.1979 | 123.143 | 123.4268 | -18.3197
2626.5156 | 123.3444 | -96.2585 | 27.0126 | 0.14954 | 0.021217 | 0.0011493 | 0.014317 | -0.021689 | 0.0048984 | 0.0036209 | 0.079574 | 0.024934 | -0.0097904 | 0.0099314 | -0.0010082 | 0.0076477 | 1.3412 | 1.3046 | 1.2085 | 1.3458 | 1.5472 | 1.3046 | 1.1261 | 26.944 | 27.0447 | 27.0493 | 27.0309 | 26.944 | 8.7799 | 8.67 | 97.5632 | 97.3846 | -25.4654 | 97.5632 | 97.6044 | 0.21973 | -25.6714 | 105.0385 | 104.9286 | 0.018311 | 123.2025 | 123.3078 | 18.3792 | -0.068664 | 97.8058 | 97.5998 | 97.467 | -25.8865 | 123.2895 | 123.2025 | 123.3032 | -18.3426
2627.5156 | 123.4451 | -96.2494 | 26.9394 | 0.18005 | 0.013954 | -0.00013251 | 0.012181 | -0.019126 | -0.0019376 | 0.0019119 | 0.23979 | 0.01938 | -0.013636 | 0.01164 | -0.0025036 | 0.011279 | 1.4236 | 1.4832 | 1.3687 | 1.4236 | 1.5106 | 1.3321 | 1.1765 | 27.0309 | 27.095 | 27.0859 | 26.9623 | 26.9073 | 8.7799 | 8.6792 | 97.5815 | 97.4258 | -25.4288 | 97.7325 | 97.673 | 0.24719 | -25.5157 | 105.0293 | 104.9286 | 0.022888 | 123.2803 | 123.3353 | 18.4067 | -0.032043 | 97.76 | 97.673 | 97.6181 | -25.7629 | 123.2117 | 123.1567 | 123.3444 | -18.2602
2628.5156 | 123.3444 | -96.3593 | 26.9394 | 0.11139 | 0.019295 | 0.00050849 | 0.015812 | -0.019766 | 0.0042576 | 0.0025529 | 0.033798 | 0.022157 | -0.0097904 | 0.011427 | 0.00027337 | 0.0089295 | 1.3687 | 1.3229 | 1.236 | 1.3596 | 1.561 | 1.3092 | 1.1124 | 26.8616 | 26.9211 | 26.8936 | 26.9577 | 26.8753 | 8.7708 | 8.6746 | 97.6685 | 97.4716 | -25.3784 | 97.6822 | 97.7188 | 0.24719 | -25.5707 | 105.13 | 105.0339 | 0.018311 | 123.2208 | 123.2529 | 18.219 | -0.064087 | 97.9202 | 97.728 | 97.5952 | -25.827 | 123.317 | 123.2346 | 123.2803 | -18.2648
2629.5156 | 123.3856 | -96.3867 | 26.8982 | 0.18005 | 0.01844 | 0.0015765 | 0.011754 | -0.018698 | 0.0038304 | 0.0036209 | 0.10246 | 0.02173 | -0.009363 | 0.013349 | -0.00015383 | 0.011707 | 1.3229 | 1.3092 | 1.2268 | 1.3321 | 1.5472 | 1.2909 | 1.1307 | 26.77 | 26.8707 | 27.0859 | 26.9211 | 26.8433 | 8.7845 | 8.6792 | 97.6776 | 97.5174 | -25.351 | 97.6959 | 97.7188 | 0.20142 | -25.5753 | 105.1712 | 105.0659 | 0.022889 | 123.1567 | 123.4726 | 18.4067 | -0.054931 | 97.934 | 97.7097 | 97.6135 | -25.7675 | 123.3078 | 123.23 | 123.2574 | -18.219
2630.5156 | 123.4726 | -96.3867 | 26.8341 | 0.21057 | 0.016945 | 0.0015765 | 0.01154 | -0.019339 | -0.001083 | 0.0025529 | 0.23979 | 0.023652 | -0.012995 | 0.01164 | -0.0012218 | 0.0093567 | 1.4053 | 1.4282 | 1.3367 | 1.4145 | 1.5015 | 1.3229 | 1.1673 | 26.9165 | 26.9897 | 26.9714 | 26.8387 | 26.7746 | 8.7708 | 8.6792 | 97.7097 | 97.554 | -25.3326 | 97.8149 | 97.8012 | 0.24719 | -25.4288 | 105.1575 | 105.0659 | 0.004578 | 123.3032 | 123.3582 | 18.2922 | -0.059509 | 97.8882 | 97.7921 | 97.7234 | -25.6668 | 123.2254 | 123.1613 | 123.3765 | -18.1549
2631.5312 | 123.3765 | -96.4828 | 26.7975 | 0.057983 | 0.020576 | 0.00050849 | 0.014744 | -0.019126 | 0.0031894 | 0.0042619 | 0.041427 | 0.023225 | -0.0095768 | 0.012495 | -0.0033582 | 0.010638 | 1.3458 | 1.3504 | 1.2497 | 1.355 | 1.5335 | 1.3 | 1.1169 | 26.7471 | 26.8387 | 26.8021 | 26.8433 | 26.77 | 8.7799 | 8.6792 | 97.7829 | 97.5998 | -25.264 | 97.8333 | 97.8378 | 0.23804 | -25.4517 | 105.2628 | 105.162 | 0.045777 | 123.23 | 123.2849 | 18.1229 | -0.027465 | 98.0164 | 97.8287 | 97.7325 | -25.6805 | 123.3261 | 123.2529 | 123.3215 | -18.1183
2632.5156 | 123.3902 | -96.4966 | 26.7929 | -0.12512 | 0.019081 | 0.0030719 | 0.015385 | -0.017417 | 0.0012668 | 0.0019119 | -0.019608 | 0.02408 | -0.0097904 | 0.012708 | -0.0025036 | 0.010425 | 1.3962 | 1.3916 | 1.2863 | 1.3962 | 1.5427 | 1.3138 | 1.1261 | 26.7654 | 26.8707 | 26.8158 | 26.77 | 26.7426 | 8.7753 | 8.6792 | 97.8104 | 97.6227 | -25.2502 | 97.8882 | 97.8928 | 0.27008 | -25.3967 | 105.2719 | 105.1758 | -0.022888 | 123.262 | 123.3124 | 18.1366 | -0.050354 | 98.0392 | 97.8928 | 97.7829 | -25.6668 | 123.2666 | 123.2391 | 123.3673 | -18.1137
2633.5156 | 123.3948 | -96.5378 | 26.7334 | -0.010681 | 0.018654 | 0.0022175 | 0.013676 | -0.019553 | 0.0025486 | 0.0034073 | 0.026169 | 0.023225 | -0.010218 | 0.012495 | -0.00229 | 0.010638 | 1.3733 | 1.3916 | 1.2817 | 1.387 | 1.5335 | 1.2909 | 1.1215 | 26.7059 | 26.7883 | 26.7563 | 26.7654 | 26.6739 | 8.7799 | 8.67 | 97.8287 | 97.6593 | -25.1999 | 97.9294 | 97.9248 | 0.2655 | -25.3601 | 105.3177 | 105.2078 | 0.032044 | 123.2437 | 123.2941 | 18.0862 | -0.059509 | 98.0713 | 97.9111 | 97.8195 | -25.6119 | 123.3032 | 123.2117 | 123.3261 | -18.0634
2634.5156 | 123.4039 | -96.6293 | 26.683 | -0.13275 | 0.01609 | 0.00072209 | 0.012608 | -0.016349 | 0.0010532 | 0.0027665 | -0.13405 | 0.020875 | -0.010858 | 0.013136 | -0.0016492 | 0.010211 | 1.3687 | 1.3916 | 1.268 | 1.3824 | 1.5427 | 1.2863 | 1.1307 | 26.651 | 26.7746 | 26.7288 | 26.7105 | 26.6235 | 8.7753 | 8.6746 | 97.9156 | 97.76 | -25.1404 | 98.0209 | 98.0118 | 0.25177 | -25.3143 | 105.4047 | 105.304 | 0.027466 | 123.2803 | 123.3582 | 18.0542 | -0.059509 | 98.172 | 97.998 | 97.8973 | -25.5524 | 123.3398 | 123.2529 | 123.4039 | -18.0084
2635.5312 | 123.4772 | -96.5881 | 26.6373 | -0.41504 | 0.012245 | 0.0088397 | 0.011967 | -0.019553 | -0.0055692 | 0.0019119 | 0.13298 | 0.020448 | -0.01214 | 0.011854 | -0.0052808 | 0.012775 | 1.3184 | 1.3962 | 1.3184 | 1.387 | 1.506 | 1.3 | 1.1536 | 26.6281 | 26.7426 | 26.77 | 26.6281 | 26.5869 | 8.7799 | 8.6746 | 97.8882 | 97.7417 | -25.1312 | 97.9843 | 97.9752 | 0.23346 | -25.3189 | 105.368 | 105.2628 | -0.009155 | 123.2162 | 123.3582 | 18.0954 | -0.050354 | 98.0942 | 97.9065 | 97.9065 | -25.4837 | 123.2162 | 123.175 | 123.3307 | -17.9626
2636.5156 | 123.3719 | -96.6568 | 26.6327 | -0.23193 | 0.012245 | 0.0030719 | 0.013035 | -0.021262 | -0.0023648 | 0.00041648 | 1.0867 | 0.019807 | -0.010645 | 0.012495 | -0.00229 | 0.0074341 | 1.3275 | 1.3504 | 1.2451 | 1.3412 | 1.5564 | 1.2817 | 1.1353 | 26.5366 | 26.6556 | 26.6281 | 26.6281 | 26.5869 | 8.7799 | 8.6792 | 97.9385 | 97.7921 | -25.0763 | 98.0072 | 97.998 | 0.20599 | -25.3052 | 105.4367 | 105.336 | -0.004577 | 123.1934 | 123.2849 | 17.9489 | -0.045776 | 98.2132 | 97.9843 | 97.9019 | -25.4974 | 123.2849 | 123.2437 | 123.3124 | -17.9535
2637.5156 | 123.4268 | -96.666 | 26.6052 | -0.16327 | 0.016945 | 0.0022175 | 0.015812 | -0.019766 | 0.0031894 | 0.0019119 | -0.14931 | 0.021302 | -0.010218 | 0.012922 | -0.0014356 | 0.0070067 | 1.3824 | 1.387 | 1.2817 | 1.3916 | 1.5427 | 1.2863 | 1.1398 | 26.564 | 26.6602 | 26.6098 | 26.5823 | 26.5091 | 8.7799 | 8.6792 | 97.9523 | 97.8058 | -25.0626 | 98.053 | 98.0576 | 0.25177 | -25.2228 | 105.4459 | 105.3452 | -0.022889 | 123.23 | 123.2758 | 17.9306 | -0.096131 | 98.2086 | 98.0484 | 97.9477 | -25.4654 | 123.2483 | 123.175 | 123.3261 | -17.926
2638.5156 | 123.3719 | -96.7438 | 26.5457 | -0.14038 | 0.017372 | 0.0013629 | 0.013463 | -0.019766 | 0.00019875 | 0.00063028 | -0.15694 | 0.021089 | -0.0091494 | 0.012495 | -0.0035718 | 0.011066 | 1.3321 | 1.3641 | 1.2405 | 1.3504 | 1.5472 | 1.2863 | 1.1261 | 26.4633 | 26.5869 | 26.5732 | 26.5549 | 26.4816 | 8.7753 | 8.6746 | 98.0301 | 97.8699 | -24.9985 | 98.1079 | 98.0942 | 0.2243 | -25.2136 | 105.5191 | 105.4184 | 0.009156 | 123.2071 | 123.317 | 17.8986 | -0.064087 | 98.291 | 98.0759 | 97.9843 | -25.4196 | 123.2986 | 123.2254 | 123.3307 | -17.8711
2639.5156 | 123.3627 | -96.8033 | 26.4954 | 0.050354 | 0.02079 | 0.0015765 | 0.013463 | -0.016989 | 0.0031894 | 0.0012711 | 0.033798 | 0.019166 | -0.0097904 | 0.012495 | 0.0013416 | 0.012134 | 1.3321 | 1.3641 | 1.2497 | 1.3458 | 1.506 | 1.2863 | 1.1215 | 26.4313 | 26.532 | 26.4999 | 26.5182 | 26.4359 | 8.7799 | 8.6746 | 98.0896 | 97.9248 | -24.9893 | 98.1674 | 98.1491 | 0.2243 | -25.1633 | 105.5832 | 105.4779 | 0.022889 | 123.2346 | 123.3032 | 17.8253 | -0.059509 | 98.3093 | 98.1354 | 98.053 | -25.3738 | 123.3215 | 123.2391 | 123.3353 | -17.8207
2640.5312 | 123.4955 | -96.7896 | 26.413 | 0.20294 | 0.015236 | 0.0030719 | 0.013463 | -0.021689 | -0.001083 | 0.00020288 | 0.1635 | 0.019593 | -0.0091494 | 0.015058 | -0.0020764 | 0.010638 | 1.387 | 1.4328 | 1.3275 | 1.4236 | 1.5152 | 1.3321 | 1.1536 | 26.4725 | 26.564 | 26.5686 | 26.4221 | 26.3626 | 8.7799 | 8.6792 | 98.1216 | 97.9431 | -24.8978 | 98.2224 | 98.2132 | 0.27008 | -25.0259 | 105.5695 | 105.4688 | 0.009155 | 123.262 | 123.3582 | 17.8894 | -0.050354 | 98.3047 | 98.1766 | 98.1171 | -25.2594 | 123.2117 | 123.1522 | 123.3536 | -17.7338
2641.5312 | 123.4268 | -96.8811 | 26.3855 | -0.17853 | 0.0092541 | 0.0030719 | 0.012608 | -0.021048 | -0.0021512 | -0.00022432 | -0.11116 | 0.020448 | -0.012354 | 0.010359 | -0.0050672 | 0.010638 | 1.3962 | 1.4786 | 1.3504 | 1.4374 | 1.5289 | 1.3367 | 1.1581 | 26.3809 | 26.5228 | 26.4999 | 26.3809 | 26.3351 | 8.7845 | 8.6746 | 98.2178 | 98.0392 | -24.8566 | 98.3597 | 98.3185 | 0.27924 | -24.9893 | 105.6656 | 105.5557 | -0.004578 | 123.262 | 123.381 | 17.8253 | -0.050354 | 98.41 | 98.2773 | 98.2315 | -25.2274 | 123.262 | 123.2162 | 123.4039 | -17.7109
2642.5156 | 123.4818 | -96.9223 | 26.326 | -0.056458 | 0.010963 | 0.00093569 | 0.013463 | -0.019126 | -0.0042874 | 0.0012711 | -0.057755 | 0.016389 | -0.012995 | 0.01164 | -0.0035718 | 0.010638 | 1.3916 | 1.5335 | 1.3824 | 1.442 | 1.5244 | 1.3275 | 1.1856 | 26.3672 | 26.5274 | 26.5137 | 26.3351 | 26.2527 | 8.7799 | 8.6838 | 98.2498 | 98.1079 | -24.8016 | 98.4558 | 98.3643 | 0.25635 | -24.9344 | 105.7022 | 105.6061 | 0.009155 | 123.2895 | 123.436 | 17.8299 | -0.073242 | 98.4467 | 98.3139 | 98.3047 | -25.1404 | 123.2574 | 123.175 | 123.4497 | -17.6422
2643.5156 | 123.3902 | -97.0001 | 26.3077 | -0.16327 | 0.016945 | 0.0032855 | 0.013035 | -0.019339 | 0.0031894 | 0.0029801 | -0.19508 | 0.02173 | -0.0095768 | 0.012708 | -0.0025036 | 0.0095703 | 1.3504 | 1.3504 | 1.2543 | 1.3596 | 1.5564 | 1.3 | 1.1169 | 26.239 | 26.3397 | 26.326 | 26.3443 | 26.2253 | 8.7708 | 8.6746 | 98.3002 | 98.1171 | -24.7513 | 98.3505 | 98.3597 | 0.24262 | -24.9573 | 105.7709 | 105.6747 | 0.036621 | 123.2391 | 123.3261 | 17.6514 | -0.082397 | 98.5565 | 98.3505 | 98.2544 | -25.1907 | 123.3444 | 123.2254 | 123.3398 | -17.6331
2644.5156 | 123.4863 | -96.991 | 26.2344 | -3.5812 | 0.0088269 | 0.00093569 | 0.0083356 | -0.021689 | -0.0042874 | 0.00084388 | -0.088272 | 0.017244 | -0.012781 | 0.011854 | -0.0016492 | 0.0091431 | 1.3458 | 1.5244 | 1.3962 | 1.442 | 1.4969 | 1.3092 | 1.149 | 26.2894 | 26.4313 | 26.3901 | 26.207 | 26.1841 | 8.7799 | 8.6746 | 98.3002 | 98.14 | -24.7375 | 98.5153 | 98.4329 | 0.29297 | -24.8886 | 105.7709 | 105.6656 | -0.027466 | 123.2803 | 123.381 | 17.7155 | -0.050354 | 98.4879 | 98.3368 | 98.3871 | -25.0854 | 123.1979 | 123.175 | 123.4222 | -17.5598
2645.5312 | 123.4406 | -97.0825 | 26.1658 | 0.18768 | 0.016731 | 0.0026447 | 0.013035 | -0.01998 | 0.0044712 | 0.0025529 | 0.17876 | 0.022157 | -0.011499 | 0.013777 | -0.0016492 | 0.0080749 | 1.3321 | 1.3596 | 1.2589 | 1.3367 | 1.5244 | 1.3 | 1.1261 | 26.1795 | 26.2253 | 26.2482 | 26.1978 | 26.1108 | 8.7753 | 8.6792 | 98.3826 | 98.2086 | -24.6414 | 98.4421 | 98.4192 | 0.21057 | -24.8337 | 105.8578 | 105.7617 | 0.032044 | 123.262 | 123.3307 | 17.569 | -0.054931 | 98.6069 | 98.4146 | 98.3414 | -25.0397 | 123.2803 | 123.1934 | 123.3078 | -17.4866
2646.5156 | 123.4955 | -97.0642 | 26.1383 | -0.0030518 | 0.0086133 | 0.0062763 | 0.012608 | -0.020835 | -0.0038602 | 0.0019119 | 0.064316 | 0.019166 | -0.011499 | 0.010572 | -0.003999 | 0.0087157 | 1.3824 | 1.5106 | 1.3824 | 1.442 | 1.5289 | 1.3412 | 1.181 | 26.2207 | 26.3489 | 26.3351 | 26.1383 | 26.0696 | 8.7708 | 8.6792 | 98.4055 | 98.2452 | -24.6094 | 98.5748 | 98.5062 | 0.26093 | -24.7559 | 105.835 | 105.7434 | 0 | 123.2849 | 123.3994 | 17.6559 | -0.068665 | 98.5931 | 98.4467 | 98.4467 | -24.9573 | 123.2025 | 123.1339 | 123.4131 | -17.4591
2647.5156 | 123.3627 | -97.142 | 26.1429 | -0.26245 | 0.013527 | 0.0037127 | 0.014958 | -0.019126 | -1.505e-05 | 0.00084388 | -0.19508 | 0.020662 | -0.0091494 | 0.012495 | -0.0050672 | 0.0082885 | 1.3229 | 1.3733 | 1.2405 | 1.3367 | 1.5518 | 1.2955 | 1.1261 | 26.2024 | 26.0788 | 26.0284 | 26.1749 | 26.0925 | 8.7845 | 8.6792 | 98.4375 | 98.2681 | -24.5911 | 98.5153 | 98.4787 | 0.21057 | -24.8199 | 105.9265 | 105.8212 | 0.032044 | 123.3444 | 123.1705 | 17.3492 | -0.050354 | 98.6938 | 98.465 | 98.3826 | -25.0168 | 123.317 | 123.2346 | 123.2208 | -17.4637
2648.5156 | 123.4955 | -97.1695 | 26.0696 | -0.056458 | 0.011177 | 0.0047809 | 0.013463 | -0.018698 | -0.0042874 | 0.00041648 | 0.033798 | 0.018739 | -0.015131 | 0.012281 | -0.0050672 | 0.0099975 | 1.3962 | 1.4832 | 1.3687 | 1.4191 | 1.5106 | 1.3458 | 1.1719 | 26.1337 | 26.2161 | 26.2299 | 26.0742 | 25.9827 | 8.7799 | 8.6792 | 98.5153 | 98.3414 | -24.559 | 98.6526 | 98.5886 | 0.24719 | -24.6735 | 105.9494 | 105.8487 | 0.004578 | 123.3032 | 123.3994 | 17.5507 | -0.086975 | 98.6801 | 98.5657 | 98.5382 | -24.8978 | 123.2437 | 123.1522 | 123.3856 | -17.3904
2649.5156 | 123.5092 | -97.2061 | 25.9964 | -0.041199 | 0.0090405 | 0.0043537 | 0.01154 | -0.021475 | -0.0036464 | 0.0010575 | -0.11116 | 0.017244 | -0.012354 | 0.012495 | -0.0050672 | 0.0097839 | 1.4145 | 1.506 | 1.3687 | 1.4282 | 1.5152 | 1.3458 | 1.1765 | 26.1108 | 26.1887 | 26.1932 | 26.0147 | 25.9277 | 8.7799 | 8.6792 | 98.5519 | 98.3826 | -24.4812 | 98.7122 | 98.6343 | 0.25177 | -24.5819 | 105.986 | 105.8853 | 0.01831 | 123.317 | 123.3994 | 17.514 | -0.068665 | 98.7213 | 98.6206 | 98.5748 | -24.8199 | 123.2208 | 123.1338 | 123.3948 | -17.3172
2650.5156 | 123.4451 | -97.2794 | 25.9369 | 0.16479 | 0.011177 | 0.0047809 | 0.013035 | -0.019339 | -0.0015102 | 0.00063028 | 0.19402 | 0.018098 | -0.014063 | 0.010786 | -0.0033582 | 0.010852 | 1.3687 | 1.4236 | 1.3229 | 1.3733 | 1.5198 | 1.3367 | 1.1581 | 25.9735 | 26.0559 | 26.033 | 25.9552 | 25.8682 | 8.7753 | 8.6746 | 98.616 | 98.4375 | -24.4171 | 98.703 | 98.6526 | 0.21515 | -24.5682 | 106.0547 | 105.954 | 0.01831 | 123.2529 | 123.3124 | 17.3584 | -0.068665 | 98.7991 | 98.6481 | 98.6023 | -24.7787 | 123.2346 | 123.1476 | 123.3353 | -17.2623
2651.5312 | 123.5001 | -97.3251 | 25.8499 | 0.21057 | 0.013954 | 0.0026447 | 0.010258 | -0.019766 | 0.005112 | -0.00022432 | -0.96565 | 0.018739 | -0.013636 | 0.01164 | -0.00015383 | 0.0097839 | 1.4236 | 1.4557 | 1.3641 | 1.4282 | 1.4786 | 1.3138 | 1.149 | 25.9506 | 25.9964 | 26.001 | 25.8499 | 25.7492 | 8.7799 | 8.6838 | 98.6389 | 98.4741 | -24.3713 | 98.7808 | 98.7534 | 0.27924 | -24.4263 | 106.105 | 106.0089 | 0 | 123.2758 | 123.3261 | 17.3172 | -0.10071 | 98.8037 | 98.7488 | 98.6893 | -24.7009 | 123.175 | 123.0743 | 123.3215 | -17.1661
2652.5156 | 123.4497 | -97.4213 | 25.8133 | 0.11902 | 0.01075 | 0.0026447 | 0.013249 | -0.021475 | -0.0021512 | 0.00041648 | 0.18639 | 0.020448 | -0.012354 | 0.013777 | -0.0054944 | 0.0095703 | 1.3824 | 1.4191 | 1.3138 | 1.387 | 1.4877 | 1.3367 | 1.1673 | 25.8453 | 25.8957 | 25.9232 | 25.8316 | 25.7629 | 8.7799 | 8.67 | 98.7579 | 98.5886 | -24.3256 | 98.8403 | 98.8083 | 0.21973 | -24.4308 | 106.2012 | 106.0913 | 0.018311 | 123.2666 | 123.3444 | 17.2531 | -0.050354 | 98.909 | 98.8037 | 98.735 | -24.646 | 123.2529 | 123.1842 | 123.317 | -17.1432
2653.5156 | 123.468 | -97.467 | 25.7584 | 0.019836 | 0.0088269 | 0.0034991 | 0.011967 | -0.019126 | -0.00022865 | 0.00020288 | 0.049057 | 0.018739 | -0.013849 | 0.013136 | -0.003999 | 0.0093567 | 1.3596 | 1.4328 | 1.3184 | 1.3824 | 1.5198 | 1.3321 | 1.1444 | 25.8041 | 25.882 | 25.9003 | 25.7492 | 25.6989 | 8.7799 | 8.6838 | 98.7991 | 98.6114 | -24.2386 | 98.8998 | 98.8495 | 0.23804 | -24.3988 | 106.2469 | 106.1508 | -0.009155 | 123.2712 | 123.3673 | 17.2165 | -0.059509 | 98.9868 | 98.8266 | 98.7854 | -24.614 | 123.2162 | 123.1659 | 123.349 | -17.0746
2654.5156 | 123.4589 | -97.5174 | 25.6943 | 0.18768 | 0.013313 | 0.0024311 | 0.012822 | -0.02233 | 0.0010532 | 0.0038345 | 0.17876 | 0.020234 | -0.011286 | 0.013563 | -0.00229 | 0.0099975 | 1.4191 | 1.442 | 1.3458 | 1.3962 | 1.474 | 1.3092 | 1.1398 | 25.795 | 25.8316 | 25.8316 | 25.708 | 25.6302 | 8.7799 | 8.6792 | 98.8266 | 98.6572 | -24.2203 | 98.9594 | 98.9136 | 0.25635 | -24.2752 | 106.2973 | 106.1966 | 0.013733 | 123.3124 | 123.349 | 17.1524 | -0.064087 | 98.9914 | 98.9365 | 98.8632 | -24.5544 | 123.2254 | 123.1476 | 123.349 | -17.0151
2655.5156 | 123.4268 | -97.5861 | 25.6668 | 0.12665 | 0.01075 | 0.0043537 | 0.010258 | -0.021262 | -0.001083 | -0.0010787 | 0.049057 | 0.020021 | -0.013636 | 0.01164 | -0.00229 | 0.0095703 | 1.3687 | 1.4008 | 1.2955 | 1.3596 | 1.5015 | 1.2955 | 1.1261 | 25.6439 | 25.7263 | 25.708 | 25.6393 | 25.6027 | 8.7753 | 8.6792 | 98.8815 | 98.7122 | -24.1653 | 98.9868 | 98.9456 | 0.23346 | -24.2981 | 106.3614 | 106.2653 | -0.027466 | 123.23 | 123.2941 | 17.0288 | -0.064087 | 99.0875 | 98.9548 | 98.8815 | -24.5407 | 123.2254 | 123.1888 | 123.3124 | -16.9876
2656.5156 | 123.4726 | -97.5906 | 25.6256 | 0.18768 | 0.011818 | 0.0011493 | 0.013676 | -0.019766 | 0.0025486 | 0.00084388 | 0.18639 | 0.018739 | -0.012995 | 0.012922 | -0.0016492 | 0.0087157 | 1.4191 | 1.4603 | 1.3458 | 1.4008 | 1.4694 | 1.3 | 1.1536 | 25.6989 | 25.7355 | 25.7217 | 25.621 | 25.5249 | 8.7936 | 8.6838 | 98.8907 | 98.7442 | -24.1562 | 99.0509 | 98.9914 | 0.24719 | -24.2065 | 106.3843 | 106.2744 | -0.004577 | 123.2895 | 123.3124 | 17.038 | -0.10071 | 99.0601 | 99.0097 | 98.9365 | -24.472 | 123.2117 | 123.1155 | 123.3261 | -16.9418
2657.5156 | 123.4497 | -97.6639 | 25.5249 | 0.16479 | 0.012245 | 0.0043537 | 0.011113 | -0.01998 | -0.00044225 | 0.0023391 | 0.19402 | 0.018739 | -0.011499 | 0.012281 | -0.0037854 | 0.011066 | 1.4099 | 1.4465 | 1.3367 | 1.3916 | 1.4923 | 1.3229 | 1.1353 | 25.589 | 25.6348 | 25.6439 | 25.5386 | 25.4517 | 8.7753 | 8.6746 | 98.9868 | 98.7991 | -24.0326 | 99.1104 | 99.0555 | 0.25635 | -24.115 | 106.4392 | 106.3385 | 0.013733 | 123.2529 | 123.3078 | 16.9693 | -0.073242 | 99.1562 | 99.0738 | 99.0005 | -24.3896 | 123.2025 | 123.1155 | 123.2986 | -16.8503
2658.5156 | 123.5046 | -97.76 | 25.4517 | 0.22583 | 0.017799 | 0.0020037 | 0.011113 | -0.01763 | 0.0021214 | 0.0053299 | 0.2169 | 0.019593 | -0.010645 | 0.010572 | 0.0013416 | 0.010638 | 1.2085 | 1.2497 | 1.3138 | 1.4648 | 1.4328 | 1.2863 | 1.0986 | 25.5615 | 25.6119 | 25.6027 | 25.4562 | 25.3876 | 8.7799 | 8.6838 | 99.0463 | 98.8586 | -24.0189 | 99.0097 | 99.2249 | 0.36621 | -24.2432 | 106.5399 | 106.4438 | 0.004578 | 123.3215 | 123.3627 | 16.9189 | -0.064087 | 99.1928 | 98.9685 | 99.0738 | -24.353 | 123.2162 | 123.1476 | 123.3719 | -16.7679
2659.5156 | 123.4543 | -97.7966 | 25.4288 | 0.18768 | 0.012459 | 0.0030719 | 0.011326 | -0.021903 | 0.00041235 | 0.0034073 | 0.19402 | 0.018739 | -0.011713 | 0.01399 | -0.0025036 | 0.0097839 | 1.4053 | 1.4374 | 1.3275 | 1.3962 | 1.4694 | 1.3046 | 1.1398 | 25.4837 | 25.5295 | 25.5386 | 25.4379 | 25.3555 | 8.7799 | 8.6838 | 99.1013 | 98.9365 | -23.9594 | 99.234 | 99.1928 | 0.25635 | -24.0234 | 106.5765 | 106.4804 | 0.009155 | 123.2803 | 123.3353 | 16.8549 | -0.073242 | 99.2661 | 99.202 | 99.1241 | -24.2889 | 123.2346 | 123.1522 | 123.3261 | -16.745
2660.5156 | 123.4818 | -97.8287 | 25.3738 | 0.21057 | 0.017586 | 0.0020037 | 0.014317 | -0.017844 | 0.0036166 | 0.0029801 | 0.20164 | 0.020448 | -0.011499 | 0.011427 | -0.0014356 | 0.0082885 | 1.3733 | 1.3504 | 1.2634 | 1.3596 | 1.4969 | 1.2772 | 1.1124 | 25.4791 | 25.5203 | 25.5249 | 25.4059 | 25.3326 | 8.7753 | 8.67 | 99.1058 | 98.941 | -23.877 | 99.1791 | 99.1882 | 0.24719 | -24.0005 | 106.604 | 106.4987 | 0.032044 | 123.3078 | 123.3536 | 16.8549 | -0.041198 | 99.3256 | 99.202 | 99.0921 | -24.2615 | 123.2346 | 123.1613 | 123.349 | -16.7038
2661.5312 | 123.4726 | -97.8378 | 25.351 | 0.2182 | 0.014381 | 0.0030719 | 0.010472 | -0.021262 | -0.00022865 | 0.0031937 | 0.14824 | 0.018312 | -0.012354 | 0.012495 | -0.0016492 | 0.011279 | 1.4008 | 1.4511 | 1.3412 | 1.4053 | 1.4694 | 1.3138 | 1.149 | 25.4425 | 25.5157 | 25.4929 | 25.3555 | 25.3006 | 8.7799 | 8.6746 | 99.1516 | 98.9868 | -23.8815 | 99.2889 | 99.2432 | 0.25635 | -23.9502 | 106.6177 | 106.5125 | 0.004578 | 123.2803 | 123.3307 | 16.8182 | -0.050354 | 99.3073 | 99.2386 | 99.1791 | -24.202 | 123.1934 | 123.1384 | 123.3536 | -16.6763
2662.5156 | 123.4955 | -97.8424 | 25.3418 | 0.20294 | 0.018654 | 0.0041401 | 0.013463 | -0.019126 | 0.0031894 | 0.0059707 | 0.17113 | 0.019807 | -0.0097904 | 0.011854 | -0.00036743 | 0.0091431 | 1.3596 | 1.3779 | 1.2817 | 1.3641 | 1.506 | 1.2863 | 1.1169 | 25.4425 | 25.4745 | 25.4791 | 25.3693 | 25.2777 | 8.7799 | 8.6792 | 99.1287 | 98.9594 | -23.8358 | 99.2203 | 99.2065 | 0.24719 | -23.9822 | 106.6223 | 106.5216 | 0.027466 | 123.2849 | 123.3215 | 16.7999 | -0.064087 | 99.3484 | 99.202 | 99.1241 | -24.2249 | 123.2117 | 123.1201 | 123.317 | -16.6626
2663.5469 | 123.4726 | -97.9065 | 25.3235 | 0.53101 | 0.0086133 | 0.0062763 | 0.011754 | -0.020835 | -0.0023648 | 0.00041648 | -0.073013 | 0.018953 | -0.011927 | 0.012495 | -0.0044262 | 0.0095703 | 1.4053 | 1.4557 | 1.3229 | 1.3824 | 1.4603 | 1.2817 | 1.1124 | 25.3876 | 25.5249 | 25.4791 | 25.3143 | 25.2823 | 8.7799 | 8.6792 | 99.1882 | 99.0189 | -23.8632 | 99.3622 | 99.2889 | 0.27008 | -23.9182 | 106.6864 | 106.5857 | -0.009155 | 123.2941 | 123.3856 | 16.7999 | -0.041198 | 99.3668 | 99.3118 | 99.2294 | -24.2111 | 123.2208 | 123.1888 | 123.4314 | -16.6443
2664.5156 | 123.4131 | -97.9752 | 25.2869 | 0.15717 | 0.015663 | 0.0045673 | 0.012394 | -0.021048 | 0.0029758 | 0.0040481 | 0.15587 | 0.020448 | -0.010431 | 0.013349 | 0.00048697 | 0.0085021 | 1.3138 | 1.2817 | 1.1993 | 1.2955 | 1.506 | 1.2451 | 1.0757 | 25.2777 | 25.3235 | 25.3189 | 25.3189 | 25.209 | 8.7708 | 8.6746 | 99.2203 | 99.0509 | -23.7808 | 99.2569 | 99.2706 | 0.21973 | -23.9731 | 106.7459 | 106.6498 | 0.032044 | 123.2529 | 123.2941 | 16.6443 | -0.07782 | 99.4812 | 99.2889 | 99.1745 | -24.2111 | 123.2941 | 123.1842 | 123.2986 | -16.6122
2665.5156 | 123.4818 | -97.966 | 25.2457 | 0.19531 | 0.015663 | 0.0020037 | 0.014958 | -0.021048 | 0.0031894 | 0.0025529 | 0.20164 | 0.01938 | -0.011499 | 0.010359 | -0.00229 | 0.010852 | 1.3824 | 1.4099 | 1.3046 | 1.3916 | 1.4465 | 1.2772 | 1.0986 | 25.3326 | 25.4105 | 25.4105 | 25.264 | 25.177 | 8.7799 | 8.6792 | 99.2432 | 99.0646 | -23.7991 | 99.3759 | 99.3576 | 0.29297 | -23.8632 | 106.7459 | 106.6452 | 0.01831 | 123.2986 | 123.3765 | 16.7313 | -0.068665 | 99.4125 | 99.3484 | 99.2706 | -24.147 | 123.23 | 123.143 | 123.3765 | -16.5665
2666.5156 | 123.4268 | -98.0301 | 25.1907 | 0.11139 | 0.010322 | 0.0032855 | 0.013463 | -0.020194 | -0.0032192 | 0.0025529 | 0.14061 | 0.020021 | -0.011499 | 0.0075814 | -0.0063488 | 0.011279 | 1.3321 | 1.3641 | 1.2863 | 1.3596 | 1.4694 | 1.2726 | 1.1215 | 25.145 | 25.296 | 25.3143 | 25.1862 | 25.1129 | 8.7799 | 8.6746 | 99.3027 | 99.1516 | -23.7213 | 99.3942 | 99.3896 | 0.23804 | -23.8586 | 106.81 | 106.7047 | -0.004578 | 123.175 | 123.3444 | 16.6397 | -0.07782 | 99.4995 | 99.3622 | 99.3164 | -24.0692 | 123.2162 | 123.143 | 123.3261 | -16.5161
2667.5156 | 123.4818 | -98.0759 | 25.1312 | 1.004 | 0.011604 | 0.0069171 | 0.013676 | -0.018271 | 0.00083955 | 0.0027665 | 0.19402 | 0.018953 | -0.0095768 | 0.01164 | -0.00229 | 0.0082885 | 1.4145 | 1.3962 | 1.2955 | 1.3733 | 1.4236 | 1.2451 | 1.1032 | 25.2136 | 25.2686 | 25.264 | 25.1358 | 25.0259 | 8.7936 | 8.6838 | 99.321 | 99.1791 | -23.7076 | 99.472 | 99.4492 | 0.27008 | -23.7167 | 106.8695 | 106.7596 | 0.004577 | 123.2895 | 123.3398 | 16.5802 | -0.10529 | 99.4995 | 99.4904 | 99.3713 | -24.028 | 123.2117 | 123.1018 | 123.3444 | -16.4474
2668.5156 | 123.4497 | -98.1125 | 25.058 | 0.13428 | 0.014381 | 0.0017901 | 0.011326 | -0.019126 | -0.0017238 | 0.00020288 | 0.22453 | 0.020234 | -0.011713 | 0.010786 | -0.0016492 | 0.0093567 | 1.4008 | 1.4053 | 1.3229 | 1.3641 | 1.4603 | 1.2772 | 1.1078 | 25.1678 | 25.2365 | 25.2319 | 25.0854 | 25.0214 | 8.7799 | 8.6792 | 99.3896 | 99.2203 | -23.5977 | 99.5178 | 99.4766 | 0.25635 | -23.6572 | 106.8924 | 106.7917 | 0.027466 | 123.2803 | 123.3444 | 16.5527 | -0.036621 | 99.5728 | 99.5132 | 99.4354 | -23.9502 | 123.1979 | 123.1338 | 123.349 | -16.3788
2669.5156 | 123.4726 | -98.1583 | 25.0305 | 0.17242 | 0.013527 | 0.0026447 | 0.012181 | -0.017417 | 0.0010532 | 0.0034073 | 0.18639 | 0.020021 | -0.012995 | 0.01164 | -0.0031446 | 0.0095703 | 1.3916 | 1.4236 | 1.3092 | 1.3641 | 1.4603 | 1.268 | 1.1215 | 25.1266 | 25.1953 | 25.1862 | 25.0443 | 24.9847 | 8.7845 | 8.6746 | 99.4263 | 99.2798 | -23.5703 | 99.5819 | 99.5224 | 0.24262 | -23.6389 | 106.9427 | 106.8329 | 0.013732 | 123.2849 | 123.3444 | 16.5115 | -0.045777 | 99.6185 | 99.5499 | 99.4675 | -23.909 | 123.2025 | 123.143 | 123.3536 | -16.3559
2670.5156 | 123.3902 | -98.2635 | 25.0397 | 0.17242 | 0.018226 | 0.0028583 | 0.014531 | -0.019766 | 0.0036166 | 0.0021255 | 0.11009 | 0.022798 | -0.0095768 | 0.014845 | -0.0012218 | 0.0095703 | 1.3138 | 1.2589 | 1.181 | 1.2909 | 1.4877 | 1.2314 | 1.0712 | 25.0076 | 25.0443 | 25.0351 | 25.0443 | 24.9847 | 8.7708 | 8.6746 | 99.4949 | 99.3347 | -23.5519 | 99.5224 | 99.5544 | 0.21973 | -23.7259 | 107.0343 | 106.9382 | 0.004577 | 123.2712 | 123.2986 | 16.3605 | -0.054932 | 99.7513 | 99.5773 | 99.4446 | -23.9685 | 123.3078 | 123.2483 | 123.3078 | -16.3651
2671.5312 | 123.4268 | -98.204 | 25.0351 | -0.19379 | 0.012031 | 0.0045673 | 0.013249 | -0.020835 | -0.0017238 | 0.0016983 | -0.1722 | 0.019166 | -0.010218 | 0.012495 | -0.0033582 | 0.010211 | 1.3641 | 1.4099 | 1.3 | 1.3824 | 1.4923 | 1.2726 | 1.1124 | 25.0534 | 25.1816 | 25.1266 | 25.058 | 24.9756 | 8.7753 | 8.6792 | 99.4766 | 99.3164 | -23.5428 | 99.614 | 99.5865 | 0.27008 | -23.671 | 106.9794 | 106.8832 | 0.022888 | 123.2574 | 123.3307 | 16.4474 | -0.059509 | 99.6964 | 99.5682 | 99.5041 | -23.9227 | 123.262 | 123.1796 | 123.3856 | -16.3559
2672.5156 | 123.4726 | -98.2544 | 24.9435 | 0.17242 | 0.01374 | 0.0045673 | 0.015172 | -0.020194 | 0.0014804 | 0.0021255 | 0.24742 | 0.019593 | -0.012354 | 0.014845 | -0.0031446 | 0.011066 | 1.3596 | 1.4008 | 1.3184 | 1.3687 | 1.474 | 1.2772 | 1.1215 | 25.0397 | 25.1175 | 25.1083 | 24.9664 | 24.884 | 8.7845 | 8.6838 | 99.5316 | 99.3759 | -23.4695 | 99.6552 | 99.6231 | 0.24719 | -23.584 | 107.0389 | 106.9382 | 0.022889 | 123.2941 | 123.3627 | 16.4246 | -0.059509 | 99.7284 | 99.614 | 99.5728 | -23.822 | 123.2208 | 123.1384 | 123.3719 | -16.2598
2673.5156 | 123.5046 | -98.3093 | 24.8886 | 0.21057 | 0.01609 | 0.0024311 | 0.011967 | -0.016989 | 0.0010532 | 0.0029801 | 0.23216 | 0.021516 | -0.010858 | 0.011213 | -0.0016492 | 0.0099975 | 1.3779 | 1.4008 | 1.2909 | 1.3733 | 1.4557 | 1.2817 | 1.1169 | 25.0122 | 25.0168 | 25.0763 | 24.8795 | 24.8428 | 8.7799 | 8.6792 | 99.5911 | 99.4263 | -23.4329 | 99.7101 | 99.6826 | 0.25635 | -23.5107 | 107.0892 | 106.9885 | -0.009155 | 123.3215 | 123.3856 | 16.3971 | -0.045777 | 99.765 | 99.6872 | 99.6002 | -23.7717 | 123.1888 | 123.1522 | 123.3261 | -16.2094
2674.5156 | 123.4085 | -98.3871 | 24.884 | 0.3479 | 0.018013 | 0.0013629 | 0.013035 | -0.021475 | 0.005112 | 0.0042619 | 0.10246 | 0.021943 | -0.011927 | 0.014417 | -0.0012218 | 0.0080749 | 1.2955 | 1.268 | 1.1673 | 1.2955 | 1.4877 | 1.236 | 1.0757 | 24.8566 | 24.884 | 24.8795 | 24.884 | 24.8291 | 8.7753 | 8.67 | 99.6231 | 99.4629 | -23.3963 | 99.6552 | 99.6826 | 0.21973 | -23.5886 | 107.1625 | 107.0572 | 0 | 123.2437 | 123.2666 | 16.2094 | -0.054931 | 99.8749 | 99.6826 | 99.5544 | -23.8083 | 123.2712 | 123.2162 | 123.2712 | -16.214
2675.5156 | 123.4818 | -98.3917 | 24.8108 | 0.16479 | 0.017158 | 0.00093569 | 0.013249 | -0.020407 | 0.0012668 | 0.0036209 | 2.376 | 0.020234 | -0.012995 | 0.0090768 | -0.00229 | 0.01192 | 1.3641 | 1.3916 | 1.3 | 1.3733 | 1.4236 | 1.268 | 1.0941 | 24.8703 | 24.9985 | 24.9619 | 24.8062 | 24.7513 | 8.7845 | 8.6792 | 99.6597 | 99.4858 | -23.3871 | 99.7833 | 99.765 | 0.27924 | -23.4467 | 107.1762 | 107.0709 | -0.004578 | 123.262 | 123.3536 | 16.2827 | -0.059509 | 99.8154 | 99.7559 | 99.6918 | -23.7167 | 123.1979 | 123.143 | 123.3902 | -16.1316
2676.5312 | 123.4131 | -98.4833 | 24.7787 | 0.14191 | 0.019508 | 0.00093569 | 0.014531 | -0.01763 | 0.0055392 | 0.0025529 | 0.14061 | 0.022157 | -0.011927 | 0.014845 | -0.0010082 | 0.0091431 | 1.2863 | 1.2451 | 1.1673 | 1.2863 | 1.4877 | 1.2314 | 1.0666 | 24.7696 | 24.7879 | 24.8016 | 24.7833 | 24.7147 | 8.7708 | 8.6746 | 99.7147 | 99.5499 | -23.291 | 99.7284 | 99.7696 | 0.21973 | -23.4924 | 107.254 | 107.1579 | 0.004577 | 123.2529 | 123.2849 | 16.127 | -0.064087 | 99.971 | 99.7696 | 99.6506 | -23.7122 | 123.2666 | 123.1979 | 123.2712 | -16.1041
2677.5156 | 123.468 | -98.4924 | 24.678 | 0.20294 | 0.013313 | 0.00093569 | 0.010258 | -0.021475 | -0.0019376 | 0.0072525 | 0.24742 | 0.020234 | -0.012354 | 0.011854 | -0.0014356 | 0.0082885 | 1.3412 | 1.3962 | 1.3 | 1.3458 | 1.4282 | 1.2863 | 1.1032 | 24.7787 | 24.8657 | 24.8474 | 24.7101 | 24.6597 | 8.7753 | 8.6838 | 99.7787 | 99.5956 | -23.2498 | 99.8886 | 99.8383 | 0.24262 | -23.3368 | 107.2678 | 107.1762 | 0.032043 | 123.2712 | 123.3398 | 16.1636 | -0.018311 | 99.9207 | 99.8337 | 99.7925 | -23.5748 | 123.2025 | 123.1522 | 123.3582 | -15.9943
2678.5156 | 123.4955 | -98.5153 | 24.6643 | 0.21057 | 0.01609 | 0.0011493 | 0.012822 | -0.018271 | 0.00083955 | 0.0029801 | 0.26268 | 0.020662 | -0.0091494 | 0.012068 | -0.0027172 | 0.010211 | 1.3733 | 1.3779 | 1.2955 | 1.3641 | 1.4191 | 1.2817 | 1.1078 | 24.8245 | 24.7742 | 24.852 | 24.6643 | 24.6048 | 8.7845 | 8.6746 | 99.7971 | 99.6231 | -23.2452 | 99.8932 | 99.8795 | 0.25635 | -23.291 | 107.2998 | 107.1899 | 0 | 123.3398 | 123.3673 | 16.1774 | -0.05951 | 99.9344 | 99.8886 | 99.8108 | -23.5565 | 123.1796 | 123.1201 | 123.2895 | -15.9897
2679.5156 | 123.4543 | -98.584 | 24.6414 | 0.16479 | 0.013527 | 0.0037127 | 0.0087628 | -0.02233 | -0.0019376 | 0.0051163 | 0.18639 | 0.019593 | -0.010645 | 0.010145 | -0.0033582 | 0.010852 | 1.3321 | 1.3596 | 1.268 | 1.3275 | 1.4282 | 1.2634 | 1.0895 | 24.678 | 24.7375 | 24.7559 | 24.6506 | 24.5865 | 8.7753 | 8.67 | 99.8474 | 99.6735 | -23.2132 | 99.9435 | 99.9115 | 0.23804 | -23.3093 | 107.3593 | 107.254 | 0.009156 | 123.262 | 123.3398 | 16.0858 | -0.054931 | 100.0122 | 99.9161 | 99.852 | -23.5519 | 123.2346 | 123.1705 | 123.3215 | -15.9714
2680.5156 | 123.4589 | -98.6481 | 24.6094 | -0.0030518 | 0.0088269 | 0.0052081 | 0.013463 | -0.017844 | -0.0034328 | 0.00084388 | 0.20927 | 0.019807 | -0.011286 | 0.013349 | -0.0046398 | 0.0095703 | 1.1627 | 1.1719 | 1.1673 | 1.3 | 1.3687 | 1.2131 | 1.0254 | 24.5911 | 24.6689 | 24.7009 | 24.614 | 24.5361 | 8.7799 | 8.6792 | 99.8611 | 99.6735 | -23.2407 | 99.8199 | 99.9481 | 0.27466 | -23.4467 | 107.428 | 107.3273 | 0.004578 | 123.2391 | 123.349 | 16.0217 | -0.073242 | 100.0168 | 99.8108 | 99.8154 | -23.584 | 123.262 | 123.1842 | 123.317 | -15.9302
2681.5312 | 123.4589 | -98.6755 | 24.5132 | 0.18768 | 0.01075 | 0.0030719 | 0.011113 | -0.019766 | -0.00044225 | 0.0010575 | 0.23979 | 0.018953 | -0.012354 | 0.012281 | -0.0014356 | 0.0097839 | 1.3596 | 1.4008 | 1.2863 | 1.3367 | 1.4465 | 1.2543 | 1.0986 | 24.6002 | 24.6552 | 24.6552 | 24.5453 | 24.4675 | 8.7845 | 8.6838 | 99.9298 | 99.7742 | -23.0667 | 100.0763 | 100.0122 | 0.23804 | -23.1537 | 107.46 | 107.3593 | 0.032043 | 123.2758 | 123.3307 | 15.9714 | -0.045777 | 100.1221 | 100.0351 | 99.9619 | -23.4146 | 123.2208 | 123.143 | 123.3307 | -15.8295
2682.5156 | 123.4726 | -98.7076 | 24.4858 | 0.18005 | 0.012245 | 0.0020037 | 0.014531 | -0.019126 | -0.00086945 | 0.0016983 | 0.2169 | 0.019807 | -0.0095768 | 0.012495 | -0.0018628 | 0.010211 | 1.3596 | 1.3824 | 1.2863 | 1.3412 | 1.4511 | 1.2726 | 1.0803 | 24.5911 | 24.6185 | 24.6231 | 24.5087 | 24.4308 | 8.7799 | 8.6746 | 99.9802 | 99.7879 | -23.0347 | 100.09 | 100.0488 | 0.26093 | -23.1262 | 107.4875 | 107.3822 | 0.022888 | 123.2986 | 123.3307 | 15.9485 | -0.054932 | 100.1587 | 100.0671 | 99.9939 | -23.4055 | 123.2162 | 123.1384 | 123.3261 | -15.8112
2683.5156 | 123.4772 | -98.7854 | 24.4263 | 0.035095 | 0.010322 | 0.0056353 | 0.012608 | -0.020194 | -0.002792 | 0.00041648 | -0.011978 | 0.018098 | -0.010431 | 0.01164 | -0.0037854 | 0.011707 | 1.3275 | 1.3596 | 1.268 | 1.3367 | 1.474 | 1.2543 | 1.0941 | 24.5087 | 24.5956 | 24.5911 | 24.4492 | 24.3805 | 8.7753 | 8.6838 | 100.0397 | 99.8795 | -22.9523 | 100.145 | 100.1221 | 0.24262 | -23.0988 | 107.5607 | 107.4692 | 0.022888 | 123.2941 | 123.3765 | 15.9073 | -0.045777 | 100.2594 | 100.1129 | 100.0534 | -23.3322 | 123.2346 | 123.1659 | 123.381 | -15.7425
2684.5156 | 123.4406 | -98.8129 | 24.3988 | 0.19531 | 0.011604 | 0.0028583 | 0.012181 | -0.018057 | 0.00083955 | 0.0023391 | 0.19402 | 0.018739 | -0.012781 | 0.013349 | -0.0025036 | 0.0093567 | 1.3412 | 1.355 | 1.2634 | 1.3229 | 1.4374 | 1.2589 | 1.0986 | 24.4446 | 24.5087 | 24.5041 | 24.4354 | 24.3164 | 8.7753 | 8.6746 | 100.0717 | 99.9115 | -22.9614 | 100.1678 | 100.1358 | 0.2243 | -23.0576 | 107.5882 | 107.4875 | 0.036621 | 123.2574 | 123.317 | 15.8295 | -0.082398 | 100.2502 | 100.1541 | 100.0763 | -23.3002 | 123.2483 | 123.1293 | 123.3215 | -15.7242
2685.5156 | 123.4634 | -98.8815 | 24.3759 | 0.19531 | 0.012245 | 0.0039263 | 0.013035 | -0.021262 | 0.0010532 | 0.0021255 | 0.17113 | 0.019807 | -0.013849 | 0.010572 | -0.0025036 | 0.0091431 | 1.3275 | 1.3596 | 1.2634 | 1.3046 | 1.442 | 1.268 | 1.0803 | 24.408 | 24.4583 | 24.4629 | 24.3805 | 24.2981 | 8.7753 | 8.6746 | 100.1495 | 99.9619 | -22.934 | 100.2411 | 100.1862 | 0.2243 | -23.0484 | 107.6569 | 107.5562 | 0.004577 | 123.2895 | 123.3444 | 15.7883 | -0.07782 | 100.3235 | 100.209 | 100.145 | -23.2956 | 123.262 | 123.1796 | 123.3398 | -15.7013
2686.5312 | 123.4863 | -98.8861 | 24.3027 | -0.02594 | 0.0088269 | 0.0047809 | 0.014317 | -0.018698 | -0.001083 | 0.0010575 | -0.034867 | 0.018312 | -0.011286 | 0.010572 | -0.0018628 | 0.0099975 | 1.355 | 1.3916 | 1.2817 | 1.3687 | 1.4511 | 1.2589 | 1.0941 | 24.4171 | 24.4949 | 24.4858 | 24.3393 | 24.2661 | 8.7845 | 8.6746 | 100.145 | 99.9802 | -22.8516 | 100.2777 | 100.2548 | 0.27466 | -22.9477 | 107.6706 | 107.5607 | 0.036621 | 123.3032 | 123.3719 | 15.8112 | -0.036621 | 100.3372 | 100.2411 | 100.1678 | -23.2086 | 123.2254 | 123.1522 | 123.381 | -15.6281
2687.5156 | 123.4589 | -98.9227 | 24.3164 | 0.11902 | 0.012672 | 0.00072209 | 0.013035 | -0.019766 | 0.0010532 | 0.00063028 | 0.18639 | 0.018312 | -0.012781 | 0.009504 | -0.00079463 | 0.010211 | 1.3458 | 1.3824 | 1.268 | 1.3184 | 1.4282 | 1.2543 | 1.0895 | 24.3301 | 24.3622 | 24.3759 | 24.2981 | 24.2065 | 8.7753 | 8.6746 | 100.177 | 100.0122 | -22.8882 | 100.3052 | 100.2411 | 0.22888 | -22.9706 | 107.6981 | 107.5974 | -0.01831 | 123.2529 | 123.2986 | 15.7013 | -0.10986 | 100.351 | 100.2686 | 100.1907 | -23.2269 | 123.2208 | 123.1293 | 123.2849 | -15.6418
2688.5156 | 123.5001 | -98.9502 | 24.2477 | 0.14954 | 0.015663 | 0.0037127 | 0.012181 | -0.017203 | 0.0012668 | 0.0038345 | 0.17113 | 0.020662 | -0.010645 | 0.011213 | -0.0016492 | 0.0063659 | 1.3779 | 1.387 | 1.2726 | 1.3458 | 1.4328 | 1.2451 | 1.0986 | 24.4492 | 24.3896 | 24.3988 | 24.2523 | 24.1608 | 8.7799 | 8.6746 | 100.1953 | 100.0488 | -22.8149 | 100.3372 | 100.296 | 0.24719 | -22.8699 | 107.7301 | 107.6248 | 0.004577 | 123.3994 | 123.349 | 15.7242 | -0.086975 | 100.383 | 100.3281 | 100.2228 | -23.1491 | 123.2025 | 123.111 | 123.3398 | -15.5731
2689.5156 | 123.4497 | -99.0143 | 24.2294 | 0.10376 | 0.011604 | 0.0022175 | 0.011326 | -0.019553 | -0.00065585 | 0.0019119 | -0.23323 | 0.020021 | -0.011072 | 0.01164 | -0.0031446 | 0.0080749 | 1.3 | 1.3367 | 1.2222 | 1.2909 | 1.4328 | 1.2222 | 1.062 | 24.2386 | 24.3027 | 24.3073 | 24.2203 | 24.1516 | 8.7753 | 8.6746 | 100.2365 | 100.0763 | -22.7966 | 100.351 | 100.3052 | 0.22888 | -22.9294 | 107.7896 | 107.6889 | -0.009155 | 123.2529 | 123.3215 | 15.6326 | -0.07782 | 100.4471 | 100.3143 | 100.2365 | -23.1674 | 123.2346 | 123.1659 | 123.317 | -15.5548
2690.5156 | 123.4863 | -99.0555 | 24.1562 | 0.042725 | 0.013313 | 0.00093569 | 0.011754 | -0.019339 | 0.0025486 | 0.0010575 | 0.13298 | 0.018525 | -0.012781 | 0.010786 | -0.0016492 | 0.0099975 | 1.3779 | 1.3916 | 1.2955 | 1.3412 | 1.4236 | 1.268 | 1.0941 | 24.2477 | 24.3164 | 24.3118 | 24.1974 | 24.1013 | 8.7845 | 8.6792 | 100.3235 | 100.1495 | -22.7325 | 100.4471 | 100.3967 | 0.24719 | -22.7783 | 107.84 | 107.7347 | 0.041199 | 123.3032 | 123.3673 | 15.6326 | -0.054932 | 100.4791 | 100.4334 | 100.351 | -23.0621 | 123.2529 | 123.1567 | 123.3719 | -15.477
2691.5469 | 123.4131 | -99.0967 | 24.1928 | -0.13275 | 0.017586 | 0.0024311 | 0.016667 | -0.018698 | 0.0059666 | 0.0044755 | -0.14931 | 0.02173 | -0.012567 | 0.013136 | -0.00058103 | 0.0095703 | 1.3367 | 1.3184 | 1.2131 | 1.3138 | 1.4603 | 1.2268 | 1.0483 | 24.2432 | 24.1837 | 24.2477 | 24.2157 | 24.1516 | 8.7799 | 8.6838 | 100.3235 | 100.145 | -22.7325 | 100.415 | 100.4105 | 0.2655 | -22.8561 | 107.8766 | 107.7805 | 0.022888 | 123.3398 | 123.3444 | 15.564 | -0.041199 | 100.5569 | 100.4334 | 100.3098 | -23.1445 | 123.3124 | 123.2483 | 123.2803 | -15.509
2692.5156 | 123.4818 | -99.1333 | 24.0829 | -0.9491 | 0.013313 | 0.0022175 | 0.014103 | -0.019766 | 0.0027622 | 0.0042619 | 0.17876 | 0.018953 | -0.012995 | 0.012068 | -0.0016492 | 0.0082885 | 1.3275 | 1.4099 | 1.3 | 1.3275 | 1.4053 | 1.2131 | 1.0437 | 24.1653 | 24.2477 | 24.2157 | 24.0829 | 24.0005 | 8.7799 | 8.6838 | 100.3464 | 100.177 | -22.6776 | 100.5432 | 100.4608 | 0.28381 | -22.7554 | 107.9132 | 107.8171 | 0 | 123.2986 | 123.349 | 15.5319 | -0.082398 | 100.5386 | 100.4608 | 100.4334 | -23.0392 | 123.2162 | 123.1338 | 123.381 | -15.3992
2693.5156 | 123.4589 | -99.1653 | 24.0601 | 0.13428 | 0.0090405 | 0.0039263 | 0.012822 | -0.018271 | -0.0019376 | 0.00041648 | 0.087204 | 0.01938 | -0.013208 | 0.012068 | -0.0025036 | 0.0091431 | 1.2772 | 1.3275 | 1.2405 | 1.3138 | 1.4282 | 1.2177 | 1.0666 | 24.0921 | 24.1837 | 24.1928 | 24.0646 | 23.9914 | 8.7799 | 8.6746 | 100.383 | 100.2319 | -22.6318 | 100.4929 | 100.4791 | 0.24719 | -22.7829 | 107.9453 | 107.84 | 0.004577 | 123.2574 | 123.3582 | 15.5182 | -0.068665 | 100.5936 | 100.4425 | 100.4059 | -22.9935 | 123.23 | 123.1567 | 123.349 | -15.3854
2694.5156 | 123.4268 | -99.2111 | 24.0051 | 0.14954 | 0.010536 | 0.0045673 | 0.012181 | -0.021475 | -0.001083 | 0.0019119 | 0.14824 | 0.020448 | -0.012995 | 0.0092904 | -0.0031446 | 0.0087157 | 1.2955 | 1.3504 | 1.2497 | 1.3046 | 1.4328 | 1.2589 | 1.0666 | 24.0372 | 24.1104 | 24.1196 | 24.0005 | 23.9365 | 8.7799 | 8.6792 | 100.47 | 100.2777 | -22.5723 | 100.5615 | 100.5157 | 0.23804 | -22.7097 | 107.991 | 107.8903 | -0.004578 | 123.2483 | 123.3307 | 15.4404 | -0.068665 | 100.6439 | 100.5066 | 100.4608 | -22.9385 | 123.2117 | 123.1476 | 123.3215 | -15.3259
2695.5156 | 123.5779 | -99.2661 | 23.9914 | -0.079346 | 0.01075 | 0.0062763 | 0.012608 | -0.019553 | -0.0023648 | 0.0010575 | -0.073013 | 0.017884 | -0.012995 | 0.012068 | -0.0018628 | 0.0082885 | 1.3641 | 1.4282 | 1.2863 | 1.3504 | 1.4374 | 1.2589 | 1.0666 | 24.0646 | 24.1882 | 24.1608 | 23.9868 | 23.8953 | 8.7753 | 8.6792 | 100.5249 | 100.3326 | -22.554 | 100.6943 | 100.6165 | 0.28381 | -22.6273 | 108.0414 | 107.9453 | -0.004578 | 123.3307 | 123.4268 | 15.4816 | -0.09613 | 100.7034 | 100.6302 | 100.5524 | -22.9248 | 123.2529 | 123.1613 | 123.4543 | -15.3122
2696.5312 | 123.4131 | -99.3347 | 23.9502 | -0.14801 | 0.017372 | 0.0032855 | 0.016026 | -0.019339 | 0.0046848 | 0.0027665 | -0.24086 | 0.021089 | -0.0089358 | 0.011427 | -0.00058103 | 0.0074341 | 1.268 | 1.268 | 1.1536 | 1.2726 | 1.4511 | 1.2177 | 1.0254 | 23.9456 | 24.0326 | 23.9731 | 23.9822 | 23.8586 | 8.7845 | 8.6746 | 100.5524 | 100.3601 | -22.4991 | 100.6027 | 100.6073 | 0.24719 | -22.6822 | 108.1192 | 108.0093 | 0.032044 | 123.2803 | 123.3078 | 15.2985 | -0.091552 | 100.7858 | 100.6027 | 100.4883 | -22.9248 | 123.317 | 123.1934 | 123.3673 | -15.2756
2697.5156 | 123.4543 | -99.3622 | 23.8907 | 0.073242 | 0.010963 | 0.0041401 | 0.0094038 | -0.020621 | -0.0025784 | 0.00084388 | 0.31609 | 0.016603 | -0.012354 | 0.011427 | -0.0033582 | 0.010211 | 1.2634 | 1.1765 | 1.0345 | 1.236 | 1.3916 | 1.1902 | 1.0162 | 23.8861 | 23.9868 | 24.0005 | 23.8861 | 23.79 | 8.7753 | 8.67 | 100.5524 | 100.3784 | -22.4991 | 100.5386 | 100.5981 | 0.21973 | -22.6273 | 108.1375 | 108.0322 | -0.004578 | 123.2483 | 123.3627 | 15.3305 | -0.10071 | 100.7538 | 100.6256 | 100.3967 | -22.8745 | 123.2483 | 123.1522 | 123.349 | -15.2206
2698.5156 | 123.4863 | -99.3668 | 23.8312 | 0.16479 | 0.015449 | 0.0024311 | 0.011326 | -0.018271 | 0.0021214 | 0.0023391 | 0.1635 | 0.019593 | -0.013849 | 0.011427 | -0.00036743 | 0.0085021 | 1.3275 | 1.3733 | 1.2772 | 1.3184 | 1.4099 | 1.2314 | 1.0803 | 23.909 | 23.9594 | 23.9639 | 23.8449 | 23.7534 | 8.7891 | 8.6746 | 100.5981 | 100.4471 | -22.4213 | 100.7401 | 100.6851 | 0.23804 | -22.5037 | 108.1558 | 108.0414 | 0.013733 | 123.2758 | 123.3307 | 15.2893 | -0.07782 | 100.7767 | 100.6943 | 100.6439 | -22.7509 | 123.2117 | 123.1201 | 123.3261 | -15.1566
2699.5156 | 123.468 | -99.4263 | 23.7808 | -0.0030518 | 0.0075451 | 0.0039263 | 0.013463 | -0.019339 | 0.00019875 | -0.00022432 | 0.056686 | 0.018953 | -0.013208 | 0.010145 | -0.0029308 | 0.010638 | 1.268 | 1.355 | 1.2405 | 1.3092 | 1.4328 | 1.2268 | 1.0757 | 23.8403 | 23.9273 | 23.9319 | 23.8083 | 23.7213 | 8.7799 | 8.6746 | 100.6531 | 100.502 | -22.348 | 100.7812 | 100.7355 | 0.23346 | -22.5128 | 108.2062 | 108.1009 | 0.027466 | 123.2666 | 123.3582 | 15.2573 | -0.05951 | 100.8591 | 100.6943 | 100.6668 | -22.7051 | 123.2346 | 123.1476 | 123.3536 | -15.1062
2700.5156 | 123.4909 | -99.4675 | 23.7396 | -0.086975 | 0.015236 | 0.0022175 | 0.014744 | -0.019553 | 0.0019078 | 0.0023391 | 0.14061 | 0.019807 | -0.01214 | 0.012495 | -0.0018628 | 0.010425 | 1.3412 | 1.387 | 1.2772 | 1.3367 | 1.4008 | 1.2268 | 1.0529 | 23.8312 | 23.8907 | 23.8724 | 23.7259 | 23.6572 | 8.7891 | 8.6746 | 100.6943 | 100.5203 | -22.3389 | 100.8545 | 100.8041 | 0.28381 | -22.3984 | 108.2565 | 108.1421 | -0.013733 | 123.2986 | 123.3398 | 15.1978 | -0.082397 | 100.8682 | 100.8087 | 100.7446 | -22.6868 | 123.1934 | 123.1247 | 123.3582 | -15.065
2701.5312 | 123.3765 | -99.559 | 23.735 | 0.28687 | 0.01844 | 0.0017901 | 0.015172 | -0.017844 | 0.0031894 | 0.0019119 | 0.079574 | 0.021516 | -0.0087222 | 0.013349 | -0.0010082 | 0.0080749 | 1.2589 | 1.2177 | 1.1398 | 1.2589 | 1.4557 | 1.1902 | 1.0345 | 23.6984 | 23.7076 | 23.7122 | 23.7534 | 23.6755 | 8.7753 | 8.67 | 100.7492 | 100.5936 | -22.2794 | 100.7767 | 100.8179 | 0.2243 | -22.4762 | 108.3344 | 108.2291 | 0.018311 | 123.2574 | 123.2712 | 15.0421 | -0.059509 | 101.0147 | 100.8179 | 100.6989 | -22.7005 | 123.3124 | 123.2346 | 123.2666 | -15.065
2702.5156 | 123.4589 | -99.5499 | 23.6435 | 0.18005 | 0.01374 | 0.0024311 | 0.013249 | -0.01998 | -0.0025784 | 0.0023391 | 0.17876 | 0.021516 | -0.013208 | 0.013136 | -0.003999 | 0.011279 | 1.3321 | 1.3687 | 1.268 | 1.3138 | 1.4008 | 1.2405 | 1.0574 | 23.7396 | 23.79 | 23.7717 | 23.6618 | 23.6069 | 8.7845 | 8.6792 | 100.7904 | 100.6073 | -22.2427 | 100.9186 | 100.8636 | 0.25635 | -22.3114 | 108.3344 | 108.2291 | 0.01831 | 123.2895 | 123.3215 | 15.0925 | -0.036621 | 100.9506 | 100.882 | 100.8179 | -22.5861 | 123.2117 | 123.1567 | 123.3398 | -14.9643
2703.5156 | 123.468 | -99.5956 | 23.6298 | 0.12665 | 0.010536 | 0.00029489 | 0.012394 | -0.021048 | -0.0019376 | -0.00022432 | 0.22453 | 0.020448 | -0.013208 | 0.012281 | -0.0020764 | 0.010211 | 1.3092 | 1.3367 | 1.2405 | 1.2817 | 1.4191 | 1.2405 | 1.0849 | 23.671 | 23.7213 | 23.735 | 23.6252 | 23.5611 | 8.7753 | 8.6792 | 100.8362 | 100.6805 | -22.2107 | 100.9323 | 100.8774 | 0.19684 | -22.3206 | 108.371 | 108.2748 | -0.004578 | 123.2666 | 123.3307 | 15.0558 | -0.068665 | 101.0147 | 100.9048 | 100.8362 | -22.5449 | 123.2208 | 123.1567 | 123.317 | -14.9506
2704.5156 | 123.4955 | -99.6414 | 23.5565 | 0.24872 | 0.015663 | 0.0030719 | 0.012181 | -0.016562 | 0.0027622 | 0.0027665 | -0.72151 | 0.018525 | -0.011072 | 0.013349 | -0.0012218 | 0.010425 | 1.3412 | 1.3596 | 1.2543 | 1.3412 | 1.4099 | 1.2268 | 1.0712 | 23.671 | 23.6984 | 23.7305 | 23.5657 | 23.4879 | 8.7753 | 8.6884 | 100.8682 | 100.7126 | -22.1466 | 101.001 | 100.9827 | 0.27008 | -22.2153 | 108.4167 | 108.3298 | 0.009155 | 123.3124 | 123.3719 | 15.0421 | -0.068665 | 101.0513 | 100.9827 | 100.8957 | -22.4854 | 123.2071 | 123.1293 | 123.3398 | -14.8682
2705.5156 | 123.4543 | -99.6643 | 23.5291 | 0.15717 | 0.01075 | 0.0024311 | 0.010472 | -0.020621 | -0.00065585 | 0.00084388 | 0.23216 | 0.020021 | -0.011713 | 0.012922 | -0.0042126 | 0.0082885 | 1.3184 | 1.3367 | 1.2497 | 1.3046 | 1.4099 | 1.2222 | 1.0895 | 23.584 | 23.6572 | 23.6572 | 23.5611 | 23.497 | 8.7753 | 8.6746 | 100.8865 | 100.7538 | -22.1191 | 101.001 | 100.9689 | 0.21515 | -22.2107 | 108.4396 | 108.3389 | 0.032043 | 123.2483 | 123.3215 | 14.9826 | -0.032044 | 101.0742 | 100.9827 | 100.914 | -22.4396 | 123.2254 | 123.1613 | 123.3215 | -14.8544
2706.5156 | 123.3673 | -99.7284 | 23.5474 | -0.20142 | 0.013954 | 0.0037127 | 0.015172 | -0.019126 | -0.00022865 | 0.00020288 | -0.26375 | 0.020875 | -0.012781 | 0.012495 | -0.0048534 | 0.0078613 | 1.2817 | 1.2955 | 1.1902 | 1.2955 | 1.4465 | 1.2085 | 1.0529 | 23.4833 | 23.584 | 23.5565 | 23.5565 | 23.4833 | 8.7753 | 8.6746 | 100.9369 | 100.7812 | -22.1008 | 101.0239 | 101.0239 | 0.24262 | -22.2656 | 108.5037 | 108.403 | 0.009156 | 123.2117 | 123.2849 | 14.8819 | -0.064087 | 101.1749 | 101.0101 | 100.9186 | -22.4945 | 123.2849 | 123.2117 | 123.3124 | -14.8727
2707.5156 | 123.5001 | -99.733 | 23.4879 | -0.041199 | 0.010109 | 0.0069171 | 0.010685 | -0.018271 | -0.0030056 | -0.00022432 | -0.0043486 | 0.018953 | -0.012567 | 0.011854 | -0.0042126 | 0.010425 | 1.3092 | 1.3641 | 1.2772 | 1.3321 | 1.4191 | 1.2451 | 1.0666 | 23.5519 | 23.6435 | 23.6343 | 23.4695 | 23.4055 | 8.7708 | 8.6792 | 100.9781 | 100.7996 | -22.0688 | 101.0971 | 101.0651 | 0.2655 | -22.1786 | 108.5037 | 108.4122 | -0.018311 | 123.2849 | 123.3673 | 14.9551 | -0.082397 | 101.152 | 101.0422 | 101.0101 | -22.4213 | 123.2025 | 123.1384 | 123.3765 | -14.8087
2708.5156 | 123.4726 | -99.8062 | 23.4467 | -0.26245 | 0.0079723 | 0.0052081 | 0.014531 | -0.019126 | -0.0034328 | 0.0012711 | 0.033798 | 0.019807 | -0.014276 | 0.0086496 | -0.003999 | 0.0091431 | 1.2634 | 1.3138 | 1.2268 | 1.2817 | 1.4053 | 1.1948 | 1.0529 | 23.4558 | 23.5611 | 23.5657 | 23.4604 | 23.3688 | 8.7799 | 8.67 | 101.001 | 100.8591 | -22.0413 | 101.12 | 101.088 | 0.22888 | -22.1832 | 108.5861 | 108.4763 | 0.013733 | 123.262 | 123.3719 | 14.8956 | -0.07782 | 101.2115 | 101.0696 | 101.033 | -22.3938 | 123.2666 | 123.175 | 123.3673 | -14.7766
2709.5156 | 123.4589 | -99.8428 | 23.378 | 0.16479 | 0.012459 | 0.0020037 | 0.014317 | -0.021903 | 0.00019875 | 0.0029801 | 0.10246 | 0.020234 | -0.010858 | 0.011213 | -0.0042126 | 0.0082885 | 1.2955 | 1.3275 | 1.2451 | 1.3 | 1.4099 | 1.2268 | 1.0757 | 23.4009 | 23.4787 | 23.4833 | 23.3871 | 23.3139 | 8.7845 | 8.6746 | 101.0696 | 100.9186 | -21.9681 | 101.1703 | 101.1429 | 0.2243 | -22.0825 | 108.6273 | 108.5175 | 0.009155 | 123.2437 | 123.3261 | 14.8087 | -0.064087 | 101.2527 | 101.1383 | 101.088 | -22.3022 | 123.23 | 123.1567 | 123.3215 | -14.7034
2710.5156 | 123.4863 | -99.8611 | 23.3459 | 0.21057 | 0.013099 | 0.0026447 | 0.012181 | -0.020407 | 0.001694 | 0.0014847 | 0.17113 | 0.018953 | -0.01214 | 0.012922 | -0.00058103 | 0.0087157 | 1.3458 | 1.3596 | 1.2589 | 1.3092 | 1.4008 | 1.236 | 1.0666 | 23.4375 | 23.4879 | 23.4787 | 23.3505 | 23.2773 | 8.7845 | 8.6838 | 101.0971 | 100.9277 | -21.9452 | 101.2207 | 101.1703 | 0.24262 | -22.0001 | 108.6456 | 108.5449 | 0.004578 | 123.2986 | 123.3398 | 14.7949 | -0.068664 | 101.2619 | 101.207 | 101.12 | -22.2794 | 123.2117 | 123.1384 | 123.349 | -14.6622
2711.5156 | 123.4177 | -99.9573 | 23.3139 | -0.10223 | 0.01844 | 0.0026447 | 0.014958 | -0.017203 | 0.007462 | 0.0014847 | -0.18745 | 0.021302 | -0.011713 | 0.014417 | -0.00015383 | 0.0076477 | 1.3092 | 1.2863 | 1.1719 | 1.2863 | 1.4374 | 1.1948 | 1.0117 | 23.3093 | 23.4055 | 23.3459 | 23.3368 | 23.2635 | 8.7845 | 8.6838 | 101.152 | 100.9689 | -21.8765 | 101.2436 | 101.2436 | 0.27466 | -22.0047 | 108.7418 | 108.6411 | 0.022888 | 123.2666 | 123.3032 | 14.6622 | -0.050354 | 101.3947 | 101.2665 | 101.1291 | -22.3022 | 123.2941 | 123.2208 | 123.3627 | -14.6301
2712.5156 | 123.4955 | -99.9756 | 23.2132 | 0.31738 | 0.014168 | 0.0026447 | 0.010685 | -0.018698 | 0.0014804 | 0.0038345 | 0.17876 | 0.018739 | -0.010431 | 0.013777 | -0.0025036 | 0.010211 | 1.3367 | 1.3458 | 1.2405 | 1.3138 | 1.387 | 1.2039 | 1.0712 | 23.3139 | 23.14 | 23.2315 | 23.1857 | 23.1445 | 8.7799 | 8.6746 | 101.1795 | 101.0468 | -21.8262 | 101.3214 | 101.2894 | 0.24262 | -21.8765 | 108.7555 | 108.6502 | -0.027466 | 123.2895 | 123.2071 | 14.5569 | -0.068665 | 101.3626 | 101.3123 | 101.2161 | -22.142 | 123.1613 | 123.1201 | 123.1155 | -14.5386
2713.5156 | 123.4497 | -100.0214 | 23.2086 | 0.012207 | 0.010963 | 0.0020037 | 0.010899 | -0.022971 | -0.0021512 | 0.0021255 | 0.087204 | 0.021089 | -0.012995 | 0.009504 | -0.0035718 | 0.013202 | 1.2543 | 1.3138 | 1.1948 | 1.2817 | 1.3962 | 1.2222 | 1.0345 | 23.1995 | 23.2635 | 23.3276 | 23.1766 | 23.1354 | 8.7753 | 8.6746 | 101.2436 | 101.0559 | -21.8124 | 101.3351 | 101.3031 | 0.24719 | -21.9543 | 108.7967 | 108.696 | -0.032043 | 123.2208 | 123.349 | 14.653 | -0.073242 | 101.4175 | 101.2756 | 101.2161 | -22.1741 | 123.1979 | 123.1567 | 123.2849 | -14.534
2714.5156 | 123.4543 | -100.0443 | 23.1628 | 0.16479 | 0.010963 | 0.0028583 | 0.015385 | -0.021048 | -1.505e-05 | 0.0021255 | 0.2169 | 0.019807 | -0.013849 | 0.013349 | -0.0018628 | 0.010211 | 1.3229 | 1.355 | 1.236 | 1.3 | 1.4053 | 1.1902 | 1.0529 | 23.2178 | 23.3002 | 23.2819 | 23.1949 | 23.085 | 8.7799 | 8.6746 | 101.2344 | 101.0971 | -21.7575 | 101.3992 | 101.3443 | 0.24719 | -21.8399 | 108.8242 | 108.7189 | 0.032043 | 123.262 | 123.3261 | 14.6072 | -0.07782 | 101.4496 | 101.3672 | 101.2802 | -22.11 | 123.2391 | 123.1293 | 123.3444 | -14.4882
2715.5156 | 123.5001 | -100.0717 | 23.1354 | -0.056458 | 0.0088269 | 0.0052081 | 0.0096174 | -0.016776 | -0.0032192 | -0.00086512 | -0.011978 | 0.019166 | -0.010645 | 0.011213 | -0.0025036 | 0.0095703 | 1.3 | 1.355 | 1.2451 | 1.3138 | 1.3962 | 1.2314 | 1.062 | 23.2224 | 23.3002 | 23.2956 | 23.1491 | 23.0988 | 8.7799 | 8.6838 | 101.3031 | 101.1337 | -21.7392 | 101.4267 | 101.3855 | 0.25177 | -21.8353 | 108.8516 | 108.7555 | 0.013733 | 123.2941 | 123.3673 | 14.6118 | -0.036621 | 101.4679 | 101.3718 | 101.3168 | -22.0734 | 123.2208 | 123.1705 | 123.3719 | -14.4516
2716.5156 | 123.5001 | -100.1038 | 23.0804 | -0.033569 | 0.0079723 | 0.0058491 | 0.011967 | -0.018485 | -0.0021512 | 0.0010575 | -0.019608 | 0.019807 | -0.014063 | 0.01164 | -0.0035718 | 0.0085021 | 1.3046 | 1.3641 | 1.2543 | 1.3184 | 1.4191 | 1.2131 | 1.0666 | 23.1766 | 23.2544 | 23.2635 | 23.1125 | 23.0164 | 8.7845 | 8.6792 | 101.3168 | 101.1703 | -21.6614 | 101.4679 | 101.4221 | 0.25177 | -21.7758 | 108.8882 | 108.783 | 0.032044 | 123.2803 | 123.3673 | 14.5844 | -0.064087 | 101.5228 | 101.4084 | 101.358 | -22.0139 | 123.2162 | 123.1201 | 123.3582 | -14.4012
2717.5156 | 123.3948 | -100.2182 | 23.0072 | 0.10376 | 0.012672 | 0.0045673 | 0.011967 | -0.017844 | -1.505e-05 | 0.00063028 | 0.079574 | 0.019807 | -0.012781 | 0.010145 | -0.0035718 | 0.0095703 | 1.2955 | 1.3092 | 1.2131 | 1.2772 | 1.4145 | 1.2177 | 1.0574 | 23.085 | 23.1537 | 23.1583 | 23.0621 | 22.9797 | 8.7799 | 8.6746 | 101.4359 | 101.2756 | -21.5927 | 101.5274 | 101.4954 | 0.21973 | -21.7117 | 108.9981 | 108.8928 | 0.054932 | 123.3032 | 123.3765 | 14.4836 | -0.027466 | 101.6327 | 101.5137 | 101.4313 | -21.9498 | 123.2803 | 123.1979 | 123.3719 | -14.3326
2718.5156 | 123.4863 | -100.2182 | 22.966 | 1.0117 | 0.012031 | 0.0037127 | 0.011754 | -0.020194 | 0.0031894 | 0.00063028 | 0.17876 | 0.020875 | -0.0085086 | 0.0099314 | -0.0031446 | 0.0070067 | 1.3596 | 1.3229 | 1.236 | 1.3046 | 1.355 | 1.1856 | 1.0162 | 23.0896 | 23.1491 | 23.1125 | 23.0118 | 22.9294 | 8.7799 | 8.6792 | 101.4038 | 101.2344 | -21.611 | 101.5411 | 101.5228 | 0.28839 | -21.6064 | 108.9981 | 108.8974 | 0.045777 | 123.3078 | 123.3307 | 14.4333 | -0.036621 | 101.5732 | 101.5778 | 101.4542 | -21.9498 | 123.23 | 123.1476 | 123.3673 | -14.2868
2719.5156 | 123.4909 | -100.2686 | 22.9477 | -0.048828 | 0.011177 | 0.0034991 | 0.014103 | -0.019766 | 0.00019875 | 0.00084388 | -0.0043486 | 0.018953 | -0.013849 | 0.010359 | -0.0025036 | 0.0085021 | 1.3046 | 1.3504 | 1.236 | 1.3092 | 1.4053 | 1.2131 | 1.0483 | 23.0255 | 23.1262 | 23.1079 | 22.966 | 22.9019 | 8.7799 | 8.6838 | 101.4816 | 101.3168 | -21.5424 | 101.619 | 101.5778 | 0.26093 | -21.6431 | 109.0485 | 108.9523 | 0.01831 | 123.2941 | 123.3765 | 14.4241 | -0.045776 | 101.6739 | 101.5732 | 101.5045 | -21.8994 | 123.2346 | 123.1705 | 123.3948 | -14.2639
2720.5156 | 123.5001 | -100.2869 | 22.9202 | -0.041199 | 0.0096813 | 0.0060627 | 0.010685 | -0.022971 | 0.00041235 | -1.0724e-05 | -0.011978 | 0.018739 | -0.013636 | 0.011427 | -0.0031446 | 0.0097839 | 1.3138 | 1.3504 | 1.2268 | 1.3046 | 1.3916 | 1.1948 | 1.0483 | 22.9889 | 23.085 | 23.0667 | 22.9111 | 22.8653 | 8.7845 | 8.6746 | 101.4816 | 101.3351 | -21.5286 | 101.6373 | 101.5915 | 0.25635 | -21.6064 | 109.0714 | 108.9615 | -0.009155 | 123.2758 | 123.3536 | 14.3921 | -0.054932 | 101.6785 | 101.6006 | 101.5137 | -21.8719 | 123.1979 | 123.1522 | 123.3719 | -14.2456
2721.5156 | 123.3994 | -100.3967 | 22.9065 | -0.17853 | 0.013099 | 0.0020037 | 0.016453 | -0.018271 | 0.0036166 | 0.00084388 | -0.26375 | 0.020875 | -0.009363 | 0.012281 | 5.9768e-05 | 0.0072205 | 1.236 | 1.2222 | 1.1215 | 1.2268 | 1.4282 | 1.1536 | 0.98419 | 22.847 | 22.9202 | 22.8882 | 22.9156 | 22.8516 | 8.7753 | 8.6792 | 101.5503 | 101.3809 | -21.4783 | 101.619 | 101.6235 | 0.24262 | -21.6705 | 109.1721 | 109.0759 | 0.009155 | 123.2437 | 123.2849 | 14.209 | -0.054932 | 101.825 | 101.6327 | 101.5182 | -21.9223 | 123.3124 | 123.2483 | 123.317 | -14.2273
2722.5156 | 123.4451 | -100.4334 | 22.7966 | 0.17242 | 0.013313 | 0.0032855 | 0.012181 | -0.019766 | -0.0019376 | 0.0021255 | 0.14824 | 0.018525 | -0.013422 | 0.010999 | -0.0031446 | 0.010638 | 1.2589 | 1.3046 | 1.1993 | 1.268 | 1.387 | 1.2222 | 1.0208 | 22.8424 | 22.9111 | 22.9248 | 22.8058 | 22.7463 | 8.7799 | 8.6792 | 101.6556 | 101.4542 | -21.4096 | 101.738 | 101.7014 | 0.24719 | -21.5378 | 109.2133 | 109.1125 | 0.009155 | 123.2758 | 123.3582 | 14.2456 | -0.050354 | 101.8204 | 101.6922 | 101.6327 | -21.7758 | 123.2391 | 123.1796 | 123.3444 | -14.1174
2723.5156 | 123.5367 | -100.4517 | 22.7509 | -0.0030518 | 0.0094677 | 0.0030719 | 0.014103 | -0.020194 | -0.0030056 | 0.00084388 | -0.10353 | 0.019166 | -0.013422 | 0.010359 | -0.0012218 | 0.0087157 | 1.3184 | 1.387 | 1.2589 | 1.3092 | 1.3641 | 1.2177 | 1.0437 | 22.8699 | 22.8836 | 23.1628 | 22.8012 | 22.7417 | 8.7891 | 8.6838 | 101.6693 | 101.4954 | -21.3867 | 101.8387 | 101.7609 | 0.2655 | -21.4325 | 109.2407 | 109.1354 | 0.050354 | 123.3215 | 123.6145 | 14.4791 | -0.009155 | 101.8158 | 101.77 | 101.7105 | -21.7072 | 123.2529 | 123.1934 | 123.3353 | -14.0671
2724.5156 | 123.4955 | -100.4929 | 22.7463 | -0.010681 | 0.010963 | 0.0054217 | 0.013676 | -0.020194 | -0.0038602 | 0.0023391 | -0.027237 | 0.019593 | -0.013636 | 0.0099314 | -0.003999 | 0.0095703 | 1.2863 | 1.3321 | 1.2268 | 1.2909 | 1.4191 | 1.2085 | 1.0391 | 22.8058 | 22.8928 | 22.879 | 22.7554 | 22.6639 | 8.7753 | 8.6792 | 101.7014 | 101.532 | -21.3272 | 101.825 | 101.7838 | 0.25177 | -21.46 | 109.2682 | 109.1721 | 0.009155 | 123.2986 | 123.3719 | 14.1998 | -0.082398 | 101.9119 | 101.7792 | 101.7197 | -21.7072 | 123.2483 | 123.1567 | 123.3856 | -14.0671
2725.5156 | 123.4543 | -100.5295 | 22.6776 | 0.18005 | 0.011177 | 0.0052081 | 0.012394 | -0.019766 | -0.0012966 | 0.00041648 | 0.049057 | 0.018953 | -0.011072 | 0.011427 | -0.0031446 | 0.0099975 | 1.2405 | 1.2726 | 1.1856 | 1.268 | 1.3321 | 1.1581 | 0.99335 | 22.7234 | 22.8058 | 22.8012 | 22.7188 | 22.6135 | 8.7753 | 8.6792 | 101.6876 | 101.5228 | -21.3455 | 101.8021 | 101.7975 | 0.27466 | -21.4371 | 109.3048 | 109.2087 | 0.041199 | 123.2529 | 123.3307 | 14.122 | -0.064087 | 101.8616 | 101.77 | 101.7151 | -21.6843 | 123.2483 | 123.143 | 123.3353 | -13.9984
2726.5156 | 123.5001 | -100.5661 | 22.6593 | -0.40741 | 0.011177 | 0.0024311 | 0.012394 | -0.020835 | -1.505e-05 | 0.00020288 | -0.080643 | 0.019166 | -0.014276 | 0.012068 | -0.0016492 | 0.0095703 | 1.3046 | 1.3733 | 1.2497 | 1.3184 | 1.3824 | 1.1902 | 1.0254 | 22.7188 | 22.8378 | 22.7875 | 22.6639 | 22.5906 | 8.7753 | 8.6838 | 101.7563 | 101.5915 | -21.2769 | 101.9394 | 101.8845 | 0.29297 | -21.3547 | 109.3414 | 109.2499 | 0.004577 | 123.2849 | 123.3536 | 14.1037 | -0.068665 | 101.9485 | 101.8707 | 101.8158 | -21.6339 | 123.23 | 123.1567 | 123.4039 | -13.9755
2727.5156 | 123.5138 | -100.589 | 22.5998 | -0.02594 | 0.0079723 | 0.0032855 | 0.010899 | -0.020407 | 0.00083955 | 0.0023391 | -0.034867 | 0.018098 | -0.012567 | 0.010786 | -0.0025036 | 0.0093567 | 1.3092 | 1.3824 | 1.2589 | 1.3138 | 1.4008 | 1.1993 | 1.0391 | 22.7188 | 22.8058 | 22.7783 | 22.6227 | 22.5128 | 8.7891 | 8.6838 | 101.7883 | 101.6281 | -21.199 | 101.9714 | 101.9028 | 0.27466 | -21.2906 | 109.3781 | 109.2728 | 0.022889 | 123.3078 | 123.3673 | 14.0945 | -0.086975 | 101.9897 | 101.8982 | 101.8478 | -21.5607 | 123.2117 | 123.1018 | 123.3948 | -13.916
2728.5156 | 123.4497 | -100.6485 | 22.5769 | 0.21057 | 0.01139 | 0.0045673 | 0.013676 | -0.021689 | 0.0010532 | 0.0034073 | 0.19402 | 0.018739 | -0.010858 | 0.011427 | -0.003999 | 0.010638 | 1.2726 | 1.3229 | 1.2085 | 1.268 | 1.3916 | 1.1948 | 1.0345 | 22.6227 | 22.6868 | 22.6776 | 22.5906 | 22.4991 | 8.7753 | 8.6746 | 101.8433 | 101.683 | -21.1853 | 101.9714 | 101.9165 | 0.23346 | -21.3043 | 109.4238 | 109.3231 | 0.013733 | 123.2712 | 123.3261 | 14.003 | -0.07782 | 102.0401 | 101.9211 | 101.857 | -21.5424 | 123.2391 | 123.1476 | 123.3353 | -13.9023
2729.5156 | 123.4863 | -100.6943 | 22.522 | 0.0045777 | 0.0094677 | 0.0045673 | 0.013035 | -0.022116 | -0.00044225 | 0.0019119 | -0.019608 | 0.018739 | -0.011499 | 0.012708 | -0.0059216 | 0.0091431 | 1.2589 | 1.3275 | 1.2085 | 1.2955 | 1.4008 | 1.181 | 1.03 | 22.6044 | 22.673 | 22.6822 | 22.5677 | 22.4533 | 8.7753 | 8.6838 | 101.8753 | 101.7242 | -21.1212 | 102.0218 | 101.9897 | 0.2655 | -21.2631 | 109.4696 | 109.3781 | 0.045776 | 123.2986 | 123.3765 | 13.9984 | -0.068665 | 102.095 | 101.9531 | 101.9028 | -21.492 | 123.262 | 123.1476 | 123.3673 | -13.8382
2730.5156 | 123.4314 | -100.7172 | 22.4762 | 0.18005 | 0.012459 | 0.0028583 | 0.014103 | -0.017417 | 0.0021214 | 0.0021255 | 0.1635 | 0.02173 | -0.011927 | 0.011854 | -0.0025036 | 0.0082885 | 1.2634 | 1.3138 | 1.2085 | 1.2634 | 1.3779 | 1.1902 | 1.0437 | 22.5357 | 22.5815 | 22.5815 | 22.5037 | 22.4167 | 8.7753 | 8.6746 | 101.9073 | 101.7609 | -21.0983 | 102.0309 | 101.9806 | 0.21973 | -21.2128 | 109.4925 | 109.3918 | 0.027466 | 123.2529 | 123.2986 | 13.9069 | -0.059509 | 102.095 | 101.9806 | 101.9257 | -21.4325 | 123.2208 | 123.1338 | 123.2986 | -13.8016
2731.5312 | 123.4085 | -100.795 | 22.5128 | -0.0030518 | 0.020363 | 8.1086e-05 | 0.016453 | -0.01763 | 0.0053256 | 0.0025529 | -0.080643 | 0.023225 | -0.01214 | 0.012922 | 0.0013416 | 0.0070067 | 1.2955 | 1.2589 | 1.1398 | 1.2451 | 1.387 | 1.1627 | 0.96588 | 22.4854 | 22.5449 | 22.4762 | 22.5174 | 22.4304 | 8.7753 | 8.67 | 101.9577 | 101.7609 | -21.1258 | 102.0538 | 102.0401 | 0.27924 | -21.2173 | 109.5703 | 109.465 | 0.004578 | 123.2803 | 123.2712 | 13.8062 | -0.082397 | 102.182 | 102.0905 | 101.9348 | -21.5469 | 123.3124 | 123.2254 | 123.3398 | -13.8428
2732.5156 | 123.4909 | -100.8362 | 22.4167 | 0.050354 | 0.01075 | 0.0011493 | 0.012394 | -0.01998 | -0.0038602 | 0.0010575 | -0.011978 | 0.017671 | -0.012781 | 0.012922 | -0.0031446 | 0.0087157 | 1.2451 | 1.3229 | 1.2039 | 1.2726 | 1.387 | 1.1993 | 1.0162 | 22.4579 | 22.5494 | 22.5403 | 22.3892 | 22.3343 | 8.7799 | 8.6838 | 102.0355 | 101.8524 | -21.0297 | 102.1591 | 102.1088 | 0.25635 | -21.1716 | 109.6161 | 109.52 | -0.027466 | 123.2941 | 123.3765 | 13.8565 | -0.082397 | 102.2232 | 102.0813 | 102.0401 | -21.4005 | 123.2254 | 123.1705 | 123.3856 | -13.7329
2733.5156 | 123.4909 | -100.8636 | 22.3389 | 0.019836 | 0.010536 | 0.0045673 | 0.01154 | -0.016989 | -0.0038602 | 0.0014847 | 0.049057 | 0.021302 | -0.013636 | 0.010786 | -0.0025036 | 0.0097839 | 1.236 | 1.3046 | 1.1902 | 1.2634 | 1.3733 | 1.1948 | 1.0162 | 22.4121 | 22.4945 | 22.4945 | 22.348 | 22.2885 | 8.7799 | 8.6792 | 102.0584 | 101.8799 | -20.9656 | 102.1683 | 102.1271 | 0.24719 | -21.1029 | 109.6436 | 109.5428 | 0.009155 | 123.2758 | 123.3582 | 13.8153 | -0.050354 | 102.2369 | 102.0996 | 102.0538 | -21.3226 | 123.2117 | 123.1522 | 123.3582 | -13.6597
2734.5156 | 123.4634 | -100.9003 | 22.3663 | 0.057983 | 0.01139 | 0.0047809 | 0.0096174 | -0.019126 | -0.0012966 | -0.0010787 | 0.14824 | 0.01938 | -0.011499 | 0.011213 | -0.0014356 | 0.0078613 | 1.1444 | 1.1261 | 1.0986 | 1.2634 | 1.3275 | 1.1307 | 0.95673 | 22.3618 | 22.4487 | 22.467 | 22.3618 | 22.2839 | 8.7753 | 8.6655 | 102.0309 | 101.857 | -21.0388 | 102.0264 | 102.1637 | 0.3067 | -21.2219 | 109.6756 | 109.5657 | -0.004578 | 123.262 | 123.3673 | 13.8016 | -0.082397 | 102.2278 | 102.0447 | 101.9989 | -21.4096 | 123.262 | 123.1842 | 123.349 | -13.7009
2735.5156 | 123.4955 | -101.0651 | 22.1329 | 1.004 | 0.012459 | 0.0037127 | 0.014103 | -0.018912 | -0.00065585 | 0.00063028 | -0.1722 | 0.017884 | -0.012354 | 0.010572 | -0.00229 | 0.0087157 | 1.3184 | 1.3275 | 1.1948 | 1.2955 | 1.3458 | 1.1902 | 1.0025 | 22.2382 | 22.3434 | 22.2931 | 22.1787 | 22.0642 | 8.7753 | 8.6792 | 102.2552 | 102.0676 | -20.787 | 102.3926 | 102.3605 | 0.29297 | -20.8145 | 109.8404 | 109.7443 | 0.045776 | 123.3032 | 123.3582 | 13.6139 | -0.068665 | 102.4109 | 102.3834 | 102.2598 | -21.1304 | 123.2437 | 123.1293 | 123.4085 | -13.4537
2736.5156 | 123.4314 | -101.1475 | 22.1329 | -0.12512 | 0.019081 | 0.0013629 | 0.015172 | -0.018057 | 0.0070346 | 0.0021255 | -0.20271 | 0.02173 | -0.011286 | 0.01399 | 0.0013416 | 0.0067931 | 1.2497 | 1.268 | 1.1261 | 1.2589 | 1.3779 | 1.1353 | 0.9613 | 22.2153 | 22.1603 | 22.1466 | 22.1603 | 22.0825 | 8.7753 | 8.6792 | 102.2827 | 102.1088 | -20.755 | 102.4155 | 102.4063 | 0.29755 | -20.8832 | 109.9228 | 109.8267 | 0.027465 | 123.3627 | 123.2941 | 13.4674 | -0.050354 | 102.5253 | 102.3972 | 102.2736 | -21.1716 | 123.3078 | 123.23 | 123.3078 | -13.4537
2737.5156 | 123.5229 | -100.9598 | 22.2336 | -0.033569 | 0.011818 | 0.0056353 | 0.013463 | -0.019339 | -0.002792 | -0.00022432 | -0.027237 | 0.018739 | -0.012995 | 0.013777 | -0.0044262 | 0.01192 | 1.2589 | 1.3824 | 1.2497 | 1.2863 | 1.3779 | 1.1993 | 1.03 | 22.3114 | 22.4304 | 22.403 | 22.2336 | 22.1603 | 8.7845 | 8.6838 | 102.1591 | 101.9897 | -20.8557 | 102.3422 | 102.2461 | 0.25635 | -20.9747 | 109.7443 | 109.6436 | 0 | 123.2712 | 123.3627 | 13.7192 | -0.073243 | 102.3376 | 102.2186 | 102.2095 | -21.2036 | 123.1934 | 123.1201 | 123.3902 | -13.5498
2738.5156 | 123.4955 | -101.0101 | 22.2198 | 0.012207 | 0.0098951 | 0.0039263 | 0.010685 | -0.020194 | 0.00062595 | 0.0012711 | 0.026169 | 0.020234 | -0.013849 | 0.012708 | -0.003999 | 0.011493 | 1.2314 | 1.3092 | 1.2039 | 1.2634 | 1.3779 | 1.1765 | 1.0208 | 22.2473 | 22.3572 | 22.3389 | 22.2198 | 22.1466 | 8.7799 | 8.6792 | 102.1866 | 102.0309 | -20.842 | 102.3193 | 102.2736 | 0.24262 | -20.9885 | 109.79 | 109.6893 | 0 | 123.2574 | 123.349 | 13.6597 | -0.073243 | 102.388 | 102.2415 | 102.2141 | -21.199 | 123.23 | 123.1567 | 123.3673 | -13.5406
2739.5156 | 123.5001 | -101.1017 | 22.1283 | -0.16327 | 0.014595 | -0.0014141 | 0.014744 | -0.021689 | 0.0025486 | 0.0038345 | -0.11116 | 0.01938 | -0.012781 | 0.012068 | -0.0042126 | 0.0076477 | 1.2268 | 1.3687 | 1.2222 | 1.2726 | 1.3458 | 1.1627 | 1.0025 | 22.197 | 22.3022 | 22.2656 | 22.1054 | 22.023 | 8.7845 | 8.6746 | 102.2644 | 102.1042 | -20.7825 | 102.4704 | 102.3743 | 0.27008 | -20.9015 | 109.8862 | 109.7763 | -0.022888 | 123.2986 | 123.3673 | 13.591 | -0.10529 | 102.4475 | 102.3285 | 102.3239 | -21.1258 | 123.2071 | 123.1247 | 123.4039 | -13.4537
2740.5156 | 123.5275 | -101.12 | 22.1237 | -0.064087 | 0.0086133 | 0.0041401 | 0.012394 | -0.019339 | 0.00083955 | 0.0014847 | -0.0043486 | 0.019593 | -0.013636 | 0.01164 | -0.0029308 | 0.0076477 | 1.2863 | 1.3641 | 1.2131 | 1.2909 | 1.3779 | 1.2131 | 1.0437 | 22.2153 | 22.3022 | 22.3022 | 22.11 | 22.0139 | 8.7799 | 8.6838 | 102.3331 | 102.1637 | -20.7458 | 102.4841 | 102.4109 | 0.24719 | -20.8374 | 109.8999 | 109.8038 | -0.013733 | 123.3353 | 123.4222 | 13.6185 | -0.10986 | 102.4979 | 102.4063 | 102.3331 | -21.08 | 123.23 | 123.1338 | 123.4222 | -13.4399
2741.5156 | 123.4268 | -101.1703 | 22.1008 | -0.056458 | 0.02079 | 0.0030719 | 0.018162 | -0.021689 | 0.0070346 | 0.0031937 | -0.19508 | 0.021516 | -0.0087222 | 0.013349 | -0.0033582 | 0.0089295 | 1.2817 | 1.268 | 1.1353 | 1.2497 | 1.3824 | 1.1398 | 0.97961 | 22.0871 | 22.3206 | 22.142 | 22.1649 | 22.0459 | 8.7753 | 8.6838 | 102.3102 | 102.15 | -20.7184 | 102.4384 | 102.42 | 0.27008 | -20.8191 | 109.9457 | 109.8541 | 0.064087 | 123.2574 | 123.3124 | 13.4583 | -0.054932 | 102.5528 | 102.4521 | 102.3056 | -21.1212 | 123.3353 | 123.2162 | 123.4909 | -13.4171
2742.5156 | 123.4818 | -101.1841 | 22.0184 | 0.019836 | 0.0092541 | 0.0045673 | 0.011754 | -0.02233 | -0.0023648 | 0.0023391 | 0.056686 | 0.02173 | -0.011499 | 0.010999 | -0.0025036 | 0.011066 | 1.2085 | 1.3 | 1.1856 | 1.2405 | 1.3687 | 1.1673 | 1.0117 | 22.0596 | 22.1741 | 22.1512 | 22.0322 | 21.936 | 8.7799 | 8.6838 | 102.3514 | 102.1957 | -20.6497 | 102.4841 | 102.4246 | 0.22888 | -20.8099 | 109.964 | 109.8679 | 0.013733 | 123.2437 | 123.3353 | 13.4674 | -0.082398 | 102.5528 | 102.3926 | 102.3697 | -21.0068 | 123.2162 | 123.1201 | 123.3582 | -13.3347
2743.5156 | 123.4451 | -101.2207 | 22.0184 | -0.14801 | 0.012886 | 0.0037127 | 0.013035 | -0.020621 | 0.0010532 | 0.0021255 | -0.16457 | 0.020448 | -0.012354 | 0.013349 | -0.0027172 | 0.010852 | 1.2497 | 1.3367 | 1.1948 | 1.2863 | 1.3458 | 1.1627 | 1.0025 | 22.0184 | 22.1329 | 22.0963 | 22.0322 | 21.9406 | 8.7753 | 8.6838 | 102.3834 | 102.2232 | -20.6726 | 102.5574 | 102.507 | 0.28381 | -20.7687 | 109.996 | 109.9045 | 0.013733 | 123.2391 | 123.317 | 13.4125 | -0.07782 | 102.5665 | 102.4704 | 102.4155 | -21.0159 | 123.2529 | 123.1613 | 123.3536 | -13.3347
2744.5156 | 123.4955 | -101.2939 | 21.9543 | 0.012207 | 0.0083997 | 0.0054217 | 0.01154 | -0.020194 | -0.0038602 | 0.0012711 | -0.0043486 | 0.018312 | -0.014276 | 0.010786 | -0.0018628 | 0.0093567 | 1.1902 | 1.3 | 1.181 | 1.2589 | 1.3641 | 1.1673 | 0.98877 | 21.9727 | 22.0779 | 22.0779 | 21.9223 | 21.8582 | 8.7753 | 8.6792 | 102.4612 | 102.2827 | -20.5902 | 102.594 | 102.5528 | 0.27008 | -20.7642 | 110.0693 | 109.9731 | -0.032044 | 123.2666 | 123.3719 | 13.3987 | -0.096131 | 102.6581 | 102.4841 | 102.475 | -20.9656 | 123.2162 | 123.1522 | 123.3719 | -13.2751
2745.5156 | 123.4863 | -101.3397 | 21.9086 | -0.14038 | 0.0094677 | 0.0047809 | 0.017308 | -0.019126 | 0.0042576 | 0.0010575 | -0.27138 | 0.020662 | -0.013208 | 0.011213 | -0.00058103 | 0.0089295 | 1.2405 | 1.3458 | 1.1902 | 1.2589 | 1.3275 | 1.149 | 0.98877 | 21.9681 | 22.0825 | 22.0505 | 21.9131 | 21.8124 | 8.7799 | 8.6838 | 102.4887 | 102.3285 | -20.5811 | 102.6855 | 102.5986 | 0.27008 | -20.668 | 110.1196 | 110.0235 | 0.004578 | 123.3078 | 123.3902 | 13.3667 | -0.09613 | 102.6672 | 102.5803 | 102.5299 | -20.9198 | 123.2529 | 123.1522 | 123.4222 | -13.2248
2746.5156 | 123.4497 | -101.3809 | 21.8994 | -0.13275 | 0.0096813 | 0.0049945 | 0.014317 | -0.019553 | 0.00041235 | -0.00022432 | -0.17983 | 0.020021 | -0.011927 | 0.014845 | -0.003999 | 0.0093567 | 1.2634 | 1.3458 | 1.1902 | 1.2863 | 1.3641 | 1.1673 | 0.99335 | 21.9086 | 22.0413 | 21.9818 | 21.9269 | 21.8079 | 8.7845 | 8.6792 | 102.5482 | 102.3743 | -20.5353 | 102.7267 | 102.6672 | 0.29297 | -20.636 | 110.1654 | 110.0601 | 0.027466 | 123.2895 | 123.3627 | 13.3026 | -0.091553 | 102.7451 | 102.6443 | 102.5711 | -20.9061 | 123.3078 | 123.1888 | 123.4222 | -13.2202
2747.5156 | 123.4909 | -101.4313 | 21.8216 | -0.16327 | 0.0028455 | 0.0056353 | 0.01154 | -0.020835 | 0.00062595 | 0.0016983 | -0.11116 | 0.019166 | -0.010431 | 0.011213 | -0.003999 | 0.0089295 | 1.3504 | 1.3 | 1.1948 | 1.2955 | 1.3092 | 1.149 | 0.99792 | 21.8811 | 22.0047 | 21.9589 | 21.8307 | 21.7255 | 8.7799 | 8.6746 | 102.5803 | 102.4292 | -20.5124 | 102.7313 | 102.7267 | 0.29755 | -20.4712 | 110.2112 | 110.1059 | 0.009156 | 123.3124 | 123.3902 | 13.2843 | -0.09613 | 102.7405 | 102.7817 | 102.626 | -20.8237 | 123.262 | 123.1567 | 123.436 | -13.147
2748.5156 | 123.468 | -101.4313 | 21.817 | -0.19379 | 0.012245 | 0.0028583 | 0.013676 | -0.019126 | 0.00041235 | 0.00020288 | -0.1722 | 0.018739 | -0.011286 | 0.012068 | -0.0012218 | 0.0082885 | 1.2405 | 1.3367 | 1.1856 | 1.2634 | 1.3824 | 1.1627 | 0.97961 | 21.8124 | 21.9315 | 21.8903 | 21.8079 | 21.7529 | 8.7753 | 8.6746 | 102.594 | 102.4109 | -20.4346 | 102.7679 | 102.6947 | 0.28381 | -20.5765 | 110.2066 | 110.1059 | -0.009156 | 123.2437 | 123.3215 | 13.2156 | -0.064087 | 102.8137 | 102.6718 | 102.6169 | -20.8374 | 123.2391 | 123.1842 | 123.3627 | -13.1424
2749.5156 | 123.4589 | -101.4954 | 21.7712 | -0.15564 | 0.014168 | 0.0037127 | 0.011967 | -0.016776 | -1.505e-05 | 0.0012711 | -0.18745 | 0.020021 | -0.011713 | 0.011854 | -0.0018628 | 0.0093567 | 1.2314 | 1.3412 | 1.2039 | 1.2589 | 1.3596 | 1.1673 | 0.97961 | 21.7758 | 21.8857 | 21.8491 | 21.7896 | 21.6797 | 8.7753 | 8.6838 | 102.6627 | 102.475 | -20.4117 | 102.8366 | 102.7542 | 0.27924 | -20.5399 | 110.2707 | 110.1791 | 0.018311 | 123.2712 | 123.3444 | 13.1653 | -0.091553 | 102.8549 | 102.7267 | 102.6993 | -20.7916 | 123.2849 | 123.175 | 123.381 | -13.0875
2750.5156 | 123.5046 | -101.5045 | 21.6843 | -0.010681 | 0.0090405 | 0.0052081 | 0.013249 | -0.020621 | -0.0017238 | -0.00043792 | 0.049057 | 0.019593 | -0.011286 | 0.010572 | -0.0020764 | 0.011493 | 1.2405 | 1.3596 | 1.2177 | 1.2726 | 1.3779 | 1.1673 | 1.0208 | 21.785 | 21.8903 | 21.8582 | 21.698 | 21.6156 | 8.7845 | 8.6838 | 102.6718 | 102.5253 | -20.3064 | 102.8641 | 102.7771 | 0.25177 | -20.4437 | 110.289 | 110.1883 | 0.013733 | 123.2895 | 123.3627 | 13.1744 | -0.068664 | 102.8824 | 102.7451 | 102.7222 | -20.6635 | 123.2025 | 123.1201 | 123.3948 | -13.0005
2751.5156 | 123.4451 | -101.7746 | 21.492 | 0.2182 | 0.019081 | 0.0037127 | 0.017308 | -0.01763 | 0.0048984 | 0.0053299 | 0.17113 | 0.020875 | -0.011072 | 0.011854 | -0.0018628 | 0.0076477 | 1.1719 | 1.1856 | 1.0849 | 1.1765 | 1.3641 | 1.1307 | 0.95673 | 21.5195 | 21.5286 | 21.5332 | 21.5195 | 21.4279 | 8.7799 | 8.6792 | 102.9053 | 102.7313 | -20.1279 | 102.9602 | 102.951 | 0.21973 | -20.3201 | 110.5545 | 110.4538 | 0.027466 | 123.2941 | 123.3078 | 12.854 | -0.064087 | 103.1387 | 102.9465 | 102.8595 | -20.5353 | 123.2941 | 123.2025 | 123.3032 | -12.8128
2752.5156 | 123.381 | -101.8158 | 21.5012 | -0.18616 | 0.011177 | 0.0039263 | 0.012394 | -0.018057 | 0.0010532 | 0.00063028 | -0.15694 | 0.022584 | -0.012354 | 0.011213 | -0.0033582 | 0.012347 | 1.181 | 1.2589 | 1.1215 | 1.2177 | 1.3779 | 1.1261 | 0.9613 | 21.4325 | 21.5195 | 21.492 | 21.5149 | 21.4462 | 8.7799 | 8.6838 | 102.9419 | 102.7771 | -20.1233 | 103.0746 | 103.0334 | 0.25635 | -20.3201 | 110.5957 | 110.4996 | 0.013733 | 123.2483 | 123.3078 | 12.8082 | -0.054932 | 103.1937 | 102.9968 | 102.9373 | -20.5399 | 123.3307 | 123.262 | 123.3353 | -12.8174
2753.5156 | 123.4039 | -101.7105 | 21.5973 | -0.19379 | 0.012031 | 0.0030719 | 0.013463 | -0.017203 | -1.505e-05 | -0.00086512 | -0.20271 | 0.020021 | -0.011713 | 0.012068 | -0.0027172 | 0.0078613 | 1.1993 | 1.2817 | 1.1398 | 1.2268 | 1.3824 | 1.1215 | 0.97046 | 21.5698 | 21.6751 | 21.611 | 21.6019 | 21.5378 | 8.7799 | 8.6792 | 102.832 | 102.681 | -20.2148 | 102.9922 | 102.9373 | 0.25635 | -20.3979 | 110.4904 | 110.3897 | 0.004578 | 123.2803 | 123.3215 | 12.9318 | -0.059509 | 103.093 | 102.9099 | 102.8503 | -20.6268 | 123.3124 | 123.2483 | 123.3856 | -12.9181
2754.5156 | 123.5184 | -101.6922 | 21.5149 | -0.079346 | 0.0088269 | 0.0062763 | 0.010685 | -0.018485 | -0.0038602 | 0.0012711 | -0.11879 | 0.018739 | -0.012995 | 0.0060862 | -0.0063488 | 0.010425 | 1.2451 | 1.3779 | 1.2131 | 1.2726 | 1.3367 | 1.149 | 0.97504 | 21.6522 | 21.3318 | 21.7072 | 21.5057 | 21.4279 | 8.7799 | 8.6838 | 102.8412 | 102.6672 | -20.1782 | 103.0701 | 102.9648 | 0.29755 | -20.2698 | 110.4721 | 110.376 | -0.009156 | 123.3444 | 123.3994 | 13.0234 | -0.086976 | 103.0289 | 102.9373 | 102.9053 | -20.5399 | 123.1979 | 123.1201 | 123.024 | -12.8311
2755.5156 | 123.3902 | -101.7609 | 21.5378 | -0.20905 | 0.012886 | 0.0034991 | 0.013676 | -0.018698 | 0.00083955 | -0.00022432 | -0.17983 | 0.022584 | -0.01449 | 0.011213 | -0.0027172 | 0.0085021 | 1.2131 | 1.2817 | 1.1719 | 1.2314 | 1.3596 | 1.1398 | 0.97961 | 21.4874 | 21.5927 | 21.5698 | 21.524 | 21.4462 | 8.7708 | 8.6746 | 102.9007 | 102.7405 | -20.1782 | 103.0426 | 102.9922 | 0.25177 | -20.3247 | 110.5316 | 110.4355 | -0.013733 | 123.2483 | 123.3307 | 12.8952 | -0.091553 | 103.1204 | 102.9739 | 102.9327 | -20.5582 | 123.2849 | 123.2071 | 123.3536 | -12.8632
2756.5156 | 123.4085 | -102.0035 | 21.3226 | -0.14038 | 0.013954 | 0.0017901 | 0.014531 | -0.017844 | 0.0036166 | 0.0014847 | -0.21797 | 0.021302 | -0.0087222 | 0.011854 | -0.0042126 | 0.0089295 | 1.1353 | 1.1902 | 1.0391 | 1.1856 | 1.3779 | 1.0895 | 0.93384 | 21.2311 | 21.3455 | 21.2906 | 21.3547 | 21.2402 | 8.7753 | 8.6746 | 103.093 | 102.9373 | -19.9448 | 103.1937 | 103.1891 | 0.25177 | -20.1874 | 110.7788 | 110.6781 | 0.032043 | 123.2346 | 123.2941 | 12.616 | -0.082398 | 103.3813 | 103.1387 | 103.0426 | -20.3888 | 123.3582 | 123.2437 | 123.349 | -12.648
2757.5312 | 123.3719 | -101.9577 | 21.3638 | 0.12665 | 0.022072 | -0.00055971 | 0.01389 | -0.019339 | 0.004044 | 0.0051163 | 0.41527 | 0.020662 | -0.011072 | 0.013777 | -0.00058103 | 0.0089295 | 0.94299 | 1.4145 | 1.2039 | 1.2222 | 1.3687 | 1.1398 | 0.97046 | 21.2677 | 21.3318 | 21.3089 | 21.3455 | 21.2769 | 8.7708 | 8.67 | 103.0975 | 102.9282 | -19.9951 | 103.3722 | 103.1799 | 0.25177 | -20.4208 | 110.7285 | 110.6277 | -0.018311 | 123.2254 | 123.2666 | 12.6389 | -0.086976 | 103.3264 | 102.9007 | 103.1616 | -20.3934 | 123.3032 | 123.2346 | 123.2895 | -12.6938
2758.5156 | 123.5321 | -101.8845 | 21.3547 | -0.010681 | 0.0064771 | 0.0026447 | 0.012608 | -0.020194 | -0.0042874 | 0.0029801 | 0.018539 | 0.020021 | -0.012995 | 0.012922 | -0.0046398 | 0.011707 | 1.2405 | 1.3596 | 1.2131 | 1.2543 | 1.3367 | 1.1581 | 0.98419 | 21.4188 | 21.5515 | 21.524 | 21.3501 | 21.2906 | 8.7753 | 8.6792 | 103.0426 | 102.8687 | -20.018 | 103.244 | 103.1387 | 0.27008 | -20.1141 | 110.6598 | 110.5637 | -0.004577 | 123.3032 | 123.4085 | 12.8448 | -0.064087 | 103.2211 | 103.125 | 103.0975 | -20.3705 | 123.2346 | 123.175 | 123.436 | -12.6755
2759.5156 | 123.3398 | -101.9257 | 21.373 | -0.20142 | 0.014168 | 0.00050849 | 0.014531 | -0.016135 | 0.0019078 | 0.0014847 | -0.14931 | 0.021516 | -0.010431 | 0.010999 | -0.0037854 | 0.0093567 | 1.149 | 1.2131 | 1.0941 | 1.1948 | 1.3687 | 1.1215 | 0.94757 | 21.2677 | 21.3593 | 21.3364 | 21.373 | 21.286 | 8.7845 | 8.6792 | 103.0472 | 102.8732 | -20.0043 | 103.1387 | 103.1204 | 0.24719 | -20.224 | 110.7101 | 110.6049 | 0 | 123.1934 | 123.262 | 12.6572 | -0.086975 | 103.2944 | 103.0746 | 103.0197 | -20.4254 | 123.2986 | 123.2117 | 123.2849 | -12.6938
2760.5156 | 123.5046 | -101.9394 | 21.2723 | -0.15564 | 0.010963 | 0.0041401 | 0.013676 | -0.018912 | -0.0081326 | 0.0025529 | 0.17113 | 0.020234 | -0.012781 | 0.010786 | -0.0033582 | 0.0076477 | 1.3596 | 1.1261 | 1.1581 | 1.2726 | 1.3092 | 1.1353 | 0.95673 | 21.3272 | 21.4691 | 21.4279 | 21.2814 | 21.2219 | 8.7799 | 8.6746 | 103.0746 | 102.8961 | -19.9631 | 103.0655 | 103.212 | 0.31586 | -19.9127 | 110.7193 | 110.614 | 0.009155 | 123.2666 | 123.3673 | 12.7533 | -0.050354 | 103.2486 | 103.299 | 103.0975 | -20.3156 | 123.2208 | 123.1613 | 123.4085 | -12.5977
2761.5156 | 123.4268 | -102.063 | 21.2082 | 0.080872 | 0.020149 | 0.00093569 | 0.016026 | -0.018485 | 0.005112 | 0.0042619 | -0.073013 | 0.021943 | -0.0072268 | 0.013349 | -0.0012218 | 0.0061523 | 1.2085 | 1.2222 | 1.1078 | 1.1993 | 1.3687 | 1.1078 | 0.94299 | 21.2036 | 21.2814 | 21.2219 | 21.2357 | 21.1441 | 8.7753 | 8.6746 | 103.1708 | 103.006 | -19.8395 | 103.2852 | 103.2623 | 0.25635 | -19.9997 | 110.8383 | 110.7376 | 0.027466 | 123.2666 | 123.2849 | 12.5473 | -0.064087 | 103.4317 | 103.2715 | 103.1708 | -20.2652 | 123.2986 | 123.2071 | 123.3444 | -12.5336
2762.5156 | 123.4085 | -102.1133 | 21.199 | -0.18616 | 0.014168 | 0.0037127 | 0.015599 | -0.018912 | 0.003403 | 0.0019119 | -0.17983 | 0.022798 | -0.011286 | 0.01399 | -0.0016492 | 0.0091431 | 1.1261 | 1.1765 | 1.062 | 1.1719 | 1.3641 | 1.0986 | 0.92468 | 21.1258 | 21.2311 | 21.1899 | 21.2219 | 21.1166 | 8.7753 | 8.6746 | 103.212 | 103.038 | -19.8349 | 103.2898 | 103.2852 | 0.24719 | -20.0729 | 110.8887 | 110.788 | 0.022888 | 123.2391 | 123.3032 | 12.5153 | -0.082398 | 103.4775 | 103.2394 | 103.1754 | -20.2744 | 123.3353 | 123.23 | 123.3444 | -12.5244
2763.5156 | 123.4039 | -102.15 | 21.1624 | -0.2243 | 0.013099 | 0.0022175 | 0.015172 | -0.018912 | 0.00019875 | 0.0036209 | -0.073013 | 0.020875 | -0.011713 | 0.012068 | -0.0027172 | 0.0095703 | 0.98877 | 1.2085 | 1.0849 | 1.1627 | 1.4099 | 1.1353 | 0.95215 | 21.048 | 21.1716 | 21.1304 | 21.1395 | 21.0617 | 8.7799 | 8.67 | 103.2852 | 103.1021 | -19.7525 | 103.3585 | 103.3127 | 0.21057 | -20.1736 | 110.9299 | 110.82 | -0.022889 | 123.1979 | 123.2803 | 12.4603 | -0.10071 | 103.5599 | 103.1387 | 103.2349 | -20.2103 | 123.2895 | 123.2117 | 123.3215 | -12.4924
2764.5156 | 123.4039 | -102.2003 | 21.1258 | -0.19379 | 0.01075 | 0.0037127 | 0.010685 | -0.018912 | -0.0019376 | 0.0010575 | -0.14168 | 0.020234 | -0.0095768 | 0.01399 | -0.0029308 | 0.0099975 | 1.1536 | 1.2589 | 1.1169 | 1.2314 | 1.3504 | 1.1169 | 0.95673 | 21.0342 | 21.167 | 21.1258 | 21.1441 | 21.0342 | 8.7799 | 8.6838 | 103.3173 | 103.157 | -19.7754 | 103.4592 | 103.4317 | 0.27466 | -19.9722 | 110.9802 | 110.8841 | 0.018311 | 123.2346 | 123.3261 | 12.442 | -0.091552 | 103.5507 | 103.3539 | 103.3173 | -20.1691 | 123.3444 | 123.2346 | 123.3673 | -12.442
2765.5156 | 123.3719 | -102.2644 | 21.0617 | -0.21667 | 0.014168 | 0.0058491 | 0.015172 | -0.020194 | -1.505e-05 | 0.00041648 | -0.095902 | 0.01938 | -0.011286 | 0.013349 | -0.0044262 | 0.0087157 | 1.1536 | 1.236 | 1.1169 | 1.1993 | 1.355 | 1.1215 | 0.95215 | 20.9839 | 21.0663 | 21.048 | 21.0938 | 20.9839 | 8.7753 | 8.6792 | 103.3859 | 103.2166 | -19.7067 | 103.5004 | 103.4637 | 0.24719 | -19.9081 | 111.0397 | 110.9436 | 0.032043 | 123.2483 | 123.3124 | 12.3688 | -0.07782 | 103.6194 | 103.418 | 103.3813 | -20.1096 | 123.3582 | 123.2483 | 123.3307 | -12.3825
2766.5156 | 123.4131 | -102.2919 | 21.0159 | -0.23956 | 0.019081 | 8.1086e-05 | 0.013249 | -0.019553 | 0.005753 | 0.0036209 | -0.073013 | 0.023866 | -0.0078678 | 0.013777 | -0.0016492 | 0.0059387 | 1.1856 | 1.236 | 1.0895 | 1.1856 | 1.3687 | 1.1078 | 0.95215 | 20.9793 | 21.048 | 21.0159 | 21.0068 | 20.9335 | 8.7799 | 8.6746 | 103.3997 | 103.244 | -19.6472 | 103.5278 | 103.4775 | 0.23346 | -19.8303 | 111.0718 | 110.9665 | -0.009155 | 123.2712 | 123.3078 | 12.3413 | -0.082397 | 103.6606 | 103.4775 | 103.3813 | -20.0638 | 123.2986 | 123.2254 | 123.3398 | -12.3413
2767.5312 | 123.4909 | -102.3422 | 20.8649 | 0.19531 | 0.017586 | 0.0013629 | 0.012822 | -0.018057 | -1.505e-05 | 0.0040481 | -0.91225 | 0.022157 | -0.010004 | 0.012068 | -0.0027172 | 0.0085021 | 1.1993 | 1.2772 | 1.1581 | 1.236 | 1.3138 | 1.1444 | 0.95215 | 20.9518 | 20.9976 | 21.0159 | 20.8786 | 20.8191 | 8.7753 | 8.67 | 103.4866 | 103.2944 | -19.5511 | 103.6194 | 103.5782 | 0.28381 | -19.6655 | 111.1176 | 111.0123 | 0.013733 | 123.2941 | 123.3582 | 12.3459 | -0.045776 | 103.656 | 103.5416 | 103.5004 | -19.9127 | 123.2208 | 123.1613 | 123.3398 | -12.1948
2768.5156 | 123.3856 | -102.388 | 20.8969 | -0.17853 | 0.012245 | 0.0039263 | 0.015172 | -0.020194 | -0.0036464 | 0.0016983 | -0.21034 | 0.021089 | -0.015345 | 0.013136 | -0.0035718 | 0.0082885 | 1.1398 | 1.2131 | 1.0941 | 1.1719 | 1.3504 | 1.1169 | 0.95215 | 20.8099 | 20.9427 | 20.9106 | 20.9335 | 20.8694 | 8.7753 | 8.6838 | 103.5049 | 103.3401 | -19.5465 | 103.6011 | 103.5599 | 0.21973 | -19.7571 | 111.1633 | 111.0718 | 0.036621 | 123.1979 | 123.2986 | 12.2269 | -0.027466 | 103.7384 | 103.5278 | 103.4821 | -19.9448 | 123.3215 | 123.2574 | 123.3307 | -12.2131
2769.5156 | 123.3673 | -102.4063 | 20.8969 | 0.79803 | 0.017158 | 0.0039263 | 0.014103 | -0.019126 | 0.00083955 | 0.0021255 | -0.17983 | 0.021302 | -0.0091494 | 0.01164 | -0.0016492 | 0.0093567 | 1.1078 | 1.1536 | 1.0437 | 1.1581 | 1.387 | 1.1307 | 0.94299 | 20.8099 | 20.9106 | 20.874 | 20.9244 | 20.8466 | 8.7753 | 8.6838 | 103.537 | 103.3493 | -19.5099 | 103.5599 | 103.5645 | 0.21515 | -19.7891 | 111.1816 | 111.0901 | 0.027465 | 123.2162 | 123.2803 | 12.1902 | -0.050354 | 103.7933 | 103.5141 | 103.45 | -19.9539 | 123.3307 | 123.2529 | 123.317 | -12.2131
2770.5156 | 123.4589 | -102.4338 | 20.8466 | -0.16327 | 0.01374 | 0.0062763 | 0.010899 | -0.020407 | -0.0032192 | 0.0021255 | -0.14168 | 0.018098 | -0.011927 | 0.012281 | -0.0020764 | 0.010425 | 1.1856 | 1.2955 | 1.1581 | 1.236 | 1.3321 | 1.1215 | 0.96588 | 20.8374 | 20.9427 | 20.9152 | 20.8374 | 20.7687 | 8.7799 | 8.6838 | 103.5553 | 103.3997 | -19.5145 | 103.7292 | 103.6697 | 0.27008 | -19.661 | 111.2137 | 111.1176 | -0.009156 | 123.2712 | 123.349 | 12.2314 | -0.07782 | 103.7659 | 103.6194 | 103.5919 | -19.8807 | 123.2712 | 123.2025 | 123.3765 | -12.1628
2771.5156 | 123.3719 | -102.5253 | 20.7687 | 0.050354 | 0.020149 | 0.0011493 | 0.016453 | -0.017417 | 0.0059666 | 0.0023391 | 0.0032804 | 0.02472 | -0.0087222 | 0.011854 | -0.00058103 | 0.0085021 | 1.1261 | 1.1398 | 1.0254 | 1.149 | 1.3229 | 1.0757 | 0.9201 | 20.6818 | 20.755 | 20.7184 | 20.8099 | 20.7138 | 8.7753 | 8.6746 | 103.6011 | 103.4454 | -19.4458 | 103.6652 | 103.6743 | 0.22888 | -19.6426 | 111.3007 | 111.2 | 0.041199 | 123.2071 | 123.2437 | 12.0438 | -0.054932 | 103.8483 | 103.6514 | 103.5507 | -19.8486 | 123.3353 | 123.2391 | 123.2803 | -12.0941
2772.5156 | 123.4268 | -102.562 | 20.6955 | 0.21057 | 0.017158 | 0.0022175 | 0.014531 | -0.019553 | 0.00083955 | 0.0042619 | 0.19402 | 0.02173 | -0.0080814 | 0.012068 | -0.0031446 | 0.0097839 | 1.1169 | 1.1353 | 1.0483 | 1.1444 | 1.3458 | 1.0895 | 0.92468 | 20.6726 | 20.7092 | 20.7047 | 20.6955 | 20.6451 | 8.7708 | 8.6792 | 103.6514 | 103.4866 | -19.3497 | 103.6972 | 103.7064 | 0.21973 | -19.5786 | 111.3327 | 111.2411 | 0 | 123.2346 | 123.2666 | 12.0255 | -0.050354 | 103.9078 | 103.6789 | 103.6102 | -19.7708 | 123.2574 | 123.2071 | 123.2712 | -12.0163
2773.5156 | 123.4085 | -102.6123 | 20.6726 | -0.018311 | 0.01844 | 0.0034991 | 0.015812 | -0.017203 | 0.005753 | 0.00063028 | 0.018539 | 0.023652 | -0.0085086 | 0.013349 | 0.00027337 | 0.0078613 | 1.1719 | 1.1902 | 1.0666 | 1.1627 | 1.3229 | 1.0712 | 0.91095 | 20.6268 | 20.6909 | 20.6497 | 20.7001 | 20.6314 | 8.7708 | 8.6746 | 103.6835 | 103.5233 | -19.3497 | 103.8025 | 103.775 | 0.25177 | -19.5007 | 111.3831 | 111.2869 | 0.027466 | 123.2391 | 123.262 | 11.9751 | -0.041198 | 103.9352 | 103.7842 | 103.6789 | -19.7617 | 123.3124 | 123.2437 | 123.3032 | -11.998
2774.5156 | 123.4222 | -102.6672 | 20.6635 | -0.20142 | 0.0096813 | 0.0030719 | 0.011326 | -0.018698 | -0.0032192 | -0.0030013 | -0.14168 | 0.020662 | -0.011072 | 0.011854 | -0.0048534 | 0.011707 | 1.1536 | 1.236 | 1.1307 | 1.2085 | 1.3229 | 1.1124 | 0.95673 | 20.5994 | 20.7459 | 20.7047 | 20.6635 | 20.5994 | 8.7845 | 8.6838 | 103.7796 | 103.624 | -19.3405 | 103.9032 | 103.8757 | 0.25177 | -19.5099 | 111.4517 | 111.351 | 0 | 123.2666 | 123.3719 | 12.0209 | -0.064087 | 103.9902 | 103.8208 | 103.7979 | -19.7067 | 123.3307 | 123.2666 | 123.4131 | -11.9797
2775.5156 | 123.4314 | -102.6581 | 20.636 | -0.16327 | 0.015663 | 0.0011493 | 0.013035 | -0.019766 | 0.0036166 | 0.0029801 | -0.20271 | 0.02173 | -0.0095768 | 0.012495 | -0.0018628 | 0.0055115 | 1.1353 | 1.181 | 1.062 | 1.181 | 1.3321 | 1.0712 | 0.91553 | 20.5856 | 20.6863 | 20.6406 | 20.636 | 20.5673 | 8.7799 | 8.6838 | 103.7292 | 103.5736 | -19.3039 | 103.8391 | 103.8391 | 0.2655 | -19.5007 | 111.438 | 111.3419 | 0 | 123.2437 | 123.2986 | 11.9568 | -0.068664 | 103.9902 | 103.7933 | 103.7201 | -19.7205 | 123.2941 | 123.2254 | 123.3444 | -11.9522
2776.5156 | 123.4589 | -102.7725 | 20.517 | 0.21057 | 0.017158 | 0.0028583 | 0.012822 | -0.018057 | 0.0029758 | 0.0031937 | 0.2169 | 0.01938 | -0.0095768 | 0.013136 | -0.0031446 | 0.0091431 | 1.1169 | 1.1581 | 1.0483 | 1.149 | 1.3275 | 1.0803 | 0.93384 | 20.4941 | 20.5536 | 20.5536 | 20.5124 | 20.4391 | 8.7708 | 8.67 | 103.8528 | 103.7064 | -19.1895 | 103.9307 | 103.9215 | 0.21515 | -19.4 | 111.5433 | 111.4426 | -0.004578 | 123.2666 | 123.3261 | 11.8835 | -0.07782 | 104.1 | 103.8895 | 103.8208 | -19.5831 | 123.2849 | 123.2117 | 123.3261 | -11.8469
2777.5156 | 123.436 | -102.7817 | 20.5399 | -0.14801 | 0.015449 | 0.0028583 | 0.014317 | -0.019339 | -0.00065585 | 0.0010575 | -0.14168 | 0.021943 | -0.009363 | 0.01399 | -0.00058103 | 0.0093567 | 1.1398 | 1.1856 | 1.0666 | 1.1765 | 1.3229 | 1.0986 | 0.89264 | 20.4941 | 20.5673 | 20.5353 | 20.5627 | 20.4575 | 8.7799 | 8.6792 | 103.8803 | 103.6743 | -19.2169 | 103.9673 | 103.9581 | 0.28381 | -19.4 | 111.5616 | 111.4609 | 0.022888 | 123.2758 | 123.317 | 11.8561 | -0.082398 | 104.1046 | 103.9215 | 103.8483 | -19.6472 | 123.3444 | 123.2391 | 123.349 | -11.8607
2778.5156 | 123.381 | -102.8275 | 20.4987 | -0.23193 | 0.013954 | 0.0073443 | 0.012394 | -0.020407 | 0.00041235 | 0.00063028 | -0.21034 | 0.023225 | -0.012567 | 0.010999 | -0.003999 | 0.0097839 | 1.149 | 1.1124 | 1.0345 | 1.149 | 1.3779 | 1.1078 | 0.9201 | 20.3705 | 20.4941 | 20.462 | 20.4941 | 20.4575 | 8.7753 | 8.6746 | 103.9352 | 103.7476 | -19.1208 | 103.9398 | 103.9764 | 0.22888 | -19.3497 | 111.6028 | 111.5021 | -0.004577 | 123.1979 | 123.2895 | 11.7874 | -0.041199 | 104.2053 | 103.9764 | 103.862 | -19.5786 | 123.3215 | 123.2849 | 123.3215 | -11.824
2779.5156 | 123.4222 | -102.8183 | 20.4666 | -0.13275 | 0.018654 | -0.00077331 | 0.014744 | -0.020407 | 0.0014804 | 0.00084388 | -0.042496 | 0.022157 | -0.010431 | 0.012708 | -0.00079463 | 0.0099975 | 1.1627 | 1.1765 | 1.062 | 1.1765 | 1.3321 | 1.0941 | 0.91095 | 20.3979 | 20.4941 | 20.4346 | 20.4346 | 20.3934 | 8.7845 | 8.67 | 103.9124 | 103.7292 | -19.1345 | 103.9948 | 103.9948 | 0.2655 | -19.3039 | 111.6028 | 111.4883 | -0.032044 | 123.2162 | 123.2529 | 11.7645 | -0.073242 | 104.1504 | 103.981 | 103.8803 | -19.5557 | 123.2529 | 123.2117 | 123.3124 | -11.7966
2780.5156 | 123.4314 | -102.9053 | 20.4025 | -0.14801 | 0.016517 | 0.0030719 | 0.013463 | -0.018057 | 0.0012668 | 0.00020288 | -0.12642 | 0.020234 | -0.012354 | 0.012068 | -0.00229 | 0.0076477 | 1.1124 | 1.1581 | 1.0345 | 1.1536 | 1.3367 | 1.0803 | 0.91095 | 20.3156 | 20.4483 | 20.3979 | 20.4254 | 20.343 | 8.7845 | 8.67 | 103.9856 | 103.8162 | -19.0659 | 104.0634 | 104.0588 | 0.24261 | -19.2902 | 111.6898 | 111.5753 | 0.022888 | 123.2208 | 123.3032 | 11.7279 | -0.059509 | 104.2419 | 104.0176 | 103.9398 | -19.4916 | 123.3307 | 123.2483 | 123.3536 | -11.7325
2781.5312 | 123.5458 | -102.9877 | 20.3064 | 0.15717 | 0.011604 | 0.0032855 | 0.012181 | -0.020835 | -0.0053554 | -0.00086512 | 0.26268 | 0.019166 | -0.014063 | 0.013136 | -0.0037854 | 0.013843 | 1.1215 | 1.1902 | 1.0941 | 1.1719 | 1.3046 | 1.1215 | 0.95215 | 20.311 | 20.4208 | 20.4208 | 20.3201 | 20.256 | 8.7753 | 8.6838 | 104.1092 | 103.9398 | -19.0018 | 104.1779 | 104.1595 | 0.21973 | -19.1849 | 111.763 | 111.6714 | 0.013733 | 123.2986 | 123.4085 | 11.7371 | -0.050354 | 104.2923 | 104.1092 | 104.0817 | -19.3542 | 123.3078 | 123.2437 | 123.4085 | -11.6226
2782.5156 | 123.4177 | -102.9877 | 20.311 | -0.15564 | 0.018867 | 0.0024311 | 0.014103 | -0.015708 | 0.001694 | 0.0021255 | -0.16457 | 0.021302 | -0.010858 | 0.011854 | -0.00079463 | 0.0091431 | 1.1124 | 1.1353 | 1.0345 | 1.1444 | 1.3229 | 1.0666 | 0.89722 | 20.2652 | 20.3568 | 20.3018 | 20.3384 | 20.2652 | 8.7708 | 8.67 | 104.0543 | 103.8849 | -18.988 | 104.1229 | 104.1321 | 0.24719 | -19.1986 | 111.7584 | 111.6577 | 0.027466 | 123.2529 | 123.2895 | 11.6318 | -0.045776 | 104.3106 | 104.1 | 104.0222 | -19.4138 | 123.3261 | 123.2529 | 123.3444 | -11.6409
2783.5156 | 123.3994 | -103.0563 | 20.256 | 0.0045777 | 0.019295 | 0.0022175 | 0.017308 | -0.018485 | 0.0046848 | 0.0019119 | 0.0032804 | 0.023439 | -0.0078678 | 0.010572 | -0.00229 | 0.0093567 | 1.1627 | 1.1536 | 1.0483 | 1.1581 | 1.3138 | 1.0803 | 0.89264 | 20.2011 | 20.2698 | 20.224 | 20.2698 | 20.2332 | 8.7753 | 8.6792 | 104.1367 | 103.949 | -18.9423 | 104.2099 | 104.2145 | 0.2655 | -19.0933 | 111.8317 | 111.7355 | 0.013733 | 123.2574 | 123.2803 | 11.5448 | -0.022888 | 104.3701 | 104.2191 | 104.1046 | -19.3634 | 123.3261 | 123.2895 | 123.3261 | -11.5768
2784.5156 | 123.4268 | -103.0563 | 20.2148 | -0.071716 | 0.018013 | -0.00055971 | 0.013463 | -0.020194 | 0.005753 | -0.00086512 | -0.14168 | 0.022584 | -0.011499 | 0.012495 | 0.00048697 | 0.0091431 | 1.2772 | 1.1673 | 1.0757 | 1.1948 | 1.3824 | 1.1398 | 0.97046 | 20.192 | 20.2744 | 20.2194 | 20.2286 | 20.1874 | 8.7845 | 8.6746 | 104.1962 | 104.0268 | -18.8324 | 104.2236 | 104.2511 | 0.2243 | -18.9377 | 111.8408 | 111.731 | 0.013733 | 123.2483 | 123.2758 | 11.5448 | -0.027466 | 104.4388 | 104.3335 | 104.1321 | -19.2444 | 123.2849 | 123.2437 | 123.3307 | -11.5402
2785.5156 | 123.3902 | -103.1525 | 20.137 | 0.0045777 | 0.017799 | 0.0034991 | 0.012822 | -0.018271 | 0.003403 | 0.0029801 | 0.11772 | 0.022798 | -0.0080814 | 0.012281 | -0.0014356 | 0.0099975 | 1.1307 | 1.1261 | 1.0345 | 1.149 | 1.3 | 1.0529 | 0.89722 | 20.0684 | 20.1462 | 20.1279 | 20.1645 | 20.1141 | 8.7753 | 8.6746 | 104.2053 | 104.0497 | -18.837 | 104.2786 | 104.3015 | 0.25177 | -19.0063 | 111.9278 | 111.8271 | 0.027466 | 123.2208 | 123.2803 | 11.4532 | -0.022888 | 104.4525 | 104.2831 | 104.187 | -19.2398 | 123.317 | 123.2666 | 123.2986 | -11.4624
2786.5156 | 123.4634 | -103.157 | 20.105 | 0.20294 | 0.01844 | 0.0024311 | 0.013035 | -0.01998 | -0.001083 | 0.00041648 | 0.23216 | 0.020875 | -0.0087222 | 0.011427 | -0.0025036 | 0.010638 | 1.1124 | 1.1398 | 1.0574 | 1.1353 | 1.2955 | 1.0574 | 0.9201 | 20.0867 | 20.1599 | 20.1599 | 20.1233 | 20.0592 | 8.7708 | 8.67 | 104.2145 | 104.0771 | -18.8095 | 104.2969 | 104.2923 | 0.21515 | -18.9926 | 111.9278 | 111.8271 | 0.018311 | 123.2437 | 123.317 | 11.4899 | -0.045776 | 104.4525 | 104.2694 | 104.2145 | -19.1849 | 123.2803 | 123.2162 | 123.317 | -11.4349
2787.5156 | 123.4177 | -103.2074 | 20.1004 | 0.19531 | 0.018226 | 0.0032855 | 0.01389 | -0.01998 | 0.00062595 | 0.00063028 | 0.17113 | 0.02173 | -0.008295 | 0.012281 | -0.0029308 | 0.0093567 | 1.1078 | 1.0941 | 1.0025 | 1.1124 | 1.3275 | 1.0574 | 0.89264 | 20.018 | 20.0592 | 20.0775 | 20.1004 | 20.0592 | 8.7799 | 8.6746 | 104.2648 | 104.1 | -18.7729 | 104.3015 | 104.3198 | 0.21973 | -18.9926 | 111.9873 | 111.882 | 0 | 123.2254 | 123.2849 | 11.4029 | -0.041199 | 104.5349 | 104.3152 | 104.2099 | -19.2078 | 123.3078 | 123.2666 | 123.2666 | -11.4258
2788.5156 | 123.3994 | -103.2898 | 20.0272 | -0.041199 | 0.019081 | 0.0034991 | 0.013463 | -0.01998 | 0.002335 | 0.0010575 | -0.034867 | 0.023225 | -0.010645 | 0.014204 | -0.0018628 | 0.0085021 | 1.149 | 1.1627 | 1.0437 | 1.1536 | 1.3184 | 1.0666 | 0.89264 | 19.9677 | 20.0455 | 20.0043 | 20.0088 | 19.9631 | 8.7753 | 8.6746 | 104.3564 | 104.1824 | -18.7088 | 104.4525 | 104.4434 | 0.26093 | -18.8782 | 112.0651 | 111.9644 | -0.018311 | 123.2574 | 123.2941 | 11.3297 | -0.064087 | 104.6082 | 104.4388 | 104.3335 | -19.1345 | 123.2986 | 123.2529 | 123.3353 | -11.3525
2789.5156 | 123.4222 | -103.2532 | 20.018 | 0.18768 | 0.017158 | 0.0037127 | 0.012181 | -0.018912 | 0.00062595 | 0.0025529 | 0.2169 | 0.020875 | -0.010858 | 0.013136 | -0.0027172 | 0.010852 | 1.0849 | 1.1078 | 1.0025 | 1.1169 | 1.3046 | 1.062 | 0.88806 | 19.9631 | 20.0272 | 20.018 | 20.0546 | 19.9677 | 8.7753 | 8.6655 | 104.3152 | 104.1412 | -18.7134 | 104.361 | 104.3701 | 0.22888 | -18.9331 | 112.0285 | 111.9186 | 0.036621 | 123.2162 | 123.2712 | 11.3525 | -0.050354 | 104.5578 | 104.3381 | 104.2557 | -19.1299 | 123.3078 | 123.2208 | 123.2803 | -11.3525
2790.5156 | 123.381 | -103.2898 | 20.0317 | 0.012207 | 0.017586 | 0.0022175 | 0.017735 | -0.018485 | 0.003403 | 0.0019119 | 0.079574 | 0.02173 | -0.0095768 | 0.012495 | -0.0033582 | 0.0087157 | 1.1353 | 1.1307 | 1.0162 | 1.1398 | 1.3092 | 1.062 | 0.88806 | 19.9265 | 20.0088 | 19.9631 | 20.0088 | 19.9768 | 8.7708 | 8.6746 | 104.3518 | 104.1779 | -18.7225 | 104.4205 | 104.4296 | 0.25177 | -18.8965 | 112.0605 | 111.9644 | -0.022888 | 123.2162 | 123.2529 | 11.2885 | -0.054931 | 104.599 | 104.425 | 104.306 | -19.1437 | 123.2986 | 123.2666 | 123.2986 | -11.3571
2791.5156 | 123.4497 | -103.2944 | 19.9493 | 0.11902 | 0.010536 | 0.0037127 | 0.011113 | -0.021689 | -0.0047146 | 0.00020288 | 0.23979 | 0.020662 | -0.013208 | 0.0099314 | -0.0029308 | 0.010638 | 1.1581 | 1.1993 | 1.1124 | 1.1719 | 1.2909 | 1.1032 | 0.93384 | 19.9356 | 20.018 | 20.0226 | 19.931 | 19.9036 | 8.7799 | 8.6746 | 104.3976 | 104.2282 | -18.6584 | 104.4937 | 104.4662 | 0.23804 | -18.7912 | 112.0743 | 111.969 | -0.018311 | 123.23 | 123.317 | 11.348 | -0.045777 | 104.5853 | 104.4525 | 104.4067 | -19.0155 | 123.2254 | 123.1979 | 123.3124 | -11.2747
2792.5156 | 123.3673 | -103.3813 | 19.9219 | 0.14954 | 0.02079 | 0.0024311 | 0.014958 | -0.019766 | 0.0044712 | 0.0019119 | 0.12535 | 0.022371 | -0.0087222 | 0.013349 | -0.00079463 | 0.014056 | 1.0803 | 1.0574 | 0.97046 | 1.0941 | 1.3 | 1.0574 | 0.89264 | 19.7617 | 19.812 | 20.0867 | 19.9265 | 19.8898 | 8.7753 | 8.6838 | 104.4388 | 104.274 | -18.6218 | 104.4388 | 104.4754 | 0.20142 | -18.8416 | 112.1567 | 112.0651 | 0.004578 | 123.143 | 123.468 | 11.4029 | -0.032043 | 104.6814 | 104.4617 | 104.3518 | -19.0292 | 123.3078 | 123.2712 | 123.1934 | -11.2381
2793.5156 | 123.5138 | -103.3813 | 19.8349 | 0.18005 | 0.016304 | 0.0039263 | 0.011113 | -0.018271 | -0.00022865 | -0.00086512 | 0.13298 | 0.021302 | -0.010004 | 0.01164 | -0.00229 | 0.010638 | 1.2177 | 1.2314 | 1.1124 | 1.1719 | 1.2314 | 1.0529 | 0.90179 | 19.8853 | 19.9677 | 19.9402 | 19.8349 | 19.7754 | 8.7799 | 8.6655 | 104.4342 | 104.2831 | -18.6035 | 104.6127 | 104.5532 | 0.27008 | -18.6172 | 112.1613 | 112.0468 | 0 | 123.2666 | 123.3215 | 11.2747 | -0.059509 | 104.6127 | 104.599 | 104.4937 | -18.9331 | 123.2162 | 123.1567 | 123.349 | -11.1694
2794.5156 | 123.3582 | -103.4912 | 19.812 | 0.050354 | 0.02079 | 0.0022175 | 0.012822 | -0.01998 | 0.0036166 | 0.0014847 | 0.01091 | 0.021089 | -0.0091494 | 0.012281 | -0.0010082 | 0.0076477 | 1.1078 | 1.0483 | 0.98419 | 1.1032 | 1.2955 | 1.0483 | 0.8606 | 19.7021 | 19.7479 | 19.7342 | 19.8074 | 19.7708 | 8.7753 | 8.67 | 104.5395 | 104.3518 | -18.5165 | 104.5395 | 104.5944 | 0.24261 | -18.7042 | 112.2665 | 112.1613 | -0.004578 | 123.1934 | 123.2254 | 11.0641 | -0.041199 | 104.7867 | 104.599 | 104.4754 | -18.9514 | 123.2986 | 123.262 | 123.2391 | -11.142
2795.5156 | 123.4543 | -103.4958 | 19.7479 | 0.19531 | 0.01844 | 0.0024311 | 0.0096174 | -0.021262 | 0.0029758 | 0.0019119 | 0.20164 | 0.022798 | -0.011286 | 0.013563 | -0.0025036 | 0.0095703 | 1.1124 | 1.0986 | 1.0117 | 1.1078 | 1.3184 | 1.0803 | 0.90179 | 19.7388 | 19.7845 | 19.7891 | 19.78 | 19.7159 | 8.7753 | 8.6792 | 104.5761 | 104.3976 | -18.4296 | 104.5944 | 104.6036 | 0.20599 | -18.6356 | 112.2711 | 112.175 | 0.032043 | 123.2346 | 123.2849 | 11.1099 | -0.032044 | 104.8141 | 104.6082 | 104.5074 | -18.8461 | 123.2758 | 123.2117 | 123.2803 | -11.0687
2796.5156 | 123.4543 | -103.5141 | 19.7388 | 0.080872 | 0.012245 | 0.0062763 | 0.01154 | -0.016776 | -0.0064236 | 0.00084388 | 1.3689 | 0.018312 | -0.01214 | 0.014631 | -0.0044262 | 0.011707 | 1.1169 | 1.1719 | 1.0712 | 1.149 | 1.2863 | 1.0757 | 0.90179 | 19.7113 | 19.7845 | 19.812 | 19.7159 | 19.693 | 8.7799 | 8.6746 | 104.5898 | 104.4159 | -18.4525 | 104.686 | 104.6631 | 0.24719 | -18.6218 | 112.294 | 112.1887 | -0.022889 | 123.2254 | 123.3261 | 11.1374 | -0.045777 | 104.8004 | 104.631 | 104.5853 | -18.837 | 123.23 | 123.2071 | 123.2986 | -11.0641
2797.5156 | 123.4589 | -103.5736 | 19.693 | 0.14954 | 0.011818 | 0.0032855 | 0.012608 | -0.020621 | -0.0036464 | 0.00063028 | 0.23979 | 0.020234 | -0.012567 | 0.010786 | -0.0025036 | 0.011279 | 1.1673 | 1.1948 | 1.0895 | 1.1444 | 1.2772 | 1.1124 | 0.92468 | 19.6838 | 19.7479 | 19.7662 | 19.6793 | 19.6564 | 8.7753 | 8.6746 | 104.686 | 104.4983 | -18.4158 | 104.7684 | 104.718 | 0.21973 | -18.5257 | 112.3489 | 112.2482 | -0.013733 | 123.2574 | 123.3398 | 11.0916 | -0.036621 | 104.8508 | 104.7409 | 104.6631 | -18.7683 | 123.2529 | 123.23 | 123.3215 | -11.0184
2798.5156 | 123.4772 | -103.6102 | 19.6564 | 0.14954 | 0.012886 | 0.0043537 | 0.012608 | -0.01998 | -0.00086945 | -0.0012923 | 0.2169 | 0.020448 | -0.011072 | 0.011213 | -0.0042126 | 0.010211 | 1.1902 | 1.1993 | 1.1261 | 1.1627 | 1.2497 | 1.0986 | 0.9201 | 19.6884 | 19.7479 | 19.7342 | 19.6564 | 19.5969 | 8.7799 | 8.6746 | 104.7089 | 104.5303 | -18.4067 | 104.8096 | 104.7729 | 0.24262 | -18.4662 | 112.3901 | 112.2849 | 0 | 123.2986 | 123.3444 | 11.0596 | -0.059509 | 104.8599 | 104.8004 | 104.7363 | -18.7363 | 123.2666 | 123.2071 | 123.3582 | -10.9818
2799.5156 | 123.468 | -103.656 | 19.5694 | 0.19531 | 0.013099 | 0.0037127 | 0.010899 | -0.019126 | -0.00086945 | 0.0021255 | 0.20164 | 0.01938 | -0.011927 | 0.011854 | -0.0031446 | 0.010425 | 1.181 | 1.1993 | 1.1124 | 1.1719 | 1.268 | 1.0895 | 0.92468 | 19.5969 | 19.6564 | 19.6655 | 19.5648 | 19.519 | 8.7753 | 8.6746 | 104.7455 | 104.5807 | -18.3014 | 104.8553 | 104.8279 | 0.24719 | -18.3884 | 112.4313 | 112.3306 | -0.004578 | 123.2529 | 123.3215 | 10.9909 | -0.050354 | 104.924 | 104.837 | 104.7684 | -18.6447 | 123.2208 | 123.175 | 123.3124 | -10.8948
2800.5156 | 123.5001 | -103.6697 | 19.5328 | 0.21057 | 0.014595 | 0.0026447 | 0.014103 | -0.020621 | 0.0029758 | 0.0016983 | 0.12535 | 0.020662 | -0.0097904 | 0.012068 | -0.0012218 | 0.0085021 | 1.1765 | 1.1765 | 1.0849 | 1.1673 | 1.2726 | 1.0803 | 0.90637 | 19.5969 | 19.6289 | 19.6243 | 19.5282 | 19.4778 | 8.7799 | 8.67 | 104.7501 | 104.5761 | -18.2602 | 104.8462 | 104.837 | 0.26093 | -18.3563 | 112.4496 | 112.3398 | -0.004578 | 123.2666 | 123.2941 | 10.9543 | -0.054932 | 104.9423 | 104.8462 | 104.7546 | -18.6264 | 123.1979 | 123.1476 | 123.2986 | -10.8627
2801.5156 | 123.3902 | -103.7613 | 19.5511 | -0.15564 | 0.016517 | 0.0020037 | 0.017094 | -0.019339 | 0.0019078 | 0.0012711 | -0.19508 | 0.023866 | -0.011072 | 0.01164 | -0.0014356 | 0.0063659 | 1.1169 | 1.1032 | 1.0025 | 1.1124 | 1.2909 | 1.0345 | 0.8606 | 19.4733 | 19.5648 | 19.5145 | 19.5786 | 19.5328 | 8.7845 | 8.6746 | 104.7958 | 104.6219 | -18.2602 | 104.8645 | 104.8737 | 0.25177 | -18.4341 | 112.5458 | 112.4359 | 0.027466 | 123.2346 | 123.2758 | 10.8398 | -0.01831 | 105.0522 | 104.8782 | 104.7638 | -18.6905 | 123.3398 | 123.2941 | 123.3261 | -10.8765
2802.5156 | 123.436 | -103.7842 | 19.4641 | 0.18005 | 0.016304 | 0.0011493 | 0.013249 | -0.020621 | 0.00083955 | 0.0023391 | 0.17876 | 0.02173 | -0.012781 | 0.014417 | -0.00229 | 0.010211 | 1.0941 | 1.0895 | 1.0071 | 1.0986 | 1.2863 | 1.0529 | 0.88348 | 19.4687 | 19.5145 | 19.4916 | 19.5099 | 19.4321 | 8.7845 | 8.6655 | 104.837 | 104.6677 | -18.1778 | 104.8737 | 104.8828 | 0.21515 | -18.3701 | 112.5687 | 112.4496 | 0.045777 | 123.2529 | 123.2758 | 10.8261 | -0.032043 | 105.0705 | 104.8782 | 104.7913 | -18.5806 | 123.2941 | 123.2162 | 123.2986 | -10.7986
2803.5156 | 123.4543 | -103.8116 | 19.4275 | 0.065613 | 0.0096813 | 0.0056353 | 0.01154 | -0.019553 | -0.0036464 | 0.00041648 | -0.042496 | 0.021943 | -0.011499 | 0.0086496 | -0.0042126 | 0.010425 | 1.1032 | 1.1719 | 1.0895 | 1.1398 | 1.2772 | 1.0757 | 0.90637 | 19.3863 | 19.5236 | 19.487 | 19.4183 | 19.3588 | 8.7799 | 8.6792 | 104.8874 | 104.718 | -18.1503 | 104.9835 | 104.9515 | 0.23346 | -18.3243 | 112.5916 | 112.4908 | -0.009155 | 123.1979 | 123.2986 | 10.8078 | -0.068664 | 105.0888 | 104.9149 | 104.9011 | -18.5211 | 123.23 | 123.1705 | 123.3353 | -10.7483
2804.5156 | 123.4955 | -103.8437 | 19.4138 | 0.17242 | 0.015236 | 0.0026447 | 0.013463 | -0.019766 | -0.0017238 | 0.0010575 | 0.17876 | 0.021089 | -0.012995 | 0.011854 | -0.00229 | 0.0082885 | 1.1856 | 1.2085 | 1.1169 | 1.1673 | 1.2497 | 1.0849 | 0.90637 | 19.4504 | 19.5099 | 19.5007 | 19.3817 | 19.3359 | 8.7845 | 8.6746 | 104.9286 | 104.7501 | -18.1641 | 105.0522 | 105.011 | 0.26093 | -18.2281 | 112.6282 | 112.5183 | -0.032043 | 123.2941 | 123.3444 | 10.8261 | -0.07782 | 105.0934 | 105.0293 | 104.9606 | -18.5074 | 123.2254 | 123.1796 | 123.3536 | -10.7391
2805.5156 | 123.4818 | -103.8757 | 19.3542 | 0.019836 | 0.0092541 | 0.0034991 | 0.012394 | -0.021689 | -0.00086945 | -0.00065152 | 0.049057 | 0.018739 | -0.011499 | 0.012068 | -0.003999 | 0.0078613 | 1.1215 | 1.1627 | 1.0757 | 1.149 | 1.268 | 1.0895 | 0.89722 | 19.3817 | 19.4641 | 19.4687 | 19.3726 | 19.3085 | 8.7708 | 8.6746 | 104.9652 | 104.7729 | -18.0862 | 105.0385 | 105.0247 | 0.25177 | -18.2327 | 112.6465 | 112.5504 | 0.018311 | 123.2574 | 123.3444 | 10.7941 | -0.045776 | 105.1437 | 104.9973 | 104.9515 | -18.457 | 123.2483 | 123.1842 | 123.3398 | -10.6796
2806.5156 | 123.5092 | -103.894 | 19.3039 | 1.0727 | 0.011177 | 0.0049945 | 0.014744 | -0.019553 | -0.001083 | -0.00043792 | -0.13405 | 0.018098 | -0.010004 | 0.013349 | -0.00229 | 0.0085021 | 1.1902 | 1.2085 | 1.1078 | 1.1765 | 1.2543 | 1.0574 | 0.91553 | 19.368 | 19.4733 | 19.4275 | 19.3085 | 19.2444 | 8.7845 | 8.6838 | 104.9515 | 104.8096 | -18.0496 | 105.1025 | 105.0705 | 0.26093 | -18.1137 | 112.6785 | 112.5778 | 0.004578 | 123.262 | 123.3215 | 10.7437 | -0.059509 | 105.1483 | 105.0842 | 105.0018 | -18.3884 | 123.2025 | 123.1384 | 123.3673 | -10.6201
2807.5156 | 123.5184 | -103.9719 | 19.2627 | -0.26245 | 0.010109 | 0.0037127 | 0.01154 | -0.019126 | -1.505e-05 | 0.0019119 | -0.11116 | 0.020875 | -0.010004 | 0.010786 | -0.0020764 | 0.0085021 | 1.1398 | 1.2634 | 1.1169 | 1.1765 | 1.2405 | 1.0803 | 0.88806 | 19.3222 | 19.4229 | 19.3863 | 19.2581 | 19.1757 | 8.7799 | 8.6746 | 105.0522 | 104.8599 | -18.0222 | 105.2353 | 105.1483 | 0.28839 | -18.1229 | 112.7518 | 112.6465 | -0.004577 | 123.2941 | 123.3582 | 10.7117 | -0.086975 | 105.2124 | 105.1117 | 105.0888 | -18.3746 | 123.23 | 123.1476 | 123.3948 | -10.5881
2808.5156 | 123.4863 | -103.9948 | 19.2123 | 0.17242 | 0.015449 | 0.0045673 | 0.011754 | -0.021262 | 0.0012668 | 0.00041648 | 0.11772 | 0.020448 | -0.011286 | 0.010786 | -0.0027172 | 0.0080749 | 1.1536 | 1.2222 | 1.1078 | 1.1627 | 1.236 | 1.0666 | 0.90637 | 19.2856 | 19.313 | 19.3039 | 19.2261 | 19.1254 | 8.7799 | 8.6792 | 105.0613 | 104.9011 | -17.9764 | 105.217 | 105.1575 | 0.25635 | -18.0588 | 112.7747 | 112.6739 | 0.013733 | 123.2803 | 123.2986 | 10.6247 | -0.086975 | 105.2307 | 105.1483 | 105.1025 | -18.306 | 123.2208 | 123.1201 | 123.3078 | -10.5331
2809.5156 | 123.5138 | -104.0771 | 19.1803 | 0.0045777 | 0.010109 | 0.0043537 | 0.012608 | -0.020835 | -0.0021512 | 0.00084388 | -0.011978 | 0.019166 | -0.011927 | 0.012068 | -0.003999 | 0.0078613 | 1.1444 | 1.2085 | 1.0803 | 1.1765 | 1.2772 | 1.0803 | 0.90637 | 19.2078 | 19.2947 | 19.281 | 19.1666 | 19.1162 | 8.7753 | 8.6746 | 105.1575 | 104.9835 | -17.9031 | 105.2856 | 105.2536 | 0.27008 | -18.0359 | 112.8525 | 112.7518 | -0.013733 | 123.2849 | 123.3582 | 10.6064 | -0.064087 | 105.3543 | 105.2216 | 105.1575 | -18.2739 | 123.2437 | 123.1934 | 123.3719 | -10.5057
2810.5156 | 123.4772 | -104.1 | 19.1299 | -0.65155 | 0.011604 | 0.0028583 | 0.010899 | -0.020194 | -0.0012966 | 0.0010575 | 0.056686 | 0.020021 | -0.013208 | 0.0082224 | -0.0037854 | 0.0097839 | 1.1078 | 1.149 | 1.0712 | 1.1353 | 1.236 | 1.0483 | 0.86975 | 19.1162 | 19.2123 | 19.1849 | 19.1483 | 19.0659 | 8.7799 | 8.6746 | 105.1483 | 104.9698 | -17.894 | 105.249 | 105.2353 | 0.2655 | -18.0222 | 112.8799 | 112.7747 | 0.01831 | 123.2162 | 123.2849 | 10.5103 | -0.064087 | 105.336 | 105.2078 | 105.1712 | -18.2602 | 123.2483 | 123.1659 | 123.3124 | -10.4553
2811.5156 | 123.3765 | -104.2053 | 19.1208 | -0.056458 | 0.015236 | 0.0034991 | 0.016026 | -0.018485 | 0.0038304 | -0.00086512 | -0.10353 | 0.020875 | -0.0097904 | 0.013136 | 0.00070077 | 0.0080749 | 1.0941 | 1.0986 | 0.99335 | 1.0941 | 1.2955 | 1.0208 | 0.85144 | 19.0613 | 19.0842 | 19.0933 | 19.1299 | 19.0842 | 8.7753 | 8.6746 | 105.2261 | 105.0568 | -17.8253 | 105.304 | 105.2994 | 0.24262 | -18.0267 | 112.9807 | 112.8799 | 0.009155 | 123.2666 | 123.2986 | 10.4187 | -0.036622 | 105.5008 | 105.2994 | 105.1987 | -18.2693 | 123.3353 | 123.2895 | 123.2895 | -10.4462
2812.5156 | 123.4726 | -104.1962 | 19.0384 | -0.23956 | 0.0088269 | 0.0049945 | 0.01154 | -0.020407 | -0.0038602 | 0.00020288 | 0.064316 | 0.01938 | -0.01449 | 0.0097176 | -0.0020764 | 0.0095703 | 1.0941 | 1.1581 | 1.0529 | 1.1307 | 1.2405 | 1.062 | 0.87891 | 19.0521 | 19.1116 | 19.1254 | 19.0475 | 18.9697 | 8.7799 | 8.67 | 105.2582 | 105.0751 | -17.7979 | 105.3543 | 105.3268 | 0.25177 | -17.9443 | 112.9761 | 112.8662 | 0.009155 | 123.2483 | 123.3215 | 10.4553 | -0.068664 | 105.4367 | 105.2902 | 105.249 | -18.1595 | 123.2437 | 123.1659 | 123.3078 | -10.3683
2813.5156 | 123.4863 | -104.2648 | 18.9926 | -0.14038 | 0.0096813 | 0.0054217 | 0.012822 | -0.018057 | -0.00022865 | 0.0014847 | -0.12642 | 0.020875 | -0.012995 | 0.011427 | -0.0031446 | 0.0091431 | 1.1581 | 1.2451 | 1.1078 | 1.1719 | 1.2543 | 1.0712 | 0.87891 | 19.043 | 19.1711 | 19.0933 | 19.0018 | 18.9285 | 8.7799 | 8.6746 | 105.336 | 105.1437 | -17.7383 | 105.5099 | 105.4367 | 0.29297 | -17.8345 | 113.0447 | 112.9395 | 0.009155 | 123.3078 | 123.3582 | 10.4187 | -0.064087 | 105.5191 | 105.423 | 105.3726 | -18.1137 | 123.2666 | 123.1934 | 123.436 | -10.318
2814.5156 | 123.4863 | -104.3106 | 18.9514 | 0.27924 | 0.010536 | 0.0049945 | 0.01389 | -0.01998 | 0.00019875 | 0.0010575 | 0.041427 | 0.019166 | -0.013208 | 0.011854 | -0.0029308 | 0.010852 | 1.0803 | 1.1581 | 1.0391 | 1.1124 | 1.2497 | 1.0574 | 0.87891 | 18.9468 | 19.0201 | 19.0384 | 18.9468 | 18.8873 | 8.7753 | 8.67 | 105.368 | 105.1895 | -17.7017 | 105.4688 | 105.423 | 0.23346 | -17.8711 | 113.0859 | 112.9807 | -0.004578 | 123.2574 | 123.349 | 10.3683 | -0.064087 | 105.5603 | 105.3909 | 105.3497 | -18.0725 | 123.2574 | 123.1979 | 123.3307 | -10.2814
2815.5156 | 123.3994 | -104.3701 | 18.9514 | -0.18616 | 0.012886 | 0.0034991 | 0.016453 | -0.02233 | 0.0019078 | 0.00020288 | -0.21034 | 0.020234 | -0.010858 | 0.010999 | -0.0020764 | 0.0097839 | 1.1169 | 1.1856 | 1.0529 | 1.1353 | 1.2543 | 1.03 | 0.86975 | 18.8919 | 18.988 | 18.9468 | 18.9468 | 18.8507 | 8.7753 | 8.6792 | 105.4001 | 105.2399 | -17.6971 | 105.5557 | 105.5054 | 0.2655 | -17.8345 | 113.1454 | 113.0493 | -0.004578 | 123.262 | 123.317 | 10.2676 | -0.10071 | 105.6244 | 105.4871 | 105.423 | -18.0817 | 123.317 | 123.2208 | 123.3582 | -10.2722
2816.5156 | 123.4818 | -104.3793 | 18.8416 | -0.0030518 | 0.011177 | 0.0045673 | 0.012394 | -0.020621 | -0.0019376 | 0.0012711 | 0.071945 | 0.020021 | -0.012354 | 0.011854 | -0.0027172 | 0.0085021 | 1.0757 | 1.1673 | 1.03 | 1.1215 | 1.2497 | 1.0483 | 0.89264 | 18.8644 | 18.9331 | 18.9331 | 18.8461 | 18.7729 | 8.7753 | 8.67 | 105.4276 | 105.2719 | -17.5919 | 105.5466 | 105.5008 | 0.22888 | -17.7658 | 113.1546 | 113.0493 | 0.004577 | 123.2437 | 123.3124 | 10.2631 | -0.068665 | 105.629 | 105.455 | 105.4092 | -17.9489 | 123.2254 | 123.1522 | 123.3124 | -10.1715
2817.5156 | 123.4909 | -104.425 | 18.8187 | -0.12512 | 0.012245 | 0.0034991 | 0.010472 | -0.018698 | 0.0010532 | 0.0016983 | -0.14168 | 0.021516 | -0.011927 | 0.0086496 | -0.0025036 | 0.0097839 | 1.1398 | 1.2222 | 1.0895 | 1.1581 | 1.236 | 1.0483 | 0.89722 | 18.8736 | 18.9926 | 18.8965 | 18.837 | 18.7592 | 8.7845 | 8.6746 | 105.4733 | 105.3223 | -17.5827 | 105.6473 | 105.5832 | 0.26092 | -17.6788 | 113.2095 | 113.0997 | 0.01831 | 123.2986 | 123.3215 | 10.2219 | -0.05951 | 105.661 | 105.5649 | 105.5145 | -17.9214 | 123.262 | 123.1842 | 123.4177 | -10.144
2818.5156 | 123.4039 | -104.4937 | 18.7958 | -0.1709 | 0.018013 | 0.0047809 | 0.016667 | -0.020194 | 0.0036166 | 0.0034073 | -0.23323 | 0.023225 | -0.010431 | 0.012708 | -0.0012218 | 0.0059387 | 1.0712 | 1.1032 | 0.97504 | 1.0986 | 1.268 | 1.0117 | 0.83771 | 18.75 | 18.8278 | 18.7683 | 18.8187 | 18.718 | 8.7753 | 8.67 | 105.5054 | 105.3314 | -17.5278 | 105.5969 | 105.5923 | 0.26092 | -17.7246 | 113.269 | 113.1638 | 0.022889 | 123.2437 | 123.262 | 10.0983 | -0.077819 | 105.7617 | 105.5649 | 105.4688 | -17.9581 | 123.3124 | 123.2117 | 123.3215 | -10.1257
2819.5156 | 123.3902 | -104.5532 | 18.7912 | -0.1709 | 0.014168 | 0.0052081 | 0.013249 | -0.019126 | -0.00065585 | 0.0021255 | -0.17983 | 0.021516 | -0.012354 | 0.012922 | -0.0031446 | 0.0085021 | 1.0712 | 1.1398 | 1.0071 | 1.0941 | 1.2634 | 1.0391 | 0.8606 | 18.6951 | 18.8004 | 18.75 | 18.7866 | 18.7042 | 8.7891 | 8.6746 | 105.5923 | 105.4138 | -17.5278 | 105.6931 | 105.6473 | 0.23346 | -17.72 | 113.3423 | 113.2278 | -0.004578 | 123.2483 | 123.3032 | 10.0754 | -0.086975 | 105.8167 | 105.6244 | 105.5603 | -17.9306 | 123.3398 | 123.2574 | 123.3536 | -10.1166
2820.5156 | 123.5275 | -104.512 | 18.6905 | -0.056458 | 0.0096813 | 0.0062763 | 0.012608 | -0.018271 | -0.0032192 | 0.00020288 | -0.027237 | 0.020234 | -0.011927 | 0.012281 | -0.0048534 | 0.0093567 | 1.1307 | 1.2314 | 1.0941 | 1.1581 | 1.2497 | 1.0712 | 0.89722 | 18.7912 | 18.8873 | 18.8461 | 18.718 | 18.6218 | 8.7753 | 8.6746 | 105.5832 | 105.4092 | -17.4408 | 105.7434 | 105.6702 | 0.26092 | -17.5598 | 113.2874 | 113.1866 | 0.027466 | 123.3032 | 123.3582 | 10.1715 | -0.068665 | 105.7617 | 105.6427 | 105.6061 | -17.7933 | 123.23 | 123.1338 | 123.3994 | -10.0159
2821.5156 | 123.4314 | -104.5944 | 18.7134 | -0.048828 | 0.02079 | 0.00029489 | 0.019444 | -0.019126 | 0.0059666 | 0.00084388 | -0.14931 | 0.02408 | -0.011072 | 0.013349 | -0.0012218 | 0.0074341 | 1.1078 | 1.1398 | 1.0025 | 1.1032 | 1.2589 | 1.0071 | 0.83771 | 18.6447 | 18.956 | 18.6722 | 18.7454 | 18.6356 | 8.7799 | 8.6792 | 105.6015 | 105.4321 | -17.4545 | 105.7343 | 105.6976 | 0.2655 | -17.6056 | 113.3743 | 113.2736 | 0.032043 | 123.2391 | 123.2666 | 9.993 | -0.07782 | 105.8533 | 105.7022 | 105.5969 | -17.8757 | 123.3398 | 123.23 | 123.5504 | -10.0342
2822.5156 | 123.5413 | -104.6173 | 18.6401 | -0.0030518 | 0.012459 | 0.0062763 | 0.011967 | -0.018485 | -0.0040738 | 0.00041648 | -0.034867 | 0.020875 | -0.01214 | 0.013563 | -0.0035718 | 0.0099975 | 1.1078 | 1.2497 | 1.0895 | 1.1536 | 1.236 | 1.062 | 0.86975 | 18.7134 | 18.8141 | 18.7729 | 18.6127 | 18.5349 | 8.7799 | 8.6838 | 105.6793 | 105.4871 | -17.4042 | 105.867 | 105.7709 | 0.28381 | -17.5323 | 113.3972 | 113.3011 | -0.027466 | 123.3307 | 123.3902 | 10.0891 | -0.10529 | 105.8533 | 105.7251 | 105.7068 | -17.7704 | 123.23 | 123.1522 | 123.4314 | -9.9564
2823.5312 | 123.3948 | -104.686 | 18.6081 | -0.02594 | 0.020576 | 0.0037127 | 0.016881 | -0.020835 | 0.005753 | 0.0044755 | -0.080643 | 0.024293 | -0.0087222 | 0.01164 | -0.00058103 | 0.0074341 | 1.0895 | 1.1215 | 0.97961 | 1.0803 | 1.2405 | 1.0025 | 0.83313 | 18.576 | 18.631 | 18.5669 | 18.6356 | 18.544 | 8.7753 | 8.6746 | 105.6885 | 105.5191 | -17.3676 | 105.8075 | 105.7663 | 0.24719 | -17.5186 | 113.4613 | 113.3606 | 0.027466 | 123.262 | 123.2529 | 9.8923 | -0.064087 | 105.9265 | 105.7755 | 105.6656 | -17.775 | 123.3215 | 123.23 | 123.317 | -9.9335
2824.5156 | 123.6191 | -104.718 | 18.5577 | -0.033569 | 0.0094677 | 0.0045673 | 0.011754 | -0.018485 | -0.0053554 | 0.0027665 | -0.0043486 | 0.020021 | -0.012781 | 0.012281 | -0.0052808 | 0.010211 | 1.1398 | 1.2589 | 1.0941 | 1.1536 | 1.2314 | 1.0529 | 0.88348 | 18.631 | 18.7592 | 18.6905 | 18.5532 | 18.4982 | 8.7845 | 8.6884 | 105.7709 | 105.6015 | -17.3264 | 105.9769 | 105.8716 | 0.27008 | -17.4179 | 113.5025 | 113.4064 | -0.004577 | 123.349 | 123.4085 | 10.0021 | -0.059509 | 105.9494 | 105.8578 | 105.8121 | -17.6743 | 123.2712 | 123.2162 | 123.4772 | -9.8694
2825.5156 | 123.4177 | -104.7546 | 18.5577 | -0.20142 | 0.012886 | 0.0011493 | 0.012181 | -0.01763 | 0.00062595 | 0.0016983 | -0.14168 | 0.019807 | -0.013208 | 0.012281 | -0.0029308 | 0.0076477 | 1.0803 | 1.181 | 1.0391 | 1.1169 | 1.2405 | 1.0162 | 0.83771 | 18.4845 | 18.6127 | 18.5532 | 18.5715 | 18.4525 | 8.7753 | 8.6746 | 105.7709 | 105.5923 | -17.3172 | 105.9357 | 105.8716 | 0.27924 | -17.4774 | 113.53 | 113.4293 | 0.013733 | 123.2391 | 123.3078 | 9.8785 | -0.10529 | 105.9952 | 105.835 | 105.7938 | -17.72 | 123.3261 | 123.2071 | 123.3673 | -9.8831
2826.5156 | 123.4177 | -104.7729 | 18.5165 | -0.17853 | 0.010536 | 0.0060627 | 0.010685 | -0.018485 | -0.00065585 | 0.0012711 | -0.18745 | 0.020234 | -0.0095768 | 0.010999 | -0.0031446 | 0.0099975 | 1.0941 | 1.1627 | 1.0391 | 1.1307 | 1.2497 | 1.0208 | 0.84686 | 18.4433 | 18.5623 | 18.5074 | 18.5165 | 18.4341 | 8.7708 | 8.6746 | 105.7938 | 105.6198 | -17.2668 | 105.9357 | 105.9036 | 0.28381 | -17.4225 | 113.5437 | 113.4476 | 0 | 123.2162 | 123.2803 | 9.8328 | -0.082398 | 106.0226 | 105.867 | 105.8121 | -17.6697 | 123.2895 | 123.2071 | 123.3353 | -9.8419
2827.5156 | 123.3902 | -104.8691 | 18.4662 | -0.14038 | 0.018013 | 0.0056353 | 0.01389 | -0.01998 | 0.0021214 | 0.0019119 | -0.21034 | 0.020448 | -0.0091494 | 0.010359 | -0.0016492 | 0.0095703 | 1.0208 | 1.0803 | 0.95215 | 1.0712 | 1.2497 | 0.98419 | 0.82398 | 18.3838 | 18.4753 | 18.4341 | 18.4891 | 18.3975 | 8.7753 | 8.6746 | 105.8533 | 105.6931 | -17.2165 | 105.9494 | 105.9402 | 0.24719 | -17.4454 | 113.6444 | 113.5437 | 0.022888 | 123.2529 | 123.3032 | 9.7595 | -0.068665 | 106.1188 | 105.8899 | 105.8212 | -17.6422 | 123.3582 | 123.2666 | 123.3444 | -9.7916
2828.5156 | 123.4039 | -104.8965 | 18.4296 | 0.012207 | 0.01844 | 0.0026447 | 0.014531 | -0.018057 | 0.0046848 | 0.0029801 | -0.019608 | 0.020448 | -0.0087222 | 0.013136 | -0.0012218 | 0.0085021 | 1.0529 | 1.0986 | 0.9613 | 1.0574 | 1.2543 | 0.99792 | 0.82855 | 18.3563 | 18.4113 | 18.3746 | 18.4204 | 18.3426 | 8.7708 | 8.6746 | 105.8945 | 105.7251 | -17.1753 | 105.9952 | 105.954 | 0.22888 | -17.3767 | 113.6673 | 113.5712 | -0.009155 | 123.2529 | 123.2712 | 9.7 | -0.086975 | 106.1508 | 105.9494 | 105.8578 | -17.601 | 123.317 | 123.2391 | 123.3078 | -9.7549
2829.5156 | 123.3902 | -104.9515 | 18.4021 | -0.19379 | 0.010536 | 0.0020037 | 0.015172 | -0.018485 | -0.002792 | 0.0014847 | -0.17983 | 0.020662 | -0.012567 | 0.014204 | -0.003999 | 0.0097839 | 1.062 | 1.1627 | 1.0391 | 1.1215 | 1.236 | 1.0071 | 0.85144 | 18.3151 | 18.4433 | 18.3884 | 18.3884 | 18.338 | 8.7753 | 8.6838 | 105.9586 | 105.8029 | -17.1661 | 106.1142 | 106.073 | 0.27008 | -17.3401 | 113.7268 | 113.6353 | -0.013733 | 123.2666 | 123.3398 | 9.7046 | -0.064087 | 106.1874 | 106.0135 | 105.9906 | -17.5507 | 123.3398 | 123.2895 | 123.3948 | -9.7183
2830.5156 | 123.4131 | -104.9652 | 18.3746 | -0.18616 | 0.012031 | 0.0056353 | 0.013035 | -0.021048 | -0.0023648 | 0.0010575 | -0.11879 | 0.019807 | -0.013422 | 0.012495 | -0.0010082 | 0.0091431 | 1.062 | 1.1581 | 1.03 | 1.1078 | 1.2451 | 1.0208 | 0.85144 | 18.2831 | 18.3929 | 18.3517 | 18.338 | 18.3014 | 8.7799 | 8.6838 | 105.986 | 105.8166 | -17.1295 | 106.1234 | 106.073 | 0.25635 | -17.3126 | 113.7451 | 113.649 | -0.036621 | 123.2483 | 123.317 | 9.668 | -0.073242 | 106.2103 | 106.0272 | 105.9952 | -17.5232 | 123.3032 | 123.2666 | 123.3582 | -9.6909
2831.5312 | 123.3765 | -105.0247 | 18.3014 | 0.035095 | 0.019935 | 0.00093569 | 0.015385 | -0.016989 | 0.0055392 | 0.0025529 | -0.042496 | 0.022157 | -0.0085086 | 0.015058 | -0.0010082 | 0.0080749 | 1.0071 | 1.0345 | 0.91095 | 1.0391 | 1.2085 | 0.97961 | 0.8194 | 18.187 | 18.2419 | 18.2144 | 18.3105 | 18.2465 | 8.7662 | 8.6746 | 106.0043 | 105.8441 | -17.0929 | 106.0593 | 106.0638 | 0.21973 | -17.2943 | 113.7909 | 113.6993 | 0.009155 | 123.2117 | 123.2391 | 9.5398 | -0.054932 | 106.2332 | 106.0318 | 105.9357 | -17.482 | 123.3353 | 123.2712 | 123.2666 | -9.6268
2832.5156 | 123.4909 | -104.9973 | 18.2602 | -0.12512 | 0.0096813 | 0.0034991 | 0.014531 | -0.018271 | -0.0055692 | 0.0016983 | -0.095902 | 0.019593 | -0.01449 | 0.012495 | -0.0027172 | 0.012134 | 1.0803 | 1.2131 | 1.0757 | 1.1398 | 1.2177 | 1.0345 | 0.86517 | 18.2739 | 18.4067 | 18.3609 | 18.2465 | 18.1915 | 8.7799 | 8.6792 | 106.0318 | 105.8624 | -17.0425 | 106.2103 | 106.1371 | 0.27466 | -17.1799 | 113.7772 | 113.6765 | -0.013733 | 123.2712 | 123.3582 | 9.6817 | -0.068665 | 106.2149 | 106.0776 | 106.073 | -17.395 | 123.2437 | 123.1888 | 123.4039 | -9.581
2833.5156 | 123.4085 | -105.0705 | 18.2465 | -0.1709 | 0.015877 | 0.0020037 | 0.012608 | -0.017844 | 0.0036166 | 0.00041648 | -0.16457 | 0.022584 | -0.0085086 | 0.010786 | -0.0027172 | 0.0091431 | 1.0162 | 1.0666 | 0.94299 | 1.0529 | 1.2451 | 0.97504 | 0.80109 | 18.1412 | 18.2465 | 18.2098 | 18.2556 | 18.1732 | 8.7799 | 8.6655 | 106.0455 | 105.8716 | -17.0013 | 106.1371 | 106.1234 | 0.25177 | -17.2302 | 113.8504 | 113.736 | 0.009155 | 123.2117 | 123.2803 | 9.5444 | -0.073242 | 106.3156 | 106.0867 | 106.0135 | -17.4454 | 123.3261 | 123.2437 | 123.317 | -9.581
2834.5156 | 123.4909 | -105.098 | 18.1824 | -0.14801 | 0.011604 | 0.0034991 | 0.013249 | -0.019339 | -0.0047146 | 0.0019119 | -0.095902 | 0.018953 | -0.015131 | 0.011854 | -0.0046398 | 0.012134 | 1.1124 | 1.1856 | 1.062 | 1.1307 | 1.1948 | 1.03 | 0.84686 | 18.1824 | 18.3289 | 18.2877 | 18.187 | 18.1183 | 8.7799 | 8.6746 | 106.1279 | 105.9448 | -16.9876 | 106.2836 | 106.2286 | 0.28381 | -17.07 | 113.8779 | 113.7726 | 0.004578 | 123.2803 | 123.3856 | 9.613 | -0.064087 | 106.2927 | 106.2103 | 106.16 | -17.3355 | 123.2849 | 123.2162 | 123.4268 | -9.5078
2835.5156 | 123.3902 | -105.1529 | 18.1503 | -0.16327 | 0.016731 | 0.0043537 | 0.016026 | -0.018057 | 0.001694 | 0.0010575 | -0.15694 | 0.022371 | -0.011286 | 0.012495 | -0.0029308 | 0.0080749 | 1.0254 | 1.0529 | 0.92926 | 1.0483 | 1.2451 | 0.96588 | 0.81482 | 18.045 | 18.1549 | 18.1 | 18.1549 | 18.1046 | 8.7799 | 8.67 | 106.1188 | 105.9677 | -16.9052 | 106.2057 | 106.2012 | 0.23346 | -17.1249 | 113.9328 | 113.8229 | 0.004577 | 123.1979 | 123.2529 | 9.4299 | -0.045777 | 106.398 | 106.1783 | 106.0822 | -17.3355 | 123.3078 | 123.2574 | 123.3078 | -9.4803
2836.5156 | 123.436 | -105.1804 | 18.1183 | -0.18616 | 0.011818 | 0.0034991 | 0.012181 | -0.020621 | -0.002792 | 0.00063028 | -0.18745 | 0.018098 | -0.011713 | 0.010359 | -0.0037854 | 0.0097839 | 1.0712 | 1.1673 | 1.03 | 1.1169 | 1.2039 | 0.99335 | 0.84228 | 18.0679 | 18.1915 | 18.1366 | 18.1 | 18.0359 | 8.7708 | 8.6792 | 106.1737 | 106.0226 | -16.9144 | 106.3477 | 106.2973 | 0.27466 | -17.0471 | 113.9511 | 113.8596 | -0.01831 | 123.2483 | 123.317 | 9.4574 | -0.082397 | 106.3843 | 106.2515 | 106.2103 | -17.276 | 123.2803 | 123.2162 | 123.3719 | -9.4391
2837.5156 | 123.3994 | -105.249 | 18.0725 | -0.02594 | 0.016517 | 0.0041401 | 0.014103 | -0.019339 | 0.0025486 | 0.0023391 | -0.17983 | 0.022584 | -0.010431 | 0.012495 | -0.00058103 | 0.010425 | 1.0071 | 1.0574 | 0.9201 | 1.062 | 1.236 | 0.97961 | 0.82398 | 17.9718 | 18.0679 | 18.0222 | 18.0817 | 18.013 | 8.7708 | 8.6792 | 106.2286 | 106.073 | -16.8365 | 106.3065 | 106.311 | 0.23804 | -17.0654 | 114.0198 | 113.9282 | 0.009155 | 123.2208 | 123.2712 | 9.343 | -0.05951 | 106.485 | 106.2561 | 106.1691 | -17.2485 | 123.3307 | 123.262 | 123.317 | -9.3933
2838.5156 | 123.2895 | -105.2765 | 18.0634 | -0.23193 | 0.013099 | 0.0054217 | 0.012181 | -0.017844 | -0.0015102 | 0.0019119 | -0.16457 | 0.01938 | -0.011286 | 0.014417 | -0.0025036 | 0.0093567 | 1.0208 | 1.0895 | 0.97046 | 1.0483 | 1.2314 | 0.9613 | 0.80566 | 17.9398 | 18.0496 | 17.9764 | 18.0496 | 17.9535 | 8.7708 | 8.67 | 106.2378 | 106.0822 | -16.832 | 106.366 | 106.3248 | 0.24261 | -17.0425 | 114.0472 | 113.9465 | -0.013732 | 123.2162 | 123.2529 | 9.3063 | -0.10986 | 106.5079 | 106.2973 | 106.2469 | -17.2577 | 123.3261 | 123.23 | 123.3261 | -9.3933
2839.5156 | 123.4314 | -105.3268 | 17.9855 | -0.15564 | 0.013954 | 0.0054217 | 0.017308 | -0.018698 | 0.00083955 | 0.0016983 | -0.1722 | 0.021089 | -0.011072 | 0.013136 | -0.0035718 | 0.0080749 | 1.0254 | 1.0391 | 0.9201 | 1.0437 | 1.2222 | 0.9613 | 0.79651 | 17.9077 | 17.9993 | 17.9535 | 17.981 | 17.9306 | 8.7845 | 8.67 | 106.2881 | 106.1234 | -16.7633 | 106.366 | 106.3705 | 0.24719 | -16.9601 | 114.1113 | 113.9969 | -0.004578 | 123.2346 | 123.2803 | 9.2834 | -0.054932 | 106.5491 | 106.3522 | 106.2469 | -17.189 | 123.3078 | 123.2574 | 123.3261 | -9.3155
2840.5156 | 123.3994 | -105.3726 | 17.9718 | -0.18616 | 0.013527 | 0.0030719 | 0.012181 | -0.020407 | -0.0021512 | 0.0021255 | -0.11879 | 0.021302 | -0.011499 | 0.010999 | -0.0027172 | 0.0093567 | 1.0437 | 1.1215 | 0.97961 | 1.0712 | 1.2131 | 0.98419 | 0.83771 | 17.8711 | 17.9489 | 17.9306 | 17.9718 | 17.8848 | 8.7753 | 8.6792 | 106.3568 | 106.2103 | -16.7587 | 106.4941 | 106.4438 | 0.23346 | -16.9281 | 114.1479 | 114.0518 | 0 | 123.2437 | 123.3032 | 9.2514 | -0.086975 | 106.5857 | 106.4163 | 106.3522 | -17.1341 | 123.3444 | 123.2574 | 123.3215 | -9.2926
2841.5156 | 123.4268 | -105.3955 | 17.9123 | 0.78278 | 0.022926 | 0.0022175 | 0.017094 | -0.018912 | 0.00083955 | 0.0019119 | -0.10353 | 0.022371 | -0.011072 | 0.014417 | -0.0012218 | 0.0074341 | 1.1261 | 1.1124 | 0.99335 | 1.0895 | 1.2817 | 1.0071 | 0.85602 | 17.8711 | 17.9398 | 17.894 | 17.9214 | 17.8391 | 8.7708 | 8.6792 | 106.4026 | 106.2515 | -16.6306 | 106.5079 | 106.485 | 0.23346 | -16.7862 | 114.1663 | 114.0747 | 0.009156 | 123.2666 | 123.2895 | 9.2148 | -0.073242 | 106.6772 | 106.5216 | 106.3889 | -17.0563 | 123.317 | 123.2346 | 123.3353 | -9.2331
2842.5156 | 123.3856 | -105.455 | 17.9123 | -0.19379 | 0.014808 | 0.0079853 | 0.016881 | -0.020621 | -0.00065585 | 0.00041648 | 0.79674 | 0.023866 | -0.010858 | 0.012495 | -0.0035718 | 0.010638 | 0.98419 | 1.0483 | 0.92926 | 1.03 | 1.2268 | 0.97961 | 0.81482 | 17.7704 | 17.926 | 17.8345 | 17.9214 | 17.8528 | 8.7708 | 8.6746 | 106.4346 | 106.2698 | -16.6855 | 106.5033 | 106.485 | 0.21515 | -16.9281 | 114.2258 | 114.1296 | 0.009156 | 123.2254 | 123.2895 | 9.1599 | -0.059509 | 106.6818 | 106.4392 | 106.3843 | -17.0975 | 123.3765 | 123.3078 | 123.381 | -9.2377
2843.5156 | 123.3994 | -105.5008 | 17.8345 | -0.14801 | 0.015663 | 0.0034991 | 0.014744 | -0.019339 | 0.001694 | 0.0016983 | -0.14931 | 0.022157 | -0.010645 | 0.012068 | -0.0031446 | 0.0087157 | 0.97961 | 1.0529 | 0.9201 | 1.0483 | 1.236 | 0.96588 | 0.79651 | 17.7429 | 17.8436 | 17.7933 | 17.8391 | 17.7979 | 8.7708 | 8.67 | 106.4667 | 106.2973 | -16.5985 | 106.5536 | 106.5491 | 0.25177 | -16.8549 | 114.2715 | 114.1708 | 0.004577 | 123.2437 | 123.2941 | 9.1232 | -0.036621 | 106.7368 | 106.4804 | 106.4209 | -17.038 | 123.3398 | 123.2986 | 123.3444 | -9.1644
2844.5156 | 123.4085 | -105.4733 | 17.8299 | -0.19379 | 0.0096813 | 0.00093569 | 0.013249 | -0.019766 | -0.0021512 | -1.0724e-05 | -0.13405 | 0.020448 | -0.011499 | 0.011854 | -0.00229 | 0.0095703 | 1.062 | 1.1581 | 1.0117 | 1.0986 | 1.1948 | 0.99335 | 0.83313 | 17.7338 | 17.8894 | 17.8253 | 17.807 | 17.7704 | 8.7799 | 8.6746 | 106.4667 | 106.3065 | -16.6351 | 106.6315 | 106.572 | 0.2655 | -16.7679 | 114.2532 | 114.1479 | -0.022888 | 123.2071 | 123.2986 | 9.1507 | -0.059509 | 106.6681 | 106.5353 | 106.485 | -16.9968 | 123.2803 | 123.2437 | 123.3627 | -9.1553
2845.5156 | 123.4177 | -105.5283 | 17.775 | -0.018311 | 0.019508 | 0.0017901 | 0.016026 | -0.020835 | 0.0063938 | 0.0034073 | -1.2098 | 0.023225 | -0.010645 | 0.012281 | -0.0035718 | 0.0070067 | 1.0666 | 1.0849 | 0.97046 | 1.0666 | 1.2222 | 0.97504 | 0.82398 | 17.7429 | 17.8391 | 17.7612 | 17.7887 | 17.7383 | 8.7708 | 8.67 | 106.5033 | 106.3522 | -16.5527 | 106.6132 | 106.5948 | 0.24261 | -16.7084 | 114.299 | 114.1983 | 0.013733 | 123.2712 | 123.2895 | 9.0912 | -0.036621 | 106.7505 | 106.5948 | 106.4987 | -16.951 | 123.317 | 123.2666 | 123.3673 | -9.1049
2846.5156 | 123.436 | -105.5603 | 17.7521 | -0.02594 | 0.017799 | 0.0030719 | 0.017949 | -0.016776 | 0.0021214 | 0.0016983 | -0.21797 | 0.020875 | -0.0085086 | 0.010359 | -0.0046398 | 0.010638 | 1.0437 | 1.0895 | 0.96588 | 1.0529 | 1.2131 | 0.97046 | 0.80566 | 17.7063 | 17.7841 | 17.72 | 17.7567 | 17.6971 | 8.7799 | 8.67 | 106.5308 | 106.366 | -16.539 | 106.6498 | 106.6132 | 0.24719 | -16.7084 | 114.3402 | 114.2303 | 0.004578 | 123.2666 | 123.2803 | 9.05 | -0.054931 | 106.7734 | 106.604 | 106.5262 | -16.9464 | 123.317 | 123.2574 | 123.3444 | -9.082
2847.5156 | 123.3719 | -105.6061 | 17.7155 | 0.050354 | 0.018226 | 0.0024311 | 0.013035 | -0.018271 | 0.0010532 | 0.0044755 | 0.0032804 | 0.022371 | -0.009363 | 0.015486 | -0.0029308 | 0.0087157 | 0.97046 | 1.0345 | 0.90179 | 1.0208 | 1.1993 | 0.97046 | 0.78278 | 17.5781 | 17.6468 | 17.6193 | 17.72 | 17.6559 | 8.7753 | 8.67 | 106.5765 | 106.3889 | -16.5161 | 106.6406 | 106.6269 | 0.23804 | -16.745 | 114.3814 | 114.2761 | 0.004578 | 123.1842 | 123.2254 | 8.9493 | -0.059509 | 106.8054 | 106.5765 | 106.5079 | -16.9327 | 123.3261 | 123.262 | 123.2529 | -9.0454
2848.5156 | 123.4039 | -105.6519 | 17.6788 | -0.14801 | 0.013099 | 0.0032855 | 0.015172 | -0.01763 | -0.0017238 | 0.00084388 | -0.13405 | 0.020662 | -0.0097904 | 0.010145 | -0.0046398 | 0.012134 | 0.9613 | 1.0483 | 0.9201 | 1.0162 | 1.1948 | 0.95215 | 0.78735 | 17.5735 | 17.514 | 17.6697 | 17.688 | 17.6376 | 8.7799 | 8.6746 | 106.604 | 106.4392 | -16.4841 | 106.7001 | 106.6681 | 0.22888 | -16.7175 | 114.4318 | 114.3265 | 0.009155 | 123.2254 | 123.3215 | 8.9951 | -0.041199 | 106.8466 | 106.6132 | 106.572 | -16.8915 | 123.3398 | 123.2895 | 123.1659 | -9.0042
2849.5156 | 123.3948 | -105.7159 | 17.6056 | -0.0030518 | 0.01844 | 0.00093569 | 0.017735 | -0.019553 | 0.0010532 | 0.0023391 | 0.018539 | 0.023652 | -0.0091494 | 0.012922 | -0.0010082 | 0.0091431 | 1.0391 | 1.0574 | 0.92468 | 1.0483 | 1.1948 | 0.97504 | 0.80109 | 17.5369 | 17.5919 | 17.5644 | 17.5964 | 17.5781 | 8.7753 | 8.6746 | 106.691 | 106.517 | -16.4108 | 106.7734 | 106.7642 | 0.24719 | -16.5665 | 114.4913 | 114.3906 | -0.009155 | 123.2529 | 123.2803 | 8.8898 | -0.027466 | 106.9107 | 106.7551 | 106.6406 | -16.8045 | 123.3124 | 123.2941 | 123.3078 | -8.931
2850.5156 | 123.381 | -105.7251 | 17.5919 | -0.18616 | 0.015236 | 0.0032855 | 0.013676 | -0.019339 | 0.00062595 | -0.0010787 | -0.14168 | 0.021089 | -0.015345 | 0.010572 | -0.0035718 | 0.01192 | 0.96588 | 1.0391 | 0.9201 | 1.0071 | 1.236 | 0.97046 | 0.78278 | 17.4408 | 17.5415 | 17.5873 | 17.6239 | 17.5873 | 8.7799 | 8.67 | 106.6956 | 106.5079 | -16.3559 | 106.7642 | 106.7322 | 0.2243 | -16.626 | 114.505 | 114.3951 | 0.032043 | 123.1659 | 123.3124 | 8.9172 | -0.004578 | 106.9611 | 106.691 | 106.6452 | -16.8091 | 123.349 | 123.3124 | 123.2666 | -8.9218
2851.5938 | 123.4818 | -105.7159 | 17.4957 | 0.19531 | 0.014595 | 0.0017901 | 0.010685 | -0.017417 | -0.0032192 | 0.0021255 | 0.22453 | 0.022157 | -0.012567 | 0.012495 | -0.003999 | 0.011707 | 1.0574 | 1.1398 | 1.0162 | 1.0849 | 1.1765 | 0.99792 | 0.84686 | 17.5369 | 17.6193 | 17.601 | 17.4957 | 17.4637 | 8.7753 | 8.6746 | 106.7139 | 106.5628 | -16.3193 | 106.8558 | 106.8008 | 0.23804 | -16.4383 | 114.4913 | 114.3906 | 0 | 123.2529 | 123.317 | 8.9264 | -0.032044 | 106.8924 | 106.7734 | 106.7322 | -16.6489 | 123.2117 | 123.1796 | 123.3353 | -8.8211
2852.625 | 123.5092 | -105.8075 | 17.4179 | 0.16479 | 0.019295 | 0.0039263 | 0.013676 | -0.019126 | 0.00041235 | 0.00084388 | 0.27031 | 0.021302 | -0.012567 | 0.009504 | -0.0012218 | 0.0089295 | 1.0666 | 1.1078 | 1.03 | 1.0849 | 1.181 | 0.99792 | 0.82855 | 17.5049 | 17.5735 | 17.5598 | 17.482 | 17.4088 | 8.7845 | 8.6838 | 106.8054 | 106.636 | -16.2369 | 106.9153 | 106.8924 | 0.25635 | -16.3513 | 114.592 | 114.4913 | 0.064087 | 123.3124 | 123.3673 | 8.876 | -0.009156 | 106.9885 | 106.8741 | 106.8375 | -16.5894 | 123.2895 | 123.2162 | 123.381 | -8.7341
2853.5156 | 123.4039 | -105.835 | 17.4774 | -0.16327 | 0.016731 | 0.0030719 | 0.014103 | -0.021048 | -0.00044225 | 0.00020288 | -0.14168 | 0.02408 | -0.010218 | 0.010786 | -0.0010082 | 0.010425 | 1.0025 | 1.0117 | 0.90179 | 1.0208 | 1.1856 | 0.95215 | 0.7782 | 17.3813 | 17.4774 | 17.4271 | 17.4912 | 17.4179 | 8.7753 | 8.6746 | 106.7871 | 106.6132 | -16.2918 | 106.8466 | 106.8558 | 0.24262 | -16.4749 | 114.6103 | 114.5096 | 0.013733 | 123.2162 | 123.262 | 8.7524 | -0.059509 | 107.0206 | 106.8375 | 106.7368 | -16.6992 | 123.3261 | 123.2529 | 123.3124 | -8.8028
2854.5156 | 123.436 | -105.8853 | 17.4362 | -0.1709 | 0.015877 | 0.0011493 | 0.013676 | -0.018912 | 0.0031894 | -1.0724e-05 | -0.11879 | 0.022157 | -0.010858 | 0.010572 | -0.0031446 | 0.0074341 | 1.0208 | 1.0391 | 0.93384 | 1.0391 | 1.1993 | 0.93842 | 0.78278 | 17.3813 | 17.482 | 17.4088 | 17.4545 | 17.3767 | 8.7799 | 8.67 | 106.8237 | 106.6681 | -16.2369 | 106.9244 | 106.9244 | 0.25635 | -16.4154 | 114.6652 | 114.5554 | 0.018311 | 123.2666 | 123.2941 | 8.7387 | -0.059509 | 107.0847 | 106.9061 | 106.8192 | -16.6534 | 123.3398 | 123.262 | 123.3673 | -8.7662
2855.5156 | 123.4222 | -105.8945 | 17.4225 | -0.19379 | 0.015877 | 0.0028583 | 0.013676 | -0.019553 | 0.0014804 | 0.0012711 | -0.13405 | 0.022798 | -0.010645 | 0.012281 | -0.0027172 | 0.010425 | 0.97504 | 1.0071 | 0.91095 | 1.0071 | 1.2085 | 0.9613 | 0.77362 | 17.2852 | 17.3904 | 17.3584 | 17.4316 | 17.3447 | 8.7799 | 8.6838 | 106.8558 | 106.6681 | -16.214 | 106.9016 | 106.9016 | 0.23346 | -16.4474 | 114.6744 | 114.5782 | 0.009156 | 123.1796 | 123.2529 | 8.6746 | -0.077819 | 107.103 | 106.8695 | 106.8054 | -16.6489 | 123.3261 | 123.2391 | 123.2849 | -8.7387
2856.5312 | 123.3948 | -105.9586 | 17.3859 | -0.21667 | 0.013313 | 0.0058491 | 0.013676 | -0.017417 | -0.0023648 | -0.00043792 | -0.019608 | 0.020448 | -0.010218 | 0.011854 | -0.0031446 | 0.010211 | 0.97504 | 1.0483 | 0.93384 | 1.0345 | 1.1902 | 0.9613 | 0.78278 | 17.2623 | 17.3538 | 17.3447 | 17.3859 | 17.3447 | 8.7753 | 8.6746 | 106.9199 | 106.7413 | -16.1957 | 107.0068 | 106.9931 | 0.25177 | -16.4108 | 114.7339 | 114.6332 | 0 | 123.2208 | 123.3032 | 8.67 | -0.041198 | 107.1487 | 106.9336 | 106.8924 | -16.6031 | 123.3444 | 123.3032 | 123.3124 | -8.7112
2857.5156 | 123.3948 | -106.0135 | 17.3126 | -0.010681 | 0.019935 | 0.0037127 | 0.013035 | -0.020194 | 0.0055392 | 0.0029801 | 0.041427 | 0.02173 | -0.0076542 | 0.012281 | -0.0031446 | 0.0080749 | 0.99335 | 1.0208 | 0.90637 | 1.0117 | 1.181 | 0.93384 | 0.77362 | 17.2165 | 17.2897 | 17.2485 | 17.308 | 17.2806 | 8.7753 | 8.67 | 106.9473 | 106.7871 | -16.1316 | 107.0343 | 107.0251 | 0.23804 | -16.3193 | 114.7888 | 114.6835 | -0.004578 | 123.23 | 123.262 | 8.5785 | -0.032043 | 107.1945 | 107.0068 | 106.9199 | -16.539 | 123.3215 | 123.2941 | 123.3032 | -8.6426
2858.5156 | 123.4314 | -106.0593 | 17.2668 | -0.14801 | 0.020363 | 0.0039263 | 0.014744 | -0.019766 | 0.0021214 | 0.0025529 | -0.17983 | 0.020448 | -0.010645 | 0.013136 | -0.0033582 | 0.0095703 | 0.98877 | 1.0391 | 0.91553 | 1.0208 | 1.1856 | 0.92926 | 0.75531 | 17.1982 | 17.2989 | 17.2531 | 17.2577 | 17.2119 | 8.7845 | 8.6746 | 106.9885 | 106.8146 | -16.0812 | 107.0984 | 107.0801 | 0.2655 | -16.2781 | 114.8438 | 114.7339 | -0.009156 | 123.2574 | 123.3124 | 8.5785 | -0.054932 | 107.2449 | 107.048 | 106.9748 | -16.5115 | 123.317 | 123.2712 | 123.3582 | -8.5922
2859.5156 | 123.4177 | -106.073 | 17.2485 | -0.048828 | 0.019295 | -0.00034611 | 0.015812 | -0.020407 | 0.0014804 | 0.00020288 | -0.088272 | 0.022584 | -0.0089358 | 0.015272 | -0.0033582 | 0.0072205 | 1.0437 | 1.0712 | 0.94757 | 1.0345 | 1.2451 | 0.98419 | 0.83771 | 17.1844 | 17.2806 | 17.2073 | 17.2211 | 17.1799 | 8.7753 | 8.6746 | 107.0572 | 106.9107 | -16.0034 | 107.1442 | 107.1075 | 0.19684 | -16.2048 | 114.8483 | 114.7476 | -0.027466 | 123.2574 | 123.2803 | 8.5327 | -0.068664 | 107.3181 | 107.1167 | 107.0206 | -16.4108 | 123.2941 | 123.2529 | 123.3536 | -8.5739
2860.5156 | 123.3856 | -106.1325 | 17.2211 | -0.2243 | 0.014168 | 0.0024311 | 0.014103 | -0.019766 | -0.001083 | -0.0010787 | -0.23323 | 0.022371 | -0.010218 | 0.012922 | -0.0037854 | 0.012134 | 1.1581 | 1.1581 | 0.90179 | 0.92926 | 1.2497 | 0.96588 | 0.80109 | 17.0792 | 17.157 | 17.1478 | 17.2073 | 17.1707 | 8.7845 | 8.6746 | 107.0984 | 106.9336 | -15.9714 | 107.2906 | 107.0618 | 0.12817 | -16.0629 | 114.917 | 114.8071 | -0.013733 | 123.2117 | 123.2803 | 8.4732 | -0.050354 | 107.3822 | 107.2906 | 107.0343 | -16.42 | 123.3398 | 123.3032 | 123.2895 | -8.5464
2861.5156 | 123.4177 | -106.1508 | 17.1478 | -1.3611 | 0.020149 | 0.00029489 | 0.014103 | -0.018057 | 0.0010532 | 0.0040481 | -0.0043486 | 0.023225 | -0.0097904 | 0.011427 | 0.00048697 | 0.0091431 | 1.0254 | 1.0712 | 0.93384 | 1.0437 | 1.2131 | 0.97961 | 0.80109 | 17.0837 | 17.1661 | 17.1204 | 17.1524 | 17.0883 | 8.7753 | 8.6746 | 107.1304 | 106.9519 | -15.9348 | 107.222 | 107.1945 | 0.24262 | -16.1224 | 114.9261 | 114.8254 | 0.004578 | 123.2346 | 123.2712 | 8.4457 | -0.059509 | 107.3639 | 107.1762 | 107.0847 | -16.3467 | 123.3032 | 123.2391 | 123.317 | -8.4732
2862.5156 | 123.3765 | -106.2057 | 17.157 | -0.19379 | 0.014808 | 0.0054217 | 0.014103 | -0.019766 | -0.0021512 | -0.0017197 | -0.16457 | 0.020448 | -0.0091494 | 0.012281 | -0.0052808 | 0.010211 | 1.2268 | 0.88806 | 0.8194 | 0.98877 | 1.2451 | 0.96588 | 0.78735 | 17.0013 | 17.0837 | 17.0609 | 17.1524 | 17.0792 | 8.7753 | 8.67 | 107.1716 | 106.9931 | -15.9119 | 107.0938 | 107.1945 | 0.20142 | -15.9302 | 114.9811 | 114.8758 | -0.004577 | 123.2071 | 123.2666 | 8.3908 | -0.077819 | 107.4509 | 107.4326 | 107.0251 | -16.3696 | 123.3582 | 123.2849 | 123.2895 | -8.4869
2863.5156 | 123.4222 | -106.2653 | 17.0609 | -0.16327 | 0.018013 | 0.0030719 | 0.018803 | -0.019553 | 0.0048984 | 0.0023391 | -0.11116 | 0.022371 | -0.0078678 | 0.009504 | -0.0010082 | 0.010211 | 0.97961 | 1.0345 | 0.9201 | 1.0437 | 1.1765 | 0.93384 | 0.75989 | 17.0197 | 17.1112 | 17.0609 | 17.0883 | 17.0242 | 8.7799 | 8.6792 | 107.1991 | 107.0251 | -15.8844 | 107.2998 | 107.309 | 0.28381 | -16.0812 | 115.0452 | 114.9445 | 0.027466 | 123.2849 | 123.3261 | 8.3817 | -0.036621 | 107.4417 | 107.2449 | 107.1854 | -16.301 | 123.3536 | 123.2895 | 123.3765 | -8.3817
2864.5156 | 123.5001 | -106.2469 | 16.9922 | 0.24109 | 0.016517 | 0.0026447 | 0.012608 | -0.018698 | -0.0015102 | 0.0019119 | 1.8801 | 0.02173 | -0.010218 | 0.010999 | -0.00229 | 0.011066 | 1.0437 | 1.0941 | 0.98877 | 1.0666 | 1.1536 | 0.97961 | 0.8194 | 17.0059 | 17.1341 | 17.0792 | 16.9739 | 16.951 | 8.7845 | 8.6792 | 107.2266 | 107.0663 | -15.8386 | 107.341 | 107.3135 | 0.24719 | -15.9485 | 115.0314 | 114.9261 | -0.01831 | 123.2529 | 123.3261 | 8.4 | -0.041198 | 107.4005 | 107.2906 | 107.2357 | -16.1728 | 123.2208 | 123.1979 | 123.381 | -8.313
2865.5156 | 123.4039 | -106.3293 | 17.0151 | 0.10376 | 0.018867 | 0.0013629 | 0.013676 | -0.018698 | 0.0012668 | 0.0025529 | 0.11772 | 0.025148 | -0.0078678 | 0.011427 | -0.00015383 | 0.012561 | 0.92468 | 0.93384 | 0.85602 | 0.97046 | 1.1902 | 0.92468 | 0.76904 | 16.9327 | 16.6672 | 17.1616 | 17.0059 | 16.983 | 8.7753 | 8.6792 | 107.254 | 107.0984 | -15.8249 | 107.2632 | 107.2998 | 0.20142 | -16.0904 | 115.1047 | 115.0085 | -0.009156 | 123.262 | 123.4909 | 8.4824 | -0.032044 | 107.5195 | 107.254 | 107.1854 | -16.246 | 123.3353 | 123.3124 | 122.9965 | -8.3359
2866.5156 | 123.4085 | -106.3522 | 16.9647 | -0.094604 | 0.018867 | 0.0026447 | 0.014103 | -0.019339 | 0.0027622 | 0.0036209 | -0.011978 | 0.022157 | -0.0074404 | 0.0099314 | -0.0027172 | 0.010852 | 1.0254 | 1.0345 | 0.90179 | 1.0162 | 1.1719 | 0.94757 | 0.78735 | 16.9006 | 16.9739 | 16.9235 | 16.9785 | 16.9281 | 8.7845 | 8.6746 | 107.2998 | 107.1396 | -15.7928 | 107.3868 | 107.3685 | 0.22888 | -15.9393 | 115.1367 | 115.0269 | 0.013733 | 123.2529 | 123.2758 | 8.2489 | -0.036621 | 107.5241 | 107.3776 | 107.254 | -16.1774 | 123.3307 | 123.2803 | 123.3261 | -8.2901
2867.5156 | 123.381 | -106.4117 | 16.9052 | 0.057983 | 0.021431 | 0.0028583 | 0.013676 | -0.019126 | 0.0048984 | 0.0023391 | -0.019608 | 0.024507 | -0.0085086 | 0.011213 | -0.00229 | 0.0095703 | 0.9613 | 0.95673 | 0.86975 | 0.98419 | 1.1719 | 0.93384 | 0.75073 | 16.8137 | 16.8823 | 16.8274 | 16.9327 | 16.8777 | 8.7708 | 8.6746 | 107.3456 | 107.1625 | -15.7333 | 107.3685 | 107.3959 | 0.23346 | -15.9439 | 115.1825 | 115.0864 | 0.027466 | 123.2254 | 123.2391 | 8.1528 | -0.027465 | 107.5836 | 107.373 | 107.2815 | -16.1545 | 123.3444 | 123.2895 | 123.2941 | -8.2306
2868.5156 | 123.436 | -106.4072 | 16.9464 | -0.11749 | 0.018867 | 0.0020037 | 0.016881 | -0.01763 | 0.0012668 | 0.0021255 | -0.034867 | 0.022584 | -0.011713 | 0.012281 | -0.0016492 | 0.011493 | 0.99792 | 1.0254 | 0.9201 | 1.0162 | 1.1581 | 0.9201 | 0.75531 | 16.832 | 16.9281 | 16.8549 | 16.8869 | 16.8686 | 8.7799 | 8.6655 | 107.3273 | 107.1625 | -15.7883 | 107.4326 | 107.4234 | 0.26092 | -15.9485 | 115.1871 | 115.0726 | -0.059509 | 123.2391 | 123.262 | 8.1894 | -0.07782 | 107.5653 | 107.4051 | 107.3273 | -16.1911 | 123.2941 | 123.2758 | 123.3353 | -8.2809
2869.5156 | 123.5229 | -106.4117 | 16.8137 | 0.2182 | 0.016304 | 0.0028583 | 0.010045 | -0.019339 | -0.0030056 | 0.0036209 | 0.41527 | 0.022798 | -0.013636 | 0.009504 | -0.0029308 | 0.010852 | 0.74616 | 1.0574 | 1.0345 | 1.1078 | 1.0803 | 0.91553 | 0.737 | 16.8503 | 16.9327 | 16.9327 | 16.832 | 16.7725 | 8.7799 | 8.6792 | 107.3273 | 107.1487 | -15.7333 | 107.4692 | 107.5195 | 0.37079 | -16.0675 | 115.1916 | 115.0909 | 0.01831 | 123.262 | 123.3444 | 8.2535 | -0.041199 | 107.4921 | 107.1579 | 107.4463 | -16.0767 | 123.2437 | 123.1842 | 123.3444 | -8.1345
2870.5156 | 123.4222 | -106.4804 | 16.8411 | -0.14038 | 0.020576 | 0.0041401 | 0.015172 | -0.018057 | 0.0031894 | 0.0038345 | -0.027237 | 0.021302 | -0.010004 | 0.011213 | -0.0016492 | 0.0087157 | 1.0208 | 1.0117 | 0.90637 | 1.0071 | 1.1856 | 0.9201 | 0.737 | 16.8823 | 16.7908 | 16.8777 | 16.8594 | 16.8137 | 8.7799 | 8.6838 | 107.4005 | 107.2174 | -15.6555 | 107.4921 | 107.4875 | 0.27008 | -15.8203 | 115.2603 | 115.1642 | 0.018311 | 123.3627 | 123.3582 | 8.194 | -0.027465 | 107.666 | 107.5012 | 107.3868 | -16.1041 | 123.3398 | 123.2941 | 123.2712 | -8.1573
2871.5156 | 123.3673 | -106.5491 | 16.7816 | 0.073242 | 0.018226 | 0.0020037 | 0.013463 | -0.018271 | 0.002335 | 0.0023391 | 0.064316 | 0.023225 | -0.010858 | 0.010145 | -0.0016492 | 0.0091431 | 0.94757 | 0.95673 | 0.85144 | 0.97504 | 1.1581 | 0.9201 | 0.72327 | 16.6397 | 16.7038 | 16.6763 | 16.7816 | 16.7267 | 8.7708 | 8.67 | 107.4692 | 107.2723 | -15.6235 | 107.5058 | 107.5241 | 0.25177 | -15.834 | 115.3198 | 115.2191 | 0 | 123.1888 | 123.2254 | 8.0063 | -0.054931 | 107.7072 | 107.4966 | 107.4005 | -16.0583 | 123.3307 | 123.2758 | 123.2529 | -8.1116
2872.5156 | 123.4085 | -106.5811 | 16.7358 | -0.041199 | 0.018654 | 0.0017901 | 0.014958 | -0.01763 | 0.001694 | 0.0025529 | 0.01091 | 0.023866 | -0.0080814 | 0.012281 | -0.00079463 | 0.0093567 | 0.97504 | 0.99792 | 0.89264 | 1.0025 | 1.149 | 0.92468 | 0.74616 | 16.6534 | 16.7358 | 16.6946 | 16.7633 | 16.7038 | 8.7753 | 8.6746 | 107.5058 | 107.3273 | -15.5869 | 107.579 | 107.5836 | 0.25635 | -15.7608 | 115.3564 | 115.2557 | 0.027466 | 123.2346 | 123.2758 | 8.02 | -0.032044 | 107.7301 | 107.5562 | 107.4738 | -15.9897 | 123.3444 | 123.2849 | 123.317 | -8.0612
2873.5156 | 123.5092 | -106.5811 | 16.6443 | 0.24109 | 0.015877 | 0.0015765 | 0.013035 | -0.01998 | 0.00019875 | 0.0019119 | 0.1635 | 0.021302 | -0.0078678 | 0.012922 | -0.00229 | 0.011493 | 1.0117 | 1.0437 | 0.94299 | 1.0345 | 1.1353 | 0.95673 | 0.76446 | 16.6901 | 16.7679 | 16.7541 | 16.6763 | 16.6351 | 8.7799 | 8.67 | 107.5378 | 107.3456 | -15.509 | 107.6248 | 107.6157 | 0.27008 | -15.6326 | 115.361 | 115.2512 | 0.032044 | 123.2712 | 123.3353 | 8.0841 | -0.009155 | 107.7164 | 107.5928 | 107.5241 | -15.8798 | 123.2574 | 123.2162 | 123.349 | -7.9742
2874.5156 | 123.5001 | -106.5994 | 16.6534 | 0.36316 | 0.015236 | 0.0022175 | 0.010685 | -0.018057 | -0.0025784 | -0.00043792 | 0.25505 | 0.023225 | -0.012567 | 0.010999 | -0.0037854 | 0.0099975 | 1.0437 | 1.0666 | 0.97961 | 1.0529 | 1.1032 | 0.94299 | 0.78278 | 16.6763 | 16.7496 | 16.7404 | 16.6534 | 16.5985 | 8.7753 | 8.67 | 107.5424 | 107.3822 | -15.5502 | 107.666 | 107.6523 | 0.27008 | -15.6097 | 115.3748 | 115.2695 | 0 | 123.2758 | 123.3398 | 8.0704 | -0.054931 | 107.7026 | 107.6431 | 107.579 | -15.8707 | 123.2529 | 123.1979 | 123.349 | -7.9834
2875.5156 | 123.3856 | -106.691 | 16.6534 | 0.24872 | 0.023994 | 0.0011493 | 0.020298 | -0.019766 | 0.0031894 | 0.0014847 | 0.094833 | 0.021943 | -0.008295 | 0.011854 | -0.0014356 | 0.010638 | 0.9201 | 0.97046 | 0.84228 | 0.96588 | 1.1856 | 0.94299 | 0.75531 | 16.539 | 16.5665 | 16.5527 | 16.6489 | 16.5939 | 8.7708 | 8.6655 | 107.634 | 107.4463 | -15.4678 | 107.6614 | 107.6569 | 0.21057 | -15.7333 | 115.4617 | 115.3564 | -0.004577 | 123.23 | 123.2437 | 7.8873 | -0.059509 | 107.8766 | 107.6111 | 107.5333 | -15.8981 | 123.3398 | 123.2849 | 123.2574 | -7.988
2876.5156 | 123.4497 | -106.7139 | 16.5802 | 0.2182 | 0.018867 | 0.0017901 | 0.014531 | -0.019126 | 0.001694 | 0.0010575 | 0.2169 | 0.022798 | -0.0095768 | 0.011427 | -0.0020764 | 0.010638 | 0.95673 | 0.94757 | 0.86975 | 0.97046 | 1.1627 | 0.90179 | 0.74158 | 16.5344 | 16.5848 | 16.5619 | 16.5848 | 16.5436 | 8.7662 | 8.6792 | 107.6157 | 107.4554 | -15.4175 | 107.6614 | 107.6843 | 0.22888 | -15.6235 | 115.48 | 115.3931 | 0.004578 | 123.2483 | 123.2758 | 7.8827 | -0.036621 | 107.8766 | 107.6706 | 107.5836 | -15.8386 | 123.2986 | 123.2574 | 123.2986 | -7.901
2877.5156 | 123.3673 | -106.7871 | 16.5527 | 0.019836 | 0.018867 | 0.0015765 | 0.01389 | -0.018485 | 0.0019078 | 0.0034073 | 0.13298 | 0.020448 | -0.0080814 | 0.012708 | -0.0020764 | 0.0089295 | 0.92468 | 0.90179 | 0.83771 | 0.95673 | 1.1444 | 0.89264 | 0.71869 | 16.42 | 16.4841 | 16.4337 | 16.571 | 16.5207 | 8.7708 | 8.67 | 107.6797 | 107.5058 | -15.4083 | 107.6889 | 107.7438 | 0.23804 | -15.6281 | 115.5579 | 115.4572 | 0.018311 | 123.2071 | 123.2208 | 7.7637 | -0.032043 | 107.9315 | 107.7118 | 107.6248 | -15.834 | 123.3582 | 123.3078 | 123.2712 | -7.8827
2878.5156 | 123.3765 | -106.8008 | 16.4841 | -0.0030518 | 0.020149 | 0.00093569 | 0.01389 | -0.018698 | 0.0010532 | 0.0029801 | 0.049057 | 0.024293 | -0.011072 | 0.013349 | -0.0012218 | 0.0093567 | 0.97961 | 0.9613 | 0.87433 | 0.98419 | 1.1444 | 0.91553 | 0.73242 | 16.4154 | 16.4932 | 16.4154 | 16.5161 | 16.4795 | 8.7799 | 8.6746 | 107.7164 | 107.5333 | -15.3397 | 107.7621 | 107.785 | 0.25177 | -15.5045 | 115.5807 | 115.4755 | 0.032043 | 123.2162 | 123.2162 | 7.7408 | -0.004578 | 107.9453 | 107.7805 | 107.6752 | -15.7516 | 123.317 | 123.2803 | 123.2941 | -7.8094
2879.5156 | 123.4589 | -106.8054 | 16.452 | 0.14954 | 0.015022 | 0.0049945 | 0.011326 | -0.020835 | -0.0051418 | 0.00020288 | 0.27794 | 0.020021 | -0.011927 | 0.012708 | -0.0035718 | 0.011707 | 1.0162 | 1.0712 | 0.96588 | 1.0162 | 1.1169 | 0.93842 | 0.78735 | 16.4337 | 16.5115 | 16.4978 | 16.452 | 16.4108 | 8.7753 | 8.6655 | 107.7438 | 107.5928 | -15.3351 | 107.8766 | 107.8217 | 0.22888 | -15.4358 | 115.5807 | 115.4709 | 0 | 123.2391 | 123.3032 | 7.8323 | -0.041198 | 107.9224 | 107.8217 | 107.7713 | -15.6647 | 123.2574 | 123.2162 | 123.317 | -7.7866
2880.5156 | 123.4177 | -106.9107 | 16.42 | -0.048828 | 0.021004 | 0.0017901 | 0.015385 | -0.019766 | 0.003403 | -1.0724e-05 | 0.1635 | 0.023011 | -0.0080814 | 0.012068 | -0.00079463 | 0.0072205 | 0.94299 | 0.91095 | 0.8194 | 0.9613 | 1.1581 | 0.89264 | 0.71869 | 16.3239 | 16.3651 | 16.3605 | 16.4383 | 16.3879 | 8.7753 | 8.6746 | 107.8033 | 107.6294 | -15.2618 | 107.8217 | 107.872 | 0.24262 | -15.477 | 115.686 | 115.5853 | 0.01831 | 123.2346 | 123.2712 | 7.6859 | -0.032044 | 108.0688 | 107.8537 | 107.7301 | -15.7013 | 123.349 | 123.2986 | 123.2758 | -7.7454
2881.5156 | 123.4909 | -106.8649 | 16.3834 | 0.22583 | 0.016517 | 0.0030719 | 0.01389 | -0.018057 | -0.0021512 | 0.0019119 | 0.27031 | 0.019807 | -0.012781 | 0.012922 | -0.00036743 | 0.0093567 | 1.03 | 1.0757 | 0.9613 | 1.0345 | 1.1307 | 0.93384 | 0.76446 | 16.4062 | 16.4703 | 16.4612 | 16.3742 | 16.3147 | 8.7845 | 8.6746 | 107.7988 | 107.6294 | -15.2527 | 107.9407 | 107.8995 | 0.27008 | -15.3534 | 115.6494 | 115.5396 | -0.009155 | 123.2712 | 123.3261 | 7.7866 | -0.068665 | 107.9956 | 107.8949 | 107.8262 | -15.6189 | 123.2391 | 123.1796 | 123.3353 | -7.7087
2882.5156 | 123.4131 | -106.9702 | 16.3422 | 0.16479 | 0.019295 | 0.0037127 | 0.015599 | -0.023184 | 0.003403 | 0.0029801 | 0.15587 | 0.022371 | -0.0089358 | 0.012068 | 0.00027337 | 0.0097839 | 0.94299 | 0.90637 | 0.82398 | 0.95215 | 1.149 | 0.87891 | 0.737 | 16.2643 | 16.2964 | 16.2872 | 16.3651 | 16.3193 | 8.7753 | 8.6655 | 107.8491 | 107.7072 | -15.1932 | 107.8766 | 107.9224 | 0.21515 | -15.3992 | 115.7455 | 115.6357 | 0.022888 | 123.2346 | 123.2574 | 7.6218 | -0.022888 | 108.1192 | 107.9132 | 107.7942 | -15.6052 | 123.3353 | 123.2895 | 123.2666 | -7.6767
2883.5156 | 123.4818 | -106.9611 | 16.3101 | 0.19531 | 0.017586 | 0.0032855 | 0.013676 | -0.021475 | 0.0021214 | 0.0012711 | 0.19402 | 0.020662 | -0.011286 | 0.010999 | -0.0035718 | 0.0097839 | 0.97504 | 0.96588 | 0.88348 | 0.97046 | 1.1307 | 0.91095 | 0.737 | 16.3193 | 16.3559 | 16.3513 | 16.3055 | 16.2598 | 8.7753 | 8.67 | 107.872 | 107.6981 | -15.1794 | 107.9269 | 107.9315 | 0.23346 | -15.3351 | 115.7364 | 115.6311 | -0.004578 | 123.2803 | 123.3124 | 7.6813 | -0.050354 | 108.0917 | 107.9361 | 107.8445 | -15.5731 | 123.2666 | 123.2208 | 123.317 | -7.6401
2884.5312 | 123.5138 | -106.9885 | 16.2598 | -1.3916 | 0.01075 | 0.0037127 | 0.011113 | -0.020835 | -0.001083 | 0.0027665 | -0.011978 | 0.018312 | -0.014063 | 0.010572 | -0.0044262 | 0.010211 | 0.99335 | 1.1124 | 0.98877 | 1.0345 | 1.1215 | 0.91553 | 0.75531 | 16.2872 | 16.3971 | 16.3605 | 16.2506 | 16.2231 | 8.7799 | 8.6792 | 107.9041 | 107.7438 | -15.1382 | 108.1009 | 108.0231 | 0.27924 | -15.2664 | 115.7684 | 115.6677 | -0.009156 | 123.2758 | 123.349 | 7.6813 | -0.036621 | 108.11 | 107.9819 | 107.9773 | -15.5045 | 123.2391 | 123.2117 | 123.3856 | -7.5806
2885.5156 | 123.5001 | -107.016 | 16.2048 | 0.20294 | 0.013527 | 0.0024311 | 0.011967 | -0.019766 | 0.00019875 | 0.0010575 | 0.48393 | 0.02173 | -0.012781 | 0.010359 | -0.0014356 | 0.010638 | 1.03 | 1.0483 | 0.96588 | 0.91553 | 1.0941 | 0.93384 | 0.75073 | 16.2506 | 16.3376 | 16.2735 | 16.2048 | 16.1453 | 8.7753 | 8.6792 | 107.9498 | 107.7667 | -15.1108 | 108.0643 | 107.9315 | 0.1648 | -15.1749 | 115.7913 | 115.6952 | 0 | 123.2666 | 123.2895 | 7.5943 | -0.059509 | 108.11 | 108.046 | 107.9819 | -15.4541 | 123.2208 | 123.1613 | 123.3536 | -7.5256
2886.5156 | 123.5001 | -107.0709 | 16.1728 | 0.20294 | 0.018226 | 0.0024311 | 0.016881 | -0.018271 | 0.00041235 | 0.0010575 | 0.14824 | 0.020448 | -0.010004 | 0.010786 | -0.0016492 | 0.0097839 | 1.0391 | 1.0391 | 0.95673 | 1.0345 | 1.0803 | 0.9201 | 0.75989 | 16.214 | 16.2872 | 16.2552 | 16.1957 | 16.1224 | 8.7799 | 8.67 | 107.991 | 107.8308 | -15.0925 | 108.11 | 108.1055 | 0.27466 | -15.1337 | 115.8508 | 115.741 | 0.022888 | 123.2849 | 123.3261 | 7.5851 | -0.050354 | 108.1512 | 108.11 | 108.0276 | -15.4129 | 123.2666 | 123.1934 | 123.3582 | -7.5027
2887.5156 | 123.4909 | -107.1396 | 16.1179 | 0.16479 | 0.016517 | 0.0017901 | 0.011967 | -0.019126 | 0.0010532 | 0.00063028 | 0.20927 | 0.02173 | -0.0080814 | 0.011854 | -0.0016492 | 0.0082885 | 0.99335 | 0.96588 | 0.87433 | 0.97046 | 1.1307 | 0.90179 | 0.737 | 16.1499 | 16.1957 | 16.1682 | 16.1545 | 16.1041 | 8.7845 | 8.67 | 108.0414 | 107.8766 | -14.9872 | 108.1055 | 108.11 | 0.23346 | -15.1245 | 115.9241 | 115.8096 | 0.036621 | 123.2895 | 123.3078 | 7.4982 | -0.013733 | 108.2703 | 108.1329 | 108.0139 | -15.3809 | 123.2941 | 123.2437 | 123.3353 | -7.4478
2888.5156 | 123.4863 | -107.1442 | 16.1224 | 0.20294 | 0.019508 | 0.0017901 | 0.013463 | -0.018912 | 0.0014804 | 0.0040481 | 0.1635 | 0.021089 | -0.0072268 | 0.012922 | -0.00058103 | 0.0076477 | 0.98419 | 0.94757 | 0.87891 | 0.9613 | 1.1215 | 0.90179 | 0.74158 | 16.1179 | 16.1591 | 16.1316 | 16.1179 | 16.0721 | 8.7799 | 8.6746 | 108.046 | 107.8857 | -15.0009 | 108.0917 | 108.1055 | 0.21973 | -15.1382 | 115.9241 | 115.8188 | -0.004578 | 123.262 | 123.2758 | 7.457 | -0.050354 | 108.2657 | 108.1284 | 108.0231 | -15.3809 | 123.262 | 123.2162 | 123.3032 | -7.4478
2889.5156 | 123.4818 | -107.1991 | 16.095 | 0.21057 | 0.019508 | 0.0020037 | 0.014103 | -0.018912 | 0.00083955 | 0.0027665 | 0.20927 | 0.022157 | -0.010431 | 0.010786 | -0.0020764 | 0.0099975 | 0.97046 | 0.95215 | 0.87433 | 0.94757 | 1.1307 | 0.89722 | 0.71869 | 16.1041 | 16.1087 | 16.0904 | 16.0858 | 16.0538 | 8.7708 | 8.6792 | 108.0963 | 107.9178 | -14.9643 | 108.1512 | 108.1467 | 0.22888 | -15.1245 | 115.9698 | 115.8783 | -0.009156 | 123.3032 | 123.2895 | 7.4112 | -0.041199 | 108.3298 | 108.1696 | 108.0734 | -15.3763 | 123.2849 | 123.2529 | 123.3078 | -7.4158
2890.5156 | 123.4818 | -107.1945 | 16.0629 | 0.24872 | 0.017586 | 0.00050849 | 0.014317 | -0.018057 | -0.00022865 | 0.0014847 | 0.2169 | 0.020875 | -0.0085086 | 0.0099314 | -0.00079463 | 0.0089295 | 0.95673 | 0.95673 | 0.87433 | 0.97046 | 1.1215 | 0.90637 | 0.72327 | 16.0584 | 16.095 | 16.0767 | 16.0629 | 16.0263 | 8.7753 | 8.67 | 108.1009 | 107.9178 | -14.9414 | 108.1512 | 108.165 | 0.24719 | -15.1062 | 115.9698 | 115.8646 | 0 | 123.2529 | 123.2712 | 7.4066 | -0.036621 | 108.316 | 108.1512 | 108.0688 | -15.3397 | 123.2574 | 123.2208 | 123.2895 | -7.3929
2891.5156 | 123.3902 | -107.254 | 16.0858 | -0.17853 | 0.012672 | 0.0054217 | 0.009831 | -0.019126 | -0.0030056 | 0.0025529 | -0.15694 | 0.020875 | -0.012567 | 0.012068 | -0.0035718 | 0.011707 | 0.97504 | 1.0254 | 0.91095 | 0.98877 | 1.1307 | 0.91095 | 0.72784 | 15.9851 | 16.0812 | 16.0263 | 16.0812 | 16.0263 | 8.7753 | 8.6655 | 108.165 | 107.9819 | -14.9551 | 108.2794 | 108.2428 | 0.26093 | -15.1108 | 116.0294 | 115.9195 | -0.004577 | 123.2391 | 123.2803 | 7.3608 | -0.059509 | 108.3847 | 108.2291 | 108.165 | -15.358 | 123.3353 | 123.2803 | 123.3353 | -7.4203
2892.5156 | 123.3765 | -107.3135 | 16.0355 | 1.004 | 0.016945 | 0.0043537 | 0.01389 | -0.01763 | 0.0021214 | 0.0023391 | 0.14061 | 0.022584 | -0.0089358 | 0.010786 | -0.0012218 | 0.0099975 | 0.95673 | 0.89264 | 0.80566 | 0.92926 | 1.149 | 0.90179 | 0.71869 | 15.9164 | 15.9576 | 15.9439 | 16.0217 | 15.976 | 8.7708 | 8.6655 | 108.2153 | 108.0322 | -14.8865 | 108.2062 | 108.2428 | 0.21057 | -15.0787 | 116.0843 | 115.979 | -0.013732 | 123.23 | 123.2574 | 7.2784 | -0.059509 | 108.4625 | 108.2703 | 108.1192 | -15.3168 | 123.3353 | 123.2895 | 123.2712 | -7.37
2893.5156 | 123.468 | -107.3044 | 15.9485 | 0.18768 | 0.015877 | 0.0028583 | 0.013035 | -0.021262 | -0.0019376 | 0.00063028 | 0.26268 | 0.020448 | -0.011499 | 0.012068 | -0.0050672 | 0.011279 | 1.0117 | 1.0574 | 0.95673 | 1.0071 | 1.1124 | 0.93842 | 0.76446 | 15.9714 | 16.0217 | 16.008 | 15.9393 | 15.9073 | 8.7799 | 8.67 | 108.2428 | 108.0688 | -14.8361 | 108.3618 | 108.3115 | 0.24262 | -14.9368 | 116.0843 | 115.9744 | -0.009155 | 123.2758 | 123.3124 | 7.338 | -0.041198 | 108.4167 | 108.316 | 108.2611 | -15.184 | 123.2437 | 123.2117 | 123.3261 | -7.2784
2894.5156 | 123.4406 | -107.3685 | 15.9393 | 0.17242 | 0.020363 | 0.0011493 | 0.014531 | -0.018485 | 0.0014804 | 0.0025529 | 0.20164 | 0.022798 | -0.0076542 | 0.011213 | -0.0012218 | 0.0091431 | 0.94757 | 0.9201 | 0.84228 | 0.92468 | 1.1398 | 0.88348 | 0.68665 | 15.889 | 15.9256 | 15.8981 | 15.9439 | 15.889 | 8.7753 | 8.6792 | 108.252 | 108.0551 | -14.7995 | 108.2886 | 108.2932 | 0.23804 | -14.9918 | 116.1438 | 116.0477 | 0.004578 | 123.2574 | 123.2666 | 7.2189 | -0.050354 | 108.5083 | 108.316 | 108.2108 | -15.2527 | 123.3124 | 123.2574 | 123.2941 | -7.2601
2895.5156 | 123.5184 | -107.3685 | 15.8661 | 0.51575 | 0.013527 | 0.0043537 | 0.010685 | -0.018271 | -0.0012966 | 0.0010575 | 0.20927 | 0.02173 | -0.010431 | 0.0099314 | -0.00229 | 0.0087157 | 1.03 | 1.0162 | 0.94757 | 1.0208 | 1.0529 | 0.88348 | 0.71869 | 15.921 | 15.9897 | 15.9714 | 15.8569 | 15.834 | 8.7753 | 8.67 | 108.252 | 108.0872 | -14.8132 | 108.3847 | 108.3893 | 0.30212 | -14.8361 | 116.1438 | 116.0385 | -0.009155 | 123.2895 | 123.3398 | 7.3013 | -0.032044 | 108.4213 | 108.3984 | 108.316 | -15.1474 | 123.2254 | 123.2025 | 123.3582 | -7.196
2896.5156 | 123.4772 | -107.4142 | 15.8524 | 0.15717 | 0.012245 | 0.0032855 | 0.009831 | -0.019766 | -0.0036464 | 0.0016983 | 0.20927 | 0.021089 | -0.012995 | 0.0092904 | -0.0018628 | 0.010852 | 0.96588 | 1.0208 | 0.91095 | 0.96588 | 1.1124 | 0.9201 | 0.737 | 15.8386 | 15.9027 | 15.8981 | 15.8478 | 15.7974 | 8.7662 | 8.67 | 108.3344 | 108.1512 | -14.74 | 108.4351 | 108.3801 | 0.22888 | -14.8865 | 116.1804 | 116.0843 | -0.004578 | 123.2529 | 123.3124 | 7.2281 | -0.054932 | 108.5266 | 108.3801 | 108.3252 | -15.1154 | 123.262 | 123.2117 | 123.317 | -7.1823
2897.5156 | 123.4726 | -107.4371 | 15.8112 | 0.13428 | 0.011604 | 0.0032855 | 0.014103 | -0.021689 | -0.0015102 | -0.0017197 | 0.20927 | 0.018739 | -0.012995 | 0.011427 | -0.0012218 | 0.0089295 | 0.97046 | 1.0071 | 0.89722 | 0.97504 | 1.1032 | 0.90637 | 0.75073 | 15.8112 | 15.8661 | 15.8569 | 15.8295 | 15.7837 | 8.7708 | 8.6746 | 108.3435 | 108.1879 | -14.7079 | 108.4442 | 108.4122 | 0.22431 | -14.8407 | 116.2079 | 116.1118 | 0.018311 | 123.2483 | 123.2941 | 7.1823 | -0.027466 | 108.5403 | 108.4076 | 108.3344 | -15.0604 | 123.2666 | 123.2208 | 123.3032 | -7.1365
2898.5156 | 123.3719 | -107.5287 | 15.7883 | 0.27161 | 0.019508 | 0.0026447 | 0.014317 | -0.018912 | 0.0021214 | 0.0029801 | 0.087204 | 0.022371 | -0.010645 | 0.011854 | -0.00036743 | 0.0052979 | 0.94299 | 0.88348 | 0.80109 | 0.92926 | 1.1261 | 0.8606 | 0.71869 | 15.7333 | 15.7242 | 15.7196 | 15.8112 | 15.7425 | 8.7753 | 8.6792 | 108.3893 | 108.2474 | -14.6622 | 108.4122 | 108.4579 | 0.21057 | -14.8453 | 116.304 | 116.2079 | 0.022888 | 123.262 | 123.2483 | 7.0404 | -0.045776 | 108.6548 | 108.4717 | 108.3298 | -15.0696 | 123.3398 | 123.2712 | 123.2529 | -7.1091
2899.5156 | 123.4955 | -107.4738 | 15.7516 | 0.18768 | 0.011818 | 0.0017901 | 0.010472 | -0.015921 | -0.001083 | 0.00084388 | 0.22453 | 0.019593 | -0.011499 | 0.011213 | -0.003999 | 0.0089295 | 1.0117 | 1.0437 | 0.94299 | 1.0025 | 1.0895 | 0.90637 | 0.75073 | 15.7928 | 15.8478 | 15.8112 | 15.7425 | 15.6692 | 8.7799 | 8.6746 | 108.3801 | 108.2245 | -14.6622 | 108.5175 | 108.4763 | 0.25177 | -14.74 | 116.2537 | 116.1484 | -0.009155 | 123.2666 | 123.2849 | 7.1365 | -0.082398 | 108.5632 | 108.4854 | 108.4167 | -15.0009 | 123.2162 | 123.143 | 123.3215 | -7.077
2900.5156 | 123.4451 | -107.5424 | 15.7196 | 0.21057 | 0.018654 | 0.0026447 | 0.015172 | -0.020835 | 0.00062595 | 0.0010575 | 0.17113 | 0.02173 | -0.010645 | 0.010999 | 0.00048697 | 0.0085021 | 0.94299 | 0.90637 | 0.84228 | 0.92926 | 1.1124 | 0.88348 | 0.70038 | 15.6876 | 15.715 | 15.7104 | 15.715 | 15.6692 | 8.7753 | 8.6746 | 108.4259 | 108.2428 | -14.6072 | 108.4488 | 108.4717 | 0.22888 | -14.7766 | 116.3177 | 116.217 | -0.004577 | 123.23 | 123.2529 | 7.0358 | -0.050354 | 108.6548 | 108.4854 | 108.3847 | -15.0192 | 123.2574 | 123.2117 | 123.2574 | -7.045
2901.5156 | 123.5229 | -107.5699 | 15.6967 | 0.012207 | 0.013954 | -0.034312 | 0.011113 | -0.020407 | -0.0030056 | -1.0724e-05 | 0.018539 | 0.018525 | -0.01449 | 0.010786 | -0.0046398 | 0.010638 | 0.98419 | 1.0483 | 0.94757 | 0.99335 | 1.1078 | 0.90179 | 0.74616 | 15.7104 | 15.8066 | 15.7837 | 15.6921 | 15.6372 | 8.7799 | 8.6746 | 108.4717 | 108.316 | -14.5889 | 108.6182 | 108.5632 | 0.24719 | -14.7125 | 116.3498 | 116.2445 | -0.004577 | 123.2803 | 123.3536 | 7.1091 | -0.059509 | 108.6777 | 108.5541 | 108.5175 | -14.9506 | 123.262 | 123.2071 | 123.3765 | -7.0221
2902.5156 | 123.3994 | -107.6752 | 15.6555 | 0.13428 | 0.017158 | 0.0026447 | 0.014317 | -0.018485 | 0.0031894 | 0.0034073 | 0.14824 | 0.021516 | -0.012567 | 0.013136 | 5.9768e-05 | 0.0067931 | 0.92468 | 0.88806 | 0.81024 | 0.91553 | 1.1169 | 0.86975 | 0.69122 | 15.5823 | 15.6052 | 15.596 | 15.6738 | 15.5823 | 8.7753 | 8.6655 | 108.5449 | 108.3664 | -14.5386 | 108.5632 | 108.5907 | 0.2243 | -14.7308 | 116.4505 | 116.3406 | 0.01831 | 123.2574 | 123.2712 | 6.9305 | -0.073243 | 108.7921 | 108.5999 | 108.4854 | -14.9643 | 123.349 | 123.2574 | 123.2803 | -6.9901
2903.5156 | 123.5229 | -107.634 | 15.5914 | 0.2182 | 0.017586 | 0.00093569 | 0.0096174 | -0.020621 | 0.0021214 | 0.0031937 | 0.2169 | 0.020875 | -0.013208 | 0.010786 | -0.0020764 | 0.0082885 | 1.0071 | 1.0345 | 0.9201 | 0.98419 | 1.0849 | 0.91095 | 0.73242 | 15.7104 | 15.6464 | 15.6876 | 15.5823 | 15.5136 | 8.7799 | 8.67 | 108.5449 | 108.3664 | -14.5065 | 108.6685 | 108.6182 | 0.25177 | -14.5844 | 116.4139 | 116.304 | -0.009156 | 123.3444 | 123.3215 | 7.0175 | -0.07782 | 108.7189 | 108.6411 | 108.5541 | -14.859 | 123.2162 | 123.1476 | 123.2803 | -6.9214
2904.5156 | 123.4955 | -107.6477 | 15.5594 | -0.0030518 | 0.01609 | 0.0043537 | 0.015385 | -0.018057 | -0.00022865 | 0.0023391 | 0.23979 | 0.022157 | -0.0091494 | 0.011213 | -0.00229 | 0.011493 | 0.99335 | 1.0254 | 0.94299 | 0.99792 | 1.0666 | 0.91553 | 0.73242 | 15.6097 | 15.6692 | 15.6372 | 15.5548 | 15.5045 | 8.7799 | 8.6746 | 108.5632 | 108.3801 | -14.4928 | 108.6731 | 108.6456 | 0.2655 | -14.566 | 116.4276 | 116.3223 | -0.004577 | 123.2574 | 123.2849 | 6.9626 | -0.054931 | 108.7143 | 108.6411 | 108.5907 | -14.827 | 123.2025 | 123.1522 | 123.317 | -6.8848
2905.5156 | 123.5092 | -107.7209 | 15.5502 | 0.63019 | 0.014595 | 0.0047809 | 0.012822 | -0.01763 | -1.505e-05 | -1.0724e-05 | 0.19402 | 0.020021 | -0.0097904 | 0.011854 | -0.0018628 | 0.0087157 | 1.0071 | 1.0254 | 0.92926 | 0.99792 | 1.0529 | 0.87433 | 0.71411 | 15.5777 | 15.6326 | 15.6052 | 15.5136 | 15.477 | 8.7799 | 8.6746 | 108.5953 | 108.4351 | -14.4974 | 108.7463 | 108.7189 | 0.28381 | -14.5432 | 116.5009 | 116.3956 | -0.036621 | 123.2986 | 123.3261 | 6.9305 | -0.073242 | 108.7738 | 108.728 | 108.6502 | -14.8361 | 123.2346 | 123.1979 | 123.3536 | -6.8756
2906.5156 | 123.5138 | -107.7759 | 15.4816 | 0.21057 | 0.017586 | 0.0037127 | 0.013676 | -0.017844 | 0.0021214 | 0.0016983 | 0.071945 | 0.021302 | -0.0095768 | 0.011213 | -0.0010082 | 0.0085021 | 1.0757 | 0.65002 | 0.76446 | 1.0162 | 1.03 | 0.87433 | 0.70038 | 15.5319 | 15.596 | 15.5731 | 15.4953 | 15.4404 | 8.7799 | 8.6746 | 108.6502 | 108.4763 | -14.4516 | 108.4259 | 108.7921 | 0.31586 | -14.4058 | 116.5558 | 116.4505 | 0.013733 | 123.3078 | 123.349 | 6.8985 | -0.041198 | 108.8058 | 108.8516 | 108.5403 | -14.7812 | 123.2712 | 123.2162 | 123.3719 | -6.8069
2907.5156 | 123.5092 | -107.7896 | 15.4587 | 0.19531 | 0.01609 | 0.0043537 | 0.011113 | -0.015921 | 0.0019078 | 0.0029801 | 0.20164 | 0.020448 | -0.012781 | 0.011427 | -0.00036743 | 0.0089295 | 1.0117 | 1.0254 | 0.92468 | 1.0162 | 1.0757 | 0.87891 | 0.72784 | 15.4907 | 15.7333 | 15.509 | 15.4404 | 15.3854 | 8.7845 | 8.6746 | 108.6685 | 108.5175 | -14.3829 | 108.815 | 108.8058 | 0.28839 | -14.447 | 116.5741 | 116.4642 | -0.01831 | 123.2803 | 123.2986 | 6.8344 | -0.073242 | 108.8654 | 108.8013 | 108.7143 | -14.7308 | 123.23 | 123.175 | 123.5229 | -6.7841
2908.5156 | 123.3765 | -107.8583 | 15.4816 | 0.37079 | 0.023994 | 0.0022175 | 0.020298 | -0.020621 | 0.0044712 | 0.00084388 | 0.056686 | 0.022157 | -0.010218 | 0.013563 | -0.00079463 | 0.0089295 | 0.88348 | 0.90637 | 0.79193 | 0.91095 | 1.1124 | 0.85144 | 0.6958 | 15.3763 | 15.4037 | 15.3854 | 15.4724 | 15.4358 | 8.7753 | 8.67 | 108.7097 | 108.5541 | -14.3692 | 108.7646 | 108.7692 | 0.21515 | -14.5981 | 116.6336 | 116.5283 | -0.009155 | 123.2346 | 123.2437 | 6.7154 | -0.045776 | 108.9706 | 108.7418 | 108.6502 | -14.7858 | 123.3307 | 123.2941 | 123.262 | -6.8115
2909.5156 | 123.5138 | -107.8445 | 15.4175 | 0.20294 | 0.015236 | 0.00072209 | 0.010685 | -0.018057 | -0.0025784 | 0.00041648 | 0.27794 | 0.021516 | -0.0091494 | 0.01164 | -0.00036743 | 0.0082885 | 1.0803 | 0.97046 | 0.90637 | 0.99335 | 1.0162 | 0.85602 | 0.68665 | 15.4404 | 15.509 | 15.477 | 15.4037 | 15.3488 | 8.7799 | 8.6746 | 108.7006 | 108.5312 | -14.4012 | 108.815 | 108.8379 | 0.3067 | -14.3372 | 116.6244 | 116.5192 | -0.013732 | 123.2849 | 123.3215 | 6.8024 | -0.068664 | 108.8608 | 108.9249 | 108.7509 | -14.7308 | 123.2483 | 123.1934 | 123.3536 | -6.7429
2910.5156 | 123.4314 | -107.8949 | 15.4129 | 0.22583 | 0.019508 | 0.0015765 | 0.014958 | -0.017844 | 0.003403 | -1.0724e-05 | 0.10246 | 0.023439 | -0.0095768 | 0.011854 | 0.00027337 | 0.0089295 | 0.87433 | 0.87433 | 0.75989 | 0.91095 | 1.1124 | 0.85144 | 0.68207 | 15.3305 | 14.9734 | 15.3122 | 15.3992 | 15.3534 | 8.7616 | 8.67 | 108.7463 | 108.577 | -14.3005 | 108.7692 | 108.8058 | 0.22888 | -14.5386 | 116.6565 | 116.5649 | -0.013733 | 123.2254 | 123.2071 | 6.6422 | -0.059509 | 109.0073 | 108.7692 | 108.6548 | -14.7308 | 123.2941 | 123.2483 | 122.8683 | -6.7429
2911.5156 | 123.4772 | -107.9224 | 15.3397 | 0.080872 | 0.012886 | 0.0054217 | 0.013249 | -0.019126 | -0.0051418 | 0.0021255 | -0.56892 | 0.01938 | -0.011713 | 0.012708 | -0.0046398 | 0.0097839 | 0.90179 | 0.97961 | 0.88806 | 0.94757 | 1.0941 | 0.86975 | 0.70953 | 15.3259 | 15.3625 | 15.3992 | 15.3076 | 15.2664 | 8.7753 | 8.6746 | 108.7921 | 108.6319 | -14.2456 | 108.902 | 108.8699 | 0.23804 | -14.4379 | 116.6977 | 116.597 | -0.032044 | 123.2483 | 123.3215 | 6.7245 | -0.073243 | 109.0164 | 108.8242 | 108.8104 | -14.6301 | 123.23 | 123.1888 | 123.2849 | -6.665
2912.5156 | 123.3856 | -108.0368 | 15.3442 | 0.14954 | 0.015877 | 0.0024311 | 0.014958 | -0.018912 | 0.006821 | 0.0046891 | -0.20271 | 0.023225 | -0.0070132 | 0.012068 | -0.00058103 | 0.0074341 | 0.68665 | 1.0895 | 0.84228 | 0.87891 | 1.0986 | 0.86975 | 0.68665 | 15.239 | 15.2618 | 15.2435 | 15.3534 | 15.2802 | 8.7845 | 8.6746 | 108.9066 | 108.7234 | -14.2456 | 109.1263 | 108.9157 | 0.19226 | -14.6576 | 116.8213 | 116.7114 | 0.009156 | 123.2758 | 123.2803 | 6.5689 | -0.064087 | 109.1354 | 108.7234 | 108.8791 | -14.6576 | 123.3902 | 123.317 | 123.2986 | -6.6696
2913.5156 | 123.5001 | -107.9727 | 15.2802 | 0.2182 | 0.015877 | 0.0024311 | 0.01154 | -0.019766 | 0.0029758 | 0.00084388 | 0.19402 | 0.021943 | -0.01214 | 0.011213 | -0.0027172 | 0.0082885 | 0.93384 | 0.94299 | 0.83313 | 0.94299 | 1.0895 | 0.86975 | 0.70038 | 15.303 | 15.3397 | 15.3488 | 15.2893 | 15.2161 | 8.7753 | 8.6746 | 108.8425 | 108.6731 | -14.1907 | 108.9157 | 108.9157 | 0.24262 | -14.3463 | 116.748 | 116.6473 | 0.009156 | 123.2758 | 123.3215 | 6.6742 | -0.064087 | 109.0622 | 108.9066 | 108.8058 | -14.5798 | 123.262 | 123.1888 | 123.3124 | -6.6055
2914.5156 | 123.3582 | -108.0505 | 15.2939 | 0.09613 | 0.020576 | -0.00034611 | 0.013676 | -0.019766 | 0.0046848 | 0.0021255 | 0.14061 | 0.024934 | -0.010645 | 0.010359 | -0.00058103 | 0.0085021 | 0.89264 | 0.84686 | 0.77362 | 0.90179 | 1.1032 | 0.84228 | 0.66834 | 15.1657 | 15.1978 | 15.065 | 15.2664 | 15.2206 | 8.7708 | 8.67 | 108.8928 | 108.7189 | -14.1907 | 108.8974 | 108.9523 | 0.23346 | -14.4012 | 116.8213 | 116.7206 | -0.027466 | 123.2162 | 123.1155 | 6.395 | -0.073242 | 109.1537 | 108.9432 | 108.8242 | -14.6255 | 123.317 | 123.2712 | 123.2483 | -6.6238
2915.5156 | 123.5733 | -108.078 | 15.1794 | 0.20294 | 0.019081 | 0.0011493 | 0.010258 | -0.01998 | -1.505e-05 | 0.0034073 | 0.23979 | 0.020662 | -0.011713 | 0.011427 | -0.0031446 | 0.010852 | 0.95673 | 0.98877 | 0.89264 | 0.96588 | 1.0666 | 0.8606 | 0.70953 | 15.2344 | 15.303 | 15.2802 | 15.2115 | 15.152 | 8.7845 | 8.6746 | 108.9386 | 108.7875 | -14.1129 | 109.0668 | 109.0439 | 0.25635 | -14.2227 | 116.8625 | 116.7526 | 0.032044 | 123.3124 | 123.3582 | 6.6055 | -0.027465 | 109.1446 | 109.0347 | 108.9706 | -14.4699 | 123.2895 | 123.23 | 123.381 | -6.5048
2916.5156 | 123.5001 | -108.078 | 15.1978 | 0.14954 | 0.018226 | 0.0028583 | 0.012394 | -0.019766 | -0.002792 | 0.0010575 | 0.26268 | 0.023439 | -0.009363 | 0.010572 | -0.0035718 | 0.010211 | 0.97046 | 1.0025 | 0.92468 | 0.96588 | 1.0529 | 0.90179 | 0.71411 | 15.2161 | 15.271 | 15.2664 | 15.184 | 15.152 | 8.7799 | 8.6792 | 108.9798 | 108.7921 | -14.1449 | 109.0805 | 109.0439 | 0.25177 | -14.2273 | 116.8579 | 116.7572 | -0.013733 | 123.2941 | 123.3444 | 6.5872 | -0.045776 | 109.1309 | 109.0485 | 109.0027 | -14.4836 | 123.262 | 123.23 | 123.349 | -6.5186
2917.5156 | 123.4818 | -108.11 | 15.1611 | 0.24872 | 0.019081 | 0.0028583 | 0.015172 | -0.019126 | 0.003403 | 0.00041648 | 0.27031 | 0.023225 | -0.010858 | 0.011427 | -0.0010082 | 0.0080749 | 0.93384 | 0.93384 | 0.83313 | 0.92468 | 1.0757 | 0.85144 | 0.68665 | 15.152 | 15.2206 | 15.2023 | 15.1657 | 15.0925 | 8.7708 | 8.67 | 108.9615 | 108.7967 | -14.0854 | 109.0439 | 109.0347 | 0.23804 | -14.2273 | 116.8808 | 116.7801 | 0.004577 | 123.262 | 123.3124 | 6.5323 | -0.068665 | 109.1858 | 109.0439 | 108.9432 | -14.4745 | 123.2758 | 123.2025 | 123.3307 | -6.4911
2918.5156 | 123.1796 | -108.1329 | 15.1337 | 0.080872 | 0.018654 | 0.0028583 | 0.015599 | -0.018912 | 0.003403 | 0.0014847 | 0.071945 | 0.024507 | -0.0095768 | 0.010786 | 0.00091437 | 0.0061523 | 0.89722 | 0.84228 | 0.76904 | 0.88806 | 1.1032 | 0.85144 | 0.65918 | 15.0238 | 15.0787 | 15.0513 | 15.1794 | 15.1245 | 8.7708 | 8.6746 | 108.9844 | 108.7921 | -14.0305 | 108.9752 | 109.021 | 0.22888 | -14.2365 | 116.9037 | 116.8076 | 0.045776 | 123.1567 | 123.1842 | 6.3766 | -0.009155 | 109.2361 | 109.0302 | 108.902 | -14.4745 | 123.3124 | 123.2574 | 123.2117 | -6.459
2919.5156 | 123.4131 | -108.1879 | 15.097 | -0.018311 | 0.019935 | -0.00098691 | 0.01154 | -0.020621 | 0.002335 | 0.0029801 | -0.027237 | 0.021516 | -0.010004 | 0.010786 | -0.00058103 | 0.010211 | 0.94757 | 0.9201 | 0.80566 | 0.91553 | 1.0895 | 0.82855 | 0.66376 | 15.0284 | 15.0925 | 15.0238 | 15.1337 | 15.065 | 8.7753 | 8.67 | 109.0164 | 108.8516 | -14.0076 | 109.108 | 109.1034 | 0.25177 | -14.1495 | 116.9632 | 116.8579 | 0.036621 | 123.2162 | 123.2117 | 6.3538 | -0.032044 | 109.2773 | 109.1354 | 108.9935 | -14.4333 | 123.3215 | 123.2529 | 123.2803 | -6.427
2920.5156 | 123.3902 | -108.2565 | 15.097 | 0.16479 | 0.022072 | 0.0013629 | 0.01389 | -0.020407 | 0.0012668 | 0.0012711 | -0.20271 | 0.020662 | -0.011713 | 0.011854 | -0.0010082 | 0.0099975 | 0.84686 | 0.83313 | 0.75073 | 0.86975 | 1.0986 | 0.8606 | 0.67291 | 15.0055 | 15.033 | 15.0009 | 15.1016 | 15.0742 | 8.7708 | 8.67 | 109.1171 | 108.9294 | -13.9984 | 109.0897 | 109.1263 | 0.19684 | -14.2502 | 117.0273 | 116.9266 | 0.004578 | 123.262 | 123.2574 | 6.3309 | -0.022888 | 109.3552 | 109.1034 | 109.0073 | -14.4241 | 123.3582 | 123.3307 | 123.2895 | -6.427
2921.5156 | 123.4818 | -108.2474 | 15.0467 | 0.23346 | 0.019508 | 0.00093569 | 0.014531 | -0.015921 | 0.00019875 | 0.0019119 | 0.19402 | 0.021943 | -0.009363 | 0.011854 | -0.003999 | 0.0099975 | 0.89264 | 0.89722 | 0.84228 | 0.90637 | 1.0666 | 0.87433 | 0.68207 | 15.033 | 15.0787 | 15.065 | 15.0467 | 14.9872 | 8.7708 | 8.67 | 109.1217 | 108.9294 | -13.9801 | 109.1446 | 109.1537 | 0.2243 | -14.1541 | 117.0181 | 116.9174 | 0 | 123.2803 | 123.3124 | 6.395 | -0.059509 | 109.314 | 109.14 | 109.0897 | -14.3646 | 123.2941 | 123.2346 | 123.3261 | -6.3766
2922.5156 | 123.3994 | -108.2977 | 15.0467 | 0.012207 | 0.019935 | 0.0024311 | 0.015599 | -0.017844 | 0.00019875 | 0.0023391 | 0.018539 | 0.023439 | -0.010645 | 0.010786 | -0.0016492 | 0.0093567 | 0.91553 | 0.90179 | 0.78735 | 0.91553 | 1.0391 | 0.82855 | 0.66376 | 14.9231 | 15.0009 | 14.9414 | 15.0192 | 15.0055 | 8.7753 | 8.6655 | 109.1263 | 108.9615 | -14.0076 | 109.1995 | 109.2133 | 0.25177 | -14.1312 | 117.0731 | 116.9632 | -0.027466 | 123.2208 | 123.2391 | 6.2759 | -0.041199 | 109.3369 | 109.2133 | 109.0851 | -14.3829 | 123.317 | 123.3032 | 123.2986 | -6.3812
2923.5156 | 123.381 | -108.3389 | 15.0055 | 0.17242 | 0.019722 | 0.0022175 | 0.014103 | -0.019126 | 0.00041235 | 0.0049027 | 0.25505 | 0.022798 | -0.011286 | 0.011854 | -0.0029308 | 0.0099975 | 0.98419 | 0.7782 | 0.78735 | 1.0208 | 1.1169 | 0.8606 | 0.68665 | 14.8727 | 14.9231 | 14.9002 | 15.0192 | 14.9689 | 8.7753 | 8.6792 | 109.1995 | 109.0256 | -13.8885 | 109.1171 | 109.3597 | 0.33417 | -14.0213 | 117.1143 | 117.0181 | 0.013733 | 123.2117 | 123.2391 | 6.221 | -0.036621 | 109.4559 | 109.3231 | 109.1263 | -14.3188 | 123.3582 | 123.3078 | 123.262 | -6.3263
2924.5156 | 123.381 | -108.3572 | 14.9826 | 0.11139 | 0.021217 | 0.0024311 | 0.012394 | -0.018271 | 0.002335 | 0.0012711 | 2.4065 | 0.026643 | -0.0089358 | 0.0088632 | -0.0020764 | 0.011707 | 0.84686 | 0.80566 | 0.737 | 0.86975 | 1.0803 | 0.83313 | 0.63171 | 14.7583 | 15.0146 | 14.8956 | 15.033 | 14.9414 | 8.7753 | 8.67 | 109.1904 | 108.989 | -13.9023 | 109.1629 | 109.227 | 0.23804 | -14.1357 | 117.1326 | 117.0273 | 0.050354 | 123.1155 | 123.2529 | 6.2256 | -0.041199 | 109.4376 | 109.2041 | 109.0942 | -14.3509 | 123.3902 | 123.2986 | 123.3719 | -6.3126
2925.5156 | 123.4222 | -108.3801 | 14.9506 | 0.14191 | 0.018226 | 0.0022175 | 0.01154 | -0.018698 | 0.001694 | 0.0016983 | 0.2169 | 0.023011 | -0.0076542 | 0.012068 | -0.0025036 | 0.0091431 | 0.84686 | 0.84686 | 0.75531 | 0.88806 | 1.0757 | 0.81024 | 0.65002 | 14.8361 | 14.8727 | 14.8636 | 14.946 | 14.8956 | 8.7753 | 8.6746 | 109.1904 | 109.0302 | -13.8748 | 109.227 | 109.2682 | 0.23804 | -14.1037 | 117.1555 | 117.0547 | -0.004578 | 123.2162 | 123.2437 | 6.189 | -0.054932 | 109.4559 | 109.227 | 109.1354 | -14.3005 | 123.3261 | 123.2758 | 123.2529 | -6.2759
2926.5156 | 123.4085 | -108.4396 | 14.9139 | 0.77515 | 0.021004 | 0.00072209 | 0.014531 | -0.020407 | 0.003403 | 0.0019119 | 0.1635 | 0.022157 | -0.010858 | 0.012068 | -0.0010082 | 0.010211 | 0.88806 | 0.82855 | 0.74616 | 0.87433 | 1.0986 | 0.84228 | 0.63629 | 14.772 | 14.8132 | 14.8315 | 14.9139 | 14.8682 | 8.7799 | 8.67 | 109.2819 | 109.0759 | -13.8153 | 109.2682 | 109.314 | 0.23804 | -14.0259 | 117.2195 | 117.1097 | 0 | 123.2117 | 123.2712 | 6.1615 | -0.045776 | 109.5383 | 109.3277 | 109.1858 | -14.2776 | 123.3536 | 123.3078 | 123.2529 | -6.2439
2927.5156 | 123.3994 | -108.4579 | 14.8773 | 0.16479 | 0.017799 | 0.0020037 | 0.008122 | -0.018912 | -0.00065585 | -0.0030013 | 0.23216 | 0.022798 | -0.009363 | 0.012068 | -0.00229 | 0.010638 | 1.0849 | 0.75989 | 0.70953 | 0.90179 | 1.1078 | 0.84228 | 0.68207 | 14.7629 | 14.7903 | 14.7949 | 14.8727 | 14.8315 | 8.7708 | 8.67 | 109.3002 | 109.14 | -13.7695 | 109.2178 | 109.3597 | 0.21973 | -13.7924 | 117.2287 | 117.128 | -0.004577 | 123.2208 | 123.2529 | 6.1249 | -0.045776 | 109.5657 | 109.5428 | 109.1675 | -14.1953 | 123.3307 | 123.2895 | 123.2483 | -6.2073
2928.5156 | 123.3902 | -108.5129 | 14.827 | 0.09613 | 0.019722 | 0.0013629 | 0.012394 | -0.022544 | 0.0019078 | 0.0023391 | 0.25505 | 0.020234 | -0.011499 | 0.013349 | -0.0016492 | 0.010211 | 0.85144 | 0.82398 | 0.89264 | 0.80109 | 1.0666 | 0.83771 | 0.69122 | 14.7354 | 14.7308 | 14.7491 | 14.859 | 14.7995 | 8.7708 | 8.6746 | 109.3506 | 109.2041 | -13.7604 | 109.3369 | 109.314 | 0.10986 | -13.9755 | 117.2836 | 117.1875 | 0.032044 | 123.2483 | 123.262 | 6.0745 | -0.027465 | 109.5795 | 109.3643 | 109.4055 | -14.1357 | 123.3719 | 123.3124 | 123.2437 | -6.1523
2929.5156 | 123.4222 | -108.5266 | 14.7858 | 0.17242 | 0.018013 | 0.0039263 | 0.013463 | -0.020835 | -0.00065585 | 0.0014847 | 0.14824 | 0.021089 | -0.009363 | 0.012068 | -0.0025036 | 0.0099975 | 0.85144 | 0.84228 | 0.7782 | 0.87433 | 1.0712 | 0.81482 | 0.6546 | 14.7079 | 14.7446 | 14.7446 | 14.827 | 14.7812 | 8.7753 | 8.6746 | 109.3414 | 109.1812 | -13.7146 | 109.3689 | 109.4009 | 0.21973 | -13.9343 | 117.3019 | 117.2012 | 0.041198 | 123.2346 | 123.2712 | 6.0699 | -0.004578 | 109.5978 | 109.3781 | 109.3048 | -14.1312 | 123.3536 | 123.3078 | 123.2712 | -6.1111
2930.5156 | 123.4268 | -108.5632 | 14.7949 | -0.4303 | 0.019295 | 0.0020037 | 0.014531 | -0.018912 | 0.0027622 | 0.00041648 | -0.019608 | 0.022584 | -0.0091494 | 0.012068 | -0.0029308 | 0.0095703 | 0.92468 | 0.92468 | 0.80566 | 0.90179 | 1.0849 | 0.85144 | 0.66834 | 14.7034 | 14.7629 | 14.6896 | 14.7675 | 14.7446 | 8.7753 | 8.67 | 109.4147 | 109.2316 | -13.71 | 109.4879 | 109.465 | 0.23346 | -13.8702 | 117.3386 | 117.2333 | -0.027466 | 123.2666 | 123.2529 | 6.0196 | -0.050354 | 109.6481 | 109.4879 | 109.3689 | -14.1266 | 123.3307 | 123.3078 | 123.3261 | -6.1249
2931.5156 | 123.4863 | -108.5587 | 14.7079 | 0.14954 | 0.01844 | 0.0039263 | 0.014531 | -0.019339 | -0.0036464 | -0.00022432 | 0.23979 | 0.020234 | -0.0097904 | 0.012281 | -0.0042126 | 0.0082885 | 0.92926 | 0.98877 | 0.88806 | 0.93842 | 1.0437 | 0.86975 | 0.70496 | 14.7217 | 14.8041 | 14.7858 | 14.7125 | 14.6667 | 8.7753 | 8.6746 | 109.4284 | 109.2636 | -13.6642 | 109.5474 | 109.4971 | 0.23346 | -13.7787 | 117.334 | 117.2333 | 0.004577 | 123.2803 | 123.3444 | 6.1111 | -0.041199 | 109.6024 | 109.4879 | 109.4467 | -14.003 | 123.2712 | 123.2254 | 123.3627 | -6.0333
2932.5156 | 123.4268 | -108.609 | 14.7079 | -0.079346 | 0.022072 | 0.0030719 | 0.016881 | -0.019339 | 0.0083164 | 0.00063028 | -0.073013 | 0.023011 | -0.0072268 | 0.0097176 | -0.00229 | 0.0074341 | 0.88806 | 1.0208 | 0.81024 | 0.93384 | 1.1307 | 0.88806 | 0.70496 | 14.653 | 14.7125 | 14.6439 | 14.6988 | 14.653 | 8.7708 | 8.6746 | 109.4971 | 109.314 | -13.5773 | 109.6298 | 109.5428 | 0.22888 | -13.8199 | 117.3798 | 117.2836 | -0.009155 | 123.262 | 123.2529 | 5.9692 | -0.054932 | 109.7397 | 109.4971 | 109.4193 | -14.003 | 123.3078 | 123.262 | 123.3215 | -6.0333
2933.5156 | 123.3765 | -108.6823 | 14.6805 | 0.050354 | 0.019081 | 0.0022175 | 0.014958 | -0.020835 | 0.0038304 | 0.0019119 | 0.026169 | 0.02173 | -0.0089358 | 0.014204 | -0.0014356 | 0.0093567 | 0.83771 | 0.83313 | 0.75531 | 0.8606 | 1.0437 | 0.80109 | 0.63629 | 14.534 | 14.6027 | 14.5615 | 14.6805 | 14.6164 | 8.7753 | 8.67 | 109.4833 | 109.3185 | -13.6368 | 109.5154 | 109.5428 | 0.2243 | -13.8428 | 117.4576 | 117.3523 | 0 | 123.2162 | 123.2437 | 5.8914 | -0.064087 | 109.726 | 109.52 | 109.4376 | -14.0442 | 123.3627 | 123.2986 | 123.2849 | -6.0104
2934.5156 | 123.4131 | -108.7143 | 14.6439 | 0.027466 | 0.019508 | 0.0024311 | 0.013249 | -0.018057 | 0.001694 | 0.0021255 | 0.0032804 | 0.022157 | -0.0089358 | 0.011427 | 0.00048697 | 0.0099975 | 0.90179 | 0.90637 | 0.80109 | 0.90637 | 1.0666 | 0.81482 | 0.64087 | 14.5432 | 14.6301 | 14.5615 | 14.6484 | 14.5935 | 8.7708 | 8.67 | 109.5291 | 109.3552 | -13.5773 | 109.6207 | 109.6207 | 0.2655 | -13.7421 | 117.485 | 117.3843 | 0.004577 | 123.2574 | 123.2758 | 5.8914 | -0.050354 | 109.7809 | 109.6161 | 109.5154 | -14.003 | 123.3627 | 123.3078 | 123.3444 | -5.9738
2935.5156 | 123.3948 | -108.7326 | 14.6118 | 0.12665 | 0.021431 | 0.0026447 | 0.016026 | -0.020194 | 0.0010532 | 0.0046891 | 0.1635 | 0.023439 | -0.0074404 | 0.016767 | -0.0037854 | 0.0074341 | 0.83771 | 0.80566 | 0.71869 | 0.85602 | 1.0803 | 0.81482 | 0.65002 | 14.5798 | 14.5752 | 14.4562 | 14.6301 | 14.5981 | 8.7708 | 8.6746 | 109.5474 | 109.3826 | -13.5315 | 109.5383 | 109.5886 | 0.20599 | -13.7741 | 117.5034 | 117.4072 | 0.018311 | 123.3124 | 123.1888 | 5.7816 | -0.013733 | 109.8129 | 109.5703 | 109.4513 | -13.9618 | 123.3627 | 123.3307 | 123.3078 | -5.9372
2936.5156 | 123.4177 | -108.7418 | 14.5844 | -0.29297 | 0.01844 | 0.00093569 | 0.01624 | -0.019553 | 0.0038304 | 0.0027665 | -0.0043486 | 0.021302 | -0.0076542 | 0.012922 | -0.0014356 | 0.0095703 | 0.90179 | 0.92926 | 0.81024 | 0.89722 | 1.0895 | 0.84228 | 0.68665 | 14.4928 | 14.5844 | 14.5203 | 14.5752 | 14.5203 | 8.7708 | 8.67 | 109.584 | 109.4284 | -13.4949 | 109.671 | 109.639 | 0.21057 | -13.6826 | 117.5125 | 117.4118 | -0.009156 | 123.2346 | 123.262 | 5.8502 | -0.064087 | 109.8312 | 109.6436 | 109.552 | -13.8977 | 123.317 | 123.262 | 123.3261 | -5.9143
2937.5156 | 123.381 | -108.783 | 14.5386 | 0.080872 | 0.018226 | 0.0015765 | 0.014317 | -0.018271 | 0.003403 | 0.0016983 | 0.11009 | 0.022798 | -0.0087222 | 0.012922 | -0.0010082 | 0.0095703 | 0.82398 | 0.8194 | 0.737 | 0.84686 | 1.0437 | 0.80109 | 0.63171 | 14.3875 | 14.4745 | 14.4241 | 14.5615 | 14.5065 | 8.7708 | 8.6655 | 109.584 | 109.4147 | -13.4949 | 109.6024 | 109.6298 | 0.21515 | -13.7146 | 117.5537 | 117.4484 | 0.022888 | 123.1705 | 123.2071 | 5.7587 | -0.032043 | 109.8267 | 109.6069 | 109.52 | -13.9069 | 123.3444 | 123.2895 | 123.2574 | -5.8731
2938.5156 | 123.4406 | -108.8104 | 14.5294 | -0.12512 | 0.017799 | 0.0024311 | 0.012394 | -0.016562 | -0.00044225 | 0.0012711 | -0.1722 | 0.023011 | -0.010858 | 0.012281 | -0.0020764 | 0.011493 | 0.83313 | 0.85144 | 0.75531 | 0.88806 | 1.0666 | 0.80566 | 0.62714 | 14.4058 | 14.5248 | 14.4699 | 14.502 | 14.4791 | 8.7799 | 8.67 | 109.6161 | 109.4376 | -13.4628 | 109.6619 | 109.6985 | 0.26093 | -13.6963 | 117.5903 | 117.4805 | -0.027466 | 123.2162 | 123.2803 | 5.7999 | -0.050354 | 109.877 | 109.6436 | 109.5657 | -13.9023 | 123.3124 | 123.2895 | 123.3353 | -5.8594
2939.5156 | 123.4314 | -108.847 | 14.5111 | 0.14954 | 0.01844 | 0.0011493 | 0.015385 | -0.018485 | 0.0010532 | 0.0010575 | 0.11772 | 0.022798 | -0.0087222 | 0.010572 | -0.00015383 | 0.011493 | 0.82398 | 0.81024 | 0.71869 | 0.84686 | 1.0666 | 0.80109 | 0.65002 | 14.4379 | 14.1129 | 14.5844 | 14.4791 | 14.4562 | 8.7708 | 8.6746 | 109.6481 | 109.4971 | -13.4445 | 109.6573 | 109.6939 | 0.19684 | -13.6871 | 117.6178 | 117.5217 | -0.032043 | 123.2849 | 123.4314 | 5.9097 | -0.054931 | 109.9136 | 109.671 | 109.5657 | -13.8611 | 123.3261 | 123.3032 | 122.9599 | -5.8365
2940.5156 | 123.5092 | -108.8287 | 14.415 | 0.34027 | 0.017158 | 0.0026447 | 0.014317 | -0.01998 | -0.0030056 | 0.00020288 | 0.24742 | 0.022584 | -0.0087222 | 0.010359 | -0.0031446 | 0.0099975 | 0.90637 | 0.97961 | 0.88806 | 0.92926 | 1.0162 | 0.85602 | 0.68207 | 14.4104 | 14.5065 | 14.4699 | 14.3829 | 14.3646 | 8.7799 | 8.6746 | 109.6848 | 109.5108 | -13.3987 | 109.8083 | 109.758 | 0.24719 | -13.5086 | 117.6086 | 117.5034 | -0.032043 | 123.2391 | 123.2986 | 5.7953 | -0.050354 | 109.845 | 109.7351 | 109.7168 | -13.7329 | 123.2117 | 123.1934 | 123.3353 | -5.7404
2941.5156 | 123.3948 | -108.9569 | 14.4333 | 0.11902 | 0.020149 | 0.0013629 | 0.014531 | -0.018057 | 0.003403 | 0.0031937 | 0.43053 | 0.021943 | -0.0097904 | 0.013136 | -0.0012218 | 0.0091431 | 0.72327 | 0.92468 | 0.87891 | 0.93384 | 1.0757 | 0.83313 | 0.64545 | 14.2639 | 14.3234 | 14.296 | 14.4333 | 14.3738 | 8.7708 | 8.6838 | 109.79 | 109.6024 | -13.3575 | 109.8816 | 109.8907 | 0.28839 | -13.71 | 117.7277 | 117.6407 | 0 | 123.2208 | 123.2529 | 5.6122 | -0.05951 | 110.0327 | 109.6802 | 109.8358 | -13.7878 | 123.3902 | 123.3307 | 123.2803 | -5.7495
2942.5156 | 123.4451 | -108.8745 | 14.4745 | -0.079346 | 0.02079 | 0.0011493 | 0.01154 | -0.018912 | 0.00019875 | 0.0010575 | -0.019608 | 0.023866 | -0.010431 | 0.010786 | -0.00036743 | 0.011493 | 0.90179 | 0.89722 | 0.80109 | 0.90637 | 1.0529 | 0.80566 | 0.64545 | 14.2868 | 14.3829 | 14.3234 | 14.3829 | 14.3326 | 8.7799 | 8.6746 | 109.6802 | 109.52 | -13.4216 | 109.7717 | 109.7809 | 0.26092 | -13.5727 | 117.6544 | 117.5491 | -0.091552 | 123.1613 | 123.1979 | 5.6488 | -0.14191 | 109.9274 | 109.7763 | 109.6756 | -13.829 | 123.2574 | 123.2071 | 123.2574 | -5.7999
2943.5156 | 123.4177 | -108.9981 | 14.36 | 0.027466 | 0.019722 | 0.0020037 | 0.013463 | -0.018912 | 0.0021214 | 0.0016983 | 0.071945 | 0.022157 | -0.0072268 | 0.01164 | -0.0012218 | 0.010425 | 0.86517 | 0.8606 | 0.75531 | 0.87433 | 1.03 | 0.81024 | 0.62714 | 14.2364 | 14.2914 | 14.2593 | 14.3509 | 14.3097 | 8.7799 | 8.6746 | 109.8084 | 109.6252 | -13.3301 | 109.8587 | 109.8724 | 0.24719 | -13.4949 | 117.778 | 117.6727 | -0.009155 | 123.2346 | 123.2574 | 5.5847 | -0.050354 | 110.0281 | 109.8633 | 109.7534 | -13.7329 | 123.349 | 123.3078 | 123.2895 | -5.6854
2944.5156 | 123.3902 | -109.0164 | 14.3143 | 0.0045777 | 0.018226 | 0.0028583 | 0.013463 | -0.022116 | 0.0021214 | 0.0021255 | -0.0043486 | 0.02408 | -0.010004 | 0.012068 | -0.00079463 | 0.0099975 | 0.87433 | 0.87891 | 0.77362 | 0.86975 | 1.0483 | 0.79193 | 0.63171 | 14.2227 | 14.3005 | 14.241 | 14.328 | 14.2822 | 8.7662 | 8.6655 | 109.8083 | 109.6481 | -13.266 | 109.8953 | 109.8862 | 0.23804 | -13.4399 | 117.7826 | 117.6819 | 0.013733 | 123.2391 | 123.2574 | 5.5756 | -0.032043 | 110.0647 | 109.8907 | 109.79 | -13.6826 | 123.3444 | 123.2986 | 123.317 | -5.6488
2945.5156 | 123.4909 | -109.0164 | 14.2868 | 0.065613 | 0.013313 | 0.0047809 | 0.012822 | -0.020621 | -0.004501 | -0.00043792 | 0.81963 | 0.021516 | -0.01449 | 0.0092904 | -0.0042126 | 0.010425 | 0.83313 | 0.90637 | 0.83313 | 0.89722 | 1.0208 | 0.84228 | 0.65918 | 14.1953 | 14.2822 | 14.2914 | 14.2364 | 14.2044 | 8.7662 | 8.67 | 109.8587 | 109.6756 | -13.266 | 109.9228 | 109.9136 | 0.23804 | -13.4537 | 117.7826 | 117.6865 | -0.050354 | 123.2117 | 123.3078 | 5.6213 | -0.082397 | 110.0372 | 109.8495 | 109.8495 | -13.6276 | 123.2529 | 123.2208 | 123.2986 | -5.6168
2946.5156 | 123.4177 | -109.0897 | 14.2776 | -0.14038 | 0.019508 | 0.0034991 | 0.014317 | -0.018485 | 0.00019875 | -1.0724e-05 | -0.10353 | 0.023652 | -0.0076542 | 0.009504 | -0.0012218 | 0.0089295 | 0.84228 | 0.82855 | 0.74616 | 0.85144 | 1.062 | 0.79193 | 0.62256 | 14.1266 | 14.2456 | 14.1815 | 14.2685 | 14.2319 | 8.7753 | 8.6746 | 109.8816 | 109.7122 | -13.2156 | 109.9182 | 109.9411 | 0.22888 | -13.4354 | 117.865 | 117.7643 | -0.009155 | 123.2162 | 123.2712 | 5.5069 | -0.045776 | 110.1517 | 109.9319 | 109.8358 | -13.6551 | 123.3582 | 123.3215 | 123.3353 | -5.603
2947.5156 | 123.4314 | -109.0668 | 14.2181 | -0.056458 | 0.019081 | 0.0013629 | 0.014317 | -0.019126 | 0.0027622 | 0.00084388 | -0.3553 | 0.023225 | -0.0089358 | 0.010145 | -0.0014356 | 0.0082885 | 0.88806 | 0.89264 | 1.062 | 1.03 | 1.0666 | 0.84686 | 0.67291 | 14.1541 | 14.241 | 14.1861 | 14.2273 | 14.1815 | 8.7753 | 8.6746 | 109.9136 | 109.7397 | -13.1516 | 109.9594 | 110.0967 | 0.35706 | -13.3301 | 117.8421 | 117.7414 | 0.009155 | 123.2208 | 123.2529 | 5.5115 | -0.036621 | 110.1334 | 109.9548 | 110.1288 | -13.5452 | 123.2941 | 123.2483 | 123.3078 | -5.5435
2948.5156 | 123.436 | -109.1354 | 14.1815 | -0.16327 | 0.018013 | 0.0022175 | 0.013035 | -0.019766 | -0.00022865 | 0.0016983 | -0.15694 | 0.021302 | -0.0091494 | 0.0086496 | -0.0014356 | 0.0085021 | 0.8194 | 0.84228 | 0.737 | 0.86517 | 1.0391 | 0.79193 | 0.60425 | 14.0717 | 14.1998 | 14.1449 | 14.1953 | 14.1541 | 8.7753 | 8.67 | 109.9274 | 109.7397 | -13.1424 | 109.9777 | 110.0006 | 0.26092 | -13.3621 | 117.9108 | 117.8055 | 0.013732 | 123.2071 | 123.2803 | 5.4749 | -0.027466 | 110.1746 | 109.9548 | 109.8724 | -13.5773 | 123.3307 | 123.2895 | 123.3353 | -5.5115
2949.5156 | 123.436 | -109.1721 | 14.1632 | -0.20905 | 0.018867 | 0.0020037 | 0.013676 | -0.018912 | 0.0019078 | 0.0023391 | 0.0032804 | 0.022371 | -0.0085086 | 0.0099314 | -0.0033582 | 0.0091431 | 0.87891 | 0.90637 | 0.7782 | 0.88348 | 1.0391 | 0.78735 | 0.60883 | 14.0762 | 14.1541 | 14.0854 | 14.1495 | 14.1083 | 8.7799 | 8.67 | 109.9594 | 109.7809 | -13.1241 | 110.0784 | 110.0555 | 0.27466 | -13.2843 | 117.952 | 117.8421 | -0.013733 | 123.2483 | 123.2574 | 5.4153 | -0.054932 | 110.2112 | 110.051 | 109.9503 | -13.5544 | 123.3215 | 123.2803 | 123.3261 | -5.4932
2950.5156 | 123.4222 | -109.2361 | 14.1174 | 0.18768 | 0.021217 | 0.0043537 | 0.01624 | -0.018057 | 0.0010532 | 0.00041648 | 0.12535 | 0.02472 | -0.0085086 | 0.013563 | -0.0025036 | 0.011066 | 0.80566 | 0.8194 | 0.72327 | 0.8194 | 1.0437 | 0.77362 | 0.6134 | 13.9847 | 14.0305 | 14.0167 | 14.1266 | 14.0442 | 8.7799 | 8.6746 | 110.0098 | 109.8495 | -13.0737 | 110.0555 | 110.0555 | 0.20599 | -13.3118 | 118.0161 | 117.9108 | 0.009155 | 123.2208 | 123.2529 | 5.3421 | -0.073243 | 110.2798 | 110.0418 | 109.9594 | -13.504 | 123.3627 | 123.2803 | 123.2666 | -5.4428
2951.5156 | 123.4406 | -109.2361 | 14.1037 | -0.056458 | 0.016945 | 0.0037127 | 0.013035 | -0.018271 | -1.505e-05 | 0.0027665 | 0.25505 | 0.024507 | -0.0087222 | 0.011427 | -0.0035718 | 0.0082885 | 0.91095 | 1.03 | 0.88348 | 0.95215 | 1.0757 | 0.84228 | 0.67749 | 14.0305 | 14.09 | 14.035 | 14.09 | 14.0671 | 8.7753 | 8.6746 | 110.0784 | 109.9136 | -13.028 | 110.2661 | 110.1883 | 0.27466 | -13.1927 | 118.0115 | 117.9108 | -0.013733 | 123.2666 | 123.2712 | 5.3604 | -0.036621 | 110.3119 | 110.1471 | 110.1196 | -13.4262 | 123.3261 | 123.3032 | 123.3261 | -5.4291
2952.5156 | 123.4543 | -109.2545 | 14.0625 | -0.14801 | 0.016731 | 0.0032855 | 0.012822 | -0.020621 | 0.00041235 | 0.00084388 | -0.15694 | 0.02173 | -0.0091494 | 0.011213 | -0.0027172 | 0.0099975 | 0.81482 | 0.83313 | 0.74616 | 0.85602 | 1.0254 | 0.77362 | 0.59509 | 13.9572 | 14.0717 | 14.0121 | 14.0717 | 14.0259 | 8.7708 | 8.67 | 110.0281 | 109.8495 | -13.0371 | 110.0876 | 110.1105 | 0.26092 | -13.2477 | 118.0252 | 117.9245 | 0.009155 | 123.2117 | 123.2666 | 5.3421 | -0.036621 | 110.2798 | 110.0693 | 110.0006 | -13.4674 | 123.3261 | 123.2803 | 123.3261 | -5.3925
2953.5156 | 123.4406 | -109.2773 | 14.0717 | -0.16327 | 0.018867 | 0.0024311 | 0.014317 | -0.017844 | 0.0019078 | 0.0029801 | -0.11879 | 0.022371 | -0.0087222 | 0.011854 | -0.0025036 | 0.0074341 | 0.8606 | 0.89264 | 0.77362 | 0.87891 | 1.0345 | 0.80109 | 0.60883 | 13.9435 | 14.0533 | 14.0076 | 14.0533 | 13.9984 | 8.7753 | 8.6792 | 110.0784 | 109.8862 | -13.0371 | 110.17 | 110.1562 | 0.27008 | -13.2111 | 118.0527 | 117.9565 | -0.01831 | 123.2208 | 123.2849 | 5.3284 | -0.073242 | 110.3119 | 110.1379 | 110.051 | -13.4628 | 123.3307 | 123.2758 | 123.3307 | -5.3925
2954.5156 | 123.4039 | -109.3323 | 14.0259 | -0.1709 | 0.015663 | 0.0039263 | 0.016881 | -0.019766 | -0.0015102 | 0.00084388 | -0.13405 | 0.020234 | -0.0089358 | 0.010572 | -0.003999 | 0.0097839 | 0.69122 | 0.91553 | 0.75073 | 0.84686 | 1.0849 | 0.8194 | 0.64087 | 13.8519 | 13.9709 | 13.9481 | 14.0259 | 13.9755 | 8.7845 | 8.6746 | 110.1517 | 109.9731 | -12.941 | 110.2478 | 110.1791 | 0.20599 | -13.3347 | 118.1168 | 118.0069 | 0 | 123.1842 | 123.2803 | 5.2734 | -0.050354 | 110.4172 | 110.0235 | 110.083 | -13.385 | 123.3582 | 123.3078 | 123.3032 | -5.3513
2955.5312 | 123.5229 | -109.3597 | 13.9206 | 0.27161 | 0.018013 | 0.0020037 | 0.014744 | -0.018485 | 0.0012668 | 0.0012711 | 0.25505 | 0.019166 | -0.0091494 | 0.0097176 | -0.0027172 | 0.0099975 | 0.88806 | 0.93384 | 0.84686 | 0.9201 | 0.98877 | 0.82398 | 0.63171 | 13.8977 | 13.6368 | 14.035 | 13.884 | 13.8199 | 8.7753 | 8.67 | 110.1837 | 109.9915 | -12.9318 | 110.2936 | 110.2798 | 0.28839 | -13.0325 | 118.1351 | 118.0298 | -0.036621 | 123.2574 | 123.3948 | 5.365 | -0.10071 | 110.3485 | 110.2478 | 110.2066 | -13.2889 | 123.2437 | 123.1796 | 122.9965 | -5.2505
2956.5156 | 123.4177 | -109.4193 | 13.9572 | -0.10986 | 0.015663 | 0.0056353 | 0.01389 | -0.01998 | -0.0012966 | 0.00084388 | -0.1722 | 0.023225 | -0.011286 | 0.012708 | -0.0029308 | 0.0082885 | 0.80566 | 0.83313 | 0.72327 | 0.84686 | 1.03 | 0.77362 | 0.59967 | 13.8062 | 13.9023 | 13.8519 | 13.9481 | 13.9114 | 8.7799 | 8.67 | 110.1929 | 110.0189 | -12.9272 | 110.2524 | 110.2661 | 0.24719 | -13.1516 | 118.1992 | 118.0893 | -0.009155 | 123.2254 | 123.2712 | 5.1819 | -0.045776 | 110.4492 | 110.2249 | 110.1425 | -13.3575 | 123.3673 | 123.3307 | 123.3215 | -5.2872
2957.5156 | 123.4406 | -109.4009 | 13.884 | -0.041199 | 0.020576 | 0.0028583 | 0.013249 | -0.021262 | 0.001694 | 0.0019119 | -1.1716 | 0.023439 | -0.0085086 | 0.010786 | -0.0012218 | 0.0061523 | 0.86975 | 0.87891 | 0.77362 | 0.86975 | 1.03 | 0.77362 | 0.63171 | 13.829 | 13.9343 | 13.8657 | 13.9206 | 13.8794 | 8.7753 | 8.67 | 110.1746 | 110.0327 | -12.854 | 110.2798 | 110.2707 | 0.23804 | -13.0142 | 118.1763 | 118.071 | 0.036621 | 123.23 | 123.2666 | 5.1956 | -0.004577 | 110.4309 | 110.2707 | 110.1746 | -13.2523 | 123.3215 | 123.2803 | 123.3353 | -5.2139
2958.5156 | 123.4222 | -109.4467 | 13.8702 | -0.18616 | 0.016945 | 0.0030719 | 0.01389 | -0.020835 | -0.00086945 | -0.00065152 | -0.14168 | 0.021302 | -0.012995 | 0.013777 | -0.0014356 | 0.0099975 | 0.79193 | 0.83313 | 0.72784 | 0.83771 | 1.0529 | 0.76446 | 0.59509 | 13.7283 | 13.829 | 13.7878 | 13.9023 | 13.8702 | 8.7708 | 8.6746 | 110.2112 | 110.0418 | -12.8174 | 110.2798 | 110.2844 | 0.24262 | -13.0783 | 118.2175 | 118.1213 | 0.032044 | 123.175 | 123.2346 | 5.1132 | 0 | 110.4996 | 110.2386 | 110.1746 | -13.2751 | 123.349 | 123.317 | 123.2758 | -5.1956
2959.5156 | 123.4589 | -109.4513 | 13.9206 | -0.094604 | 0.018013 | 0.0015765 | 0.015172 | -0.018057 | 0.00019875 | 0.0014847 | -0.10353 | 0.022584 | -0.0091494 | 0.013136 | -0.00079463 | 0.0074341 | 0.85144 | 0.87433 | 0.77362 | 0.87433 | 1.0529 | 0.75989 | 0.59509 | 13.7787 | 13.8519 | 13.8016 | 13.8611 | 13.8062 | 8.7708 | 8.67 | 110.2112 | 110.0464 | -12.8677 | 110.3256 | 110.3256 | 0.27924 | -13.0692 | 118.222 | 118.1213 | -0.059509 | 123.23 | 123.2529 | 5.1315 | -0.11444 | 110.5042 | 110.3027 | 110.2249 | -13.3255 | 123.3124 | 123.2574 | 123.3032 | -5.2505
2960.5156 | 123.3902 | -109.5383 | 13.8199 | -0.20905 | 0.01374 | 0.0049945 | 0.012394 | -0.019553 | -0.0019376 | 0.0012711 | -0.26375 | 0.02173 | -0.011499 | 0.011213 | -0.0063488 | 0.011066 | 0.80566 | 0.88806 | 0.76904 | 0.8606 | 1.0254 | 0.79651 | 0.61798 | 13.6871 | 13.7878 | 13.7512 | 13.8336 | 13.7878 | 8.7799 | 8.6746 | 110.3348 | 110.1562 | -12.7945 | 110.4263 | 110.3989 | 0.24262 | -13.0142 | 118.3182 | 118.2129 | 0.013733 | 123.2254 | 123.2895 | 5.0766 | -0.032043 | 110.5637 | 110.3439 | 110.3073 | -13.2019 | 123.3719 | 123.3261 | 123.3261 | -5.1453
2961.5156 | 123.4406 | -109.5291 | 13.7833 | -0.10986 | 0.018226 | 0.0030719 | 0.013249 | -0.019553 | 0.0021214 | -0.00043792 | -0.12642 | 0.023225 | -0.0080814 | 0.012495 | -0.0012218 | 0.0095703 | 0.84686 | 0.85602 | 0.76446 | 0.86975 | 1.0254 | 0.76904 | 0.59509 | 13.7054 | 13.8016 | 13.7283 | 13.7833 | 13.7375 | 8.7708 | 8.67 | 110.2982 | 110.1242 | -12.7579 | 110.3851 | 110.3989 | 0.27466 | -12.9364 | 118.2999 | 118.1992 | 0 | 123.2346 | 123.2574 | 5.0583 | -0.045776 | 110.5545 | 110.376 | 110.2936 | -13.1882 | 123.3124 | 123.2666 | 123.3307 | -5.1132
2962.5156 | 123.436 | -109.5978 | 13.7558 | -0.18616 | 0.014595 | 0.0041401 | 0.013035 | -0.018485 | 0.00041235 | -0.00065152 | -0.1722 | 0.021943 | -0.009363 | 0.012068 | -0.0035718 | 0.0080749 | 0.78278 | 0.82855 | 0.72784 | 0.83313 | 1.03 | 0.76904 | 0.59052 | 13.6139 | 13.7329 | 13.678 | 13.7741 | 13.7054 | 8.7753 | 8.6655 | 110.3668 | 110.1883 | -12.7258 | 110.4263 | 110.4309 | 0.24262 | -12.973 | 118.3731 | 118.2632 | 0.018311 | 123.2117 | 123.2758 | 5.0125 | -0.050354 | 110.6277 | 110.3806 | 110.3256 | -13.1653 | 123.3719 | 123.3032 | 123.3307 | -5.0903
2963.5156 | 123.4314 | -109.5932 | 13.7329 | -0.033569 | 0.021004 | 0.0022175 | 0.013676 | -0.016349 | 0.002335 | 0.00084388 | -0.53078 | 0.020021 | -0.0095768 | 0.011427 | -0.0033582 | 0.0082885 | 0.85144 | 0.9201 | 1.0071 | 0.98419 | 1.0574 | 0.82398 | 0.66376 | 13.6597 | 13.7238 | 13.6642 | 13.7466 | 13.6642 | 8.7753 | 8.67 | 110.4172 | 110.257 | -12.6755 | 110.5133 | 110.5774 | 0.32043 | -12.8815 | 118.3685 | 118.2632 | 0.013733 | 123.2529 | 123.2574 | 4.9942 | -0.068664 | 110.6506 | 110.4446 | 110.6003 | -13.0692 | 123.3398 | 123.2574 | 123.317 | -5.0629
2964.5156 | 123.4131 | -109.6344 | 13.7329 | -0.13275 | 0.01609 | 0.0032855 | 0.01389 | -0.019339 | -0.0017238 | 0.0010575 | -0.10353 | 0.021089 | -0.010218 | 0.012922 | -0.0035718 | 0.011707 | 0.7782 | 0.83771 | 0.71869 | 0.82855 | 1.0437 | 0.76446 | 0.58136 | 13.5498 | 13.6459 | 13.6139 | 13.7146 | 13.6642 | 8.7753 | 8.6746 | 110.3989 | 110.2158 | -12.6892 | 110.4721 | 110.463 | 0.24719 | -12.9547 | 118.4097 | 118.309 | -0.01831 | 123.1842 | 123.2483 | 4.9393 | -0.068664 | 110.6781 | 110.4126 | 110.3531 | -13.1516 | 123.349 | 123.2986 | 123.2803 | -5.0583
2965.5156 | 123.4543 | -109.6436 | 13.6917 | -0.13275 | 0.017158 | 0.00050849 | 0.015385 | -0.020194 | 0.00019875 | 0.0019119 | -0.065384 | 0.022584 | -0.0097904 | 0.012068 | -0.0042126 | 0.0089295 | 0.83771 | 0.87433 | 0.76446 | 0.86517 | 1.0208 | 0.77362 | 0.59052 | 13.5544 | 13.678 | 13.6276 | 13.7192 | 13.6414 | 8.7799 | 8.67 | 110.4172 | 110.2341 | -12.6709 | 110.5179 | 110.5087 | 0.27466 | -12.854 | 118.4235 | 118.3136 | 0.027466 | 123.1979 | 123.2712 | 4.9576 | -0.050354 | 110.6644 | 110.4813 | 110.408 | -13.1012 | 123.3627 | 123.2849 | 123.3215 | -5.0217
2966.5156 | 123.4451 | -109.6756 | 13.6505 | -0.094604 | 0.016731 | 0.0041401 | 0.014958 | -0.015921 | 0.0021214 | 0.0019119 | -0.16457 | 0.019593 | -0.009363 | 0.012068 | -0.0020764 | 0.0091431 | 0.77362 | 0.82398 | 0.71869 | 0.83313 | 1.0208 | 0.75989 | 0.58594 | 13.5132 | 13.6322 | 13.5818 | 13.6505 | 13.5818 | 8.7753 | 8.6746 | 110.4355 | 110.2615 | -12.6297 | 110.4996 | 110.5087 | 0.24719 | -12.8769 | 118.4509 | 118.3502 | 0 | 123.1888 | 123.2574 | 4.9072 | -0.068665 | 110.6964 | 110.4492 | 110.3943 | -13.0646 | 123.3261 | 123.2574 | 123.3078 | -4.9759
2967.5156 | 123.4131 | -109.6802 | 13.6551 | -0.10986 | 0.017158 | 0.0022175 | 0.014531 | -0.018912 | 0.0031894 | 0.0021255 | -0.11879 | 0.023652 | -0.0095768 | 0.012281 | -0.0012218 | 0.0080749 | 0.84228 | 0.8606 | 0.74616 | 0.87433 | 1.0071 | 0.76904 | 0.58136 | 13.5132 | 13.6093 | 13.559 | 13.6002 | 13.5818 | 8.7799 | 8.67 | 110.4492 | 110.2615 | -12.648 | 110.5408 | 110.5545 | 0.29297 | -12.8128 | 118.4601 | 118.3502 | -0.054931 | 123.1934 | 123.2391 | 4.8889 | -0.073242 | 110.6873 | 110.5225 | 110.4263 | -13.0737 | 123.2803 | 123.262 | 123.2895 | -4.985
2968.5156 | 123.3856 | -109.79 | 13.5727 | -1.6968 | 0.018654 | 0.0020037 | 0.011326 | -0.018057 | -0.0030056 | 0.00084388 | -0.065384 | 0.023011 | -0.011072 | 0.010145 | -0.0035718 | 0.0097839 | 0.75989 | 0.83313 | 0.72784 | 0.82398 | 1.0529 | 0.78735 | 0.59967 | 13.4262 | 13.5361 | 13.4995 | 13.5773 | 13.5452 | 8.7708 | 8.6746 | 110.5774 | 110.3897 | -12.5198 | 110.6232 | 110.614 | 0.2243 | -12.8128 | 118.5608 | 118.4647 | 0.004578 | 123.2162 | 123.2895 | 4.8248 | -0.027466 | 110.8429 | 110.5499 | 110.5179 | -12.973 | 123.3673 | 123.3353 | 123.3261 | -4.8981
2969.5156 | 123.4406 | -109.79 | 13.559 | -0.70496 | 0.024849 | 0.0032855 | 0.014317 | -0.020407 | 0.0010532 | 0.0019119 | -0.011978 | 0.022798 | -0.0095768 | 0.010999 | -0.0016492 | 0.0082885 | 0.86517 | 0.86975 | 0.74158 | 0.85602 | 1.0391 | 0.78735 | 0.62714 | 13.4537 | 13.5223 | 13.4674 | 13.5269 | 13.4903 | 8.7708 | 8.67 | 110.5774 | 110.4172 | -12.5198 | 110.6598 | 110.6461 | 0.22888 | -12.6938 | 118.5608 | 118.4601 | -0.032043 | 123.2437 | 123.2574 | 4.7974 | -0.068665 | 110.8292 | 110.6552 | 110.5316 | -12.9318 | 123.317 | 123.2803 | 123.3124 | -4.8889
2970.5156 | 123.436 | -109.8312 | 13.5361 | -0.20905 | 0.017158 | 0.0037127 | 0.015385 | -0.018485 | 0.00062595 | 0.00063028 | -0.11879 | 0.021302 | -0.009363 | 0.012922 | -0.0033582 | 0.0072205 | 0.78735 | 0.8194 | 0.70953 | 0.8194 | 1.0254 | 0.75073 | 0.59052 | 13.3667 | 13.4995 | 13.4445 | 13.5269 | 13.4949 | 8.7708 | 8.6746 | 110.582 | 110.4218 | -12.5107 | 110.6506 | 110.6506 | 0.22888 | -12.7487 | 118.602 | 118.5059 | -0.009155 | 123.1979 | 123.2758 | 4.7699 | -0.041199 | 110.8566 | 110.6186 | 110.5408 | -12.9456 | 123.3582 | 123.3261 | 123.3307 | -4.8615
2971.5156 | 123.4497 | -109.8404 | 13.472 | -0.033569 | 0.021431 | 0.0020037 | 0.016667 | -0.01763 | 0.0027622 | -0.00043792 | -0.26375 | 0.023652 | -0.010858 | 0.012708 | -0.00229 | 0.0093567 | 0.83771 | 1.0117 | 0.97504 | 0.93384 | 1.0483 | 0.81024 | 0.64087 | 13.4216 | 13.4583 | 13.4216 | 13.4811 | 13.4216 | 8.7799 | 8.67 | 110.6506 | 110.4813 | -12.4237 | 110.8521 | 110.7742 | 0.29297 | -12.6343 | 118.6203 | 118.5104 | 0.009155 | 123.262 | 123.262 | 4.7516 | -0.050354 | 110.8887 | 110.6781 | 110.8154 | -12.8311 | 123.3215 | 123.262 | 123.2986 | -4.8019
2972.5156 | 123.3994 | -109.8679 | 13.4583 | -0.033569 | 0.015877 | 0.0037127 | 0.012608 | -0.020407 | -0.001083 | 0.0010575 | -0.14168 | 0.02408 | -0.009363 | 0.01164 | -0.003999 | 0.010425 | 0.78278 | 0.81482 | 0.6958 | 0.82398 | 1.0391 | 0.74158 | 0.58136 | 13.3072 | 13.4033 | 13.3804 | 13.4674 | 13.4171 | 8.7799 | 8.67 | 110.6094 | 110.4492 | -12.4191 | 110.6827 | 110.6918 | 0.24262 | -12.6755 | 118.6478 | 118.5379 | 0.009155 | 123.175 | 123.2483 | 4.7104 | -0.041199 | 110.907 | 110.6506 | 110.5637 | -12.8769 | 123.3353 | 123.2849 | 123.2712 | -4.7882
2973.5156 | 123.4222 | -109.9274 | 13.4125 | 0.0045777 | 0.017799 | 0.0017901 | 0.016026 | -0.019766 | 0.0027622 | 0.0010575 | -0.027237 | 0.023866 | -0.010645 | 0.012068 | -0.0027172 | 0.0089295 | 0.82855 | 0.8606 | 0.74158 | 0.84228 | 1.0071 | 0.75989 | 0.59509 | 13.3209 | 13.4125 | 13.3575 | 13.4354 | 13.385 | 8.7753 | 8.67 | 110.6873 | 110.5225 | -12.4054 | 110.788 | 110.7697 | 0.24719 | -12.5839 | 118.7027 | 118.5974 | 0.022888 | 123.2483 | 123.2849 | 4.6875 | -0.027466 | 110.9344 | 110.7559 | 110.6689 | -12.8174 | 123.3627 | 123.3124 | 123.3398 | -4.7424
2974.5156 | 123.4177 | -109.9686 | 13.4125 | -0.17853 | 0.015236 | 0.0022175 | 0.017949 | -0.018485 | 0.0014804 | -0.00065152 | -0.19508 | 0.020662 | -0.011072 | 0.010786 | -0.0031446 | 0.011707 | 0.66376 | 0.86975 | 0.73242 | 0.81482 | 1.0712 | 0.79193 | 0.6134 | 13.2431 | 13.3484 | 13.3163 | 13.4033 | 13.3759 | 8.7708 | 8.67 | 110.7605 | 110.582 | -12.3413 | 110.8383 | 110.7834 | 0.20142 | -12.7487 | 118.7393 | 118.6386 | -0.009156 | 123.2117 | 123.2849 | 4.6463 | -0.036622 | 111.0397 | 110.6323 | 110.701 | -12.7991 | 123.3719 | 123.3444 | 123.317 | -4.7424
2975.5156 | 123.4451 | -109.9869 | 13.3575 | -0.15564 | 0.018867 | 0.0015765 | 0.014531 | -0.018912 | 0.0031894 | 0.0014847 | -0.14168 | 0.022371 | -0.0087222 | 0.012068 | -0.0020764 | 0.0089295 | 0.81024 | 0.83313 | 0.74158 | 0.83771 | 0.99335 | 0.74158 | 0.56763 | 13.2614 | 13.353 | 13.3072 | 13.3804 | 13.3118 | 8.7708 | 8.67 | 110.7285 | 110.5545 | -12.3642 | 110.82 | 110.8246 | 0.27008 | -12.5473 | 118.7576 | 118.6569 | 0.022888 | 123.2483 | 123.2941 | 4.6371 | -0.045776 | 110.9802 | 110.7971 | 110.7285 | -12.7899 | 123.3673 | 123.2986 | 123.3398 | -4.6875
2976.5156 | 123.4177 | -110.0052 | 13.3163 | -0.1709 | 0.019081 | 0.0045673 | 0.016026 | -0.019766 | 0.00062595 | -1.0724e-05 | -0.11116 | 0.026216 | -0.0080814 | 0.0097176 | -0.003999 | 0.0093567 | 0.76904 | 0.80109 | 0.70038 | 0.80566 | 1.0025 | 0.737 | 0.56305 | 13.1882 | 13.2889 | 13.266 | 13.3438 | 13.2935 | 8.7753 | 8.67 | 110.7422 | 110.5682 | -12.3138 | 110.8063 | 110.8109 | 0.24262 | -12.5473 | 118.7805 | 118.6752 | 0.027466 | 123.1934 | 123.2712 | 4.5959 | -0.022888 | 111.0077 | 110.7742 | 110.7056 | -12.7533 | 123.349 | 123.2986 | 123.2941 | -4.6463
2977.5156 | 123.4589 | -110.0052 | 13.298 | -0.086975 | 0.01844 | 0.0024311 | 0.013463 | -0.020621 | 0.0027622 | -0.0017197 | -0.065384 | 0.023011 | -0.0061588 | 0.011427 | -0.0031446 | 0.0080749 | 0.83313 | 0.85602 | 0.737 | 0.83771 | 0.99335 | 0.76446 | 0.57678 | 13.2111 | 13.3026 | 13.2614 | 13.3575 | 13.2889 | 8.7799 | 8.67 | 110.7697 | 110.582 | -12.3047 | 110.8612 | 110.8429 | 0.26093 | -12.4649 | 118.7851 | 118.6752 | 0.059509 | 123.2162 | 123.2666 | 4.5914 | -0.009156 | 110.9985 | 110.8383 | 110.7422 | -12.7213 | 123.3627 | 123.2941 | 123.3078 | -4.628
2978.5156 | 123.4039 | -110.0464 | 13.3026 | -0.27008 | 0.014595 | 0.0043537 | 0.014744 | -0.021262 | -0.00086945 | -0.00065152 | -0.16457 | 0.022584 | -0.0078678 | 0.011213 | -0.0037854 | 0.011066 | 0.76446 | 0.80566 | 0.68665 | 0.81482 | 1.03 | 0.74616 | 0.57678 | 13.1241 | 13.2477 | 13.2019 | 13.2797 | 13.2477 | 8.7753 | 8.67 | 110.7925 | 110.6232 | -12.2726 | 110.8521 | 110.8612 | 0.23804 | -12.5381 | 118.8217 | 118.7164 | -0.022888 | 123.1705 | 123.2483 | 4.5319 | -0.054931 | 111.0764 | 110.8109 | 110.733 | -12.7258 | 123.3261 | 123.2941 | 123.2941 | -4.6326
2979.5156 | 123.3444 | -110.0006 | 13.3163 | -0.094604 | 0.018226 | 0.0037127 | 0.013676 | -0.020407 | 0.00083955 | 0.0021255 | -0.14931 | 0.022798 | -0.011927 | 0.010999 | -0.0012218 | 0.0097839 | 0.82398 | 0.8606 | 0.73242 | 0.83771 | 0.99792 | 0.73242 | 0.56763 | 13.1424 | 13.2385 | 13.1973 | 13.2523 | 13.2065 | 8.7799 | 8.67 | 110.733 | 110.5682 | -12.3184 | 110.8612 | 110.8383 | 0.27008 | -12.4924 | 118.7805 | 118.6707 | -0.064087 | 123.143 | 123.1979 | 4.5273 | -0.10986 | 110.9985 | 110.8246 | 110.733 | -12.7487 | 123.2529 | 123.2071 | 123.2391 | -4.6463
2980.5156 | 123.4085 | -110.1379 | 13.2294 | -0.17853 | 0.013527 | 0.0022175 | 0.01389 | -0.019553 | -0.0032192 | -0.00065152 | -0.011978 | 0.021089 | -0.012995 | 0.012708 | -0.0031446 | 0.0097839 | 0.82855 | 0.70038 | 0.68207 | 0.83313 | 1.0483 | 0.78735 | 0.59967 | 13.0646 | 13.1699 | 13.1332 | 13.2477 | 13.1744 | 8.7799 | 8.6746 | 110.9253 | 110.7376 | -12.1811 | 110.8383 | 110.9711 | 0.23346 | -12.4008 | 118.9178 | 118.8126 | 0.018311 | 123.2025 | 123.2712 | 4.4586 | -0.054932 | 111.1862 | 110.9665 | 110.82 | -12.6297 | 123.3856 | 123.3124 | 123.3078 | -4.5547
2981.5156 | 123.4268 | -110.1288 | 13.2019 | -0.14038 | 0.019508 | 0.00072209 | 0.01389 | -0.017844 | 0.0025486 | 0.0019119 | -0.14931 | 0.022584 | -0.0063724 | 0.013349 | -0.0020764 | 0.0091431 | 0.7782 | 0.83771 | 0.71869 | 0.82398 | 0.99335 | 0.72327 | 0.56763 | 13.0783 | 13.1882 | 13.1104 | 13.1927 | 13.147 | 8.7708 | 8.6746 | 110.8521 | 110.6964 | -12.2086 | 110.9665 | 110.9528 | 0.25635 | -12.4237 | 118.8995 | 118.8034 | -0.009155 | 123.2071 | 123.2391 | 4.4357 | -0.054931 | 111.1221 | 110.907 | 110.8475 | -12.6343 | 123.3215 | 123.2758 | 123.317 | -4.5273
2982.5156 | 123.4039 | -110.1746 | 13.1699 | -0.20142 | 0.01609 | 0.0020037 | 0.015172 | -0.021262 | -0.0038602 | -0.00043792 | -1.1793 | 0.025789 | -0.010004 | 0.011213 | -0.0061352 | 0.0087157 | 0.74616 | 0.79651 | 0.70038 | 0.79193 | 0.99792 | 0.73242 | 0.56763 | 13.0325 | 13.1104 | 13.0966 | 13.2111 | 13.147 | 8.7662 | 8.6655 | 110.907 | 110.7422 | -12.1719 | 110.9711 | 110.9665 | 0.2243 | -12.4237 | 118.9407 | 118.84 | 0.041199 | 123.2071 | 123.2712 | 4.4312 | -0.022888 | 111.1725 | 110.9207 | 110.8749 | -12.6022 | 123.3856 | 123.3215 | 123.2849 | -4.5044
2983.5156 | 123.436 | -110.1837 | 13.1424 | -0.056458 | 0.017586 | 0.0043537 | 0.015599 | -0.019126 | 0.0031894 | 0.0010575 | 0.37712 | 0.020448 | -0.0089358 | 0.01164 | -0.00058103 | 0.0091431 | 0.81024 | 0.86517 | 0.737 | 0.84228 | 1.0071 | 0.76446 | 0.61798 | 13.0554 | 13.1332 | 13.0875 | 13.1378 | 13.0875 | 8.7799 | 8.6746 | 110.9482 | 110.8017 | -12.1353 | 111.0489 | 111.026 | 0.2243 | -12.3322 | 118.9636 | 118.8583 | -0.004578 | 123.2391 | 123.2712 | 4.4128 | -0.054932 | 111.1908 | 110.994 | 110.9207 | -12.5244 | 123.3215 | 123.2712 | 123.317 | -4.4678
2984.5156 | 123.4039 | -110.2478 | 13.1195 | -0.056458 | 0.015663 | 0.0022175 | 0.013676 | -0.018485 | -0.001083 | -0.00022432 | -0.13405 | 0.023225 | -0.012567 | 0.011213 | -0.0031446 | 0.010211 | 0.74616 | 0.80566 | 0.69122 | 0.79651 | 1.0025 | 0.737 | 0.56763 | 12.9547 | 13.06 | 13.0051 | 13.1058 | 13.0508 | 8.7799 | 8.67 | 110.9848 | 110.8154 | -12.117 | 111.0535 | 111.0443 | 0.22888 | -12.3734 | 119.0277 | 118.9178 | -0.013733 | 123.2025 | 123.2529 | 4.335 | -0.068665 | 111.2503 | 110.994 | 110.939 | -12.5519 | 123.3536 | 123.2986 | 123.3078 | -4.4495
2985.5156 | 123.4222 | -110.1883 | 13.1287 | -0.079346 | 0.017372 | 0.0020037 | 0.014103 | -0.019553 | 0.0019078 | 0.0021255 | -0.034867 | 0.02173 | -0.0072268 | 0.01164 | 0.00027337 | 0.0076477 | 0.81482 | 0.84686 | 0.72784 | 0.84228 | 1.0025 | 0.737 | 0.55389 | 12.9913 | 13.0875 | 13.028 | 13.0737 | 13.0417 | 8.7708 | 8.67 | 110.9253 | 110.7422 | -12.1262 | 111.0352 | 111.0306 | 0.28839 | -12.3138 | 118.959 | 118.8583 | -0.054932 | 123.1796 | 123.2162 | 4.3579 | -0.086975 | 111.1908 | 111.0031 | 110.9161 | -12.5748 | 123.262 | 123.23 | 123.2758 | -4.4586
2986.5156 | 123.4039 | -110.2798 | 13.0783 | -0.19379 | 0.01609 | 0.0045673 | 0.013249 | -0.020407 | -1.505e-05 | 0.00063028 | -0.12642 | 0.020448 | -0.012354 | 0.010572 | -0.0029308 | 0.0097839 | 0.78278 | 0.76904 | 0.67749 | 0.80566 | 1.0529 | 0.76446 | 0.59052 | 12.9135 | 12.9913 | 12.9639 | 13.0737 | 13.0096 | 8.7799 | 8.6792 | 111.0443 | 110.8704 | -12.0255 | 111.0489 | 111.0855 | 0.21515 | -12.2955 | 119.0598 | 118.959 | -0.004578 | 123.1934 | 123.2437 | 4.2847 | -0.068664 | 111.3327 | 111.0626 | 110.9573 | -12.4878 | 123.3536 | 123.2895 | 123.2712 | -4.3991
2987.5156 | 123.4268 | -110.289 | 13.0325 | -0.23956 | 0.016945 | 0.0024311 | 0.014103 | -0.01998 | 0.0012668 | 0.00063028 | -0.0043486 | 0.022798 | -0.011286 | 0.011427 | -0.0027172 | 0.0087157 | 0.83313 | 0.86975 | 0.737 | 0.82855 | 1.0117 | 0.75989 | 0.61798 | 12.941 | 13.0142 | 12.9501 | 13.0142 | 12.9684 | 8.7708 | 8.67 | 111.0489 | 110.907 | -12.0209 | 111.1588 | 111.1176 | 0.21057 | -12.1994 | 119.0598 | 118.959 | -0.018311 | 123.23 | 123.2391 | 4.2801 | -0.064087 | 111.3007 | 111.1221 | 111.026 | -12.4146 | 123.3032 | 123.2574 | 123.3032 | -4.3625
2988.5156 | 123.3994 | -110.3668 | 12.9913 | -0.018311 | 0.018654 | 0.0013629 | 0.014958 | -0.016776 | 0.0019078 | -0.00022432 | 0.033798 | 0.023225 | -0.009363 | 0.0099314 | -0.0012218 | 0.011066 | 0.78278 | 0.80109 | 0.6958 | 0.81024 | 0.99335 | 0.70038 | 0.54932 | 12.8586 | 12.9364 | 12.8723 | 12.9684 | 12.9456 | 8.7708 | 8.6655 | 111.0672 | 110.9161 | -11.998 | 111.1679 | 111.1771 | 0.26093 | -12.2086 | 119.1376 | 119.0323 | -0.022888 | 123.2254 | 123.2391 | 4.2068 | -0.045776 | 111.3602 | 111.1496 | 111.0626 | -12.442 | 123.3353 | 123.3124 | 123.3032 | -4.3259
2989.5156 | 123.4268 | -110.3714 | 12.9776 | -0.056458 | 0.018226 | 0.0011493 | 0.013463 | -0.019553 | 0.0010532 | 0.0016983 | -0.11116 | 0.024293 | -0.011286 | 0.0099314 | -0.00229 | 0.0093567 | 0.79651 | 0.83313 | 0.71869 | 0.82398 | 0.98877 | 0.73242 | 0.55847 | 12.9227 | 12.9547 | 12.9089 | 12.9959 | 12.9318 | 8.7753 | 8.6792 | 111.1038 | 110.9299 | -11.9888 | 111.2045 | 111.1954 | 0.2655 | -12.1811 | 119.1467 | 119.0506 | 0.018311 | 123.2941 | 123.2803 | 4.2297 | -0.045776 | 111.3602 | 111.1679 | 111.0901 | -12.4191 | 123.3673 | 123.3032 | 123.3261 | -4.2984
2990.5156 | 123.4039 | -110.4126 | 12.941 | 0.14191 | 0.015663 | 0.0015765 | 0.013249 | -0.016135 | -0.00022865 | 0.0016983 | -0.10353 | 0.022584 | -0.01214 | 0.011213 | -0.0037854 | 0.0097839 | 0.75531 | 0.78278 | 0.66834 | 0.78735 | 1.0025 | 0.72784 | 0.54932 | 12.7853 | 12.8952 | 12.8403 | 12.9639 | 12.9044 | 8.7708 | 8.6746 | 111.1404 | 110.9619 | -11.9385 | 111.1954 | 111.2 | 0.23804 | -12.1857 | 119.1834 | 119.0872 | 0.022888 | 123.1979 | 123.2529 | 4.1656 | -0.036621 | 111.4151 | 111.1679 | 111.0809 | -12.3917 | 123.3765 | 123.317 | 123.3078 | -4.2664
2991.5156 | 123.4955 | -110.3806 | 12.9227 | -0.12512 | 0.017799 | 0.0015765 | 0.014744 | -0.018698 | 0.00083955 | 0.0010575 | -0.080643 | 0.022584 | -0.009363 | 0.010572 | -0.00015383 | 0.011493 | 0.78735 | 0.82855 | 0.71869 | 0.82398 | 0.98877 | 0.72327 | 0.54932 | 12.822 | 12.9089 | 12.8448 | 12.8906 | 12.8677 | 8.7708 | 8.67 | 111.1038 | 110.9299 | -11.9339 | 111.2091 | 111.2045 | 0.27466 | -12.1353 | 119.1513 | 119.0506 | -0.032043 | 123.2025 | 123.2254 | 4.1748 | -0.054931 | 111.3693 | 111.1679 | 111.0992 | -12.3734 | 123.2712 | 123.2483 | 123.2895 | -4.2526
2992.5156 | 123.4039 | -110.4446 | 12.886 | -0.20142 | 0.014381 | 0.0039263 | 0.013463 | -0.01998 | -0.0021512 | -0.0021469 | 0.0032804 | 0.021943 | -0.0097904 | 0.013563 | -0.0020764 | 0.0093567 | 0.72784 | 0.67291 | 0.90637 | 0.96588 | 1.0254 | 0.76446 | 0.59052 | 12.7121 | 12.8494 | 12.8036 | 12.9135 | 12.8769 | 8.7662 | 8.67 | 111.2091 | 111.0352 | -11.8607 | 111.1176 | 111.4105 | 0.37537 | -12.1582 | 119.2108 | 119.1147 | 0.027466 | 123.1567 | 123.2483 | 4.1336 | -0.009155 | 111.47 | 111.1725 | 111.351 | -12.2955 | 123.3582 | 123.3215 | 123.2941 | -4.216
2993.5156 | 123.4314 | -110.4584 | 12.8632 | -0.10223 | 0.019508 | 0.0049945 | 0.01624 | -0.020407 | 0.0010532 | -1.0724e-05 | -0.14168 | 0.02173 | -0.012781 | 0.012495 | -0.0018628 | 0.0085021 | 0.75531 | 0.80566 | 0.68665 | 0.81024 | 0.97504 | 0.72784 | 0.55847 | 12.7533 | 12.8448 | 12.7853 | 12.8677 | 12.8128 | 8.7708 | 8.6746 | 111.1862 | 111.0168 | -11.8881 | 111.264 | 111.2686 | 0.25177 | -12.1078 | 119.2291 | 119.133 | 0.004578 | 123.2117 | 123.2437 | 4.1107 | -0.050354 | 111.4334 | 111.2137 | 111.145 | -12.3047 | 123.3261 | 123.2712 | 123.3032 | -4.1885
2994.5156 | 123.4039 | -110.5133 | 12.854 | -0.28534 | 0.015449 | 0.0047809 | 0.014958 | -0.01763 | -0.0017238 | -0.00022432 | -0.16457 | 0.02173 | -0.010645 | 0.011427 | -0.0033582 | 0.0095703 | 0.72327 | 0.7782 | 0.66834 | 0.7782 | 0.99792 | 0.70953 | 0.54932 | 12.6801 | 12.7808 | 12.7304 | 12.8448 | 12.7899 | 8.7708 | 8.6609 | 111.2228 | 111.0626 | -11.8561 | 111.2915 | 111.2915 | 0.22888 | -12.1307 | 119.2841 | 119.1742 | -0.009155 | 123.1934 | 123.2437 | 4.0695 | -0.064087 | 111.5112 | 111.2366 | 111.1816 | -12.3047 | 123.3582 | 123.3032 | 123.2941 | -4.1931
2995.5156 | 123.4406 | -110.5591 | 12.7945 | -0.13275 | 0.018867 | 0.0037127 | 0.016026 | -0.020407 | -0.00022865 | 0.00063028 | -0.12642 | 0.024934 | -0.008295 | 0.010999 | -0.0016492 | 0.010638 | 0.74158 | 0.77362 | 0.67291 | 0.79651 | 0.97961 | 0.70496 | 0.55389 | 12.6572 | 12.767 | 12.7121 | 12.8128 | 12.7716 | 8.7708 | 8.6609 | 111.264 | 111.113 | -11.8149 | 111.3327 | 111.3556 | 0.24262 | -12.0529 | 119.3298 | 119.22 | 0.01831 | 123.2162 | 123.2712 | 4.0512 | -0.022889 | 111.5387 | 111.3007 | 111.232 | -12.2406 | 123.3719 | 123.3307 | 123.3261 | -4.1336
2996.5156 | 123.4085 | -110.5728 | 12.767 | -0.23956 | 0.012245 | 0.0026447 | 0.014958 | -0.018912 | -0.0025784 | -0.00022432 | -0.31715 | 0.023011 | -0.009363 | 0.012495 | -0.0042126 | 0.0097839 | 0.737 | 0.76446 | 0.67291 | 0.94757 | 0.99335 | 0.737 | 0.56763 | 12.6297 | 12.6938 | 12.6892 | 12.7853 | 12.7258 | 8.7616 | 8.6655 | 111.3098 | 111.1404 | -11.7737 | 111.3373 | 111.5204 | 0.37994 | -12.03 | 119.3344 | 119.2383 | 0.01831 | 123.2025 | 123.262 | 4.0237 | -0.041199 | 111.5662 | 111.3098 | 111.2457 | -12.1994 | 123.3582 | 123.2986 | 123.2666 | -4.1016
2997.5156 | 123.4268 | -110.5911 | 12.7533 | -0.12512 | 0.017586 | 0.0032855 | 0.014531 | -0.020407 | 0.00062595 | -0.0012923 | -0.050125 | 0.022371 | -0.010431 | 0.009504 | -0.0018628 | 0.0072205 | 0.75989 | 0.78735 | 0.6958 | 0.80566 | 0.97046 | 0.71411 | 0.54474 | 12.6251 | 12.7304 | 12.6709 | 12.7579 | 12.6984 | 8.7708 | 8.6746 | 111.3052 | 111.1359 | -11.7828 | 111.3785 | 111.3968 | 0.26093 | -11.9934 | 119.3619 | 119.2657 | 0.004578 | 123.2162 | 123.262 | 3.9963 | -0.054932 | 111.5616 | 111.351 | 111.2869 | -12.2086 | 123.349 | 123.2895 | 123.3215 | -4.0787
2998.5156 | 123.4268 | -110.5545 | 12.7762 | -0.20142 | 0.012031 | 0.0026447 | 0.014531 | -0.023184 | -0.0017238 | -0.0019333 | -0.11879 | 0.021516 | -0.011713 | 0.012281 | -0.0037854 | 0.0087157 | 0.74158 | 0.81024 | 0.68207 | 0.76904 | 0.97504 | 0.72327 | 0.55389 | 12.5748 | 12.6801 | 12.6251 | 12.7304 | 12.6617 | 8.7616 | 8.6746 | 111.2778 | 111.1084 | -11.8011 | 111.3647 | 111.3235 | 0.21515 | -12.0346 | 119.3161 | 119.2291 | -0.045776 | 123.1293 | 123.1796 | 3.9505 | -0.11444 | 111.5295 | 111.2961 | 111.2366 | -12.2223 | 123.2849 | 123.2162 | 123.2346 | -4.1016
2999.5156 | 123.4451 | -110.6644 | 12.6892 | -0.2243 | 0.016731 | 0.0043537 | 0.014958 | -0.020621 | -0.00065585 | -0.00065152 | -0.12642 | 0.020875 | -0.008295 | 0.012495 | -0.0050672 | 0.0089295 | 0.75073 | 0.75531 | 0.67291 | 0.77362 | 0.97961 | 0.70953 | 0.53558 | 12.561 | 12.6572 | 12.6022 | 12.6892 | 12.6205 | 8.7662 | 8.6655 | 111.3739 | 111.2 | -11.7096 | 111.4197 | 111.438 | 0.23804 | -11.9385 | 119.4305 | 119.3298 | 0 | 123.2254 | 123.2666 | 3.9368 | -0.068665 | 111.644 | 111.4151 | 111.3373 | -12.1536 | 123.3536 | 123.2849 | 123.3215 | -4.0237
3000.5156 | 123.4222 | -110.6827 | 12.6663 | -0.19379 | 0.01374 | 0.0028583 | 0.013463 | -0.018912 | -0.0042874 | 0.00020288 | -0.14168 | 0.021089 | -0.01214 | 0.010359 | -0.0029308 | 0.010638 | 0.78278 | 0.84686 | 0.74158 | 0.82855 | 0.95215 | 0.72327 | 0.5722 | 12.5336 | 12.6343 | 12.6068 | 12.6526 | 12.6114 | 8.7662 | 8.6655 | 111.4059 | 111.2549 | -11.7142 | 111.5295 | 111.5112 | 0.25635 | -11.8835 | 119.4489 | 119.3481 | -0.013733 | 123.2162 | 123.2895 | 3.9413 | -0.054932 | 111.6348 | 111.4655 | 111.4243 | -12.0941 | 123.3353 | 123.2941 | 123.317 | -4.0009
3001.5156 | 123.4314 | -110.7056 | 12.6343 | -0.13275 | 0.018654 | 0.0022175 | 0.01389 | -0.018057 | 0.0012668 | 0.00041648 | -0.15694 | 0.020875 | -0.0085086 | 0.011427 | -0.0025036 | 0.0080749 | 0.75531 | 0.79193 | 0.68665 | 0.80109 | 0.97504 | 0.70496 | 0.54474 | 12.5244 | 12.6114 | 12.5702 | 12.6389 | 12.5793 | 8.7708 | 8.6609 | 111.4105 | 111.2503 | -11.6592 | 111.4975 | 111.5067 | 0.25635 | -11.879 | 119.4763 | 119.3665 | 0.004578 | 123.23 | 123.2758 | 3.9093 | -0.054931 | 111.6806 | 111.4609 | 111.3922 | -12.0895 | 123.3444 | 123.2849 | 123.317 | -3.9734
3002.5156 | 123.4634 | -110.7147 | 12.5977 | -0.16327 | 0.013954 | 0.0032855 | 0.014531 | -0.01998 | -0.0049282 | -0.0015061 | -0.15694 | 0.020662 | -0.011072 | 0.011427 | -0.003999 | 0.0082885 | 0.78735 | 0.89264 | 0.76446 | 0.83313 | 0.95215 | 0.73242 | 0.55847 | 12.5107 | 12.6251 | 12.5885 | 12.5977 | 12.5381 | 8.7616 | 8.67 | 111.4471 | 111.2732 | -11.6455 | 111.6074 | 111.5479 | 0.27466 | -11.8103 | 119.4763 | 119.3848 | 0 | 123.2254 | 123.3032 | 3.9185 | -0.059509 | 111.6669 | 111.5021 | 111.4792 | -12.0392 | 123.3124 | 123.2529 | 123.3398 | -3.9276
3003.5156 | 123.3856 | -110.7651 | 12.5977 | -0.43793 | 0.016945 | 0.0028583 | 0.017094 | -0.018271 | -0.00065585 | -0.00043792 | -0.15694 | 0.022584 | -0.0087222 | 0.010145 | -0.0018628 | 0.0078613 | 0.70496 | 0.77362 | 0.66376 | 0.75989 | 0.97961 | 0.71869 | 0.54932 | 12.4329 | 12.5198 | 12.4649 | 12.6022 | 12.5107 | 8.7662 | 8.6655 | 111.4838 | 111.3144 | -11.618 | 111.5387 | 111.525 | 0.21057 | -11.8927 | 119.5312 | 119.4305 | 0.004578 | 123.1979 | 123.23 | 3.7994 | -0.086975 | 111.7447 | 111.47 | 111.4288 | -12.0483 | 123.3673 | 123.2758 | 123.2849 | -3.9322
3004.5156 | 123.4818 | -110.7605 | 12.5244 | -0.14801 | 0.012245 | 0.0037127 | 0.012822 | -0.022116 | -0.0038602 | 0.0019119 | -0.11116 | 0.018312 | -0.011072 | 0.012281 | -0.0031446 | 0.0087157 | 0.80566 | 0.91553 | 0.79193 | 0.85602 | 0.93842 | 0.73242 | 0.5722 | 12.4878 | 12.6205 | 12.5473 | 12.5107 | 12.4741 | 8.7616 | 8.6655 | 111.4929 | 111.3327 | -11.586 | 111.676 | 111.6165 | 0.28381 | -11.7188 | 119.5221 | 119.426 | -0.013733 | 123.2483 | 123.3078 | 3.8818 | -0.050354 | 111.6989 | 111.5662 | 111.5524 | -11.9522 | 123.2712 | 123.2346 | 123.381 | -3.8589
3005.5156 | 123.4177 | -110.82 | 12.529 | -0.17853 | 0.016517 | 0.0017901 | 0.015172 | -0.018698 | 0.0021214 | 0.0010575 | -0.16457 | 0.023652 | -0.0087222 | 0.013136 | -0.00058103 | 0.0087157 | 0.72784 | 0.76904 | 0.65918 | 0.76904 | 0.97046 | 0.71411 | 0.54016 | 12.3825 | 12.4603 | 12.4146 | 12.5381 | 12.4741 | 8.7662 | 8.6655 | 111.5341 | 111.3602 | -11.5585 | 111.5891 | 111.5891 | 0.22888 | -11.8011 | 119.5862 | 119.4855 | 0.009155 | 123.2025 | 123.2346 | 3.7491 | -0.054932 | 111.7905 | 111.5479 | 111.4792 | -11.9888 | 123.3582 | 123.2941 | 123.2803 | -3.8635
3006.5156 | 123.3994 | -110.8292 | 12.5061 | -0.14801 | 0.015663 | 0.0037127 | 0.014103 | -0.017844 | 0.0010532 | 0.00063028 | -0.12642 | 0.022371 | -0.011927 | 0.012281 | -0.003999 | 0.0099975 | 0.72327 | 0.78278 | 0.65918 | 0.78278 | 0.97961 | 0.70496 | 0.52185 | 12.3596 | 12.4466 | 12.3825 | 12.5198 | 12.4512 | 8.7616 | 8.6746 | 111.5341 | 111.351 | -11.5265 | 111.6119 | 111.6119 | 0.26093 | -11.7828 | 119.5908 | 119.5038 | 0.013732 | 123.1888 | 123.2117 | 3.7079 | -0.054932 | 111.8088 | 111.5524 | 111.4883 | -11.9843 | 123.349 | 123.2803 | 123.2758 | -3.8315
3007.5156 | 123.3994 | -110.8566 | 12.4786 | -0.033569 | 0.016731 | 0.0024311 | 0.014744 | -0.016776 | -0.0017238 | -0.00022432 | -0.11116 | 0.023225 | -0.0091494 | 0.012708 | -0.0044262 | 0.0078613 | 0.737 | 0.76904 | 0.6546 | 0.76904 | 0.97504 | 0.70953 | 0.53101 | 12.3413 | 12.41 | 12.3505 | 12.4695 | 12.4237 | 8.7708 | 8.6655 | 111.5662 | 111.3876 | -11.5036 | 111.6257 | 111.6257 | 0.23804 | -11.7416 | 119.6274 | 119.5221 | -0.009156 | 123.1979 | 123.2071 | 3.685 | -0.054932 | 111.8317 | 111.5936 | 111.5112 | -11.9476 | 123.3261 | 123.2803 | 123.2666 | -3.8132
3008.5156 | 123.4863 | -110.8932 | 12.442 | -0.1709 | 0.010536 | 0.0041401 | 0.011113 | -0.019126 | -0.0032192 | 0.0019119 | -0.12642 | 0.022371 | -0.012354 | 0.010999 | -0.0050672 | 0.0082885 | 0.80109 | 0.90637 | 0.78735 | 0.84686 | 0.93842 | 0.73242 | 0.58136 | 12.3734 | 12.5061 | 12.4603 | 12.4329 | 12.3642 | 8.757 | 8.67 | 111.6257 | 111.4746 | -11.5036 | 111.7996 | 111.7401 | 0.2655 | -11.6409 | 119.6503 | 119.5633 | -0.009156 | 123.2666 | 123.3536 | 3.7903 | -0.07782 | 111.8317 | 111.6943 | 111.6806 | -11.8607 | 123.3261 | 123.2574 | 123.3994 | -3.772
3009.5156 | 123.4177 | -110.9299 | 12.4054 | -0.20905 | 0.015022 | 0.0047809 | 0.015599 | -0.020194 | -0.00044225 | -0.0010787 | 0.18639 | 0.022371 | -0.0089358 | 0.0092904 | -0.0025036 | 0.0070067 | 0.71411 | 0.82855 | 0.92468 | 0.89722 | 1.0117 | 0.72327 | 0.54932 | 12.2589 | 12.3734 | 12.323 | 12.4283 | 12.3642 | 8.7616 | 8.6609 | 111.6531 | 111.4792 | -11.3937 | 111.7584 | 111.8271 | 0.3479 | -11.6913 | 119.6915 | 119.5908 | 0.022888 | 123.1888 | 123.2529 | 3.6621 | -0.041199 | 111.9415 | 111.644 | 111.8546 | -11.8561 | 123.3582 | 123.2941 | 123.3032 | -3.7445
3010.5156 | 123.4451 | -110.9665 | 12.3779 | -0.20142 | 0.011818 | 0.0045673 | 0.012608 | -0.01998 | -0.001083 | -1.0724e-05 | -0.12642 | 0.020662 | -0.011286 | 0.011213 | -0.0042126 | 0.0099975 | 0.78278 | 0.87891 | 0.76904 | 0.84228 | 0.93842 | 0.72327 | 0.54016 | 12.3047 | 12.4054 | 12.323 | 12.3825 | 12.3459 | 8.7616 | 8.67 | 111.6898 | 111.5067 | -11.4395 | 111.8454 | 111.8088 | 0.30212 | -11.5952 | 119.7281 | 119.6365 | 0.004577 | 123.2712 | 123.2895 | 3.653 | -0.032044 | 111.9049 | 111.7493 | 111.7355 | -11.8378 | 123.349 | 123.3124 | 123.3719 | -3.7079
3011.5312 | 123.5138 | -110.9299 | 12.3184 | 0.2182 | 0.015236 | 0.0022175 | 0.014317 | -0.020621 | 0.0027622 | 0.0029801 | 0.15587 | 0.021516 | -0.011713 | 0.011854 | 0.001128 | 0.0072205 | 0.78278 | 0.81024 | 0.71411 | 0.79651 | 0.94757 | 0.71869 | 0.54016 | 12.3138 | 12.3779 | 12.3276 | 12.3184 | 12.2452 | 8.7616 | 8.6655 | 111.6486 | 111.47 | -11.3708 | 111.7401 | 111.7264 | 0.25635 | -11.5356 | 119.6915 | 119.5953 | 0 | 123.2437 | 123.2574 | 3.6621 | -0.073242 | 111.8774 | 111.7126 | 111.644 | -11.7783 | 123.2483 | 123.175 | 123.3078 | -3.653
3012.5156 | 123.4772 | -110.9573 | 12.2955 | -0.16327 | 0.01139 | 0.0052081 | 0.013249 | -0.018057 | -0.0030056 | 0.00084388 | -0.11879 | 0.019593 | -0.011499 | 0.012068 | -0.0025036 | 0.0095703 | 0.81024 | 0.89722 | 0.77362 | 0.83313 | 0.92926 | 0.72784 | 0.5722 | 12.2772 | 12.3917 | 12.323 | 12.3138 | 12.2772 | 8.7616 | 8.67 | 111.6852 | 111.5295 | -11.3663 | 111.8546 | 111.7905 | 0.26093 | -11.4853 | 119.7189 | 119.6274 | 0.018311 | 123.2346 | 123.2803 | 3.653 | -0.01831 | 111.8866 | 111.7676 | 111.731 | -11.7233 | 123.2712 | 123.2346 | 123.349 | -3.6255
3013.5156 | 123.4039 | -111.0214 | 12.323 | -0.19379 | 0.015877 | 0.0054217 | 0.016667 | -0.020621 | 0.0012668 | -0.0025741 | -0.24086 | 0.024934 | -0.010431 | 0.011213 | -0.0035718 | 0.0099975 | 1.0025 | 0.70496 | 0.57678 | 0.72784 | 1.0025 | 0.737 | 0.55847 | 12.1857 | 12.2452 | 12.204 | 12.3367 | 12.2772 | 8.7616 | 8.6517 | 111.7584 | 111.5799 | -11.3205 | 111.7264 | 111.7493 | 0.16937 | -11.3205 | 119.783 | 119.6732 | 0.013733 | 123.2071 | 123.2254 | 3.5522 | -0.045776 | 112.0239 | 112.0239 | 111.5982 | -11.7645 | 123.3582 | 123.2986 | 123.2666 | -3.6713
3014.5156 | 123.4955 | -111.0214 | 12.2681 | -0.094604 | 0.011604 | 0.0056353 | 0.011754 | -0.019766 | -0.0019376 | 0.0019119 | -0.11879 | 0.019807 | -0.011286 | 0.010999 | -0.0029308 | 0.010211 | 0.78735 | 0.91553 | 0.78278 | 0.83313 | 0.9201 | 0.73242 | 0.5722 | 12.236 | 12.3734 | 12.3093 | 12.2543 | 12.2131 | 8.7524 | 8.6655 | 111.7538 | 111.5936 | -11.348 | 111.9369 | 111.8546 | 0.26093 | -11.4807 | 119.7739 | 119.6869 | -0.013733 | 123.2574 | 123.3307 | 3.6438 | -0.054931 | 111.9415 | 111.8088 | 111.8042 | -11.6959 | 123.2758 | 123.2346 | 123.3948 | -3.6026
3015.5156 | 123.3948 | -111.0992 | 12.2864 | -0.11749 | 0.01609 | 0.0034991 | 0.012608 | -0.020621 | 0.00041235 | 0.0014847 | -0.19508 | 0.023011 | -0.010858 | 0.013777 | -0.0014356 | 0.0085021 | 0.72327 | 0.78735 | 0.64545 | 0.75531 | 0.96588 | 0.67291 | 0.50812 | 12.1353 | 12.2086 | 12.1628 | 12.291 | 12.1811 | 8.757 | 8.6563 | 111.7722 | 111.6074 | -11.3205 | 111.8866 | 111.8546 | 0.24719 | -11.5631 | 119.8563 | 119.7556 | 0.004578 | 123.2346 | 123.262 | 3.5065 | -0.10529 | 112.0651 | 111.8225 | 111.7447 | -11.7783 | 123.3902 | 123.2803 | 123.3078 | -3.6301
3016.5156 | 123.4222 | -111.0672 | 12.2635 | -0.12512 | 0.016517 | 0.0015765 | 0.018376 | -0.017844 | 0.0055392 | 0.0023391 | -0.13405 | 0.023011 | -0.011072 | 0.013349 | -0.00036743 | 0.0042297 | 0.7782 | 0.8194 | 0.68665 | 0.79651 | 0.94757 | 0.70038 | 0.53101 | 12.3184 | 12.204 | 12.236 | 12.291 | 12.2406 | 8.757 | 8.6517 | 111.7676 | 111.5982 | -11.3159 | 111.8866 | 111.8637 | 0.2655 | -11.4853 | 119.8242 | 119.7189 | 0.027466 | 123.3856 | 123.3032 | 3.5843 | -0.022888 | 112.0148 | 111.8454 | 111.7538 | -11.7325 | 123.3582 | 123.3078 | 123.2712 | -3.6118
3017.5156 | 123.3948 | -111.1313 | 12.2131 | -0.20905 | 0.012245 | 0.0032855 | 0.014317 | -0.018698 | -1.505e-05 | 0.00020288 | -0.23323 | 0.023439 | -0.0091494 | 0.011427 | -0.0037854 | 0.0095703 | 0.74158 | 0.8194 | 0.68207 | 0.76446 | 0.95673 | 0.68665 | 0.54016 | 12.0712 | 12.1811 | 12.117 | 12.2269 | 12.1674 | 8.7524 | 8.6563 | 111.8179 | 111.6714 | -11.2564 | 111.9507 | 111.8958 | 0.2243 | -11.4716 | 119.8837 | 119.7876 | 0.013733 | 123.2025 | 123.2483 | 3.4607 | -0.045777 | 112.088 | 111.8729 | 111.8134 | -11.673 | 123.3582 | 123.2986 | 123.3124 | -3.5568
3018.5156 | 123.5046 | -111.1176 | 12.1857 | -0.19379 | 0.011818 | 0.0032855 | 0.012394 | -0.019766 | -0.0047146 | 0.0023391 | -0.057755 | 0.02173 | -0.01449 | 0.010145 | -0.0042126 | 0.010211 | 0.79193 | 0.90179 | 0.76446 | 0.84228 | 0.93842 | 0.71869 | 0.58136 | 12.1262 | 12.2498 | 12.204 | 12.1307 | 12.1033 | 8.7479 | 8.6609 | 111.8362 | 111.6989 | -11.2473 | 112.0193 | 111.9598 | 0.26092 | -11.3937 | 119.8654 | 119.7784 | -0.054932 | 123.2437 | 123.3215 | 3.5431 | -0.082398 | 112.056 | 111.9095 | 111.882 | -11.6043 | 123.2483 | 123.2208 | 123.3673 | -3.5248
3019.5156 | 123.3994 | -111.1633 | 12.1719 | -0.12512 | 0.013099 | 0.0026447 | 0.013035 | -0.020835 | 0.0021214 | 0.00020288 | -0.14931 | 0.021302 | -0.0087222 | 0.010999 | -0.00229 | 0.0076477 | 0.71411 | 0.75989 | 0.6546 | 0.75989 | 0.9613 | 0.69122 | 0.50354 | 12.1902 | 12.117 | 11.9614 | 12.204 | 12.1628 | 8.757 | 8.6609 | 111.8546 | 111.6669 | -11.2106 | 111.9232 | 111.9232 | 0.25635 | -11.4578 | 119.9203 | 119.8242 | 0.032043 | 123.3536 | 123.1247 | 3.3005 | -0.009155 | 112.1246 | 111.8774 | 111.8179 | -11.6684 | 123.3673 | 123.3261 | 123.2803 | -3.511
3020.5156 | 123.5413 | -111.1725 | 12.1124 | -0.048828 | 0.012672 | 0.0039263 | 0.011754 | -0.01998 | -0.0021512 | -0.00086512 | -0.080643 | 0.019807 | -0.010645 | 0.0069406 | -0.0044262 | 0.010425 | 0.79193 | 0.91095 | 0.79193 | 0.82855 | 0.93384 | 0.72327 | 0.56763 | 12.117 | 12.2269 | 12.1719 | 12.085 | 12.0346 | 8.7479 | 8.6609 | 111.8958 | 111.7401 | -11.1786 | 112.0834 | 112.001 | 0.26092 | -11.3205 | 119.9203 | 119.8334 | -0.027466 | 123.2895 | 123.3444 | 3.511 | -0.07782 | 112.1063 | 111.9644 | 111.9644 | -11.5448 | 123.2574 | 123.2071 | 123.3994 | -3.4515
3021.5312 | 123.5138 | -111.2091 | 12.03 | 0.24872 | 0.016304 | 0.0020037 | 0.013249 | -0.01763 | -0.00065585 | 0.0029801 | 0.20927 | 0.02173 | -0.009363 | 0.010145 | -0.0020764 | 0.0076477 | 0.82398 | 0.86517 | 0.75073 | 0.82398 | 0.92468 | 0.72327 | 0.56305 | 12.0758 | 12.0804 | 12.1033 | 12.0209 | 11.9751 | 8.7479 | 8.6563 | 111.9324 | 111.7722 | -11.1053 | 112.0743 | 112.0331 | 0.26093 | -11.2061 | 119.957 | 119.8654 | -0.009155 | 123.2849 | 123.3124 | 3.447 | -0.054931 | 112.1338 | 112.0331 | 111.9598 | -11.467 | 123.23 | 123.1842 | 123.2895 | -3.3737
3022.5156 | 123.555 | -111.2412 | 12.0255 | -0.033569 | 0.0096813 | 0.0045673 | 0.011754 | -0.019766 | -0.0019376 | 0.00063028 | -0.065384 | 0.020234 | -0.012567 | 0.01164 | -0.0037854 | 0.0091431 | 0.81482 | 0.91095 | 0.79651 | 0.83771 | 0.9201 | 0.73242 | 0.55389 | 12.0529 | 12.1582 | 12.1216 | 12.0346 | 11.9751 | 8.7524 | 8.6517 | 111.9736 | 111.795 | -11.1053 | 112.1521 | 112.0789 | 0.28381 | -11.2106 | 119.9936 | 119.8929 | 0.009155 | 123.2941 | 123.3627 | 3.4698 | -0.050354 | 112.1613 | 112.056 | 112.0377 | -11.4716 | 123.2758 | 123.2162 | 123.3994 | -3.3737
3023.5156 | 123.468 | -111.2686 | 12.0575 | -0.16327 | 0.012672 | 0.0052081 | 0.015172 | -0.018057 | 0.00062595 | 0.00084388 | -0.15694 | 0.022584 | -0.011499 | 0.010359 | -0.0033582 | 0.0080749 | 0.80566 | 0.88348 | 0.74158 | 0.82398 | 0.92468 | 0.71869 | 0.55847 | 11.9888 | 12.1033 | 12.03 | 12.0392 | 11.9568 | 8.7479 | 8.6563 | 111.9873 | 111.8271 | -11.1328 | 112.1521 | 112.0926 | 0.2655 | -11.2518 | 120.0165 | 119.9249 | -0.01831 | 123.2574 | 123.2986 | 3.3737 | -0.10071 | 112.1933 | 112.0743 | 112.0102 | -11.499 | 123.3078 | 123.2254 | 123.3719 | -3.4012
3024.5156 | 123.5321 | -111.264 | 12.0026 | -0.19379 | 0.011818 | 0.0030719 | 0.012822 | -0.018057 | -0.002792 | 0.00041648 | -3.0561 | 0.017884 | -0.011713 | 0.012068 | -0.0035718 | 0.0080749 | 0.81482 | 0.93842 | 0.80566 | 0.84228 | 0.90637 | 0.70496 | 0.54474 | 12.0575 | 11.9888 | 12.0621 | 11.998 | 11.9202 | 8.7479 | 8.6563 | 111.969 | 111.8088 | -11.0962 | 112.2025 | 112.1063 | 0.29755 | -11.1877 | 120.0119 | 119.9203 | -0.004577 | 123.3215 | 123.3261 | 3.4058 | -0.082397 | 112.1704 | 112.0789 | 112.0697 | -11.4578 | 123.262 | 123.1842 | 123.2529 | -3.3463
3025.5156 | 123.4268 | -111.319 | 11.9934 | -0.1709 | 0.013954 | 0.0043537 | 0.013249 | -0.019339 | -0.00022865 | -0.0010787 | -0.1722 | 0.022157 | -0.012995 | 0.010359 | -0.0037854 | 0.0085021 | 0.79193 | 0.87891 | 0.737 | 0.80566 | 0.9201 | 0.70038 | 0.54016 | 11.9247 | 12.0163 | 11.9568 | 11.9888 | 11.9247 | 8.7479 | 8.6563 | 112.0193 | 111.8591 | -11.0733 | 112.1979 | 112.1246 | 0.2655 | -11.2015 | 120.0668 | 119.9753 | -0.004577 | 123.2437 | 123.2758 | 3.3005 | -0.068664 | 112.2391 | 112.1109 | 112.056 | -11.4532 | 123.3078 | 123.2437 | 123.3353 | -3.3371
3026.5156 | 123.5275 | -111.3052 | 11.9476 | -0.086975 | 0.012031 | 0.0017901 | 0.013463 | -0.021262 | -0.0019376 | -1.0724e-05 | 0.0032804 | 0.020021 | -0.012995 | 0.012708 | -0.00229 | 0.0093567 | 0.79193 | 0.88348 | 0.76446 | 0.8194 | 0.90637 | 0.72327 | 0.55847 | 11.9705 | 12.0392 | 12.0163 | 11.9522 | 11.8652 | 8.7433 | 8.6517 | 112.0285 | 111.8637 | -11.0413 | 112.1887 | 112.1246 | 0.26093 | -11.1557 | 120.0485 | 119.957 | 0.004577 | 123.2758 | 123.3215 | 3.3646 | -0.082398 | 112.2116 | 112.0972 | 112.0697 | -11.3892 | 123.2574 | 123.1705 | 123.3444 | -3.2959
3027.5156 | 123.4955 | -111.3693 | 11.9293 | -0.12512 | 0.013099 | 0.0062763 | 0.012608 | -0.018057 | 0.0010532 | -0.0030013 | -0.13405 | 0.021089 | -0.012995 | 0.0088632 | -0.0020764 | 0.0093567 | 0.80566 | 0.88806 | 0.76446 | 0.82398 | 0.91095 | 0.71869 | 0.56763 | 11.9019 | 12.0255 | 11.9476 | 11.8973 | 11.8652 | 8.7433 | 8.6563 | 112.088 | 111.937 | -11.0184 | 112.2574 | 112.1933 | 0.25635 | -11.1237 | 120.1126 | 120.0256 | -0.032043 | 123.2712 | 123.317 | 3.2913 | -0.064087 | 112.2803 | 112.175 | 112.1338 | -11.3617 | 123.2666 | 123.2346 | 123.3948 | -3.273
3028.5156 | 123.5138 | -111.4014 | 11.8881 | 0.027466 | 0.0083997 | 0.0037127 | 0.010899 | -0.021262 | -0.0012966 | 0.00084388 | 0.026169 | 0.019807 | -0.013422 | 0.011213 | -0.003999 | 0.0070067 | 0.76904 | 0.85602 | 0.73242 | 0.80109 | 0.91553 | 0.70038 | 0.55389 | 11.8744 | 11.9476 | 11.9247 | 11.9019 | 11.8286 | 8.7341 | 8.6426 | 112.1017 | 111.9553 | -10.9726 | 112.2574 | 112.2025 | 0.24719 | -11.1191 | 120.1355 | 120.0439 | 0.013732 | 123.2758 | 123.3261 | 3.2822 | -0.05951 | 112.3169 | 112.1704 | 112.1338 | -11.3342 | 123.3032 | 123.23 | 123.349 | -3.2455
3029.5156 | 123.4818 | -111.4151 | 11.8698 | -0.11749 | 0.013954 | 0.0030719 | 0.010472 | -0.018271 | 0.0014804 | 0.00084388 | -0.16457 | 0.019807 | -0.013422 | 0.012068 | -0.0010082 | 0.0070067 | 0.81024 | 0.88806 | 0.75531 | 0.82398 | 0.90179 | 0.70953 | 0.55389 | 11.8561 | 11.9705 | 11.8881 | 11.8652 | 11.7828 | 8.7479 | 8.6609 | 112.1246 | 111.969 | -10.968 | 112.3032 | 112.2391 | 0.27008 | -11.0596 | 120.163 | 120.076 | -0.004578 | 123.2712 | 123.3032 | 3.2272 | -0.086975 | 112.3169 | 112.2253 | 112.1704 | -11.3159 | 123.2803 | 123.1979 | 123.3856 | -3.2089
3030.5156 | 123.4772 | -111.4563 | 11.8607 | 0.15717 | 0.012886 | 0.0041401 | 0.011113 | -0.020407 | -0.001083 | -0.0010787 | 0.18639 | 0.022371 | -0.011927 | 0.01164 | -0.0031446 | 0.0082885 | 0.75989 | 0.82855 | 0.73242 | 0.77362 | 0.89722 | 0.72327 | 0.54932 | 11.8057 | 11.8607 | 11.8332 | 11.8378 | 11.7554 | 8.7387 | 8.6517 | 112.1796 | 112.0056 | -10.9634 | 112.2849 | 112.2299 | 0.2243 | -11.1008 | 120.195 | 120.108 | -0.022888 | 123.262 | 123.2895 | 3.1815 | -0.10529 | 112.3535 | 112.2162 | 112.1887 | -11.3113 | 123.2941 | 123.2117 | 123.317 | -3.2089
3031.5156 | 123.5321 | -111.4517 | 11.792 | -0.14038 | 0.010109 | 0.0039263 | 0.013463 | -0.021262 | -0.0036464 | -0.0012923 | 0.041427 | 0.022157 | -0.013422 | 0.010786 | -0.0048534 | 0.0076477 | 0.96588 | 0.55389 | 0.62714 | 0.82855 | 0.88806 | 0.67749 | 0.5127 | 11.8149 | 11.9019 | 11.8698 | 11.7874 | 11.7462 | 8.7387 | 8.6472 | 112.1292 | 111.9644 | -10.9039 | 112.0056 | 112.2803 | 0.31586 | -10.8261 | 120.1904 | 120.0989 | -0.004577 | 123.2666 | 123.3215 | 3.2227 | -0.045776 | 112.3398 | 112.4176 | 112.0789 | -11.2793 | 123.2391 | 123.1979 | 123.3536 | -3.1448
3032.5156 | 123.5138 | -111.4883 | 11.7737 | -0.3006 | 0.01139 | 0.0056353 | 0.012608 | -0.020835 | -0.0019376 | 0.00063028 | 0.026169 | 0.020448 | -0.011713 | 0.010572 | -0.0033582 | 0.0080749 | 0.76446 | 0.79651 | 0.70953 | 0.7782 | 0.91553 | 0.6958 | 0.53558 | 11.7416 | 11.8195 | 11.792 | 11.7874 | 11.7325 | 8.7341 | 8.6517 | 112.1841 | 112.0239 | -10.8582 | 112.2849 | 112.2665 | 0.24261 | -11.0092 | 120.2225 | 120.1401 | 0.013733 | 123.23 | 123.2803 | 3.1403 | -0.041199 | 112.4039 | 112.2528 | 112.1979 | -11.2381 | 123.2758 | 123.2208 | 123.3078 | -3.1219
3033.5156 | 123.5458 | -111.5158 | 11.7599 | -0.064087 | 0.0090405 | 0.0024311 | 0.0096174 | -0.020194 | -0.00022865 | 0.00020288 | 0.056686 | 0.02173 | -0.010218 | 0.011427 | -0.0044262 | 0.010211 | 0.82398 | 0.89264 | 0.77362 | 0.8194 | 0.91553 | 0.71411 | 0.53101 | 11.8011 | 11.8515 | 11.8195 | 11.7645 | 11.6959 | 8.7387 | 8.6472 | 112.2299 | 112.0468 | -10.8444 | 112.4084 | 112.3352 | 0.28839 | -10.936 | 120.2545 | 120.163 | 0.004577 | 123.317 | 123.3353 | 3.1723 | -0.064087 | 112.4313 | 112.3398 | 112.2894 | -11.2289 | 123.2803 | 123.2117 | 123.3673 | -3.1128
3034.5156 | 123.5504 | -111.6211 | 11.6638 | 0.16479 | 0.012886 | 0.0013629 | 0.012608 | -0.020621 | 0.00019875 | -0.00022432 | 0.087204 | 0.021516 | -0.011286 | 0.009504 | -0.0012218 | 0.0093567 | 0.75989 | 0.81482 | 0.68665 | 0.76446 | 0.90179 | 0.72327 | 0.54016 | 11.7004 | 11.7325 | 11.7233 | 11.7325 | 11.6638 | 8.7341 | 8.6472 | 112.3444 | 112.1613 | -10.762 | 112.4359 | 112.3856 | 0.2243 | -10.9039 | 120.3552 | 120.2682 | 0.068665 | 123.3215 | 123.3444 | 3.0762 | 0 | 112.5229 | 112.381 | 112.3077 | -11.1237 | 123.3536 | 123.2849 | 123.3536 | -3.0167
3035.5156 | 123.5413 | -111.5616 | 11.7004 | -0.041199 | 0.011818 | 0.0041401 | 0.012822 | -0.019766 | -0.0019376 | 0.0010575 | -0.027237 | 0.021302 | -0.0097904 | 0.011213 | -0.0025036 | 0.0072205 | 0.80566 | 0.89722 | 0.75989 | 0.81024 | 0.91095 | 0.71411 | 0.55847 | 11.7371 | 11.8011 | 11.7554 | 11.6913 | 11.6226 | 8.7433 | 8.638 | 112.2757 | 112.1201 | -10.7895 | 112.4588 | 112.3718 | 0.25177 | -10.8948 | 120.3049 | 120.1996 | -0.009155 | 123.2986 | 123.317 | 3.1174 | -0.077819 | 112.4725 | 112.3672 | 112.3215 | -11.142 | 123.2529 | 123.1842 | 123.3627 | -3.0624
3036.5156 | 123.4863 | -111.6074 | 11.6776 | 0.14954 | 0.014168 | 0.0026447 | 0.010899 | -0.020194 | 0.00041235 | 0.00020288 | 0.18639 | 0.021302 | -0.011713 | 0.009504 | -0.00058103 | 0.0067931 | 0.80109 | 0.86517 | 0.75073 | 0.7782 | 0.86975 | 0.70038 | 0.54016 | 11.705 | 11.7096 | 11.6821 | 11.673 | 11.5997 | 8.7387 | 8.6426 | 112.3077 | 112.1475 | -10.8078 | 112.4725 | 112.3856 | 0.23804 | -10.8765 | 120.3461 | 120.2499 | -0.004577 | 123.3124 | 123.2895 | 3.0396 | -0.07782 | 112.4771 | 112.4084 | 112.3581 | -11.1374 | 123.2803 | 123.2071 | 123.317 | -3.035
3037.5156 | 123.4726 | -111.6211 | 11.6592 | 0.11139 | 0.01075 | 0.0041401 | 0.013463 | -0.019553 | -0.00086945 | 0.0025529 | 0.48393 | 0.021302 | -0.012781 | 0.010359 | -0.00079463 | 0.0074341 | 0.74616 | 0.8194 | 0.42572 | 0.63171 | 0.88348 | 0.64087 | 0.48065 | 11.6043 | 11.6592 | 11.6501 | 11.6547 | 11.5768 | 8.7296 | 8.6426 | 112.262 | 112.1017 | -10.7758 | 112.4405 | 112.2528 | 0.15106 | -10.9131 | 120.3506 | 120.2637 | -0.004578 | 123.2254 | 123.2712 | 3.0075 | -0.082398 | 112.5046 | 112.3672 | 112.0468 | -11.1786 | 123.2758 | 123.1979 | 123.2803 | -3.0167
3038.5156 | 123.4863 | -111.6669 | 11.618 | 0.17242 | 0.013099 | 0.0032855 | 0.012608 | -0.020407 | 0.0010532 | 0.00084388 | 0.17113 | 0.021516 | -0.011927 | 0.0092904 | -0.00079463 | 0.0080749 | 0.81024 | 0.85144 | 0.74616 | 0.78278 | 0.90179 | 0.69122 | 0.54932 | 11.6547 | 11.6684 | 11.6455 | 11.618 | 11.554 | 8.7341 | 8.6334 | 112.3581 | 112.2162 | -10.7162 | 112.5183 | 112.4496 | 0.23346 | -10.8078 | 120.401 | 120.3003 | 0 | 123.3215 | 123.3124 | 3.0121 | -0.064087 | 112.5687 | 112.4771 | 112.413 | -11.0687 | 123.2849 | 123.2208 | 123.3353 | -2.9846
3039.5156 | 123.4726 | -111.6806 | 11.5814 | 0.035095 | 0.0090405 | 0.0028583 | 0.013249 | -0.017417 | -0.0017238 | -0.00065152 | -0.11116 | 0.021089 | -0.013422 | 0.010786 | -0.0033582 | 0.0067931 | 0.46692 | 0.62714 | 0.64545 | 0.67749 | 0.85602 | 0.64545 | 0.4715 | 11.5677 | 11.6364 | 11.5997 | 11.6135 | 11.5585 | 8.7204 | 8.638 | 112.3261 | 112.1521 | -10.7254 | 112.3077 | 112.3581 | 0.20599 | -11.1145 | 120.401 | 120.3186 | 0.032043 | 123.2483 | 123.2803 | 2.9617 | -0.022888 | 112.5366 | 112.1475 | 112.3261 | -11.1099 | 123.2941 | 123.2391 | 123.317 | -2.9434
3040.5156 | 123.5321 | -111.7126 | 11.5952 | 0.43182 | 0.014595 | 0.0030719 | 0.014103 | -0.019553 | 0.0042576 | 0.0016983 | 0.1635 | 0.020875 | -0.009363 | 0.0092904 | -0.00036743 | 0.0080749 | 0.80566 | 0.84228 | 0.74158 | 0.80566 | 0.85144 | 0.67749 | 0.54016 | 11.6043 | 11.6409 | 11.5952 | 11.5814 | 11.5082 | 8.7341 | 8.6334 | 112.3901 | 112.2528 | -10.7437 | 112.5549 | 112.5183 | 0.2655 | -10.7895 | 120.4468 | 120.3461 | -0.013733 | 123.317 | 123.3078 | 2.9617 | -0.086975 | 112.5641 | 112.5183 | 112.4542 | -11.055 | 123.2941 | 123.2208 | 123.3536 | -2.9617
3041.5156 | 123.4772 | -111.7035 | 11.5585 | 0.14954 | 0.013099 | 0.0032855 | 0.012181 | -0.018485 | 0.00019875 | 0.00084388 | 0.20164 | 0.021089 | -0.010858 | 0.008436 | -0.00079463 | 0.010852 | 0.76904 | 0.81024 | 0.71411 | 0.75531 | 0.90179 | 0.70496 | 0.53558 | 11.5356 | 11.5768 | 11.554 | 11.5494 | 11.499 | 8.7158 | 8.6334 | 112.4084 | 112.2391 | -10.6567 | 112.5137 | 112.4588 | 0.21973 | -10.7895 | 120.4193 | 120.3369 | -0.009156 | 123.2391 | 123.2574 | 2.9205 | -0.05951 | 112.6053 | 112.4725 | 112.4176 | -11.0229 | 123.2529 | 123.2025 | 123.2803 | -2.9251
3042.5156 | 123.5092 | -111.7767 | 11.5128 | 0.25635 | 0.016304 | 0.0011493 | 0.014317 | -0.019339 | 0.0019078 | 0.0016983 | 0.2169 | 0.020875 | -0.014704 | 0.010572 | -0.0020764 | 0.0095703 | 0.80109 | 0.83313 | 0.72784 | 0.79651 | 0.87433 | 0.68665 | 0.51727 | 11.5768 | 11.5952 | 11.5448 | 11.5356 | 11.467 | 8.7204 | 8.638 | 112.4634 | 112.294 | -10.6384 | 112.6099 | 112.5732 | 0.27924 | -10.7117 | 120.4971 | 120.4147 | 0.022889 | 123.3536 | 123.3215 | 2.9068 | -0.045776 | 112.6511 | 112.5778 | 112.5046 | -10.9955 | 123.3124 | 123.2437 | 123.3719 | -2.8748
3043.5156 | 123.4909 | -111.7676 | 11.5082 | 0.14954 | 0.013099 | 0.0022175 | 0.010472 | -0.021475 | 0.0019078 | 0.0012711 | 0.17113 | 0.022798 | -0.010431 | 0.010145 | -0.0016492 | 0.0087157 | 0.80109 | 0.83771 | 0.73242 | 0.7782 | 0.89264 | 0.70496 | 0.53558 | 11.5356 | 11.5814 | 11.5265 | 11.4761 | 11.4395 | 8.7204 | 8.6334 | 112.4725 | 112.3032 | -10.6155 | 112.6053 | 112.5458 | 0.24261 | -10.7071 | 120.488 | 120.401 | -0.032044 | 123.3032 | 123.2941 | 2.8931 | -0.068665 | 112.6602 | 112.5687 | 112.5 | -10.9726 | 123.2437 | 123.2071 | 123.349 | -2.8748
3044.5156 | 123.4818 | -111.8042 | 11.4899 | 0.22583 | 0.017799 | 0.0022175 | 0.015385 | -0.020194 | 0.004044 | 0.0042619 | 0.15587 | 0.023866 | -0.011072 | 0.011427 | -0.0025036 | 0.0080749 | 0.75073 | 0.71869 | 0.62714 | 0.72784 | 0.90637 | 0.66376 | 0.48981 | 11.4532 | 11.4716 | 11.4578 | 11.5128 | 11.4395 | 8.7112 | 8.6288 | 112.468 | 112.294 | -10.5835 | 112.5229 | 112.532 | 0.23804 | -10.7391 | 120.5154 | 120.433 | 0.022888 | 123.2574 | 123.262 | 2.829 | -0.050354 | 112.7106 | 112.5549 | 112.4313 | -11.0001 | 123.317 | 123.2437 | 123.2758 | -2.861
3045.5156 | 123.4726 | -111.795 | 11.4532 | 0.18005 | 0.014381 | 0.0022175 | 0.011326 | -0.019339 | -0.00065585 | 0.0027665 | 0.17113 | 0.023866 | -0.010858 | 0.0097176 | -0.0031446 | 0.0085021 | 0.80566 | 0.83313 | 0.71869 | 0.77362 | 0.88806 | 0.70038 | 0.51727 | 11.4807 | 11.5219 | 11.4807 | 11.4487 | 11.4212 | 8.7204 | 8.638 | 112.4954 | 112.3123 | -10.5652 | 112.6282 | 112.5687 | 0.25635 | -10.6476 | 120.5154 | 120.433 | -0.004578 | 123.2758 | 123.2758 | 2.8427 | -0.032043 | 112.6831 | 112.6007 | 112.5137 | -10.936 | 123.2437 | 123.2162 | 123.317 | -2.8152
3046.5156 | 123.5138 | -111.8362 | 11.4258 | 0.19531 | 0.018654 | 0.0022175 | 0.011326 | -0.020194 | 0.0025486 | 0.0038345 | 0.17876 | 0.024507 | -0.010218 | 0.010572 | -0.0010082 | 0.0065795 | 0.75073 | 0.73242 | 0.64087 | 0.72784 | 0.89264 | 0.65918 | 0.50812 | 11.4212 | 11.4761 | 11.4304 | 11.4578 | 11.3754 | 8.7067 | 8.6288 | 112.4954 | 112.3444 | -10.5331 | 112.5687 | 112.5641 | 0.21973 | -10.675 | 120.5429 | 120.4651 | 0.032044 | 123.2574 | 123.2666 | 2.8015 | -0.050354 | 112.7289 | 112.587 | 112.4771 | -10.9177 | 123.2941 | 123.2117 | 123.3124 | -2.7969
3047.5156 | 123.5046 | -111.8591 | 11.4258 | 0.12665 | 0.016304 | 0.0030719 | 0.01389 | -0.018912 | -0.001083 | 0.0038345 | 0.17113 | 0.021516 | -0.011713 | 0.012281 | -0.0018628 | 0.0082885 | 0.79651 | 0.83771 | 0.737 | 0.78278 | 0.86517 | 0.69122 | 0.54016 | 11.4258 | 11.4899 | 11.4395 | 11.4029 | 11.3525 | 8.7204 | 8.6334 | 112.5504 | 112.3993 | -10.5606 | 112.6968 | 112.6419 | 0.24262 | -10.6293 | 120.5795 | 120.4926 | -0.022888 | 123.2849 | 123.2986 | 2.8061 | -0.073242 | 112.7243 | 112.6556 | 112.5961 | -10.8856 | 123.262 | 123.2117 | 123.349 | -2.7924
3048.5156 | 123.4406 | -111.9232 | 11.4075 | 0.15717 | 0.018013 | 0.0017901 | 0.014103 | -0.019553 | 0.0025486 | 0.0019119 | 0.17113 | 0.022157 | -0.011499 | 0.010786 | 0.0013416 | 0.0078613 | 0.71869 | 0.70038 | 0.59052 | 0.71411 | 0.9201 | 0.65002 | 0.47607 | 11.3388 | 11.348 | 11.3388 | 11.412 | 11.3617 | 8.7112 | 8.6288 | 112.5732 | 112.3993 | -10.4874 | 112.6236 | 112.6373 | 0.23804 | -10.6888 | 120.6345 | 120.5521 | 0.004577 | 123.262 | 123.262 | 2.71 | -0.045777 | 112.8433 | 112.6419 | 112.5137 | -10.9314 | 123.3353 | 123.2849 | 123.2712 | -2.7786
3049.5156 | 123.5001 | -111.9232 | 11.3663 | 0.14191 | 0.015022 | 0.0052081 | 0.01389 | -0.021048 | -0.0040738 | 0.0021255 | 0.20164 | 0.021516 | -0.012567 | 0.010786 | -0.00229 | 0.0076477 | 0.78735 | 0.83771 | 0.72784 | 0.7782 | 0.87433 | 0.6958 | 0.51727 | 11.3892 | 11.4349 | 11.3983 | 11.3617 | 11.3113 | 8.7204 | 8.6288 | 112.619 | 112.4405 | -10.4919 | 112.7609 | 112.7014 | 0.26092 | -10.5789 | 120.6436 | 120.5521 | -0.004578 | 123.3124 | 123.3215 | 2.7695 | -0.054932 | 112.7975 | 112.7106 | 112.6511 | -10.849 | 123.2849 | 123.2346 | 123.3582 | -2.7374
3050.5156 | 123.4222 | -111.9873 | 11.3663 | -0.1709 | 0.02079 | 0.0045673 | 0.015812 | -0.020194 | 0.005112 | 0.0019119 | 0.12535 | 0.026002 | -0.0097904 | 0.01164 | -0.00015383 | 0.0076477 | 0.71411 | 0.64087 | 0.58136 | 0.69122 | 0.91095 | 0.6546 | 0.48523 | 11.2335 | 11.2793 | 11.2656 | 11.3617 | 11.3205 | 8.7021 | 8.6243 | 112.6419 | 112.4725 | -10.4553 | 112.6282 | 112.6785 | 0.20599 | -10.6522 | 120.6894 | 120.6116 | -0.004578 | 123.2208 | 123.2529 | 2.6413 | -0.045776 | 112.8983 | 112.7014 | 112.5687 | -10.881 | 123.349 | 123.3078 | 123.2666 | -2.742
3051.5156 | 123.5229 | -111.9461 | 11.3159 | 1.8127 | 0.017586 | 0.0045673 | 0.015385 | -0.017417 | -0.0017238 | 0.0031937 | 0.20164 | 0.01938 | -0.012995 | 0.011854 | -0.0014356 | 0.010852 | 0.76446 | 0.82398 | 0.70953 | 0.77362 | 0.83771 | 0.66376 | 0.50812 | 11.3251 | 11.3846 | 11.3571 | 11.3068 | 11.2289 | 8.7067 | 8.6197 | 112.6099 | 112.4542 | -10.4782 | 112.7701 | 112.7197 | 0.2655 | -10.5515 | 120.6528 | 120.5658 | -0.009155 | 123.2712 | 123.3032 | 2.7374 | -0.086975 | 112.7838 | 112.7106 | 112.6556 | -10.8078 | 123.2529 | 123.175 | 123.3307 | -2.6962
3052.5156 | 123.4268 | -112.0285 | 11.3022 | 0.16479 | 0.018867 | 0.0041401 | 0.014317 | -0.018698 | 0.0012668 | 0.0023391 | 0.13298 | 0.023652 | -0.0063724 | 0.010145 | -0.0020764 | 0.0082885 | 0.70038 | 0.66834 | 0.60425 | 0.70038 | 0.89722 | 0.64545 | 0.48065 | 11.1923 | 11.2106 | 11.1877 | 11.3297 | 11.2656 | 8.6929 | 8.6197 | 112.674 | 112.5092 | -10.405 | 112.6968 | 112.7289 | 0.21973 | -10.6018 | 120.7214 | 120.6482 | 0.027466 | 123.2208 | 123.2162 | 2.5681 | -0.036621 | 112.9257 | 112.7289 | 112.6328 | -10.8215 | 123.3582 | 123.2941 | 123.2391 | -2.6825
3053.5156 | 123.5092 | -112.0377 | 11.2198 | 0.17242 | 0.015022 | 0.0032855 | 0.011754 | -0.021048 | 0.00041235 | 0.0031937 | 0.23216 | 0.021943 | -0.011499 | 0.010999 | -0.0016492 | 0.0078613 | 0.79193 | 0.80566 | 0.70496 | 0.78735 | 0.88348 | 0.68207 | 0.50354 | 11.2656 | 11.3113 | 11.2885 | 11.2289 | 11.1877 | 8.7112 | 8.6151 | 112.7197 | 112.5412 | -10.3363 | 112.8433 | 112.825 | 0.28381 | -10.4279 | 120.7489 | 120.6528 | 0.009155 | 123.3032 | 123.3261 | 2.6733 | -0.032044 | 112.9211 | 112.8296 | 112.7426 | -10.7162 | 123.2666 | 123.2254 | 123.349 | -2.6047
3054.5156 | 123.3994 | -112.0789 | 11.2701 | 0.16479 | 0.019722 | 0.0020037 | 0.015172 | -0.018485 | 0.0091708 | -0.00043792 | -0.12642 | 0.02408 | -0.0059452 | 0.010572 | -0.0010082 | 0.0091431 | 0.55389 | 0.85144 | 0.6134 | 0.67291 | 0.92468 | 0.67749 | 0.48065 | 11.1374 | 11.1832 | 11.1465 | 11.2839 | 11.2335 | 8.6975 | 8.6105 | 112.7563 | 112.5595 | -10.3455 | 112.9303 | 112.7518 | 0.19226 | -10.7162 | 120.7764 | 120.6894 | 0.013733 | 123.2162 | 123.2254 | 2.536 | -0.036621 | 113.0035 | 112.6328 | 112.6923 | -10.7895 | 123.3627 | 123.3124 | 123.262 | -2.6596
3055.5156 | 123.5184 | -112.0514 | 11.2061 | 0.20294 | 0.016731 | 0.0032855 | 0.012394 | -0.019766 | 0.00062595 | -1.0724e-05 | 0.20927 | 0.02173 | -0.012567 | 0.007795 | -0.0027172 | 0.0097839 | 0.73242 | 0.737 | 0.66376 | 0.72784 | 0.87891 | 0.65918 | 0.49439 | 11.2106 | 11.2518 | 11.2381 | 11.2106 | 11.1649 | 8.6975 | 8.6151 | 112.7106 | 112.5458 | -10.3271 | 112.7884 | 112.7792 | 0.23346 | -10.4736 | 120.7489 | 120.6665 | 0.004577 | 123.262 | 123.2895 | 2.623 | -0.041199 | 112.9303 | 112.7838 | 112.7151 | -10.7117 | 123.262 | 123.2162 | 123.3032 | -2.5909
3056.5156 | 123.4177 | -112.0972 | 11.2015 | 0.17242 | 0.019295 | 0.0024311 | 0.014531 | -0.018485 | -1.505e-05 | 0.0031937 | 0.1635 | 0.023652 | -0.0085086 | 0.0097176 | -0.0012218 | 0.010638 | 0.68207 | 0.65918 | 0.58136 | 0.70038 | 0.90179 | 0.64087 | 0.47607 | 11.0916 | 11.1237 | 11.1191 | 11.2427 | 11.1694 | 8.6884 | 8.6014 | 112.738 | 112.5732 | -10.2997 | 112.7563 | 112.7975 | 0.2243 | -10.5194 | 120.7855 | 120.6985 | 0.041199 | 123.1888 | 123.2162 | 2.5177 | -0.032043 | 112.999 | 112.7792 | 112.6785 | -10.7254 | 123.3398 | 123.2666 | 123.2208 | -2.6001
3057.5156 | 123.4543 | -112.1292 | 11.1694 | 0.21057 | 0.016731 | 0.0043537 | 0.013035 | -0.022757 | 0.0021214 | 0.0012711 | 0.23216 | 0.024293 | -0.0097904 | 0.011427 | -0.0010082 | 0.0072205 | 0.70038 | 0.6958 | 0.6134 | 0.70953 | 0.89264 | 0.64087 | 0.48065 | 11.1053 | 11.1603 | 11.1465 | 11.1969 | 11.1328 | 8.6975 | 8.6151 | 112.7701 | 112.6099 | -10.2768 | 112.825 | 112.8387 | 0.22888 | -10.4691 | 120.8267 | 120.7443 | 0.027465 | 123.2346 | 123.2758 | 2.5314 | -0.036622 | 113.0219 | 112.8296 | 112.7426 | -10.6888 | 123.3261 | 123.262 | 123.2895 | -2.5543
3058.5156 | 123.381 | -112.175 | 11.1649 | 0.019836 | 0.021217 | 0.0020037 | 0.014958 | -0.018485 | 0.0014804 | 0.0034073 | 0.079574 | 0.025361 | -0.0097904 | 0.010145 | 0.00048697 | 0.0091431 | 0.67749 | 0.65918 | 0.58136 | 0.68207 | 0.87433 | 0.63171 | 0.4715 | 11.0001 | 11.0733 | 11.0321 | 11.1832 | 11.1465 | 8.6929 | 8.6151 | 112.8067 | 112.6465 | -10.2905 | 112.8342 | 112.8571 | 0.21057 | -10.4874 | 120.8679 | 120.7901 | 0.018311 | 123.175 | 123.2071 | 2.417 | -0.018311 | 113.0493 | 112.8525 | 112.7563 | -10.6934 | 123.3582 | 123.3215 | 123.2483 | -2.5497
3059.5156 | 123.5275 | -112.1475 | 11.1053 | 0.20294 | 0.01844 | 0.0015765 | 0.013463 | -0.019553 | -0.00044225 | 0.00063028 | 0.27794 | 0.023652 | -0.010431 | 0.010359 | -0.0010082 | 0.011066 | 0.70038 | 0.81024 | 0.70496 | 0.76904 | 0.83313 | 0.63629 | 0.48981 | 11.1282 | 11.1923 | 11.1649 | 11.1008 | 11.0779 | 8.6929 | 8.6105 | 112.7838 | 112.6373 | -10.2722 | 112.9578 | 112.9166 | 0.27924 | -10.405 | 120.8405 | 120.7581 | -0.004578 | 123.2758 | 123.3124 | 2.5543 | -0.027466 | 112.9807 | 112.8479 | 112.8525 | -10.6155 | 123.2483 | 123.2254 | 123.3398 | -2.4948
3060.5156 | 123.4177 | -112.2345 | 11.1053 | 0.21057 | 0.020576 | 0.0011493 | 0.014744 | -0.022116 | 0.001694 | 0.0016983 | 0.12535 | 0.02173 | -0.004877 | 0.0090768 | -0.00036743 | 0.0080749 | 0.66834 | 0.66376 | 0.59052 | 0.68207 | 0.90179 | 0.64087 | 0.44403 | 11.0001 | 11.0367 | 11.0092 | 11.1145 | 11.0779 | 8.6792 | 8.6014 | 112.8754 | 112.6785 | -10.2036 | 112.8983 | 112.9166 | 0.23804 | -10.437 | 120.9137 | 120.8359 | 0.009155 | 123.2346 | 123.2437 | 2.4078 | -0.027466 | 113.1363 | 112.9028 | 112.825 | -10.6613 | 123.349 | 123.3124 | 123.2712 | -2.504
3061.5156 | 123.4909 | -112.207 | 11.0458 | 0.20294 | 0.019081 | 0.0045673 | 0.013676 | -0.019766 | 0.00041235 | -1.0724e-05 | 0.25505 | 0.022157 | -0.010004 | 0.010359 | -0.00058103 | 0.0097839 | 0.70496 | 0.70038 | 0.62256 | 0.6958 | 0.89722 | 0.64087 | 0.4715 | 11.0229 | 11.0687 | 11.0367 | 11.087 | 11.0641 | 8.6884 | 8.6014 | 112.8479 | 112.6785 | -10.1486 | 112.9074 | 112.9028 | 0.2243 | -10.3409 | 120.8954 | 120.8084 | 0.041199 | 123.23 | 123.2437 | 2.4353 | 0.018311 | 113.1042 | 112.912 | 112.8296 | -10.5743 | 123.2941 | 123.2712 | 123.2758 | -2.4445
3062.5156 | 123.4131 | -112.2803 | 11.055 | 1.3702 | 0.018867 | 0.0045673 | 0.013463 | -0.021048 | 0.00041235 | 0.0027665 | 0.17113 | 0.02408 | -0.0091494 | 0.012495 | -0.0025036 | 0.0091431 | 0.70038 | 0.62256 | 0.56305 | 0.67749 | 0.89722 | 0.63171 | 0.46234 | 10.936 | 10.968 | 10.9451 | 11.0825 | 11.0321 | 8.6838 | 8.6014 | 112.912 | 112.7426 | -10.1578 | 112.9028 | 112.9578 | 0.21515 | -10.3546 | 120.964 | 120.8817 | 0.027465 | 123.2162 | 123.2254 | 2.3438 | -0.022889 | 113.1775 | 112.9807 | 112.8433 | -10.5927 | 123.3627 | 123.3124 | 123.2483 | -2.4536
3063.5156 | 123.5229 | -112.2345 | 11.0184 | 0.21057 | 0.016945 | 0.0034991 | 0.010258 | -0.017417 | -1.505e-05 | 0.00063028 | 0.22453 | 0.022584 | -0.01214 | 0.0097176 | -0.0010082 | 0.0078613 | 0.73242 | 0.74158 | 0.67291 | 0.75989 | 0.86517 | 0.66376 | 0.46692 | 11.0184 | 11.0641 | 11.0596 | 11.0092 | 10.9726 | 8.6838 | 8.6105 | 112.8983 | 112.7014 | -10.1532 | 112.9761 | 112.9944 | 0.29297 | -10.2859 | 120.9183 | 120.845 | -0.009156 | 123.2529 | 123.2941 | 2.449 | -0.045777 | 113.0997 | 112.9669 | 112.9074 | -10.5515 | 123.2437 | 123.2071 | 123.2986 | -2.4078
3064.5156 | 123.3856 | -112.3077 | 11.0046 | 0.035095 | 0.019081 | 0.0030719 | 0.012608 | -0.020407 | 0.0025486 | 0.00020288 | 0.026169 | 0.023439 | -0.0080814 | 0.0099314 | 0.0013416 | 0.0055115 | 0.6958 | 0.65918 | 0.59052 | 0.69122 | 0.88806 | 0.64087 | 0.44403 | 10.8765 | 10.9406 | 10.8948 | 11.0138 | 10.9863 | 8.67 | 8.6014 | 112.9486 | 112.7518 | -10.1166 | 112.9669 | 112.999 | 0.24719 | -10.3088 | 120.9778 | 120.9091 | 0.009155 | 123.1842 | 123.2025 | 2.2934 | -0.018311 | 113.1958 | 113.0035 | 112.8983 | -10.5606 | 123.3215 | 123.2941 | 123.2483 | -2.4033
3065.5156 | 123.4085 | -112.3535 | 10.9955 | 0.19531 | 0.015663 | 0.0034991 | 0.013249 | -0.019339 | 0.00062595 | 0.0010575 | 0.14824 | 0.023652 | -0.011927 | 0.010999 | -0.0031446 | 0.011279 | 0.66834 | 0.6546 | 0.55389 | 0.67291 | 0.89722 | 0.62714 | 0.44861 | 10.8627 | 10.9131 | 10.8856 | 11.0046 | 10.9634 | 8.6746 | 8.5968 | 112.9807 | 112.8021 | -10.0983 | 113.0081 | 113.0264 | 0.2243 | -10.3271 | 121.0281 | 120.9503 | 0.009156 | 123.2162 | 123.2391 | 2.2888 | -0.032043 | 113.2507 | 113.0219 | 112.9074 | -10.5469 | 123.3582 | 123.317 | 123.2666 | -2.3987
3066.5156 | 123.5321 | -112.3672 | 10.9955 | 0.12665 | 0.021217 | 0.0024311 | 0.015599 | -0.018698 | 0.0025486 | 0.0025529 | 0.13298 | 0.023652 | -0.0091494 | 0.012922 | 0.00027337 | 0.0087157 | 0.65918 | 0.62256 | 0.56305 | 0.67749 | 0.88348 | 0.62714 | 0.43488 | 10.7986 | 10.8536 | 10.8444 | 10.9955 | 10.936 | 8.6746 | 8.5968 | 112.9944 | 112.8021 | -10.112 | 112.9898 | 113.0447 | 0.24262 | -10.3363 | 121.0419 | 120.9641 | 0 | 123.1659 | 123.2117 | 2.2476 | -0.059509 | 113.2507 | 113.0264 | 112.9303 | -10.5606 | 123.3627 | 123.3032 | 123.2208 | -2.3987
3067.5156 | 123.4406 | -112.3993 | 10.9406 | 0.2182 | 0.017586 | 0.0054217 | 0.013463 | -0.021048 | 0.00019875 | 0.0027665 | 0.20927 | 0.022798 | -0.0097904 | 0.012708 | -0.0014356 | 0.0095703 | 0.67749 | 0.69122 | 0.59967 | 0.68207 | 0.87891 | 0.63629 | 0.46234 | 10.8536 | 10.9039 | 10.8948 | 10.9543 | 10.8948 | 8.6655 | 8.5922 | 113.0356 | 112.8616 | -10.0616 | 113.0905 | 113.0814 | 0.21973 | -10.2631 | 121.0648 | 120.9915 | 0.013733 | 123.2529 | 123.2941 | 2.3026 | -0.045777 | 113.2782 | 113.0768 | 112.999 | -10.4782 | 123.3536 | 123.2941 | 123.3032 | -2.3483
3068.5156 | 123.3856 | -112.4222 | 10.9406 | 0.088501 | 0.020149 | 0.00029489 | 0.015385 | -0.017417 | 0.002335 | 0.0031937 | 0.056686 | 0.024293 | -0.0080814 | 0.012281 | 5.9768e-05 | 0.0097839 | 0.66834 | 0.63629 | 0.55389 | 0.67749 | 0.86975 | 0.62714 | 0.44861 | 10.7483 | 10.8398 | 10.7712 | 10.9222 | 10.881 | 8.6655 | 8.5876 | 113.0493 | 112.8708 | -10.0708 | 113.0585 | 113.0997 | 0.22888 | -10.2722 | 121.0876 | 121.0098 | -0.018311 | 123.1705 | 123.1934 | 2.1835 | -0.05951 | 113.2919 | 113.0905 | 112.9761 | -10.4919 | 123.3444 | 123.3032 | 123.262 | -2.3529
3069.5156 | 123.4406 | -112.4405 | 10.9131 | 0.16479 | 0.02079 | 0.0020037 | 0.014103 | -0.021048 | 0.00083955 | 0.0038345 | 0.20164 | 0.025789 | -0.009363 | 0.012068 | -0.00079463 | 0.010425 | 0.67749 | 0.65002 | 0.56763 | 0.68207 | 0.89264 | 0.63171 | 0.44861 | 10.7758 | 10.8078 | 10.8261 | 10.9222 | 10.8673 | 8.6563 | 8.5876 | 113.0722 | 112.8891 | -10.0204 | 113.0905 | 113.1226 | 0.23346 | -10.2356 | 121.0968 | 121.0281 | 0.009155 | 123.2162 | 123.2666 | 2.2385 | -0.045776 | 113.3331 | 113.118 | 113.0081 | -10.4645 | 123.3627 | 123.3078 | 123.2483 | -2.3254
3070.5156 | 123.3948 | -112.4588 | 10.881 | 0.012207 | 0.020363 | 0.0013629 | 0.014958 | -0.019339 | 0.0029758 | 0.0014847 | 0.026169 | 0.022371 | -0.010431 | 0.012708 | -0.0020764 | 0.010211 | 0.67749 | 0.6546 | 0.56763 | 0.67749 | 0.85602 | 0.61798 | 0.44861 | 10.7346 | 10.7986 | 10.7437 | 10.8902 | 10.8444 | 8.6563 | 8.5876 | 113.0768 | 112.9074 | -10.025 | 113.1134 | 113.1363 | 0.22888 | -10.2036 | 121.1151 | 121.0464 | 0.009156 | 123.1934 | 123.2025 | 2.1561 | -0.036621 | 113.3148 | 113.1363 | 113.0264 | -10.4324 | 123.349 | 123.3032 | 123.2574 | -2.2934
3071.5156 | 123.4131 | -112.4954 | 10.8444 | -0.14038 | 0.018867 | 0.0032855 | 0.01389 | -0.021689 | 0.003403 | 0.0016983 | 0.17876 | 0.021943 | -0.0078678 | 0.012068 | 0.00027337 | 0.010211 | 0.6546 | 0.63629 | 0.54932 | 0.67749 | 0.88806 | 0.6134 | 0.44861 | 10.73 | 10.7437 | 10.7391 | 10.8673 | 10.7986 | 8.6472 | 8.5785 | 113.1088 | 112.944 | -9.9564 | 113.1317 | 113.1729 | 0.22888 | -10.1898 | 121.1426 | 121.0739 | 0.022889 | 123.2254 | 123.2346 | 2.1606 | -0.045776 | 113.3835 | 113.15 | 113.0447 | -10.3958 | 123.3627 | 123.2941 | 123.2391 | -2.2659
3072.5156 | 123.4039 | -112.5046 | 10.817 | -0.018311 | 0.016304 | 0.0052081 | 0.016667 | -0.016349 | 0.0019078 | 0.0027665 | 0.041427 | 0.022157 | -0.0087222 | 0.01164 | -0.0014356 | 0.0097839 | 0.69122 | 0.68207 | 0.58594 | 0.68207 | 0.87891 | 0.62714 | 0.43488 | 10.7025 | 10.7574 | 10.6934 | 10.817 | 10.7986 | 8.6517 | 8.5739 | 113.1317 | 112.9395 | -9.938 | 113.1866 | 113.1866 | 0.24719 | -10.1257 | 121.1563 | 121.0785 | 0 | 123.2071 | 123.1979 | 2.1194 | -0.018311 | 113.3835 | 113.1958 | 113.0905 | -10.3821 | 123.3215 | 123.3032 | 123.262 | -2.243
3073.5156 | 123.4222 | -112.5229 | 10.7849 | 0.18768 | 0.018013 | 0.0030719 | 0.015385 | -0.017844 | 0.00083955 | -0.00022432 | 0.24742 | 0.023439 | -0.0076542 | 0.01164 | -0.0025036 | 0.0082885 | 0.6546 | 0.65002 | 0.56305 | 0.67749 | 0.88348 | 0.60883 | 0.45319 | 10.6934 | 10.7483 | 10.7117 | 10.8032 | 10.7666 | 8.6472 | 8.5739 | 113.1317 | 112.9761 | -9.9014 | 113.1729 | 113.2004 | 0.2243 | -10.1303 | 121.17 | 121.0968 | 0.018311 | 123.2162 | 123.2346 | 2.1378 | -0.01831 | 113.4064 | 113.1775 | 113.0859 | -10.3317 | 123.3261 | 123.2895 | 123.2712 | -2.211
3074.5156 | 123.3856 | -112.5732 | 10.8078 | 0.019836 | 0.021431 | 0.0028583 | 0.016667 | -0.019126 | 0.0010532 | 0.0010575 | 0.041427 | 0.023225 | -0.010004 | 0.012708 | -0.0012218 | 0.0097839 | 0.67749 | 0.64087 | 0.55847 | 0.68207 | 0.85602 | 0.6134 | 0.43488 | 10.6201 | 10.6979 | 10.6384 | 10.7986 | 10.7437 | 8.6472 | 8.5739 | 113.1866 | 113.0081 | -9.9518 | 113.2141 | 113.2553 | 0.24719 | -10.1303 | 121.2204 | 121.1472 | -0.009155 | 123.1934 | 123.2117 | 2.0645 | -0.064087 | 113.4293 | 113.2507 | 113.1317 | -10.3729 | 123.3719 | 123.317 | 123.2712 | -2.2339
3075.5156 | 123.4131 | -112.5549 | 10.7803 | 0.30975 | 0.01844 | 0.0052081 | 0.017094 | -0.019339 | 0.0019078 | 0.0029801 | 0.15587 | 0.023225 | -0.0095768 | 0.0097176 | -0.0020764 | 0.0093567 | 0.65002 | 0.63171 | 0.54474 | 0.68207 | 0.87891 | 0.62714 | 0.43945 | 10.6247 | 10.6705 | 10.6613 | 10.762 | 10.7117 | 8.638 | 8.5739 | 113.1821 | 112.9944 | -9.9014 | 113.1866 | 113.237 | 0.24262 | -10.1303 | 121.1929 | 121.1288 | -0.01831 | 123.1796 | 123.2162 | 2.0874 | -0.068664 | 113.4338 | 113.205 | 113.0997 | -10.3409 | 123.317 | 123.2666 | 123.2254 | -2.2064
3076.5156 | 123.381 | -112.6419 | 10.7483 | 0.088501 | 0.019508 | 0.0039263 | 0.010685 | -0.017203 | 0.0019078 | 0.00063028 | 0.11009 | 0.022371 | -0.0057316 | 0.011213 | -0.00036743 | 0.0082885 | 0.64545 | 0.62256 | 0.54016 | 0.65918 | 0.87433 | 0.6134 | 0.41657 | 10.5606 | 10.6293 | 10.6018 | 10.7803 | 10.7117 | 8.638 | 8.5739 | 113.2553 | 113.0585 | -9.874 | 113.2645 | 113.3011 | 0.24261 | -10.1028 | 121.2799 | 121.2158 | 0.032043 | 123.2025 | 123.2437 | 2.0279 | -0.036621 | 113.5162 | 113.2874 | 113.1821 | -10.3317 | 123.4222 | 123.3536 | 123.2712 | -2.1744
3077.5312 | 123.5184 | -112.5916 | 10.7025 | -0.12512 | 0.013527 | 0.0030719 | 0.014317 | -0.018057 | -0.0049282 | -0.00022432 | -0.073013 | 0.020448 | -0.012781 | 0.012068 | -0.0037854 | 0.011493 | 0.72327 | 0.78735 | 0.70038 | 0.76446 | 0.84686 | 0.65002 | 0.50812 | 10.6476 | 10.8032 | 10.7346 | 10.6934 | 10.675 | 8.638 | 8.5739 | 113.2416 | 113.0997 | -9.8557 | 113.3789 | 113.356 | 0.25635 | -9.9792 | 121.2296 | 121.1655 | -0.009156 | 123.2391 | 123.3261 | 2.1606 | -0.027466 | 113.4384 | 113.3148 | 113.2919 | -10.1944 | 123.2849 | 123.2666 | 123.3948 | -2.1286
3078.5156 | 123.436 | -112.674 | 10.7025 | -0.27008 | 0.022712 | 0.00029489 | 0.013035 | -0.019766 | 0.005753 | -0.0010787 | -0.057755 | 0.022798 | -0.010431 | 0.0097176 | -0.00229 | 0.0072205 | 0.72784 | 0.70953 | 0.59509 | 0.6958 | 0.88806 | 0.63171 | 0.45319 | 10.5835 | 10.6567 | 10.6018 | 10.6934 | 10.6339 | 8.6334 | 8.5648 | 113.3057 | 113.1271 | -9.8145 | 113.3835 | 113.3698 | 0.24262 | -9.9747 | 121.3074 | 121.2387 | -0.009156 | 123.2574 | 123.2758 | 2.037 | -0.068665 | 113.562 | 113.4018 | 113.269 | -10.2493 | 123.3673 | 123.3078 | 123.3307 | -2.1378
3079.5156 | 123.3856 | -112.6831 | 10.6934 | 0.088501 | 0.021004 | 0.0026447 | 0.015385 | -0.018485 | 0.003403 | 0.0038345 | 0.064316 | 0.022584 | -0.010004 | 0.010145 | -0.00079463 | 0.0099975 | 0.63171 | 0.63171 | 0.54016 | 0.66376 | 0.87891 | 0.60425 | 0.42114 | 10.5057 | 10.556 | 10.5194 | 10.6934 | 10.6476 | 8.6334 | 8.5602 | 113.2874 | 113.1042 | -9.8145 | 113.3148 | 113.3469 | 0.24261 | -10.0616 | 121.3165 | 121.2433 | 0 | 123.1888 | 123.2025 | 1.9592 | -0.045776 | 113.562 | 113.3148 | 113.2233 | -10.2722 | 123.3765 | 123.3307 | 123.2391 | -2.1332
3080.5156 | 123.4222 | -112.6923 | 10.6567 | 0.14954 | 0.020149 | 0.0026447 | 0.015385 | -0.019339 | 0.00083955 | 0.00084388 | 0.19402 | 0.023011 | -0.0074404 | 0.010786 | -0.0031446 | 0.0099975 | 0.64545 | 0.64087 | 0.55389 | 0.66376 | 0.87433 | 0.62256 | 0.43945 | 10.524 | 10.5515 | 10.5377 | 10.6613 | 10.611 | 8.6334 | 8.5556 | 113.3148 | 113.1317 | -9.7824 | 113.3331 | 113.356 | 0.2243 | -10.0113 | 121.3257 | 121.2479 | 0.004578 | 123.2162 | 123.23 | 1.9821 | -0.045776 | 113.5666 | 113.3377 | 113.2462 | -10.2173 | 123.3536 | 123.3032 | 123.2437 | -2.1011
3081.5156 | 123.3765 | -112.706 | 10.6522 | 0.057983 | 0.019935 | 0.0015765 | 0.016881 | -0.019126 | 0.0021214 | 0.0019119 | 0.094833 | 0.025575 | -0.0072268 | 0.0092904 | -0.00058103 | 0.0078613 | 0.6134 | 0.6134 | 0.53558 | 0.67291 | 0.86517 | 0.60425 | 0.43488 | 10.4599 | 10.4919 | 10.4828 | 10.6522 | 10.5927 | 8.6243 | 8.5556 | 113.3102 | 113.1409 | -9.787 | 113.3194 | 113.3789 | 0.23804 | -10.0388 | 121.3303 | 121.2616 | 0 | 123.1659 | 123.1888 | 1.9272 | -0.05951 | 113.5712 | 113.3194 | 113.2416 | -10.2173 | 123.3582 | 123.2986 | 123.1979 | -2.0966
3082.5312 | 123.4909 | -112.7014 | 10.6064 | 0.15717 | 0.012886 | 0.0043537 | 0.010899 | -0.021048 | -0.0055692 | -0.00086512 | 0.23216 | 0.01938 | -0.011713 | 0.009504 | -0.0054944 | 0.011707 | 0.67749 | 0.72784 | 0.63171 | 0.68207 | 0.84228 | 0.64545 | 0.48065 | 10.5103 | 10.5927 | 10.5743 | 10.5743 | 10.5377 | 8.6197 | 8.5556 | 113.3469 | 113.1821 | -9.7641 | 113.4293 | 113.3835 | 0.20142 | -9.9289 | 121.3211 | 121.257 | -0.032043 | 123.2117 | 123.2758 | 2.0187 | -0.068664 | 113.5437 | 113.3789 | 113.3331 | -10.1257 | 123.2758 | 123.2391 | 123.2941 | -2.0508
3083.5156 | 123.2117 | -112.7243 | 10.6064 | 0.17242 | 0.019508 | 0.00029489 | 0.014103 | -0.021903 | 0.0038304 | 0.0012711 | 0.094833 | 0.023225 | -0.009363 | 0.0088632 | -0.00058103 | 0.0089295 | 0.64545 | 0.60425 | 0.54474 | 0.65918 | 0.8606 | 0.60883 | 0.43488 | 10.4004 | 10.4462 | 10.405 | 10.611 | 10.556 | 8.6197 | 8.5419 | 113.3331 | 113.1592 | -9.7458 | 113.3286 | 113.3835 | 0.2243 | -9.9609 | 121.344 | 121.2662 | 0.004578 | 123.1247 | 123.1293 | 1.8631 | -0.050354 | 113.5849 | 113.3698 | 113.269 | -10.1715 | 123.3353 | 123.2803 | 123.1705 | -2.0645
3084.5156 | 123.4497 | -112.7655 | 10.556 | -0.033569 | 0.019722 | 0.0020037 | 0.01389 | -0.01763 | 0.0014804 | 0.0012711 | -0.095902 | 0.025148 | -0.0085086 | 0.0082224 | -0.00036743 | 0.0074341 | 0.70496 | 0.70953 | 0.60883 | 0.69122 | 0.87433 | 0.6134 | 0.42572 | 10.4599 | 10.6064 | 10.4691 | 10.6247 | 10.5515 | 8.6105 | 8.5419 | 113.3789 | 113.1912 | -9.6817 | 113.475 | 113.4567 | 0.2655 | -9.8511 | 121.376 | 121.3074 | 0.068665 | 123.2254 | 123.2346 | 1.9272 | -0.004577 | 113.6398 | 113.4705 | 113.3743 | -10.1303 | 123.3902 | 123.317 | 123.3719 | -2.0142
3085.5156 | 123.4406 | -112.825 | 10.5286 | 0.23346 | 0.019722 | 0.0017901 | 0.014744 | -0.020194 | 0.0021214 | 0.0044755 | -0.0043486 | 0.022371 | -0.010004 | 0.011427 | -0.00015383 | 0.0087157 | 0.73242 | 0.71869 | 0.59509 | 0.70953 | 0.89264 | 0.62714 | 0.44403 | 10.4324 | 10.5057 | 10.4324 | 10.524 | 10.5011 | 8.606 | 8.551 | 113.4521 | 113.269 | -9.6359 | 113.5437 | 113.5345 | 0.2655 | -9.7961 | 121.431 | 121.376 | -0.004577 | 123.2574 | 123.2574 | 1.8814 | -0.027465 | 113.7177 | 113.5574 | 113.4201 | -10.0845 | 123.349 | 123.3261 | 123.3307 | -1.9775
3086.5156 | 123.4039 | -112.8067 | 10.5377 | -0.20905 | 0.016945 | 0.0034991 | 0.01154 | -0.018485 | 0.00062595 | -0.00086512 | -0.11879 | 0.021089 | -0.012995 | 0.0088632 | -0.0046398 | 0.0095703 | 0.62714 | 0.65918 | 0.55389 | 0.66834 | 0.85602 | 0.60425 | 0.40741 | 10.3546 | 10.4507 | 10.4095 | 10.5377 | 10.4828 | 8.6105 | 8.5373 | 113.4109 | 113.2141 | -9.6817 | 113.4659 | 113.475 | 0.26093 | -9.9106 | 121.4172 | 121.344 | 0 | 123.1613 | 123.2162 | 1.8723 | -0.054932 | 113.6627 | 113.4338 | 113.3606 | -10.1303 | 123.3444 | 123.2895 | 123.2574 | -2.0004
3087.5312 | 123.4955 | -112.8159 | 10.4553 | 0.26398 | 0.016517 | 0.0026447 | 0.012181 | -0.019553 | -0.0021512 | 0.0023391 | 1.5063 | 0.021302 | -0.012781 | 0.011427 | -0.0020764 | 0.0078613 | 0.73242 | 0.78735 | 0.67291 | 0.75989 | 0.8194 | 0.64087 | 0.4715 | 10.4462 | 10.5469 | 10.4736 | 10.4416 | 10.3958 | 8.6151 | 8.5327 | 113.4567 | 113.2874 | -9.6359 | 113.6032 | 113.5757 | 0.28839 | -9.7229 | 121.431 | 121.3486 | -0.013733 | 123.262 | 123.2895 | 1.9409 | -0.059509 | 113.6353 | 113.5483 | 113.4888 | -9.9838 | 123.2574 | 123.2117 | 123.3627 | -1.9226
3088.5156 | 123.4268 | -112.9028 | 10.4736 | -0.18616 | 0.016517 | 0.0047809 | 0.013676 | -0.018485 | 0.0019078 | -0.00065152 | -0.13405 | 0.022157 | -0.0097904 | 0.010572 | -0.0031446 | 0.0085021 | 0.63629 | 0.64087 | 0.55389 | 0.66376 | 0.86975 | 0.59509 | 0.42572 | 10.3134 | 10.4187 | 10.3546 | 10.5011 | 10.4599 | 8.606 | 8.5281 | 113.4979 | 113.3286 | -9.6039 | 113.5437 | 113.5666 | 0.23804 | -9.8373 | 121.5088 | 121.431 | 0.027466 | 123.2162 | 123.2574 | 1.8265 | -0.013733 | 113.7726 | 113.5391 | 113.4567 | -10.0479 | 123.4039 | 123.3627 | 123.3215 | -1.9455
3089.5156 | 123.4634 | -112.8571 | 10.4874 | -0.14801 | 0.01844 | 0.0047809 | 0.016453 | -0.018057 | 0.002335 | 0.00041648 | -0.095902 | 0.022371 | -0.010004 | 0.014204 | -0.00058103 | 0.0089295 | 0.69122 | 0.6958 | 0.59052 | 0.70496 | 0.87891 | 0.62256 | 0.43488 | 10.3455 | 10.4462 | 10.4279 | 10.4645 | 10.4462 | 8.6014 | 8.5281 | 113.4796 | 113.2919 | -9.6085 | 113.5529 | 113.562 | 0.27008 | -9.7961 | 121.4584 | 121.3852 | -0.022888 | 123.2025 | 123.2849 | 1.8997 | -0.041199 | 113.736 | 113.5483 | 113.4476 | -10.0525 | 123.3215 | 123.3032 | 123.3032 | -1.9592
3090.5156 | 123.4222 | -112.9349 | 10.4462 | -0.15564 | 0.015663 | 0.0047809 | 0.015599 | -0.019553 | 0.0010532 | 0.0010575 | -0.10353 | 0.022371 | -0.0097904 | 0.010999 | -0.0031446 | 0.0093567 | 0.63171 | 0.65002 | 0.54932 | 0.67291 | 0.83771 | 0.58594 | 0.41657 | 10.2585 | 10.3592 | 10.3271 | 10.4279 | 10.3821 | 8.5922 | 8.519 | 113.5208 | 113.3514 | -9.6085 | 113.5849 | 113.6078 | 0.25635 | -9.8145 | 121.5271 | 121.4539 | -0.018311 | 123.1934 | 123.262 | 1.8082 | -0.064087 | 113.7726 | 113.5666 | 113.4842 | -10.0296 | 123.3627 | 123.317 | 123.2941 | -1.9272
3091.5156 | 123.4406 | -112.9349 | 10.4141 | -0.15564 | 0.016517 | 0.0024311 | 0.013463 | -0.020194 | -0.0012966 | 0.0034073 | -0.16457 | 0.022798 | -0.011499 | 0.012922 | -0.0029308 | 0.0072205 | 0.63171 | 0.67291 | 0.56763 | 0.68665 | 0.84686 | 0.59509 | 0.42572 | 10.2859 | 10.3821 | 10.318 | 10.4004 | 10.3729 | 8.5922 | 8.5236 | 113.53 | 113.3606 | -9.5673 | 113.6078 | 113.6215 | 0.26093 | -9.7824 | 121.5271 | 121.4584 | -0.013733 | 123.2208 | 123.2529 | 1.7944 | -0.041199 | 113.7817 | 113.5666 | 113.5025 | -9.9884 | 123.3353 | 123.3078 | 123.317 | -1.8906
3092.5312 | 123.5184 | -112.9257 | 10.3226 | 0.20294 | 0.016945 | 0.0020037 | 0.012181 | -0.015921 | -0.0038602 | 0.0057571 | 0.36949 | 0.020662 | -0.010858 | 0.010999 | -0.0033582 | 0.010211 | 0.43488 | 0.68207 | 0.68207 | 0.77362 | 0.76446 | 0.57678 | 0.42572 | 10.3271 | 10.4141 | 10.3775 | 10.3363 | 10.2905 | 8.5968 | 8.5281 | 113.5025 | 113.3514 | -9.5581 | 113.6078 | 113.6993 | 0.3479 | -9.8877 | 121.5225 | 121.4539 | 0.013733 | 123.2529 | 123.3032 | 1.8494 | -0.032044 | 113.6902 | 113.3606 | 113.6078 | -9.8969 | 123.262 | 123.2162 | 123.3398 | -1.7944
3093.5156 | 123.4451 | -112.9944 | 10.3683 | -0.15564 | 0.01844 | 0.0013629 | 0.01624 | -0.019553 | -1.505e-05 | 0.00041648 | -0.14168 | 0.024507 | -0.0097904 | 0.010359 | -0.0037854 | 0.0067931 | 0.64087 | 0.63629 | 0.55389 | 0.66834 | 0.86975 | 0.56763 | 0.43488 | 10.199 | 10.3134 | 10.2448 | 10.3546 | 10.3043 | 8.5693 | 8.5052 | 113.562 | 113.4293 | -9.4986 | 113.6307 | 113.6627 | 0.23346 | -9.7275 | 121.5637 | 121.4996 | -0.013733 | 123.1934 | 123.2391 | 1.7395 | -0.064087 | 113.8641 | 113.6353 | 113.5483 | -9.9335 | 123.349 | 123.2986 | 123.3078 | -1.8631
3094.5156 | 123.4039 | -113.0264 | 10.3546 | -0.19379 | 0.016517 | 0.0041401 | 0.012608 | -0.018912 | -0.0021512 | -0.0017197 | -1.9041 | 0.020234 | -0.0097904 | 0.01164 | -0.0025036 | 0.0095703 | 0.60425 | 0.6546 | 0.54932 | 0.65918 | 0.8606 | 0.59509 | 0.42114 | 10.199 | 10.2493 | 10.2173 | 10.3729 | 10.3317 | 8.5785 | 8.519 | 113.6215 | 113.4476 | -9.494 | 113.681 | 113.6856 | 0.23804 | -9.7504 | 121.6049 | 121.5454 | 0.018311 | 123.2254 | 123.2437 | 1.6983 | -0.022888 | 113.887 | 113.6307 | 113.5757 | -9.9335 | 123.3994 | 123.3582 | 123.2758 | -1.8356
3095.5156 | 123.4497 | -113.0585 | 10.2951 | -0.16327 | 0.017372 | 0.0026447 | 0.017735 | -0.021048 | -0.00044225 | -0.00022432 | -0.13405 | 0.021516 | -0.010218 | 0.010359 | -0.0037854 | 0.0080749 | 0.61798 | 0.6546 | 0.55389 | 0.66834 | 0.84228 | 0.5722 | 0.42114 | 10.1761 | 10.2676 | 10.2127 | 10.3043 | 10.2768 | 8.5785 | 8.5052 | 113.6307 | 113.4796 | -9.4528 | 113.7131 | 113.7268 | 0.24719 | -9.6771 | 121.637 | 121.5637 | 0.009155 | 123.2346 | 123.2712 | 1.7075 | -0.018311 | 113.9008 | 113.6765 | 113.6124 | -9.874 | 123.3627 | 123.3353 | 123.3261 | -1.7899
3096.5156 | 123.4177 | -113.0722 | 10.3088 | -0.19379 | 0.014808 | 0.0043537 | 0.014103 | -0.020194 | -0.0036464 | 0.00041648 | -0.1722 | 0.021943 | -0.0097904 | 0.010999 | -0.0025036 | 0.010852 | 0.63171 | 0.70496 | 0.58594 | 0.68207 | 0.84686 | 0.59967 | 0.4303 | 10.1395 | 10.2402 | 10.1807 | 10.3226 | 10.2676 | 8.5831 | 8.5052 | 113.6719 | 113.5025 | -9.462 | 113.7772 | 113.7543 | 0.25177 | -9.6771 | 121.6553 | 121.5775 | 0.013733 | 123.2117 | 123.2529 | 1.6754 | -0.041199 | 113.9191 | 113.7039 | 113.6581 | -9.8785 | 123.3948 | 123.3398 | 123.3124 | -1.8036
3097.5156 | 123.5184 | -113.0768 | 10.2264 | 0.48523 | 0.01609 | 0.0017901 | 0.014958 | -0.019339 | -1.505e-05 | 0.0019119 | 0.22453 | 0.020448 | -0.0087222 | 0.011854 | -0.0025036 | 0.0091431 | 0.70496 | 0.76904 | 0.65918 | 0.71869 | 0.78278 | 0.62256 | 0.44861 | 10.2219 | 10.2722 | 10.2448 | 10.231 | 10.1532 | 8.5739 | 8.5052 | 113.6993 | 113.5254 | -9.4437 | 113.8458 | 113.7955 | 0.27008 | -9.5215 | 121.6507 | 121.582 | 0.004578 | 123.2986 | 123.3215 | 1.7395 | -0.073242 | 113.8596 | 113.7817 | 113.736 | -9.7778 | 123.3078 | 123.23 | 123.349 | -1.7212
3098.5156 | 123.4406 | -113.1134 | 10.231 | -0.14038 | 0.015022 | 0.0052081 | 0.013249 | -0.018057 | -0.0030056 | -0.0012923 | -0.11879 | 0.019807 | -0.0097904 | 0.010786 | -0.0025036 | 0.0093567 | 0.68665 | 0.73242 | 0.63171 | 0.71411 | 0.84228 | 0.6134 | 0.44403 | 10.1212 | 10.231 | 10.1669 | 10.2264 | 10.1898 | 8.5693 | 8.5052 | 113.7268 | 113.5574 | -9.3887 | 113.8458 | 113.8275 | 0.27008 | -9.5444 | 121.6827 | 121.6187 | -0.004578 | 123.2346 | 123.2803 | 1.6617 | -0.041199 | 113.9557 | 113.8 | 113.7451 | -9.787 | 123.3398 | 123.3032 | 123.3444 | -1.7258
3099.5156 | 123.3994 | -113.1409 | 10.2081 | -0.21667 | 0.016945 | 0.0030719 | 0.016667 | -0.022116 | 0.0021214 | 0.00020288 | -0.2256 | 0.021302 | -0.0097904 | 0.010999 | -0.00079463 | 0.0074341 | 0.6134 | 0.65002 | 0.53558 | 0.66376 | 0.87433 | 0.59052 | 0.40283 | 10.0479 | 10.1303 | 10.0845 | 10.2219 | 10.1578 | 8.551 | 8.4869 | 113.7314 | 113.5437 | -9.3338 | 113.7909 | 113.8046 | 0.26093 | -9.5947 | 121.6919 | 121.6278 | 0.013733 | 123.1888 | 123.2254 | 1.5976 | -0.050354 | 114.0152 | 113.7543 | 113.6765 | -9.8053 | 123.3627 | 123.2986 | 123.2712 | -1.7212
3100.5156 | 123.4909 | -113.1454 | 10.1715 | -0.18616 | 0.011177 | 0.0041401 | 0.013035 | -0.019553 | -0.002792 | 0.0025529 | -0.11879 | 0.022371 | -0.011713 | 0.0099314 | -0.0027172 | 0.0095703 | 0.68207 | 0.79651 | 0.65002 | 0.73242 | 0.8194 | 0.60883 | 0.45319 | 10.0983 | 10.231 | 10.1486 | 10.1532 | 10.1166 | 8.5556 | 8.4915 | 113.7543 | 113.5986 | -9.3521 | 113.942 | 113.8779 | 0.27924 | -9.4894 | 121.7011 | 121.637 | -0.018311 | 123.2437 | 123.2941 | 1.6571 | -0.054932 | 113.9648 | 113.8275 | 113.7955 | -9.7183 | 123.2986 | 123.262 | 123.3765 | -1.68
3101.5156 | 123.4222 | -113.2278 | 10.1669 | -0.14801 | 0.01844 | 0.0039263 | 0.015172 | -0.019766 | 0.0019078 | 0.0031937 | -0.12642 | 0.021302 | -0.010858 | 0.011213 | -0.0029308 | 0.0076477 | 0.61798 | 0.65918 | 0.53558 | 0.65918 | 0.85144 | 0.57678 | 0.40283 | 10.0204 | 10.1074 | 10.0296 | 10.1669 | 10.0983 | 8.551 | 8.4778 | 113.8046 | 113.6307 | -9.3155 | 113.887 | 113.887 | 0.25635 | -9.5489 | 121.7789 | 121.7056 | 0 | 123.2483 | 123.2574 | 1.5518 | -0.068664 | 114.0793 | 113.8458 | 113.7634 | -9.7641 | 123.3948 | 123.3261 | 123.3353 | -1.6891
3102.5156 | 123.436 | -113.1912 | 10.1578 | -0.18616 | 0.01374 | 0.0045673 | 0.014531 | -0.019766 | -0.001083 | -0.00043792 | -0.15694 | 0.022798 | -0.010004 | 0.010572 | -0.0044262 | 0.0085021 | 0.65918 | 0.75073 | 0.62256 | 0.72784 | 0.82398 | 0.6134 | 0.44861 | 10.025 | 10.1257 | 10.0708 | 10.1486 | 10.1028 | 8.5464 | 8.4824 | 113.8046 | 113.6398 | -9.3338 | 113.942 | 113.9191 | 0.27924 | -9.4986 | 121.7377 | 121.6736 | -0.009155 | 123.2162 | 123.262 | 1.5884 | -0.054932 | 114.0152 | 113.8504 | 113.8138 | -9.7092 | 123.3398 | 123.2941 | 123.317 | -1.6754
3103.5156 | 123.4131 | -113.2187 | 10.1257 | -0.056458 | 0.015022 | 0.0028583 | 0.014744 | -0.01998 | 0.0012668 | -1.0724e-05 | -0.16457 | 0.022371 | -0.010645 | 0.009504 | -0.0016492 | 0.0089295 | 0.62256 | 0.64087 | 0.53558 | 0.6546 | 0.86975 | 0.5722 | 0.40283 | 9.9609 | 10.0525 | 9.9884 | 10.1303 | 10.08 | 8.5327 | 8.4778 | 113.7909 | 113.6215 | -9.256 | 113.8596 | 113.8733 | 0.25177 | -9.5032 | 121.7514 | 121.6965 | 0.004578 | 123.1796 | 123.2071 | 1.5106 | -0.045776 | 114.0884 | 113.8412 | 113.7543 | -9.7229 | 123.349 | 123.2986 | 123.2712 | -1.6479
3104.5156 | 123.4177 | -113.269 | 10.1212 | -0.21667 | 0.012886 | 0.0043537 | 0.011326 | -0.018271 | -0.001083 | 0.00020288 | -0.095902 | 0.020448 | -0.01214 | 0.010999 | -0.0020764 | 0.010425 | 0.63629 | 0.67749 | 0.55847 | 0.65918 | 0.83313 | 0.59052 | 0.41657 | 9.938 | 10.025 | 9.9884 | 10.1074 | 10.0433 | 8.5281 | 8.4641 | 113.8596 | 113.6856 | -9.288 | 113.9465 | 113.9282 | 0.24261 | -9.4849 | 121.7972 | 121.7331 | -0.013733 | 123.2071 | 123.2574 | 1.5244 | -0.07782 | 114.1022 | 113.9053 | 113.8275 | -9.7046 | 123.3765 | 123.3124 | 123.2941 | -1.6571
3105.5156 | 123.4314 | -113.3011 | 10.0662 | -0.13275 | 0.017799 | 0.0060627 | 0.014103 | -0.019766 | 0.0027622 | 0.0023391 | -0.18745 | 0.02173 | -0.010645 | 0.0097176 | -0.0010082 | 0.0067931 | 0.61798 | 0.64087 | 0.53101 | 0.6546 | 0.85602 | 0.5722 | 0.41199 | 9.9197 | 10.0067 | 9.9426 | 10.0662 | 10.0159 | 8.5281 | 8.4641 | 113.8733 | 113.7131 | -9.2102 | 113.942 | 113.9557 | 0.24262 | -9.4482 | 121.8292 | 121.7651 | 0 | 123.2208 | 123.2437 | 1.4786 | -0.050354 | 114.1571 | 113.9191 | 113.8321 | -9.6542 | 123.3673 | 123.317 | 123.3078 | -1.6022
3106.5156 | 123.5001 | -113.2645 | 10.0616 | -0.14801 | 0.011818 | 0.0032855 | 0.011326 | -0.021689 | -0.0038602 | 0.0012711 | -0.11116 | 0.020448 | -0.011927 | 0.0097176 | -0.0031446 | 0.010211 | 0.68665 | 0.78735 | 0.66376 | 0.73242 | 0.80566 | 0.6134 | 0.46234 | 10.0021 | 10.1166 | 10.0525 | 10.0021 | 9.993 | 8.5236 | 8.4686 | 113.8779 | 113.7268 | -9.256 | 114.0518 | 113.9969 | 0.27008 | -9.375 | 121.788 | 121.7331 | -0.05951 | 123.2666 | 123.317 | 1.5839 | -0.068665 | 114.0701 | 113.9511 | 113.9282 | -9.5993 | 123.2666 | 123.2574 | 123.381 | -1.593
3107.5156 | 123.4177 | -113.3743 | 9.993 | -0.10986 | 0.015022 | 0.0037127 | 0.01389 | -0.018698 | 0.0036166 | -0.0021469 | -0.1722 | 0.023866 | -0.0080814 | 0.012708 | -0.0037854 | 0.0085021 | 0.59967 | 0.63629 | 0.52643 | 0.6546 | 0.85144 | 0.5722 | 0.40741 | 9.8419 | 9.9197 | 9.8694 | 9.9976 | 9.9518 | 8.5098 | 8.4412 | 113.9465 | 113.7817 | -9.1415 | 114.0106 | 114.0289 | 0.24719 | -9.3933 | 121.8842 | 121.8155 | 0.004578 | 123.2162 | 123.2437 | 1.4282 | -0.041199 | 114.2258 | 113.974 | 113.9008 | -9.5856 | 123.3719 | 123.3261 | 123.2941 | -1.5518
3108.5156 | 123.4772 | -113.4384 | 9.874 | -0.15564 | 0.012672 | 0.0037127 | 0.011754 | -0.021048 | -0.0030056 | 0.00041648 | -0.14931 | 0.021089 | -0.011713 | 0.010572 | -0.0033582 | 0.0065795 | 0.66834 | 0.78278 | 0.64087 | 0.70496 | 0.81482 | 0.59967 | 0.43945 | 9.8007 | 9.9197 | 9.8419 | 9.8694 | 9.8007 | 8.4824 | 8.432 | 114.0381 | 113.8779 | -9.0591 | 114.2212 | 114.1434 | 0.2655 | -9.2056 | 121.9208 | 121.8704 | -0.004577 | 123.2391 | 123.2803 | 1.4099 | -0.073242 | 114.2532 | 114.1068 | 114.0793 | -9.4345 | 123.3078 | 123.2391 | 123.3582 | -1.442
3109.5156 | 123.3948 | -113.5574 | 9.8053 | -1.651 | 0.013527 | -0.00013251 | 0.01154 | -0.01998 | -0.00065585 | 0.00084388 | -0.13405 | 0.021516 | -0.0095768 | 0.0097176 | -0.0020764 | 0.0076477 | 0.6134 | 0.64545 | 0.53558 | 0.64545 | 0.8606 | 0.60883 | 0.4303 | 9.6359 | 9.7183 | 9.6634 | 9.8236 | 9.7641 | 8.4503 | 8.4 | 114.1663 | 113.9877 | -8.9447 | 114.2029 | 114.2029 | 0.21515 | -9.1919 | 122.0078 | 121.9574 | 0.01831 | 123.1934 | 123.2208 | 1.2634 | -0.041199 | 114.418 | 114.1708 | 114.093 | -9.375 | 123.381 | 123.3215 | 123.2758 | -1.4053
3110.5156 | 123.5001 | -113.5529 | 9.7412 | -0.1709 | 0.013527 | 0.0054217 | 0.012181 | -0.019766 | -0.0040738 | -0.0012923 | -0.088272 | 0.020662 | -0.012995 | 0.0099314 | -0.0037854 | 0.0095703 | 0.68207 | 0.79651 | 0.64087 | 0.71869 | 0.79193 | 0.6134 | 0.43945 | 9.6817 | 9.8053 | 9.7229 | 9.7 | 9.6634 | 8.4412 | 8.3862 | 114.1663 | 113.9923 | -8.9493 | 114.3494 | 114.2715 | 0.27924 | -9.0591 | 121.994 | 121.9391 | -0.041199 | 123.2346 | 123.2758 | 1.3367 | -0.07782 | 114.3448 | 114.2349 | 114.1937 | -9.3018 | 123.2529 | 123.2162 | 123.3582 | -1.355
3111.5156 | 123.4314 | -113.6581 | 9.7 | -0.20905 | 0.01844 | 0.0034991 | 0.015172 | -0.021903 | 0.0025486 | 0.00041648 | -0.11879 | 0.020662 | -0.010858 | 0.010359 | -0.0012218 | 0.0078613 | 0.6134 | 0.63171 | 0.50812 | 0.63171 | 0.82855 | 0.54474 | 0.38452 | 9.5352 | 9.5993 | 9.5535 | 9.7 | 9.6176 | 8.4229 | 8.3588 | 114.2029 | 114.0427 | -8.8715 | 114.2899 | 114.2899 | 0.24719 | -9.0866 | 122.081 | 122.0169 | 0 | 123.1934 | 123.2117 | 1.1948 | -0.082397 | 114.4867 | 114.2715 | 114.1663 | -9.3155 | 123.3582 | 123.2758 | 123.2574 | -1.3412
3112.5156 | 123.5184 | -113.6719 | 9.6085 | 1.828 | 0.013099 | 0.0058491 | 0.0096174 | -0.021475 | -0.0036464 | 0.00084388 | -0.11116 | 0.021089 | -0.014276 | 0.011427 | -0.0033582 | 0.0093567 | 0.70038 | 0.76446 | 0.6546 | 0.71869 | 0.7782 | 0.59052 | 0.42572 | 9.5764 | 9.6954 | 9.6451 | 9.6085 | 9.5352 | 8.4183 | 8.3633 | 114.2624 | 114.0976 | -8.8303 | 114.4363 | 114.3906 | 0.29297 | -8.9081 | 122.0901 | 122.0352 | 0 | 123.2483 | 123.317 | 1.2817 | -0.073242 | 114.4501 | 114.3723 | 114.3265 | -9.1827 | 123.2803 | 123.2071 | 123.3673 | -1.2451
3113.5156 | 123.4131 | -113.768 | 9.6085 | -0.19379 | 0.014168 | 0.00050849 | 0.010258 | -0.016349 | 0.00083955 | 0.00041648 | -0.042496 | 0.021302 | -0.011499 | 0.012068 | -0.0037854 | 0.0076477 | 0.62714 | 0.68207 | 0.56763 | 0.64087 | 0.84228 | 0.58594 | 0.40741 | 9.4574 | 9.5078 | 9.4482 | 9.6405 | 9.5489 | 8.4 | 8.345 | 114.3539 | 114.1754 | -8.7662 | 114.4501 | 114.4089 | 0.23346 | -8.9813 | 122.168 | 122.113 | 0.032044 | 123.2254 | 123.2162 | 1.1032 | -0.059509 | 114.6103 | 114.3951 | 114.3356 | -9.201 | 123.4085 | 123.317 | 123.2758 | -1.2634
3114.5156 | 123.4955 | -113.7817 | 9.5581 | -0.14038 | 0.012459 | 0.0026447 | 0.01389 | -0.021048 | -0.0032192 | 0.00020288 | -0.11116 | 0.020021 | -0.012781 | 0.0090768 | -0.0025036 | 0.010425 | 0.68207 | 0.78278 | 0.64545 | 0.71869 | 0.80566 | 0.59967 | 0.44403 | 9.4757 | 9.581 | 9.5352 | 9.5352 | 9.4757 | 8.3817 | 8.3359 | 114.3814 | 114.2258 | -8.7524 | 114.5645 | 114.5004 | 0.27466 | -8.876 | 122.1634 | 122.1176 | -0.022888 | 123.2574 | 123.317 | 1.1993 | -0.082397 | 114.5874 | 114.4638 | 114.4272 | -9.1141 | 123.317 | 123.2574 | 123.3627 | -1.2222
3115.5156 | 123.4222 | -113.8412 | 9.5261 | -0.20142 | 0.014381 | 0.0039263 | 0.016026 | -0.01763 | 0.0021214 | -0.00022432 | -1.8354 | 0.023225 | -0.009363 | 0.013777 | -0.0035718 | 0.0076477 | 0.60425 | 0.64087 | 0.52643 | 0.6134 | 0.82855 | 0.55847 | 0.3891 | 9.3704 | 9.3796 | 9.3933 | 9.5444 | 9.4894 | 8.3679 | 8.313 | 114.3997 | 114.2303 | -8.6975 | 114.4821 | 114.4547 | 0.2243 | -8.9218 | 122.2092 | 122.1542 | 0.018311 | 123.2117 | 123.2346 | 1.0803 | -0.036621 | 114.6698 | 114.4455 | 114.3677 | -9.137 | 123.3856 | 123.3307 | 123.2208 | -1.2131
3116.5156 | 123.5641 | -113.8321 | 9.4437 | -0.056458 | 0.0086133 | 0.0052081 | 0.013463 | -0.018698 | -0.0047146 | -0.0023605 | -0.0043486 | 0.018739 | -0.011286 | 0.01164 | -0.0029308 | 0.0089295 | 0.67749 | 0.77362 | 0.66376 | 0.70496 | 0.80566 | 0.59509 | 0.44403 | 9.4528 | 9.5489 | 9.4986 | 9.4299 | 9.375 | 8.3588 | 8.3176 | 114.4272 | 114.2761 | -8.638 | 114.6057 | 114.537 | 0.26093 | -8.7662 | 122.1909 | 122.1497 | -0.013733 | 123.2849 | 123.3307 | 1.181 | -0.068665 | 114.6378 | 114.5096 | 114.4958 | -8.9996 | 123.262 | 123.2071 | 123.381 | -1.1261
3117.5156 | 123.4131 | -113.9236 | 9.4574 | -0.46844 | 0.017372 | 0.0017901 | 0.018376 | -0.021903 | 0.0029758 | -0.0017197 | -0.21797 | 0.023225 | -0.0089358 | 0.010786 | -0.00229 | 0.0087157 | 0.59509 | 0.65002 | 0.53101 | 0.63629 | 0.86517 | 0.5722 | 0.39368 | 9.2743 | 9.3521 | 9.288 | 9.4437 | 9.375 | 8.3267 | 8.2764 | 114.4958 | 114.3173 | -8.5922 | 114.5737 | 114.5599 | 0.24261 | -8.8623 | 122.2504 | 122.2 | -0.013732 | 123.1979 | 123.2117 | 1.0117 | -0.082397 | 114.7888 | 114.5187 | 114.4547 | -9.0637 | 123.3673 | 123.2986 | 123.2758 | -1.181
3118.5156 | 123.4955 | -113.9374 | 9.3796 | -0.13275 | 0.012672 | 0.0028583 | 0.010685 | -0.019126 | -0.0030056 | -0.00022432 | -0.13405 | 0.022584 | -0.012781 | 0.009504 | -0.0048534 | 0.0099975 | 0.69122 | 0.75989 | 0.63171 | 0.68665 | 0.78278 | 0.59967 | 0.41657 | 9.3246 | 9.4345 | 9.3567 | 9.3887 | 9.3018 | 8.3267 | 8.2809 | 114.537 | 114.3539 | -8.5968 | 114.6973 | 114.624 | 0.27008 | -8.6884 | 122.2641 | 122.2183 | 0.009155 | 123.262 | 123.2941 | 1.0757 | -0.07782 | 114.7202 | 114.6286 | 114.5691 | -8.963 | 123.3261 | 123.2391 | 123.3719 | -1.0986
3119.5156 | 123.4451 | -114.0015 | 9.3475 | -0.15564 | 0.011177 | 0.0049945 | 0.013035 | -0.01998 | -0.00065585 | 0.00041648 | -0.17983 | 0.02173 | -0.010645 | 0.008436 | -0.00229 | 0.0080749 | 0.64545 | 0.72327 | 0.58594 | 0.66376 | 0.79651 | 0.58594 | 0.40741 | 9.2239 | 9.3109 | 9.2697 | 9.3567 | 9.288 | 8.3038 | 8.2626 | 114.5874 | 114.4089 | -8.551 | 114.7247 | 114.6652 | 0.25635 | -8.7021 | 122.3053 | 122.2641 | 0.009155 | 123.2254 | 123.2712 | 1.0071 | -0.059509 | 114.798 | 114.6469 | 114.5874 | -8.9401 | 123.3582 | 123.2895 | 123.3124 | -1.0849
3120.5156 | 123.5458 | -113.9969 | 9.288 | -0.056458 | 0.0098951 | 0.0028583 | 0.014317 | -0.021475 | -0.0034328 | -0.00086512 | -0.095902 | 0.018953 | -0.012354 | 0.0097176 | -0.0033582 | 0.0087157 | 0.68665 | 0.80566 | 0.64545 | 0.70038 | 0.80566 | 0.59967 | 0.44403 | 9.3063 | 9.3979 | 9.343 | 9.2972 | 9.2239 | 8.2993 | 8.2489 | 114.5966 | 114.4409 | -8.4824 | 114.8026 | 114.6973 | 0.25635 | -8.6014 | 122.2961 | 122.2458 | 0.009155 | 123.3032 | 123.3398 | 1.0941 | -0.064087 | 114.8026 | 114.6835 | 114.6423 | -8.844 | 123.2941 | 123.2208 | 123.3948 | -1.0391
3121.5156 | 123.3994 | -114.0564 | 9.288 | -0.25482 | 0.014808 | 0.0043537 | 0.014103 | -0.019126 | 0.0019078 | 0.00063028 | -0.14168 | 0.022157 | -0.010431 | 0.010999 | -0.0018628 | 0.0072205 | 0.60425 | 0.67749 | 0.54016 | 0.63171 | 0.82855 | 0.55389 | 0.38452 | 9.1278 | 9.1965 | 9.1461 | 9.2972 | 9.2194 | 8.2718 | 8.226 | 114.6103 | 114.4409 | -8.4595 | 114.7339 | 114.6881 | 0.24719 | -8.6838 | 122.3282 | 122.2824 | 0.009155 | 123.1842 | 123.2025 | 0.9201 | -0.068665 | 114.8849 | 114.6606 | 114.5966 | -8.9035 | 123.3536 | 123.2758 | 123.2529 | -1.062
3122.5156 | 123.5321 | -114.0427 | 9.2011 | -0.079346 | 0.01075 | 0.0032855 | 0.0096174 | -0.018698 | -0.0023648 | -0.00043792 | -1.5226 | 0.020234 | -0.011713 | 0.012495 | -0.0033582 | 0.0089295 | 0.70496 | 0.78278 | 0.63171 | 0.6134 | 0.79193 | 0.5722 | 0.40283 | 9.1965 | 9.2606 | 9.2514 | 9.2011 | 9.1599 | 8.2672 | 8.2169 | 114.6149 | 114.4455 | -8.4091 | 114.8254 | 114.6561 | 0.21057 | -8.4961 | 122.3099 | 122.2595 | 0 | 123.2391 | 123.2941 | 1.0345 | -0.041199 | 114.8346 | 114.7476 | 114.6744 | -8.7982 | 123.2437 | 123.2025 | 123.3032 | -0.98419
3123.5156 | 123.4131 | -114.1479 | 9.2102 | -0.18616 | 0.014808 | 0.0052081 | 0.016026 | -0.016989 | 0.00019875 | 0.0010575 | -0.17983 | 0.023225 | -0.0097904 | 0.0092904 | -0.0027172 | 0.0091431 | 0.65002 | 0.70953 | 0.5722 | 0.66376 | 0.80566 | 0.5722 | 0.40283 | 9.0729 | 9.1553 | 9.0866 | 9.2194 | 9.1415 | 8.2352 | 8.1985 | 114.7202 | 114.5508 | -8.4045 | 114.8575 | 114.8117 | 0.26093 | -8.5602 | 122.3831 | 122.3465 | 0.009155 | 123.2208 | 123.2346 | 0.88806 | -0.068664 | 114.9536 | 114.798 | 114.7202 | -8.8074 | 123.3673 | 123.2895 | 123.3032 | -1.0117
3124.5156 | 123.4726 | -114.18 | 9.1232 | -0.033569 | 0.01139 | 0.0022175 | 0.014531 | -0.020621 | -0.0036464 | -0.00043792 | -0.050125 | 0.020875 | -0.013849 | 0.010359 | -0.0037854 | 0.0078613 | 0.68207 | 0.80109 | 0.65002 | 0.68665 | 0.79193 | 0.57678 | 0.43488 | 9.1644 | 9.2468 | 9.169 | 9.137 | 9.0683 | 8.2352 | 8.1848 | 114.7568 | 114.6149 | -8.3313 | 114.9811 | 114.8666 | 0.25177 | -8.4412 | 122.4152 | 122.3648 | 0.013733 | 123.3444 | 123.349 | 0.98419 | -0.054932 | 114.9719 | 114.8621 | 114.83 | -8.6884 | 123.317 | 123.2483 | 123.4268 | -0.93842
3125.5156 | 123.3582 | -114.1937 | 9.1919 | -0.23193 | 0.015236 | 0.0034991 | 0.014958 | -0.020621 | -1.505e-05 | -0.00022432 | -0.1722 | 0.021302 | -0.0095768 | 0.0092904 | -0.0016492 | 0.0082885 | 0.59509 | 0.64087 | 0.52643 | 0.61798 | 0.82398 | 0.55389 | 0.3891 | 8.9813 | 9.0408 | 8.9951 | 9.1507 | 9.0775 | 8.2077 | 8.1528 | 114.7476 | 114.5828 | -8.3679 | 114.8346 | 114.8117 | 0.22888 | -8.5968 | 122.4014 | 122.3465 | -0.041199 | 123.175 | 123.1888 | 0.84229 | -0.11444 | 115.0177 | 114.7888 | 114.7202 | -8.8028 | 123.3444 | 123.2712 | 123.2346 | -1.0391
3126.5156 | 123.555 | -114.2166 | 9.05 | -0.056458 | 0.0083997 | 0.0058491 | 0.010685 | -0.021048 | -0.0017238 | 0.00020288 | -0.011978 | 0.019807 | -0.011927 | 0.010359 | -0.0031446 | 0.011066 | 0.67291 | 0.7782 | 0.63171 | 0.6958 | 0.81024 | 0.59967 | 0.41657 | 9.0729 | 9.1324 | 9.1003 | 9.0775 | 8.9996 | 8.1985 | 8.1573 | 114.8163 | 114.6332 | -8.2397 | 114.9948 | 114.9124 | 0.27924 | -8.3771 | 122.4152 | 122.374 | 0.027466 | 123.2895 | 123.317 | 0.94299 | -0.050354 | 115.0269 | 114.8895 | 114.8483 | -8.6334 | 123.2941 | 123.2162 | 123.349 | -0.89264
3127.5156 | 123.3994 | -114.2853 | 9.082 | -0.21667 | 0.01609 | 0.0028583 | 0.016453 | -0.01998 | 0.00041235 | -0.00065152 | -0.1722 | 0.02173 | -0.011499 | 0.009504 | -0.0029308 | 0.0091431 | 0.62256 | 0.6958 | 0.56305 | 0.66834 | 0.80109 | 0.55389 | 0.39368 | 8.9172 | 8.9722 | 8.9401 | 9.0546 | 9.0179 | 8.1665 | 8.1161 | 114.8392 | 114.679 | -8.2809 | 114.9811 | 114.9536 | 0.27466 | -8.4595 | 122.4518 | 122.4014 | -0.027466 | 123.2025 | 123.2254 | 0.82398 | -0.064087 | 115.0864 | 114.9078 | 114.8483 | -8.6884 | 123.3398 | 123.3032 | 123.2574 | -0.96588
3128.5156 | 123.5275 | -114.267 | 9.0042 | -0.056458 | 0.010109 | 0.0067035 | 0.010258 | -0.018057 | -0.0036464 | 0.0016983 | 0.01091 | 0.019593 | -0.010645 | 0.010359 | -0.0029308 | 0.0095703 | 0.64545 | 0.75531 | 0.62714 | 0.68207 | 0.80109 | 0.59509 | 0.42114 | 9.0042 | 9.0729 | 9.0134 | 9.0088 | 8.9493 | 8.1573 | 8.1207 | 114.8621 | 114.6881 | -8.2031 | 115.0223 | 114.949 | 0.26093 | -8.3588 | 122.4243 | 122.3877 | 0.004578 | 123.2712 | 123.2803 | 0.89264 | -0.054931 | 115.0681 | 114.9124 | 114.8941 | -8.5831 | 123.2758 | 123.2162 | 123.3398 | -0.88348
3129.5156 | 123.4222 | -114.3448 | 9.0088 | -0.19379 | 0.014168 | 0.0043537 | 0.014317 | -0.019766 | 0.00019875 | 0.00020288 | -0.16457 | 0.023439 | -0.013636 | 0.0097176 | -0.0020764 | 0.0082885 | 0.6546 | 0.72784 | 0.57678 | 0.67749 | 0.80109 | 0.56305 | 0.39368 | 8.876 | 8.9676 | 8.8989 | 9.0042 | 8.9401 | 8.1482 | 8.107 | 114.9078 | 114.7385 | -8.2077 | 115.0726 | 115.0223 | 0.28381 | -8.3542 | 122.493 | 122.4518 | -0.004578 | 123.2208 | 123.2437 | 0.79193 | -0.068664 | 115.1459 | 114.9994 | 114.9216 | -8.6151 | 123.349 | 123.2849 | 123.3124 | -0.90179
3130.5156 | 123.6603 | -114.3539 | 8.9676 | -0.048828 | 0.01075 | 0.0056353 | 0.010685 | -0.019339 | -0.0036464 | -1.0724e-05 | -0.050125 | 0.020875 | -0.012354 | 0.0090768 | -0.0035718 | 0.0091431 | 0.66834 | 0.78735 | 0.63171 | 0.70038 | 0.80109 | 0.57678 | 0.41657 | 8.9539 | 9.0637 | 8.9996 | 8.931 | 8.8669 | 8.1528 | 8.0978 | 114.9307 | 114.7705 | -8.1665 | 115.1413 | 115.0543 | 0.28381 | -8.2993 | 122.5067 | 122.4518 | -0.036621 | 123.3078 | 123.3536 | 0.90179 | -0.10071 | 115.155 | 115.0223 | 114.9857 | -8.551 | 123.2849 | 123.2208 | 123.4177 | -0.86975
3131.5156 | 123.3765 | -114.3768 | 8.9859 | -0.15564 | 0.014595 | 0.0030719 | 0.012822 | -0.019339 | 0.00062595 | -0.00022432 | -0.15694 | 0.021089 | -0.010431 | 0.0088632 | -0.0016492 | 0.0080749 | 0.59509 | 0.6546 | 0.52185 | 0.6134 | 0.81482 | 0.54474 | 0.36163 | 8.7845 | 8.8623 | 8.7982 | 8.9584 | 8.8943 | 8.1024 | 8.0612 | 114.9216 | 114.7385 | -8.1711 | 115.0314 | 114.9902 | 0.25177 | -8.3908 | 122.4792 | 122.438 | -0.027466 | 123.1613 | 123.175 | 0.737 | -0.091553 | 115.1916 | 114.9719 | 114.8987 | -8.6243 | 123.3353 | 123.2712 | 123.2391 | -0.92468
3132.5156 | 123.5367 | -114.4135 | 8.8806 | -0.14801 | 0.0066907 | 0.0062763 | 0.011113 | -0.017417 | -0.0030056 | 0.0010575 | -0.080643 | 0.020448 | -0.013422 | 0.010359 | -0.003999 | 0.0087157 | 0.77362 | 0.70038 | 0.59967 | 0.6958 | 0.76446 | 0.5722 | 0.39368 | 8.8623 | 8.963 | 8.8898 | 8.8577 | 8.7982 | 8.0933 | 8.0566 | 114.9857 | 114.8071 | -8.1162 | 115.1138 | 115.1093 | 0.30212 | -8.107 | 122.5067 | 122.4701 | -0.022888 | 123.2758 | 123.3032 | 0.83313 | -0.082397 | 115.1779 | 115.1871 | 115.0131 | -8.4869 | 123.2712 | 123.2117 | 123.3765 | -0.82397
3133.5156 | 123.4772 | -114.473 | 8.8669 | -0.1709 | 0.010109 | 0.0043537 | 0.011326 | -0.021475 | -0.0023648 | -0.0017197 | -0.16457 | 0.022157 | -0.01214 | 0.0097176 | -0.0037854 | 0.0067931 | 0.6546 | 0.7782 | 0.6134 | 0.69122 | 0.7782 | 0.5722 | 0.40283 | 8.7799 | 8.8852 | 8.812 | 8.8531 | 8.7708 | 8.0795 | 8.0338 | 115.0452 | 114.8758 | -8.0887 | 115.2512 | 115.1642 | 0.28839 | -8.2123 | 122.5525 | 122.5067 | -0.013733 | 123.2529 | 123.2849 | 0.7782 | -0.09613 | 115.2512 | 115.1276 | 115.0864 | -8.4641 | 123.3261 | 123.2437 | 123.3582 | -0.83313
3134.5156 | 123.5229 | -114.4684 | 8.7982 | -0.079346 | 0.010963 | 0.0047809 | 0.010045 | -0.020621 | -0.001083 | 0.00020288 | 0.01091 | 0.021089 | -0.01214 | 0.009504 | -0.0020764 | 0.0097839 | 0.65002 | 0.75989 | 0.62256 | 0.6958 | 0.79651 | 0.58136 | 0.41657 | 8.8165 | 8.8715 | 8.8394 | 8.8303 | 8.7387 | 8.0658 | 8.0154 | 115.0497 | 114.8849 | -8.0017 | 115.2283 | 115.1642 | 0.27924 | -8.1482 | 122.5342 | 122.4838 | 0.032043 | 123.2849 | 123.3078 | 0.82397 | -0.05951 | 115.2649 | 115.1184 | 115.0909 | -8.3817 | 123.2986 | 123.2071 | 123.3398 | -0.78278
3135.5156 | 123.4085 | -114.5691 | 8.812 | -0.18616 | 0.016517 | 0.0028583 | 0.011967 | -0.019126 | 0.0042576 | -0.0023605 | -0.36293 | 0.023011 | -0.0097904 | 0.010786 | -0.00229 | 0.0082885 | 0.8606 | 0.58594 | 0.43945 | 0.5722 | 0.86517 | 0.58594 | 0.39825 | 8.6563 | 8.7067 | 8.6609 | 8.8257 | 8.7433 | 8.0338 | 7.9788 | 115.155 | 114.9673 | -7.9468 | 115.155 | 115.1413 | 0.17395 | -7.9514 | 122.6028 | 122.5479 | 0.013733 | 123.2254 | 123.23 | 0.68207 | -0.068665 | 115.4343 | 115.4297 | 115.0085 | -8.4137 | 123.3948 | 123.3124 | 123.2758 | -0.83313
3136.5156 | 123.5504 | -114.5142 | 8.7387 | -0.071716 | 0.012245 | 0.0047809 | 0.011754 | -0.020621 | -0.0019376 | 0.00063028 | -0.11116 | 0.018525 | -0.013208 | 0.011854 | -0.0033582 | 0.0078613 | 0.66834 | 0.80109 | 0.65002 | 0.6958 | 0.77362 | 0.57678 | 0.41199 | 8.8028 | 8.4 | 8.725 | 8.7341 | 8.6609 | 8.0292 | 7.9926 | 115.0909 | 114.9261 | -7.9651 | 115.3152 | 115.21 | 0.28381 | -8.0704 | 122.5433 | 122.5067 | -0.004577 | 123.317 | 123.2391 | 0.73242 | -0.077819 | 115.2878 | 115.1825 | 115.1642 | -8.3267 | 123.2483 | 123.175 | 122.9141 | -0.74615
3137.5156 | 123.5138 | -114.5737 | 8.7296 | -0.10986 | 0.01374 | 0.0022175 | 0.011754 | -0.020407 | -0.00086945 | 0.0014847 | -0.11879 | 0.020875 | -0.01214 | 0.0090768 | -0.0031446 | 0.0072205 | 0.66376 | 0.78278 | 0.62714 | 0.6958 | 0.76446 | 0.56763 | 0.41199 | 8.7021 | 8.812 | 8.7479 | 8.7433 | 8.6609 | 8.0109 | 7.9834 | 115.1413 | 114.9857 | -7.9651 | 115.3564 | 115.2695 | 0.28381 | -8.0658 | 122.5845 | 122.5571 | 0.013733 | 123.2758 | 123.3215 | 0.76447 | -0.068664 | 115.3381 | 115.2374 | 115.2008 | -8.3176 | 123.317 | 123.2346 | 123.3856 | -0.74615
3138.5156 | 123.5229 | -114.6103 | 8.7021 | -0.29297 | 0.010963 | 0.0041401 | 0.013249 | -0.021262 | -1.505e-05 | -0.00065152 | -0.095902 | 0.01938 | -0.010858 | 0.0088632 | -0.0012218 | 0.0074341 | 0.65002 | 0.77362 | 0.62256 | 0.67291 | 0.76904 | 0.55847 | 0.39825 | 8.6884 | 8.7891 | 8.7158 | 8.7112 | 8.6243 | 8.0017 | 7.9605 | 115.1688 | 115.0085 | -7.933 | 115.3839 | 115.2832 | 0.27466 | -8.0521 | 122.612 | 122.5708 | 0.009156 | 123.2986 | 123.3261 | 0.75531 | -0.077819 | 115.3793 | 115.2603 | 115.2328 | -8.3038 | 123.3215 | 123.2346 | 123.3994 | -0.74158
3139.5156 | 123.3994 | -114.5966 | 8.7524 | -0.17853 | 0.012672 | 0.0041401 | 0.014531 | -0.020407 | 0.0025486 | 0.0029801 | -0.19508 | 0.021943 | -0.0091494 | 0.010572 | -0.00079463 | 0.0085021 | 0.58136 | 0.66376 | 0.5127 | 0.60883 | 0.80566 | 0.54474 | 0.37079 | 8.5419 | 8.6288 | 8.5602 | 8.7204 | 8.6334 | 7.9651 | 7.9239 | 115.1413 | 114.9673 | -7.9468 | 115.2603 | 115.2054 | 0.23804 | -8.1711 | 122.5616 | 122.5204 | -0.032043 | 123.1384 | 123.1567 | 0.63629 | -0.11902 | 115.4022 | 115.1779 | 115.1093 | -8.3817 | 123.317 | 123.23 | 123.2254 | -0.82855
3140.5156 | 123.5413 | -114.6515 | 8.6517 | -0.064087 | 0.011604 | 0.0064899 | 0.012394 | -0.020194 | -0.002792 | 0.0027665 | -0.027237 | 0.018953 | -0.012354 | 0.01164 | -0.0025036 | 0.010425 | 0.63629 | 0.77362 | 0.6134 | 0.67749 | 0.78735 | 0.58594 | 0.41199 | 8.6334 | 8.725 | 8.6838 | 8.6472 | 8.5831 | 7.9559 | 7.9285 | 115.2374 | 115.0635 | -7.8644 | 115.4251 | 115.329 | 0.2655 | -8.0154 | 122.6074 | 122.58 | -0.004577 | 123.2849 | 123.3353 | 0.75531 | -0.068664 | 115.4388 | 115.2878 | 115.2649 | -8.2397 | 123.2986 | 123.2346 | 123.3765 | -0.72327
3141.5156 | 123.5138 | -114.6881 | 8.6426 | -0.086975 | 0.013313 | 0.0041401 | 0.014744 | -0.021475 | -0.00022865 | 0.0014847 | -0.11879 | 0.01938 | -0.0095768 | 0.0099314 | -0.0031446 | 0.0080749 | 0.64087 | 0.76904 | 0.6134 | 0.68207 | 0.76446 | 0.56305 | 0.39368 | 8.5785 | 8.6655 | 8.606 | 8.6243 | 8.5327 | 7.9376 | 7.901 | 115.2512 | 115.0818 | -7.8781 | 115.4572 | 115.3702 | 0.28839 | -8.0017 | 122.6257 | 122.5891 | -0.01831 | 123.2666 | 123.2941 | 0.70496 | -0.10986 | 115.4526 | 115.329 | 115.3015 | -8.2489 | 123.3124 | 123.2208 | 123.3536 | -0.74158
3142.5156 | 123.5046 | -114.7293 | 8.5739 | -0.02594 | 0.010536 | 0.0047809 | 0.013035 | -0.023184 | -0.00044225 | 0.00020288 | -0.10353 | 0.02173 | -0.011713 | 0.009504 | -0.0025036 | 0.0046569 | 0.67291 | 0.79193 | 0.63171 | 0.70038 | 0.76904 | 0.56763 | 0.39368 | 8.4686 | 8.8943 | 8.3588 | 8.5556 | 8.5052 | 7.9239 | 7.8781 | 115.2969 | 115.123 | -7.8049 | 115.5212 | 115.4297 | 0.3067 | -7.901 | 122.6532 | 122.6074 | -0.018311 | 123.1979 | 123.0881 | 0.48065 | -0.068665 | 115.4984 | 115.4022 | 115.361 | -8.1802 | 123.2849 | 123.2346 | 123.6237 | -0.6958
3143.5156 | 123.4772 | -114.7797 | 8.5648 | -0.18616 | 0.012245 | 0.0028583 | 0.013676 | -0.018912 | -0.00086945 | -1.0724e-05 | -0.18745 | 0.023011 | -0.010858 | 0.010359 | -0.0020764 | 0.0076477 | 0.64545 | 0.737 | 0.59052 | 0.67291 | 0.77362 | 0.55847 | 0.37994 | 8.4732 | 8.5693 | 8.5007 | 8.5785 | 8.5007 | 7.901 | 7.8552 | 115.3381 | 115.1596 | -7.7911 | 115.5167 | 115.4526 | 0.29297 | -7.9193 | 122.6807 | 122.6349 | 0.013733 | 123.2529 | 123.2803 | 0.64545 | -0.064087 | 115.5533 | 115.4251 | 115.3702 | -8.1848 | 123.3582 | 123.2803 | 123.349 | -0.70953
3144.5156 | 123.5504 | -114.7568 | 8.5052 | -0.056458 | 0.011818 | 0.0049945 | 0.011967 | -0.021262 | -0.001083 | -0.00065152 | 0.01091 | 0.019166 | -0.01449 | 0.010786 | -0.0025036 | 0.0093567 | 0.67291 | 0.7782 | 0.61798 | 0.68207 | 0.77362 | 0.59052 | 0.39825 | 8.5144 | 8.5922 | 8.551 | 8.5052 | 8.432 | 7.8781 | 7.8415 | 115.3473 | 115.155 | -7.7316 | 115.535 | 115.4388 | 0.28381 | -7.8323 | 122.6349 | 122.5983 | 0 | 123.2712 | 123.3078 | 0.70953 | -0.073242 | 115.5304 | 115.4297 | 115.3748 | -8.107 | 123.262 | 123.1888 | 123.349 | -0.66376
3145.5156 | 123.3994 | -114.8575 | 8.5236 | -0.20905 | 0.014168 | 0.0017901 | 0.013463 | -0.019126 | 0.00062595 | 0.0010575 | -0.16457 | 0.022157 | -0.011286 | 0.010572 | -0.005708 | 0.0070067 | 0.59967 | 0.67749 | 0.53558 | 0.62714 | 0.78735 | 0.54932 | 0.37994 | 8.3542 | 8.4274 | 8.3862 | 8.5052 | 8.4366 | 7.8461 | 7.8003 | 115.4068 | 115.2374 | -7.7362 | 115.535 | 115.4846 | 0.24719 | -7.9239 | 122.7036 | 122.6578 | -0.018311 | 123.2117 | 123.2437 | 0.58594 | -0.086976 | 115.6448 | 115.4572 | 115.3931 | -8.1436 | 123.3627 | 123.2941 | 123.2849 | -0.72327
3146.5156 | 123.5321 | -114.8254 | 8.4595 | -0.071716 | 0.011604 | 0.0041401 | 0.012394 | -0.020194 | -0.0034328 | 0.00084388 | -0.10353 | 0.020021 | -0.011927 | 0.0037362 | -0.00229 | 0.012988 | 0.6546 | 0.79193 | 0.62714 | 0.69122 | 0.76904 | 0.55389 | 0.39368 | 8.3588 | 8.3725 | 8.519 | 8.4274 | 8.3542 | 7.8323 | 7.7957 | 115.3793 | 115.2191 | -7.6904 | 115.6174 | 115.5167 | 0.29755 | -7.8049 | 122.6578 | 122.6212 | -0.032044 | 123.1842 | 123.3444 | 0.72327 | -0.10529 | 115.5945 | 115.48 | 115.4526 | -8.0658 | 123.2529 | 123.1796 | 123.1979 | -0.66376
3147.5156 | 123.5367 | -114.8895 | 8.4229 | -0.24719 | 0.014168 | 0.0026447 | 0.013249 | -0.019339 | -0.00044225 | 0.0016983 | -0.14168 | 0.021302 | -0.011927 | 0.0086496 | -0.0018628 | 0.0080749 | 0.65002 | 0.75531 | 0.6134 | 0.66376 | 0.74158 | 0.55847 | 0.40283 | 8.3908 | 8.5098 | 8.4274 | 8.4091 | 8.3496 | 7.8003 | 7.782 | 115.448 | 115.2924 | -7.6813 | 115.6448 | 115.5533 | 0.26093 | -7.7728 | 122.6898 | 122.6715 | -0.013733 | 123.2803 | 123.317 | 0.64545 | -0.073243 | 115.6311 | 115.5396 | 115.5029 | -8.02 | 123.2986 | 123.2391 | 123.3994 | -0.64087
3148.5312 | 123.4451 | -114.9902 | 8.4 | -0.018311 | 0.022285 | 0.0026447 | 0.012394 | -0.016989 | 0.0061802 | 0.00041648 | -0.095902 | 0.023439 | -0.0078678 | 0.010359 | 0.0015552 | 0.0052979 | 0.65002 | 0.66376 | 0.5127 | 0.61798 | 0.77362 | 0.52643 | 0.36163 | 8.3176 | 8.3359 | 8.2626 | 8.4183 | 8.3405 | 7.7728 | 7.7316 | 115.5167 | 115.3519 | -7.6263 | 115.654 | 115.6082 | 0.25635 | -7.7499 | 122.7631 | 122.7219 | 0.018311 | 123.3078 | 123.2529 | 0.53101 | -0.059509 | 115.7639 | 115.6403 | 115.5029 | -8.0383 | 123.4085 | 123.3307 | 123.3261 | -0.66833
3149.5156 | 123.5092 | -114.917 | 8.3725 | -0.10223 | 0.013099 | 0.0039263 | 0.011967 | -0.022116 | -0.0019376 | 0.0014847 | -0.13405 | 0.021302 | -0.010645 | 0.0097176 | -0.0046398 | 0.0087157 | 0.64087 | 0.76446 | 0.60883 | 0.67749 | 0.75989 | 0.55847 | 0.39825 | 8.3221 | 8.4274 | 8.3588 | 8.3588 | 8.3405 | 7.7728 | 7.7362 | 115.4755 | 115.3152 | -7.6126 | 115.6815 | 115.5945 | 0.27924 | -7.7316 | 122.6898 | 122.6532 | -0.013733 | 123.2391 | 123.2758 | 0.62256 | -0.032044 | 115.6769 | 115.5579 | 115.5258 | -7.9742 | 123.2758 | 123.2574 | 123.3444 | -0.63629
3150.5156 | 123.5275 | -114.9216 | 8.3588 | -0.033569 | 0.010963 | 0.0030719 | 0.012181 | -0.020835 | -0.0040738 | 0.00041648 | -0.0043486 | 0.01938 | -0.013422 | 0.007795 | -0.0025036 | 0.0074341 | 0.62256 | 0.71411 | 0.59052 | 0.66376 | 0.78735 | 0.54932 | 0.38452 | 8.3176 | 8.3908 | 8.3405 | 8.3405 | 8.2764 | 7.7499 | 7.7225 | 115.4709 | 115.3061 | -7.5714 | 115.6357 | 115.5853 | 0.27924 | -7.7362 | 122.6715 | 122.644 | -0.018311 | 123.2391 | 123.262 | 0.61798 | -0.082398 | 115.7089 | 115.5441 | 115.5121 | -7.9742 | 123.262 | 123.1979 | 123.3124 | -0.63629
3151.5156 | 123.5321 | -114.9902 | 8.313 | -0.12512 | 0.012459 | 0.0054217 | 0.018803 | -0.020835 | 0.0046848 | 0.00084388 | -0.28664 | 0.018953 | -0.011499 | 0.0092904 | -0.0018628 | 0.0087157 | 0.48523 | 0.82398 | 0.62256 | 0.63629 | 0.71411 | 0.52185 | 0.38452 | 8.2718 | 8.3771 | 8.3313 | 8.2901 | 8.2306 | 7.7316 | 7.695 | 115.5121 | 115.3748 | -7.5989 | 115.8142 | 115.6265 | 0.25177 | -7.8278 | 122.7219 | 122.6852 | -0.022888 | 123.262 | 123.3215 | 0.63629 | -0.082397 | 115.7043 | 115.4755 | 115.6128 | -7.9285 | 123.2803 | 123.2208 | 123.3673 | -0.61798
3152.5156 | 123.5321 | -115.0269 | 8.2901 | 0.012207 | 0.012245 | 0.0041401 | 0.009831 | -0.018698 | -0.0017238 | -0.00065152 | 0.049057 | 0.021302 | -0.012995 | 0.010572 | -0.0029308 | 0.0070067 | 0.64545 | 0.73242 | 0.59509 | 0.6546 | 0.78278 | 0.5722 | 0.40283 | 8.2626 | 8.313 | 8.2901 | 8.2672 | 8.2077 | 7.7133 | 7.6675 | 115.5991 | 115.4297 | -7.5073 | 115.7593 | 115.6815 | 0.25177 | -7.6447 | 122.7402 | 122.6944 | -0.022888 | 123.2895 | 123.317 | 0.62256 | -0.082397 | 115.8096 | 115.6723 | 115.6219 | -7.8873 | 123.2941 | 123.2346 | 123.3398 | -0.62256
3153.5312 | 123.4406 | -115.1047 | 8.226 | 0.14954 | 0.019935 | 0.00050849 | 0.016453 | -0.01998 | 0.0055392 | 0.0012711 | 0.13298 | 0.023866 | -0.0085086 | 0.0097176 | -0.0018628 | 0.0048705 | 0.57678 | 0.59967 | 0.47607 | 0.5722 | 0.79193 | 0.53101 | 0.35706 | 8.139 | 8.1573 | 8.1161 | 8.2672 | 8.1802 | 7.663 | 7.6126 | 115.6357 | 115.4617 | -7.4341 | 115.7043 | 115.6769 | 0.21515 | -7.6492 | 122.7676 | 122.7173 | 0.041199 | 123.2437 | 123.2208 | 0.50354 | -0.045776 | 115.8966 | 115.6815 | 115.5807 | -7.869 | 123.3719 | 123.2849 | 123.262 | -0.6134
3154.5156 | 123.4726 | -115.123 | 8.2031 | 0.12665 | 0.011177 | 0.0039263 | 0.014317 | -0.019553 | -0.0042874 | 0.00041648 | 0.12535 | 0.020234 | -0.015558 | 0.010572 | -0.0016492 | 0.0095703 | 0.59052 | 0.6546 | 0.54016 | 0.62256 | 0.75531 | 0.54016 | 0.38452 | 8.1482 | 8.1711 | 8.1482 | 8.1482 | 8.0933 | 7.6538 | 7.6035 | 115.6631 | 115.5075 | -7.4478 | 115.7776 | 115.7455 | 0.23804 | -7.6126 | 122.7768 | 122.7264 | -0.054932 | 123.2712 | 123.2712 | 0.54474 | -0.10986 | 115.8783 | 115.7135 | 115.6631 | -7.8186 | 123.2712 | 123.2162 | 123.2941 | -0.59967
3155.5156 | 123.5229 | -115.123 | 8.1802 | -0.056458 | 0.010963 | 0.0030719 | 0.012394 | -0.018271 | -0.0030056 | -0.00086512 | -0.011978 | 0.019593 | -0.010218 | 0.012281 | -0.00229 | 0.0085021 | 0.62256 | 0.72327 | 0.58594 | 0.66376 | 0.75531 | 0.59509 | 0.39368 | 8.1665 | 8.2214 | 8.2077 | 8.194 | 8.1299 | 7.6355 | 7.6035 | 115.7181 | 115.5167 | -7.4249 | 115.8463 | 115.7867 | 0.27008 | -7.5577 | 122.7585 | 122.7264 | 0.013733 | 123.2895 | 123.3307 | 0.60425 | -0.050354 | 115.8783 | 115.7455 | 115.7089 | -7.7866 | 123.317 | 123.2529 | 123.3444 | -0.57678
3156.5156 | 123.4772 | -115.1733 | 8.1665 | 0.17242 | 0.014595 | 0.0013629 | 0.011754 | -0.019553 | -0.00044225 | 0.0016983 | 0.15587 | 0.022371 | -0.011713 | 0.0099314 | -0.0029308 | 0.0067931 | 0.64087 | 0.69122 | 0.57678 | 0.63629 | 0.78278 | 0.55847 | 0.40283 | 8.107 | 8.1345 | 8.1024 | 8.1299 | 8.0658 | 7.6172 | 7.5714 | 115.7318 | 115.5762 | -7.3837 | 115.8646 | 115.8096 | 0.23346 | -7.5256 | 122.7905 | 122.7448 | -0.036621 | 123.2803 | 123.2758 | 0.53101 | -0.10071 | 115.9561 | 115.8142 | 115.7501 | -7.7637 | 123.3032 | 123.2391 | 123.3078 | -0.59509
3157.5156 | 123.5092 | -115.155 | 8.1345 | -0.048828 | 0.010536 | 0.0058491 | 0.01154 | -0.019339 | -0.0023648 | -0.0012923 | -0.057755 | 0.020875 | -0.01214 | 0.0092904 | -0.0037854 | 0.0057251 | 0.63629 | 0.74158 | 0.58136 | 0.6546 | 0.78278 | 0.56763 | 0.37994 | 8.1253 | 8.1985 | 8.1528 | 8.1299 | 8.0658 | 7.6035 | 7.576 | 115.7227 | 115.535 | -7.3517 | 115.8966 | 115.8096 | 0.27466 | -7.4982 | 122.7585 | 122.731 | -0.004577 | 123.2803 | 123.3078 | 0.57678 | -0.068664 | 115.9378 | 115.7913 | 115.7364 | -7.7545 | 123.2849 | 123.2208 | 123.3536 | -0.55847
3158.5156 | 123.4131 | -115.2512 | 8.1299 | -0.13275 | 0.018226 | 0.0026447 | 0.013676 | -0.019339 | 0.003403 | 0.0010575 | -0.2256 | 0.023011 | -0.010431 | 0.0086496 | -0.0025036 | 0.0061523 | 0.57678 | 0.60425 | 0.46692 | 0.58136 | 0.79651 | 0.50354 | 0.32959 | 7.9788 | 8.0383 | 7.9834 | 8.1482 | 8.0612 | 7.5577 | 7.5165 | 115.7547 | 115.5807 | -7.3334 | 115.8554 | 115.8325 | 0.25177 | -7.5531 | 122.8088 | 122.7676 | 0.01831 | 123.23 | 123.2346 | 0.46692 | -0.068665 | 116.0477 | 115.8279 | 115.7181 | -7.8003 | 123.3994 | 123.3124 | 123.2895 | -0.6134
3159.5156 | 123.5321 | -115.21 | 8.0887 | 0.0045777 | 0.0092541 | 0.0030719 | 0.011326 | -0.020407 | -0.0019376 | 0.0010575 | -0.011978 | 0.021302 | -0.012995 | 0.010359 | -0.0031446 | 0.0085021 | 0.63629 | 0.737 | 0.60425 | 0.67291 | 0.76904 | 0.56763 | 0.40283 | 8.0658 | 8.139 | 8.1024 | 8.0658 | 8.0063 | 7.576 | 7.5211 | 115.7776 | 115.6128 | -7.3196 | 115.947 | 115.8829 | 0.27008 | -7.4524 | 122.786 | 122.731 | -0.022888 | 123.2758 | 123.3124 | 0.58136 | -0.082397 | 115.979 | 115.8463 | 115.8142 | -7.6859 | 123.2758 | 123.2162 | 123.349 | -0.56763
3160.5156 | 123.4818 | -115.274 | 8.0338 | 0.12665 | 0.011818 | 0.0020037 | 0.014103 | -0.023398 | 0.00019875 | -0.00022432 | 0.17113 | 0.020448 | -0.0085086 | 0.010572 | -0.0033582 | 0.0085021 | 0.59509 | 0.67291 | 0.55389 | 0.6134 | 0.75531 | 0.55389 | 0.37994 | 7.9742 | 8.0063 | 7.9926 | 8.0338 | 7.9697 | 7.5165 | 7.4936 | 115.8279 | 115.654 | -7.2784 | 115.947 | 115.8875 | 0.23346 | -7.4387 | 122.7905 | 122.7676 | 0 | 123.2483 | 123.2666 | 0.49896 | -0.064086 | 116.0294 | 115.8691 | 115.8279 | -7.6538 | 123.3078 | 123.2437 | 123.2803 | -0.54016
3161.5156 | 123.4955 | -115.2969 | 7.9926 | 0.057983 | 0.012672 | 0.0043537 | 0.010045 | -0.016989 | -0.00065585 | 0.0012711 | 0.41527 | 0.021089 | -0.011286 | 0.012281 | -0.0012218 | 0.0074341 | 0.59509 | 0.66376 | 0.55389 | 0.37079 | 0.72784 | 0.51727 | 0.33417 | 7.9102 | 7.9514 | 7.9559 | 7.9834 | 7.9102 | 7.4844 | 7.4432 | 115.8142 | 115.6311 | -7.2647 | 115.9607 | 115.6677 | 0.036622 | -7.3975 | 122.7814 | 122.7402 | -0.009156 | 123.2071 | 123.2529 | 0.5127 | -0.082398 | 116.0248 | 115.892 | 115.8508 | -7.6584 | 123.2803 | 123.2071 | 123.2483 | -0.54932
3162.5156 | 123.4863 | -115.3427 | 7.9559 | 0.17242 | 0.01374 | 0.0026447 | 0.013463 | -0.018485 | 0.00062595 | -0.00043792 | 0.20927 | 0.020448 | -0.010218 | 0.0097176 | -0.0027172 | 0.010638 | 0.65002 | 0.71869 | 0.57678 | 0.64545 | 0.72784 | 0.56763 | 0.3891 | 7.9239 | 7.9514 | 7.9239 | 7.9376 | 7.8781 | 7.4524 | 7.4158 | 115.9103 | 115.7318 | -7.2281 | 116.0614 | 115.9882 | 0.25635 | -7.3059 | 122.7951 | 122.7585 | -0.018311 | 123.2666 | 123.2666 | 0.50812 | -0.07782 | 116.0706 | 115.9927 | 115.9195 | -7.5668 | 123.2803 | 123.2208 | 123.2941 | -0.54016
3163.5312 | 123.4726 | -115.4388 | 7.9422 | -0.13275 | 0.019935 | 0.0030719 | 0.017308 | -0.020621 | 0.0044712 | 0.00063028 | -0.24086 | 0.023011 | -0.0091494 | 0.0092904 | -0.00036743 | 0.0029479 | 0.59052 | 0.58594 | 0.46692 | 0.6134 | 0.78278 | 0.51727 | 0.33417 | 7.8415 | 7.8781 | 7.8003 | 7.9514 | 7.8735 | 7.4066 | 7.37 | 115.9561 | 115.773 | -7.1594 | 116.0248 | 116.0522 | 0.27924 | -7.3517 | 122.8455 | 122.8088 | 0.009155 | 123.2803 | 123.2391 | 0.4303 | -0.068665 | 116.2216 | 116.0294 | 115.9058 | -7.608 | 123.3902 | 123.3124 | 123.317 | -0.5722
3164.5156 | 123.5092 | -115.4068 | 7.8827 | 0.073242 | 0.016945 | 0.0024311 | 0.011326 | -0.019126 | 0.00062595 | 0.0014847 | 0.17876 | 0.018953 | -0.0089358 | 0.008436 | -0.0018628 | 0.0085021 | 0.6546 | 0.71411 | 0.59052 | 0.64545 | 0.737 | 0.55389 | 0.39368 | 7.8781 | 7.9193 | 7.8735 | 7.8873 | 7.7957 | 7.4249 | 7.3654 | 115.9607 | 115.8005 | -7.1457 | 116.1209 | 116.0522 | 0.25177 | -7.2281 | 122.8317 | 122.7722 | 0.004578 | 123.2849 | 123.2803 | 0.50812 | -0.086975 | 116.1438 | 116.0614 | 115.9973 | -7.489 | 123.2941 | 123.2025 | 123.3261 | -0.51727
3165.5156 | 123.5001 | -115.4251 | 7.8552 | 0.12665 | 0.010109 | 0.0047809 | 0.010685 | -0.020194 | -0.0023648 | -0.00086512 | 0.11772 | 0.020234 | -0.011713 | 0.0088632 | -0.0018628 | 0.0095703 | 0.59967 | 0.66834 | 0.54016 | 0.59967 | 0.76904 | 0.55847 | 0.37994 | 7.7957 | 7.8323 | 7.8186 | 7.8552 | 7.7957 | 7.3929 | 7.3517 | 115.9836 | 115.8051 | -7.0862 | 116.0934 | 116.0248 | 0.21973 | -7.2556 | 122.818 | 122.7768 | 0 | 123.2208 | 123.2437 | 0.46692 | -0.05951 | 116.1942 | 116.0248 | 115.9653 | -7.4753 | 123.2803 | 123.2208 | 123.2574 | -0.50354
3166.5156 | 123.5046 | -115.4709 | 7.8369 | 0.19531 | 0.014381 | 0.0020037 | 0.012608 | -0.021903 | -0.0019376 | 0.0016983 | 0.2169 | 0.021302 | -0.010645 | 0.010145 | -0.00229 | 0.0085021 | 0.6546 | 0.71411 | 0.59967 | 0.64545 | 0.74616 | 0.55389 | 0.38452 | 7.814 | 7.8369 | 7.8003 | 7.8323 | 7.7545 | 7.3608 | 7.3151 | 116.0248 | 115.8554 | -7.0908 | 116.185 | 116.1163 | 0.26093 | -7.1823 | 122.8317 | 122.7859 | -0.004578 | 123.2849 | 123.2712 | 0.48523 | -0.082397 | 116.217 | 116.1255 | 116.0706 | -7.4524 | 123.3032 | 123.2254 | 123.3078 | -0.52185
3167.5156 | 123.5046 | -115.5487 | 7.7454 | 0.21057 | 0.013099 | 0.0030719 | 0.011113 | -0.019339 | -0.0019376 | 0.00084388 | 0.071945 | 0.023011 | -0.010645 | 0.0092904 | -0.00036743 | 0.0085021 | 0.59509 | 0.66834 | 0.54474 | 0.61798 | 0.76446 | 0.55389 | 0.37537 | 7.5302 | 7.8003 | 7.6721 | 7.7591 | 7.6813 | 7.3334 | 7.2922 | 116.1026 | 115.9241 | -6.9809 | 116.217 | 116.1667 | 0.24262 | -7.1503 | 122.8821 | 122.8409 | 0.013733 | 123.0789 | 123.2208 | 0.37994 | -0.064087 | 116.3132 | 116.1438 | 116.0934 | -7.37 | 123.3078 | 123.23 | 123.349 | -0.45319
3168.5156 | 123.4955 | -115.5396 | 7.7591 | 0.23346 | 0.016731 | 0.0022175 | 0.011754 | -0.019339 | 0.002335 | 0.0016983 | 0.18639 | 0.024507 | -0.011499 | 0.010786 | -0.00058103 | 0.0055115 | 0.60883 | 0.60425 | 0.5127 | 0.59967 | 0.75073 | 0.54016 | 0.36163 | 7.7454 | 7.7454 | 7.7225 | 7.7774 | 7.7042 | 7.3105 | 7.2739 | 116.0797 | 115.9012 | -7.0084 | 116.1438 | 116.1392 | 0.23804 | -7.1503 | 122.85 | 122.8134 | 0.018311 | 123.2849 | 123.262 | 0.44861 | -0.054931 | 116.2903 | 116.1484 | 116.0522 | -7.3975 | 123.317 | 123.2437 | 123.2849 | -0.48523
3169.5156 | 123.5229 | -115.5441 | 7.7133 | 0.18768 | 0.013099 | 0.0045673 | 0.010472 | -0.018912 | 0.0012668 | 0.0031937 | 0.18639 | 0.020448 | -0.013636 | 0.010999 | -0.00079463 | 0.0095703 | 0.6546 | 0.71411 | 0.58594 | 0.63629 | 0.72784 | 0.56305 | 0.37994 | 7.7545 | 7.7683 | 7.7316 | 7.7499 | 7.6859 | 7.2968 | 7.2647 | 116.1072 | 115.9241 | -6.9855 | 116.2582 | 116.1804 | 0.25635 | -7.0587 | 122.8409 | 122.8088 | 0.036621 | 123.2986 | 123.2758 | 0.46692 | -0.027466 | 116.272 | 116.1987 | 116.1301 | -7.3334 | 123.2941 | 123.23 | 123.3124 | -0.44861
3170.5156 | 123.5229 | -115.5624 | 7.6904 | 0.23346 | 0.019081 | 0.0022175 | 0.015599 | -0.018698 | 0.004044 | 0.0021255 | 0.15587 | 0.023225 | -0.012995 | 0.010786 | -0.00058103 | 0.0076477 | 0.62714 | 0.66834 | 0.54016 | 0.63171 | 0.75531 | 0.54474 | 0.38452 | 7.6996 | 7.7499 | 7.695 | 7.7225 | 7.6584 | 7.2784 | 7.2372 | 116.1072 | 115.947 | -6.9351 | 116.2308 | 116.1942 | 0.24719 | -7.0633 | 122.8409 | 122.7997 | 0.032043 | 123.262 | 123.2574 | 0.45776 | -0.032044 | 116.3177 | 116.1896 | 116.1026 | -7.3059 | 123.2849 | 123.2208 | 123.3124 | -0.45319
3171.5156 | 123.5001 | -115.5945 | 7.6904 | 0.21057 | 0.013099 | 0.0017901 | 0.013463 | -0.018271 | -0.0012966 | 0.0012711 | 0.20164 | 0.021302 | -0.010858 | 0.011213 | -0.0025036 | 0.0089295 | 0.63629 | 0.70496 | 0.58136 | 0.63629 | 0.71411 | 0.55847 | 0.3891 | 7.6996 | 7.7133 | 7.6859 | 7.7042 | 7.6309 | 7.2601 | 7.2189 | 116.153 | 115.9836 | -6.9763 | 116.2994 | 116.2308 | 0.24719 | -7.0541 | 122.8546 | 122.8134 | 0.013733 | 123.2941 | 123.2803 | 0.46692 | -0.05951 | 116.3086 | 116.2308 | 116.1758 | -7.3013 | 123.2986 | 123.2254 | 123.3078 | -0.4715
3172.5156 | 123.468 | -115.6357 | 7.6859 | 0.19531 | 0.017158 | 0.0034991 | 0.01389 | -0.019553 | 0.00083955 | -0.00022432 | 0.17876 | 0.023866 | -0.010858 | 0.0088632 | -0.00036743 | 0.0076477 | 0.5722 | 0.5722 | 0.4715 | 0.56763 | 0.77362 | 0.52643 | 0.35706 | 7.608 | 7.6309 | 7.608 | 7.7179 | 7.6355 | 7.2144 | 7.1777 | 116.1621 | 115.9927 | -6.9122 | 116.2079 | 116.2033 | 0.21057 | -7.1136 | 122.85 | 122.8134 | 0.032044 | 123.2437 | 123.2437 | 0.4303 | -0.050354 | 116.4093 | 116.2079 | 116.1072 | -7.3288 | 123.3536 | 123.2712 | 123.2666 | -0.50812
3173.5156 | 123.4909 | -115.6219 | 7.6309 | 0.18005 | 0.015236 | 0.0049945 | 0.010045 | -0.020835 | -0.0025784 | 0.0027665 | 0.20927 | 0.02173 | -0.012567 | 0.010786 | -0.0025036 | 0.0091431 | 0.6546 | 0.68207 | 0.59509 | 0.63171 | 0.737 | 0.56763 | 0.37537 | 7.6218 | 7.6584 | 7.6263 | 7.6584 | 7.6172 | 7.2144 | 7.1732 | 116.1896 | 115.9973 | -6.8939 | 116.304 | 116.2537 | 0.25635 | -6.9763 | 122.8363 | 122.7951 | 0.027466 | 123.2437 | 123.2483 | 0.45319 | -0.013733 | 116.3589 | 116.2766 | 116.217 | -7.2556 | 123.2803 | 123.2391 | 123.2803 | -0.45776
3174.5156 | 123.4177 | -115.7272 | 7.6309 | 0.20294 | 0.019295 | 0.0022175 | 0.010899 | -0.019553 | 0.0029758 | 0.0042619 | 0.11772 | 0.022584 | -0.011072 | 0.010145 | -0.00036743 | 0.010638 | 0.56763 | 0.55847 | 0.44403 | 0.55847 | 0.76904 | 0.49439 | 0.32501 | 7.4936 | 7.5256 | 7.4982 | 7.6538 | 7.6126 | 7.164 | 7.1228 | 116.2216 | 116.0522 | -6.8619 | 116.2857 | 116.2857 | 0.23346 | -7.0633 | 122.8912 | 122.85 | 0.022889 | 123.2208 | 123.2254 | 0.37537 | -0.01831 | 116.4963 | 116.2949 | 116.1713 | -7.3059 | 123.381 | 123.3398 | 123.2529 | -0.50812
3175.5156 | 123.5504 | -115.7089 | 7.5577 | 0.2182 | 0.016731 | 0.0049945 | 0.010899 | -0.01763 | 0.00041235 | 0.0010575 | 0.19402 | 0.021302 | -0.008295 | 0.010145 | -0.00058103 | 0.0089295 | 0.64087 | 0.68207 | 0.56305 | 0.62714 | 0.74158 | 0.54016 | 0.37079 | 7.5806 | 7.6218 | 7.5806 | 7.5897 | 7.5027 | 7.1823 | 7.1274 | 116.2491 | 116.0797 | -6.8161 | 116.391 | 116.3361 | 0.25635 | -6.9168 | 122.8912 | 122.8363 | 0.032044 | 123.2895 | 123.2895 | 0.45319 | -0.054931 | 116.4505 | 116.3498 | 116.272 | -7.1869 | 123.2986 | 123.2117 | 123.3307 | -0.4303
3176.5156 | 123.4222 | -115.7547 | 7.5989 | 0.17242 | 0.020363 | 0.0047809 | 0.01389 | -0.019553 | 0.0042576 | 0.0016983 | 0.18639 | 0.023225 | -0.0097904 | 0.011854 | 0.00091437 | 0.0070067 | 0.54932 | 0.54474 | 0.43488 | 0.55389 | 0.76446 | 0.48981 | 0.33875 | 7.4661 | 7.489 | 7.4478 | 7.5943 | 7.5302 | 7.1228 | 7.0724 | 116.2445 | 116.0934 | -6.8344 | 116.2994 | 116.3086 | 0.21515 | -7.0496 | 122.8775 | 122.8271 | -0.004578 | 123.2208 | 123.2025 | 0.37537 | -0.068665 | 116.5192 | 116.304 | 116.1896 | -7.2601 | 123.349 | 123.2849 | 123.2437 | -0.52643
3177.5156 | 123.5413 | -115.7684 | 7.5165 | 0.18768 | 0.016731 | 0.0030719 | 0.012608 | -0.018698 | -0.00044225 | 0.0014847 | 0.20164 | 0.02173 | -0.0091494 | 0.0071542 | -0.0016492 | 0.0080749 | 0.62714 | 0.66834 | 0.5722 | 0.67291 | 0.73242 | 0.54016 | 0.36163 | 7.5577 | 7.4982 | 7.5485 | 7.5119 | 7.4478 | 7.1228 | 7.0633 | 116.3086 | 116.1301 | -6.7841 | 116.4368 | 116.4413 | 0.31128 | -6.8893 | 122.8912 | 122.8317 | -0.004577 | 123.3261 | 123.317 | 0.48523 | -0.068664 | 116.5009 | 116.3956 | 116.3406 | -7.1548 | 123.2803 | 123.2162 | 123.2666 | -0.45319
3178.5156 | 123.3948 | -115.8279 | 7.5439 | 0.19531 | 0.02079 | 0.0043537 | 0.010045 | -0.017417 | -0.0032192 | -0.00065152 | 0.28557 | 0.02472 | -0.0095768 | 0.012495 | -0.0016492 | 0.0070067 | 0.7782 | 0.44403 | 0.40741 | 0.58594 | 0.79651 | 0.52185 | 0.35248 | 7.3746 | 7.3975 | 7.3792 | 7.5348 | 7.4936 | 7.0679 | 7.0267 | 116.3498 | 116.1804 | -6.7474 | 116.272 | 116.4139 | 0.23346 | -6.7657 | 122.8958 | 122.8546 | -0.009155 | 123.2025 | 123.2071 | 0.35248 | -0.050354 | 116.6245 | 116.6061 | 116.2354 | -7.1915 | 123.3627 | 123.3215 | 123.2254 | -0.51727
3179.5156 | 123.5275 | -115.8142 | 7.4707 | 0.15717 | 0.016304 | 0.0024311 | 0.011326 | -0.018698 | 0.00062595 | 0.0031937 | 0.70518 | 0.021943 | -0.010858 | 0.0092904 | -0.00079463 | 0.010211 | 0.63171 | 0.68207 | 0.57678 | 0.60883 | 0.71411 | 0.53101 | 0.35706 | 7.4387 | 7.5348 | 7.4753 | 7.457 | 7.3975 | 7.0633 | 7.0175 | 116.3452 | 116.1713 | -6.7566 | 116.4963 | 116.423 | 0.25177 | -6.839 | 122.8775 | 122.8317 | -0.013733 | 123.2529 | 123.2895 | 0.45776 | -0.073242 | 116.5283 | 116.4459 | 116.391 | -7.1136 | 123.2712 | 123.2117 | 123.349 | -0.45319
3180.5156 | 123.4177 | -115.8875 | 7.4799 | -2.0172 | 0.01844 | -0.00013251 | 0.014531 | -0.018271 | 0.00019875 | 0.0029801 | 0.20927 | 0.021943 | -0.0076542 | 0.012068 | -0.0010082 | 0.0080749 | 0.50354 | 0.55389 | 0.45319 | 0.55847 | 0.78278 | 0.50354 | 0.32501 | 7.3242 | 7.3334 | 7.3196 | 7.4982 | 7.4524 | 7.0312 | 6.9763 | 116.391 | 116.2125 | -6.6971 | 116.4413 | 116.4459 | 0.23346 | -6.9763 | 122.9187 | 122.8638 | 0.018311 | 123.2117 | 123.2071 | 0.34332 | -0.027465 | 116.6702 | 116.391 | 116.3406 | -7.1548 | 123.3856 | 123.3398 | 123.2208 | -0.50354
3181.5156 | 123.5275 | -115.8691 | 7.4295 | 0.21057 | 0.01844 | 0.0052081 | 0.012394 | -0.01998 | 0.0012668 | -0.00022432 | 0.20927 | 0.02408 | -0.010218 | 0.01164 | -0.00036743 | 0.0097839 | 0.57678 | 0.59967 | 0.49439 | 0.58594 | 0.73242 | 0.52185 | 0.35248 | 7.4066 | 7.4249 | 7.4158 | 7.4432 | 7.3837 | 7.0312 | 6.9946 | 116.391 | 116.2216 | -6.6971 | 116.4688 | 116.4551 | 0.23346 | -6.8527 | 122.9004 | 122.8638 | 0.013733 | 123.2758 | 123.2849 | 0.42114 | -0.045776 | 116.6016 | 116.4459 | 116.3635 | -7.077 | 123.3124 | 123.2529 | 123.2941 | -0.43487
3182.5156 | 123.4131 | -115.9103 | 7.4524 | 0.027466 | 0.019935 | 0.0032855 | 0.013249 | -0.017203 | 0.0025486 | 0.0016983 | 0.0032804 | 0.022584 | -0.010218 | 0.010999 | -0.00079463 | 0.0080749 | 0.55847 | 0.5722 | 0.45776 | 0.5722 | 0.74158 | 0.50812 | 0.32501 | 7.2968 | 7.3563 | 7.2876 | 7.4432 | 7.4158 | 6.9992 | 6.9489 | 116.4185 | 116.2354 | -6.7108 | 116.4825 | 116.4825 | 0.24719 | -6.8939 | 122.9095 | 122.8592 | -0.009156 | 123.2071 | 123.1979 | 0.33875 | -0.036622 | 116.6519 | 116.4688 | 116.3681 | -7.1274 | 123.3536 | 123.3261 | 123.2666 | -0.50354
3183.5156 | 123.3902 | -115.9607 | 7.4158 | 0.11902 | 0.019081 | 0.0060627 | 0.010899 | -0.016349 | 0.002335 | 0.0027665 | 1.6436 | 0.022371 | -0.01214 | 0.013349 | -0.00015383 | 0.0093567 | 0.51727 | 0.53558 | 0.43488 | 0.62714 | 0.77362 | 0.51727 | 0.35248 | 7.2556 | 7.3425 | 7.2418 | 7.4249 | 7.3837 | 6.9717 | 6.9214 | 116.478 | 116.3132 | -6.6421 | 116.4963 | 116.5878 | 0.27466 | -6.8985 | 122.9324 | 122.8821 | 0.009156 | 123.2162 | 123.2025 | 0.32043 | -0.032043 | 116.7343 | 116.478 | 116.3956 | -7.0633 | 123.3856 | 123.3444 | 123.3032 | -0.49438
3184.5156 | 123.4131 | -115.979 | 7.3929 | 0.019836 | 0.021858 | 0.0017901 | 0.014317 | -0.020621 | 0.002335 | 0.0027665 | 0.026169 | 0.023866 | -0.0091494 | 0.0092904 | 0.001128 | 0.0093567 | 0.56305 | 0.56305 | 0.45319 | 0.56305 | 0.75531 | 0.4715 | 0.32044 | 7.2327 | 7.2968 | 7.2281 | 7.4112 | 7.3517 | 6.9672 | 6.9168 | 116.4505 | 116.2994 | -6.6376 | 116.5421 | 116.5421 | 0.24261 | -6.8298 | 122.9462 | 122.8958 | 0.018311 | 123.2117 | 123.2071 | 0.31128 | -0.041198 | 116.7343 | 116.5421 | 116.4322 | -7.0724 | 123.3902 | 123.3307 | 123.2758 | -0.47607
3185.5156 | 123.3948 | -116.0156 | 7.37 | 0.073242 | 0.022499 | 0.0017901 | 0.013249 | -0.017844 | 0.002335 | 0.0014847 | 0.026169 | 0.024507 | -0.0072268 | 0.007795 | -0.0010082 | 0.0085021 | 0.5127 | 0.52185 | 0.42114 | 0.54932 | 0.75531 | 0.47607 | 0.28839 | 7.1686 | 7.2418 | 7.1915 | 7.402 | 7.3334 | 6.9168 | 6.871 | 116.4917 | 116.304 | -6.6147 | 116.5375 | 116.5649 | 0.26093 | -6.8573 | 122.9324 | 122.8867 | 0.032044 | 123.1842 | 123.2071 | 0.32043 | -0.036621 | 116.7709 | 116.5283 | 116.4368 | -7.0816 | 123.4177 | 123.349 | 123.2574 | -0.49896
3186.5156 | 123.436 | -116.0156 | 7.3242 | -0.39215 | 0.021644 | 0.0037127 | 0.015172 | -0.020407 | 0.004044 | 0.0012711 | 0.01091 | 0.024934 | -0.0074404 | 0.010572 | -0.00229 | 0.0085021 | 0.59967 | 0.59509 | 0.48523 | 0.59509 | 0.75989 | 0.5127 | 0.32959 | 7.2052 | 7.2784 | 7.2098 | 7.3242 | 7.3105 | 6.926 | 6.8756 | 116.5283 | 116.3452 | -6.5643 | 116.6107 | 116.6107 | 0.2655 | -6.7245 | 122.9416 | 122.8912 | 0 | 123.2208 | 123.2254 | 0.33417 | -0.013733 | 116.7755 | 116.6153 | 116.5009 | -6.9946 | 123.3398 | 123.3261 | 123.2941 | -0.44861
3187.5156 | 123.4085 | -116.0522 | 7.3059 | 0.16479 | 0.021431 | 0.0034991 | 0.013676 | -0.021048 | 0.0087436 | 0.0014847 | -0.21034 | 0.022157 | -0.0089358 | 0.0088632 | -0.0012218 | 0.010211 | 0.32044 | 0.76904 | 0.52185 | 0.5127 | 0.77362 | 0.49896 | 0.3479 | 7.1411 | 7.1732 | 7.1365 | 7.3013 | 7.3013 | 6.8756 | 6.8253 | 116.5512 | 116.4001 | -6.5323 | 116.8213 | 116.5649 | 0.1648 | -6.9855 | 122.9279 | 122.8775 | -0.004577 | 123.1934 | 123.1888 | 0.31128 | -0.004577 | 116.8259 | 116.3727 | 116.5741 | -6.958 | 123.3536 | 123.3536 | 123.2254 | -0.48065
3188.5156 | 123.5184 | -116.0522 | 7.3242 | -0.086975 | 0.019722 | 0.0043537 | 0.015812 | -0.019766 | 0.00083955 | 0.00063028 | -0.073013 | 0.023652 | -0.010218 | 0.010145 | -0.0012218 | 0.0089295 | 0.58136 | 0.59052 | 0.48981 | 0.59052 | 0.75073 | 0.48981 | 0.32501 | 7.1594 | 7.251 | 7.1823 | 7.3013 | 7.2693 | 6.8527 | 6.8161 | 116.5421 | 116.3773 | -6.5735 | 116.6428 | 116.6428 | 0.2655 | -6.7429 | 122.905 | 122.8683 | -0.022888 | 123.2117 | 123.2346 | 0.36621 | -0.054932 | 116.803 | 116.6336 | 116.5421 | -6.9992 | 123.3536 | 123.3215 | 123.3032 | -0.50812
3189.5156 | 123.4131 | -116.1026 | 7.2601 | 0.0045777 | 0.019935 | 0.0028583 | 0.013463 | -0.021903 | 0.0027622 | 0.0010575 | 0.033798 | 0.025789 | -0.0067996 | 0.013349 | -0.00036743 | 0.011279 | 0.56305 | 0.57678 | 0.46234 | 0.5722 | 0.74616 | 0.48523 | 0.32959 | 7.0999 | 7.1594 | 7.1045 | 7.2693 | 7.2372 | 6.8298 | 6.7886 | 116.5878 | 116.4322 | -6.514 | 116.6794 | 116.6748 | 0.24261 | -6.6971 | 122.9324 | 122.8912 | 0.009155 | 123.2025 | 123.2071 | 0.31586 | -0.022888 | 116.8488 | 116.6656 | 116.5649 | -6.9305 | 123.3719 | 123.3398 | 123.262 | -0.4715
3190.5156 | 123.381 | -116.0065 | 7.2968 | -0.079346 | 0.018867 | 0.0043537 | 0.016026 | -0.019553 | -0.0019376 | 0.0012711 | -0.095902 | 0.023011 | -0.0085086 | 0.010572 | -0.0010082 | 0.0082885 | 0.56763 | 0.59052 | 0.47607 | 0.59052 | 0.74616 | 0.49439 | 0.31586 | 7.1182 | 7.196 | 7.1274 | 7.2601 | 7.2281 | 6.8207 | 6.7749 | 116.5009 | 116.3223 | -6.5506 | 116.597 | 116.597 | 0.27466 | -6.7291 | 122.8271 | 122.7814 | -0.036621 | 123.1247 | 123.1338 | 0.35248 | -0.068665 | 116.7526 | 116.5741 | 116.4825 | -6.9809 | 123.2666 | 123.2346 | 123.2025 | -0.52185
3191.5156 | 123.4177 | -116.1209 | 7.2372 | -0.010681 | 0.021431 | 0.0015765 | 0.014744 | -0.022116 | 0.002335 | 0.0014847 | 0.033798 | 0.02472 | -0.0091494 | 0.013777 | -0.0020764 | 0.0070067 | 0.56305 | 0.55389 | 0.44861 | 0.57678 | 0.75073 | 0.47607 | 0.31586 | 7.0587 | 7.1365 | 7.0724 | 7.2464 | 7.1915 | 6.8024 | 6.7612 | 116.597 | 116.4368 | -6.4865 | 116.6748 | 116.6977 | 0.26093 | -6.6742 | 122.9233 | 122.8821 | 0.009155 | 123.1796 | 123.1934 | 0.31128 | -0.045777 | 116.8716 | 116.684 | 116.5695 | -6.9214 | 123.3673 | 123.3124 | 123.2574 | -0.47607
3192.5156 | 123.4589 | -116.1438 | 7.2235 | -0.1709 | 0.017799 | 0.0049945 | 0.015385 | -0.018912 | 0.0019078 | 0.00084388 | -0.16457 | 0.023225 | -0.0097904 | 0.010786 | -0.00229 | 0.010638 | 0.51727 | 0.55389 | 0.43488 | 0.56305 | 0.74616 | 0.4715 | 0.31128 | 7.0587 | 7.1548 | 7.0999 | 7.2235 | 7.164 | 6.7886 | 6.752 | 116.6153 | 116.4551 | -6.4774 | 116.6977 | 116.7068 | 0.25177 | -6.7062 | 122.9324 | 122.8958 | 0 | 123.2025 | 123.2437 | 0.3479 | -0.05951 | 116.89 | 116.6611 | 116.5787 | -6.9122 | 123.3673 | 123.3078 | 123.2986 | -0.4715
3193.5156 | 123.4451 | -116.1667 | 7.2006 | 0.13428 | 0.02079 | 0.0015765 | 0.01389 | -0.021475 | 0.004044 | 0.0029801 | 0.01091 | 0.023439 | -0.0089358 | 0.0086496 | -0.00058103 | 0.0089295 | 0.58136 | 0.60425 | 0.48523 | 0.60425 | 0.78278 | 0.53101 | 0.36621 | 7.0587 | 7.1045 | 7.0633 | 7.196 | 7.1457 | 6.7703 | 6.7337 | 116.6977 | 116.5329 | -6.4178 | 116.7709 | 116.7709 | 0.23804 | -6.6193 | 122.937 | 122.9004 | -0.004578 | 123.2254 | 123.23 | 0.32959 | -0.054932 | 116.9495 | 116.748 | 116.6519 | -6.8344 | 123.3627 | 123.3124 | 123.2712 | -0.46692
3194.5156 | 123.4497 | -116.1987 | 7.1594 | -0.18616 | 0.018226 | 0.0013629 | 0.01154 | -0.021689 | 0.00019875 | -0.00043792 | -0.11879 | 0.023225 | -0.0087222 | 0.0092904 | -0.0029308 | 0.0093567 | 0.5127 | 0.56305 | 0.44861 | 0.56763 | 0.74616 | 0.48523 | 0.3067 | 6.9809 | 7.0862 | 7.0267 | 7.1411 | 7.1274 | 6.7154 | 6.6925 | 116.684 | 116.5054 | -6.4133 | 116.7618 | 116.7664 | 0.26093 | -6.6467 | 122.9141 | 122.8912 | -0.018311 | 123.1796 | 123.2254 | 0.33417 | -0.032044 | 116.9449 | 116.7114 | 116.6473 | -6.8527 | 123.3398 | 123.3261 | 123.2849 | -0.46692
3195.5156 | 123.4039 | -116.1667 | 7.1823 | -0.12512 | 0.020576 | 0.0024311 | 0.017308 | -0.016562 | 0.0036166 | 0.00041648 | -0.057755 | 0.023011 | -0.0097904 | 0.012708 | -0.0016492 | 0.0089295 | 0.56305 | 0.59052 | 0.48981 | 0.5722 | 0.75531 | 0.49896 | 0.32501 | 6.9809 | 7.0587 | 7.0084 | 7.1228 | 7.0816 | 6.7017 | 6.665 | 116.6656 | 116.4917 | -6.427 | 116.7572 | 116.7389 | 0.24719 | -6.6193 | 122.8683 | 122.8317 | -0.059509 | 123.1476 | 123.175 | 0.34332 | -0.10071 | 116.922 | 116.7297 | 116.6565 | -6.8573 | 123.2895 | 123.2483 | 123.2254 | -0.51727
3196.5156 | 123.4131 | -116.272 | 7.132 | -0.23193 | 0.015236 | 0.0043537 | 0.015385 | -0.016776 | -0.0025784 | -0.00086512 | 1.1172 | 0.023225 | -0.010431 | 0.010786 | -0.0042126 | 0.0093567 | 0.49439 | 0.54016 | 0.43945 | 0.55389 | 0.76446 | 0.48065 | 0.3067 | 6.9077 | 7.0038 | 6.9351 | 7.1274 | 7.0862 | 6.6742 | 6.6467 | 116.7526 | 116.5787 | -6.3675 | 116.8121 | 116.8259 | 0.24719 | -6.6376 | 122.9462 | 122.9187 | -0.004578 | 123.1796 | 123.2071 | 0.28839 | -0.045776 | 117.0364 | 116.7664 | 116.7114 | -6.8253 | 123.3994 | 123.3582 | 123.2758 | -0.48523
3197.5156 | 123.4863 | -116.2857 | 7.0862 | -0.094604 | 0.019508 | 0.0030719 | 0.015385 | -0.020407 | 0.0014804 | 0.0023391 | -0.019608 | 0.023439 | -0.0074404 | 0.011213 | -0.0042126 | 0.0061523 | 0.56763 | 0.6134 | 0.47607 | 0.58136 | 0.74616 | 0.48981 | 0.32501 | 6.9122 | 7.0312 | 6.9626 | 7.1136 | 7.0816 | 6.6879 | 6.6238 | 116.7755 | 116.6107 | -6.34 | 116.8991 | 116.8671 | 0.25635 | -6.5186 | 122.9736 | 122.9095 | 0.027465 | 123.1979 | 123.2483 | 0.33874 | -0.004578 | 117.0319 | 116.8533 | 116.7618 | -6.7612 | 123.3994 | 123.3673 | 123.317 | -0.46234
3198.5156 | 123.4314 | -116.3269 | 7.045 | -0.20905 | 0.018654 | 0.0058491 | 0.014958 | -0.01998 | -0.0017238 | -0.00065152 | -0.17983 | 0.021302 | -0.011286 | 0.010999 | -0.0031446 | 0.0099975 | 0.56305 | 0.52643 | 0.4303 | 0.56305 | 0.80566 | 0.51727 | 0.35248 | 6.8665 | 6.9397 | 6.9031 | 7.0679 | 7.0175 | 6.633 | 6.6055 | 116.8442 | 116.6794 | -6.2393 | 116.8533 | 116.89 | 0.21057 | -6.4819 | 122.9599 | 122.9324 | 0.022888 | 123.1934 | 123.23 | 0.29755 | -0.027466 | 117.1326 | 116.89 | 116.7572 | -6.6925 | 123.3948 | 123.3444 | 123.2666 | -0.43945
3199.5156 | 123.4634 | -116.3544 | 7.0404 | -0.12512 | 0.020576 | 0.0013629 | 0.013035 | -0.01763 | 0.0019078 | 0.00063028 | -0.14931 | 0.023225 | -0.012354 | 0.0097176 | -0.0029308 | 0.0059387 | 0.53558 | 0.57678 | 0.45776 | 0.56763 | 0.75531 | 0.47607 | 0.30212 | 6.8665 | 6.9672 | 6.8985 | 7.0084 | 6.9946 | 6.6101 | 6.5689 | 116.8304 | 116.6565 | -6.2851 | 116.9312 | 116.922 | 0.2655 | -6.5048 | 122.9645 | 122.9233 | -0.032043 | 123.2208 | 123.2529 | 0.32959 | -0.045776 | 117.1097 | 116.89 | 116.8121 | -6.7383 | 123.3627 | 123.349 | 123.3215 | -0.4715
3200.5156 | 123.4131 | -116.391 | 7.0175 | -0.354 | 0.015449 | 0.0045673 | 0.015812 | -0.020621 | -0.001083 | 0.0014847 | -0.16457 | 0.022798 | -0.011499 | 0.010359 | -0.0027172 | 0.010852 | 0.48523 | 0.55847 | 0.44861 | 0.54932 | 0.76446 | 0.47607 | 0.29755 | 6.7978 | 6.8893 | 6.8527 | 7.0129 | 6.958 | 6.5872 | 6.546 | 116.8671 | 116.6885 | -6.2531 | 116.9495 | 116.9403 | 0.25177 | -6.5323 | 122.9782 | 122.937 | -0.004578 | 123.1888 | 123.2437 | 0.3067 | -0.059509 | 117.1555 | 116.8762 | 116.8396 | -6.72 | 123.4039 | 123.349 | 123.2803 | -0.4715
3201.5156 | 123.4451 | -116.4093 | 6.9717 | -0.11749 | 0.019935 | 0.0013629 | 0.015599 | -0.021903 | 0.00083955 | -1.0724e-05 | -0.050125 | 0.023439 | -0.0085086 | 0.0092904 | -0.0018628 | 0.0080749 | 0.54474 | 0.58594 | 0.46692 | 0.59052 | 0.75531 | 0.49439 | 0.32959 | 6.8298 | 6.9031 | 6.8527 | 6.9809 | 6.9168 | 6.5598 | 6.5369 | 116.9037 | 116.7389 | -6.2164 | 116.9952 | 116.9998 | 0.26093 | -6.427 | 122.9691 | 122.9462 | 0.009155 | 123.2391 | 123.262 | 0.31586 | -0.054932 | 117.1646 | 116.954 | 116.8762 | -6.6422 | 123.3902 | 123.3261 | 123.3124 | -0.43488
3202.5156 | 123.5321 | -116.3864 | 6.9397 | 0.22583 | 0.013313 | 0.0030719 | 0.012394 | -0.01998 | -0.0055692 | -0.0021469 | -0.065384 | 0.022798 | -0.011713 | 0.010572 | -0.0048534 | 0.010211 | 0.59967 | 0.69122 | 0.56763 | 0.63629 | 0.71869 | 0.51727 | 0.35706 | 6.8573 | 6.9763 | 6.9122 | 6.9122 | 6.9031 | 6.5689 | 6.5186 | 116.9037 | 116.7435 | -6.221 | 117.0776 | 117.0227 | 0.27924 | -6.34 | 122.9553 | 122.905 | -0.027466 | 123.2437 | 123.2986 | 0.39368 | -0.036621 | 117.1051 | 116.9861 | 116.954 | -6.5826 | 123.2986 | 123.2895 | 123.3627 | -0.42114
3203.5156 | 123.4543 | -116.4597 | 6.9214 | -0.10986 | 0.017158 | 0.0030719 | 0.015812 | -0.019553 | 0.0021214 | 0.0012711 | -0.18745 | 0.02472 | -0.011072 | 0.010786 | -0.00058103 | 0.0059387 | 0.5127 | 0.53558 | 0.44403 | 0.55847 | 0.737 | 0.48065 | 0.29297 | 6.7566 | 6.8436 | 6.7841 | 6.9443 | 6.8848 | 6.5094 | 6.4728 | 116.9403 | 116.7526 | -6.1844 | 116.9952 | 117.0181 | 0.2655 | -6.4087 | 122.9691 | 122.9324 | 0.022888 | 123.2162 | 123.2437 | 0.31128 | -0.036621 | 117.1967 | 116.9724 | 116.9037 | -6.6284 | 123.4039 | 123.3444 | 123.3032 | -0.44861
3204.5156 | 123.4131 | -116.4505 | 6.926 | -0.20142 | 0.01374 | 0.0034991 | 0.013676 | -0.01763 | -0.0032192 | -0.00086512 | -0.11879 | 0.021516 | -0.011713 | 0.009504 | -0.003999 | 0.010638 | 0.55389 | 0.62256 | 0.48523 | 0.59509 | 0.737 | 0.48981 | 0.34332 | 6.7337 | 6.8344 | 6.7841 | 6.926 | 6.8665 | 6.514 | 6.4636 | 116.9403 | 116.7938 | -6.189 | 117.0731 | 117.0456 | 0.25177 | -6.3721 | 122.9645 | 122.9141 | 0 | 123.1842 | 123.2346 | 0.32043 | -0.059509 | 117.1875 | 117.0044 | 116.9357 | -6.5826 | 123.3765 | 123.317 | 123.2849 | -0.46234
3205.5156 | 123.3902 | -116.478 | 6.9305 | -0.28534 | 0.013313 | 0.0030719 | 0.012608 | -0.01763 | -0.0017238 | -0.00086512 | -0.12642 | 0.023866 | -0.012567 | 0.010572 | -0.0048534 | 0.0046569 | 0.49439 | 0.56305 | 0.4303 | 0.53101 | 0.74616 | 0.4715 | 0.31586 | 6.7886 | 7.0358 | 6.6467 | 6.9489 | 6.9031 | 6.4774 | 6.4316 | 116.9495 | 116.7938 | -6.1844 | 117.041 | 117.009 | 0.21515 | -6.4362 | 122.9553 | 122.9095 | 0.018311 | 123.2666 | 123.1247 | 0.21515 | -0.027466 | 117.2241 | 116.9724 | 116.9083 | -6.6147 | 123.4268 | 123.381 | 123.5138 | -0.49896
3206.5156 | 123.5046 | -116.478 | 6.8436 | -0.1709 | 0.012459 | 0.0030719 | 0.012608 | -0.01998 | -0.001083 | -0.0015061 | -0.14931 | 0.020021 | -0.011072 | 0.010786 | -0.0037854 | 0.0087157 | 0.59052 | 0.69122 | 0.55389 | 0.62714 | 0.72327 | 0.50354 | 0.34332 | 6.7337 | 6.8344 | 6.7932 | 6.8298 | 6.7886 | 6.4728 | 6.4224 | 116.9815 | 116.8213 | -6.1203 | 117.1692 | 117.1051 | 0.28381 | -6.2531 | 122.9507 | 122.9004 | -0.013733 | 123.2117 | 123.2712 | 0.37079 | -0.054932 | 117.2012 | 117.0685 | 117.0319 | -6.5002 | 123.3078 | 123.2666 | 123.3124 | -0.42114
3207.5156 | 123.3948 | -116.5466 | 6.8161 | -0.23193 | 0.015022 | 0.0041401 | 0.013249 | -0.021262 | 0.00041235 | -0.00043792 | -0.42397 | 0.020875 | -0.011499 | 0.010145 | -0.0033582 | 0.0091431 | 0.50812 | 0.54932 | 0.43945 | 0.72784 | 0.7782 | 0.48981 | 0.31128 | 6.6513 | 6.6788 | 6.665 | 6.8527 | 6.7886 | 6.4316 | 6.3721 | 117.0364 | 116.8579 | -6.0379 | 117.0959 | 117.2745 | 0.41657 | -6.308 | 122.9782 | 122.9187 | 0.036621 | 123.1979 | 123.2117 | 0.29297 | -0.027466 | 117.3248 | 117.0547 | 116.9861 | -6.5048 | 123.3994 | 123.3353 | 123.2254 | -0.44403
3208.5156 | 123.4634 | -116.5741 | 6.7886 | -0.16327 | 0.015877 | 0.0058491 | 0.013035 | -0.01998 | -0.001083 | -0.0010787 | -0.13405 | 0.020448 | -0.011499 | 0.010572 | -0.0042126 | 0.0095703 | 0.5722 | 0.6546 | 0.53558 | 0.60883 | 0.72327 | 0.49896 | 0.35706 | 6.6742 | 6.7429 | 6.7062 | 6.7795 | 6.7383 | 6.4178 | 6.3675 | 117.0731 | 116.9312 | -6.0654 | 117.2287 | 117.1829 | 0.25177 | -6.2164 | 122.9919 | 122.9416 | -0.009155 | 123.2483 | 123.2803 | 0.33875 | -0.050354 | 117.2974 | 117.1463 | 117.1097 | -6.4316 | 123.3536 | 123.3124 | 123.317 | -0.42114
3209.5156 | 123.4177 | -116.597 | 6.7795 | -0.18616 | 0.014595 | 0.0056353 | 0.015385 | -0.018485 | -0.001083 | -0.00043792 | -0.11879 | 0.022584 | -0.0087222 | 0.0099314 | -0.0035718 | 0.0095703 | 0.50812 | 0.59509 | 0.45319 | 0.55847 | 0.75989 | 0.47607 | 0.29755 | 6.5918 | 6.6742 | 6.6284 | 6.7841 | 6.7429 | 6.3721 | 6.3263 | 117.0731 | 116.8945 | -6.0196 | 117.1921 | 117.1555 | 0.26093 | -6.2714 | 122.9691 | 122.9233 | 0.004578 | 123.1888 | 123.2254 | 0.30212 | -0.036621 | 117.3569 | 117.1051 | 117.0502 | -6.4819 | 123.381 | 123.3398 | 123.2712 | -0.45319
3210.5156 | 123.5504 | -116.6061 | 6.7383 | -0.12512 | 0.011818 | 0.0047809 | 0.013463 | -0.018271 | -0.0032192 | -0.0021469 | -2.7433 | 0.021089 | -0.0078678 | 0.010999 | -0.0046398 | 0.0089295 | 0.59509 | 0.737 | 0.58594 | 0.64545 | 0.70953 | 0.51727 | 0.33875 | 6.6833 | 6.6605 | 6.7383 | 6.7017 | 6.633 | 6.3766 | 6.3309 | 117.1234 | 116.9449 | -6.0287 | 117.3431 | 117.2516 | 0.3067 | -6.1432 | 122.9828 | 122.937 | -0.036621 | 123.2895 | 123.3444 | 0.40741 | -0.10528 | 117.3157 | 117.2012 | 117.1921 | -6.3995 | 123.3078 | 123.2391 | 123.2666 | -0.40741
3211.5156 | 123.4085 | -116.6519 | 6.7429 | -0.13275 | 0.015663 | 0.0041401 | 0.015812 | -0.018912 | 0.0012668 | -0.00065152 | -0.17983 | 0.021516 | -0.0095768 | 0.0099314 | -0.0018628 | 0.0085021 | 0.5127 | 0.5722 | 0.43488 | 0.52643 | 0.74158 | 0.46234 | 0.28839 | 6.4819 | 6.5872 | 6.5826 | 6.8024 | 6.7062 | 6.3354 | 6.2897 | 117.1143 | 116.9403 | -6.0013 | 117.2241 | 117.1783 | 0.23804 | -6.2302 | 122.9874 | 122.9416 | 0.059509 | 123.1339 | 123.2346 | 0.29297 | -0.036621 | 117.3935 | 117.1646 | 117.0868 | -6.4545 | 123.4543 | 123.3582 | 123.2391 | -0.45319
3212.5156 | 123.5367 | -116.6107 | 6.7017 | -1.8265 | 0.0077587 | 0.00072209 | 0.007481 | -0.019553 | -0.002792 | -1.0724e-05 | -0.027237 | 0.021302 | -0.011927 | 0.0092904 | -0.0029308 | 0.0080749 | 0.58594 | 0.67749 | 0.5722 | 0.62256 | 0.70496 | 0.50354 | 0.32959 | 6.6376 | 6.7337 | 6.6788 | 6.6696 | 6.6238 | 6.3354 | 6.2988 | 117.1143 | 116.9403 | -5.9967 | 117.2882 | 117.2333 | 0.29297 | -6.1157 | 122.9462 | 122.9095 | -0.032043 | 123.2483 | 123.2895 | 0.37994 | -0.07782 | 117.3157 | 117.1967 | 117.1829 | -6.3721 | 123.2803 | 123.2346 | 123.3444 | -0.40283
3213.5156 | 123.4177 | -116.684 | 6.6833 | -0.19379 | 0.014381 | 0.0032855 | 0.01389 | -0.018271 | -0.00044225 | -0.00043792 | -0.12642 | 0.02173 | -0.010004 | 0.010145 | -0.0012218 | 0.011066 | 0.55847 | 0.62256 | 0.49896 | 0.58136 | 0.74616 | 0.49896 | 0.32044 | 6.5231 | 6.6193 | 6.5277 | 6.6788 | 6.6513 | 6.2988 | 6.2576 | 117.1829 | 117.0044 | -5.9372 | 117.3065 | 117.2653 | 0.26092 | -6.1249 | 122.9828 | 122.9416 | -0.004578 | 123.2071 | 123.2117 | 0.27008 | -0.032044 | 117.4301 | 117.2424 | 117.1829 | -6.3629 | 123.3627 | 123.3353 | 123.3032 | -0.42572
3214.5156 | 123.4085 | -116.7068 | 6.6696 | -0.14038 | 0.015022 | 0.0037127 | 0.014103 | -0.018271 | 0.0014804 | 0.0014847 | -0.24086 | 0.023866 | -0.010431 | 0.010999 | -0.0014356 | 0.0076477 | 0.50354 | 0.54016 | 0.42572 | 0.53558 | 0.76446 | 0.45776 | 0.28381 | 6.4911 | 6.5735 | 6.4911 | 6.6925 | 6.6284 | 6.2759 | 6.221 | 117.1646 | 116.9907 | -5.9052 | 117.247 | 117.2424 | 0.25177 | -6.1661 | 122.9828 | 122.9279 | 0.022888 | 123.1979 | 123.1979 | 0.27008 | -0.041199 | 117.4713 | 117.2104 | 117.1326 | -6.3858 | 123.3994 | 123.3353 | 123.2803 | -0.44861
3215.5156 | 123.3444 | -116.6611 | 6.7108 | -0.20142 | 0.017372 | 0.0043537 | 0.015172 | -0.019339 | -0.0015102 | 0.0012711 | -0.1722 | 0.022157 | -0.011072 | 0.012495 | -0.0020764 | 0.010211 | 0.50354 | 0.58136 | 0.45776 | 0.53558 | 0.74158 | 0.46234 | 0.31128 | 6.4545 | 6.5414 | 6.4911 | 6.6696 | 6.5826 | 6.2622 | 6.2119 | 117.1234 | 116.9724 | -5.9692 | 117.2424 | 117.1967 | 0.2243 | -6.2073 | 122.9233 | 122.8729 | -0.041198 | 123.1155 | 123.1522 | 0.27924 | -0.12817 | 117.4026 | 117.1646 | 117.1188 | -6.3995 | 123.3307 | 123.2437 | 123.2025 | -0.49896
3216.5156 | 123.555 | -116.6931 | 6.5872 | -0.041199 | 0.01139 | 0.0024311 | 0.012394 | -0.021262 | -0.0036464 | -0.0010787 | 0.049057 | 0.019807 | -0.010858 | 0.0097176 | -0.0025036 | 0.010211 | 0.56305 | 0.67291 | 0.56305 | 0.6134 | 0.73242 | 0.52185 | 0.35706 | 6.5598 | 6.6422 | 6.5918 | 6.6101 | 6.5231 | 6.2668 | 6.2302 | 117.215 | 117.0502 | -5.8548 | 117.366 | 117.3065 | 0.25635 | -6.0242 | 122.9599 | 122.9233 | 0.022888 | 123.2529 | 123.2849 | 0.36163 | -0.064087 | 117.4255 | 117.2562 | 117.2562 | -6.2302 | 123.3032 | 123.2162 | 123.3353 | -0.35705
3217.5156 | 123.5092 | -116.7252 | 6.5872 | -0.056458 | 0.012031 | 0.0054217 | 0.013249 | -0.01763 | -0.00022865 | -0.00086512 | -0.12642 | 0.020662 | -0.010431 | 0.0099314 | -0.0027172 | 0.0076477 | 0.59509 | 0.70038 | 0.54932 | 0.63171 | 0.72327 | 0.49896 | 0.3479 | 6.5186 | 6.6193 | 6.5369 | 6.5552 | 6.5231 | 6.2302 | 6.189 | 117.2241 | 117.0731 | -5.864 | 117.4255 | 117.3569 | 0.28381 | -5.9921 | 122.9553 | 122.9141 | -0.032043 | 123.2437 | 123.262 | 0.3479 | -0.064087 | 117.4484 | 117.3203 | 117.2745 | -6.2393 | 123.2803 | 123.2483 | 123.3444 | -0.39825
3218.5156 | 123.555 | -116.7572 | 6.5231 | -0.10223 | 0.010322 | 0.0032855 | 0.010258 | -0.017844 | -0.0036464 | -0.0012923 | 0.0032804 | 0.023652 | -0.011927 | 0.0092904 | -0.0027172 | 0.0085021 | 0.59509 | 0.6958 | 0.57678 | 0.61798 | 0.72327 | 0.52643 | 0.36163 | 6.5414 | 6.5964 | 6.546 | 6.5506 | 6.4728 | 6.2302 | 6.1707 | 117.2836 | 117.1188 | -5.7999 | 117.453 | 117.3752 | 0.25635 | -5.928 | 122.9874 | 122.9279 | 0.027466 | 123.2986 | 123.3032 | 0.37537 | -0.050354 | 117.4805 | 117.3523 | 117.334 | -6.1615 | 123.3078 | 123.23 | 123.3536 | -0.35248
3219.5156 | 123.4314 | -116.8121 | 6.514 | 0.17242 | 0.021858 | 8.1086e-05 | 0.017521 | -0.020194 | 0.0063938 | 0.0042619 | -0.11879 | 0.023225 | -0.0085086 | 0.010145 | -0.00058103 | 0.0070067 | 0.59509 | 0.60883 | 0.46234 | 0.54932 | 0.75073 | 0.46692 | 0.30212 | 6.4178 | 6.4453 | 6.3766 | 6.5323 | 6.4728 | 6.1661 | 6.1111 | 117.2791 | 117.1143 | -5.7632 | 117.421 | 117.3615 | 0.24719 | -5.9189 | 122.9782 | 122.9233 | 0.018311 | 123.23 | 123.1888 | 0.2655 | -0.041199 | 117.5629 | 117.4072 | 117.2745 | -6.2119 | 123.3444 | 123.2849 | 123.2574 | -0.40283
3220.5156 | 123.5229 | -116.803 | 6.5094 | -0.0030518 | 0.012245 | 0.0058491 | 0.012181 | -0.016135 | -0.0038602 | 0.00041648 | -0.034867 | 0.02173 | -0.012995 | 0.010359 | -0.0050672 | 0.010425 | 0.55389 | 0.65002 | 0.54474 | 0.60883 | 0.73242 | 0.51727 | 0.35706 | 6.4682 | 6.5323 | 6.4819 | 6.4865 | 6.4545 | 6.1661 | 6.1295 | 117.3203 | 117.16 | -5.777 | 117.453 | 117.4118 | 0.25177 | -5.9555 | 122.9691 | 122.9324 | -0.022888 | 123.2712 | 123.2849 | 0.35248 | -0.054931 | 117.5354 | 117.3569 | 117.3477 | -6.1523 | 123.2895 | 123.2574 | 123.3353 | -0.37994
3221.5156 | 123.4818 | -116.8579 | 6.4819 | -0.16327 | 0.015663 | 0.0067035 | 0.0094038 | -0.020194 | 0.00019875 | 0.0010575 | -0.18745 | 0.022157 | -0.01214 | 0.011213 | -0.0025036 | 0.0085021 | 0.56763 | 0.66834 | 0.53558 | 0.59052 | 0.6958 | 0.48523 | 0.32501 | 6.3721 | 6.4682 | 6.395 | 6.4819 | 6.395 | 6.1386 | 6.0745 | 117.3431 | 117.1829 | -5.7861 | 117.5262 | 117.4484 | 0.2655 | -5.9143 | 122.9965 | 122.9324 | 0 | 123.23 | 123.2529 | 0.32043 | -0.086976 | 117.5537 | 117.4255 | 117.3935 | -6.1569 | 123.3398 | 123.2529 | 123.3261 | -0.40741
3222.5156 | 123.5596 | -116.8396 | 6.4636 | -0.02594 | 0.010963 | 0.0054217 | 0.010899 | -0.021475 | -0.0017238 | -0.00043792 | 0.064316 | 0.020662 | -0.011072 | 0.011213 | -0.0018628 | 0.0085021 | 0.58594 | 0.69122 | 0.55847 | 0.59509 | 0.71411 | 0.50812 | 0.32959 | 6.4316 | 6.4819 | 6.4407 | 6.4545 | 6.3766 | 6.1157 | 6.0791 | 117.3477 | 117.1692 | -5.7495 | 117.5308 | 117.4347 | 0.2655 | -5.8777 | 122.9553 | 122.9187 | -0.009155 | 123.2712 | 123.2803 | 0.36163 | -0.086975 | 117.5537 | 117.4255 | 117.3981 | -6.134 | 123.2941 | 123.2162 | 123.3215 | -0.38452
3223.5156 | 123.5321 | -116.89 | 6.4178 | -0.086975 | 0.013527 | 0.0024311 | 0.013249 | -0.019126 | -0.0021512 | -0.00043792 | -0.12642 | 0.021302 | -0.011072 | 0.010999 | -0.00036743 | 0.0076477 | 0.58136 | 0.68665 | 0.54932 | 0.6134 | 0.6958 | 0.50354 | 0.33417 | 6.3675 | 6.4728 | 6.3812 | 6.4316 | 6.3538 | 6.1066 | 6.0516 | 117.3935 | 117.2241 | -5.722 | 117.5766 | 117.5034 | 0.27924 | -5.8365 | 122.9965 | 122.9416 | 0.013733 | 123.2574 | 123.2712 | 0.32959 | -0.064087 | 117.5858 | 117.4713 | 117.4393 | -6.0837 | 123.3215 | 123.2437 | 123.3627 | -0.36621
3224.5156 | 123.436 | -116.9678 | 6.4041 | -0.13275 | 0.021004 | 0.0032855 | 0.016667 | -0.019126 | 0.004044 | 0.0019119 | -0.21034 | 0.024934 | -0.008295 | 0.01164 | -0.0027172 | 0.0042297 | 0.51727 | 0.54932 | 0.42572 | 0.54016 | 0.72784 | 0.46234 | 0.29755 | 6.2805 | 6.3446 | 6.2668 | 6.4087 | 6.3446 | 6.0287 | 5.9875 | 117.4301 | 117.2653 | -5.6763 | 117.5171 | 117.5079 | 0.24262 | -5.8868 | 122.9965 | 122.9553 | 0.004577 | 123.2483 | 123.2346 | 0.27924 | -0.05951 | 117.6956 | 117.485 | 117.3935 | -6.1066 | 123.3765 | 123.3124 | 123.3124 | -0.41657
3225.5156 | 123.5367 | -116.954 | 6.3858 | -0.17853 | 0.01075 | 0.0052081 | 0.012822 | -0.018271 | -0.0021512 | -0.00022432 | 0.033798 | 0.021302 | -0.011713 | 0.010786 | -0.0020764 | 0.0091431 | 0.28381 | 0.89264 | 0.6134 | 0.48065 | 0.68207 | 0.48523 | 0.31586 | 6.3354 | 6.4133 | 6.3492 | 6.3629 | 6.2988 | 6.0562 | 5.9967 | 117.4393 | 117.2699 | -5.7037 | 117.8467 | 117.4347 | 0.1648 | -6.102 | 123.0103 | 122.9507 | -0.022888 | 123.2895 | 123.3032 | 0.35248 | -0.086975 | 117.6361 | 117.2379 | 117.5674 | -6.0699 | 123.317 | 123.2529 | 123.3673 | -0.3891
3226.5156 | 123.5184 | -116.9495 | 6.3629 | 0.09613 | 0.012459 | 0.0041401 | 0.013035 | -0.019553 | -0.002792 | -0.00065152 | 0.079574 | 0.019807 | -0.013636 | 0.0097176 | -0.0033582 | 0.010425 | 0.50812 | 0.62256 | 0.49439 | 0.56305 | 0.70953 | 0.48065 | 0.31586 | 6.2851 | 6.3354 | 6.308 | 6.3538 | 6.2988 | 6.0242 | 5.983 | 117.4301 | 117.2653 | -5.6534 | 117.572 | 117.5125 | 0.24719 | -5.8548 | 122.9736 | 122.9324 | -0.009155 | 123.2346 | 123.2574 | 0.32501 | -0.064087 | 117.659 | 117.4576 | 117.4438 | -6.0471 | 123.3032 | 123.2483 | 123.2849 | -0.37994
3227.5156 | 123.6465 | -116.9861 | 6.3217 | -0.048828 | 0.012459 | 0.0034991 | 0.010899 | -0.021475 | -0.0042874 | 0.0019119 | -0.057755 | 0.021516 | -0.011499 | 0.0097176 | -0.003999 | 0.0061523 | 0.59967 | 0.69122 | 0.55847 | 0.62256 | 0.6958 | 0.5127 | 0.3479 | 6.3354 | 6.3995 | 6.3354 | 6.3446 | 6.2714 | 6.0379 | 5.9647 | 117.4988 | 117.334 | -5.6259 | 117.6773 | 117.6086 | 0.27466 | -5.722 | 123.024 | 122.9507 | 0.022888 | 123.3215 | 123.3215 | 0.37079 | -0.050354 | 117.6819 | 117.5858 | 117.5446 | -5.9738 | 123.3307 | 123.2574 | 123.3856 | -0.35705
3228.5156 | 123.4955 | -116.9998 | 6.3309 | 0.12665 | 0.011604 | 0.0024311 | 0.01389 | -0.020407 | -0.0015102 | 0.00020288 | 0.064316 | 0.019593 | -0.012995 | 0.0097176 | -0.0042126 | 0.0093567 | 0.53558 | 0.60883 | 0.48523 | 0.38452 | 0.67291 | 0.4715 | 0.29755 | 6.2073 | 6.2439 | 6.2622 | 6.2851 | 6.2622 | 5.9692 | 5.9189 | 117.4713 | 117.2974 | -5.658 | 117.6086 | 117.3843 | 0.086975 | -5.7953 | 122.9691 | 122.9187 | -0.045777 | 123.2071 | 123.262 | 0.34332 | -0.068665 | 117.6727 | 117.5354 | 117.485 | -6.0333 | 123.2849 | 123.262 | 123.2437 | -0.41199
3229.5156 | 123.4222 | -117.0547 | 6.2897 | 0.0045777 | 0.017372 | 0.0041401 | 0.014531 | -0.018912 | 0.0083164 | 0.0021255 | -0.34004 | 0.025789 | -0.010004 | 0.011213 | 0.0019824 | 0.0074341 | 0.58136 | 0.57678 | 0.42572 | 0.55389 | 0.73242 | 0.48981 | 0.3067 | 6.1569 | 6.2119 | 6.1249 | 6.3034 | 6.2485 | 5.9647 | 5.9052 | 117.5446 | 117.3615 | -5.5573 | 117.6315 | 117.6086 | 0.24719 | -5.7083 | 123.0194 | 122.9599 | 0.013733 | 123.2117 | 123.1796 | 0.21973 | -0.041199 | 117.7872 | 117.6361 | 117.4805 | -5.983 | 123.3582 | 123.3032 | 123.2666 | -0.38452
3230.5156 | 123.5001 | -117.0593 | 6.2759 | 0.14954 | 0.01139 | 0.0041401 | 0.013463 | -0.023398 | -0.002792 | 0.0019119 | 0.20927 | 0.021943 | -0.01214 | 0.012708 | -0.0033582 | 0.0085021 | 0.56305 | 0.59052 | 0.48523 | 0.54932 | 0.70038 | 0.48523 | 0.33417 | 6.1752 | 6.2027 | 6.2073 | 6.2576 | 6.1981 | 5.9326 | 5.8914 | 117.5446 | 117.3935 | -5.5756 | 117.6498 | 117.6086 | 0.21515 | -5.7129 | 122.9919 | 122.9507 | -0.018311 | 123.2346 | 123.2666 | 0.31586 | -0.07782 | 117.7597 | 117.6224 | 117.5446 | -5.9418 | 123.317 | 123.2574 | 123.262 | -0.38452

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2 | Cable 3
-0.3865 | 20.601 | 20.4103 | 20.5567 | 20.2627
0.6135 | 20.6003 | 20.4007 | 20.5659 | 20.2581
1.6135 | 20.5955 | 20.4044 | 20.5499 | 20.2526
2.6135 | 20.6121 | 20.4075 | 20.5591 | 20.2547
3.6135 | 20.9366 | 20.4089 | 20.5581 | 20.2665
4.6135 | 21.973 | 20.4037 | 20.5584 | 20.2514
5.6135 | 23.7838 | 20.4134 | 20.5648 | 20.2618
6.6135 | 26.2999 | 20.419 | 20.5754 | 20.257
7.6135 | 29.369 | 20.4427 | 20.5761 | 20.2527
8.6135 | 32.8958 | 20.4506 | 20.583 | 20.2573
9.6135 | 36.8119 | 20.4676 | 20.6003 | 20.2596
10.6135 | 41.0297 | 20.4823 | 20.6149 | 20.2588
11.6135 | 45.4921 | 20.4976 | 20.6412 | 20.2613
12.6135 | 50.156 | 20.5156 | 20.6653 | 20.262
13.6135 | 54.9994 | 20.5444 | 20.7084 | 20.2508
14.6135 | 60.0175 | 20.5839 | 20.7455 | 20.2561
15.6135 | 65.1814 | 20.6208 | 20.7934 | 20.2598
16.6135 | 70.5006 | 20.6817 | 20.8324 | 20.2557
17.6135 | 75.9303 | 20.7497 | 20.8842 | 20.2679
18.6135 | 81.4576 | 20.8025 | 20.9582 | 20.2511
19.6135 | 87.1069 | 20.8791 | 20.9949 | 20.2544
20.6135 | 92.8394 | 20.9667 | 21.056 | 20.2502
21.6135 | 98.7003 | 21.0471 | 21.1262 | 20.2529
22.6135 | 104.6092 | 21.1449 | 21.1746 | 20.2549
23.6135 | 110.5266 | 21.2428 | 21.2631 | 20.252
24.6135 | 116.4932 | 21.3374 | 21.3468 | 20.2642
25.6135 | 122.4832 | 21.4273 | 21.3976 | 20.2524
26.6135 | 128.5491 | 21.533 | 21.4817 | 20.2542
27.6135 | 134.6005 | 21.6529 | 21.6192 | 20.2543
28.6135 | 140.6636 | 21.8042 | 21.6944 | 20.2672
29.6135 | 146.7016 | 21.9557 | 21.8446 | 20.2683
30.6135 | 152.7716 | 22.1668 | 22.041 | 20.2721
31.6135 | 158.8023 | 22.3009 | 22.1709 | 20.2694
32.6135 | 164.6734 | 22.4371 | 22.2244 | 20.2732
33.6135 | 170.7215 | 22.591 | 22.3322 | 20.2786
34.6135 | 176.7929 | 22.7534 | 22.5603 | 20.2673
35.6135 | 182.858 | 22.9497 | 22.6879 | 20.2741
36.6135 | 188.8913 | 23.1573 | 22.8708 | 20.2749
37.6135 | 194.9455 | 23.3748 | 23.1236 | 20.2701
38.6135 | 200.9653 | 23.5822 | 23.3431 | 20.2754
39.6135 | 206.9377 | 23.8047 | 23.6485 | 20.2751
40.6135 | 212.9256 | 24.0358 | 23.8811 | 20.2792
41.6135 | 218.96 | 24.2934 | 24.0697 | 20.2732
42.6135 | 224.9115 | 24.5984 | 24.1246 | 20.2832
43.6135 | 230.8275 | 24.8757 | 24.2813 | 20.2883
44.6135 | 236.7214 | 25.1246 | 24.5509 | 20.2908
45.6135 | 242.6439 | 25.4157 | 24.876 | 20.2903
46.6135 | 248.5367 | 25.7541 | 25.2523 | 20.2922
47.6135 | 254.4132 | 26.025 | 25.432 | 20.2933
48.6135 | 260.2671 | 26.4189 | 25.6416 | 20.2974
49.6135 | 266.1235 | 26.7637 | 25.9628 | 20.3035
50.6135 | 271.8706 | 27.0862 | 26.1841 | 20.2994
51.6135 | 277.5449 | 27.4724 | 26.4303 | 20.312
52.6135 | 283.3389 | 27.9089 | 26.734 | 20.3142
53.6135 | 289.0422 | 28.3032 | 27.174 | 20.3218
54.6135 | 294.8058 | 28.6514 | 27.6473 | 20.3224
55.6135 | 300.5837 | 29.0646 | 28.0216 | 20.3216
56.6135 | 306.2857 | 29.5056 | 28.441 | 20.3376
57.6135 | 311.9695 | 29.9188 | 28.8162 | 20.3347
58.6135 | 317.5558 | 30.4213 | 28.9971 | 20.3449
59.6135 | 323.0623 | 30.87 | 29.1961 | 20.3569
60.6135 | 328.6607 | 31.3712 | 29.521 | 20.3542
61.6135 | 334.3225 | 31.824 | 29.9034 | 20.3639
62.6135 | 339.8993 | 32.3966 | 30.5173 | 20.3772
63.6135 | 345.3281 | 32.9305 | 31.1928 | 20.3782
64.6135 | 350.8925 | 33.5465 | 31.5997 | 20.3838
65.6448 | 356.4442 | 34.6669 | 32.0053 | 20.3982
66.6135 | 361.6074 | 35.027 | 32.6246 | 20.4054
67.6135 | 366.9338 | 35.5806 | 33.2326 | 20.4176
68.6135 | 372.291 | 36.176 | 33.8996 | 20.4292
69.6135 | 377.6457 | 36.7835 | 34.1997 | 20.4364
70.6135 | 382.8973 | 37.3556 | 34.4728 | 20.4474
71.6135 | 388.1507 | 37.9435 | 34.822 | 20.469
72.6135 | 393.4001 | 38.6797 | 35.2951 | 20.4784
73.6135 | 398.6564 | 39.4349 | 35.7449 | 20.4949
74.6135 | 403.8091 | 40.2217 | 36.3621 | 20.5067
75.6135 | 408.8773 | 40.9852 | 37.0608 | 20.521
76.6135 | 414.0017 | 41.7269 | 37.8404 | 20.5402
77.6135 | 419.0568 | 42.5411 | 38.4218 | 20.5602
78.6135 | 424.0514 | 43.2903 | 39.2164 | 20.5732
79.6135 | 429.1208 | 44.2362 | 40.2574 | 20.5969
80.6135 | 434.1941 | 45.0958 | 41.1319 | 20.6162
81.6135 | 439.0728 | 45.9147 | 41.6483 | 20.6401
82.6135 | 443.9911 | 46.8374 | 42.1538 | 20.6523
83.6135 | 448.8984 | 47.7852 | 42.991 | 20.6817
84.6135 | 453.9065 | 48.7315 | 43.9214 | 20.712
85.6135 | 458.7598 | 49.6732 | 44.7134 | 20.7283
86.6135 | 463.4526 | 50.6095 | 45.492 | 20.7626
87.6135 | 468.2514 | 51.5891 | 46.5863 | 20.7975
88.6135 | 472.9506 | 52.6314 | 47.666 | 20.8309
89.6135 | 477.415 | 53.7435 | 48.1727 | 20.8577
90.6135 | 481.398 | 55.0656 | 48.71 | 20.8955
91.6135 | 484.9921 | 56.0456 | 49.3685 | 20.9314
92.6135 | 488.098 | 57.1882 | 50.275 | 20.9735
93.6135 | 491.0012 | 58.2248 | 51.1319 | 21.0237
94.6135 | 493.8244 | 59.1269 | 52.138 | 21.0601
95.6135 | 496.6904 | 60.2865 | 52.939 | 21.116
96.6135 | 499.4038 | 61.3411 | 54.1016 | 21.1558
97.6135 | 501.94 | 62.4099 | 54.9597 | 21.2168
98.6135 | 504.5161 | 63.4916 | 55.9421 | 21.2758
99.6135 | 507.1189 | 64.6004 | 57.0012 | 21.3338
100.6135 | 509.4403 | 65.6599 | 57.6743 | 21.3912
101.6135 | 511.4735 | 66.6588 | 58.4235 | 21.4614
102.6135 | 513.2575 | 67.8228 | 59.4519 | 21.5382
103.6135 | 514.7237 | 69.0002 | 60.3869 | 21.6075
104.6135 | 515.896 | 69.9889 | 61.6209 | 21.6829
105.6135 | 517.0502 | 70.9955 | 62.6224 | 21.7677
106.6135 | 517.9196 | 72.177 | 63.5293 | 21.857
107.6135 | 518.5001 | 73.2693 | 64.2653 | 21.9404
108.6135 | 519.1035 | 74.3472 | 65.0796 | 22.0424
109.6135 | 519.3537 | 75.415 | 65.9565 | 22.1336
110.6135 | 519.5943 | 76.4863 | 66.9469 | 22.2298
111.6135 | 519.7521 | 77.3946 | 67.9787 | 22.3311
112.6135 | 519.8587 | 78.4055 | 68.9413 | 22.4296
113.6135 | 519.8167 | 79.5293 | 69.5853 | 22.549
114.6135 | 519.8398 | 80.5824 | 70.3717 | 22.6655
115.6135 | 519.7802 | 81.7869 | 71.5034 | 22.789
116.6135 | 519.7866 | 82.823 | 72.5572 | 22.9023
117.6135 | 519.907 | 83.8065 | 73.4855 | 23.0308
118.6135 | 519.8578 | 84.7097 | 74.2606 | 23.1642
119.6135 | 519.844 | 85.8629 | 74.9897 | 23.2944
120.6135 | 519.8002 | 86.9641 | 75.8961 | 23.446
121.6135 | 519.8546 | 88.0509 | 76.7363 | 23.5852
122.6135 | 520.0229 | 89.0097 | 77.6346 | 23.7291
123.6135 | 520.1322 | 90.0834 | 78.4577 | 23.8817
124.6135 | 520.1766 | 91.0891 | 79.4138 | 24.0374
125.6135 | 520.3143 | 91.9909 | 80.4097 | 24.19
126.6135 | 520.5504 | 93.0587 | 81.2461 | 24.3495
127.6135 | 520.73 | 94.1124 | 82.0441 | 24.5049
128.6135 | 520.9665 | 95.1131 | 83.0088 | 24.6676
129.6135 | 521.2285 | 96.2566 | 83.8388 | 24.8502
130.6135 | 521.501 | 97.1917 | 84.6725 | 25.005
131.6135 | 521.6011 | 98.271 | 85.5232 | 25.188
132.6135 | 521.8647 | 99.2426 | 86.5376 | 25.3564
133.6135 | 522.158 | 100.2247 | 87.5828 | 25.5396
134.6135 | 522.3134 | 101.1024 | 88.3226 | 25.725
135.6135 | 522.439 | 102.1044 | 89.1247 | 25.8969
136.6135 | 522.5907 | 103.1501 | 90.0633 | 26.0904
137.6135 | 522.6813 | 104.1734 | 90.9191 | 26.2667
138.6135 | 522.7419 | 105.1819 | 91.8677 | 26.4617
139.6135 | 522.7628 | 106.2218 | 92.9331 | 26.6441
140.6135 | 522.9023 | 107.2564 | 93.571 | 26.8418
141.6135 | 522.9162 | 108.4309 | 94.3556 | 27.031
142.6135 | 522.9367 | 109.3713 | 95.3338 | 27.2344
143.6135 | 522.8551 | 110.3143 | 96.1677 | 27.4319
144.6135 | 523.0107 | 111.3428 | 96.9811 | 27.6229
145.6135 | 523.1432 | 112.2604 | 97.9845 | 27.8339
146.6135 | 523.158 | 113.163 | 98.9826 | 28.0249
147.6135 | 523.2611 | 114.0807 | 99.6341 | 28.2301
148.6135 | 523.4351 | 115.215 | 100.5096 | 28.4273
149.6135 | 523.6832 | 116.1908 | 101.5248 | 28.6297
150.6135 | 523.7486 | 117.2066 | 102.6574 | 28.8374
151.6135 | 523.7537 | 118.1207 | 103.4279 | 29.0248
152.6135 | 523.8272 | 119.1352 | 104.132 | 29.2255
153.6135 | 523.6816 | 120.082 | 105.074 | 29.4309
154.6135 | 523.7436 | 121.0666 | 105.9862 | 29.6361
155.6135 | 523.8539 | 121.9853 | 106.7057 | 29.8365
156.6135 | 524.0185 | 122.9997 | 107.4202 | 30.0426
157.6135 | 524.2472 | 124.0476 | 108.3834 | 30.2449
158.6135 | 524.3549 | 124.9998 | 109.39 | 30.4452
159.6135 | 524.5329 | 125.938 | 110.2102 | 30.6545
160.6135 | 524.4744 | 126.8771 | 111.0552 | 30.8451
161.6135 | 524.3184 | 127.8331 | 111.9677 | 31.0555
162.6135 | 524.4087 | 128.8622 | 112.884 | 31.2518
163.6135 | 524.5161 | 129.8068 | 113.7972 | 31.4516
164.6135 | 524.6272 | 130.7487 | 114.5572 | 31.6528
165.6135 | 524.8439 | 131.7402 | 115.3929 | 31.8555
166.6135 | 524.9138 | 132.6931 | 116.1843 | 32.0521
167.6135 | 525.024 | 133.6157 | 116.9888 | 32.2491
168.6135 | 524.9822 | 134.5218 | 117.7301 | 32.4547
169.6135 | 525.0643 | 135.4671 | 118.6022 | 32.6518
170.6135 | 525.1765 | 136.4107 | 119.5445 | 32.8492
171.6135 | 525.1411 | 137.371 | 120.6023 | 33.0443
172.6135 | 525.21 | 138.235 | 121.4391 | 33.2422
173.6135 | 525.1977 | 139.1475 | 122.1664 | 33.4342
174.6135 | 525.2521 | 140.0812 | 123.0247 | 33.6257
175.6135 | 525.2364 | 141.1068 | 123.905 | 33.8289
176.6135 | 525.2481 | 142.0247 | 124.7702 | 34.019
177.6135 | 525.277 | 143.0199 | 125.7601 | 34.2151
178.6135 | 525.2154 | 143.9095 | 126.5952 | 34.409
179.6135 | 525.0558 | 144.8724 | 127.3863 | 34.6
180.6135 | 524.9731 | 145.7404 | 128.0986 | 34.7872
181.6135 | 524.8906 | 146.6621 | 128.9433 | 34.9733
182.6135 | 524.7274 | 147.5673 | 129.8003 | 35.1689
183.6135 | 524.624 | 148.5941 | 130.7136 | 35.3519
184.6135 | 524.6445 | 149.5633 | 131.5344 | 35.5397
185.6135 | 524.574 | 150.457 | 132.4412 | 35.7266
186.6135 | 524.5382 | 151.2375 | 133.2204 | 35.9207
187.6135 | 524.4485 | 152.1087 | 134.0474 | 36.1136
188.6135 | 524.3837 | 152.954 | 134.8988 | 36.297
189.6135 | 524.4669 | 153.8795 | 135.78 | 36.4856
190.6135 | 524.5123 | 154.8142 | 136.5508 | 36.6744
191.6135 | 524.4738 | 155.6914 | 137.4353 | 36.8794
192.6135 | 524.4664 | 156.5866 | 138.295 | 37.0523
193.6135 | 524.4928 | 157.4954 | 139.0095 | 37.2504
194.6135 | 524.5445 | 158.3866 | 139.9081 | 37.4246
195.6135 | 524.7269 | 159.2294 | 140.6431 | 37.6131
196.6135 | 524.7814 | 160.0907 | 141.4616 | 37.7921
197.6135 | 524.6213 | 160.9564 | 142.3177 | 37.9744
198.6135 | 524.6914 | 161.8947 | 143.101 | 38.1495
199.6135 | 524.7154 | 162.789 | 143.9614 | 38.3195
200.6135 | 524.507 | 163.6399 | 144.8258 | 38.4984
201.6135 | 524.4278 | 164.5133 | 145.621 | 38.6627
202.6135 | 524.4038 | 165.3719 | 146.4302 | 38.8385
203.6135 | 524.4876 | 166.2593 | 147.1737 | 39.0151
204.6135 | 524.5118 | 167.1207 | 148.0119 | 39.1827
205.6135 | 524.558 | 167.9416 | 148.9377 | 39.3561
206.6135 | 524.5294 | 168.8431 | 149.7348 | 39.5297
207.6135 | 524.5773 | 169.7044 | 150.4798 | 39.7076
208.6135 | 524.5272 | 170.553 | 151.2306 | 39.8763
209.6135 | 524.3262 | 171.416 | 152.003 | 40.0466
210.6135 | 524.2085 | 172.272 | 152.7896 | 40.2226
211.6135 | 524.2035 | 173.0797 | 153.6246 | 40.3925
212.6135 | 524.2163 | 173.9482 | 154.4063 | 40.564
213.6135 | 524.4519 | 174.7858 | 155.1443 | 40.7419
214.6135 | 524.6006 | 175.679 | 155.9314 | 40.9076
215.6135 | 524.6675 | 176.5395 | 156.6652 | 41.0782
216.6135 | 524.6718 | 177.2963 | 157.3706 | 41.2356
217.6135 | 524.7349 | 178.1472 | 158.2065 | 41.3976
218.6135 | 524.779 | 178.9712 | 158.9935 | 41.562
219.6135 | 524.8679 | 179.7707 | 159.8323 | 41.7128
220.6135 | 524.8485 | 180.5545 | 160.6187 | 41.8699
221.6135 | 524.8927 | 181.3556 | 161.3593 | 42.0194
222.6135 | 524.9101 | 182.2268 | 162.1565 | 42.1648
223.6135 | 525.1247 | 183.0895 | 162.9007 | 42.31
224.6135 | 525.2859 | 183.9417 | 163.6671 | 42.4457
225.6135 | 525.3252 | 184.8064 | 164.3933 | 42.5811
226.6135 | 525.3787 | 185.6058 | 165.2262 | 42.7139
227.6135 | 525.447 | 186.3498 | 165.9817 | 42.8521
228.6135 | 525.4982 | 187.1596 | 166.7024 | 42.975
229.6135 | 525.2817 | 188.0537 | 167.5044 | 43.1012
230.6135 | 525.1496 | 188.8057 | 168.2167 | 43.2333
231.6135 | 525.1125 | 189.6424 | 168.9256 | 43.348
232.6135 | 525.038 | 190.4808 | 169.717 | 43.4826
233.6135 | 524.9129 | 191.2428 | 170.4857 | 43.6055
234.6135 | 524.9453 | 192.0463 | 171.2351 | 43.7276
235.6135 | 524.9138 | 192.7811 | 172.0008 | 43.8544
236.6135 | 524.8399 | 193.5846 | 172.73 | 43.9747
237.6135 | 524.7545 | 194.3782 | 173.4782 | 44.1043
238.6135 | 524.6191 | 195.1615 | 174.2199 | 44.2309
239.6135 | 524.6621 | 195.9845 | 174.9554 | 44.3631
240.6135 | 524.6481 | 196.7902 | 175.7089 | 44.4818
241.6135 | 524.4874 | 197.5241 | 176.4156 | 44.6178
242.6135 | 524.3023 | 198.3138 | 177.1041 | 44.748
243.6135 | 524.2476 | 199.0777 | 177.826 | 44.8814
244.6135 | 524.2407 | 199.8868 | 178.5309 | 45.0132
245.6135 | 524.2023 | 200.6762 | 179.2619 | 45.1545
246.6135 | 524.1794 | 201.4561 | 179.9847 | 45.2922
247.6135 | 524.1424 | 202.2386 | 180.7522 | 45.4237
248.6135 | 524.2116 | 203.0241 | 181.4794 | 45.5701
249.6135 | 524.2439 | 203.7654 | 182.183 | 45.7136
250.6135 | 524.3359 | 204.5168 | 182.9073 | 45.877
251.6135 | 524.4647 | 205.3045 | 183.6362 | 46.0445
252.6135 | 524.6866 | 206.0562 | 184.3533 | 46.2256
253.6135 | 524.8549 | 206.856 | 185.0945 | 46.4235
254.6135 | 524.9616 | 207.5926 | 185.7947 | 46.6296
255.6135 | 524.8849 | 208.3281 | 186.489 | 46.8406
256.6135 | 524.8517 | 209.1141 | 187.2577 | 47.0491
257.6135 | 524.9115 | 209.8192 | 187.9649 | 47.2797
258.6135 | 524.9386 | 210.6006 | 188.6609 | 47.5038
259.6135 | 524.6952 | 211.3823 | 189.408 | 47.7432
260.6135 | 524.5224 | 212.1686 | 190.1479 | 47.9703
261.6135 | 524.5327 | 212.9527 | 190.863 | 48.2166
262.6135 | 524.4463 | 213.6777 | 191.6227 | 48.4638
263.6135 | 524.4582 | 214.3848 | 192.2988 | 48.7055
264.6135 | 524.388 | 215.1683 | 192.9214 | 48.959
265.6135 | 524.2122 | 215.9123 | 193.58 | 49.2167
266.6135 | 524.1157 | 216.6244 | 194.2524 | 49.4805
267.6135 | 524.0401 | 217.3382 | 194.9155 | 49.7369
268.6135 | 523.9124 | 218.1032 | 195.6083 | 50.0034
269.6135 | 523.6544 | 218.8589 | 196.2928 | 50.2653
270.6135 | 523.414 | 219.6144 | 196.9542 | 50.5395
271.6135 | 523.4642 | 220.3321 | 197.6698 | 50.8096
272.6135 | 523.5377 | 221.0543 | 198.4091 | 51.0818
273.6135 | 523.545 | 221.7249 | 199.0664 | 51.3632
274.6135 | 523.6511 | 222.465 | 199.7521 | 51.6438
275.6135 | 523.7479 | 223.2084 | 200.4117 | 51.9332
276.6135 | 523.6606 | 223.8814 | 201.156 | 52.2169
277.6135 | 523.6438 | 224.5935 | 201.8467 | 52.5027
278.6135 | 523.6947 | 225.3187 | 202.4641 | 52.8053
279.6135 | 523.8008 | 226.0557 | 203.1273 | 53.0929
280.6135 | 523.8639 | 226.7766 | 203.8055 | 53.3897
281.6135 | 523.7119 | 227.4911 | 204.447 | 53.6852
282.6135 | 523.557 | 228.165 | 205.1414 | 53.99
283.6135 | 523.3494 | 228.872 | 205.8373 | 54.2808
284.6135 | 523.3975 | 229.5925 | 206.5774 | 54.5885
285.6135 | 523.5124 | 230.2933 | 207.1912 | 54.8878
286.6135 | 523.5601 | 230.9854 | 207.8199 | 55.1958
287.6135 | 523.6062 | 231.6775 | 208.4805 | 55.4908
288.6135 | 523.5003 | 232.372 | 209.119 | 55.8062
289.6135 | 523.6322 | 233.0652 | 209.7864 | 56.1223
290.6135 | 523.609 | 233.7683 | 210.4966 | 56.4169
291.6135 | 523.6158 | 234.4859 | 211.1322 | 56.7311
292.6135 | 523.514 | 235.1969 | 211.7949 | 57.0355
293.6135 | 523.4445 | 235.8881 | 212.4356 | 57.35
294.6135 | 523.3437 | 236.5974 | 213.1177 | 57.6517
295.6135 | 523.3714 | 237.2699 | 213.7907 | 57.9701
296.6135 | 523.1167 | 237.9397 | 214.4012 | 58.2862
297.6135 | 523.0206 | 238.638 | 215.0145 | 58.5918
298.6135 | 523.0849 | 239.3374 | 215.7266 | 58.9114
299.6135 | 523.2361 | 239.9963 | 216.3697 | 59.22
300.6135 | 523.4709 | 240.6603 | 217.0068 | 59.5462
301.6135 | 523.6145 | 241.3304 | 217.625 | 59.8623
302.6135 | 523.643 | 242.0121 | 218.2503 | 60.1748
303.6135 | 523.6583 | 242.6554 | 218.9428 | 60.4959
304.6135 | 523.725 | 243.3606 | 219.6344 | 60.8077
305.6135 | 523.7334 | 244.0342 | 220.2582 | 61.13
306.6135 | 523.678 | 244.6478 | 220.9507 | 61.4507
307.6135 | 523.6185 | 245.3061 | 221.5496 | 61.7764
308.6135 | 523.7062 | 245.9522 | 222.1313 | 62.095
309.6135 | 523.6922 | 246.6428 | 222.7406 | 62.4204
310.6135 | 523.5739 | 247.2969 | 223.4057 | 62.7504
311.6135 | 523.6047 | 247.9803 | 224.0617 | 63.079
312.6135 | 523.6332 | 248.663 | 224.6974 | 63.4104
313.6135 | 523.5735 | 249.3263 | 225.428 | 63.7268
314.6135 | 523.5622 | 249.9671 | 226.0547 | 64.0695
315.6135 | 523.5188 | 250.591 | 226.6585 | 64.3982
316.6135 | 523.4772 | 251.2483 | 227.2224 | 64.7264
317.6135 | 523.5977 | 251.9025 | 227.8078 | 65.0647
318.6135 | 523.6673 | 252.5541 | 228.3816 | 65.4105
319.6135 | 523.732 | 253.192 | 228.9706 | 65.7432
320.6135 | 523.6167 | 253.8423 | 229.5401 | 66.0765
321.6135 | 523.6004 | 254.4609 | 230.1969 | 66.4173
322.6135 | 523.552 | 255.1169 | 230.801 | 66.7528
323.6135 | 523.4161 | 255.748 | 231.3653 | 67.0985
324.6135 | 523.5018 | 256.3813 | 232.0259 | 67.4287
325.6135 | 523.5694 | 257.0169 | 232.7196 | 67.7791
326.6135 | 523.5635 | 257.6751 | 233.3378 | 68.1265
327.6135 | 523.4734 | 258.3242 | 234.0087 | 68.4643
328.6135 | 523.4964 | 258.9422 | 234.5994 | 68.8156
329.6135 | 523.3879 | 259.5577 | 235.0952 | 69.1587
330.6135 | 523.4489 | 260.1791 | 235.6592 | 69.5108
331.6135 | 523.4635 | 260.7962 | 236.3286 | 69.8518
332.6135 | 523.4775 | 261.4179 | 236.9042 | 70.1997
333.6135 | 523.484 | 262.0259 | 237.5903 | 70.5477
334.6135 | 523.4842 | 262.6454 | 238.1909 | 70.9062
335.6135 | 523.3741 | 263.233 | 238.8262 | 71.2484
336.6135 | 523.3272 | 263.8722 | 239.4483 | 71.6021
337.6135 | 523.2551 | 264.449 | 239.958 | 71.9536
338.6135 | 523.241 | 265.0624 | 240.4941 | 72.3031
339.6135 | 523.2172 | 265.6592 | 241.2095 | 72.6651
340.6135 | 523.1113 | 266.2662 | 241.7575 | 73.0164
341.6135 | 523.0314 | 266.8784 | 242.3209 | 73.3722
342.6135 | 523.049 | 267.5001 | 242.9246 | 73.7189
343.6135 | 523.1571 | 268.1025 | 243.5044 | 74.087
344.6135 | 523.1943 | 268.6882 | 244.0357 | 74.4342
345.6135 | 523.2493 | 269.2417 | 244.5878 | 74.8082
346.6135 | 523.1091 | 269.8437 | 245.1316 | 75.1696
347.6135 | 523.1256 | 270.43 | 245.6654 | 75.5171
348.6135 | 523.0213 | 271.0357 | 246.2442 | 75.8967
349.6135 | 523.1015 | 271.6283 | 246.9458 | 76.2452
350.6135 | 523.1462 | 272.2094 | 247.4907 | 76.6142
351.6135 | 523.0778 | 272.7713 | 247.9507 | 76.9737
352.6135 | 523.2275 | 273.3761 | 248.4956 | 77.3436
353.6135 | 523.2359 | 273.9974 | 249.1801 | 77.7079
354.6135 | 523.2493 | 274.5589 | 249.764 | 78.0732
355.6135 | 523.355 | 275.1194 | 250.2923 | 78.4455
356.6135 | 523.2535 | 275.6948 | 250.7699 | 78.8014
357.6135 | 523.3029 | 276.2543 | 251.4475 | 79.1869
358.6135 | 523.2414 | 276.8147 | 252.1031 | 79.5475
359.6135 | 523.3022 | 277.4192 | 252.5755 | 79.9205
360.6135 | 523.2751 | 277.9666 | 253.1161 | 80.2931
361.6135 | 523.305 | 278.5349 | 253.6578 | 80.66
362.6135 | 523.3892 | 279.085 | 254.3102 | 81.0342
363.6135 | 523.3633 | 279.6569 | 254.9503 | 81.4082
364.6135 | 523.4084 | 280.211 | 255.5682 | 81.7851
365.6135 | 523.3522 | 280.7615 | 256.0023 | 82.149
366.6135 | 523.2516 | 281.3284 | 256.4518 | 82.5332
367.6135 | 523.316 | 281.918 | 257.0041 | 82.9002
368.6135 | 523.4422 | 282.4965 | 257.5815 | 83.2801
369.6135 | 523.595 | 283.0667 | 258.2004 | 83.6534
370.6135 | 523.6921 | 283.6106 | 258.7798 | 84.0342
371.6135 | 523.6646 | 284.1579 | 259.2991 | 84.4153
372.6135 | 523.7704 | 284.7069 | 259.8998 | 84.7873
373.6135 | 523.9206 | 285.2611 | 260.557 | 85.168
374.6135 | 523.9574 | 285.8174 | 261.1132 | 85.5426
375.6135 | 524.0027 | 286.3966 | 261.5893 | 85.9193
376.6135 | 523.9488 | 286.9376 | 262.0938 | 86.2912
377.6135 | 523.8596 | 287.4645 | 262.5473 | 86.6685
378.6135 | 523.757 | 288.0082 | 263.1844 | 87.0399
379.6135 | 523.7687 | 288.5499 | 263.7147 | 87.4169
380.6135 | 523.7417 | 289.0761 | 264.141 | 87.7973
381.6135 | 523.7085 | 289.6329 | 264.6112 | 88.1675
382.6135 | 523.6598 | 290.1677 | 265.115 | 88.5569
383.6135 | 523.7136 | 290.6886 | 265.5987 | 88.9217
384.6135 | 523.7002 | 291.2225 | 266.1707 | 89.2998
385.6135 | 523.6472 | 291.7622 | 266.6351 | 89.6807
386.6135 | 523.653 | 292.303 | 267.173 | 90.0575
387.6135 | 523.7192 | 292.8332 | 267.7794 | 90.4422
388.6135 | 523.6644 | 293.3478 | 268.2175 | 90.8145
389.6135 | 523.6827 | 293.8906 | 268.6502 | 91.2023
390.6135 | 523.7235 | 294.4272 | 269.2233 | 91.5765
391.6135 | 523.7929 | 294.9525 | 269.887 | 91.961
392.6135 | 523.6735 | 295.487 | 270.3291 | 92.3401
393.6135 | 523.6228 | 295.9908 | 270.893 | 92.7292
394.6135 | 523.4254 | 296.5021 | 271.3645 | 93.1164
395.6135 | 523.388 | 297.0293 | 271.909 | 93.4987
396.6135 | 523.3876 | 297.5541 | 272.4874 | 93.8954
397.6135 | 523.2356 | 298.0678 | 273.1037 | 94.2818
398.6135 | 523.2093 | 298.59 | 273.6686 | 94.6632
399.6135 | 523.1483 | 299.094 | 274.0009 | 95.05
400.6135 | 523.0651 | 299.6005 | 274.4965 | 95.4403
401.6135 | 522.86 | 300.1059 | 275.0404 | 95.8237
402.6135 | 522.6732 | 300.619 | 275.5632 | 96.2178
403.6135 | 522.6474 | 301.1329 | 276.0698 | 96.6063
404.6135 | 522.701 | 301.6329 | 276.5563 | 96.9923
405.6135 | 522.7765 | 302.1184 | 277.1012 | 97.3738
406.6135 | 522.7293 | 302.6096 | 277.5743 | 97.7731
407.6135 | 522.7589 | 303.1011 | 277.9358 | 98.1608
408.6135 | 522.7709 | 303.6128 | 278.5741 | 98.5527
409.6135 | 522.8734 | 304.0954 | 279.1031 | 98.9422
410.6135 | 522.9267 | 304.594 | 279.4968 | 99.3331
411.6135 | 522.8311 | 305.1076 | 280.0463 | 99.7252
412.6135 | 522.8188 | 305.6045 | 280.4027 | 100.1136
413.6135 | 522.7671 | 306.0892 | 280.8389 | 100.4986
414.6135 | 522.7398 | 306.5734 | 281.4058 | 100.9005
415.6135 | 522.781 | 307.0973 | 281.7891 | 101.285
416.6135 | 522.7846 | 307.5879 | 282.2536 | 101.6786
417.6135 | 522.6879 | 308.08 | 282.7838 | 102.0792
418.6135 | 522.6424 | 308.5795 | 283.1247 | 102.4703
419.6135 | 522.7999 | 309.0555 | 283.688 | 102.8699
420.6135 | 522.834 | 309.5378 | 284.3385 | 103.2668
421.6135 | 522.8554 | 310.0219 | 284.7589 | 103.6602
422.6135 | 522.7829 | 310.5064 | 285.098 | 104.0596
423.6135 | 522.7091 | 310.9783 | 285.6897 | 104.4546
424.6135 | 522.6361 | 311.4855 | 286.2541 | 104.8498
425.6135 | 522.6727 | 311.9506 | 286.7065 | 105.2514
426.6135 | 522.7798 | 312.4192 | 287.2007 | 105.6486
427.6135 | 522.9092 | 312.8759 | 287.646 | 106.042
428.6135 | 522.9911 | 313.3433 | 287.9696 | 106.4422
429.6135 | 523.0587 | 313.8165 | 288.513 | 106.8426
430.6135 | 523.3024 | 314.3037 | 288.9448 | 107.2494
431.6135 | 523.4166 | 314.7838 | 289.5283 | 107.6443
432.6135 | 523.484 | 315.2379 | 290.0745 | 108.0495
433.6135 | 523.4169 | 315.7343 | 290.5576 | 108.4333
434.6135 | 523.3979 | 316.2025 | 291.108 | 108.8421
435.6135 | 523.3904 | 316.6932 | 291.5398 | 109.2495
436.6135 | 523.4054 | 317.1588 | 292.0586 | 109.6432
437.6135 | 523.5221 | 317.6233 | 292.5087 | 110.0396
438.6135 | 523.3701 | 318.0955 | 292.796 | 110.4375
439.6135 | 523.1887 | 318.5675 | 293.1034 | 110.8399
440.6135 | 523.2079 | 319.0289 | 293.6712 | 111.2357
441.6135 | 523.1752 | 319.4941 | 294.1365 | 111.6404
442.6135 | 523.0443 | 319.9661 | 294.4971 | 112.0305
443.6135 | 523.0143 | 320.4443 | 294.8521 | 112.4386
444.6135 | 522.9195 | 320.8984 | 295.3191 | 112.8329
445.6135 | 522.8915 | 321.3663 | 295.7601 | 113.2348
446.6135 | 522.7974 | 321.7945 | 296.1793 | 113.6312
447.6135 | 522.6175 | 322.251 | 296.7022 | 114.0255
448.6135 | 522.6067 | 322.7183 | 297.2563 | 114.4209
449.6135 | 522.4079 | 323.1663 | 297.7129 | 114.8127
450.6135 | 522.3087 | 323.6274 | 298.1446 | 115.2216
451.6135 | 522.1403 | 324.0725 | 298.5011 | 115.6159
452.6135 | 521.9374 | 324.522 | 299.0323 | 116.0165
453.6135 | 521.8667 | 324.9595 | 299.5252 | 116.4157
454.6135 | 521.9029 | 325.4201 | 300.0043 | 116.8047
455.6135 | 521.9237 | 325.8691 | 300.4514 | 117.2067
456.6135 | 521.9243 | 326.3124 | 300.8534 | 117.6044
457.6135 | 521.8945 | 326.7564 | 301.1319 | 117.9953
458.6135 | 521.8604 | 327.1901 | 301.6628 | 118.3857
459.6135 | 521.8245 | 327.6097 | 302.0706 | 118.7783
460.6135 | 521.9687 | 328.0551 | 302.3595 | 119.1672
461.6135 | 522.1504 | 328.4972 | 302.9183 | 119.5533
462.6135 | 522.254 | 328.9354 | 303.4468 | 119.9485
463.6135 | 522.3206 | 329.3759 | 303.861 | 120.3285
464.6135 | 522.4202 | 329.8081 | 304.024 | 120.7157
465.6135 | 522.5066 | 330.2466 | 304.3413 | 121.0921
466.6135 | 522.5342 | 330.6842 | 304.6973 | 121.4703
467.6135 | 522.5227 | 331.1077 | 305.2469 | 121.8524
468.6135 | 522.4936 | 331.535 | 305.6754 | 122.2299
469.6135 | 522.4696 | 331.9568 | 306.052 | 122.5977
470.6135 | 522.3324 | 332.3844 | 306.5333 | 122.9661
471.6135 | 522.1718 | 332.8092 | 306.9487 | 123.332
472.6135 | 522.0251 | 333.237 | 307.268 | 123.6931
473.6135 | 522.0241 | 333.6549 | 307.7396 | 124.0646
474.6135 | 522.0211 | 334.0908 | 308.0494 | 124.4209
475.6135 | 522.0219 | 334.5002 | 308.514 | 124.778
476.6135 | 522.0851 | 334.92 | 309.1202 | 125.1354
477.6135 | 522.0579 | 335.3375 | 309.6589 | 125.486
478.6135 | 522.0584 | 335.7651 | 310.1136 | 125.8394
479.6135 | 522.108 | 336.1867 | 310.4734 | 126.1761
480.6135 | 522.2122 | 336.6006 | 310.8145 | 126.5322
481.6135 | 522.3386 | 337.0048 | 311.148 | 126.8664
482.6135 | 522.3319 | 337.3904 | 311.3972 | 127.2101
483.6135 | 522.3803 | 337.8265 | 312.009 | 127.548
484.6135 | 522.4563 | 338.2223 | 312.4179 | 127.8926
485.6135 | 522.5837 | 338.6363 | 312.8481 | 128.2198
486.6135 | 522.7283 | 339.0477 | 313.1771 | 128.5529
487.6135 | 522.7624 | 339.4568 | 313.4146 | 128.8891
488.6135 | 522.8237 | 339.8541 | 313.9312 | 129.2128
489.6135 | 522.8861 | 340.2648 | 314.2379 | 129.5412
490.6135 | 522.8859 | 340.682 | 314.6941 | 129.8682
491.6135 | 522.874 | 341.0828 | 315.0434 | 130.2019
492.6135 | 522.8148 | 341.4859 | 315.4352 | 130.5264
493.6135 | 522.8267 | 341.8939 | 315.9198 | 130.8527
494.6135 | 522.91 | 342.2946 | 316.2355 | 131.1775
495.6135 | 523.0551 | 342.6998 | 316.6289 | 131.4926
496.6135 | 523.0558 | 343.0939 | 317.2121 | 131.8287
497.6135 | 523.0771 | 343.4955 | 317.531 | 132.1489
498.6135 | 523.0839 | 343.8993 | 317.8684 | 132.4699
499.6135 | 523.0897 | 344.2843 | 318.3196 | 132.7919
500.6135 | 522.9608 | 344.6306 | 318.7765 | 133.1072
501.6135 | 522.794 | 345.0415 | 319.2471 | 133.437
502.6135 | 522.7986 | 345.4447 | 319.5245 | 133.7657
503.6135 | 522.6513 | 345.8334 | 320.0231 | 134.0947
504.6135 | 522.5073 | 346.2374 | 320.3834 | 134.4122
505.6135 | 522.3771 | 346.6252 | 320.5513 | 134.7356
506.6135 | 522.3847 | 347.0033 | 320.8766 | 135.0694
507.6135 | 522.3353 | 347.3856 | 321.4034 | 135.3876
508.6135 | 522.3522 | 347.7568 | 321.5569 | 135.7166
509.6135 | 522.3305 | 348.1466 | 322.0842 | 136.0355
510.6135 | 522.3794 | 348.5164 | 322.6261 | 136.3725
511.6135 | 522.3863 | 348.8998 | 323.0308 | 136.6923
512.6135 | 522.4078 | 349.2773 | 323.3569 | 137.016
513.6135 | 522.3253 | 349.6606 | 323.8131 | 137.3513
514.6135 | 522.3308 | 350.0521 | 324.1581 | 137.6726
515.6135 | 522.3818 | 350.4139 | 324.3642 | 138.0173
516.6135 | 522.2496 | 350.7876 | 324.6419 | 138.3431
517.6135 | 522.2491 | 351.1712 | 324.8052 | 138.6736
518.6135 | 522.3079 | 351.5553 | 325.3945 | 138.9981
519.6135 | 522.2858 | 351.9272 | 325.8554 | 139.3343
520.6135 | 522.1839 | 352.3058 | 326.2851 | 139.6681
521.6135 | 522.3867 | 352.6618 | 326.4796 | 139.9995
522.6135 | 522.4359 | 353.0343 | 326.9052 | 140.3457
523.6135 | 522.4149 | 353.4147 | 327.1872 | 140.6817
524.6135 | 522.3844 | 353.7835 | 327.6481 | 141.0323
525.6135 | 522.3381 | 354.1365 | 328.1712 | 141.3812
526.6135 | 522.2771 | 354.4967 | 328.494 | 141.7428
527.6135 | 522.31 | 354.8551 | 328.8639 | 142.0874
528.6135 | 522.3926 | 355.2178 | 329.3235 | 142.4395
529.6135 | 522.401 | 355.5858 | 329.6992 | 142.8199
530.6135 | 522.3666 | 355.9543 | 329.98 | 143.1657
531.6135 | 522.3177 | 356.3137 | 330.2765 | 143.5438
532.6135 | 522.3308 | 356.6651 | 330.5252 | 143.9083
533.6135 | 522.4909 | 357.0085 | 330.9091 | 144.2888
534.6135 | 522.6332 | 357.383 | 331.3157 | 144.6634
535.6135 | 522.4984 | 357.7341 | 331.7202 | 145.044
536.6135 | 522.5358 | 358.0164 | 332.0634 | 145.424
537.6135 | 522.5417 | 358.3831 | 332.5983 | 145.8024
538.6135 | 522.5832 | 358.7367 | 332.9407 | 146.1922
539.6135 | 522.4934 | 359.0981 | 333.2 | 146.5739
540.6135 | 522.4955 | 359.463 | 333.6449 | 146.9726
541.6135 | 522.4622 | 359.8228 | 333.7797 | 147.3637
542.6135 | 522.4062 | 360.1612 | 334.0364 | 147.7561
543.6135 | 522.3748 | 360.5063 | 334.473 | 148.1524
544.6135 | 522.343 | 360.8599 | 335.0209 | 148.5525
545.6135 | 522.4365 | 361.1988 | 335.4649 | 148.9602
546.6135 | 522.483 | 361.5459 | 335.8828 | 149.3535
547.6135 | 522.3116 | 361.8947 | 336.1777 | 149.7525
548.6135 | 522.2666 | 362.2477 | 336.4189 | 150.1585
549.6135 | 522.2785 | 362.5741 | 336.5851 | 150.5645
550.6135 | 522.1286 | 362.9183 | 337.0009 | 150.972
551.6135 | 522.1057 | 363.2584 | 337.4019 | 151.3847
552.6135 | 522.0594 | 363.5988 | 337.6166 | 151.7951
553.6135 | 522.1916 | 363.9263 | 337.7941 | 152.213
554.6135 | 522.1828 | 364.281 | 338.1226 | 152.6314
555.6135 | 522.2052 | 364.6198 | 338.6119 | 153.0483
556.6135 | 522.141 | 364.9273 | 338.9008 | 153.4762
557.6135 | 522.1811 | 365.2711 | 339.2302 | 153.8979
558.6135 | 522.1806 | 365.6093 | 339.5954 | 154.3253
559.6135 | 522.0976 | 365.9361 | 339.9554 | 154.7494
560.6135 | 522.0212 | 366.2704 | 340.3734 | 155.184
561.6135 | 522.0601 | 366.5964 | 340.5175 | 155.626
562.6135 | 521.9836 | 366.9314 | 340.8912 | 156.0641
563.6135 | 521.9769 | 367.2297 | 341.3299 | 156.5069
564.6135 | 521.9642 | 367.545 | 341.5546 | 156.9412
565.6135 | 521.9923 | 367.8917 | 341.9758 | 157.3987
566.6135 | 522.085 | 368.2198 | 342.2869 | 157.8414
567.6135 | 522.0167 | 368.5515 | 342.3579 | 158.3004
568.6135 | 521.9837 | 368.8667 | 342.8407 | 158.7507
569.6135 | 521.9919 | 369.1834 | 343.1462 | 159.2009
570.6135 | 521.8541 | 369.5175 | 343.4767 | 159.664
571.6135 | 521.8856 | 369.8471 | 343.852 | 160.1114
572.6135 | 521.8833 | 370.1811 | 344.172 | 160.5821
573.6135 | 521.9208 | 370.4892 | 344.5931 | 161.0567
574.6135 | 521.9197 | 370.8239 | 344.9205 | 161.5081
575.6135 | 521.9946 | 371.1445 | 345.3468 | 161.9709
576.6135 | 522.1858 | 371.455 | 345.4698 | 162.433
577.6135 | 522.422 | 371.7774 | 345.7265 | 162.9
578.6135 | 522.5074 | 372.0814 | 346.0214 | 163.3556
579.6135 | 522.5019 | 372.3828 | 346.4868 | 163.8263
580.6135 | 522.6819 | 372.7092 | 346.8599 | 164.2739
581.6135 | 522.8079 | 373.0127 | 347.2552 | 164.7514
582.6135 | 522.6973 | 373.3301 | 347.7394 | 165.2097
583.6135 | 522.699 | 373.6349 | 347.9331 | 165.678
584.6135 | 522.6424 | 373.9548 | 348.184 | 166.1386
585.6135 | 522.6998 | 374.2544 | 348.4565 | 166.6018
586.6135 | 522.6364 | 374.5259 | 348.9007 | 167.0727
587.6135 | 522.6699 | 374.8496 | 349.2664 | 167.5327
588.6135 | 522.7276 | 375.1468 | 349.6739 | 168.0014
589.6135 | 522.6099 | 375.3895 | 350.0336 | 168.4694
590.6135 | 522.4287 | 375.705 | 350.3639 | 168.9319
591.6135 | 522.3471 | 375.9904 | 350.7742 | 169.398
592.6135 | 522.3588 | 376.2859 | 351.1022 | 169.8631
593.6135 | 522.508 | 376.6074 | 351.4337 | 170.3341
594.6135 | 522.5429 | 376.9049 | 351.6654 | 170.807
595.6135 | 522.5392 | 377.2026 | 351.9653 | 171.2755
596.6135 | 522.3834 | 377.5411 | 352.2594 | 171.7383
597.6135 | 522.333 | 377.8213 | 352.4912 | 172.2046
598.6135 | 522.3477 | 378.1301 | 352.6591 | 172.6762
599.6135 | 522.339 | 378.4054 | 353.0424 | 173.1437
600.6135 | 522.2675 | 378.7019 | 353.2687 | 173.6228
601.6135 | 522.4149 | 378.9801 | 353.4381 | 174.088
602.6135 | 522.4574 | 379.2824 | 353.792 | 174.5642
603.6135 | 522.369 | 379.5778 | 353.7943 | 175.0399
604.6135 | 522.3884 | 379.8784 | 354.081 | 175.5176
605.6135 | 522.3655 | 380.1873 | 354.4904 | 175.9963
606.6135 | 522.2408 | 380.425 | 354.798 | 176.4753
607.6135 | 522.2479 | 380.7241 | 355.3075 | 176.9601
608.6135 | 522.191 | 381.0301 | 355.6371 | 177.44
609.6135 | 522.1765 | 381.3115 | 355.808 | 177.9268
610.6135 | 522.1562 | 381.6067 | 356.0334 | 178.4032
611.6135 | 522.1282 | 381.8774 | 356.2829 | 178.8887
612.6135 | 522.1538 | 382.1856 | 356.5709 | 179.3795
613.6135 | 522.2148 | 382.4587 | 356.7106 | 179.8714
614.6135 | 522.1513 | 382.7354 | 356.924 | 180.3655
615.6135 | 522.0133 | 383.0224 | 357.2873 | 180.8543
616.6135 | 521.995 | 383.3143 | 357.6058 | 181.3432
617.6135 | 521.9013 | 383.5911 | 358.0737 | 181.8365
618.6135 | 521.7925 | 383.8794 | 358.2887 | 182.325
619.6135 | 521.7188 | 384.1701 | 358.6082 | 182.8197
620.6135 | 521.6395 | 384.4076 | 358.8547 | 183.2997
621.6135 | 521.6297 | 384.6966 | 359.147 | 183.7966
622.6135 | 521.5979 | 384.9649 | 359.6016 | 184.2881
623.6135 | 521.6077 | 385.2259 | 359.7769 | 184.7791
624.6135 | 521.6595 | 385.5006 | 359.8273 | 185.2666
625.6135 | 521.7164 | 385.7469 | 360.1005 | 185.763
626.6135 | 521.776 | 386.0113 | 360.543 | 186.254
627.6135 | 521.7105 | 386.312 | 360.7291 | 186.7462
628.6135 | 521.8011 | 386.5832 | 361.0134 | 187.2466
629.6135 | 522.0178 | 386.8731 | 361.3167 | 187.7428
630.6135 | 522.132 | 387.1337 | 361.3757 | 188.2226
631.6135 | 522.2065 | 387.401 | 361.7339 | 188.7188
632.6135 | 522.2351 | 387.6981 | 362.0964 | 189.2135
633.6135 | 522.3142 | 387.9718 | 362.1227 | 189.7001
634.6135 | 522.2993 | 388.2123 | 362.5106 | 190.2054
635.6135 | 522.4798 | 388.4808 | 363.0676 | 190.7019
636.6135 | 522.5611 | 388.7414 | 363.4391 | 191.1922
637.6135 | 522.5112 | 389.0449 | 363.7815 | 191.6788
638.6135 | 522.3751 | 389.2927 | 364.0952 | 192.1765
639.6135 | 522.3322 | 389.5724 | 364.2512 | 192.6722
640.6135 | 522.2396 | 389.8384 | 364.3644 | 193.166
641.6135 | 522.2268 | 390.0979 | 364.8103 | 193.6519
642.6135 | 522.2931 | 390.3418 | 365.1589 | 194.1453
643.6135 | 522.203 | 390.6096 | 365.2648 | 194.6429
644.6135 | 522.1076 | 390.8776 | 365.4378 | 195.1255
645.6135 | 522.0279 | 391.1357 | 365.6424 | 195.6238
646.6135 | 522.0509 | 391.4108 | 365.76 | 196.1177
647.6135 | 522.0693 | 391.6498 | 366.2884 | 196.6039
648.6135 | 522.1428 | 391.9388 | 366.609 | 197.0945
649.6135 | 522.2692 | 392.1761 | 366.652 | 197.5949
650.6135 | 522.4645 | 392.4529 | 367.0065 | 198.0813
651.6135 | 522.5643 | 392.7093 | 367.5148 | 198.5665
652.6135 | 522.6376 | 392.9706 | 367.9095 | 199.062
653.6135 | 522.6551 | 393.2206 | 368.197 | 199.5513
654.6135 | 522.7194 | 393.5008 | 368.5036 | 200.0587
655.6135 | 522.8749 | 393.756 | 368.7499 | 200.5471
656.6135 | 522.9097 | 393.986 | 368.813 | 201.0425
657.6135 | 522.865 | 394.2517 | 369.1924 | 201.5315
658.6135 | 522.8242 | 394.5028 | 369.4746 | 202.0157
659.6135 | 522.8731 | 394.7709 | 369.8942 | 202.5066
660.6135 | 522.9542 | 395.0505 | 370.0438 | 202.9854
661.6135 | 522.9575 | 395.2888 | 370.2475 | 203.4724
662.6135 | 522.9746 | 395.5233 | 370.6067 | 203.9603
663.6135 | 522.9607 | 395.7635 | 370.9309 | 204.4582
664.6135 | 523.0959 | 396.0001 | 371.2167 | 204.9389
665.6135 | 523.2098 | 396.2739 | 371.5402 | 205.4318
666.6135 | 523.349 | 396.5095 | 371.7891 | 205.9097
667.6135 | 523.2971 | 396.7707 | 372.1292 | 206.4019
668.6135 | 523.2609 | 397.0179 | 372.3764 | 206.8948
669.6135 | 523.264 | 397.2844 | 372.5648 | 207.3711
670.6135 | 523.183 | 397.5429 | 372.8091 | 207.867
671.6135 | 523.2448 | 397.7723 | 373.1421 | 208.35
672.6135 | 523.2842 | 398.0081 | 373.3548 | 208.8403
673.6135 | 523.2016 | 398.264 | 373.5874 | 209.3176
674.6135 | 523.1477 | 398.5342 | 374.0068 | 209.8142
675.6135 | 523.0625 | 398.766 | 374.3654 | 210.3015
676.6135 | 523.1308 | 399.0093 | 374.5648 | 210.78
677.6135 | 523.0717 | 399.2507 | 374.7966 | 211.2702
678.6135 | 523.0211 | 399.4988 | 375.1015 | 211.7445
679.6135 | 522.8973 | 399.7458 | 375.292 | 212.2329
680.6135 | 522.8312 | 399.9847 | 375.4349 | 212.7182
681.6135 | 522.8061 | 400.1833 | 375.7731 | 213.2093
682.6135 | 522.9162 | 400.4322 | 375.9152 | 213.6865
683.6135 | 522.925 | 400.6621 | 376.1825 | 214.1771
684.6135 | 523.0132 | 400.9101 | 376.5244 | 214.6491
685.6135 | 523.0401 | 401.1032 | 376.8233 | 215.1375
686.6135 | 523.0281 | 401.3113 | 377.1086 | 215.6218
687.6135 | 523.0332 | 401.5445 | 377.3783 | 216.1098
688.6135 | 523.0802 | 401.8147 | 377.577 | 216.6097
689.6292 | 523.1267 | 402.0454 | 377.7102 | 217.0994
690.6135 | 523.0907 | 402.2798 | 378.0711 | 217.5848
691.6135 | 523.0643 | 402.454 | 378.2388 | 218.086
692.6135 | 522.8648 | 402.7321 | 378.5172 | 218.5837
693.6135 | 522.6256 | 402.9749 | 378.6267 | 219.0923
694.6135 | 522.5261 | 403.2164 | 378.6499 | 219.61
695.6135 | 522.3755 | 403.4486 | 379.1196 | 220.1112
696.6135 | 522.494 | 403.6916 | 379.5197 | 220.6197
697.6135 | 522.6637 | 403.9221 | 379.5917 | 221.0989
698.6135 | 522.7269 | 404.1388 | 379.5433 | 221.5662
699.6135 | 522.6221 | 404.3791 | 379.7823 | 222.0572
700.6135 | 522.544 | 404.6201 | 380.2027 | 222.5455
701.6135 | 522.5839 | 404.8368 | 380.4479 | 223.0349
702.6135 | 522.6039 | 404.9973 | 380.4801 | 223.5498
703.6135 | 522.5579 | 405.256 | 380.8003 | 224.07
704.6135 | 522.4914 | 405.4985 | 381.0735 | 224.5929
705.6135 | 522.7055 | 405.7309 | 381.4536 | 225.1387
706.6135 | 522.9255 | 405.9426 | 381.6825 | 225.7022
707.6135 | 523.0485 | 406.1727 | 381.9597 | 226.3392
708.6135 | 523.1134 | 406.4092 | 382.3323 | 227.0969
709.6135 | 522.9916 | 406.5964 | 382.553 | 227.8824
710.6135 | 522.9522 | 406.851 | 382.7705 | 228.6929
711.6135 | 523.1091 | 407.0751 | 382.8477 | 229.5465
712.6135 | 523.2829 | 407.2862 | 383.1261 | 230.3917
713.6135 | 523.2394 | 407.5278 | 383.5051 | 231.1635
714.6135 | 523.2171 | 407.7739 | 383.6177 | 231.8817
715.6135 | 523.3252 | 407.9883 | 383.7834 | 232.555
716.6135 | 523.2926 | 408.1838 | 383.9969 | 233.1953
717.6135 | 523.0839 | 408.4188 | 384.3699 | 233.8036
718.6135 | 522.9124 | 408.6483 | 384.5781 | 234.371
719.6135 | 522.9805 | 408.8789 | 384.6039 | 234.9461
720.6135 | 522.8304 | 409.1097 | 384.8904 | 235.4326
721.6135 | 522.7105 | 409.3128 | 385.1043 | 235.8987
722.6135 | 522.6344 | 409.5329 | 385.075 | 236.4111
723.6135 | 522.5754 | 409.7525 | 385.3593 | 236.891
724.6135 | 522.4857 | 409.9782 | 385.5728 | 237.4208
725.6135 | 522.4354 | 410.1815 | 385.9857 | 238.0332
726.6135 | 522.4322 | 410.4189 | 386.1389 | 238.6243
727.6135 | 522.4338 | 410.6507 | 386.6045 | 239.2212
728.6135 | 522.3874 | 410.8465 | 386.9458 | 239.7931
729.6135 | 522.4152 | 411.0758 | 386.9649 | 240.4113
730.6135 | 522.4735 | 411.2887 | 387.2826 | 241.0512
731.6135 | 522.616 | 411.532 | 387.4687 | 241.7022
732.6135 | 522.7137 | 411.7573 | 387.5907 | 242.3562
733.6135 | 522.7745 | 411.9575 | 387.9203 | 242.9254
734.6135 | 522.8232 | 412.1574 | 388.2656 | 243.4343
735.6135 | 522.8716 | 412.3855 | 388.304 | 243.8644
736.6135 | 522.7985 | 412.5905 | 388.2467 | 244.2965
737.6135 | 522.7912 | 412.8182 | 388.5854 | 244.7524
738.6135 | 522.7988 | 413.0143 | 388.7782 | 245.1759
739.6135 | 522.7152 | 413.2473 | 389.0266 | 245.4106
740.6135 | 522.5856 | 413.4807 | 389.105 | 245.7366
741.6135 | 522.5339 | 413.7141 | 389.3289 | 246.1723
742.6135 | 522.4705 | 413.9306 | 389.3955 | 246.608
743.6135 | 522.3678 | 414.1655 | 389.8428 | 247.081
744.6135 | 522.3321 | 414.3843 | 390.0552 | 247.5918
745.6135 | 522.4111 | 414.6094 | 390.2316 | 248.0709
746.6135 | 522.3462 | 414.8444 | 390.4122 | 248.588
747.6135 | 522.407 | 415.0427 | 390.4263 | 249.095
748.6135 | 522.4776 | 415.2871 | 390.6711 | 249.5543
749.6135 | 522.4465 | 415.5423 | 391.1604 | 249.9452
750.6135 | 522.3677 | 415.7522 | 391.2379 | 250.3645
751.6135 | 522.4222 | 415.9576 | 391.4248 | 250.763
752.6135 | 522.4242 | 416.1944 | 391.6171 | 251.1901
753.6135 | 522.2859 | 416.404 | 391.7473 | 251.6094
754.6135 | 522.2914 | 416.6216 | 392.1135 | 252.0148
755.6135 | 522.4536 | 416.8402 | 392.5647 | 252.4425
756.6135 | 522.5634 | 417.0659 | 392.834 | 252.8295
757.6135 | 522.6078 | 417.2988 | 392.8593 | 253.3338
758.6135 | 522.6515 | 417.5341 | 392.6506 | 253.8738
759.6135 | 522.6638 | 417.7594 | 392.8099 | 254.4094
760.6135 | 522.75 | 417.9987 | 393.1063 | 254.9705
761.6135 | 522.6856 | 418.2198 | 393.3813 | 255.4554
762.6135 | 522.7179 | 418.4528 | 393.6824 | 255.8378
763.6135 | 522.6846 | 418.6694 | 393.8737 | 256.4874
764.6135 | 522.5992 | 418.885 | 394.126 | 257.0113
765.6135 | 522.6794 | 419.0955 | 394.4444 | 257.5958
766.6135 | 522.6485 | 419.3226 | 394.7815 | 258.17
767.6135 | 522.6621 | 419.5534 | 394.9516 | 258.6757
768.6135 | 522.7456 | 419.7792 | 395.027 | 259.1431
769.6135 | 522.6869 | 419.9962 | 395.3385 | 259.5579
770.6135 | 522.6607 | 420.2552 | 395.6262 | 259.6423
771.6135 | 522.74 | 420.4649 | 395.7459 | 259.8397
772.6135 | 522.6698 | 420.7031 | 395.6709 | 260.0461
773.6135 | 522.5508 | 420.9149 | 395.9984 | 260.6083
774.6135 | 522.4973 | 421.1187 | 396.4068 | 261.0678
775.6135 | 522.3462 | 421.366 | 396.5465 | 261.4558
776.6135 | 522.3108 | 421.5826 | 396.6365 | 261.6301
777.6135 | 522.4078 | 421.8269 | 397.0722 | 261.8295
778.6135 | 522.4397 | 422.0396 | 397.1279 | 261.9486
779.6135 | 522.4155 | 422.2429 | 397.2271 | 262.0246
780.6135 | 522.4918 | 422.4542 | 397.4958 | 262.3533
781.6135 | 522.4983 | 422.7052 | 397.8274 | 262.8054
782.6135 | 522.5255 | 422.9212 | 397.9627 | 263.0777
783.6135 | 522.6847 | 423.1303 | 398.4123 | 263.3702
784.6135 | 522.8093 | 423.3758 | 398.7525 | 263.6247
785.6135 | 522.8633 | 423.6045 | 398.7859 | 263.9562
786.6135 | 522.8817 | 423.8203 | 399.0704 | 264.3138
787.6135 | 522.8718 | 424.069 | 399.4238 | 264.7058
788.6135 | 522.965 | 424.2663 | 399.5733 | 265.0866
789.6135 | 522.987 | 424.5007 | 399.7049 | 265.4414
790.6135 | 523.1117 | 424.7428 | 400.0661 | 265.7807
791.6135 | 523.2088 | 424.9316 | 400.3617 | 266.1226
792.6135 | 523.2727 | 425.1608 | 400.5462 | 266.36
793.6135 | 523.2878 | 425.4064 | 400.759 | 266.5885
794.6135 | 523.2422 | 425.6317 | 401.0042 | 266.7944
795.6135 | 523.2286 | 425.8025 | 401.1554 | 267.055
796.6135 | 523.1903 | 426.0511 | 401.0434 | 267.362
797.6135 | 523.1067 | 426.2567 | 401.3872 | 267.6991
798.6135 | 522.9768 | 426.5289 | 401.7316 | 268.0498
799.6135 | 522.9446 | 426.7681 | 401.9281 | 268.6856
800.6135 | 522.899 | 426.9899 | 401.7037 | 269.8003
801.6135 | 522.7031 | 427.229 | 402.0068 | 270.4962
802.6135 | 522.6648 | 427.431 | 402.382 | 271.0793
803.6135 | 522.6603 | 427.6444 | 402.5257 | 271.6164
804.6135 | 522.5695 | 427.8851 | 402.6434 | 272.1242
805.6135 | 522.3511 | 428.1064 | 402.9102 | 272.6116
806.6135 | 522.3337 | 428.3008 | 403.2572 | 273.092
807.6135 | 522.5195 | 428.5332 | 403.3823 | 273.6016
808.6135 | 522.5232 | 428.7668 | 403.7778 | 274.0905
809.6135 | 522.5367 | 428.9911 | 404.0314 | 274.579
810.6135 | 522.6242 | 429.2321 | 404.2427 | 275.1053
811.6135 | 522.6036 | 429.4204 | 404.2366 | 275.57
812.6135 | 522.5632 | 429.6544 | 404.236 | 276.0327
813.6135 | 522.5869 | 429.8697 | 404.3896 | 276.452
814.6135 | 522.6601 | 430.1061 | 404.5413 | 276.9644
815.6135 | 522.7581 | 430.3365 | 404.8892 | 277.4515
816.6135 | 522.8787 | 430.5549 | 404.9029 | 277.9518
817.6135 | 522.9308 | 430.7397 | 405.2532 | 278.4139
818.6135 | 522.9947 | 430.9928 | 405.3869 | 278.8945
819.6135 | 523.0739 | 431.2362 | 405.6192 | 279.4081
820.6135 | 523.1362 | 431.4649 | 405.6355 | 279.9578
821.6135 | 523.0957 | 431.6823 | 405.8253 | 280.5306
822.6135 | 522.9472 | 431.8959 | 405.8957 | 281.1375
823.6135 | 523.0693 | 432.0979 | 406.1351 | 281.7114
824.6135 | 523.0823 | 432.3489 | 406.3664 | 282.2563
825.6135 | 523.0228 | 432.5656 | 406.3353 | 282.7589
826.6135 | 523.0543 | 432.7684 | 406.3955 | 283.2783
827.6135 | 522.9523 | 432.9795 | 406.7517 | 283.7609
828.6135 | 522.9603 | 433.1494 | 407.1876 | 284.2445
829.6135 | 522.9413 | 433.3521 | 407.4865 | 284.681
830.6135 | 522.8234 | 433.5578 | 407.6359 | 285.1479
831.6292 | 522.8518 | 433.7741 | 408.0139 | 285.5875
832.6135 | 522.8337 | 433.9773 | 408.1605 | 286.0012
833.6135 | 522.8277 | 434.1826 | 408.2457 | 286.4155
834.6135 | 522.8235 | 434.3898 | 408.6216 | 286.8455
835.6135 | 522.6442 | 434.6392 | 408.8796 | 287.2064
836.6135 | 522.5208 | 434.8554 | 409.0884 | 287.484
837.6135 | 522.4786 | 435.0887 | 409.126 | 287.7217
838.6135 | 522.4119 | 435.3289 | 409.0979 | 287.989
839.6135 | 522.344 | 435.5409 | 409.2098 | 288.2934
840.6135 | 522.2956 | 435.7088 | 409.4928 | 288.5911
841.6135 | 522.2765 | 435.9262 | 409.6873 | 288.9052
842.6135 | 522.2418 | 436.1124 | 409.9419 | 289.1954
843.6135 | 522.2367 | 436.3288 | 410.1528 | 289.5267
844.6135 | 522.3527 | 436.5513 | 410.3826 | 289.7817
845.6135 | 522.399 | 436.761 | 410.6533 | 290.0864
846.6135 | 522.3468 | 436.9664 | 410.4124 | 290.3792
847.6135 | 522.3662 | 437.1645 | 410.5225 | 290.7017
848.6135 | 522.3602 | 437.3709 | 410.8359 | 291.031
849.6135 | 522.3366 | 437.5749 | 410.9739 | 291.3436
850.6135 | 522.4229 | 437.7546 | 411.1805 | 291.63
851.6135 | 522.4598 | 437.9319 | 411.288 | 291.9881
852.6135 | 522.4749 | 438.1372 | 411.537 | 292.3225
853.6135 | 522.4921 | 438.341 | 411.8534 | 292.6959
854.6135 | 522.569 | 438.55 | 412.1498 | 293.0689
855.6135 | 522.4939 | 438.7627 | 412.3258 | 293.4621
856.6135 | 522.5329 | 438.951 | 412.4766 | 293.8529
857.6135 | 522.5425 | 439.1522 | 412.6815 | 294.2335
858.6135 | 522.4674 | 439.3535 | 412.9031 | 294.6363
859.6135 | 522.3748 | 439.5341 | 413.116 | 295.0494
860.6135 | 522.4485 | 439.7292 | 413.2779 | 295.4745
861.6292 | 522.5551 | 439.9068 | 413.4025 | 295.893
862.6135 | 522.5153 | 440.0808 | 413.6228 | 296.3261
863.6135 | 522.539 | 440.2603 | 413.8426 | 296.7268
864.6135 | 522.7072 | 440.4499 | 413.91 | 297.1737
865.6135 | 522.6926 | 440.6444 | 414.1393 | 297.5925
866.6135 | 522.7097 | 440.8315 | 414.2082 | 298.0429
867.6135 | 522.7897 | 441.0486 | 414.445 | 298.5048
868.6135 | 522.7573 | 441.2093 | 414.5004 | 298.9246
869.6135 | 522.7161 | 441.3959 | 414.4273 | 299.3461
870.6135 | 522.7295 | 441.5976 | 414.4062 | 299.7739
871.6135 | 522.7766 | 441.7733 | 414.8383 | 300.2256
872.6135 | 522.7692 | 441.959 | 415.0298 | 300.6734
873.6135 | 522.9082 | 442.1414 | 415.1355 | 301.1303
874.6135 | 522.698 | 442.3238 | 415.2184 | 301.5895
875.6135 | 522.5656 | 442.5298 | 415.5556 | 302.0503
876.6135 | 522.728 | 442.7283 | 415.6412 | 302.507
877.6135 | 522.8733 | 442.936 | 415.6501 | 302.9671
878.6135 | 522.8834 | 443.145 | 415.7619 | 303.4368
879.6135 | 522.927 | 443.3338 | 415.9034 | 303.8726
880.6135 | 522.9691 | 443.5244 | 416.2693 | 304.3439
881.6135 | 522.9624 | 443.7193 | 416.3835 | 304.8027
882.6135 | 522.974 | 443.9044 | 416.6012 | 305.2587
883.6135 | 522.9829 | 444.0778 | 416.9246 | 305.7426
884.6135 | 523.0376 | 444.2504 | 417.2382 | 306.2017
885.6135 | 523.1019 | 444.4277 | 417.5201 | 306.6678
886.6135 | 523.1642 | 444.5824 | 417.6087 | 307.1272
887.6135 | 523.2553 | 444.7225 | 417.42 | 307.5833
888.6135 | 523.392 | 444.9183 | 417.5169 | 308.0394
889.6135 | 523.3395 | 445.1097 | 417.8519 | 308.5126
890.6135 | 523.5024 | 445.2989 | 417.9721 | 308.9432
891.6135 | 523.5605 | 445.4998 | 418.1196 | 309.3731
892.6135 | 523.4452 | 445.663 | 418.2989 | 309.808
893.6135 | 523.2357 | 445.8496 | 418.4292 | 310.2358
894.6135 | 523.1407 | 445.9946 | 418.6322 | 310.665
895.6135 | 523.0006 | 446.1891 | 418.8489 | 311.1004
896.6135 | 522.9871 | 446.3434 | 418.994 | 311.521
897.6135 | 522.7755 | 446.5199 | 419.1697 | 311.9379
898.6135 | 522.6133 | 446.7058 | 419.2911 | 312.3552
899.6135 | 522.5813 | 446.8823 | 419.5353 | 312.7649
900.6135 | 522.6159 | 447.0623 | 419.7865 | 313.1459
901.6135 | 522.5626 | 447.2366 | 419.9055 | 313.5402
902.6135 | 522.5909 | 447.3986 | 420.2383 | 313.9576
903.6135 | 522.5241 | 447.5486 | 420.2664 | 314.4017
904.6135 | 522.4808 | 447.7379 | 420.1966 | 314.8545
905.6135 | 522.3736 | 447.9084 | 420.4236 | 315.3394
906.6135 | 522.2266 | 448.0713 | 420.6355 | 315.8279
907.6135 | 522.1363 | 448.2386 | 420.6454 | 316.3145
908.6135 | 522.1744 | 448.4004 | 420.9417 | 316.7912
909.6135 | 522.108 | 448.5476 | 420.9107 | 317.2718
910.6135 | 521.9956 | 448.718 | 421.0363 | 317.7597
911.6135 | 522.0236 | 448.837 | 421.2122 | 318.2259
912.6135 | 522.2755 | 449.0314 | 421.4732 | 318.7011
913.6135 | 522.2612 | 449.2212 | 421.624 | 319.1557
914.6135 | 522.1944 | 449.3795 | 421.5101 | 319.6332
915.6135 | 522.2499 | 449.5338 | 421.3752 | 320.1232
916.6135 | 522.2659 | 449.7376 | 421.5517 | 320.6099
917.6135 | 522.3457 | 449.8891 | 421.9962 | 321.1007
918.6135 | 522.2796 | 450.0783 | 422.2339 | 321.587
919.6135 | 522.2106 | 450.2477 | 422.2754 | 322.067
920.6135 | 522.2565 | 450.4249 | 422.6148 | 322.5328
921.6135 | 522.2033 | 450.5972 | 422.8955 | 323.0111
922.6135 | 522.2131 | 450.7395 | 423.0199 | 323.4756
923.6135 | 522.2749 | 450.8545 | 423.0967 | 323.9423
924.6135 | 522.3479 | 451.0601 | 423.2966 | 324.4296
925.6135 | 522.3051 | 451.2434 | 423.143 | 324.8919
926.6135 | 522.3724 | 451.4043 | 423.3422 | 325.3826
927.6135 | 522.4297 | 451.5743 | 423.5966 | 325.8661
928.6135 | 522.4539 | 451.7261 | 423.5584 | 326.3457
929.6135 | 522.5 | 451.9065 | 423.8413 | 326.839
930.6135 | 522.5675 | 452.0772 | 424.1458 | 327.2989
931.6135 | 522.6839 | 452.2484 | 424.4225 | 327.7908
932.6135 | 522.7283 | 452.4115 | 424.2794 | 328.2704
933.6135 | 522.7556 | 452.5476 | 424.4107 | 328.7386
934.6135 | 522.7248 | 452.7562 | 424.677 | 329.1945
935.6135 | 522.7225 | 452.8884 | 424.6641 | 329.6461
936.6135 | 522.6118 | 453.0425 | 424.7871 | 330.0756
937.6135 | 522.5429 | 453.1976 | 424.7755 | 330.509
938.6135 | 522.6381 | 453.3908 | 425.008 | 330.935
939.6135 | 522.6573 | 453.573 | 425.0225 | 331.3676
940.6135 | 522.6428 | 453.7467 | 425.1586 | 331.7962
941.6135 | 522.7558 | 453.9118 | 425.1584 | 332.2158
942.6135 | 522.8951 | 454.0469 | 425.2858 | 332.635
943.6135 | 523.0173 | 454.2128 | 425.6241 | 333.0489
944.6135 | 523.1581 | 454.3844 | 425.9224 | 333.4575
945.6135 | 523.175 | 454.5626 | 426.1894 | 333.8758
946.6135 | 523.2584 | 454.725 | 426.0869 | 334.2712
947.6135 | 523.3335 | 454.8935 | 426.2585 | 334.6575
948.6135 | 523.4359 | 455.0378 | 426.5177 | 335.0008
949.6135 | 523.3605 | 455.2035 | 426.7058 | 335.3887
950.6135 | 523.3296 | 455.3667 | 426.7002 | 335.7746
951.6135 | 523.3163 | 455.5172 | 426.3957 | 336.1739
952.6135 | 523.35 | 455.6537 | 426.4142 | 336.5543
953.6135 | 523.3896 | 455.8114 | 426.5896 | 336.931
954.6135 | 523.2958 | 455.9761 | 426.96 | 337.269
955.6135 | 523.3192 | 456.086 | 427.2447 | 337.6116
956.6135 | 523.2618 | 456.2335 | 427.5128 | 337.9208
957.6135 | 523.1306 | 456.3619 | 427.6912 | 338.2414
958.6135 | 523.0326 | 456.5316 | 427.6268 | 338.554
959.6135 | 522.9247 | 456.7047 | 427.873 | 338.8588
960.6135 | 522.8728 | 456.8662 | 428.1471 | 339.1671
961.6135 | 522.7952 | 456.9774 | 428.2813 | 339.4715
962.6135 | 522.7776 | 457.021 | 428.388 | 339.7121
963.6135 | 522.7103 | 457.2275 | 428.5459 | 339.9559
964.6135 | 522.5955 | 457.362 | 428.6948 | 340.1969
965.6135 | 522.3796 | 457.5486 | 428.8267 | 340.4535
966.6135 | 522.3826 | 457.6705 | 428.8913 | 340.7205
967.6135 | 522.3711 | 457.8411 | 429.0484 | 340.995
968.6135 | 522.424 | 458.0078 | 429.0554 | 341.2905
969.6135 | 522.6016 | 458.1396 | 429.195 | 341.5698
970.6135 | 522.6888 | 458.2541 | 429.3115 | 341.8451
971.6135 | 522.7446 | 458.3944 | 429.3468 | 342.0917
972.6135 | 522.7241 | 458.5667 | 429.5478 | 342.3519
973.6135 | 522.6316 | 458.7077 | 429.6747 | 342.6095
974.6135 | 522.4773 | 458.8515 | 429.5731 | 342.8824
975.6135 | 522.3245 | 459.0002 | 429.8702 | 343.1715
976.6135 | 522.2761 | 459.1028 | 430.1597 | 343.4509
977.6135 | 522.1455 | 459.2465 | 430.2974 | 343.7305
978.6135 | 521.9609 | 459.4089 | 430.2624 | 344.0068
979.6135 | 521.8771 | 459.4701 | 430.3225 | 344.3056
980.6135 | 522.0142 | 459.6122 | 430.4159 | 344.6164
981.6135 | 521.9845 | 459.7893 | 430.6207 | 344.9112
982.6135 | 522.039 | 459.8982 | 430.5751 | 345.1946
983.6135 | 522.0971 | 460.0048 | 430.6383 | 345.4812
984.6135 | 522.1441 | 460.1851 | 430.7372 | 345.7507
985.6135 | 522.0704 | 460.3328 | 430.8751 | 346.0044
986.6135 | 522.1177 | 460.4616 | 430.9869 | 346.2114
987.6135 | 521.993 | 460.6151 | 431.0482 | 346.4786
988.6135 | 521.8744 | 460.7429 | 431.3944 | 346.7731
989.6135 | 521.9932 | 460.8487 | 431.5884 | 347.0504
990.6135 | 522.0774 | 460.9953 | 431.6815 | 347.3406
991.6135 | 522.2197 | 461.1106 | 431.8326 | 347.6122
992.6135 | 522.1607 | 461.2676 | 431.9142 | 347.8794
993.6135 | 522.1081 | 461.3938 | 431.9618 | 348.1616
994.6135 | 522.088 | 461.5376 | 432.1319 | 348.4284
995.6135 | 522.235 | 461.6626 | 432.3896 | 348.6995
996.6135 | 522.2924 | 461.8162 | 432.4303 | 348.9614
997.6135 | 522.3562 | 461.9716 | 432.3613 | 349.1612
998.6135 | 522.3655 | 462.0896 | 432.5682 | 349.3888
999.6135 | 522.3604 | 462.2052 | 432.426 | 349.6838
1000.6135 | 522.4124 | 462.3531 | 432.3658 | 349.9719
1001.6135 | 522.3008 | 462.5045 | 432.5353 | 350.2468
1002.6135 | 522.3026 | 462.6225 | 432.8768 | 350.5213
1003.6135 | 522.3822 | 462.7642 | 432.9079 | 350.7829
1004.6135 | 522.3595 | 462.8845 | 432.9414 | 351.0543
1005.6135 | 522.3145 | 463.0257 | 433.1509 | 351.3212
1006.6135 | 522.2249 | 463.1781 | 433.1705 | 351.5966
1007.6135 | 522.235 | 463.2568 | 433.4299 | 351.8589
1008.6135 | 522.0792 | 463.3718 | 433.5496 | 352.1239
1009.6135 | 521.9197 | 463.4424 | 433.4955 | 352.3846
1010.6135 | 521.9046 | 463.5795 | 433.4305 | 352.6547
1011.6135 | 521.9129 | 463.6865 | 433.7463 | 352.9386
1012.6135 | 521.9791 | 463.8317 | 434.0491 | 353.2042
1013.6135 | 522.0802 | 463.9924 | 434.0581 | 353.4706
1014.6135 | 522.1444 | 464.1151 | 434.1828 | 353.7349
1015.6135 | 522.2784 | 464.2447 | 434.2879 | 353.9946
1016.6135 | 522.2819 | 464.3524 | 434.603 | 354.258
1017.6135 | 522.254 | 464.48 | 434.8273 | 354.5204
1018.6135 | 522.2282 | 464.6358 | 435.0354 | 354.7766
1019.6135 | 522.1119 | 464.7722 | 435.1349 | 355.0308
1020.6135 | 522.0642 | 464.9186 | 435.3232 | 355.2845
1021.6135 | 522.1637 | 465.0517 | 435.4405 | 355.547
1022.6135 | 522.1601 | 465.1509 | 435.4016 | 355.8164
1023.6135 | 522.3208 | 465.3153 | 435.5878 | 356.0684
1024.6135 | 522.3429 | 465.4455 | 435.811 | 356.3405
1025.6135 | 522.3736 | 465.5604 | 435.9142 | 356.5936
1026.6135 | 522.3038 | 465.7222 | 435.7626 | 356.8503
1027.6135 | 522.4349 | 465.8334 | 435.8317 | 357.0373
1028.6135 | 522.4552 | 465.9584 | 435.8528 | 357.2063
1029.6135 | 522.5736 | 466.1094 | 436.1322 | 357.415
1030.6135 | 522.6706 | 466.2278 | 436.2635 | 357.6818
1031.6135 | 522.6757 | 466.367 | 436.5668 | 357.9682
1032.6135 | 522.6087 | 466.4539 | 436.6803 | 358.1981
1033.6135 | 522.5482 | 466.5897 | 436.5661 | 358.3832
1034.6135 | 522.4805 | 466.7433 | 436.5893 | 358.5745
1035.6135 | 522.5302 | 466.8177 | 436.9356 | 358.7767
1036.6135 | 522.4599 | 466.9458 | 437.0364 | 358.9956
1037.6135 | 522.458 | 467.1023 | 437.1459 | 359.2084
1038.6135 | 522.5646 | 467.2437 | 437.0501 | 359.4367
1039.6135 | 522.686 | 467.3853 | 437.141 | 359.6567
1040.6135 | 522.6773 | 467.5198 | 437.3899 | 359.8809
1041.6135 | 522.7087 | 467.6525 | 437.5205 | 360.0918
1042.6135 | 522.74 | 467.78 | 437.3526 | 360.3021
1043.6135 | 522.7743 | 467.917 | 437.3695 | 360.522
1044.6135 | 522.6806 | 468.0554 | 437.6931 | 360.7581
1045.6135 | 522.6155 | 468.2145 | 437.8939 | 360.993
1046.6135 | 522.6069 | 468.325 | 437.9675 | 361.2161
1047.6135 | 522.7477 | 468.4486 | 438.2607 | 361.4467
1048.6135 | 522.9123 | 468.5715 | 438.499 | 361.6809
1049.6135 | 522.9356 | 468.6467 | 438.6723 | 361.9227
1050.6135 | 522.926 | 468.7352 | 438.7039 | 362.1537
1051.6135 | 522.8581 | 468.8807 | 438.6466 | 362.3731
1052.6135 | 522.8581 | 468.9918 | 438.698 | 362.6205
1053.6135 | 522.8499 | 469.1057 | 438.7668 | 362.854
1054.6135 | 522.8262 | 469.244 | 439.0147 | 363.0762
1055.6135 | 522.7889 | 469.4053 | 439.0052 | 363.2895
1056.6135 | 522.77 | 469.5259 | 439.2832 | 363.5245
1057.6135 | 522.7219 | 469.6381 | 439.1699 | 363.7388
1058.6135 | 522.6581 | 469.7569 | 439.2495 | 363.9726
1059.6135 | 522.5103 | 469.8364 | 439.3581 | 364.2616
1060.6135 | 522.4966 | 469.9734 | 439.5294 | 364.5905
1061.6135 | 522.4275 | 470.0788 | 439.7583 | 364.9052
1062.6135 | 522.4055 | 470.2118 | 439.933 | 365.1844
1063.6135 | 522.4248 | 470.2924 | 440.0303 | 365.4187
1064.6135 | 522.4561 | 470.3952 | 440.1849 | 365.7036
1065.6135 | 522.4677 | 470.5305 | 440.1309 | 366.0146
1066.6135 | 522.3896 | 470.6989 | 440.0925 | 366.2277
1067.6135 | 522.4152 | 470.8005 | 440.4009 | 366.4514
1068.6135 | 522.4081 | 470.9241 | 440.5873 | 366.6915
1069.6135 | 522.5499 | 471.0585 | 440.3282 | 366.9063
1070.6135 | 522.5255 | 471.1916 | 440.256 | 367.1302
1071.6135 | 522.5804 | 471.3126 | 440.3612 | 367.3691
1072.6135 | 522.5213 | 471.4231 | 440.6003 | 367.626
1073.6135 | 522.4601 | 471.5328 | 440.7874 | 367.8785
1074.6135 | 522.3638 | 471.625 | 441.0739 | 368.1259
1075.6135 | 522.3829 | 471.7793 | 441.0634 | 368.3969
1076.6135 | 522.3579 | 471.8649 | 441.2814 | 368.6753
1077.6135 | 522.4005 | 471.9648 | 441.3704 | 368.9431
1078.6135 | 522.5323 | 472.0733 | 441.4992 | 369.2188
1079.6135 | 522.5858 | 472.2409 | 441.6517 | 369.4957
1080.6135 | 522.4721 | 472.3752 | 441.8027 | 369.7691
1081.6135 | 522.5064 | 472.464 | 441.868 | 370.0428
1082.6135 | 522.5098 | 472.5965 | 441.8087 | 370.3193
1083.6135 | 522.4711 | 472.6747 | 441.871 | 370.5805
1084.6135 | 522.5178 | 472.8096 | 442.1231 | 370.854
1085.6135 | 522.5361 | 472.8985 | 442.2869 | 371.1031
1086.6135 | 522.5856 | 472.9878 | 442.3882 | 371.3459
1087.6135 | 522.5593 | 473.1079 | 442.5641 | 371.5831
1088.6135 | 522.5624 | 473.2223 | 442.8036 | 371.8236
1089.6135 | 522.6034 | 473.2965 | 442.8488 | 372.0493
1090.6135 | 522.6742 | 473.3774 | 442.961 | 372.2968
1091.6135 | 522.8251 | 473.5021 | 443.1453 | 372.5277
1092.6135 | 522.845 | 473.668 | 443.202 | 372.7635
1093.6135 | 522.9168 | 473.7969 | 443.1593 | 372.9965
1094.6135 | 523.0246 | 473.9021 | 443.1709 | 373.2177
1095.6135 | 523.0342 | 474.0356 | 443.2268 | 373.5088
1096.6135 | 523.0328 | 474.1395 | 443.5377 | 373.7838
1097.6135 | 523.0854 | 474.2661 | 443.7019 | 374.0619
1098.6135 | 523.078 | 474.3781 | 443.6746 | 374.328
1099.6135 | 523.0717 | 474.4933 | 443.823 | 374.5749
1100.6135 | 523.0678 | 474.6079 | 443.9464 | 374.8196
1101.6135 | 523.185 | 474.7345 | 444.1989 | 375.0444
1102.6135 | 523.133 | 474.8409 | 444.344 | 375.2781
1103.6135 | 523.0453 | 474.9298 | 444.1727 | 375.5175
1104.6135 | 522.9889 | 475.0475 | 444.0071 | 375.736
1105.6135 | 522.8747 | 475.1674 | 444.2579 | 375.9574
1106.6135 | 522.8855 | 475.2859 | 444.5308 | 376.1867
1107.6135 | 522.8439 | 475.3989 | 444.486 | 376.4136
1108.6135 | 522.9881 | 475.4597 | 444.5539 | 376.6431
1109.6135 | 522.9624 | 475.5736 | 444.6682 | 376.8711
1110.6135 | 522.8252 | 475.7006 | 444.8098 | 377.108
1111.6135 | 522.8039 | 475.8281 | 444.7553 | 377.3326
1112.6135 | 522.7718 | 475.9527 | 444.9905 | 377.5585
1113.6135 | 522.6133 | 476.0415 | 445.0987 | 377.7976
1114.6135 | 522.5348 | 476.1458 | 445.303 | 378.0246
1115.6135 | 522.6241 | 476.3115 | 445.5434 | 378.2665
1116.6135 | 522.6192 | 476.4101 | 445.6807 | 378.4981
1117.6135 | 522.5667 | 476.4842 | 445.6027 | 378.7391
1118.6135 | 522.4321 | 476.6343 | 445.5396 | 378.9805
1119.6135 | 522.5456 | 476.7805 | 445.6459 | 379.2055
1120.6135 | 522.5896 | 476.8744 | 445.8218 | 379.4772
1121.6135 | 522.5916 | 476.9892 | 445.7426 | 379.736
1122.6135 | 522.4553 | 477.1155 | 445.6882 | 379.9946
1123.6135 | 522.3978 | 477.2116 | 445.8126 | 380.2494
1124.6135 | 522.4565 | 477.3721 | 446.0348 | 380.5072
1125.6135 | 522.483 | 477.4666 | 445.9418 | 380.8154
1126.6135 | 522.4517 | 477.556 | 445.9496 | 381.0876
1127.6135 | 522.4293 | 477.6516 | 446.3064 | 381.3686
1128.6135 | 522.5185 | 477.7941 | 446.5225 | 381.6367
1129.6135 | 522.471 | 477.8756 | 446.5492 | 381.9179
1130.6135 | 522.4862 | 478.0028 | 446.7355 | 382.1841
1131.6135 | 522.6446 | 478.1257 | 446.7573 | 382.4653
1132.6135 | 522.6179 | 478.2341 | 446.8318 | 382.7243
1133.6135 | 522.6647 | 478.3343 | 446.9577 | 383.0564
1134.6135 | 522.7839 | 478.4076 | 446.9641 | 383.3574
1135.6135 | 522.6234 | 478.5298 | 446.9621 | 383.6366
1136.6135 | 522.5576 | 478.6567 | 447.0698 | 383.9181
1137.6135 | 522.5224 | 478.7407 | 447.2334 | 384.2451
1138.6135 | 522.5588 | 478.8574 | 447.48 | 384.5667
1139.6135 | 522.6269 | 478.9165 | 447.4846 | 384.8733
1140.6135 | 522.7012 | 479.0658 | 447.413 | 385.1835
1141.6135 | 522.6616 | 479.1942 | 447.6202 | 385.4814
1142.6135 | 522.658 | 479.3199 | 447.8285 | 385.7663
1143.6135 | 522.6725 | 479.4471 | 447.7812 | 386.0147
1144.6135 | 522.61 | 479.4929 | 447.9679 | 386.3056
1145.6135 | 522.516 | 479.6234 | 447.9597 | 386.586
1146.6135 | 522.5998 | 479.7655 | 447.9806 | 386.8771
1147.6135 | 522.7953 | 479.9213 | 448.2512 | 387.1133
1148.6135 | 522.7481 | 480.0202 | 448.3574 | 387.3106
1149.6135 | 522.7621 | 480.0714 | 448.5828 | 387.5114
1150.6135 | 522.701 | 480.1938 | 448.6508 | 387.7465
1151.6135 | 522.7236 | 480.3329 | 448.5996 | 387.9928
1152.6135 | 522.8485 | 480.489 | 448.8569 | 388.232
1153.6135 | 522.78 | 480.6204 | 448.9656 | 388.4655
1154.6135 | 522.7775 | 480.717 | 448.8752 | 388.6818
1155.6135 | 522.7488 | 480.8413 | 449.1063 | 388.9186
1156.6135 | 522.8264 | 480.9496 | 449.2039 | 389.1592
1157.6135 | 522.908 | 481.0793 | 449.525 | 389.3645
1158.6135 | 522.8752 | 481.2022 | 449.6155 | 389.5718
1159.6135 | 522.7519 | 481.3258 | 449.5172 | 389.7854
1160.6135 | 522.7625 | 481.4758 | 449.6892 | 389.9596
1161.6135 | 522.7585 | 481.6061 | 449.8539 | 390.1136
1162.6135 | 522.6413 | 481.6963 | 449.6991 | 390.2702
1163.6135 | 522.6268 | 481.8164 | 449.6843 | 390.4538
1164.6135 | 522.5846 | 481.9783 | 449.847 | 390.6589
1165.6135 | 522.5402 | 482.133 | 450.04 | 390.8878
1166.6135 | 522.4608 | 482.2404 | 450.2838 | 391.0936
1167.6135 | 522.4352 | 482.3809 | 450.3458 | 391.298
1168.6135 | 522.4703 | 482.5022 | 450.4008 | 391.5248
1169.6135 | 522.3686 | 482.6436 | 450.1686 | 391.737
1170.6135 | 522.3557 | 482.781 | 449.9015 | 391.9516
1171.6135 | 522.3512 | 482.9365 | 450.1556 | 392.2978
1172.6135 | 522.3239 | 483.039 | 450.4807 | 392.5679
1173.6135 | 522.2813 | 483.1506 | 450.552 | 392.775
1174.6135 | 522.3347 | 483.2828 | 450.5556 | 393.0437
1175.6135 | 522.3649 | 483.4252 | 450.6727 | 393.2797
1176.6135 | 522.5235 | 483.5359 | 450.7512 | 393.5022
1177.6135 | 522.6139 | 483.6174 | 450.8294 | 393.7258
1178.6135 | 522.7589 | 483.7839 | 450.6374 | 393.9429
1179.6135 | 522.8233 | 483.8986 | 450.9323 | 394.162
1180.6135 | 522.9024 | 484.0458 | 451.1196 | 394.3775
1181.6135 | 522.94 | 484.1611 | 451.1483 | 394.6155
1182.6135 | 522.9551 | 484.3192 | 451.1918 | 394.8547
1183.6135 | 522.9749 | 484.4141 | 451.4319 | 395.0522
1184.6135 | 523.058 | 484.5653 | 451.1038 | 395.2711
1185.6135 | 523.0964 | 484.7255 | 451.1987 | 395.4703
1186.6135 | 523.1224 | 484.8345 | 451.4736 | 395.6783
1187.6135 | 523.1348 | 484.9616 | 451.5381 | 395.8883
1188.6135 | 523.1483 | 485.1286 | 451.4781 | 396.0994
1189.6135 | 523.2404 | 485.2921 | 451.787 | 396.3155
1190.6135 | 523.2452 | 485.4116 | 451.9027 | 396.5178
1191.6135 | 523.2774 | 485.5036 | 451.8887 | 396.7171
1192.6135 | 523.3795 | 485.5907 | 452.1395 | 396.9185
1193.6135 | 523.5639 | 485.6086 | 452.2871 | 397.1227
1194.6135 | 523.6858 | 485.6967 | 452.4446 | 397.3377
1195.6135 | 523.7 | 485.7824 | 452.6205 | 397.5456
1196.6135 | 523.7545 | 485.8408 | 452.5628 | 397.7616
1197.6135 | 523.6849 | 485.8973 | 452.4786 | 397.9684
1198.6135 | 523.534 | 485.9855 | 452.4706 | 398.1872
1199.6135 | 523.4977 | 486.0414 | 452.6682 | 398.3773
1200.6135 | 523.4173 | 486.1031 | 452.5662 | 398.5809
1201.6135 | 523.4704 | 486.1937 | 452.5598 | 398.7916
1202.6135 | 523.5287 | 486.3261 | 452.4387 | 398.9939
1203.6135 | 523.5097 | 486.4557 | 452.6421 | 399.2095
1204.6135 | 523.4967 | 486.558 | 452.7683 | 399.3799
1205.6135 | 523.4932 | 486.7572 | 452.7701 | 399.4107
1206.6135 | 523.4923 | 486.8826 | 453.1062 | 399.5281
1207.6135 | 523.5644 | 486.9811 | 453.1244 | 399.6931
1208.6135 | 523.5724 | 487.0789 | 453.2645 | 399.887
1209.6135 | 523.5092 | 487.164 | 453.3558 | 400.0794
1210.6135 | 523.5896 | 487.2633 | 453.4104 | 400.2662
1211.6135 | 523.6101 | 487.3608 | 453.3868 | 400.4876
1212.6135 | 523.7034 | 487.4225 | 453.6319 | 400.7082
1213.6135 | 523.7332 | 487.4753 | 453.9259 | 400.9415
1214.6135 | 523.8341 | 487.5547 | 453.9683 | 401.1754
1215.6135 | 523.8961 | 487.6469 | 453.9394 | 401.4074
1216.6135 | 523.9024 | 487.7098 | 454.1292 | 401.6366
1217.6135 | 523.8587 | 487.7794 | 454.2324 | 401.8509
1218.6135 | 523.7623 | 487.8501 | 454.1758 | 402.0687
1219.6135 | 523.7341 | 487.9685 | 454.3903 | 402.2723
1220.6135 | 523.8123 | 488.1074 | 454.5366 | 402.4773
1221.6135 | 523.8296 | 488.2036 | 454.7838 | 402.6901
1222.6135 | 523.8265 | 488.2406 | 454.8664 | 402.8783
1223.6135 | 523.6955 | 488.3365 | 454.6645 | 403.086
1224.6135 | 523.6397 | 488.4085 | 454.9553 | 403.2911
1225.6135 | 523.7751 | 488.4603 | 454.9905 | 403.4905
1226.6135 | 523.8626 | 488.5323 | 454.7568 | 403.7061
1227.6135 | 523.9459 | 488.6022 | 454.8661 | 403.8977
1228.6135 | 524.0882 | 488.7067 | 455.0358 | 404.0978
1229.6135 | 524.0693 | 488.8096 | 455.4115 | 404.2771
1230.6135 | 524.1571 | 488.895 | 455.1597 | 404.4702
1231.6135 | 524.2369 | 488.9848 | 455.322 | 404.6625
1232.6135 | 524.2709 | 489.03 | 455.2404 | 404.8542
1233.6135 | 524.3939 | 489.1454 | 455.0887 | 405.0367
1234.6135 | 524.5901 | 489.2115 | 455.4682 | 405.2271
1235.6135 | 524.6251 | 489.3006 | 455.7171 | 405.4112
1236.6135 | 524.6638 | 489.3889 | 455.8435 | 405.5972
1237.6135 | 524.5442 | 489.5012 | 455.8194 | 405.7771
1238.6135 | 524.4077 | 489.6169 | 455.8666 | 405.9598
1239.6135 | 524.3686 | 489.7197 | 455.948 | 406.1599
1240.6135 | 524.3151 | 489.7956 | 456.133 | 406.3493
1241.6135 | 524.2029 | 489.9345 | 455.8214 | 406.558
1242.6135 | 524.0472 | 490.0458 | 456.0459 | 406.7575
1243.6135 | 523.9353 | 490.147 | 456.1163 | 406.9626
1244.6135 | 523.7852 | 490.2894 | 456.3873 | 407.168
1245.6135 | 523.7339 | 490.3715 | 456.6283 | 407.3695
1246.6135 | 523.6538 | 490.423 | 456.798 | 407.5872
1247.6135 | 523.501 | 490.5351 | 456.9498 | 407.8344
1248.6135 | 523.429 | 490.6441 | 456.9627 | 408.05
1249.6135 | 523.2691 | 490.7594 | 456.7894 | 408.2386
1250.6135 | 523.1914 | 490.867 | 456.9696 | 408.4519
1251.6135 | 523.096 | 490.9646 | 457.1865 | 408.6463
1252.6135 | 523.0708 | 491.0435 | 457.0736 | 408.8388
1253.6135 | 523.1342 | 491.1481 | 456.957 | 409.0541
1254.6135 | 522.9739 | 491.249 | 457.165 | 409.2574
1255.6135 | 523.0224 | 491.3183 | 457.3159 | 409.4757
1256.6135 | 523.0298 | 491.3997 | 457.5153 | 409.6761
1257.6135 | 523.0465 | 491.4832 | 457.5418 | 409.892
1258.6135 | 523.0721 | 491.5279 | 457.667 | 410.0891
1259.6135 | 523.152 | 491.5693 | 457.8074 | 410.3082
1260.6135 | 523.2581 | 491.645 | 457.8238 | 410.5213
1261.6135 | 523.3389 | 491.678 | 457.9894 | 410.7248
1262.6135 | 523.4522 | 491.7294 | 457.8834 | 410.9624
1263.6135 | 523.3069 | 491.8163 | 457.936 | 411.1399
1264.6135 | 523.3632 | 491.8479 | 457.7332 | 411.3384
1265.6135 | 523.3316 | 491.8893 | 457.7975 | 411.5362
1266.6135 | 523.2545 | 491.9487 | 457.8436 | 411.7374
1267.6135 | 523.237 | 491.9892 | 458.0365 | 411.9557
1268.6135 | 523.1634 | 491.988 | 458.0757 | 412.1557
1269.6135 | 523.127 | 492.0087 | 458.3564 | 412.3816
1270.6135 | 523.1222 | 492.024 | 458.3693 | 412.6002
1271.6135 | 523.0876 | 492.0238 | 458.531 | 412.8454
1272.6135 | 522.8739 | 492.0232 | 458.401 | 413.0744
1273.6135 | 522.9633 | 491.9995 | 458.3596 | 413.2535
1274.6135 | 522.8753 | 492.0118 | 458.3449 | 413.4487
1275.6135 | 522.8147 | 492.0252 | 458.5232 | 413.6221
1276.6135 | 522.7277 | 492.0555 | 458.6514 | 413.8188
1277.6135 | 522.5822 | 492.096 | 458.7178 | 414.005
1278.6135 | 522.4523 | 492.1355 | 458.6917 | 414.2033
1279.6135 | 522.4208 | 492.1197 | 458.6973 | 414.3918
1280.6135 | 522.3529 | 492.1735 | 459.0077 | 414.7601
1281.6135 | 522.2512 | 492.1963 | 459.229 | 414.9302
1282.6135 | 522.283 | 492.1986 | 458.8979 | 414.986
1283.6135 | 522.3042 | 492.2891 | 459.1372 | 415.183
1284.6135 | 522.2079 | 492.3346 | 459.1887 | 415.3832
1285.6135 | 522.1644 | 492.3743 | 459.3571 | 415.5742
1286.6135 | 522.1582 | 492.4452 | 459.543 | 415.766
1287.6135 | 522.089 | 492.5147 | 459.6503 | 415.9635
1288.6135 | 521.9651 | 492.547 | 459.6117 | 416.1625
1289.6292 | 521.9951 | 492.5681 | 459.5667 | 416.3612
1290.6135 | 522.0024 | 492.6843 | 459.3584 | 416.5542
1291.6135 | 522.0348 | 492.7157 | 459.4146 | 416.7498
1292.6135 | 522.0525 | 492.7914 | 459.6589 | 416.9404
1293.6135 | 522.1272 | 492.8501 | 459.8165 | 417.1227
1294.6135 | 522.0995 | 492.9325 | 459.8962 | 417.3208
1295.6135 | 522.1432 | 492.9439 | 460.1259 | 417.5043
1296.6135 | 522.2161 | 492.9601 | 459.9739 | 417.713
1297.6135 | 522.1673 | 493.0121 | 460.1522 | 417.903
1298.6135 | 522.2608 | 493.0917 | 460.3272 | 418.0921
1299.6135 | 522.3675 | 493.1269 | 460.4507 | 418.2817
1300.6135 | 522.4696 | 493.1887 | 460.4067 | 418.4752
1301.6135 | 522.5319 | 493.2615 | 460.1559 | 418.6675
1302.6135 | 522.5756 | 493.2829 | 460.4219 | 418.8523
1303.6135 | 522.4537 | 493.3653 | 460.6197 | 419.0441
1304.6135 | 522.485 | 493.3935 | 460.8022 | 419.224
1305.6135 | 522.6594 | 493.4776 | 460.7336 | 419.4168
1306.6135 | 522.7086 | 493.5162 | 461.006 | 419.594
1307.6135 | 522.7669 | 493.5575 | 461.1231 | 419.7831
1308.6135 | 522.9239 | 493.5971 | 460.9874 | 419.9678
1309.6135 | 523.0494 | 493.604 | 460.967 | 420.1511
1310.6135 | 523.1366 | 493.5932 | 460.9373 | 420.3407
1311.6135 | 523.0116 | 493.5798 | 460.8322 | 420.5232
1312.6135 | 523.0723 | 493.569 | 460.8818 | 420.6944
1313.6135 | 523.0456 | 493.5388 | 460.8892 | 420.8755
1314.6135 | 523.1278 | 493.5307 | 460.9721 | 421.053
1315.6135 | 522.9736 | 493.5546 | 461.1071 | 421.2137
1316.6135 | 522.95 | 493.5154 | 461.3822 | 421.3917
1317.6135 | 522.9544 | 493.5086 | 461.4169 | 421.5653
1318.6135 | 522.9273 | 493.5908 | 461.3143 | 421.727
1319.6135 | 522.7934 | 493.6301 | 461.5122 | 421.9192
1320.6135 | 522.7906 | 493.7199 | 461.5948 | 422.0757
1321.6135 | 522.8619 | 493.8204 | 461.7867 | 422.2454
1322.6135 | 522.8513 | 493.9076 | 461.8234 | 422.4072
1323.6135 | 522.7362 | 493.95 | 461.8795 | 422.5593
1324.6135 | 522.6675 | 493.9964 | 462.0429 | 422.7226
1325.6135 | 522.6803 | 494.0524 | 462.1346 | 422.8875
1326.6135 | 522.7021 | 494.1758 | 462.2038 | 423.0571
1327.6135 | 522.7297 | 494.2929 | 462.0347 | 423.2271
1328.6135 | 522.7802 | 494.3518 | 462.4157 | 423.3881
1329.6135 | 522.8973 | 494.4189 | 462.5955 | 423.529
1330.6135 | 522.9822 | 494.4069 | 462.5635 | 423.6975
1331.6135 | 523.0767 | 494.5387 | 462.4967 | 423.8471
1332.6135 | 523.027 | 494.6755 | 462.1177 | 424.0189
1333.6135 | 522.9449 | 494.7446 | 462.267 | 424.1859
1334.6135 | 522.867 | 494.7374 | 462.3453 | 424.3368
1335.6135 | 522.9461 | 494.8729 | 462.4401 | 424.503
1336.6135 | 522.8999 | 494.985 | 462.7275 | 424.6605
1337.6135 | 522.7963 | 495.0539 | 462.8242 | 424.8205
1338.6135 | 522.7955 | 495.1169 | 462.7107 | 425.2355
1339.6135 | 522.9143 | 495.1918 | 462.7467 | 425.4423
1340.6135 | 522.963 | 495.1948 | 462.9572 | 425.5937
1341.6135 | 523.0534 | 495.132 | 462.894 | 425.598
1342.6135 | 523.0566 | 495.1545 | 462.8171 | 425.6752
1343.6135 | 523.0363 | 495.1738 | 462.8647 | 425.8084
1344.6135 | 522.9654 | 495.1512 | 462.9683 | 425.9658
1345.6135 | 522.8601 | 495.1831 | 463.2117 | 426.1205
1346.6135 | 522.7299 | 495.2019 | 463.029 | 426.2873
1347.6135 | 522.6168 | 495.1965 | 463.0856 | 426.4383
1348.6135 | 522.4934 | 495.1937 | 463.2464 | 426.5987
1349.6135 | 522.4353 | 495.2075 | 463.1035 | 426.746
1350.6135 | 522.3709 | 495.2631 | 463.2594 | 426.9056
1351.6135 | 522.3874 | 495.31 | 463.4414 | 427.0607
1352.6135 | 522.4412 | 495.299 | 463.5317 | 427.213
1353.6135 | 522.4732 | 495.3606 | 463.786 | 427.3557
1354.6135 | 522.5622 | 495.4325 | 463.8029 | 427.502
1355.6135 | 522.6408 | 495.4838 | 463.8293 | 427.6657
1356.6135 | 522.7382 | 495.4957 | 463.7939 | 427.8233
1357.6135 | 522.6818 | 495.5811 | 463.6985 | 427.9879
1358.6135 | 522.6009 | 495.5488 | 463.8375 | 428.153
1359.6135 | 522.4912 | 495.4843 | 463.8185 | 428.3131
1360.6135 | 522.3136 | 495.5448 | 463.8003 | 428.4863
1361.6135 | 522.0595 | 495.574 | 463.9698 | 428.6515
1362.6135 | 521.9301 | 495.5613 | 463.9923 | 428.8196
1363.6135 | 521.9154 | 495.5704 | 464.2119 | 428.9859
1364.6135 | 521.9485 | 495.5951 | 464.2898 | 429.1578
1365.6135 | 522.0745 | 495.5663 | 464.3434 | 429.3377
1366.6135 | 522.1851 | 495.5818 | 464.462 | 429.4854
1367.6135 | 522.319 | 495.5896 | 464.4606 | 429.6738
1368.6135 | 522.4291 | 495.6591 | 464.5853 | 429.8411
1369.6135 | 522.5 | 495.6957 | 464.7073 | 430.0124
1370.6135 | 522.4743 | 495.7419 | 464.7616 | 430.1764
1371.6135 | 522.332 | 495.7601 | 464.8689 | 430.3437
1372.6135 | 522.3079 | 495.7934 | 464.8889 | 430.5086
1373.6135 | 522.5429 | 495.8005 | 465.0175 | 430.6703
1374.6135 | 522.6215 | 495.8524 | 465.1516 | 430.842
1375.6135 | 522.6894 | 495.8397 | 465.1733 | 431.0087
1376.6135 | 522.8142 | 495.8711 | 465.2345 | 431.1794
1377.6135 | 522.7809 | 495.9353 | 465.2728 | 431.3531
1378.6135 | 522.7843 | 495.9421 | 465.0897 | 431.5664
1379.6135 | 522.787 | 496.012 | 465.0049 | 432.0845
1380.6135 | 522.7424 | 496.0255 | 465.1288 | 432.0981
1381.6135 | 522.8496 | 496.08 | 465.2392 | 432.2188
1382.6135 | 522.7422 | 496.1256 | 465.1823 | 432.3397
1383.6135 | 522.7229 | 496.1523 | 465.0069 | 432.4754
1384.6135 | 522.6745 | 496.2143 | 464.9174 | 432.5803
1385.6135 | 522.5936 | 496.2284 | 464.8061 | 432.6596
1386.6135 | 522.7218 | 496.3122 | 465.2415 | 432.8131
1387.6135 | 522.6215 | 496.3519 | 465.4886 | 432.9873
1388.6135 | 522.5901 | 496.3966 | 465.2425 | 433.1575
1389.6135 | 522.6922 | 496.4131 | 465.572 | 433.3695
1390.6135 | 522.8522 | 496.4286 | 465.5995 | 433.6637
1391.6135 | 522.9357 | 496.3933 | 465.5111 | 433.8561
1392.6135 | 522.9501 | 496.3431 | 465.5377 | 434.055
1393.6135 | 522.8952 | 496.3222 | 465.7226 | 434.1678
1394.6135 | 522.9378 | 496.3289 | 465.7568 | 434.2957
1395.6135 | 522.8973 | 496.3278 | 465.8628 | 434.4543
1396.6135 | 522.8734 | 496.3486 | 466.0738 | 434.6141
1397.6135 | 522.7623 | 496.3812 | 466.1125 | 434.7577
1398.6135 | 522.7532 | 496.4122 | 466.1459 | 434.9375
1399.6135 | 522.6019 | 496.4708 | 466.2631 | 435.1068
1400.6135 | 522.515 | 496.5173 | 466.0067 | 435.3463
1401.6135 | 522.5465 | 496.5618 | 466.2201 | 435.4388
1402.6135 | 522.5084 | 496.6096 | 466.3579 | 435.5406
1403.6135 | 522.4262 | 496.6388 | 466.3866 | 435.665
1404.6135 | 522.4671 | 496.7049 | 466.1171 | 435.8446
1405.6135 | 522.3365 | 496.7454 | 466.4035 | 435.9911
1406.6135 | 522.2257 | 496.7391 | 466.2789 | 436.1519
1407.6135 | 522.1752 | 496.7958 | 466.3417 | 436.2806
1408.6135 | 522.1815 | 496.8582 | 466.5455 | 436.4425
1409.6135 | 522.1775 | 496.8908 | 466.7119 | 436.5894
1410.6135 | 522.0629 | 496.9152 | 466.5699 | 436.7502
1411.6135 | 522.0272 | 496.9687 | 466.634 | 436.886
1412.6135 | 522.1416 | 496.9891 | 466.7391 | 437.0328
1413.6135 | 522.1346 | 497.0036 | 466.5698 | 437.1684
1414.6135 | 522.2182 | 497.0021 | 466.8148 | 437.3064
1415.6135 | 522.1478 | 496.987 | 466.9251 | 437.4257
1416.6135 | 522.0714 | 496.9802 | 466.9107 | 437.558
1417.6135 | 522.1027 | 496.9511 | 467.0858 | 437.8637
1418.6135 | 522.1193 | 496.9132 | 467.1847 | 437.7588
1419.6135 | 522.1097 | 496.9511 | 467.357 | 437.9136
1420.6135 | 522.19 | 496.9733 | 467.2684 | 438.0429
1421.6135 | 522.2012 | 497.0128 | 467.0455 | 438.1877
1422.6135 | 522.1186 | 497.0426 | 466.9088 | 438.3065
1423.6135 | 522.1174 | 497.0096 | 467.026 | 438.432
1424.6135 | 522.1555 | 496.9737 | 466.8314 | 438.5538
1425.6135 | 522.2256 | 496.9283 | 467.1817 | 438.6717
1426.6135 | 522.3038 | 496.8102 | 467.3694 | 438.8039
1427.6135 | 522.3875 | 496.7627 | 467.2588 | 438.9056
1428.6135 | 522.5171 | 496.7574 | 467.2158 | 438.9444
1429.6135 | 522.627 | 496.7598 | 467.3233 | 439.0587
1430.6135 | 522.7757 | 496.7547 | 467.5245 | 439.1372
1431.6135 | 522.763 | 496.7626 | 467.2737 | 439.2725
1432.6135 | 522.8019 | 496.7594 | 467.2603 | 439.3521
1433.6135 | 522.928 | 496.7641 | 467.4255 | 439.4382
1434.6135 | 522.862 | 496.8196 | 467.5318 | 439.525
1435.6135 | 522.9432 | 496.8483 | 467.7195 | 439.5962
1436.6135 | 522.9753 | 496.8621 | 467.7565 | 439.7106
1437.6135 | 522.9591 | 496.873 | 467.7275 | 439.8438
1438.6135 | 522.9786 | 496.9447 | 467.8347 | 439.9215
1439.6135 | 522.9325 | 496.9649 | 468.0038 | 440.0118
1440.6135 | 522.9519 | 497.0073 | 468.1699 | 439.9958
1441.6135 | 523.1051 | 497.0282 | 468.2893 | 440.0907
1442.6135 | 523.2132 | 497.1164 | 468.3213 | 440.2072
1443.6135 | 523.0609 | 497.1773 | 468.2051 | 440.2808
1444.6135 | 523.0222 | 497.2241 | 468.2377 | 440.3664
1445.6135 | 523.0777 | 497.2731 | 468.3289 | 440.4619
1446.6135 | 523.1561 | 497.2739 | 468.2471 | 440.5605
1447.6135 | 523.2269 | 497.3231 | 468.0373 | 440.6776
1448.6135 | 523.2949 | 497.3749 | 468.2645 | 440.7961
1449.6135 | 523.3778 | 497.4071 | 468.5674 | 441.2531
1450.6135 | 523.4802 | 497.4026 | 468.5048 | 441.3692
1451.6135 | 523.5806 | 497.443 | 468.3236 | 441.5904
1452.6135 | 523.737 | 497.4855 | 468.5054 | 441.5995
1453.6135 | 523.8387 | 497.5393 | 468.6579 | 441.6189
1454.6135 | 523.8066 | 497.588 | 468.7587 | 441.3344
1455.6135 | 523.958 | 497.6448 | 468.8752 | 441.9132
1456.6135 | 524.0283 | 497.6801 | 468.7782 | 441.9464
1457.6135 | 523.9551 | 497.727 | 468.8013 | 442.3005
1458.6135 | 523.9139 | 497.706 | 468.741 | 442.3987
1459.6135 | 523.8964 | 497.6776 | 468.8542 | 442.045
1460.6135 | 523.8149 | 497.6972 | 469.048 | 442.5441
1461.6135 | 523.7106 | 497.7623 | 469.101 | 442.6822
1462.6135 | 523.617 | 497.7959 | 468.9744 | 442.776
1463.6135 | 523.4179 | 497.8282 | 469.0593 | 442.3898
1464.6135 | 523.4242 | 497.867 | 469.0749 | 442.4919
1465.6135 | 523.4251 | 497.9385 | 469.149 | 442.3277
1466.6135 | 523.3561 | 498.0007 | 469.1832 | 442.2239
1467.6135 | 523.2352 | 498.113 | 469.3155 | 442.3552
1468.6135 | 523.2218 | 498.1475 | 469.5399 | 442.3854
1469.6135 | 523.2663 | 498.1302 | 469.6561 | 442.4443
1470.6135 | 523.2377 | 498.1097 | 469.6861 | 442.5782
1471.6135 | 523.2723 | 498.0596 | 469.658 | 442.5478
1472.6135 | 523.3478 | 498.0666 | 469.8487 | 443.0148
1473.6135 | 523.3482 | 498.1338 | 469.9471 | 442.8322
1474.6135 | 523.3185 | 498.193 | 469.9064 | 442.7623
1475.6135 | 523.3143 | 498.2807 | 469.941 | 442.8917
1476.6135 | 523.2762 | 498.2972 | 470.0333 | 442.9895
1477.6135 | 523.2449 | 498.2922 | 470.1798 | 443.0449
1478.6135 | 523.1904 | 498.2974 | 469.9402 | 443.0567
1479.6135 | 523.0555 | 498.3065 | 470.1115 | 443.1352
1480.6135 | 522.9968 | 498.3377 | 470.0417 | 443.2309
1481.6135 | 522.9428 | 498.4156 | 470.0586 | 443.314
1482.6135 | 522.7915 | 498.5005 | 470.1174 | 443.4189
1483.6135 | 522.7048 | 498.623 | 470.1944 | 443.3498
1484.6135 | 522.7631 | 498.7158 | 470.0214 | 443.2822
1485.6135 | 522.6977 | 498.7808 | 470.0793 | 443.364
1486.6135 | 522.7619 | 498.9033 | 469.895 | 443.4483
1487.6135 | 522.8474 | 499.0393 | 470.0015 | 443.5639
1488.6135 | 522.8386 | 499.1476 | 470.0127 | 443.6625
1489.6135 | 522.7622 | 499.3032 | 470.0217 | 443.7515
1490.6135 | 522.711 | 499.4208 | 469.9942 | 443.7693
1491.6135 | 522.75 | 499.5102 | 470.139 | 443.7931
1492.6135 | 522.7042 | 499.6074 | 470.3266 | 443.9882
1493.6135 | 522.5757 | 499.6913 | 470.4355 | 444.226
1494.6135 | 522.5346 | 499.7294 | 470.6324 | 445.1241
1495.6135 | 522.6856 | 499.6875 | 470.661 | 445.1579
1496.6135 | 522.791 | 499.6653 | 470.6481 | 444.4332
1497.6135 | 522.6987 | 499.6255 | 470.6609 | 444.336
1498.6135 | 522.6821 | 499.5792 | 470.6803 | 444.3348
1499.6135 | 522.6086 | 499.5282 | 470.5974 | 444.3996
1500.6135 | 522.5458 | 499.5055 | 470.5697 | 444.4966
1501.6135 | 522.5842 | 499.5064 | 470.4792 | 444.5687
1502.6135 | 522.657 | 499.5423 | 470.5296 | 444.6796
1503.6135 | 522.6317 | 499.5471 | 470.5161 | 444.5849
1504.6135 | 522.7316 | 499.6146 | 470.742 | 444.7337
1505.6135 | 522.7675 | 499.6877 | 470.8799 | 444.7564
1506.6135 | 522.7208 | 499.7076 | 470.8644 | 444.7728
1507.6135 | 522.7455 | 499.7385 | 470.9566 | 444.8282
1508.6135 | 522.6833 | 499.8372 | 470.8918 | 444.8593
1509.6135 | 522.7573 | 499.854 | 470.9123 | 444.9274
1510.6135 | 522.8523 | 499.8503 | 470.8531 | 445.0075
1511.6135 | 523.0341 | 499.8977 | 470.9989 | 445.1321
1512.6135 | 523.1175 | 499.9413 | 470.8923 | 445.2228
1513.6135 | 523.0703 | 499.9475 | 471.0611 | 445.2395
1514.6135 | 523.1004 | 499.9804 | 471.2853 | 445.2854
1515.6135 | 523.251 | 499.9536 | 471.2886 | 445.213
1516.6135 | 523.3819 | 500.0186 | 471.1413 | 445.2664
1517.6135 | 523.4474 | 500.0119 | 470.974 | 445.4169
1518.6135 | 523.4801 | 500.0108 | 471.0852 | 445.2905
1519.6135 | 523.503 | 500.0756 | 471.2229 | 445.2506
1520.6135 | 523.4758 | 500.0323 | 471.2013 | 445.3346
1521.6135 | 523.6225 | 499.952 | 471.2853 | 445.3561
1522.6135 | 523.7838 | 500.0133 | 471.1586 | 445.412
1523.6135 | 523.7495 | 500.0462 | 471.1973 | 445.4351
1524.6135 | 523.727 | 500.1238 | 471.3676 | 445.5315
1525.6135 | 523.8143 | 500.236 | 471.587 | 445.5841
1526.6135 | 524.0095 | 500.2502 | 471.5511 | 445.6024
1527.6135 | 524.0933 | 500.4087 | 471.6746 | 445.6356
1528.6135 | 524.0523 | 500.5041 | 471.8041 | 445.6703
1529.6135 | 524.1732 | 500.5877 | 471.8722 | 445.774
1530.6135 | 524.244 | 500.6924 | 471.8886 | 445.8107
1531.6135 | 524.195 | 500.7975 | 471.8862 | 446.1243
1532.6135 | 524.2133 | 500.8979 | 471.7957 | 446.2865
1533.6135 | 524.1105 | 501.0305 | 471.841 | 446.3709
1534.6135 | 524.0247 | 501.1384 | 472.0096 | 446.3461
1535.6135 | 524.0912 | 501.2336 | 472.0245 | 446.3287
1536.6135 | 524.0495 | 501.2932 | 472.2169 | 446.5145
1537.6135 | 524.0854 | 501.2896 | 472.1298 | 446.7153
1538.6135 | 524.0994 | 501.2263 | 472.2125 | 447.747
1539.6135 | 524.152 | 501.1969 | 472.1545 | 447.7728
1540.6135 | 523.9273 | 501.1913 | 472.2327 | 447.8463
1541.6135 | 523.8917 | 501.1247 | 472.3152 | 447.9266
1542.6135 | 523.8964 | 500.9915 | 472.5284 | 447.982
1543.6135 | 523.9551 | 501.0394 | 472.4941 | 448.0164
1544.6135 | 523.9956 | 501.0687 | 472.5979 | 447.0421
1545.6135 | 524.0213 | 501.0106 | 472.5441 | 447.8892
1546.6135 | 524.0306 | 501.1599 | 472.5307 | 447.3286
1547.6135 | 524.1088 | 501.1979 | 472.6501 | 447.1435
1548.6135 | 524.1172 | 501.3316 | 472.785 | 446.9984
1549.6135 | 524.2254 | 501.4031 | 472.8524 | 446.8996
1550.6135 | 524.3226 | 501.4766 | 472.7912 | 446.9806
1551.6135 | 524.4598 | 501.5784 | 472.9313 | 446.8212
1552.6135 | 524.3636 | 501.6166 | 473.0255 | 446.8836
1553.6135 | 524.275 | 501.6517 | 473.0992 | 446.9911
1554.6135 | 524.0533 | 501.7049 | 473.0641 | 446.9923
1555.6135 | 523.8206 | 501.7564 | 473.0662 | 446.9407
1556.6135 | 523.695 | 501.8285 | 472.9261 | 446.8771
1557.6135 | 523.71 | 501.8621 | 472.7166 | 446.8452
1558.6135 | 523.7691 | 501.8788 | 472.6744 | 446.708
1559.6135 | 523.7592 | 501.9342 | 472.5621 | 446.7383
1560.6135 | 523.8161 | 501.9649 | 472.8959 | 446.7697
1561.6135 | 523.8377 | 501.9944 | 472.9512 | 446.8244
1562.6135 | 523.7438 | 502.0344 | 473.0748 | 446.7045
1563.6135 | 523.8066 | 502.0377 | 473.1205 | 446.6372
1564.6135 | 523.7324 | 502.0916 | 473.1391 | 446.5011
1565.6135 | 523.6837 | 502.0964 | 473.2399 | 446.3802
1566.6135 | 523.7102 | 502.1402 | 473.1514 | 446.2645
1567.6135 | 523.7215 | 502.2002 | 473.292 | 446.1702
1568.6135 | 523.6533 | 502.249 | 473.3804 | 446.0162
1569.6135 | 523.7352 | 502.2842 | 473.4169 | 445.9072
1570.6135 | 523.8716 | 502.2996 | 473.3428 | 445.942
1571.6135 | 523.8184 | 502.3406 | 473.3074 | 445.9445
1572.6135 | 523.7993 | 502.3597 | 473.439 | 445.8348
1573.6135 | 523.835 | 502.4257 | 473.4821 | 445.6598
1574.6135 | 523.9587 | 502.4625 | 473.5409 | 445.5483
1575.6135 | 523.9452 | 502.5065 | 473.5456 | 445.5743
1576.6135 | 523.9789 | 502.4884 | 473.7103 | 445.4747
1577.6135 | 524.0015 | 502.5212 | 473.8089 | 445.3568
1578.6135 | 524.0401 | 502.5085 | 473.5081 | 445.3416
1579.6135 | 524.1517 | 502.5443 | 473.4947 | 445.1761
1580.6135 | 524.2288 | 502.5428 | 473.7456 | 445.1522
1581.6135 | 524.1293 | 502.5939 | 473.9886 | 445.1103
1582.6135 | 524.1347 | 502.6035 | 473.6077 | 445.1114
1583.6135 | 524.1379 | 502.6126 | 473.61 | 444.9244
1584.6135 | 524.0759 | 502.6896 | 473.8175 | 444.8532
1585.6135 | 524.0478 | 502.7653 | 473.9856 | 444.8572
1586.6135 | 523.9605 | 502.768 | 474.1424 | 444.8023
1587.6135 | 523.8464 | 502.8253 | 474.2491 | 444.816
1588.6135 | 523.8529 | 502.8697 | 474.2194 | 444.7944
1589.6135 | 523.945 | 502.923 | 474.3634 | 444.6776
1590.6135 | 524.0243 | 502.9393 | 474.3971 | 444.7084
1591.6135 | 524.0495 | 502.9543 | 474.2034 | 444.4504
1592.6135 | 524.0887 | 502.9757 | 474.0354 | 444.1813
1593.6135 | 524.2115 | 503.0352 | 473.9025 | 444.083
1594.6135 | 524.2743 | 503.088 | 474.0379 | 443.9462
1595.6135 | 524.2107 | 503.1017 | 474.3009 | 443.9467
1596.6135 | 524.2177 | 503.134 | 474.5545 | 443.7846
1597.6135 | 524.2168 | 503.182 | 474.6434 | 443.6523
1598.6135 | 524.159 | 503.2702 | 474.2656 | 443.5811
1599.6135 | 524.182 | 503.312 | 474.3413 | 443.6368
1600.6135 | 524.1974 | 503.2917 | 474.4767 | 443.7111
1601.6135 | 524.1775 | 503.3005 | 474.3634 | 443.786
1602.6135 | 524.2991 | 503.3176 | 474.4805 | 443.6126
1603.6135 | 524.2807 | 503.3246 | 474.7021 | 443.5637
1604.6135 | 524.2695 | 503.3947 | 474.803 | 443.6341
1605.6135 | 524.1053 | 503.4059 | 474.939 | 443.5733
1606.6135 | 524.1956 | 503.4912 | 474.9801 | 443.7193
1607.6135 | 524.253 | 503.5911 | 475.0325 | 443.6896
1608.6135 | 524.2068 | 503.6311 | 474.975 | 443.8635
1609.6135 | 524.0533 | 503.6995 | 474.973 | 443.7958
1610.6135 | 523.9818 | 503.7887 | 474.833 | 443.9029
1611.6135 | 523.8605 | 503.833 | 474.9842 | 443.8527
1612.6135 | 523.8272 | 503.8852 | 475.0399 | 444.3171
1613.6135 | 523.8291 | 503.9674 | 475.2266 | 444.1595
1614.6135 | 523.7705 | 503.9832 | 475.2327 | 444.0996
1615.6135 | 523.7672 | 504.0584 | 475.0918 | 444.0709
1616.6135 | 523.79 | 504.1226 | 474.9246 | 443.9669
1617.6135 | 523.8166 | 504.1866 | 475.0927 | 444.0127
1618.6135 | 523.8321 | 504.2552 | 475.2485 | 444.0048
1619.6135 | 523.7778 | 504.3169 | 475.3145 | 443.9715
1620.6135 | 523.7031 | 504.3731 | 475.4976 | 443.9818
1621.6135 | 523.6675 | 504.3914 | 475.5504 | 444.1542
1622.6135 | 523.7645 | 504.4323 | 475.2456 | 443.9988
1623.6135 | 523.7115 | 504.4621 | 475.2738 | 444.0803
1624.6135 | 523.7857 | 504.4863 | 475.3499 | 443.6639
1625.6135 | 523.6939 | 504.4822 | 475.1427 | 442.682
1626.6135 | 523.6894 | 504.4459 | 475.2408 | 441.8441
1627.6135 | 523.7644 | 504.432 | 475.5881 | 441.5417
1628.6135 | 523.8185 | 504.3691 | 475.7012 | 441.2527
1629.6135 | 523.7769 | 504.3812 | 475.7178 | 441.4693
1630.6135 | 523.7091 | 504.3765 | 475.6134 | 441.0767
1631.6135 | 523.6623 | 504.3923 | 475.6678 | 441.1797
1632.6135 | 523.7153 | 504.4053 | 475.69 | 441.1662
1633.6135 | 523.717 | 504.3824 | 475.5305 | 441.2099
1634.6135 | 523.8197 | 504.4029 | 475.746 | 441.4586
1635.6135 | 523.8235 | 504.3866 | 475.6083 | 441.3873
1636.6135 | 523.7647 | 504.447 | 475.5888 | 441.4413
1637.6135 | 523.7512 | 504.5054 | 475.572 | 441.5355
1638.6135 | 523.6886 | 504.5748 | 475.7018 | 441.5112
1639.6135 | 523.6592 | 504.5918 | 475.7182 | 441.6182
1640.6135 | 523.7085 | 504.6332 | 475.8294 | 441.6653
1641.6135 | 523.7545 | 504.6171 | 475.9379 | 441.7637
1642.6135 | 523.7751 | 504.5714 | 475.9532 | 441.7635
1643.6135 | 523.9061 | 504.6197 | 475.9066 | 441.9915
1644.6135 | 523.8942 | 504.6782 | 476.0995 | 441.883
1645.6135 | 523.9391 | 504.6697 | 476.2249 | 441.8937
1646.6135 | 524.0748 | 504.696 | 476.2687 | 442.0049
1647.6135 | 524.2938 | 504.7451 | 476.3057 | 442.1395
1648.6135 | 524.253 | 504.7606 | 476.3253 | 442.0806
1649.6135 | 524.2501 | 504.7384 | 476.3019 | 442.1458
1650.6135 | 524.2187 | 504.697 | 476.2075 | 442.2486
1651.6135 | 524.347 | 504.7158 | 475.985 | 442.1199
1652.6135 | 524.2821 | 504.7066 | 476.1738 | 437.7673
1653.6135 | 524.1154 | 504.6929 | 476.1879 | 441.5136
1654.6135 | 524.0887 | 504.7142 | 476.2205 | 441.9342
1655.6135 | 524.0125 | 504.7642 | 476.0801 | 441.9404
1656.6135 | 523.942 | 504.7979 | 476.0507 | 441.8636
1657.6135 | 523.9159 | 504.8063 | 476.2594 | 441.8568
1658.6135 | 523.9107 | 504.8307 | 476.3889 | 441.8583
1659.6135 | 523.7754 | 504.8849 | 476.3643 | 441.917
1660.6135 | 523.7508 | 504.9196 | 476.5214 | 442.7713
1661.6135 | 523.7486 | 504.9545 | 476.5996 | 442.0687
1662.6135 | 523.6267 | 505.0137 | 476.5332 | 442.5467
1663.6135 | 523.612 | 505.0727 | 476.5304 | 442.7607
1664.6135 | 523.5928 | 505.0992 | 476.5745 | 443.0235
1665.6135 | 523.6076 | 505.1222 | 476.3671 | 443.0489
1666.6135 | 523.5737 | 505.1656 | 476.2345 | 442.9198
1667.6135 | 523.5108 | 505.164 | 476.3724 | 442.9832
1668.6135 | 523.4894 | 505.1978 | 476.2185 | 443.119
1669.6135 | 523.3939 | 505.2333 | 476.3829 | 442.9971
1670.6135 | 523.2691 | 505.3 | 476.2588 | 443.0855
1671.6135 | 523.2105 | 505.288 | 475.9473 | 443.102
1672.6135 | 523.1794 | 505.3206 | 476.1382 | 443.3366
1673.6135 | 523.21 | 505.3427 | 476.4093 | 443.3552
1674.6135 | 523.2691 | 505.3045 | 476.363 | 443.2783
1675.6135 | 523.2863 | 505.3549 | 476.5371 | 443.4669
1676.6135 | 523.2296 | 505.3727 | 476.6789 | 443.4522
1677.6135 | 523.2242 | 505.3555 | 476.6228 | 443.8278
1678.6135 | 523.2314 | 505.3848 | 476.4763 | 443.897
1679.6135 | 523.1676 | 505.3929 | 476.4754 | 443.9264
1680.6135 | 523.1178 | 505.3824 | 476.675 | 444.1776
1681.6135 | 523.0382 | 505.4035 | 476.7939 | 444.2138
1682.6135 | 523.0884 | 505.3814 | 476.5962 | 444.3229
1683.6135 | 523.1557 | 505.384 | 476.6756 | 444.5437
1684.6135 | 523.0808 | 505.3717 | 476.8707 | 444.7162
1685.6135 | 523.1139 | 505.345 | 476.7346 | 444.8914
1686.6135 | 523.173 | 505.3661 | 476.6044 | 444.909
1687.6135 | 523.1913 | 505.3429 | 476.616 | 445.1245
1688.6135 | 523.1611 | 505.3304 | 476.7025 | 445.1625
1689.6135 | 523.1656 | 505.3077 | 476.8271 | 445.2578
1690.6135 | 523.1514 | 505.2859 | 476.6169 | 445.1774
1691.6135 | 523.1702 | 505.3318 | 476.512 | 445.202
1692.6135 | 523.1187 | 505.3408 | 476.5333 | 445.2579
1693.6135 | 523.075 | 505.3503 | 476.6886 | 445.2861
1694.6135 | 523.0444 | 505.376 | 476.6646 | 445.2558
1695.6135 | 523.0622 | 505.4004 | 476.7728 | 445.4066
1696.6135 | 523.0183 | 505.4399 | 476.9117 | 445.5523
1697.6135 | 522.977 | 505.4514 | 476.9165 | 445.7128
1698.6135 | 522.8792 | 505.449 | 477.0248 | 445.654
1699.6135 | 522.8996 | 505.4426 | 477.0126 | 445.826
1700.6135 | 522.9912 | 505.484 | 476.9579 | 445.7762
1701.6135 | 522.9771 | 505.4269 | 477.093 | 445.9237
1702.6135 | 522.9835 | 505.3918 | 477.1872 | 445.9553
1703.6135 | 523.0265 | 505.4152 | 477.2609 | 446.1571
1704.6135 | 523.0362 | 505.4348 | 477.1364 | 446.236
1705.6135 | 522.8877 | 505.4392 | 477.0688 | 446.441
1706.6135 | 522.8841 | 505.4595 | 477.13 | 446.4377
1707.6135 | 522.825 | 505.4177 | 477.2351 | 446.4377
1708.6135 | 522.824 | 505.4109 | 477.2408 | 446.6442
1709.6135 | 522.826 | 505.4368 | 477.0198 | 446.6059
1710.6135 | 522.7418 | 505.461 | 477.1693 | 446.7517
1711.6135 | 522.6541 | 505.4883 | 477.2943 | 446.8285
1712.6135 | 522.6452 | 505.4822 | 477.3067 | 446.8427
1713.6135 | 522.7069 | 505.4204 | 477.3186 | 447.0502
1714.6135 | 522.7574 | 505.4484 | 477.2116 | 447.0753
1715.6135 | 522.8288 | 505.5071 | 476.6604 | 446.9663
1716.6135 | 522.7047 | 505.5373 | 476.6186 | 447.0482
1717.6135 | 522.7863 | 505.559 | 476.9349 | 447.0464
1718.6135 | 522.8881 | 505.5756 | 477.037 | 447.4112
1719.6135 | 522.91 | 505.527 | 476.7845 | 447.3249
1720.6135 | 522.8359 | 505.5783 | 476.9911 | 447.4479
1721.6135 | 522.9178 | 505.5667 | 477.1387 | 447.3905
1722.6135 | 523.0368 | 505.6442 | 477.166 | 447.5389
1723.6135 | 522.9331 | 505.6949 | 477.2495 | 447.5476
1724.6135 | 523.0557 | 505.6974 | 477.3286 | 447.7083
1725.6135 | 523.2049 | 505.7186 | 477.3047 | 447.6895
1726.6135 | 523.0864 | 505.7167 | 477.3385 | 447.6676
1727.6135 | 523.1093 | 505.6944 | 477.3819 | 448.0016
1728.6135 | 523.126 | 505.7449 | 477.3965 | 450.1923
1729.6135 | 523.2866 | 505.7728 | 477.3798 | 452.3405
1730.6135 | 523.4025 | 505.7226 | 477.1423 | 452.3154
1731.6135 | 523.5205 | 505.7629 | 477.2565 | 452.1774
1732.6135 | 523.5067 | 505.7965 | 477.3777 | 448.1642
1733.6135 | 523.5411 | 505.8209 | 477.5988 | 448.2396
1734.6135 | 523.5428 | 505.8293 | 477.6803 | 448.068
1735.6135 | 523.3784 | 505.8583 | 477.5663 | 448.2195
1736.6135 | 523.4354 | 505.8315 | 477.5797 | 448.303
1737.6135 | 523.3399 | 505.843 | 477.2807 | 448.4513
1738.6135 | 523.4087 | 505.874 | 477.2703 | 448.4963
1739.6135 | 523.372 | 505.866 | 477.4434 | 448.3461
1740.6135 | 523.3193 | 505.8399 | 477.4882 | 448.6728
1741.6135 | 523.2685 | 505.8808 | 477.5485 | 448.8274
1742.6135 | 523.2772 | 505.9095 | 477.6342 | 448.9167
1743.6135 | 523.3555 | 505.9187 | 477.4647 | 470.5066
1744.6135 | 523.2335 | 505.8821 | 477.4893 | 481.9755
1745.6135 | 523.2688 | 505.7166 | 477.5867 | 481.8587
1746.6135 | 523.2343 | 505.6117 | 477.6532 | 482.0349
1747.6135 | 523.1804 | 505.5236 | 477.7626 | 482.5539
1748.6135 | 523.2406 | 505.4647 | 477.7158 | 482.4001
1749.6135 | 523.2379 | 505.3866 | 477.708 | 482.9765
1750.6135 | 523.225 | 505.3113 | 477.695 | 483.4323
1751.6135 | 523.3037 | 505.2543 | 477.6477 | 483.5601
1752.6135 | 523.3962 | 505.2401 | 477.6925 | 483.2846
1753.6135 | 523.503 | 505.2006 | 477.7432 | 483.5514
1754.6135 | 523.5212 | 505.1135 | 477.7787 | 483.6845
1755.6135 | 523.6075 | 505.0447 | 477.7574 | 483.6334
1756.6135 | 523.6292 | 505.024 | 477.8264 | 483.9807
1757.6135 | 523.6732 | 505.0033 | 477.485 | 484.4421
1758.6135 | 523.7129 | 504.995 | 477.5703 | 484.423
1759.6135 | 523.6732 | 504.9439 | 477.7123 | 484.7458
1760.6135 | 523.525 | 504.942 | 477.6766 | 484.9197
1761.6135 | 523.4952 | 504.9213 | 477.8151 | 485.6909
1762.6135 | 523.5476 | 504.9155 | 477.4827 | 485.7961
1763.6135 | 523.5955 | 504.8719 | 477.6434 | 485.8546
1764.6135 | 523.7371 | 504.8705 | 477.5324 | 485.8954
1765.6135 | 523.7031 | 504.8767 | 477.6012 | 485.7432
1766.6135 | 523.6394 | 504.8551 | 477.6709 | 485.6136
1767.6135 | 523.6824 | 504.8633 | 477.737 | 485.7852
1768.6135 | 523.7041 | 504.8599 | 477.7774 | 485.795
1769.6135 | 523.6955 | 504.8568 | 477.8864 | 485.866
1770.6135 | 523.7313 | 504.831 | 477.6915 | 485.9768
1771.6135 | 523.7251 | 504.8472 | 477.6974 | 486.1838
1772.6135 | 523.6904 | 504.8288 | 477.4893 | 486.2023
1773.6135 | 523.526 | 504.801 | 477.4853 | 486.1109
1774.6135 | 523.6171 | 504.8179 | 477.7249 | 486.1421
1775.6135 | 523.7469 | 504.8113 | 477.8175 | 486.2248
1776.6135 | 523.7345 | 504.7927 | 477.906 | 486.4261
1777.6135 | 523.78 | 504.794 | 477.8123 | 486.5085
1778.6135 | 523.6516 | 504.7647 | 477.6014 | 486.5739
1779.6135 | 523.4963 | 504.7535 | 477.6311 | 486.5571
1780.6135 | 523.3679 | 504.7821 | 477.593 | 486.5978
1781.6135 | 523.3365 | 504.7843 | 477.6446 | 486.7676
1782.6135 | 523.3672 | 504.8193 | 477.6706 | 486.6601
1783.6135 | 523.4107 | 504.815 | 477.6857 | 486.5226
1784.6135 | 523.4139 | 504.8361 | 477.7851 | 486.6989
1785.6135 | 523.456 | 504.8891 | 477.8417 | 486.8971
1786.6135 | 523.5347 | 504.8802 | 477.9666 | 486.8866
1787.6135 | 523.5854 | 504.932 | 477.8723 | 487.2057
1788.6135 | 523.6562 | 504.9214 | 477.8363 | 487.3717
1789.6135 | 523.7168 | 504.9724 | 477.7178 | 487.3383
1790.6135 | 523.8319 | 505.0094 | 477.6918 | 487.8542
1791.6135 | 523.8512 | 505.0374 | 477.6625 | 487.7391
1792.6135 | 523.9351 | 505.0754 | 477.8004 | 487.8872
1793.6135 | 523.9313 | 505.1184 | 477.7874 | 487.7286
1794.6135 | 524.0544 | 505.1588 | 477.8733 | 487.5987
1795.6135 | 524.0153 | 505.1787 | 477.9085 | 487.9326
1796.6135 | 523.9632 | 505.1782 | 478.0688 | 488.3677
1797.6135 | 524.0997 | 505.2261 | 478.1086 | 488.1312
1798.6135 | 524.1786 | 505.2322 | 478.1275 | 488.1587
1799.6135 | 524.307 | 505.2638 | 478.1023 | 488.1827
1800.6135 | 524.1633 | 505.2833 | 477.7966 | 488.4117
1801.6135 | 524.1191 | 505.3091 | 477.8838 | 488.2341
1802.6135 | 524.1456 | 505.3369 | 478.0399 | 488.4579
1803.6135 | 524.125 | 505.2616 | 478.0157 | 488.2132
1804.6135 | 524.1492 | 505.3 | 477.943 | 488.1095
1805.6135 | 524.1564 | 505.3315 | 477.8868 | 488.3845
1806.6135 | 524.1531 | 505.3652 | 477.614 | 488.3179
1807.6135 | 524.0536 | 505.381 | 477.8377 | 488.4257
1808.6135 | 524.0153 | 505.4064 | 477.7908 | 488.2039
1809.6135 | 523.9036 | 505.4254 | 477.8745 | 488.7367
1810.6135 | 523.8748 | 505.417 | 477.8129 | 489.0149
1811.6135 | 523.7347 | 505.4464 | 478.0201 | 488.5007
1812.6135 | 523.5919 | 505.4002 | 478.1945 | 488.5955
1813.6135 | 523.6194 | 505.4065 | 478.1676 | 488.7041
1814.6135 | 523.8145 | 505.4134 | 478.228 | 488.6956
1815.6135 | 523.9302 | 505.4434 | 478.0797 | 488.7246
1816.6135 | 523.9681 | 505.4403 | 477.9846 | 488.6415
1817.6135 | 523.9389 | 505.4352 | 477.812 | 488.8907
1818.6135 | 523.8261 | 505.4258 | 477.7308 | 488.6871
1819.6135 | 523.6918 | 505.4175 | 477.8556 | 488.5492
1820.6135 | 523.7784 | 505.3987 | 477.9991 | 488.6856
1821.6135 | 523.8584 | 505.4198 | 477.9804 | 488.7118
1822.6292 | 523.7726 | 505.4089 | 477.9678 | 488.5671
1823.6135 | 523.7639 | 505.389 | 477.9782 | 488.5849
1824.6135 | 523.7155 | 505.3775 | 477.9617 | 488.6276
1825.6135 | 523.7437 | 505.3702 | 478.0768 | 488.3122
1826.6135 | 523.6412 | 505.43 | 478.1329 | 488.4161
1827.6135 | 523.6976 | 505.4409 | 477.9627 | 488.0311
1828.6135 | 523.7446 | 505.45 | 477.8188 | 487.9497
1829.6135 | 523.6904 | 505.4635 | 477.9218 | 488.1675
1830.6135 | 523.6131 | 505.4836 | 477.9269 | 488.3607
1831.6135 | 523.7153 | 505.51 | 478.0314 | 488.1092
1832.6135 | 523.8027 | 505.5384 | 478.1463 | 487.5257
1833.6135 | 523.8468 | 505.517 | 478.0256 | 487.359
1834.6135 | 523.7484 | 505.5415 | 478.0625 | 487.0096
1835.6135 | 523.6546 | 505.5699 | 478.169 | 487.286
1836.6135 | 523.5136 | 505.562 | 478.2379 | 487.4475
1837.6135 | 523.4839 | 505.5763 | 478.243 | 487.6164
1838.6135 | 523.4798 | 505.5716 | 478.3036 | 487.8148
1839.6135 | 523.5954 | 505.5415 | 478.2704 | 487.9667
1840.6135 | 523.6224 | 505.5316 | 478.0416 | 487.9952
1841.6135 | 523.6532 | 505.5868 | 478.2333 | 488.2463
1842.6135 | 523.723 | 505.5853 | 478.3324 | 487.6204
1843.6135 | 523.665 | 505.5885 | 478.235 | 488.6591
1844.6135 | 523.7347 | 505.5461 | 478.2637 | 488.4922
1845.6135 | 523.6362 | 505.5736 | 478.0755 | 488.0736
1846.6135 | 523.5351 | 505.575 | 477.9813 | 489.0315
1847.6135 | 523.4848 | 505.5473 | 478.1352 | 488.8982
1848.6135 | 523.44 | 505.5197 | 478.2413 | 488.9643
1849.6135 | 523.3875 | 505.5436 | 478.3135 | 488.8663
1850.6135 | 523.4772 | 505.5332 | 478.349 | 489.2645
1851.6135 | 523.5649 | 505.5147 | 478.2704 | 488.9833
1852.6292 | 523.6301 | 505.5296 | 478.4322 | 488.7771
1853.6135 | 523.6717 | 505.5038 | 478.4969 | 488.4646
1854.6135 | 523.7343 | 505.4783 | 478.4559 | 488.7086
1855.6135 | 523.7882 | 505.4698 | 478.4292 | 488.5801
1856.6135 | 523.7469 | 505.4506 | 478.4708 | 488.0882
1857.6135 | 523.5847 | 505.3959 | 478.5398 | 488.3347
1858.6135 | 523.5186 | 505.4125 | 478.4648 | 487.7901
1859.6135 | 523.5891 | 505.3788 | 478.4387 | 488.4246
1860.6135 | 523.5573 | 505.3036 | 478.3569 | 488.603
1861.6135 | 523.5522 | 505.2976 | 478.4448 | 488.4347
1862.6135 | 523.5885 | 505.2818 | 478.4846 | 487.2483
1863.6135 | 523.7443 | 505.2402 | 478.5784 | 487.6188
1864.6135 | 523.6959 | 505.196 | 478.391 | 487.7534
1865.6135 | 523.5585 | 505.1637 | 478.4606 | 487.7619
1866.6135 | 523.3392 | 505.1471 | 478.4884 | 487.7348
1867.6135 | 523.2744 | 505.06 | 478.4024 | 487.7937
1868.6135 | 523.2071 | 505.0429 | 478.5276 | 488.1186
1869.6135 | 523.2877 | 504.9809 | 478.4133 | 487.8854
1870.6135 | 523.3522 | 504.9529 | 478.1446 | 487.9684
1871.6135 | 523.3309 | 504.9505 | 478.2558 | 487.5358
1872.6135 | 523.2673 | 504.9481 | 478.4045 | 487.668
1873.6135 | 523.2551 | 504.8954 | 478.429 | 487.3581
1874.6135 | 523.3399 | 504.8528 | 478.5072 | 487.9014
1875.6135 | 523.4003 | 504.79 | 478.337 | 488.0038
1876.6135 | 523.4539 | 504.7622 | 478.1148 | 487.7819
1877.6135 | 523.3428 | 504.7593 | 478.1936 | 487.9407
1878.6135 | 523.3516 | 504.7297 | 478.3186 | 487.9756
1879.6135 | 523.4258 | 504.688 | 478.503 | 488.0407
1880.6135 | 523.5915 | 504.6621 | 478.5651 | 487.7172
1881.6135 | 523.7004 | 504.6564 | 478.4985 | 487.445
1882.6135 | 523.8119 | 504.6345 | 478.4062 | 487.571
1883.6135 | 523.8011 | 504.5992 | 478.3897 | 487.2114
1884.6135 | 523.7982 | 504.5965 | 478.5796 | 487.0846
1885.6135 | 523.83 | 504.5913 | 478.453 | 487.5319
1886.6135 | 523.9139 | 504.5645 | 478.6159 | 487.5374
1887.6135 | 523.8866 | 504.5269 | 478.5899 | 487.8552
1888.6135 | 523.9675 | 504.5159 | 478.534 | 487.8927
1889.6292 | 523.9235 | 504.4795 | 478.6105 | 487.9654
1890.6135 | 523.7962 | 504.4651 | 478.6286 | 488.0243
1891.6135 | 523.8537 | 504.453 | 478.4396 | 488.0382
1892.6135 | 523.7731 | 504.3933 | 478.5164 | 488.3741
1893.6135 | 523.7415 | 504.3955 | 478.7184 | 488.4589
1894.6135 | 523.7524 | 504.3235 | 478.6453 | 487.8175
1895.6135 | 523.8109 | 504.3388 | 478.7304 | 488.2504
1896.6135 | 523.756 | 504.3327 | 478.7492 | 488.4289
1897.6135 | 523.8071 | 504.3149 | 478.7018 | 488.3916
1898.6135 | 523.9205 | 504.2719 | 478.6477 | 488.4661
1899.6135 | 523.9381 | 504.2818 | 478.5043 | 487.8196
1900.6135 | 524.0008 | 504.2924 | 478.7057 | 487.8604
1901.6135 | 523.9714 | 504.2446 | 478.5331 | 488.3199
1902.6135 | 523.8882 | 504.2487 | 478.5734 | 488.0626
1903.6135 | 523.8285 | 504.2494 | 478.4214 | 488.1494
1904.6135 | 523.7776 | 504.2823 | 478.5857 | 488.5665
1905.6135 | 523.8922 | 504.2988 | 478.5471 | 488.4699
1906.6135 | 523.91 | 504.2828 | 478.2348 | 488.6468
1907.6135 | 523.9275 | 504.2856 | 478.4702 | 488.624
1908.6135 | 523.9472 | 504.2534 | 478.5435 | 488.6222
1909.6135 | 523.9125 | 504.2815 | 478.6066 | 487.4102
1910.6135 | 523.7904 | 504.3021 | 478.7242 | 487.76
1911.6135 | 523.8009 | 504.2913 | 478.8232 | 487.9668
1912.6135 | 523.8503 | 504.3095 | 478.7404 | 487.3603
1913.6135 | 523.9258 | 504.2781 | 478.6337 | 487.4199
1914.6135 | 523.882 | 504.2979 | 478.7063 | 487.4566
1915.6135 | 523.9069 | 504.2929 | 478.6903 | 487.2434
1916.6135 | 524.0136 | 504.2856 | 478.7923 | 487.0968
1917.6135 | 524.0797 | 504.2658 | 478.7301 | 487.4144
1918.6135 | 523.9805 | 504.273 | 478.5779 | 487.2784
1919.6135 | 523.9614 | 504.2806 | 478.6897 | 487.1222
1920.6135 | 523.794 | 504.3162 | 478.6395 | 487.2644
1921.6135 | 523.7372 | 504.3289 | 478.6919 | 487.4696
1922.6135 | 523.7225 | 504.3103 | 478.6745 | 487.8028
1923.6135 | 523.6904 | 504.3019 | 478.8241 | 487.7773
1924.6135 | 523.6706 | 504.2944 | 478.7448 | 487.2743
1925.6135 | 523.535 | 504.2986 | 478.6585 | 487.3884
1926.6135 | 523.5539 | 504.301 | 478.4926 | 487.974
1927.6135 | 523.4912 | 504.3368 | 478.6309 | 488.003
1928.6135 | 523.4033 | 504.3132 | 478.7387 | 487.9671
1929.6135 | 523.384 | 504.3457 | 478.8464 | 488.0333
1930.6135 | 523.3569 | 504.3581 | 478.7784 | 488.1918
1931.6135 | 523.3161 | 504.3317 | 478.9148 | 488.2624
1932.6135 | 523.258 | 504.3046 | 478.9806 | 488.6545
1933.6135 | 523.106 | 504.2922 | 479.0182 | 487.4847
1934.6135 | 523.0767 | 504.2882 | 478.8809 | 487.5785
1935.6135 | 523.1323 | 504.3556 | 478.8009 | 488.1804
1936.6135 | 523.0849 | 504.3897 | 478.7979 | 488.2421
1937.6135 | 523.0222 | 504.386 | 478.8692 | 488.3947
1938.6135 | 523.0258 | 504.3988 | 478.8034 | 488.2631
1939.6135 | 522.8633 | 504.3692 | 478.7144 | 488.3712
1940.6135 | 522.7382 | 504.3778 | 478.8773 | 488.3364
1941.6135 | 522.7252 | 504.3818 | 478.636 | 488.7076
1942.6135 | 522.812 | 504.3659 | 478.7403 | 488.6628
1943.6135 | 522.8628 | 504.3017 | 478.6859 | 488.902
1944.6135 | 522.8461 | 504.3638 | 478.6759 | 488.8773
1945.6135 | 522.8211 | 504.3324 | 478.3181 | 488.7825
1946.6135 | 522.9173 | 504.3607 | 478.3544 | 489.0731
1947.6135 | 523.0522 | 504.3489 | 478.2028 | 489.0685
1948.6135 | 523.0598 | 504.364 | 478.3241 | 488.9652
1949.6135 | 523.255 | 504.3478 | 478.2134 | 489.2405
1950.6135 | 523.2797 | 504.3661 | 478.2202 | 488.9955
1951.6135 | 523.1643 | 504.3447 | 478.354 | 488.8643
1952.6135 | 523.1619 | 504.3874 | 478.5397 | 488.9821
1953.6135 | 523.3146 | 504.4088 | 478.5434 | 489.0373
1954.6135 | 523.3657 | 504.4307 | 478.38 | 488.9704
1955.6135 | 523.4522 | 504.4489 | 478.4916 | 488.8668
1956.6135 | 523.4882 | 504.448 | 478.4319 | 489.0247
1957.6135 | 523.4943 | 504.4441 | 478.4451 | 489.0318
1958.6135 | 523.3698 | 504.4736 | 478.5453 | 489.0049
1959.6135 | 523.3737 | 504.4671 | 478.7699 | 488.8373
1960.6135 | 523.3204 | 504.479 | 478.7184 | 488.8193
1961.6135 | 523.353 | 504.5065 | 478.5525 | 488.762
1962.6135 | 523.3868 | 504.4847 | 478.149 | 488.847
1963.6135 | 523.3952 | 504.487 | 478.4256 | 489.0037
1964.6135 | 523.4916 | 504.4376 | 478.7217 | 489.1569
1965.6135 | 523.5825 | 504.489 | 478.6539 | 489.1668
1966.6135 | 523.6173 | 504.481 | 478.6634 | 489.1922
1967.6135 | 523.6273 | 504.5318 | 478.6401 | 489.2265
1968.6135 | 523.6697 | 504.5458 | 478.5704 | 489.3616
1969.6135 | 523.7496 | 504.5431 | 478.5324 | 489.2558
1970.6135 | 523.712 | 504.5629 | 478.4241 | 489.4299
1971.6135 | 523.6886 | 504.5427 | 478.4521 | 489.4895
1972.6135 | 523.622 | 504.5786 | 478.5298 | 489.6613
1973.6135 | 523.587 | 504.5967 | 478.5078 | 489.4767
1974.6135 | 523.471 | 504.6061 | 478.4278 | 489.4419
1975.6135 | 523.2962 | 504.6168 | 478.5247 | 489.6998
1976.6135 | 523.2845 | 504.6053 | 478.5411 | 489.69
1977.6135 | 523.3579 | 504.6283 | 478.6719 | 489.341
1978.6135 | 523.394 | 504.6429 | 478.7167 | 490.0591
1979.6135 | 523.4797 | 504.6136 | 478.579 | 490.0211
1980.6135 | 523.437 | 504.6221 | 478.6658 | 490.0544
1981.6135 | 523.3608 | 504.6519 | 478.4301 | 489.9993
1982.6135 | 523.3572 | 504.6514 | 478.7109 | 489.9607
1983.6135 | 523.3749 | 504.6408 | 478.8596 | 489.838
1984.6135 | 523.2844 | 504.6321 | 478.5784 | 490.0046
1985.6135 | 523.2138 | 504.6468 | 478.466 | 489.5175
1986.6135 | 523.3329 | 504.6623 | 478.647 | 489.8745
1987.6135 | 523.297 | 504.6489 | 478.5892 | 489.9167
1988.6135 | 523.388 | 504.6611 | 478.7149 | 489.5058
1989.6135 | 523.5557 | 504.6962 | 478.5544 | 490.1584
1990.6135 | 523.4871 | 504.6902 | 478.3231 | 490.2332
1991.6135 | 523.5174 | 504.6732 | 478.4752 | 490.3275
1992.6135 | 523.7077 | 504.7271 | 478.1117 | 490.2573
1993.6135 | 523.6905 | 504.7373 | 478.3188 | 490.4789
1994.6135 | 523.7698 | 504.7423 | 478.3367 | 490.4463
1995.6135 | 523.7825 | 504.7603 | 478.431 | 490.6496
1996.6135 | 523.656 | 504.7705 | 478.6311 | 490.6053
1997.6135 | 523.7163 | 504.7872 | 478.7363 | 490.1459
1998.6135 | 523.6639 | 504.7954 | 478.528 | 490.0965
1999.6135 | 523.6035 | 504.7847 | 478.7493 | 490.1123
2000.6135 | 523.6917 | 504.8148 | 478.697 | 490.1591
2001.6135 | 523.7758 | 504.8055 | 478.7505 | 490.0913
2002.6135 | 523.6773 | 504.8359 | 478.8559 | 490.0336
2003.6135 | 523.5489 | 504.8526 | 478.9543 | 490.0272
2004.6135 | 523.5018 | 504.8327 | 479.0197 | 490.0672
2005.6135 | 523.6046 | 504.8572 | 478.9681 | 490.1551
2006.6135 | 523.7066 | 504.8788 | 479.0117 | 490.3331
2007.6135 | 523.7014 | 504.8823 | 478.9755 | 490.1927
2008.6135 | 523.7162 | 504.9029 | 478.7115 | 490.2609
2009.6135 | 523.6958 | 504.8859 | 478.7607 | 489.651
2010.6135 | 523.7461 | 504.911 | 478.9284 | 490.3353
2011.6135 | 523.865 | 504.884 | 478.9757 | 490.3677
2012.6135 | 523.9694 | 504.9127 | 478.9249 | 490.3742
2013.6135 | 524.1083 | 504.9348 | 479.0437 | 490.4462
2014.6135 | 524.1008 | 504.9384 | 479.092 | 490.6592
2015.6135 | 524.0884 | 504.9507 | 479.0601 | 490.7186
2016.6135 | 523.9912 | 504.9669 | 479.0409 | 490.5366
2017.6135 | 524.0105 | 504.9637 | 479.1804 | 490.6064
2018.6135 | 523.9875 | 505.0024 | 479.2315 | 490.8117
2019.6135 | 523.9247 | 505.0114 | 478.9168 | 490.8465
2020.6135 | 523.8256 | 505.0252 | 478.709 | 491.2518
2021.6135 | 523.9198 | 505.0519 | 479.0525 | 491.4295
2022.6135 | 523.9734 | 505.0069 | 479.1796 | 491.3965
2023.6135 | 523.9535 | 504.9912 | 479.17 | 491.1168
2024.6135 | 523.8636 | 504.9933 | 479.1267 | 490.6598
2025.6135 | 523.8963 | 505.0514 | 479.2027 | 491.5508
2026.6135 | 523.8754 | 504.952 | 479.2504 | 491.4425
2027.6135 | 523.8259 | 505.0318 | 479.0501 | 490.0917
2028.6135 | 523.8097 | 505.0685 | 478.8679 | 490.6549
2029.6135 | 523.7783 | 505.1025 | 478.7551 | 490.4304
2030.6135 | 523.7857 | 505.0592 | 479.0333 | 490.931
2031.6135 | 523.6533 | 505.0982 | 479.222 | 490.6971
2032.6135 | 523.4818 | 505.0804 | 479.2979 | 491.1068
2033.6135 | 523.4443 | 505.0819 | 478.981 | 491.3707
2034.6135 | 523.4888 | 505.1063 | 478.9082 | 491.2469
2035.6135 | 523.4603 | 505.1359 | 479.0025 | 491.4343
2036.6135 | 523.55 | 505.1551 | 478.8648 | 491.6077
2037.6135 | 523.5122 | 505.1573 | 478.9352 | 491.3775
2038.6135 | 523.4915 | 505.1544 | 479.0012 | 491.1964
2039.6135 | 523.4603 | 505.1642 | 479.1801 | 491.7031
2040.6135 | 523.4737 | 505.1491 | 479.2258 | 491.8262
2041.6135 | 523.6658 | 505.1253 | 479.1611 | 491.9373
2042.6135 | 523.687 | 505.1163 | 478.8423 | 492.0478
2043.6135 | 523.6246 | 505.105 | 478.9766 | 491.9756
2044.6135 | 523.5975 | 505.1109 | 479.1629 | 492.0077
2045.6135 | 523.6995 | 505.0785 | 479.0986 | 492.0684
2046.6135 | 523.6669 | 505.0877 | 479.098 | 491.2598
2047.6135 | 523.6836 | 505.1109 | 479.3178 | 492.3611
2048.6135 | 523.7527 | 505.0802 | 479.0961 | 492.4866
2049.6135 | 523.7837 | 505.1371 | 479.2879 | 492.4022
2050.6135 | 523.8988 | 505.1179 | 479.3349 | 492.365
2051.6135 | 523.9866 | 505.1243 | 479.402 | 492.1836
2052.6135 | 524.1362 | 505.138 | 478.9265 | 491.7498
2053.6135 | 524.0754 | 505.1715 | 479.0841 | 492.5547
2054.6135 | 524.1338 | 505.1827 | 479.3355 | 492.1565
2055.6135 | 524.1868 | 505.2146 | 479.4446 | 490.3745
2056.6135 | 524.1992 | 505.2127 | 479.5934 | 492.1332
2057.6135 | 524.2547 | 505.2093 | 479.331 | 492.4892
2058.6135 | 524.27 | 505.1914 | 479.3132 | 492.3189
2059.6135 | 524.1172 | 505.2038 | 479.5448 | 491.6459
2060.6135 | 524.0701 | 505.2215 | 479.6168 | 492.3819
2061.6135 | 524.1468 | 505.2129 | 479.6098 | 492.8728
2062.6135 | 524.1437 | 505.2375 | 479.5084 | 492.5182
2063.6135 | 524.1145 | 505.2412 | 479.0915 | 490.7586
2064.6135 | 524.1533 | 505.2557 | 479.2535 | 490.9096
2065.6135 | 524.2052 | 505.2784 | 479.4189 | 490.8473
2066.6135 | 524.2133 | 505.2736 | 479.3764 | 490.9493
2067.6135 | 524.1679 | 505.3098 | 479.1689 | 492.48
2068.6135 | 524.2614 | 505.2999 | 479.3294 | 490.7005
2069.6135 | 524.3126 | 505.2885 | 479.6802 | 492.9695
2070.6135 | 524.4245 | 505.3244 | 479.5346 | 493.2545
2071.6135 | 524.6167 | 505.3125 | 479.6371 | 491.126
2072.6135 | 524.6013 | 505.3602 | 479.4224 | 493.3751
2073.6135 | 524.6528 | 505.4048 | 479.5398 | 491.5434
2074.6135 | 524.6918 | 505.416 | 479.5013 | 491.3378
2075.6135 | 524.6343 | 505.4086 | 479.3999 | 491.2849
2076.6135 | 524.6338 | 505.4401 | 479.4844 | 491.5112
2077.6135 | 524.6901 | 505.4203 | 479.5111 | 491.5304
2078.6135 | 524.5344 | 505.4506 | 479.6067 | 491.5546
2079.6135 | 524.5377 | 505.4817 | 479.5794 | 491.7996
2080.6135 | 524.53 | 505.4925 | 479.5655 | 491.7842
2081.6135 | 524.3848 | 505.4797 | 479.6591 | 491.8102
2082.6135 | 524.3461 | 505.477 | 479.8769 | 491.9135
2083.6135 | 524.4226 | 505.469 | 479.8846 | 491.9376
2084.6135 | 524.4206 | 505.4415 | 479.7917 | 492.0495
2085.6135 | 524.4095 | 505.4662 | 479.4632 | 492.1197
2086.6135 | 524.4936 | 505.4855 | 479.4755 | 492.0785
2087.6135 | 524.5836 | 505.4785 | 479.6138 | 492.2864
2088.6135 | 524.5707 | 505.4945 | 479.5172 | 492.3854
2089.6135 | 524.5483 | 505.4657 | 479.5528 | 492.3308
2090.6135 | 524.6269 | 505.4764 | 479.3894 | 491.7401
2091.6135 | 524.7224 | 505.433 | 479.4382 | 491.8234
2092.6135 | 524.8288 | 505.4419 | 479.4426 | 491.9858
2093.6135 | 524.8746 | 505.442 | 479.4957 | 492.0173
2094.6135 | 524.7457 | 505.44 | 479.5925 | 492.0825
2095.6135 | 524.6184 | 505.4499 | 479.7294 | 492.0953
2096.6135 | 524.5566 | 505.4368 | 479.9168 | 492.1951
2097.6135 | 524.5249 | 505.4563 | 480.016 | 492.3254
2098.6135 | 524.5472 | 505.4869 | 479.8877 | 492.474
2099.6135 | 524.5241 | 505.4999 | 479.942 | 492.4226
2100.6135 | 524.3813 | 505.477 | 479.9424 | 492.5062
2101.6135 | 524.4818 | 505.4967 | 480.1835 | 492.5803
2102.6135 | 524.4493 | 505.5026 | 480.147 | 492.8083
2103.6135 | 524.3897 | 505.5234 | 479.9123 | 492.7526
2104.6135 | 524.2648 | 505.5763 | 480.0075 | 492.8131
2105.6135 | 524.2122 | 505.5786 | 479.998 | 492.7602
2106.6135 | 524.281 | 505.5629 | 479.9866 | 493.0651
2107.6135 | 524.3106 | 505.5993 | 479.9034 | 493.2249
2108.6135 | 524.3448 | 505.5877 | 479.9205 | 493.0688
2109.6135 | 524.4447 | 505.6023 | 479.9141 | 493.1305
2110.6135 | 524.5622 | 505.5992 | 479.895 | 493.3007
2111.6135 | 524.5505 | 505.6103 | 480.023 | 493.265
2112.6135 | 524.5648 | 505.624 | 479.9985 | 493.4905
2113.6135 | 524.3884 | 505.609 | 480.0006 | 493.5963
2114.6135 | 524.3307 | 505.6384 | 479.8357 | 493.8201
2115.6135 | 524.2187 | 505.6225 | 479.7428 | 493.8835
2116.6135 | 523.8991 | 505.59 | 479.9841 | 493.8052
2117.6135 | 523.8143 | 505.6429 | 480.0406 | 493.8676
2118.6135 | 523.8457 | 505.5522 | 480.0091 | 494.0991
2119.6135 | 523.8616 | 505.552 | 480.1178 | 494.1775
2120.6135 | 523.8858 | 505.594 | 480.2514 | 494.3005
2121.6135 | 523.9308 | 505.6335 | 480.2619 | 494.3719
2122.6135 | 523.8473 | 505.5963 | 480.3455 | 494.4638
2123.6135 | 523.9206 | 505.5631 | 480.2331 | 494.625
2124.6135 | 523.9016 | 505.5344 | 480.1417 | 494.6581
2125.6135 | 523.9752 | 505.5245 | 480.2728 | 494.5222
2126.6135 | 523.9887 | 505.553 | 480.429 | 494.6266
2127.6135 | 524.0451 | 505.5312 | 480.3448 | 495.0023
2128.6135 | 524.1543 | 505.5475 | 480.0817 | 495.0405
2129.6135 | 524.1681 | 505.543 | 479.8275 | 494.9641
2130.6135 | 524.123 | 505.4726 | 480.0218 | 495.0709
2131.6135 | 524.2077 | 505.4813 | 480.0857 | 495.15
2132.6135 | 524.1994 | 505.4769 | 480.2606 | 495.3143
2133.6135 | 524.3141 | 505.5269 | 480.3932 | 495.2764
2134.6135 | 524.4494 | 505.5388 | 480.3329 | 495.3403
2135.6135 | 524.4626 | 505.5652 | 480.3712 | 495.3765
2136.6135 | 524.4989 | 505.5608 | 480.3486 | 495.5142
2137.6135 | 524.4071 | 505.5363 | 480.5598 | 495.533
2138.6135 | 524.4342 | 505.5168 | 480.6092 | 495.6559
2139.6135 | 524.5389 | 505.5628 | 480.3877 | 495.7183
2140.6135 | 524.5389 | 505.5835 | 480.2055 | 495.8243
2141.6135 | 524.6024 | 505.5831 | 479.9886 | 495.7768
2142.6135 | 524.7174 | 505.6308 | 479.9706 | 495.7731
2143.6135 | 524.7187 | 505.6403 | 480.1578 | 495.9028
2144.6135 | 524.6476 | 505.617 | 479.8428 | 496.151
2145.6135 | 524.6841 | 505.6548 | 480.0572 | 496.1281
2146.6135 | 524.6412 | 505.6705 | 480.1073 | 496.3429
2147.6135 | 524.5244 | 505.6891 | 480.1825 | 496.4919
2148.6135 | 524.4049 | 505.6664 | 480.312 | 496.5436
2149.6135 | 524.3678 | 505.7044 | 480.3183 | 496.6689
2150.6135 | 524.2984 | 505.7683 | 480.0934 | 496.5776
2151.6135 | 524.2638 | 505.7481 | 480.1404 | 496.4444
2152.6135 | 524.3942 | 505.7774 | 480.3713 | 496.7466
2153.6135 | 524.4615 | 505.782 | 480.4828 | 496.7208
2154.6135 | 524.4685 | 505.8224 | 480.519 | 497.0622
2155.6135 | 524.4856 | 505.8593 | 480.4564 | 496.9498
2156.6135 | 524.6556 | 505.8645 | 480.4529 | 496.9435
2157.6135 | 524.7547 | 505.8867 | 480.2769 | 497.0313
2158.6135 | 524.7528 | 505.9036 | 480.1544 | 497.1896
2159.6135 | 524.7607 | 505.9402 | 480.3282 | 497.2147
2160.6135 | 524.7589 | 505.9023 | 480.1497 | 497.2434
2161.6135 | 524.7029 | 505.9571 | 480.3633 | 497.2278
2162.6135 | 524.5225 | 505.979 | 480.2615 | 497.1665
2163.6135 | 524.4492 | 506.0213 | 480.0938 | 497.3523
2164.6135 | 524.4773 | 506.0221 | 480.1944 | 497.5256
2165.6135 | 524.3976 | 506.0455 | 480.3431 | 497.7004
2166.6135 | 524.3875 | 506.0794 | 480.2551 | 497.8475
2167.6135 | 524.2143 | 506.1121 | 480.4171 | 497.9642
2168.6135 | 524.1845 | 506.0879 | 480.64 | 498.043
2169.6135 | 524.2065 | 506.1108 | 480.8297 | 498.1968
2170.6135 | 524.1188 | 506.1271 | 480.9024 | 498.1071
2171.6135 | 524.0001 | 506.1347 | 480.673 | 498.3711
2172.6135 | 523.804 | 506.1548 | 480.6116 | 498.3643
2173.6135 | 523.749 | 506.1386 | 480.5881 | 498.4666
2174.6135 | 523.6185 | 506.1315 | 480.6156 | 498.3943
2175.6135 | 523.5618 | 506.1745 | 480.3572 | 498.51
2176.6135 | 523.516 | 506.2 | 480.5014 | 498.7368
2177.6135 | 523.387 | 506.1999 | 480.4234 | 498.7347
2178.6135 | 523.4329 | 506.1763 | 480.4708 | 498.9359
2179.6135 | 523.2813 | 506.2353 | 480.6531 | 499.1913
2180.6135 | 523.2022 | 506.28 | 480.7878 | 499.209
2181.6135 | 523.3176 | 506.2708 | 480.7829 | 499.0718
2182.6135 | 523.4528 | 506.26 | 480.8226 | 499.2215
2183.6135 | 523.558 | 506.2243 | 480.8863 | 499.3767
2184.6135 | 523.5639 | 506.1313 | 480.7263 | 499.2238
2185.6135 | 523.5668 | 506.1297 | 480.5619 | 499.5385
2186.6135 | 523.5246 | 506.0807 | 480.5545 | 499.7952
2187.6135 | 523.4674 | 506.0316 | 480.7408 | 499.8394
2188.6135 | 523.4052 | 505.9555 | 480.7917 | 500.1134
2189.6135 | 523.4155 | 505.877 | 480.9635 | 500.3176
2190.6135 | 523.4674 | 505.7536 | 480.9828 | 500.411
2191.6135 | 523.6114 | 505.7397 | 480.8367 | 500.4566
2192.6135 | 523.6679 | 505.6715 | 480.7918 | 500.5336
2193.6135 | 523.7495 | 505.6332 | 480.8996 | 500.5642
2194.6135 | 523.8242 | 505.6106 | 480.8741 | 500.5937
2195.6135 | 523.8404 | 505.5515 | 481.0338 | 500.2674
2196.6135 | 523.8147 | 505.4832 | 481.0929 | 500.3016
2197.6135 | 523.6986 | 505.4405 | 481.1178 | 500.5586
2198.6135 | 523.6829 | 505.3704 | 481.0122 | 500.5505
2199.6135 | 523.7434 | 505.3261 | 481.0918 | 500.68
2200.6135 | 523.5301 | 505.2614 | 481.2515 | 500.9093
2201.6135 | 523.5341 | 505.2095 | 480.9759 | 500.9798
2202.6135 | 523.725 | 505.1962 | 481.0022 | 501.169
2203.6135 | 523.7681 | 505.1664 | 481.2981 | 501.2276
2204.6135 | 523.8073 | 505.158 | 481.2556 | 501.265
2205.6135 | 523.7666 | 505.1815 | 480.8998 | 501.2405
2206.6135 | 523.647 | 505.2043 | 481.0326 | 501.2075
2207.6135 | 523.6823 | 505.212 | 481.2263 | 501.233
2208.6135 | 523.6105 | 505.2577 | 481.3206 | 501.4917
2209.6135 | 523.6557 | 505.2728 | 480.8603 | 501.8499
2210.6135 | 523.6228 | 505.3163 | 480.9083 | 501.9426
2211.6135 | 523.5521 | 505.3145 | 481.1839 | 502.2002
2212.6135 | 523.5774 | 505.3099 | 481.0547 | 502.0868
2213.6135 | 523.6818 | 505.3751 | 481.2428 | 502.2304
2214.6135 | 523.8584 | 505.3919 | 481.271 | 502.335
2215.6135 | 523.7894 | 505.4392 | 481.0386 | 502.3441
2216.6135 | 523.7586 | 505.4821 | 481.1783 | 502.411
2217.6135 | 523.8254 | 505.5334 | 481.2201 | 502.4354
2218.6135 | 523.8755 | 505.5708 | 481.3059 | 502.6047
2219.6135 | 523.96 | 505.6171 | 481.3668 | 502.5852
2220.6135 | 524.0533 | 505.662 | 481.2523 | 502.6879
2221.6135 | 524.0042 | 505.7143 | 481.2482 | 502.8074
2222.6135 | 523.8266 | 505.7625 | 481.4469 | 502.8272
2223.6135 | 523.7579 | 505.7814 | 481.4947 | 503.1311
2224.6135 | 523.7936 | 505.8265 | 481.4968 | 503.1523
2225.6135 | 523.84 | 505.8526 | 481.5135 | 503.4121
2226.6135 | 523.9219 | 505.9075 | 481.5367 | 503.3996
2227.6135 | 523.9059 | 505.9383 | 481.39 | 503.4661
2228.6135 | 523.8052 | 505.9481 | 481.5085 | 503.5382
2229.6135 | 523.7803 | 505.9574 | 481.5436 | 503.7194
2230.6135 | 523.7326 | 506.0099 | 481.557 | 503.9649
2231.6135 | 523.752 | 506.031 | 481.5838 | 504.1162
2232.6135 | 523.7145 | 506.0949 | 481.6878 | 504.1904
2233.6135 | 523.6097 | 506.09 | 481.768 | 504.3169
2234.6135 | 523.6281 | 506.1343 | 481.8516 | 504.4105
2235.6135 | 523.6079 | 506.1795 | 481.8138 | 504.6187
2236.6135 | 523.6295 | 506.1966 | 481.6783 | 504.5887
2237.6135 | 523.7508 | 506.2153 | 481.3748 | 504.8226
2238.6135 | 523.6677 | 506.2291 | 481.4956 | 505.0099
2239.6135 | 523.6405 | 506.2448 | 481.2733 | 505.0517
2240.6135 | 523.4768 | 506.2857 | 481.4031 | 505.2684
2241.6135 | 523.3984 | 506.2944 | 481.4893 | 505.2639
2242.6135 | 523.417 | 506.345 | 481.5675 | 505.2728
2243.6135 | 523.3963 | 506.3382 | 481.5376 | 505.2456
2244.6135 | 523.4361 | 506.3655 | 481.5518 | 505.3312
2245.6135 | 523.3872 | 506.3999 | 481.5808 | 505.491
2246.6135 | 523.4946 | 506.4337 | 481.568 | 505.4511
2247.6135 | 523.5743 | 506.4789 | 481.6752 | 505.6148
2248.6135 | 523.5079 | 506.5074 | 481.4892 | 505.8408
2249.6135 | 523.5124 | 506.5428 | 481.5564 | 505.836
2250.6135 | 523.6111 | 506.5727 | 481.8186 | 505.8715
2251.6135 | 523.6173 | 506.5453 | 481.9674 | 505.9877
2252.6135 | 523.7094 | 506.5669 | 481.8981 | 506.2182
2253.6135 | 523.8887 | 506.6203 | 481.4822 | 506.3593
2254.6135 | 523.9946 | 506.6526 | 481.4328 | 506.6028
2255.6135 | 524.0791 | 506.6141 | 481.5473 | 506.4393
2256.6135 | 524.1425 | 506.6551 | 481.8584 | 506.5285
2257.6135 | 524.2375 | 506.6759 | 481.7507 | 506.5673
2258.6135 | 524.1915 | 506.6784 | 481.6151 | 506.6053
2259.6135 | 524.4042 | 506.6917 | 481.5606 | 506.5447
2260.6135 | 524.3089 | 506.7114 | 481.5325 | 506.8193
2261.6135 | 524.1555 | 506.7774 | 481.423 | 506.9667
2262.6135 | 524.1125 | 506.7954 | 481.6018 | 506.9862
2263.6135 | 524.0899 | 506.8056 | 481.7713 | 506.9261
2264.6135 | 524.1291 | 506.8128 | 481.7704 | 507.1006
2265.6135 | 524.1158 | 506.8292 | 481.917 | 507.199
2266.6135 | 524.0888 | 506.8065 | 481.9522 | 507.5027
2267.6135 | 524.1679 | 506.8451 | 481.8746 | 507.3876
2268.6135 | 524.1369 | 506.8612 | 482.0853 | 507.6339
2269.6135 | 524.1479 | 506.8665 | 482.1175 | 507.8869
2270.6135 | 524.2295 | 506.883 | 481.6387 | 508.0254
2271.6135 | 524.1623 | 506.9085 | 481.3715 | 508.164
2272.6135 | 524.1361 | 506.9518 | 481.5726 | 508.0653
2273.6135 | 524.1811 | 506.9024 | 481.6127 | 508.1296
2274.6135 | 524.1474 | 506.9308 | 481.8931 | 508.411
2275.6135 | 524.1848 | 506.9538 | 481.8677 | 508.4845
2276.6135 | 524.2087 | 506.9644 | 481.8036 | 508.4009
2277.6135 | 524.2879 | 506.9563 | 481.9562 | 508.6789
2278.6135 | 524.2194 | 506.9703 | 481.9327 | 508.6246
2279.6135 | 524.1086 | 506.9731 | 482.0008 | 508.4599
2280.6135 | 524.0439 | 506.9954 | 482.0321 | 508.712
2281.6135 | 523.961 | 506.9941 | 482.0721 | 508.8182
2282.6135 | 523.9455 | 507.0137 | 482.1016 | 508.793
2283.6135 | 523.9892 | 507.0299 | 482.2565 | 509.0195
2284.6135 | 524.0494 | 507.084 | 482.2909 | 509.169
2285.6135 | 524.1177 | 507.0894 | 481.9879 | 509.3597
2286.6135 | 524.1121 | 507.0994 | 481.9528 | 509.4542
2287.6135 | 523.9729 | 507.136 | 482.024 | 509.4417
2288.6135 | 523.8035 | 507.1635 | 482.1558 | 509.4696
2289.6135 | 523.7338 | 507.1972 | 482.0273 | 509.5899
2290.6135 | 523.788 | 507.2282 | 481.953 | 509.8573
2291.6135 | 523.6416 | 507.2572 | 482.0726 | 509.9211
2292.6135 | 523.6391 | 507.2708 | 482.1267 | 510.1082
2293.6135 | 523.6448 | 507.2916 | 482.0978 | 510.3413
2294.6135 | 523.6481 | 507.3122 | 481.8401 | 510.3811
2295.6135 | 523.5766 | 507.35 | 481.9787 | 510.4698
2296.6135 | 523.6639 | 507.3547 | 482.1447 | 510.7028
2297.6135 | 523.6048 | 507.3565 | 482.1667 | 510.7235
2298.6135 | 523.6253 | 507.374 | 481.8842 | 510.5719
2299.6135 | 523.64 | 507.3863 | 482.0017 | 510.7768
2300.6135 | 523.6633 | 507.3966 | 482.0888 | 510.7895
2301.6135 | 523.6897 | 507.4256 | 482.0749 | 510.9717
2302.6135 | 523.674 | 507.4681 | 482.2584 | 511.0808
2303.6135 | 523.6487 | 507.4756 | 481.9411 | 511.2406
2304.6135 | 523.6442 | 507.5147 | 481.9757 | 511.4689
2305.6135 | 523.7178 | 507.5382 | 481.9865 | 511.6362
2306.6135 | 523.8479 | 507.573 | 482.2063 | 511.5021
2307.6135 | 523.8868 | 507.6048 | 482.297 | 511.6913
2308.6135 | 523.9289 | 507.6032 | 482.3055 | 511.6479
2309.6135 | 523.9625 | 507.5955 | 481.991 | 511.6696
2310.6135 | 524.006 | 507.606 | 482.086 | 511.7196
2311.6135 | 524.1565 | 507.643 | 482.1705 | 511.9719
2312.6135 | 524.2343 | 507.6361 | 482.1996 | 512.2967
2313.7854 | 524.1394 | 507.7123 | 482.2617 | 512.4098
2314.6135 | 524.1372 | 507.7472 | 482.2746 | 512.4384
2315.6135 | 524.1383 | 507.775 | 482.0246 | 512.5225
2316.6135 | 524.1355 | 507.801 | 482.2052 | 512.6043
2317.6135 | 524.1233 | 507.8174 | 482.3872 | 512.6523
2318.6135 | 524.0992 | 507.8598 | 482.5073 | 512.8099
2319.6135 | 524.0868 | 507.8535 | 482.4835 | 512.8309
2320.6135 | 524.1041 | 507.8555 | 482.4436 | 513.0258
2321.6135 | 524.2621 | 507.8138 | 482.3415 | 513.1545
2322.6135 | 524.3321 | 507.8847 | 482.4259 | 513.1981
2323.6135 | 524.4206 | 507.8685 | 482.4898 | 513.3224
2324.8167 | 524.3751 | 507.922 | 482.6248 | 513.5098
2325.6135 | 524.3688 | 507.9537 | 482.6681 | 513.3997
2326.6135 | 524.416 | 508.0093 | 482.7128 | 513.5634
2327.6135 | 524.4012 | 507.9883 | 482.8395 | 513.7798
2328.6135 | 524.2829 | 508.0402 | 482.9127 | 513.7651
2329.6135 | 524.3068 | 508.0812 | 482.8996 | 513.9773
2330.6135 | 524.2527 | 508.0914 | 482.6575 | 514.1978
2331.6135 | 524.1694 | 508.1082 | 482.7094 | 514.3123
2332.6135 | 524.2369 | 508.1323 | 482.5764 | 514.2216
2333.6135 | 524.166 | 508.1626 | 482.5991 | 514.317
2334.8792 | 524.0272 | 508.1312 | 482.6675 | 514.8119
2335.6135 | 524.044 | 508.1715 | 482.654 | 514.7071
2336.6135 | 524.1196 | 508.2108 | 482.6563 | 514.8809
2337.6135 | 524.0906 | 508.0992 | 482.6107 | 515.0082
2338.6135 | 523.9938 | 508.0767 | 482.7953 | 515.2782
2339.6135 | 523.9667 | 508.172 | 482.9443 | 515.3829
2340.6135 | 524.0578 | 508.2261 | 482.8191 | 515.461
2341.6135 | 523.8892 | 508.269 | 482.5959 | 515.5953
2342.6135 | 523.7549 | 508.2883 | 482.579 | 515.821
2343.6135 | 523.6664 | 508.3156 | 482.5448 | 515.7126
2344.6135 | 523.669 | 508.3433 | 482.5777 | 515.6713
2345.6135 | 523.678 | 508.3751 | 482.5709 | 515.9381
2346.6135 | 523.7146 | 508.4021 | 482.6451 | 515.7086
2347.6135 | 523.7561 | 508.422 | 482.7139 | 515.9617
2348.6135 | 523.8191 | 508.46 | 482.8076 | 515.9648
2349.6135 | 523.9284 | 508.4811 | 482.6374 | 516.2097
2350.6135 | 524.0099 | 508.4981 | 482.5089 | 516.275
2351.6135 | 524.0422 | 508.5156 | 482.38 | 516.6107
2352.6135 | 523.928 | 508.5167 | 482.3272 | 516.7841
2353.6135 | 523.7336 | 508.5472 | 482.7286 | 516.8415
2354.6135 | 523.659 | 508.5848 | 482.75 | 517.1178
2355.6135 | 523.6224 | 508.5503 | 482.7474 | 517.4836
2356.6135 | 523.4685 | 508.558 | 482.7824 | 517.5908
2357.6135 | 523.3854 | 508.6001 | 482.9191 | 517.5825
2358.6135 | 523.3423 | 508.6417 | 483.1313 | 517.6556
2359.6135 | 523.5124 | 508.658 | 483.1962 | 517.5549
2360.6135 | 523.5419 | 508.6585 | 483.0271 | 517.6867
2361.6135 | 523.4309 | 508.6623 | 482.9876 | 517.76
2362.6135 | 523.4973 | 508.6887 | 483.0755 | 517.8354
2363.6135 | 523.4671 | 508.6318 | 483.1864 | 517.9359
2364.6135 | 523.4402 | 508.5662 | 482.8815 | 518.1247
2365.6135 | 523.4428 | 508.6095 | 482.9641 | 518.1854
2366.6135 | 523.5326 | 508.5915 | 482.8586 | 518.3202
2367.6135 | 523.5515 | 508.6029 | 482.9705 | 518.5105
2368.6135 | 523.5394 | 508.6547 | 483.1518 | 518.6851
2369.6135 | 523.6607 | 508.6817 | 483.1827 | 518.7029
2370.6135 | 523.641 | 508.6998 | 483.2649 | 518.9157
2371.6135 | 523.5908 | 508.707 | 483.3952 | 519.1667
2372.6135 | 523.6322 | 508.7152 | 483.2582 | 519.159
2373.6135 | 523.6867 | 508.7461 | 483.1365 | 519.4334
2374.6135 | 523.8813 | 508.7661 | 483.1696 | 519.5184
2375.6135 | 523.8058 | 508.7851 | 483.3171 | 520.0173
2376.6135 | 523.864 | 508.7801 | 483.4203 | 519.9801
2377.6135 | 523.8766 | 508.8161 | 483.2117 | 519.9154
2378.6135 | 523.91 | 508.8516 | 483.2686 | 520.0712
2379.6135 | 523.8798 | 508.8542 | 483.3322 | 520.2492
2380.6135 | 523.9089 | 508.8734 | 482.9692 | 520.4338
2381.6135 | 523.8376 | 508.8955 | 483.1006 | 520.5596
2382.6135 | 523.8481 | 508.8955 | 483.223 | 520.746
2383.6135 | 523.778 | 508.8955 | 483.2947 | 520.9752
2384.6135 | 523.7363 | 508.9333 | 483.5072 | 520.9364
2385.6135 | 523.7386 | 508.9087 | 483.7004 | 521.0587
2386.6135 | 523.6999 | 508.9636 | 483.4978 | 521.0433
2387.6135 | 523.6532 | 509.0094 | 483.4256 | 521.4435
2388.6135 | 523.6738 | 509.0082 | 483.2987 | 521.5209
2389.6135 | 523.687 | 509.0418 | 483.2443 | 521.6956
2390.6135 | 523.7512 | 509.0785 | 483.3317 | 521.2839
2391.6135 | 523.8156 | 509.068 | 483.5587 | 521.4433
2392.6135 | 523.7698 | 509.0872 | 483.6681 | 521.5814
2393.6135 | 523.7299 | 509.1406 | 483.617 | 521.6666
2394.6135 | 523.6898 | 509.1679 | 483.6706 | 522.0622
2395.6135 | 523.6539 | 509.2498 | 483.6322 | 521.9883
2396.6135 | 523.6462 | 509.2869 | 483.6412 | 522.1245
2397.6135 | 523.5804 | 509.3405 | 483.3188 | 522.1174
2398.6135 | 523.5059 | 509.3864 | 483.4253 | 522.232
2399.6135 | 523.3695 | 509.4097 | 483.4683 | 522.4226
2400.6135 | 523.3335 | 509.5097 | 483.5386 | 522.424
2401.6135 | 523.4792 | 509.521 | 483.2874 | 522.6055
2402.6135 | 523.4886 | 509.577 | 483.351 | 522.9311
2403.6135 | 523.4852 | 509.6485 | 483.4998 | 523.0615
2404.6135 | 523.5006 | 509.663 | 483.6054 | 523.2924
2405.6135 | 523.4669 | 509.7148 | 483.7456 | 523.3673
2406.6135 | 523.4845 | 509.7809 | 483.7765 | 523.5033
2407.6135 | 523.3783 | 509.8391 | 483.6584 | 523.684
2408.6135 | 523.2523 | 509.9099 | 483.7207 | 523.8586
2409.6135 | 523.2341 | 509.9286 | 483.7832 | 523.9965
2410.6135 | 523.1386 | 509.9714 | 483.957 | 524.1465
2411.6135 | 523.0432 | 509.9942 | 483.9927 | 524.4327
2412.6135 | 523.0737 | 509.9995 | 483.7942 | 524.9269
2413.6135 | 523.0831 | 510.008 | 483.6223 | 524.9547
2414.6135 | 523.133 | 510.1042 | 483.8563 | 524.9997
2415.6135 | 523.181 | 510.1602 | 483.8733 | 525.0923
2416.6135 | 523.1434 | 510.1979 | 483.9416 | 525.2936
2417.6135 | 523.1683 | 510.1919 | 484.0074 | 525.4038
2418.6135 | 523.3629 | 510.2161 | 484.0621 | 525.6123
2419.6135 | 523.4643 | 510.2437 | 483.9814 | 525.5297
2420.6135 | 523.6234 | 510.2409 | 484.1781 | 525.5755
2421.6135 | 523.551 | 510.1956 | 484.206 | 526.1253
2422.6135 | 523.4487 | 510.1914 | 484.1656 | 526.3485
2423.6135 | 523.6071 | 510.2044 | 484.167 | 526.4998
2424.6135 | 523.7598 | 510.2373 | 484.1729 | 526.7105
2425.6135 | 523.9109 | 510.1752 | 484.0984 | 526.805
2426.6135 | 524.0311 | 510.2151 | 484.1836 | 526.8962
2427.6135 | 524.0384 | 510.2952 | 484.3764 | 526.9784
2428.6135 | 524.1386 | 510.2734 | 484.3281 | 527.1906
2429.6135 | 524.2707 | 510.2523 | 484.2786 | 527.609
2430.6135 | 524.3794 | 510.3016 | 484.3056 | 527.6633
2431.6135 | 524.3095 | 510.362 | 484.104 | 527.8184
2432.6135 | 524.4311 | 510.3819 | 484.1152 | 528.0396
2433.6135 | 524.5754 | 510.4202 | 484.2208 | 528.3394
2434.6135 | 524.7216 | 510.489 | 484.3042 | 528.3901
2435.6135 | 524.7662 | 510.4745 | 484.0703 | 528.4165
2436.6135 | 524.7627 | 510.436 | 484.1982 | 528.5242
2437.6135 | 524.7654 | 510.3789 | 484.035 | 528.7373
2438.6135 | 524.7589 | 510.3813 | 484.2108 | 528.8664
2439.6135 | 524.8858 | 510.3438 | 484.2692 | 529.1217
2440.6135 | 524.8916 | 510.3417 | 484.3415 | 529.3499
2441.6135 | 524.9634 | 510.3906 | 484.3424 | 529.4147
2442.6135 | 524.918 | 510.4231 | 484.0377 | 529.5911
2443.6135 | 524.8495 | 510.4209 | 484.1726 | 529.7105
2444.6135 | 524.8965 | 510.5022 | 484.2396 | 529.9027
2445.6135 | 524.9338 | 510.5261 | 484.2043 | 529.998
2446.6135 | 524.7553 | 510.5534 | 484.1279 | 530.2227
2447.6135 | 524.6 | 510.5825 | 484.2055 | 530.4527
2448.6135 | 524.5642 | 510.6195 | 484.4533 | 530.6833
2449.6135 | 524.5446 | 510.6192 | 484.5119 | 530.8715
2450.6135 | 524.6685 | 510.677 | 484.6113 | 531.0226
2451.6135 | 524.7176 | 510.7116 | 484.4198 | 531.1534
2452.6135 | 524.7402 | 510.7549 | 484.5667 | 531.3422
2453.6135 | 524.6923 | 510.7495 | 484.6896 | 531.6289
2454.6135 | 524.6453 | 510.7575 | 484.5164 | 531.7963
2455.6135 | 524.6453 | 510.772 | 484.6242 | 532.1292
2456.6135 | 524.5311 | 510.801 | 484.6914 | 532.329
2457.6135 | 524.4801 | 510.8108 | 484.8024 | 532.4352
2458.6135 | 524.5594 | 510.8671 | 484.8271 | 532.6846
2459.6135 | 524.5042 | 510.8868 | 484.8015 | 532.8812
2460.6135 | 524.4486 | 510.8881 | 484.8658 | 533.0586
2461.6135 | 524.3138 | 510.9174 | 484.973 | 533.3157
2462.6135 | 524.1854 | 510.9101 | 484.9619 | 533.5841
2463.6135 | 524.1403 | 510.9278 | 484.9394 | 533.7332
2464.6135 | 524.1746 | 510.9421 | 485.0312 | 533.8183
2465.6135 | 524.2899 | 511.0072 | 485.1328 | 534.1899
2466.6135 | 524.3307 | 511.0223 | 484.6328 | 534.3742
2467.6135 | 524.4927 | 511.1051 | 484.7814 | 534.7486
2468.6135 | 524.4788 | 511.1548 | 484.8616 | 534.9556
2469.6135 | 524.4345 | 511.1943 | 484.9696 | 535.0523
2470.6135 | 524.4749 | 511.2841 | 485.0334 | 535.3987
2471.6135 | 524.471 | 511.3478 | 485.0992 | 535.6799
2472.6135 | 524.343 | 511.4021 | 484.9947 | 535.9255
2473.6135 | 524.2189 | 511.426 | 485.1265 | 536.2804
2474.6135 | 524.2108 | 511.4993 | 485.0139 | 536.4199
2475.6135 | 524.0908 | 511.5345 | 484.7433 | 536.806
2476.6135 | 524.0009 | 511.6159 | 484.6645 | 537.1455
2477.6135 | 523.905 | 511.6448 | 484.8682 | 537.3282
2478.6135 | 523.8547 | 511.6738 | 484.8062 | 536.9717
2479.6135 | 523.7176 | 511.6429 | 484.8223 | 537.4606
2480.6135 | 523.5127 | 511.6322 | 485.0825 | 537.7044
2481.6135 | 523.485 | 511.615 | 485.1501 | 537.9621
2482.6135 | 523.571 | 511.6338 | 485.2393 | 538.0466
2483.6135 | 523.5592 | 511.6425 | 485.0959 | 538.3654
2484.6135 | 523.5998 | 511.679 | 485.0268 | 538.744
2485.6135 | 523.6467 | 511.7206 | 485.2077 | 538.9726
2486.6135 | 523.6101 | 511.73 | 485.0415 | 539.2395
2487.6135 | 523.7507 | 511.7762 | 484.9371 | 539.5138
2488.6135 | 523.8845 | 511.8078 | 484.9716 | 539.8131
2489.6135 | 523.8838 | 511.839 | 485.1898 | 540.1988
2490.6135 | 523.6921 | 511.9163 | 485.2634 | 540.0716
2491.6135 | 523.6882 | 511.9441 | 485.2799 | 540.4108
2492.6135 | 523.6382 | 511.954 | 485.3475 | 540.5649
2493.6135 | 523.5551 | 511.9561 | 485.2902 | 540.9298
2494.6135 | 523.5258 | 511.9708 | 485.1879 | 541.1436
2495.6135 | 523.6098 | 512.0092 | 485.3588 | 541.5133
2496.6135 | 523.6527 | 512.0643 | 485.4093 | 541.8019
2497.6135 | 523.7369 | 512.1014 | 485.4086 | 542.2672
2498.6135 | 523.7901 | 512.1716 | 485.5682 | 542.573
2499.6135 | 523.6659 | 512.2557 | 485.5512 | 542.8118
2500.6135 | 523.6309 | 512.2884 | 485.6003 | 542.845
2501.6135 | 523.6287 | 512.3078 | 485.7395 | 543.2094
2502.6135 | 523.6027 | 512.373 | 485.4435 | 543.5057
2503.6135 | 523.5817 | 512.452 | 485.0658 | 543.694
2504.6135 | 523.6453 | 512.51 | 485.0343 | 544.2037
2505.6135 | 523.7239 | 512.5283 | 485.2433 | 544.4113
2506.6135 | 523.6156 | 512.5816 | 485.4483 | 544.5099
2507.6135 | 523.7381 | 512.6206 | 485.4362 | 544.8499
2508.6135 | 523.5762 | 512.6474 | 485.4978 | 545.3168
2509.6135 | 523.6033 | 512.7017 | 485.4997 | 545.6669
2510.6135 | 523.5218 | 512.7422 | 485.5951 | 545.8048
2511.6135 | 523.3906 | 512.7839 | 485.7297 | 546.2262
2512.6135 | 523.418 | 512.8337 | 485.78 | 546.4701
2513.6135 | 523.3308 | 512.8643 | 485.313 | 546.5528
2514.6135 | 523.1697 | 512.9067 | 485.4427 | 546.9158
2515.6135 | 523.1327 | 512.9587 | 485.5662 | 547.1202
2516.6135 | 523.1022 | 512.9909 | 485.6793 | 547.4259
2517.6135 | 523.2258 | 512.9984 | 485.7512 | 547.5163
2518.6135 | 523.377 | 513.0411 | 485.7051 | 547.2944
2519.6135 | 523.3975 | 513.0478 | 485.4594 | 547.1773
2520.6135 | 523.2104 | 512.9987 | 485.6284 | 546.8911
2521.6135 | 523.1518 | 512.9408 | 485.7555 | 546.8402
2522.6135 | 523.2203 | 512.8321 | 485.4778 | 546.9374
2523.6135 | 523.2003 | 512.746 | 485.6671 | 546.9824
2524.6135 | 523.2299 | 512.6442 | 485.5944 | 547.043
2525.6135 | 523.2428 | 512.5458 | 485.3858 | 547.1292
2526.6135 | 523.2627 | 512.5007 | 485.4262 | 547.0705
2527.6135 | 523.2492 | 512.364 | 485.7475 | 547.1294
2528.6135 | 523.1528 | 512.2491 | 485.8232 | 547.1497
2529.6135 | 522.9522 | 512.1756 | 485.6976 | 547.1088
2530.6135 | 522.8951 | 512.0442 | 485.4483 | 547.1288
2531.6135 | 522.9203 | 511.9417 | 485.2973 | 547.1962
2532.6135 | 523.0481 | 511.8953 | 485.4088 | 547.2589
2533.6135 | 523.1277 | 511.8456 | 485.5931 | 547.0842
2534.6135 | 523.347 | 511.7183 | 485.816 | 547.1722
2535.6135 | 523.3602 | 511.6265 | 485.9986 | 547.2472
2536.6135 | 523.3703 | 511.5238 | 486.0368 | 547.2405
2537.6135 | 523.3438 | 511.4663 | 485.9745 | 547.331
2538.6135 | 523.2188 | 511.3879 | 486.0276 | 547.2513
2539.6135 | 523.1475 | 511.2699 | 485.5497 | 547.3627
2540.6135 | 523.2314 | 511.1687 | 485.3835 | 547.3218
2541.6135 | 523.2102 | 511.091 | 485.6638 | 547.4996
2542.6135 | 523.1664 | 511.0107 | 485.7992 | 547.6191
2543.6135 | 523.1754 | 510.9242 | 485.7689 | 547.6313
2544.6135 | 523.1489 | 510.7923 | 485.6708 | 547.5495
2545.6135 | 523.1653 | 510.7269 | 485.9101 | 547.8137
2546.6135 | 523.2103 | 510.6524 | 485.9277 | 547.9868
2547.6135 | 523.1661 | 510.5705 | 486.0421 | 547.865
2548.6135 | 523.069 | 510.5107 | 486.2447 | 547.6851
2549.6135 | 523.0298 | 510.3692 | 486.3228 | 547.8057
2550.6135 | 523.0449 | 510.2223 | 486.229 | 548.1963
2551.6135 | 522.9655 | 510.1721 | 486.0788 | 548.4044
2552.6135 | 523.1016 | 510.0988 | 486.028 | 548.5252
2553.6135 | 523.2319 | 510.0095 | 486.0924 | 548.6919
2554.6135 | 523.2339 | 509.877 | 485.9746 | 548.6387
2555.6135 | 523.2493 | 509.8707 | 486.1048 | 548.9975
2556.6135 | 523.3288 | 509.804 | 486.2521 | 549.2106
2557.6135 | 523.3286 | 509.7439 | 486.3335 | 549.4879
2558.6135 | 523.2782 | 509.7045 | 486.3556 | 549.6576
2559.6135 | 523.4724 | 509.628 | 486.3133 | 549.8063
2560.6135 | 523.5093 | 509.5014 | 486.2812 | 550.0211
2561.6135 | 523.5792 | 509.4337 | 486.1269 | 549.9242
2562.6135 | 523.5444 | 509.3464 | 486.2396 | 550.1323
2563.6135 | 523.6829 | 509.2882 | 486.3744 | 550.3933
2564.6135 | 523.6768 | 509.2375 | 486.2292 | 550.374
2565.6135 | 523.6375 | 509.1633 | 486.294 | 550.4848
2566.6135 | 523.7823 | 509.0789 | 486.3447 | 550.4388
2567.6135 | 523.698 | 508.9915 | 486.4717 | 550.775
2568.6135 | 523.6732 | 508.9401 | 486.5087 | 550.9147
2569.6135 | 523.7109 | 508.8535 | 486.5676 | 550.7483
2570.6135 | 523.7256 | 508.8177 | 486.5803 | 550.9337
2571.6135 | 523.8041 | 508.7562 | 486.3759 | 550.9882
2572.6135 | 523.8325 | 508.7019 | 486.189 | 551.0983
2573.6135 | 523.899 | 508.6581 | 486.2679 | 551.1111
2574.6135 | 523.8996 | 508.5712 | 486.0774 | 551.3097
2575.6135 | 523.8502 | 508.5246 | 486.0281 | 551.4022
2576.6135 | 523.7878 | 508.4704 | 486.0721 | 551.3888
2577.6135 | 523.6644 | 508.4125 | 486.2555 | 551.2614
2578.6135 | 523.6608 | 508.2852 | 486.4021 | 551.0838
2579.6135 | 523.4991 | 508.1886 | 486.1893 | 551.1564
2580.6135 | 523.4808 | 508.1307 | 486.213 | 551.4573
2581.6135 | 523.478 | 508.1302 | 486.2227 | 551.7523
2582.6135 | 523.4677 | 508.0444 | 486.2851 | 551.8183
2583.6135 | 523.4288 | 507.9801 | 486.4546 | 551.4924
2584.6135 | 523.3643 | 507.9264 | 486.4901 | 551.7183
2585.6135 | 523.4958 | 507.8851 | 486.4695 | 552.0665
2586.6135 | 523.5998 | 507.8239 | 486.2632 | 551.9741
2587.6135 | 523.6098 | 507.7345 | 486.1224 | 551.8536
2588.6135 | 523.4903 | 507.6627 | 486.3693 | 552.091
2589.6135 | 523.4973 | 507.6196 | 486.3087 | 552.1556
2590.6135 | 523.4951 | 507.5664 | 486.0573 | 552.4081
2591.6135 | 523.4432 | 507.5196 | 486.1374 | 552.5809
2592.6135 | 523.3455 | 507.4932 | 486.3215 | 552.9927
2593.6135 | 523.3616 | 507.4319 | 486.4654 | 553.0327
2594.6135 | 523.3335 | 507.3262 | 486.4631 | 553.1098
2595.6135 | 523.1524 | 507.2986 | 486.3938 | 553.0577
2596.6135 | 523.0384 | 507.2579 | 486.1548 | 552.9271
2597.6135 | 523.025 | 507.1987 | 486.2023 | 553.127
2598.6135 | 523.0615 | 507.0928 | 486.4284 | 553.3684
2599.6135 | 523.0666 | 507.0134 | 486.3441 | 553.3816
2600.6135 | 523.0673 | 507.0017 | 486.3752 | 553.4279
2601.6135 | 523.1041 | 506.9719 | 486.5025 | 553.3761
2602.6135 | 523.1463 | 506.9243 | 486.6019 | 553.7186
2603.6135 | 523.119 | 506.8159 | 486.5433 | 554.4463
2604.6135 | 523.1281 | 506.7904 | 486.6012 | 555.066
2605.6135 | 523.0406 | 506.7281 | 486.5261 | 554.8517
2606.6135 | 523.124 | 506.7154 | 486.2193 | 555.0684
2607.6135 | 522.9947 | 506.6545 | 486.2573 | 554.9382
2608.6135 | 523.1228 | 506.6217 | 486.3685 | 555.0239
2609.6135 | 523.1836 | 506.5959 | 486.5241 | 554.9975
2610.6135 | 523.2041 | 506.5483 | 486.5874 | 554.9717
2611.6135 | 523.1512 | 506.5181 | 486.4813 | 555.2934
2612.6135 | 523.2115 | 506.4986 | 486.5941 | 555.3782
2613.6135 | 523.1716 | 506.4239 | 486.7043 | 555.4861
2614.6135 | 523.2033 | 506.3466 | 486.6519 | 555.5657
2615.6135 | 523.2505 | 506.2877 | 486.7363 | 555.5141
2616.6135 | 523.303 | 506.2429 | 486.667 | 555.5879
2617.6135 | 523.4058 | 506.2456 | 486.5932 | 555.5228
2618.6135 | 523.3898 | 506.2019 | 486.5803 | 555.5909
2619.6135 | 523.4087 | 506.0501 | 486.4655 | 555.4462
2620.6135 | 523.491 | 506.091 | 486.4755 | 555.7034
2621.6135 | 523.4799 | 506.0803 | 486.3441 | 555.4591
2622.6135 | 523.54 | 506.0026 | 486.5645 | 555.8288
2623.6135 | 523.5317 | 506.0072 | 486.7037 | 556.1076
2624.6135 | 523.6904 | 505.9475 | 486.8386 | 556.35
2625.6135 | 523.8842 | 505.9324 | 486.7953 | 556.5365
2626.6135 | 524.009 | 505.9012 | 486.7891 | 556.6525
2627.6135 | 524.0681 | 505.8595 | 486.7934 | 557.007
2628.6135 | 524.0914 | 505.8161 | 486.7616 | 557.1586
2629.6135 | 524.039 | 505.7799 | 486.8836 | 557.2941
2630.6135 | 523.8796 | 505.7141 | 486.9831 | 557.2634
2631.6135 | 523.719 | 505.6695 | 486.9238 | 557.2351
2632.6135 | 523.6793 | 505.647 | 486.6433 | 557.3234
2633.6135 | 523.6495 | 505.5719 | 486.6409 | 557.3848
2634.6135 | 523.5274 | 505.5415 | 486.7635 | 557.4641
2635.6135 | 523.6173 | 505.5333 | 486.6963 | 557.5318
2636.6135 | 523.574 | 505.4359 | 486.6213 | 557.4548
2637.6135 | 523.5073 | 505.4376 | 486.8022 | 557.6764
2638.6135 | 523.5223 | 505.3794 | 487.0595 | 557.5714
2639.6135 | 523.4296 | 505.3611 | 487.0773 | 557.6496
2640.6135 | 523.4158 | 505.3279 | 487.0048 | 557.8503
2641.6135 | 523.3957 | 505.2587 | 486.9676 | 557.8469
2642.6135 | 523.3465 | 505.2548 | 487.0471 | 557.7698
2643.6135 | 523.3165 | 505.2056 | 486.9799 | 558.4321
2644.6135 | 523.4724 | 505.1834 | 486.9694 | 558.587
2645.6135 | 523.636 | 505.1587 | 486.9429 | 558.5884
2646.6135 | 523.5761 | 505.111 | 486.9257 | 558.639
2647.6135 | 523.4905 | 505.0585 | 486.9733 | 558.5402
2648.6135 | 523.4755 | 505.0487 | 487.0562 | 558.7788
2649.6135 | 523.4317 | 505.0458 | 486.8774 | 559.2336
2650.6135 | 523.6105 | 504.9992 | 486.9241 | 559.3667
2651.6135 | 523.7435 | 504.9633 | 487.001 | 559.3949
2652.6135 | 523.9349 | 504.9303 | 486.8447 | 559.7078
2653.6135 | 523.925 | 504.9053 | 486.5739 | 559.8613
2654.6135 | 523.895 | 504.8951 | 486.6148 | 559.8538
2655.6135 | 523.9022 | 504.8785 | 486.7894 | 560.4061
2656.6135 | 523.8126 | 504.8734 | 486.7281 | 560.642
2657.6135 | 523.9069 | 504.8297 | 486.7937 | 561.0847
2658.6135 | 523.9637 | 504.8183 | 486.5201 | 561.102
2659.6135 | 523.9612 | 504.7709 | 486.592 | 561.7547
2660.6135 | 524.0279 | 504.775 | 486.7978 | 562.1483
2661.6135 | 524.0615 | 504.7376 | 486.454 | 562.2119
2662.6135 | 524.0603 | 504.7199 | 486.6171 | 562.1696
2663.6135 | 523.9529 | 504.6456 | 486.6422 | 561.876
2664.6135 | 523.939 | 504.618 | 486.7756 | 562.0044
2665.6135 | 524.0558 | 504.6198 | 486.8591 | 562.2154
2666.6135 | 524.0262 | 504.6394 | 486.9521 | 562.018
2667.6135 | 523.9714 | 504.6228 | 487.0539 | 562.3051
2668.6135 | 524.0371 | 504.5255 | 487.0649 | 562.4973
2669.6135 | 524.0267 | 504.5421 | 486.9988 | 562.8273
2670.6135 | 523.9697 | 504.4907 | 486.9959 | 562.8286
2671.6135 | 524.0404 | 504.4767 | 486.994 | 562.6195
2672.6135 | 524.0451 | 504.492 | 486.9839 | 562.9004
2673.6135 | 523.9757 | 504.4735 | 487.0699 | 562.8848
2674.6135 | 524.0448 | 504.4313 | 486.9948 | 563.0791
2675.6135 | 524.071 | 504.4019 | 486.9287 | 563.2051
2676.6135 | 524.0083 | 504.3859 | 486.9396 | 563.2512
2677.6135 | 524.095 | 504.3869 | 486.8591 | 563.3672
2678.6135 | 524.0878 | 504.2832 | 486.8986 | 563.3293
2679.6135 | 523.9825 | 504.2206 | 486.722 | 563.3504
2680.6135 | 523.8306 | 504.2588 | 486.8722 | 563.57
2681.6135 | 523.6992 | 504.2991 | 486.9444 | 563.2291
2682.6135 | 523.561 | 504.278 | 486.9722 | 563.8092
2683.6135 | 523.4098 | 504.2406 | 487.0005 | 563.9088
2684.6135 | 523.3233 | 504.2366 | 486.7414 | 564.121
2685.6135 | 523.2313 | 504.2044 | 486.6848 | 564.1959
2686.6135 | 523.0565 | 504.2354 | 486.8631 | 564.3835
2687.6135 | 523.0794 | 504.1993 | 486.9215 | 564.435
2688.6135 | 523.1033 | 504.1626 | 486.8965 | 564.1654
2689.6135 | 523.1865 | 504.1687 | 486.9241 | 564.1797
2690.6135 | 523.2724 | 504.1458 | 487.013 | 564.3745
2691.6135 | 523.2278 | 504.1232 | 486.9316 | 564.5865
2692.6135 | 523.2327 | 504.1074 | 486.8189 | 564.6361
2693.6135 | 523.2821 | 504.0681 | 486.8352 | 564.3822
2694.6135 | 523.3398 | 504.0432 | 486.7011 | 564.6121
2695.6135 | 523.3885 | 504.0244 | 486.7781 | 564.7218
2696.6135 | 523.4032 | 503.9917 | 486.747 | 565.1581
2697.6135 | 523.4347 | 504.0052 | 486.8729 | 565.0427
2698.6135 | 523.6051 | 504.0039 | 486.9521 | 565.1806
2699.6135 | 523.6147 | 503.9646 | 486.848 | 565.1351
2700.6135 | 523.757 | 503.9832 | 486.8997 | 565.5294
2701.6135 | 523.9128 | 503.9768 | 486.7875 | 565.5388
2702.6135 | 523.8208 | 503.958 | 486.8629 | 565.6334
2703.6135 | 523.8384 | 503.915 | 486.922 | 565.7262
2704.6135 | 523.7845 | 503.8921 | 486.8998 | 565.732
2705.6135 | 523.7736 | 503.8932 | 486.989 | 565.7517
2706.6135 | 523.87 | 503.903 | 486.5194 | 565.5721
2707.6135 | 523.9225 | 503.9032 | 486.8104 | 565.6115
2708.6135 | 523.9609 | 503.8501 | 486.8784 | 565.9347
2709.6135 | 524.0173 | 503.8454 | 486.9569 | 566.2156
2710.6135 | 523.9313 | 503.8202 | 486.7527 | 565.8723
2711.6135 | 523.9626 | 503.8107 | 486.4265 | 565.998
2712.6135 | 523.9302 | 503.8168 | 486.6215 | 566.1092
2713.6135 | 524.0469 | 503.8074 | 486.5863 | 566.4404
2714.6135 | 524.1774 | 503.785 | 486.6171 | 566.386
2715.6135 | 524.1363 | 503.7858 | 486.5593 | 566.4384
2716.6135 | 523.8409 | 503.7758 | 486.6287 | 566.55
2717.6135 | 523.693 | 503.7145 | 486.709 | 566.3575
2718.6135 | 523.4976 | 503.7048 | 486.8209 | 566.554
2719.6135 | 523.4021 | 503.6502 | 486.7381 | 566.6974
2720.6135 | 523.3707 | 503.6467 | 486.7352 | 567.1259
2721.6135 | 523.3078 | 503.6542 | 486.7052 | 566.9565
2722.6135 | 523.1847 | 503.638 | 486.5719 | 567.1734
2723.6135 | 523.1371 | 503.6442 | 486.639 | 567.3887
2724.6135 | 523.0758 | 503.6134 | 486.6461 | 567.6167
2725.6135 | 523.0633 | 503.5988 | 486.3807 | 567.3027
2726.6135 | 523.1426 | 503.5716 | 486.5426 | 567.4743
2727.6135 | 523.1292 | 503.5661 | 486.6585 | 567.6778
2728.6135 | 523.1291 | 503.5389 | 486.706 | 567.6852
2729.6135 | 523.059 | 503.5351 | 486.6591 | 567.5196
2730.6135 | 522.9954 | 503.4858 | 486.6482 | 567.5389
2731.6135 | 522.9459 | 503.5144 | 486.7448 | 567.518
2732.6135 | 522.9655 | 503.4931 | 486.4781 | 567.6937
2733.6135 | 523.1317 | 503.4715 | 486.528 | 567.5714
2734.6135 | 523.2539 | 503.4386 | 486.6461 | 567.1693
2735.6135 | 523.4107 | 503.418 | 486.825 | 567.7515
2736.6135 | 523.5331 | 503.3606 | 487.0035 | 566.9766
2737.6135 | 523.5819 | 503.3782 | 486.9506 | 567.0811
2738.6135 | 523.4567 | 503.3974 | 486.8463 | 567.1384
2739.6135 | 523.3478 | 503.3692 | 486.6546 | 567.5701
2740.6135 | 523.2706 | 503.3351 | 486.5828 | 567.898
2741.6135 | 523.2727 | 503.3086 | 486.747 | 567.5374
2742.6135 | 523.3049 | 503.3044 | 486.7531 | 567.5903
2743.6135 | 523.2575 | 503.3021 | 486.8278 | 568.3282
2744.6135 | 523.2852 | 503.3003 | 486.863 | 567.9618
2745.6135 | 523.2431 | 503.2737 | 486.7276 | 568.2468
2746.6135 | 523.2661 | 503.26 | 486.8086 | 567.9537
2747.6135 | 523.292 | 503.2379 | 486.9525 | 568.3369
2748.6135 | 523.3381 | 503.2267 | 486.7612 | 568.3182
2749.6135 | 523.4112 | 503.2311 | 486.8113 | 568.0231
2750.6135 | 523.467 | 503.2019 | 486.7714 | 568.2451
2751.6135 | 523.3473 | 503.191 | 486.5934 | 567.9947
2752.6135 | 523.292 | 503.1797 | 486.5242 | 568.0072
2753.6135 | 523.2465 | 503.1551 | 486.4326 | 567.7658
2754.6135 | 523.1435 | 503.1167 | 486.6131 | 568.1413
2755.6135 | 523.152 | 503.0801 | 486.7717 | 568.4894
2756.6135 | 523.1615 | 503.0651 | 486.8047 | 568.4046
2757.6135 | 523.1857 | 503.0386 | 486.6874 | 568.1716
2758.6135 | 523.1745 | 503.0586 | 486.8747 | 568.4207
2759.6135 | 523.2166 | 502.9999 | 486.9434 | 568.3705
2760.6135 | 523.1474 | 502.9939 | 486.9397 | 568.8224
2761.6135 | 523.0705 | 502.9803 | 486.9323 | 568.8297
2762.6135 | 523.1078 | 502.9621 | 486.7877 | 568.5384
2763.6135 | 523.1241 | 502.9826 | 486.5966 | 569.146
2764.6135 | 523.1216 | 502.9772 | 486.7447 | 569.1342
2765.6135 | 523.3619 | 502.9436 | 486.9684 | 569.4678
2766.6135 | 523.5981 | 502.9585 | 486.9902 | 569.5829
2767.6135 | 523.6742 | 502.959 | 486.9705 | 569.6031
2768.6135 | 523.7578 | 502.9739 | 486.8185 | 569.4422
2769.6135 | 523.6344 | 502.9903 | 486.7531 | 569.395
2770.6135 | 523.7033 | 502.989 | 486.9229 | 569.7062
2771.6135 | 523.8153 | 502.9704 | 486.8628 | 569.6706
2772.6135 | 523.848 | 502.9274 | 486.645 | 569.2096
2773.6135 | 523.8957 | 502.8908 | 486.6022 | 569.2403
2774.6135 | 523.83 | 502.9187 | 486.6279 | 569.6393
2775.6135 | 523.7789 | 502.933 | 486.7687 | 569.7368
2776.6135 | 523.6481 | 502.9046 | 486.8486 | 569.8434
2777.6135 | 523.5673 | 502.885 | 486.9362 | 569.9947
2778.6135 | 523.5681 | 502.8725 | 486.7724 | 569.6337
2779.6135 | 523.6553 | 502.8891 | 486.6039 | 570.1985
2780.6135 | 523.6089 | 502.8736 | 486.4736 | 569.7839
2781.6135 | 523.4815 | 502.868 | 486.5944 | 570.0225
2782.6135 | 523.5087 | 502.8632 | 486.8268 | 570.1176
2783.6135 | 523.487 | 502.8202 | 486.8603 | 569.9374
2784.6135 | 523.5401 | 502.8603 | 486.6624 | 570.4095
2785.6135 | 523.5984 | 502.8645 | 486.6763 | 570.0782
2786.6135 | 523.6748 | 502.8323 | 486.7696 | 570.1434
2787.6135 | 523.7435 | 502.8559 | 486.8357 | 570.2352
2788.6135 | 523.8509 | 502.8693 | 486.9663 | 570.4296
2789.6135 | 524.0072 | 502.8379 | 487.0325 | 570.5141
2790.6135 | 524.1618 | 502.8363 | 486.9303 | 570.4003
2791.6135 | 524.1027 | 502.8559 | 486.987 | 570.6607
2792.6135 | 524.0699 | 502.7844 | 487.0002 | 570.6904
2793.6135 | 524.1614 | 502.7698 | 486.9419 | 570.5122
2794.6135 | 524.138 | 502.7282 | 487.016 | 570.9285
2795.6135 | 524.2384 | 502.7009 | 486.9376 | 570.5478
2796.6135 | 524.0891 | 502.7401 | 486.9777 | 570.597
2797.6135 | 524.0677 | 502.7388 | 486.8366 | 570.2862
2798.6135 | 523.9846 | 502.7485 | 486.7923 | 570.4737
2799.6135 | 523.9935 | 502.7468 | 486.8211 | 571.0212
2800.6135 | 523.9851 | 502.7123 | 486.8355 | 570.7924
2801.6135 | 523.9931 | 502.7309 | 486.7774 | 570.9301
2802.6135 | 523.9231 | 502.7391 | 486.6608 | 570.8594
2803.6135 | 523.9147 | 502.7315 | 486.7239 | 571.2242
2804.6135 | 523.9699 | 502.7556 | 486.7895 | 571.3519
2805.6135 | 523.8451 | 502.7488 | 486.7807 | 571.4049
2806.6135 | 523.7041 | 502.7216 | 486.7602 | 570.9425
2807.6135 | 523.7042 | 502.7276 | 486.8956 | 571.3208
2808.6135 | 523.6467 | 502.6936 | 487.0241 | 570.9849
2809.6135 | 523.7078 | 502.6978 | 486.8921 | 571.5272
2810.6135 | 523.7092 | 502.6961 | 486.7641 | 571.2186
2811.6135 | 523.695 | 502.701 | 486.7349 | 571.6025
2812.6135 | 523.7144 | 502.6953 | 486.6612 | 571.6586
2813.6135 | 523.7622 | 502.6133 | 486.5984 | 571.9816
2814.6135 | 523.8069 | 502.6598 | 486.7088 | 571.8576
2815.6135 | 523.8555 | 502.6857 | 486.7665 | 571.6884
2816.6135 | 524.0487 | 502.6713 | 486.8723 | 572.3826
2817.6135 | 524.1995 | 502.6599 | 486.5641 | 572.2051
2818.6135 | 524.3923 | 502.6284 | 486.5273 | 572.0747
2819.6135 | 524.5575 | 502.6226 | 486.6458 | 572.3909
2820.6135 | 524.5622 | 502.642 | 486.5379 | 572.1391
2821.6135 | 524.6325 | 502.6579 | 486.6739 | 572.2014
2822.6135 | 524.6016 | 502.6592 | 486.5863 | 572.2767
2823.6135 | 524.681 | 502.6403 | 486.6054 | 572.3222
2824.6135 | 524.6862 | 502.6566 | 486.7468 | 572.3652
2825.6135 | 524.7002 | 502.6728 | 486.7125 | 572.3958
2826.6135 | 524.7913 | 502.6724 | 486.8687 | 571.9263
2827.6135 | 524.8174 | 502.6776 | 486.9487 | 571.988
2828.6135 | 524.7925 | 502.671 | 486.9763 | 572.5927
2829.6135 | 524.7666 | 502.6548 | 487.0674 | 572.5039
2830.6135 | 524.7401 | 502.6313 | 487.0374 | 572.1146
2831.6135 | 524.7572 | 502.6526 | 487.0043 | 572.6212
2832.6135 | 524.6152 | 502.6273 | 486.9289 | 572.5181
2833.6135 | 524.5554 | 502.622 | 486.9949 | 572.6833
2834.6135 | 524.5539 | 502.6145 | 486.9813 | 572.6855
2835.6135 | 524.4837 | 502.6053 | 486.9957 | 572.5214
2836.6135 | 524.4205 | 502.6313 | 487.077 | 572.6393
2837.6135 | 524.4628 | 502.6687 | 487.1487 | 572.6934
2838.6135 | 524.47 | 502.6487 | 487.1651 | 573.0451
2839.6135 | 524.3918 | 502.6382 | 487.0974 | 572.606
2840.6135 | 524.4078 | 502.61 | 487.1635 | 572.8517
2841.6135 | 524.4824 | 502.6385 | 487.1237 | 572.9631
2842.6135 | 524.4257 | 502.6321 | 487.0698 | 572.8173
2843.6135 | 524.3178 | 502.6313 | 487.0515 | 573.0589
2844.6135 | 524.3303 | 502.6327 | 486.8788 | 572.9752
2845.6135 | 524.4697 | 502.6025 | 486.8722 | 572.9632
2846.6135 | 524.4709 | 502.6234 | 486.8189 | 573.2414
2847.6135 | 524.5038 | 502.6205 | 486.9387 | 573.0659
2848.6135 | 524.6248 | 502.6271 | 486.8528 | 573.1221
2849.6135 | 524.6006 | 502.6163 | 486.9861 | 573.2656
2850.6135 | 524.5695 | 502.6274 | 487.1387 | 573.3758
2851.6135 | 524.6688 | 502.6628 | 487.1436 | 573.1788
2852.6135 | 524.7249 | 502.661 | 487.2053 | 573.3046
2853.6135 | 524.8025 | 502.5744 | 487.1806 | 573.3897
2854.6135 | 524.6509 | 502.5754 | 486.9889 | 573.363
2855.6135 | 524.4455 | 502.5937 | 486.9327 | 573.4835
2856.6135 | 524.4395 | 502.6019 | 486.9322 | 573.5125
2857.6135 | 524.5641 | 502.6086 | 487.0667 | 573.566
2858.6135 | 524.4945 | 502.6118 | 487.0363 | 573.5882
2859.6135 | 524.3479 | 502.6134 | 486.9811 | 573.6009
2860.6135 | 524.1922 | 502.6084 | 487.0342 | 573.8418
2861.6135 | 524.1082 | 502.6006 | 487.131 | 573.9785
2862.6135 | 523.9317 | 502.5681 | 487.0848 | 574.1097
2863.6135 | 523.8455 | 502.5538 | 487.1771 | 573.9092
2864.6135 | 523.7886 | 502.5733 | 487.1189 | 574.281
2865.6135 | 523.8282 | 502.5668 | 487.0568 | 574.2541
2866.6135 | 523.8896 | 502.5746 | 486.9725 | 574.0777
2867.6135 | 523.9618 | 502.5098 | 486.9218 | 574.2652
2868.6135 | 523.9553 | 502.5338 | 486.9967 | 574.2464
2869.6135 | 523.9584 | 502.5325 | 486.9642 | 573.8494
2870.6135 | 524.042 | 502.5183 | 486.9134 | 574.3605
2871.6135 | 523.9924 | 502.5547 | 486.9169 | 574.4239
2872.6135 | 524.0144 | 502.5575 | 486.8395 | 574.0695
2873.6135 | 523.9115 | 502.568 | 486.8987 | 574.3778
2874.6135 | 523.8753 | 502.5629 | 486.8989 | 574.5367
2875.6135 | 523.907 | 502.5308 | 486.9193 | 574.5756
2876.6135 | 523.8841 | 502.5492 | 486.9935 | 574.6253
2877.6135 | 523.7554 | 502.5864 | 486.7799 | 574.3004
2878.6135 | 523.6029 | 502.5851 | 486.8378 | 574.7328
2879.6135 | 523.6015 | 502.5805 | 486.8669 | 574.7389
2880.6135 | 523.5667 | 502.5841 | 486.9133 | 574.811
2881.6135 | 523.4612 | 502.5483 | 486.7624 | 574.5487
2882.6135 | 523.4658 | 502.5478 | 486.9441 | 574.8525
2883.6135 | 523.3521 | 502.5229 | 486.7058 | 575.0475
2884.6135 | 523.4231 | 502.5463 | 486.6402 | 574.6618
2885.6135 | 523.3139 | 502.5677 | 486.8864 | 574.852
2886.6135 | 523.3546 | 502.5537 | 487.0148 | 575.1049
2887.6135 | 523.4406 | 502.5087 | 487.1311 | 574.7499
2888.6135 | 523.4331 | 502.4998 | 486.9004 | 574.8454
2889.6135 | 523.4257 | 502.5203 | 486.6981 | 575.2837
2890.6135 | 523.5749 | 502.533 | 486.827 | 574.9022
2891.6135 | 523.5196 | 502.5363 | 486.9453 | 575.3159
2892.6135 | 523.3842 | 502.5416 | 486.7284 | 574.9558
2893.6135 | 523.3288 | 502.52 | 486.7216 | 575.2399
2894.6135 | 523.5078 | 502.4955 | 486.8117 | 575.3379
2895.6135 | 523.626 | 502.4968 | 486.8706 | 575.099
2896.6135 | 523.5232 | 502.5038 | 486.7805 | 575.2687
2897.6135 | 523.4226 | 502.5097 | 486.7386 | 575.1599
2898.6135 | 523.4845 | 502.5083 | 486.5463 | 575.5837
2899.6135 | 523.493 | 502.5176 | 486.6482 | 575.685
2900.6135 | 523.4849 | 502.5126 | 486.8153 | 575.2067
2901.6135 | 523.5094 | 502.5156 | 486.9954 | 575.3157
2902.6135 | 523.578 | 502.4975 | 487.1459 | 575.165
2903.6135 | 523.569 | 502.4813 | 487.236 | 575.8186
2904.6135 | 523.621 | 502.4689 | 487.0485 | 575.1354
2905.6135 | 523.5913 | 502.4631 | 486.8054 | 575.6805
2906.6135 | 523.6211 | 502.4657 | 486.8622 | 575.6521
2907.6135 | 523.5209 | 502.4475 | 486.9822 | 575.8236
2908.6135 | 523.383 | 502.4422 | 486.9677 | 575.5301
2909.6135 | 523.2885 | 502.4506 | 486.9362 | 575.7165
2910.6135 | 523.225 | 502.4602 | 486.8354 | 575.9352
2911.6135 | 523.2737 | 502.4687 | 486.6548 | 575.9411
2912.6135 | 523.2074 | 502.4793 | 486.6616 | 575.5855
2913.6135 | 523.2157 | 502.4799 | 486.8374 | 575.6938
2914.6135 | 523.3561 | 502.4619 | 486.9589 | 575.7898
2915.6135 | 523.3001 | 502.4873 | 486.7824 | 576.1826
2916.6135 | 523.2173 | 502.4658 | 486.8695 | 576.1007
2917.6135 | 523.3631 | 502.3984 | 486.7414 | 576.171
2918.6135 | 523.5098 | 502.4009 | 486.823 | 576.1015
2919.6135 | 523.6623 | 502.446 | 486.7508 | 575.8129
2920.6135 | 523.5529 | 502.4174 | 486.8017 | 576.1071
2921.6135 | 523.3903 | 502.436 | 486.7605 | 575.9953
2922.6135 | 523.347 | 502.4483 | 486.7591 | 575.474
2923.6135 | 523.3678 | 502.4469 | 486.8574 | 575.7502
2924.6135 | 523.3849 | 502.4271 | 486.8968 | 575.9647
2925.6135 | 523.3496 | 502.4049 | 486.7775 | 576.0192
2926.6135 | 523.5538 | 502.4364 | 486.8098 | 575.9408
2927.6135 | 523.6021 | 502.4365 | 486.9169 | 576.2526
2928.6135 | 523.6523 | 502.4563 | 486.9616 | 576.2786
2929.6135 | 523.5926 | 502.4246 | 486.8115 | 576.404
2930.6135 | 523.5851 | 502.4181 | 486.8398 | 576.3606
2931.6135 | 523.763 | 502.4028 | 486.8132 | 575.8466
2932.6135 | 523.9039 | 502.4312 | 486.9574 | 575.8387
2933.6135 | 523.989 | 502.4093 | 486.7217 | 576.4648
2934.6135 | 523.9888 | 502.4039 | 486.6836 | 576.3243
2935.6135 | 523.9351 | 502.3891 | 486.936 | 576.5318
2936.6135 | 523.9442 | 502.4095 | 486.7625 | 576.3168
2937.6135 | 523.8137 | 502.4151 | 486.7984 | 576.5351
2938.6135 | 523.7729 | 502.3891 | 486.8891 | 576.5343
2939.6135 | 523.8406 | 502.3739 | 486.9677 | 576.4667
2940.6135 | 523.8514 | 502.3934 | 487.049 | 577.0029
2941.6135 | 523.7813 | 502.4363 | 486.8683 | 576.6729
2942.6135 | 523.699 | 502.4202 | 486.8486 | 576.3261
2943.6135 | 523.7129 | 502.3891 | 486.9645 | 577.0296
2944.6135 | 523.7706 | 502.4115 | 486.6944 | 576.9899
2945.6135 | 523.8375 | 502.4488 | 486.7569 | 577.0103
2946.6135 | 523.8698 | 502.4655 | 486.6496 | 577.0666
2947.6135 | 523.8926 | 502.4656 | 486.8298 | 576.6395
2948.6135 | 523.9997 | 502.3985 | 486.9149 | 577.3554
2949.6135 | 523.9083 | 502.4069 | 487.0657 | 577.4298
2950.6135 | 523.8778 | 502.3915 | 486.9123 | 577.577
2951.6135 | 523.9414 | 502.4137 | 486.8782 | 577.4771
2952.6135 | 524.0205 | 502.4219 | 486.9423 | 576.7374
2953.6135 | 524.1222 | 502.4687 | 487.003 | 577.6252
2954.6135 | 524.0568 | 502.4812 | 487.083 | 577.8349
2955.6135 | 524.0443 | 502.4685 | 487.1194 | 577.7969
2956.6135 | 523.9432 | 502.4663 | 487.1419 | 577.5699
2957.6135 | 523.8901 | 502.4558 | 486.9394 | 577.3507
2958.6135 | 523.9106 | 502.4637 | 486.9531 | 577.825
2959.6135 | 523.7965 | 502.499 | 487.024 | 577.8835
2960.6135 | 523.8054 | 502.5012 | 487.0199 | 577.6521
2961.6135 | 523.6576 | 502.4994 | 486.8223 | 577.9278
2962.6135 | 523.5479 | 502.5167 | 486.982 | 577.7422
2963.6135 | 523.4739 | 502.528 | 487.0912 | 577.936
2964.6135 | 523.5078 | 502.5399 | 486.9088 | 577.4883
2965.6135 | 523.4831 | 502.5194 | 486.9574 | 578.1847
2966.6135 | 523.6283 | 502.5223 | 487.0352 | 577.6132
2967.6135 | 523.6342 | 502.5023 | 486.9064 | 577.9795
2968.6135 | 523.5087 | 502.4995 | 486.6849 | 578.4188
2969.6135 | 523.5094 | 502.5035 | 486.8089 | 578.3045
2970.6135 | 523.5888 | 502.4933 | 486.9807 | 578.0564
2971.6135 | 523.5542 | 502.4818 | 487.1206 | 578.5944
2972.6135 | 523.5662 | 502.4676 | 486.8514 | 578.3575
2973.6135 | 523.6144 | 502.4887 | 486.9152 | 577.9178
2974.6135 | 523.6207 | 502.5066 | 486.9944 | 578.5229
2975.6135 | 523.4351 | 502.4999 | 487.0206 | 578.573
2976.6135 | 523.4261 | 502.5192 | 486.9841 | 578.1227
2977.6135 | 523.4446 | 502.5123 | 486.7615 | 578.8016
2978.6135 | 523.4589 | 502.5301 | 486.9017 | 578.749
2979.6135 | 523.3122 | 502.4936 | 486.9464 | 578.6647
2980.6135 | 523.3061 | 502.5331 | 487.0099 | 579.0239
2981.6135 | 523.2575 | 502.5281 | 486.8696 | 578.8404
2982.6135 | 523.3861 | 502.5199 | 486.5918 | 579.006
2983.6135 | 523.325 | 502.5504 | 486.5043 | 579.0084
2984.6135 | 523.307 | 502.5438 | 486.6024 | 579.0022
2985.6135 | 523.3966 | 502.551 | 486.6686 | 578.9768
2986.6135 | 523.4893 | 502.5516 | 486.7292 | 579.0242
2987.6135 | 523.5625 | 502.5266 | 486.8188 | 578.7195
2988.6135 | 523.5366 | 502.5525 | 486.7038 | 578.7957
2989.6135 | 523.5481 | 502.5531 | 486.5958 | 578.3379
2990.6135 | 523.5816 | 502.5609 | 486.7149 | 578.5103
2991.6135 | 523.5658 | 502.5143 | 486.8352 | 579.0167
2992.6135 | 523.5569 | 502.534 | 486.6565 | 578.4256
2993.6135 | 523.4732 | 502.5629 | 486.7032 | 579.3243
2994.6135 | 523.4902 | 502.5442 | 486.7395 | 578.9985
2995.6135 | 523.4565 | 502.5641 | 486.9973 | 579.4695
2996.6135 | 523.4866 | 502.5711 | 487.1353 | 579.2568
2997.6135 | 523.4537 | 502.5617 | 486.9871 | 579.0712
2998.6135 | 523.338 | 502.5575 | 486.9647 | 579.5583
2999.6135 | 523.1806 | 502.5364 | 487.0177 | 579.4719
3000.6135 | 523.1917 | 502.5342 | 486.9581 | 579.2664
3001.6135 | 523.1988 | 502.5631 | 487.0134 | 579.5591
3002.6135 | 523.1709 | 502.5597 | 487.0975 | 579.4546
3003.6135 | 523.1687 | 502.5458 | 487.1704 | 579.5866
3004.6135 | 523.2349 | 502.527 | 487.2292 | 578.9458
3005.6135 | 523.1839 | 502.5541 | 487.1325 | 579.4468
3006.6135 | 523.2991 | 502.5663 | 487.0778 | 579.1595
3007.6135 | 523.4425 | 502.5706 | 486.7396 | 579.6693
3008.6135 | 523.4848 | 502.5812 | 486.939 | 579.6686
3009.6135 | 523.5413 | 502.5773 | 486.7553 | 579.7942
3010.6135 | 523.5972 | 502.5916 | 486.7294 | 579.7827
3011.6135 | 523.6194 | 502.5831 | 486.8788 | 579.8558
3012.6135 | 523.7531 | 502.5663 | 487.0886 | 579.5363
3013.6135 | 523.7602 | 502.5751 | 487.1807 | 579.7777
3014.6135 | 523.714 | 502.5844 | 487.2504 | 580.0295
3015.6135 | 523.7588 | 502.5784 | 487.2409 | 579.9053
3016.6135 | 523.6881 | 502.581 | 487.1919 | 579.5323
3017.6135 | 523.6284 | 502.5938 | 487.2675 | 580.0493
3018.6135 | 523.8439 | 502.5676 | 487.2462 | 579.6016
3019.6135 | 523.9491 | 502.5537 | 487.4214 | 579.8401
3020.6135 | 523.8898 | 502.5532 | 487.2352 | 579.4712
3021.6135 | 523.7162 | 502.5839 | 487.3258 | 579.509
3022.6135 | 523.6452 | 502.6199 | 487.2478 | 579.0862
3023.6135 | 523.646 | 502.6027 | 487.4056 | 579.9065
3024.6135 | 523.6425 | 502.5565 | 487.3352 | 579.9573
3025.6135 | 523.7135 | 502.5854 | 487.3625 | 580.0175
3026.6135 | 523.6621 | 502.5668 | 487.3322 | 580.2261
3027.6135 | 523.5332 | 502.5879 | 487.1382 | 580.2003
3028.6135 | 523.574 | 502.599 | 487.2435 | 580.1368
3029.6135 | 523.6897 | 502.5532 | 487.1744 | 579.8416
3030.6135 | 523.7198 | 502.615 | 486.851 | 579.9223
3031.6135 | 523.6526 | 502.6206 | 486.8004 | 580.1998
3032.6135 | 523.683 | 502.626 | 486.7634 | 580.2955
3033.6135 | 523.7065 | 502.6092 | 486.7286 | 580.1718
3034.6135 | 523.7052 | 502.6466 | 486.9268 | 580.655
3035.6135 | 523.718 | 502.6482 | 487.1481 | 580.3813
3036.6135 | 523.7867 | 502.6625 | 487.2287 | 580.1388
3037.6135 | 523.9611 | 502.678 | 487.3902 | 580.66
3038.6135 | 524.0689 | 502.6784 | 487.4045 | 580.6185
3039.6135 | 524.114 | 502.6669 | 487.2874 | 580.5959
3040.6135 | 524.0203 | 502.6794 | 487.2912 | 580.2354
3041.6135 | 524.1209 | 502.6917 | 487.3564 | 580.2063
3042.6135 | 524.2008 | 502.6912 | 487.2854 | 580.0893
3043.6135 | 524.1399 | 502.6856 | 487.2488 | 580.2559
3044.6135 | 524.2109 | 502.675 | 487.2459 | 580.1961
3045.6135 | 524.1397 | 502.7007 | 486.9899 | 579.9192
3046.6135 | 523.9921 | 502.6918 | 487.0974 | 580.2072
3047.6135 | 524.0412 | 502.7221 | 487.2876 | 580.2137
3048.6135 | 524.0069 | 502.6953 | 487.1846 | 580.0741
3049.6135 | 523.9747 | 502.6899 | 487.0419 | 580.1498
3050.6135 | 523.9116 | 502.7118 | 487.2333 | 580.1833
3051.6135 | 523.8817 | 502.7125 | 487.2975 | 579.6702
3052.6135 | 523.7609 | 502.7214 | 487.2452 | 580.0318
3053.6135 | 523.7672 | 502.7206 | 487.3074 | 580.5623
3054.6135 | 523.7188 | 502.7111 | 487.1799 | 579.6352
3055.6135 | 523.6206 | 502.7117 | 487.1456 | 580.3967
3056.6135 | 523.619 | 502.6828 | 487.2649 | 580.2845
3057.6135 | 523.7139 | 502.6712 | 487.3023 | 580.0797
3058.6135 | 523.833 | 502.6524 | 487.3321 | 580.4956
3059.6135 | 523.7217 | 502.6778 | 487.3285 | 580.4893
3060.6135 | 523.7549 | 502.7023 | 487.3636 | 580.2648
3061.6135 | 523.7017 | 502.6952 | 487.2798 | 580.7536
3062.6135 | 523.7374 | 502.6815 | 487.0633 | 579.8825
3063.6135 | 523.6635 | 502.7199 | 487.3033 | 580.2964
3064.6135 | 523.5985 | 502.7309 | 487.2244 | 580.5982
3065.6135 | 523.6324 | 502.6917 | 487.2496 | 579.7314
3066.6135 | 523.6716 | 502.6993 | 486.9791 | 580.6837
3067.6135 | 523.5787 | 502.6855 | 486.9942 | 580.7315
3068.6135 | 523.4665 | 502.7045 | 486.8786 | 580.8213
3069.6135 | 523.5116 | 502.7403 | 487.0516 | 580.6482
3070.6135 | 523.6009 | 502.7359 | 487.1897 | 580.9984
3071.6135 | 523.6102 | 502.7345 | 487.1288 | 580.6987
3072.6135 | 523.6288 | 502.6969 | 487.3369 | 580.7273
3073.6135 | 523.6032 | 502.712 | 486.9724 | 580.7784
3074.6135 | 523.6573 | 502.7313 | 486.67 | 580.306
3075.6135 | 523.6274 | 502.7426 | 486.9568 | 580.8664
3076.6135 | 523.6438 | 502.7407 | 487.1844 | 580.9992
3077.6135 | 523.707 | 502.7571 | 487.0644 | 581.018
3078.6135 | 523.639 | 502.7705 | 487.2158 | 581.0616
3079.6135 | 523.6762 | 502.7183 | 487.1615 | 580.8419
3080.6135 | 523.6586 | 502.7458 | 487.2332 | 580.7904
3081.6135 | 523.7543 | 502.7754 | 487.2264 | 581.2107
3082.6135 | 523.7165 | 502.765 | 487.2224 | 581.0861
3083.6135 | 523.6132 | 502.7395 | 487.3178 | 580.9037
3084.6135 | 523.5678 | 502.7587 | 486.8307 | 581.5027
3085.6135 | 523.521 | 502.7616 | 487.0828 | 581.2615
3086.6135 | 523.5154 | 502.7283 | 487.06 | 581.3386
3087.6135 | 523.5902 | 502.7575 | 487.1081 | 580.3011
3088.6135 | 523.6801 | 502.7781 | 487.061 | 581.1631
3089.6135 | 523.6178 | 502.7819 | 487.1508 | 581.535
3090.6135 | 523.5104 | 502.7829 | 487.3497 | 581.0867
3091.6135 | 523.5393 | 502.7628 | 487.1806 | 581.5399
3092.6135 | 523.5137 | 502.7426 | 487.1715 | 581.5825
3093.6135 | 523.3495 | 502.7566 | 487.3155 | 581.3879
3094.6135 | 523.2721 | 502.7665 | 487.3481 | 580.4878
3095.6135 | 523.2264 | 502.7743 | 487.1022 | 581.2993
3096.6135 | 523.135 | 502.7927 | 487.1415 | 581.437
3097.6135 | 523.0562 | 502.7855 | 487.3408 | 581.6499
3098.6135 | 523.0087 | 502.7806 | 487.3474 | 581.6782
3099.6135 | 522.9466 | 502.7813 | 487.107 | 581.6628
3100.6135 | 522.9743 | 502.8043 | 487.0626 | 581.9592
3101.6135 | 523.1022 | 502.7926 | 486.987 | 581.3649
3102.6135 | 523.129 | 502.7785 | 487.1755 | 581.8493
3103.6135 | 523.1248 | 502.7874 | 487.3047 | 581.8615
3104.6135 | 523.2476 | 502.7954 | 486.9719 | 581.9851
3105.6135 | 523.254 | 502.8294 | 487.0332 | 581.7863
3106.6135 | 523.2941 | 502.8363 | 487.0444 | 581.9016
3107.6135 | 523.3485 | 502.8468 | 487.1706 | 582.259
3108.6135 | 523.2815 | 502.8868 | 487.2891 | 582.1822
3109.6135 | 523.3702 | 502.8571 | 487.2828 | 583.4665
3110.6135 | 523.3849 | 502.8498 | 487.2537 | 585.6262
3111.6135 | 523.2378 | 502.8967 | 487.3739 | 586.565
3112.6135 | 523.3688 | 502.9416 | 487.2513 | 587.3732
3113.6135 | 523.3572 | 503.0256 | 487.3177 | 588.0511
3114.6135 | 523.3172 | 503.1084 | 487.3582 | 588.6522
3115.6135 | 523.1896 | 503.1963 | 487.1337 | 589.251
3116.6135 | 523.2949 | 503.3109 | 487.126 | 589.7637
3117.6135 | 523.3137 | 503.4271 | 487.2654 | 590.4781
3118.6135 | 523.4262 | 503.4542 | 487.1464 | 590.9755
3119.6135 | 523.4495 | 503.6038 | 487.1955 | 591.5053
3120.6135 | 523.6529 | 503.7262 | 487.3529 | 591.5348
3121.6135 | 523.7314 | 503.8611 | 487.1802 | 591.8683
3122.6135 | 523.7012 | 503.9716 | 486.9222 | 592.7242
3123.6135 | 523.6903 | 504.0969 | 487.1381 | 593.338
3124.6135 | 523.6783 | 504.2056 | 487.2708 | 593.9163
3125.6135 | 523.6385 | 504.2982 | 487.0879 | 594.3967
3126.6135 | 523.4868 | 504.418 | 486.8392 | 594.7788
3127.6135 | 523.3546 | 504.5384 | 487.0482 | 595.4047
3128.6135 | 523.3576 | 504.6681 | 487.0774 | 595.7839
3129.6135 | 523.446 | 504.7803 | 486.8993 | 596.1523
3130.6135 | 523.363 | 504.9285 | 487.1119 | 596.6369
3131.6135 | 523.4089 | 505.0721 | 487.244 | 596.9616
3132.6135 | 523.3422 | 505.1562 | 487.2623 | 597.3015
3133.6135 | 523.3074 | 505.2657 | 487.1026 | 597.8928
3134.6135 | 523.3579 | 505.4069 | 487.0042 | 597.2473
3135.6135 | 523.4636 | 505.5049 | 487.056 | 598.7843
3136.6135 | 523.4201 | 505.6368 | 487.0539 | 599.2507
3137.6135 | 523.437 | 505.757 | 487.2829 | 599.1545
3138.6135 | 523.3452 | 505.8816 | 487.3379 | 599.9547
3139.6135 | 523.3439 | 505.9732 | 487.4655 | 600.17
3140.6135 | 523.4067 | 506.0309 | 487.1906 | 600.1931
3141.6135 | 523.399 | 506.1238 | 486.9582 | 600.3044
3142.6135 | 523.3156 | 506.2468 | 487.0659 | 600.6611
3143.6135 | 523.3445 | 506.3675 | 487.1797 | 601.6549
3144.6135 | 523.4122 | 506.4578 | 487.1704 | 602.3215
3145.6135 | 523.5483 | 506.5517 | 487.054 | 602.2494
3146.6135 | 523.5144 | 506.692 | 487.0955 | 602.9917
3147.6135 | 523.6006 | 506.8014 | 487.0973 | 603.6976
3148.6135 | 523.6354 | 506.8776 | 487.1091 | 604.2832
3149.6135 | 523.5724 | 506.9828 | 486.8689 | 604.4699
3150.6135 | 523.5925 | 507.1295 | 487.1821 | 604.6959
3151.6135 | 523.5827 | 507.2327 | 487.1885 | 605.2288
3152.6135 | 523.6013 | 507.3186 | 487.2622 | 605.4165
3153.6135 | 523.6149 | 507.4235 | 487.2629 | 605.8804
3154.6135 | 523.6114 | 507.5131 | 487.338 | 606.2547
3155.6135 | 523.5641 | 507.6225 | 487.234 | 606.5314
3156.6135 | 523.4461 | 507.7179 | 487.1177 | 606.7857
3157.6135 | 523.418 | 507.8105 | 487.2949 | 607.2934
3158.6135 | 523.4466 | 507.9333 | 487.3986 | 607.1
3159.6135 | 523.431 | 507.9272 | 487.5068 | 608.0586
3160.6135 | 523.4832 | 508.0102 | 487.3692 | 607.8021
3161.6135 | 523.432 | 508.1078 | 487.4162 | 608.9254
3162.6135 | 523.4831 | 508.1833 | 487.359 | 609.4166
3163.6135 | 523.4105 | 508.3135 | 487.4518 | 609.5728
3164.6135 | 523.3867 | 508.4344 | 487.5533 | 610.4212
3165.6135 | 523.4588 | 508.5312 | 487.557 | 611.1394
3166.6135 | 523.4796 | 508.6241 | 487.6284 | 611.6636
3167.6135 | 523.3839 | 508.6936 | 487.7381 | 611.4168
3168.6135 | 523.4694 | 508.8017 | 487.7437 | 612.7508
3169.6135 | 523.4557 | 508.8907 | 487.4043 | 613.215
3170.6135 | 523.4894 | 509.0053 | 487.4251 | 612.5145
3171.6135 | 523.6009 | 509.1262 | 487.5277 | 612.6275
3172.6135 | 523.5656 | 509.1871 | 487.532 | 613.8948
3173.6135 | 523.625 | 509.2676 | 487.6507 | 612.8964
3174.6135 | 523.6393 | 509.3607 | 487.4802 | 614.3332
3175.6135 | 523.6327 | 509.453 | 487.4954 | 614.2696
3176.6135 | 523.6336 | 509.5105 | 487.5291 | 614.8568
3177.6135 | 523.737 | 509.5874 | 487.4858 | 615.3983
3178.6135 | 523.8265 | 509.6485 | 487.6205 | 615.4745
3179.6135 | 524.0037 | 509.6904 | 487.7388 | 616.2195
3180.6135 | 524.036 | 509.7767 | 487.5749 | 616.5576
3181.6135 | 524.0498 | 509.9223 | 487.7326 | 616.701
3182.6135 | 524.1221 | 510.0008 | 487.8356 | 616.58
3183.6135 | 524.2553 | 510.0821 | 487.7267 | 617.371
3184.6135 | 524.2795 | 510.1797 | 487.7636 | 617.2268
3185.6135 | 524.2044 | 510.2376 | 487.6586 | 617.2437
3186.6135 | 524.2095 | 510.3111 | 487.7796 | 617.8971
3187.6135 | 524.2538 | 510.3795 | 488.0573 | 618.0515
3188.6135 | 524.1035 | 510.4006 | 488.1303 | 618.0123
3189.6135 | 523.9944 | 510.4755 | 488.0152 | 618.4829
3190.6135 | 523.874 | 510.5597 | 487.9184 | 619.0765
3191.6135 | 523.8509 | 510.6325 | 487.8797 | 619.4288
3192.6135 | 523.7995 | 510.7175 | 487.9081 | 619.5231
3193.6135 | 523.815 | 510.7925 | 487.7303 | 618.7871
3194.6135 | 523.7637 | 510.8193 | 487.8919 | 619.9333
3195.6135 | 523.8059 | 510.8926 | 487.9647 | 619.761
3196.6135 | 523.6769 | 510.9402 | 488.0895 | 619.4091
3197.6135 | 523.6323 | 511.0313 | 488.1488 | 621.0996
3198.6135 | 523.7518 | 511.1021 | 488.264 | 621.3433
3199.6135 | 523.6847 | 511.1445 | 488.0859 | 620.8646
3200.6135 | 523.6545 | 511.2255 | 488.1158 | 621.9847
3201.6135 | 523.6029 | 511.2891 | 488.0794 | 621.9202
3202.6135 | 523.5314 | 511.3047 | 488.1623 | 622.2782
3203.6135 | 523.4972 | 511.3725 | 488.2853 | 620.8914
3204.6135 | 523.4808 | 511.4675 | 488.3836 | 622.8318
3205.6135 | 523.3233 | 511.5297 | 488.2517 | 623.2432
3206.6135 | 523.0885 | 511.5609 | 488.2151 | 623.3815
3207.6135 | 522.9902 | 511.6286 | 488.1824 | 623.4821
3208.6135 | 522.9905 | 511.6736 | 488.1374 | 622.7444
3209.6135 | 523.0022 | 511.7471 | 488.3338 | 623.9906
3210.6135 | 522.8611 | 511.7938 | 488.4066 | 623.8908
3211.6135 | 522.7732 | 511.8658 | 488.3736 | 624.0723
3212.6135 | 522.7698 | 511.9261 | 488.4084 | 624.7633
3213.6135 | 522.8143 | 511.9379 | 488.3454 | 623.5342
3214.6135 | 522.8768 | 511.9565 | 488.4713 | 624.5225
3215.6135 | 522.8675 | 512.0447 | 488.4779 | 625.3006
3216.6135 | 523.0939 | 512.1008 | 488.2037 | 624.199
3217.6135 | 523.1425 | 512.1456 | 488.2537 | 626.0119
3218.6135 | 523.2648 | 512.2018 | 488.4714 | 626.2397
3219.6135 | 523.3225 | 512.23 | 488.4708 | 625.9827
3220.6135 | 523.3502 | 512.2772 | 488.5156 | 626.4193
3221.6135 | 523.1803 | 512.3239 | 488.4892 | 626.9678
3222.6135 | 523.1365 | 512.3402 | 488.5866 | 627.2098
3223.6135 | 523.1805 | 512.4027 | 488.6878 | 627.617
3224.6135 | 523.2914 | 512.4116 | 488.7086 | 627.9374
3225.6135 | 523.319 | 512.5069 | 488.8337 | 628.0386
3226.6135 | 523.272 | 512.5184 | 488.7611 | 626.586
3227.6135 | 523.356 | 512.5941 | 488.6466 | 628.0836
3228.6135 | 523.4705 | 512.6447 | 488.7105 | 628.0076
3229.6135 | 523.4881 | 512.6982 | 488.7807 | 628.3563
3230.6135 | 523.5993 | 512.6981 | 488.9379 | 628.2578