## Test Conditions
DESIREE-FIRE Test Number 40 - Circuit Data Data Only
Test Date: | 2009-08-12
DCSim DAQ Start Time | 10:34
DCSim Time for Synchronization | 10:47
Heat Source Synchronization | 0:14 | hours:minutes:seconds
Heat Source DAQ Start Time | 10:34
Fire Time | 10:50
Offset | 0:16 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 960 | seconds
Heat Source Offset | 0:17 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 1011 | seconds
Heat Source Stop Time | 12:13
Test Duration | 1:22 | hours:minutes:seconds
| 4950 | seconds
CT500 turns | 2 |  | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5
Pre-Test Baseline: | Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
1" Solenoid Valve | PE/PVC, 7c, 12AWG |  | Channel 3 and Channel 4 represent the top and bottom of the conduit, respectively. Channel 5 represents the cable temperature within the conduit. | Channel 4 which represents TC25 in the Temperature Data File
Large Coil | PE/PVC, 7c, 12AWG |  | Channel 3 and Channel 4 represent the top and bottom of the conduit, respectively. Channel 5 represents the cable temperature within the conduit. | Channel 4 which represents TC25 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | 1"Coil_CT500 | 1"Coil_CT35_1_P | 1"Coil_CT35_2_G | 1"Coil_CT35_3_R | 1"Coil_CT35_4_N2 | 1"Coil_CT35_5_S | 1"Coil_CT35_6_N1 | LgCoil_CT500 | LgCoil_CT35_1_P | LgCoil_CT35_2_G | LgCoil_CT35_3_N2 | LgCoil_CT35_4_S | LgCoil_CT35_5_N1 | 1"Coil_VT7_1_G | 1"Coil_VT7_2_R | 1"Coil_VT7_3_SP | 1"Coil_VT7_4_S | 1"Coil_VTU_1_P | 1"Coil_VTU_2_N2 | 1"Coil_VTU_3_N1 | LgCoil_VT7_1_R | LgCoil_VT7_2_SP | LgCoil_VT7_3_S | LgCoil_VTU_1_P | LgCoil_VTU_2_G | LgCoil_VTU_3_N2 | LgCoil_VTU_4_N1 | {1"Valve} V(N2) - V(Batt -) | {1"Valve} V(N1) - V(Batt -) | {1"Valve} V(P) - V(Batt +) | {1"Valve} V(R) - V(Batt -) | {1"Valve} V(S) - V(Batt -) | {1"Valve} V(S) - V(N1) | {1"Valve} V(G) - V(Batt +) | {LgCoil} V(N2) - V(Batt -) | {LgCoil} V(N1) - V(Batt -) | {LgCoil} V(P) - V(Batt +) | {LgCoil} V(R) - V(Batt -) | {LgCoil} V(S) - V(Batt -) | {LgCoil} V(S) - V(N1) | {LgCoil} V(G) - V(Batt +) | {1"Valve} V(P) - V(Batt -) | {1"Valve} V(G) - V(Batt -) | {1"Valve} V(SP) - V(Batt -) | {1"Valve} V(N1) - V(Batt +) | {LgCoil} V(P) - V(Batt -) | {LgCoil} V(G) - V(Batt -) | {LgCoil} V(SP) - V(Batt -) | {LgCoil} V(N1) - V(Batt +)
-0.98438 | 123.2162 | -59.0469 | 63.826 | -0.0383 | 0.0010403 | 0.06825 | 0.066885 | 0.13121 | -0.0019995 | -0.0015231 | -0.015411 | -0.00229 | 0.062769 | 0.06103 | 0.00014962 | -0.0036424 | 63.8947 | 64.0045 | 0.013733 | -59.23 | 63.8718 | -59.0607 | -59.1202 | -58.9279 | 0.09613 | -59.2667 | 63.8535 | 63.7711 | -59.1156 | -59.2209 | -0.013733 | -0.073242 | 0.045776 | 123.0515 | -0.18311 | -0.10986 | 0.068664 | -0.068665 | -0.17395 | 0.027466 | 0.11902 | -0.21973 | -0.045777 | -0.054932 | 122.9187 | 122.9416 | 59.0607 | -122.9462 | 122.9004 | 122.818 | 59.1431 | -123.0469
0.015625 | 123.23 | -59.0103 | 63.8397 | -0.076447 | 0.0025357 | 0.067396 | 0.070303 | 0.13313 | -0.0013587 | -0.0023777 | 0.25925 | -0.0035718 | 0.061273 | 0.059107 | 0.0031402 | -0.0027878 | 63.9359 | 64.064 | 0.041199 | -59.2255 | 63.826 | -59.0561 | -59.1202 | -58.9279 | 0.1831 | -59.2026 | 63.8809 | 63.7711 | -59.1019 | -59.2026 | -0.045776 | -0.10986 | -0.013733 | 123.0743 | -0.21515 | -0.10529 | 0.09613 | -0.091553 | -0.19226 | 0.041198 | 0.082398 | -0.19226 | 0 | -0.068665 | 122.8363 | 122.9462 | 59.0515 | -122.9599 | 122.8912 | 122.7814 | 59.1934 | -123.0423
1.0156 | 123.1934 | -59.0057 | 63.8489 | -0.12222 | -0.00045509 | 0.067823 | 0.068167 | 0.1327 | -0.0017859 | -2.7856e-05 | -0.17563 | -0.0027174 | 0.063623 | 0.062312 | 0.0024994 | -0.002147 | 63.9496 | 64.0778 | 0.091553 | -59.2072 | 63.8718 | -59.0698 | -59.1202 | -58.9188 | 0.17853 | -59.2255 | 63.8489 | 63.7436 | -59.0973 | -59.2209 | -0.064087 | -0.11444 | 0.022888 | 123.0835 | -0.20142 | -0.086975 | 0.10071 | -0.091553 | -0.21515 | 0 | 0.086975 | -0.21973 | -0.004578 | -0.10529 | 122.8775 | 122.9553 | 59.0973 | -122.9691 | 122.8546 | 122.7493 | 59.1843 | -123.0698
2.0156 | 123.2025 | -59.0561 | 63.826 | 0.15244 | 0.0038175 | 0.064832 | 0.06774 | 0.13249 | 0.0020593 | -0.0025913 | 0.19821 | -0.0018628 | 0.06341 | 0.061457 | 0.0039948 | -0.00043797 | 63.8901 | 64.0228 | -0.027466 | -59.2575 | 63.8397 | -59.1293 | -59.1476 | -58.9645 | -0.027466 | -59.1751 | 63.8489 | 63.7482 | -59.1202 | -59.2667 | -0.073242 | -0.091553 | 0.013733 | 123.0789 | -0.20142 | -0.10986 | 0.064087 | -0.064087 | -0.21057 | 0.022888 | 0.091552 | -0.11902 | 0.091553 | -0.07782 | 122.8958 | 122.9462 | 59.0286 | -122.9736 | 122.905 | 122.8043 | 59.0286 | -123.0927
3.0156 | 123.1338 | -59.0607 | 63.9084 | -0.23666 | 0.0027493 | 0.068037 | 0.066885 | 0.13121 | -0.00071785 | 0.0018947 | -0.2977 | -0.0025038 | 0.063837 | 0.061671 | 0.0018584 | -0.003215 | 63.9038 | 64.0366 | 0.045776 | -59.2255 | 63.8901 | -59.0973 | -59.1431 | -59.0195 | 0.091553 | -59.3124 | 63.9359 | 63.7985 | -59.1248 | -59.23 | -0.036621 | -0.082397 | -0.01831 | 123.0972 | -0.1648 | -0.082398 | -0.004577 | -0.064087 | -0.16937 | 0.027466 | 0.041199 | -0.25177 | -0.082397 | -0.10986 | 122.9507 | 122.9645 | 59.1064 | -123.0515 | 122.9965 | 122.8592 | 59.1522 | -123.1384
4.0156 | 123.1659 | -59.0698 | 63.7939 | 0.14481 | 0.0050991 | 0.066541 | 0.067526 | 0.13313 | 0.00056395 | 0.00018594 | 0.17532 | -0.003999 | 0.064264 | 0.062739 | 0.0014312 | -0.0027878 | 63.8901 | 64.0137 | -0.009155 | -59.2667 | 63.826 | -59.0927 | -59.1568 | -58.9554 | 0.050354 | -59.2804 | 63.858 | 63.7344 | -59.1431 | -59.2438 | -0.022888 | -0.086975 | 0.032044 | 123.0835 | -0.19684 | -0.10986 | 0.096131 | -0.073242 | -0.17395 | 0.064087 | 0.11444 | -0.21057 | -0.036622 | -0.059509 | 122.8958 | 122.9599 | 59.0607 | -122.9507 | 122.9279 | 122.8043 | 59.1202 | -123.0377
5.0156 | 123.1659 | -59.0469 | 63.826 | 0.16006 | 0.0014675 | 0.067396 | 0.067526 | 0.13142 | -0.00071785 | -0.0019505 | 0.083771 | -0.0018628 | 0.063623 | 0.062525 | 0.0012176 | -0.0047104 | 63.9816 | 64.0228 | -0.086975 | -59.3124 | 63.8397 | -59.0973 | -59.1248 | -58.992 | 0.009155 | -59.2941 | 63.8626 | 63.7665 | -59.0973 | -59.23 | -0.050354 | -0.07782 | 0.013733 | 123.0698 | -0.2655 | -0.18768 | 0.15564 | -0.050354 | -0.18311 | 0.036621 | 0.054932 | -0.24719 | -0.064086 | -0.05951 | 122.8867 | 123.0286 | 58.96 | -122.9507 | 122.9095 | 122.8134 | 59.0561 | -123.056
6.0156 | 123.2162 | -59.0607 | 63.7756 | 0.25925 | 0.0046719 | 0.065473 | 0.068381 | 0.13099 | 0.0012047 | 0.00039954 | 0.18295 | -0.0025038 | 0.066828 | 0.062739 | 0.0046356 | -0.0027878 | 63.8947 | 63.9954 | -0.054932 | -59.2346 | 63.8443 | -59.0973 | -59.1293 | -58.9554 | 0.018311 | -59.2804 | 63.858 | 63.7207 | -59.1614 | -59.2255 | -0.036621 | -0.068664 | 0.068664 | 123.056 | -0.17395 | -0.10529 | 0.11902 | -0.10071 | -0.1648 | 0.082397 | 0.10529 | -0.21973 | -0.054932 | -0.054932 | 122.905 | 122.9553 | 59.0057 | -122.905 | 122.9187 | 122.7814 | 59.079 | -123.0011
7.0156 | 123.1842 | -59.0607 | 63.826 | 0.18295 | 0.0029629 | 0.06761 | 0.067526 | 0.13398 | -0.0030677 | -0.00066866 | 0.17532 | -0.0031446 | 0.062128 | 0.062953 | 0.00036322 | -0.002147 | 63.8443 | 63.9679 | -0.041199 | -59.2804 | 63.8351 | -59.0973 | -59.1385 | -58.992 | 0.013733 | -59.2896 | 63.8443 | 63.7619 | -59.1339 | -59.2209 | -0.036621 | -0.07782 | 0.009155 | 123.0286 | -0.21973 | -0.14191 | 0.01831 | -0.073242 | -0.16022 | 0.01831 | 0.068665 | -0.22888 | -0.068665 | -0.064087 | 122.8958 | 122.905 | 59.0195 | -122.9645 | 122.905 | 122.8226 | 59.0744 | -123.0469
8.0156 | 123.1979 | -59.0561 | 63.8031 | 0.16769 | 0.0046719 | 0.066114 | 0.067313 | 0.13078 | 0.00056395 | -0.00066866 | 0.17532 | -0.0035718 | 0.063196 | 0.063594 | 0.0018584 | -0.0017196 | 63.9038 | 64.0228 | -0.018311 | -59.2392 | 63.8031 | -59.0881 | -59.1431 | -58.96 | 0.041199 | -59.2804 | 63.8351 | 63.7115 | -59.1293 | -59.2438 | -0.032044 | -0.086975 | 0 | 123.0789 | -0.18311 | -0.096131 | 0.10071 | -0.073242 | -0.18768 | 0.032043 | 0.09613 | -0.22431 | -0.036622 | -0.091553 | 122.8592 | 122.9599 | 59.0378 | -122.9462 | 122.8912 | 122.7676 | 59.0973 | -123.0469
9.0156 | 123.1796 | -59.0561 | 63.8214 | 0.015106 | -0.0013095 | 0.068464 | 0.068808 | 0.12993 | -0.0015723 | -0.0013095 | 0.12192 | -0.0035718 | 0.062769 | 0.060389 | 0.0014312 | -0.0030014 | 63.8443 | 63.9587 | -0.041199 | -59.2667 | 63.8306 | -59.0881 | -59.1339 | -59.0012 | 0.036621 | -59.3124 | 63.8535 | 63.7573 | -59.1248 | -59.2392 | -0.032044 | -0.07782 | 0.009155 | 123.0148 | -0.21057 | -0.13275 | 0.022888 | -0.068665 | -0.18311 | 0.032044 | 0.054931 | -0.25635 | -0.073242 | -0.064087 | 122.8867 | 122.9004 | 59.0149 | -122.9553 | 122.9095 | 122.8134 | 59.0927 | -123.0606
10.0156 | 123.1705 | -59.0195 | 63.8718 | -0.19089 | 0.00039951 | 0.065901 | 0.068594 | 0.13121 | -0.0019995 | -0.00045506 | -0.14511 | -0.0035718 | 0.06341 | 0.062953 | 0.0022858 | -0.0017196 | 63.9221 | 64.0594 | 0.086975 | -59.2026 | 63.8535 | -59.079 | -59.1064 | -58.9554 | 0.16479 | -59.2529 | 63.8672 | 63.7848 | -59.111 | -59.2163 | -0.059509 | -0.086975 | -0.01831 | 123.0789 | -0.18311 | -0.096131 | 0.050354 | -0.091553 | -0.19684 | -0.004578 | 0.064087 | -0.23346 | -0.036621 | -0.086975 | 122.8729 | 122.9416 | 59.1064 | -122.9782 | 122.8867 | 122.8043 | 59.1843 | -123.0881
11.0156 | 123.1155 | -59.0652 | 63.8214 | 0.045624 | 0.0018949 | 0.066755 | 0.066031 | 0.13206 | -0.0017859 | 0.00061314 | 0.14481 | -0.003999 | 0.061914 | 0.061457 | 0.001004 | -0.0010788 | 63.858 | 63.9771 | -0.045776 | -59.2667 | 63.8489 | -59.0744 | -59.1248 | -58.992 | 0.022888 | -59.3124 | 63.8535 | 63.739 | -59.1431 | -59.2438 | -0.009155 | -0.059509 | 0.027466 | 123.0423 | -0.20142 | -0.14191 | 0.036621 | -0.077819 | -0.17853 | 0.032044 | 0.073243 | -0.24719 | -0.068665 | -0.082397 | 122.9141 | 122.9233 | 59.0195 | -122.9462 | 122.9187 | 122.8043 | 59.0881 | -123.0652
12.0156 | 123.1979 | -59.0424 | 63.8031 | 0.25925 | 0.0046719 | 0.066969 | 0.069022 | 0.13121 | 0.0039819 | 0.0023221 | -0.076446 | 0.0015552 | 0.064478 | 0.061885 | 0.004422 | -0.003215 | 63.8626 | 63.9404 | -0.10071 | -59.2667 | 63.8718 | -59.0973 | -59.1431 | -58.9828 | -0.027466 | -59.3079 | 63.8397 | 63.7253 | -59.1522 | -59.2392 | -0.054932 | -0.10071 | 0.068664 | 122.9828 | -0.22431 | -0.1236 | 0.059509 | -0.10986 | -0.19684 | 0.036621 | 0.059509 | -0.2655 | -0.068664 | -0.07782 | 122.9141 | 122.905 | 58.9417 | -122.9462 | 122.8821 | 122.7676 | 59.0149 | -123.0423
13.0156 | 123.1705 | -59.0561 | 63.7848 | 0.19058 | 0.0031765 | 0.065473 | 0.064322 | 0.13398 | -0.00050425 | 0.0016811 | 0.2211 | -0.00229 | 0.062128 | 0.062953 | 0.004422 | -0.003215 | 63.8901 | 64.0137 | -0.013733 | -59.2484 | 63.8031 | -59.0927 | -59.1522 | -58.96 | 0.036621 | -59.2941 | 63.8306 | 63.7253 | -59.1339 | -59.2392 | -0.036621 | -0.096131 | 0.018311 | 123.0698 | -0.19226 | -0.09613 | 0.10529 | -0.07782 | -0.18311 | 0.045776 | 0.09613 | -0.23804 | -0.054931 | -0.059509 | 122.8592 | 122.9462 | 59.0424 | -122.937 | 122.8867 | 122.7814 | 59.0927 | -123.024
14.0156 | 123.2071 | -59.0607 | 63.8123 | 0.19058 | 0.0057401 | 0.065901 | 0.069876 | 0.13163 | 0.0020593 | -2.7856e-05 | 0.2211 | -0.0044264 | 0.06341 | 0.062953 | 0.0012176 | -0.00065157 | 63.8992 | 63.9999 | -0.036621 | -59.2392 | 63.8168 | -59.1156 | -59.1568 | -58.9554 | 0.050354 | -59.2712 | 63.858 | 63.7299 | -59.1293 | -59.2163 | -0.054932 | -0.09613 | 0.004577 | 123.0606 | -0.17853 | -0.082398 | 0.086975 | -0.068664 | -0.15564 | 0.045776 | 0.10529 | -0.21057 | -0.054931 | -0.082398 | 122.8775 | 122.9599 | 59.024 | -122.9691 | 122.9187 | 122.7905 | 59.111 | -123.0286
15.0156 | 123.0698 | -59.0973 | 63.8855 | -0.19852 | 0.0048855 | 0.066114 | 0.070731 | 0.13057 | 0.00077755 | -0.0021641 | -0.22903 | 0.00048704 | 0.068109 | 0.063807 | 0.0018584 | -0.0025742 | 63.8489 | 63.913 | -0.059509 | -59.2529 | 63.9038 | -59.0927 | -59.166 | -59.0515 | 0.059509 | -59.3491 | 63.9267 | 63.8535 | -59.1339 | -59.2346 | 0.004578 | -0.068665 | 0.018311 | 123.0103 | -0.15564 | -0.086975 | -0.036621 | -0.036621 | -0.13733 | 0.041199 | 0.045776 | -0.25177 | -0.11444 | -0.032043 | 123.0011 | 122.9462 | 59.0378 | -123.0515 | 123.024 | 122.9507 | 59.1568 | -123.1201
16.0156 | 123.1934 | -59.0515 | 63.8077 | 0.23636 | 0.0074491 | 0.065473 | 0.068594 | 0.13206 | 0.0020593 | 0.0012539 | 0.23636 | -0.0025038 | 0.063196 | 0.064021 | 0.0016448 | -0.002147 | 63.8992 | 63.9862 | -0.050354 | -59.2346 | 63.8306 | -59.0881 | -59.1293 | -58.9691 | 0.036621 | -59.2667 | 63.8123 | 63.7436 | -59.1614 | -59.2392 | -0.036621 | -0.077819 | 0.022888 | 123.0377 | -0.18311 | -0.10529 | 0.091553 | -0.10986 | -0.18768 | 0.004578 | 0.082398 | -0.21515 | -0.027466 | -0.064087 | 122.8821 | 122.9507 | 59.0012 | -122.937 | 122.8638 | 122.7951 | 59.0881 | -123.0469
17.0156 | 123.1613 | -59.0607 | 63.826 | 0.16006 | 0.0027493 | 0.066969 | 0.066885 | 0.13292 | -0.0026405 | -0.00066866 | 0.24399 | -0.0016492 | 0.061487 | 0.060176 | 0.001004 | 0.00041663 | 63.8672 | 63.9862 | -0.027466 | -59.2575 | 63.8168 | -59.0836 | -59.1339 | -59.0332 | -0.032043 | -59.2804 | 63.8397 | 63.7665 | -59.1248 | -59.2575 | -0.022888 | -0.073242 | -0.009156 | 123.0469 | -0.19684 | -0.1236 | 0.041198 | -0.064087 | -0.19684 | 0.013733 | 0.027466 | -0.21973 | -0.022889 | -0.05951 | 122.8775 | 122.9279 | 59.0332 | -122.9599 | 122.9004 | 122.8271 | 59.0286 | -123.0835
18.0156 | 123.1659 | -59.0515 | 63.7939 | -0.96146 | 0.0038175 | 0.064619 | 0.069449 | 0.13099 | -0.00050425 | -0.0013095 | 0.19821 | -0.00015376 | 0.063623 | 0.060603 | 0.004422 | -0.0023606 | 63.8306 | 63.9313 | -0.059509 | -59.2438 | 63.858 | -59.1156 | -59.1522 | -58.9645 | 0.041199 | -59.2941 | 63.8443 | 63.7115 | -59.1385 | -59.2346 | -0.064087 | -0.10071 | 0.064087 | 122.9828 | -0.19226 | -0.091552 | 0.036621 | -0.086975 | -0.18311 | 0.050354 | 0.086975 | -0.24261 | -0.059509 | -0.082397 | 122.9095 | 122.8821 | 58.992 | -122.9462 | 122.8958 | 122.7631 | 59.0927 | -123.0286
19.0156 | 123.2483 | -59.0469 | 63.7848 | 0.19821 | 0.0053129 | 0.067396 | 0.06539 | 0.13484 | -0.00093145 | 0.00082674 | 0.23636 | -0.0018628 | 0.062982 | 0.061885 | 0.0014312 | -0.003215 | 63.8855 | 63.9954 | -0.041199 | -59.23 | 63.8397 | -59.1064 | -59.1522 | -58.96 | 0.045776 | -59.2758 | 63.7939 | 63.7482 | -59.1339 | -59.2346 | -0.059509 | -0.10529 | 0.054932 | 123.0423 | -0.18311 | -0.07782 | 0.10071 | -0.086975 | -0.18768 | 0.009155 | 0.086975 | -0.22888 | -0.041199 | -0.036621 | 122.8867 | 122.9324 | 59.0057 | -122.937 | 122.8409 | 122.7951 | 59.0927 | -123.0194
20.0156 | 123.1567 | -59.0469 | 63.826 | 0.045624 | 0.0018949 | 0.066755 | 0.068381 | 0.13035 | -0.0052039 | -2.7856e-05 | 0.18295 | -0.0033582 | 0.061487 | 0.059535 | 0.00036322 | -0.0017196 | 63.8443 | 63.9633 | -0.036621 | -59.2621 | 63.8535 | -59.0881 | -59.1248 | -59.0103 | 0.036621 | -59.2987 | 63.8397 | 63.7756 | -59.1019 | -59.2346 | -0.041199 | -0.07782 | 0.027466 | 123.0103 | -0.21515 | -0.13733 | 0.01831 | -0.054932 | -0.18768 | 0.013733 | 0.036621 | -0.25177 | -0.064087 | -0.050354 | 122.9004 | 122.8912 | 59.0103 | -122.9507 | 122.8867 | 122.8226 | 59.0836 | -123.0606
21.0156 | 123.1979 | -59.0607 | 63.7848 | 0.17532 | 0.0042447 | 0.064832 | 0.065604 | 0.13185 | -7.6852e-05 | -0.0015231 | 0.25162 | -0.00058096 | 0.06106 | 0.062739 | 0.00057682 | -0.0027878 | 63.8855 | 63.9816 | -0.018311 | -59.2346 | 63.7894 | -59.0881 | -59.1293 | -58.9645 | 0.041199 | -59.2804 | 63.826 | 63.7161 | -59.1339 | -59.2255 | -0.027466 | -0.068664 | 0.004578 | 123.0423 | -0.17395 | -0.10529 | 0.10071 | -0.073242 | -0.1648 | 0.041199 | 0.09613 | -0.21973 | -0.054932 | -0.068665 | 122.85 | 122.9462 | 59.0424 | -122.9141 | 122.8867 | 122.7768 | 59.1019 | -123.0103
22.0156 | 123.1842 | -59.0424 | 63.7894 | -0.67154 | 0.0074491 | 0.063551 | 0.066031 | 0.13078 | 0.0020593 | 0.00039954 | 0.21347 | -0.002931 | 0.065759 | 0.063166 | 0.0016448 | -0.0040696 | 63.7985 | 63.9496 | -0.073242 | -59.2621 | 63.8351 | -59.1064 | -59.1476 | -58.9737 | 0.018311 | -59.2941 | 63.8397 | 63.7527 | -59.1385 | -59.2072 | -0.064087 | -0.10529 | 0.045776 | 122.9919 | -0.21973 | -0.11444 | 0.009155 | -0.096131 | -0.16479 | 0.050354 | 0.068664 | -0.25177 | -0.086975 | -0.036621 | 122.8775 | 122.8409 | 58.9691 | -122.937 | 122.8821 | 122.7951 | 59.0607 | -122.9965
23.0156 | 123.1979 | -59.0561 | 63.7848 | 0.16769 | 0.0048855 | 0.065687 | 0.067526 | 0.13206 | -0.0015723 | 0.00018594 | 0.2211 | -0.0025038 | 0.061701 | 0.063166 | 0.0014312 | -0.0017196 | 63.8809 | 63.9954 | -0.027466 | -59.2484 | 63.8306 | -59.1064 | -59.1385 | -58.9737 | 0.032043 | -59.2712 | 63.8351 | 63.7482 | -59.1248 | -59.23 | -0.050354 | -0.082398 | 0.045776 | 123.0515 | -0.19226 | -0.10986 | 0.09613 | -0.068665 | -0.17395 | 0.050354 | 0.082397 | -0.21515 | -0.041198 | -0.036621 | 122.8867 | 122.937 | 59.0286 | -122.9233 | 122.8912 | 122.8043 | 59.0881 | -123.0148
24.0156 | 123.1659 | -59.0744 | 63.8031 | 0.13718 | 0.0093717 | 0.067182 | 0.068167 | 0.13206 | -0.00050425 | -0.0019505 | 0.20584 | -0.001222 | 0.061914 | 0.063807 | 0.0016448 | -0.0036424 | 63.8443 | 63.8855 | -0.11902 | -59.2941 | 63.858 | -59.1248 | -59.166 | -59.0332 | -0.004578 | -59.3628 | 63.8718 | 63.7619 | -59.1476 | -59.2438 | -0.050354 | -0.091553 | 0.054931 | 122.9599 | -0.21973 | -0.12817 | 0.041198 | -0.073242 | -0.16937 | 0.068664 | 0.041199 | -0.28839 | -0.11902 | -0.041199 | 122.9324 | 122.9187 | 58.9554 | -122.9691 | 122.9462 | 122.8363 | 59.0698 | -123.0469
25.0156 | 123.2025 | -59.0195 | 63.8489 | -0.19089 | 0.0014675 | 0.06825 | 0.069235 | 0.13313 | -0.0022131 | 0.00018594 | -0.13748 | -0.00229 | 0.061701 | 0.061885 | 0.001004 | -0.001506 | 63.9221 | 64.0411 | 0.07782 | -59.1934 | 63.8626 | -59.0561 | -59.1064 | -58.9737 | 0.16937 | -59.2438 | 63.8763 | 63.8031 | -59.1019 | -59.2072 | -0.036621 | -0.086975 | 0.013733 | 123.0606 | -0.17395 | -0.086975 | 0.073242 | -0.082398 | -0.18768 | 0.027466 | 0.045776 | -0.2243 | -0.036621 | -0.045776 | 122.8821 | 122.9416 | 59.0973 | -122.9553 | 122.8958 | 122.8226 | 59.1888 | -123.056
26.0156 | 123.0881 | -59.1156 | 63.8443 | 0.12955 | 0.0085171 | 0.064619 | 0.070944 | 0.1295 | 0.0024865 | -0.00088226 | 0.10666 | -0.00229 | 0.064051 | 0.062312 | 0.0029266 | -0.003856 | 63.7848 | 63.8397 | -0.14648 | -59.3124 | 63.8718 | -59.111 | -59.1568 | -59.0744 | -0.073242 | -59.3994 | 63.8901 | 63.7894 | -59.1705 | -59.2804 | 0.004578 | -0.041198 | 0.027466 | 122.9553 | -0.19684 | -0.15564 | -0.059509 | -0.054931 | -0.1648 | 0.045777 | 0.041199 | -0.28381 | -0.11902 | -0.054931 | 122.9874 | 122.9004 | 58.9691 | -123.0011 | 123.0057 | 122.905 | 59.0424 | -123.1247
27.0156 | 123.1796 | -59.0561 | 63.7665 | 0.20584 | 0.0057401 | 0.066969 | 0.066245 | 0.13099 | -7.6852e-05 | -0.00066866 | 0.18295 | -0.0025038 | 0.062128 | 0.064662 | 0.0018584 | -0.0012924 | 63.9633 | 63.8306 | -0.17853 | -59.3079 | 63.8443 | -59.111 | -59.166 | -58.992 | 0.009155 | -59.2941 | 63.8397 | 63.7619 | -59.1431 | -59.2346 | -0.054932 | -0.10986 | 0.07782 | 122.8867 | -0.25177 | -0.14191 | 0.19684 | -0.086975 | -0.17853 | 0.073243 | 0.064087 | -0.23804 | -0.059509 | -0.004577 | 122.9004 | 123.0194 | 58.8776 | -122.9324 | 122.8958 | 122.818 | 59.0652 | -123.0011
28.0156 | 123.0927 | -59.0973 | 63.8351 | 0.11429 | 0.010226 | 0.06526 | 0.06774 | 0.13121 | 0.0020593 | 0.00082674 | 0.15244 | -0.0018628 | 0.0664 | 0.063807 | 0.001004 | -0.0036424 | 63.8123 | 63.8443 | -0.13733 | -59.3033 | 63.8901 | -59.1248 | -59.1568 | -59.0744 | -0.09613 | -59.3948 | 63.8901 | 63.8031 | -59.1476 | -59.2621 | -0.027466 | -0.059509 | 0.054932 | 122.9416 | -0.20599 | -0.14648 | -0.022888 | -0.050354 | -0.16479 | 0.054932 | 0.022888 | -0.29755 | -0.13275 | -0.032043 | 122.9874 | 122.9095 | 58.96 | -122.9919 | 122.9874 | 122.9004 | 59.0012 | -123.0972
29.0156 | 123.1934 | -59.0607 | 63.8077 | 0.18295 | 0.0046719 | 0.066541 | 0.067526 | 0.13014 | -0.0022131 | -0.0013095 | 0.27451 | -0.0014356 | 0.062982 | 0.062953 | 0.00057682 | -0.0019334 | 63.8718 | 63.9954 | -0.041199 | -59.2438 | 63.7985 | -59.0836 | -59.111 | -58.992 | 0.032043 | -59.2667 | 63.8123 | 63.7665 | -59.111 | -59.23 | -0.022888 | -0.050354 | -0.009155 | 123.056 | -0.18311 | -0.13275 | 0.064087 | -0.050354 | -0.16937 | 0.004578 | 0.068665 | -0.20599 | -0.036621 | -0.041199 | 122.8592 | 122.9324 | 59.0195 | -122.9187 | 122.8729 | 122.8271 | 59.0927 | -123.0377
30.0156 | 123.2529 | -59.0195 | 63.8626 | -0.14511 | 0.0014675 | 0.065473 | 0.072653 | 0.12971 | -0.0056311 | -0.0040867 | -0.0077819 | -0.0020764 | 0.06341 | 0.062953 | -0.0019868 | -0.0012924 | 63.9267 | 64.0686 | 0.082397 | -59.2026 | 63.8214 | -59.0607 | -59.0927 | -58.9279 | 0.16479 | -59.198 | 63.8718 | 63.8123 | -59.0973 | -59.2209 | -0.041199 | -0.073242 | -0.041199 | 123.0881 | -0.18311 | -0.10986 | 0.064087 | -0.07782 | -0.20142 | 0.009155 | 0.091553 | -0.17853 | 0.022888 | -0.050354 | 122.8409 | 122.9462 | 59.1019 | -122.9553 | 122.8912 | 122.8317 | 59.1843 | -123.0835
31.0156 | 123.2208 | -59.0698 | 63.8306 | 0.14481 | 0.0061673 | 0.065473 | 0.066245 | 0.13356 | 0.00056395 | -0.0015231 | 0.17532 | -0.0037854 | 0.064051 | 0.062953 | 0.0020722 | -0.0030014 | 63.8763 | 63.9816 | -0.032043 | -59.2392 | 63.8397 | -59.0881 | -59.1293 | -58.9783 | 0.032043 | -59.2758 | 63.8306 | 63.7344 | -59.1431 | -59.2163 | -0.018311 | -0.059509 | 0.009156 | 123.0515 | -0.16937 | -0.10986 | 0.045777 | -0.073242 | -0.14649 | 0 | 0.091553 | -0.20599 | -0.059509 | -0.09613 | 122.9095 | 122.9462 | 59.0378 | -122.9599 | 122.9004 | 122.8043 | 59.1019 | -123.0469
32.0156 | 123.1201 | -59.0927 | 63.8397 | 0.12955 | 0.0089443 | 0.065473 | 0.069235 | 0.13185 | 0.00077755 | 0.0010403 | 0.12192 | -0.0020764 | 0.062555 | 0.061671 | 0.0033538 | -0.0036424 | 63.7894 | 63.8672 | -0.13733 | -59.317 | 63.8672 | -59.111 | -59.1614 | -59.0515 | -0.09613 | -59.3994 | 63.8855 | 63.7985 | -59.1339 | -59.2712 | -0.018311 | -0.068665 | 0.027465 | 122.9599 | -0.22431 | -0.15564 | -0.050354 | -0.041199 | -0.17853 | 0.045776 | 0.041198 | -0.3067 | -0.12817 | -0.041199 | 122.9599 | 122.8821 | 58.9554 | -123.0011 | 122.9782 | 122.8912 | 58.9966 | -123.111
33.0156 | 123.1567 | -59.0698 | 63.7985 | 0.16769 | 0.0061673 | 0.067396 | 0.068808 | 0.1295 | -0.00050425 | -0.00088226 | 0.21347 | -0.0014356 | 0.061701 | 0.065943 | 0.00057682 | -0.0012924 | 63.8168 | 63.858 | -0.12817 | -59.3124 | 63.8489 | -59.1293 | -59.1614 | -59.0286 | -0.050354 | -59.3582 | 63.858 | 63.7619 | -59.1385 | -59.2346 | -0.059509 | -0.091553 | 0.050354 | 122.9279 | -0.24262 | -0.15106 | 0.01831 | -0.068665 | -0.1648 | 0.059509 | 0.041199 | -0.28839 | -0.1236 | -0.036621 | 122.9187 | 122.8867 | 58.9416 | -122.9599 | 122.9279 | 122.8317 | 59.0195 | -123.0331
34.0156 | 123.0835 | -59.1064 | 63.8718 | 0.099029 | 0.0087307 | 0.067396 | 0.069235 | 0.13142 | 0.00013675 | -0.00045506 | 0.12955 | -0.00036736 | 0.063196 | 0.062739 | 0.0024994 | -0.0019334 | 63.7802 | 63.8077 | -0.15564 | -59.3308 | 63.8672 | -59.1248 | -59.166 | -59.0744 | -0.091553 | -59.404 | 63.858 | 63.8077 | -59.1339 | -59.285 | -0.018311 | -0.05951 | -0.004578 | 122.9141 | -0.22431 | -0.1648 | -0.091553 | -0.027466 | -0.17853 | -0.013733 | 0.032043 | -0.29755 | -0.11902 | -0.064087 | 122.9736 | 122.8867 | 58.9508 | -123.0377 | 122.9645 | 122.9141 | 59.0149 | -123.1567
35.0156 | 123.1888 | -59.0607 | 63.8168 | 0.13718 | 0.0044583 | 0.065901 | 0.065817 | 0.13206 | -0.0017859 | -0.00088226 | 0.25925 | -0.0050672 | 0.061273 | 0.062098 | 0.0020722 | -0.0017196 | 63.8855 | 63.9816 | -0.032043 | -59.2438 | 63.8214 | -59.1202 | -59.1202 | -58.9645 | 0.036621 | -59.2804 | 63.8123 | 63.7756 | -59.1568 | -59.2346 | -0.059509 | -0.059509 | 0.004578 | 123.0423 | -0.18311 | -0.1236 | 0.068665 | -0.09613 | -0.17395 | -0.004577 | 0.09613 | -0.21973 | -0.045777 | -0.041198 | 122.8821 | 122.9462 | 59.0286 | -122.937 | 122.8729 | 122.8363 | 59.0973 | -123.0515
36.0156 | 123.0972 | -59.079 | 63.8443 | 0.15244 | 0.0055265 | 0.065901 | 0.067313 | 0.13185 | -0.00071785 | -0.0023777 | 0.11429 | -0.0033582 | 0.06341 | 0.062312 | 0.0031402 | -0.0030014 | 63.7711 | 63.8489 | -0.13733 | -59.317 | 63.8809 | -59.1156 | -59.1705 | -59.0744 | -0.09613 | -59.3857 | 63.8992 | 63.7894 | -59.166 | -59.2667 | -0.036622 | -0.091553 | 0.036621 | 122.9279 | -0.23804 | -0.14648 | -0.073242 | -0.086976 | -0.18768 | 0.054932 | 0.004577 | -0.3067 | -0.11902 | -0.054931 | 122.9599 | 122.85 | 58.9416 | -123.0148 | 122.9782 | 122.8683 | 58.9828 | -123.111
37.0156 | 123.1842 | -59.0561 | 63.8031 | 0.2211 | 0.0059537 | 0.066114 | 0.067954 | 0.13377 | -0.0013587 | -2.7856e-05 | 0.22873 | -0.00036736 | 0.064478 | 0.062098 | 0.0016448 | -0.0017196 | 63.8626 | 63.9587 | -0.064087 | -59.2392 | 63.8351 | -59.1064 | -59.1522 | -58.9737 | 0.027466 | -59.2758 | 63.8351 | 63.7711 | -59.1339 | -59.2255 | -0.050354 | -0.096131 | 0.032043 | 123.0148 | -0.18311 | -0.086975 | 0.059509 | -0.07782 | -0.16937 | 0.032043 | 0.082397 | -0.21973 | -0.050354 | -0.032044 | 122.8912 | 122.9187 | 58.992 | -122.9553 | 122.8912 | 122.8271 | 59.0836 | -123.0286
38.0156 | 123.0927 | -59.1019 | 63.8397 | 0.16769 | 0.0080899 | 0.065473 | 0.071158 | 0.13121 | 0.0016321 | 0.00039954 | 0.12955 | -0.0020764 | 0.063837 | 0.062098 | 0.00549 | -0.0040696 | 63.7756 | 63.8397 | -0.11902 | -59.3033 | 63.8763 | -59.1064 | -59.1431 | -59.0836 | -0.09613 | -59.3994 | 63.8718 | 63.8214 | -59.1522 | -59.2621 | -0.004577 | -0.041198 | 0.036621 | 122.9416 | -0.20142 | -0.16022 | -0.064087 | -0.050354 | -0.16022 | 0.032043 | 0.018311 | -0.29755 | -0.13733 | -0.018311 | 122.9782 | 122.8775 | 58.9828 | -122.9828 | 122.9736 | 122.9233 | 59.0057 | -123.1018
39.0156 | 123.1842 | -59.0744 | 63.7894 | -0.77835 | 0.0080899 | 0.067182 | 0.069449 | 0.13185 | -7.6852e-05 | -0.0015231 | 0.25925 | -0.0018628 | 0.062769 | 0.063166 | 0.00014962 | -0.003856 | 63.8031 | 63.9359 | -0.07782 | -59.2667 | 63.8168 | -59.1064 | -59.1385 | -58.9783 | 0.022888 | -59.2896 | 63.8351 | 63.7619 | -59.1385 | -59.2072 | -0.032043 | -0.064087 | 0.027465 | 123.0103 | -0.19226 | -0.12817 | 0.013733 | -0.064087 | -0.13275 | 0.045776 | 0.096131 | -0.21515 | -0.082398 | -0.027466 | 122.8912 | 122.8775 | 58.9966 | -122.9279 | 122.9095 | 122.8363 | 59.0973 | -122.9965
40.0156 | 123.056 | -59.1248 | 63.8489 | 0.060882 | 0.0078763 | 0.065687 | 0.071158 | 0.13142 | 0.0012047 | -0.0015231 | 0.15244 | -0.0014356 | 0.064264 | 0.062312 | 0.0018584 | -0.0044968 | 63.7756 | 63.8077 | -0.15564 | -59.3216 | 63.8763 | -59.111 | -59.166 | -59.0698 | -0.086975 | -59.404 | 63.9038 | 63.8214 | -59.1568 | -59.2575 | 0.013733 | -0.041199 | 0.027466 | 122.9324 | -0.19684 | -0.15564 | -0.073242 | -0.032043 | -0.13275 | 0.054932 | 0.054932 | -0.27924 | -0.14649 | -0.027466 | 123.0011 | 122.9004 | 58.9691 | -123.0148 | 123.0286 | 122.9462 | 59.0378 | -123.1064
41.0156 | 123.1796 | -59.0607 | 63.8077 | 0.21347 | 0.0080899 | 0.066114 | 0.065604 | 0.13099 | -0.0043495 | -0.0028049 | 0.17532 | -0.0014356 | 0.063623 | 0.066371 | 0.0029266 | -0.0017196 | 63.9175 | 63.7894 | -0.15106 | -59.2712 | 63.8306 | -59.1064 | -59.1568 | -59.0012 | 0 | -59.2941 | 63.8397 | 63.7573 | -59.1431 | -59.2621 | -0.045776 | -0.09613 | 0.022888 | 122.85 | -0.21057 | -0.11444 | 0.10986 | -0.082397 | -0.20142 | 0.032044 | 0.059509 | -0.23346 | -0.032043 | -0.050354 | 122.8912 | 122.9782 | 58.9096 | -122.9645 | 122.9004 | 122.818 | 59.0607 | -123.0698
42.0156 | 123.0927 | -59.0927 | 63.826 | 0.14481 | 0.0061673 | 0.067182 | 0.070731 | 0.13334 | -0.00029045 | -0.0010959 | 0.19821 | -0.0014356 | 0.065546 | 0.061244 | 0.0035674 | -0.0012924 | 63.7894 | 63.8626 | -0.14191 | -59.3079 | 63.8901 | -59.0973 | -59.1568 | -59.0561 | -0.086975 | -59.3719 | 63.8718 | 63.7939 | -59.1614 | -59.2575 | -0.004578 | -0.064087 | 0.064087 | 122.9553 | -0.21515 | -0.15106 | -0.036621 | -0.068665 | -0.16479 | 0.045776 | 0.036621 | -0.27924 | -0.11444 | -0.032044 | 122.9828 | 122.8821 | 58.9508 | -122.9828 | 122.9645 | 122.8867 | 59.0057 | -123.0835
43.0156 | 123.1979 | -59.0698 | 63.7939 | 0.16006 | 0.0061673 | 0.067396 | 0.066031 | 0.13185 | -0.0022131 | -0.0023777 | 0.26688 | -0.001222 | 0.06106 | 0.061457 | 0.0033538 | -0.0034286 | 63.8443 | 63.9999 | -0.022888 | -59.2163 | 63.8031 | -59.0973 | -59.1293 | -58.9645 | 0.018311 | -59.2758 | 63.7985 | 63.7573 | -59.1476 | -59.2621 | -0.027466 | -0.059509 | 0.009156 | 123.0698 | -0.14649 | -0.086976 | 0.050354 | -0.07782 | -0.19226 | 0.004578 | 0.10528 | -0.20599 | -0.013733 | -0.036621 | 122.8729 | 122.9141 | 59.0469 | -122.9233 | 122.8683 | 122.8271 | 59.0881 | -123.056
44.0781 | 123.1522 | -59.0744 | 63.8489 | -0.11459 | 0.0083035 | 0.066328 | 0.068808 | 0.13441 | 0.0016321 | -0.00045506 | -0.099335 | -0.0016492 | 0.064051 | 0.062525 | 0.0029266 | -0.0040696 | 63.8672 | 63.9404 | -0.027466 | -59.2392 | 63.8992 | -59.0881 | -59.1293 | -58.9966 | 0.064087 | -59.3124 | 63.913 | 63.8443 | -59.1202 | -59.2712 | -0.013733 | -0.054931 | 0.050354 | 123.0148 | -0.16479 | -0.10986 | 0.01831 | -0.045776 | -0.19684 | 0.064087 | 0.07782 | -0.23804 | -0.041199 | -0.004578 | 122.9736 | 122.9416 | 59.0469 | -122.9782 | 122.9874 | 122.9187 | 59.1385 | -123.1201
45.0156 | 123.2025 | -59.0561 | 63.8123 | 0.16006 | 0.0048855 | 0.066541 | 0.067954 | 0.13099 | -0.0013587 | 0.00039954 | 0.25925 | -0.0018628 | 0.064905 | 0.061244 | 0.0024994 | -0.0027878 | 63.8763 | 63.9816 | -0.027466 | -59.2438 | 63.826 | -59.0881 | -59.1293 | -58.9783 | 0.032043 | -59.2667 | 63.8214 | 63.7436 | -59.1522 | -59.2346 | -0.032044 | -0.073242 | 0.013733 | 123.0377 | -0.18768 | -0.11444 | 0.064087 | -0.096131 | -0.17853 | 0.009155 | 0.07782 | -0.21057 | -0.032044 | -0.068665 | 122.8821 | 122.9324 | 59.0286 | -122.9416 | 122.8775 | 122.7997 | 59.0881 | -123.0469
46.0156 | 123.0515 | -59.079 | 63.858 | 0.10666 | 0.0087307 | 0.066328 | 0.068381 | 0.13014 | 0.00077755 | -0.00024146 | 0.12955 | -0.0016492 | 0.064264 | 0.063807 | 0.0022858 | -0.003215 | 63.7711 | 63.826 | -0.15106 | -59.3079 | 63.8809 | -59.1202 | -59.166 | -59.0927 | -0.086975 | -59.404 | 63.8809 | 63.8123 | -59.1522 | -59.2758 | -0.041199 | -0.086976 | 0.022888 | 122.905 | -0.22888 | -0.14191 | -0.086975 | -0.073243 | -0.19684 | 0.022888 | -0.013733 | -0.32501 | -0.12817 | -0.045776 | 122.9599 | 122.85 | 58.9279 | -123.024 | 122.9599 | 122.8912 | 58.992 | -123.1338
47.0156 | 123.1796 | -59.0424 | 63.8031 | 0.21347 | 0.0063809 | 0.065473 | 0.068167 | 0.13014 | -0.0037085 | -0.0028049 | 0.19058 | -0.0018628 | 0.064051 | 0.06103 | 0.0031402 | -0.003215 | 63.9633 | 63.8809 | -0.17395 | -59.3124 | 63.8672 | -59.1019 | -59.1568 | -59.0012 | 0 | -59.2941 | 63.826 | 63.7665 | -59.1248 | -59.2255 | -0.05951 | -0.11444 | 0.064086 | 122.9233 | -0.27008 | -0.15564 | 0.16022 | -0.082398 | -0.18311 | 0.022888 | 0.041198 | -0.25177 | -0.068664 | -0.036622 | 122.9095 | 123.0057 | 58.8684 | -122.9599 | 122.8683 | 122.8088 | 59.0424 | -123.0286
48.0156 | 123.111 | -59.0927 | 63.8397 | 0.16769 | 0.0093717 | 0.06761 | 0.067313 | 0.13099 | -0.00029045 | -0.00045506 | 0.20584 | -0.0025038 | 0.065332 | 0.061885 | -0.00049138 | -0.0012924 | 63.7985 | 63.8443 | -0.13733 | -59.3033 | 63.8763 | -59.111 | -59.1568 | -59.0515 | -0.082397 | -59.3674 | 63.8718 | 63.7985 | -59.1431 | -59.2667 | -0.018311 | -0.064087 | 0.036621 | 122.937 | -0.21057 | -0.14648 | -0.041199 | -0.050354 | -0.17395 | 0.032043 | 0.041198 | -0.27466 | -0.10071 | -0.041199 | 122.9691 | 122.8912 | 58.9554 | -122.9965 | 122.9645 | 122.8912 | 59.0103 | -123.1064
49.0156 | 123.1338 | -59.0424 | 63.8306 | 0.16769 | 0.0036039 | 0.067396 | 0.067954 | 0.12864 | -0.0052039 | 0.0012539 | 0.27451 | -0.00036736 | 0.063623 | 0.062525 | 0.0012176 | -1.0768e-05 | 63.858 | 63.9816 | -0.032043 | -59.2621 | 63.8123 | -59.079 | -59.1339 | -58.9828 | 0.022888 | -59.285 | 63.8168 | 63.7756 | -59.1385 | -59.2621 | -0.036621 | -0.091553 | -0.01831 | 123.024 | -0.21973 | -0.12817 | 0.027466 | -0.096131 | -0.21973 | -0.013733 | 0.059509 | -0.24262 | -0.022888 | -0.054931 | 122.8546 | 122.9004 | 59.0103 | -122.9645 | 122.8592 | 122.818 | 59.0652 | -123.0927
50.0156 | 123.1934 | -59.0836 | 63.8077 | 1.4494 | 0.0063809 | 0.068037 | 0.069022 | 0.1327 | -0.00029045 | -0.0021641 | 0.36606 | -0.002931 | 0.063623 | 0.06103 | 0.00079042 | -0.0025742 | 63.8672 | 63.9404 | -0.073242 | -59.2529 | 63.826 | -59.0881 | -59.1339 | -58.9874 | 0.009155 | -59.285 | 63.826 | 63.7665 | -59.1248 | -59.23 | -0.004578 | -0.050354 | 0.018311 | 123.024 | -0.16937 | -0.11902 | 0.059509 | -0.041199 | -0.14648 | 0.018311 | 0.09613 | -0.20142 | -0.054931 | -0.041199 | 122.9095 | 122.9507 | 59.0103 | -122.9416 | 122.9095 | 122.85 | 59.0927 | -123.0377
51.0156 | 123.0972 | -59.0698 | 63.7894 | 0.16769 | 0.0040311 | 0.066114 | 0.06774 | 0.12758 | -0.0043495 | -0.0034457 | 0.30502 | -0.0037854 | 0.064264 | 0.06103 | -0.00049138 | -0.00065157 | 63.8535 | 63.9771 | -0.032043 | -59.2484 | 63.7985 | -59.0836 | -59.1202 | -58.992 | 0.20599 | -59.3353 | 63.8489 | 63.7711 | -59.1293 | -59.2484 | -0.013733 | -0.050354 | 0.009155 | 123.0469 | -0.17853 | -0.12817 | 0.064087 | -0.059509 | -0.17853 | 0.059509 | 0.07782 | -0.2655 | -0.086975 | -0.018311 | 122.8683 | 122.9233 | 59.0378 | -122.9095 | 122.9187 | 122.8409 | 59.2758 | -123.0377
52.0156 | 123.2117 | -59.0332 | 63.7848 | 0.28976 | 0.0085171 | 0.067823 | 0.068594 | 0.13142 | -0.0011451 | -0.0023777 | 0.20584 | -0.0016492 | 0.065332 | 0.063807 | 0.0024994 | -0.0030014 | 63.858 | 63.9816 | -0.045776 | -59.2484 | 63.826 | -59.079 | -59.1248 | -58.9691 | 0.013733 | -59.2804 | 63.8351 | 63.7711 | -59.1431 | -59.2621 | -0.045776 | -0.091553 | 0.041199 | 123.0148 | -0.21515 | -0.1236 | 0.073242 | -0.10986 | -0.22888 | 0.050354 | 0.064087 | -0.24719 | -0.018311 | -0.013733 | 122.8592 | 122.8912 | 58.9874 | -122.9095 | 122.8683 | 122.8043 | 59.0469 | -123.0469
53.0156 | 123.1659 | -59.0286 | 63.8123 | 0.12955 | 0.0023221 | 0.065901 | 0.067954 | 0.1295 | -0.0062721 | -0.0030185 | -0.099335 | -0.0031446 | 0.062342 | 0.063166 | 0.0016448 | -0.00086517 | 63.858 | 63.9816 | -0.045776 | -59.2621 | 63.8168 | -59.079 | -59.1339 | -59.0012 | 0.009155 | -59.3079 | 63.8306 | 63.8031 | -59.1293 | -59.2392 | -0.050354 | -0.10529 | 0.004577 | 123.0103 | -0.23346 | -0.12817 | 0.045776 | -0.10071 | -0.21057 | 0.01831 | 0.027465 | -0.27924 | -0.068664 | -0.009155 | 122.8455 | 122.8867 | 58.9828 | -122.9462 | 122.8592 | 122.8317 | 59.0378 | -123.0515
54.0156 | 123.1842 | -59.0698 | 63.8168 | 0.19058 | 0.0087307 | 0.066328 | 0.069663 | 0.13099 | 0.00099115 | -0.00024146 | 1.4113 | -0.0035718 | 0.063196 | 0.06338 | 0.0059174 | -0.0036424 | 63.826 | 63.8992 | -0.11444 | -59.2804 | 63.8535 | -59.1064 | -59.1431 | -59.0103 | -0.004578 | -59.317 | 63.8443 | 63.7619 | -59.1431 | -59.2438 | -0.036621 | -0.073242 | 0.036622 | 122.9691 | -0.21057 | -0.13733 | 0.009156 | -0.073242 | -0.17395 | 0.027466 | 0.059509 | -0.24719 | -0.073243 | -0.054931 | 122.9233 | 122.8958 | 58.9554 | -122.9599 | 122.9141 | 122.8317 | 59.0652 | -123.0606
55.0156 | 123.1338 | -59.0652 | 63.826 | -1.0835 | 0.0029629 | 0.064405 | 0.066458 | 0.13206 | -0.0011451 | -0.0021641 | 0.20584 | -0.00464 | 0.062128 | 0.064662 | 0.0029266 | -0.00043797 | 63.8123 | 63.9587 | -0.050354 | -59.2804 | 63.8168 | -59.0836 | -59.1293 | -59.0057 | 0.018311 | -59.2941 | 63.8397 | 63.7848 | -59.1293 | -59.2484 | -0.01831 | -0.064086 | -0.009156 | 123.024 | -0.21515 | -0.15106 | -0.013733 | -0.064086 | -0.1831 | 0.013733 | 0.05951 | -0.22888 | -0.045776 | -0.041199 | 122.8821 | 122.8775 | 59.0149 | -122.9553 | 122.905 | 122.85 | 59.0836 | -123.0743
56.0156 | 123.1888 | -59.0469 | 63.8306 | 0.23636 | 0.0046719 | 0.066114 | 0.068167 | 0.13142 | -0.0037085 | -0.0017369 | 0.10666 | -0.003999 | 0.063837 | 0.063594 | -0.00070498 | -0.0017196 | 63.8397 | 63.9496 | -0.050354 | -59.2712 | 63.8535 | -59.0836 | -59.1019 | -59.0012 | 0.013733 | -59.2941 | 63.858 | 63.7711 | -59.1293 | -59.2484 | -0.036621 | -0.054932 | 0.022889 | 122.9965 | -0.2243 | -0.16937 | 0.009156 | -0.082397 | -0.20142 | 0.027466 | 0.045776 | -0.24719 | -0.045776 | -0.059509 | 122.9004 | 122.8867 | 58.9966 | -122.9324 | 122.905 | 122.818 | 59.0607 | -123.0789
57.0156 | 123.1796 | -59.0378 | 63.8306 | 0.022736 | -0.00024129 | 0.06825 | 0.069449 | 0.12928 | -0.0030677 | -0.0010959 | 0.12192 | -0.0020764 | 0.061914 | 0.063807 | 0.0012176 | -0.0023606 | 63.8489 | 63.945 | -0.022888 | -59.2392 | 63.8535 | -59.0881 | -59.0881 | -58.9966 | 0.050354 | -59.2758 | 63.8672 | 63.7802 | -59.1019 | -59.2072 | -0.050354 | -0.050354 | 0.022889 | 122.9828 | -0.20142 | -0.15106 | 0.018311 | -0.064087 | -0.16937 | 0.036621 | 0.041199 | -0.23804 | -0.068665 | -0.050354 | 122.8912 | 122.8867 | 59.0149 | -122.9187 | 122.905 | 122.818 | 59.0881 | -123.0377
58.0156 | 123.1567 | -59.0652 | 63.8077 | 0.16006 | 0.0031765 | 0.064832 | 0.066672 | 0.1295 | 0.0018457 | -0.0017369 | 0.24399 | -0.0027174 | 0.062342 | 0.060603 | -0.00070498 | -0.00065157 | 63.8763 | 63.9862 | -0.013733 | -59.2484 | 63.8351 | -59.1202 | -59.1156 | -58.9828 | -0.09613 | -59.2941 | 63.8306 | 63.7482 | -59.1431 | -59.2438 | -0.054931 | -0.050354 | 0.027466 | 123.0515 | -0.1831 | -0.13275 | 0.068665 | -0.077819 | -0.17853 | 0.022888 | 0.082398 | -0.22888 | -0.050354 | -0.059509 | 122.9004 | 122.9416 | 59.0515 | -122.9233 | 122.8958 | 122.8134 | 58.9691 | -123.0515
59.0156 | 123.1796 | -59.0607 | 63.8168 | -0.0077822 | 0.0010403 | 0.06526 | 0.069663 | 0.13142 | -0.0030677 | -0.0030185 | 0.060883 | -0.0052808 | 0.062342 | 0.062098 | 0.0016448 | -0.0034286 | 63.8443 | 63.9542 | -0.027466 | -59.2346 | 63.8718 | -59.0973 | -59.1339 | -58.9828 | 0.064087 | -59.2484 | 63.858 | 63.7985 | -59.1202 | -59.2117 | -0.036621 | -0.073242 | 0.054932 | 123.0148 | -0.17395 | -0.10071 | 0.027466 | -0.059509 | -0.15106 | 0.041199 | 0.07782 | -0.18768 | -0.036621 | -0.01831 | 122.9324 | 122.905 | 59.0332 | -122.9507 | 122.9187 | 122.8592 | 59.1248 | -123.0286
60.0156 | 123.1842 | -59.0378 | 63.8214 | 0.17532 | 0.0040311 | 0.068037 | 0.066672 | 0.13249 | 0.0018457 | -0.0017369 | 0.27451 | -0.00464 | 0.063196 | 0.063166 | 0.0029266 | -0.002147 | 63.8901 | 64.0137 | -0.018311 | -59.2392 | 63.8168 | -59.079 | -59.1202 | -58.9691 | 0.050354 | -59.2667 | 63.8489 | 63.7436 | -59.1568 | -59.2346 | -0.041198 | -0.082397 | -0.004578 | 123.0515 | -0.20142 | -0.11902 | 0.068665 | -0.11902 | -0.19684 | 0.027466 | 0.068665 | -0.22888 | -0.032044 | -0.07782 | 122.8546 | 122.9279 | 59.0195 | -122.9416 | 122.8867 | 122.7814 | 59.0881 | -123.056
61.0156 | 123.1705 | -59.0332 | 63.8214 | -0.015411 | -0.00088229 | 0.066114 | 0.064536 | 0.12993 | -0.0032813 | -0.0036595 | 0.19058 | -0.0035718 | 0.063196 | 0.061885 | 0.0035674 | -0.0023606 | 63.8535 | 63.9587 | -0.036621 | -59.2575 | 63.8626 | -59.0881 | -59.1293 | -59.0012 | 0.013733 | -59.2896 | 63.8351 | 63.7665 | -59.111 | -59.23 | -0.054932 | -0.09613 | 0.041199 | 122.9919 | -0.2243 | -0.12817 | 0.032044 | -0.07782 | -0.19684 | 0.013733 | 0.032043 | -0.25635 | -0.059509 | -0.054932 | 122.8958 | 122.8867 | 58.9966 | -122.9507 | 122.8683 | 122.7997 | 59.0469 | -123.0515
62.0156 | 123.143 | -59.0561 | 63.8168 | 0.16006 | 0.0029629 | 0.066755 | 0.067526 | 0.13398 | 0.00035035 | 0.00039954 | 0.12192 | -0.0016492 | 0.064264 | 0.061457 | 0.001004 | -0.0019334 | 63.7573 | 64.0228 | -0.022888 | -59.285 | 63.8351 | -59.079 | -59.1202 | -58.9874 | 0.018311 | -59.3124 | 63.8443 | 63.7482 | -59.1248 | -59.2346 | -0.022888 | -0.064087 | 0.018311 | 123.0789 | -0.22888 | -0.16479 | -0.059509 | -0.068665 | -0.17853 | 0.027466 | 0.068664 | -0.25635 | -0.07782 | -0.068664 | 122.8912 | 122.8134 | 59.0332 | -122.937 | 122.9004 | 122.8043 | 59.0744 | -123.0515
63.0156 | 123.2162 | -59.0057 | 63.8306 | -0.015411 | 0.00061311 | 0.066755 | 0.067526 | 0.1327 | -0.0011451 | -0.0013095 | -0.015411 | -0.0018628 | 0.063623 | 0.064662 | -0.0013458 | -0.0030014 | 63.9221 | 64.0411 | 0.054932 | -59.2117 | 63.858 | -59.0607 | -59.1248 | -58.905 | 0.1831 | -59.1797 | 63.858 | 63.7665 | -59.0881 | -59.2117 | -0.054932 | -0.11902 | 0.027466 | 123.0469 | -0.20599 | -0.086975 | 0.091553 | -0.082398 | -0.20599 | 0.027466 | 0.10071 | -0.17395 | 0.032044 | -0.064087 | 122.8638 | 122.9279 | 59.0607 | -122.9553 | 122.8638 | 122.7722 | 59.1888 | -123.0423
64.0156 | 123.1796 | -59.0469 | 63.8351 | -0.00015269 | 0.0018949 | 0.06526 | 0.069663 | 0.12993 | 0.00056395 | -0.0043003 | 0.09903 | -0.00464 | 0.06106 | 0.062312 | 0.0014312 | -0.001506 | 63.8489 | 63.9633 | -0.041199 | -59.2621 | 63.8443 | -59.0698 | -59.1293 | -58.9966 | 0.036621 | -59.3079 | 63.8535 | 63.7756 | -59.1248 | -59.2209 | -0.022888 | -0.082397 | 0.009155 | 123.0103 | -0.21515 | -0.13275 | 0.013733 | -0.07782 | -0.17395 | 0.018311 | 0.050354 | -0.26093 | -0.086975 | -0.059509 | 122.8912 | 122.8958 | 59.0057 | -122.9645 | 122.9004 | 122.8226 | 59.0836 | -123.056
65.0156 | 123.23 | -59.0149 | 63.8443 | -0.12985 | 0.0023221 | 0.067823 | 0.068167 | 0.13099 | 0.00099115 | -0.0017369 | -0.0077819 | -0.002931 | 0.062769 | 0.061885 | 0.0020722 | -0.003856 | 63.9038 | 64.064 | 0.059509 | -59.1934 | 63.8489 | -59.0927 | -59.111 | -58.8913 | 0.16937 | -59.198 | 63.858 | 63.7756 | -59.0973 | -59.23 | -0.077819 | -0.09613 | 0.004578 | 123.0789 | -0.17853 | -0.082397 | 0.05951 | -0.082397 | -0.21515 | 0.013733 | 0.1236 | -0.1831 | 0.032044 | -0.068664 | 122.8638 | 122.9187 | 59.0744 | -122.9553 | 122.8729 | 122.7905 | 59.1843 | -123.0743
66.0156 | 123.1522 | -59.0744 | 63.826 | 0.045624 | 0.00082671 | 0.067396 | 0.067313 | 0.13163 | -0.0022131 | -0.00045506 | 0.068512 | -0.002931 | 0.062982 | 0.061885 | -6.4178e-05 | -0.001506 | 63.8123 | 63.9725 | -0.032043 | -59.2575 | 63.8397 | -59.0698 | -59.1385 | -58.9828 | 0.022888 | -59.2987 | 63.858 | 63.739 | -59.1293 | -59.2392 | 0.004578 | -0.064087 | 0.013733 | 123.0469 | -0.1831 | -0.11902 | -0.013733 | -0.054931 | -0.16479 | 0.032043 | 0.091553 | -0.2243 | -0.059509 | -0.086975 | 122.9141 | 122.8867 | 59.0424 | -122.9645 | 122.9324 | 122.8134 | 59.0973 | -123.0652
67.0156 | 123.1842 | -59.0424 | 63.8306 | -0.0383 | 0.0014675 | 0.06526 | 0.068808 | 0.13121 | -0.0011451 | -0.0010959 | -0.00015237 | -0.0033582 | 0.063623 | 0.063166 | 0.0012176 | -0.0025742 | 63.8718 | 63.9908 | 0.013733 | -59.23 | 63.8535 | -59.0927 | -59.1248 | -58.9417 | 0.10529 | -59.2392 | 63.8672 | 63.7619 | -59.111 | -59.2209 | -0.050354 | -0.082398 | 0.022889 | 123.0331 | -0.18768 | -0.10529 | 0.041199 | -0.068665 | -0.17853 | 0.036621 | 0.10071 | -0.19684 | -0.018311 | -0.068664 | 122.8958 | 122.9141 | 59.0561 | -122.9553 | 122.9095 | 122.8043 | 59.1476 | -123.0515
68.0156 | 123.1796 | -59.0561 | 63.8168 | 0.17532 | 0.0025357 | 0.068037 | 0.064108 | 0.1295 | 0.00013675 | -0.0032321 | 0.13718 | -0.0027174 | 0.06106 | 0.06103 | 0.0029266 | -0.0025742 | 63.8947 | 63.9313 | -0.073242 | -59.2758 | 63.7985 | -59.0973 | -59.1522 | -58.9828 | 0.018311 | -59.2941 | 63.8718 | 63.7573 | -59.1293 | -59.2255 | -0.041199 | -0.096131 | -0.01831 | 122.9874 | -0.21973 | -0.1236 | 0.07782 | -0.073242 | -0.16937 | 0.054932 | 0.073242 | -0.23804 | -0.068664 | -0.059509 | 122.8546 | 122.9507 | 58.9828 | -122.9691 | 122.9279 | 122.8134 | 59.0744 | -123.0423
69.0156 | 123.2254 | -59.0149 | 63.8489 | -0.045929 | 0.00061311 | 0.06526 | 0.07009 | 0.13163 | -0.0015723 | -0.0013095 | -0.091705 | -0.0033582 | 0.064478 | 0.061671 | -6.4178e-05 | -0.0040696 | 63.9175 | 64.0594 | 0.050354 | -59.2117 | 63.8901 | -59.0652 | -59.1156 | -58.9096 | 0.16937 | -59.2072 | 63.8489 | 63.7802 | -59.1019 | -59.2072 | -0.050354 | -0.10071 | 0.041199 | 123.0743 | -0.19684 | -0.09613 | 0.068665 | -0.086975 | -0.19226 | 0 | 0.10529 | -0.19226 | 0 | -0.068665 | 122.905 | 122.9324 | 59.0652 | -122.9645 | 122.8638 | 122.7951 | 59.1843 | -123.056
70.0156 | 123.1979 | -59.024 | 63.8443 | -0.023041 | 0.0029629 | 0.066328 | 0.069022 | 0.12993 | -0.0017859 | -0.0045139 | -0.038299 | -0.0031446 | 0.061914 | 0.063594 | 0.0014312 | -0.0017196 | 63.858 | 64.0045 | -0.009155 | -59.2346 | 63.8718 | -59.0881 | -59.1156 | -58.9554 | 0.10529 | -59.2117 | 63.8718 | 63.8077 | -59.1064 | -59.166 | -0.064087 | -0.091553 | 0.027466 | 123.0286 | -0.21057 | -0.11902 | 0.013733 | -0.082397 | -0.14191 | 0.027466 | 0.068665 | -0.18768 | -0.045776 | -0.036621 | 122.8958 | 122.8821 | 59.0149 | -122.9599 | 122.8958 | 122.8317 | 59.1293 | -123.0103
71.0156 | 123.1613 | -59.0469 | 63.826 | -0.12985 | 0.0025357 | 0.06825 | 0.067099 | 0.13099 | -7.6852e-05 | -0.0021641 | -0.099335 | -0.002931 | 0.059992 | 0.062312 | 0.0024994 | -0.0036424 | 63.8992 | 64.064 | 0.082397 | -59.198 | 63.8626 | -59.0561 | -59.1064 | -58.9233 | 0.19684 | -59.2255 | 63.8855 | 63.7573 | -59.1064 | -59.2163 | -0.009155 | -0.059509 | 0.036621 | 123.111 | -0.15106 | -0.091553 | 0.073242 | -0.059509 | -0.16937 | 0.059509 | 0.1236 | -0.17853 | -0.009155 | -0.068665 | 122.9095 | 122.9462 | 59.1293 | -122.9324 | 122.9324 | 122.8043 | 59.2438 | -123.0423
72.0156 | 123.1888 | -59.0332 | 63.8123 | 0.0074768 | 0.0036039 | 0.068037 | 0.066458 | 0.13121 | -0.0017859 | -0.0023777 | 0.022736 | -0.0035718 | 0.061273 | 0.063807 | 0.0014312 | -0.0025742 | 63.8535 | 63.9908 | -0.027466 | -59.2392 | 63.8535 | -59.079 | -59.1064 | -58.96 | 0.07782 | -59.2484 | 63.8535 | 63.7573 | -59.111 | -59.2026 | -0.045776 | -0.073242 | 0.041199 | 123.024 | -0.20599 | -0.13275 | 0.041199 | -0.07782 | -0.16937 | 0.041199 | 0.073242 | -0.21515 | -0.045776 | -0.054932 | 122.8867 | 122.8867 | 59.0057 | -122.9187 | 122.8867 | 122.7905 | 59.111 | -123.0148
73.0156 | 123.1979 | -59.024 | 63.8489 | -0.14511 | 0.0018949 | 0.066755 | 0.068381 | 0.12928 | -0.00071785 | -0.0015231 | -0.076446 | -0.0033582 | 0.062128 | 0.062312 | 0.002713 | -0.0040696 | 63.9404 | 64.0961 | 0.10071 | -59.1797 | 63.8626 | -59.0469 | -59.1019 | -58.9188 | 0.17853 | -59.2209 | 63.8809 | 63.7299 | -59.1019 | -59.23 | -0.022888 | -0.07782 | 0.013733 | 123.1201 | -0.15564 | -0.077819 | 0.091553 | -0.07782 | -0.20599 | 0.032043 | 0.10529 | -0.19684 | 0.009156 | -0.11902 | 122.8867 | 122.9645 | 59.1248 | -122.9507 | 122.905 | 122.7539 | 59.2026 | -123.0789
74.0156 | 123.1293 | -59.0698 | 63.8351 | 0.19058 | 0.00082671 | 0.065901 | 0.068808 | 0.13035 | -0.0013587 | -2.7856e-05 | 0.12955 | -0.0037854 | 0.061701 | 0.060603 | -6.4178e-05 | -0.0025742 | 63.8443 | 63.9771 | -0.036621 | -59.2712 | 63.8763 | -59.0744 | -59.1248 | -58.9783 | 0.027466 | -59.2896 | 63.8443 | 63.7527 | -59.1156 | -59.2209 | -0.004578 | -0.054932 | 0.041199 | 123.0469 | -0.20142 | -0.14648 | 0.009155 | -0.045777 | -0.15106 | 0.009155 | 0.091553 | -0.21973 | -0.068665 | -0.082397 | 122.9462 | 122.9141 | 59.0332 | -122.9599 | 122.9141 | 122.8226 | 59.0973 | -123.056
75.0156 | 123.2071 | -59.0149 | 63.8535 | -0.084076 | 0.0027493 | 0.068678 | 0.067526 | 0.13185 | -0.0015723 | -0.0015231 | 0.62546 | -0.002931 | 0.06341 | 0.062525 | 0.0024994 | -0.0025742 | 63.8718 | 63.913 | 0.32501 | -59.0469 | 63.9267 | -59.0195 | -59.1385 | -58.9645 | 0.11902 | -59.2484 | 63.8672 | 63.7344 | -59.1248 | -59.2255 | -0.004577 | -0.1236 | 0.073242 | 122.9279 | -0.032043 | 0.091553 | 0.01831 | -0.10986 | -0.21057 | 0.013732 | 0.050354 | -0.23346 | -0.022888 | -0.11902 | 122.9416 | 122.8867 | 59.3399 | -122.9919 | 122.8821 | 122.7493 | 59.1339 | -123.0789
76.0156 | 123.1567 | -59.0561 | 63.8123 | 0.037994 | 0.00082671 | 0.069319 | 0.068808 | 0.1327 | -7.6852e-05 | -0.0025913 | 0.083771 | -0.0048536 | 0.06106 | 0.062739 | 0.0012176 | -0.002147 | 63.8306 | 63.9633 | -0.027466 | -59.2438 | 63.8626 | -59.0927 | -59.111 | -58.9966 | 0.041199 | -59.285 | 63.858 | 63.7482 | -59.1476 | -59.2438 | -0.036621 | -0.054932 | 0.050354 | 123.0194 | -0.18768 | -0.13275 | 0.01831 | -0.091553 | -0.18768 | 0.045776 | 0.059509 | -0.22888 | -0.041199 | -0.064087 | 122.9187 | 122.8867 | 59.0286 | -122.9233 | 122.9141 | 122.8043 | 59.0973 | -123.056
77.0156 | 123.1888 | -59.0286 | 63.8626 | -0.14511 | 0.0010403 | 0.068678 | 0.068167 | 0.12971 | -0.0019995 | -0.0030185 | -0.12985 | -0.002931 | 0.062555 | 0.061885 | 0.0035674 | -0.0040696 | 63.9313 | 64.0732 | 0.091553 | -59.2026 | 63.8214 | -59.0744 | -59.1019 | -58.9417 | 0.18768 | -59.23 | 63.8672 | 63.7436 | -59.0927 | -59.2072 | -0.045777 | -0.073243 | -0.041199 | 123.1018 | -0.17395 | -0.10071 | 0.068664 | -0.064087 | -0.17853 | 0.004577 | 0.086975 | -0.20142 | -0.022889 | -0.11902 | 122.85 | 122.9599 | 59.1202 | -122.9645 | 122.8958 | 122.7722 | 59.2163 | -123.0698
78.0156 | 123.2346 | -59.0332 | 63.8351 | -0.0383 | 0.00018591 | 0.06761 | 0.069022 | 0.12993 | -0.00071785 | -0.0021641 | 0.060883 | -0.0037854 | 0.061914 | 0.061244 | 0.0022858 | -0.0027878 | 63.8718 | 64.0137 | 0.004578 | -59.23 | 63.8535 | -59.0744 | -59.1202 | -58.9371 | 0.10986 | -58.9188 | 63.9313 | 63.8031 | -59.0652 | -59.2209 | -0.041199 | -0.086975 | 0.018311 | 123.0469 | -0.19684 | -0.10986 | 0.036621 | -0.032044 | -0.18768 | 0.09613 | 0.09613 | 0.11444 | 0.30212 | -0.032043 | 122.8867 | 122.905 | 59.0378 | -122.9553 | 122.9645 | 122.8363 | 59.1431 | -123.056
79.0156 | 123.2162 | -59.0012 | 63.8535 | -0.18326 | 0.0025357 | 0.066328 | 0.069022 | 0.13163 | -7.6852e-05 | -0.0010959 | -0.13748 | -0.0037854 | 0.062128 | 0.063166 | 0.0022858 | -0.003215 | 63.9221 | 64.0686 | 0.07782 | -59.1888 | 63.858 | -59.0607 | -59.1064 | -58.905 | 0.1831 | -59.2072 | 63.8718 | 63.7527 | -59.0927 | -59.2072 | -0.059509 | -0.10529 | 0.004577 | 123.0698 | -0.18768 | -0.082398 | 0.068664 | -0.091552 | -0.20599 | 0.01831 | 0.096131 | -0.20599 | 0 | -0.10071 | 122.8592 | 122.9233 | 59.079 | -122.9599 | 122.8729 | 122.7539 | 59.1843 | -123.0606
80.0156 | 123.1384 | -59.0424 | 63.8489 | 0.015106 | 0.0010403 | 0.065687 | 0.068381 | 0.12971 | -0.00029045 | -0.0021641 | -0.0077819 | -0.0031446 | 0.061914 | 0.06338 | 0.0024994 | -0.003856 | 63.8397 | 63.9908 | -0.009155 | -59.2346 | 63.8809 | -59.1019 | -59.1385 | -58.9554 | 0.10529 | -59.2621 | 63.8489 | 63.7436 | -59.1293 | -59.23 | -0.05951 | -0.096131 | 0.032043 | 123.0331 | -0.19226 | -0.09613 | -0.009155 | -0.086975 | -0.18768 | 0 | 0.086975 | -0.21973 | -0.032043 | -0.10529 | 122.9233 | 122.8821 | 59.0332 | -122.9874 | 122.8912 | 122.7859 | 59.1476 | -123.0789
81.0156 | 123.2986 | -59.0378 | 63.8077 | -0.061188 | 0.00061311 | 0.068464 | 0.067313 | 0.13292 | -0.00050425 | -0.0025913 | 0.015106 | -0.0052808 | 0.059992 | 0.05868 | 0.002713 | -0.003856 | 63.8809 | 64.0274 | 0.036621 | -59.2209 | 63.8443 | -59.079 | -59.1339 | -58.9142 | 0.17395 | -59.0103 | 63.9404 | 63.8214 | -59.0652 | -59.1705 | -0.041198 | -0.09613 | 0.036621 | 123.0652 | -0.1831 | -0.086975 | 0.073242 | -0.027466 | -0.13275 | 0.13275 | 0.1236 | 0.027466 | 0.16022 | 0.013733 | 122.8821 | 122.9187 | 59.0744 | -122.9416 | 122.9782 | 122.8592 | 59.2117 | -122.9782
82.0156 | 123.1613 | -59.0424 | 63.8443 | -0.00015269 | 0.0010403 | 0.066969 | 0.067313 | 0.13078 | -0.0011451 | -0.0023777 | 0.053253 | -0.003999 | 0.06341 | 0.059962 | 0.0018584 | -0.002147 | 63.826 | 63.9771 | -0.032043 | -59.2529 | 63.8626 | -59.0744 | -59.1476 | -58.9737 | 0.086975 | -59.2484 | 63.8672 | 63.739 | -59.1339 | -59.2346 | -0.032044 | -0.10529 | 0.018311 | 123.0194 | -0.21057 | -0.10529 | -0.01831 | -0.091553 | -0.19226 | 0.022888 | 0.068664 | -0.20599 | -0.013733 | -0.10529 | 122.905 | 122.8683 | 59.0103 | -122.9919 | 122.9095 | 122.7814 | 59.1293 | -123.0789
83.0156 | 123.2071 | -59.0012 | 63.8397 | -0.13748 | 0.0012539 | 0.066969 | 0.070517 | 0.13249 | 0.00035035 | -0.0028049 | 3.4941 | -0.0031446 | 0.059778 | 0.062525 | 0.0029266 | -0.0036424 | 63.913 | 64.1006 | 0.10986 | -59.1751 | 63.858 | -59.0469 | -59.079 | -58.9417 | 0.23804 | -59.2438 | 63.858 | 63.7344 | -59.0927 | -59.1888 | -0.045776 | -0.077819 | 0.01831 | 123.1018 | -0.17395 | -0.096131 | 0.073242 | -0.091552 | -0.18768 | 0.01831 | 0.05951 | -0.24261 | -0.054931 | -0.10529 | 122.8592 | 122.9141 | 59.111 | -122.9187 | 122.8592 | 122.7356 | 59.2392 | -123.0286
84.0156 | 123.1842 | -59.0378 | 63.8489 | -0.084076 | 0.0036039 | 0.065687 | 0.066885 | 0.13249 | -0.0013587 | -0.00088226 | 0.037995 | -0.0025038 | 0.062342 | 0.06103 | 0.0012176 | -0.0036424 | 63.8672 | 63.9999 | 0.018311 | -59.2117 | 63.8672 | -59.079 | -59.1064 | -58.9371 | 0.086975 | -59.2392 | 63.858 | 63.7207 | -59.1019 | -59.2026 | -0.041198 | -0.068664 | 0.01831 | 123.0377 | -0.17395 | -0.10529 | 0.01831 | -0.064087 | -0.16479 | 0.009155 | 0.10071 | -0.20142 | -0.036621 | -0.12817 | 122.905 | 122.905 | 59.0561 | -122.9553 | 122.8958 | 122.7585 | 59.1248 | -123.0515
85.0156 | 123.2025 | -59.0103 | 63.8397 | -3.3495 | 0.0044583 | 0.067182 | 0.066885 | 0.13142 | -0.0024269 | -0.00066866 | -0.061188 | -0.0018628 | 0.060633 | 0.061457 | 0.0022858 | -0.003215 | 63.8397 | 64.064 | 0.086975 | -59.1934 | 63.8672 | -59.0515 | -59.0973 | -58.9325 | 0.17395 | -59.2255 | 63.8535 | 63.7436 | -59.0973 | -59.198 | -0.041199 | -0.086975 | 0.027465 | 123.0743 | -0.18311 | -0.09613 | 0 | -0.086975 | -0.18768 | 0.013733 | 0.07782 | -0.21515 | -0.027466 | -0.096131 | 122.8775 | 122.85 | 59.0973 | -122.937 | 122.8638 | 122.7539 | 59.1843 | -123.0377
86.0156 | 123.1934 | -59.0332 | 63.8397 | -0.0077822 | -0.00088229 | 0.066114 | 0.067313 | 0.13185 | -0.00093145 | -0.0015231 | -0.015411 | -0.0044264 | 0.061487 | 0.061671 | 0.0014312 | -0.0017196 | 63.8397 | 63.9862 | -0.013733 | -59.2346 | 63.858 | -59.0881 | -59.1385 | -58.9462 | 0.082397 | -59.2621 | 63.8535 | 63.7299 | -59.111 | -59.23 | -0.054932 | -0.10529 | 0.01831 | 123.0194 | -0.20142 | -0.09613 | 0 | -0.07782 | -0.19684 | 0.013733 | 0.086975 | -0.22888 | -0.032043 | -0.10986 | 122.8912 | 122.8729 | 59.0195 | -122.9782 | 122.8867 | 122.7631 | 59.1156 | -123.0698
87.0156 | 123.1842 | -59.0149 | 63.8535 | -0.22141 | 0.00082671 | 0.06825 | 0.068594 | 0.13163 | -0.0024269 | -2.7856e-05 | -0.12222 | -0.0025038 | 0.061701 | 0.061671 | 0.0018584 | -0.0096238 | 63.9496 | 64.1098 | 0.086975 | -59.1705 | 63.8626 | -59.0607 | -59.0973 | -58.905 | 0.5722 | -59.3536 | 63.913 | 63.7573 | -59.111 | -59.2163 | -0.045776 | -0.082397 | 0.009155 | 123.1247 | -0.15564 | -0.073242 | 0.09613 | -0.09613 | -0.20142 | 0.059509 | 0.10986 | -0.33874 | -0.13733 | -0.096131 | 122.8775 | 122.9645 | 59.1019 | -122.9507 | 122.9279 | 122.7722 | 59.5871 | -123.0698
88.0156 | 123.1522 | -59.0469 | 63.8351 | 0.10666 | 0.0023221 | 0.06761 | 0.066672 | 0.13099 | -0.0017859 | -0.00088226 | 0.09903 | -0.0018628 | 0.06341 | 0.062312 | 0.0022858 | -0.0025742 | 63.8351 | 63.9771 | -0.045776 | -59.2621 | 63.8443 | -59.0836 | -59.1248 | -58.9783 | 0.036621 | -59.2896 | 63.8443 | 63.7482 | -59.1293 | -59.2117 | -0.036621 | -0.07782 | 0.009155 | 123.024 | -0.21515 | -0.13733 | 0 | -0.082397 | -0.16479 | 0.009155 | 0.068665 | -0.24262 | -0.07782 | -0.086975 | 122.8912 | 122.8821 | 59.0012 | -122.9599 | 122.8912 | 122.7951 | 59.0836 | -123.0469
89.0156 | 123.1888 | -59.0469 | 63.8443 | -0.0383 | 0.0033901 | 0.069319 | 0.068808 | 0.13057 | -0.00050425 | -0.0023777 | -0.00015237 | -0.00229 | 0.060846 | 0.063166 | 0.00079042 | -0.0030014 | 63.8763 | 64.0182 | 0.013733 | -59.2255 | 63.8443 | -59.0698 | -59.111 | -58.9325 | 0.10986 | -59.2621 | 63.8672 | 63.7207 | -59.111 | -59.1934 | -0.022888 | -0.064087 | 0 | 123.0652 | -0.17853 | -0.11444 | 0.032044 | -0.064087 | -0.14648 | 0.022888 | 0.11444 | -0.21515 | -0.068665 | -0.1236 | 122.8912 | 122.9233 | 59.0607 | -122.9553 | 122.9141 | 122.7676 | 59.1568 | -123.0377
90.0156 | 123.1567 | -59.0469 | 63.8123 | 0.037994 | 0.0025357 | 0.069746 | 0.069022 | 0.12993 | 0.0012047 | -0.0032321 | 0.076141 | -0.0033582 | 0.062982 | 0.059535 | 0.0016448 | -0.0034286 | 63.8443 | 63.9725 | -0.027466 | -59.2575 | 63.8626 | -59.0881 | -59.1339 | -58.9966 | 0.045776 | -59.2941 | 63.8489 | 63.7253 | -59.1156 | -59.2026 | -0.041199 | -0.086975 | 0.050354 | 123.0194 | -0.21057 | -0.1236 | 0.032043 | -0.068665 | -0.15564 | 0.036621 | 0.050354 | -0.24719 | -0.091552 | -0.086975 | 122.9095 | 122.8912 | 59.0195 | -122.9462 | 122.8958 | 122.7722 | 59.0927 | -123.0148
91.0156 | 123.1476 | -59.0286 | 63.8077 | -0.18326 | 0.0027493 | 0.067823 | 0.069876 | 0.13313 | -0.0019995 | -0.0021641 | -0.12222 | -0.0044264 | 0.060633 | 0.062098 | 0.0046356 | -0.0040696 | 63.9313 | 64.064 | 0.091553 | -59.198 | 63.8489 | -59.0561 | -59.1064 | -59.0607 | 0.32959 | -59.2575 | 63.8535 | 63.7344 | -59.1064 | -59.2072 | -0.027466 | -0.07782 | 0.041199 | 123.0927 | -0.16937 | -0.091553 | 0.1236 | -0.07782 | -0.17853 | 0.045777 | -0.032044 | -0.22888 | -0.050354 | -0.073242 | 122.8775 | 122.9599 | 59.1202 | -122.9141 | 122.8821 | 122.7631 | 59.3582 | -123.0148
92.0156 | 123.1934 | -59.0286 | 63.8123 | 0.068512 | 0.0023221 | 0.067182 | 0.067313 | 0.12843 | -0.0015723 | -0.0023777 | 0.068512 | -0.00464 | 0.060633 | 0.062312 | 0.00036322 | -0.0017196 | 63.8489 | 63.9771 | -0.022888 | -59.2255 | 63.858 | -59.0561 | -59.1248 | -58.9691 | 0.091553 | -59.2575 | 63.8535 | 63.7436 | -59.1385 | -59.2255 | -0.027466 | -0.096131 | 0.045776 | 123.0057 | -0.19684 | -0.10071 | 0.036621 | -0.10986 | -0.19684 | 0.041199 | 0.059509 | -0.22888 | -0.032043 | -0.068665 | 122.8867 | 122.8775 | 59.0057 | -122.937 | 122.8821 | 122.7722 | 59.1202 | -123.0377
93.0156 | 123.1979 | -59.0103 | 63.8214 | -0.19089 | 0.0016813 | 0.068037 | 0.069235 | 0.13163 | -0.0017859 | 0.00018594 | -0.053558 | -0.0050672 | 0.063196 | 0.060603 | 0.00057682 | -0.003215 | 63.945 | 64.1052 | 0.082397 | -59.166 | 63.8626 | -59.079 | -59.1019 | -58.9188 | 0.19684 | -59.2163 | 63.8489 | 63.7299 | -59.111 | -59.1705 | -0.068664 | -0.091553 | 0.041199 | 123.1155 | -0.15564 | -0.064087 | 0.1236 | -0.10071 | -0.16022 | 0.027466 | 0.091553 | -0.20599 | -0.045777 | -0.091553 | 122.8729 | 122.9553 | 59.0927 | -122.9233 | 122.8592 | 122.7402 | 59.2072 | -122.9919
94.0156 | 123.1567 | -59.0469 | 63.8351 | 0.015106 | 0.0021085 | 0.065473 | 0.066031 | 0.12864 | -0.00029045 | 0.0016811 | 0.13718 | -0.00464 | 0.061273 | 0.06338 | 0.0031402 | -0.0012924 | 63.7527 | 63.9908 | -0.022888 | -59.2529 | 63.8718 | -59.0881 | -59.1202 | -58.9828 | 0.054932 | -59.2804 | 63.8763 | 63.7344 | -59.1385 | -59.2438 | -0.041199 | -0.073242 | 0.036621 | 123.0377 | -0.20599 | -0.13275 | -0.082397 | -0.091553 | -0.19684 | 0.041199 | 0.064087 | -0.23346 | -0.036622 | -0.10071 | 122.9187 | 122.7997 | 59.024 | -122.9553 | 122.9233 | 122.7814 | 59.1019 | -123.0789
95.0156 | 123.2208 | -59.0286 | 63.8214 | -0.053558 | 0.0021085 | 0.066755 | 0.069022 | 0.13228 | -0.0030677 | -0.0034457 | 0.0074766 | -0.0035718 | 0.061701 | 0.063594 | 0.0016448 | -0.004924 | 63.8763 | 64.0137 | 0.009155 | -59.198 | 63.8626 | -59.0607 | -59.1339 | -58.9188 | 0.10986 | -59.2392 | 63.8626 | 63.7573 | -59.1064 | -59.2117 | -0.032044 | -0.10529 | 0.041199 | 123.0423 | -0.16937 | -0.064087 | 0.054932 | -0.07782 | -0.18311 | 0.041199 | 0.10986 | -0.21057 | -0.027466 | -0.064087 | 122.8912 | 122.905 | 59.0378 | -122.9553 | 122.8912 | 122.7859 | 59.1385 | -123.0331
96.0156 | 123.1155 | -59.0561 | 63.826 | 0.0074768 | 0.0029629 | 0.068464 | 0.067954 | 0.12864 | -0.00071785 | -0.0017369 | 0.076141 | -0.0035718 | 0.061914 | 0.063166 | 0.0022858 | -0.0023606 | 63.8168 | 63.9771 | -0.027466 | -59.2484 | 63.8489 | -59.0973 | -59.1202 | -58.9691 | 0.041199 | -59.285 | 63.8947 | 63.7527 | -59.1431 | -59.2392 | -0.041199 | -0.064087 | 0.022888 | 123.0331 | -0.19226 | -0.12817 | -0.009156 | -0.086975 | -0.18311 | 0.068664 | 0.086975 | -0.22888 | -0.045776 | -0.073242 | 122.905 | 122.8729 | 59.0286 | -122.9462 | 122.9507 | 122.8088 | 59.0973 | -123.0652
97.0156 | 123.2254 | -59.0103 | 63.8489 | -0.061188 | 0.0010403 | 0.06526 | 0.069449 | 0.12864 | -0.0013587 | -0.00088226 | -0.068817 | -0.0027174 | 0.061914 | 0.059962 | 0.0012176 | -0.0017196 | 63.9084 | 64.0869 | 0.073242 | -59.2026 | 63.858 | -59.0469 | -59.0973 | -58.8867 | 0.19684 | -59.1751 | 63.8718 | 63.7619 | -59.1064 | -59.1934 | -0.036621 | -0.086975 | 0.009155 | 123.0972 | -0.19226 | -0.10529 | 0.059509 | -0.09613 | -0.18311 | 0.022888 | 0.1236 | -0.16479 | 0.01831 | -0.086975 | 122.8683 | 122.9187 | 59.0836 | -122.9462 | 122.8821 | 122.7722 | 59.2072 | -123.0423
98.0156 | 123.175 | -59.0515 | 63.8443 | 0.015106 | 0.0010403 | 0.067182 | 0.068594 | 0.1327 | -0.00071785 | -0.00088226 | 0.030365 | -0.0054944 | 0.061273 | 0.060816 | 0.0020722 | -0.0036424 | 63.8535 | 63.9954 | -0.004578 | -59.2209 | 63.8626 | -59.0744 | -59.1339 | -58.9325 | 0.086975 | -59.2484 | 63.8855 | 63.7482 | -59.111 | -59.2026 | -0.022888 | -0.082397 | 0.018311 | 123.0469 | -0.16937 | -0.086975 | 0.009156 | -0.059509 | -0.15106 | 0.041199 | 0.11902 | -0.19684 | -0.045776 | -0.09613 | 122.9141 | 122.905 | 59.0469 | -122.9782 | 122.937 | 122.7997 | 59.1385 | -123.0469
99.0156 | 123.1888 | -59.0424 | 63.8214 | -0.21378 | 0.0014675 | 0.066755 | 0.068808 | 0.1295 | -0.0013587 | -0.00024146 | -0.11459 | -0.00464 | 0.058496 | 0.059321 | 0.0029266 | -0.0012924 | 63.9175 | 64.0823 | 0.07782 | -59.2072 | 63.8397 | -59.0607 | -59.111 | -59.0927 | 0.16479 | -59.1934 | 63.8672 | 63.707 | -59.111 | -59.23 | -0.018311 | -0.068665 | 0.018311 | 123.1247 | -0.16479 | -0.09613 | 0.096131 | -0.068665 | -0.18768 | 0.045776 | -0.050354 | -0.15106 | 0.036622 | -0.11444 | 122.8821 | 122.9599 | 59.1202 | -122.9324 | 122.9095 | 122.7493 | 59.2072 | -123.0515
100.0156 | 123.1613 | -59.024 | 63.8214 | 0.0074768 | 0.0027493 | 0.068037 | 0.065817 | 0.12907 | 0.00035035 | -0.0021641 | 0.068512 | -0.0044264 | 0.061914 | 0.06103 | 0.0018584 | -0.0036424 | 63.8214 | 63.9771 | -0.032043 | -59.2438 | 63.8351 | -59.0698 | -59.1248 | -58.9691 | 0.082397 | -59.2575 | 63.8809 | 63.7436 | -59.1202 | -59.2209 | -0.045776 | -0.10071 | 0.013733 | 123.0011 | -0.21973 | -0.11902 | 0 | -0.09613 | -0.19684 | 0.059509 | 0.054932 | -0.23346 | -0.036621 | -0.07782 | 122.8592 | 122.8455 | 58.992 | -122.9462 | 122.905 | 122.7676 | 59.1064 | -123.0423
101.0156 | 123.0652 | -59.0424 | 63.8901 | -0.24429 | 0.0057401 | 0.067182 | 0.068594 | 0.13057 | -0.00050425 | -0.0017369 | -0.19089 | -0.0031446 | 0.062128 | 0.063166 | 0.0016448 | -0.003215 | 63.8763 | 63.9954 | 0.018311 | -59.2392 | 63.8947 | -59.0881 | -59.111 | -58.9966 | 0.068665 | -59.3079 | 63.9221 | 63.8031 | -59.1248 | -59.2346 | -0.045777 | -0.068665 | 0.004577 | 123.0377 | -0.19684 | -0.12817 | -0.013733 | -0.082398 | -0.19226 | 0.032043 | 0.045776 | -0.2655 | -0.073242 | -0.086975 | 122.937 | 122.9187 | 59.0607 | -123.0011 | 122.9645 | 122.8455 | 59.111 | -123.1247
102.0156 | 123.1476 | -59.0469 | 63.826 | 0.16769 | 0.00082671 | 0.068037 | 0.066031 | 0.13035 | -0.00071785 | -0.0021641 | 0.15244 | -0.0025038 | 0.059351 | 0.062953 | 0.0012176 | -0.003215 | 63.8306 | 63.9862 | -0.032043 | -59.2575 | 63.858 | -59.0744 | -59.1293 | -58.9874 | 0.045776 | -59.2896 | 63.8306 | 63.7482 | -59.1248 | -59.2209 | -0.027466 | -0.082397 | 0.032043 | 123.0331 | -0.21057 | -0.12817 | 0.004577 | -0.07782 | -0.17395 | 0.004577 | 0.059509 | -0.24262 | -0.068665 | -0.07782 | 122.905 | 122.8775 | 59.0149 | -122.9553 | 122.8775 | 122.7951 | 59.0927 | -123.0469
103.0156 | 123.1842 | -59.0286 | 63.8351 | -0.084076 | 0.00082671 | 0.066114 | 0.067526 | 0.13057 | -0.0013587 | -0.0010959 | 0.076141 | -0.002931 | 0.061273 | 0.061671 | 0.0014312 | -0.002147 | 63.8672 | 64.0366 | 0.027466 | -59.2209 | 63.8489 | -59.0744 | -59.111 | -58.9371 | 0.14191 | -59.2117 | 63.858 | 63.7573 | -59.1064 | -59.2072 | -0.045777 | -0.082398 | 0.013733 | 123.0652 | -0.19226 | -0.10986 | 0.032043 | -0.07782 | -0.17853 | 0.022888 | 0.091552 | -0.18311 | -0.004578 | -0.07782 | 122.8775 | 122.8958 | 59.0561 | -122.9462 | 122.8867 | 122.7859 | 59.1705 | -123.0423
104.0156 | 123.2117 | -58.9783 | 63.8397 | -0.0077822 | 0.0010403 | 0.063551 | 0.067313 | 0.13078 | -0.0026405 | -0.0013095 | 0.015106 | -0.0033582 | 0.060419 | 0.061885 | 0.0024994 | -0.003215 | 63.8763 | 64.0182 | 0.022888 | -59.23 | 63.8809 | -59.0652 | -59.1248 | -58.9508 | 0.10071 | -59.1934 | 63.8718 | 63.7619 | -59.1019 | -59.2117 | -0.086976 | -0.14648 | 0.041198 | 122.9965 | -0.25177 | -0.10529 | 0.036621 | -0.1236 | -0.23346 | 0.032043 | 0.027465 | -0.21515 | 0.018311 | -0.07782 | 122.8592 | 122.8546 | 59.0012 | -122.9645 | 122.85 | 122.7402 | 59.079 | -123.0515
105.0156 | 123.1659 | -59.0012 | 63.8535 | -0.4808 | 0.0027493 | 0.065901 | 0.068167 | 0.13014 | -0.0017859 | -0.0023777 | -0.099335 | -0.0042126 | 0.060633 | 0.062953 | 0.0020722 | -0.0051376 | 63.9084 | 64.064 | 0.086975 | -59.1843 | 63.8626 | -59.0652 | -59.111 | -58.9371 | 0.17395 | -59.23 | 63.8763 | 63.7665 | -59.0836 | -59.1934 | -0.064087 | -0.10986 | 0.009155 | 123.0652 | -0.18311 | -0.073242 | 0.054931 | -0.082397 | -0.19226 | 0.022888 | 0.064087 | -0.22888 | -0.036622 | -0.086976 | 122.8638 | 122.9095 | 59.0881 | -122.9645 | 122.8775 | 122.7676 | 59.1751 | -123.0469
106.0156 | 123.1201 | -59.0607 | 63.8626 | -0.023041 | 0.010013 | 0.065473 | 0.070944 | 0.12907 | 0.0071863 | -0.00088226 | -0.076446 | 0.00027344 | 0.063196 | 0.063807 | 0.0037812 | -0.003856 | 63.8443 | 63.945 | -0.059509 | -59.2621 | 63.9038 | -59.1064 | -59.1476 | -59.0195 | -0.004578 | -59.3674 | 63.8809 | 63.7573 | -59.1248 | -59.2484 | -0.045776 | -0.086975 | 0.041199 | 123.0057 | -0.20142 | -0.11444 | -0.018311 | -0.064087 | -0.18768 | 0.01831 | 0.041199 | -0.3067 | -0.11902 | -0.10529 | 122.9645 | 122.905 | 59.0012 | -123.0103 | 122.9416 | 122.818 | 59.0561 | -123.111
107.0156 | 123.1613 | -59.0332 | 63.8351 | -0.56473 | 0.00082671 | 0.066328 | 0.069663 | 0.13377 | -0.0032813 | 0.00018594 | -0.068817 | -0.0020764 | 0.060419 | 0.063594 | 0.0012176 | -0.00043797 | 63.8947 | 64.0457 | 0.086975 | -59.1934 | 63.8351 | -59.0698 | -59.0927 | -58.9508 | 0.1831 | -59.2163 | 63.8443 | 63.7756 | -59.1019 | -59.2026 | -0.036621 | -0.059509 | 0 | 123.0789 | -0.16022 | -0.10071 | 0.059509 | -0.068665 | -0.16937 | 0.009155 | 0.082397 | -0.18311 | -0.013733 | -0.059509 | 122.8683 | 122.9279 | 59.1202 | -122.9279 | 122.8775 | 122.8088 | 59.2163 | -123.0377
108.0156 | 123.2071 | -59.0286 | 63.8214 | -0.12222 | -0.0015231 | 0.065687 | 0.065176 | 0.12993 | -0.0034949 | -0.0017369 | 0.037995 | -0.00464 | 0.065759 | 0.061671 | 0.00057682 | -0.0017196 | 63.858 | 64.0137 | 0.009155 | -59.2163 | 63.8718 | -59.0424 | -59.1064 | -58.9371 | 0.10986 | -59.2209 | 63.8489 | 63.7527 | -59.1156 | -59.23 | -0.013733 | -0.07782 | 0.050354 | 123.0423 | -0.18768 | -0.10986 | 0.036621 | -0.086976 | -0.20142 | 0.027466 | 0.091552 | -0.19226 | 0.009156 | -0.068664 | 122.9004 | 122.8867 | 59.0378 | -122.9279 | 122.8775 | 122.7814 | 59.1385 | -123.0515
109.0156 | 123.1522 | -59.024 | 63.8306 | -0.43503 | 0.0050991 | 0.065687 | 0.070731 | 0.13057 | -0.0019995 | -0.00045506 | -0.099335 | -0.0035718 | 0.062769 | 0.061671 | 0.001004 | -0.0034286 | 63.8855 | 64.0778 | 0.09613 | -59.198 | 63.8672 | -59.0744 | -59.1064 | -58.9325 | 0.16022 | -59.2117 | 63.858 | 63.7665 | -59.1064 | -59.2255 | -0.050354 | -0.082397 | 0.036621 | 123.1018 | -0.17395 | -0.091553 | 0.054932 | -0.082397 | -0.20142 | 0.027466 | 0.091553 | -0.18768 | 0.013733 | -0.064087 | 122.8912 | 122.9095 | 59.1202 | -122.937 | 122.8821 | 122.7905 | 59.1843 | -123.056
110.0156 | 123.143 | -59.0378 | 63.8351 | -0.068817 | 0.0018949 | 0.069105 | 0.064749 | 0.13035 | -0.0032813 | -0.0030185 | 0.045624 | -0.0035718 | 0.062555 | 0.062739 | 0.0018584 | -0.0019334 | 63.8626 | 64.0045 | 0.004578 | -59.2255 | 63.8397 | -59.0561 | -59.1019 | -58.9462 | 0.10529 | -59.2484 | 63.8351 | 63.7299 | -59.1019 | -59.2209 | -0.01831 | -0.064087 | 0.004578 | 123.0423 | -0.18768 | -0.1236 | 0.027466 | -0.064087 | -0.1831 | 0 | 0.091553 | -0.21057 | -0.027466 | -0.10529 | 122.8775 | 122.9004 | 59.0424 | -122.937 | 122.8729 | 122.7676 | 59.1431 | -123.056
111.0156 | 123.0789 | -59.0607 | 63.8306 | -0.068817 | 0.0097989 | 0.064405 | 0.070303 | 0.13163 | 0.0056909 | 0.00061314 | -0.023041 | -0.00036736 | 0.066828 | 0.064021 | 0.0057038 | -0.0062058 | 63.858 | 63.945 | -0.032043 | -59.2438 | 63.8901 | -59.0881 | -59.1156 | -59.0195 | 0.009155 | -59.3262 | 63.9038 | 63.7802 | -59.1248 | -59.2484 | -0.027466 | -0.054932 | 0.05951 | 123.0057 | -0.18311 | -0.12817 | 0.027466 | -0.064087 | -0.18768 | 0.073243 | 0.041199 | -0.2655 | -0.07782 | -0.050354 | 122.9507 | 122.9187 | 59.0286 | -122.9462 | 122.9645 | 122.8409 | 59.0698 | -123.0789
112.0156 | 123.1842 | -59.0332 | 63.826 | -0.091705 | 0.0023221 | 0.066114 | 0.06774 | 0.13249 | -0.0047767 | -0.0032321 | -0.17563 | -0.0037854 | 0.063623 | 0.064448 | -0.00027778 | -0.00065157 | 63.8672 | 64.0503 | 0.041199 | -59.1843 | 63.8397 | -59.0561 | -59.111 | -58.8913 | 0.20142 | -59.1751 | 63.858 | 63.7665 | -59.0927 | -59.2072 | -0.022888 | -0.07782 | 0.013733 | 123.0835 | -0.15106 | -0.073242 | 0.041198 | -0.059509 | -0.17395 | 0.032043 | 0.14191 | -0.14191 | 0.032043 | -0.05951 | 122.8729 | 122.9004 | 59.0744 | -122.937 | 122.8912 | 122.7997 | 59.2346 | -123.0331
113.0156 | 123.1293 | -59.0469 | 63.8855 | -0.22903 | 0.0050991 | 0.068678 | 0.066672 | 0.12993 | -0.0019995 | -0.00066866 | -0.15274 | -0.0042126 | 0.061914 | 0.062098 | 0.0012176 | -0.0027878 | 63.8809 | 64.0457 | 0.064087 | -59.2072 | 63.858 | -59.0652 | -59.111 | -58.9691 | 0.14648 | -59.2438 | 63.8763 | 63.7802 | -59.1339 | -59.2438 | -0.018311 | -0.064087 | -0.027466 | 123.0927 | -0.16022 | -0.09613 | -0.004578 | -0.086975 | -0.19684 | -0.009155 | 0.07782 | -0.19684 | 0 | -0.10529 | 122.905 | 122.9279 | 59.111 | -122.9965 | 122.9233 | 122.8271 | 59.1934 | -123.1293
114.0156 | 123.2025 | -59.0012 | 63.8535 | -0.076447 | 0.00018591 | 0.065046 | 0.069449 | 0.13377 | -0.0041357 | -0.0047275 | -0.099335 | -0.0050672 | 0.06106 | 0.062525 | -0.00049138 | -0.0042832 | 63.8809 | 64.0732 | 0.064087 | -59.2163 | 63.8535 | -59.0881 | -59.1156 | -58.9142 | 0.17395 | -59.1843 | 63.8443 | 63.7344 | -59.0836 | -59.2163 | -0.086975 | -0.11444 | 0 | 123.0743 | -0.21515 | -0.10071 | 0.027465 | -0.082397 | -0.21515 | -0.009156 | 0.086975 | -0.18311 | 0.032044 | -0.11902 | 122.8546 | 122.8821 | 59.0652 | -122.9691 | 122.8455 | 122.7356 | 59.1751 | -123.0698
115.0156 | 123.1522 | -59.0469 | 63.858 | -0.17563 | 0.0021085 | 0.066114 | 0.070517 | 0.13121 | 0.0012047 | -0.0019505 | -0.15274 | -0.0025038 | 0.061701 | 0.064448 | 0.0014312 | -0.0017196 | 63.8718 | 64.064 | 0.073242 | -59.1888 | 63.8855 | -59.0515 | -59.1019 | -58.9645 | 0.16479 | -59.2392 | 63.8947 | 63.7756 | -59.0927 | -59.2209 | -0.004578 | -0.054932 | 0.027466 | 123.111 | -0.14191 | -0.086975 | 0.013733 | -0.045776 | -0.17395 | 0.036621 | 0.082397 | -0.19226 | -0.018311 | -0.082397 | 122.9324 | 122.9187 | 59.1202 | -122.9599 | 122.9416 | 122.8226 | 59.2117 | -123.0789
116.0156 | 123.0011 | -59.0744 | 63.8351 | 0.068512 | 0.0097989 | 0.06526 | 0.07244 | 0.13078 | 0.0059045 | 0.0014675 | 0.045624 | -0.0018628 | 0.064691 | 0.063594 | 0.002713 | -0.003856 | 63.7711 | 63.8351 | -0.13733 | -59.2987 | 63.8901 | -59.1293 | -59.1522 | -59.0744 | -0.07782 | -59.5367 | 63.8535 | 63.6887 | -59.1797 | -59.2987 | -0.054931 | -0.07782 | 0.054932 | 122.9095 | -0.2243 | -0.14648 | -0.064087 | -0.10529 | -0.2243 | 0.018311 | 0 | -0.46234 | -0.23804 | -0.14648 | 122.9645 | 122.8455 | 58.9371 | -122.9874 | 122.9279 | 122.7631 | 58.9966 | -123.1338
117.0156 | 123.1796 | -59.024 | 63.8397 | -0.14511 | 0.0033901 | 0.065473 | 0.06539 | 0.13014 | -0.0039221 | -0.0021641 | -0.045929 | -0.0084852 | 0.058924 | 0.060816 | 0.0042084 | -0.0034286 | 63.9175 | 64.0915 | 0.10529 | -59.166 | 63.8489 | -59.0561 | -59.1156 | -59.0973 | 0.35706 | -59.2712 | 63.8535 | 63.7482 | -59.1064 | -59.2117 | -0.032043 | -0.091553 | 0.009155 | 123.1155 | -0.14191 | -0.050354 | 0.07782 | -0.082397 | -0.18768 | 0.013733 | -0.073242 | -0.24719 | -0.059509 | -0.091553 | 122.8729 | 122.9416 | 59.1293 | -122.9553 | 122.8775 | 122.7722 | 59.3811 | -123.0515
118.0156 | 123.1476 | -59.024 | 63.826 | -0.17563 | -0.00066869 | 0.069532 | 0.067313 | 0.13099 | -0.0041357 | -0.0030185 | -0.061188 | -0.002931 | 0.059778 | 0.061244 | -6.4178e-05 | -0.0091966 | 63.8992 | 64.0961 | 0.10529 | -59.1751 | 63.8718 | -59.0469 | -59.1064 | -58.7952 | 0.53558 | -59.4406 | 63.8947 | 63.7665 | -59.1293 | -59.2117 | -0.022888 | -0.082397 | 0.045776 | 123.1201 | -0.15106 | -0.068665 | 0.073242 | -0.10529 | -0.18768 | 0.068664 | 0.22888 | -0.41656 | -0.22888 | -0.05951 | 122.8958 | 122.9233 | 59.1293 | -122.9324 | 122.9187 | 122.7905 | 59.5596 | -123.0377
119.0156 | 123.0972 | -59.024 | 63.8855 | -0.22903 | 0.0042447 | 0.067396 | 0.067526 | 0.13099 | 0.00077755 | 0.00061314 | -0.16037 | -0.0027174 | 0.062342 | 0.062098 | 0.0031402 | -0.0027878 | 63.8626 | 64.0228 | 0.050354 | -59.2026 | 63.8626 | -59.0652 | -59.1248 | -58.9874 | 0.13733 | -59.2667 | 63.8901 | 63.7939 | -59.1248 | -59.2209 | -0.041199 | -0.10071 | -0.022888 | 123.0469 | -0.17853 | -0.07782 | -0.022888 | -0.10071 | -0.19684 | 0.004578 | 0.036621 | -0.24262 | -0.045777 | -0.091553 | 122.8867 | 122.8867 | 59.0744 | -123.0103 | 122.9141 | 122.818 | 59.1614 | -123.1064
120.0156 | 123.2391 | -58.9874 | 63.858 | -0.061188 | 0.0016813 | 0.066541 | 0.065604 | 0.13163 | -0.0024269 | -0.0015231 | -0.03067 | -0.0037854 | 0.059992 | 0.061244 | 0.0014312 | -0.003215 | 63.8718 | 64.0503 | 0.064087 | -59.1843 | 63.8672 | -59.0607 | -59.1248 | -58.873 | 0.1831 | -59.1934 | 63.8397 | 63.7619 | -59.1202 | -59.1843 | -0.073242 | -0.13733 | 0.009155 | 123.0377 | -0.19684 | -0.059509 | 0.013733 | -0.13275 | -0.19684 | -0.01831 | 0.11444 | -0.20599 | -0.009155 | -0.09613 | 122.8546 | 122.8592 | 59.0515 | -122.9828 | 122.8271 | 122.7493 | 59.1705 | -123.0423
121.0156 | 123.0789 | -59.0561 | 63.8672 | -0.03067 | 0.0093717 | 0.063337 | 0.072867 | 0.12993 | 0.0052637 | 0.00018594 | -0.091705 | -0.0010084 | 0.064264 | 0.06338 | 0.0018584 | -0.0057786 | 63.8855 | 63.945 | -0.032043 | -59.2712 | 63.8901 | -59.1248 | -59.1522 | -59.0012 | 0.032043 | -59.3353 | 63.8947 | 63.7711 | -59.1476 | -59.2484 | -0.068665 | -0.096131 | 0.022889 | 123.0011 | -0.21515 | -0.11902 | 0.018311 | -0.091553 | -0.19226 | 0.027466 | 0.054931 | -0.27924 | -0.086975 | -0.09613 | 122.9462 | 122.9416 | 59.024 | -123.0194 | 122.9507 | 122.8271 | 59.0881 | -123.1155
122.0156 | 123.1842 | -59.0378 | 63.8306 | 0.015106 | 0.0012539 | 0.067396 | 0.066031 | 0.13163 | -0.0039221 | -0.0030185 | 0.060883 | -0.00464 | 0.061701 | 0.062098 | -0.00027778 | -0.001506 | 63.8123 | 63.9862 | -0.022888 | -59.23 | 63.8443 | -59.079 | -59.1431 | -58.96 | 0.091553 | -59.2484 | 63.8535 | 63.7802 | -59.1293 | -59.2209 | -0.041198 | -0.10528 | 0.013733 | 123.024 | -0.19226 | -0.086976 | -0.01831 | -0.091552 | -0.1831 | 0.022889 | 0.07782 | -0.21057 | -0.027466 | -0.050354 | 122.8821 | 122.85 | 59.0149 | -122.9736 | 122.8912 | 122.818 | 59.1293 | -123.0515
123.0156 | 123.1934 | -59.0012 | 63.8489 | -0.11459 | 0.0048855 | 0.066541 | 0.067954 | 0.12928 | -0.0034949 | -0.0015231 | 0.88486 | -0.0035718 | 0.063623 | 0.061671 | 0.0031402 | -0.0034286 | 63.9221 | 64.2975 | 0.29755 | -58.9828 | 63.9496 | -59.024 | -59.0973 | -58.9554 | 0.21515 | -59.198 | 63.8489 | 63.7436 | -59.1019 | -59.2117 | -0.022888 | -0.09613 | 0.10071 | 123.2986 | 0.018311 | 0.11444 | 0.073242 | -0.10071 | -0.21057 | 0 | 0.045777 | -0.19684 | 0.013733 | -0.10529 | 122.9507 | 122.9233 | 59.2987 | -122.9462 | 122.85 | 122.7448 | 59.2163 | -123.0606
124.0156 | 123.1842 | -59.0103 | 63.826 | -0.053558 | 0.0018949 | 0.066755 | 0.067313 | 0.1327 | -0.0037085 | -0.0032321 | 0.045624 | -0.0052808 | 0.062342 | 0.06338 | 0.0031402 | -0.0047104 | 63.8763 | 63.9908 | 0.018311 | -59.1934 | 63.8443 | -59.079 | -59.111 | -58.9554 | 0.13733 | -59.1934 | 63.8626 | 63.7802 | -59.0927 | -59.23 | -0.068664 | -0.10071 | 0.01831 | 123.0011 | -0.18311 | -0.082397 | 0.050354 | -0.082397 | -0.21973 | 0.036621 | 0.054932 | -0.18311 | 0.036622 | -0.045777 | 122.8546 | 122.8867 | 59.0286 | -122.937 | 122.8729 | 122.7905 | 59.1476 | -123.056
125.0156 | 123.0972 | -59.0195 | 63.8809 | -0.25955 | 0.0057401 | 0.065901 | 0.068808 | 0.13356 | -0.0015723 | -0.0021641 | -0.20615 | -0.0025038 | 0.061701 | 0.062739 | 0.0012176 | -0.003856 | 63.8809 | 64.0182 | 0.045776 | -59.2117 | 63.8809 | -59.0652 | -59.1293 | -59.0057 | 0.10071 | -59.2896 | 63.9038 | 63.7756 | -59.1522 | -59.198 | -0.045777 | -0.10986 | 0 | 123.0377 | -0.19226 | -0.082398 | 0 | -0.13275 | -0.17853 | 0.022889 | 0.013733 | -0.27008 | -0.091553 | -0.10529 | 122.9004 | 122.9004 | 59.0652 | -123.0103 | 122.9233 | 122.7951 | 59.1202 | -123.0789
126.0156 | 123.0789 | -59.0332 | 63.8489 | -0.16037 | 0.0059537 | 0.065473 | 0.066031 | 0.13228 | 0.0031273 | -0.0019505 | -0.20615 | -0.0016492 | 0.062342 | 0.061244 | 0.0039948 | -0.0019334 | 63.8443 | 63.9496 | -0.036621 | -59.2209 | 63.913 | -59.0927 | -59.1339 | -58.992 | 0.082397 | -59.2987 | 63.8855 | 63.7985 | -59.1248 | -59.2438 | -0.059509 | -0.10071 | 0.064087 | 122.9828 | -0.18768 | -0.086975 | -0.004578 | -0.091553 | -0.21057 | 0.036621 | 0.041199 | -0.2655 | -0.054932 | -0.050354 | 122.9462 | 122.8775 | 58.9966 | -122.9828 | 122.9187 | 122.8317 | 59.1156 | -123.0927
127.0156 | 123.1155 | -59.0424 | 63.8626 | -0.19852 | 0.0027493 | 0.068464 | 0.068808 | 0.13099 | -0.00093145 | 0.00061314 | -0.15274 | -0.0033582 | 0.061914 | 0.064021 | 0.001004 | -0.0023606 | 63.8672 | 64.0366 | 0.054932 | -59.1934 | 63.8626 | -59.0698 | -59.111 | -58.9874 | 0.15106 | -59.2438 | 63.8947 | 63.8077 | -59.1339 | -59.23 | -0.027466 | -0.068665 | 0 | 123.0789 | -0.15106 | -0.082397 | 0.004577 | -0.091553 | -0.18768 | 0.032043 | 0.054931 | -0.20142 | -0.013732 | -0.054932 | 122.905 | 122.9095 | 59.0973 | -122.9736 | 122.937 | 122.85 | 59.1934 | -123.0927
128.0156 | 123.1796 | -58.9874 | 63.8306 | -0.061188 | 0.0027493 | 0.067823 | 0.066672 | 0.12971 | -0.0047767 | -0.0010959 | 0.053253 | -0.0044264 | 0.060846 | 0.06338 | 0.0016448 | -0.001506 | 63.8718 | 64.0228 | 0.050354 | -59.2026 | 63.8535 | -59.0515 | -59.1293 | -58.9188 | 0.18768 | -59.2072 | 63.8489 | 63.7527 | -59.111 | -59.1797 | -0.064087 | -0.14191 | 0.022889 | 123.0103 | -0.21515 | -0.073243 | 0.041199 | -0.1236 | -0.19226 | 0.018311 | 0.068665 | -0.21973 | -0.027466 | -0.077819 | 122.8409 | 122.8592 | 59.0378 | -122.9599 | 122.8363 | 122.7402 | 59.1751 | -123.0103
129.0156 | 123.1888 | -59.0012 | 63.8397 | -0.13748 | 0.0042447 | 0.067396 | 0.070303 | 0.13377 | -0.0041357 | -0.0032321 | -0.11459 | -0.0052808 | 0.062555 | 0.064021 | 0.0018584 | -0.0019334 | 63.8809 | 64.0274 | 0.086975 | -59.1888 | 63.8763 | -59.0515 | -59.0973 | -58.9554 | 0.16937 | -59.2255 | 63.8763 | 63.7619 | -59.1202 | -59.1843 | -0.050354 | -0.09613 | 0.036621 | 123.0286 | -0.18768 | -0.091553 | 0.041198 | -0.11902 | -0.18311 | 0.036621 | 0.045777 | -0.2243 | -0.041199 | -0.07782 | 122.8775 | 122.8821 | 59.0881 | -122.937 | 122.8775 | 122.7631 | 59.1705 | -123.024
130.0156 | 123.1705 | -59.0378 | 63.826 | 1.5105 | 0.0038175 | 0.066755 | 0.06774 | 0.12864 | -0.0039221 | -0.0025913 | 0.0914 | -0.0020764 | 0.060419 | 0.062739 | 0.0020722 | -0.002147 | 63.7939 | 63.9496 | -0.041199 | -59.2392 | 63.8306 | -59.0881 | -59.1568 | -59.0012 | 0.050354 | -59.285 | 63.8306 | 63.7436 | -59.1293 | -59.2026 | -0.050354 | -0.11902 | 0.004577 | 122.9874 | -0.20142 | -0.082398 | -0.032044 | -0.091552 | -0.16479 | 0.004577 | 0.036621 | -0.24719 | -0.082397 | -0.082398 | 122.8683 | 122.8317 | 58.9966 | -122.9828 | 122.8683 | 122.7814 | 59.0881 | -123.0286
131.0156 | 123.1842 | -59.0195 | 63.8489 | -0.045929 | 0.0036039 | 0.068891 | 0.071585 | 0.13035 | -0.0015723 | -0.0019505 | -0.16037 | -0.0044264 | 0.062342 | 0.061244 | 0.00036322 | -0.0034286 | 63.858 | 64.0869 | 0.059509 | -59.198 | 63.8489 | -59.0652 | -59.1019 | -58.9508 | 0.17853 | -59.198 | 63.8535 | 63.7161 | -59.1064 | -59.2072 | -0.045777 | -0.082398 | 0 | 123.1064 | -0.17853 | -0.09613 | 0.009155 | -0.086975 | -0.18768 | 0.004578 | 0.068664 | -0.17853 | 0.009155 | -0.13275 | 122.8683 | 122.8775 | 59.079 | -122.9507 | 122.8729 | 122.7356 | 59.198 | -123.056
132.0156 | 123.1979 | -59.0149 | 63.8351 | -0.00015269 | 0.0018949 | 0.068678 | 0.067526 | 0.13185 | -0.00050425 | -0.0032321 | 0.037995 | -0.0035718 | 0.061273 | 0.061671 | 0.0020722 | -0.0030014 | 63.8763 | 64.0182 | 0.045776 | -59.198 | 63.8626 | -59.0744 | -59.1248 | -58.9142 | 0.16937 | -59.1888 | 63.8626 | 63.7573 | -59.1248 | -59.2026 | -0.059509 | -0.10986 | 0.027466 | 123.0331 | -0.1831 | -0.073242 | 0.041199 | -0.10986 | -0.18768 | 0.027466 | 0.10071 | -0.17395 | 0.013733 | -0.07782 | 122.8775 | 122.8912 | 59.0607 | -122.9599 | 122.8775 | 122.7722 | 59.1843 | -123.0377
133.0156 | 123.1888 | -59.0195 | 63.8306 | -0.17563 | 0.0040311 | 0.066541 | 0.069235 | 0.13185 | 0.00099115 | -0.0019505 | -0.12985 | -0.0037854 | 0.060419 | 0.062098 | 0.001004 | -0.0030014 | 63.9038 | 64.0366 | 0.064087 | -59.198 | 63.8626 | -59.0424 | -59.1019 | -58.96 | 0.17395 | -59.2255 | 63.8901 | 63.7665 | -59.0973 | -59.2117 | -0.022888 | -0.082398 | 0.032044 | 123.056 | -0.17853 | -0.09613 | 0.073243 | -0.07782 | -0.19226 | 0.05951 | 0.059509 | -0.20599 | -0.013733 | -0.064087 | 122.8821 | 122.9233 | 59.0836 | -122.9324 | 122.9095 | 122.7859 | 59.1934 | -123.0423
134.0156 | 123.1888 | -59.024 | 63.8397 | -0.061188 | 0.00061311 | 0.066755 | 0.065817 | 0.13228 | -0.0017859 | -0.0023777 | 0.076141 | -0.0020764 | 0.061701 | 0.061244 | 0.00079042 | -0.0040696 | 63.8718 | 64.0045 | 0.022888 | -59.2209 | 63.8763 | -59.0607 | -59.1339 | -58.9508 | 0.10529 | -59.2117 | 63.8672 | 63.7344 | -59.1064 | -59.2209 | -0.036621 | -0.10986 | 0.036621 | 123.0286 | -0.19684 | -0.086975 | 0.032043 | -0.082397 | -0.19684 | 0.027465 | 0.073242 | -0.18768 | 0.009155 | -0.10529 | 122.9004 | 122.8958 | 59.0469 | -122.9736 | 122.8912 | 122.7585 | 59.1293 | -123.0606
135.0156 | 123.1842 | -59.0057 | 63.826 | -0.93094 | -2.7692e-05 | 0.065473 | 0.068594 | 0.13206 | -0.0013587 | -0.0013095 | -0.061188 | -0.0033582 | 0.064691 | 0.063166 | 0.0018584 | -0.0034286 | 63.858 | 64.0961 | 0.10071 | -59.198 | 63.8535 | -59.0515 | -59.1064 | -58.9325 | 0.17853 | -59.2117 | 63.8535 | 63.739 | -59.1064 | -59.198 | -0.045777 | -0.10071 | 0.027466 | 123.1018 | -0.19226 | -0.091553 | 0.032043 | -0.10071 | -0.19226 | 0.027466 | 0.073242 | -0.20599 | -0.013733 | -0.086975 | 122.8592 | 122.8638 | 59.1064 | -122.9324 | 122.8592 | 122.7448 | 59.1843 | -123.024
136.0156 | 123.1705 | -59.0424 | 63.8168 | -0.015411 | 0.00082671 | 0.066755 | 0.064963 | 0.13185 | -0.0024269 | -0.0030185 | -0.045929 | -0.0020764 | 0.063623 | 0.062739 | 0.0018584 | -0.0053512 | 63.8168 | 63.9771 | -0.032043 | -59.23 | 63.8763 | -59.079 | -59.0927 | -59.0012 | 0.022888 | -59.3033 | 63.8443 | 63.739 | -59.1293 | -59.2438 | -0.036621 | -0.050354 | 0.05951 | 123.0194 | -0.18768 | -0.13733 | 0 | -0.086975 | -0.20142 | 0.027466 | 0.041198 | -0.26093 | -0.05951 | -0.077819 | 122.9187 | 122.8592 | 59.0103 | -122.9095 | 122.8867 | 122.7814 | 59.0652 | -123.0606
137.0156 | 123.1979 | -59.0195 | 63.8489 | -0.091705 | 0.0038175 | 0.066969 | 0.06774 | 0.13142 | -0.0028541 | -0.0028049 | 0.0074766 | -0.0031446 | 0.060846 | 0.062312 | 0.0024994 | -0.002147 | 63.8901 | 64.0411 | 0.036621 | -59.2163 | 63.8489 | -59.0607 | -59.1019 | -58.9142 | 0.16479 | -59.1934 | 63.8535 | 63.7665 | -59.1064 | -59.1888 | -0.041199 | -0.082398 | 0 | 123.0606 | -0.19684 | -0.11444 | 0.041199 | -0.086975 | -0.16937 | 0.004578 | 0.10528 | -0.17395 | -0.004577 | -0.082398 | 122.8683 | 122.9095 | 59.0561 | -122.9507 | 122.8729 | 122.7859 | 59.1843 | -123.0377
138.0156 | 123.175 | -59.0378 | 63.826 | 0.045624 | 0.0023221 | 0.06761 | 0.066031 | 0.13163 | -0.0026405 | -0.0019505 | 0.060883 | -0.0020764 | 0.060633 | 0.062953 | 0.0016448 | -0.0044968 | 63.8214 | 63.9725 | -0.004578 | -59.2163 | 63.8626 | -59.0927 | -59.111 | -58.9691 | 0.073242 | -59.2529 | 63.858 | 63.7344 | -59.1248 | -59.23 | -0.054931 | -0.073242 | 0.036621 | 123.0103 | -0.17853 | -0.10529 | -0.004578 | -0.086975 | -0.19226 | 0.032043 | 0.068665 | -0.21515 | -0.022888 | -0.091553 | 122.9004 | 122.8592 | 59.0332 | -122.937 | 122.8958 | 122.7722 | 59.111 | -123.056
139.0156 | 123.1522 | -59.0286 | 63.8306 | -0.25955 | 0.0027493 | 0.066541 | 0.068808 | 0.13313 | 0.00099115 | -0.0010959 | -0.14511 | -0.00464 | 0.061487 | 0.061885 | 0.0012176 | -0.0034286 | 63.8901 | 64.0594 | 0.073242 | -59.1843 | 63.858 | -59.0515 | -59.1064 | -58.9371 | 0.16479 | -59.23 | 63.8626 | 63.7482 | -59.1064 | -59.1934 | -0.022889 | -0.07782 | 0.027466 | 123.0881 | -0.15564 | -0.07782 | 0.05951 | -0.07782 | -0.1648 | 0.032044 | 0.091552 | -0.20142 | -0.036622 | -0.082397 | 122.8867 | 122.9187 | 59.1019 | -122.937 | 122.8912 | 122.7768 | 59.1934 | -123.024
140.0156 | 123.2025 | -59.0424 | 63.8626 | -0.053558 | 0.0021085 | 0.06825 | 0.070303 | 0.13249 | -0.0011451 | -0.0034457 | -0.015411 | -0.0054944 | 0.060846 | 0.063166 | -6.4178e-05 | -0.0023606 | 63.8672 | 64.0182 | 0.027466 | -59.23 | 63.8489 | -59.0652 | -59.1202 | -58.9142 | 0.10529 | -59.2346 | 63.8535 | 63.7527 | -59.0881 | -59.2117 | -0.022889 | -0.07782 | -0.013733 | 123.0606 | -0.18768 | -0.10986 | 0.004577 | -0.045777 | -0.16937 | -0.009155 | 0.12817 | -0.19226 | -0.022888 | -0.10986 | 122.8912 | 122.9095 | 59.0698 | -122.9828 | 122.8958 | 122.7951 | 59.1476 | -123.0743
141.0156 | 123.1705 | -59.0012 | 63.8489 | -0.37399 | -0.0030185 | 0.06761 | 0.06539 | 0.13185 | -0.00050425 | -0.0025913 | -0.099335 | -0.00464 | 0.061487 | 0.06103 | 0.0016448 | -0.003856 | 63.9084 | 64.0228 | 0.07782 | -59.1751 | 63.8489 | -59.0698 | -59.0744 | -58.9233 | 0.1831 | -59.2026 | 63.8718 | 63.7573 | -59.1248 | -59.2026 | -0.068664 | -0.073242 | 0 | 123.024 | -0.17395 | -0.10071 | 0.059509 | -0.1236 | -0.20142 | 0.022888 | 0.07782 | -0.20142 | 0 | -0.091553 | 122.85 | 122.9095 | 59.079 | -122.9233 | 122.8729 | 122.7585 | 59.1843 | -123.0515
142.0156 | 123.1888 | -59.0469 | 63.8123 | -0.023041 | 0.00061311 | 0.067182 | 0.067526 | 0.13078 | -0.0026405 | 0.00061314 | 0.0074766 | -0.0035718 | 0.061487 | 0.063807 | -6.4178e-05 | -0.0042832 | 63.8443 | 63.9771 | -0.009155 | -59.2026 | 63.858 | -59.0836 | -59.1064 | -58.9417 | 0.09613 | -59.2392 | 63.858 | 63.7482 | -59.0881 | -59.23 | -0.036621 | -0.059509 | 0.045776 | 123.024 | -0.15564 | -0.096131 | 0.032043 | -0.041199 | -0.18311 | 0.045776 | 0.10529 | -0.19226 | -0.009155 | -0.064087 | 122.905 | 122.8912 | 59.0378 | -122.9187 | 122.905 | 122.7951 | 59.1431 | -123.0423
143.0156 | 123.1979 | -59.0012 | 63.8397 | -0.00015269 | 0.0025357 | 0.069105 | 0.070303 | 0.13206 | -0.0011451 | -0.0023777 | 0.022736 | -0.0037854 | 0.060633 | 0.061244 | 0.001004 | -0.0034286 | 63.8992 | 64.0411 | 0.036621 | -59.1934 | 63.8535 | -59.0744 | -59.0973 | -58.8776 | 0.16479 | -59.2026 | 63.8535 | 63.7482 | -59.0973 | -59.198 | -0.073242 | -0.09613 | 0.013733 | 123.0423 | -0.19226 | -0.09613 | 0.059509 | -0.09613 | -0.19684 | 0.013733 | 0.1236 | -0.20142 | -0.004578 | -0.091553 | 122.8546 | 122.9004 | 59.0378 | -122.937 | 122.8546 | 122.7493 | 59.166 | -123.0377
144.0156 | 123.1338 | -59.0469 | 63.826 | 0.13718 | 0.0018949 | 0.066969 | 0.065817 | 0.13078 | -0.00093145 | -0.0025913 | 0.11429 | -0.0044264 | 0.061487 | 0.060389 | 0.0022858 | -0.0044968 | 63.826 | 63.9542 | -0.041199 | -59.2484 | 63.8535 | -59.079 | -59.1156 | -58.873 | -0.15106 | -59.2575 | 63.8626 | 63.7527 | -59.111 | -59.23 | -0.032043 | -0.068665 | 0.027466 | 123.0011 | -0.20142 | -0.13275 | 0 | -0.064087 | -0.18311 | 0.036621 | 0.17395 | -0.21057 | -0.027465 | -0.073242 | 122.9004 | 122.8729 | 59.0057 | -122.9416 | 122.9095 | 122.7997 | 58.8959 | -123.056
145.0156 | 123.2025 | -59.0286 | 63.8031 | -0.17563 | 0.0018949 | 0.06761 | 0.070303 | 0.13185 | 0.00035035 | -0.0034457 | -1.465 | -0.0044264 | 0.06341 | 0.062739 | 0.0014312 | -0.0040696 | 63.9313 | 64.0732 | 0.086975 | -59.166 | 63.8672 | -59.0652 | -59.0836 | -58.9005 | 0.018311 | -59.1934 | 63.8535 | 63.7207 | -59.1248 | -59.2117 | -0.036622 | -0.054932 | 0.064086 | 123.1018 | -0.13733 | -0.082398 | 0.12817 | -0.096131 | -0.18311 | 0.050354 | 0.12817 | -0.1648 | 0.018311 | -0.082398 | 122.8958 | 122.9599 | 59.1156 | -122.8867 | 122.8821 | 122.7493 | 59.0469 | -123.0148
146.0156 | 123.1613 | -59.0286 | 63.826 | -0.061188 | 0.0012539 | 0.069532 | 0.068381 | 0.13228 | -0.00050425 | -0.0019505 | 0.015106 | -0.0061352 | 0.062982 | 0.062739 | 0.0016448 | -0.0036424 | 63.8718 | 64.0182 | 0.018311 | -59.2163 | 63.8626 | -59.0378 | -59.111 | -58.9417 | 0.1236 | -59.2117 | 63.8489 | 63.7207 | -59.1339 | -59.2026 | -0.009156 | -0.082398 | 0.036621 | 123.0469 | -0.18768 | -0.10529 | 0.045776 | -0.10529 | -0.17395 | 0.022888 | 0.086975 | -0.18311 | -0.009155 | -0.10529 | 122.8912 | 122.9004 | 59.0469 | -122.937 | 122.8775 | 122.7493 | 59.1522 | -123.0286
147.0156 | 123.175 | -59.0149 | 63.8535 | -0.12222 | 0.0033901 | 0.066328 | 0.066885 | 0.13249 | -0.00050425 | -0.0010959 | -0.16037 | -0.00229 | 0.061487 | 0.064021 | 0.002713 | -0.003215 | 63.9221 | 64.0457 | 0.086975 | -59.2072 | 63.8535 | -59.0469 | -59.0698 | -58.9233 | 0.16937 | -59.2255 | 63.8763 | 63.7848 | -59.079 | -59.198 | -0.032043 | -0.054931 | 0 | 123.0606 | -0.19226 | -0.13733 | 0.068664 | -0.064086 | -0.1831 | 0.022888 | 0.091553 | -0.21057 | -0.027466 | -0.068665 | 122.8683 | 122.937 | 59.1019 | -122.9233 | 122.8912 | 122.7997 | 59.1843 | -123.0515
148.0156 | 123.175 | -59.0332 | 63.8351 | -0.068817 | 0.0040311 | 0.066328 | 0.069022 | 0.13163 | -0.0011451 | -0.0017369 | 0.015106 | -0.002931 | 0.058924 | 0.062098 | 0.0022858 | -0.0027878 | 63.8626 | 63.9999 | 0.022888 | -59.2072 | 63.8397 | -59.0561 | -59.1156 | -58.9325 | 0.10529 | -59.2163 | 63.8351 | 63.7527 | -59.1293 | -59.2484 | -0.022888 | -0.082398 | 0.004578 | 123.0331 | -0.17395 | -0.091552 | 0.027466 | -0.09613 | -0.21515 | 0 | 0.10071 | -0.18311 | 0.032043 | -0.082397 | 122.8729 | 122.8958 | 59.0561 | -122.9507 | 122.8683 | 122.7859 | 59.1385 | -123.0835
149.0156 | 123.1613 | -59.0057 | 63.8535 | -0.053558 | 0.0029629 | 0.065473 | 0.069022 | 0.13163 | -7.6852e-05 | -0.0013095 | -0.068817 | -0.0033582 | 0.062342 | 0.061885 | 0.0018584 | -0.0034286 | 63.9175 | 64.0594 | 0.064087 | -59.1843 | 63.8397 | -59.0698 | -59.0973 | -58.9233 | 0.1831 | -59.198 | 63.8763 | 63.7665 | -59.1202 | -59.2117 | -0.064087 | -0.091553 | -0.013733 | 123.0652 | -0.17853 | -0.086975 | 0.064087 | -0.11444 | -0.20599 | 0.022888 | 0.082397 | -0.19226 | 0.013733 | -0.086976 | 122.8455 | 122.9233 | 59.0698 | -122.9507 | 122.8821 | 122.7722 | 59.1888 | -123.0652
150.0156 | 123.1567 | -59.0424 | 63.8489 | 0.030365 | 0.0027493 | 0.066969 | 0.070303 | 0.12907 | -0.0026405 | -0.0028049 | 0.0914 | -0.003999 | 0.060633 | 0.061885 | 0.0014312 | -0.0030014 | 64.0091 | 63.826 | -0.091553 | -59.23 | 63.8351 | -59.0698 | -59.0927 | -58.9966 | 0.013733 | -59.2804 | 63.8443 | 63.7619 | -59.1293 | -59.2392 | -0.027466 | -0.050354 | -0.013733 | 122.8683 | -0.18768 | -0.13733 | 0.16022 | -0.086975 | -0.19684 | -0.004578 | 0.045776 | -0.23804 | -0.041199 | -0.086975 | 122.8775 | 123.0515 | 58.9508 | -122.9416 | 122.8867 | 122.8043 | 59.0561 | -123.0881
151.0156 | 123.1888 | -59.0057 | 63.8214 | -0.10696 | 0.0021085 | 0.068464 | 0.071799 | 0.13206 | -0.00050425 | -0.0040867 | -0.16037 | -0.0048536 | 0.061914 | 0.061671 | 0.0029266 | -0.0036424 | 63.8901 | 64.0411 | 0.027466 | -59.2072 | 63.8535 | -59.0652 | -59.0973 | -58.8776 | 0.16022 | -59.1705 | 63.8535 | 63.7436 | -59.1293 | -59.1614 | -0.05951 | -0.091553 | 0.032044 | 123.0469 | -0.20142 | -0.10986 | 0.068665 | -0.1236 | -0.15564 | 0.032044 | 0.12817 | -0.16479 | -0.009155 | -0.07782 | 122.8592 | 122.8958 | 59.0332 | -122.9187 | 122.8592 | 122.7493 | 59.166 | -122.9828
152.0156 | 123.1888 | -59.0332 | 63.8489 | 0.015106 | 0.0029629 | 0.065687 | 0.067526 | 0.13099 | -0.0022131 | -0.0045139 | 0.045624 | -0.0027174 | 0.059778 | 0.060816 | 0.00036322 | -0.003856 | 63.8443 | 63.9633 | -0.018311 | -59.2392 | 63.858 | -59.0744 | -59.1293 | -58.96 | 0.091553 | -59.2438 | 63.8718 | 63.7436 | -59.111 | -59.2072 | -0.041199 | -0.09613 | 0.009155 | 122.9965 | -0.20599 | -0.10986 | -0.004578 | -0.07782 | -0.17395 | 0.022888 | 0.073242 | -0.21057 | -0.036621 | -0.10529 | 122.8912 | 122.8775 | 59.0149 | -122.9782 | 122.905 | 122.7768 | 59.1248 | -123.056
153.0156 | 123.1476 | -59.0332 | 63.8489 | -0.23666 | 0.0044583 | 0.065687 | 0.07009 | 0.13356 | -0.00050425 | -0.0013095 | -0.16037 | -0.003999 | 0.062555 | 0.06338 | 0.002713 | -0.0034286 | 63.8992 | 64.0411 | 0.082397 | -59.1751 | 63.858 | -59.0469 | -59.1385 | -58.9417 | 0.17853 | -59.2209 | 63.8672 | 63.7711 | -59.1248 | -59.2026 | -0.013733 | -0.10529 | 0.009155 | 123.0743 | -0.14191 | -0.036621 | 0.050354 | -0.091553 | -0.16937 | 0.01831 | 0.091553 | -0.18768 | -0.01831 | -0.07782 | 122.8912 | 122.9324 | 59.1156 | -122.9874 | 122.9004 | 122.8043 | 59.2117 | -123.0515
154.0156 | 123.175 | -59.0195 | 63.8077 | -0.0383 | -2.7692e-05 | 0.069532 | 0.068808 | 0.12907 | -0.0019995 | -0.0028049 | 0.022736 | -0.0031446 | 0.061273 | 0.062312 | 0.00014962 | -0.002147 | 63.8763 | 64.0182 | 0.027466 | -59.2346 | 63.8443 | -59.0652 | -59.1476 | -58.9096 | 0.12817 | -59.2117 | 63.8489 | 63.739 | -59.111 | -59.1934 | -0.045777 | -0.12817 | 0.036621 | 123.0377 | -0.21515 | -0.086975 | 0.068665 | -0.091553 | -0.17395 | 0.041199 | 0.10986 | -0.19226 | -0.018311 | -0.068664 | 122.8638 | 122.8958 | 59.0469 | -122.9553 | 122.8683 | 122.7585 | 59.1476 | -123.0011
155.0156 | 123.1338 | -59.0286 | 63.8443 | -0.12222 | 0.0038175 | 0.068678 | 0.07009 | 0.13228 | -0.00029045 | -2.7856e-05 | -0.16037 | -0.0031446 | 0.061487 | 0.062525 | 0.0018584 | -0.003856 | 63.9038 | 64.0366 | 0.086975 | -59.1888 | 63.8718 | -59.0378 | -59.1064 | -58.9233 | 0.1831 | -59.2209 | 63.8626 | 63.7619 | -59.1064 | -59.1843 | -0.009156 | -0.07782 | 0.027466 | 123.0652 | -0.16022 | -0.082398 | 0.05951 | -0.07782 | -0.15564 | 0.018311 | 0.10528 | -0.19226 | -0.036621 | -0.082397 | 122.9004 | 122.9324 | 59.1156 | -122.9507 | 122.8912 | 122.7905 | 59.2117 | -123.0286
156.0156 | 123.143 | -59.0378 | 63.8306 | -0.03067 | 0.00082671 | 0.067182 | 0.067313 | 0.13078 | 0.00013675 | -0.0028049 | -0.068817 | -0.0048536 | 0.061273 | 0.062953 | 0.0014312 | -0.0036424 | 63.8443 | 63.9954 | 0.004578 | -59.2209 | 63.8351 | -59.0698 | -59.0973 | -58.9279 | 0.10986 | -59.2255 | 63.8718 | 63.7299 | -59.1064 | -59.2072 | -0.032043 | -0.059509 | 0.004578 | 123.0331 | -0.1831 | -0.1236 | 0.013733 | -0.068664 | -0.16937 | 0.041199 | 0.10986 | -0.18768 | -0.018311 | -0.10071 | 122.8729 | 122.8821 | 59.0424 | -122.9279 | 122.9095 | 122.7676 | 59.1476 | -123.0377
157.0156 | 123.1934 | -59.0149 | 63.8397 | -0.11459 | 0.00061311 | 0.067182 | 0.065604 | 0.1327 | -0.0026405 | -0.0034457 | -0.076446 | -0.005708 | 0.060633 | 0.06338 | 0.0016448 | -0.004924 | 63.9084 | 64.0686 | 0.068665 | -59.1888 | 63.8626 | -59.0836 | -59.1339 | -58.8684 | 0.20599 | -59.1705 | 63.8535 | 63.7253 | -59.1019 | -59.2117 | -0.068664 | -0.11902 | 0.022888 | 123.0835 | -0.17395 | -0.054932 | 0.068664 | -0.086975 | -0.19684 | 0.013733 | 0.14648 | -0.15564 | 0.041199 | -0.11444 | 122.8775 | 122.9233 | 59.0836 | -122.9736 | 122.8683 | 122.7402 | 59.2209 | -123.0515
158.0156 | 123.143 | -59.0424 | 63.826 | 0.015106 | 0.0023221 | 0.067396 | 0.067313 | 0.1295 | -0.00071785 | -0.0030185 | 0.6102 | -0.0031446 | 0.059992 | 0.063594 | 0.0035674 | -0.0034286 | 63.8168 | 63.9542 | 0.050354 | -59.0973 | 63.9496 | -59.0424 | -59.0927 | -59.0012 | 0.027466 | -59.2667 | 63.8626 | 63.7482 | -59.1476 | -59.2484 | 0 | -0.050354 | 0.1236 | 122.9965 | -0.054932 | -0.004578 | -0.009156 | -0.10529 | -0.20599 | 0.036621 | 0.041198 | -0.22431 | -0.018311 | -0.07782 | 122.9919 | 122.8592 | 59.0927 | -122.9187 | 122.905 | 122.7905 | 59.0698 | -123.0743
159.0156 | 123.1796 | -59.0195 | 63.8214 | -0.19089 | 0.0057401 | 0.067396 | 0.071158 | 0.13228 | -0.0032813 | -0.0013095 | 0.13718 | -0.0037854 | 0.063196 | 0.062525 | 0.002713 | -0.003215 | 64.064 | 63.8351 | -0.073242 | -59.1385 | 63.8443 | -59.0607 | -59.1019 | -58.9188 | 0.19226 | -59.198 | 63.8763 | 63.7482 | -59.1064 | -59.2072 | -0.041199 | -0.082398 | 0.022888 | 122.8546 | -0.11902 | -0.036621 | 0.24262 | -0.086975 | -0.18768 | 0.054932 | 0.10071 | -0.17853 | 0.009155 | -0.073242 | 122.8638 | 123.0835 | 58.9462 | -122.9233 | 122.8958 | 122.7676 | 59.2117 | -123.0286
160.0156 | 123.1659 | -59.0012 | 63.826 | -0.0383 | 0.0027493 | 0.066755 | 0.067099 | 0.13163 | -0.0022131 | -0.0010959 | -0.053558 | -0.0048536 | 0.060205 | 0.063807 | 0.0014312 | -0.0027878 | 63.8718 | 64.032 | 0.036621 | -59.198 | 63.8214 | -59.0607 | -59.111 | -58.873 | 0.13275 | -59.1751 | 63.8718 | 63.739 | -59.1156 | -59.2026 | -0.059509 | -0.10986 | -0.004578 | 123.0331 | -0.19684 | -0.086975 | 0.045776 | -0.11444 | -0.20142 | 0.045776 | 0.12817 | -0.17395 | 0.027466 | -0.086975 | 122.8226 | 122.8729 | 59.0378 | -122.937 | 122.8729 | 122.7402 | 59.1339 | -123.0286
161.0156 | 123.1247 | -59.0012 | 63.8443 | -0.15274 | 0.0050991 | 0.067396 | 0.070517 | 0.13121 | -0.0019995 | -0.0013095 | -0.18326 | -0.0054944 | 0.060846 | 0.061457 | 0.0018584 | -0.0036424 | 63.8855 | 64.0274 | 0.068665 | -59.1888 | 63.8397 | -59.0607 | -59.1064 | -58.9417 | 0.15564 | -59.2392 | 63.8763 | 63.7482 | -59.0973 | -59.2117 | -0.059509 | -0.10529 | -0.004577 | 123.0286 | -0.18768 | -0.082398 | 0.041199 | -0.09613 | -0.21057 | 0.032044 | 0.05951 | -0.23804 | -0.027466 | -0.09613 | 122.8409 | 122.8867 | 59.0698 | -122.9507 | 122.8775 | 122.7493 | 59.1568 | -123.056
162.0156 | 123.1567 | -59.0332 | 63.826 | -0.091705 | 0.00061311 | 0.065687 | 0.066245 | 0.13206 | -0.00071785 | -0.0013095 | 0.022736 | -0.0033582 | 0.062128 | 0.062739 | 0.0018584 | -0.0036424 | 63.8672 | 64.0182 | 0.018311 | -59.2163 | 63.8855 | -59.0515 | -59.111 | -58.9279 | 0.13275 | -59.2163 | 63.826 | 63.7207 | -59.1019 | -59.2209 | -0.018311 | -0.07782 | 0.059509 | 123.0515 | -0.18311 | -0.10529 | 0.041198 | -0.068665 | -0.18768 | 0 | 0.10529 | -0.18311 | 0.004577 | -0.10529 | 122.9187 | 122.9004 | 59.0515 | -122.937 | 122.8592 | 122.7539 | 59.166 | -123.0469
163.0156 | 123.1384 | -59.0012 | 63.8672 | -0.15274 | 0.0012539 | 0.066328 | 0.067313 | 0.13078 | 0.00056395 | -0.00024146 | -0.13748 | -0.0031446 | 0.060633 | 0.06103 | 0.0031402 | -0.0030014 | 63.8855 | 64.064 | 0.086975 | -59.1751 | 63.8489 | -59.0698 | -59.0881 | -58.9462 | 0.17395 | -59.2209 | 63.8763 | 63.7527 | -59.1202 | -59.2163 | -0.068664 | -0.086975 | -0.01831 | 123.0652 | -0.17395 | -0.086975 | 0.018311 | -0.11902 | -0.21515 | 0.009156 | 0.054932 | -0.21973 | -0.004577 | -0.11444 | 122.85 | 122.8867 | 59.0881 | -122.9553 | 122.8775 | 122.7539 | 59.1751 | -123.0835
164.0156 | 123.1476 | -59.0332 | 63.8168 | -0.053558 | 0.00082671 | 0.066969 | 0.067099 | 0.13014 | -0.00071785 | -0.0010959 | 0.076141 | -0.0052808 | 0.062342 | 0.059962 | 0.00079042 | -0.0030014 | 63.8077 | 63.9679 | -0.022888 | -59.2392 | 63.8535 | -59.0973 | -59.111 | -58.9783 | 0.064087 | -59.2529 | 63.8901 | 63.7299 | -59.1202 | -59.2209 | -0.064087 | -0.07782 | 0.036622 | 123.0011 | -0.20599 | -0.12817 | -0.009155 | -0.086975 | -0.18768 | 0.073243 | 0.054932 | -0.21973 | -0.032044 | -0.086975 | 122.8867 | 122.8409 | 59.0103 | -122.9279 | 122.9233 | 122.7631 | 59.0973 | -123.0377
165.0156 | 123.2712 | -59.0195 | 63.8123 | -0.053558 | 0.0040311 | 0.066755 | 0.069449 | 0.1327 | -0.00050425 | -0.0025913 | -0.12222 | -0.0027174 | 0.059564 | 0.061244 | -0.00070498 | -0.0036424 | 63.9084 | 64.0686 | 0.091553 | -59.1843 | 63.8535 | -59.0195 | -59.0927 | -58.9005 | 0.17395 | -59.0012 | 63.8992 | 63.8168 | -59.0515 | -59.198 | 0 | -0.073242 | 0.041199 | 123.0881 | -0.1648 | -0.091553 | 0.09613 | -0.032044 | -0.17853 | 0.086975 | 0.11902 | 0.01831 | 0.19684 | 0.004577 | 122.8729 | 122.9279 | 59.111 | -122.905 | 122.9187 | 122.8363 | 59.1934 | -123.0103
166.0156 | 123.2071 | -59.0286 | 63.8214 | -0.03067 | 0.0027493 | 0.064619 | 0.069876 | 0.13655 | 0.00035035 | -0.0034457 | -0.068817 | -0.0031446 | 0.061273 | 0.062739 | 0.0014312 | -0.0036424 | 63.8443 | 64.0274 | 0 | -59.2072 | 63.8489 | -59.0698 | -59.111 | -58.9233 | 0.10071 | -59.2392 | 63.8351 | 63.7344 | -59.1202 | -59.2209 | -0.041199 | -0.082398 | 0.027466 | 123.056 | -0.17853 | -0.09613 | 0.022888 | -0.091553 | -0.19226 | 0.013733 | 0.10528 | -0.21057 | -0.018311 | -0.086975 | 122.8775 | 122.8729 | 59.0286 | -122.9324 | 122.8638 | 122.7631 | 59.1293 | -123.0423
167.0156 | 123.0972 | -59.024 | 63.8397 | -0.20615 | 0.0036039 | 0.06761 | 0.071372 | 0.13163 | 0.00035035 | -0.0013095 | -0.14511 | -0.0042126 | 0.061914 | 0.062953 | 0.00079042 | -0.0025742 | 63.8809 | 64.0182 | 0.059509 | -59.2026 | 63.8718 | -59.0652 | -59.0927 | -58.9783 | 0.14191 | -59.2621 | 63.8855 | 63.7802 | -59.1019 | -59.2209 | -0.041199 | -0.068664 | 0.032043 | 123.0423 | -0.17853 | -0.10986 | 0.041198 | -0.07782 | -0.19684 | 0.045776 | 0.045777 | -0.23804 | -0.041199 | -0.05951 | 122.8958 | 122.905 | 59.0836 | -122.9324 | 122.9095 | 122.8043 | 59.166 | -123.0606
168.0156 | 123.2208 | -58.9966 | 63.8351 | -0.12222 | 0.0023221 | 0.066328 | 0.067526 | 0.12971 | -0.0015723 | -0.00088226 | -0.068817 | -0.003999 | 0.061273 | 0.061671 | 0.0033538 | -0.003856 | 63.8809 | 64.0594 | 0.059509 | -59.1934 | 63.8489 | -59.0927 | -59.111 | -58.8821 | 0.1831 | -59.166 | 63.858 | 63.7299 | -59.079 | -59.198 | -0.09613 | -0.11444 | 0.013733 | 123.056 | -0.19684 | -0.082397 | 0.045776 | -0.082397 | -0.20142 | 0.022888 | 0.11444 | -0.16937 | 0.032043 | -0.10529 | 122.8455 | 122.8775 | 59.0561 | -122.9462 | 122.8546 | 122.7264 | 59.1797 | -123.0331
169.0156 | 123.1155 | -59.0332 | 63.8535 | -0.22141 | 0.0036039 | 0.067823 | 0.070731 | 0.13099 | 0.00056395 | -0.0032321 | -0.2214 | -0.0033582 | 0.062128 | 0.061244 | 0.0050628 | -0.002147 | 63.8901 | 64.0366 | 0.073242 | -59.1751 | 63.8626 | -59.0561 | -59.111 | -58.9508 | 0.16022 | -59.2529 | 63.8855 | 63.7482 | -59.1293 | -59.2163 | -0.022888 | -0.07782 | 0.009155 | 123.0698 | -0.14191 | -0.064087 | 0.036621 | -0.09613 | -0.18311 | 0.032043 | 0.082397 | -0.21973 | -0.036621 | -0.10529 | 122.8958 | 122.9233 | 59.1064 | -122.9645 | 122.9187 | 122.7814 | 59.1934 | -123.0698
170.0156 | 123.2162 | -59.0378 | 63.8306 | -0.099335 | -0.00088229 | 0.068464 | 0.068381 | 0.13099 | -0.0013587 | -0.0023777 | -0.053558 | -0.0035718 | 0.060633 | 0.061244 | 0.0024994 | -0.0019334 | 63.8809 | 64.0182 | 0.036621 | -59.198 | 63.8443 | -59.0836 | -59.111 | -58.9096 | 0.10071 | -59.1797 | 63.8397 | 63.7802 | -59.1064 | -59.2072 | -0.045776 | -0.073242 | 0.013733 | 123.056 | -0.16022 | -0.086975 | 0.050354 | -0.068664 | -0.16937 | 0.009156 | 0.12817 | -0.14191 | 0.027466 | -0.050354 | 122.8821 | 122.9187 | 59.0744 | -122.9416 | 122.8775 | 122.818 | 59.1385 | -123.0377
171.0156 | 123.1659 | -59.0195 | 63.8443 | -0.084076 | 0.0010403 | 0.06825 | 0.069235 | 0.13142 | -0.0013587 | -0.0013095 | -0.099335 | -0.0052808 | 0.057855 | 0.057398 | 0.0014312 | -0.0019334 | 63.9221 | 64.0823 | 0.086975 | -59.1751 | 63.858 | -59.0515 | -59.0973 | -59.0927 | 0.045776 | -59.1614 | 63.8397 | 63.7161 | -59.111 | -59.2255 | -0.032044 | -0.07782 | 0.013733 | 123.1018 | -0.15564 | -0.07782 | 0.07782 | -0.091553 | -0.20599 | -0.004577 | -0.073242 | -0.14191 | 0.064087 | -0.12817 | 122.8775 | 122.9416 | 59.1064 | -122.9416 | 122.8592 | 122.7356 | 59.0652 | -123.0698
172.0156 | 123.1567 | -59.0652 | 63.826 | -0.076447 | 0.0025357 | 0.065687 | 0.067954 | 0.13142 | -0.00029045 | -0.0025913 | 0.09903 | -0.0042126 | 0.062342 | 0.060816 | 0.0014312 | -0.004924 | 63.8123 | 63.9633 | -0.032043 | -59.2484 | 63.8443 | -59.0744 | -59.1476 | -58.9828 | 0.059509 | -59.2529 | 63.8535 | 63.7299 | -59.1339 | -59.2255 | -0.009155 | -0.082397 | 0.01831 | 123.0286 | -0.1831 | -0.10071 | -0.013733 | -0.068664 | -0.16022 | 0.027466 | 0.082398 | -0.18768 | -0.027466 | -0.096131 | 122.9095 | 122.8775 | 59.0332 | -122.9736 | 122.9187 | 122.7951 | 59.1248 | -123.0515
173.0156 | 123.0835 | -59.0149 | 63.8672 | -0.22141 | 0.0044583 | 0.06761 | 0.069876 | 0.13035 | 0.0018457 | -0.0038731 | -0.23666 | -0.0044264 | 0.061914 | 0.063166 | 0.0039948 | -0.0027878 | 63.8763 | 64.0182 | 0.068665 | -59.2026 | 63.8626 | -59.0881 | -59.1293 | -58.9828 | 0.11902 | -59.2667 | 63.913 | 63.7802 | -59.111 | -59.2209 | -0.073242 | -0.11444 | -0.004577 | 123.0331 | -0.18768 | -0.073243 | 0.009156 | -0.09613 | -0.20599 | 0.045777 | 0.032044 | -0.25177 | -0.045777 | -0.086975 | 122.8775 | 122.8912 | 59.0836 | -122.9965 | 122.9279 | 122.7951 | 59.1339 | -123.0881
174.0156 | 123.1842 | -59.0149 | 63.8397 | -0.084076 | 0.0023221 | 0.067823 | 0.067099 | 0.13014 | 0.00013675 | -0.0010959 | 0.037995 | -0.0031446 | 0.059778 | 0.062525 | 0.001004 | -0.0030014 | 63.8947 | 64.0411 | 0.059509 | -59.2026 | 63.8535 | -59.0652 | -59.0881 | -58.8776 | 0.19684 | -59.1751 | 63.858 | 63.7619 | -59.0973 | -59.198 | -0.050354 | -0.073242 | 0.013733 | 123.056 | -0.18768 | -0.11444 | 0.054931 | -0.082397 | -0.1831 | 0.01831 | 0.13733 | -0.16022 | 0.022888 | -0.07782 | 122.8683 | 122.9095 | 59.0744 | -122.9279 | 122.8729 | 122.7768 | 59.2117 | -123.0377
175.0156 | 123.111 | -59.0378 | 63.8672 | -0.18326 | 0.0046719 | 0.068891 | 0.070303 | 0.13035 | 0.0016321 | -0.0010959 | -0.19089 | -0.0031446 | 0.060846 | 0.060389 | 0.0018584 | -0.0042832 | 63.8763 | 64.0182 | 0.073242 | -59.1843 | 63.8672 | -59.0424 | -59.0973 | -58.9371 | 0.13733 | -59.2392 | 63.8809 | 63.7665 | -59.1019 | -59.2117 | -0.004577 | -0.059509 | 0 | 123.056 | -0.14648 | -0.086975 | 0.009156 | -0.064087 | -0.17395 | 0.013733 | 0.10071 | -0.20142 | -0.027466 | -0.10071 | 122.905 | 122.9141 | 59.111 | -122.9645 | 122.9187 | 122.8043 | 59.1751 | -123.0789
176.0156 | 123.1842 | -59.0103 | 63.8535 | -0.015411 | 0.00061311 | 0.067823 | 0.066245 | 0.13035 | -0.00093145 | -0.0017369 | -0.03067 | -0.002931 | 0.061487 | 0.06103 | -0.00049138 | -0.0027878 | 63.8809 | 64.0274 | 0.027466 | -59.1934 | 63.8489 | -59.0881 | -59.1064 | -58.9005 | 0.16479 | -59.1934 | 63.8626 | 63.7436 | -59.111 | -59.2117 | -0.07782 | -0.09613 | -0.004578 | 123.0377 | -0.18311 | -0.086975 | 0.027465 | -0.10071 | -0.20142 | 0.009155 | 0.10986 | -0.18311 | 0.018311 | -0.10986 | 122.8592 | 122.8912 | 59.0378 | -122.9599 | 122.8729 | 122.7539 | 59.1751 | -123.0652
177.0156 | 123.1338 | -59.0149 | 63.8443 | -0.19852 | 0.0044583 | 0.066541 | 0.069235 | 0.13228 | -7.6852e-05 | -0.0017369 | -0.18326 | -0.0037854 | 0.061273 | 0.060603 | 0.0029266 | -0.0047104 | 63.8855 | 64.0366 | 0.068665 | -59.1843 | 63.858 | -59.0469 | -59.111 | -58.9462 | 0.16022 | -59.2209 | 63.8809 | 63.7756 | -59.1202 | -59.1888 | -0.032043 | -0.09613 | 0.013733 | 123.0515 | -0.16937 | -0.073242 | 0.041199 | -0.10529 | -0.17395 | 0.036621 | 0.068665 | -0.20599 | -0.032043 | -0.068664 | 122.8729 | 122.9004 | 59.0836 | -122.9553 | 122.8958 | 122.7905 | 59.1751 | -123.0331
178.0156 | 123.1613 | -59.0149 | 63.8351 | -0.0077822 | 0.0072355 | 0.067823 | 0.067313 | 0.12971 | -0.0034949 | -0.0010959 | 0.045624 | -0.0035718 | 0.060846 | 0.061244 | 0.00057682 | -0.003215 | 63.7985 | 63.9679 | -0.022888 | -59.2392 | 63.8489 | -59.079 | -59.1202 | -58.96 | 0.073242 | -59.2346 | 63.8626 | 63.7344 | -59.1339 | -59.2209 | -0.064086 | -0.10529 | 0.013733 | 122.9828 | -0.2243 | -0.11902 | -0.036621 | -0.11902 | -0.20599 | 0.027466 | 0.054932 | -0.21973 | -0.013733 | -0.10071 | 122.8638 | 122.8134 | 58.992 | -122.9553 | 122.8775 | 122.7493 | 59.0881 | -123.056
179.0156 | 123.2162 | -58.9966 | 63.8443 | -0.14511 | 0.0023221 | 0.066755 | 0.069022 | 0.12907 | -0.0015723 | -0.0036595 | -1.404 | -0.0037854 | 0.064051 | 0.062098 | 0.0024994 | -0.0034286 | 63.9175 | 64.0961 | 0.091553 | -59.1568 | 63.8443 | -59.0561 | -59.1202 | -58.9005 | 0.032043 | -59.1934 | 63.8535 | 63.7115 | -59.1293 | -59.2209 | -0.059509 | -0.1236 | 0 | 123.0927 | -0.16022 | -0.036621 | 0.073243 | -0.13275 | -0.2243 | 0.009156 | 0.09613 | -0.19684 | 0.027466 | -0.13275 | 122.8409 | 122.9141 | 59.0881 | -122.9645 | 122.85 | 122.7081 | 59.0286 | -123.0652
180.0156 | 123.1338 | -59.0149 | 63.8123 | -0.14511 | 0.0016813 | 0.067396 | 0.064963 | 0.13057 | 0.00035035 | -0.0010959 | -0.13748 | -0.0035718 | 0.060633 | 0.06103 | 0.0050628 | -0.003215 | 63.9038 | 64.0869 | 0.10071 | -59.166 | 63.8672 | -59.0561 | -59.0881 | -59.0836 | 0.36163 | -59.23 | 63.8489 | 63.7115 | -59.1339 | -59.2072 | -0.041198 | -0.073242 | 0.054931 | 123.1018 | -0.15106 | -0.07782 | 0.091553 | -0.11902 | -0.19226 | 0.036621 | -0.068664 | -0.21515 | -0.022889 | -0.10071 | 122.8821 | 122.9187 | 59.1156 | -122.9004 | 122.8638 | 122.7264 | 59.3765 | -123.0194
181.0156 | 123.1018 | -59.0469 | 63.8672 | -0.22903 | 0.0053129 | 0.06526 | 0.069235 | 0.13249 | 0.00035035 | -0.0025913 | -0.21378 | -0.0031446 | 0.063837 | 0.061457 | 0.0016448 | -0.0030014 | 63.8672 | 64.0091 | 0.032043 | -59.2117 | 63.8718 | -59.0469 | -59.1248 | -58.9966 | 0.086975 | -59.2896 | 63.9038 | 63.7573 | -59.1156 | -59.2392 | 0 | -0.07782 | 0.004578 | 123.056 | -0.16479 | -0.086975 | 0 | -0.068665 | -0.19226 | 0.036622 | 0.050354 | -0.24262 | -0.050354 | -0.10986 | 122.9187 | 122.9141 | 59.079 | -122.9919 | 122.9507 | 122.8043 | 59.1339 | -123.1064
182.0156 | 123.2162 | -59.0378 | 63.8168 | -0.015411 | 0.0023221 | 0.066114 | 0.069663 | 0.12715 | -0.0011451 | -0.0017369 | -0.12985 | -0.00229 | 0.059564 | 0.061457 | -0.00027778 | -0.0036424 | 63.8947 | 64.0732 | 0.086975 | -59.166 | 63.858 | -59.0378 | -59.0973 | -58.7494 | -0.20142 | -59.3216 | 63.8626 | 63.7344 | -59.1019 | -59.2026 | 0 | -0.059509 | 0.041199 | 123.111 | -0.12817 | -0.068665 | 0.07782 | -0.064087 | -0.16479 | 0.045777 | 0.28839 | -0.28381 | -0.11902 | -0.082397 | 122.8958 | 122.9324 | 59.1248 | -122.9141 | 122.9004 | 122.7722 | 58.8364 | -123.0194
183.0156 | 123.0652 | -59.0378 | 63.913 | -0.22903 | 0.0046719 | 0.068464 | 0.069235 | 0.1342 | 0.00056395 | -0.0023777 | -0.20615 | -0.002931 | 0.062342 | 0.061457 | 0.0024994 | -0.003215 | 63.8535 | 63.9816 | 0.032043 | -59.2117 | 63.8535 | -59.0607 | -59.1019 | -58.9783 | 0.091553 | -59.2804 | 63.913 | 63.7894 | -59.1339 | -59.2163 | -0.022888 | -0.064087 | -0.059509 | 123.0194 | -0.17395 | -0.10986 | -0.059509 | -0.09613 | -0.17853 | 0 | 0.05951 | -0.24262 | -0.064087 | -0.1236 | 122.8912 | 122.8912 | 59.0698 | -123.0148 | 122.9507 | 122.8271 | 59.1293 | -123.1293
184.0156 | 123.1247 | -59.0103 | 63.8214 | -0.13748 | 0.0012539 | 0.067823 | 0.068808 | 0.12736 | -0.0032813 | -0.00045506 | -0.15274 | -0.0033582 | 0.061701 | 0.064234 | 0.00057682 | -0.0047104 | 63.8763 | 64.0961 | 0.073242 | -59.1751 | 63.8763 | -59.0515 | -59.0652 | -58.9783 | 0.70496 | -59.1751 | 63.913 | 63.7802 | -59.1064 | -59.2255 | -0.041199 | -0.054932 | 0.054932 | 123.1064 | -0.16479 | -0.10986 | 0.054932 | -0.09613 | -0.21515 | 0.091553 | 0.032044 | -0.16479 | 0.050354 | -0.041199 | 122.8867 | 122.8867 | 59.0836 | -122.8867 | 122.9233 | 122.7905 | 59.7153 | -123.0469
185.0156 | 123.1522 | -59.0149 | 63.8672 | 0.31265 | 0.0057401 | 0.070387 | 0.07009 | 0.13078 | -0.00093145 | -0.0017369 | -0.16037 | -0.0050672 | 0.061273 | 0.060603 | 0.0014312 | -0.003856 | 63.8947 | 64.0503 | 0.082397 | -59.1934 | 63.8718 | -59.0515 | -59.1156 | -58.9371 | 0.17853 | -59.2117 | 63.8901 | 63.7299 | -59.0927 | -59.2072 | -0.036621 | -0.10071 | 0.004578 | 123.0652 | -0.17853 | -0.077819 | 0.027466 | -0.077819 | -0.19226 | 0.022889 | 0.07782 | -0.19684 | -0.004578 | -0.13733 | 122.8867 | 122.9095 | 59.0973 | -122.9828 | 122.905 | 122.7448 | 59.1934 | -123.0743
186.0156 | 123.262 | -58.9691 | 63.858 | -0.14511 | 0.0021085 | 0.066969 | 0.066672 | 0.13078 | -0.0022131 | -0.0013095 | -0.091705 | -0.0027174 | 0.063196 | 0.063594 | 0.00014962 | -0.003215 | 63.8809 | 64.0732 | 0.082397 | -59.1888 | 63.8535 | -59.0378 | -59.0973 | -58.8867 | 0.1831 | -59.1843 | 63.8443 | 63.7344 | -59.1019 | -59.2072 | -0.068665 | -0.12817 | -0.004577 | 123.0423 | -0.21973 | -0.091553 | 0.022888 | -0.13275 | -0.23804 | -0.013733 | 0.082397 | -0.21515 | 0.022888 | -0.1236 | 122.8226 | 122.85 | 59.0515 | -122.9553 | 122.8134 | 122.7036 | 59.1522 | -123.0652
187.0156 | 123.0469 | -59.0561 | 63.8992 | -0.12985 | 0.0070217 | 0.065687 | 0.070731 | 0.1342 | 0.00056395 | -0.0017369 | -0.2214 | -0.0025038 | 0.064691 | 0.061885 | 0.0012176 | -0.002147 | 63.8123 | 63.9267 | -0.027466 | -59.2529 | 63.8992 | -59.0927 | -59.1339 | -59.0195 | 0.11444 | -59.1339 | 63.9587 | 63.8077 | -59.111 | -59.2163 | -0.036621 | -0.07782 | 0 | 122.9828 | -0.19684 | -0.11902 | -0.086975 | -0.054932 | -0.16022 | 0.059509 | 0.036621 | -0.07782 | 0.082398 | -0.091553 | 122.9553 | 122.8683 | 59.0286 | -123.0331 | 123.0148 | 122.8638 | 59.1705 | -123.1155
188.0156 | 123.1705 | -59.0195 | 63.8443 | -1.5184 | 0.0038175 | 0.065046 | 0.065817 | 0.13057 | -0.0019995 | -0.00088226 | -0.11459 | -0.0042126 | 0.061273 | 0.059962 | 0.0029266 | -0.002147 | 63.7527 | 64.0915 | 0.11444 | -59.1888 | 63.826 | -59.0515 | -59.1019 | -58.9233 | 0.18768 | -59.198 | 63.8397 | 63.7573 | -59.1202 | -59.2072 | -0.032044 | -0.082398 | -0.01831 | 123.111 | -0.16937 | -0.086975 | -0.091552 | -0.10071 | -0.18768 | -0.004577 | 0.09613 | -0.17853 | 0.009155 | -0.086975 | 122.8455 | 122.7722 | 59.1339 | -122.9462 | 122.8592 | 122.7768 | 59.2072 | -123.0515
189.0156 | 123.056 | -59.0195 | 63.9038 | -0.26718 | 0.0070217 | 0.066328 | 0.069022 | 0.13142 | -0.00071785 | -0.0036595 | -0.168 | -0.002931 | 0.062555 | 0.061671 | 0.0018584 | -0.0042832 | 63.8214 | 63.9221 | -0.032043 | -59.2667 | 63.9084 | -59.0927 | -59.1156 | -59.024 | 0.054932 | -59.3079 | 63.9267 | 63.7939 | -59.1431 | -59.2163 | -0.073242 | -0.096131 | 0.004577 | 122.9416 | -0.24719 | -0.15106 | -0.082398 | -0.1236 | -0.19684 | 0.022888 | -0.004578 | -0.28839 | -0.091552 | -0.10986 | 122.9279 | 122.8409 | 58.9874 | -123.0194 | 122.9462 | 122.8134 | 59.0744 | -123.1201
190.0156 | 123.1522 | -59.024 | 63.8443 | -0.168 | 0.0012539 | 0.066755 | 0.068381 | 0.13228 | -0.00093145 | -0.0021641 | -0.068817 | -0.0042126 | 0.060419 | 0.062098 | -0.00027778 | -0.0068466 | 63.8168 | 64.3387 | 0.24719 | -59.3857 | 63.8535 | -59.0607 | -59.1248 | -58.9096 | 0.1831 | -59.2026 | 63.8443 | 63.7527 | -59.0927 | -59.2209 | -0.036621 | -0.10071 | 0.009156 | 123.3627 | -0.36163 | -0.26093 | -0.027466 | -0.068664 | -0.19684 | 0 | 0.11444 | -0.17853 | 0.01831 | -0.091552 | 122.8775 | 122.8409 | 59.2712 | -122.9691 | 122.8683 | 122.7768 | 59.2072 | -123.0652
191.0156 | 123.0377 | -59.0378 | 63.8809 | -0.25192 | 0.0050991 | 0.067182 | 0.068594 | 0.13057 | -0.00093145 | -0.0017369 | -0.38925 | -0.003999 | 0.062982 | 0.06103 | 0.0014312 | -0.0030014 | 63.826 | 63.9633 | 0 | -59.2346 | 63.8992 | -59.079 | -59.1293 | -59.024 | 0.068665 | -59.3033 | 63.9084 | 63.7939 | -59.1385 | -59.2392 | -0.041198 | -0.091552 | 0.018311 | 123.0011 | -0.19684 | -0.10529 | -0.054931 | -0.10071 | -0.20142 | 0.027466 | 0.013733 | -0.2655 | -0.064087 | -0.086975 | 122.937 | 122.8638 | 59.0378 | -123.0103 | 122.9462 | 122.8317 | 59.1064 | -123.1201
192.0156 | 123.1613 | -59.0012 | 63.8214 | -0.045929 | 0.0031765 | 0.065473 | 0.064963 | 0.13099 | -0.0019995 | -0.0034457 | 0.030365 | -0.0037854 | 0.061487 | 0.060816 | 0.0016448 | -0.0023606 | 63.8489 | 64.0091 | 0.013733 | -59.2163 | 63.8535 | -59.079 | -59.0973 | -58.9279 | 0.14191 | -59.2072 | 63.8443 | 63.7482 | -59.0836 | -59.2163 | -0.077819 | -0.09613 | 0.032044 | 123.0103 | -0.21515 | -0.11902 | 0.027466 | -0.082397 | -0.21515 | 0.022888 | 0.073243 | -0.20599 | 0.009156 | -0.073242 | 122.8546 | 122.85 | 59.0149 | -122.9187 | 122.8455 | 122.7493 | 59.1431 | -123.0377
193.0156 | 123.056 | -59.0424 | 63.8718 | -0.22141 | 0.0048855 | 0.068678 | 0.071799 | 0.13398 | 0.00035035 | -0.0015231 | -0.18326 | -0.0025038 | 0.062982 | 0.061457 | 0.0018584 | -0.0044968 | 63.826 | 63.9816 | 0.032043 | -59.198 | 63.8992 | -59.0652 | -59.1064 | -59.0057 | 0.11444 | -59.2987 | 63.8992 | 63.7756 | -59.1431 | -59.2209 | -0.022889 | -0.064087 | 0.027466 | 123.024 | -0.15564 | -0.091553 | -0.045776 | -0.10071 | -0.17853 | 0.027466 | 0.036621 | -0.25635 | -0.07782 | -0.09613 | 122.9416 | 122.8683 | 59.0744 | -122.9782 | 122.9416 | 122.818 | 59.1568 | -123.0927
194.0156 | 123.1384 | -59.0103 | 63.858 | -0.40451 | 0.00061311 | 0.069959 | 0.066885 | 0.12907 | -0.0024269 | -0.0019505 | -0.12222 | -0.0044264 | 0.060633 | 0.061885 | 0.0016448 | -0.0025742 | 63.8718 | 64.0549 | 0.064087 | -59.1797 | 63.8672 | -59.0607 | -59.1064 | -58.9417 | 0.17395 | -59.2163 | 63.8626 | 63.7482 | -59.0927 | -59.198 | -0.050354 | -0.09613 | 0.009155 | 123.0652 | -0.16937 | -0.073242 | 0.013733 | -0.082397 | -0.18768 | 0.004578 | 0.068665 | -0.20599 | -0.018311 | -0.10986 | 122.8775 | 122.8821 | 59.0744 | -122.9645 | 122.8729 | 122.7585 | 59.1843 | -123.056
195.0156 | 123.0331 | -59.0698 | 63.8672 | -0.24429 | 0.0070217 | 0.066328 | 0.071158 | 0.13035 | 0.00056395 | -0.0032321 | -0.17563 | -0.002931 | 0.064264 | 0.058894 | 0.00057682 | -0.003215 | 63.7939 | 63.9175 | -0.009155 | -59.2484 | 63.9313 | -59.1019 | -59.1339 | -59.0012 | -0.16479 | -59.3216 | 63.9221 | 63.8214 | -59.1476 | -59.2575 | -0.032044 | -0.064087 | 0.064087 | 122.9874 | -0.17853 | -0.11444 | -0.073242 | -0.07782 | -0.18768 | 0.054932 | 0.068664 | -0.25177 | -0.064087 | -0.045776 | 123.0011 | 122.8638 | 59.0607 | -123.0011 | 122.9919 | 122.8912 | 58.905 | -123.1247
196.0156 | 123.1293 | -59.0012 | 63.826 | 0.4805 | 0.0042447 | 0.066114 | 0.067526 | 0.13356 | -0.0017859 | -0.0038731 | -0.12222 | -0.002931 | 0.061487 | 0.063807 | 0.0020722 | -0.003215 | 63.8809 | 64.064 | 0.082397 | -59.1934 | 63.8855 | -59.0378 | -59.0744 | -58.9325 | 0.17853 | -59.2026 | 63.8672 | 63.7573 | -59.0836 | -59.2026 | -0.036621 | -0.073242 | 0.059509 | 123.0652 | -0.19226 | -0.11902 | 0.054931 | -0.082397 | -0.20142 | 0.041198 | 0.068665 | -0.20142 | 0 | -0.068665 | 122.8867 | 122.8821 | 59.0836 | -122.9004 | 122.8683 | 122.7585 | 59.1797 | -123.0286
197.0156 | 122.9782 | -59.0469 | 63.8672 | -0.53421 | 0.0046719 | 0.06761 | 0.069022 | 0.1295 | -0.0011451 | -0.0023777 | -0.168 | -0.003999 | 0.064264 | 0.061671 | 0.001004 | -0.0042832 | 63.8123 | 63.913 | -0.027466 | -59.2575 | 63.9267 | -59.0927 | -59.1248 | -59.0195 | 0.064087 | -59.3216 | 63.9221 | 63.8031 | -59.1064 | -59.2163 | -0.045776 | -0.07782 | 0.05951 | 122.9599 | -0.21057 | -0.13275 | -0.054931 | -0.059509 | -0.16937 | 0.054932 | 0.027466 | -0.27466 | -0.10528 | -0.064086 | 122.9736 | 122.8592 | 59.0195 | -122.9919 | 122.9691 | 122.85 | 59.111 | -123.0835
198.0156 | 123.1934 | -59.0012 | 63.8489 | -0.12985 | 0.0040311 | 0.066969 | 0.069663 | 0.13078 | -0.0034949 | -0.0038731 | -0.13748 | -0.0048536 | 0.062982 | 0.062739 | -0.0011322 | -0.0027878 | 63.8763 | 64.0366 | 0.041199 | -59.1705 | 63.858 | -59.0286 | -59.0836 | -58.8959 | 0.18768 | -59.166 | 63.8535 | 63.7482 | -59.079 | -59.2117 | -0.027465 | -0.082397 | 0.009155 | 123.0377 | -0.16937 | -0.086975 | 0.027466 | -0.077819 | -0.21057 | 0.004578 | 0.10529 | -0.16479 | 0.045776 | -0.10071 | 122.8592 | 122.8775 | 59.0424 | -122.9324 | 122.8546 | 122.7493 | 59.1888 | -123.0606
199.0156 | 123.1018 | -59.0057 | 63.8718 | -0.17563 | 0.0061673 | 0.06825 | 0.06539 | 0.13185 | -0.00093145 | -0.00066866 | -0.14511 | -0.003999 | 0.062982 | 0.062739 | 0.0016448 | -0.0027878 | 63.8535 | 64.0228 | 0.068665 | -59.1751 | 63.8489 | -59.0607 | -59.1248 | -58.9645 | 0.13733 | -59.2346 | 63.8672 | 63.7665 | -59.0973 | -59.2072 | -0.054932 | -0.11902 | -0.022888 | 123.0286 | -0.16937 | -0.050354 | -0.01831 | -0.091553 | -0.20142 | -0.004578 | 0.041198 | -0.22888 | -0.027466 | -0.10529 | 122.8546 | 122.8592 | 59.0744 | -122.9965 | 122.8729 | 122.7722 | 59.1431 | -123.0789
200.0156 | 123.175 | -59.0057 | 63.8351 | -0.18326 | 0.0021085 | 0.067396 | 0.066458 | 0.13292 | -0.00093145 | -0.0021641 | -0.30533 | -0.002931 | 0.059992 | 0.063594 | 0.0035674 | -0.0042832 | 63.8992 | 64.2792 | 0.21057 | -59.3811 | 63.8718 | -59.0378 | -59.1293 | -58.905 | 0.17395 | -59.2026 | 63.858 | 63.7482 | -59.1064 | -59.2209 | -0.032044 | -0.1236 | 0.036621 | 123.2849 | -0.37537 | -0.25177 | 0.064087 | -0.10071 | -0.21515 | 0.022888 | 0.10071 | -0.19684 | 0.01831 | -0.086975 | 122.8775 | 122.905 | 59.2163 | -122.9645 | 122.8638 | 122.7539 | 59.1797 | -123.056
201.0156 | 123.0469 | -59.0515 | 63.8763 | -0.23666 | 0.0068081 | 0.069105 | 0.074576 | 0.13057 | 0.0033411 | -0.0013095 | -0.34348 | -0.0027174 | 0.063837 | 0.061885 | 0.0020722 | -0.0047104 | 63.7207 | 63.913 | -0.059509 | -59.2804 | 63.9084 | -59.0881 | -59.1568 | -59.0286 | 0.050354 | -59.3124 | 63.913 | 63.7802 | -59.1614 | -59.23 | -0.036621 | -0.10529 | 0.032043 | 122.9645 | -0.22888 | -0.1236 | -0.15564 | -0.10986 | -0.17853 | 0.036621 | 0.022889 | -0.26093 | -0.082397 | -0.096131 | 122.9599 | 122.7722 | 58.992 | -123.0331 | 122.9645 | 122.8317 | 59.1019 | -123.1064
202.0156 | 123.1659 | -59.1156 | 63.8443 | 0.18295 | 0.011935 | 0.068891 | 0.071799 | 0.12971 | 0.0016321 | -0.00024146 | 0.083771 | -0.0018628 | 0.064478 | 0.062739 | 0.0029266 | -0.0034286 | 63.7619 | 63.8214 | -0.15564 | -59.2758 | 63.8901 | -59.1064 | -59.166 | -59.0652 | -0.082397 | -59.3811 | 63.8718 | 63.7939 | -59.1751 | -59.2712 | 0.009156 | -0.050354 | 0.045777 | 122.937 | -0.16022 | -0.10986 | -0.082397 | -0.059509 | -0.15564 | 0.027466 | 0.050354 | -0.2655 | -0.10986 | -0.050354 | 123.0057 | 122.8775 | 58.96 | -123.0103 | 122.9874 | 122.9095 | 59.0332 | -123.1155
203.0156 | 123.0286 | -59.0469 | 63.8763 | -0.20615 | 0.0063809 | 0.065687 | 0.071799 | 0.13099 | 0.00077755 | 0.00018594 | 0.10666 | -0.0016492 | 0.061487 | 0.063594 | 0.00036322 | -0.002147 | 63.7985 | 63.9542 | 0.14648 | -59.166 | 63.9267 | -59.0515 | -59.1202 | -59.0561 | 0.082397 | -59.3308 | 63.9084 | 63.826 | -59.1339 | -59.2392 | -0.004578 | -0.073242 | 0.050354 | 123.0011 | -0.11902 | -0.045777 | -0.07782 | -0.086975 | -0.19226 | 0.032043 | -0.009155 | -0.28381 | -0.091553 | -0.050354 | 122.9736 | 122.8455 | 59.1934 | -122.9965 | 122.9553 | 122.8729 | 59.1293 | -123.1155
204.0156 | 123.143 | -59.0195 | 63.8443 | -0.12222 | 0.0036039 | 0.068037 | 0.068167 | 0.13142 | -0.0039221 | -0.0036595 | -0.076446 | -0.0048536 | 0.062555 | 0.061457 | 0.0029266 | -0.003215 | 63.8626 | 64.0228 | 0.086975 | -59.1797 | 63.8535 | -59.0561 | -59.1202 | -58.9279 | 0.16937 | -59.2026 | 63.8397 | 63.7711 | -59.0973 | -59.2026 | -0.036621 | -0.10071 | 0.009156 | 123.0423 | -0.16022 | -0.059509 | 0.018311 | -0.07782 | -0.18311 | -0.004577 | 0.091553 | -0.18311 | 0 | -0.073242 | 122.8729 | 122.8821 | 59.1064 | -122.9645 | 122.8592 | 122.7905 | 59.1888 | -123.0469
205.0156 | 123.0469 | -59.0561 | 63.8718 | -0.26718 | 0.0063809 | 0.06761 | 0.06774 | 0.1327 | -0.0011451 | -0.0010959 | 0.19821 | -0.0031446 | 0.061701 | 0.06103 | 0.0014312 | -0.0047104 | 63.7848 | 63.9038 | -0.027466 | -59.2621 | 63.9038 | -59.0744 | -59.1293 | -59.0652 | 0.041199 | -59.3216 | 63.913 | 63.7985 | -59.1339 | -59.2484 | -0.018311 | -0.073242 | 0.032044 | 122.9599 | -0.20599 | -0.13275 | -0.086975 | -0.07782 | -0.19226 | 0.041199 | -0.009156 | -0.2655 | -0.073242 | -0.073242 | 122.9599 | 122.8409 | 59.0286 | -123.0011 | 122.9691 | 122.8546 | 59.0973 | -123.1201
206.0156 | 123.2162 | -59.0378 | 63.8077 | -0.19852 | 0.0023221 | 0.068037 | 0.065817 | 0.13121 | -0.0024269 | -2.7856e-05 | -0.061188 | -0.0031446 | 0.062769 | 0.061885 | -0.00070498 | -0.0051376 | 63.8809 | 64.0503 | 0.07782 | -59.1797 | 63.858 | -59.0378 | -59.111 | -58.9325 | 0.17853 | -59.0927 | 63.8626 | 63.8306 | -59.0424 | -59.2026 | 0 | -0.073242 | 0.050354 | 123.0881 | -0.14191 | -0.068664 | 0.073242 | -0.004577 | -0.16479 | 0.054932 | 0.10529 | -0.054931 | 0.10986 | 0.022888 | 122.8958 | 122.9187 | 59.1156 | -122.9187 | 122.9004 | 122.8683 | 59.2163 | -123.0103
207.0156 | 123.1155 | -59.0652 | 63.8168 | 0.15244 | 0.0085171 | 0.067182 | 0.069663 | 0.13078 | 0.0029137 | -0.0013095 | 0.19821 | -0.0014356 | 0.062555 | 0.06338 | 0.0031402 | -0.0042832 | 63.7756 | 63.8672 | -0.13733 | -59.2941 | 63.8718 | -59.0927 | -59.1522 | -59.0195 | -0.045776 | -59.317 | 63.8672 | 63.7573 | -59.1476 | -59.2529 | -0.027465 | -0.086975 | 0.054932 | 122.9324 | -0.22888 | -0.14191 | -0.041198 | -0.082397 | -0.18768 | 0.050354 | 0.045777 | -0.25177 | -0.064087 | -0.059509 | 122.937 | 122.8409 | 58.9279 | -122.9691 | 122.9324 | 122.8226 | 59.0195 | -123.0698
208.0156 | 123.0835 | -59.0424 | 63.8626 | -0.22903 | 0.0025357 | 0.066541 | 0.070517 | 0.13228 | -0.0032813 | -0.0025913 | -0.168 | -0.0016492 | 0.062769 | 0.062739 | 0.001004 | -0.0040696 | 63.8397 | 63.9999 | 0.054932 | -59.198 | 63.858 | -59.0424 | -59.111 | -58.9966 | 0.13275 | -59.2438 | 63.8763 | 63.8123 | -59.111 | -59.1888 | 0 | -0.068665 | -0.004578 | 123.0423 | -0.15564 | -0.086975 | -0.022888 | -0.068665 | -0.14648 | 0.013733 | 0.045776 | -0.20142 | -0.054931 | -0.050354 | 122.9004 | 122.8821 | 59.0973 | -122.9736 | 122.9187 | 122.8546 | 59.1751 | -123.0515
209.0156 | 123.056 | -59.024 | 63.8718 | -0.35873 | 0.0070217 | 0.066541 | 0.068381 | 0.13206 | 0.0020593 | -0.0021641 | -0.19852 | -0.0018628 | 0.063196 | 0.061671 | 0.0033538 | -0.003215 | 63.7802 | 63.8992 | -0.041199 | -59.2438 | 63.913 | -59.079 | -59.1339 | -59.0332 | 0.059509 | -59.3308 | 63.913 | 63.8077 | -59.111 | -59.2438 | -0.054931 | -0.10986 | 0.041199 | 122.9233 | -0.21973 | -0.10986 | -0.091553 | -0.086975 | -0.21973 | 0.041199 | -0.009155 | -0.3067 | -0.086976 | -0.064087 | 122.937 | 122.8043 | 58.9828 | -123.0057 | 122.937 | 122.8317 | 59.0836 | -123.1155
210.0156 | 123.111 | -59.0103 | 63.8672 | -0.22141 | 0.0036039 | 0.066969 | 0.066672 | 0.13377 | -0.0019995 | -0.0038731 | -0.12222 | -0.0027174 | 0.061701 | 0.062312 | 0.00036322 | -0.0023606 | 63.8535 | 64.0091 | 0.064087 | -59.1797 | 63.8672 | -59.0332 | -59.1156 | -58.9737 | 0.14191 | -59.2438 | 63.858 | 63.8214 | -59.1019 | -59.198 | -0.022888 | -0.10529 | 0 | 123.0194 | -0.16937 | -0.064086 | -0.013732 | -0.091553 | -0.18768 | -0.009155 | 0.036621 | -0.23346 | -0.045776 | -0.045776 | 122.8775 | 122.8638 | 59.0744 | -122.9828 | 122.8683 | 122.8317 | 59.1522 | -123.0652
211.0156 | 123.0194 | -59.0652 | 63.8947 | -0.22903 | 0.0061673 | 0.071027 | 0.07009 | 0.13035 | -0.0013587 | -0.00088226 | -0.26718 | -0.0033582 | 0.062342 | 0.060176 | -6.4178e-05 | -0.003856 | 63.8626 | 63.8397 | -0.059509 | -59.2667 | 63.9267 | -59.0836 | -59.1385 | -59.0332 | 0.050354 | -59.3124 | 63.9221 | 63.7894 | -59.1339 | -59.2346 | -0.01831 | -0.073242 | 0.032044 | 122.905 | -0.20142 | -0.12817 | -0.032043 | -0.068664 | -0.16937 | 0.027466 | 0.032044 | -0.24719 | -0.07782 | -0.10528 | 122.9919 | 122.9279 | 59.0057 | -123.0331 | 122.9874 | 122.8546 | 59.1156 | -123.1293
212.0156 | 123.0881 | -59.0607 | 63.8489 | -0.16037 | 0.011294 | 0.067823 | 0.068808 | 0.13292 | 0.0035547 | -0.0040867 | -0.11459 | -0.00229 | 0.062982 | 0.060176 | 0.0029266 | -0.0070602 | 63.8306 | 63.945 | -0.013733 | -59.2072 | 63.9175 | -59.0698 | -59.1156 | -59.0149 | 0.064087 | -59.2987 | 63.8718 | 63.7939 | -59.1339 | -59.2346 | -0.009155 | -0.054932 | 0.068665 | 123.0057 | -0.14648 | -0.091552 | -0.018311 | -0.073242 | -0.17395 | 0.022888 | 0.045776 | -0.23804 | -0.064087 | -0.054932 | 122.9782 | 122.8912 | 59.0469 | -122.9645 | 122.9324 | 122.8546 | 59.1248 | -123.0835
213.0156 | 123.0515 | -59.0469 | 63.8718 | -0.24429 | 0.0059537 | 0.067396 | 0.070731 | 0.13398 | -0.0034949 | -0.00088226 | -0.16037 | -0.0027174 | 0.064051 | 0.06103 | -0.0011322 | -0.0027878 | 63.8397 | 63.9771 | 0.022888 | -59.1934 | 63.8672 | -59.0698 | -59.111 | -59.0195 | 0.11444 | -59.2667 | 63.9221 | 63.8168 | -59.111 | -59.2117 | -0.022888 | -0.064087 | -0.004578 | 123.024 | -0.14648 | -0.082397 | -0.032043 | -0.064087 | -0.16479 | 0.050354 | 0.027466 | -0.21973 | -0.054932 | -0.054932 | 122.9141 | 122.8867 | 59.0698 | -122.9828 | 122.9691 | 122.8638 | 59.1614 | -123.0835
214.0156 | 123.1201 | -59.0012 | 63.8626 | -0.2977 | 0.00018591 | 0.067396 | 0.069022 | 0.13206 | -0.0041357 | -0.0019505 | -0.091705 | -0.002931 | 0.060419 | 0.061885 | 0.0014312 | -0.002147 | 63.8489 | 64.0366 | 0.091553 | -59.1934 | 63.826 | -59.0469 | -59.1064 | -58.9508 | 0.17395 | -59.2072 | 63.8489 | 63.7665 | -59.1064 | -59.2026 | -0.045776 | -0.10529 | -0.036621 | 123.0377 | -0.19226 | -0.086975 | -0.013733 | -0.10529 | -0.20142 | -0.013733 | 0.050354 | -0.20599 | -0.004577 | -0.096131 | 122.8271 | 122.85 | 59.0927 | -122.9691 | 122.85 | 122.7676 | 59.1751 | -123.0652
215.0156 | 123.056 | -59.0332 | 63.858 | -0.19089 | 0.0080899 | 0.067823 | 0.070944 | 0.13121 | 0.00077755 | -0.0040867 | -0.14511 | -0.00229 | 0.064264 | 0.062312 | 0.0029266 | -0.0012924 | 63.7894 | 63.8901 | -0.018311 | -59.23 | 63.9084 | -59.0881 | -59.1248 | -59.0286 | 0.041199 | -59.3124 | 63.9267 | 63.8168 | -59.1339 | -59.23 | -0.054932 | -0.091553 | 0.050354 | 122.9233 | -0.19684 | -0.10529 | -0.068664 | -0.10071 | -0.19684 | 0.068665 | 0.004578 | -0.27924 | -0.082397 | -0.041199 | 122.9416 | 122.8226 | 59.0149 | -122.9828 | 122.9599 | 122.85 | 59.0744 | -123.0881
216.0156 | 123.0606 | -59.0195 | 63.8397 | -0.22903 | 0.0018949 | 0.065901 | 0.067954 | 0.13142 | -0.0034949 | -0.00066866 | -0.11459 | -0.003999 | 0.059992 | 0.063166 | 0.002713 | -0.0036424 | 63.8443 | 63.9999 | 0.059509 | -59.1934 | 63.8626 | -59.0561 | -59.1293 | -58.9966 | 0.12817 | -59.2255 | 63.8855 | 63.7848 | -59.111 | -59.2255 | -0.036621 | -0.10986 | 0.022888 | 123.0194 | -0.17395 | -0.064087 | 0.004577 | -0.091553 | -0.20599 | 0.045776 | 0.022888 | -0.20599 | 0 | -0.054932 | 122.8821 | 122.8638 | 59.079 | -122.9691 | 122.905 | 122.8043 | 59.1476 | -123.0652
217.0156 | 123.1842 | -59.0561 | 63.7939 | 0.19058 | 0.0078763 | 0.067396 | 0.069022 | 0.1295 | 0.00077755 | -0.0015231 | 0.22873 | -0.0042126 | 0.062555 | 0.063166 | 0.0022858 | -0.003215 | 63.9038 | 63.7436 | -0.091553 | -59.1202 | 63.8123 | -59.0881 | -59.0973 | -58.9783 | 0.032043 | -59.2529 | 63.8123 | 63.7161 | -59.1385 | -59.23 | -0.032044 | -0.041199 | 0.018311 | 122.7997 | -0.064087 | -0.022888 | 0.10986 | -0.082398 | -0.17395 | 0.018311 | 0.07782 | -0.19684 | -0.022888 | -0.07782 | 122.8683 | 122.9599 | 58.9645 | -122.8912 | 122.8683 | 122.7722 | 59.0881 | -123.024
218.0156 | 123.1293 | -59.024 | 63.8626 | -0.17563 | 0.0059537 | 0.067182 | 0.069235 | 0.13035 | -0.0017859 | -0.0019505 | -0.12222 | -0.0061352 | 0.06106 | 0.060603 | 0.0012176 | -0.0040696 | 63.8672 | 64.0091 | 0.064087 | -59.1751 | 63.8672 | -59.0424 | -59.0881 | -58.9462 | 0.14648 | -59.2255 | 63.8626 | 63.8077 | -59.1064 | -59.2209 | -0.01831 | -0.064087 | 0.004577 | 123.0331 | -0.15106 | -0.086975 | 0.004577 | -0.082397 | -0.19684 | 0 | 0.07782 | -0.20142 | -0.004578 | -0.054932 | 122.8912 | 122.8912 | 59.0881 | -122.9507 | 122.8867 | 122.8317 | 59.1705 | -123.0835
219.0156 | 123.0469 | -59.0424 | 63.8718 | -0.23666 | 0.0065945 | 0.066328 | 0.067099 | 0.13099 | 0.0014185 | -0.0028049 | -0.14511 | -0.0042126 | 0.064905 | 0.06103 | 0.00057682 | -0.0030014 | 63.8214 | 63.9542 | 0.022888 | -59.2209 | 63.9084 | -59.0607 | -59.1064 | -59.0378 | 0.07782 | -59.2941 | 63.8947 | 63.8077 | -59.1385 | -59.2209 | -0.018311 | -0.064087 | 0.036621 | 122.9965 | -0.17853 | -0.11444 | -0.050354 | -0.096131 | -0.17853 | 0.022888 | 0.004577 | -0.25177 | -0.073242 | -0.064087 | 122.9507 | 122.8638 | 59.0652 | -122.9782 | 122.937 | 122.85 | 59.1202 | -123.0927
220.0156 | 123.1796 | -59.024 | 63.826 | -0.10696 | 0.0021085 | 0.069105 | 0.066885 | 0.13121 | -0.0026405 | -0.0038731 | -0.10696 | -0.0048536 | 0.063196 | 0.059107 | -0.0011322 | -0.0019334 | 63.8901 | 64.0778 | 0.09613 | -59.1705 | 63.8763 | -59.0332 | -59.1019 | -59.0973 | -0.032043 | -59.1476 | 63.8763 | 63.7436 | -59.1064 | -59.2072 | -0.009155 | -0.07782 | 0.050354 | 123.1018 | -0.14648 | -0.068664 | 0.064087 | -0.082397 | -0.1831 | 0.050354 | -0.073242 | -0.1236 | 0.059509 | -0.082398 | 122.9004 | 122.9141 | 59.1202 | -122.9279 | 122.9004 | 122.7676 | 58.992 | -123.0331
221.0156 | 123.0927 | -59.0836 | 63.8535 | -0.21378 | 0.0078763 | 0.069959 | 0.069876 | 0.13185 | 0.0039819 | -0.0019505 | -0.19089 | -0.0025038 | 0.064264 | 0.060389 | 0.0037812 | -0.0051376 | 63.7985 | 63.8855 | -0.032043 | -59.23 | 63.8901 | -59.0836 | -59.1156 | -59.0469 | 0.064087 | -59.3308 | 63.8992 | 63.8214 | -59.1385 | -59.23 | 0 | -0.032044 | 0.036621 | 122.9691 | -0.14648 | -0.11444 | -0.054932 | -0.054932 | -0.14648 | 0.045776 | 0.036621 | -0.24719 | -0.10071 | -0.032044 | 122.9736 | 122.8821 | 59.0515 | -122.9691 | 122.9828 | 122.905 | 59.1476 | -123.0835
222.0156 | 123.0194 | -59.0652 | 63.8535 | 0.030365 | 0.0070217 | 0.064619 | 0.066245 | 0.13206 | 0.0022729 | -0.0019505 | 0.13718 | -0.00079476 | 0.064264 | 0.065303 | 0.0052764 | -0.0034286 | 63.7848 | 63.8443 | -0.12817 | -59.2392 | 63.8947 | -59.1202 | -59.1431 | -59.0881 | -0.073242 | -59.404 | 63.8763 | 63.7756 | -59.1797 | -59.2758 | -0.054931 | -0.077819 | 0.041198 | 122.9095 | -0.17395 | -0.096131 | -0.068665 | -0.11444 | -0.21057 | 0.022888 | -0.022888 | -0.33875 | -0.12817 | -0.07782 | 122.9599 | 122.85 | 58.9371 | -122.9965 | 122.9416 | 122.8409 | 58.992 | -123.1293
223.0156 | 123.056 | -59.0469 | 63.8809 | -0.21378 | 0.0074491 | 0.066541 | 0.069449 | 0.13121 | -7.6852e-05 | -0.0017369 | -0.084076 | -0.001222 | 0.062342 | 0.062098 | 0.0012176 | -0.0044968 | 63.7848 | 63.8855 | -0.041199 | -59.2346 | 63.8809 | -59.079 | -59.1293 | -59.0332 | 0.059509 | -59.3033 | 63.9267 | 63.8443 | -59.1064 | -59.2392 | -0.032043 | -0.082397 | 0 | 122.9324 | -0.18768 | -0.10529 | -0.09613 | -0.059509 | -0.19226 | 0.045777 | 0.013733 | -0.25635 | -0.064087 | -0.036621 | 122.9279 | 122.8317 | 59.0057 | -123.0103 | 122.9736 | 122.8912 | 59.1064 | -123.1201
224.0156 | 123.0469 | -59.0378 | 63.8809 | -0.22141 | 0.0040311 | 0.068037 | 0.067954 | 0.13099 | -0.0037085 | -0.0013095 | -0.12985 | -0.0050672 | 0.061487 | 0.063166 | 0.00036322 | -0.00086517 | 63.8489 | 63.9908 | 0.041199 | -59.1934 | 63.8718 | -59.0698 | -59.1293 | -59.0195 | 0.10529 | -59.2758 | 63.8992 | 63.8168 | -59.1248 | -59.2209 | -0.032043 | -0.091552 | -0.009155 | 123.0286 | -0.15564 | -0.064087 | -0.032043 | -0.086975 | -0.1831 | 0.018311 | 0.018311 | -0.23804 | -0.054932 | -0.064087 | 122.9095 | 122.8867 | 59.079 | -123.0103 | 122.937 | 122.8546 | 59.1431 | -123.1018
225.0156 | 123.0835 | -59.0515 | 63.8855 | -0.24429 | 0.0065945 | 0.066755 | 0.07009 | 0.13377 | 0.0029137 | -0.00088226 | -0.10696 | -0.0020764 | 0.063837 | 0.06103 | 0.0012176 | -0.0034286 | 63.7756 | 63.8809 | -0.045776 | -59.2346 | 63.9359 | -59.0881 | -59.1476 | -59.0424 | 0.064087 | -59.2987 | 63.8901 | 63.7894 | -59.1156 | -59.23 | -0.036621 | -0.09613 | 0.050354 | 122.9324 | -0.18311 | -0.086975 | -0.10986 | -0.064087 | -0.17853 | 0.004578 | 0.009156 | -0.24719 | -0.068664 | -0.09613 | 122.9874 | 122.8271 | 59.0057 | -123.0331 | 122.9416 | 122.8409 | 59.1156 | -123.1155
226.0156 | 123.1155 | -59.0057 | 63.8123 | -0.23666 | 0.0053129 | 0.066755 | 0.068594 | 0.13206 | -0.0039221 | -0.0034457 | -0.076446 | -0.0018628 | 0.063196 | 0.064448 | 0.00057682 | -0.0040696 | 63.858 | 63.9999 | 0.086975 | -59.1888 | 63.8351 | -59.0469 | -59.1019 | -58.9645 | 0.17853 | -59.2117 | 63.8718 | 63.8077 | -59.0973 | -59.2209 | -0.041199 | -0.096131 | 0.022888 | 123.0057 | -0.18311 | -0.086975 | 0.045776 | -0.091553 | -0.21515 | 0.059509 | 0.041198 | -0.20599 | 0.009155 | -0.004578 | 122.8409 | 122.8638 | 59.0927 | -122.9141 | 122.8775 | 122.8134 | 59.1843 | -123.0331
227.0156 | 123.0423 | -59.024 | 63.8855 | -0.21378 | 0.0085171 | 0.06825 | 0.071585 | 0.13035 | -7.6852e-05 | -0.0021641 | 0.16769 | -0.0035718 | 0.064478 | 0.061457 | -0.0015594 | -0.0025742 | 63.7894 | 64.151 | 0.1831 | -59.3033 | 63.9359 | -59.0424 | -59.1202 | -59.0515 | 0.073242 | -59.317 | 63.9267 | 63.8351 | -59.1476 | -59.2484 | -0.01831 | -0.09613 | 0.050354 | 123.175 | -0.27924 | -0.18311 | -0.09613 | -0.1236 | -0.2243 | 0.041199 | -0.027466 | -0.29297 | -0.068665 | -0.050354 | 122.9599 | 122.8134 | 59.2072 | -123.0057 | 122.9507 | 122.8592 | 59.0973 | -123.1338
228.0156 | 123.0469 | -59.0286 | 63.8535 | -0.22903 | 0.0085171 | 0.068464 | 0.070944 | 0.12928 | -0.0026405 | -0.0019505 | -0.053558 | -0.0018628 | 0.063623 | 0.060603 | 0.0020722 | -0.0027878 | 63.858 | 63.7344 | -0.12817 | -59.2117 | 63.9084 | -59.0652 | -59.1522 | -59.0332 | 0.064087 | -59.3079 | 63.9267 | 63.8306 | -59.1431 | -59.2438 | -0.036622 | -0.1236 | 0.054931 | 122.7631 | -0.18311 | -0.059509 | 0.004577 | -0.11444 | -0.21515 | 0.073242 | -0.004578 | -0.27924 | -0.064087 | -0.022889 | 122.937 | 122.8867 | 58.9005 | -123.0057 | 122.9553 | 122.8592 | 59.0927 | -123.0972
229.0156 | 122.9645 | -59.0698 | 63.8443 | -0.11459 | 0.01044 | 0.067823 | 0.072653 | 0.1327 | 0.0020593 | -0.0019505 | -0.11459 | -0.0014356 | 0.063837 | 0.063166 | 0.0037812 | -0.0047104 | 63.8168 | 63.9542 | -0.004578 | -59.2163 | 63.8901 | -59.0652 | -59.1431 | -59.0057 | 0.059509 | -59.2987 | 63.8763 | 63.7939 | -59.111 | -59.2484 | 0.004577 | -0.073242 | 0.045777 | 123.024 | -0.14649 | -0.073243 | -0.027466 | -0.041199 | -0.17853 | 0.032044 | 0.064087 | -0.22888 | -0.050354 | -0.050354 | 122.9599 | 122.8867 | 59.0652 | -122.9874 | 122.9462 | 122.8638 | 59.1293 | -123.0927
230.0156 | 123.0331 | -59.0378 | 63.8626 | -0.17563 | 0.0059537 | 0.067396 | 0.066885 | 0.13313 | -0.0019995 | 0.0010403 | -0.15274 | -0.0035718 | 0.062982 | 0.06338 | 0.0012176 | -0.0025742 | 63.7527 | 63.913 | -0.027466 | -59.2484 | 63.8947 | -59.0698 | -59.1431 | -59.024 | 0.045776 | -59.3308 | 63.8992 | 63.8535 | -59.1293 | -59.2209 | -0.032043 | -0.10528 | 0.032043 | 122.9507 | -0.21057 | -0.10529 | -0.10986 | -0.091552 | -0.1831 | 0.036621 | 0.013733 | -0.29297 | -0.10986 | -0.009155 | 122.9324 | 122.7905 | 59.0103 | -123.0057 | 122.937 | 122.8912 | 59.0836 | -123.0835
231.0156 | 123.0423 | -59.0607 | 63.8489 | -0.061188 | 0.010867 | 0.066541 | 0.069022 | 0.13185 | 0.0016321 | -0.0021641 | -0.0077819 | -0.0020764 | 0.062982 | 0.061885 | 0.004422 | -0.0047104 | 63.8123 | 63.8947 | -0.036621 | -59.2529 | 63.858 | -59.0973 | -59.1293 | -59.024 | 0.009155 | -59.3216 | 63.8672 | 63.7939 | -59.1339 | -59.2392 | -0.036621 | -0.068664 | 0.009155 | 122.9553 | -0.19226 | -0.1236 | -0.036621 | -0.073242 | -0.17853 | 0.01831 | 0.036621 | -0.26093 | -0.082397 | -0.054932 | 122.9187 | 122.8729 | 59.024 | -122.9782 | 122.9279 | 122.8546 | 59.0698 | -123.0881
232.0156 | 123.0331 | -59.0469 | 63.8992 | -0.17563 | 0.0076627 | 0.066969 | 0.072653 | 0.12971 | -0.0022131 | -0.0023777 | -0.10696 | -0.0010084 | 0.063196 | 0.059962 | 0.0014312 | -0.0044968 | 63.7894 | 63.8947 | -0.036621 | -59.2392 | 63.9084 | -59.111 | -59.111 | -59.0424 | 0.050354 | -59.2941 | 63.9084 | 63.8626 | -59.1293 | -59.23 | -0.064087 | -0.064087 | 0.009155 | 122.9416 | -0.19226 | -0.12817 | -0.10986 | -0.082397 | -0.18311 | 0.009155 | 0.004578 | -0.24719 | -0.064086 | -0.036621 | 122.9553 | 122.8363 | 59.0103 | -123.0103 | 122.9553 | 122.9095 | 59.0973 | -123.1293
233.0156 | 123.0972 | -59.0515 | 63.8443 | -0.17563 | 0.0070217 | 0.064619 | 0.069663 | 0.13142 | 0.00056395 | -0.00066866 | -0.14511 | -0.0016492 | 0.063837 | 0.063594 | 0.002713 | -0.0051376 | 63.8168 | 63.9221 | -0.013733 | -59.2117 | 63.8901 | -59.0881 | -59.1202 | -58.9966 | 0.073242 | -59.285 | 63.8947 | 63.8443 | -59.1385 | -59.2346 | -0.036621 | -0.068664 | 0.045777 | 122.9736 | -0.16022 | -0.091553 | -0.027466 | -0.086975 | -0.18311 | 0.050354 | 0.054932 | -0.23346 | -0.050354 | 0 | 122.9416 | 122.8683 | 59.0378 | -122.9645 | 122.9462 | 122.8958 | 59.1248 | -123.0789
234.0156 | 123.0469 | -59.0424 | 63.8901 | -0.22141 | 0.0053129 | 0.069319 | 0.071799 | 0.1327 | -0.00093145 | -0.0030185 | -0.32059 | -0.0014356 | 0.062342 | 0.059962 | 0.0024994 | -0.0012924 | 63.7619 | 63.8443 | -0.045776 | -59.285 | 63.9038 | -59.1019 | -59.1431 | -59.024 | 0.045776 | -59.3079 | 63.9038 | 63.858 | -59.1385 | -59.2072 | -0.05951 | -0.10071 | 0.013733 | 122.8867 | -0.24262 | -0.14191 | -0.12817 | -0.096131 | -0.16479 | 0.013733 | 0.01831 | -0.2655 | -0.10071 | -0.032044 | 122.9462 | 122.8043 | 58.9966 | -123.0331 | 122.9462 | 122.9004 | 59.0881 | -123.0972
235.0156 | 123.0286 | -59.0561 | 63.8489 | 0.0074768 | 0.0091581 | 0.06526 | 0.070303 | 0.13185 | 0.00056395 | -0.00066866 | -0.00015237 | -0.0027174 | 0.063623 | 0.062312 | 0.0031402 | -0.0017196 | 63.7756 | 63.8535 | -0.086975 | -59.2712 | 63.8718 | -59.1019 | -59.1431 | -59.0652 | -0.018311 | -59.3719 | 63.8992 | 63.8214 | -59.1476 | -59.2346 | -0.045777 | -0.086975 | 0.022888 | 122.9095 | -0.21515 | -0.12817 | -0.073242 | -0.091553 | -0.17853 | 0.050354 | -0.009156 | -0.31586 | -0.13733 | -0.027466 | 122.9279 | 122.8317 | 58.9691 | -122.9919 | 122.9553 | 122.8775 | 59.0378 | -123.0835
236.0156 | 123.024 | -59.0561 | 63.8397 | -0.045929 | 0.012149 | 0.066328 | 0.071372 | 0.13014 | 0.00099115 | -0.00088226 | 0.030365 | -0.002931 | 0.067041 | 0.062953 | 0.002713 | -0.0025742 | 63.8077 | 63.913 | -0.050354 | -59.2392 | 63.8489 | -59.0881 | -59.1293 | -59.0195 | 0.004578 | -59.3399 | 63.858 | 63.7848 | -59.1476 | -59.2346 | -0.032044 | -0.073242 | 0.009155 | 122.9691 | -0.18311 | -0.10986 | -0.032044 | -0.091553 | -0.17853 | 0.01831 | 0.036621 | -0.28381 | -0.10529 | -0.054932 | 122.905 | 122.8638 | 59.0057 | -122.9691 | 122.9141 | 122.8409 | 59.0607 | -123.0743
237.0156 | 123.0194 | -59.0836 | 63.858 | 0.030365 | 0.013003 | 0.065473 | 0.068594 | 0.13313 | -0.00093145 | -0.00088226 | -0.015411 | -0.001222 | 0.064264 | 0.062739 | 0.0037812 | -0.0027878 | 63.7619 | 63.8351 | -0.11902 | -59.2712 | 63.8901 | -59.1156 | -59.1568 | -59.1019 | -0.07782 | -59.3948 | 63.8489 | 63.8214 | -59.1751 | -59.2667 | -0.032044 | -0.073242 | 0.032044 | 122.9187 | -0.18768 | -0.11444 | -0.09613 | -0.091553 | -0.18311 | -0.009155 | -0.018311 | -0.31128 | -0.12817 | -0.036621 | 122.9736 | 122.8455 | 58.9645 | -123.0148 | 122.9324 | 122.905 | 59.0057 | -123.1247
238.0156 | 123.0835 | -59.0424 | 63.8489 | 1.1824 | 0.0093717 | 0.065687 | 0.072867 | 0.13228 | -7.6852e-05 | -0.0025913 | -0.0077819 | -0.0037854 | 0.065332 | 0.061244 | 0.0039948 | -0.0027878 | 63.8672 | 63.9038 | -0.013733 | -59.2255 | 63.8901 | -59.0698 | -59.1431 | -59.024 | 0.059509 | -59.2941 | 63.8718 | 63.7848 | -59.1522 | -59.2529 | -0.027466 | -0.10071 | 0.041199 | 122.9462 | -0.18311 | -0.082398 | 0.01831 | -0.10986 | -0.21057 | 0.022888 | 0.01831 | -0.25177 | -0.041198 | -0.064087 | 122.9324 | 122.9095 | 59.0286 | -122.9919 | 122.9141 | 122.8271 | 59.1019 | -123.1018
239.0156 | 122.9874 | -59.0744 | 63.8535 | 0.12955 | 0.01044 | 0.067823 | 0.068594 | 0.13121 | 0.0029137 | -0.0013095 | 0.14481 | -0.00079476 | 0.063837 | 0.06103 | 0.00057682 | -0.0027878 | 63.7299 | 63.8168 | -0.15106 | -59.3079 | 63.9038 | -59.1064 | -59.1568 | -59.079 | -0.064087 | -59.6466 | 63.7985 | 63.7299 | -59.1888 | -59.2712 | -0.032043 | -0.082397 | 0.050354 | 122.8912 | -0.23346 | -0.15106 | -0.1236 | -0.11444 | -0.19684 | -0.054932 | -0.004577 | -0.5722 | -0.37537 | -0.1236 | 122.9782 | 122.8043 | 58.9233 | -123.0103 | 122.8729 | 122.8043 | 59.0103 | -123.1247
240.0156 | 123.0881 | -59.0515 | 63.8397 | -0.0383 | 0.011081 | 0.06761 | 0.072012 | 0.13099 | 0.0012047 | -0.0049411 | -0.03067 | -0.0027174 | 0.063196 | 0.062953 | 0.0022858 | -0.0030014 | 63.8123 | 63.913 | -0.027466 | -59.2346 | 63.8443 | -59.079 | -59.1339 | -59.0286 | 0.018311 | -59.3124 | 63.8809 | 63.8031 | -59.1431 | -59.2346 | -0.027465 | -0.082397 | 0.004577 | 122.9645 | -0.18311 | -0.10071 | -0.027466 | -0.091552 | -0.18311 | 0.041198 | 0.022889 | -0.26093 | -0.07782 | -0.036621 | 122.8958 | 122.8638 | 59.024 | -122.9736 | 122.9324 | 122.8546 | 59.0698 | -123.0743
241.0156 | 123.0057 | -59.0881 | 63.8443 | 0.076141 | 0.010226 | 0.066755 | 0.072653 | 0.13035 | -0.00050425 | -0.0013095 | 0.0914 | -0.00079476 | 0.063837 | 0.062525 | 0.0029266 | -0.001506 | 63.7665 | 63.8626 | -0.091553 | -59.2712 | 63.8718 | -59.1019 | -59.1476 | -59.0698 | -0.013733 | -59.3857 | 63.8901 | 63.8351 | -59.1339 | -59.2575 | -0.013733 | -0.059509 | 0.027466 | 122.9507 | -0.1831 | -0.1236 | -0.07782 | -0.045776 | -0.16937 | 0.045777 | 0.018311 | -0.29755 | -0.12817 | -0.009155 | 122.9599 | 122.8546 | 58.9966 | -122.9919 | 122.9782 | 122.9233 | 59.0744 | -123.1018
242.0156 | 123.024 | -59.0836 | 63.8397 | 0.037994 | 0.010653 | 0.068678 | 0.070303 | 0.13313 | 0.0027001 | -0.0032321 | 0.0914 | -0.0020764 | 0.067041 | 0.06103 | 0.0016448 | -0.0025742 | 63.7619 | 63.8535 | -0.10071 | -59.2667 | 63.8763 | -59.111 | -59.1522 | -59.1019 | -0.059509 | -59.3857 | 63.8855 | 63.8306 | -59.1568 | -59.2758 | -0.027466 | -0.068665 | 0.036621 | 122.937 | -0.18311 | -0.11444 | -0.07782 | -0.073242 | -0.19226 | 0.045776 | -0.018311 | -0.30212 | -0.10986 | -0.009156 | 122.9599 | 122.8455 | 58.9828 | -122.9919 | 122.9691 | 122.9141 | 59.024 | -123.1155
243.0156 | 123.1018 | -59.0469 | 63.7756 | 0.14481 | 0.0087307 | 0.068678 | 0.069663 | 0.12864 | -0.0011451 | -0.0017369 | 0.26688 | -0.0025038 | 0.061701 | 0.060603 | 0.0018584 | -0.00043797 | 63.7253 | 63.8489 | -0.13275 | -59.2712 | 63.8443 | -59.111 | -59.1248 | -59.0332 | -0.050354 | -59.3124 | 63.8718 | 63.7756 | -59.1339 | -59.2575 | -0.064087 | -0.07782 | 0.068664 | 122.8958 | -0.2243 | -0.14648 | -0.050354 | -0.086975 | -0.21057 | 0.09613 | 0.013733 | -0.2655 | -0.054932 | 0 | 122.8912 | 122.7722 | 58.9142 | -122.9004 | 122.9187 | 122.8226 | 58.9966 | -123.0331
244.0156 | 123.024 | -59.0698 | 63.8168 | 0.037994 | 0.0093717 | 0.067823 | 0.07009 | 0.13142 | -0.00029045 | -0.0019505 | 0.14481 | -0.0042126 | 0.066828 | 0.061671 | 0.0020722 | -0.0036424 | 63.739 | 63.8214 | -0.11444 | -59.2896 | 63.858 | -59.1019 | -59.1431 | -59.111 | -0.086975 | -59.3857 | 63.8901 | 63.826 | -59.1843 | -59.2621 | -0.032044 | -0.073242 | 0.041199 | 122.8912 | -0.21973 | -0.14649 | -0.077819 | -0.11444 | -0.19226 | 0.073243 | -0.041199 | -0.31586 | -0.1236 | 0.009156 | 122.9279 | 122.8088 | 58.9554 | -122.9599 | 122.9599 | 122.8958 | 58.9828 | -123.0789
245.0156 | 123.1018 | -59.0515 | 63.7985 | 0.18295 | 0.0087307 | 0.066328 | 0.070303 | 0.13185 | -0.0011451 | -0.00088226 | 0.26688 | -0.00079476 | 0.064478 | 0.063166 | 0.0016448 | -0.0017196 | 63.7573 | 63.8535 | -0.13275 | -59.2575 | 63.858 | -59.0927 | -59.1431 | -59.0149 | -0.045776 | -59.3124 | 63.8489 | 63.7848 | -59.1385 | -59.2392 | -0.041198 | -0.091552 | 0.059509 | 122.905 | -0.20599 | -0.11444 | -0.041199 | -0.086975 | -0.18768 | 0.050354 | 0.036621 | -0.26093 | -0.073242 | -0.013733 | 122.9095 | 122.8088 | 58.9188 | -122.9416 | 122.9004 | 122.8363 | 59.0057 | -123.0377
246.0156 | 123.1705 | -59.1064 | 63.8443 | 0.022736 | 0.0091581 | 0.064619 | 0.071585 | 0.13206 | 0.0016321 | -0.0025913 | 0.12955 | -0.0018628 | 0.065119 | 0.062312 | 0.0018584 | -0.0040696 | 63.7115 | 63.8031 | -0.13275 | -59.285 | 63.8855 | -59.0927 | -59.166 | -59.1156 | -0.086975 | -59.3719 | 63.8763 | 63.8351 | -59.1888 | -59.285 | 0.013733 | -0.05951 | 0.041199 | 122.9095 | -0.17853 | -0.11902 | -0.13275 | -0.082398 | -0.17853 | 0.032044 | -0.009156 | -0.2655 | -0.086975 | -0.009155 | 122.9919 | 122.818 | 58.9737 | -123.0103 | 122.9828 | 122.9416 | 59.0195 | -123.1293
247.0156 | 123.0652 | -59.0836 | 63.8123 | 0.068512 | 0.0087307 | 0.065901 | 0.068167 | 0.13014 | -0.00029045 | -0.0032321 | 0.18295 | -0.0014356 | 0.065119 | 0.062098 | -0.00049138 | -0.001506 | 63.739 | 63.8306 | -0.14191 | -59.2758 | 63.8489 | -59.111 | -59.1568 | -59.0424 | -0.082397 | -59.3674 | 63.8443 | 63.8123 | -59.1705 | -59.2667 | -0.027466 | -0.073242 | 0.036621 | 122.9141 | -0.19226 | -0.11902 | -0.073242 | -0.086975 | -0.18311 | 0.032043 | 0.041199 | -0.28381 | -0.10071 | 0 | 122.9324 | 122.8226 | 58.9416 | -122.9691 | 122.9279 | 122.8958 | 59.0012 | -123.0789
248.0156 | 122.9782 | -59.079 | 63.858 | 0.060882 | 0.0097989 | 0.067182 | 0.07009 | 0.13163 | 0.00099115 | -0.0023777 | 0.17532 | -0.001222 | 0.067041 | 0.062739 | 0.0048492 | -0.001506 | 63.7207 | 63.7848 | -0.16022 | -59.2941 | 63.8855 | -59.1019 | -59.1476 | -59.2346 | 0.3891 | -59.3216 | 63.8855 | 63.8123 | -59.1339 | -59.2667 | -0.022889 | -0.068665 | 0.027466 | 122.8638 | -0.21515 | -0.14648 | -0.13733 | -0.054932 | -0.18768 | 0.027466 | -0.15564 | -0.24262 | -0.054931 | -0.045776 | 122.9645 | 122.7997 | 58.9188 | -123.0057 | 122.9645 | 122.8912 | 59.4681 | -123.1247
249.0156 | 123.1338 | -59.0378 | 63.7848 | 0.12955 | 0.0036039 | 0.066755 | 0.067099 | 0.13185 | -0.0058447 | -0.0017369 | 0.31265 | -0.0042126 | 0.063196 | 0.061457 | 0.0014312 | -0.0036424 | 63.826 | 63.9313 | -0.032043 | -59.23 | 63.7848 | -59.1064 | -59.1202 | -58.9874 | 0.009155 | -59.2621 | 63.8031 | 63.7985 | -59.1385 | -59.2484 | -0.068664 | -0.082397 | 0 | 122.9691 | -0.19226 | -0.10986 | 0.041199 | -0.10071 | -0.21057 | 0.018311 | 0.050354 | -0.2243 | -0.013733 | 0.013733 | 122.8226 | 122.8638 | 59.0057 | -122.905 | 122.8409 | 122.8363 | 59.0469 | -123.0331
250.0156 | 123.0606 | -59.079 | 63.8214 | 0.045624 | 0.0095853 | 0.065046 | 0.071372 | 0.13014 | -0.00050425 | -0.0013095 | 0.28214 | -0.0018628 | 0.064051 | 0.060816 | 0.0022858 | -0.0044968 | 63.7619 | 63.8168 | -0.13275 | -59.2896 | 63.8535 | -59.1156 | -59.1476 | -59.0424 | -0.07782 | -59.3353 | 63.8626 | 63.7985 | -59.1705 | -59.2392 | -0.036622 | -0.068665 | 0.032044 | 122.8958 | -0.21057 | -0.14191 | -0.059509 | -0.091553 | -0.16022 | 0.041199 | 0.036621 | -0.25635 | -0.09613 | -0.022888 | 122.9324 | 122.8409 | 58.9462 | -122.9691 | 122.9416 | 122.8775 | 59.0012 | -123.0606
251.0156 | 123.1567 | -59.0515 | 63.7756 | 0.20584 | 0.0091581 | 0.06526 | 0.072012 | 0.13057 | -0.0013587 | -0.0051547 | 0.24399 | -0.00229 | 0.065332 | 0.06338 | 0.0033538 | -0.0010788 | 63.8306 | 64.0182 | -0.013733 | -59.2255 | 63.8031 | -59.0515 | -59.1248 | -58.9508 | 0.036621 | -59.2392 | 63.8123 | 63.7711 | -59.1522 | -59.2209 | 0 | -0.073242 | 0.027466 | 123.0698 | -0.17395 | -0.10071 | 0.054931 | -0.10071 | -0.16937 | 0.036621 | 0.10071 | -0.18768 | -0.018311 | -0.004578 | 122.8546 | 122.8821 | 59.0378 | -122.9004 | 122.8638 | 122.8226 | 59.0881 | -122.9965
252.0156 | 123.0835 | -59.0744 | 63.8214 | 0.14481 | 0.0093717 | 0.066328 | 0.068808 | 0.13142 | 0.00035035 | -0.0032321 | 0.20584 | -0.0027174 | 0.064051 | 0.064234 | 0.0029266 | -0.003215 | 63.7756 | 63.8306 | -0.14191 | -59.285 | 63.8672 | -59.1064 | -59.1522 | -59.0286 | -0.064087 | -59.3308 | 63.8489 | 63.7802 | -59.1431 | -59.2621 | -0.032043 | -0.07782 | 0.045776 | 122.905 | -0.21057 | -0.13275 | -0.045776 | -0.068664 | -0.18768 | 0.027466 | 0.045777 | -0.25635 | -0.068665 | -0.041199 | 122.9416 | 122.85 | 58.9325 | -122.9736 | 122.9233 | 122.8546 | 59.0103 | -123.0835
253.0156 | 123.1705 | -59.0103 | 63.7756 | 0.60257 | 0.0050991 | 0.06761 | 0.068167 | 0.13228 | -0.0013587 | -0.0013095 | 0.28214 | -0.0025038 | 0.063196 | 0.061457 | 0.0033538 | -0.0053512 | 63.8626 | 63.9359 | -0.041199 | -59.2209 | 63.8214 | -59.0652 | -59.1476 | -58.9645 | 0.018311 | -59.2438 | 63.8306 | 63.7756 | -59.1156 | -59.23 | -0.054932 | -0.13733 | 0.045776 | 122.9462 | -0.21057 | -0.073242 | 0.086975 | -0.10529 | -0.21973 | 0.054931 | 0.045776 | -0.23346 | -0.013732 | 0 | 122.8317 | 122.8729 | 58.9691 | -122.9233 | 122.8409 | 122.7859 | 59.0286 | -123.0057
254.0156 | 123.0743 | -59.0561 | 63.8123 | 3.5017 | 0.011294 | 0.067823 | 0.07244 | 0.13185 | 0.0044091 | -0.0019505 | 0.068512 | -0.002931 | 0.063196 | 0.063166 | 0.0050628 | -0.004924 | 63.8214 | 63.8123 | -0.14191 | -59.3033 | 63.8763 | -59.0927 | -59.1705 | -59.0652 | -0.10071 | -59.3582 | 63.8763 | 63.8031 | -59.1522 | -59.2438 | -0.036621 | -0.11444 | 0.064087 | 122.8683 | -0.24719 | -0.13275 | 0.009155 | -0.096131 | -0.18768 | 0.064087 | -0.009156 | -0.30212 | -0.11444 | -0.009155 | 122.9324 | 122.8775 | 58.9142 | -122.9828 | 122.9324 | 122.8592 | 58.9554 | -123.056
255.0156 | 123.1201 | -59.0561 | 63.7665 | 0.16006 | 0.0070217 | 0.065901 | 0.066672 | 0.13121 | 0.0012047 | -0.0030185 | 0.26688 | -0.001222 | 0.062982 | 0.061885 | 0.0022858 | -0.0023606 | 63.858 | 63.9313 | -0.064087 | -59.2026 | 63.8306 | -59.079 | -59.1431 | -58.96 | 0.009155 | -59.2484 | 63.7939 | 63.7711 | -59.1431 | -59.2255 | -0.022888 | -0.086975 | 0.064087 | 122.9874 | -0.14648 | -0.05951 | 0.091553 | -0.086975 | -0.16937 | 0.027466 | 0.09613 | -0.19226 | -0.022888 | 0.004578 | 122.8867 | 122.9141 | 58.992 | -122.9095 | 122.85 | 122.8271 | 59.0652 | -122.9919
256.0156 | 123.2574 | -59.0652 | 63.7802 | 0.12192 | 0.0080899 | 0.067396 | 0.066245 | 0.13313 | -0.0013587 | 0.00018594 | 0.19821 | -0.0033582 | 0.064051 | 0.063807 | 0.0037812 | -0.0034286 | 63.8443 | 63.9313 | -0.059509 | -59.2255 | 63.8168 | -59.0515 | -59.1339 | -58.96 | 0.018311 | -59.2712 | 63.8123 | 63.7115 | -59.1568 | -59.285 | 0.013733 | -0.068664 | 0.036621 | 122.9965 | -0.16022 | -0.091553 | 0.064087 | -0.091552 | -0.21973 | 0.032044 | 0.10529 | -0.20599 | 0.013733 | -0.068664 | 122.8821 | 122.9095 | 59.0057 | -122.9141 | 122.8775 | 122.7768 | 59.0836 | -123.0652
257.0156 | 123.1247 | -59.0378 | 63.7985 | 0.045624 | 0.0027493 | 0.06761 | 0.068594 | 0.13057 | -0.0058447 | -0.0036595 | 0.17532 | -0.0052808 | 0.061914 | 0.062953 | 0.001004 | -0.0034286 | 63.7894 | 63.9221 | -0.054932 | -59.2438 | 63.8306 | -59.0698 | -59.111 | -58.9508 | -0.050354 | -59.2712 | 63.8123 | 63.7939 | -59.1202 | -59.2346 | -0.032043 | -0.073242 | 0.032043 | 122.9599 | -0.20599 | -0.13275 | -0.009155 | -0.082397 | -0.19684 | 0.013733 | 0.086975 | -0.23346 | -0.036621 | -0.004578 | 122.8683 | 122.8271 | 58.9828 | -122.9095 | 122.85 | 122.8317 | 58.9874 | -123.0331
258.0156 | 123.143 | -59.0103 | 63.7894 | 0.33554 | 0.010013 | 0.06526 | 0.068808 | 0.13206 | 0.0018457 | -0.0032321 | 0.25925 | -0.003999 | 0.059778 | 0.062312 | 0.0016448 | -0.005565 | 63.858 | 63.9267 | -0.045776 | -59.2163 | 63.8123 | -59.0973 | -59.1156 | -58.9645 | 0.018311 | -59.2758 | 63.7985 | 63.7299 | -59.198 | -59.2529 | -0.086975 | -0.10529 | 0.022888 | 122.937 | -0.20599 | -0.10071 | 0.068664 | -0.18768 | -0.24262 | 0.009155 | 0.045776 | -0.2655 | -0.022888 | -0.05951 | 122.8226 | 122.8683 | 58.9645 | -122.905 | 122.8088 | 122.7402 | 59.0286 | -123.0423
259.0156 | 123.1247 | -59.0286 | 63.7894 | 0.15244 | 0.0068081 | 0.066328 | 0.067099 | 0.13014 | -0.0026405 | -0.0021641 | 0.27451 | -0.0061352 | 0.064051 | 0.06103 | 0.00036322 | -0.003215 | 63.8306 | 63.9404 | -0.027466 | -59.2346 | 63.826 | -59.0652 | -59.1156 | -58.992 | 0.018311 | -59.2667 | 63.8306 | 63.7619 | -59.1156 | -59.2484 | -0.036622 | -0.086976 | 0.036621 | 122.9691 | -0.20599 | -0.11902 | 0.041198 | -0.086976 | -0.21973 | 0.041198 | 0.036621 | -0.23804 | -0.018311 | -0.027466 | 122.8546 | 122.8592 | 59.0012 | -122.905 | 122.8592 | 122.7905 | 59.0469 | -123.0377
260.0156 | 123.1018 | -59.0607 | 63.7894 | 0.15244 | 0.0093717 | 0.066969 | 0.067313 | 0.12864 | 0.0018457 | -0.0017369 | 0.19058 | -0.0027174 | 0.064051 | 0.062312 | 0.0031402 | -0.0053512 | 63.7939 | 63.8489 | -0.11902 | -59.2575 | 63.8626 | -59.1156 | -59.1431 | -59.0057 | -0.045776 | -59.3124 | 63.8535 | 63.7573 | -59.1522 | -59.2209 | -0.054932 | -0.082397 | 0.073242 | 122.9095 | -0.19684 | -0.11444 | 0.004577 | -0.091553 | -0.16022 | 0.064087 | 0.054932 | -0.25177 | -0.091553 | -0.032044 | 122.9233 | 122.8546 | 58.9416 | -122.9324 | 122.9141 | 122.818 | 59.0149 | -123.0103
261.0156 | 123.1979 | -59.0424 | 63.7802 | 0.38895 | 0.0029629 | 0.067396 | 0.066458 | 0.13142 | -0.0024269 | -0.0017369 | 0.22873 | -0.0018628 | 0.061914 | 0.062739 | 0.0042084 | -0.0040696 | 63.8443 | 63.9359 | -0.036621 | -59.2209 | 63.8031 | -59.0744 | -59.1202 | -58.9462 | 0.032043 | -59.2484 | 63.8123 | 63.7527 | -59.1202 | -59.2438 | -0.032044 | -0.07782 | 0.022889 | 122.9782 | -0.17853 | -0.10071 | 0.064087 | -0.07782 | -0.20142 | 0.032044 | 0.09613 | -0.20599 | -0.004578 | -0.027465 | 122.8455 | 122.8867 | 59.0057 | -122.9004 | 122.8546 | 122.7951 | 59.0744 | -123.024
262.0156 | 123.0606 | -59.0424 | 63.7115 | 0.16769 | 0.0057401 | 0.066541 | 0.066672 | 0.13185 | 0.0031273 | -0.0023777 | 0.17532 | -0.003999 | 0.06341 | 0.061885 | 0.0042084 | -0.0051376 | 63.858 | 63.9587 | -0.050354 | -59.2117 | 63.8168 | -59.0973 | -59.1248 | -58.9462 | 0.032043 | -59.2621 | 63.8306 | 63.7299 | -59.1522 | -59.2392 | -0.054932 | -0.082398 | 0.10529 | 123.0011 | -0.16937 | -0.086975 | 0.14648 | -0.10986 | -0.19684 | 0.11902 | 0.09613 | -0.21973 | -0.022888 | 0.01831 | 122.8592 | 122.9004 | 58.992 | -122.8363 | 122.8729 | 122.7722 | 59.0744 | -122.9507
263.0156 | 123.0698 | -59.0378 | 63.8214 | 0.060882 | 0.0023221 | 0.065687 | 0.067313 | 0.13142 | -0.0047767 | -0.0023777 | 0.17532 | -0.0050672 | 0.061701 | 0.060389 | 0.0020722 | -0.0030014 | 63.7985 | 63.913 | -0.050354 | -59.2255 | 63.8489 | -59.0515 | -59.1293 | -58.992 | 0.036621 | -59.1064 | 63.8626 | 63.826 | -59.1202 | -59.2163 | -0.013733 | -0.091552 | 0.027466 | 122.9507 | -0.18768 | -0.096131 | -0.022888 | -0.082397 | -0.17853 | 0.041199 | 0.045777 | -0.068664 | 0.10986 | 0.004578 | 122.8867 | 122.8363 | 58.9874 | -122.9507 | 122.9004 | 122.8638 | 59.0744 | -123.0377
264.0156 | 123.1476 | -59.0286 | 63.7985 | -1.2132 | 0.0065945 | 0.065687 | 0.068594 | 0.13292 | -0.00071785 | -0.0028049 | 0.28214 | -0.003999 | 0.063837 | 0.061671 | 0.0022858 | -0.0042832 | 63.8397 | 63.9862 | -0.009155 | -59.2072 | 63.8168 | -59.0332 | -59.1156 | -58.9417 | 0.036621 | -59.2392 | 63.8214 | 63.7344 | -59.1568 | -59.2346 | -0.004578 | -0.086976 | 0.01831 | 123.0148 | -0.17853 | -0.091552 | 0.041199 | -0.12817 | -0.20599 | 0.022888 | 0.086975 | -0.21057 | -0.004578 | -0.064087 | 122.8455 | 122.8683 | 59.0195 | -122.9141 | 122.85 | 122.7631 | 59.0652 | -123.0331
265.0156 | 123.0881 | -58.9966 | 63.8489 | 0.17532 | 0.0040311 | 0.068464 | 0.067526 | 0.13249 | -0.0026405 | -0.0040867 | 0.11429 | -0.0052808 | 0.062342 | 0.062525 | 0.0012176 | -0.0023606 | 63.8123 | 63.9175 | -0.050354 | -59.2529 | 63.8489 | -59.0836 | -59.1202 | -58.9874 | 0.022888 | -59.2804 | 63.8489 | 63.7665 | -59.111 | -59.23 | -0.086975 | -0.1236 | 0 | 122.9141 | -0.25635 | -0.13275 | -0.036621 | -0.11444 | -0.23346 | 0 | 0.009155 | -0.28381 | -0.050354 | -0.082398 | 122.8455 | 122.8088 | 58.9462 | -122.9691 | 122.8455 | 122.7631 | 59.0195 | -123.0789
266.0156 | 123.1293 | -59.0332 | 63.7894 | 0.19058 | 0.0085171 | 0.065046 | 0.067954 | 0.13057 | 0.0018457 | -2.7856e-05 | 0.21347 | -0.00464 | 0.062342 | 0.061885 | 0.0039948 | -0.0051376 | 63.6932 | 64.183 | 0.10071 | -59.2072 | 63.8214 | -59.0607 | -59.1293 | -58.9417 | 0.027466 | -59.2346 | 63.8123 | 63.7344 | -59.1476 | -59.2255 | -0.027466 | -0.09613 | 0.032043 | 123.2162 | -0.17395 | -0.07782 | -0.096131 | -0.11444 | -0.19226 | 0.022888 | 0.091553 | -0.20142 | -0.009155 | -0.054932 | 122.8546 | 122.7264 | 59.1339 | -122.9187 | 122.8455 | 122.7676 | 59.0607 | -123.0148
267.0156 | 123.1384 | -59.0195 | 63.7985 | 0.12955 | 0.0031765 | 0.06526 | 0.066458 | 0.12971 | -0.0011451 | -0.0025913 | 0.09903 | -0.003999 | 0.062555 | 0.062312 | 0.0024994 | -0.004924 | 63.8077 | 63.9175 | -0.054932 | -59.2484 | 63.8443 | -59.0927 | -59.1019 | -58.9828 | 0.018311 | -59.2667 | 63.8214 | 63.7665 | -59.1248 | -59.2346 | -0.073242 | -0.082398 | 0.045776 | 122.937 | -0.22888 | -0.14648 | 0.009155 | -0.10529 | -0.21515 | 0.022888 | 0.036621 | -0.24719 | -0.032044 | -0.032044 | 122.8638 | 122.8271 | 58.9645 | -122.9004 | 122.8409 | 122.7859 | 59.0378 | -123.0331
268.0156 | 123.1522 | -59.0424 | 63.7756 | 0.18295 | 0.0091581 | 0.064405 | 0.069235 | 0.13206 | 0.0031273 | -2.7856e-05 | 0.19058 | 5.9836e-05 | 0.06341 | 0.061457 | 0.00549 | -0.004924 | 63.7894 | 63.8763 | -0.11444 | -59.2621 | 63.8397 | -59.1019 | -59.1476 | -58.9691 | -0.009155 | -59.285 | 63.8168 | 63.7344 | -59.166 | -59.23 | -0.05951 | -0.10529 | 0.064087 | 122.9187 | -0.21973 | -0.11444 | 0.013733 | -0.1236 | -0.18768 | 0.041198 | 0.073242 | -0.24262 | -0.054931 | -0.041199 | 122.8821 | 122.8317 | 58.9279 | -122.9233 | 122.8592 | 122.7768 | 59.0332 | -123.0057
269.0156 | 123.0881 | -59.0424 | 63.8123 | 0.12955 | 0.0027493 | 0.068891 | 0.068381 | 0.12907 | -0.0019995 | -0.0019505 | 0.2211 | -0.0042126 | 0.062769 | 0.062739 | -0.0015594 | -0.0057786 | 63.8168 | 63.9404 | -0.041199 | -59.2529 | 63.8306 | -59.0836 | -59.1202 | -58.9645 | 0.004578 | -59.2758 | 63.8214 | 63.7299 | -59.111 | -59.2163 | -0.041199 | -0.07782 | 0.01831 | 122.9828 | -0.21057 | -0.13275 | 0.004577 | -0.068665 | -0.17395 | 0.009155 | 0.077819 | -0.23346 | -0.059509 | -0.082398 | 122.8729 | 122.8592 | 59.0012 | -122.9324 | 122.8638 | 122.7722 | 59.0469 | -123.0286
270.0156 | 123.1705 | -59.0332 | 63.7894 | 0.14481 | 0.0072355 | 0.06761 | 0.068381 | 0.12928 | -0.0011451 | -0.0010959 | 0.19058 | -0.003999 | 0.064478 | 0.060816 | 0.0014312 | -0.0051376 | 63.8443 | 63.9633 | -0.018311 | -59.2163 | 63.8123 | -59.0698 | -59.1293 | -58.9417 | 0.036621 | -59.2438 | 63.8214 | 63.7115 | -59.1385 | -59.2255 | -0.036621 | -0.09613 | 0.022888 | 122.9965 | -0.18311 | -0.086976 | 0.054931 | -0.10529 | -0.19226 | 0.032043 | 0.091553 | -0.21057 | -0.01831 | -0.07782 | 122.8455 | 122.8775 | 59.0149 | -122.9187 | 122.8546 | 122.7448 | 59.0698 | -123.0148
271.0156 | 123.2071 | -59.0057 | 63.8077 | 0.11429 | 0.0031765 | 0.06825 | 0.066672 | 0.12971 | -0.0037085 | -0.0021641 | 0.11429 | -0.0037854 | 0.061701 | 0.060389 | 0.00057682 | -0.0036424 | 63.7985 | 63.9221 | -0.050354 | -59.2346 | 63.8397 | -59.079 | -59.111 | -58.9691 | 0.018311 | -59.2712 | 63.8489 | 63.7344 | -59.1385 | -59.2117 | -0.073242 | -0.10529 | 0.032044 | 122.9279 | -0.22888 | -0.1236 | -0.009155 | -0.13275 | -0.20599 | 0.041199 | 0.036621 | -0.2655 | -0.059509 | -0.073242 | 122.8455 | 122.8043 | 58.9554 | -122.9187 | 122.8546 | 122.7402 | 59.024 | -123.0194
272.0156 | 123.1888 | -59.0378 | 63.7802 | 0.20584 | 0.0087307 | 0.064405 | 0.070303 | 0.12864 | 0.00056395 | 0.00018594 | 0.43472 | -0.003999 | 0.06341 | 0.06103 | 0.004422 | -0.0042832 | 63.6246 | 64.032 | 0.022888 | -59.111 | 63.8031 | -59.0744 | -59.1064 | -58.9508 | 0.045776 | -59.2392 | 63.826 | 63.707 | -59.1339 | -59.23 | -0.036621 | -0.068664 | 0.022889 | 123.0698 | -0.073242 | -0.004578 | -0.15564 | -0.09613 | -0.19226 | 0.045777 | 0.086975 | -0.20142 | -0.009155 | -0.073242 | 122.8409 | 122.6624 | 59.0607 | -122.8867 | 122.8638 | 122.7448 | 59.0836 | -123.0103
273.0156 | 123.0972 | -59.0195 | 63.7802 | 0.13718 | 0.0068081 | 0.067396 | 0.069663 | 0.13356 | -0.0026405 | -0.0017369 | 0.19821 | -0.0044264 | 0.06106 | 0.062525 | 0.0024994 | -0.0019334 | 63.7894 | 63.9359 | -0.054932 | -59.2438 | 63.826 | -59.0607 | -59.111 | -58.9737 | 0.004578 | -59.2621 | 63.8351 | 63.7482 | -59.1064 | -59.2346 | -0.041199 | -0.091553 | 0.045777 | 122.9553 | -0.2243 | -0.13275 | 0.009156 | -0.086975 | -0.21515 | 0.054932 | 0.045776 | -0.24262 | -0.027466 | -0.032043 | 122.8455 | 122.8088 | 58.9645 | -122.8912 | 122.8546 | 122.7676 | 59.024 | -123.0148
274.0156 | 123.111 | -59.0469 | 63.7985 | 0.15244 | 0.0097989 | 0.065901 | 0.067954 | 0.13121 | 0.0018457 | -0.00088226 | 0.16769 | -0.00229 | 0.062769 | 0.061671 | 0.00549 | -0.0051376 | 63.8031 | 63.8672 | -0.10986 | -59.2758 | 63.8763 | -59.1064 | -59.1385 | -58.9828 | -0.041199 | -59.3033 | 63.858 | 63.7527 | -59.1476 | -59.2438 | -0.059509 | -0.091553 | 0.07782 | 122.9141 | -0.22888 | -0.13733 | 0.004578 | -0.10071 | -0.19684 | 0.059509 | 0.064087 | -0.25635 | -0.05951 | -0.045776 | 122.9233 | 122.85 | 58.9371 | -122.937 | 122.905 | 122.7997 | 59.0057 | -123.0423
275.0156 | 123.1705 | -59.0424 | 63.7939 | 0.41183 | 0.0050991 | 0.066755 | 0.069876 | 0.13163 | -0.0015723 | -0.00045506 | 0.19821 | -0.0035718 | 0.063196 | 0.060603 | 0.0031402 | -0.0040696 | 63.8809 | 63.9725 | -0.036621 | -59.2255 | 63.7894 | -59.0744 | -59.1293 | -58.9325 | 0.036621 | -59.2575 | 63.8214 | 63.7299 | -59.1293 | -59.2346 | -0.032044 | -0.086975 | -0.004577 | 123.0148 | -0.18311 | -0.096131 | 0.086975 | -0.086975 | -0.19226 | 0.027466 | 0.10986 | -0.21515 | -0.022888 | -0.064087 | 122.8317 | 122.9233 | 59.0057 | -122.9233 | 122.8638 | 122.7722 | 59.079 | -123.0286
276.0156 | 123.1293 | -59.0286 | 63.7711 | 0.21347 | 0.0070217 | 0.065687 | 0.069449 | 0.13078 | 0.00077755 | -0.00088226 | 0.19058 | -0.0010084 | 0.067041 | 0.06103 | 0.0035674 | -0.0036424 | 63.8077 | 63.9221 | -0.07782 | -59.2438 | 63.8168 | -59.079 | -59.1705 | -58.9462 | 0.018311 | -59.2667 | 63.8626 | 63.7344 | -59.1385 | -59.2255 | -0.050354 | -0.14191 | 0.045776 | 122.9507 | -0.21515 | -0.073242 | 0.036621 | -0.10986 | -0.19684 | 0.091553 | 0.082397 | -0.23804 | -0.041199 | -0.036621 | 122.8455 | 122.8363 | 58.9508 | -122.9416 | 122.8912 | 122.7631 | 59.0469 | -122.9965
277.0156 | 123.1201 | -59.0195 | 63.8031 | 0.19821 | 0.0038175 | 0.066969 | 0.066458 | 0.12886 | -0.0013587 | -0.0034457 | 0.22873 | -0.0044264 | 0.064691 | 0.061244 | 0.0018584 | -0.002147 | 63.8077 | 63.9313 | -0.050354 | -59.2438 | 63.8123 | -59.0744 | -59.0973 | -58.9828 | 0.009155 | -59.2667 | 63.8214 | 63.7619 | -59.1156 | -59.2346 | -0.054932 | -0.07782 | 0.009155 | 122.9507 | -0.2243 | -0.14648 | 0.004577 | -0.096131 | -0.21515 | 0.01831 | 0.036621 | -0.24719 | -0.032044 | -0.041199 | 122.8317 | 122.8271 | 58.9691 | -122.9004 | 122.8409 | 122.7814 | 59.0286 | -123.0377
278.0156 | 123.2254 | -59.0286 | 63.7802 | 0.14481 | 0.0065945 | 0.066755 | 0.070731 | 0.13163 | 0.0012047 | -0.0017369 | 0.2211 | -0.0014356 | 0.064691 | 0.062312 | 0.0018584 | -0.003856 | 63.8626 | 63.9267 | -0.045776 | -59.2163 | 63.8397 | -59.0744 | -59.1156 | -58.9417 | 0.036621 | -59.2575 | 63.8168 | 63.7299 | -59.1248 | -59.2529 | -0.045777 | -0.086976 | 0.05951 | 122.9553 | -0.18768 | -0.10071 | 0.082398 | -0.096131 | -0.22431 | 0.036621 | 0.086975 | -0.22888 | -0.004577 | -0.050354 | 122.8683 | 122.8912 | 58.9828 | -122.8958 | 122.8455 | 122.7585 | 59.0652 | -123.0331
279.0156 | 123.1247 | -59.024 | 63.7848 | 0.12192 | 0.0065945 | 0.067823 | 0.066672 | 0.13121 | -0.0013587 | -0.0019505 | 0.26688 | -0.0052808 | 0.063196 | 0.061457 | 0.0029266 | -0.0027878 | 63.8397 | 63.9587 | -0.022888 | -59.2255 | 63.8168 | -59.0698 | -59.1156 | -58.9508 | 0.041199 | -59.2667 | 63.8214 | 63.7573 | -59.1339 | -59.2209 | -0.045776 | -0.091553 | 0.032043 | 122.9828 | -0.20142 | -0.10986 | 0.054932 | -0.10986 | -0.19684 | 0.036621 | 0.073242 | -0.24262 | -0.045777 | -0.027466 | 122.8409 | 122.8638 | 59.0012 | -122.9004 | 122.8455 | 122.7814 | 59.0652 | -123.0057
280.0156 | 123.1476 | -59.0424 | 63.7802 | 0.15244 | 0.0097989 | 0.066755 | 0.069663 | 0.1327 | 0.0018457 | -0.0013095 | 0.19821 | -0.0027174 | 0.063196 | 0.063166 | 0.0052764 | -0.0044968 | 63.8031 | 63.8855 | -0.086975 | -59.2667 | 63.8535 | -59.0836 | -59.1385 | -58.9645 | -0.004578 | -59.2712 | 63.826 | 63.739 | -59.1522 | -59.2163 | -0.041199 | -0.096131 | 0.073243 | 122.9279 | -0.22431 | -0.12817 | 0.022889 | -0.10986 | -0.17395 | 0.045777 | 0.077819 | -0.22888 | -0.054931 | -0.041198 | 122.8958 | 122.8455 | 58.9554 | -122.9187 | 122.8683 | 122.7814 | 59.0378 | -122.9965
281.0156 | 123.2483 | -59.0744 | 63.7756 | 0.18295 | 0.0063809 | 0.067182 | 0.067954 | 0.13035 | 0.00077755 | -0.0025913 | 0.17532 | -0.0031446 | 0.059778 | 0.062525 | 0.0042084 | -0.005565 | 63.8351 | 63.945 | -0.050354 | -59.1934 | 63.8168 | -59.079 | -59.1385 | -58.9417 | 0.032043 | -59.2575 | 63.8214 | 63.7344 | -59.166 | -59.2575 | -0.004577 | -0.064087 | 0.041198 | 123.0194 | -0.11902 | -0.054931 | 0.059509 | -0.091553 | -0.1831 | 0.045776 | 0.13275 | -0.1831 | 0 | -0.041199 | 122.8912 | 122.9095 | 59.024 | -122.9141 | 122.8958 | 122.8088 | 59.1064 | -123.0331
282.0156 | 123.0377 | -59.0881 | 63.8077 | 0.12955 | 0.010013 | 0.066328 | 0.069663 | 0.12886 | 0.0029137 | -0.0019505 | -2.4492 | -0.0027174 | 0.064051 | 0.061457 | 0.0020722 | -0.003856 | 63.7573 | 63.7848 | -0.14648 | -59.2941 | 63.8947 | -59.1019 | -59.1614 | -59.0195 | -0.13733 | -59.317 | 63.9084 | 63.7985 | -59.166 | -59.2575 | -0.013733 | -0.073242 | 0.086975 | 122.8729 | -0.20599 | -0.13275 | -0.050354 | -0.07782 | -0.16937 | 0.10071 | 0.068665 | -0.22888 | -0.05951 | -0.009155 | 122.9828 | 122.8455 | 58.9417 | -122.9691 | 122.9965 | 122.8867 | 58.9508 | -123.0652
283.0156 | 123.1613 | -59.0286 | 63.7756 | 0.12955 | 0.0063809 | 0.068037 | 0.064322 | 0.13228 | -0.0022131 | -0.0013095 | 0.25925 | -0.003999 | 0.061487 | 0.063166 | 0.0024994 | -0.0012924 | 63.8306 | 63.9542 | -0.041199 | -59.2163 | 63.8077 | -59.0973 | -59.1019 | -58.9417 | 0.041199 | -59.2484 | 63.8123 | 63.7573 | -59.1522 | -59.2392 | -0.068665 | -0.073243 | 0.032043 | 122.9828 | -0.18768 | -0.11444 | 0.054931 | -0.1236 | -0.21057 | 0.036621 | 0.086975 | -0.21973 | -0.009155 | -0.018311 | 122.8363 | 122.8592 | 58.9874 | -122.8775 | 122.8409 | 122.7859 | 59.0698 | -123.0148
284.0156 | 123.0972 | -59.0652 | 63.8031 | 0.16006 | 0.010013 | 0.065473 | 0.06774 | 0.1327 | 0.0024865 | -0.00066866 | 0.20584 | -0.002931 | 0.061273 | 0.061244 | 0.0037812 | -0.0036424 | 63.7756 | 63.8443 | -0.11902 | -59.2758 | 63.8489 | -59.1019 | -59.1522 | -58.9966 | -0.054932 | -59.2941 | 63.8443 | 63.7848 | -59.1522 | -59.2346 | -0.036621 | -0.086975 | 0.045776 | 122.9095 | -0.21057 | -0.1236 | -0.027466 | -0.086975 | -0.16937 | 0.041198 | 0.068665 | -0.22888 | -0.059509 | -0.018311 | 122.9141 | 122.8409 | 58.9462 | -122.9553 | 122.9095 | 122.85 | 59.0103 | -123.0377
285.0156 | 123.1384 | -59.0057 | 63.8443 | 0.22873 | 0.0033901 | 0.067396 | 0.065604 | 0.13527 | -0.0039221 | -0.0030185 | -0.084076 | -0.0033582 | 0.062128 | 0.058253 | 0.00014962 | -0.0034286 | 63.8672 | 64.0045 | 0.064087 | -59.1751 | 63.8306 | -59.0561 | -59.1064 | -58.9325 | 0.1831 | -59.2117 | 63.8763 | 63.7802 | -59.1064 | -59.2117 | -0.050354 | -0.10071 | -0.013733 | 123.0103 | -0.16937 | -0.068665 | 0.022888 | -0.10071 | -0.20599 | 0.032044 | 0.073242 | -0.20599 | 0 | -0.064087 | 122.8363 | 122.8729 | 59.0698 | -122.9507 | 122.8821 | 122.7859 | 59.1888 | -123.056
286.0156 | 123.0743 | -59.0607 | 63.8168 | 0.11429 | 0.0095853 | 0.067182 | 0.070303 | 0.13249 | 0.00099115 | -0.0010959 | 0.16769 | -0.0010084 | 0.064051 | 0.064234 | 0.0029266 | -0.0059922 | 63.7665 | 63.8168 | -0.14648 | -59.285 | 63.8763 | -59.0881 | -59.166 | -59.0515 | -0.059509 | -59.3582 | 63.8763 | 63.8031 | -59.2026 | -59.2621 | -0.027466 | -0.10529 | 0.05951 | 122.8775 | -0.2243 | -0.11902 | -0.050354 | -0.14191 | -0.20142 | 0.05951 | 0.009155 | -0.29755 | -0.09613 | -0.013732 | 122.937 | 122.8271 | 58.9142 | -122.9828 | 122.937 | 122.8638 | 59.0012 | -123.0789
287.0156 | 123.0743 | -59.0698 | 63.7436 | 0.29739 | 0.0095853 | 0.066541 | 0.066458 | 0.13035 | -0.0030677 | -0.0010959 | 0.23636 | -0.0016492 | 0.061273 | 0.062098 | 0.0022858 | -0.0025742 | 63.8397 | 63.9359 | -0.045776 | -59.2117 | 63.8168 | -59.0698 | -59.1431 | -58.9462 | 0.027466 | -59.2484 | 63.8077 | 63.7436 | -59.1385 | -59.2117 | 0 | -0.073242 | 0.073242 | 123.0057 | -0.14191 | -0.068665 | 0.096131 | -0.068665 | -0.14191 | 0.064087 | 0.1236 | -0.17853 | -0.036621 | 0 | 122.8867 | 122.9095 | 59.024 | -122.8867 | 122.8775 | 122.8134 | 59.0973 | -122.9553
288.0156 | 123.1659 | -58.992 | 63.8351 | -0.11459 | 0.0025357 | 0.067182 | 0.06539 | 0.12907 | -0.0045631 | -0.0034457 | -0.061188 | -0.0033582 | 0.061487 | 0.059107 | 0.0035674 | -0.003856 | 63.8718 | 64.0137 | 0.068665 | -59.1568 | 63.8535 | -59.0561 | -59.0973 | -58.9325 | 0.17853 | -59.198 | 63.8489 | 63.8168 | -59.0927 | -59.2117 | -0.064087 | -0.10529 | 0.018311 | 123.0057 | -0.16479 | -0.059509 | 0.036621 | -0.10071 | -0.21973 | 0.013733 | 0.059509 | -0.20599 | 0.013733 | -0.018311 | 122.8455 | 122.8638 | 59.0607 | -122.9324 | 122.8409 | 122.8088 | 59.1705 | -123.0469
289.0156 | 123.056 | -59.0561 | 63.8031 | 0.18295 | 0.010013 | 0.067182 | 0.07009 | 0.1295 | 0.0018457 | -0.0013095 | 0.19821 | -0.0016492 | 0.061701 | 0.062312 | 0.0035674 | -0.003856 | 63.7711 | 63.8351 | -0.13275 | -59.2758 | 63.8672 | -59.1019 | -59.1797 | -59.0378 | -0.086975 | -59.3353 | 63.858 | 63.7756 | -59.1705 | -59.2712 | -0.045777 | -0.1236 | 0.064086 | 122.8912 | -0.21973 | -0.096131 | -0.032044 | -0.11444 | -0.21515 | 0.054931 | 0.01831 | -0.27924 | -0.064087 | -0.027466 | 122.9233 | 122.8271 | 58.9233 | -122.9828 | 122.9141 | 122.8317 | 58.9691 | -123.0743
290.0156 | 123.056 | -59.0744 | 63.8123 | 0.3508 | 0.010226 | 0.065901 | 0.069449 | 0.13014 | -0.00071785 | -0.0013095 | 0.17532 | -0.0033582 | 0.064051 | 0.062739 | 0.0031402 | -0.0042832 | 63.7802 | 63.8214 | -0.16022 | -59.2712 | 63.8718 | -59.0927 | -59.1431 | -59.0469 | -0.073242 | -59.3582 | 63.8763 | 63.7802 | -59.1476 | -59.2712 | -0.01831 | -0.068664 | 0.059509 | 122.8958 | -0.19684 | -0.12817 | -0.032044 | -0.073242 | -0.19684 | 0.064087 | 0.027466 | -0.28381 | -0.086975 | -0.032044 | 122.9462 | 122.8546 | 58.9142 | -122.9553 | 122.9507 | 122.8546 | 59.0012 | -123.0835
291.0156 | 123.1293 | -59.0607 | 63.7711 | 0.31265 | 0.0085171 | 0.068037 | 0.068808 | 0.13142 | -0.00050425 | 0.00061314 | 0.24399 | -0.002931 | 0.061273 | 0.062312 | 0.0012176 | -0.0025742 | 63.8443 | 63.9267 | -0.045776 | -59.2163 | 63.8168 | -59.1064 | -59.1248 | -58.96 | 0.036621 | -59.2346 | 63.7894 | 63.739 | -59.1156 | -59.23 | -0.045776 | -0.064087 | 0.045776 | 122.9874 | -0.15564 | -0.091553 | 0.073242 | -0.054932 | -0.16937 | 0.018311 | 0.10071 | -0.17395 | -0.004577 | -0.032043 | 122.8775 | 122.905 | 59.0149 | -122.8958 | 122.85 | 122.7997 | 59.0973 | -123.0011
292.0156 | 123.0286 | -59.0744 | 63.8168 | 0.16006 | 0.011081 | 0.066328 | 0.069022 | 0.13185 | 0.0012047 | 0.0040311 | 0.28976 | -0.003999 | 0.064264 | 0.063594 | 0.0029266 | -0.003215 | 63.4369 | 63.8535 | -0.013733 | -59.1705 | 63.8855 | -59.0973 | -59.1568 | -59.0469 | -0.059509 | -59.3719 | 63.8672 | 63.7939 | -59.1248 | -59.2438 | -0.022888 | -0.082397 | 0.068665 | 122.9279 | -0.09613 | -0.013733 | -0.37994 | -0.050354 | -0.16937 | 0.050354 | 0.027466 | -0.29755 | -0.12817 | -0.022888 | 122.9599 | 122.5113 | 59.0607 | -122.9736 | 122.9416 | 122.8683 | 59.0149 | -123.0606
293.0156 | 123.1384 | -59.0012 | 63.8351 | -0.23666 | 0.0044583 | 0.067823 | 0.068808 | 0.13121 | -0.0052039 | -0.0015231 | -0.076446 | -0.002931 | 0.060205 | 0.060389 | 0.0020722 | -0.002147 | 63.8489 | 64.0091 | 0.054932 | -59.1751 | 63.8351 | -59.0378 | -59.0881 | -58.96 | 0.1831 | -59.2026 | 63.8718 | 63.7985 | -59.1156 | -59.2163 | -0.036621 | -0.086975 | 0 | 123.0103 | -0.17395 | -0.086975 | 0.013733 | -0.11444 | -0.21515 | 0.036621 | 0.041199 | -0.20142 | 0.013733 | -0.036621 | 122.8363 | 122.85 | 59.0561 | -122.9233 | 122.8729 | 122.7997 | 59.1843 | -123.0515
294.0156 | 123.024 | -59.0607 | 63.8489 | 0.16769 | 0.0097989 | 0.063764 | 0.069235 | 0.12843 | 0.00077755 | 0.0010403 | 0.13718 | -0.00058096 | 0.065759 | 0.062525 | 0.00079042 | -0.0053512 | 63.7436 | 63.7756 | -0.14191 | -59.2987 | 63.8718 | -59.0881 | -59.1522 | -58.9142 | -0.18768 | -59.3399 | 63.9038 | 63.8123 | -59.1614 | -59.2484 | -0.027466 | -0.091553 | 0.022888 | 122.8363 | -0.23804 | -0.14648 | -0.10529 | -0.10071 | -0.18768 | 0.054932 | 0.14648 | -0.27924 | -0.091553 | -0.036621 | 122.9324 | 122.8043 | 58.9188 | -123.0011 | 122.9645 | 122.8729 | 58.873 | -123.0972
295.0156 | 123.056 | -59.0698 | 63.8306 | 0.11429 | 0.0080899 | 0.067396 | 0.066031 | 0.12993 | 0.00077755 | -0.0019505 | 0.16006 | -0.0033582 | 0.064478 | 0.061885 | 0.0022858 | -0.0036424 | 63.7665 | 63.8306 | -0.13733 | -59.2758 | 63.8901 | -59.0927 | -59.166 | -59.0515 | -0.082397 | -59.3491 | 63.8489 | 63.7894 | -59.166 | -59.2392 | -0.022888 | -0.096131 | 0.05951 | 122.9004 | -0.20599 | -0.10986 | -0.064087 | -0.096131 | -0.16937 | 0.018311 | 0.01831 | -0.27924 | -0.10986 | -0.041198 | 122.9599 | 122.8363 | 58.9325 | -122.9965 | 122.9187 | 122.8592 | 58.9874 | -123.0698
296.0156 | 123.0286 | -59.0469 | 63.858 | 0.053253 | 0.012576 | 0.068891 | 0.067954 | 0.12993 | 0.0035547 | -0.0017369 | 0.037995 | -0.0031446 | 0.0664 | 0.061885 | 0.0039948 | -0.0053512 | 63.7894 | 63.8489 | -0.082397 | -59.2484 | 63.8809 | -59.0927 | -59.1385 | -59.0378 | -0.032043 | -59.3353 | 63.8947 | 63.7985 | -59.1385 | -59.2575 | -0.045776 | -0.091553 | 0.022888 | 122.8958 | -0.20142 | -0.10986 | -0.068664 | -0.091553 | -0.21057 | 0.036621 | 0.009155 | -0.28839 | -0.07782 | -0.059509 | 122.9279 | 122.8363 | 58.9645 | -122.9965 | 122.9416 | 122.8455 | 59.0149 | -123.1155
297.0156 | 123.143 | -59.0286 | 63.826 | 0.22873 | 0.0055265 | 0.065687 | 0.069876 | 0.13142 | -0.0022131 | -0.0013095 | 0.28214 | -0.0025038 | 0.061914 | 0.062098 | 0.0022858 | -0.00065157 | 63.8306 | 63.945 | -0.032043 | -59.2117 | 63.8031 | -59.0881 | -59.1293 | -58.9554 | -0.2243 | -59.1431 | 63.7894 | 63.7161 | -59.1522 | -59.2117 | -0.05951 | -0.10071 | -0.022888 | 122.9736 | -0.18311 | -0.082398 | 0.004577 | -0.1236 | -0.18311 | -0.036621 | 0.073242 | -0.11444 | 0.068665 | -0.10986 | 122.8317 | 122.8592 | 58.9966 | -122.9553 | 122.818 | 122.7447 | 58.8043 | -123.0377
298.0156 | 123.1201 | -59.0469 | 63.8168 | 0.030365 | 0.0027493 | 0.068037 | 0.069022 | 0.13014 | -0.0049903 | -0.0030185 | 0.25162 | -0.0061352 | 0.060419 | 0.060389 | 0.0018584 | -0.003215 | 63.7939 | 63.8901 | -0.045776 | -59.2438 | 63.8535 | -59.0652 | -59.1156 | -58.992 | 0.027466 | -59.2758 | 63.8489 | 63.8031 | -59.1202 | -59.1934 | -0.018311 | -0.068665 | 0.036622 | 122.937 | -0.19684 | -0.12817 | -0.022888 | -0.073242 | -0.14648 | 0.032044 | 0.054932 | -0.22888 | -0.082398 | -0.013732 | 122.9004 | 122.8409 | 59.0012 | -122.9324 | 122.8958 | 122.85 | 59.0744 | -123.0103
299.0156 | 123.0743 | -59.0652 | 63.7207 | 0.25925 | 0.0076627 | 0.06761 | 0.068167 | 0.1327 | -0.0017859 | -0.0013095 | 0.26688 | -0.0037854 | 0.063196 | 0.060389 | 0.0037812 | -0.0034286 | 63.8535 | 63.9404 | -0.045776 | -59.2072 | 63.7985 | -59.0698 | -59.1202 | -58.96 | 0.032043 | -59.2484 | 63.8214 | 63.7436 | -59.1705 | -59.2209 | -0.004577 | -0.054931 | 0.07782 | 123.0057 | -0.14191 | -0.086975 | 0.13275 | -0.10529 | -0.15564 | 0.10071 | 0.10529 | -0.1831 | -0.027466 | 0.022888 | 122.8638 | 122.9187 | 59.0195 | -122.8409 | 122.8867 | 122.8088 | 59.0973 | -122.9416
300.0156 | 123.024 | -59.0652 | 63.8168 | 0.14481 | 0.0087307 | 0.067396 | 0.066245 | 0.12928 | -0.0013587 | -0.0030185 | 0.12955 | -0.0035718 | 0.065973 | 0.064021 | 0.0046356 | -0.0064194 | 64.0045 | 63.7161 | -0.1831 | -59.2072 | 63.9084 | -59.1064 | -59.1339 | -59.0378 | -0.082397 | -59.3674 | 63.8535 | 63.8031 | -59.1705 | -59.2621 | -0.041198 | -0.068664 | 0.091553 | 122.7814 | -0.14191 | -0.073242 | 0.18768 | -0.10529 | -0.19684 | 0.036622 | 0.027466 | -0.30212 | -0.10529 | -0.013732 | 122.9736 | 123.0698 | 58.8821 | -122.9507 | 122.9187 | 122.8683 | 58.9828 | -123.0789
301.0156 | 123.1888 | -59.0378 | 63.7756 | 0.2211 | 0.0087307 | 0.063551 | 0.069876 | 0.13185 | -0.0017859 | -0.00045506 | 0.22873 | -0.0033582 | 0.065119 | 0.062525 | 0.0024994 | -0.0025742 | 63.8397 | 63.8901 | -0.091553 | -59.2438 | 63.826 | -59.0652 | -59.1476 | -58.9691 | 0.036621 | -59.2392 | 63.7985 | 63.7482 | -59.1614 | -59.2438 | -0.027466 | -0.10986 | 0.050354 | 122.9279 | -0.20599 | -0.09613 | 0.064087 | -0.1236 | -0.20599 | 0.022888 | 0.068665 | -0.20142 | 0.004577 | -0.027466 | 122.8638 | 122.8775 | 58.9462 | -122.9233 | 122.8363 | 122.7859 | 59.0744 | -123.0194
302.0156 | 123.0194 | -59.0836 | 63.8306 | -0.076447 | 0.010226 | 0.064405 | 0.071158 | 0.13035 | 0.0029137 | -0.00066866 | -0.00015237 | -0.0027174 | 0.063196 | 0.061885 | 0.0029266 | -0.003215 | 63.7894 | 63.8351 | -0.10071 | -59.2575 | 63.8718 | -59.1019 | -59.1568 | -59.0652 | -0.050354 | -59.3719 | 63.8763 | 63.8214 | -59.1522 | -59.2621 | -0.018311 | -0.073242 | 0.041199 | 122.9187 | -0.17395 | -0.10071 | -0.041198 | -0.068665 | -0.17853 | 0.045777 | 0.01831 | -0.28839 | -0.10986 | -0.009155 | 122.9553 | 122.8729 | 58.9828 | -122.9874 | 122.9599 | 122.905 | 59.0332 | -123.0927
303.0156 | 123.0881 | -58.9966 | 63.826 | -0.3511 | 0.0029629 | 0.066969 | 0.066672 | 0.13078 | -0.0049903 | -0.0034457 | -0.045929 | -0.00464 | 0.061701 | 0.06103 | 0.0012176 | -0.0023606 | 63.8489 | 64.0091 | 0.07782 | -59.166 | 63.8351 | -59.0424 | -59.1019 | -58.9371 | 0.16479 | -59.1934 | 63.8489 | 63.8123 | -59.1019 | -59.1934 | -0.045776 | -0.10529 | 0.009155 | 123.0057 | -0.16937 | -0.064087 | 0.022888 | -0.10529 | -0.19684 | 0.022888 | 0.059509 | -0.19684 | 0 | -0.013733 | 122.8317 | 122.8455 | 59.0744 | -122.9279 | 122.8455 | 122.8088 | 59.1614 | -123.0194
304.0156 | 123.0515 | -59.0424 | 63.8168 | 0.17532 | 0.011081 | 0.069105 | 0.068594 | 0.13185 | 0.0014185 | -0.00088226 | 0.21347 | -0.0020764 | 0.065546 | 0.060816 | 0.0016448 | -0.0040696 | 63.7756 | 63.8123 | -0.1236 | -59.2941 | 63.8809 | -59.0836 | -59.1568 | -59.0332 | -0.073242 | -59.3262 | 63.8672 | 63.7756 | -59.1843 | -59.2987 | -0.041199 | -0.11444 | 0.064087 | 122.8546 | -0.25177 | -0.13733 | -0.041198 | -0.14191 | -0.25635 | 0.050354 | 0.009155 | -0.28381 | -0.027466 | -0.041198 | 122.9233 | 122.818 | 58.9188 | -122.9736 | 122.9095 | 122.818 | 58.9691 | -123.1155
305.0156 | 123.1155 | -59.0195 | 63.7939 | 0.18295 | 0.0083035 | 0.067182 | 0.066672 | 0.1295 | -0.0019995 | -0.00066866 | -0.21378 | -0.0052808 | 0.062555 | 0.062312 | 0.00079042 | -0.0019334 | 63.8351 | 63.9404 | -0.041199 | -59.2072 | 63.8123 | -59.0927 | -59.1476 | -58.9233 | 0.045776 | -59.23 | 63.8214 | 63.7665 | -59.1064 | -59.23 | -0.073242 | -0.12817 | 0.018311 | 122.9599 | -0.18768 | -0.059509 | 0.041199 | -0.086975 | -0.21057 | 0.027466 | 0.09613 | -0.21057 | 0 | -0.027466 | 122.8317 | 122.8546 | 58.9783 | -122.9416 | 122.8409 | 122.7859 | 59.0652 | -123.024
306.0156 | 123.0698 | -59.0881 | 63.8077 | 0.31265 | 0.01044 | 0.067396 | 0.071158 | 0.13163 | 0.0020593 | -0.0034457 | 0.16769 | -0.0018628 | 0.062982 | 0.062098 | 0.0024994 | -0.003215 | 63.7711 | 63.7985 | -0.13275 | -59.285 | 63.8855 | -59.0927 | -59.1385 | -59.0607 | -0.082397 | -59.3308 | 63.8718 | 63.7985 | -59.1705 | -59.2712 | -0.004577 | -0.050354 | 0.07782 | 122.8867 | -0.19684 | -0.14648 | -0.036621 | -0.082397 | -0.1831 | 0.064087 | 0.027466 | -0.24262 | -0.05951 | -0.009155 | 122.9736 | 122.8592 | 58.9554 | -122.9462 | 122.9599 | 122.8867 | 59.0057 | -123.0789
307.0156 | 123.1338 | -59.0149 | 63.7756 | 0.2211 | 0.0061673 | 0.065473 | 0.066031 | 0.12993 | -0.0017859 | -0.00045506 | 0.27451 | -0.0048536 | 0.06341 | 0.062312 | 0.0024994 | -0.0057786 | 63.8443 | 63.9313 | -0.045776 | -59.2072 | 63.826 | -59.0744 | -59.1202 | -58.9142 | 0.1831 | -59.2621 | 63.7848 | 63.7665 | -59.0973 | -59.2346 | -0.059509 | -0.10529 | 0.050354 | 122.9462 | -0.19226 | -0.086975 | 0.068664 | -0.082397 | -0.21973 | 0.009155 | 0.10071 | -0.24719 | -0.027466 | -0.009156 | 122.8409 | 122.8592 | 58.9691 | -122.8958 | 122.7997 | 122.7814 | 59.198 | -123.0103
308.0156 | 123.1018 | -59.0286 | 63.8168 | 0.030365 | 0.0025357 | 0.069959 | 0.067313 | 0.13206 | -0.0045631 | -0.00066866 | -0.38925 | -0.0050672 | 0.061914 | 0.061671 | 0.0012176 | -0.0042832 | 63.7894 | 63.8947 | -0.050354 | -59.2346 | 63.8214 | -59.0515 | -59.1156 | -59.0057 | 0.018311 | -59.2667 | 63.826 | 63.7573 | -59.1293 | -59.2255 | -0.022889 | -0.086976 | 0.004578 | 122.9233 | -0.20599 | -0.11902 | -0.027465 | -0.10071 | -0.19684 | 0.009156 | 0.022888 | -0.23804 | -0.041199 | -0.059509 | 122.85 | 122.818 | 58.9783 | -122.9324 | 122.8546 | 122.7859 | 59.0469 | -123.0423
309.0156 | 123.1476 | -59.0424 | 63.7711 | 0.20584 | 0.0059537 | 0.066755 | 0.069022 | 0.13206 | 0.0029137 | -0.0032321 | 0.25162 | -0.0031446 | 0.065332 | 0.065089 | 0.0033538 | -0.003215 | 63.7985 | 63.8306 | -0.10071 | -59.2667 | 63.858 | -59.0881 | -59.1248 | -58.9828 | -0.032043 | -59.2941 | 63.8397 | 63.7711 | -59.1431 | -59.2529 | -0.045777 | -0.082398 | 0.086975 | 122.8729 | -0.22431 | -0.14191 | 0.027466 | -0.10071 | -0.21057 | 0.068665 | 0.059509 | -0.25177 | -0.041198 | 0 | 122.9004 | 122.8409 | 58.9417 | -122.8958 | 122.8821 | 122.8134 | 59.0103 | -123.024
310.0156 | 123.024 | -59.0607 | 63.7756 | 0.10666 | 0.0097989 | 0.065687 | 0.070944 | 0.13163 | 0.0039819 | -0.0010959 | 0.10666 | -0.0037854 | 0.063837 | 0.061671 | 0.0046356 | -0.0040696 | 63.7756 | 63.7985 | -0.13733 | -59.2941 | 63.8809 | -59.1064 | -59.1476 | -59.0836 | -0.07782 | -59.3903 | 63.8855 | 63.8123 | -59.1385 | -59.2484 | -0.045776 | -0.086975 | 0.10529 | 122.8592 | -0.23346 | -0.14648 | 0 | -0.07782 | -0.18768 | 0.10986 | -0.022888 | -0.32959 | -0.14191 | 0.036621 | 122.9416 | 122.8363 | 58.9233 | -122.9233 | 122.9462 | 122.8729 | 58.9828 | -123.024
311.0156 | 123.1293 | -59.0057 | 63.7848 | 0.24399 | 0.0070217 | 0.066755 | 0.067954 | 0.12822 | -0.0056311 | -0.0025913 | 0.22873 | -0.0035718 | 0.063837 | 0.063594 | 0.0016448 | -0.003215 | 63.8397 | 63.9221 | -0.041199 | -59.2346 | 63.8168 | -59.0515 | -59.1385 | -58.9508 | 0.045776 | -59.23 | 63.8031 | 63.7527 | -59.1248 | -59.2255 | -0.045777 | -0.13275 | 0.032043 | 122.9279 | -0.22888 | -0.09613 | 0.054932 | -0.11902 | -0.21973 | 0.018311 | 0.054931 | -0.2243 | -0.004578 | -0.032043 | 122.8226 | 122.8455 | 58.9645 | -122.9233 | 122.8088 | 122.7585 | 59.0515 | -123.0103
312.0156 | 123.0789 | -59.0378 | 63.7939 | 0.18295 | 0.0089443 | 0.066328 | 0.070944 | 0.13057 | 0.0018457 | -0.0028049 | 0.21347 | -0.002931 | 0.061487 | 0.062098 | 0.0031402 | -0.0036424 | 63.7894 | 63.8718 | -0.11902 | -59.2621 | 63.8397 | -59.0927 | -59.1339 | -58.9874 | -0.041199 | -59.285 | 63.8489 | 63.7619 | -59.1568 | -59.2438 | -0.054931 | -0.09613 | 0.045777 | 122.9095 | -0.2243 | -0.12817 | -0.004577 | -0.11902 | -0.20599 | 0.054932 | 0.050354 | -0.24719 | -0.041199 | -0.032043 | 122.8775 | 122.8271 | 58.9188 | -122.9279 | 122.8867 | 122.7997 | 58.9966 | -123.0377
313.0156 | 123.1567 | -59.0195 | 63.7848 | 0.14481 | 0.0070217 | 0.067823 | 0.068381 | 0.13185 | -0.0045631 | -0.0019505 | 0.22873 | -0.0037854 | 0.062342 | 0.061885 | 0.0048492 | -0.002147 | 63.8397 | 63.9404 | -0.018311 | -59.2346 | 63.8077 | -59.0652 | -59.1248 | -58.9554 | 0.027466 | -59.2392 | 63.8123 | 63.7665 | -59.1248 | -59.2392 | -0.045777 | -0.10529 | 0.022888 | 122.9599 | -0.21515 | -0.10986 | 0.054932 | -0.10529 | -0.21973 | 0.027466 | 0.064087 | -0.21973 | 0 | -0.018311 | 122.8271 | 122.8592 | 59.0012 | -122.9095 | 122.8317 | 122.7859 | 59.0469 | -123.024
314.0156 | 123.1293 | -59.0515 | 63.8077 | 0.19821 | 0.0085171 | 0.068037 | 0.07009 | 0.13099 | 0.00077755 | -0.0021641 | 0.16769 | -0.00229 | 0.063837 | 0.062525 | 0.002713 | -0.003856 | 63.7802 | 63.8443 | -0.11444 | -59.2529 | 63.8535 | -59.1019 | -59.1293 | -59.0012 | -0.027466 | -59.2941 | 63.8672 | 63.7573 | -59.1568 | -59.2438 | -0.050354 | -0.077819 | 0.045777 | 122.8958 | -0.20142 | -0.1236 | -0.027466 | -0.10529 | -0.19226 | 0.059509 | 0.050354 | -0.24261 | -0.050354 | -0.050354 | 122.905 | 122.8317 | 58.9371 | -122.937 | 122.9187 | 122.8088 | 59.024 | -123.0515
315.0156 | 123.1293 | -59.0103 | 63.7756 | 0.16769 | 0.0048855 | 0.068037 | 0.068381 | 0.12864 | -0.0019995 | -0.0023777 | 0.21347 | -0.0027174 | 0.064051 | 0.06103 | 0.0031402 | -0.0027878 | 63.8397 | 63.9359 | -0.027466 | -59.2163 | 63.7939 | -59.0561 | -59.111 | -58.9417 | 0.036621 | -59.2346 | 63.7985 | 63.7711 | -59.1568 | -59.23 | -0.045776 | -0.10071 | 0.01831 | 122.9462 | -0.20599 | -0.10529 | 0.064087 | -0.14648 | -0.21973 | 0.022888 | 0.068665 | -0.2243 | -0.004577 | -0.004578 | 122.8043 | 122.85 | 58.9828 | -122.8867 | 122.8088 | 122.7814 | 59.0469 | -123.0057
316.0156 | 123.0515 | -59.0469 | 63.8077 | 0.25162 | 0.0087307 | 0.066114 | 0.070303 | 0.12928 | 0.0024865 | -0.0036595 | 0.16769 | -0.0014356 | 0.06341 | 0.062739 | 0.0052764 | -0.0036424 | 63.7711 | 63.8031 | -0.13275 | -59.2804 | 63.8718 | -59.1064 | -59.1568 | -59.0515 | -0.073242 | -59.3582 | 63.8763 | 63.7802 | -59.166 | -59.2484 | -0.059509 | -0.10986 | 0.064087 | 122.85 | -0.23346 | -0.1236 | -0.036621 | -0.11902 | -0.20142 | 0.068665 | -0.004578 | -0.31128 | -0.10986 | -0.027466 | 122.9187 | 122.818 | 58.9142 | -122.9645 | 122.9233 | 122.8271 | 58.9737 | -123.056
317.0156 | 123.143 | -59.0012 | 63.8031 | 0.12955 | 0.0076627 | 0.067182 | 0.067526 | 0.13057 | -0.00050425 | -0.0021641 | 0.25925 | -0.0037854 | 0.062769 | 0.061885 | 0.001004 | -0.0036424 | 63.8397 | 63.9313 | -0.027466 | -59.2072 | 63.8031 | -59.0652 | -59.111 | -58.8821 | -0.018311 | -59.1934 | 63.826 | 63.7711 | -59.1156 | -59.198 | -0.064087 | -0.10986 | 0 | 122.9324 | -0.20599 | -0.09613 | 0.036621 | -0.11444 | -0.19684 | 0.022888 | 0.11902 | -0.19226 | 0.004578 | -0.032044 | 122.8043 | 122.8409 | 58.9737 | -122.9141 | 122.8271 | 122.7722 | 58.9828 | -123.0011
318.0156 | 123.1522 | -59.0149 | 63.7894 | 0.18295 | 0.0072355 | 0.068891 | 0.071585 | 0.13463 | -0.00071785 | -0.0025913 | 1.6402 | -0.0031446 | 0.064264 | 0.063594 | 0.002713 | -0.0042832 | 63.8397 | 63.9359 | -0.036621 | -59.2072 | 63.8123 | -59.0836 | -59.1248 | -58.9874 | 0.068665 | -59.2255 | 63.8306 | 63.7756 | -59.1156 | -59.2026 | -0.068664 | -0.10986 | 0.022888 | 122.9507 | -0.19226 | -0.082397 | 0.050354 | -0.10071 | -0.18768 | 0.041198 | 0.027466 | -0.21057 | -0.022888 | -0.013733 | 122.8271 | 122.8546 | 58.9783 | -122.9141 | 122.8455 | 122.7905 | 59.0836 | -122.9919
319.0156 | 123.1064 | -59.024 | 63.8123 | 0.13718 | 0.0038175 | 0.06761 | 0.066885 | 0.12736 | -0.0019995 | -0.0025913 | 0.20584 | -0.0067762 | 0.063196 | 0.059962 | 0.0029266 | -0.0030014 | 63.7756 | 63.9084 | -0.045776 | -59.2575 | 63.8306 | -59.0332 | -59.1293 | -58.992 | 0.018311 | -59.2621 | 63.858 | 63.7573 | -59.1476 | -59.23 | -0.009155 | -0.10529 | 0.01831 | 122.9324 | -0.23346 | -0.12817 | -0.036621 | -0.1236 | -0.20599 | 0.045776 | 0.032044 | -0.23804 | -0.032043 | -0.054932 | 122.8546 | 122.7997 | 58.9783 | -122.9416 | 122.8821 | 122.7814 | 59.0424 | -123.0423
320.0156 | 123.1705 | -59.0195 | 63.7711 | 0.20584 | 0.0074491 | 0.06526 | 0.067954 | 0.13121 | 0.00035035 | -0.0025913 | -0.10696 | -0.0042126 | 0.062982 | 0.061457 | 0.0022858 | -0.0053512 | 63.8351 | 63.9404 | -0.036621 | -59.2117 | 63.8214 | -59.079 | -59.1522 | -58.9645 | 0.041199 | -59.2255 | 63.8351 | 63.7344 | -59.1202 | -59.2392 | -0.059509 | -0.13275 | 0.050354 | 122.9599 | -0.19226 | -0.059509 | 0.064087 | -0.10071 | -0.21973 | 0.064087 | 0.054931 | -0.20599 | 0.013733 | -0.036621 | 122.8409 | 122.8546 | 58.9828 | -122.9233 | 122.8546 | 122.7539 | 59.0607 | -123.0103
321.0156 | 123.1201 | -59.024 | 63.7939 | 0.11429 | 0.0040311 | 0.069746 | 0.067526 | 0.12864 | -0.0049903 | -0.0032321 | 0.13718 | -0.0033582 | 0.06106 | 0.062098 | 0.0016448 | -0.0042832 | 63.7894 | 63.8992 | -0.068665 | -59.2484 | 63.8443 | -59.0744 | -59.1248 | -58.9874 | 0.004578 | -59.2575 | 63.826 | 63.7711 | -59.1293 | -59.2346 | -0.050354 | -0.10071 | 0.050354 | 122.9233 | -0.2243 | -0.1236 | -0.004577 | -0.10529 | -0.21057 | 0.032044 | 0.036621 | -0.23346 | -0.022888 | -0.022888 | 122.8683 | 122.8134 | 58.9554 | -122.9187 | 122.85 | 122.7951 | 59.0286 | -123.0286
322.0156 | 123.1247 | -59.0195 | 63.7802 | 0.14481 | 0.0057401 | 0.066755 | 0.06774 | 0.12928 | -0.0015723 | 0.00018594 | 0.22873 | -0.0048536 | 0.062769 | 0.062098 | 0.0029266 | -0.004924 | 63.8489 | 63.945 | -0.036621 | -59.2346 | 63.8031 | -59.079 | -59.1156 | -58.9508 | 0.018311 | -59.2438 | 63.8168 | 63.7482 | -59.1248 | -59.2255 | -0.059509 | -0.096131 | 0.022889 | 122.9645 | -0.21515 | -0.11902 | 0.068665 | -0.10529 | -0.20599 | 0.036621 | 0.068664 | -0.2243 | -0.01831 | -0.032043 | 122.8226 | 122.8683 | 58.9828 | -122.8958 | 122.8363 | 122.7676 | 59.0378 | -123.0057
323.0156 | 123.1064 | -59.0103 | 63.7756 | 0.12192 | 0.0070217 | 0.066328 | 0.069876 | 0.13249 | -0.0019995 | -0.0034457 | 0.2211 | -0.002931 | 0.06341 | 0.062098 | 0.00057682 | -0.002147 | 63.8443 | 63.9313 | -0.032043 | -59.23 | 63.8168 | -59.0744 | -59.1293 | -58.9554 | 0.013733 | -59.2484 | 63.826 | 63.7527 | -59.1522 | -59.2392 | -0.064087 | -0.11902 | 0.041198 | 122.9416 | -0.21973 | -0.10071 | 0.068664 | -0.14191 | -0.22888 | 0.050354 | 0.054932 | -0.23804 | -0.009155 | -0.022888 | 122.8271 | 122.8546 | 58.9783 | -122.905 | 122.8363 | 122.7631 | 59.024 | -123.0148
324.0156 | 123.1155 | -59.0286 | 63.7756 | 0.20584 | 0.0080899 | 0.064619 | 0.066672 | 0.13078 | -0.00071785 | 0.0016811 | -0.091705 | -0.003999 | 0.064264 | 0.06103 | 0.004422 | -0.0034286 | 63.945 | 63.6795 | -0.16937 | -59.1568 | 63.8031 | -59.079 | -59.0927 | -58.9462 | 0.018311 | -59.2346 | 63.8351 | 63.7207 | -59.166 | -59.2346 | -0.050354 | -0.064087 | 0.027466 | 122.7081 | -0.12817 | -0.064087 | 0.16937 | -0.13733 | -0.20599 | 0.059509 | 0.082397 | -0.20599 | 0 | -0.054932 | 122.8317 | 122.9736 | 58.8593 | -122.8683 | 122.8638 | 122.7493 | 59.0469 | -123.0103
325.0156 | 123.1155 | -59.0332 | 63.8123 | -0.2977 | 0.0038175 | 0.068037 | 0.068808 | 0.13014 | -0.0045631 | -0.0034457 | 0.15244 | -0.0052808 | 0.062769 | 0.062953 | 0.0016448 | -0.0023606 | 63.7985 | 63.9038 | -0.041199 | -59.2438 | 63.858 | -59.0698 | -59.111 | -58.9691 | 0.054932 | -59.2575 | 63.8397 | 63.7756 | -59.1248 | -59.2117 | -0.036621 | -0.07782 | 0.045776 | 122.937 | -0.21057 | -0.13275 | -0.013733 | -0.091553 | -0.17853 | 0.027466 | 0.064087 | -0.2243 | -0.045776 | -0.036621 | 122.8912 | 122.8317 | 58.992 | -122.9233 | 122.8729 | 122.8088 | 59.0881 | -123.024
326.0156 | 123.1064 | -59.0378 | 63.7894 | 0.17532 | 0.0033901 | 0.064405 | 0.07009 | 0.13292 | -0.0013587 | -0.0021641 | 0.2211 | -0.0025038 | 0.061273 | 0.062312 | 0.001004 | -0.004924 | 63.8397 | 63.9496 | -0.032043 | -59.2255 | 63.826 | -59.079 | -59.1202 | -58.9462 | 0.032043 | -59.2529 | 63.8077 | 63.739 | -59.1385 | -59.2484 | -0.041198 | -0.082397 | 0.036621 | 122.9874 | -0.18768 | -0.10529 | 0.050354 | -0.10071 | -0.21057 | 0.01831 | 0.091553 | -0.21515 | -0.004578 | -0.050354 | 122.8638 | 122.8775 | 59.0057 | -122.9095 | 122.8455 | 122.7768 | 59.0698 | -123.0377
327.0156 | 123.1338 | -59.0195 | 63.826 | -0.77072 | 0.0029629 | 0.06526 | 0.068594 | 0.13099 | -0.0019995 | -0.0032321 | 0.09903 | -0.002931 | 0.061701 | 0.061671 | 0.001004 | -0.0034286 | 63.7711 | 63.9267 | -0.050354 | -59.2117 | 63.8626 | -59.0515 | -59.1156 | -58.9783 | 0.050354 | -59.2529 | 63.858 | 63.7802 | -59.111 | -59.2209 | -0.032044 | -0.096131 | 0.036621 | 122.9462 | -0.19226 | -0.09613 | -0.054932 | -0.091553 | -0.20142 | 0.032043 | 0.041199 | -0.23346 | -0.032044 | -0.045777 | 122.8821 | 122.7905 | 58.9691 | -122.9416 | 122.8775 | 122.7997 | 59.0698 | -123.0469
328.0156 | 123.1064 | -59.0378 | 63.7894 | 0.12955 | 0.0080899 | 0.066755 | 0.069022 | 0.13014 | 0.0012047 | -0.0021641 | 0.25162 | -0.0035718 | 0.062769 | 0.061671 | 0.001004 | -0.004924 | 63.8489 | 63.9587 | -0.022888 | -59.23 | 63.8168 | -59.0836 | -59.1202 | -58.9371 | 0.032043 | -59.2392 | 63.8443 | 63.739 | -59.1522 | -59.2392 | -0.045776 | -0.082397 | 0.027465 | 122.9965 | -0.19226 | -0.10986 | 0.059509 | -0.11444 | -0.20142 | 0.054931 | 0.10071 | -0.20142 | 0 | -0.050354 | 122.8546 | 122.8867 | 59.0149 | -122.9095 | 122.8821 | 122.7768 | 59.0698 | -123.0286
329.0156 | 123.0927 | -59.0103 | 63.7939 | 0.030365 | 0.0029629 | 0.06761 | 0.07009 | 0.13035 | -0.0013587 | -0.0010959 | 0.060883 | -0.0050672 | 0.059564 | 0.061671 | 0.0024994 | -0.0036424 | 63.7024 | 63.9221 | -0.022888 | -59.2484 | 63.8489 | -59.0515 | -59.1202 | -58.9737 | 0.018311 | -59.2529 | 63.8443 | 63.7665 | -59.1431 | -59.2117 | -0.041199 | -0.10986 | 0.054932 | 122.9324 | -0.23804 | -0.12817 | -0.091552 | -0.13275 | -0.20142 | 0.050354 | 0.036621 | -0.24262 | -0.041199 | -0.027466 | 122.8592 | 122.7127 | 58.9874 | -122.9141 | 122.8546 | 122.7768 | 59.0286 | -123.0057
330.0625 | 123.0286 | -59.0149 | 63.8809 | -0.33585 | 0.0055265 | 0.066969 | 0.073081 | 0.12993 | -0.0013587 | -0.0049411 | -0.2214 | -0.0018628 | 0.062982 | 0.062312 | 0.0022858 | -0.006633 | 63.8077 | 63.8809 | -0.022888 | -59.2392 | 63.9038 | -59.0607 | -59.1339 | -59.0057 | 0.054932 | -59.3033 | 63.9267 | 63.826 | -59.1476 | -59.2163 | -0.045776 | -0.11902 | 0.022889 | 122.8958 | -0.2243 | -0.10529 | -0.073242 | -0.13275 | -0.20142 | 0.045777 | 0.009156 | -0.28839 | -0.086975 | -0.054931 | 122.9187 | 122.8226 | 58.992 | -123.0148 | 122.9416 | 122.8409 | 59.0698 | -123.0972
331.0625 | 123.0927 | -59.024 | 63.8535 | -0.14511 | 0.0095853 | 0.067182 | 0.07009 | 0.12993 | 0.0046227 | -0.0032321 | -0.19089 | -0.00229 | 0.061273 | 0.063166 | 0.002713 | -0.003856 | 63.8443 | 63.9267 | -0.004578 | -59.2117 | 63.913 | -59.0927 | -59.1568 | -58.9828 | 0.073242 | -59.285 | 63.8809 | 63.7619 | -59.1293 | -59.23 | -0.068664 | -0.13275 | 0.059509 | 122.9507 | -0.18768 | -0.054932 | -0.009156 | -0.10529 | -0.20599 | 0.027465 | 0.041199 | -0.26093 | -0.054931 | -0.091553 | 122.937 | 122.8683 | 59.0195 | -123.0103 | 122.905 | 122.7859 | 59.0973 | -123.0835
332.0156 | 123.0881 | -59.0195 | 63.8168 | 0.17532 | 0.0046719 | 0.066114 | 0.067099 | 0.12993 | -0.0032813 | -2.7856e-05 | 0.21347 | -0.0042126 | 0.061273 | 0.062953 | 0.0012176 | -0.0017196 | 63.7985 | 63.9496 | -0.036621 | -59.2346 | 63.7985 | -59.0698 | -59.1248 | -58.9645 | 0.013733 | -59.2575 | 63.8123 | 63.7527 | -59.1476 | -59.2529 | -0.050354 | -0.10529 | -0.01831 | 122.9691 | -0.21515 | -0.10986 | -0.01831 | -0.12817 | -0.23346 | -0.004577 | 0.054931 | -0.23804 | -0.004577 | -0.064086 | 122.818 | 122.818 | 58.9828 | -122.9416 | 122.8317 | 122.7722 | 59.0332 | -123.0698
333.0156 | 123.1338 | -59.0103 | 63.7985 | -0.0077822 | 0.0014675 | 0.067396 | 0.068808 | 0.13185 | -0.0034949 | -0.0034457 | 0.0074766 | -0.0050672 | 0.062769 | 0.061244 | -0.00027778 | -0.0034286 | 63.8077 | 63.9404 | -0.018311 | -59.2209 | 63.8306 | -59.0744 | -59.1019 | -58.9417 | 0.07782 | -59.2392 | 63.8306 | 63.7665 | -59.1431 | -59.1888 | -0.064087 | -0.091553 | 0.032043 | 122.9507 | -0.21057 | -0.11902 | 0.009155 | -0.13275 | -0.17853 | 0.032043 | 0.068665 | -0.22888 | -0.050354 | -0.032044 | 122.8409 | 122.818 | 58.992 | -122.9004 | 122.8409 | 122.7768 | 59.0881 | -122.9874
334.0156 | 123.1155 | -59.0469 | 63.8077 | 0.13718 | 0.0065945 | 0.067182 | 0.068167 | 0.1295 | 0.00035035 | -0.0043003 | 0.17532 | -0.006349 | 0.062982 | 0.061671 | 0.002713 | -0.0023606 | 63.8214 | 63.9542 | -0.036621 | -59.23 | 63.8214 | -59.0652 | -59.1202 | -58.9691 | 0.032043 | -59.2758 | 63.8306 | 63.7299 | -59.1293 | -59.2712 | -0.018311 | -0.073242 | 0.013733 | 123.0011 | -0.18311 | -0.10986 | 0.013733 | -0.082397 | -0.2243 | 0.022888 | 0.07782 | -0.22888 | -0.004578 | -0.07782 | 122.8683 | 122.8683 | 59.0103 | -122.9279 | 122.8775 | 122.7768 | 59.079 | -123.0789
335.0156 | 123.111 | -59.024 | 63.8077 | 0.38895 | 0.00018591 | 0.068464 | 0.065817 | 0.12864 | -0.0017859 | -0.0040867 | 0.0914 | -0.0059216 | 0.060205 | 0.061885 | 0.00036322 | -0.0047104 | 63.7802 | 63.9267 | -0.041199 | -59.23 | 63.8535 | -59.0744 | -59.1156 | -58.9783 | 0.036621 | -59.2529 | 63.8168 | 63.7711 | -59.1293 | -59.23 | -0.050354 | -0.091553 | 0.045777 | 122.9507 | -0.20599 | -0.11444 | -0.027466 | -0.10529 | -0.20599 | 0.009155 | 0.045777 | -0.22888 | -0.022888 | -0.036621 | 122.8775 | 122.8043 | 58.9828 | -122.9233 | 122.8409 | 122.7951 | 59.0607 | -123.0377
336.0156 | 123.1476 | -59.0149 | 63.7894 | 0.19821 | 0.0059537 | 0.06761 | 0.068381 | 0.13121 | 0.00013675 | -0.0013095 | 0.81619 | -0.0031446 | 0.060846 | 0.061457 | 0.0046356 | -0.0044968 | 63.8443 | 63.9542 | -0.036621 | -59.2484 | 63.8123 | -59.0973 | -59.1431 | -58.9417 | 0.073242 | -59.23 | 63.8031 | 63.7436 | -59.1202 | -59.2072 | -0.082397 | -0.12817 | 0.022888 | 122.9691 | -0.23346 | -0.10529 | 0.054931 | -0.10529 | -0.19226 | 0.013733 | 0.073243 | -0.21515 | -0.022889 | -0.045777 | 122.8271 | 122.8592 | 58.9783 | -122.9324 | 122.818 | 122.7585 | 59.0881 | -122.9965
337.0156 | 123.0743 | -59.0103 | 63.7939 | 0.16006 | 0.0029629 | 0.066328 | 0.069022 | 0.13078 | -0.0041357 | -0.0010959 | 0.16769 | -0.0033582 | 0.062982 | 0.061671 | 0.0033538 | -0.003856 | 63.8077 | 63.9313 | -0.032043 | -59.2255 | 63.8077 | -59.0744 | -59.1156 | -58.9737 | -0.004578 | -59.2575 | 63.8306 | 63.7573 | -59.1293 | -59.2163 | -0.064087 | -0.10529 | 0.013733 | 122.9416 | -0.21515 | -0.10986 | 0.013733 | -0.11902 | -0.20599 | 0.036621 | 0.036621 | -0.24719 | -0.041198 | -0.036621 | 122.818 | 122.818 | 58.9783 | -122.9095 | 122.8409 | 122.7676 | 59.0057 | -123.0103
338.0156 | 123.1522 | -59.024 | 63.7802 | 0.030365 | 0.0057401 | 0.065901 | 0.067526 | 0.13185 | 0.0012047 | -0.0013095 | 0.24399 | -0.0048536 | 0.064691 | 0.063807 | 0.0037812 | -0.004924 | 63.8489 | 63.9587 | -0.018311 | -59.2117 | 63.8306 | -59.0652 | -59.1248 | -58.9371 | 0.036621 | -59.2392 | 63.8306 | 63.7482 | -59.1431 | -59.2255 | -0.041199 | -0.10071 | 0.050354 | 122.9828 | -0.18768 | -0.086975 | 0.068665 | -0.11902 | -0.20142 | 0.050354 | 0.086975 | -0.21515 | -0.013733 | -0.032043 | 122.8546 | 122.8729 | 59.0057 | -122.905 | 122.8546 | 122.7722 | 59.0607 | -123.0057
339.0156 | 123.1018 | -59.0332 | 63.7985 | 0.19821 | 0.00082671 | 0.067396 | 0.068808 | 0.13078 | -0.0054175 | -0.0010959 | 0.0914 | -0.0031446 | 0.061701 | 0.062739 | 0.001004 | -0.0025742 | 63.7939 | 63.9084 | -0.036621 | -59.2072 | 63.8626 | -59.0698 | -59.1156 | -58.9508 | 0.054932 | -59.23 | 63.8306 | 63.7482 | -59.1202 | -59.2117 | -0.036621 | -0.082398 | 0.064087 | 122.9416 | -0.17395 | -0.091552 | -0.004578 | -0.086975 | -0.17853 | 0.032043 | 0.082397 | -0.19684 | -0.018311 | -0.050354 | 122.8958 | 122.8271 | 58.9966 | -122.9141 | 122.8638 | 122.7814 | 59.0881 | -123.0103
340.0156 | 123.111 | -59.0378 | 63.7985 | 0.11429 | 0.0057401 | 0.063978 | 0.067313 | 0.12822 | -0.00093145 | -0.0025913 | 0.24399 | -0.0031446 | 0.062555 | 0.06103 | 0.0048492 | -0.0053512 | 63.858 | 63.9587 | -0.018311 | -59.2209 | 63.8168 | -59.0561 | -59.1202 | -58.9462 | 0.032043 | -59.2575 | 63.8214 | 63.7527 | -59.1339 | -59.2346 | -0.01831 | -0.082397 | 0.01831 | 122.9965 | -0.1831 | -0.10071 | 0.059509 | -0.09613 | -0.19684 | 0.022888 | 0.091553 | -0.21973 | -0.022888 | -0.045776 | 122.8546 | 122.8958 | 59.0195 | -122.9187 | 122.8592 | 122.7905 | 59.0698 | -123.0331
341.0156 | 123.1064 | -59.0103 | 63.8123 | 0.099029 | -0.00088229 | 0.069959 | 0.06774 | 0.13035 | -0.0024269 | -0.0034457 | 0.20584 | -0.0042126 | 0.063196 | 0.062312 | 0.0033538 | -0.0019334 | 63.8214 | 63.8992 | -0.086975 | -59.0561 | 63.8626 | -59.0195 | -59.1156 | -58.9828 | 0.032043 | -59.2484 | 63.8397 | 63.7573 | -59.1614 | -59.2255 | -0.009155 | -0.10529 | 0.050354 | 122.9095 | -0.045776 | 0.05951 | 0.009155 | -0.15106 | -0.21515 | 0.027466 | 0.027466 | -0.23804 | -0.022888 | -0.054932 | 122.8729 | 122.8317 | 58.9233 | -122.9279 | 122.85 | 122.7676 | 59.0424 | -123.0377
342.0156 | 123.1247 | -59.024 | 63.7711 | -0.20615 | 0.0074491 | 0.066755 | 0.070517 | 0.13185 | 0.00099115 | -0.00088226 | 0.2211 | -0.002931 | 0.062982 | 0.060603 | 0.0012176 | -0.005565 | 63.8306 | 63.9587 | -0.022888 | -59.2072 | 63.8123 | -59.0561 | -59.1064 | -58.9417 | 0.045776 | -59.2346 | 63.8168 | 63.7161 | -59.1339 | -59.23 | -0.032043 | -0.082397 | 0.041199 | 122.9828 | -0.1831 | -0.10071 | 0.059509 | -0.10986 | -0.20599 | 0.045776 | 0.082398 | -0.21057 | -0.004577 | -0.054932 | 122.8363 | 122.8546 | 59.0012 | -122.8775 | 122.8409 | 122.7402 | 59.0698 | -123.0011
343.0156 | 123.1155 | -59.0057 | 63.8214 | 0.10666 | 0.0057401 | 0.067823 | 0.066458 | 0.1295 | 0.00099115 | -0.0025913 | 0.16769 | -0.0031446 | 0.061914 | 0.062525 | 0.0022858 | -0.0047104 | 63.7985 | 63.9175 | -0.059509 | -59.2438 | 63.8351 | -59.0652 | -59.1293 | -58.9691 | 0.045776 | -59.2621 | 63.8306 | 63.7527 | -59.1339 | -59.2117 | -0.05951 | -0.1236 | 0.013733 | 122.9233 | -0.23804 | -0.11444 | -0.022888 | -0.12817 | -0.20599 | 0.009155 | 0.036621 | -0.25635 | -0.050354 | -0.068664 | 122.8409 | 122.8043 | 58.9462 | -122.9507 | 122.8363 | 122.7585 | 59.0515 | -123.0331
344.0156 | 123.143 | -59.0195 | 63.7939 | 0.20584 | 0.0063809 | 0.066755 | 0.070517 | 0.13121 | 0.0033411 | -0.0021641 | 0.2211 | -0.0027174 | 0.062982 | 0.061457 | 0.0052764 | -0.003856 | 63.8214 | 63.8763 | -0.10529 | -59.2621 | 63.8718 | -59.1064 | -59.1431 | -58.9554 | 0.022888 | -59.2575 | 63.8214 | 63.7344 | -59.1614 | -59.2392 | -0.086975 | -0.1236 | 0.07782 | 122.8958 | -0.24262 | -0.11902 | 0.027466 | -0.14191 | -0.21973 | 0.027466 | 0.064087 | -0.23804 | -0.01831 | -0.059509 | 122.8912 | 122.8409 | 58.9142 | -122.937 | 122.8409 | 122.7539 | 59.0424 | -123.0331
345.0156 | 123.0927 | -59.0149 | 63.8306 | -0.18326 | 0.0046719 | 0.069319 | 0.068381 | 0.13292 | -0.0022131 | -0.0021641 | -0.17563 | -0.0027174 | 0.061273 | 0.061457 | -0.0011322 | -0.0030014 | 63.8718 | 63.9999 | 0.073242 | -59.1751 | 63.8351 | -59.0149 | -59.111 | -58.9417 | 0.16022 | -59.2346 | 63.8947 | 63.7939 | -59.1156 | -59.2163 | 0 | -0.09613 | 0.004578 | 123.0148 | -0.16022 | -0.064087 | 0.041199 | -0.10071 | -0.20142 | 0.064087 | 0.073243 | -0.21973 | -0.01831 | -0.036621 | 122.85 | 122.8867 | 59.0881 | -122.9416 | 122.9095 | 122.8088 | 59.1751 | -123.0469
346.0156 | 123.1384 | -59.0378 | 63.7756 | 0.12955 | 0.0061673 | 0.065687 | 0.068594 | 0.13185 | 0.00099115 | -0.0013095 | 0.14481 | -0.0035718 | 0.060846 | 0.060176 | 0.0035674 | -0.0034286 | 63.8489 | 63.9816 | -0.022888 | -59.2117 | 63.8168 | -59.0652 | -59.1248 | -58.9371 | 0.050354 | -59.2209 | 63.7939 | 63.7207 | -59.1568 | -59.2438 | -0.027466 | -0.086975 | 0.041198 | 123.0194 | -0.17395 | -0.086975 | 0.073242 | -0.11902 | -0.20599 | 0.01831 | 0.10071 | -0.1831 | 0.022888 | -0.054932 | 122.8546 | 122.8867 | 59.0149 | -122.9004 | 122.8317 | 122.7585 | 59.0881 | -123.0194
347.0156 | 123.1293 | -59.0424 | 63.8031 | 0.11429 | 0.0038175 | 0.068037 | 0.069235 | 0.1295 | -0.0026405 | -0.0015231 | 0.10666 | -0.0033582 | 0.061914 | 0.058894 | 0.0014312 | -0.0040696 | 63.7985 | 63.9221 | -0.041199 | -59.2575 | 63.8214 | -59.0836 | -59.1156 | -58.9737 | 0.027466 | -59.2484 | 63.8397 | 63.7665 | -59.1431 | -59.2117 | -0.041199 | -0.073243 | 0.01831 | 122.9645 | -0.21515 | -0.14191 | -0.004578 | -0.10071 | -0.16937 | 0.036621 | 0.068664 | -0.20599 | -0.036621 | -0.036622 | 122.8638 | 122.8409 | 59.0012 | -122.9187 | 122.8821 | 122.8088 | 59.0698 | -123.0148
348.0156 | 123.1613 | -59.0149 | 63.8031 | 0.11429 | 0.0076627 | 0.066969 | 0.067954 | 0.13313 | -0.0019995 | -0.0023777 | 0.20584 | -0.005708 | 0.063623 | 0.059535 | 0.002713 | -0.0062058 | 63.8397 | 63.9404 | -0.050354 | -59.1843 | 63.8168 | -59.0652 | -59.111 | -58.873 | 0.16022 | -59.2575 | 63.826 | 63.739 | -59.0973 | -59.2072 | -0.050354 | -0.09613 | 0.013732 | 122.9553 | -0.16937 | -0.073242 | 0.036621 | -0.082397 | -0.19226 | 0.022888 | 0.14191 | -0.24261 | -0.050354 | -0.064087 | 122.8317 | 122.8546 | 58.9645 | -122.9141 | 122.8409 | 122.7539 | 59.1751 | -123.0103
349.0469 | 123.0377 | -59.024 | 63.8489 | -0.0077822 | 0.0095853 | 0.06761 | 0.069663 | 0.13377 | 0.0046227 | -0.0025913 | 0.015106 | -0.00229 | 0.067041 | 0.062098 | 0.0042084 | -0.0047104 | 63.8351 | 63.8718 | -0.082397 | -59.2346 | 63.8809 | -59.0836 | -59.1339 | -59.0149 | 0 | -59.3262 | 63.8718 | 63.7939 | -59.1476 | -59.2575 | -0.059509 | -0.10986 | 0.032043 | 122.8958 | -0.21057 | -0.10071 | -0.013733 | -0.1236 | -0.23346 | 0.022888 | 0.009155 | -0.30212 | -0.068665 | -0.054932 | 122.905 | 122.8592 | 58.9417 | -122.9828 | 122.8958 | 122.818 | 59.024 | -123.1064
350.0156 | 123.0789 | -59.0515 | 63.8123 | 0.12192 | 0.0068081 | 0.065473 | 0.069022 | 0.13014 | 0.00035035 | 0.0016811 | 0.18295 | -0.0027174 | 0.062555 | 0.061671 | 0.0016448 | -0.004924 | 63.7665 | 63.8397 | -0.12817 | -59.2712 | 63.8535 | -59.111 | -59.1476 | -59.0012 | -0.050354 | -59.3216 | 63.8672 | 63.7527 | -59.1705 | -59.23 | -0.059509 | -0.09613 | 0.041199 | 122.8912 | -0.21973 | -0.1236 | -0.045777 | -0.11902 | -0.17853 | 0.054931 | 0.050354 | -0.27008 | -0.091552 | -0.059509 | 122.905 | 122.818 | 58.9233 | -122.9599 | 122.9187 | 122.8043 | 59.0012 | -123.0423
351.0156 | 123.1522 | -59.024 | 63.7939 | 0.14481 | 0.0070217 | 0.065687 | 0.066031 | 0.13206 | -0.0019995 | -0.0025913 | 0.90775 | -0.0048536 | 0.061487 | 0.059962 | 0.004422 | -0.0053512 | 63.8351 | 63.9359 | -0.036621 | -59.2438 | 63.7939 | -59.1019 | -59.1431 | -58.9371 | 0.07782 | -59.2438 | 63.8214 | 63.7573 | -59.1431 | -59.2117 | -0.07782 | -0.11902 | 0 | 122.9599 | -0.21973 | -0.10071 | 0.041199 | -0.11902 | -0.18768 | 0.027466 | 0.086975 | -0.21973 | -0.032043 | -0.036621 | 122.818 | 122.8592 | 58.9874 | -122.937 | 122.8455 | 122.7814 | 59.1019 | -123.0057
352.0156 | 123.1613 | -59.0424 | 63.8077 | 0.20584 | 0.0070217 | 0.067182 | 0.069235 | 0.13035 | -0.00093145 | 0.00061314 | 0.27451 | -0.0033582 | 0.062128 | 0.06103 | 0.0042084 | -0.0030014 | 63.8489 | 63.9221 | -0.027466 | -59.2026 | 63.7985 | -59.0881 | -59.1293 | -58.9783 | -0.1831 | -59.1064 | 63.7711 | 63.739 | -59.1385 | -59.2163 | -0.045777 | -0.086975 | -0.009155 | 122.9645 | -0.16022 | -0.073243 | 0.041199 | -0.096131 | -0.17395 | -0.036621 | 0.064087 | -0.064087 | 0.10986 | -0.068664 | 122.8409 | 122.8912 | 59.0149 | -122.937 | 122.8134 | 122.7814 | 58.8593 | -123.024
353.0156 | 123.111 | -59.024 | 63.8077 | 0.12192 | 0.0042447 | 0.066328 | 0.068808 | 0.13334 | -0.0019995 | -0.0034457 | 0.27451 | -0.0033582 | 0.062982 | 0.062739 | 0.002713 | -0.0019334 | 63.8031 | 63.9267 | -0.032043 | -59.2255 | 63.8168 | -59.0652 | -59.1339 | -58.9783 | 0.022888 | -59.2621 | 63.8351 | 63.7619 | -59.1339 | -59.23 | -0.041199 | -0.10986 | 0.009155 | 122.9507 | -0.20142 | -0.091553 | -0.004577 | -0.10986 | -0.20599 | 0.027466 | 0.045777 | -0.23804 | -0.032043 | -0.045776 | 122.8409 | 122.8271 | 58.992 | -122.9416 | 122.8592 | 122.7859 | 59.0469 | -123.0377
354.0156 | 123.1613 | -59.0103 | 63.7985 | 0.21347 | 0.0091581 | 0.06825 | 0.071585 | 0.1327 | -7.6852e-05 | -0.0013095 | 0.19058 | -0.00229 | 0.062342 | 0.061244 | 0.0037812 | -0.0051376 | 63.8306 | 63.9221 | -0.064087 | -59.198 | 63.8443 | -59.0469 | -59.1202 | -58.9417 | 0.027466 | -59.23 | 63.8214 | 63.6978 | -59.166 | -59.2255 | -0.036621 | -0.10986 | 0.045776 | 122.9324 | -0.18768 | -0.07782 | 0.032043 | -0.15564 | -0.21515 | 0.022888 | 0.068665 | -0.21973 | -0.004578 | -0.10071 | 122.8546 | 122.8409 | 58.9462 | -122.9187 | 122.8317 | 122.7081 | 59.0378 | -123.024
355.0156 | 123.1018 | -59.0286 | 63.7939 | 0.17532 | 0.0072355 | 0.06761 | 0.068167 | 0.13078 | -0.0013587 | -0.0040867 | 0.23636 | -0.003999 | 0.059564 | 0.061457 | 0.004422 | -0.0030014 | 63.8306 | 63.9404 | -0.027466 | -59.2209 | 63.7985 | -59.0744 | -59.1248 | -58.96 | 0.013733 | -59.23 | 63.8168 | 63.7665 | -59.1431 | -59.2392 | -0.045777 | -0.096131 | 0.004578 | 122.9691 | -0.19226 | -0.09613 | 0.036621 | -0.11444 | -0.21057 | 0.022888 | 0.068664 | -0.20142 | 0.009155 | -0.027466 | 122.8271 | 122.8592 | 59.0012 | -122.9187 | 122.8455 | 122.7951 | 59.0424 | -123.0331
356.0156 | 123.1247 | -59.0378 | 63.7756 | 0.21347 | 0.0093717 | 0.068678 | 0.069022 | 0.128 | 0.0022729 | -0.00045506 | 0.21347 | -0.0050672 | 0.062128 | 0.060603 | 0.004422 | -0.0036424 | 63.8123 | 63.8535 | -0.10529 | -59.2575 | 63.8535 | -59.0973 | -59.1568 | -58.9828 | -0.018311 | -59.2758 | 63.8306 | 63.7436 | -59.1385 | -59.2346 | -0.059509 | -0.11902 | 0.07782 | 122.8912 | -0.21973 | -0.10071 | 0.036621 | -0.10071 | -0.19684 | 0.054931 | 0.054932 | -0.23804 | -0.041199 | -0.032044 | 122.8912 | 122.85 | 58.9325 | -122.9324 | 122.8683 | 122.7814 | 59.0195 | -123.0103
357.0156 | 123.2162 | -59.0607 | 63.7527 | 0.15244 | 0.0068081 | 0.064405 | 0.067313 | 0.13163 | 0.00077755 | -0.0015231 | 0.21347 | -0.0037854 | 0.06106 | 0.06338 | 0.0039948 | -0.0025742 | 63.8443 | 63.9359 | -0.041199 | -59.2072 | 63.8123 | -59.079 | -59.1476 | -58.9462 | 0.022888 | -59.2392 | 63.8123 | 63.7207 | -59.166 | -59.2529 | -0.01831 | -0.086975 | 0.059509 | 122.9965 | -0.14648 | -0.059509 | 0.091552 | -0.10529 | -0.19226 | 0.059509 | 0.11444 | -0.17853 | 0.013733 | -0.032044 | 122.8729 | 122.905 | 59.0195 | -122.9004 | 122.8729 | 122.7814 | 59.0836 | -123.0057
358.0156 | 123.0057 | -59.0652 | 63.8214 | 0.13718 | 0.0095853 | 0.066328 | 0.067099 | 0.12822 | 0.0048363 | -0.0030185 | 0.09903 | -0.001222 | 0.061701 | 0.06103 | 0.0033538 | -0.0036424 | 64.064 | 63.7207 | -0.20599 | -59.2255 | 63.8901 | -59.0881 | -59.1476 | -59.0424 | -0.064087 | -59.3445 | 63.858 | 63.7939 | -59.166 | -59.2667 | -0.022888 | -0.082397 | 0.068665 | 122.7859 | -0.16022 | -0.07782 | 0.24262 | -0.10071 | -0.20142 | 0.036621 | 0.022889 | -0.27923 | -0.077819 | -0.027466 | 122.9553 | 123.1293 | 58.8593 | -122.9691 | 122.9233 | 122.8592 | 59.0012 | -123.0881
359.0156 | 123.111 | -59.0561 | 63.7939 | 0.16006 | 0.0048855 | 0.06761 | 0.065604 | 0.13228 | -0.0041357 | -0.0021641 | 0.23636 | -0.0027174 | 0.06106 | 0.061244 | 0.004422 | -0.00065157 | 63.826 | 63.9496 | -0.041199 | -59.2163 | 63.8031 | -59.0698 | -59.1156 | -58.9554 | 0.013733 | -59.2667 | 63.7939 | 63.7436 | -59.1339 | -59.2438 | -0.013733 | -0.05951 | 0.009156 | 123.0057 | -0.16022 | -0.10071 | 0.032044 | -0.07782 | -0.18768 | 0 | 0.10071 | -0.21057 | -0.022889 | -0.050354 | 122.8592 | 122.8821 | 59.0149 | -122.9095 | 122.85 | 122.7997 | 59.0698 | -123.0377
360.0156 | 123.1338 | -59.0012 | 63.7756 | 0.20584 | 0.0091581 | 0.065901 | 0.06774 | 0.13121 | 0.00077755 | 0.00018594 | 0.17532 | -0.0048536 | 0.062128 | 0.060603 | 0.0039948 | -0.0053512 | 63.8443 | 63.8992 | -0.073242 | -59.2255 | 63.826 | -59.0973 | -59.1293 | -58.9554 | 0.027466 | -59.2529 | 63.8397 | 63.7299 | -59.1614 | -59.2209 | -0.09613 | -0.12817 | 0.050354 | 122.9004 | -0.2243 | -0.096131 | 0.068664 | -0.16022 | -0.21973 | 0.064087 | 0.045777 | -0.25177 | -0.032044 | -0.045777 | 122.8271 | 122.8455 | 58.9279 | -122.905 | 122.8409 | 122.731 | 59.0286 | -122.9965
361.0156 | 123.111 | -59.0286 | 63.7894 | 0.13718 | 0.0078763 | 0.066969 | 0.068167 | 0.12971 | -0.0032813 | -0.0047275 | 0.27451 | -0.0031446 | 0.062769 | 0.061244 | 0.0029266 | -0.002147 | 63.8397 | 63.9313 | -0.045776 | -59.2255 | 63.8306 | -59.0881 | -59.1248 | -58.9554 | 0.027466 | -59.2438 | 63.7985 | 63.7665 | -59.1431 | -59.2209 | -0.05951 | -0.096131 | 0.041198 | 122.9599 | -0.19684 | -0.10071 | 0.050354 | -0.11444 | -0.19226 | 0.009155 | 0.073242 | -0.21515 | -0.022888 | -0.022889 | 122.8592 | 122.8683 | 58.9828 | -122.9141 | 122.8271 | 122.7951 | 59.0561 | -123.0103
362.0156 | 123.1522 | -59.024 | 63.8031 | 0.19821 | 0.0093717 | 0.064832 | 0.07009 | 0.13185 | 0.00035035 | -0.00045506 | 0.076141 | -0.0031446 | 0.061914 | 0.059107 | 0.0039948 | -0.0053512 | 63.8168 | 63.8855 | -0.073242 | -59.2346 | 63.8351 | -59.0652 | -59.1431 | -58.9554 | 0 | -59.2484 | 63.8306 | 63.7344 | -59.1293 | -59.2346 | -0.041199 | -0.11902 | 0.032043 | 122.9095 | -0.21057 | -0.091553 | 0.013732 | -0.10529 | -0.21057 | 0.027465 | 0.068665 | -0.2243 | -0.013733 | -0.068665 | 122.8592 | 122.8409 | 58.9508 | -122.9462 | 122.8546 | 122.7585 | 59.024 | -123.0377
363.0156 | 123.1247 | -59.0515 | 63.7756 | 0.15244 | 0.0063809 | 0.065687 | 0.066885 | 0.12971 | -0.0017859 | -0.0013095 | 0.25925 | -0.002931 | 0.062982 | 0.061457 | 0.0016448 | -0.0027878 | 63.8306 | 63.945 | -0.032043 | -59.2209 | 63.7894 | -59.0836 | -59.111 | -58.9462 | 0.027466 | -59.2529 | 63.8168 | 63.7802 | -59.1248 | -59.2438 | -0.032043 | -0.059509 | 0.013733 | 122.9965 | -0.16937 | -0.10986 | 0.054931 | -0.073242 | -0.19226 | 0.041198 | 0.10529 | -0.20142 | -0.009156 | 0.004577 | 122.8409 | 122.8821 | 59.0195 | -122.8867 | 122.8683 | 122.8317 | 59.079 | -123.0194
364.0156 | 123.0652 | -59.0332 | 63.8168 | 0.13718 | 0.010653 | 0.066541 | 0.069876 | 0.13014 | 0.0014185 | -0.00045506 | 0.16006 | -0.00229 | 0.065119 | 0.063594 | 0.0020722 | -0.0036424 | 63.7756 | 63.8168 | -0.13275 | -59.2667 | 63.8809 | -59.0881 | -59.1385 | -59.0149 | -0.059509 | -59.3399 | 63.8672 | 63.7711 | -59.1385 | -59.2484 | -0.054932 | -0.10529 | 0.064087 | 122.85 | -0.23346 | -0.12817 | -0.041198 | -0.10529 | -0.21515 | 0.050354 | 0.01831 | -0.3067 | -0.091553 | -0.045776 | 122.9141 | 122.8088 | 58.9005 | -122.9553 | 122.9004 | 122.8043 | 58.9737 | -123.0652
365.0469 | 123.024 | -59.0378 | 63.8672 | -0.15274 | 0.0070217 | 0.065046 | 0.06774 | 0.12971 | -0.00071785 | -0.0015231 | -0.17563 | -0.0035718 | 0.060633 | 0.062525 | 0.0024994 | -0.003856 | 63.7985 | 63.8672 | -0.045776 | -59.2209 | 63.8901 | -59.079 | -59.1248 | -59.0149 | 0.064087 | -59.2941 | 63.9038 | 63.8214 | -59.1385 | -59.2163 | -0.041198 | -0.086975 | 0.022889 | 122.905 | -0.1831 | -0.09613 | -0.068664 | -0.10071 | -0.17853 | 0.036622 | 0.022888 | -0.25635 | -0.077819 | -0.045776 | 122.9279 | 122.8363 | 58.992 | -122.9919 | 122.9416 | 122.8592 | 59.1019 | -123.0835
366.0156 | 123.143 | -59.0195 | 63.7802 | 0.17532 | 0.0074491 | 0.066541 | 0.068167 | 0.12928 | -0.00093145 | -0.0017369 | 0.045624 | -0.0031446 | 0.062342 | 0.06103 | 0.001004 | -0.0027878 | 63.8351 | 63.9359 | -0.19684 | -59.2987 | 63.7711 | -59.0973 | -59.1293 | -58.9371 | 0.018311 | -59.2255 | 63.8214 | 63.7527 | -59.1385 | -59.2346 | -0.07782 | -0.10986 | -0.009155 | 122.9553 | -0.27924 | -0.16937 | 0.054932 | -0.11902 | -0.21515 | 0.041199 | 0.082397 | -0.20599 | 0.009155 | -0.027465 | 122.7905 | 122.8546 | 58.8226 | -122.9095 | 122.8409 | 122.7722 | 59.0378 | -123.0148
367.0156 | 123.0789 | -59.0332 | 63.8214 | 0.0914 | 0.0040311 | 0.065046 | 0.068594 | 0.13078 | -0.0041357 | -0.0036595 | 0.25162 | -0.0069898 | 0.064051 | 0.062312 | 0.00036322 | -0.003856 | 63.7939 | 63.8992 | -0.050354 | -59.23 | 63.8443 | -59.0561 | -59.1019 | -58.9737 | 0.013733 | -59.2575 | 63.858 | 63.7482 | -59.1202 | -59.2438 | -0.022888 | -0.068665 | 0.022888 | 122.9324 | -0.19684 | -0.12817 | -0.027466 | -0.086975 | -0.21057 | 0.036621 | 0.059509 | -0.2243 | -0.013733 | -0.073242 | 122.8775 | 122.8271 | 58.9828 | -122.9233 | 122.8912 | 122.7814 | 59.0469 | -123.0652
368.0156 | 123.1384 | -59.0332 | 63.7848 | 0.19821 | 0.0074491 | 0.06825 | 0.068594 | 0.12993 | -0.00093145 | -0.0023777 | -0.053558 | -0.0042126 | 0.061701 | 0.060389 | 0.0035674 | -0.0027878 | 63.9359 | 63.6658 | -0.16937 | -59.1431 | 63.7939 | -59.0652 | -59.1202 | -58.9508 | 0.018311 | -59.23 | 63.826 | 63.739 | -59.1522 | -59.23 | -0.032044 | -0.086975 | 0.009155 | 122.699 | -0.10986 | -0.022888 | 0.15106 | -0.11902 | -0.19684 | 0.041199 | 0.082397 | -0.19684 | 0 | -0.045776 | 122.8271 | 122.9691 | 58.8638 | -122.905 | 122.8592 | 122.7722 | 59.0515 | -123.0148
369.0156 | 123.0835 | -59.0103 | 63.8077 | 0.0914 | 0.0027493 | 0.066541 | 0.066672 | 0.13014 | -0.0043495 | -0.0053683 | 0.16769 | -0.0037854 | 0.062555 | 0.060603 | 0.0012176 | -0.0030014 | 63.8123 | 63.8763 | -0.068665 | -59.2392 | 63.8535 | -59.0561 | -59.111 | -58.9783 | 0.018311 | -59.2484 | 63.8306 | 63.7939 | -59.1293 | -59.2392 | -0.045776 | -0.10071 | 0.045777 | 122.8867 | -0.22888 | -0.12817 | 0.004578 | -0.11902 | -0.22888 | 0.022888 | 0.032044 | -0.23804 | -0.009155 | -0.013733 | 122.8638 | 122.8226 | 58.9416 | -122.9187 | 122.8409 | 122.8043 | 59.0286 | -123.0469
370.0156 | 123.1705 | -59.0195 | 63.7985 | 0.2211 | 0.0091581 | 0.066541 | 0.069449 | 0.13099 | 0.0018457 | -0.00066866 | 0.19058 | -0.0037854 | 0.061914 | 0.062739 | 0.0046356 | -0.0044968 | 63.7024 | 64.1281 | 0.09613 | -59.1888 | 63.8123 | -59.0927 | -59.1156 | -58.9325 | 0.027466 | -59.23 | 63.8031 | 63.7665 | -59.1522 | -59.2255 | -0.073242 | -0.096131 | 0.013733 | 123.1476 | -0.16937 | -0.073242 | -0.09613 | -0.13275 | -0.20599 | 0.004578 | 0.086975 | -0.21057 | -0.004578 | -0.032044 | 122.8317 | 122.7219 | 59.1156 | -122.9141 | 122.8226 | 122.7859 | 59.0469 | -123.024
371.0156 | 123.111 | -59.0332 | 63.7802 | 0.12192 | 0.0025357 | 0.066328 | 0.067313 | 0.13206 | -0.0024269 | -0.0049411 | 0.24399 | -0.003999 | 0.063196 | 0.061885 | 0.0024994 | -0.0025742 | 63.8351 | 63.9496 | -0.027466 | -59.2163 | 63.8123 | -59.0652 | -59.1293 | -58.9508 | 0.027466 | -59.2621 | 63.8077 | 63.7299 | -59.1339 | -59.2209 | -0.032044 | -0.09613 | 0.032044 | 122.9828 | -0.18311 | -0.086976 | 0.054932 | -0.10071 | -0.18768 | 0.027466 | 0.082397 | -0.22888 | -0.041199 | -0.050354 | 122.8455 | 122.8683 | 59.0057 | -122.9095 | 122.8409 | 122.7631 | 59.0607 | -123.0011
372.0156 | 123.1338 | -59.0057 | 63.7665 | 0.19821 | 0.0093717 | 0.06761 | 0.068594 | 0.13057 | 0.00035035 | -0.0025913 | 0.21347 | -0.0025038 | 0.061914 | 0.060389 | 0.0033538 | -0.0057786 | 63.8214 | 63.8947 | -0.086975 | -59.2072 | 63.8306 | -59.0698 | -59.1339 | -58.9371 | 0.013733 | -59.2529 | 63.858 | 63.7436 | -59.1568 | -59.23 | -0.064087 | -0.12817 | 0.064087 | 122.9004 | -0.20142 | -0.073242 | 0.054932 | -0.15106 | -0.2243 | 0.091553 | 0.068664 | -0.24719 | -0.022888 | -0.022888 | 122.8363 | 122.8271 | 58.9188 | -122.9004 | 122.8638 | 122.7493 | 59.0195 | -122.9965
373.0156 | 123.1064 | -59.0103 | 63.8077 | 0.13718 | 0.0016813 | 0.066541 | 0.070517 | 0.12971 | -0.0054175 | -0.0034457 | 0.11429 | -0.0048536 | 0.061273 | 0.062312 | 0.0022858 | -0.0023606 | 63.7985 | 63.913 | -0.068665 | -59.2255 | 63.858 | -59.0607 | -59.1476 | -58.9737 | 0.054932 | -59.2484 | 63.8443 | 63.7802 | -59.1339 | -59.2072 | -0.050354 | -0.13733 | 0.050354 | 122.9233 | -0.21515 | -0.07782 | -0.009155 | -0.1236 | -0.19684 | 0.036621 | 0.036621 | -0.23804 | -0.041199 | -0.027466 | 122.8683 | 122.8088 | 58.9416 | -122.9553 | 122.8546 | 122.7905 | 59.0652 | -123.0148
374.0156 | 123.0286 | -59.0057 | 63.8626 | -0.22903 | 0.0036039 | 0.067182 | 0.068167 | 0.13334 | -0.00093145 | -0.0023777 | -0.17563 | -0.0069898 | 0.062982 | 0.062739 | 0.0046356 | -0.005565 | 63.858 | 63.9542 | 0.045776 | -59.198 | 63.8763 | -59.0195 | -59.0881 | -58.992 | 0.10071 | -59.2621 | 63.913 | 63.8214 | -59.1293 | -59.2255 | -0.013733 | -0.082398 | 0.013733 | 122.9599 | -0.19226 | -0.10986 | -0.004578 | -0.1236 | -0.21973 | 0.050354 | 0.013733 | -0.25635 | -0.036621 | -0.041199 | 122.8821 | 122.8638 | 59.0515 | -122.9507 | 122.9187 | 122.8271 | 59.1064 | -123.0881
375.0156 | 123.1384 | -59.0195 | 63.8214 | 0.28213 | 0.0038175 | 0.065687 | 0.06774 | 0.13035 | -0.0041357 | -0.0023777 | 0.12955 | -0.0052808 | 0.060846 | 0.060816 | 0.0012176 | -0.0025742 | 63.7711 | 63.9038 | -0.054932 | -59.23 | 63.8535 | -59.0698 | -59.1339 | -58.9874 | 0.036621 | -59.2529 | 63.8443 | 63.7711 | -59.1248 | -59.23 | -0.050354 | -0.11444 | 0.032044 | 122.9233 | -0.21057 | -0.096131 | -0.050354 | -0.10529 | -0.21057 | 0.022888 | 0.032043 | -0.23346 | -0.022888 | -0.050354 | 122.8729 | 122.7905 | 58.9645 | -122.9553 | 122.8638 | 122.7905 | 59.0561 | -123.0515
376.0156 | 123.111 | -59.0424 | 63.8077 | 0.13718 | 0.0080899 | 0.06825 | 0.070944 | 0.13163 | -0.00029045 | -0.00066866 | 0.21347 | -0.0044264 | 0.061701 | 0.06103 | 0.0016448 | -0.004924 | 63.826 | 63.9587 | -0.022888 | -59.2255 | 63.8168 | -59.0652 | -59.1385 | -58.9462 | 0.022888 | -59.2438 | 63.8031 | 63.7207 | -59.1522 | -59.2209 | -0.022889 | -0.096131 | 0.009155 | 123.0011 | -0.18311 | -0.086975 | 0.018311 | -0.10986 | -0.17853 | -0.004577 | 0.09613 | -0.20142 | -0.022888 | -0.086975 | 122.8592 | 122.8683 | 59.0195 | -122.9462 | 122.8455 | 122.7631 | 59.0652 | -123.0286
377.0156 | 123.1293 | -59.0195 | 63.7985 | 0.41183 | 0.0053129 | 0.067182 | 0.069022 | 0.12864 | -0.0028541 | -0.0028049 | 0.10666 | -0.005708 | 0.061914 | 0.059748 | 0.0018584 | -0.0042832 | 63.7894 | 63.9038 | -0.050354 | -59.2255 | 63.8351 | -59.0607 | -59.1385 | -58.9737 | 0.022888 | -59.2484 | 63.858 | 63.7527 | -59.1293 | -59.2255 | -0.041199 | -0.11902 | 0.036621 | 122.9233 | -0.20599 | -0.086975 | -0.009155 | -0.10986 | -0.20599 | 0.059509 | 0.045776 | -0.22888 | -0.022888 | -0.045776 | 122.8546 | 122.8088 | 58.9691 | -122.937 | 122.8775 | 122.7722 | 59.0424 | -123.024
378.0156 | 123.1613 | -59.0103 | 63.7756 | 0.17532 | 0.0072355 | 0.065687 | 0.068594 | 0.13228 | 0.0014185 | -0.0015231 | -0.091705 | -0.00464 | 0.061914 | 0.06103 | 0.0048492 | -0.0053512 | 63.8626 | 63.9542 | -0.1831 | -59.2804 | 63.7711 | -59.0881 | -59.1248 | -58.9142 | 0.018311 | -59.2438 | 63.7985 | 63.7024 | -59.1476 | -59.2209 | -0.07782 | -0.11444 | -0.004578 | 122.9645 | -0.27008 | -0.15564 | 0.086975 | -0.13733 | -0.21057 | 0.022888 | 0.09613 | -0.23346 | -0.022888 | -0.073242 | 122.7814 | 122.8729 | 58.8272 | -122.9004 | 122.8088 | 122.7127 | 59.0286 | -122.9965
379.0156 | 123.0331 | -59.0332 | 63.8535 | -0.12985 | 0.0068081 | 0.067182 | 0.070517 | 0.13121 | -0.00050425 | -0.0023777 | -0.23666 | -0.0020764 | 0.064051 | 0.063594 | 0.0012176 | -0.0057786 | 63.8168 | 63.9038 | -0.018311 | -59.2392 | 63.9221 | -59.0561 | -59.111 | -59.0012 | 0.045776 | -59.2758 | 63.9084 | 63.8443 | -59.1385 | -59.2072 | -0.022888 | -0.07782 | 0.068664 | 122.937 | -0.20599 | -0.12817 | -0.036622 | -0.10529 | -0.17395 | 0.054931 | 0.032043 | -0.24262 | -0.068665 | -0.009156 | 122.9553 | 122.85 | 59.0149 | -122.9645 | 122.9416 | 122.8775 | 59.079 | -123.0606
380.0156 | 123.1384 | -59.0332 | 63.8306 | 0.12192 | 0.0048855 | 0.068037 | 0.067954 | 0.1295 | -0.0041357 | -0.0021641 | 0.24399 | -0.0031446 | 0.061487 | 0.060603 | 0.0033538 | -0.0047104 | 63.7894 | 63.9267 | -0.050354 | -59.2392 | 63.8168 | -59.0561 | -59.0927 | -58.9737 | 0.022888 | -59.2529 | 63.8214 | 63.7344 | -59.1248 | -59.2255 | -0.022888 | -0.059509 | -0.013733 | 122.9599 | -0.20599 | -0.14648 | -0.041198 | -0.091553 | -0.19226 | -0.009155 | 0.059509 | -0.21973 | -0.027466 | -0.09613 | 122.85 | 122.8226 | 58.9828 | -122.9233 | 122.8546 | 122.7676 | 59.0561 | -123.056
381.0156 | 123.1064 | -59.0149 | 63.8397 | -0.015411 | 0.0016813 | 0.067396 | 0.067313 | 0.13035 | -0.0028541 | -0.0049411 | 0.015106 | -0.0042126 | 0.063623 | 0.059962 | 0.0022858 | -0.003215 | 63.7985 | 63.9359 | -0.022888 | -59.2117 | 63.858 | -59.0469 | -59.111 | -58.9508 | 0.086975 | -59.2026 | 63.8489 | 63.7527 | -59.1293 | -59.2163 | -0.032043 | -0.09613 | 0.01831 | 122.9507 | -0.19684 | -0.10071 | -0.041199 | -0.11444 | -0.20142 | 0.009155 | 0.064087 | -0.18768 | 0.013733 | -0.086975 | 122.8729 | 122.8134 | 58.992 | -122.9507 | 122.8638 | 122.7676 | 59.1019 | -123.056
382.0156 | 123.1018 | -59.0378 | 63.7939 | 0.14481 | 0.0036039 | 0.06761 | 0.067099 | 0.13035 | -0.0019995 | -0.0025913 | 0.19058 | -0.0044264 | 0.063837 | 0.062953 | 0.0031402 | -0.0027878 | 63.8077 | 63.9313 | -0.059509 | -59.2346 | 63.8031 | -59.079 | -59.1248 | -58.96 | 0.009155 | -59.285 | 63.8397 | 63.7344 | -59.1522 | -59.2117 | -0.041198 | -0.086975 | 0.009156 | 122.9691 | -0.19684 | -0.10986 | 0.013733 | -0.11444 | -0.17395 | 0.045777 | 0.07782 | -0.24719 | -0.073242 | -0.059509 | 122.8409 | 122.8455 | 58.9783 | -122.9187 | 122.8775 | 122.7722 | 59.0469 | -123.0057
383.0156 | 123.1064 | -59.0149 | 63.8123 | 0.030365 | 0.00082671 | 0.067823 | 0.066672 | 0.12928 | -0.0022131 | -0.0028049 | 0.0074766 | -0.0044264 | 0.060205 | 0.059321 | 0.0016448 | -0.0040696 | 63.8077 | 63.9175 | -0.018311 | -59.2209 | 63.8489 | -59.0378 | -59.1248 | -58.9508 | 0.091553 | -59.2209 | 63.8535 | 63.7482 | -59.0927 | -59.2163 | -0.022888 | -0.10986 | 0.036621 | 122.9324 | -0.20599 | -0.09613 | -0.004578 | -0.077819 | -0.20142 | 0.041199 | 0.064087 | -0.20599 | -0.004577 | -0.064087 | 122.8638 | 122.8226 | 58.9966 | -122.937 | 122.8683 | 122.7631 | 59.1064 | -123.0286
384.0156 | 123.1018 | -59.024 | 63.8306 | -0.18326 | 0.0044583 | 0.06761 | 0.066458 | 0.13313 | 0.00013675 | -0.0028049 | -0.168 | -0.006349 | 0.060633 | 0.060176 | 0.002713 | -0.004924 | 63.8718 | 64.0137 | 0.073242 | -59.1705 | 63.8535 | -59.0469 | -59.111 | -58.9371 | 0.15106 | -59.2026 | 63.8855 | 63.7848 | -59.1064 | -59.1888 | -0.022888 | -0.086975 | 0.022889 | 123.0377 | -0.14648 | -0.059509 | 0.041199 | -0.082397 | -0.16479 | 0.054932 | 0.086975 | -0.17853 | -0.013733 | -0.045776 | 122.8775 | 122.8958 | 59.0973 | -122.9416 | 122.9095 | 122.8088 | 59.1751 | -123.0194
385.0156 | 123.0881 | -59.0286 | 63.7848 | 0.0914 | 0.0029629 | 0.068464 | 0.07009 | 0.13121 | -7.6852e-05 | -0.0019505 | 0.083771 | -0.005708 | 0.062769 | 0.058467 | 0.002713 | -0.0044968 | 63.7848 | 63.9359 | -0.064087 | -59.23 | 63.8397 | -59.0652 | -59.1019 | -58.9828 | 0.041199 | -59.0927 | 63.8763 | 63.7802 | -59.1156 | -59.2438 | -0.036622 | -0.073243 | 0.054932 | 122.9645 | -0.20142 | -0.12817 | 0 | -0.086976 | -0.21515 | 0.091553 | 0.045776 | -0.064087 | 0.15106 | -0.004578 | 122.8683 | 122.8134 | 58.9645 | -122.8867 | 122.905 | 122.8088 | 59.0698 | -123.0286
386.0156 | 123.0972 | -59.0424 | 63.7985 | 0.16006 | 0.0044583 | 0.065046 | 0.069663 | 0.12758 | -0.0017859 | -0.0028049 | 0.20584 | -0.0027174 | 0.062128 | 0.061244 | 0.0035674 | -0.003856 | 63.8351 | 63.9542 | -0.036621 | -59.2346 | 63.8214 | -59.0836 | -59.1339 | -58.9462 | 0.013733 | -59.2438 | 63.8397 | 63.707 | -59.1385 | -59.2438 | -0.041199 | -0.091553 | 0.022888 | 122.9965 | -0.19226 | -0.10071 | 0.036621 | -0.096131 | -0.20142 | 0.041199 | 0.09613 | -0.20142 | 0 | -0.091553 | 122.8638 | 122.8775 | 59.0057 | -122.9324 | 122.8821 | 122.7493 | 59.0561 | -123.0423
387.0156 | 123.1338 | -58.9874 | 63.8077 | -0.076447 | 0.0012539 | 0.06761 | 0.066031 | 0.13078 | -0.0028541 | -0.0028049 | -0.023041 | -0.0050672 | 0.059778 | 0.060816 | 0.0022858 | -0.0053512 | 63.8535 | 63.9496 | -0.004578 | -59.1843 | 63.8672 | -59.0515 | -59.0881 | -58.905 | 0.11444 | -59.198 | 63.8443 | 63.7527 | -59.1293 | -59.198 | -0.064087 | -0.10071 | 0.059509 | 122.937 | -0.19684 | -0.09613 | 0.045777 | -0.14191 | -0.21057 | 0.036621 | 0.082398 | -0.21057 | 0 | -0.054931 | 122.8546 | 122.8409 | 58.9828 | -122.8958 | 122.8317 | 122.7402 | 59.1019 | -123.0057
388.0156 | 123.056 | -59.024 | 63.826 | 0.083771 | 0.0033901 | 0.068464 | 0.068594 | 0.13185 | -0.0043495 | -0.0010959 | 0.13718 | -0.0048536 | 0.058069 | 0.058253 | 0.0033538 | -0.004924 | 63.8077 | 63.913 | -0.064087 | -59.2392 | 63.8168 | -59.0469 | -59.1202 | -58.9554 | 0.032043 | -59.2484 | 63.8489 | 63.7436 | -59.1385 | -59.23 | -0.022888 | -0.09613 | -0.009156 | 122.937 | -0.21515 | -0.11902 | -0.018311 | -0.11444 | -0.20599 | 0.022888 | 0.068665 | -0.2243 | -0.01831 | -0.082398 | 122.8409 | 122.8317 | 58.96 | -122.9462 | 122.8729 | 122.7676 | 59.0561 | -123.056
389.0156 | 123.0743 | -59.0332 | 63.8351 | -0.22141 | 0.0093717 | 0.065687 | 0.071158 | 0.13398 | 0.0044091 | -2.7856e-05 | -0.18326 | -0.0033582 | 0.065332 | 0.058894 | 0.0035674 | -0.0074876 | 63.8443 | 63.9175 | -0.009155 | -59.1888 | 63.9038 | -59.0698 | -59.1293 | -58.96 | 0.050354 | -59.2804 | 63.8901 | 63.7894 | -59.1431 | -59.2163 | -0.036621 | -0.09613 | 0.068665 | 122.9507 | -0.15564 | -0.05951 | 0.009155 | -0.10986 | -0.18311 | 0.054932 | 0.073242 | -0.24719 | -0.064087 | -0.045776 | 122.937 | 122.8775 | 59.024 | -122.9645 | 122.9233 | 122.8226 | 59.0836 | -123.0515
390.0156 | 123.0698 | -59.0286 | 63.7985 | 0.14481 | 0.0042447 | 0.06825 | 0.065604 | 0.13057 | -0.0037085 | -0.0032321 | 0.23636 | -0.0050672 | 0.061273 | 0.062098 | 0.0039948 | -0.004924 | 63.7848 | 63.9313 | -0.045776 | -59.2392 | 63.8214 | -59.0698 | -59.1431 | -58.9691 | 0.036621 | -59.2575 | 63.8626 | 63.7344 | -59.1431 | -59.2392 | -0.041199 | -0.11444 | 0.022888 | 122.9599 | -0.21057 | -0.096131 | -0.013733 | -0.11444 | -0.21057 | 0.064087 | 0.059509 | -0.22888 | -0.01831 | -0.064087 | 122.85 | 122.8134 | 58.9828 | -122.9416 | 122.8912 | 122.7631 | 59.0652 | -123.0377
391.0156 | 123.1567 | -58.9966 | 63.8214 | -0.045929 | 0.0027493 | 0.068037 | 0.069022 | 0.12843 | -0.0045631 | -0.0017369 | 0.053253 | -0.0050672 | 0.062555 | 0.061885 | 0.0012176 | -0.0042832 | 63.8123 | 63.9633 | 0.004578 | -59.1843 | 63.8443 | -59.0607 | -59.1202 | -58.9279 | 0.091553 | -59.2026 | 63.8306 | 63.7436 | -59.1339 | -59.2209 | -0.064087 | -0.1236 | 0.022888 | 122.9599 | -0.18768 | -0.064087 | -0.009155 | -0.13733 | -0.2243 | 0.009155 | 0.068665 | -0.20599 | 0.01831 | -0.07782 | 122.8409 | 122.8088 | 59.0012 | -122.9416 | 122.8271 | 122.7402 | 59.0881 | -123.0423
392.0156 | 123.1155 | -59.0103 | 63.7894 | 0.16006 | 0.0072355 | 0.065687 | 0.069022 | 0.13228 | -0.00050425 | -0.0021641 | 0.16769 | -0.0042126 | 0.060633 | 0.059321 | 0.0031402 | -0.0036424 | 63.8397 | 63.9587 | -0.027466 | -59.2163 | 63.8031 | -59.079 | -59.1431 | -58.9188 | 0.032043 | -59.2209 | 63.7985 | 63.7024 | -59.1476 | -59.2438 | -0.068664 | -0.13275 | 0.013733 | 122.9691 | -0.20599 | -0.073243 | 0.050354 | -0.13733 | -0.23346 | 0.009155 | 0.091553 | -0.21057 | 0.022888 | -0.086975 | 122.8134 | 122.85 | 58.9828 | -122.9324 | 122.8088 | 122.7127 | 59.0424 | -123.0331
393.0156 | 123.0743 | -58.992 | 63.7939 | -0.023041 | 0.0046719 | 0.065687 | 0.068808 | 0.1327 | -0.0017859 | -0.0040867 | -0.2214 | -0.0054944 | 0.063837 | 0.060176 | 0.0035674 | -0.0036424 | 63.7939 | 63.913 | -0.054932 | -59.2987 | 63.8626 | -59.0561 | -59.1156 | -58.9874 | 0.041199 | -59.2484 | 63.8443 | 63.7665 | -59.1476 | -59.2209 | -0.064087 | -0.1236 | 0.068665 | 122.905 | -0.3067 | -0.18311 | 0 | -0.15564 | -0.22888 | 0.050354 | 0.004577 | -0.25635 | -0.027466 | -0.027466 | 122.8546 | 122.7859 | 58.9371 | -122.9095 | 122.8363 | 122.7585 | 59.0332 | -123.0148
394.0156 | 123.0148 | -59.0057 | 63.8626 | 0.015106 | 0.0057401 | 0.065046 | 0.069449 | 0.13142 | 0.0020593 | -0.0017369 | -0.23666 | -0.0016492 | 0.061914 | 0.06103 | 0.0022858 | -0.004924 | 63.7619 | 63.8901 | -0.045776 | -59.2484 | 63.8901 | -59.0973 | -59.1202 | -59.0286 | 0.054932 | -59.3079 | 63.9313 | 63.8214 | -59.1476 | -59.23 | -0.091553 | -0.11444 | 0.027466 | 122.8958 | -0.24261 | -0.12817 | -0.10071 | -0.14191 | -0.2243 | 0.068664 | -0.022888 | -0.30212 | -0.077819 | -0.041199 | 122.8958 | 122.7676 | 58.96 | -122.9828 | 122.937 | 122.8271 | 59.0607 | -123.0927
395.0156 | 123.1476 | -58.9737 | 63.8168 | -0.084076 | 0.0010403 | 0.066969 | 0.068167 | 0.12864 | -0.0028541 | -0.0023777 | 0.037995 | -0.0033582 | 0.061273 | 0.060816 | 0.00036322 | -0.0047104 | 63.8351 | 63.9999 | 0.032043 | -59.1934 | 63.8489 | -59.0424 | -59.0927 | -58.8959 | 0.16022 | -59.1614 | 63.8489 | 63.7527 | -59.0927 | -59.2026 | -0.068664 | -0.11902 | 0.032044 | 122.9736 | -0.21973 | -0.10071 | 0.018311 | -0.11902 | -0.22888 | 0.032044 | 0.07782 | -0.18768 | 0.041199 | -0.064086 | 122.8226 | 122.8088 | 59.0057 | -122.9095 | 122.8226 | 122.7264 | 59.1339 | -123.0194
396.0156 | 123.0789 | -59.0149 | 63.7802 | -0.015411 | 0.0021085 | 0.068037 | 0.069235 | 0.12758 | -0.0024269 | -0.0036595 | 0.14481 | -0.0042126 | 0.062128 | 0.059962 | 0.0022858 | -0.003856 | 63.7802 | 63.9175 | -0.045776 | -59.2163 | 63.8535 | -59.0698 | -59.0973 | -58.9737 | 0.022888 | -59.1019 | 63.8672 | 63.7848 | -59.1156 | -59.2117 | -0.054931 | -0.082397 | 0.073243 | 122.9324 | -0.20142 | -0.11902 | 0 | -0.10071 | -0.19684 | 0.086975 | 0.041199 | -0.086975 | 0.10986 | 0.004578 | 122.8683 | 122.7951 | 58.9691 | -122.8775 | 122.8821 | 122.7997 | 59.0378 | -122.9919
397.0156 | 123.1338 | -58.9874 | 63.8031 | -0.03067 | 0.0046719 | 0.066328 | 0.069235 | 0.12928 | -0.0013587 | -0.0034457 | -0.0077819 | -0.0014356 | 0.061273 | 0.061671 | 0.00079042 | -0.005565 | 63.826 | 63.9816 | 0.032043 | -59.1843 | 63.8443 | -59.0469 | -59.1156 | -58.8913 | 0.13275 | -59.1888 | 63.8443 | 63.739 | -59.1248 | -59.2072 | -0.059509 | -0.12817 | 0.041198 | 122.9691 | -0.19684 | -0.068664 | 0.022888 | -0.13733 | -0.21973 | 0.041198 | 0.096131 | -0.20142 | 0.01831 | -0.064087 | 122.8317 | 122.8134 | 59.0195 | -122.9187 | 122.8317 | 122.7264 | 59.1202 | -123.0103
398.0156 | 123.0698 | -59.0424 | 63.7848 | 0.14481 | 0.0044583 | 0.065473 | 0.068167 | 0.13142 | -0.00029045 | -0.0015231 | 0.19058 | -0.005708 | 0.062982 | 0.061885 | 0.0016448 | -0.0051376 | 63.826 | 63.9587 | -0.036621 | -59.2255 | 63.7985 | -59.0744 | -59.1385 | -58.9371 | 0.041199 | -59.2438 | 63.826 | 63.7024 | -59.1385 | -59.2438 | -0.032044 | -0.096131 | 0.013733 | 123.0011 | -0.18311 | -0.086975 | 0.041199 | -0.096131 | -0.20142 | 0.041199 | 0.10529 | -0.20142 | 0 | -0.082397 | 122.8409 | 122.8683 | 59.0057 | -122.9233 | 122.8683 | 122.7448 | 59.0836 | -123.0286
399.0156 | 123.1247 | -59.0012 | 63.7985 | -1.2895 | 0.0031765 | 0.065687 | 0.068167 | 0.12971 | -0.0015723 | -0.0025913 | 0.09903 | -0.0048536 | 0.062128 | 0.062953 | 0.0022858 | -0.0051376 | 63.7665 | 63.9175 | -0.041199 | -59.2209 | 63.8763 | -59.0607 | -59.1293 | -58.9691 | 0.036621 | -59.2438 | 63.8397 | 63.7482 | -59.1431 | -59.2209 | -0.059509 | -0.12817 | 0.07782 | 122.9187 | -0.21973 | -0.091553 | -0.032044 | -0.14191 | -0.21973 | 0.041199 | 0.032044 | -0.24261 | -0.022888 | -0.050354 | 122.8775 | 122.7676 | 58.96 | -122.9279 | 122.8409 | 122.7493 | 59.0378 | -123.0194
400.0156 | 123.0606 | -59.024 | 63.8031 | 0.015106 | 0.0023221 | 0.068891 | 0.067099 | 0.13057 | -0.00071785 | -0.0017369 | 0.076141 | -0.003999 | 0.060846 | 0.060389 | 0.00057682 | -0.0042832 | 63.6383 | 63.9542 | -0.032043 | -59.2529 | 63.8535 | -59.079 | -59.1522 | -58.9691 | 0.045776 | -59.2484 | 63.8489 | 63.7482 | -59.1293 | -59.2117 | -0.054931 | -0.12817 | 0.050354 | 122.9782 | -0.22888 | -0.10071 | -0.16479 | -0.10529 | -0.18768 | 0.045776 | 0.054932 | -0.2243 | -0.036621 | -0.054932 | 122.8775 | 122.6624 | 58.992 | -122.9553 | 122.8729 | 122.7722 | 59.0698 | -123.0148
401.0156 | 123.1705 | -58.9966 | 63.8077 | -0.084076 | 0.0055265 | 0.067823 | 0.07009 | 0.13035 | -0.0041357 | -0.0049411 | -0.12985 | -0.005708 | 0.06106 | 0.059321 | 0.001004 | -0.0051376 | 63.858 | 63.9999 | 0.041199 | -59.1751 | 63.826 | -59.0378 | -59.1156 | -58.873 | 0.17395 | -59.1431 | 63.8443 | 63.7299 | -59.1064 | -59.2072 | -0.041199 | -0.11902 | 0.018311 | 122.9965 | -0.17853 | -0.059509 | 0.050354 | -0.10986 | -0.21057 | 0.036621 | 0.1236 | -0.14648 | 0.064087 | -0.07782 | 122.8226 | 122.8546 | 59.0378 | -122.9233 | 122.8409 | 122.7264 | 59.1705 | -123.0148
402.0156 | 123.0927 | -59.0149 | 63.8168 | 0.045624 | 0.0036039 | 0.064405 | 0.06774 | 0.12864 | -0.0032813 | -0.0023777 | -0.14511 | -0.0037854 | 0.062982 | 0.06103 | 0.0018584 | -0.0057786 | 63.8031 | 63.9221 | -0.032043 | -59.1843 | 63.8718 | -59.0515 | -59.0973 | -58.992 | 0.027466 | -59.2621 | 63.858 | 63.7253 | -59.1156 | -59.23 | -0.036621 | -0.082397 | 0.054932 | 122.937 | -0.16937 | -0.086975 | -0.013732 | -0.10071 | -0.21515 | 0.041199 | 0.022889 | -0.24719 | -0.032043 | -0.091552 | 122.8867 | 122.818 | 58.9828 | -122.9141 | 122.8729 | 122.7402 | 59.0424 | -123.0469
403.0156 | 123.1567 | -59.0103 | 63.8077 | -0.061188 | 0.0040311 | 0.066755 | 0.069663 | 0.13014 | -0.0019995 | -0.0032321 | 0.015106 | -0.0061352 | 0.059351 | 0.061457 | 0.002713 | -0.0040696 | 63.8535 | 63.9771 | 0.022888 | -59.1797 | 63.8672 | -59.0607 | -59.0927 | -58.8821 | 0.14648 | -59.1614 | 63.8672 | 63.7344 | -59.0927 | -59.1888 | -0.050354 | -0.082397 | 0.059509 | 122.9874 | -0.16937 | -0.086975 | 0.045777 | -0.082397 | -0.17853 | 0.059509 | 0.12817 | -0.15106 | 0.027466 | -0.073242 | 122.8775 | 122.8638 | 59.0332 | -122.9004 | 122.8775 | 122.7448 | 59.1568 | -122.9965
404.0156 | 123.111 | -59.0103 | 63.8077 | 0.0914 | 0.0048855 | 0.066541 | 0.068167 | 0.13057 | -0.00029045 | -0.0032321 | 0.10666 | -0.0078442 | 0.062128 | 0.059107 | -0.00070498 | -0.004924 | 63.7848 | 63.9267 | -0.054932 | -59.2255 | 63.8489 | -59.0836 | -59.1064 | -58.8501 | -0.09613 | -59.285 | 63.8626 | 63.7527 | -59.1248 | -59.2346 | -0.073242 | -0.09613 | 0.041199 | 122.937 | -0.21515 | -0.11902 | -0.022888 | -0.11444 | -0.2243 | 0.054932 | 0.16022 | -0.27466 | -0.050354 | -0.054931 | 122.8592 | 122.7951 | 58.9554 | -122.9141 | 122.8729 | 122.7631 | 58.9142 | -123.0423
405.0156 | 123.024 | -59.0057 | 63.8672 | -0.22903 | 0.0018949 | 0.065473 | 0.070944 | 0.13334 | 0.00056395 | -0.0032321 | -0.14511 | -0.0048536 | 0.061273 | 0.06103 | 0.0020722 | -0.0064194 | 63.8306 | 63.9542 | 0.027466 | -59.198 | 63.8718 | -59.0149 | -59.1248 | -58.9691 | 0.091553 | -59.2896 | 63.9359 | 63.7665 | -59.1339 | -59.2484 | -0.009156 | -0.11902 | 0.004578 | 122.9599 | -0.19226 | -0.073242 | -0.036621 | -0.12817 | -0.24261 | 0.068665 | 0.036621 | -0.28381 | -0.041199 | -0.10071 | 122.8775 | 122.8363 | 59.0332 | -122.9919 | 122.9416 | 122.7722 | 59.0973 | -123.1155
406.0156 | 123.1018 | -59.0149 | 63.7756 | 0.16006 | 0.0057401 | 0.062696 | 0.066672 | 0.13014 | 0.00013675 | -0.0021641 | 0.20584 | -0.0042126 | 0.063196 | 0.061244 | 0.004422 | -0.0025742 | 63.8214 | 63.9816 | -0.027466 | -59.2163 | 63.7985 | -59.0652 | -59.1339 | -58.9417 | 0.009155 | -59.2346 | 63.8397 | 63.7024 | -59.1476 | -59.2529 | -0.050354 | -0.11902 | 0.022888 | 122.9965 | -0.20142 | -0.082398 | 0.045776 | -0.13275 | -0.23804 | 0.064087 | 0.073243 | -0.21973 | 0.018311 | -0.073242 | 122.8134 | 122.8363 | 58.9874 | -122.9095 | 122.8546 | 122.7173 | 59.024 | -123.0286
407.0156 | 123.1064 | -58.9874 | 63.7848 | -0.0383 | 0.0012539 | 0.06761 | 0.069449 | 0.12886 | -0.00050425 | -0.0015231 | 0.076141 | -0.0054944 | 0.06106 | 0.059962 | 0.001004 | -0.003856 | 63.826 | 63.9862 | 0.022888 | -59.198 | 63.8626 | -59.0652 | -59.0973 | -58.9142 | 0.11444 | -59.1797 | 63.8489 | 63.7573 | -59.1385 | -59.198 | -0.07782 | -0.10986 | 0.07782 | 122.9736 | -0.21057 | -0.10071 | 0.041199 | -0.15106 | -0.21057 | 0.064087 | 0.073242 | -0.19226 | 0.018311 | -0.027466 | 122.85 | 122.8134 | 59.0103 | -122.8821 | 122.8363 | 122.7448 | 59.1019 | -122.9828
408.0156 | 123.0927 | -59.0195 | 63.7985 | -1.6023 | 0.0029629 | 0.065687 | 0.069235 | 0.13142 | 0.00013675 | -0.0025913 | 0.068512 | -0.002931 | 0.062128 | 0.061244 | 0.0024994 | -0.003856 | 63.7802 | 63.9221 | -0.050354 | -59.2255 | 63.8626 | -59.0698 | -59.1202 | -58.9828 | 0.041199 | -59.23 | 63.8535 | 63.7253 | -59.1293 | -59.2209 | -0.050354 | -0.10071 | 0.064087 | 122.9416 | -0.20599 | -0.10529 | -0.018311 | -0.10986 | -0.20142 | 0.054932 | 0.036621 | -0.21057 | -0.009156 | -0.073242 | 122.8821 | 122.7997 | 58.9691 | -122.9187 | 122.8729 | 122.7448 | 59.0607 | -123.0194
409.0156 | 123.1338 | -58.9783 | 63.8077 | -0.12985 | 0.0038175 | 0.06761 | 0.068381 | 0.13014 | -0.0019995 | -0.0028049 | -0.03067 | -0.0044264 | 0.060633 | 0.061457 | 0.0012176 | -0.005565 | 63.9084 | 63.9999 | 0.068665 | -59.1568 | 63.8443 | -59.0515 | -59.0927 | -58.8547 | 0.19684 | -59.1476 | 63.8718 | 63.7344 | -59.1156 | -59.2072 | -0.073243 | -0.11444 | 0.036621 | 122.9782 | -0.17853 | -0.064087 | 0.10071 | -0.13733 | -0.22888 | 0.064087 | 0.1236 | -0.16937 | 0.059509 | -0.073242 | 122.8226 | 122.8867 | 59.0469 | -122.9004 | 122.85 | 122.7127 | 59.1751 | -123.0148
410.0156 | 123.0972 | -59.0103 | 63.8443 | 0.022736 | 0.0027493 | 0.067396 | 0.068808 | 0.12822 | -0.0019995 | -0.0030185 | 0.076141 | -0.0048536 | 0.062342 | 0.062098 | 0.002713 | -0.0047104 | 63.7527 | 64.064 | 0.10529 | -59.2896 | 63.8626 | -59.0424 | -59.1156 | -58.9737 | 0.032043 | -59.2575 | 63.858 | 63.7436 | -59.1339 | -59.2255 | -0.032043 | -0.10529 | 0.018311 | 123.0743 | -0.27924 | -0.17395 | -0.091552 | -0.1236 | -0.21515 | 0.013733 | 0.036621 | -0.24719 | -0.032043 | -0.10071 | 122.8729 | 122.7631 | 59.1156 | -122.9599 | 122.8683 | 122.7539 | 59.0424 | -123.0698
411.0156 | 123.1659 | -58.9828 | 63.7894 | -0.10696 | 0.0025357 | 0.068678 | 0.068594 | 0.12971 | -7.6852e-05 | -0.0019505 | -0.168 | -0.0044264 | 0.061914 | 0.058253 | 0.0029266 | -0.0044968 | 63.8763 | 64.0045 | 0.045776 | -59.1797 | 63.858 | -59.0515 | -59.1064 | -58.8684 | 0.15564 | -59.1568 | 63.8535 | 63.739 | -59.0973 | -59.198 | -0.068665 | -0.1236 | 0.068664 | 122.9874 | -0.19684 | -0.073242 | 0.086975 | -0.11444 | -0.21515 | 0.064087 | 0.11444 | -0.17395 | 0.041199 | -0.050354 | 122.8409 | 122.8592 | 59.0286 | -122.8958 | 122.8363 | 122.7219 | 59.1385 | -122.9874
412.0156 | 123.0698 | -59.0286 | 63.7894 | 0.16006 | 0.0033901 | 0.06761 | 0.069876 | 0.12928 | 0.00013675 | -0.00088226 | 0.18295 | -0.00464 | 0.061701 | 0.06103 | 0.0037812 | -0.005565 | 63.8123 | 63.9496 | -0.022888 | -59.2346 | 63.8168 | -59.0698 | -59.1293 | -58.9508 | 0.027466 | -59.2758 | 63.826 | 63.6978 | -59.1248 | -59.2255 | -0.041199 | -0.10071 | 0.027465 | 122.9782 | -0.20599 | -0.10529 | 0.022888 | -0.096131 | -0.19684 | 0.036621 | 0.077819 | -0.24719 | -0.050354 | -0.091553 | 122.8455 | 122.8409 | 59.0057 | -122.9187 | 122.8546 | 122.7264 | 59.0561 | -123.0148
413.0156 | 123.1522 | -58.9874 | 63.7985 | -0.0077822 | 0.0036039 | 0.066328 | 0.069022 | 0.13035 | -0.0024269 | -0.0017369 | 0.068512 | -0.0044264 | 0.061701 | 0.06103 | 0.001004 | -0.0044968 | 63.8031 | 63.9359 | -0.036621 | -59.2209 | 63.8489 | -59.0607 | -59.1064 | -58.9462 | 0.073242 | -59.2163 | 63.8214 | 63.7344 | -59.1202 | -59.2117 | -0.073242 | -0.11902 | 0.050354 | 122.9233 | -0.23346 | -0.11444 | 0.004578 | -0.13275 | -0.2243 | 0.022888 | 0.041199 | -0.22888 | -0.004578 | -0.064087 | 122.8363 | 122.7905 | 58.9508 | -122.905 | 122.8088 | 122.7219 | 59.0607 | -123.0103
414.0156 | 123.0972 | -59.0103 | 63.8123 | 0.053253 | 0.0046719 | 0.06526 | 0.06774 | 0.12822 | -0.0017859 | -0.0025913 | 0.045624 | -0.003999 | 0.060633 | 0.06103 | 0.0012176 | -0.0047104 | 63.7894 | 63.9175 | -0.032043 | -59.2209 | 63.858 | -59.0652 | -59.1202 | -58.9508 | 0.064087 | -59.23 | 63.8351 | 63.7482 | -59.1293 | -59.2163 | -0.054932 | -0.10986 | 0.045776 | 122.9279 | -0.21057 | -0.10071 | -0.022888 | -0.11902 | -0.20599 | 0.022888 | 0.059509 | -0.21973 | -0.013733 | -0.064087 | 122.8683 | 122.7997 | 58.9783 | -122.9324 | 122.8455 | 122.7585 | 59.0744 | -123.0286
415.0156 | 123.1476 | -58.992 | 63.8214 | -0.28244 | 0.00018591 | 0.06761 | 0.06774 | 0.13099 | 0.00013675 | -0.0036595 | -0.084076 | -0.006349 | 0.060419 | 0.06103 | 0.0018584 | -0.0047104 | 63.8763 | 64.0457 | 0.082397 | -59.1522 | 63.8718 | -59.024 | -59.1064 | -58.8959 | 0.16937 | -59.1751 | 63.8672 | 63.7756 | -59.0744 | -59.1751 | -0.032044 | -0.11444 | 0.050354 | 123.0377 | -0.16022 | -0.045777 | 0.054932 | -0.082398 | -0.18311 | 0.045776 | 0.09613 | -0.18311 | 0 | -0.045776 | 122.8638 | 122.8683 | 59.0744 | -122.9279 | 122.8592 | 122.7676 | 59.1614 | -122.9965
416.0156 | 123.111 | -59.0332 | 63.8306 | 0.045624 | 0.0021085 | 0.0706 | 0.069235 | 0.12822 | -0.0015723 | -0.0038731 | 0.045624 | -0.00464 | 0.060846 | 0.060176 | 0.0033538 | -0.003856 | 63.8168 | 63.8992 | -0.045776 | -59.2117 | 63.8718 | -59.0561 | -59.1476 | -58.9645 | 0.045776 | -59.2484 | 63.8489 | 63.7253 | -59.1522 | -59.2163 | -0.022888 | -0.11444 | 0.041199 | 122.9324 | -0.17853 | -0.064087 | -0.013733 | -0.11902 | -0.18311 | 0.018311 | 0.068664 | -0.21515 | -0.032043 | -0.10528 | 122.905 | 122.85 | 58.9874 | -122.9782 | 122.8821 | 122.7585 | 59.079 | -123.0469
417.0156 | 123.1842 | -58.9737 | 63.8168 | -0.045929 | 0.0027493 | 0.068464 | 0.07009 | 0.13078 | -0.0011451 | -0.0034457 | -0.076446 | -0.00464 | 0.060633 | 0.061244 | 0.0018584 | -0.0053512 | 63.858 | 64.0274 | 0.054932 | -59.1751 | 63.8672 | -59.0515 | -59.1202 | -58.8684 | 0.19226 | -59.166 | 63.8306 | 63.7436 | -59.1019 | -59.1843 | -0.07782 | -0.14648 | 0.050354 | 123.0011 | -0.20142 | -0.054932 | 0.041199 | -0.12817 | -0.21057 | 0.013733 | 0.10529 | -0.19226 | 0.01831 | -0.073242 | 122.8409 | 122.8317 | 59.0286 | -122.937 | 122.8043 | 122.7173 | 59.166 | -123.0011
418.0156 | 123.1064 | -59.0286 | 63.8123 | 0.0074768 | 0.0033901 | 0.068891 | 0.069876 | 0.13057 | 0.00099115 | -0.0049411 | -0.35873 | -0.0035718 | 0.062342 | 0.059962 | 0.0024994 | -0.0057786 | 63.7756 | 63.9404 | -0.054932 | -59.2163 | 63.858 | -59.0515 | -59.0973 | -58.9691 | 0.036621 | -59.2575 | 63.8626 | 63.7253 | -59.1293 | -59.2484 | -0.022889 | -0.068665 | 0.045776 | 122.9691 | -0.18768 | -0.11902 | -0.036621 | -0.10071 | -0.21973 | 0.050354 | 0.059509 | -0.22888 | -0.009155 | -0.086975 | 122.8867 | 122.8043 | 58.9737 | -122.9095 | 122.8912 | 122.7539 | 59.0652 | -123.0606
419.0156 | 123.1201 | -58.9966 | 63.8168 | 0.037994 | 0.0018949 | 0.068037 | 0.068167 | 0.13057 | -0.0024269 | -0.0019505 | 0.015106 | -0.005708 | 0.058924 | 0.059962 | 0.0020722 | -0.0057786 | 63.7985 | 63.9542 | -0.022888 | -59.1934 | 63.8489 | -59.0652 | -59.0973 | -58.9462 | 0.10071 | -59.2117 | 63.8351 | 63.7344 | -59.1156 | -59.2163 | -0.068665 | -0.10071 | 0.032044 | 122.9507 | -0.19684 | -0.09613 | -0.01831 | -0.11902 | -0.21973 | 0.018311 | 0.050354 | -0.21515 | 0.004578 | -0.082397 | 122.8455 | 122.7951 | 58.9737 | -122.9141 | 122.8317 | 122.731 | 59.0973 | -123.0331
420.0156 | 123.0789 | -59.0057 | 63.8168 | 0.16006 | 0.0044583 | 0.06761 | 0.068594 | 0.13163 | 0.00056395 | -0.0017369 | 0.19058 | -0.0052808 | 0.059992 | 0.059748 | 0.0029266 | -0.0059922 | 63.8123 | 63.9404 | -0.022888 | -59.2209 | 63.8123 | -59.0469 | -59.111 | -58.9417 | 0.009155 | -59.2529 | 63.8214 | 63.7253 | -59.111 | -59.2255 | -0.041199 | -0.10529 | -0.004577 | 122.9462 | -0.21515 | -0.10986 | -0.004577 | -0.10529 | -0.21973 | 0.004578 | 0.064087 | -0.24719 | -0.027466 | -0.091552 | 122.818 | 122.818 | 58.9828 | -122.9279 | 122.8271 | 122.731 | 59.0149 | -123.0423
421.0156 | 123.1247 | -59.0149 | 63.8214 | -0.18326 | 0.0033901 | 0.066541 | 0.066245 | 0.12993 | -0.00050425 | -0.0023777 | -0.96909 | -0.0076306 | 0.062982 | 0.065303 | 0.0037812 | -0.006633 | 63.913 | 64.0549 | 0.068665 | -59.1293 | 63.8672 | -59.0378 | -59.0881 | -58.8272 | 0.15106 | -59.2346 | 63.8351 | 63.739 | -59.1064 | -59.2072 | -0.022888 | -0.073242 | 0.045776 | 123.0698 | -0.11444 | -0.041198 | 0.091553 | -0.091552 | -0.19226 | 0.013733 | 0.18768 | -0.21973 | -0.027466 | -0.082397 | 122.8821 | 122.9279 | 59.0836 | -122.9095 | 122.85 | 122.7539 | 59.166 | -123.0286
422.0156 | 123.1155 | -59.0149 | 63.8168 | 0.0914 | 0.0025357 | 0.066755 | 0.068808 | 0.13206 | -0.0017859 | -0.0023777 | 0.037995 | -0.0050672 | 0.061701 | 0.060816 | 0.0029266 | -0.004924 | 63.7802 | 63.9267 | -0.041199 | -59.2072 | 63.858 | -59.0698 | -59.111 | -58.9737 | 0.050354 | -59.2255 | 63.8489 | 63.7161 | -59.1431 | -59.2438 | -0.054931 | -0.09613 | 0.041199 | 122.9416 | -0.19226 | -0.09613 | -0.036621 | -0.12817 | -0.22888 | 0.032044 | 0.041199 | -0.21057 | 0.01831 | -0.10071 | 122.8729 | 122.7951 | 58.9737 | -122.9279 | 122.8638 | 122.731 | 59.0652 | -123.0606
423.0156 | 123.1705 | -59.0103 | 63.7985 | -0.14511 | 0.0031765 | 0.066969 | 0.069022 | 0.12864 | -0.00050425 | -0.00088226 | -0.15274 | -0.0054944 | 0.062342 | 0.060816 | 0.0035674 | -0.005565 | 63.8626 | 64.0503 | 0.073242 | -59.1522 | 63.8718 | -59.0286 | -59.1019 | -58.8867 | 0.19226 | -59.1339 | 63.8718 | 63.7894 | -59.079 | -59.166 | -0.01831 | -0.091553 | 0.073242 | 123.0606 | -0.14191 | -0.050354 | 0.064087 | -0.068664 | -0.15564 | 0.073242 | 0.1236 | -0.1236 | 0.032044 | -0.009155 | 122.8821 | 122.8729 | 59.0836 | -122.9004 | 122.8821 | 122.7997 | 59.2026 | -122.9645
424.0156 | 123.0881 | -59.0057 | 63.8123 | 0.076141 | 0.0040311 | 0.066755 | 0.071158 | 0.13121 | -0.00071785 | -0.0013095 | 0.045624 | -0.005708 | 0.062555 | 0.062098 | 0.0016448 | -0.0047104 | 63.7939 | 63.9175 | -0.045776 | -59.2255 | 63.8626 | -59.0698 | -59.1522 | -58.96 | 0.050354 | -59.2346 | 63.8626 | 63.7344 | -59.1156 | -59.2255 | -0.064087 | -0.14648 | 0.050354 | 122.9233 | -0.21973 | -0.073242 | -0.018311 | -0.10986 | -0.21973 | 0.050354 | 0.045776 | -0.22888 | -0.009155 | -0.07782 | 122.8683 | 122.7997 | 58.96 | -122.9645 | 122.8683 | 122.7402 | 59.0561 | -123.0377
425.0156 | 123.1476 | -58.9874 | 63.8535 | -0.076447 | 0.0018949 | 0.065046 | 0.069235 | 0.13121 | -0.0017859 | -0.0034457 | -0.084076 | -0.00464 | 0.061701 | 0.061671 | 0.0031402 | -0.0062058 | 63.8489 | 64.0411 | 0.073242 | -59.166 | 63.8626 | -59.0286 | -59.0652 | -58.8638 | 0.20142 | -59.1339 | 63.8535 | 63.739 | -59.1156 | -59.1751 | -0.041198 | -0.07782 | 0.009155 | 123.0286 | -0.17853 | -0.10071 | -0.004578 | -0.12817 | -0.18768 | 0 | 0.1236 | -0.14648 | 0.041199 | -0.11444 | 122.85 | 122.8363 | 59.0607 | -122.9187 | 122.8409 | 122.7264 | 59.1888 | -123.0286
426.0156 | 123.0789 | -58.992 | 63.8306 | 0.12955 | 0.0033901 | 0.067182 | 0.067526 | 0.12993 | -0.0013587 | -0.00066866 | 0.31265 | -0.0052808 | 0.063196 | 0.060176 | 0.0018584 | -0.0036424 | 63.7894 | 63.9267 | -0.041199 | -59.2346 | 63.8397 | -59.0652 | -59.1019 | -58.9691 | 0.036621 | -59.2575 | 63.8397 | 63.7299 | -59.1385 | -59.2392 | -0.073243 | -0.10986 | 0.009156 | 122.9187 | -0.24262 | -0.13275 | -0.041198 | -0.14648 | -0.24719 | 0.009156 | 0.022888 | -0.2655 | -0.01831 | -0.10071 | 122.8317 | 122.7814 | 58.9508 | -122.9324 | 122.8317 | 122.7219 | 59.0286 | -123.0698
427.0156 | 123.143 | -59.0149 | 63.7985 | -0.03067 | 0.0027493 | 0.068037 | 0.069235 | 0.12843 | -0.0017859 | -0.0028049 | 0.0074766 | -0.0044264 | 0.059564 | 0.060389 | 0.0031402 | -0.0044968 | 63.8168 | 63.9633 | 0.009155 | -59.1934 | 63.8443 | -59.0744 | -59.1019 | -58.9188 | 0.10529 | -59.198 | 63.8718 | 63.7253 | -59.111 | -59.2209 | -0.059509 | -0.086975 | 0.045776 | 122.9782 | -0.17853 | -0.091552 | 0.01831 | -0.09613 | -0.20599 | 0.073242 | 0.096131 | -0.1831 | 0.022888 | -0.073242 | 122.8592 | 122.8317 | 59.024 | -122.9004 | 122.8867 | 122.7402 | 59.1202 | -123.0194
428.0156 | 123.1155 | -59.0012 | 63.8168 | -0.0077822 | 0.0031765 | 0.068891 | 0.067313 | 0.13078 | -7.6852e-05 | -0.0038731 | 0.015106 | -0.0044264 | 0.061273 | 0.059748 | 0.0014312 | -0.0051376 | 63.8214 | 63.9542 | -0.004578 | -59.198 | 63.8535 | -59.0652 | -59.1019 | -58.9142 | 0.10529 | -59.1934 | 63.8443 | 63.7161 | -59.1019 | -59.1934 | -0.064087 | -0.10071 | 0.036622 | 122.9553 | -0.19684 | -0.09613 | 0.004578 | -0.10071 | -0.19226 | 0.027466 | 0.086975 | -0.19226 | 0 | -0.10071 | 122.8546 | 122.8226 | 58.9966 | -122.9187 | 122.8455 | 122.7173 | 59.1064 | -123.0103
429.0156 | 123.1293 | -59.0012 | 63.8351 | -0.18326 | 0.0031765 | 0.067823 | 0.073508 | 0.12822 | 0.0056909 | -0.00024146 | -0.11459 | -0.0050672 | 0.060846 | 0.06103 | 0.0033538 | -0.003856 | 63.6612 | 64.1052 | 0.10986 | -59.2575 | 63.8306 | -59.0607 | -59.1156 | -58.9096 | 0.16937 | -59.1797 | 63.8672 | 63.7436 | -59.0744 | -59.1751 | -0.059509 | -0.11444 | -0.004578 | 123.1064 | -0.25635 | -0.14191 | -0.17395 | -0.073242 | -0.17395 | 0.032043 | 0.091553 | -0.17853 | -0.004577 | -0.091553 | 122.8317 | 122.6624 | 59.111 | -122.9507 | 122.8683 | 122.7448 | 59.1705 | -123.0103
430.0156 | 123.0972 | -59.0149 | 63.8031 | -0.015411 | 0.0010403 | 0.06825 | 0.066458 | 0.12758 | -0.0019995 | -0.00066866 | 0.0074766 | -0.0054944 | 0.060846 | 0.061671 | 0.002713 | -0.0053512 | 63.7848 | 63.9542 | -0.009155 | -59.2026 | 63.8718 | -59.0561 | -59.111 | -58.9279 | 0.10071 | -59.2072 | 63.8535 | 63.7436 | -59.1522 | -59.2209 | -0.041198 | -0.09613 | 0.068664 | 122.9691 | -0.18768 | -0.091553 | -0.018311 | -0.13733 | -0.20599 | 0.050354 | 0.086976 | -0.19226 | 0.013733 | -0.05951 | 122.8867 | 122.7997 | 59.0057 | -122.9141 | 122.8683 | 122.7585 | 59.1156 | -123.024
431.0156 | 123.1293 | -59.0149 | 63.8214 | -0.18326 | 0.0029629 | 0.069746 | 0.068594 | 0.13014 | -0.0028541 | -0.0038731 | -0.061188 | -0.0044264 | 0.060419 | 0.059962 | 0.0012176 | -0.0081284 | 64.0961 | 63.7344 | -0.068665 | -59.1522 | 63.8397 | -59.0515 | -59.1019 | -58.9096 | 0.19226 | -59.1614 | 63.8626 | 63.7253 | -59.1019 | -59.1934 | -0.036621 | -0.086975 | 0.018311 | 122.7493 | -0.13733 | -0.050354 | 0.27466 | -0.086975 | -0.17853 | 0.041199 | 0.10529 | -0.14648 | 0.032043 | -0.09613 | 122.8546 | 123.111 | 58.9462 | -122.9233 | 122.8775 | 122.7402 | 59.2072 | -123.0148
432.0156 | 123.1338 | -58.9783 | 63.8168 | -0.015411 | 0.0033901 | 0.068678 | 0.066458 | 0.13185 | -0.0024269 | -0.0019505 | 0.015106 | -0.0042126 | 0.060205 | 0.058894 | 0.0018584 | -0.004924 | 63.8031 | 63.9587 | -0.018311 | -59.198 | 63.8718 | -59.0652 | -59.111 | -58.9371 | 0.07782 | -59.2117 | 63.8489 | 63.7207 | -59.1064 | -59.2255 | -0.086976 | -0.13275 | 0.054932 | 122.937 | -0.21973 | -0.086975 | -0.013732 | -0.12817 | -0.24719 | 0.032044 | 0.041198 | -0.23346 | 0.013733 | -0.09613 | 122.85 | 122.7814 | 58.96 | -122.9279 | 122.8271 | 122.699 | 59.0561 | -123.0423
433.0156 | 123.1384 | -58.9874 | 63.8306 | -0.099335 | 0.0036039 | 0.06825 | 0.069235 | 0.13163 | -0.0022131 | -0.0017369 | -0.091705 | -0.005708 | 0.059137 | 0.059107 | 0.0014312 | -0.0023606 | 63.8397 | 64.0045 | 0.045776 | -59.1705 | 63.8489 | -59.0515 | -59.111 | -58.8638 | 0.17853 | -59.1522 | 63.8535 | 63.7436 | -59.0973 | -59.1934 | -0.064087 | -0.1236 | 0.018311 | 122.9919 | -0.18311 | -0.059509 | 0.009156 | -0.10986 | -0.20599 | 0.022889 | 0.1236 | -0.1648 | 0.041198 | -0.086975 | 122.8363 | 122.8271 | 59.0332 | -122.9416 | 122.8409 | 122.731 | 59.166 | -123.024
434.0156 | 123.0927 | -59.0149 | 63.7711 | 0.099029 | 0.0014675 | 0.069105 | 0.068167 | 0.13292 | -0.0022131 | -0.0025913 | -0.29007 | -0.0069898 | 0.062342 | 0.062098 | 0.0046356 | -0.0051376 | 63.8031 | 63.9496 | -0.032043 | -59.2575 | 63.858 | -59.0652 | -59.0973 | -58.9874 | 0.009155 | -59.2529 | 63.8397 | 63.7024 | -59.1339 | -59.2575 | -0.050354 | -0.082397 | 0.086975 | 122.9645 | -0.24261 | -0.16022 | 0.032044 | -0.11902 | -0.24261 | 0.068665 | 0.027466 | -0.23804 | 0.004577 | -0.068664 | 122.8729 | 122.818 | 58.9828 | -122.8683 | 122.8546 | 122.7173 | 59.024 | -123.0286
435.0156 | 123.0652 | -58.9737 | 63.8535 | -0.21378 | 0.0031765 | 0.06761 | 0.070731 | 0.13206 | -7.6852e-05 | -0.0030185 | -0.19089 | -0.0042126 | 0.061273 | 0.059962 | 0.0012176 | -0.0057786 | 63.8535 | 64.0091 | 0.059509 | -59.1568 | 63.8626 | -59.0469 | -59.0927 | -58.9462 | 0.15106 | -59.2209 | 63.8626 | 63.7711 | -59.1248 | -59.2117 | -0.073242 | -0.11902 | 0.009155 | 122.9828 | -0.1831 | -0.064087 | 0 | -0.15106 | -0.23804 | 0.009155 | 0.027466 | -0.24719 | -0.009155 | -0.082398 | 122.8363 | 122.8271 | 59.0332 | -122.9462 | 122.8363 | 122.7448 | 59.1248 | -123.0652
436.0156 | 123.1659 | -58.9737 | 63.8077 | -0.12222 | 0.0018949 | 0.066969 | 0.069022 | 0.13078 | -0.0030677 | -0.0013095 | -0.045929 | -0.005708 | 0.061914 | 0.061244 | 0.002713 | -0.0036424 | 63.8306 | 64.0137 | 0.045776 | -59.166 | 63.8535 | -59.0378 | -59.0881 | -58.8593 | 0.16937 | -59.1339 | 63.858 | 63.7253 | -59.0927 | -59.2026 | -0.064087 | -0.11444 | 0.045777 | 122.9874 | -0.19226 | -0.07782 | 0.022888 | -0.11902 | -0.22888 | 0.050354 | 0.11444 | -0.16022 | 0.068665 | -0.082397 | 122.8271 | 122.8043 | 59.0195 | -122.8958 | 122.8317 | 122.699 | 59.1431 | -123.0103
437.0156 | 123.0469 | -59.0057 | 63.8718 | -0.24429 | 0.0044583 | 0.069746 | 0.069876 | 0.12907 | 0.00035035 | -0.0019505 | -0.19089 | -0.003999 | 0.059564 | 0.061244 | 0.0018584 | -0.0057786 | 63.8489 | 64.0045 | 0.068665 | -59.1751 | 63.8672 | -59.0652 | -59.1156 | -58.9645 | 0.13275 | -59.23 | 63.9038 | 63.7619 | -59.1476 | -59.2163 | -0.05951 | -0.10986 | -0.004578 | 123.0103 | -0.16937 | -0.059509 | -0.022888 | -0.14191 | -0.21057 | 0.032044 | 0.041198 | -0.2243 | -0.013733 | -0.10986 | 122.8729 | 122.8546 | 59.0744 | -122.9874 | 122.9095 | 122.7676 | 59.1385 | -123.0881
438.0156 | 123.1567 | -58.9828 | 63.8123 | -0.084076 | 0.0038175 | 0.069105 | 0.06774 | 0.13185 | -0.0013587 | -0.0030185 | -0.084076 | -0.0050672 | 0.062555 | 0.060389 | 0.0012176 | -0.005565 | 63.8489 | 64.0503 | 0.064087 | -59.166 | 63.858 | -59.0469 | -59.0973 | -58.8593 | 0.19226 | -59.1431 | 63.858 | 63.7344 | -59.1156 | -59.2209 | -0.064087 | -0.11444 | 0.045776 | 123.0331 | -0.18311 | -0.068665 | 0.036621 | -0.13275 | -0.23804 | 0.045776 | 0.1236 | -0.16022 | 0.07782 | -0.07782 | 122.8409 | 122.8317 | 59.0469 | -122.9095 | 122.8409 | 122.7173 | 59.1751 | -123.0331
439.0156 | 123.0606 | -59.0012 | 63.8489 | -0.22903 | 0.0036039 | 0.069746 | 0.068594 | 0.13057 | 0.0012047 | -0.0015231 | -0.21378 | -0.0067762 | 0.059778 | 0.061457 | 0.00079042 | -0.0040696 | 63.8306 | 63.9908 | 0.050354 | -59.1751 | 63.8718 | -59.0424 | -59.0973 | -58.9645 | 0.12817 | -59.2346 | 63.9038 | 63.7619 | -59.1248 | -59.2255 | -0.041198 | -0.09613 | 0.022888 | 122.9919 | -0.17395 | -0.07782 | -0.018311 | -0.1236 | -0.2243 | 0.054932 | 0.036621 | -0.23346 | -0.009155 | -0.086975 | 122.8729 | 122.8317 | 59.0515 | -122.9462 | 122.905 | 122.7631 | 59.1293 | -123.0743
440.0156 | 123.1293 | -59.0012 | 63.8168 | -0.053558 | 0.0027493 | 0.068037 | 0.069235 | 0.12907 | -0.0032813 | -0.0036595 | -0.0077819 | -0.006349 | 0.059992 | 0.060389 | 0.0029266 | -0.0053512 | 63.7894 | 63.9954 | 0 | -59.1843 | 63.8626 | -59.0698 | -59.1202 | -58.9188 | 0.11902 | -59.1888 | 63.8489 | 63.7344 | -59.1202 | -59.2026 | -0.068664 | -0.11902 | 0.045777 | 122.9965 | -0.18311 | -0.064087 | -0.027465 | -0.11902 | -0.20142 | 0.032044 | 0.082398 | -0.18768 | 0.013733 | -0.082397 | 122.8638 | 122.7905 | 59.0012 | -122.937 | 122.85 | 122.7356 | 59.1202 | -123.0194
441.0156 | 123.1293 | -58.9874 | 63.8214 | 0.17532 | 0.0070217 | 0.066969 | 0.070944 | 0.13099 | 0.00056395 | -0.0025913 | -0.10696 | -0.0065626 | 0.060205 | 0.059321 | 0.0016448 | -0.006633 | 63.8535 | 64.0274 | 0.073242 | -59.1614 | 63.8626 | -59.0378 | -59.111 | -58.9142 | 0.17395 | -59.1614 | 63.858 | 63.7207 | -59.1202 | -59.2026 | -0.050354 | -0.1236 | 0.041199 | 123.0148 | -0.17395 | -0.050354 | 0.032044 | -0.13275 | -0.21515 | 0.036621 | 0.073242 | -0.17395 | 0.041199 | -0.10071 | 122.85 | 122.8409 | 59.0607 | -122.9324 | 122.8455 | 122.7081 | 59.1614 | -123.024
442.0156 | 123.1155 | -58.9966 | 63.8351 | 0.045624 | 0.0040311 | 0.06825 | 0.067954 | 0.12822 | -0.0015723 | -0.0032321 | -0.168 | -0.005708 | 0.061487 | 0.059962 | 0.0033538 | -0.0044968 | 63.8443 | 64.0274 | 0.073242 | -59.166 | 63.8489 | -59.024 | -59.0836 | -58.9233 | 0.16937 | -59.1705 | 63.8718 | 63.7344 | -59.1019 | -59.198 | -0.027466 | -0.086975 | 0.013733 | 123.024 | -0.16937 | -0.082398 | 0.009155 | -0.10529 | -0.20142 | 0.036621 | 0.073242 | -0.17395 | 0.027466 | -0.10071 | 122.8455 | 122.8409 | 59.0698 | -122.9187 | 122.8683 | 122.731 | 59.166 | -123.0331
443.0156 | 123.0286 | -59.024 | 63.8397 | -0.24429 | 0.0091581 | 0.069319 | 0.070731 | 0.13078 | -0.00050425 | -0.0010959 | -1.7168 | -0.0048536 | 0.066187 | 0.061457 | 0.002713 | -0.003856 | 63.7527 | 63.9084 | -0.036621 | -59.2346 | 63.913 | -59.079 | -59.1293 | -59.0057 | -0.004578 | -59.3079 | 63.913 | 63.7527 | -59.1385 | -59.2438 | -0.054931 | -0.10529 | 0.073242 | 122.9324 | -0.21057 | -0.10529 | -0.086975 | -0.11444 | -0.21973 | 0.073242 | 0.018311 | -0.28381 | -0.064087 | -0.086975 | 122.937 | 122.7768 | 58.9874 | -122.9691 | 122.937 | 122.7768 | 59.0195 | -123.0835
444.0156 | 123.1155 | -58.9874 | 63.858 | -0.17563 | 0.0018949 | 0.069319 | 0.067954 | 0.13078 | -0.00050425 | -0.0021641 | -0.14511 | -0.006349 | 0.061487 | 0.059107 | 0.002713 | -0.005565 | 63.8306 | 64.0182 | 0.086975 | -59.166 | 63.8718 | -59.0332 | -59.079 | -58.9279 | 0.1831 | -59.1934 | 63.8626 | 63.7436 | -59.1064 | -59.1888 | -0.045776 | -0.091552 | 0.013733 | 123.0057 | -0.17853 | -0.086976 | -0.027466 | -0.11902 | -0.20142 | 0.004578 | 0.05951 | -0.20599 | -0.004577 | -0.11444 | 122.8592 | 122.818 | 59.0744 | -122.937 | 122.85 | 122.731 | 59.1705 | -123.0469
445.0156 | 123.0331 | -59.0149 | 63.8718 | -0.25192 | 0.0080899 | 0.068037 | 0.069663 | 0.13057 | 0.00099115 | -0.0023777 | 0.068512 | -0.0035718 | 0.062128 | 0.060389 | 0.0029266 | -0.003856 | 63.7619 | 63.8031 | 0.050354 | -59.0973 | 63.9679 | -59.0286 | -59.1019 | -59.0286 | 0.064087 | -59.285 | 63.9313 | 63.7985 | -59.1614 | -59.2163 | -0.013732 | -0.086975 | 0.096131 | 122.818 | -0.082397 | 0.004578 | -0.10986 | -0.14648 | -0.20142 | 0.059509 | -0.013732 | -0.27008 | -0.068664 | -0.073242 | 122.9828 | 122.7768 | 59.0652 | -122.9736 | 122.9462 | 122.8134 | 59.079 | -123.0881
446.0156 | 123.1064 | -59.0195 | 63.8351 | -0.19852 | 0.0040311 | 0.067396 | 0.068594 | 0.12886 | -0.0013587 | -0.0025913 | -0.18326 | -0.003999 | 0.062769 | 0.059107 | 0.0014312 | -0.0036424 | 63.8306 | 64.032 | 0.073242 | -59.1614 | 63.8626 | -59.024 | -59.0927 | -58.9233 | 0.16937 | -59.1934 | 63.8809 | 63.7344 | -59.1064 | -59.2117 | -0.004578 | -0.073242 | 0.027466 | 123.0515 | -0.14191 | -0.068665 | -0.004578 | -0.086975 | -0.19226 | 0.045776 | 0.09613 | -0.17395 | 0.018311 | -0.10071 | 122.8821 | 122.85 | 59.0927 | -122.9279 | 122.9004 | 122.7539 | 59.1888 | -123.0469
447.0156 | 123.024 | -59.0332 | 63.8718 | -0.25192 | 0.0042447 | 0.068678 | 0.071372 | 0.13313 | -0.0030677 | -0.0015231 | -0.4274 | -0.0044264 | 0.061487 | 0.060816 | 0.0020722 | -0.0044968 | 63.7985 | 63.9587 | 0.013733 | -59.2072 | 63.8992 | -59.0561 | -59.1202 | -58.9966 | 0.068665 | -59.2712 | 63.8901 | 63.7711 | -59.1385 | -59.2163 | -0.022888 | -0.086975 | 0.027466 | 122.9919 | -0.17395 | -0.086975 | -0.073242 | -0.10529 | -0.18311 | 0.018311 | 0.036621 | -0.23804 | -0.054931 | -0.10071 | 122.9324 | 122.8317 | 59.0469 | -122.9919 | 122.9233 | 122.8043 | 59.1019 | -123.0881
448.0156 | 123.0927 | -59.0057 | 63.8626 | -0.20615 | 0.0038175 | 0.065687 | 0.065817 | 0.1295 | -0.0026405 | -0.0032321 | -0.14511 | -0.0048536 | 0.060205 | 0.061244 | 0.0029266 | -0.005565 | 63.8214 | 64.0045 | 0.064087 | -59.166 | 63.8626 | -59.0561 | -59.0927 | -58.9554 | 0.16479 | -59.2026 | 63.8626 | 63.7299 | -59.0973 | -59.2255 | -0.050354 | -0.086975 | 0 | 123.0103 | -0.16022 | -0.073243 | -0.041199 | -0.091553 | -0.21973 | 0 | 0.050354 | -0.19684 | 0.022888 | -0.13275 | 122.8683 | 122.8271 | 59.0698 | -122.9553 | 122.8683 | 122.7356 | 59.1705 | -123.0881
449.0156 | 123.0469 | -59.0424 | 63.8855 | -0.17563 | 0.0078763 | 0.066328 | 0.067313 | 0.13099 | 0.0022729 | -0.0025913 | -0.22903 | -0.0027174 | 0.061273 | 0.06103 | 0.0048492 | -0.0072738 | 63.7756 | 63.8992 | -0.027466 | -59.198 | 63.9084 | -59.0652 | -59.1019 | -58.992 | 0.07782 | -59.2804 | 63.9038 | 63.7665 | -59.1476 | -59.23 | -0.022889 | -0.05951 | 0.022888 | 122.9416 | -0.15564 | -0.09613 | -0.10986 | -0.10529 | -0.18768 | 0.018311 | 0.050354 | -0.23804 | -0.050354 | -0.11902 | 122.9507 | 122.818 | 59.0149 | -122.9874 | 122.9462 | 122.8088 | 59.1202 | -123.1155
450.0156 | 123.0377 | -59.0286 | 63.8672 | -0.25955 | 0.0055265 | 0.068464 | 0.065817 | 0.12907 | -0.0026405 | -0.0032321 | -0.20615 | -0.0048536 | 0.059992 | 0.062098 | 0.00079042 | -0.003856 | 63.7711 | 63.9404 | -0.009155 | -59.2392 | 63.8855 | -59.0698 | -59.1339 | -59.0103 | 0.054932 | -59.285 | 63.9175 | 63.7848 | -59.1385 | -59.2255 | -0.041199 | -0.10529 | 0.018311 | 122.9691 | -0.21057 | -0.10529 | -0.09613 | -0.10986 | -0.19684 | 0.050355 | 0.01831 | -0.25635 | -0.059509 | -0.082397 | 122.9141 | 122.7997 | 59.0195 | -123.0011 | 122.9462 | 122.8134 | 59.0836 | -123.0927
451.0156 | 123.0469 | -59.0103 | 63.8443 | -0.21378 | 0.0089443 | 0.06761 | 0.070517 | 0.13142 | 0.0037683 | -0.0017369 | -0.168 | -0.0033582 | 0.062982 | 0.059748 | 0.002713 | -0.0053512 | 63.7985 | 63.8992 | -0.022888 | -59.2026 | 63.9084 | -59.0698 | -59.1156 | -58.9874 | 0.091553 | -59.2575 | 63.9221 | 63.7848 | -59.1431 | -59.2392 | -0.059509 | -0.10529 | 0.064087 | 122.9095 | -0.19226 | -0.086975 | -0.045776 | -0.13275 | -0.22888 | 0.07782 | 0.022888 | -0.24719 | -0.01831 | -0.059509 | 122.9187 | 122.8088 | 58.9874 | -122.9599 | 122.9324 | 122.7951 | 59.1019 | -123.0835
452.0156 | 123.0103 | -59.0561 | 63.8809 | -0.19089 | 0.0061673 | 0.068464 | 0.070731 | 0.1327 | -0.0015723 | -0.0028049 | -0.14511 | -0.0033582 | 0.06341 | 0.062953 | 0.0016448 | -1.0768e-05 | 63.739 | 63.9175 | -0.018311 | -59.23 | 63.9038 | -59.079 | -59.1385 | -59.0103 | 0.068665 | -59.2758 | 63.9038 | 63.7985 | -59.1339 | -59.2072 | -0.022888 | -0.082398 | 0.022889 | 122.9736 | -0.17395 | -0.091553 | -0.14191 | -0.07782 | -0.15106 | 0.022889 | 0.045776 | -0.21973 | -0.068665 | -0.082397 | 122.9599 | 122.7951 | 59.0378 | -123.0194 | 122.9599 | 122.8546 | 59.1248 | -123.0881
453.0156 | 123.0423 | -59.0286 | 63.8443 | -0.20615 | 0.0083035 | 0.068891 | 0.072653 | 0.13035 | 0.00056395 | -0.0045139 | -0.17563 | -0.0025038 | 0.064051 | 0.061885 | 0.0037812 | -0.0053512 | 63.7802 | 63.8855 | -0.027466 | -59.2026 | 63.9267 | -59.1156 | -59.111 | -58.992 | 0.091553 | -59.2621 | 63.9038 | 63.7939 | -59.1202 | -59.2346 | -0.086976 | -0.082398 | 0.082398 | 122.9141 | -0.17395 | -0.091553 | -0.064087 | -0.091553 | -0.20599 | 0.05951 | 0.036621 | -0.23346 | -0.027466 | -0.050354 | 122.9553 | 122.8088 | 59.0012 | -122.9553 | 122.9324 | 122.8226 | 59.1202 | -123.0789
454.0156 | 123.0606 | -59.0012 | 63.8626 | -0.20615 | 0.0053129 | 0.06825 | 0.069663 | 0.1327 | -0.0022131 | -0.0030185 | -0.12985 | -0.00464 | 0.062342 | 0.061885 | 0.0020722 | -0.0042832 | 63.8031 | 63.9908 | 0.045776 | -59.1705 | 63.8992 | -59.0332 | -59.1064 | -58.9691 | 0.14648 | -59.2209 | 63.8718 | 63.7756 | -59.1156 | -59.198 | -0.032043 | -0.10529 | 0.036621 | 122.9919 | -0.16937 | -0.064087 | -0.059509 | -0.11444 | -0.19684 | 0.009155 | 0.032044 | -0.21973 | -0.022888 | -0.086975 | 122.9004 | 122.8043 | 59.0469 | -122.9691 | 122.8729 | 122.7768 | 59.1476 | -123.0606
455.0156 | 123.0698 | -59.0195 | 63.8718 | -0.17563 | 0.0091581 | 0.06526 | 0.073508 | 0.13099 | -7.6852e-05 | 0.00082674 | -0.20615 | -0.00464 | 0.064051 | 0.062739 | 0.0033538 | -0.003856 | 63.7848 | 63.9084 | -0.032043 | -59.2072 | 63.9313 | -59.0836 | -59.1431 | -58.9966 | 0.082397 | -59.2575 | 63.8901 | 63.7939 | -59.1385 | -59.2346 | -0.064087 | -0.1236 | 0.059509 | 122.9279 | -0.18768 | -0.064087 | -0.086975 | -0.11902 | -0.21515 | 0.018311 | 0.022888 | -0.23804 | -0.022888 | -0.07782 | 122.9507 | 122.8043 | 58.9874 | -123.0148 | 122.9095 | 122.8134 | 59.1019 | -123.1064
456.0156 | 123.0103 | -59.0469 | 63.858 | 0.037994 | 0.0068081 | 0.06825 | 0.069022 | 0.13014 | 0.00013675 | -0.0013095 | -0.17563 | -0.0035718 | 0.062555 | 0.059748 | 0.002713 | -0.0012924 | 63.7711 | 63.8855 | -0.050354 | -59.2346 | 63.8901 | -59.0836 | -59.1476 | -59.0149 | 0.059509 | -59.2804 | 63.8992 | 63.7985 | -59.1431 | -59.2117 | -0.036621 | -0.10071 | 0.032044 | 122.9324 | -0.18768 | -0.086975 | -0.086975 | -0.09613 | -0.16479 | 0.041199 | 0.032043 | -0.23346 | -0.068665 | -0.059509 | 122.937 | 122.818 | 58.9966 | -123.0057 | 122.9462 | 122.8455 | 59.1064 | -123.0698
457.0156 | 123.0972 | -59.0469 | 63.8443 | -0.11459 | 0.011935 | 0.06526 | 0.069235 | 0.13228 | 0.00099115 | -0.00066866 | -0.00015237 | -0.0033582 | 0.064264 | 0.059535 | 0.0037812 | -0.0053512 | 63.8031 | 63.913 | -0.027466 | -59.2026 | 63.8901 | -59.079 | -59.1293 | -58.992 | 0.091553 | -59.4269 | 63.8489 | 63.7436 | -59.1568 | -59.2484 | -0.032043 | -0.082397 | 0.045777 | 122.9599 | -0.15564 | -0.073243 | -0.041198 | -0.10986 | -0.20142 | 0.004578 | 0.054932 | -0.37994 | -0.17853 | -0.10071 | 122.937 | 122.85 | 59.0195 | -122.9736 | 122.8958 | 122.7905 | 59.1385 | -123.0927
458.0156 | 123.0377 | -59.0561 | 63.8535 | -0.24429 | 0.0080899 | 0.067396 | 0.069022 | 0.13057 | 0.00056395 | -0.0023777 | -0.17563 | -0.0044264 | 0.065546 | 0.062098 | 0.00036322 | -0.0027878 | 63.7299 | 63.8763 | -0.041199 | -59.2392 | 63.8855 | -59.0698 | -59.1431 | -59.0424 | 0.054932 | -59.2896 | 63.8855 | 63.826 | -59.1522 | -59.2209 | -0.013733 | -0.086975 | 0.032043 | 122.9324 | -0.18311 | -0.096131 | -0.1236 | -0.096131 | -0.16479 | 0.032043 | 0.013733 | -0.23346 | -0.068665 | -0.027466 | 122.9416 | 122.7859 | 59.0149 | -122.9965 | 122.9416 | 122.8821 | 59.111 | -123.0743
459.0156 | 123.0698 | -59.0469 | 63.8489 | -0.11459 | 0.011508 | 0.066755 | 0.071799 | 0.13014 | 0.0012047 | -0.0010959 | -0.053558 | -0.0044264 | 0.063837 | 0.061457 | 0.0018584 | -0.005565 | 63.7848 | 63.913 | -0.027466 | -59.2072 | 63.8718 | -59.0469 | -59.1064 | -58.9828 | 0.10529 | -59.4177 | 63.8535 | 63.7482 | -59.1751 | -59.2667 | 0 | -0.059509 | 0.022888 | 122.9599 | -0.16022 | -0.10071 | -0.064087 | -0.12817 | -0.21973 | 0.004578 | 0.064087 | -0.37079 | -0.15106 | -0.10071 | 122.9187 | 122.8317 | 59.0195 | -122.9553 | 122.9004 | 122.7951 | 59.1522 | -123.1155
460.0156 | 123.0331 | -59.0286 | 63.8718 | -0.12985 | 0.010867 | 0.067823 | 0.067099 | 0.13249 | -0.0017859 | -0.0015231 | -0.053558 | -0.0033582 | 0.063837 | 0.062312 | 0.0018584 | -0.0042832 | 63.7756 | 63.9038 | -0.032043 | -59.2117 | 63.8718 | -59.0927 | -59.1248 | -58.9874 | 0.082397 | -59.2575 | 63.8855 | 63.7711 | -59.1522 | -59.2621 | -0.064087 | -0.096131 | 0 | 122.9324 | -0.18311 | -0.086975 | -0.09613 | -0.1236 | -0.23346 | 0.013733 | 0.041198 | -0.22888 | 0.004578 | -0.10071 | 122.9004 | 122.8043 | 58.9966 | -122.9965 | 122.9141 | 122.7997 | 59.111 | -123.1338
461.0156 | 123.056 | -59.0561 | 63.858 | -0.14511 | 0.010653 | 0.068464 | 0.072012 | 0.13334 | -0.0026405 | -0.00088226 | -0.16037 | -0.003999 | 0.064691 | 0.060816 | 0.0037812 | -0.0036424 | 63.7665 | 63.8901 | -0.018311 | -59.2117 | 63.913 | -59.0927 | -59.1339 | -59.0149 | 0.10529 | -59.2621 | 63.8992 | 63.8123 | -59.1522 | -59.2117 | -0.036621 | -0.07782 | 0.054932 | 122.9462 | -0.15564 | -0.07782 | -0.091553 | -0.096131 | -0.15564 | 0.041199 | 0.041198 | -0.20599 | -0.050354 | -0.045776 | 122.9691 | 122.8226 | 59.0378 | -122.9919 | 122.9553 | 122.8683 | 59.1614 | -123.0698
462.0156 | 123.0606 | -59.0515 | 63.858 | -0.168 | 0.0097989 | 0.069319 | 0.071372 | 0.13099 | -0.00093145 | -0.0028049 | -0.168 | -0.0044264 | 0.061701 | 0.062098 | 0.0016448 | -0.0040696 | 63.7619 | 63.8901 | -0.036621 | -59.2072 | 63.8947 | -59.0881 | -59.1248 | -59.0149 | 0.07782 | -59.2529 | 63.9084 | 63.8214 | -59.1385 | -59.23 | -0.036621 | -0.073242 | 0.036621 | 122.9416 | -0.15564 | -0.082397 | -0.09613 | -0.086975 | -0.17853 | 0.050354 | 0.036621 | -0.20142 | -0.022888 | -0.036621 | 122.9462 | 122.8134 | 59.0149 | -122.9828 | 122.9599 | 122.8729 | 59.1293 | -123.0881
463.0156 | 123.0377 | -59.0561 | 63.8214 | -0.068817 | 0.012362 | 0.065473 | 0.072653 | 0.13163 | -0.0013587 | -2.7856e-05 | 0.030365 | -0.00229 | 0.065546 | 0.061885 | 0.0022858 | -0.0044968 | 63.7756 | 63.8901 | -0.045776 | -59.2117 | 63.8947 | -59.079 | -59.1568 | -59.0332 | 0.022888 | -59.2804 | 63.8763 | 63.7848 | -59.1568 | -59.2529 | -0.022888 | -0.10071 | 0.073242 | 122.9462 | -0.15564 | -0.054932 | -0.045776 | -0.10071 | -0.19684 | 0.054932 | 0.022888 | -0.22431 | -0.027466 | -0.036621 | 122.9507 | 122.8317 | 59.0103 | -122.9782 | 122.9324 | 122.8409 | 59.079 | -123.0743
464.0156 | 123.0606 | -59.0515 | 63.8489 | -0.17563 | 0.010226 | 0.064832 | 0.070517 | 0.12993 | -0.00093145 | -0.0019505 | -0.16037 | -0.0033582 | 0.063837 | 0.062312 | -0.00027778 | -0.0042832 | 63.7436 | 63.8809 | -0.041199 | -59.198 | 63.913 | -59.0698 | -59.1202 | -59.0057 | 0.086975 | -59.2621 | 63.913 | 63.8031 | -59.1476 | -59.2209 | -0.01831 | -0.068664 | 0.064087 | 122.9324 | -0.14648 | -0.07782 | -0.10529 | -0.09613 | -0.16937 | 0.064087 | 0.045777 | -0.21057 | -0.041199 | -0.045776 | 122.9645 | 122.7951 | 59.0103 | -122.9691 | 122.9645 | 122.8546 | 59.1385 | -123.0698
465.0312 | 123.111 | -58.9828 | 63.8718 | -0.099335 | 0.0036039 | 0.068891 | 0.069022 | 0.13099 | -0.0090491 | -0.0034457 | 0.037995 | -0.0050672 | 0.059992 | 0.059321 | 0.00079042 | -0.0040696 | 63.8077 | 64.0228 | 0.07782 | -59.1568 | 63.8351 | -59.0469 | -59.079 | -58.9005 | 0.16022 | -59.1293 | 63.8077 | 63.7711 | -59.1202 | -59.1934 | -0.064087 | -0.09613 | -0.036621 | 123.0057 | -0.17395 | -0.07782 | -0.064087 | -0.13733 | -0.21057 | -0.064087 | 0.082397 | -0.14648 | 0.064087 | -0.10071 | 122.818 | 122.7905 | 59.0607 | -122.9507 | 122.7905 | 122.7539 | 59.1431 | -123.0652
466.0156 | 123.0515 | -59.024 | 63.858 | -0.20615 | 0.0095853 | 0.067823 | 0.068381 | 0.13035 | 0.0016321 | -0.0030185 | -0.13748 | -0.0050672 | 0.065759 | 0.060816 | 0.0037812 | -0.004924 | 63.7619 | 63.8763 | -0.032043 | -59.2209 | 63.8992 | -59.0652 | -59.111 | -59.0195 | 0.068665 | -59.2667 | 63.9221 | 63.8351 | -59.1293 | -59.2117 | -0.041199 | -0.086975 | 0.041199 | 122.9004 | -0.19684 | -0.10986 | -0.09613 | -0.10529 | -0.18768 | 0.064087 | 0.004578 | -0.24262 | -0.054932 | -0.022888 | 122.9233 | 122.7859 | 58.992 | -122.9691 | 122.9462 | 122.8592 | 59.0927 | -123.0698
467.0156 | 123.0377 | -59.0378 | 63.8535 | -0.44266 | 0.013003 | 0.066969 | 0.071372 | 0.13142 | 0.0020593 | -0.0034457 | -0.023041 | -0.0033582 | 0.06341 | 0.062953 | 0.0039948 | -0.0034286 | 63.8031 | 63.8947 | -0.027466 | -59.2117 | 63.8489 | -59.0469 | -59.1293 | -59.0103 | 0.050354 | -59.2941 | 63.8535 | 63.8031 | -59.1476 | -59.2529 | -0.009155 | -0.091552 | -0.004578 | 122.9324 | -0.17395 | -0.082398 | -0.050354 | -0.10986 | -0.21515 | 0 | 0.027466 | -0.25635 | -0.041198 | -0.050354 | 122.8867 | 122.8409 | 59.0103 | -122.9828 | 122.8912 | 122.8409 | 59.0881 | -123.1064
468.0156 | 123.024 | -59.0424 | 63.9038 | -0.25955 | 0.011081 | 0.068464 | 0.07009 | 0.13206 | -0.0066993 | -0.0028049 | -0.045929 | -0.003999 | 0.063623 | 0.061671 | 0.0012176 | -0.003856 | 63.7756 | 63.7161 | -0.14648 | -59.2163 | 63.9084 | -59.0836 | -59.1431 | -59.0424 | 0.050354 | -59.2987 | 63.8992 | 63.8535 | -59.1431 | -59.2392 | -0.041199 | -0.10071 | 0.004577 | 122.7585 | -0.17395 | -0.073243 | -0.12817 | -0.10071 | -0.19684 | -0.004578 | 0 | -0.25635 | -0.059509 | -0.050354 | 122.9507 | 122.818 | 58.8959 | -123.0469 | 122.9416 | 122.8958 | 59.0927 | -123.143
469.0156 | 123.0469 | -59.0469 | 63.8535 | 0.97641 | 0.010226 | 0.069319 | 0.072226 | 0.13206 | 0.0018457 | -0.0030185 | -0.015411 | -0.003999 | 0.062769 | 0.061244 | 0.0035674 | -0.0070602 | 63.7665 | 63.9175 | -0.027466 | -59.2255 | 63.8626 | -59.0652 | -59.1248 | -59.0012 | 0.045776 | -59.2941 | 63.8763 | 63.7894 | -59.1522 | -59.2346 | -0.018311 | -0.07782 | 0.009155 | 122.9645 | -0.17853 | -0.10071 | -0.086976 | -0.10529 | -0.18768 | 0.022888 | 0.045776 | -0.24719 | -0.059509 | -0.064087 | 122.9095 | 122.8134 | 59.0195 | -122.9782 | 122.9233 | 122.8363 | 59.0927 | -123.0881
470.0156 | 123.1384 | -59.0057 | 63.8168 | 0.14481 | 0.0085171 | 0.065901 | 0.068167 | 0.13121 | -0.0043495 | -0.0025913 | 0.32791 | -0.00464 | 0.062555 | 0.060389 | 0.0033538 | -0.0036424 | 63.7756 | 63.9267 | -0.032043 | -59.198 | 63.8123 | -59.0744 | -59.1431 | -58.9325 | -0.18768 | -59.3124 | 63.7619 | 63.7207 | -59.1705 | -59.2209 | -0.068665 | -0.13733 | -0.004577 | 122.9324 | -0.19226 | -0.054932 | -0.041198 | -0.16479 | -0.21515 | -0.054931 | 0.073242 | -0.3067 | -0.091553 | -0.09613 | 122.818 | 122.7814 | 58.9737 | -122.9599 | 122.7676 | 122.7264 | 58.8181 | -123.0377
471.0156 | 123.0423 | -59.0469 | 63.826 | -0.03067 | 0.012362 | 0.068464 | 0.07009 | 0.1295 | 0.0014185 | -0.0013095 | -0.015411 | -0.0025038 | 0.065332 | 0.059535 | 0.0024994 | -0.0064194 | 63.7756 | 63.8626 | -0.068665 | -59.2438 | 63.8992 | -59.0744 | -59.1248 | -59.0332 | -0.013733 | -59.3216 | 63.8809 | 63.7939 | -59.1522 | -59.23 | -0.027466 | -0.07782 | 0.073242 | 122.9095 | -0.19684 | -0.11902 | -0.050354 | -0.10529 | -0.18311 | 0.054931 | 0.013733 | -0.27466 | -0.091552 | -0.032044 | 122.9462 | 122.8226 | 58.9783 | -122.9507 | 122.9279 | 122.8409 | 59.0332 | -123.056
472.0156 | 123.0698 | -59.0469 | 63.8443 | -0.17563 | 0.010653 | 0.066541 | 0.069663 | 0.13121 | -0.0034949 | -0.0017369 | -0.15274 | -0.0033582 | 0.065546 | 0.061885 | 0.0033538 | -0.006633 | 63.7802 | 63.8809 | -0.009155 | -59.198 | 63.8901 | -59.0469 | -59.1248 | -59.0012 | 0.068665 | -59.2712 | 63.8901 | 63.8123 | -59.1156 | -59.2392 | 0 | -0.07782 | 0.045777 | 122.9279 | -0.15106 | -0.073242 | -0.064087 | -0.068665 | -0.19226 | 0.045777 | 0.045776 | -0.2243 | -0.032043 | -0.032043 | 122.937 | 122.8271 | 59.0378 | -122.9691 | 122.937 | 122.8592 | 59.1156 | -123.0835
473.0156 | 123.0148 | -59.0607 | 63.8535 | -0.045929 | 0.011935 | 0.068464 | 0.071158 | 0.13035 | -0.00029045 | -0.00045506 | 0.045624 | -0.0020764 | 0.062769 | 0.060603 | 0.0046356 | -0.0034286 | 63.7756 | 63.8809 | -0.064087 | -59.2392 | 63.8672 | -59.0836 | -59.1248 | -59.0195 | 0.009155 | -59.3262 | 63.8718 | 63.8077 | -59.1568 | -59.2667 | -0.022888 | -0.064087 | 0.013732 | 122.9416 | -0.17853 | -0.11444 | -0.07782 | -0.09613 | -0.20599 | 0.01831 | 0.041199 | -0.2655 | -0.059509 | -0.045777 | 122.9279 | 122.8363 | 58.9966 | -122.9782 | 122.9324 | 122.8683 | 59.0698 | -123.1201
474.0156 | 123.0057 | -59.024 | 63.8855 | -0.30533 | 0.0070217 | 0.069959 | 0.071585 | 0.13078 | -0.0028541 | -0.0040867 | -0.13748 | -0.0037854 | 0.0664 | 0.060603 | 0.0020722 | -0.0019334 | 63.7527 | 63.8626 | -0.041199 | -59.23 | 63.8947 | -59.0698 | -59.1156 | -59.0286 | 0.045776 | -59.2941 | 63.9084 | 63.8168 | -59.1431 | -59.2209 | -0.045776 | -0.091553 | 0.009155 | 122.8867 | -0.20599 | -0.11444 | -0.13275 | -0.11902 | -0.19684 | 0.022888 | -0.004577 | -0.27008 | -0.073242 | -0.068665 | 122.9187 | 122.7768 | 58.9828 | -123.0011 | 122.9324 | 122.8409 | 59.0698 | -123.1064
475.0156 | 123.1247 | -59.0103 | 63.7802 | 0.16769 | 0.0055265 | 0.068037 | 0.067526 | 0.1327 | -0.0071265 | -0.0051547 | 0.32028 | -0.0059216 | 0.063837 | 0.060176 | 0.0020722 | -0.0019334 | 63.7573 | 63.945 | -0.027466 | -59.2163 | 63.7985 | -59.0469 | -59.1339 | -58.9737 | 0.009155 | -59.23 | 63.8214 | 63.739 | -59.1339 | -59.2575 | -0.036621 | -0.1236 | 0.018311 | 122.9553 | -0.20599 | -0.082398 | -0.022888 | -0.1236 | -0.24719 | 0.041199 | 0.036621 | -0.21973 | 0.027465 | -0.041198 | 122.8088 | 122.7676 | 58.9828 | -122.9141 | 122.8317 | 122.7493 | 59.0195 | -123.0377
476.0156 | 122.9507 | -59.0561 | 63.8351 | -0.15274 | 0.010226 | 0.068037 | 0.07009 | 0.13206 | 0.0022729 | -0.0010959 | -0.045929 | -0.003999 | 0.063623 | 0.061885 | 0.0031402 | -0.0036424 | 63.8031 | 63.8809 | -0.022888 | -59.2026 | 63.8809 | -59.0607 | -59.1202 | -58.9966 | 0.054932 | -59.2712 | 63.8763 | 63.8168 | -59.1248 | -59.2255 | -0.004578 | -0.064087 | 0.045776 | 122.937 | -0.14648 | -0.082398 | -0.032043 | -0.068665 | -0.16937 | 0.041199 | 0.059509 | -0.21515 | -0.045776 | -0.018311 | 122.937 | 122.8592 | 59.0332 | -122.9553 | 122.9324 | 122.8729 | 59.111 | -123.0606
477.0156 | 123.024 | -59.0561 | 63.8443 | 0.053253 | 0.011294 | 0.067823 | 0.070517 | 0.13163 | 0.0012047 | -0.0028049 | 0.053253 | -0.0027174 | 0.062555 | 0.060603 | 0.0033538 | -0.003215 | 63.7527 | 63.8443 | -0.082397 | -59.2575 | 63.8626 | -59.0744 | -59.1248 | -59.0561 | -0.018311 | -59.3216 | 63.8626 | 63.8123 | -59.1614 | -59.2438 | -0.018311 | -0.068665 | 0.018311 | 122.9004 | -0.20142 | -0.13275 | -0.091552 | -0.10529 | -0.18768 | 0.018311 | 0 | -0.2655 | -0.07782 | -0.032043 | 122.9187 | 122.8088 | 58.9737 | -122.9691 | 122.9187 | 122.8683 | 59.0378 | -123.0881
478.0156 | 123.0331 | -59.0195 | 63.8489 | -0.17563 | 0.011081 | 0.067823 | 0.070303 | 0.13249 | -0.0039221 | -0.0023777 | -0.099335 | -0.0035718 | 0.064905 | 0.060176 | 0.0014312 | -0.0040696 | 63.8077 | 63.8901 | -0.022888 | -59.2026 | 63.8947 | -59.0698 | -59.1339 | -58.9966 | 0.073242 | -59.2804 | 63.8809 | 63.8351 | -59.1431 | -59.23 | -0.050354 | -0.11444 | 0.045776 | 122.9095 | -0.18311 | -0.068665 | -0.041199 | -0.1236 | -0.21057 | 0.032043 | 0.022888 | -0.26093 | -0.050354 | -0.013733 | 122.9141 | 122.8271 | 58.9966 | -122.9828 | 122.9004 | 122.8546 | 59.0927 | -123.0789
479.0156 | 123.0286 | -59.0378 | 63.8535 | -0.0077822 | 0.013644 | 0.069532 | 0.071585 | 0.12993 | 0.0027001 | 0.00018594 | 0.022736 | -0.0025038 | 0.064264 | 0.061885 | 0.0029266 | -0.0059922 | 63.7573 | 63.8672 | -0.073242 | -59.2438 | 63.8947 | -59.079 | -59.1293 | -59.0515 | -0.018311 | -59.3262 | 63.8626 | 63.8123 | -59.166 | -59.2438 | -0.041198 | -0.091552 | 0.041198 | 122.905 | -0.20599 | -0.11444 | -0.096131 | -0.12817 | -0.20599 | 0.009155 | -0.013733 | -0.28839 | -0.082398 | -0.041199 | 122.9324 | 122.7951 | 58.9645 | -122.9828 | 122.9004 | 122.85 | 59.0195 | -123.0972
480.0156 | 123.1064 | -59.0469 | 63.7756 | -0.11459 | 0.0091581 | 0.067182 | 0.068808 | 0.13163 | -0.0030677 | -0.0028049 | 0.31265 | -0.0054944 | 0.064051 | 0.062525 | -0.00091858 | -0.0034286 | 63.7802 | 63.9267 | -0.022888 | -59.2072 | 63.8077 | -59.0698 | -59.1202 | -58.9645 | 0.032043 | -59.2209 | 63.8031 | 63.7573 | -59.1476 | -59.2163 | -0.022888 | -0.073242 | 0.032043 | 122.9736 | -0.16022 | -0.086975 | 0.004577 | -0.10071 | -0.16937 | 0.027466 | 0.082397 | -0.17395 | -0.004577 | -0.018311 | 122.8546 | 122.8271 | 59.024 | -122.8958 | 122.85 | 122.8043 | 59.079 | -122.9919
481.0156 | 123.0103 | -59.0469 | 63.826 | -0.068817 | 0.011081 | 0.06761 | 0.070731 | 0.12993 | 0.0029137 | -0.0021641 | 0.0074766 | -0.0020764 | 0.063837 | 0.061885 | 0.0024994 | -0.0051376 | 63.7985 | 63.8672 | -0.054932 | -59.2346 | 63.8855 | -59.0881 | -59.1202 | -59.0378 | -0.009155 | -59.3124 | 63.8718 | 63.8214 | -59.166 | -59.2529 | -0.041199 | -0.073242 | 0.059509 | 122.9141 | -0.18768 | -0.11444 | -0.027466 | -0.11902 | -0.20599 | 0.045776 | 0.009155 | -0.2655 | -0.059509 | -0.004578 | 122.9324 | 122.8455 | 58.992 | -122.9462 | 122.9187 | 122.8683 | 59.0378 | -123.0789
482.0156 | 123.0515 | -59.0424 | 63.8809 | -0.25192 | 0.0063809 | 0.066969 | 0.069022 | 0.12864 | -0.0030677 | -0.0017369 | -0.11459 | -0.0042126 | 0.062982 | 0.060176 | 0.0024994 | -0.0036424 | 63.7482 | 63.8535 | -0.050354 | -59.2255 | 63.8901 | -59.0607 | -59.1248 | -59.0378 | 0.045776 | -59.2941 | 63.9267 | 63.858 | -59.1476 | -59.2255 | -0.018311 | -0.082398 | 0.009156 | 122.8958 | -0.18311 | -0.10071 | -0.13275 | -0.10529 | -0.18311 | 0.045777 | 0.004577 | -0.25177 | -0.068664 | -0.022888 | 122.9324 | 122.7905 | 58.992 | -123.0057 | 122.9691 | 122.9004 | 59.0881 | -123.1064
483.0156 | 123.0286 | -59.0469 | 63.8397 | 0.060882 | 0.011722 | 0.066328 | 0.068381 | 0.13185 | 0.00056395 | -0.0028049 | 0.053253 | -0.0042126 | 0.061701 | 0.060603 | 0.0029266 | -0.0042832 | 63.739 | 63.8306 | -0.10071 | -59.2529 | 63.8809 | -59.1019 | -59.1522 | -59.0652 | -0.082397 | -59.3811 | 63.8763 | 63.8168 | -59.1568 | -59.2667 | -0.054932 | -0.10529 | 0.041198 | 122.8775 | -0.20599 | -0.10071 | -0.10071 | -0.10986 | -0.21973 | 0.036621 | -0.018311 | -0.33417 | -0.11444 | -0.022889 | 122.9279 | 122.7859 | 58.9462 | -122.9919 | 122.9233 | 122.8638 | 58.9645 | -123.1064
484.0156 | 123.0927 | -59.0332 | 63.8443 | -0.16037 | 0.0097989 | 0.066328 | 0.072653 | 0.13228 | -0.00029045 | -0.0017369 | -0.068817 | -0.0037854 | 0.064905 | 0.060603 | 0.0018584 | -0.0064194 | 63.7711 | 63.8992 | -0.013733 | -59.198 | 63.8855 | -59.079 | -59.1522 | -58.9966 | -0.12817 | -59.3491 | 63.8489 | 63.8031 | -59.1614 | -59.2392 | -0.045776 | -0.11902 | 0.041199 | 122.9324 | -0.16479 | -0.045776 | -0.073242 | -0.12817 | -0.20599 | 0.004578 | 0.036621 | -0.31586 | -0.10986 | -0.041198 | 122.9187 | 122.8043 | 59.0195 | -122.9965 | 122.8821 | 122.8363 | 58.905 | -123.0835
485.0156 | 123.143 | -59.0332 | 63.7939 | 0.19821 | 0.0095853 | 0.068678 | 0.068167 | 0.13142 | -0.0024269 | -0.0032321 | 0.015106 | -0.00464 | 0.064478 | 0.059321 | 0.00079042 | -0.0017196 | 63.7848 | 63.8443 | -0.23346 | -59.23 | 63.7665 | -59.1202 | -59.1248 | -58.9462 | 0.009155 | -59.2163 | 63.7848 | 63.7482 | -59.1339 | -59.23 | -0.086975 | -0.091553 | -0.027466 | 122.8775 | -0.19684 | -0.10529 | -0.009155 | -0.10071 | -0.19684 | -0.009155 | 0.086975 | -0.18311 | 0.013733 | -0.045776 | 122.7997 | 122.818 | 58.7997 | -122.9187 | 122.818 | 122.7814 | 59.0424 | -123.024
486.0156 | 123.0606 | -59.0652 | 63.8397 | -0.10696 | 0.0097989 | 0.066328 | 0.069876 | 0.13121 | 0.00035035 | -0.0021641 | -0.068817 | -0.003999 | 0.064478 | 0.061885 | 0.001004 | -0.003856 | 63.7894 | 63.8901 | -0.009155 | -59.2026 | 63.9084 | -59.0652 | -59.1385 | -58.992 | 0.059509 | -59.2758 | 63.8763 | 63.8077 | -59.1339 | -59.23 | 0 | -0.073242 | 0.068664 | 122.9553 | -0.13733 | -0.064087 | -0.050354 | -0.068664 | -0.16479 | 0.036621 | 0.073243 | -0.21057 | -0.045776 | -0.032044 | 122.9736 | 122.8546 | 59.0561 | -122.9782 | 122.9416 | 122.8729 | 59.1248 | -123.0698
487.0156 | 122.9782 | -59.0698 | 63.8306 | 0.0074768 | 0.011722 | 0.06761 | 0.069022 | 0.13163 | 0.00099115 | -0.0017369 | 0.068512 | -0.0031446 | 0.067468 | 0.061885 | 0.0031402 | -0.0044968 | 63.7527 | 63.8351 | -0.091553 | -59.2438 | 63.8855 | -59.0836 | -59.1476 | -59.0424 | -0.032043 | -59.3399 | 63.8809 | 63.8123 | -59.166 | -59.2575 | -0.013733 | -0.07782 | 0.054932 | 122.905 | -0.17395 | -0.09613 | -0.077819 | -0.096131 | -0.18768 | 0.050354 | 0.027466 | -0.27008 | -0.082398 | -0.01831 | 122.9553 | 122.8226 | 58.9783 | -122.9782 | 122.9507 | 122.8821 | 59.0378 | -123.0881
488.0156 | 123.0515 | -59.0195 | 63.8809 | -0.18326 | 0.0095853 | 0.06526 | 0.068808 | 0.12907 | -7.6852e-05 | -0.0034457 | -0.17563 | -0.0048536 | 0.063837 | 0.061244 | 0.002713 | -0.0051376 | 63.7527 | 63.858 | -0.036621 | -59.2255 | 63.8901 | -59.0607 | -59.1385 | -59.0286 | 0.050354 | -59.2758 | 63.8718 | 63.8214 | -59.1339 | -59.2026 | -0.041199 | -0.11902 | 0.009156 | 122.8775 | -0.20599 | -0.086975 | -0.12817 | -0.11444 | -0.18311 | -0.009155 | -0.009155 | -0.25635 | -0.073242 | -0.059509 | 122.9095 | 122.7722 | 58.9828 | -123.0194 | 122.8912 | 122.8409 | 59.0698 | -123.0835
489.0156 | 123.0469 | -59.0378 | 63.8351 | -0.35873 | 0.012149 | 0.066969 | 0.070944 | 0.13121 | 0.0014185 | -0.0013095 | 0.015106 | -0.0042126 | 0.063623 | 0.062525 | 0.0037812 | -0.0036424 | 63.7939 | 63.9084 | -0.022888 | -59.2163 | 63.8901 | -59.0652 | -59.1339 | -58.9966 | 0.045776 | -59.2987 | 63.8626 | 63.8306 | -59.1385 | -59.2255 | -0.027466 | -0.09613 | 0.054932 | 122.9462 | -0.17853 | -0.082398 | -0.041199 | -0.10071 | -0.18768 | 0.027466 | 0.041199 | -0.26093 | -0.073242 | -0.004578 | 122.9279 | 122.8317 | 59.0149 | -122.9691 | 122.9004 | 122.8683 | 59.0836 | -123.0606
490.0156 | 122.9782 | -59.0286 | 63.8306 | -0.32059 | 0.011935 | 0.06825 | 0.07009 | 0.13057 | -0.00029045 | -0.0019505 | -0.03067 | -0.0027174 | 0.065332 | 0.062525 | 0.0022858 | -0.0047104 | 63.7985 | 63.8763 | -0.032043 | -59.2117 | 63.8718 | -59.0744 | -59.1293 | -58.9966 | 0.050354 | -59.2941 | 63.858 | 63.8123 | -59.1339 | -59.2392 | -0.045777 | -0.10071 | 0.041199 | 122.905 | -0.18311 | -0.082398 | -0.032043 | -0.10529 | -0.21057 | 0.027466 | 0.032043 | -0.2655 | -0.054931 | -0.01831 | 122.9004 | 122.8271 | 58.9966 | -122.9599 | 122.8867 | 122.8409 | 59.079 | -123.0698
491.0156 | 123.0057 | -59.0515 | 63.8489 | 0.10666 | 0.010013 | 0.066755 | 0.070517 | 0.12993 | 0.00056395 | -0.0032321 | 0.19058 | -0.0027174 | 0.065973 | 0.061457 | 0.0024994 | -0.003215 | 63.707 | 63.7756 | -0.15564 | -59.2712 | 63.8763 | -59.0744 | -59.1385 | -59.0698 | -0.21515 | -59.5505 | 63.7894 | 63.7894 | -59.1888 | -59.2529 | -0.022888 | -0.086975 | 0.027466 | 122.8271 | -0.21973 | -0.13275 | -0.14191 | -0.13733 | -0.20142 | -0.059509 | -0.01831 | -0.49896 | -0.29755 | -0.059509 | 122.9279 | 122.7585 | 58.8959 | -122.9874 | 122.8409 | 122.8409 | 58.8364 | -123.1018
492.0156 | 123.0377 | -59.0378 | 63.826 | -0.045929 | 0.01044 | 0.066114 | 0.070944 | 0.13206 | 0.00013675 | -0.0021641 | 0.0074766 | -0.0031446 | 0.062342 | 0.062739 | 0.0022858 | -0.0047104 | 63.8077 | 63.8855 | -0.041199 | -59.2255 | 63.858 | -59.0561 | -59.1248 | -58.9874 | 0.041199 | -59.2804 | 63.858 | 63.8306 | -59.166 | -59.2117 | -0.01831 | -0.086975 | 0.032043 | 122.9233 | -0.18768 | -0.10071 | -0.018311 | -0.12817 | -0.17395 | 0.032043 | 0.050354 | -0.24262 | -0.068665 | 0.004577 | 122.8958 | 122.8455 | 58.9966 | -122.9507 | 122.8958 | 122.8683 | 59.079 | -123.0377
493.0156 | 123.0011 | -59.0469 | 63.8535 | -0.015411 | 0.012149 | 0.06761 | 0.071158 | 0.13099 | -7.6852e-05 | -0.0019505 | 0.17532 | -0.0054944 | 0.066187 | 0.060603 | 0.0031402 | -0.0040696 | 63.6978 | 63.7802 | -0.15564 | -59.2758 | 63.8809 | -59.0881 | -59.1568 | -59.0744 | -0.34332 | -59.5276 | 63.7985 | 63.7802 | -59.1843 | -59.2621 | -0.041199 | -0.10986 | 0.027465 | 122.8271 | -0.22888 | -0.11902 | -0.15564 | -0.13733 | -0.21515 | -0.054932 | -0.027466 | -0.48065 | -0.2655 | -0.073243 | 122.9279 | 122.7448 | 58.8913 | -123.0103 | 122.8455 | 122.8271 | 58.7036 | -123.1155
494.0156 | 123.0652 | -59.0607 | 63.8351 | -0.0383 | 0.011508 | 0.064619 | 0.067954 | 0.13121 | -0.00029045 | -0.0032321 | -0.0077819 | -0.00229 | 0.064691 | 0.061885 | 0.0020722 | -0.0027878 | 63.8123 | 63.8809 | -0.036621 | -59.2209 | 63.8901 | -59.0561 | -59.1431 | -58.992 | 0.027466 | -59.2987 | 63.8626 | 63.826 | -59.1339 | -59.2529 | 0.004578 | -0.082397 | 0.054932 | 122.9416 | -0.16022 | -0.07782 | -0.022888 | -0.073242 | -0.19226 | 0.027466 | 0.068665 | -0.23804 | -0.045776 | -0.009155 | 122.9507 | 122.8729 | 59.024 | -122.9782 | 122.9233 | 122.8867 | 59.0881 | -123.0881
495.0156 | 122.9965 | -59.0378 | 63.8397 | 0.045624 | 0.012149 | 0.068678 | 0.068594 | 0.12907 | -0.00029045 | -0.00045506 | 0.076141 | -0.002931 | 0.066828 | 0.061885 | 0.0033538 | -0.004924 | 63.7344 | 63.8535 | -0.086975 | -59.2438 | 63.8672 | -59.0881 | -59.1293 | -59.0607 | -0.013733 | -59.3216 | 63.8763 | 63.826 | -59.1705 | -59.2484 | -0.050354 | -0.091552 | 0.027465 | 122.8912 | -0.20599 | -0.11444 | -0.10529 | -0.13275 | -0.21057 | 0.036621 | -0.022888 | -0.28381 | -0.073242 | -0.013733 | 122.905 | 122.7722 | 58.9508 | -122.9691 | 122.9141 | 122.8638 | 59.024 | -123.0881
496.0156 | 123.0011 | -59.0424 | 63.8168 | -0.12985 | 0.0095853 | 0.069746 | 0.068381 | 0.12822 | -0.0028541 | -0.0019505 | -0.03067 | -0.003999 | 0.068323 | 0.060816 | 0.0042084 | -0.005565 | 63.7848 | 63.8855 | -0.013733 | -59.2072 | 63.8901 | -59.079 | -59.1293 | -58.992 | 0.068665 | -59.2621 | 63.8809 | 63.8306 | -59.1614 | -59.2484 | -0.036621 | -0.086975 | 0.073243 | 122.9279 | -0.16479 | -0.07782 | -0.032043 | -0.11902 | -0.20599 | 0.064087 | 0.050354 | -0.21973 | -0.013733 | 0.013733 | 122.9324 | 122.8271 | 59.0286 | -122.9462 | 122.9233 | 122.8729 | 59.111 | -123.0652
497.0156 | 123.0286 | -59.0698 | 63.8077 | 0.14481 | 0.011081 | 0.068037 | 0.069449 | 0.13185 | 0.00056395 | -0.0032321 | 0.22873 | -0.0050672 | 0.064264 | 0.059748 | 0.0012176 | -0.0053512 | 63.7161 | 63.8168 | -0.15106 | -59.2621 | 63.8809 | -59.0973 | -59.1614 | -59.0561 | -0.086975 | -59.3308 | 63.8489 | 63.7848 | -59.1614 | -59.2392 | -0.027466 | -0.091553 | 0.073242 | 122.8867 | -0.19226 | -0.10071 | -0.091553 | -0.091553 | -0.16937 | 0.041199 | 0.013733 | -0.26093 | -0.091553 | -0.022888 | 122.9507 | 122.7859 | 58.9188 | -122.9691 | 122.9187 | 122.8546 | 58.9828 | -123.0469
498.0156 | 123.0057 | -59.0469 | 63.826 | -0.015411 | 0.012576 | 0.066541 | 0.071158 | 0.12971 | 0.0024865 | -0.0017369 | 0.0914 | -0.0044264 | 0.065973 | 0.060389 | 0.0037812 | -0.0044968 | 63.7527 | 63.8123 | -0.091553 | -59.2529 | 63.8535 | -59.0836 | -59.1293 | -59.0607 | -0.036621 | -59.3308 | 63.8763 | 63.826 | -59.1522 | -59.2346 | -0.036621 | -0.082397 | 0.027466 | 122.8592 | -0.20599 | -0.1236 | -0.073242 | -0.10529 | -0.18768 | 0.050354 | -0.013733 | -0.28381 | -0.096131 | 0 | 122.9004 | 122.7997 | 58.9554 | -122.9553 | 122.9233 | 122.8729 | 59.0103 | -123.0606
499.0156 | 123.0515 | -59.0561 | 63.8031 | 0.10666 | 0.010867 | 0.067182 | 0.068808 | 0.12993 | -0.0017859 | -0.0038731 | 0.26688 | -0.0020764 | 0.064905 | 0.062098 | 0.002713 | -0.0040696 | 63.7207 | 63.8077 | -0.13733 | -59.2667 | 63.8763 | -59.0836 | -59.1522 | -59.0515 | -0.073242 | -59.317 | 63.858 | 63.8168 | -59.1797 | -59.2392 | -0.027466 | -0.096131 | 0.073242 | 122.8638 | -0.21057 | -0.11444 | -0.082398 | -0.1236 | -0.18311 | 0.054931 | 0.004577 | -0.26093 | -0.07782 | 0.013732 | 122.9324 | 122.7768 | 58.9188 | -122.9553 | 122.9141 | 122.8729 | 58.9828 | -123.0423
500.0156 | 122.9828 | -59.0607 | 63.8351 | 0.0074768 | 0.010013 | 0.06825 | 0.069663 | 0.13078 | 0.0031273 | -0.00088226 | 0.09903 | -0.0016492 | 0.063196 | 0.064021 | 0.004422 | -0.0019334 | 63.7436 | 63.8214 | -0.10071 | -59.2575 | 63.8672 | -59.0973 | -59.1568 | -59.0607 | -0.054932 | -59.3216 | 63.8718 | 63.8214 | -59.1568 | -59.2529 | -0.036621 | -0.09613 | 0.032043 | 122.8821 | -0.19684 | -0.10071 | -0.091553 | -0.09613 | -0.19226 | 0.036621 | 0 | -0.26093 | -0.068664 | -0.013733 | 122.9279 | 122.8043 | 58.96 | -122.9919 | 122.9324 | 122.8821 | 59.0057 | -123.0881
501.0156 | 123.0286 | -59.0469 | 63.8123 | 0.12192 | 0.010013 | 0.067823 | 0.071372 | 0.13185 | -0.00071785 | -0.0023777 | 0.22873 | -0.0033582 | 0.062555 | 0.061244 | 0.0024994 | -0.0036424 | 63.7207 | 63.7939 | -0.14191 | -59.2667 | 63.8718 | -59.111 | -59.1568 | -59.0378 | -0.073242 | -59.3033 | 63.8443 | 63.8168 | -59.1751 | -59.2484 | -0.064087 | -0.10986 | 0.059509 | 122.8409 | -0.21973 | -0.10986 | -0.091553 | -0.12817 | -0.20142 | 0.032043 | 0.009155 | -0.25635 | -0.054932 | 0.004577 | 122.9187 | 122.7676 | 58.905 | -122.9691 | 122.8912 | 122.8638 | 58.9737 | -123.0606
502.0156 | 123.0011 | -59.0469 | 63.8168 | -0.045929 | 0.010653 | 0.066328 | 0.071372 | 0.13142 | -7.6852e-05 | -0.0028049 | 0.022736 | -0.0027174 | 0.065546 | 0.059962 | 0.0029266 | -0.0062058 | 63.7939 | 63.858 | -0.054932 | -59.2209 | 63.8672 | -59.0744 | -59.1522 | -59.0378 | 0 | -59.3124 | 63.8535 | 63.8306 | -59.1476 | -59.2346 | -0.027466 | -0.10529 | 0.050354 | 122.905 | -0.17395 | -0.068664 | -0.022888 | -0.10071 | -0.18768 | 0.036622 | 0.009155 | -0.2655 | -0.07782 | 0.013733 | 122.9141 | 122.8409 | 58.992 | -122.9691 | 122.9004 | 122.8775 | 59.0469 | -123.0515
503.0156 | 123.0011 | -59.0515 | 63.826 | 0.14481 | 0.010653 | 0.065687 | 0.069235 | 0.13185 | -0.00029045 | -0.0036595 | 1.3121 | -0.0048536 | 0.063837 | 0.062312 | 0.0024994 | -0.0023606 | 63.7253 | 63.7665 | -0.16022 | -59.3994 | 63.8306 | -59.1202 | -59.1934 | -59.0515 | -0.041199 | -59.3582 | 63.8855 | 63.8168 | -59.1476 | -59.2712 | -0.068664 | -0.14191 | 0.004577 | 122.818 | -0.3479 | -0.20599 | -0.10071 | -0.09613 | -0.21973 | 0.059509 | 0 | -0.3067 | -0.086975 | -0.009156 | 122.8821 | 122.7768 | 58.8913 | -123.0194 | 122.937 | 122.8683 | 59.0103 | -123.0972
504.0156 | 123.0331 | -59.0698 | 63.8351 | 0.13718 | 0.011722 | 0.066328 | 0.071372 | 0.12736 | -0.00029045 | -0.0040867 | -0.54947 | -0.0033582 | 0.066187 | 0.060603 | 0.0029266 | -0.0025742 | 63.8077 | 63.382 | -0.35706 | -59.166 | 63.8214 | -59.1202 | -59.166 | -59.0698 | -0.10529 | -59.3582 | 63.8672 | 63.8214 | -59.1705 | -59.2529 | -0.050354 | -0.096131 | -0.013733 | 122.4518 | -0.096131 | 0 | -0.027466 | -0.10071 | -0.18311 | 0.032043 | 0 | -0.28839 | -0.10529 | -0.013733 | 122.8912 | 122.8775 | 58.7128 | -123.0011 | 122.937 | 122.8912 | 58.9645 | -123.0881
505.0156 | 123.1522 | -59.0286 | 63.7848 | 0.19821 | 0.010013 | 0.064405 | 0.069663 | 0.13057 | -0.0028541 | -0.0030185 | 0.27451 | -0.0033582 | 0.06341 | 0.061885 | 0.0035674 | -0.004924 | 63.7848 | 63.8763 | -0.064087 | -59.1934 | 63.8168 | -59.0607 | -59.111 | -58.9508 | 0.032043 | -59.23 | 63.7848 | 63.7619 | -59.1431 | -59.2392 | -0.032044 | -0.082398 | 0.032043 | 122.905 | -0.1648 | -0.082397 | 0 | -0.11444 | -0.21057 | 0 | 0.077819 | -0.20142 | 0.009155 | -0.022888 | 122.8455 | 122.8134 | 58.9645 | -122.8958 | 122.8134 | 122.7905 | 59.0607 | -123.024
506.0156 | 123.0331 | -59.0607 | 63.7985 | 0.12955 | 0.011081 | 0.06825 | 0.070303 | 0.12971 | 0.0059045 | -0.0017369 | 0.13718 | -0.00464 | 0.066614 | 0.062525 | 0.0035674 | -0.003215 | 63.4827 | 64.0823 | 0 | -59.285 | 63.8763 | -59.0698 | -59.166 | -59.0469 | -0.10529 | -59.3582 | 63.8809 | 63.7985 | -59.1888 | -59.2575 | -0.009155 | -0.10529 | 0.07782 | 123.143 | -0.2243 | -0.11902 | -0.31586 | -0.12817 | -0.19684 | 0.082397 | 0.013733 | -0.29755 | -0.10071 | 0 | 122.937 | 122.5433 | 59.0607 | -122.9645 | 122.9416 | 122.8592 | 58.9554 | -123.056
507.0156 | 123.1155 | -59.0149 | 63.7802 | 0.19821 | 0.0078763 | 0.066541 | 0.069235 | 0.13142 | -0.0013587 | -0.0021641 | 0.28976 | -0.0059216 | 0.064264 | 0.059748 | 0.0042084 | -0.003215 | 63.7482 | 63.9084 | -0.036621 | -59.2072 | 63.8351 | -59.0744 | -59.1293 | -58.9691 | 0.027466 | -59.2392 | 63.8168 | 63.7848 | -59.1431 | -59.2392 | -0.059509 | -0.11444 | 0.054932 | 122.9233 | -0.19226 | -0.07782 | -0.032043 | -0.12817 | -0.2243 | 0.036621 | 0.045777 | -0.2243 | 0 | 0.004578 | 122.85 | 122.7631 | 58.9783 | -122.9095 | 122.8317 | 122.7997 | 59.0424 | -123.0194
508.0156 | 123.0103 | -59.0424 | 63.8306 | 0.16769 | 0.011081 | 0.065901 | 0.070731 | 0.13099 | 0.0054773 | -0.0017369 | 0.27451 | -0.002931 | 0.063837 | 0.061885 | 0.002713 | -0.0059922 | 63.4735 | 64.1144 | 0.009155 | -59.2712 | 63.8763 | -59.0836 | -59.1431 | -59.0378 | -0.086975 | -59.3399 | 63.858 | 63.826 | -59.1614 | -59.2392 | -0.041199 | -0.10071 | 0.045777 | 123.1567 | -0.22888 | -0.12817 | -0.35705 | -0.11902 | -0.19684 | 0.027466 | 0.004577 | -0.29755 | -0.10071 | -0.004577 | 122.9187 | 122.5159 | 59.0515 | -122.9736 | 122.9004 | 122.8683 | 58.9554 | -123.0698
509.0156 | 123.056 | -59.0424 | 63.7894 | 0.16006 | 0.0093717 | 0.066969 | 0.069449 | 0.13057 | -0.0017859 | -0.0025913 | 0.24399 | -0.0042126 | 0.065973 | 0.061671 | 0.0016448 | -0.003856 | 63.7436 | 63.8123 | -0.1236 | -59.2712 | 63.8718 | -59.0836 | -59.1431 | -59.024 | -0.059509 | -59.3124 | 63.8351 | 63.8123 | -59.1476 | -59.2667 | -0.041199 | -0.10071 | 0.082397 | 122.8546 | -0.22888 | -0.12817 | -0.045777 | -0.10529 | -0.22431 | 0.045776 | 0.01831 | -0.27008 | -0.045776 | 0.022888 | 122.9141 | 122.7859 | 58.9188 | -122.9324 | 122.8775 | 122.8546 | 58.9828 | -123.056
510.0156 | 123.0011 | -59.0515 | 63.8168 | 0.12192 | 0.012362 | 0.065687 | 0.069235 | 0.13057 | -0.00029045 | 0.0029629 | 0.44998 | -0.0048536 | 0.064051 | 0.063807 | 0.0024994 | -0.0044968 | 63.4415 | 63.707 | -0.07782 | -59.1064 | 63.8855 | -59.0881 | -59.1614 | -59.0561 | -0.07782 | -59.3536 | 63.8763 | 63.8306 | -59.1888 | -59.2529 | -0.036621 | -0.10986 | 0.068665 | 122.7585 | -0.054931 | 0.054932 | -0.37537 | -0.13733 | -0.20142 | 0.05951 | -0.004577 | -0.30212 | -0.10071 | 0.013733 | 122.937 | 122.493 | 58.9737 | -122.9782 | 122.9279 | 122.8821 | 58.9737 | -123.0698
511.0156 | 123.111 | -59.0149 | 63.7802 | 0.57968 | 0.0068081 | 0.066755 | 0.066031 | 0.13014 | -0.0049903 | -0.0017369 | 0.28976 | -0.005708 | 0.062982 | 0.060603 | 0.00057682 | -0.0030014 | 63.8489 | 63.8992 | -0.027466 | -59.1934 | 63.8031 | -59.0424 | -59.1064 | -58.9371 | 0.041199 | -59.2255 | 63.8123 | 63.7665 | -59.1339 | -59.23 | -0.027465 | -0.091552 | 0.022889 | 122.9141 | -0.17853 | -0.086975 | 0.068665 | -0.11902 | -0.21515 | 0.032044 | 0.07782 | -0.21057 | 0.004578 | -0.013733 | 122.818 | 122.8638 | 58.9874 | -122.8867 | 122.8271 | 122.7814 | 59.0561 | -123.0103
512.0156 | 123.0286 | -59.0515 | 63.8306 | 0.16769 | 0.0087307 | 0.06761 | 0.072653 | 0.13078 | 0.00056395 | -0.00024146 | 0.23636 | -0.00229 | 0.062982 | 0.06103 | 0.0024994 | -0.0051376 | 63.7344 | 63.7848 | -0.13733 | -59.2712 | 63.8535 | -59.079 | -59.1522 | -59.0057 | -0.064087 | -59.2987 | 63.8397 | 63.8031 | -59.1614 | -59.2667 | -0.027465 | -0.10071 | 0.022889 | 122.8363 | -0.21973 | -0.11902 | -0.09613 | -0.10986 | -0.21515 | 0.009156 | 0.045777 | -0.24719 | -0.032043 | -0.027465 | 122.905 | 122.7859 | 58.9142 | -122.9828 | 122.8912 | 122.8546 | 58.9874 | -123.0972
513.0156 | 123.1247 | -59.0286 | 63.7848 | 0.16006 | 0.0078763 | 0.065046 | 0.06774 | 0.12843 | -0.0030677 | -0.0053683 | 0.23636 | -0.003999 | 0.061914 | 0.06103 | 0.00036322 | -0.004924 | 63.9633 | 63.9221 | -0.064087 | -59.166 | 63.8306 | -59.0607 | -59.1019 | -58.9325 | 0.036621 | -59.2209 | 63.8123 | 63.7711 | -59.1385 | -59.2346 | -0.032044 | -0.073243 | 0.045776 | 122.9507 | -0.13733 | -0.064087 | 0.17853 | -0.10986 | -0.20599 | 0.027466 | 0.09613 | -0.19226 | 0.013733 | -0.013733 | 122.8592 | 122.9919 | 58.9645 | -122.8867 | 122.8409 | 122.7997 | 59.0652 | -123.0194
514.0156 | 123.0423 | -59.0378 | 63.8123 | 0.11429 | 0.0074491 | 0.067396 | 0.069449 | 0.12971 | 0.00056395 | -0.0015231 | 0.20584 | -0.003999 | 0.064478 | 0.06103 | 0.0024994 | -0.0051376 | 63.7436 | 63.7939 | -0.13733 | -59.2667 | 63.8763 | -59.0927 | -59.1293 | -59.0286 | -0.091553 | -59.3124 | 63.8443 | 63.7894 | -59.1705 | -59.2575 | -0.054931 | -0.091552 | 0.064087 | 122.8317 | -0.22888 | -0.13733 | -0.068665 | -0.13275 | -0.21973 | 0.032043 | 0.009156 | -0.27466 | -0.054932 | -0.022888 | 122.9141 | 122.7814 | 58.9005 | -122.9416 | 122.8821 | 122.8271 | 58.9462 | -123.0698
515.0156 | 123.1384 | -59.0103 | 63.7756 | 0.16006 | 0.0080899 | 0.068464 | 0.067954 | 0.13163 | -0.0032813 | -0.0028049 | -0.076446 | -0.0054944 | 0.063196 | 0.060816 | 0.0024994 | -0.0023606 | 63.8077 | 63.7161 | -0.23346 | -59.2117 | 63.7756 | -59.0836 | -59.1293 | -58.9325 | 0.004578 | -59.2255 | 63.8168 | 63.7573 | -59.1431 | -59.2255 | -0.073242 | -0.11902 | 0 | 122.7264 | -0.20142 | -0.082398 | 0.032043 | -0.13275 | -0.21515 | 0.041198 | 0.07782 | -0.21515 | 0 | -0.018311 | 122.7859 | 122.818 | 58.7769 | -122.905 | 122.8271 | 122.7676 | 59.0149 | -123.0011
516.0156 | 122.9965 | -59.0561 | 63.8123 | 0.10666 | 0.011294 | 0.067182 | 0.07009 | 0.13057 | 0.0018457 | -0.0034457 | 0.12955 | -0.0042126 | 0.062769 | 0.064448 | 0.0046356 | -0.010265 | 63.7253 | 63.7482 | -0.16022 | -59.285 | 63.9038 | -59.1019 | -59.1568 | -58.992 | 0.19684 | -59.3765 | 63.8718 | 63.8306 | -59.1797 | -59.2621 | -0.045777 | -0.10071 | 0.091553 | 122.8043 | -0.22888 | -0.12817 | -0.086975 | -0.1236 | -0.20599 | 0.059509 | 0.064087 | -0.32043 | -0.11444 | 0.01831 | 122.9599 | 122.7814 | 58.8959 | -122.9691 | 122.9279 | 122.8867 | 59.2529 | -123.0743
517.0156 | 123.0972 | -59.0378 | 63.7939 | 0.12955 | 0.0046719 | 0.066114 | 0.069235 | 0.13014 | -0.0045631 | -0.0025913 | 0.33554 | -0.005708 | 0.062555 | 0.062525 | 0.0022858 | -0.0042832 | 63.7894 | 63.9038 | -0.027466 | -59.2117 | 63.8168 | -59.079 | -59.1385 | -58.9371 | 0.036621 | -59.2255 | 63.7939 | 63.7848 | -59.1385 | -59.2392 | -0.041198 | -0.10071 | 0.022888 | 122.9416 | -0.17395 | -0.073242 | -0.004577 | -0.10071 | -0.20142 | 0 | 0.10071 | -0.18768 | 0.013733 | -0.009155 | 122.8546 | 122.8271 | 59.0103 | -122.9324 | 122.8317 | 122.8226 | 59.0744 | -123.0331
518.0156 | 123.0881 | -59.0469 | 63.7939 | 0.16769 | 0.0083035 | 0.06761 | 0.071158 | 0.12971 | 0.00077755 | -0.0028049 | 0.22873 | -0.0020764 | 0.064691 | 0.060389 | 0.0042084 | -0.0053512 | 63.7665 | 63.8214 | -0.10529 | -59.2575 | 63.8718 | -59.079 | -59.1431 | -58.9691 | -0.013733 | -59.2712 | 63.826 | 63.7894 | -59.1705 | -59.2117 | -0.032043 | -0.09613 | 0.07782 | 122.8683 | -0.21057 | -0.11444 | -0.027466 | -0.1236 | -0.16479 | 0.032044 | 0.07782 | -0.2243 | -0.059509 | -0.004577 | 122.9187 | 122.8134 | 58.9417 | -122.937 | 122.8729 | 122.8363 | 59.0332 | -123.0057
519.0156 | 123.1064 | -59.0149 | 63.7894 | -0.0383 | 0.0076627 | 0.066969 | 0.067313 | 0.13249 | -0.0017859 | -0.0030185 | 0.30502 | -0.005708 | 0.061487 | 0.060603 | 0.0014312 | -0.003856 | 63.8123 | 63.9221 | -0.022888 | -59.2026 | 63.8031 | -59.0652 | -59.1156 | -58.9188 | 0.027466 | -59.2209 | 63.8077 | 63.739 | -59.1293 | -59.2255 | -0.050354 | -0.10071 | 0.013733 | 122.937 | -0.18768 | -0.086975 | 0.022888 | -0.11444 | -0.21057 | 0.01831 | 0.096131 | -0.20599 | 0.004578 | -0.050354 | 122.818 | 122.8271 | 58.992 | -122.905 | 122.8226 | 122.7539 | 59.0424 | -123.0148
520.0156 | 123.0743 | -59.024 | 63.7802 | 0.16769 | 0.0085171 | 0.065687 | 0.070303 | 0.13014 | 0.00013675 | -0.0038731 | 0.21347 | -0.0035718 | 0.061701 | 0.061457 | 0.0024994 | -0.0051376 | 63.7756 | 63.8214 | -0.12817 | -59.2575 | 63.858 | -59.0881 | -59.1431 | -58.9874 | -0.054932 | -59.2941 | 63.8489 | 63.7894 | -59.1385 | -59.2575 | -0.064087 | -0.11902 | 0.07782 | 122.8455 | -0.23346 | -0.11444 | -0.004577 | -0.11444 | -0.23346 | 0.068665 | 0.036621 | -0.27008 | -0.036621 | 0.009156 | 122.8821 | 122.7997 | 58.8959 | -122.9233 | 122.8729 | 122.8134 | 58.9691 | -123.0377
521.0156 | 123.1018 | -59.0286 | 63.7848 | 1.7928 | 0.0074491 | 0.065687 | 0.068381 | 0.13057 | -0.0039221 | -0.0040867 | 0.24399 | -0.0044264 | 0.060846 | 0.062525 | 0.0033538 | -0.0064194 | 63.8763 | 63.9175 | -0.032043 | -59.1888 | 63.7939 | -59.0515 | -59.1019 | -58.9462 | 0.032043 | -59.23 | 63.7894 | 63.7619 | -59.1248 | -59.2438 | -0.022889 | -0.073243 | 0.009155 | 122.9462 | -0.16022 | -0.086975 | 0.091553 | -0.096131 | -0.21515 | 0.004578 | 0.082397 | -0.20142 | 0.013732 | -0.022888 | 122.8226 | 122.905 | 58.9966 | -122.8867 | 122.818 | 122.7905 | 59.0607 | -123.0286
522.0156 | 123.0698 | -59.0561 | 63.826 | 0.099029 | 0.010867 | 0.066755 | 0.067954 | 0.13099 | 0.0027001 | -0.0028049 | 0.2211 | -0.0037854 | 0.065332 | 0.061885 | 0.0014312 | -0.0057786 | 63.7756 | 63.7985 | -0.13733 | -59.2712 | 63.8718 | -59.0927 | -59.1476 | -59.0286 | -0.064087 | -59.3033 | 63.8351 | 63.8031 | -59.1476 | -59.2438 | -0.036621 | -0.091553 | 0.045776 | 122.8546 | -0.21515 | -0.1236 | -0.050354 | -0.091553 | -0.18768 | 0.009155 | 0.027466 | -0.24719 | -0.05951 | -0.022888 | 122.9279 | 122.8317 | 58.9188 | -122.9736 | 122.8912 | 122.8592 | 58.992 | -123.0698
523.0156 | 123.1247 | -59.0195 | 63.7665 | 0.19821 | 0.0070217 | 0.067396 | 0.068808 | 0.13078 | -0.00093145 | -0.0025913 | 0.25925 | -0.003999 | 0.061914 | 0.059962 | 0.0035674 | -0.0042832 | 63.7711 | 63.858 | -0.10071 | -59.2438 | 63.8306 | -59.0927 | -59.1431 | -58.96 | 0.004578 | -59.2438 | 63.8123 | 63.7665 | -59.1385 | -59.2484 | -0.073242 | -0.1236 | 0.064087 | 122.8775 | -0.2243 | -0.10071 | 0.004578 | -0.11902 | -0.22888 | 0.045777 | 0.059509 | -0.2243 | 0.004578 | 0 | 122.85 | 122.7905 | 58.9188 | -122.9095 | 122.8317 | 122.7859 | 59.024 | -123.0148
524.0156 | 123.0103 | -59.0561 | 63.7985 | 0.13718 | 0.0083035 | 0.065687 | 0.066885 | 0.13057 | 0.0031273 | -0.0013095 | 0.16769 | -0.0033582 | 0.06106 | 0.061885 | 0.0059174 | -0.0044968 | 63.7482 | 63.7939 | -0.13733 | -59.2621 | 63.8718 | -59.0881 | -59.1385 | -59.0286 | -0.07782 | -59.3399 | 63.8397 | 63.8123 | -59.1568 | -59.2575 | -0.032044 | -0.082398 | 0.073242 | 122.85 | -0.20599 | -0.1236 | -0.050354 | -0.10071 | -0.20142 | 0.041199 | 0.027466 | -0.28381 | -0.082398 | 0.013733 | 122.9279 | 122.8043 | 58.9188 | -122.937 | 122.8958 | 122.8683 | 58.9783 | -123.056
525.0156 | 123.0972 | -59.0149 | 63.7939 | 0.022736 | 0.0070217 | 0.069105 | 0.067099 | 0.13035 | -0.0041357 | -0.0028049 | 0.26688 | -0.0042126 | 0.061914 | 0.059962 | 0.0031402 | -0.0040696 | 63.8031 | 63.945 | -0.041199 | -59.2072 | 63.8077 | -59.0561 | -59.1293 | -58.9462 | 0.036621 | -59.2255 | 63.8168 | 63.7665 | -59.1431 | -59.2484 | -0.041198 | -0.11444 | 0.013733 | 122.9599 | -0.19226 | -0.07782 | 0.009156 | -0.12817 | -0.23346 | 0.022888 | 0.068665 | -0.21057 | 0.022888 | -0.027466 | 122.8226 | 122.818 | 58.9737 | -122.9233 | 122.8317 | 122.7814 | 59.0515 | -123.0423
526.0156 | 123.0423 | -59.0469 | 63.7985 | 0.18295 | 0.010226 | 0.066969 | 0.070944 | 0.1295 | 0.0018457 | -0.00066866 | 0.2211 | -0.003999 | 0.065759 | 0.061244 | 0.0029266 | -0.0051376 | 63.7482 | 63.8351 | -0.13275 | -59.2758 | 63.8626 | -59.0927 | -59.1568 | -58.9966 | -0.032043 | -59.2941 | 63.8489 | 63.7482 | -59.1751 | -59.2712 | -0.045776 | -0.10986 | 0.064087 | 122.8821 | -0.22888 | -0.11902 | -0.050354 | -0.12817 | -0.2243 | 0.050354 | 0.050354 | -0.24719 | -0.022888 | -0.050354 | 122.9095 | 122.7951 | 58.9142 | -122.9553 | 122.8958 | 122.7951 | 59.0149 | -123.0698
527.0156 | 123.143 | -59.0195 | 63.7939 | 0.21347 | 0.0068081 | 0.068891 | 0.068808 | 0.13249 | 0.00035035 | -0.00024146 | 0.21347 | -0.0042126 | 0.064691 | 0.059962 | 0.0024994 | -0.0068466 | 63.652 | 64.119 | 0.091553 | -59.1797 | 63.8077 | -59.0607 | -59.0973 | -58.9325 | 0.045776 | -59.23 | 63.7985 | 63.7527 | -59.1248 | -59.2392 | -0.041199 | -0.07782 | 0.013733 | 123.1384 | -0.16022 | -0.082397 | -0.14191 | -0.10529 | -0.21973 | 0.004578 | 0.086975 | -0.21057 | 0.009155 | -0.041198 | 122.8271 | 122.6715 | 59.111 | -122.8912 | 122.818 | 122.7722 | 59.0652 | -123.0331
528.0156 | 123.0469 | -59.0515 | 63.8031 | 0.19821 | 0.011722 | 0.066755 | 0.072653 | 0.12971 | 0.00099115 | -0.00066866 | 0.19058 | -0.0020764 | 0.064051 | 0.06103 | 0.0022858 | -0.0057786 | 63.7344 | 63.8077 | -0.13275 | -59.2667 | 63.8626 | -59.0881 | -59.1522 | -59.0378 | -0.059509 | -59.317 | 63.8718 | 63.7985 | -59.1751 | -59.2621 | -0.036621 | -0.10071 | 0.059509 | 122.8592 | -0.21515 | -0.11444 | -0.068665 | -0.1236 | -0.21057 | 0.068664 | 0.013733 | -0.2655 | -0.054932 | -0.004578 | 122.9141 | 122.7859 | 58.9188 | -122.9553 | 122.9233 | 122.85 | 58.992 | -123.0652
529.0156 | 123.1293 | -58.9828 | 63.7756 | 0.14481 | 0.0083035 | 0.067182 | 0.070303 | 0.1327 | -0.0028541 | -0.0019505 | 0.26688 | -0.00464 | 0.064478 | 0.061885 | 0.0033538 | -0.005565 | 63.8306 | 63.9084 | -0.032043 | -59.1934 | 63.8123 | -59.0698 | -59.1248 | -58.9645 | 0.018311 | -59.2758 | 63.8123 | 63.7344 | -59.198 | -59.2667 | -0.086975 | -0.14191 | 0.036621 | 122.8912 | -0.21057 | -0.068664 | 0.054931 | -0.21515 | -0.28381 | 0.036621 | 0.01831 | -0.29297 | -0.009155 | -0.041199 | 122.7951 | 122.8134 | 58.9508 | -122.9004 | 122.7951 | 122.7173 | 59.0012 | -123.0423
530.0156 | 123.0011 | -59.079 | 63.8306 | -0.015411 | 0.014071 | 0.068464 | 0.068167 | 0.13121 | 0.0018457 | -0.0034457 | 0.037995 | -0.0010084 | 0.063623 | 0.061885 | 0.0031402 | -0.0068466 | 63.7527 | 63.7985 | -0.11902 | -59.2575 | 63.9084 | -59.0881 | -59.1293 | -59.0881 | -0.07782 | -59.3719 | 63.858 | 63.7985 | -59.1568 | -59.2621 | -0.009156 | -0.050354 | 0.07782 | 122.8775 | -0.17853 | -0.12817 | -0.077819 | -0.07782 | -0.18311 | 0.027466 | -0.009156 | -0.29297 | -0.10986 | -0.032043 | 122.9874 | 122.8317 | 58.96 | -122.9599 | 122.937 | 122.8775 | 59.0012 | -123.0927
531.0156 | 123.1018 | -59.0195 | 63.7711 | 0.19058 | 0.0089443 | 0.06761 | 0.067526 | 0.13099 | -0.0017859 | -0.00045506 | 0.26688 | -0.0048536 | 0.064905 | 0.061671 | 0.0022858 | -0.0040696 | 63.7756 | 63.8672 | -0.068665 | -59.2117 | 63.8306 | -59.0744 | -59.1385 | -58.9554 | 0.022888 | -59.2484 | 63.7894 | 63.739 | -59.1293 | -59.2255 | -0.054932 | -0.11902 | 0.059509 | 122.8867 | -0.19226 | -0.073242 | 0.004578 | -0.10986 | -0.20599 | 0.018311 | 0.064087 | -0.22888 | -0.022888 | -0.032043 | 122.85 | 122.7951 | 58.9508 | -122.9095 | 122.8088 | 122.7585 | 59.0424 | -122.9965
532.0156 | 123.0377 | -59.0561 | 63.8123 | 0.12955 | 0.010653 | 0.066541 | 0.070731 | 0.12993 | -0.0017859 | -0.0017369 | 0.16769 | -0.003999 | 0.065973 | 0.060176 | 0.004422 | -0.0036424 | 63.7344 | 63.7848 | -0.14191 | -59.2758 | 63.8809 | -59.0836 | -59.1568 | -59.0286 | -0.082397 | -59.3308 | 63.8626 | 63.8031 | -59.1751 | -59.2529 | -0.027466 | -0.10071 | 0.068664 | 122.8409 | -0.21973 | -0.11902 | -0.07782 | -0.11902 | -0.19684 | 0.050354 | 0.027466 | -0.27466 | -0.07782 | -0.009155 | 122.937 | 122.7905 | 58.9142 | -122.9691 | 122.9187 | 122.8592 | 58.9737 | -123.0652
533.0156 | 123.1155 | -59.0424 | 63.7802 | 0.18295 | 0.0083035 | 0.068891 | 0.067099 | 0.13099 | -0.0024269 | -0.0010959 | 0.28214 | -0.0035718 | 0.062342 | 0.061244 | 0.0048492 | -0.0044968 | 63.8168 | 63.8901 | -0.045776 | -59.1934 | 63.7894 | -59.0836 | -59.1339 | -59.0973 | -0.10529 | -59.1064 | 63.8077 | 63.7573 | -59.1248 | -59.2209 | -0.041199 | -0.091553 | 0.009156 | 122.9324 | -0.15106 | -0.059509 | 0.036621 | -0.082398 | -0.17853 | 0.027466 | -0.054932 | -0.064087 | 0.11444 | -0.022888 | 122.8317 | 122.8592 | 58.9966 | -122.9141 | 122.85 | 122.7997 | 58.9371 | -123.0011
534.0156 | 123.0286 | -59.0515 | 63.8031 | 1.5028 | 0.011081 | 0.068037 | 0.071799 | 0.13142 | -7.6852e-05 | -0.0021641 | 0.16006 | -0.0042126 | 0.064478 | 0.061671 | 0.0016448 | -0.004924 | 63.8489 | 63.7665 | -0.16479 | -59.2484 | 63.8763 | -59.0744 | -59.1522 | -59.0469 | -0.082397 | -59.3399 | 63.8763 | 63.8214 | -59.1797 | -59.2667 | -0.022888 | -0.10071 | 0.073242 | 122.818 | -0.19684 | -0.09613 | 0.045776 | -0.12817 | -0.21515 | 0.073242 | 0.004578 | -0.28839 | -0.073242 | 0.01831 | 122.9279 | 122.9004 | 58.8867 | -122.9553 | 122.9279 | 122.8729 | 58.9691 | -123.0698
535.0156 | 123.1338 | -59.024 | 63.7527 | 0.17532 | 0.0074491 | 0.065473 | 0.068808 | 0.13057 | -0.00093145 | -0.0021641 | 0.27451 | -0.0069898 | 0.063837 | 0.061244 | 0.0029266 | -0.0036424 | 63.7802 | 63.858 | -0.068665 | -59.1888 | 63.8489 | -59.0652 | -59.1431 | -58.9645 | 0.036621 | -59.2163 | 63.7985 | 63.7665 | -59.1476 | -59.2209 | -0.041199 | -0.11902 | 0.09613 | 122.8821 | -0.16479 | -0.045777 | 0.027465 | -0.1236 | -0.19684 | 0.045776 | 0.059509 | -0.19226 | 0.004577 | 0.013732 | 122.8729 | 122.8043 | 58.9554 | -122.8958 | 122.8226 | 122.7905 | 59.0607 | -122.9736
536.0156 | 122.9736 | -59.0378 | 63.8168 | 0.083771 | 0.010653 | 0.067396 | 0.067954 | 0.1295 | 0.0022729 | -0.0021641 | 0.0074766 | -0.0020764 | 0.063623 | 0.060816 | 0.0018584 | -0.0051376 | 63.739 | 63.8077 | -0.10986 | -59.2484 | 63.8809 | -59.1019 | -59.1476 | -59.0698 | -0.045776 | -59.3582 | 63.8672 | 63.826 | -59.1751 | -59.2712 | -0.064087 | -0.10986 | 0.064087 | 122.8455 | -0.21057 | -0.10071 | -0.077819 | -0.13733 | -0.23346 | 0.050354 | -0.032043 | -0.32043 | -0.086975 | 0.009156 | 122.9187 | 122.7768 | 58.9279 | -122.9645 | 122.905 | 122.8638 | 58.992 | -123.0881
537.0156 | 123.056 | -59.0561 | 63.8168 | 0.12955 | 0.011294 | 0.068037 | 0.069022 | 0.128 | -0.0011451 | -0.0019505 | 0.22873 | -0.0031446 | 0.062769 | 0.06103 | 0.004422 | -0.0040696 | 63.7253 | 63.7939 | -0.13275 | -59.2667 | 63.8626 | -59.0973 | -59.1614 | -59.024 | -0.068665 | -59.3216 | 63.8535 | 63.7894 | -59.1888 | -59.2484 | -0.041199 | -0.10529 | 0.045777 | 122.85 | -0.21057 | -0.10529 | -0.091552 | -0.13275 | -0.19226 | 0.036622 | 0.032043 | -0.2655 | -0.073242 | -0.027465 | 122.9187 | 122.7814 | 58.9233 | -122.9782 | 122.9095 | 122.8455 | 58.9874 | -123.0652
538.0156 | 123.0377 | -59.0561 | 63.7985 | 0.099029 | 0.011081 | 0.06761 | 0.07009 | 0.13292 | 0.00035035 | -0.00045506 | 0.19821 | -0.0037854 | 0.065546 | 0.060389 | 0.0031402 | -0.0059922 | 63.7299 | 63.7985 | -0.13733 | -59.2621 | 63.8489 | -59.079 | -59.1339 | -59.0332 | -0.064087 | -59.3124 | 63.8489 | 63.8123 | -59.166 | -59.2529 | -0.022888 | -0.07782 | 0.050354 | 122.8546 | -0.20599 | -0.12817 | -0.068665 | -0.10986 | -0.19684 | 0.050354 | 0.022888 | -0.25635 | -0.059509 | 0.013733 | 122.905 | 122.7859 | 58.9188 | -122.9324 | 122.905 | 122.8683 | 58.992 | -123.0515
539.0156 | 123.1155 | -59.0057 | 63.7848 | 0.17532 | 0.0083035 | 0.06825 | 0.069663 | 0.12886 | -0.0026405 | -0.0013095 | 0.31265 | -0.0035718 | 0.062342 | 0.056971 | -6.4178e-05 | -0.0053512 | 63.8168 | 63.8901 | -0.045776 | -59.2072 | 63.8123 | -59.0744 | -59.1202 | -58.9828 | 0.045776 | -59.1934 | 63.8214 | 63.7619 | -59.1476 | -59.2117 | -0.068665 | -0.11444 | 0.027466 | 122.8958 | -0.20142 | -0.086975 | 0.032043 | -0.14191 | -0.20599 | 0.036621 | 0.022888 | -0.18768 | 0.018311 | -0.022888 | 122.818 | 122.8226 | 58.96 | -122.905 | 122.8271 | 122.7676 | 59.0515 | -122.9965
540.0156 | 123.0103 | -59.0378 | 63.8168 | -0.03067 | 0.0093717 | 0.067823 | 0.069449 | 0.13057 | 0.0014185 | -0.0030185 | 0.17532 | -0.0042126 | 0.065332 | 0.062098 | 0.0020722 | -0.005565 | 63.7253 | 63.7848 | -0.14191 | -59.2667 | 63.8809 | -59.0973 | -59.1705 | -59.024 | -0.082397 | -59.3491 | 63.8718 | 63.826 | -59.166 | -59.23 | -0.059509 | -0.13275 | 0.064087 | 122.8226 | -0.22888 | -0.096131 | -0.091552 | -0.12817 | -0.19226 | 0.054932 | 0.013733 | -0.31128 | -0.11902 | 0.009156 | 122.9187 | 122.7631 | 58.8959 | -122.9874 | 122.9095 | 122.8638 | 58.9554 | -123.0469
541.0156 | 123.1338 | -58.992 | 63.7894 | 0.19821 | 0.0087307 | 0.066755 | 0.066885 | 0.13142 | -7.6852e-05 | -0.0028049 | 0.32028 | -0.0059216 | 0.062342 | 0.059748 | 0.0033538 | -0.0025742 | 63.8168 | 63.8992 | -0.050354 | -59.2026 | 63.7939 | -59.0744 | -59.1476 | -59.0973 | -0.032043 | -59.1156 | 63.7985 | 63.7665 | -59.1156 | -59.2209 | -0.082398 | -0.15564 | 0.004577 | 122.8912 | -0.21057 | -0.054932 | 0.027465 | -0.1236 | -0.22888 | 0.009155 | -0.10529 | -0.1236 | 0.10529 | -0.022889 | 122.7859 | 122.8088 | 58.9417 | -122.937 | 122.7905 | 122.7585 | 58.96 | -123.0103
542.0156 | 123.0881 | -59.024 | 63.7756 | 0.16769 | 0.010013 | 0.066541 | 0.069235 | 0.12864 | -0.00071785 | -0.0036595 | 0.2211 | -0.0027174 | 0.063623 | 0.059748 | 0.0042084 | -0.003215 | 63.7573 | 63.8123 | -0.11902 | -59.2484 | 63.858 | -59.0607 | -59.1385 | -58.9874 | -0.027466 | -59.2896 | 63.8351 | 63.7802 | -59.1568 | -59.2484 | -0.036621 | -0.11444 | 0.082397 | 122.8363 | -0.2243 | -0.10986 | -0.018311 | -0.13275 | -0.2243 | 0.059509 | 0.036621 | -0.2655 | -0.041199 | 0.004577 | 122.8821 | 122.7814 | 58.905 | -122.9141 | 122.8592 | 122.8043 | 58.9966 | -123.024
543.0156 | 123.0927 | -59.0057 | 63.739 | 0.3508 | 0.0087307 | 0.06761 | 0.069235 | 0.13035 | -0.0013587 | -0.0034457 | 0.29739 | -0.0050672 | 0.065332 | 0.060603 | 0.0012176 | -0.0040696 | 63.8351 | 63.9038 | -0.036621 | -59.1797 | 63.8077 | -59.0515 | -59.1202 | -58.9554 | 0.013733 | -59.2575 | 63.8031 | 63.7207 | -59.1751 | -59.2758 | -0.045777 | -0.11444 | 0.068664 | 122.9095 | -0.17395 | -0.059509 | 0.09613 | -0.16937 | -0.27008 | 0.064087 | 0.050354 | -0.25177 | 0.018311 | -0.018311 | 122.8134 | 122.8409 | 58.9691 | -122.8592 | 122.8088 | 122.7264 | 59.0195 | -123.0148
544.0156 | 123.0331 | -59.024 | 63.7985 | 0.4805 | 0.010867 | 0.068037 | 0.073508 | 0.12907 | 0.00056395 | 0.00039954 | 0.16006 | -0.002931 | 0.062982 | 0.061885 | 0.0018584 | -0.005565 | 63.7527 | 63.7756 | -0.14648 | -59.2712 | 63.8763 | -59.0973 | -59.1797 | -59.0332 | -0.07782 | -59.3445 | 63.858 | 63.8123 | -59.166 | -59.2575 | -0.073242 | -0.15564 | 0.07782 | 122.7997 | -0.24719 | -0.091553 | -0.045776 | -0.14191 | -0.23346 | 0.059509 | -0.009155 | -0.32043 | -0.086975 | 0.013733 | 122.9004 | 122.7768 | 58.8776 | -122.9782 | 122.8821 | 122.8363 | 58.9462 | -123.056
545.0156 | 123.1018 | -59.0286 | 63.7573 | 0.0074768 | 0.0048855 | 0.065901 | 0.067313 | 0.13099 | -0.0041357 | -0.0021641 | 0.25925 | -0.0059216 | 0.064264 | 0.063807 | 0.0029266 | -0.0036424 | 63.8123 | 63.9313 | -0.022888 | -59.2026 | 63.8031 | -59.0561 | -59.111 | -58.9462 | 0.036621 | -59.2255 | 63.8123 | 63.7665 | -59.1431 | -59.2209 | -0.027466 | -0.082398 | 0.045777 | 122.9599 | -0.17395 | -0.091553 | 0.054932 | -0.11444 | -0.19226 | 0.054932 | 0.082397 | -0.19684 | -0.004578 | 0.009155 | 122.8317 | 122.8409 | 59.0057 | -122.8683 | 122.8409 | 122.7951 | 59.0652 | -122.9782
546.0156 | 123.0881 | -59.0378 | 63.7985 | 0.16769 | 0.0097989 | 0.068891 | 0.070517 | 0.1295 | 0.0016321 | -0.0030185 | 0.25162 | -0.0061352 | 0.063837 | 0.061885 | 0.001004 | -0.0034286 | 63.7619 | 63.8123 | -0.1236 | -59.2621 | 63.8763 | -59.0927 | -59.1797 | -58.992 | -0.032043 | -59.2987 | 63.8306 | 63.7848 | -59.1614 | -59.2346 | -0.054931 | -0.14191 | 0.07782 | 122.85 | -0.2243 | -0.082398 | -0.036621 | -0.1236 | -0.19684 | 0.032043 | 0.045777 | -0.26093 | -0.064087 | -0.013733 | 122.9141 | 122.7997 | 58.9142 | -122.9782 | 122.8683 | 122.8226 | 59.0057 | -123.0331
547.0156 | 123.1155 | -59.0149 | 63.8123 | 0.030365 | 0.0068081 | 0.06526 | 0.068594 | 0.12886 | -0.0011451 | -0.0038731 | 0.27451 | -0.0048536 | 0.062982 | 0.062953 | 0.0020722 | -0.0019334 | 63.8168 | 63.9175 | -0.036621 | -59.198 | 63.7985 | -59.079 | -59.1248 | -58.9371 | 0.041199 | -59.23 | 63.8031 | 63.7665 | -59.1385 | -59.2346 | -0.064086 | -0.10986 | -0.013733 | 122.9324 | -0.1831 | -0.073242 | 0.004577 | -0.1236 | -0.21973 | -0.009155 | 0.07782 | -0.21515 | 0.004577 | -0.045777 | 122.8134 | 122.8317 | 58.9783 | -122.937 | 122.818 | 122.7814 | 59.0561 | -123.0469
548.0156 | 123.0515 | -59.0378 | 63.7985 | 0.24399 | 0.011722 | 0.068464 | 0.069235 | 0.13292 | 0.0018457 | -0.0021641 | 0.19058 | -0.003999 | 0.065546 | 0.061885 | 0.0039948 | -0.0051376 | 63.7573 | 63.8123 | -0.12817 | -59.2484 | 63.8489 | -59.1019 | -59.1248 | -58.992 | -0.045776 | -59.2804 | 63.8443 | 63.7756 | -59.1385 | -59.2484 | -0.064087 | -0.086975 | 0.050354 | 122.85 | -0.21057 | -0.1236 | -0.041199 | -0.10071 | -0.21057 | 0.045776 | 0.045777 | -0.24262 | -0.032044 | -0.022888 | 122.8867 | 122.7951 | 58.9096 | -122.9233 | 122.8821 | 122.8134 | 58.992 | -123.0469
549.0156 | 123.0972 | -59.024 | 63.7756 | -0.00015269 | 0.0085171 | 0.066114 | 0.067313 | 0.13057 | -0.0019995 | -0.0030185 | 0.28214 | -0.0044264 | 0.065119 | 0.060603 | 0.0014312 | -0.0064194 | 63.8123 | 63.9221 | -0.027466 | -59.2117 | 63.826 | -59.0652 | -59.1064 | -58.9417 | 0.027466 | -59.2255 | 63.8077 | 63.7756 | -59.1476 | -59.2438 | -0.041199 | -0.082397 | 0.050354 | 122.9462 | -0.18768 | -0.10529 | 0.036621 | -0.1236 | -0.21973 | 0.032043 | 0.082398 | -0.20142 | 0.01831 | 0 | 122.85 | 122.8363 | 58.9966 | -122.8821 | 122.8317 | 122.7997 | 59.0515 | -123.0194
550.0156 | 123.0011 | -59.079 | 63.8077 | -2.9298 | 0.0087307 | 0.063551 | 0.069876 | 0.13035 | 0.0016321 | -0.0015231 | 0.23636 | -0.0042126 | 0.062342 | 0.061244 | 0.0050628 | -0.005565 | 63.6978 | 63.8214 | -0.11902 | -59.2712 | 63.8947 | -59.079 | -59.1476 | -59.0424 | -0.07782 | -59.3353 | 63.858 | 63.7985 | -59.2026 | -59.2438 | 0 | -0.068665 | 0.086975 | 122.9004 | -0.19226 | -0.1236 | -0.10986 | -0.1236 | -0.1648 | 0.050354 | 0.036621 | -0.25635 | -0.091553 | -0.009155 | 122.9736 | 122.7768 | 58.96 | -122.9553 | 122.937 | 122.8775 | 59.0012 | -123.0515
551.0156 | 122.9736 | -59.0195 | 63.8672 | -0.25955 | 0.0072355 | 0.067396 | 0.071585 | 0.13121 | -0.0030677 | -0.0030185 | -0.17563 | -0.005708 | 0.061914 | 0.059535 | 0.0035674 | -0.0064194 | 63.7802 | 63.8763 | -0.009155 | -59.2026 | 63.8901 | -59.0195 | -59.079 | -59.0149 | 0.068665 | -59.2896 | 63.9267 | 63.8535 | -59.1476 | -59.23 | 0 | -0.059509 | 0.022889 | 122.8958 | -0.18311 | -0.1236 | -0.086975 | -0.12817 | -0.21057 | 0.05951 | 0.004577 | -0.27008 | -0.059509 | -0.013732 | 122.9095 | 122.7997 | 59.0103 | -122.9462 | 122.9462 | 122.8729 | 59.0881 | -123.0972
552.0156 | 123.1018 | -59.0286 | 63.7802 | 0.35843 | 0.0076627 | 0.06526 | 0.068167 | 0.13078 | -0.00093145 | -0.0010959 | 0.21347 | -0.0042126 | 0.063623 | 0.059107 | 0.0031402 | -0.0040696 | 63.8077 | 63.9084 | -0.041199 | -59.1934 | 63.8214 | -59.0652 | -59.111 | -58.9554 | 0.032043 | -59.3308 | 63.8077 | 63.707 | -59.2072 | -59.2438 | -0.036622 | -0.082398 | 0.041199 | 122.937 | -0.1648 | -0.082397 | 0.027466 | -0.17853 | -0.21515 | 0.027466 | 0.073242 | -0.30213 | -0.086976 | -0.073242 | 122.85 | 122.8363 | 58.9874 | -122.8912 | 122.8363 | 122.7356 | 59.0607 | -123.024
553.0156 | 123.0789 | -59.0195 | 63.7894 | 0.11429 | 0.0042447 | 0.067823 | 0.067954 | 0.12886 | -0.0026405 | -0.0030185 | 0.29739 | -0.0048536 | 0.061914 | 0.060603 | 0.0031402 | -0.0047104 | 63.7894 | 63.8901 | -0.045776 | -59.2209 | 63.8077 | -59.0607 | -59.1293 | -58.9874 | 0 | -59.2621 | 63.8214 | 63.7711 | -59.1248 | -59.2209 | -0.041199 | -0.10986 | 0.01831 | 122.9095 | -0.20142 | -0.091553 | 0 | -0.10529 | -0.20142 | 0.032043 | 0.032043 | -0.24262 | -0.041199 | -0.018311 | 122.8271 | 122.8088 | 58.9737 | -122.9187 | 122.8409 | 122.7905 | 59.0195 | -123.0103
554.0156 | 123.1201 | -59.0195 | 63.7985 | 0.36606 | 0.0095853 | 0.062055 | 0.070731 | 0.13228 | -0.00050425 | -0.00088226 | 0.19058 | -0.002931 | 0.062128 | 0.060176 | 0.0035674 | -0.0053512 | 63.8214 | 63.9175 | -0.027466 | -59.2163 | 63.8123 | -59.0515 | -59.1202 | -58.9462 | 0.027466 | -59.2255 | 63.8214 | 63.7527 | -59.1888 | -59.2804 | -0.032044 | -0.10071 | 0.013733 | 122.937 | -0.19684 | -0.096131 | 0.022888 | -0.16937 | -0.26093 | 0.022888 | 0.073242 | -0.20599 | 0.054932 | -0.045776 | 122.8317 | 122.8409 | 58.992 | -122.9187 | 122.8409 | 122.7722 | 59.0469 | -123.0789
555.0156 | 123.1018 | -59.024 | 63.7848 | 0.12955 | 0.0053129 | 0.06761 | 0.06774 | 0.128 | -0.0034949 | -0.0038731 | 0.23636 | -0.0059216 | 0.061701 | 0.064234 | 0.0022858 | -0.0030014 | 63.8077 | 63.913 | -0.027466 | -59.2392 | 63.8077 | -59.0652 | -59.1248 | -58.9645 | -0.009155 | -59.2438 | 63.8077 | 63.7939 | -59.1293 | -59.2209 | -0.041199 | -0.10071 | 0.022888 | 122.937 | -0.21515 | -0.11444 | 0.022888 | -0.10529 | -0.19684 | 0.022888 | 0.059509 | -0.21973 | -0.022888 | 0.009155 | 122.8317 | 122.8317 | 58.9966 | -122.9095 | 122.8317 | 122.818 | 59.0149 | -123.0057
556.0156 | 122.9919 | -59.0286 | 63.8626 | -0.24429 | 0.0063809 | 0.065687 | 0.070303 | 0.13142 | -0.00029045 | -0.0062229 | -0.03067 | -0.005708 | 0.0664 | 0.059535 | 0.0022858 | -0.0053512 | 63.7894 | 63.8855 | -0.013733 | -59.2255 | 63.9038 | -59.0515 | -59.1064 | -59.0149 | 0.064087 | -59.2896 | 63.8855 | 63.826 | -59.1568 | -59.2163 | -0.022889 | -0.07782 | 0.041199 | 122.9141 | -0.19684 | -0.11902 | -0.073242 | -0.12817 | -0.18768 | 0.022888 | 0.013732 | -0.26093 | -0.073242 | -0.036621 | 122.9324 | 122.818 | 59.0149 | -122.9691 | 122.9141 | 122.8546 | 59.0927 | -123.0789
557.0625 | 122.9965 | -59.0332 | 63.826 | -0.4808 | 0.0042447 | 0.06761 | 0.065817 | 0.13099 | 0.00077755 | -0.0019505 | 0.17532 | -0.0052808 | 0.064691 | 0.06103 | 0.0050628 | -0.0057786 | 63.7527 | 63.8031 | -0.12817 | -59.2621 | 63.8809 | -59.0973 | -59.1293 | -59.0378 | -0.07782 | -59.3582 | 63.8855 | 63.7848 | -59.1934 | -59.2712 | -0.064087 | -0.09613 | 0.054931 | 122.8363 | -0.22888 | -0.13275 | -0.073242 | -0.16022 | -0.23804 | 0.059509 | -0.004578 | -0.32501 | -0.086975 | -0.041199 | 122.9141 | 122.7859 | 58.905 | -122.9553 | 122.9187 | 122.818 | 58.9554 | -123.0972
558.0156 | 123.0469 | -59.0561 | 63.7939 | 0.19058 | 0.01044 | 0.063764 | 0.068381 | 0.13121 | 0.0027001 | -0.0019505 | 0.19821 | -0.0059216 | 0.061701 | 0.059321 | 0.0022858 | -0.005565 | 63.7482 | 63.8214 | -0.11902 | -59.2484 | 63.8672 | -59.0927 | -59.1339 | -58.9828 | -0.045776 | -59.2621 | 63.8351 | 63.7848 | -59.1476 | -59.2438 | -0.036621 | -0.07782 | 0.073242 | 122.8775 | -0.19226 | -0.11444 | -0.045776 | -0.091553 | -0.18768 | 0.041199 | 0.073242 | -0.20599 | -0.018311 | -0.009155 | 122.9233 | 122.8043 | 58.9371 | -122.9279 | 122.8912 | 122.8409 | 59.0103 | -123.0377
559.0156 | 123.0423 | -59.0195 | 63.8031 | 0.045624 | 0.0023221 | 0.069746 | 0.068167 | 0.12907 | -0.0028541 | -0.0032321 | 0.19058 | -0.0067762 | 0.059778 | 0.060389 | 0.0012176 | -0.003856 | 63.7482 | 63.8992 | -0.036621 | -59.2117 | 63.8489 | -59.0561 | -59.111 | -58.9737 | 0.24719 | -59.166 | 63.8718 | 63.8077 | -59.1248 | -59.2346 | -0.036621 | -0.091553 | 0.045776 | 122.9187 | -0.19226 | -0.10071 | -0.054932 | -0.10529 | -0.21515 | 0.068664 | 0.045776 | -0.14648 | 0.068664 | 0.004577 | 122.8683 | 122.7676 | 58.9828 | -122.9141 | 122.8912 | 122.8271 | 59.2667 | -123.0377
560.0156 | 123.1155 | -58.9874 | 63.7756 | 0.083771 | 0.0078763 | 0.067823 | 0.069449 | 0.13035 | -0.0024269 | -0.0043003 | 0.21347 | -0.003999 | 0.063196 | 0.060176 | 0.0024994 | -0.0064194 | 63.8351 | 63.945 | -0.022888 | -59.2072 | 63.8168 | -59.0424 | -59.1339 | -58.9371 | 0.022888 | -59.2346 | 63.8031 | 63.7299 | -59.1385 | -59.2529 | -0.054931 | -0.14648 | 0.041198 | 122.9324 | -0.21973 | -0.073242 | 0.059509 | -0.15106 | -0.2655 | 0.027466 | 0.050354 | -0.24719 | 0.018311 | -0.045777 | 122.8043 | 122.8226 | 58.9645 | -122.9095 | 122.7905 | 122.7173 | 59.0103 | -123.0286
561.0312 | 123.0194 | -59.024 | 63.8123 | -0.053558 | 0.011722 | 0.064192 | 0.069663 | 0.12971 | 0.0020593 | -0.0019505 | -0.045929 | -0.003999 | 0.065119 | 0.063807 | 0.0050628 | -0.0070602 | 63.826 | 63.9084 | -0.018311 | -59.2163 | 63.9038 | -59.0607 | -59.1431 | -58.9783 | 0.032043 | -59.285 | 63.858 | 63.7848 | -59.1522 | -59.2163 | -0.036621 | -0.11902 | 0.091553 | 122.9324 | -0.19226 | -0.073243 | 0.013733 | -0.12817 | -0.19226 | 0.045776 | 0.045777 | -0.26093 | -0.068664 | -0.027466 | 122.9279 | 122.85 | 59.0057 | -122.9553 | 122.8821 | 122.8088 | 59.0561 | -123.0286
562.0156 | 123.0881 | -58.9966 | 63.7848 | 1.7241 | 0.0095853 | 0.067182 | 0.069235 | 0.13163 | -0.0022131 | -0.0021641 | 0.21347 | -0.0065626 | 0.061487 | 0.060603 | 0.0012176 | -0.003856 | 63.8214 | 63.9313 | -0.022888 | -59.1888 | 63.8306 | -59.0515 | -59.1019 | -58.9462 | 0.041199 | -59.2255 | 63.8123 | 63.7207 | -59.1568 | -59.2117 | -0.054932 | -0.10529 | 0.045776 | 122.9279 | -0.19226 | -0.086975 | 0.036621 | -0.16022 | -0.21515 | 0.027466 | 0.050354 | -0.22888 | -0.013733 | -0.064087 | 122.8271 | 122.818 | 58.9737 | -122.8867 | 122.8088 | 122.7173 | 59.0378 | -122.9965
563.0156 | 123.1064 | -59.0057 | 63.8077 | 0.16769 | 0.0053129 | 0.068891 | 0.06774 | 0.1295 | -0.0043495 | -0.0032321 | 0.13718 | -0.0067762 | 0.063837 | 0.060816 | 0.0022858 | -0.0030014 | 63.7711 | 63.8901 | -0.059509 | -59.2255 | 63.8489 | -59.0561 | -59.1293 | -58.9783 | 0.022888 | -59.2484 | 63.8168 | 63.7711 | -59.1248 | -59.2255 | -0.050354 | -0.1236 | 0.041199 | 122.8958 | -0.21973 | -0.096131 | -0.036621 | -0.11902 | -0.21973 | 0.009155 | 0.027466 | -0.24261 | -0.022888 | -0.036621 | 122.8546 | 122.7768 | 58.9462 | -122.937 | 122.8226 | 122.7768 | 59.0286 | -123.0331
564.0156 | 123.143 | -59.0057 | 63.7619 | 0.20584 | 0.0080899 | 0.065473 | 0.069449 | 0.13121 | 0.0014185 | -0.0034457 | 0.23636 | -0.0033582 | 0.065546 | 0.062525 | 0.0052764 | -0.0074876 | 63.7802 | 63.8763 | -0.086975 | -59.2072 | 63.8535 | -59.0698 | -59.1248 | -58.9371 | 0.013733 | -59.2392 | 63.8306 | 63.7482 | -59.166 | -59.2392 | -0.064087 | -0.11902 | 0.091553 | 122.8821 | -0.20142 | -0.082397 | 0.01831 | -0.16022 | -0.23346 | 0.068664 | 0.068664 | -0.23346 | 0 | -0.013733 | 122.8592 | 122.7859 | 58.9188 | -122.8867 | 122.8363 | 122.7539 | 59.0195 | -123.0011
565.0156 | 123.1155 | -59.024 | 63.7482 | 0.14481 | 0.0044583 | 0.065901 | 0.068381 | 0.13163 | -0.0011451 | -0.0013095 | 0.25925 | -0.0050672 | 0.063196 | 0.059962 | 0.0022858 | -0.003215 | 63.8077 | 63.9359 | -0.032043 | -59.2209 | 63.8123 | -59.0744 | -59.1431 | -58.9462 | 0.032043 | -59.2346 | 63.8168 | 63.7161 | -59.1385 | -59.2575 | -0.050354 | -0.11902 | 0.064087 | 122.9599 | -0.19684 | -0.07782 | 0.059509 | -0.11444 | -0.23346 | 0.068664 | 0.07782 | -0.21057 | 0.022888 | -0.032044 | 122.8363 | 122.8317 | 58.992 | -122.8912 | 122.8409 | 122.7402 | 59.0561 | -123.0057
566.0156 | 123.1018 | -58.9874 | 63.8168 | -0.88516 | 0.0065945 | 0.066328 | 0.067313 | 0.13163 | -0.0032813 | -0.0030185 | -0.084076 | -0.00464 | 0.06106 | 0.058467 | 0.0020722 | -0.005565 | 63.8351 | 64.0137 | 0.07782 | -59.1614 | 63.8626 | -59.0424 | -59.0881 | -58.9188 | 0.16937 | -59.1797 | 63.8397 | 63.7802 | -59.1202 | -59.198 | -0.054931 | -0.10071 | 0.045777 | 123.0011 | -0.17395 | -0.073242 | 0.018311 | -0.13275 | -0.21057 | 0.022889 | 0.068665 | -0.19226 | 0.018311 | -0.036621 | 122.85 | 122.8226 | 59.0652 | -122.905 | 122.8271 | 122.7676 | 59.1568 | -123.0148
567.0156 | 123.1018 | -59.0286 | 63.7985 | -0.00015269 | 0.0018949 | 0.066114 | 0.066245 | 0.13078 | -0.0079811 | -0.0034457 | 0.10666 | -0.0061352 | 0.061701 | 0.060603 | 0.0024994 | -0.005565 | 63.8947 | 63.7985 | -0.07782 | -59.2026 | 63.858 | -59.0286 | -59.1248 | -58.9645 | 0.041199 | -59.2392 | 63.8306 | 63.7482 | -59.1522 | -59.2575 | 0 | -0.096131 | 0.059509 | 122.8271 | -0.17395 | -0.07782 | 0.09613 | -0.1236 | -0.22888 | 0.032043 | 0.064086 | -0.21057 | 0.01831 | -0.050354 | 122.8867 | 122.9233 | 58.9508 | -122.9233 | 122.8592 | 122.7768 | 59.0698 | -123.056
568.0156 | 123.111 | -59.024 | 63.7665 | 0.14481 | 0.0087307 | 0.06825 | 0.072012 | 0.13078 | -0.0017859 | -0.0023777 | 0.19821 | -0.0042126 | 0.063623 | 0.059962 | 0.0035674 | -0.0047104 | 63.8168 | 63.9404 | -0.018311 | -59.2072 | 63.8306 | -59.0652 | -59.1385 | -58.9233 | 0.022888 | -59.2392 | 63.826 | 63.739 | -59.1431 | -59.2712 | -0.041199 | -0.11444 | 0.064087 | 122.9645 | -0.1831 | -0.068664 | 0.050354 | -0.11902 | -0.24719 | 0.05951 | 0.10071 | -0.21515 | 0.032043 | -0.027465 | 122.8546 | 122.8409 | 59.0057 | -122.905 | 122.85 | 122.7631 | 59.0469 | -123.0377
569.0156 | 123.0789 | -59.0057 | 63.7756 | 0.0914 | 0.0038175 | 0.067182 | 0.07009 | 0.12886 | -0.0022131 | -0.0030185 | 1.2587 | -0.0065626 | 0.060846 | 0.061244 | 0.0024994 | -0.0064194 | 63.7848 | 63.8992 | -0.041199 | -59.2255 | 63.8489 | -59.0469 | -59.1293 | -58.96 | 0.036621 | -59.2575 | 63.8351 | 63.7573 | -59.1293 | -59.2209 | -0.041199 | -0.1236 | 0.073242 | 122.905 | -0.21973 | -0.096131 | 0.009155 | -0.1236 | -0.21515 | 0.059509 | 0.045776 | -0.25177 | -0.036621 | -0.018311 | 122.8546 | 122.7905 | 58.9645 | -122.905 | 122.8409 | 122.7631 | 59.0424 | -122.9965
570.0156 | 123.1293 | -59.024 | 63.7711 | 0.27451 | 0.0076627 | 0.068037 | 0.070517 | 0.13206 | 0.0018457 | -0.0040867 | 0.19058 | -0.0072034 | 0.062982 | 0.060816 | 0.0035674 | -0.0062058 | 63.8351 | 63.9359 | -0.013733 | -59.198 | 63.8443 | -59.0744 | -59.1202 | -58.9279 | 0.027466 | -59.2163 | 63.8214 | 63.7299 | -59.1385 | -59.2484 | -0.050354 | -0.09613 | 0.073242 | 122.9599 | -0.17395 | -0.07782 | 0.064087 | -0.11444 | -0.2243 | 0.050354 | 0.096131 | -0.19226 | 0.032043 | -0.041199 | 122.8683 | 122.8592 | 59.0103 | -122.8912 | 122.8455 | 122.7539 | 59.0515 | -123.0194
571.0156 | 123.0148 | -59.0332 | 63.8809 | -1.7778 | 0.0031765 | 0.066328 | 0.068381 | 0.12928 | 0.0029137 | -0.00088226 | -0.17563 | -0.0033582 | 0.060205 | 0.061671 | 0.0037812 | -0.0059922 | 63.7482 | 63.8718 | -0.027466 | -59.2438 | 63.8992 | -59.0836 | -59.1522 | -59.0103 | 0.054932 | -59.2941 | 63.9038 | 63.8077 | -59.1339 | -59.2209 | -0.050354 | -0.11902 | 0.018311 | 122.905 | -0.21057 | -0.091552 | -0.13275 | -0.10071 | -0.18768 | 0.022889 | 0.022888 | -0.26093 | -0.073242 | -0.073242 | 122.9324 | 122.7814 | 59.0057 | -123.0331 | 122.937 | 122.8409 | 59.0881 | -123.1018
572.0156 | 123.0927 | -59.0149 | 63.7848 | 0.099029 | 0.0059537 | 0.066541 | 0.069022 | 0.13014 | 0.00035035 | -0.0030185 | 0.2211 | -0.0059216 | 0.064051 | 0.062098 | 0.0037812 | -0.005565 | 63.8168 | 63.9496 | -0.022888 | -59.198 | 63.826 | -59.079 | -59.111 | -58.9371 | 0.027466 | -59.2209 | 63.8077 | 63.7436 | -59.1797 | -59.2346 | -0.064086 | -0.09613 | 0.041199 | 122.9645 | -0.1831 | -0.086975 | 0.032043 | -0.16479 | -0.21973 | 0.022888 | 0.07782 | -0.20599 | 0.013733 | -0.041199 | 122.8409 | 122.8317 | 58.992 | -122.8958 | 122.8226 | 122.7585 | 59.0424 | -123.0194
573.0156 | 123.0927 | -58.9874 | 63.7939 | -0.00015269 | 0.0044583 | 0.067182 | 0.067099 | 0.12651 | -0.0045631 | -0.0049411 | 0.068512 | -0.006349 | 0.062128 | 0.062098 | 0.00036322 | -0.0057786 | 63.7894 | 63.9084 | -0.013733 | -59.2117 | 63.858 | -59.0515 | -59.1202 | -58.9325 | 0.082397 | -59.198 | 63.8535 | 63.7802 | -59.1248 | -59.2255 | -0.064087 | -0.13275 | 0.064087 | 122.8958 | -0.2243 | -0.091553 | -0.004577 | -0.13733 | -0.23804 | 0.05951 | 0.054932 | -0.21057 | 0.027466 | -0.013733 | 122.8455 | 122.7768 | 58.9737 | -122.9141 | 122.8409 | 122.7676 | 59.0698 | -123.0194
574.0156 | 123.0789 | -58.9874 | 63.7985 | 0.022736 | 0.0057401 | 0.067823 | 0.068808 | 0.12886 | -0.0043495 | -0.0034457 | 0.10666 | -0.0052808 | 0.062982 | 0.058253 | 0.0029266 | -0.0053512 | 63.7756 | 63.8855 | -0.054932 | -59.2209 | 63.8763 | -59.0424 | -59.1339 | -58.9737 | -0.018311 | -59.2209 | 63.8489 | 63.7436 | -59.1385 | -59.2117 | -0.054931 | -0.14648 | 0.07782 | 122.8729 | -0.23346 | -0.086975 | -0.022888 | -0.15106 | -0.2243 | 0.050354 | 0.013733 | -0.23346 | -0.009155 | -0.054932 | 122.8638 | 122.7631 | 58.9325 | -122.9324 | 122.8363 | 122.731 | 58.9691 | -123.0103
575.0156 | 123.111 | -58.992 | 63.8077 | 0.037994 | 0.0018949 | 0.065473 | 0.069235 | 0.1295 | -0.0028541 | -0.0057957 | 0.0074766 | -0.0048536 | 0.059992 | 0.060389 | 0.0035674 | -0.003856 | 63.7848 | 63.9175 | -0.018311 | -59.1934 | 63.8626 | -59.0561 | -59.1064 | -58.9325 | 0.082397 | -59.198 | 63.8443 | 63.739 | -59.1339 | -59.2026 | -0.064087 | -0.11444 | 0.054932 | 122.9095 | -0.20142 | -0.086975 | -0.022888 | -0.14191 | -0.21057 | 0.036621 | 0.059509 | -0.20599 | 0.004578 | -0.068664 | 122.8546 | 122.7768 | 58.9737 | -122.9141 | 122.8363 | 122.731 | 59.0744 | -123.0103
576.0156 | 123.0515 | -59.0195 | 63.7848 | 0.060882 | 0.0036039 | 0.0706 | 0.068167 | 0.12971 | -0.0039221 | -0.0049411 | 0.13718 | -0.007417 | 0.059778 | 0.055476 | 0.0042084 | -0.003856 | 63.7848 | 63.9084 | -0.041199 | -59.2026 | 63.8443 | -59.0652 | -59.1202 | -59.0515 | 0.050354 | -59.2438 | 63.8489 | 63.7619 | -59.1431 | -59.2209 | -0.045777 | -0.10071 | 0.059509 | 122.9279 | -0.18311 | -0.082398 | 0 | -0.1236 | -0.20142 | 0.064087 | -0.032044 | -0.2243 | -0.022888 | -0.022888 | 122.8638 | 122.8043 | 58.9783 | -122.905 | 122.8683 | 122.7814 | 59.0698 | -123.0057
577.0156 | 123.1338 | -59.0195 | 63.826 | -0.0077822 | 0.0018949 | 0.069746 | 0.068808 | 0.13185 | -0.0011451 | -0.0023777 | 0.083771 | -0.0072034 | 0.060633 | 0.06103 | 0.0024994 | -0.0057786 | 63.7848 | 63.9175 | -0.013733 | -59.1934 | 63.8443 | -59.0652 | -59.1248 | -58.9462 | 0.086975 | -59.2072 | 63.826 | 63.7436 | -59.1431 | -59.2209 | -0.045777 | -0.10529 | 0.01831 | 122.937 | -0.17395 | -0.068664 | -0.041199 | -0.1236 | -0.20142 | 0 | 0.073242 | -0.18768 | 0.013733 | -0.082398 | 122.8638 | 122.8043 | 59.0057 | -122.9507 | 122.8455 | 122.7631 | 59.1064 | -123.0469
578.0156 | 123.0789 | -59.0149 | 63.7939 | 0.16769 | 0.0055265 | 0.066328 | 0.067526 | 0.13078 | -0.00029045 | -0.0028049 | 0.2211 | -0.00464 | 0.061701 | 0.061457 | 0.0014312 | -0.0044968 | 63.7985 | 63.9359 | -0.054932 | -59.2163 | 63.8214 | -59.0607 | -59.111 | -58.9371 | 0.022888 | -59.2529 | 63.8168 | 63.7299 | -59.1476 | -59.2255 | -0.045776 | -0.09613 | 0.027466 | 122.9507 | -0.20142 | -0.10529 | 0.004578 | -0.13275 | -0.21057 | 0.022888 | 0.07782 | -0.23804 | -0.027466 | -0.064087 | 122.8363 | 122.8134 | 58.96 | -122.905 | 122.8317 | 122.7448 | 59.0378 | -123.0194
579.0156 | 123.111 | -59.024 | 63.826 | -0.0077822 | 0.0038175 | 0.069319 | 0.069876 | 0.1295 | -0.00093145 | -0.0053683 | 0.030365 | -0.007417 | 0.060419 | 0.061671 | 0.0024994 | -0.0044968 | 63.7985 | 63.913 | -0.013733 | -59.198 | 63.8672 | -59.0744 | -59.1019 | -58.9371 | 0.091553 | -59.198 | 63.8443 | 63.739 | -59.1339 | -59.2255 | -0.050354 | -0.07782 | 0.041198 | 122.937 | -0.17395 | -0.09613 | -0.027466 | -0.10986 | -0.20142 | 0.01831 | 0.086975 | -0.17395 | 0.027466 | -0.086975 | 122.8912 | 122.8226 | 59.0103 | -122.9279 | 122.8683 | 122.7631 | 59.1156 | -123.0515
580.0156 | 123.0835 | -59.0057 | 63.7665 | 0.0914 | 0.0016813 | 0.066541 | 0.069235 | 0.12928 | -0.0019995 | -0.0028049 | 0.083771 | -0.0050672 | 0.063837 | 0.057398 | 0.0024994 | -0.0053512 | 63.7711 | 63.9084 | -0.050354 | -59.2255 | 63.8626 | -59.079 | -59.1019 | -58.9966 | 0.004578 | -59.2392 | 63.8672 | 63.7436 | -59.1476 | -59.2209 | -0.073242 | -0.096131 | 0.096131 | 122.9141 | -0.21973 | -0.1236 | 0.004578 | -0.14191 | -0.21515 | 0.10071 | 0.009155 | -0.23346 | -0.018311 | -0.022888 | 122.8683 | 122.7768 | 58.9554 | -122.8683 | 122.8729 | 122.7493 | 59.0103 | -122.9874
581.0156 | 123.1247 | -58.9691 | 63.8077 | -0.084076 | 0.0029629 | 0.069105 | 0.070303 | 0.13228 | -0.0030677 | -0.0019505 | -0.015411 | -0.0037854 | 0.06106 | 0.059962 | 0.0024994 | -0.0047104 | 63.8443 | 63.9725 | 0.036621 | -59.1843 | 63.8397 | -59.0378 | -59.0836 | -58.8959 | 0.15106 | -59.1614 | 63.8672 | 63.7482 | -59.1248 | -59.2072 | -0.068665 | -0.11444 | 0.032044 | 122.9416 | -0.21515 | -0.10071 | 0.036621 | -0.15564 | -0.23804 | 0.059509 | 0.073242 | -0.19226 | 0.045776 | -0.059509 | 122.8088 | 122.8134 | 59.0057 | -122.8912 | 122.8363 | 122.7173 | 59.1202 | -123.0148
582.0156 | 123.0789 | -59.0195 | 63.8168 | 0.068512 | 0.0031765 | 0.067823 | 0.069449 | 0.12843 | -0.0030677 | -0.0049411 | 0.083771 | -0.0082716 | 0.058496 | 0.060816 | 0.0039948 | -0.0047104 | 63.7711 | 63.913 | -0.045776 | -59.2163 | 63.8626 | -59.0698 | -59.1202 | -58.8684 | -0.027466 | -59.2621 | 63.8489 | 63.7573 | -59.1156 | -59.2346 | -0.050354 | -0.10071 | 0.045777 | 122.9324 | -0.19684 | -0.096131 | -0.045776 | -0.096131 | -0.21515 | 0.032044 | 0.15106 | -0.24262 | -0.027466 | -0.059509 | 122.8821 | 122.7905 | 58.9737 | -122.937 | 122.8683 | 122.7768 | 58.992 | -123.0515
583.0156 | 123.1155 | -58.9737 | 63.8031 | -0.091705 | 0.0048855 | 0.069532 | 0.069663 | 0.13078 | -0.0026405 | -0.0047275 | -0.053558 | -0.0054944 | 0.059992 | 0.060176 | 0.001004 | -0.003215 | 63.8443 | 63.9954 | 0.032043 | -59.1751 | 63.8672 | -59.0469 | -59.0973 | -58.8821 | 0.16937 | -59.1797 | 63.8718 | 63.7482 | -59.0973 | -59.1797 | -0.073242 | -0.1236 | 0.064086 | 122.9691 | -0.20142 | -0.07782 | 0.041198 | -0.1236 | -0.20599 | 0.068664 | 0.091553 | -0.20599 | 0 | -0.054932 | 122.8409 | 122.818 | 59.0057 | -122.9004 | 122.8455 | 122.7219 | 59.1431 | -122.9828
584.0156 | 123.0698 | -59.0103 | 63.7894 | -0.045929 | 0.0021085 | 0.06825 | 0.066672 | 0.12928 | 0.00077755 | -0.0030185 | 0.10666 | -0.0078442 | 0.062982 | 0.059535 | 0.0029266 | -0.0023606 | 63.7894 | 63.9313 | -0.032043 | -59.2026 | 63.8672 | -59.0607 | -59.1248 | -58.8867 | 0.17395 | -59.2804 | 63.8397 | 63.7482 | -59.1339 | -59.2346 | -0.050354 | -0.11444 | 0.077819 | 122.9416 | -0.19226 | -0.07782 | 0 | -0.1236 | -0.2243 | 0.050354 | 0.1236 | -0.27008 | -0.045777 | -0.041199 | 122.8775 | 122.7997 | 58.9783 | -122.9141 | 122.85 | 122.7585 | 59.1843 | -123.024
585.0156 | 123.1018 | -58.9828 | 63.7939 | -0.0077822 | 0.0025357 | 0.071668 | 0.069235 | 0.13014 | -0.0022131 | -0.0030185 | 0.030365 | -0.0061352 | 0.062555 | 0.060389 | 0.0016448 | -0.005565 | 63.7802 | 63.9221 | -0.022888 | -59.2026 | 63.8672 | -59.0652 | -59.1064 | -58.9371 | 0.073242 | -59.2072 | 63.8626 | 63.7161 | -59.1339 | -59.23 | -0.082398 | -0.1236 | 0.073242 | 122.905 | -0.21973 | -0.096131 | -0.013733 | -0.15106 | -0.24719 | 0.068665 | 0.045776 | -0.2243 | 0.022889 | -0.07782 | 122.85 | 122.7631 | 58.96 | -122.9004 | 122.8455 | 122.699 | 59.0561 | -123.024
586.0156 | 123.0743 | -59.0103 | 63.826 | 0.099029 | 0.0036039 | 0.067182 | 0.069235 | 0.13057 | 0.00056395 | -0.0045139 | 0.12192 | -0.0072034 | 0.058069 | 0.059748 | 0.0031402 | -0.004924 | 63.7894 | 63.9038 | -0.036621 | -59.2209 | 63.8626 | -59.0698 | -59.1431 | -58.9737 | -0.027466 | -59.0836 | 63.8535 | 63.7436 | -59.1248 | -59.2209 | -0.059509 | -0.13275 | 0.036621 | 122.9141 | -0.21057 | -0.07782 | -0.036621 | -0.11444 | -0.21057 | 0.027466 | 0.036621 | -0.073242 | 0.13733 | -0.082398 | 122.8729 | 122.7997 | 58.9737 | -122.9691 | 122.8638 | 122.7539 | 58.9828 | -123.0469
587.0156 | 123.111 | -58.9691 | 63.8306 | -0.18326 | 0.0053129 | 0.068464 | 0.068808 | 0.12971 | -0.0015723 | -0.0019505 | -0.053558 | -0.0052808 | 0.058924 | 0.060389 | 0.0039948 | -0.0064194 | 63.8809 | 64.0457 | 0.07782 | -59.1522 | 63.8718 | -59.0515 | -59.0973 | -59.0515 | 0.32501 | -59.1888 | 63.8397 | 63.7161 | -59.166 | -59.2026 | -0.082398 | -0.12817 | 0.041199 | 123.0148 | -0.18311 | -0.054932 | 0.050354 | -0.19684 | -0.23346 | 0.009156 | -0.082398 | -0.21973 | 0.013733 | -0.11444 | 122.8409 | 122.85 | 59.0469 | -122.9279 | 122.8088 | 122.6852 | 59.2941 | -123.0331
588.0156 | 123.0743 | -58.9828 | 63.8168 | -0.03067 | 0.0046719 | 0.06825 | 0.067099 | 0.12971 | -0.0019995 | -0.0038731 | 0.060883 | -0.0059216 | 0.06106 | 0.059748 | 0.00014962 | -0.005565 | 63.7527 | 63.9359 | -0.027466 | -59.2117 | 63.8397 | -59.0927 | -59.1293 | -58.9417 | 0.064087 | -59.2209 | 63.8443 | 63.739 | -59.1248 | -59.2209 | -0.10986 | -0.14648 | 0.022889 | 122.9187 | -0.22888 | -0.082398 | -0.064086 | -0.14191 | -0.23804 | 0.027466 | 0.041199 | -0.23804 | 0 | -0.077819 | 122.8226 | 122.7356 | 58.9554 | -122.9462 | 122.8271 | 122.7219 | 59.0469 | -123.0377
589.0156 | 123.1522 | -58.992 | 63.7939 | -0.12222 | 0.0042447 | 0.067823 | 0.070517 | 0.13121 | -7.6852e-05 | -0.0051547 | -0.11459 | -0.0059216 | 0.06341 | 0.058467 | 0.0033538 | -0.0057786 | 63.8901 | 64.0549 | 0.082397 | -59.1293 | 63.8535 | -59.0332 | -59.0927 | -58.8684 | 0.16937 | -59.1019 | 63.8489 | 63.7848 | -59.0881 | -59.198 | -0.041199 | -0.10071 | 0.05951 | 123.0469 | -0.13733 | -0.036621 | 0.096131 | -0.096131 | -0.20599 | 0.054932 | 0.1236 | -0.10986 | 0.09613 | -0.009155 | 122.8455 | 122.8821 | 59.0744 | -122.8867 | 122.8409 | 122.7768 | 59.1614 | -122.9919
590.0156 | 123.1064 | -58.992 | 63.8077 | -1.1522 | 0.0038175 | 0.068037 | 0.069876 | 0.13099 | -0.00050425 | -0.0047275 | 0.060883 | -0.0059216 | 0.065546 | 0.062739 | 0.0014312 | -0.0047104 | 63.7939 | 63.9038 | -0.045776 | -59.2209 | 63.8672 | -59.0698 | -59.1202 | -58.9462 | 0.050354 | -59.2255 | 63.8351 | 63.7161 | -59.1568 | -59.2484 | -0.07782 | -0.12817 | 0.059509 | 122.8958 | -0.22888 | -0.10071 | -0.013733 | -0.16479 | -0.25635 | 0.027466 | 0.045776 | -0.23346 | 0.022888 | -0.091553 | 122.8592 | 122.7859 | 58.9462 | -122.9279 | 122.8271 | 122.7081 | 59.0424 | -123.056
591.0156 | 123.1659 | -58.9691 | 63.7939 | -0.10696 | 0.0065945 | 0.068678 | 0.070731 | 0.13035 | -0.0013587 | -0.0028049 | -0.13748 | -0.006349 | 0.059351 | 0.061885 | 0.0024994 | -0.0068466 | 63.8718 | 64.0137 | 0.045776 | -59.1614 | 63.8489 | -59.0378 | -59.0973 | -58.8547 | 0.20599 | -59.1385 | 63.8489 | 63.7482 | -59.1248 | -59.2117 | -0.068665 | -0.12817 | 0.054932 | 122.9828 | -0.19226 | -0.064087 | 0.07782 | -0.15564 | -0.24262 | 0.054932 | 0.11444 | -0.16937 | 0.073242 | -0.045776 | 122.818 | 122.8409 | 59.0149 | -122.8912 | 122.818 | 122.7173 | 59.1751 | -123.0057
592.0156 | 123.1247 | -58.992 | 63.7894 | 0.13718 | 0.0038175 | 0.064832 | 0.066458 | 0.13142 | -0.00050425 | -0.0013095 | 0.16769 | -0.0048536 | 0.063623 | 0.061244 | 0.0024994 | -0.006633 | 63.7848 | 63.9084 | -0.064087 | -59.2209 | 63.8351 | -59.0561 | -59.1202 | -58.9508 | 0.022888 | -59.2484 | 63.8351 | 63.7207 | -59.1339 | -59.2255 | -0.064087 | -0.12817 | 0.045776 | 122.9004 | -0.22888 | -0.10071 | -0.004578 | -0.14191 | -0.23346 | 0.045776 | 0.041198 | -0.25635 | -0.022888 | -0.068665 | 122.8271 | 122.7768 | 58.9279 | -122.9095 | 122.8271 | 122.7127 | 59.0149 | -123.0148
593.0156 | 123.111 | -58.9783 | 63.8077 | -0.076447 | 0.0012539 | 0.069105 | 0.070517 | 0.12971 | -0.0019995 | -0.0025913 | -0.053558 | -0.0078442 | 0.061701 | 0.060389 | 0.0012176 | -0.0070602 | 63.8351 | 63.9954 | 0.041199 | -59.1797 | 63.8626 | -59.0561 | -59.0927 | -58.8776 | 0.16937 | -59.1476 | 63.8397 | 63.7436 | -59.0698 | -59.1843 | -0.07782 | -0.11444 | 0.054932 | 122.9736 | -0.20142 | -0.086975 | 0.027466 | -0.091553 | -0.20599 | 0.032044 | 0.10071 | -0.16937 | 0.036621 | -0.064087 | 122.8409 | 122.8134 | 59.0195 | -122.9004 | 122.818 | 122.7219 | 59.1476 | -122.9919
594.0156 | 123.1247 | -58.992 | 63.7894 | -0.015411 | 0.0033901 | 0.067823 | 0.067526 | 0.12907 | -0.00071785 | -0.0032321 | 0.0074766 | -0.0048536 | 0.060846 | 0.060389 | 0.0016448 | -0.003856 | 63.7939 | 63.9221 | -0.013733 | -59.2209 | 63.8535 | -59.0607 | -59.1064 | -58.9371 | 0.09613 | -59.2117 | 63.8535 | 63.739 | -59.1064 | -59.2026 | -0.068665 | -0.11444 | 0.064087 | 122.9141 | -0.22888 | -0.11444 | 0.004577 | -0.11444 | -0.21057 | 0.064087 | 0.054931 | -0.21973 | -0.009155 | -0.050354 | 122.8455 | 122.7859 | 58.9783 | -122.8958 | 122.8455 | 122.731 | 59.0881 | -122.9919
595.0156 | 123.1201 | -58.9783 | 63.8397 | -0.22141 | 0.0044583 | 0.068678 | 0.069449 | 0.13057 | -0.0015723 | -0.0013095 | 0.94589 | -0.0048536 | 0.06106 | 0.057612 | 0.0031402 | -0.0053512 | 63.8672 | 64.032 | 0.07782 | -59.1476 | 63.8763 | -59.0195 | -59.0927 | -58.96 | 0.19684 | -59.1568 | 63.8535 | 63.7573 | -59.1019 | -59.2209 | -0.041199 | -0.11444 | 0.036621 | 123.0103 | -0.16937 | -0.054932 | 0.027465 | -0.1236 | -0.24262 | 0.013733 | 0.01831 | -0.17853 | 0.064087 | -0.082398 | 122.8546 | 122.8455 | 59.0561 | -122.9324 | 122.8317 | 122.7356 | 59.1751 | -123.0606
596.0156 | 123.1201 | -59.0149 | 63.8123 | 0.030365 | 0.0044583 | 0.06761 | 0.067526 | 0.12864 | -0.0013587 | -0.00024146 | 0.053253 | -0.0044264 | 0.058496 | 0.060176 | 0.0031402 | -0.0057786 | 63.7665 | 63.9267 | -0.041199 | -59.2117 | 63.8626 | -59.079 | -59.1248 | -58.9508 | 0.059509 | -59.2072 | 63.8489 | 63.7344 | -59.1202 | -59.2209 | -0.064086 | -0.10986 | 0.050354 | 122.9416 | -0.19684 | -0.086975 | -0.045777 | -0.10529 | -0.20599 | 0.036621 | 0.064087 | -0.19226 | 0.013733 | -0.07782 | 122.8775 | 122.7814 | 58.9737 | -122.937 | 122.8638 | 122.7493 | 59.0744 | -123.0331
597.0156 | 122.9828 | -58.9783 | 63.8214 | -0.14511 | 0.0038175 | 0.06825 | 0.066672 | 0.12971 | -0.0013587 | -0.0015231 | -0.12222 | -0.005708 | 0.060419 | 0.060176 | 0.0024994 | -0.0057786 | 63.8535 | 64.0457 | 0.07782 | -59.1522 | 63.8489 | -59.024 | -59.0836 | -58.8913 | 0.17853 | -59.166 | 63.8489 | 63.7482 | -59.0973 | -59.1705 | -0.045777 | -0.10529 | 0.027466 | 123.024 | -0.17395 | -0.068665 | 0.032044 | -0.11902 | -0.19226 | 0.027466 | 0.086975 | -0.18768 | 0.004577 | -0.073242 | 122.8271 | 122.8317 | 59.0561 | -122.905 | 122.8271 | 122.7264 | 59.1568 | -122.9919
598.0156 | 123.0789 | -59.0057 | 63.8397 | 0.12192 | 0.0027493 | 0.067182 | 0.070944 | 0.13014 | -0.00029045 | -0.0021641 | 0.053253 | -0.0059216 | 0.05871 | 0.060389 | 0.0020722 | -0.0047104 | 63.7161 | 63.945 | -0.068665 | -59.2163 | 63.858 | -59.0652 | -59.111 | -58.9737 | 0.022888 | -59.2346 | 63.858 | 63.7024 | -59.1293 | -59.2209 | -0.05951 | -0.10529 | 0.01831 | 122.9507 | -0.21057 | -0.10529 | -0.1236 | -0.1236 | -0.21515 | 0.01831 | 0.032043 | -0.22888 | -0.013733 | -0.13733 | 122.8638 | 122.7219 | 58.9371 | -122.9507 | 122.8638 | 122.7081 | 59.0286 | -123.0606
599.0156 | 123.1384 | -59.0103 | 63.8031 | -0.03067 | 0.0016813 | 0.070173 | 0.069449 | 0.12971 | -0.0030677 | -0.0043003 | -0.00015237 | -0.0065626 | 0.06106 | 0.057612 | 0.0033538 | -0.004924 | 63.7848 | 63.9542 | 0.013733 | -59.1888 | 63.8763 | -59.0607 | -59.1064 | -58.9142 | 0.10529 | -59.1888 | 63.8535 | 63.7619 | -59.1431 | -59.2255 | -0.050354 | -0.09613 | 0.073242 | 122.9645 | -0.17853 | -0.082398 | -0.018311 | -0.13275 | -0.21515 | 0.050354 | 0.09613 | -0.17853 | 0.036621 | -0.041199 | 122.8867 | 122.7951 | 59.024 | -122.9095 | 122.8638 | 122.7722 | 59.1156 | -123.0286
600.0156 | 123.0972 | -58.9828 | 63.8077 | 0.030365 | 0.0025357 | 0.069319 | 0.06539 | 0.13099 | -0.00050425 | -0.0064365 | 0.060883 | -0.0059216 | 0.060846 | 0.062525 | 0.0020722 | -0.0057786 | 63.7848 | 63.9404 | -0.032043 | -59.1934 | 63.8626 | -59.0561 | -59.1293 | -58.9371 | 0.10071 | -59.198 | 63.8718 | 63.7344 | -59.1522 | -59.2117 | -0.073242 | -0.14648 | 0.054932 | 122.9233 | -0.21057 | -0.064087 | -0.022888 | -0.16937 | -0.22888 | 0.064087 | 0.045776 | -0.21515 | 0.013733 | -0.073242 | 122.8455 | 122.7676 | 58.9508 | -122.937 | 122.8546 | 122.7173 | 59.0836 | -123.0194
601.0156 | 123.1567 | -58.9737 | 63.7756 | -0.14511 | 0.0040311 | 0.068891 | 0.070517 | 0.13249 | -0.00071785 | -0.0023777 | -0.10696 | -0.011049 | 0.058924 | 0.063594 | 0.004422 | -0.006633 | 63.8763 | 64.032 | 0.064087 | -59.1385 | 63.8947 | -59.0149 | -59.1019 | -58.8409 | 0.16937 | -59.2346 | 63.8214 | 63.7161 | -59.111 | -59.2163 | -0.041199 | -0.12817 | 0.11902 | 123.0057 | -0.16479 | -0.036621 | 0.10071 | -0.13733 | -0.24262 | 0.045776 | 0.13275 | -0.26093 | -0.01831 | -0.05951 | 122.8683 | 122.85 | 59.0378 | -122.8775 | 122.7951 | 122.6898 | 59.1431 | -122.9919
602.0156 | 123.0972 | -58.992 | 63.8168 | 0.12955 | 0.0033901 | 0.066969 | 0.06774 | 0.13078 | -0.0013587 | -0.0047275 | 0.0914 | -0.0072034 | 0.06106 | 0.061244 | 0.0029266 | -0.005565 | 63.7482 | 63.9267 | -0.036621 | -59.2117 | 63.8535 | -59.0607 | -59.1293 | -58.9462 | 0.045776 | -59.2117 | 63.8535 | 63.7253 | -59.1385 | -59.2438 | -0.068665 | -0.13733 | 0.036622 | 122.9187 | -0.21973 | -0.082398 | -0.068664 | -0.14648 | -0.25177 | 0.036622 | 0.045776 | -0.21973 | 0.032043 | -0.091552 | 122.8455 | 122.7402 | 58.9554 | -122.9462 | 122.8455 | 122.7173 | 59.0378 | -123.0606
603.0156 | 123.2437 | -58.96 | 63.858 | -0.15274 | 0.0033901 | 0.066969 | 0.069449 | 0.12993 | -0.0024269 | -0.0032321 | -0.091705 | -0.0052808 | 0.061914 | 0.059962 | 0.0018584 | -0.0064194 | 63.8489 | 64.0274 | 0.073242 | -59.1431 | 63.8443 | -59.0286 | -59.1064 | -58.8821 | 0.17853 | -59.1705 | 63.858 | 63.7253 | -59.1064 | -59.198 | -0.068664 | -0.14648 | -0.013733 | 122.9874 | -0.1831 | -0.036621 | -0.009155 | -0.14648 | -0.23804 | 0 | 0.07782 | -0.21057 | 0.027466 | -0.13275 | 122.8043 | 122.8088 | 59.0332 | -122.9645 | 122.818 | 122.6852 | 59.1385 | -123.056
604.0156 | 123.1247 | -59.0103 | 63.8214 | -0.00015269 | 0.0025357 | 0.068037 | 0.068594 | 0.13035 | -0.00071785 | -0.0017369 | 0.11429 | -0.0059216 | 0.062982 | 0.059748 | 0.00079042 | -0.0036424 | 63.6566 | 63.9404 | -0.027466 | -59.2346 | 63.8489 | -59.0561 | -59.1202 | -58.9462 | 0.036621 | -59.23 | 63.826 | 63.7344 | -59.1614 | -59.2346 | -0.045776 | -0.10986 | 0.027466 | 122.9507 | -0.2243 | -0.11444 | -0.16479 | -0.15106 | -0.2243 | 0.004578 | 0.064087 | -0.21973 | 0.004577 | -0.086975 | 122.8592 | 122.6669 | 58.9828 | -122.9416 | 122.8363 | 122.7448 | 59.0469 | -123.056
605.0156 | 123.1522 | -58.992 | 63.8077 | -0.053558 | 0.0029629 | 0.066328 | 0.066885 | 0.13035 | 0.00099115 | -0.0038731 | -0.084076 | -0.0067762 | 0.060205 | 0.059321 | 0.002713 | -0.0059922 | 63.8306 | 64.0182 | 0.045776 | -59.1705 | 63.8489 | -59.0332 | -59.0744 | -58.8638 | 0.16937 | -59.1339 | 63.8489 | 63.7207 | -59.1019 | -59.198 | -0.041199 | -0.082398 | 0.041199 | 123.0103 | -0.17853 | -0.09613 | 0.022888 | -0.10986 | -0.20599 | 0.041199 | 0.12817 | -0.14191 | 0.064087 | -0.086975 | 122.8409 | 122.8226 | 59.0378 | -122.8821 | 122.8409 | 122.7127 | 59.1614 | -123.0057
606.0156 | 123.0881 | -58.9828 | 63.8123 | 0.13718 | 0.0046719 | 0.068891 | 0.069022 | 0.13121 | 0.00099115 | -0.0019505 | 0.2211 | -0.0054944 | 0.062769 | 0.061244 | 0.0014312 | -0.005565 | 63.7985 | 63.9404 | -0.036621 | -59.2392 | 63.826 | -59.0607 | -59.1019 | -58.9508 | 0.004578 | -59.2392 | 63.8031 | 63.6978 | -59.1522 | -59.2209 | -0.07782 | -0.11902 | 0.013733 | 122.9233 | -0.25635 | -0.13733 | -0.013733 | -0.16937 | -0.23804 | -0.009155 | 0.032043 | -0.25635 | -0.018311 | -0.11444 | 122.8088 | 122.7814 | 58.9462 | -122.9141 | 122.7859 | 122.6807 | 58.9874 | -123.0331
607.0156 | 123.111 | -58.9874 | 63.8168 | -0.17563 | 0.0053129 | 0.066969 | 0.071372 | 0.1342 | -7.6852e-05 | -0.0038731 | 2.0827 | -0.0033582 | 0.060633 | 0.061457 | 0.002713 | -0.0053512 | 63.8718 | 64.0182 | 0.073242 | -59.1476 | 63.8672 | -59.0698 | -59.0881 | -58.905 | 0.21515 | -59.1843 | 63.8535 | 63.7299 | -59.1385 | -59.2072 | -0.082397 | -0.10071 | 0.050354 | 123.0057 | -0.16022 | -0.059509 | 0.054932 | -0.15106 | -0.21973 | 0.036622 | 0.082398 | -0.19684 | 0.022888 | -0.086975 | 122.8546 | 122.8592 | 59.0607 | -122.905 | 122.8409 | 122.7173 | 59.2026 | -123.024
608.0156 | 123.1018 | -58.9966 | 63.7985 | 0.0914 | 0.0042447 | 0.06761 | 0.068167 | 0.13078 | -0.0026405 | -0.0019505 | 0.030365 | -0.0061352 | 0.060419 | 0.06103 | 0.0012176 | -0.003856 | 63.7711 | 63.9267 | -0.032043 | -59.2026 | 63.8672 | -59.0607 | -59.1202 | -58.9554 | 0.064087 | -59.1934 | 63.8397 | 63.7573 | -59.1339 | -59.2255 | -0.064087 | -0.1236 | 0.068664 | 122.9233 | -0.20599 | -0.082398 | -0.027466 | -0.13733 | -0.22888 | 0.041199 | 0.041199 | -0.19684 | 0.032044 | -0.041199 | 122.8638 | 122.7676 | 58.9645 | -122.9187 | 122.8363 | 122.7539 | 59.0607 | -123.024
609.0156 | 123.0881 | -58.9966 | 63.8214 | -0.10696 | 0.0042447 | 0.067396 | 0.069663 | 0.12736 | 0.0020593 | -0.0030185 | -0.15274 | -0.00464 | 0.060633 | 0.059748 | 0.0029266 | -0.0070602 | 63.8626 | 63.9954 | 0.054932 | -59.1476 | 63.8443 | -59.0469 | -59.1064 | -58.9142 | 0.1831 | -59.1888 | 63.8718 | 63.7711 | -59.1293 | -59.2026 | -0.050354 | -0.10986 | 0.022888 | 122.9919 | -0.15106 | -0.041199 | 0.041199 | -0.13275 | -0.20599 | 0.050354 | 0.082397 | -0.19226 | 0.013733 | -0.050354 | 122.8409 | 122.8592 | 59.0515 | -122.9279 | 122.8683 | 122.7676 | 59.1797 | -123.024
610.0156 | 123.0972 | -58.9874 | 63.8077 | 1.2434 | 0.0016813 | 0.069319 | 0.068381 | 0.13014 | -0.0011451 | -0.0036595 | 0.060883 | -0.0069898 | 0.061273 | 0.060176 | 0.0022858 | -0.0042832 | 63.7573 | 63.913 | -0.041199 | -59.2072 | 63.8672 | -59.0652 | -59.1293 | -58.9508 | 0.050354 | -59.2255 | 63.8397 | 63.7253 | -59.1522 | -59.23 | -0.07782 | -0.14191 | 0.059509 | 122.9004 | -0.21973 | -0.07782 | -0.050354 | -0.1648 | -0.24262 | 0.032044 | 0.036621 | -0.23804 | 0.004578 | -0.082397 | 122.8546 | 122.7448 | 58.9462 | -122.937 | 122.8271 | 122.7127 | 59.0378 | -123.0377
611.0156 | 123.0057 | -58.9554 | 63.8626 | -0.12222 | 0.0044583 | 0.067823 | 0.068808 | 0.13142 | -0.0015723 | -0.0040867 | -0.15274 | -0.0037854 | 0.061273 | 0.060389 | 0.0037812 | -0.0051376 | 63.8351 | 64.0411 | 0.091553 | -59.1476 | 63.8718 | -59.0424 | -59.1064 | -58.8684 | 0.1831 | -59.1293 | 63.8397 | 63.7482 | -59.1019 | -59.1934 | -0.086975 | -0.15106 | 0.009155 | 122.9965 | -0.19226 | -0.041199 | -0.027466 | -0.14649 | -0.23804 | -0.022888 | 0.086975 | -0.17395 | 0.064087 | -0.11444 | 122.8271 | 122.7905 | 59.0469 | -122.9691 | 122.7951 | 122.7036 | 59.1385 | -123.056
612.0156 | 123.0789 | -59.0286 | 63.7939 | 0.12955 | 0.0033901 | 0.068678 | 0.068594 | 0.13185 | -0.00029045 | -0.0032321 | 0.27451 | -0.00464 | 0.058069 | 0.060389 | 0.0046356 | -0.0053512 | 63.7756 | 63.9221 | -0.045776 | -59.23 | 63.8306 | -59.0698 | -59.111 | -58.9462 | 0.036621 | -59.2438 | 63.8351 | 63.7344 | -59.1614 | -59.2255 | -0.041199 | -0.082398 | 0.036621 | 122.9507 | -0.20142 | -0.11902 | -0.01831 | -0.13275 | -0.19684 | 0.041199 | 0.082397 | -0.21515 | -0.01831 | -0.059509 | 122.8592 | 122.8043 | 58.9828 | -122.905 | 122.8638 | 122.7631 | 59.0652 | -123.0194
613.0156 | 123.1338 | -59.0012 | 63.7985 | -0.0383 | 0.0053129 | 0.066541 | 0.067526 | 0.13163 | -0.0034949 | -0.0036595 | -0.00015237 | -0.0042126 | 0.062769 | 0.061671 | 0.0018584 | -0.0053512 | 63.7939 | 63.9633 | -0.013733 | -59.1888 | 63.8489 | -59.0561 | -59.1202 | -58.9142 | 0.11444 | -59.1934 | 63.8306 | 63.7436 | -59.1202 | -59.2026 | -0.054931 | -0.11902 | 0.050354 | 122.9645 | -0.18768 | -0.068665 | -0.004578 | -0.11902 | -0.20142 | 0.032043 | 0.086975 | -0.19226 | 0.009156 | -0.054932 | 122.85 | 122.7951 | 58.9874 | -122.9187 | 122.8317 | 122.7448 | 59.1156 | -123.0011
614.0156 | 123.0927 | -58.9645 | 63.7985 | 0.022736 | 0.0040311 | 0.06761 | 0.067954 | 0.12843 | -0.0017859 | -0.0021641 | 0.0074766 | -0.0065626 | 0.060419 | 0.059321 | 0.0031402 | -0.006633 | 63.7894 | 63.9267 | -0.004578 | -59.198 | 63.8718 | -59.0561 | -59.1156 | -58.9325 | 0.10071 | -59.2026 | 63.858 | 63.7115 | -59.1385 | -59.23 | -0.091552 | -0.15106 | 0.073242 | 122.8912 | -0.23346 | -0.082397 | -0.009155 | -0.17395 | -0.2655 | 0.059509 | 0.032044 | -0.23804 | 0.027466 | -0.086975 | 122.8363 | 122.7539 | 58.96 | -122.9141 | 122.8226 | 122.6761 | 59.0652 | -123.0286
615.0156 | 123.143 | -58.9828 | 63.8168 | -0.13748 | 0.0038175 | 0.067823 | 0.07009 | 0.13142 | -0.0011451 | -0.0032321 | -1.3277 | -0.0052808 | 0.062555 | 0.058894 | 0.00079042 | -0.0072738 | 63.858 | 64.0091 | -0.059509 | -58.9417 | 63.9038 | -59.0149 | -59.0927 | -58.9005 | 0.13275 | -59.1476 | 63.8535 | 63.7436 | -59.1019 | -59.198 | -0.032044 | -0.10986 | 0.086976 | 122.9919 | 0.041199 | 0.15106 | 0.041199 | -0.11902 | -0.21515 | 0.036622 | 0.082397 | -0.16479 | 0.050354 | -0.073242 | 122.8867 | 122.8409 | 58.9233 | -122.9095 | 122.8363 | 122.7264 | 59.1156 | -123.0148
616.0156 | 123.1018 | -58.9966 | 63.8123 | -0.045929 | 0.0029629 | 0.068891 | 0.069235 | 0.13035 | -0.0037085 | -0.0028049 | 0.045624 | -0.0050672 | 0.060633 | 0.05868 | 0.002713 | -0.005565 | 63.7711 | 63.9313 | -0.027466 | -59.2072 | 63.8626 | -59.0424 | -59.1202 | -58.9462 | 0.068665 | -59.2163 | 63.8397 | 63.7344 | -59.1385 | -59.2209 | -0.045776 | -0.1236 | 0.050354 | 122.9279 | -0.21057 | -0.086975 | -0.041199 | -0.14191 | -0.2243 | 0.027466 | 0.050354 | -0.21973 | 0.004577 | -0.07782 | 122.8592 | 122.7676 | 58.9691 | -122.9324 | 122.8363 | 122.731 | 59.0652 | -123.0331
617.0156 | 123.0927 | -58.9783 | 63.8123 | -0.11459 | 0.0010403 | 0.069532 | 0.071799 | 0.12971 | -0.0017859 | -0.0040867 | -0.21378 | -0.0059216 | 0.061914 | 0.06103 | 0.004422 | -0.013042 | 63.8855 | 64.0457 | 0.09613 | -59.1522 | 63.8901 | -59.0652 | -59.1064 | -58.7906 | 0.49439 | -59.404 | 63.8947 | 63.7207 | -59.1156 | -59.2026 | -0.086976 | -0.12817 | 0.07782 | 123.024 | -0.17395 | -0.045777 | 0.073242 | -0.13733 | -0.22431 | 0.082397 | 0.18768 | -0.42572 | -0.20142 | -0.091553 | 122.8683 | 122.8638 | 59.0744 | -122.9187 | 122.8729 | 122.699 | 59.4727 | -123.0148
618.0156 | 123.1247 | -58.9874 | 63.826 | 0.41183 | 0.0048855 | 0.067823 | 0.068381 | 0.12928 | -0.00029045 | -0.0023777 | 0.076141 | -0.0048536 | 0.061273 | 0.060389 | 0.0024994 | -0.0072738 | 63.7756 | 63.913 | -0.045776 | -59.2209 | 63.8535 | -59.0561 | -59.1156 | -58.9508 | 0.050354 | -59.2117 | 63.8535 | 63.7161 | -59.1476 | -59.2255 | -0.068664 | -0.12817 | 0.027466 | 122.9004 | -0.23346 | -0.10529 | -0.050354 | -0.16022 | -0.23804 | 0.027466 | 0.036621 | -0.2243 | 0.013733 | -0.10986 | 122.8409 | 122.7631 | 58.9417 | -122.9416 | 122.8409 | 122.7036 | 59.0378 | -123.0515
619.0156 | 123.1201 | -59.0103 | 63.8306 | -0.061188 | 0.0036039 | 0.066969 | 0.069449 | 0.13185 | -0.0015723 | -0.0025913 | -0.038299 | -0.00464 | 0.062769 | 0.060816 | 0.0022858 | -0.0064194 | 63.858 | 63.9725 | 0.064087 | -59.1293 | 63.8626 | -59.0424 | -59.0881 | -58.905 | 0.16937 | -59.1751 | 63.8626 | 63.7482 | -59.111 | -59.1843 | -0.032043 | -0.07782 | 0.032044 | 122.9828 | -0.11902 | -0.041198 | 0.027466 | -0.10071 | -0.17395 | 0.032044 | 0.10529 | -0.16479 | 0.009155 | -0.082397 | 122.8729 | 122.8683 | 59.0744 | -122.9187 | 122.8729 | 122.7585 | 59.1797 | -123.0148
620.0156 | 123.0652 | -58.9828 | 63.7985 | 0.10666 | 0.0038175 | 0.06526 | 0.067526 | 0.12779 | -0.0017859 | -0.0032321 | 0.17532 | -0.0076306 | 0.061273 | 0.061244 | 0.00079042 | -0.0062058 | 63.7711 | 63.9221 | -0.059509 | -59.2209 | 63.8397 | -59.079 | -59.1339 | -58.9508 | 0 | -59.2438 | 63.8306 | 63.7161 | -59.1614 | -59.2346 | -0.09613 | -0.15106 | 0.041199 | 122.905 | -0.23804 | -0.086975 | -0.027466 | -0.17853 | -0.25177 | 0.032043 | 0.032043 | -0.26093 | -0.009155 | -0.082398 | 122.8226 | 122.7539 | 58.9233 | -122.9324 | 122.8134 | 122.699 | 58.9828 | -123.0331
621.0156 | 123.0652 | -58.9783 | 63.8351 | -0.19089 | 0.0053129 | 0.068037 | 0.070944 | 0.13206 | 0.00013675 | -0.0028049 | -0.18326 | -0.0054944 | 0.061487 | 0.061457 | 0.0020722 | -0.0079148 | 63.8306 | 64.0045 | 0.068665 | -59.166 | 63.8718 | -59.0286 | -59.1019 | -58.9279 | 0.16479 | -59.2026 | 63.8809 | 63.7482 | -59.111 | -59.2072 | -0.050354 | -0.1236 | 0.036621 | 122.9828 | -0.18768 | -0.064087 | -0.004578 | -0.13275 | -0.22888 | 0.045776 | 0.050354 | -0.22431 | 0.004577 | -0.086975 | 122.85 | 122.8088 | 59.0469 | -122.937 | 122.8592 | 122.7264 | 59.1431 | -123.0423
622.0156 | 123.0972 | -59.024 | 63.8123 | 0.045624 | 0.0038175 | 0.066541 | 0.067313 | 0.13463 | -0.00071785 | -0.0023777 | -0.00015237 | -0.006349 | 0.059992 | 0.060816 | 0.00036322 | -0.0053512 | 63.7619 | 63.9359 | -0.022888 | -59.2163 | 63.8718 | -59.0652 | -59.1339 | -58.9325 | 0.068665 | -59.2026 | 63.858 | 63.7527 | -59.1339 | -59.2392 | -0.041199 | -0.10986 | 0.059509 | 122.9599 | -0.19226 | -0.082398 | -0.050354 | -0.10986 | -0.21515 | 0.045776 | 0.091553 | -0.17853 | 0.036621 | -0.059509 | 122.8958 | 122.7859 | 59.0012 | -122.9462 | 122.8821 | 122.7768 | 59.0927 | -123.0515
623.0156 | 123.1613 | -58.9783 | 63.7848 | -0.22903 | 0.0036039 | 0.066541 | 0.067313 | 0.13014 | -0.0019995 | -0.0030185 | -0.11459 | -0.00464 | 0.061273 | 0.06103 | 0.0024994 | -0.004924 | 63.8535 | 64.0457 | 0.091553 | -59.1385 | 63.8809 | -59.0424 | -59.0973 | -58.8959 | 0.16937 | -58.8638 | 63.8901 | 63.8031 | -59.0973 | -59.2026 | -0.064087 | -0.11902 | 0.09613 | 123.024 | -0.16022 | -0.041199 | 0.068665 | -0.11902 | -0.22431 | 0.10529 | 0.082397 | 0.11444 | 0.33875 | 0.018311 | 122.8592 | 122.8317 | 59.0698 | -122.8821 | 122.8683 | 122.7814 | 59.1476 | -122.9874
624.0156 | 123.056 | -59.0149 | 63.7985 | 0.030365 | 0.0023221 | 0.072096 | 0.067526 | 0.12822 | -0.00093145 | -0.0030185 | 0.053253 | -0.0061352 | 0.061701 | 0.059535 | 0.0020722 | -0.0051376 | 63.7573 | 63.8992 | -0.032043 | -59.2072 | 63.8763 | -59.0881 | -59.1248 | -58.9508 | 0.064087 | -59.2163 | 63.858 | 63.7344 | -59.1568 | -59.198 | -0.073242 | -0.10986 | 0.07782 | 122.9141 | -0.19226 | -0.082397 | -0.041199 | -0.14191 | -0.1831 | 0.059509 | 0.064087 | -0.20142 | -0.018311 | -0.064087 | 122.8912 | 122.7722 | 58.9828 | -122.9233 | 122.8729 | 122.7493 | 59.079 | -122.9965
625.0156 | 123.1247 | -58.96 | 63.8031 | -3.8148 | 0.0072355 | 0.063337 | 0.06774 | 0.12928 | -0.0015723 | -0.0043003 | -0.023041 | -0.005708 | 0.062769 | 0.060603 | 0.0029266 | -0.0062058 | 63.739 | 64.0182 | 0.086975 | -59.1385 | 63.8489 | -59.0332 | -59.1156 | -58.905 | 0.17395 | -59.1797 | 63.8443 | 63.7527 | -59.111 | -59.2026 | -0.073242 | -0.15564 | 0.045776 | 122.9782 | -0.17853 | -0.022888 | -0.064087 | -0.15106 | -0.24262 | 0.041198 | 0.054932 | -0.21973 | 0.022889 | -0.050354 | 122.8088 | 122.699 | 59.0469 | -122.9187 | 122.8043 | 122.7127 | 59.1339 | -123.0057
626.0156 | 123.0652 | -59.024 | 63.7985 | 0.13718 | 0.0053129 | 0.068464 | 0.069663 | 0.1295 | -0.00093145 | -0.0047275 | 0.19821 | -0.0050672 | 0.060633 | 0.06103 | 0.0029266 | -0.0042832 | 63.7848 | 63.9313 | -0.054932 | -59.2163 | 63.8168 | -59.079 | -59.1431 | -58.96 | 0.004578 | -59.2438 | 63.8214 | 63.7024 | -59.1293 | -59.2621 | -0.054931 | -0.11902 | 0.01831 | 122.9553 | -0.19226 | -0.073243 | -0.013733 | -0.10529 | -0.23804 | 0.022888 | 0.064087 | -0.21973 | 0.018311 | -0.09613 | 122.8409 | 122.8088 | 58.9691 | -122.9416 | 122.8455 | 122.7264 | 59.0286 | -123.0606
627.0156 | 123.0835 | -58.9966 | 63.8214 | 0.0074768 | 0.00018591 | 0.068464 | 0.069663 | 0.12886 | -0.0034949 | -0.0028049 | 0.076141 | -0.006349 | 0.061487 | 0.060389 | 0.0037812 | -0.0062058 | 63.7436 | 63.9359 | -0.036621 | -59.2026 | 63.858 | -59.0744 | -59.1385 | -58.96 | 0.07782 | -59.2163 | 63.8443 | 63.7619 | -59.1293 | -59.2072 | -0.07782 | -0.14191 | 0.036621 | 122.9324 | -0.20599 | -0.064087 | -0.07782 | -0.13275 | -0.21057 | 0.022888 | 0.036621 | -0.21973 | -0.009156 | -0.059509 | 122.8546 | 122.7402 | 58.96 | -122.9599 | 122.8409 | 122.7585 | 59.0744 | -123.0286
628.0156 | 123.1064 | -59.0012 | 63.8168 | 0.63309 | 0.0033901 | 0.068891 | 0.064536 | 0.13035 | -0.0019995 | -0.0017369 | 0.076141 | -0.0067762 | 0.06106 | 0.061244 | 0.0022858 | -0.004924 | 63.7482 | 63.8992 | -0.041199 | -59.2072 | 63.8672 | -59.0607 | -59.1339 | -58.9554 | 0.050354 | -59.2346 | 63.8397 | 63.7253 | -59.166 | -59.2209 | -0.059509 | -0.13275 | 0.050354 | 122.9004 | -0.20599 | -0.073242 | -0.068664 | -0.16479 | -0.21973 | 0.022889 | 0.045777 | -0.23346 | -0.013733 | -0.091552 | 122.8683 | 122.7493 | 58.96 | -122.9507 | 122.8409 | 122.7264 | 59.0515 | -123.0377
629.0156 | 123.1613 | -58.9691 | 63.8123 | -0.053558 | 0.0048855 | 0.067823 | 0.070303 | 0.13121 | -0.0028541 | -0.0010959 | -0.099335 | -0.0059216 | 0.061701 | 0.058253 | 0.0022858 | -0.005565 | 63.8168 | 64.032 | 0.073242 | -59.1476 | 63.8763 | -59.0469 | -59.1156 | -58.8638 | 0.18768 | -59.1293 | 63.8809 | 63.7482 | -59.0927 | -59.1934 | -0.07782 | -0.14648 | 0.064087 | 123.0011 | -0.17853 | -0.032043 | 0.004577 | -0.1236 | -0.2243 | 0.068664 | 0.10529 | -0.16022 | 0.064087 | -0.064087 | 122.8455 | 122.7859 | 59.0424 | -122.9279 | 122.85 | 122.7173 | 59.1568 | -123.0057
630.0156 | 123.0881 | -59.0103 | 63.7939 | -0.0077822 | 0.0029629 | 0.066541 | 0.069663 | 0.12886 | -0.0022131 | -0.0021641 | -1.4421 | -0.0065626 | 0.062555 | 0.060389 | 0.0012176 | -0.0070602 | 63.7619 | 63.9221 | -0.036621 | -59.2072 | 63.8718 | -59.0744 | -59.1293 | -58.9783 | 0.027466 | -59.2438 | 63.8443 | 63.7115 | -59.1248 | -59.2392 | -0.064087 | -0.11902 | 0.07782 | 122.9324 | -0.19684 | -0.07782 | -0.032043 | -0.11444 | -0.22888 | 0.050354 | 0.032044 | -0.23346 | -0.004577 | -0.082397 | 122.8821 | 122.7722 | 58.9737 | -122.9233 | 122.8546 | 122.7219 | 59.0378 | -123.0331
631.0156 | 123.111 | -58.9783 | 63.7894 | -0.099335 | 0.0027493 | 0.067823 | 0.067526 | 0.13334 | -0.00093145 | -0.0023777 | -0.0077819 | -0.0052808 | 0.061273 | 0.059321 | 0.0022858 | -0.0057786 | 63.8351 | 63.9908 | 0.013733 | -59.1843 | 63.8809 | -59.0469 | -59.1202 | -58.8913 | 0.12817 | -59.1614 | 63.8443 | 63.7299 | -59.0881 | -59.2209 | -0.068665 | -0.14191 | 0.091552 | 122.9691 | -0.20599 | -0.064087 | 0.045776 | -0.10986 | -0.24262 | 0.054931 | 0.086975 | -0.18311 | 0.059509 | -0.05951 | 122.8592 | 122.8134 | 58.992 | -122.9095 | 122.8226 | 122.7081 | 59.1064 | -123.0103
632.0156 | 123.0743 | -59.0012 | 63.7802 | 0.076141 | 0.0053129 | 0.066114 | 0.068381 | 0.128 | -0.00029045 | 0.00039954 | 0.20584 | -0.00464 | 0.063623 | 0.059321 | 0.0042084 | -0.0053512 | 63.7665 | 63.9175 | -0.050354 | -59.2163 | 63.8443 | -59.0561 | -59.1248 | -58.9417 | 0.009155 | -59.23 | 63.8489 | 63.739 | -59.1385 | -59.2392 | -0.054931 | -0.1236 | 0.064087 | 122.9187 | -0.21515 | -0.091553 | -0.013733 | -0.13733 | -0.23804 | 0.068665 | 0.05951 | -0.22888 | 0.009155 | -0.041198 | 122.8455 | 122.7676 | 58.9508 | -122.905 | 122.85 | 122.7402 | 59.0103 | -123.0194
633.0156 | 123.0515 | -59.0103 | 63.7939 | 0.015106 | 0.0029629 | 0.066114 | 0.068381 | 0.13377 | 0.00056395 | 0.00061314 | 0.09903 | -0.0048536 | 0.061273 | 0.058894 | 0.0018584 | -0.0062058 | 63.6337 | 63.9359 | -0.045776 | -59.2346 | 63.8489 | -59.0607 | -59.1019 | -58.9645 | 0.045776 | -59.23 | 63.8535 | 63.7299 | -59.1339 | -59.198 | -0.050354 | -0.091553 | 0.054932 | 122.9462 | -0.2243 | -0.13275 | -0.16022 | -0.1236 | -0.18768 | 0.05951 | 0.045776 | -0.21973 | -0.032044 | -0.064087 | 122.8592 | 122.644 | 58.9645 | -122.8958 | 122.8638 | 122.7402 | 59.0561 | -122.9919
634.0156 | 123.0927 | -59.0149 | 63.7665 | 0.21347 | 0.0072355 | 0.06761 | 0.068594 | 0.13163 | 0.0012047 | -0.00045506 | 0.12192 | -0.0061352 | 0.06106 | 0.060603 | 0.0042084 | -0.0068466 | 63.826 | 63.9404 | -0.036621 | -59.2026 | 63.8214 | -59.0561 | -59.1339 | -58.905 | 0.041199 | -59.2346 | 63.8031 | 63.7161 | -59.1293 | -59.2163 | -0.041198 | -0.11902 | 0.054932 | 122.9553 | -0.18768 | -0.068665 | 0.05951 | -0.11444 | -0.20142 | 0.036622 | 0.10986 | -0.21973 | -0.01831 | -0.050354 | 122.8363 | 122.8409 | 58.9783 | -122.9004 | 122.818 | 122.731 | 59.0561 | -122.9828
635.0156 | 123.1201 | -58.9691 | 63.7985 | -0.10696 | 0.0027493 | 0.067182 | 0.069663 | 0.12971 | -0.0019995 | -0.0030185 | -0.0077819 | -0.0050672 | 0.061914 | 0.059321 | -0.00027778 | -0.0057786 | 63.8397 | 63.9771 | 0.032043 | -59.1797 | 63.8626 | -59.024 | -59.111 | -58.8684 | 0.16022 | -59.1614 | 63.8397 | 63.739 | -59.1202 | -59.1934 | -0.054932 | -0.14191 | 0.064087 | 122.9462 | -0.21057 | -0.068664 | 0.041199 | -0.15106 | -0.2243 | 0.041199 | 0.10071 | -0.19226 | 0.032043 | -0.059509 | 122.8317 | 122.8088 | 59.0012 | -122.9095 | 122.8088 | 122.7081 | 59.1293 | -122.9919
636.0156 | 123.0423 | -58.9966 | 63.8077 | 0.060882 | 0.0063809 | 0.06825 | 0.070731 | 0.1295 | -0.0024269 | -0.0017369 | 0.13718 | -0.0050672 | 0.061273 | 0.06103 | 0.00079042 | -0.006633 | 63.7711 | 63.9221 | -0.050354 | -59.2117 | 63.8535 | -59.0698 | -59.1202 | -58.9691 | 0.027466 | -59.2484 | 63.858 | 63.7527 | -59.1248 | -59.1888 | -0.073242 | -0.1236 | 0.045777 | 122.9187 | -0.21515 | -0.091553 | -0.036621 | -0.12817 | -0.19226 | 0.050354 | 0.027466 | -0.25177 | -0.059509 | -0.054931 | 122.85 | 122.7676 | 58.9462 | -122.9279 | 122.8546 | 122.7493 | 59.024 | -122.9965
637.0156 | 123.1155 | -58.9737 | 63.8077 | -0.045929 | 0.0021085 | 0.068464 | 0.067954 | 0.13185 | -0.0017859 | -0.0040867 | -0.00015237 | -0.0076306 | 0.060205 | 0.058894 | 0.0022858 | -0.0057786 | 63.8214 | 63.9404 | 0.013733 | -59.1705 | 63.8489 | -59.024 | -59.0973 | -58.8959 | 0.12817 | -59.1751 | 63.8763 | 63.739 | -59.1339 | -59.2392 | -0.050354 | -0.1236 | 0.041199 | 122.9141 | -0.19684 | -0.073242 | 0.013733 | -0.16022 | -0.2655 | 0.068665 | 0.07782 | -0.20142 | 0.064087 | -0.068664 | 122.8226 | 122.7951 | 58.9874 | -122.905 | 122.85 | 122.7127 | 59.1019 | -123.0469
638.0156 | 123.0789 | -59.0012 | 63.7939 | 0.076141 | 0.0048855 | 0.066328 | 0.068808 | 0.12993 | 0.00013675 | -0.0036595 | 0.09903 | -0.0059216 | 0.058496 | 0.059321 | 0.002713 | -0.004924 | 63.7848 | 63.9038 | -0.064087 | -59.2255 | 63.8443 | -59.0424 | -59.1339 | -58.96 | 0.045776 | -59.2346 | 63.8306 | 63.7527 | -59.1293 | -59.23 | -0.041198 | -0.13275 | 0.050354 | 122.905 | -0.2243 | -0.091553 | -0.009155 | -0.12817 | -0.22888 | 0.036621 | 0.041199 | -0.23346 | -0.004577 | -0.041198 | 122.8455 | 122.7859 | 58.9371 | -122.9279 | 122.8317 | 122.7539 | 59.0469 | -123.024
639.0156 | 123.1064 | -58.9828 | 63.7848 | -0.045929 | 0.0059537 | 0.06761 | 0.068381 | 0.1295 | -0.0015723 | -0.0023777 | 0.045624 | -0.0037854 | 0.059137 | 0.058253 | 0.0031402 | -0.005565 | 63.7894 | 63.945 | -0.004578 | -59.1705 | 63.858 | -59.0378 | -59.0973 | -58.9096 | 0.086975 | -59.1934 | 63.8443 | 63.7207 | -59.1202 | -59.2117 | -0.054932 | -0.11444 | 0.073242 | 122.9279 | -0.18768 | -0.073242 | 0.004578 | -0.13733 | -0.22888 | 0.059509 | 0.073242 | -0.21057 | 0.018311 | -0.064087 | 122.8409 | 122.7722 | 58.9783 | -122.8821 | 122.8271 | 122.7036 | 59.0698 | -122.9965
640.0156 | 123.1338 | -58.9966 | 63.7573 | 0.12955 | 0.0055265 | 0.066328 | 0.068167 | 0.13163 | 0.0014185 | -0.0023777 | 0.20584 | -0.0050672 | 0.061273 | 0.059748 | 0.002713 | -0.0068466 | 63.8077 | 63.9359 | -0.032043 | -59.198 | 63.8306 | -59.0744 | -59.1156 | -58.905 | 0.022888 | -59.2392 | 63.8031 | 63.7115 | -59.1568 | -59.2392 | -0.07782 | -0.11902 | 0.073242 | 122.9324 | -0.20142 | -0.082397 | 0.050354 | -0.16022 | -0.24262 | 0.045777 | 0.091553 | -0.24262 | 0 | -0.045776 | 122.8271 | 122.8043 | 58.9645 | -122.8729 | 122.7997 | 122.7081 | 59.0195 | -122.9965
641.0156 | 123.056 | -59.0012 | 63.8123 | -0.00015269 | 0.0036039 | 0.06526 | 0.07009 | 0.12822 | -0.0028541 | -0.0040867 | -0.0077819 | -0.0031446 | 0.060633 | 0.059962 | 0.0037812 | -0.006633 | 63.7848 | 63.9221 | -0.018311 | -59.1843 | 63.8672 | -59.0607 | -59.1339 | -58.9325 | 0.086975 | -59.1843 | 63.8306 | 63.7344 | -59.1385 | -59.2392 | -0.059509 | -0.13275 | 0.054931 | 122.9233 | -0.18311 | -0.050354 | -0.027466 | -0.13733 | -0.23804 | 0.01831 | 0.068665 | -0.18311 | 0.054932 | -0.07782 | 122.8683 | 122.7859 | 58.9828 | -122.9462 | 122.8317 | 122.7356 | 59.0881 | -123.0515
642.0156 | 122.9919 | -58.9966 | 63.8763 | -0.22141 | 0.0055265 | 0.06761 | 0.069449 | 0.13292 | 0.0012047 | -0.0019505 | -0.51132 | -0.0048536 | 0.060419 | 0.058039 | 0.0029266 | -0.004924 | 63.8031 | 63.9221 | 0.004578 | -59.198 | 63.9038 | -59.0378 | -59.1339 | -58.9874 | 0.07782 | -59.2712 | 63.9267 | 63.7939 | -59.1522 | -59.2026 | -0.041199 | -0.13733 | 0.027466 | 122.9187 | -0.20142 | -0.064087 | -0.073242 | -0.15564 | -0.20599 | 0.050354 | 0.009155 | -0.27466 | -0.068664 | -0.082398 | 122.9004 | 122.7997 | 59.0012 | -123.0103 | 122.9233 | 122.7905 | 59.0744 | -123.0789
643.0156 | 123.0789 | -58.9966 | 63.8123 | -0.084076 | 0.0033901 | 0.068891 | 0.066672 | 0.12864 | -0.0037085 | -0.0023777 | 0.037995 | -0.005708 | 0.05871 | 0.06103 | 0.0029266 | -0.0051376 | 63.8214 | 63.9633 | 0.022888 | -59.1843 | 63.8672 | -59.0424 | -59.1064 | -58.905 | 0.13733 | -59.1614 | 63.8489 | 63.7344 | -59.1248 | -59.2163 | -0.045776 | -0.10986 | 0.054931 | 122.9599 | -0.18768 | -0.07782 | 0.009155 | -0.12817 | -0.21973 | 0.036621 | 0.091553 | -0.1648 | 0.054932 | -0.07782 | 122.8638 | 122.818 | 59.0195 | -122.9187 | 122.8455 | 122.731 | 59.1339 | -123.0286
644.0156 | 123.0377 | -59.0195 | 63.8077 | 0.0914 | 0.0087307 | 0.065473 | 0.068808 | 0.12822 | -0.0017859 | -0.0038731 | 0.11429 | -0.0067762 | 0.061487 | 0.05868 | 0.0035674 | -0.0062058 | 63.7665 | 63.8855 | -0.054932 | -59.2209 | 63.8351 | -59.0652 | -59.1064 | -58.9645 | 0.027466 | -59.2438 | 63.8443 | 63.7161 | -59.1339 | -59.23 | -0.045777 | -0.086975 | 0.027466 | 122.905 | -0.20142 | -0.11444 | -0.041199 | -0.11444 | -0.21057 | 0.036621 | 0.054931 | -0.2243 | -0.013732 | -0.091553 | 122.8546 | 122.7859 | 58.9645 | -122.9141 | 122.8638 | 122.7356 | 59.0469 | -123.0377
645.0156 | 123.1201 | -58.9828 | 63.7985 | -0.03067 | 0.0031765 | 0.068678 | 0.068167 | 0.13035 | -0.0026405 | -0.0043003 | -0.0077819 | -0.0048536 | 0.06106 | 0.059962 | 0.0035674 | -0.0053512 | 63.7985 | 63.9587 | 0 | -59.1888 | 63.8947 | -59.0469 | -59.1385 | -58.9096 | 0.11444 | -59.2026 | 63.8489 | 63.7299 | -59.1248 | -59.23 | -0.064087 | -0.15564 | 0.09613 | 122.9416 | -0.20599 | -0.050354 | 0 | -0.14191 | -0.24719 | 0.050354 | 0.073242 | -0.21973 | 0.027466 | -0.068665 | 122.8775 | 122.7814 | 58.9828 | -122.937 | 122.8317 | 122.7127 | 59.0973 | -123.0286
646.0156 | 123.0469 | -59.024 | 63.8031 | 0.12192 | 0.0055265 | 0.066755 | 0.06774 | 0.13057 | -0.0017859 | -0.0025913 | 0.12955 | -0.0048536 | 0.062769 | 0.06103 | 0.0012176 | -0.0047104 | 63.7619 | 63.9267 | -0.054932 | -59.2209 | 63.8214 | -59.0652 | -59.1019 | -58.9554 | -0.009155 | -59.23 | 63.8306 | 63.7207 | -59.1476 | -59.2438 | -0.041199 | -0.07782 | 0.01831 | 122.9507 | -0.19684 | -0.11902 | -0.041199 | -0.1236 | -0.21973 | 0.027465 | 0.068665 | -0.20599 | 0.013732 | -0.082398 | 122.8455 | 122.7859 | 58.9691 | -122.905 | 122.8546 | 122.7448 | 59.0149 | -123.0469
647.0156 | 123.024 | -59.024 | 63.8672 | -0.24429 | 0.0083035 | 0.066755 | 0.07479 | 0.13398 | 0.0031273 | -0.0021641 | -0.20615 | -0.0027174 | 0.063623 | 0.060176 | 0.0022858 | -0.0074876 | 63.6063 | 63.9084 | -0.013733 | -59.2758 | 63.8901 | -59.0973 | -59.1614 | -58.992 | 0.045776 | -59.2941 | 63.9404 | 63.7894 | -59.1568 | -59.23 | -0.073242 | -0.13733 | 0.022889 | 122.9324 | -0.25177 | -0.11444 | -0.26093 | -0.13275 | -0.20599 | 0.073243 | 0.032044 | -0.27008 | -0.064086 | -0.077819 | 122.9141 | 122.6303 | 59.0103 | -123.0286 | 122.9645 | 122.8134 | 59.0698 | -123.0972
648.0156 | 123.1384 | -58.9966 | 63.8168 | 0.10666 | 0.0063809 | 0.067823 | 0.067526 | 0.12928 | -0.0030677 | -0.0034457 | 0.14481 | -0.0054944 | 0.060419 | 0.059962 | 0.0020722 | -0.003215 | 63.7573 | 63.8992 | -0.064087 | -59.2346 | 63.8168 | -59.0607 | -59.1202 | -58.9554 | 0.032043 | -59.2392 | 63.8306 | 63.7482 | -59.1522 | -59.2255 | -0.064087 | -0.1236 | 0 | 122.8958 | -0.23804 | -0.11444 | -0.059509 | -0.15564 | -0.22888 | 0.013733 | 0.041199 | -0.24262 | -0.013733 | -0.068664 | 122.8134 | 122.7539 | 58.9325 | -122.937 | 122.8271 | 122.7448 | 59.0286 | -123.0423
649.0156 | 123.111 | -59.0012 | 63.8123 | -0.091705 | 0.0063809 | 0.069746 | 0.068381 | 0.13035 | -0.0028541 | -0.0043003 | 0.015106 | -0.0052808 | 0.055933 | 0.060816 | 0.0024994 | -0.0053512 | 63.7985 | 63.9633 | 0 | -59.1797 | 63.8672 | -59.0652 | -59.1064 | -58.905 | 0.11444 | -59.1934 | 63.826 | 63.7482 | -59.1064 | -59.2209 | -0.064087 | -0.10529 | 0.054931 | 122.9645 | -0.17853 | -0.073242 | -0.013733 | -0.10529 | -0.21973 | 0.013733 | 0.096131 | -0.19226 | 0.027466 | -0.064087 | 122.8683 | 122.7997 | 59.0012 | -122.9187 | 122.8271 | 122.7493 | 59.1156 | -123.0331
650.0156 | 123.0789 | -59.0149 | 63.8077 | 0.12192 | 0.0044583 | 0.066328 | 0.071799 | 0.12928 | -7.6852e-05 | -0.0017369 | 0.19058 | -0.0059216 | 0.06341 | 0.062098 | 0.0012176 | -0.005565 | 63.7802 | 63.9359 | -0.045776 | -59.2117 | 63.8123 | -59.0698 | -59.1339 | -58.9554 | 0.004578 | -59.2484 | 63.8397 | 63.7253 | -59.1431 | -59.2163 | -0.054931 | -0.11902 | 0.004578 | 122.9507 | -0.19684 | -0.07782 | -0.027466 | -0.12817 | -0.20142 | 0.032044 | 0.05951 | -0.23346 | -0.032043 | -0.082397 | 122.8271 | 122.7951 | 58.9691 | -122.9416 | 122.8546 | 122.7402 | 59.0195 | -123.024
651.0156 | 123.0972 | -58.992 | 63.7939 | -0.00015269 | 0.0048855 | 0.06825 | 0.067954 | 0.13035 | -0.0015723 | -0.0043003 | 0.068512 | -0.006349 | 0.060419 | 0.062098 | 0.0031402 | -0.005565 | 63.7756 | 63.9267 | -0.036621 | -59.2163 | 63.8626 | -59.0652 | -59.1293 | -58.9371 | 0.073242 | -59.2072 | 63.8443 | 63.7253 | -59.1293 | -59.2255 | -0.073243 | -0.13733 | 0.068665 | 122.9187 | -0.22431 | -0.086976 | -0.01831 | -0.13733 | -0.23346 | 0.050354 | 0.054931 | -0.21515 | 0.018311 | -0.068664 | 122.8546 | 122.7676 | 58.9554 | -122.9233 | 122.8363 | 122.7173 | 59.0652 | -123.0194
652.0156 | 122.9965 | -59.0515 | 63.8672 | -0.22903 | 0.0068081 | 0.067823 | 0.070731 | 0.13057 | 0.00099115 | -0.0030185 | -0.25955 | -0.003999 | 0.063196 | 0.060389 | 0.004422 | -0.006633 | 63.7665 | 63.8763 | -0.036621 | -59.23 | 63.9175 | -59.0515 | -59.111 | -59.0698 | 0.12817 | -59.3399 | 63.9313 | 63.7894 | -59.1797 | -59.23 | 0 | -0.059509 | 0.050355 | 122.9279 | -0.17853 | -0.11902 | -0.10071 | -0.12817 | -0.17853 | 0.064087 | -0.01831 | -0.28839 | -0.10986 | -0.077819 | 122.9691 | 122.818 | 59.0149 | -122.9782 | 122.9828 | 122.8409 | 59.1797 | -123.0972
653.0156 | 123.0789 | -58.9966 | 63.8123 | 0.030365 | 0.0033901 | 0.069105 | 0.066458 | 0.12715 | -0.00093145 | -0.0034457 | 0.17532 | -0.0054944 | 0.061273 | 0.06103 | 0.0037812 | -0.0040696 | 63.826 | 63.9908 | 0.032043 | -59.2804 | 63.8672 | -59.0378 | -59.1293 | -58.96 | 0.022888 | -59.2255 | 63.826 | 63.7207 | -59.1431 | -59.2117 | -0.041199 | -0.13275 | 0.054931 | 122.9874 | -0.28381 | -0.15106 | 0.013733 | -0.14648 | -0.21515 | 0.013733 | 0.036621 | -0.22888 | -0.013733 | -0.091553 | 122.8638 | 122.8226 | 59.0286 | -122.9416 | 122.8226 | 122.7173 | 59.0195 | -123.024
654.0156 | 123.1705 | -59.0378 | 63.7848 | 0.54153 | 0.0097989 | 0.067182 | 0.070303 | 0.13206 | 0.0031273 | -0.00066866 | 0.19821 | -0.0054944 | 0.062342 | 0.059748 | 0.0033538 | -0.0072738 | 63.8168 | 63.9496 | -0.032043 | -59.1888 | 63.826 | -59.0744 | -59.1248 | -58.9279 | 0.032043 | -59.23 | 63.8168 | 63.7161 | -59.1797 | -59.2575 | -0.036621 | -0.086975 | 0.041199 | 122.9874 | -0.15106 | -0.064087 | 0.032043 | -0.14191 | -0.21973 | 0.032043 | 0.10986 | -0.19226 | 0.027465 | -0.068665 | 122.8638 | 122.8546 | 59.0057 | -122.9095 | 122.8546 | 122.7539 | 59.0698 | -123.0423
655.0156 | 123.111 | -58.9874 | 63.7894 | 0.076141 | 0.0053129 | 0.067396 | 0.067313 | 0.128 | -0.0047767 | -0.0053683 | 0.09903 | -0.007417 | 0.059351 | 0.061885 | 0.0029266 | -0.003215 | 63.7573 | 63.9084 | -0.027466 | -59.198 | 63.8672 | -59.0424 | -59.1431 | -58.9508 | 0.073242 | -59.2026 | 63.8397 | 63.7527 | -59.1293 | -59.2255 | -0.054931 | -0.15564 | 0.077819 | 122.8958 | -0.21057 | -0.054932 | -0.032044 | -0.14191 | -0.23804 | 0.050354 | 0.036621 | -0.21515 | 0.022888 | -0.036621 | 122.8546 | 122.7448 | 58.96 | -122.9324 | 122.8271 | 122.7402 | 59.0607 | -123.0148
656.0156 | 123.0789 | -59.0057 | 63.7802 | 0.19058 | 0.0074491 | 0.068464 | 0.070303 | 0.1295 | -0.0015723 | -0.0023777 | 0.20584 | -0.0054944 | 0.062555 | 0.059748 | 0.0024994 | -0.0064194 | 63.8077 | 63.9404 | -0.036621 | -59.2072 | 63.8123 | -59.0561 | -59.1019 | -58.9233 | 0.027466 | -59.2255 | 63.8168 | 63.7024 | -59.1614 | -59.2209 | -0.050354 | -0.096131 | 0.032044 | 122.9462 | -0.20142 | -0.10528 | 0.027466 | -0.15564 | -0.21515 | 0.036621 | 0.082397 | -0.21973 | -0.004578 | -0.077819 | 122.818 | 122.8134 | 58.9691 | -122.8821 | 122.8226 | 122.7081 | 59.0332 | -123.0011
657.0156 | 123.0515 | -59.0149 | 63.8489 | -0.22141 | 0.010013 | 0.068037 | 0.07009 | 0.13228 | 0.0039819 | -0.00045506 | -0.24429 | -0.005708 | 0.064905 | 0.059107 | 0.0031402 | -0.0094102 | 63.7756 | 63.8626 | -0.036621 | -59.198 | 63.9404 | -59.0424 | -59.0881 | -58.9691 | 0.073242 | -59.2529 | 63.9267 | 63.8031 | -59.1293 | -59.23 | -0.027465 | -0.073242 | 0.091553 | 122.8775 | -0.1831 | -0.10986 | -0.073242 | -0.11444 | -0.21515 | 0.07782 | 0.045777 | -0.23804 | -0.022888 | -0.045776 | 122.9553 | 122.7905 | 58.9783 | -122.937 | 122.9416 | 122.818 | 59.0881 | -123.0789
658.0156 | 123.1064 | -59.0149 | 63.7848 | 0.38895 | 0.0097989 | 0.066114 | 0.067526 | 0.13228 | -0.0013587 | -0.0013095 | 0.16006 | -0.006349 | 0.062555 | 0.060603 | 0.0033538 | -0.0059922 | 63.8214 | 63.945 | -0.032043 | -59.2209 | 63.8168 | -59.0836 | -59.1248 | -58.9279 | 0.045776 | -59.2117 | 63.8214 | 63.7161 | -59.1522 | -59.2117 | -0.068664 | -0.10986 | 0.032043 | 122.9599 | -0.20599 | -0.09613 | 0.036621 | -0.13733 | -0.19684 | 0.036621 | 0.086976 | -0.19684 | 0 | -0.068665 | 122.8317 | 122.8363 | 58.9828 | -122.9095 | 122.8363 | 122.731 | 59.0607 | -122.9965
659.0156 | 123.0835 | -59.0057 | 63.7802 | 0.12192 | 0.0025357 | 0.068037 | 0.069449 | 0.12928 | -0.0011451 | -0.0034457 | 0.11429 | -0.0054944 | 0.060633 | 0.06103 | 0.0029266 | -0.0025742 | 63.7848 | 63.8763 | -0.064087 | -59.2392 | 63.8535 | -59.0561 | -59.1339 | -58.9737 | 0.045776 | -59.2438 | 63.8123 | 63.7299 | -59.1248 | -59.2255 | -0.050354 | -0.12817 | 0.073243 | 122.8821 | -0.23346 | -0.10529 | 0.004578 | -0.11902 | -0.21973 | 0.032044 | 0.032043 | -0.23804 | -0.01831 | -0.050354 | 122.8592 | 122.7905 | 58.9417 | -122.9141 | 122.818 | 122.7356 | 59.0515 | -123.0057
660.0156 | 123.1384 | -59.0012 | 63.7711 | 0.2211 | 0.0097989 | 0.064405 | 0.069449 | 0.12971 | -7.6852e-05 | -2.7856e-05 | 0.21347 | -0.0042126 | 0.064264 | 0.061885 | 0.0039948 | -0.0077012 | 63.8123 | 63.9221 | -0.036621 | -59.1751 | 63.8214 | -59.079 | -59.1339 | -58.8318 | 0.10986 | -59.2163 | 63.8306 | 63.7299 | -59.1522 | -59.2117 | -0.077819 | -0.13275 | 0.050354 | 122.9233 | -0.17395 | -0.041199 | 0.041199 | -0.15106 | -0.21057 | 0.059509 | 0.16937 | -0.21515 | -0.004578 | -0.041199 | 122.8226 | 122.8134 | 58.9645 | -122.905 | 122.8317 | 122.731 | 59.111 | -122.9828
661.0156 | 123.0927 | -58.9874 | 63.7756 | -0.24429 | 0.0097989 | 0.067823 | 0.068381 | 0.13228 | -0.00093145 | -0.0023777 | 0.19821 | -0.0037854 | 0.061273 | 0.058894 | 0.0048492 | -0.004924 | 63.8031 | 63.9496 | -0.032043 | -59.2026 | 63.8214 | -59.0836 | -59.1202 | -58.9325 | 0.050354 | -59.2209 | 63.8351 | 63.7207 | -59.1385 | -59.2255 | -0.09613 | -0.13275 | 0.045776 | 122.937 | -0.21515 | -0.082398 | 0.027466 | -0.15106 | -0.23804 | 0.059509 | 0.054932 | -0.23346 | 0.004578 | -0.054932 | 122.8088 | 122.7905 | 58.9554 | -122.8958 | 122.8226 | 122.7081 | 59.0378 | -123.0011
662.0156 | 123.1247 | -59.0378 | 63.7619 | 0.21347 | 0.0074491 | 0.065687 | 0.066458 | 0.12993 | 0.0041955 | -0.0040867 | -0.023041 | -0.0054944 | 0.063623 | 0.059962 | 0.0029266 | -0.0074876 | 63.8626 | 64.0045 | -0.004578 | -59.2026 | 63.826 | -59.0561 | -59.1248 | -58.9233 | 0.050354 | -59.2072 | 63.8168 | 63.7161 | -59.1705 | -59.2255 | -0.01831 | -0.086975 | 0.064087 | 123.0423 | -0.16479 | -0.07782 | 0.10071 | -0.13275 | -0.18768 | 0.054931 | 0.11444 | -0.16937 | 0.018311 | -0.045777 | 122.8638 | 122.9004 | 59.0332 | -122.8867 | 122.8546 | 122.7539 | 59.0881 | -122.9874
663.0156 | 123.0652 | -59.0103 | 63.8031 | 0.12955 | 0.0044583 | 0.068464 | 0.069876 | 0.13014 | -0.0015723 | -0.0017369 | 0.17532 | -0.005708 | 0.062342 | 0.06103 | 0.00079042 | -0.004924 | 63.7756 | 63.8947 | -0.064087 | -59.2163 | 63.8123 | -59.0469 | -59.1431 | -58.9554 | -0.004578 | -59.2392 | 63.826 | 63.7527 | -59.1339 | -59.2484 | -0.036621 | -0.13275 | 0.009155 | 122.905 | -0.20599 | -0.073243 | -0.027466 | -0.1236 | -0.23804 | 0.022888 | 0.054932 | -0.22888 | 0.009155 | -0.050354 | 122.8226 | 122.7859 | 58.9462 | -122.9462 | 122.8363 | 122.7631 | 59.0057 | -123.0515
664.0156 | 123.1338 | -59.0469 | 63.7253 | 0.22873 | 0.010653 | 0.067823 | 0.068594 | 0.13142 | 0.0022729 | -0.0015231 | 0.20584 | -0.0054944 | 0.060633 | 0.059107 | 0.0024994 | -0.0068466 | 63.8214 | 63.9221 | -0.041199 | -59.1888 | 63.8351 | -59.0561 | -59.1431 | -58.9371 | 0.032043 | -59.2346 | 63.8306 | 63.7253 | -59.1568 | -59.2255 | -0.009155 | -0.09613 | 0.10986 | 122.9691 | -0.14191 | -0.045777 | 0.09613 | -0.10986 | -0.17853 | 0.10528 | 0.10986 | -0.18768 | -0.009155 | 0 | 122.8821 | 122.8683 | 59.0057 | -122.8683 | 122.8775 | 122.7722 | 59.079 | -122.9507
665.0156 | 123.0835 | -59.0103 | 63.7802 | 0.083771 | 0.0053129 | 0.06526 | 0.070303 | 0.12864 | -0.00050425 | -0.0015231 | 0.22873 | -0.00464 | 0.060633 | 0.061457 | 0.0037812 | -0.0068466 | 63.8168 | 63.9313 | -0.022888 | -59.2163 | 63.8168 | -59.079 | -59.1522 | -58.9417 | 0.036621 | -59.2163 | 63.8123 | 63.739 | -59.1568 | -59.2529 | -0.068664 | -0.14191 | 0.036621 | 122.9416 | -0.20599 | -0.064087 | 0.036621 | -0.14648 | -0.24262 | 0.032044 | 0.068665 | -0.20599 | 0.036621 | -0.041198 | 122.8271 | 122.8271 | 58.9874 | -122.9324 | 122.8226 | 122.7493 | 59.0469 | -123.0331
666.0156 | 123.0789 | -59.024 | 63.7573 | 0.19058 | 0.010653 | 0.06825 | 0.069663 | 0.13078 | 0.0016321 | -0.0028049 | 0.21347 | -0.0044264 | 0.06341 | 0.061457 | 0.0037812 | -0.004924 | 63.7802 | 63.8443 | -0.10986 | -59.2438 | 63.8718 | -59.0973 | -59.1202 | -58.9508 | -0.018311 | -59.2575 | 63.8351 | 63.7527 | -59.1705 | -59.2438 | -0.073242 | -0.09613 | 0.11444 | 122.8683 | -0.21973 | -0.1236 | 0.022888 | -0.14648 | -0.21973 | 0.07782 | 0.073242 | -0.23346 | -0.013733 | -0.004577 | 122.8958 | 122.8043 | 58.9142 | -122.8775 | 122.8592 | 122.7768 | 59.0057 | -123.0011
667.0156 | 123.0652 | -58.9966 | 63.7985 | -0.03067 | 0.0044583 | 0.069105 | 0.066885 | 0.12864 | -0.0037085 | -0.0028049 | 0.16006 | -0.0054944 | 0.06106 | 0.062525 | 0.0016448 | -0.0053512 | 63.7665 | 63.8901 | -0.032043 | -59.2209 | 63.8306 | -59.0652 | -59.1385 | -58.9783 | 0.091553 | -59.111 | 63.8718 | 63.7802 | -59.1293 | -59.2209 | -0.068665 | -0.14191 | 0.032043 | 122.8867 | -0.2243 | -0.082397 | -0.032044 | -0.13275 | -0.2243 | 0.073242 | 0.018311 | -0.11444 | 0.10986 | -0.018311 | 122.8271 | 122.7631 | 58.9645 | -122.937 | 122.8683 | 122.7768 | 59.0881 | -123.0194
668.0156 | 122.9874 | -59.0515 | 63.8397 | 0.083771 | 0.013003 | 0.068037 | 0.069235 | 0.13035 | 0.0044091 | -0.0021641 | 1.8614 | -0.00229 | 0.062769 | 0.059321 | 0.0086944 | -0.0053512 | 63.7115 | 63.7756 | -0.14648 | -59.2712 | 63.8672 | -59.1064 | -59.1476 | -59.1156 | 0.018311 | -59.2804 | 63.8992 | 63.7894 | -59.1934 | -59.2438 | -0.054931 | -0.09613 | 0.027465 | 122.8271 | -0.21973 | -0.1236 | -0.12817 | -0.14191 | -0.19226 | 0.059509 | -0.064087 | -0.22888 | -0.036622 | -0.050354 | 122.9187 | 122.7631 | 58.905 | -122.9874 | 122.9507 | 122.8409 | 59.0698 | -123.0835
669.0156 | 123.1247 | -58.9874 | 63.7939 | 0.25925 | 0.0087307 | 0.065901 | 0.067313 | 0.13078 | 0.00013675 | -0.0032321 | 0.23636 | -0.0048536 | 0.062342 | 0.06103 | 0.0037812 | -0.0044968 | 63.826 | 63.913 | -0.050354 | -59.1797 | 63.8123 | -59.0698 | -59.1476 | -59.0515 | -0.13275 | -59.0744 | 63.8031 | 63.7115 | -59.1751 | -59.2117 | -0.082397 | -0.16022 | 0.018311 | 122.9004 | -0.19226 | -0.032043 | 0.032044 | -0.18768 | -0.2243 | 0.009156 | -0.064087 | -0.086975 | 0.13733 | -0.082397 | 122.7997 | 122.8134 | 58.9371 | -122.9416 | 122.7905 | 122.699 | 58.8547 | -123.0057
670.0156 | 123.0606 | -59.0332 | 63.7894 | 0.17532 | 0.013217 | 0.066114 | 0.071158 | 0.13099 | 0.00099115 | -2.7856e-05 | 0.19058 | -0.0037854 | 0.063837 | 0.061671 | 0.0046356 | -0.0051376 | 63.739 | 63.8077 | -0.13275 | -59.2621 | 63.8718 | -59.0973 | -59.1476 | -58.992 | -0.054932 | -59.2896 | 63.8443 | 63.7436 | -59.1614 | -59.2575 | -0.064087 | -0.11444 | 0.082397 | 122.8409 | -0.22888 | -0.11444 | -0.050354 | -0.12817 | -0.2243 | 0.054931 | 0.041199 | -0.25635 | -0.032044 | -0.045777 | 122.905 | 122.7722 | 58.9005 | -122.937 | 122.8775 | 122.7768 | 58.9783 | -123.0469
671.0156 | 123.1247 | -59.0195 | 63.7756 | 0.22873 | 0.0076627 | 0.067396 | 0.069876 | 0.13292 | -7.6852e-05 | -0.0023777 | 0.3508 | -0.0059216 | 0.061487 | 0.06103 | 0.0046356 | -0.006633 | 63.8031 | 63.9267 | -0.041199 | -59.166 | 63.8489 | -59.0836 | -59.1476 | -58.9508 | 0.07782 | -59.198 | 63.8214 | 63.7436 | -59.1431 | -59.2392 | -0.064087 | -0.12817 | 0.073242 | 122.9462 | -0.14648 | -0.018311 | 0.027466 | -0.1236 | -0.21973 | 0.045776 | 0.068664 | -0.17853 | 0.041199 | -0.032044 | 122.8683 | 122.8226 | 58.9783 | -122.9233 | 122.8409 | 122.7631 | 59.0973 | -123.0148
672.0156 | 123.0194 | -59.0652 | 63.8031 | 0.52628 | 0.014071 | 0.066328 | 0.070944 | 0.13035 | 0.0029137 | -0.0013095 | 0.09903 | -0.0031446 | 0.061273 | 0.060603 | 0.0052764 | -0.0059922 | 63.7527 | 63.7939 | -0.14648 | -59.285 | 63.8718 | -59.1019 | -59.1476 | -59.024 | -0.082397 | -59.3216 | 63.8763 | 63.7985 | -59.1568 | -59.2438 | -0.036621 | -0.082397 | 0.068664 | 122.8592 | -0.21973 | -0.13733 | -0.050354 | -0.091552 | -0.17853 | 0.073242 | 0.041199 | -0.25635 | -0.07782 | -0.004578 | 122.937 | 122.818 | 58.9188 | -122.9507 | 122.9416 | 122.8638 | 58.9828 | -123.0469
673.0156 | 123.0881 | -59.0012 | 63.7711 | 0.16769 | 0.011508 | 0.067396 | 0.068167 | 0.13099 | -0.00029045 | -0.00024146 | 0.29739 | -0.0050672 | 0.061273 | 0.05868 | 0.0018584 | -0.0059922 | 63.7894 | 63.913 | -0.050354 | -59.2209 | 63.8351 | -59.0698 | -59.1476 | -58.9371 | 0.032043 | -59.2163 | 63.8306 | 63.739 | -59.1934 | -59.23 | -0.068664 | -0.14648 | 0.064087 | 122.9141 | -0.21973 | -0.073242 | 0.018311 | -0.19226 | -0.22888 | 0.059509 | 0.064087 | -0.21515 | 0.013733 | -0.032043 | 122.8363 | 122.7905 | 58.9508 | -122.9187 | 122.8317 | 122.7402 | 59.0332 | -123.0011
674.0156 | 122.9965 | -59.0332 | 63.8214 | -0.00015269 | 0.013644 | 0.065901 | 0.070303 | 0.13206 | 0.00056395 | -0.0021641 | 0.030365 | -0.0035718 | 0.062982 | 0.060816 | 0.0046356 | -0.005565 | 63.7344 | 63.8351 | -0.09613 | -59.2346 | 63.8809 | -59.0744 | -59.1568 | -59.024 | -0.018311 | -59.3308 | 63.8672 | 63.8031 | -59.1705 | -59.2575 | -0.041199 | -0.1236 | 0.059509 | 122.8683 | -0.20142 | -0.07782 | -0.086975 | -0.13733 | -0.2243 | 0.045776 | 0.009155 | -0.29755 | -0.073243 | -0.01831 | 122.9141 | 122.7676 | 58.9371 | -122.9782 | 122.9004 | 122.8363 | 59.0149 | -123.0789
675.0156 | 123.0011 | -59.0698 | 63.8077 | -0.35873 | 0.012576 | 0.066541 | 0.072226 | 0.12822 | 0.00013675 | -0.00088226 | 0.12955 | -0.003999 | 0.0664 | 0.060176 | 0.0052764 | -0.0027878 | 63.6978 | 63.8123 | -0.13275 | -59.2667 | 63.8809 | -59.0927 | -59.1568 | -59.0332 | -0.073242 | -59.317 | 63.8626 | 63.7848 | -59.1614 | -59.2575 | -0.022888 | -0.086975 | 0.073242 | 122.8821 | -0.19684 | -0.10986 | -0.10986 | -0.091553 | -0.18768 | 0.054932 | 0.036621 | -0.24719 | -0.05951 | -0.022888 | 122.9507 | 122.7676 | 58.9371 | -122.9645 | 122.9324 | 122.8546 | 58.9966 | -123.0652
676.0156 | 122.9828 | -59.024 | 63.8214 | 0.11429 | 0.012576 | 0.068678 | 0.070303 | 0.13163 | -0.00029045 | -0.00066866 | 0.47287 | -0.00229 | 0.067041 | 0.061671 | 0.0037812 | -0.0036424 | 63.3865 | 63.7985 | -0.027466 | -59.111 | 63.8901 | -59.0744 | -59.1339 | -59.0652 | -0.054932 | -59.3308 | 63.8718 | 63.7939 | -59.1705 | -59.2621 | -0.050354 | -0.10986 | 0.068665 | 122.8226 | -0.086975 | 0.022888 | -0.43487 | -0.14648 | -0.23804 | 0.050354 | -0.041199 | -0.3067 | -0.068665 | -0.027466 | 122.9141 | 122.4106 | 58.9966 | -122.9553 | 122.8958 | 122.818 | 58.9691 | -123.0835
677.0156 | 123.1338 | -59.0195 | 63.7848 | 0.19821 | 0.0089443 | 0.066328 | 0.068594 | 0.13334 | -0.0030677 | -0.0019505 | 0.24399 | -0.0052808 | 0.066187 | 0.060603 | 0.004422 | -0.0036424 | 63.7527 | 63.858 | -0.091553 | -59.23 | 63.8214 | -59.0652 | -59.1431 | -58.9645 | 0.045776 | -59.2438 | 63.8168 | 63.7573 | -59.1431 | -59.2117 | -0.045777 | -0.1236 | 0.036621 | 122.8775 | -0.21057 | -0.086976 | -0.032043 | -0.1236 | -0.19226 | 0.032043 | 0.054931 | -0.2243 | -0.032043 | -0.027466 | 122.8409 | 122.7722 | 58.9279 | -122.9279 | 122.8363 | 122.7768 | 59.0652 | -122.9965
678.0156 | 122.9782 | -59.0652 | 63.7939 | 0.12192 | 0.011722 | 0.067182 | 0.068594 | 0.13078 | 0.0014185 | -0.0030185 | 0.12955 | -0.0025038 | 0.065119 | 0.059748 | 0.0039948 | -0.0042832 | 63.7161 | 63.7573 | -0.15106 | -59.2804 | 63.8672 | -59.0698 | -59.1751 | -59.0561 | -0.082397 | -59.3308 | 63.8626 | 63.8031 | -59.1888 | -59.2667 | -0.004577 | -0.10986 | 0.073242 | 122.8226 | -0.21515 | -0.10529 | -0.07782 | -0.1236 | -0.20142 | 0.068665 | 0.009156 | -0.2655 | -0.064087 | 0.009156 | 122.9324 | 122.7814 | 58.9142 | -122.9691 | 122.9279 | 122.8683 | 58.9828 | -123.0606
679.0156 | 123.0652 | -59.0378 | 63.7894 | 0.14481 | 0.0091581 | 0.069105 | 0.070303 | 0.12886 | -0.00071785 | 0.00039954 | 0.2211 | -0.0059216 | 0.064478 | 0.061244 | 0.0031402 | -0.0059922 | 63.7344 | 63.8168 | -0.11902 | -59.2575 | 63.8443 | -59.0698 | -59.1751 | -58.9874 | -0.041199 | -59.2712 | 63.8535 | 63.7619 | -59.1751 | -59.2392 | -0.032043 | -0.13733 | 0.054931 | 122.8546 | -0.21973 | -0.082397 | -0.054932 | -0.13733 | -0.20142 | 0.064087 | 0.050354 | -0.23346 | -0.032043 | -0.027466 | 122.8821 | 122.7722 | 58.9188 | -122.9645 | 122.8912 | 122.7997 | 58.9966 | -123.0286
680.0156 | 123.0011 | -59.0698 | 63.826 | -0.015411 | 0.011935 | 0.066541 | 0.068808 | 0.13035 | 0.00035035 | -0.0021641 | 0.12955 | -0.0037854 | 0.063837 | 0.062098 | 0.0033538 | -0.0059922 | 63.7344 | 63.7985 | -0.10986 | -59.2575 | 63.8855 | -59.0744 | -59.1614 | -59.0744 | -0.073242 | -59.3491 | 63.8809 | 63.8123 | -59.1705 | -59.2896 | -0.004578 | -0.091553 | 0.059509 | 122.8683 | -0.18768 | -0.09613 | -0.091553 | -0.10071 | -0.21973 | 0.054931 | -0.004578 | -0.27924 | -0.059509 | -0.013733 | 122.9553 | 122.8043 | 58.96 | -122.9874 | 122.9507 | 122.8821 | 58.9966 | -123.1155
681.0156 | 123.0331 | -59.0424 | 63.8031 | 0.19821 | 0.01044 | 0.06825 | 0.069876 | 0.13035 | 0.00056395 | -0.00088226 | 0.23636 | -0.002931 | 0.063196 | 0.060603 | 0.0039948 | -0.0027878 | 63.707 | 63.7802 | -0.14191 | -59.2667 | 63.8535 | -59.079 | -59.1431 | -59.0378 | -0.059509 | -59.3124 | 63.8626 | 63.7939 | -59.1888 | -59.2484 | -0.036621 | -0.10071 | 0.050354 | 122.8226 | -0.22431 | -0.1236 | -0.096131 | -0.14648 | -0.20599 | 0.059509 | 0.004577 | -0.27008 | -0.064087 | -0.009156 | 122.8958 | 122.7493 | 58.9005 | -122.9462 | 122.905 | 122.8363 | 58.9828 | -123.0515
682.0156 | 123.0011 | -59.0515 | 63.8397 | 0.022736 | 0.014926 | 0.067182 | 0.073935 | 0.13099 | 0.0012047 | -0.0019505 | -0.023041 | -0.0052808 | 0.064905 | 0.060816 | 0.0037812 | -0.005565 | 63.8306 | 63.8718 | -0.027466 | -59.2163 | 63.8992 | -59.0515 | -59.1568 | -58.9874 | 0.059509 | -59.2712 | 63.8626 | 63.8123 | -59.1293 | -59.23 | 0 | -0.10529 | 0.059509 | 122.9233 | -0.1648 | -0.05951 | -0.009156 | -0.077819 | -0.17853 | 0.022888 | 0.064087 | -0.21973 | -0.041198 | -0.027466 | 122.9507 | 122.8821 | 59.024 | -122.9965 | 122.9141 | 122.8638 | 59.111 | -123.0698
683.0156 | 123.0515 | -59.024 | 63.8031 | 0.15244 | 0.010226 | 0.066328 | 0.066245 | 0.12693 | -0.0013587 | -0.0032321 | 0.21347 | -0.0035718 | 0.064691 | 0.058467 | 0.0031402 | -0.0042832 | 63.7344 | 63.8031 | -0.13275 | -59.2621 | 63.8535 | -59.079 | -59.1614 | -59.0012 | -0.027466 | -59.2667 | 63.8397 | 63.7711 | -59.166 | -59.23 | -0.054931 | -0.13733 | 0.050354 | 122.8271 | -0.23804 | -0.10071 | -0.068665 | -0.14191 | -0.20599 | 0.036621 | 0.022888 | -0.24262 | -0.036621 | -0.032044 | 122.8775 | 122.7585 | 58.8913 | -122.9645 | 122.8638 | 122.7951 | 58.9966 | -123.0331
684.0156 | 122.9645 | -59.0561 | 63.8168 | 0.045624 | 0.011722 | 0.065687 | 0.071372 | 0.13035 | -0.00029045 | -0.0036595 | 0.0074766 | -0.0031446 | 0.06341 | 0.059535 | 0.0033538 | -0.0036424 | 63.7436 | 63.8077 | -0.10986 | -59.23 | 63.8855 | -59.0744 | -59.1568 | -59.0652 | -0.073242 | -59.3536 | 63.8855 | 63.8123 | -59.1797 | -59.2712 | -0.018311 | -0.10071 | 0.068665 | 122.8638 | -0.17395 | -0.073243 | -0.073242 | -0.1236 | -0.21515 | 0.068665 | -0.009156 | -0.29755 | -0.082398 | -0.004577 | 122.9416 | 122.7997 | 58.9462 | -122.9736 | 122.9416 | 122.8683 | 58.9828 | -123.0881
685.0156 | 123.0148 | -59.024 | 63.8168 | 0.30502 | 0.010013 | 0.06825 | 0.069663 | 0.13057 | 0.00035035 | -0.0034457 | 0.2211 | -0.0031446 | 0.065546 | 0.061671 | 0.0022858 | -0.0012924 | 63.7161 | 63.7848 | -0.14191 | -59.2621 | 63.8855 | -59.0973 | -59.1293 | -59.0378 | -0.068665 | -59.2987 | 63.8855 | 63.8031 | -59.166 | -59.2712 | -0.073242 | -0.10529 | 0.068665 | 122.8088 | -0.23804 | -0.13275 | -0.10071 | -0.14191 | -0.24719 | 0.068665 | -0.013733 | -0.27466 | -0.027466 | -0.013732 | 122.9095 | 122.7402 | 58.8821 | -122.9462 | 122.9095 | 122.8271 | 58.9554 | -123.0881
686.0156 | 122.9691 | -59.0561 | 63.8397 | 0.022736 | 0.012362 | 0.068037 | 0.072012 | 0.13035 | 0.00077755 | -0.0013095 | 0.068512 | -0.0031446 | 0.063837 | 0.059321 | 0.004422 | -0.0042832 | 63.7527 | 63.8214 | -0.091553 | -59.2346 | 63.8626 | -59.0652 | -59.166 | -59.0378 | -0.009155 | -59.3124 | 63.8718 | 63.8214 | -59.1797 | -59.2529 | -0.009156 | -0.10986 | 0.022888 | 122.8775 | -0.17853 | -0.068664 | -0.086975 | -0.1236 | -0.19684 | 0.032043 | 0.01831 | -0.25635 | -0.059509 | -0.018311 | 122.9187 | 122.8088 | 58.9645 | -123.0057 | 122.9279 | 122.8775 | 59.0469 | -123.0927
687.0156 | 122.9965 | -59.079 | 63.8306 | 0.12192 | 0.010867 | 0.066969 | 0.068808 | 0.13185 | 0.00013675 | -0.0057957 | 0.29739 | -0.0033582 | 0.064905 | 0.06103 | 0.004422 | -0.0047104 | 63.6978 | 63.533 | -0.29297 | -59.0652 | 63.8672 | -59.0744 | -59.1248 | -59.0652 | -0.082397 | -59.3124 | 63.8901 | 63.8351 | -59.1888 | -59.2758 | 0.004577 | -0.045777 | 0.036621 | 122.612 | 0.013732 | 0.059509 | -0.13275 | -0.10986 | -0.19684 | 0.05951 | 0.013732 | -0.23346 | -0.036621 | 0.004578 | 122.9462 | 122.7768 | 58.786 | -122.9553 | 122.9691 | 122.9141 | 58.9966 | -123.1064
688.0156 | 123.0469 | -59.0561 | 63.8123 | -0.084076 | 0.011935 | 0.067396 | 0.075644 | 0.13142 | -0.0019995 | -0.0023777 | -0.015411 | -0.0033582 | 0.065973 | 0.059107 | 0.0012176 | -0.0036424 | 63.7756 | 63.8855 | -0.027466 | -59.198 | 63.8855 | -59.0698 | -59.111 | -58.9828 | 0.068665 | -59.2667 | 63.8901 | 63.8443 | -59.1751 | -59.2758 | -0.013733 | -0.054932 | 0.073242 | 122.9416 | -0.14191 | -0.086975 | -0.036621 | -0.11902 | -0.21973 | 0.07782 | 0.073242 | -0.21057 | 0.009155 | 0.032043 | 122.9416 | 122.8317 | 59.0286 | -122.9233 | 122.9462 | 122.9004 | 59.1248 | -123.0881
689.0156 | 122.8958 | -59.0561 | 63.7344 | 0.0914 | 0.010653 | 0.069319 | 0.070303 | 0.13185 | 0.00099115 | -0.0019505 | 0.16769 | -0.0048536 | 0.064051 | 0.061671 | 0.0050628 | -0.0047104 | 63.6887 | 63.7619 | -0.15106 | -59.2712 | 63.8626 | -59.0927 | -59.1568 | -59.0652 | -0.09613 | -59.3491 | 63.8443 | 63.7894 | -59.198 | -59.2575 | -0.036621 | -0.10071 | 0.12817 | 122.818 | -0.21515 | -0.11444 | -0.045776 | -0.14191 | -0.20142 | 0.10986 | -0.009156 | -0.29297 | -0.091553 | 0.054932 | 122.9187 | 122.7448 | 58.905 | -122.8912 | 122.9004 | 122.8455 | 58.96 | -122.9919
690.0156 | 123.0194 | -59.0286 | 63.826 | -0.00015269 | 0.014712 | 0.064405 | 0.070944 | 0.13163 | -0.0015723 | -0.0036595 | 0.045624 | -0.0025038 | 0.062128 | 0.061885 | 0.0039948 | -0.0053512 | 63.7665 | 63.8443 | -0.082397 | -59.23 | 63.8626 | -59.0561 | -59.1385 | -59.0286 | -0.009155 | -59.317 | 63.8718 | 63.7939 | -59.1568 | -59.2529 | -0.027466 | -0.10986 | 0.036621 | 122.8729 | -0.20142 | -0.091553 | -0.05951 | -0.12817 | -0.22431 | 0.045776 | 0 | -0.28839 | -0.064087 | -0.032044 | 122.8912 | 122.7951 | 58.9462 | -122.9645 | 122.9004 | 122.8226 | 59.0195 | -123.0789
691.0156 | 123.0103 | -59.0469 | 63.8214 | 0.14481 | 0.010867 | 0.066969 | 0.069235 | 0.13078 | 0.00099115 | -0.0021641 | -1.9838 | -0.005708 | 0.064264 | 0.061244 | 0.0014312 | -0.0059922 | 63.6932 | 63.7985 | -0.15106 | -59.2758 | 63.858 | -59.1202 | -59.198 | -59.0424 | -0.11902 | -59.3033 | 63.8718 | 63.8306 | -59.1614 | -59.2438 | -0.073242 | -0.15106 | 0.036621 | 122.8455 | -0.22888 | -0.07782 | -0.12817 | -0.11444 | -0.19684 | 0.050354 | 0.004578 | -0.25635 | -0.05951 | 0.009155 | 122.905 | 122.7402 | 58.8959 | -123.0194 | 122.9187 | 122.8775 | 58.9279 | -123.0652
692.0156 | 123.0194 | -59.0469 | 63.8306 | 0.083771 | 0.01279 | 0.065687 | 0.068808 | 0.13014 | 0.00077755 | -0.0030185 | -0.00015237 | -0.00229 | 0.065759 | 0.061671 | 0.0033538 | -0.0053512 | 63.7894 | 63.8672 | -0.022888 | -59.2117 | 63.8626 | -59.0469 | -59.1385 | -59.0149 | 0.022888 | -59.285 | 63.8855 | 63.8077 | -59.1614 | -59.2346 | 0 | -0.091553 | 0.032044 | 122.9141 | -0.16479 | -0.073242 | -0.041198 | -0.11444 | -0.18768 | 0.054932 | 0.032043 | -0.23804 | -0.050354 | -0.022888 | 122.9095 | 122.8363 | 59.024 | -122.9691 | 122.9324 | 122.8546 | 59.0698 | -123.0652
693.0156 | 122.9599 | -59.0561 | 63.7802 | -0.03067 | 0.013003 | 0.06761 | 0.070517 | 0.13078 | 0.0016321 | -0.0047275 | 0.12192 | -0.0027174 | 0.067682 | 0.061457 | 0.0012176 | -0.004924 | 63.6841 | 63.7573 | -0.13733 | -59.2667 | 63.8718 | -59.1019 | -59.1568 | -59.0836 | -0.082397 | -59.3216 | 63.8535 | 63.8214 | -59.2026 | -59.2484 | -0.045777 | -0.10071 | 0.091553 | 122.8134 | -0.21057 | -0.10986 | -0.09613 | -0.14648 | -0.19226 | 0.073243 | -0.027466 | -0.2655 | -0.073242 | 0.041199 | 122.9279 | 122.7402 | 58.9188 | -122.937 | 122.9095 | 122.8775 | 58.9737 | -123.0286
694.0156 | 123.024 | -59.024 | 63.8397 | -0.084076 | 0.011508 | 0.065687 | 0.069449 | 0.13121 | 0.00056395 | -0.0038731 | -0.023041 | -0.002931 | 0.064905 | 0.06103 | 0.0022858 | -0.003856 | 63.7848 | 63.8718 | -0.032043 | -59.3308 | 63.8397 | -59.0881 | -59.1476 | -58.9691 | 0.059509 | -59.2575 | 63.8672 | 63.858 | -59.1705 | -59.198 | -0.064087 | -0.1236 | 0 | 122.8958 | -0.3067 | -0.18311 | -0.054932 | -0.14648 | -0.17395 | 0.027465 | 0.054932 | -0.23346 | -0.059509 | 0.01831 | 122.8638 | 122.8088 | 58.992 | -122.9874 | 122.8912 | 122.8821 | 59.0836 | -123.0377
695.0156 | 123.024 | -59.0515 | 63.8168 | -0.076447 | 0.013003 | 0.066755 | 0.071799 | 0.13185 | -7.6852e-05 | -2.7856e-05 | 0.068512 | -0.0033582 | 0.062555 | 0.061671 | 0.0029266 | -0.0053512 | 63.7802 | 63.8626 | -0.050354 | -59.2255 | 63.8947 | -59.079 | -59.1385 | -59.0195 | 0.004578 | -59.2896 | 63.8763 | 63.8077 | -59.1797 | -59.2529 | -0.027465 | -0.086975 | 0.07782 | 122.9141 | -0.17395 | -0.086975 | -0.036621 | -0.12817 | -0.20142 | 0.05951 | 0.032044 | -0.23804 | -0.036621 | -0.009155 | 122.9462 | 122.8317 | 59.0012 | -122.9553 | 122.9279 | 122.8592 | 59.0561 | -123.0698
696.0156 | 122.9919 | -59.0195 | 63.858 | -0.11459 | 0.013217 | 0.065473 | 0.070303 | 0.12971 | -0.00050425 | -0.0032321 | -0.053558 | -0.0035718 | 0.064478 | 0.059962 | 0.0018584 | -0.0077012 | 63.7711 | 63.8763 | -0.018311 | -59.1888 | 63.8901 | -59.079 | -59.1385 | -58.9966 | 0.059509 | -59.3262 | 63.8535 | 63.7848 | -59.1751 | -59.2758 | -0.059509 | -0.11902 | 0.032044 | 122.8958 | -0.16937 | -0.050354 | -0.086975 | -0.15564 | -0.25635 | -0.004577 | 0.022888 | -0.3067 | -0.050354 | -0.073242 | 122.9095 | 122.7905 | 59.0012 | -122.9965 | 122.8729 | 122.8043 | 59.079 | -123.1338
697.0156 | 122.9645 | -59.0561 | 63.8672 | 0.16006 | 0.010653 | 0.065473 | 0.070517 | 0.12843 | -0.00071785 | -0.0053683 | 0.19058 | -0.0072034 | 0.063623 | 0.062953 | 0.0031402 | -0.0034286 | 63.6703 | 63.7527 | -0.15564 | -59.285 | 63.8947 | -59.0927 | -59.1522 | -59.0652 | -0.14648 | -59.6008 | 63.7894 | 63.7527 | -59.2392 | -59.2712 | -0.036621 | -0.096131 | 0.027466 | 122.8088 | -0.22888 | -0.13275 | -0.19684 | -0.18311 | -0.21515 | -0.077819 | -0.009156 | -0.54474 | -0.32959 | -0.11444 | 122.9507 | 122.7264 | 58.9005 | -123.0194 | 122.8455 | 122.8088 | 58.9096 | -123.1384
698.0156 | 123.0057 | -59.0149 | 63.8489 | -0.12222 | 0.013644 | 0.067396 | 0.07244 | 0.12928 | -0.00071785 | -0.0017369 | 0.045624 | -0.002931 | 0.0664 | 0.061671 | 0.0035674 | -0.0053512 | 63.8077 | 63.8718 | -0.041199 | -59.2117 | 63.8947 | -59.0424 | -59.1202 | -59.0103 | 0.041199 | -59.2712 | 63.858 | 63.8397 | -59.1522 | -59.2438 | -0.027465 | -0.10529 | 0.045776 | 122.8867 | -0.19684 | -0.091553 | -0.041199 | -0.13733 | -0.22888 | 0.009155 | 0.004578 | -0.25635 | -0.027466 | -0.009155 | 122.9095 | 122.8226 | 58.9737 | -122.9691 | 122.8729 | 122.8546 | 59.0561 | -123.0927
699.0156 | 123.0972 | -59.0515 | 63.7848 | 0.19821 | 0.013217 | 0.069105 | 0.070944 | 0.13313 | -0.0028541 | -0.0051547 | 0.26688 | -0.005708 | 0.06106 | 0.062098 | 0.0012176 | -0.0019334 | 63.707 | 63.7985 | -0.1236 | -59.2621 | 63.8443 | -59.0881 | -59.1431 | -59.0057 | -0.036621 | -59.285 | 63.8672 | 63.7756 | -59.1614 | -59.2392 | -0.036621 | -0.091552 | 0.059509 | 122.85 | -0.21057 | -0.11902 | -0.07782 | -0.10986 | -0.18768 | 0.082397 | 0.045777 | -0.23346 | -0.045776 | -0.009155 | 122.8958 | 122.7585 | 58.9279 | -122.9279 | 122.9187 | 122.8271 | 59.0149 | -123.024
700.0156 | 122.9553 | -59.0698 | 63.8351 | 0.076141 | 0.012149 | 0.067396 | 0.070303 | 0.13121 | 0.0018457 | -0.0034457 | 0.053253 | -0.0037854 | 0.064478 | 0.062312 | 0.0020722 | -0.0053512 | 63.7344 | 63.7985 | -0.1236 | -59.2484 | 63.8809 | -59.0652 | -59.1476 | -59.0881 | -0.054932 | -59.3536 | 63.8809 | 63.826 | -59.1614 | -59.2804 | 0.004577 | -0.07782 | 0.045776 | 122.8683 | -0.17853 | -0.10071 | -0.10071 | -0.091553 | -0.21057 | 0.045776 | -0.018311 | -0.28381 | -0.073242 | -0.009155 | 122.9507 | 122.8043 | 58.9462 | -122.9828 | 122.9507 | 122.8958 | 59.0149 | -123.1155
701.0156 | 123.0194 | -59.0469 | 63.8031 | 0.19821 | 0.0097989 | 0.066969 | 0.071158 | 0.13014 | 0.00013675 | -0.00045506 | 0.2211 | -0.0048536 | 0.065759 | 0.060816 | 0.0035674 | -0.0047104 | 63.7024 | 63.7848 | -0.15564 | -59.2758 | 63.8535 | -59.0836 | -59.1614 | -59.0332 | -0.082397 | -59.3033 | 63.8443 | 63.8077 | -59.1751 | -59.2621 | -0.036621 | -0.11444 | 0.050354 | 122.8317 | -0.22888 | -0.11444 | -0.10071 | -0.12817 | -0.21515 | 0.041198 | 0.013733 | -0.25635 | -0.041199 | 0.004577 | 122.9004 | 122.7493 | 58.8913 | -122.9645 | 122.8912 | 122.8546 | 58.9645 | -123.0652
702.0156 | 123.0469 | -59.0332 | 63.8443 | 0.21347 | 0.010867 | 0.065473 | 0.069235 | 0.13142 | 0.00035035 | -0.0015231 | -0.061188 | -0.00229 | 0.064051 | 0.059962 | 0.0039948 | -0.0053512 | 63.7894 | 63.858 | -0.032043 | -59.1934 | 63.8763 | -59.0836 | -59.111 | -58.9874 | 0.041199 | -59.285 | 63.858 | 63.8351 | -59.1339 | -59.23 | -0.050354 | -0.07782 | 0.032044 | 122.8912 | -0.16022 | -0.082397 | -0.054931 | -0.10071 | -0.19684 | 0.013733 | 0.045776 | -0.25177 | -0.054931 | -0.009155 | 122.9095 | 122.8226 | 59.0012 | -122.9553 | 122.8912 | 122.8683 | 59.0744 | -123.0743
703.0156 | 122.9599 | -59.0744 | 63.826 | 0.015106 | 0.014499 | 0.066969 | 0.072226 | 0.13185 | 0.00013675 | -0.0036595 | 0.23636 | -0.0042126 | 0.065973 | 0.059962 | 0.0037812 | -0.003856 | 63.7161 | 63.7802 | -0.12817 | -59.2438 | 63.8855 | -59.0744 | -59.1614 | -59.0836 | -0.068665 | -59.3582 | 63.8718 | 63.8168 | -59.1797 | -59.2712 | 0 | -0.086975 | 0.059509 | 122.8546 | -0.16937 | -0.082397 | -0.10986 | -0.10529 | -0.19684 | 0.045776 | -0.009155 | -0.28381 | -0.086975 | -0.009156 | 122.9599 | 122.7905 | 58.9462 | -122.9874 | 122.9462 | 122.8912 | 59.0057 | -123.0972
704.0156 | 123.0423 | -59.0286 | 63.8397 | -0.03067 | 0.010226 | 0.067182 | 0.07009 | 0.13185 | 0.0014185 | -0.0034457 | 0.045624 | -0.0052808 | 0.065332 | 0.061244 | 0.0033538 | -0.0040696 | 63.7802 | 63.858 | -0.045776 | -59.2117 | 63.8763 | -59.0652 | -59.1064 | -59.024 | 0.018311 | -59.3124 | 63.8718 | 63.8351 | -59.1522 | -59.23 | -0.036622 | -0.07782 | 0.036621 | 122.8867 | -0.18311 | -0.10529 | -0.05951 | -0.1236 | -0.20142 | 0.032043 | 0.004577 | -0.28381 | -0.082397 | -0.004578 | 122.905 | 122.8088 | 58.9828 | -122.9462 | 122.9004 | 122.8638 | 59.0469 | -123.0698
705.0156 | 123.0927 | -59.0698 | 63.8168 | 0.16006 | 0.011508 | 0.068037 | 0.072012 | 0.13035 | -0.00071785 | -0.0040867 | 0.22873 | -0.0050672 | 0.062982 | 0.060816 | 0.0046356 | -0.0042832 | 63.6978 | 63.7436 | -0.15564 | -59.2758 | 63.8855 | -59.1019 | -59.166 | -59.0698 | -0.07782 | -59.3399 | 63.8535 | 63.8077 | -59.198 | -59.2941 | -0.032044 | -0.096131 | 0.068665 | 122.8134 | -0.20599 | -0.10986 | -0.11902 | -0.12817 | -0.2243 | 0.036622 | 0 | -0.27008 | -0.045777 | -0.009155 | 122.9553 | 122.7676 | 58.9142 | -122.9828 | 122.9233 | 122.8775 | 58.992 | -123.111
706.0156 | 123.0377 | -59.0286 | 63.8214 | -0.084076 | 0.011935 | 0.065901 | 0.070944 | 0.12907 | 0.00099115 | -0.0023777 | 0.16006 | -0.0037854 | 0.064264 | 0.060816 | 0.0031402 | -0.0062058 | 63.858 | 63.6063 | -0.13733 | -59.2072 | 63.8718 | -59.0744 | -59.1476 | -58.9783 | 0.045776 | -59.2621 | 63.8535 | 63.8351 | -59.1431 | -59.2255 | -0.045777 | -0.11902 | 0.050354 | 122.6349 | -0.17853 | -0.059509 | 0.036621 | -0.11444 | -0.19684 | 0.032044 | 0.050354 | -0.23346 | -0.036621 | 0.013733 | 122.9004 | 122.8867 | 58.8913 | -122.9691 | 122.8821 | 122.8638 | 59.0744 | -123.0469
707.0156 | 122.9828 | -59.0515 | 63.8489 | 0.12955 | 0.012149 | 0.066114 | 0.069022 | 0.12971 | 0.00035035 | -0.0036595 | 0.61783 | -0.0037854 | 0.065759 | 0.060389 | 0.0029266 | -0.0057786 | 63.6795 | 63.7802 | -0.15564 | -59.1339 | 63.858 | -59.0881 | -59.1705 | -59.0927 | -0.027466 | -59.3399 | 63.8901 | 63.826 | -59.1751 | -59.2758 | -0.036621 | -0.11902 | 0.009155 | 122.8317 | -0.082397 | 0.036621 | -0.16937 | -0.1236 | -0.2243 | 0.041199 | -0.041198 | -0.28839 | -0.064087 | -0.022888 | 122.9095 | 122.731 | 58.8959 | -123.0194 | 122.9416 | 122.8775 | 59.024 | -123.1247
708.0156 | 123.0194 | -59.0149 | 63.8397 | -0.168 | 0.011935 | 0.065901 | 0.07009 | 0.13334 | 0.00035035 | -0.0030185 | -0.0077819 | -0.0037854 | 0.063196 | 0.060603 | 0.0031402 | -0.0062058 | 63.7985 | 63.8626 | -0.022888 | -59.2072 | 63.8718 | -59.0561 | -59.111 | -59.0057 | 0.032043 | -59.2896 | 63.858 | 63.8489 | -59.1522 | -59.2438 | -0.041198 | -0.09613 | 0.032043 | 122.8775 | -0.19226 | -0.09613 | -0.041199 | -0.13733 | -0.22888 | 0.01831 | 0.009156 | -0.27466 | -0.045777 | 0.009155 | 122.8867 | 122.8134 | 58.992 | -122.9507 | 122.8729 | 122.8638 | 59.0469 | -123.0835
709.0156 | 122.9691 | -59.0652 | 63.8214 | 0.015106 | 0.011081 | 0.06526 | 0.069235 | 0.13377 | -0.00029045 | -0.0021641 | 0.15244 | -0.002931 | 0.063196 | 0.061885 | 0.0029266 | -0.0047104 | 63.6841 | 63.7985 | -0.1236 | -59.2484 | 63.9038 | -59.0973 | -59.1614 | -59.0973 | -0.10529 | -59.3674 | 63.8626 | 63.8489 | -59.1843 | -59.2575 | -0.032043 | -0.09613 | 0.082398 | 122.8638 | -0.1831 | -0.086975 | -0.13733 | -0.11902 | -0.19226 | 0.041199 | -0.032043 | -0.30212 | -0.10986 | 0.027466 | 122.9691 | 122.7493 | 58.9417 | -122.9828 | 122.9279 | 122.9141 | 58.96 | -123.0789
710.0156 | 123.0423 | -59.0149 | 63.8351 | -0.14511 | 0.011081 | 0.068678 | 0.072653 | 0.13099 | -0.00093145 | -0.0034457 | -0.16037 | -0.0037854 | 0.063623 | 0.060389 | 0.0033538 | -0.0044968 | 63.7436 | 63.8443 | -0.027466 | -59.2026 | 63.913 | -59.0698 | -59.1339 | -58.9966 | 0.082397 | -59.2575 | 63.913 | 63.8443 | -59.1522 | -59.2255 | -0.054931 | -0.11902 | 0.07782 | 122.8592 | -0.18768 | -0.068665 | -0.091553 | -0.13733 | -0.21057 | 0.07782 | 0.018311 | -0.24261 | -0.032043 | 0.009155 | 122.9279 | 122.7585 | 58.9874 | -122.9691 | 122.9279 | 122.8592 | 59.0973 | -123.0606
711.0156 | 122.9919 | -59.0378 | 63.8306 | 0.053253 | 0.011935 | 0.065473 | 0.069449 | 0.12907 | 0.00056395 | -0.0019505 | 0.11429 | -0.003999 | 0.063623 | 0.059321 | 0.0048492 | -0.0064194 | 63.7024 | 63.826 | -0.09613 | -59.2255 | 63.8809 | -59.079 | -59.1476 | -59.0469 | -0.036621 | -59.3353 | 63.8855 | 63.8123 | -59.1614 | -59.2484 | -0.041198 | -0.10986 | 0.050354 | 122.8638 | -0.18768 | -0.07782 | -0.12817 | -0.1236 | -0.21057 | 0.054932 | -0.009155 | -0.29755 | -0.086975 | -0.01831 | 122.9187 | 122.7402 | 58.9417 | -122.9782 | 122.9233 | 122.85 | 59.0012 | -123.0789
712.0156 | 123.0652 | -59.0195 | 63.8489 | -0.18326 | 0.012576 | 0.067823 | 0.070517 | 0.1295 | -0.0022131 | -0.0021641 | -0.053558 | -0.0050672 | 0.065332 | 0.060389 | 0.0031402 | -0.0064194 | 63.7619 | 63.8855 | -0.022888 | -59.1797 | 63.8992 | -59.0698 | -59.1476 | -59.0057 | 0.073242 | -59.2667 | 63.9038 | 63.8168 | -59.166 | -59.2346 | -0.050354 | -0.12817 | 0.050354 | 122.905 | -0.16022 | -0.032043 | -0.086975 | -0.14648 | -0.21515 | 0.054932 | 0.013733 | -0.24719 | -0.032044 | -0.032044 | 122.9187 | 122.7814 | 58.9966 | -122.9965 | 122.9233 | 122.8363 | 59.0927 | -123.0835
713.0156 | 122.9965 | -59.0607 | 63.8168 | 0.099029 | 0.01044 | 0.067823 | 0.07009 | 0.13035 | -0.00050425 | -0.0038731 | -0.72494 | -0.0044264 | 0.064264 | 0.061457 | 0.0014312 | -0.0070602 | 63.6749 | 63.8306 | -0.24261 | -59.4955 | 63.8123 | -59.1202 | -59.1705 | -59.0332 | -0.11444 | -59.3445 | 63.8489 | 63.7985 | -59.1797 | -59.2529 | -0.059509 | -0.10986 | -0.004577 | 122.8912 | -0.43488 | -0.32501 | -0.14191 | -0.11902 | -0.19226 | 0.032044 | 0.027466 | -0.28381 | -0.091552 | -0.01831 | 122.8729 | 122.7356 | 58.8181 | -122.9874 | 122.9095 | 122.8592 | 58.9462 | -123.0698
714.0156 | 123.0515 | -59.0195 | 63.8626 | -0.168 | 0.0097989 | 0.067182 | 0.071799 | 0.12971 | -0.00029045 | -0.0045139 | -0.10696 | -0.0042126 | 0.062982 | 0.061457 | 0.0020722 | -0.0042832 | 63.739 | 63.8397 | -0.041199 | -59.198 | 63.9221 | -59.0424 | -59.1339 | -59.0057 | 0.082397 | -59.2484 | 63.8809 | 63.8535 | -59.1385 | -59.2392 | -0.022888 | -0.11444 | 0.059509 | 122.8592 | -0.17853 | -0.064087 | -0.1236 | -0.11902 | -0.21973 | 0.01831 | 0.013733 | -0.22888 | -0.009155 | -0.009155 | 122.9416 | 122.7585 | 58.9783 | -122.9965 | 122.9004 | 122.8729 | 59.1019 | -123.1018
715.0156 | 123.0011 | -59.0378 | 63.8351 | -0.061188 | 0.010013 | 0.067396 | 0.065604 | 0.12907 | -0.00050425 | -0.0023777 | -0.00015237 | -0.0054944 | 0.066187 | 0.061457 | 0.0012176 | -0.0068466 | 63.7573 | 63.9313 | -0.009155 | -59.2072 | 63.8855 | -59.0607 | -59.1248 | -59.0057 | 0.036621 | -59.2667 | 63.8763 | 63.8168 | -59.1751 | -59.2529 | -0.022888 | -0.086975 | 0.050354 | 122.9691 | -0.16937 | -0.082397 | -0.07782 | -0.13733 | -0.21515 | 0.041199 | 0.032044 | -0.22888 | -0.013733 | -0.018311 | 122.9233 | 122.7951 | 59.0286 | -122.9599 | 122.9141 | 122.8546 | 59.0744 | -123.0881
716.0156 | 122.9828 | -59.0515 | 63.8718 | -0.25955 | 0.0074491 | 0.066328 | 0.068594 | 0.13057 | -0.0069129 | -0.0053683 | -0.13748 | -0.0048536 | 0.063196 | 0.059535 | 0.0039948 | -0.0068466 | 63.7161 | 63.858 | -0.027466 | -59.2255 | 63.9038 | -59.0698 | -59.1385 | -59.0424 | 0.050354 | -59.0927 | 63.9313 | 63.8992 | -59.111 | -59.2163 | -0.01831 | -0.086975 | 0.032044 | 122.9095 | -0.17395 | -0.086975 | -0.15564 | -0.059509 | -0.1648 | 0.059509 | 0.009156 | -0.041198 | 0.1236 | 0.027466 | 122.9553 | 122.7676 | 59.024 | -123.0103 | 122.9828 | 122.9507 | 59.1019 | -123.0881
717.0156 | 122.9691 | -59.0012 | 63.8168 | -0.12985 | 0.011722 | 0.068037 | 0.069449 | 0.13099 | 0.00099115 | -0.0021641 | -0.061188 | -0.0048536 | 0.065119 | 0.058467 | 0.0022858 | -0.0059922 | 63.7802 | 63.8763 | -0.027466 | -59.198 | 63.8947 | -59.0607 | -59.1476 | -58.9966 | 0.050354 | -59.2621 | 63.8718 | 63.8077 | -59.1202 | -59.2392 | -0.059509 | -0.14648 | 0.07782 | 122.8775 | -0.19684 | -0.050354 | -0.036621 | -0.11902 | -0.23804 | 0.054932 | 0.004578 | -0.26093 | -0.022888 | -0.009155 | 122.8958 | 122.7814 | 58.9737 | -122.9645 | 122.8729 | 122.8088 | 59.0515 | -123.056
718.0156 | 123.0057 | -59.0286 | 63.8351 | -0.19089 | 0.012576 | 0.065046 | 0.069876 | 0.12993 | 0.00035035 | -0.0028049 | -0.053558 | -0.0050672 | 0.064905 | 0.060816 | 0.0033538 | -0.004924 | 63.7756 | 63.8809 | -0.022888 | -59.1843 | 63.9084 | -59.0698 | -59.1339 | -59.0149 | 0.054932 | -59.2621 | 63.8947 | 63.826 | -59.166 | -59.23 | -0.041199 | -0.10529 | 0.073242 | 122.9095 | -0.15564 | -0.050354 | -0.059509 | -0.13733 | -0.20142 | 0.059509 | 0.013732 | -0.23346 | -0.032043 | -0.009155 | 122.937 | 122.8043 | 59.0057 | -122.9691 | 122.9233 | 122.8546 | 59.0836 | -123.0652
719.0156 | 123.0286 | -59.024 | 63.8443 | -0.11459 | 0.011508 | 0.067182 | 0.071585 | 0.1295 | 0.00013675 | -0.0028049 | 0.2211 | -0.002931 | 0.062555 | 0.060816 | 0.0016448 | -0.0040696 | 63.7711 | 63.8992 | -0.022888 | -59.198 | 63.8992 | -59.0607 | -59.1339 | -58.9737 | 0.036621 | -59.2712 | 63.8855 | 63.8077 | -59.1614 | -59.2438 | -0.036621 | -0.10986 | 0.054932 | 122.9233 | -0.17395 | -0.064087 | -0.073242 | -0.13733 | -0.21973 | 0.041199 | 0.050354 | -0.24719 | -0.027466 | -0.036621 | 122.9233 | 122.7951 | 59.0012 | -122.9782 | 122.9095 | 122.8317 | 59.0607 | -123.0881
720.0156 | 123.0103 | -59.0286 | 63.8626 | 0.30502 | 0.010013 | 0.068891 | 0.067526 | 0.12843 | -0.0034949 | -0.0036595 | -0.045929 | -0.0027174 | 0.065332 | 0.060816 | -6.4178e-05 | -0.0047104 | 63.7024 | 63.8351 | -0.054932 | -59.1934 | 63.8992 | -59.0744 | -59.1202 | -59.0378 | 0.041199 | -59.2804 | 63.8992 | 63.8214 | -59.1614 | -59.2346 | -0.045777 | -0.091553 | 0.036621 | 122.8638 | -0.1648 | -0.073242 | -0.16022 | -0.13275 | -0.20599 | 0.036621 | -0.009156 | -0.25177 | -0.045777 | -0.041199 | 122.9279 | 122.731 | 58.9737 | -122.9828 | 122.9279 | 122.85 | 59.0698 | -123.0972
721.0156 | 123.0515 | -59.0286 | 63.8397 | -0.11459 | 0.012362 | 0.06761 | 0.068808 | 0.13163 | 0.00056395 | -0.0017369 | -0.068817 | -0.00464 | 0.063196 | 0.060176 | 0.0046356 | -0.0042832 | 63.7482 | 63.9221 | 0.004578 | -59.1888 | 63.8901 | -59.0744 | -59.1156 | -59.0057 | 0.068665 | -59.2621 | 63.8809 | 63.8443 | -59.1476 | -59.23 | -0.045777 | -0.086976 | 0.050354 | 122.9507 | -0.16022 | -0.073242 | -0.091553 | -0.11902 | -0.20142 | 0.041198 | 0.022888 | -0.23346 | -0.032043 | 0.004577 | 122.9187 | 122.7768 | 59.0332 | -122.9553 | 122.9095 | 122.8729 | 59.0973 | -123.0698
722.0156 | 122.9828 | -59.0469 | 63.8489 | -0.22903 | 0.0080899 | 0.066755 | 0.071799 | 0.12993 | -0.0019995 | -0.0053683 | -0.18326 | -0.0035718 | 0.061273 | 0.060176 | 0.0042084 | -0.0030014 | 63.707 | 63.8626 | -0.045776 | -59.2255 | 63.9221 | -59.0515 | -59.1385 | -59.166 | 0.12817 | -59.3216 | 63.9038 | 63.8397 | -59.1705 | -59.2392 | -0.004578 | -0.091553 | 0.073242 | 122.9095 | -0.17853 | -0.086975 | -0.14191 | -0.1236 | -0.19226 | 0.054932 | -0.11902 | -0.27466 | -0.082397 | -0.009155 | 122.9691 | 122.7539 | 59.0012 | -122.9874 | 122.9507 | 122.8867 | 59.1751 | -123.0881
723.0156 | 123.0331 | -59.0332 | 63.8168 | 0.16769 | 0.011508 | 0.066328 | 0.06774 | 0.13185 | -0.0011451 | -0.0023777 | 0.24399 | -0.0050672 | 0.063196 | 0.061671 | 0.0035674 | -0.0036424 | 63.6932 | 63.7985 | -0.15106 | -59.2621 | 63.8718 | -59.0927 | -59.1476 | -59.0286 | -0.068665 | -59.3033 | 63.8443 | 63.7756 | -59.1934 | -59.2529 | -0.059509 | -0.11444 | 0.054932 | 122.8317 | -0.22888 | -0.11444 | -0.1236 | -0.16022 | -0.21973 | 0.027466 | 0.004578 | -0.27008 | -0.050354 | -0.041198 | 122.905 | 122.7264 | 58.8821 | -122.9645 | 122.8775 | 122.8088 | 58.9645 | -123.0698
724.0156 | 122.9965 | -59.024 | 63.8626 | -0.26718 | 0.0093717 | 0.068891 | 0.069876 | 0.13142 | -0.0032813 | -0.0062229 | -0.16037 | -0.00464 | 0.062555 | 0.058253 | 0.0022858 | -0.0040696 | 63.7436 | 63.858 | -0.041199 | -59.1888 | 63.913 | -59.0424 | -59.1019 | -59.024 | 0.054932 | -59.2758 | 63.9175 | 63.8443 | -59.1614 | -59.2575 | -0.01831 | -0.07782 | 0.050354 | 122.8821 | -0.16479 | -0.086975 | -0.11902 | -0.13733 | -0.23346 | 0.054932 | 0 | -0.25177 | -0.018311 | -0.018311 | 122.937 | 122.7676 | 58.9828 | -122.9645 | 122.9416 | 122.8683 | 59.079 | -123.1201
725.0156 | 123.0515 | -59.0286 | 63.8535 | -0.19089 | 0.013431 | 0.066755 | 0.069876 | 0.13249 | 0.0014185 | -0.0032321 | -0.099335 | -0.0027174 | 0.06341 | 0.060816 | 0.0050628 | -0.0079148 | 63.7527 | 63.9038 | -0.018311 | -59.1888 | 63.913 | -59.0561 | -59.1202 | -58.9966 | 0.068665 | -59.2621 | 63.8855 | 63.7802 | -59.1339 | -59.2529 | -0.027466 | -0.091553 | 0.059509 | 122.9324 | -0.16022 | -0.068665 | -0.10071 | -0.10529 | -0.22431 | 0.032043 | 0.032043 | -0.23346 | -0.009155 | -0.073243 | 122.9416 | 122.7814 | 59.0103 | -122.9736 | 122.9141 | 122.8088 | 59.0973 | -123.1064
726.0156 | 122.9919 | -59.0469 | 63.8535 | -0.23666 | 0.0078763 | 0.068037 | 0.06774 | 0.13142 | -0.0015723 | -0.0062229 | -0.12222 | -0.00464 | 0.061273 | 0.060176 | 0.00079042 | -0.0042832 | 63.6978 | 63.8626 | -0.027466 | -59.2209 | 63.9175 | -59.0515 | -59.1156 | -59.0698 | 0.35706 | -59.3765 | 63.9359 | 63.8443 | -59.1568 | -59.2484 | -0.004578 | -0.068665 | 0.064087 | 122.9095 | -0.17395 | -0.10529 | -0.15564 | -0.10986 | -0.20142 | 0.082397 | -0.022888 | -0.32959 | -0.12817 | -0.009156 | 122.9645 | 122.7448 | 59.0195 | -122.9691 | 122.9828 | 122.8912 | 59.404 | -123.1018
727.0156 | 123.024 | -59.0149 | 63.8672 | -0.22141 | 0.010226 | 0.065473 | 0.070303 | 0.13035 | 0.00077755 | -0.0030185 | -0.17563 | -0.0044264 | 0.064478 | 0.060176 | 0.0033538 | -0.006633 | 63.7344 | 63.8763 | -0.032043 | -59.2026 | 63.9359 | -59.0836 | -59.1019 | -58.992 | 0.073242 | -59.2575 | 63.8901 | 63.8214 | -59.1476 | -59.2163 | -0.068664 | -0.086975 | 0.068665 | 122.8912 | -0.18768 | -0.10071 | -0.13275 | -0.13275 | -0.20142 | 0.022889 | 0.022889 | -0.24261 | -0.041198 | -0.045776 | 122.9507 | 122.7493 | 58.9828 | -122.9691 | 122.905 | 122.8363 | 59.0881 | -123.0835
728.0156 | 123.0057 | -59.0469 | 63.8489 | 0.045624 | 0.014712 | 0.066969 | 0.069022 | 0.12907 | 0.0012047 | -0.0017369 | 0.030365 | -0.00464 | 0.063623 | 0.060176 | 0.0012176 | -0.005565 | 63.7344 | 63.8306 | -0.082397 | -59.2392 | 63.9038 | -59.0515 | -59.1339 | -59.0378 | -0.032043 | -59.3308 | 63.913 | 63.8031 | -59.1751 | -59.2438 | -0.004578 | -0.086975 | 0.054932 | 122.8775 | -0.19226 | -0.10529 | -0.11444 | -0.12817 | -0.19684 | 0.064087 | 0.009155 | -0.28381 | -0.086976 | -0.045776 | 122.9507 | 122.7814 | 58.9645 | -122.9828 | 122.9599 | 122.85 | 59.0149 | -123.0927
729.0156 | 123.0286 | -59.0103 | 63.858 | -0.22903 | 0.0087307 | 0.069319 | 0.071372 | 0.13121 | -0.0015723 | -0.0057957 | -0.12985 | -0.0048536 | 0.063837 | 0.05868 | 0.0024994 | -0.0044968 | 63.7253 | 63.8626 | -0.041199 | -59.2117 | 63.9221 | -59.0744 | -59.1522 | -59.0332 | 0.059509 | -59.2667 | 63.8947 | 63.8489 | -59.1293 | -59.2438 | -0.064087 | -0.14191 | 0.064087 | 122.8729 | -0.20142 | -0.059509 | -0.13275 | -0.11902 | -0.23346 | 0.036621 | -0.022888 | -0.25635 | -0.022889 | -0.009155 | 122.9324 | 122.7356 | 58.9691 | -123.0103 | 122.905 | 122.8592 | 59.0698 | -123.1018
730.0156 | 123.1155 | -59.0012 | 63.8214 | 0.25162 | 0.00082671 | 0.071882 | 0.066672 | 0.13163 | -0.0066993 | -0.0070773 | 0.022736 | -0.007417 | 0.062128 | 0.060176 | 0.0018584 | -0.0036424 | 63.8031 | 63.9633 | 0.059509 | -59.1339 | 63.8443 | -59.0332 | -59.0836 | -58.9417 | 0.16479 | -59.1751 | 63.8123 | 63.7848 | -59.0927 | -59.1934 | -0.032043 | -0.082397 | 0.022888 | 122.9645 | -0.13275 | -0.050354 | -0.01831 | -0.091552 | -0.19226 | -0.009155 | 0.05951 | -0.17395 | 0.01831 | -0.036621 | 122.8455 | 122.8043 | 59.0607 | -122.905 | 122.8134 | 122.7859 | 59.166 | -123.0148
731.0156 | 123.056 | -59.0149 | 63.8626 | -0.15274 | 0.010013 | 0.066969 | 0.072867 | 0.13249 | -0.00071785 | -0.0030185 | -0.18326 | -0.0042126 | 0.063623 | 0.061885 | 0.002713 | -0.0062058 | 63.739 | 63.8809 | -0.027466 | -59.1888 | 63.913 | -59.0469 | -59.1431 | -58.9966 | 0.073242 | -59.2529 | 63.8809 | 63.8214 | -59.1476 | -59.2255 | -0.032043 | -0.12817 | 0.050354 | 122.8958 | -0.17395 | -0.045777 | -0.1236 | -0.13275 | -0.21057 | 0.01831 | 0.018311 | -0.23804 | -0.027466 | -0.041199 | 122.9279 | 122.7539 | 58.9874 | -123.0057 | 122.8958 | 122.8363 | 59.0881 | -123.0881
732.0156 | 122.9965 | -59.024 | 63.8763 | -0.24429 | 0.0046719 | 0.067823 | 0.071158 | 0.13292 | -0.0034949 | -0.0051547 | -0.22903 | -0.0072034 | 0.06341 | 0.061457 | 0.0031402 | -0.0062058 | 63.7573 | 63.9038 | 0.018311 | -59.1888 | 63.9175 | -59.0469 | -59.1064 | -59.0195 | 0.059509 | -59.2575 | 63.8992 | 63.8306 | -59.1568 | -59.2346 | -0.022888 | -0.082397 | 0.041199 | 122.9279 | -0.16479 | -0.082398 | -0.11902 | -0.13275 | -0.21057 | 0.022888 | 0.004578 | -0.23346 | -0.022888 | -0.045777 | 122.9416 | 122.7814 | 59.0424 | -122.9828 | 122.9233 | 122.8546 | 59.0836 | -123.111
733.0312 | 123.0972 | -59.0057 | 63.7939 | -0.0077822 | 0.0063809 | 0.067182 | 0.06539 | 0.12971 | -0.0030677 | -0.0036595 | 0.35843 | -0.0042126 | 0.061273 | 0.060389 | 0.0012176 | -0.003856 | 63.7573 | 63.9359 | -0.032043 | -59.1843 | 63.8351 | -59.0607 | -59.1431 | -58.9462 | 0.032043 | -59.2255 | 63.7985 | 63.7436 | -59.1385 | -59.23 | -0.054932 | -0.13733 | 0.041199 | 122.9416 | -0.17853 | -0.041199 | -0.036621 | -0.13275 | -0.2243 | 0.004578 | 0.059509 | -0.21973 | 0.004578 | -0.050354 | 122.8409 | 122.7631 | 58.9737 | -122.937 | 122.8043 | 122.7493 | 59.0378 | -123.024
734.0156 | 123.0286 | -59.0012 | 63.8489 | -0.20615 | 0.0063809 | 0.068891 | 0.070303 | 0.13078 | -0.0017859 | -0.0040867 | -0.11459 | -0.0059216 | 0.061701 | 0.059535 | 0.0012176 | -0.0064194 | 63.7894 | 63.9404 | 0.036621 | -59.1797 | 63.8763 | -59.0561 | -59.0973 | -58.9737 | 0.10529 | -59.2438 | 63.8901 | 63.8535 | -59.1293 | -59.2255 | -0.054931 | -0.09613 | 0.027466 | 122.9416 | -0.17853 | -0.082397 | -0.059509 | -0.12817 | -0.2243 | 0.041199 | 0.027466 | -0.24261 | -0.01831 | 0.004578 | 122.8775 | 122.7905 | 59.0378 | -122.9462 | 122.8912 | 122.8546 | 59.1064 | -123.0743
735.0156 | 122.9736 | -59.0286 | 63.858 | 0.030365 | 0.0095853 | 0.066328 | 0.070731 | 0.13014 | 0.00099115 | -0.0028049 | -0.19089 | -0.003999 | 0.063623 | 0.05868 | 0.0029266 | -0.0079148 | 63.7436 | 63.8397 | -0.041199 | -59.2163 | 63.8947 | -59.0698 | -59.1476 | -59.0286 | 0.036621 | -59.285 | 63.8992 | 63.8351 | -59.1568 | -59.2484 | -0.041199 | -0.11902 | 0.036621 | 122.8683 | -0.18768 | -0.068665 | -0.11444 | -0.12817 | -0.21973 | 0.041199 | 0 | -0.25635 | -0.036621 | -0.022888 | 122.9233 | 122.7722 | 58.9874 | -123.0057 | 122.9279 | 122.8638 | 59.0652 | -123.1064
736.0156 | 123.0515 | -59.0057 | 63.8626 | -0.21378 | 0.0059537 | 0.069105 | 0.065817 | 0.13057 | -0.0039221 | -0.0068637 | -0.12222 | -0.0065626 | 0.062769 | 0.058894 | 0.0014312 | -0.0059922 | 63.7894 | 63.9679 | 0.059509 | -59.1751 | 63.8626 | -59.0424 | -59.1156 | -58.9645 | 0.11444 | -59.2163 | 63.8855 | 63.7939 | -59.1293 | -59.2072 | -0.036621 | -0.10986 | 0 | 122.9736 | -0.16937 | -0.059509 | -0.073242 | -0.1236 | -0.20142 | 0.022888 | 0.041198 | -0.21057 | -0.009156 | -0.068665 | 122.8683 | 122.7951 | 59.0652 | -122.9782 | 122.8912 | 122.7997 | 59.1202 | -123.0698
737.0156 | 122.9965 | -59.0332 | 63.8489 | 0.41183 | 0.010013 | 0.067823 | 0.072226 | 0.13078 | -0.00029045 | -0.0038731 | -0.13748 | -0.0048536 | 0.061273 | 0.060816 | 0.0048492 | -0.0040696 | 63.7207 | 63.8443 | -0.045776 | -59.198 | 63.9221 | -59.0652 | -59.1339 | -59.0195 | 0.036621 | -59.3033 | 63.8992 | 63.8168 | -59.1614 | -59.2392 | -0.032044 | -0.10071 | 0.073242 | 122.8775 | -0.16479 | -0.064087 | -0.12817 | -0.12817 | -0.20599 | 0.050354 | 0.013733 | -0.27008 | -0.064087 | -0.032044 | 122.9553 | 122.7539 | 58.9874 | -122.9828 | 122.9324 | 122.85 | 59.0698 | -123.0881
738.0312 | 123.0606 | -59.0149 | 63.8443 | -0.0077822 | 0.011508 | 0.065687 | 0.06774 | 0.1327 | 0.00077755 | -0.0036595 | 0.8696 | -0.002931 | 0.06341 | 0.061244 | 0.004422 | -0.0051376 | 63.7756 | 63.9038 | -0.013733 | -59.2072 | 63.8992 | -59.0744 | -59.1248 | -58.9737 | 0.086975 | -59.285 | 63.8992 | 63.7894 | -59.1705 | -59.23 | -0.059509 | -0.10986 | 0.054932 | 122.9187 | -0.19226 | -0.082397 | -0.068664 | -0.15564 | -0.21515 | 0.054932 | 0.041199 | -0.27008 | -0.054931 | -0.054931 | 122.9141 | 122.7905 | 59.0012 | -122.9691 | 122.9141 | 122.8043 | 59.1019 | -123.0743
739.0156 | 123.0286 | -59.0149 | 63.8626 | -0.23666 | 0.011081 | 0.065901 | 0.070944 | 0.13121 | -0.0011451 | -0.00088226 | -0.168 | -0.0048536 | 0.062128 | 0.059962 | 0.0020722 | -0.0077012 | 63.7482 | 63.8718 | -0.027466 | -59.2072 | 63.945 | -59.0607 | -59.1385 | -58.9966 | 0.07782 | -59.2758 | 63.9084 | 63.8123 | -59.1293 | -59.23 | -0.045776 | -0.1236 | 0.082397 | 122.8867 | -0.19226 | -0.068664 | -0.11444 | -0.11444 | -0.21515 | 0.045776 | 0.018311 | -0.26093 | -0.045776 | -0.050354 | 122.9599 | 122.7631 | 58.9874 | -123.0011 | 122.9233 | 122.8271 | 59.0927 | -123.0927
740.0156 | 123.0286 | -59.0286 | 63.8718 | -0.12985 | 0.010867 | 0.066969 | 0.067526 | 0.13163 | -0.0013587 | -0.0017369 | -0.19089 | -0.0035718 | 0.063623 | 0.059107 | 0.0020722 | -0.0057786 | 63.739 | 63.8672 | -0.027466 | -59.2026 | 63.9038 | -59.0561 | -59.1156 | -59.0103 | 0.086975 | -59.2575 | 63.8809 | 63.8214 | -59.1385 | -59.2346 | -0.027466 | -0.086976 | 0.032044 | 122.8958 | -0.17395 | -0.086975 | -0.13275 | -0.10986 | -0.20599 | 0.009155 | 0.01831 | -0.22888 | -0.022888 | -0.050354 | 122.9324 | 122.7676 | 59.0012 | -122.9874 | 122.9095 | 122.85 | 59.1156 | -123.1064
741.0156 | 122.9828 | -59.0286 | 63.8397 | -0.11459 | 0.011722 | 0.067182 | 0.071585 | 0.13078 | 0.00035035 | -0.0030185 | -0.053558 | -0.006349 | 0.064691 | 0.061671 | 0.0031402 | -0.004924 | 63.7573 | 63.9038 | -0.004578 | -59.1888 | 63.8672 | -59.0698 | -59.1339 | -58.9783 | 0.064087 | -59.2758 | 63.8626 | 63.7985 | -59.1705 | -59.2438 | -0.041199 | -0.10529 | 0.027465 | 122.9324 | -0.16022 | -0.054932 | -0.082398 | -0.14191 | -0.21515 | 0.022888 | 0.050354 | -0.24719 | -0.032044 | -0.041199 | 122.8958 | 122.7859 | 59.024 | -122.9736 | 122.8912 | 122.8271 | 59.0927 | -123.0835
742.0156 | 122.9782 | -59.0195 | 63.8351 | 0.037994 | 0.012576 | 0.065901 | 0.069876 | 0.12886 | 0.00077755 | -0.0015231 | 0.076141 | -0.0042126 | 0.063196 | 0.06103 | 0.0016448 | -0.005565 | 63.7253 | 63.8443 | -0.082397 | -59.2392 | 63.8901 | -59.0836 | -59.1385 | -59.0515 | -0.036621 | -59.317 | 63.8855 | 63.7939 | -59.1751 | -59.2484 | -0.064087 | -0.11902 | 0.054932 | 122.8638 | -0.21973 | -0.10071 | -0.10986 | -0.15564 | -0.22888 | 0.050354 | -0.032044 | -0.29755 | -0.068665 | -0.041199 | 122.9095 | 122.7448 | 58.9371 | -122.9736 | 122.905 | 122.8134 | 58.9828 | -123.0835
743.0469 | 123.111 | -59.0149 | 63.7894 | 0.50339 | 0.0080899 | 0.068464 | 0.06539 | 0.13099 | -0.0066993 | -0.0053683 | 0.32791 | -0.0048536 | 0.064264 | 0.058894 | 0.0046356 | -0.0040696 | 63.826 | 63.8947 | -0.032043 | -59.1751 | 63.8214 | -59.0744 | -59.1293 | -58.9417 | 0.036621 | -59.2209 | 63.7848 | 63.7665 | -59.1522 | -59.2163 | -0.059509 | -0.11444 | 0.032043 | 122.9095 | -0.16022 | -0.045777 | 0.036621 | -0.13733 | -0.20142 | -0.004578 | 0.073243 | -0.20599 | -0.004577 | -0.022889 | 122.8363 | 122.8409 | 58.9828 | -122.9187 | 122.7997 | 122.7814 | 59.0515 | -123.0057
744.0156 | 123.0057 | -59.0469 | 63.8489 | 0.030365 | 0.010653 | 0.069959 | 0.069663 | 0.13057 | 0.00077755 | -0.0045139 | -0.14511 | -0.0033582 | 0.063623 | 0.060603 | -6.4178e-05 | -0.005565 | 63.7253 | 63.8214 | -0.073242 | -59.2255 | 63.9038 | -59.0607 | -59.1339 | -59.024 | 0.045776 | -59.285 | 63.9038 | 63.8672 | -59.1431 | -59.2117 | -0.013733 | -0.086975 | 0.054932 | 122.8683 | -0.17853 | -0.091553 | -0.1236 | -0.09613 | -0.16479 | 0.054932 | 0.022888 | -0.23804 | -0.073242 | 0.01831 | 122.9507 | 122.7722 | 58.9737 | -122.9828 | 122.9507 | 122.9141 | 59.0927 | -123.0606
745.0156 | 123.0515 | -59.0469 | 63.8489 | -0.19852 | 0.011722 | 0.066114 | 0.073081 | 0.1342 | 0.00056395 | -0.0040867 | -0.14511 | -0.0054944 | 0.064691 | 0.060816 | 0.0035674 | -0.0053512 | 63.739 | 63.858 | -0.036621 | -59.198 | 63.9359 | -59.0561 | -59.1385 | -59.0195 | 0.073242 | -59.2438 | 63.8855 | 63.8168 | -59.1705 | -59.2438 | -0.009155 | -0.091553 | 0.086975 | 122.905 | -0.15106 | -0.059509 | -0.10986 | -0.1236 | -0.19684 | 0.036621 | 0.027466 | -0.19684 | 0 | -0.032044 | 122.9828 | 122.7859 | 59.0103 | -122.9874 | 122.9324 | 122.8638 | 59.1202 | -123.0927
746.0156 | 123.0011 | -59.0469 | 63.8306 | -0.084076 | 0.01279 | 0.066755 | 0.070944 | 0.13206 | 0.0018457 | -0.0023777 | 0.0074766 | -0.0031446 | 0.066614 | 0.060176 | 0.004422 | -0.0057786 | 63.7802 | 63.8672 | -0.032043 | -59.2072 | 63.8901 | -59.079 | -59.1431 | -58.992 | 0.009155 | -59.285 | 63.8672 | 63.7894 | -59.166 | -59.2621 | -0.032043 | -0.09613 | 0.05951 | 122.9141 | -0.16022 | -0.064087 | -0.050354 | -0.11902 | -0.21515 | 0.036621 | 0.054932 | -0.23804 | -0.022888 | -0.041198 | 122.937 | 122.8271 | 59.0149 | -122.9736 | 122.9141 | 122.8363 | 59.0561 | -123.0927
747.0156 | 123.0011 | -59.0424 | 63.8535 | -0.00015269 | 0.013431 | 0.068037 | 0.071372 | 0.12843 | -0.00071785 | -0.0013095 | 0.037995 | -0.0044264 | 0.06341 | 0.059321 | 0.004422 | -0.0074876 | 63.7253 | 63.8214 | -0.086975 | -59.2392 | 63.8763 | -59.079 | -59.1751 | -59.0469 | -0.050354 | -59.3399 | 63.8489 | 63.7985 | -59.198 | -59.2392 | -0.036621 | -0.13275 | 0.022888 | 122.8638 | -0.19684 | -0.064087 | -0.12817 | -0.15564 | -0.19684 | -0.004578 | -0.004578 | -0.29755 | -0.10071 | -0.054932 | 122.9187 | 122.7676 | 58.9554 | -123.0286 | 122.8912 | 122.8409 | 58.992 | -123.0927
748.0312 | 122.9782 | -59.0652 | 63.8214 | 0.015106 | 0.013003 | 0.067182 | 0.071799 | 0.13185 | 0.0016321 | -0.0023777 | 0.12192 | -0.003999 | 0.062342 | 0.061244 | 0.0029266 | -0.0057786 | 63.707 | 63.7848 | -0.1236 | -59.2392 | 63.8763 | -59.0698 | -59.1522 | -59.0973 | -0.086975 | -59.3628 | 63.8718 | 63.826 | -59.1705 | -59.2621 | -0.004577 | -0.086975 | 0.054932 | 122.85 | -0.17395 | -0.086975 | -0.11444 | -0.10529 | -0.19684 | 0.050354 | -0.032043 | -0.29755 | -0.10071 | 0.004578 | 122.9416 | 122.7722 | 58.9417 | -122.9736 | 122.937 | 122.8912 | 58.9783 | -123.0835
749.0156 | 123.0377 | -59.0561 | 63.8397 | -0.00015269 | 0.013858 | 0.065687 | 0.071799 | 0.13014 | 0.0027001 | -0.0021641 | 0.015106 | -0.0035718 | 0.064905 | 0.060816 | 0.0024994 | -0.005565 | 63.7756 | 63.8535 | -0.068665 | -59.2026 | 63.8626 | -59.0515 | -59.1293 | -58.992 | 0.027466 | -59.285 | 63.8718 | 63.826 | -59.1797 | -59.2667 | 0.004577 | -0.073242 | 0.022888 | 122.9095 | -0.14648 | -0.073243 | -0.064087 | -0.1236 | -0.21057 | 0.032043 | 0.064087 | -0.22888 | -0.01831 | -0.013733 | 122.9187 | 122.8317 | 58.9874 | -122.9691 | 122.9279 | 122.8821 | 59.0836 | -123.1064
750.0156 | 122.9736 | -59.0607 | 63.826 | 0.14481 | 0.013217 | 0.065901 | 0.07009 | 0.13121 | -0.0011451 | -0.0030185 | 3.7154 | -0.0016492 | 0.060846 | 0.060176 | 0.0024994 | -0.0042832 | 63.6612 | 63.7482 | -0.15106 | -59.2804 | 63.8763 | -59.1019 | -59.1614 | -59.1019 | 0.068665 | -59.3216 | 63.8718 | 63.8214 | -59.1614 | -59.2667 | -0.041199 | -0.10071 | 0.050354 | 122.8088 | -0.21973 | -0.11902 | -0.16479 | -0.10071 | -0.20599 | 0.045776 | -0.041199 | -0.26093 | -0.054931 | -0.004578 | 122.937 | 122.7219 | 58.9096 | -122.9874 | 122.9324 | 122.8821 | 59.1293 | -123.0927
751.0156 | 122.9691 | -59.0561 | 63.826 | 0.060882 | 0.013003 | 0.063978 | 0.068381 | 0.12993 | -0.0015723 | -0.0030185 | 3.2729 | -0.0018628 | 0.062982 | 0.059535 | 0.0029266 | -0.0042832 | 63.6795 | 63.7436 | -0.13733 | -59.2804 | 63.8901 | -59.0927 | -59.166 | -59.1339 | 0.073242 | -59.3124 | 63.8992 | 63.8306 | -59.1797 | -59.2575 | -0.036621 | -0.10986 | 0.064087 | 122.7997 | -0.22431 | -0.11444 | -0.14648 | -0.1236 | -0.20142 | 0.073242 | -0.07782 | -0.25635 | -0.054932 | 0.004577 | 122.9462 | 122.7356 | 58.9188 | -122.9919 | 122.9553 | 122.8867 | 59.1293 | -123.0835
752.0156 | 123.0194 | -59.0332 | 63.8763 | -0.15274 | 0.013858 | 0.065473 | 0.069449 | 0.13121 | 0.00013675 | -0.0019505 | -0.0077819 | -0.0031446 | 0.061273 | 0.061885 | 0.0022858 | -0.0059922 | 63.7619 | 63.8489 | -0.027466 | -59.2026 | 63.8809 | -59.079 | -59.1431 | -58.9874 | 0.068665 | -59.2575 | 63.8718 | 63.8031 | -59.1751 | -59.2484 | -0.045776 | -0.10986 | 0.004577 | 122.8821 | -0.16937 | -0.05951 | -0.11444 | -0.14191 | -0.21515 | -0.004578 | 0.045776 | -0.2243 | -0.009155 | -0.073242 | 122.9141 | 122.7951 | 59.0057 | -123.0194 | 122.905 | 122.8363 | 59.1019 | -123.1247
753.0312 | 123.1018 | -59.0195 | 63.7619 | 0.18295 | 0.0085171 | 0.067182 | 0.067313 | 0.13014 | -0.0022131 | -0.0025913 | 0.32028 | -0.0061352 | 0.062128 | 0.06103 | 0.0024994 | -0.0062058 | 63.7253 | 63.9038 | -0.054932 | -59.1888 | 63.8123 | -59.0652 | -59.1293 | -58.9828 | 0.027466 | -59.23 | 63.826 | 63.7299 | -59.1385 | -59.2392 | -0.045777 | -0.10986 | 0.050354 | 122.9233 | -0.16937 | -0.05951 | -0.036621 | -0.11902 | -0.21973 | 0.064087 | 0.036621 | -0.21057 | 0.009155 | -0.032044 | 122.8317 | 122.7448 | 58.9645 | -122.8912 | 122.8455 | 122.7493 | 59.0469 | -123.0011
754.0156 | 122.9599 | -59.0561 | 63.8306 | 0.037994 | 0.014712 | 0.066755 | 0.073294 | 0.13121 | 0.0016321 | -0.0043003 | 0.0914 | -0.0048536 | 0.064051 | 0.059321 | 0.0031402 | -0.005565 | 63.7482 | 63.8123 | -0.091553 | -59.2209 | 63.9038 | -59.079 | -59.1476 | -59.0378 | -0.036621 | -59.3216 | 63.8535 | 63.8077 | -59.1614 | -59.2484 | -0.022888 | -0.091553 | 0.073243 | 122.8683 | -0.16479 | -0.073242 | -0.082397 | -0.10529 | -0.19226 | 0.022889 | 0.01831 | -0.2655 | -0.073242 | -0.022888 | 122.9599 | 122.8043 | 58.9645 | -122.9782 | 122.9095 | 122.8638 | 59.0195 | -123.0789
755.0156 | 123.0606 | -59.0332 | 63.8397 | 0.11429 | 0.011081 | 0.067396 | 0.070731 | 0.12993 | 0.0033411 | -0.0036595 | 0.0074766 | -0.005708 | 0.063837 | 0.061244 | 0.0033538 | -0.0059922 | 63.7802 | 63.8718 | -0.036621 | -59.1888 | 63.8901 | -59.0607 | -59.1385 | -59.0057 | 0.018311 | -59.2941 | 63.8855 | 63.8397 | -59.1431 | -59.23 | -0.027466 | -0.10529 | 0.050354 | 122.905 | -0.15564 | -0.050354 | -0.05951 | -0.10986 | -0.19684 | 0.045776 | 0.027466 | -0.26093 | -0.064086 | 0 | 122.9233 | 122.8134 | 58.9966 | -122.9782 | 122.9187 | 122.8729 | 59.0515 | -123.0698
756.0156 | 122.9965 | -59.0561 | 63.8351 | 0.045624 | 0.010013 | 0.065687 | 0.069876 | 0.13014 | 0.00077755 | -0.0025913 | -0.023041 | -0.0042126 | 0.062128 | 0.061671 | 0.0029266 | -0.0040696 | 63.7253 | 63.7985 | -0.09613 | -59.2484 | 63.8809 | -59.0836 | -59.1522 | -59.0561 | -0.036621 | -59.317 | 63.8809 | 63.8168 | -59.1705 | -59.2392 | -0.027466 | -0.096131 | 0.045776 | 122.8546 | -0.19226 | -0.09613 | -0.10986 | -0.11444 | -0.18311 | 0.045776 | 0 | -0.26093 | -0.07782 | -0.018311 | 122.937 | 122.7814 | 58.96 | -122.9874 | 122.937 | 122.8729 | 59.0195 | -123.0743
757.0156 | 123.0423 | -59.0607 | 63.8168 | -0.17563 | 0.011722 | 0.066541 | 0.06774 | 0.13228 | -0.00029045 | -0.0025913 | 0.25925 | -0.0042126 | 0.065119 | 0.060389 | 0.0020722 | -0.0070602 | 63.6887 | 63.7848 | -0.14191 | -59.2575 | 63.8535 | -59.1064 | -59.1522 | -59.0378 | -0.082397 | -59.3262 | 63.8397 | 63.826 | -59.1843 | -59.2575 | -0.045776 | -0.091553 | 0.036622 | 122.8455 | -0.19684 | -0.10528 | -0.12817 | -0.1236 | -0.19684 | 0.022889 | 0.022888 | -0.2655 | -0.068665 | 0.009156 | 122.9141 | 122.7493 | 58.9188 | -122.9691 | 122.9004 | 122.8867 | 58.9783 | -123.0743
758.0312 | 123.1064 | -59.0332 | 63.7985 | 0.20584 | 0.01044 | 0.068464 | 0.071158 | 0.13035 | -0.0022131 | -0.0032321 | 0.28214 | -0.003999 | 0.065119 | 0.06103 | 0.0033538 | -0.0062058 | 63.7436 | 63.8397 | -0.091553 | -59.2255 | 63.8397 | -59.0652 | -59.1385 | -58.9691 | 0.022888 | -59.2392 | 63.8397 | 63.7665 | -59.1476 | -59.2346 | -0.032044 | -0.10529 | 0.041199 | 122.8729 | -0.19226 | -0.086975 | -0.054932 | -0.11444 | -0.20142 | 0.041199 | 0.064087 | -0.20599 | -0.004578 | -0.032044 | 122.8729 | 122.7768 | 58.9417 | -122.937 | 122.8729 | 122.7997 | 59.0561 | -123.0331
759.0156 | 123.0103 | -59.0378 | 63.8351 | -0.96909 | 0.012362 | 0.065473 | 0.069876 | 0.12928 | 0.00035035 | -0.0032321 | 0.19821 | -0.003999 | 0.064051 | 0.060389 | 0.0035674 | -0.0057786 | 63.6749 | 63.8031 | -0.12817 | -59.2667 | 63.9084 | -59.0881 | -59.1522 | -59.0469 | -0.07782 | -59.3308 | 63.8626 | 63.7985 | -59.1705 | -59.2621 | -0.050354 | -0.11444 | 0.073242 | 122.8409 | -0.22888 | -0.11444 | -0.16022 | -0.13275 | -0.2243 | 0.027466 | -0.009155 | -0.29297 | -0.068665 | -0.036621 | 122.9462 | 122.7127 | 58.9096 | -122.9874 | 122.9004 | 122.8363 | 58.96 | -123.0972
760.0156 | 123.0194 | -59.0286 | 63.8306 | -0.061188 | 0.011508 | 0.065901 | 0.071585 | 0.13228 | 0.0020593 | -0.0036595 | 0.076141 | -0.0050672 | 0.065119 | 0.060816 | 0.0042084 | -0.0068466 | 63.7665 | 63.8306 | -0.073242 | -59.23 | 63.8901 | -59.0652 | -59.1522 | -59.024 | -0.018311 | -59.3124 | 63.858 | 63.8168 | -59.166 | -59.2712 | -0.036622 | -0.1236 | 0.05951 | 122.8592 | -0.20142 | -0.07782 | -0.064087 | -0.13733 | -0.24262 | 0.027466 | 0.004577 | -0.28381 | -0.041199 | -0.013733 | 122.9187 | 122.7951 | 58.9554 | -122.9828 | 122.8867 | 122.8455 | 59.0103 | -123.1018
761.0156 | 122.9828 | -59.0561 | 63.826 | -0.0383 | 0.011081 | 0.066541 | 0.069449 | 0.12928 | 0.0014185 | -0.0019505 | 0.037995 | -0.0050672 | 0.062982 | 0.063166 | 0.0037812 | -0.003215 | 63.7619 | 63.8489 | -0.054932 | -59.2209 | 63.8718 | -59.0698 | -59.1293 | -59.0424 | -0.009155 | -59.317 | 63.8489 | 63.8306 | -59.1705 | -59.2575 | -0.013733 | -0.073242 | 0.045776 | 122.905 | -0.16479 | -0.091553 | -0.064087 | -0.11444 | -0.20142 | 0.022888 | 0.013733 | -0.26093 | -0.05951 | 0.004577 | 122.9279 | 122.818 | 59.0012 | -122.9553 | 122.905 | 122.8867 | 59.0469 | -123.0835
762.0156 | 123.024 | -59.0607 | 63.8214 | 0.099029 | 0.013217 | 0.065473 | 0.069235 | 0.13057 | -0.0015723 | -0.0043003 | 4.0053 | -0.0025038 | 0.061914 | 0.059748 | 0.0024994 | -0.0030014 | 63.6887 | 63.7436 | -0.16022 | -59.285 | 63.8855 | -59.1019 | -59.1476 | -59.1156 | 0.050354 | -59.3124 | 63.8718 | 63.8397 | -59.1705 | -59.2529 | -0.041199 | -0.086975 | 0.064087 | 122.8043 | -0.2243 | -0.13733 | -0.13275 | -0.10986 | -0.19226 | 0.050354 | -0.054932 | -0.25177 | -0.059509 | 0.018311 | 122.9462 | 122.7493 | 58.9005 | -122.9691 | 122.9324 | 122.9004 | 59.111 | -123.0743
763.0156 | 123.111 | -59.0012 | 63.8031 | 0.19058 | 0.0097989 | 0.063978 | 0.068167 | 0.12971 | -0.0013587 | -0.0023777 | 0.29739 | -0.005708 | 0.062769 | 0.059748 | 0.0033538 | -0.0042832 | 63.739 | 63.8443 | -0.11444 | -59.23 | 63.8443 | -59.0881 | -59.1248 | -58.9828 | 0.009155 | -59.2255 | 63.8351 | 63.7939 | -59.1476 | -59.2346 | -0.086975 | -0.1236 | 0.041198 | 122.8455 | -0.22888 | -0.10529 | -0.064087 | -0.14648 | -0.23346 | 0.032043 | 0.018311 | -0.2243 | 0.009155 | -0.009156 | 122.8455 | 122.7402 | 58.8867 | -122.9279 | 122.8363 | 122.7951 | 59.0103 | -123.0377
764.0156 | 123.0469 | -59.024 | 63.8397 | -0.084076 | 0.013003 | 0.06825 | 0.071799 | 0.1295 | 0.0031273 | -0.0030185 | -0.076446 | -0.0044264 | 0.06341 | 0.060603 | 0.0029266 | -0.0053512 | 63.7161 | 63.9084 | -0.045776 | -59.1843 | 63.8992 | -59.0515 | -59.1248 | -58.9966 | 0.045776 | -59.285 | 63.8718 | 63.7894 | -59.1705 | -59.2438 | -0.027466 | -0.10071 | 0.059509 | 122.9324 | -0.16022 | -0.059509 | -0.1236 | -0.14648 | -0.21973 | 0.032043 | 0.027466 | -0.26093 | -0.041199 | -0.050354 | 122.9233 | 122.7402 | 58.9783 | -122.9645 | 122.8958 | 122.8134 | 59.0698 | -123.0835
765.0156 | 123.0286 | -59.0103 | 63.8626 | -0.10696 | 0.013003 | 0.066969 | 0.072226 | 0.13121 | 0.0016321 | -0.0023777 | -0.41214 | -0.0052808 | 0.064051 | 0.061244 | 0.0035674 | -0.0057786 | 63.7756 | 63.8718 | -0.018311 | -59.2117 | 63.8947 | -59.0652 | -59.1339 | -58.9691 | 0.045776 | -59.2621 | 63.8809 | 63.8031 | -59.166 | -59.2484 | -0.054932 | -0.1236 | 0.032043 | 122.8821 | -0.20142 | -0.07782 | -0.086975 | -0.15564 | -0.23804 | 0.01831 | 0.041199 | -0.25177 | -0.013733 | -0.059509 | 122.905 | 122.7859 | 58.992 | -122.9965 | 122.8912 | 122.8134 | 59.0561 | -123.111
766.0156 | 122.9919 | -59.0332 | 63.8306 | -0.084076 | 0.013858 | 0.068464 | 0.073721 | 0.12928 | 0.0018457 | -0.0034457 | -0.00015237 | -0.00464 | 0.065546 | 0.063166 | 0.0039948 | -0.0057786 | 63.7665 | 63.8626 | -0.045776 | -59.2163 | 63.8855 | -59.0836 | -59.1476 | -59.024 | 0.004578 | -59.2804 | 63.8992 | 63.8306 | -59.1705 | -59.2438 | -0.050354 | -0.11444 | 0.054932 | 122.8958 | -0.18311 | -0.068665 | -0.064087 | -0.13733 | -0.21057 | 0.068665 | 0.009155 | -0.24719 | -0.036622 | 0 | 122.9187 | 122.7997 | 58.9874 | -122.9782 | 122.9324 | 122.8638 | 59.0378 | -123.0743
767.0156 | 122.8592 | -59.0652 | 63.7848 | 0.12192 | 0.010867 | 0.067396 | 0.069876 | 0.12843 | -7.6852e-05 | -0.0034457 | 0.12192 | -0.0050672 | 0.0664 | 0.060603 | 0.0024994 | -0.005565 | 63.6749 | 63.7527 | -0.14191 | -59.285 | 63.8809 | -59.0973 | -59.1522 | -59.0698 | -0.082397 | -59.3445 | 63.8809 | 63.826 | -59.2072 | -59.2712 | -0.032043 | -0.086975 | 0.09613 | 122.818 | -0.21973 | -0.13275 | -0.10986 | -0.14191 | -0.20599 | 0.09613 | -0.004577 | -0.27923 | -0.073242 | 0.041199 | 122.9462 | 122.7402 | 58.9233 | -122.937 | 122.9462 | 122.8912 | 58.9828 | -123.056
768.0156 | 123.1384 | -59.0103 | 63.7619 | 0.12955 | 0.0093717 | 0.066755 | 0.067954 | 0.13014 | -0.0034949 | -0.0025913 | 0.29739 | -0.0050672 | 0.063623 | 0.060389 | 0.0037812 | -0.0068466 | 63.7711 | 63.8947 | -0.054932 | -59.1934 | 63.8077 | -59.079 | -59.1476 | -58.96 | 0.009155 | -59.2255 | 63.7894 | 63.7436 | -59.1476 | -59.2621 | -0.068664 | -0.13733 | 0.045776 | 122.905 | -0.18311 | -0.045776 | 0.009155 | -0.13733 | -0.25177 | 0.027466 | 0.050354 | -0.21515 | 0.036621 | -0.018311 | 122.818 | 122.7814 | 58.9554 | -122.9095 | 122.7997 | 122.7539 | 59.0195 | -123.024
769.0156 | 123.024 | -59.0332 | 63.826 | -0.00015269 | 0.010226 | 0.065901 | 0.072012 | 0.13163 | -0.00093145 | -0.0032321 | 0.015106 | -0.0061352 | 0.065332 | 0.063166 | 0.0042084 | -0.0047104 | 63.7711 | 63.8901 | -0.045776 | -59.2072 | 63.9038 | -59.079 | -59.1431 | -59.0057 | 0 | -59.2896 | 63.8901 | 63.8077 | -59.1705 | -59.2346 | -0.045776 | -0.10986 | 0.07782 | 122.9233 | -0.17395 | -0.064087 | -0.054932 | -0.13733 | -0.20142 | 0.064087 | 0.027466 | -0.25635 | -0.054932 | -0.018311 | 122.937 | 122.8043 | 58.9874 | -122.9691 | 122.9233 | 122.8409 | 59.0332 | -123.0606
770.0156 | 123.024 | -59.024 | 63.8489 | 0.060882 | 0.011508 | 0.06761 | 0.071372 | 0.13057 | 0.00077755 | -0.0017369 | -0.015411 | -0.0033582 | 0.066187 | 0.059321 | 0.0039948 | -0.0047104 | 63.7665 | 63.8901 | -0.036621 | -59.198 | 63.8672 | -59.079 | -59.1431 | -59.0057 | 0.041199 | -59.2804 | 63.8626 | 63.8123 | -59.1568 | -59.2346 | -0.054931 | -0.11902 | 0.01831 | 122.9141 | -0.17395 | -0.054932 | -0.082398 | -0.13275 | -0.21057 | 0.013733 | 0.018311 | -0.25635 | -0.045777 | -0.036621 | 122.8912 | 122.7905 | 58.9874 | -122.9919 | 122.8867 | 122.8363 | 59.0652 | -123.0835
771.0156 | 123.0057 | -59.024 | 63.8855 | -0.18326 | 0.0080899 | 0.066755 | 0.069663 | 0.13035 | 0.0012047 | -0.0055821 | -0.14511 | -0.005708 | 0.060846 | 0.058253 | 0.0018584 | -0.0034286 | 63.7207 | 63.8306 | -0.032043 | -59.2072 | 63.9038 | -59.0698 | -59.1431 | -59.0286 | 0.059509 | -59.285 | 63.9175 | 63.8397 | -59.166 | -59.2163 | -0.045776 | -0.11902 | 0.018311 | 122.8546 | -0.1831 | -0.064087 | -0.16479 | -0.14191 | -0.19226 | 0.032044 | -0.004577 | -0.26093 | -0.068664 | -0.045776 | 122.9279 | 122.7448 | 58.992 | -123.0286 | 122.9416 | 122.8638 | 59.0836 | -123.1018
772.0156 | 123.0011 | -59.0149 | 63.8718 | -0.32059 | 0.0091581 | 0.070173 | 0.07009 | 0.13035 | -0.0022131 | -0.0038731 | -0.11459 | -0.0016492 | 0.064051 | 0.059321 | -6.4178e-05 | -0.0042832 | 63.7115 | 63.826 | -0.050354 | -59.2163 | 63.913 | -59.0561 | -59.1248 | -59.0286 | 0.054932 | -59.2804 | 63.8992 | 63.8306 | -59.1751 | -59.2392 | -0.041198 | -0.10986 | 0.041199 | 122.8409 | -0.20142 | -0.091553 | -0.16022 | -0.16022 | -0.2243 | 0.027466 | -0.013732 | -0.2655 | -0.041199 | -0.041199 | 122.9279 | 122.7264 | 58.9645 | -122.9965 | 122.9141 | 122.8455 | 59.0698 | -123.111
773.0156 | 123.0377 | -59.0424 | 63.8351 | 0.0914 | 0.012149 | 0.065687 | 0.072226 | 0.12993 | 0.00056395 | -0.0010959 | 0.18295 | -0.0042126 | 0.064905 | 0.059321 | -6.4178e-05 | -0.0059922 | 63.6566 | 63.7527 | -0.13733 | -59.2621 | 63.8855 | -59.0881 | -59.1522 | -58.905 | -0.24719 | -59.3124 | 63.8763 | 63.8306 | -59.1751 | -59.2667 | -0.045777 | -0.10986 | 0.050354 | 122.7951 | -0.21973 | -0.10986 | -0.17853 | -0.13275 | -0.22431 | 0.041199 | 0.13733 | -0.27008 | -0.045776 | -0.004578 | 122.9279 | 122.699 | 58.905 | -122.9874 | 122.9187 | 122.8729 | 58.7952 | -123.1018
774.0156 | 123.0286 | -59.0149 | 63.8306 | -0.14511 | 0.013431 | 0.066114 | 0.070517 | 0.12993 | 0.0020593 | -0.0030185 | -0.053558 | -0.0052808 | 0.065759 | 0.058253 | 0.0037812 | -0.0072738 | 63.7527 | 63.8947 | -0.013733 | -59.1888 | 63.9084 | -59.0469 | -59.1385 | -59.0012 | 0.059509 | -59.2712 | 63.8809 | 63.8077 | -59.1614 | -59.2438 | -0.032043 | -0.1236 | 0.07782 | 122.9095 | -0.17395 | -0.050354 | -0.077819 | -0.14648 | -0.22888 | 0.050354 | 0.013733 | -0.25635 | -0.027466 | -0.022888 | 122.9233 | 122.7676 | 59.0012 | -122.9691 | 122.8958 | 122.8226 | 59.0744 | -123.0743
775.0156 | 122.9965 | -59.0286 | 63.8535 | -0.053558 | 0.013431 | 0.066541 | 0.070731 | 0.13035 | 0.0012047 | -0.0036595 | 0.030365 | -0.0033582 | 0.065119 | 0.06103 | 0.0022858 | -0.0053512 | 63.7299 | 63.858 | -0.068665 | -59.2255 | 63.8992 | -59.0698 | -59.1293 | -59.0332 | -0.013733 | -59.317 | 63.8626 | 63.8123 | -59.1797 | -59.2529 | -0.041199 | -0.10071 | 0.045776 | 122.8867 | -0.19684 | -0.096131 | -0.1236 | -0.15106 | -0.22431 | 0.009155 | -0.004578 | -0.28839 | -0.064087 | -0.041199 | 122.9279 | 122.7585 | 58.96 | -122.9828 | 122.8912 | 122.8409 | 59.0149 | -123.1064
776.0156 | 123.0194 | -59.0195 | 63.8535 | -0.21378 | 0.01044 | 0.065473 | 0.071372 | 0.13142 | -0.0013587 | -0.0023777 | -0.18326 | -0.002931 | 0.067255 | 0.060389 | 0.002713 | -0.0068466 | 63.7344 | 63.8672 | -0.027466 | -59.1751 | 63.9038 | -59.0698 | -59.111 | -58.992 | 0.086975 | -59.2575 | 63.8901 | 63.8168 | -59.1614 | -59.2163 | -0.050354 | -0.091553 | 0.050354 | 122.8867 | -0.15564 | -0.064087 | -0.11902 | -0.14191 | -0.19684 | 0.036621 | 0.027466 | -0.23804 | -0.041198 | -0.036622 | 122.9233 | 122.7539 | 58.992 | -122.9645 | 122.9095 | 122.8363 | 59.1064 | -123.0698
777.0156 | 123.0377 | -59.0057 | 63.8672 | -0.16037 | 0.010867 | 0.066969 | 0.071799 | 0.12843 | -0.00050425 | -0.0025913 | -0.16037 | -0.0054944 | 0.065546 | 0.060816 | 0.0016448 | -0.0062058 | 63.7299 | 63.8489 | -0.045776 | -59.1934 | 63.9175 | -59.0515 | -59.1476 | -59.0195 | 0.064087 | -59.2438 | 63.9038 | 63.8535 | -59.1568 | -59.2209 | -0.045777 | -0.14191 | 0.050355 | 122.8546 | -0.18768 | -0.045776 | -0.13733 | -0.15106 | -0.21515 | 0.036622 | -0.013733 | -0.23804 | -0.022888 | -0.013732 | 122.9233 | 122.7356 | 58.96 | -123.0148 | 122.9095 | 122.8592 | 59.0698 | -123.0881
778.0156 | 123.0743 | -59.0195 | 63.7711 | 0.15244 | 0.011935 | 0.068891 | 0.067526 | 0.12758 | -0.00071785 | -0.0017369 | 0.28214 | -0.0042126 | 0.063837 | 0.064021 | 0.0035674 | -0.0059922 | 63.6932 | 63.8214 | -0.11444 | -59.2438 | 63.8672 | -59.079 | -59.1614 | -59.0012 | -0.036621 | -59.2575 | 63.8397 | 63.7619 | -59.1476 | -59.2529 | -0.059509 | -0.14191 | 0.09613 | 122.8409 | -0.2243 | -0.082397 | -0.07782 | -0.12817 | -0.23346 | 0.068665 | 0.01831 | -0.23804 | -0.004577 | -0.009155 | 122.8867 | 122.7127 | 58.905 | -122.9324 | 122.8592 | 122.7814 | 58.9828 | -123.024
779.0156 | 123.0423 | -59.024 | 63.8306 | -0.03067 | 0.011935 | 0.065473 | 0.072867 | 0.12864 | -0.00050425 | -0.0043003 | 0.41183 | -0.003999 | 0.065973 | 0.061457 | 0.0022858 | -0.0074876 | 63.7665 | 63.8809 | -0.032043 | -59.1888 | 63.8855 | -59.0607 | -59.1476 | -58.9874 | 0.082397 | -59.2712 | 63.8809 | 63.8123 | -59.1522 | -59.23 | -0.036621 | -0.1236 | 0.054932 | 122.905 | -0.16479 | -0.041199 | -0.064087 | -0.12817 | -0.20599 | 0.050354 | 0.036621 | -0.24719 | -0.041198 | -0.01831 | 122.9095 | 122.7905 | 58.992 | -122.9782 | 122.905 | 122.8363 | 59.1064 | -123.0606
780.0156 | 123.0331 | -59.0149 | 63.8489 | -0.22903 | 0.011508 | 0.06761 | 0.070517 | 0.13185 | 0.00013675 | -0.0019505 | -0.14511 | -0.0052808 | 0.063623 | 0.059748 | 0.0024994 | -0.0047104 | 63.7299 | 63.8672 | -0.036621 | -59.2072 | 63.8718 | -59.0698 | -59.1385 | -58.9828 | 0.082397 | -59.2529 | 63.8718 | 63.8306 | -59.1293 | -59.23 | -0.054931 | -0.1236 | 0.022888 | 122.8821 | -0.19226 | -0.068664 | -0.11902 | -0.11444 | -0.21515 | 0.022888 | 0.032044 | -0.23804 | -0.022888 | -0.018311 | 122.8867 | 122.7448 | 58.9783 | -122.9874 | 122.8867 | 122.8455 | 59.0973 | -123.0789
781.0156 | 123.0331 | -59.0012 | 63.8672 | -0.16037 | 0.0095853 | 0.067182 | 0.072226 | 0.1295 | -0.00093145 | -0.0038731 | -0.14511 | -0.0054944 | 0.06341 | 0.057612 | 0.0012176 | -0.005565 | 63.7115 | 63.858 | -0.022888 | -59.198 | 63.913 | -59.0515 | -59.1202 | -59.0195 | 0.07782 | -59.2529 | 63.8947 | 63.826 | -59.1568 | -59.2346 | -0.050354 | -0.11902 | 0.045777 | 122.8592 | -0.19684 | -0.07782 | -0.15564 | -0.15564 | -0.23346 | 0.027466 | -0.01831 | -0.25177 | -0.018311 | -0.041198 | 122.9141 | 122.7127 | 58.9783 | -122.9874 | 122.8958 | 122.8271 | 59.079 | -123.1018
782.0156 | 123.024 | -59.0286 | 63.8168 | -0.12985 | 0.013003 | 0.06825 | 0.070731 | 0.12928 | -0.00050425 | -0.00045506 | -0.045929 | -0.0052808 | 0.065546 | 0.059962 | 0.0037812 | -0.005565 | 63.7436 | 63.8855 | -0.018311 | -59.1934 | 63.8901 | -59.079 | -59.1248 | -58.992 | 0.068665 | -59.2621 | 63.8763 | 63.8031 | -59.1614 | -59.2392 | -0.050354 | -0.096131 | 0.073243 | 122.9141 | -0.1648 | -0.068664 | -0.073242 | -0.13275 | -0.21057 | 0.05951 | 0.036621 | -0.23346 | -0.022888 | -0.013732 | 122.9187 | 122.7722 | 59.0103 | -122.9416 | 122.905 | 122.8317 | 59.0973 | -123.056
783.0156 | 123.0011 | -59.0424 | 63.8351 | -2.9756 | 0.0091581 | 0.065046 | 0.071372 | 0.13014 | -7.6852e-05 | -0.0015231 | 0.25162 | -0.0059216 | 0.065759 | 0.061244 | 0.0033538 | -0.0042832 | 63.6383 | 63.8306 | -0.11444 | -59.2575 | 63.8855 | -59.0744 | -59.1385 | -59.0469 | -0.07782 | -59.3353 | 63.8718 | 63.7756 | -59.1934 | -59.2758 | -0.032044 | -0.096131 | 0.050354 | 122.8729 | -0.21515 | -0.11902 | -0.19684 | -0.15106 | -0.23346 | 0.036621 | -0.004578 | -0.29297 | -0.059509 | -0.059509 | 122.9279 | 122.6807 | 58.9279 | -122.9736 | 122.9141 | 122.818 | 58.9645 | -123.111
784.0156 | 123.0286 | -59.0195 | 63.8855 | -0.19852 | 0.0091581 | 0.06761 | 0.072867 | 0.13121 | -0.0017859 | -0.0062229 | -0.099335 | -0.0027174 | 0.065546 | 0.060816 | 0.002713 | -0.0047104 | 63.707 | 63.8443 | -0.045776 | -59.2026 | 63.8763 | -59.0652 | -59.1339 | -59.0149 | 0.050354 | -59.285 | 63.9038 | 63.8306 | -59.1431 | -59.2209 | -0.045777 | -0.11444 | -0.009155 | 122.8638 | -0.18311 | -0.068665 | -0.17853 | -0.1236 | -0.20142 | 0.018311 | 0.004577 | -0.2655 | -0.064087 | -0.054932 | 122.8958 | 122.7264 | 58.9737 | -123.0194 | 122.9233 | 122.85 | 59.0698 | -123.1064
785.0156 | 123.0148 | -59.0195 | 63.9175 | -0.30533 | 0.0097989 | 0.068464 | 0.071158 | 0.13185 | -0.0039221 | -0.0064365 | -0.091705 | -0.0054944 | 0.063837 | 0.059107 | 0.002713 | -0.004924 | 63.6932 | 63.8535 | -0.027466 | -59.2026 | 63.9084 | -59.0698 | -59.1293 | -59.0424 | 0.050354 | -59.2667 | 63.913 | 63.8397 | -59.1614 | -59.2392 | -0.050354 | -0.10986 | -0.009156 | 122.8729 | -0.18311 | -0.073243 | -0.2243 | -0.14191 | -0.21973 | -0.004578 | -0.022888 | -0.24719 | -0.027466 | -0.07782 | 122.9279 | 122.7127 | 58.992 | -123.0469 | 122.9324 | 122.8592 | 59.0698 | -123.1567
786.0156 | 123.0515 | -58.9966 | 63.858 | -0.20615 | 0.013003 | 0.068464 | 0.070944 | 0.12822 | 0.0020593 | -0.0028049 | -0.12985 | -0.0050672 | 0.061701 | 0.061885 | 0.0024994 | -0.0053512 | 63.7115 | 63.858 | -0.032043 | -59.198 | 63.913 | -59.0561 | -59.1248 | -59.0012 | 0.054932 | -59.2575 | 63.8901 | 63.7802 | -59.1385 | -59.2529 | -0.059509 | -0.12817 | 0.054932 | 122.8546 | -0.20142 | -0.073242 | -0.14648 | -0.14191 | -0.25635 | 0.032044 | -0.004578 | -0.26093 | -0.004577 | -0.07782 | 122.9095 | 122.7081 | 58.9645 | -122.9828 | 122.8867 | 122.7768 | 59.0515 | -123.111
787.0156 | 122.9965 | -59.0012 | 63.8397 | -0.076447 | 0.013644 | 0.062696 | 0.073081 | 0.13121 | 0.00035035 | -0.0034457 | -0.00015237 | -0.0033582 | 0.062769 | 0.061457 | 0.0052764 | -0.004924 | 63.739 | 63.8855 | -0.041199 | -59.2026 | 63.8901 | -59.0881 | -59.1248 | -58.9874 | 0.050354 | -59.2712 | 63.8672 | 63.7985 | -59.1843 | -59.2575 | -0.086975 | -0.1236 | 0.050354 | 122.8867 | -0.20142 | -0.07782 | -0.10071 | -0.18311 | -0.25635 | 0.027465 | 0.013733 | -0.27008 | -0.013733 | -0.041199 | 122.8912 | 122.7402 | 58.96 | -122.9645 | 122.8683 | 122.7997 | 59.0515 | -123.0972
788.0156 | 122.9874 | -59.0515 | 63.8397 | 0.068512 | 0.014926 | 0.066541 | 0.071585 | 0.13121 | -0.00050425 | -0.0019505 | 0.037995 | -0.0044264 | 0.065546 | 0.060816 | 0.0039948 | -0.004924 | 63.7024 | 63.7985 | -0.1236 | -59.2621 | 63.8855 | -59.1019 | -59.1202 | -59.0927 | -0.082397 | -59.3765 | 63.8901 | 63.8168 | -59.1797 | -59.2529 | -0.050354 | -0.068664 | 0.045776 | 122.85 | -0.21057 | -0.14191 | -0.13733 | -0.12817 | -0.20142 | 0.050354 | -0.041198 | -0.32501 | -0.1236 | -0.022889 | 122.937 | 122.7539 | 58.9279 | -122.9599 | 122.9416 | 122.8683 | 58.9691 | -123.0927
789.0156 | 123.0148 | -59.0103 | 63.8626 | -0.0383 | 0.0085171 | 0.068037 | 0.070731 | 0.12822 | -0.0017859 | -0.0043003 | -0.12985 | -0.0025038 | 0.062769 | 0.061671 | 0.0024994 | -0.0044968 | 63.7299 | 63.8443 | -0.045776 | -59.2346 | 63.9038 | -59.0698 | -59.1385 | -59.024 | 0.036621 | -59.285 | 63.9084 | 63.8489 | -59.1385 | -59.2346 | -0.059509 | -0.12817 | 0.041199 | 122.8546 | -0.2243 | -0.09613 | -0.13275 | -0.12817 | -0.2243 | 0.045776 | -0.013733 | -0.27466 | -0.050354 | -0.013733 | 122.9141 | 122.7402 | 58.9645 | -123.0011 | 122.9187 | 122.8592 | 59.0469 | -123.0972
790.0156 | 123.0103 | -59.024 | 63.8626 | -0.13748 | 0.011081 | 0.066114 | 0.071799 | 0.12886 | -0.0015723 | -0.0047275 | -0.16037 | -0.0044264 | 0.063196 | 0.060816 | 0.0024994 | -0.0064194 | 63.7299 | 63.858 | -0.032043 | -59.1797 | 63.9404 | -59.0515 | -59.1476 | -59.0103 | 0.086975 | -59.2484 | 63.9038 | 63.8306 | -59.1705 | -59.2392 | -0.027466 | -0.1236 | 0.07782 | 122.8821 | -0.15564 | -0.032043 | -0.13275 | -0.14648 | -0.21515 | 0.041199 | 0.013733 | -0.2243 | -0.009155 | -0.032044 | 122.9645 | 122.7539 | 58.992 | -123.0103 | 122.9279 | 122.8546 | 59.111 | -123.1018
791.0156 | 123.0515 | -59.0332 | 63.8672 | -0.14511 | 0.01279 | 0.063978 | 0.072012 | 0.12928 | 0.00099115 | -0.0030185 | -0.03067 | -0.003999 | 0.066187 | 0.061671 | 0.0031402 | -0.0068466 | 63.7619 | 63.8763 | -0.022888 | -59.1797 | 63.8901 | -59.0836 | -59.1339 | -58.9874 | 0.059509 | -59.2667 | 63.8809 | 63.8123 | -59.1705 | -59.2255 | -0.050354 | -0.10071 | 0.022889 | 122.9095 | -0.14648 | -0.045776 | -0.10529 | -0.13733 | -0.19226 | 0.013733 | 0.045776 | -0.23346 | -0.041199 | -0.054931 | 122.9233 | 122.7951 | 59.0103 | -123.0011 | 122.9141 | 122.8455 | 59.0927 | -123.0927
792.0156 | 123.0103 | -59.0378 | 63.8718 | -0.25192 | 0.0076627 | 0.069532 | 0.070517 | 0.13249 | -0.0049903 | -0.0055821 | -0.091705 | -0.0067762 | 0.061914 | 0.060389 | 0.00057682 | -0.0047104 | 63.7482 | 63.9221 | 0.027466 | -59.1797 | 63.8809 | -59.0561 | -59.111 | -59.0057 | 0.07782 | -59.2621 | 63.9038 | 63.8351 | -59.1568 | -59.2346 | -0.01831 | -0.073242 | 0.009155 | 122.9599 | -0.14191 | -0.068664 | -0.1236 | -0.11902 | -0.19684 | 0.032044 | 0.032044 | -0.2243 | -0.027466 | -0.036621 | 122.9187 | 122.7859 | 59.0652 | -122.9828 | 122.9416 | 122.8729 | 59.1156 | -123.1064
793.0156 | 122.9736 | -59.0469 | 63.8123 | 0.022736 | 0.01279 | 0.065473 | 0.07009 | 0.13057 | -7.6852e-05 | -0.0047275 | 0.083771 | -0.0033582 | 0.063623 | 0.059962 | 0.0024994 | -0.0059922 | 63.6978 | 63.8031 | -0.12817 | -59.2484 | 63.8992 | -59.0881 | -59.1522 | -59.079 | -0.086975 | -59.3628 | 63.8763 | 63.7985 | -59.1797 | -59.2575 | -0.041199 | -0.10529 | 0.086975 | 122.85 | -0.20142 | -0.09613 | -0.11444 | -0.13275 | -0.21057 | 0.064087 | -0.032043 | -0.31586 | -0.10529 | -0.013733 | 122.9462 | 122.7448 | 58.9188 | -122.9645 | 122.9233 | 122.8455 | 58.96 | -123.0698
794.0156 | 123.0148 | -59.0195 | 63.8763 | -0.31296 | 0.0093717 | 0.067823 | 0.068594 | 0.13185 | 0.00013675 | -0.0043003 | -0.091705 | -0.0048536 | 0.064691 | 0.059107 | 0.0029266 | -0.0034286 | 63.6932 | 63.8489 | -0.059509 | -59.2072 | 63.9221 | -59.0744 | -59.1431 | -59.0332 | 0.050354 | -59.285 | 63.913 | 63.8397 | -59.1385 | -59.2117 | -0.054932 | -0.1236 | 0.045776 | 122.8683 | -0.18768 | -0.064087 | -0.18311 | -0.11902 | -0.19226 | 0.036621 | -0.013733 | -0.2655 | -0.073242 | -0.036621 | 122.9416 | 122.7127 | 58.96 | -123.0194 | 122.9324 | 122.8592 | 59.0698 | -123.0881
795.0156 | 123.0286 | -59.0332 | 63.8489 | -0.19852 | 0.010226 | 0.06761 | 0.07009 | 0.13014 | -0.00093145 | -0.0040867 | -0.16037 | -0.0050672 | 0.062342 | 0.061244 | 0.0018584 | -0.0059922 | 63.7299 | 63.8672 | -0.032043 | -59.1888 | 63.9175 | -59.0607 | -59.1248 | -59.0103 | 0.07782 | -59.2575 | 63.9084 | 63.8306 | -59.1568 | -59.2163 | -0.027466 | -0.091553 | 0.068665 | 122.9004 | -0.15564 | -0.064087 | -0.11902 | -0.1236 | -0.18311 | 0.059509 | 0.022888 | -0.2243 | -0.041198 | -0.018311 | 122.9507 | 122.7631 | 59.0012 | -122.9736 | 122.9416 | 122.8638 | 59.111 | -123.0652
796.0156 | 123.0606 | -59.0057 | 63.8535 | -0.22141 | 0.0061673 | 0.06761 | 0.068594 | 0.13185 | -0.0043495 | -0.0043003 | -0.061188 | -0.0086988 | 0.060846 | 0.06103 | 0.00036322 | -0.0027878 | 63.7711 | 63.9862 | 0.073242 | -59.1431 | 63.8626 | -59.0286 | -59.0652 | -58.9783 | 0.16479 | -59.2026 | 63.8489 | 63.8077 | -59.1476 | -59.2072 | -0.022888 | -0.05951 | 0.009155 | 122.9919 | -0.13733 | -0.077819 | -0.082398 | -0.14191 | -0.20142 | -0.004578 | 0.027466 | -0.19684 | 0.004577 | -0.045777 | 122.8683 | 122.7768 | 59.079 | -122.9187 | 122.8546 | 122.8134 | 59.1705 | -123.0606
797.0156 | 122.9874 | -59.0103 | 63.8672 | -0.25955 | 0.0089443 | 0.069105 | 0.071158 | 0.12993 | -0.0017859 | -0.0032321 | 0.09903 | -0.0050672 | 0.064264 | 0.060816 | 0.0031402 | -0.0030014 | 63.6063 | 64.0961 | 0.082397 | -59.3033 | 63.9404 | -59.0561 | -59.1431 | -59.0149 | 0.050354 | -59.2987 | 63.9359 | 63.8214 | -59.166 | -59.2163 | -0.045776 | -0.13275 | 0.073243 | 123.1064 | -0.29297 | -0.16022 | -0.26093 | -0.15564 | -0.20599 | 0.068665 | -0.004578 | -0.28839 | -0.082397 | -0.045776 | 122.9507 | 122.6166 | 59.0927 | -123.0103 | 122.9462 | 122.8317 | 59.0607 | -123.0835
798.0156 | 122.9736 | -59.0561 | 63.8397 | 0.083771 | 0.013858 | 0.066114 | 0.075003 | 0.12886 | 0.00013675 | -0.0019505 | 0.10666 | -0.0065626 | 0.064691 | 0.061457 | 0.0035674 | -0.0047104 | 63.6658 | 63.7985 | -0.12817 | -59.2712 | 63.8809 | -59.0881 | -59.1385 | -59.0744 | -0.10071 | -59.3674 | 63.8443 | 63.7894 | -59.1843 | -59.2575 | -0.032044 | -0.082398 | 0.041198 | 122.8546 | -0.21515 | -0.13275 | -0.17395 | -0.12817 | -0.20142 | 0.004577 | -0.018311 | -0.31128 | -0.10986 | -0.050354 | 122.937 | 122.7219 | 58.9279 | -122.9782 | 122.9004 | 122.8455 | 58.9554 | -123.0972
799.0156 | 123.0103 | -59.0332 | 63.8901 | -0.22903 | 0.010867 | 0.066114 | 0.069876 | 0.13121 | 0.00013675 | -0.0028049 | -0.13748 | -0.0048536 | 0.064051 | 0.059748 | 0.0012176 | -0.0077012 | 63.7299 | 63.8351 | -0.050354 | -59.2209 | 63.9084 | -59.0836 | -59.1202 | -59.0195 | 0.036621 | -59.2804 | 63.9084 | 63.8535 | -59.1431 | -59.2209 | -0.050354 | -0.086975 | 0.01831 | 122.8683 | -0.18768 | -0.10071 | -0.16022 | -0.10986 | -0.18768 | 0.01831 | 0.013733 | -0.24719 | -0.05951 | -0.036621 | 122.9416 | 122.7631 | 58.9828 | -123.0103 | 122.9416 | 122.8867 | 59.0698 | -123.111
800.0156 | 123.0286 | -59.024 | 63.8535 | -0.168 | 0.0095853 | 0.067396 | 0.070303 | 0.13099 | -0.00093145 | -0.0023777 | -0.061188 | -0.005708 | 0.062769 | 0.061671 | 0.004422 | -0.006633 | 63.7527 | 63.8809 | -0.018311 | -59.1705 | 63.9175 | -59.0469 | -59.1431 | -58.9874 | 0.10986 | -59.2484 | 63.8672 | 63.7985 | -59.1522 | -59.2209 | -0.022888 | -0.11902 | 0.064087 | 122.905 | -0.14648 | -0.027466 | -0.10071 | -0.12817 | -0.19684 | 0.013732 | 0.036621 | -0.2243 | -0.027466 | -0.054932 | 122.9416 | 122.7768 | 59.0057 | -122.9965 | 122.8912 | 122.8226 | 59.1339 | -123.0743
801.0156 | 122.9965 | -59.0149 | 63.8809 | -0.32059 | 0.010867 | 0.066755 | 0.07009 | 0.13206 | -0.0011451 | -0.0036595 | -0.11459 | -0.0035718 | 0.061273 | 0.06103 | 0.0022858 | -0.0034286 | 63.7115 | 63.8718 | -0.041199 | -59.198 | 63.9084 | -59.079 | -59.1293 | -59.0195 | 0.045776 | -59.2804 | 63.8901 | 63.8306 | -59.1705 | -59.23 | -0.064086 | -0.11444 | 0.027466 | 122.8867 | -0.1831 | -0.068665 | -0.16937 | -0.15564 | -0.21515 | 0.009156 | -0.004577 | -0.2655 | -0.050354 | -0.050354 | 122.9233 | 122.7264 | 58.9737 | -123.0103 | 122.905 | 122.8455 | 59.0607 | -123.111
802.0156 | 123.056 | -59.0057 | 63.8535 | -0.19089 | 0.011508 | 0.068678 | 0.070944 | 0.12886 | 0.00035035 | -0.0028049 | -0.14511 | -0.0044264 | 0.065332 | 0.060603 | 0.0022858 | -0.0036424 | 63.7115 | 63.8763 | -0.036621 | -59.198 | 63.9221 | -59.0561 | -59.1202 | -59.0103 | 0.091553 | -59.2575 | 63.8855 | 63.8123 | -59.1751 | -59.2484 | -0.050354 | -0.11444 | 0.068664 | 122.8821 | -0.19226 | -0.07782 | -0.14191 | -0.16937 | -0.24261 | 0.032043 | -0.004578 | -0.25177 | -0.009155 | -0.041199 | 122.9279 | 122.7173 | 58.9691 | -122.9736 | 122.8912 | 122.818 | 59.0973 | -123.1018
803.0156 | 123.0286 | -59.0515 | 63.8214 | 0.11429 | 0.0087307 | 0.06761 | 0.070731 | 0.12907 | -0.00050425 | -0.0043003 | 0.19821 | -0.0037854 | 0.063196 | 0.061457 | 0.0037812 | -0.003856 | 63.6887 | 63.826 | -0.14191 | -59.2438 | 63.8718 | -59.0927 | -59.1522 | -59.024 | -0.07782 | -59.3033 | 63.8672 | 63.7848 | -59.1843 | -59.23 | -0.041198 | -0.10071 | 0.050354 | 122.8775 | -0.19226 | -0.091552 | -0.13275 | -0.13275 | -0.17853 | 0.045776 | 0.027466 | -0.25177 | -0.073242 | -0.036621 | 122.9233 | 122.7402 | 58.9096 | -122.9736 | 122.9187 | 122.8363 | 58.9737 | -123.0515
804.0156 | 122.9691 | -59.0012 | 63.8672 | -0.25955 | 0.0072355 | 0.068037 | 0.067954 | 0.12907 | -0.0047767 | -0.0030185 | -0.0077819 | -0.003999 | 0.061701 | 0.06103 | 0.002713 | -0.0047104 | 63.7253 | 63.8763 | -0.018311 | -59.1888 | 63.9084 | -59.0881 | -59.1385 | -59.024 | 0.07782 | -59.2667 | 63.8947 | 63.8535 | -59.1385 | -59.2438 | -0.086975 | -0.13733 | 0.041199 | 122.8775 | -0.18768 | -0.050354 | -0.14191 | -0.13733 | -0.24261 | 0.027466 | -0.022888 | -0.2655 | -0.022889 | -0.013732 | 122.9095 | 122.7264 | 58.9828 | -123.0057 | 122.8958 | 122.8546 | 59.079 | -123.111
805.0156 | 123.0057 | -59.0195 | 63.8718 | -0.24429 | 0.0093717 | 0.06825 | 0.069022 | 0.13206 | -0.0026405 | -0.0034457 | 0.23636 | -0.0037854 | 0.062342 | 0.059107 | 0.0018584 | -0.0062058 | 63.7115 | 63.8489 | 0.10986 | -59.111 | 63.945 | -59.024 | -59.1019 | -59.0378 | 0.064087 | -59.2712 | 63.9313 | 63.8306 | -59.166 | -59.2209 | -0.004578 | -0.082398 | 0.073242 | 122.8683 | -0.091553 | -0.009155 | -0.16022 | -0.14648 | -0.20142 | 0.059509 | -0.018311 | -0.25177 | -0.050354 | -0.041199 | 122.9645 | 122.731 | 59.1293 | -122.9736 | 122.9507 | 122.85 | 59.0836 | -123.0927
806.0156 | 123.0194 | -59.0424 | 63.8809 | -0.23666 | 0.0091581 | 0.068037 | 0.070944 | 0.1327 | -0.0039221 | -0.0068637 | -0.12985 | -0.0072034 | 0.062982 | 0.063166 | 0.0018584 | -0.005565 | 63.7482 | 63.9221 | 0.036621 | -59.1843 | 63.8901 | -59.0652 | -59.1064 | -59.0103 | 0.091553 | -59.2758 | 63.8763 | 63.8123 | -59.1431 | -59.2209 | -0.022889 | -0.064087 | 0.009156 | 122.9645 | -0.14191 | -0.07782 | -0.13275 | -0.10071 | -0.17853 | -0.004577 | 0.032043 | -0.23346 | -0.054932 | -0.068664 | 122.9324 | 122.7905 | 59.079 | -122.9874 | 122.9187 | 122.8546 | 59.1339 | -123.1018
807.0156 | 123.0652 | -59.0195 | 63.8397 | -0.22141 | 0.012362 | 0.067182 | 0.070731 | 0.13035 | 0.0022729 | -0.0045139 | -0.14511 | -0.0048536 | 0.062555 | 0.05868 | 0.0037812 | -0.0081284 | 63.7344 | 63.8809 | -0.036621 | -59.1843 | 63.9267 | -59.0515 | -59.1202 | -58.9874 | 0.068665 | -59.2712 | 63.8901 | 63.8397 | -59.1568 | -59.2346 | -0.032044 | -0.10071 | 0.086975 | 122.9004 | -0.1648 | -0.064087 | -0.10529 | -0.13733 | -0.21515 | 0.050354 | 0.032043 | -0.25177 | -0.036621 | 0 | 122.9462 | 122.7539 | 58.9828 | -122.9599 | 122.9095 | 122.8592 | 59.0881 | -123.0743
808.0156 | 122.9691 | -59.0607 | 63.8351 | 0.015106 | 0.013431 | 0.067823 | 0.070731 | 0.13163 | 0.0018457 | -0.0010959 | 0.068512 | -0.0059216 | 0.065119 | 0.062525 | 0.0035674 | -0.0053512 | 63.707 | 63.8168 | -0.09613 | -59.23 | 63.8901 | -59.079 | -59.166 | -59.0698 | -0.050354 | -59.3582 | 63.858 | 63.7894 | -59.1705 | -59.2667 | -0.01831 | -0.10529 | 0.054932 | 122.8775 | -0.16937 | -0.064087 | -0.12817 | -0.10986 | -0.20599 | 0.022888 | -0.009155 | -0.29755 | -0.091552 | -0.045776 | 122.9507 | 122.7676 | 58.9645 | -123.0011 | 122.9187 | 122.85 | 59.0103 | -123.1018
809.0156 | 122.9782 | -59.0103 | 63.8855 | -0.22903 | 0.0078763 | 0.070173 | 0.071799 | 0.12843 | -0.00093145 | -0.0055821 | -0.168 | -0.00464 | 0.063196 | 0.060816 | 0.0037812 | -0.0062058 | 63.7756 | 63.7985 | -0.07782 | -59.23 | 63.9084 | -59.079 | -59.1568 | -59.0286 | 0.054932 | -59.285 | 63.9038 | 63.8443 | -59.1385 | -59.2072 | -0.068664 | -0.14648 | 0.022888 | 122.8088 | -0.21973 | -0.073243 | -0.10986 | -0.12817 | -0.19684 | 0.018311 | -0.01831 | -0.27466 | -0.07782 | -0.041199 | 122.9187 | 122.7859 | 58.9325 | -123.0423 | 122.9141 | 122.8546 | 59.0652 | -123.0927
810.0156 | 123.0469 | -59.0286 | 63.8718 | -0.19852 | 0.0091581 | 0.067396 | 0.071158 | 0.12993 | -0.00071785 | -0.0019505 | -0.11459 | -0.0052808 | 0.064478 | 0.060176 | 0.0020722 | -0.0062058 | 63.7115 | 63.8535 | -0.036621 | -59.2117 | 63.8947 | -59.0332 | -59.111 | -59.0057 | 0.054932 | -59.2575 | 63.8992 | 63.8489 | -59.1614 | -59.2484 | -0.004578 | -0.082398 | 0.022888 | 122.8821 | -0.18311 | -0.10071 | -0.16022 | -0.13275 | -0.21973 | 0.027466 | 0.022888 | -0.22888 | -0.009155 | -0.022888 | 122.9233 | 122.7402 | 58.992 | -122.9828 | 122.9279 | 122.8775 | 59.0836 | -123.1201
811.0312 | 123.0972 | -58.9737 | 63.8351 | -0.168 | 0.0023221 | 0.067182 | 0.067099 | 0.13078 | -0.0066993 | -0.0032321 | -3.2808 | -0.0027174 | 0.064051 | 0.059748 | 0.0012176 | -0.0040696 | 63.7985 | 64.0137 | 0.054932 | -59.1476 | 63.8626 | -59.0424 | -59.0881 | -58.873 | 0.013733 | -59.166 | 63.8168 | 63.7619 | -59.1293 | -59.2117 | -0.068664 | -0.11444 | 0.027466 | 122.9874 | -0.17395 | -0.059509 | -0.036621 | -0.15564 | -0.23804 | -0.018311 | 0.10071 | -0.19226 | 0.045776 | -0.073242 | 122.8363 | 122.7722 | 59.0286 | -122.9233 | 122.7905 | 122.7356 | 58.9874 | -123.0469
812.0156 | 123.1064 | -58.9737 | 63.8397 | -2.9756 | -0.0010959 | 0.068678 | 0.066885 | 0.1295 | -0.0043495 | -0.0034457 | -0.00015237 | -0.0078442 | 0.063623 | 0.058039 | 0.0020722 | -0.005565 | 63.6841 | 63.9908 | 0.091553 | -59.1614 | 63.8809 | -59.0378 | -59.1248 | -58.9462 | 0.16479 | -59.1797 | 63.858 | 63.7848 | -59.1293 | -59.2117 | -0.064087 | -0.15106 | 0.041198 | 122.9645 | -0.18768 | -0.036621 | -0.15564 | -0.15564 | -0.23804 | 0.01831 | 0.027466 | -0.20599 | 0.032044 | -0.054932 | 122.8546 | 122.6578 | 59.0652 | -122.9645 | 122.8317 | 122.7585 | 59.1385 | -123.0515
813.0156 | 123.0011 | -59.0515 | 63.8397 | -0.00015269 | 0.01279 | 0.066328 | 0.072653 | 0.1295 | 0.0024865 | -0.0021641 | 0.045624 | -0.0052808 | 0.068537 | 0.05868 | 0.0020722 | -0.006633 | 63.7299 | 63.8351 | -0.091553 | -59.2346 | 63.8855 | -59.0927 | -59.1705 | -59.0332 | -0.041199 | -59.3353 | 63.8626 | 63.7939 | -59.1614 | -59.2667 | -0.041198 | -0.11902 | 0.045776 | 122.8867 | -0.18311 | -0.064087 | -0.10986 | -0.10986 | -0.21515 | 0.022888 | 0.018311 | -0.28381 | -0.068664 | -0.045777 | 122.937 | 122.7814 | 58.96 | -123.0103 | 122.9141 | 122.8455 | 59.0103 | -123.1064
814.0156 | 123.0835 | -59.0012 | 63.8306 | -0.22141 | 0.0061673 | 0.069319 | 0.069449 | 0.13035 | -0.0049903 | -0.0040867 | -0.061188 | -0.0076306 | 0.061914 | 0.06103 | -6.4178e-05 | -0.005565 | 63.7848 | 63.9771 | 0.068665 | -59.1431 | 63.8718 | -59.0332 | -59.1019 | -58.9417 | 0.17395 | -59.198 | 63.8718 | 63.8031 | -59.1431 | -59.1934 | -0.032043 | -0.10071 | 0.041199 | 122.9782 | -0.14191 | -0.041198 | -0.045776 | -0.14191 | -0.19226 | 0.041199 | 0.05951 | -0.19684 | -0.004578 | -0.027465 | 122.8729 | 122.7859 | 59.0698 | -122.9324 | 122.8729 | 122.8043 | 59.1751 | -123.024
815.0156 | 123.0011 | -59.0332 | 63.8626 | -0.15274 | 0.0093717 | 0.068464 | 0.072653 | 0.13142 | 0.00099115 | -0.0040867 | -0.17563 | -0.0044264 | 0.064264 | 0.059962 | 0.0018584 | -0.0077012 | 63.7253 | 63.858 | -0.059509 | -59.2026 | 63.9404 | -59.0744 | -59.1614 | -59.0195 | 0.045776 | -59.2941 | 63.913 | 63.8443 | -59.1431 | -59.2163 | -0.041199 | -0.12817 | 0.07782 | 122.8912 | -0.16937 | -0.041199 | -0.13733 | -0.10986 | -0.18311 | 0.050354 | 0.013733 | -0.26093 | -0.077819 | -0.018311 | 122.9736 | 122.7585 | 58.9737 | -123.024 | 122.9462 | 122.8775 | 59.079 | -123.0789
816.0156 | 122.9965 | -59.0286 | 63.8672 | 1.3731 | 0.01044 | 0.068891 | 0.070303 | 0.1295 | -0.00071785 | -0.0043003 | -0.15274 | -0.0048536 | 0.064478 | 0.060176 | 0.0048492 | -0.0051376 | 63.7436 | 63.8077 | -0.064087 | -59.2163 | 63.8901 | -59.079 | -59.1339 | -59.0149 | 0.050354 | -59.285 | 63.9175 | 63.8168 | -59.166 | -59.2209 | -0.050354 | -0.10529 | 0.022889 | 122.8363 | -0.18768 | -0.082398 | -0.1236 | -0.13733 | -0.19226 | 0.050355 | 0.013732 | -0.25635 | -0.064087 | -0.050354 | 122.9187 | 122.7722 | 58.9645 | -123.0011 | 122.9462 | 122.8455 | 59.079 | -123.0881
817.0156 | 123.0057 | -59.0332 | 63.8718 | -0.27481 | 0.0050991 | 0.066328 | 0.070303 | 0.13078 | -0.0043495 | -0.0060093 | -0.13748 | -0.0061352 | 0.060419 | 0.06103 | 0.0016448 | -0.0064194 | 63.7482 | 63.9404 | 0.009155 | -59.1751 | 63.913 | -59.0332 | -59.1019 | -58.9966 | 0.068665 | -59.2621 | 63.8947 | 63.8306 | -59.1431 | -59.23 | 0 | -0.068665 | 0.041199 | 122.9736 | -0.14191 | -0.073242 | -0.1236 | -0.10986 | -0.19684 | 0.022888 | 0.036621 | -0.22888 | -0.032043 | -0.041199 | 122.9462 | 122.7814 | 59.0424 | -122.9736 | 122.9279 | 122.8638 | 59.1019 | -123.1018
818.0156 | 122.9828 | -58.9874 | 63.8489 | -0.21378 | 0.0074491 | 0.070173 | 0.067526 | 0.13228 | -0.0019995 | -0.0047275 | -0.13748 | -0.003999 | 0.061701 | 0.059321 | 0.0024994 | -0.0042832 | 63.7665 | 63.9359 | 0.045776 | -59.166 | 63.8809 | -59.024 | -59.1293 | -58.9691 | 0.11444 | -59.2209 | 63.8855 | 63.8123 | -59.1293 | -59.2255 | -0.036621 | -0.14191 | 0.032043 | 122.9233 | -0.17853 | -0.036622 | -0.082398 | -0.14191 | -0.23804 | 0.036621 | 0.018311 | -0.23346 | 0.004578 | -0.036621 | 122.8683 | 122.7539 | 59.0332 | -122.9782 | 122.8729 | 122.7997 | 59.1019 | -123.0743
819.0156 | 123.0286 | -58.9966 | 63.8672 | -0.25955 | 0.0074491 | 0.06761 | 0.069235 | 0.12886 | 0.00099115 | -0.0034457 | -0.14511 | -0.0048536 | 0.060846 | 0.060816 | 0.0020722 | -0.0064194 | 63.739 | 63.9267 | -0.004578 | -59.2346 | 63.9084 | -59.0698 | -59.111 | -59.0012 | 0.064087 | -59.2712 | 63.9175 | 63.8123 | -59.1614 | -59.2438 | -0.073242 | -0.11444 | 0.041199 | 122.9233 | -0.23804 | -0.1236 | -0.12817 | -0.1648 | -0.24719 | 0.050355 | -0.004578 | -0.27466 | -0.027466 | -0.054931 | 122.905 | 122.7356 | 58.992 | -122.9782 | 122.9141 | 122.8088 | 59.0607 | -123.111
820.0156 | 122.9782 | -59.0103 | 63.858 | -0.24429 | 0.0070217 | 0.066969 | 0.070303 | 0.13057 | -0.00050425 | -0.0045139 | -0.12222 | -0.0069898 | 0.061487 | 0.06103 | -0.00027778 | -0.005565 | 63.7619 | 63.945 | 0.032043 | -59.1888 | 63.9038 | -59.0652 | -59.1202 | -58.9874 | 0.059509 | -59.2667 | 63.9084 | 63.7894 | -59.1293 | -59.2163 | -0.054932 | -0.10986 | 0.045777 | 122.9553 | -0.17853 | -0.068665 | -0.09613 | -0.11902 | -0.20599 | 0.050354 | 0.022888 | -0.25635 | -0.050354 | -0.068664 | 122.9141 | 122.7722 | 59.0424 | -122.9782 | 122.9187 | 122.7997 | 59.0698 | -123.0743
821.0156 | 123.0194 | -58.9783 | 63.8718 | -0.22141 | 0.0059537 | 0.06825 | 0.067526 | 0.13121 | -0.0011451 | -0.0045139 | -0.16037 | -0.0050672 | 0.064051 | 0.059962 | 0.0039948 | -0.0057786 | 63.7665 | 63.9725 | 0.059509 | -59.1614 | 63.8809 | -59.0424 | -59.111 | -58.9783 | 0.11902 | -59.23 | 63.8992 | 63.8031 | -59.1293 | -59.2117 | -0.064087 | -0.13275 | 0.009155 | 122.9507 | -0.18311 | -0.050354 | -0.10529 | -0.15106 | -0.23346 | 0.027466 | 0 | -0.25177 | -0.018311 | -0.068664 | 122.8592 | 122.7447 | 59.0378 | -122.9828 | 122.8775 | 122.7814 | 59.0973 | -123.0835
822.0156 | 123.1522 | -58.9783 | 63.8214 | -0.18326 | 0.0036039 | 0.070387 | 0.069663 | 0.13356 | -0.0037085 | -0.0057957 | -0.068817 | -0.0089124 | 0.062128 | 0.061885 | 0.0018584 | -0.0047104 | 63.739 | 64.3066 | 0.25177 | -59.3491 | 63.9084 | -59.0378 | -59.1248 | -58.8959 | 0.1831 | -59.1431 | 63.8489 | 63.7711 | -59.1019 | -59.1888 | -0.05951 | -0.14648 | 0.086975 | 123.2849 | -0.37079 | -0.2243 | -0.082397 | -0.1236 | -0.21057 | 0.027466 | 0.082397 | -0.16479 | 0.045777 | -0.050354 | 122.8867 | 122.7173 | 59.23 | -122.9462 | 122.8271 | 122.7493 | 59.1614 | -123.0103
823.0312 | 122.9965 | -59.0515 | 63.8306 | -0.16037 | 0.011722 | 0.065046 | 0.075644 | 0.12907 | 0.0022729 | -0.0010959 | 0.0914 | -0.0042126 | 0.064478 | 0.063807 | 0.00549 | -0.0072738 | 63.6887 | 63.8306 | -0.11902 | -59.2667 | 63.9175 | -59.1156 | -59.1705 | -59.0378 | -0.086975 | -59.3399 | 63.8535 | 63.7665 | -59.1797 | -59.2712 | -0.064087 | -0.11902 | 0.086976 | 122.8821 | -0.21515 | -0.096131 | -0.14191 | -0.12817 | -0.21973 | 0.022889 | 0.013733 | -0.28839 | -0.068665 | -0.064087 | 122.9691 | 122.7402 | 58.9325 | -123.0011 | 122.905 | 122.818 | 58.9645 | -123.1018
824.0156 | 123.0515 | -58.992 | 63.858 | -0.22903 | 0.0046719 | 0.069105 | 0.069449 | 0.13163 | -0.0041357 | -0.0023777 | -0.12222 | -0.0067762 | 0.061701 | 0.062098 | 0.0020722 | -0.0064194 | 63.7711 | 63.9679 | 0.036621 | -59.1614 | 63.8947 | -59.0561 | -59.1385 | -58.9691 | 0.12817 | -59.2117 | 63.8992 | 63.7848 | -59.1431 | -59.2209 | -0.064087 | -0.14648 | 0.036621 | 122.9599 | -0.16937 | -0.022888 | -0.086975 | -0.15106 | -0.22888 | 0.041199 | 0.022888 | -0.21973 | 0.009155 | -0.073242 | 122.8867 | 122.7631 | 59.0286 | -122.9965 | 122.8912 | 122.7768 | 59.1202 | -123.0789
825.0156 | 123.0972 | -58.9783 | 63.8123 | -0.19852 | 0.0040311 | 0.066755 | 0.067954 | 0.13035 | -0.0043495 | -0.0057957 | -0.80887 | -0.00464 | 0.063623 | 0.05868 | 0.001004 | -0.0077012 | 63.8031 | 63.9954 | 0.068665 | -59.1202 | 63.9038 | -59.0286 | -59.079 | -58.8959 | 0.10529 | -59.1705 | 63.8489 | 63.7848 | -59.1248 | -59.198 | -0.050354 | -0.10071 | 0.091553 | 122.9736 | -0.14191 | -0.041199 | -0.009155 | -0.14648 | -0.21973 | 0.036621 | 0.082397 | -0.19226 | 0.027466 | -0.027466 | 122.8821 | 122.7814 | 59.0469 | -122.8912 | 122.8271 | 122.7631 | 59.0836 | -123.0103
826.0156 | 123.1247 | -58.9828 | 63.7894 | -0.18326 | 0.0038175 | 0.068464 | 0.070517 | 0.12822 | -0.0039221 | -0.0045139 | -0.084076 | -0.0048536 | 0.061914 | 0.061244 | 0.001004 | -0.0062058 | 63.8351 | 64.0228 | 0.073242 | -59.1293 | 63.8855 | -59.0469 | -59.0973 | -58.9005 | 0.24719 | -58.9233 | 63.9267 | 63.8123 | -59.0836 | -59.2209 | -0.064087 | -0.11444 | 0.09613 | 123.0057 | -0.14648 | -0.032043 | 0.045776 | -0.10071 | -0.23804 | 0.13733 | 0.082397 | 0.059509 | 0.29755 | 0.022888 | 122.8683 | 122.818 | 59.0561 | -122.8867 | 122.9095 | 122.7951 | 59.23 | -123.0103
827.0156 | 123.1476 | -58.992 | 63.8168 | -0.15274 | 0.0021085 | 0.068464 | 0.070731 | 0.13057 | -0.0037085 | -0.0055821 | -0.038299 | -0.0069898 | 0.061701 | 0.058467 | 0.0020722 | -0.0036424 | 63.8123 | 63.9954 | 0.050354 | -59.1476 | 63.8718 | -59.0378 | -59.0927 | -58.873 | 0.1831 | -59.1385 | 63.8397 | 63.7665 | -59.111 | -59.2117 | -0.045777 | -0.10071 | 0.054932 | 122.9874 | -0.15564 | -0.054932 | -0.004577 | -0.11902 | -0.21973 | 0.022889 | 0.11902 | -0.14648 | 0.073242 | -0.050354 | 122.8638 | 122.8043 | 59.0424 | -122.9095 | 122.8317 | 122.7585 | 59.1751 | -123.0286
828.0156 | 123.024 | -59.0057 | 63.8947 | -0.21378 | 0.012576 | 0.068891 | 0.069663 | 0.13292 | -7.6852e-05 | -0.0051547 | -0.00015237 | -0.0052808 | 0.064051 | 0.061244 | 0.004422 | -0.0072738 | 63.652 | 63.8123 | -0.041199 | -59.2346 | 63.9175 | -59.0698 | -59.1385 | -59.024 | 0.041199 | -59.2896 | 63.913 | 63.8123 | -59.1568 | -59.2346 | -0.064087 | -0.13275 | 0.022889 | 122.818 | -0.22888 | -0.09613 | -0.24261 | -0.15106 | -0.22888 | 0.018311 | -0.018311 | -0.28381 | -0.054932 | -0.082397 | 122.9233 | 122.6578 | 58.9645 | -123.0331 | 122.9187 | 122.818 | 59.0469 | -123.1293
829.0156 | 122.9919 | -59.0057 | 63.8626 | -0.22903 | 0.0055265 | 0.069319 | 0.068594 | 0.13099 | -0.0015723 | -0.0053683 | -0.17563 | -0.0061352 | 0.062128 | 0.061457 | 0.0024994 | -0.0053512 | 63.7756 | 63.9633 | 0.032043 | -59.1568 | 63.8992 | -59.0195 | -59.1156 | -58.9737 | 0.07782 | -59.2575 | 63.9038 | 63.8214 | -59.1293 | -59.2255 | -0.013733 | -0.10986 | 0.036621 | 122.9691 | -0.15106 | -0.041198 | -0.086975 | -0.1236 | -0.21973 | 0.041199 | 0.032043 | -0.25177 | -0.032043 | -0.041199 | 122.905 | 122.7814 | 59.0378 | -122.9782 | 122.9095 | 122.8271 | 59.0836 | -123.0881
830.0156 | 123.0835 | -58.9783 | 63.8168 | -0.03067 | 0.0057401 | 0.068464 | 0.066458 | 0.12907 | -0.0034949 | -0.0030185 | 0.030365 | -0.0082716 | 0.062342 | 0.060816 | 0.0031402 | -0.0051376 | 63.7527 | 63.9633 | -0.004578 | -59.166 | 63.8718 | -59.0561 | -59.1202 | -58.9279 | 0.091553 | -59.1888 | 63.8718 | 63.7711 | -59.1385 | -59.2255 | -0.07782 | -0.14191 | 0.054932 | 122.9416 | -0.18768 | -0.045777 | -0.064086 | -0.16022 | -0.24719 | 0.054932 | 0.050354 | -0.21057 | 0.036621 | -0.045776 | 122.85 | 122.731 | 58.9737 | -122.937 | 122.85 | 122.7493 | 59.0698 | -123.0423
831.0156 | 123.111 | -58.992 | 63.8077 | -0.23666 | 0.0057401 | 0.068678 | 0.069235 | 0.13014 | -0.00093145 | -0.0055821 | 0.39658 | -0.006349 | 0.061487 | 0.059321 | 0.0024994 | -0.0072738 | 63.6612 | 64.3524 | 0.30212 | -59.3262 | 63.8947 | -59.024 | -59.1339 | -58.9005 | 0.17395 | -59.1705 | 63.858 | 63.7527 | -59.1293 | -59.2026 | -0.032044 | -0.14191 | 0.086975 | 123.3444 | -0.33417 | -0.19226 | -0.14648 | -0.13733 | -0.21057 | 0.050354 | 0.091552 | -0.17853 | 0.032044 | -0.054931 | 122.8867 | 122.6532 | 59.2941 | -122.9416 | 122.85 | 122.7448 | 59.166 | -123.0103
832.0156 | 123.0698 | -58.9645 | 63.8351 | -0.16037 | 0.0055265 | 0.069319 | 0.070303 | 0.12864 | -0.00071785 | -0.0045139 | -0.15274 | -0.0095532 | 0.064051 | 0.059962 | 0.0022858 | -0.006633 | 63.8077 | 63.9999 | 0.059509 | -59.1431 | 63.8763 | -59.0332 | -59.1019 | -58.9279 | 0.17395 | -59.2026 | 63.8901 | 63.7848 | -59.1293 | -59.2072 | -0.068664 | -0.13733 | 0.041199 | 122.9645 | -0.17853 | -0.041198 | -0.027466 | -0.16479 | -0.24261 | 0.054932 | 0.036622 | -0.23804 | 0.004577 | -0.050354 | 122.8409 | 122.7722 | 59.024 | -122.937 | 122.8546 | 122.7493 | 59.1385 | -123.0423
833.0156 | 122.9782 | -59.0424 | 63.8489 | -0.22903 | 0.0083035 | 0.070173 | 0.068167 | 0.12907 | 0.00056395 | -0.0053683 | -0.17563 | -0.0067762 | 0.061914 | 0.061671 | 0.0067718 | -0.0051376 | 63.7253 | 63.8901 | -0.036621 | -59.2117 | 63.9084 | -59.0652 | -59.1293 | -59.1202 | 0.14191 | -59.3353 | 63.9175 | 63.7848 | -59.1888 | -59.2392 | -0.022889 | -0.086975 | 0.059509 | 122.9324 | -0.16937 | -0.082398 | -0.1236 | -0.14648 | -0.19684 | 0.068665 | -0.07782 | -0.29297 | -0.09613 | -0.064087 | 122.9507 | 122.7676 | 59.0057 | -122.9782 | 122.9599 | 122.8271 | 59.1843 | -123.0881
834.0156 | 123.0057 | -59.0424 | 63.8214 | 0.068512 | 0.011081 | 0.066541 | 0.07009 | 0.13035 | 0.0022729 | -0.0023777 | 0.10666 | -0.0044264 | 0.063623 | 0.062739 | 0.00549 | -0.0027878 | 63.6795 | 63.7894 | -0.16022 | -59.285 | 63.9038 | -59.079 | -59.1797 | -59.1797 | -0.24261 | -59.1019 | 63.8626 | 63.7802 | -59.1751 | -59.2438 | -0.036621 | -0.13733 | 0.082398 | 122.8317 | -0.24262 | -0.10529 | -0.14191 | -0.13275 | -0.20142 | 0.041199 | -0.13733 | -0.05951 | 0.14191 | -0.041199 | 122.9462 | 122.7219 | 58.8821 | -123.0011 | 122.905 | 122.8226 | 58.7997 | -123.0652
835.0156 | 123.1201 | -58.9645 | 63.8031 | -0.045929 | 0.0027493 | 0.067823 | 0.068594 | 0.12886 | -0.0054175 | -0.0015231 | 0.030365 | -0.0061352 | 0.06341 | 0.06103 | 0.002713 | -0.0047104 | 63.7939 | 63.9862 | 0.032043 | -59.1568 | 63.8763 | -59.0332 | -59.1019 | -58.8776 | 0.18768 | -59.1476 | 63.8535 | 63.7756 | -59.1019 | -59.1934 | -0.068664 | -0.13733 | 0.073242 | 122.9507 | -0.19226 | -0.054931 | -0.009156 | -0.13733 | -0.22888 | 0.050354 | 0.086976 | -0.1831 | 0.045776 | -0.027466 | 122.8409 | 122.7585 | 58.9966 | -122.905 | 122.818 | 122.7402 | 59.1522 | -122.9965
836.0156 | 123.1155 | -58.9691 | 63.8168 | -0.17563 | 0.0061673 | 0.069105 | 0.068594 | 0.13014 | -0.0034949 | -0.0034457 | 0.84671 | -0.0076306 | 0.058924 | 0.059321 | 0.0033538 | -0.0057786 | 63.6292 | 64.4577 | 0.3067 | -59.2072 | 63.9038 | -59.0195 | -59.1064 | -58.8913 | 0.19684 | -59.1705 | 63.8535 | 63.7482 | -59.0973 | -59.2026 | -0.050354 | -0.13733 | 0.086976 | 123.4268 | -0.23804 | -0.10071 | -0.18768 | -0.12817 | -0.23346 | 0.036622 | 0.07782 | -0.20142 | 0.032044 | -0.068664 | 122.8729 | 122.5983 | 59.2758 | -122.9233 | 122.8226 | 122.7173 | 59.166 | -123.0194
837.0156 | 123.0972 | -58.9783 | 63.8077 | -0.11459 | 0.0036039 | 0.068464 | 0.068594 | 0.12928 | -0.0030677 | -0.0053683 | 0.045624 | -0.0061352 | 0.061487 | 0.06103 | 0.0037812 | -0.0077012 | 63.7894 | 63.9862 | 0.027466 | -59.1522 | 63.8855 | -59.0561 | -59.0836 | -58.8776 | 0.15564 | -59.1522 | 63.8535 | 63.7527 | -59.1293 | -59.2117 | -0.07782 | -0.10529 | 0.07782 | 122.9645 | -0.17395 | -0.068665 | -0.01831 | -0.15106 | -0.23346 | 0.045777 | 0.10071 | -0.17395 | 0.059509 | -0.054931 | 122.8638 | 122.7676 | 59.0057 | -122.8912 | 122.8317 | 122.731 | 59.1339 | -123.0194
838.0156 | 123.1659 | -58.9828 | 63.8031 | -0.19852 | 0.0042447 | 0.068678 | 0.068594 | 0.128 | -0.0015723 | -0.0023777 | -0.10696 | -0.0061352 | 0.06106 | 0.059321 | -0.0022004 | -0.0051376 | 63.858 | 64.0274 | 0.068665 | -59.1385 | 63.8672 | -59.024 | -59.0927 | -58.7494 | -0.30212 | -59.198 | 63.8535 | 63.7711 | -59.111 | -59.2117 | -0.041199 | -0.10986 | 0.064086 | 123.0103 | -0.15564 | -0.045777 | 0.054931 | -0.12817 | -0.22888 | 0.050354 | 0.23346 | -0.21515 | 0.013733 | -0.032044 | 122.85 | 122.8409 | 59.0515 | -122.8958 | 122.8363 | 122.7539 | 58.6807 | -123.0148
839.0156 | 122.9507 | -59.024 | 63.8718 | -0.22141 | 0.0083035 | 0.067182 | 0.072226 | 0.13142 | 0.00077755 | -0.0021641 | -1.938 | -0.006349 | 0.064478 | 0.059962 | 0.0012176 | -0.006633 | 63.739 | 63.858 | -0.036621 | -59.2209 | 63.9267 | -59.0561 | -59.1293 | -59.0057 | -0.032043 | -59.2896 | 63.9175 | 63.7848 | -59.1843 | -59.2438 | -0.032043 | -0.10529 | 0.054932 | 122.8821 | -0.19684 | -0.091553 | -0.13275 | -0.16022 | -0.21973 | 0.045777 | 0.018311 | -0.2655 | -0.045777 | -0.086975 | 122.9507 | 122.7631 | 58.9874 | -123.0011 | 122.9416 | 122.8088 | 58.992 | -123.1155
840.0156 | 123.175 | -58.9508 | 63.8397 | -0.15274 | 0.0038175 | 0.069319 | 0.067313 | 0.13057 | -0.0041357 | -0.0043003 | -0.045929 | -0.0093396 | 0.064051 | 0.060389 | 0.0014312 | -0.003215 | 63.8306 | 64.0411 | 0.068665 | -59.1156 | 63.8672 | -59.0424 | -59.1064 | -58.8867 | 0.1831 | -59.1568 | 63.8443 | 63.7527 | -59.1248 | -59.1843 | -0.091552 | -0.15564 | 0.027465 | 122.9919 | -0.16479 | -0.009156 | -0.009156 | -0.17395 | -0.23346 | 0.004577 | 0.064087 | -0.20599 | 0.027466 | -0.086975 | 122.818 | 122.7814 | 59.0195 | -122.9462 | 122.7951 | 122.7036 | 59.1339 | -123.024
841.0156 | 123.1018 | -58.9828 | 63.8489 | -1.3887 | 0.0063809 | 0.066541 | 0.070517 | 0.12971 | -0.00050425 | -0.0013095 | -0.099335 | -0.0054944 | 0.061914 | 0.06103 | 0.0035674 | -0.0074876 | 63.7756 | 64.0274 | 0.086975 | -59.1431 | 63.858 | -59.0424 | -59.1019 | -58.905 | 0.17395 | -59.166 | 63.8626 | 63.7436 | -59.1202 | -59.2163 | -0.059509 | -0.11902 | 0.009155 | 123.0103 | -0.16022 | -0.041198 | -0.073242 | -0.13733 | -0.23346 | 0.013733 | 0.07782 | -0.18311 | 0.050354 | -0.10529 | 122.8409 | 122.7585 | 59.0698 | -122.9507 | 122.8455 | 122.7264 | 59.1568 | -123.0652
842.0156 | 123.111 | -58.992 | 63.8306 | -0.068817 | 0.0044583 | 0.06825 | 0.067954 | 0.12864 | -0.0041357 | -0.0053683 | -0.11459 | -0.0076306 | 0.062982 | 0.059748 | 0.0020722 | -0.0068466 | 63.8397 | 64.0091 | 0.054932 | -59.1614 | 63.8947 | -59.024 | -59.0973 | -58.8638 | 0.20142 | -59.1339 | 63.8351 | 63.7619 | -59.1202 | -59.2072 | -0.032044 | -0.10529 | 0.064087 | 123.0011 | -0.16937 | -0.064087 | 0.009156 | -0.12817 | -0.21515 | 0.004578 | 0.12817 | -0.14191 | 0.073242 | -0.068664 | 122.8867 | 122.8317 | 59.0469 | -122.9279 | 122.8271 | 122.7539 | 59.1934 | -123.0377
843.0156 | 123.0057 | -59.0286 | 63.8718 | 0.12955 | 0.0093717 | 0.065901 | 0.072226 | 0.13099 | 0.0041955 | -0.0017369 | -0.22903 | -0.0052808 | 0.064691 | 0.06103 | 0.0037812 | -0.0079148 | 63.7619 | 63.8855 | -0.041199 | -59.2117 | 63.9175 | -59.0607 | -59.1339 | -59.0012 | 0.045776 | -59.2804 | 63.9038 | 63.7894 | -59.1705 | -59.2392 | -0.032044 | -0.10529 | 0.045777 | 122.9141 | -0.18311 | -0.07782 | -0.10986 | -0.14191 | -0.21057 | 0.032044 | 0.027465 | -0.25177 | -0.041199 | -0.082397 | 122.9462 | 122.7905 | 58.9874 | -123.0057 | 122.9324 | 122.818 | 59.0744 | -123.111
844.0156 | 123.0377 | -59.0286 | 63.8306 | -0.084076 | 0.012362 | 0.065046 | 0.073294 | 0.13377 | 0.0027001 | -0.0040867 | -0.068817 | -0.00464 | 0.064264 | 0.061244 | 0.0046356 | -0.0047104 | 63.7939 | 63.8947 | -0.041199 | -59.2072 | 63.8809 | -59.0698 | -59.1522 | -58.9645 | 0.027466 | -59.2941 | 63.8626 | 63.7665 | -59.1476 | -59.2346 | -0.041199 | -0.1236 | 0.050354 | 122.9233 | -0.17853 | -0.054931 | -0.036621 | -0.11902 | -0.20599 | 0.032044 | 0.064086 | -0.2655 | -0.059509 | -0.064087 | 122.9095 | 122.8226 | 58.9874 | -122.9828 | 122.8912 | 122.7951 | 59.0561 | -123.0652
845.0156 | 123.0835 | -58.96 | 63.8397 | -0.061188 | 0.0040311 | 0.069105 | 0.067099 | 0.13014 | -0.0043495 | -0.0049411 | -0.0077819 | -0.0067762 | 0.057215 | 0.059962 | 0.0012176 | -0.0059922 | 63.7802 | 63.9725 | 0.041199 | -59.1476 | 63.8718 | -59.0378 | -59.1019 | -58.8913 | 0.16479 | -59.1293 | 63.8535 | 63.7711 | -59.111 | -59.2117 | -0.07782 | -0.14191 | 0.032043 | 122.9324 | -0.18768 | -0.045776 | -0.05951 | -0.15106 | -0.25177 | 0.013733 | 0.068665 | -0.16937 | 0.082398 | -0.068665 | 122.8317 | 122.7402 | 59.0012 | -122.9416 | 122.8134 | 122.731 | 59.1248 | -123.0515
846.0156 | 123.143 | -58.9783 | 63.7939 | -0.061188 | 0.0033901 | 0.067182 | 0.068167 | 0.12693 | -0.0034949 | -0.0028049 | -0.023041 | -0.0065626 | 0.061914 | 0.061457 | 0.0016448 | -0.0057786 | 63.7848 | 63.9587 | 0.032043 | -59.166 | 63.8763 | -59.0332 | -59.1064 | -58.8913 | 0.13275 | -59.1339 | 63.8397 | 63.7573 | -59.1156 | -59.1705 | -0.054932 | -0.12817 | 0.082398 | 122.937 | -0.18768 | -0.05951 | -0.009155 | -0.13733 | -0.19226 | 0.045777 | 0.086975 | -0.15564 | 0.036621 | -0.036621 | 122.8546 | 122.7631 | 59.0103 | -122.9004 | 122.818 | 122.7356 | 59.111 | -122.9645
847.0156 | 123.0606 | -58.9554 | 63.8397 | -0.168 | 0.0072355 | 0.068891 | 0.066885 | 0.13078 | -0.0017859 | -0.0028049 | -0.12985 | -0.005708 | 0.059351 | 0.05868 | 0.0020722 | -0.0062058 | 63.8077 | 64.0045 | 0.068665 | -59.1385 | 63.858 | -59.0286 | -59.0973 | -58.9142 | 0.16479 | -59.1797 | 63.8855 | 63.7665 | -59.1156 | -59.2026 | -0.073242 | -0.14191 | 0.01831 | 122.9599 | -0.18311 | -0.041199 | -0.032044 | -0.16022 | -0.24719 | 0.045776 | 0.041198 | -0.2243 | 0.022889 | -0.073243 | 122.8134 | 122.7631 | 59.024 | -122.937 | 122.8409 | 122.7219 | 59.1202 | -123.0423
848.0156 | 123.0652 | -58.9783 | 63.826 | -0.21378 | 0.0038175 | 0.068464 | 0.069235 | 0.13035 | -0.00093145 | -0.0028049 | -0.13748 | -0.0065626 | 0.061273 | 0.059321 | 0.00079042 | -0.0074876 | 63.8077 | 63.9954 | 0.073242 | -59.1431 | 63.8718 | -59.024 | -59.1019 | -58.9371 | 0.1831 | -59.1797 | 63.8672 | 63.7619 | -59.1431 | -59.2117 | -0.045777 | -0.1236 | 0.045776 | 122.9736 | -0.16479 | -0.041198 | -0.018311 | -0.16479 | -0.23346 | 0.041198 | 0.041198 | -0.20142 | 0.032044 | -0.064087 | 122.85 | 122.7859 | 59.0515 | -122.9279 | 122.8455 | 122.7402 | 59.1614 | -123.0377
849.0156 | 123.024 | -59.0195 | 63.8489 | -0.084076 | 0.010226 | 0.067182 | 0.069022 | 0.12907 | 0.0039819 | -0.00024146 | -0.084076 | -0.0054944 | 0.065332 | 0.062739 | 0.0069854 | -0.010265 | 63.8214 | 63.7482 | -0.15564 | -59.1293 | 63.8901 | -59.079 | -59.1431 | -58.9417 | 0.064087 | -59.2575 | 63.8992 | 63.7939 | -59.1568 | -59.2529 | -0.059509 | -0.1236 | 0.041199 | 122.7676 | -0.10986 | 0.013733 | -0.027466 | -0.13733 | -0.23346 | 0.050354 | 0.07782 | -0.23804 | -0.004577 | -0.054932 | 122.9095 | 122.8409 | 58.8638 | -122.9919 | 122.9187 | 122.8134 | 59.0836 | -123.1018
850.0156 | 123.0057 | -58.9645 | 63.8077 | -0.0077822 | 0.0016813 | 0.069959 | 0.067313 | 0.13057 | -0.0056311 | -0.0028049 | -0.053558 | -0.008058 | 0.059992 | 0.060176 | 0.0018584 | -0.0062058 | 63.8443 | 63.9954 | 0.07782 | -59.1293 | 63.8626 | -59.0149 | -59.1064 | -58.8959 | 0.17395 | -59.1476 | 63.8489 | 63.7482 | -59.1156 | -59.1705 | -0.050354 | -0.14191 | 0.054932 | 122.9599 | -0.16479 | -0.022888 | 0.036621 | -0.15106 | -0.20599 | 0.041199 | 0.068665 | -0.1831 | 0.022888 | -0.059509 | 122.8271 | 122.8088 | 59.0424 | -122.9141 | 122.8134 | 122.7127 | 59.1385 | -122.9782
851.0156 | 123.1705 | -58.9508 | 63.8763 | -0.14511 | 0.0048855 | 0.070387 | 0.068381 | 0.12928 | -0.0049903 | -0.0034457 | -0.053558 | -0.0067762 | 0.06106 | 0.06103 | 0.0024994 | -0.0053512 | 63.8077 | 64.0091 | 0.064087 | -59.1339 | 63.8763 | -59.0378 | -59.1019 | -58.8776 | 0.18768 | -59.1476 | 63.8535 | 63.7711 | -59.1202 | -59.2072 | -0.086975 | -0.15106 | 0 | 122.9599 | -0.1831 | -0.032043 | -0.068665 | -0.16937 | -0.25635 | -0.022888 | 0.073243 | -0.19684 | 0.059509 | -0.10529 | 122.8271 | 122.7585 | 59.0149 | -122.9782 | 122.8043 | 122.7219 | 59.1385 | -123.0835
852.0156 | 123.0194 | -58.992 | 63.8397 | -0.22141 | 0.0029629 | 0.069105 | 0.069449 | 0.13014 | 0.0016321 | -0.0038731 | -0.16037 | -0.0061352 | 0.060419 | 0.060603 | 0.0033538 | -0.0077012 | 63.7985 | 63.9725 | 0.045776 | -59.1705 | 63.8672 | -59.0561 | -59.0973 | -58.9554 | 0.1236 | -59.2117 | 63.8855 | 63.7894 | -59.1476 | -59.2209 | -0.064087 | -0.10529 | 0.027465 | 122.9645 | -0.17853 | -0.073242 | -0.041199 | -0.15564 | -0.22888 | 0.045776 | 0.036621 | -0.21973 | 0.009155 | -0.050354 | 122.8592 | 122.7905 | 59.0378 | -122.937 | 122.8775 | 122.7814 | 59.1156 | -123.0606
853.0156 | 123.0011 | -59.0195 | 63.8397 | -0.36636 | 0.0093717 | 0.06825 | 0.069235 | 0.12886 | 0.0020593 | -0.0047275 | -0.21378 | -0.0027174 | 0.064478 | 0.059962 | 0.0048492 | -0.0081284 | 63.7344 | 63.8672 | -0.059509 | -59.2117 | 63.9221 | -59.0744 | -59.1293 | -59.0057 | 0.059509 | -59.2804 | 63.9221 | 63.7939 | -59.1522 | -59.23 | -0.054932 | -0.10986 | 0.082397 | 122.8867 | -0.19226 | -0.082398 | -0.10529 | -0.13275 | -0.21057 | 0.082397 | 0.013733 | -0.26093 | -0.050354 | -0.045777 | 122.9416 | 122.7539 | 58.96 | -122.9691 | 122.9416 | 122.8134 | 59.079 | -123.0698
854.0156 | 123.0972 | -59.0057 | 63.8123 | -0.0077822 | 0.0046719 | 0.069532 | 0.068381 | 0.12886 | -0.0041357 | -0.0030185 | 0.068512 | -0.0086988 | 0.059137 | 0.062312 | 0.0024994 | -0.0051376 | 63.7573 | 63.9404 | -0.018311 | -59.1797 | 63.8763 | -59.0607 | -59.1064 | -58.9325 | 0.11444 | -59.1751 | 63.8306 | 63.7665 | -59.1248 | -59.2117 | -0.054932 | -0.10071 | 0.064087 | 122.9462 | -0.17395 | -0.073242 | -0.054932 | -0.11902 | -0.20599 | 0.01831 | 0.073242 | -0.16937 | 0.036621 | -0.045777 | 122.8821 | 122.7631 | 58.9874 | -122.9187 | 122.8363 | 122.7722 | 59.1202 | -123.024
855.0156 | 123.1018 | -58.9737 | 63.826 | -0.084076 | 0.0046719 | 0.068464 | 0.07009 | 0.13121 | -0.0032813 | -0.0045139 | 0.053253 | -0.0052808 | 0.059778 | 0.059321 | 0.0012176 | -0.006633 | 63.8031 | 63.9908 | 0.032043 | -59.1614 | 63.8809 | -59.0332 | -59.1019 | -58.8867 | 0.15564 | -59.1339 | 63.858 | 63.7482 | -59.1064 | -59.198 | -0.059509 | -0.12817 | 0.054931 | 122.9645 | -0.18768 | -0.059509 | -0.022888 | -0.13275 | -0.2243 | 0.032043 | 0.086975 | -0.16022 | 0.064087 | -0.07782 | 122.8546 | 122.7768 | 59.0057 | -122.9279 | 122.8317 | 122.7219 | 59.1293 | -123.024
856.0156 | 123.0743 | -58.992 | 63.8306 | -0.25955 | 0.0057401 | 0.067823 | 0.069876 | 0.13035 | -0.0013587 | -0.0045139 | -0.13748 | -0.0076306 | 0.060205 | 0.057185 | 0.0020722 | -0.006633 | 63.8031 | 63.9816 | 0.068665 | -59.1522 | 63.8855 | -59.0332 | -59.1156 | -58.9279 | 0.14191 | -59.1843 | 63.8809 | 63.7527 | -59.111 | -59.2209 | -0.041199 | -0.1236 | 0.054932 | 122.9736 | -0.16022 | -0.036621 | -0.027465 | -0.11902 | -0.22888 | 0.050354 | 0.064087 | -0.19226 | 0.036621 | -0.077819 | 122.8775 | 122.7951 | 59.0607 | -122.9462 | 122.8729 | 122.7448 | 59.1339 | -123.0515
857.0156 | 122.9965 | -59.0057 | 63.8947 | -0.22903 | 0.0063809 | 0.067396 | 0.072867 | 0.13228 | 0.00077755 | -0.0038731 | -0.14511 | -0.0061352 | 0.064905 | 0.06103 | 0.0035674 | -0.0064194 | 63.7619 | 63.9542 | 0.009155 | -59.166 | 63.8947 | -59.0332 | -59.111 | -58.992 | 0.07782 | -59.2667 | 63.9267 | 63.7894 | -59.1751 | -59.2209 | -0.027466 | -0.10529 | 0 | 122.9599 | -0.16022 | -0.054932 | -0.13275 | -0.16937 | -0.21515 | 0.032044 | 0.013733 | -0.26093 | -0.045777 | -0.10528 | 122.9004 | 122.7676 | 59.0149 | -123.0057 | 122.9324 | 122.7951 | 59.0836 | -123.1155
858.0156 | 123.024 | -59.0103 | 63.8306 | -0.19852 | 0.012362 | 0.065046 | 0.070731 | 0.12779 | 0.0027001 | -0.0034457 | -0.32059 | -0.00464 | 0.063196 | 0.062312 | 0.00549 | -0.008342 | 63.7939 | 63.9175 | -0.018311 | -59.166 | 63.9267 | -59.0698 | -59.1248 | -58.9462 | 0.068665 | -59.2484 | 63.8809 | 63.7711 | -59.1431 | -59.2255 | -0.059509 | -0.11444 | 0.096131 | 122.9279 | -0.15564 | -0.041199 | -0.036621 | -0.13275 | -0.21515 | 0.050354 | 0.064087 | -0.23804 | -0.022888 | -0.059509 | 122.937 | 122.8043 | 58.992 | -122.9553 | 122.8912 | 122.7814 | 59.079 | -123.056
859.0156 | 123.1247 | -58.9554 | 63.8763 | -0.023041 | 0.0029629 | 0.067182 | 0.070944 | 0.12971 | -0.0054175 | -0.0034457 | -0.015411 | -0.0065626 | 0.061487 | 0.06103 | 0.0024994 | -0.0064194 | 63.8214 | 64.0274 | 0.064087 | -59.1339 | 63.8855 | -59.0424 | -59.079 | -58.8684 | 0.16937 | -59.1431 | 63.858 | 63.7619 | -59.1385 | -59.2072 | -0.086975 | -0.1236 | 0.009155 | 122.9828 | -0.17853 | -0.054932 | -0.054932 | -0.18311 | -0.25177 | -0.018311 | 0.086975 | -0.18768 | 0.064087 | -0.11444 | 122.8409 | 122.7768 | 59.0195 | -122.9553 | 122.8134 | 122.7173 | 59.1248 | -123.0835
860.0156 | 123.0927 | -58.9691 | 63.8168 | 0.015106 | 0.0095853 | 0.067182 | 0.071158 | 0.13163 | 0.00013675 | -0.0025913 | -0.16037 | -0.0050672 | 0.061273 | 0.05868 | 0.0033538 | -0.006633 | 63.7665 | 64.0457 | 0.054932 | -59.1476 | 63.8763 | -59.0424 | -59.1019 | -58.9005 | 0.16479 | -59.1568 | 63.8535 | 63.7527 | -59.111 | -59.1888 | -0.073242 | -0.13275 | 0.05951 | 123.0148 | -0.17853 | -0.045776 | -0.050354 | -0.14191 | -0.21973 | 0.036622 | 0.068664 | -0.18768 | 0.032044 | -0.064086 | 122.8455 | 122.7356 | 59.024 | -122.9187 | 122.8226 | 122.7219 | 59.1339 | -123.0057
861.0156 | 123.1018 | -58.9966 | 63.8214 | -0.023041 | 0.0044583 | 0.068464 | 0.070517 | 0.12993 | -0.0028541 | -0.0060093 | 0.060883 | -0.005708 | 0.061701 | 0.059962 | 0.0029266 | -0.0059922 | 63.7711 | 63.9267 | -0.018311 | -59.1705 | 63.8809 | -59.0469 | -59.1385 | -58.9279 | 0.091553 | -59.1797 | 63.8535 | 63.7436 | -59.1293 | -59.23 | -0.050354 | -0.14191 | 0.059509 | 122.9233 | -0.17395 | -0.032043 | -0.050354 | -0.13275 | -0.23346 | 0.032044 | 0.068665 | -0.18311 | 0.050355 | -0.07782 | 122.8775 | 122.7676 | 58.9783 | -122.9599 | 122.85 | 122.7402 | 59.0881 | -123.0515
862.0156 | 123.1018 | -58.9737 | 63.8077 | 0.0074768 | 0.0048855 | 0.06761 | 0.069449 | 0.12886 | -0.0022131 | -0.0051547 | 0.076141 | -0.0069898 | 0.061487 | 0.058039 | 0.0042084 | -0.0068466 | 63.7527 | 63.9267 | -0.027466 | -59.1843 | 63.8855 | -59.0698 | -59.1248 | -58.9371 | 0.091553 | -59.1843 | 63.8855 | 63.7619 | -59.1339 | -59.2209 | -0.09613 | -0.15106 | 0.07782 | 122.9004 | -0.21057 | -0.059509 | -0.054931 | -0.16022 | -0.24719 | 0.07782 | 0.036621 | -0.21057 | 0.036621 | -0.045776 | 122.8592 | 122.7264 | 58.9462 | -122.9324 | 122.8592 | 122.7356 | 59.0652 | -123.0286
863.0156 | 123.0286 | -59.0012 | 63.8718 | -0.17563 | 0.010226 | 0.066969 | 0.073721 | 0.13185 | 0.0059045 | -0.0030185 | -0.2214 | -0.0050672 | 0.064691 | 0.058467 | 0.0037812 | -0.0091966 | 63.7711 | 63.8763 | -0.032043 | -59.198 | 63.9267 | -59.0744 | -59.1339 | -58.9783 | 0.050354 | -59.2575 | 63.9267 | 63.8077 | -59.1522 | -59.2209 | -0.073242 | -0.13275 | 0.054932 | 122.8775 | -0.19684 | -0.064087 | -0.10071 | -0.15106 | -0.21973 | 0.054932 | 0.022889 | -0.25635 | -0.036621 | -0.064087 | 122.9279 | 122.7722 | 58.9691 | -123.0057 | 122.9279 | 122.8088 | 59.0515 | -123.0927
864.0156 | 123.0835 | -58.9691 | 63.826 | -0.12985 | 0.0055265 | 0.066328 | 0.068381 | 0.13014 | -0.0030677 | -0.0036595 | -0.11459 | -0.0067762 | 0.06106 | 0.060176 | 0.001004 | -0.003856 | 63.8168 | 63.9999 | 0.059509 | -59.1339 | 63.8855 | -59.024 | -59.0973 | -58.9142 | 0.17853 | -59.166 | 63.8763 | 63.7848 | -59.1339 | -59.2026 | -0.054932 | -0.12817 | 0.059509 | 122.9691 | -0.16479 | -0.036621 | -0.009156 | -0.16479 | -0.23346 | 0.050354 | 0.054931 | -0.19684 | 0.036621 | -0.041199 | 122.8546 | 122.7859 | 59.0286 | -122.9233 | 122.8455 | 122.7539 | 59.1476 | -123.0286
865.0156 | 123.0103 | -58.992 | 63.8626 | -0.21378 | 0.0068081 | 0.067823 | 0.070517 | 0.12822 | 0.0016321 | -0.0032321 | -0.18326 | -0.00464 | 0.06106 | 0.061244 | 0.0016448 | -0.0070602 | 63.7802 | 63.9542 | 0.022888 | -59.1614 | 63.9038 | -59.0378 | -59.1202 | -58.9691 | 0.10071 | -59.2392 | 63.9313 | 63.8031 | -59.1431 | -59.2163 | -0.045777 | -0.12817 | 0.041199 | 122.9462 | -0.16937 | -0.041199 | -0.082398 | -0.15106 | -0.22431 | 0.068664 | 0.022888 | -0.24719 | -0.022888 | -0.059509 | 122.8958 | 122.7722 | 59.0149 | -122.9828 | 122.9233 | 122.7951 | 59.0927 | -123.0789
866.0156 | 123.1567 | -58.9691 | 63.8351 | -0.076447 | 0.0044583 | 0.06825 | 0.069876 | 0.13185 | -0.0039221 | -0.0043003 | -0.10696 | -0.0052808 | 0.062555 | 0.060389 | 0.002713 | -0.0077012 | 63.8031 | 64.0228 | 0.082397 | -59.1431 | 63.8626 | -59.0469 | -59.0881 | -58.8547 | 0.1831 | -59.1385 | 63.858 | 63.7619 | -59.1293 | -59.198 | -0.07782 | -0.11902 | 0.027466 | 122.9919 | -0.17395 | -0.054931 | -0.032043 | -0.16022 | -0.22888 | 0.022888 | 0.11444 | -0.16937 | 0.059509 | -0.073242 | 122.8317 | 122.7722 | 59.0515 | -122.9233 | 122.8271 | 122.731 | 59.1522 | -123.0331
867.0156 | 123.1155 | -58.9508 | 63.8306 | -0.023041 | 0.0021085 | 0.069319 | 0.067313 | 0.13228 | -0.0041357 | -0.0036595 | -0.038299 | -0.0054944 | 0.061701 | 0.057398 | 0.0018584 | -0.0064194 | 63.8168 | 63.9999 | 0.041199 | -59.1476 | 63.8901 | -59.0286 | -59.0744 | -58.873 | 0.18768 | -59.1156 | 63.858 | 63.7527 | -59.1248 | -59.2163 | -0.077819 | -0.1236 | 0.05951 | 122.9507 | -0.19684 | -0.073242 | -0.013733 | -0.17395 | -0.2655 | 0.027466 | 0.07782 | -0.16479 | 0.10071 | -0.077819 | 122.8409 | 122.7676 | 58.992 | -122.905 | 122.8088 | 122.7036 | 59.1385 | -123.0469
868.0156 | 123.0331 | -59.0103 | 63.8535 | -0.18326 | 0.01279 | 0.068464 | 0.074149 | 0.13014 | 0.0052637 | -0.0034457 | -0.20615 | -0.0048536 | 0.062342 | 0.059321 | 0.0042084 | -0.011119 | 63.7665 | 63.8809 | -0.027466 | -59.1888 | 63.9359 | -59.0515 | -59.1476 | -58.9645 | 0.068665 | -59.2438 | 63.9221 | 63.7848 | -59.1385 | -59.2209 | -0.041199 | -0.13733 | 0.082397 | 122.8912 | -0.17853 | -0.041199 | -0.086976 | -0.12817 | -0.21057 | 0.068664 | 0.045776 | -0.23346 | -0.022888 | -0.068665 | 122.9462 | 122.7768 | 58.9828 | -123.0011 | 122.9324 | 122.7951 | 59.079 | -123.0743
869.0156 | 123.1247 | -58.9737 | 63.8214 | -0.20615 | 0.0050991 | 0.068678 | 0.068381 | 0.12971 | -0.0030677 | -0.0028049 | -0.47317 | -0.0050672 | 0.060419 | 0.060389 | 0.0022858 | -0.0059922 | 63.8077 | 64.0228 | 0.07782 | -59.1614 | 63.8718 | -59.0286 | -59.079 | -58.873 | 0.13733 | -59.1614 | 63.8351 | 63.7527 | -59.1156 | -59.1888 | -0.054931 | -0.10528 | 0.050354 | 122.9965 | -0.18768 | -0.082398 | -0.013733 | -0.14191 | -0.21515 | 0.013733 | 0.10071 | -0.18768 | 0.027466 | -0.068664 | 122.8455 | 122.7814 | 59.0515 | -122.9004 | 122.8088 | 122.7264 | 59.111 | -123.0103
870.0156 | 123.111 | -58.96 | 63.826 | -0.015411 | 0.0040311 | 0.068891 | 0.069235 | 0.12993 | -0.0041357 | -0.0045139 | 0.076141 | -0.0067762 | 0.060205 | 0.059107 | 0.0029266 | -0.005565 | 63.7939 | 63.9771 | 0.022888 | -59.1431 | 63.8718 | -59.0378 | -59.0927 | -58.9096 | 0.14648 | -59.1385 | 63.8535 | 63.7756 | -59.111 | -59.2072 | -0.07782 | -0.13275 | 0.045776 | 122.937 | -0.1831 | -0.050354 | -0.032044 | -0.15106 | -0.24719 | 0.027466 | 0.050354 | -0.17853 | 0.068664 | -0.050354 | 122.8317 | 122.7539 | 58.9828 | -122.9187 | 122.8134 | 122.7356 | 59.1064 | -123.0331
871.0156 | 123.143 | -58.9874 | 63.7985 | -0.14511 | 0.0057401 | 0.067823 | 0.068167 | 0.13014 | -0.0013587 | -0.0032321 | -0.10696 | -0.0054944 | 0.06106 | 0.058894 | 0.002713 | -0.0068466 | 63.8489 | 64.0366 | 0.082397 | -59.1248 | 63.8809 | -59.0149 | -59.1019 | -58.8959 | 0.13733 | -58.8776 | 63.8901 | 63.8351 | -59.0927 | -59.2026 | -0.027466 | -0.11444 | 0.082397 | 123.024 | -0.13733 | -0.022888 | 0.050354 | -0.10529 | -0.21515 | 0.091553 | 0.091553 | 0.10986 | 0.32501 | 0.036621 | 122.8683 | 122.8363 | 59.0698 | -122.9004 | 122.8775 | 122.8226 | 59.1248 | -123.0011
872.0156 | 123.1018 | -58.9828 | 63.8535 | -0.52658 | 0.0046719 | 0.069105 | 0.071585 | 0.12928 | -0.0011451 | -0.0036595 | -0.084076 | -0.0054944 | 0.061701 | 0.059107 | 0.0052764 | -0.0074876 | 63.8306 | 64.0091 | 0.07782 | -59.1293 | 63.8718 | -59.0332 | -59.0973 | -58.9142 | 0.17853 | -59.1614 | 63.8809 | 63.7573 | -59.1385 | -59.2163 | -0.050354 | -0.11444 | 0.01831 | 122.9919 | -0.14648 | -0.032043 | -0.022889 | -0.15564 | -0.23346 | 0.027465 | 0.068664 | -0.17853 | 0.054932 | -0.096131 | 122.8546 | 122.8134 | 59.0607 | -122.9507 | 122.8638 | 122.7402 | 59.1614 | -123.0698
873.0156 | 123.0286 | -58.9828 | 63.8672 | -0.19089 | 0.0061673 | 0.066755 | 0.069449 | 0.13249 | -0.00093145 | -0.0055821 | -0.17563 | -0.0067762 | 0.060633 | 0.062953 | 0.0037812 | -0.0068466 | 63.7985 | 63.9633 | 0.045776 | -59.1476 | 63.8992 | -59.0378 | -59.1064 | -58.9462 | 0.11902 | -59.23 | 63.9175 | 63.7573 | -59.1339 | -59.2072 | -0.054932 | -0.1236 | 0.032044 | 122.9462 | -0.16479 | -0.041199 | -0.068664 | -0.15106 | -0.2243 | 0.050355 | 0.036621 | -0.24719 | -0.022889 | -0.10986 | 122.8821 | 122.7814 | 59.0286 | -122.9736 | 122.9004 | 122.7402 | 59.1019 | -123.0743
874.0156 | 123.0743 | -58.9966 | 63.8123 | 0.0074768 | 0.0036039 | 0.06761 | 0.069235 | 0.12971 | -0.0045631 | -0.0047275 | 0.022736 | -0.0072034 | 0.060419 | 0.059748 | -0.00027778 | -0.0044968 | 63.7482 | 63.9542 | -0.004578 | -59.166 | 63.8809 | -59.0424 | -59.1064 | -58.905 | 0.091553 | -59.1751 | 63.8718 | 63.7665 | -59.1156 | -59.1934 | -0.045776 | -0.10986 | 0.068664 | 122.9507 | -0.16937 | -0.05951 | -0.064087 | -0.11902 | -0.19684 | 0.059509 | 0.091553 | -0.17853 | 0.01831 | -0.045777 | 122.8775 | 122.7448 | 58.992 | -122.9187 | 122.8683 | 122.7631 | 59.0881 | -123.0057
875.0156 | 123.1064 | -58.96 | 63.8306 | -0.091705 | 0.0042447 | 0.067823 | 0.06774 | 0.12907 | -0.0019995 | -0.0043003 | 0.0074766 | -0.0067762 | 0.057855 | 0.058894 | 0.00057682 | -0.006633 | 63.8123 | 63.9862 | 0.036621 | -59.1568 | 63.8855 | -59.0424 | -59.1064 | -58.873 | 0.16022 | -59.1385 | 63.858 | 63.7573 | -59.1293 | -59.2072 | -0.082397 | -0.14648 | 0.054932 | 122.9462 | -0.19684 | -0.050354 | -0.01831 | -0.16937 | -0.24719 | 0.027466 | 0.086975 | -0.17853 | 0.068664 | -0.073242 | 122.8455 | 122.7722 | 58.9966 | -122.937 | 122.818 | 122.7173 | 59.1202 | -123.0377
876.0156 | 123.0881 | -58.9828 | 63.8123 | -0.12985 | 0.0042447 | 0.066755 | 0.066031 | 0.13142 | 0.00035035 | -0.0032321 | -0.12985 | -0.0061352 | 0.059137 | 0.057826 | 0.0057038 | -0.0059922 | 63.8809 | 64.0366 | 0.091553 | -59.111 | 63.8763 | -59.0195 | -59.0927 | -58.7631 | 0.48065 | -59.3903 | 63.8947 | 63.7619 | -59.1156 | -59.2117 | -0.036621 | -0.10986 | 0.064087 | 123.0194 | -0.12817 | -0.018311 | 0.068664 | -0.13275 | -0.22888 | 0.082397 | 0.21973 | -0.40741 | -0.17853 | -0.050354 | 122.8592 | 122.8638 | 59.0744 | -122.905 | 122.8775 | 122.7448 | 59.4635 | -123.024
877.0156 | 123.1064 | -58.9691 | 63.858 | -0.57999 | 0.0065945 | 0.06761 | 0.067954 | 0.12993 | -0.0032813 | -0.0023777 | -0.10696 | -0.008058 | 0.059992 | 0.059107 | 0.0018584 | -0.0077012 | 63.8306 | 63.9999 | 0.073242 | -59.1385 | 63.8763 | -59.0469 | -59.0881 | -58.9005 | 0.16937 | -59.1614 | 63.8718 | 63.7527 | -59.1064 | -59.2072 | -0.07782 | -0.11902 | 0.018311 | 122.9691 | -0.16937 | -0.050354 | -0.027466 | -0.13733 | -0.23804 | 0.013733 | 0.068664 | -0.19226 | 0.045776 | -0.10529 | 122.8455 | 122.7997 | 59.0424 | -122.9462 | 122.8409 | 122.7219 | 59.1385 | -123.0652
878.0156 | 123.0469 | -58.9874 | 63.8535 | -0.26718 | 0.0072355 | 0.066969 | 0.069663 | 0.12715 | 0.00013675 | -0.0038731 | -0.19852 | -0.0072034 | 0.060205 | 0.059321 | 0.0024994 | -0.0077012 | 63.7939 | 63.9725 | 0.054932 | -59.1522 | 63.8947 | -59.0332 | -59.111 | -58.9371 | 0.13733 | -59.2072 | 63.9038 | 63.7756 | -59.1293 | -59.2209 | -0.045776 | -0.1236 | 0.041198 | 122.9599 | -0.1648 | -0.041199 | -0.05951 | -0.14191 | -0.23346 | 0.050354 | 0.050354 | -0.21973 | 0.013733 | -0.07782 | 122.8821 | 122.7814 | 59.0424 | -122.9645 | 122.8912 | 122.7631 | 59.1248 | -123.0743
879.0156 | 123.1064 | -58.96 | 63.8214 | -0.053558 | 0.0029629 | 0.069959 | 0.067526 | 0.12758 | -0.0041357 | -0.0034457 | -0.015411 | -0.0082716 | 0.062128 | 0.06103 | 0.00079042 | -0.005565 | 63.7939 | 64.0045 | 0.041199 | -59.1568 | 63.8672 | -59.0424 | -59.1019 | -58.873 | 0.15106 | -59.1385 | 63.8489 | 63.739 | -59.1064 | -59.1934 | -0.082397 | -0.14191 | 0.045776 | 122.9645 | -0.19684 | -0.054931 | -0.027466 | -0.14648 | -0.23346 | 0.027466 | 0.086975 | -0.17853 | 0.054931 | -0.082397 | 122.8271 | 122.7539 | 59.0012 | -122.9233 | 122.8088 | 122.699 | 59.111 | -123.0148
880.0156 | 123.1476 | -58.9737 | 63.8214 | -0.068817 | 0.0023221 | 0.069532 | 0.070731 | 0.13014 | -0.0015723 | -0.0045139 | 0.053253 | -0.0089124 | 0.061701 | 0.058039 | 0.0024994 | -0.0074876 | 63.8031 | 63.9542 | 0.027466 | -59.1614 | 63.8809 | -59.0286 | -59.0973 | -58.9005 | 0.15564 | -59.1522 | 63.8443 | 63.7573 | -59.1202 | -59.2072 | -0.054931 | -0.1236 | 0.059509 | 122.9279 | -0.18768 | -0.064087 | -0.01831 | -0.14648 | -0.23346 | 0.022888 | 0.073242 | -0.17853 | 0.054931 | -0.064087 | 122.8546 | 122.7768 | 59.0012 | -122.9187 | 122.818 | 122.731 | 59.1293 | -123.0286
881.0156 | 123.1064 | -58.9783 | 63.8077 | 0.65598 | 0.0057401 | 0.069105 | 0.068167 | 0.13014 | -0.00029045 | -0.0025913 | -0.099335 | -0.0059216 | 0.059564 | 0.059321 | 0.0016448 | -0.0079148 | 63.8351 | 64.0091 | 0.064087 | -59.1431 | 63.8855 | -59.0332 | -59.0973 | -58.9005 | 0.16479 | -59.1568 | 63.8947 | 63.7665 | -59.111 | -59.1888 | -0.054932 | -0.11902 | 0.07782 | 122.9874 | -0.16479 | -0.045776 | 0.027466 | -0.13275 | -0.21057 | 0.086975 | 0.077819 | -0.17853 | 0.032044 | -0.041199 | 122.8638 | 122.8134 | 59.0424 | -122.905 | 122.8729 | 122.7447 | 59.1431 | -122.9965
882.0156 | 123.1155 | -59.0012 | 63.8214 | -0.15274 | 0.0065945 | 0.070387 | 0.069449 | 0.12993 | 0.0035547 | -0.0025913 | -0.36636 | -0.007417 | 0.061273 | 0.060603 | 0.0031402 | -0.0068466 | 63.8672 | 63.9954 | 0.018311 | -59.1797 | 63.8626 | -59.0378 | -59.0973 | -58.8959 | 0.16022 | -59.1522 | 63.8763 | 63.7527 | -59.1156 | -59.1797 | -0.036621 | -0.09613 | 0.041199 | 122.9965 | -0.17853 | -0.082397 | 0.045776 | -0.11444 | -0.17853 | 0.054932 | 0.10529 | -0.15106 | 0.027465 | -0.068664 | 122.8638 | 122.8683 | 59.0195 | -122.9187 | 122.8775 | 122.7539 | 59.1614 | -123.0011
883.0156 | 123.0652 | -58.9874 | 63.8443 | -0.14511 | 0.0065945 | 0.067823 | 0.069876 | 0.1295 | -0.0013587 | -0.0047275 | -0.168 | -0.0059216 | 0.063837 | 0.057826 | 0.002713 | -0.006633 | 63.8123 | 64.0228 | 0.064087 | -59.1385 | 63.913 | -59.0469 | -59.1248 | -58.9188 | 0.15106 | -59.1934 | 63.8809 | 63.7482 | -59.1156 | -59.2072 | -0.059509 | -0.13733 | 0.068665 | 123.0103 | -0.15106 | -0.013733 | -0.032043 | -0.12817 | -0.21973 | 0.036621 | 0.068665 | -0.20599 | 0.013733 | -0.09613 | 122.9004 | 122.7997 | 59.0515 | -122.9691 | 122.8683 | 122.7356 | 59.1385 | -123.0515
884.0156 | 123.1064 | -58.9691 | 63.8077 | 0.0074768 | 0.0018949 | 0.069319 | 0.067954 | 0.12971 | -0.0026405 | -0.0049411 | 0.083771 | -0.008058 | 0.05871 | 0.060389 | 0.002713 | -0.0064194 | 63.8123 | 63.9771 | 0.013733 | -59.1751 | 63.8855 | -59.0424 | -59.111 | -58.8959 | 0.13275 | -59.166 | 63.8535 | 63.7344 | -59.1202 | -59.2163 | -0.073242 | -0.14191 | 0.07782 | 122.9462 | -0.20599 | -0.064087 | 0.004578 | -0.15106 | -0.24719 | 0.045777 | 0.073242 | -0.19684 | 0.050354 | -0.073242 | 122.8546 | 122.7814 | 58.9828 | -122.9187 | 122.8226 | 122.7036 | 59.1019 | -123.024
885.0156 | 123.0743 | -58.9737 | 63.8351 | 0.75516 | 0.0048855 | 0.068678 | 0.071158 | 0.13185 | -0.0028541 | -0.0038731 | -0.168 | -0.0078442 | 0.061487 | 0.058894 | 0.0018584 | -0.0085556 | 63.8489 | 64.0228 | 0.059509 | -59.1431 | 63.8809 | -59.0561 | -59.1202 | -58.9005 | 0.1831 | -59.1614 | 63.8947 | 63.739 | -59.1202 | -59.1934 | -0.082397 | -0.14648 | 0.045776 | 122.9965 | -0.16937 | -0.022888 | 0.013733 | -0.14648 | -0.21973 | 0.059509 | 0.073242 | -0.18768 | 0.032043 | -0.09613 | 122.8546 | 122.8226 | 59.0332 | -122.9553 | 122.8683 | 122.7127 | 59.1568 | -123.0286
886.0156 | 123.0743 | -58.9874 | 63.7985 | 0.15244 | 0.0048855 | 0.06761 | 0.066458 | 0.12843 | 0.00013675 | -0.0034457 | 0.13718 | -0.0059216 | 0.060846 | 0.05868 | 0.001004 | -0.0051376 | 63.7573 | 63.913 | -0.07782 | -59.2117 | 63.858 | -59.0332 | -59.1293 | -58.9554 | 0.004578 | -59.2346 | 63.8397 | 63.7299 | -59.1293 | -59.2209 | -0.045776 | -0.14191 | 0.059509 | 122.9004 | -0.2243 | -0.082398 | -0.041199 | -0.14191 | -0.23346 | 0.041199 | 0.032044 | -0.24719 | -0.013733 | -0.068665 | 122.8455 | 122.7448 | 58.9096 | -122.9279 | 122.8271 | 122.7173 | 58.992 | -123.0194
887.0156 | 123.0835 | -58.9783 | 63.8077 | -0.03067 | 0.0046719 | 0.069105 | 0.071799 | 0.13035 | -0.0024269 | -0.0055821 | -0.0077819 | -0.005708 | 0.059564 | 0.058039 | 0.002713 | -0.006633 | 63.7802 | 63.8992 | -0.009155 | -59.1751 | 63.858 | -59.0607 | -59.1064 | -58.9142 | 0.10071 | -59.1797 | 63.8489 | 63.7436 | -59.1339 | -59.2163 | -0.082398 | -0.12817 | 0.050354 | 122.8775 | -0.19684 | -0.068665 | -0.027466 | -0.15564 | -0.23804 | 0.041199 | 0.064086 | -0.20142 | 0.036622 | -0.064087 | 122.8363 | 122.7585 | 58.9691 | -122.9141 | 122.8271 | 122.7219 | 59.079 | -123.024
888.0156 | 123.1293 | -58.9645 | 63.8168 | -0.091705 | 0.0033901 | 0.070387 | 0.069663 | 0.12864 | -0.0017859 | -0.0045139 | -0.0077819 | -0.0082716 | 0.059778 | 0.06103 | 0.0018584 | -0.0062058 | 63.8123 | 63.9816 | 0.027466 | -59.1568 | 63.913 | -59.0424 | -59.1019 | -58.8867 | 0.13733 | -59.1431 | 63.8535 | 63.7482 | -59.0836 | -59.2072 | -0.077819 | -0.13733 | 0.096131 | 122.9462 | -0.19226 | -0.054931 | -0.004577 | -0.11902 | -0.24261 | 0.036622 | 0.07782 | -0.17853 | 0.064087 | -0.068664 | 122.8775 | 122.7768 | 58.992 | -122.9187 | 122.818 | 122.7127 | 59.1019 | -123.024
889.0156 | 123.0743 | -59.0103 | 63.8077 | -0.091705 | 0.0044583 | 0.070173 | 0.069022 | 0.13121 | 0.00035035 | -0.0051547 | 0.068512 | -0.007417 | 0.059564 | 0.060389 | 0.0024994 | -0.0051376 | 63.7573 | 63.9221 | -0.032043 | -59.2026 | 63.8626 | -59.0469 | -59.1156 | -58.9233 | 0.054932 | -59.198 | 63.8672 | 63.7527 | -59.1522 | -59.2072 | -0.036621 | -0.10529 | 0.054932 | 122.9324 | -0.19226 | -0.086975 | -0.050354 | -0.14191 | -0.19684 | 0.059509 | 0.086975 | -0.18768 | 0.009155 | -0.054931 | 122.8729 | 122.7676 | 58.9783 | -122.9233 | 122.8775 | 122.7631 | 59.0652 | -123.0148
890.0156 | 123.0698 | -59.0195 | 63.7939 | 0.10666 | 0.0055265 | 0.067182 | 0.069449 | 0.12822 | -0.0024269 | -0.0030185 | 0.12192 | -0.0067762 | 0.060633 | 0.059748 | 0.0042084 | -0.0081284 | 63.7711 | 63.8992 | -0.059509 | -59.2072 | 63.8535 | -59.0424 | -59.1202 | -58.9508 | 0.032043 | -59.2255 | 63.8535 | 63.7436 | -59.1339 | -59.2255 | -0.022888 | -0.10071 | 0.05951 | 122.9187 | -0.18768 | -0.086975 | -0.022888 | -0.11444 | -0.20599 | 0.05951 | 0.068664 | -0.20599 | 0 | -0.050354 | 122.8729 | 122.7905 | 58.96 | -122.9141 | 122.8729 | 122.7631 | 59.0515 | -123.0194
891.0156 | 123.111 | -58.992 | 63.8123 | -0.053558 | 0.0033901 | 0.068464 | 0.067099 | 0.13228 | -0.0013587 | -0.0047275 | -0.03067 | -0.005708 | 0.062128 | 0.060176 | 0.0016448 | -0.0070602 | 63.7985 | 63.9496 | 0 | -59.166 | 63.8672 | -59.0469 | -59.0927 | -58.8821 | 0.1236 | -59.1751 | 63.8443 | 63.7527 | -59.1248 | -59.2163 | -0.054932 | -0.10071 | 0.054931 | 122.9416 | -0.17395 | -0.073243 | -0.013733 | -0.13275 | -0.22431 | 0.032043 | 0.10986 | -0.18311 | 0.041199 | -0.059509 | 122.8592 | 122.7905 | 58.992 | -122.905 | 122.8363 | 122.7448 | 59.1156 | -123.0286
892.0156 | 123.1384 | -58.9737 | 63.8306 | -0.099335 | 0.0042447 | 0.06825 | 0.068167 | 0.13163 | 0.00013675 | -0.0043003 | -0.015411 | -0.0067762 | 0.060846 | 0.058894 | 0.0037812 | -0.0094102 | 63.8443 | 64.0045 | 0.045776 | -59.1339 | 63.8763 | -59.0103 | -59.1064 | -58.8455 | 0.1831 | -59.1202 | 63.8397 | 63.7573 | -59.1019 | -59.1888 | -0.036621 | -0.13275 | 0.045777 | 122.9782 | -0.16022 | -0.027466 | 0.013733 | -0.12817 | -0.21515 | 0.009156 | 0.12817 | -0.14648 | 0.068665 | -0.073242 | 122.85 | 122.818 | 59.0195 | -122.937 | 122.8134 | 122.731 | 59.1568 | -123.0194
893.0156 | 123.056 | -58.9691 | 63.826 | -0.21378 | 0.0093717 | 0.067182 | 0.069449 | 0.13057 | 0.0012047 | -0.0040867 | -0.16037 | -0.0061352 | 0.060419 | 0.059321 | 0.0016448 | -0.0081284 | 63.8168 | 64.0045 | 0.054932 | -59.1339 | 63.8763 | -59.0378 | -59.1202 | -58.9279 | 0.14648 | -59.2026 | 63.8992 | 63.7619 | -59.1156 | -59.1934 | -0.068665 | -0.15106 | 0.050354 | 122.9736 | -0.16479 | -0.013733 | -0.009156 | -0.14648 | -0.2243 | 0.073242 | 0.041199 | -0.23346 | -0.009156 | -0.064087 | 122.8455 | 122.7859 | 59.024 | -122.9462 | 122.8683 | 122.731 | 59.1156 | -123.0194
894.0156 | 123.0698 | -59.0012 | 63.8123 | 0.099029 | 0.0050991 | 0.065901 | 0.069022 | 0.13099 | -0.0022131 | -0.0028049 | 0.076141 | -0.0065626 | 0.060846 | 0.059535 | 0.0016448 | -0.0068466 | 63.7527 | 63.9267 | -0.050354 | -59.1843 | 63.8535 | -59.0469 | -59.1156 | -58.9462 | 0.25177 | -59.1797 | 63.8718 | 63.7482 | -59.1248 | -59.2072 | -0.045776 | -0.11444 | 0.041199 | 122.9279 | -0.18311 | -0.068664 | -0.059509 | -0.1236 | -0.20599 | 0.059509 | 0.054932 | -0.17853 | 0.027466 | -0.064087 | 122.8546 | 122.7539 | 58.9508 | -122.9279 | 122.8729 | 122.7493 | 59.2529 | -123.0194
895.0156 | 123.1293 | -58.9828 | 63.8306 | -0.068817 | 0.0036039 | 0.067396 | 0.067526 | 0.13078 | -0.0019995 | -0.0025913 | -0.00015237 | -0.0048536 | 0.061487 | 0.059107 | 0.0039948 | -0.0057786 | 63.8168 | 63.9633 | 0.022888 | -59.1568 | 63.9038 | -59.0332 | -59.1019 | -58.8776 | 0.14648 | -59.1476 | 63.8718 | 63.7436 | -59.111 | -59.198 | -0.050354 | -0.11902 | 0.073243 | 122.9462 | -0.17395 | -0.054931 | -0.013733 | -0.12817 | -0.21515 | 0.041199 | 0.10529 | -0.16479 | 0.050354 | -0.086975 | 122.8867 | 122.7997 | 59.0057 | -122.9324 | 122.8546 | 122.7264 | 59.1293 | -123.0286
896.0156 | 123.0789 | -58.9462 | 63.8123 | -0.061188 | 0.0053129 | 0.069959 | 0.068381 | 0.13099 | -0.0013587 | -0.0036595 | -0.03067 | -0.006349 | 0.059992 | 0.058253 | 0.0012176 | -0.0089828 | 63.8077 | 63.9679 | 0.018311 | -59.1522 | 63.8855 | -59.0607 | -59.0973 | -58.8867 | 0.10071 | -59.1522 | 63.8626 | 63.7665 | -59.1156 | -59.1934 | -0.11444 | -0.15106 | 0.073242 | 122.9141 | -0.20599 | -0.054932 | -0.004578 | -0.16937 | -0.24719 | 0.050354 | 0.059509 | -0.20599 | 0.041198 | -0.045777 | 122.8317 | 122.7539 | 58.9645 | -122.9095 | 122.8088 | 122.7127 | 59.0469 | -123.0057
897.0156 | 123.1567 | -58.9508 | 63.826 | -0.015411 | 0.0038175 | 0.06761 | 0.068167 | 0.13249 | -0.0026405 | -0.0049411 | -0.091705 | -0.007417 | 0.061273 | 0.059748 | 0.0035674 | -0.0081284 | 63.858 | 64.0366 | 0.068665 | -59.1202 | 63.8718 | -59.0012 | -59.079 | -58.8455 | 0.17853 | -59.1248 | 63.8763 | 63.7527 | -59.1293 | -59.2026 | -0.050354 | -0.12817 | 0.045776 | 122.9874 | -0.16937 | -0.041199 | 0.032043 | -0.17853 | -0.25177 | 0.050354 | 0.10529 | -0.17395 | 0.07782 | -0.073242 | 122.8226 | 122.8088 | 59.0195 | -122.905 | 122.8271 | 122.7036 | 59.1293 | -123.0286
898.0156 | 123.0881 | -58.9645 | 63.8168 | -0.13748 | 0.0063809 | 0.070173 | 0.073081 | 0.12886 | 0.0037683 | -0.0036595 | -0.36636 | -0.008058 | 0.059778 | 0.059748 | 0.0033538 | -0.0053512 | 63.7527 | 64.0274 | 0.054932 | -59.1934 | 63.8763 | -59.0286 | -59.0973 | -58.8776 | 0.16937 | -59.1568 | 63.8763 | 63.7619 | -59.1431 | -59.1843 | -0.064086 | -0.13275 | 0.05951 | 122.9919 | -0.22888 | -0.09613 | -0.064086 | -0.17853 | -0.21973 | 0.05951 | 0.086976 | -0.19226 | 0.027466 | -0.054931 | 122.8409 | 122.7173 | 59.0195 | -122.9141 | 122.8409 | 122.7264 | 59.1339 | -123.0011
899.0156 | 123.0743 | -58.992 | 63.8306 | 0.0074768 | 0.0023221 | 0.069105 | 0.069449 | 0.12928 | -0.0026405 | -0.0040867 | -0.00015237 | -0.0089124 | 0.058924 | 0.06103 | 0.004422 | -0.0057786 | 63.7848 | 63.9542 | -0.013733 | -59.1797 | 63.8809 | -59.0469 | -59.1019 | -58.9188 | 0.10529 | -59.1751 | 63.8672 | 63.7299 | -59.1431 | -59.2072 | -0.054932 | -0.10986 | 0.050354 | 122.9462 | -0.18768 | -0.077819 | -0.045776 | -0.15106 | -0.21515 | 0.036621 | 0.073242 | -0.18311 | 0.032043 | -0.10071 | 122.8729 | 122.7768 | 58.9783 | -122.9324 | 122.8592 | 122.7219 | 59.0973 | -123.0377
900.0156 | 123.1522 | -58.9325 | 63.8077 | -0.12985 | 0.0038175 | 0.072096 | 0.068167 | 0.13228 | -0.0032813 | -0.00088226 | -0.12222 | -0.012971 | 0.062982 | 0.062525 | 0.0046356 | -0.0068466 | 63.8718 | 64.0594 | 0.073242 | -59.1339 | 63.9038 | -59.0286 | -59.0836 | -58.8226 | 0.14191 | -59.2163 | 63.858 | 63.7436 | -59.1339 | -59.1705 | -0.09613 | -0.15106 | 0.096131 | 122.9919 | -0.20142 | -0.050354 | 0.064087 | -0.20142 | -0.23804 | 0.050354 | 0.10986 | -0.28381 | -0.045777 | -0.064087 | 122.8363 | 122.8043 | 59.0057 | -122.8912 | 122.7905 | 122.6761 | 59.0744 | -122.9782
901.0156 | 123.0743 | -58.9783 | 63.8306 | 0.083771 | 0.0055265 | 0.068037 | 0.069876 | 0.1295 | 0.00056395 | -0.0036595 | 0.060883 | -0.0093396 | 0.06106 | 0.059107 | 0.0029266 | -0.0051376 | 63.7527 | 63.9221 | -0.050354 | -59.198 | 63.8947 | -59.0744 | -59.1293 | -58.9096 | 0.064087 | -59.198 | 63.8672 | 63.7527 | -59.1202 | -59.2117 | -0.096131 | -0.15106 | 0.064087 | 122.9004 | -0.21973 | -0.068665 | -0.077819 | -0.14191 | -0.23346 | 0.036621 | 0.068664 | -0.21973 | 0.013733 | -0.077819 | 122.8729 | 122.731 | 58.9279 | -122.9599 | 122.8455 | 122.731 | 59.0424 | -123.0423
902.0156 | 123.1247 | -58.9737 | 63.8077 | -0.045929 | 0.0048855 | 0.06761 | 0.067954 | 0.13014 | -0.0026405 | -0.0030185 | 0.037995 | -0.008058 | 0.059351 | 0.059107 | 0.002713 | -0.0070602 | 63.8214 | 63.9404 | 0.022888 | -59.1568 | 63.8763 | -59.0378 | -59.1064 | -58.9142 | 0.13275 | -59.1614 | 63.858 | 63.7344 | -59.1293 | -59.198 | -0.064087 | -0.13275 | 0.068665 | 122.9141 | -0.1831 | -0.050354 | 0.013733 | -0.15564 | -0.2243 | 0.050354 | 0.059509 | -0.18768 | 0.036621 | -0.073242 | 122.85 | 122.7951 | 58.9966 | -122.9141 | 122.8317 | 122.7081 | 59.1064 | -123.0057
903.0156 | 123.0057 | -58.9783 | 63.8535 | -0.23666 | 0.0061673 | 0.06761 | 0.070731 | 0.13206 | 0.00077755 | -0.0023777 | -0.20615 | -0.0065626 | 0.061701 | 0.058894 | 0.0048492 | -0.0085556 | 63.8351 | 63.9908 | 0.045776 | -59.1476 | 63.9084 | -59.0378 | -59.0836 | -58.9188 | 0.1236 | -59.198 | 63.9221 | 63.7802 | -59.1385 | -59.1888 | -0.05951 | -0.10529 | 0.054931 | 122.9691 | -0.16937 | -0.064087 | -0.018311 | -0.16022 | -0.21057 | 0.068664 | 0.059509 | -0.21973 | -0.009155 | -0.073243 | 122.8867 | 122.8134 | 59.024 | -122.937 | 122.9004 | 122.7585 | 59.1019 | -123.0423
904.0156 | 123.0652 | -58.9691 | 63.826 | 0.015106 | 0.0042447 | 0.068037 | 0.067526 | 0.13185 | -0.0015723 | -0.0045139 | 0.022736 | -0.0059216 | 0.060633 | 0.059748 | 0.0022858 | -0.0040696 | 63.7802 | 63.9404 | -0.027466 | -59.1797 | 63.9267 | -59.0286 | -59.0973 | -58.9005 | 0.086975 | -59.1705 | 63.8626 | 63.7573 | -59.1385 | -59.1934 | -0.059509 | -0.12817 | 0.10071 | 122.9095 | -0.21057 | -0.082397 | -0.045777 | -0.16937 | -0.2243 | 0.036621 | 0.068664 | -0.20142 | 0.022888 | -0.068665 | 122.8958 | 122.7493 | 58.9417 | -122.9233 | 122.8317 | 122.7264 | 59.0561 | -123.0194
905.0156 | 123.111 | -58.96 | 63.8306 | 0.015106 | 0.0068081 | 0.066969 | 0.069449 | 0.12886 | -0.0015723 | -0.0017369 | 0.0074766 | -0.0078442 | 0.060205 | 0.05868 | 0.0039948 | -0.0059922 | 63.7802 | 63.9313 | -0.027466 | -59.1751 | 63.8992 | -59.024 | -59.0973 | -58.9096 | 0.068665 | -59.1751 | 63.8672 | 63.7665 | -59.111 | -59.2163 | -0.064087 | -0.13733 | 0.068665 | 122.8912 | -0.21515 | -0.07782 | -0.050354 | -0.15106 | -0.25635 | 0.036621 | 0.050354 | -0.21515 | 0.041199 | -0.064087 | 122.8592 | 122.7402 | 58.9325 | -122.9279 | 122.8271 | 122.7264 | 59.0286 | -123.0469
906.0156 | 123.0331 | -58.9966 | 63.8214 | -0.31296 | 0.0063809 | 0.068891 | 0.069235 | 0.12971 | -0.0024269 | -0.0040867 | 0.030365 | -0.0078442 | 0.058069 | 0.058894 | 0.0031402 | -0.0068466 | 63.7619 | 63.8992 | -0.045776 | -59.1843 | 63.8763 | -59.0607 | -59.1293 | -58.9371 | 0.041199 | -59.2026 | 63.8763 | 63.7482 | -59.1385 | -59.2163 | -0.064087 | -0.13275 | 0.054932 | 122.8958 | -0.18768 | -0.054932 | -0.059509 | -0.14191 | -0.21973 | 0.054932 | 0.059509 | -0.20599 | 0.013733 | -0.073242 | 122.8729 | 122.7585 | 58.9508 | -122.9507 | 122.8729 | 122.7448 | 59.0378 | -123.0377
907.0156 | 123.1064 | -58.9783 | 63.8123 | -0.053558 | 0.0048855 | 0.068464 | 0.067954 | 0.12672 | -0.00093145 | -0.0051547 | 0.022736 | -0.0050672 | 0.062342 | 0.060816 | 0.0018584 | -0.0053512 | 63.8123 | 63.9542 | -0.004578 | -59.166 | 63.8947 | -59.0286 | -59.1064 | -58.9096 | 0.09613 | -59.166 | 63.858 | 63.7436 | -59.1293 | -59.1797 | -0.050354 | -0.12817 | 0.082397 | 122.9324 | -0.18768 | -0.05951 | 0 | -0.15106 | -0.20142 | 0.045776 | 0.068664 | -0.18768 | 0.013732 | -0.068665 | 122.8729 | 122.7905 | 58.9737 | -122.9187 | 122.8363 | 122.7219 | 59.0744 | -122.9919
908.0156 | 123.1201 | -58.9508 | 63.8535 | -0.19852 | 0.0055265 | 0.067823 | 0.069449 | 0.12822 | -0.00093145 | -0.0040867 | 0.75516 | -0.0069898 | 0.063623 | 0.05868 | 0.0020722 | -0.008342 | 63.7619 | 64.4302 | 0.30212 | -59.2438 | 63.9221 | -59.0103 | -59.1248 | -58.8547 | 0.19226 | -59.1568 | 63.9084 | 63.7711 | -59.1385 | -59.1797 | -0.059509 | -0.17395 | 0.068664 | 123.381 | -0.29297 | -0.11902 | -0.091553 | -0.18768 | -0.22888 | 0.054931 | 0.096131 | -0.20599 | 0.022888 | -0.082398 | 122.8729 | 122.7127 | 59.2529 | -122.9782 | 122.8592 | 122.7219 | 59.1431 | -123.0331
909.0156 | 123.1064 | -58.9783 | 63.8397 | 0.053253 | 0.0036039 | 0.068891 | 0.067526 | 0.12886 | -0.0049903 | -0.0028049 | 0.060883 | -0.0061352 | 0.060633 | 0.059962 | 0.0033538 | -0.0074876 | 63.7756 | 63.9221 | -0.032043 | -59.1843 | 63.8763 | -59.0698 | -59.0927 | -58.9279 | 0.07782 | -59.1888 | 63.8809 | 63.7756 | -59.1293 | -59.2026 | -0.091553 | -0.11444 | 0.036621 | 122.9004 | -0.20599 | -0.091553 | -0.064087 | -0.15106 | -0.22431 | 0.041198 | 0.050354 | -0.21057 | 0.013733 | -0.064087 | 122.8546 | 122.7539 | 58.9462 | -122.9324 | 122.8592 | 122.7539 | 59.0561 | -123.0423
910.0156 | 123.0927 | -58.9783 | 63.8077 | 0.13718 | 0.0072355 | 0.069319 | 0.069663 | 0.13228 | -7.6852e-05 | -0.0013095 | 0.20584 | -0.0069898 | 0.061701 | 0.059107 | 0.0035674 | -0.0072738 | 63.826 | 63.9542 | -0.050354 | -59.1888 | 63.8763 | -59.0515 | -59.111 | -58.905 | 0.027466 | -59.2072 | 63.8489 | 63.7436 | -59.1339 | -59.2117 | -0.073243 | -0.13275 | 0.068665 | 122.9324 | -0.21057 | -0.07782 | 0.018311 | -0.15564 | -0.23346 | 0.041199 | 0.073242 | -0.22888 | 0.004578 | -0.064087 | 122.8546 | 122.8043 | 58.9279 | -122.9187 | 122.8271 | 122.7219 | 59.0057 | -123.0194
911.0156 | 123.0881 | -58.96 | 63.8351 | 0.022736 | 0.0033901 | 0.068037 | 0.066885 | 0.13057 | -0.0011451 | -0.0034457 | -0.038299 | -0.0044264 | 0.062128 | 0.059748 | 0.0031402 | -0.0077012 | 63.8077 | 63.945 | 0.004578 | -59.1476 | 63.9084 | -59.0515 | -59.0881 | -58.8913 | 0.10071 | -59.1614 | 63.8763 | 63.7711 | -59.1156 | -59.1934 | -0.091553 | -0.12817 | 0.073242 | 122.905 | -0.18768 | -0.059509 | -0.027466 | -0.15564 | -0.23346 | 0.041199 | 0.068665 | -0.20142 | 0.032043 | -0.064087 | 122.8683 | 122.7676 | 58.9645 | -122.9233 | 122.8363 | 122.731 | 59.0607 | -123.0286
912.0156 | 123.0927 | -58.9828 | 63.8351 | -0.00015269 | 0.0010403 | 0.068891 | 0.07009 | 0.12822 | -0.0024269 | -0.0030185 | 0.045624 | -0.007417 | 0.062769 | 0.059107 | 0.0031402 | -0.0062058 | 63.7848 | 63.9313 | -0.013733 | -59.1751 | 63.8809 | -59.0332 | -59.0973 | -58.8959 | 0.086975 | -59.1705 | 63.8672 | 63.7482 | -59.1156 | -59.2026 | -0.050354 | -0.11444 | 0.045776 | 122.9141 | -0.19226 | -0.07782 | -0.050354 | -0.13275 | -0.21973 | 0.032043 | 0.086975 | -0.18768 | 0.032044 | -0.086975 | 122.8638 | 122.7676 | 58.9691 | -122.9324 | 122.85 | 122.731 | 59.0698 | -123.0377
913.0156 | 123.1293 | -58.9554 | 63.8306 | -0.084076 | 0.0031765 | 0.068037 | 0.069235 | 0.13014 | -0.0011451 | -0.0040867 | -0.038299 | -0.0072034 | 0.061701 | 0.059962 | 0.0033538 | -0.0057786 | 63.8214 | 63.9954 | 0.027466 | -59.1476 | 63.913 | -59.0332 | -59.0973 | -58.8547 | 0.11902 | -59.1431 | 63.8809 | 63.7665 | -59.1202 | -59.2117 | -0.07782 | -0.14191 | 0.082398 | 122.9507 | -0.19226 | -0.050354 | -0.009155 | -0.1648 | -0.25635 | 0.050354 | 0.10071 | -0.18768 | 0.068665 | -0.064087 | 122.8683 | 122.7768 | 58.9828 | -122.9279 | 122.8363 | 122.7219 | 59.0744 | -123.0423
914.0156 | 123.0469 | -58.9828 | 63.8214 | 0.12192 | 0.0061673 | 0.067396 | 0.069876 | 0.12971 | 0.00056395 | -0.0036595 | 0.19058 | -0.007417 | 0.061701 | 0.059321 | 0.0050628 | -0.0074876 | 63.8306 | 63.9587 | -0.050354 | -59.1843 | 63.8535 | -59.0378 | -59.0881 | -58.9005 | 0.027466 | -59.198 | 63.858 | 63.739 | -59.111 | -59.2163 | -0.054932 | -0.10529 | 0.032044 | 122.9416 | -0.20142 | -0.09613 | 0.009155 | -0.12817 | -0.23346 | 0.036621 | 0.082397 | -0.21515 | 0.018311 | -0.082397 | 122.8363 | 122.8134 | 58.9325 | -122.9095 | 122.8409 | 122.7219 | 59.0103 | -123.0377
915.0156 | 123.0698 | -58.9874 | 63.8626 | 0.083771 | 0.0036039 | 0.066541 | 0.066458 | 0.13014 | -0.0030677 | -0.0034457 | 0.16769 | -0.0061352 | 0.061487 | 0.059748 | 0.0020722 | -0.0051376 | 63.7573 | 64.0411 | 0.036621 | -59.2438 | 63.8947 | -59.0286 | -59.0973 | -58.9371 | 0.036621 | -59.2026 | 63.8626 | 63.7573 | -59.1202 | -59.2072 | -0.041198 | -0.10986 | 0.032043 | 123.0286 | -0.25635 | -0.14648 | -0.10529 | -0.13275 | -0.21973 | 0 | 0.050354 | -0.21515 | 0.004577 | -0.10529 | 122.8821 | 122.7448 | 59.024 | -122.9599 | 122.85 | 122.7448 | 59.024 | -123.0698
916.0156 | 123.1155 | -58.992 | 63.8077 | -0.03067 | 0.0042447 | 0.069105 | 0.066672 | 0.13035 | -0.0011451 | -0.0051547 | -0.0077819 | -0.0059216 | 0.059564 | 0.057612 | 0.0035674 | -0.0072738 | 63.8077 | 63.945 | -0.018311 | -59.1476 | 63.9038 | -59.0469 | -59.0836 | -58.9096 | 0.091553 | -59.1522 | 63.8763 | 63.7665 | -59.111 | -59.1751 | -0.054932 | -0.091553 | 0.096131 | 122.937 | -0.15564 | -0.064087 | 0 | -0.11902 | -0.18311 | 0.068665 | 0.082397 | -0.16022 | 0.022888 | -0.041199 | 122.8958 | 122.7997 | 58.9737 | -122.8912 | 122.8683 | 122.7585 | 59.0836 | -122.9828
917.0156 | 123.1293 | -58.9828 | 63.8123 | 0.14481 | 0.0072355 | 0.068464 | 0.068594 | 0.12822 | -0.0022131 | -0.0032321 | 0.18295 | -0.0050672 | 0.059992 | 0.058253 | 0.0033538 | -0.0079148 | 63.8123 | 63.9496 | -0.032043 | -59.1385 | 63.8397 | -59.0103 | -59.0973 | -58.9096 | 0.018311 | -59.2072 | 63.8397 | 63.7299 | -59.1293 | -59.198 | -0.027466 | -0.11444 | 0.027466 | 122.9324 | -0.15564 | -0.041199 | 0 | -0.14648 | -0.21515 | 0.027466 | 0.073242 | -0.2243 | -0.009155 | -0.082398 | 122.8226 | 122.7951 | 58.9508 | -122.9095 | 122.8226 | 122.7127 | 59.0012 | -123.0103
918.0156 | 123.0652 | -58.992 | 63.8077 | 0.13718 | 0.010013 | 0.069532 | 0.068167 | 0.13099 | 0.00077755 | -0.0032321 | 0.19058 | -0.0059216 | 0.062555 | 0.060389 | 0.0042084 | -0.0051376 | 63.8397 | 63.9725 | -0.018311 | -59.1568 | 63.8809 | -59.0561 | -59.0973 | -58.9142 | 0.036621 | -59.1934 | 63.8626 | 63.739 | -59.1339 | -59.2209 | -0.064087 | -0.10529 | 0.073242 | 122.9645 | -0.16479 | -0.059509 | 0.032044 | -0.14191 | -0.22888 | 0.054932 | 0.077819 | -0.20142 | 0.027466 | -0.068664 | 122.8729 | 122.8317 | 58.9737 | -122.905 | 122.8546 | 122.731 | 59.0286 | -123.0286
919.0156 | 123.0789 | -58.992 | 63.8306 | 0.16769 | 0.0050991 | 0.06761 | 0.06774 | 0.13078 | -0.00029045 | -0.0021641 | 0.068512 | -0.0082716 | 0.061914 | 0.058467 | 0.0022858 | -0.0064194 | 63.7985 | 63.9267 | -0.054932 | -59.198 | 63.8763 | -59.0515 | -59.1156 | -58.9142 | 0.004578 | -59.2072 | 63.8718 | 63.7711 | -59.1156 | -59.2072 | -0.05951 | -0.1236 | 0.045777 | 122.9187 | -0.20599 | -0.082397 | -0.032043 | -0.1236 | -0.21515 | 0.041199 | 0.077819 | -0.21515 | 0 | -0.059509 | 122.8683 | 122.7905 | 58.9371 | -122.9462 | 122.8638 | 122.7631 | 58.9966 | -123.0377
920.0156 | 123.0652 | -58.992 | 63.8168 | 0.060882 | 0.0053129 | 0.068891 | 0.070944 | 0.12608 | -0.0015723 | -0.0043003 | -1.877 | -0.006349 | 0.061701 | 0.061885 | 0.0029266 | -0.0070602 | 63.7848 | 63.9359 | -0.041199 | -59.1843 | 63.9038 | -59.0378 | -59.1385 | -58.9417 | 0.022888 | -59.2026 | 63.8718 | 63.7848 | -59.1202 | -59.2209 | -0.045777 | -0.14648 | 0.086976 | 122.9279 | -0.19226 | -0.045776 | -0.032043 | -0.12817 | -0.22888 | 0.054932 | 0.050354 | -0.21057 | 0.01831 | -0.032043 | 122.8958 | 122.7768 | 58.9508 | -122.9553 | 122.8638 | 122.7768 | 59.0149 | -123.0377
921.0156 | 123.0469 | -58.9874 | 63.8031 | 0.15244 | 0.0080899 | 0.068464 | 0.068381 | 0.12907 | 0.00099115 | -0.0028049 | 0.23636 | -0.0059216 | 0.059564 | 0.058039 | 0.0031402 | -0.005565 | 63.826 | 63.9496 | -0.050354 | -59.198 | 63.8626 | -59.0378 | -59.1064 | -58.9142 | 0.013733 | -59.2163 | 63.8535 | 63.7802 | -59.1614 | -59.2209 | -0.050354 | -0.11902 | 0.059509 | 122.937 | -0.21057 | -0.091553 | 0.022888 | -0.17395 | -0.23346 | 0.050354 | 0.073242 | -0.22888 | 0.004577 | -0.022889 | 122.85 | 122.8134 | 58.9371 | -122.9095 | 122.8409 | 122.7676 | 59.0012 | -123.024
922.0156 | 123.0789 | -58.9874 | 63.8351 | 0.11429 | 0.0074491 | 0.068678 | 0.068594 | 0.12736 | 0.00013675 | -0.0021641 | 0.10666 | -0.0067762 | 0.060633 | 0.05868 | 0.0029266 | -0.0062058 | 63.8077 | 63.9221 | -0.050354 | -59.1843 | 63.8992 | -59.0103 | -59.079 | -58.9233 | 0.036621 | -59.1888 | 63.8672 | 63.7665 | -59.1293 | -59.1888 | -0.022888 | -0.091552 | 0.064087 | 122.9095 | -0.19684 | -0.10529 | -0.027466 | -0.14191 | -0.20142 | 0.032043 | 0.064087 | -0.20142 | 0 | -0.068665 | 122.8867 | 122.7951 | 58.9371 | -122.9141 | 122.8546 | 122.7539 | 59.024 | -123.024
923.0156 | 123.1338 | -58.9233 | 63.8306 | -0.14511 | 0.0025357 | 0.071668 | 0.068167 | 0.12843 | -0.0017859 | -0.0045139 | -0.10696 | -0.0082716 | 0.060205 | 0.059321 | 0.0039948 | -0.006633 | 63.8855 | 63.9999 | 0.050354 | -59.1019 | 63.913 | -59.0103 | -59.079 | -58.8089 | 0.19684 | -59.0973 | 63.9084 | 63.7939 | -59.1019 | -59.1797 | -0.086975 | -0.15564 | 0.082398 | 122.9233 | -0.17853 | -0.022889 | 0.054932 | -0.17853 | -0.25635 | 0.07782 | 0.11444 | -0.17395 | 0.082397 | -0.036621 | 122.8363 | 122.8088 | 58.9737 | -122.9095 | 122.8317 | 122.7173 | 59.1202 | -123.0103
924.0156 | 123.0652 | -58.9966 | 63.7939 | 0.099029 | 0.0063809 | 0.069319 | 0.068594 | 0.12993 | -0.0017859 | -0.0040867 | 0.17532 | -0.0076306 | 0.060846 | 0.060389 | 0.0029266 | -0.005565 | 63.7939 | 63.9313 | -0.073242 | -59.1888 | 63.8626 | -59.0378 | -59.111 | -58.9233 | 0.009155 | -59.1888 | 63.8535 | 63.7619 | -59.1385 | -59.2209 | -0.041199 | -0.11444 | 0.068665 | 122.9279 | -0.19226 | -0.07782 | 0 | -0.14191 | -0.2243 | 0.05951 | 0.073242 | -0.19226 | 0.032043 | -0.032043 | 122.8592 | 122.7905 | 58.9233 | -122.905 | 122.85 | 122.7585 | 59.0057 | -123.0148
925.0312 | 122.9919 | -58.9508 | 63.8855 | -2.083 | 0.0091581 | 0.068037 | 0.067099 | 0.13206 | 0.0022729 | -0.0032321 | -0.16037 | -0.0065626 | 0.061701 | 0.059962 | 0.004422 | -0.0085556 | 63.7756 | 63.8809 | -0.041199 | -59.1751 | 63.9587 | -59.0561 | -59.1202 | -58.9554 | 0.045776 | -59.2667 | 63.9496 | 63.8443 | -59.1431 | -59.2072 | -0.10529 | -0.16937 | 0.073242 | 122.8317 | -0.2243 | -0.054932 | -0.10986 | -0.19226 | -0.25635 | 0.064087 | -0.004577 | -0.31586 | -0.05951 | -0.041199 | 122.9095 | 122.7264 | 58.9096 | -123.0057 | 122.9004 | 122.7951 | 58.9966 | -123.0927
926.0156 | 123.056 | -58.9783 | 63.8214 | 0.16006 | 0.0057401 | 0.068037 | 0.068167 | 0.13078 | -0.00071785 | -0.0038731 | 0.22873 | -0.0054944 | 0.062128 | 0.059321 | 0.0039948 | -0.005565 | 63.7894 | 63.9542 | -0.036621 | -59.1797 | 63.8809 | -59.0378 | -59.0973 | -58.9188 | 0.022888 | -59.198 | 63.8626 | 63.7527 | -59.1248 | -59.2255 | -0.05951 | -0.11902 | 0.059509 | 122.9324 | -0.20142 | -0.082397 | -0.032043 | -0.14648 | -0.24719 | 0.041199 | 0.059509 | -0.21973 | 0.027466 | -0.068664 | 122.8592 | 122.7676 | 58.9417 | -122.9187 | 122.8409 | 122.731 | 59.0012 | -123.0469
927.0156 | 123.0606 | -58.9645 | 63.8306 | 0.11429 | 0.0063809 | 0.066969 | 0.068594 | 0.13078 | -0.0011451 | -0.0034457 | 0.24399 | -0.006349 | 0.060419 | 0.060603 | 0.0035674 | -0.0074876 | 63.8123 | 63.9542 | -0.050354 | -59.1705 | 63.858 | -59.0378 | -59.0881 | -58.8867 | 0.018311 | -59.2026 | 63.8443 | 63.7848 | -59.1248 | -59.198 | -0.073242 | -0.1236 | 0.027466 | 122.9187 | -0.20599 | -0.082397 | -0.01831 | -0.16022 | -0.23346 | 0.013733 | 0.07782 | -0.23804 | -0.004578 | -0.045776 | 122.8226 | 122.7768 | 58.9142 | -122.9187 | 122.8088 | 122.7493 | 58.9828 | -123.0286
928.0156 | 123.2986 | -58.9325 | 63.9038 | -0.061188 | 0.0031765 | 0.069532 | 0.067954 | 0.12971 | -0.0019995 | -0.0028049 | -0.061188 | -0.0061352 | 0.062342 | 0.058894 | 0.002713 | -0.0068466 | 63.8901 | 64.032 | 0.068665 | -59.1019 | 63.9267 | -59.024 | -59.0515 | -58.8364 | 0.16937 | -59.0927 | 63.8763 | 63.7985 | -59.0927 | -59.1751 | -0.091553 | -0.11902 | 0.022888 | 122.9645 | -0.16937 | -0.050354 | -0.013733 | -0.16022 | -0.24261 | -0.027466 | 0.09613 | -0.16022 | 0.082398 | -0.10529 | 122.8592 | 122.8226 | 59.0012 | -122.9553 | 122.8088 | 122.731 | 59.1019 | -123.0789
929.0156 | 123.0835 | -58.9691 | 63.8306 | 0.17532 | 0.0087307 | 0.069319 | 0.067313 | 0.13163 | -0.0011451 | -0.0021641 | 0.22873 | -0.007417 | 0.061914 | 0.056758 | 0.0039948 | -0.008342 | 63.8397 | 63.9587 | -0.050354 | -59.1522 | 63.8626 | -59.0469 | -59.0927 | -58.8593 | 0.036621 | -59.1843 | 63.8763 | 63.7665 | -59.1476 | -59.2163 | -0.07782 | -0.1236 | 0.032044 | 122.9279 | -0.18311 | -0.05951 | 0.009156 | -0.17853 | -0.24719 | 0.045777 | 0.10986 | -0.21515 | 0.032044 | -0.064087 | 122.8317 | 122.8088 | 58.9188 | -122.9233 | 122.8455 | 122.7356 | 59.0057 | -123.0469
930.0156 | 122.9919 | -58.9828 | 63.9084 | -0.23666 | 0.0046719 | 0.06825 | 0.07009 | 0.12907 | 0.00035035 | -0.0028049 | -0.19852 | -0.0052808 | 0.062128 | 0.060816 | 0.0022858 | -0.0077012 | 63.8123 | 63.8992 | -0.022888 | -59.166 | 63.9816 | -59.0332 | -59.0927 | -58.9737 | 0.07782 | -59.2392 | 63.945 | 63.8626 | -59.1248 | -59.1934 | -0.050354 | -0.10986 | 0.073242 | 122.8821 | -0.18311 | -0.073243 | -0.09613 | -0.14191 | -0.21057 | 0.036621 | 0.009155 | -0.25635 | -0.045777 | -0.045776 | 122.9645 | 122.7951 | 58.96 | -123.0011 | 122.9279 | 122.8455 | 59.0607 | -123.1018
931.0156 | 123.0881 | -58.9737 | 63.8306 | 0.030365 | 0.0063809 | 0.066541 | 0.068808 | 0.12907 | -0.0049903 | -0.0036595 | 0.11429 | -0.0061352 | 0.059992 | 0.057612 | 0.0037812 | -0.005565 | 63.7802 | 63.9359 | -0.041199 | -59.1568 | 63.9084 | -59.0332 | -59.0927 | -59.0103 | 0.041199 | -59.2026 | 63.8763 | 63.7756 | -59.1156 | -59.2072 | -0.059509 | -0.11902 | 0.07782 | 122.9095 | -0.1831 | -0.064087 | -0.050354 | -0.14191 | -0.23346 | 0.045777 | -0.036621 | -0.22888 | 0.004577 | -0.054931 | 122.8821 | 122.7539 | 58.9325 | -122.9233 | 122.85 | 122.7493 | 59.0149 | -123.0377
932.0156 | 123.0743 | -58.9508 | 63.8351 | 0.14481 | 0.0074491 | 0.068678 | 0.071585 | 0.12843 | -0.0011451 | -0.0038731 | 0.19821 | -0.0054944 | 0.060205 | 0.059748 | 0.0031402 | -0.0064194 | 63.8306 | 63.9542 | -0.036621 | -59.1614 | 63.8672 | -59.0378 | -59.0973 | -58.9005 | 0.022888 | -59.2072 | 63.8718 | 63.7527 | -59.1202 | -59.1843 | -0.086975 | -0.14648 | 0.032043 | 122.905 | -0.21057 | -0.064087 | -0.004578 | -0.16937 | -0.23346 | 0.036621 | 0.050354 | -0.25635 | -0.022888 | -0.082397 | 122.818 | 122.7814 | 58.9142 | -122.9324 | 122.8226 | 122.7036 | 58.9737 | -123.0194
933.0312 | 123.0377 | -58.992 | 63.8214 | 0.16769 | 0.012149 | 0.066541 | 0.070303 | 0.12993 | 0.0033411 | -0.0015231 | 0.17532 | -0.0042126 | 0.061487 | 0.061244 | 0.004422 | -0.0072738 | 63.8031 | 63.8535 | -0.086975 | -59.1293 | 63.8947 | -59.0515 | -59.1293 | -58.9279 | -0.045776 | -59.2346 | 63.9038 | 63.7756 | -59.1248 | -59.2163 | -0.05951 | -0.13733 | 0.073242 | 122.8455 | -0.13733 | 0 | -0.01831 | -0.13275 | -0.22431 | 0.082398 | 0.064087 | -0.24262 | -0.01831 | -0.045776 | 122.8867 | 122.7951 | 58.905 | -122.9507 | 122.8958 | 122.7676 | 58.9462 | -123.0377
934.0156 | 123.1201 | -58.9828 | 63.8306 | 0.17532 | 0.010867 | 0.065046 | 0.069235 | 0.13206 | 0.00056395 | -0.0021641 | 0.32028 | -0.0044264 | 0.064691 | 0.060389 | 0.0042084 | -0.0081284 | 63.8306 | 63.913 | -0.07782 | -59.1476 | 63.8947 | -59.0515 | -59.079 | -58.8776 | 0.036621 | -59.1934 | 63.8901 | 63.7756 | -59.1431 | -59.1843 | -0.068665 | -0.09613 | 0.064087 | 122.8958 | -0.16479 | -0.068665 | 0 | -0.16022 | -0.20142 | 0.05951 | 0.10529 | -0.21057 | -0.009155 | -0.054931 | 122.8775 | 122.8134 | 58.905 | -122.9095 | 122.8729 | 122.7585 | 59.0195 | -123.0148
935.0156 | 122.9782 | -58.9417 | 63.8947 | -0.24429 | 0.0050991 | 0.067823 | 0.066245 | 0.12822 | -0.0037085 | -0.0034457 | -0.15274 | -0.0052808 | 0.061701 | 0.06103 | 0.0037812 | -0.0062058 | 63.8489 | 63.9679 | 0.032043 | -59.1156 | 63.9084 | -59.0103 | -59.0881 | -58.9279 | 0.1236 | -59.1843 | 63.9359 | 63.8397 | -59.0973 | -59.1705 | -0.068665 | -0.14648 | 0.013733 | 122.9095 | -0.17395 | -0.027466 | -0.045776 | -0.15564 | -0.22888 | 0.041199 | 0.013733 | -0.24262 | -0.013733 | -0.054931 | 122.85 | 122.7905 | 58.9737 | -122.9828 | 122.8775 | 122.7814 | 59.0652 | -123.0652
936.0156 | 123.1064 | -58.9737 | 63.8168 | 0.16006 | 0.010013 | 0.06761 | 0.066031 | 0.13249 | -0.0026405 | -0.0023777 | 0.20584 | -0.0072034 | 0.063837 | 0.061671 | 0.0039948 | -0.0068466 | 63.8214 | 63.9725 | -0.013733 | -59.1385 | 63.8763 | -59.0286 | -59.079 | -58.8776 | 0.041199 | -59.1614 | 63.8443 | 63.7711 | -59.1339 | -59.2392 | -0.054931 | -0.10528 | 0.05951 | 122.9462 | -0.16479 | -0.05951 | 0.004578 | -0.16022 | -0.2655 | 0.027466 | 0.096131 | -0.18768 | 0.07782 | -0.045776 | 122.85 | 122.7951 | 58.96 | -122.8958 | 122.818 | 122.7448 | 59.0149 | -123.056
937.0156 | 123.0698 | -58.9966 | 63.8077 | 0.10666 | 0.0055265 | 0.067182 | 0.066031 | 0.12907 | -0.00050425 | -0.0032321 | 0.2211 | -0.006349 | 0.059992 | 0.059748 | 0.0033538 | -0.0059922 | 63.8351 | 63.9771 | -0.045776 | -59.1522 | 63.8809 | -59.0286 | -59.0836 | -58.8776 | 0.036621 | -59.1568 | 63.8718 | 63.7527 | -59.1202 | -59.2117 | -0.032043 | -0.086975 | 0.073242 | 122.9736 | -0.15564 | -0.068665 | 0.027466 | -0.1236 | -0.21515 | 0.064087 | 0.11902 | -0.16022 | 0.054932 | -0.054931 | 122.8775 | 122.8317 | 58.9508 | -122.8912 | 122.8683 | 122.7493 | 59.0332 | -123.0194
938.0156 | 123.0881 | -58.9508 | 63.8077 | 0.16006 | 0.010653 | 0.066755 | 0.070303 | 0.13057 | 0.0020593 | -0.0034457 | 0.25162 | -0.0048536 | 0.060633 | 0.059321 | 0.0039948 | -0.0062058 | 63.8397 | 63.9542 | -0.054932 | -59.1431 | 63.8855 | -59.0286 | -59.0744 | -58.8821 | 0.045776 | -59.2255 | 63.8718 | 63.7482 | -59.1797 | -59.2255 | -0.077819 | -0.1236 | 0.07782 | 122.905 | -0.19226 | -0.068664 | 0.032044 | -0.22888 | -0.27466 | 0.064087 | 0.068665 | -0.27466 | 0 | -0.059509 | 122.8363 | 122.7905 | 58.8959 | -122.8821 | 122.8226 | 122.699 | 58.9966 | -123.0331
939.0156 | 123.0606 | -58.9828 | 63.7939 | 0.037994 | 0.0091581 | 0.066969 | 0.068594 | 0.13163 | 0.00099115 | -0.0034457 | 0.19058 | -0.0069898 | 0.063196 | 0.059748 | 0.00549 | -0.006633 | 63.8535 | 63.945 | -0.045776 | -59.1568 | 63.8855 | -59.0149 | -59.0927 | -58.8867 | 0.022888 | -59.1614 | 63.858 | 63.7711 | -59.1339 | -59.1888 | -0.032044 | -0.10986 | 0.091553 | 122.9279 | -0.17395 | -0.064087 | 0.05951 | -0.15106 | -0.20599 | 0.064087 | 0.09613 | -0.17853 | 0.027466 | -0.022888 | 122.8683 | 122.8363 | 58.9371 | -122.8867 | 122.8409 | 122.7539 | 59.0057 | -122.9828
940.0156 | 123.0057 | -58.9645 | 63.8901 | -0.27481 | 0.0091581 | 0.067823 | 0.071158 | 0.12693 | 0.00013675 | -0.0034457 | 0.19821 | -0.0044264 | 0.062128 | 0.058894 | 0.001004 | -0.0051376 | 63.7115 | 64.1693 | 0.11902 | -59.198 | 63.9999 | -59.0057 | -59.111 | -58.9508 | 0.068665 | -59.2438 | 63.9587 | 63.8809 | -59.1019 | -59.1888 | -0.041198 | -0.14648 | 0.10986 | 123.1339 | -0.23346 | -0.086975 | -0.17853 | -0.13733 | -0.2243 | 0.068664 | 0.013733 | -0.27923 | -0.054931 | -0.009156 | 122.9645 | 122.6761 | 59.0836 | -123.0011 | 122.9233 | 122.8455 | 59.0332 | -123.0789
941.0156 | 123.0743 | -58.9691 | 63.826 | 0.12955 | 0.0061673 | 0.067396 | 0.064963 | 0.12822 | -0.0030677 | -0.0028049 | 0.27451 | -0.0065626 | 0.060205 | 0.058467 | 0.002713 | -0.005565 | 63.8214 | 63.9771 | -0.036621 | -59.1339 | 63.8672 | -59.024 | -59.0836 | -58.8913 | 0.018311 | -59.1888 | 63.8718 | 63.7802 | -59.1339 | -59.1934 | -0.054932 | -0.11444 | 0.041198 | 122.9462 | -0.16479 | -0.050354 | -0.004578 | -0.16479 | -0.2243 | 0.045776 | 0.07782 | -0.21973 | 0.004577 | -0.045777 | 122.8363 | 122.7905 | 58.9325 | -122.9095 | 122.8409 | 122.7493 | 58.9874 | -123.0194
942.0156 | 123.0972 | -58.9417 | 63.8168 | 0.18295 | 0.0087307 | 0.067182 | 0.069235 | 0.13057 | -0.0017859 | -0.0062229 | 0.32028 | -0.0067762 | 0.062982 | 0.060389 | 0.0039948 | -0.0062058 | 64.0228 | 63.9221 | -0.045776 | -59.0698 | 63.8992 | -58.9966 | -59.0698 | -58.8821 | 0.050354 | -59.1522 | 63.8672 | 63.7802 | -59.111 | -59.2117 | -0.054932 | -0.12817 | 0.082398 | 122.8638 | -0.12817 | 0 | 0.20599 | -0.16937 | -0.27008 | 0.050354 | 0.059509 | -0.21057 | 0.059509 | -0.036621 | 122.8409 | 122.9645 | 58.8959 | -122.8867 | 122.8088 | 122.7219 | 58.992 | -123.0286
943.0156 | 123.0743 | -58.9737 | 63.8535 | -0.023041 | 0.0048855 | 0.070387 | 0.069235 | 0.12843 | -0.0034949 | -0.0040867 | 0.10666 | -0.0069898 | 0.064905 | 0.05868 | 0.0014312 | -0.0051376 | 63.8031 | 63.9221 | -0.041199 | -59.1522 | 63.913 | -58.992 | -59.0744 | -58.9005 | 0.059509 | -59.1476 | 63.913 | 63.8123 | -59.0927 | -59.1751 | -0.01831 | -0.10071 | 0.059509 | 122.8958 | -0.17853 | -0.07782 | -0.050354 | -0.11902 | -0.20142 | 0.059509 | 0.073242 | -0.17395 | 0.027466 | -0.041199 | 122.8867 | 122.7768 | 58.9325 | -122.9279 | 122.8867 | 122.7859 | 59.0332 | -123.0286
944.0156 | 123.0789 | -58.9462 | 63.826 | 0.0914 | 0.0065945 | 0.068037 | 0.06774 | 0.12843 | -0.00050425 | -0.0036595 | 0.24399 | -0.007417 | 0.062555 | 0.059321 | 0.0057038 | -0.005565 | 63.8443 | 63.9404 | -0.032043 | -59.1522 | 63.8809 | -58.9966 | -59.0378 | -58.8684 | 0.036621 | -59.1705 | 63.8763 | 63.7802 | -59.1156 | -59.2346 | -0.050354 | -0.091553 | 0.054931 | 122.8867 | -0.20599 | -0.11444 | 0.01831 | -0.16937 | -0.28839 | 0.050354 | 0.07782 | -0.2243 | 0.064087 | -0.045777 | 122.8271 | 122.7905 | 58.9142 | -122.8638 | 122.8226 | 122.7264 | 58.9828 | -123.0606
945.0156 | 123.024 | -58.9554 | 63.8947 | -0.25192 | 0.0087307 | 0.067396 | 0.072226 | 0.13163 | -0.0011451 | -0.0064365 | -0.17563 | -0.0065626 | 0.062555 | 0.059962 | 0.0035674 | -0.0070602 | 63.8351 | 63.9313 | -0.027466 | -59.1476 | 63.9679 | -59.0195 | -59.1019 | -58.9279 | 0.073242 | -59.2255 | 63.9816 | 63.858 | -59.1064 | -59.1751 | -0.064087 | -0.14649 | 0.073243 | 122.8867 | -0.19226 | -0.045776 | -0.059509 | -0.15106 | -0.21973 | 0.086975 | 0.027466 | -0.27008 | -0.050354 | -0.036621 | 122.9233 | 122.7905 | 58.9279 | -122.9965 | 122.937 | 122.8134 | 59.0286 | -123.0698
946.0156 | 123.111 | -58.96 | 63.8626 | 0.12955 | 0.0095853 | 0.067823 | 0.068808 | 0.13163 | 0.0024865 | -0.00045506 | 0.21347 | -0.0065626 | 0.063837 | 0.058039 | 0.0050628 | -0.0051376 | 63.8535 | 63.9542 | -0.050354 | -59.1293 | 63.9038 | -59.0332 | -59.0698 | -58.8593 | 0.022888 | -59.1522 | 63.9038 | 63.7756 | -59.1476 | -59.1751 | -0.073242 | -0.10986 | 0.041199 | 122.9141 | -0.16937 | -0.059509 | -0.009155 | -0.18768 | -0.21515 | 0.041199 | 0.10071 | -0.19226 | 0.022888 | -0.086975 | 122.8638 | 122.8134 | 58.9096 | -122.9324 | 122.8638 | 122.7356 | 58.9828 | -123.0377
947.0156 | 123.1064 | -58.9371 | 63.8351 | 0.12192 | 0.0095853 | 0.067182 | 0.067526 | 0.12907 | 0.0020593 | -0.00045506 | 0.2211 | -0.0076306 | 0.061914 | 0.060816 | 0.0048492 | -0.008342 | 63.6887 | 64.1693 | 0.07782 | -59.1293 | 63.8809 | -59.0103 | -59.0607 | -58.8638 | 0.041199 | -59.1568 | 63.8809 | 63.7756 | -59.1019 | -59.2026 | -0.073242 | -0.1236 | 0.045776 | 123.1064 | -0.19226 | -0.068664 | -0.14648 | -0.1648 | -0.2655 | 0.045776 | 0.073242 | -0.21973 | 0.045777 | -0.059509 | 122.818 | 122.6257 | 59.0149 | -122.8958 | 122.818 | 122.7127 | 58.9783 | -123.0377
948.0156 | 123.111 | -58.9554 | 63.8489 | 0.053253 | 0.0048855 | 0.06825 | 0.068594 | 0.128 | -0.0071265 | -0.0049411 | 0.12955 | -0.0086988 | 0.061487 | 0.055689 | 0.002713 | -0.0057786 | 63.9496 | 63.8351 | -0.07782 | -59.1385 | 63.9587 | -59.0057 | -59.0561 | -58.9233 | 0.036621 | -59.166 | 63.9038 | 63.8214 | -59.0836 | -59.1843 | -0.050354 | -0.10071 | 0.10986 | 122.7905 | -0.18311 | -0.082398 | 0.10071 | -0.12817 | -0.22888 | 0.054932 | 0.032043 | -0.21057 | 0.01831 | -0.027466 | 122.9141 | 122.905 | 58.8776 | -122.905 | 122.8592 | 122.7768 | 58.992 | -123.0331
949.0156 | 123.1338 | -58.9371 | 63.8397 | 0.20584 | 0.011722 | 0.067823 | 0.070944 | 0.12907 | 0.00099115 | -0.0028049 | 0.23636 | -0.005708 | 0.06341 | 0.059962 | 0.0052764 | -0.0074876 | 63.8718 | 63.9633 | -0.036621 | -59.1293 | 63.8947 | -59.0469 | -59.0698 | -58.8455 | -0.28381 | -59.079 | 63.8535 | 63.7711 | -59.1202 | -59.1888 | -0.10986 | -0.13275 | 0.054931 | 122.9004 | -0.19226 | -0.059509 | 0.032043 | -0.18311 | -0.25177 | 0.013733 | 0.091553 | -0.14191 | 0.10986 | -0.068665 | 122.8317 | 122.8088 | 58.9005 | -122.9095 | 122.7905 | 122.7081 | 58.6533 | -123.0286
950.0156 | 123.111 | -58.9691 | 63.7756 | 0.16006 | 0.010226 | 0.066969 | 0.069235 | 0.13185 | 0.0022729 | -0.00066866 | 0.28976 | -0.0048536 | 0.061701 | 0.058467 | 0.002713 | -0.0072738 | 63.8718 | 63.945 | -0.054932 | -59.1248 | 63.8855 | -59.024 | -59.0744 | -58.873 | 0.041199 | -59.1568 | 63.858 | 63.7802 | -59.1248 | -59.198 | -0.054932 | -0.10529 | 0.10986 | 122.9141 | -0.15564 | -0.050354 | 0.09613 | -0.15564 | -0.22888 | 0.082397 | 0.09613 | -0.18768 | 0.041199 | 0.004577 | 122.8546 | 122.8409 | 58.9142 | -122.85 | 122.8271 | 122.7493 | 59.0103 | -122.9736
951.0156 | 123.1384 | -58.9554 | 63.8168 | 0.19058 | 0.0095853 | 0.064832 | 0.066458 | 0.13142 | 0.0037683 | -0.0017369 | 0.28214 | -0.0067762 | 0.062769 | 0.059321 | 0.0050628 | -0.0068466 | 63.8306 | 63.9679 | -0.054932 | -59.166 | 63.8992 | -59.0012 | -59.0744 | -58.8638 | 0.027466 | -59.1705 | 63.8809 | 63.7711 | -59.1019 | -59.1751 | -0.045777 | -0.11902 | 0.082398 | 122.9233 | -0.21057 | -0.091553 | 0.013733 | -0.14649 | -0.21973 | 0.064087 | 0.091552 | -0.21515 | 0.004578 | -0.045776 | 122.8546 | 122.7859 | 58.9005 | -122.8912 | 122.8363 | 122.7264 | 58.9828 | -122.9919
952.0156 | 123.0789 | -58.9417 | 63.858 | 0.16769 | 0.0095853 | 0.066541 | 0.068167 | 0.12993 | 0.00077755 | -0.0021641 | 0.76279 | -0.006349 | 0.06106 | 0.06103 | 0.0037812 | -0.0059922 | 63.8443 | 63.9725 | 0.004578 | -59.2117 | 63.8718 | -59.0195 | -59.1156 | -58.8455 | 0.045776 | -59.1614 | 63.8901 | 63.7939 | -59.1019 | -59.1888 | -0.07782 | -0.17395 | 0.013733 | 122.9141 | -0.27008 | -0.09613 | -0.013733 | -0.16022 | -0.24719 | 0.032044 | 0.09613 | -0.21973 | 0.027466 | -0.064087 | 122.8134 | 122.7859 | 58.9462 | -122.9736 | 122.8317 | 122.7356 | 58.9874 | -123.0469
953.0156 | 123.1155 | -58.9462 | 63.8443 | -0.023041 | 0.0021085 | 0.068891 | 0.069449 | 0.12928 | -0.0045631 | -0.0015231 | 0.037995 | -0.007417 | 0.059992 | 0.061244 | 0.00079042 | -0.0062058 | 63.826 | 63.9542 | -0.004578 | -59.1156 | 63.9496 | -59.0057 | -59.0515 | -58.8638 | 0.086975 | -59.1156 | 63.9359 | 63.8351 | -59.079 | -59.1705 | -0.059509 | -0.10529 | 0.10529 | 122.9004 | -0.16937 | -0.064087 | -0.01831 | -0.13275 | -0.2243 | 0.091553 | 0.082397 | -0.16937 | 0.054931 | -0.009155 | 122.8958 | 122.7722 | 58.9416 | -122.8958 | 122.8821 | 122.7814 | 59.0332 | -123.0148
954.0156 | 123.1613 | -58.9874 | 63.826 | 0.21347 | 0.0091581 | 0.066541 | 0.07009 | 0.13249 | 0.0018457 | -0.0036595 | 0.2211 | -0.0067762 | 0.060846 | 0.059321 | 0.004422 | -0.0070602 | 63.8626 | 63.9679 | -0.073242 | -59.1019 | 63.8718 | -59.0057 | -59.0836 | -58.8226 | 0.032043 | -59.1614 | 63.8809 | 63.7848 | -59.1202 | -59.1888 | -0.01831 | -0.09613 | 0.045776 | 122.9553 | -0.11444 | -0.018311 | 0.036621 | -0.13275 | -0.20142 | 0.054931 | 0.16479 | -0.17395 | 0.027466 | -0.041199 | 122.8592 | 122.85 | 58.9142 | -122.9095 | 122.8683 | 122.7722 | 59.0195 | -123.0148
955.0156 | 123.1064 | -58.9508 | 63.8351 | 0.20584 | 0.0080899 | 0.068678 | 0.067099 | 0.13163 | 0.0012047 | -0.0036595 | 0.22873 | -0.0065626 | 0.063196 | 0.056971 | 0.0033538 | -0.0081284 | 63.8489 | 63.9542 | -0.064087 | -59.0881 | 63.9084 | -59.0195 | -59.0836 | -58.8593 | 0.018311 | -59.1522 | 63.8947 | 63.7848 | -59.1019 | -59.1888 | -0.068664 | -0.13275 | 0.073242 | 122.905 | -0.13733 | -0.004578 | 0.013733 | -0.15106 | -0.23804 | 0.059509 | 0.091553 | -0.20142 | 0.036621 | -0.050354 | 122.8592 | 122.7997 | 58.8867 | -122.9187 | 122.8455 | 122.7356 | 58.9691 | -123.024
956.0156 | 123.0515 | -58.9508 | 63.8718 | 0.10666 | 0.0087307 | 0.067823 | 0.068808 | 0.12928 | -0.00050425 | -0.0025913 | 0.26688 | -0.0072034 | 0.059137 | 0.057185 | 0.0048492 | -0.0064194 | 63.8443 | 63.9862 | -0.036621 | -59.1156 | 63.8901 | -58.9828 | -59.0836 | -58.8638 | 0.032043 | -59.1705 | 63.8809 | 63.7756 | -59.1064 | -59.1751 | -0.032043 | -0.13275 | 0.018311 | 122.937 | -0.16479 | -0.032044 | -0.027466 | -0.15564 | -0.2243 | 0.009155 | 0.086975 | -0.21973 | 0.004578 | -0.09613 | 122.8409 | 122.7951 | 58.9142 | -122.9553 | 122.8317 | 122.7264 | 58.9828 | -123.0469
957.0156 | 123.1247 | -58.9417 | 63.8672 | 0.16006 | 0.0083035 | 0.067182 | 0.069663 | 0.13121 | 0.00056395 | -0.0030185 | -1.404 | -0.0076306 | 0.06341 | 0.059535 | 0.0039948 | -0.0091966 | 63.8718 | 63.9816 | -0.032043 | -59.111 | 63.8809 | -58.9874 | -59.0652 | -58.8135 | 0.036621 | -59.1293 | 63.8901 | 63.8031 | -59.0836 | -59.1751 | -0.045777 | -0.1236 | 0.013733 | 122.9233 | -0.16937 | -0.045776 | 0.004578 | -0.14191 | -0.23346 | 0.022889 | 0.12817 | -0.18768 | 0.045777 | -0.064086 | 122.8226 | 122.8134 | 58.9096 | -122.9324 | 122.8317 | 122.7448 | 58.9783 | -123.0423
958.0156 | 123.0698 | -58.9508 | 63.8397 | 0.18295 | 0.0063809 | 0.067823 | 0.070731 | 0.13057 | -0.0024269 | -0.0032321 | 0.19821 | -0.0076306 | 0.065332 | 0.05868 | 0.0014312 | -0.0064194 | 63.8489 | 63.9816 | -0.045776 | -59.111 | 63.8718 | -59.0057 | -59.079 | -58.8409 | 0.027466 | -59.1476 | 63.8809 | 63.8077 | -59.0836 | -59.1843 | -0.054931 | -0.12817 | 0.032043 | 122.9324 | -0.16022 | -0.032044 | 0.009155 | -0.13275 | -0.23346 | 0.041198 | 0.10986 | -0.19684 | 0.036621 | -0.032044 | 122.8226 | 122.7997 | 58.905 | -122.9187 | 122.8317 | 122.7585 | 58.9783 | -123.024
959.0156 | 123.1659 | -58.96 | 63.8489 | 0.31265 | 0.011294 | 0.067182 | 0.070517 | 0.13014 | 0.00099115 | -0.0021641 | 0.20584 | -0.007417 | 0.062128 | 0.059321 | 0.00549 | -0.006633 | 63.8763 | 63.9771 | -0.050354 | -59.0973 | 63.9267 | -58.9783 | -59.079 | -58.8455 | 0.036621 | -59.1385 | 63.8809 | 63.7848 | -59.0927 | -59.1934 | -0.01831 | -0.11902 | 0.07782 | 122.937 | -0.13733 | -0.018311 | 0.027466 | -0.13275 | -0.23346 | 0.032043 | 0.11444 | -0.17853 | 0.054931 | -0.064087 | 122.8867 | 122.8363 | 58.9096 | -122.9279 | 122.8409 | 122.7448 | 58.9966 | -123.0423
960.0156 | 123.1018 | -58.9508 | 63.8489 | 0.20584 | 0.0083035 | 0.066328 | 0.069022 | 0.1342 | -0.00050425 | -0.0036595 | 0.19821 | -0.005708 | 0.062982 | 0.058467 | 0.0052764 | -0.0072738 | 63.8672 | 63.9267 | -0.073242 | -59.111 | 63.9175 | -59.0103 | -59.0652 | -58.8684 | 0.022888 | -59.1431 | 63.8855 | 63.8077 | -59.1339 | -59.1385 | -0.059509 | -0.11444 | 0.068665 | 122.8775 | -0.16022 | -0.045776 | 0.01831 | -0.1831 | -0.18768 | 0.036621 | 0.082398 | -0.19226 | -0.004577 | -0.041199 | 122.8683 | 122.818 | 58.8776 | -122.9141 | 122.8363 | 122.7585 | 58.9737 | -122.9874
961.0156 | 123.111 | -58.9417 | 63.8397 | 0.16769 | 0.010226 | 0.068678 | 0.066672 | 0.13185 | 0.00077755 | -0.0017369 | 0.022736 | -0.0095532 | 0.06341 | 0.060603 | 0.0029266 | -0.0057786 | 63.8763 | 64.119 | 0.022888 | -59.1248 | 63.8855 | -58.9966 | -59.0515 | -58.8409 | 0.054932 | -59.1293 | 63.8947 | 63.8077 | -59.0744 | -59.1614 | -0.054932 | -0.10986 | 0.045776 | 123.0606 | -0.18311 | -0.073242 | 0.036621 | -0.13275 | -0.21973 | 0.054931 | 0.10071 | -0.18768 | 0.032044 | -0.032044 | 122.8271 | 122.818 | 58.9645 | -122.8912 | 122.8363 | 122.7493 | 58.9966 | -123.0011
962.0156 | 123.1064 | -58.9233 | 63.8443 | 0.14481 | 0.012149 | 0.066541 | 0.071585 | 0.12864 | 0.0022729 | -0.0032321 | 0.17532 | -0.006349 | 0.062769 | 0.059748 | 0.0024994 | -0.006633 | 63.8214 | 63.9221 | -0.11444 | -59.1522 | 63.9496 | -58.9966 | -59.0652 | -58.8364 | -0.027466 | -59.198 | 63.9175 | 63.8214 | -59.0973 | -59.1614 | -0.073242 | -0.14191 | 0.10529 | 122.8455 | -0.22888 | -0.086975 | -0.022888 | -0.17395 | -0.23804 | 0.073243 | 0.086975 | -0.27466 | -0.036621 | -0.022888 | 122.8729 | 122.7448 | 58.8089 | -122.9095 | 122.8409 | 122.7448 | 58.8959 | -123.0057
963.0156 | 123.1247 | -58.9325 | 63.8626 | -0.0383 | 0.0070217 | 0.066755 | 0.069235 | 0.12715 | -0.0049903 | -0.0053683 | 0.053253 | -0.005708 | 0.061273 | 0.058894 | 0.00057682 | -0.0064194 | 63.8443 | 63.9771 | -0.018311 | -59.1019 | 63.9496 | -58.9783 | -59.0469 | -58.8409 | 0.09613 | -59.1019 | 63.9038 | 63.826 | -59.0424 | -59.1614 | -0.045776 | -0.11444 | 0.086975 | 122.9095 | -0.16937 | -0.054932 | -0.018311 | -0.10986 | -0.22888 | 0.041199 | 0.091553 | -0.16937 | 0.059509 | -0.036621 | 122.8821 | 122.7768 | 58.9142 | -122.9095 | 122.8363 | 122.7585 | 59.0286 | -123.024
964.0156 | 123.0881 | -58.9371 | 63.8626 | 0.068512 | 0.011081 | 0.067182 | 0.069876 | 0.13313 | -0.00029045 | -0.0034457 | 0.20584 | -0.0065626 | 0.064478 | 0.058039 | 0.0048492 | -0.0077012 | 63.8718 | 64.0182 | -0.041199 | -59.111 | 63.9175 | -58.992 | -59.0607 | -58.8272 | 0.059509 | -59.1293 | 63.913 | 63.8123 | -59.1019 | -59.1568 | -0.054931 | -0.1236 | 0.054932 | 122.9553 | -0.17395 | -0.050354 | 0.009155 | -0.1648 | -0.21973 | 0.050354 | 0.10986 | -0.19226 | 0.027466 | -0.050354 | 122.8546 | 122.8088 | 58.8959 | -122.9233 | 122.85 | 122.7493 | 58.9966 | -123.0194
965.0156 | 123.0286 | -58.96 | 63.8718 | 0.16769 | 0.010653 | 0.067182 | 0.068808 | 0.12736 | 0.0012047 | -0.0019505 | 0.2211 | -0.002931 | 0.063196 | 0.059535 | 0.00549 | -0.0064194 | 63.8306 | 63.8947 | -0.14648 | -59.1797 | 63.9633 | -59.0012 | -59.079 | -58.8867 | -0.032043 | -59.2026 | 63.9542 | 63.8351 | -59.1019 | -59.1751 | -0.041199 | -0.11902 | 0.091553 | 122.8546 | -0.21973 | -0.10071 | -0.041199 | -0.14191 | -0.21515 | 0.082398 | 0.073242 | -0.24262 | -0.027466 | -0.036621 | 122.9233 | 122.7905 | 58.8135 | -122.9507 | 122.9141 | 122.7951 | 58.9279 | -123.0469
966.0156 | 123.056 | -58.9691 | 63.8626 | 0.14481 | 0.011081 | 0.06761 | 0.073508 | 0.13206 | 0.0018457 | -0.0017369 | 0.20584 | -0.0048536 | 0.063837 | 0.06103 | 0.0048492 | -0.0089828 | 63.7985 | 63.8855 | -0.15564 | -59.1843 | 63.9587 | -59.0149 | -59.0698 | -58.8913 | -0.041199 | -59.198 | 63.9404 | 63.8672 | -59.0973 | -59.1888 | -0.045777 | -0.10071 | 0.09613 | 122.8546 | -0.21515 | -0.11444 | -0.064087 | -0.12817 | -0.21973 | 0.07782 | 0.07782 | -0.22888 | -0.009155 | 0.004577 | 122.9279 | 122.7676 | 58.8135 | -122.9324 | 122.9095 | 122.8363 | 58.9279 | -123.0515
967.0156 | 123.0881 | -58.9554 | 63.8489 | 0.099029 | 0.0080899 | 0.069532 | 0.071158 | 0.12843 | -0.0026405 | -0.0010959 | 0.27451 | -0.007417 | 0.062982 | 0.060176 | 0.0024994 | -0.0051376 | 63.8535 | 63.9999 | -0.050354 | -59.1156 | 63.913 | -58.9874 | -59.0515 | -58.8455 | 0.027466 | -59.1339 | 63.8901 | 63.8168 | -59.0881 | -59.1614 | -0.032044 | -0.096131 | 0.064087 | 122.9553 | -0.16022 | -0.064087 | 0.004578 | -0.13275 | -0.20599 | 0.041199 | 0.10986 | -0.17853 | 0.027466 | -0.032044 | 122.8683 | 122.8088 | 58.905 | -122.9004 | 122.8455 | 122.7722 | 58.9828 | -123.0103
968.0156 | 123.0698 | -58.9462 | 63.8855 | -1.5718 | 0.0080899 | 0.066969 | 0.069235 | 0.128 | -0.0043495 | -0.0034457 | 0.12192 | -0.0072034 | 0.061914 | 0.060816 | 0.00079042 | -0.0070602 | 63.7894 | 63.9816 | -0.036621 | -59.1202 | 63.9587 | -58.9874 | -59.0515 | -58.8913 | 0.064087 | -59.1248 | 63.9313 | 63.8351 | -59.0836 | -59.1568 | -0.041199 | -0.10529 | 0.073242 | 122.9279 | -0.17395 | -0.068664 | -0.09613 | -0.13733 | -0.21057 | 0.045776 | 0.054932 | -0.17853 | 0.032043 | -0.050354 | 122.905 | 122.7356 | 58.9096 | -122.937 | 122.8775 | 122.7814 | 59.0103 | -123.0423
969.0156 | 123.111 | -58.9325 | 63.8489 | 0.20584 | 0.01044 | 0.065473 | 0.067954 | 0.13014 | 0.0054773 | -0.0030185 | 0.19058 | -0.0059216 | 0.064051 | 0.059748 | 0.0048492 | -0.0059922 | 63.858 | 63.9221 | -0.11444 | -59.1476 | 63.9359 | -58.9966 | -59.0607 | -58.8638 | 0.027466 | -59.1888 | 63.8992 | 63.8214 | -59.079 | -59.1522 | -0.064087 | -0.12817 | 0.086975 | 122.8546 | -0.21515 | -0.086975 | 0.009155 | -0.14648 | -0.21973 | 0.050354 | 0.068664 | -0.25635 | -0.036621 | -0.027466 | 122.8683 | 122.7905 | 58.8181 | -122.9095 | 122.8317 | 122.7539 | 58.96 | -123.0011
970.0156 | 123.0835 | -58.9462 | 63.8855 | 0.19058 | 0.010653 | 0.065901 | 0.070517 | 0.13121 | -0.00029045 | -0.0030185 | 0.18295 | -0.005708 | 0.064478 | 0.059321 | 0.0052764 | -0.0070602 | 63.8443 | 63.9267 | -0.10529 | -59.1522 | 63.945 | -59.0103 | -59.0515 | -58.8501 | 0 | -59.1522 | 63.945 | 63.8351 | -59.0698 | -59.1614 | -0.064087 | -0.10529 | 0.059509 | 122.8729 | -0.20599 | -0.10071 | -0.041199 | -0.1236 | -0.21515 | 0.059509 | 0.09613 | -0.20599 | 0.009155 | -0.050354 | 122.8912 | 122.7905 | 58.8409 | -122.937 | 122.8912 | 122.7814 | 58.9462 | -123.0469
971.0156 | 123.0652 | -58.9188 | 63.8901 | 0.12192 | 0.0074491 | 0.066541 | 0.069022 | 0.12864 | -0.0039221 | -0.0028049 | 0.25925 | -0.0084852 | 0.062555 | 0.060176 | 0.0033538 | -0.0044968 | 63.8397 | 63.9908 | -0.050354 | -59.1339 | 63.9267 | -58.9508 | -59.0286 | -58.8684 | -0.004578 | -59.1339 | 63.9175 | 63.8214 | -59.0836 | -59.1568 | -0.032044 | -0.10986 | 0.036621 | 122.9095 | -0.21515 | -0.10529 | -0.050354 | -0.16479 | -0.23804 | 0.027466 | 0.050354 | -0.21515 | 0.022888 | -0.068665 | 122.8455 | 122.7585 | 58.8684 | -122.9187 | 122.8363 | 122.7402 | 58.9142 | -123.0469
972.0156 | 123.0377 | -58.9371 | 63.8901 | 0.19058 | 0.013644 | 0.067396 | 0.069235 | 0.13057 | 0.0022729 | -0.0023777 | 0.20584 | -0.0050672 | 0.064051 | 0.059107 | 0.004422 | -0.0059922 | 63.8306 | 63.8992 | -0.11902 | -59.1568 | 63.9999 | -59.0012 | -59.0744 | -58.8684 | -0.036621 | -59.1751 | 63.9496 | 63.8626 | -59.1019 | -59.1385 | -0.064087 | -0.13733 | 0.10986 | 122.8363 | -0.21973 | -0.082397 | -0.05951 | -0.1648 | -0.20142 | 0.059509 | 0.068665 | -0.23804 | -0.036621 | -0.027466 | 122.937 | 122.7676 | 58.8181 | -122.9645 | 122.8867 | 122.7997 | 58.9005 | -123.0286
973.0156 | 123.0515 | -58.8959 | 63.8947 | -0.0077822 | 0.0059537 | 0.067396 | 0.068381 | 0.13078 | -0.0052039 | -0.0015231 | 0.21347 | -0.006349 | 0.060633 | 0.058467 | 0.0020722 | -0.004924 | 63.8123 | 63.9862 | -0.050354 | -59.1064 | 63.9679 | -58.9371 | -59.024 | -58.8684 | 0.032043 | -58.9874 | 63.9496 | 63.913 | -59.0286 | -59.1156 | -0.041199 | -0.12817 | 0.073243 | 122.8821 | -0.21057 | -0.082397 | -0.082397 | -0.13275 | -0.21973 | 0.054932 | 0.027466 | -0.091553 | 0.12817 | 0.018311 | 122.8638 | 122.7081 | 58.8455 | -122.9187 | 122.8455 | 122.8088 | 58.9279 | -123.0103
974.0156 | 123.0286 | -58.9554 | 63.9038 | 0.17532 | 0.012362 | 0.069959 | 0.07009 | 0.13142 | 0.0018457 | -0.0030185 | 0.20584 | -0.0052808 | 0.063196 | 0.057612 | 0.0042084 | -0.008342 | 63.8306 | 63.8947 | -0.15564 | -59.1614 | 63.9816 | -59.0012 | -59.0561 | -58.873 | -0.054932 | -59.1843 | 63.9587 | 63.8397 | -59.1064 | -59.166 | -0.045777 | -0.10071 | 0.077819 | 122.85 | -0.20599 | -0.10529 | -0.073243 | -0.15106 | -0.21057 | 0.054931 | 0.082397 | -0.22888 | -0.01831 | -0.064087 | 122.937 | 122.7859 | 58.7997 | -122.9599 | 122.9141 | 122.7951 | 58.9005 | -123.0698
975.0156 | 123.0698 | -58.9371 | 63.8901 | 0.0914 | 0.0053129 | 0.06825 | 0.067099 | 0.12758 | -0.0032813 | -0.0047275 | 0.24399 | -0.0054944 | 0.062769 | 0.060389 | 0.0031402 | -0.006633 | 63.826 | 63.9862 | -0.064087 | -59.1202 | 63.9542 | -58.9554 | -59.0469 | -58.8867 | 0.027466 | -59.1293 | 63.9359 | 63.8718 | -59.0515 | -59.1248 | -0.01831 | -0.10986 | 0.064087 | 122.9233 | -0.18311 | -0.073242 | -0.064087 | -0.11444 | -0.18768 | 0.045776 | 0.050354 | -0.19226 | -0.004577 | -0.018311 | 122.8912 | 122.7631 | 58.873 | -122.937 | 122.8729 | 122.8088 | 58.9645 | -123.0148
976.0156 | 123.0881 | -58.905 | 63.8947 | 0.11429 | 0.0074491 | 0.06761 | 0.068808 | 0.12822 | -0.0047767 | -0.0045139 | 0.13718 | -0.0076306 | 0.062769 | 0.058467 | 0.002713 | -0.0070602 | 63.8535 | 63.9816 | -0.073242 | -59.111 | 63.9542 | -58.9554 | -59.0286 | -58.8821 | 0.004578 | -59.1202 | 63.9725 | 63.8535 | -59.0515 | -59.1156 | -0.050354 | -0.1236 | 0.05951 | 122.8867 | -0.20599 | -0.082398 | -0.041198 | -0.14648 | -0.21057 | 0.07782 | 0.022888 | -0.21515 | -0.004577 | -0.041198 | 122.8592 | 122.7585 | 58.8318 | -122.9233 | 122.8775 | 122.7585 | 58.9096 | -123.0103
977.0156 | 123.0927 | -58.9005 | 63.8763 | 0.10666 | 0.0087307 | 0.067396 | 0.068381 | 0.13057 | 0.00056395 | -0.0040867 | 0.19058 | -0.0084852 | 0.061487 | 0.059748 | 0.0037812 | -0.0059922 | 63.8901 | 64.0228 | -0.054932 | -59.1019 | 63.9313 | -58.9691 | -59.0195 | -58.8135 | 0.036621 | -59.1064 | 63.9496 | 63.8306 | -59.0607 | -59.1568 | -0.068664 | -0.11902 | 0.054931 | 122.9233 | -0.20142 | -0.082398 | 0.013733 | -0.16022 | -0.25635 | 0.073242 | 0.086975 | -0.20599 | 0.050354 | -0.045777 | 122.8317 | 122.7905 | 58.8455 | -122.8958 | 122.85 | 122.731 | 58.9371 | -123.0331
978.0156 | 123.0743 | -58.9005 | 63.9038 | 0.28213 | 0.010653 | 0.06526 | 0.069876 | 0.1295 | -0.0022131 | -0.0025913 | 0.19058 | -0.0078442 | 0.061914 | 0.058894 | 0.0046356 | -0.0081284 | 63.9084 | 64.0228 | -0.032043 | -59.0836 | 63.9175 | -58.96 | -59.0103 | -58.8181 | 0.050354 | -59.1248 | 63.9267 | 63.8397 | -59.0469 | -59.1476 | -0.059509 | -0.10986 | 0.013733 | 122.9233 | -0.1831 | -0.073242 | 0.004577 | -0.14648 | -0.24719 | 0.022888 | 0.082398 | -0.2243 | 0.022888 | -0.064087 | 122.818 | 122.8088 | 58.8684 | -122.9141 | 122.8271 | 122.7402 | 58.9508 | -123.0515
979.0156 | 123.0469 | -58.8913 | 63.9267 | 0.083771 | 0.0050991 | 0.067182 | 0.066245 | 0.12758 | -0.0034949 | -0.0038731 | 0.11429 | -0.0059216 | 0.06106 | 0.057612 | 0.0035674 | -0.0057786 | 63.858 | 63.9771 | -0.073242 | -59.1202 | 63.9587 | -58.9462 | -59.024 | -58.7952 | 0.16937 | -59.166 | 63.9679 | 63.9084 | -59.0286 | -59.1248 | -0.054932 | -0.13275 | 0.032043 | 122.8683 | -0.22888 | -0.09613 | -0.068665 | -0.13733 | -0.23346 | 0.041199 | 0.09613 | -0.27466 | -0.041199 | -0.018311 | 122.85 | 122.7493 | 58.8181 | -122.9507 | 122.8592 | 122.7997 | 59.0607 | -123.0515
980.0156 | 123.1018 | -58.905 | 63.8901 | -1.0301 | 0.0083035 | 0.068037 | 0.069235 | 0.13121 | 0.00099115 | -0.0053683 | 0.21347 | -0.0052808 | 0.061273 | 0.058467 | 0.0046356 | -0.0059922 | 63.913 | 64.064 | -0.004578 | -59.0652 | 63.9359 | -58.9508 | -59.0195 | -58.7997 | 0.041199 | -59.1064 | 63.9633 | 63.8306 | -59.0607 | -59.1339 | -0.045777 | -0.11444 | 0.045776 | 122.9691 | -0.16022 | -0.045777 | 0.022888 | -0.15564 | -0.22888 | 0.073242 | 0.10529 | -0.20142 | 0.027466 | -0.05951 | 122.8409 | 122.818 | 58.9005 | -122.9095 | 122.8683 | 122.7356 | 58.9462 | -123.024
981.0156 | 123.1293 | -58.8776 | 63.8809 | 0.19058 | 0.011294 | 0.065473 | 0.066672 | 0.13099 | -0.0019995 | -0.0025913 | 0.34317 | -0.0050672 | 0.062555 | 0.058467 | 0.004422 | -0.008342 | 63.8718 | 64.0869 | -0.022888 | -59.0469 | 63.9542 | -58.9554 | -58.992 | -58.8043 | 0.050354 | -59.0973 | 63.945 | 63.8397 | -59.0469 | -59.1476 | -0.07782 | -0.11444 | 0.073243 | 122.9645 | -0.16937 | -0.054932 | -0.009155 | -0.16937 | -0.27008 | 0.064087 | 0.073242 | -0.21973 | 0.050354 | -0.041198 | 122.8317 | 122.7493 | 58.8547 | -122.8729 | 122.8226 | 122.7173 | 58.9279 | -123.0286
982.0156 | 123.0743 | -58.8913 | 63.8809 | 0.20584 | 0.011935 | 0.069532 | 0.070517 | 0.13206 | 0.0016321 | -0.0025913 | 0.19821 | -0.006349 | 0.060846 | 0.060176 | 0.0042084 | -0.0085556 | 63.8901 | 63.9679 | -0.10071 | -59.079 | 63.9771 | -58.9508 | -59.0286 | -58.7997 | 0.027466 | -59.1156 | 63.9496 | 63.8489 | -59.079 | -59.1202 | -0.05951 | -0.13733 | 0.096131 | 122.8592 | -0.18768 | -0.050354 | 0.009156 | -0.18768 | -0.22888 | 0.068665 | 0.091552 | -0.22431 | 0.004577 | -0.032043 | 122.8683 | 122.7814 | 58.7906 | -122.9095 | 122.8409 | 122.7402 | 58.9188 | -123.0011
983.0156 | 123.0972 | -58.8776 | 63.8809 | 0.16006 | 0.0097989 | 0.068678 | 0.068167 | 0.12971 | -0.00071785 | -0.0019505 | -1.1446 | -0.0065626 | 0.05871 | 0.06103 | 0.004422 | -0.0074876 | 63.9359 | 64.0228 | -0.050354 | -59.0561 | 63.945 | -58.9096 | -59.0103 | -58.754 | 0.022888 | -59.0607 | 63.9359 | 63.8809 | -59.0424 | -59.1064 | -0.032044 | -0.13275 | 0.064087 | 122.9004 | -0.17853 | -0.045776 | 0.054932 | -0.16479 | -0.22888 | 0.054932 | 0.1236 | -0.18311 | 0.045776 | 0 | 122.8226 | 122.8134 | 58.8272 | -122.8912 | 122.8134 | 122.7585 | 58.9005 | -122.9874
984.0156 | 123.0743 | -58.8867 | 63.9038 | 0.18295 | 0.012149 | 0.067823 | 0.071585 | 0.12843 | 0.0024865 | -0.0045139 | 0.18295 | -0.0054944 | 0.06341 | 0.059535 | 0.004422 | -0.0072738 | 63.8763 | 63.9587 | -0.1236 | -59.1064 | 63.9862 | -58.9645 | -59.024 | -58.8135 | -0.009155 | -59.1339 | 63.9725 | 63.8672 | -59.0652 | -59.111 | -0.07782 | -0.13733 | 0.082397 | 122.8455 | -0.21973 | -0.082397 | -0.027466 | -0.17853 | -0.2243 | 0.068664 | 0.073242 | -0.24719 | -0.022888 | -0.036622 | 122.8729 | 122.7631 | 58.7631 | -122.9279 | 122.8592 | 122.7539 | 58.8776 | -123.0148
985.0156 | 123.0698 | -58.8959 | 63.913 | 0.16006 | 0.013003 | 0.064405 | 0.070731 | 0.12843 | 0.00099115 | -0.0019505 | 0.19821 | -0.0037854 | 0.061487 | 0.061885 | 0.0057038 | -0.0053512 | 63.8672 | 63.9542 | -0.14648 | -59.1019 | 64.0137 | -58.9554 | -59.024 | -58.8409 | -0.027466 | -59.1431 | 63.9862 | 63.8855 | -59.0561 | -59.1385 | -0.059509 | -0.12817 | 0.10071 | 122.85 | -0.20599 | -0.07782 | -0.045777 | -0.16022 | -0.24262 | 0.073242 | 0.054932 | -0.24719 | -0.004577 | -0.027466 | 122.9095 | 122.7631 | 58.7494 | -122.937 | 122.8821 | 122.7814 | 58.8684 | -123.0515
986.0156 | 123.0057 | -58.9188 | 63.9359 | 3.372 | 0.013858 | 0.068037 | 0.07479 | 0.1295 | 0.0024865 | -0.0043003 | 0.053253 | -0.0061352 | 0.062342 | 0.059748 | 0.0046356 | -0.0047104 | 63.945 | 63.913 | -0.16937 | -59.1293 | 64.032 | -58.9462 | -59.0012 | -58.8821 | -0.073242 | -59.1934 | 64.0274 | 63.945 | -59.0607 | -59.1248 | -0.027466 | -0.082398 | 0.09613 | 122.8317 | -0.21057 | -0.12817 | 0.009155 | -0.14191 | -0.20599 | 0.091553 | 0.036621 | -0.27466 | -0.068664 | 0.009155 | 122.9507 | 122.8638 | 58.7494 | -122.937 | 122.9462 | 122.8638 | 58.8455 | -123.0606
987.0156 | 123.0331 | -58.8684 | 63.945 | 0.14481 | 0.0083035 | 0.069532 | 0.070517 | 0.13121 | -0.0039221 | -0.0053683 | 0.13718 | -0.0054944 | 0.060846 | 0.059535 | 0.00036322 | -0.004924 | 63.8809 | 64.0045 | -0.07782 | -59.0607 | 63.9725 | -58.9188 | -59.0195 | -58.8272 | 0.036621 | -59.0744 | 63.9862 | 63.8992 | -59.0103 | -59.0836 | -0.050354 | -0.15106 | 0.027466 | 122.8729 | -0.19226 | -0.041199 | -0.064087 | -0.14191 | -0.21515 | 0.041199 | 0.041199 | -0.20599 | 0.009155 | -0.045776 | 122.8409 | 122.7493 | 58.7906 | -122.9645 | 122.8546 | 122.7676 | 58.905 | -123.0286
988.0156 | 123.0698 | -58.9005 | 63.913 | 0.083771 | 0.011935 | 0.069319 | 0.069663 | 0.13035 | -0.0032813 | -0.0040867 | 0.26688 | -0.006349 | 0.062555 | 0.057185 | 0.0037812 | -0.0062058 | 63.9221 | 64.032 | -0.059509 | -59.0561 | 63.9679 | -58.9188 | -58.9783 | -58.7906 | 0.041199 | -59.0836 | 63.9542 | 63.8809 | -59.0378 | -59.1064 | -0.01831 | -0.077819 | 0.054932 | 122.9324 | -0.15564 | -0.07782 | 0.009155 | -0.13733 | -0.20599 | 0.041199 | 0.10986 | -0.1831 | 0.022888 | -0.032044 | 122.8683 | 122.8226 | 58.8409 | -122.8912 | 122.8546 | 122.7814 | 58.9417 | -123.0194
989.0156 | 123.1018 | -58.873 | 63.9038 | 0.19821 | 0.010013 | 0.06761 | 0.067099 | 0.12971 | 0.0022729 | -0.0019505 | 0.16769 | -0.005708 | 0.061273 | 0.057826 | 0.0046356 | -0.0072738 | 63.913 | 63.9908 | -0.11902 | -59.0973 | 63.9999 | -58.9371 | -59.0195 | -58.8226 | 0.022888 | -59.0881 | 63.9816 | 63.8855 | -59.0149 | -59.0973 | -0.064087 | -0.14648 | 0.09613 | 122.8638 | -0.2243 | -0.07782 | 0.009155 | -0.14191 | -0.2243 | 0.077819 | 0.050354 | -0.21515 | 0.009155 | -0.018311 | 122.8729 | 122.7859 | 58.754 | -122.9233 | 122.8546 | 122.7585 | 58.8959 | -123.0011
990.0156 | 122.9828 | -58.8913 | 63.9954 | 0.053253 | 0.013003 | 0.067823 | 0.070731 | 0.12758 | 0.00099115 | -0.0032321 | 0.12192 | -0.00464 | 0.062342 | 0.060603 | 0.0048492 | -0.0059922 | 63.8718 | 63.8947 | -0.17853 | -59.1293 | 64.0366 | -58.9417 | -59.0286 | -58.8821 | -0.14191 | -59.4269 | 63.9679 | 63.8718 | -59.079 | -59.1385 | -0.050354 | -0.13733 | 0.041199 | 122.7859 | -0.23804 | -0.10071 | -0.1236 | -0.18768 | -0.24719 | -0.027465 | 0.009155 | -0.53558 | -0.28839 | -0.1236 | 122.9279 | 122.7631 | 58.7128 | -123.024 | 122.8592 | 122.7631 | 58.7494 | -123.1338
991.0156 | 123.111 | -58.8409 | 63.9313 | 0.16006 | 0.0091581 | 0.066541 | 0.06774 | 0.13078 | -0.0017859 | -0.0049411 | 0.27451 | -0.0052808 | 0.06106 | 0.059962 | 0.0050628 | -0.0025742 | 63.9404 | 64.0594 | -0.068665 | -59.0286 | 63.9725 | -58.9371 | -58.9691 | -58.8547 | -0.18768 | -58.9371 | 63.9359 | 63.9175 | -59.0149 | -59.0744 | -0.096131 | -0.12817 | 0.041199 | 122.9004 | -0.18768 | -0.059509 | 0.009156 | -0.17395 | -0.23346 | 0.004578 | -0.013733 | -0.096131 | 0.13733 | -0.013732 | 122.8134 | 122.7814 | 58.7723 | -122.9004 | 122.7768 | 122.7585 | 58.6533 | -123.0057
992.0156 | 122.9645 | -58.905 | 63.9633 | 0.045624 | 0.014499 | 0.067823 | 0.07009 | 0.12971 | 0.0024865 | -0.0038731 | 0.12192 | -0.0048536 | 0.065119 | 0.057826 | 0.0039948 | -0.0068466 | 63.8672 | 63.945 | -0.1236 | -59.0698 | 64.0457 | -58.9325 | -59.0195 | -58.9005 | -0.059509 | -59.2072 | 64.0182 | 63.945 | -59.0332 | -59.1248 | -0.027466 | -0.11444 | 0.082397 | 122.85 | -0.16479 | -0.050354 | -0.096131 | -0.12817 | -0.21973 | 0.054932 | 0.004577 | -0.30212 | -0.082397 | -0.018311 | 122.9507 | 122.7722 | 58.7814 | -122.9828 | 122.9233 | 122.85 | 58.8455 | -123.0881
993.0156 | 123.0698 | -58.905 | 63.9084 | 0.27451 | 0.011294 | 0.06526 | 0.069022 | 0.1295 | -0.0026405 | -0.0040867 | 0.27451 | -0.0059216 | 0.059992 | 0.059535 | 0.0048492 | -0.0062058 | 63.9175 | 64.0045 | -0.10071 | -59.0469 | 63.9816 | -58.9096 | -59.024 | -58.7906 | 0.16022 | -59.079 | 63.9633 | 63.8855 | -59.0286 | -59.1156 | -0.004578 | -0.11902 | 0.073242 | 122.9095 | -0.14191 | -0.022888 | 0.009156 | -0.1236 | -0.21057 | 0.054932 | 0.11444 | -0.17395 | 0.036622 | -0.022888 | 122.8867 | 122.8226 | 58.8043 | -122.9324 | 122.8683 | 122.7905 | 59.0652 | -123.024
994.0156 | 122.9828 | -58.9005 | 63.9633 | 0.14481 | 0.014712 | 0.065687 | 0.069449 | 0.13014 | 0.00099115 | -0.0021641 | -1.3277 | -0.007417 | 0.066828 | 0.060816 | 0.0033538 | -0.0079148 | 63.8351 | 63.8809 | -0.17395 | -59.1293 | 64.0411 | -58.9508 | -59.0515 | -58.8135 | 0.009155 | -59.1888 | 64.0228 | 63.9587 | -59.0515 | -59.1385 | -0.050354 | -0.15106 | 0.07782 | 122.7814 | -0.22888 | -0.077819 | -0.12817 | -0.15106 | -0.23804 | 0.059509 | 0.086975 | -0.28839 | -0.050354 | -0.004578 | 122.9416 | 122.7356 | 58.7265 | -123.0148 | 122.9233 | 122.8592 | 58.9096 | -123.1018
995.0156 | 123.0743 | -58.8867 | 63.8992 | 0.19821 | 0.0083035 | 0.066541 | 0.069449 | 0.12886 | -0.0026405 | -2.7856e-05 | -1.0606 | -0.0069898 | 0.062555 | 0.058467 | 0.0018584 | -0.0079148 | 63.9221 | 64.0366 | -0.064087 | -59.0469 | 63.9404 | -58.9462 | -59.0149 | -58.7814 | 0.15106 | -59.0515 | 63.9725 | 63.8809 | -59.024 | -59.0973 | -0.059509 | -0.12817 | 0.041199 | 122.9233 | -0.16022 | -0.032043 | 0.022888 | -0.13733 | -0.21057 | 0.073242 | 0.10529 | -0.16479 | 0.045776 | -0.018311 | 122.8271 | 122.8088 | 58.8226 | -122.9141 | 122.8592 | 122.7676 | 59.0378 | -122.9965
996.0156 | 122.9507 | -58.9188 | 63.9313 | 0.12192 | 0.015353 | 0.067823 | 0.068167 | 0.13185 | 0.00077755 | -0.0015231 | 0.068512 | -0.0031446 | 0.065119 | 0.061244 | 0.0042084 | -0.0064194 | 63.8351 | 63.8992 | -0.16937 | -59.1156 | 64.0457 | -58.9371 | -59.0195 | -58.9279 | 0.050354 | -59.2026 | 64.0137 | 63.945 | -59.0515 | -59.1385 | -0.018311 | -0.10071 | 0.11444 | 122.818 | -0.19684 | -0.096131 | -0.09613 | -0.13275 | -0.21973 | 0.082398 | -0.009155 | -0.28381 | -0.064087 | 0.013733 | 122.9645 | 122.7539 | 58.7494 | -122.9507 | 122.9324 | 122.8638 | 58.9691 | -123.0698
997.0156 | 123.0606 | -58.873 | 63.9633 | 0.19058 | 0.011081 | 0.06761 | 0.069876 | 0.13206 | -0.0011451 | -0.0049411 | 0.23636 | -0.0061352 | 0.06341 | 0.059748 | 0.0031402 | -0.0062058 | 63.8855 | 63.9542 | -0.15564 | -59.0927 | 64.032 | -58.9188 | -59.0149 | -58.8226 | -0.009155 | -59.1064 | 64.0137 | 63.945 | -59.0424 | -59.0973 | -0.045776 | -0.14191 | 0.068664 | 122.8271 | -0.21973 | -0.077819 | -0.07782 | -0.16937 | -0.2243 | 0.050354 | 0.050354 | -0.23346 | -0.009155 | -0.018311 | 122.905 | 122.7585 | 58.7173 | -122.9782 | 122.8867 | 122.818 | 58.8638 | -123.0606
998.0156 | 123.0377 | -58.8638 | 63.9587 | 0.14481 | 0.014499 | 0.068891 | 0.069663 | 0.12886 | 0.00013675 | -0.0028049 | 0.2211 | -0.0048536 | 0.064051 | 0.062098 | 0.0031402 | -0.0062058 | 63.8718 | 63.9313 | -0.15564 | -59.0881 | 64.0457 | -58.9279 | -59.0195 | -58.8272 | -0.004578 | -59.111 | 64.032 | 63.9496 | -59.0378 | -59.1019 | -0.064086 | -0.15564 | 0.086975 | 122.7951 | -0.2243 | -0.068665 | -0.086975 | -0.17395 | -0.23804 | 0.073242 | 0.036622 | -0.24719 | -0.009155 | -0.009155 | 122.9095 | 122.7356 | 58.7082 | -122.9782 | 122.8958 | 122.8134 | 58.8593 | -123.0606
999.0156 | 123.0148 | -58.8821 | 63.9633 | 0.11429 | 0.011935 | 0.066969 | 0.068594 | 0.12886 | -0.0024269 | -0.0028049 | 0.22873 | -0.0052808 | 0.062128 | 0.06103 | 0.0020722 | -0.006633 | 63.8718 | 63.9221 | -0.15564 | -59.0973 | 64.0274 | -58.9325 | -59.024 | -58.8593 | 0.013733 | -59.1568 | 64.0228 | 63.9496 | -59.0195 | -59.111 | -0.050354 | -0.14191 | 0.064087 | 122.8043 | -0.21515 | -0.073242 | -0.091553 | -0.13733 | -0.22888 | 0.059509 | 0.022888 | -0.27466 | -0.045776 | -0.013733 | 122.9095 | 122.7539 | 58.7265 | -122.9874 | 122.905 | 122.8317 | 58.8959 | -123.0743
1000.0156 | 123.0972 | -58.9005 | 63.9313 | 0.17532 | 0.013858 | 0.067823 | 0.069449 | 0.13099 | -0.0011451 | -0.0038731 | 0.24399 | -0.0054944 | 0.062769 | 0.059748 | 0.0035674 | -0.0079148 | 63.8992 | 63.9725 | -0.13733 | -59.0927 | 63.9999 | -58.9371 | -59.0057 | -58.8181 | 0.1236 | -59.0973 | 64.0045 | 63.9084 | -59.024 | -59.1202 | -0.036621 | -0.10529 | 0.068665 | 122.8729 | -0.19226 | -0.086975 | -0.032043 | -0.1236 | -0.21973 | 0.073243 | 0.082398 | -0.19684 | 0.022888 | -0.022888 | 122.9004 | 122.7997 | 58.7631 | -122.937 | 122.905 | 122.8088 | 59.024 | -123.0515
1001.0156 | 123.056 | -58.8959 | 63.9313 | 0.16769 | 0.012362 | 0.066755 | 0.068594 | 0.13078 | -0.00029045 | -0.0025913 | 0.2211 | -0.003999 | 0.064264 | 0.058253 | 0.0042084 | -0.005565 | 63.8718 | 63.945 | -0.14191 | -59.1064 | 64.0137 | -58.9279 | -59.0149 | -58.8409 | 0.09613 | -59.1293 | 63.9862 | 63.9542 | -59.024 | -59.1064 | -0.032043 | -0.11902 | 0.082398 | 122.8409 | -0.21057 | -0.091552 | -0.059509 | -0.12817 | -0.21057 | 0.054932 | 0.054932 | -0.23346 | -0.022888 | 0.022889 | 122.9095 | 122.7676 | 58.754 | -122.9462 | 122.8821 | 122.85 | 58.992 | -123.0377
1002.0156 | 123.0835 | -58.8913 | 63.9084 | 0.13718 | 0.01044 | 0.066541 | 0.072012 | 0.12822 | -0.0039221 | -0.0038731 | 0.30502 | -0.0069898 | 0.064264 | 0.059107 | 0.0018584 | -0.0040696 | 63.8901 | 64.0228 | -0.068665 | -59.0881 | 63.9633 | -58.9188 | -58.9828 | -58.8272 | 0.25177 | -59.1064 | 63.9404 | 63.913 | -59.0515 | -59.1202 | -0.027466 | -0.091553 | 0.054932 | 122.9141 | -0.19684 | -0.10529 | -0.01831 | -0.16022 | -0.22888 | 0.032044 | 0.064087 | -0.21515 | 0.013733 | 0.004578 | 122.8546 | 122.7814 | 58.8226 | -122.8912 | 122.8317 | 122.8043 | 59.1431 | -123.0286
1003.0156 | 123.0743 | -58.8959 | 63.8901 | 0.13718 | 0.0089443 | 0.067182 | 0.067954 | 0.12822 | -0.0037085 | -0.0051547 | 0.22873 | -0.0052808 | 0.065546 | 0.061457 | 0.0031402 | -0.0053512 | 63.9175 | 64.0228 | -0.064087 | -59.0698 | 63.945 | -58.9233 | -58.9966 | -58.8043 | 0.28381 | -59.0973 | 63.9404 | 63.913 | -59.0332 | -59.1064 | -0.027466 | -0.10071 | 0.054931 | 122.9187 | -0.17395 | -0.073242 | 0.027466 | -0.13733 | -0.21057 | 0.050354 | 0.091553 | -0.20142 | 0.009155 | 0.022888 | 122.8409 | 122.8134 | 58.8318 | -122.8867 | 122.8363 | 122.8088 | 59.1797 | -122.9965
1004.0156 | 123.0011 | -58.9142 | 63.9816 | -0.0077822 | 0.016421 | 0.066541 | 0.068594 | 0.13398 | 0.0018457 | -0.0025913 | 0.053253 | -0.0054944 | 0.063196 | 0.059107 | 0.00549 | -0.0091966 | 63.9084 | 63.9404 | -0.14191 | -59.0881 | 64.0182 | -58.9279 | -59.0332 | -58.8867 | 0.26093 | -59.1934 | 64.0182 | 63.945 | -59.0469 | -59.1248 | -0.013732 | -0.11902 | 0.036622 | 122.8546 | -0.17395 | -0.054932 | -0.073242 | -0.13275 | -0.21057 | 0.036622 | 0.027466 | -0.27923 | -0.068664 | -0.036621 | 122.9324 | 122.8226 | 58.7723 | -123.0148 | 122.9324 | 122.8592 | 59.1751 | -123.1064
1005.0156 | 123.0515 | -58.8776 | 63.9175 | 0.12955 | 0.0048855 | 0.066755 | 0.069449 | 0.12993 | -0.0032813 | -0.0055821 | 0.27451 | -0.006349 | 0.061273 | 0.059107 | 0.0012176 | -0.0047104 | 63.8809 | 64.0182 | -0.073242 | -59.0744 | 63.9679 | -58.9371 | -58.9828 | -58.8272 | 0.28839 | -59.0973 | 63.9404 | 63.9267 | -59.0378 | -59.0881 | -0.05951 | -0.10529 | 0.050354 | 122.8958 | -0.19684 | -0.091553 | -0.036622 | -0.16022 | -0.21057 | 0.022888 | 0.050354 | -0.21973 | -0.009155 | 0.009155 | 122.8455 | 122.7585 | 58.8043 | -122.9004 | 122.818 | 122.8043 | 59.166 | -123.0057
1006.0156 | 123.0148 | -58.9417 | 63.9587 | -0.053558 | 0.013003 | 0.068464 | 0.070517 | 0.12928 | 0.0035547 | -0.0019505 | -0.03067 | -0.0048536 | 0.064478 | 0.059962 | 0.0050628 | -0.0070602 | 63.9267 | 63.9862 | -0.09613 | -59.0698 | 64.032 | -58.9371 | -59.0149 | -58.8776 | 0.30212 | -59.1751 | 64.0274 | 63.9587 | -59.0607 | -59.1339 | 0.004577 | -0.073243 | 0.073242 | 122.9279 | -0.12817 | -0.054931 | -0.032043 | -0.11902 | -0.19226 | 0.068665 | 0.064087 | -0.23346 | -0.041199 | 0 | 122.9736 | 122.8683 | 58.8455 | -122.9736 | 122.9691 | 122.9004 | 59.2438 | -123.0927
1007.0156 | 123.0148 | -58.905 | 63.945 | 0.030365 | 0.011935 | 0.068891 | 0.068167 | 0.13142 | -0.0013587 | -0.0023777 | 0.16769 | -0.00464 | 0.064051 | 0.058039 | 0.0046356 | -0.0057786 | 63.858 | 63.9221 | -0.19226 | -59.1248 | 64.032 | -58.9462 | -59.0149 | -58.873 | 0.21973 | -59.166 | 64.0045 | 63.945 | -59.0561 | -59.1339 | -0.041199 | -0.10986 | 0.086975 | 122.8271 | -0.21973 | -0.10986 | -0.086975 | -0.15106 | -0.22888 | 0.05951 | 0.032043 | -0.26093 | -0.032044 | 0 | 122.937 | 122.7631 | 58.7128 | -122.9599 | 122.9095 | 122.85 | 59.1248 | -123.0789
1008.0156 | 122.9874 | -58.8593 | 63.9771 | -0.0077822 | 0.01514 | 0.065046 | 0.07009 | 0.12971 | 0.00099115 | -0.0017369 | 0.030365 | -0.0042126 | 0.062982 | 0.058253 | 0.004422 | -0.008342 | 63.9038 | 63.9954 | -0.1236 | -59.0698 | 64.0549 | -58.9142 | -59.0057 | -58.8409 | 0.16937 | -59.1751 | 64.0411 | 63.9816 | -59.0332 | -59.0881 | -0.054932 | -0.14648 | 0.07782 | 122.8546 | -0.21057 | -0.064087 | -0.073242 | -0.17395 | -0.22888 | 0.064087 | 0.018311 | -0.31586 | -0.086975 | 0.004577 | 122.9141 | 122.7631 | 58.7357 | -122.9828 | 122.9004 | 122.8409 | 59.0286 | -123.0652
1009.0156 | 122.9965 | -58.873 | 63.9908 | 0.14481 | 0.01514 | 0.066755 | 0.070303 | 0.12907 | -0.00029045 | -0.0028049 | -0.11459 | -0.0054944 | 0.062769 | 0.059748 | 0.0031402 | -0.0044968 | 63.9862 | 63.6017 | -0.37537 | -58.8913 | 64.0274 | -58.9279 | -58.9737 | -58.8821 | 0.009155 | -59.1568 | 64.0366 | 63.9679 | -59.0378 | -59.0973 | -0.054931 | -0.10071 | 0.036621 | 122.4747 | -0.01831 | 0.082398 | -0.004578 | -0.1648 | -0.2243 | 0.045776 | -0.009155 | -0.28381 | -0.059509 | -0.022888 | 122.9004 | 122.8592 | 58.4976 | -122.9645 | 122.9095 | 122.8409 | 58.8821 | -123.0881
1010.0156 | 123.0423 | -58.8501 | 64.0182 | -0.068817 | 0.014926 | 0.067396 | 0.071799 | 0.12928 | -7.6852e-05 | -0.0030185 | 0.015106 | -0.005708 | 0.063623 | 0.061244 | 0.0039948 | -0.0072738 | 63.9404 | 64.032 | -0.082397 | -59.0515 | 64.0594 | -58.9005 | -58.9645 | -58.8226 | 0.09613 | -59.1248 | 64.0732 | 64.0045 | -59.0012 | -59.0744 | -0.050354 | -0.11444 | 0.041198 | 122.8821 | -0.20142 | -0.086975 | -0.07782 | -0.15106 | -0.2243 | 0.054931 | 0.027466 | -0.27466 | -0.050354 | -0.013733 | 122.9095 | 122.7905 | 58.7677 | -122.9828 | 122.9233 | 122.8546 | 58.9462 | -123.0927
1011.0156 | 122.8455 | -58.9188 | 63.9725 | 0.045624 | 0.013003 | 0.067182 | 0.071158 | 0.12864 | 0.00035035 | -0.0028049 | 0.12192 | -0.002931 | 0.064264 | 0.060389 | 0.0042084 | -0.0068466 | 63.8489 | 63.9313 | -0.21057 | -59.0927 | 64.0823 | -58.9142 | -58.9828 | -58.8684 | 0.041199 | -59.1614 | 64.0503 | 63.9954 | -59.0149 | -59.0836 | 0.004577 | -0.064087 | 0.10986 | 122.85 | -0.17395 | -0.10986 | -0.1236 | -0.096131 | -0.16479 | 0.07782 | 0.050354 | -0.24262 | -0.07782 | 0.022888 | 123.0011 | 122.7676 | 58.7082 | -122.9553 | 122.9691 | 122.9141 | 58.96 | -123.056
1012.0156 | 123.0148 | -58.8547 | 63.9816 | -0.061188 | 0.013858 | 0.066755 | 0.072867 | 0.12907 | -0.0011451 | -0.0030185 | -0.068817 | -0.00464 | 0.0664 | 0.061244 | 0.0031402 | -0.004924 | 63.9496 | 64.0457 | -0.07782 | -59.1431 | 64.0411 | -58.9279 | -58.9783 | -58.7906 | 0.28381 | -59.0927 | 64.0457 | 64.0091 | -59.0103 | -59.0652 | -0.073242 | -0.1236 | 0.05951 | 122.9004 | -0.28839 | -0.16479 | -0.032043 | -0.15564 | -0.21057 | 0.064087 | 0.064087 | -0.23804 | -0.027465 | 0.027466 | 122.8958 | 122.8043 | 58.7769 | -122.9599 | 122.9004 | 122.8638 | 59.1385 | -123.0469
1013.0156 | 122.9599 | -58.905 | 63.9954 | -0.00015269 | 0.014712 | 0.067823 | 0.070517 | 0.13163 | 0.00013675 | -0.0030185 | 0.060883 | -0.0031446 | 0.064905 | 0.060816 | 0.0039948 | -0.0051376 | 63.8809 | 63.9633 | -0.15564 | -59.0744 | 64.0686 | -58.9417 | -59.0012 | -58.9005 | 0.22888 | -59.1751 | 64.032 | 63.9771 | -59.0332 | -59.0881 | -0.036621 | -0.096131 | 0.073243 | 122.8683 | -0.16937 | -0.073242 | -0.11444 | -0.12817 | -0.18311 | 0.036621 | 0.004577 | -0.27008 | -0.086975 | -0.01831 | 122.9736 | 122.7859 | 58.7494 | -122.9965 | 122.937 | 122.8821 | 59.1339 | -123.0835
1014.0156 | 123.024 | -58.8776 | 63.9999 | -0.091705 | 0.012362 | 0.066328 | 0.069022 | 0.1295 | 0.00099115 | -0.0040867 | 0.0074766 | -0.0050672 | 0.064051 | 0.059748 | 0.0050628 | -0.0072738 | 63.9313 | 63.9999 | -0.10071 | -59.0469 | 64.0457 | -58.9233 | -58.9874 | -58.8409 | 0.36163 | -59.1293 | 64.032 | 63.9816 | -59.0286 | -59.0836 | -0.045777 | -0.10986 | 0.045776 | 122.8775 | -0.16937 | -0.059509 | -0.068665 | -0.15106 | -0.20599 | 0.032043 | 0.036621 | -0.25177 | -0.045776 | -0.018311 | 122.9233 | 122.8088 | 58.7769 | -122.9874 | 122.9095 | 122.8592 | 59.2392 | -123.0835
1015.0156 | 123.1155 | -58.8913 | 64.0091 | 0.11429 | 0.012149 | 0.066969 | 0.071372 | 0.12864 | -0.0011451 | -0.0023777 | 0.17532 | -0.0069898 | 0.065332 | 0.060389 | 0.0037812 | -0.0051376 | 63.8443 | 63.9221 | -0.20142 | -59.1019 | 64.0411 | -58.9233 | -59.0012 | -58.8913 | 0.27466 | -59.1797 | 64.032 | 63.9725 | -59.0469 | -59.1476 | -0.032044 | -0.10986 | 0.032044 | 122.8134 | -0.21057 | -0.10071 | -0.1648 | -0.15564 | -0.25635 | 0.022888 | 0 | -0.28839 | -0.032043 | -0.036621 | 122.9324 | 122.7356 | 58.6899 | -123.0103 | 122.9233 | 122.8638 | 59.166 | -123.1567
1016.0156 | 123.0194 | -58.7906 | 64.0503 | -0.084076 | 0.014071 | 0.066755 | 0.070517 | 0.12971 | 0.00035035 | -0.0023777 | -0.038299 | -0.0037854 | 0.062555 | 0.061671 | 0.0039948 | -0.0051376 | 63.8626 | 64.1464 | -0.086975 | -58.9874 | 64.0823 | -58.8913 | -58.9417 | -58.7814 | 0.4303 | -59.0607 | 64.0915 | 64.0366 | -58.9417 | -59.0424 | -0.10071 | -0.15106 | 0.032043 | 122.937 | -0.19684 | -0.045777 | -0.18768 | -0.15106 | -0.25177 | 0.041199 | 0.009155 | -0.27008 | -0.018311 | -0.013733 | 122.8729 | 122.6532 | 58.7036 | -122.9919 | 122.8821 | 122.8271 | 59.2209 | -123.0927
1017.0156 | 122.9507 | -58.8364 | 64.0457 | 0.11429 | 0.01578 | 0.066541 | 0.069876 | 0.13078 | -7.6852e-05 | -0.0043003 | 0.09903 | -0.0042126 | 0.059778 | 0.058894 | 0.0037812 | -0.005565 | 63.9221 | 63.9954 | -0.18768 | -59.024 | 64.1235 | -58.8593 | -58.9371 | -58.8318 | 0.32959 | -59.1019 | 64.119 | 64.0594 | -58.9554 | -59.0286 | -0.022888 | -0.10071 | 0.07782 | 122.8317 | -0.18768 | -0.086975 | -0.1236 | -0.11902 | -0.19226 | 0.073243 | 0.004578 | -0.2655 | -0.073243 | 0.013733 | 122.9599 | 122.7585 | 58.6487 | -122.9828 | 122.9553 | 122.8958 | 59.166 | -123.0743
1018.0156 | 123.0148 | -58.786 | 64.1006 | -0.15274 | 0.013858 | 0.066114 | 0.070303 | 0.13014 | 0.00013675 | -0.0045139 | -0.053558 | -0.0054944 | 0.062769 | 0.059535 | 0.006131 | -0.0085556 | 64.0137 | 64.0961 | -0.09613 | -58.96 | 64.119 | -58.8272 | -58.9325 | -58.8547 | 0.63629 | -59.0332 | 64.1098 | 64.0503 | -58.9508 | -59.0103 | -0.041198 | -0.14648 | 0.018311 | 122.8821 | -0.17395 | -0.027466 | -0.086975 | -0.16479 | -0.2243 | 0.009155 | -0.068664 | -0.24719 | -0.022888 | -0.050354 | 122.905 | 122.7997 | 58.6899 | -123.0331 | 122.8958 | 122.8363 | 59.4223 | -123.111
1019.0156 | 122.9965 | -58.8501 | 64.0137 | 0.10666 | 0.013217 | 0.066114 | 0.068381 | 0.12971 | 0.00013675 | -0.0051547 | 0.28976 | -0.0035718 | 0.064051 | 0.060816 | 0.002713 | -0.0062058 | 63.9038 | 63.9587 | -0.18768 | -59.0652 | 64.0549 | -58.9142 | -58.9874 | -58.8318 | 0.3891 | -59.0973 | 64.0411 | 64.0137 | -59.024 | -59.0607 | -0.064087 | -0.13733 | 0.041199 | 122.8088 | -0.21515 | -0.07782 | -0.10986 | -0.17395 | -0.21057 | 0.027466 | 0.018311 | -0.24719 | -0.036621 | 0 | 122.905 | 122.7539 | 58.6624 | -123.0011 | 122.8912 | 122.8638 | 59.2392 | -123.0743
1020.0156 | 123.0011 | -58.8409 | 63.9908 | -0.015411 | 0.015567 | 0.066755 | 0.070303 | 0.12886 | 0.00077755 | -0.0045139 | 0.030365 | -0.0048536 | 0.064051 | 0.059535 | 0.0037812 | -0.0087692 | 63.9496 | 64.032 | -0.086975 | -59.0378 | 64.0594 | -58.8959 | -58.9783 | -58.8318 | 0.49896 | -59.1064 | 64.0686 | 63.9954 | -58.992 | -59.0927 | -0.054932 | -0.13733 | 0.068664 | 122.8729 | -0.19684 | -0.05951 | -0.041199 | -0.15106 | -0.25177 | 0.07782 | 0.009155 | -0.2655 | -0.013733 | 0.004577 | 122.9004 | 122.7905 | 58.754 | -122.9691 | 122.9095 | 122.8363 | 59.3399 | -123.0835
1021.0156 | 123.1201 | -58.8364 | 64.0091 | -0.03067 | 0.0057401 | 0.068678 | 0.067954 | 0.128 | -0.0075537 | -0.0068637 | 0.0914 | -0.0078442 | 0.059992 | 0.060603 | 0.00036322 | -0.0030014 | 63.8947 | 64.064 | -0.054932 | -59.0057 | 64.0411 | -58.8913 | -58.9325 | -58.7723 | 0.60883 | -59.0149 | 64.0274 | 63.9587 | -58.992 | -59.0744 | -0.054931 | -0.09613 | 0.032044 | 122.9004 | -0.16937 | -0.073242 | -0.11444 | -0.15564 | -0.23804 | 0.018311 | 0.064087 | -0.17853 | 0.059509 | -0.050354 | 122.8775 | 122.731 | 58.7814 | -122.9416 | 122.8638 | 122.7951 | 59.4452 | -123.0835
1022.0156 | 123.0148 | -58.873 | 64.0274 | 0.015106 | 0.011508 | 0.06761 | 0.07244 | 0.1327 | 0.0033411 | -0.0028049 | 0.022736 | -0.0033582 | 0.064051 | 0.059107 | 0.0039948 | -0.0074876 | 63.9221 | 63.9908 | -0.13733 | -59.0652 | 64.064 | -58.9005 | -58.9828 | -58.8501 | 0.48981 | -59.1293 | 64.0594 | 64.0045 | -59.024 | -59.0744 | -0.027466 | -0.10986 | 0.036621 | 122.8638 | -0.19226 | -0.082398 | -0.10529 | -0.15106 | -0.20142 | 0.032043 | 0.022888 | -0.25635 | -0.054931 | -0.022888 | 122.937 | 122.7951 | 58.7357 | -123.0103 | 122.9324 | 122.8775 | 59.3628 | -123.1018
1023.0156 | 122.9599 | -58.8318 | 63.9725 | -2.6781 | 0.010226 | 0.06291 | 0.071158 | 0.13014 | -0.0026405 | -0.0038731 | 0.18295 | -0.0048536 | 0.065119 | 0.06103 | 0.0035674 | -0.005565 | 63.8214 | 63.9908 | -0.17395 | -59.0836 | 64.0869 | -58.8913 | -58.9828 | -58.8409 | 0.43945 | -59.1248 | 64.0457 | 64.0091 | -59.0378 | -59.0744 | -0.059509 | -0.15106 | 0.11444 | 122.8226 | -0.25177 | -0.10071 | -0.15106 | -0.20599 | -0.24262 | 0.073242 | -0.009155 | -0.29297 | -0.050354 | 0.036621 | 122.9187 | 122.6532 | 58.6578 | -122.9553 | 122.8775 | 122.8409 | 59.2712 | -123.0469
1024.0156 | 122.9965 | -58.8593 | 64.0091 | -0.045929 | 0.013217 | 0.068037 | 0.072867 | 0.12822 | 0.0016321 | -0.0036595 | 0.053253 | -0.003999 | 0.064691 | 0.060389 | 0.0048492 | -0.008342 | 63.9359 | 64.0137 | -0.14648 | -59.0332 | 64.0732 | -58.8959 | -58.9737 | -58.8318 | 0.49896 | -59.111 | 64.0732 | 64.0274 | -58.992 | -59.0652 | -0.036621 | -0.11444 | 0.064087 | 122.8729 | -0.17395 | -0.059509 | -0.073242 | -0.13275 | -0.20599 | 0.064087 | 0.027466 | -0.25177 | -0.045776 | 0.018311 | 122.9324 | 122.7951 | 58.7128 | -122.9828 | 122.9324 | 122.8867 | 59.3582 | -123.0743
1025.1562 | 123.2117 | -58.7677 | 64.0503 | -0.19852 | 0.0038175 | 0.066328 | 0.069235 | 0.12993 | -0.0062721 | -0.0036595 | -0.0077819 | -0.0076306 | 0.061914 | 0.060389 | -0.00049138 | -0.003856 | 63.9771 | 64.1785 | 0.013733 | -58.9554 | 64.0503 | -58.8501 | -58.905 | -58.7036 | 0.67749 | -58.9645 | 64.032 | 64.0045 | -58.9554 | -59.0149 | -0.082398 | -0.13733 | 0 | 122.9462 | -0.18768 | -0.050354 | -0.073242 | -0.18768 | -0.24719 | -0.018311 | 0.064087 | -0.19684 | 0.050354 | -0.045776 | 122.818 | 122.7448 | 58.7814 | -122.9553 | 122.7997 | 122.7722 | 59.4452 | -123.0652
1026.0156 | 123.0606 | -58.8226 | 63.9862 | 0.16006 | 0.011508 | 0.067823 | 0.071585 | 0.13014 | -0.0039221 | -0.0045139 | 0.31265 | -0.0052808 | 0.066187 | 0.058467 | 0.0022858 | -0.0057786 | 63.9359 | 64.0869 | -0.091553 | -59.0149 | 64.0411 | -58.8684 | -58.9233 | -58.786 | 0.55389 | -59.0469 | 64.0274 | 63.9587 | -58.9828 | -59.0561 | -0.045776 | -0.10071 | 0.054932 | 122.9095 | -0.19226 | -0.091553 | -0.050354 | -0.16022 | -0.23346 | 0.041199 | 0.036621 | -0.2243 | 0.009155 | -0.027466 | 122.8638 | 122.7585 | 58.7311 | -122.9095 | 122.85 | 122.7814 | 59.3765 | -123.0423
1027.0156 | 123.0423 | -58.8409 | 64.0228 | 0.13718 | 0.012576 | 0.069319 | 0.069663 | 0.1295 | 0.0024865 | -0.0043003 | -0.67154 | -0.0035718 | 0.065759 | 0.060389 | 0.0042084 | -0.0074876 | 63.9175 | 64.0411 | -0.43488 | -59.2117 | 64.0182 | -58.9188 | -58.9371 | -58.7952 | 0.41199 | -59.1385 | 64.0732 | 64.032 | -58.9966 | -59.0607 | -0.07782 | -0.096131 | -0.004577 | 122.8821 | -0.37079 | -0.27466 | -0.10529 | -0.15564 | -0.21973 | 0.050354 | 0.045776 | -0.29755 | -0.07782 | 0.009155 | 122.8592 | 122.7585 | 58.4061 | -122.9599 | 122.9141 | 122.8729 | 59.2529 | -123.0835
1028.0156 | 123.024 | -58.8089 | 64.0091 | -0.0383 | 0.014285 | 0.067182 | 0.068808 | 0.13142 | 0.0014185 | -0.0023777 | 0.045624 | -0.0052808 | 0.065332 | 0.061457 | 0.0050628 | -0.0079148 | 63.9908 | 64.0549 | -0.1236 | -59.0057 | 64.0961 | -58.873 | -58.9462 | -58.786 | 0.54016 | -59.111 | 64.0732 | 64.0366 | -58.9508 | -59.0378 | -0.064087 | -0.13733 | 0.086975 | 122.8638 | -0.19684 | -0.059509 | -0.01831 | -0.14191 | -0.22888 | 0.064087 | 0.022888 | -0.30212 | -0.073242 | 0.027466 | 122.905 | 122.7997 | 58.6853 | -122.9553 | 122.8821 | 122.8455 | 59.3491 | -123.0469
1029.0156 | 122.9645 | -58.8547 | 64.0182 | 0.16769 | 0.011508 | 0.06825 | 0.071158 | 0.13163 | 0.0014185 | -0.0040867 | 3.6848 | -0.0044264 | 0.061914 | 0.059748 | 0.0046356 | -0.0053512 | 63.8809 | 63.9587 | -0.21515 | -59.0561 | 64.0915 | -58.8913 | -58.9508 | -58.8959 | 0.61798 | -59.1293 | 64.0823 | 64.032 | -58.9828 | -59.0561 | -0.036621 | -0.096131 | 0.073242 | 122.8134 | -0.20142 | -0.10529 | -0.13733 | -0.12817 | -0.20142 | 0.064086 | -0.041199 | -0.27466 | -0.073242 | 0.013732 | 122.9462 | 122.7356 | 58.6395 | -122.9691 | 122.937 | 122.8867 | 59.4727 | -123.0743
1030.0156 | 123.024 | -58.8318 | 64.0457 | -0.03067 | 0.012362 | 0.068037 | 0.069663 | 0.12971 | 0.0022729 | -0.0019505 | -0.023041 | -0.0052808 | 0.063623 | 0.059962 | 0.0057038 | -0.0053512 | 63.9816 | 64.0778 | -0.11902 | -59.0057 | 64.1052 | -58.8684 | -58.9325 | -58.7723 | 0.5722 | -59.0927 | 64.0961 | 64.0411 | -58.9417 | -59.0332 | -0.036621 | -0.10071 | 0.05951 | 122.9095 | -0.17395 | -0.073242 | -0.064087 | -0.10986 | -0.20142 | 0.050354 | 0.059509 | -0.26093 | -0.059509 | -0.004577 | 122.937 | 122.8134 | 58.7128 | -122.9782 | 122.9279 | 122.8729 | 59.404 | -123.0789
1031.0156 | 122.9416 | -58.8318 | 64.0274 | 0.060882 | 0.013217 | 0.066969 | 0.070944 | 0.13057 | 0.00099115 | -0.0030185 | 0.10666 | -0.0031446 | 0.06341 | 0.06103 | 0.008908 | -0.0047104 | 63.8809 | 63.9404 | -0.23346 | -59.0607 | 64.1006 | -58.8776 | -58.9783 | -58.96 | 0.55389 | -58.9508 | 64.1006 | 64.0686 | -58.9508 | -59.0515 | -0.045776 | -0.14648 | 0.073242 | 122.7722 | -0.22888 | -0.082398 | -0.14648 | -0.11902 | -0.21973 | 0.073242 | -0.12817 | -0.11902 | 0.10071 | 0.041199 | 122.9324 | 122.7127 | 58.5983 | -123.0057 | 122.9324 | 122.9004 | 59.3857 | -123.0789
1032.0156 | 123.0103 | -58.786 | 64.0549 | 0.053253 | 0.012149 | 0.066328 | 0.069235 | 0.13099 | 0.00035035 | -0.0036595 | -0.015411 | -0.006349 | 0.063837 | 0.060816 | 0.004422 | -0.0077012 | 63.9816 | 64.0915 | -0.10071 | -58.9737 | 64.1235 | -58.8593 | -58.9233 | -58.7585 | 0.58594 | -59.0698 | 64.0778 | 64.0411 | -58.96 | -59.0332 | -0.073242 | -0.13733 | 0.068664 | 122.8775 | -0.18768 | -0.050354 | -0.073243 | -0.17395 | -0.24719 | 0.022888 | 0.027466 | -0.28381 | -0.036621 | -0.013733 | 122.9095 | 122.7676 | 58.6853 | -122.9782 | 122.8638 | 122.8271 | 59.3719 | -123.0881
1033.0156 | 122.9507 | -58.8547 | 64.0457 | 0.15244 | 0.013217 | 0.067823 | 0.070303 | 0.12971 | 0.00056395 | -0.0025913 | 0.17532 | -0.0035718 | 0.062342 | 0.058467 | 0.002713 | -0.0070602 | 63.8855 | 63.9725 | -0.24261 | -59.0332 | 64.1281 | -58.8821 | -58.9645 | -58.8089 | 0.52643 | -59.404 | 64.0732 | 63.9954 | -59.0103 | -59.0698 | -0.027466 | -0.10986 | 0.082398 | 122.8271 | -0.17853 | -0.068664 | -0.16022 | -0.15564 | -0.21515 | 0.027466 | 0.045776 | -0.54932 | -0.33417 | -0.050354 | 122.9828 | 122.7402 | 58.6121 | -123.0103 | 122.9279 | 122.85 | 59.3811 | -123.1155
1034.0156 | 123.0011 | -58.8089 | 64.0594 | -0.099335 | 0.013431 | 0.069105 | 0.070731 | 0.12886 | 0.00013675 | -0.0013095 | -0.015411 | -0.0050672 | 0.065332 | 0.062739 | 0.0020722 | -0.0059922 | 63.9954 | 64.0732 | -0.11902 | -58.9783 | 64.1098 | -58.8501 | -58.9279 | -58.7677 | 0.60425 | -59.0744 | 64.0915 | 64.0457 | -58.9325 | -59.0561 | -0.041199 | -0.11902 | 0.050354 | 122.8821 | -0.16937 | -0.050354 | -0.064087 | -0.1236 | -0.24719 | 0.032044 | 0.041199 | -0.2655 | -0.018311 | -0.013733 | 122.9187 | 122.8043 | 58.6899 | -122.9874 | 122.9004 | 122.8546 | 59.4131 | -123.1155
1035.0156 | 123.0103 | -58.8364 | 64.0411 | 0.11429 | 0.013003 | 0.06526 | 0.069449 | 0.12971 | -0.0019995 | -0.0038731 | 0.19058 | -0.0042126 | 0.065119 | 0.058253 | 0.0039948 | -0.0034286 | 63.913 | 63.9999 | -0.21973 | -59.0469 | 64.1052 | -58.8776 | -58.96 | -58.8181 | 0.48981 | -59.0927 | 64.0869 | 64.0182 | -58.9737 | -59.0286 | -0.041198 | -0.1236 | 0.064087 | 122.8363 | -0.21057 | -0.086975 | -0.12817 | -0.13733 | -0.19226 | 0.045776 | 0.018311 | -0.25635 | -0.064087 | -0.022888 | 122.9416 | 122.7493 | 58.6166 | -123.0011 | 122.9233 | 122.8546 | 59.3262 | -123.0698
1036.0156 | 122.9691 | -58.8364 | 64.0503 | 0.022736 | 0.013431 | 0.066328 | 0.07009 | 0.13014 | 0.0022729 | -0.0053683 | 0.09903 | -0.0054944 | 0.065119 | 0.059748 | 0.0014312 | -0.0077012 | 63.9313 | 64.0274 | -0.16022 | -59.024 | 64.1144 | -58.8638 | -58.9279 | -58.8272 | 0.54016 | -59.1248 | 64.0823 | 64.0549 | -58.9828 | -59.0515 | -0.027466 | -0.091552 | 0.064087 | 122.8638 | -0.18768 | -0.096131 | -0.11902 | -0.14648 | -0.21515 | 0.032043 | 0.009156 | -0.28839 | -0.073242 | 0.004578 | 122.9507 | 122.7676 | 58.6761 | -122.9782 | 122.9187 | 122.8912 | 59.3765 | -123.1018
1037.0156 | 123.0331 | -58.8226 | 63.9999 | 0.16006 | 0.012149 | 0.068037 | 0.070517 | 0.12907 | -0.00071785 | -0.0045139 | 0.20584 | -0.005708 | 0.064478 | 0.060603 | 0.0020722 | -0.0057786 | 63.8947 | 64.0045 | -0.20599 | -59.0424 | 64.0823 | -58.8959 | -58.9645 | -58.7952 | 0.49896 | -59.0927 | 64.0823 | 64.0137 | -58.9737 | -59.0469 | -0.073242 | -0.14191 | 0.082397 | 122.8271 | -0.21973 | -0.077819 | -0.10529 | -0.15106 | -0.2243 | 0.082397 | 0.027466 | -0.27008 | -0.045776 | 0.013733 | 122.905 | 122.7173 | 58.6166 | -122.9645 | 122.905 | 122.8363 | 59.3216 | -123.0469
1038.0156 | 122.9782 | -58.8501 | 64.032 | 0.030365 | 0.01279 | 0.066328 | 0.072012 | 0.128 | 0.00099115 | -0.0043003 | 0.09903 | -0.0035718 | 0.063837 | 0.060816 | 0.004422 | -0.0062058 | 63.9175 | 63.9954 | -0.1831 | -59.0286 | 64.1235 | -58.8593 | -58.9233 | -58.8547 | 0.50812 | -59.1476 | 64.0915 | 64.0411 | -58.9737 | -59.0744 | -0.009155 | -0.073242 | 0.091553 | 122.8455 | -0.17853 | -0.10528 | -0.11444 | -0.1236 | -0.2243 | 0.05951 | -0.004577 | -0.29755 | -0.073242 | 0.009156 | 122.9736 | 122.7676 | 58.667 | -122.9553 | 122.9416 | 122.8912 | 59.3582 | -123.1064
1039.0156 | 123.0606 | -58.8318 | 64.0091 | 0.15244 | 0.010867 | 0.065901 | 0.07009 | 0.12843 | 0.00056395 | -0.0025913 | 0.25925 | -0.0044264 | 0.064051 | 0.059107 | 0.0031402 | -0.0057786 | 63.9175 | 63.9862 | -0.20599 | -59.0378 | 64.0778 | -58.8684 | -58.9691 | -58.7906 | 0.50812 | -59.0698 | 64.0686 | 64.0228 | -58.9783 | -59.0469 | -0.036621 | -0.13733 | 0.068665 | 122.818 | -0.20599 | -0.068665 | -0.091552 | -0.14648 | -0.21515 | 0.05951 | 0.041199 | -0.23804 | -0.022888 | 0.013733 | 122.9095 | 122.7493 | 58.6258 | -122.9782 | 122.9004 | 122.8546 | 59.3399 | -123.056
1040.0469 | 123.0927 | -58.7677 | 63.9771 | 0.13718 | 0.013644 | 0.065687 | 0.070517 | 0.12886 | -0.0013587 | -0.0051547 | 0.25162 | -0.007417 | 0.062128 | 0.060389 | 0.0024994 | -0.006633 | 63.9999 | 64.1052 | -0.1236 | -58.9737 | 64.0503 | -58.8409 | -58.9096 | -58.7082 | 0.58594 | -58.992 | 64.0503 | 63.9908 | -58.9645 | -59.0195 | -0.073242 | -0.14191 | 0.073242 | 122.8729 | -0.20599 | -0.064087 | 0.022888 | -0.19684 | -0.25177 | 0.073242 | 0.059509 | -0.2243 | 0.027466 | 0.013733 | 122.818 | 122.7676 | 58.6441 | -122.8867 | 122.818 | 122.7585 | 59.3536 | -122.9965
1041.0156 | 123.0743 | -58.8135 | 64.0091 | 0.17532 | 0.010653 | 0.067396 | 0.067313 | 0.13014 | -0.00029045 | -0.0051547 | 0.26688 | -0.0069898 | 0.065119 | 0.058894 | 0.0042084 | -0.006633 | 63.9175 | 64.0182 | -0.20599 | -59.024 | 64.0823 | -58.8364 | -58.9188 | -58.7448 | 0.49439 | -59.0561 | 64.0778 | 63.9908 | -58.9645 | -59.024 | -0.022888 | -0.10529 | 0.073242 | 122.8317 | -0.21057 | -0.10529 | -0.091552 | -0.15106 | -0.21057 | 0.068665 | 0.068665 | -0.24261 | -0.032043 | -0.01831 | 122.8958 | 122.731 | 58.6075 | -122.9279 | 122.8912 | 122.8043 | 59.3079 | -123.0331
1042.0156 | 123.024 | -58.8364 | 64.032 | 0.5339 | 0.013003 | 0.06825 | 0.071158 | 0.13313 | 0.0016321 | -0.0053683 | 0.14481 | -0.0054944 | 0.062982 | 0.061244 | 0.0039948 | -0.0057786 | 63.9542 | 63.9816 | -0.24261 | -59.0378 | 64.119 | -58.8776 | -58.9325 | -58.8089 | 0.4715 | -59.111 | 64.0961 | 64.0091 | -58.9737 | -59.079 | -0.041198 | -0.09613 | 0.086976 | 122.818 | -0.20142 | -0.10529 | -0.077819 | -0.13733 | -0.24261 | 0.064087 | 0.027466 | -0.27466 | -0.032044 | -0.022888 | 122.9553 | 122.7905 | 58.5938 | -122.9645 | 122.9324 | 122.8455 | 59.3079 | -123.111
1043.0156 | 123.0652 | -58.7769 | 63.9999 | 0.16769 | 0.0089443 | 0.06825 | 0.069449 | 0.13014 | -0.0015723 | -0.0036595 | 0.26688 | -0.0065626 | 0.061914 | 0.059321 | 0.0065582 | -0.0079148 | 63.9954 | 64.1235 | -0.10986 | -58.96 | 64.0366 | -58.8547 | -58.9142 | -58.7631 | 0.82398 | -58.9325 | 64.0411 | 63.9816 | -58.9462 | -59.024 | -0.07782 | -0.13733 | 0.036621 | 122.9004 | -0.18311 | -0.045776 | -0.004578 | -0.16937 | -0.24719 | 0.041199 | 0.013732 | -0.15564 | 0.091553 | -0.018311 | 122.8134 | 122.7722 | 58.667 | -122.9141 | 122.818 | 122.7585 | 59.6008 | -123.024
1044.0156 | 123.0103 | -58.8043 | 64.0732 | 0.32791 | 0.011508 | 0.067396 | 0.07244 | 0.12993 | 0.0031273 | -0.0019505 | 0.19821 | -0.0067762 | 0.062342 | 0.061244 | 0.0029266 | -0.0074876 | 63.9404 | 64.0137 | -0.2243 | -58.9874 | 64.1556 | -58.8318 | -58.9188 | -58.7769 | 0.37079 | -59.0652 | 64.1052 | 64.064 | -58.9508 | -59.0149 | -0.027466 | -0.11444 | 0.082398 | 122.818 | -0.18311 | -0.068665 | -0.13275 | -0.14648 | -0.21057 | 0.032044 | 0.027466 | -0.26093 | -0.050354 | -0.009155 | 122.9599 | 122.7448 | 58.58 | -122.9919 | 122.9095 | 122.8683 | 59.1751 | -123.0881
1045.0156 | 123.111 | -58.7036 | 64.0869 | 0.16006 | 0.0093717 | 0.066114 | 0.069663 | 0.12993 | -0.0034949 | -0.0045139 | 0.65598 | -0.0050672 | 0.061487 | 0.05868 | 0.0024994 | -0.006633 | 64.0686 | 64.2014 | -0.10986 | -58.8638 | 64.0961 | -58.786 | -58.873 | -58.6533 | 0.14648 | -58.9233 | 64.1052 | 64.0732 | -58.8593 | -58.9508 | -0.082398 | -0.16937 | 0.009155 | 122.905 | -0.16022 | 0.009155 | -0.01831 | -0.15564 | -0.24719 | 0.018311 | 0.050354 | -0.21973 | 0.027466 | -0.013733 | 122.7997 | 122.7722 | 58.5938 | -122.9599 | 122.8088 | 122.7768 | 58.8501 | -123.0377
1046.0156 | 123.0011 | -58.7448 | 64.0869 | 0.12955 | 0.010867 | 0.065473 | 0.07244 | 0.13099 | 0.0012047 | -0.0043003 | 0.25162 | -0.0052808 | 0.065119 | 0.058894 | 0.0022858 | -0.0072738 | 63.9999 | 64.0457 | -0.21057 | -58.9645 | 64.1785 | -58.8089 | -58.8684 | -58.7082 | 0 | -59.0286 | 64.1327 | 64.0869 | -58.9142 | -58.9645 | -0.064087 | -0.1236 | 0.091553 | 122.7905 | -0.21973 | -0.096131 | -0.086975 | -0.16937 | -0.21973 | 0.045776 | 0.036621 | -0.28381 | -0.064086 | 0 | 122.9233 | 122.7448 | 58.5342 | -122.9553 | 122.8775 | 122.8317 | 58.7448 | -123.0515
1047.0156 | 123.1247 | -58.699 | 64.0823 | 0.16006 | 0.0087307 | 0.064832 | 0.066885 | 0.13121 | -0.0037085 | -0.0043003 | 0.41183 | -0.005708 | 0.063196 | 0.061457 | 0.0037812 | -0.0091966 | 64.032 | 64.2426 | -0.086975 | -58.8638 | 64.1281 | -58.7311 | -58.8318 | -58.6121 | 0.11444 | -58.9142 | 64.119 | 64.0457 | -58.8821 | -58.9462 | -0.032043 | -0.13275 | 0.045777 | 122.9416 | -0.16479 | -0.032044 | -0.050354 | -0.1831 | -0.24719 | 0.036622 | 0.086975 | -0.21515 | 0.032043 | -0.036621 | 122.8271 | 122.731 | 58.6121 | -122.9141 | 122.818 | 122.7448 | 58.8135 | -123.0286
1048.1094 | 123.0698 | -58.6853 | 64.1098 | 0.50339 | 0.0076627 | 0.069959 | 0.068808 | 0.12993 | -0.0024269 | -0.0049411 | 0.32791 | -0.0084852 | 0.062982 | 0.060816 | 0.0029266 | -0.0081284 | 64.1235 | 64.2014 | -0.15106 | -58.8547 | 64.151 | -58.7402 | -58.8043 | -58.5938 | 0.10529 | -58.8913 | 64.1602 | 64.0778 | -58.8409 | -58.9554 | -0.054931 | -0.11902 | 0.041199 | 122.8867 | -0.16937 | -0.050354 | 0.013733 | -0.15564 | -0.27008 | 0.050354 | 0.091553 | -0.20599 | 0.064087 | -0.032043 | 122.8363 | 122.8088 | 58.5342 | -122.9141 | 122.8455 | 122.7631 | 58.7906 | -123.0652
1049.125 | 123.0377 | -58.6716 | 64.1556 | -0.14511 | 0.0087307 | 0.069746 | 0.066672 | 0.12993 | 0.00035035 | -0.0036595 | -0.17563 | -0.0054944 | 0.063623 | 0.061885 | 0.0048492 | -0.0072738 | 64.0594 | 64.1556 | -0.15106 | -58.8913 | 64.2242 | -58.7448 | -58.8318 | -58.6533 | 0.10986 | -58.9417 | 64.2288 | 64.1647 | -58.8455 | -58.9325 | -0.073242 | -0.16022 | 0.068664 | 122.8271 | -0.21973 | -0.059509 | -0.096131 | -0.17395 | -0.26093 | 0.073242 | 0.018311 | -0.27008 | -0.009155 | 0.009155 | 122.8958 | 122.731 | 58.5205 | -122.9874 | 122.9004 | 122.8363 | 58.7814 | -123.0881
1050.4688 | 123.0423 | -58.7402 | 64.1235 | -0.19852 | 0.0097989 | 0.067396 | 0.07009 | 0.13228 | 0.00077755 | -0.0038731 | -0.16037 | -0.0072034 | 0.06341 | 0.058467 | 0.0042084 | -0.0070602 | 64.0137 | 64.1602 | -0.15106 | -58.9005 | 64.1922 | -58.7631 | -58.8684 | -58.6899 | 0.60425 | -58.9783 | 64.1647 | 64.1006 | -58.8867 | -58.9737 | -0.022889 | -0.12817 | 0.068665 | 122.9004 | -0.16022 | -0.032044 | -0.10986 | -0.14648 | -0.23346 | 0.041199 | 0.050354 | -0.23804 | -0.004577 | -0.022888 | 122.9324 | 122.7539 | 58.5892 | -122.9919 | 122.905 | 122.8409 | 59.3445 | -123.0972
1052.0156 | 122.9736 | -58.6533 | 64.1922 | -0.11459 | 0.0031765 | 0.072309 | 0.067313 | 0.12928 | -0.0079811 | -0.0045139 | -0.023041 | -0.0086988 | 0.06106 | 0.058467 | 0.00079042 | -0.0072738 | 64.0961 | 64.3295 | -0.050354 | -58.8272 | 64.1785 | -58.7219 | -58.7906 | -58.548 | 0.19684 | -58.8181 | 64.1693 | 64.0961 | -58.8089 | -58.905 | -0.068665 | -0.13733 | -0.013733 | 122.9828 | -0.17395 | -0.036621 | -0.096131 | -0.15564 | -0.25177 | -0.022888 | 0.10528 | -0.16479 | 0.086975 | -0.096131 | 122.8317 | 122.7493 | 58.6029 | -122.9828 | 122.8226 | 122.7493 | 58.8501 | -123.0972
1052.6562 | 123.0789 | -58.6441 | 64.151 | -0.15274 | 0.0016813 | 0.067396 | 0.06539 | 0.12779 | -0.0075537 | -0.0055821 | 0.015106 | -0.0078442 | 0.062342 | 0.060816 | 0.0031402 | -0.0079148 | 64.1693 | 64.2014 | -0.091553 | -58.786 | 64.1739 | -58.7219 | -58.7814 | -58.5846 | 0.20142 | -58.8318 | 64.2197 | 64.1144 | -58.8135 | -58.8821 | -0.07782 | -0.13733 | 0.022888 | 122.8455 | -0.14191 | -0.004578 | 0.018311 | -0.16937 | -0.23804 | 0.068665 | 0.059509 | -0.18768 | 0.050354 | -0.036621 | 122.818 | 122.8134 | 58.5526 | -122.9324 | 122.8638 | 122.7585 | 58.8455 | -123.0331
1054.6094 | 122.9553 | -58.6899 | 64.1693 | 0.12192 | 0.012362 | 0.06825 | 0.071158 | 0.13099 | 0.0033411 | -0.0028049 | 0.060883 | -0.0059216 | 0.064264 | 0.059962 | 0.0057038 | -0.0089828 | 64.0366 | 64.1144 | -0.25177 | -58.905 | 64.2517 | -58.7357 | -58.8226 | -58.7036 | -0.068665 | -59.0332 | 64.2288 | 64.1098 | -58.8547 | -58.9462 | -0.045777 | -0.13275 | 0.082397 | 122.8043 | -0.21515 | -0.082397 | -0.13275 | -0.16479 | -0.25635 | 0.059509 | -0.013733 | -0.34332 | -0.086975 | -0.05951 | 122.9416 | 122.7264 | 58.4381 | -122.9919 | 122.9187 | 122.7997 | 58.6212 | -123.1155
1055.75 | 123.1567 | -58.6121 | 64.1602 | -0.15274 | 0.0070217 | 0.068891 | 0.067954 | 0.12736 | -0.0043495 | -0.0060093 | -1.9991 | -0.0052808 | 0.06106 | 0.058039 | 0.0018584 | -0.0053512 | 64.1693 | 64.3707 | -0.054932 | -58.7723 | 64.2334 | -58.7036 | -58.7631 | -58.5297 | 0.013733 | -58.7997 | 64.1968 | 64.1098 | -58.7952 | -58.8593 | -0.091552 | -0.15106 | 0.073242 | 122.9828 | -0.16022 | -0.009155 | 0.009156 | -0.18311 | -0.24719 | 0.036621 | 0.082398 | -0.18768 | 0.059509 | -0.050354 | 122.8455 | 122.7814 | 58.5571 | -122.9233 | 122.8088 | 122.7219 | 58.6258 | -123.0194
1056.4531 | 123.143 | -58.6212 | 64.1464 | -0.023041 | 0.0040311 | 0.067182 | 0.070303 | 0.13121 | -0.0037085 | -0.0047275 | 0.015106 | -0.0065626 | 0.061701 | 0.058467 | 0.002713 | -0.0072738 | 64.1144 | 64.3021 | -0.086975 | -58.8226 | 64.238 | -58.6853 | -58.7814 | -58.5297 | 0.16022 | -58.7997 | 64.1739 | 64.1144 | -58.7814 | -58.8638 | -0.064087 | -0.16022 | 0.091553 | 122.9233 | -0.20142 | -0.041199 | -0.032043 | -0.16022 | -0.24262 | 0.027466 | 0.091553 | -0.17853 | 0.064087 | -0.032043 | 122.8592 | 122.7356 | 58.5342 | -122.9279 | 122.7951 | 122.7356 | 58.7814 | -123.0103
1060.9375 | 123.0011 | -58.6899 | 64.1785 | 0.28213 | 0.0057401 | 0.068891 | 0.069876 | 0.13206 | 0.00013675 | -0.0045139 | -0.18326 | -0.0076306 | 0.064051 | 0.059748 | 0.004422 | -0.0072738 | 64.0549 | 64.1693 | -0.19226 | -58.8547 | 64.2517 | -58.7448 | -58.8135 | -58.6441 | 0.13275 | -58.96 | 64.2563 | 64.1602 | -58.8364 | -58.9096 | -0.054932 | -0.1236 | 0.073242 | 122.8592 | -0.16479 | -0.041198 | -0.1236 | -0.14648 | -0.21973 | 0.07782 | 0.045776 | -0.27008 | -0.050354 | -0.018311 | 122.9416 | 122.7448 | 58.4976 | -122.9919 | 122.9462 | 122.85 | 58.8226 | -123.0881
1061.5781 | 123.143 | -58.5938 | 64.1922 | -0.068817 | 0.0057401 | 0.068678 | 0.069022 | 0.12779 | -0.0060585 | -0.0045139 | -0.023041 | -0.0050672 | 0.061701 | 0.058253 | -0.00049138 | -0.0070602 | 64.1693 | 64.3387 | -0.068665 | -58.7814 | 64.2563 | -58.6624 | -58.7357 | -58.4564 | 0.25177 | -58.7494 | 64.2059 | 64.1281 | -58.7448 | -58.8272 | -0.068665 | -0.14191 | 0.064087 | 122.9324 | -0.18768 | -0.045776 | -0.022888 | -0.15106 | -0.23346 | 0.013733 | 0.13733 | -0.15564 | 0.077819 | -0.064087 | 122.85 | 122.7631 | 58.5251 | -122.9279 | 122.7997 | 122.7219 | 58.8455 | -123.0194
1062.1406 | 123.0881 | -58.6075 | 64.1556 | 0.19058 | 0.010013 | 0.066328 | 0.068808 | 0.13014 | 0.0024865 | -0.00066866 | 0.21347 | -0.0067762 | 0.061273 | 0.058894 | 0.0052764 | -0.0072738 | 63.9954 | 64.5081 | -0.036621 | -58.786 | 64.2014 | -58.6533 | -58.7311 | -58.4976 | 0.1236 | -58.8409 | 64.2288 | 64.119 | -58.7769 | -58.8776 | -0.045776 | -0.1236 | 0.045776 | 123.1155 | -0.17853 | -0.054932 | -0.16022 | -0.16937 | -0.27008 | 0.073242 | 0.10986 | -0.23346 | 0.036621 | -0.036621 | 122.8088 | 122.6028 | 58.5709 | -122.8867 | 122.8363 | 122.7264 | 58.7311 | -123.0331
1063.0156 | 123.143 | -58.6075 | 64.1693 | -0.19089 | 0.0027493 | 0.069532 | 0.068381 | 0.13078 | -0.00029045 | -0.0040867 | -0.51895 | -0.0084852 | 0.062555 | 0.059535 | 0.0024994 | -0.0081284 | 64.1785 | 64.3341 | -0.054932 | -58.7814 | 64.2242 | -58.6716 | -58.7219 | -58.4564 | 0.24719 | -58.8226 | 64.1968 | 64.1281 | -58.7814 | -58.8226 | -0.064087 | -0.11444 | 0.054931 | 122.9416 | -0.17395 | -0.059509 | 0.009155 | -0.17395 | -0.21515 | 0.027465 | 0.15106 | -0.21515 | 0 | -0.041199 | 122.8317 | 122.7859 | 58.5526 | -122.8912 | 122.8043 | 122.7356 | 58.8547 | -122.9919
1064.0156 | 123.0972 | -58.6258 | 64.1785 | -0.03067 | 0.0044583 | 0.067396 | 0.070303 | 0.12971 | -0.0047767 | -0.0064365 | 0.053253 | -0.007417 | 0.062342 | 0.059535 | 0.0014312 | -0.0085556 | 64.1235 | 64.2838 | -0.16022 | -58.8043 | 64.2563 | -58.6853 | -58.7494 | -58.5068 | 0.19226 | -58.7997 | 64.2197 | 64.1602 | -58.786 | -58.8409 | -0.05951 | -0.1236 | 0.07782 | 122.9095 | -0.17853 | -0.054931 | -0.054932 | -0.16022 | -0.21515 | 0.041199 | 0.11902 | -0.17395 | 0.041198 | -0.018311 | 122.8821 | 122.7493 | 58.4656 | -122.9279 | 122.8455 | 122.7859 | 58.8181 | -123.0194
1065.0156 | 123.1247 | -58.6258 | 64.1922 | -0.18326 | 0.0061673 | 0.069105 | 0.072226 | 0.13035 | -0.00050425 | -0.0043003 | 0.74753 | -0.0095532 | 0.061273 | 0.058253 | 0.0020722 | -0.0072738 | 64.1785 | 64.6957 | 0.16937 | -58.7814 | 64.2838 | -58.667 | -58.7311 | -58.4702 | 0.27924 | -58.8226 | 64.2288 | 64.1144 | -58.7402 | -58.8501 | -0.041199 | -0.10529 | 0.091552 | 123.3215 | -0.15564 | -0.050354 | -0.013733 | -0.11444 | -0.22431 | 0.036621 | 0.15564 | -0.19684 | 0.027466 | -0.07782 | 122.9095 | 122.8043 | 58.7952 | -122.9233 | 122.8546 | 122.7402 | 58.905 | -123.0423
1066.0156 | 122.9919 | -58.6258 | 64.2792 | -2.0601 | 0.011081 | 0.066969 | 0.069235 | 0.12907 | 0.0029137 | -0.0021641 | -0.19089 | -0.0061352 | 0.061701 | 0.059321 | 0.0046356 | -0.008342 | 64.1006 | 64.2609 | -0.19684 | -58.8181 | 64.3433 | -58.7036 | -58.7585 | -58.5342 | 0.14191 | -58.8821 | 64.3295 | 64.1968 | -58.7723 | -58.873 | -0.07782 | -0.13275 | 0.064087 | 122.8867 | -0.19226 | -0.059509 | -0.17853 | -0.14648 | -0.24719 | 0.050354 | 0.091552 | -0.25635 | -0.009155 | -0.082398 | 122.9691 | 122.7264 | 58.429 | -123.0377 | 122.9553 | 122.8226 | 58.7677 | -123.1522
1067.0156 | 123.0606 | -58.548 | 64.2654 | -0.17563 | 0.0063809 | 0.06825 | 0.070944 | 0.12715 | -0.0013587 | -0.0040867 | -0.19089 | -0.0069898 | 0.061487 | 0.060816 | 0.0029266 | -0.0079148 | 64.2288 | 64.3936 | -0.10071 | -58.7173 | 64.2929 | -58.6258 | -58.6853 | -58.4564 | 0.13275 | -58.7769 | 64.2929 | 64.2151 | -58.7448 | -58.7997 | -0.077819 | -0.13733 | 0.027466 | 122.9416 | -0.16937 | -0.032043 | -0.036621 | -0.19684 | -0.25177 | 0.027466 | 0.091553 | -0.22888 | 0.022889 | -0.050354 | 122.8409 | 122.7768 | 58.4473 | -122.9507 | 122.8409 | 122.7631 | 58.6807 | -123.0652
1068.0156 | 123.0972 | -58.548 | 64.2609 | -0.0077822 | 0.0027493 | 0.067823 | 0.067526 | 0.13014 | -0.0043495 | -0.0064365 | 0.037995 | -0.0095532 | 0.06106 | 0.060603 | 0.0022858 | -0.0062058 | 64.2059 | 64.3707 | -0.19684 | -58.7311 | 64.357 | -58.6212 | -58.6624 | -58.4244 | 0.082397 | -58.754 | 64.2929 | 64.2105 | -58.6853 | -58.7814 | -0.073242 | -0.11444 | 0.096131 | 122.9187 | -0.1831 | -0.068664 | -0.054931 | -0.13733 | -0.23346 | 0.032044 | 0.1236 | -0.20599 | 0.027466 | -0.050354 | 122.905 | 122.7539 | 58.3511 | -122.9233 | 122.8409 | 122.7585 | 58.6304 | -123.0423
1069.0156 | 123.1155 | -58.5205 | 64.2654 | -0.19089 | 0.0063809 | 0.069959 | 0.068594 | 0.12758 | -0.0011451 | -0.0057957 | -0.56473 | -0.0093396 | 0.062982 | 0.058467 | 0.0014312 | -0.0089828 | 64.4669 | 64.5538 | -0.12817 | -58.8913 | 64.3204 | -58.6121 | -58.6716 | -58.4015 | 0.16479 | -58.7082 | 64.2746 | 64.1922 | -58.6899 | -58.7814 | -0.091553 | -0.15106 | 0.054932 | 123.0743 | -0.37079 | -0.21973 | 0.20142 | -0.16937 | -0.26093 | 0.009155 | 0.11902 | -0.18768 | 0.073242 | -0.073242 | 122.8409 | 122.9874 | 58.3923 | -122.937 | 122.7951 | 122.7127 | 58.6853 | -123.0469
1070.0156 | 123.1155 | -58.5434 | 64.2471 | -0.091705 | 0.0057401 | 0.069319 | 0.070517 | 0.12971 | -0.0049903 | -0.0040867 | -0.0077819 | -0.010835 | 0.059778 | 0.059535 | 0.0031402 | -0.0072738 | 64.2197 | 64.4257 | -0.12817 | -58.7082 | 64.3204 | -58.6075 | -58.6899 | -58.374 | 0.17395 | -58.7036 | 64.3158 | 64.1785 | -58.6716 | -58.7631 | -0.064087 | -0.14648 | 0.073243 | 122.9691 | -0.16479 | -0.018311 | -0.027465 | -0.12817 | -0.21973 | 0.068665 | 0.16937 | -0.16022 | 0.05951 | -0.068664 | 122.8638 | 122.7631 | 58.4152 | -122.937 | 122.8592 | 122.7219 | 58.7173 | -123.0103
1071.0156 | 123.0469 | -58.5754 | 64.2792 | -0.18326 | 0.0057401 | 0.066755 | 0.067526 | 0.1295 | -0.0015723 | -0.0053683 | -0.15274 | -0.0086988 | 0.063837 | 0.059107 | 0.0050628 | -0.0079148 | 64.2242 | 64.3982 | -0.10986 | -58.7265 | 64.2883 | -58.6212 | -58.699 | -58.4381 | 0.16937 | -58.7906 | 64.2975 | 64.1739 | -58.7265 | -58.8181 | -0.045777 | -0.1236 | 0.009155 | 122.9736 | -0.15106 | -0.027465 | -0.054932 | -0.15106 | -0.24261 | 0.01831 | 0.13733 | -0.21515 | 0.027466 | -0.10529 | 122.8638 | 122.7997 | 58.4656 | -122.9782 | 122.8729 | 122.7493 | 58.7448 | -123.0972
1072.0156 | 123.1155 | -58.5892 | 64.2105 | -0.03067 | 0.0057401 | 0.06825 | 0.069022 | 0.13035 | -0.0024269 | -0.0043003 | 0.037995 | -0.006349 | 0.05871 | 0.059107 | 0.0022858 | -0.0072738 | 64.1876 | 64.3662 | -0.14191 | -58.7723 | 64.2792 | -58.6807 | -58.7082 | -58.4335 | 0.18768 | -58.7494 | 64.2517 | 64.1602 | -58.7494 | -58.8043 | -0.091553 | -0.11902 | 0.068665 | 122.9553 | -0.18311 | -0.064087 | -0.022888 | -0.16022 | -0.21515 | 0.041199 | 0.15564 | -0.16022 | 0.054931 | -0.050354 | 122.8683 | 122.7768 | 58.4473 | -122.9187 | 122.8409 | 122.7493 | 58.7769 | -123.0148
1073.0156 | 123.0652 | -58.5617 | 64.2929 | -0.18326 | 0.0046719 | 0.069319 | 0.069663 | 0.12907 | 0.00077755 | -0.0049411 | -0.18326 | -0.0069898 | 0.06106 | 0.058253 | 0.0031402 | -0.0087692 | 64.2242 | 64.4119 | -0.13275 | -58.7219 | 64.3066 | -58.6075 | -58.699 | -58.4564 | 0.17853 | -58.7906 | 64.3112 | 64.1968 | -58.7311 | -58.7997 | -0.045776 | -0.13733 | 0.013733 | 122.9736 | -0.16022 | -0.022888 | -0.068665 | -0.16937 | -0.23804 | 0.01831 | 0.10529 | -0.22888 | 0.009156 | -0.096131 | 122.8683 | 122.7859 | 58.429 | -122.9919 | 122.8729 | 122.7585 | 58.7402 | -123.0927
1074.0156 | 123.1155 | -58.5709 | 64.2242 | -0.091705 | 0.0023221 | 0.06761 | 0.069235 | 0.12993 | 0.00035035 | -0.0057957 | -0.015411 | -0.0082716 | 0.060846 | 0.05868 | 0.0022858 | -0.0077012 | 64.1785 | 64.3799 | -0.1831 | -58.754 | 64.2792 | -58.6624 | -58.699 | -58.4473 | 0.19684 | -58.7402 | 64.2517 | 64.1647 | -58.7448 | -58.8318 | -0.091553 | -0.12817 | 0.054932 | 122.9507 | -0.18311 | -0.054931 | -0.045776 | -0.17395 | -0.26093 | 0.027466 | 0.1236 | -0.16937 | 0.091553 | -0.059509 | 122.85 | 122.7493 | 58.3878 | -122.9233 | 122.8226 | 122.7356 | 58.7677 | -123.056
1075.0156 | 123.0743 | -58.5754 | 64.2471 | -0.18326 | 0.0076627 | 0.066541 | 0.070303 | 0.13206 | -0.0015723 | -0.0049411 | -0.13748 | -0.0072034 | 0.059778 | 0.057826 | 0.0024994 | -0.0077012 | 64.2151 | 64.4028 | -0.15106 | -58.7357 | 64.2975 | -58.6624 | -58.699 | -58.4518 | 0.21515 | -58.8043 | 64.2975 | 64.1693 | -58.7311 | -58.7997 | -0.086976 | -0.1236 | 0.050354 | 122.9782 | -0.16022 | -0.036621 | -0.032043 | -0.15564 | -0.2243 | 0.050354 | 0.1236 | -0.22888 | -0.004577 | -0.077819 | 122.8729 | 122.7905 | 58.4244 | -122.9462 | 122.8729 | 122.7448 | 58.7906 | -123.0469
1076.0156 | 123.111 | -58.58 | 64.2471 | -0.20615 | 0.0048855 | 0.069105 | 0.069235 | 0.12971 | -0.00050425 | -0.0032321 | -0.11459 | -0.0097668 | 0.057428 | 0.060389 | 0.008908 | -0.0070602 | 64.2471 | 64.4394 | -0.14648 | -58.7311 | 64.3021 | -58.6304 | -58.7173 | -58.5663 | 0.40741 | -58.7997 | 64.2426 | 64.1464 | -58.7585 | -58.8043 | -0.050354 | -0.13733 | 0.054932 | 123.0194 | -0.15106 | -0.013733 | 0 | -0.17853 | -0.2243 | -0.004577 | 0.013733 | -0.21973 | 0.004577 | -0.10071 | 122.8821 | 122.8271 | 58.4335 | -122.9645 | 122.8226 | 122.7264 | 58.9874 | -123.0515
1077.0156 | 123.0057 | -58.6029 | 64.3112 | -0.22903 | 0.0080899 | 0.069532 | 0.070303 | 0.12864 | 0.0014185 | -0.0038731 | -0.168 | -0.005708 | 0.062982 | 0.059321 | 0.0031402 | -0.0094102 | 64.2014 | 64.357 | -0.2243 | -58.7494 | 64.3387 | -58.6441 | -58.699 | -58.5159 | 0.11902 | -58.8364 | 64.3524 | 64.2288 | -58.7448 | -58.8181 | -0.041199 | -0.096131 | 0.027466 | 122.9599 | -0.14648 | -0.050354 | -0.10986 | -0.14191 | -0.21515 | 0.041199 | 0.086975 | -0.23346 | -0.018311 | -0.082397 | 122.9416 | 122.8043 | 58.3786 | -123.0103 | 122.9553 | 122.8317 | 58.7219 | -123.1293
1078.0156 | 123.0789 | -58.5846 | 64.2609 | -0.22903 | 0.0057401 | 0.066541 | 0.069235 | 0.1295 | -0.00093145 | -0.0038731 | -0.168 | -0.0065626 | 0.062128 | 0.059748 | 0.0037812 | -0.0070602 | 64.2059 | 64.4302 | -0.1831 | -58.7082 | 64.3021 | -58.6304 | -58.7082 | -58.4381 | 0.18768 | -58.7585 | 64.3021 | 64.1785 | -58.7219 | -58.7906 | -0.045776 | -0.1236 | 0.041199 | 123.0148 | -0.1236 | 0 | -0.054931 | -0.13733 | -0.20599 | 0.041199 | 0.14648 | -0.17395 | 0.032043 | -0.082397 | 122.8867 | 122.7905 | 58.4015 | -122.9691 | 122.8867 | 122.7631 | 58.7723 | -123.0515
1079.0156 | 122.9645 | -58.6212 | 64.2426 | -0.17563 | 0.0063809 | 0.066969 | 0.073081 | 0.13035 | -0.00029045 | -0.0036595 | -0.18326 | -0.0067762 | 0.063837 | 0.057398 | 0.0033538 | -0.0068466 | 64.1556 | 64.3204 | -0.19226 | -58.7814 | 64.2929 | -58.6395 | -58.7036 | -58.5205 | 0.14648 | -58.8776 | 64.3112 | 64.183 | -58.7677 | -58.8455 | -0.01831 | -0.082397 | 0.050354 | 122.9416 | -0.16022 | -0.07782 | -0.086975 | -0.14648 | -0.2243 | 0.068664 | 0.10071 | -0.25635 | -0.032043 | -0.05951 | 122.9141 | 122.7768 | 58.429 | -122.9462 | 122.9324 | 122.8043 | 58.7677 | -123.0881
1080.0156 | 123.1064 | -58.5846 | 64.2288 | -0.045929 | 0.0044583 | 0.067823 | 0.068594 | 0.12779 | -0.0026405 | -0.0034457 | -0.10696 | -0.0086988 | 0.060633 | 0.058467 | -0.00049138 | -0.0089828 | 64.2197 | 64.444 | -0.11444 | -58.7173 | 64.2792 | -58.6441 | -58.6945 | -58.4427 | 0.21057 | -58.7494 | 64.2426 | 64.1693 | -58.7219 | -58.7997 | -0.059509 | -0.10986 | 0.050354 | 123.0286 | -0.13275 | -0.022888 | -0.009155 | -0.13733 | -0.21515 | 0.013733 | 0.14191 | -0.16479 | 0.050354 | -0.059509 | 122.8638 | 122.8043 | 58.4702 | -122.9233 | 122.8271 | 122.7539 | 58.7952 | -123.0286
1081.0156 | 122.9645 | -58.6304 | 64.27 | -0.25192 | 0.0080899 | 0.067396 | 0.072653 | 0.12864 | 0.00035035 | -0.0049411 | -0.19852 | -0.0059216 | 0.062342 | 0.058253 | 0.0012176 | -0.0064194 | 64.1327 | 64.2654 | -0.2243 | -58.8089 | 64.3387 | -58.6716 | -58.7402 | -58.4793 | -0.12817 | -58.9554 | 64.3204 | 64.1739 | -58.786 | -58.8455 | -0.041199 | -0.10986 | 0.068664 | 122.8958 | -0.17853 | -0.068665 | -0.13733 | -0.15564 | -0.21515 | 0.050354 | 0.15106 | -0.32501 | -0.10986 | -0.096131 | 122.9691 | 122.7631 | 58.4061 | -123.0103 | 122.9507 | 122.8043 | 58.5022 | -123.1155
1082.0156 | 123.0881 | -58.5754 | 64.2563 | -0.00015269 | 0.0061673 | 0.069959 | 0.068381 | 0.12822 | -0.0034949 | -0.0030185 | -0.076446 | -0.0082716 | 0.060633 | 0.058039 | 0.0016448 | -0.0057786 | 64.2151 | 64.4302 | -0.11444 | -58.7311 | 64.2838 | -58.6166 | -58.7036 | -58.4381 | 0.23804 | -58.754 | 64.2563 | 64.183 | -58.7448 | -58.8272 | -0.041199 | -0.12817 | 0.027465 | 123.0057 | -0.15564 | -0.027466 | -0.041199 | -0.16937 | -0.25177 | 0 | 0.13733 | -0.17853 | 0.073242 | -0.073243 | 122.8592 | 122.7905 | 58.461 | -122.9599 | 122.8317 | 122.7585 | 58.8135 | -123.0835
1083.0156 | 123.0469 | -58.6395 | 64.2334 | -0.18326 | 0.013217 | 0.067396 | 0.070517 | 0.13121 | 0.0056909 | -0.0021641 | -0.19852 | -0.005708 | 0.062555 | 0.05868 | 0.0050628 | -0.0087692 | 64.1373 | 64.2654 | -0.23346 | -58.8089 | 64.3112 | -58.7082 | -58.7769 | -58.5342 | 0.21515 | -58.8776 | 64.2883 | 64.1647 | -58.786 | -58.9005 | -0.068665 | -0.13733 | 0.07782 | 122.905 | -0.16937 | -0.032044 | -0.09613 | -0.14649 | -0.26093 | 0.054932 | 0.10528 | -0.23804 | 0.022889 | -0.068664 | 122.9507 | 122.7768 | 58.4061 | -123.0103 | 122.9279 | 122.8043 | 58.8547 | -123.1338
1084.0156 | 123.1064 | -58.5846 | 64.2288 | -0.12222 | 0.0012539 | 0.068678 | 0.063254 | 0.12971 | -0.0054175 | -0.0043003 | -0.00015237 | -0.0076306 | 0.061273 | 0.058253 | 0.00079042 | -0.0053512 | 64.2517 | 64.2563 | -0.17853 | -58.7448 | 64.2471 | -58.6624 | -58.7219 | -58.461 | 0.33417 | -58.7723 | 64.2426 | 64.1327 | -58.754 | -58.8043 | -0.07782 | -0.13733 | 0.01831 | 122.8409 | -0.16022 | -0.022888 | 0.022888 | -0.16937 | -0.21973 | 0.013733 | 0.1236 | -0.18768 | 0.032043 | -0.096131 | 122.8317 | 122.8363 | 58.4061 | -122.9507 | 122.8271 | 122.7173 | 58.9188 | -123.0331
1085.0156 | 123.0011 | -58.6441 | 64.2471 | -0.20615 | 0.0080899 | 0.06825 | 0.071585 | 0.13057 | -0.00093145 | -0.0038731 | -0.17563 | -0.0059216 | 0.063196 | 0.058039 | 0.0022858 | -0.0059922 | 64.0823 | 64.2792 | -0.22888 | -58.8226 | 64.2975 | -58.7128 | -58.7723 | -58.5526 | 0.19226 | -58.8959 | 64.2929 | 64.1693 | -58.7952 | -58.8684 | -0.068665 | -0.12817 | 0.050354 | 122.9233 | -0.17853 | -0.050354 | -0.16479 | -0.15106 | -0.2243 | 0.045777 | 0.091553 | -0.25177 | -0.027466 | -0.077819 | 122.9416 | 122.7264 | 58.4152 | -123.0194 | 122.937 | 122.8134 | 58.8364 | -123.1155
1086.0156 | 123.1201 | -58.5983 | 64.2288 | -0.20615 | 0.0027493 | 0.068891 | 0.069663 | 0.12886 | -0.0039221 | -0.010709 | -0.4808 | -0.0093396 | 0.059992 | 0.059107 | 0.0022858 | -0.004924 | 64.4073 | 64.4897 | -0.19226 | -58.9233 | 64.2609 | -58.6807 | -58.7311 | -58.4427 | 0.28839 | -58.7814 | 64.2197 | 64.151 | -58.7631 | -58.8226 | -0.082397 | -0.13275 | 0.032043 | 123.0881 | -0.32501 | -0.19226 | 0.17853 | -0.16479 | -0.2243 | -0.009155 | 0.15564 | -0.1831 | 0.041199 | -0.07782 | 122.8592 | 123.0057 | 58.4061 | -122.9599 | 122.818 | 122.7493 | 58.8867 | -123.0515
1087.0156 | 123.0057 | -58.6533 | 64.2471 | -0.25192 | 0.0074491 | 0.069105 | 0.070944 | 0.13078 | 0.0012047 | -0.0030185 | -0.168 | -0.0035718 | 0.062342 | 0.059321 | 0.0018584 | -0.0079148 | 64.0915 | 64.2929 | -0.1831 | -58.8272 | 64.3158 | -58.6899 | -58.7906 | -58.58 | 0.15564 | -58.8821 | 64.2929 | 64.1647 | -58.7952 | -58.8913 | -0.036621 | -0.13733 | 0.068665 | 122.9462 | -0.17395 | -0.036621 | -0.15564 | -0.14191 | -0.23804 | 0.045777 | 0.073242 | -0.22888 | 0.009155 | -0.082397 | 122.9691 | 122.7448 | 58.4702 | -123.0377 | 122.9462 | 122.818 | 58.8089 | -123.1384
1088.0156 | 123.0377 | -58.6899 | 64.2014 | -0.22141 | 0.01279 | 0.068037 | 0.067954 | 0.13035 | 0.0044091 | -0.0013095 | -0.038299 | -0.0061352 | 0.063623 | 0.060603 | 0.0046356 | -0.0085556 | 64.1327 | 64.2654 | -0.23346 | -58.8364 | 64.2792 | -58.7219 | -58.7677 | -58.5617 | 0.33875 | -58.9279 | 64.2517 | 64.1235 | -58.8043 | -58.8913 | -0.032044 | -0.07782 | 0.07782 | 122.9553 | -0.14648 | -0.068665 | -0.068665 | -0.11444 | -0.20142 | 0.050354 | 0.12817 | -0.23804 | -0.036621 | -0.07782 | 122.9691 | 122.8226 | 58.4564 | -122.9691 | 122.9416 | 122.8134 | 59.0286 | -123.0927
1089.0156 | 123.0057 | -58.6853 | 64.2197 | -0.21378 | 0.0093717 | 0.070173 | 0.069876 | 0.13121 | -0.0032813 | -0.0025913 | -0.25955 | -0.0059216 | 0.063196 | 0.060816 | 0.001004 | -0.006633 | 64.0823 | 64.2517 | -0.19226 | -58.8593 | 64.238 | -58.7357 | -58.7952 | -58.58 | 0.19226 | -58.9188 | 64.2746 | 64.1693 | -58.8181 | -58.873 | -0.050354 | -0.10986 | 0.01831 | 122.937 | -0.17395 | -0.064087 | -0.13733 | -0.13275 | -0.18768 | 0.054931 | 0.10529 | -0.23346 | -0.045776 | -0.050354 | 122.9233 | 122.7676 | 58.493 | -123.0148 | 122.9599 | 122.8546 | 58.8776 | -123.0927
1090.0156 | 123.0835 | -58.6395 | 64.1968 | -0.18326 | 0.0055265 | 0.068464 | 0.066885 | 0.13121 | -0.0041357 | -0.0030185 | -0.14511 | -0.0059216 | 0.059351 | 0.05868 | 0.0020722 | -0.0081284 | 64.1235 | 64.3387 | -0.12817 | -58.8043 | 64.2242 | -58.6853 | -58.7769 | -58.548 | 0.32959 | -58.8593 | 64.2059 | 64.1327 | -58.8089 | -58.8455 | -0.045777 | -0.13733 | 0.027466 | 122.9782 | -0.1648 | -0.027466 | -0.073242 | -0.16937 | -0.20599 | 0.009156 | 0.091552 | -0.21973 | -0.013733 | -0.064087 | 122.8638 | 122.7631 | 58.5114 | -122.9736 | 122.8455 | 122.7722 | 58.9691 | -123.0423
1091.0156 | 122.9919 | -58.6807 | 64.2151 | -0.22141 | 0.0089443 | 0.064832 | 0.071799 | 0.13099 | 0.00035035 | -0.0070773 | -0.36636 | -0.005708 | 0.061487 | 0.059962 | 0.0035674 | -0.0070602 | 64.1739 | 64.2838 | -0.25177 | -58.9691 | 64.3021 | -58.7265 | -58.7814 | -58.58 | 0.15106 | -58.9279 | 64.2838 | 64.1739 | -58.8089 | -58.8913 | -0.045776 | -0.10071 | 0.086975 | 122.9645 | -0.28839 | -0.18768 | -0.041199 | -0.12817 | -0.21057 | 0.068664 | 0.10071 | -0.24719 | -0.036621 | -0.041199 | 122.9828 | 122.8546 | 58.429 | -122.9965 | 122.9645 | 122.8546 | 58.8318 | -123.1064
1092.0156 | 123.0469 | -58.6304 | 64.2105 | -0.18326 | 0.0057401 | 0.068464 | 0.069876 | 0.12629 | -0.00093145 | -0.0023777 | -0.15274 | -0.0054944 | 0.062769 | 0.061244 | 0.0029266 | -0.0062058 | 64.1327 | 64.3433 | -0.10071 | -58.7906 | 64.2609 | -58.6716 | -58.7585 | -58.5022 | 0.26093 | -58.8089 | 64.2471 | 64.1464 | -58.7952 | -58.8684 | -0.041199 | -0.12817 | 0.050354 | 122.9736 | -0.16022 | -0.032043 | -0.07782 | -0.1648 | -0.23804 | 0.036621 | 0.12817 | -0.17853 | 0.059509 | -0.064087 | 122.8912 | 122.7631 | 58.5297 | -122.9691 | 122.8775 | 122.7768 | 58.8913 | -123.0789
1093.0156 | 123.0148 | -58.7402 | 64.1556 | 0.34317 | 0.012576 | 0.066969 | 0.07543 | 0.13185 | 0.0027001 | -2.7856e-05 | 0.16006 | -0.005708 | 0.064905 | 0.059535 | 0.0039948 | -0.0072738 | 64.0503 | 64.1281 | -0.29297 | -58.9142 | 64.2426 | -58.7448 | -58.8181 | -58.6441 | 0.086975 | -58.992 | 64.2059 | 64.0869 | -58.8684 | -58.9417 | -0.004578 | -0.07782 | 0.086975 | 122.8683 | -0.17395 | -0.096131 | -0.10529 | -0.12817 | -0.20142 | 0.050354 | 0.09613 | -0.25177 | -0.050354 | -0.068665 | 122.9828 | 122.7905 | 58.4473 | -122.9736 | 122.9462 | 122.8271 | 58.8272 | -123.0972
1094.0156 | 123.0469 | -58.6807 | 64.151 | -0.15274 | 0.0059537 | 0.067823 | 0.068167 | 0.13078 | -0.0017859 | -0.0015231 | -0.076446 | -0.0078442 | 0.061487 | 0.059748 | 0.0012176 | -0.0064194 | 64.119 | 64.3066 | -0.064087 | -58.8043 | 64.2197 | -58.699 | -58.7814 | -58.5342 | 0.36163 | -58.8455 | 64.2105 | 64.1327 | -58.8135 | -58.8821 | -0.018311 | -0.10071 | 0.068665 | 122.9874 | -0.1236 | -0.022888 | -0.032043 | -0.13275 | -0.20142 | 0.059509 | 0.14648 | -0.16479 | 0.036621 | -0.018311 | 122.9004 | 122.7997 | 58.6166 | -122.9324 | 122.8912 | 122.8134 | 59.0424 | -123.0331
1095.0156 | 123.0148 | -58.7082 | 64.2014 | -0.20615 | 0.011935 | 0.06761 | 0.071799 | 0.12907 | -0.0011451 | -0.0032321 | 0.022736 | -0.00464 | 0.064905 | 0.060816 | 0.0016448 | -0.0051376 | 63.9267 | 64.1098 | -0.16937 | -58.9188 | 64.2288 | -58.7723 | -58.8135 | -58.6441 | 0.33875 | -58.96 | 64.2288 | 64.1556 | -58.8272 | -58.9142 | -0.064087 | -0.10529 | 0.027466 | 122.818 | -0.21057 | -0.10529 | -0.27466 | -0.11902 | -0.20599 | 0.027466 | 0.064087 | -0.25177 | -0.045776 | -0.045776 | 122.937 | 122.6349 | 58.5388 | -123.0148 | 122.937 | 122.8638 | 59.0469 | -123.1155
1096.0156 | 123.0698 | -58.6899 | 64.1693 | -0.19852 | 0.0091581 | 0.070173 | 0.069235 | 0.13014 | -0.0030677 | -0.0023777 | -0.11459 | -0.0082716 | 0.062769 | 0.058467 | 0.0016448 | -0.0072738 | 64.0869 | 64.2975 | -0.073242 | -58.8181 | 64.2014 | -58.7265 | -58.8043 | -58.5709 | 0.43488 | -58.8638 | 64.1693 | 64.119 | -58.8318 | -58.905 | -0.036621 | -0.11444 | 0.032043 | 122.9874 | -0.12817 | -0.013733 | -0.082398 | -0.14191 | -0.21515 | 0 | 0.11902 | -0.17395 | 0.041198 | -0.050354 | 122.8912 | 122.7768 | 58.6166 | -122.9736 | 122.8592 | 122.8088 | 59.1248 | -123.0743
1097.0156 | 123.0698 | -58.7128 | 64.183 | -0.20615 | 0.0091581 | 0.068678 | 0.069235 | 0.1295 | 0.0014185 | -0.0017369 | -0.24429 | -0.0065626 | 0.063837 | 0.059107 | 0.0046356 | -0.0068466 | 64.0503 | 64.1876 | -0.19226 | -58.873 | 64.2654 | -58.7219 | -58.8409 | -58.6029 | 0.34332 | -58.9417 | 64.2242 | 64.119 | -58.8409 | -58.9279 | -0.009155 | -0.12817 | 0.082398 | 122.9004 | -0.16022 | -0.032044 | -0.13275 | -0.12817 | -0.21515 | 0.041199 | 0.10986 | -0.22888 | -0.013733 | -0.064086 | 122.9782 | 122.7631 | 58.5205 | -123.024 | 122.937 | 122.8317 | 59.0561 | -123.111
1098.0156 | 123.024 | -58.7311 | 64.1144 | 0.18295 | 0.012362 | 0.066541 | 0.071372 | 0.1295 | 0.00099115 | -0.0034457 | 0.19821 | -0.005708 | 0.062769 | 0.061457 | 0.00549 | -0.0068466 | 64.0091 | 64.1373 | -0.28381 | -58.9508 | 64.2242 | -58.7814 | -58.8455 | -58.6121 | 0.1236 | -59.0012 | 64.1922 | 64.0869 | -58.8776 | -58.9508 | -0.050354 | -0.11444 | 0.10986 | 122.8683 | -0.21973 | -0.10529 | -0.10529 | -0.14648 | -0.21973 | 0.07782 | 0.11902 | -0.27008 | -0.050354 | -0.027466 | 122.9553 | 122.7402 | 58.4473 | -122.9599 | 122.9233 | 122.818 | 58.8547 | -123.0652
1099.0156 | 123.0515 | -58.786 | 64.1052 | -0.16037 | 0.011935 | 0.068037 | 0.07009 | 0.13121 | -7.6852e-05 | -0.0013095 | -0.168 | -0.0044264 | 0.064264 | 0.059748 | 0.0042084 | -0.0072738 | 63.9908 | 64.1235 | -0.17395 | -58.9325 | 64.2105 | -58.8089 | -58.8776 | -58.667 | 0.27924 | -58.9737 | 64.1876 | 64.0961 | -58.8867 | -58.9691 | -0.022888 | -0.091552 | 0.10528 | 122.9095 | -0.14648 | -0.054932 | -0.11444 | -0.10071 | -0.1831 | 0.082397 | 0.11902 | -0.18768 | -0.004578 | -0.009156 | 122.9965 | 122.7768 | 58.6121 | -122.9828 | 122.9736 | 122.8821 | 59.0652 | -123.0743
1100.0156 | 122.9965 | -58.7677 | 64.1052 | -0.18326 | 0.0087307 | 0.066755 | 0.070731 | 0.13099 | -0.0026405 | -0.0060093 | -0.14511 | -0.0050672 | 0.060205 | 0.060816 | 0.0020722 | -0.005565 | 63.9313 | 64.1098 | -0.15106 | -58.9783 | 64.1647 | -58.8364 | -58.9005 | -58.699 | 0.27924 | -59.0286 | 64.1464 | 64.0732 | -58.9462 | -58.9828 | -0.068665 | -0.13275 | 0.059509 | 122.8775 | -0.21057 | -0.077819 | -0.17395 | -0.17853 | -0.21515 | 0.041198 | 0.068664 | -0.26093 | -0.045776 | -0.032044 | 122.9324 | 122.699 | 58.6166 | -123.0057 | 122.9141 | 122.8409 | 59.0469 | -123.0881
1101.0156 | 123.0377 | -58.7769 | 64.1052 | -0.19852 | 0.011081 | 0.069959 | 0.068381 | 0.1295 | 0.00077755 | -0.0017369 | -0.19089 | -0.005708 | 0.063196 | 0.058039 | 0.0050628 | -0.008342 | 63.9633 | 64.1098 | -0.16479 | -58.9417 | 64.1922 | -58.8089 | -58.905 | -58.6807 | 0.32959 | -59.0332 | 64.1418 | 64.0228 | -58.9462 | -59.0057 | -0.032044 | -0.12817 | 0.086975 | 122.8867 | -0.1648 | -0.036621 | -0.14191 | -0.16937 | -0.22888 | 0.036621 | 0.09613 | -0.25635 | -0.027466 | -0.082398 | 122.9691 | 122.7402 | 58.6121 | -123.0103 | 122.9187 | 122.7997 | 59.1064 | -123.111
1102.0156 | 122.8958 | -58.7402 | 64.1235 | -0.4274 | 0.0093717 | 0.06761 | 0.070731 | 0.13249 | -0.0030677 | -0.0036595 | -0.11459 | -0.0067762 | 0.062342 | 0.05868 | 0.0035674 | -0.0040696 | 63.9587 | 64.1281 | -0.15106 | -58.9737 | 64.1739 | -58.8043 | -58.9005 | -58.6899 | 0.29755 | -59.024 | 64.1922 | 64.0778 | -58.905 | -58.9233 | -0.064087 | -0.16022 | 0.050354 | 122.8683 | -0.23346 | -0.073242 | -0.1648 | -0.16479 | -0.18311 | 0.068665 | 0.050354 | -0.28381 | -0.10071 | -0.045776 | 122.9141 | 122.699 | 58.5892 | -123.024 | 122.9324 | 122.818 | 59.0378 | -123.0469
1103.0156 | 123.024 | -58.7585 | 64.1098 | -0.19852 | 0.010867 | 0.068891 | 0.068808 | 0.13185 | 0.00056395 | -0.0060093 | -0.15274 | -0.0059216 | 0.06341 | 0.059962 | 0.0067718 | -0.0059922 | 64.0045 | 64.1602 | -0.16937 | -58.8959 | 64.1785 | -58.786 | -58.8684 | -58.6441 | 0.33417 | -58.9783 | 64.1693 | 64.0778 | -58.9279 | -58.9783 | -0.027466 | -0.10986 | 0.068665 | 122.9187 | -0.13733 | -0.027466 | -0.10528 | -0.16937 | -0.21973 | 0.05951 | 0.11444 | -0.21973 | 0 | -0.032043 | 122.937 | 122.7631 | 58.5892 | -122.9782 | 122.9279 | 122.8363 | 59.0927 | -123.0881
1104.0156 | 123.0194 | -58.7814 | 64.0961 | -0.13748 | 0.010226 | 0.068464 | 0.069449 | 0.13078 | -0.00093145 | -0.0040867 | -0.099335 | -0.0050672 | 0.064478 | 0.061457 | 0.00549 | -0.0059922 | 63.9404 | 64.0823 | -0.18768 | -58.96 | 64.151 | -58.8409 | -58.9371 | -58.7219 | 0.28839 | -59.0378 | 64.1373 | 64.0823 | -58.905 | -58.992 | -0.059509 | -0.15564 | 0.054932 | 122.8638 | -0.17853 | -0.022888 | -0.15564 | -0.1236 | -0.21057 | 0.041199 | 0.059509 | -0.25635 | -0.045777 | -0.013733 | 122.9324 | 122.7219 | 58.5938 | -123.0331 | 122.9187 | 122.8638 | 59.0698 | -123.0881
1105.0156 | 123.0377 | -58.7631 | 64.0869 | -0.084076 | 0.013003 | 0.06825 | 0.073935 | 0.12822 | 0.0035547 | -0.0023777 | -0.15274 | -0.005708 | 0.063837 | 0.059107 | 0.0042084 | -0.0085556 | 64.0045 | 64.1464 | -0.16022 | -58.992 | 64.151 | -58.8455 | -58.9142 | -58.6533 | 0.26093 | -59.0057 | 64.1327 | 64.0594 | -58.9417 | -59.0103 | -0.082397 | -0.15106 | 0.064087 | 122.9095 | -0.22888 | -0.077819 | -0.082397 | -0.17853 | -0.24719 | 0.045776 | 0.10986 | -0.24261 | 0.004578 | -0.027466 | 122.9141 | 122.7676 | 58.6029 | -123.0011 | 122.8958 | 122.8226 | 59.024 | -123.0972
1106.0156 | 123.024 | -58.8089 | 64.1052 | -0.19852 | 0.0095853 | 0.069532 | 0.070944 | 0.12864 | -0.0013587 | -0.0045139 | -0.19089 | -0.0065626 | 0.064264 | 0.059535 | 0.0029266 | -0.0070602 | 63.9404 | 64.0823 | -0.1831 | -58.9691 | 64.1281 | -58.8318 | -58.9005 | -58.7173 | 0.29297 | -59.0424 | 64.1281 | 64.0732 | -58.9417 | -58.992 | -0.022888 | -0.091553 | 0.022888 | 122.8912 | -0.16022 | -0.068664 | -0.1648 | -0.13275 | -0.18311 | 0.022888 | 0.091553 | -0.23346 | -0.050354 | -0.032044 | 122.937 | 122.7493 | 58.6258 | -123.0057 | 122.937 | 122.8821 | 59.1019 | -123.0972
1107.0156 | 123.0377 | -58.7128 | 64.0961 | -0.10696 | 0.015567 | 0.06825 | 0.071799 | 0.13206 | 0.0012047 | -0.0010959 | -0.045929 | -0.0037854 | 0.065119 | 0.060389 | 0.0050628 | -0.0059922 | 63.8992 | 64.1327 | -0.20599 | -58.8776 | 64.1602 | -58.7997 | -58.8684 | -58.6166 | 0.28381 | -58.9783 | 64.1739 | 64.1052 | -58.8547 | -58.9462 | -0.086975 | -0.15564 | 0.064087 | 122.8455 | -0.16479 | -0.009155 | -0.19684 | -0.14191 | -0.23346 | 0.07782 | 0.096131 | -0.2655 | -0.032043 | 0.009156 | 122.8729 | 122.612 | 58.5068 | -122.9645 | 122.8867 | 122.818 | 58.9966 | -123.0423
1108.0156 | 123.0148 | -58.7402 | 64.1327 | -0.168 | 0.010226 | 0.06825 | 0.073508 | 0.12886 | -7.6852e-05 | -0.0045139 | -0.13748 | -0.0061352 | 0.064691 | 0.059321 | 0.0039948 | -0.0085556 | 64.0274 | 64.1693 | -0.18768 | -58.9142 | 64.1739 | -58.786 | -58.905 | -58.6304 | 0.31128 | -58.9645 | 64.1556 | 64.1052 | -58.8867 | -58.9783 | -0.045777 | -0.16479 | 0.041199 | 122.9095 | -0.17395 | -0.009156 | -0.10528 | -0.14648 | -0.23804 | 0.022889 | 0.10986 | -0.22431 | 0.013732 | -0.027465 | 122.9141 | 122.7676 | 58.5526 | -123.0377 | 122.8958 | 122.8455 | 59.0515 | -123.111
1109.0156 | 123.0194 | -58.7814 | 64.064 | -0.099335 | 0.012149 | 0.068678 | 0.066458 | 0.13377 | -0.00093145 | -0.0045139 | -0.00015237 | -0.0048536 | 0.064905 | 0.060389 | 0.0037812 | -0.0070602 | 63.9725 | 64.1464 | -0.17853 | -58.96 | 64.1464 | -58.8318 | -58.9462 | -58.6761 | 0.27008 | -59.0378 | 64.1235 | 64.0457 | -58.9279 | -59.0149 | -0.050354 | -0.16479 | 0.082397 | 122.9279 | -0.17853 | -0.013733 | -0.091553 | -0.14648 | -0.23346 | 0.059509 | 0.10529 | -0.25635 | -0.022888 | -0.018311 | 122.9279 | 122.7539 | 58.6029 | -123.0103 | 122.905 | 122.8271 | 59.0515 | -123.0789
1110.0156 | 123.0377 | -58.7357 | 64.1235 | -0.16037 | 0.0083035 | 0.070387 | 0.070517 | 0.13014 | -0.0011451 | -0.0051547 | -0.15274 | -0.0052808 | 0.064264 | 0.06103 | 0.0033538 | -0.0070602 | 63.9862 | 64.1052 | -0.23346 | -58.9096 | 64.2014 | -58.7906 | -58.8409 | -58.667 | 0.3067 | -58.9828 | 64.2059 | 64.1281 | -58.8959 | -58.96 | -0.054931 | -0.10528 | 0.07782 | 122.8409 | -0.17395 | -0.068665 | -0.13733 | -0.16022 | -0.2243 | 0.082398 | 0.068665 | -0.24719 | -0.022888 | 0.004578 | 122.937 | 122.7219 | 58.5022 | -122.9645 | 122.9416 | 122.8638 | 59.0424 | -123.0835
1111.0156 | 122.9965 | -58.786 | 64.0778 | -0.0077822 | 0.013431 | 0.067182 | 0.07244 | 0.13121 | -0.00050425 | -0.0025913 | 0.060883 | -0.0059216 | 0.062982 | 0.058894 | 0.0039948 | -0.0064194 | 63.9542 | 64.0823 | -0.26093 | -58.9783 | 64.1464 | -58.8318 | -58.905 | -58.7173 | 0.28381 | -59.0469 | 64.1556 | 64.064 | -58.9371 | -58.9966 | -0.045776 | -0.11902 | 0.068664 | 122.8683 | -0.19226 | -0.073242 | -0.1236 | -0.15106 | -0.21057 | 0.07782 | 0.068665 | -0.26093 | -0.050354 | -0.013733 | 122.9324 | 122.7402 | 58.5251 | -122.9828 | 122.9416 | 122.85 | 59.0698 | -123.0743
1112.0156 | 123.0515 | -58.7631 | 64.1281 | -0.168 | 0.013217 | 0.066969 | 0.072012 | 0.13078 | 0.00013675 | -0.0045139 | -0.061188 | -0.0059216 | 0.063837 | 0.059748 | 0.0046356 | -0.0068466 | 64.0274 | 64.151 | -0.2243 | -58.9096 | 64.183 | -58.786 | -58.8913 | -58.6487 | 0.37994 | -58.9874 | 64.183 | 64.1144 | -58.9005 | -58.9828 | -0.022888 | -0.12817 | 0.054931 | 122.9141 | -0.14648 | -0.018311 | -0.10071 | -0.13733 | -0.21973 | 0.054931 | 0.11444 | -0.2243 | -0.004578 | -0.013733 | 122.9462 | 122.7905 | 58.5388 | -123.0194 | 122.9462 | 122.8775 | 59.1431 | -123.111
1113.0156 | 122.9828 | -58.7952 | 64.1052 | 0.022736 | 0.014285 | 0.06761 | 0.07244 | 0.12993 | 0.0020593 | -0.0038731 | 0.060883 | -0.0065626 | 0.065332 | 0.05868 | 0.0031402 | -0.0068466 | 63.9725 | 64.0823 | -0.3067 | -58.9783 | 64.1647 | -58.8272 | -58.8959 | -58.7036 | 0.22888 | -59.0332 | 64.1785 | 64.0594 | -58.9005 | -59.0103 | -0.032043 | -0.10071 | 0.059509 | 122.8775 | -0.1831 | -0.082397 | -0.13275 | -0.10529 | -0.21515 | 0.073242 | 0.091553 | -0.23804 | -0.022888 | -0.045777 | 122.9599 | 122.7676 | 58.4885 | -123.0011 | 122.9736 | 122.8546 | 59.024 | -123.1155
1114.0156 | 123.0286 | -58.7997 | 64.064 | -0.16037 | 0.013217 | 0.066755 | 0.071585 | 0.13035 | -0.00029045 | -0.0045139 | -0.068817 | -0.0067762 | 0.062982 | 0.058894 | 0.0042084 | -0.0053512 | 63.9725 | 64.1098 | -0.23346 | -58.9691 | 64.1373 | -58.8318 | -58.9417 | -58.6807 | 0.31586 | -59.024 | 64.1144 | 64.0732 | -58.9462 | -59.024 | -0.032043 | -0.14191 | 0.073242 | 122.9095 | -0.16937 | -0.027466 | -0.091553 | -0.14648 | -0.2243 | 0.050354 | 0.11902 | -0.2243 | 0 | 0.009155 | 122.937 | 122.7722 | 58.5663 | -123.0057 | 122.9141 | 122.8729 | 59.1156 | -123.0881
1115.0156 | 122.9691 | -58.8135 | 64.0594 | 0.030365 | 0.013644 | 0.064832 | 0.071372 | 0.13121 | -0.0017859 | -0.0030185 | 0.25925 | -0.0044264 | 0.064264 | 0.059107 | 0.0048492 | -0.0070602 | 63.8809 | 63.9633 | -0.36621 | -59.0561 | 64.1235 | -58.8913 | -58.9554 | -58.7723 | 0.11902 | -59.317 | 64.0503 | 64.0091 | -59.0378 | -59.0469 | -0.077819 | -0.14191 | 0.064087 | 122.7768 | -0.24261 | -0.10071 | -0.17853 | -0.2243 | -0.23346 | -0.009155 | 0.041199 | -0.50354 | -0.27008 | -0.050354 | 122.937 | 122.6944 | 58.4473 | -123.0148 | 122.8638 | 122.8226 | 58.9325 | -123.1064
1116.0156 | 123.0148 | -58.7814 | 64.0686 | -0.068817 | 0.010653 | 0.068464 | 0.070731 | 0.12822 | 0.00035035 | -0.0051547 | -0.0077819 | -0.006349 | 0.062769 | 0.059535 | 0.0018584 | -0.0070602 | 63.9908 | 64.0823 | -0.23346 | -58.9737 | 64.119 | -58.8455 | -58.9096 | -58.699 | 0.36163 | -59.0332 | 64.119 | 64.0594 | -58.9233 | -59.024 | -0.064087 | -0.12817 | 0.050354 | 122.8638 | -0.19226 | -0.064087 | -0.07782 | -0.14191 | -0.24262 | 0.050354 | 0.082397 | -0.25177 | -0.009155 | -0.009156 | 122.9004 | 122.7722 | 58.548 | -122.9782 | 122.9004 | 122.8409 | 59.1431 | -123.0927
1117.0156 | 122.9874 | -58.7952 | 64.1006 | 0.037994 | 0.013644 | 0.06825 | 0.071585 | 0.13035 | 0.00056395 | -0.0051547 | 0.037995 | -0.005708 | 0.061701 | 0.060816 | 0.0059174 | -0.0057786 | 63.9496 | 64.064 | -0.31128 | -58.9783 | 64.1235 | -58.8455 | -58.9188 | -58.7265 | 0.19684 | -59.0515 | 64.151 | 64.1052 | -58.9188 | -58.992 | -0.050354 | -0.1236 | 0.022888 | 122.8592 | -0.1831 | -0.059509 | -0.15106 | -0.1236 | -0.19684 | 0.050354 | 0.068665 | -0.25635 | -0.05951 | 0.004578 | 122.9187 | 122.7448 | 58.4839 | -123.0194 | 122.9462 | 122.9004 | 58.992 | -123.0927
1118.0156 | 123.0148 | -58.8226 | 64.0869 | -0.12222 | 0.015567 | 0.06825 | 0.071799 | 0.12886 | 0.0020593 | -0.0034457 | -0.015411 | -0.0042126 | 0.063196 | 0.059321 | 0.0035674 | -0.0068466 | 63.9908 | 64.0823 | -0.26093 | -58.9691 | 64.1235 | -58.8501 | -58.9188 | -58.7082 | 0.35706 | -59.0607 | 64.1098 | 64.0457 | -58.9508 | -59.0332 | -0.027466 | -0.09613 | 0.036621 | 122.905 | -0.14648 | -0.050354 | -0.09613 | -0.12817 | -0.21057 | 0.022888 | 0.11444 | -0.23804 | -0.027466 | -0.041199 | 122.9462 | 122.8134 | 58.5617 | -123.0057 | 122.9324 | 122.8683 | 59.1797 | -123.1201
1119.0156 | 122.9919 | -58.8318 | 64.0503 | 0.068512 | 0.013217 | 0.067182 | 0.071372 | 0.13099 | 0.00056395 | -0.0030185 | 0.18295 | -0.0067762 | 0.068964 | 0.061244 | 0.006131 | -0.0098374 | 63.8535 | 63.9496 | -0.37079 | -59.0652 | 64.1006 | -58.8776 | -58.9508 | -58.5846 | 0.3891 | -59.1385 | 64.0778 | 64.0366 | -58.9828 | -59.079 | -0.045776 | -0.11902 | 0.050354 | 122.7814 | -0.23346 | -0.11444 | -0.19684 | -0.15106 | -0.24719 | 0.027466 | 0.24719 | -0.3067 | -0.05951 | -0.013733 | 122.9324 | 122.6852 | 58.461 | -123.0011 | 122.9095 | 122.8683 | 59.2209 | -123.1293
1120.0156 | 123.024 | -58.8135 | 64.0503 | -0.10696 | 0.012149 | 0.065687 | 0.070944 | 0.12672 | 0.0012047 | -0.0038731 | 0.022736 | -0.0061352 | 0.062769 | 0.06103 | 0.0029266 | -0.0077012 | 63.9587 | 64.0686 | -0.28839 | -59.0103 | 64.1006 | -58.873 | -58.96 | -58.7265 | 0.41199 | -59.079 | 64.1235 | 64.0503 | -58.9966 | -59.0561 | -0.059509 | -0.14648 | 0.050354 | 122.8821 | -0.19684 | -0.050354 | -0.091553 | -0.1831 | -0.24261 | 0.073242 | 0.086976 | -0.2655 | -0.022888 | 0 | 122.9141 | 122.7722 | 58.5251 | -123.0103 | 122.937 | 122.8638 | 59.2255 | -123.1064
1121.0156 | 122.9782 | -58.8455 | 64.0228 | 0.16006 | 0.01279 | 0.06825 | 0.069663 | 0.12822 | -0.00093145 | -0.0057957 | 2.7769 | -0.0072034 | 0.061914 | 0.060816 | 0.006131 | -0.004924 | 63.8626 | 63.945 | -0.3891 | -59.0515 | 64.0915 | -58.8913 | -58.9691 | -58.7952 | 0.52643 | -59.1202 | 64.1006 | 64.0411 | -58.9691 | -59.0515 | -0.045776 | -0.1236 | 0.068665 | 122.7905 | -0.20599 | -0.082398 | -0.16022 | -0.1236 | -0.20599 | 0.07782 | 0.050354 | -0.27466 | -0.068664 | 0.018311 | 122.937 | 122.7081 | 58.4564 | -122.9919 | 122.9462 | 122.8867 | 59.3719 | -123.0743
1122.0156 | 123.0103 | -58.8318 | 64.0594 | 0.037994 | 0.016208 | 0.066755 | 0.07009 | 0.12971 | -0.00071785 | -0.0057957 | -0.023041 | -0.003999 | 0.063623 | 0.059962 | 0.0046356 | -0.0062058 | 63.9221 | 64.0091 | -0.3479 | -59.024 | 64.1052 | -58.8821 | -58.9462 | -58.7906 | 0.40283 | -59.1431 | 64.0961 | 64.0503 | -58.9828 | -59.0561 | -0.050354 | -0.11444 | 0.045777 | 122.8409 | -0.19226 | -0.07782 | -0.13733 | -0.15106 | -0.2243 | 0.036621 | 0.041199 | -0.31128 | -0.086975 | -0.009155 | 122.937 | 122.7539 | 58.4839 | -123.0057 | 122.9279 | 122.8821 | 59.2346 | -123.1155
1123.0156 | 123.0103 | -58.8455 | 64.0503 | 0.083771 | 0.014499 | 0.066755 | 0.071372 | 0.1295 | -7.6852e-05 | -0.0013095 | -0.15274 | -0.0065626 | 0.061487 | 0.062953 | 0.0031402 | -0.0062058 | 63.8901 | 63.9816 | -0.41657 | -59.024 | 64.119 | -58.8776 | -58.9508 | -58.699 | 0.42114 | -59.1293 | 64.1098 | 64.0732 | -58.9554 | -59.0515 | -0.032043 | -0.10529 | 0.068665 | 122.8271 | -0.17853 | -0.073242 | -0.16022 | -0.10986 | -0.20599 | 0.059509 | 0.14648 | -0.28381 | -0.077819 | 0.022888 | 122.9645 | 122.7356 | 58.429 | -123.0011 | 122.9553 | 122.9187 | 59.2667 | -123.1018
1124.0156 | 122.9691 | -58.8501 | 64.0228 | -0.023041 | 0.013858 | 0.06761 | 0.071372 | 0.12907 | -0.0017859 | -0.0040867 | 0.11429 | -0.0065626 | 0.065119 | 0.060176 | 0.004422 | -0.008342 | 63.913 | 64.0091 | -0.37079 | -59.0378 | 64.0869 | -58.8776 | -58.9371 | -58.7814 | 0.44861 | -59.1202 | 64.0869 | 64.0274 | -58.9737 | -59.0515 | -0.027465 | -0.086975 | 0.064087 | 122.8592 | -0.18768 | -0.10071 | -0.10986 | -0.1236 | -0.20142 | 0.064087 | 0.068665 | -0.27008 | -0.068664 | 0.004578 | 122.937 | 122.7631 | 58.4793 | -122.9599 | 122.937 | 122.8775 | 59.2987 | -123.0743
1125.0156 | 123.024 | -58.8226 | 64.0228 | 0.11429 | 0.011081 | 0.067396 | 0.070731 | 0.13185 | -0.0017859 | -0.0036595 | 0.23636 | -0.007417 | 0.063196 | 0.057398 | 0.0035674 | -0.0059922 | 63.8901 | 64.0045 | -0.41657 | -59.0424 | 64.1052 | -58.8638 | -58.9462 | -58.7448 | 0.52185 | -59.079 | 64.0686 | 64.0228 | -58.9691 | -59.0515 | -0.041199 | -0.1236 | 0.082398 | 122.8271 | -0.21973 | -0.09613 | -0.13275 | -0.14648 | -0.22888 | 0.045777 | 0.07782 | -0.25635 | -0.027465 | 0 | 122.9279 | 122.7127 | 58.4061 | -122.9691 | 122.8912 | 122.8455 | 59.3445 | -123.0743
1126.0156 | 123.1064 | -58.8593 | 63.9267 | 0.13718 | 0.0068081 | 0.067823 | 0.068167 | 0.12822 | -0.0066993 | -0.0066501 | 0.33554 | -0.0067762 | 0.06106 | 0.060603 | 0.002713 | -0.004924 | 63.8901 | 64.0594 | -0.31586 | -59.0469 | 63.9587 | -58.8959 | -58.992 | -58.754 | 0.71411 | -59.0881 | 63.9542 | 63.9221 | -58.9874 | -59.1019 | -0.036621 | -0.13275 | 0.032043 | 122.9187 | -0.18768 | -0.054932 | -0.036621 | -0.12817 | -0.24262 | 0.027466 | 0.10529 | -0.22888 | 0.013733 | -0.004578 | 122.818 | 122.7493 | 58.5434 | -122.9187 | 122.8134 | 122.7814 | 59.5734 | -123.0286
1127.0156 | 123.0423 | -58.8593 | 63.9542 | 0.14481 | 0.011508 | 0.066969 | 0.068381 | 0.12971 | -7.6852e-05 | -0.0049411 | 0.26688 | -0.0067762 | 0.06341 | 0.05868 | 0.002713 | -0.006633 | 63.8672 | 63.9313 | -0.4303 | -59.1019 | 64.0411 | -58.9371 | -59.0195 | -58.8089 | 0.60883 | -59.1385 | 64.0045 | 63.9542 | -59.0286 | -59.111 | -0.07782 | -0.16022 | 0.086975 | 122.7905 | -0.24262 | -0.082398 | -0.086976 | -0.16937 | -0.25177 | 0.050354 | 0.050354 | -0.27924 | -0.027466 | 0 | 122.9004 | 122.7264 | 58.429 | -122.9736 | 122.8638 | 122.8134 | 59.4681 | -123.0652
1128.0156 | 122.9828 | -58.9005 | 63.9679 | 0.022736 | 0.017276 | 0.068464 | 0.070731 | 0.13228 | 0.00077755 | -0.0028049 | 0.16006 | -0.005708 | 0.065119 | 0.05868 | 0.0059174 | -0.0094102 | 63.8443 | 63.9084 | -0.40741 | -59.111 | 64.0137 | -58.9691 | -59.0378 | -58.8684 | 0.67749 | -59.2072 | 64.0091 | 63.9725 | -59.0652 | -59.1248 | -0.068664 | -0.13733 | 0.045776 | 122.8088 | -0.21057 | -0.073242 | -0.1236 | -0.16479 | -0.2243 | 0.041198 | 0.032044 | -0.3067 | -0.082397 | 0.004577 | 122.9141 | 122.7448 | 58.493 | -123.0057 | 122.9095 | 122.8729 | 59.5779 | -123.0927
1129.0156 | 123.1201 | -58.9279 | 63.8489 | 0.19821 | 0.010653 | 0.067182 | 0.067526 | 0.13163 | -0.0019995 | -0.0045139 | 0.50339 | -0.0052808 | 0.064051 | 0.059535 | 0.0016448 | -0.0077012 | 63.8443 | 63.9679 | -0.3891 | -59.1248 | 63.945 | -58.9828 | -59.0515 | -58.786 | 0.82398 | -59.1156 | 63.9221 | 63.8809 | -59.0744 | -59.1705 | -0.054932 | -0.1236 | 0.09613 | 122.8958 | -0.19684 | -0.073242 | -0.004578 | -0.14648 | -0.24262 | 0.073242 | 0.14191 | -0.18768 | 0.054931 | 0.032043 | 122.8729 | 122.7722 | 58.5388 | -122.9004 | 122.85 | 122.8088 | 59.7519 | -123.0194
1130.0156 | 122.9919 | -58.9279 | 63.9404 | -0.015411 | 0.012149 | 0.066328 | 0.070731 | 0.12993 | 0.0014185 | -0.0034457 | 0.068512 | -0.0065626 | 0.062982 | 0.059107 | 0.0046356 | -0.006633 | 63.8351 | 63.9038 | -0.44861 | -59.1476 | 63.9816 | -58.992 | -59.0515 | -58.8776 | 0.84228 | -59.2438 | 63.9862 | 63.9313 | -59.0836 | -59.1614 | -0.064087 | -0.1236 | 0.041198 | 122.8317 | -0.21973 | -0.09613 | -0.10529 | -0.15564 | -0.23346 | 0.045776 | 0.050354 | -0.31586 | -0.082397 | -0.009156 | 122.9095 | 122.7631 | 58.4793 | -122.9919 | 122.9141 | 122.8592 | 59.7702 | -123.1018
1131.0156 | 123.0011 | -59.0195 | 63.8535 | 0.12192 | 0.012576 | 0.069319 | 0.068167 | 0.13057 | 0.00035035 | -0.0030185 | 0.19058 | -0.0059216 | 0.064691 | 0.059107 | 0.0022858 | -0.0059922 | 63.7253 | 63.8168 | -0.44403 | -59.2163 | 63.9175 | -59.0836 | -59.111 | -58.9142 | 1.0666 | -59.2575 | 63.8947 | 63.8489 | -59.1568 | -59.2209 | -0.064087 | -0.091553 | 0.064087 | 122.8363 | -0.19684 | -0.10529 | -0.12817 | -0.13733 | -0.20142 | 0.041198 | 0.10528 | -0.23804 | -0.036621 | -0.004578 | 122.937 | 122.7448 | 58.5754 | -122.9645 | 122.9141 | 122.8683 | 60.0861 | -123.0743
1132.0156 | 122.9736 | -59.0332 | 63.8306 | 0.045624 | 0.01279 | 0.066541 | 0.072226 | 0.12822 | 0.0031273 | -0.0021641 | 2.8075 | -0.0031446 | 0.062555 | 0.059748 | 0.0022858 | -0.006633 | 63.6658 | 63.7436 | -0.44861 | -59.2712 | 63.8992 | -59.0973 | -59.2072 | -59.0698 | 1.3229 | -59.2896 | 63.8855 | 63.826 | -59.1888 | -59.2575 | -0.064087 | -0.17395 | 0.068665 | 122.7768 | -0.23804 | -0.064087 | -0.16479 | -0.15564 | -0.2243 | 0.054932 | -0.036621 | -0.25635 | -0.032044 | -0.004577 | 122.9324 | 122.699 | 58.5846 | -123.0377 | 122.9187 | 122.8592 | 60.3561 | -123.0881
1133.0156 | 123.0835 | -59.0195 | 63.7527 | 0.19821 | 0.010867 | 0.066328 | 0.068381 | 0.13078 | -0.0011451 | -0.0040867 | 0.16769 | -0.0069898 | 0.064691 | 0.058039 | 0.0037812 | -0.0062058 | 63.7344 | 63.826 | -0.37079 | -59.2209 | 63.8214 | -59.0927 | -59.1522 | -58.8821 | 1.4603 | -59.2438 | 63.8031 | 63.7848 | -59.2026 | -59.2346 | -0.073242 | -0.13275 | 0.068664 | 122.8455 | -0.20142 | -0.068664 | -0.018311 | -0.18311 | -0.21515 | 0.050354 | 0.13733 | -0.2243 | -0.009155 | 0.032043 | 122.8409 | 122.7539 | 58.6487 | -122.905 | 122.8226 | 122.8043 | 60.4797 | -122.9874
1134.0156 | 122.9691 | -59.0652 | 63.8168 | 0.068512 | 0.01279 | 0.066969 | 0.072867 | 0.13035 | 0.0016321 | -0.0017369 | 0.12955 | -0.0033582 | 0.062555 | 0.064021 | 0.004422 | -0.0085556 | 63.6566 | 63.7253 | -0.44403 | -59.2987 | 63.8718 | -59.1202 | -59.1888 | -59.111 | 1.8402 | -59.3445 | 63.8901 | 63.8168 | -59.2026 | -59.2941 | -0.054931 | -0.1236 | 0.054932 | 122.7905 | -0.23346 | -0.10986 | -0.16022 | -0.13733 | -0.22888 | 0.073243 | -0.045776 | -0.27923 | -0.050354 | 0 | 122.937 | 122.7219 | 58.6212 | -123.0057 | 122.9553 | 122.8821 | 60.9055 | -123.111
1135.0156 | 123.111 | -59.0332 | 63.7894 | 0.17532 | 0.012149 | 0.06825 | 0.069876 | 0.128 | -0.0022131 | -0.0038731 | 0.24399 | -0.0072034 | 0.063196 | 0.059107 | 0.0042084 | -0.006633 | 63.707 | 63.8031 | -0.37079 | -59.2392 | 63.8489 | -59.1385 | -59.1843 | -58.9279 | 1.4694 | -59.2438 | 63.7985 | 63.7619 | -59.198 | -59.2987 | -0.10529 | -0.15106 | 0.059509 | 122.8363 | -0.20599 | -0.054932 | -0.082398 | -0.16479 | -0.2655 | 0.009155 | 0.10529 | -0.21057 | 0.054932 | -0.027466 | 122.8821 | 122.7402 | 58.6624 | -122.9736 | 122.8317 | 122.7951 | 60.5026 | -123.0881
1136.0156 | 123.0148 | -59.0927 | 63.7619 | 0.10666 | 0.013003 | 0.068037 | 0.072226 | 0.13099 | -0.00071785 | -0.0023777 | 0.20584 | -0.00464 | 0.06341 | 0.060176 | 0.0031402 | -0.0074876 | 63.652 | 63.7161 | -0.48981 | -59.2896 | 63.8443 | -59.1431 | -59.2026 | -58.9828 | 1.3046 | -59.3491 | 63.8351 | 63.7711 | -59.2117 | -59.3033 | -0.050354 | -0.10986 | 0.082397 | 122.8088 | -0.19684 | -0.086975 | -0.10986 | -0.11902 | -0.21057 | 0.073242 | 0.10986 | -0.25635 | -0.045776 | 0.009155 | 122.937 | 122.7448 | 58.6029 | -122.9645 | 122.9279 | 122.8638 | 60.3973 | -123.0652
1137.0156 | 123.0835 | -59.0607 | 63.7573 | 0.19821 | 0.01044 | 0.068464 | 0.071158 | 0.1295 | -0.0034949 | -0.0034457 | 0.28976 | -0.005708 | 0.062982 | 0.060816 | 0.0022858 | -0.0085556 | 63.6703 | 63.7848 | -0.37079 | -59.2758 | 63.8214 | -59.1385 | -59.2072 | -58.9233 | 1.6205 | -59.2804 | 63.7802 | 63.7299 | -59.23 | -59.3079 | -0.07782 | -0.14648 | 0.064087 | 122.8455 | -0.21515 | -0.068665 | -0.086975 | -0.16937 | -0.24719 | 0.022888 | 0.13733 | -0.21973 | 0.027465 | -0.027466 | 122.8821 | 122.731 | 58.6899 | -122.9645 | 122.8409 | 122.7905 | 60.6812 | -123.0652
1138.0156 | 122.9919 | -59.0927 | 63.7344 | 0.57968 | 0.013217 | 0.06825 | 0.071158 | 0.13057 | 0.00056395 | -0.0040867 | 0.12192 | -0.005708 | 0.065973 | 0.060389 | 0.0029266 | -0.0068466 | 63.6246 | 63.7024 | -0.4303 | -59.3216 | 63.8351 | -59.1385 | -59.23 | -59.024 | 1.593 | -59.3765 | 63.8031 | 63.7573 | -59.2438 | -59.3353 | -0.045777 | -0.13733 | 0.10071 | 122.7951 | -0.22888 | -0.091552 | -0.10986 | -0.15106 | -0.24262 | 0.068665 | 0.068664 | -0.28381 | -0.041199 | 0.022888 | 122.9279 | 122.7173 | 58.6624 | -122.9645 | 122.8958 | 122.85 | 60.6857 | -123.0698
1139.0156 | 123.0927 | -59.0744 | 63.7115 | 0.16769 | 0.0097989 | 0.067823 | 0.069022 | 0.13014 | -0.00093145 | -0.0034457 | 0.30502 | -0.0059216 | 0.064264 | 0.058039 | 0.0031402 | -0.006633 | 63.7161 | 63.8123 | -0.35248 | -59.2392 | 63.7848 | -59.1614 | -59.2072 | -58.9279 | 1.7578 | -59.2987 | 63.7207 | 63.6932 | -59.2896 | -59.3628 | -0.086975 | -0.13275 | 0.073242 | 122.8867 | -0.16479 | -0.032044 | 0.004577 | -0.21515 | -0.28839 | 0.009155 | 0.14648 | -0.2243 | 0.064087 | -0.018311 | 122.8592 | 122.7905 | 58.7219 | -122.9187 | 122.7951 | 122.7676 | 60.8322 | -123.0743
1140.0156 | 123.0057 | -59.1019 | 63.7619 | 0.10666 | 0.018344 | 0.066969 | 0.074149 | 0.13249 | 0.0016321 | -0.0017369 | 0.10666 | -0.0054944 | 0.063623 | 0.059107 | 0.0046356 | -0.0089828 | 63.5605 | 63.858 | -0.41657 | -59.317 | 63.8672 | -59.1431 | -59.2392 | -58.9966 | 1.561 | -59.3857 | 63.8443 | 63.7894 | -59.2484 | -59.3216 | -0.041198 | -0.13733 | 0.10529 | 122.9599 | -0.21515 | -0.07782 | -0.20142 | -0.14648 | -0.21973 | 0.082397 | 0.10529 | -0.28381 | -0.064087 | 0.027466 | 122.9691 | 122.6624 | 58.6853 | -123.0011 | 122.9462 | 122.8912 | 60.6628 | -123.0835
1141.0156 | 123.1384 | -58.9828 | 63.8123 | 0.16006 | 0.012362 | 0.066755 | 0.069449 | 0.12928 | -0.0026405 | -0.0049411 | 0.28214 | -0.006349 | 0.065973 | 0.057612 | 0.0029266 | -0.0064194 | 63.7619 | 63.9084 | -0.40283 | -59.1614 | 63.8672 | -59.0652 | -59.1156 | -58.8364 | 1.8723 | -59.198 | 63.8306 | 63.7985 | -59.1476 | -59.2209 | -0.082398 | -0.13275 | 0.054931 | 122.8912 | -0.17853 | -0.045776 | -0.050354 | -0.16479 | -0.23804 | 0.01831 | 0.14648 | -0.21515 | 0.022888 | -0.013733 | 122.85 | 122.7448 | 58.58 | -122.9279 | 122.8134 | 122.7814 | 60.8551 | -123.0331
1142.0156 | 123.0011 | -59.0057 | 63.8535 | 0.12955 | 0.014285 | 0.069105 | 0.071158 | 0.13121 | 0.00077755 | -0.0017369 | 0.72464 | -0.0042126 | 0.06341 | 0.059321 | 0.0024994 | -0.0072738 | 63.7436 | 63.7985 | -0.48981 | -59.2255 | 63.9038 | -59.0515 | -59.1568 | -58.9417 | 1.9913 | -59.2896 | 63.8992 | 63.8626 | -59.1431 | -59.23 | -0.045777 | -0.15106 | 0.050354 | 122.8043 | -0.21973 | -0.068665 | -0.10986 | -0.13733 | -0.2243 | 0.045776 | 0.064087 | -0.28381 | -0.059509 | 0.009155 | 122.9095 | 122.7493 | 58.5159 | -123.0103 | 122.905 | 122.8683 | 60.997 | -123.0835
1143.0156 | 123.1155 | -58.9783 | 63.826 | 0.16769 | 0.01044 | 0.067823 | 0.068167 | 0.13142 | -0.0052039 | -0.0047275 | -0.12222 | -0.0069898 | 0.063196 | 0.059535 | 0.0031402 | -0.006633 | 63.7939 | 63.6749 | -0.59967 | -59.1156 | 63.8351 | -59.0652 | -59.0881 | -58.8272 | 2.1698 | -59.1797 | 63.8672 | 63.8168 | -59.1431 | -59.2163 | -0.086976 | -0.10986 | 0.009155 | 122.6532 | -0.13733 | -0.027466 | -0.032044 | -0.16479 | -0.23804 | 0.041198 | 0.15106 | -0.20142 | 0.036622 | -0.009156 | 122.8134 | 122.7722 | 58.3786 | -122.9141 | 122.8455 | 122.7951 | 61.1481 | -123.0423
1144.0156 | 123.0103 | -58.9874 | 63.8626 | 0.14481 | 0.015567 | 0.066114 | 0.069022 | 0.12993 | 0.00056395 | -0.0021641 | 0.12192 | -0.006349 | 0.063837 | 0.059107 | 0.0037812 | -0.0085556 | 63.7161 | 63.7665 | -0.54932 | -59.2392 | 63.9359 | -59.079 | -59.1385 | -58.9462 | 2.0416 | -59.5093 | 63.8351 | 63.8168 | -59.1843 | -59.2484 | -0.091552 | -0.15106 | 0.073242 | 122.7539 | -0.25177 | -0.10071 | -0.14648 | -0.19684 | -0.26093 | -0.027466 | 0.041199 | -0.52185 | -0.26093 | -0.045777 | 122.9233 | 122.7036 | 58.4381 | -123.0011 | 122.8226 | 122.8043 | 61.0291 | -123.111
1145.0156 | 123.1293 | -58.9966 | 63.7802 | 0.13718 | 0.0095853 | 0.068891 | 0.067526 | 0.12736 | -0.0026405 | -0.0017369 | 0.29739 | -0.0072034 | 0.060633 | 0.059748 | 0.0031402 | -0.0068466 | 63.7939 | 63.8947 | -0.42572 | -59.1797 | 63.8489 | -59.0881 | -59.1385 | -59.0012 | 2.2018 | -59.1156 | 63.7848 | 63.7711 | -59.1797 | -59.2529 | -0.091553 | -0.14191 | 0.068665 | 122.8912 | -0.18311 | -0.041198 | 0.013733 | -0.18311 | -0.25635 | 0.004578 | -0.004578 | -0.11902 | 0.13733 | -0.009155 | 122.8455 | 122.7905 | 58.5709 | -122.9187 | 122.7814 | 122.7676 | 61.1984 | -123.0331
1146.0156 | 122.9782 | -59.0424 | 63.8672 | 0.060882 | 0.0097989 | 0.06825 | 0.069449 | 0.13078 | -0.00071785 | -0.0045139 | 0.20584 | -0.0054944 | 0.065546 | 0.061457 | 0.006131 | -0.008342 | 63.7848 | 63.7344 | -0.55847 | -59.2072 | 63.945 | -59.0652 | -59.1293 | -58.9279 | 2.3254 | -59.3033 | 63.9084 | 63.8672 | -59.1705 | -59.2438 | -0.022889 | -0.086975 | 0.07782 | 122.7768 | -0.16479 | -0.07782 | -0.082397 | -0.12817 | -0.20142 | 0.041199 | 0.11444 | -0.26093 | -0.05951 | 0 | 122.9874 | 122.8271 | 58.4839 | -122.9965 | 122.9507 | 122.9095 | 61.3678 | -123.111
1147.0156 | 123.1201 | -59.0149 | 63.7619 | 0.17532 | 0.010013 | 0.068464 | 0.068167 | 0.12886 | -0.0019995 | -0.0049411 | 0.19058 | -0.0052808 | 0.062128 | 0.059321 | 0.0033538 | -0.006633 | 63.7756 | 63.8718 | -0.4715 | -59.1934 | 63.8031 | -59.0698 | -59.166 | -58.8867 | 2.5223 | -59.2346 | 63.7894 | 63.7619 | -59.2026 | -59.2758 | -0.054931 | -0.15106 | 0.041199 | 122.8867 | -0.17853 | -0.027465 | 0.013733 | -0.18768 | -0.26093 | 0.027466 | 0.12817 | -0.21973 | 0.041199 | 0 | 122.818 | 122.7905 | 58.5434 | -122.9279 | 122.8043 | 122.7768 | 61.5372 | -123.0377
1148.0156 | 122.9965 | -59.0515 | 63.8214 | 0.15244 | 0.010653 | 0.066328 | 0.069876 | 0.12971 | 0.00013675 | -0.0036595 | 0.78568 | -0.0048536 | 0.062982 | 0.059962 | 0.0039948 | -0.0074876 | 63.7161 | 63.7619 | -0.4715 | -59.5139 | 63.858 | -59.1019 | -59.1934 | -58.9325 | 2.5543 | -59.3353 | 63.8947 | 63.8077 | -59.198 | -59.2758 | -0.050354 | -0.14191 | 0.036621 | 122.8134 | -0.46234 | -0.32043 | -0.10529 | -0.14648 | -0.2243 | 0.073242 | 0.11902 | -0.28381 | -0.059509 | -0.013733 | 122.9095 | 122.7676 | 58.58 | -123.0148 | 122.9462 | 122.8592 | 61.6058 | -123.0972
1149.0156 | 123.0927 | -59.0286 | 63.7344 | 0.20584 | 0.010226 | 0.069105 | 0.066458 | 0.12928 | -0.0030677 | -0.0036595 | -0.084076 | -0.0065626 | 0.063623 | 0.061244 | 0.0022858 | -0.0070602 | 63.7436 | 63.8763 | -0.27924 | -59.3857 | 63.7527 | -59.1293 | -59.1614 | -58.8776 | 2.6001 | -59.2621 | 63.7985 | 63.7253 | -59.198 | -59.2804 | -0.10071 | -0.13275 | 0.018311 | 122.905 | -0.35706 | -0.2243 | 0.009155 | -0.16937 | -0.25177 | 0.064087 | 0.15106 | -0.23346 | 0.018311 | -0.009155 | 122.7814 | 122.7722 | 58.7494 | -122.8958 | 122.8271 | 122.7539 | 61.6287 | -123.0148
1150.0156 | 123.0927 | -59.1019 | 63.8031 | 0.12192 | 0.013217 | 0.066755 | 0.073081 | 0.12822 | 0.00099115 | -0.0040867 | 0.15244 | -0.0050672 | 0.065119 | 0.058467 | 0.0033538 | -0.006633 | 63.6475 | 63.6841 | -0.28381 | -59.3262 | 63.858 | -59.1431 | -59.2209 | -59.0057 | 2.5177 | -59.3994 | 63.826 | 63.7756 | -59.2529 | -59.3536 | -0.041198 | -0.11902 | 0.054931 | 122.7859 | -0.2243 | -0.10529 | -0.15564 | -0.15106 | -0.25177 | 0.022888 | 0.096131 | -0.29755 | -0.045776 | -0.027466 | 122.9599 | 122.7493 | 58.8181 | -123.024 | 122.9279 | 122.8775 | 61.6196 | -123.1567
1151.0156 | 123.0881 | -59.079 | 63.7253 | 0.19821 | 0.0095853 | 0.06526 | 0.069022 | 0.12971 | -0.0017859 | -0.0023777 | 0.25162 | -0.0078442 | 0.061273 | 0.059962 | 0.0037812 | -0.0077012 | 63.6749 | 63.7253 | -0.10529 | -59.3124 | 63.8077 | -59.1614 | -59.2117 | -58.9691 | 2.4857 | -59.3399 | 63.7848 | 63.7436 | -59.2484 | -59.3262 | -0.082398 | -0.13275 | 0.082397 | 122.8043 | -0.23346 | -0.10071 | -0.050354 | -0.16937 | -0.24719 | 0.059509 | 0.10986 | -0.26093 | -0.013733 | 0.01831 | 122.8867 | 122.7539 | 58.9737 | -122.937 | 122.8638 | 122.8226 | 61.5646 | -123.0515
1152.0156 | 122.9919 | -59.1156 | 63.7344 | 0.14481 | 0.012149 | 0.068464 | 0.072012 | 0.13142 | 0.0054773 | -0.0060093 | -0.045929 | -0.0037854 | 0.064905 | 0.060389 | 0.0057038 | -0.0085556 | 63.9175 | 63.707 | -0.10071 | -59.3216 | 63.8443 | -59.1614 | -59.2255 | -59.0378 | 2.4261 | -59.4086 | 63.7985 | 63.7573 | -59.2804 | -59.3399 | -0.045776 | -0.10986 | 0.10986 | 122.8226 | -0.20599 | -0.09613 | 0.18311 | -0.1648 | -0.2243 | 0.064087 | 0.07782 | -0.29297 | -0.068664 | 0.022888 | 122.9599 | 123.0331 | 59.0149 | -122.9599 | 122.9141 | 122.8729 | 61.5417 | -123.0743
1153.0156 | 123.111 | -59.1064 | 63.6887 | 0.19821 | 0.012149 | 0.069746 | 0.06774 | 0.12864 | -0.0017859 | -0.0015231 | 0.2211 | -0.005708 | 0.064478 | 0.062525 | 0.0031402 | -0.0074876 | 63.6612 | 63.7619 | 0.11444 | -59.2667 | 63.7436 | -59.1705 | -59.2392 | -58.9737 | 2.5909 | -59.3216 | 63.7253 | 63.6841 | -59.2438 | -59.3445 | -0.064087 | -0.13275 | 0.054931 | 122.8683 | -0.16022 | -0.027466 | -0.027466 | -0.13733 | -0.23804 | 0.036621 | 0.13275 | -0.21515 | 0.022888 | -0.004578 | 122.85 | 122.7676 | 59.2209 | -122.9279 | 122.8317 | 122.7905 | 61.6974 | -123.0331
1154.0156 | 123.0743 | -59.111 | 63.7527 | 0.076141 | 0.011935 | 0.067182 | 0.070517 | 0.13035 | -0.00071785 | -0.0032321 | 0.17532 | -0.003999 | 0.064478 | 0.061244 | 0.0046356 | -0.0042832 | 63.5834 | 63.6475 | 0.068665 | -59.3536 | 63.8077 | -59.1751 | -59.2484 | -59.0881 | 2.0416 | -59.2712 | 63.7299 | 63.7344 | -59.2896 | -59.3536 | -0.064087 | -0.13733 | 0.054931 | 122.7585 | -0.24261 | -0.10529 | -0.16937 | -0.17853 | -0.24261 | -0.022889 | 0.022888 | -0.16022 | 0.082398 | -0.018311 | 122.9187 | 122.6944 | 59.1797 | -123.0011 | 122.8409 | 122.8455 | 61.1526 | -123.1064
1155.0156 | 123.056 | -59.0927 | 63.7253 | 0.12955 | 0.0097989 | 0.067823 | 0.069663 | 0.12971 | -7.6852e-05 | -0.0030185 | 0.25162 | -0.005708 | 0.063837 | 0.059107 | 0.0033538 | -0.0057786 | 63.6429 | 63.7299 | 0.20142 | -59.3033 | 63.7894 | -59.1843 | -59.2575 | -58.992 | 2.5314 | -59.3445 | 63.7619 | 63.7161 | -59.2575 | -59.3308 | -0.091553 | -0.16479 | 0.064087 | 122.8226 | -0.21057 | -0.045777 | -0.082398 | -0.16479 | -0.23804 | 0.036621 | 0.10071 | -0.25177 | -0.013732 | -0.009156 | 122.8821 | 122.7356 | 59.2941 | -122.9828 | 122.8546 | 122.8088 | 61.6241 | -123.056
1156.0156 | 122.9736 | -59.1248 | 63.7299 | 0.015106 | 0.011935 | 0.066755 | 0.071158 | 0.12864 | 0.00099115 | -0.0028049 | 0.12955 | -0.0067762 | 0.064478 | 0.059962 | 0.004422 | -0.0074876 | 63.62 | 63.6749 | 0.27924 | -59.3124 | 63.8077 | -59.1705 | -59.2529 | -59.0744 | 2.4673 | -59.4498 | 63.8077 | 63.7299 | -59.2896 | -59.3491 | -0.045776 | -0.12817 | 0.07782 | 122.7997 | -0.18768 | -0.059509 | -0.10986 | -0.1648 | -0.2243 | 0.07782 | 0.050354 | -0.32501 | -0.10071 | 0 | 122.9324 | 122.7448 | 59.404 | -122.9828 | 122.9324 | 122.8546 | 61.5921 | -123.0789
1157.0156 | 123.0881 | -59.1156 | 63.6795 | 0.17532 | 0.012362 | 0.066755 | 0.069663 | 0.12971 | -0.0026405 | -0.0030185 | 0.30502 | -0.0069898 | 0.06106 | 0.061457 | 0.0046356 | -0.0079148 | 63.6566 | 63.7756 | 0.35248 | -59.2987 | 63.7619 | -59.1568 | -59.2392 | -58.96 | 2.6688 | -59.3033 | 63.7436 | 63.6703 | -59.2667 | -59.3308 | -0.041198 | -0.1236 | 0.082398 | 122.8912 | -0.18311 | -0.059509 | -0.022888 | -0.15106 | -0.21515 | 0.064087 | 0.15564 | -0.18768 | 0.027466 | -0.009155 | 122.8775 | 122.7722 | 59.4681 | -122.9187 | 122.8592 | 122.7859 | 61.7844 | -123.0103
1158.0156 | 122.9874 | -59.1522 | 63.7207 | 0.0074768 | 0.014499 | 0.068037 | 0.072867 | 0.12843 | 0.0012047 | -0.0040867 | 0.037995 | -0.0044264 | 0.064905 | 0.05868 | 0.0046356 | -0.0064194 | 63.6246 | 63.6978 | 0.3479 | -59.3353 | 63.7756 | -59.1705 | -59.2621 | -59.0515 | 2.8564 | -59.4269 | 63.7894 | 63.7207 | -59.2712 | -59.3903 | -0.01831 | -0.10986 | 0.054932 | 122.85 | -0.1831 | -0.073242 | -0.09613 | -0.11902 | -0.23804 | 0.068665 | 0.10071 | -0.27466 | -0.036621 | 0 | 122.9279 | 122.7768 | 59.5001 | -122.9828 | 122.9416 | 122.8729 | 62.0087 | -123.111
1159.0156 | 123.0652 | -59.1705 | 63.6566 | 0.16769 | 0.01279 | 0.069105 | 0.070517 | 0.13035 | -0.0022131 | -0.0032321 | 0.25162 | -0.0069898 | 0.059564 | 0.059535 | 0.0039948 | -0.0072738 | 63.5925 | 63.6566 | 0.40283 | -59.3674 | 63.7482 | -59.23 | -59.285 | -59.0515 | 2.8748 | -59.3994 | 63.7161 | 63.6703 | -59.317 | -59.3765 | -0.05951 | -0.11444 | 0.091553 | 122.8271 | -0.19684 | -0.082398 | -0.064087 | -0.14648 | -0.20599 | 0.059509 | 0.11902 | -0.22888 | -0.022888 | 0.013733 | 122.9187 | 122.7631 | 59.5734 | -122.9416 | 122.8867 | 122.8409 | 62.0453 | -123.0331
1160.0156 | 122.9874 | -59.1614 | 63.7253 | 0.060882 | 0.012362 | 0.068464 | 0.072012 | 0.12907 | 0.00099115 | -0.0028049 | 0.083771 | -0.0067762 | 0.062769 | 0.059535 | 0.0048492 | -0.0064194 | 63.6246 | 63.6749 | 0.25635 | -59.3491 | 63.7848 | -59.1843 | -59.2484 | -59.0927 | 2.861 | -59.436 | 63.7802 | 63.7207 | -59.3033 | -59.3811 | -0.022888 | -0.086975 | 0.059509 | 122.8363 | -0.18768 | -0.10071 | -0.10071 | -0.14191 | -0.21973 | 0.054931 | 0.068665 | -0.27466 | -0.054931 | -0.004578 | 122.9462 | 122.7859 | 59.4177 | -122.9736 | 122.9416 | 122.8821 | 62.0224 | -123.1064
1161.0156 | 123.0377 | -59.1568 | 63.7024 | 0.083771 | 0.01279 | 0.066755 | 0.06774 | 0.12779 | -7.6852e-05 | -0.0040867 | 0.2211 | -0.005708 | 0.064264 | 0.059535 | 0.0014312 | -0.0085556 | 63.5834 | 63.6566 | 0.16022 | -59.3491 | 63.7894 | -59.2117 | -59.2896 | -59.0469 | 2.9388 | -59.4131 | 63.7573 | 63.7115 | -59.3216 | -59.3628 | -0.054932 | -0.13275 | 0.086975 | 122.8134 | -0.19226 | -0.059509 | -0.11902 | -0.16479 | -0.20599 | 0.054931 | 0.10986 | -0.25635 | -0.050354 | 0.009155 | 122.9462 | 122.7402 | 59.317 | -122.9919 | 122.9141 | 122.8683 | 62.0956 | -123.0652
1162.0156 | 123.0148 | -59.1568 | 63.7024 | 0.015106 | 0.014499 | 0.067182 | 0.069876 | 0.13099 | 0.0014185 | -0.0032321 | 0.037995 | -0.0033582 | 0.064051 | 0.058467 | 0.002713 | -0.006633 | 63.6108 | 63.6795 | 0.45776 | -59.3491 | 63.7665 | -59.2209 | -59.3079 | -59.0927 | 3.1311 | -59.4406 | 63.7436 | 63.7207 | -59.3216 | -59.3948 | -0.064087 | -0.15106 | 0.064086 | 122.8363 | -0.19226 | -0.041199 | -0.091553 | -0.16479 | -0.23804 | 0.041198 | 0.064087 | -0.28381 | -0.045777 | 0.01831 | 122.9233 | 122.7676 | 59.6146 | -123.0103 | 122.9004 | 122.8775 | 62.2879 | -123.0972
1163.0156 | 123.0148 | -59.198 | 63.7161 | 0.12192 | 0.014071 | 0.070173 | 0.071372 | 0.13121 | 0.0067589 | -0.0038731 | -0.03067 | -0.0037854 | 0.065119 | 0.059107 | 0.002713 | -0.0044968 | 63.3865 | 63.8992 | 0.6958 | -59.4086 | 63.8077 | -59.2346 | -59.2804 | -59.0836 | 3.0487 | -59.4452 | 63.7619 | 63.6978 | -59.3445 | -59.4086 | -0.036621 | -0.082398 | 0.091553 | 123.0972 | -0.21057 | -0.12817 | -0.32959 | -0.14648 | -0.21057 | 0.045777 | 0.11444 | -0.24719 | -0.036621 | -0.01831 | 123.0057 | 122.5845 | 59.8938 | -122.9965 | 122.9599 | 122.8958 | 62.2467 | -123.1247
1164.0156 | 123.0286 | -59.1476 | 63.7207 | -0.053558 | 0.013431 | 0.066969 | 0.069449 | 0.13035 | 0.0016321 | -0.0045139 | 0.037995 | -0.006349 | 0.063623 | 0.059535 | 0.0042084 | -0.0068466 | 63.6429 | 63.7115 | 0.6958 | -59.3262 | 63.7665 | -59.198 | -59.2941 | -59.0561 | 3.0441 | -59.4269 | 63.7436 | 63.7115 | -59.3353 | -59.3948 | -0.050354 | -0.14648 | 0.045776 | 122.8592 | -0.17853 | -0.032044 | -0.07782 | -0.18768 | -0.24719 | 0.022888 | 0.091553 | -0.27924 | -0.032044 | -0.009155 | 122.9141 | 122.7905 | 59.8434 | -123.0148 | 122.8912 | 122.8592 | 62.1918 | -123.1155
1165.0156 | 122.9553 | -59.198 | 63.7344 | 0.18295 | 0.012149 | 0.064832 | 0.068381 | 0.12971 | 0.00035035 | -0.0025913 | 0.16006 | -0.005708 | 0.065332 | 0.058253 | 0.0046356 | -0.0053512 | 63.5376 | 63.5788 | 0.50812 | -59.4086 | 63.7665 | -59.2484 | -59.3216 | -59.1248 | 2.5223 | -59.7473 | 63.707 | 63.6154 | -59.3628 | -59.4269 | -0.050354 | -0.1236 | 0.032043 | 122.7768 | -0.21057 | -0.086975 | -0.19684 | -0.1648 | -0.22888 | -0.027466 | 0.073242 | -0.54932 | -0.32043 | -0.11902 | 122.9645 | 122.7356 | 59.7061 | -123.056 | 122.905 | 122.8134 | 61.7203 | -123.1613
1166.0156 | 123.0103 | -59.166 | 63.707 | 0.053253 | 0.011081 | 0.06761 | 0.07244 | 0.13057 | 0.00013675 | -0.0040867 | 0.0074766 | -0.0044264 | 0.062982 | 0.060176 | 0.0020722 | -0.006633 | 63.588 | 63.6887 | 0.55389 | -59.3536 | 63.7527 | -59.23 | -59.2987 | -59.0836 | 2.6917 | -59.4498 | 63.7619 | 63.6932 | -59.3399 | -59.3948 | -0.064087 | -0.13275 | 0.045777 | 122.8546 | -0.18768 | -0.054932 | -0.11902 | -0.17395 | -0.22888 | 0.054932 | 0.082398 | -0.28381 | -0.054932 | -0.013733 | 122.9187 | 122.7539 | 59.7198 | -123.0057 | 122.9279 | 122.8592 | 61.8576 | -123.1018
1167.0156 | 122.9782 | -59.1934 | 63.6932 | 0.16006 | 0.01514 | 0.063337 | 0.068167 | 0.13057 | -0.0026405 | -0.0040867 | 0.44235 | -0.00464 | 0.062555 | 0.059748 | 0.0031402 | -0.0072738 | 63.6337 | 63.6108 | 0.56763 | -59.3124 | 63.7619 | -59.2255 | -59.3216 | -59.1202 | 2.5589 | -59.4589 | 63.739 | 63.6841 | -59.3216 | -59.4086 | -0.032044 | -0.12817 | 0.068665 | 122.8043 | -0.11902 | 0.009155 | -0.059509 | -0.12817 | -0.21515 | 0.045777 | 0.073242 | -0.2655 | -0.050354 | -0.009155 | 122.9553 | 122.8271 | 59.761 | -123.0148 | 122.9324 | 122.8775 | 61.7523 | -123.1018
1168.0156 | 122.9919 | -59.1522 | 63.7161 | -0.045929 | 0.013858 | 0.068037 | 0.072867 | 0.1327 | 0.0024865 | -0.0032321 | 0.037995 | -0.0061352 | 0.064478 | 0.058253 | 0.0048492 | -0.0077012 | 63.6337 | 63.7161 | 0.59967 | -59.3216 | 63.7848 | -59.1843 | -59.2621 | -59.0561 | 2.1835 | -59.4131 | 63.7619 | 63.6978 | -59.2941 | -59.3903 | -0.032043 | -0.10986 | 0.068665 | 122.8683 | -0.16937 | -0.059509 | -0.082397 | -0.14191 | -0.23804 | 0.045777 | 0.096131 | -0.26093 | -0.022888 | -0.01831 | 122.937 | 122.7859 | 59.7519 | -122.9782 | 122.9141 | 122.85 | 61.3358 | -123.1064
1169.0156 | 122.9919 | -59.1522 | 63.7436 | 0.16769 | 0.013003 | 0.066541 | 0.069235 | 0.13121 | 0.0018457 | -0.0028049 | 0.16769 | -0.0052808 | 0.068964 | 0.062098 | 0.0029266 | -0.0091966 | 63.5513 | 63.6108 | 0.68207 | -59.3811 | 63.7894 | -59.198 | -59.2941 | -58.9142 | 1.6571 | -59.4864 | 63.7665 | 63.7527 | -59.3262 | -59.3674 | -0.045776 | -0.14191 | 0.045777 | 122.7631 | -0.22888 | -0.086976 | -0.19226 | -0.17395 | -0.21515 | 0.022888 | 0.23804 | -0.33417 | -0.11902 | 0.009156 | 122.9416 | 122.7036 | 59.8343 | -123.0377 | 122.9187 | 122.905 | 60.8093 | -123.111
1170.0156 | 122.9736 | -59.1843 | 63.7161 | 0.015106 | 0.014499 | 0.069746 | 0.070944 | 0.13249 | 0.0022729 | -0.0032321 | 0.045624 | -0.0050672 | 0.063196 | 0.060603 | 0.0039948 | -0.005565 | 63.6108 | 63.6932 | 0.57678 | -59.3536 | 63.7665 | -59.1751 | -59.2758 | -59.0881 | 1.2863 | -59.4315 | 63.7711 | 63.7299 | -59.3262 | -59.3903 | 0.009155 | -0.091553 | 0.050354 | 122.8775 | -0.16937 | -0.07782 | -0.10528 | -0.14191 | -0.20599 | 0.054932 | 0.09613 | -0.24719 | -0.041199 | 0.013733 | 122.9507 | 122.7951 | 59.761 | -122.9919 | 122.9553 | 122.9141 | 60.4706 | -123.1064
1171.0156 | 122.9919 | -59.1751 | 63.6978 | -0.015411 | 0.013431 | 0.066328 | 0.070944 | 0.128 | 0.0020593 | -0.0045139 | 0.18295 | -0.0042126 | 0.064905 | 0.060176 | 0.0033538 | -0.0072738 | 63.5696 | 63.6246 | 0.50812 | -59.3445 | 63.7848 | -59.2163 | -59.2896 | -59.1385 | 1.0437 | -59.4681 | 63.7665 | 63.7207 | -59.3399 | -59.3994 | -0.041199 | -0.11444 | 0.086975 | 122.7997 | -0.16937 | -0.054931 | -0.12817 | -0.1648 | -0.2243 | 0.068664 | 0.036621 | -0.29297 | -0.068665 | 0.022888 | 122.9599 | 122.7448 | 59.6832 | -122.9874 | 122.9416 | 122.8958 | 60.2188 | -123.0972
1172.0156 | 123.0377 | -59.1385 | 63.7436 | -0.068817 | 0.014499 | 0.06825 | 0.070944 | 0.1295 | 0.0012047 | -0.0053683 | -1.1217 | -0.0033582 | 0.065759 | 0.058467 | 0.0016448 | -0.0062058 | 63.6566 | 63.7436 | 0.64545 | -59.2941 | 63.8077 | -59.1934 | -59.2346 | -59.0195 | 1.1169 | -59.3719 | 63.7802 | 63.7482 | -59.2987 | -59.3582 | -0.054931 | -0.09613 | 0.064087 | 122.8821 | -0.15564 | -0.059509 | -0.086975 | -0.16022 | -0.21973 | 0.036621 | 0.11902 | -0.23346 | -0.013733 | 0.004578 | 122.9462 | 122.7951 | 59.7839 | -122.9782 | 122.9187 | 122.8867 | 60.2554 | -123.1018
1173.0156 | 122.9782 | -59.166 | 63.7115 | 0.13718 | 0.014285 | 0.067396 | 0.068381 | 0.13163 | -0.00050425 | -0.0045139 | 0.61783 | -0.0065626 | 0.064264 | 0.058894 | 0.0037812 | -0.0064194 | 63.5605 | 63.62 | 0.63629 | -59.2987 | 63.7619 | -59.2392 | -59.3033 | -59.1339 | 1.0117 | -59.436 | 63.7802 | 63.7161 | -59.3308 | -59.404 | -0.073242 | -0.13733 | 0.050354 | 122.7859 | -0.13275 | 0.004578 | -0.15106 | -0.1648 | -0.23804 | 0.068664 | 0.032044 | -0.27008 | -0.032043 | 0.004577 | 122.9279 | 122.7264 | 59.8022 | -123.0148 | 122.9462 | 122.8821 | 60.1776 | -123.1155
1174.0156 | 123.0698 | -59.1248 | 63.6841 | 0.0914 | 0.0074491 | 0.068678 | 0.07009 | 0.12779 | -0.0088355 | -0.0057957 | 0.28976 | -0.007417 | 0.061487 | 0.056758 | 0.00036322 | -0.003856 | 63.5788 | 63.7344 | 0.77362 | -59.3582 | 63.7436 | -59.1934 | -59.2621 | -59.0469 | 1.0437 | -59.3628 | 63.7115 | 63.6841 | -59.2896 | -59.3765 | -0.068664 | -0.13733 | 0.059509 | 122.8592 | -0.23346 | -0.09613 | -0.10529 | -0.1648 | -0.25177 | 0.027466 | 0.07782 | -0.23804 | 0.013733 | 0 | 122.8683 | 122.7036 | 59.8984 | -122.9462 | 122.8363 | 122.8088 | 60.1685 | -123.0606
1175.0156 | 122.9965 | -59.1431 | 63.7344 | 0.015106 | 0.013003 | 0.067182 | 0.072653 | 0.13057 | 0.0046227 | -0.0036595 | 0.13718 | -0.003999 | 0.064905 | 0.060389 | 0.0050628 | -0.0089828 | 63.6154 | 63.6566 | 0.58136 | -59.3399 | 63.8077 | -59.166 | -59.2712 | -59.0561 | 0.66376 | -59.5825 | 63.739 | 63.6978 | -59.3033 | -59.3628 | -0.022889 | -0.12817 | 0.073242 | 122.7997 | -0.19684 | -0.068665 | -0.11902 | -0.16022 | -0.21973 | 0.004578 | 0.086975 | -0.43945 | -0.21973 | -0.036621 | 122.9507 | 122.7585 | 59.7244 | -123.0057 | 122.8821 | 122.8409 | 59.8068 | -123.0972
1176.0156 | 123.0377 | -59.0698 | 63.7894 | 1.2434 | 0.013858 | 0.069319 | 0.072012 | 0.13099 | 0.00013675 | -0.0040867 | -0.00015237 | -0.008058 | 0.061701 | 0.060176 | 0.0057038 | -0.0070602 | 63.7299 | 63.8123 | 0.59967 | -59.2484 | 63.8626 | -59.1339 | -59.1888 | -58.9783 | 0.97961 | -59.3308 | 63.8031 | 63.7711 | -59.2392 | -59.317 | -0.064087 | -0.11902 | 0.073242 | 122.8821 | -0.17853 | -0.059509 | -0.05951 | -0.16937 | -0.24719 | 0.013733 | 0.091553 | -0.26093 | -0.013733 | -0.018311 | 122.9324 | 122.7997 | 59.6695 | -122.9782 | 122.8729 | 122.8409 | 60.0494 | -123.1064
1177.0156 | 122.9919 | -59.111 | 63.7711 | 0.5339 | 0.013217 | 0.066969 | 0.07244 | 0.13035 | -0.00029045 | -0.0040867 | 0.13718 | -0.0054944 | 0.062128 | 0.059321 | 0.0024994 | -0.0064194 | 63.6703 | 63.7299 | 0.46234 | -59.2941 | 63.8443 | -59.1476 | -59.2117 | -59.0195 | 0.89264 | -59.3582 | 63.8443 | 63.7756 | -59.2484 | -59.3308 | -0.036621 | -0.10071 | 0.073242 | 122.8409 | -0.1831 | -0.082397 | -0.10071 | -0.13733 | -0.21973 | 0.073242 | 0.091553 | -0.24719 | -0.027465 | 0.004578 | 122.9553 | 122.7814 | 59.5734 | -122.9828 | 122.9553 | 122.8867 | 60.0037 | -123.1018
1178.0156 | 123.0103 | -59.079 | 63.8031 | -0.076447 | 0.013217 | 0.067396 | 0.073721 | 0.12864 | 0.0031273 | -0.0010959 | -0.045929 | -0.0052808 | 0.064691 | 0.059748 | 0.0033538 | -0.0062058 | 63.5605 | 63.7436 | 0.70038 | -59.2484 | 63.8397 | -59.1202 | -59.23 | -58.9737 | 1.0574 | -59.3308 | 63.8168 | 63.7848 | -59.2575 | -59.3262 | -0.041199 | -0.15106 | 0.036621 | 122.8226 | -0.16937 | -0.01831 | -0.24262 | -0.17853 | -0.24719 | 0.013732 | 0.10528 | -0.25177 | -0.004578 | -0.018311 | 122.9187 | 122.6395 | 59.7794 | -123.0331 | 122.8958 | 122.8638 | 60.1364 | -123.1293
1179.0156 | 123.1064 | -59.0561 | 63.7527 | 0.030365 | 0.0063809 | -0.035357 | 0.066458 | 0.12864 | -0.0084083 | -0.0062229 | 0.13718 | -0.005708 | 0.059992 | 0.060816 | 0.0024994 | -0.0064194 | 63.652 | 63.8031 | 0.80566 | -59.2712 | 63.8031 | -59.1385 | -59.2072 | -58.96 | 1.236 | -59.2758 | 63.7985 | 63.7482 | -59.23 | -59.2987 | -0.082398 | -0.15106 | 0.050354 | 122.8592 | -0.21515 | -0.064087 | -0.10071 | -0.17395 | -0.24262 | 0.045776 | 0.09613 | -0.21973 | 0.022888 | -0.004578 | 122.8592 | 122.7081 | 59.8618 | -122.9599 | 122.8546 | 122.8043 | 60.2921 | -123.0515
1180.0156 | 122.9965 | -59.1064 | 63.7619 | -0.053558 | 0.015353 | 0.068464 | 0.070517 | 0.12907 | 0.0039819 | -0.0049411 | 0.015106 | -0.0044264 | 0.065973 | 0.059535 | 0.0052764 | -0.0074876 | 63.6658 | 63.7436 | 0.82398 | -59.2941 | 63.8214 | -59.1476 | -59.23 | -59.0286 | 0.99792 | -59.3948 | 63.8168 | 63.7619 | -59.2804 | -59.3445 | -0.041199 | -0.1236 | 0.059509 | 122.85 | -0.18768 | -0.064086 | -0.096131 | -0.17395 | -0.23804 | 0.054931 | 0.07782 | -0.28839 | -0.050354 | 0 | 122.9279 | 122.7722 | 59.9304 | -122.9919 | 122.9233 | 122.8683 | 60.1044 | -123.1064
1181.0625 | 122.9965 | -59.1019 | 63.8123 | -0.29007 | 0.011081 | 0.070173 | 0.070944 | 0.13185 | -0.0015723 | -0.0017369 | -0.15274 | -0.0050672 | 0.062555 | 0.058894 | 0.0031402 | -0.0068466 | 63.6475 | 63.7573 | 0.7782 | -59.2484 | 63.8672 | -59.1568 | -59.2026 | -59.0057 | 1.4786 | -59.3399 | 63.8626 | 63.8123 | -59.2438 | -59.2987 | -0.054931 | -0.10071 | 0.054931 | 122.8592 | -0.14648 | -0.045776 | -0.16479 | -0.14191 | -0.19684 | 0.050354 | 0.096131 | -0.23804 | -0.041199 | 0 | 122.9691 | 122.7493 | 59.8801 | -123.0148 | 122.9645 | 122.9141 | 60.5804 | -123.111
1182.0156 | 123.0194 | -59.0927 | 63.7756 | -0.084076 | 0.014712 | 0.067823 | 0.070731 | 0.12971 | 0.0012047 | -0.0047275 | 0.045624 | -0.0052808 | 0.065332 | 0.058253 | 0.0039948 | -0.0081284 | 63.6932 | 63.7848 | 0.88348 | -59.2575 | 63.8443 | -59.1339 | -59.2163 | -59.0149 | 1.7212 | -59.3811 | 63.8351 | 63.7802 | -59.2346 | -59.3445 | -0.041199 | -0.1236 | 0.068664 | 122.8775 | -0.16479 | -0.041198 | -0.082398 | -0.14191 | -0.25177 | 0.059509 | 0.077819 | -0.28839 | -0.036622 | 0.004577 | 122.937 | 122.7859 | 59.9762 | -122.9919 | 122.9279 | 122.8729 | 60.8139 | -123.1201
1183.0156 | 122.9874 | -59.111 | 63.7619 | 0.12955 | 0.013217 | 0.066541 | 0.070303 | 0.12928 | 0.00099115 | -0.0051547 | 0.55679 | -0.005708 | 0.062982 | 0.058253 | 0.0018584 | -0.0057786 | 63.6292 | 63.6978 | 0.85144 | -59.3033 | 63.8351 | -59.1522 | -59.2667 | -59.0744 | 1.6846 | -59.3765 | 63.826 | 63.7527 | -59.2712 | -59.3399 | -0.041199 | -0.15564 | 0.073242 | 122.8088 | -0.19226 | -0.036621 | -0.13275 | -0.16022 | -0.22888 | 0.064087 | 0.036621 | -0.2655 | -0.036621 | -0.009155 | 122.9462 | 122.7402 | 59.9625 | -123.0286 | 122.937 | 122.8638 | 60.7956 | -123.1018
1184.0156 | 123.056 | -59.0561 | 63.739 | 0.16006 | 0.0085171 | 0.069319 | 0.064322 | 0.13035 | -0.0049903 | -0.0070773 | 0.34317 | -0.0072034 | 0.062128 | 0.059321 | 0.0022858 | -0.006633 | 63.7024 | 63.8306 | 0.83313 | -59.2484 | 63.7711 | -59.1476 | -59.1888 | -58.9371 | 1.6937 | -59.285 | 63.7527 | 63.7436 | -59.2255 | -59.2804 | -0.091553 | -0.13275 | 0.032043 | 122.8867 | -0.19226 | -0.059509 | -0.036621 | -0.16937 | -0.22431 | 0.013733 | 0.11902 | -0.22888 | -0.004577 | 0.004577 | 122.8271 | 122.7585 | 59.8892 | -122.9279 | 122.8088 | 122.7997 | 60.7498 | -123.0194
1185.0156 | 122.9736 | -59.1202 | 63.7711 | 0.16006 | 0.013431 | 0.06761 | 0.068381 | 0.1295 | 0.00056395 | -0.0028049 | 0.39658 | -0.0059216 | 0.060419 | 0.057826 | 0.0048492 | -0.008342 | 63.652 | 63.707 | 0.71411 | -59.285 | 63.8672 | -59.1293 | -59.2346 | -59.0378 | 1.0895 | -59.3491 | 63.8351 | 63.7939 | -59.2438 | -59.285 | -0.009155 | -0.11444 | 0.09613 | 122.8271 | -0.16479 | -0.050354 | -0.11902 | -0.1236 | -0.16479 | 0.064087 | 0.082397 | -0.22888 | -0.064087 | 0.022888 | 122.9874 | 122.7722 | 59.8343 | -123.0057 | 122.9553 | 122.9141 | 60.2097 | -123.056
1186.0156 | 123.1155 | -59.0286 | 63.7711 | 0.19058 | 0.0068081 | 0.067396 | 0.066885 | 0.12928 | -0.0024269 | -0.0040867 | 0.12955 | -0.006349 | 0.063837 | 0.060816 | 0.004422 | -0.006633 | 63.858 | 63.9175 | 0.80566 | -59.1797 | 63.7985 | -59.0744 | -59.166 | -58.9142 | 0.92468 | -59.2484 | 63.7985 | 63.7573 | -59.2026 | -59.2712 | -0.045777 | -0.13733 | 0.027466 | 122.9462 | -0.15106 | -0.013732 | 0.086975 | -0.17395 | -0.24262 | 0.027466 | 0.11444 | -0.21973 | 0.022888 | -0.013733 | 122.8271 | 122.8867 | 59.8343 | -122.937 | 122.8271 | 122.7859 | 59.9533 | -123.0423
1187.0156 | 123.0469 | -59.0515 | 63.7756 | 0.13718 | 0.011935 | 0.068464 | 0.072012 | 0.12993 | -0.0011451 | -0.0040867 | 0.26688 | -0.0050672 | 0.063837 | 0.058039 | 0.0031402 | -0.0064194 | 63.707 | 63.7482 | 0.70038 | -59.2667 | 63.8489 | -59.1019 | -59.1843 | -58.9554 | 1.4328 | -59.3262 | 63.8214 | 63.7756 | -59.2392 | -59.2987 | -0.050354 | -0.13275 | 0.073242 | 122.7997 | -0.21515 | -0.082398 | -0.068665 | -0.18768 | -0.24719 | 0.045776 | 0.096131 | -0.27466 | -0.027466 | 0 | 122.9004 | 122.7585 | 59.7519 | -122.9599 | 122.8729 | 122.8271 | 60.4843 | -123.0743
1188.0156 | 122.9599 | -59.1064 | 63.8031 | 0.030365 | 0.013217 | 0.067182 | 0.068594 | 0.13185 | 0.0020593 | -0.0030185 | 0.09903 | -0.0069898 | 0.064051 | 0.059321 | 0.0037812 | -0.0094102 | 63.6932 | 63.7482 | 0.86517 | -59.2804 | 63.8351 | -59.1156 | -59.2072 | -59.024 | 1.6846 | -59.3857 | 63.8397 | 63.7985 | -59.2621 | -59.3353 | -0.009156 | -0.10071 | 0.032043 | 122.8546 | -0.17395 | -0.073243 | -0.10986 | -0.15564 | -0.22888 | 0.036621 | 0.082397 | -0.27924 | -0.050354 | -0.004578 | 122.9416 | 122.7997 | 59.9716 | -123.0103 | 122.9462 | 122.905 | 60.791 | -123.1384
1189.0156 | 123.0606 | -59.0607 | 63.739 | -0.084076 | 0.0040311 | 0.069746 | 0.066458 | 0.13014 | -0.0079811 | -0.0066501 | 0.015106 | -0.0095532 | 0.058924 | 0.060603 | 0.0012176 | -0.005565 | 63.7619 | 63.9267 | 1.03 | -59.2026 | 63.8214 | -59.1248 | -59.1751 | -58.9691 | 2.8748 | -59.1476 | 63.8992 | 63.7756 | -59.2209 | -59.2804 | -0.064087 | -0.11444 | 0.082397 | 122.9874 | -0.14191 | -0.027466 | 0.022888 | -0.16022 | -0.21973 | 0.16022 | 0.091553 | -0.086975 | 0.13275 | 0.036621 | 122.8821 | 122.8226 | 60.0906 | -122.9141 | 122.9599 | 122.8363 | 61.9354 | -123.0194
1190.0156 | 122.9874 | -59.1293 | 63.7848 | 0.060882 | 0.014285 | 0.067182 | 0.069663 | 0.1327 | 0.00077755 | -0.0038731 | 0.015106 | -0.0061352 | 0.064905 | 0.060389 | 0.004422 | -0.0087692 | 63.652 | 63.7115 | 0.87891 | -59.2896 | 63.8626 | -59.1476 | -59.2392 | -59.0652 | 2.4033 | -59.4223 | 63.826 | 63.7802 | -59.2529 | -59.3399 | -0.018311 | -0.10986 | 0.07782 | 122.8409 | -0.16022 | -0.050354 | -0.13275 | -0.1236 | -0.21057 | 0.041199 | 0.064086 | -0.29297 | -0.082397 | -0.004578 | 122.9919 | 122.7814 | 60.0082 | -123.024 | 122.9553 | 122.9095 | 61.5326 | -123.1247
1191.0156 | 123.0972 | -59.1064 | 63.6887 | 0.22873 | 0.011508 | 0.069532 | 0.071799 | 0.13163 | -0.00029045 | -0.0043003 | 0.24399 | -0.0065626 | 0.062769 | 0.059321 | 0.0020722 | -0.008342 | 63.7024 | 63.7711 | 1.0712 | -59.2758 | 63.7802 | -59.1797 | -59.2438 | -58.9417 | 2.7008 | -59.2987 | 63.7482 | 63.6887 | -59.2621 | -59.317 | -0.073242 | -0.13733 | 0.091552 | 122.8775 | -0.16937 | -0.032044 | 0.013733 | -0.15564 | -0.21057 | 0.059509 | 0.16479 | -0.19226 | 0.018311 | 0 | 122.8867 | 122.8088 | 60.1776 | -122.9324 | 122.8546 | 122.7951 | 61.8073 | -123.0057
1192.0156 | 122.9599 | -59.1339 | 63.739 | 0.0074768 | 0.014499 | 0.06761 | 0.069876 | 0.12971 | 0.0016321 | -0.0047275 | 0.12192 | -0.0031446 | 0.063837 | 0.060176 | 0.0050628 | -0.0081284 | 63.6337 | 63.7161 | 1.1032 | -59.3033 | 63.8077 | -59.166 | -59.2529 | -59.0607 | 2.9938 | -59.4223 | 63.8031 | 63.7619 | -59.2667 | -59.3628 | -0.032044 | -0.11902 | 0.068664 | 122.85 | -0.16937 | -0.050354 | -0.10529 | -0.13275 | -0.22888 | 0.064087 | 0.073242 | -0.28839 | -0.059509 | 0.022888 | 122.9416 | 122.7676 | 60.2371 | -122.9919 | 122.937 | 122.8958 | 62.1277 | -123.1018
1193.0156 | 123.0286 | -59.1019 | 63.7115 | 0.14481 | 0.011722 | 0.066755 | 0.069449 | 0.12928 | 0.00035035 | -0.0049411 | 0.19821 | -0.0067762 | 0.064478 | 0.059535 | 0.004422 | -0.0087692 | 63.6292 | 63.6841 | 1.1673 | -59.3216 | 63.7985 | -59.2026 | -59.2712 | -59.0103 | 3.1677 | -59.3765 | 63.739 | 63.7253 | -59.2758 | -59.3536 | -0.10071 | -0.16937 | 0.086975 | 122.7859 | -0.21973 | -0.050354 | -0.082398 | -0.17395 | -0.25177 | 0.027466 | 0.091553 | -0.27466 | -0.022888 | 0.013733 | 122.9004 | 122.731 | 60.2692 | -122.9828 | 122.8409 | 122.8271 | 62.2696 | -123.0652
1194.0156 | 123.0881 | -59.1156 | 63.6978 | 0.045624 | 0.0076627 | 0.0706 | 0.070517 | 0.12843 | -0.0062721 | -0.0047275 | 0.10666 | -0.0097668 | 0.064051 | 0.058894 | -0.0011322 | -0.005565 | 63.6246 | 63.7665 | 1.2634 | -59.2941 | 63.7848 | -59.1705 | -59.2346 | -58.992 | 3.4195 | -59.3033 | 63.7482 | 63.7115 | -59.2667 | -59.3582 | -0.054931 | -0.11902 | 0.086975 | 122.8821 | -0.17853 | -0.059509 | -0.073242 | -0.15106 | -0.24261 | 0.050354 | 0.1236 | -0.18768 | 0.054931 | 0.013733 | 122.9004 | 122.7402 | 60.379 | -122.9324 | 122.8638 | 122.8271 | 62.5351 | -123.056
1195.0156 | 123.1293 | -59.1293 | 63.6429 | 0.19058 | 0.0087307 | 0.068037 | 0.069235 | 0.13078 | -0.0011451 | -0.0045139 | 0.23636 | -0.007417 | 0.062342 | 0.05868 | 0.0042084 | -0.0074876 | 63.6703 | 63.7665 | 1.1719 | -59.2896 | 63.7527 | -59.1705 | -59.2667 | -58.992 | 3.5706 | -59.3353 | 63.7207 | 63.6292 | -59.2804 | -59.3399 | -0.041199 | -0.13733 | 0.10986 | 122.8958 | -0.16022 | -0.022888 | 0.027466 | -0.15106 | -0.21057 | 0.07782 | 0.13733 | -0.20599 | 0.004578 | -0.013733 | 122.8821 | 122.7997 | 60.3012 | -122.9095 | 122.85 | 122.7585 | 62.6999 | -122.9828
1196.0156 | 123.0057 | -59.1843 | 63.6932 | 0.15244 | 0.013217 | 0.061414 | 0.069663 | 0.12993 | 0.00099115 | -0.0015231 | 0.25925 | -0.0050672 | 0.065973 | 0.059962 | 0.0050628 | -0.0087692 | 63.4872 | 63.7344 | 1.062 | -59.3582 | 63.7894 | -59.1934 | -59.285 | -59.0836 | 3.6163 | -59.436 | 63.739 | 63.7161 | -59.3216 | -59.3674 | -0.009155 | -0.10071 | 0.096131 | 122.9187 | -0.17395 | -0.073242 | -0.20599 | -0.13733 | -0.18311 | 0.045777 | 0.10071 | -0.25177 | -0.068664 | 0.022888 | 122.9736 | 122.6715 | 60.2463 | -122.9782 | 122.9233 | 122.9004 | 62.8006 | -123.0606
1197.0156 | 123.0789 | -59.166 | 63.588 | 0.40421 | 0.011294 | 0.068891 | 0.065817 | 0.13078 | 0.00035035 | -0.0030185 | 0.31265 | -0.0078442 | 0.064264 | 0.057826 | 0.0024994 | -0.0074876 | 63.6475 | 63.7527 | 1.0391 | -59.3033 | 63.7115 | -59.2163 | -59.2621 | -58.9966 | 4.0787 | -59.3399 | 63.6612 | 63.6612 | -59.317 | -59.3719 | -0.050354 | -0.09613 | 0.1236 | 122.9187 | -0.13733 | -0.041199 | 0.059509 | -0.15106 | -0.20599 | 0.073242 | 0.16937 | -0.17395 | 0.032043 | 0.073242 | 122.8775 | 122.8134 | 60.2051 | -122.85 | 122.8271 | 122.8271 | 63.2446 | -122.9599
1198.0156 | 123.0469 | -59.1431 | 63.6475 | 0.16006 | 0.012149 | 0.066541 | 0.069235 | 0.13014 | 0.00099115 | -0.0043003 | 0.23636 | -0.0061352 | 0.064905 | 0.057398 | 0.0039948 | -0.0062058 | 63.588 | 63.6795 | 0.9201 | -59.3491 | 63.739 | -59.2392 | -59.2941 | -59.0332 | 4.2435 | -59.4131 | 63.707 | 63.6703 | -59.3124 | -59.3857 | -0.096131 | -0.15106 | 0.091553 | 122.8226 | -0.20599 | -0.054932 | -0.059509 | -0.16937 | -0.24262 | 0.059509 | 0.10986 | -0.27008 | -0.027466 | 0.022888 | 122.8821 | 122.731 | 60.0632 | -122.9416 | 122.85 | 122.8134 | 63.3865 | -123.0331
1199.0156 | 123.1567 | -59.1843 | 63.6154 | 0.015106 | 0.013003 | 0.067396 | 0.067954 | 0.12886 | -0.00093145 | -0.0017369 | 0.28976 | -0.0065626 | 0.061487 | 0.059535 | 0.0042084 | -0.0079148 | 63.6246 | 63.7573 | 0.99335 | -59.3124 | 63.7024 | -59.2072 | -59.2804 | -59.0103 | 4.7104 | -59.3445 | 63.6749 | 63.6292 | -59.3216 | -59.3948 | -0.022888 | -0.096131 | 0.086976 | 122.9416 | -0.12817 | -0.032043 | 0.009156 | -0.13733 | -0.21057 | 0.05951 | 0.17395 | -0.16022 | 0.050354 | 0.013733 | 122.8867 | 122.8088 | 60.1776 | -122.8958 | 122.8592 | 122.8134 | 63.8947 | -123.0103
1200.0156 | 123.0698 | -59.1431 | 63.6703 | 0.19821 | 0.013431 | 0.06761 | 0.069449 | 0.12928 | -0.00029045 | -0.0045139 | 0.22873 | -0.0059216 | 0.064691 | 0.058894 | 0.004422 | -0.008342 | 63.5925 | 63.7024 | 0.97504 | -59.3582 | 63.7802 | -59.2117 | -59.2804 | -59.024 | 4.5319 | -59.3811 | 63.7161 | 63.652 | -59.3262 | -59.3903 | -0.068665 | -0.13733 | 0.10986 | 122.8455 | -0.21515 | -0.077819 | -0.07782 | -0.18311 | -0.24719 | 0.045776 | 0.11902 | -0.23804 | 0.009155 | -0.01831 | 122.9233 | 122.7356 | 60.1181 | -122.9507 | 122.8592 | 122.7951 | 63.6749 | -123.0606
1201.0156 | 123.0789 | -59.1614 | 63.652 | 0.25925 | 0.0089443 | 0.068037 | 0.068167 | 0.12886 | -0.0047767 | -0.0040867 | 0.27451 | -0.0072034 | 0.061487 | 0.058039 | 0.0029266 | -0.008342 | 63.652 | 63.7802 | 1.1902 | -59.3216 | 63.7161 | -59.2163 | -59.2712 | -58.992 | 4.1611 | -59.3491 | 63.7024 | 63.6383 | -59.3079 | -59.3903 | -0.054932 | -0.10986 | 0.064086 | 122.9416 | -0.16022 | -0.050354 | 0 | -0.14648 | -0.22888 | 0.050354 | 0.16937 | -0.18768 | 0.041199 | -0.013733 | 122.8775 | 122.8134 | 60.3516 | -122.9233 | 122.8638 | 122.7997 | 63.3224 | -123.0423
1202.0156 | 123.0927 | -59.1431 | 63.6749 | 0.17532 | 0.012149 | 0.069105 | 0.069876 | 0.12843 | -0.00050425 | -0.0025913 | 0.24399 | -0.0065626 | 0.063837 | 0.059321 | 0.0059174 | -0.0074876 | 63.5925 | 63.707 | 1.3458 | -59.3445 | 63.7344 | -59.2117 | -59.3033 | -59.0378 | 3.6713 | -59.3994 | 63.707 | 63.6337 | -59.3262 | -59.3811 | -0.068665 | -0.16022 | 0.059509 | 122.85 | -0.20142 | -0.041198 | -0.082398 | -0.18311 | -0.23804 | 0.032043 | 0.10528 | -0.25635 | -0.01831 | -0.041199 | 122.8775 | 122.7356 | 60.4889 | -122.9782 | 122.85 | 122.7768 | 62.8143 | -123.056
1203.0156 | 123.0606 | -59.1156 | 63.6887 | 0.18295 | 0.0070217 | 0.068678 | 0.069449 | 0.13099 | -0.0034949 | -0.0043003 | 0.25925 | -0.0082716 | 0.062769 | 0.058039 | 0.0033538 | -0.0064194 | 63.6749 | 63.8123 | 1.4877 | -59.2804 | 63.7436 | -59.1568 | -59.23 | -58.9462 | 3.4744 | -59.2941 | 63.7527 | 63.6703 | -59.2804 | -59.3308 | -0.041198 | -0.11444 | 0.054931 | 122.9279 | -0.1648 | -0.050354 | -0.013733 | -0.1648 | -0.21515 | 0.064087 | 0.16937 | -0.17853 | 0.036622 | -0.018311 | 122.8592 | 122.7905 | 60.6033 | -122.9187 | 122.8683 | 122.7859 | 62.59 | -123.0194
1204.0156 | 123.0972 | -59.1385 | 63.7024 | 0.19821 | 0.012362 | 0.065687 | 0.071585 | 0.13185 | 0.0022729 | -0.0023777 | 0.27451 | -0.0042126 | 0.064478 | 0.059107 | 0.0024994 | -0.0091966 | 63.6429 | 63.7299 | 1.5289 | -59.3216 | 63.7802 | -59.1888 | -59.2667 | -58.9737 | 3.7994 | -59.3216 | 63.7482 | 63.6703 | -59.2941 | -59.3582 | -0.050354 | -0.12817 | 0.077819 | 122.8683 | -0.1831 | -0.054931 | -0.05951 | -0.15564 | -0.21973 | 0.045776 | 0.16479 | -0.1831 | 0.036621 | -0.032044 | 122.9187 | 122.7814 | 60.6674 | -122.9691 | 122.8867 | 122.8088 | 62.9379 | -123.0606
1205.0156 | 123.0743 | -59.1339 | 63.6841 | 0.12955 | 0.0050991 | 0.069319 | 0.070517 | 0.12928 | -0.0039221 | -0.0051547 | 0.17532 | -0.0069898 | 0.064051 | 0.058894 | 0.0024994 | -0.0051376 | 63.5925 | 63.7711 | 1.6983 | -59.3262 | 63.739 | -59.1797 | -59.2804 | -59.0057 | 4.5319 | -59.3491 | 63.7344 | 63.6612 | -59.2712 | -59.3628 | -0.045776 | -0.14649 | 0.054932 | 122.905 | -0.19226 | -0.045776 | -0.091553 | -0.13733 | -0.22888 | 0.050354 | 0.12817 | -0.21515 | 0.013733 | -0.022888 | 122.8729 | 122.7264 | 60.8322 | -122.9645 | 122.8683 | 122.7951 | 63.6658 | -123.0469
1206.0156 | 123.1018 | -59.1568 | 63.6292 | 0.15244 | 0.013003 | 0.068037 | 0.071372 | 0.13057 | 0.0012047 | -0.0047275 | 0.2211 | -0.0061352 | 0.063623 | 0.059748 | 0.0042084 | -0.0085556 | 63.5971 | 63.6932 | 1.8311 | -59.3628 | 63.707 | -59.2346 | -59.3079 | -59.0469 | 4.5136 | -59.3811 | 63.7115 | 63.5788 | -59.3079 | -59.3903 | -0.07782 | -0.15106 | 0.07782 | 122.85 | -0.20599 | -0.054932 | -0.032043 | -0.15106 | -0.23346 | 0.082398 | 0.10986 | -0.22431 | 0.009155 | -0.050354 | 122.8638 | 122.7539 | 60.9879 | -122.937 | 122.8683 | 122.7356 | 63.6703 | -123.0194
1207.0156 | 123.111 | -59.1339 | 63.6658 | 0.13718 | 0.0048855 | 0.067182 | 0.069663 | 0.12843 | -0.0032813 | -0.0047275 | 0.25162 | -0.0076306 | 0.060846 | 0.059107 | 0.00057682 | -0.0053512 | 63.6154 | 63.707 | 1.8631 | -59.3491 | 63.739 | -59.1934 | -59.2804 | -59.0332 | 4.7012 | -59.3628 | 63.7115 | 63.6703 | -59.2804 | -59.3582 | -0.059509 | -0.14649 | 0.073243 | 122.8409 | -0.21515 | -0.068664 | -0.050354 | -0.14649 | -0.2243 | 0.045777 | 0.10071 | -0.22888 | -0.004578 | 0.004578 | 122.8729 | 122.7493 | 60.997 | -122.9462 | 122.8455 | 122.8043 | 63.8351 | -123.024
1208.0156 | 123.1155 | -59.1522 | 63.6292 | 0.19058 | 0.010013 | 0.068891 | 0.070517 | 0.12864 | -0.00029045 | -0.0062229 | 0.030365 | -0.0067762 | 0.063623 | 0.059748 | 0.006131 | -0.0074876 | 63.6154 | 63.913 | 1.9821 | -59.3399 | 63.7115 | -59.1614 | -59.2621 | -58.9874 | 4.7516 | -59.3353 | 63.6612 | 63.6063 | -59.2941 | -59.3811 | -0.009155 | -0.10986 | 0.082398 | 123.0652 | -0.18768 | -0.07782 | -0.013733 | -0.14191 | -0.22888 | 0.032044 | 0.1648 | -0.1831 | 0.045777 | -0.022888 | 122.8638 | 122.7676 | 61.1343 | -122.8912 | 122.8134 | 122.7585 | 63.9038 | -123.0103
1209.0156 | 123.0606 | -59.166 | 63.6292 | 0.083771 | 0.0061673 | 0.070173 | 0.067954 | 0.12758 | -0.0039221 | -0.0075047 | 0.14481 | -0.0059216 | 0.061273 | 0.056117 | 0.0024994 | -0.0094102 | 63.588 | 63.7115 | 1.8494 | -59.3582 | 63.7161 | -59.2392 | -59.2712 | -59.0515 | 4.866 | -59.3811 | 63.6887 | 63.6108 | -59.3262 | -59.4131 | -0.073242 | -0.10529 | 0.086975 | 122.8775 | -0.19226 | -0.086975 | -0.041198 | -0.16022 | -0.24719 | 0.05951 | 0.11444 | -0.21515 | 0.032043 | -0.01831 | 122.8821 | 122.7539 | 61.0153 | -122.9004 | 122.8546 | 122.7768 | 64.032 | -123.0423
1210.0156 | 123.111 | -59.166 | 63.6337 | 0.19058 | 0.0091581 | 0.065046 | 0.070944 | 0.13185 | -0.00093145 | -0.0040867 | 0.25925 | -0.0084852 | 0.062555 | 0.06103 | 0.0046356 | -0.0089828 | 63.5788 | 63.8214 | 1.8814 | -59.3308 | 63.707 | -59.2163 | -59.2667 | -58.9966 | 4.8889 | -59.3628 | 63.6795 | 63.6017 | -59.3308 | -59.4131 | -0.050354 | -0.10071 | 0.073242 | 122.9874 | -0.1648 | -0.064087 | -0.054932 | -0.1648 | -0.24719 | 0.045776 | 0.16937 | -0.19684 | 0.050354 | -0.032043 | 122.8729 | 122.7448 | 61.0474 | -122.9004 | 122.8455 | 122.7676 | 64.0549 | -123.0469
1211.0156 | 123.1476 | -59.1934 | 63.6475 | 0.076141 | 0.0036039 | 0.068037 | 0.068167 | 0.12928 | -0.0043495 | -0.0064365 | 0.13718 | -0.0097668 | 0.060419 | 0.059321 | 0.0031402 | -0.0077012 | 63.5834 | 63.6932 | 1.8127 | -59.3719 | 63.7115 | -59.2209 | -59.3033 | -59.0469 | 4.6326 | -59.3903 | 63.6703 | 63.62 | -59.3445 | -59.3994 | -0.027466 | -0.10986 | 0.064087 | 122.8867 | -0.17853 | -0.068664 | -0.064087 | -0.15106 | -0.20599 | 0.022888 | 0.14648 | -0.19684 | 0.009155 | -0.027466 | 122.905 | 122.7768 | 61.0062 | -122.9507 | 122.8638 | 122.8134 | 63.826 | -123.0469
1212.0156 | 123.1064 | -59.1751 | 63.5834 | 1.9377 | 0.011508 | 0.067823 | 0.071158 | 0.13292 | 0.00056395 | -0.0043003 | 0.19058 | -0.0065626 | 0.062769 | 0.060603 | 0.006131 | -0.0079148 | 63.6383 | 63.7711 | 1.8127 | -59.3536 | 63.6749 | -59.2255 | -59.3033 | -59.0149 | 4.985 | -59.3903 | 63.6612 | 63.5513 | -59.3582 | -59.4131 | -0.050354 | -0.12817 | 0.091553 | 122.9462 | -0.17853 | -0.050354 | 0.054932 | -0.18311 | -0.23804 | 0.07782 | 0.16022 | -0.21515 | 0.022888 | -0.032043 | 122.85 | 122.8134 | 60.9879 | -122.8867 | 122.8363 | 122.7264 | 64.1602 | -122.9965
1213.0156 | 123.0972 | -59.1934 | 63.6154 | 0.16769 | 0.0055265 | 0.067823 | 0.069876 | 0.12886 | -0.00093145 | -0.0066501 | 0.076141 | -0.0072034 | 0.060633 | 0.06103 | 0.0029266 | -0.0059922 | 63.5605 | 63.6841 | 1.7807 | -59.3903 | 63.6932 | -59.2575 | -59.317 | -59.0881 | 5.1041 | -59.4223 | 63.6612 | 63.5559 | -59.3719 | -59.4269 | -0.064087 | -0.1236 | 0.07782 | 122.8775 | -0.19684 | -0.073242 | -0.054931 | -0.17853 | -0.23346 | 0.045777 | 0.10529 | -0.22888 | 0.004578 | -0.059509 | 122.8867 | 122.7539 | 60.9741 | -122.9324 | 122.8546 | 122.7493 | 64.2975 | -123.0423
1214.0156 | 123.0515 | -59.2117 | 63.5788 | 0.13718 | 0.0070217 | 0.069746 | 0.071799 | 0.128 | 0.00013675 | -0.0053683 | 0.30502 | -0.007417 | 0.064478 | 0.058039 | 0.0037812 | -0.0059922 | 63.5925 | 63.7207 | 1.8448 | -59.3948 | 63.6612 | -59.2484 | -59.3353 | -59.0698 | 5.0446 | -59.436 | 63.6383 | 63.5422 | -59.3903 | -59.4543 | -0.036621 | -0.1236 | 0.082398 | 122.9324 | -0.1831 | -0.059509 | 0.013733 | -0.17853 | -0.24262 | 0.05951 | 0.14191 | -0.2243 | 0.018311 | -0.036621 | 122.8729 | 122.8043 | 61.0565 | -122.9141 | 122.85 | 122.7539 | 64.2563 | -123.0331
1215.0156 | 123.0835 | -59.2117 | 63.6292 | -0.37399 | 0.0065945 | 0.06825 | 0.067526 | 0.12672 | -0.00050425 | -0.0049411 | 0.09903 | -0.0082716 | 0.061914 | 0.057826 | 0.0037812 | -0.0094102 | 63.5239 | 63.6749 | 1.918 | -59.3857 | 63.6887 | -59.285 | -59.317 | -59.079 | 4.7516 | -59.3903 | 63.6795 | 63.5605 | -59.3674 | -59.4177 | -0.073242 | -0.10529 | 0.05951 | 122.8867 | -0.17395 | -0.068664 | -0.10529 | -0.15564 | -0.20599 | 0.050354 | 0.13275 | -0.17853 | 0.027466 | -0.068664 | 122.9004 | 122.7356 | 61.1298 | -122.9462 | 122.8912 | 122.7722 | 63.9633 | -123.0469
1216.0156 | 123.0698 | -59.2072 | 63.5513 | 0.12192 | 0.0085171 | 0.067182 | 0.069235 | 0.12843 | -0.0028541 | -0.0036595 | 0.2211 | -0.0059216 | 0.064691 | 0.056971 | 0.0031402 | -0.0072738 | 63.5605 | 63.6795 | 2.1011 | -59.4223 | 63.6154 | -59.2987 | -59.3628 | -59.0836 | 4.2526 | -59.4498 | 63.6246 | 63.5056 | -59.4086 | -59.4727 | -0.091553 | -0.15564 | 0.064086 | 122.8867 | -0.21515 | -0.059509 | 0.009155 | -0.20142 | -0.2655 | 0.073242 | 0.1236 | -0.24262 | 0.022888 | -0.045777 | 122.8226 | 122.7676 | 61.3083 | -122.9141 | 122.8317 | 122.7127 | 63.4598 | -123.024
1217.0156 | 123.0881 | -59.2346 | 63.5788 | -0.0077822 | 0.0059537 | 0.0706 | 0.073508 | 0.12907 | -0.0011451 | -0.0057957 | 0.060883 | -0.0078442 | 0.059778 | 0.057612 | 0.00036322 | -0.0062058 | 63.5193 | 63.6383 | 2.2385 | -59.4131 | 63.6612 | -59.3124 | -59.3536 | -59.1019 | 4.4037 | -59.4406 | 63.6429 | 63.5422 | -59.3948 | -59.4635 | -0.07782 | -0.11902 | 0.082398 | 122.8729 | -0.17853 | -0.059509 | -0.059509 | -0.16022 | -0.22888 | 0.064087 | 0.13275 | -0.20599 | 0.022888 | -0.036621 | 122.8958 | 122.7539 | 61.4731 | -122.9324 | 122.8775 | 122.7768 | 63.6383 | -123.0423
1218.0156 | 123.0606 | -59.2117 | 63.5834 | 0.12192 | 0.0033901 | 0.067823 | 0.066885 | 0.13249 | -0.00093145 | -0.0047275 | 0.13718 | -0.0050672 | 0.060419 | 0.057826 | 0.00079042 | -0.0087692 | 63.5147 | 63.6566 | 2.4582 | -59.436 | 63.6429 | -59.2987 | -59.3811 | -59.1019 | 4.2755 | -59.4681 | 63.6108 | 63.5056 | -59.3994 | -59.4681 | -0.086975 | -0.16937 | 0.059509 | 122.8683 | -0.2243 | -0.054931 | -0.068665 | -0.18768 | -0.25635 | 0.027466 | 0.10986 | -0.25635 | 0 | -0.07782 | 122.8546 | 122.7264 | 61.6699 | -122.9645 | 122.8226 | 122.7173 | 63.4872 | -123.0515
1219.0156 | 123.1384 | -59.2163 | 63.5605 | -0.00015269 | 0.0046719 | 0.06761 | 0.069876 | 0.12864 | -0.0032813 | -0.0047275 | 0.022736 | -0.0072034 | 0.061914 | 0.058253 | 0.0046356 | -0.008342 | 63.5147 | 63.7024 | 2.4033 | -59.4177 | 63.6612 | -59.2941 | -59.3719 | -59.0698 | 4.4037 | -59.4269 | 63.6337 | 63.4872 | -59.4131 | -59.4589 | -0.077819 | -0.15564 | 0.10071 | 122.9187 | -0.20142 | -0.045777 | -0.045777 | -0.19684 | -0.24261 | 0.073242 | 0.14649 | -0.21057 | 0.032043 | -0.073242 | 122.8775 | 122.731 | 61.6196 | -122.9324 | 122.85 | 122.7036 | 63.62 | -123.0194
1220.0156 | 123.0927 | -59.2484 | 63.5559 | 0.10666 | 0.0085171 | 0.067396 | 0.068594 | 0.13377 | 0.00077755 | -0.0023777 | 0.16769 | -0.0052808 | 0.062982 | 0.059748 | 0.0057038 | -0.0081284 | 63.5605 | 63.6887 | 2.3758 | -59.4086 | 63.6108 | -59.2941 | -59.3857 | -59.0561 | 4.4128 | -59.4543 | 63.6154 | 63.4964 | -59.4223 | -59.4955 | -0.045776 | -0.13733 | 0.054932 | 122.937 | -0.16022 | -0.022888 | 0.004578 | -0.17395 | -0.24719 | 0.059509 | 0.19226 | -0.20599 | 0.041198 | -0.059509 | 122.8592 | 122.8088 | 61.6241 | -122.9416 | 122.8638 | 122.7448 | 63.6612 | -123.0515
1221.0156 | 123.0881 | -59.2346 | 63.5925 | -0.015411 | 0.0033901 | 0.06761 | 0.068594 | 0.13035 | -0.0019995 | -0.0053683 | 0.060883 | -0.0069898 | 0.060633 | 0.058894 | 0.0016448 | -0.010478 | 63.5193 | 63.6932 | 2.3071 | -59.4177 | 63.6475 | -59.285 | -59.3719 | -59.0836 | 4.5868 | -59.4269 | 63.62 | 63.501 | -59.3994 | -59.4543 | -0.050354 | -0.13733 | 0.054932 | 122.9279 | -0.18311 | -0.045777 | -0.073242 | -0.16479 | -0.21973 | 0.027466 | 0.15106 | -0.19226 | 0.027466 | -0.091552 | 122.8821 | 122.7539 | 61.5417 | -122.9645 | 122.8546 | 122.7356 | 63.8214 | -123.0469
1222.0156 | 123.0652 | -59.23 | 63.5376 | 0.16006 | 0.0070217 | 0.068037 | 0.070303 | 0.12779 | 0.00035035 | -0.0038731 | 0.19058 | -0.0099806 | 0.060846 | 0.059962 | 0.0033538 | -0.0059922 | 63.5376 | 63.6658 | 2.2797 | -59.4406 | 63.6337 | -59.3033 | -59.3536 | -59.1064 | 4.628 | -59.491 | 63.6063 | 63.5101 | -59.3903 | -59.4589 | -0.073242 | -0.1236 | 0.09613 | 122.8958 | -0.21057 | -0.086975 | 0 | -0.16022 | -0.22888 | 0.068664 | 0.1236 | -0.26093 | -0.032044 | -0.027466 | 122.8638 | 122.7676 | 61.5097 | -122.8912 | 122.8363 | 122.7402 | 63.858 | -122.9965
1223.0156 | 123.1155 | -59.23 | 63.6017 | 0.045624 | 0.0031765 | 0.069319 | 0.066031 | 0.12843 | -0.0024269 | -0.0032321 | -0.00015237 | -0.0076306 | 0.065119 | 0.059535 | 0.002713 | -0.0081284 | 63.5147 | 63.6841 | 2.3895 | -59.4269 | 63.6795 | -59.2896 | -59.3674 | -59.0881 | 4.7745 | -59.4315 | 63.6292 | 63.5559 | -59.3857 | -59.4727 | -0.059509 | -0.13733 | 0.077819 | 122.9141 | -0.19684 | -0.059509 | -0.086976 | -0.15564 | -0.24261 | 0.027465 | 0.14191 | -0.20142 | 0.041198 | -0.045777 | 122.9095 | 122.7448 | 61.6196 | -122.9691 | 122.8592 | 122.7859 | 64.0045 | -123.0743
1224.0156 | 123.0423 | -59.2667 | 63.5239 | 0.099029 | 0.0080899 | 0.068678 | 0.069876 | 0.12971 | -0.00093145 | -0.0030185 | 0.20584 | -0.0082716 | 0.061701 | 0.060603 | 0.004422 | -0.0077012 | 63.5193 | 63.6429 | 2.4261 | -59.4727 | 63.6063 | -59.3216 | -59.4131 | -59.1064 | 4.6783 | -59.4955 | 63.5742 | 63.4689 | -59.436 | -59.5276 | -0.054931 | -0.14648 | 0.082397 | 122.9095 | -0.20599 | -0.059509 | -0.004578 | -0.16937 | -0.26093 | 0.050354 | 0.16022 | -0.22888 | 0.032044 | -0.054932 | 122.8729 | 122.7859 | 61.6928 | -122.937 | 122.8409 | 122.7356 | 63.945 | -123.0515
1225.0156 | 123.1293 | -59.2438 | 63.5239 | -0.03067 | 0.0040311 | 0.066755 | 0.069663 | 0.12864 | -0.0037085 | -0.0045139 | -0.00015237 | -0.0084852 | 0.06106 | 0.059107 | 0.0035674 | -0.0091966 | 63.5056 | 63.6612 | 2.7466 | -59.4315 | 63.62 | -59.3308 | -59.4131 | -59.1019 | 4.8294 | -59.4589 | 63.5788 | 63.4644 | -59.4452 | -59.4955 | -0.086976 | -0.16937 | 0.09613 | 122.905 | -0.18768 | -0.018311 | -0.018311 | -0.20142 | -0.25177 | 0.054931 | 0.14191 | -0.21515 | 0.036621 | -0.05951 | 122.8638 | 122.7493 | 61.9904 | -122.937 | 122.8226 | 122.7081 | 64.0732 | -123.0194
1226.0156 | 123.0698 | -59.3079 | 63.4781 | 0.11429 | 0.0061673 | 0.067823 | 0.069663 | 0.13057 | 0.0029137 | -0.0051547 | 0.22873 | -0.0089124 | 0.062342 | 0.05868 | 0.0033538 | -0.0070602 | 63.4964 | 63.652 | 2.7924 | -59.4681 | 63.5559 | -59.3674 | -59.3903 | -59.1339 | 4.8889 | -59.5139 | 63.5468 | 63.4415 | -59.4772 | -59.5367 | -0.05951 | -0.082398 | 0.07782 | 122.9599 | -0.16022 | -0.07782 | 0.018311 | -0.16937 | -0.22888 | 0.068665 | 0.17395 | -0.20599 | 0.022888 | -0.036621 | 122.8638 | 122.8043 | 62.1002 | -122.8683 | 122.8546 | 122.7493 | 64.1968 | -123.0148
1227.0156 | 123.0972 | -59.2712 | 63.5193 | -0.015411 | 0.0053129 | 0.068464 | 0.069235 | 0.12864 | -0.0019995 | -0.0053683 | 0.053253 | -0.0086988 | 0.060633 | 0.057612 | 0.0012176 | -0.0068466 | 63.501 | 63.6429 | 2.9251 | -59.4543 | 63.6017 | -59.3491 | -59.4177 | -59.1339 | 4.8569 | -59.4589 | 63.5788 | 63.4827 | -59.4543 | -59.5139 | -0.07782 | -0.14648 | 0.082398 | 122.9141 | -0.18311 | -0.036621 | -0.01831 | -0.18311 | -0.24262 | 0.059509 | 0.13733 | -0.18768 | 0.054932 | -0.036621 | 122.8729 | 122.7722 | 62.1963 | -122.937 | 122.85 | 122.7539 | 64.1281 | -123.0331
1228.0156 | 123.0881 | -59.3079 | 63.5101 | 0.14481 | 0.0078763 | 0.067396 | 0.069022 | 0.12715 | -0.00050425 | -0.0049411 | 0.19058 | -0.009126 | 0.062769 | 0.060389 | 0.0035674 | -0.0074876 | 63.4598 | 63.6017 | 2.8519 | -59.5047 | 63.5559 | -59.3765 | -59.4177 | -59.1797 | 5.5389 | -59.5322 | 63.5696 | 63.4415 | -59.4818 | -59.5551 | -0.068665 | -0.10986 | 0.045776 | 122.9095 | -0.19684 | -0.086975 | -0.050354 | -0.17395 | -0.24719 | 0.059509 | 0.12817 | -0.2243 | 0.022888 | -0.068665 | 122.8638 | 122.7676 | 62.1597 | -122.9279 | 122.8775 | 122.7493 | 64.8468 | -123.0652
1229.0156 | 123.0927 | -59.2804 | 63.5239 | -0.015411 | 0.0068081 | 0.069319 | 0.069449 | 0.12971 | -0.0028541 | -0.0057957 | 0.037995 | -0.0067762 | 0.060419 | 0.058894 | 0.002713 | -0.0094102 | 63.4369 | 63.62 | 2.9205 | -59.4681 | 63.5742 | -59.3445 | -59.4223 | -59.1339 | 5.6122 | -59.4818 | 63.5742 | 63.446 | -59.4543 | -59.5047 | -0.064086 | -0.14191 | 0.050354 | 122.9004 | -0.18768 | -0.045777 | -0.086975 | -0.17395 | -0.2243 | 0.050354 | 0.14649 | -0.20142 | 0.022888 | -0.07782 | 122.8546 | 122.7173 | 62.2009 | -122.9462 | 122.8546 | 122.7264 | 64.8926 | -123.0286
1230.0156 | 123.056 | -59.285 | 63.5193 | 0.11429 | 0.0085171 | 0.068464 | 0.070517 | 0.13163 | 0.00056395 | -0.0034457 | 0.19058 | -0.006349 | 0.062128 | 0.059535 | 0.0057038 | -0.0077012 | 63.4827 | 63.6429 | 2.6688 | -59.4681 | 63.588 | -59.3628 | -59.4452 | -59.1385 | 4.9438 | -59.5367 | 63.5696 | 63.4552 | -59.4589 | -59.5139 | -0.07782 | -0.16022 | 0.068665 | 122.9279 | -0.18311 | -0.022889 | -0.036621 | -0.17395 | -0.22888 | 0.050354 | 0.14648 | -0.25177 | -0.022888 | -0.064087 | 122.8729 | 122.7676 | 61.9537 | -122.9645 | 122.8546 | 122.7402 | 64.2288 | -123.0331
1231.0156 | 123.0835 | -59.3033 | 63.5193 | 0.13718 | 0.0055265 | 0.06825 | 0.067526 | 0.12651 | -0.0017859 | -0.0043003 | 0.083771 | -0.008058 | 0.06106 | 0.059321 | 0.0033538 | -0.0072738 | 63.4415 | 63.6108 | 2.8381 | -59.4818 | 63.6017 | -59.3262 | -59.4223 | -59.1476 | 4.8935 | -59.4864 | 63.5696 | 63.4415 | -59.4269 | -59.5047 | -0.022888 | -0.11902 | 0.082398 | 122.9141 | -0.17853 | -0.05951 | -0.07782 | -0.1236 | -0.20142 | 0.050354 | 0.15564 | -0.18311 | 0.018311 | -0.07782 | 122.905 | 122.7448 | 62.1414 | -122.9416 | 122.8729 | 122.7448 | 64.1968 | -123.024
1232.0156 | 123.0606 | -59.3033 | 63.501 | 0.099029 | 0.0036039 | 0.068464 | 0.07009 | 0.12907 | -0.0024269 | -0.0030185 | 0.14481 | -0.0059216 | 0.060419 | 0.058467 | 0.0014312 | -0.0070602 | 63.446 | 63.5925 | 2.9068 | -59.5001 | 63.5605 | -59.3536 | -59.4315 | -59.166 | 5.2963 | -59.523 | 63.5513 | 63.4506 | -59.4727 | -59.5505 | -0.050354 | -0.12817 | 0.059509 | 122.8958 | -0.19684 | -0.068664 | -0.054932 | -0.16937 | -0.24719 | 0.050354 | 0.13733 | -0.21973 | 0.027466 | -0.050354 | 122.8638 | 122.7493 | 62.2101 | -122.9324 | 122.8546 | 122.7539 | 64.5996 | -123.0515
1233.0156 | 123.0652 | -59.2712 | 63.5422 | 0.083771 | 0.0044583 | 0.069959 | 0.065817 | 0.13078 | -0.00029045 | -0.0023777 | 0.0914 | -0.0078442 | 0.062769 | 0.05868 | 0.0037812 | -0.0087692 | 63.3133 | 63.6475 | 3.1265 | -59.5047 | 63.588 | -59.3399 | -59.404 | -59.1705 | 5.452 | -59.4864 | 63.5834 | 63.4781 | -59.4498 | -59.5093 | -0.068665 | -0.13275 | 0.045777 | 122.9187 | -0.23346 | -0.10071 | -0.22888 | -0.17853 | -0.23804 | 0.041199 | 0.10071 | -0.21515 | 0.022888 | -0.064087 | 122.8592 | 122.5845 | 62.3978 | -122.9462 | 122.8546 | 122.7493 | 64.7232 | -123.0515
1234.0156 | 123.0698 | -59.3079 | 63.5193 | 0.12955 | 0.0057401 | 0.066969 | 0.07009 | 0.12928 | 0.0014185 | -0.0062229 | 0.18295 | -0.008058 | 0.059778 | 0.057612 | 0.0050628 | -0.0087692 | 63.4506 | 63.5971 | 3.0899 | -59.5093 | 63.5468 | -59.3353 | -59.4406 | -59.1522 | 5.7449 | -59.5367 | 63.5742 | 63.4644 | -59.491 | -59.5505 | -0.027466 | -0.13275 | 0.027466 | 122.905 | -0.20142 | -0.068664 | -0.068664 | -0.18311 | -0.24262 | 0.054932 | 0.15564 | -0.22888 | 0.013733 | -0.054932 | 122.8546 | 122.7585 | 62.3978 | -122.9599 | 122.8821 | 122.7722 | 65.0528 | -123.0698
1235.0156 | 123.1201 | -59.3079 | 63.5056 | -0.00015269 | 0.0027493 | 0.069105 | 0.069663 | 0.12843 | -0.0022131 | -0.0045139 | 0.015106 | -0.0061352 | 0.058924 | 0.057826 | 0.004422 | -0.0068466 | 63.4506 | 63.6108 | 3.1357 | -59.4818 | 63.5834 | -59.3719 | -59.4589 | -59.1522 | 5.9143 | -59.491 | 63.5605 | 63.4369 | -59.4681 | -59.5413 | -0.064087 | -0.15106 | 0.07782 | 122.9187 | -0.17395 | -0.022889 | -0.054931 | -0.16022 | -0.23346 | 0.054932 | 0.15564 | -0.18311 | 0.050354 | -0.068664 | 122.8912 | 122.7585 | 62.4435 | -122.9645 | 122.8683 | 122.7448 | 65.2222 | -123.0469
1236.0156 | 123.0789 | -59.3124 | 63.4918 | 0.16769 | 0.0048855 | 0.068464 | 0.069876 | 0.13035 | -0.00050425 | -0.0049411 | 0.17532 | -0.0086988 | 0.062769 | 0.060603 | 0.0042084 | -0.0096238 | 63.4689 | 63.6246 | 3.2364 | -59.4772 | 63.5468 | -59.3811 | -59.4315 | -59.1476 | 6.3492 | -59.5367 | 63.5422 | 63.414 | -59.4818 | -59.5596 | -0.068665 | -0.11902 | 0.054932 | 122.937 | -0.1648 | -0.045776 | -0.022888 | -0.16937 | -0.24719 | 0.050354 | 0.16479 | -0.2243 | 0.022888 | -0.07782 | 122.8592 | 122.7814 | 62.5488 | -122.9233 | 122.8546 | 122.7264 | 65.6616 | -123.0515
1237.0156 | 123.0789 | -59.2987 | 63.5147 | 1.1671 | 0.0040311 | 0.069959 | 0.068381 | 0.12971 | -0.0028541 | -0.0053683 | 0.068512 | -0.0082716 | 0.061487 | 0.059962 | 0.0014312 | -0.0081284 | 63.4323 | 63.6108 | 2.9709 | -59.4818 | 63.5971 | -59.3628 | -59.4269 | -59.1568 | 5.9463 | -59.4955 | 63.5696 | 63.4689 | -59.4681 | -59.5322 | -0.064087 | -0.12817 | 0.082398 | 122.9095 | -0.18311 | -0.054932 | -0.082397 | -0.16937 | -0.23346 | 0.054932 | 0.14191 | -0.19684 | 0.036622 | -0.045776 | 122.8958 | 122.731 | 62.2696 | -122.9416 | 122.8683 | 122.7676 | 65.2451 | -123.0469
1238.0156 | 123.0881 | -59.2941 | 63.4872 | 0.12955 | 0.0068081 | 0.070173 | 0.070303 | 0.1295 | 0.00035035 | -0.0032321 | 0.25162 | -0.0076306 | 0.063837 | 0.058894 | 0.0031402 | -0.0074876 | 63.4918 | 63.652 | 3.4149 | -59.4452 | 63.5696 | -59.3536 | -59.4406 | -59.1293 | 5.9372 | -59.5001 | 63.5376 | 63.4277 | -59.491 | -59.5367 | -0.05951 | -0.14648 | 0.082397 | 122.9462 | -0.15106 | -0.004577 | 0.004577 | -0.19684 | -0.24262 | 0.050354 | 0.16479 | -0.20599 | 0.036621 | -0.05951 | 122.8638 | 122.7859 | 62.709 | -122.9279 | 122.8317 | 122.7219 | 65.2313 | -123.024
1239.0156 | 123.1064 | -59.3079 | 63.5284 | -0.015411 | 0.0042447 | 0.069746 | 0.069235 | 0.13057 | -0.0015723 | -0.0043003 | 0.015106 | -0.0078442 | 0.062555 | 0.059535 | 0.0020722 | -0.0087692 | 63.4781 | 63.6475 | 3.0853 | -59.4727 | 63.6154 | -59.3353 | -59.4177 | -59.1248 | 5.7861 | -59.4727 | 63.5788 | 63.4689 | -59.436 | -59.5276 | -0.027466 | -0.10986 | 0.086975 | 122.9553 | -0.16479 | -0.054931 | -0.050354 | -0.12817 | -0.21973 | 0.050354 | 0.18311 | -0.16479 | 0.054932 | -0.059509 | 122.9233 | 122.7859 | 62.3932 | -122.9462 | 122.8867 | 122.7768 | 65.094 | -123.056
1240.0156 | 123.0972 | -59.2896 | 63.5147 | 0.037994 | 0.0072355 | 0.068678 | 0.068808 | 0.13292 | 0.0012047 | -0.0036595 | 0.19058 | -0.0069898 | 0.059992 | 0.058894 | 0.0069854 | -0.0085556 | 63.4918 | 63.652 | 3.1265 | -59.4543 | 63.5696 | -59.3628 | -59.4315 | -59.111 | 5.6534 | -59.4955 | 63.5742 | 63.414 | -59.4543 | -59.5184 | -0.073242 | -0.14191 | 0.054932 | 122.9416 | -0.16479 | -0.022888 | -0.022888 | -0.16479 | -0.22888 | 0.05951 | 0.17853 | -0.20599 | 0.022889 | -0.10071 | 122.8592 | 122.7814 | 62.4161 | -122.9462 | 122.8638 | 122.7036 | 64.9429 | -123.0331
1241.0156 | 123.0652 | -59.2941 | 63.5193 | 0.030365 | 0.0072355 | 0.068037 | 0.069449 | 0.12907 | -0.0011451 | -0.0036595 | 0.060883 | -0.0078442 | 0.06106 | 0.060176 | 0.0039948 | -0.008342 | 63.4506 | 63.5971 | 3.2181 | -59.4818 | 63.6108 | -59.3628 | -59.4543 | -59.1431 | 5.8136 | -59.4818 | 63.5925 | 63.4735 | -59.4635 | -59.5459 | -0.068665 | -0.16022 | 0.091553 | 122.8912 | -0.18768 | -0.027466 | -0.068664 | -0.16937 | -0.25177 | 0.073242 | 0.15106 | -0.18768 | 0.064086 | -0.045776 | 122.905 | 122.7448 | 62.5122 | -122.9736 | 122.8867 | 122.7676 | 65.1077 | -123.0652
1242.0156 | 123.0377 | -59.3536 | 63.4415 | 0.053253 | 0.0095853 | 0.066969 | 0.071799 | 0.13057 | 0.00013675 | -0.0030185 | 0.19058 | -0.0082716 | 0.060419 | 0.060816 | 0.0046356 | -0.0072738 | 63.4369 | 63.5834 | 4.3442 | -59.5459 | 63.5101 | -59.4269 | -59.4818 | -59.1888 | 5.9601 | -59.5825 | 63.5101 | 63.3865 | -59.5505 | -59.6054 | -0.073242 | -0.12817 | 0.068665 | 122.937 | -0.19226 | -0.064086 | -0.004577 | -0.19684 | -0.25177 | 0.068665 | 0.16479 | -0.22888 | 0.022888 | -0.054931 | 122.8638 | 122.7905 | 63.6978 | -122.9233 | 122.8638 | 122.7402 | 65.3137 | -123.0469
1243.0156 | 123.0972 | -59.3719 | 63.4552 | 0.053253 | 0.0018949 | 0.071241 | 0.070944 | 0.12864 | -0.0019995 | -0.0040867 | 0.060883 | -0.0076306 | 0.060846 | 0.059107 | 0.0024994 | -0.010051 | 63.382 | 63.5101 | 4.5319 | -59.5551 | 63.5101 | -59.4086 | -59.5047 | -59.2438 | 6.0699 | -59.5779 | 63.5239 | 63.3636 | -59.5367 | -59.5917 | -0.036621 | -0.13275 | 0.054932 | 122.8821 | -0.18311 | -0.050354 | -0.073242 | -0.16479 | -0.21973 | 0.068665 | 0.12817 | -0.20599 | 0.013733 | -0.091553 | 122.8821 | 122.7539 | 63.9038 | -122.9599 | 122.8958 | 122.7356 | 65.4419 | -123.0469
1244.0156 | 123.0927 | -59.3765 | 63.4048 | 0.17532 | 0.01044 | 0.067182 | 0.066885 | 0.13484 | -0.00050425 | -0.0038731 | 0.20584 | -0.006349 | 0.061273 | 0.058894 | 0.0031402 | -0.0089828 | 63.4094 | 63.5559 | 4.6875 | -59.5734 | 63.4506 | -59.4589 | -59.5093 | -59.2072 | 6.0608 | -59.6054 | 63.4598 | 63.3545 | -59.5688 | -59.6191 | -0.082397 | -0.13275 | 0.045777 | 122.9324 | -0.19684 | -0.064087 | 0.004578 | -0.19226 | -0.24262 | 0.054932 | 0.16937 | -0.22888 | 0.013733 | -0.050354 | 122.8271 | 122.7859 | 64.064 | -122.9141 | 122.8363 | 122.731 | 65.4373 | -123.024
1245.0156 | 123.0698 | -59.3582 | 63.4644 | 0.022736 | 0.0068081 | 0.069319 | 0.069449 | 0.13313 | -0.00071785 | -0.0028049 | -0.30533 | -0.0089124 | 0.059992 | 0.059107 | 0.0033538 | -0.006633 | 63.3682 | 63.5605 | 4.454 | -59.5551 | 63.5239 | -59.4177 | -59.4727 | -59.2484 | 6.1203 | -59.5779 | 63.5193 | 63.3774 | -59.5459 | -59.6054 | -0.05951 | -0.11444 | 0.05951 | 122.9187 | -0.19684 | -0.082398 | -0.09613 | -0.18768 | -0.24719 | 0.054932 | 0.10986 | -0.21973 | 0.027466 | -0.086975 | 122.8821 | 122.7264 | 63.8123 | -122.937 | 122.8775 | 122.7356 | 65.4785 | -123.0698
1246.0156 | 123.0515 | -59.3445 | 63.4918 | -0.22903 | 0.0083035 | 0.070173 | 0.068167 | 0.12864 | 0.0014185 | -0.0032321 | -0.15274 | -0.0076306 | 0.060419 | 0.059107 | 0.0033538 | -0.0098374 | 63.4369 | 63.6246 | 4.7012 | -59.5047 | 63.5376 | -59.404 | -59.4772 | -59.2072 | 6.2988 | -59.5642 | 63.533 | 63.3865 | -59.5184 | -59.5871 | -0.05951 | -0.13275 | 0.045777 | 122.9691 | -0.16022 | -0.027466 | -0.054931 | -0.17395 | -0.24262 | 0.041199 | 0.13733 | -0.21973 | 0.022888 | -0.10529 | 122.8821 | 122.7814 | 64.0457 | -122.9691 | 122.8775 | 122.731 | 65.6433 | -123.0789
1247.0156 | 123.0698 | -59.3674 | 63.4506 | 0.0914 | 0.0053129 | 0.067823 | 0.070731 | 0.12779 | -0.0022131 | -0.0047275 | 0.12955 | -0.0050672 | 0.057215 | 0.057612 | 0.0042084 | -0.008342 | 63.3865 | 63.5605 | 4.4037 | -59.5505 | 63.5147 | -59.4223 | -59.4864 | -59.2163 | 5.7678 | -59.5276 | 63.5468 | 63.4186 | -59.4818 | -59.5825 | -0.054931 | -0.11902 | 0.064086 | 122.9279 | -0.18311 | -0.064087 | -0.064087 | -0.11444 | -0.21515 | 0.09613 | 0.15106 | -0.16022 | 0.054932 | -0.032044 | 122.8821 | 122.7539 | 63.7711 | -122.937 | 122.9141 | 122.7859 | 65.1352 | -123.0331
1248.0156 | 123.1064 | -59.3536 | 63.4232 | 0.16769 | 0.0065945 | 0.069959 | 0.065176 | 0.12886 | -0.00029045 | -0.0051547 | 0.24399 | -0.0069898 | 0.061273 | 0.058253 | 0.004422 | -0.008342 | 63.6108 | 63.533 | 4.9164 | -59.5001 | 63.5056 | -59.4315 | -59.5001 | -59.1843 | 5.7907 | -59.5505 | 63.4827 | 63.3545 | -59.5459 | -59.6237 | -0.07782 | -0.14648 | 0.082397 | 122.8867 | -0.14648 | 0 | 0.18768 | -0.19226 | -0.27008 | 0.059509 | 0.16937 | -0.19684 | 0.073242 | -0.068665 | 122.8592 | 122.9645 | 64.27 | -122.9233 | 122.8363 | 122.7081 | 65.1443 | -123.0469
1249.0156 | 123.0743 | -59.3582 | 63.4369 | 0.068512 | 0.0036039 | 0.068891 | 0.070303 | 0.12971 | 0.00013675 | -0.0055821 | 0.09903 | -0.0093396 | 0.061273 | 0.059962 | 0.0031402 | -0.0068466 | 63.3728 | 63.4781 | 5.4428 | -59.5505 | 63.5101 | -59.4589 | -59.5322 | -59.2575 | 5.7312 | -59.5917 | 63.4918 | 63.3728 | -59.5688 | -59.6054 | -0.10071 | -0.17395 | 0.073242 | 122.8363 | -0.19226 | -0.01831 | -0.064087 | -0.21057 | -0.24719 | 0.054931 | 0.10071 | -0.23346 | 0.013733 | -0.064087 | 122.8683 | 122.731 | 64.801 | -122.9691 | 122.85 | 122.731 | 65.0894 | -123.0423
1250.0156 | 123.1018 | -59.3903 | 63.4048 | 0.17532 | 0.0078763 | 0.067182 | 0.07009 | 0.12971 | 0.00035035 | -0.0049411 | 0.16006 | -0.008058 | 0.062128 | 0.057185 | 0.0039948 | -0.0094102 | 63.4048 | 63.5559 | 5.8136 | -59.5642 | 63.446 | -59.4818 | -59.5139 | -59.2163 | 5.7129 | -59.5917 | 63.4781 | 63.3224 | -59.5688 | -59.6558 | -0.091553 | -0.1236 | 0.041199 | 122.9462 | -0.17395 | -0.050354 | 0 | -0.17853 | -0.2655 | 0.073242 | 0.17395 | -0.20142 | 0.064087 | -0.082397 | 122.8363 | 122.7951 | 65.2039 | -122.9187 | 122.8683 | 122.7127 | 65.1031 | -123.0606
1251.0156 | 123.0331 | -59.3948 | 63.4186 | 0.037994 | 0.0053129 | 0.066755 | 0.069876 | 0.13078 | -0.0019995 | -0.0047275 | 0.12955 | -0.0067762 | 0.062982 | 0.058467 | 0.0022858 | -0.0074876 | 63.3774 | 63.5056 | 5.6488 | -59.5642 | 63.501 | -59.4406 | -59.4955 | -59.2255 | 6.0196 | -59.5734 | 63.4872 | 63.3682 | -59.523 | -59.61 | -0.045777 | -0.10071 | 0.082398 | 122.9004 | -0.16937 | -0.068665 | -0.041199 | -0.12817 | -0.21515 | 0.068665 | 0.16937 | -0.17853 | 0.036621 | -0.050354 | 122.8958 | 122.7722 | 65.0436 | -122.9141 | 122.8821 | 122.7631 | 65.4144 | -123.0286
1252.0156 | 123.1155 | -59.3857 | 63.3774 | 0.18295 | 0.0093717 | 0.065687 | 0.067954 | 0.12907 | 0.00077755 | -0.0055821 | 0.19058 | -0.00464 | 0.062769 | 0.05868 | 0.0052764 | -0.0089828 | 63.5696 | 63.5101 | 5.777 | -59.5139 | 63.4598 | -59.4498 | -59.5322 | -59.2026 | 5.8685 | -59.5779 | 63.446 | 63.3408 | -59.5688 | -59.6054 | -0.064087 | -0.14648 | 0.082398 | 122.8958 | -0.12817 | 0.018311 | 0.19226 | -0.18311 | -0.21973 | 0.068665 | 0.1831 | -0.19226 | 0.027466 | -0.036621 | 122.8455 | 122.9553 | 65.1627 | -122.9095 | 122.8317 | 122.7264 | 65.2542 | -122.9828
1253.0156 | 123.0835 | -59.3765 | 63.4186 | 0.015106 | 0.0063809 | 0.068891 | 0.069449 | 0.12843 | -0.0047767 | -0.0055821 | 0.12192 | -0.0061352 | 0.059137 | 0.059107 | 0.0031402 | -0.0064194 | 63.4689 | 63.414 | 5.5344 | -59.5596 | 63.5101 | -59.4635 | -59.5322 | -59.2392 | 6.633 | -59.5963 | 63.4781 | 63.3499 | -59.5505 | -59.6466 | -0.086975 | -0.15564 | 0.091553 | 122.7905 | -0.18311 | -0.027465 | 0.050354 | -0.17395 | -0.27008 | 0.059509 | 0.13733 | -0.21973 | 0.050354 | -0.068664 | 122.8867 | 122.8455 | 64.9109 | -122.9507 | 122.8546 | 122.7264 | 66.0095 | -123.0652
1254.0156 | 123.111 | -59.4177 | 63.382 | 0.21347 | 0.010013 | 0.065687 | 0.068808 | 0.13099 | 0.0016321 | -0.0023777 | 0.21347 | -0.0072034 | 0.061914 | 0.058894 | 0.00549 | -0.010051 | 63.3865 | 63.5101 | 5.5801 | -59.5825 | 63.4369 | -59.5047 | -59.5505 | -59.2438 | 6.6559 | -59.6237 | 63.4232 | 63.2675 | -59.6512 | -59.6878 | -0.086975 | -0.13275 | 0.054932 | 122.9279 | -0.1648 | -0.032044 | 0.004578 | -0.23346 | -0.27008 | 0.041199 | 0.17395 | -0.20599 | 0.064087 | -0.11444 | 122.8546 | 122.8043 | 64.9979 | -122.9324 | 122.8409 | 122.6852 | 66.0736 | -123.0698
1255.0156 | 123.0789 | -59.4177 | 63.4277 | 0.12192 | 0.0097989 | 0.068464 | 0.068381 | 0.12843 | -0.00071785 | -0.0047275 | 0.25925 | -0.0061352 | 0.062128 | 0.057185 | 0.0037812 | -0.0057786 | 63.3774 | 63.5147 | 5.5756 | -59.5917 | 63.4506 | -59.4406 | -59.5459 | -59.2484 | 6.4087 | -59.6146 | 63.4644 | 63.3591 | -59.5642 | -59.6466 | -0.022888 | -0.12817 | 0.022889 | 122.9324 | -0.17395 | -0.045777 | -0.050354 | -0.14648 | -0.22888 | 0.036621 | 0.16937 | -0.19684 | 0.032043 | -0.068664 | 122.8683 | 122.7951 | 64.9933 | -122.9736 | 122.8821 | 122.7768 | 65.8264 | -123.0743
1256.0156 | 123.1522 | -59.4131 | 63.3774 | 0.16769 | 0.010013 | 0.065901 | 0.070731 | 0.12843 | 0.0012047 | -0.0028049 | -0.14511 | -0.0069898 | 0.062128 | 0.056758 | 0.0039948 | -0.0087692 | 63.4003 | 63.588 | 5.809 | -59.7061 | 63.4003 | -59.5047 | -59.5551 | -59.2026 | 6.3812 | -59.6146 | 63.4323 | 63.3316 | -59.5917 | -59.6146 | -0.091553 | -0.14191 | 0.022889 | 123.0011 | -0.29297 | -0.15106 | 0.022889 | -0.17853 | -0.20142 | 0.054932 | 0.21057 | -0.20142 | 0 | -0.045776 | 122.8134 | 122.8134 | 65.2222 | -122.9324 | 122.8455 | 122.7448 | 65.7944 | -122.9919
1257.0156 | 123.0743 | -59.3674 | 63.4186 | 0.0914 | 0.0085171 | 0.068678 | 0.06774 | 0.12693 | -0.0011451 | -0.0047275 | 0.19821 | -0.0065626 | 0.060419 | 0.05868 | 0.0029266 | -0.0062058 | 63.3499 | 63.5147 | 5.9921 | -59.5917 | 63.4644 | -59.4543 | -59.5139 | -59.2392 | 6.34 | -59.6191 | 63.4689 | 63.3774 | -59.5596 | -59.6329 | -0.086975 | -0.14648 | 0.045776 | 122.8821 | -0.2243 | -0.07782 | -0.068664 | -0.19226 | -0.2655 | 0.050354 | 0.12817 | -0.25177 | 0.013733 | -0.041199 | 122.8317 | 122.7173 | 65.3595 | -122.9324 | 122.8363 | 122.7448 | 65.7074 | -123.0515
1258.0156 | 123.1384 | -59.4131 | 63.3545 | 0.083771 | 0.012149 | 0.065901 | 0.071158 | 0.13057 | 0.00035035 | -0.0043003 | 0.20584 | -0.0067762 | 0.060419 | 0.059962 | 0.0059174 | -0.0089828 | 63.4048 | 63.5056 | 6.102 | -59.5322 | 63.4644 | -59.4543 | -59.5551 | -59.2117 | 6.3583 | -59.6054 | 63.4094 | 63.3408 | -59.5871 | -59.6283 | -0.041199 | -0.14191 | 0.10986 | 122.9187 | -0.11902 | 0.022888 | 0.050354 | -0.17395 | -0.21515 | 0.054932 | 0.20142 | -0.19226 | 0.022888 | -0.013733 | 122.8775 | 122.818 | 65.5151 | -122.9095 | 122.8226 | 122.7539 | 65.7715 | -122.9828
1259.0156 | 123.0423 | -59.404 | 63.3957 | 0.16006 | 0.0068081 | 0.0706 | 0.067313 | 0.12886 | -0.00071785 | -0.00024146 | 0.26688 | -0.0069898 | 0.059778 | 0.058894 | 0.0037812 | -0.0091966 | 63.3453 | 63.533 | 6.4636 | -59.5779 | 63.4415 | -59.491 | -59.5367 | -59.2438 | 6.2531 | -59.6329 | 63.4232 | 63.327 | -59.5917 | -59.6558 | -0.086975 | -0.13275 | 0.045776 | 122.937 | -0.17395 | -0.041199 | -0.050354 | -0.18768 | -0.25177 | 0.027466 | 0.16022 | -0.22888 | 0.022888 | -0.068665 | 122.8455 | 122.7493 | 65.8676 | -122.9324 | 122.8271 | 122.731 | 65.657 | -123.0515
1260.0156 | 123.0698 | -59.3674 | 63.3865 | 0.19058 | 0.011081 | 0.06761 | 0.069235 | 0.12864 | 0.00077755 | -0.0021641 | 0.40421 | -0.0069898 | 0.060419 | 0.056971 | 0.0050628 | -0.0087692 | 63.4232 | 63.5422 | 6.0699 | -59.5413 | 63.4689 | -59.4223 | -59.4955 | -59.1888 | 6.2851 | -59.5825 | 63.4827 | 63.3636 | -59.5367 | -59.6237 | -0.054931 | -0.12817 | 0.082397 | 122.9095 | -0.17395 | -0.045777 | 0.036621 | -0.16937 | -0.25635 | 0.09613 | 0.17853 | -0.21515 | 0.041198 | -0.022889 | 122.8363 | 122.7905 | 65.4373 | -122.8821 | 122.85 | 122.731 | 65.6525 | -123.0103
1261.0156 | 123.1018 | -59.4269 | 63.3728 | 0.20584 | 0.01044 | 0.068464 | 0.071158 | 0.13121 | -0.0011451 | -0.0030185 | 0.18295 | -0.0084852 | 0.060846 | 0.05868 | 0.0046356 | -0.0079148 | 63.382 | 63.5422 | 6.6513 | -59.5688 | 63.4369 | -59.4727 | -59.5459 | -59.2392 | 6.1615 | -59.5963 | 63.4506 | 63.3499 | -59.5688 | -59.642 | -0.045776 | -0.11902 | 0.064087 | 122.9691 | -0.14191 | -0.022889 | 0.009155 | -0.14191 | -0.21515 | 0.07782 | 0.18768 | -0.16937 | 0.045777 | -0.022888 | 122.8638 | 122.8088 | 66.0782 | -122.9187 | 122.8775 | 122.7768 | 65.5884 | -123.0148
1262.0156 | 123.0789 | -59.4131 | 63.3728 | 0.17532 | 0.011081 | 0.066541 | 0.069022 | 0.13142 | 0.00035035 | -0.0038731 | 0.19821 | -0.007417 | 0.061487 | 0.059748 | 0.004422 | -0.0079148 | 63.382 | 63.5101 | 6.5186 | -59.5917 | 63.4689 | -59.4955 | -59.5505 | -59.23 | 6.4407 | -59.61 | 63.4415 | 63.3499 | -59.6008 | -59.6558 | -0.082397 | -0.13733 | 0.09613 | 122.9233 | -0.17853 | -0.041199 | 0.009155 | -0.18768 | -0.24262 | 0.068664 | 0.18311 | -0.19684 | 0.045777 | -0.022888 | 122.8821 | 122.7951 | 65.9317 | -122.9233 | 122.8546 | 122.7631 | 65.8539 | -123.0286
1263.0156 | 123.0972 | -59.4131 | 63.4048 | 0.16006 | 0.0078763 | 0.06761 | 0.068808 | 0.13163 | -0.0013587 | -0.0040867 | 0.22873 | -0.0052808 | 0.063623 | 0.059321 | 0.0035674 | -0.0072738 | 63.3865 | 63.5284 | 6.6605 | -59.5779 | 63.4689 | -59.436 | -59.5367 | -59.23 | 6.3034 | -59.5963 | 63.4369 | 63.3453 | -59.5551 | -59.6283 | -0.022888 | -0.1236 | 0.064087 | 122.9416 | -0.16479 | -0.041199 | -0.01831 | -0.14191 | -0.21515 | 0.032044 | 0.18311 | -0.1831 | 0.032044 | -0.059509 | 122.8821 | 122.7997 | 66.0736 | -122.9416 | 122.85 | 122.7585 | 65.7166 | -123.0331
1264.0156 | 123.1155 | -59.3994 | 63.3774 | 0.20584 | 0.011935 | 0.067823 | 0.068381 | 0.13228 | 0.0035547 | -0.00066866 | 0.19058 | -0.005708 | 0.062982 | 0.059748 | 0.006131 | -0.0085556 | 63.3499 | 63.4735 | 6.7612 | -59.5825 | 63.4964 | -59.4727 | -59.5367 | -59.2209 | 5.4611 | -59.6283 | 63.4918 | 63.3499 | -59.5871 | -59.6329 | -0.073242 | -0.13733 | 0.11902 | 122.8729 | -0.18311 | -0.045777 | -0.027465 | -0.18768 | -0.23346 | 0.11444 | 0.17853 | -0.22888 | 0.004578 | -0.027465 | 122.8958 | 122.7493 | 66.1606 | -122.9141 | 122.8912 | 122.7493 | 64.8605 | -123.0103
1265.0156 | 123.1247 | -59.3948 | 63.414 | -0.10696 | 0.0040311 | 0.070173 | 0.067954 | 0.1295 | -0.0039221 | -0.0045139 | 0.037995 | -0.0072034 | 0.063623 | 0.059962 | 0.0018584 | -0.006633 | 63.3911 | 63.5696 | 6.9855 | -59.5322 | 63.5101 | -59.4498 | -59.523 | -59.1888 | 5.3101 | -59.5322 | 63.4323 | 63.3728 | -59.5551 | -59.6375 | -0.054932 | -0.12817 | 0.096131 | 122.9645 | -0.13733 | -0.009156 | -0.022888 | -0.16022 | -0.24262 | 0.018311 | 0.20599 | -0.13733 | 0.10529 | -0.041198 | 122.905 | 122.7859 | 66.3803 | -122.937 | 122.8271 | 122.7676 | 64.7049 | -123.0515
1266.0156 | 123.0469 | -59.4315 | 63.3865 | 0.19058 | 0.01279 | 0.068464 | 0.070731 | 0.13078 | 0.0029137 | -0.0043003 | 0.16006 | -0.0054944 | 0.060633 | 0.059321 | 0.0057038 | -0.0085556 | 63.3041 | 63.4003 | 6.9351 | -59.6375 | 63.4872 | -59.5001 | -59.5779 | -59.3124 | 5.5435 | -59.6832 | 63.4872 | 63.3408 | -59.61 | -59.6832 | -0.068664 | -0.14648 | 0.10071 | 122.8317 | -0.20599 | -0.059509 | -0.082398 | -0.17853 | -0.25177 | 0.10071 | 0.11902 | -0.25177 | 0 | -0.045777 | 122.9187 | 122.7356 | 66.3666 | -122.9645 | 122.9187 | 122.7722 | 64.975 | -123.0698
1267.0156 | 123.0606 | -59.4086 | 63.4003 | 0.15244 | 0.0061673 | 0.069532 | 0.06774 | 0.1327 | -0.0052039 | -0.0051547 | 0.15244 | -0.0097668 | 0.061914 | 0.059107 | 0.001004 | -0.0062058 | 63.3041 | 63.4781 | 7.1732 | -59.6054 | 63.4506 | -59.4772 | -59.5505 | -59.2804 | 5.3055 | -59.6283 | 63.4323 | 63.3499 | -59.5734 | -59.6466 | -0.068665 | -0.14191 | 0.050354 | 122.8867 | -0.19684 | -0.054932 | -0.096131 | -0.16479 | -0.23804 | 0.032043 | 0.12817 | -0.21973 | 0.01831 | -0.050354 | 122.8592 | 122.7127 | 66.5817 | -122.9507 | 122.8409 | 122.7585 | 64.7141 | -123.0469
1268.0156 | 123.0057 | -59.4498 | 63.3911 | -0.64102 | 0.014071 | 0.06526 | 0.073081 | 0.12864 | 0.0024865 | -0.0023777 | 0.10666 | -0.0069898 | 0.064264 | 0.059107 | 0.004422 | -0.0091966 | 63.2904 | 63.382 | 7.164 | -59.6558 | 63.4964 | -59.5322 | -59.6146 | -59.3353 | 5.7678 | -59.7244 | 63.4598 | 63.3636 | -59.6329 | -59.6786 | -0.082398 | -0.16479 | 0.10529 | 122.8317 | -0.20599 | -0.041199 | -0.10071 | -0.18311 | -0.22888 | 0.068665 | 0.11444 | -0.27466 | -0.045776 | -0.027466 | 122.9462 | 122.7402 | 66.6138 | -123.0057 | 122.9095 | 122.8134 | 65.2176 | -123.0698
1269.0156 | 123.0881 | -59.4131 | 63.3453 | -1.3658 | 0.0065945 | 0.06761 | 0.066458 | 0.12971 | -0.0013587 | -0.0047275 | 0.2211 | -0.0072034 | 0.061914 | 0.059321 | 0.0037812 | -0.0079148 | 63.3362 | 63.5376 | 7.3471 | -59.5917 | 63.4323 | -59.4772 | -59.5825 | -59.2392 | 5.9555 | -59.6237 | 63.4232 | 63.3179 | -59.6146 | -59.6786 | -0.064087 | -0.16937 | 0.086975 | 122.9507 | -0.17853 | -0.009155 | -0.009155 | -0.20142 | -0.2655 | 0.07782 | 0.17395 | -0.21057 | 0.054932 | -0.027466 | 122.8455 | 122.7493 | 66.7603 | -122.9279 | 122.8363 | 122.731 | 65.3687 | -123.024
1270.0156 | 122.9691 | -59.3765 | 63.4644 | -0.068817 | 0.0059537 | 0.0706 | 0.069663 | 0.12971 | -0.0064857 | -0.0049411 | -0.068817 | -0.0089124 | 0.059778 | 0.058039 | 0.0039948 | -0.0079148 | 63.4323 | 63.5788 | 7.2144 | -59.5139 | 63.4735 | -59.4406 | -59.5047 | -59.1888 | 4.9072 | -59.5505 | 63.4689 | 63.3545 | -59.523 | -59.6054 | -0.064087 | -0.12817 | 0.009156 | 122.9553 | -0.13733 | -0.009155 | -0.032043 | -0.14648 | -0.22888 | 0.004578 | 0.18768 | -0.17395 | 0.054932 | -0.10986 | 122.85 | 122.8088 | 66.5909 | -122.9691 | 122.8455 | 122.731 | 64.2838 | -123.0698
1271.0156 | 123.1201 | -59.4131 | 63.3865 | 0.19058 | 0.010226 | 0.070173 | 0.070303 | 0.13099 | 0.0014185 | -0.0028049 | 0.21347 | -0.0072034 | 0.062555 | 0.056971 | 0.0065582 | -0.0085556 | 63.382 | 63.5193 | 6.9901 | -59.5734 | 63.4506 | -59.4635 | -59.5276 | -59.1751 | 4.0146 | -59.6191 | 63.414 | 63.3087 | -59.5963 | -59.642 | -0.050354 | -0.11444 | 0.064087 | 122.9324 | -0.16022 | -0.045776 | -0.004578 | -0.1831 | -0.22888 | 0.027465 | 0.23804 | -0.20599 | 0.022888 | -0.07782 | 122.8638 | 122.7951 | 66.4032 | -122.9141 | 122.8271 | 122.7219 | 63.4277 | -123.0286
1272.0156 | 122.9919 | -59.436 | 63.446 | 0.10666 | 0.01578 | 0.06825 | 0.068594 | 0.12715 | 0.0022729 | -0.00024146 | 0.45761 | -0.0042126 | 0.063623 | 0.058253 | 0.00549 | -0.0079148 | 62.9745 | 63.4232 | 6.6696 | -59.4727 | 63.5193 | -59.4772 | -59.5505 | -59.317 | 4.4037 | -59.697 | 63.5284 | 63.4186 | -59.5734 | -59.6695 | -0.041199 | -0.11444 | 0.073242 | 122.8592 | -0.036621 | 0.07782 | -0.4715 | -0.13733 | -0.23346 | 0.082397 | 0.11902 | -0.26093 | -0.027465 | -0.027466 | 122.9553 | 122.4106 | 66.1057 | -122.9965 | 122.9645 | 122.8546 | 63.8397 | -123.1155
1273.0156 | 123.111 | -59.4131 | 63.4186 | 0.18295 | 0.010226 | 0.06761 | 0.068808 | 0.13014 | 0.00077755 | -0.0019505 | -1.4268 | -0.006349 | 0.063196 | 0.059962 | 0.002713 | -0.0062058 | 63.4048 | 63.5284 | 6.5231 | -59.5642 | 63.4506 | -59.4681 | -59.5596 | -59.1888 | 4.5227 | -59.5505 | 63.4598 | 63.3545 | -59.5367 | -59.6191 | -0.054932 | -0.14648 | 0.032044 | 122.9416 | -0.15106 | -0.004578 | -0.013733 | -0.1236 | -0.20599 | 0.041199 | 0.2243 | -0.13733 | 0.068665 | -0.064087 | 122.8638 | 122.818 | 65.9363 | -122.9782 | 122.8729 | 122.7676 | 63.9359 | -123.0377
1274.0156 | 122.9736 | -59.4223 | 63.4598 | 0.083771 | 0.013858 | 0.066969 | 0.070944 | 0.12971 | 0.0014185 | -0.0025913 | 0.13718 | -0.005708 | 0.061914 | 0.060176 | 0.0052764 | -0.0089828 | 63.3453 | 63.4277 | 6.3538 | -59.5963 | 63.5513 | -59.436 | -59.5276 | -59.317 | 4.8706 | -59.7061 | 63.5284 | 63.4552 | -59.5825 | -59.6558 | -0.013733 | -0.10529 | 0.091553 | 122.85 | -0.17395 | -0.068664 | -0.11444 | -0.16022 | -0.23346 | 0.068664 | 0.10529 | -0.28381 | -0.050354 | -0.004578 | 122.9736 | 122.7676 | 65.7761 | -122.9874 | 122.9507 | 122.8775 | 64.2929 | -123.1155
1275.0156 | 123.1018 | -59.3445 | 63.4323 | -0.0077822 | 0.0048855 | -0.03557 | 0.066245 | 0.12693 | -0.0064857 | -0.0023777 | 0.10666 | -0.0084852 | 0.062769 | 0.055903 | 0.0031402 | -0.0062058 | 63.3774 | 63.5239 | 6.2668 | -59.5322 | 63.5422 | -59.436 | -59.4955 | -59.2026 | 5.3787 | -59.5322 | 63.5101 | 63.414 | -59.5047 | -59.5734 | -0.091553 | -0.15106 | 0.10986 | 122.8683 | -0.18768 | -0.036622 | -0.054932 | -0.16022 | -0.22888 | 0.07782 | 0.14191 | -0.18768 | 0.041198 | -0.018311 | 122.8867 | 122.7219 | 65.6113 | -122.9279 | 122.8546 | 122.7585 | 64.7232 | -123.0057
1276.0156 | 123.0057 | -59.3811 | 63.4506 | 0.0914 | 0.01578 | 0.068891 | 0.069663 | 0.13121 | 0.0039819 | -0.0023777 | 0.10666 | -0.0042126 | 0.065119 | 0.05633 | 0.0052764 | -0.0077012 | 63.3499 | 63.3957 | 6.0425 | -59.61 | 63.5651 | -59.4543 | -59.5184 | -59.3124 | 5.6122 | -59.5779 | 63.5742 | 63.4598 | -59.5688 | -59.6283 | -0.073242 | -0.13733 | 0.11444 | 122.7768 | -0.22888 | -0.091552 | -0.10071 | -0.18768 | -0.24719 | 0.1236 | 0.068665 | -0.19684 | 0.050354 | 0.009155 | 122.9462 | 122.731 | 65.4236 | -122.9691 | 122.9553 | 122.8409 | 64.9933 | -123.0789
1277.0156 | 123.0606 | -59.4086 | 63.4186 | 0.19058 | 0.013003 | 0.066969 | 0.069235 | 0.1295 | 0.0014185 | -0.0030185 | 0.20584 | -0.0050672 | 0.06341 | 0.057826 | 0.0037812 | -0.0079148 | 63.3682 | 63.4644 | 6.1707 | -59.5871 | 63.5056 | -59.4452 | -59.5139 | -59.2484 | 5.6442 | -59.6054 | 63.4918 | 63.382 | -59.5413 | -59.6237 | -0.036621 | -0.10529 | 0.086975 | 122.8729 | -0.17853 | -0.073242 | -0.050354 | -0.13275 | -0.21515 | 0.073242 | 0.16022 | -0.19684 | 0.01831 | -0.036621 | 122.9141 | 122.7768 | 65.5792 | -122.9324 | 122.9004 | 122.7905 | 65.0528 | -123.0423
1278.0156 | 122.9691 | -59.4131 | 63.4598 | 0.053253 | 0.016208 | 0.065901 | 0.073721 | 0.12993 | 0.0018457 | -0.0015231 | 0.11429 | -0.002931 | 0.0664 | 0.060176 | 0.0048492 | -0.0098374 | 63.327 | 63.3774 | 6.2988 | -59.6146 | 63.5376 | -59.4635 | -59.5505 | -59.3445 | 5.8456 | -59.729 | 63.5101 | 63.4369 | -59.5779 | -59.6558 | -0.050354 | -0.13733 | 0.07782 | 122.7905 | -0.20142 | -0.064087 | -0.13275 | -0.16479 | -0.24262 | 0.050354 | 0.068665 | -0.31586 | -0.073242 | -0.022888 | 122.9507 | 122.7402 | 65.712 | -123.0103 | 122.9233 | 122.85 | 65.2588 | -123.1155
1279.0156 | 123.0881 | -59.3948 | 63.3911 | 0.2211 | 0.0091581 | 0.066755 | 0.06774 | 0.13099 | -0.0011451 | -0.0036595 | 0.19058 | -0.0059216 | 0.06341 | 0.057612 | 0.0022858 | -0.0079148 | 63.4232 | 63.4552 | 6.2851 | -59.5551 | 63.4598 | -59.4589 | -59.523 | -59.23 | 6.0837 | -59.5963 | 63.4598 | 63.3636 | -59.5642 | -59.6146 | -0.064087 | -0.12817 | 0.068665 | 122.85 | -0.16022 | -0.032044 | 0.032044 | -0.16937 | -0.21973 | 0.068665 | 0.16479 | -0.20142 | 0.018311 | -0.027466 | 122.8546 | 122.818 | 65.6799 | -122.9141 | 122.8546 | 122.7585 | 65.4785 | -123.0057
1280.0156 | 122.9691 | -59.3903 | 63.4094 | -0.084076 | 0.0070217 | 0.069532 | 0.069663 | 0.12993 | -0.0052039 | -0.0066501 | -0.03067 | -0.006349 | 0.058283 | 0.056971 | 0.0014312 | -0.0064194 | 63.3957 | 63.5788 | 6.4041 | -59.5139 | 63.5056 | -59.4269 | -59.5139 | -59.2255 | 6.1752 | -59.5322 | 63.446 | 63.3911 | -59.5367 | -59.6237 | -0.036621 | -0.1236 | 0.09613 | 122.9691 | -0.1236 | 0 | -0.013733 | -0.14648 | -0.23346 | 0.036621 | 0.16479 | -0.14191 | 0.091552 | -0.018311 | 122.8958 | 122.7859 | 65.7944 | -122.9233 | 122.8363 | 122.7814 | 65.5655 | -123.0331
1281.0156 | 123.1155 | -59.4177 | 63.3774 | 0.19058 | 0.010013 | 0.068037 | 0.06774 | 0.12843 | 0.0016321 | -0.0021641 | 0.24399 | -0.0069898 | 0.063623 | 0.058253 | 0.00549 | -0.0057786 | 63.3316 | 63.4369 | 6.3034 | -59.6237 | 63.4827 | -59.4955 | -59.5825 | -59.2621 | 5.9647 | -59.6191 | 63.414 | 63.327 | -59.6008 | -59.6649 | -0.077819 | -0.1648 | 0.10529 | 122.8546 | -0.20599 | -0.041198 | -0.045776 | -0.18311 | -0.24719 | 0.036621 | 0.15564 | -0.20142 | 0.045776 | -0.050354 | 122.9004 | 122.7493 | 65.7211 | -122.9599 | 122.8317 | 122.7448 | 65.3824 | -123.0423
1282.0156 | 122.9965 | -59.4315 | 63.4506 | -0.023041 | 0.014499 | 0.066969 | 0.071158 | 0.13163 | 0.0027001 | -0.0010959 | 0.060883 | -0.0061352 | 0.062982 | 0.059107 | 0.0029266 | -0.0094102 | 63.3545 | 63.4186 | 6.5094 | -59.6146 | 63.501 | -59.4681 | -59.5596 | -59.3262 | 5.6992 | -59.7198 | 63.4872 | 63.3957 | -59.6008 | -59.6603 | -0.036621 | -0.12817 | 0.050354 | 122.85 | -0.1831 | -0.054932 | -0.096131 | -0.16937 | -0.22888 | 0.036621 | 0.10529 | -0.28839 | -0.05951 | -0.054932 | 122.9324 | 122.7859 | 65.9409 | -123.0103 | 122.9187 | 122.8271 | 65.1306 | -123.111
1283.0156 | 123.1064 | -59.3948 | 63.4048 | 0.17532 | 0.01279 | 0.068464 | 0.070944 | 0.12907 | -0.0015723 | -0.0040867 | 0.24399 | -0.0086988 | 0.064264 | 0.058039 | 0.0033538 | -0.006633 | 63.3362 | 63.4323 | 6.6559 | -59.5963 | 63.5101 | -59.4727 | -59.5322 | -59.2346 | 5.6442 | -59.6283 | 63.4369 | 63.4048 | -59.5779 | -59.642 | -0.07782 | -0.13733 | 0.10529 | 122.8271 | -0.20142 | -0.064086 | -0.068664 | -0.18311 | -0.24719 | 0.032044 | 0.16022 | -0.23346 | 0.013733 | 0 | 122.905 | 122.731 | 66.0507 | -122.937 | 122.8317 | 122.7997 | 65.0391 | -123.0469
1284.0156 | 122.9782 | -59.4315 | 63.4232 | 0.060882 | 0.011081 | 0.067823 | 0.069022 | 0.13099 | 0.0027001 | -0.0017369 | 0.11429 | -0.0054944 | 0.065332 | 0.060816 | 0.0033538 | -0.0079148 | 63.3087 | 63.3774 | 6.8573 | -59.6283 | 63.5101 | -59.5139 | -59.5688 | -59.3399 | 5.3101 | -59.7473 | 63.5147 | 63.4644 | -59.5963 | -59.6924 | -0.082397 | -0.13733 | 0.086975 | 122.8088 | -0.19684 | -0.059509 | -0.11444 | -0.16479 | -0.26093 | 0.091552 | 0.091553 | -0.31586 | -0.054931 | 0.041198 | 122.9416 | 122.7402 | 66.2888 | -122.9919 | 122.9462 | 122.8958 | 64.7415 | -123.1155
1285.0156 | 123.0515 | -59.3857 | 63.4323 | 0.20584 | 0.011294 | 0.066969 | 0.071372 | 0.13014 | -0.00029045 | -0.0021641 | 0.22873 | -0.0048536 | 0.063196 | 0.058894 | 0.0024994 | -0.0062058 | 63.3545 | 63.4277 | 6.8527 | -59.5779 | 63.5239 | -59.4452 | -59.5184 | -59.2667 | 5.5161 | -59.642 | 63.4964 | 63.4186 | -59.5734 | -59.6191 | -0.059509 | -0.13275 | 0.091553 | 122.8134 | -0.19226 | -0.059509 | -0.07782 | -0.18768 | -0.23346 | 0.064087 | 0.11902 | -0.25635 | -0.022888 | -0.013733 | 122.9095 | 122.7402 | 66.2384 | -122.9507 | 122.8821 | 122.8043 | 64.9017 | -123.0515
1286.0156 | 122.9645 | -59.4223 | 63.4918 | -0.00015269 | 0.014071 | 0.066541 | 0.071158 | 0.12693 | 0.0039819 | -0.0034457 | 0.11429 | -0.0048536 | 0.063623 | 0.055262 | 0.0031402 | -0.008342 | 63.3728 | 63.4323 | 6.6925 | -59.5734 | 63.5513 | -59.4452 | -59.523 | -59.3079 | 5.365 | -59.7015 | 63.5422 | 63.4644 | -59.5367 | -59.642 | -0.022888 | -0.10071 | 0.05951 | 122.8546 | -0.15106 | -0.050354 | -0.11902 | -0.11444 | -0.21973 | 0.050354 | 0.11444 | -0.27924 | -0.059509 | -0.027466 | 122.9736 | 122.7951 | 66.1148 | -123.0148 | 122.9645 | 122.8867 | 64.7873 | -123.1338
1287.0156 | 123.1293 | -59.4131 | 63.382 | 0.21347 | 0.0097989 | 0.067396 | 0.065817 | 0.12886 | -0.0041357 | -0.0047275 | 0.22873 | -0.0050672 | 0.064478 | 0.060389 | 0.0029266 | -0.0068466 | 63.3545 | 63.4781 | 7.0496 | -59.5688 | 63.446 | -59.4818 | -59.5367 | -59.23 | 5.452 | -59.61 | 63.4277 | 63.3728 | -59.5963 | -59.6466 | -0.068665 | -0.1236 | 0.064087 | 122.8912 | -0.15564 | -0.032044 | -0.027466 | -0.1831 | -0.23346 | 0.045776 | 0.18311 | -0.19684 | 0.036621 | -0.009155 | 122.8592 | 122.7676 | 66.4627 | -122.9187 | 122.8409 | 122.7859 | 64.8651 | -123.0286
1288.0156 | 122.9691 | -59.3994 | 63.4689 | -0.0077822 | 0.013858 | 0.067823 | 0.073294 | 0.13099 | 0.00056395 | -0.0053683 | -0.015411 | -0.003999 | 0.064905 | 0.058894 | 0.0033538 | -0.008342 | 63.3636 | 63.4277 | 6.9168 | -59.5688 | 63.5651 | -59.4269 | -59.523 | -59.2941 | 5.452 | -59.6878 | 63.5422 | 63.4872 | -59.5459 | -59.6375 | -0.027466 | -0.1236 | 0.09613 | 122.8271 | -0.16937 | -0.045777 | -0.10529 | -0.14648 | -0.23804 | 0.073242 | 0.10529 | -0.28839 | -0.050354 | 0.018311 | 122.9645 | 122.7631 | 66.3162 | -122.9919 | 122.9416 | 122.8867 | 64.8514 | -123.1064
1289.0156 | 123.0286 | -59.3536 | 63.4964 | 0.16006 | 0.015353 | 0.065473 | 0.069663 | 0.13057 | -0.00093145 | -0.0030185 | 0.25162 | -0.0059216 | 0.064051 | 0.058894 | 0.002713 | -0.0057786 | 63.3728 | 63.4689 | 6.7886 | -59.5642 | 63.588 | -59.4269 | -59.4543 | -59.2072 | 5.246 | -59.5963 | 63.5513 | 63.4964 | -59.4955 | -59.5688 | -0.073242 | -0.10071 | 0.091553 | 122.8226 | -0.21057 | -0.10986 | -0.1236 | -0.14191 | -0.21515 | 0.054932 | 0.14648 | -0.24261 | -0.027465 | 0 | 122.9416 | 122.7264 | 66.1423 | -122.9507 | 122.905 | 122.85 | 64.5996 | -123.0652
1290.0156 | 122.9736 | -59.3719 | 63.5239 | 0.18295 | 0.013431 | 0.067823 | 0.070303 | 0.12993 | -0.00050425 | -0.0034457 | -0.3511 | -0.0086988 | 0.064905 | 0.059748 | 0.00079042 | -0.0085556 | 63.382 | 63.446 | 6.5277 | -59.5367 | 63.5925 | -59.4269 | -59.4864 | -59.1797 | 5.3192 | -59.6329 | 63.5696 | 63.5239 | -59.523 | -59.5917 | -0.054932 | -0.11444 | 0.068664 | 122.818 | -0.16479 | -0.050354 | -0.14191 | -0.15106 | -0.21973 | 0.045776 | 0.19226 | -0.26093 | -0.041199 | 0 | 122.9645 | 122.7539 | 65.8997 | -123.0103 | 122.9416 | 122.8958 | 64.6912 | -123.1155
1291.0156 | 123.0972 | -59.3674 | 63.414 | 0.19058 | 0.010653 | 0.068678 | 0.070731 | 0.1295 | 0.00077755 | -0.0040867 | 0.34317 | -0.006349 | 0.062128 | 0.058894 | 0.0031402 | -0.0094102 | 63.382 | 63.5101 | 6.8024 | -59.5413 | 63.5193 | -59.4177 | -59.4955 | -59.2072 | 5.3009 | -59.5596 | 63.4827 | 63.4186 | -59.5505 | -59.5825 | -0.050354 | -0.12817 | 0.10529 | 122.8775 | -0.17395 | -0.045777 | -0.032043 | -0.18311 | -0.21515 | 0.068665 | 0.16022 | -0.19226 | 0.022889 | 0.004578 | 122.8867 | 122.7493 | 66.1697 | -122.9095 | 122.85 | 122.7859 | 64.6683 | -122.9965
1292.0156 | 122.9691 | -59.3308 | 63.5376 | 0.13718 | 0.016421 | 0.065687 | 0.071372 | 0.13121 | 0.00099115 | -0.0036595 | 0.12192 | -0.0037854 | 0.067682 | 0.057612 | 0.0012176 | -0.0072738 | 63.3682 | 63.4369 | 6.7245 | -59.523 | 63.6108 | -59.3857 | -59.4818 | -59.0881 | 4.9576 | -59.5642 | 63.6154 | 63.533 | -59.4635 | -59.5688 | -0.054931 | -0.15106 | 0.073242 | 122.7676 | -0.19226 | -0.041198 | -0.16937 | -0.13275 | -0.23804 | 0.077819 | 0.24262 | -0.23346 | 0.004578 | -0.004578 | 122.9416 | 122.699 | 66.0553 | -123.0194 | 122.9462 | 122.8638 | 64.2883 | -123.1064
1293.0156 | 123.1201 | -59.3216 | 63.4918 | 0.20584 | 0.012149 | 0.06825 | 0.070303 | 0.12864 | -0.00093145 | -0.0053683 | 0.24399 | -0.007417 | 0.063623 | 0.059748 | 0.0020722 | -0.0096238 | 63.4277 | 63.5193 | 6.6879 | -59.491 | 63.5376 | -59.3903 | -59.4543 | -59.1568 | 5.246 | -59.523 | 63.5284 | 63.4689 | -59.4955 | -59.5688 | -0.068665 | -0.13275 | 0.045777 | 122.8409 | -0.16937 | -0.036621 | -0.064087 | -0.17395 | -0.24719 | 0.036621 | 0.16479 | -0.20142 | 0.045777 | -0.022888 | 122.8592 | 122.7493 | 66.0095 | -122.9462 | 122.85 | 122.7905 | 64.5676 | -123.0606
1294.0156 | 123.0331 | -59.3262 | 63.5193 | 0.30502 | 0.013431 | 0.067396 | 0.07009 | 0.1327 | 0.00035035 | -0.0043003 | 0.18295 | -0.006349 | 0.065546 | 0.059748 | 0.0035674 | -0.0077012 | 63.4369 | 63.4872 | 6.0471 | -59.5047 | 63.6292 | -59.3536 | -59.4681 | -59.1888 | 5.0125 | -59.5917 | 63.5925 | 63.5696 | -59.4818 | -59.5505 | -0.027466 | -0.14191 | 0.10986 | 122.8134 | -0.17853 | -0.036621 | -0.082397 | -0.15564 | -0.2243 | 0.073242 | 0.13733 | -0.2655 | -0.041199 | 0.050354 | 122.9553 | 122.7631 | 65.3732 | -122.9874 | 122.9187 | 122.8958 | 64.3387 | -123.0698
1295.0156 | 123.0789 | -59.3033 | 63.4872 | 0.13718 | 0.01044 | 0.069532 | 0.069235 | 0.13185 | -0.0017859 | -0.0053683 | 0.26688 | -0.0048536 | 0.063196 | 0.059321 | 0.0029266 | -0.0064194 | 63.4369 | 63.5239 | 5.983 | -59.5001 | 63.5742 | -59.3674 | -59.4543 | -59.1476 | 5.2734 | -59.5184 | 63.5422 | 63.5101 | -59.4589 | -59.5551 | -0.064087 | -0.15106 | 0.086975 | 122.8271 | -0.19684 | -0.045776 | -0.050354 | -0.15564 | -0.25177 | 0.054931 | 0.15564 | -0.21515 | 0.036621 | 0.022888 | 122.8775 | 122.7402 | 65.2863 | -122.9416 | 122.8455 | 122.8134 | 64.5767 | -123.0423
1296.0156 | 122.8683 | -59.3719 | 63.4598 | 0.099029 | 0.016208 | 0.068464 | 0.069663 | 0.12779 | 0.00035035 | -0.0047275 | 0.15244 | -0.0054944 | 0.064051 | 0.060389 | 0.0050628 | -0.0074876 | 63.4003 | 63.4781 | 6.0425 | -59.6741 | 63.6154 | -59.3903 | -59.4772 | -59.2346 | 5.2689 | -59.6283 | 63.5925 | 63.5468 | -59.5184 | -59.5734 | -0.018311 | -0.10529 | 0.15564 | 122.85 | -0.30212 | -0.19684 | -0.059509 | -0.14648 | -0.20142 | 0.13275 | 0.13733 | -0.25635 | -0.054932 | 0.086975 | 122.9874 | 122.7722 | 65.4144 | -122.937 | 122.9645 | 122.9187 | 64.6408 | -123.0331
1297.0156 | 123.0652 | -59.2667 | 63.5239 | 0.34317 | 0.013217 | 0.068037 | 0.069449 | 0.12993 | -0.0028541 | -0.0036595 | 0.29739 | -0.0086988 | 0.064264 | 0.059535 | 0.0037812 | -0.0068466 | 63.4918 | 63.6246 | 6.2714 | -59.4086 | 63.5696 | -59.3491 | -59.3857 | -59.0927 | 5.5252 | -59.6283 | 63.5284 | 63.4552 | -59.491 | -59.5322 | -0.082397 | -0.11902 | 0.045776 | 122.8912 | -0.14191 | -0.022888 | -0.032044 | -0.2243 | -0.2655 | 0.004577 | 0.17395 | -0.36163 | -0.09613 | -0.068665 | 122.8363 | 122.7585 | 65.538 | -122.9095 | 122.7951 | 122.7219 | 64.7919 | -123.056
1298.0156 | 123.0057 | -59.3124 | 63.5788 | -0.58762 | 0.0087307 | 0.068037 | 0.068594 | 0.12993 | -0.0017859 | -0.0038731 | 0.25162 | -0.0054944 | 0.065546 | 0.058253 | 0.0033538 | -0.0074876 | 63.4232 | 63.4964 | 6.0242 | -59.5825 | 63.6292 | -59.3903 | -59.4727 | -59.1751 | 5.4703 | -59.5596 | 63.6246 | 63.5605 | -59.4543 | -59.5413 | -0.07782 | -0.16022 | 0.050354 | 122.8088 | -0.27008 | -0.10986 | -0.15564 | -0.14191 | -0.22888 | 0.045777 | 0.13733 | -0.24719 | -0.01831 | -0.01831 | 122.9416 | 122.7356 | 65.3366 | -123.0515 | 122.937 | 122.8729 | 64.7827 | -123.1201
1299.0156 | 123.0515 | -59.2987 | 63.4644 | 0.26688 | 0.010867 | 0.066541 | 0.066885 | 0.12864 | -0.0022131 | -0.0040867 | 0.29739 | -0.0054944 | 0.064905 | 0.058039 | 0.0033538 | -0.008342 | 63.4872 | 63.6337 | 6.1935 | -59.4223 | 63.5971 | -59.3491 | -59.4177 | -59.0973 | 5.5756 | -59.4681 | 63.5605 | 63.5056 | -59.4452 | -59.523 | -0.050354 | -0.11902 | 0.13275 | 122.9324 | -0.1236 | -0.004577 | 0.022889 | -0.14648 | -0.2243 | 0.096131 | 0.20142 | -0.16937 | 0.054931 | 0.041199 | 122.8958 | 122.7859 | 65.4922 | -122.8821 | 122.8592 | 122.8043 | 64.8743 | -122.9874
1300.0156 | 122.9782 | -59.3124 | 63.5513 | 0.22873 | 0.013003 | 0.06761 | 0.064536 | 0.13206 | -0.0030677 | -0.0032321 | 0.26688 | -0.0072034 | 0.064691 | 0.061244 | 0.00549 | -0.008342 | 63.6383 | 63.4827 | 5.9738 | -59.3811 | 63.6749 | -59.3216 | -59.4131 | -59.1843 | 5.3696 | -59.5596 | 63.6429 | 63.5651 | -59.4589 | -59.5276 | -0.009155 | -0.10071 | 0.1236 | 122.7951 | -0.068665 | 0.032043 | 0.086975 | -0.14648 | -0.21515 | 0.091552 | 0.12817 | -0.24719 | -0.032043 | 0.013732 | 122.9874 | 122.9507 | 65.2863 | -122.9645 | 122.9553 | 122.8775 | 64.682 | -123.0789
1301.0156 | 123.1155 | -59.2712 | 63.5239 | 1.4342 | 0.0072355 | 0.0706 | 0.069235 | 0.12928 | -0.0017859 | -0.0047275 | 0.25162 | -0.0086988 | 0.062342 | 0.059962 | 0.0042084 | -0.0068466 | 63.5513 | 63.6337 | 6.2027 | -59.3994 | 63.5834 | -59.3079 | -59.404 | -59.0927 | 5.4565 | -59.4589 | 63.588 | 63.5147 | -59.4452 | -59.5184 | -0.036621 | -0.13275 | 0.059509 | 122.905 | -0.12817 | 0.004578 | 0.027466 | -0.17395 | -0.24719 | 0.064087 | 0.17853 | -0.18768 | 0.05951 | -0.009156 | 122.8546 | 122.8226 | 65.4739 | -122.9279 | 122.8592 | 122.7859 | 64.7278 | -123.0423
1302.0156 | 122.9828 | -59.3033 | 63.5742 | 0.12192 | 0.01514 | 0.066114 | 0.074362 | 0.12736 | 0.0020593 | -0.0051547 | 0.64835 | -0.0037854 | 0.065332 | 0.060389 | 0.0050628 | -0.0070602 | 63.4232 | 63.5056 | 5.9601 | -59.3582 | 63.6108 | -59.3719 | -59.4315 | -59.198 | 5.4245 | -59.5871 | 63.6612 | 63.5971 | -59.4589 | -59.5367 | -0.068664 | -0.12817 | 0.036621 | 122.8088 | -0.054931 | 0.073243 | -0.15106 | -0.15564 | -0.23346 | 0.086975 | 0.10529 | -0.28381 | -0.050354 | 0.022888 | 122.9141 | 122.7264 | 65.2634 | -123.0057 | 122.9645 | 122.9004 | 64.7278 | -123.111
1303.0156 | 123.1247 | -59.2072 | 63.5971 | 0.16006 | 0.013217 | 0.06526 | 0.068808 | 0.13014 | 0.00013675 | -0.0023777 | 0.35843 | -0.0065626 | 0.063196 | 0.059321 | 0.0052764 | -0.0091966 | 63.5193 | 63.6475 | 6.0562 | -59.404 | 63.6429 | -59.2941 | -59.3674 | -59.0561 | 5.4977 | -59.436 | 63.6337 | 63.5742 | -59.3674 | -59.4635 | -0.086975 | -0.16022 | 0.045776 | 122.8546 | -0.19684 | -0.036621 | -0.07782 | -0.16022 | -0.25635 | 0.036621 | 0.15106 | -0.22888 | 0.027466 | -0.022888 | 122.85 | 122.7264 | 65.2634 | -122.9645 | 122.8409 | 122.7814 | 64.7049 | -123.0606
1304.0156 | 123.0377 | -59.317 | 63.5193 | 0.21347 | 0.013431 | 0.06761 | 0.07009 | 0.1295 | 0.00099115 | -0.0030185 | 0.18295 | -0.005708 | 0.066614 | 0.058253 | 0.0046356 | -0.0074876 | 63.4232 | 63.4827 | 6.1066 | -59.523 | 63.6154 | -59.3903 | -59.4543 | -59.1797 | 5.4703 | -59.5871 | 63.5834 | 63.5101 | -59.4727 | -59.5413 | -0.073242 | -0.13733 | 0.09613 | 122.7997 | -0.20599 | -0.068664 | -0.09613 | -0.15564 | -0.2243 | 0.064087 | 0.13733 | -0.27008 | -0.045776 | -0.009155 | 122.9324 | 122.7402 | 65.4236 | -122.9736 | 122.9004 | 122.8271 | 64.7873 | -123.0606
1305.0156 | 123.1155 | -59.2117 | 63.5284 | 0.17532 | 0.0083035 | 0.068678 | 0.066885 | 0.13142 | -0.0019995 | -0.0030185 | 1.5028 | -0.0084852 | 0.062555 | 0.058253 | 0.0046356 | -0.0074876 | 63.5559 | 63.6658 | 6.4819 | -59.3811 | 63.62 | -59.2941 | -59.3857 | -59.024 | 5.8136 | -59.4269 | 63.6154 | 63.5513 | -59.3811 | -59.436 | -0.082397 | -0.17395 | 0.091553 | 122.8775 | -0.16937 | 0.004577 | 0.027466 | -0.16937 | -0.2243 | 0.086975 | 0.18768 | -0.21515 | 0.009155 | 0.022889 | 122.8317 | 122.7676 | 65.6937 | -122.9141 | 122.8271 | 122.7631 | 65.0253 | -122.9645
1306.0156 | 123.0469 | -59.2941 | 63.533 | 0.053253 | 0.0074491 | 0.072309 | 0.066885 | 0.12715 | -0.0081947 | -0.0066501 | 0.30502 | -0.0078442 | 0.059992 | 0.059107 | 0.002713 | -0.0072738 | 63.4323 | 63.5971 | 6.8527 | -59.3536 | 63.62 | -59.317 | -59.3994 | -59.1476 | 5.7495 | -59.4772 | 63.588 | 63.5101 | -59.4452 | -59.5093 | -0.022889 | -0.10529 | 0.086975 | 122.8912 | -0.05951 | 0.045776 | -0.10071 | -0.15106 | -0.21515 | 0.054932 | 0.14648 | -0.18311 | 0.032043 | -0.022888 | 122.9141 | 122.7264 | 66.1469 | -122.9324 | 122.8821 | 122.8043 | 65.0436 | -123.0423
1307.0156 | 123.1338 | -59.2621 | 63.5056 | 0.20584 | 0.011935 | 0.066114 | 0.071372 | 0.13078 | -7.6852e-05 | -0.0049411 | 0.24399 | -0.0078442 | 0.061914 | 0.057398 | 0.0033538 | -0.0085556 | 63.5101 | 63.6154 | 6.871 | -59.4223 | 63.5925 | -59.3353 | -59.4177 | -59.0561 | 5.4062 | -59.5276 | 63.5284 | 63.4735 | -59.4772 | -59.5276 | -0.073242 | -0.15564 | 0.086975 | 122.8775 | -0.16022 | -0.004577 | 0.004578 | -0.21515 | -0.2655 | 0.022888 | 0.20599 | -0.2655 | 0 | -0.032043 | 122.8546 | 122.7722 | 66.1331 | -122.9233 | 122.7905 | 122.7356 | 64.6683 | -123.0331
1308.0156 | 123.0743 | -59.317 | 63.4964 | 0.14481 | 0.01279 | 0.068678 | 0.07009 | 0.12928 | -0.00050425 | -0.0036595 | 0.20584 | -0.0069898 | 0.064691 | 0.059962 | 0.0057038 | -0.008342 | 63.4644 | 63.5193 | 6.9397 | -59.5001 | 63.6292 | -59.3903 | -59.4452 | -59.1385 | 5.5023 | -59.5688 | 63.5834 | 63.4964 | -59.4681 | -59.5505 | -0.073242 | -0.12817 | 0.13275 | 122.8363 | -0.1831 | -0.054932 | -0.032044 | -0.15106 | -0.23346 | 0.086975 | 0.17853 | -0.25177 | -0.018311 | 0 | 122.9462 | 122.7814 | 66.2567 | -122.9416 | 122.9004 | 122.8134 | 64.8193 | -123.0469
1309.0156 | 123.1567 | -59.2758 | 63.501 | 0.16006 | 0.010013 | 0.066541 | 0.068594 | 0.1295 | 0.0014185 | -0.0053683 | 0.28214 | -0.0082716 | 0.061701 | 0.059107 | 0.00549 | -0.0091966 | 63.5284 | 63.6108 | 6.5918 | -59.4269 | 63.588 | -59.3262 | -59.3948 | -59.0836 | 5.8044 | -59.4955 | 63.5559 | 63.5101 | -59.4589 | -59.5093 | -0.050354 | -0.11902 | 0.086975 | 122.8867 | -0.15106 | -0.032044 | 0.027465 | -0.1831 | -0.23346 | 0.054931 | 0.19226 | -0.21973 | 0.013733 | 0.009155 | 122.8638 | 122.8043 | 65.8676 | -122.8958 | 122.8317 | 122.7859 | 65.0803 | -123.0103
1310.0156 | 123.0286 | -59.3536 | 63.5101 | 0.12192 | 0.012576 | 0.068037 | 0.070944 | 0.12971 | 0.0014185 | -0.0034457 | 0.17532 | -0.006349 | 0.062128 | 0.058039 | 0.0035674 | -0.0085556 | 63.4277 | 63.4872 | 6.3995 | -59.5276 | 63.5925 | -59.404 | -59.4772 | -59.1705 | 5.896 | -59.5734 | 63.5651 | 63.4872 | -59.491 | -59.5367 | -0.050354 | -0.1236 | 0.082397 | 122.8409 | -0.17395 | -0.050354 | -0.082398 | -0.13733 | -0.18311 | 0.054931 | 0.18311 | -0.21973 | -0.036621 | -0.022888 | 122.9462 | 122.7814 | 65.7532 | -122.9874 | 122.9187 | 122.8409 | 65.2496 | -123.0469
1311.0156 | 123.0972 | -59.3445 | 63.4415 | 0.16769 | 0.011294 | 0.063978 | 0.064536 | 0.12993 | -0.0041357 | -0.0060093 | 0.32791 | -0.0095532 | 0.061487 | 0.059321 | 0.0050628 | -0.006633 | 63.5605 | 63.5513 | 6.4682 | -59.4543 | 63.5193 | -59.3994 | -59.4818 | -59.1248 | 6.0333 | -59.5276 | 63.4872 | 63.4506 | -59.5001 | -59.5871 | -0.054932 | -0.13733 | 0.07782 | 122.8958 | -0.10986 | 0.027466 | 0.11902 | -0.15564 | -0.24262 | 0.045777 | 0.21973 | -0.18311 | 0.059509 | 0.009156 | 122.8638 | 122.905 | 65.8127 | -122.9233 | 122.8317 | 122.7951 | 65.3778 | -123.0286
1312.0156 | 123.0286 | -59.3491 | 63.5147 | 0.11429 | 0.013858 | 0.066114 | 0.072867 | 0.12886 | 0.0018457 | -0.0034457 | 0.20584 | -0.0078442 | 0.064264 | 0.060176 | 0.0050628 | -0.0087692 | 63.414 | 63.4781 | 6.4407 | -59.5413 | 63.6154 | -59.3994 | -59.4635 | -59.166 | 5.777 | -59.61 | 63.5834 | 63.5101 | -59.5047 | -59.5688 | -0.050354 | -0.11444 | 0.10071 | 122.8271 | -0.19226 | -0.07782 | -0.10071 | -0.15564 | -0.21973 | 0.068665 | 0.18311 | -0.26093 | -0.041198 | -0.004577 | 122.9645 | 122.7631 | 65.7898 | -122.9782 | 122.9324 | 122.8592 | 65.126 | -123.0835
1313.0156 | 123.1338 | -59.2804 | 63.533 | 0.18295 | 0.011508 | 0.064405 | 0.069022 | 0.13078 | -0.0034949 | -0.0021641 | -0.9996 | -0.0069898 | 0.062982 | 0.058253 | 0.0035674 | -0.0074876 | 63.5101 | 63.6337 | 6.4728 | -59.4223 | 63.5651 | -59.3536 | -59.404 | -59.0286 | 5.603 | -59.4543 | 63.5834 | 63.5193 | -59.4452 | -59.5184 | -0.073242 | -0.1236 | 0.032043 | 122.9141 | -0.14191 | -0.01831 | -0.022888 | -0.16479 | -0.23804 | 0.050354 | 0.25177 | -0.17395 | 0.064087 | -0.013733 | 122.8455 | 122.7905 | 65.7532 | -122.937 | 122.8638 | 122.7997 | 64.8834 | -123.0515
1314.0156 | 123.0286 | -59.3079 | 63.5284 | 0.57968 | 0.013217 | 0.068037 | 0.073294 | 0.12864 | 0.00035035 | -0.0049411 | 0.18295 | -0.0059216 | 0.065546 | 0.060603 | 0.0035674 | -0.0096238 | 63.4552 | 63.4872 | 6.4178 | -59.4955 | 63.6429 | -59.3765 | -59.4498 | -59.1705 | 5.5252 | -59.6008 | 63.6017 | 63.5513 | -59.4727 | -59.5551 | -0.068665 | -0.14191 | 0.11444 | 122.7951 | -0.18768 | -0.045776 | -0.073242 | -0.16479 | -0.24719 | 0.073243 | 0.13733 | -0.29297 | -0.045776 | 0.022889 | 122.9507 | 122.7631 | 65.7257 | -122.9782 | 122.9095 | 122.8592 | 64.8331 | -123.0835
1315.0156 | 123.1201 | -59.2941 | 63.4964 | 0.14481 | 0.0087307 | 0.06526 | 0.069235 | 0.13121 | -0.00071785 | -0.0043003 | 0.29739 | -0.0082716 | 0.061701 | 0.059748 | 0.0035674 | -0.0064194 | 63.4781 | 63.6017 | 6.8985 | -59.4452 | 63.5651 | -59.3536 | -59.4406 | -59.0927 | 5.5115 | -59.4955 | 63.5193 | 63.4827 | -59.4635 | -59.5367 | -0.05951 | -0.14648 | 0.068664 | 122.8958 | -0.15106 | -0.004577 | -0.018311 | -0.16937 | -0.24262 | 0.022888 | 0.20142 | -0.20142 | 0.041199 | -0.013733 | 122.8592 | 122.7722 | 66.1926 | -122.937 | 122.8134 | 122.7768 | 64.8056 | -123.0331
1316.0156 | 123.0103 | -59.3399 | 63.533 | 0.16006 | 0.011722 | 0.065687 | 0.073508 | 0.12993 | -7.6852e-05 | -0.0017369 | 0.28976 | -0.0067762 | 0.063623 | 0.059748 | 0.0042084 | -0.0085556 | 63.0844 | 63.6887 | 7.0038 | -59.4269 | 63.6383 | -59.3674 | -59.4543 | -59.1888 | 5.4016 | -59.6054 | 63.6154 | 63.5422 | -59.4818 | -59.5688 | -0.027466 | -0.11444 | 0.10529 | 123.0286 | -0.086975 | 0.027466 | -0.44861 | -0.14191 | -0.22888 | 0.082397 | 0.15106 | -0.2655 | -0.036621 | 0.009155 | 122.9782 | 122.4243 | 66.3437 | -122.9874 | 122.9553 | 122.8821 | 64.7415 | -123.1018
1317.0156 | 123.0881 | -59.3079 | 63.4918 | 0.19058 | 0.011722 | 0.065046 | 0.07009 | 0.12736 | -0.0022131 | -0.0051547 | 0.52628 | -0.0076306 | 0.064478 | 0.059748 | 0.0059174 | -0.0077012 | 63.4644 | 63.5422 | 6.7383 | -59.4818 | 63.5651 | -59.3719 | -59.4315 | -59.111 | 5.3741 | -59.5139 | 63.5284 | 63.4781 | -59.5001 | -59.5322 | -0.064087 | -0.1236 | 0.073242 | 122.85 | -0.17395 | -0.050354 | -0.027466 | -0.19226 | -0.2243 | 0.036621 | 0.19684 | -0.20599 | 0.018311 | -0.013733 | 122.8729 | 122.7722 | 66.0461 | -122.9233 | 122.8363 | 122.7859 | 64.682 | -123.024
1318.0156 | 123.024 | -59.3399 | 63.5101 | 0.037994 | 0.01279 | 0.067823 | 0.071372 | 0.13356 | 0.0014185 | -0.0015231 | 0.12955 | -0.0059216 | 0.067041 | 0.057185 | 0.0039948 | -0.008342 | 63.4277 | 63.4918 | 6.6101 | -59.5367 | 63.6154 | -59.404 | -59.4589 | -59.1705 | 5.0537 | -59.5871 | 63.5925 | 63.5101 | -59.5047 | -59.5642 | -0.064087 | -0.11902 | 0.10529 | 122.8317 | -0.19684 | -0.07782 | -0.082398 | -0.16479 | -0.2243 | 0.082397 | 0.16937 | -0.24719 | -0.022888 | 0 | 122.9553 | 122.7676 | 65.95 | -122.9691 | 122.9324 | 122.85 | 64.3936 | -123.0743
1319.0156 | 123.1018 | -59.3445 | 63.4552 | 0.17532 | 0.01044 | 0.068891 | 0.069235 | 0.13142 | -0.0015723 | -0.0034457 | 0.27451 | -0.0072034 | 0.063837 | 0.060176 | 0.0046356 | -0.0087692 | 63.4506 | 63.5605 | 6.9992 | -59.4864 | 63.501 | -59.3948 | -59.4681 | -59.1156 | 5.3879 | -59.7015 | 63.4781 | 63.4186 | -59.5139 | -59.5871 | -0.050354 | -0.1236 | 0.045777 | 122.905 | -0.14191 | -0.01831 | -0.004577 | -0.16937 | -0.24262 | 0.022888 | 0.22888 | -0.35706 | -0.11444 | -0.036621 | 122.8455 | 122.7951 | 66.3437 | -122.9233 | 122.8226 | 122.7631 | 64.7324 | -123.0423
1320.0156 | 122.9828 | -59.3262 | 63.5559 | 0.11429 | 0.014285 | 0.068464 | 0.072653 | 0.12971 | 0.0031273 | -0.0030185 | 0.045624 | -0.0050672 | 0.062342 | 0.060389 | 0.0063446 | -0.0077012 | 63.208 | 63.7711 | 6.7245 | -59.5551 | 63.6475 | -59.3719 | -59.4406 | -59.1614 | 5.3787 | -59.6146 | 63.5925 | 63.5651 | -59.4955 | -59.5688 | -0.045776 | -0.11444 | 0.091553 | 123.0972 | -0.22888 | -0.11444 | -0.3479 | -0.16937 | -0.24262 | 0.036621 | 0.16479 | -0.28839 | -0.045776 | 0.009155 | 122.9736 | 122.5342 | 66.0507 | -122.9965 | 122.9187 | 122.8912 | 64.7049 | -123.1247
1321.0156 | 123.111 | -59.2758 | 63.5147 | 0.18295 | 0.012149 | 0.067823 | 0.067526 | 0.13249 | 0.00099115 | -0.0043003 | 0.28976 | -0.0048536 | 0.061914 | 0.059748 | 0.002713 | -0.0085556 | 63.4781 | 63.5651 | 6.4957 | -59.4589 | 63.5971 | -59.3582 | -59.4543 | -59.079 | 5.1682 | -59.4955 | 63.5696 | 63.5056 | -59.4635 | -59.5505 | -0.082397 | -0.17853 | 0.082398 | 122.8409 | -0.1831 | -0.004577 | -0.036621 | -0.18768 | -0.27466 | 0.054932 | 0.19684 | -0.21973 | 0.054932 | -0.009155 | 122.8729 | 122.7539 | 65.7715 | -122.9691 | 122.8455 | 122.7814 | 64.444 | -123.0652
1322.0156 | 123.0148 | -59.2987 | 63.5605 | -0.2977 | 0.01279 | 0.067396 | 0.070517 | 0.13014 | 0.00099115 | -0.0025913 | 0.19058 | -0.00464 | 0.064264 | 0.060816 | 0.0048492 | -0.0077012 | 63.4506 | 63.5284 | 5.9555 | -59.4864 | 63.652 | -59.3536 | -59.4406 | -59.1156 | 5.2231 | -59.5825 | 63.6292 | 63.5696 | -59.4818 | -59.5139 | -0.054932 | -0.14191 | 0.091553 | 122.8271 | -0.18768 | -0.045776 | -0.10986 | -0.18311 | -0.21515 | 0.068664 | 0.18311 | -0.28381 | -0.068665 | 0.009155 | 122.9507 | 122.7493 | 65.2542 | -123.0011 | 122.9279 | 122.8683 | 64.5218 | -123.0743
1323.0156 | 123.0972 | -59.2941 | 63.501 | 0.20584 | 0.012149 | 0.066755 | 0.067954 | 0.12993 | -0.0015723 | -0.0023777 | 0.24399 | -0.0078442 | 0.06341 | 0.061885 | 0.004422 | -0.0057786 | 63.4689 | 63.533 | 6.0471 | -59.4818 | 63.6154 | -59.3536 | -59.436 | -59.0927 | 5.159 | -59.5276 | 63.6063 | 63.5422 | -59.4589 | -59.5184 | -0.05951 | -0.14191 | 0.11444 | 122.8271 | -0.18768 | -0.045777 | -0.032044 | -0.16479 | -0.22431 | 0.10529 | 0.20142 | -0.23346 | -0.009155 | 0.041198 | 122.9095 | 122.7631 | 65.3412 | -122.937 | 122.9004 | 122.8363 | 64.4531 | -123.0194
1324.0156 | 122.9828 | -59.3536 | 63.533 | 0.099029 | 0.015353 | 0.066969 | 0.07009 | 0.12822 | 0.0014185 | -0.0015231 | 0.49576 | -0.006349 | 0.064905 | 0.061244 | 0.0024994 | -0.0077012 | 63.4369 | 63.4689 | 6.6101 | -59.5139 | 63.6292 | -59.3674 | -59.4955 | -59.1934 | 5.1453 | -59.5871 | 63.6154 | 63.5742 | -59.491 | -59.5596 | -0.013733 | -0.14191 | 0.09613 | 122.8226 | -0.16022 | -0.018311 | -0.09613 | -0.13733 | -0.20599 | 0.082397 | 0.16022 | -0.23346 | -0.027466 | 0.041199 | 122.9828 | 122.7905 | 65.9637 | -123.0286 | 122.9691 | 122.9279 | 64.4989 | -123.0927
1325.0156 | 123.0972 | -59.285 | 63.5239 | 0.18295 | 0.01044 | 0.066969 | 0.071585 | 0.128 | -0.0022131 | -0.0021641 | 0.25925 | -0.0050672 | 0.063623 | 0.059962 | 0.0039948 | -0.0064194 | 63.4827 | 63.5605 | 6.7612 | -59.4498 | 63.6017 | -59.3216 | -59.4269 | -59.0561 | 5.0674 | -59.4864 | 63.5788 | 63.5284 | -59.4589 | -59.5047 | -0.036621 | -0.14191 | 0.07782 | 122.8455 | -0.16479 | -0.022888 | -0.041199 | -0.17395 | -0.21973 | 0.054931 | 0.22888 | -0.20142 | 0.018311 | 0.004577 | 122.8867 | 122.7676 | 66.0461 | -122.9507 | 122.8638 | 122.8134 | 64.3524 | -123.0286
1326.0156 | 122.9645 | -59.317 | 63.5742 | 0.0074768 | 0.014926 | 0.068037 | 0.07009 | 0.12971 | 0.0024865 | -0.0023777 | 0.12955 | -0.0052808 | 0.065759 | 0.060603 | 0.00549 | -0.0074876 | 63.4369 | 63.5056 | 6.8344 | -59.491 | 63.6612 | -59.3536 | -59.4223 | -59.1339 | 4.39 | -59.6008 | 63.6292 | 63.5971 | -59.4406 | -59.5505 | -0.036621 | -0.10529 | 0.086975 | 122.8226 | -0.17395 | -0.068665 | -0.13733 | -0.1236 | -0.23346 | 0.054931 | 0.18311 | -0.28381 | -0.050354 | 0.022888 | 122.9782 | 122.7539 | 66.1514 | -122.9965 | 122.9462 | 122.9141 | 63.707 | -123.1247
1327.0156 | 123.143 | -59.3079 | 63.501 | 0.15244 | 0.0095853 | 0.068037 | 0.067526 | 0.13228 | -0.0015723 | -0.0038731 | 0.25925 | -0.0065626 | 0.062342 | 0.059321 | 0.002713 | -0.0064194 | 63.4644 | 63.588 | 7.2052 | -59.4589 | 63.5651 | -59.3445 | -59.4269 | -59.0469 | 4.5868 | -59.5047 | 63.5193 | 63.4598 | -59.4681 | -59.5322 | -0.036621 | -0.11902 | 0.064086 | 122.8958 | -0.15106 | -0.032043 | -0.036622 | -0.16022 | -0.2243 | 0.01831 | 0.26093 | -0.19684 | 0.027466 | -0.041199 | 122.8729 | 122.7722 | 66.5131 | -122.9279 | 122.8271 | 122.7676 | 63.8947 | -123.0331
1328.0156 | 123.0331 | -59.3445 | 63.5651 | 0.11429 | 0.016208 | 0.066541 | 0.068381 | 0.12907 | 0.0012047 | -0.0055821 | 0.16769 | -0.001222 | 0.062769 | 0.058467 | 0.002713 | -0.0074876 | 63.382 | 63.4415 | 6.8939 | -59.523 | 63.62 | -59.3811 | -59.4543 | -59.1156 | 4.4083 | -59.5367 | 63.5925 | 63.5605 | -59.4681 | -59.5688 | -0.036622 | -0.10986 | 0.054932 | 122.7859 | -0.17853 | -0.068664 | -0.18311 | -0.1236 | -0.22431 | 0.027466 | 0.22888 | -0.19226 | 0.032044 | -0.004577 | 122.9645 | 122.7264 | 66.2384 | -123.0194 | 122.937 | 122.905 | 63.7527 | -123.1338
1329.0156 | 123.1018 | -59.2896 | 63.5147 | 0.18295 | 0.010653 | 0.069532 | 0.069663 | 0.13099 | -0.0028541 | -0.0032321 | 0.25162 | -0.0035718 | 0.063623 | 0.058253 | 0.0039948 | -0.008342 | 63.4369 | 63.533 | 6.9855 | -59.4818 | 63.6017 | -59.3857 | -59.4406 | -59.0469 | 4.5136 | -59.5139 | 63.5742 | 63.4918 | -59.491 | -59.5093 | -0.09613 | -0.15106 | 0.086976 | 122.8226 | -0.19226 | -0.041199 | -0.077819 | -0.20142 | -0.21973 | 0.05951 | 0.24262 | -0.2243 | -0.004578 | -0.022888 | 122.8912 | 122.7264 | 66.275 | -122.9553 | 122.8638 | 122.7814 | 63.8031 | -123.024
1330.0156 | 122.9645 | -59.3262 | 63.5651 | -0.015411 | 0.014285 | 0.066328 | 0.073081 | 0.13014 | 0.0016321 | -0.0047275 | 0.060883 | -0.0076306 | 0.06341 | 0.059535 | 0.0024994 | -0.0089828 | 63.4781 | 63.5513 | 7.2052 | -59.4727 | 63.6292 | -59.3491 | -59.4223 | -59.0881 | 4.8614 | -59.5642 | 63.6292 | 63.588 | -59.4772 | -59.5413 | -0.022888 | -0.09613 | 0.064087 | 122.8775 | -0.14648 | -0.050354 | -0.086975 | -0.15106 | -0.21515 | 0.064087 | 0.23804 | -0.23804 | -0.022888 | 0.022889 | 122.9553 | 122.8043 | 66.5314 | -122.9874 | 122.9553 | 122.9141 | 64.1876 | -123.1064
1331.0156 | 123.0148 | -59.3216 | 63.5422 | 0.060882 | 0.014285 | 0.068891 | 0.069235 | 0.13292 | 0.00035035 | -0.0045139 | -0.67917 | -0.0069898 | 0.062555 | 0.059321 | 0.0033538 | -0.0081284 | 63.3865 | 63.2492 | 7.1686 | -59.7061 | 63.5422 | -59.4177 | -59.491 | -59.111 | 4.866 | -59.6191 | 63.5925 | 63.5376 | -59.4955 | -59.5459 | -0.096131 | -0.16937 | 0 | 122.5708 | -0.38452 | -0.21515 | -0.15564 | -0.17395 | -0.2243 | 0.050354 | 0.21057 | -0.29755 | -0.073243 | -0.004577 | 122.8638 | 122.7081 | 66.4902 | -123.0331 | 122.9141 | 122.8592 | 64.1876 | -123.0881
1332.0156 | 122.9828 | -59.3491 | 63.533 | 0.0074768 | 0.014071 | 0.065901 | 0.07009 | 0.12928 | 0.00099115 | -0.0021641 | 0.0914 | -0.0076306 | 0.064691 | 0.059962 | 0.00549 | -0.0077012 | 63.4277 | 63.4781 | 7.4249 | -59.5093 | 63.6154 | -59.3811 | -59.491 | -59.1431 | 4.6051 | -59.642 | 63.5559 | 63.5468 | -59.5139 | -59.5551 | -0.032044 | -0.14191 | 0.082397 | 122.8271 | -0.16022 | -0.01831 | -0.10529 | -0.16479 | -0.20599 | 0.022888 | 0.20599 | -0.29297 | -0.086975 | 0.013733 | 122.9645 | 122.7768 | 66.774 | -123.024 | 122.905 | 122.8958 | 63.9542 | -123.0881
1333.0156 | 123.0194 | -59.3353 | 63.5605 | -0.19852 | 0.012362 | 0.069959 | 0.07009 | 0.12886 | -0.0024269 | -0.0034457 | 0.19821 | -0.006349 | 0.062982 | 0.060389 | 0.0046356 | -0.0057786 | 63.4003 | 63.4964 | 7.3654 | -59.523 | 63.6292 | -59.3582 | -59.4772 | -59.0973 | 4.5547 | -59.5917 | 63.588 | 63.5147 | -59.5139 | -59.5505 | -0.022888 | -0.14191 | 0.068664 | 122.8317 | -0.18768 | -0.045776 | -0.16022 | -0.17853 | -0.21515 | 0.027466 | 0.23804 | -0.25635 | -0.041199 | -0.045777 | 122.9645 | 122.7356 | 66.7007 | -123.0377 | 122.9233 | 122.85 | 63.8901 | -123.111
1334.0156 | 122.9828 | -59.285 | 63.5971 | 0.022736 | 0.01578 | 0.065687 | 0.07244 | 0.13014 | -0.0017859 | -0.0013095 | 0.053253 | -0.0050672 | 0.064691 | 0.060176 | 0.0029266 | -0.008342 | 63.4689 | 63.5559 | 7.5256 | -59.4955 | 63.6337 | -59.3536 | -59.4223 | -59.0836 | 4.834 | -59.5642 | 63.6154 | 63.5834 | -59.4727 | -59.5551 | -0.068665 | -0.13733 | 0.036621 | 122.8409 | -0.21057 | -0.073242 | -0.12817 | -0.18768 | -0.27008 | 0.01831 | 0.20142 | -0.27924 | -0.009155 | -0.013733 | 122.9187 | 122.7539 | 66.8106 | -123.0194 | 122.9004 | 122.8683 | 64.119 | -123.1522
1335.0156 | 123.0789 | -59.317 | 63.5468 | 0.19058 | 0.014499 | 0.066969 | 0.072012 | 0.12758 | 0.00035035 | -0.0051547 | 0.25162 | -0.0059216 | 0.065119 | 0.058894 | 0.0050628 | -0.0077012 | 63.4186 | 63.5239 | 7.4661 | -59.5093 | 63.6063 | -59.3811 | -59.4315 | -59.0469 | 4.6234 | -59.5413 | 63.5925 | 63.5651 | -59.4818 | -59.523 | -0.064087 | -0.11444 | 0.059509 | 122.8409 | -0.19226 | -0.077819 | -0.12817 | -0.16479 | -0.20599 | 0.045776 | 0.27008 | -0.2243 | -0.018311 | 0.01831 | 122.9233 | 122.7356 | 66.7831 | -122.9782 | 122.9095 | 122.8821 | 63.9404 | -123.0698
1336.0156 | 123.0194 | -59.3353 | 63.5376 | -0.0383 | 0.013431 | 0.066755 | 0.071158 | 0.12886 | 0.0014185 | -0.0034457 | 0.060883 | -0.0042126 | 0.064691 | 0.059962 | 0.0052764 | -0.0087692 | 63.4689 | 63.5376 | 7.3196 | -59.5596 | 63.6154 | -59.3811 | -59.4498 | -59.1202 | 4.9438 | -59.5963 | 63.5925 | 63.5376 | -59.4818 | -59.5688 | -0.045777 | -0.11444 | 0.077819 | 122.8729 | -0.2243 | -0.10986 | -0.068665 | -0.14648 | -0.23346 | 0.054931 | 0.21515 | -0.26093 | -0.027465 | 0 | 122.9507 | 122.8043 | 66.655 | -122.9874 | 122.9279 | 122.8729 | 64.2792 | -123.1064
1337.0156 | 123.056 | -59.317 | 63.5513 | 0.0914 | 0.015994 | 0.068678 | 0.07009 | 0.13121 | 0.00056395 | -0.0034457 | 0.13718 | -0.0059216 | 0.064478 | 0.057826 | 0.0035674 | -0.004924 | 63.382 | 63.4415 | 7.0404 | -59.523 | 63.6154 | -59.3719 | -59.4498 | -59.1064 | 4.4724 | -59.4727 | 63.5834 | 63.5559 | -59.4818 | -59.5367 | -0.054931 | -0.13275 | 0.064086 | 122.7585 | -0.20599 | -0.073242 | -0.16937 | -0.16479 | -0.21973 | 0.032043 | 0.21057 | -0.15564 | 0.064087 | 0.004577 | 122.9324 | 122.699 | 66.3574 | -123.0011 | 122.9004 | 122.8729 | 63.7894 | -123.0881
1338.0156 | 123.0194 | -59.3216 | 63.5788 | 0.022736 | 0.014926 | 0.065687 | 0.070944 | 0.13078 | 0.00056395 | -0.0036595 | 0.053253 | -0.0052808 | 0.065973 | 0.059321 | 0.0031402 | -0.0074876 | 63.4323 | 63.5376 | 7.3334 | -59.4818 | 63.6063 | -59.3628 | -59.4589 | -59.1019 | 5.2505 | -59.6008 | 63.6154 | 63.5513 | -59.491 | -59.5734 | -0.041199 | -0.13733 | 0.027466 | 122.8592 | -0.16022 | -0.022889 | -0.14648 | -0.16937 | -0.25177 | 0.036621 | 0.21973 | -0.27924 | -0.027466 | -0.027465 | 122.9279 | 122.7539 | 66.655 | -123.0377 | 122.937 | 122.8729 | 64.5721 | -123.1522
1339.0156 | 122.9691 | -59.3445 | 63.5147 | 0.12955 | 0.014071 | 0.06761 | 0.064108 | 0.12864 | -0.0017859 | -0.0079319 | 0.18295 | -0.0050672 | 0.064051 | 0.060389 | 0.0033538 | -0.0079148 | 63.6383 | 63.3362 | 7.3013 | -59.4635 | 63.6292 | -59.4086 | -59.4772 | -59.1156 | 5.2277 | -59.6191 | 63.5788 | 63.5513 | -59.523 | -59.5871 | -0.064087 | -0.13275 | 0.11444 | 122.6807 | -0.11902 | 0.013733 | 0.1236 | -0.17853 | -0.24262 | 0.064087 | 0.22888 | -0.27466 | -0.032044 | 0.036622 | 122.9736 | 122.9828 | 66.6458 | -122.9919 | 122.9233 | 122.8958 | 64.5721 | -123.1018
1340.0156 | 122.9919 | -59.3536 | 63.5468 | -0.076447 | 0.014926 | 0.068037 | 0.071158 | 0.12886 | -7.6852e-05 | -0.0047275 | 0.045624 | -0.0076306 | 0.065759 | 0.058894 | 0.00549 | -0.0068466 | 63.4369 | 63.5376 | 7.3471 | -59.5001 | 63.588 | -59.3765 | -59.4727 | -59.1064 | 5.6122 | -59.5963 | 63.5696 | 63.533 | -59.5093 | -59.5688 | -0.022888 | -0.11902 | 0.041199 | 122.8912 | -0.14648 | -0.027466 | -0.10986 | -0.15564 | -0.21515 | 0.022888 | 0.24719 | -0.24261 | -0.027465 | -0.013733 | 122.9416 | 122.7905 | 66.7007 | -123.0194 | 122.9233 | 122.8867 | 64.9658 | -123.1155
1341.0156 | 122.9507 | -59.3674 | 63.5422 | 0.11429 | 0.01578 | 0.06761 | 0.069449 | 0.13035 | 0.00099115 | -0.0034457 | 0.15244 | -0.0044264 | 0.064905 | 0.060816 | 0.0037812 | -0.008342 | 63.3408 | 63.4094 | 7.2327 | -59.5825 | 63.5925 | -59.4177 | -59.5001 | -59.166 | 5.9875 | -59.6191 | 63.5605 | 63.4415 | -59.5596 | -59.6375 | -0.050354 | -0.13275 | 0.050354 | 122.7768 | -0.21515 | -0.082398 | -0.20142 | -0.19226 | -0.27008 | 0.018311 | 0.20142 | -0.25177 | 0.01831 | -0.10071 | 122.9599 | 122.7081 | 66.6 | -123.0423 | 122.9279 | 122.8088 | 65.3549 | -123.1796
1342.0156 | 123.0011 | -59.4131 | 63.4827 | -0.0383 | 0.013858 | 0.065046 | 0.070731 | 0.13035 | 0.0016321 | -0.0036595 | 0.083771 | -0.0059216 | 0.065332 | 0.060176 | 0.0029266 | -0.0081284 | 63.3911 | 63.4598 | 7.1548 | -59.5413 | 63.5651 | -59.4315 | -59.5001 | -59.1568 | 5.9967 | -59.6512 | 63.5376 | 63.4872 | -59.5734 | -59.6146 | -0.018311 | -0.086975 | 0.082397 | 122.8729 | -0.12817 | -0.041199 | -0.091553 | -0.16022 | -0.20142 | 0.054932 | 0.25635 | -0.23804 | -0.036621 | 0.004578 | 122.9782 | 122.8043 | 66.568 | -122.9828 | 122.9507 | 122.9004 | 65.4099 | -123.0972
1343.0156 | 123.0148 | -59.4131 | 63.4872 | 0.076141 | 0.013431 | 0.068678 | 0.070303 | 0.13078 | -7.6852e-05 | -0.0055821 | -0.69443 | -0.0069898 | 0.063837 | 0.059748 | 0.0031402 | -0.0072738 | 63.3179 | 63.1943 | 6.8253 | -59.761 | 63.4735 | -59.4864 | -59.5413 | -59.1568 | 5.6351 | -59.6741 | 63.5147 | 63.4781 | -59.5734 | -59.6283 | -0.073242 | -0.12817 | -0.013733 | 122.6074 | -0.3479 | -0.21973 | -0.16937 | -0.16022 | -0.21515 | 0.027465 | 0.25635 | -0.26093 | -0.045776 | -0.009156 | 122.8867 | 122.731 | 66.2384 | -123.0286 | 122.9279 | 122.8912 | 65.0482 | -123.1155
1344.0156 | 123.0881 | -59.3536 | 63.5239 | -0.084076 | 0.013431 | 0.066969 | 0.069663 | 0.13121 | -7.6852e-05 | -0.0062229 | 0.0074766 | -0.009126 | 0.064051 | 0.057398 | 0.0029266 | -0.0081284 | 63.4552 | 63.533 | 7.0496 | -59.4818 | 63.5925 | -59.3903 | -59.4727 | -59.0881 | 5.864 | -59.5825 | 63.5605 | 63.5376 | -59.5459 | -59.6008 | -0.036621 | -0.11902 | 0.068664 | 122.8867 | -0.12817 | -0.009156 | -0.068665 | -0.19226 | -0.24719 | 0.036621 | 0.2655 | -0.22888 | 0.01831 | 0.013733 | 122.9462 | 122.8088 | 66.4032 | -122.9965 | 122.9141 | 122.8912 | 65.2176 | -123.1247
1345.0156 | 122.8592 | -59.3948 | 63.4644 | 0.045624 | 0.015994 | 0.066114 | 0.070303 | 0.12886 | 0.00035035 | -0.0038731 | 0.20584 | -0.005708 | 0.064691 | 0.062098 | 0.0035674 | -0.0059922 | 63.3545 | 63.4232 | 7.0221 | -59.5642 | 63.6063 | -59.436 | -59.491 | -59.1431 | 5.0491 | -59.642 | 63.5651 | 63.5056 | -59.5367 | -59.6191 | -0.041199 | -0.096131 | 0.14191 | 122.818 | -0.16937 | -0.073242 | -0.10986 | -0.14191 | -0.22431 | 0.10071 | 0.25177 | -0.24719 | -0.022888 | 0.041199 | 123.0011 | 122.7493 | 66.4169 | -122.9553 | 122.9599 | 122.9004 | 64.444 | -123.0835
1346.0156 | 123.0331 | -59.3353 | 63.5101 | -0.15274 | 0.012362 | 0.067396 | 0.070517 | 0.13014 | 0.00099115 | -0.0032321 | -0.19089 | -0.0072034 | 0.064478 | 0.061244 | 0.0048492 | -0.0070602 | 63.4369 | 63.5468 | 7.1503 | -59.5963 | 63.5696 | -59.4131 | -59.5001 | -59.0652 | 5.0537 | -59.5825 | 63.5742 | 63.5239 | -59.523 | -59.5734 | -0.07782 | -0.16479 | 0.059509 | 122.8821 | -0.26093 | -0.09613 | -0.073242 | -0.18768 | -0.23804 | 0.064087 | 0.27008 | -0.24719 | -0.009156 | 0.013733 | 122.905 | 122.7722 | 66.4856 | -123.0103 | 122.9095 | 122.8592 | 64.389 | -123.0835
1347.0156 | 122.9828 | -59.4315 | 63.4735 | 0.045624 | 0.013431 | 0.065901 | 0.071158 | 0.13057 | 0.00077755 | -0.0055821 | 0.11429 | -0.00464 | 0.0664 | 0.059535 | 0.0048492 | -0.0094102 | 63.3362 | 63.4323 | 7.2281 | -59.5505 | 63.5513 | -59.4498 | -59.5047 | -59.1797 | 5.0583 | -59.697 | 63.533 | 63.4689 | -59.6054 | -59.6283 | -0.01831 | -0.073242 | 0.07782 | 122.8638 | -0.11902 | -0.045776 | -0.13733 | -0.17395 | -0.19684 | 0.059509 | 0.25177 | -0.2655 | -0.068664 | -0.004578 | 122.9828 | 122.7676 | 66.6595 | -122.9782 | 122.9645 | 122.9004 | 64.4897 | -123.1018
1348.0156 | 123.0377 | -59.3674 | 63.5101 | -0.16037 | 0.013858 | 0.066114 | 0.07009 | 0.12907 | 0.0014185 | -0.0034457 | 0.0074766 | -0.0076306 | 0.065119 | 0.059748 | 0.0035674 | -0.0085556 | 63.4186 | 63.5239 | 7.2052 | -59.491 | 63.6108 | -59.4177 | -59.4818 | -59.0881 | 4.7333 | -59.5825 | 63.5742 | 63.5147 | -59.523 | -59.6146 | -0.050354 | -0.11444 | 0.10071 | 122.8912 | -0.1236 | -0.009155 | -0.091553 | -0.15564 | -0.24719 | 0.064087 | 0.27924 | -0.21515 | 0.032043 | 0.004577 | 122.9782 | 122.7859 | 66.5726 | -122.9919 | 122.9416 | 122.8821 | 64.1006 | -123.1247
1349.0156 | 122.9736 | -59.3719 | 63.5468 | -0.0077822 | 0.015567 | 0.065473 | 0.072012 | 0.128 | 0.00099115 | -0.0036595 | 0.16006 | -0.0065626 | 0.063623 | 0.061244 | 0.0074126 | -0.0070602 | 63.3453 | 63.4644 | 6.9489 | -59.523 | 63.5925 | -59.4131 | -59.5047 | -59.1476 | 4.1931 | -59.6512 | 63.5605 | 63.5147 | -59.5322 | -59.5917 | -0.041199 | -0.13275 | 0.045776 | 122.8363 | -0.15106 | -0.01831 | -0.20142 | -0.16022 | -0.21973 | 0.013733 | 0.2243 | -0.27924 | -0.059509 | -0.032044 | 122.9645 | 122.7173 | 66.3208 | -123.0515 | 122.9324 | 122.8867 | 63.5651 | -123.1384
1350.0156 | 123.0377 | -59.3308 | 63.5422 | -0.13748 | 0.011935 | 0.067823 | 0.070944 | 0.12993 | 0.00035035 | -0.0034457 | -0.015411 | -0.006349 | 0.061914 | 0.06103 | 0.0024994 | -0.0087692 | 63.4277 | 63.5651 | 7.3563 | -59.4269 | 63.6108 | -59.3674 | -59.4452 | -59.0698 | 4.2252 | -59.5596 | 63.6108 | 63.5284 | -59.5093 | -59.5779 | -0.036621 | -0.11444 | 0.068665 | 122.8958 | -0.09613 | 0.01831 | -0.11444 | -0.17853 | -0.24719 | 0.068665 | 0.26093 | -0.22888 | 0.018311 | -0.013733 | 122.9416 | 122.7585 | 66.687 | -122.9874 | 122.9416 | 122.8592 | 63.5559 | -123.1201
1351.0156 | 123.0148 | -59.2941 | 63.5925 | -0.061188 | 0.014285 | 0.067823 | 0.067313 | 0.12864 | 0.0020593 | -0.0057957 | 0.045624 | -0.0067762 | 0.065119 | 0.059962 | 0.0029266 | -0.008342 | 63.4598 | 63.5788 | 7.1182 | -59.4269 | 63.6429 | -59.3582 | -59.4498 | -59.0332 | 3.9368 | -59.5734 | 63.6337 | 63.5788 | -59.4772 | -59.5367 | -0.064087 | -0.15564 | 0.050354 | 122.8729 | -0.13275 | 0.022888 | -0.13275 | -0.18311 | -0.24262 | 0.041199 | 0.26093 | -0.27924 | -0.036621 | -0.013733 | 122.937 | 122.7539 | 66.4124 | -123.0423 | 122.9279 | 122.8729 | 63.2309 | -123.1293
1352.0156 | 122.9874 | -59.3536 | 63.5239 | -0.12222 | 0.012149 | 0.067182 | 0.068381 | 0.12928 | -0.00071785 | -0.0045139 | 0.030365 | -0.0078442 | 0.064905 | 0.06103 | 0.0033538 | -0.006633 | 63.4323 | 63.5788 | 7.3471 | -59.4727 | 63.6108 | -59.3903 | -59.4406 | -59.0378 | 4.4815 | -59.5688 | 63.5788 | 63.5422 | -59.5047 | -59.5871 | -0.036621 | -0.086975 | 0.086975 | 122.9324 | -0.11902 | -0.032043 | -0.091553 | -0.15106 | -0.23346 | 0.054931 | 0.31586 | -0.21515 | 0.01831 | 0.01831 | 122.9645 | 122.7859 | 66.7007 | -122.9645 | 122.9324 | 122.8958 | 63.8351 | -123.111
1353.0156 | 122.9965 | -59.3719 | 63.5147 | -0.053558 | 0.014499 | 0.068464 | 0.072012 | 0.13014 | 0.0022729 | -0.0030185 | 0.060883 | -0.0037854 | 0.062982 | 0.059535 | 0.0059174 | -0.0059922 | 63.3957 | 63.4918 | 7.3013 | -59.5093 | 63.5834 | -59.4269 | -59.491 | -59.0973 | 4.5959 | -59.6329 | 63.5696 | 63.5284 | -59.5139 | -59.5871 | -0.054932 | -0.11902 | 0.068665 | 122.8638 | -0.13733 | -0.01831 | -0.11902 | -0.14191 | -0.21515 | 0.054932 | 0.27466 | -0.26093 | -0.045777 | 0.013733 | 122.9553 | 122.7676 | 66.6733 | -123.0057 | 122.9416 | 122.9004 | 63.9679 | -123.1018
1354.0156 | 123.0286 | -59.3262 | 63.5376 | -0.21378 | 0.012149 | 0.069532 | 0.072653 | 0.12971 | 0.00013675 | -0.0047275 | -0.099335 | -0.00464 | 0.063196 | 0.059535 | 0.0037812 | -0.0074876 | 63.4506 | 63.5651 | 7.3792 | -59.4635 | 63.6292 | -59.3811 | -59.4635 | -59.0378 | 4.5364 | -59.5505 | 63.5742 | 63.5651 | -59.4772 | -59.5551 | -0.054932 | -0.13733 | 0.091552 | 122.8912 | -0.13733 | 0 | -0.086975 | -0.15106 | -0.22888 | 0.036621 | 0.28839 | -0.2243 | 0.004578 | 0.027465 | 122.9553 | 122.7768 | 66.7053 | -123.0011 | 122.9004 | 122.8912 | 63.8626 | -123.0927
1355.0156 | 122.9736 | -59.3445 | 63.5513 | 0.068512 | 0.013644 | 0.067182 | 0.070517 | 0.12907 | -7.6852e-05 | -0.0036595 | 0.12192 | -0.0067762 | 0.064051 | 0.061244 | 0.004422 | -0.0068466 | 63.414 | 63.5193 | 6.189 | -59.491 | 63.6337 | -59.3536 | -59.4315 | -59.0698 | 4.1473 | -59.61 | 63.6246 | 63.5468 | -59.4955 | -59.5642 | -0.009156 | -0.086976 | 0.082397 | 122.8638 | -0.14648 | -0.059509 | -0.13733 | -0.15106 | -0.21973 | 0.073242 | 0.27466 | -0.2655 | -0.045776 | -0.004578 | 122.9782 | 122.7585 | 65.5334 | -122.9828 | 122.9691 | 122.8912 | 63.4918 | -123.1155
1356.0156 | 123.111 | -59.2575 | 63.533 | 0.2211 | 0.011935 | 0.070814 | 0.070517 | 0.13057 | -0.0024269 | -0.0028049 | 0.14481 | -0.0082716 | 0.064264 | 0.059321 | 0.0033538 | -0.0053512 | 63.6017 | 63.3362 | 6.395 | -59.3353 | 63.5468 | -59.3582 | -59.4223 | -58.9645 | 4.3442 | -59.4589 | 63.5513 | 63.5284 | -59.4452 | -59.5001 | -0.10071 | -0.1648 | 0.013733 | 122.5937 | -0.07782 | 0.086975 | 0.068665 | -0.18768 | -0.24262 | 0.018311 | 0.29297 | -0.20142 | 0.041199 | -0.004578 | 122.8043 | 122.8592 | 65.6525 | -122.9553 | 122.8088 | 122.7859 | 63.6017 | -123.0331
1357.0156 | 123.0377 | -59.2575 | 63.5971 | -0.045929 | 0.016849 | 0.071027 | 0.070731 | 0.13249 | 0.0033411 | -0.0038731 | -0.023041 | -0.00464 | 0.063623 | 0.058253 | 0.0039948 | -0.006633 | 63.5513 | 63.6108 | 6.3217 | -59.4131 | 63.6932 | -59.3079 | -59.3719 | -58.9554 | 4.1061 | -59.5184 | 63.6566 | 63.5971 | -59.4315 | -59.491 | -0.050354 | -0.11444 | 0.09613 | 122.8683 | -0.15564 | -0.041199 | -0.045776 | -0.17395 | -0.23346 | 0.059509 | 0.30212 | -0.26093 | -0.027466 | 0 | 122.9507 | 122.8088 | 65.5792 | -122.9691 | 122.9141 | 122.8546 | 63.3636 | -123.0881
1358.0156 | 123.0881 | -59.2758 | 63.6429 | -0.16037 | 0.010867 | 0.068037 | 0.074149 | 0.12843 | -0.0026405 | -0.0040867 | -0.15274 | -0.0065626 | 0.062128 | 0.060176 | 0.0014312 | -0.008342 | 63.4827 | 63.5971 | 6.3858 | -59.404 | 63.7161 | -59.3079 | -59.3719 | -58.9828 | 3.8681 | -59.4864 | 63.6932 | 63.6246 | -59.4223 | -59.4727 | -0.032043 | -0.09613 | 0.073242 | 122.8729 | -0.12817 | -0.032044 | -0.16022 | -0.14648 | -0.19684 | 0.050354 | 0.29297 | -0.21057 | -0.013733 | -0.01831 | 122.9919 | 122.7585 | 65.6616 | -123.0148 | 122.9691 | 122.9004 | 63.1439 | -123.1155
1359.0156 | 122.9919 | -59.2392 | 63.6795 | -0.00015269 | 0.016635 | 0.069532 | 0.071158 | 0.13292 | 0.0022729 | -0.0034457 | 0.09903 | -0.0052808 | 0.064905 | 0.058894 | 0.0031402 | -0.0087692 | 63.5376 | 63.652 | 5.864 | -59.3719 | 63.739 | -59.2712 | -59.3582 | -58.9462 | 3.8086 | -59.5001 | 63.7024 | 63.6566 | -59.3948 | -59.4635 | -0.032043 | -0.11902 | 0.05951 | 122.8912 | -0.13275 | -0.013733 | -0.14191 | -0.15564 | -0.2243 | 0.022889 | 0.29297 | -0.26093 | -0.036621 | -0.022888 | 122.9782 | 122.7768 | 65.1031 | -123.0377 | 122.9416 | 122.8958 | 63.0478 | -123.143
1360.0156 | 123.0515 | -59.2163 | 63.6429 | -0.19089 | 0.014071 | 0.06761 | 0.067099 | 0.12971 | 0.00013675 | -0.0034457 | -0.11459 | -0.0061352 | 0.063196 | 0.059321 | 0.002713 | -0.0098374 | 63.5239 | 63.652 | 6.1478 | -59.3582 | 63.7299 | -59.2621 | -59.3399 | -58.9279 | 3.5065 | -59.4681 | 63.6978 | 63.6292 | -59.3903 | -59.4635 | -0.045776 | -0.1236 | 0.086975 | 122.8683 | -0.14191 | -0.01831 | -0.11902 | -0.17395 | -0.24719 | 0.054932 | 0.28839 | -0.25177 | -0.004578 | -0.013733 | 122.9462 | 122.7402 | 65.3641 | -122.9828 | 122.9141 | 122.8455 | 62.7228 | -123.1064
1361.0156 | 123.0881 | -59.2392 | 63.5788 | 0.16769 | 0.0095853 | 0.068037 | 0.066245 | 0.12779 | -0.0043495 | -0.0081455 | 0.30502 | -0.0082716 | 0.06106 | 0.059107 | 0.0029266 | -0.006633 | 63.5056 | 63.6703 | 6.1478 | -59.3765 | 63.6383 | -59.2896 | -59.3811 | -58.9233 | 3.6209 | -59.4406 | 63.6154 | 63.5834 | -59.3948 | -59.4543 | -0.050354 | -0.14191 | 0.05951 | 122.9095 | -0.13733 | 0.004578 | -0.073242 | -0.15564 | -0.21515 | 0.036621 | 0.31586 | -0.20142 | 0.013733 | 0.004578 | 122.8775 | 122.7448 | 65.387 | -122.9599 | 122.8546 | 122.8226 | 62.8601 | -123.0331
1362.0156 | 123.0194 | -59.2438 | 63.6337 | -0.17563 | 0.01044 | 0.067823 | 0.072867 | 0.13185 | 0.00077755 | -0.0049411 | -0.16037 | -0.0054944 | 0.064691 | 0.05868 | 0.0037812 | -0.0089828 | 63.501 | 63.5971 | 5.983 | -59.3948 | 63.7024 | -59.2941 | -59.3491 | -58.9645 | 3.5614 | -59.491 | 63.6932 | 63.652 | -59.3994 | -59.4818 | -0.050354 | -0.10529 | 0.068665 | 122.8409 | -0.15106 | -0.045776 | -0.13275 | -0.15564 | -0.23804 | 0.059509 | 0.27923 | -0.24719 | -0.009155 | 0.018311 | 122.9462 | 122.7448 | 65.2267 | -122.9828 | 122.937 | 122.8958 | 62.8052 | -123.1155
1363.0156 | 122.9828 | -59.2392 | 63.6337 | -0.023041 | 0.014712 | 0.069105 | 0.071799 | 0.13035 | 0.0031273 | -0.0045139 | 0.037995 | -0.0065626 | 0.064478 | 0.05868 | 0.0046356 | -0.0068466 | 63.5101 | 63.6063 | 6.2531 | -59.404 | 63.6932 | -59.3079 | -59.3811 | -58.9828 | 3.5156 | -59.5184 | 63.6887 | 63.62 | -59.4131 | -59.4955 | -0.068664 | -0.14191 | 0.059509 | 122.8455 | -0.1648 | -0.022888 | -0.1236 | -0.17395 | -0.25635 | 0.054932 | 0.25635 | -0.27924 | -0.022889 | -0.013733 | 122.9324 | 122.7493 | 65.4922 | -123.0148 | 122.9279 | 122.8592 | 62.7548 | -123.1293
1364.0156 | 123.0057 | -59.2209 | 63.6749 | -0.22903 | 0.010867 | 0.066969 | 0.071799 | 0.12715 | -0.0011451 | -0.0040867 | -0.13748 | -0.005708 | 0.063837 | 0.061457 | 0.0039948 | -0.0074876 | 63.5147 | 63.6246 | 6.308 | -59.3765 | 63.739 | -59.2667 | -59.3445 | -58.96 | 3.1998 | -59.4589 | 63.7299 | 63.6612 | -59.3994 | -59.4452 | -0.045777 | -0.1236 | 0.064087 | 122.8455 | -0.15564 | -0.032044 | -0.16022 | -0.17853 | -0.2243 | 0.054931 | 0.26093 | -0.23804 | -0.013733 | -0.013733 | 122.9599 | 122.7356 | 65.5289 | -123.0194 | 122.9507 | 122.8821 | 62.4207 | -123.1201
1365.0156 | 123.056 | -59.2163 | 63.6566 | -0.068817 | 0.013431 | 0.068464 | 0.069876 | 0.12907 | 0.00035035 | -0.0047275 | -0.023041 | -0.0048536 | 0.0664 | 0.06103 | 0.0035674 | -0.0079148 | 63.5513 | 63.6749 | 6.2347 | -59.3674 | 63.7207 | -59.2987 | -59.3491 | -58.9142 | 2.829 | -59.5276 | 63.6887 | 63.6292 | -59.3948 | -59.4498 | -0.082397 | -0.13275 | 0.064087 | 122.8912 | -0.15106 | -0.018311 | -0.10529 | -0.17853 | -0.23346 | 0.032044 | 0.30212 | -0.31128 | -0.07782 | -0.027466 | 122.937 | 122.7676 | 65.4511 | -123.0057 | 122.905 | 122.8455 | 62.0453 | -123.1064
1366.0312 | 123.1201 | -59.198 | 63.62 | -0.084076 | 0.0063809 | -0.035357 | 0.06539 | 0.12715 | -0.0084083 | -0.0079319 | 0.12192 | -0.0095532 | 0.059778 | 0.060816 | 0.00014962 | -0.0059922 | 63.5193 | 63.7161 | 6.4499 | -59.3399 | 63.6749 | -59.2667 | -59.3262 | -58.8776 | 3.1128 | -59.3811 | 63.6612 | 63.5925 | -59.3399 | -59.4406 | -0.068665 | -0.12817 | 0.054932 | 122.9141 | -0.14191 | -0.013733 | -0.10071 | -0.14191 | -0.24262 | 0.041199 | 0.32043 | -0.18311 | 0.059509 | -0.027466 | 122.8729 | 122.7173 | 65.6479 | -122.9462 | 122.8592 | 122.7905 | 62.3108 | -123.0606
1367.0156 | 123.0606 | -59.2117 | 63.6154 | -0.076447 | 0.014712 | 0.066969 | 0.075003 | 0.12886 | 0.0022729 | -0.0085727 | -0.03067 | -0.0069898 | 0.064691 | 0.059321 | 0.0042084 | -0.0098374 | 63.4323 | 63.6566 | 6.2714 | -59.3308 | 63.7024 | -59.2712 | -59.3628 | -58.9005 | 3.1357 | -59.4818 | 63.6978 | 63.62 | -59.3948 | -59.4269 | -0.059509 | -0.15106 | 0.086976 | 122.8683 | -0.11902 | 0.032043 | -0.1831 | -0.1831 | -0.21515 | 0.082398 | 0.31128 | -0.27008 | -0.054932 | 0.004578 | 122.9141 | 122.644 | 65.4831 | -122.9782 | 122.9095 | 122.8317 | 62.3474 | -123.0423
1368.0156 | 122.9965 | -59.2026 | 63.6795 | -0.19089 | 0.0091581 | 0.070173 | 0.069876 | 0.13057 | -0.0026405 | -0.0030185 | -0.11459 | -0.0065626 | 0.062342 | 0.060816 | 0.0014312 | -0.0068466 | 63.5147 | 63.6475 | 5.7861 | -59.3765 | 63.7665 | -59.2712 | -59.3399 | -58.9371 | 3.2547 | -59.4681 | 63.7299 | 63.6749 | -59.3765 | -59.4452 | -0.068664 | -0.13733 | 0.086975 | 122.85 | -0.17395 | -0.036621 | -0.16479 | -0.17395 | -0.24261 | 0.050354 | 0.2655 | -0.2655 | -0.022889 | -0.004577 | 122.9691 | 122.7173 | 64.9887 | -123.0194 | 122.9324 | 122.8775 | 62.4573 | -123.1247
1369.0156 | 123.0835 | -59.1614 | 63.6932 | -0.13748 | 0.015567 | 0.067182 | 0.070517 | 0.13014 | 0.0014185 | -0.0036595 | -0.0077819 | -0.006349 | 0.066187 | 0.059321 | 0.0042084 | -0.0077012 | 63.588 | 63.7207 | 6.0242 | -59.3079 | 63.7711 | -59.2392 | -59.3033 | -58.8684 | 2.9388 | -59.4223 | 63.7253 | 63.6703 | -59.3399 | -59.4177 | -0.07782 | -0.14191 | 0.07782 | 122.8821 | -0.14648 | -0.004577 | -0.10529 | -0.17853 | -0.25635 | 0.032044 | 0.29297 | -0.26093 | -0.004577 | -0.022888 | 122.9324 | 122.7493 | 65.1855 | -122.9965 | 122.8867 | 122.8317 | 62.1002 | -123.111
1370.0156 | 123.0331 | -59.1888 | 63.6887 | -0.18326 | 0.011081 | 0.068891 | 0.069663 | 0.12907 | -0.0013587 | -0.0036595 | -0.14511 | -0.0076306 | 0.062342 | 0.059107 | 0.0029266 | -0.0077012 | 63.5376 | 63.6749 | 5.7358 | -59.3445 | 63.7756 | -59.2392 | -59.3262 | -58.9096 | 3.0624 | -59.436 | 63.7207 | 63.7024 | -59.3811 | -59.4223 | -0.050354 | -0.13733 | 0.086975 | 122.8638 | -0.15564 | -0.01831 | -0.15106 | -0.19226 | -0.23346 | 0.032043 | 0.27924 | -0.24719 | -0.013733 | 0.013733 | 122.9645 | 122.7264 | 64.9246 | -123.0148 | 122.9095 | 122.8912 | 62.2513 | -123.111
1371.0156 | 123.0469 | -59.1934 | 63.6246 | 0.15244 | 0.0065945 | 0.06825 | 0.070517 | 0.13057 | -0.0052039 | -0.0066501 | 0.31265 | -0.007417 | 0.062555 | 0.059962 | 0.0014312 | -0.0068466 | 63.5513 | 63.7299 | 5.7312 | -59.3491 | 63.6703 | -59.2346 | -59.3262 | -58.873 | 3.0396 | -59.3903 | 63.6612 | 63.5971 | -59.3719 | -59.4498 | -0.041199 | -0.13275 | 0.045776 | 122.9233 | -0.15564 | -0.022888 | -0.073242 | -0.17853 | -0.25635 | 0.036621 | 0.32043 | -0.19684 | 0.059509 | -0.027466 | 122.8638 | 122.7448 | 64.9246 | -122.9507 | 122.8546 | 122.7905 | 62.233 | -123.0743
1372.0156 | 123.0103 | -59.1751 | 63.739 | -0.31296 | 0.010653 | 0.06761 | 0.071585 | 0.1295 | -0.0015723 | -0.0047275 | -0.038299 | -0.008058 | 0.06341 | 0.059962 | 0.0048492 | -0.0085556 | 63.5284 | 63.7482 | 5.7907 | -59.3308 | 63.7802 | -59.2072 | -59.2758 | -58.8776 | 2.9114 | -59.4223 | 63.7756 | 63.707 | -59.3536 | -59.3903 | -0.032043 | -0.10071 | 0.041198 | 122.9233 | -0.15564 | -0.054932 | -0.21057 | -0.17853 | -0.21515 | 0.036621 | 0.29755 | -0.24719 | -0.032043 | -0.032044 | 122.9553 | 122.7036 | 64.9658 | -123.0148 | 122.9507 | 122.8821 | 62.0865 | -123.1293
1373.0156 | 122.9965 | -59.1888 | 63.6841 | -0.168 | 0.014071 | 0.066755 | 0.073294 | 0.13014 | 0.0033411 | -0.0036595 | -0.15274 | -0.008058 | 0.065119 | 0.059107 | 0.0042084 | -0.0085556 | 63.588 | 63.7024 | 5.4016 | -59.3124 | 63.7527 | -59.2529 | -59.2941 | -58.8776 | 3.2913 | -59.4269 | 63.7207 | 63.6383 | -59.3491 | -59.4131 | -0.064087 | -0.10529 | 0.068665 | 122.8912 | -0.1236 | -0.018311 | -0.09613 | -0.16022 | -0.2243 | 0.036621 | 0.31128 | -0.23804 | -0.013733 | -0.045776 | 122.9416 | 122.7768 | 64.5905 | -122.9782 | 122.9095 | 122.8271 | 62.4802 | -123.0972
1374.0156 | 123.0057 | -59.1522 | 63.707 | -0.19089 | 0.0072355 | 0.070173 | 0.069663 | 0.13121 | -0.0032813 | -0.0034457 | -0.19089 | -0.0065626 | 0.062342 | 0.059321 | 0.0018584 | -0.0064194 | 63.5696 | 63.7161 | 4.5273 | -59.3124 | 63.7894 | -59.2163 | -59.285 | -58.873 | 3.0304 | -59.3857 | 63.826 | 63.7482 | -59.2712 | -59.3674 | -0.064087 | -0.13275 | 0.082398 | 122.8683 | -0.16022 | -0.027466 | -0.13733 | -0.11902 | -0.21515 | 0.11902 | 0.27924 | -0.23346 | -0.01831 | 0.041199 | 122.9416 | 122.7219 | 63.6795 | -122.9919 | 122.9782 | 122.9004 | 62.1826 | -123.0743
1375.0156 | 123.0423 | -59.1476 | 63.7299 | -0.21378 | 0.0097989 | 0.068891 | 0.069663 | 0.12864 | 0.00099115 | -0.0060093 | -0.16037 | -0.0059216 | 0.066187 | 0.058467 | 0.0033538 | -0.0089828 | 63.5742 | 63.7024 | 4.2847 | -59.3079 | 63.8031 | -59.2209 | -59.2941 | -58.8593 | 2.7924 | -59.3903 | 63.7756 | 63.6749 | -59.3536 | -59.3948 | -0.073242 | -0.14648 | 0.073243 | 122.85 | -0.16022 | -0.013733 | -0.15564 | -0.20599 | -0.24719 | 0.045777 | 0.28839 | -0.24262 | 0.004577 | -0.054931 | 122.9507 | 122.7219 | 63.4323 | -123.024 | 122.9233 | 122.8226 | 61.94 | -123.1247
1376.0156 | 122.9965 | -59.1751 | 63.6932 | -0.22903 | 0.0080899 | 0.069319 | 0.070944 | 0.1295 | -0.0013587 | -0.0066501 | -0.77072 | -0.0052808 | 0.064051 | 0.060176 | 0.0037812 | -0.0081284 | 63.5147 | 63.6841 | 4.4495 | -59.3491 | 63.7802 | -59.2209 | -59.2987 | -58.9279 | 2.6917 | -59.4315 | 63.7527 | 63.6566 | -59.3582 | -59.4086 | -0.045776 | -0.1236 | 0.086975 | 122.8592 | -0.17395 | -0.050354 | -0.17853 | -0.18311 | -0.23346 | 0.05951 | 0.24719 | -0.25635 | -0.022889 | -0.036621 | 122.9553 | 122.6898 | 63.6246 | -122.9919 | 122.9279 | 122.8317 | 61.8668 | -123.1018
1377.0156 | 123.0515 | -59.1843 | 63.7115 | -0.16037 | 0.011935 | 0.068891 | 0.073294 | 0.1295 | 0.0018457 | -0.0021641 | -0.11459 | -0.0059216 | 0.062982 | 0.058253 | 0.0037812 | -0.0072738 | 63.5696 | 63.7299 | 4.5319 | -59.285 | 63.7482 | -59.2072 | -59.3124 | -58.8501 | 2.5406 | -59.4177 | 63.7299 | 63.6658 | -59.3308 | -59.4131 | -0.022888 | -0.12817 | 0.036621 | 122.9141 | -0.10071 | 0.027466 | -0.14191 | -0.14648 | -0.22888 | 0.01831 | 0.33417 | -0.23346 | -0.004578 | -0.045777 | 122.9324 | 122.7539 | 63.7161 | -123.024 | 122.9141 | 122.85 | 61.7249 | -123.1247
1378.0156 | 123.0469 | -59.1293 | 63.7253 | -0.168 | 0.0072355 | 0.067182 | 0.070731 | 0.12993 | -0.0047767 | -0.0045139 | -0.061188 | -0.0084852 | 0.061487 | 0.059748 | 0.0046356 | -0.006633 | 63.6292 | 63.8443 | 4.4083 | -59.2438 | 63.7802 | -59.1751 | -59.2621 | -58.8135 | 2.2934 | -59.317 | 63.7802 | 63.6887 | -59.285 | -59.3491 | -0.045777 | -0.13275 | 0.054931 | 122.9736 | -0.11444 | 0.018311 | -0.096131 | -0.15564 | -0.21973 | 0.054931 | 0.31586 | -0.18768 | 0.032043 | -0.036621 | 122.9095 | 122.7585 | 63.5376 | -122.9874 | 122.9095 | 122.818 | 61.4227 | -123.0743
1379.0156 | 122.9965 | -59.1568 | 63.7115 | -0.25955 | 0.01044 | 0.069105 | 0.073508 | 0.13035 | -0.00071785 | -0.0057957 | 0.0074766 | -0.006349 | 0.062982 | 0.061244 | 0.0042084 | -0.008342 | 63.4369 | 63.9999 | 4.4724 | -59.4086 | 63.8397 | -59.2072 | -59.2804 | -58.8684 | 2.6093 | -59.4086 | 63.8077 | 63.7161 | -59.3124 | -59.3719 | -0.050354 | -0.1236 | 0.12817 | 123.1567 | -0.25177 | -0.12817 | -0.27466 | -0.15564 | -0.21515 | 0.09613 | 0.28839 | -0.25177 | -0.036621 | 0.004577 | 122.9965 | 122.5937 | 63.6291 | -122.9919 | 122.9645 | 122.8729 | 61.7661 | -123.0835
1380.0156 | 122.9736 | -59.1797 | 63.7436 | -0.20615 | 0.0068081 | 0.069105 | 0.073081 | 0.12971 | -0.0022131 | -0.0043003 | -0.19089 | -0.0082716 | 0.061273 | 0.060389 | 0.0074126 | -0.008342 | 63.5559 | 63.707 | 3.9688 | -59.3674 | 63.7985 | -59.2255 | -59.3033 | -58.9462 | 2.829 | -59.4681 | 63.7894 | 63.6612 | -59.3445 | -59.4131 | -0.045777 | -0.1236 | 0.054932 | 122.8867 | -0.18768 | -0.064087 | -0.18768 | -0.16479 | -0.23346 | 0.045777 | 0.23346 | -0.28839 | -0.054932 | -0.082397 | 122.9782 | 122.7356 | 63.1485 | -123.0469 | 122.9691 | 122.8409 | 62.0087 | -123.1567
1381.0156 | 123.0103 | -59.1797 | 63.7115 | 0.015106 | 0.010867 | 0.068464 | 0.073294 | 0.13099 | 0.00056395 | -0.0053683 | -0.099335 | -0.0072034 | 0.063837 | 0.060389 | 0.0020722 | -0.0089828 | 63.5422 | 63.6887 | 3.9001 | -59.3445 | 63.7848 | -59.2209 | -59.3124 | -58.8684 | 2.33 | -59.4177 | 63.7802 | 63.6703 | -59.3628 | -59.3903 | -0.041199 | -0.13275 | 0.073242 | 122.8683 | -0.16479 | -0.032043 | -0.16937 | -0.18311 | -0.21057 | 0.068664 | 0.31128 | -0.23804 | -0.027466 | -0.041199 | 122.9645 | 122.7219 | 63.0798 | -123.024 | 122.9599 | 122.85 | 61.5097 | -123.1018
1382.0156 | 123.0469 | -59.1522 | 63.6932 | -0.19089 | 0.0076627 | 0.068678 | 0.070731 | 0.12907 | -0.0047767 | -0.0051547 | -0.099335 | -0.008058 | 0.061914 | 0.059748 | 0.0031402 | -0.008342 | 63.588 | 63.7756 | 4.1885 | -59.2804 | 63.7344 | -59.2072 | -59.2987 | -58.8226 | 2.4353 | -59.3536 | 63.7344 | 63.6703 | -59.3308 | -59.3948 | -0.054931 | -0.14648 | 0.041199 | 122.9279 | -0.12817 | 0.01831 | -0.10529 | -0.17853 | -0.24261 | 0.041199 | 0.32959 | -0.20142 | 0.041198 | -0.022888 | 122.8867 | 122.7402 | 63.3408 | -122.9919 | 122.8867 | 122.8226 | 61.5875 | -123.0881
1383.0156 | 123.0469 | -59.1705 | 63.6978 | -0.15274 | 0.01279 | 0.068678 | 0.072012 | 0.12864 | 0.0018457 | -0.0038731 | -0.14511 | -0.0052808 | 0.060633 | 0.060176 | 0.0048492 | -0.010905 | 63.5605 | 63.6795 | 4.5273 | -59.3445 | 63.7894 | -59.2072 | -59.3308 | -58.8638 | 2.3987 | -59.4131 | 63.7619 | 63.6795 | -59.3491 | -59.4177 | -0.036621 | -0.16022 | 0.091553 | 122.85 | -0.17395 | -0.013732 | -0.13733 | -0.17853 | -0.24719 | 0.064087 | 0.3067 | -0.24262 | 0.004578 | -0.018311 | 122.9599 | 122.731 | 63.6978 | -123.0286 | 122.9324 | 122.85 | 61.5692 | -123.1155
1384.0156 | 122.9965 | -59.1751 | 63.707 | -0.22141 | 0.0080899 | 0.067182 | 0.068381 | 0.12886 | -0.00071785 | -0.0043003 | -0.11459 | -0.006349 | 0.06106 | 0.060176 | 0.0031402 | -0.008342 | 63.5742 | 63.7482 | 4.4083 | -59.3216 | 63.7802 | -59.2209 | -59.3033 | -58.8455 | 2.1881 | -59.4223 | 63.7665 | 63.6749 | -59.3445 | -59.4269 | -0.045776 | -0.12817 | 0.073242 | 122.9233 | -0.14648 | -0.01831 | -0.13275 | -0.16937 | -0.25177 | 0.059509 | 0.32959 | -0.24719 | 0.004578 | -0.032043 | 122.9553 | 122.7493 | 63.5834 | -123.0103 | 122.9416 | 122.85 | 61.3632 | -123.1338
1385.0156 | 122.9965 | -59.2072 | 63.7115 | -0.23666 | 0.011935 | 0.069105 | 0.073508 | 0.13142 | -0.0024269 | -0.0040867 | -0.13748 | -0.0078442 | 0.063623 | 0.057612 | 0.0016448 | -0.0059922 | 63.5193 | 63.6887 | 4.1885 | -59.3628 | 63.8031 | -59.2667 | -59.3491 | -58.9142 | 2.0737 | -59.3857 | 63.7665 | 63.6795 | -59.3674 | -59.4269 | -0.05951 | -0.14191 | 0.091553 | 122.8958 | -0.15564 | -0.013733 | -0.19226 | -0.16022 | -0.21973 | 0.054931 | 0.29297 | -0.17853 | 0.041199 | -0.032044 | 123.0103 | 122.7264 | 63.3957 | -123.0606 | 122.9736 | 122.8867 | 61.2808 | -123.1384
1386.0156 | 123.0515 | -59.1476 | 63.7207 | -0.23666 | 0.0089443 | 0.070387 | 0.068808 | 0.12864 | -0.0037085 | -0.0062229 | -0.091705 | -0.0089124 | 0.061273 | 0.058253 | 0.0024994 | -0.0070602 | 63.588 | 63.8168 | 4.4037 | -59.2941 | 63.7573 | -59.198 | -59.3033 | -58.8181 | 2.0187 | -59.3719 | 63.7527 | 63.6703 | -59.2941 | -59.3811 | -0.050354 | -0.15564 | 0.036621 | 122.9645 | -0.14648 | 0.009156 | -0.13275 | -0.14648 | -0.23346 | 0.032044 | 0.32959 | -0.2243 | 0.009156 | -0.050354 | 122.905 | 122.7356 | 63.5513 | -123.024 | 122.9004 | 122.818 | 61.1664 | -123.1018
1387.0156 | 123.0011 | -59.1934 | 63.7253 | -0.19852 | 0.011081 | 0.069105 | 0.073721 | 0.12971 | 0.0016321 | -0.0043003 | -0.21378 | -0.005708 | 0.063196 | 0.058894 | 0.002713 | -0.0070602 | 63.5422 | 63.7115 | 4.0283 | -59.3491 | 63.8214 | -59.23 | -59.3262 | -58.8684 | 1.6525 | -59.436 | 63.7802 | 63.6887 | -59.3399 | -59.404 | -0.036622 | -0.13275 | 0.09613 | 122.905 | -0.15564 | -0.022888 | -0.18311 | -0.14648 | -0.21057 | 0.054931 | 0.32501 | -0.24261 | -0.032043 | -0.036621 | 123.0148 | 122.7356 | 63.2217 | -123.0515 | 122.9736 | 122.8821 | 60.8459 | -123.1293
1388.0156 | 123.056 | -59.1339 | 63.7344 | -0.17563 | 0.0070217 | 0.069532 | 0.069235 | 0.12864 | -0.0041357 | -0.0049411 | -0.13748 | -0.009126 | 0.060846 | 0.05868 | 0.0031402 | -0.0085556 | 63.6246 | 63.8351 | 4.2755 | -59.2529 | 63.7482 | -59.1888 | -59.2621 | -58.7814 | 1.5656 | -59.3308 | 63.7527 | 63.6795 | -59.2941 | -59.3674 | -0.054932 | -0.12817 | 0.013733 | 122.9691 | -0.11902 | 0.009155 | -0.10986 | -0.16022 | -0.23346 | 0.018311 | 0.35248 | -0.19684 | 0.036621 | -0.054932 | 122.8821 | 122.7585 | 63.4094 | -122.9965 | 122.8867 | 122.8134 | 60.6995 | -123.1018
1389.0156 | 123.0057 | -59.1614 | 63.7299 | -0.25192 | 0.012576 | 0.068464 | 0.071799 | 0.12993 | -0.0022131 | -0.0062229 | -0.13748 | -0.0059216 | 0.062128 | 0.059107 | 0.0052764 | -0.0072738 | 63.5605 | 63.9359 | 4.4449 | -59.3765 | 63.858 | -59.1934 | -59.2575 | -58.8135 | 1.5701 | -59.3948 | 63.8214 | 63.7115 | -59.3216 | -59.3628 | -0.032043 | -0.09613 | 0.12817 | 123.0972 | -0.21515 | -0.11902 | -0.16937 | -0.16022 | -0.20142 | 0.091553 | 0.3479 | -0.23346 | -0.032043 | -0.01831 | 123.0194 | 122.7219 | 63.6063 | -122.9874 | 122.9828 | 122.8729 | 60.7315 | -123.0927
1390.0156 | 122.9874 | -59.1293 | 63.7527 | -0.20615 | 0.0072355 | 0.067823 | 0.072012 | 0.13078 | -0.0041357 | -0.0047275 | -0.168 | -0.0067762 | 0.062128 | 0.059107 | 0.0033538 | -0.0089828 | 63.6063 | 63.8168 | 4.5593 | -59.2712 | 63.7665 | -59.1705 | -59.2392 | -58.8181 | 1.7578 | -59.3353 | 63.7802 | 63.6978 | -59.2987 | -59.3536 | -0.041199 | -0.10986 | 0.013732 | 122.9462 | -0.14191 | -0.032043 | -0.14648 | -0.16937 | -0.2243 | 0.027465 | 0.31128 | -0.20599 | 0.018311 | -0.054932 | 122.8958 | 122.7356 | 63.6887 | -122.9919 | 122.9095 | 122.8271 | 60.8871 | -123.1064
1391.0156 | 123.024 | -59.1385 | 63.7207 | -0.20615 | 0.012362 | 0.069105 | 0.073081 | 0.13121 | -7.6852e-05 | -0.0034457 | -0.12222 | -0.0050672 | 0.06341 | 0.061671 | 0.0042084 | -0.0098374 | 63.6108 | 63.739 | 4.2755 | -59.2941 | 63.7848 | -59.2209 | -59.2896 | -58.7906 | 2.1515 | -59.3948 | 63.7802 | 63.6703 | -59.3033 | -59.3857 | -0.082397 | -0.15106 | 0.064087 | 122.8775 | -0.15564 | -0.004577 | -0.10986 | -0.16479 | -0.24719 | 0.059509 | 0.3479 | -0.25635 | -0.009155 | -0.050354 | 122.9233 | 122.7493 | 63.414 | -123.0103 | 122.9187 | 122.8088 | 61.29 | -123.1064
1392.0156 | 123.1201 | -59.1064 | 63.7207 | 2.7922 | 0.0093717 | 0.071027 | 0.072226 | 0.13185 | -0.0026405 | -0.0053683 | -0.091705 | -0.0084852 | 0.061701 | 0.059107 | 0.002713 | -0.0072738 | 63.6978 | 63.826 | 4.3762 | -59.23 | 63.7482 | -59.1614 | -59.2392 | -58.7265 | 2.1423 | -59.2712 | 63.7436 | 63.6749 | -59.2941 | -59.3353 | -0.054932 | -0.13275 | 0.027466 | 122.9324 | -0.1236 | 0.009155 | -0.022888 | -0.18768 | -0.22888 | 0.022888 | 0.37994 | -0.16479 | 0.064087 | -0.045776 | 122.8546 | 122.8043 | 63.4827 | -122.9599 | 122.85 | 122.7814 | 61.2488 | -123.056
1393.0156 | 123.0057 | -59.1431 | 63.7573 | -0.25955 | 0.0095853 | 0.06825 | 0.071799 | 0.13121 | -0.00093145 | -0.0040867 | -0.053558 | -0.0054944 | 0.063837 | 0.058253 | 0.0029266 | -0.0089828 | 63.5513 | 63.8031 | 4.2068 | -59.3033 | 63.7894 | -59.1843 | -59.2712 | -58.8089 | 2.1469 | -59.3903 | 63.8031 | 63.707 | -59.3216 | -59.3674 | -0.041199 | -0.12817 | 0.032044 | 122.9462 | -0.16022 | -0.032044 | -0.20599 | -0.17853 | -0.22431 | 0.045777 | 0.33417 | -0.24719 | -0.022888 | -0.050354 | 122.9324 | 122.6944 | 63.3499 | -123.0286 | 122.9462 | 122.85 | 61.29 | -123.1247
1394.0156 | 123.1064 | -59.1522 | 63.6795 | -0.21378 | 0.0044583 | 0.070173 | 0.068808 | 0.12928 | -0.0028541 | -0.0057957 | -0.13748 | -0.0089124 | 0.060846 | 0.059535 | 0.0016448 | -0.0081284 | 63.5971 | 63.7985 | 4.335 | -59.2941 | 63.7253 | -59.2163 | -59.3216 | -58.8043 | 2.4353 | -59.3399 | 63.7115 | 63.6337 | -59.3216 | -59.3857 | -0.064087 | -0.16937 | 0.045777 | 122.9507 | -0.14191 | 0.027466 | -0.082397 | -0.16937 | -0.23346 | 0.032044 | 0.3479 | -0.18768 | 0.045776 | -0.045776 | 122.8775 | 122.7493 | 63.4872 | -123.0011 | 122.8638 | 122.7859 | 61.5875 | -123.0652
1395.0156 | 122.9691 | -59.1522 | 63.7299 | -0.26718 | 0.011081 | 0.068037 | 0.069022 | 0.13185 | 0.0020593 | -0.0053683 | 0.09903 | -0.0076306 | 0.064264 | 0.059748 | 0.0018584 | -0.0072738 | 63.5605 | 63.7161 | 4.5136 | -59.1156 | 63.8672 | -59.1888 | -59.2575 | -58.8455 | 2.0599 | -59.3948 | 63.7985 | 63.6887 | -59.3399 | -59.3857 | -0.036621 | -0.10528 | 0.13733 | 122.8683 | 0.036621 | 0.14191 | -0.16937 | -0.18768 | -0.23346 | 0.068665 | 0.3067 | -0.24261 | -0.009155 | -0.041198 | 123.0194 | 122.7127 | 63.6658 | -122.9874 | 122.9507 | 122.8409 | 61.2122 | -123.1155
1396.0156 | 123.0789 | -59.1431 | 63.7024 | -0.18326 | 0.0048855 | 0.069319 | 0.070944 | 0.12672 | -0.0041357 | -0.0040867 | -0.091705 | -0.0078442 | 0.062769 | 0.058467 | 0.0018584 | -0.0087692 | 63.6246 | 63.8397 | 4.39 | -59.2804 | 63.7436 | -59.2163 | -59.2667 | -58.754 | 1.9043 | -59.3079 | 63.7115 | 63.6383 | -59.3124 | -59.3857 | -0.073243 | -0.1236 | 0.041198 | 122.9828 | -0.13733 | -0.013733 | -0.07782 | -0.16937 | -0.24262 | 0.009155 | 0.3891 | -0.1648 | 0.07782 | -0.064087 | 122.8867 | 122.7676 | 63.533 | -122.9691 | 122.8546 | 122.7814 | 61.0474 | -123.0881
1397.0156 | 123.0377 | -59.2438 | 63.6429 | -0.16037 | 0.013431 | 0.065687 | 0.070944 | 0.13185 | 0.0024865 | -0.0023777 | -0.168 | -0.0059216 | 0.064051 | 0.058894 | 0.0042084 | -0.0098374 | 63.5193 | 63.6703 | 4.454 | -59.3811 | 63.7482 | -59.2896 | -59.3765 | -58.8684 | 2.0325 | -59.4681 | 63.7024 | 63.6108 | -59.3903 | -59.4681 | -0.045777 | -0.13275 | 0.10529 | 122.9141 | -0.13733 | -0.004578 | -0.1236 | -0.14648 | -0.22431 | 0.05951 | 0.37537 | -0.22431 | 0 | -0.032043 | 122.9919 | 122.7631 | 63.6978 | -123.0194 | 122.9462 | 122.8546 | 61.2762 | -123.111
1398.0156 | 123.0927 | -59.2575 | 63.5376 | -0.14511 | 0.0057401 | 0.070173 | 0.070517 | 0.12886 | -0.0039221 | -0.0057957 | -0.20615 | -0.0078442 | 0.06341 | 0.057826 | 0.0024994 | -0.0081284 | 63.5971 | 63.6154 | 4.3854 | -59.4223 | 63.5834 | -59.3262 | -59.4177 | -58.8547 | 1.8173 | -59.4452 | 63.5696 | 63.5147 | -59.4269 | -59.4955 | -0.068665 | -0.16022 | 0.045776 | 122.8729 | -0.1648 | -0.004577 | 0.059509 | -0.16937 | -0.23804 | 0.032043 | 0.40283 | -0.18768 | 0.050354 | -0.022889 | 122.8409 | 122.8546 | 63.6429 | -122.9553 | 122.8271 | 122.7722 | 61.0748 | -123.0331
1399.0156 | 122.9919 | -59.285 | 63.5742 | -1.259 | 0.010867 | 0.066755 | 0.072867 | 0.13142 | 0.00013675 | -0.0030185 | -0.16037 | -0.0076306 | 0.067682 | 0.060176 | 0.0039948 | -0.0087692 | 63.3957 | 63.6017 | 4.1656 | -59.4681 | 63.6703 | -59.3582 | -59.4452 | -58.9279 | 1.2589 | -59.5184 | 63.6612 | 63.5651 | -59.4498 | -59.5093 | -0.073242 | -0.16022 | 0.09613 | 122.8867 | -0.18311 | -0.022889 | -0.17853 | -0.16479 | -0.2243 | 0.086975 | 0.35706 | -0.23346 | -0.009156 | -0.009156 | 122.9553 | 122.6807 | 63.4506 | -123.0194 | 122.9462 | 122.85 | 60.5438 | -123.0835
1400.0156 | 123.0652 | -59.23 | 63.5651 | -0.18326 | 0.0068081 | 0.068891 | 0.069449 | 0.13035 | -0.0032813 | -0.0038731 | -0.15274 | -0.0089124 | 0.061487 | 0.060603 | 0.0037812 | -0.0085556 | 63.501 | 63.7344 | 4.3533 | -59.3765 | 63.6475 | -59.3079 | -59.3674 | -58.8593 | 1.2131 | -59.436 | 63.6246 | 63.533 | -59.4406 | -59.491 | -0.077819 | -0.13733 | 0.082398 | 122.9645 | -0.14648 | -0.009155 | -0.064086 | -0.21057 | -0.26093 | 0.05951 | 0.37079 | -0.20599 | 0.054932 | -0.032043 | 122.8775 | 122.731 | 63.5834 | -122.9324 | 122.8546 | 122.7631 | 60.4431 | -123.056
1401.0156 | 123.0103 | -59.2941 | 63.6017 | -0.20615 | 0.010867 | 0.069319 | 0.073294 | 0.12907 | 0.0022729 | -0.0045139 | -0.16037 | -0.0065626 | 0.064905 | 0.060389 | 0.0029266 | -0.0098374 | 63.4415 | 63.5925 | 4.184 | -59.436 | 63.6887 | -59.3628 | -59.4086 | -58.9142 | 1.1169 | -59.5276 | 63.6566 | 63.5513 | -59.4406 | -59.5322 | -0.068665 | -0.11444 | 0.086975 | 122.8867 | -0.14191 | -0.027466 | -0.16022 | -0.14648 | -0.23804 | 0.054931 | 0.37994 | -0.23346 | 0.004578 | -0.050354 | 122.9828 | 122.7356 | 63.4781 | -123.0103 | 122.9507 | 122.8455 | 60.4111 | -123.1339
1402.0156 | 123.0469 | -59.1843 | 63.5971 | -0.33585 | 0.0061673 | 0.069746 | 0.068808 | 0.1295 | -0.0049903 | -0.0049411 | -0.068817 | -0.0084852 | 0.061914 | 0.05868 | 0.001004 | -0.0079148 | 63.5468 | 63.7665 | 4.1519 | -59.3628 | 63.6337 | -59.285 | -59.3628 | -58.8043 | 1.2634 | -59.3994 | 63.652 | 63.5376 | -59.3994 | -59.4498 | -0.10071 | -0.17853 | 0.036621 | 122.9507 | -0.17853 | 0 | -0.050354 | -0.21515 | -0.2655 | 0.054932 | 0.37994 | -0.21515 | 0.050354 | -0.059509 | 122.818 | 122.731 | 63.3362 | -122.9599 | 122.8363 | 122.7219 | 60.4477 | -123.0469
1403.0156 | 122.9507 | -59.23 | 63.6429 | -0.168 | 0.0080899 | 0.070387 | 0.070303 | 0.12993 | 0.00056395 | -0.0079319 | -0.14511 | -0.0072034 | 0.063623 | 0.05868 | 0.0024994 | -0.0085556 | 63.4644 | 63.62 | 4.1748 | -59.4315 | 63.7161 | -59.3124 | -59.3811 | -58.8913 | 1.1353 | -59.5139 | 63.6978 | 63.5925 | -59.4223 | -59.4727 | -0.082397 | -0.15106 | 0.073242 | 122.85 | -0.20142 | -0.050354 | -0.17853 | -0.19226 | -0.24261 | 0.054932 | 0.33875 | -0.28381 | -0.041199 | -0.050354 | 122.9462 | 122.6944 | 63.4048 | -123.024 | 122.9279 | 122.8226 | 60.3653 | -123.1155
1404.0156 | 123.0606 | -59.198 | 63.6658 | -0.20615 | 0.0087307 | 0.068678 | 0.069449 | 0.13078 | -0.0017859 | -0.0064365 | -0.12222 | -0.0086988 | 0.061914 | 0.060816 | 0.0022858 | -0.008342 | 63.5605 | 63.7802 | 3.8498 | -59.3308 | 63.7115 | -59.2667 | -59.3491 | -58.7952 | 1.0941 | -59.404 | 63.6978 | 63.5925 | -59.3674 | -59.4315 | -0.068665 | -0.15106 | 0.045777 | 122.9782 | -0.13275 | 0.01831 | -0.10529 | -0.16937 | -0.23346 | 0.032044 | 0.40283 | -0.20599 | 0.027466 | -0.073242 | 122.9095 | 122.7585 | 63.0478 | -123.0148 | 122.8958 | 122.7905 | 60.2921 | -123.0972
1405.0156 | 123.024 | -59.23 | 63.6566 | -0.25192 | 0.0091581 | 0.071027 | 0.070944 | 0.13014 | -0.0011451 | -0.0070773 | -0.30533 | -0.0076306 | 0.064905 | 0.059535 | 0.0037812 | -0.008342 | 63.7482 | 63.5284 | 3.9276 | -59.5047 | 63.7253 | -59.2941 | -59.3582 | -58.8501 | 0.9201 | -59.4864 | 63.7253 | 63.6063 | -59.3903 | -59.4818 | -0.064086 | -0.12817 | 0.068665 | 122.7585 | -0.27466 | -0.14648 | 0.091553 | -0.16022 | -0.25177 | 0.068665 | 0.37994 | -0.25635 | -0.004577 | -0.050354 | 122.9553 | 122.9782 | 63.1577 | -123.0148 | 122.9553 | 122.8363 | 60.1501 | -123.1384
1406.0156 | 123.1201 | -59.1843 | 63.62 | -0.168 | 0.0080899 | 0.069746 | 0.069663 | 0.13099 | -0.0043495 | -0.0049411 | -0.076446 | -0.0065626 | 0.061914 | 0.060389 | 0.0024994 | -0.0081284 | 63.5513 | 63.7573 | 4.4128 | -59.3399 | 63.6703 | -59.2529 | -59.3445 | -58.786 | 1.1581 | -59.3857 | 63.6612 | 63.5742 | -59.3674 | -59.4452 | -0.068665 | -0.16022 | 0.050354 | 122.9416 | -0.15564 | 0.004577 | -0.068664 | -0.18311 | -0.26092 | 0.041199 | 0.39825 | -0.20142 | 0.059509 | -0.045776 | 122.8546 | 122.7356 | 63.5971 | -122.9645 | 122.8455 | 122.7585 | 60.3424 | -123.0652
1407.0156 | 122.905 | -59.2438 | 63.6658 | -0.46555 | 0.0068081 | 0.068464 | 0.070517 | 0.1295 | 0.00077755 | -0.0049411 | -0.16037 | -0.0076306 | 0.060633 | 0.058253 | 0.0035674 | -0.0094102 | 63.4689 | 63.6429 | 4.5181 | -59.4269 | 63.6978 | -59.2896 | -59.3857 | -58.8776 | 1.4969 | -59.5001 | 63.7115 | 63.588 | -59.4177 | -59.4269 | -0.045777 | -0.14191 | 0.032044 | 122.8867 | -0.18311 | -0.041199 | -0.19684 | -0.17395 | -0.18311 | 0.045777 | 0.36621 | -0.25635 | -0.073242 | -0.077819 | 122.9416 | 122.7127 | 63.7619 | -123.0515 | 122.9553 | 122.8317 | 60.7407 | -123.0927
1408.0156 | 123.0881 | -59.2163 | 63.6154 | -0.21378 | 0.0085171 | 0.06761 | 0.068167 | 0.12736 | -0.0024269 | -0.0057957 | -0.14511 | -0.007417 | 0.063837 | 0.059962 | 0.0029266 | -0.0087692 | 63.533 | 63.7482 | 4.3625 | -59.3399 | 63.6749 | -59.2941 | -59.3445 | -58.8089 | 1.5518 | -59.4223 | 63.6749 | 63.5468 | -59.3994 | -59.4727 | -0.077819 | -0.12817 | 0.05951 | 122.9645 | -0.1236 | 0.004577 | -0.082397 | -0.1831 | -0.25635 | 0.05951 | 0.40741 | -0.20599 | 0.050354 | -0.068664 | 122.8912 | 122.7493 | 63.5788 | -122.9599 | 122.8912 | 122.7631 | 60.7681 | -123.0881
1409.0156 | 122.9874 | -59.2346 | 63.6383 | -0.21378 | 0.0055265 | 0.068678 | 0.071158 | 0.12715 | 0.00035035 | -0.0030185 | -0.20615 | -0.006349 | 0.062555 | 0.05868 | 0.0031402 | -0.008342 | 63.4964 | 63.7024 | 4.1702 | -59.3903 | 63.6795 | -59.2987 | -59.3628 | -58.8638 | 1.6342 | -59.4452 | 63.7024 | 63.6017 | -59.4269 | -59.4727 | -0.064087 | -0.12817 | 0.041198 | 122.937 | -0.15564 | -0.027466 | -0.14191 | -0.19226 | -0.23804 | 0.064087 | 0.37079 | -0.21057 | 0.027466 | -0.036621 | 122.9141 | 122.731 | 63.4048 | -123.0011 | 122.937 | 122.8363 | 60.8688 | -123.111
1410.0156 | 123.1293 | -59.23 | 63.6154 | -0.11459 | 0.0053129 | 0.068464 | 0.07009 | 0.12993 | -0.0049903 | -0.0045139 | -0.045929 | -0.0078442 | 0.061701 | 0.056544 | 0.0020722 | -0.008342 | 63.5147 | 63.7665 | 4.0924 | -59.3353 | 63.6566 | -59.3079 | -59.3628 | -58.754 | 2.0142 | -59.3811 | 63.62 | 63.5284 | -59.4131 | -59.4818 | -0.077819 | -0.13275 | 0.041199 | 122.9965 | -0.10529 | 0.027466 | -0.10071 | -0.18311 | -0.25177 | 0.004578 | 0.47607 | -0.15106 | 0.10071 | -0.086975 | 122.8867 | 122.7448 | 63.3224 | -122.9782 | 122.85 | 122.7585 | 61.2442 | -123.0972
1411.0156 | 123.0194 | -59.285 | 63.6154 | -0.25192 | 0.0076627 | 0.070387 | 0.070731 | 0.13121 | -0.00071785 | -0.0047275 | -0.168 | -0.0065626 | 0.064478 | 0.057826 | 0.0035674 | -0.01176 | 63.4598 | 63.6566 | 4.0741 | -59.4223 | 63.6887 | -59.317 | -59.404 | -58.873 | 2.1194 | -59.5367 | 63.6612 | 63.5605 | -59.4452 | -59.5139 | -0.032044 | -0.11902 | 0.073243 | 122.9416 | -0.13733 | -0.01831 | -0.15564 | -0.16022 | -0.22888 | 0.045777 | 0.41199 | -0.25177 | -0.022888 | -0.054931 | 122.9736 | 122.7448 | 63.3591 | -123.0194 | 122.9462 | 122.8455 | 61.4044 | -123.1293
1412.0156 | 123.1018 | -59.2621 | 63.5651 | -0.03067 | 0.0040311 | 0.069746 | 0.069449 | 0.12779 | -0.0054175 | -0.0055821 | 0.083771 | -0.0095532 | 0.062128 | 0.057826 | 0.0016448 | -0.0077012 | 63.4735 | 63.6978 | 3.6667 | -59.3903 | 63.6612 | -59.3399 | -59.404 | -58.8181 | 2.2156 | -59.4223 | 63.6108 | 63.5056 | -59.4223 | -59.5001 | -0.07782 | -0.14191 | 0.096131 | 122.9599 | -0.12817 | 0.013733 | -0.091552 | -0.16022 | -0.23804 | 0.045777 | 0.44403 | -0.16022 | 0.07782 | -0.059509 | 122.9233 | 122.7356 | 62.9288 | -122.9691 | 122.8729 | 122.7676 | 61.4777 | -123.0652
1413.0156 | 123.1064 | -59.2392 | 63.588 | -0.30533 | 0.0027493 | 0.06761 | 0.062827 | 0.13142 | -0.0052039 | -0.0051547 | -0.023041 | -0.0082716 | 0.061914 | 0.058467 | 0.0033538 | -0.0091966 | 63.5788 | 63.6703 | 3.6209 | -59.3308 | 63.6429 | -59.2896 | -59.3674 | -58.8135 | 2.0004 | -59.3948 | 63.6475 | 63.5239 | -59.3857 | -59.4727 | -0.050354 | -0.12817 | 0.054931 | 122.9095 | -0.091553 | 0.036621 | -0.009156 | -0.14648 | -0.23346 | 0.059509 | 0.42572 | -0.15564 | 0.07782 | -0.064087 | 122.8821 | 122.818 | 62.8601 | -122.9553 | 122.8867 | 122.7631 | 61.2396 | -123.0606
1414.0156 | 123.1201 | -59.166 | 63.5971 | -0.10696 | 0.0078763 | 0.069532 | 0.068808 | 0.12886 | -0.0022131 | -0.0064365 | -0.015411 | -0.0099806 | 0.061273 | 0.059535 | 0.002713 | -0.0085556 | 63.5834 | 63.7711 | 3.1906 | -59.3353 | 63.6887 | -59.2529 | -59.3445 | -58.7311 | 1.561 | -59.3491 | 63.6932 | 63.5696 | -59.3399 | -59.4223 | -0.086975 | -0.17853 | 0.091553 | 122.937 | -0.16937 | 0.009155 | -0.013733 | -0.17395 | -0.25635 | 0.09613 | 0.43488 | -0.18311 | 0.073242 | -0.027466 | 122.8546 | 122.7493 | 62.3566 | -122.9416 | 122.8592 | 122.7356 | 60.7269 | -123.0194
1415.0156 | 123.1155 | -59.1339 | 63.7115 | -0.62576 | 0.0063809 | 0.069319 | 0.069876 | 0.12843 | -0.00093145 | -0.0062229 | -0.11459 | -0.0095532 | 0.063196 | 0.056117 | 0.0046356 | -0.0089828 | 63.6383 | 63.8306 | 2.9022 | -59.2621 | 63.7482 | -59.1843 | -59.2667 | -58.6899 | 0.83771 | -59.3033 | 63.7344 | 63.6337 | -59.2987 | -59.3674 | -0.050354 | -0.13275 | 0.036621 | 122.9645 | -0.12817 | 0.004578 | -0.073242 | -0.1648 | -0.23346 | 0.022888 | 0.44403 | -0.16937 | 0.064087 | -0.07782 | 122.8821 | 122.7722 | 62.0361 | -122.9782 | 122.8683 | 122.7676 | 59.9716 | -123.0789
1416.0156 | 123.1018 | -59.1293 | 63.6749 | 0.015106 | 0.00082671 | 0.066328 | 0.070517 | 0.1295 | -0.0017859 | -0.0053683 | 0.022736 | -0.0072034 | 0.06106 | 0.059107 | 0.0024994 | -0.0081284 | 63.6017 | 63.7939 | 2.4124 | -59.2804 | 63.7573 | -59.1934 | -59.2758 | -58.7173 | 0.50812 | -59.2941 | 63.7299 | 63.6383 | -59.2941 | -59.3582 | -0.064087 | -0.14648 | 0.082397 | 122.9233 | -0.15106 | -0.004578 | -0.073242 | -0.16479 | -0.22888 | 0.054931 | 0.41199 | -0.16479 | 0.064087 | -0.036621 | 122.8867 | 122.731 | 61.5417 | -122.9507 | 122.8592 | 122.7676 | 59.6375 | -123.0331
1417.0156 | 123.1338 | -59.1064 | 63.6887 | -0.12985 | 0.0050991 | 0.069959 | 0.069449 | 0.13014 | -0.0032813 | -0.0075047 | -0.061188 | -0.0086988 | 0.061273 | 0.05868 | 0.0014312 | -0.013255 | 63.7024 | 63.9359 | 2.2934 | -59.2163 | 63.7848 | -59.1751 | -59.2209 | -58.493 | 1.4191 | -59.5139 | 63.7711 | 63.6108 | -59.2621 | -59.3399 | -0.068665 | -0.11444 | 0.09613 | 123.0423 | -0.10986 | 0.004577 | 0.013733 | -0.15564 | -0.23346 | 0.082397 | 0.6134 | -0.40741 | -0.17395 | -0.07782 | 122.8912 | 122.8088 | 61.3998 | -122.9095 | 122.8775 | 122.7173 | 60.5255 | -123.0286
1418.0156 | 123.0789 | -59.0836 | 63.7161 | 0.015106 | 0.0068081 | 0.069959 | 0.07009 | 0.12971 | -0.00093145 | -0.0047275 | -0.00015237 | -0.0084852 | 0.061914 | 0.057826 | 0.0039948 | -0.0087692 | 63.6612 | 63.826 | 2.0416 | -59.2484 | 63.8077 | -59.1568 | -59.2346 | -58.667 | 1.3138 | -59.2758 | 63.7802 | 63.6749 | -59.2667 | -59.3445 | -0.073242 | -0.15106 | 0.091553 | 122.9095 | -0.16479 | -0.013733 | -0.054931 | -0.18311 | -0.26093 | 0.064087 | 0.41656 | -0.19226 | 0.068664 | -0.041198 | 122.8912 | 122.7448 | 61.1252 | -122.9507 | 122.8638 | 122.7585 | 60.3973 | -123.0606
1419.0156 | 123.1018 | -59.0744 | 63.7115 | -0.10696 | 0.0063809 | 0.068891 | 0.069449 | 0.12736 | -0.0013587 | -0.0055821 | -0.0077819 | -0.007417 | 0.06106 | 0.059535 | 0.0037812 | -0.0096238 | 63.6978 | 63.8809 | 2.092 | -59.2163 | 63.8077 | -59.1385 | -59.2026 | -58.6349 | 1.6846 | -59.23 | 63.7848 | 63.6887 | -59.2667 | -59.317 | -0.064087 | -0.12817 | 0.09613 | 122.9553 | -0.14191 | -0.013733 | -0.013733 | -0.19226 | -0.24262 | 0.073242 | 0.43945 | -0.15564 | 0.086975 | -0.022888 | 122.8821 | 122.7722 | 61.1664 | -122.9141 | 122.8592 | 122.7631 | 60.759 | -123.0286
1420.0156 | 123.0927 | -59.079 | 63.7482 | 0.12192 | 0.0048855 | 0.069105 | 0.067313 | 0.13035 | 0.0016321 | -0.0045139 | 0.09903 | -0.009126 | 0.062769 | 0.056758 | 0.0042084 | -0.010478 | 63.6566 | 63.7894 | 2.1332 | -59.2667 | 63.7848 | -59.1705 | -59.2346 | -58.6807 | 1.8219 | -59.2941 | 63.7756 | 63.6703 | -59.2484 | -59.3674 | -0.091553 | -0.15564 | 0.036621 | 122.8683 | -0.18768 | -0.032044 | -0.091553 | -0.16937 | -0.28839 | 0.027466 | 0.39825 | -0.21515 | 0.073243 | -0.07782 | 122.8638 | 122.7356 | 61.2122 | -122.9828 | 122.8546 | 122.7493 | 60.9009 | -123.1155
1421.0156 | 123.1338 | -59.0515 | 63.707 | -0.11459 | 0.0063809 | 0.069105 | 0.067313 | 0.12993 | -0.0022131 | -0.0055821 | -0.084076 | -0.0084852 | 0.06341 | 0.056544 | 0.0024994 | -0.0072738 | 63.7207 | 63.8855 | 2.2568 | -59.2346 | 63.8123 | -59.1568 | -59.2117 | -58.6029 | 2.1881 | -59.2392 | 63.8031 | 63.6612 | -59.2484 | -59.3033 | -0.10529 | -0.16022 | 0.10529 | 122.937 | -0.18311 | -0.022888 | 0.013733 | -0.19684 | -0.25177 | 0.096131 | 0.44861 | -0.18768 | 0.064087 | -0.045776 | 122.8638 | 122.7722 | 61.3083 | -122.9187 | 122.8546 | 122.7127 | 61.2396 | -123.0103
1422.0156 | 123.0927 | -59.0515 | 63.7527 | -0.068817 | 0.0042447 | 0.068037 | 0.068808 | 0.12672 | -7.6852e-05 | -0.0055821 | 0.068512 | -0.0072034 | 0.063196 | 0.059107 | 0.0042084 | -0.0074876 | 63.6749 | 63.8443 | 1.8723 | -59.23 | 63.8351 | -59.1339 | -59.1843 | -58.6304 | 1.6937 | -59.2712 | 63.7985 | 63.7253 | -59.2346 | -59.2804 | -0.082397 | -0.13275 | 0.082397 | 122.8958 | -0.17853 | -0.045777 | -0.07782 | -0.18311 | -0.22888 | 0.045776 | 0.42114 | -0.21973 | 0.009156 | -0.027466 | 122.8867 | 122.7264 | 60.9238 | -122.937 | 122.85 | 122.7768 | 60.7452 | -123.0331
1423.0156 | 123.1064 | -59.0515 | 63.7527 | -0.0383 | 0.0063809 | 0.068037 | 0.069235 | 0.12864 | -0.00050425 | -0.0045139 | 0.045624 | -0.0076306 | 0.060633 | 0.058039 | 0.0031402 | -0.0096238 | 63.7207 | 63.8901 | 2.1378 | -59.2026 | 63.8489 | -59.1293 | -59.1934 | -58.5983 | 1.5656 | -59.23 | 63.8123 | 63.7024 | -59.2117 | -59.2758 | -0.077819 | -0.14191 | 0.09613 | 122.9416 | -0.15106 | -0.009156 | -0.032044 | -0.16022 | -0.2243 | 0.059509 | 0.45319 | -0.17853 | 0.045776 | -0.050354 | 122.9004 | 122.7722 | 61.1893 | -122.9462 | 122.8638 | 122.7539 | 60.6171 | -123.0286
1424.0156 | 123.0515 | -59.0836 | 63.7756 | 0.037994 | 0.0074491 | 0.068037 | 0.070731 | 0.12971 | -0.0013587 | -0.0036595 | 0.060883 | -0.011476 | 0.060846 | 0.058894 | 0.0042084 | -0.0096238 | 63.6932 | 63.8306 | 2.4628 | -59.23 | 63.8489 | -59.1202 | -59.2026 | -58.6349 | 1.5106 | -59.2758 | 63.8306 | 63.6932 | -59.23 | -59.3216 | -0.036621 | -0.11902 | 0.073242 | 122.9141 | -0.14648 | -0.027466 | -0.082398 | -0.14648 | -0.23804 | 0.054931 | 0.44861 | -0.19226 | 0.045776 | -0.082398 | 122.9324 | 122.7768 | 61.5463 | -122.9782 | 122.9141 | 122.7768 | 60.5942 | -123.0972
1425.0156 | 123.1338 | -58.9966 | 63.7802 | -0.061188 | 0.0065945 | 0.070387 | 0.070944 | 0.13163 | -0.0019995 | -0.0043003 | 0.015106 | -0.0086988 | 0.05871 | 0.056971 | 0.0039948 | -0.0087692 | 63.7619 | 63.9038 | 2.6871 | -59.1705 | 63.8489 | -59.0973 | -59.1751 | -58.5434 | 1.5656 | -59.1843 | 63.8351 | 63.739 | -59.2072 | -59.2621 | -0.10071 | -0.17853 | 0.068665 | 122.9004 | -0.17395 | 0.004578 | -0.01831 | -0.21057 | -0.2655 | 0.054932 | 0.45319 | -0.18768 | 0.07782 | -0.041198 | 122.8455 | 122.7585 | 61.6837 | -122.9553 | 122.8317 | 122.7356 | 60.5621 | -123.0423
1426.0156 | 123.1155 | -58.992 | 63.7939 | 2.7617 | 0.0095853 | 0.069319 | 0.067954 | 0.12864 | 0.0016321 | -0.0028049 | -0.14511 | -0.0084852 | 0.062982 | 0.058253 | 0.0059174 | -0.010051 | 63.8306 | 63.9175 | 2.4948 | -59.1476 | 63.8809 | -59.0744 | -59.1751 | -58.5342 | 1.7258 | -59.198 | 63.858 | 63.739 | -59.2117 | -59.2575 | -0.082398 | -0.18311 | 0.086975 | 122.9095 | -0.15564 | 0.027466 | 0.036621 | -0.21973 | -0.2655 | 0.064087 | 0.45776 | -0.20599 | 0.059509 | -0.054931 | 122.8729 | 122.8226 | 61.4868 | -122.9691 | 122.85 | 122.731 | 60.7178 | -123.0515
1427.0156 | 123.0652 | -59.0652 | 63.7802 | 0.068512 | 0.0040311 | 0.068037 | 0.071799 | 0.1295 | -0.0017859 | -0.0038731 | 0.09903 | -0.0078442 | 0.060419 | 0.057398 | 0.0046356 | -0.0077012 | 63.7115 | 63.8443 | 2.3529 | -59.2117 | 63.8626 | -59.111 | -59.2209 | -58.6807 | 1.561 | -59.2712 | 63.8123 | 63.7299 | -59.2346 | -59.3079 | -0.045776 | -0.15564 | 0.082398 | 122.9095 | -0.14648 | 0.009155 | -0.068664 | -0.16937 | -0.24261 | 0.032044 | 0.38452 | -0.20599 | 0.036621 | -0.050354 | 122.9279 | 122.7768 | 61.4182 | -123.0011 | 122.8775 | 122.7951 | 60.6262 | -123.0881
1428.0156 | 123.0927 | -59.0515 | 63.7619 | 0.10666 | 0.010226 | 0.06825 | 0.070944 | 0.12907 | -7.6852e-05 | -0.0038731 | 0.15244 | -0.0052808 | 0.061487 | 0.058894 | 0.0046356 | -0.0089828 | 63.7161 | 63.8626 | 2.0096 | -59.2392 | 63.7894 | -59.1248 | -59.1843 | -58.6075 | 2.092 | -59.2667 | 63.8031 | 63.6703 | -59.2529 | -59.2987 | -0.073242 | -0.13275 | 0.027466 | 122.9141 | -0.18768 | -0.054932 | -0.045777 | -0.20142 | -0.24719 | 0.041199 | 0.44403 | -0.21515 | 0.032043 | -0.091553 | 122.8409 | 122.7676 | 61.0611 | -122.9462 | 122.8546 | 122.7219 | 61.1435 | -123.0606
1429.0156 | 123.0927 | -59.0195 | 63.7756 | 0.037994 | 0.0057401 | 0.069959 | 0.068167 | 0.13142 | -0.0024269 | -0.0060093 | 0.14481 | -0.0099806 | 0.062128 | 0.058253 | 0.0046356 | -0.008342 | 63.7711 | 63.7939 | 1.8723 | -59.198 | 63.8718 | -59.1339 | -59.1888 | -58.5983 | 1.9547 | -59.23 | 63.8443 | 63.7207 | -59.2026 | -59.2529 | -0.11444 | -0.16937 | 0.09613 | 122.8134 | -0.17853 | -0.009155 | -0.004578 | -0.18311 | -0.23346 | 0.068664 | 0.42114 | -0.21057 | 0.022888 | -0.054932 | 122.8912 | 122.7905 | 60.8917 | -122.9645 | 122.8638 | 122.7402 | 60.9741 | -123.0286
1430.0156 | 123.0881 | -59.0652 | 63.7161 | 0.27451 | 0.0097989 | 0.069746 | 0.069022 | 0.12971 | 0.0020593 | -0.0030185 | 0.16006 | -0.0093396 | 0.063196 | 0.060816 | 0.0037812 | -0.0085556 | 63.739 | 63.8718 | 1.9363 | -59.2117 | 63.8077 | -59.111 | -59.2072 | -58.5892 | 2.0279 | -59.2712 | 63.7894 | 63.6703 | -59.2621 | -59.3399 | -0.045776 | -0.14191 | 0.091553 | 122.937 | -0.14648 | -0.004578 | 0.022889 | -0.19684 | -0.27466 | 0.073243 | 0.47608 | -0.20599 | 0.068665 | -0.045776 | 122.8729 | 122.8043 | 61.0016 | -122.9233 | 122.8546 | 122.7356 | 61.0931 | -123.056
1431.0156 | 123.0835 | -59.0607 | 63.7482 | 0.0074768 | 0.0068081 | 0.070173 | 0.067099 | 0.13121 | 0.00035035 | -0.0038731 | 0.037995 | -0.0067762 | 0.061701 | 0.058253 | 0.004422 | -0.0085556 | 63.6841 | 63.8397 | 1.9821 | -59.2209 | 63.8443 | -59.1431 | -59.198 | -58.6075 | 2.4261 | -59.2575 | 63.7848 | 63.7161 | -59.2438 | -59.317 | -0.082397 | -0.13733 | 0.09613 | 122.9004 | -0.16022 | -0.022888 | -0.064087 | -0.18311 | -0.25635 | 0.036621 | 0.45319 | -0.19684 | 0.05951 | -0.032044 | 122.905 | 122.7448 | 61.0428 | -122.9462 | 122.8455 | 122.7768 | 61.4868 | -123.0652
1432.0156 | 123.0743 | -59.0744 | 63.707 | 0.16769 | 0.0091581 | 0.069746 | 0.071585 | 0.13035 | -0.00071785 | -0.0038731 | 0.19058 | -0.009126 | 0.061701 | 0.059321 | 0.0042084 | -0.008342 | 63.7115 | 63.8443 | 1.918 | -59.2072 | 63.7939 | -59.1293 | -59.2209 | -58.6212 | 2.3804 | -59.2987 | 63.7711 | 63.6887 | -59.2712 | -59.3079 | -0.054931 | -0.14648 | 0.086975 | 122.9187 | -0.13275 | 0.013733 | 0.004578 | -0.19684 | -0.23346 | 0.064087 | 0.45319 | -0.2243 | 0.009155 | -0.01831 | 122.8683 | 122.7859 | 60.9924 | -122.9279 | 122.8455 | 122.7631 | 61.4548 | -123.0148
1433.0156 | 123.056 | -59.0836 | 63.7573 | 0.083771 | 0.0070217 | 0.068464 | 0.069235 | 0.12758 | -0.0026405 | -0.0062229 | 0.11429 | -0.006349 | 0.063623 | 0.05868 | 0.0042084 | -0.0091966 | 63.6749 | 63.826 | 1.6342 | -59.2575 | 63.8123 | -59.1339 | -59.198 | -58.6258 | 1.9455 | -59.2712 | 63.7848 | 63.6978 | -59.2529 | -59.2987 | -0.050354 | -0.11444 | 0.054932 | 122.9095 | -0.17395 | -0.059509 | -0.082397 | -0.16937 | -0.21515 | 0.027466 | 0.45776 | -0.18768 | 0.027466 | -0.059509 | 122.8958 | 122.7585 | 60.7178 | -122.9553 | 122.8683 | 122.7814 | 61.0291 | -123.056
1434.0156 | 123.0972 | -59.0607 | 63.7207 | 0.20584 | 0.012362 | 0.068678 | 0.072012 | 0.13377 | 0.0027001 | -0.0028049 | 0.19058 | -0.006349 | 0.064264 | 0.058894 | 0.0039948 | -0.0091966 | 63.739 | 63.8626 | 1.6525 | -59.2072 | 63.8123 | -59.1339 | -59.2163 | -58.58 | 1.3138 | -59.4177 | 63.7665 | 63.6337 | -59.2758 | -59.3308 | -0.073242 | -0.15564 | 0.091553 | 122.9233 | -0.14648 | 0.009156 | 0.018311 | -0.21515 | -0.27008 | 0.045776 | 0.48065 | -0.35706 | -0.086975 | -0.086975 | 122.8729 | 122.7997 | 60.7132 | -122.937 | 122.8271 | 122.6944 | 60.3745 | -123.0515
1435.0156 | 123.0835 | -59.0286 | 63.7802 | 0.045624 | 0.0042447 | 0.069959 | 0.069235 | 0.12608 | -0.0030677 | -0.0049411 | 0.045624 | -0.0067762 | 0.060419 | 0.058253 | 0.002713 | -0.0077012 | 63.739 | 63.858 | 1.474 | -59.1934 | 63.8718 | -59.1156 | -59.166 | -58.5754 | 1.6205 | -59.1568 | 63.8672 | 63.7711 | -59.198 | -59.2712 | -0.086976 | -0.13733 | 0.091553 | 122.8867 | -0.1648 | -0.027465 | -0.041198 | -0.16937 | -0.24262 | 0.086975 | 0.45319 | -0.12817 | 0.11444 | -0.009155 | 122.9004 | 122.7676 | 60.5026 | -122.9462 | 122.8958 | 122.7997 | 60.6491 | -123.0515
1436.0156 | 123.0972 | -59.0378 | 63.7711 | 0.18295 | 0.010867 | 0.068678 | 0.070944 | 0.12993 | 0.0014185 | -0.0055821 | 0.09903 | -0.006349 | 0.061914 | 0.058467 | 0.0063446 | -0.010051 | 63.9175 | 63.8947 | 1.5289 | -59.1431 | 63.8351 | -59.0836 | -59.1751 | -58.5342 | 1.7029 | -59.1934 | 63.8489 | 63.7161 | -59.2163 | -59.2575 | -0.045776 | -0.13733 | 0.064087 | 122.9324 | -0.10528 | 0.032044 | 0.14648 | -0.17853 | -0.21973 | 0.07782 | 0.50354 | -0.15564 | 0.064087 | -0.054932 | 122.8729 | 122.9553 | 60.5667 | -122.9462 | 122.8867 | 122.7539 | 60.7407 | -123.0286
1437.0156 | 123.0972 | -59.0424 | 63.7894 | 0.14481 | 0.0095853 | 0.066969 | 0.06539 | 0.1295 | -0.0013587 | -0.0023777 | 0.19821 | -0.0095532 | 0.061701 | 0.057398 | 0.0046356 | -0.0085556 | 63.7299 | 63.8535 | 1.5976 | -59.2209 | 63.8672 | -59.0836 | -59.1568 | -58.6121 | 1.6846 | -59.2438 | 63.8168 | 63.7207 | -59.2255 | -59.285 | -0.041199 | -0.11444 | 0.077819 | 122.8958 | -0.17853 | -0.064087 | -0.05951 | -0.18311 | -0.24262 | 0.027465 | 0.4303 | -0.20142 | 0.041199 | -0.068665 | 122.9095 | 122.7722 | 60.64 | -122.9462 | 122.8592 | 122.7631 | 60.7269 | -123.0743
1438.0156 | 123.0927 | -59.0332 | 63.7344 | 0.28213 | 0.010867 | 0.06761 | 0.070303 | 0.1295 | 0.00099115 | -0.0019505 | 0.14481 | -0.0054944 | 0.061487 | 0.059321 | 0.004422 | -0.008342 | 63.7665 | 63.8901 | 1.5564 | -59.198 | 63.8123 | -59.0927 | -59.1751 | -58.5663 | 1.973 | -59.2392 | 63.826 | 63.7253 | -59.2163 | -59.2804 | -0.059509 | -0.14191 | 0.07782 | 122.9233 | -0.16479 | -0.022888 | 0.032043 | -0.18311 | -0.24719 | 0.091553 | 0.46692 | -0.20599 | 0.041199 | -0.009155 | 122.8455 | 122.7997 | 60.5896 | -122.9095 | 122.8592 | 122.7585 | 61.0062 | -123.0148
1439.0156 | 123.1338 | -59.0286 | 63.7802 | 0.068512 | 0.0057401 | 0.068678 | 0.07009 | 0.13014 | -0.0015723 | -0.0062229 | 0.11429 | -0.008058 | 0.059778 | 0.057185 | 0.0048492 | -0.0081284 | 63.739 | 63.8763 | 1.1536 | -59.1843 | 63.8901 | -59.0927 | -59.166 | -58.5938 | 1.9409 | -59.2392 | 63.858 | 63.7527 | -59.198 | -59.2438 | -0.064087 | -0.13733 | 0.10986 | 122.905 | -0.15564 | -0.01831 | -0.041198 | -0.16937 | -0.21515 | 0.07782 | 0.43487 | -0.21057 | 0.004577 | -0.027465 | 122.9187 | 122.7676 | 60.1822 | -122.9462 | 122.8867 | 122.7814 | 60.9695 | -123.024
1440.0156 | 123.1293 | -59.0012 | 63.7527 | 0.17532 | 0.01044 | 0.067396 | 0.069876 | 0.12993 | 0.0027001 | -0.0036595 | 0.19821 | -0.0082716 | 0.064051 | 0.058253 | 0.0050628 | -0.010051 | 63.739 | 63.8397 | 1.0666 | -59.1934 | 63.8763 | -59.1019 | -59.1751 | -58.5297 | 1.8677 | -59.23 | 63.858 | 63.7344 | -59.2072 | -59.2621 | -0.10071 | -0.17395 | 0.1236 | 122.8409 | -0.19226 | -0.01831 | -0.013733 | -0.20599 | -0.26093 | 0.10529 | 0.4715 | -0.22888 | 0.032043 | -0.018311 | 122.8775 | 122.7402 | 60.0677 | -122.9279 | 122.8592 | 122.7356 | 60.8688 | -123.0148
1441.0156 | 123.0698 | -59.0286 | 63.7619 | 0.20584 | 0.0070217 | 0.067823 | 0.067313 | 0.13057 | -0.00050425 | -0.0036595 | 0.19821 | -0.008058 | 0.060633 | 0.06103 | 0.0048492 | -0.0072738 | 63.7802 | 63.9038 | 0.90179 | -59.1934 | 63.8489 | -59.1019 | -59.1797 | -58.5342 | 1.8997 | -59.2117 | 63.8077 | 63.7436 | -59.2026 | -59.2712 | -0.073243 | -0.15106 | 0.086975 | 122.9324 | -0.1648 | -0.013733 | 0.01831 | -0.17395 | -0.24262 | 0.045776 | 0.49438 | -0.18311 | 0.059509 | -0.018311 | 122.8775 | 122.8088 | 59.9304 | -122.9416 | 122.8363 | 122.7722 | 60.9283 | -123.0331
1442.0156 | 123.0972 | -58.9874 | 63.8306 | 0.16769 | 0.0070217 | 0.067182 | 0.068381 | 0.12886 | -0.0015723 | -0.0030185 | 0.20584 | -0.0065626 | 0.061701 | 0.057398 | 0.002713 | -0.0077012 | 63.7939 | 63.9359 | 0.36163 | -59.1522 | 63.8626 | -59.0469 | -59.1156 | -58.5114 | 1.6708 | -59.198 | 63.8626 | 63.7756 | -59.1797 | -59.2255 | -0.059509 | -0.12817 | 0.032044 | 122.9233 | -0.1648 | -0.036621 | -0.036621 | -0.19226 | -0.23804 | 0.032044 | 0.47607 | -0.21057 | 0.027466 | -0.054931 | 122.85 | 122.7814 | 59.3491 | -122.9462 | 122.85 | 122.7631 | 60.6583 | -123.056
1443.0156 | 123.0835 | -58.9462 | 63.8489 | 0.099029 | 0.0085171 | 0.067823 | 0.069235 | 0.12971 | -0.00050425 | -0.0040867 | 0.20584 | -0.0093396 | 0.062982 | 0.059321 | 0.0039948 | -0.0070602 | 63.8489 | 63.9725 | 0.013733 | -59.1156 | 63.913 | -59.024 | -59.0881 | -58.4656 | 1.561 | -59.1522 | 63.9175 | 63.7894 | -59.1339 | -59.2209 | -0.07782 | -0.14191 | 0.064087 | 122.9187 | -0.16937 | -0.027466 | 0 | -0.18768 | -0.27466 | 0.068665 | 0.48065 | -0.20599 | 0.068664 | -0.059509 | 122.8592 | 122.7951 | 58.96 | -122.937 | 122.8638 | 122.7356 | 60.5072 | -123.0698
1444.0156 | 123.0652 | -58.9554 | 63.8306 | 0.18295 | 0.010867 | 0.069319 | 0.071585 | 0.13249 | 0.0012047 | -0.0023777 | 0.16006 | -0.0059216 | 0.064051 | 0.058467 | 0.006131 | -0.0096238 | 63.8031 | 63.8901 | 0.51727 | -59.1614 | 63.9496 | -59.0561 | -59.0973 | -58.5068 | 1.7075 | -59.1934 | 63.8855 | 63.7848 | -59.1568 | -59.2117 | -0.10071 | -0.14191 | 0.11902 | 122.8455 | -0.20599 | -0.064087 | -0.027465 | -0.20142 | -0.25635 | 0.054932 | 0.44861 | -0.23804 | 0.018311 | -0.045776 | 122.905 | 122.7585 | 59.4727 | -122.9279 | 122.8409 | 122.7402 | 60.6628 | -123.0423
1445.0156 | 123.0698 | -58.9874 | 63.8626 | 0.17532 | 0.0070217 | 0.068891 | 0.066031 | 0.13099 | -0.0022131 | -0.0047275 | 0.25162 | -0.007417 | 0.06106 | 0.060603 | 0.004422 | -0.0094102 | 63.8123 | 63.9404 | 0.6546 | -59.1248 | 63.8901 | -59.0195 | -59.0927 | -58.5114 | 1.7624 | -59.1751 | 63.8901 | 63.7985 | -59.1522 | -59.2072 | -0.032043 | -0.10529 | 0.027466 | 122.9279 | -0.13733 | -0.032044 | -0.050354 | -0.1648 | -0.21973 | 0.027466 | 0.47607 | -0.18768 | 0.032043 | -0.064087 | 122.8775 | 122.7997 | 59.642 | -122.9553 | 122.8775 | 122.7859 | 60.7498 | -123.0698
1446.0156 | 123.1293 | -58.9462 | 63.8763 | 0.18295 | 0.013644 | 0.069319 | 0.068594 | 0.13249 | 0.0012047 | -0.0015231 | 0.022736 | -0.0044264 | 0.062769 | 0.059321 | 0.0065582 | -0.0081284 | 63.858 | 63.9313 | 0.23346 | -59.0881 | 63.9725 | -58.9874 | -59.0698 | -58.461 | 1.1627 | -59.1339 | 63.9359 | 63.8489 | -59.1385 | -59.166 | -0.041199 | -0.1236 | 0.09613 | 122.8775 | -0.14191 | -0.018311 | -0.018311 | -0.19226 | -0.21973 | 0.059509 | 0.48523 | -0.18768 | 0.032044 | -0.027466 | 122.9187 | 122.8043 | 59.1797 | -122.9462 | 122.8821 | 122.7951 | 60.1089 | -123.0423
1447.0156 | 123.0698 | -58.9188 | 63.945 | -0.17563 | 0.0070217 | 0.067182 | 0.066885 | 0.13057 | -0.0013587 | -0.0051547 | -0.18326 | -0.0069898 | 0.060205 | 0.057398 | 0.00549 | -0.0064194 | 63.8809 | 64.0457 | 0.35248 | -59.0378 | 63.9633 | -58.9691 | -59.0515 | -58.4839 | 1.2589 | -59.1064 | 63.9679 | 63.8763 | -59.1019 | -59.1614 | -0.050354 | -0.13275 | 0.018311 | 122.9645 | -0.11902 | 0.013733 | -0.064087 | -0.18311 | -0.24262 | 0.022889 | 0.43487 | -0.18768 | 0.054932 | -0.068664 | 122.8821 | 122.7997 | 59.2712 | -122.9965 | 122.8867 | 122.7951 | 60.1776 | -123.1064
1448.0156 | 123.0148 | -58.9279 | 63.9084 | 0.12192 | 0.011294 | 0.066969 | 0.07009 | 0.12993 | 0.0024865 | -0.0019505 | 0.17532 | -0.0052808 | 0.066187 | 0.059748 | 0.0059174 | -0.010265 | 63.826 | 63.9038 | -0.068665 | -59.1248 | 64.0045 | -58.9828 | -59.0881 | -58.4885 | 1.2085 | -59.1705 | 63.9679 | 63.8763 | -59.1385 | -59.1934 | -0.054932 | -0.16022 | 0.096131 | 122.8317 | -0.19684 | -0.036621 | -0.082397 | -0.21057 | -0.2655 | 0.05951 | 0.43945 | -0.24262 | 0.022888 | -0.032043 | 122.9324 | 122.7539 | 58.8593 | -122.9965 | 122.8958 | 122.8043 | 60.1364 | -123.1018
1449.0156 | 123.1155 | -58.8959 | 63.8763 | 0.18295 | 0.01044 | 0.067823 | 0.068808 | 0.12971 | 0.00035035 | -0.0038731 | -0.5571 | -0.005708 | 0.059778 | 0.059321 | 0.0042084 | -0.011119 | 63.8718 | 63.9816 | 0.19684 | -59.0561 | 63.9313 | -58.9783 | -59.1156 | -58.461 | 1.1124 | -59.079 | 63.9404 | 63.8397 | -59.111 | -59.1705 | -0.082397 | -0.21973 | 0.054931 | 122.8775 | -0.16022 | 0.05951 | -0.004578 | -0.21515 | -0.27466 | 0.064087 | 0.43487 | -0.1831 | 0.091553 | -0.036621 | 122.8271 | 122.7676 | 59.0927 | -122.9919 | 122.8363 | 122.7356 | 60.0082 | -123.0469
1450.0156 | 122.9828 | -58.9233 | 63.9175 | -1.0683 | 0.01044 | 0.066755 | 0.068594 | 0.13099 | 0.0018457 | -0.0043003 | 0.21347 | -0.008058 | 0.0664 | 0.058253 | 0.0033538 | -0.0091966 | 63.8306 | 63.8901 | -0.032043 | -59.1064 | 64.032 | -59.0057 | -59.0698 | -58.5388 | 0.80566 | -59.2117 | 64.0091 | 63.9175 | -59.1019 | -59.166 | -0.082397 | -0.14648 | 0.11444 | 122.8134 | -0.1831 | -0.036621 | -0.086976 | -0.17853 | -0.24261 | 0.091552 | 0.38452 | -0.28839 | -0.045776 | 0 | 122.9553 | 122.7539 | 58.8913 | -122.9874 | 122.9324 | 122.8409 | 59.729 | -123.0835
1451.0156 | 123.1293 | -58.9096 | 63.8763 | 0.20584 | 0.010867 | 0.067823 | 0.067313 | 0.12907 | -0.0011451 | -0.0015231 | 0.18295 | -0.0050672 | 0.061914 | 0.057398 | 0.0065582 | -0.0081284 | 63.8626 | 63.9771 | 0.29297 | -59.0836 | 63.9725 | -59.0012 | -59.0607 | -58.4656 | 1.474 | -59.1339 | 63.9175 | 63.8489 | -59.111 | -59.1797 | -0.091553 | -0.15106 | 0.09613 | 122.8867 | -0.17395 | -0.022888 | -0.013733 | -0.20142 | -0.27008 | 0.041199 | 0.44403 | -0.2243 | 0.045776 | -0.027466 | 122.8821 | 122.7722 | 59.2026 | -122.937 | 122.8271 | 122.7585 | 60.3836 | -123.056
1452.0156 | 123.0423 | -58.9188 | 63.9175 | -0.0383 | 0.0070217 | 0.069746 | 0.069235 | 0.12886 | -0.0056311 | -0.0053683 | 0.0914 | -0.0065626 | 0.061914 | 0.059321 | 0.0029266 | -0.006633 | 63.8077 | 63.9816 | 0.07782 | -59.024 | 64.0091 | -58.9645 | -59.0378 | -58.5159 | 1.7761 | -59.1202 | 63.9221 | 63.9084 | -59.1202 | -59.1385 | -0.045777 | -0.11902 | 0.091552 | 122.9004 | -0.10529 | 0.013733 | -0.10986 | -0.20142 | -0.21973 | 0.004577 | 0.40283 | -0.20142 | 0.018311 | -0.009156 | 122.9279 | 122.7264 | 58.9966 | -122.9553 | 122.8409 | 122.8271 | 60.6949 | -123.056
1453.0156 | 123.1247 | -58.8959 | 63.8535 | 0.25925 | 0.011294 | 0.066541 | 0.071372 | 0.1327 | 0.00077755 | -0.0034457 | 0.25162 | -0.0078442 | 0.063196 | 0.057826 | 0.0050628 | -0.0081284 | 63.9221 | 64.0091 | -0.67749 | -59.0286 | 63.9999 | -58.96 | -59.0149 | -58.4381 | 1.6708 | -59.0973 | 63.9771 | 63.8672 | -59.0836 | -59.1522 | -0.064087 | -0.11902 | 0.14648 | 122.905 | -0.13275 | -0.013732 | 0.068664 | -0.18768 | -0.25635 | 0.1236 | 0.45776 | -0.20142 | 0.054932 | 0.013732 | 122.8958 | 122.818 | 58.2184 | -122.8683 | 122.8729 | 122.7631 | 60.5667 | -123.0057
1454.0156 | 122.9828 | -58.9371 | 63.945 | 0.030365 | 0.012362 | 0.068678 | 0.070303 | 0.13099 | 0.0041955 | -0.0021641 | 0.015106 | -0.0050672 | 0.064051 | 0.059535 | 0.0063446 | -0.010905 | 63.8535 | 63.9038 | -0.40741 | -59.0927 | 64.0366 | -58.9966 | -59.0652 | -58.5754 | 1.3046 | -59.2255 | 64.0182 | 63.9359 | -59.1019 | -59.1751 | -0.059509 | -0.12817 | 0.091553 | 122.8409 | -0.15564 | -0.027465 | -0.091552 | -0.1648 | -0.23804 | 0.073243 | 0.36163 | -0.28839 | -0.050354 | -0.009155 | 122.9736 | 122.7905 | 58.5297 | -123.0103 | 122.9553 | 122.8729 | 60.2417 | -123.1201
1455.0156 | 122.9919 | -58.905 | 63.9771 | 0.083771 | 0.014071 | 0.06761 | 0.071585 | 0.13163 | 0.0018457 | -0.0023777 | 0.16769 | -0.0048536 | 0.062555 | 0.057185 | 0.00549 | -0.0072738 | 63.826 | 63.9038 | -0.62714 | -59.0881 | 64.0549 | -58.96 | -59.024 | -58.493 | 1.4328 | -59.1568 | 64.0137 | 63.9221 | -59.0744 | -59.1522 | -0.054932 | -0.11902 | 0.07782 | 122.8088 | -0.18311 | -0.064087 | -0.15106 | -0.16937 | -0.24719 | 0.036621 | 0.41199 | -0.25177 | -0.004577 | -0.054932 | 122.9599 | 122.731 | 58.2779 | -123.0011 | 122.9187 | 122.8271 | 60.3378 | -123.1293
1456.0156 | 122.9691 | -58.8776 | 63.9954 | 0.045624 | 0.017062 | 0.067396 | 0.07244 | 0.12971 | 0.0027001 | -0.0015231 | 0.14481 | -0.006349 | 0.063623 | 0.060603 | 0.0065582 | -0.0077012 | 63.858 | 63.913 | -1.2863 | -59.0561 | 64.0915 | -58.9371 | -59.0103 | -58.5205 | 1.0986 | -59.1888 | 64.0732 | 63.9679 | -59.0469 | -59.1339 | -0.05951 | -0.13275 | 0.096131 | 122.7905 | -0.17853 | -0.045776 | -0.13733 | -0.16937 | -0.25635 | 0.07782 | 0.35706 | -0.31128 | -0.054932 | -0.027465 | 122.9691 | 122.7356 | 57.5912 | -123.0057 | 122.9507 | 122.8455 | 59.9762 | -123.1293
1457.0156 | 123.0652 | -58.7997 | 63.9954 | -0.19089 | 0.0055265 | 0.07295 | 0.069876 | 0.128 | -0.0054175 | -0.0051547 | -0.03067 | -0.008058 | 0.059778 | 0.057185 | 0.0022858 | -0.0064194 | 63.9725 | 64.1876 | -1.6022 | -58.9279 | 64.0732 | -58.873 | -58.9462 | -58.4152 | 1.5289 | -58.9828 | 64.0823 | 63.9679 | -59.0012 | -59.0698 | -0.073242 | -0.14648 | 0.07782 | 122.9874 | -0.12817 | 0.018311 | -0.022888 | -0.20142 | -0.27008 | 0.086975 | 0.38452 | -0.18311 | 0.086975 | -0.027465 | 122.8729 | 122.7722 | 57.1976 | -122.9416 | 122.8821 | 122.7676 | 60.3287 | -123.0652
1458.0156 | 122.9736 | -58.8867 | 63.9908 | -0.015411 | 0.013217 | 0.066541 | 0.072012 | 0.13249 | 0.0029137 | -0.0021641 | 0.030365 | -0.0061352 | 0.066828 | 0.058253 | 0.0082672 | -0.010905 | 63.8992 | 63.9862 | -1.712 | -59.0378 | 64.0869 | -58.9371 | -58.992 | -58.5068 | 0.737 | -59.1339 | 64.0869 | 63.9725 | -59.0424 | -59.1339 | -0.050354 | -0.10529 | 0.09613 | 122.8729 | -0.15106 | -0.045777 | -0.091553 | -0.15564 | -0.24719 | 0.09613 | 0.37994 | -0.24719 | 0 | -0.018311 | 122.9736 | 122.7859 | 57.1747 | -122.9828 | 122.9736 | 122.8592 | 59.6237 | -123.1247
1459.0156 | 123.0972 | -58.8593 | 63.9679 | 0.18295 | 0.013858 | 0.068037 | 0.071799 | 0.12779 | -0.00071785 | -0.0038731 | 0.23636 | -0.0061352 | 0.06106 | 0.05868 | 0.0050628 | -0.0072738 | 63.8763 | 63.9954 | -1.2955 | -59.0332 | 64.0823 | -58.9462 | -58.9874 | -58.4335 | 0.74158 | -59.0652 | 64.0137 | 63.9542 | -59.0286 | -59.1064 | -0.086975 | -0.12817 | 0.11444 | 122.8546 | -0.17395 | -0.045776 | -0.091553 | -0.16937 | -0.24719 | 0.045776 | 0.42572 | -0.20599 | 0.041198 | -0.013733 | 122.9416 | 122.7356 | 57.5638 | -122.9553 | 122.8729 | 122.8134 | 59.6008 | -123.0743
1460.0156 | 122.9599 | -58.8455 | 63.9908 | 0.053253 | 0.014499 | 0.066755 | 0.071585 | 0.12907 | 0.0020593 | -0.0036595 | -0.00015237 | -0.0054944 | 0.063196 | 0.060603 | 0.0039948 | -0.0089828 | 63.8947 | 63.9725 | -1.3779 | -59.0652 | 64.1052 | -58.9188 | -58.9828 | -58.5205 | 0.52643 | -59.1614 | 64.0503 | 64.0045 | -59.0378 | -59.1339 | -0.073242 | -0.13733 | 0.11444 | 122.818 | -0.21973 | -0.082398 | -0.096131 | -0.19226 | -0.28839 | 0.059509 | 0.32501 | -0.31586 | -0.027466 | 0.013733 | 122.9507 | 122.7402 | 57.4677 | -122.9736 | 122.8958 | 122.85 | 59.3719 | -123.1247
1461.0156 | 123.0057 | -58.8501 | 64.0091 | 0.13718 | 0.015567 | 0.066114 | 0.071158 | 0.13142 | 0.0022729 | -0.0010959 | -1.6328 | -0.005708 | 0.064264 | 0.05633 | 0.0029266 | -0.0074876 | 63.8763 | 63.9587 | -1.8768 | -59.0332 | 64.1281 | -58.9188 | -59.0012 | -58.4839 | 0.3479 | -59.0927 | 64.0915 | 64.0137 | -59.0424 | -59.079 | -0.068664 | -0.15106 | 0.11902 | 122.8088 | -0.1831 | -0.032043 | -0.13275 | -0.19226 | -0.22888 | 0.082398 | 0.36621 | -0.24261 | -0.013733 | 0.004578 | 122.9782 | 122.7264 | 56.9733 | -123.0103 | 122.9416 | 122.8638 | 59.198 | -123.0881
1462.0156 | 123.0972 | -58.8089 | 63.9954 | 0.16769 | 0.011294 | 0.069746 | 0.069663 | 0.12864 | -0.0019995 | -0.0013095 | 0.068512 | -0.0095532 | 0.06106 | 0.059748 | 0.0037812 | -0.006633 | 63.945 | 64.0778 | -2.1561 | -58.9417 | 64.0594 | -58.8593 | -58.9828 | -58.3786 | 0.5722 | -59.0149 | 64.0366 | 63.9954 | -58.9783 | -59.0424 | -0.050354 | -0.17395 | 0.064087 | 122.8867 | -0.13275 | 0.041199 | -0.050354 | -0.16937 | -0.23346 | 0.041199 | 0.4303 | -0.20599 | 0.027465 | 0 | 122.8683 | 122.7539 | 56.6528 | -122.9782 | 122.8455 | 122.8043 | 59.3811 | -123.0377
1463.0156 | 123.0331 | -58.8364 | 64.0137 | 1.4037 | 0.013431 | 0.070173 | 0.07009 | 0.128 | -0.00071785 | -0.0025913 | 0.16769 | -0.005708 | 0.063623 | 0.059107 | 0.0067718 | -0.0089828 | 63.9359 | 63.9359 | -2.2156 | -59.0149 | 64.1052 | -58.9188 | -58.9828 | -58.4473 | 0.78278 | -59.1156 | 64.0869 | 64.0366 | -59.0469 | -59.0836 | -0.082397 | -0.14648 | 0.091553 | 122.7722 | -0.17853 | -0.032044 | -0.07782 | -0.21057 | -0.24719 | 0.073242 | 0.3891 | -0.27924 | -0.032044 | 0.022888 | 122.9416 | 122.7722 | 56.6208 | -122.9965 | 122.9233 | 122.8729 | 59.6191 | -123.0972
1464.0156 | 123.0103 | -58.8318 | 64.0686 | -0.03067 | 0.014071 | 0.069105 | 0.072226 | 0.13185 | 0.00013675 | -0.0010959 | 0.037995 | -0.0069898 | 0.065332 | 0.058253 | 0.0059174 | -0.0089828 | 63.9679 | 64.0411 | -1.8631 | -58.9691 | 64.1235 | -58.8501 | -58.9554 | -58.4381 | 0.60883 | -59.1019 | 64.1098 | 64.0366 | -59.0103 | -59.0607 | -0.018311 | -0.1236 | 0.054931 | 122.8729 | -0.13733 | -0.013733 | -0.10071 | -0.17853 | -0.22888 | 0.041198 | 0.39368 | -0.27008 | -0.041199 | -0.032044 | 122.9553 | 122.7997 | 56.9687 | -123.024 | 122.9416 | 122.8683 | 59.4406 | -123.1293
1465.0156 | 122.9874 | -58.8364 | 64.0549 | 0.11429 | 0.013858 | 0.067182 | 0.07244 | 0.12907 | 0.00056395 | -0.0045139 | 0.14481 | -0.0033582 | 0.067255 | 0.055476 | 0.00057682 | -0.0074876 | 63.8855 | 63.9725 | -2.1332 | -59.024 | 64.1647 | -58.8867 | -58.9508 | -58.3099 | 0.41657 | -59.0424 | 64.119 | 64.064 | -58.9828 | -59.0378 | -0.050354 | -0.11444 | 0.10986 | 122.8088 | -0.18768 | -0.073242 | -0.16937 | -0.14648 | -0.20142 | 0.064087 | 0.52643 | -0.20599 | -0.004577 | 0.009155 | 123.0011 | 122.7219 | 56.7032 | -123.0057 | 122.9553 | 122.9004 | 59.2529 | -123.0927
1466.0156 | 123.0057 | -58.8547 | 64.0503 | -0.023041 | 0.014285 | 0.065687 | 0.071585 | 0.13014 | 0.0016321 | -0.0051547 | 0.030365 | -0.007417 | 0.064691 | 0.060389 | 0.0022858 | -0.008342 | 63.945 | 64.0366 | -1.8631 | -58.992 | 64.1144 | -58.8821 | -58.9554 | -58.4381 | 0.72327 | -59.0927 | 64.1052 | 64.0503 | -58.992 | -59.0744 | -0.027466 | -0.10071 | 0.064087 | 122.8912 | -0.13733 | -0.036621 | -0.10529 | -0.13733 | -0.21973 | 0.054932 | 0.41656 | -0.23804 | -0.01831 | 0 | 122.9691 | 122.7997 | 56.9916 | -123.0057 | 122.9599 | 122.905 | 59.5779 | -123.1247
1467.0156 | 123.0011 | -58.8684 | 64.0366 | 0.13718 | 0.014071 | 0.068464 | 0.066458 | 0.12758 | -0.0013587 | -0.0057957 | 0.16769 | -0.0052808 | 0.064691 | 0.058039 | 0.0069854 | -0.006633 | 64.1464 | 63.8626 | -2.1057 | -58.9417 | 64.1418 | -58.8776 | -58.9828 | -58.461 | 0.19226 | -59.0973 | 64.1144 | 64.0503 | -59.0149 | -59.0744 | -0.009155 | -0.11444 | 0.10529 | 122.731 | -0.073242 | 0.041199 | 0.10986 | -0.14648 | -0.20599 | 0.07782 | 0.40741 | -0.22888 | -0.022888 | 0.013733 | 123.0103 | 123.0148 | 56.7627 | -123.0194 | 122.9828 | 122.9187 | 59.0607 | -123.111
1468.0156 | 123.0469 | -58.8089 | 64.0549 | -0.076447 | 0.01514 | 0.067396 | 0.070517 | 0.12928 | 0.0016321 | -0.0053683 | -0.023041 | -0.0048536 | 0.064478 | 0.059107 | 0.0035674 | -0.0089828 | 63.9633 | 64.0778 | -2.1881 | -58.9508 | 64.1418 | -58.8821 | -58.9371 | -58.3832 | 0.34332 | -59.0973 | 64.0869 | 64.0457 | -58.9874 | -59.0744 | -0.073242 | -0.12817 | 0.086975 | 122.8867 | -0.14191 | -0.013733 | -0.091553 | -0.17853 | -0.2655 | 0.032043 | 0.42572 | -0.28839 | -0.022888 | -0.009156 | 122.9507 | 122.7722 | 56.6208 | -122.9919 | 122.8958 | 122.8546 | 59.1522 | -123.1293
1469.0156 | 123.0011 | -58.8364 | 64.032 | -0.31296 | 0.014712 | 0.069532 | 0.070731 | 0.12886 | 0.00013675 | -0.0045139 | 0.19821 | -0.0069898 | 0.061914 | 0.058467 | 0.0048492 | -0.0074876 | 63.8809 | 64.0137 | -2.0966 | -58.9966 | 64.1281 | -58.905 | -58.9417 | -58.4473 | 0.59052 | -59.0836 | 64.1052 | 64.0182 | -59.0149 | -59.0607 | -0.068664 | -0.10529 | 0.096131 | 122.85 | -0.16022 | -0.054932 | -0.15106 | -0.17853 | -0.2243 | 0.073243 | 0.3891 | -0.24719 | -0.022888 | -0.013732 | 122.9645 | 122.7173 | 56.7398 | -122.9736 | 122.9416 | 122.8546 | 59.4269 | -123.0927
1470.0156 | 123.0011 | -58.7952 | 64.0549 | -0.053558 | 0.013217 | 0.067823 | 0.072226 | 0.12907 | 0.0022729 | -0.0036595 | 0.15244 | -0.0059216 | 0.064905 | 0.059962 | 0.0039948 | -0.0070602 | 64.0961 | 63.7939 | -2.6138 | -58.9325 | 64.119 | -58.8821 | -58.9325 | -58.3786 | 0.61798 | -59.0149 | 64.1098 | 64.064 | -58.9691 | -59.0286 | -0.086975 | -0.13733 | 0.064087 | 122.5891 | -0.13733 | 0 | 0.041198 | -0.17395 | -0.23346 | 0.054931 | 0.41656 | -0.21973 | 0.013732 | 0.009155 | 122.9141 | 122.8912 | 56.1813 | -122.9874 | 122.905 | 122.8592 | 59.4131 | -123.0835
1471.0156 | 122.9965 | -58.8272 | 64.064 | 0.015106 | 0.016849 | 0.070387 | 0.070303 | 0.13057 | 0.00035035 | -0.0057957 | 0.09903 | -0.005708 | 0.063837 | 0.060816 | 0.0039948 | -0.0064194 | 63.9175 | 64.0182 | -2.4673 | -58.9508 | 64.1327 | -58.873 | -58.9279 | -58.4564 | 0.5127 | -59.0973 | 64.1281 | 64.0823 | -58.992 | -59.0561 | -0.045777 | -0.10071 | 0.068664 | 122.8455 | -0.1236 | -0.022889 | -0.14648 | -0.16479 | -0.22888 | 0.064087 | 0.37079 | -0.27008 | -0.041199 | 0.01831 | 122.9599 | 122.7448 | 56.3599 | -122.9919 | 122.9553 | 122.9095 | 59.3399 | -123.1201
1472.0156 | 123.1018 | -58.7906 | 64.0915 | -0.15274 | 0.01514 | 0.066541 | 0.07244 | 0.13057 | -7.6852e-05 | -0.0049411 | -0.015411 | -0.0061352 | 0.064264 | 0.058894 | 0.004422 | -0.006633 | 63.9954 | 64.1006 | -2.9526 | -58.9142 | 64.1418 | -58.8364 | -58.9142 | -58.3786 | 0.36163 | -59.0103 | 64.1418 | 64.0823 | -58.9508 | -59.0286 | -0.045777 | -0.1236 | 0.050354 | 122.8912 | -0.1236 | 0 | -0.096131 | -0.16022 | -0.23804 | 0.050354 | 0.41199 | -0.21973 | 0.01831 | -0.009156 | 122.9324 | 122.7859 | 55.838 | -123.0057 | 122.9324 | 122.8729 | 59.1522 | -123.1201
1473.0156 | 122.9691 | -58.8318 | 64.0549 | 0.17532 | 0.01514 | 0.067396 | 0.070731 | 0.12993 | 0.00099115 | -0.0030185 | 0.15244 | -0.0052808 | 0.063837 | 0.06103 | 0.0035674 | -0.0062058 | 63.8809 | 63.9999 | -2.8473 | -58.992 | 64.1235 | -58.8547 | -58.9645 | -58.5068 | 0.73242 | -59.1156 | 64.1098 | 64.064 | -58.9966 | -59.0652 | -0.022888 | -0.13275 | 0.068664 | 122.8317 | -0.16022 | -0.027465 | -0.17395 | -0.16479 | -0.23346 | 0.054931 | 0.32501 | -0.28381 | -0.050354 | 0.009155 | 122.9553 | 122.7127 | 55.9845 | -123.0194 | 122.9416 | 122.8958 | 59.5642 | -123.1201
1474.0156 | 123.0377 | -58.7952 | 64.0869 | -0.25192 | 0.011294 | 0.069746 | 0.072653 | 0.13142 | -0.00071785 | -0.0055821 | -0.10696 | -0.0061352 | 0.064905 | 0.059535 | 0.0033538 | -0.0074876 | 63.9587 | 64.0686 | -3.2318 | -58.9279 | 64.183 | -58.8364 | -58.9279 | -58.4015 | 1.0437 | -59.0149 | 64.1281 | 64.0915 | -58.9554 | -59.0149 | -0.041199 | -0.13275 | 0.09613 | 122.8638 | -0.13275 | 0 | -0.12817 | -0.16022 | -0.21973 | 0.041199 | 0.39368 | -0.21973 | 0 | 0.004578 | 122.9782 | 122.7539 | 55.5634 | -123.0148 | 122.9233 | 122.8867 | 59.8389 | -123.1018
1475.0156 | 123.024 | -58.8593 | 64.0274 | -0.061188 | 0.016421 | 0.064832 | 0.071585 | 0.13057 | 0.0035547 | -0.0040867 | 0.022736 | -0.0067762 | 0.064691 | 0.059748 | 0.0031402 | -0.008342 | 63.9404 | 64.0457 | -2.4719 | -59.0012 | 64.1098 | -58.873 | -58.96 | -58.4518 | 1.355 | -59.0927 | 64.1006 | 64.032 | -59.0195 | -59.0744 | -0.013733 | -0.10071 | 0.082397 | 122.905 | -0.14191 | -0.041199 | -0.086975 | -0.16022 | -0.21515 | 0.073242 | 0.40741 | -0.23346 | -0.01831 | 0.004577 | 122.9691 | 122.7997 | 56.3873 | -122.9874 | 122.9599 | 122.8912 | 60.2142 | -123.1018
1476.0156 | 123.024 | -58.8272 | 64.0457 | -0.19089 | 0.012362 | 0.069532 | 0.069449 | 0.13014 | -0.00050425 | -0.0036595 | 0.053253 | -0.0052808 | 0.061914 | 0.060176 | 0.0067718 | -0.0087692 | 63.9221 | 64.0549 | -2.1698 | -58.9554 | 64.1281 | -58.8959 | -58.9828 | -58.429 | 1.506 | -59.0652 | 64.0778 | 64.0411 | -59.0103 | -59.0698 | -0.068665 | -0.15564 | 0.082398 | 122.8821 | -0.12817 | 0.027466 | -0.1236 | -0.18311 | -0.24261 | 0.032044 | 0.39825 | -0.23804 | 0.004577 | -0.004577 | 122.9553 | 122.7493 | 56.6574 | -123.0286 | 122.905 | 122.8683 | 60.3333 | -123.1155
1477.0156 | 122.9874 | -58.8364 | 64.0594 | 0.0074768 | 0.014926 | 0.06825 | 0.070517 | 0.13035 | 0.00077755 | -0.0028049 | 0.10666 | -0.0059216 | 0.064264 | 0.058894 | 0.0033538 | -0.0094102 | 63.9221 | 64.0228 | -2.6733 | -58.992 | 64.1144 | -58.8959 | -58.96 | -58.4656 | 1.2589 | -59.1064 | 64.0869 | 64.032 | -59.0286 | -59.0927 | -0.059509 | -0.1236 | 0.054932 | 122.8592 | -0.15564 | -0.032043 | -0.13733 | -0.19226 | -0.25635 | 0.027466 | 0.37079 | -0.27008 | -0.013733 | -0.027466 | 122.9507 | 122.7585 | 56.163 | -123.0194 | 122.9233 | 122.8683 | 60.0952 | -123.1522
1478.0156 | 123.0286 | -58.8638 | 64.0228 | -0.20615 | 0.013644 | 0.06825 | 0.073294 | 0.13078 | 0.00056395 | -0.0053683 | -0.10696 | -0.0069898 | 0.065546 | 0.059748 | 0.00549 | -0.0087692 | 63.8992 | 64.032 | -2.33 | -58.9783 | 64.1235 | -58.8913 | -58.9874 | -58.4518 | 1.474 | -59.0652 | 64.0961 | 64.064 | -59.0103 | -59.0927 | -0.027465 | -0.1236 | 0.10071 | 122.8958 | -0.11444 | 0.009156 | -0.1236 | -0.14648 | -0.22888 | 0.073242 | 0.41199 | -0.20142 | 0.027465 | 0.041199 | 122.9874 | 122.7631 | 56.5338 | -123.0103 | 122.9599 | 122.9279 | 60.3378 | -123.1155
1479.0156 | 122.9736 | -58.873 | 64.0228 | -0.00015269 | 0.015353 | 0.066969 | 0.069876 | 0.13249 | 0.0012047 | -0.0023777 | 0.11429 | -0.006349 | 0.065332 | 0.057398 | 0.0050628 | -0.0051376 | 63.8626 | 63.9816 | -2.861 | -59.024 | 64.0915 | -58.9279 | -58.9874 | -58.5068 | 1.5152 | -59.1476 | 64.0732 | 63.9954 | -59.0607 | -59.1202 | -0.054931 | -0.11444 | 0.068665 | 122.8546 | -0.15106 | -0.036621 | -0.16022 | -0.18768 | -0.24719 | 0.050354 | 0.36621 | -0.27466 | -0.027466 | -0.027466 | 122.9645 | 122.7356 | 56.012 | -123.0103 | 122.9462 | 122.8683 | 60.3882 | -123.143
1480.0156 | 123.0377 | -58.8181 | 64.064 | -0.13748 | 0.01514 | 0.0706 | 0.070731 | 0.13313 | 0.0012047 | -0.0049411 | -0.0077819 | -0.0061352 | 0.064691 | 0.060603 | 0.0039948 | -0.006633 | 63.9587 | 64.0732 | -2.8519 | -58.9554 | 64.1235 | -58.873 | -58.9691 | -58.429 | 1.5015 | -59.0469 | 64.1327 | 64.0503 | -58.992 | -59.0469 | -0.054932 | -0.15106 | 0.059509 | 122.8912 | -0.13733 | 0.013733 | -0.10529 | -0.17395 | -0.22888 | 0.068664 | 0.3891 | -0.22888 | 0 | -0.013733 | 122.9416 | 122.7768 | 55.9662 | -123.0331 | 122.9507 | 122.8683 | 60.3195 | -123.111
1481.0156 | 123.0377 | -58.8776 | 64.0182 | -0.00015269 | 0.014926 | 0.06825 | 0.069876 | 0.13099 | 0.00077755 | -0.0043003 | -0.015411 | -0.0044264 | 0.063623 | 0.059107 | 0.006131 | -0.0079148 | 63.8992 | 64.0366 | -2.4536 | -59.0149 | 64.0457 | -58.9142 | -59.0103 | -58.4747 | 1.7166 | -59.1156 | 64.0366 | 63.9771 | -59.0652 | -59.0927 | -0.036622 | -0.13275 | 0.027465 | 122.9141 | -0.13733 | -0.004578 | -0.11902 | -0.18768 | -0.21515 | 0.01831 | 0.40283 | -0.23804 | -0.022889 | -0.041199 | 122.9233 | 122.7768 | 56.424 | -123.0286 | 122.9141 | 122.8546 | 60.5942 | -123.111
1482.0156 | 123.0515 | -58.8455 | 64.0182 | -0.22903 | 0.014285 | 0.068678 | 0.07009 | 0.1295 | 0.00013675 | -0.0036595 | -0.14511 | -0.0050672 | 0.065546 | 0.060816 | 0.0035674 | -0.0070602 | 63.8535 | 63.9954 | -2.4719 | -59.0195 | 64.0915 | -58.9142 | -58.9966 | -58.5114 | 1.6205 | -59.0927 | 64.0732 | 64.0366 | -59.0378 | -59.1019 | -0.068665 | -0.15106 | 0.073242 | 122.8409 | -0.17395 | -0.022888 | -0.16479 | -0.19226 | -0.25635 | 0.054931 | 0.33417 | -0.24719 | 0.009156 | 0.01831 | 122.937 | 122.699 | 56.3736 | -123.0148 | 122.9187 | 122.8821 | 60.466 | -123.1201
1483.0156 | 122.9965 | -58.8638 | 64.0228 | -0.015411 | 0.011935 | 0.066541 | 0.07244 | 0.12843 | 0.0024865 | -0.0062229 | 0.0914 | -0.008058 | 0.064905 | 0.056971 | 0.0052764 | -0.0081284 | 63.8992 | 63.9999 | -2.6505 | -59.0286 | 64.0961 | -58.905 | -58.9783 | -58.4976 | 1.3321 | -59.111 | 64.0778 | 64.0366 | -59.0195 | -59.079 | -0.041198 | -0.11444 | 0.073242 | 122.8638 | -0.16479 | -0.050354 | -0.1236 | -0.15564 | -0.21515 | 0.054932 | 0.36621 | -0.24719 | -0.032044 | 0.013733 | 122.9599 | 122.7631 | 56.2134 | -123.0011 | 122.9416 | 122.9004 | 60.1959 | -123.1018
1484.0156 | 123.0515 | -58.8684 | 64.0366 | -0.20615 | 0.013003 | 0.067182 | 0.069876 | 0.12843 | 0.00077755 | -0.0053683 | -0.076446 | -0.0076306 | 0.063196 | 0.058467 | 0.0039948 | -0.0077012 | 63.8901 | 64.0228 | -2.4673 | -58.9737 | 64.0915 | -58.8913 | -59.0103 | -58.4564 | 1.3824 | -59.0652 | 64.0869 | 64.0274 | -59.0332 | -59.0927 | -0.022888 | -0.14191 | 0.054932 | 122.8912 | -0.10529 | 0.036621 | -0.14648 | -0.16479 | -0.2243 | 0.050354 | 0.41199 | -0.19684 | 0.027465 | -0.009155 | 122.9599 | 122.7585 | 56.4011 | -123.0469 | 122.9553 | 122.8958 | 60.2509 | -123.1293
1485.0156 | 122.9919 | -58.8913 | 64.032 | -0.068817 | 0.011508 | 0.069319 | 0.070303 | 0.12886 | 0.00056395 | -0.0045139 | 0.068512 | -0.0050672 | 0.063837 | 0.059321 | 0.0052764 | -0.0091966 | 63.9084 | 64.0228 | -2.6321 | -58.992 | 64.1052 | -58.873 | -58.9828 | -58.4702 | 1.1078 | -59.1019 | 64.0686 | 64.0137 | -59.0378 | -59.079 | 0.01831 | -0.091553 | 0.073243 | 122.9141 | -0.10071 | -0.009155 | -0.1236 | -0.14649 | -0.18768 | 0.036622 | 0.42114 | -0.21057 | -0.022889 | -0.01831 | 122.9965 | 122.7997 | 56.2592 | -123.0148 | 122.9599 | 122.905 | 59.9991 | -123.111
1486.0156 | 123.0835 | -58.8135 | 64.0594 | -0.076447 | 0.014071 | 0.068464 | 0.070944 | 0.13185 | 0.0014185 | -0.0038731 | -0.015411 | -0.0078442 | 0.064264 | 0.058253 | 0.0046356 | -0.0070602 | 63.945 | 64.0686 | -2.7878 | -58.96 | 64.1098 | -58.8593 | -58.9508 | -58.4427 | 1.0803 | -59.1431 | 64.064 | 64.0457 | -59.0195 | -59.0744 | -0.045776 | -0.13733 | 0.050354 | 122.8821 | -0.14648 | -0.009155 | -0.11444 | -0.20599 | -0.26093 | 0.004578 | 0.37079 | -0.32959 | -0.068664 | -0.013733 | 122.9233 | 122.7585 | 56.0257 | -123.0103 | 122.8775 | 122.8592 | 59.8938 | -123.1338
1487.0156 | 122.9782 | -58.8226 | 64.0594 | 0.0074768 | 0.017062 | 0.069532 | 0.070731 | 0.12758 | 0.0037683 | -0.0034457 | 0.045624 | -0.0069898 | 0.064051 | 0.059962 | 0.006131 | -0.0098374 | 63.8901 | 63.9999 | -2.7878 | -58.9966 | 64.1235 | -58.9005 | -58.9645 | -58.4885 | 0.85602 | -59.111 | 64.1098 | 64.0594 | -59.0195 | -59.0881 | -0.07782 | -0.14191 | 0.064087 | 122.8226 | -0.17395 | -0.032043 | -0.16937 | -0.19684 | -0.2655 | 0.050354 | 0.33417 | -0.28839 | -0.022888 | 0 | 122.9462 | 122.7127 | 56.0349 | -123.024 | 122.9324 | 122.8821 | 59.6786 | -123.1476
1488.0156 | 123.0103 | -58.8135 | 64.0732 | -0.15274 | 0.012576 | 0.067396 | 0.069022 | 0.12544 | -0.0022131 | -0.0062229 | -0.14511 | -0.0084852 | 0.063196 | 0.058253 | 0.002713 | -0.008342 | 63.9221 | 64.0457 | -2.6871 | -58.9645 | 64.1556 | -58.8501 | -58.96 | -58.4335 | 0.71869 | -59.0424 | 64.1373 | 64.0869 | -58.992 | -59.0515 | -0.036621 | -0.14648 | 0.082398 | 122.8592 | -0.15106 | -0.004578 | -0.15106 | -0.17853 | -0.23804 | 0.064087 | 0.37994 | -0.22888 | 0.009156 | 0.013733 | 122.9691 | 122.7356 | 56.1264 | -123.0331 | 122.9507 | 122.9004 | 59.5322 | -123.1247
1489.0156 | 123.0423 | -58.8455 | 64.0594 | -0.045929 | 0.019839 | 0.066328 | 0.074149 | 0.13078 | 0.0012047 | -0.0038731 | 0.0074766 | -0.0078442 | 0.062982 | 0.058039 | 0.0042084 | -0.006633 | 63.9725 | 64.0961 | -2.6505 | -58.9462 | 64.1327 | -58.873 | -58.9462 | -58.4244 | 0.55389 | -59.0607 | 64.1006 | 64.0503 | -59.0149 | -59.0378 | -0.027466 | -0.10071 | 0.073242 | 122.9416 | -0.10071 | 0 | -0.086975 | -0.16937 | -0.19226 | 0.041199 | 0.42114 | -0.21515 | -0.022888 | -0.009155 | 122.9782 | 122.818 | 56.1951 | -123.0057 | 122.9462 | 122.8958 | 59.3994 | -123.0972
1490.0156 | 123.0148 | -58.7997 | 64.0778 | -0.22141 | 0.010226 | 0.069959 | 0.069235 | 0.13014 | 0.00056395 | -0.0036595 | -0.25192 | -0.0072034 | 0.064478 | 0.057398 | 0.0057038 | -0.0072738 | 63.9542 | 64.1235 | -2.8702 | -58.9142 | 64.1739 | -58.8409 | -58.9188 | -58.3878 | 0.50354 | -59.0195 | 64.1464 | 64.0732 | -58.9691 | -59.0012 | -0.041198 | -0.11902 | 0.09613 | 122.9233 | -0.11444 | 0.004577 | -0.1236 | -0.16937 | -0.20142 | 0.068664 | 0.41199 | -0.21973 | -0.01831 | -0.004578 | 122.9736 | 122.7539 | 55.9296 | -122.9965 | 122.9462 | 122.8729 | 59.3033 | -123.0789
1491.0156 | 123.0103 | -58.7906 | 64.0869 | -0.0383 | 0.014712 | 0.06761 | 0.070303 | 0.1295 | 0.0039819 | -0.0055821 | 0.037995 | -0.0076306 | 0.064051 | 0.059962 | 0.0035674 | -0.0098374 | 63.9542 | 64.0823 | -3.2272 | -58.9554 | 64.1327 | -58.8547 | -58.905 | -58.4335 | 0.56305 | -59.0607 | 64.1281 | 64.064 | -58.9874 | -59.0469 | -0.064087 | -0.11444 | 0.045776 | 122.8729 | -0.16479 | -0.050354 | -0.13275 | -0.19684 | -0.25635 | 0.041199 | 0.35706 | -0.27008 | -0.013733 | -0.022888 | 122.9233 | 122.7448 | 55.5634 | -122.9919 | 122.9187 | 122.8546 | 59.3536 | -123.1338
1492.0156 | 123.056 | -58.7906 | 64.1052 | -0.22903 | 0.010653 | 0.070173 | 0.071158 | 0.12971 | 0.00099115 | -0.0038731 | -0.10696 | -0.006349 | 0.062769 | 0.059535 | 0.0020722 | -0.0087692 | 63.9587 | 64.0961 | -2.8885 | -58.9142 | 64.1968 | -58.8409 | -58.9233 | -58.3969 | 0.33417 | -58.9874 | 64.1647 | 64.0823 | -58.96 | -58.9966 | -0.050354 | -0.13275 | 0.091552 | 122.8867 | -0.1236 | 0.009155 | -0.14649 | -0.16937 | -0.20599 | 0.059509 | 0.39368 | -0.19684 | 0.009155 | -0.022889 | 122.9874 | 122.7493 | 55.9021 | -123.0286 | 122.9553 | 122.8729 | 59.1248 | -123.1018
1493.0156 | 122.9828 | -58.7997 | 64.1235 | 0.0074768 | 0.014712 | 0.067396 | 0.070731 | 0.12886 | 0.0020593 | -0.0043003 | 0.076141 | -0.0065626 | 0.065546 | 0.058467 | 0.004422 | -0.0085556 | 63.9496 | 64.0686 | -2.9709 | -58.9371 | 64.1785 | -58.8501 | -58.8913 | -58.461 | 0.004578 | -59.0607 | 64.1693 | 64.119 | -58.9691 | -58.9966 | -0.050354 | -0.091552 | 0.054932 | 122.8683 | -0.13733 | -0.045777 | -0.17395 | -0.16937 | -0.19684 | 0.045777 | 0.33874 | -0.26093 | -0.064087 | -0.004577 | 122.9782 | 122.7493 | 55.8289 | -123.0148 | 122.9691 | 122.9187 | 58.8043 | -123.1201
1494.0156 | 123.024 | -58.7814 | 64.1418 | -0.19852 | 0.013431 | 0.068037 | 0.069022 | 0.13142 | 0.00077755 | -0.0049411 | -0.023041 | -0.0044264 | 0.065332 | 0.057612 | 0.002713 | -0.0072738 | 63.9954 | 64.1327 | -2.8931 | -58.9005 | 64.1693 | -58.8181 | -58.8913 | -58.3603 | -0.19684 | -59.0836 | 64.1418 | 64.1006 | -58.9645 | -59.0149 | -0.036621 | -0.10986 | 0.027466 | 122.9141 | -0.11902 | -0.009156 | -0.14648 | -0.18311 | -0.23346 | 0 | 0.42114 | -0.30212 | -0.068664 | -0.041199 | 122.9507 | 122.7768 | 55.8884 | -123.0331 | 122.9233 | 122.8821 | 58.5846 | -123.1567
1495.0156 | 123.0011 | -58.7814 | 64.1281 | -0.091705 | 0.011081 | 0.068464 | 0.072226 | 0.13228 | 0.00077755 | -0.0040867 | 0.015106 | -0.0054944 | 0.065332 | 0.059748 | 0.0042084 | -0.0072738 | 64.0045 | 64.1235 | -3.2043 | -58.8776 | 64.1647 | -58.8364 | -58.905 | -58.3603 | -0.21515 | -59.0332 | 64.1602 | 64.1052 | -58.9371 | -58.9874 | -0.054932 | -0.1236 | 0.036621 | 122.905 | -0.09613 | 0.027466 | -0.1236 | -0.15564 | -0.20599 | 0.032043 | 0.42114 | -0.25177 | -0.045776 | -0.022888 | 122.9462 | 122.786 | 55.5771 | -123.0331 | 122.9416 | 122.8867 | 58.5663 | -123.1155
1496.0156 | 123.0286 | -58.7219 | 64.1647 | -0.168 | 0.0097989 | 0.067823 | 0.070517 | 0.1327 | -0.0013587 | -0.0051547 | -0.168 | -0.007417 | 0.061914 | 0.059107 | 0.0033538 | -0.0077012 | 63.9999 | 64.1281 | -3.6392 | -58.8226 | 64.2426 | -58.786 | -58.8959 | -58.3694 | -0.50354 | -58.96 | 64.2242 | 64.1464 | -58.8913 | -58.96 | -0.064087 | -0.17395 | 0.07782 | 122.85 | -0.10071 | 0.073242 | -0.16479 | -0.16937 | -0.23804 | 0.059509 | 0.35248 | -0.23804 | 0 | -0.018311 | 122.9645 | 122.7219 | 55.0827 | -123.0606 | 122.9462 | 122.8683 | 58.2184 | -123.1247
1497.0156 | 122.9874 | -58.7769 | 64.119 | 0.030365 | 0.014926 | 0.065901 | 0.071799 | 0.12886 | 0.0029137 | -0.0038731 | 0.09903 | -0.0072034 | 0.063623 | 0.060603 | 0.0067718 | -0.0085556 | 63.9587 | 64.0869 | -3.7674 | -58.9279 | 64.1785 | -58.8593 | -58.8959 | -58.4198 | -0.53101 | -59.0698 | 64.1739 | 64.1281 | -58.9508 | -59.0332 | -0.082398 | -0.11902 | 0.059509 | 122.8638 | -0.15106 | -0.032043 | -0.16022 | -0.17395 | -0.25635 | 0.054931 | 0.35705 | -0.29297 | -0.036621 | 0.009155 | 122.9553 | 122.7356 | 55.0095 | -123.0148 | 122.9507 | 122.905 | 58.2458 | -123.1522
1498.0156 | 123.0469 | -58.7997 | 64.1006 | -0.091705 | 0.014926 | 0.070387 | 0.072867 | 0.128 | 0.0020593 | -0.0045139 | 0.030365 | -0.0059216 | 0.064051 | 0.058894 | 0.0039948 | -0.0085556 | 63.9908 | 64.1006 | -2.9984 | -58.8959 | 64.1556 | -58.8638 | -58.9233 | -58.3969 | 0.16937 | -59.024 | 64.1556 | 64.0732 | -58.9645 | -59.0057 | -0.064087 | -0.1236 | 0.054932 | 122.9004 | -0.09613 | 0.027466 | -0.10986 | -0.1648 | -0.20599 | 0.054932 | 0.40283 | -0.2243 | -0.018311 | -0.027466 | 122.9553 | 122.7905 | 55.8014 | -123.024 | 122.9553 | 122.8729 | 58.9691 | -123.1064
1499.0156 | 122.9919 | -58.8043 | 64.1006 | 0.083771 | 0.014712 | 0.065687 | 0.070731 | 0.12907 | 0.00099115 | -0.0034457 | 0.076141 | -0.005708 | 0.06341 | 0.059748 | 0.0033538 | -0.0089828 | 63.9404 | 64.0778 | -3.0441 | -58.9554 | 64.1739 | -58.8547 | -58.9325 | -58.4381 | 0.13733 | -59.0744 | 64.151 | 64.0778 | -58.9828 | -59.0332 | -0.050354 | -0.12817 | 0.073242 | 122.8821 | -0.15106 | -0.022888 | -0.16022 | -0.17853 | -0.22888 | 0.050354 | 0.36621 | -0.27008 | -0.041199 | -0.022888 | 122.9782 | 122.7448 | 55.7602 | -123.0331 | 122.9553 | 122.8821 | 58.9417 | -123.1338
1500.0156 | 123.0057 | -58.7631 | 64.1235 | -0.091705 | 0.014926 | 0.067823 | 0.068808 | 0.13099 | 0.00056395 | -0.0032321 | -0.015411 | -0.0050672 | 0.064691 | 0.060603 | 0.0046356 | -0.0074876 | 63.9999 | 64.1373 | -3.1128 | -58.905 | 64.1602 | -58.8089 | -58.9096 | -58.3832 | 0.32501 | -59.0195 | 64.1556 | 64.1006 | -58.9325 | -59.024 | -0.045776 | -0.14648 | 0.036621 | 122.9004 | -0.14191 | 0.004578 | -0.1236 | -0.16937 | -0.26093 | 0.032044 | 0.37994 | -0.25635 | 0.004578 | -0.022888 | 122.9233 | 122.7631 | 55.6503 | -123.0331 | 122.9187 | 122.8638 | 59.0881 | -123.1476
1501.0156 | 122.9919 | -58.7769 | 64.1098 | 0.015106 | 0.014712 | 0.069105 | 0.071585 | 0.13249 | -0.0013587 | -0.0051547 | 0.16006 | -0.0059216 | 0.065759 | 0.060176 | 0.0031402 | -0.0059922 | 63.9267 | 64.0228 | -3.392 | -58.96 | 64.1922 | -58.8043 | -58.9233 | -58.4656 | 0.082397 | -59.0881 | 64.1556 | 64.1098 | -58.96 | -59.0103 | -0.027466 | -0.14649 | 0.082398 | 122.7997 | -0.18311 | -0.036621 | -0.18311 | -0.18311 | -0.23346 | 0.045777 | 0.31128 | -0.31128 | -0.07782 | 0 | 122.9691 | 122.7036 | 55.3848 | -123.0331 | 122.9324 | 122.8867 | 58.8593 | -123.1201
1502.0156 | 123.0698 | -58.7723 | 64.1281 | -0.20615 | 0.010653 | 0.069105 | 0.070303 | 0.12971 | -7.6852e-05 | -0.0053683 | -0.03067 | -0.005708 | 0.065759 | 0.059107 | 0.0057038 | -0.0072738 | 64.0045 | 64.1373 | -3.2684 | -58.8821 | 64.2242 | -58.7906 | -58.8913 | -58.3603 | 0.009155 | -58.9874 | 64.1602 | 64.151 | -58.8776 | -59.0012 | -0.01831 | -0.11902 | 0.09613 | 122.9095 | -0.10986 | 0.009155 | -0.1236 | -0.10529 | -0.22888 | 0.032043 | 0.41199 | -0.21515 | 0.013733 | 0.022888 | 122.9965 | 122.7768 | 55.5038 | -123.0194 | 122.9324 | 122.9233 | 58.7814 | -123.1293
1503.0156 | 122.9965 | -58.754 | 64.1556 | 0.083771 | 0.014285 | 0.066328 | 0.067313 | 0.12993 | -0.00029045 | -0.0036595 | 0.23636 | -0.0067762 | 0.065332 | 0.059321 | 0.0048492 | -0.0081284 | 63.9771 | 64.0778 | -3.4744 | -58.905 | 64.2059 | -58.8089 | -58.8593 | -58.4244 | -0.14191 | -59.0698 | 64.2151 | 64.119 | -58.9279 | -58.9691 | -0.054932 | -0.10529 | 0.050354 | 122.8317 | -0.15106 | -0.045776 | -0.17853 | -0.17395 | -0.21515 | 0.059509 | 0.32959 | -0.31586 | -0.10071 | -0.036621 | 122.9599 | 122.731 | 55.2795 | -123.0148 | 122.9691 | 122.8729 | 58.6121 | -123.1247
1504.0156 | 123.0652 | -58.699 | 64.1739 | -0.19089 | 0.014071 | 0.067823 | 0.071799 | 0.128 | 0.0016321 | -0.0017369 | 0.015106 | -0.0050672 | 0.065546 | 0.058467 | 0.0018584 | -0.0087692 | 64.0778 | 64.1785 | -3.6026 | -58.8364 | 64.238 | -58.7631 | -58.8455 | -58.3237 | -0.25635 | -58.9417 | 64.2334 | 64.1602 | -58.8776 | -58.9279 | -0.064087 | -0.14648 | 0.064087 | 122.8775 | -0.13733 | 0.009155 | -0.09613 | -0.17853 | -0.22888 | 0.059509 | 0.37537 | -0.24261 | -0.013733 | -0.013733 | 122.937 | 122.7768 | 55.0964 | -123.0194 | 122.9324 | 122.8592 | 58.4427 | -123.1018
1505.0156 | 122.9828 | -58.7128 | 64.2059 | 0.030365 | 0.014712 | 0.068037 | 0.071799 | 0.12928 | 0.0014185 | -0.0032321 | 0.14481 | -0.005708 | 0.064478 | 0.058467 | 0.0048492 | -0.0072738 | 64.032 | 64.1418 | -4.0924 | -58.8593 | 64.2517 | -58.7494 | -58.8226 | -58.3878 | -0.59052 | -58.992 | 64.2014 | 64.1876 | -58.8821 | -58.9645 | -0.036621 | -0.10986 | 0.045776 | 122.8546 | -0.14648 | -0.036621 | -0.17395 | -0.16937 | -0.25177 | -0.004578 | 0.32501 | -0.27923 | -0.027465 | -0.018311 | 122.9645 | 122.7448 | 54.6204 | -123.0286 | 122.9141 | 122.9004 | 58.1223 | -123.1705
1506.0156 | 123.0515 | -58.6716 | 64.2105 | -0.03067 | 0.013431 | 0.065901 | 0.073294 | 0.1295 | 0.0029137 | -0.0032321 | 0.0074766 | -0.0076306 | 0.064478 | 0.058467 | 0.0035674 | -0.0085556 | 64.1052 | 64.2151 | -4.3625 | -58.7997 | 64.2975 | -58.7173 | -58.786 | -58.2916 | -0.48523 | -58.8913 | 64.2288 | 64.2197 | -58.8409 | -58.9142 | -0.045776 | -0.11444 | 0.086975 | 122.8867 | -0.12817 | -0.013733 | -0.10528 | -0.16937 | -0.24262 | 0.018311 | 0.37994 | -0.21973 | 0.022889 | 0.009156 | 122.9691 | 122.7768 | 54.3091 | -122.9965 | 122.9004 | 122.8912 | 58.1863 | -123.1247
1507.0156 | 122.9141 | -58.7036 | 64.1785 | 0.045624 | 0.017276 | 0.065901 | 0.070944 | 0.13014 | 0.00035035 | -0.0047275 | 0.20584 | -0.00464 | 0.063623 | 0.061244 | 0.004422 | -0.0074876 | 63.9908 | 64.0732 | -3.6072 | -58.873 | 64.3066 | -58.7585 | -58.8364 | -58.3649 | -0.64087 | -59.2117 | 64.2059 | 64.119 | -58.9005 | -58.9508 | -0.054932 | -0.13275 | 0.12817 | 122.7768 | -0.16937 | -0.036621 | -0.18768 | -0.19684 | -0.24719 | 0.027466 | 0.33874 | -0.50812 | -0.26093 | -0.059509 | 123.0103 | 122.6944 | 55.0964 | -123.0148 | 122.9095 | 122.8226 | 58.0627 | -123.1293
1508.0156 | 122.9965 | -58.6853 | 64.2334 | -0.068817 | 0.015353 | 0.067182 | 0.07479 | 0.13121 | -0.00093145 | -0.0049411 | 0.030365 | -0.0031446 | 0.067255 | 0.059962 | 0.0048492 | -0.0079148 | 64.1602 | 64.2288 | -3.653 | -58.7952 | 64.2929 | -58.699 | -58.7585 | -58.2779 | -1.0162 | -58.9005 | 64.2792 | 64.238 | -58.8318 | -58.8913 | -0.013733 | -0.073242 | 0.05951 | 122.9141 | -0.10986 | -0.036621 | -0.073242 | -0.14648 | -0.20599 | 0.045777 | 0.40741 | -0.21515 | -0.009156 | 0.004578 | 122.9782 | 122.8455 | 55.0323 | -122.9919 | 122.9645 | 122.9233 | 57.6691 | -123.1247
1509.0156 | 123.0011 | -58.699 | 64.2151 | -0.0383 | 0.015353 | 0.068891 | 0.072226 | 0.13014 | -0.00029045 | -0.0025913 | 0.083771 | -0.005708 | 0.0664 | 0.062739 | 0.0050628 | -0.0079148 | 64.0594 | 64.1602 | -3.6484 | -58.8318 | 64.2517 | -58.7357 | -58.8455 | -58.3466 | -0.56763 | -58.9554 | 64.238 | 64.183 | -58.873 | -58.9233 | -0.036621 | -0.14648 | 0.036621 | 122.8592 | -0.13275 | 0.013733 | -0.15564 | -0.17395 | -0.2243 | 0.022888 | 0.35248 | -0.25635 | -0.032043 | -0.032044 | 122.9507 | 122.7585 | 55.0507 | -123.0606 | 122.937 | 122.8821 | 58.1314 | -123.1384
1510.0156 | 123.0286 | -58.6624 | 64.2105 | -0.10696 | 0.01514 | 0.067823 | 0.072012 | 0.12758 | 0.0022729 | -0.0038731 | -0.10696 | -0.0067762 | 0.067682 | 0.058894 | 0.0035674 | -0.0074876 | 64.1281 | 64.2197 | -4.0329 | -58.9096 | 64.2517 | -58.7173 | -58.8318 | -58.3054 | -0.54932 | -58.8959 | 64.2654 | 64.2197 | -58.8409 | -58.8821 | -0.054931 | -0.16937 | 0.041199 | 122.8821 | -0.24719 | -0.07782 | -0.082397 | -0.17853 | -0.21973 | 0.054932 | 0.35706 | -0.23346 | -0.013733 | 0.009156 | 122.9141 | 122.7905 | 54.6295 | -123.0423 | 122.9279 | 122.8821 | 58.1131 | -123.0927
1511.0156 | 122.9782 | -58.6945 | 64.2197 | 0.037994 | 0.014499 | 0.068037 | 0.071799 | 0.128 | 0.00013675 | -0.0036595 | 0.060883 | -0.0052808 | 0.063196 | 0.059321 | 0.0050628 | -0.0068466 | 64.0549 | 64.1327 | -4.3304 | -58.8226 | 64.2746 | -58.7265 | -58.8135 | -58.4106 | -0.33417 | -58.9828 | 64.2746 | 64.2059 | -58.8684 | -58.9188 | -0.032043 | -0.11902 | 0.054931 | 122.8271 | -0.12817 | -0.009155 | -0.16479 | -0.17395 | -0.2243 | 0.054931 | 0.28381 | -0.28839 | -0.064087 | -0.013733 | 122.9691 | 122.7493 | 54.364 | -123.0331 | 122.9691 | 122.9004 | 58.3603 | -123.1384
1512.0156 | 123.0286 | -58.6349 | 64.2197 | -0.061188 | 0.013431 | 0.068037 | 0.072012 | 0.13313 | -7.6852e-05 | -0.0036595 | -0.068817 | -0.0059216 | 0.064264 | 0.056971 | 0.0050628 | -0.0096238 | 64.1235 | 64.238 | -4.2572 | -58.7769 | 64.2975 | -58.699 | -58.786 | -58.2779 | -0.064087 | -58.905 | 64.2517 | 64.2197 | -58.8455 | -58.9142 | -0.064087 | -0.15106 | 0.077819 | 122.8729 | -0.14191 | 0.009156 | -0.096131 | -0.21057 | -0.27924 | 0.032043 | 0.35706 | -0.27008 | 0.009156 | 0 | 122.9324 | 122.7585 | 54.3777 | -123.0057 | 122.8867 | 122.8546 | 58.5709 | -123.1339
1513.0156 | 122.9965 | -58.6533 | 64.238 | -0.023041 | 0.01279 | 0.069532 | 0.071372 | 0.12886 | -7.6852e-05 | -0.0049411 | 0.12192 | -0.007417 | 0.066828 | 0.059748 | 0.0035674 | -0.0081284 | 64.1052 | 64.1968 | -4.3121 | -58.7769 | 64.2975 | -58.7173 | -58.7585 | -58.3466 | -0.23804 | -58.9417 | 64.2883 | 64.2288 | -58.8501 | -58.8776 | -0.064087 | -0.10529 | 0.059509 | 122.85 | -0.1236 | -0.01831 | -0.13275 | -0.19684 | -0.2243 | 0.050354 | 0.3067 | -0.28839 | -0.064087 | -0.009155 | 122.9507 | 122.7585 | 54.3411 | -122.9965 | 122.9416 | 122.8821 | 58.4152 | -123.1155
1514.0156 | 123.0148 | -58.6349 | 64.2288 | -0.27481 | 0.016849 | 0.066328 | 0.071158 | 0.13121 | 0.00035035 | -0.0053683 | 0.045624 | -0.0061352 | 0.062555 | 0.06103 | 0.0042084 | -0.0074876 | 64.151 | 64.2746 | -4.2435 | -58.7494 | 64.3204 | -58.6899 | -58.7631 | -58.2687 | -0.19684 | -58.8867 | 64.2975 | 64.27 | -58.7997 | -58.8455 | -0.054931 | -0.12817 | 0.091553 | 122.9095 | -0.11444 | 0.013733 | -0.07782 | -0.16479 | -0.21057 | 0.068664 | 0.36621 | -0.25177 | -0.041199 | 0.041199 | 122.9553 | 122.7859 | 54.3915 | -122.9919 | 122.9324 | 122.905 | 58.4381 | -123.0743
1515.0156 | 122.9691 | -58.6487 | 64.2471 | 0.12192 | 0.018985 | 0.066969 | 0.069663 | 0.12843 | 0.0020593 | -0.0036595 | 0.18295 | -0.008058 | 0.065973 | 0.060389 | 0.0046356 | -0.0064194 | 64.0503 | 64.1647 | -4.4724 | -58.7997 | 64.3295 | -58.7173 | -58.7814 | -58.3374 | -0.67291 | -58.9279 | 64.3021 | 64.2654 | -58.8455 | -58.9005 | -0.068664 | -0.13275 | 0.082398 | 122.8134 | -0.15106 | -0.018311 | -0.19684 | -0.19684 | -0.25177 | 0.054932 | 0.31128 | -0.27923 | -0.027465 | 0.018311 | 122.9782 | 122.699 | 54.1763 | -123.0286 | 122.9507 | 122.9141 | 57.9758 | -123.1476
1516.0156 | 123.0377 | -58.6533 | 64.2517 | -0.17563 | 0.01279 | 0.067182 | 0.071799 | 0.13099 | 0.0016321 | -0.0038731 | -0.038299 | -0.0067762 | 0.067041 | 0.060389 | 0.0039948 | -0.0072738 | 64.1235 | 64.2426 | -4.0787 | -58.7906 | 64.3112 | -58.7265 | -58.7769 | -58.2962 | -0.29755 | -58.8776 | 64.27 | 64.238 | -58.8181 | -58.8913 | -0.073242 | -0.1236 | 0.059509 | 122.8958 | -0.13733 | -0.013733 | -0.12817 | -0.16479 | -0.23804 | 0.018311 | 0.35705 | -0.2243 | 0.013733 | -0.013733 | 122.9645 | 122.7768 | 54.5746 | -123.0286 | 122.9233 | 122.8912 | 58.3557 | -123.143
1517.0156 | 122.9874 | -58.6578 | 64.2471 | -0.053558 | 0.01578 | 0.070387 | 0.07009 | 0.13014 | 0.00056395 | -0.0032321 | 0.076141 | -0.0067762 | 0.062769 | 0.058467 | 0.0031402 | -0.0085556 | 64.1327 | 64.238 | -3.9597 | -58.7952 | 64.3387 | -58.6899 | -58.754 | -58.2962 | -0.56763 | -58.9005 | 64.2792 | 64.2563 | -58.8226 | -58.8821 | -0.032043 | -0.09613 | 0.091553 | 122.8958 | -0.13733 | -0.041199 | -0.11444 | -0.16479 | -0.2243 | 0.032044 | 0.36163 | -0.24262 | -0.018311 | 0.009156 | 122.9965 | 122.7905 | 54.6982 | -123.0011 | 122.937 | 122.9141 | 58.0902 | -123.1293
1518.0156 | 123.0423 | -58.6578 | 64.2197 | -0.14511 | 0.013217 | 0.066328 | 0.073721 | 0.12886 | 0.0012047 | -0.0043003 | -0.0077819 | -0.008058 | 0.063837 | 0.059321 | 0.0033538 | -0.0087692 | 64.1052 | 64.2105 | -3.3142 | -58.7952 | 64.2746 | -58.7128 | -58.7906 | -58.2962 | -0.39825 | -58.9462 | 64.27 | 64.1785 | -58.8455 | -58.9096 | -0.054932 | -0.13275 | 0.054931 | 122.8683 | -0.13733 | -0.004578 | -0.11444 | -0.18768 | -0.25177 | 0.050354 | 0.36163 | -0.28839 | -0.036621 | -0.041199 | 122.9324 | 122.7631 | 55.3436 | -123.0103 | 122.9279 | 122.8363 | 58.2596 | -123.1293
1519.0156 | 123.0148 | -58.6945 | 64.2242 | -0.00015269 | 0.015567 | 0.066328 | 0.071158 | 0.1295 | 0.00099115 | -0.0049411 | 0.09903 | -0.0052808 | 0.064478 | 0.059107 | 0.0033538 | -0.0070602 | 64.064 | 64.1693 | -3.2684 | -58.8455 | 64.2792 | -58.7265 | -58.8181 | -58.3466 | -0.32959 | -58.9691 | 64.2654 | 64.2242 | -58.8547 | -58.9233 | -0.032043 | -0.1236 | 0.054932 | 122.8638 | -0.15106 | -0.027466 | -0.16022 | -0.16022 | -0.22888 | 0.041199 | 0.3479 | -0.27466 | -0.045776 | 0 | 122.9736 | 122.7585 | 55.426 | -123.0423 | 122.9599 | 122.9187 | 58.3649 | -123.1476
1520.0156 | 123.0194 | -58.6212 | 64.2471 | -0.15274 | 0.011294 | 0.067823 | 0.07009 | 0.12822 | 0.00077755 | -0.0049411 | 0.030365 | -0.006349 | 0.060633 | 0.060816 | 0.0033538 | -0.0072738 | 64.1373 | 64.2471 | -3.4698 | -58.7494 | 64.3158 | -58.6945 | -58.8089 | -58.287 | -0.64087 | -58.8593 | 64.3021 | 64.2517 | -58.8043 | -58.8593 | -0.073242 | -0.18768 | 0.068665 | 122.8683 | -0.12817 | 0.059509 | -0.10986 | -0.18311 | -0.23804 | 0.054932 | 0.33417 | -0.23804 | 0 | 0.004578 | 122.937 | 122.7585 | 55.1514 | -123.056 | 122.9233 | 122.8729 | 57.9803 | -123.1064
1521.0156 | 122.9782 | -58.6807 | 64.2242 | -0.00015269 | 0.015353 | 0.065473 | 0.070517 | 0.13035 | -0.00029045 | -0.0025913 | 0.16006 | -0.0054944 | 0.065759 | 0.059748 | 0.00549 | -0.0074876 | 64.0503 | 64.1418 | -3.7537 | -58.8226 | 64.3112 | -58.7402 | -58.8089 | -58.374 | -0.60883 | -58.9508 | 64.2654 | 64.2151 | -58.8501 | -58.8867 | -0.059509 | -0.12817 | 0.086975 | 122.8226 | -0.14191 | -0.013733 | -0.17395 | -0.16937 | -0.20599 | 0.041199 | 0.3067 | -0.27008 | -0.064087 | -0.009155 | 122.9919 | 122.731 | 54.9271 | -123.0331 | 122.9462 | 122.8958 | 58.0719 | -123.111
1522.0156 | 123.0377 | -58.6624 | 64.2288 | -0.076447 | 0.015353 | 0.066755 | 0.072012 | 0.13035 | 0.00013675 | -0.0034457 | -0.038299 | -0.0069898 | 0.065546 | 0.060389 | 0.0037812 | -0.0094102 | 64.1144 | 64.2334 | -3.0441 | -58.9188 | 64.27 | -58.7265 | -58.8226 | -58.2916 | -0.40741 | -58.9005 | 64.27 | 64.2242 | -58.8364 | -58.8959 | -0.064086 | -0.16022 | 0.041199 | 122.8958 | -0.25635 | -0.09613 | -0.11444 | -0.17395 | -0.23346 | 0.041199 | 0.37079 | -0.23804 | -0.004578 | -0.004578 | 122.9324 | 122.7768 | 55.6183 | -123.0515 | 122.9324 | 122.8867 | 58.255 | -123.1247
1523.0156 | 122.9782 | -58.6807 | 64.2014 | -0.023041 | 0.01578 | 0.067396 | 0.071372 | 0.12971 | 0.0020593 | -0.0053683 | 0.060883 | -0.0050672 | 0.06341 | 0.060176 | 0.0029266 | -0.0064194 | 64.0823 | 64.1922 | -2.9663 | -58.8318 | 64.2746 | -58.7402 | -58.8226 | -58.3374 | -0.55389 | -58.9417 | 64.2746 | 64.2059 | -58.8455 | -58.9233 | -0.059509 | -0.14191 | 0.073242 | 122.8729 | -0.15106 | -0.009155 | -0.11902 | -0.16479 | -0.24262 | 0.073242 | 0.34332 | -0.26093 | -0.01831 | 0.004578 | 122.9553 | 122.7631 | 55.7144 | -123.024 | 122.9553 | 122.8867 | 58.1268 | -123.1247
1524.0156 | 123.0652 | -58.6716 | 64.2014 | -0.12985 | 0.014712 | 0.06825 | 0.068594 | 0.12971 | -0.0019995 | -0.0034457 | -0.015411 | -0.0072034 | 0.062769 | 0.061671 | 0.0035674 | -0.0091966 | 64.1098 | 64.238 | -2.9297 | -58.7906 | 64.3021 | -58.7219 | -58.8226 | -58.2687 | -0.43488 | -58.9279 | 64.2654 | 64.2105 | -58.8226 | -58.9142 | -0.050354 | -0.15106 | 0.10071 | 122.9095 | -0.11902 | 0.032044 | -0.091553 | -0.15106 | -0.24262 | 0.064087 | 0.40283 | -0.25635 | -0.013732 | 0.009155 | 122.9736 | 122.7814 | 55.7419 | -123.024 | 122.937 | 122.8821 | 58.2367 | -123.1155
1525.0156 | 122.9599 | -58.7036 | 64.2197 | -0.0077822 | 0.013217 | 0.066541 | 0.069663 | 0.13142 | 0.0012047 | -0.0021641 | 0.12192 | -0.0061352 | 0.061273 | 0.059535 | 0.0033538 | -0.0098374 | 64.0549 | 64.1876 | -2.6779 | -58.8364 | 64.27 | -58.699 | -58.8043 | -58.3694 | -0.97504 | -58.96 | 64.2517 | 64.2151 | -58.8638 | -58.9188 | 0.004577 | -0.10071 | 0.050354 | 122.8912 | -0.13275 | -0.032044 | -0.16479 | -0.16022 | -0.21515 | 0.032043 | 0.33417 | -0.25635 | -0.041199 | -0.004578 | 122.9736 | 122.7585 | 56.0257 | -123.024 | 122.9553 | 122.9187 | 57.7286 | -123.1384
1526.0156 | 123.0331 | -58.6395 | 64.2242 | -0.13748 | 0.014071 | 0.065473 | 0.073081 | 0.12822 | 0.0012047 | -0.0049411 | -0.12222 | -0.0065626 | 0.064905 | 0.056544 | 0.0039948 | -0.0079148 | 64.1098 | 64.2471 | -3.241 | -58.7723 | 64.3021 | -58.7036 | -58.7769 | -58.2916 | -0.94299 | -58.8821 | 64.2975 | 64.238 | -58.7997 | -58.8684 | -0.064087 | -0.13733 | 0.07782 | 122.8867 | -0.13275 | 0.004577 | -0.11444 | -0.16022 | -0.22888 | 0.073242 | 0.3479 | -0.24262 | -0.013733 | 0.013733 | 122.9416 | 122.7493 | 55.3986 | -123.0011 | 122.937 | 122.8775 | 57.6965 | -123.0927
1527.0156 | 122.9736 | -58.7082 | 64.2242 | 0.015106 | 0.01514 | 0.06761 | 0.071799 | 0.13099 | 0.0014185 | -0.0030185 | 0.060883 | -0.0052808 | 0.064905 | 0.057398 | 0.0050628 | -0.0068466 | 64.0686 | 64.183 | -2.8656 | -58.8226 | 64.2929 | -58.7448 | -58.7997 | -58.3557 | -0.94299 | -58.9508 | 64.2517 | 64.1876 | -58.8226 | -58.9142 | -0.036621 | -0.091553 | 0.068665 | 122.8912 | -0.11444 | -0.022888 | -0.15564 | -0.11444 | -0.20599 | 0.027466 | 0.35248 | -0.24262 | -0.036621 | -0.036621 | 123.0011 | 122.7768 | 55.8426 | -123.024 | 122.9599 | 122.8958 | 57.7652 | -123.1384
1528.0156 | 123.0423 | -58.7036 | 64.1739 | -0.10696 | 0.013858 | 0.067823 | 0.07009 | 0.13014 | 0.0052637 | -0.0034457 | -0.015411 | -0.005708 | 0.065332 | 0.056758 | 0.0042084 | -0.0094102 | 63.9404 | 64.2975 | -2.6001 | -58.8364 | 64.2563 | -58.7494 | -58.8547 | -58.3511 | -0.63171 | -58.9417 | 64.2242 | 64.1968 | -58.8821 | -58.9371 | -0.045777 | -0.15106 | 0.082398 | 123.0011 | -0.13275 | 0.01831 | -0.23346 | -0.17853 | -0.23346 | 0.050354 | 0.35248 | -0.23804 | -0.004577 | 0.022888 | 122.9599 | 122.644 | 56.1035 | -123.0286 | 122.9279 | 122.9004 | 58.0719 | -123.111
1529.0156 | 122.9599 | -58.754 | 64.1647 | 0.060882 | 0.014285 | 0.065687 | 0.073294 | 0.1295 | 0.00013675 | -0.0043003 | 0.16769 | -0.0076306 | 0.064905 | 0.057398 | 0.0052764 | -0.0062058 | 63.9908 | 64.0503 | -2.5726 | -58.905 | 64.2288 | -58.786 | -58.8867 | -58.461 | -0.52185 | -59.0424 | 64.2151 | 64.1647 | -58.9325 | -58.9783 | -0.032044 | -0.13275 | 0.064087 | 122.8043 | -0.15106 | -0.01831 | -0.17395 | -0.17853 | -0.2243 | 0.050354 | 0.29297 | -0.28839 | -0.064087 | 0 | 122.9828 | 122.7448 | 56.1813 | -123.0515 | 122.9691 | 122.9187 | 58.2321 | -123.143
1530.0156 | 123.0286 | -58.7128 | 64.1602 | -0.17563 | 0.014071 | 0.068464 | 0.072653 | 0.12993 | -0.0015723 | -0.0040867 | -0.16037 | -0.0059216 | 0.062128 | 0.059107 | 0.0031402 | -0.0064194 | 64.0366 | 64.1281 | -2.4445 | -58.8501 | 64.2334 | -58.7723 | -58.8593 | -58.3969 | -0.21057 | -58.9554 | 64.2334 | 64.1602 | -58.905 | -58.9828 | -0.059509 | -0.14648 | 0.073242 | 122.8409 | -0.13733 | 0.009155 | -0.1236 | -0.19226 | -0.27008 | 0.073242 | 0.31586 | -0.24261 | 0.027466 | 0 | 122.9462 | 122.7493 | 56.2683 | -123.0194 | 122.9462 | 122.8729 | 58.5022 | -123.143
1531.0156 | 123.0103 | -58.7585 | 64.1556 | 0.015106 | 0.016635 | 0.067396 | 0.069876 | 0.12928 | 0.0033411 | -0.0045139 | 0.14481 | -0.0050672 | 0.064905 | 0.058039 | 0.0037812 | -0.0087692 | 63.9999 | 64.1281 | -2.623 | -58.8776 | 64.2059 | -58.7814 | -58.8593 | -58.4244 | -0.59509 | -59.0286 | 64.2151 | 64.1556 | -58.9279 | -58.96 | -0.022888 | -0.10071 | 0.050354 | 122.8867 | -0.11902 | -0.01831 | -0.15564 | -0.16937 | -0.20142 | 0.059509 | 0.33417 | -0.27008 | -0.068664 | 0 | 122.9645 | 122.7585 | 56.1356 | -123.0148 | 122.9736 | 122.9141 | 58.1635 | -123.1155
1532.0156 | 123.0469 | -58.7265 | 64.1418 | -0.22141 | 0.013217 | 0.067823 | 0.071372 | 0.1327 | 0.00099115 | -0.0038731 | -0.053558 | -0.0044264 | 0.064051 | 0.058467 | 0.0039948 | -0.0074876 | 64.0411 | 64.1785 | -2.5314 | -58.8593 | 64.238 | -58.7906 | -58.8638 | -58.3878 | -0.59967 | -58.96 | 64.1968 | 64.1647 | -58.9188 | -58.9645 | -0.064087 | -0.13733 | 0.09613 | 122.905 | -0.13275 | 0.004578 | -0.10071 | -0.19226 | -0.23804 | 0.054931 | 0.33874 | -0.23346 | 0.004578 | 0.022888 | 122.9645 | 122.7676 | 56.1951 | -123.0057 | 122.9233 | 122.8912 | 58.1268 | -123.1064
1533.0156 | 123.0881 | -58.6945 | 64.1373 | 0.015106 | 0.0044583 | -0.03557 | 0.068381 | 0.12907 | -0.0071265 | -0.0096409 | 0.16006 | -0.0078442 | 0.059992 | 0.058467 | -0.0077546 | -0.0051376 | 63.9908 | 64.2014 | -2.6093 | -58.8455 | 64.2242 | -58.7494 | -58.8364 | -58.3649 | -0.89264 | -58.8776 | 64.1647 | 64.1373 | -58.8821 | -58.9417 | -0.054932 | -0.14191 | 0.086975 | 122.8958 | -0.15106 | -0.009155 | -0.14648 | -0.18768 | -0.24719 | 0.027466 | 0.32959 | -0.18311 | 0.064087 | 0 | 122.9187 | 122.6852 | 56.0852 | -122.9736 | 122.8592 | 122.8317 | 57.8018 | -123.0789
1534.0156 | 123.0423 | -58.754 | 64.1281 | -0.091705 | 0.013644 | 0.068037 | 0.072226 | 0.13014 | 0.0022729 | -0.0049411 | -0.00015237 | -0.0059216 | 0.066614 | 0.05868 | 0.0050628 | -0.0070602 | 64.064 | 64.1373 | -2.6642 | -58.8593 | 64.2288 | -58.7814 | -58.8821 | -58.4702 | -1.0071 | -58.9325 | 64.1968 | 64.1235 | -58.9371 | -58.9737 | -0.027466 | -0.12817 | 0.10071 | 122.8912 | -0.10529 | 0.022888 | -0.064087 | -0.18311 | -0.21973 | 0.068664 | 0.28381 | -0.17853 | 0.041199 | -0.004578 | 122.9828 | 122.818 | 56.0898 | -123.0103 | 122.9507 | 122.8775 | 57.7469 | -123.1018
1535.0156 | 122.9645 | -58.7585 | 64.151 | 0.037994 | 0.013003 | 0.068037 | 0.071799 | 0.13078 | 0.0012047 | -0.0047275 | 0.083771 | -0.007417 | 0.064691 | 0.05868 | 0.0035674 | -0.0079148 | 64.0045 | 64.1144 | -2.4902 | -58.9005 | 64.2197 | -58.8135 | -58.8867 | -58.4564 | -0.90179 | -59.0332 | 64.183 | 64.1556 | -58.9096 | -58.9828 | -0.054932 | -0.12817 | 0.068665 | 122.8729 | -0.14191 | -0.013733 | -0.14648 | -0.15106 | -0.2243 | 0.032043 | 0.30212 | -0.27466 | -0.050354 | 0.004578 | 122.9782 | 122.7631 | 56.2683 | -123.0377 | 122.9416 | 122.9141 | 57.8568 | -123.1338
1536.0156 | 123.0011 | -58.7128 | 64.1785 | -0.19089 | 0.01279 | 0.069319 | 0.073508 | 0.13035 | -0.0015723 | -0.0025913 | -0.12985 | -0.007417 | 0.064905 | 0.059107 | 0.0018584 | -0.0074876 | 64.0137 | 64.1418 | -2.6596 | -58.8455 | 64.2517 | -58.7631 | -58.8455 | -58.3923 | -1.1948 | -58.96 | 64.238 | 64.183 | -58.8959 | -58.9371 | -0.050354 | -0.13275 | 0.073242 | 122.8546 | -0.13275 | 0 | -0.16479 | -0.1831 | -0.2243 | 0.059509 | 0.32044 | -0.24719 | -0.022888 | 0.004577 | 122.9645 | 122.7264 | 56.0532 | -123.024 | 122.9507 | 122.8958 | 57.518 | -123.1155
1537.0156 | 123.0331 | -58.7219 | 64.1464 | -0.076447 | 0.014712 | 0.068891 | 0.072012 | 0.13014 | 0.0014185 | -0.0047275 | -0.19089 | -0.0065626 | 0.064478 | 0.059321 | 0.0050628 | -0.0074876 | 64.0549 | 64.1739 | -2.5589 | -58.9554 | 64.2059 | -58.7769 | -58.873 | -58.3832 | -1.2726 | -58.9554 | 64.2059 | 64.1418 | -58.9142 | -58.9371 | -0.054931 | -0.15106 | 0.05951 | 122.8958 | -0.23346 | -0.082397 | -0.091552 | -0.19226 | -0.21515 | 0.05951 | 0.33875 | -0.23346 | -0.01831 | -0.004577 | 122.9279 | 122.7768 | 56.163 | -123.0194 | 122.9279 | 122.8638 | 57.4493 | -123.0835
1538.0156 | 123.1384 | -58.7265 | 64.0778 | 0.16006 | 0.011508 | 0.071027 | 0.070303 | 0.12864 | -0.0028541 | -0.0047275 | 0.30502 | -0.0086988 | 0.063837 | 0.057826 | 0.0022858 | -0.0085556 | 64.0137 | 64.1693 | -2.8656 | -58.8547 | 64.1647 | -58.7906 | -58.8638 | -58.342 | -1.3 | -58.9233 | 64.1098 | 64.0869 | -58.9096 | -58.96 | -0.064087 | -0.13733 | 0.086975 | 122.8958 | -0.12817 | 0.009156 | -0.064087 | -0.18311 | -0.23346 | 0.032043 | 0.38452 | -0.19684 | 0.036621 | 0.009155 | 122.8912 | 122.7402 | 55.8609 | -122.9416 | 122.8363 | 122.8134 | 57.4265 | -123.0377
1539.0156 | 123.0148 | -58.7402 | 64.1556 | -0.11459 | 0.015567 | 0.069105 | 0.073081 | 0.13142 | 0.0029137 | -0.0036595 | -0.015411 | -0.0052808 | 0.064478 | 0.059748 | 0.0035674 | -0.0098374 | 64.0778 | 64.1739 | -2.7237 | -58.8593 | 64.2288 | -58.754 | -58.8501 | -58.3786 | -1.149 | -58.9783 | 64.1922 | 64.1693 | -58.8776 | -58.9645 | -0.013733 | -0.10986 | 0.073242 | 122.9141 | -0.11902 | -0.009155 | -0.07782 | -0.13733 | -0.22431 | 0.036621 | 0.36163 | -0.23804 | -0.013732 | 0.013733 | 122.9691 | 122.818 | 56.0165 | -123.0057 | 122.9324 | 122.9095 | 57.5912 | -123.1201
1540.0156 | 123.0377 | -58.7082 | 64.1922 | -0.16037 | 0.011294 | 0.068037 | 0.069876 | 0.12971 | -0.0028541 | -0.0057957 | -0.15274 | -0.0078442 | 0.064264 | 0.05868 | 0.002713 | -0.0081284 | 64.0228 | 64.1602 | -2.6596 | -58.8547 | 64.2746 | -58.7723 | -58.8318 | -58.3923 | -1.1169 | -58.9325 | 64.2609 | 64.2105 | -58.8867 | -58.9233 | -0.064087 | -0.1236 | 0.082397 | 122.8683 | -0.14648 | -0.022888 | -0.16937 | -0.17853 | -0.21515 | 0.068664 | 0.31586 | -0.2243 | -0.009155 | 0.01831 | 122.9828 | 122.731 | 56.0486 | -123.024 | 122.9691 | 122.9187 | 57.5912 | -123.1155
1541.0156 | 123.0011 | -58.7082 | 64.1922 | -0.00015269 | 0.015567 | 0.067396 | 0.069876 | 0.13206 | 0.00099115 | -0.0055821 | 0.045624 | -0.006349 | 0.06341 | 0.058039 | 0.0037812 | -0.0091966 | 64.0411 | 64.1602 | -2.9297 | -58.8501 | 64.2334 | -58.7769 | -58.8226 | -58.3786 | -1.2909 | -58.9874 | 64.1968 | 64.1785 | -58.8867 | -58.9462 | -0.068664 | -0.11444 | 0.041198 | 122.8683 | -0.14191 | -0.027466 | -0.15106 | -0.17853 | -0.23804 | 0.004577 | 0.32959 | -0.27924 | -0.041199 | -0.013733 | 122.9416 | 122.7493 | 55.7785 | -123.0148 | 122.905 | 122.8867 | 57.4173 | -123.1384
1542.0156 | 123.024 | -58.7402 | 64.1647 | -0.20615 | 0.012149 | 0.068678 | 0.071585 | 0.12843 | -0.0013587 | -0.0060093 | -0.19089 | -0.0065626 | 0.061914 | 0.057398 | 0.0024994 | -0.0081284 | 64.0182 | 64.1602 | -2.5726 | -58.8501 | 64.2426 | -58.7814 | -58.8501 | -58.3694 | -1.2085 | -58.9554 | 64.1922 | 64.151 | -58.905 | -58.9828 | -0.041199 | -0.10986 | 0.07782 | 122.9004 | -0.10986 | 0 | -0.14648 | -0.16479 | -0.24262 | 0.027466 | 0.37079 | -0.21515 | 0.027466 | -0.013733 | 122.9828 | 122.7585 | 56.1676 | -123.0148 | 122.9324 | 122.8912 | 57.5317 | -123.1476
1543.0156 | 123.143 | -58.6487 | 64.1464 | -0.10696 | 0.0048855 | -0.035784 | 0.069235 | 0.12843 | -0.0090491 | -0.0051547 | 0.030365 | -0.0067762 | 0.062342 | 0.057612 | 0.00036322 | -0.0072738 | 64.0915 | 64.2838 | -2.4399 | -58.7906 | 64.2197 | -58.7448 | -58.8181 | -58.2825 | -0.97961 | -58.7952 | 64.1876 | 64.1235 | -58.8364 | -58.8913 | -0.09613 | -0.16937 | 0.073243 | 122.9324 | -0.14191 | 0.027466 | -0.054931 | -0.18768 | -0.24261 | 0.041199 | 0.36621 | -0.14648 | 0.09613 | -0.022888 | 122.8683 | 122.7402 | 56.2088 | -122.9645 | 122.8363 | 122.7722 | 57.6691 | -123.0377
1544.0156 | 123.0011 | -58.6533 | 64.2242 | -0.22903 | 0.012362 | 0.071027 | 0.069235 | 0.12993 | -0.00093145 | -0.0079319 | -0.12222 | -0.0082716 | 0.064478 | 0.058039 | 0.0022858 | -0.0081284 | 64.3112 | 63.9862 | -3.1357 | -58.8913 | 64.2975 | -58.7311 | -58.7677 | -58.3557 | -1.6296 | -58.9279 | 64.3066 | 64.2197 | -58.8364 | -58.8913 | -0.07782 | -0.11444 | 0.073242 | 122.6395 | -0.23804 | -0.1236 | 0.086975 | -0.18311 | -0.23804 | 0.082398 | 0.29755 | -0.27466 | -0.036621 | -0.004577 | 122.9507 | 122.9645 | 55.5176 | -122.9919 | 122.9599 | 122.8729 | 57.0236 | -123.1155
1545.0156 | 122.9919 | -58.6945 | 64.2288 | -0.091705 | 0.014926 | 0.069746 | 0.072226 | 0.13228 | 0.0022729 | -0.00066866 | -0.015411 | -0.0065626 | 0.061701 | 0.059321 | 0.0039948 | -0.011333 | 63.9954 | 64.325 | -2.5406 | -58.8089 | 64.2929 | -58.7265 | -58.8226 | -58.3237 | -1.5381 | -58.9096 | 64.27 | 64.1785 | -58.8501 | -58.9005 | -0.032043 | -0.12817 | 0.064087 | 123.0194 | -0.11444 | 0.013733 | -0.23346 | -0.15564 | -0.20599 | 0.041199 | 0.37079 | -0.21515 | -0.009155 | -0.050354 | 122.9874 | 122.6898 | 56.1539 | -123.0515 | 122.9645 | 122.8729 | 57.1564 | -123.1293
1546.0156 | 123.0194 | -58.699 | 64.1876 | -0.19089 | 0.010653 | 0.067823 | 0.071158 | 0.13014 | -0.0013587 | -0.0064365 | -0.17563 | -0.0059216 | 0.064905 | 0.060176 | 0.0046356 | -0.0077012 | 64.032 | 64.1602 | -2.5772 | -58.8455 | 64.2654 | -58.7494 | -58.8455 | -58.3878 | -1.5884 | -58.9325 | 64.2563 | 64.1785 | -58.873 | -58.9417 | -0.050354 | -0.14648 | 0.07782 | 122.8592 | -0.14648 | 0 | -0.15564 | -0.17395 | -0.24261 | 0.068665 | 0.31128 | -0.23346 | 0.009155 | -0.009155 | 122.9645 | 122.731 | 56.1218 | -123.0331 | 122.9553 | 122.8775 | 57.1106 | -123.1293
1547.0156 | 123.0377 | -58.7631 | 64.1098 | -0.12222 | 0.01279 | 0.067182 | 0.071585 | 0.13142 | 0.0022729 | -0.0047275 | -0.068817 | -0.0078442 | 0.067896 | 0.060176 | 0.00549 | -0.0096238 | 64.0228 | 64.1281 | -2.1103 | -58.8821 | 64.1693 | -58.8135 | -58.8913 | -58.4793 | -1.2451 | -58.9645 | 64.1556 | 64.119 | -58.9233 | -58.992 | -0.050354 | -0.12817 | 0.05951 | 122.8912 | -0.11902 | 0.009155 | -0.086975 | -0.16022 | -0.22888 | 0.045777 | 0.28381 | -0.20142 | 0.027465 | 0.009156 | 122.9324 | 122.786 | 56.6528 | -123.0011 | 122.9187 | 122.8821 | 57.518 | -123.1018
1548.0156 | 123.1064 | -58.7585 | 64.0778 | 0.19821 | 0.013003 | 0.06825 | 0.070731 | 0.12928 | -0.00071785 | -0.0032321 | 0.26688 | -0.0069898 | 0.064051 | 0.06103 | 0.0052764 | -0.010905 | 63.9816 | 64.1281 | -1.7807 | -58.905 | 64.1602 | -58.786 | -58.9096 | -58.3969 | -1.387 | -58.96 | 64.0961 | 64.064 | -58.96 | -58.9737 | -0.027466 | -0.15106 | 0.082397 | 122.8867 | -0.14648 | 0.004578 | -0.096131 | -0.20142 | -0.21515 | 0.01831 | 0.36163 | -0.20142 | 0.013733 | -0.013733 | 122.9187 | 122.7402 | 56.9778 | -122.9874 | 122.8546 | 122.8226 | 57.3715 | -123.0515
1549.0156 | 123.0423 | -58.7402 | 64.119 | -0.22141 | 0.01578 | 0.06761 | 0.070303 | 0.12758 | 0.0020593 | -0.0051547 | -0.015411 | -0.0052808 | 0.066614 | 0.060176 | 0.0035674 | -0.0098374 | 64.0457 | 64.1464 | -1.7853 | -58.873 | 64.2105 | -58.7997 | -58.8501 | -58.3923 | -1.68 | -59.0057 | 64.1739 | 64.1327 | -58.9188 | -58.9645 | -0.05951 | -0.10986 | 0.091552 | 122.8867 | -0.13275 | -0.022888 | -0.073243 | -0.17853 | -0.22431 | 0.054931 | 0.3479 | -0.2655 | -0.041198 | 0.013732 | 122.9507 | 122.7859 | 56.955 | -122.9691 | 122.9141 | 122.8729 | 57.0602 | -123.0835
1550.0156 | 123.0011 | -58.7357 | 64.183 | -0.27481 | 0.01044 | 0.068678 | 0.070944 | 0.12886 | -0.0032813 | -0.0062229 | 0.48813 | -0.0067762 | 0.061701 | 0.057826 | 0.0031402 | -0.006633 | 63.9908 | 64.1373 | -2.5818 | -58.8776 | 64.2609 | -58.7769 | -58.8181 | -58.4106 | -1.7258 | -58.9874 | 64.2197 | 64.183 | -58.8867 | -58.9371 | -0.041198 | -0.082397 | 0.07782 | 122.8729 | -0.14191 | -0.059509 | -0.19226 | -0.15106 | -0.20142 | 0.036622 | 0.32501 | -0.25177 | -0.050354 | 0 | 122.9965 | 122.7264 | 56.1539 | -123.0011 | 122.9553 | 122.9187 | 57.0099 | -123.1201
1551.0156 | 123.0286 | -58.7494 | 64.1418 | -0.19089 | 0.015567 | 0.06825 | 0.071585 | 0.12971 | 0.00035035 | -0.0051547 | -0.13748 | -0.0078442 | 0.06341 | 0.060389 | 0.0039948 | -0.0072738 | 64.0228 | 64.1602 | -2.4445 | -58.8409 | 64.2334 | -58.7906 | -58.8776 | -58.3832 | -1.7624 | -58.9645 | 64.2105 | 64.1281 | -58.905 | -58.9828 | -0.041198 | -0.12817 | 0.091552 | 122.9095 | -0.091552 | 0.036621 | -0.11902 | -0.15564 | -0.23346 | 0.068664 | 0.36621 | -0.21515 | 0.01831 | -0.013733 | 122.9828 | 122.7722 | 56.3049 | -123.0194 | 122.9599 | 122.8775 | 56.987 | -123.1247
1552.0156 | 123.0194 | -58.7219 | 64.1647 | -0.29007 | 0.010653 | 0.067396 | 0.071585 | 0.12993 | -0.0024269 | -0.0047275 | -0.13748 | -0.0061352 | 0.061914 | 0.058467 | 0.0037812 | -0.0077012 | 63.9816 | 64.1327 | -2.5589 | -58.873 | 64.2471 | -58.7814 | -58.8593 | -58.4244 | -1.8311 | -58.9645 | 64.2517 | 64.1647 | -58.9005 | -58.9737 | -0.059509 | -0.13733 | 0.082397 | 122.8546 | -0.15106 | -0.013733 | -0.18311 | -0.17853 | -0.25177 | 0.086975 | 0.29755 | -0.24262 | 0.009155 | 0 | 122.9691 | 122.7036 | 56.163 | -123.024 | 122.9736 | 122.8867 | 56.8909 | -123.1384
1553.0156 | 123.0652 | -58.7265 | 64.0961 | 0.13718 | 0.010867 | 0.066969 | 0.070517 | 0.12971 | -0.0058447 | -0.0043003 | 0.34317 | -0.008058 | 0.064264 | 0.057185 | 0.002713 | -0.008342 | 64.0137 | 64.1876 | -2.3026 | -58.8684 | 64.1556 | -58.786 | -58.8272 | -58.3694 | -1.7899 | -58.9279 | 64.1281 | 64.064 | -58.905 | -58.9874 | -0.05951 | -0.10071 | 0.05951 | 122.9141 | -0.14191 | -0.041199 | -0.082397 | -0.17853 | -0.26093 | 0.032044 | 0.35705 | -0.20142 | 0.05951 | -0.032043 | 122.8821 | 122.7402 | 56.4239 | -122.9233 | 122.8546 | 122.7905 | 56.9366 | -123.0835
1554.0156 | 123.0423 | -58.7036 | 64.183 | -0.18326 | 0.01279 | 0.067396 | 0.069022 | 0.12886 | 0.00056395 | -0.0049411 | -0.19089 | -0.0078442 | 0.065546 | 0.057398 | 0.0039948 | -0.0094102 | 64.0457 | 64.1647 | -2.3666 | -58.8226 | 64.27 | -58.7494 | -58.8272 | -58.374 | -2.2247 | -58.9279 | 64.2517 | 64.1922 | -58.873 | -58.9371 | -0.045777 | -0.1236 | 0.086976 | 122.8683 | -0.11902 | 0.004577 | -0.13733 | -0.16937 | -0.23346 | 0.068665 | 0.32959 | -0.2243 | 0.009156 | 0.009156 | 122.9736 | 122.7493 | 56.337 | -123.0103 | 122.9553 | 122.8958 | 56.4789 | -123.1201
1555.0156 | 122.9965 | -58.7082 | 64.1739 | -0.045929 | 0.015994 | 0.06825 | 0.070517 | 0.12928 | 0.00099115 | -0.0028049 | -0.015411 | -0.0059216 | 0.064691 | 0.056758 | 0.004422 | -0.0087692 | 64.0915 | 64.2197 | -2.5635 | -58.8364 | 64.2654 | -58.7723 | -58.8547 | -58.3694 | -2.4216 | -58.9783 | 64.238 | 64.151 | -58.8776 | -58.9417 | -0.064087 | -0.14648 | 0.091553 | 122.9279 | -0.12817 | 0.01831 | -0.082397 | -0.16937 | -0.23346 | 0.064087 | 0.33874 | -0.27008 | -0.036621 | -0.022888 | 122.9736 | 122.7997 | 56.1447 | -123.0286 | 122.9462 | 122.8592 | 56.2866 | -123.1155
1556.0156 | 123.024 | -58.7082 | 64.2059 | -0.17563 | 0.010867 | 0.069959 | 0.069663 | 0.12928 | -0.0013587 | -0.0040867 | -0.099335 | -0.0059216 | 0.063837 | 0.059321 | 0.0020722 | -0.0068466 | 64.032 | 64.1556 | -2.6047 | -58.8455 | 64.27 | -58.7769 | -58.8501 | -58.4198 | -2.5818 | -58.9462 | 64.2517 | 64.183 | -58.8959 | -58.96 | -0.068664 | -0.14191 | 0.064087 | 122.8638 | -0.13733 | 0.004578 | -0.17395 | -0.18768 | -0.25177 | 0.045776 | 0.28839 | -0.23804 | 0.013733 | -0.022889 | 122.9782 | 122.7402 | 56.1035 | -123.056 | 122.9599 | 122.8912 | 56.1264 | -123.1659
1557.0156 | 123.024 | -58.7448 | 64.1464 | -0.17563 | 0.011935 | 0.069319 | 0.071372 | 0.12993 | 0.00013675 | -0.0043003 | -0.18326 | -0.0065626 | 0.065759 | 0.057612 | 0.0029266 | -0.0085556 | 64.0182 | 64.1464 | -2.536 | -58.8684 | 64.2426 | -58.8135 | -58.8821 | -58.4244 | -2.3804 | -58.9828 | 64.1739 | 64.1144 | -58.9462 | -58.9828 | -0.068665 | -0.13733 | 0.096131 | 122.8912 | -0.1236 | 0.013733 | -0.12817 | -0.20142 | -0.23804 | 0.027466 | 0.32044 | -0.23804 | 0 | -0.032043 | 122.9874 | 122.7631 | 56.2088 | -123.0286 | 122.9187 | 122.8592 | 56.3644 | -123.1293
1558.0156 | 123.0194 | -58.7723 | 64.119 | -0.17563 | 0.010653 | 0.070387 | 0.07244 | 0.13014 | -0.0041357 | -0.0051547 | -0.16037 | -0.0082716 | 0.061487 | 0.060603 | 0.00079042 | -0.0074876 | 63.9404 | 64.1144 | -2.6413 | -58.905 | 64.2059 | -58.8181 | -58.8913 | -58.4381 | -2.4902 | -59.0332 | 64.1922 | 64.1006 | -58.9691 | -59.0149 | -0.045776 | -0.11902 | 0.086975 | 122.8867 | -0.13275 | -0.013733 | -0.17853 | -0.19684 | -0.24262 | 0.073242 | 0.33417 | -0.26093 | -0.01831 | -0.018311 | 122.9782 | 122.7127 | 56.131 | -123.0103 | 122.9645 | 122.8729 | 56.282 | -123.1339
1559.0156 | 123.0423 | -58.7402 | 64.1144 | -0.076447 | 0.014499 | 0.069959 | 0.072867 | 0.13121 | 0.0016321 | -0.0043003 | -0.03067 | -0.005708 | 0.064051 | 0.058894 | 0.0014312 | -0.0096238 | 64.0274 | 64.1281 | -2.5314 | -58.8776 | 64.1968 | -58.8043 | -58.8867 | -58.4473 | -2.5223 | -58.9737 | 64.1785 | 64.1052 | -58.9462 | -58.9691 | -0.064087 | -0.14648 | 0.082397 | 122.8683 | -0.13733 | 0.009156 | -0.086975 | -0.20599 | -0.22888 | 0.064087 | 0.29297 | -0.23346 | -0.004578 | -0.009155 | 122.937 | 122.7676 | 56.2088 | -123.0011 | 122.9187 | 122.8455 | 56.218 | -123.0835
1560.0156 | 122.9874 | -58.7906 | 64.119 | -0.67154 | 0.011508 | 0.069105 | 0.071158 | 0.12928 | -0.0026405 | -0.0047275 | -0.12222 | -0.0078442 | 0.062128 | 0.062312 | 0.0016448 | -0.0070602 | 63.913 | 64.0778 | -2.1698 | -58.9188 | 64.1785 | -58.8364 | -58.9096 | -58.4976 | -2.4902 | -59.024 | 64.1968 | 64.1098 | -58.9462 | -59.0149 | -0.045777 | -0.11902 | 0.059509 | 122.8683 | -0.12817 | -0.009155 | -0.20599 | -0.15564 | -0.22431 | 0.077819 | 0.29297 | -0.23346 | -0.009155 | -0.009156 | 122.9691 | 122.7036 | 56.6208 | -123.0286 | 122.9874 | 122.9004 | 56.3004 | -123.1339
1561.0156 | 123.024 | -58.754 | 64.1098 | -0.12985 | 0.012362 | 0.068464 | 0.073721 | 0.12886 | 0.00056395 | -0.0032321 | -0.091705 | -0.0078442 | 0.062342 | 0.059962 | 0.004422 | -0.0074876 | 63.9999 | 64.1373 | -2.4765 | -58.8776 | 64.2197 | -58.8181 | -58.8959 | -58.4427 | -2.5864 | -59.0103 | 64.1785 | 64.1052 | -58.9371 | -59.0057 | -0.064087 | -0.14191 | 0.10986 | 122.8912 | -0.1236 | 0.018311 | -0.10986 | -0.18311 | -0.25177 | 0.068665 | 0.31128 | -0.25635 | -0.004578 | -0.004577 | 122.9736 | 122.7539 | 56.2775 | -123.0057 | 122.9324 | 122.8592 | 56.1676 | -123.1155
1562.0156 | 123.0469 | -58.7723 | 64.1235 | -0.168 | 0.013217 | 0.068037 | 0.070944 | 0.12971 | -0.00029045 | -0.0057957 | -0.17563 | -0.0065626 | 0.061487 | 0.059321 | 0.0024994 | -0.006633 | 63.9313 | 64.0823 | -2.5772 | -58.9371 | 64.1556 | -58.8364 | -58.9325 | -58.5022 | -2.4353 | -59.0195 | 64.183 | 64.0961 | -58.96 | -59.0332 | -0.064087 | -0.16022 | 0.032044 | 122.8546 | -0.16479 | -0.004578 | -0.19226 | -0.18768 | -0.26093 | 0.059509 | 0.27008 | -0.24719 | 0.013733 | -0.027466 | 122.9279 | 122.7036 | 56.1951 | -123.056 | 122.9553 | 122.8683 | 56.337 | -123.1567
1563.0156 | 123.0331 | -58.786 | 64.0732 | -0.10696 | 0.014071 | 0.069532 | 0.072653 | 0.13014 | 0.0050499 | -0.0036595 | -0.045929 | -0.0061352 | 0.062982 | 0.06103 | 0.0039948 | -0.0098374 | 63.8443 | 64.2014 | -2.3804 | -58.9325 | 64.1693 | -58.8501 | -58.9279 | -58.4656 | -2.417 | -59.0424 | 64.1235 | 64.0594 | -58.9874 | -59.0515 | -0.064087 | -0.14191 | 0.096131 | 122.9874 | -0.14648 | -0.004578 | -0.22888 | -0.20142 | -0.2655 | 0.050354 | 0.32044 | -0.25635 | 0.009156 | -0.013733 | 122.9553 | 122.6303 | 56.4056 | -123.0011 | 122.9095 | 122.8455 | 56.369 | -123.1247
1564.0156 | 122.9965 | -58.7769 | 64.1235 | -0.22903 | 0.011935 | 0.068464 | 0.071799 | 0.12864 | -0.0030677 | -0.0049411 | -0.12985 | -0.0069898 | 0.064905 | 0.058894 | 0.0039948 | -0.0059922 | 63.9313 | 64.0915 | -2.5909 | -58.9279 | 64.2059 | -58.8272 | -58.8959 | -58.6304 | -2.6093 | -59.0652 | 64.1876 | 64.0778 | -58.9783 | -59.0149 | -0.050354 | -0.11902 | 0.082398 | 122.8683 | -0.15106 | -0.032043 | -0.19226 | -0.20142 | -0.23804 | 0.064087 | 0.14648 | -0.28839 | -0.050354 | -0.045776 | 122.9828 | 122.7081 | 56.1859 | -123.0194 | 122.9645 | 122.8546 | 56.1676 | -123.1384
1565.0156 | 123.0286 | -58.7677 | 64.1052 | -0.084076 | 0.014712 | 0.066755 | 0.072867 | 0.1295 | 0.0014185 | -0.0040867 | 0.38132 | -0.0072034 | 0.067896 | 0.058894 | 0.0048492 | -0.0081284 | 63.9999 | 64.1281 | -2.7008 | -58.905 | 64.1739 | -58.8226 | -58.9233 | -58.4747 | -2.8198 | -59.0012 | 64.1556 | 64.0778 | -58.9462 | -59.0057 | -0.054932 | -0.15564 | 0.068664 | 122.8958 | -0.13733 | 0.018311 | -0.10529 | -0.17853 | -0.23804 | 0.050354 | 0.29297 | -0.23346 | 0.004577 | -0.027466 | 122.9416 | 122.7676 | 56.0669 | -123.0286 | 122.9233 | 122.8455 | 55.9479 | -123.111
1566.0156 | 123.0103 | -58.7494 | 64.119 | -0.18326 | 0.011722 | 0.069959 | 0.070303 | 0.12822 | 0.00013675 | -0.0066501 | -0.12222 | -0.0076306 | 0.065546 | 0.058894 | 0.0022858 | -0.0059922 | 63.9267 | 64.0869 | -2.8152 | -58.905 | 64.1968 | -58.8409 | -58.905 | -58.5114 | -3.0487 | -59.0332 | 64.1922 | 64.1052 | -58.9325 | -59.0149 | -0.091552 | -0.15564 | 0.077819 | 122.8363 | -0.15564 | 0 | -0.19226 | -0.18311 | -0.2655 | 0.073242 | 0.23804 | -0.28381 | -0.01831 | -0.013733 | 122.9462 | 122.6761 | 55.9341 | -123.024 | 122.9416 | 122.8546 | 55.7007 | -123.1339
1567.0156 | 123.0423 | -58.7631 | 64.0778 | -0.061188 | 0.015567 | 0.070814 | 0.073294 | 0.12907 | 0.0020593 | -0.0053683 | 0.96878 | -0.0069898 | 0.061914 | 0.056971 | 0.0033538 | -0.0091966 | 63.9679 | 64.1098 | -2.6962 | -58.8959 | 64.1602 | -58.8455 | -58.9508 | -58.4564 | -2.8244 | -59.024 | 64.1418 | 64.0228 | -58.9508 | -59.0195 | -0.082397 | -0.18768 | 0.082397 | 122.8729 | -0.13275 | 0.054932 | -0.10986 | -0.18768 | -0.25635 | 0.064087 | 0.3067 | -0.26093 | -0.004578 | -0.054932 | 122.9233 | 122.731 | 56.0669 | -123.0286 | 122.905 | 122.786 | 55.9387 | -123.0972
1568.0156 | 123.0103 | -58.7585 | 64.1052 | -0.15274 | 0.012149 | 0.069105 | 0.073081 | 0.12907 | -0.0015723 | -0.0032321 | -0.091705 | -0.0067762 | 0.064478 | 0.059748 | 0.0014312 | -0.0077012 | 63.9267 | 64.0686 | -2.7008 | -58.9233 | 64.183 | -58.8409 | -58.9142 | -58.5114 | -3.0258 | -59.024 | 64.1602 | 64.119 | -58.9645 | -59.0012 | -0.082397 | -0.15564 | 0.077819 | 122.8271 | -0.1648 | -0.009155 | -0.17853 | -0.20599 | -0.24262 | 0.054931 | 0.24719 | -0.2655 | -0.022888 | 0.013733 | 122.9416 | 122.6852 | 56.0577 | -123.0194 | 122.9187 | 122.8775 | 55.7327 | -123.1064
1569.0156 | 123.0331 | -58.8547 | 64.0457 | -0.045929 | 0.01514 | 0.068678 | 0.071585 | 0.13185 | 0.0027001 | -0.0043003 | -0.0077819 | -0.0059216 | 0.062342 | 0.058039 | 0.0029266 | -0.0089828 | 63.9587 | 64.0549 | -2.4078 | -58.9737 | 64.1373 | -58.8547 | -58.9645 | -58.5251 | -2.9068 | -59.0927 | 64.0915 | 64.0366 | -59.0057 | -59.0424 | 0 | -0.10986 | 0.091553 | 122.9095 | -0.11902 | -0.009155 | -0.086975 | -0.15106 | -0.18768 | 0.045777 | 0.32959 | -0.23804 | -0.050354 | -0.009155 | 122.9919 | 122.8134 | 56.4468 | -123.0103 | 122.9462 | 122.8912 | 55.9479 | -123.0881
1570.0156 | 123.0515 | -58.8272 | 64.032 | -0.17563 | 0.011722 | 0.070814 | 0.070944 | 0.12971 | 0.00013675 | -0.0060093 | -0.15274 | -0.0054944 | 0.064051 | 0.058894 | 0.0029266 | -0.0096238 | 63.8992 | 64.0228 | -2.3987 | -58.9691 | 64.1327 | -58.9142 | -58.9828 | -58.5571 | -2.3758 | -59.0652 | 64.1006 | 64.0091 | -59.0332 | -59.0607 | -0.086976 | -0.15564 | 0.10071 | 122.85 | -0.14191 | 0.013733 | -0.13275 | -0.20599 | -0.23346 | 0.068665 | 0.27008 | -0.23804 | -0.004578 | -0.022888 | 122.9599 | 122.7264 | 56.4285 | -123.0148 | 122.9279 | 122.8363 | 56.4514 | -123.0927
1571.0156 | 123.0331 | -58.8043 | 64.0823 | -0.091705 | 0.013858 | 0.06761 | 0.072226 | 0.13057 | 0.0016321 | -0.0047275 | -0.061188 | -0.0050672 | 0.062128 | 0.059107 | 0.0048492 | -0.0094102 | 63.9496 | 64.0823 | -2.5955 | -58.9325 | 64.1464 | -58.8867 | -58.96 | -58.5297 | -2.6047 | -59.0652 | 64.0961 | 64.0457 | -58.9966 | -59.0607 | -0.082398 | -0.15564 | 0.064087 | 122.8867 | -0.12817 | 0.027466 | -0.13275 | -0.19226 | -0.25635 | 0.013733 | 0.27466 | -0.26093 | -0.004578 | -0.036621 | 122.9507 | 122.7539 | 56.2088 | -123.0423 | 122.9004 | 122.85 | 56.1996 | -123.143
1572.0156 | 122.9965 | -58.8135 | 64.0961 | 0.12955 | 0.013003 | 0.071027 | 0.071799 | 0.1295 | -0.0030677 | -0.0062229 | -0.099335 | -0.0065626 | 0.062342 | 0.058253 | 0.002713 | -0.0068466 | 63.9313 | 64.0411 | -2.536 | -58.9325 | 64.1647 | -58.8913 | -58.9417 | -58.5434 | -2.3621 | -59.0652 | 64.1373 | 64.0915 | -59.0057 | -59.0286 | -0.077819 | -0.12817 | 0.068665 | 122.8546 | -0.11902 | 0.009155 | -0.16479 | -0.19226 | -0.21515 | 0.041199 | 0.27008 | -0.25177 | -0.036622 | -0.004577 | 122.9782 | 122.7448 | 56.2775 | -123.0377 | 122.9507 | 122.905 | 56.4514 | -123.1247
1573.0156 | 123.024 | -58.8135 | 64.0778 | -0.0383 | 0.014285 | 0.068037 | 0.072653 | 0.128 | 0.00077755 | -0.0057957 | 0.022736 | -0.0050672 | 0.062342 | 0.060389 | 0.0042084 | -0.0087692 | 63.9587 | 64.0686 | -2.6871 | -58.9371 | 64.1373 | -58.8455 | -58.9325 | -58.5068 | -2.6093 | -59.0744 | 64.1327 | 64.0503 | -59.0012 | -59.0698 | -0.032043 | -0.11902 | 0.059509 | 122.8821 | -0.1236 | -0.004578 | -0.11902 | -0.18768 | -0.25635 | 0.054931 | 0.3067 | -0.26093 | -0.004578 | -0.027466 | 122.9507 | 122.7722 | 56.1264 | -123.0103 | 122.9462 | 122.8638 | 56.2042 | -123.1476
1574.0156 | 123.0286 | -58.8043 | 64.1052 | -0.19089 | 0.011508 | 0.066114 | 0.071158 | 0.12993 | -0.00071785 | -0.0032321 | -0.14511 | -0.008058 | 0.066828 | 0.058253 | 0.004422 | -0.0072738 | 63.9221 | 64.0961 | -2.9022 | -58.9096 | 64.2014 | -58.8364 | -58.9188 | -58.4976 | -2.7557 | -59.0195 | 64.1693 | 64.0915 | -58.9691 | -59.0332 | -0.032044 | -0.11444 | 0.09613 | 122.9004 | -0.10529 | 0.009155 | -0.18311 | -0.16479 | -0.22888 | 0.064087 | 0.3067 | -0.21515 | 0.013733 | -0.013733 | 123.0057 | 122.7264 | 55.9021 | -123.024 | 122.9736 | 122.8958 | 56.0486 | -123.1384
1575.0156 | 123.0377 | -58.8318 | 64.0228 | -0.076447 | 0.012362 | 0.06761 | 0.072653 | 0.12993 | 0.0012047 | -0.0034457 | -0.00015237 | -0.0078442 | 0.064691 | 0.060176 | 0.0057038 | -0.008342 | 63.945 | 64.0732 | -2.8061 | -58.9508 | 64.1464 | -58.8821 | -58.9554 | -58.5251 | -2.4673 | -59.079 | 64.0961 | 64.0457 | -58.9966 | -59.0424 | -0.050354 | -0.1236 | 0.1236 | 122.905 | -0.11902 | 0.004577 | -0.07782 | -0.16479 | -0.21057 | 0.073242 | 0.3067 | -0.24719 | -0.036621 | 0.022888 | 122.9782 | 122.7768 | 56.0257 | -122.9782 | 122.9279 | 122.8775 | 56.3644 | -123.0652
1576.0156 | 122.9507 | -58.7997 | 64.0732 | -0.076447 | 0.01578 | 0.068037 | 0.071585 | 0.12971 | -7.6852e-05 | -0.0051547 | -0.03067 | -0.00464 | 0.063837 | 0.058467 | 0.0057038 | -0.010051 | 63.9496 | 64.0961 | -2.8793 | -58.9188 | 64.1739 | -58.873 | -58.9279 | -58.493 | -2.7466 | -59.0286 | 64.1373 | 64.0869 | -58.96 | -59.024 | -0.073242 | -0.12817 | 0.10071 | 122.8958 | -0.11902 | 0.009155 | -0.1236 | -0.16022 | -0.2243 | 0.064087 | 0.3067 | -0.22888 | -0.004577 | 0.013733 | 122.9736 | 122.7493 | 55.9204 | -123.0011 | 122.937 | 122.8867 | 56.0532 | -123.0972
1577.0156 | 123.0286 | -58.8135 | 64.0549 | 0.015106 | 0.014712 | 0.06761 | 0.070944 | 0.12993 | -7.6852e-05 | -0.0043003 | 0.09903 | -0.0065626 | 0.065759 | 0.059107 | 0.007199 | -0.0064194 | 63.8992 | 64.0457 | -2.9022 | -58.9783 | 64.1373 | -58.8776 | -58.9828 | -58.5754 | -2.8839 | -59.1064 | 64.1052 | 64.0549 | -58.992 | -59.0561 | -0.064086 | -0.16937 | 0.082397 | 122.8592 | -0.16479 | 0.004578 | -0.15564 | -0.17853 | -0.24261 | 0.050354 | 0.23804 | -0.29297 | -0.050354 | 0 | 122.9507 | 122.7127 | 55.9113 | -123.0377 | 122.9187 | 122.8683 | 55.9296 | -123.111
1578.0156 | 123.0286 | -58.8409 | 64.0594 | -0.14511 | 0.012576 | 0.068464 | 0.072226 | 0.12971 | -0.0022131 | -0.0051547 | -0.10696 | -0.0067762 | 0.064478 | 0.059107 | 0.001004 | -0.0077012 | 63.8947 | 64.0503 | -2.6825 | -58.9691 | 64.1281 | -58.8913 | -58.9645 | -58.5709 | -2.9938 | -59.0561 | 64.1373 | 64.0778 | -59.0286 | -59.0286 | -0.050354 | -0.1236 | 0.068665 | 122.8912 | -0.12817 | -0.004577 | -0.1648 | -0.18768 | -0.18768 | 0.07782 | 0.27008 | -0.21515 | -0.027466 | 0.018311 | 122.9691 | 122.7356 | 56.1584 | -123.024 | 122.9782 | 122.9187 | 55.8472 | -123.0881
1579.0156 | 122.9965 | -58.8318 | 64.0732 | -0.10696 | 0.014499 | 0.065046 | 0.06539 | 0.13142 | 0.00035035 | -0.0060093 | 0.030365 | -0.0069898 | 0.065332 | 0.056758 | 0.0046356 | -0.010051 | 63.8992 | 64.1098 | -2.4582 | -58.9737 | 64.1418 | -58.8867 | -58.9828 | -58.5388 | -2.8748 | -59.079 | 64.0915 | 64.032 | -58.9966 | -59.0652 | -0.054932 | -0.15106 | 0.068665 | 122.9416 | -0.14191 | 0.009155 | -0.17395 | -0.16479 | -0.23346 | 0.018311 | 0.29297 | -0.24719 | -0.013732 | -0.041199 | 122.9736 | 122.731 | 56.3736 | -123.056 | 122.9233 | 122.8638 | 55.957 | -123.1384
1580.0156 | 123.0652 | -58.8226 | 64.0594 | -0.18326 | 0.014499 | 0.066328 | 0.068167 | 0.13057 | 0.00035035 | -0.0053683 | -0.076446 | -0.0069898 | 0.064905 | 0.058039 | 0.0042084 | -0.0096238 | 63.9267 | 64.0686 | -2.655 | -58.9417 | 64.151 | -58.8913 | -58.9508 | -58.5297 | -2.8976 | -59.0652 | 64.0915 | 64.0182 | -59.0057 | -59.079 | -0.068664 | -0.12817 | 0.091553 | 122.8912 | -0.11902 | 0.009156 | -0.13275 | -0.18311 | -0.25635 | 0.032044 | 0.29297 | -0.24262 | 0.013732 | -0.041198 | 122.9736 | 122.7493 | 56.1676 | -123.0103 | 122.9141 | 122.8409 | 55.925 | -123.1384
1581.0625 | 123.2666 | -58.8043 | 64.0778 | -0.33585 | 0.0089443 | 0.069319 | 0.07479 | 0.1295 | -0.0084083 | -0.0075047 | 0.0074766 | -0.010194 | 0.063837 | 0.058253 | 0.00057682 | -0.0044968 | 63.9313 | 64.1739 | -2.3071 | -58.9096 | 64.0732 | -58.8593 | -58.96 | -58.5068 | -2.417 | -58.9691 | 64.0411 | 63.9862 | -58.9783 | -59.0469 | -0.054932 | -0.15564 | -0.004578 | 122.9782 | -0.10529 | 0.050354 | -0.14648 | -0.17395 | -0.24262 | -0.036621 | 0.29755 | -0.16479 | 0.07782 | -0.091553 | 122.8775 | 122.7356 | 56.4972 | -123.0377 | 122.8455 | 122.7905 | 56.3873 | -123.1247
1582.0156 | 123.0606 | -58.8593 | 64.0411 | -0.084076 | 0.016849 | 0.069532 | 0.072012 | 0.13014 | 0.0029137 | -0.0053683 | -0.038299 | -0.0065626 | 0.065119 | 0.059748 | 0.004422 | -0.0074876 | 63.9313 | 64.0457 | -2.4307 | -58.9737 | 64.1281 | -58.9096 | -58.9966 | -58.5342 | -2.6688 | -59.0698 | 64.0686 | 63.9771 | -59.0149 | -59.0881 | -0.050354 | -0.13733 | 0.086975 | 122.905 | -0.11444 | 0.022888 | -0.10986 | -0.15564 | -0.22888 | 0.027466 | 0.32501 | -0.21057 | 0.018311 | -0.064087 | 122.9874 | 122.7905 | 56.4285 | -123.0377 | 122.9279 | 122.8363 | 56.1905 | -123.1293
1583.0156 | 122.9828 | -58.8776 | 64.0274 | -0.0077822 | 0.014499 | 0.067182 | 0.072653 | 0.13228 | -0.00050425 | -0.0038731 | 0.076141 | -0.0089124 | 0.064478 | 0.057826 | 0.0031402 | -0.010478 | 63.8809 | 63.9999 | -2.4399 | -59.0195 | 64.1235 | -58.905 | -59.0149 | -58.6121 | -3.1631 | -59.1431 | 64.0869 | 64.0411 | -59.0378 | -59.1156 | -0.027466 | -0.13733 | 0.09613 | 122.8775 | -0.14191 | -0.004577 | -0.14648 | -0.16022 | -0.23804 | 0.059509 | 0.2655 | -0.2655 | -0.027465 | 0.013733 | 123.0011 | 122.7585 | 56.4377 | -123.0423 | 122.9645 | 122.9187 | 55.7144 | -123.143
1584.0156 | 123.0881 | -58.8455 | 64.0732 | -0.13748 | 0.014499 | 0.068891 | 0.069235 | 0.13292 | 0.00056395 | -0.0021641 | -0.076446 | -0.0072034 | 0.062769 | 0.059748 | 0.0048492 | -0.0089828 | 63.9313 | 64.064 | -2.243 | -58.9737 | 64.1144 | -58.8913 | -58.9783 | -58.548 | -2.9572 | -59.0836 | 64.0869 | 64.032 | -59.0057 | -59.0561 | -0.045776 | -0.13275 | 0.041199 | 122.9095 | -0.12817 | 0.004577 | -0.14191 | -0.16022 | -0.21057 | 0.013733 | 0.29755 | -0.23804 | -0.027466 | -0.041199 | 122.9599 | 122.7768 | 56.6025 | -123.0515 | 122.9324 | 122.8775 | 55.8884 | -123.1293
1585.0156 | 123.0194 | -58.873 | 63.9908 | -0.16037 | 0.014285 | 0.069959 | 0.07009 | 0.13035 | 0.00077755 | -0.0057957 | -0.00015237 | -0.0052808 | 0.062769 | 0.059107 | 0.004422 | -0.0070602 | 63.9221 | 64.0457 | -2.211 | -59.0012 | 64.0869 | -58.9279 | -59.0149 | -58.5938 | -3.1723 | -59.1064 | 64.0457 | 63.9999 | -59.0424 | -59.1248 | -0.054931 | -0.14191 | 0.09613 | 122.9187 | -0.12817 | 0.013733 | -0.068665 | -0.16937 | -0.25177 | 0.054931 | 0.27924 | -0.23346 | 0.018311 | 0.009155 | 122.9599 | 122.7951 | 56.662 | -123.0057 | 122.9187 | 122.8729 | 55.7007 | -123.1155
1586.0156 | 123.0423 | -58.8547 | 63.9908 | -0.12985 | 0.013431 | 0.067823 | 0.069449 | 0.13142 | -0.0013587 | -0.0032321 | 0.015106 | -0.0069898 | 0.064691 | 0.057826 | 0.0039948 | -0.0087692 | 63.8992 | 64.0182 | -2.0828 | -58.9874 | 64.064 | -58.9188 | -59.0149 | -58.58 | -3.2547 | -59.0973 | 64.0686 | 63.9771 | -59.0744 | -59.1202 | -0.064087 | -0.16022 | 0.073242 | 122.8729 | -0.13275 | 0.027466 | -0.091553 | -0.21973 | -0.2655 | 0.07782 | 0.27466 | -0.24262 | 0.022888 | -0.013733 | 122.9187 | 122.7539 | 56.7719 | -123.0057 | 122.9233 | 122.8317 | 55.6 | -123.111
1587.0156 | 123.0011 | -58.873 | 64.0182 | -0.0383 | 0.016208 | 0.066969 | 0.070731 | 0.12928 | -7.6852e-05 | -0.0053683 | 0.10666 | -0.0042126 | 0.062128 | 0.058894 | 0.0037812 | -0.0077012 | 63.8626 | 63.9816 | -2.3026 | -59.0286 | 64.0869 | -58.9325 | -59.0149 | -58.6258 | -3.3371 | -59.1568 | 64.0457 | 63.9908 | -59.0515 | -59.1156 | -0.059509 | -0.14191 | 0.068664 | 122.8546 | -0.15564 | -0.013732 | -0.15564 | -0.17853 | -0.24262 | 0.027465 | 0.24719 | -0.28381 | -0.041198 | -0.027466 | 122.9599 | 122.7356 | 56.5704 | -123.0331 | 122.9187 | 122.8638 | 55.5359 | -123.1339
1588.0156 | 123.056 | -58.8638 | 63.9999 | -0.19852 | 0.015567 | 0.069319 | 0.07244 | 0.12886 | 0.00077755 | -0.0047275 | -0.091705 | -0.005708 | 0.063837 | 0.05868 | 0.0020722 | -0.0072738 | 63.8809 | 64.0182 | -2.33 | -59.0103 | 64.064 | -58.9462 | -59.0012 | -58.5938 | -2.9251 | -59.1248 | 64.0411 | 63.9954 | -59.0652 | -59.111 | -0.082397 | -0.13733 | 0.064087 | 122.8821 | -0.14648 | -0.009155 | -0.11902 | -0.20142 | -0.24719 | 0.041199 | 0.27008 | -0.26093 | -0.013733 | -0.004578 | 122.9279 | 122.7448 | 56.5338 | -123.0011 | 122.905 | 122.8592 | 55.9387 | -123.111
1589.0156 | 122.9782 | -58.9371 | 63.9954 | 0.045624 | 0.016208 | 0.067182 | 0.07244 | 0.13121 | 0.00056395 | -0.0047275 | 0.12192 | -0.0042126 | 0.066614 | 0.060816 | 0.0052764 | -0.008342 | 63.7848 | 63.9221 | -2.1103 | -59.0607 | 64.0732 | -58.9691 | -59.0515 | -58.6945 | -2.8198 | -59.23 | 64.0274 | 63.9542 | -59.0744 | -59.1431 | -0.032043 | -0.11444 | 0.07782 | 122.8592 | -0.1236 | -0.009155 | -0.21057 | -0.13733 | -0.20599 | 0.032044 | 0.24262 | -0.29297 | -0.086976 | -0.041198 | 123.0103 | 122.7219 | 56.8268 | -123.0469 | 122.9645 | 122.8912 | 56.1172 | -123.1384
1590.0156 | 123.0469 | -58.8959 | 63.9908 | -0.10696 | 0.015567 | 0.068037 | 0.072867 | 0.13035 | 0.0012047 | -0.0030185 | -0.0077819 | -0.0052808 | 0.064264 | 0.058039 | 0.0042084 | -0.0070602 | 63.8718 | 64.0045 | -1.9501 | -59.0195 | 64.064 | -58.9371 | -59.0195 | -58.7036 | -2.7649 | -59.1293 | 64.0366 | 63.9862 | -59.0744 | -59.1156 | -0.041199 | -0.1236 | 0.073242 | 122.9004 | -0.1236 | 0 | -0.11902 | -0.17853 | -0.21973 | 0.045776 | 0.19226 | -0.23346 | -0.013732 | -0.004578 | 122.9599 | 122.7676 | 56.9458 | -123.0103 | 122.9324 | 122.8821 | 56.131 | -123.1064
1591.0156 | 122.9645 | -58.9096 | 63.9908 | 0.060882 | 0.014712 | 0.06825 | 0.071372 | 0.13057 | 0.00056395 | -0.0040867 | 0.12192 | -0.0044264 | 0.063196 | 0.056971 | 0.0033538 | -0.0077012 | 63.8397 | 63.945 | -2.0004 | -59.0652 | 64.0503 | -58.9828 | -59.0469 | -58.699 | -3.1952 | -59.198 | 63.9999 | 63.9816 | -59.0927 | -59.1431 | -0.073242 | -0.13733 | 0.059509 | 122.8546 | -0.15564 | -0.018311 | -0.15106 | -0.1831 | -0.23346 | 0.009155 | 0.21057 | -0.28839 | -0.054932 | -0.009156 | 122.9599 | 122.7493 | 56.9092 | -123.0377 | 122.9095 | 122.8912 | 55.7144 | -123.1338
1592.0156 | 123.0057 | -58.905 | 64.0045 | -0.19089 | 0.012362 | 0.068891 | 0.071585 | 0.12758 | -0.0028541 | -0.0043003 | -0.14511 | -0.0069898 | 0.064264 | 0.05868 | 0.0037812 | -0.011333 | 63.8214 | 63.945 | -2.0004 | -59.0469 | 64.0549 | -58.9462 | -59.0424 | -58.6395 | -2.8381 | -59.111 | 64.0366 | 63.9999 | -59.0836 | -59.111 | -0.041199 | -0.13733 | 0.050354 | 122.85 | -0.14191 | -0.004578 | -0.18311 | -0.17853 | -0.20599 | 0.032043 | 0.2655 | -0.20599 | 0 | -0.004578 | 122.9599 | 122.7264 | 56.9046 | -123.0469 | 122.9416 | 122.905 | 56.0669 | -123.1155
1593.0156 | 122.9874 | -58.9417 | 63.9725 | 0.0074768 | 0.013003 | 0.068037 | 0.07244 | 0.13163 | 0.0016321 | -0.0045139 | 0.076141 | -0.0076306 | 0.063196 | 0.058253 | 0.0059174 | -0.0085556 | 63.8351 | 63.9267 | -2.1011 | -59.0881 | 64.0411 | -58.9737 | -59.0607 | -58.6945 | -2.8885 | -59.1934 | 64.0366 | 63.9542 | -59.1293 | -59.1476 | -0.032044 | -0.11902 | 0.068665 | 122.8683 | -0.14648 | -0.027466 | -0.13733 | -0.18768 | -0.20599 | 0.064087 | 0.24719 | -0.25177 | -0.045776 | -0.01831 | 122.9828 | 122.7768 | 56.8405 | -123.0331 | 122.9782 | 122.8958 | 56.0532 | -123.1201
1594.0156 | 123.024 | -58.905 | 63.9816 | -0.18326 | 0.013217 | 0.067396 | 0.071585 | 0.12886 | -7.6852e-05 | -0.0047275 | -0.10696 | -0.0065626 | 0.065546 | 0.058039 | 0.002713 | -0.0091966 | 63.858 | 63.9816 | -1.9867 | -59.0332 | 64.064 | -58.9691 | -59.0561 | -58.6395 | -2.5543 | -59.1476 | 64.0182 | 63.9862 | -59.0698 | -59.1522 | -0.064087 | -0.15106 | 0.082398 | 122.8867 | -0.12817 | 0.022888 | -0.1236 | -0.16479 | -0.24719 | 0.036622 | 0.2655 | -0.24262 | 0.004578 | 0.004578 | 122.9691 | 122.7631 | 56.9183 | -123.0377 | 122.9233 | 122.8912 | 56.3507 | -123.1338
1595.0156 | 123.0377 | -58.9142 | 63.9725 | -0.045929 | 0.017489 | 0.068464 | 0.071158 | 0.13313 | 0.00099115 | -0.0038731 | 0.068512 | -0.00464 | 0.064264 | 0.059107 | 0.0057038 | -0.0094102 | 63.8214 | 63.9633 | -1.9775 | -59.0744 | 64.0549 | -58.9874 | -59.0378 | -58.6761 | -2.6917 | -59.198 | 64.0045 | 63.9404 | -59.0881 | -59.1568 | -0.073242 | -0.1236 | 0.082398 | 122.8775 | -0.16022 | -0.036621 | -0.15106 | -0.17395 | -0.24261 | 0.032044 | 0.23804 | -0.28381 | -0.041199 | -0.032043 | 122.9691 | 122.7356 | 56.9366 | -123.0103 | 122.9187 | 122.8546 | 56.2225 | -123.1293
1596.0156 | 123.0743 | -58.9142 | 63.9908 | -0.068817 | 0.010867 | 0.066541 | 0.072653 | 0.13185 | 0.0012047 | -0.0053683 | -0.00015237 | -0.0054944 | 0.067041 | 0.061244 | 0.0035674 | -0.0094102 | 63.8718 | 64.0091 | -2.092 | -59.0012 | 64.0686 | -58.9462 | -59.0286 | -58.5434 | -2.7512 | -59.111 | 64.0366 | 63.9725 | -59.0698 | -59.1339 | -0.032043 | -0.11444 | 0.07782 | 122.9233 | -0.086975 | 0.027465 | -0.11902 | -0.15564 | -0.21973 | 0.045776 | 0.37079 | -0.19684 | 0.022888 | -0.018311 | 122.9828 | 122.786 | 56.8222 | -123.0194 | 122.9507 | 122.8867 | 56.163 | -123.1247
1597.0156 | 122.9828 | -58.9462 | 63.9679 | 0.060882 | 0.01279 | 0.068464 | 0.071799 | 0.13142 | 0.0024865 | -0.0025913 | 0.10666 | -0.0078442 | 0.065332 | 0.059321 | 0.0031402 | -0.0068466 | 63.8123 | 63.9175 | -2.0279 | -59.0836 | 64.0457 | -58.992 | -59.0698 | -58.7128 | -2.7145 | -59.2255 | 64.032 | 63.9816 | -59.1202 | -59.1888 | -0.045776 | -0.1236 | 0.077819 | 122.8638 | -0.13733 | -0.013733 | -0.15564 | -0.17395 | -0.24262 | 0.064086 | 0.23346 | -0.27924 | -0.036621 | 0.013732 | 122.9919 | 122.7585 | 56.9183 | -123.0377 | 122.9782 | 122.9279 | 56.2317 | -123.1567
1598.0156 | 123.0606 | -58.9096 | 63.9771 | -0.19852 | 0.012362 | 0.069319 | 0.073081 | 0.12993 | -0.00071785 | -0.0040867 | -0.10696 | -0.005708 | 0.063837 | 0.059535 | 0.0022858 | -0.0089828 | 63.8123 | 63.9633 | -1.886 | -59.0424 | 64.0457 | -58.9966 | -59.0652 | -58.6761 | -2.4536 | -59.1431 | 64.032 | 63.9633 | -59.0698 | -59.1568 | -0.086975 | -0.15564 | 0.068664 | 122.8729 | -0.13275 | 0.022889 | -0.1648 | -0.16022 | -0.24719 | 0.054931 | 0.23346 | -0.23346 | 0.013733 | -0.013733 | 122.9553 | 122.7219 | 57.0236 | -123.0423 | 122.9416 | 122.8729 | 56.456 | -123.1338
1599.0156 | 122.9645 | -58.9188 | 63.9816 | 0.060882 | 0.014285 | 0.068037 | 0.071158 | 0.13057 | 0.0012047 | -0.0040867 | 0.12955 | -0.0069898 | 0.063196 | 0.059535 | 0.004422 | -0.0074876 | 63.8168 | 63.9313 | -1.9043 | -59.1019 | 64.0274 | -59.0149 | -59.0561 | -58.6899 | -2.5681 | -59.1843 | 64.0137 | 63.9633 | -59.1064 | -59.1751 | -0.096131 | -0.13733 | 0.045777 | 122.85 | -0.18311 | -0.045777 | -0.16479 | -0.18768 | -0.25635 | 0.032044 | 0.22888 | -0.2655 | -0.009155 | -0.01831 | 122.9462 | 122.7356 | 57.0145 | -123.0377 | 122.9324 | 122.8821 | 56.3507 | -123.1567
1600.0156 | 122.9965 | -58.905 | 63.9862 | -0.17563 | 0.011935 | 0.068464 | 0.070303 | 0.13163 | 0.0024865 | -0.0038731 | -0.168 | -0.008058 | 0.065332 | 0.058894 | 0.0035674 | -0.0079148 | 63.8443 | 64.0045 | -1.8631 | -59.0195 | 64.0594 | -58.96 | -59.024 | -58.6395 | -3.1357 | -59.1385 | 64.032 | 63.9771 | -59.079 | -59.111 | -0.054932 | -0.11902 | 0.073242 | 122.9095 | -0.11444 | 0.004578 | -0.14191 | -0.17395 | -0.20599 | 0.045776 | 0.2655 | -0.23346 | -0.027466 | -0.009155 | 122.9645 | 122.7493 | 57.0419 | -123.0103 | 122.937 | 122.8821 | 55.7693 | -123.0972
1601.0156 | 123.0148 | -58.9233 | 63.9816 | -0.03067 | 0.014285 | 0.06825 | 0.073935 | 0.12907 | 0.0016321 | -0.0030185 | 0.09903 | -0.0048536 | 0.064051 | 0.058467 | 0.0037812 | -0.0089828 | 63.8306 | 63.9496 | -1.8265 | -59.0561 | 64.0503 | -58.9737 | -59.0515 | -58.6853 | -2.742 | -59.1751 | 64.0411 | 63.9542 | -59.1019 | -59.1614 | -0.050354 | -0.12817 | 0.068665 | 122.8729 | -0.13275 | -0.004577 | -0.15106 | -0.17853 | -0.23804 | 0.05951 | 0.23804 | -0.25177 | -0.013733 | -0.027465 | 122.9736 | 122.7539 | 57.0969 | -123.0331 | 122.9645 | 122.8775 | 56.1813 | -123.143
1602.0156 | 123.056 | -58.8867 | 64.0091 | -0.168 | 0.016635 | 0.066755 | 0.073294 | 0.12993 | -0.00029045 | -0.0019505 | -0.10696 | -0.0072034 | 0.062982 | 0.056758 | 0.0042084 | -0.0074876 | 63.8489 | 63.9908 | -1.8539 | -59.0012 | 64.0869 | -58.9462 | -59.0057 | -58.6121 | -2.8107 | -59.1064 | 64.064 | 63.9954 | -59.0652 | -59.1431 | -0.059509 | -0.11902 | 0.07782 | 122.8775 | -0.11444 | 0.004577 | -0.16022 | -0.17853 | -0.25635 | 0.054932 | 0.27466 | -0.21973 | 0.036621 | -0.013733 | 122.9736 | 122.7356 | 57.0328 | -123.0148 | 122.9507 | 122.8821 | 56.0761 | -123.1522
1603.0156 | 122.9828 | -58.8959 | 64.0091 | 0.076141 | 0.015353 | 0.068891 | 0.071799 | 0.12822 | 0.0012047 | -0.0055821 | 0.14481 | -0.0050672 | 0.063196 | 0.058894 | 0.004422 | -0.006633 | 63.858 | 63.9587 | -1.6983 | -59.0424 | 64.064 | -58.9233 | -59.0378 | -58.6807 | -2.916 | -59.1751 | 64.0182 | 63.9908 | -59.111 | -59.1431 | -0.027466 | -0.14191 | 0.054932 | 122.8546 | -0.14648 | -0.004577 | -0.15106 | -0.21515 | -0.24719 | 0.009156 | 0.21515 | -0.27924 | -0.032044 | -0.01831 | 122.9599 | 122.7539 | 57.1976 | -123.0469 | 122.9141 | 122.8867 | 55.9799 | -123.1522
1604.0156 | 123.0377 | -58.8776 | 63.9862 | -0.12985 | 0.017062 | 0.065901 | 0.070303 | 0.12928 | -0.0015723 | -0.0038731 | 0.022736 | -0.0059216 | 0.064264 | 0.060816 | 0.0029266 | -0.0087692 | 63.8809 | 64.0274 | -1.8173 | -59.0012 | 64.064 | -58.9417 | -59.0286 | -58.6075 | -3.1906 | -59.111 | 64.0778 | 64.0045 | -59.0652 | -59.111 | -0.064087 | -0.15106 | 0.07782 | 122.905 | -0.1236 | 0.027465 | -0.10529 | -0.18768 | -0.23346 | 0.091553 | 0.27008 | -0.23346 | 0 | 0.018311 | 122.9416 | 122.7585 | 57.0602 | -123.0148 | 122.9553 | 122.8821 | 55.687 | -123.0972
1605.0156 | 122.9645 | -58.9005 | 63.9862 | 0.015106 | 0.01578 | 0.067182 | 0.072226 | 0.12971 | -0.0015723 | -0.0034457 | 0.053253 | -0.0048536 | 0.065546 | 0.05868 | 0.0042084 | -0.0072738 | 63.8351 | 63.9542 | -2.0782 | -59.0515 | 64.0457 | -58.9371 | -59.0149 | -58.6533 | -3.2272 | -59.166 | 64.0503 | 63.9816 | -59.0652 | -59.1385 | -0.036621 | -0.11444 | 0.059509 | 122.8546 | -0.15106 | -0.036621 | -0.15106 | -0.16479 | -0.23804 | 0.064087 | 0.24719 | -0.2655 | -0.027466 | -0.004578 | 122.9462 | 122.7356 | 56.8222 | -123.0011 | 122.9507 | 122.8821 | 55.6732 | -123.1247
1606.0156 | 123.0331 | -58.9233 | 63.9999 | -0.17563 | 0.010653 | 0.068464 | 0.071372 | 0.13142 | -0.00050425 | -0.0057957 | -0.091705 | -0.0089124 | 0.065332 | 0.05868 | 0.002713 | -0.0085556 | 63.7939 | 63.9404 | -1.8997 | -59.0515 | 64.0503 | -58.9737 | -59.0378 | -58.6624 | -3.0808 | -59.1568 | 64.0503 | 63.9633 | -59.0744 | -59.1248 | -0.050354 | -0.11444 | 0.050354 | 122.8638 | -0.12817 | -0.013733 | -0.20599 | -0.15106 | -0.20142 | 0.050354 | 0.26093 | -0.23346 | -0.032043 | -0.036621 | 122.9736 | 122.7173 | 57.0236 | -123.0377 | 122.9736 | 122.8867 | 55.8426 | -123.1247
1607.0156 | 122.9965 | -58.9417 | 63.9313 | -0.076447 | 0.014926 | 0.06825 | 0.071799 | 0.1295 | 0.0022729 | -0.0049411 | 0.060883 | -0.006349 | 0.064691 | 0.058894 | 0.0035674 | -0.010265 | 63.8168 | 63.9313 | -1.7944 | -59.0836 | 64.0091 | -58.9966 | -59.0881 | -58.699 | -3.2135 | -59.2255 | 63.9816 | 63.9313 | -59.1339 | -59.1934 | -0.054932 | -0.14648 | 0.07782 | 122.8729 | -0.14191 | 0.004578 | -0.11444 | -0.19226 | -0.25177 | 0.050354 | 0.24261 | -0.28381 | -0.032044 | 0 | 122.9507 | 122.7585 | 57.1472 | -123.0194 | 122.9233 | 122.8729 | 55.7281 | -123.1247
1608.0156 | 123.0377 | -58.9279 | 63.9908 | -0.21378 | 0.013858 | 0.068678 | 0.071585 | 0.13099 | -0.00071785 | -0.0057957 | -0.12222 | -0.007417 | 0.064264 | 0.05868 | 0.0035674 | -0.0085556 | 63.8214 | 63.9496 | -2.0508 | -59.0469 | 64.0366 | -58.9737 | -59.0515 | -58.667 | -3.2913 | -59.1614 | 64.0182 | 63.9633 | -59.1019 | -59.1751 | -0.045777 | -0.1236 | 0.045776 | 122.8775 | -0.11902 | 0.004578 | -0.16937 | -0.17395 | -0.24719 | 0.027466 | 0.26093 | -0.23346 | 0.013733 | -0.027466 | 122.9645 | 122.7493 | 56.8771 | -123.0423 | 122.9462 | 122.8912 | 55.6366 | -123.1659
1609.0156 | 123.0194 | -58.9508 | 63.9404 | -0.061188 | 0.016421 | 0.066114 | 0.071372 | 0.13057 | 0.0016321 | -0.0053683 | -0.00015237 | -0.0065626 | 0.064051 | 0.05868 | 0.0046356 | -0.0094102 | 63.8443 | 63.9633 | -1.9043 | -59.0881 | 64.0228 | -58.9874 | -59.0836 | -58.6807 | -2.9297 | -59.2072 | 63.9954 | 63.9267 | -59.1293 | -59.1797 | -0.036621 | -0.13275 | 0.082397 | 122.9141 | -0.13733 | -0.004578 | -0.096131 | -0.17853 | -0.22888 | 0.054931 | 0.27008 | -0.25635 | -0.027466 | -0.013733 | 122.9736 | 122.7951 | 57.0465 | -123.024 | 122.9462 | 122.8775 | 56.0211 | -123.1201
1610.0156 | 123.0377 | -58.9462 | 63.9496 | -0.19852 | 0.013003 | 0.066541 | 0.069663 | 0.13185 | 0.00056395 | -0.0057957 | -0.038299 | -0.0042126 | 0.063196 | 0.059535 | 0.0022858 | -0.010692 | 63.8397 | 63.9359 | -1.7761 | -59.0698 | 64.0228 | -58.992 | -59.0881 | -58.6807 | -3.0945 | -59.1751 | 63.9725 | 63.9404 | -59.1431 | -59.1888 | -0.045776 | -0.14191 | 0.073242 | 122.8821 | -0.1236 | 0.018311 | -0.10986 | -0.19684 | -0.24262 | 0.022888 | 0.2655 | -0.22888 | 0.013733 | -0.009155 | 122.9691 | 122.7859 | 57.1701 | -123.0377 | 122.9187 | 122.8867 | 55.8517 | -123.1384
1611.0156 | 122.9965 | -58.9691 | 63.9267 | 0.022736 | 0.014499 | 0.065473 | 0.072653 | 0.12928 | 0.00099115 | -0.0017369 | 0.076141 | -0.006349 | 0.065332 | 0.058894 | 0.004422 | -0.0087692 | 63.7756 | 63.9038 | -1.7212 | -59.1202 | 63.9771 | -59.0103 | -59.1019 | -58.7402 | -3.1586 | -59.2392 | 63.9542 | 63.913 | -59.1568 | -59.1751 | -0.041199 | -0.13275 | 0.050354 | 122.8729 | -0.15106 | -0.01831 | -0.15106 | -0.18768 | -0.20599 | 0.027466 | 0.22888 | -0.27008 | -0.064087 | -0.013733 | 122.9462 | 122.7448 | 57.2479 | -123.0286 | 122.9233 | 122.8821 | 55.8105 | -123.1018
1612.0156 | 123.0194 | -58.9966 | 63.9404 | -0.19089 | 0.011508 | 0.070387 | 0.071585 | 0.12993 | -0.0026405 | -0.0045139 | -0.13748 | -0.0078442 | 0.063196 | 0.057826 | 0.0031402 | -0.0077012 | 63.739 | 63.8809 | -1.767 | -59.111 | 64.0091 | -59.0149 | -59.1156 | -58.7219 | -2.8976 | -59.2117 | 64.0182 | 63.9359 | -59.1431 | -59.1934 | -0.018311 | -0.11902 | 0.068664 | 122.8775 | -0.11444 | 0.004578 | -0.20142 | -0.14648 | -0.19684 | 0.07782 | 0.27466 | -0.21515 | -0.018311 | -0.004578 | 123.0057 | 122.7356 | 57.2296 | -123.056 | 123.0148 | 122.9324 | 56.0989 | -123.1338
1613.0156 | 123.0652 | -58.9645 | 63.9267 | -0.091705 | 0.014071 | 0.067823 | 0.072867 | 0.13206 | 0.0016321 | -0.0045139 | 0.015106 | -0.0048536 | 0.06106 | 0.057185 | 0.0039948 | -0.0081284 | 63.8077 | 63.9267 | -1.712 | -59.0973 | 63.9679 | -59.0195 | -59.111 | -58.754 | -2.9938 | -59.166 | 63.9404 | 63.9038 | -59.1705 | -59.2255 | -0.054931 | -0.14648 | 0.041199 | 122.8912 | -0.13275 | 0.013733 | -0.11902 | -0.20599 | -0.26093 | 0.013733 | 0.21057 | -0.20142 | 0.059509 | -0.022888 | 122.9324 | 122.7722 | 57.2525 | -123.0377 | 122.905 | 122.8683 | 55.9708 | -123.1522
1614.0156 | 123.0652 | -58.9691 | 63.9313 | -0.16037 | 0.012149 | 0.068891 | 0.07244 | 0.12928 | 0.00035035 | -0.0062229 | -0.12222 | -0.007417 | 0.06341 | 0.059321 | 0.0035674 | -0.0089828 | 63.7527 | 63.8992 | -1.9363 | -59.111 | 63.9999 | -59.0332 | -59.1064 | -58.7265 | -2.7557 | -59.1934 | 63.9725 | 63.9359 | -59.1385 | -59.2072 | -0.064087 | -0.13733 | 0.068665 | 122.8683 | -0.14191 | -0.004578 | -0.17853 | -0.16937 | -0.23804 | 0.041199 | 0.24262 | -0.2243 | 0.013733 | 0.004578 | 122.9691 | 122.7219 | 57.0328 | -123.0377 | 122.9416 | 122.905 | 56.2134 | -123.1384
1615.0156 | 123.0011 | -58.9691 | 63.9221 | -0.78598 | 0.015353 | 0.068891 | 0.073294 | 0.12886 | 0.0024865 | -0.0023777 | -0.0077819 | -0.005708 | 0.064478 | 0.057826 | 0.0052764 | -0.0094102 | 63.7985 | 63.9404 | -1.8082 | -59.0881 | 63.9862 | -59.0149 | -59.0698 | -58.699 | -2.8793 | -59.2026 | 63.9816 | 63.8763 | -59.1293 | -59.2117 | -0.045777 | -0.10071 | 0.064087 | 122.9095 | -0.11902 | -0.018311 | -0.1236 | -0.16022 | -0.24262 | 0.059509 | 0.27008 | -0.23346 | 0.009155 | -0.045776 | 122.9553 | 122.7676 | 57.1609 | -122.9919 | 122.9507 | 122.8455 | 56.0898 | -123.1338
1616.0156 | 123.0286 | -58.9874 | 63.9175 | -0.25955 | 0.0097989 | 0.06825 | 0.073721 | 0.12928 | -0.0030677 | -0.0055821 | -0.12222 | -0.0069898 | 0.064691 | 0.058467 | 0.0031402 | -0.0077012 | 63.7573 | 63.8855 | -1.8082 | -59.1156 | 63.9999 | -59.0332 | -59.1339 | -58.7173 | -3.2089 | -59.2072 | 63.9771 | 63.9267 | -59.1339 | -59.2255 | -0.045776 | -0.14648 | 0.082397 | 122.8729 | -0.12817 | 0.01831 | -0.16022 | -0.14648 | -0.23804 | 0.059509 | 0.27008 | -0.21973 | 0.018311 | 0.009155 | 122.9874 | 122.7448 | 57.1793 | -123.0515 | 122.9645 | 122.9141 | 55.7785 | -123.143
1617.0156 | 122.9874 | -58.9691 | 63.9359 | -0.045929 | 0.017917 | 0.065046 | 0.071585 | 0.12822 | 0.00035035 | -0.0040867 | 0.10666 | -0.0078442 | 0.062982 | 0.058467 | 0.00549 | -0.008342 | 63.7848 | 63.9175 | -2.0737 | -59.1019 | 63.9862 | -59.0378 | -59.0744 | -58.7082 | -3.0167 | -59.2438 | 63.9587 | 63.9038 | -59.1385 | -59.2026 | -0.068665 | -0.10529 | 0.050354 | 122.8867 | -0.13275 | -0.027466 | -0.15106 | -0.16937 | -0.23346 | 0.022888 | 0.26093 | -0.27466 | -0.041198 | -0.032043 | 122.9553 | 122.7539 | 56.8954 | -123.0103 | 122.9279 | 122.8729 | 55.9525 | -123.1384
1618.0156 | 123.0469 | -58.9554 | 63.9496 | -0.20615 | 0.011722 | 0.070387 | 0.070731 | 0.13078 | 0.0020593 | -0.0053683 | -0.12985 | -0.0061352 | 0.064051 | 0.060389 | 0.0033538 | -0.008342 | 63.7894 | 63.9404 | -1.8906 | -59.0652 | 64.0228 | -59.0103 | -59.0836 | -58.6716 | -2.9846 | -59.166 | 63.9908 | 63.9359 | -59.1202 | -59.1751 | -0.054932 | -0.12817 | 0.073242 | 122.8958 | -0.10986 | 0.01831 | -0.16022 | -0.1648 | -0.21973 | 0.041199 | 0.28381 | -0.21057 | 0.009155 | -0.013733 | 122.9782 | 122.7448 | 57.0648 | -123.0331 | 122.9462 | 122.8912 | 55.9708 | -123.1247
1619.0156 | 123.0148 | -58.9645 | 63.8992 | 0.11429 | 0.013217 | 0.069746 | 0.070517 | 0.128 | -7.6852e-05 | -0.0036595 | 0.24399 | -0.007417 | 0.060846 | 0.058467 | 0.0039948 | -0.0044968 | 63.7573 | 63.8855 | -2.0645 | -59.111 | 64.0091 | -59.0195 | -59.1019 | -58.6761 | -3.0029 | -59.1888 | 63.9771 | 63.9175 | -59.1202 | -59.1843 | -0.054931 | -0.13733 | 0.10986 | 122.85 | -0.14648 | -0.009155 | -0.14191 | -0.15564 | -0.21973 | 0.07782 | 0.28839 | -0.2243 | -0.004578 | 0.018311 | 122.9736 | 122.7219 | 56.9 | -123.0011 | 122.9416 | 122.8821 | 55.9616 | -123.0835
1620.0156 | 122.9965 | -58.9142 | 63.9725 | -0.23666 | 0.014285 | 0.071027 | 0.07244 | 0.12886 | -0.0028541 | -0.0072911 | -0.14511 | -0.0044264 | 0.063623 | 0.060176 | 0.0024994 | -0.0074876 | 63.7756 | 63.9404 | -2.2064 | -59.0881 | 64.0503 | -58.9737 | -59.0744 | -58.6807 | -3.0853 | -59.166 | 64.0274 | 64.0091 | -59.0836 | -59.166 | -0.059509 | -0.16022 | 0.07782 | 122.8546 | -0.17395 | -0.013733 | -0.19684 | -0.16937 | -0.25177 | 0.054932 | 0.23346 | -0.25177 | 0 | 0.036621 | 122.9645 | 122.6898 | 56.7078 | -123.0469 | 122.9416 | 122.9233 | 55.8289 | -123.1384
1621.0156 | 123.0286 | -58.9371 | 63.9587 | 0.24399 | 0.015353 | 0.067396 | 0.070517 | 0.13142 | -0.00029045 | -0.0049411 | 0.0074766 | -0.005708 | 0.061914 | 0.058039 | 0.0050628 | -0.0096238 | 63.8535 | 63.9816 | -2.1286 | -59.0652 | 64.0182 | -58.9966 | -59.0698 | -58.6304 | -2.8885 | -59.1843 | 63.9816 | 63.9221 | -59.0927 | -59.1797 | -0.059509 | -0.13275 | 0.05951 | 122.9187 | -0.12817 | 0.004577 | -0.10529 | -0.15564 | -0.24261 | 0.022888 | 0.3067 | -0.24719 | -0.004578 | -0.036621 | 122.9553 | 122.7905 | 56.8085 | -123.0286 | 122.9187 | 122.8592 | 56.0486 | -123.1384
1622.0156 | 123.024 | -58.9508 | 63.9633 | -0.15274 | 0.010867 | 0.068464 | 0.069022 | 0.13057 | -0.0011451 | -0.0045139 | -0.16037 | -0.0072034 | 0.064478 | 0.057185 | 0.0031402 | -0.008342 | 63.7711 | 63.9175 | -2.1332 | -59.0836 | 64.0503 | -59.024 | -59.0836 | -58.6761 | -2.4719 | -59.1522 | 64.0228 | 63.9496 | -59.1156 | -59.1843 | -0.073242 | -0.13275 | 0.086975 | 122.8683 | -0.13275 | 0 | -0.19226 | -0.16479 | -0.23346 | 0.059509 | 0.27466 | -0.20142 | 0.032043 | -0.013733 | 123.0011 | 122.7219 | 56.8176 | -123.0469 | 122.9736 | 122.9004 | 56.4789 | -123.1476
1623.0156 | 123.0194 | -58.9325 | 63.9633 | -0.061188 | 0.014712 | 0.06825 | 0.070944 | 0.13014 | 0.0031273 | -0.0051547 | -0.00015237 | -0.0067762 | 0.06341 | 0.059107 | 0.0031402 | -0.0089828 | 63.7024 | 64.0503 | -2.1149 | -59.0652 | 64.0182 | -58.9874 | -59.0744 | -58.6395 | -2.3987 | -59.1751 | 64.0045 | 63.9221 | -59.1248 | -59.1888 | -0.054932 | -0.14191 | 0.054932 | 122.9828 | -0.13275 | 0.009155 | -0.26093 | -0.19226 | -0.25635 | 0.041199 | 0.29297 | -0.24261 | 0.013733 | -0.041199 | 122.9507 | 122.6349 | 56.8176 | -123.0377 | 122.937 | 122.8546 | 56.5338 | -123.1522
1624.0156 | 123.1155 | -58.9142 | 63.8947 | 0.62546 | 0.011508 | 0.067823 | 0.069022 | 0.12993 | -0.0032813 | -0.0045139 | 0.32028 | -0.0078442 | 0.06341 | 0.057398 | 0.0035674 | -0.0096238 | 63.8214 | 63.9954 | -1.9318 | -59.0469 | 63.945 | -58.9737 | -59.0652 | -58.6075 | -2.2659 | -59.1064 | 63.9313 | 63.8626 | -59.1248 | -59.1797 | -0.059509 | -0.15106 | 0.050354 | 122.9095 | -0.13275 | 0.018311 | -0.073242 | -0.21057 | -0.2655 | 0.036621 | 0.3067 | -0.19226 | 0.073242 | -0.032043 | 122.8592 | 122.7356 | 56.9824 | -122.9599 | 122.8455 | 122.7768 | 56.6483 | -123.0743
1625.0156 | 123.0194 | -58.9188 | 63.9404 | -0.0077822 | 0.01578 | 0.067396 | 0.073935 | 0.1295 | 0.0024865 | -0.0043003 | 0.0074766 | -0.005708 | 0.066187 | 0.059321 | 0.0046356 | -0.010265 | 63.8672 | 63.9496 | -1.8494 | -59.0561 | 64.0549 | -58.9691 | -59.0652 | -58.6807 | -2.3163 | -59.198 | 64.0182 | 63.9542 | -59.111 | -59.1522 | -0.050354 | -0.14648 | 0.11444 | 122.8683 | -0.13733 | 0.009156 | -0.073243 | -0.19226 | -0.23346 | 0.07782 | 0.23804 | -0.27924 | -0.045776 | 0.013733 | 122.9736 | 122.7859 | 57.0694 | -123.0057 | 122.937 | 122.8729 | 56.6025 | -123.0927
1626.0156 | 122.9599 | -58.9142 | 63.9771 | -0.35873 | 0.0093717 | 0.068891 | 0.070731 | 0.12864 | -0.0019995 | -0.0064365 | -0.12222 | -0.0078442 | 0.064691 | 0.058039 | 0.0022858 | -0.0081284 | 63.8306 | 63.945 | -1.7899 | -59.0607 | 64.0594 | -58.9691 | -59.0424 | -58.6716 | -2.6413 | -59.1843 | 64.032 | 63.9908 | -59.1019 | -59.1385 | -0.054931 | -0.12817 | 0.082397 | 122.8592 | -0.14648 | -0.018311 | -0.14649 | -0.18768 | -0.2243 | 0.054931 | 0.24262 | -0.27008 | -0.045776 | 0.013733 | 122.9736 | 122.7448 | 57.1243 | -123.0194 | 122.9462 | 122.905 | 56.2729 | -123.1155
1627.0156 | 123.0148 | -58.9325 | 63.9404 | -0.091705 | 0.014926 | 0.06761 | 0.072867 | 0.13185 | 0.0039819 | -0.0051547 | 0.030365 | -0.0065626 | 0.063837 | 0.059321 | 0.0039948 | -0.0094102 | 63.8489 | 63.9633 | -1.5106 | -59.079 | 64.0137 | -58.9554 | -59.0424 | -58.667 | -2.6733 | -59.2072 | 64.0182 | 63.9359 | -59.1339 | -59.166 | -0.022888 | -0.10986 | 0.073242 | 122.8958 | -0.14648 | -0.036621 | -0.091553 | -0.20142 | -0.23346 | 0.07782 | 0.2655 | -0.27466 | -0.041198 | -0.004578 | 122.9462 | 122.7814 | 57.4219 | -122.9828 | 122.9507 | 122.8683 | 56.2592 | -123.1064
1628.0156 | 123.0423 | -58.96 | 63.9725 | -0.16037 | 0.011081 | 0.068464 | 0.069449 | 0.13057 | -0.0013587 | -0.0047275 | -0.16037 | -0.0069898 | 0.063196 | 0.058894 | 0.0039948 | -0.0074876 | 63.8031 | 63.9175 | -1.6251 | -59.0836 | 64.0366 | -58.9828 | -59.0424 | -58.6899 | -2.8061 | -59.1797 | 63.9999 | 63.9267 | -59.1293 | -59.1568 | -0.022888 | -0.082397 | 0.064087 | 122.8775 | -0.1236 | -0.041199 | -0.16937 | -0.16937 | -0.19684 | 0.027466 | 0.27008 | -0.21973 | -0.022888 | -0.045776 | 122.9965 | 122.7631 | 57.3349 | -123.0148 | 122.9599 | 122.8867 | 56.1539 | -123.1293
1629.0156 | 123.0972 | -58.9737 | 63.8306 | 0.16769 | 0.012576 | 0.066328 | 0.068167 | 0.13121 | -0.00071785 | -0.0047275 | 0.30502 | -0.011049 | 0.063623 | 0.060389 | 0.0042084 | -0.0094102 | 63.7665 | 63.9359 | -1.5472 | -59.1064 | 63.8901 | -59.0424 | -59.1385 | -58.6853 | -2.3346 | -59.2026 | 63.8763 | 63.8123 | -59.1568 | -59.1934 | -0.068664 | -0.16479 | 0.05951 | 122.9095 | -0.13275 | 0.032044 | -0.064087 | -0.1831 | -0.21973 | 0.045777 | 0.28839 | -0.22888 | -0.009156 | -0.01831 | 122.8638 | 122.7402 | 57.4265 | -122.9691 | 122.85 | 122.7859 | 56.6391 | -123.024
1630.0156 | 123.0148 | -58.9966 | 63.8992 | -0.20615 | 0.013858 | 0.068678 | 0.071799 | 0.13057 | -0.0013587 | -0.0036595 | -0.16037 | -0.0048536 | 0.062982 | 0.058894 | 0.0037812 | -0.0087692 | 63.7299 | 63.8397 | -1.7303 | -59.1385 | 63.9771 | -59.0607 | -59.1385 | -58.7585 | -2.7283 | -59.23 | 63.9542 | 63.8901 | -59.1568 | -59.2392 | -0.064087 | -0.14191 | 0.07782 | 122.8363 | -0.14191 | 0 | -0.16937 | -0.16022 | -0.24262 | 0.054932 | 0.23804 | -0.23346 | 0.009155 | -0.009155 | 122.9736 | 122.7264 | 57.2662 | -123.0377 | 122.9507 | 122.8867 | 56.2683 | -123.1384
1631.0156 | 123.0286 | -58.96 | 63.945 | -0.0077822 | 0.014712 | 0.068891 | 0.073294 | 0.13035 | 0.0018457 | -0.0045139 | 0.076141 | -0.007417 | 0.06341 | 0.059962 | 0.0039948 | -0.010478 | 63.8123 | 63.8901 | -1.5427 | -59.0881 | 63.9999 | -59.0012 | -59.1019 | -58.7082 | -2.7283 | -59.2346 | 63.9999 | 63.9359 | -59.1293 | -59.198 | -0.041199 | -0.14191 | 0.054932 | 122.85 | -0.12817 | 0.013733 | -0.13275 | -0.16937 | -0.23804 | 0.054932 | 0.25177 | -0.27466 | -0.036621 | -0.009155 | 122.9599 | 122.7722 | 57.4173 | -123.0469 | 122.9599 | 122.8958 | 56.2317 | -123.143
1632.0156 | 123.0606 | -58.9737 | 63.9359 | -0.22141 | 0.013644 | 0.067823 | 0.071799 | 0.13057 | -0.0013587 | -0.0025913 | -0.12222 | -0.006349 | 0.061487 | 0.059962 | 0.0039948 | -0.0087692 | 63.7802 | 63.9404 | -1.5884 | -59.0881 | 63.9999 | -59.024 | -59.111 | -58.6899 | -2.5772 | -59.1797 | 63.9816 | 63.9313 | -59.1431 | -59.2026 | -0.050354 | -0.13733 | 0.064087 | 122.9141 | -0.11444 | 0.022888 | -0.15564 | -0.16937 | -0.22888 | 0.045776 | 0.28381 | -0.20599 | 0.022889 | -0.004578 | 122.9736 | 122.7539 | 57.3853 | -123.0469 | 122.9553 | 122.905 | 56.3965 | -123.1384
1633.0156 | 123.0515 | -58.9371 | 63.9542 | -0.076447 | 0.014071 | 0.067182 | 0.069876 | 0.13035 | 0.00099115 | -0.0038731 | -0.015411 | -0.0067762 | 0.065119 | 0.060816 | 0.002713 | -0.010265 | 63.8397 | 63.9862 | -1.7578 | -59.0652 | 64.0182 | -58.9966 | -59.0881 | -58.7128 | -2.7969 | -59.1843 | 63.9954 | 63.9313 | -59.111 | -59.1751 | -0.059509 | -0.15106 | 0.064087 | 122.9233 | -0.12817 | 0.022888 | -0.11444 | -0.17395 | -0.23804 | 0.041198 | 0.2243 | -0.24719 | -0.009155 | -0.022889 | 122.9553 | 122.7768 | 57.1793 | -123.0423 | 122.9324 | 122.8683 | 56.1401 | -123.1293
1634.0156 | 123.0927 | -58.9188 | 63.8947 | 0.13718 | 0.0087307 | 0.065901 | 0.069449 | 0.12822 | -0.0032813 | -0.0040867 | 0.22873 | -0.009126 | 0.061273 | 0.05633 | 0.0050628 | -0.0070602 | 63.8168 | 63.9816 | -1.5198 | -59.2804 | 63.8901 | -59.0378 | -59.1202 | -58.6121 | -2.6184 | -59.1476 | 63.9313 | 63.858 | -59.1293 | -59.1705 | -0.11902 | -0.20142 | -0.004577 | 122.9004 | -0.36163 | -0.16022 | -0.07782 | -0.21057 | -0.25177 | 0.036621 | 0.3067 | -0.22888 | 0.022888 | -0.036621 | 122.8088 | 122.7356 | 57.399 | -123.0148 | 122.85 | 122.7768 | 56.3004 | -123.0652
1635.0156 | 123.0103 | -58.9096 | 63.9267 | -1.1522 | 0.017489 | 0.068464 | 0.075217 | 0.13099 | 0.0016321 | -0.0032321 | -0.023041 | -0.005708 | 0.063623 | 0.058467 | 0.0035674 | -0.0096238 | 63.8489 | 63.9725 | -1.712 | -59.0378 | 64.0732 | -58.96 | -59.0286 | -58.6624 | -2.6321 | -59.1843 | 64.0182 | 63.9404 | -59.0881 | -59.1476 | -0.050354 | -0.11902 | 0.14648 | 122.8821 | -0.12817 | -0.009156 | -0.07782 | -0.17853 | -0.23804 | 0.091553 | 0.24719 | -0.27466 | -0.036621 | 0.013733 | 122.9828 | 122.7585 | 57.1976 | -122.9553 | 122.9279 | 122.85 | 56.2775 | -123.0743
1636.0156 | 123.0148 | -58.9096 | 64.0091 | -0.23666 | 0.012362 | 0.069532 | 0.072012 | 0.128 | -0.0015723 | -0.0038731 | -0.13748 | -0.0067762 | 0.064051 | 0.059535 | 0.0018584 | -0.0077012 | 63.8351 | 63.9633 | -2.0782 | -59.0424 | 64.0778 | -58.9645 | -59.0286 | -58.6487 | -2.6321 | -59.1431 | 64.0732 | 64.0091 | -59.0515 | -59.1248 | -0.054932 | -0.11902 | 0.068665 | 122.8729 | -0.13275 | -0.013733 | -0.17395 | -0.14191 | -0.21515 | 0.064087 | 0.26093 | -0.23346 | -0.01831 | 0 | 122.9874 | 122.7448 | 56.8314 | -123.0377 | 122.9828 | 122.9187 | 56.2775 | -123.1338
1637.0156 | 123.0286 | -58.8867 | 64.0228 | -0.0383 | 0.015353 | 0.066969 | 0.071799 | 0.13142 | 0.0029137 | -0.0043003 | 0.083771 | -0.0061352 | 0.064264 | 0.059748 | 0.0052764 | -0.0096238 | 63.8809 | 64.0137 | -2.1469 | -59.024 | 64.0961 | -58.9233 | -59.024 | -58.6395 | -2.5497 | -59.1431 | 64.0549 | 64.0091 | -59.0836 | -59.111 | -0.036621 | -0.13733 | 0.073242 | 122.9004 | -0.13733 | 0 | -0.14191 | -0.19684 | -0.2243 | 0.032044 | 0.24719 | -0.25635 | -0.032043 | -0.013733 | 122.9828 | 122.7676 | 56.7398 | -123.0469 | 122.9416 | 122.8958 | 56.337 | -123.1339
1638.0156 | 123.0652 | -58.8089 | 64.0823 | -0.18326 | 0.01514 | 0.06761 | 0.071158 | 0.13014 | 0.00099115 | -0.0057957 | -0.13748 | -0.0084852 | 0.061914 | 0.05868 | 0.0039948 | -0.010478 | 63.9221 | 64.0594 | -2.2797 | -58.9508 | 64.1418 | -58.8913 | -58.96 | -58.5617 | -2.7786 | -59.0515 | 64.1373 | 64.0549 | -59.0103 | -59.0195 | -0.082397 | -0.15106 | 0.05951 | 122.8683 | -0.14191 | 0.009155 | -0.16022 | -0.20142 | -0.21057 | 0.054932 | 0.24719 | -0.24262 | -0.032044 | -0.027465 | 122.9507 | 122.731 | 56.5292 | -123.0423 | 122.9462 | 122.8638 | 56.0303 | -123.1018
1639.0156 | 123.1018 | -58.8547 | 63.9816 | 0.21347 | 0.012362 | 0.066328 | 0.073294 | 0.12843 | 0.00013675 | -0.0034457 | 0.28214 | -0.008058 | 0.063623 | 0.055903 | 0.0022858 | -0.0077012 | 63.8809 | 64.0274 | -2.1561 | -59.0103 | 64.0778 | -58.8913 | -58.9966 | -58.5617 | -2.6321 | -59.0424 | 64.0091 | 63.9359 | -59.0332 | -59.0698 | -0.036621 | -0.14191 | 0.096131 | 122.8821 | -0.15564 | -0.013733 | -0.10071 | -0.17853 | -0.21515 | 0.027466 | 0.29297 | -0.18768 | 0.027466 | -0.045776 | 122.9324 | 122.7356 | 56.6986 | -122.9782 | 122.8638 | 122.7905 | 56.2225 | -123.0515
1640.0156 | 123.024 | -58.8226 | 64.119 | -0.24429 | 0.010867 | 0.069959 | 0.073294 | 0.13057 | -0.0045631 | -0.0075047 | -0.54184 | -0.0086988 | 0.064264 | 0.059107 | 0.0042084 | -0.0081284 | 63.9267 | 64.0594 | -2.243 | -58.8455 | 64.1876 | -58.8226 | -58.9005 | -58.58 | -2.774 | -59.0515 | 64.1464 | 64.1052 | -58.992 | -59.0424 | 0 | -0.07782 | 0.068664 | 122.8821 | -0.022888 | 0.054932 | -0.19226 | -0.16937 | -0.21973 | 0.027465 | 0.24262 | -0.22888 | -0.009156 | -0.013733 | 123.0103 | 122.7493 | 56.5796 | -123.0194 | 122.9691 | 122.9279 | 56.0486 | -123.1613
1641.0156 | 123.0469 | -58.7219 | 64.1602 | -0.16037 | 0.01279 | 0.069319 | 0.072012 | 0.12822 | -0.0013587 | -0.0023777 | -0.076446 | -0.007417 | 0.064691 | 0.058253 | 0.0037812 | -0.010478 | 64.0366 | 64.1693 | -2.2522 | -58.8593 | 64.2563 | -58.7952 | -58.8638 | -58.461 | -2.6505 | -58.9508 | 64.2197 | 64.1144 | -58.9096 | -58.96 | -0.073242 | -0.14191 | 0.096131 | 122.8912 | -0.13733 | 0.004578 | -0.1236 | -0.18768 | -0.23804 | 0.05951 | 0.26093 | -0.22888 | 0.009155 | -0.045776 | 122.9782 | 122.7585 | 56.4697 | -123.024 | 122.9416 | 122.8363 | 56.0715 | -123.1201
1642.0156 | 123.0011 | -58.7631 | 64.1785 | -0.32059 | 0.010867 | 0.06825 | 0.071585 | 0.13121 | -0.0011451 | -0.0057957 | -0.023041 | -0.0067762 | 0.063196 | 0.057612 | 0.0039948 | -0.0077012 | 63.9496 | 64.1281 | -2.1149 | -58.8638 | 64.2517 | -58.786 | -58.873 | -58.493 | -2.8656 | -58.9828 | 64.2059 | 64.1647 | -58.9096 | -58.9554 | -0.022888 | -0.10986 | 0.073242 | 122.8912 | -0.10071 | 0.009155 | -0.22888 | -0.14648 | -0.19226 | 0.027466 | 0.27008 | -0.21973 | -0.027466 | -0.013733 | 123.0148 | 122.7127 | 56.6483 | -123.0515 | 122.9691 | 122.9279 | 55.8975 | -123.1338
1643.0156 | 123.0148 | -58.754 | 64.1464 | -0.16037 | 0.013644 | 0.068037 | 0.07244 | 0.12886 | -0.00071785 | -0.0049411 | 0.015106 | -0.0069898 | 0.061701 | 0.059107 | 0.0039948 | -0.0098374 | 64.0274 | 64.1739 | -2.2156 | -58.8364 | 64.2471 | -58.7769 | -58.8776 | -58.4656 | -3.5934 | -58.9691 | 64.2059 | 64.1144 | -58.9188 | -58.9783 | -0.022888 | -0.1236 | 0.10071 | 122.9279 | -0.082398 | 0.041198 | -0.11902 | -0.16479 | -0.2243 | 0.05951 | 0.28839 | -0.21515 | 0.009155 | -0.032043 | 123.0011 | 122.7814 | 56.5384 | -123.024 | 122.9599 | 122.8683 | 55.1605 | -123.1247
1644.0156 | 123.0194 | -58.7677 | 64.1373 | -0.24429 | 0.01279 | 0.069746 | 0.070731 | 0.13121 | -0.0017859 | -0.0070773 | -0.11459 | -0.0072034 | 0.063623 | 0.056971 | 0.0020722 | -0.0059922 | 63.945 | 64.0869 | -1.9318 | -58.9142 | 64.2105 | -58.8409 | -58.9188 | -58.548 | -3.4195 | -59.0195 | 64.2014 | 64.0915 | -58.9462 | -59.0149 | -0.073242 | -0.15106 | 0.073242 | 122.8546 | -0.14649 | 0.004577 | -0.19226 | -0.17853 | -0.24719 | 0.064087 | 0.21973 | -0.25177 | -0.004577 | -0.045776 | 122.9782 | 122.7127 | 56.8359 | -123.056 | 122.9691 | 122.8592 | 55.3482 | -123.1522
1645.0156 | 123.0606 | -58.7769 | 64.0869 | -0.084076 | 0.015567 | 0.068037 | 0.071799 | 0.13014 | -0.00029045 | -0.0051547 | -0.076446 | -0.0052808 | 0.065759 | 0.056544 | 0.0024994 | -0.010051 | 63.9908 | 64.1281 | -1.7944 | -58.905 | 64.1739 | -58.8272 | -58.9142 | -58.5022 | -3.0396 | -59.0195 | 64.1602 | 64.0823 | -58.9508 | -59.0149 | -0.050354 | -0.13733 | 0.086975 | 122.905 | -0.12817 | 0.009156 | -0.09613 | -0.17395 | -0.23804 | 0.073242 | 0.27466 | -0.24262 | -0.004577 | -0.004578 | 122.9507 | 122.7676 | 56.9824 | -123.0011 | 122.937 | 122.8592 | 55.7373 | -123.1018
1646.0156 | 122.9691 | -58.7357 | 64.1693 | -0.22141 | 0.0095853 | 0.0706 | 0.070303 | 0.12886 | -0.0045631 | -0.0057957 | -0.038299 | -0.008058 | 0.064264 | 0.058894 | 0.0042084 | -0.0077012 | 63.9862 | 64.1144 | -1.8311 | -58.8959 | 64.2517 | -58.7997 | -58.8455 | -58.5114 | -3.035 | -58.992 | 64.1876 | 64.1418 | -58.9371 | -58.9828 | -0.064087 | -0.10986 | 0.082397 | 122.85 | -0.16022 | -0.050354 | -0.18311 | -0.20142 | -0.24719 | 0.01831 | 0.2243 | -0.25635 | -0.009155 | -0.027466 | 122.9874 | 122.7219 | 56.9046 | -123.0148 | 122.9233 | 122.8775 | 55.7007 | -123.1522
1647.0156 | 123.024 | -58.7448 | 64.1602 | -0.00015269 | 0.011508 | 0.069746 | 0.069876 | 0.12928 | -0.00093145 | -0.0072911 | -0.10696 | -0.005708 | 0.066187 | 0.060389 | 0.0016448 | -0.0059922 | 63.9771 | 64.119 | -1.6891 | -58.8913 | 64.2746 | -58.7952 | -58.8821 | -58.5205 | -2.9343 | -58.9966 | 64.2105 | 64.1327 | -58.9233 | -58.9828 | -0.050354 | -0.13733 | 0.11444 | 122.8638 | -0.14648 | -0.009155 | -0.1831 | -0.17853 | -0.23804 | 0.050354 | 0.2243 | -0.25177 | -0.013733 | -0.027466 | 123.0194 | 122.7219 | 57.0557 | -123.0423 | 122.9553 | 122.8775 | 55.8105 | -123.143
1648.0156 | 123.024 | -58.6945 | 64.2014 | -0.24429 | 0.0089443 | 0.069105 | 0.07009 | 0.13057 | -0.0045631 | -0.0077183 | -0.11459 | -0.0099806 | 0.063623 | 0.057398 | 0.0014312 | -0.0081284 | 64.0274 | 64.2151 | -1.9089 | -58.8272 | 64.2609 | -58.7311 | -58.8089 | -58.4885 | -2.9388 | -58.9371 | 64.2654 | 64.2014 | -58.8776 | -58.9279 | -0.036621 | -0.11444 | 0.059509 | 122.9095 | -0.13275 | -0.01831 | -0.17395 | -0.18311 | -0.23346 | 0.064087 | 0.20599 | -0.24262 | -0.009156 | 0 | 122.9553 | 122.7219 | 56.7856 | -123.0103 | 122.9599 | 122.8958 | 55.7556 | -123.1293
1649.0469 | 123.1247 | -58.6853 | 64.1464 | -0.061188 | 0.010867 | 0.068037 | 0.071799 | 0.1295 | -0.0069129 | -0.0053683 | 0.045624 | -0.011476 | 0.062555 | 0.057398 | 0.0012176 | -0.0096238 | 64.0137 | 64.2288 | -1.9958 | -58.8181 | 64.2151 | -58.7402 | -58.8409 | -58.4244 | -3.067 | -58.8638 | 64.1464 | 64.0869 | -58.905 | -58.9554 | -0.054931 | -0.15564 | 0.068665 | 122.9141 | -0.13275 | 0.022888 | -0.13275 | -0.21973 | -0.27008 | 0 | 0.26093 | -0.17853 | 0.091552 | -0.059509 | 122.9004 | 122.699 | 56.6895 | -122.9874 | 122.8317 | 122.7722 | 55.6183 | -123.1018
1650.0156 | 123.0469 | -58.6853 | 64.1693 | -0.19852 | 0.0087307 | 0.06761 | 0.070303 | 0.13078 | -0.0049903 | -0.0064365 | -0.11459 | -0.0086988 | 0.062982 | 0.058253 | 0.0046356 | -0.011546 | 64.0778 | 64.238 | -1.8539 | -58.7952 | 64.2654 | -58.754 | -58.8226 | -58.4335 | -3.1265 | -58.8959 | 64.2242 | 64.183 | -58.8638 | -58.905 | -0.068664 | -0.13733 | 0.09613 | 122.9233 | -0.10986 | 0.027466 | -0.091553 | -0.17853 | -0.21973 | 0.054931 | 0.25177 | -0.21057 | 0.009155 | 0.013732 | 122.9507 | 122.7631 | 56.8314 | -122.9919 | 122.9095 | 122.8683 | 55.5588 | -123.0743
1651.0156 | 123.0103 | -58.6624 | 64.2151 | -0.168 | 0.012149 | 0.06761 | 0.072012 | 0.12843 | 0.00056395 | -0.0083591 | -0.18326 | -0.0082716 | 0.065119 | 0.058253 | 0.004422 | -0.011546 | 64.0823 | 64.2105 | -1.8494 | -58.7997 | 64.3158 | -58.7311 | -58.7997 | -58.4335 | -3.3508 | -58.905 | 64.2929 | 64.1968 | -58.8318 | -58.9005 | -0.068664 | -0.13733 | 0.10071 | 122.8729 | -0.13733 | 0 | -0.13275 | -0.16937 | -0.23804 | 0.07782 | 0.22888 | -0.24261 | -0.004577 | -0.018311 | 122.9782 | 122.7448 | 56.8131 | -123.0148 | 122.9553 | 122.8592 | 55.3116 | -123.1155
1652.0156 | 123.0011 | -58.6578 | 64.2197 | -0.22141 | 0.0063809 | 0.069105 | 0.073721 | 0.1327 | -0.0015723 | -0.0062229 | -0.10696 | -0.0095532 | 0.061701 | 0.058894 | 0.0022858 | -0.0077012 | 64.0961 | 64.2654 | -1.712 | -58.786 | 64.27 | -58.6945 | -58.786 | -58.429 | -3.0212 | -58.8684 | 64.27 | 64.2105 | -58.8409 | -58.8959 | -0.036621 | -0.12817 | 0.050354 | 122.9233 | -0.12817 | 0 | -0.1236 | -0.1831 | -0.23804 | 0.050354 | 0.22888 | -0.21057 | 0.027466 | -0.009156 | 122.9279 | 122.7539 | 56.9458 | -123.0057 | 122.9279 | 122.8683 | 55.6366 | -123.1155
1653.0156 | 122.9919 | -58.6578 | 64.2334 | 1.4189 | 0.013644 | 0.068678 | 0.074362 | 0.13014 | -7.6852e-05 | -0.0032321 | -0.15274 | -0.006349 | 0.064264 | 0.058253 | 0.004422 | -0.0074876 | 64.0778 | 64.1739 | -1.8265 | -58.8181 | 64.3112 | -58.7402 | -58.786 | -58.4381 | -3.4378 | -58.9233 | 64.2746 | 64.1968 | -58.8455 | -58.9096 | -0.082397 | -0.12817 | 0.07782 | 122.8317 | -0.16022 | -0.032043 | -0.15564 | -0.18768 | -0.25177 | 0.041199 | 0.21973 | -0.2655 | -0.013733 | -0.036621 | 122.9691 | 122.7356 | 56.8314 | -123.0194 | 122.9324 | 122.8546 | 55.22 | -123.143
1654.0156 | 123.1155 | -58.5983 | 64.2242 | -0.17563 | 0.0068081 | 0.069105 | 0.072012 | 0.1327 | -0.0056311 | -0.0060093 | -0.061188 | -0.016389 | 0.061914 | 0.060176 | 0.006131 | -0.010051 | 64.1693 | 64.3982 | -1.68 | -58.6899 | 64.3204 | -58.6578 | -58.7357 | -58.4793 | -2.9709 | -58.8181 | 64.2471 | 64.1602 | -58.7997 | -58.8638 | -0.059509 | -0.13733 | 0.096131 | 122.9965 | -0.091552 | 0.045777 | -0.054931 | -0.20142 | -0.2655 | 0.022888 | 0.11902 | -0.21973 | 0.045777 | -0.064087 | 122.9187 | 122.7676 | 56.9183 | -122.9599 | 122.8455 | 122.7585 | 55.6274 | -123.0881
1655.0156 | 123.0057 | -58.6624 | 64.238 | -0.22903 | 0.0091581 | 0.06761 | 0.069449 | 0.1327 | -0.0015723 | -0.0051547 | -0.14511 | -0.005708 | 0.059992 | 0.060816 | 0.0029266 | -0.0085556 | 64.1006 | 64.2746 | -1.5884 | -58.786 | 64.27 | -58.7173 | -58.786 | -58.4244 | -3.1265 | -58.905 | 64.2609 | 64.1785 | -58.8501 | -58.9188 | -0.054931 | -0.1236 | 0.032044 | 122.937 | -0.1236 | 0 | -0.13733 | -0.18768 | -0.25635 | 0.022888 | 0.23804 | -0.24261 | 0.013733 | -0.059509 | 122.9324 | 122.7631 | 57.074 | -123.024 | 122.9233 | 122.8409 | 55.5359 | -123.1567
1656.0156 | 123.111 | -58.6395 | 64.1785 | -0.168 | 0.0038175 | 0.069319 | 0.064536 | 0.13035 | -0.0054175 | -0.0060093 | -0.023041 | -0.007417 | 0.062128 | 0.05868 | 0.0052764 | -0.0091966 | 64.151 | 64.2334 | -1.5793 | -58.7585 | 64.238 | -58.7494 | -58.7769 | -58.3878 | -2.4078 | -58.8318 | 64.2014 | 64.1373 | -58.8638 | -58.9005 | -0.10986 | -0.13733 | 0.059509 | 122.8729 | -0.11902 | 0.01831 | -0.027466 | -0.22431 | -0.26093 | 0.022888 | 0.25177 | -0.19226 | 0.068665 | -0.041199 | 122.8775 | 122.7905 | 57.0602 | -122.9553 | 122.8409 | 122.7768 | 56.2317 | -123.0789
1657.0156 | 123.024 | -58.6395 | 64.2471 | -0.23666 | 0.0063809 | 0.069959 | 0.069876 | 0.13121 | -0.00029045 | -0.0047275 | -0.15274 | -0.010408 | 0.063623 | 0.060603 | 0.0031402 | -0.0094102 | 64.0869 | 64.2151 | -1.6251 | -58.7631 | 64.3295 | -58.7311 | -58.7952 | -58.429 | -2.8152 | -58.9005 | 64.3158 | 64.1876 | -58.8364 | -58.873 | -0.091553 | -0.15564 | 0.082398 | 122.8546 | -0.1236 | 0.032043 | -0.16022 | -0.19684 | -0.23346 | 0.068665 | 0.21057 | -0.26093 | -0.027466 | -0.059509 | 122.9691 | 122.7264 | 57.0145 | -123.0423 | 122.9553 | 122.8271 | 55.8243 | -123.1201
1658.0156 | 123.111 | -58.5617 | 64.2609 | -0.23666 | 0.0083035 | 0.067182 | 0.069235 | 0.13035 | -0.0032813 | -0.0049411 | -0.15274 | -0.009126 | 0.060846 | 0.059321 | 0.0024994 | -0.0096238 | 64.183 | 64.3982 | -1.3641 | -58.6853 | 64.3433 | -58.6487 | -58.6945 | -58.3054 | -2.8381 | -58.7631 | 64.3066 | 64.2197 | -58.7723 | -58.7997 | -0.086975 | -0.13275 | 0.082398 | 122.9599 | -0.1236 | 0.009155 | -0.07782 | -0.21057 | -0.23804 | 0.045777 | 0.25635 | -0.20142 | 0.036621 | -0.041198 | 122.905 | 122.7448 | 57.1976 | -122.9553 | 122.8683 | 122.7814 | 55.7236 | -123.0606
1659.0156 | 122.9874 | -58.5892 | 64.3066 | -0.20615 | 0.010653 | 0.069105 | 0.073721 | 0.1295 | -0.00071785 | -0.0062229 | -0.21378 | -0.0072034 | 0.063196 | 0.060176 | 0.001004 | -0.0096238 | 64.1235 | 64.2883 | -1.3046 | -58.7585 | 64.3936 | -58.6533 | -58.7448 | -58.2825 | -3.1174 | -58.9462 | 64.3616 | 64.2563 | -58.7631 | -58.8455 | -0.064087 | -0.15564 | 0.086975 | 122.8775 | -0.16937 | -0.013733 | -0.18311 | -0.17395 | -0.25635 | 0.054931 | 0.3067 | -0.35706 | -0.10071 | -0.050354 | 122.9828 | 122.7127 | 57.2845 | -123.0515 | 122.9507 | 122.8455 | 55.4718 | -123.1522
1660.0156 | 123.1476 | -58.5709 | 64.2746 | -0.068817 | 0.0070217 | 0.067823 | 0.070731 | 0.12629 | -0.0045631 | -0.0053683 | -0.053558 | -0.010835 | 0.060205 | 0.058894 | 0.0016448 | -0.0087692 | 64.2059 | 64.3936 | -1.2039 | -58.6761 | 64.3387 | -58.6441 | -58.7173 | -58.2413 | -2.9617 | -58.7082 | 64.2792 | 64.2426 | -58.7265 | -58.8135 | -0.073242 | -0.14648 | 0.064087 | 122.9645 | -0.10529 | 0.041199 | -0.068664 | -0.15564 | -0.24262 | 0.004578 | 0.32959 | -0.13733 | 0.10529 | -0.032043 | 122.9095 | 122.7768 | 57.3669 | -122.9919 | 122.85 | 122.8134 | 55.6091 | -123.0881
1661.0156 | 123.0743 | -58.5892 | 64.2242 | -0.19852 | 0.0093717 | 0.069959 | 0.070944 | 0.12907 | -0.0024269 | -0.0064365 | -0.12985 | -0.0086988 | 0.06106 | 0.057185 | 0.0035674 | -0.0098374 | 64.1647 | 64.3341 | -0.92926 | -58.7357 | 64.3021 | -58.6716 | -58.7494 | -58.3466 | -2.4124 | -58.8089 | 64.2883 | 64.2059 | -58.7997 | -58.8501 | -0.082398 | -0.16022 | 0.07782 | 122.9233 | -0.14649 | 0.013733 | -0.059509 | -0.21057 | -0.26093 | 0.064087 | 0.24261 | -0.21973 | 0.041199 | -0.01831 | 122.8912 | 122.7539 | 57.6599 | -122.9736 | 122.8775 | 122.7951 | 56.1768 | -123.0743
1662.0156 | 123.1338 | -58.6121 | 64.2014 | -0.15274 | 0.0063809 | 0.070387 | 0.071158 | 0.12907 | -0.0026405 | -0.0062229 | -0.20615 | -0.0067762 | 0.063623 | 0.055049 | 0.0042084 | -0.0074876 | 64.1739 | 64.3478 | -0.6958 | -58.7494 | 64.2838 | -58.699 | -58.7677 | -58.3832 | -2.2156 | -58.7677 | 64.2151 | 64.1693 | -58.8135 | -58.8959 | -0.086975 | -0.15564 | 0.082397 | 122.9599 | -0.13733 | 0.01831 | -0.027466 | -0.20142 | -0.28381 | 0.013733 | 0.22888 | -0.15564 | 0.12817 | -0.032043 | 122.8958 | 122.7859 | 57.9163 | -122.9691 | 122.8271 | 122.7814 | 56.3965 | -123.0972
1663.0156 | 123.024 | -58.6349 | 64.2746 | -0.22141 | 0.0091581 | 0.06761 | 0.072226 | 0.12928 | -0.0015723 | -0.0049411 | -0.16037 | -0.0076306 | 0.063196 | 0.059535 | 0.0020722 | -0.0089828 | 64.1235 | 64.3112 | -0.95673 | -58.7631 | 64.3112 | -58.6945 | -58.7677 | -58.3832 | -2.3163 | -58.8684 | 64.3204 | 64.2242 | -58.8089 | -58.873 | -0.059509 | -0.13275 | 0.036621 | 122.9462 | -0.12817 | 0.004577 | -0.15106 | -0.17395 | -0.23804 | 0.045777 | 0.25177 | -0.23346 | 0.004578 | -0.050354 | 122.9462 | 122.7585 | 57.6782 | -123.0423 | 122.9553 | 122.8592 | 56.3187 | -123.1476
1664.0156 | 123.1796 | -58.6212 | 64.2197 | -0.12222 | 0.0057401 | 0.0706 | 0.070517 | 0.12843 | -0.0026405 | -0.0051547 | -0.099335 | -0.010408 | 0.063196 | 0.056544 | 0.0016448 | -0.0089828 | 64.1739 | 64.4119 | -0.88348 | -58.7219 | 64.2929 | -58.6716 | -58.7357 | -58.287 | -2.3849 | -58.7265 | 64.2654 | 64.2059 | -58.7585 | -58.8364 | -0.050354 | -0.11444 | 0.073242 | 123.0331 | -0.10071 | 0.013733 | -0.045777 | -0.13733 | -0.21515 | 0.045776 | 0.33417 | -0.10529 | 0.10986 | -0.013733 | 122.9141 | 122.7951 | 57.7377 | -122.9553 | 122.8867 | 122.8271 | 56.2363 | -123.056
1665.0156 | 122.9828 | -58.5846 | 64.3204 | -0.19089 | 0.0091581 | 0.06825 | 0.071585 | 0.13078 | 0.0024865 | -0.0053683 | -0.21378 | -0.0067762 | 0.061914 | 0.057612 | 0.0048492 | -0.0085556 | 64.183 | 64.2929 | -0.76446 | -58.7448 | 64.4119 | -58.6578 | -58.7265 | -58.3832 | -2.4536 | -58.9142 | 64.4119 | 64.2838 | -58.754 | -58.8272 | -0.073242 | -0.14191 | 0.091552 | 122.8775 | -0.16022 | -0.018311 | -0.13733 | -0.16937 | -0.24261 | 0.091552 | 0.20142 | -0.32959 | -0.086976 | -0.036622 | 122.9965 | 122.7676 | 57.8201 | -123.0469 | 122.9965 | 122.8683 | 56.131 | -123.1476
1666.0156 | 123.1201 | -58.5663 | 64.2883 | 1.2511 | 0.0055265 | 0.071241 | 0.07009 | 0.13035 | -0.0022131 | -0.0053683 | -0.068817 | -0.0078442 | 0.06106 | 0.059321 | 0.0037812 | -0.0087692 | 64.2609 | 64.3616 | -0.60883 | -58.6487 | 64.3478 | -58.6304 | -58.7082 | -58.2687 | -2.8427 | -58.7448 | 64.3066 | 64.2059 | -58.7219 | -58.7997 | -0.064087 | -0.14191 | 0.059509 | 122.9279 | -0.082398 | 0.059509 | -0.027466 | -0.15564 | -0.23346 | 0.018311 | 0.29755 | -0.17853 | 0.054932 | -0.082397 | 122.9141 | 122.8271 | 57.9575 | -122.9965 | 122.8729 | 122.7722 | 55.7236 | -123.0881
1667.0156 | 123.0835 | -58.5709 | 64.3433 | -0.33585 | 0.010867 | 0.069532 | 0.072012 | 0.13163 | -7.6852e-05 | -0.0055821 | -0.2214 | -0.0076306 | 0.064051 | 0.059107 | 0.0035674 | -0.0081284 | 64.151 | 64.3021 | -0.41657 | -58.7357 | 64.389 | -58.667 | -58.7814 | -58.3694 | -3.273 | -58.8409 | 64.3936 | 64.2563 | -58.7677 | -58.8135 | -0.09613 | -0.21057 | 0.045776 | 122.8729 | -0.1648 | 0.045776 | -0.19226 | -0.19684 | -0.24262 | 0.050354 | 0.20142 | -0.27008 | -0.027465 | -0.086975 | 122.9599 | 122.7219 | 58.1543 | -123.1247 | 122.9645 | 122.8271 | 55.2979 | -123.1567
1668.0156 | 123.111 | -58.5526 | 64.2197 | -0.0383 | 0.0050991 | 0.067182 | 0.067099 | 0.12779 | -0.0032813 | -0.0047275 | -0.045929 | -0.0086988 | 0.060419 | 0.058039 | 0.00057682 | -0.010051 | 64.1876 | 64.389 | -0.28839 | -58.7173 | 64.325 | -58.6441 | -58.7448 | -58.2596 | -2.8244 | -58.7219 | 64.2929 | 64.1876 | -58.754 | -58.8409 | -0.091553 | -0.19226 | 0.10528 | 122.9416 | -0.16479 | 0.027466 | -0.032044 | -0.20142 | -0.28839 | 0.073242 | 0.29297 | -0.16937 | 0.11902 | -0.032044 | 122.8775 | 122.7402 | 58.2642 | -122.9645 | 122.8455 | 122.7402 | 55.7281 | -123.0606
1669.0156 | 123.0011 | -58.6029 | 64.2746 | -0.24429 | 0.0072355 | 0.068464 | 0.072867 | 0.13206 | 0.0018457 | -0.0049411 | -0.091705 | -0.0067762 | 0.062555 | 0.05868 | 0.0024994 | -0.010905 | 64.0823 | 64.3112 | -0.14648 | -58.7769 | 64.357 | -58.667 | -58.7494 | -58.4061 | -3.1128 | -58.8821 | 64.3478 | 64.2014 | -58.8135 | -58.873 | -0.064087 | -0.14648 | 0.082398 | 122.9141 | -0.17395 | -0.027465 | -0.19226 | -0.21057 | -0.27008 | 0.073242 | 0.19684 | -0.27924 | -0.009155 | -0.073242 | 122.9599 | 122.6852 | 58.4564 | -123.024 | 122.9507 | 122.8043 | 55.4901 | -123.1476
1670.0156 | 123.0881 | -58.6258 | 64.2014 | -0.18326 | 0.0063809 | 0.070814 | 0.069235 | 0.13014 | -0.0039221 | -0.0043003 | -0.9462 | -0.0086988 | 0.062128 | 0.057612 | 0.0012176 | -0.010692 | 64.1464 | 64.3524 | -0.10071 | -58.7128 | 64.3066 | -58.6807 | -58.7402 | -58.3145 | -3.1265 | -58.7723 | 64.2563 | 64.151 | -58.8089 | -58.8638 | -0.054932 | -0.11444 | 0.10529 | 122.9782 | -0.086976 | 0.027465 | -0.054932 | -0.18311 | -0.23804 | 0.054932 | 0.31128 | -0.14648 | 0.091553 | -0.050354 | 122.9324 | 122.7722 | 58.5251 | -122.9416 | 122.8821 | 122.7768 | 55.4993 | -123.0652
1671.0156 | 123.0148 | -58.6533 | 64.2654 | -0.25955 | 0.0089443 | 0.06825 | 0.074149 | 0.12886 | -0.0013587 | -0.0062229 | 0.037995 | -0.0072034 | 0.06341 | 0.060176 | 0.0031402 | -0.0081284 | 64.1052 | 64.2929 | -0.28381 | -58.786 | 64.325 | -58.6807 | -58.754 | -58.3969 | -3.1677 | -58.8867 | 64.3112 | 64.2197 | -58.8226 | -58.8638 | -0.027466 | -0.10071 | 0.059509 | 122.9462 | -0.13275 | -0.032044 | -0.16022 | -0.16937 | -0.21057 | 0.045776 | 0.25635 | -0.23346 | -0.022888 | -0.045776 | 122.9782 | 122.7585 | 58.3694 | -123.0194 | 122.9645 | 122.8729 | 55.4855 | -123.1293
1672.0156 | 123.0652 | -58.6166 | 64.2563 | -0.21378 | 0.0065945 | 0.067823 | 0.071158 | 0.12843 | -0.0032813 | -0.0043003 | -0.15274 | -0.007417 | 0.060633 | 0.058253 | 0.0020722 | -0.0098374 | 64.1693 | 64.3936 | -0.21973 | -58.7082 | 64.3021 | -58.6395 | -58.7173 | -58.3191 | -3.2181 | -58.7814 | 64.2929 | 64.183 | -58.7814 | -58.8364 | -0.022888 | -0.10071 | 0.045776 | 123.0103 | -0.091553 | 0.009155 | -0.086975 | -0.16479 | -0.21973 | 0.036621 | 0.29755 | -0.16479 | 0.054932 | -0.073243 | 122.9187 | 122.786 | 58.3969 | -122.9736 | 122.9095 | 122.7997 | 55.3986 | -123.0927
1673.0156 | 122.9965 | -58.5983 | 64.3066 | -0.22141 | 0.011935 | 0.069319 | 0.071158 | 0.13121 | 0.0012047 | -0.0051547 | 0.16769 | -0.0082716 | 0.064051 | 0.057398 | 0.0050628 | -0.0098374 | 64.1327 | 64.476 | -0.059509 | -58.7357 | 64.3982 | -58.6487 | -58.7265 | -58.3603 | -3.566 | -58.8593 | 64.3982 | 64.27 | -58.7631 | -58.8318 | -0.050354 | -0.12817 | 0.091552 | 123.0743 | -0.13733 | -0.009156 | -0.17395 | -0.16479 | -0.23346 | 0.091552 | 0.23804 | -0.26093 | -0.027466 | -0.036621 | 122.9965 | 122.731 | 58.5388 | -123.0331 | 122.9965 | 122.8683 | 55.0323 | -123.1384
1674.0156 | 123.1155 | -58.5434 | 64.2609 | -0.17563 | 0.0063809 | 0.070173 | 0.067099 | 0.12971 | -0.0034949 | -0.0045139 | -0.084076 | -0.0069898 | 0.05871 | 0.057826 | 0.0067718 | -0.0091966 | 64.2426 | 64.476 | -0.37994 | -58.6349 | 64.357 | -58.6121 | -58.6899 | -58.4061 | -3.2684 | -58.7311 | 64.3158 | 64.2105 | -58.7402 | -58.7906 | -0.068665 | -0.14648 | 0.096131 | 123.0194 | -0.091553 | 0.054931 | -0.01831 | -0.19684 | -0.24719 | 0.054932 | 0.13733 | -0.18768 | 0.059509 | -0.050354 | 122.9004 | 122.7859 | 58.1635 | -122.9507 | 122.8592 | 122.7539 | 55.275 | -123.0515
1675.0156 | 122.9691 | -58.6075 | 64.3204 | -0.22141 | 0.0093717 | 0.069105 | 0.07244 | 0.12886 | 0.00056395 | -0.0057957 | -0.28244 | -0.006349 | 0.063837 | 0.060176 | 0.0022858 | -0.0077012 | 64.1693 | 64.3524 | -0.1236 | -58.7173 | 64.3753 | -58.6258 | -58.7219 | -58.3557 | -3.392 | -58.8089 | 64.3662 | 64.2563 | -58.7677 | -58.8089 | -0.01831 | -0.11444 | 0.054931 | 122.9599 | -0.10986 | 0.004578 | -0.15106 | -0.16022 | -0.20142 | 0.045776 | 0.25177 | -0.20142 | 0 | -0.064087 | 122.9828 | 122.7768 | 58.4839 | -123.0423 | 122.9736 | 122.8638 | 55.2155 | -123.1293
1676.0156 | 123.0606 | -58.5297 | 64.3066 | -0.18326 | 0.0065945 | 0.069105 | 0.071585 | 0.13099 | -0.0019995 | -0.0040867 | -0.14511 | -0.0084852 | 0.061273 | 0.058253 | 0.0024994 | -0.0081284 | 64.2197 | 64.4531 | 0.013733 | -58.6304 | 64.3799 | -58.6075 | -58.6807 | -58.2687 | -3.0899 | -58.7311 | 64.357 | 64.2517 | -58.7082 | -58.7952 | -0.07782 | -0.15106 | 0.073242 | 122.9828 | -0.10071 | 0.050354 | -0.086975 | -0.17853 | -0.2655 | 0.050354 | 0.26093 | -0.20142 | 0.064087 | -0.054932 | 122.9095 | 122.7493 | 58.5434 | -122.9874 | 122.8867 | 122.7814 | 55.4398 | -123.1018
1677.0156 | 122.9828 | -58.5617 | 64.357 | -0.23666 | 0.010867 | 0.068037 | 0.070944 | 0.13121 | -0.00050425 | -0.0053683 | -0.12985 | -0.0082716 | 0.063623 | 0.058467 | 0.0039948 | -0.010692 | 64.3066 | 64.1464 | -0.6958 | -58.7036 | 64.4119 | -58.6349 | -58.7173 | -58.3282 | -3.2501 | -58.8318 | 64.4165 | 64.2838 | -58.7311 | -58.7952 | -0.073242 | -0.15564 | 0.054931 | 122.7081 | -0.14191 | 0.013733 | -0.050354 | -0.16937 | -0.23346 | 0.059509 | 0.23346 | -0.27008 | -0.036621 | -0.073243 | 122.9736 | 122.8683 | 57.8659 | -123.0743 | 122.9782 | 122.8455 | 55.3116 | -123.1522
1678.0156 | 123.0515 | -58.5617 | 64.3021 | -0.20615 | 0.0065945 | 0.069105 | 0.069876 | 0.13099 | -0.0030677 | -0.0051547 | -0.091705 | -0.0086988 | 0.060846 | 0.058253 | 0.0042084 | -0.0091966 | 64.183 | 64.4165 | -0.1831 | -58.6716 | 64.325 | -58.6121 | -58.667 | -58.3008 | -3.6392 | -58.7769 | 64.3341 | 64.2197 | -58.7585 | -58.8135 | -0.050354 | -0.10529 | 0.022888 | 122.9782 | -0.10986 | -0.004578 | -0.11902 | -0.19684 | -0.25177 | 0.032043 | 0.26093 | -0.21515 | 0.036622 | -0.082397 | 122.8867 | 122.7448 | 58.3786 | -122.9691 | 122.8958 | 122.7814 | 54.9225 | -123.1155
1679.0156 | 123.0743 | -58.6212 | 64.2838 | -0.19852 | 0.013003 | 0.068891 | 0.072867 | 0.1295 | 0.0024865 | -0.0028049 | -0.17563 | -0.0076306 | 0.062555 | 0.061457 | 0.0039948 | -0.010265 | 64.1144 | 64.2883 | -0.14191 | -58.7357 | 64.357 | -58.6624 | -58.7494 | -58.3649 | -3.6026 | -58.8455 | 64.325 | 64.2197 | -58.7723 | -58.8776 | -0.041199 | -0.12817 | 0.073243 | 122.9095 | -0.11444 | 0.013733 | -0.16937 | -0.15106 | -0.25635 | 0.041199 | 0.25635 | -0.2243 | 0.032043 | -0.064086 | 122.9782 | 122.7356 | 58.4793 | -123.0331 | 122.9462 | 122.8409 | 55.0186 | -123.1613
1680.0156 | 122.9965 | -58.5983 | 64.3295 | -0.22141 | 0.0093717 | 0.0706 | 0.071372 | 0.13142 | -0.0028541 | -0.0062229 | -0.14511 | -0.0069898 | 0.061701 | 0.059962 | 0.0042084 | -0.008342 | 64.1052 | 64.3204 | -0.27924 | -58.7448 | 64.3799 | -58.6624 | -58.7402 | -58.3511 | -3.6667 | -58.8272 | 64.3753 | 64.2654 | -58.7723 | -58.8181 | -0.064087 | -0.14191 | 0.050354 | 122.9187 | -0.14648 | -0.004578 | -0.2243 | -0.17395 | -0.21973 | 0.045776 | 0.24719 | -0.22888 | -0.009155 | -0.064087 | 122.9782 | 122.7036 | 58.3191 | -123.0698 | 122.9736 | 122.8638 | 54.9316 | -123.1476
1681.0156 | 123.0011 | -58.5709 | 64.3204 | 0.19058 | 0.013644 | 0.066328 | 0.072226 | 0.12843 | 0.00056395 | -0.0051547 | -0.18326 | -0.0059216 | 0.061914 | 0.059107 | 0.0046356 | -0.008342 | 64.151 | 64.3204 | -0.31586 | -58.7173 | 64.4211 | -58.6716 | -58.7311 | -58.3466 | -3.7811 | -58.8181 | 64.3936 | 64.2517 | -58.754 | -58.8226 | -0.10071 | -0.16022 | 0.10071 | 122.8912 | -0.14648 | 0.013733 | -0.16937 | -0.18311 | -0.25177 | 0.073242 | 0.2243 | -0.24719 | 0.004578 | -0.068665 | 122.9919 | 122.7219 | 58.255 | -123.0515 | 122.9645 | 122.8226 | 54.7897 | -123.143
1682.0156 | 123.0469 | -58.548 | 64.3295 | -0.22141 | 0.0083035 | 0.068678 | 0.069876 | 0.12822 | -0.0028541 | -0.0062229 | -0.12222 | -0.0069898 | 0.063623 | 0.05633 | 0.0016448 | -0.0091966 | 64.1922 | 64.3982 | -0.33875 | -58.6716 | 64.3616 | -58.6029 | -58.6945 | -58.3145 | -3.7857 | -58.7677 | 64.3845 | 64.2883 | -58.7311 | -58.7906 | -0.054931 | -0.14648 | 0.032043 | 122.9462 | -0.1236 | 0.022888 | -0.13733 | -0.1831 | -0.24261 | 0.054931 | 0.23346 | -0.21973 | 0.022888 | -0.041199 | 122.9095 | 122.7402 | 58.2092 | -123.024 | 122.9324 | 122.8363 | 54.7623 | -123.1201
1683.0156 | 123.0194 | -58.6075 | 64.2975 | -0.17563 | 0.012149 | 0.066969 | 0.072012 | 0.12993 | 0.0018457 | -0.0021641 | -0.12985 | -0.0069898 | 0.062342 | 0.05868 | 0.0050628 | -0.0096238 | 64.1556 | 64.3204 | -0.46234 | -58.7219 | 64.3982 | -58.6578 | -58.7494 | -58.3328 | -4.2664 | -58.8272 | 64.3478 | 64.2288 | -58.7814 | -58.8593 | -0.050354 | -0.14191 | 0.10071 | 122.9279 | -0.11444 | 0.027466 | -0.14191 | -0.17395 | -0.25177 | 0.050354 | 0.27466 | -0.21973 | 0.032044 | -0.068664 | 123.0057 | 122.7631 | 58.1451 | -123.0469 | 122.9553 | 122.8363 | 54.3411 | -123.1567
1684.0156 | 122.9736 | -58.5892 | 64.3387 | -0.22903 | 0.0091581 | 0.071455 | 0.071585 | 0.13014 | -0.0022131 | -0.0045139 | -0.168 | -0.0084852 | 0.060205 | 0.05868 | 0.0016448 | -0.0077012 | 64.1144 | 64.3112 | -0.48981 | -58.7357 | 64.3845 | -58.6487 | -58.7082 | -58.4564 | -4.2938 | -58.8181 | 64.4073 | 64.2563 | -58.7631 | -58.8135 | -0.05951 | -0.11902 | 0.045776 | 122.9004 | -0.14649 | -0.027466 | -0.2243 | -0.17395 | -0.22431 | 0.068665 | 0.13275 | -0.22888 | -0.004577 | -0.082397 | 122.9736 | 122.7036 | 58.0994 | -123.0469 | 122.9965 | 122.8455 | 54.2953 | -123.1522
1685.0156 | 123.0377 | -58.5663 | 64.3158 | -0.19852 | 0.013003 | 0.068678 | 0.069022 | 0.12971 | 0.00077755 | -0.0028049 | -0.168 | -0.0065626 | 0.063196 | 0.059962 | 0.0050628 | -0.010265 | 64.1876 | 64.3387 | -0.68665 | -58.699 | 64.4165 | -58.6487 | -58.7173 | -58.3145 | -3.9276 | -58.7906 | 64.3707 | 64.2517 | -58.7448 | -58.8089 | -0.082398 | -0.15106 | 0.10071 | 122.905 | -0.13275 | 0.01831 | -0.12817 | -0.17853 | -0.24261 | 0.054932 | 0.25177 | -0.2243 | 0.018311 | -0.064087 | 122.9828 | 122.7539 | 57.8796 | -123.0331 | 122.937 | 122.818 | 54.6387 | -123.1247
1686.0156 | 123.0286 | -58.6395 | 64.2609 | -0.16037 | 0.014285 | 0.068037 | 0.07244 | 0.1295 | 0.0018457 | -0.0036595 | -0.023041 | -0.0067762 | 0.064478 | 0.060816 | 0.004422 | -0.010051 | 64.1739 | 64.3478 | -0.70038 | -58.7173 | 64.3707 | -58.6487 | -58.7585 | -58.3374 | -3.9597 | -58.8135 | 64.3295 | 64.2517 | -58.7723 | -58.8501 | -0.009156 | -0.11902 | 0.10986 | 122.9874 | -0.07782 | 0.041199 | -0.086975 | -0.13275 | -0.21057 | 0.068665 | 0.30212 | -0.17395 | 0.036621 | -0.009155 | 123.0103 | 122.8134 | 57.9391 | -123.0194 | 122.9691 | 122.8912 | 54.6799 | -123.111
1687.0156 | 123.0194 | -58.6304 | 64.2654 | 0.10666 | 0.016635 | 0.067396 | 0.071585 | 0.13078 | 0.0024865 | 0.00061314 | -0.03067 | -0.0059216 | 0.061914 | 0.059962 | 0.0048492 | -0.010051 | 64.1693 | 64.3021 | -0.60425 | -58.7585 | 64.3478 | -58.6578 | -58.7723 | -58.3511 | -4.0558 | -58.8638 | 64.3158 | 64.238 | -58.7906 | -58.8593 | -0.027466 | -0.14191 | 0.082397 | 122.9324 | -0.12817 | 0.013733 | -0.09613 | -0.16022 | -0.22888 | 0.050354 | 0.27924 | -0.23346 | -0.004578 | -0.027466 | 122.9782 | 122.7997 | 58.0261 | -123.0377 | 122.9462 | 122.8683 | 54.5746 | -123.1247
1688.0156 | 123.0057 | -58.5571 | 64.3387 | -0.25192 | 0.0091581 | 0.067182 | 0.069876 | 0.13099 | -0.0041357 | -0.0055821 | -0.099335 | -0.0082716 | 0.064051 | 0.057826 | 0.0018584 | -0.0077012 | 64.151 | 64.2654 | -0.63629 | -58.7128 | 64.4119 | -58.6212 | -58.7082 | -58.3603 | -4.1199 | -58.8043 | 64.4073 | 64.3204 | -58.7311 | -58.7723 | -0.064087 | -0.15106 | 0.073242 | 122.8226 | -0.15564 | -0.004578 | -0.18768 | -0.17395 | -0.21515 | 0.068665 | 0.19684 | -0.24719 | -0.032043 | -0.01831 | 122.9691 | 122.7081 | 57.9208 | -123.0469 | 122.9645 | 122.8775 | 54.4373 | -123.111
1689.0156 | 123.0835 | -58.5388 | 64.3753 | -0.045929 | 0.013858 | 0.068891 | 0.072226 | 0.13078 | 0.00056395 | -0.0045139 | -0.10696 | -0.006349 | 0.062982 | 0.057612 | 0.004422 | -0.0087692 | 64.2242 | 64.389 | -0.45319 | -58.6624 | 64.4211 | -58.5754 | -58.667 | -58.2825 | -4.1153 | -58.7402 | 64.4165 | 64.3387 | -58.7265 | -58.7769 | -0.036621 | -0.12817 | 0.045777 | 122.9279 | -0.1236 | 0.004577 | -0.15106 | -0.18768 | -0.23804 | 0.041199 | 0.25635 | -0.20142 | 0.036621 | -0.036621 | 122.9599 | 122.7631 | 58.0856 | -123.0423 | 122.9553 | 122.8775 | 54.4235 | -123.1522
1690.0156 | 123.0652 | -58.5342 | 64.357 | -0.17563 | 0.011722 | 0.069532 | 0.074362 | 0.12907 | -0.0013587 | -0.0036595 | -0.18326 | -0.0082716 | 0.062982 | 0.057398 | 0.0022858 | -0.0077012 | 64.1968 | 64.357 | -0.40741 | -58.6533 | 64.4485 | -58.5892 | -58.6624 | -58.3099 | -3.9322 | -58.7357 | 64.4165 | 64.3341 | -58.7082 | -58.7677 | -0.054931 | -0.12817 | 0.091552 | 122.8912 | -0.11902 | 0.009156 | -0.16022 | -0.17395 | -0.23346 | 0.059509 | 0.2243 | -0.20142 | 0.032043 | -0.022889 | 122.9828 | 122.731 | 58.1268 | -123.0194 | 122.9507 | 122.8683 | 54.6021 | -123.1247
1691.0156 | 123.024 | -58.548 | 64.3753 | -0.0383 | 0.01514 | 0.069959 | 0.071799 | 0.12928 | 0.0012047 | -0.0040867 | 0.060883 | -0.0067762 | 0.064905 | 0.058894 | 0.0067718 | -0.010692 | 64.2242 | 64.3616 | -0.41657 | -58.6807 | 64.4302 | -58.5938 | -58.667 | -58.3099 | -4.4449 | -58.8089 | 64.4073 | 64.2975 | -58.7036 | -58.7631 | -0.045776 | -0.11902 | 0.054932 | 122.9095 | -0.13275 | -0.013733 | -0.15106 | -0.15564 | -0.21515 | 0.032044 | 0.23804 | -0.26092 | -0.045776 | -0.07782 | 122.9782 | 122.7722 | 58.1314 | -123.0423 | 122.9553 | 122.8455 | 54.1031 | -123.1384
1692.0156 | 123.056 | -58.5114 | 64.3845 | -0.19852 | 0.013217 | 0.068678 | 0.070731 | 0.128 | -0.0011451 | -0.0051547 | -0.10696 | -0.0078442 | 0.065546 | 0.05868 | 0.0039948 | -0.0091966 | 64.2517 | 64.4165 | -0.37994 | -58.6258 | 64.4943 | -58.5388 | -58.6121 | -58.2642 | -4.2068 | -58.699 | 64.4577 | 64.3707 | -58.6716 | -58.7173 | -0.027465 | -0.10071 | 0.10986 | 122.9279 | -0.11444 | -0.013732 | -0.13275 | -0.16022 | -0.20599 | 0.073243 | 0.24719 | -0.18768 | 0.01831 | -0.013732 | 123.0057 | 122.7631 | 58.1314 | -122.9965 | 122.9691 | 122.8821 | 54.3045 | -123.1018
1693.0156 | 122.9507 | -58.5526 | 64.3616 | 0.030365 | 0.014926 | 0.068678 | 0.071799 | 0.1295 | -0.00050425 | -0.0038731 | -0.00015237 | -0.0067762 | 0.065332 | 0.060176 | 0.004422 | -0.0081284 | 64.1922 | 64.3341 | -0.35248 | -58.6807 | 64.4577 | -58.5571 | -58.6624 | -58.342 | -4.184 | -58.8043 | 64.4119 | 64.3387 | -58.7128 | -58.7631 | -0.004578 | -0.10986 | 0.096131 | 122.8867 | -0.12817 | -0.01831 | -0.16937 | -0.16022 | -0.21057 | 0.050354 | 0.21057 | -0.25177 | -0.041198 | -0.022888 | 123.0103 | 122.7448 | 58.2001 | -123.024 | 122.9645 | 122.8912 | 54.3686 | -123.1247
1694.0156 | 123.0148 | -58.4702 | 64.4119 | -0.068817 | 0.015567 | 0.066969 | 0.070731 | 0.12928 | 0.00056395 | -0.0034457 | -0.13748 | -0.006349 | 0.065119 | 0.059535 | 0.0039948 | -0.0085556 | 64.2883 | 64.4257 | -0.50812 | -58.7036 | 64.444 | -58.5388 | -58.6166 | -58.2184 | -3.8773 | -58.7036 | 64.4577 | 64.3845 | -58.6578 | -58.7036 | -0.068664 | -0.14648 | 0.032044 | 122.8958 | -0.23346 | -0.086975 | -0.1236 | -0.18768 | -0.23346 | 0.045777 | 0.25177 | -0.23346 | 0 | -0.027466 | 122.9141 | 122.7585 | 57.962 | -123.0286 | 122.9279 | 122.8546 | 54.5929 | -123.1155
1695.0156 | 123.024 | -58.4473 | 64.4623 | -0.0077822 | 0.016208 | 0.066755 | 0.073508 | 0.12822 | 0.0029137 | -0.0038731 | 0.076141 | -0.0061352 | 0.065332 | 0.060389 | 0.002713 | -0.0062058 | 64.3021 | 64.4348 | -0.51727 | -58.5983 | 64.5447 | -58.4976 | -58.5938 | -58.2275 | -3.9597 | -58.7036 | 64.4943 | 64.4348 | -58.6212 | -58.6899 | -0.050354 | -0.14648 | 0.082398 | 122.8821 | -0.15106 | -0.004578 | -0.16022 | -0.17395 | -0.24261 | 0.032044 | 0.21973 | -0.25635 | -0.013733 | -0.027466 | 122.9919 | 122.7493 | 57.93 | -123.056 | 122.9416 | 122.8821 | 54.4876 | -123.1522
1696.0156 | 123.0377 | -58.461 | 64.4073 | -0.21378 | 0.013431 | 0.066114 | 0.070731 | 0.13099 | 0.00099115 | -0.0036595 | -0.068817 | -0.007417 | 0.061487 | 0.058039 | 0.0048492 | -0.010051 | 64.2975 | 64.4211 | -0.3067 | -58.5846 | 64.4943 | -58.5205 | -58.5938 | -58.2138 | -3.9917 | -58.699 | 64.4943 | 64.4394 | -58.6487 | -58.6853 | -0.059509 | -0.13275 | 0.086975 | 122.8821 | -0.1236 | 0.009155 | -0.10986 | -0.18768 | -0.2243 | 0.086975 | 0.24719 | -0.23804 | -0.013733 | 0.032043 | 122.9553 | 122.7585 | 58.1543 | -123.0011 | 122.9553 | 122.9004 | 54.4693 | -123.0927
1697.0156 | 122.9828 | -58.5251 | 64.3936 | 0.12192 | 0.015994 | 0.06825 | 0.072226 | 0.13356 | 0.00056395 | -0.0055821 | 0.17532 | -0.0065626 | 0.064478 | 0.058253 | 0.004422 | -0.0087692 | 64.1876 | 64.2975 | -0.2243 | -58.6716 | 64.4852 | -58.5663 | -58.6349 | -58.3054 | -4.1702 | -58.7814 | 64.4485 | 64.3707 | -58.7219 | -58.7311 | -0.041199 | -0.10986 | 0.091552 | 122.8226 | -0.14649 | -0.036621 | -0.20599 | -0.19684 | -0.20599 | 0.054931 | 0.21973 | -0.25635 | -0.050354 | -0.022888 | 123.0103 | 122.7127 | 58.3008 | -123.0286 | 122.9736 | 122.8958 | 54.3549 | -123.1247
1698.0156 | 123.0469 | -58.4381 | 64.4531 | -0.24429 | 0.013858 | 0.064619 | 0.073721 | 0.13313 | 0.0016321 | -0.0045139 | 0.053253 | -0.0078442 | 0.062555 | 0.058253 | 0.0014312 | -0.0081284 | 64.3478 | 64.4577 | -0.25177 | -58.5709 | 64.5218 | -58.5022 | -58.5526 | -58.1863 | -4.097 | -58.6899 | 64.5172 | 64.4348 | -58.5892 | -58.6624 | -0.064087 | -0.11444 | 0.068665 | 122.8958 | -0.13275 | -0.018311 | -0.10529 | -0.15106 | -0.22431 | 0.064087 | 0.25177 | -0.25177 | -0.027465 | -0.018311 | 122.9599 | 122.7859 | 58.1863 | -123.0057 | 122.9553 | 122.8729 | 54.3411 | -123.1155
1699.0156 | 122.9874 | -58.3923 | 64.476 | 0.16006 | 0.013431 | 0.069319 | 0.071799 | 0.13078 | -0.0013587 | -0.0049411 | 0.2211 | -0.0076306 | 0.063196 | 0.059748 | 0.0057038 | -0.0068466 | 64.3112 | 64.4348 | -0.32044 | -58.5526 | 64.5584 | -58.4656 | -58.548 | -58.1772 | -4.2206 | -58.6624 | 64.5218 | 64.4714 | -58.5892 | -58.6441 | -0.073242 | -0.15564 | 0.082398 | 122.8271 | -0.16022 | -0.004577 | -0.16479 | -0.19684 | -0.25177 | 0.045777 | 0.21515 | -0.27008 | -0.018311 | -0.004577 | 122.9507 | 122.7036 | 58.0719 | -123.024 | 122.9141 | 122.8638 | 54.1718 | -123.1201
1700.0156 | 122.9782 | -58.3603 | 64.5218 | -0.0077822 | 0.016208 | 0.069319 | 0.072653 | 0.12822 | 0.0018457 | -0.0060093 | 0.045624 | -0.0054944 | 0.065119 | 0.057185 | 0.004422 | -0.0098374 | 64.3936 | 64.4669 | -0.37537 | -58.493 | 64.595 | -58.429 | -58.4839 | -58.136 | -4.3579 | -58.6212 | 64.5813 | 64.5355 | -58.5342 | -58.6212 | -0.068664 | -0.1236 | 0.073242 | 122.8271 | -0.13275 | -0.009155 | -0.12817 | -0.17395 | -0.26093 | 0.059509 | 0.2243 | -0.26093 | 0 | 0.013732 | 122.9553 | 122.7539 | 57.9849 | -123.0057 | 122.9416 | 122.8958 | 54.0024 | -123.143
1701.0156 | 123.0377 | -58.3557 | 64.5401 | 0.10666 | 0.01514 | 0.069532 | 0.072653 | 0.13057 | -0.00071785 | -0.0055821 | 0.19058 | -0.0067762 | 0.062769 | 0.060816 | 0.0037812 | -0.0089828 | 64.3753 | 64.4852 | -0.45319 | -58.5114 | 64.6271 | -58.4244 | -58.5022 | -58.1131 | -4.2755 | -58.6075 | 64.5996 | 64.5538 | -58.5114 | -58.5846 | -0.068664 | -0.14648 | 0.086975 | 122.8409 | -0.15564 | -0.009156 | -0.16479 | -0.15564 | -0.22888 | 0.059509 | 0.24262 | -0.25177 | -0.022888 | 0.013733 | 122.9828 | 122.731 | 57.9025 | -123.0423 | 122.9553 | 122.9095 | 54.0802 | -123.1247
1702.0156 | 123.0377 | -58.3466 | 64.5355 | 0.18295 | 0.013003 | 0.066114 | 0.073294 | 0.13142 | 0.00099115 | -0.0049411 | -0.00015237 | -0.0054944 | 0.062769 | 0.057612 | 0.0050628 | -0.0098374 | 64.4577 | 64.563 | -0.082397 | -58.4564 | 64.6271 | -58.3878 | -58.4564 | -58.0719 | -3.9917 | -58.5663 | 64.5905 | 64.5538 | -58.5022 | -58.5571 | -0.041198 | -0.10986 | 0.091553 | 122.9095 | -0.10986 | 0 | -0.077819 | -0.15564 | -0.21057 | 0.054932 | 0.27466 | -0.21973 | -0.009155 | 0.018311 | 122.9736 | 122.8043 | 58.2642 | -122.9919 | 122.937 | 122.9004 | 54.3549 | -123.0927
1703.0156 | 122.9736 | -58.342 | 64.563 | 0.18295 | 0.01279 | 0.065901 | 0.071585 | 0.13014 | 0.0014185 | -0.0030185 | 0.19821 | -0.006349 | 0.063837 | 0.058039 | 0.0048492 | -0.0085556 | 64.3707 | 64.476 | -0.045776 | -58.4885 | 64.6179 | -58.4244 | -58.5022 | -58.1589 | -4.2435 | -58.6212 | 64.5996 | 64.5493 | -58.5251 | -58.58 | -0.082397 | -0.16022 | 0.054932 | 122.818 | -0.14648 | 0.013733 | -0.19226 | -0.1831 | -0.23804 | 0.036621 | 0.1831 | -0.27924 | -0.041199 | -0.013733 | 122.9599 | 122.7127 | 58.2962 | -123.0652 | 122.9416 | 122.8912 | 54.0985 | -123.143
1704.0156 | 122.9919 | -58.374 | 64.5218 | 0.030365 | 0.016849 | 0.068464 | 0.073935 | 0.12629 | 0.00077755 | -0.0045139 | 0.12192 | -0.0061352 | 0.064051 | 0.05868 | 0.006131 | -0.0091966 | 64.3707 | 64.4485 | 0.064087 | -58.5022 | 64.5996 | -58.3969 | -58.5022 | -58.1726 | -4.1931 | -58.6624 | 64.595 | 64.5493 | -58.5297 | -58.6212 | -0.022889 | -0.12817 | 0.077819 | 122.8226 | -0.12817 | 0 | -0.15106 | -0.15564 | -0.24719 | 0.073242 | 0.20142 | -0.28839 | -0.041199 | 0.027465 | 122.9736 | 122.7448 | 58.4381 | -123.024 | 122.9691 | 122.9233 | 54.1809 | -123.143
1705.0156 | 123.1338 | -58.374 | 64.4348 | -0.091705 | 0.0059537 | 0.071882 | 0.07009 | 0.12971 | -0.0094763 | -0.0068637 | 0.09903 | -0.0076306 | 0.062342 | 0.058467 | -0.00070498 | -0.0074876 | 64.3478 | 64.5355 | 0.25635 | -58.5159 | 64.5172 | -58.4564 | -58.5388 | -58.1131 | -3.772 | -58.5297 | 64.4806 | 64.444 | -58.5846 | -58.6304 | -0.082398 | -0.16479 | 0.082398 | 122.9095 | -0.14191 | 0.022888 | -0.086975 | -0.21057 | -0.25635 | 0.045777 | 0.26093 | -0.15564 | 0.10071 | 0.009156 | 122.8912 | 122.7219 | 58.6304 | -122.9736 | 122.8546 | 122.818 | 54.602 | -123.0652
1706.0156 | 122.9691 | -58.4152 | 64.4714 | 0.030365 | 0.017489 | 0.066541 | 0.070517 | 0.13121 | 0.0014185 | -0.0047275 | 0.068512 | -0.007417 | 0.063196 | 0.057612 | 0.0052764 | -0.010051 | 64.325 | 64.4165 | 0.26093 | -58.5892 | 64.5401 | -58.461 | -58.5571 | -58.2184 | -3.9505 | -58.7219 | 64.5401 | 64.476 | -58.6166 | -58.6716 | -0.045777 | -0.14191 | 0.068664 | 122.8317 | -0.17395 | -0.032043 | -0.14648 | -0.20142 | -0.25635 | 0.068664 | 0.19684 | -0.3067 | -0.050354 | 0.004577 | 122.9553 | 122.7402 | 58.6761 | -123.0286 | 122.9553 | 122.8912 | 54.4647 | -123.143
1707.0156 | 123.0423 | -58.3832 | 64.4943 | 0.33554 | 0.013217 | 0.068891 | 0.071799 | 0.12928 | 0.0014185 | -0.0049411 | 0.19058 | -0.0093396 | 0.065332 | 0.059962 | 0.0057038 | -0.0089828 | 64.3616 | 64.4394 | 0.46234 | -58.5297 | 64.595 | -58.429 | -58.5526 | -58.1268 | -4.0558 | -58.6304 | 64.563 | 64.4714 | -58.5526 | -58.6121 | -0.045776 | -0.16937 | 0.10071 | 122.8226 | -0.14648 | 0.022888 | -0.13275 | -0.16937 | -0.22888 | 0.068664 | 0.25635 | -0.24719 | -0.01831 | -0.022888 | 122.9782 | 122.7448 | 58.8455 | -123.0469 | 122.9462 | 122.8546 | 54.3274 | -123.1064
1708.0156 | 122.9919 | -58.3649 | 64.5035 | -0.015411 | 0.01514 | 0.069105 | 0.07009 | 0.13014 | 0.00013675 | -0.0036595 | 0.0914 | -0.0067762 | 0.065332 | 0.059321 | 0.0042084 | -0.0089828 | 64.3799 | 64.4852 | 0.54016 | -58.5114 | 64.6088 | -58.4152 | -58.4839 | -58.1314 | -3.9734 | -58.6533 | 64.5721 | 64.5355 | -58.5251 | -58.6166 | -0.050354 | -0.11902 | 0.10529 | 122.85 | -0.14648 | -0.027466 | -0.1236 | -0.16022 | -0.25177 | 0.068665 | 0.23346 | -0.28839 | -0.036621 | 0.032043 | 122.9736 | 122.7448 | 58.905 | -122.9874 | 122.937 | 122.9004 | 54.3915 | -123.1201
1709.0156 | 123.0652 | -58.3328 | 64.5309 | 0.15244 | 0.014071 | 0.06761 | 0.070303 | 0.13121 | -0.0011451 | -0.0051547 | 0.23636 | -0.007417 | 0.063837 | 0.058253 | 0.0052764 | -0.0081284 | 64.389 | 64.4897 | 0.40741 | -58.5114 | 64.6179 | -58.4106 | -58.5159 | -58.0811 | -3.6255 | -58.5983 | 64.5676 | 64.5218 | -58.5159 | -58.5754 | -0.07782 | -0.1831 | 0.086975 | 122.8226 | -0.17853 | 0.004577 | -0.14191 | -0.1831 | -0.24261 | 0.036621 | 0.25177 | -0.2655 | -0.022889 | -0.009155 | 122.9507 | 122.7219 | 58.7402 | -123.0469 | 122.9004 | 122.8546 | 54.7073 | -123.1064
1710.0156 | 123.0377 | -58.3145 | 64.5172 | 0.0914 | 0.013431 | 0.069746 | 0.072226 | 0.1295 | 0.0027001 | -0.0053683 | 0.22873 | -0.0076306 | 0.064264 | 0.056544 | 0.0042084 | -0.0085556 | 64.389 | 64.476 | 0.78735 | -58.4885 | 64.5813 | -58.4015 | -58.4747 | -58.0902 | -3.6072 | -58.5983 | 64.5721 | 64.5355 | -58.5434 | -58.5846 | -0.086975 | -0.16022 | 0.064087 | 122.7905 | -0.17395 | -0.013733 | -0.12817 | -0.22888 | -0.27008 | 0.054932 | 0.2243 | -0.28381 | -0.013733 | 0.01831 | 122.8958 | 122.7036 | 59.1019 | -122.9919 | 122.8867 | 122.85 | 54.7073 | -123.1018
1711.0156 | 122.9645 | -58.3694 | 64.5493 | 0.015106 | 0.014285 | 0.069532 | 0.07543 | 0.13078 | 0.00013675 | -0.0038731 | 0.16006 | -0.0072034 | 0.064478 | 0.058467 | 0.0048492 | -0.0081284 | 64.389 | 64.4302 | 0.50354 | -58.5114 | 64.6408 | -58.3923 | -58.4747 | -58.1223 | -4.1107 | -58.6258 | 64.6042 | 64.563 | -58.5068 | -58.5846 | -0.022888 | -0.10528 | 0.091553 | 122.7997 | -0.14191 | -0.036622 | -0.16022 | -0.13733 | -0.21515 | 0.054932 | 0.24719 | -0.25635 | -0.041198 | 0.013733 | 123.0103 | 122.7585 | 58.873 | -123.024 | 122.9736 | 122.9324 | 54.2587 | -123.1338
1712.0156 | 123.0423 | -58.2687 | 64.5905 | -0.099335 | 0.014712 | 0.066541 | 0.073508 | 0.13035 | 0.00035035 | -0.0032321 | 0.36606 | -0.006349 | 0.064691 | 0.060176 | 0.004422 | -0.0087692 | 64.5264 | 64.595 | 0.3067 | -58.4152 | 64.6866 | -58.3374 | -58.4244 | -58.0078 | -3.9597 | -58.5251 | 64.6637 | 64.595 | -58.4381 | -58.5342 | -0.068664 | -0.15564 | 0.09613 | 122.8638 | -0.14648 | 0.009155 | -0.064087 | -0.16937 | -0.2655 | 0.073242 | 0.26093 | -0.25635 | 0.009156 | 0.004578 | 122.9553 | 122.7951 | 58.5754 | -123.0148 | 122.9324 | 122.8638 | 54.3091 | -123.1247
1713.0156 | 122.9828 | -58.3374 | 64.5401 | 0.10666 | 0.015994 | 0.068464 | 0.071799 | 0.12971 | -0.0011451 | -0.0034457 | 1.6554 | -0.00464 | 0.062982 | 0.057826 | 0.0065582 | -0.008342 | 64.3845 | 64.4577 | 0.52185 | -58.5068 | 64.6317 | -58.3786 | -58.4702 | -58.2001 | -3.7354 | -58.5709 | 64.6317 | 64.5721 | -58.5251 | -58.5526 | -0.041199 | -0.13275 | 0.091553 | 122.7951 | -0.16937 | -0.036621 | -0.15564 | -0.18768 | -0.21515 | 0.091553 | 0.13733 | -0.23346 | -0.018311 | 0.032044 | 122.9691 | 122.7219 | 58.8593 | -123.0103 | 122.9691 | 122.9095 | 54.602 | -123.0927
1714.0156 | 123.0331 | -58.4198 | 64.4394 | 0.30502 | 0.013003 | 0.070814 | 0.071372 | 0.12907 | 0.00099115 | -0.0057957 | 0.21347 | -0.0054944 | 0.064051 | 0.057612 | 0.0031402 | -0.0096238 | 64.3066 | 64.357 | 0.58594 | -58.6029 | 64.5309 | -58.4976 | -58.5938 | -58.2184 | -3.9734 | -58.7036 | 64.4852 | 64.4394 | -58.6258 | -58.6624 | -0.07782 | -0.17395 | 0.091553 | 122.7768 | -0.1831 | -0.009155 | -0.13275 | -0.20599 | -0.24262 | 0.045776 | 0.20142 | -0.28381 | -0.041198 | 0 | 122.9507 | 122.7264 | 59.0057 | -123.0331 | 122.905 | 122.8592 | 54.4464 | -123.1018
1715.0156 | 123.0881 | -58.3328 | 64.476 | -0.40451 | 0.0078763 | 0.071882 | 0.066245 | 0.12993 | -0.0060585 | -0.0064365 | -0.03067 | -0.007417 | 0.059564 | 0.057826 | 0.0037812 | -0.0089828 | 64.4028 | 64.595 | 0.91095 | -58.493 | 64.5355 | -58.4106 | -58.5205 | -58.0811 | -3.5477 | -58.5159 | 64.5264 | 64.476 | -58.5297 | -58.58 | -0.07782 | -0.18768 | 0.059509 | 122.9279 | -0.16022 | 0.027466 | -0.073242 | -0.19684 | -0.24719 | 0.050354 | 0.25177 | -0.1831 | 0.064087 | 0 | 122.8683 | 122.7356 | 59.2438 | -122.9965 | 122.8592 | 122.8088 | 54.7852 | -123.056
1716.0156 | 123.0377 | -58.3191 | 64.5355 | -0.16037 | 0.016208 | 0.068037 | 0.072012 | 0.13014 | 0.00035035 | -0.0072911 | -0.15274 | -0.0086988 | 0.063623 | 0.058039 | 0.0020722 | -0.0098374 | 64.444 | 64.5538 | 0.73242 | -58.4473 | 64.682 | -58.3786 | -58.4564 | -58.0765 | -3.8727 | -58.548 | 64.65 | 64.5584 | -58.5159 | -58.5342 | -0.059509 | -0.13733 | 0.14648 | 122.8729 | -0.12817 | 0.009155 | -0.091552 | -0.19684 | -0.21515 | 0.11444 | 0.24262 | -0.22888 | -0.013733 | 0.022889 | 123.0011 | 122.7631 | 59.0515 | -122.9919 | 122.9691 | 122.8775 | 54.4464 | -123.0698
1717.0156 | 123.0469 | -58.3099 | 64.5859 | -0.38925 | 0.014285 | 0.068464 | 0.071799 | 0.13121 | 0.0035547 | -0.0025913 | -0.015411 | -0.009126 | 0.064691 | 0.059321 | 0.0042084 | -0.010265 | 64.4669 | 64.5721 | 0.79193 | -58.4381 | 64.6545 | -58.3557 | -58.4335 | -58.0673 | -4.1565 | -58.5617 | 64.6179 | 64.5401 | -58.4656 | -58.5571 | -0.045776 | -0.1236 | 0.068665 | 122.8821 | -0.12817 | -0.004577 | -0.11902 | -0.15564 | -0.24719 | 0.032044 | 0.24262 | -0.25177 | -0.004578 | -0.045776 | 122.9645 | 122.7768 | 59.1019 | -123.0194 | 122.9279 | 122.85 | 54.1534 | -123.143
1718.0156 | 123.0423 | -58.2916 | 64.5813 | -0.20615 | 0.014071 | 0.068037 | 0.071585 | 0.12779 | 0.0018457 | -0.0062229 | -0.15274 | -0.0082716 | 0.063837 | 0.057826 | 0.004422 | -0.0087692 | 64.4623 | 64.5905 | 0.8194 | -58.4015 | 64.6729 | -58.342 | -58.4473 | -58.0353 | -4.0329 | -58.5297 | 64.6454 | 64.5676 | -58.4839 | -58.5342 | -0.050354 | -0.15564 | 0.091553 | 122.8821 | -0.10986 | 0.045777 | -0.11902 | -0.19226 | -0.24262 | 0.064087 | 0.25635 | -0.23804 | 0.004578 | -0.013733 | 122.9645 | 122.7539 | 59.111 | -123.0286 | 122.937 | 122.8592 | 54.2587 | -123.1155
1719.0156 | 123.0606 | -58.3557 | 64.4943 | 0.12192 | 0.011294 | 0.067823 | 0.068808 | 0.12651 | -0.0037085 | -0.0053683 | 0.32791 | -0.010835 | 0.063623 | 0.05868 | 0.0012176 | -0.006633 | 64.3982 | 64.6042 | 1.1169 | -58.4747 | 64.5493 | -58.3923 | -58.461 | -58.0765 | -3.8544 | -58.5434 | 64.5264 | 64.444 | -58.5434 | -58.58 | -0.036621 | -0.10529 | 0.054931 | 122.9599 | -0.11902 | -0.013732 | -0.096131 | -0.18768 | -0.2243 | 0.032043 | 0.27924 | -0.18768 | 0.036621 | -0.050354 | 122.905 | 122.7539 | 59.4727 | -122.9553 | 122.8821 | 122.7997 | 54.5013 | -123.0743
1720.0156 | 123.111 | -58.3328 | 64.5035 | 0.18295 | 0.0089443 | 0.066541 | 0.068167 | 0.12822 | -0.0017859 | -0.0064365 | 0.24399 | -0.0086988 | 0.062982 | 0.057398 | 0.0031402 | -0.0096238 | 64.4257 | 64.5859 | 1.0117 | -58.4564 | 64.5584 | -58.3923 | -58.4747 | -58.017 | -3.8086 | -58.493 | 64.5264 | 64.5081 | -58.5114 | -58.5754 | -0.059509 | -0.14191 | 0.054932 | 122.9187 | -0.1236 | 0.01831 | -0.07782 | -0.17853 | -0.24261 | 0.022888 | 0.31586 | -0.16022 | 0.082397 | 0.004578 | 122.8912 | 122.7585 | 59.3445 | -122.9782 | 122.8592 | 122.8409 | 54.5242 | -123.0789
1721.0156 | 123.0057 | -58.3466 | 64.5309 | -0.091705 | 0.015353 | 0.067182 | 0.07479 | 0.1295 | 0.0035547 | -0.0025913 | 0.045624 | -0.0052808 | 0.064051 | 0.058894 | 0.006131 | -0.01176 | 64.444 | 64.5309 | 0.71411 | -58.4656 | 64.6271 | -58.3923 | -58.4656 | -58.0902 | -3.923 | -58.6029 | 64.6042 | 64.5401 | -58.5114 | -58.5709 | -0.045776 | -0.11902 | 0.09613 | 122.8775 | -0.11902 | 0 | -0.086975 | -0.16479 | -0.2243 | 0.073242 | 0.25635 | -0.25635 | -0.032043 | 0.009155 | 122.9736 | 122.7905 | 59.0607 | -122.9965 | 122.9507 | 122.8867 | 54.4235 | -123.1018
1722.0156 | 122.9965 | -58.3191 | 64.5859 | -0.57999 | 0.014071 | 0.065687 | 0.072012 | 0.13334 | -0.0030677 | -0.0051547 | -0.19089 | -0.0069898 | 0.064051 | 0.059535 | 0.0042084 | -0.0096238 | 64.3936 | 64.5493 | 0.45319 | -58.461 | 64.6957 | -58.3786 | -58.4564 | -58.0948 | -4.0192 | -58.5571 | 64.6683 | 64.5996 | -58.493 | -58.5297 | -0.059509 | -0.13733 | 0.10986 | 122.8683 | -0.14191 | -0.004578 | -0.19226 | -0.17395 | -0.21057 | 0.082398 | 0.2243 | -0.23804 | -0.027466 | 0.013733 | 123.0148 | 122.7127 | 58.7723 | -123.0423 | 122.9874 | 122.9187 | 54.2999 | -123.1155
1723.0156 | 123.0103 | -58.3694 | 64.5035 | -0.18326 | 0.012576 | 0.071027 | 0.071585 | 0.12971 | 0.00035035 | -0.0043003 | -0.061188 | -0.007417 | 0.063623 | 0.057398 | 0.0031402 | -0.0096238 | 64.4073 | 64.5355 | 0.61798 | -58.4656 | 64.5859 | -58.4244 | -58.5068 | -58.1131 | -4.2892 | -58.6166 | 64.5584 | 64.5035 | -58.5617 | -58.6166 | -0.054931 | -0.13733 | 0.082397 | 122.905 | -0.09613 | 0.041199 | -0.09613 | -0.19226 | -0.24719 | 0.054932 | 0.25635 | -0.24719 | 0 | 0 | 122.9553 | 122.7768 | 58.9874 | -123.0103 | 122.9279 | 122.8729 | 54.0802 | -123.1201
1724.0156 | 122.9736 | -58.4885 | 64.444 | -0.0077822 | 0.016208 | 0.068464 | 0.072012 | 0.1295 | 0.0018457 | -0.0038731 | -0.03067 | -0.0069898 | 0.066828 | 0.060816 | 0.0057038 | -0.0091966 | 64.2792 | 64.389 | 0.54016 | -58.6166 | 64.4852 | -58.5022 | -58.5938 | -58.2642 | -4.5364 | -58.754 | 64.4897 | 64.4165 | -58.6578 | -58.7128 | -0.013733 | -0.10529 | 0.041198 | 122.8775 | -0.12817 | -0.022888 | -0.16479 | -0.16937 | -0.22431 | 0.045776 | 0.2243 | -0.2655 | -0.041198 | -0.027466 | 122.9736 | 122.7676 | 59.0286 | -123.0377 | 122.9782 | 122.905 | 53.952 | -123.1567
1725.0156 | 123.1338 | -58.4564 | 64.3295 | 0.14481 | 0.010226 | 0.06825 | 0.067313 | 0.128 | -0.0030677 | -0.0028049 | 0.29739 | -0.0069898 | 0.061701 | 0.057826 | 0.0067718 | -0.0068466 | 64.2883 | 64.4348 | 0.24261 | -58.6121 | 64.4211 | -58.5388 | -58.6395 | -58.2733 | -4.1565 | -58.5938 | 64.3753 | 64.3341 | -58.6441 | -58.6899 | -0.082397 | -0.1831 | 0.091553 | 122.8912 | -0.15564 | 0.027465 | -0.041199 | -0.18768 | -0.23346 | 0.045776 | 0.18311 | -0.13733 | 0.09613 | 0.004577 | 122.8775 | 122.7448 | 58.699 | -122.9691 | 122.8317 | 122.7905 | 54.2999 | -123.0194
1726.0156 | 122.9874 | -58.374 | 64.5447 | -0.30533 | 0.01044 | 0.069105 | 0.073508 | 0.12864 | -0.0032813 | -0.0060093 | -0.16037 | -0.007417 | 0.060419 | 0.057185 | 0.0033538 | -0.011119 | 64.3753 | 64.4989 | 0.20599 | -58.4976 | 64.6179 | -58.4152 | -58.4976 | -58.1909 | -3.7903 | -58.5846 | 64.6683 | 64.563 | -58.5297 | -58.5983 | -0.041199 | -0.1236 | 0.073242 | 122.8729 | -0.1236 | 0 | -0.16937 | -0.15564 | -0.22431 | 0.1236 | 0.1831 | -0.21057 | 0.013733 | 0.01831 | 122.9919 | 122.7493 | 58.58 | -123.0423 | 123.0423 | 122.937 | 54.5837 | -123.143
1727.0156 | 122.9874 | -58.4702 | 64.4073 | -0.16037 | 0.013644 | 0.06825 | 0.071158 | 0.12736 | 0.0022729 | -0.0030185 | -0.061188 | -0.006349 | 0.059778 | 0.057826 | 0.0031402 | -0.010478 | 64.3387 | 64.4073 | -0.14191 | -58.6029 | 64.4852 | -58.5571 | -58.6395 | -58.2138 | -4.4174 | -58.7128 | 64.4394 | 64.4119 | -58.6441 | -58.699 | -0.086975 | -0.16937 | 0.077819 | 122.8775 | -0.13275 | 0.036621 | -0.068665 | -0.17395 | -0.22888 | 0.032043 | 0.25635 | -0.24262 | -0.013733 | 0.004577 | 122.9553 | 122.8088 | 58.3282 | -123.0469 | 122.9095 | 122.8821 | 54.0527 | -123.1064
1728.0156 | 122.9828 | -58.287 | 64.6362 | -0.23666 | 0.0083035 | 0.071027 | 0.072226 | 0.1295 | -0.0017859 | -0.0077183 | -1.6634 | -0.0067762 | 0.062769 | 0.060816 | 0.0016448 | -0.0094102 | 64.4669 | 64.5813 | 0.036621 | -58.4106 | 64.7003 | -58.3328 | -58.4061 | -58.0307 | -4.4907 | -58.5297 | 64.6912 | 64.6317 | -58.461 | -58.5205 | -0.045777 | -0.11902 | 0.064087 | 122.8683 | -0.1236 | -0.004578 | -0.16937 | -0.17395 | -0.23346 | 0.054932 | 0.25635 | -0.24262 | -0.009155 | -0.004577 | 122.9874 | 122.7539 | 58.3237 | -123.0423 | 122.9782 | 122.9187 | 53.7964 | -123.1567
1729.0312 | 123.1888 | -58.3237 | 64.4943 | -0.16037 | 0.0070217 | 0.071455 | 0.067099 | 0.12822 | -0.0081947 | -0.0070773 | -0.038299 | -0.011049 | 0.060633 | 0.056758 | 0.0029266 | -0.0087692 | 64.3982 | 64.6179 | -0.16479 | -58.4793 | 64.563 | -58.3969 | -58.5022 | -58.0811 | -4.2755 | -58.5114 | 64.5035 | 64.4485 | -58.548 | -58.5983 | -0.073243 | -0.17853 | 0.068664 | 122.9416 | -0.15564 | 0.022888 | -0.096131 | -0.22431 | -0.27466 | 0.009155 | 0.24261 | -0.18768 | 0.086975 | -0.045777 | 122.8867 | 122.7219 | 58.1589 | -122.9965 | 122.8271 | 122.7722 | 54.0482 | -123.0927
1730.0156 | 122.9645 | -58.2916 | 64.563 | 0.13718 | 0.012149 | 0.066541 | 0.070303 | 0.12886 | 0.0041955 | -0.0049411 | 0.13718 | -0.0078442 | 0.064051 | 0.05868 | 0.006131 | -0.010478 | 64.4577 | 64.5218 | -0.041199 | -58.4381 | 64.7095 | -58.3282 | -58.429 | -58.1039 | -4.4266 | -58.5983 | 64.65 | 64.5721 | -58.4747 | -58.5159 | -0.036621 | -0.13733 | 0.14648 | 122.8134 | -0.14648 | -0.009155 | -0.10529 | -0.1831 | -0.2243 | 0.086975 | 0.18768 | -0.3067 | -0.082398 | 0.009156 | 123.0011 | 122.7493 | 58.2504 | -122.9919 | 122.9416 | 122.8638 | 53.8651 | -123.0789
1731.0156 | 122.9691 | -58.4152 | 64.5081 | -0.068817 | 0.013431 | 0.068891 | 0.072012 | 0.12758 | -7.6852e-05 | -0.0053683 | -0.14511 | -0.0052808 | 0.061273 | 0.057826 | 0.0039948 | -0.010478 | 64.325 | 64.4302 | 0.041199 | -58.5571 | 64.5721 | -58.4656 | -58.5342 | -58.1726 | -4.3396 | -58.6578 | 64.5676 | 64.4852 | -58.58 | -58.6578 | -0.050354 | -0.11902 | 0.064087 | 122.8455 | -0.14191 | -0.022888 | -0.18311 | -0.16479 | -0.24262 | 0.059509 | 0.24262 | -0.24262 | 0 | -0.022889 | 122.9874 | 122.7402 | 58.4564 | -123.0423 | 122.9828 | 122.9004 | 54.0756 | -123.1659
1732.0156 | 123.0606 | -58.4015 | 64.4806 | -0.19089 | 0.0063809 | 0.071027 | 0.071799 | 0.12822 | -0.0039221 | -0.0060093 | -0.11459 | -0.010194 | 0.061273 | 0.058894 | 0.0016448 | -0.0085556 | 64.3753 | 64.5584 | 0.13275 | -58.5068 | 64.5218 | -58.4473 | -58.5205 | -58.1543 | -4.1748 | -58.5892 | 64.5035 | 64.4257 | -58.58 | -58.6441 | -0.045777 | -0.11902 | 0.041199 | 122.9599 | -0.10529 | 0.013733 | -0.10529 | -0.17853 | -0.24262 | 0.022888 | 0.24719 | -0.18768 | 0.054932 | -0.054932 | 122.9233 | 122.7768 | 58.5342 | -123.0011 | 122.905 | 122.8271 | 54.2267 | -123.1247
1733.0156 | 123.0331 | -58.3466 | 64.5493 | -0.18326 | 0.011294 | 0.069319 | 0.073721 | 0.12864 | -0.0011451 | -0.0060093 | -0.18326 | -0.0048536 | 0.065973 | 0.058039 | 0.0046356 | -0.0096238 | 64.3753 | 64.5218 | 0.013733 | -58.4793 | 64.6317 | -58.4152 | -58.4885 | -58.1223 | -4.0512 | -58.58 | 64.6179 | 64.5401 | -58.5251 | -58.5846 | -0.068664 | -0.14191 | 0.082398 | 122.8683 | -0.13275 | 0.009155 | -0.17395 | -0.17853 | -0.23804 | 0.068665 | 0.22431 | -0.23346 | 0.004578 | -0.009155 | 122.9782 | 122.7219 | 58.3603 | -123.0377 | 122.9645 | 122.8867 | 54.2953 | -123.1338
1734.0312 | 123.1338 | -58.2275 | 64.6042 | -0.068817 | 0.0065945 | 0.076795 | 0.068381 | 0.12993 | -0.0071265 | -0.0053683 | 0.068512 | -0.010408 | 0.06106 | 0.055903 | 0.0037812 | -0.0085556 | 64.5584 | 64.7415 | 0.059509 | -58.342 | 64.6683 | -58.2825 | -58.3923 | -57.9117 | -4.0237 | -58.3649 | 64.65 | 64.5676 | -58.4152 | -58.4747 | -0.054932 | -0.16479 | 0.064087 | 122.9691 | -0.11444 | 0.050354 | -0.045776 | -0.18768 | -0.24719 | 0.045776 | 0.31586 | -0.13733 | 0.10986 | -0.036621 | 122.8958 | 122.786 | 58.287 | -122.9965 | 122.8775 | 122.7951 | 54.2038 | -123.0789
1735.0156 | 123.0286 | -58.1818 | 64.7049 | -0.045929 | 0.01514 | 0.068464 | 0.071585 | 0.12907 | 0.0022729 | -0.0043003 | -0.11459 | -0.0089124 | 0.065973 | 0.057612 | 0.0035674 | -0.010692 | 64.5081 | 64.6866 | 0.050354 | -58.2687 | 64.7873 | -58.2687 | -58.3191 | -57.9025 | -4.4128 | -58.4244 | 64.7552 | 64.6866 | -58.3649 | -58.4244 | -0.086975 | -0.13733 | 0.082397 | 122.8683 | -0.086975 | 0.050354 | -0.19684 | -0.18311 | -0.24261 | 0.050354 | 0.27924 | -0.24261 | 0 | -0.018311 | 122.9691 | 122.6898 | 58.2321 | -123.024 | 122.937 | 122.8683 | 53.7689 | -123.1293
1736.0156 | 123.1567 | -58.049 | 64.7461 | -0.17563 | 0.0063809 | 0.066755 | 0.069663 | 0.13057 | -0.0039221 | -0.0021641 | 0.14481 | -0.008058 | 0.060419 | 0.058039 | 0.0031402 | -0.0079148 | 64.3662 | 64.8972 | 0.28381 | -58.1909 | 64.8422 | -58.1406 | -58.2367 | -57.7881 | -4.0237 | -58.2413 | 64.7919 | 64.7278 | -58.2458 | -58.3237 | -0.091553 | -0.18768 | 0.09613 | 122.9462 | -0.14191 | 0.045776 | -0.37994 | -0.19684 | -0.27466 | 0.045776 | 0.26093 | -0.19226 | 0.082397 | -0.018311 | 122.8912 | 122.4152 | 58.3328 | -122.9828 | 122.8409 | 122.7768 | 54.0253 | -123.0698
1737.0156 | 123.0515 | -58.1131 | 64.7552 | -0.12222 | 0.011935 | 0.068037 | 0.071585 | 0.13057 | 0.0024865 | -0.0015231 | -0.053558 | -0.006349 | 0.065759 | 0.056758 | 0.006131 | -0.012187 | 64.5218 | 64.8788 | 0.1831 | -58.2504 | 64.8605 | -58.1635 | -58.2184 | -57.8339 | -4.0466 | -58.3557 | 64.8285 | 64.7507 | -58.2779 | -58.3237 | -0.050354 | -0.10529 | 0.10529 | 122.9919 | -0.13733 | -0.032043 | -0.23346 | -0.16479 | -0.21057 | 0.073242 | 0.27924 | -0.24262 | -0.032044 | -0.004578 | 122.9736 | 122.6349 | 58.2962 | -122.9736 | 122.9416 | 122.8638 | 54.0665 | -123.0789
1738.0156 | 123.0194 | -58.1039 | 64.8285 | -0.22141 | 0.010653 | 0.068678 | 0.072867 | 0.13163 | -0.0011451 | -0.0057957 | -0.099335 | -0.0082716 | 0.06106 | 0.05868 | 0.0018584 | -0.0098374 | 64.6637 | 64.801 | -0.28839 | -58.223 | 64.8972 | -58.1497 | -58.2047 | -57.8522 | -4.1931 | -58.3282 | 64.8788 | 64.801 | -58.2596 | -58.3145 | -0.045776 | -0.10071 | 0.068665 | 122.905 | -0.11902 | -0.01831 | -0.16479 | -0.15564 | -0.21057 | 0.050354 | 0.25177 | -0.2243 | -0.013733 | -0.027466 | 123.0011 | 122.7676 | 57.8156 | -123.0331 | 122.9828 | 122.905 | 53.9108 | -123.143
1739.0312 | 123.0652 | -58.0582 | 64.8239 | -0.18326 | 0.0072355 | 0.070173 | 0.071158 | 0.13014 | -0.0028541 | -0.0057957 | -0.14511 | -0.0084852 | 0.059778 | 0.057398 | 0.0014312 | -0.0079148 | 64.7141 | 64.92 | -0.09613 | -58.1543 | 64.8605 | -58.1085 | -58.1818 | -57.7744 | -4.2389 | -58.2367 | 64.8605 | 64.7461 | -58.2458 | -58.287 | -0.050354 | -0.1236 | 0.036621 | 122.9782 | -0.09613 | 0.027466 | -0.10986 | -0.18768 | -0.22888 | 0.036621 | 0.28381 | -0.17853 | 0.050354 | -0.07782 | 122.9187 | 122.7722 | 57.962 | -123.0057 | 122.9187 | 122.8043 | 53.8193 | -123.111
1740.0156 | 123.1064 | -58.0353 | 64.7873 | -0.0383 | 0.0055265 | 0.069319 | 0.070731 | 0.12864 | -0.0049903 | -0.0068637 | 0.0074766 | -0.0093396 | 0.060419 | 0.057398 | 0.00057682 | -0.0081284 | 64.7186 | 64.9246 | 0.15106 | -58.1589 | 64.8697 | -58.0856 | -58.1909 | -57.7286 | -4.4495 | -58.168 | 64.8056 | 64.7598 | -58.2184 | -58.2733 | -0.050354 | -0.15564 | 0.082398 | 122.9599 | -0.1236 | 0.032043 | -0.068664 | -0.18311 | -0.23804 | 0.018311 | 0.3067 | -0.13275 | 0.10528 | -0.027465 | 122.905 | 122.7539 | 58.1863 | -122.9782 | 122.8409 | 122.7951 | 53.5858 | -123.0606
1741.0156 | 123.0057 | -58.1863 | 64.7095 | -0.22903 | 0.0087307 | 0.068678 | 0.07009 | 0.12736 | 0.0018457 | -0.0053683 | -0.20615 | -0.009126 | 0.06106 | 0.061244 | 0.0020722 | -0.0089828 | 64.563 | 64.7461 | 0.21057 | -58.3008 | 64.7598 | -58.2321 | -58.3328 | -57.9346 | -4.8981 | -58.4335 | 64.769 | 64.65 | -58.374 | -58.4381 | -0.045777 | -0.14648 | 0.050354 | 122.9324 | -0.11444 | 0.032044 | -0.14648 | -0.18768 | -0.25177 | 0.059509 | 0.25177 | -0.24719 | 0.004577 | -0.05951 | 122.9462 | 122.7493 | 58.3969 | -123.0423 | 122.9553 | 122.8363 | 53.2883 | -123.1476
1742.0156 | 123.0515 | -58.1406 | 64.7003 | -0.168 | 0.0063809 | 0.070387 | 0.07009 | 0.13057 | -0.00050425 | -0.0055821 | -0.13748 | -0.0078442 | 0.061701 | 0.059535 | 0.002713 | -0.011119 | 64.6179 | 64.7964 | 0.2243 | -58.2642 | 64.7736 | -58.2092 | -58.2962 | -57.8842 | -4.834 | -58.3649 | 64.7278 | 64.6591 | -58.3282 | -58.3878 | -0.068665 | -0.15564 | 0.073243 | 122.937 | -0.1236 | 0.032044 | -0.082397 | -0.18768 | -0.24719 | 0.027466 | 0.25635 | -0.2243 | 0.022888 | -0.041198 | 122.9141 | 122.7585 | 58.3649 | -122.9965 | 122.8683 | 122.7997 | 53.3066 | -123.0881
1743.0156 | 123.0331 | -58.1543 | 64.7186 | -0.22141 | 0.0097989 | 0.070173 | 0.071372 | 0.12993 | -0.00071785 | -0.0053683 | -0.14511 | -0.0097668 | 0.062342 | 0.059535 | 0.0033538 | -0.011119 | 64.595 | 64.7781 | 0.37537 | -58.287 | 64.7781 | -58.2092 | -58.3282 | -57.9208 | -5.0858 | -58.3923 | 64.7827 | 64.6591 | -58.374 | -58.3969 | -0.054932 | -0.17395 | 0.059509 | 122.9324 | -0.13275 | 0.041199 | -0.1236 | -0.21973 | -0.24262 | 0.064087 | 0.23346 | -0.23804 | 0.004578 | -0.059509 | 122.9324 | 122.7493 | 58.5297 | -123.0469 | 122.937 | 122.8134 | 53.0685 | -123.1155
1744.0312 | 123.0881 | -58.2687 | 64.5538 | 0.060882 | 0.0065945 | 0.069319 | 0.070303 | 0.12715 | -0.0030677 | -0.0060093 | 0.14481 | -0.0099806 | 0.06341 | 0.058467 | 0.002713 | -0.010478 | 64.5172 | 64.5721 | 0.48065 | -58.4381 | 64.6408 | -58.342 | -58.4061 | -58.0353 | -5.0583 | -58.4702 | 64.5721 | 64.5309 | -58.4702 | -58.5205 | -0.073242 | -0.13733 | 0.086975 | 122.8409 | -0.16937 | -0.032043 | -0.036621 | -0.20142 | -0.25177 | 0.018311 | 0.23346 | -0.20142 | 0.050354 | -0.022888 | 122.9095 | 122.7859 | 58.7494 | -122.9599 | 122.8409 | 122.7997 | 53.2104 | -123.0743
1745.0156 | 123.0469 | -58.3008 | 64.5905 | -0.21378 | 0.0095853 | 0.069319 | 0.072867 | 0.12907 | -7.6852e-05 | -0.0032321 | -0.13748 | -0.0082716 | 0.065119 | 0.05868 | 0.0020722 | -0.010265 | 64.4669 | 64.6408 | 0.51727 | -58.4381 | 64.6408 | -58.3603 | -58.4152 | -58.049 | -5.0812 | -58.548 | 64.6179 | 64.5218 | -58.4839 | -58.5297 | -0.05951 | -0.11444 | 0.050354 | 122.9416 | -0.13733 | -0.022888 | -0.1236 | -0.18311 | -0.22888 | 0.027466 | 0.25177 | -0.24719 | -0.018311 | -0.068664 | 122.9416 | 122.7676 | 58.8181 | -123.0057 | 122.9187 | 122.8226 | 53.2196 | -123.1201
1746.0156 | 123.0606 | -58.3099 | 64.5493 | 0.14481 | 0.0072355 | 0.069959 | 0.06774 | 0.1295 | -0.00050425 | -0.0060093 | 0.2211 | -0.0069898 | 0.062342 | 0.058467 | 0.0029266 | -0.0096238 | 64.4623 | 64.6225 | 0.42114 | -58.4335 | 64.6042 | -58.3603 | -58.4198 | -57.9987 | -5.2414 | -58.4976 | 64.5767 | 64.5172 | -58.4793 | -58.5114 | -0.050354 | -0.10986 | 0.054932 | 122.9324 | -0.1236 | -0.013733 | -0.086975 | -0.16937 | -0.20142 | 0.027466 | 0.31128 | -0.18768 | 0.013733 | -0.032043 | 122.9141 | 122.7722 | 58.7311 | -122.9691 | 122.8867 | 122.8271 | 53.0685 | -123.0606
1747.0156 | 123.0469 | -58.1909 | 64.6179 | -0.14511 | 0.0061673 | 0.069959 | 0.068594 | 0.12886 | -0.0019995 | -0.0038731 | -0.11459 | -0.0095532 | 0.062128 | 0.058039 | 0.0033538 | -0.010905 | 64.6133 | 64.8102 | 0.67749 | -58.3054 | 64.7278 | -58.2779 | -58.3374 | -57.8888 | -5.1132 | -58.3786 | 64.7049 | 64.6179 | -58.3649 | -58.4015 | -0.086975 | -0.14648 | 0.10986 | 123.0011 | -0.11444 | 0.032043 | -0.004578 | -0.17395 | -0.21057 | 0.086975 | 0.30212 | -0.18768 | 0.022888 | 0 | 122.9187 | 122.8043 | 58.8684 | -122.9553 | 122.8958 | 122.8088 | 53.0777 | -123.0194
1748.0156 | 123.0606 | -58.3054 | 64.5035 | 0.13718 | 0.0089443 | 0.069319 | 0.067954 | 0.12907 | -7.6852e-05 | -0.0077183 | 0.13718 | -0.0076306 | 0.061914 | 0.059107 | 0.0037812 | -0.011974 | 64.4531 | 64.6042 | 0.32501 | -58.4747 | 64.5905 | -58.3511 | -58.4518 | -58.0399 | -5.2872 | -58.5159 | 64.5721 | 64.4852 | -58.4793 | -58.5342 | -0.045776 | -0.14648 | 0.086975 | 122.9095 | -0.16937 | -0.022888 | -0.050354 | -0.17395 | -0.22888 | 0.068665 | 0.2655 | -0.21057 | 0.018311 | -0.018311 | 122.8958 | 122.7585 | 58.6304 | -122.9553 | 122.8775 | 122.7905 | 53.0182 | -123.0377
1749.0312 | 123.1384 | -58.2779 | 64.4943 | -0.076447 | 0.0059537 | 0.069746 | 0.069663 | 0.12907 | 0.00013675 | -0.0066501 | 0.0074766 | -0.0082716 | 0.060419 | 0.059321 | 0.0029266 | -0.0096238 | 64.4577 | 64.6225 | 0.2655 | -58.4427 | 64.5721 | -58.3786 | -58.4885 | -57.9803 | -4.7516 | -58.4564 | 64.5721 | 64.4852 | -58.4976 | -58.5205 | -0.10071 | -0.21057 | 0.07782 | 122.9004 | -0.16479 | 0.045776 | -0.036621 | -0.21973 | -0.24262 | 0.07782 | 0.29755 | -0.17853 | 0.064087 | -0.009156 | 122.85 | 122.7356 | 58.5434 | -122.9828 | 122.85 | 122.7631 | 53.5263 | -123.0148
1750.0156 | 123.0698 | -58.342 | 64.476 | 0.15244 | 0.0057401 | 0.070173 | 0.070731 | 0.12971 | -0.0022131 | -0.0036595 | 0.12955 | -0.0084852 | 0.062555 | 0.057612 | 0.0050628 | -0.01176 | 64.4028 | 64.5538 | 0.80109 | -58.5114 | 64.5401 | -58.3786 | -58.4976 | -58.0719 | -4.8203 | -58.5754 | 64.5447 | 64.4394 | -58.5159 | -58.5983 | -0.036621 | -0.15564 | 0.064087 | 122.8958 | -0.16937 | -0.013733 | -0.073242 | -0.17395 | -0.25635 | 0.068665 | 0.27008 | -0.23346 | 0.022889 | -0.036621 | 122.8821 | 122.7448 | 59.1431 | -122.9736 | 122.8867 | 122.7814 | 53.5217 | -123.0743
1751.0156 | 123.1384 | -58.3145 | 64.5218 | -0.053558 | 0.0057401 | 0.071455 | 0.068594 | 0.1295 | -0.0013587 | -0.0049411 | 0.015106 | -0.0082716 | 0.059992 | 0.057612 | 0.0035674 | -0.0094102 | 64.4623 | 64.6408 | 1.0529 | -58.4473 | 64.595 | -58.3786 | -58.4335 | -57.962 | -4.9255 | -58.4473 | 64.5676 | 64.4852 | -58.4885 | -58.5205 | -0.064087 | -0.11902 | 0.073242 | 122.9553 | -0.13275 | -0.013733 | -0.05951 | -0.17395 | -0.20599 | 0.045776 | 0.35248 | -0.13275 | 0.073242 | -0.036622 | 122.9095 | 122.7768 | 59.3674 | -122.9553 | 122.8821 | 122.7997 | 53.389 | -123.0423
1752.0156 | 123.0972 | -58.3099 | 64.5081 | 0.13718 | 0.01044 | 0.069105 | 0.068594 | 0.13057 | 0.00099115 | -0.0038731 | 0.22873 | -0.0097668 | 0.060846 | 0.056544 | 0.004422 | -0.0094102 | 64.4531 | 64.595 | 0.81024 | -58.4885 | 64.5447 | -58.4244 | -58.4839 | -58.0261 | -5.1224 | -58.5388 | 64.5264 | 64.4302 | -58.5251 | -58.58 | -0.11444 | -0.17395 | 0.036621 | 122.905 | -0.17853 | -0.004577 | -0.054932 | -0.21515 | -0.27008 | 0.01831 | 0.28381 | -0.22888 | 0.041199 | -0.07782 | 122.8546 | 122.7631 | 59.1202 | -122.9919 | 122.8363 | 122.7402 | 53.1876 | -123.0881
1753.0156 | 122.9828 | -58.3145 | 64.5905 | -1.4879 | 0.010653 | 0.069319 | 0.068808 | 0.128 | 0.0041955 | -0.0047275 | -0.2214 | -0.0089124 | 0.064264 | 0.05633 | 0.0065582 | -0.012187 | 64.4531 | 64.563 | 0.49439 | -58.4564 | 64.6683 | -58.3557 | -58.461 | -58.0582 | -5.159 | -58.5526 | 64.6729 | 64.5859 | -58.4747 | -58.5251 | -0.041199 | -0.14648 | 0.07782 | 122.8775 | -0.14191 | 0.004578 | -0.13733 | -0.16022 | -0.21057 | 0.082398 | 0.25635 | -0.23804 | -0.027466 | -0.004578 | 122.9828 | 122.7676 | 58.8089 | -123.0515 | 122.9874 | 122.9004 | 53.1555 | -123.1155
1754.0156 | 122.9965 | -58.2825 | 64.6042 | -0.23666 | 0.010867 | 0.070173 | 0.069663 | 0.12864 | 0.0016321 | -0.0045139 | -0.061188 | -0.0065626 | 0.061487 | 0.057185 | 0.0037812 | -0.010265 | 64.444 | 64.6179 | 0.16937 | -58.4473 | 64.7049 | -58.3374 | -58.4198 | -58.0307 | -5.4153 | -58.5159 | 64.6774 | 64.563 | -58.4793 | -58.5251 | -0.054931 | -0.13733 | 0.10071 | 122.9004 | -0.16479 | -0.027466 | -0.16022 | -0.19684 | -0.24261 | 0.073242 | 0.25177 | -0.23346 | 0.009155 | -0.041199 | 122.9874 | 122.7264 | 58.4518 | -123.024 | 122.9599 | 122.8455 | 52.8671 | -123.1293
1755.0156 | 123.0881 | -58.255 | 64.5676 | 0.16006 | 0.0063809 | 0.072096 | 0.069876 | 0.128 | -0.00029045 | -0.0045139 | 0.37369 | -0.009126 | 0.058924 | 0.058894 | 0.0059174 | -0.0085556 | 64.4577 | 64.6591 | 0.27008 | -58.4656 | 64.6454 | -58.3328 | -58.374 | -57.9987 | -5.3696 | -58.4747 | 64.6179 | 64.5355 | -58.461 | -58.5022 | -0.07782 | -0.11902 | 0.07782 | 122.9141 | -0.21057 | -0.091553 | -0.10986 | -0.20599 | -0.24719 | 0.050354 | 0.25635 | -0.21973 | 0.027466 | -0.032044 | 122.9004 | 122.7127 | 58.5251 | -122.9416 | 122.8729 | 122.7905 | 52.8854 | -123.0698
1756.0156 | 123.1384 | -58.3145 | 64.4714 | 0.28976 | 0.012362 | 0.06761 | 0.069663 | 0.12886 | 0.00035035 | -0.0025913 | 0.19058 | -0.0065626 | 0.060633 | 0.058894 | 0.0052764 | -0.010265 | 64.4943 | 64.6408 | 0.31586 | -58.4244 | 64.595 | -58.3511 | -58.4335 | -57.9758 | -5.3284 | -58.4976 | 64.5676 | 64.4623 | -58.4885 | -58.548 | -0.036621 | -0.11902 | 0.1236 | 122.9553 | -0.10986 | 0.009156 | 0.022888 | -0.17395 | -0.23346 | 0.09613 | 0.33875 | -0.18311 | 0.050354 | -0.009156 | 122.9095 | 122.8088 | 58.6304 | -122.905 | 122.8821 | 122.7768 | 52.9861 | -123.0194
1757.0156 | 123.1155 | -58.287 | 64.5538 | -0.03067 | 0.0057401 | 0.072736 | 0.070731 | 0.12971 | -0.0032813 | -0.0057957 | 0.030365 | -0.009126 | 0.062555 | 0.057826 | 0.001004 | -0.0087692 | 64.4806 | 64.6683 | 0.40741 | -58.4152 | 64.6408 | -58.342 | -58.4427 | -57.962 | -5.2505 | -58.4381 | 64.5813 | 64.5264 | -58.4564 | -58.5205 | -0.054932 | -0.15564 | 0.086975 | 122.9553 | -0.12817 | 0.027466 | -0.073242 | -0.16937 | -0.23346 | 0.027466 | 0.32501 | -0.15106 | 0.082398 | -0.027466 | 122.9279 | 122.7676 | 58.6945 | -122.9965 | 122.8683 | 122.8134 | 53.0365 | -123.0743
1758.0156 | 123.1293 | -58.2916 | 64.5126 | 0.20584 | 0.010653 | 0.069746 | 0.071158 | 0.12907 | 0.0018457 | -0.0032321 | 0.20584 | -0.0078442 | 0.059351 | 0.058253 | 0.00784 | -0.010905 | 64.4943 | 64.6317 | 0.61798 | -58.4335 | 64.5905 | -58.3694 | -58.4473 | -58.0719 | -5.1041 | -58.4152 | 64.5767 | 64.4714 | -58.4839 | -58.5297 | -0.07782 | -0.15564 | 0.07782 | 122.9233 | -0.14191 | 0.013733 | -0.01831 | -0.19226 | -0.23804 | 0.064087 | 0.21973 | -0.1236 | 0.11444 | -0.041198 | 122.8821 | 122.786 | 58.9096 | -122.9599 | 122.8683 | 122.7631 | 53.1876 | -123.0423
1759.0156 | 123.0515 | -58.2733 | 64.563 | 0.16769 | 0.0057401 | 0.069746 | 0.069235 | 0.12864 | -0.0041357 | -0.0043003 | 0.12192 | -0.0078442 | 0.061701 | 0.056971 | 0.0016448 | -0.008342 | 64.4714 | 64.6317 | 0.70953 | -58.429 | 64.6362 | -58.3191 | -58.429 | -57.9987 | -5.3192 | -58.4747 | 64.6362 | 64.5538 | -58.4427 | -58.4793 | -0.045777 | -0.15564 | 0.073242 | 122.905 | -0.15564 | 0 | -0.091552 | -0.16937 | -0.20599 | 0.073242 | 0.27466 | -0.20142 | 0.004578 | -0.009155 | 122.9095 | 122.7448 | 58.9828 | -122.9919 | 122.9095 | 122.8271 | 52.9541 | -123.0423
1760.0156 | 123.0286 | -58.3054 | 64.5447 | 0.12955 | 0.014071 | 0.069746 | 0.071799 | 0.12993 | 0.0031273 | -0.0055821 | 0.15244 | -0.007417 | 0.062342 | 0.058894 | 0.004422 | -0.010265 | 64.4669 | 64.5218 | 0.52185 | -58.4976 | 64.6774 | -58.3603 | -58.4839 | -58.0307 | -5.4291 | -58.5434 | 64.65 | 64.5264 | -58.4793 | -58.5571 | -0.054932 | -0.17853 | 0.13275 | 122.8271 | -0.19226 | -0.013733 | -0.07782 | -0.17395 | -0.25177 | 0.10528 | 0.27466 | -0.23804 | 0.013733 | -0.018311 | 122.9828 | 122.7722 | 58.8272 | -123.0286 | 122.9553 | 122.8317 | 52.8763 | -123.1018
1761.0156 | 123.1522 | -58.2596 | 64.5538 | 0.022736 | 0.0070217 | 0.071455 | 0.069663 | 0.12822 | -0.0077673 | -0.0036595 | 0.0914 | -0.0084852 | 0.058496 | 0.058467 | 0.0035674 | -0.0072738 | 64.4897 | 64.6454 | 0.52643 | -58.4152 | 64.65 | -58.3191 | -58.4198 | -57.9666 | -5.3604 | -58.429 | 64.6133 | 64.5355 | -58.461 | -58.4885 | -0.059509 | -0.16022 | 0.09613 | 122.905 | -0.15564 | 0.004578 | -0.064087 | -0.20142 | -0.22888 | 0.059509 | 0.29297 | -0.16937 | 0.059509 | -0.018311 | 122.9095 | 122.7493 | 58.786 | -122.9736 | 122.8729 | 122.7951 | 52.8992 | -123.0423
1762.0156 | 123.0972 | -58.2413 | 64.563 | 0.18295 | 0.013003 | 0.06825 | 0.070303 | 0.12928 | 0.00056395 | -0.0028049 | -0.015411 | -0.0072034 | 0.06341 | 0.057826 | 0.0057038 | -0.011333 | 64.5309 | 64.65 | 0.51727 | -58.3969 | 64.6774 | -58.3054 | -58.3923 | -57.9529 | -5.3558 | -58.4427 | 64.6362 | 64.5493 | -58.4518 | -58.493 | -0.064087 | -0.15106 | 0.11444 | 122.8912 | -0.15564 | -0.004578 | -0.032043 | -0.21057 | -0.25177 | 0.073242 | 0.28839 | -0.20142 | 0.050354 | -0.013733 | 122.9187 | 122.7722 | 58.7585 | -122.9553 | 122.8775 | 122.7905 | 52.8854 | -123.056
1763.0156 | 123.1018 | -58.2687 | 64.5401 | 0.10666 | 0.01044 | 0.068037 | 0.069235 | 0.12864 | -0.00050425 | -0.0040867 | 0.23636 | -0.0082716 | 0.060846 | 0.058467 | 0.0035674 | -0.011119 | 64.5309 | 64.682 | 0.77362 | -58.4061 | 64.6408 | -58.3237 | -58.4061 | -57.9437 | -5.3329 | -58.429 | 64.6042 | 64.5218 | -58.4244 | -58.4976 | -0.054931 | -0.13733 | 0.10071 | 122.9507 | -0.13733 | 0 | -0.009155 | -0.15564 | -0.22888 | 0.064087 | 0.32501 | -0.16022 | 0.068665 | -0.01831 | 122.9095 | 122.7997 | 59.0424 | -122.9462 | 122.8729 | 122.7905 | 52.9358 | -123.0377
1764.0156 | 123.1613 | -58.2184 | 64.6317 | -0.068817 | 0.0040311 | 0.072736 | 0.069022 | 0.12886 | -0.0052039 | -0.0053683 | -0.015411 | -0.0086988 | 0.059992 | 0.057612 | 0.0050628 | -0.0062058 | 64.5996 | 64.7324 | 0.56763 | -58.3328 | 64.7186 | -58.2596 | -58.3282 | -57.8613 | -5.4291 | -58.3374 | 64.6729 | 64.6179 | -58.374 | -58.4473 | -0.041199 | -0.10986 | 0.086975 | 122.9507 | -0.11444 | -0.004578 | -0.032044 | -0.15564 | -0.22888 | 0.041199 | 0.35706 | -0.11902 | 0.10986 | -0.013733 | 122.937 | 122.818 | 58.786 | -122.9599 | 122.8912 | 122.8363 | 52.7893 | -123.0789
1765.0156 | 123.111 | -58.2138 | 64.6179 | 0.11429 | 0.0087307 | 0.069319 | 0.069235 | 0.13078 | -0.00050425 | -0.0049411 | 0.2211 | -0.0097668 | 0.061273 | 0.059107 | 0.00549 | -0.0098374 | 64.6179 | 64.7507 | 0.31586 | -58.3328 | 64.6912 | -58.255 | -58.3466 | -57.8842 | -5.2368 | -58.3878 | 64.6866 | 64.5813 | -58.374 | -58.4198 | -0.041199 | -0.13275 | 0.073242 | 122.9645 | -0.11902 | 0.013733 | 0 | -0.16022 | -0.20599 | 0.068664 | 0.32959 | -0.17395 | 0.032044 | -0.036621 | 122.905 | 122.8317 | 58.5297 | -122.9645 | 122.9004 | 122.7951 | 52.977 | -123.0377
1766.0156 | 123.0698 | -58.223 | 64.6545 | 0.19821 | 0.014071 | 0.06761 | 0.069235 | 0.1295 | 0.0014185 | -0.0013095 | 0.16769 | -0.0065626 | 0.064264 | 0.059748 | 0.0050628 | -0.010051 | 64.5813 | 64.6362 | 0.09613 | -58.3878 | 64.7552 | -58.2779 | -58.3511 | -57.9208 | -5.2277 | -58.4427 | 64.7141 | 64.6408 | -58.3969 | -58.4335 | -0.054932 | -0.12817 | 0.10071 | 122.8592 | -0.1648 | -0.036621 | -0.073242 | -0.17395 | -0.21057 | 0.059509 | 0.30212 | -0.21973 | -0.009155 | -0.013733 | 122.9782 | 122.8043 | 58.3191 | -123.0057 | 122.937 | 122.8638 | 52.9953 | -123.0881
1767.0156 | 123.1018 | -58.136 | 64.6912 | 0.10666 | 0.0080899 | 0.074232 | 0.066885 | 0.12779 | -0.0043495 | -0.0049411 | 0.11429 | -0.007417 | 0.058924 | 0.055476 | 0.0029266 | -0.0085556 | 64.6317 | 64.7186 | -0.12817 | -58.2916 | 64.7873 | -58.1955 | -58.2779 | -57.8659 | -5.397 | -58.3237 | 64.7598 | 64.6683 | -58.3145 | -58.3511 | -0.05951 | -0.14191 | 0.09613 | 122.8546 | -0.15564 | -0.013733 | -0.059509 | -0.17853 | -0.21515 | 0.068665 | 0.27008 | -0.18768 | 0.027466 | -0.022888 | 122.9233 | 122.7676 | 58.0078 | -122.9691 | 122.8958 | 122.8043 | 52.739 | -123.0423
1768.0156 | 122.9874 | -58.1543 | 64.7095 | 0.045624 | 0.016208 | 0.068891 | 0.073081 | 0.12886 | 0.0035547 | -0.0045139 | 0.037995 | -0.007417 | 0.065119 | 0.058894 | 0.0052764 | -0.01176 | 64.5859 | 64.6683 | 0.027466 | -58.3603 | 64.8193 | -58.2458 | -58.3099 | -57.9437 | -5.9418 | -58.4656 | 64.8102 | 64.6866 | -58.342 | -58.4061 | -0.091553 | -0.15564 | 0.10986 | 122.8226 | -0.20599 | -0.050354 | -0.1236 | -0.18768 | -0.25177 | 0.10071 | 0.21057 | -0.31128 | -0.059509 | -0.022889 | 122.9736 | 122.7402 | 58.1818 | -123.0194 | 122.9645 | 122.8409 | 52.2125 | -123.1155
1769.0312 | 123.1018 | -58.1268 | 64.6774 | -0.14511 | 0.0068081 | 0.069532 | 0.068594 | 0.12993 | -0.0037085 | -0.0060093 | -0.099335 | -0.010194 | 0.060846 | 0.057612 | 0.0042084 | -0.010692 | 64.6362 | 64.801 | 0.38452 | -58.3008 | 64.7324 | -58.2138 | -58.2916 | -57.8567 | -5.4153 | -58.3282 | 64.7736 | 64.6545 | -58.3328 | -58.3786 | -0.086975 | -0.16479 | 0.054932 | 122.9279 | -0.17395 | -0.009155 | -0.041199 | -0.20599 | -0.25177 | 0.096131 | 0.27008 | -0.20142 | 0.050354 | -0.022888 | 122.8592 | 122.7631 | 58.5114 | -122.9691 | 122.9004 | 122.7814 | 52.7115 | -123.056
1770.0156 | 122.8638 | -58.2733 | 64.6042 | 0.13718 | 0.015994 | 0.066328 | 0.073508 | 0.12886 | 0.0035547 | -0.0034457 | 0.0914 | -0.0059216 | 0.064478 | 0.059107 | 0.0074126 | -0.0087692 | 64.5264 | 64.5493 | -0.19684 | -58.429 | 64.7415 | -58.3145 | -58.4015 | -58.017 | -5.6625 | -58.5342 | 64.7232 | 64.6133 | -58.4473 | -58.4976 | -0.041199 | -0.12817 | 0.13733 | 122.8226 | -0.15564 | -0.027466 | -0.07782 | -0.17395 | -0.22431 | 0.11902 | 0.25635 | -0.26093 | -0.036621 | 0.009155 | 123.0148 | 122.7997 | 58.0765 | -123.0057 | 122.9965 | 122.8867 | 52.6108 | -123.1018
1771.5 | 123.0057 | -58.1497 | 64.7095 | 0.44235 | 0.016635 | 0.068464 | 0.07244 | 0.13185 | 0.0018457 | -0.0019505 | -0.03067 | -0.00464 | 0.0664 | 0.059321 | 0.004422 | -0.011974 | 64.6454 | 64.7324 | -0.36621 | -58.3145 | 64.7827 | -58.1955 | -58.3099 | -57.8842 | -5.4245 | -58.429 | 64.7736 | 64.6957 | -58.3328 | -58.4244 | -0.045777 | -0.16022 | 0.073242 | 122.8821 | -0.1648 | -0.004577 | -0.064087 | -0.18311 | -0.27466 | 0.064087 | 0.2655 | -0.27924 | -0.004578 | -0.013733 | 122.9324 | 122.7951 | 57.7835 | -123.0194 | 122.9233 | 122.8455 | 52.7252 | -123.1338
1772.0938 | 123.1064 | -58.2047 | 64.65 | 0.15244 | 0.0059537 | 0.068037 | 0.069235 | 0.12907 | -0.0052039 | -0.0055821 | 0.0914 | -0.0084852 | 0.064264 | 0.057612 | 0.0046356 | -0.0072738 | 64.5172 | 64.7186 | -0.40741 | -58.3466 | 64.7186 | -58.2458 | -58.3282 | -57.9163 | -5.6305 | -58.374 | 64.6957 | 64.595 | -58.3786 | -58.4152 | -0.041199 | -0.1236 | 0.068665 | 122.9233 | -0.14191 | -0.018311 | -0.13275 | -0.17395 | -0.21057 | 0.045777 | 0.28839 | -0.16937 | 0.041199 | -0.054931 | 122.9233 | 122.7219 | 57.7972 | -122.9782 | 122.9004 | 122.7997 | 52.5742 | -123.0652
1773.0156 | 123.0835 | -58.2047 | 64.6088 | 0.21347 | 0.012362 | 0.068037 | 0.070517 | 0.12886 | -0.00050425 | -0.0032321 | 0.18295 | -0.0059216 | 0.062342 | 0.058039 | 0.0050628 | -0.010478 | 64.5355 | 64.6545 | -0.25635 | -58.3878 | 64.7415 | -58.2596 | -58.3511 | -57.93 | -5.3925 | -58.4244 | 64.7232 | 64.6179 | -58.4061 | -58.4381 | -0.054932 | -0.14648 | 0.13275 | 122.8592 | -0.18311 | -0.036621 | -0.073243 | -0.20142 | -0.23346 | 0.11444 | 0.27466 | -0.21973 | 0.013733 | 0.009155 | 122.9462 | 122.7402 | 57.9483 | -122.9599 | 122.9279 | 122.8226 | 52.8122 | -123.0469
1774.0156 | 122.9691 | -58.2962 | 64.6133 | -0.045929 | 0.014285 | 0.067396 | 0.072012 | 0.12993 | 0.0016321 | -0.0049411 | 0.083771 | -0.0086988 | 0.063623 | 0.058467 | 0.00549 | -0.0081284 | 64.4806 | 64.5813 | -0.10529 | -58.4244 | 64.7095 | -58.3282 | -58.4381 | -58.0261 | -5.5481 | -58.548 | 64.6729 | 64.6133 | -58.461 | -58.5068 | -0.032043 | -0.14191 | 0.096131 | 122.8775 | -0.12817 | 0.013733 | -0.13275 | -0.16479 | -0.21057 | 0.05951 | 0.27008 | -0.25177 | -0.041199 | 0 | 123.0057 | 122.7768 | 58.1909 | -123.0515 | 122.9691 | 122.9095 | 52.7481 | -123.1201
1775.0156 | 123.1522 | -58.2092 | 64.6088 | 0.19058 | 0.011081 | 0.06825 | 0.064963 | 0.13206 | -0.0011451 | -0.0023777 | 0.27451 | -0.0082716 | 0.062342 | 0.05868 | 0.007199 | -0.0096238 | 64.5493 | 64.7141 | 0.53558 | -58.3557 | 64.6454 | -58.2825 | -58.3557 | -57.8659 | -5.3101 | -58.4244 | 64.6683 | 64.5584 | -58.3786 | -58.4335 | -0.073242 | -0.14648 | 0.036621 | 122.9233 | -0.14648 | 0 | -0.05951 | -0.16937 | -0.2243 | 0.059509 | 0.34332 | -0.21515 | 0.009156 | -0.050354 | 122.8546 | 122.7585 | 58.7448 | -122.9645 | 122.8775 | 122.7676 | 52.8992 | -123.0423
1776.0312 | 123.1247 | -58.1818 | 64.6133 | 0.19821 | 0.011935 | 0.068678 | 0.069022 | 0.12907 | -0.0011451 | -0.0053683 | 0.24399 | -0.0078442 | 0.060633 | 0.058467 | 0.0035674 | -0.006633 | 64.5813 | 64.7186 | 0.59052 | -58.3328 | 64.6957 | -58.2733 | -58.3603 | -58.0307 | -5.6076 | -58.2687 | 64.6545 | 64.5813 | -58.3923 | -58.4564 | -0.091552 | -0.17853 | 0.082398 | 122.9004 | -0.15106 | 0.027466 | -0.032043 | -0.21057 | -0.27466 | 0.041199 | 0.15106 | -0.086975 | 0.18768 | -0.032043 | 122.8775 | 122.7631 | 58.7723 | -122.9736 | 122.8363 | 122.7631 | 52.5742 | -123.0698
1777.0156 | 123.0423 | -58.2092 | 64.65 | 0.19821 | 0.01514 | 0.068037 | 0.072653 | 0.12736 | 0.00077755 | -0.0053683 | 0.24399 | -0.0067762 | 0.064691 | 0.059748 | 0.0020722 | -0.010265 | 64.563 | 64.6042 | 0.27466 | -58.3878 | 64.769 | -58.255 | -58.3603 | -57.9254 | -5.5527 | -58.4564 | 64.7324 | 64.6729 | -58.4106 | -58.4473 | -0.045776 | -0.15106 | 0.11902 | 122.8134 | -0.17853 | -0.027465 | -0.086975 | -0.20142 | -0.23804 | 0.082398 | 0.28381 | -0.24719 | -0.009155 | 0.022889 | 122.9782 | 122.7722 | 58.4839 | -123.0103 | 122.9416 | 122.8821 | 52.6566 | -123.0972
1778.0156 | 123.0423 | -58.2321 | 64.6774 | -0.15274 | 0.014499 | 0.068678 | 0.071158 | 0.13014 | 0.0020593 | -0.0040867 | -0.091705 | -0.0069898 | 0.064051 | 0.058253 | 0.0048492 | -0.010051 | 64.595 | 64.6591 | 0.55389 | -58.3511 | 64.7461 | -58.2642 | -58.3282 | -57.9254 | -5.4886 | -58.4427 | 64.7186 | 64.6454 | -58.4152 | -58.4656 | -0.032043 | -0.09613 | 0.068665 | 122.8912 | -0.11902 | -0.022888 | -0.082397 | -0.1831 | -0.23346 | 0.041199 | 0.3067 | -0.21057 | 0.022888 | -0.032043 | 122.9782 | 122.8271 | 58.786 | -123.0057 | 122.9507 | 122.8775 | 52.7435 | -123.143
1779.0156 | 123.0698 | -58.2779 | 64.6042 | -0.061188 | 0.015353 | 0.068037 | 0.071372 | 0.13035 | 0.0018457 | -0.0032321 | -0.015411 | -0.006349 | 0.065973 | 0.059748 | 0.0033538 | -0.0091966 | 64.4943 | 64.6133 | 0.20599 | -58.4381 | 64.6866 | -58.3557 | -58.4198 | -57.9346 | -5.3696 | -58.4976 | 64.6591 | 64.5767 | -58.4518 | -58.5159 | -0.07782 | -0.14191 | 0.082397 | 122.8912 | -0.16022 | -0.01831 | -0.10986 | -0.17395 | -0.23804 | 0.054932 | 0.34332 | -0.21973 | 0.01831 | -0.027466 | 122.9645 | 122.7722 | 58.4839 | -123.024 | 122.937 | 122.8546 | 52.9083 | -123.1201
1780.0156 | 123.0469 | -58.255 | 64.6545 | -0.23666 | 0.013858 | 0.069319 | 0.070731 | 0.12971 | 0.00035035 | -0.0025913 | -0.14511 | -0.006349 | 0.062769 | 0.05868 | 0.0050628 | -0.0091966 | 64.5126 | 64.6088 | 0.43488 | -58.4061 | 64.7415 | -58.2642 | -58.3557 | -57.9666 | -5.5893 | -58.4702 | 64.7369 | 64.6362 | -58.4244 | -58.4976 | -0.009155 | -0.10071 | 0.086975 | 122.8638 | -0.15106 | -0.050354 | -0.14191 | -0.16937 | -0.24262 | 0.082397 | 0.28839 | -0.21515 | 0.027466 | -0.018311 | 122.9965 | 122.7676 | 58.6899 | -123.0103 | 122.9919 | 122.8912 | 52.6657 | -123.1522
1781.0156 | 123.024 | -58.2367 | 64.6317 | 0.099029 | 0.014926 | 0.066328 | 0.072012 | 0.12928 | 0.0018457 | -0.0047275 | 0.14481 | -0.0054944 | 0.064051 | 0.059748 | 0.0046356 | -0.0077012 | 64.3433 | 64.7049 | -0.13733 | -58.4106 | 64.7369 | -58.2733 | -58.3832 | -57.9849 | -5.8273 | -58.4976 | 64.7278 | 64.6317 | -58.4244 | -58.4702 | -0.036621 | -0.14648 | 0.10528 | 122.9416 | -0.17395 | -0.027466 | -0.28839 | -0.18768 | -0.23346 | 0.09613 | 0.25177 | -0.26093 | -0.027466 | 0 | 122.9736 | 122.58 | 58.0994 | -123.0148 | 122.9645 | 122.8683 | 52.4094 | -123.1018
1782.0156 | 123.056 | -58.1909 | 64.7003 | -0.15274 | 0.013217 | 0.068891 | 0.073508 | 0.13121 | -7.6852e-05 | -0.0040867 | -0.17563 | -0.0082716 | 0.062769 | 0.05868 | 0.0022858 | -0.0098374 | 64.563 | 64.7049 | -0.29755 | -58.3145 | 64.7736 | -58.2367 | -58.3237 | -57.9117 | -5.7632 | -58.3786 | 64.7919 | 64.6729 | -58.3694 | -58.4427 | -0.045776 | -0.13275 | 0.073243 | 122.8958 | -0.1236 | 0.009155 | -0.13733 | -0.17853 | -0.25177 | 0.091553 | 0.27924 | -0.18768 | 0.064087 | -0.027465 | 122.9645 | 122.7539 | 57.8934 | -123.024 | 122.9828 | 122.8638 | 52.4277 | -123.143
1783.0156 | 123.0286 | -58.2001 | 64.6912 | -0.64102 | 0.014926 | 0.066328 | 0.070944 | 0.12886 | -0.00029045 | -0.0049411 | 0.17532 | -0.007417 | 0.063623 | 0.060603 | 0.0035674 | -0.0087692 | 64.5264 | 64.6637 | -0.45776 | -58.3466 | 64.7964 | -58.2321 | -58.3282 | -57.93 | -5.6671 | -58.4427 | 64.7598 | 64.6729 | -58.3786 | -58.4198 | -0.032044 | -0.12817 | 0.10529 | 122.8638 | -0.14648 | -0.018311 | -0.1648 | -0.17853 | -0.21973 | 0.068665 | 0.27008 | -0.24261 | -0.022888 | -0.01831 | 122.9965 | 122.7264 | 57.7423 | -123.0194 | 122.9599 | 122.8729 | 52.533 | -123.111
1784.0156 | 123.0652 | -58.1543 | 64.7507 | -0.21378 | 0.014285 | 0.066114 | 0.073935 | 0.13121 | 0.00013675 | -0.0043003 | -0.11459 | -0.0086988 | 0.062982 | 0.057612 | 0.0039948 | -0.011333 | 64.5996 | 64.7278 | -0.2243 | -58.2687 | 64.8239 | -58.2047 | -58.2962 | -57.8705 | -5.6122 | -58.3557 | 64.7873 | 64.7324 | -58.3328 | -58.4061 | -0.050354 | -0.14191 | 0.073243 | 122.8821 | -0.11444 | 0.027466 | -0.15106 | -0.17853 | -0.25177 | 0.036621 | 0.28381 | -0.20142 | 0.050354 | -0.01831 | 122.9782 | 122.7539 | 57.93 | -123.0469 | 122.9416 | 122.8867 | 52.5421 | -123.1567
1785.0156 | 123.0377 | -58.0902 | 64.7781 | -0.15274 | 0.01514 | 0.068037 | 0.070517 | 0.12864 | 0.0022729 | -0.0028049 | -0.015411 | -0.009126 | 0.063196 | 0.05868 | 0.0052764 | -0.0094102 | 64.6912 | 64.801 | -0.31586 | -58.2458 | 64.8468 | -58.1497 | -58.2184 | -57.8384 | -5.5573 | -58.3466 | 64.8285 | 64.7507 | -58.2916 | -58.342 | -0.059509 | -0.12817 | 0.068665 | 122.8912 | -0.15564 | -0.027466 | -0.086975 | -0.20142 | -0.25177 | 0.050354 | 0.25177 | -0.25635 | -0.004578 | -0.027466 | 122.937 | 122.7814 | 57.7744 | -122.9965 | 122.9187 | 122.8409 | 52.533 | -123.1201
1786.0156 | 123.024 | -58.0811 | 64.7873 | -0.061188 | 0.014712 | 0.068678 | 0.073508 | 0.12779 | 0.0016321 | -0.0040867 | 0.10666 | -0.0084852 | 0.064691 | 0.058467 | 0.0059174 | -0.010692 | 64.6729 | 64.8056 | -0.41199 | -58.2367 | 64.8788 | -58.1177 | -58.2138 | -57.8339 | -5.5847 | -58.3374 | 64.8697 | 64.8193 | -58.2733 | -58.3054 | -0.036621 | -0.13275 | 0.091553 | 122.8867 | -0.15564 | -0.022888 | -0.11444 | -0.19226 | -0.2243 | 0.082398 | 0.24719 | -0.25635 | -0.032043 | 0.032044 | 122.9599 | 122.7539 | 57.6691 | -123.0011 | 122.9507 | 122.9004 | 52.4963 | -123.0927
1787.0156 | 123.0469 | -58.0261 | 64.8514 | -0.24429 | 0.013644 | 0.066755 | 0.072867 | 0.13163 | -0.00050425 | -0.0036595 | -0.15274 | -0.009126 | 0.062769 | 0.059107 | 0.0029266 | -0.010478 | 64.6957 | 64.8376 | -0.47607 | -58.1909 | 64.9384 | -58.0994 | -58.1726 | -57.7972 | -5.7037 | -58.2596 | 64.9155 | 64.8514 | -58.2275 | -58.2733 | -0.073242 | -0.14648 | 0.086975 | 122.8638 | -0.1648 | -0.018311 | -0.15564 | -0.20142 | -0.24719 | 0.064087 | 0.22888 | -0.23346 | 0.013732 | 0 | 122.9645 | 122.7219 | 57.55 | -123.024 | 122.9416 | 122.8775 | 52.3224 | -123.1247
1788.0156 | 123.0286 | -58.0856 | 64.8422 | -0.22903 | 0.0074491 | 0.069959 | 0.067099 | 0.12928 | -0.0062721 | -0.0070773 | -0.076446 | -0.0078442 | 0.061914 | 0.060816 | 0.0029266 | -0.0064194 | 64.6454 | 64.8468 | -0.17395 | -58.2047 | 64.856 | -58.1314 | -58.223 | -57.8384 | -6.0287 | -58.3145 | 64.8926 | 64.7827 | -58.2779 | -58.3008 | -0.045777 | -0.13733 | 0.013733 | 122.9324 | -0.11902 | 0.01831 | -0.19684 | -0.19226 | -0.21515 | 0.050354 | 0.24719 | -0.22888 | -0.013733 | -0.059509 | 122.9416 | 122.731 | 57.9117 | -123.0652 | 122.9782 | 122.8683 | 52.0569 | -123.143
1789.0156 | 123.0515 | -58.1406 | 64.7461 | -0.053558 | 0.015353 | 0.069959 | 0.074362 | 0.13228 | 0.0031273 | -0.0049411 | -0.068817 | -0.0059216 | 0.064264 | 0.062312 | 0.0057038 | -0.010905 | 64.6225 | 64.7736 | -0.09613 | -58.2733 | 64.8605 | -58.1863 | -58.2779 | -57.9437 | -5.9784 | -58.3786 | 64.8148 | 64.7232 | -58.3054 | -58.374 | -0.045776 | -0.13733 | 0.11444 | 122.9141 | -0.13275 | 0.004578 | -0.1236 | -0.1648 | -0.23346 | 0.068664 | 0.19684 | -0.23804 | -0.004578 | -0.022888 | 123.0011 | 122.7631 | 58.0444 | -123.024 | 122.9553 | 122.8638 | 52.1622 | -123.1201
1790.0156 | 123.0057 | -58.0902 | 64.801 | -0.24429 | 0.010226 | 0.06825 | 0.07009 | 0.12928 | -0.0032813 | -0.0057957 | -0.10696 | -0.0065626 | 0.063196 | 0.059107 | 0.0033538 | -0.0085556 | 64.7552 | 64.5538 | 0.045776 | -58.2687 | 64.888 | -58.1589 | -58.2687 | -57.8659 | -5.8685 | -58.342 | 64.8743 | 64.801 | -58.287 | -58.3374 | -0.068665 | -0.17853 | 0.086975 | 122.644 | -0.17853 | 0 | -0.045776 | -0.19684 | -0.24719 | 0.073243 | 0.2243 | -0.25177 | -0.004578 | 0 | 122.9782 | 122.8455 | 58.136 | -123.0698 | 122.9645 | 122.8912 | 52.2217 | -123.1384
1791.0312 | 123.0011 | -58.1085 | 64.8285 | -0.18326 | 0.011294 | 0.069959 | 0.073935 | 0.13035 | -0.0022131 | -0.0060093 | 0.2211 | -0.0084852 | 0.062555 | 0.057612 | 0.004422 | -0.0089828 | 64.6042 | 64.8651 | 0.21057 | -58.2092 | 64.9292 | -58.1085 | -58.2367 | -57.8705 | -5.9601 | -58.3191 | 64.8834 | 64.7919 | -58.2916 | -58.3054 | 0 | -0.12817 | 0.10071 | 122.9736 | -0.10071 | 0.027465 | -0.2243 | -0.1831 | -0.19684 | 0.054932 | 0.23804 | -0.21057 | -0.013733 | -0.036621 | 123.0377 | 122.7127 | 58.3191 | -123.0652 | 122.9919 | 122.9004 | 52.1484 | -123.1338
1792.0156 | 123.1201 | -57.9987 | 64.8056 | -0.19089 | 0.0061673 | 0.069746 | 0.068594 | 0.13163 | -0.0058447 | -0.0068637 | 0.54916 | -0.0089124 | 0.060205 | 0.059962 | 0.00079042 | -0.0094102 | 64.5081 | 65.3412 | 0.082397 | -58.3282 | 64.8926 | -58.0719 | -58.1589 | -57.7057 | -6.0608 | -58.1818 | 64.856 | 64.7827 | -58.2001 | -58.2733 | -0.073242 | -0.16022 | 0.086975 | 123.3398 | -0.32959 | -0.16937 | -0.29755 | -0.20142 | -0.27466 | 0.050354 | 0.29297 | -0.18311 | 0.091552 | -0.022888 | 122.8912 | 122.5067 | 58.0811 | -122.9645 | 122.8546 | 122.7814 | 51.9379 | -123.0789
1793.0156 | 123.0469 | -58.0994 | 64.8193 | -0.168 | 0.01514 | 0.066969 | 0.074362 | 0.13078 | 0.0014185 | -0.0062229 | -0.045929 | -0.0072034 | 0.065119 | 0.058253 | 0.0046356 | -0.010905 | 64.7049 | 64.8422 | -0.20142 | -58.1955 | 64.9612 | -58.1177 | -58.2184 | -57.7835 | -5.8777 | -58.2916 | 64.8697 | 64.7964 | -58.255 | -58.3099 | -0.018311 | -0.11902 | 0.14191 | 122.9416 | -0.096131 | 0.022888 | -0.11444 | -0.15564 | -0.21057 | 0.050354 | 0.31586 | -0.19226 | 0.018311 | -0.022888 | 123.0606 | 122.8043 | 57.8979 | -123.0377 | 122.9691 | 122.8958 | 52.2217 | -123.1293
1794.0156 | 123.0515 | -58.0078 | 64.856 | -0.19089 | 0.0076627 | 0.069746 | 0.072012 | 0.13185 | -0.0052039 | -0.0057957 | -0.099335 | -0.009126 | 0.06341 | 0.059321 | 0.002713 | -0.0089828 | 64.7324 | 64.9567 | -0.11902 | -58.1268 | 64.9109 | -58.0582 | -58.136 | -57.7194 | -5.7678 | -58.2275 | 64.9063 | 64.8468 | -58.2138 | -58.2596 | -0.050355 | -0.12817 | 0.054932 | 122.9645 | -0.11902 | 0.009155 | -0.1236 | -0.20599 | -0.25177 | 0.050354 | 0.28839 | -0.21973 | 0.032044 | -0.009155 | 122.9187 | 122.7402 | 57.8888 | -122.9919 | 122.9141 | 122.8546 | 52.24 | -123.1155
1795.0156 | 123.0148 | -57.9987 | 64.8651 | -0.22903 | 0.010867 | 0.069105 | 0.07009 | 0.13121 | -0.0026405 | -0.0075047 | -0.11459 | -0.0086988 | 0.062982 | 0.061457 | 0.00057682 | -0.010051 | 64.7324 | 64.9155 | -0.32959 | -58.1635 | 64.9567 | -58.0673 | -58.1314 | -57.756 | -5.7404 | -58.2458 | 64.975 | 64.8605 | -58.1818 | -58.2413 | -0.068665 | -0.13275 | 0.091553 | 122.9141 | -0.16479 | -0.032043 | -0.13275 | -0.18311 | -0.24262 | 0.10986 | 0.24262 | -0.24719 | -0.004578 | -0.004577 | 122.9553 | 122.731 | 57.6691 | -122.9965 | 122.9736 | 122.8592 | 52.2583 | -123.1064
1796.0312 | 123.0881 | -58.0536 | 64.7873 | 0.0914 | 0.0087307 | 0.070814 | 0.070303 | 0.13035 | -0.0034949 | -0.0075047 | 0.16006 | -0.0084852 | 0.062982 | 0.05633 | 0.0033538 | -0.0079148 | 64.6408 | 64.856 | -0.027466 | -58.2367 | 64.8788 | -58.1223 | -58.223 | -57.7835 | -5.9967 | -58.255 | 64.8285 | 64.7415 | -58.2275 | -58.2825 | -0.068664 | -0.16937 | 0.091553 | 122.9095 | -0.1831 | -0.013733 | -0.14648 | -0.17395 | -0.22888 | 0.041199 | 0.27008 | -0.20142 | 0.027466 | -0.045776 | 122.9324 | 122.6944 | 58.0261 | -123.0103 | 122.8821 | 122.7951 | 52.0569 | -123.0698
1797.0156 | 123.0148 | -58.0261 | 64.8697 | -0.25955 | 0.010867 | 0.070814 | 0.076285 | 0.13035 | 0.0037683 | -0.0066501 | -0.22903 | -0.0078442 | 0.062982 | 0.059107 | 0.0037812 | -0.010051 | 64.5355 | 64.8697 | 0.073242 | -58.2275 | 64.9521 | -58.1177 | -58.1863 | -57.7927 | -6.3263 | -58.2916 | 64.9612 | 64.8422 | -58.2092 | -58.2962 | -0.091553 | -0.16022 | 0.082397 | 122.8958 | -0.20142 | -0.041199 | -0.33417 | -0.18311 | -0.27008 | 0.091553 | 0.23346 | -0.2655 | 0.004578 | -0.027466 | 122.9782 | 122.5616 | 58.0994 | -123.056 | 122.9874 | 122.8683 | 51.6998 | -123.1659
1798.0156 | 123.1293 | -57.9025 | 64.9017 | -0.30533 | 0.0059537 | 0.068891 | 0.068381 | 0.1295 | -0.0043495 | -0.0038731 | -0.038299 | -0.0089124 | 0.063196 | 0.058039 | 0.0031402 | -0.008342 | 64.8285 | 65.0345 | -0.10529 | -58.0536 | 64.9658 | -57.9895 | -58.0902 | -57.6279 | -6.1203 | -58.0948 | 64.9475 | 64.8514 | -58.0902 | -58.1909 | -0.086975 | -0.18768 | 0.064087 | 122.937 | -0.15106 | 0.036621 | -0.073242 | -0.18768 | -0.28839 | 0.045777 | 0.27466 | -0.19226 | 0.09613 | -0.050354 | 122.8683 | 122.731 | 57.7972 | -122.9919 | 122.85 | 122.7539 | 51.7822 | -123.0927
1799.0156 | 123.1018 | -58.0353 | 64.8422 | -0.068817 | 0.016849 | 0.06825 | 0.072867 | 0.13185 | 0.0035547 | -0.0025913 | -0.12222 | -0.0069898 | 0.063196 | 0.058039 | 0.0050628 | -0.01176 | 64.7507 | 64.8514 | -0.16022 | -58.1772 | 64.92 | -58.1039 | -58.1909 | -57.7423 | -6.1798 | -58.2916 | 64.9017 | 64.8148 | -58.2642 | -58.3008 | -0.068665 | -0.15564 | 0.07782 | 122.8867 | -0.14191 | 0.013733 | -0.091553 | -0.22888 | -0.2655 | 0.059509 | 0.29297 | -0.25635 | 0.009155 | -0.027466 | 122.9553 | 122.7859 | 57.8751 | -123.0331 | 122.937 | 122.85 | 51.8555 | -123.143
1800.0156 | 123.0835 | -57.9895 | 64.8422 | -0.12222 | 0.0046719 | 0.071027 | 0.071372 | 0.13014 | -0.0047767 | -0.0077183 | -0.015411 | -0.012117 | 0.061701 | 0.059962 | 0.0031402 | -0.014537 | 64.7964 | 65.0162 | -0.073242 | -58.1497 | 64.9155 | -58.049 | -58.1406 | -57.5729 | -6.0928 | -58.3786 | 64.9338 | 64.8148 | -58.2092 | -58.2367 | -0.059509 | -0.15106 | 0.073242 | 123.0057 | -0.16022 | -0.009155 | -0.045776 | -0.21973 | -0.24719 | 0.091553 | 0.41656 | -0.3891 | -0.14191 | -0.027466 | 122.905 | 122.7859 | 57.9163 | -122.9828 | 122.9233 | 122.8043 | 51.8967 | -123.0789
1801.0156 | 123.0331 | -58.0627 | 64.8376 | -0.045929 | 0.018771 | 0.06761 | 0.073935 | 0.13099 | 0.0050499 | -0.0010959 | -0.023041 | -0.007417 | 0.065759 | 0.058894 | 0.0067718 | -0.011974 | 64.7461 | 64.856 | -0.14191 | -58.1818 | 64.9246 | -58.1039 | -58.2047 | -57.7515 | -6.4453 | -58.3191 | 64.8926 | 64.7919 | -58.2458 | -58.2825 | -0.041199 | -0.14191 | 0.086976 | 122.9187 | -0.11902 | 0.022888 | -0.091552 | -0.18311 | -0.21973 | 0.054932 | 0.31128 | -0.25635 | -0.036621 | -0.045776 | 122.9874 | 122.8088 | 57.9208 | -123.0423 | 122.9553 | 122.8546 | 51.6174 | -123.1201
1802.0156 | 123.1018 | -57.9895 | 64.8239 | -0.068817 | 0.0053129 | 0.0706 | 0.070303 | 0.12822 | -0.0077673 | -0.0066501 | 0.0074766 | -0.010194 | 0.061914 | 0.058467 | 0.0012176 | -0.010265 | 64.7324 | 64.9521 | -0.091553 | -58.168 | 64.9017 | -58.0902 | -58.1589 | -57.6736 | -6.5048 | -58.136 | 64.8834 | 64.7827 | -58.1726 | -58.2275 | -0.10071 | -0.16937 | 0.077819 | 122.9416 | -0.17853 | -0.009155 | -0.091553 | -0.1831 | -0.23804 | 0.059509 | 0.31586 | -0.14648 | 0.091553 | -0.041199 | 122.8912 | 122.7219 | 57.8979 | -122.9828 | 122.8729 | 122.7722 | 51.4847 | -123.0515
1803.0156 | 123.0148 | -58.0124 | 64.888 | -0.21378 | 0.0093717 | 0.069319 | 0.07244 | 0.13206 | -0.00071785 | -0.0077183 | -0.14511 | -0.0059216 | 0.063623 | 0.058894 | 0.0050628 | -0.0091966 | 64.7141 | 64.8468 | -0.20142 | -58.1909 | 64.9612 | -58.1039 | -58.1863 | -57.7652 | -6.0837 | -58.2733 | 64.9429 | 64.8422 | -58.2184 | -58.2687 | -0.091553 | -0.17395 | 0.073243 | 122.8592 | -0.17853 | -0.004578 | -0.17395 | -0.20599 | -0.25635 | 0.054932 | 0.24719 | -0.26092 | -0.004577 | -0.045776 | 122.9736 | 122.7264 | 57.811 | -123.0743 | 122.9553 | 122.8546 | 51.9287 | -123.1567
1804.0156 | 123.111 | -58.0032 | 64.856 | 0.037994 | 0.0053129 | 0.069532 | 0.069022 | 0.12629 | -0.0032813 | -0.0045139 | 0.083771 | -0.0089124 | 0.06106 | 0.059748 | 0.0022858 | -0.0094102 | 64.7141 | 64.92 | -0.10071 | -58.1406 | 64.9109 | -58.0444 | -58.1451 | -57.6874 | -5.8777 | -58.168 | 64.8926 | 64.7827 | -58.168 | -58.2413 | -0.041199 | -0.14191 | 0.054932 | 122.9233 | -0.13733 | 0.004578 | -0.14191 | -0.1648 | -0.23804 | 0.036621 | 0.31586 | -0.1648 | 0.073242 | -0.073242 | 122.9141 | 122.7173 | 57.9025 | -123.0011 | 122.8958 | 122.7859 | 52.1255 | -123.0972
1805.0156 | 123.0881 | -57.9529 | 64.8972 | -0.12222 | 0.010867 | 0.067182 | 0.070517 | 0.13014 | -0.0022131 | -0.0062229 | -0.076446 | -0.008058 | 0.060205 | 0.057826 | 0.0037812 | -0.010478 | 64.8193 | 64.9933 | 0.11902 | -58.0582 | 64.9612 | -58.0215 | -58.0948 | -57.6416 | -6.0242 | -58.1451 | 64.9429 | 64.8697 | -58.1589 | -58.2092 | -0.068664 | -0.14191 | 0.064087 | 122.9462 | -0.10529 | 0.036621 | -0.07782 | -0.20599 | -0.25635 | 0.045776 | 0.31128 | -0.19226 | 0.064087 | -0.027466 | 122.9141 | 122.7722 | 58.0719 | -122.9919 | 122.8958 | 122.8226 | 51.9287 | -123.1064
1806.0156 | 123.024 | -58.0902 | 64.8148 | -0.045929 | 0.012576 | 0.067182 | 0.072653 | 0.12928 | 0.0061181 | -0.0040867 | 0.030365 | -0.0065626 | 0.062342 | 0.058467 | 0.0074126 | -0.012614 | 64.7324 | 64.8422 | -0.018311 | -58.2047 | 64.8834 | -58.1314 | -58.2092 | -57.7927 | -6.1935 | -58.3237 | 64.8972 | 64.7873 | -58.255 | -58.2962 | -0.041199 | -0.11902 | 0.068665 | 122.9324 | -0.11444 | 0.004578 | -0.082397 | -0.16479 | -0.20599 | 0.082398 | 0.29755 | -0.23346 | -0.027465 | -0.027466 | 122.9736 | 122.8226 | 58.0719 | -123.024 | 122.9874 | 122.8775 | 51.8967 | -123.111
1807.0156 | 123.0148 | -58.0353 | 64.8834 | -0.23666 | 0.011294 | 0.069105 | 0.072012 | 0.12907 | -0.0019995 | -0.0043003 | -0.17563 | -0.0054944 | 0.066614 | 0.058253 | 0.0035674 | -0.0072738 | 64.8468 | 64.6408 | 0.050354 | -58.1955 | 64.9521 | -58.1039 | -58.1863 | -57.7606 | -6.4224 | -58.2825 | 64.9475 | 64.8651 | -58.2184 | -58.2596 | -0.068665 | -0.15106 | 0.068664 | 122.6761 | -0.16022 | -0.009156 | -0.036621 | -0.18311 | -0.22431 | 0.064087 | 0.27466 | -0.24719 | -0.022888 | -0.018311 | 122.9874 | 122.8821 | 58.0856 | -123.0698 | 122.9828 | 122.9004 | 51.6129 | -123.143
1808.0156 | 123.111 | -58.0765 | 64.7873 | -1.1751 | 0.0076627 | 0.067823 | 0.069876 | 0.12928 | -0.0054175 | -0.0079319 | 0.12192 | -0.0084852 | 0.060633 | 0.05868 | 0.0018584 | -0.0079148 | 64.6591 | 64.8605 | 0.073242 | -58.2138 | 64.8834 | -58.1177 | -58.2001 | -57.7652 | -6.0974 | -58.2367 | 64.8331 | 64.7736 | -58.2367 | -58.3054 | -0.041199 | -0.1236 | 0.096131 | 122.937 | -0.13733 | -0.013733 | -0.12817 | -0.16022 | -0.22888 | 0.045777 | 0.31128 | -0.16022 | 0.068665 | -0.013732 | 122.9599 | 122.7356 | 58.1497 | -122.9874 | 122.9095 | 122.85 | 51.9791 | -123.0927
1809.0156 | 123.1384 | -58.0582 | 64.7736 | -0.17563 | 0.0053129 | 0.067823 | 0.07009 | 0.13185 | -0.0077673 | -0.0051547 | -0.11459 | -0.0086988 | 0.064051 | 0.057612 | 0.0029266 | -0.0094102 | 64.9521 | 64.5493 | -0.073242 | -58.1589 | 64.8514 | -58.1268 | -58.2413 | -57.756 | -5.9235 | -58.2413 | 64.8148 | 64.7278 | -58.2642 | -58.3237 | -0.068664 | -0.18311 | 0.077819 | 122.6074 | -0.10071 | 0.082397 | 0.17853 | -0.20599 | -0.2655 | 0.041198 | 0.30212 | -0.18311 | 0.082397 | -0.045777 | 122.9095 | 123.0103 | 57.9849 | -123.0148 | 122.8729 | 122.7859 | 52.1347 | -123.0972
1810.0156 | 123.0789 | -58.0444 | 64.8056 | 0.083771 | 0.010226 | 0.070173 | 0.070944 | 0.12886 | -0.0043495 | -0.0060093 | 0.13718 | -0.009126 | 0.062342 | 0.056758 | 0.0035674 | -0.0094102 | 64.6317 | 64.8468 | 0.022888 | -58.2184 | 64.8743 | -58.1223 | -58.2275 | -57.7835 | -6.2119 | -58.2642 | 64.8285 | 64.7278 | -58.2321 | -58.3099 | -0.077819 | -0.1831 | 0.068665 | 122.8912 | -0.17395 | 0.009155 | -0.17395 | -0.18768 | -0.2655 | 0.022888 | 0.26093 | -0.21973 | 0.045777 | -0.07782 | 122.9187 | 122.6761 | 58.0673 | -123.0331 | 122.8729 | 122.7722 | 51.8326 | -123.1155
1811.0312 | 122.9462 | -58.1406 | 64.7552 | 0.083771 | 0.015567 | 0.067823 | 0.073935 | 0.1295 | 0.0056909 | -0.0045139 | 0.09903 | -0.0044264 | 0.064691 | 0.05868 | 0.0057038 | -0.012828 | 64.6362 | 64.7186 | -0.17853 | -58.2916 | 64.8468 | -58.1818 | -58.2642 | -57.8567 | -6.3354 | -58.429 | 64.8239 | 64.7186 | -58.3282 | -58.3878 | -0.041199 | -0.1236 | 0.091553 | 122.8592 | -0.15106 | -0.027466 | -0.11902 | -0.18768 | -0.24719 | 0.068665 | 0.28381 | -0.28839 | -0.041199 | -0.036621 | 122.9874 | 122.7768 | 57.962 | -123.0194 | 122.9645 | 122.8592 | 51.8051 | -123.143
1812.0156 | 123.1064 | -58.0124 | 64.769 | -0.18326 | 0.011294 | 0.066755 | 0.068381 | 0.12928 | -0.0011451 | -0.0038731 | 0.27451 | -0.0086988 | 0.06341 | 0.058467 | 0.0046356 | -0.0079148 | 64.7415 | 64.9109 | -0.091553 | -58.1818 | 64.8743 | -58.0673 | -58.1726 | -57.692 | -6.3812 | -58.2184 | 64.8468 | 64.7507 | -58.2138 | -58.2733 | -0.054932 | -0.16022 | 0.10529 | 122.9233 | -0.16937 | -0.009156 | -0.027466 | -0.20142 | -0.26092 | 0.07782 | 0.32043 | -0.20599 | 0.054931 | -0.018311 | 122.8867 | 122.7539 | 57.9208 | -122.9416 | 122.8592 | 122.7631 | 51.6312 | -123.0423
1813.0156 | 123.0881 | -58.0261 | 64.8239 | -1.6405 | 0.0057401 | 0.069532 | 0.068594 | 0.12843 | -0.0060585 | -0.0068637 | 0.13718 | -0.009126 | 0.060846 | 0.058894 | 0.0031402 | -0.0087692 | 64.6866 | 64.8605 | -0.25635 | -58.1818 | 64.9109 | -58.0994 | -58.1589 | -57.7377 | -6.3629 | -58.2047 | 64.8926 | 64.8148 | -58.2092 | -58.2458 | -0.073242 | -0.13275 | 0.086975 | 122.8867 | -0.15564 | -0.022888 | -0.13733 | -0.18311 | -0.21973 | 0.068664 | 0.28839 | -0.17853 | 0.041199 | -0.009156 | 122.937 | 122.7127 | 57.7698 | -122.9828 | 122.9187 | 122.8409 | 51.6632 | -123.0698
1814.0156 | 123.0652 | -58.0124 | 64.8376 | 0.10666 | 0.0080899 | 0.068891 | 0.070303 | 0.12971 | -0.0030677 | -0.0034457 | 0.24399 | -0.0082716 | 0.060205 | 0.058039 | 0.0037812 | -0.0087692 | 64.7369 | 64.888 | -0.50354 | -58.1772 | 64.8788 | -58.0902 | -58.1406 | -57.6965 | -6.3812 | -58.2458 | 64.8605 | 64.7964 | -58.1955 | -58.2779 | -0.07782 | -0.12817 | 0.041199 | 122.9004 | -0.16479 | -0.036621 | -0.10071 | -0.18311 | -0.2655 | 0.022889 | 0.31586 | -0.23346 | 0.032043 | -0.041198 | 122.8912 | 122.7493 | 57.5089 | -122.9782 | 122.8729 | 122.8088 | 51.6312 | -123.1155
1815.0156 | 123.0927 | -57.9895 | 64.8331 | -0.25955 | 0.0083035 | 0.068678 | 0.071799 | 0.13099 | -0.0017859 | -0.0057957 | -0.11459 | -0.0078442 | 0.059351 | 0.05868 | 0.0033538 | -0.0096238 | 64.7827 | 64.9567 | -0.48065 | -58.1406 | 64.8972 | -58.0673 | -58.1497 | -57.692 | -6.4224 | -58.1818 | 64.8651 | 64.8102 | -58.2047 | -58.2092 | -0.07782 | -0.16022 | 0.064087 | 122.9462 | -0.15106 | 0.009155 | -0.050354 | -0.21515 | -0.21973 | 0.032043 | 0.29755 | -0.19226 | 0.027466 | -0.022888 | 122.8867 | 122.7722 | 57.5089 | -122.9828 | 122.8546 | 122.7997 | 51.5671 | -123.0423
1816.0156 | 123.0011 | -58.0399 | 64.8697 | -0.25192 | 0.01279 | 0.070173 | 0.073294 | 0.13185 | 0.0016321 | -0.0040867 | -0.25955 | -0.0078442 | 0.062128 | 0.05633 | 0.0059174 | -0.010692 | 64.7003 | 64.8285 | -0.88348 | -58.2184 | 64.9475 | -58.1543 | -58.1772 | -57.7927 | -6.4819 | -58.2962 | 64.9155 | 64.8056 | -58.2825 | -58.2916 | -0.11444 | -0.13733 | 0.07782 | 122.8683 | -0.17853 | -0.041199 | -0.16937 | -0.24262 | -0.25177 | 0.045776 | 0.24719 | -0.25635 | -0.004578 | -0.064087 | 122.9874 | 122.7402 | 57.1564 | -123.0469 | 122.9553 | 122.8455 | 51.5579 | -123.1613
1817.0156 | 123.1018 | -58.0627 | 64.7827 | -0.023041 | 0.0065945 | 0.071241 | 0.068167 | 0.12672 | -0.0032813 | -0.0064365 | 0.076141 | -0.0095532 | 0.060205 | 0.059321 | 0.0022858 | -0.0068466 | 64.6545 | 64.8468 | -0.55847 | -58.2092 | 64.8743 | -58.1451 | -58.2138 | -57.7606 | -6.1935 | -58.2321 | 64.8056 | 64.7507 | -58.255 | -58.3237 | -0.082398 | -0.15106 | 0.091553 | 122.9095 | -0.14648 | 0.004577 | -0.12817 | -0.19226 | -0.26093 | 0.022888 | 0.30212 | -0.16937 | 0.091552 | -0.032044 | 122.937 | 122.7173 | 57.5043 | -122.9965 | 122.8683 | 122.8134 | 51.8692 | -123.1064
1818.0156 | 123.1247 | -58.0811 | 64.7186 | 0.13718 | 0.0085171 | 0.068678 | 0.069449 | 0.13057 | -0.00093145 | -0.0062229 | 0.40421 | -0.009126 | 0.064264 | 0.055689 | 0.006131 | -0.010478 | 64.7232 | 64.8376 | -0.44861 | -58.3786 | 64.7919 | -58.1818 | -58.2733 | -57.7423 | -6.0059 | -58.2825 | 64.8102 | 64.7003 | -58.2642 | -58.3191 | -0.10071 | -0.19226 | 0.073242 | 122.9187 | -0.29755 | -0.10529 | 0.004578 | -0.1831 | -0.23804 | 0.091553 | 0.33874 | -0.20142 | 0.036621 | -0.018311 | 122.8729 | 122.8043 | 57.6324 | -122.9919 | 122.8912 | 122.7814 | 52.0752 | -123.0377
1819.0156 | 123.0972 | -58.0353 | 64.7873 | -0.15274 | 0.0063809 | 0.070387 | 0.067954 | 0.13014 | 0.00035035 | -0.0049411 | -0.23666 | -0.0086988 | 0.059992 | 0.056117 | 0.0031402 | -0.0091966 | 64.7415 | 64.9246 | -0.53558 | -57.9208 | 64.9429 | -58.0811 | -58.168 | -57.7469 | -6.1844 | -58.1909 | 64.8331 | 64.7598 | -58.2275 | -58.2779 | -0.045777 | -0.13275 | 0.15564 | 122.9599 | 0.11444 | 0.24719 | -0.045776 | -0.19226 | -0.24262 | 0.045777 | 0.28839 | -0.15564 | 0.086975 | -0.027465 | 122.9782 | 122.7768 | 57.4997 | -122.9553 | 122.8683 | 122.7951 | 51.8509 | -123.0652
1820.0156 | 123.0423 | -58.0124 | 64.8422 | 0.16769 | 0.013003 | 0.068678 | 0.070731 | 0.12971 | 0.0037683 | -0.0053683 | 0.20584 | -0.0061352 | 0.062982 | 0.056544 | 0.0048492 | -0.01176 | 64.7141 | 64.8285 | -0.77362 | -58.2092 | 64.9338 | -58.0948 | -58.1863 | -57.7332 | -6.4819 | -58.2642 | 64.8972 | 64.7964 | -58.2321 | -58.2916 | -0.082398 | -0.17395 | 0.091553 | 122.8409 | -0.19684 | -0.022889 | -0.12817 | -0.21973 | -0.27924 | 0.054932 | 0.27924 | -0.25177 | 0.027466 | -0.045776 | 122.9462 | 122.7264 | 57.2388 | -123.0286 | 122.9095 | 122.8088 | 51.5305 | -123.1338
1821.0156 | 123.1018 | -58.017 | 64.8422 | 0.0074768 | 0.0063809 | 0.071027 | 0.067526 | 0.13099 | -0.0056311 | -0.0062229 | 0.053253 | -0.008058 | 0.059778 | 0.057185 | 0.0022858 | -0.0094102 | 64.7461 | 64.9109 | -0.58136 | -58.1497 | 64.9155 | -58.0765 | -58.1543 | -57.692 | -6.1844 | -58.1726 | 64.8926 | 64.8056 | -58.1726 | -58.2413 | -0.059509 | -0.13733 | 0.073242 | 122.9279 | -0.13275 | 0.004578 | -0.09613 | -0.15564 | -0.2243 | 0.050354 | 0.32501 | -0.15564 | 0.068665 | -0.036621 | 122.9324 | 122.7631 | 57.4356 | -122.9965 | 122.9095 | 122.8226 | 51.8326 | -123.0835
1822.0156 | 123.1293 | -58.017 | 64.7644 | 0.14481 | 0.013217 | 0.069532 | 0.069876 | 0.13142 | 0.0035547 | -0.0049411 | 0.28976 | -0.0078442 | 0.061701 | 0.058894 | 0.0069854 | -0.0089828 | 64.7278 | 64.9246 | -0.33875 | -58.1451 | 64.8788 | -58.0811 | -58.1772 | -57.692 | -6.0013 | -58.2184 | 64.8697 | 64.7461 | -58.2184 | -58.2596 | -0.064087 | -0.16022 | 0.11444 | 122.9416 | -0.12817 | 0.032043 | -0.036621 | -0.20142 | -0.24262 | 0.10529 | 0.32501 | -0.20142 | 0.041199 | -0.01831 | 122.8958 | 122.7448 | 57.6782 | -122.9416 | 122.8867 | 122.7631 | 52.0157 | -123.024
1823.0156 | 123.0743 | -58.0353 | 64.7873 | 0.015106 | 0.0061673 | 0.069746 | 0.068808 | 0.12843 | -0.0039221 | -0.0068637 | 0.09903 | -0.0093396 | 0.059351 | 0.057185 | 0.0031402 | -0.008342 | 64.7003 | 64.8148 | -0.19226 | -58.1863 | 64.888 | -58.0994 | -58.1955 | -57.7606 | -6.3263 | -58.2275 | 64.8697 | 64.7552 | -58.2413 | -58.2779 | -0.064087 | -0.16022 | 0.10071 | 122.85 | -0.15106 | 0.009156 | -0.086975 | -0.20599 | -0.24262 | 0.082398 | 0.27466 | -0.19226 | 0.050354 | -0.032043 | 122.9233 | 122.7356 | 57.843 | -122.9828 | 122.905 | 122.7905 | 51.709 | -123.0652
1824.0156 | 123.0881 | -58.0399 | 64.7461 | 0.30502 | 0.0087307 | 0.070387 | 0.070517 | 0.12928 | 0.0020593 | -0.0064365 | 0.19821 | -0.007417 | 0.061914 | 0.058894 | 0.006131 | -0.0094102 | 64.7369 | 64.8834 | -0.19684 | -58.1863 | 64.8468 | -58.1131 | -58.2184 | -57.7148 | -6.2027 | -58.2504 | 64.8331 | 64.7369 | -58.2596 | -58.2916 | -0.073242 | -0.17853 | 0.10071 | 122.9233 | -0.14648 | 0.032044 | -0.009156 | -0.21973 | -0.25177 | 0.086975 | 0.32501 | -0.21057 | 0.041199 | -0.009156 | 122.8867 | 122.7768 | 57.843 | -122.9645 | 122.8729 | 122.7768 | 51.8372 | -123.0377
1825.0156 | 123.0423 | -58.0536 | 64.7827 | 0.16006 | 0.0072355 | 0.071882 | 0.067954 | 0.128 | -0.0017859 | -0.0062229 | 0.09903 | -0.0097668 | 0.057215 | 0.055262 | 0.0042084 | -0.0074876 | 64.6774 | 64.8285 | -0.25635 | -58.2321 | 64.8697 | -58.1314 | -58.2275 | -57.7881 | -6.3354 | -58.2687 | 64.8422 | 64.7644 | -58.255 | -58.2962 | -0.07782 | -0.17395 | 0.086975 | 122.8821 | -0.17853 | -0.004578 | -0.10529 | -0.20142 | -0.24262 | 0.059509 | 0.2655 | -0.21515 | 0.027466 | -0.018311 | 122.9233 | 122.731 | 57.7972 | -123.0103 | 122.8958 | 122.818 | 51.7181 | -123.0789
1826.0156 | 123.0881 | -58.0582 | 64.7415 | -0.045929 | 0.0076627 | -0.03557 | 0.06774 | 0.12843 | -0.0022131 | -0.0057957 | 0.045624 | -0.0086988 | 0.060205 | 0.057612 | 0.0037812 | -0.0098374 | 64.6912 | 64.8376 | 0.12817 | -58.1909 | 64.8376 | -58.1314 | -58.2321 | -57.7698 | -6.1295 | -58.2687 | 64.8102 | 64.7232 | -58.2687 | -58.3282 | -0.073242 | -0.17395 | 0.09613 | 122.8958 | -0.13275 | 0.041199 | -0.050354 | -0.21057 | -0.27008 | 0.068665 | 0.28839 | -0.21057 | 0.059509 | -0.01831 | 122.8958 | 122.7493 | 58.1863 | -122.9736 | 122.8683 | 122.7814 | 51.9287 | -123.0698
1827.0156 | 123.0881 | -58.1085 | 64.7095 | 0.068512 | 0.0059537 | 0.071668 | 0.068381 | 0.12779 | -0.0022131 | -0.0072911 | 0.12192 | -0.010408 | 0.061273 | 0.056117 | 0.0052764 | -0.0096238 | 64.6637 | 64.7919 | 0.4303 | -58.2687 | 64.8193 | -58.1726 | -58.2367 | -57.843 | -5.9189 | -58.2504 | 64.8376 | 64.7232 | -58.255 | -58.3099 | -0.064086 | -0.12817 | 0.10986 | 122.9004 | -0.16022 | -0.032044 | -0.045777 | -0.14648 | -0.20142 | 0.12817 | 0.2655 | -0.14191 | 0.05951 | 0.013733 | 122.9279 | 122.7722 | 58.5388 | -122.9462 | 122.9462 | 122.8317 | 52.1896 | -123.0194
1828.0156 | 122.9736 | -58.136 | 64.7461 | 0.099029 | 0.015994 | 0.067396 | 0.072226 | 0.12928 | 0.0039819 | -0.0038731 | 1.5715 | -0.0020764 | 0.062555 | 0.05633 | 0.0074126 | -0.010692 | 64.6042 | 64.6637 | 0.24719 | -58.3328 | 64.856 | -58.2184 | -58.2825 | -57.9575 | -5.5801 | -58.3832 | 64.8331 | 64.7324 | -58.3191 | -58.3603 | -0.082398 | -0.14648 | 0.10986 | 122.7997 | -0.19684 | -0.050354 | -0.14191 | -0.18311 | -0.2243 | 0.086975 | 0.17853 | -0.24719 | -0.022888 | -0.013733 | 122.9919 | 122.7402 | 58.3832 | -123.0286 | 122.9691 | 122.8683 | 52.5558 | -123.1064
1829.0156 | 123.0927 | -58.1268 | 64.7186 | 0.32028 | 0.010226 | 0.068037 | 0.067526 | 0.12629 | -0.0011451 | -0.0064365 | 0.19058 | -0.008058 | 0.059351 | 0.057398 | 0.0029266 | -0.010265 | 64.6912 | 64.8239 | 0.41657 | -58.2458 | 64.7736 | -58.1863 | -58.2596 | -57.7835 | -5.658 | -58.3008 | 64.7369 | 64.6774 | -58.2916 | -58.3832 | -0.059509 | -0.13275 | 0.054932 | 122.9507 | -0.11902 | 0.013733 | -0.027466 | -0.16479 | -0.25635 | 0.01831 | 0.34332 | -0.17395 | 0.082398 | -0.041199 | 122.9004 | 122.818 | 58.5434 | -122.9782 | 122.8638 | 122.8043 | 52.4689 | -123.1018
1830.0156 | 123.0652 | -58.1177 | 64.7278 | 0.14481 | 0.013858 | 0.06761 | 0.071158 | 0.13014 | 0.0016321 | -0.0040867 | 0.19058 | -0.0093396 | 0.064478 | 0.056117 | 0.00549 | -0.010905 | 64.6545 | 64.7186 | 0.48523 | -58.2916 | 64.8514 | -58.1772 | -58.2642 | -57.8384 | -6.0059 | -58.3649 | 64.8239 | 64.7095 | -58.3099 | -58.3466 | -0.059509 | -0.14648 | 0.1236 | 122.8363 | -0.17395 | -0.027466 | -0.073242 | -0.19226 | -0.22888 | 0.096131 | 0.27924 | -0.24719 | -0.01831 | -0.01831 | 122.9691 | 122.7722 | 58.6029 | -122.9919 | 122.9416 | 122.8271 | 52.1118 | -123.0743
1831.0312 | 123.0789 | -58.0719 | 64.8056 | -0.19089 | 0.0097989 | 0.074018 | 0.073081 | 0.1295 | -0.0028541 | -0.0049411 | -0.168 | -0.0076306 | 0.059992 | 0.057612 | 0.002713 | -0.0072738 | 64.6957 | 64.8743 | 0.6134 | -58.2001 | 64.8468 | -58.1451 | -58.223 | -57.7972 | -5.6717 | -58.2779 | 64.8193 | 64.7736 | -58.2733 | -58.3191 | -0.073243 | -0.15106 | 0.041199 | 122.9462 | -0.12817 | 0.022888 | -0.10986 | -0.20142 | -0.24719 | 0.013733 | 0.27466 | -0.20599 | 0.041199 | -0.032043 | 122.9187 | 122.7676 | 58.6853 | -123.0286 | 122.8912 | 122.8455 | 52.4002 | -123.1247
1832.0156 | 123.056 | -58.1497 | 64.6912 | 0.15244 | 0.014499 | 0.066755 | 0.069663 | 0.12779 | 0.0022729 | -0.0051547 | 0.18295 | -0.0072034 | 0.061487 | 0.057185 | 0.0039948 | -0.010692 | 64.6179 | 64.6912 | 0.75531 | -58.3282 | 64.8102 | -58.1863 | -58.3054 | -57.8659 | -6.0883 | -58.3786 | 64.7827 | 64.7095 | -58.3282 | -58.3969 | -0.036621 | -0.15564 | 0.11902 | 122.8409 | -0.17853 | -0.022888 | -0.073242 | -0.17853 | -0.24719 | 0.091553 | 0.28381 | -0.22888 | 0.018311 | 0.018311 | 122.9599 | 122.7676 | 58.905 | -122.9965 | 122.9324 | 122.8592 | 52.0615 | -123.0881
1833.0156 | 123.0194 | -58.1085 | 64.7324 | 0.10666 | 0.014285 | 0.070173 | 0.07009 | 0.13014 | 0.0016321 | -0.0040867 | 0.19058 | -0.007417 | 0.061701 | 0.057398 | 0.0050628 | -0.0081284 | 64.6362 | 64.6957 | 1.1719 | -58.2962 | 64.8834 | -58.1863 | -58.2916 | -57.8339 | -5.9418 | -58.3786 | 64.801 | 64.7461 | -58.3145 | -58.3694 | -0.077819 | -0.1831 | 0.15106 | 122.8043 | -0.18768 | -0.004578 | -0.096131 | -0.20599 | -0.26093 | 0.068664 | 0.27466 | -0.27008 | -0.009155 | 0.013733 | 122.9919 | 122.7448 | 59.2804 | -123.024 | 122.9095 | 122.8546 | 52.1667 | -123.1018
1834.0156 | 123.0057 | -58.1314 | 64.7552 | -0.068817 | 0.015567 | 0.068037 | 0.073294 | 0.12886 | 0.0020593 | -0.00088226 | -0.00015237 | -0.0082716 | 0.066187 | 0.059321 | 0.0059174 | -0.0091966 | 64.6362 | 64.7324 | 1.593 | -58.2916 | 64.8285 | -58.1955 | -58.2779 | -57.8659 | -5.9509 | -58.4061 | 64.801 | 64.7278 | -58.3282 | -58.3832 | -0.064087 | -0.14648 | 0.073242 | 122.8638 | -0.16022 | -0.013733 | -0.11902 | -0.19684 | -0.25177 | 0.045776 | 0.2655 | -0.27466 | -0.022888 | -0.027466 | 122.9599 | 122.7676 | 59.7244 | -123.0331 | 122.9324 | 122.8592 | 52.1805 | -123.1384
1835.0156 | 123.1155 | -58.1085 | 64.6957 | 0.15244 | 0.010653 | 0.067823 | 0.068381 | 0.13035 | -0.00050425 | -0.0045139 | 0.13718 | -0.008058 | 0.061914 | 0.055476 | 0.0033538 | -0.0094102 | 64.6088 | 64.9475 | 1.9226 | -58.255 | 64.7598 | -58.1497 | -58.255 | -57.7789 | -6.1935 | -58.2962 | 64.7507 | 64.682 | -58.3099 | -58.3466 | -0.041198 | -0.14648 | 0.064087 | 123.056 | -0.14648 | 0 | -0.086975 | -0.20142 | -0.23804 | 0.054931 | 0.32959 | -0.18768 | 0.050354 | -0.013733 | 122.8683 | 122.7173 | 60.0311 | -122.9507 | 122.8592 | 122.7905 | 51.915 | -123.0423
1836.0312 | 123.1201 | -58.1268 | 64.6912 | 0.17532 | 0.012149 | 0.069105 | 0.069663 | 0.12928 | -0.0019995 | -0.0030185 | 0.22873 | -0.009126 | 0.063623 | 0.058253 | 0.0035674 | -0.010692 | 64.6545 | 64.7461 | 1.8814 | -58.2458 | 64.769 | -58.1955 | -58.2779 | -57.8247 | -6.2393 | -58.3328 | 64.7781 | 64.6866 | -58.3282 | -58.3649 | -0.068665 | -0.15106 | 0.07782 | 122.8729 | -0.11902 | 0.032043 | -0.036621 | -0.20142 | -0.23804 | 0.086975 | 0.30212 | -0.20599 | 0.032043 | -0.004578 | 122.8958 | 122.7814 | 60.0082 | -122.9691 | 122.905 | 122.8134 | 51.8875 | -123.056
1837.0156 | 123.0194 | -58.1909 | 64.7095 | 0.20584 | 0.014926 | 0.063337 | 0.067954 | 0.13099 | -0.0011451 | -0.0021641 | 0.41946 | -0.0078442 | 0.064478 | 0.059321 | 0.007199 | -0.0077012 | 64.6408 | 64.6408 | 2.0599 | -58.2733 | 64.8331 | -58.2321 | -58.3145 | -57.9025 | -6.2622 | -58.429 | 64.7736 | 64.7049 | -58.3466 | -58.4152 | -0.041199 | -0.1236 | 0.1236 | 122.8317 | -0.082397 | 0.041199 | -0.068665 | -0.15564 | -0.2243 | 0.064087 | 0.28839 | -0.23804 | -0.013733 | -0.004578 | 123.024 | 122.8317 | 60.2509 | -123.024 | 122.9645 | 122.8958 | 51.9287 | -123.1247
1838.0469 | 123.056 | -58.1451 | 64.7644 | -0.084076 | 0.015353 | 0.067823 | 0.071799 | 0.13142 | 0.00013675 | -0.0023777 | -0.099335 | -0.0059216 | 0.062128 | 0.059107 | 0.0065582 | -0.013255 | 64.6683 | 64.769 | 1.6159 | -58.2413 | 64.8605 | -58.1726 | -58.2504 | -57.8384 | -6.1066 | -58.5068 | 64.8148 | 64.7278 | -58.3099 | -58.3694 | -0.027465 | -0.10529 | 0.096131 | 122.9141 | -0.09613 | 0.009155 | -0.09613 | -0.16479 | -0.2243 | 0.050354 | 0.3067 | -0.36163 | -0.13733 | -0.036621 | 123.0057 | 122.8134 | 59.761 | -123.0148 | 122.9599 | 122.8729 | 52.0386 | -123.1338
1839.0156 | 123.1201 | -58.1039 | 64.6866 | 0.19058 | 0.013217 | 0.06825 | 0.068381 | 0.12864 | -0.00093145 | -0.0038731 | 0.22873 | -0.0061352 | 0.062982 | 0.057185 | 0.0037812 | -0.0091966 | 64.6362 | 64.7507 | 1.6571 | -58.2825 | 64.8193 | -58.1909 | -58.287 | -57.8018 | -6.0242 | -58.3328 | 64.7736 | 64.7003 | -58.3054 | -58.3466 | -0.086975 | -0.1831 | 0.13275 | 122.8546 | -0.17853 | 0.004577 | -0.050354 | -0.20142 | -0.24262 | 0.086976 | 0.30212 | -0.22888 | 0.013733 | 0.013733 | 122.9233 | 122.7402 | 59.761 | -122.9736 | 122.8775 | 122.8043 | 52.0798 | -123.0331
1840.0156 | 123.0103 | -58.1406 | 64.7507 | -0.0077822 | 0.017917 | 0.069746 | 0.072653 | 0.12758 | 0.0031273 | -0.0049411 | 0.037995 | -0.0067762 | 0.065759 | 0.058039 | 0.00549 | -0.011119 | 64.6637 | 64.7186 | 1.9867 | -58.287 | 64.856 | -58.2092 | -58.2596 | -57.8659 | -5.9509 | -58.4061 | 64.8376 | 64.7415 | -58.3099 | -58.3969 | -0.068665 | -0.11902 | 0.10529 | 122.8592 | -0.14648 | -0.027465 | -0.086975 | -0.16937 | -0.25635 | 0.086975 | 0.27466 | -0.2655 | -0.009155 | -0.009155 | 122.9965 | 122.8043 | 60.1273 | -123.0103 | 122.9782 | 122.8821 | 52.1896 | -123.1476
1841.0156 | 123.0972 | -58.1589 | 64.7141 | 0.030365 | 0.0059537 | -0.03557 | 0.068808 | 0.12843 | -0.0073401 | -0.0066501 | 0.15244 | -0.0076306 | 0.060419 | 0.056971 | 0.0031402 | -0.0064194 | 64.5767 | 64.7369 | 2.4857 | -58.287 | 64.7919 | -58.1909 | -58.287 | -57.8567 | -5.7724 | -58.2962 | 64.7552 | 64.6957 | -58.3466 | -58.3832 | -0.032043 | -0.12817 | 0.07782 | 122.8958 | -0.12817 | 0 | -0.13733 | -0.18768 | -0.2243 | 0.041199 | 0.30213 | -0.13733 | 0.086975 | -0.01831 | 122.9507 | 122.7356 | 60.6445 | -123.0011 | 122.9141 | 122.8546 | 52.3865 | -123.0972
1842.0156 | 122.9462 | -58.1039 | 64.7644 | -0.15274 | 0.013644 | 0.067823 | 0.071585 | 0.13057 | 0.0024865 | -0.0047275 | -0.03067 | -0.0093396 | 0.065119 | 0.058467 | 0.0042084 | -0.012401 | 64.6729 | 64.7827 | 2.3483 | -58.255 | 64.8697 | -58.1909 | -58.255 | -57.8247 | -5.9555 | -58.3511 | 64.8193 | 64.7278 | -58.3054 | -58.3557 | -0.086975 | -0.15106 | 0.10529 | 122.8867 | -0.15106 | 0 | -0.091552 | -0.20142 | -0.25177 | 0.054932 | 0.27924 | -0.24719 | 0.004578 | -0.036621 | 122.9736 | 122.7768 | 60.4523 | -123.0194 | 122.9233 | 122.8317 | 52.1484 | -123.1201
1843.0156 | 123.0698 | -58.1268 | 64.6866 | 0.18295 | 0.014071 | 0.071027 | 0.070303 | 0.12864 | 0.00077755 | -0.0053683 | 0.25162 | -0.0069898 | 0.062128 | 0.058467 | 0.0039948 | -0.0089828 | 64.6042 | 64.7003 | 2.0737 | -58.3099 | 64.8056 | -58.2184 | -58.287 | -57.8613 | -5.9143 | -58.3511 | 64.7415 | 64.682 | -58.3237 | -58.3466 | -0.091553 | -0.16022 | 0.11902 | 122.8271 | -0.18311 | -0.022889 | -0.082397 | -0.19684 | -0.21973 | 0.054932 | 0.2655 | -0.2243 | -0.004577 | -0.004577 | 122.9324 | 122.731 | 60.2005 | -122.9736 | 122.8683 | 122.8088 | 52.2125 | -123.0331
1844.0156 | 123.0011 | -58.1543 | 64.7415 | -0.045929 | 0.016635 | 0.067396 | 0.073721 | 0.13099 | 0.0024865 | -0.0045139 | 0.0074766 | -0.0054944 | 0.062982 | 0.058253 | 0.004422 | -0.010051 | 64.65 | 64.7232 | 1.9867 | -58.287 | 64.8376 | -58.1909 | -58.2779 | -57.8751 | -5.7312 | -58.3969 | 64.8193 | 64.7324 | -58.3191 | -58.3649 | -0.036621 | -0.1236 | 0.09613 | 122.8775 | -0.13275 | -0.009155 | -0.091553 | -0.16479 | -0.21057 | 0.07782 | 0.27924 | -0.24262 | -0.032044 | -0.009155 | 122.9919 | 122.8043 | 60.141 | -123.0194 | 122.9736 | 122.8867 | 52.4231 | -123.1064
1845.0156 | 122.9965 | -58.1451 | 64.7827 | 0.030365 | 0.014499 | 0.068037 | 0.069449 | 0.12886 | 0.0037683 | -0.0047275 | 0.083771 | -0.006349 | 0.063623 | 0.057398 | 0.0050628 | -0.010265 | 64.6454 | 64.7186 | 1.7944 | -58.2825 | 64.8422 | -58.1635 | -58.2596 | -57.8796 | -5.7129 | -58.4152 | 64.8239 | 64.7598 | -58.3282 | -58.3603 | -0.01831 | -0.11444 | 0.059509 | 122.8638 | -0.13733 | -0.022888 | -0.13733 | -0.1831 | -0.21515 | 0.041199 | 0.2655 | -0.27008 | -0.054931 | -0.022888 | 122.9874 | 122.7905 | 59.9396 | -123.0423 | 122.9691 | 122.905 | 52.4323 | -123.143
1846.0156 | 123.1293 | -58.1635 | 64.7507 | 0.19058 | 0.016208 | 0.067823 | 0.072012 | 0.13163 | 0.00099115 | -0.0062229 | 0.17532 | -0.0076306 | 0.064905 | 0.060389 | 0.004422 | -0.010692 | 64.5493 | 64.6362 | 1.7578 | -58.3328 | 64.8239 | -58.2047 | -58.3054 | -57.9117 | -5.5115 | -58.4106 | 64.7919 | 64.7461 | -58.3374 | -58.4015 | -0.041199 | -0.14191 | 0.073243 | 122.7997 | -0.16937 | -0.027466 | -0.20142 | -0.17395 | -0.23804 | 0.041199 | 0.25177 | -0.24719 | -0.009156 | -0.004577 | 122.9874 | 122.7127 | 59.9213 | -123.056 | 122.9553 | 122.9095 | 52.652 | -123.1522
1847.0156 | 122.9919 | -58.2047 | 64.7095 | 0.0914 | 0.014499 | 0.068037 | 0.070303 | 0.13078 | 0.00035035 | -0.0015231 | 0.21347 | -0.0050672 | 0.062769 | 0.057612 | 0.00549 | -0.0079148 | 64.5401 | 64.6042 | 2.1057 | -58.3557 | 64.7781 | -58.2321 | -58.3557 | -57.9895 | -5.5481 | -58.493 | 64.769 | 64.6683 | -58.3969 | -58.4427 | -0.027466 | -0.15106 | 0.068664 | 122.8088 | -0.15106 | 0 | -0.16937 | -0.19226 | -0.23804 | 0.059509 | 0.21515 | -0.28839 | -0.050354 | -0.041199 | 122.9828 | 122.7448 | 60.3104 | -123.0652 | 122.9736 | 122.8729 | 52.6566 | -123.1522
1848.0625 | 123.0606 | -58.0765 | 64.8285 | -0.18326 | 0.01279 | 0.072096 | 0.074149 | 0.12928 | -0.0039221 | -0.0038731 | -0.11459 | -0.005708 | 0.062769 | 0.056971 | 0.0020722 | -0.010265 | 64.6088 | 64.7552 | 2.1606 | -58.2642 | 64.8514 | -58.1772 | -58.255 | -57.8613 | -5.3329 | -58.342 | 64.8697 | 64.8056 | -58.3191 | -58.3466 | -0.10071 | -0.17853 | 0.022888 | 122.8317 | -0.18768 | -0.009155 | -0.21973 | -0.24262 | -0.27008 | 0.041199 | 0.21515 | -0.2655 | 0.004578 | -0.022888 | 122.9279 | 122.6852 | 60.2371 | -123.0835 | 122.9462 | 122.8821 | 52.7435 | -123.175
1849.0156 | 122.9828 | -58.1177 | 64.7964 | 0.022736 | 0.016849 | 0.068037 | 0.070944 | 0.12864 | 0.0035547 | -0.0057957 | 0.060883 | -0.0067762 | 0.065546 | 0.06103 | 0.0042084 | -0.010692 | 64.6545 | 64.7324 | 1.6067 | -58.2596 | 64.8651 | -58.1406 | -58.255 | -57.8659 | -5.5664 | -58.3786 | 64.8285 | 64.7827 | -58.287 | -58.3466 | -0.022888 | -0.13733 | 0.068664 | 122.85 | -0.14191 | -0.004578 | -0.14191 | -0.16937 | -0.22888 | 0.032043 | 0.25177 | -0.26093 | -0.032043 | -0.013733 | 122.9828 | 122.7722 | 59.7244 | -123.0515 | 122.9462 | 122.9004 | 52.5513 | -123.143
1850.0156 | 123.0469 | -58.1268 | 64.769 | -0.14511 | 0.011722 | 0.06825 | 0.070517 | 0.13292 | -0.0022131 | -0.0064365 | -0.16037 | -0.0067762 | 0.064691 | 0.057398 | 0.0031402 | -0.008342 | 64.6133 | 64.7369 | 2.1423 | -58.2779 | 64.8651 | -58.1543 | -58.2733 | -57.8934 | -5.3009 | -58.3557 | 64.8422 | 64.769 | -58.3145 | -58.3603 | -0.027466 | -0.14648 | 0.09613 | 122.8638 | -0.15106 | -0.004578 | -0.15564 | -0.18768 | -0.23346 | 0.073242 | 0.23346 | -0.22888 | 0.004578 | 0 | 122.9919 | 122.7402 | 60.2692 | -123.0423 | 122.9691 | 122.8958 | 52.8259 | -123.1293
1851.0312 | 123.0927 | -58.136 | 64.6866 | -0.00015269 | 0.01044 | -0.03557 | 0.068381 | 0.12822 | -0.0069129 | -0.0083591 | 0.14481 | -0.008058 | 0.061487 | 0.06103 | 0.0012176 | -0.0057786 | 64.5447 | 64.7415 | 2.6596 | -58.3008 | 64.7781 | -58.2138 | -58.287 | -57.8705 | -5.3101 | -58.3054 | 64.7369 | 64.6866 | -58.3282 | -58.3878 | -0.07782 | -0.15106 | 0.091553 | 122.8775 | -0.16479 | -0.013733 | -0.14191 | -0.19226 | -0.25177 | 0.050354 | 0.2655 | -0.16937 | 0.082397 | 0 | 122.9141 | 122.6807 | 60.7956 | -122.9736 | 122.8729 | 122.8226 | 52.8259 | -123.0743
1852.0156 | 123.0423 | -58.1863 | 64.6957 | -0.068817 | 0.013858 | 0.066755 | 0.072226 | 0.128 | 0.00099115 | -0.0053683 | -0.068817 | -0.008058 | 0.063196 | 0.057185 | 0.0046356 | -0.010478 | 64.6225 | 64.6957 | 2.8198 | -58.3191 | 64.7736 | -58.2458 | -58.3145 | -58.0124 | -5.0766 | -58.4381 | 64.7461 | 64.6683 | -58.3786 | -58.4335 | -0.05951 | -0.12817 | 0.07782 | 122.8821 | -0.13275 | -0.004578 | -0.073242 | -0.19226 | -0.24719 | 0.050354 | 0.17395 | -0.25177 | -0.004577 | -0.027466 | 122.9599 | 122.8088 | 61.0062 | -123.0103 | 122.9324 | 122.8546 | 53.1097 | -123.1293
1853.0156 | 123.024 | -58.223 | 64.6408 | -0.22903 | 0.016421 | 0.066114 | 0.070731 | 0.12693 | 0.0031273 | -0.0040867 | -0.0077819 | -0.0054944 | 0.064051 | 0.05868 | 0.0067718 | -0.0098374 | 64.5859 | 64.682 | 3.2135 | -58.3603 | 64.7552 | -58.2779 | -58.3557 | -57.9575 | -5.191 | -58.4702 | 64.7507 | 64.65 | -58.4335 | -58.4656 | -0.054932 | -0.13275 | 0.11444 | 122.905 | -0.13733 | -0.004578 | -0.054932 | -0.21057 | -0.24262 | 0.10986 | 0.2655 | -0.24719 | -0.004578 | 0.009155 | 122.9782 | 122.8088 | 61.4365 | -122.9965 | 122.9736 | 122.8729 | 53.0319 | -123.1064
1854.0156 | 123.0331 | -58.2092 | 64.7141 | -0.25955 | 0.012149 | 0.069319 | 0.071158 | 0.12822 | -0.0013587 | -0.0057957 | 0.27451 | -0.0084852 | 0.066187 | 0.060816 | 0.0022858 | -0.0072738 | 64.5172 | 64.8743 | 3.3234 | -58.3603 | 64.8285 | -58.223 | -58.342 | -57.9391 | -5.2002 | -58.4061 | 64.7964 | 64.7049 | -58.374 | -58.4198 | -0.013732 | -0.13275 | 0.11444 | 123.0835 | -0.15106 | -0.018311 | -0.19684 | -0.16479 | -0.21057 | 0.082398 | 0.27008 | -0.19684 | 0.013733 | -0.009155 | 123.0377 | 122.7264 | 61.5326 | -123.056 | 123.0057 | 122.9141 | 53.009 | -123.1338
1855.0156 | 123.024 | -58.1955 | 64.7095 | -0.045929 | 0.015567 | 0.069105 | 0.070303 | 0.12758 | 0.0029137 | -0.0051547 | 0.083771 | -0.0095532 | 0.064051 | 0.056971 | 0.0076264 | -0.0096238 | 64.5584 | 64.6866 | 2.9663 | -58.3557 | 64.7781 | -58.2687 | -58.3282 | -57.9575 | -5.3879 | -58.461 | 64.7552 | 64.6637 | -58.374 | -58.4335 | -0.073242 | -0.13275 | 0.068664 | 122.8821 | -0.16022 | -0.027466 | -0.15106 | -0.17853 | -0.23804 | 0.045776 | 0.23804 | -0.2655 | -0.027466 | -0.045777 | 122.9736 | 122.7539 | 61.1618 | -123.0377 | 122.9507 | 122.8592 | 52.8076 | -123.143
1856.0156 | 123.0331 | -58.1955 | 64.6729 | 0.17532 | 0.017062 | 0.068464 | 0.070731 | 0.12672 | -0.00029045 | -0.0053683 | 0.26688 | -0.009126 | 0.063623 | 0.058467 | 0.0039948 | -0.010051 | 64.5264 | 64.6408 | 3.0991 | -58.3603 | 64.7781 | -58.2504 | -58.3328 | -57.9163 | -5.3604 | -58.4152 | 64.7507 | 64.6637 | -58.3786 | -58.4473 | -0.054931 | -0.13733 | 0.10528 | 122.8363 | -0.16479 | -0.027466 | -0.14649 | -0.18311 | -0.25177 | 0.077819 | 0.27924 | -0.21973 | 0.032044 | -0.009156 | 122.9736 | 122.7219 | 61.2946 | -123.0057 | 122.9462 | 122.8592 | 52.8351 | -123.1201
1857.0156 | 123.0972 | -58.2047 | 64.6225 | 0.15244 | 0.01514 | 0.069532 | 0.069449 | 0.13078 | -0.00093145 | -0.0030185 | 0.23636 | -0.006349 | 0.061273 | 0.057612 | 0.004422 | -0.0094102 | 64.5355 | 64.6637 | 3.36 | -58.3603 | 64.7507 | -58.2596 | -58.3649 | -57.8979 | -5.3467 | -58.3969 | 64.7141 | 64.6454 | -58.3878 | -58.4427 | -0.054932 | -0.16022 | 0.12817 | 122.8683 | -0.15564 | 0.004577 | -0.086976 | -0.18311 | -0.23804 | 0.091552 | 0.3067 | -0.19226 | 0.045776 | 0.022888 | 122.9553 | 122.7402 | 61.5646 | -122.9874 | 122.9187 | 122.85 | 52.858 | -123.0652
1858.0156 | 123.0515 | -58.2367 | 64.6729 | -0.18326 | 0.011508 | 0.070387 | 0.071372 | 0.13142 | 0.0012047 | -0.0028049 | -0.11459 | -0.0076306 | 0.063623 | 0.057612 | 0.0046356 | -0.011974 | 64.5081 | 64.6225 | 3.2867 | -58.3557 | 64.7644 | -58.2733 | -58.3649 | -57.9712 | -4.985 | -58.4518 | 64.7278 | 64.6729 | -58.4152 | -58.4747 | -0.036621 | -0.12817 | 0.091552 | 122.8592 | -0.11902 | 0.009155 | -0.1648 | -0.17853 | -0.23804 | 0.054931 | 0.2655 | -0.21515 | 0.022888 | 0 | 123.0011 | 122.7448 | 61.5234 | -123.0377 | 122.9645 | 122.9095 | 53.2516 | -123.1476
1859.0156 | 122.9736 | -58.2413 | 64.6454 | 0.045624 | 0.017917 | 0.068678 | 0.073508 | 0.13099 | 0.00035035 | -0.0045139 | 0.17532 | -0.0069898 | 0.064478 | 0.058894 | 0.00784 | -0.011119 | 64.5035 | 64.6042 | 3.0716 | -58.4152 | 64.7552 | -58.2779 | -58.374 | -58.0307 | -4.8935 | -58.5388 | 64.7141 | 64.6637 | -58.4427 | -58.4976 | -0.036621 | -0.13275 | 0.10986 | 122.8455 | -0.17395 | -0.041199 | -0.14191 | -0.20142 | -0.25635 | 0.068664 | 0.21057 | -0.29755 | -0.041198 | 0.01831 | 122.9965 | 122.7448 | 61.3129 | -123.0194 | 122.9553 | 122.905 | 53.3478 | -123.143
1860.0156 | 123.0286 | -58.2504 | 64.65 | -0.57236 | 0.011508 | 0.068891 | 0.072653 | 0.13035 | -0.00071785 | -0.0064365 | -0.068817 | -0.005708 | 0.061487 | 0.058253 | 0.0016448 | -0.0094102 | 64.4714 | 64.6179 | 2.8519 | -58.4015 | 64.7415 | -58.2962 | -58.3878 | -58.0215 | -4.6371 | -58.493 | 64.7278 | 64.6545 | -58.4427 | -58.5068 | -0.045777 | -0.13733 | 0.091553 | 122.8683 | -0.15106 | -0.013733 | -0.17853 | -0.19226 | -0.25635 | 0.07782 | 0.22888 | -0.24262 | 0.013733 | 0.004578 | 122.9919 | 122.7219 | 61.1023 | -123.0377 | 122.9782 | 122.905 | 53.6133 | -123.1567
1861.0156 | 123.0743 | -58.2504 | 64.6912 | 0.16006 | 0.01514 | 0.069532 | 0.072653 | 0.128 | 0.00077755 | -0.0049411 | 0.21347 | -0.0078442 | 0.0664 | 0.057398 | 0.0048492 | -0.010478 | 64.4669 | 64.5813 | 2.3483 | -58.3786 | 64.7827 | -58.2596 | -58.3466 | -57.9849 | -4.7653 | -58.4747 | 64.7415 | 64.6637 | -58.4244 | -58.461 | -0.009156 | -0.096131 | 0.091553 | 122.8317 | -0.12817 | -0.032043 | -0.2243 | -0.17395 | -0.21057 | 0.050354 | 0.2655 | -0.2243 | -0.013732 | -0.027466 | 123.0331 | 122.7173 | 60.5988 | -123.0377 | 122.9919 | 122.9141 | 53.4851 | -123.1522
1862.0156 | 123.0148 | -58.1497 | 64.7598 | -0.19089 | 0.0095853 | 0.06825 | 0.071372 | 0.13035 | -0.0028541 | -0.0079319 | -0.11459 | -0.0067762 | 0.058924 | 0.057398 | 0.0022858 | -0.0064194 | 64.5905 | 64.7278 | 2.2247 | -58.2916 | 64.856 | -58.1772 | -58.2642 | -58.0032 | -4.8798 | -58.3649 | 64.8239 | 64.7598 | -58.3282 | -58.3832 | -0.027466 | -0.11444 | 0.09613 | 122.8775 | -0.14191 | -0.027466 | -0.16937 | -0.17853 | -0.23346 | 0.064087 | 0.14648 | -0.21515 | 0.018311 | 0 | 123.0057 | 122.7402 | 60.3744 | -123.024 | 122.9736 | 122.9095 | 53.27 | -123.143
1863.0156 | 123.0057 | -58.223 | 64.6866 | 0.068512 | 0.014712 | 0.070173 | 0.070303 | 0.13035 | 0.0016321 | -0.0028049 | 0.015106 | -0.0082716 | 0.064478 | 0.05868 | 0.004422 | -0.010905 | 64.5309 | 64.6317 | 2.9984 | -58.3786 | 64.7507 | -58.2642 | -58.3466 | -57.9987 | -4.6875 | -58.4839 | 64.7415 | 64.6729 | -58.3969 | -58.4747 | -0.041199 | -0.1236 | 0.064087 | 122.8546 | -0.15564 | -0.032043 | -0.15564 | -0.17395 | -0.25177 | 0.054932 | 0.2243 | -0.26093 | -0.009156 | -0.013732 | 122.9736 | 122.7539 | 61.2213 | -123.0331 | 122.9645 | 122.8958 | 53.5355 | -123.1613
1864.0156 | 123.0469 | -58.2047 | 64.6912 | -0.19852 | 0.014712 | 0.065687 | 0.072012 | 0.12864 | 0.00077755 | -0.0051547 | -0.17563 | -0.0072034 | 0.064051 | 0.059321 | 0.0042084 | -0.0094102 | 64.5355 | 64.6683 | 3.2822 | -58.3466 | 64.801 | -58.2458 | -58.342 | -57.9666 | -4.5227 | -58.4244 | 64.7461 | 64.6957 | -58.3923 | -58.4793 | -0.041199 | -0.13733 | 0.10986 | 122.8729 | -0.14191 | -0.004578 | -0.15564 | -0.18768 | -0.27466 | 0.054932 | 0.23804 | -0.21973 | 0.054932 | 0.004578 | 123.0057 | 122.7402 | 61.4868 | -123.0331 | 122.9507 | 122.9004 | 53.6819 | -123.1705
1865.0156 | 123.0103 | -58.223 | 64.6729 | 0.13718 | 0.016208 | 0.06761 | 0.066672 | 0.13099 | -0.0047767 | -0.0060093 | 0.21347 | -0.0072034 | 0.064478 | 0.055689 | 0.004422 | -0.0096238 | 64.6729 | 64.5126 | 3.3279 | -58.3054 | 64.7461 | -58.287 | -58.374 | -58.0032 | -4.4815 | -58.4885 | 64.7186 | 64.6545 | -58.4106 | -58.4702 | -0.064087 | -0.15106 | 0.073242 | 122.7356 | -0.082398 | 0.068664 | 0 | -0.18768 | -0.24719 | 0.045776 | 0.21973 | -0.2655 | -0.01831 | -0.018311 | 122.9691 | 122.8958 | 61.5509 | -123.0469 | 122.9416 | 122.8775 | 53.7415 | -123.143
1866.0156 | 123.0698 | -58.3008 | 64.6088 | -0.023041 | 0.013003 | 0.06761 | 0.074576 | 0.12971 | 0.0018457 | -0.0047275 | -0.099335 | -0.005708 | 0.064051 | 0.059107 | 0.0037812 | -0.0096238 | 64.4485 | 64.5721 | 3.4653 | -58.4518 | 64.6591 | -58.3878 | -58.4747 | -58.049 | -4.5639 | -58.6716 | 64.5996 | 64.5767 | -58.4976 | -58.5754 | -0.086975 | -0.17395 | 0.050354 | 122.8729 | -0.15106 | 0.022888 | -0.16022 | -0.19684 | -0.27466 | -0.009156 | 0.25177 | -0.37079 | -0.096131 | -0.032044 | 122.9599 | 122.7493 | 61.7661 | -123.0835 | 122.9004 | 122.8775 | 53.7369 | -123.1842
1867.0156 | 123.0423 | -58.287 | 64.6042 | 0.71701 | 0.017489 | 0.068037 | 0.072653 | 0.12886 | 0.00077755 | -0.0019505 | -0.0077819 | -0.0069898 | 0.065973 | 0.059748 | 0.0046356 | -0.010692 | 64.4852 | 64.6042 | 2.8519 | -58.4518 | 64.6683 | -58.374 | -58.4427 | -58.0444 | -4.1473 | -58.548 | 64.6317 | 64.5493 | -58.4702 | -58.5571 | -0.086975 | -0.15564 | 0.064087 | 122.8912 | -0.16479 | -0.009155 | -0.11902 | -0.18311 | -0.27008 | 0.027466 | 0.24261 | -0.26093 | 0.009155 | -0.054932 | 122.9553 | 122.7722 | 61.1389 | -123.0469 | 122.9187 | 122.8363 | 54.1397 | -123.1613
1868.0156 | 123.0148 | -58.255 | 64.6545 | -0.22903 | 0.010226 | 0.069746 | 0.071158 | 0.13099 | -0.0032813 | -0.0043003 | -0.091705 | -0.0084852 | 0.061914 | 0.058039 | 0.0018584 | -0.0087692 | 64.4577 | 64.5859 | 2.7191 | -58.4106 | 64.7415 | -58.3282 | -58.3923 | -58.0353 | -4.2435 | -58.3282 | 64.7644 | 64.6866 | -58.4335 | -58.4656 | -0.073242 | -0.13733 | 0.086975 | 122.8409 | -0.15564 | -0.018311 | -0.19684 | -0.17853 | -0.21057 | 0.10986 | 0.21973 | -0.073242 | 0.13733 | 0.032043 | 122.9965 | 122.7127 | 60.9741 | -123.0469 | 123.0194 | 122.9416 | 54.0115 | -123.1201
1869.0156 | 123.024 | -58.2825 | 64.65 | -0.18326 | 0.013217 | 0.067823 | 0.070517 | 0.13163 | -0.00029045 | -0.0055821 | -0.14511 | -0.0086988 | 0.060846 | 0.058253 | 0.0042084 | -0.011974 | 64.4577 | 64.5996 | 2.9526 | -58.4198 | 64.7095 | -58.3374 | -58.4244 | -58.0215 | -4.2984 | -58.5022 | 64.6866 | 64.6179 | -58.4518 | -58.5205 | -0.054931 | -0.14191 | 0.05951 | 122.8821 | -0.13733 | 0.004577 | -0.19226 | -0.16937 | -0.23804 | 0.036621 | 0.26093 | -0.21973 | 0.018311 | -0.032043 | 122.9919 | 122.7402 | 61.235 | -123.0743 | 122.9691 | 122.9004 | 53.9841 | -123.1705
1870.0156 | 123.0927 | -58.2642 | 64.6179 | -0.15274 | 0.0097989 | 0.066969 | 0.067099 | 0.13014 | -0.0045631 | -0.0062229 | -0.068817 | -0.010194 | 0.06106 | 0.05868 | 0.0014312 | -0.0081284 | 64.4669 | 64.7003 | 2.9892 | -58.3832 | 64.6271 | -58.3145 | -58.4015 | -57.9895 | -4.0833 | -58.4335 | 64.6225 | 64.5401 | -58.4427 | -58.4976 | -0.050354 | -0.13733 | 0.009155 | 122.9645 | -0.11902 | 0.01831 | -0.15106 | -0.17853 | -0.23346 | 0.004578 | 0.27466 | -0.16937 | 0.064087 | -0.07782 | 122.8912 | 122.731 | 61.2534 | -123.0194 | 122.8867 | 122.8043 | 54.1809 | -123.1155
1871.0156 | 122.9828 | -58.3557 | 64.5721 | -0.03067 | 0.01578 | 0.068037 | 0.071585 | 0.12779 | 0.0029137 | -0.0060093 | 0.068512 | -0.0072034 | 0.064905 | 0.058894 | 0.004422 | -0.011974 | 64.3936 | 64.5126 | 3.0762 | -58.4885 | 64.6683 | -58.4015 | -58.4747 | -58.1131 | -4.1611 | -58.6212 | 64.6317 | 64.5493 | -58.5388 | -58.5983 | -0.045776 | -0.11902 | 0.09613 | 122.8683 | -0.13275 | -0.013733 | -0.17853 | -0.1831 | -0.24262 | 0.059509 | 0.24262 | -0.2655 | -0.022888 | -0.022889 | 123.024 | 122.7493 | 61.4319 | -123.0469 | 122.9874 | 122.905 | 54.1946 | -123.1705
1872.0156 | 123.0148 | -58.3237 | 64.5996 | -0.22141 | 0.0078763 | 0.069959 | 0.070517 | 0.12715 | -0.0041357 | -0.0064365 | -0.168 | -0.0084852 | 0.062982 | 0.058253 | 0.0020722 | -0.0085556 | 64.444 | 64.6088 | 3.4927 | -58.461 | 64.6545 | -58.3694 | -58.4381 | -58.0582 | -4.1382 | -58.5342 | 64.6545 | 64.5905 | -58.5159 | -58.5342 | -0.045777 | -0.11444 | 0.054932 | 122.9324 | -0.13733 | -0.022889 | -0.15564 | -0.19226 | -0.21057 | 0.054932 | 0.2655 | -0.21057 | 0 | -0.009155 | 122.9782 | 122.7676 | 61.8164 | -123.0377 | 122.9782 | 122.9141 | 54.1855 | -123.1338
1873.0156 | 123.0057 | -58.374 | 64.5584 | -0.0383 | 0.016208 | 0.068037 | 0.072653 | 0.12993 | 0.0033411 | -0.0064365 | 0.030365 | -0.0084852 | 0.064478 | 0.060389 | 0.0046356 | -0.010905 | 64.4028 | 64.5264 | 3.273 | -58.5159 | 64.6088 | -58.4198 | -58.493 | -58.0811 | -4.1702 | -58.6166 | 64.5676 | 64.5218 | -58.5434 | -58.5892 | -0.045777 | -0.11902 | 0.050354 | 122.9004 | -0.14191 | -0.022888 | -0.15564 | -0.16937 | -0.21515 | 0.009155 | 0.29297 | -0.24262 | -0.027466 | -0.036621 | 122.9828 | 122.7768 | 61.647 | -123.0515 | 122.9416 | 122.8958 | 54.2038 | -123.1476
1874.0156 | 123.1293 | -58.3466 | 64.5035 | -0.03067 | 0.0059537 | 0.069746 | 0.068381 | 0.12864 | -0.0077673 | -0.0051547 | 0.045624 | -0.011903 | 0.06106 | 0.058039 | 0.0012176 | -0.0085556 | 64.3799 | 64.595 | 3.4561 | -58.4747 | 64.5584 | -58.429 | -58.4976 | -58.0078 | -3.9368 | -58.4839 | 64.4989 | 64.4577 | -58.5388 | -58.5892 | -0.082397 | -0.15106 | 0.054932 | 122.9416 | -0.12817 | 0.022889 | -0.1236 | -0.19226 | -0.24261 | -0.004578 | 0.33875 | -0.13733 | 0.10528 | -0.045776 | 122.905 | 122.7264 | 61.8027 | -123.0011 | 122.8455 | 122.8043 | 54.4098 | -123.0927
1875.0156 | 123.0423 | -58.3557 | 64.5309 | -0.168 | 0.013003 | 0.068891 | 0.074149 | 0.12971 | 0.0018457 | -0.0047275 | -0.13748 | -0.0072034 | 0.064905 | 0.058467 | 0.0046356 | -0.0091966 | 64.4073 | 64.5218 | 3.2227 | -58.493 | 64.6271 | -58.4244 | -58.5114 | -58.0856 | -4.01 | -58.6075 | 64.5859 | 64.4989 | -58.5663 | -58.6029 | -0.068664 | -0.15564 | 0.09613 | 122.8775 | -0.13733 | 0.018311 | -0.1236 | -0.21057 | -0.24719 | 0.054931 | 0.27008 | -0.25177 | -0.004578 | -0.032044 | 122.9828 | 122.7631 | 61.5784 | -123.0423 | 122.9416 | 122.8546 | 54.3457 | -123.1338
1876.0156 | 123.0835 | -58.3328 | 64.5309 | -0.22141 | 0.0057401 | 0.070387 | 0.070944 | 0.13142 | -0.0039221 | -0.0079319 | -0.14511 | -0.0086988 | 0.062342 | 0.058039 | 0.0022858 | -0.010692 | 64.3936 | 64.6271 | 2.9984 | -58.4518 | 64.5859 | -58.3923 | -58.493 | -58.049 | -3.8681 | -58.5297 | 64.5676 | 64.5218 | -58.5297 | -58.58 | -0.059509 | -0.16022 | 0.054931 | 122.9599 | -0.11902 | 0.041199 | -0.13733 | -0.19684 | -0.24719 | 0.036621 | 0.28381 | -0.19684 | 0.050354 | -0.009155 | 122.9187 | 122.7264 | 61.3312 | -123.024 | 122.9004 | 122.8546 | 54.4647 | -123.111
1877.0312 | 123.0103 | -58.4335 | 64.4806 | 0.34317 | 0.01578 | 0.070173 | 0.069449 | 0.13249 | 0.00077755 | -0.0077183 | 0.17532 | -0.0076306 | 0.062555 | 0.059962 | 0.0020722 | -0.0096238 | 64.389 | 64.3662 | 3.1036 | -58.5526 | 64.5996 | -58.4747 | -58.5663 | -58.1726 | -3.9597 | -58.6716 | 64.5447 | 64.4531 | -58.6212 | -58.6716 | -0.041198 | -0.13275 | 0.11902 | 122.7997 | -0.11902 | 0.013733 | -0.091553 | -0.18768 | -0.23804 | 0.064087 | 0.26093 | -0.23804 | 0 | -0.027466 | 123.0331 | 122.8226 | 61.5372 | -123.0469 | 122.9782 | 122.8867 | 54.4739 | -123.1522
1878.0156 | 123.1705 | -58.3511 | 64.476 | -0.099335 | 0.0059537 | 0.069105 | 0.069235 | 0.13035 | -0.0045631 | -0.0057957 | 0.030365 | -0.0086988 | 0.059778 | 0.058894 | 0.0020722 | -0.0094102 | 64.3936 | 64.5813 | 3.3417 | -58.4702 | 64.5401 | -58.4335 | -58.5114 | -58.0124 | -3.511 | -58.4839 | 64.5309 | 64.4394 | -58.5526 | -58.6212 | -0.082398 | -0.16022 | 0.064087 | 122.9324 | -0.11902 | 0.041199 | -0.082397 | -0.20142 | -0.27008 | 0.054932 | 0.33874 | -0.13275 | 0.13733 | -0.036621 | 122.8912 | 122.7448 | 61.6928 | -122.9874 | 122.8821 | 122.7905 | 54.8401 | -123.0972
1879.0156 | 123.024 | -58.3832 | 64.5172 | -0.21378 | 0.012149 | 0.06825 | 0.074362 | 0.12779 | -0.00071785 | -0.0077183 | 0.21347 | -0.0082716 | 0.063837 | 0.05868 | 0.0033538 | -0.011119 | 64.3204 | 64.4897 | 3.7308 | -58.4381 | 64.6408 | -58.4152 | -58.5342 | -58.1497 | -3.8315 | -58.6395 | 64.595 | 64.4943 | -58.6121 | -58.6212 | -0.032043 | -0.15106 | 0.1236 | 122.8729 | -0.054931 | 0.096131 | -0.19684 | -0.22888 | -0.23804 | 0.07782 | 0.23346 | -0.25635 | -0.01831 | -0.022888 | 123.024 | 122.7036 | 62.114 | -123.0515 | 122.9782 | 122.8775 | 54.5517 | -123.1384
1880.0156 | 123.1247 | -58.3328 | 64.476 | -0.053558 | 0.0025357 | 0.069959 | 0.068808 | 0.13142 | -0.0043495 | -0.0062229 | 0.030365 | -0.0099806 | 0.062769 | 0.057398 | 0.0020722 | -0.0074876 | 64.4257 | 64.5905 | 3.7582 | -58.5022 | 64.5355 | -58.429 | -58.5159 | -58.0261 | -3.5248 | -58.5114 | 64.4989 | 64.4577 | -58.5663 | -58.6304 | -0.09613 | -0.1831 | 0.059509 | 122.9233 | -0.16937 | 0.013733 | -0.050354 | -0.23346 | -0.29755 | 0.022888 | 0.3067 | -0.17853 | 0.11902 | -0.01831 | 122.8683 | 122.7585 | 62.0911 | -122.9919 | 122.8317 | 122.7905 | 54.808 | -123.1064
1881.0156 | 123.0148 | -58.4518 | 64.4348 | -0.25192 | 0.014499 | 0.065901 | 0.073081 | 0.13142 | 0.0048363 | -0.0049411 | -0.045929 | -0.0065626 | 0.062769 | 0.060816 | 0.0046356 | -0.012187 | 64.3524 | 64.4806 | 3.6346 | -58.5663 | 64.563 | -58.4839 | -58.5938 | -58.1177 | -3.7125 | -58.6807 | 64.4943 | 64.4119 | -58.6304 | -58.7036 | -0.032044 | -0.14191 | 0.12817 | 122.9324 | -0.11444 | 0.027466 | -0.082397 | -0.17853 | -0.25177 | 0.05951 | 0.33417 | -0.22888 | 0.022888 | -0.022888 | 123.0148 | 122.8043 | 62.0865 | -123.0286 | 122.9462 | 122.8638 | 54.7394 | -123.1384
1882.0156 | 123.0972 | -58.3832 | 64.476 | -0.4274 | 0.0076627 | 0.068037 | 0.071799 | 0.13163 | -0.0030677 | -0.0055821 | -0.099335 | -0.0078442 | 0.062128 | 0.057826 | 0.0033538 | -0.0098374 | 64.3753 | 64.5996 | 3.5614 | -58.493 | 64.5309 | -58.429 | -58.5205 | -58.0627 | -3.6163 | -58.5434 | 64.5126 | 64.4348 | -58.5709 | -58.5938 | -0.045776 | -0.13733 | 0.054932 | 122.9828 | -0.10986 | 0.027466 | -0.10071 | -0.18768 | -0.21057 | 0.036621 | 0.32043 | -0.16022 | 0.050354 | -0.041199 | 122.9141 | 122.7585 | 61.9446 | -122.9965 | 122.8958 | 122.818 | 54.7668 | -123.0698
1883.0156 | 123.0789 | -58.3649 | 64.5081 | -0.20615 | 0.0057401 | 0.066969 | 0.070944 | 0.1295 | -0.00093145 | -0.0040867 | -0.12222 | -0.010835 | 0.061487 | 0.057398 | 0.0046356 | -0.0098374 | 64.3982 | 64.6133 | 3.3691 | -58.4839 | 64.5721 | -58.4427 | -58.5068 | -58.0719 | -3.5843 | -58.5617 | 64.5447 | 64.4531 | -58.5892 | -58.5983 | -0.07782 | -0.14191 | 0.064087 | 122.9782 | -0.11902 | 0.022888 | -0.10986 | -0.2243 | -0.23346 | 0.036621 | 0.29297 | -0.19684 | 0.036621 | -0.054932 | 122.937 | 122.7631 | 61.734 | -123.0148 | 122.9095 | 122.818 | 54.7806 | -123.1064
1884.0156 | 123.1064 | -58.3649 | 64.4623 | 0.0914 | 0.0055265 | 0.06825 | 0.067099 | 0.12864 | -0.0049903 | -0.0089999 | 0.12192 | -0.0089124 | 0.061701 | 0.058894 | 0.0035674 | -0.0089828 | 64.3341 | 64.5309 | 3.5202 | -58.5205 | 64.5447 | -58.429 | -58.5159 | -58.0627 | -3.4287 | -58.5434 | 64.5309 | 64.4302 | -58.5663 | -58.5892 | -0.064087 | -0.15106 | 0.082398 | 122.8958 | -0.15564 | -0.004578 | -0.12817 | -0.20142 | -0.2243 | 0.068665 | 0.30212 | -0.17853 | 0.045776 | -0.032043 | 122.9095 | 122.699 | 61.8851 | -122.9782 | 122.8958 | 122.7951 | 54.9362 | -123.0515
1885.0156 | 123.0194 | -58.342 | 64.5081 | -0.24429 | 0.0078763 | 0.068678 | 0.07009 | 0.13142 | -0.0024269 | -0.0057957 | -0.13748 | -0.0099806 | 0.06106 | 0.058253 | 0.0042084 | -0.01176 | 64.4028 | 64.6042 | 3.7399 | -58.461 | 64.6088 | -58.4106 | -58.5022 | -58.0765 | -3.5431 | -58.58 | 64.5905 | 64.4806 | -58.5342 | -58.5938 | -0.068665 | -0.16022 | 0.10071 | 122.9462 | -0.11902 | 0.041198 | -0.10529 | -0.19226 | -0.25177 | 0.082397 | 0.2655 | -0.23804 | 0.013733 | -0.027466 | 122.9507 | 122.7448 | 62.0819 | -123.0103 | 122.9324 | 122.8226 | 54.7989 | -123.1018
1886.0156 | 123.1338 | -58.287 | 64.5035 | -0.168 | 0.0053129 | 0.069105 | 0.065604 | 0.1295 | -0.0026405 | -0.0057957 | -0.2214 | -0.0078442 | 0.060205 | 0.060389 | 0.0033538 | -0.0089828 | 64.4577 | 64.6683 | 3.6163 | -58.4518 | 64.595 | -58.4015 | -58.4518 | -57.9666 | -3.3875 | -58.493 | 64.5584 | 64.476 | -58.493 | -58.5434 | -0.11444 | -0.16479 | 0.091553 | 122.9553 | -0.16479 | 0 | -0.045776 | -0.20599 | -0.25635 | 0.054932 | 0.32043 | -0.20599 | 0.050354 | -0.027466 | 122.8821 | 122.7448 | 61.9034 | -122.9553 | 122.8455 | 122.7631 | 54.8996 | -123.0469
1887.0312 | 123.0743 | -58.3191 | 64.5081 | 0.19821 | 0.014285 | 0.066755 | 0.072012 | 0.13057 | 0.0020593 | -0.0049411 | 0.15244 | -0.0065626 | 0.065119 | 0.06103 | 0.0059174 | -0.013042 | 64.3753 | 64.5172 | 2.9892 | -58.5251 | 64.5996 | -58.4244 | -58.493 | -58.0399 | -3.7445 | -58.5846 | 64.5721 | 64.4577 | -58.5342 | -58.5663 | -0.10529 | -0.17395 | 0.091552 | 122.8363 | -0.20599 | -0.032043 | -0.13275 | -0.21515 | -0.24719 | 0.064087 | 0.27924 | -0.2655 | -0.018311 | -0.050354 | 122.9187 | 122.6944 | 61.3083 | -123.0011 | 122.8912 | 122.7768 | 54.5746 | -123.0743
1888.0156 | 123.0743 | -58.287 | 64.563 | 0.12192 | 0.0085171 | 0.069105 | 0.067954 | 0.12971 | -0.0037085 | -0.0049411 | 0.24399 | -0.011689 | 0.062769 | 0.056971 | 0.002713 | -0.0072738 | 64.4531 | 64.6317 | 3.0808 | -58.4518 | 64.5996 | -58.3466 | -58.4335 | -57.9803 | -3.8681 | -58.4976 | 64.595 | 64.5172 | -58.4427 | -58.5205 | -0.05951 | -0.14648 | 0.036621 | 122.9187 | -0.16479 | -0.01831 | -0.10986 | -0.15564 | -0.23346 | 0.032044 | 0.3067 | -0.21057 | 0.022888 | -0.045776 | 122.8867 | 122.7402 | 61.3678 | -122.9965 | 122.8821 | 122.8043 | 54.4189 | -123.0835
1889.0156 | 123.0972 | -58.2458 | 64.5813 | -0.18326 | 0.0076627 | 0.070173 | 0.07009 | 0.1295 | 0.0012047 | -0.0051547 | -0.11459 | -0.0086988 | 0.062982 | 0.056544 | 0.0052764 | -0.011119 | 64.5126 | 64.6957 | 3.2318 | -58.4152 | 64.6362 | -58.3328 | -58.4152 | -57.9437 | -3.717 | -58.461 | 64.6454 | 64.5309 | -58.4656 | -58.5114 | -0.086975 | -0.16937 | 0.054931 | 122.9416 | -0.16937 | 0 | -0.068665 | -0.21973 | -0.2655 | 0.064087 | 0.30212 | -0.21515 | 0.050354 | -0.050354 | 122.8821 | 122.7585 | 61.4777 | -122.9965 | 122.8912 | 122.7768 | 54.5288 | -123.0927
1890.0156 | 123.1018 | -58.2962 | 64.5172 | 0.12192 | 0.01044 | 0.068037 | 0.069663 | 0.12843 | -0.0013587 | -0.0047275 | 0.21347 | -0.0097668 | 0.062769 | 0.059107 | 0.0033538 | -0.0098374 | 64.4806 | 64.6362 | 2.9755 | -58.429 | 64.6088 | -58.3603 | -58.4473 | -57.9529 | -3.7262 | -58.4976 | 64.5676 | 64.444 | -58.4885 | -58.5434 | -0.064087 | -0.15106 | 0.091553 | 122.9324 | -0.13275 | 0.018311 | -0.036621 | -0.19226 | -0.24719 | 0.050354 | 0.34332 | -0.20142 | 0.045776 | -0.073242 | 122.905 | 122.7768 | 61.2717 | -122.9645 | 122.8638 | 122.7402 | 54.57 | -123.0606
1891.0156 | 123.0743 | -58.2321 | 64.6133 | -0.16037 | 0.0074491 | 0.068891 | 0.069876 | 0.13035 | -0.0039221 | -0.0072911 | -0.12985 | -0.009126 | 0.061273 | 0.056544 | 0.0067718 | -0.010051 | 64.5493 | 64.7507 | 3.0533 | -58.3466 | 64.7003 | -58.2916 | -58.3649 | -57.9163 | -3.7491 | -58.429 | 64.6729 | 64.5676 | -58.4198 | -58.4381 | -0.059509 | -0.13275 | 0.086975 | 122.9828 | -0.11444 | 0.01831 | -0.064087 | -0.18768 | -0.20599 | 0.05951 | 0.31586 | -0.19684 | 0.009155 | -0.045776 | 122.9324 | 122.7814 | 61.2854 | -122.9782 | 122.905 | 122.7997 | 54.483 | -123.0515
1892.0156 | 123.0515 | -58.2275 | 64.65 | -0.24429 | 0.0091581 | 0.069959 | 0.069449 | 0.12822 | 0.0014185 | -0.0047275 | -0.18326 | -0.007417 | 0.064051 | 0.058039 | 0.0033538 | -0.012187 | 64.5538 | 64.7141 | 2.9022 | -58.3511 | 64.7049 | -58.287 | -58.3832 | -57.9437 | -3.6667 | -58.4564 | 64.7003 | 64.6225 | -58.4244 | -58.4839 | -0.059509 | -0.15564 | 0.054932 | 122.9416 | -0.1236 | 0.032044 | -0.09613 | -0.19684 | -0.25635 | 0.050354 | 0.28381 | -0.22888 | 0.027466 | -0.027465 | 122.9324 | 122.7814 | 61.1298 | -123.0331 | 122.9279 | 122.85 | 54.5609 | -123.1338
1893.0156 | 123.1338 | -58.2413 | 64.5767 | -0.19089 | 0.0078763 | 0.070173 | 0.070517 | 0.12907 | -0.0017859 | -0.0047275 | -2.3729 | -0.010835 | 0.059351 | 0.059748 | 0.0065582 | -0.010051 | 64.5813 | 64.7919 | 3.3554 | -58.3328 | 64.6683 | -58.2779 | -58.3694 | -57.8613 | -3.6621 | -58.4427 | 64.6133 | 64.5264 | -58.4106 | -58.4885 | -0.036621 | -0.12817 | 0.091553 | 123.0331 | -0.091553 | 0.036621 | 0.004578 | -0.16937 | -0.24719 | 0.036621 | 0.37994 | -0.20142 | 0.045776 | -0.050354 | 122.9095 | 122.8226 | 61.5967 | -122.9462 | 122.8546 | 122.7676 | 54.5792 | -123.0652
1894.0156 | 123.1293 | -58.2367 | 64.5859 | 0.13718 | 0.012576 | 0.066969 | 0.071372 | 0.13142 | 0.0027001 | -0.0047275 | 0.083771 | -0.009126 | 0.063837 | 0.058894 | 0.0059174 | -0.011546 | 64.5538 | 64.6957 | 3.1815 | -58.3694 | 64.6271 | -58.3237 | -58.3878 | -57.9025 | -3.891 | -58.4244 | 64.6408 | 64.5401 | -58.3878 | -58.4747 | -0.086975 | -0.15106 | 0.041199 | 122.9324 | -0.13275 | 0.01831 | -0.032043 | -0.15106 | -0.23804 | 0.054932 | 0.33417 | -0.18768 | 0.050354 | -0.045776 | 122.8638 | 122.7905 | 61.4182 | -122.9736 | 122.8775 | 122.7768 | 54.3457 | -123.0606
1895.0156 | 123.0698 | -58.2138 | 64.5859 | 0.0074768 | 0.0055265 | 0.069532 | 0.066885 | 0.12907 | -0.0026405 | -0.0047275 | 0.15244 | -0.0099806 | 0.063196 | 0.05633 | 0.0048492 | -0.0068466 | 64.4989 | 64.6683 | 3.0579 | -58.3923 | 64.7141 | -58.2962 | -58.3878 | -57.9758 | -4.0878 | -58.2825 | 64.6729 | 64.5721 | -58.4061 | -58.4656 | -0.082398 | -0.17395 | 0.12817 | 122.8821 | -0.17853 | -0.004578 | -0.086975 | -0.19226 | -0.25177 | 0.086976 | 0.23804 | -0.068665 | 0.1831 | -0.013732 | 122.9279 | 122.7127 | 61.2717 | -122.9736 | 122.8867 | 122.7859 | 54.126 | -123.0515
1896.0156 | 123.1338 | -58.168 | 64.6225 | -0.076447 | 0.0053129 | 0.0706 | 0.069449 | 0.13057 | -0.0030677 | -0.0049411 | -0.0077819 | -0.010194 | 0.058924 | 0.058253 | 0.0039948 | -0.0087692 | 64.5813 | 64.7507 | 3.3234 | -58.3008 | 64.7324 | -58.2504 | -58.3511 | -57.8384 | -4.216 | -58.3557 | 64.7461 | 64.6179 | -58.342 | -58.4106 | -0.082397 | -0.1831 | 0.10986 | 122.9187 | -0.13275 | 0.050354 | -0.041199 | -0.17395 | -0.24262 | 0.1236 | 0.32959 | -0.18768 | 0.054932 | -0.004578 | 122.9004 | 122.7493 | 61.4914 | -122.9736 | 122.9141 | 122.7859 | 53.952 | -123.0331
1897.0156 | 123.0927 | -58.1955 | 64.5996 | 0.11429 | 0.010226 | 0.070814 | 0.069663 | 0.128 | 0.00035035 | -0.0079319 | 0.23636 | -0.0099806 | 0.061273 | 0.057185 | 0.0050628 | -0.0091966 | 64.5584 | 64.6912 | 3.479 | -58.3786 | 64.7049 | -58.2779 | -58.3511 | -57.9071 | -4.2572 | -58.4152 | 64.6774 | 64.5767 | -58.4106 | -58.4656 | -0.082397 | -0.15564 | 0.10529 | 122.8867 | -0.18311 | -0.027466 | -0.041198 | -0.21515 | -0.27008 | 0.07782 | 0.28839 | -0.21973 | 0.050354 | -0.022888 | 122.9004 | 122.7539 | 61.6745 | -122.9507 | 122.8729 | 122.7722 | 53.9383 | -123.0652
1898.0156 | 123.0469 | -58.2779 | 64.5767 | 0.12192 | 0.01514 | 0.065901 | 0.071799 | 0.12886 | 0.0022729 | -0.0045139 | 0.19058 | -0.0078442 | 0.065546 | 0.057185 | 0.0050628 | -0.010478 | 64.4852 | 64.5767 | 3.1357 | -58.4427 | 64.682 | -58.3603 | -58.4198 | -57.9803 | -4.3991 | -58.5342 | 64.6683 | 64.5355 | -58.5022 | -58.5297 | -0.082398 | -0.14191 | 0.10529 | 122.8546 | -0.16479 | -0.022888 | -0.091553 | -0.2243 | -0.25177 | 0.091553 | 0.29755 | -0.25635 | -0.004578 | -0.041199 | 122.9599 | 122.7631 | 61.4136 | -122.9965 | 122.9462 | 122.8134 | 53.8788 | -123.1064
1899.0156 | 123.0881 | -58.1955 | 64.6408 | 0.0074768 | 0.0065945 | 0.069532 | 0.069663 | 0.13121 | -0.0043495 | -0.0047275 | 0.16006 | -0.0065626 | 0.060846 | 0.055903 | 0.0046356 | -0.010051 | 64.5447 | 64.682 | 3.2913 | -58.3466 | 64.7369 | -58.255 | -58.3328 | -57.9254 | -4.1565 | -58.4244 | 64.6957 | 64.5996 | -58.374 | -58.4427 | -0.059509 | -0.13733 | 0.09613 | 122.8775 | -0.15106 | -0.013733 | -0.09613 | -0.17853 | -0.24719 | 0.054932 | 0.27008 | -0.22888 | 0.018311 | -0.041199 | 122.9324 | 122.7402 | 61.4868 | -122.9736 | 122.8912 | 122.7951 | 54.039 | -123.0835
1900.0156 | 123.1293 | -58.2001 | 64.65 | 0.19821 | 0.012576 | 0.069746 | 0.070303 | 0.12886 | 0.0033411 | -0.0034457 | 0.25162 | -0.0084852 | 0.063837 | 0.059321 | 0.0052764 | -0.01176 | 64.5905 | 64.6957 | 3.2455 | -58.3374 | 64.7232 | -58.2413 | -58.3511 | -57.8522 | -4.1336 | -58.3969 | 64.7095 | 64.5813 | -58.374 | -58.4106 | -0.041199 | -0.15106 | 0.073243 | 122.8958 | -0.13733 | 0.013733 | -0.059509 | -0.17395 | -0.21057 | 0.05951 | 0.3479 | -0.19684 | 0.013733 | -0.068664 | 122.9233 | 122.7905 | 61.4456 | -123.0011 | 122.9095 | 122.7814 | 54.0665 | -123.0606
1901.0156 | 123.056 | -58.1314 | 64.7049 | -0.19852 | 0.0078763 | 0.06761 | 0.069663 | 0.12672 | -0.0032813 | -0.0019505 | -0.10696 | -0.009126 | 0.059564 | 0.058039 | 0.0037812 | -0.01176 | 64.6591 | 64.8285 | 3.1357 | -58.2413 | 64.8193 | -58.1955 | -58.2825 | -57.811 | -4.1245 | -58.342 | 64.7736 | 64.6637 | -58.3466 | -58.3603 | -0.064087 | -0.15106 | 0.11444 | 122.9599 | -0.10986 | 0.041199 | -0.045776 | -0.21515 | -0.22888 | 0.068665 | 0.32043 | -0.21057 | 0.018311 | -0.041199 | 122.9507 | 122.7905 | 61.2671 | -122.9874 | 122.905 | 122.7951 | 54.007 | -123.0652
1902.0156 | 122.9828 | -58.223 | 64.7049 | 0.076141 | 0.01514 | 0.069959 | 0.069449 | 0.12971 | 0.0035547 | -0.0036595 | 0.20584 | -0.0061352 | 0.06341 | 0.059962 | 0.0074126 | -0.010265 | 64.5584 | 64.6408 | 3.1998 | -58.3557 | 64.7736 | -58.2642 | -58.3374 | -57.9346 | -4.1931 | -58.5205 | 64.7827 | 64.6637 | -58.4198 | -58.461 | -0.041199 | -0.11444 | 0.068665 | 122.8638 | -0.13275 | -0.018311 | -0.14648 | -0.19684 | -0.23804 | 0.07782 | 0.28839 | -0.29755 | -0.059509 | -0.041199 | 122.9965 | 122.7814 | 61.4227 | -123.0423 | 123.0057 | 122.8867 | 54.0298 | -123.1659
1903.0156 | 123.0972 | -58.1909 | 64.6133 | 0.19821 | 0.0097989 | 0.069105 | 0.06774 | 0.12736 | -0.0017859 | -0.0053683 | 0.22873 | -0.0084852 | 0.061701 | 0.057185 | 0.0067718 | -0.0085556 | 64.563 | 64.7461 | 3.4973 | -58.3099 | 64.7049 | -58.2779 | -58.3237 | -57.8384 | -4.0146 | -58.3786 | 64.6729 | 64.595 | -58.3878 | -58.4427 | -0.086975 | -0.13275 | 0.091553 | 122.937 | -0.11902 | 0.013732 | -0.050354 | -0.19684 | -0.25177 | 0.05951 | 0.35248 | -0.18768 | 0.064087 | -0.01831 | 122.8958 | 122.7539 | 61.6882 | -122.937 | 122.8638 | 122.786 | 54.1763 | -123.056
1904.0156 | 123.0057 | -58.2504 | 64.6545 | 0.34317 | 0.016421 | 0.074018 | 0.073721 | 0.13099 | 0.0018457 | -0.0066501 | 0.20584 | -0.0061352 | 0.065546 | 0.059748 | 0.0048492 | -0.011546 | 64.5996 | 64.5447 | 3.4149 | -58.3786 | 64.7827 | -58.2916 | -58.3969 | -57.9346 | -4.2892 | -58.5022 | 64.7141 | 64.6545 | -58.4473 | -58.4839 | -0.041199 | -0.14648 | 0.12817 | 122.7951 | -0.12817 | 0.018311 | -0.054932 | -0.19684 | -0.23346 | 0.059509 | 0.31586 | -0.25177 | -0.01831 | 0 | 123.0331 | 122.85 | 61.6653 | -123.0515 | 122.9645 | 122.905 | 53.9612 | -123.1384
1905.0156 | 123.0835 | -58.1223 | 64.7141 | -0.053558 | 0.0080899 | -0.035998 | 0.069663 | 0.13014 | -0.0032813 | -0.0051547 | -0.00015237 | -0.0078442 | 0.059564 | 0.056971 | 0.0035674 | -0.0077012 | 64.6317 | 64.8056 | 3.4012 | -58.2596 | 64.7919 | -58.1955 | -58.2962 | -57.7881 | -4.2068 | -58.2779 | 64.7507 | 64.6774 | -58.3145 | -58.3466 | -0.073243 | -0.17395 | 0.07782 | 122.9279 | -0.13733 | 0.036621 | -0.082397 | -0.19226 | -0.22431 | 0.036621 | 0.33417 | -0.15564 | 0.068665 | -0.036621 | 122.9141 | 122.7539 | 61.5234 | -123.0103 | 122.8729 | 122.7997 | 53.9154 | -123.0606
1906.0156 | 123.0698 | -58.1726 | 64.7186 | 0.13718 | 0.01514 | 0.068678 | 0.072012 | 0.13035 | 0.0039819 | -0.0043003 | 0.10666 | -0.005708 | 0.064905 | 0.058253 | 0.004422 | -0.011974 | 64.5447 | 64.6225 | 3.1174 | -58.3557 | 64.8056 | -58.2458 | -58.3145 | -57.8705 | -4.422 | -58.4564 | 64.7644 | 64.6454 | -58.4061 | -58.4427 | -0.073243 | -0.14191 | 0.086975 | 122.7951 | -0.18311 | -0.041199 | -0.17395 | -0.23346 | -0.27008 | 0.045776 | 0.30212 | -0.28381 | -0.013733 | -0.073242 | 122.9782 | 122.7173 | 61.29 | -123.0331 | 122.937 | 122.818 | 53.7506 | -123.1613
1907.0156 | 123.0972 | -58.2458 | 64.6225 | 0.12192 | 0.010013 | 0.069532 | 0.068381 | 0.12715 | -0.0037085 | -0.0057957 | 0.23636 | -0.0089124 | 0.06106 | 0.057826 | 0.0022858 | -0.0087692 | 64.5401 | 64.682 | 3.0762 | -58.3694 | 64.6957 | -58.2596 | -58.3511 | -57.9117 | -4.1061 | -58.4381 | 64.6912 | 64.5859 | -58.4152 | -58.4656 | -0.013733 | -0.10529 | 0.073242 | 122.9279 | -0.1236 | -0.018311 | -0.082398 | -0.16937 | -0.21973 | 0.068664 | 0.33417 | -0.19226 | 0.027466 | -0.036622 | 122.9416 | 122.7859 | 61.322 | -122.9736 | 122.937 | 122.8317 | 54.1397 | -123.0881
1908.0156 | 123.0057 | -58.2504 | 64.6591 | 0.11429 | 0.01514 | 0.069319 | 0.07009 | 0.12993 | 0.0048363 | -0.0060093 | 0.41183 | -0.0072034 | 0.065332 | 0.057398 | 0.0082672 | -0.0096238 | 64.5035 | 64.5813 | 3.0167 | -58.4427 | 64.7324 | -58.3054 | -58.4106 | -57.9666 | -3.9871 | -58.5251 | 64.7186 | 64.6408 | -58.4473 | -58.4793 | -0.054932 | -0.16022 | 0.073242 | 122.8317 | -0.19226 | -0.032043 | -0.15564 | -0.19684 | -0.22888 | 0.059509 | 0.28381 | -0.27466 | -0.045776 | -0.018311 | 122.9828 | 122.7539 | 61.2671 | -123.0698 | 122.9691 | 122.8912 | 54.2633 | -123.1384
1909.0156 | 123.0743 | -58.2825 | 64.5264 | 0.13718 | 0.010653 | 0.069105 | 0.069235 | 0.12907 | -0.0045631 | -0.0053683 | 0.25162 | -0.0095532 | 0.061273 | 0.05633 | 0.0031402 | -0.0087692 | 64.4714 | 64.6408 | 3.2776 | -58.4244 | 64.595 | -58.342 | -58.4427 | -57.9529 | -3.7354 | -58.4747 | 64.5859 | 64.4989 | -58.4793 | -58.5342 | -0.059509 | -0.16022 | 0.068665 | 122.9233 | -0.14191 | 0.018311 | -0.054931 | -0.19684 | -0.25177 | 0.059509 | 0.32959 | -0.19226 | 0.05951 | -0.027466 | 122.8775 | 122.7539 | 61.5601 | -122.9691 | 122.8683 | 122.7814 | 54.5471 | -123.0606
1910.0156 | 122.9782 | -58.2825 | 64.5859 | -0.00015269 | 0.016208 | 0.066755 | 0.072012 | 0.12886 | 0.0027001 | -0.0040867 | -0.045929 | -0.0086988 | 0.06341 | 0.056544 | 0.0063446 | -0.013042 | 64.4989 | 64.5676 | 3.3051 | -58.4335 | 64.6957 | -58.3649 | -58.4198 | -57.9895 | -3.8406 | -58.5754 | 64.6591 | 64.5767 | -58.4747 | -58.5297 | -0.082397 | -0.13733 | 0.10986 | 122.85 | -0.15106 | -0.013733 | -0.086975 | -0.19226 | -0.24719 | 0.073243 | 0.29297 | -0.29297 | -0.045776 | -0.009155 | 122.9782 | 122.7814 | 61.5875 | -123.0057 | 122.9416 | 122.8592 | 54.4418 | -123.1155
1911.0156 | 123.1064 | -58.2413 | 64.6088 | 0.12955 | 0.014499 | 0.066755 | 0.071372 | 0.13035 | -0.0019995 | -0.0040867 | 0.25162 | -0.0086988 | 0.060846 | 0.058039 | 0.006131 | -0.010905 | 64.563 | 64.6683 | 3.5568 | -58.4381 | 64.6729 | -58.2962 | -58.3603 | -57.8934 | -3.8956 | -58.4427 | 64.6271 | 64.5447 | -58.4473 | -58.4747 | -0.054932 | -0.11902 | 0.064087 | 122.9095 | -0.19684 | -0.077819 | -0.045777 | -0.20599 | -0.23346 | 0.01831 | 0.3479 | -0.20142 | 0.032043 | -0.064087 | 122.9141 | 122.8043 | 61.7981 | -122.9691 | 122.8683 | 122.786 | 54.3457 | -123.0835
1912.0156 | 123.0057 | -58.2779 | 64.6271 | -0.015411 | 0.015567 | 0.068464 | 0.073508 | 0.13014 | 0.0027001 | -0.0019505 | 0.0074766 | -0.0078442 | 0.063196 | 0.058039 | 0.0067718 | -0.011974 | 64.4989 | 64.5493 | 3.6072 | -58.4152 | 64.7369 | -58.3328 | -58.3969 | -57.9803 | -4.0558 | -58.548 | 64.6912 | 64.6225 | -58.4564 | -58.5297 | -0.054932 | -0.11902 | 0.10986 | 122.8271 | -0.13733 | -0.01831 | -0.12817 | -0.17853 | -0.25177 | 0.064087 | 0.29755 | -0.27008 | -0.018311 | -0.004577 | 123.0148 | 122.7768 | 61.8851 | -123.024 | 122.9691 | 122.9004 | 54.2221 | -123.1567
1913.0156 | 123.111 | -58.255 | 64.5401 | 0.13718 | 0.014285 | 0.068891 | 0.067954 | 0.13078 | -0.00071785 | -0.0036595 | 0.27451 | -0.0078442 | 0.06341 | 0.056971 | 0.00549 | -0.0079148 | 64.4943 | 64.6088 | 3.7308 | -58.429 | 64.6683 | -58.3145 | -58.429 | -57.8842 | -3.9597 | -58.4518 | 64.6271 | 64.563 | -58.4518 | -58.493 | -0.059509 | -0.17395 | 0.12817 | 122.8638 | -0.17395 | 0 | -0.045776 | -0.19684 | -0.23804 | 0.086975 | 0.37079 | -0.19684 | 0.041199 | 0.022888 | 122.9233 | 122.7493 | 61.9858 | -122.9691 | 122.8821 | 122.818 | 54.2953 | -123.0331
1914.0156 | 123.0011 | -58.2687 | 64.6545 | -0.015411 | 0.015994 | 0.066114 | 0.070517 | 0.13078 | 0.0014185 | -0.0023777 | 0.068512 | -0.005708 | 0.06341 | 0.058039 | 0.0037812 | -0.0091966 | 64.5264 | 64.5859 | 3.8315 | -58.4198 | 64.7324 | -58.3099 | -58.3969 | -57.9346 | -4.0558 | -58.5205 | 64.7003 | 64.6271 | -58.4473 | -58.4976 | -0.041199 | -0.12817 | 0.07782 | 122.8546 | -0.15106 | -0.022888 | -0.12817 | -0.17853 | -0.22888 | 0.045776 | 0.33417 | -0.25177 | -0.022888 | -0.027466 | 123.0011 | 122.7951 | 62.1002 | -123.0515 | 122.9691 | 122.8958 | 54.213 | -123.1522
1915.0156 | 123.175 | -58.2001 | 64.5721 | 0.060882 | 0.014285 | 0.067396 | 0.06774 | 0.12758 | -0.0028541 | -0.0032321 | 0.29739 | -0.007417 | 0.060419 | 0.058039 | 0.0052764 | -0.006633 | 64.5767 | 64.7324 | 3.9413 | -58.3008 | 64.7369 | -58.2642 | -58.3466 | -57.8201 | -3.8086 | -58.3603 | 64.7141 | 64.595 | -58.3832 | -58.4381 | -0.064087 | -0.14648 | 0.16479 | 122.9324 | -0.10071 | 0.045777 | 0.004577 | -0.18311 | -0.23804 | 0.14191 | 0.37994 | -0.16022 | 0.077819 | 0.022888 | 122.937 | 122.7768 | 62.1414 | -122.9187 | 122.9141 | 122.7951 | 54.3915 | -123.0103
1916.0156 | 123.0057 | -58.2413 | 64.682 | 0.037994 | 0.014926 | 0.068037 | 0.072226 | 0.13057 | 0.0022729 | -0.0062229 | -0.0077819 | -0.007417 | 0.063837 | 0.058253 | 0.0050628 | -0.011119 | 64.5264 | 64.6225 | 3.9093 | -58.3878 | 64.7873 | -58.2733 | -58.3603 | -57.93 | -3.9001 | -58.5022 | 64.7736 | 64.6866 | -58.429 | -58.493 | -0.032043 | -0.11902 | 0.10528 | 122.8638 | -0.14648 | -0.027465 | -0.15564 | -0.18768 | -0.25177 | 0.091553 | 0.31128 | -0.26093 | -0.009155 | 0.004577 | 123.0286 | 122.7676 | 62.1506 | -123.0423 | 123.0148 | 122.9279 | 54.3411 | -123.175
1917.0156 | 123.0377 | -58.2367 | 64.6454 | 0.12192 | 0.013431 | 0.067823 | 0.068808 | 0.1295 | 0.00077755 | -0.0045139 | 0.20584 | -0.0069898 | 0.06106 | 0.059962 | 0.0046356 | -0.008342 | 64.5172 | 64.595 | 3.8086 | -58.3786 | 64.7324 | -58.3099 | -58.3694 | -57.9025 | -3.8635 | -58.4564 | 64.7003 | 64.65 | -58.4061 | -58.4702 | -0.073243 | -0.13275 | 0.086975 | 122.8317 | -0.14191 | -0.009155 | -0.12817 | -0.16937 | -0.23346 | 0.054931 | 0.33417 | -0.21973 | 0.013733 | 0.004577 | 122.9691 | 122.7539 | 62.0453 | -123.0148 | 122.937 | 122.8867 | 54.3732 | -123.1155
1918.0156 | 123.0286 | -58.1909 | 64.6866 | -1.114 | 0.016635 | 0.067396 | 0.072867 | 0.12886 | 0.0012047 | -0.0047275 | -0.015411 | -0.0084852 | 0.062342 | 0.057826 | 0.0059174 | -0.0072738 | 64.5905 | 64.7232 | 3.7857 | -58.3145 | 64.7827 | -58.2458 | -58.3282 | -57.8384 | -3.8498 | -58.4427 | 64.7736 | 64.6637 | -58.3923 | -58.4381 | -0.054932 | -0.13733 | 0.096131 | 122.9141 | -0.1236 | 0.013733 | -0.09613 | -0.20142 | -0.24719 | 0.086976 | 0.35248 | -0.25177 | -0.004578 | -0.022888 | 122.9736 | 122.7814 | 61.9766 | -123.0148 | 122.9645 | 122.8546 | 54.3411 | -123.1247
1919.0156 | 123.0881 | -58.2047 | 64.6225 | 0.11429 | 0.010653 | 0.071668 | 0.069022 | 0.12822 | -0.0045631 | -0.0036595 | 0.34317 | -0.0078442 | 0.06106 | 0.056971 | 0.0037812 | -0.0077012 | 64.5493 | 64.7232 | 3.9322 | -58.3328 | 64.6729 | -58.2687 | -58.342 | -57.811 | -3.7079 | -58.3649 | 64.6591 | 64.6042 | -58.4015 | -58.4564 | -0.064087 | -0.13733 | 0.050354 | 122.9279 | -0.12817 | 0.009155 | -0.073243 | -0.19684 | -0.25177 | 0.036621 | 0.39368 | -0.16022 | 0.091553 | -0.018311 | 122.8775 | 122.7539 | 62.1368 | -122.9645 | 122.8638 | 122.8088 | 54.4968 | -123.0789
1920.0156 | 122.9507 | -58.1955 | 64.7461 | 0.0074768 | 0.01578 | 0.067182 | 0.073294 | 0.13057 | 0.0016321 | -0.0038731 | 0.0914 | -0.0076306 | 0.063623 | 0.057398 | 0.0063446 | -0.010265 | 64.5584 | 64.6637 | 3.5934 | -58.3237 | 64.8468 | -58.2184 | -58.3099 | -57.8751 | -3.8589 | -58.4747 | 64.8056 | 64.6866 | -58.3923 | -58.4152 | -0.022888 | -0.11444 | 0.10071 | 122.8592 | -0.12817 | -0.013732 | -0.18768 | -0.19684 | -0.21973 | 0.059509 | 0.32043 | -0.27923 | -0.059509 | -0.05951 | 123.0423 | 122.7539 | 61.7889 | -123.056 | 123.0011 | 122.8821 | 54.3365 | -123.1613
1921.0156 | 123.1064 | -58.1406 | 64.6683 | -0.10696 | 0.0087307 | -0.035784 | 0.07009 | 0.12907 | -0.0064857 | -0.0072911 | 0.10666 | -0.0093396 | 0.060846 | 0.057612 | 0.0035674 | -0.0085556 | 64.5676 | 64.7507 | 3.5568 | -58.3008 | 64.7644 | -58.223 | -58.3328 | -57.8064 | -3.5019 | -58.3054 | 64.7141 | 64.6774 | -58.3282 | -58.4106 | -0.082397 | -0.19226 | 0.09613 | 122.8912 | -0.16022 | 0.032044 | -0.10071 | -0.18768 | -0.27008 | 0.045776 | 0.33417 | -0.1648 | 0.10529 | 0.009155 | 122.905 | 122.7081 | 61.6974 | -123.0011 | 122.8546 | 122.818 | 54.6387 | -123.0789
1922.0156 | 123.0652 | -58.1314 | 64.7415 | -0.19089 | 0.014712 | 0.06825 | 0.073935 | 0.1295 | 0.0035547 | -0.0049411 | -0.11459 | -0.0089124 | 0.064691 | 0.055476 | 0.0048492 | -0.011546 | 64.6729 | 64.7598 | 3.9001 | -58.2596 | 64.856 | -58.1772 | -58.2962 | -57.7789 | -3.5294 | -58.374 | 64.8239 | 64.7186 | -58.3466 | -58.3878 | -0.045776 | -0.1648 | 0.11444 | 122.8912 | -0.12817 | 0.036621 | -0.068664 | -0.21515 | -0.25635 | 0.082398 | 0.35248 | -0.24261 | 0.013733 | -0.022888 | 122.9874 | 122.8043 | 62.0316 | -123.0377 | 122.9553 | 122.85 | 54.6021 | -123.1293
1923.0156 | 122.9691 | -58.1726 | 64.7369 | 0.022736 | 0.014285 | 0.068891 | 0.073294 | 0.13014 | 0.0022729 | -0.0019505 | 0.13718 | -0.007417 | 0.064691 | 0.057826 | 0.0048492 | -0.008342 | 64.5447 | 64.6362 | 3.7628 | -58.3282 | 64.8285 | -58.2367 | -58.3191 | -57.8751 | -3.7994 | -58.4747 | 64.8102 | 64.7141 | -58.3694 | -58.4335 | -0.064087 | -0.14648 | 0.091553 | 122.8088 | -0.15564 | -0.009155 | -0.19226 | -0.19684 | -0.26093 | 0.073243 | 0.29755 | -0.30212 | -0.041198 | -0.022888 | 123.0011 | 122.7173 | 61.9354 | -123.056 | 122.9828 | 122.8867 | 54.3732 | -123.1705
1924.0156 | 123.0331 | -58.1818 | 64.7278 | 0.037994 | 0.014071 | 0.067396 | 0.072653 | 0.13099 | 0.0014185 | -0.0036595 | -0.023041 | -0.0061352 | 0.063196 | 0.060176 | 0.0033538 | -0.010051 | 64.5767 | 64.6591 | 4.129 | -58.3237 | 64.8056 | -58.2184 | -58.3145 | -57.8796 | -3.7811 | -58.461 | 64.7781 | 64.7369 | -58.3511 | -58.4152 | -0.036621 | -0.13275 | 0.07782 | 122.8409 | -0.14191 | -0.009155 | -0.15106 | -0.16937 | -0.23346 | 0.050354 | 0.30212 | -0.27924 | -0.045777 | 0.009155 | 122.9874 | 122.7585 | 62.3108 | -123.0423 | 122.9599 | 122.9187 | 54.4006 | -123.143
1925.0156 | 123.0835 | -58.2001 | 64.6317 | 0.17532 | 0.013217 | 0.069532 | 0.070303 | 0.13057 | -0.00050425 | -0.0017369 | 0.16769 | -0.006349 | 0.064478 | 0.058039 | 0.0037812 | -0.010051 | 64.5584 | 64.6729 | 4.1748 | -58.3466 | 64.7507 | -58.2733 | -58.3603 | -57.8384 | -3.6667 | -58.4015 | 64.6866 | 64.6362 | -58.3969 | -58.4198 | -0.073242 | -0.16022 | 0.11902 | 122.8729 | -0.14648 | 0.013733 | -0.073242 | -0.19684 | -0.21973 | 0.054931 | 0.36163 | -0.20142 | 0.018311 | 0.004577 | 122.9507 | 122.7585 | 62.3749 | -122.9919 | 122.8867 | 122.8363 | 54.5334 | -123.0515
1926.0156 | 123.0286 | -58.1314 | 64.7324 | 0.44235 | 0.014712 | 0.068464 | 0.071158 | 0.12715 | 0.00056395 | -0.0034457 | 0.17532 | -0.0072034 | 0.063196 | 0.057612 | 0.0033538 | -0.010051 | 64.5721 | 64.6729 | 4.3213 | -58.3054 | 64.8468 | -58.2138 | -58.2779 | -57.811 | -3.8773 | -58.4061 | 64.801 | 64.7278 | -58.3328 | -58.3786 | -0.082397 | -0.14648 | 0.11444 | 122.8043 | -0.17395 | -0.027466 | -0.16022 | -0.20142 | -0.24719 | 0.068664 | 0.32043 | -0.27466 | -0.027466 | -0.004578 | 122.9782 | 122.7036 | 62.4527 | -123.0103 | 122.9324 | 122.8592 | 54.2542 | -123.111
1927.0156 | 123.0011 | -58.2367 | 64.6591 | 0.16006 | 0.014499 | 0.068037 | 0.071585 | 0.13035 | 0.0027001 | -0.0060093 | 0.14481 | -0.0054944 | 0.064264 | 0.060816 | 0.0050628 | -0.0091966 | 64.476 | 64.5538 | 4.2068 | -58.4335 | 64.7552 | -58.3054 | -58.3969 | -57.9575 | -3.8727 | -58.5434 | 64.6957 | 64.65 | -58.4427 | -58.4976 | -0.068665 | -0.16022 | 0.09613 | 122.7905 | -0.19684 | -0.036621 | -0.18311 | -0.20599 | -0.26093 | 0.036621 | 0.27924 | -0.3067 | -0.045776 | -0.009156 | 122.9919 | 122.7127 | 62.4435 | -123.056 | 122.9324 | 122.8867 | 54.364 | -123.1567
1928.0156 | 123.0103 | -58.1726 | 64.7049 | -0.03067 | 0.016421 | 0.067182 | 0.070517 | 0.13249 | 0.0018457 | -0.0066501 | 0.030365 | -0.0078442 | 0.063196 | 0.060176 | 0.0057038 | -0.010265 | 64.5996 | 64.7003 | 4.3167 | -58.2275 | 64.7919 | -58.2596 | -58.2962 | -57.8064 | -3.6896 | -58.4244 | 64.7919 | 64.7324 | -58.3511 | -58.3969 | -0.086976 | -0.1236 | 0.086975 | 122.8729 | -0.054932 | 0.068665 | -0.10529 | -0.17853 | -0.22431 | 0.086975 | 0.36621 | -0.25177 | -0.027465 | 0.027466 | 122.9645 | 122.7722 | 62.4893 | -123.0011 | 122.9645 | 122.905 | 54.483 | -123.1018
1929.0156 | 123.056 | -58.2367 | 64.6637 | 0.2211 | 0.013217 | 0.066114 | 0.072012 | 0.12715 | -0.00050425 | -0.0030185 | 0.24399 | -0.006349 | 0.064264 | 0.059535 | 0.004422 | -0.0089828 | 64.5035 | 64.5721 | 4.2068 | -58.4015 | 64.7324 | -58.3145 | -58.374 | -57.9025 | -3.6621 | -58.4793 | 64.7141 | 64.6362 | -58.4518 | -58.4702 | -0.07782 | -0.13733 | 0.068665 | 122.8088 | -0.16479 | -0.027466 | -0.16022 | -0.21515 | -0.23346 | 0.050354 | 0.33417 | -0.24262 | -0.009155 | -0.027466 | 122.9691 | 122.7402 | 62.4435 | -123.0377 | 122.9507 | 122.8729 | 54.5746 | -123.1338
1930.0156 | 123.0469 | -58.1223 | 64.7644 | -0.168 | 0.012149 | 0.071455 | 0.073508 | 0.12886 | -0.0013587 | -0.0049411 | -0.16037 | -0.0084852 | 0.062982 | 0.058253 | 0.0031402 | -0.0098374 | 64.5905 | 64.7049 | 4.1565 | -58.2779 | 64.8605 | -58.1818 | -58.3099 | -57.811 | -3.4058 | -58.3923 | 64.8285 | 64.7781 | -58.3511 | -58.3786 | -0.05951 | -0.18768 | 0.096131 | 122.8271 | -0.15564 | 0.032044 | -0.17395 | -0.22888 | -0.25635 | 0.064087 | 0.31128 | -0.27008 | -0.013733 | 0.013733 | 122.9828 | 122.7127 | 62.2787 | -123.0743 | 122.9507 | 122.9004 | 54.7165 | -123.143
1931.0156 | 123.0606 | -58.2047 | 64.7003 | 0.14481 | 0.014071 | 0.069959 | 0.070303 | 0.12864 | -0.0019995 | -0.0051547 | 0.25925 | -0.006349 | 0.065119 | 0.059321 | 0.00549 | -0.010051 | 64.5355 | 64.6591 | 4.6097 | -58.3511 | 64.7919 | -58.2458 | -58.3557 | -57.7972 | -3.3371 | -58.3969 | 64.7644 | 64.6591 | -58.374 | -58.4244 | -0.041199 | -0.15106 | 0.091553 | 122.8638 | -0.14648 | 0.004578 | -0.16479 | -0.16937 | -0.21973 | 0.064087 | 0.40741 | -0.19226 | 0.027465 | -0.041198 | 122.9965 | 122.7402 | 62.8143 | -123.056 | 122.9691 | 122.8638 | 54.8676 | -123.1247
1932.0156 | 123.0286 | -58.1818 | 64.7552 | -0.076447 | 0.015567 | 0.068891 | 0.073721 | 0.12864 | 0.0024865 | -0.0049411 | 0.045624 | -0.0037854 | 0.065973 | 0.056544 | 0.00549 | -0.010265 | 64.6454 | 64.7049 | 4.8386 | -58.3145 | 64.8285 | -58.2275 | -58.3099 | -57.7881 | -3.3646 | -58.4198 | 64.7736 | 64.7415 | -58.3466 | -58.4244 | -0.045776 | -0.12817 | 0.073242 | 122.8867 | -0.13275 | -0.004577 | -0.10986 | -0.1648 | -0.24261 | 0.018311 | 0.39368 | -0.23804 | 0.004577 | -0.013733 | 123.0103 | 122.8271 | 63.0203 | -123.0652 | 122.9553 | 122.9233 | 54.8172 | -123.1796
1933.0156 | 123.0057 | -58.1635 | 64.7278 | 0.28976 | 0.016421 | 0.068464 | 0.071372 | 0.12993 | -0.0028541 | -0.0043003 | 0.20584 | -0.0072034 | 0.063837 | 0.057826 | 0.0039948 | -0.008342 | 64.5813 | 64.6729 | 4.8111 | -58.342 | 64.8422 | -58.2047 | -58.287 | -57.7927 | -3.6026 | -58.429 | 64.7964 | 64.7186 | -58.3466 | -58.3923 | -0.041199 | -0.1236 | 0.11444 | 122.8363 | -0.17853 | -0.054932 | -0.14648 | -0.18311 | -0.22888 | 0.068665 | 0.37079 | -0.2655 | -0.036621 | -0.009155 | 123.0057 | 122.7448 | 62.9745 | -123.0148 | 122.9599 | 122.8821 | 54.5609 | -123.1201
1934.0156 | 123.0469 | -58.168 | 64.6957 | -0.18326 | 0.013644 | 0.068037 | 0.071372 | 0.12993 | 0.0016321 | -0.0036595 | -0.053558 | -0.0086988 | 0.06106 | 0.058039 | 0.0050628 | -0.0087692 | 64.5996 | 64.7324 | 4.8706 | -58.2916 | 64.8193 | -58.2184 | -58.3328 | -57.8064 | -3.4424 | -58.3969 | 64.7736 | 64.7461 | -58.3466 | -58.4335 | -0.050354 | -0.16479 | 0.1236 | 122.9004 | -0.1236 | 0.041199 | -0.096131 | -0.17853 | -0.2655 | 0.07782 | 0.36163 | -0.22888 | 0.036621 | 0.050354 | 122.9874 | 122.7676 | 63.0386 | -123.0286 | 122.9416 | 122.9141 | 54.7256 | -123.1293
1935.0156 | 122.9782 | -58.1772 | 64.7598 | 0.060882 | 0.016849 | 0.06825 | 0.073508 | 0.13185 | 0.0020593 | -0.0055821 | 0.022736 | -0.0076306 | 0.064264 | 0.059535 | 0.0052764 | -0.0087692 | 64.6042 | 64.7003 | 4.6692 | -58.3145 | 64.8376 | -58.2047 | -58.2596 | -57.8201 | -3.2776 | -58.4381 | 64.8056 | 64.7598 | -58.3466 | -58.3969 | -0.027466 | -0.082398 | 0.077819 | 122.8775 | -0.13733 | -0.054931 | -0.15564 | -0.16937 | -0.21973 | 0.045776 | 0.35706 | -0.26093 | -0.041198 | 0 | 123.0148 | 122.7814 | 62.8464 | -123.0194 | 122.9828 | 122.937 | 54.8996 | -123.1567
1936.0156 | 123.0011 | -58.1039 | 64.801 | 0.022736 | 0.017276 | 0.066541 | 0.07244 | 0.12886 | 0.0037683 | -0.0053683 | -0.0077819 | -0.0082716 | 0.062982 | 0.058894 | 0.006131 | -0.0072738 | 64.6866 | 64.7919 | 4.8477 | -58.223 | 64.888 | -58.168 | -58.2504 | -57.7286 | -3.1311 | -58.3511 | 64.8468 | 64.7919 | -58.3008 | -58.3328 | -0.064087 | -0.14648 | 0.086975 | 122.8958 | -0.11902 | 0.027466 | -0.11444 | -0.19684 | -0.22888 | 0.045777 | 0.37537 | -0.24719 | -0.01831 | -0.009155 | 122.9919 | 122.7905 | 62.9517 | -123.0515 | 122.9507 | 122.8958 | 54.9728 | -123.1338
1937.0156 | 123.0194 | -58.1818 | 64.7095 | 0.068512 | 0.015994 | 0.066969 | 0.071585 | 0.12822 | -0.00050425 | -0.0075047 | 0.022736 | -0.0052808 | 0.064478 | 0.056971 | 0.0039948 | -0.0072738 | 64.5767 | 64.6774 | 5.0034 | -58.3374 | 64.7873 | -58.2413 | -58.3282 | -57.8613 | -3.186 | -58.4518 | 64.7736 | 64.7003 | -58.3786 | -58.429 | -0.059509 | -0.14648 | 0.077819 | 122.8592 | -0.15564 | -0.009155 | -0.13275 | -0.19684 | -0.24719 | 0.064087 | 0.32043 | -0.27008 | -0.022888 | -0.009156 | 122.9691 | 122.7585 | 63.1851 | -123.0377 | 122.9553 | 122.8821 | 54.9957 | -123.1384
1938.0156 | 123.0423 | -58.2321 | 64.6912 | -0.20615 | 0.011294 | 0.068678 | 0.07009 | 0.12779 | -0.00050425 | -0.0072911 | -0.091705 | -0.006349 | 0.06341 | 0.058253 | 0.0052764 | -0.0098374 | 64.4531 | 64.595 | 5.0995 | -58.4015 | 64.7095 | -58.3282 | -58.4244 | -57.93 | -3.067 | -58.493 | 64.7232 | 64.65 | -58.4656 | -58.4885 | -0.09613 | -0.19226 | 0.018311 | 122.8271 | -0.16937 | 0.022888 | -0.23804 | -0.23346 | -0.25635 | 0.032044 | 0.30212 | -0.26093 | -0.004578 | -0.041199 | 122.9416 | 122.6852 | 63.3316 | -123.1155 | 122.9553 | 122.8821 | 55.1651 | -123.1796
1939.0156 | 122.9782 | -58.4564 | 64.4577 | 0.030365 | 0.017489 | 0.068464 | 0.073294 | 0.12843 | 0.0022729 | -0.0053683 | 0.060883 | -0.0078442 | 0.067896 | 0.059748 | 0.0046356 | -0.0077012 | 64.2975 | 64.389 | 5.0674 | -58.5983 | 64.5355 | -58.4885 | -58.5846 | -58.1314 | -3.3142 | -58.7082 | 64.5401 | 64.444 | -58.6487 | -58.6945 | -0.032043 | -0.12817 | 0.077819 | 122.8455 | -0.14191 | -0.013733 | -0.16022 | -0.19226 | -0.23804 | 0.082397 | 0.32501 | -0.25177 | -0.013733 | -0.013733 | 122.9919 | 122.7539 | 63.5239 | -123.0423 | 122.9965 | 122.9004 | 55.1422 | -123.1522
1940.0156 | 122.9782 | -58.3282 | 64.5905 | -0.099335 | 0.015567 | 0.069959 | 0.072012 | 0.128 | 0.00035035 | -0.0049411 | 0.015106 | -0.00464 | 0.064051 | 0.058253 | 0.002713 | -0.0085556 | 64.4531 | 64.5813 | 5.1041 | -58.4564 | 64.6454 | -58.3923 | -58.4747 | -57.9483 | -3.273 | -58.5526 | 64.6133 | 64.5584 | -58.5159 | -58.5617 | -0.064087 | -0.14648 | 0.054932 | 122.9095 | -0.12817 | 0.01831 | -0.13733 | -0.18768 | -0.23346 | 0.022888 | 0.37994 | -0.2243 | 0.009156 | -0.032043 | 122.9736 | 122.7814 | 63.4323 | -123.0652 | 122.9416 | 122.8867 | 55.0552 | -123.1522
1941.0156 | 123.0148 | -58.3557 | 64.5401 | 0.42709 | 0.014926 | 0.070173 | 0.071372 | 0.1295 | -7.6852e-05 | -0.0043003 | 0.2211 | -0.008058 | 0.064478 | 0.057612 | 0.0037812 | -0.0072738 | 64.3845 | 64.4897 | 5.4062 | -58.5251 | 64.6317 | -58.4061 | -58.4976 | -57.9849 | -2.9434 | -58.5892 | 64.6042 | 64.5355 | -58.5388 | -58.5938 | -0.050354 | -0.14191 | 0.091553 | 122.8455 | -0.16937 | -0.027465 | -0.15564 | -0.1831 | -0.23804 | 0.064087 | 0.37079 | -0.23346 | 0.004578 | -0.004578 | 122.9874 | 122.7402 | 63.7619 | -123.0377 | 122.9599 | 122.8912 | 55.4123 | -123.1338
1942.0156 | 123.024 | -58.3099 | 64.6042 | -0.17563 | 0.01279 | 0.068464 | 0.070944 | 0.12971 | -0.0028541 | -0.0047275 | -0.16037 | -0.009126 | 0.064691 | 0.057612 | 0.0020722 | -0.0094102 | 64.4211 | 64.5264 | 5.5115 | -58.4702 | 64.6957 | -58.3557 | -58.4473 | -57.9666 | -3.0396 | -58.548 | 64.6637 | 64.5996 | -58.5068 | -58.5159 | -0.045776 | -0.13733 | 0.091553 | 122.8363 | -0.16022 | -0.022888 | -0.1831 | -0.19684 | -0.20599 | 0.059509 | 0.34332 | -0.23804 | -0.032044 | -0.004578 | 123.0057 | 122.731 | 63.8214 | -123.0515 | 122.9736 | 122.9095 | 55.2704 | -123.1201
1943.0156 | 123.0469 | -58.2687 | 64.6225 | -0.023041 | 0.016635 | 0.069105 | 0.072653 | 0.1295 | -7.6852e-05 | -0.0066501 | -0.015411 | -0.006349 | 0.063837 | 0.056758 | 0.00549 | -0.010051 | 64.4943 | 64.6133 | 5.4062 | -58.4244 | 64.6866 | -58.3511 | -58.4335 | -57.93 | -2.7786 | -58.5205 | 64.6545 | 64.5905 | -58.493 | -58.5526 | -0.082397 | -0.16479 | 0.064086 | 122.8821 | -0.15564 | 0.009156 | -0.12817 | -0.2243 | -0.28381 | 0.032043 | 0.33874 | -0.25177 | 0.032043 | -0.032044 | 122.9553 | 122.7631 | 63.6749 | -123.056 | 122.9233 | 122.8592 | 55.4901 | -123.175
1944.0156 | 123.0057 | -58.2779 | 64.6225 | -0.39688 | 0.011294 | 0.069959 | 0.072012 | 0.12928 | -0.0056311 | -0.0038731 | -0.076446 | -0.006349 | 0.064478 | 0.059962 | 0.0016448 | -0.010478 | 64.4119 | 64.5676 | 5.3238 | -58.4473 | 64.7095 | -58.3511 | -58.4427 | -57.9712 | -2.6962 | -58.5251 | 64.6912 | 64.6088 | -58.461 | -58.5114 | -0.073242 | -0.16479 | 0.086975 | 122.8455 | -0.16937 | -0.004578 | -0.21057 | -0.18311 | -0.23346 | 0.068664 | 0.3067 | -0.24719 | -0.013732 | -0.013733 | 122.9874 | 122.6898 | 63.6017 | -123.0652 | 122.9691 | 122.8867 | 55.5817 | -123.1339
1945.0156 | 122.9965 | -58.3374 | 64.595 | -0.015411 | 0.014926 | 0.069746 | 0.072653 | 0.13057 | 0.0024865 | -0.0028049 | 0.022736 | -0.006349 | 0.066187 | 0.059535 | 0.0033538 | -0.010265 | 64.4302 | 64.5493 | 5.0629 | -58.4747 | 64.6408 | -58.3832 | -58.4747 | -57.9941 | -2.8107 | -58.5938 | 64.6271 | 64.5584 | -58.5297 | -58.5663 | -0.045777 | -0.13733 | 0.045776 | 122.8867 | -0.13733 | 0 | -0.16479 | -0.19226 | -0.22888 | 0.032043 | 0.34332 | -0.25635 | -0.027466 | -0.036621 | 122.9782 | 122.7676 | 63.4003 | -123.0698 | 122.9645 | 122.8958 | 55.5267 | -123.1613
1946.0156 | 123.0377 | -58.3237 | 64.5905 | -0.091705 | 0.013431 | 0.066541 | 0.070517 | 0.12971 | 0.0018457 | -0.0055821 | -0.13748 | -0.0076306 | 0.061701 | 0.057826 | 0.0052764 | -0.010265 | 64.3158 | 64.5767 | 5.2139 | -58.4518 | 64.6362 | -58.4061 | -58.4839 | -57.9437 | -2.6871 | -58.5571 | 64.6088 | 64.5905 | -58.5159 | -58.5388 | -0.082398 | -0.16022 | 0.045776 | 122.9004 | -0.12817 | 0.032044 | -0.27466 | -0.19226 | -0.21515 | 0.018311 | 0.37994 | -0.23346 | -0.018311 | 0 | 122.9599 | 122.6395 | 63.5376 | -123.0743 | 122.9324 | 122.9141 | 55.6366 | -123.1293
1947.0156 | 123.0698 | -58.3969 | 64.4806 | 0.14481 | 0.014071 | 0.068464 | 0.069235 | 0.12864 | 0.00013675 | -0.0062229 | 0.28214 | -0.0069898 | 0.065973 | 0.057398 | 0.004422 | -0.0081284 | 64.3112 | 64.4348 | 5.072 | -58.5846 | 64.5493 | -58.4702 | -58.5571 | -58.0353 | -2.8244 | -58.6395 | 64.5126 | 64.4577 | -58.6212 | -58.6395 | -0.073242 | -0.16022 | 0.068664 | 122.8317 | -0.18768 | -0.027466 | -0.16937 | -0.2243 | -0.24261 | 0.032043 | 0.36163 | -0.24261 | 0 | -0.022888 | 122.9462 | 122.7081 | 63.4689 | -123.0377 | 122.9095 | 122.8546 | 55.5725 | -123.1201
1948.0156 | 123.0469 | -58.3649 | 64.5264 | -0.15274 | 0.011294 | 0.068891 | 0.073508 | 0.12971 | -7.6852e-05 | -0.0049411 | -0.11459 | -0.0089124 | 0.062982 | 0.058894 | 0.0035674 | -0.0094102 | 64.3936 | 64.4989 | 5.0079 | -58.4885 | 64.6362 | -58.429 | -58.493 | -57.9758 | -2.7328 | -58.58 | 64.5905 | 64.5538 | -58.5342 | -58.6075 | -0.064087 | -0.12817 | 0.10986 | 122.8638 | -0.1236 | 0.004578 | -0.13275 | -0.16937 | -0.24262 | 0.064087 | 0.3891 | -0.21515 | 0.027466 | 0.027466 | 123.0011 | 122.7585 | 63.3728 | -123.0194 | 122.9553 | 122.9187 | 55.632 | -123.1338
1949.0156 | 123.0103 | -58.3008 | 64.5813 | -0.00015269 | 0.01514 | 0.068037 | 0.069876 | 0.12864 | -0.00029045 | -0.0062229 | 0.14481 | -0.0082716 | 0.064905 | 0.058894 | 0.0039948 | -0.0087692 | 64.3845 | 64.4989 | 4.129 | -58.4885 | 64.6912 | -58.3786 | -58.4518 | -57.9575 | -2.6871 | -58.5983 | 64.6362 | 64.5813 | -58.4976 | -58.5297 | -0.07782 | -0.15106 | 0.10986 | 122.7997 | -0.18768 | -0.036621 | -0.19684 | -0.19684 | -0.22888 | 0.054931 | 0.34332 | -0.29755 | -0.068665 | 0 | 122.9919 | 122.6852 | 62.4298 | -123.0331 | 122.937 | 122.8821 | 55.6137 | -123.111
1950.0156 | 123.0652 | -58.3099 | 64.5905 | -0.168 | 0.017917 | 0.069105 | 0.071585 | 0.13356 | -0.00071785 | -0.0038731 | -0.11459 | -0.0061352 | 0.063837 | 0.058894 | 0.0046356 | -0.0094102 | 64.4577 | 64.6042 | 4.4312 | -58.429 | 64.7049 | -58.3557 | -58.4564 | -57.8842 | -2.6917 | -58.5434 | 64.6545 | 64.5996 | -58.4702 | -58.5297 | -0.045776 | -0.14648 | 0.11444 | 122.9141 | -0.11902 | 0.027466 | -0.13275 | -0.16022 | -0.21973 | 0.064087 | 0.42572 | -0.23346 | -0.013733 | 0.009155 | 123.0148 | 122.7676 | 62.7411 | -123.0469 | 122.9645 | 122.9095 | 55.6183 | -123.1201
1951.0156 | 123.0698 | -58.3054 | 64.5996 | -0.0383 | 0.017062 | 0.067182 | 0.071158 | 0.13121 | 0.00077755 | -0.0049411 | 0.030365 | -0.0078442 | 0.064051 | 0.058894 | 0.0048492 | -0.010051 | 64.444 | 64.5859 | 4.4449 | -58.4518 | 64.6729 | -58.374 | -58.4518 | -57.9025 | -2.8885 | -58.5526 | 64.6317 | 64.5859 | -58.493 | -58.5526 | -0.068664 | -0.14648 | 0.073243 | 122.8912 | -0.14648 | 0 | -0.15564 | -0.18768 | -0.24719 | 0.032044 | 0.40283 | -0.24719 | 0 | -0.013733 | 122.9782 | 122.7493 | 62.7502 | -123.0515 | 122.937 | 122.8912 | 55.4169 | -123.1522
1952.0156 | 123.0515 | -58.3145 | 64.5859 | -0.24429 | 0.013003 | 0.069532 | 0.069022 | 0.13057 | -0.0037085 | -0.0075047 | -0.15274 | -0.007417 | 0.063196 | 0.059321 | 0.0037812 | -0.0087692 | 64.6271 | 64.3341 | 4.2709 | -58.5342 | 64.65 | -58.3694 | -58.4793 | -57.9346 | -2.8336 | -58.5388 | 64.6729 | 64.6271 | -58.5068 | -58.5297 | -0.054932 | -0.16479 | 0.064087 | 122.6486 | -0.21973 | -0.054932 | 0.041199 | -0.19226 | -0.21515 | 0.086976 | 0.37994 | -0.2243 | -0.009155 | 0.041199 | 122.9645 | 122.9416 | 62.5854 | -123.0652 | 122.9874 | 122.9416 | 55.481 | -123.1155
1953.0156 | 123.0286 | -58.3237 | 64.5996 | -0.0077822 | 0.016635 | 0.069105 | 0.069449 | 0.13057 | -0.00050425 | -0.0028049 | 0.068512 | -0.009126 | 0.065332 | 0.058253 | 0.0057038 | -0.011119 | 64.444 | 64.5859 | 4.3442 | -58.461 | 64.682 | -58.3466 | -58.4335 | -57.93 | -2.7832 | -58.5617 | 64.6408 | 64.5905 | -58.5114 | -58.5388 | -0.022889 | -0.10986 | 0.082398 | 122.9095 | -0.13733 | -0.027466 | -0.15564 | -0.18768 | -0.21515 | 0.041199 | 0.39368 | -0.23804 | -0.022889 | -0.009155 | 123.0057 | 122.7676 | 62.6678 | -123.0331 | 122.9645 | 122.9141 | 55.5405 | -123.1384
1954.0156 | 122.9553 | -58.3099 | 64.6408 | -0.084076 | 0.0093717 | 0.071455 | 0.072226 | 0.12822 | -0.0034949 | -0.0062229 | -0.168 | -0.0084852 | 0.062555 | 0.056544 | 0.0024994 | -0.0091966 | 64.3753 | 64.563 | 4.8477 | -58.4976 | 64.6637 | -58.3832 | -58.4793 | -57.9575 | -2.6276 | -58.5571 | 64.682 | 64.5676 | -58.5159 | -58.5663 | -0.073242 | -0.16937 | 0.022888 | 122.8729 | -0.18768 | -0.018311 | -0.2655 | -0.20599 | -0.25635 | 0.041199 | 0.35248 | -0.24719 | 0.009155 | -0.073242 | 122.9736 | 122.6852 | 63.1577 | -123.1201 | 122.9919 | 122.8775 | 55.6824 | -123.2071
1955.0156 | 123.0057 | -58.4061 | 64.5172 | 0.037994 | 0.016635 | 0.066114 | 0.075217 | 0.12886 | 0.0022729 | -0.0055821 | 0.20584 | -0.0078442 | 0.064905 | 0.058253 | 0.0035674 | -0.010265 | 64.3204 | 64.4348 | 4.4403 | -58.5663 | 64.6317 | -58.4244 | -58.4976 | -58.0261 | -2.655 | -58.6441 | 64.5905 | 64.5309 | -58.5709 | -58.6304 | -0.01831 | -0.091553 | 0.11444 | 122.8409 | -0.16022 | -0.068664 | -0.19684 | -0.16479 | -0.2243 | 0.073242 | 0.37994 | -0.23804 | -0.013733 | 0.013733 | 123.0377 | 122.7264 | 62.8464 | -123.0148 | 122.9965 | 122.937 | 55.751 | -123.1476
1956.0156 | 123.056 | -58.3878 | 64.5355 | -0.21378 | 0.015353 | 0.06825 | 0.073294 | 0.12886 | 0.00077755 | -0.0036595 | -0.10696 | -0.0069898 | 0.06106 | 0.059321 | 0.0037812 | -0.010478 | 64.3845 | 64.5218 | 4.6097 | -58.5068 | 64.6179 | -58.4106 | -58.4793 | -57.9712 | -2.5177 | -58.6075 | 64.5905 | 64.5447 | -58.5434 | -58.6212 | -0.022889 | -0.091553 | 0.082398 | 122.9095 | -0.11902 | -0.027466 | -0.15106 | -0.15564 | -0.23346 | 0.054932 | 0.41657 | -0.21973 | 0.013733 | 0.009156 | 123.0057 | 122.7722 | 62.9974 | -123.0148 | 122.9782 | 122.9324 | 55.8701 | -123.1567
1957.0156 | 123.0652 | -58.3878 | 64.5081 | -0.17563 | 0.014499 | 0.067182 | 0.073081 | 0.12993 | 0.00035035 | -0.0038731 | -0.13748 | -0.0082716 | 0.062342 | 0.058894 | 0.0035674 | -0.01176 | 64.3387 | 64.476 | 4.422 | -58.5251 | 64.5996 | -58.4747 | -58.5434 | -58.0078 | -2.3026 | -58.6166 | 64.563 | 64.5172 | -58.5754 | -58.6121 | -0.086975 | -0.15564 | 0.091552 | 122.8638 | -0.13733 | 0.018311 | -0.16937 | -0.18768 | -0.2243 | 0.054931 | 0.37994 | -0.22888 | -0.004577 | 0.009155 | 122.9874 | 122.7264 | 62.8098 | -123.0515 | 122.9507 | 122.905 | 56.0852 | -123.1201
1958.0156 | 123.1064 | -58.3832 | 64.476 | -0.10696 | 0.0072355 | 0.068678 | 0.067954 | 0.13014 | -0.0054175 | -0.0038731 | -0.038299 | -0.010408 | 0.064478 | 0.058253 | 0.0024994 | -0.0089828 | 64.3387 | 64.5859 | 4.3259 | -58.5022 | 64.5355 | -58.4518 | -58.5434 | -57.9849 | -2.2202 | -58.548 | 64.5126 | 64.4531 | -58.6121 | -58.6441 | -0.068664 | -0.16022 | 0.059509 | 122.9691 | -0.11902 | 0.041199 | -0.13733 | -0.22888 | -0.26093 | 0.036621 | 0.39825 | -0.1648 | 0.09613 | -0.022888 | 122.9187 | 122.7219 | 62.709 | -123.0194 | 122.8958 | 122.8363 | 56.163 | -123.1201
1959.0156 | 123.0423 | -58.3603 | 64.5538 | -0.0077822 | 0.010867 | 0.069105 | 0.071158 | 0.1295 | -7.6852e-05 | -0.0036595 | -0.14511 | -0.0093396 | 0.062555 | 0.059748 | 0.0029266 | -0.012187 | 64.357 | 64.4943 | 3.891 | -58.5022 | 64.6362 | -58.4244 | -58.5159 | -57.9758 | -2.2659 | -58.5892 | 64.6088 | 64.5309 | -58.5846 | -58.6212 | -0.064086 | -0.15564 | 0.082397 | 122.8546 | -0.14191 | 0.013733 | -0.19684 | -0.2243 | -0.26093 | 0.054932 | 0.38452 | -0.22888 | 0.032044 | -0.022888 | 122.9965 | 122.7173 | 62.2513 | -123.0698 | 122.9691 | 122.8912 | 56.0944 | -123.175
1960.0156 | 123.1064 | -58.3191 | 64.5355 | -0.13748 | 0.0063809 | 0.070387 | 0.067954 | 0.12629 | -0.0058447 | -0.0064365 | -0.076446 | -0.0099806 | 0.062555 | 0.058253 | 0.0024994 | -0.0098374 | 64.4028 | 64.6408 | 3.978 | -58.4702 | 64.5859 | -58.3923 | -58.4702 | -57.9437 | -2.037 | -58.5205 | 64.5767 | 64.5081 | -58.5342 | -58.5709 | -0.073242 | -0.15106 | 0.050354 | 122.9599 | -0.15106 | 0 | -0.13275 | -0.21515 | -0.25177 | 0.041199 | 0.37537 | -0.20142 | 0.050354 | -0.027465 | 122.905 | 122.7219 | 62.2971 | -123.0057 | 122.8958 | 122.8271 | 56.282 | -123.1064
1961.0156 | 123.0515 | -58.3923 | 64.4989 | -0.084076 | 0.015567 | 0.067823 | 0.070517 | 0.1295 | 0.0024865 | -0.0055821 | -0.076446 | -0.008058 | 0.064691 | 0.058467 | 0.0080536 | -0.012828 | 64.3936 | 64.5309 | 4.1336 | -58.5159 | 64.595 | -58.461 | -58.5571 | -58.0902 | -1.8127 | -58.6349 | 64.5493 | 64.4943 | -58.5892 | -58.667 | -0.068665 | -0.1648 | 0.096131 | 122.9233 | -0.1236 | 0.041199 | -0.10529 | -0.19684 | -0.27466 | 0.050354 | 0.30212 | -0.24262 | 0.032043 | -0.004577 | 122.9874 | 122.7859 | 62.5259 | -123.056 | 122.9416 | 122.8867 | 56.5796 | -123.1659
1962.0156 | 123.1201 | -58.3786 | 64.4577 | -0.22141 | 0.0040311 | 0.069319 | 0.069235 | 0.13014 | -0.0060585 | -0.0089999 | -0.023041 | -0.0089124 | 0.063196 | 0.055476 | -0.0015594 | -0.0057786 | 64.4028 | 64.6362 | 4.303 | -58.4061 | 64.5355 | -58.4198 | -58.5114 | -58.1039 | -2.1423 | -58.4839 | 64.5218 | 64.4394 | -58.5709 | -58.6166 | -0.041199 | -0.13275 | 0.077819 | 123.0148 | -0.027466 | 0.10529 | -0.054932 | -0.19226 | -0.23804 | 0.064087 | 0.27466 | -0.10529 | 0.13275 | -0.018311 | 122.9141 | 122.7814 | 62.6816 | -122.9691 | 122.9004 | 122.818 | 56.2363 | -123.0743
1963.0312 | 123.1018 | -58.3557 | 64.476 | 0.099029 | 0.0053129 | 0.069319 | 0.069449 | 0.12736 | -0.0066993 | -0.0083591 | 0.16769 | -0.010621 | 0.061487 | 0.057826 | 0.0024994 | -0.0089828 | 64.3387 | 64.5447 | 4.3716 | -58.5297 | 64.5584 | -58.4244 | -58.5068 | -57.9437 | -2.1515 | -58.5434 | 64.5538 | 64.4623 | -58.5342 | -58.6166 | -0.068664 | -0.15106 | 0.082398 | 122.9004 | -0.17395 | -0.022888 | -0.13733 | -0.17853 | -0.26093 | 0.07782 | 0.41199 | -0.18768 | 0.073242 | -0.013733 | 122.9141 | 122.6944 | 62.7274 | -122.9828 | 122.9095 | 122.818 | 56.2042 | -123.0927
1964.0156 | 123.1384 | -58.3145 | 64.5126 | -0.091705 | 0.0068081 | 0.06761 | 0.072653 | 0.12758 | -0.0034949 | -0.0092137 | 0.0074766 | -0.009126 | 0.061914 | 0.05633 | 0.0020722 | -0.010265 | 64.4531 | 64.6317 | 4.3396 | -58.4564 | 64.6179 | -58.4015 | -58.429 | -57.8522 | -2.2522 | -58.4564 | 64.5813 | 64.5264 | -58.4793 | -58.5342 | -0.086975 | -0.11444 | 0.10529 | 122.9462 | -0.14191 | -0.027466 | -0.059509 | -0.16479 | -0.21973 | 0.068665 | 0.46234 | -0.14191 | 0.07782 | 0.013733 | 122.9324 | 122.7676 | 62.6541 | -122.9416 | 122.8958 | 122.8409 | 56.0623 | -123.0469
1965.0156 | 123.0652 | -58.2642 | 64.595 | -0.22903 | 0.0087307 | 0.067823 | 0.071585 | 0.13035 | 0.00013675 | -0.0072911 | -0.12222 | -0.0069898 | 0.062342 | 0.055903 | 0.0031402 | -0.011974 | 64.4806 | 64.6408 | 4.335 | -58.287 | 64.6317 | -58.3511 | -58.4152 | -57.8659 | -2.3895 | -58.5114 | 64.6408 | 64.5584 | -58.4427 | -58.5022 | -0.086975 | -0.15106 | 0.036621 | 122.905 | -0.022888 | 0.12817 | -0.11444 | -0.17853 | -0.23804 | 0.045776 | 0.39825 | -0.24719 | -0.009156 | -0.036621 | 122.8958 | 122.7448 | 62.5992 | -123.0103 | 122.905 | 122.8226 | 55.8746 | -123.0972
1966.0156 | 123.024 | -58.2504 | 64.6408 | -0.22903 | 0.0076627 | 0.070814 | 0.07009 | 0.13078 | -0.00050425 | -0.0077183 | -0.17563 | -0.008058 | 0.061914 | 0.058253 | 0.0046356 | -0.011974 | 64.4989 | 64.6774 | 4.3167 | -58.3969 | 64.7141 | -58.2962 | -58.3832 | -57.843 | -2.5452 | -58.5068 | 64.6866 | 64.595 | -58.461 | -58.5205 | -0.045777 | -0.13275 | 0.073242 | 122.9279 | -0.14648 | -0.013733 | -0.14191 | -0.21057 | -0.27008 | 0.045776 | 0.40741 | -0.25635 | 0.013733 | -0.045776 | 122.9645 | 122.7493 | 62.5671 | -123.024 | 122.937 | 122.8455 | 55.7053 | -123.1613
1967.0156 | 123.0057 | -58.2321 | 64.6591 | 0.23636 | 0.0085171 | 0.071027 | 0.070517 | 0.13099 | 0.0020593 | -0.0070773 | -0.21378 | -0.0097668 | 0.064051 | 0.057612 | 0.0048492 | -0.010692 | 64.5172 | 64.6317 | 4.2618 | -58.4015 | 64.7644 | -58.3054 | -58.4015 | -57.8522 | -2.417 | -58.5022 | 64.7461 | 64.6225 | -58.4244 | -58.5159 | -0.073242 | -0.16937 | 0.10528 | 122.8638 | -0.16937 | 0 | -0.14191 | -0.19226 | -0.28381 | 0.086975 | 0.37994 | -0.27008 | 0.013733 | -0.036621 | 122.9965 | 122.7493 | 62.4939 | -123.0606 | 122.9782 | 122.8546 | 55.8151 | -123.175
1968.0156 | 123.0789 | -58.3008 | 64.5813 | -0.0383 | 0.014712 | 0.067396 | 0.073935 | 0.12928 | 0.0041955 | -0.0051547 | -0.053558 | -0.0078442 | 0.065119 | 0.05868 | 0.0059174 | -0.011333 | 64.4852 | 64.6179 | 4.4174 | -58.4427 | 64.6866 | -58.3878 | -58.4427 | -57.8934 | -2.1286 | -58.5663 | 64.6591 | 64.5584 | -58.5022 | -58.5571 | -0.086975 | -0.14191 | 0.10528 | 122.9187 | -0.14191 | 0 | -0.096131 | -0.20142 | -0.25635 | 0.07782 | 0.40741 | -0.2655 | -0.009155 | -0.022888 | 122.9874 | 122.7859 | 62.7182 | -123.024 | 122.9599 | 122.8592 | 56.1722 | -123.1384
1969.0156 | 123.0972 | -58.1268 | 64.7278 | 1.2053 | 0.010013 | 0.068464 | 0.067954 | 0.13121 | -0.0054175 | -0.0064365 | -0.061188 | -0.0084852 | 0.063837 | 0.058253 | 0.00549 | -0.0087692 | 64.65 | 64.8239 | 4.2435 | -58.2367 | 64.769 | -58.2047 | -58.2825 | -57.6874 | -2.1561 | -58.3054 | 64.7461 | 64.6683 | -58.3649 | -58.374 | -0.07782 | -0.15564 | 0.041199 | 122.9507 | -0.10986 | 0.045777 | -0.07782 | -0.23804 | -0.24719 | 0.018311 | 0.43945 | -0.17853 | 0.068664 | -0.059509 | 122.8958 | 122.7768 | 62.3703 | -123.0103 | 122.8729 | 122.7951 | 55.9708 | -123.1018
1970.0156 | 123.0881 | -58.2504 | 64.65 | 0.083771 | 0.0085171 | 0.070173 | 0.067954 | 0.12822 | -0.0052039 | -0.0068637 | 0.15244 | -0.0099806 | 0.064051 | 0.058039 | 0.00036322 | -0.0081284 | 64.4623 | 64.6729 | 4.4724 | -58.3786 | 64.7003 | -58.3054 | -58.3694 | -57.7286 | -2.5589 | -58.4427 | 64.6545 | 64.5767 | -58.4381 | -58.493 | -0.054932 | -0.11902 | 0.050354 | 122.9233 | -0.12817 | -0.009155 | -0.18768 | -0.18768 | -0.24262 | 0.004578 | 0.52185 | -0.19226 | 0.050354 | -0.073242 | 122.9507 | 122.7127 | 62.7228 | -123.0194 | 122.905 | 122.8271 | 55.6915 | -123.143
1971.0156 | 123.0469 | -58.2184 | 64.6912 | -0.15274 | 0.010653 | 0.069532 | 0.069235 | 0.12907 | 0.0022729 | -0.0057957 | -0.14511 | -0.0076306 | 0.062769 | 0.059535 | 0.00784 | -0.012401 | 64.5264 | 64.6271 | 4.129 | -58.3832 | 64.769 | -58.3145 | -58.3923 | -57.8339 | -2.1744 | -58.4747 | 64.7507 | 64.6408 | -58.4335 | -58.4427 | -0.09613 | -0.17395 | 0.07782 | 122.8455 | -0.16479 | 0.009155 | -0.1648 | -0.21515 | -0.2243 | 0.059509 | 0.38452 | -0.25635 | -0.032043 | -0.050354 | 122.9874 | 122.7448 | 62.3474 | -123.0835 | 122.9691 | 122.8592 | 56.044 | -123.1338
1972.0156 | 123.0789 | -58.1589 | 64.682 | 0.068512 | 0.0074491 | 0.069105 | 0.066672 | 0.1295 | -0.0037085 | -0.0057957 | -0.11459 | -0.0082716 | 0.059778 | 0.059107 | 0.0016448 | -0.0091966 | 64.5355 | 64.9933 | 4.2023 | -58.3099 | 64.801 | -58.2001 | -58.3054 | -57.7698 | -2.1606 | -58.3557 | 64.7461 | 64.6591 | -58.3603 | -58.4198 | -0.041198 | -0.14648 | 0.11902 | 123.1522 | -0.15106 | -0.004578 | -0.14648 | -0.20142 | -0.26093 | 0.064087 | 0.3891 | -0.19684 | 0.064087 | -0.022888 | 122.9599 | 122.6944 | 62.3611 | -122.9874 | 122.905 | 122.818 | 55.9982 | -123.1018
1973.0156 | 123.0103 | -58.1726 | 64.7324 | -0.21378 | 0.011081 | 0.070814 | 0.07009 | 0.12864 | -0.00071785 | -0.0066501 | -0.54947 | -0.0093396 | 0.062128 | 0.059748 | 0.004422 | -0.011119 | 64.5996 | 64.7415 | 4.0649 | -58.3191 | 64.8102 | -58.2184 | -58.3145 | -57.7744 | -2.1149 | -58.429 | 64.7919 | 64.7095 | -58.3832 | -58.4106 | -0.045777 | -0.14191 | 0.07782 | 122.9141 | -0.14648 | -0.004578 | -0.13275 | -0.21057 | -0.23804 | 0.059509 | 0.39825 | -0.25635 | -0.01831 | -0.022888 | 122.9828 | 122.7722 | 62.2375 | -123.0469 | 122.9645 | 122.8821 | 56.0577 | -123.143
1974.0156 | 123.0789 | -58.2458 | 64.5813 | -0.27481 | 0.0055265 | 0.071027 | 0.07009 | 0.12907 | -0.0022131 | -0.0060093 | -0.12985 | -0.0097668 | 0.060205 | 0.060176 | 0.0029266 | -0.0094102 | 64.5767 | 64.801 | 4.3121 | -58.3557 | 64.7095 | -58.2687 | -58.3694 | -57.8293 | -1.3092 | -58.4381 | 64.7186 | 64.5767 | -58.4244 | -58.4976 | -0.022888 | -0.1236 | 0.12817 | 123.0469 | -0.10986 | 0.013733 | -0.004578 | -0.17853 | -0.25177 | 0.13733 | 0.41656 | -0.19226 | 0.05951 | -0.004578 | 122.9553 | 122.8226 | 62.558 | -122.9507 | 122.9645 | 122.8226 | 56.9366 | -123.0789
1975.0156 | 122.9919 | -58.2687 | 64.6362 | -0.32059 | 0.011722 | 0.06761 | 0.070731 | 0.12864 | 0.0022729 | -0.0070773 | -0.16037 | -0.0082716 | 0.062769 | 0.057398 | 0.0046356 | -0.010478 | 64.4577 | 64.6271 | 4.0924 | -58.4198 | 64.7415 | -58.3328 | -58.4015 | -57.8979 | -2.0508 | -58.5114 | 64.7415 | 64.5813 | -58.4564 | -58.5022 | -0.064087 | -0.13275 | 0.10529 | 122.8958 | -0.15106 | -0.018311 | -0.17853 | -0.18768 | -0.23346 | 0.10529 | 0.37079 | -0.24262 | -0.009156 | -0.054931 | 123.0103 | 122.7264 | 62.3611 | -123.0377 | 123.0103 | 122.85 | 56.218 | -123.1384
1976.0156 | 123.1338 | -58.1955 | 64.6362 | -0.19089 | 0.0091581 | 0.071027 | 0.071158 | 0.12779 | -0.0058447 | -0.0047275 | 0.022736 | -0.010194 | 0.063196 | 0.058039 | 0.0024994 | -0.0098374 | 64.8743 | 64.4485 | 4.0283 | -58.2687 | 64.7095 | -58.2779 | -58.3557 | -57.7698 | -1.9547 | -58.3557 | 64.682 | 64.5859 | -58.3786 | -58.4381 | -0.082397 | -0.16022 | 0.073243 | 122.644 | -0.073242 | 0.086975 | 0.23804 | -0.18311 | -0.24261 | 0.045777 | 0.42572 | -0.16022 | 0.082397 | -0.050354 | 122.905 | 123.0698 | 62.2238 | -122.9919 | 122.8775 | 122.7814 | 56.2408 | -123.0743
1977.0156 | 123.0835 | -58.1772 | 64.682 | -0.19089 | 0.0076627 | 0.070173 | 0.071158 | 0.12907 | -0.0024269 | -0.0053683 | -0.17563 | -0.0095532 | 0.060846 | 0.056544 | 0.0052764 | -0.011333 | 64.595 | 64.7964 | 4.1336 | -58.2916 | 64.7461 | -58.2138 | -58.342 | -57.756 | -1.8219 | -58.3649 | 64.7141 | 64.6317 | -58.3649 | -58.4198 | -0.036621 | -0.16479 | 0.064087 | 122.9736 | -0.11444 | 0.050354 | -0.086975 | -0.18768 | -0.24262 | 0.032043 | 0.42114 | -0.18768 | 0.054932 | -0.050354 | 122.9233 | 122.7722 | 62.3108 | -123.024 | 122.8912 | 122.8088 | 56.3553 | -123.1018
1978.0156 | 123.0286 | -58.0948 | 64.8193 | -0.23666 | 0.013003 | 0.068464 | 0.073935 | 0.13014 | 0.0022729 | -0.0051547 | -0.168 | -0.0084852 | 0.06341 | 0.058894 | 0.0057038 | -0.011546 | 64.6454 | 64.7781 | 3.9047 | -58.2413 | 64.9017 | -58.1497 | -58.2687 | -57.6965 | -2.2064 | -58.3511 | 64.8743 | 64.7369 | -58.2916 | -58.3649 | -0.054931 | -0.17395 | 0.082397 | 122.8729 | -0.14648 | 0.027466 | -0.17395 | -0.19684 | -0.27008 | 0.054932 | 0.39825 | -0.25635 | 0.013733 | -0.082398 | 122.9965 | 122.7402 | 61.9995 | -123.0881 | 122.9691 | 122.8317 | 55.8884 | -123.1842
1979.0156 | 123.0331 | -58.0765 | 64.7919 | -0.25192 | 0.0095853 | 0.071027 | 0.069663 | 0.12864 | -0.0022131 | -0.0040867 | -0.12985 | -0.009126 | 0.057642 | 0.057185 | 0.0046356 | -0.0089828 | 64.682 | 64.888 | 4.0512 | -58.1818 | 64.8605 | -58.1406 | -58.2047 | -57.6691 | -2.179 | -58.2779 | 64.8605 | 64.7507 | -58.2596 | -58.3191 | -0.064087 | -0.12817 | 0.068665 | 122.9645 | -0.10529 | 0.022888 | -0.10986 | -0.18311 | -0.24262 | 0.068665 | 0.40741 | -0.20142 | 0.041199 | -0.041199 | 122.937 | 122.7585 | 62.1277 | -122.9965 | 122.937 | 122.8271 | 55.8975 | -123.111
1980.0156 | 123.0835 | -58.0948 | 64.801 | 0.045624 | 0.0095853 | 0.068891 | 0.07009 | 0.13057 | -0.0043495 | -0.0075047 | 0.65598 | -0.0099806 | 0.064051 | 0.057185 | 0.0033538 | -0.010051 | 64.6545 | 64.8376 | 3.9322 | -58.2138 | 64.8788 | -58.1406 | -58.2092 | -57.692 | -2.3804 | -58.255 | 64.8193 | 64.7095 | -58.2825 | -58.3145 | -0.045776 | -0.11444 | 0.07782 | 122.9324 | -0.11902 | -0.004577 | -0.14648 | -0.18768 | -0.21973 | 0.018311 | 0.40283 | -0.16022 | 0.059509 | -0.091552 | 122.9736 | 122.7493 | 62.027 | -123.0103 | 122.9141 | 122.8043 | 55.7144 | -123.1155
1981.0156 | 123.1018 | -58.0353 | 64.8056 | -0.15274 | 0.0085171 | 0.069532 | 0.071158 | 0.12907 | -0.0022131 | -0.0062229 | -0.14511 | -0.0089124 | 0.061914 | 0.056117 | 0.004422 | -0.011546 | 64.7324 | 64.9384 | 3.7125 | -58.136 | 64.888 | -58.1131 | -58.1772 | -57.605 | -2.0096 | -58.2321 | 64.8788 | 64.7919 | -58.2413 | -58.2825 | -0.07782 | -0.14191 | 0.082397 | 122.9736 | -0.10071 | 0.041199 | -0.073242 | -0.20599 | -0.24719 | 0.073242 | 0.4303 | -0.19684 | 0.050354 | -0.013733 | 122.9233 | 122.7676 | 61.7477 | -122.9828 | 122.9141 | 122.8271 | 56.0257 | -123.0881
1982.0156 | 123.1018 | -58.1085 | 64.7141 | 0.12955 | 0.010013 | 0.067823 | 0.071799 | 0.13099 | -0.00050425 | -0.0051547 | 0.23636 | -0.0089124 | 0.062342 | 0.058253 | 0.0033538 | -0.010692 | 64.6591 | 64.8468 | 3.8315 | -58.2458 | 64.7827 | -58.1818 | -58.2642 | -57.6691 | -1.9775 | -58.3145 | 64.7644 | 64.682 | -58.3282 | -58.3511 | -0.073242 | -0.15564 | 0.068665 | 122.9553 | -0.13733 | 0.01831 | -0.054931 | -0.21973 | -0.24261 | 0.050354 | 0.43945 | -0.20599 | 0.036621 | -0.032043 | 122.8912 | 122.7676 | 61.94 | -122.9782 | 122.8729 | 122.7905 | 56.131 | -123.0652
1983.0156 | 123.0331 | -58.0765 | 64.7552 | 0.076141 | 0.011508 | 0.065687 | 0.069449 | 0.13078 | 0.0048363 | -0.0030185 | 0.13718 | -0.007417 | 0.063623 | 0.05868 | 0.0048492 | -0.011119 | 64.682 | 64.7827 | 3.5065 | -58.2596 | 64.9246 | -58.1406 | -58.2321 | -57.6782 | -1.8127 | -58.3511 | 64.8834 | 64.7781 | -58.2825 | -58.3054 | -0.064087 | -0.15564 | 0.16937 | 122.8592 | -0.18311 | -0.027466 | -0.073242 | -0.20599 | -0.22888 | 0.12817 | 0.39825 | -0.27466 | -0.045776 | 0.022888 | 123.0011 | 122.7585 | 61.5829 | -122.9874 | 122.9599 | 122.8546 | 56.2637 | -123.0606
1984.0156 | 123.0789 | -58.1314 | 64.7003 | 0.13718 | 0.011722 | 0.069105 | 0.069235 | 0.1295 | -0.0039221 | -0.0055821 | 0.26688 | -0.0076306 | 0.06341 | 0.060816 | 0.0039948 | -0.008342 | 64.6225 | 64.7736 | 3.8727 | -58.3054 | 64.7873 | -58.2047 | -58.287 | -57.7057 | -1.6296 | -58.3511 | 64.7644 | 64.6774 | -58.3145 | -58.3557 | -0.073242 | -0.15564 | 0.086975 | 122.905 | -0.17395 | -0.018311 | -0.077819 | -0.18311 | -0.2243 | 0.064087 | 0.42572 | -0.21973 | 0.004578 | -0.022888 | 122.9187 | 122.7539 | 62.0041 | -122.9874 | 122.8958 | 122.8088 | 56.5018 | -123.056
1985.0156 | 123.0835 | -58.0856 | 64.7324 | 0.030365 | 0.0087307 | 0.070387 | 0.069663 | 0.12822 | -0.0028541 | -0.0060093 | 0.14481 | -0.007417 | 0.060633 | 0.058467 | 0.0033538 | -0.0087692 | 64.6408 | 64.8148 | 3.923 | -58.2504 | 64.8285 | -58.1497 | -58.223 | -57.6645 | -1.6022 | -58.2779 | 64.8285 | 64.7552 | -58.2825 | -58.3099 | -0.064087 | -0.13733 | 0.09613 | 122.9004 | -0.1648 | -0.027466 | -0.091553 | -0.19684 | -0.22431 | 0.09613 | 0.42114 | -0.19226 | 0.032044 | 0.022888 | 122.9141 | 122.7264 | 62.0087 | -122.9553 | 122.9141 | 122.8409 | 56.4835 | -123.0423
1986.0156 | 123.056 | -58.1177 | 64.6912 | 0.13718 | 0.010653 | 0.069746 | 0.069876 | 0.12886 | 0.00013675 | -0.0049411 | 0.21347 | -0.010621 | 0.062982 | 0.058467 | 0.0039948 | -0.0091966 | 64.6774 | 64.8102 | 3.9551 | -58.2779 | 64.801 | -58.1955 | -58.2733 | -57.6599 | -1.3916 | -58.3237 | 64.7919 | 64.7003 | -58.2962 | -58.3511 | -0.07782 | -0.15564 | 0.10986 | 122.9279 | -0.16022 | -0.004578 | -0.013733 | -0.17853 | -0.23346 | 0.10071 | 0.45776 | -0.20599 | 0.027466 | 0.009155 | 122.9187 | 122.7951 | 62.0728 | -122.9645 | 122.9095 | 122.818 | 56.7261 | -123.0423
1987.0156 | 123.0927 | -58.136 | 64.7141 | 0.14481 | 0.0070217 | 0.069105 | 0.071372 | 0.13099 | -0.0013587 | -0.0077183 | 0.25162 | -0.0095532 | 0.059564 | 0.055049 | 0.0042084 | -0.010692 | 64.6317 | 64.7644 | 4.0283 | -58.3054 | 64.8148 | -58.2001 | -58.2687 | -57.7011 | -1.4145 | -58.3374 | 64.7964 | 64.6683 | -58.3191 | -58.3832 | -0.064087 | -0.13275 | 0.10071 | 122.9004 | -0.16937 | -0.036621 | -0.082397 | -0.18311 | -0.24719 | 0.082398 | 0.43488 | -0.20142 | 0.045777 | -0.045776 | 122.9507 | 122.7676 | 62.1643 | -122.9828 | 122.9324 | 122.8043 | 56.7215 | -123.0972
1988.0156 | 123.111 | -58.1497 | 64.6408 | 0.10666 | 0.011081 | 0.068891 | 0.067313 | 0.12779 | -0.0011451 | -0.0057957 | 0.2211 | -0.011476 | 0.061914 | 0.058039 | 0.0050628 | -0.011119 | 64.6408 | 64.7552 | 4.1656 | -58.3054 | 64.7232 | -58.2367 | -58.3145 | -57.6828 | -1.1673 | -58.3557 | 64.7095 | 64.6271 | -58.3603 | -58.3923 | -0.086975 | -0.1648 | 0.082398 | 122.905 | -0.15564 | 0.009155 | 0 | -0.21057 | -0.24262 | 0.068665 | 0.46692 | -0.20599 | 0.036621 | -0.013733 | 122.8729 | 122.7905 | 62.3154 | -122.9553 | 122.8592 | 122.7768 | 56.9824 | -123.0331
1989.0156 | 123.0743 | -58.1543 | 64.7095 | -0.03067 | 0.0068081 | 0.070387 | 0.071158 | 0.12993 | -0.0024269 | -0.0055821 | 0.11429 | -0.0099806 | 0.062128 | 0.057826 | 0.0046356 | -0.0096238 | 64.595 | 64.7644 | 4.2435 | -58.3008 | 64.769 | -58.2092 | -58.2916 | -57.7194 | -1.1353 | -58.1818 | 64.7827 | 64.682 | -58.3557 | -58.3878 | -0.054932 | -0.13733 | 0.059509 | 122.9187 | -0.14648 | -0.009155 | -0.11444 | -0.20142 | -0.23346 | 0.073242 | 0.43488 | -0.027466 | 0.20599 | -0.027466 | 122.9233 | 122.7493 | 62.3978 | -123.0011 | 122.937 | 122.8363 | 57.019 | -123.0972
1990.0156 | 123.1384 | -58.1818 | 64.65 | 0.18295 | 0.012576 | 0.068464 | 0.070303 | 0.12928 | 0.0027001 | -0.0083591 | 0.068512 | -0.0095532 | 0.062555 | 0.058039 | 0.0069854 | -0.012187 | 64.769 | 64.7827 | 4.1702 | -58.3054 | 64.7507 | -58.2367 | -58.3099 | -57.6782 | -1.1353 | -58.3511 | 64.7141 | 64.6133 | -58.4061 | -58.4106 | -0.054931 | -0.12817 | 0.10071 | 122.9645 | -0.1236 | 0.004578 | 0.11902 | -0.2243 | -0.22888 | 0.064087 | 0.50354 | -0.16937 | 0.05951 | -0.036621 | 122.9324 | 122.9507 | 62.352 | -122.9599 | 122.8958 | 122.7951 | 57.0465 | -123.0606
1991.0156 | 123.0423 | -58.136 | 64.6912 | 0.12955 | 0.0061673 | 0.069746 | 0.070944 | 0.13377 | -0.0026405 | -0.0049411 | 0.10666 | -0.0089124 | 0.06106 | 0.057826 | 0.0042084 | -0.010692 | 64.6042 | 64.7461 | 3.8818 | -58.3099 | 64.7781 | -58.2001 | -58.2825 | -57.6828 | -1.236 | -58.342 | 64.7598 | 64.65 | -58.3511 | -58.4106 | -0.064087 | -0.14648 | 0.086975 | 122.8821 | -0.17395 | -0.027466 | -0.086975 | -0.21515 | -0.27466 | 0.068665 | 0.45319 | -0.20599 | 0.068665 | -0.041199 | 122.9141 | 122.7402 | 62.0178 | -122.9736 | 122.8958 | 122.7859 | 56.9 | -123.1018
1992.0156 | 123.1247 | -58.1223 | 64.6912 | 0.083771 | 0.013858 | 0.069532 | 0.071372 | 0.12864 | 0.0012047 | -0.0053683 | 0.24399 | -0.009126 | 0.06341 | 0.056544 | 0.0059174 | -0.011974 | 64.6729 | 64.8102 | 3.9139 | -58.2458 | 64.7781 | -58.1909 | -58.2825 | -57.605 | -1.236 | -58.3145 | 64.7736 | 64.6317 | -58.3694 | -58.3969 | -0.068665 | -0.16022 | 0.086975 | 122.9324 | -0.1236 | 0.036621 | -0.01831 | -0.24719 | -0.27466 | 0.082398 | 0.51727 | -0.19226 | 0.082398 | -0.059509 | 122.9004 | 122.7951 | 62.0361 | -122.9736 | 122.8958 | 122.7539 | 56.8863 | -123.0881
1993.0156 | 123.0927 | -58.0994 | 64.7415 | 0.15244 | 0.0087307 | 0.06825 | 0.069449 | 0.13078 | -0.0017859 | -0.0049411 | 0.23636 | -0.0086988 | 0.060846 | 0.054835 | 0.0031402 | -0.012187 | 64.6912 | 64.8193 | 3.8818 | -58.2596 | 64.801 | -58.1726 | -58.2642 | -57.6324 | -1.0986 | -58.3054 | 64.801 | 64.7141 | -58.3145 | -58.342 | -0.073242 | -0.16479 | 0.059509 | 122.9187 | -0.16022 | 0.004577 | -0.050354 | -0.21515 | -0.24262 | 0.059509 | 0.46692 | -0.20599 | 0.036621 | -0.027466 | 122.9004 | 122.7905 | 61.9812 | -123.0057 | 122.9004 | 122.8134 | 57.0007 | -123.0835
1994.0156 | 123.1293 | -58.1406 | 64.6774 | 0.20584 | 0.013003 | 0.068678 | 0.070731 | 0.13206 | -7.6852e-05 | -0.0043003 | 0.78568 | -0.0065626 | 0.064051 | 0.057612 | 0.0057038 | -0.011974 | 64.65 | 64.8148 | 3.8132 | -58.2413 | 64.7461 | -58.2138 | -58.3099 | -57.6416 | -1.2131 | -58.3282 | 64.7461 | 64.65 | -58.3603 | -58.3786 | -0.073242 | -0.16937 | 0.068665 | 122.9553 | -0.10071 | 0.068665 | -0.027466 | -0.21973 | -0.23804 | 0.068665 | 0.49896 | -0.18768 | 0.050354 | -0.027466 | 122.8867 | 122.7905 | 61.9537 | -122.9874 | 122.8867 | 122.7905 | 56.9275 | -123.056
1995.0156 | 123.0927 | -58.0536 | 64.801 | 0.12192 | 0.0093717 | 0.06825 | 0.070303 | 0.12907 | -0.0024269 | -0.0047275 | 0.18295 | -0.0084852 | 0.059137 | 0.057185 | 0.0033538 | -0.011119 | 64.7141 | 64.8376 | 3.9551 | -58.2321 | 64.888 | -58.1314 | -58.2047 | -57.5912 | -1.0574 | -58.255 | 64.8422 | 64.7598 | -58.2184 | -58.3145 | -0.07782 | -0.15106 | 0.086975 | 122.8912 | -0.17853 | -0.027466 | -0.086975 | -0.16479 | -0.26093 | 0.041199 | 0.46234 | -0.20142 | 0.059509 | -0.041198 | 122.9416 | 122.7676 | 62.0087 | -123.0057 | 122.8958 | 122.8134 | 56.9962 | -123.1155
1996.0156 | 123.0698 | -58.0811 | 64.7736 | 0.15244 | 0.011935 | 0.069959 | 0.069449 | 0.13206 | -0.00029045 | -0.0038731 | 0.18295 | -0.0086988 | 0.064691 | 0.056117 | 0.004422 | -0.0081284 | 64.7003 | 64.8468 | 4.0375 | -58.2413 | 64.8331 | -58.1589 | -58.2138 | -57.6279 | -0.84228 | -58.3008 | 64.8102 | 64.7141 | -58.287 | -58.3374 | -0.07782 | -0.13275 | 0.059509 | 122.9279 | -0.16022 | -0.027466 | -0.073243 | -0.20599 | -0.25635 | 0.036621 | 0.45319 | -0.21973 | 0.036621 | -0.05951 | 122.9141 | 122.7814 | 62.1185 | -122.9874 | 122.8912 | 122.7951 | 57.2388 | -123.111
1997.0156 | 123.0606 | -58.0124 | 64.8285 | 0.12955 | 0.0091581 | 0.071241 | 0.068167 | 0.12715 | -0.0028541 | -0.0062229 | 0.19821 | -0.0095532 | 0.06341 | 0.055476 | 0.0048492 | -0.010265 | 64.7324 | 64.8697 | 3.7537 | -58.1909 | 64.9063 | -58.1039 | -58.1543 | -57.5775 | -0.86517 | -58.2138 | 64.8834 | 64.7964 | -58.2047 | -58.2687 | -0.091553 | -0.14191 | 0.07782 | 122.8821 | -0.17853 | -0.036621 | -0.09613 | -0.19226 | -0.25635 | 0.054932 | 0.43488 | -0.20142 | 0.054932 | -0.032043 | 122.9187 | 122.7448 | 61.7661 | -122.9828 | 122.8958 | 122.8088 | 57.1472 | -123.0972
1998.0156 | 123.0881 | -57.9712 | 64.8788 | 0.20584 | 0.01514 | 0.06825 | 0.069235 | 0.13057 | 0.0027001 | -0.0036595 | 0.16769 | -0.005708 | 0.061914 | 0.057612 | 0.0057038 | -0.012187 | 64.7919 | 64.8926 | 3.7491 | -58.1589 | 64.975 | -58.0215 | -58.0994 | -57.4814 | -1.2039 | -58.1863 | 64.9658 | 64.8376 | -58.168 | -58.2138 | -0.050354 | -0.12817 | 0.096131 | 122.8638 | -0.18768 | -0.05951 | -0.086975 | -0.19684 | -0.24262 | 0.086975 | 0.48981 | -0.21515 | 0.027466 | -0.041199 | 122.9462 | 122.7631 | 61.7203 | -122.9782 | 122.937 | 122.8088 | 56.7673 | -123.0927
1999.0156 | 123.0194 | -57.9803 | 64.8651 | 0.068512 | 0.0080899 | 0.068678 | 0.070944 | 0.12822 | -0.0026405 | -0.0070773 | 0.13718 | -0.0086988 | 0.063196 | 0.056544 | 0.0046356 | -0.0081284 | 64.7781 | 64.9384 | 3.8177 | -58.1223 | 64.9887 | -58.0124 | -58.1177 | -57.5363 | -1.3733 | -58.1543 | 64.9475 | 64.8331 | -58.1451 | -58.1863 | -0.032043 | -0.13733 | 0.1236 | 122.9187 | -0.14191 | -0.004577 | -0.086975 | -0.16479 | -0.20599 | 0.082398 | 0.44403 | -0.17395 | 0.032043 | -0.032043 | 122.9691 | 122.7585 | 61.7981 | -122.9828 | 122.9279 | 122.8134 | 56.6071 | -123.0515
2000.0156 | 123.1018 | -57.9941 | 64.8514 | 0.17532 | 0.013217 | 0.068891 | 0.068381 | 0.1295 | 0.0031273 | -0.0036595 | 0.47287 | -0.0093396 | 0.062128 | 0.058467 | 0.0033538 | -0.011333 | 64.8102 | 64.9658 | 3.8452 | -58.2504 | 64.8651 | -58.0582 | -58.1589 | -57.4585 | -1.3321 | -58.1451 | 64.92 | 64.8148 | -58.1772 | -58.2184 | -0.064087 | -0.1648 | 0.013733 | 122.9599 | -0.25635 | -0.091552 | -0.041198 | -0.18311 | -0.2243 | 0.068665 | 0.53558 | -0.15106 | 0.073242 | -0.036621 | 122.8592 | 122.8043 | 61.8393 | -123.0103 | 122.9141 | 122.8088 | 56.662 | -123.0698
2001.0156 | 123.1247 | -57.9346 | 64.8972 | -0.00015269 | 0.0065945 | 0.069105 | 0.070517 | 0.12758 | -0.0039221 | -0.0053683 | 0.022736 | -0.0082716 | 0.06341 | 0.058039 | 0.0022858 | -0.012187 | 64.7964 | 64.9521 | 3.6026 | -58.0811 | 65.007 | -58.0261 | -58.0994 | -57.4997 | -1.3 | -58.0994 | 64.9475 | 64.8651 | -58.1314 | -58.1772 | -0.091553 | -0.16479 | 0.10986 | 122.8867 | -0.14648 | 0.01831 | -0.10071 | -0.19684 | -0.24262 | 0.050354 | 0.43487 | -0.16479 | 0.07782 | -0.032044 | 122.9416 | 122.731 | 61.5372 | -122.9965 | 122.8821 | 122.7997 | 56.6345 | -123.0743
2002.0156 | 123.0515 | -57.9895 | 64.888 | 0.15244 | 0.01514 | 0.069319 | 0.073935 | 0.12928 | 0.0044091 | -0.0049411 | 0.18295 | -0.0054944 | 0.066187 | 0.055476 | 0.0076264 | -0.010692 | 64.7919 | 64.8697 | 3.5294 | -58.1635 | 64.9796 | -58.0444 | -58.1543 | -57.5363 | -1.4465 | -58.2321 | 64.9475 | 64.8468 | -58.1955 | -58.2458 | -0.054932 | -0.16479 | 0.091553 | 122.8592 | -0.17395 | -0.009155 | -0.09613 | -0.20599 | -0.25635 | 0.05951 | 0.45319 | -0.24262 | 0.013733 | -0.041198 | 122.9691 | 122.7814 | 61.5189 | -123.0423 | 122.937 | 122.8363 | 56.543 | -123.1338
2003.0156 | 123.2529 | -57.9483 | 64.92 | -0.03067 | 0.0083035 | 0.068891 | 0.070303 | 0.13163 | -0.0037085 | -0.0068637 | -0.084076 | -0.0082716 | 0.061914 | 0.057612 | 0.0039948 | -0.010478 | 64.8239 | 64.9933 | 3.598 | -58.0994 | 64.9384 | -58.0765 | -58.1406 | -57.4677 | -0.89264 | -58.1039 | 64.8972 | 64.8239 | -58.1772 | -58.2047 | -0.12817 | -0.19226 | 0.01831 | 122.9416 | -0.15106 | 0.041199 | -0.09613 | -0.22888 | -0.25635 | -0.022888 | 0.48065 | -0.15564 | 0.10071 | -0.09613 | 122.8867 | 122.7722 | 61.5463 | -123.0606 | 122.8455 | 122.7722 | 57.0557 | -123.1247
2004.0156 | 123.0194 | -58.0673 | 64.801 | 0.0074768 | 0.012576 | 0.065473 | 0.070731 | 0.12779 | 0.0044091 | -0.0034457 | 0.15244 | -0.0078442 | 0.06106 | 0.05868 | 0.0074126 | -0.0094102 | 64.6637 | 64.769 | 3.4927 | -58.2504 | 64.8972 | -58.168 | -58.2458 | -57.6508 | -0.87891 | -58.342 | 64.8788 | 64.7507 | -58.2733 | -58.3237 | -0.10071 | -0.17853 | 0.096131 | 122.8363 | -0.18311 | -0.004577 | -0.13733 | -0.20599 | -0.25635 | 0.07782 | 0.41656 | -0.27466 | -0.018311 | -0.050354 | 122.9645 | 122.731 | 61.5601 | -123.0469 | 122.9462 | 122.818 | 57.1884 | -123.1247
2005.0156 | 123.0469 | -58.0261 | 64.8422 | 0.15244 | 0.015994 | 0.06825 | 0.067954 | 0.12886 | 0.0027001 | -0.0028049 | 0.16769 | -0.0076306 | 0.064691 | 0.060176 | 0.0048492 | -0.0081284 | 64.7232 | 64.8056 | 3.685 | -58.2047 | 64.9521 | -58.1039 | -58.1635 | -57.5821 | -0.70496 | -58.2413 | 64.8972 | 64.8102 | -58.2001 | -58.2504 | -0.07782 | -0.13733 | 0.10986 | 122.8317 | -0.17853 | -0.041199 | -0.11902 | -0.17395 | -0.2243 | 0.054932 | 0.44403 | -0.21515 | 0.009155 | -0.032043 | 122.9782 | 122.7493 | 61.7111 | -123.0057 | 122.9233 | 122.8363 | 57.3212 | -123.0927
2006.0156 | 122.9828 | -57.9025 | 65.0162 | -0.00015269 | 0.014285 | 0.067823 | 0.072012 | 0.12993 | 0.0027001 | -0.0017369 | 0.0074766 | -0.0082716 | 0.062128 | 0.058253 | 0.0048492 | -0.011974 | 64.8651 | 64.9704 | 3.9368 | -58.049 | 65.0894 | -57.9666 | -58.0353 | -57.4997 | -0.5127 | -58.1772 | 65.0665 | 64.9979 | -58.0719 | -58.1497 | -0.064087 | -0.13275 | 0.073243 | 122.8729 | -0.14648 | -0.013733 | -0.15106 | -0.16937 | -0.24719 | 0.050354 | 0.40283 | -0.27466 | -0.027466 | -0.01831 | 122.9919 | 122.7676 | 61.8393 | -123.0515 | 122.9691 | 122.9004 | 57.3898 | -123.1659
2007.0156 | 123.1064 | -57.962 | 64.8697 | 0.15244 | 0.011935 | 0.068678 | 0.071372 | 0.12928 | 0.00077755 | -0.0038731 | 0.21347 | -0.0076306 | 0.062128 | 0.060389 | 0.0042084 | -0.0087692 | 64.7781 | 64.8788 | 3.6209 | -58.1589 | 64.9887 | -58.0399 | -58.136 | -57.518 | -0.33875 | -58.168 | 64.9246 | 64.8514 | -58.168 | -58.2184 | -0.07782 | -0.17395 | 0.11902 | 122.8409 | -0.19684 | -0.022889 | -0.091553 | -0.20599 | -0.25635 | 0.054932 | 0.44403 | -0.20599 | 0.050354 | -0.018311 | 122.9507 | 122.7402 | 61.5829 | -123.0057 | 122.8867 | 122.8134 | 57.6233 | -123.0881
2008.0156 | 123.0103 | -58.0719 | 64.8376 | 0.12192 | 0.015353 | 0.071027 | 0.071372 | 0.12928 | 0.0031273 | -0.0030185 | 0.32791 | -0.0065626 | 0.064478 | 0.058467 | 0.0052764 | -0.0089828 | 64.3982 | 65.1764 | 3.8406 | -58.255 | 64.9567 | -58.1314 | -58.1863 | -57.6645 | -0.2243 | -58.3054 | 64.9155 | 64.8331 | -58.2596 | -58.2779 | -0.05951 | -0.11444 | 0.11902 | 123.2483 | -0.18311 | -0.068665 | -0.43945 | -0.18768 | -0.20599 | 0.07782 | 0.40741 | -0.23346 | -0.027466 | -0.004577 | 123.0286 | 122.4701 | 61.9125 | -123.024 | 122.9874 | 122.905 | 57.8476 | -123.1155
2009.0156 | 123.1064 | -57.9391 | 64.8972 | 0.10666 | 0.014071 | 0.069532 | 0.071372 | 0.13035 | -0.0015723 | -0.0047275 | 0.23636 | -0.0093396 | 0.064691 | 0.056971 | 0.004422 | -0.008342 | 64.8331 | 64.9429 | 3.511 | -58.0948 | 65.0345 | -57.9941 | -58.0994 | -57.5089 | -0.082397 | -58.0902 | 64.9704 | 64.8834 | -58.136 | -58.1589 | -0.054932 | -0.16022 | 0.13733 | 122.8821 | -0.15564 | 0.004577 | -0.064087 | -0.19684 | -0.21973 | 0.073242 | 0.4303 | -0.15106 | 0.068665 | -0.013733 | 122.9736 | 122.7722 | 61.4502 | -122.9965 | 122.9095 | 122.8226 | 57.8568 | -123.056
2010.0156 | 122.9782 | -57.9208 | 64.9796 | 0.045624 | 0.017062 | 0.069319 | 0.070303 | 0.13014 | 0.0024865 | -0.0043003 | 0.15244 | -0.0067762 | 0.064691 | 0.057826 | 0.0059174 | -0.0087692 | 64.8605 | 64.92 | 3.2135 | -58.0582 | 65.1123 | -57.9346 | -58.0444 | -57.5455 | -0.041199 | -58.1955 | 65.0848 | 64.9887 | -58.0719 | -58.1589 | -0.013733 | -0.1236 | 0.13275 | 122.8409 | -0.13733 | -0.013733 | -0.11902 | -0.15106 | -0.23804 | 0.10529 | 0.37537 | -0.27466 | -0.036621 | 0.009155 | 123.0331 | 122.7814 | 61.1343 | -123.024 | 123.0057 | 122.9095 | 57.8796 | -123.1384
2011.0156 | 123.056 | -57.8567 | 65.0116 | 0.13718 | 0.013858 | 0.068464 | 0.069663 | 0.13057 | 0.0014185 | -0.0045139 | 0.18295 | -0.009126 | 0.06341 | 0.058894 | 0.0050628 | -0.008342 | 64.8697 | 64.9796 | 3.0991 | -58.0444 | 65.0894 | -57.9071 | -57.9987 | -57.4539 | 0.059509 | -58.0948 | 65.094 | 64.9887 | -58.0582 | -58.0994 | -0.050354 | -0.14191 | 0.07782 | 122.8363 | -0.18768 | -0.045777 | -0.14191 | -0.20142 | -0.24262 | 0.082397 | 0.40283 | -0.23804 | 0.004577 | -0.022889 | 122.9462 | 122.7264 | 60.9558 | -123.0103 | 122.9507 | 122.8455 | 57.9163 | -123.111
2012.0156 | 123.0103 | -57.7835 | 65.1123 | -0.24429 | 0.017489 | 0.0706 | 0.07244 | 0.12736 | 0.0016321 | -0.0036595 | -0.00015237 | -0.0093396 | 0.063837 | 0.057826 | 0.0063446 | -0.010905 | 65.0208 | 65.1031 | 3.3966 | -57.93 | 65.1993 | -57.843 | -57.9254 | -57.3807 | -0.004578 | -58.0124 | 65.1627 | 65.0848 | -57.9895 | -58.0399 | -0.05951 | -0.14191 | 0.086975 | 122.8867 | -0.14649 | -0.004578 | -0.091553 | -0.20599 | -0.25635 | 0.050354 | 0.40283 | -0.22888 | 0.027466 | -0.027466 | 122.9828 | 122.8043 | 61.1801 | -123.0377 | 122.9462 | 122.8683 | 57.7789 | -123.1522
2013.0156 | 123.0011 | -57.8018 | 65.1581 | 0.015106 | 0.019198 | 0.069532 | 0.066885 | 0.13014 | 0.0020593 | -0.0036595 | 0.14481 | -0.0059216 | 0.065759 | 0.060176 | 0.0057038 | -0.0081284 | 64.9384 | 65.0482 | 3.5431 | -57.9483 | 65.1993 | -57.8247 | -57.9025 | -57.4081 | -0.40283 | -58.049 | 65.213 | 65.1443 | -57.9483 | -58.0124 | -0.022888 | -0.10071 | 0.041199 | 122.85 | -0.14648 | -0.045776 | -0.21973 | -0.14648 | -0.21057 | 0.054932 | 0.39368 | -0.24719 | -0.036621 | -0.013733 | 123.0011 | 122.7402 | 61.3449 | -123.0606 | 123.0148 | 122.9462 | 57.399 | -123.1705
2014.0156 | 123.0423 | -57.7698 | 65.1215 | -0.053558 | 0.016208 | 0.069105 | 0.07009 | 0.13121 | 0.00099115 | -0.0019505 | 0.053253 | -0.0061352 | 0.064051 | 0.057185 | 0.0050628 | -0.0091966 | 65.0253 | 65.1215 | 3.598 | -57.9071 | 65.2359 | -57.8201 | -57.9025 | -57.3624 | -0.027466 | -58.017 | 65.2084 | 65.1306 | -57.9575 | -57.9941 | -0.050354 | -0.13275 | 0.11444 | 122.8912 | -0.13733 | -0.004577 | -0.09613 | -0.18768 | -0.2243 | 0.086975 | 0.40741 | -0.24719 | -0.022888 | 0.009155 | 123.0057 | 122.7951 | 61.3678 | -123.024 | 122.9782 | 122.9004 | 57.7423 | -123.1155
2015.0156 | 123.0515 | -57.93 | 64.9567 | 0.10666 | 0.014712 | 0.068464 | 0.072226 | 0.12886 | -7.6852e-05 | -0.0049411 | 0.21347 | -0.0076306 | 0.061914 | 0.057185 | 0.0035674 | -0.0096238 | 64.7781 | 64.9155 | 3.3463 | -58.1131 | 65.0528 | -58.0032 | -58.0948 | -57.5272 | 0.22888 | -58.1635 | 65.0345 | 64.9338 | -58.136 | -58.1497 | -0.073242 | -0.16479 | 0.09613 | 122.8455 | -0.1831 | -0.01831 | -0.17853 | -0.20599 | -0.21973 | 0.07782 | 0.40283 | -0.23346 | -0.013733 | -0.022888 | 122.9828 | 122.7081 | 61.2762 | -123.0515 | 122.9645 | 122.8638 | 58.1589 | -123.1064
2016.0156 | 123.0148 | -57.9712 | 64.9338 | -0.023041 | 0.01578 | 0.06761 | 0.07244 | 0.12886 | 0.0016321 | -0.0047275 | 0.076141 | -0.008058 | 0.064691 | 0.058039 | 0.0052764 | -0.0094102 | 64.8102 | 64.9109 | 3.3279 | -58.1177 | 65.0299 | -58.017 | -58.1039 | -57.5684 | 0.35706 | -58.2138 | 65.0024 | 64.9384 | -58.1726 | -58.2321 | -0.045777 | -0.13275 | 0.09613 | 122.8821 | -0.14649 | -0.013733 | -0.1236 | -0.20142 | -0.26093 | 0.068664 | 0.40283 | -0.24262 | 0.018311 | 0.004577 | 123.0011 | 122.7814 | 61.2991 | -123.0377 | 122.9736 | 122.9095 | 58.3282 | -123.1659
2017.0156 | 122.9874 | -57.9895 | 64.8926 | 0.13718 | 0.01514 | 0.067396 | 0.070517 | 0.12672 | 0.0012047 | -0.0038731 | 1.48 | -0.010194 | 0.062128 | 0.057398 | 0.0052764 | -0.011119 | 64.7461 | 64.8102 | 3.0945 | -58.1635 | 65.0162 | -58.0673 | -58.1406 | -57.637 | 0.45319 | -58.2733 | 64.9841 | 64.9155 | -58.168 | -58.2321 | -0.07782 | -0.15106 | 0.1236 | 122.7997 | -0.17395 | -0.022888 | -0.14648 | -0.17853 | -0.24262 | 0.091553 | 0.35248 | -0.28381 | -0.041198 | 0.022888 | 123.0057 | 122.7356 | 61.084 | -123.0331 | 122.9736 | 122.905 | 58.4427 | -123.1247
2018.0156 | 123.0286 | -57.9163 | 64.9704 | -0.068817 | 0.015567 | 0.066114 | 0.073294 | 0.12907 | 0.00035035 | -0.0038731 | -0.015411 | -0.009126 | 0.062555 | 0.055689 | 0.0048492 | -0.011974 | 64.9246 | 64.9933 | 3.0762 | -58.0719 | 65.0665 | -57.9895 | -58.0673 | -57.486 | 0.045776 | -58.1451 | 65.062 | 64.9841 | -58.0902 | -58.1589 | -0.073242 | -0.15106 | 0.09613 | 122.9095 | -0.15564 | -0.004577 | -0.045776 | -0.17395 | -0.24262 | 0.091553 | 0.4303 | -0.22888 | 0.013733 | 0.013733 | 122.9828 | 122.8409 | 60.9924 | -123.0377 | 122.9782 | 122.9004 | 57.962 | -123.1293
2019.0156 | 123.0469 | -57.9025 | 65.0299 | -0.053558 | 0.016635 | 0.068678 | 0.070731 | 0.12779 | 0.0024865 | -0.0047275 | 0.10666 | -0.0065626 | 0.065546 | 0.05868 | 0.0050628 | -0.0096238 | 64.8788 | 65.0024 | 3.0167 | -58.0353 | 65.1031 | -57.9163 | -57.9941 | -57.4768 | 0.16022 | -58.136 | 65.0574 | 65.0345 | -58.0719 | -58.1131 | -0.013733 | -0.091553 | 0.073242 | 122.905 | -0.13275 | -0.041198 | -0.15106 | -0.16937 | -0.21057 | 0.027466 | 0.42572 | -0.23346 | -0.022888 | 0.004578 | 123.0057 | 122.7814 | 60.9192 | -123.024 | 122.9599 | 122.937 | 58.0627 | -123.143
2020.0156 | 123.0423 | -57.8659 | 65.0024 | -0.14511 | 0.01514 | 0.070173 | 0.073508 | 0.13035 | 0.0027001 | -0.0051547 | -0.053558 | -0.005708 | 0.061701 | 0.057612 | 0.002713 | -0.01176 | 64.92 | 65.0024 | 2.9938 | -57.9895 | 65.1306 | -57.9391 | -57.9895 | -57.4219 | 0.17395 | -58.0948 | 65.0803 | 65.0116 | -58.0582 | -58.1085 | -0.073242 | -0.1236 | 0.12817 | 122.8683 | -0.1236 | 0 | -0.082397 | -0.19226 | -0.24262 | 0.07782 | 0.44403 | -0.22888 | 0.013733 | 0.009156 | 122.9965 | 122.786 | 60.8597 | -122.9919 | 122.9462 | 122.8775 | 58.0399 | -123.111
2021.0156 | 123.024 | -57.8888 | 65.0208 | -0.0077822 | 0.017276 | 0.06825 | 0.069235 | 0.1295 | 0.00077755 | -0.0070773 | 0.0914 | -0.0067762 | 0.063623 | 0.057398 | 0.0048492 | -0.011974 | 64.8743 | 64.9612 | 3.0899 | -58.0536 | 65.0848 | -57.9483 | -58.0444 | -57.4905 | 0.009155 | -58.1497 | 65.094 | 65.0024 | -58.0856 | -58.1406 | -0.059509 | -0.15564 | 0.064087 | 122.85 | -0.1648 | -0.009155 | -0.14648 | -0.19684 | -0.25177 | 0.073242 | 0.39825 | -0.26093 | -0.009155 | -0.018311 | 122.9736 | 122.7631 | 60.9787 | -123.0652 | 122.9828 | 122.8912 | 57.8979 | -123.1613
2022.0156 | 123.1293 | -57.8979 | 64.9979 | -0.068817 | 0.015567 | 0.068891 | 0.073508 | 0.12843 | -0.00050425 | -0.0057957 | 0.022736 | -0.0065626 | 0.064478 | 0.057826 | 0.0046356 | -0.010265 | 64.8788 | 64.9979 | 3.2135 | -58.0399 | 65.0848 | -57.9437 | -58.0444 | -57.4585 | 0.054932 | -58.1314 | 65.0436 | 65.0024 | -58.1131 | -58.1589 | -0.045777 | -0.14649 | 0.086975 | 122.8958 | -0.14191 | 0.004578 | -0.11902 | -0.21515 | -0.26093 | 0.045776 | 0.43945 | -0.23346 | 0.027466 | 0.004577 | 122.9828 | 122.7768 | 61.1114 | -123.0423 | 122.9416 | 122.9004 | 57.9529 | -123.1567
2023.0156 | 123.024 | -57.9849 | 64.9429 | -0.0077822 | 0.01514 | 0.068891 | 0.072226 | 0.12907 | 0.00099115 | -0.0047275 | 0.060883 | -0.0069898 | 0.063837 | 0.059321 | 0.0046356 | -0.010905 | 64.7736 | 64.8697 | 3.3051 | -58.1543 | 65.0116 | -58.0353 | -58.1268 | -57.6004 | -0.013733 | -58.2458 | 64.9658 | 64.92 | -58.1955 | -58.2367 | -0.050354 | -0.14191 | 0.068665 | 122.8546 | -0.16937 | -0.027466 | -0.16937 | -0.21057 | -0.25177 | 0.022888 | 0.38452 | -0.26093 | -0.009156 | -0.022888 | 122.9965 | 122.7585 | 61.29 | -123.0698 | 122.9507 | 122.905 | 57.9712 | -123.1796
2024.0156 | 123.0606 | -57.8751 | 65.0299 | -0.19089 | 0.011508 | 0.06825 | 0.070731 | 0.13057 | -0.00071785 | -0.0066501 | -0.11459 | -0.0078442 | 0.062342 | 0.058253 | 0.0018584 | -0.0096238 | 64.8605 | 64.9933 | 3.4149 | -58.017 | 65.1352 | -57.9529 | -58.0261 | -57.4768 | -0.022888 | -58.0811 | 65.0803 | 65.0391 | -58.0582 | -58.1085 | -0.07782 | -0.15106 | 0.10529 | 122.8683 | -0.14191 | 0.009155 | -0.16937 | -0.18311 | -0.23346 | 0.050354 | 0.39825 | -0.20599 | 0.027466 | 0.009155 | 123.0103 | 122.7356 | 61.29 | -123.056 | 122.9553 | 122.9141 | 57.8522 | -123.1384
2025.0156 | 123.024 | -57.7011 | 65.1581 | -0.015411 | 0.014499 | 0.068891 | 0.070517 | 0.12886 | -0.0015723 | -0.0047275 | -0.038299 | -0.0065626 | 0.064691 | 0.055903 | 0.00549 | -0.0096238 | 65.0574 | 65.2313 | 3.3188 | -57.8567 | 65.2908 | -57.7469 | -57.8293 | -57.28 | 0.068665 | -57.9346 | 65.2542 | 65.1993 | -57.9071 | -57.962 | -0.045776 | -0.12817 | 0.13275 | 122.9324 | -0.15564 | -0.027465 | -0.10071 | -0.20599 | -0.26093 | 0.09613 | 0.42114 | -0.23346 | 0.027466 | 0.041199 | 122.9919 | 122.7585 | 61.0199 | -122.9874 | 122.9553 | 122.9004 | 57.7698 | -123.1201
2026.0156 | 123.0377 | -57.5912 | 65.3503 | -0.25192 | 0.013431 | 0.069532 | 0.071372 | 0.13163 | -0.0026405 | -0.0087863 | -0.091705 | -0.0082716 | 0.063196 | 0.057826 | 0.0024994 | -0.0091966 | 65.1031 | 65.2496 | 3.1403 | -57.7744 | 65.3915 | -57.6691 | -57.7606 | -57.2388 | 0.13275 | -57.8339 | 65.3503 | 65.3229 | -57.8201 | -57.8339 | -0.077819 | -0.16937 | 0.041199 | 122.8409 | -0.1831 | -0.013733 | -0.24719 | -0.22888 | -0.24261 | 0 | 0.35248 | -0.24261 | 0 | -0.027466 | 122.9828 | 122.6944 | 60.7315 | -123.111 | 122.9416 | 122.9141 | 57.724 | -123.1842
2027.0156 | 123.056 | -57.9529 | 64.9704 | -0.168 | 0.013217 | 0.070173 | 0.072012 | 0.12928 | 0.0012047 | -0.0066501 | -0.12985 | -0.0072034 | 0.063623 | 0.059107 | 0.0024994 | -0.010051 | 64.7964 | 64.9155 | 2.9526 | -58.1039 | 65.0757 | -57.9941 | -58.0811 | -57.5592 | 0.30212 | -58.1772 | 65.0162 | 64.9429 | -58.1497 | -58.1955 | -0.041199 | -0.12817 | 0.10529 | 122.8683 | -0.15106 | -0.022888 | -0.17395 | -0.19684 | -0.24262 | 0.045776 | 0.39368 | -0.2243 | 0.018311 | -0.027466 | 123.0286 | 122.7493 | 60.9055 | -123.0515 | 122.9691 | 122.8958 | 58.255 | -123.1659
2028.0156 | 123.0011 | -57.93 | 64.9841 | -0.21378 | 0.010226 | 0.068891 | 0.072012 | 0.13121 | -0.0026405 | -0.0077183 | -0.14511 | -0.0084852 | 0.06341 | 0.058467 | 0.0033538 | -0.0096238 | 64.7964 | 64.9384 | 2.9022 | -58.0856 | 65.0711 | -57.9895 | -58.0765 | -57.5409 | 0.33875 | -57.9758 | 65.1077 | 65.0345 | -58.0856 | -58.1497 | -0.059509 | -0.14648 | 0.086975 | 122.8683 | -0.15564 | -0.009155 | -0.18768 | -0.15564 | -0.21973 | 0.1236 | 0.3891 | -0.045776 | 0.17395 | 0.050354 | 123.0011 | 122.7264 | 60.8322 | -123.0606 | 123.0377 | 122.9645 | 58.2687 | -123.1338
2029.0156 | 123.0743 | -57.9575 | 64.9246 | -0.168 | 0.014285 | 0.069532 | 0.073508 | 0.12971 | 0.0020593 | -0.0025913 | -0.053558 | -0.0076306 | 0.062769 | 0.057826 | 0.0024994 | -0.010905 | 64.8285 | 64.9658 | 2.916 | -58.0856 | 65.0391 | -57.9941 | -58.1039 | -57.5272 | 0.65002 | -58.1818 | 65.0208 | 64.9384 | -58.1406 | -58.2047 | -0.036622 | -0.14648 | 0.11444 | 122.9233 | -0.12817 | 0.018311 | -0.096131 | -0.18311 | -0.24719 | 0.09613 | 0.4303 | -0.2243 | 0.022888 | 0.013732 | 122.9965 | 122.7859 | 60.8734 | -123.0286 | 122.9782 | 122.8958 | 58.6075 | -123.1293
2030.0156 | 123.024 | -57.8751 | 65.0345 | -0.22903 | 0.010013 | 0.069319 | 0.070517 | 0.13313 | -0.0022131 | -0.0036595 | -0.16037 | -0.0099806 | 0.062769 | 0.05633 | 0.0065582 | -0.0094102 | 64.8239 | 64.9841 | 3.1998 | -58.0582 | 65.1169 | -57.9483 | -58.0444 | -57.6233 | 0.27466 | -58.1726 | 65.0894 | 64.9933 | -58.0902 | -58.136 | -0.073242 | -0.16937 | 0.082397 | 122.8592 | -0.18311 | -0.013733 | -0.21057 | -0.21515 | -0.26093 | 0.054932 | 0.25177 | -0.29755 | -0.036621 | -0.041199 | 122.9919 | 122.699 | 61.0748 | -123.0789 | 122.9645 | 122.8683 | 58.1497 | -123.1705
2031.0156 | 123.0423 | -57.5363 | 65.387 | -0.19089 | 0.01279 | 0.066755 | 0.071372 | 0.13057 | 0.00099115 | -0.0060093 | -0.12985 | -0.0093396 | 0.064691 | 0.057826 | 0.0052764 | -0.011546 | 65.181 | 65.3275 | 3.3508 | -57.6874 | 65.4602 | -57.6004 | -57.6874 | -57.1564 | 0.56305 | -57.7698 | 65.4282 | 65.3275 | -57.7286 | -57.8018 | -0.064087 | -0.15106 | 0.073242 | 122.8638 | -0.15106 | 0 | -0.20599 | -0.19226 | -0.2655 | 0.041199 | 0.37994 | -0.23346 | 0.032044 | -0.059509 | 122.9965 | 122.7173 | 60.8871 | -123.0743 | 122.9645 | 122.8638 | 58.0994 | -123.1888
2032.0156 | 123.0103 | -57.4493 | 65.506 | -0.25955 | 0.0087307 | 0.06825 | 0.068808 | 0.13142 | -0.0041357 | -0.0045139 | -0.47317 | -0.009126 | 0.062342 | 0.059107 | 0.001004 | -0.0096238 | 65.3275 | 65.4968 | 3.2547 | -57.5455 | 65.5746 | -57.4722 | -57.5272 | -57.0511 | 0.15564 | -57.6599 | 65.5701 | 65.4922 | -57.6187 | -57.6508 | -0.022888 | -0.07782 | 0.068665 | 122.9462 | -0.09613 | -0.01831 | -0.17853 | -0.16937 | -0.20142 | 0.064087 | 0.39825 | -0.21057 | -0.009155 | -0.013732 | 123.024 | 122.7768 | 60.704 | -123.0331 | 123.0194 | 122.9416 | 57.605 | -123.1567
2033.0156 | 123.0194 | -57.4951 | 65.4327 | -0.21378 | 0.011081 | 0.070173 | 0.071585 | 0.13014 | -0.0017859 | -0.0043003 | -0.15274 | -0.0095532 | 0.064264 | 0.057398 | 0.0012176 | -0.0091966 | 65.2451 | 65.4007 | 3.0624 | -57.6279 | 65.5243 | -57.5272 | -57.6187 | -57.074 | -0.009155 | -57.756 | 65.5197 | 65.4327 | -57.6691 | -57.7286 | -0.032044 | -0.1236 | 0.091553 | 122.8958 | -0.13275 | -0.009156 | -0.18768 | -0.17395 | -0.23346 | 0.086975 | 0.42114 | -0.26093 | -0.027465 | 0 | 123.0194 | 122.7402 | 60.5576 | -123.0515 | 123.0148 | 122.9279 | 57.486 | -123.1613
2034.0156 | 123.056 | -57.7103 | 65.1398 | -0.21378 | 0.0095853 | 0.069959 | 0.07009 | 0.13142 | -0.0022131 | -0.0075047 | -0.068817 | -0.0093396 | 0.060633 | 0.059962 | 0.0035674 | -0.010051 | 65.0299 | 65.2405 | 3.241 | -57.8339 | 65.2267 | -57.7789 | -57.8659 | -57.3303 | -0.091553 | -57.9117 | 65.2084 | 65.126 | -57.93 | -58.0032 | -0.068665 | -0.15564 | 0.086975 | 122.9507 | -0.1236 | 0.032044 | -0.10986 | -0.21973 | -0.29297 | 0.068664 | 0.37994 | -0.20142 | 0.091553 | -0.013733 | 122.937 | 122.7402 | 60.9512 | -123.0057 | 122.9187 | 122.8363 | 57.6187 | -123.143
2035.0156 | 123.0148 | -57.7423 | 65.1993 | -0.22141 | 0.01044 | 0.069319 | 0.073508 | 0.1295 | -0.0026405 | -0.0081455 | -0.30533 | -0.009126 | 0.062769 | 0.059962 | 0.0029266 | -0.011546 | 65.1352 | 65.2084 | 3.1311 | -57.9895 | 65.2908 | -57.7972 | -57.8934 | -57.3898 | -0.12817 | -57.9849 | 65.2496 | 65.1535 | -57.9437 | -57.9895 | -0.054931 | -0.15106 | 0.091553 | 122.9507 | -0.24719 | -0.09613 | -0.064087 | -0.20142 | -0.24719 | 0.050354 | 0.35248 | -0.24261 | 0.004578 | -0.045777 | 123.0331 | 122.8775 | 60.8734 | -123.0927 | 122.9919 | 122.8958 | 57.6141 | -123.1888
2036.0156 | 123.0377 | -57.8064 | 65.1077 | -0.25192 | 0.010653 | 0.067823 | 0.07009 | 0.13142 | -0.0019995 | -0.0070773 | -0.11459 | -0.0086988 | 0.060846 | 0.05633 | 0.0033538 | -0.0081284 | 64.9429 | 65.126 | 3.3737 | -57.9254 | 65.1535 | -57.8705 | -57.9391 | -57.4356 | -0.25635 | -58.0124 | 65.1443 | 65.0665 | -57.9941 | -58.0353 | -0.064087 | -0.13275 | 0.045776 | 122.9324 | -0.11902 | 0.013733 | -0.16479 | -0.18768 | -0.22888 | 0.036621 | 0.37079 | -0.20599 | 0.022888 | -0.041199 | 122.9599 | 122.7493 | 61.1801 | -123.0469 | 122.9507 | 122.8729 | 57.55 | -123.143
2037.0156 | 123.024 | -57.8751 | 65.0253 | 0.045624 | 0.013858 | 0.068464 | 0.071799 | 0.12864 | -0.00093145 | -0.0068637 | -0.18326 | -0.0067762 | 0.064478 | 0.059107 | 0.0037812 | -0.010051 | 64.8605 | 64.9887 | 3.2959 | -58.0399 | 65.1398 | -57.9254 | -58.017 | -57.5134 | 0.16937 | -58.1131 | 65.1215 | 65.0299 | -58.0719 | -58.0994 | -0.050354 | -0.14191 | 0.11444 | 122.8638 | -0.16479 | -0.022888 | -0.16479 | -0.19684 | -0.2243 | 0.09613 | 0.36163 | -0.23804 | -0.013733 | 0.004577 | 123.0148 | 122.7356 | 61.171 | -123.0423 | 122.9965 | 122.905 | 58.0444 | -123.1247
2038.0156 | 123.0881 | -57.8384 | 65.0574 | -0.21378 | 0.0074491 | 0.070387 | 0.069876 | 0.12864 | -0.0013587 | -0.0062229 | -0.11459 | -0.0089124 | 0.062342 | 0.057398 | 0.002713 | -0.010051 | 64.9292 | 65.1352 | 3.4973 | -57.9529 | 65.094 | -57.8796 | -57.9987 | -57.4265 | 0.35706 | -58.0124 | 65.0848 | 65.0162 | -58.0307 | -58.0994 | -0.041199 | -0.16022 | 0.036621 | 122.9736 | -0.11444 | 0.045776 | -0.12817 | -0.19226 | -0.26093 | 0.027466 | 0.41199 | -0.17395 | 0.086975 | -0.041199 | 122.9324 | 122.7676 | 61.3358 | -123.056 | 122.9233 | 122.8546 | 58.1955 | -123.1567
2039.0156 | 123.0103 | -57.6233 | 65.2817 | -0.25192 | 0.013003 | 0.069532 | 0.072653 | 0.13121 | -7.6852e-05 | -0.0043003 | -0.32822 | -0.0095532 | 0.063196 | 0.060816 | 0.0046356 | -0.0085556 | 65.0894 | 65.2496 | 3.3234 | -57.8247 | 65.3412 | -57.7057 | -57.7744 | -57.2754 | -0.009155 | -57.8888 | 65.3458 | 65.2359 | -57.8567 | -57.8934 | -0.082397 | -0.15106 | 0.05951 | 122.8729 | -0.20142 | -0.050354 | -0.19226 | -0.23346 | -0.27008 | 0.064087 | 0.3479 | -0.2655 | 0.004578 | -0.045776 | 122.9645 | 122.7127 | 60.9467 | -123.056 | 122.9691 | 122.8592 | 57.6141 | -123.175
2040.0156 | 123.2483 | -57.5409 | 65.3503 | 0.037994 | 0.0040311 | 0.069319 | 0.069449 | 0.12907 | -0.0056311 | -0.0075047 | -0.015411 | -0.010194 | 0.062128 | 0.055476 | 0.0020722 | -0.010905 | 65.2039 | 65.4419 | 3.1357 | -57.7011 | 65.3412 | -57.6233 | -57.7148 | -57.1198 | 0.15564 | -57.7011 | 65.3137 | 65.2313 | -57.7423 | -57.8293 | -0.082397 | -0.17395 | -0.009155 | 122.9828 | -0.16022 | 0.013733 | -0.14648 | -0.20142 | -0.28839 | -0.036621 | 0.42114 | -0.16022 | 0.12817 | -0.11902 | 122.8821 | 122.7448 | 60.6766 | -123.0652 | 122.8546 | 122.7722 | 57.6965 | -123.1796
2041.0156 | 122.9507 | -57.4814 | 65.4877 | -0.19852 | 0.011294 | 0.068464 | 0.070731 | 0.12928 | -0.0015723 | -0.0070773 | -0.15274 | -0.0069898 | 0.064691 | 0.056544 | 0.002713 | -0.011333 | 65.2542 | 65.4099 | 2.8839 | -57.6553 | 65.5243 | -57.55 | -57.6141 | -57.1152 | -0.27466 | -57.7194 | 65.506 | 65.3824 | -57.6782 | -57.7103 | -0.068665 | -0.13275 | 0.036621 | 122.8912 | -0.17395 | -0.041198 | -0.23346 | -0.19684 | -0.22888 | 0.01831 | 0.36621 | -0.23804 | -0.009155 | -0.10529 | 123.0057 | 122.7356 | 60.3653 | -123.1018 | 122.9874 | 122.8638 | 57.2067 | -123.1979
2042.0156 | 123.1338 | -57.3486 | 65.4831 | -0.168 | 0.0080899 | 0.068464 | 0.068381 | 0.13078 | -0.0047767 | -0.0053683 | 0.67886 | -0.0089124 | 0.06341 | 0.056758 | 0.0039948 | -0.010051 | 65.4053 | 65.9088 | 3.4424 | -57.3441 | 65.6342 | -57.4036 | -57.5317 | -56.955 | -0.17395 | -57.5272 | 65.5426 | 65.4327 | -57.5638 | -57.6096 | -0.054931 | -0.1831 | 0.15106 | 123.2574 | 0.004578 | 0.18768 | -0.07782 | -0.21515 | -0.26093 | 0.05951 | 0.39368 | -0.17853 | 0.082397 | -0.050354 | 122.9828 | 122.7539 | 60.791 | -123.0148 | 122.8912 | 122.7814 | 57.1747 | -123.0927
2043.0156 | 123.0377 | -57.399 | 65.5243 | -0.21378 | 0.011294 | 0.068464 | 0.071585 | 0.13057 | -0.00071785 | -0.0070773 | 0.27451 | -0.0089124 | 0.062555 | 0.058467 | 0.004422 | -0.01176 | 65.3412 | 65.6799 | 3.3325 | -57.5043 | 65.657 | -57.4173 | -57.5317 | -57.0099 | -0.39825 | -57.6187 | 65.6021 | 65.5014 | -57.5867 | -57.6233 | -0.01831 | -0.13275 | 0.13275 | 123.0789 | -0.10529 | 0.027466 | -0.1831 | -0.18768 | -0.2243 | 0.07782 | 0.3891 | -0.21973 | 0.004578 | -0.022888 | 123.056 | 122.7402 | 60.7315 | -123.056 | 123.0011 | 122.9004 | 57.0007 | -123.1476
2044.0156 | 123.1064 | -57.3578 | 65.5106 | -0.14511 | 0.0076627 | 0.069319 | 0.069449 | 0.13057 | -0.0024269 | -0.0060093 | -0.099335 | -0.010621 | 0.064264 | 0.057185 | 0.0031402 | -0.011333 | 65.4053 | 65.6296 | 3.154 | -57.4768 | 65.5746 | -57.4036 | -57.5043 | -56.8909 | -0.21057 | -57.518 | 65.538 | 65.4739 | -57.5455 | -57.5867 | -0.045776 | -0.14648 | 0.064087 | 122.9874 | -0.11902 | 0.027465 | -0.10529 | -0.18768 | -0.22888 | 0.027466 | 0.46692 | -0.16022 | 0.068665 | -0.036621 | 122.9324 | 122.7631 | 60.5118 | -123.0148 | 122.8958 | 122.8317 | 57.1472 | -123.0972
2045.0156 | 123.0057 | -57.3669 | 65.5426 | -0.17563 | 0.0095853 | 0.068037 | 0.071158 | 0.12971 | 0.00099115 | -0.0083591 | -0.16037 | -0.010408 | 0.062982 | 0.059962 | 0.0048492 | -0.0091966 | 65.3503 | 65.5243 | 3.067 | -57.5455 | 65.6525 | -57.4448 | -57.518 | -56.9916 | -0.29755 | -57.5729 | 65.6158 | 65.5563 | -57.5272 | -57.5821 | -0.07782 | -0.15106 | 0.10986 | 122.8912 | -0.17853 | -0.027466 | -0.19226 | -0.16022 | -0.21515 | 0.073242 | 0.37537 | -0.20599 | 0.009155 | 0.013732 | 123.0194 | 122.7173 | 60.434 | -123.0606 | 122.9828 | 122.9233 | 57.0694 | -123.1247
2046.0156 | 123.1476 | -57.2845 | 65.538 | -0.10696 | 0.0089443 | 0.070173 | 0.067954 | 0.12993 | -0.0026405 | -0.0066501 | -0.045929 | -0.0099806 | 0.06106 | 0.055903 | 0.0012176 | -0.0096238 | 65.4922 | 65.6891 | 3.1998 | -57.431 | 65.6387 | -57.3303 | -57.431 | -56.813 | -0.18768 | -57.431 | 65.6067 | 65.5151 | -57.4539 | -57.55 | -0.045776 | -0.14648 | 0.10071 | 122.9736 | -0.14648 | 0 | -0.045776 | -0.16937 | -0.2655 | 0.068664 | 0.4715 | -0.14648 | 0.11902 | -0.022888 | 122.9233 | 122.7768 | 60.4843 | -122.9691 | 122.8912 | 122.7997 | 57.0969 | -123.0881
2047.0156 | 123.0881 | -57.5775 | 65.2954 | -0.18326 | 0.0074491 | 0.072309 | 0.07244 | 0.12843 | -0.00071785 | -0.0068637 | -0.12222 | -0.0084852 | 0.061701 | 0.057185 | 0.0037812 | -0.010265 | 65.1947 | 65.4007 | 3.2455 | -57.6828 | 65.3549 | -57.6141 | -57.7057 | -57.1747 | 0.013733 | -57.7789 | 65.3641 | 65.2451 | -57.7972 | -57.8018 | -0.036621 | -0.12817 | 0.059509 | 122.9782 | -0.10529 | 0.022888 | -0.10071 | -0.21973 | -0.2243 | 0.068665 | 0.40283 | -0.20142 | 0.022888 | -0.050354 | 122.9324 | 122.7722 | 60.8231 | -123.0011 | 122.9416 | 122.8226 | 57.5912 | -123.0972
2048.0156 | 123.1522 | -57.3486 | 65.5243 | -0.13748 | 0.0063809 | 0.070173 | 0.069235 | 0.12779 | -0.0019995 | -0.0051547 | -3.3418 | -0.012117 | 0.065973 | 0.059535 | 0.0020722 | -0.0096238 | 65.4831 | 65.7074 | 3.3325 | -57.4265 | 65.6616 | -57.3853 | -57.431 | -56.8176 | -0.27924 | -57.4997 | 65.5334 | 65.4465 | -57.5226 | -57.5867 | -0.036621 | -0.082397 | 0.13733 | 123.056 | -0.07782 | 0.004577 | -0.041199 | -0.17395 | -0.23804 | 0.009155 | 0.53101 | -0.15106 | 0.086975 | -0.07782 | 123.0103 | 122.8317 | 60.6812 | -122.9553 | 122.8821 | 122.7951 | 57.0694 | -123.111
2049.0312 | 123.0835 | -57.3624 | 65.4831 | 0.18295 | 0.01279 | 0.067182 | 0.070944 | 0.12928 | 0.0016321 | -0.0038731 | 0.19821 | -0.0052808 | 0.062555 | 0.057612 | 0.0076264 | -0.01176 | 65.3824 | 65.5197 | 3.3463 | -57.5455 | 65.6113 | -57.4448 | -57.5089 | -56.9229 | -0.2655 | -57.5821 | 65.5838 | 65.4465 | -57.5592 | -57.5958 | -0.082397 | -0.14648 | 0.12817 | 122.8821 | -0.1831 | -0.036621 | -0.10071 | -0.19684 | -0.23346 | 0.10071 | 0.43945 | -0.21973 | 0.013733 | -0.036621 | 122.9736 | 122.7448 | 60.7086 | -122.9919 | 122.9462 | 122.8088 | 57.0969 | -123.0789
2050.0156 | 123.0927 | -57.3166 | 65.5472 | -0.43503 | 0.0053129 | 0.066969 | 0.070731 | 0.128 | -0.0015723 | -0.0051547 | -0.053558 | -0.0095532 | 0.062769 | 0.056758 | 0.001004 | -0.011974 | 65.4648 | 65.6616 | 3.4653 | -57.4402 | 65.6342 | -57.3578 | -57.4814 | -56.8451 | -0.068665 | -57.4768 | 65.6021 | 65.4877 | -57.4768 | -57.5272 | -0.041199 | -0.16479 | 0.086975 | 122.9782 | -0.1236 | 0.041198 | -0.082397 | -0.16022 | -0.21057 | 0.054932 | 0.4715 | -0.16022 | 0.050354 | -0.059509 | 122.9507 | 122.7814 | 60.7819 | -123.0286 | 122.9187 | 122.8043 | 57.2479 | -123.0743
2051.0156 | 122.9553 | -57.4951 | 65.4053 | -0.29007 | 0.0093717 | 0.068464 | 0.071372 | 0.13057 | -0.0015723 | -0.0075047 | -0.15274 | -0.0082716 | 0.063196 | 0.057612 | 0.0048492 | -0.0096238 | 65.2908 | 65.4739 | 3.4424 | -57.6096 | 65.5838 | -57.518 | -57.6233 | -57.1335 | 0.10071 | -57.7652 | 65.4877 | 65.3824 | -57.6874 | -57.724 | -0.022888 | -0.12817 | 0.17853 | 122.9691 | -0.11444 | 0.013733 | -0.11444 | -0.19226 | -0.22888 | 0.082398 | 0.36163 | -0.27008 | -0.041199 | -0.022888 | 123.0789 | 122.786 | 60.9375 | -123.0286 | 122.9828 | 122.8775 | 57.5958 | -123.1293
2052.0156 | 123.1201 | -57.2937 | 65.5655 | -0.168 | 0.0085171 | 0.069959 | 0.076498 | 0.13078 | 0.0014185 | -0.0040867 | -0.19089 | -0.010194 | 0.059564 | 0.055262 | 0.0046356 | -0.011974 | 65.2725 | 65.7486 | 3.6758 | -57.4905 | 65.6158 | -57.3624 | -57.4356 | -56.868 | 0.48981 | -57.4539 | 65.5655 | 65.5289 | -57.4814 | -57.518 | -0.068665 | -0.14191 | 0.050354 | 123.0423 | -0.19684 | -0.054932 | -0.29297 | -0.18768 | -0.2243 | 0 | 0.42572 | -0.16022 | 0.064087 | -0.036621 | 122.9095 | 122.5662 | 60.9695 | -123.0011 | 122.8592 | 122.8226 | 57.7835 | -123.0835
2053.0156 | 123.0606 | -57.2937 | 65.5975 | -0.19852 | 0.011294 | 0.067823 | 0.073294 | 0.12864 | -0.0015723 | -0.0062229 | -0.12985 | -0.0099806 | 0.062555 | 0.056971 | 0.0059174 | -0.0096238 | 65.4877 | 65.6891 | 3.566 | -57.431 | 65.6387 | -57.3349 | -57.4402 | -56.8909 | -0.14191 | -57.4814 | 65.6525 | 65.5472 | -57.486 | -57.55 | -0.041199 | -0.14648 | 0.041199 | 122.9828 | -0.13733 | 0.009156 | -0.10986 | -0.19226 | -0.25635 | 0.054932 | 0.40283 | -0.18768 | 0.068665 | -0.050354 | 122.9324 | 122.7814 | 60.8597 | -123.0377 | 122.9462 | 122.8409 | 57.1518 | -123.1476
2054.0156 | 123.024 | -57.3624 | 65.5655 | -0.98434 | 0.018558 | 0.068037 | 0.070303 | 0.13078 | 0.0048363 | -0.0038731 | -0.068817 | -0.0044264 | 0.06341 | 0.058253 | 0.0048492 | -0.011546 | 65.4831 | 65.5975 | 3.6118 | -57.4631 | 65.6616 | -57.3898 | -57.4905 | -56.9229 | 0.036621 | -57.5638 | 65.6342 | 65.5609 | -57.518 | -57.5409 | -0.027466 | -0.12817 | 0.09613 | 122.9599 | -0.10071 | 0.027466 | -0.082398 | -0.15564 | -0.17853 | 0.068664 | 0.43945 | -0.20142 | -0.022888 | -0.004578 | 123.024 | 122.8455 | 60.9741 | -123.056 | 122.9965 | 122.9233 | 57.399 | -123.1064
2055.0156 | 123.0057 | -57.7103 | 65.2405 | -0.22141 | 0.0083035 | 0.068891 | 0.072012 | 0.13228 | -0.0019995 | -0.0057957 | -0.17563 | -0.0086988 | 0.063623 | 0.059321 | 0.0024994 | -0.012187 | 65.0803 | 65.2679 | 3.4103 | -57.8201 | 65.3046 | -57.7148 | -57.8339 | -57.2983 | 0.1236 | -57.9071 | 65.2588 | 65.1718 | -57.8705 | -57.9163 | -0.004578 | -0.1236 | 0.064086 | 122.9782 | -0.10986 | 0.013733 | -0.16022 | -0.16022 | -0.20599 | 0.01831 | 0.41199 | -0.19684 | 0.009156 | -0.068665 | 123.0148 | 122.7905 | 61.1206 | -123.0743 | 122.9691 | 122.8821 | 57.8339 | -123.1567
2056.0156 | 123.1018 | -57.4448 | 65.419 | -0.32059 | 0.0068081 | 0.068037 | 0.06539 | 0.12907 | -0.0019995 | -0.0038731 | -0.076446 | -0.0089124 | 0.062342 | 0.057612 | 0.0046356 | -0.0094102 | 65.3183 | 65.538 | 3.3325 | -57.5729 | 65.5151 | -57.4997 | -57.5775 | -57.0419 | 0.35248 | -57.6096 | 65.451 | 65.3824 | -57.637 | -57.6874 | -0.054932 | -0.13275 | 0.096131 | 122.9828 | -0.12817 | 0.004578 | -0.10071 | -0.19226 | -0.24262 | 0.032044 | 0.40283 | -0.16479 | 0.07782 | -0.036621 | 122.9599 | 122.7631 | 60.7773 | -122.9965 | 122.8958 | 122.8271 | 57.7972 | -123.1064
2057.0156 | 123.0057 | -57.6279 | 65.3275 | -0.168 | 0.0093717 | 0.069532 | 0.070731 | 0.13057 | -0.0024269 | -0.0081455 | -0.21378 | -0.0069898 | 0.064051 | 0.056544 | 0.001004 | -0.0087692 | 65.1306 | 65.2908 | 2.98 | -57.7881 | 65.4236 | -57.6599 | -57.7332 | -57.1518 | -0.41657 | -57.8979 | 65.3687 | 65.2725 | -57.811 | -57.8522 | -0.032043 | -0.10529 | 0.09613 | 122.9187 | -0.16022 | -0.054932 | -0.19684 | -0.18311 | -0.2243 | 0.041198 | 0.47607 | -0.27008 | -0.045776 | -0.054932 | 123.0515 | 122.7585 | 60.6079 | -123.0606 | 122.9965 | 122.9004 | 57.2113 | -123.1796
2058.0156 | 123.1064 | -57.4768 | 65.3412 | -0.25955 | 0.0055265 | 0.069746 | 0.068808 | 0.12886 | -0.0034949 | -0.0070773 | -0.061188 | -0.011262 | 0.060633 | 0.056971 | 0.0050628 | -0.010478 | 65.2588 | 65.4373 | 2.9938 | -57.6187 | 65.4373 | -57.5867 | -57.6508 | -57.0786 | -0.15106 | -57.6462 | 65.3961 | 65.3137 | -57.6965 | -57.7377 | -0.10986 | -0.17395 | 0.09613 | 122.9141 | -0.14191 | 0.032044 | -0.082398 | -0.21973 | -0.26093 | 0.054931 | 0.39825 | -0.16937 | 0.091553 | -0.027466 | 122.9141 | 122.7356 | 60.4706 | -122.9919 | 122.8729 | 122.7905 | 57.3257 | -123.0789
2059.0156 | 122.9965 | -57.6324 | 65.3229 | 0.099029 | 0.01813 | 0.066755 | 0.074149 | 0.13099 | 0.0048363 | -0.0049411 | -0.023041 | -0.0076306 | 0.065546 | 0.058253 | 0.006131 | -0.011119 | 65.1352 | 65.2542 | 3.0853 | -57.7652 | 65.4053 | -57.6462 | -57.7606 | -57.2433 | -0.45776 | -57.8934 | 65.3503 | 65.2451 | -57.8293 | -57.8751 | -0.013733 | -0.12817 | 0.082397 | 122.8867 | -0.13275 | -0.004578 | -0.18768 | -0.19684 | -0.24262 | 0.027466 | 0.3891 | -0.26093 | -0.018311 | -0.07782 | 123.0377 | 122.7676 | 60.7178 | -123.0835 | 122.9828 | 122.8775 | 57.1747 | -123.1979
2060.0156 | 123.1796 | -57.6553 | 65.1535 | -0.061188 | 0.0070217 | 0.069105 | 0.069663 | 0.1295 | -0.0047767 | -0.0068637 | -0.12985 | -0.010621 | 0.059778 | 0.059107 | 0.0022858 | -0.01176 | 65.0665 | 65.2817 | 3.1906 | -57.8476 | 65.2451 | -57.7515 | -57.8476 | -57.2296 | -0.10986 | -57.8018 | 65.181 | 65.1031 | -57.8842 | -57.9254 | -0.096131 | -0.19226 | 0.091553 | 122.937 | -0.19226 | 0 | -0.086975 | -0.22888 | -0.27008 | 0.027466 | 0.42572 | -0.14648 | 0.1236 | -0.050354 | 122.9004 | 122.7219 | 60.8459 | -123.0011 | 122.8363 | 122.7585 | 57.5455 | -123.0789
2061.0156 | 123.0789 | -57.637 | 65.213 | -0.16037 | 0.010226 | 0.06761 | 0.072226 | 0.1295 | -0.0045631 | -0.0064365 | -0.12222 | -0.010408 | 0.061701 | 0.056117 | 0.0039948 | -0.010692 | 65.126 | 65.3229 | 3.1174 | -57.7698 | 65.2817 | -57.7057 | -57.7744 | -57.2388 | -0.36621 | -57.8201 | 65.2817 | 65.1764 | -57.8247 | -57.9025 | -0.068664 | -0.13733 | 0.068664 | 122.9599 | -0.13275 | 0.004578 | -0.086975 | -0.18768 | -0.2655 | 0.068664 | 0.39825 | -0.18311 | 0.082398 | -0.036621 | 122.9187 | 122.7631 | 60.7544 | -122.9874 | 122.9187 | 122.8134 | 57.2708 | -123.1155
2062.0156 | 123.0972 | -57.8018 | 65.0345 | -0.19089 | 0.0046719 | 0.071241 | 0.070517 | 0.12907 | -0.0041357 | -0.0066501 | -0.053558 | -0.011903 | 0.058283 | 0.05398 | 0.0042084 | -0.008342 | 64.9841 | 65.2222 | 2.5314 | -57.9254 | 65.1489 | -57.8567 | -57.962 | -57.5684 | -0.27924 | -57.9254 | 65.0803 | 64.9704 | -58.0124 | -58.0673 | -0.054931 | -0.16022 | 0.11444 | 123.024 | -0.1236 | 0.036621 | -0.050354 | -0.21057 | -0.2655 | 0.045776 | 0.23346 | -0.1236 | 0.14191 | -0.064087 | 122.9507 | 122.786 | 60.3333 | -122.9965 | 122.8821 | 122.7722 | 57.5226 | -123.1018
2063.0156 | 122.9919 | -57.8156 | 65.0757 | -0.26718 | 0.0095853 | 0.070387 | 0.070517 | 0.13099 | 0.00035035 | -0.0062229 | -0.168 | -0.0093396 | 0.062769 | 0.057612 | 0.0042084 | -0.0091966 | 64.92 | 65.0803 | 2.6093 | -57.9758 | 65.1855 | -57.8888 | -57.962 | -57.5409 | -0.50812 | -58.0307 | 65.1672 | 65.0574 | -58.0215 | -58.0582 | -0.073242 | -0.14648 | 0.10986 | 122.8958 | -0.16022 | -0.013733 | -0.15564 | -0.20599 | -0.24262 | 0.091552 | 0.27466 | -0.21515 | 0.027466 | -0.018311 | 123.0011 | 122.7356 | 60.4248 | -123.0377 | 122.9828 | 122.8729 | 57.3074 | -123.1339
2064.0156 | 123.024 | -57.93 | 65.0116 | -0.045929 | 0.016208 | 0.068891 | 0.07009 | 0.12822 | 0.0046227 | -0.0043003 | -0.00015237 | -0.0061352 | 0.064264 | 0.05868 | 0.0057038 | -0.012614 | 64.9063 | 65.0208 | 3.0029 | -58.0673 | 65.094 | -57.9666 | -58.0353 | -57.5134 | -0.40283 | -58.1543 | 65.0757 | 64.9521 | -58.0902 | -58.1497 | -0.036621 | -0.10528 | 0.082397 | 122.9507 | -0.13733 | -0.032044 | -0.10529 | -0.16022 | -0.21973 | 0.064087 | 0.41657 | -0.2243 | -0.004578 | -0.05951 | 123.024 | 122.8363 | 60.9329 | -123.0469 | 123.0057 | 122.8821 | 57.5272 | -123.1613
2065.0156 | 123.0377 | -55.3391 | 67.5934 | -0.23666 | 0.0097989 | 0.069105 | 0.070731 | 0.13249 | -0.0032813 | -0.0079319 | -0.12985 | -0.008058 | 0.061273 | 0.059748 | 0.0022858 | -0.0087692 | 67.4194 | 67.5568 | 3.717 | -55.5038 | 67.6758 | -55.3848 | -55.481 | -54.982 | 0.33417 | -55.5313 | 67.6666 | 67.5751 | -55.5313 | -55.5588 | -0.045777 | -0.14191 | 0.082397 | 122.8958 | -0.16479 | -0.022888 | -0.17395 | -0.19226 | -0.21973 | 0.073242 | 0.35706 | -0.19226 | 0.027466 | -0.018311 | 123.0148 | 122.7585 | 59.0561 | -123.0743 | 123.0057 | 122.9141 | 55.6732 | -123.1522
2066.0156 | 123.1613 | -54.2587 | 68.6142 | -0.168 | 0.0093717 | 0.068891 | 0.069663 | 0.13014 | -0.0032813 | -0.0055821 | -2.8688 | -0.010621 | 0.061914 | 0.058894 | 0.0035674 | -0.010265 | 68.5364 | 68.7332 | 4.2618 | -54.3961 | 68.692 | -54.2953 | -54.4144 | -53.7689 | 0.9201 | -54.3915 | 68.6325 | 68.5455 | -54.451 | -54.5013 | -0.036621 | -0.15564 | 0.07782 | 122.9919 | -0.13733 | 0.018311 | -0.07782 | -0.19226 | -0.24262 | 0.01831 | 0.48981 | -0.13275 | 0.10986 | -0.068665 | 122.9507 | 122.7951 | 58.5205 | -123.0286 | 122.8912 | 122.8043 | 55.1788 | -123.1155
2067.0156 | 123.0881 | -54.1397 | 68.7149 | -0.015411 | 0.0078763 | 0.070387 | 0.069663 | 0.12843 | -0.0041357 | -0.0060093 | -0.084076 | -0.011049 | 0.063837 | 0.05633 | 0.002713 | -0.011119 | 68.6142 | 68.8248 | 4.4037 | -54.2908 | 68.7973 | -54.213 | -54.2999 | -53.7781 | 1.268 | -54.2816 | 68.7927 | 68.6554 | -54.3228 | -54.4098 | -0.073243 | -0.16022 | 0.082397 | 122.9645 | -0.15106 | 0.009156 | -0.10071 | -0.18311 | -0.27008 | 0.07782 | 0.36163 | -0.14191 | 0.12817 | -0.059509 | 122.937 | 122.7539 | 58.5434 | -123.0148 | 122.9324 | 122.7951 | 55.4077 | -123.1247
2068.0156 | 123.1338 | -53.4073 | 69.4336 | -0.015411 | 0.0057401 | 0.06825 | 0.070303 | 0.12629 | -0.0049903 | -0.0066501 | 0.015106 | -0.0086988 | 0.060419 | 0.058467 | 0.0031402 | -0.0098374 | 69.3146 | 69.5023 | 4.6326 | -53.5812 | 69.516 | -53.4805 | -53.5675 | -53.0273 | 1.4786 | -53.5172 | 69.4748 | 69.3878 | -53.6133 | -53.6499 | -0.073242 | -0.16022 | 0.082397 | 122.9095 | -0.17395 | -0.013733 | -0.11902 | -0.20599 | -0.24261 | 0.041198 | 0.37994 | -0.10986 | 0.13275 | -0.045777 | 122.9233 | 122.7219 | 58.0399 | -123.0011 | 122.8821 | 122.7951 | 54.8859 | -123.0835
2069.0156 | 122.9874 | -53.0365 | 69.8959 | 0.053253 | 0.017917 | 0.069105 | 0.072867 | 0.12928 | 0.0052637 | -0.0038731 | 0.10666 | -0.0065626 | 0.064691 | 0.059748 | 0.0084808 | -0.013469 | 69.6625 | 69.7586 | 4.715 | -53.2379 | 69.9875 | -53.1326 | -53.1876 | -52.7252 | 1.3046 | -53.302 | 69.9509 | 69.7723 | -53.2425 | -53.3112 | -0.09613 | -0.15106 | 0.091553 | 122.7951 | -0.20142 | -0.050354 | -0.23346 | -0.20599 | -0.27466 | 0.054932 | 0.31128 | -0.2655 | 0.009155 | -0.1236 | 123.024 | 122.699 | 57.7515 | -123.0835 | 122.9874 | 122.8088 | 54.3411 | -123.2071
2070.0156 | 123.0835 | -52.8442 | 69.9829 | -0.14511 | 0.0080899 | 0.068037 | 0.070944 | 0.12886 | -0.0047767 | -0.0057957 | -0.045929 | -0.009126 | 0.060846 | 0.055903 | 0.0039948 | -0.010265 | 69.9142 | 70.1477 | 4.5731 | -53.009 | 70.0562 | -52.9358 | -52.9999 | -52.4414 | 1.6296 | -52.9999 | 70.015 | 69.9875 | -53.0457 | -53.0869 | -0.091553 | -0.15564 | 0.073242 | 122.9919 | -0.1648 | -0.009155 | -0.068664 | -0.20142 | -0.24262 | 0.032044 | 0.40283 | -0.15564 | 0.086975 | 0.004578 | 122.9004 | 122.7585 | 57.4173 | -122.9828 | 122.8592 | 122.8317 | 54.4739 | -123.0698
2071.0156 | 123.056 | -52.6108 | 70.3125 | -0.21378 | 0.010013 | 0.0706 | 0.069663 | 0.13121 | -0.0015723 | -0.0047275 | -0.15274 | -0.007417 | 0.061701 | 0.059535 | 0.0065582 | -0.012401 | 70.0882 | 70.3033 | 4.2892 | -52.7847 | 70.2942 | -52.7252 | -52.7939 | -52.2903 | 1.2955 | -52.8442 | 70.3262 | 70.2164 | -52.8259 | -52.858 | -0.11444 | -0.1831 | -0.018311 | 122.9141 | -0.17395 | 0.009155 | -0.2243 | -0.21515 | -0.24719 | 0.013733 | 0.32044 | -0.23346 | 0.013733 | -0.09613 | 122.905 | 122.699 | 56.9 | -123.1064 | 122.937 | 122.8271 | 53.9062 | -123.1705
2072.0156 | 123.1293 | -52.4551 | 70.3583 | -0.045929 | 0.0063809 | 0.068037 | 0.070303 | 0.12864 | -0.0045631 | -0.0051547 | 0.053253 | -0.010835 | 0.062342 | 0.058039 | 0.00549 | -0.0079148 | 70.2759 | 70.4956 | 4.6234 | -52.6382 | 70.459 | -52.533 | -52.6291 | -52.0569 | 1.8539 | -52.565 | 70.4132 | 70.3583 | -52.6337 | -52.6886 | -0.07782 | -0.17395 | 0.10071 | 122.9507 | -0.18311 | -0.009156 | -0.082397 | -0.17853 | -0.23346 | 0.054932 | 0.39825 | -0.10986 | 0.1236 | 0 | 122.9141 | 122.731 | 57.0786 | -122.9874 | 122.8683 | 122.8134 | 54.3091 | -123.0469
2073.0156 | 123.111 | -52.4963 | 70.3354 | 0.62546 | 0.0074491 | 0.071668 | 0.071799 | 0.12886 | -0.0013587 | -0.0055821 | -0.12222 | -0.0095532 | 0.061914 | 0.057398 | 0.00549 | -0.011119 | 70.4041 | 70.5872 | 4.6005 | -52.5558 | 70.5231 | -52.4231 | -52.5467 | -52.0111 | 1.8036 | -52.6199 | 70.5093 | 70.3674 | -52.6474 | -52.7069 | 0.073242 | -0.050354 | 0.18768 | 123.0835 | -0.059509 | -0.009155 | 0.068665 | -0.15106 | -0.21057 | 0.17395 | 0.48523 | -0.1236 | 0.086975 | 0.032044 | 123.0194 | 122.9004 | 57.0969 | -122.8821 | 123.0057 | 122.8638 | 54.2999 | -123.0423
2074.0156 | 123.0927 | -52.121 | 70.7611 | -0.00015269 | 0.0061673 | 0.071241 | 0.069449 | 0.13142 | -0.0015723 | -0.0057957 | 0.060883 | -0.012758 | 0.059778 | 0.059748 | 0.0050628 | -0.011119 | 70.5688 | 70.7428 | 4.7012 | -52.3041 | 70.8298 | -52.1667 | -52.2766 | -51.7227 | 1.4557 | -52.2125 | 70.8206 | 70.7336 | -52.2812 | -52.3087 | -0.045776 | -0.15564 | 0.068665 | 122.8638 | -0.1831 | -0.027466 | -0.19226 | -0.16022 | -0.18768 | 0.05951 | 0.39825 | -0.091552 | 0.096131 | -0.027465 | 122.9507 | 122.6898 | 56.8222 | -123.0377 | 122.9416 | 122.8546 | 53.5767 | -123.0698
2075.0156 | 123.1247 | -51.5488 | 71.347 | 0.022736 | 0.0083035 | 0.068891 | 0.072226 | 0.12886 | -0.0017859 | -0.0072911 | 0.037995 | -0.0086988 | 0.060419 | 0.056544 | 0.00549 | -0.01176 | 71.2738 | 71.3974 | 4.834 | -51.7227 | 71.402 | -51.6129 | -51.7136 | -51.1551 | 1.6251 | -51.7227 | 71.315 | 71.2372 | -51.7502 | -51.8005 | -0.064087 | -0.1648 | 0.054932 | 122.9462 | -0.17395 | -0.009155 | -0.073242 | -0.20142 | -0.25177 | -0.032044 | 0.39368 | -0.17395 | 0.07782 | -0.10986 | 122.9507 | 122.8226 | 56.3828 | -123.0606 | 122.8638 | 122.7859 | 53.1738 | -123.1476
2076.0156 | 123.1247 | -51.4709 | 71.3791 | 0.037994 | 0.0044583 | 0.070387 | 0.070731 | 0.12886 | -0.0019995 | -0.0064365 | 0.33554 | -0.011049 | 0.060633 | 0.056971 | 0.0052764 | -0.0089828 | 71.3104 | 71.489 | 5.2048 | -51.4938 | 71.553 | -51.4343 | -51.5442 | -51.091 | 1.6663 | -51.5991 | 71.5073 | 71.3837 | -51.6312 | -51.7136 | 0.036621 | -0.073242 | 0.17395 | 122.9599 | -0.022888 | 0.050354 | -0.068664 | -0.16022 | -0.24262 | 0.12817 | 0.37994 | -0.12817 | 0.11444 | 0.004578 | 123.024 | 122.7814 | 56.6757 | -122.9233 | 122.9782 | 122.8546 | 53.1372 | -123.0927
2077.0156 | 123.0927 | -51.4023 | 71.4615 | -0.14511 | 0.0068081 | 0.066541 | 0.072653 | 0.12758 | -7.6852e-05 | -0.0075047 | -0.12985 | -0.011689 | 0.059778 | 0.058467 | 0.010617 | -0.010265 | 71.4249 | 71.6263 | 5.2094 | -51.5167 | 71.5347 | -51.4709 | -51.5533 | -51.0818 | 2.124 | -51.5121 | 71.5027 | 71.4157 | -51.5579 | -51.6266 | -0.068664 | -0.15106 | 0.073242 | 123.0286 | -0.11444 | 0.036621 | -0.036621 | -0.15564 | -0.2243 | 0.041199 | 0.32043 | -0.10986 | 0.11444 | -0.045777 | 122.937 | 122.8271 | 56.6116 | -123.0148 | 122.905 | 122.818 | 53.5263 | -123.0881
2078.0156 | 123.0881 | -51.2558 | 71.608 | -0.0077822 | 0.0065945 | 0.06825 | 0.069022 | 0.12993 | -0.0028541 | -0.0068637 | 0.0914 | -0.011049 | 0.059351 | 0.056971 | 0.0063446 | -0.0096238 | 71.2601 | 71.5897 | 5.0262 | -51.5533 | 71.6492 | -51.3794 | -51.5076 | -50.8804 | 2.2842 | -51.3977 | 71.6629 | 71.5805 | -51.4709 | -51.503 | -0.1236 | -0.25177 | 0.041199 | 122.8455 | -0.29755 | -0.045777 | -0.3479 | -0.21515 | -0.24719 | 0.054932 | 0.37537 | -0.14191 | 0.10529 | -0.027466 | 122.905 | 122.5159 | 56.282 | -123.1155 | 122.9187 | 122.8363 | 53.54 | -123.111
2079.0156 | 123.111 | -51.2421 | 71.5897 | -0.053558 | 0.0083035 | 0.069746 | 0.070517 | 0.12779 | -0.0019995 | -0.0064365 | 0.030365 | -0.0099806 | 0.061701 | 0.057612 | 0.0048492 | -0.010692 | 71.4066 | 71.5851 | 5.0537 | -51.4938 | 71.5805 | -51.3794 | -51.503 | -50.8347 | 2.4124 | -51.3794 | 71.64 | 71.5439 | -51.4526 | -51.5121 | -0.13733 | -0.26093 | -0.009156 | 122.8271 | -0.25177 | 0.009156 | -0.18311 | -0.21057 | -0.27008 | 0.050354 | 0.40741 | -0.13733 | 0.13275 | -0.045777 | 122.8226 | 122.6486 | 56.2958 | -123.0927 | 122.8821 | 122.7859 | 53.6545 | -123.1018
2080.0156 | 123.0652 | -51.7044 | 71.1227 | 0.16006 | 0.0095853 | 0.067396 | 0.071158 | 0.128 | 0.00035035 | -0.0053683 | 0.15244 | -0.0076306 | 0.059564 | 0.05633 | 0.0059174 | -0.010692 | 70.9213 | 71.0815 | 5.0125 | -51.9882 | 71.1365 | -51.8555 | -51.9608 | -51.3245 | 2.0828 | -51.796 | 71.1914 | 71.0953 | -51.8921 | -51.9562 | -0.15106 | -0.25635 | 0.013733 | 122.7859 | -0.28381 | -0.027466 | -0.20142 | -0.18768 | -0.25177 | 0.068664 | 0.37994 | -0.091552 | 0.16022 | -0.027466 | 122.8409 | 122.6257 | 56.7169 | -123.0835 | 122.8958 | 122.7997 | 53.7872 | -123.0789
2081.0156 | 123.0972 | -51.1368 | 71.7316 | 0.053253 | 0.0055265 | 0.071027 | 0.069022 | 0.12886 | -0.0015723 | -0.0047275 | 0.09903 | -0.0097668 | 0.059564 | 0.057826 | 0.0067718 | -0.0091966 | 71.6904 | 71.846 | 5.1132 | -51.2238 | 71.8826 | -51.1002 | -51.1917 | -50.8026 | 2.0462 | -51.3016 | 71.7819 | 71.6812 | -51.329 | -51.3886 | 0.036621 | -0.054931 | 0.15106 | 122.9828 | -0.086975 | -0.032044 | -0.041198 | -0.19226 | -0.25177 | 0.050354 | 0.33417 | -0.16479 | 0.086975 | -0.050354 | 123.0194 | 122.8271 | 56.25 | -122.9233 | 122.9187 | 122.818 | 53.183 | -123.1201
2082.0156 | 123.1201 | -51.4206 | 71.4111 | 0.11429 | 0.010653 | 0.06825 | 0.069235 | 0.1295 | 0.0027001 | -0.0055821 | 0.19058 | -0.0076306 | 0.064905 | 0.057612 | 0.00549 | -0.012828 | 71.402 | 71.5439 | 4.8935 | -51.5533 | 71.5439 | -51.4435 | -51.5396 | -50.972 | 1.8997 | -51.4847 | 71.553 | 71.4294 | -51.5396 | -51.6129 | -0.022888 | -0.11902 | 0.13275 | 122.9645 | -0.13275 | -0.013733 | -0.009155 | -0.11902 | -0.19226 | 0.14191 | 0.44861 | -0.064087 | 0.12817 | 0.01831 | 122.9645 | 122.8226 | 56.3141 | -122.9507 | 122.9736 | 122.85 | 53.3203 | -123.024
2083.0156 | 123.1155 | -51.4938 | 71.3058 | 0.022736 | 0.0076627 | 0.068891 | 0.069022 | 0.12971 | -0.0022131 | -0.0079319 | -0.00015237 | -0.0097668 | 0.059778 | 0.057185 | 0.00549 | -0.0098374 | 71.196 | 71.3745 | 5.1773 | -51.7364 | 71.402 | -51.6174 | -51.7364 | -51.1551 | 2.1698 | -51.5991 | 71.4066 | 71.315 | -51.7044 | -51.7502 | -0.1236 | -0.24262 | 0.096131 | 122.8683 | -0.24262 | 0 | -0.10986 | -0.21057 | -0.25635 | 0.10071 | 0.33874 | -0.10529 | 0.15106 | 0.009155 | 122.8958 | 122.6898 | 56.6711 | -123.0423 | 122.9004 | 122.8088 | 53.6636 | -123.056
2084.0156 | 123.0927 | -51.8143 | 71.022 | 0.16006 | 0.0097989 | 0.066969 | 0.071372 | 0.12928 | -7.6852e-05 | -0.0047275 | 0.23636 | -0.010835 | 0.064905 | 0.055689 | 0.0069854 | -0.010051 | 71.0861 | 71.2509 | 4.9255 | -51.8921 | 71.2418 | -51.7868 | -51.8555 | -51.4893 | 2.037 | -51.9516 | 71.0541 | 70.9534 | -52.0386 | -52.0798 | 0.027466 | -0.041199 | 0.21973 | 123.0652 | -0.07782 | -0.036621 | 0.064087 | -0.2243 | -0.2655 | 0.032043 | 0.32501 | -0.13733 | 0.12817 | -0.068665 | 123.056 | 122.9004 | 56.7398 | -122.8775 | 122.8683 | 122.7676 | 53.8513 | -123.1018
2085.0156 | 123.0698 | -51.7776 | 71.077 | 0.060882 | 0.0072355 | 0.072096 | 0.06774 | 0.1295 | -0.0011451 | -0.0051547 | 0.24399 | -0.011049 | 0.062342 | 0.05633 | 0.0057038 | -0.0098374 | 71.0266 | 71.1319 | 4.8248 | -51.8417 | 71.2601 | -51.7685 | -51.8738 | -51.4343 | 1.8631 | -51.915 | 71.1594 | 71.0312 | -51.9653 | -52.0157 | 0.009155 | -0.09613 | 0.18311 | 122.9095 | -0.064087 | 0.032043 | -0.050354 | -0.18768 | -0.23804 | 0.082398 | 0.34332 | -0.13733 | 0.10071 | -0.045776 | 123.0377 | 122.8043 | 56.6025 | -122.9507 | 122.937 | 122.8088 | 53.6407 | -123.0927
2086.0156 | 123.1293 | -51.86 | 70.9579 | -1.3429 | 0.011081 | 0.069319 | 0.068808 | 0.13014 | 0.0012047 | -0.0055821 | 0.2211 | -0.0099806 | 0.063196 | 0.056544 | 0.0086944 | -0.0087692 | 70.9259 | 71.1319 | 4.628 | -51.9974 | 71.0724 | -51.9241 | -51.9882 | -51.5167 | 1.7075 | -52.066 | 70.99 | 70.8664 | -52.0889 | -52.1301 | -0.064087 | -0.12817 | 0.11444 | 122.9919 | -0.13733 | -0.009155 | -0.032044 | -0.22888 | -0.27008 | 0.032043 | 0.34332 | -0.20599 | 0.064087 | -0.091553 | 122.9324 | 122.7859 | 56.488 | -122.9462 | 122.85 | 122.7264 | 53.5675 | -123.0881
2087.0156 | 123.0835 | -51.0956 | 71.7545 | 0.16769 | 0.010226 | 0.068464 | 0.069022 | 0.12843 | -0.0015723 | -0.0049411 | 0.068512 | -0.0089124 | 0.061701 | 0.059321 | 0.0069854 | -0.011546 | 71.6309 | 71.8323 | 4.6371 | -51.2695 | 71.8689 | -51.1688 | -51.2512 | -50.7477 | 2.4261 | -51.2054 | 71.8277 | 71.7133 | -51.2558 | -51.3428 | -0.073242 | -0.15564 | 0.11444 | 122.9279 | -0.17395 | -0.01831 | -0.1236 | -0.16022 | -0.24719 | 0.073242 | 0.3479 | -0.10986 | 0.13733 | -0.041199 | 122.9645 | 122.7264 | 55.7327 | -123.0057 | 122.9233 | 122.8088 | 53.5217 | -123.0972
2088.0156 | 123.0469 | -52.4551 | 70.4132 | 0.16006 | 0.01578 | 0.069319 | 0.070944 | 0.1295 | 0.0029137 | -0.0023777 | 0.14481 | -0.0048536 | 0.066187 | 0.055903 | 0.0082672 | -0.01176 | 70.285 | 70.3766 | 4.2984 | -52.6566 | 70.5276 | -52.5558 | -52.6245 | -52.0981 | 1.5015 | -52.5833 | 70.5231 | 70.4132 | -52.6337 | -52.6703 | -0.10071 | -0.16937 | 0.11444 | 122.8317 | -0.20142 | -0.032043 | -0.12817 | -0.17853 | -0.21515 | 0.10986 | 0.35706 | -0.12817 | 0.086975 | 0 | 122.9828 | 122.7402 | 56.7535 | -123.0377 | 122.9782 | 122.8683 | 53.9566 | -123.0835
2089.0156 | 123.1384 | -51.9424 | 70.8481 | 0.17532 | 0.012149 | 0.069532 | 0.070944 | 0.13035 | 0.00035035 | -0.0017369 | 1.0146 | -0.010835 | 0.06106 | 0.058253 | 0.008908 | -0.011974 | 70.903 | 71.077 | 4.3488 | -52.0111 | 71.0312 | -51.947 | -52.0569 | -51.5762 | 1.8082 | -52.1576 | 70.9625 | 70.8527 | -52.121 | -52.1759 | -0.004577 | -0.11444 | 0.18311 | 123.0194 | -0.068664 | 0.045777 | 0.054932 | -0.17853 | -0.23346 | 0.11444 | 0.36621 | -0.21515 | 0.01831 | 0.004578 | 122.9736 | 122.8455 | 56.2912 | -122.905 | 122.905 | 122.7951 | 53.7506 | -123.024
2090.0156 | 123.0743 | -51.8097 | 71.0312 | 0.14481 | 0.01514 | 0.067823 | 0.072653 | 0.13228 | 0.0012047 | -0.0025913 | 0.15244 | -0.0097668 | 0.063196 | 0.057185 | 0.0069854 | -0.0098374 | 70.9076 | 71.0449 | 4.2984 | -52.0523 | 71.1868 | -51.8967 | -51.9699 | -51.4343 | 2.037 | -51.9653 | 71.1411 | 71.0083 | -52.0203 | -52.0477 | -0.086975 | -0.16022 | 0.15564 | 122.8546 | -0.24262 | -0.082397 | -0.1236 | -0.21057 | -0.23804 | 0.10986 | 0.37537 | -0.15564 | 0.082397 | -0.022888 | 122.9965 | 122.7173 | 56.1081 | -123.0011 | 122.9507 | 122.818 | 53.8467 | -123.0789
2091.0156 | 123.0835 | -50.9125 | 71.9055 | 0.10666 | 0.01279 | 0.06761 | 0.067954 | 0.13099 | -0.0019995 | -0.0043003 | 0.19058 | -0.0095532 | 0.060633 | 0.057398 | 0.006131 | -0.010478 | 71.8781 | 72.0703 | 4.6463 | -51.0406 | 72.0474 | -50.9445 | -51.0269 | -50.4868 | 2.1469 | -50.9354 | 72.0428 | 71.9421 | -51.0452 | -51.1505 | -0.032043 | -0.11444 | 0.14191 | 122.9828 | -0.12817 | -0.013732 | -0.027466 | -0.13275 | -0.23804 | 0.13733 | 0.42572 | -0.022888 | 0.21515 | 0.036621 | 122.9599 | 122.7905 | 55.5588 | -122.9324 | 122.9553 | 122.8546 | 53.0594 | -123.056
2092.0156 | 123.0835 | -51.297 | 71.5759 | 0.14481 | 0.014926 | 0.068464 | 0.069663 | 0.1295 | 0.0031273 | -0.0047275 | 0.18295 | -0.0059216 | 0.065119 | 0.059107 | 0.0082672 | -0.010478 | 71.4478 | 71.5805 | 3.9001 | -51.4801 | 71.7041 | -51.3382 | -51.4206 | -50.9628 | 2.0874 | -51.5488 | 71.6766 | 71.5576 | -51.4938 | -51.5167 | -0.041199 | -0.1236 | 0.12817 | 122.8775 | -0.18311 | -0.05951 | -0.12817 | -0.19684 | -0.21973 | 0.10071 | 0.33417 | -0.25177 | -0.032043 | -0.018311 | 123.0011 | 122.7448 | 55.1971 | -122.9965 | 122.9736 | 122.8546 | 53.3844 | -123.0927
2093.0625 | 123.0515 | -51.3611 | 71.5302 | -0.13748 | 0.013858 | 0.067396 | 0.069663 | 0.13334 | 0.00099115 | -0.0047275 | -0.10696 | -0.0084852 | 0.062769 | 0.056758 | 0.0093354 | -0.010692 | 71.5668 | 71.7133 | 4.0329 | -51.384 | 71.814 | -51.2878 | -51.3931 | -51.0223 | 1.9501 | -51.6174 | 71.6217 | 71.4706 | -51.5533 | -51.6174 | 0.073242 | -0.032043 | 0.28381 | 123.0743 | -0.022888 | 0.009155 | 0.036621 | -0.19226 | -0.25635 | 0.091553 | 0.33874 | -0.25635 | 0 | -0.059509 | 123.175 | 122.9279 | 55.394 | -122.9233 | 122.9828 | 122.8317 | 53.3112 | -123.1476
2094.0156 | 122.9691 | -50.8209 | 72.0886 | 0.030365 | 0.014499 | 0.066755 | 0.073508 | 0.12993 | 0.0024865 | -0.0055821 | -0.015411 | -0.0069898 | 0.066828 | 0.054835 | 0.011685 | -0.010692 | 71.9513 | 72.0795 | 4.2709 | -50.9766 | 72.226 | -50.853 | -50.9308 | -50.5005 | 2.1423 | -50.9674 | 72.2031 | 72.1161 | -50.9628 | -51.0223 | -0.032043 | -0.10986 | 0.13733 | 122.9004 | -0.15564 | -0.045776 | -0.13733 | -0.14191 | -0.20142 | 0.11444 | 0.32044 | -0.14648 | 0.054932 | 0.027466 | 123.0469 | 122.7722 | 55.0919 | -123.0194 | 123.024 | 122.937 | 52.9633 | -123.111
2095.0156 | 123.0469 | -50.9995 | 71.8597 | 0.12192 | 0.014285 | 0.0706 | 0.073508 | 0.12693 | -7.6852e-05 | -0.0038731 | 0.16769 | -0.0076306 | 0.064051 | 0.056758 | 0.00784 | -0.0096238 | 71.64 | 71.7911 | 4.335 | -51.2466 | 71.9513 | -51.1002 | -51.2054 | -50.6744 | 2.0737 | -51.1185 | 71.9879 | 71.8735 | -51.1963 | -51.2375 | -0.10071 | -0.20599 | 0.091553 | 122.7905 | -0.24719 | -0.041199 | -0.21973 | -0.19684 | -0.23804 | 0.12817 | 0.32501 | -0.11902 | 0.11902 | 0.013733 | 122.9507 | 122.6395 | 55.3345 | -123.0652 | 122.9874 | 122.8729 | 53.0731 | -123.0972
2096.0156 | 122.9507 | -51.6357 | 71.2784 | -0.00015269 | 0.016849 | 0.068464 | 0.071585 | 0.13035 | 0.0020593 | -0.0038731 | 0.24399 | -0.006349 | 0.06341 | 0.059535 | 0.0082672 | -0.011119 | 71.0632 | 71.1685 | 3.9413 | -51.8829 | 71.347 | -51.7593 | -51.8646 | -51.3657 | 1.8127 | -51.8784 | 71.3196 | 71.2509 | -51.8143 | -51.8738 | -0.1236 | -0.22888 | 0.068665 | 122.8043 | -0.24719 | -0.018311 | -0.21515 | -0.17853 | -0.23804 | 0.041199 | 0.27008 | -0.24262 | -0.004578 | -0.027465 | 122.9828 | 122.699 | 55.5771 | -123.143 | 122.9553 | 122.8867 | 53.4485 | -123.1522
2097.0156 | 123.0469 | -50.5692 | 72.3084 | 0.30502 | 0.015353 | 0.06761 | 0.072653 | 0.128 | 0.00077755 | -0.0030185 | 0.19058 | -0.0082716 | 0.062128 | 0.057398 | 0.0063446 | -0.010265 | 72.1756 | 72.2534 | 4.2297 | -50.7706 | 72.4365 | -50.647 | -50.7111 | -50.2487 | 1.3962 | -50.7751 | 72.4274 | 72.3084 | -50.7523 | -50.8118 | -0.07782 | -0.14191 | 0.12817 | 122.8226 | -0.20142 | -0.059509 | -0.13275 | -0.1831 | -0.24262 | 0.11902 | 0.32044 | -0.20599 | 0.036622 | 0 | 123.0057 | 122.7448 | 54.7989 | -123.0194 | 122.9965 | 122.8775 | 51.9653 | -123.1201
2098.0156 | 123.0103 | -50.5966 | 72.2992 | 0.030365 | 0.017917 | 0.068678 | 0.071585 | 0.12971 | 0.0012047 | -0.0028049 | 0.19058 | -0.0078442 | 0.064264 | 0.058253 | 0.0086944 | -0.0096238 | 72.1985 | 72.3175 | 4.3716 | -50.6927 | 72.5052 | -50.5554 | -50.6973 | -50.267 | 1.767 | -50.8987 | 72.4274 | 72.3404 | -50.766 | -50.8255 | 0.041199 | -0.10071 | 0.20599 | 122.9141 | -0.09613 | 0.004578 | -0.10071 | -0.16937 | -0.22888 | 0.12817 | 0.32959 | -0.30212 | -0.073243 | 0.041199 | 123.1018 | 122.7951 | 54.9683 | -122.9965 | 123.024 | 122.937 | 52.3636 | -123.1247
2099.0156 | 123.0103 | -49.4019 | 73.4985 | -0.46555 | 0.01514 | 0.067396 | 0.073294 | 0.12864 | -7.6852e-05 | -0.0057957 | 0.16006 | -0.0082716 | 0.062555 | 0.058894 | 0.0052764 | -0.010265 | 73.1277 | 73.2834 | 4.509 | -49.7543 | 73.4573 | -49.5987 | -49.6994 | -49.1913 | 2.3987 | -49.5392 | 73.5077 | 73.4161 | -49.6582 | -49.6857 | -0.19684 | -0.29755 | -0.041199 | 122.6852 | -0.35248 | -0.054931 | -0.37079 | -0.25635 | -0.28381 | 0.009155 | 0.21057 | -0.13733 | 0.14648 | -0.082397 | 122.8592 | 122.5296 | 53.9108 | -123.1979 | 122.9095 | 122.818 | 51.8005 | -123.1842
2100.0156 | 123.0194 | -50.9445 | 71.9604 | -0.045929 | 0.015994 | 0.068464 | 0.072867 | 0.12928 | 0.00077755 | -0.0034457 | 0.030365 | -0.006349 | 0.062982 | 0.058039 | 0.0069854 | -0.010478 | 71.8414 | 71.9421 | 3.891 | -51.1047 | 72.0749 | -50.9903 | -51.0727 | -50.5417 | 2.1652 | -51.0864 | 72.0932 | 72.0108 | -51.0864 | -51.1505 | -0.045776 | -0.12817 | 0.11444 | 122.8867 | -0.16022 | -0.032043 | -0.11902 | -0.14191 | -0.20599 | 0.13275 | 0.40283 | -0.14191 | 0.064087 | 0.050354 | 123.0194 | 122.7859 | 54.8355 | -123.0331 | 123.0377 | 122.9553 | 53.1097 | -123.111
2101.0156 | 122.8638 | -50.0015 | 72.8577 | 0.30502 | 0.017703 | 0.067396 | 0.070731 | 0.13142 | 0.0024865 | -0.0049411 | 0.13718 | -0.007417 | 0.064264 | 0.059107 | 0.0067718 | -0.011974 | 72.7432 | 72.8256 | 4.2847 | -50.1572 | 73.027 | -50.0519 | -50.116 | -49.7086 | 2.3483 | -50.1572 | 73.027 | 72.9675 | -50.1526 | -50.2029 | -0.050354 | -0.11444 | 0.16937 | 122.8271 | -0.15564 | -0.041199 | -0.11444 | -0.15106 | -0.20142 | 0.16937 | 0.29297 | -0.15564 | 0.045776 | 0.10986 | 123.0286 | 122.7448 | 54.2862 | -122.9736 | 123.0286 | 122.9691 | 52.3499 | -123.0606
2102.0156 | 123.0652 | -48.2071 | 74.6979 | -0.19852 | 0.014499 | 0.068891 | 0.072867 | 0.12971 | 0.00035035 | -0.0053683 | -0.14511 | -0.0065626 | 0.064051 | 0.056971 | 0.0065582 | -0.0057786 | 74.5148 | 74.6613 | 4.9896 | -48.3719 | 74.7986 | -48.2758 | -48.3536 | -47.9233 | 2.9526 | -48.3353 | 74.7757 | 74.6887 | -48.4085 | -48.4222 | -0.068665 | -0.14648 | 0.10071 | 122.8683 | -0.16479 | -0.01831 | -0.1831 | -0.20142 | -0.21515 | 0.07782 | 0.28381 | -0.12817 | 0.086975 | -0.009155 | 123.0057 | 122.7219 | 53.1967 | -123.0515 | 122.9828 | 122.8958 | 51.1597 | -123.1201
2103.0156 | 122.9233 | -50.473 | 72.4594 | 0.060882 | 0.018771 | 0.066755 | 0.070731 | 0.128 | 0.0012047 | -0.0030185 | 0.14481 | -0.0061352 | 0.064478 | 0.058039 | 0.006131 | -0.0087692 | 72.1252 | 72.2443 | 4.3625 | -50.7568 | 72.4594 | -50.6149 | -50.7065 | -50.2304 | 2.1606 | -50.6561 | 72.4823 | 72.4045 | -50.6882 | -50.7339 | -0.14191 | -0.23346 | 0 | 122.7173 | -0.28381 | -0.050354 | -0.33417 | -0.21515 | -0.26093 | 0.022888 | 0.24261 | -0.18311 | 0.07782 | -0.054932 | 122.9324 | 122.5983 | 54.8355 | -123.1659 | 122.9553 | 122.8775 | 52.6337 | -123.1934
2104.0156 | 123.0377 | -49.0402 | 73.8647 | -0.091705 | 0.014712 | 0.068464 | 0.074576 | 0.12886 | 0.00077755 | -0.0051547 | 0.67123 | -0.007417 | 0.064051 | 0.057826 | 0.00784 | -0.010692 | 73.5809 | 73.7 | 4.8523 | -49.3332 | 73.8281 | -49.2233 | -49.3103 | -48.7839 | 2.7649 | -49.2004 | 73.9197 | 73.8144 | -49.2599 | -49.3103 | -0.18311 | -0.27008 | -0.036621 | 122.7402 | -0.29297 | -0.022888 | -0.28381 | -0.21973 | -0.27008 | 0.054932 | 0.25635 | -0.16022 | 0.10986 | -0.050354 | 122.8683 | 122.6212 | 53.8925 | -123.175 | 122.9599 | 122.8546 | 51.8051 | -123.175
2105.0156 | 123.0103 | -49.8093 | 73.114 | 0.015106 | 0.017062 | 0.069746 | 0.073935 | 0.13057 | 0.0018457 | -0.0047275 | 0.083771 | -0.0072034 | 0.0664 | 0.057612 | 0.00784 | -0.010692 | 72.9126 | 73.0225 | 4.5685 | -49.9878 | 73.1964 | -49.855 | -49.9649 | -49.5621 | 2.5131 | -50.0473 | 73.1735 | 73.1094 | -50.0061 | -50.0427 | -0.045777 | -0.15564 | 0.082397 | 122.8317 | -0.17853 | -0.022888 | -0.20142 | -0.19684 | -0.23346 | 0.059509 | 0.24719 | -0.23804 | -0.004577 | -0.004578 | 123.0057 | 122.7219 | 54.3777 | -123.0789 | 122.9828 | 122.9187 | 52.3224 | -123.1567
2106.0156 | 123.056 | -48.793 | 74.1074 | -0.17563 | 0.016208 | 0.068464 | 0.069663 | 0.13057 | 0.0016321 | -0.0028049 | -0.11459 | -0.0082716 | 0.062982 | 0.05868 | 0.0084808 | -0.012187 | 73.9883 | 74.1211 | 4.6555 | -48.9532 | 74.2538 | -48.8113 | -48.9075 | -48.4497 | 2.6733 | -48.967 | 74.2401 | 74.1211 | -48.9624 | -49.0082 | -0.01831 | -0.11444 | 0.14648 | 122.9141 | -0.16022 | -0.045776 | -0.11902 | -0.16937 | -0.21515 | 0.13275 | 0.34332 | -0.17395 | 0.041199 | 0.013733 | 123.0469 | 122.7814 | 53.4485 | -123.0148 | 123.0331 | 122.9141 | 51.4664 | -123.1155
2107.0156 | 123.024 | -49.173 | 73.7457 | -0.053558 | 0.017276 | 0.069319 | 0.070303 | 0.128 | 0.00056395 | -0.0057957 | 0.022736 | -0.0086988 | 0.065546 | 0.058253 | 0.0074126 | -0.010478 | 73.8144 | 73.9471 | 4.6326 | -49.1318 | 74.0524 | -49.0265 | -49.1135 | -48.7747 | 1.8219 | -49.3744 | 73.9014 | 73.8052 | -49.3332 | -49.3652 | 0.14649 | 0.05951 | 0.3067 | 123.1201 | 0.041199 | -0.018311 | 0.068664 | -0.16022 | -0.19226 | 0.15564 | 0.39826 | -0.20142 | -0.009156 | 0.059509 | 123.2254 | 122.9874 | 53.8055 | -122.8592 | 123.0743 | 122.9782 | 50.9949 | -123.111
2108.0156 | 123.024 | -49.2462 | 73.6725 | -0.22141 | 0.012149 | 0.071241 | 0.070944 | 0.12993 | -0.0034949 | -0.0087863 | -0.8699 | -0.0082716 | 0.064478 | 0.056117 | 0.0052764 | -0.0077012 | 73.4985 | 73.6496 | 4.5685 | -49.3561 | 73.819 | -49.2554 | -49.3195 | -48.9853 | 2.092 | -49.4064 | 73.7549 | 73.7 | -49.4339 | -49.4888 | -0.009155 | -0.073242 | 0.14648 | 122.8958 | -0.10986 | -0.036621 | -0.17395 | -0.18768 | -0.24262 | 0.082398 | 0.26093 | -0.16022 | 0.082398 | 0.027466 | 123.0652 | 122.7448 | 53.8147 | -122.9919 | 123.0011 | 122.9462 | 51.3382 | -123.1613
2109.0156 | 123.0194 | -49.9649 | 72.9401 | -0.22903 | 0.014712 | 0.068678 | 0.073935 | 0.1295 | 0.00013675 | -0.0049411 | -0.12222 | -0.010194 | 0.064478 | 0.056758 | 0.0080536 | -0.010905 | 72.7158 | 72.8394 | 4.2755 | -50.1846 | 72.9904 | -50.0839 | -50.1801 | -49.6719 | 2.0554 | -50.148 | 73.027 | 72.9355 | -50.1343 | -50.1846 | -0.11902 | -0.21515 | 0.050354 | 122.8043 | -0.21973 | -0.004577 | -0.2243 | -0.16937 | -0.21973 | 0.086976 | 0.29297 | -0.1831 | 0.036621 | -0.004577 | 122.9553 | 122.6807 | 54.2404 | -123.1201 | 122.9919 | 122.9004 | 52.0203 | -123.1247
2110.0156 | 123.024 | -49.6811 | 73.2697 | -0.22903 | 0.01279 | 0.071455 | 0.069876 | 0.13057 | 0.00056395 | -0.0089999 | -0.20615 | -0.0099806 | 0.063196 | 0.058467 | 0.004422 | -0.0098374 | 72.8806 | 72.9538 | 4.2114 | -50.0107 | 73.1369 | -49.942 | -50.0336 | -49.5712 | 2.1744 | -50.0107 | 73.1827 | 73.1415 | -49.9374 | -49.9374 | -0.26093 | -0.35248 | -0.13275 | 122.6349 | -0.32959 | 0.022888 | -0.3891 | -0.25635 | -0.25635 | -0.086975 | 0.10986 | -0.32959 | -0.073242 | -0.12817 | 122.818 | 122.5616 | 53.8925 | -123.3032 | 122.8638 | 122.8226 | 51.8555 | -123.2071
2111.0156 | 123.0377 | -48.3078 | 74.6429 | -0.068817 | 0.016421 | 0.069105 | 0.07009 | 0.12971 | 0.0033411 | 0.00018594 | -0.0077819 | -0.0082716 | 0.064051 | 0.059107 | 0.0065582 | -0.010905 | 74.2859 | 74.588 | 4.8477 | -48.5184 | 74.675 | -48.3994 | -48.4955 | -48.0469 | 2.7008 | -48.3948 | 74.6613 | 74.5834 | -48.4817 | -48.5321 | -0.091553 | -0.18768 | 0.032044 | 122.8958 | -0.21057 | -0.022889 | -0.35706 | -0.17395 | -0.2243 | 0.018311 | 0.26093 | -0.086975 | 0.13733 | -0.059509 | 122.9828 | 122.5937 | 53.1555 | -123.1384 | 122.9691 | 122.8912 | 51.0086 | -123.175
2112.0156 | 123.0331 | -49.5575 | 73.3521 | -0.20615 | 0.01578 | 0.069532 | 0.071372 | 0.12864 | -0.0011451 | -0.0066501 | -0.14511 | -0.007417 | 0.062555 | 0.058253 | 0.007199 | -0.011974 | 73.2101 | 73.3475 | 4.3579 | -49.7177 | 73.4711 | -49.6262 | -49.7269 | -49.2325 | 2.5085 | -49.7177 | 73.4207 | 73.3749 | -49.7314 | -49.791 | -0.068665 | -0.16937 | 0.11902 | 122.905 | -0.16022 | 0.009156 | -0.14191 | -0.17395 | -0.23346 | 0.068664 | 0.32501 | -0.16022 | 0.073243 | 0.022888 | 123.0286 | 122.7676 | 53.9154 | -123.0789 | 122.9782 | 122.9324 | 52.066 | -123.143
2113.0156 | 123.056 | -49.1592 | 73.7549 | -0.023041 | 0.015353 | 0.067823 | 0.074149 | 0.12822 | 0.0031273 | -0.0053683 | -0.015411 | -0.0086988 | 0.063196 | 0.058039 | 0.0065582 | -0.010905 | 73.5031 | 73.6588 | 4.5181 | -49.4064 | 73.7595 | -49.2828 | -49.3835 | -48.912 | 2.5909 | -49.3423 | 73.764 | 73.6954 | -49.3835 | -49.4202 | -0.1236 | -0.2243 | 0.004577 | 122.818 | -0.24719 | -0.022888 | -0.25177 | -0.2243 | -0.26093 | 0.009155 | 0.24719 | -0.1831 | 0.07782 | -0.059509 | 122.9187 | 122.6624 | 53.6774 | -123.1384 | 122.9233 | 122.8546 | 51.7502 | -123.175
2114.0156 | 123.056 | -50.1846 | 72.7249 | -0.20615 | 0.011935 | 0.067823 | 0.072012 | 0.12971 | -0.0015723 | -0.0043003 | -0.11459 | -0.0093396 | 0.062555 | 0.060176 | 0.0057038 | -0.0079148 | 72.4274 | 72.5739 | 4.3121 | -50.4547 | 72.7112 | -50.3494 | -50.4364 | -49.9237 | 2.4445 | -50.3448 | 72.7707 | 72.7203 | -50.3723 | -50.4135 | -0.16479 | -0.25177 | -0.013733 | 122.7585 | -0.27008 | -0.018311 | -0.29755 | -0.18768 | -0.22888 | 0.045776 | 0.26093 | -0.16022 | 0.068664 | -0.004578 | 122.8958 | 122.612 | 54.4968 | -123.1613 | 122.9553 | 122.905 | 52.6291 | -123.1384
2115.0156 | 123.0606 | -50.8163 | 72.1161 | -0.099335 | 0.013858 | 0.067823 | 0.071372 | 0.13078 | 0.0027001 | -0.0030185 | -0.068817 | -0.010194 | 0.065973 | 0.059321 | 0.0065582 | -0.010692 | 72.0108 | 72.1298 | 4.4083 | -50.9171 | 72.2855 | -50.7431 | -50.853 | -50.4959 | 2.6138 | -51.0544 | 72.1848 | 72.0703 | -50.9949 | -51.0452 | 0.073242 | -0.036621 | 0.16937 | 122.9462 | -0.10071 | -0.064087 | -0.10529 | -0.17853 | -0.22888 | 0.068664 | 0.32043 | -0.23804 | -0.009155 | -0.045777 | 123.1018 | 122.8271 | 55.2246 | -122.9691 | 123.0011 | 122.8867 | 53.4302 | -123.1613
2116.0156 | 123.0148 | -48.9716 | 73.9517 | -0.23666 | 0.0074491 | 0.071668 | 0.07009 | 0.12928 | -0.0030677 | -0.0047275 | -0.12222 | -0.008058 | 0.062555 | 0.058039 | 0.0046356 | -0.0091966 | 73.9059 | 74.0799 | 4.9301 | -49.0173 | 74.2035 | -48.8617 | -48.9853 | -48.6969 | 3.1815 | -49.3149 | 74.0479 | 73.9746 | -49.1592 | -49.2142 | 0.10986 | -0.013733 | 0.25177 | 123.0515 | -0.045776 | -0.032043 | -0.045776 | -0.18768 | -0.24261 | 0.096131 | 0.27466 | -0.34332 | -0.10071 | 0.022888 | 123.175 | 122.8775 | 53.9017 | -122.937 | 123.0194 | 122.9462 | 52.153 | -123.1659
2117.0156 | 123.0606 | -49.6857 | 73.2239 | -0.17563 | 0.014499 | 0.06825 | 0.073294 | 0.13142 | 0.0016321 | -0.0062229 | -0.11459 | -0.0076306 | 0.063196 | 0.059321 | 0.0057038 | -0.0096238 | 73.0865 | 73.1827 | 4.7882 | -49.8505 | 73.3612 | -49.7269 | -49.8322 | -49.3835 | 2.6733 | -49.9146 | 73.2834 | 73.2193 | -49.8962 | -49.9283 | -0.041199 | -0.14648 | 0.13733 | 122.8683 | -0.1648 | -0.018311 | -0.13733 | -0.21057 | -0.24262 | 0.059509 | 0.30212 | -0.22888 | 0.013733 | -0.004578 | 123.0469 | 122.7722 | 54.4739 | -123.056 | 122.9691 | 122.905 | 52.359 | -123.1522
2118.0156 | 123.0515 | -49.3149 | 73.5947 | -0.168 | 0.012576 | 0.068891 | 0.071799 | 0.13035 | -0.00071785 | -0.0077183 | -0.099335 | -0.010194 | 0.062769 | 0.057612 | 0.0065582 | -0.0094102 | 73.4711 | 73.6084 | 4.7333 | -49.3835 | 73.8007 | -49.292 | -49.3652 | -49.0768 | 2.4399 | -49.5483 | 73.6679 | 73.5992 | -49.5163 | -49.5438 | 0.022888 | -0.050354 | 0.20599 | 122.9233 | -0.068665 | -0.018311 | -0.1236 | -0.20142 | -0.22888 | 0.073242 | 0.23804 | -0.23346 | -0.004578 | 0.004577 | 123.1155 | 122.7859 | 54.0482 | -122.9599 | 122.9828 | 122.9141 | 51.7548 | -123.1384
2119.0156 | 123.0423 | -49.3698 | 73.5443 | 0.015106 | 0.016208 | 0.069319 | 0.072226 | 0.12971 | 0.00077755 | -0.0045139 | -0.061188 | -0.007417 | 0.064691 | 0.059535 | 0.0069854 | -0.0098374 | 73.4024 | 73.526 | 4.5456 | -49.5438 | 73.6313 | -49.4247 | -49.5346 | -49.0631 | 2.6642 | -49.5667 | 73.5901 | 73.5031 | -49.585 | -49.6078 | -0.054932 | -0.16479 | 0.086975 | 122.8958 | -0.17395 | -0.009155 | -0.14191 | -0.21515 | -0.23804 | 0.045776 | 0.3067 | -0.19684 | 0.041199 | -0.041199 | 123.0011 | 122.7722 | 53.9154 | -123.0789 | 122.9599 | 122.8729 | 52.034 | -123.1522
2120.0156 | 122.9919 | -48.6786 | 74.2767 | -0.23666 | 0.0078763 | 0.069105 | 0.073935 | 0.13099 | -0.0024269 | -0.0072911 | 0.022736 | -0.0076306 | 0.062769 | 0.059535 | 0.0059174 | -0.0091966 | 73.7778 | 74.3362 | 4.6921 | -49.0768 | 74.2401 | -48.8663 | -48.9532 | -48.4131 | 2.9709 | -48.7381 | 74.3317 | 74.2767 | -48.8434 | -48.9029 | -0.18768 | -0.27466 | -0.036621 | 123.0148 | -0.39825 | -0.1236 | -0.49896 | -0.16479 | -0.2243 | 0.054932 | 0.2655 | -0.059509 | 0.16479 | 0 | 122.9187 | 122.4564 | 53.3707 | -123.23 | 123.0103 | 122.9553 | 51.6495 | -123.1796
2121.0469 | 123.1293 | -47.8226 | 75.0687 | -0.076447 | 0.0074491 | 0.071027 | 0.07244 | 0.12629 | -0.0088355 | -0.0062229 | 0.076141 | -0.011262 | 0.062769 | 0.056971 | 0.0046356 | -0.0091966 | 74.9084 | 75.0824 | 4.6463 | -48.0011 | 75.1373 | -47.8729 | -47.9691 | -47.4838 | 3.0396 | -47.8683 | 75.119 | 75.0549 | -47.9782 | -48.024 | -0.050354 | -0.14648 | 0.068664 | 122.905 | -0.17853 | -0.032044 | -0.16022 | -0.15564 | -0.20142 | 0.050354 | 0.33875 | -0.045776 | 0.15564 | -0.013733 | 122.9599 | 122.731 | 52.4689 | -123.0377 | 122.9416 | 122.8775 | 50.8621 | -123.0927
2122.0156 | 123.0515 | -47.3511 | 75.5768 | -0.20615 | 0.0074491 | 0.070387 | 0.073081 | 0.13014 | -0.0026405 | -0.010709 | -0.12222 | -0.010408 | 0.063623 | 0.059535 | 0.00549 | -0.010692 | 75.5814 | 75.7782 | 4.6783 | -47.3099 | 75.8102 | -47.2 | -47.3328 | -46.994 | 3.1631 | -47.4701 | 75.7141 | 75.5997 | -47.493 | -47.5525 | 0.15106 | 0.01831 | 0.23346 | 123.1293 | 0.041199 | 0.022889 | 0.004578 | -0.14191 | -0.20142 | 0.13733 | 0.35705 | -0.11902 | 0.082397 | 0.022888 | 123.1613 | 122.9324 | 52.0294 | -122.9095 | 123.0652 | 122.9507 | 50.5142 | -123.1293
2123.0156 | 123.0377 | -47.6028 | 75.3616 | -0.25192 | 0.011935 | 0.068678 | 0.072226 | 0.12843 | 0.00099115 | -0.0051547 | 0.030365 | -0.009126 | 0.062342 | 0.057185 | 0.0082672 | -0.010692 | 74.7849 | 75.0732 | 4.8111 | -47.9828 | 75.2609 | -47.8455 | -47.9233 | -47.4655 | 3.0899 | -47.818 | 75.3021 | 75.2014 | -47.8867 | -47.9004 | -0.24262 | -0.32044 | -0.10071 | 122.6761 | -0.37994 | -0.059509 | -0.57678 | -0.28381 | -0.29755 | -0.059509 | 0.13733 | -0.21515 | 0.082398 | -0.16022 | 122.8638 | 122.3877 | 52.4139 | -123.2849 | 122.905 | 122.8043 | 50.6927 | -123.262
2124.0156 | 123.0469 | -47.699 | 75.1556 | -0.22141 | 0.01044 | 0.069959 | 0.069022 | 0.12928 | -0.0028541 | -0.0066501 | -0.18326 | -0.0086988 | 0.064478 | 0.057826 | 0.0067718 | -0.0096238 | 75.0092 | 75.1923 | 4.7653 | -47.9004 | 75.2518 | -47.7722 | -47.8729 | -47.4701 | 3.0487 | -47.8409 | 75.2609 | 75.2014 | -47.905 | -47.9416 | -0.073242 | -0.17395 | 0.09613 | 122.8912 | -0.20142 | -0.027466 | -0.14648 | -0.20599 | -0.24261 | 0.10528 | 0.22888 | -0.14191 | 0.10071 | 0.045776 | 122.9507 | 122.7081 | 52.4643 | -123.0286 | 122.9599 | 122.9004 | 50.7477 | -123.0972
2125.0625 | 123.1338 | -46.9528 | 75.8881 | -0.11459 | 0.0093717 | 0.070814 | 0.072653 | 0.12928 | -0.0060585 | -0.0085727 | 0.045624 | -0.008058 | 0.062128 | 0.057185 | 0.00549 | -0.011546 | 75.7553 | 75.9567 | 4.8981 | -47.1451 | 76.0208 | -47.0215 | -47.1176 | -46.6278 | 3.5156 | -47.0352 | 75.9476 | 75.8835 | -47.1771 | -47.2 | -0.068664 | -0.16479 | 0.13275 | 122.9095 | -0.19226 | -0.027466 | -0.13275 | -0.2243 | -0.24719 | 0.059509 | 0.32501 | -0.082397 | 0.16479 | -0.004578 | 122.9736 | 122.7081 | 51.8509 | -123.0057 | 122.9004 | 122.8363 | 50.4684 | -123.0881
2126.0156 | 123.0515 | -48.2162 | 74.7116 | -0.25192 | 0.012149 | 0.069959 | 0.070944 | 0.13142 | -0.0013587 | -0.0079319 | -0.2214 | -0.0099806 | 0.060633 | 0.056758 | 0.0074126 | -0.010478 | 74.6246 | 74.7849 | 4.5731 | -48.3124 | 74.913 | -48.1705 | -48.2574 | -47.9782 | 3.1036 | -48.4497 | 74.8169 | 74.6887 | -48.4222 | -48.4817 | 0.045777 | -0.041198 | 0.20142 | 123.0011 | -0.09613 | -0.054932 | -0.086975 | -0.20599 | -0.2655 | 0.10529 | 0.23804 | -0.23346 | 0.032043 | -0.022888 | 123.1293 | 122.8409 | 52.7893 | -122.9691 | 123.0331 | 122.905 | 51.3199 | -123.1934
2127.0156 | 123.024 | -48.6282 | 74.2767 | -0.19089 | 0.010867 | 0.06825 | 0.074362 | 0.12907 | 0.0031273 | -0.0049411 | -0.17563 | -0.0065626 | 0.064051 | 0.056758 | 0.008908 | -0.013469 | 74.0936 | 74.2447 | 4.4724 | -48.8113 | 74.4232 | -48.6969 | -48.8068 | -48.3353 | 3.0441 | -48.7656 | 74.4049 | 74.295 | -48.7885 | -48.8342 | -0.068664 | -0.17853 | 0.14649 | 122.8729 | -0.18311 | -0.004577 | -0.1831 | -0.16022 | -0.20599 | 0.12817 | 0.29297 | -0.13733 | 0.068665 | 0.018311 | 123.0515 | 122.7219 | 53.1006 | -123.0835 | 123.0331 | 122.9233 | 51.6724 | -123.111
2128.0156 | 122.9919 | -46.6599 | 76.2909 | -0.23666 | 0.010226 | 0.069746 | 0.070731 | 0.13014 | -0.0011451 | -0.0051547 | -0.17563 | -0.0069898 | 0.06341 | 0.058253 | 0.0065582 | -0.010905 | 76.1261 | 76.2955 | 5.1178 | -46.7926 | 76.3641 | -46.6644 | -46.756 | -46.4172 | 3.978 | -46.8658 | 76.3321 | 76.2588 | -46.8155 | -46.8887 | -0.004578 | -0.09613 | 0.073242 | 122.9553 | -0.13275 | -0.036622 | -0.16479 | -0.15564 | -0.22888 | 0.041198 | 0.24262 | -0.20599 | 0.022888 | -0.032044 | 123.024 | 122.7859 | 51.7776 | -123.0469 | 122.9919 | 122.9187 | 50.6378 | -123.1796
2129.0156 | 123.0194 | -47.0444 | 75.8972 | -0.20615 | 0.011294 | 0.072096 | 0.070731 | 0.12864 | -0.00093145 | -0.0045139 | -0.13748 | -0.0076306 | 0.061273 | 0.057185 | 0.0074126 | -0.011119 | 75.705 | 75.8606 | 4.9667 | -47.2183 | 76.03 | -47.081 | -47.1497 | -46.8246 | 3.8498 | -47.2595 | 75.9476 | 75.8698 | -47.2275 | -47.2504 | -0.036621 | -0.10529 | 0.13275 | 122.905 | -0.17395 | -0.068665 | -0.19226 | -0.1831 | -0.20599 | 0.050354 | 0.21973 | -0.21515 | -0.009155 | -0.027466 | 123.0743 | 122.7493 | 52.0111 | -123.0469 | 122.9919 | 122.9141 | 50.8942 | -123.1476
2130.0156 | 123.1384 | -46.3852 | 76.4465 | -0.22141 | 0.0078763 | 0.069959 | 0.069235 | 0.12843 | -0.0064857 | -0.0083591 | -0.26718 | -0.0099806 | 0.062128 | 0.058253 | 0.0057038 | -0.010265 | 76.7441 | 76.387 | 4.7882 | -46.5729 | 76.6159 | -46.3806 | -46.4859 | -46.0876 | 4.1885 | -46.3898 | 76.5564 | 76.474 | -46.5408 | -46.6003 | 0.004578 | -0.10071 | 0.16937 | 122.7722 | -0.18768 | -0.086975 | 0.29755 | -0.15564 | -0.21515 | 0.10986 | 0.29755 | -0.004578 | 0.21057 | 0.027466 | 123.0011 | 123.1293 | 51.1734 | -122.9324 | 122.9416 | 122.8592 | 50.5737 | -123.0469
2131.0156 | 123.0286 | -47.1268 | 75.7599 | -0.22141 | 0.013858 | 0.069746 | 0.071585 | 0.12843 | -0.00029045 | -0.0075047 | -0.38925 | -0.0078442 | 0.065973 | 0.057612 | 0.0067718 | -0.013255 | 75.7553 | 75.8286 | 4.8386 | -47.3785 | 75.9659 | -47.1497 | -47.2229 | -46.8155 | 3.1036 | -47.3465 | 75.9476 | 75.8469 | -47.3007 | -47.3557 | -0.022888 | -0.09613 | 0.20599 | 122.9553 | -0.25177 | -0.15564 | -0.004578 | -0.17395 | -0.22888 | 0.18768 | 0.31128 | -0.21973 | 0.009155 | 0.086975 | 123.0927 | 122.8821 | 51.9653 | -122.9828 | 123.0743 | 122.9736 | 50.2304 | -123.1155
2132.0156 | 123.0331 | -46.5408 | 76.3412 | -0.19852 | 0.0080899 | 0.069746 | 0.072012 | 0.13035 | -0.00071785 | -0.0066501 | -0.168 | -0.0093396 | 0.060633 | 0.057612 | 0.008908 | -0.0091966 | 76.3458 | 76.5472 | 5.2917 | -46.5637 | 76.5839 | -46.4859 | -46.5363 | -46.3257 | 3.2227 | -46.6965 | 76.4603 | 76.3596 | -46.7102 | -46.7697 | 0.054932 | 0.004578 | 0.24261 | 123.0881 | -0.022888 | -0.027466 | 0.004577 | -0.16937 | -0.22888 | 0.11902 | 0.21515 | -0.15564 | 0.073242 | 0.01831 | 123.1247 | 122.8867 | 51.8326 | -122.8775 | 123.0011 | 122.9004 | 49.7635 | -123.111
2133.0156 | 123.0103 | -47.2778 | 75.65 | -0.25955 | 0.014926 | 0.069532 | 0.073721 | 0.13142 | 0.0016321 | -0.0053683 | -0.2214 | -0.0084852 | 0.06341 | 0.058253 | 0.0080536 | -0.0089828 | 75.444 | 75.6088 | 5.0812 | -47.4518 | 75.7874 | -47.2916 | -47.3923 | -47.0398 | 3.0121 | -47.4838 | 75.7187 | 75.6363 | -47.4838 | -47.525 | -0.013733 | -0.11444 | 0.13733 | 122.8867 | -0.17395 | -0.059509 | -0.20599 | -0.20599 | -0.24719 | 0.068665 | 0.23804 | -0.20599 | 0.041198 | -0.013732 | 123.0652 | 122.7219 | 52.359 | -123.0423 | 122.9965 | 122.9141 | 50.2899 | -123.175
2134.0156 | 123.0789 | -46.2891 | 76.6068 | -0.22903 | 0.010226 | 0.068891 | 0.07244 | 0.13206 | -0.0032813 | -0.0060093 | -0.12985 | -0.0082716 | 0.059351 | 0.055476 | 0.0063446 | -0.010478 | 76.3412 | 76.5976 | 5.3787 | -46.5225 | 76.6113 | -46.3898 | -46.4767 | -46.0464 | 3.2318 | -46.3623 | 76.6617 | 76.5518 | -46.4813 | -46.5408 | -0.10071 | -0.18768 | 0.004578 | 122.8867 | -0.23346 | -0.045776 | -0.2655 | -0.19226 | -0.25177 | 0.054932 | 0.24261 | -0.073243 | 0.17853 | -0.054931 | 122.9004 | 122.6303 | 51.6678 | -123.0835 | 122.9507 | 122.8409 | 49.5209 | -123.1476
2135.0156 | 123.0148 | -47.4564 | 75.4349 | -0.25192 | 0.0095853 | 0.068678 | 0.072012 | 0.12843 | 0.0018457 | -0.0064365 | -0.91568 | -0.0078442 | 0.064478 | 0.056971 | 0.0076264 | -0.0096238 | 75.2197 | 75.3891 | 4.8065 | -47.612 | 75.5585 | -47.5296 | -47.6212 | -47.1771 | 2.7924 | -47.5067 | 75.6317 | 75.4898 | -47.6349 | -47.6852 | -0.073242 | -0.1648 | 0.1236 | 122.8455 | -0.15564 | 0.009155 | -0.21515 | -0.17853 | -0.22888 | 0.19684 | 0.27924 | -0.050354 | 0.17853 | 0.054932 | 123.0148 | 122.6761 | 52.2629 | -123.056 | 123.0881 | 122.9462 | 50.2487 | -123.1201
2136.0156 | 123.1201 | -46.2158 | 76.6525 | -0.11459 | 0.0065945 | 0.068678 | 0.070303 | 0.12886 | -0.0034949 | -0.0079319 | -0.099335 | -0.0095532 | 0.061487 | 0.057398 | 0.0065582 | -0.012614 | 76.4877 | 76.7303 | 5.0995 | -46.4127 | 76.6891 | -46.2799 | -46.4127 | -45.9183 | 3.5156 | -46.2662 | 76.6891 | 76.6022 | -46.4172 | -46.4859 | -0.064087 | -0.19684 | 0.036621 | 122.9462 | -0.19684 | 0 | -0.1648 | -0.20142 | -0.27008 | 0.036621 | 0.29755 | -0.050354 | 0.21973 | -0.050354 | 122.905 | 122.7036 | 51.3153 | -123.0652 | 122.905 | 122.818 | 49.7314 | -123.1384
2137.0156 | 123.1018 | -45.932 | 76.9455 | -0.21378 | 0.012149 | 0.069105 | 0.070517 | 0.12822 | -0.0013587 | -0.0077183 | -0.14511 | -0.010621 | 0.066614 | 0.054194 | 0.007199 | -0.010692 | 76.7944 | 76.9821 | 5.191 | -46.1288 | 77.0279 | -46.0098 | -46.106 | -45.7352 | 3.3783 | -46.0648 | 76.9821 | 76.9043 | -46.138 | -46.2067 | -0.07782 | -0.17395 | 0.082397 | 122.9141 | -0.19684 | -0.022888 | -0.15106 | -0.20599 | -0.27466 | 0.036621 | 0.19684 | -0.13275 | 0.14191 | -0.041199 | 122.9599 | 122.7264 | 51.123 | -123.0515 | 122.9141 | 122.8363 | 49.3103 | -123.1522
2138.0156 | 123.0835 | -45.5338 | 77.2888 | -0.19089 | 0.0080899 | 0.069746 | 0.068808 | 0.12779 | -0.0024269 | -0.0062229 | -0.091705 | -0.009126 | 0.054437 | 0.055689 | 0.0067718 | -0.0085556 | 77.1973 | 77.4078 | 5.365 | -45.7214 | 77.3666 | -45.639 | -45.7306 | -45.5154 | 3.4927 | -45.5704 | 77.3483 | 77.243 | -45.7443 | -45.7993 | -0.10529 | -0.19684 | 0.07782 | 122.9416 | -0.18768 | 0.009155 | -0.091552 | -0.21057 | -0.2655 | 0.05951 | 0.01831 | -0.036622 | 0.22888 | -0.045776 | 122.9004 | 122.731 | 50.8987 | -123.0194 | 122.8821 | 122.7768 | 49.0265 | -123.0881
2139.0156 | 123.0011 | -44.9661 | 77.9251 | -0.20615 | 0.012576 | 0.069319 | 0.074149 | 0.12907 | 0.00077755 | -0.0064365 | -0.23666 | -0.008058 | 0.065119 | 0.056117 | 0.0080536 | -0.012187 | 77.7695 | 77.9388 | 5.4657 | -45.163 | 78.067 | -45.0211 | -45.1126 | -44.7647 | 4.2114 | -45.1263 | 78.1265 | 77.9663 | -45.1172 | -45.1859 | -0.054932 | -0.14648 | 0.14191 | 122.905 | -0.19684 | -0.050354 | -0.15564 | -0.15106 | -0.21973 | 0.20142 | 0.20142 | -0.16022 | 0.059509 | 0.041199 | 123.0331 | 122.7356 | 50.4318 | -123.0377 | 123.0927 | 122.9324 | 49.1776 | -123.111
2140.0156 | 123.0103 | -45.1584 | 77.7512 | 0.076141 | 0.017062 | 0.067823 | 0.071799 | 0.1295 | 0.0018457 | -0.0036595 | 0.0914 | -0.0082716 | 0.067896 | 0.057612 | 0.013608 | -0.011974 | 77.5223 | 77.6138 | 5.4291 | -45.433 | 77.8198 | -45.2911 | -45.369 | -45.1492 | 4.1473 | -45.282 | 77.8564 | 77.7283 | -45.3598 | -45.4239 | -0.13275 | -0.21057 | 0.068664 | 122.7722 | -0.27466 | -0.064086 | -0.22888 | -0.20142 | -0.2655 | 0.10528 | 0.009155 | -0.1236 | 0.14191 | -0.022889 | 122.9782 | 122.6807 | 50.5875 | -123.1201 | 123.0148 | 122.8867 | 49.3057 | -123.175
2141.0156 | 123.0331 | -44.5679 | 78.3234 | -0.21378 | 0.010867 | 0.06761 | 0.069663 | 0.12758 | -0.0030677 | -0.0064365 | -0.17563 | -0.010408 | 0.061487 | 0.058467 | 0.0074126 | -0.01176 | 78.0533 | 78.241 | 5.4382 | -44.8654 | 78.3142 | -44.7327 | -44.7922 | -44.3619 | 3.9413 | -44.6365 | 78.4241 | 78.3463 | -44.7327 | -44.7922 | -0.1648 | -0.2243 | -0.009155 | 122.8088 | -0.29755 | -0.073242 | -0.27008 | -0.1648 | -0.2243 | 0.10071 | 0.20599 | -0.068665 | 0.15564 | 0.022888 | 122.8821 | 122.6212 | 50.0061 | -123.1155 | 122.9919 | 122.9141 | 48.5092 | -123.1155
2142.0156 | 123.1522 | -44.5908 | 78.2913 | -0.14511 | 0.0078763 | 0.071027 | 0.070517 | 0.13142 | -0.0039221 | -0.0064365 | -0.0077819 | -0.01233 | 0.06341 | 0.057398 | 0.0046356 | -0.011546 | 78.1998 | 78.4287 | 5.0262 | -44.6869 | 78.447 | -44.5541 | -44.6777 | -44.4122 | 4.0375 | -44.7556 | 78.2089 | 78.1631 | -44.8517 | -44.9112 | 0.036621 | -0.086975 | 0.15564 | 123.0194 | -0.096131 | -0.009156 | -0.091553 | -0.26093 | -0.32044 | -0.082398 | 0.17853 | -0.16479 | 0.15564 | -0.12817 | 123.0377 | 122.7905 | 49.617 | -122.9691 | 122.7997 | 122.7539 | 48.6282 | -123.2025
2143.0156 | 123.056 | -43.7485 | 79.1336 | -0.21378 | 0.01044 | 0.071668 | 0.069876 | 0.128 | -0.00029045 | -0.0049411 | -0.14511 | -0.009126 | 0.060205 | 0.058253 | 0.0082672 | -0.011546 | 79.0009 | 79.2114 | 5.4703 | -43.9041 | 79.2252 | -43.7988 | -43.9224 | -43.5013 | 4.3533 | -43.8171 | 79.2068 | 79.1016 | -43.9453 | -43.9774 | -0.050354 | -0.17395 | 0.091553 | 122.9599 | -0.15564 | 0.01831 | -0.13275 | -0.19684 | -0.22888 | 0.073242 | 0.24719 | -0.068665 | 0.16022 | -0.032044 | 122.9736 | 122.7493 | 49.2188 | -123.056 | 122.9553 | 122.85 | 48.1018 | -123.111
2144.0156 | 123.0698 | -44.957 | 77.9114 | 0.19821 | 0.0061673 | 0.06825 | 0.067313 | 0.12993 | -0.0030677 | -0.0075047 | 0.10666 | -0.0093396 | 0.061487 | 0.057398 | 0.0084808 | -0.0096238 | 77.8931 | 78.1403 | 5.2048 | -45.0806 | 78.0899 | -44.9753 | -45.0897 | -44.6915 | 3.9368 | -44.9844 | 78.0258 | 77.8839 | -45.1401 | -45.1904 | -0.018311 | -0.13275 | 0.17853 | 123.0972 | -0.1236 | 0.009156 | -0.018311 | -0.18311 | -0.23346 | 0.11444 | 0.2655 | -0.027466 | 0.20599 | -0.027466 | 123.0469 | 122.85 | 50.1617 | -123.0011 | 122.9828 | 122.8409 | 48.8937 | -123.1018
2145.0156 | 123.0698 | -44.2108 | 78.6758 | -0.0077822 | 0.016421 | 0.066969 | 0.074576 | 0.12886 | 0.0039819 | -0.0051547 | -0.13748 | -0.0086988 | 0.066187 | 0.058253 | 0.0076264 | -0.01411 | 78.5522 | 78.6575 | 5.127 | -44.4031 | 78.7949 | -44.2886 | -44.3848 | -44.0323 | 3.9963 | -44.4077 | 78.7537 | 78.6484 | -44.4214 | -44.4626 | -0.07782 | -0.17395 | 0.11902 | 122.8683 | -0.19226 | -0.01831 | -0.1236 | -0.21057 | -0.25177 | 0.07782 | 0.17853 | -0.19684 | 0.054931 | -0.027466 | 123.0057 | 122.7631 | 49.3378 | -123.0606 | 122.9645 | 122.8592 | 48.2071 | -123.1384
2146.0156 | 123.1338 | -44.2291 | 78.6209 | -0.084076 | 0.0072355 | 0.069105 | 0.068381 | 0.13142 | -0.0047767 | -0.0064365 | -0.015411 | -0.009126 | 0.061273 | 0.05633 | 0.0057038 | -0.010692 | 78.4882 | 78.6896 | 5.1498 | -44.4305 | 78.7079 | -44.3344 | -44.4077 | -43.9865 | 3.7079 | -44.2612 | 78.685 | 78.5889 | -44.426 | -44.4809 | -0.10529 | -0.17853 | 0.086975 | 122.9187 | -0.20142 | -0.022888 | -0.13275 | -0.19684 | -0.25177 | 0.064087 | 0.24262 | -0.032043 | 0.21973 | -0.032044 | 122.937 | 122.7173 | 49.379 | -123.0286 | 122.9141 | 122.818 | 47.937 | -123.1018
2147.0156 | 123.0972 | -44.6823 | 78.154 | 0.21347 | 0.0087307 | 0.068678 | 0.07244 | 0.1295 | -0.0015723 | -0.0057957 | -0.099335 | -0.0095532 | 0.061701 | 0.057185 | 0.00784 | -0.011333 | 78.0579 | 78.3234 | 5.2551 | -44.5679 | 78.4103 | -44.5358 | -44.5908 | -44.1055 | 3.5797 | -44.664 | 78.5065 | 78.3234 | -44.7418 | -44.8746 | 0.14648 | 0.091553 | 0.25635 | 123.0057 | 0.11444 | 0.022888 | -0.096131 | -0.059509 | -0.19226 | 0.35248 | 0.57678 | 0.018311 | 0.21057 | 0.16937 | 123.0927 | 122.7402 | 49.9374 | -122.7448 | 123.1888 | 123.0057 | 48.262 | -123.0286
2148.0156 | 123.1155 | -47.8134 | 75.0458 | -0.03067 | 0.0065945 | 0.068037 | 0.07009 | 0.1295 | -0.00050425 | -0.0085727 | -0.038299 | -0.0078442 | 0.060205 | 0.057398 | 0.00784 | -0.0096238 | 74.6841 | 74.8993 | 4.2847 | -48.1522 | 74.9725 | -48.056 | -48.1155 | -47.5479 | 2.6962 | -47.8638 | 75.1053 | 75 | -48.0011 | -48.0469 | -0.24261 | -0.30212 | -0.073242 | 122.7127 | -0.33875 | -0.036621 | -0.36163 | -0.18768 | -0.23346 | 0.05951 | 0.2655 | -0.050354 | 0.1831 | -0.045776 | 122.7859 | 122.4976 | 52.0981 | -123.1613 | 122.9187 | 122.8134 | 50.5096 | -123.0927
2149.0156 | 123.111 | -47.8409 | 74.9954 | -0.20615 | 0.0087307 | 0.069532 | 0.072012 | 0.12928 | -0.0019995 | -0.0072911 | -1.465 | -0.011689 | 0.062342 | 0.05868 | 0.007199 | -0.013683 | 74.9039 | 75.1236 | 4.5502 | -48.0148 | 75.0412 | -47.9462 | -48.056 | -47.406 | 3.0075 | -47.9782 | 75.0687 | 74.9725 | -48.0515 | -48.1155 | -0.10529 | -0.21515 | 0.045777 | 122.9645 | -0.17395 | 0.041198 | -0.091552 | -0.21057 | -0.27466 | 0.073243 | 0.43488 | -0.13733 | 0.13733 | -0.022888 | 122.8821 | 122.7448 | 52.3911 | -123.0515 | 122.9095 | 122.8134 | 50.8484 | -123.111
2150.0156 | 123.0743 | -47.9919 | 74.8947 | -0.053558 | 0.016421 | 0.066328 | 0.075858 | 0.13078 | 0.0067589 | -0.0057957 | -0.038299 | -0.0095532 | 0.064264 | 0.05868 | 0.0082672 | -0.013469 | 75 | 75.1236 | 4.3579 | -47.9691 | 75.2563 | -47.8363 | -47.9141 | -47.3648 | 2.9114 | -48.0698 | 75.2747 | 75.0458 | -48.0881 | -48.2117 | 0.15564 | 0.077819 | 0.36163 | 123.1155 | 0.022888 | -0.054931 | 0.10529 | -0.096131 | -0.21973 | 0.37994 | 0.62714 | -0.07782 | 0.14191 | 0.15106 | 123.2483 | 122.9919 | 52.3499 | -122.8088 | 123.2666 | 123.0377 | 50.9033 | -123.1064
2151.0156 | 123.111 | -46.8109 | 76.0437 | 0.022736 | 0.0046719 | 0.069105 | 0.066885 | 0.12886 | -0.0054175 | -0.0068637 | 0.045624 | -0.010408 | 0.061487 | 0.05633 | 0.0065582 | -0.0094102 | 75.8194 | 76.0529 | 4.7104 | -47.0306 | 76.0849 | -46.9025 | -47.0306 | -46.6095 | 3.2593 | -46.756 | 76.0941 | 76.0162 | -46.9894 | -47.0444 | -0.091553 | -0.21973 | 0.041199 | 122.8638 | -0.21973 | 0 | -0.2243 | -0.17853 | -0.23346 | 0.050354 | 0.20142 | 0.054932 | 0.28839 | -0.027466 | 122.8958 | 122.6303 | 51.5213 | -123.0743 | 122.905 | 122.8271 | 50.0702 | -123.0881
2152.0156 | 123.0881 | -46.1105 | 76.7853 | 0.12955 | 0.0070217 | 0.06825 | 0.071158 | 0.12864 | -0.0049903 | -0.0077183 | 0.0914 | -0.011689 | 0.061914 | 0.058253 | 0.0052764 | -0.010051 | 76.4374 | 76.6388 | 4.3991 | -46.4401 | 76.6891 | -46.2982 | -46.376 | -45.8313 | 3.1403 | -46.1655 | 76.8082 | 76.6983 | -46.3165 | -46.3669 | -0.18768 | -0.2655 | -0.09613 | 122.7493 | -0.32959 | -0.064087 | -0.3479 | -0.20599 | -0.25635 | 0.022889 | 0.27924 | -0.054931 | 0.20142 | -0.086975 | 122.7997 | 122.5479 | 50.5096 | -123.1613 | 122.9187 | 122.8088 | 49.2508 | -123.1522
2153.0156 | 123.1293 | -47.1909 | 75.6088 | -0.10696 | 0.0070217 | 0.069959 | 0.070517 | 0.12843 | -0.0034949 | -0.0064365 | -0.10696 | -0.010408 | 0.06106 | 0.054194 | 0.0067718 | -0.011546 | 75.325 | 75.5219 | 4.0466 | -47.5708 | 75.5493 | -47.4518 | -47.5525 | -46.8842 | 2.916 | -47.1863 | 75.7187 | 75.5997 | -47.3969 | -47.4426 | -0.26093 | -0.36163 | -0.05951 | 122.7127 | -0.37994 | -0.018311 | -0.28381 | -0.20599 | -0.25177 | 0.10986 | 0.3067 | 0.004578 | 0.25635 | -0.009156 | 122.7402 | 122.5159 | 51.2375 | -123.1613 | 122.9095 | 122.7905 | 50.1068 | -123.0515
2154.0156 | 123.0652 | -47.6212 | 75.206 | -0.068817 | 0.0083035 | 0.069959 | 0.071372 | 0.12907 | -0.0017859 | -0.0096409 | 0.09903 | -0.0095532 | 0.060419 | 0.056117 | 0.0069854 | -0.0091966 | 75.2014 | 75.3891 | 4.2801 | -47.7036 | 75.4349 | -47.5708 | -47.6669 | -47.3602 | 2.4857 | -47.7081 | 75.3204 | 75.238 | -47.7722 | -47.8409 | 0.050354 | -0.045776 | 0.22888 | 123.0103 | -0.082397 | -0.036621 | -0.004578 | -0.15106 | -0.21973 | 0.11444 | 0.26093 | -0.086975 | 0.13275 | 0.032043 | 123.056 | 122.8226 | 51.9012 | -122.8729 | 122.9416 | 122.8592 | 50.1068 | -123.0469
2155.0156 | 122.9874 | -48.7701 | 74.1074 | 0.0074768 | 0.016635 | 0.06526 | 0.073081 | 0.12822 | 0.0044091 | -0.0034457 | -0.053558 | -0.0050672 | 0.064691 | 0.056758 | 0.010831 | -0.014751 | 73.9838 | 74.0753 | 3.8818 | -48.9716 | 74.2264 | -48.848 | -48.9624 | -48.5367 | 2.0416 | -49.0265 | 74.2493 | 74.1028 | -48.967 | -49.0173 | -0.077819 | -0.19226 | 0.11902 | 122.8455 | -0.20142 | -0.009156 | -0.1236 | -0.19684 | -0.24719 | 0.14191 | 0.23346 | -0.25635 | -0.009155 | -0.004578 | 122.9965 | 122.7539 | 52.652 | -123.0698 | 123.0194 | 122.8729 | 50.8118 | -123.1247
2156.0156 | 123.0927 | -47.7631 | 75.0778 | 0.13718 | 0.0053129 | 0.067823 | 0.068594 | 0.13014 | -0.0028541 | -0.0036595 | 0.20584 | -0.0099806 | 0.06341 | 0.059107 | 0.007199 | -0.0081284 | 75.119 | 75.3296 | 4.1519 | -47.7814 | 75.3342 | -47.6715 | -47.7356 | -47.5159 | 2.5635 | -47.9279 | 75.1602 | 75.0687 | -47.9553 | -48.0011 | 0.091553 | 0.027466 | 0.25635 | 123.0927 | -0.01831 | -0.045776 | 0.041199 | -0.19226 | -0.23804 | 0.082397 | 0.24719 | -0.16479 | 0.073243 | -0.009155 | 123.0972 | 122.8821 | 51.915 | -122.8134 | 122.9233 | 122.8317 | 50.3265 | -123.0789
2157.0156 | 123.111 | -47.2641 | 75.6363 | 0.099029 | 0.0085171 | 0.068891 | 0.068167 | 0.13014 | -0.00093145 | -0.0068637 | 0.09903 | -0.0093396 | 0.061914 | 0.058039 | 0.0084808 | -0.010692 | 75.2884 | 75.499 | 4.1931 | -47.6395 | 75.5127 | -47.5525 | -47.6395 | -47.1451 | 2.9938 | -47.5159 | 75.5219 | 75.412 | -47.5662 | -47.5845 | -0.28839 | -0.37537 | -0.1236 | 122.7631 | -0.37537 | 0 | -0.3479 | -0.30212 | -0.32043 | -0.11444 | 0.11902 | -0.25177 | 0.068665 | -0.22431 | 122.7768 | 122.5525 | 51.4572 | -123.2758 | 122.7859 | 122.6761 | 50.2579 | -123.2208
2158.0156 | 123.1155 | -46.7697 | 76.0574 | 0.099029 | 0.010653 | 0.068464 | 0.072012 | 0.128 | 0.0012047 | -0.0036595 | 0.19058 | -0.011903 | 0.062769 | 0.054835 | 0.0084808 | -0.010692 | 75.8469 | 76.0162 | 4.4174 | -47.0856 | 76.0529 | -46.9711 | -47.0444 | -46.5729 | 3.0487 | -47.113 | 76.0712 | 75.9476 | -47.0306 | -47.0261 | -0.20142 | -0.27466 | -0.004578 | 122.7859 | -0.31586 | -0.041198 | -0.21057 | -0.26093 | -0.25635 | 0.013733 | 0.19684 | -0.34332 | -0.086975 | -0.10986 | 122.8226 | 122.6166 | 51.1871 | -123.1018 | 122.8409 | 122.7173 | 49.8184 | -123.0835
2159.0156 | 123.1476 | -46.6095 | 76.2543 | 0.18295 | 0.0078763 | 0.068464 | 0.069022 | 0.12672 | -0.0022131 | -0.0051547 | 0.10666 | -0.0076306 | 0.060633 | 0.056758 | 0.00784 | -0.010478 | 76.4008 | 76.5152 | 4.7699 | -46.6003 | 76.5793 | -46.4447 | -46.5454 | -46.4218 | 3.1357 | -46.7148 | 76.3092 | 76.2268 | -46.788 | -46.8109 | 0.16479 | 0.064087 | 0.32501 | 123.1247 | 0.009155 | -0.054932 | 0.14648 | -0.17853 | -0.20142 | 0.054932 | 0.18768 | -0.10529 | 0.09613 | -0.027465 | 123.1888 | 123.0103 | 51.3794 | -122.7997 | 122.9187 | 122.8363 | 49.7452 | -123.0652
2160.0156 | 123.111 | -46.8979 | 75.9247 | 0.14481 | 0.011294 | 0.069105 | 0.071799 | 0.1295 | 0.00099115 | -0.0051547 | 0.18295 | -0.0097668 | 0.061487 | 0.056758 | 0.00784 | -0.010478 | 75.705 | 75.943 | 4.6005 | -47.1268 | 75.9842 | -47.0169 | -47.081 | -46.7331 | 3.1952 | -47.168 | 75.9247 | 75.8148 | -47.1497 | -47.1817 | -0.11902 | -0.18311 | 0.059509 | 122.8409 | -0.22888 | -0.045776 | -0.21973 | -0.25177 | -0.28381 | 0 | 0.1648 | -0.27008 | 0.013733 | -0.10986 | 122.8821 | 122.6028 | 51.4984 | -123.0057 | 122.8226 | 122.7127 | 50.0931 | -123.1064
2161.0156 | 123.1064 | -46.3486 | 76.5244 | 0.0074768 | 0.0050991 | 0.069532 | 0.070944 | 0.13142 | -0.0019995 | -0.0077183 | 0.10666 | -0.009126 | 0.061914 | 0.056117 | 0.0074126 | -0.011974 | 76.355 | 76.5198 | 4.8431 | -46.6141 | 76.593 | -46.4539 | -46.5454 | -46.0876 | 3.5431 | -46.5271 | 76.5472 | 76.442 | -46.5591 | -46.6003 | -0.10529 | -0.19684 | 0.068665 | 122.8683 | -0.2655 | -0.068665 | -0.16937 | -0.21057 | -0.25177 | 0.022888 | 0.26093 | -0.17853 | 0.073242 | -0.082397 | 122.9416 | 122.7036 | 51.1917 | -123.0698 | 122.8958 | 122.7905 | 49.8917 | -123.1247
2162.0156 | 123.1064 | -46.0007 | 76.8127 | 0.17532 | 0.013003 | 0.069319 | 0.071372 | 0.12971 | -0.0015723 | -0.0045139 | 0.015106 | -0.010621 | 0.062982 | 0.056758 | 0.0086944 | -0.011546 | 76.8539 | 76.6754 | 4.9164 | -46.0968 | 76.8723 | -46.0876 | -46.1655 | -45.8084 | 3.6758 | -46.138 | 76.8768 | 76.7395 | -46.2341 | -46.2753 | -0.086975 | -0.1648 | 0.059509 | 122.6761 | -0.096131 | 0.068664 | 0.041199 | -0.23346 | -0.27466 | 0.064087 | 0.19226 | -0.13733 | 0.13733 | -0.073242 | 122.8729 | 122.8546 | 50.9171 | -122.9782 | 122.8775 | 122.7402 | 49.6765 | -123.0881
2163.0156 | 123.0789 | -45.8817 | 76.9867 | 0.12955 | 0.0093717 | 0.070387 | 0.069449 | 0.12864 | -0.0019995 | -0.0060093 | 0.16769 | -0.010835 | 0.059564 | 0.05633 | 0.0082672 | -0.010265 | 76.8539 | 77.0233 | 5.1132 | -46.0739 | 77.0966 | -45.9366 | -46.0052 | -45.6161 | 3.7125 | -46.0419 | 77.0737 | 76.973 | -46.0831 | -46.1334 | -0.054931 | -0.1236 | 0.10986 | 122.905 | -0.19226 | -0.068665 | -0.13275 | -0.20142 | -0.25177 | 0.086975 | 0.2655 | -0.16022 | 0.091553 | -0.013733 | 122.9782 | 122.7356 | 50.9949 | -122.9919 | 122.9553 | 122.8546 | 49.5941 | -123.1201
2164.0156 | 123.0743 | -46.1197 | 76.712 | 0.16006 | 0.014285 | 0.069319 | 0.07479 | 0.12928 | 0.0039819 | -0.0034457 | 0.11429 | -0.0084852 | 0.062982 | 0.057826 | 0.0084808 | -0.011974 | 76.8906 | 76.9867 | 5.0491 | -46.1563 | 77.1332 | -45.9869 | -46.0876 | -45.726 | 3.6942 | -46.1105 | 77.0233 | 76.886 | -46.1792 | -46.2708 | 0.13275 | 0.032044 | 0.42114 | 123.1064 | -0.036621 | -0.068665 | 0.17853 | -0.059509 | -0.15106 | 0.31128 | 0.39368 | 0.009155 | 0.16022 | 0.17395 | 123.2529 | 123.0103 | 51.1688 | -122.7997 | 123.143 | 123.0057 | 49.8138 | -122.9828
2165.0156 | 123.111 | -45.9915 | 76.8036 | 0.16006 | 0.013431 | 0.069319 | 0.068594 | 0.13057 | 0.00013675 | -0.0040867 | 1.6554 | -0.0061352 | 0.061701 | 0.05633 | 0.011044 | -0.011546 | 76.7532 | 76.9089 | 5.0949 | -46.1746 | 76.9226 | -46.0693 | -46.1746 | -45.7672 | 3.8223 | -46.1288 | 76.8997 | 76.7578 | -46.2021 | -46.2341 | -0.07782 | -0.18311 | 0.11902 | 122.9004 | -0.18311 | 0 | -0.050354 | -0.21057 | -0.24262 | 0.09613 | 0.2243 | -0.13733 | 0.10529 | -0.045777 | 122.9141 | 122.7448 | 51.0864 | -122.9782 | 122.8912 | 122.7493 | 49.8138 | -123.0377
2166.0156 | 123.1338 | -45.9137 | 76.9089 | 0.13718 | 0.013431 | 0.068464 | 0.06774 | 0.12907 | 0.0014185 | -0.0025913 | 0.17532 | -0.007417 | 0.061914 | 0.056544 | 0.00784 | -0.013255 | 76.7899 | 76.8951 | 5.0949 | -46.0739 | 76.9867 | -45.9961 | -46.0373 | -45.4742 | 3.9368 | -45.607 | 77.1652 | 77.0325 | -46.0098 | -46.0648 | -0.082398 | -0.1236 | 0.077819 | 122.8088 | -0.16022 | -0.036622 | -0.11902 | -0.096131 | -0.15106 | 0.25635 | 0.43945 | 0.3067 | 0.45776 | 0.1236 | 122.9004 | 122.7036 | 51.0086 | -122.9462 | 123.0789 | 122.9462 | 49.8505 | -122.9736
2167.0156 | 123.1064 | -45.5933 | 77.2385 | 0.14481 | 0.011294 | 0.066755 | 0.067526 | 0.128 | -0.0022131 | -0.0040867 | 0.21347 | -0.0086988 | 0.062342 | 0.055049 | 0.007199 | -0.0079148 | 77.0187 | 77.2339 | 5.1407 | -45.8633 | 77.2476 | -45.7581 | -45.8221 | -45.3827 | 4.0878 | -45.6802 | 77.2888 | 77.2064 | -45.8084 | -45.8405 | -0.16479 | -0.22888 | 0.009156 | 122.8271 | -0.27008 | -0.041198 | -0.21973 | -0.21515 | -0.24719 | 0.050354 | 0.21057 | -0.086975 | 0.16022 | -0.032043 | 122.8409 | 122.612 | 50.7339 | -123.0606 | 122.8821 | 122.7997 | 49.6811 | -123.0789
2168.0156 | 123.0927 | -45.1721 | 77.7054 | 0.18295 | 0.013858 | 0.069319 | 0.073081 | 0.13185 | 0.0029137 | -0.0025913 | 0.19821 | -0.007417 | 0.064051 | 0.056971 | 0.0097626 | -0.013255 | 77.6596 | 77.774 | 5.1636 | -45.3552 | 77.8702 | -45.1904 | -45.2866 | -45.0302 | 3.4332 | -45.3644 | 77.7283 | 77.6138 | -45.401 | -45.4102 | -0.018311 | -0.11444 | 0.16479 | 122.9462 | -0.18311 | -0.068665 | -0.045776 | -0.22888 | -0.23804 | 0.022888 | 0.14191 | -0.19226 | 0.045776 | -0.091552 | 123.0423 | 122.8317 | 50.3357 | -122.9919 | 122.9004 | 122.786 | 48.6053 | -123.1155
2169.0156 | 123.1064 | -44.1055 | 78.7628 | 0.36606 | 0.01279 | 0.069319 | 0.068594 | 0.12971 | -0.00093145 | -0.0064365 | 0.16769 | -0.0082716 | 0.060846 | 0.056971 | 0.0084808 | -0.010478 | 78.4698 | 78.6758 | 5.4062 | -44.4077 | 78.6896 | -44.2932 | -44.3939 | -43.9041 | 4.1748 | -44.046 | 78.7949 | 78.7079 | -44.2978 | -44.3207 | -0.18768 | -0.28839 | -0.073242 | 122.7814 | -0.30212 | -0.013733 | -0.29297 | -0.19226 | -0.21515 | 0.032044 | 0.20142 | 0.059509 | 0.27466 | -0.054931 | 122.7951 | 122.5754 | 49.5117 | -123.1567 | 122.9004 | 122.8134 | 48.2803 | -123.0835
2170.0156 | 122.9874 | -47.2733 | 75.6317 | 0.13718 | 0.018344 | 0.068464 | 0.073081 | 0.128 | 0.0029137 | -0.0032321 | 3.7383 | -0.0061352 | 0.061273 | 0.056544 | 0.011044 | -0.010265 | 75.4486 | 75.5539 | 4.6005 | -47.4884 | 75.7553 | -47.3419 | -47.4014 | -47.1542 | 3.2043 | -47.438 | 75.7462 | 75.618 | -47.4564 | -47.5159 | -0.068665 | -0.12817 | 0.1236 | 122.8271 | -0.21515 | -0.086975 | -0.18311 | -0.18311 | -0.24262 | 0.11444 | 0.11902 | -0.16479 | 0.07782 | -0.013733 | 123.0286 | 122.7219 | 51.8738 | -123.0331 | 123.0194 | 122.8912 | 50.4776 | -123.1476
2171.0156 | 123.0972 | -45.7581 | 77.0416 | 0.17532 | 0.015353 | 0.06825 | 0.072012 | 0.13121 | -0.0022131 | -0.0049411 | 0.2211 | -0.0082716 | 0.062342 | 0.056544 | 0.011472 | -0.0098374 | 77.2522 | 77.3849 | 5.0217 | -45.694 | 77.5085 | -45.5429 | -45.6665 | -45.1675 | 3.9322 | -45.7443 | 77.4216 | 77.2568 | -45.7947 | -45.8954 | 0.21515 | 0.091553 | 0.46692 | 123.143 | 0.064087 | -0.027466 | 0.21057 | -0.036621 | -0.13733 | 0.37994 | 0.59052 | 0.013733 | 0.15106 | 0.21515 | 123.2666 | 123.0103 | 50.7797 | -122.7081 | 123.1796 | 123.0148 | 49.6902 | -122.937
2172.0156 | 123.0103 | -45.5154 | 77.4216 | 0.11429 | 0.016421 | 0.064832 | 0.067313 | 0.12779 | -0.0032813 | -0.0049411 | 0.28976 | -0.0076306 | 0.064478 | 0.057826 | 0.011044 | -0.010051 | 77.3438 | 77.3071 | 5.0629 | -45.6345 | 77.5406 | -45.5383 | -45.6619 | -45.2728 | 4.184 | -45.6619 | 77.504 | 77.3941 | -45.6757 | -45.7352 | -0.022888 | -0.14648 | 0.11902 | 122.8226 | -0.11902 | 0.027466 | -0.07782 | -0.16022 | -0.21973 | 0.082397 | 0.24262 | -0.14648 | 0.073242 | -0.027466 | 123.056 | 122.8592 | 50.5783 | -123.0835 | 123.0194 | 122.9095 | 49.6994 | -123.1567
2173.0156 | 123.1384 | -47.5754 | 75.2289 | 0.19058 | 0.010867 | 0.065901 | 0.066885 | 0.12907 | -7.6852e-05 | -0.0049411 | 0.045624 | -0.0082716 | 0.061273 | 0.057185 | 0.007199 | -0.010478 | 75.0137 | 75.3708 | 4.747 | -47.8729 | 75.238 | -47.7631 | -47.8592 | -47.2733 | 3.4332 | -47.58 | 75.3342 | 75.2609 | -47.7631 | -47.818 | -0.18768 | -0.28381 | 0.009155 | 122.9462 | -0.29755 | -0.013733 | -0.21515 | -0.18768 | -0.24262 | 0.10528 | 0.30212 | -0.004578 | 0.23804 | 0.032043 | 122.8134 | 122.5891 | 52.3224 | -123.0881 | 122.9095 | 122.8363 | 51.0086 | -123.0469
2174.0156 | 123.0469 | -46.2982 | 76.5656 | 0.083771 | 0.017062 | 0.069746 | 0.070517 | 0.13142 | 0.00099115 | -0.0051547 | 0.15244 | -0.0078442 | 0.062769 | 0.055049 | 0.0082672 | -0.0091966 | 76.474 | 76.5701 | 4.7699 | -46.4035 | 76.7899 | -46.2616 | -46.3394 | -45.8954 | 3.4058 | -46.2112 | 76.8997 | 76.7807 | -46.3211 | -46.4493 | 0.036621 | -0.041199 | 0.2243 | 122.8683 | -0.10529 | -0.064086 | -0.091553 | -0.022888 | -0.15106 | 0.33417 | 0.40283 | 0.086975 | 0.23804 | 0.21515 | 123.0881 | 122.7722 | 51.0681 | -122.905 | 123.1979 | 123.0789 | 49.704 | -123.0148
2175.0156 | 123.1384 | -45.3873 | 77.504 | 0.38132 | 0.01044 | 0.067396 | 0.067526 | 0.1295 | -0.00050425 | -0.0034457 | 0.23636 | -0.0076306 | 0.059992 | 0.057185 | 0.008908 | -0.0098374 | 77.33 | 77.4536 | 5.0308 | -45.639 | 77.4994 | -45.5154 | -45.5795 | -45.0714 | 3.5156 | -45.5612 | 77.5269 | 77.4307 | -45.5795 | -45.5978 | -0.12817 | -0.19226 | -0.004577 | 122.8409 | -0.25177 | -0.059509 | -0.17395 | -0.19226 | -0.21057 | 0.022888 | 0.31586 | -0.17395 | 0.036621 | -0.073242 | 122.8867 | 122.7173 | 50.4181 | -123.0835 | 122.9141 | 122.818 | 48.9029 | -123.1018
2176.0156 | 123.0148 | -46.637 | 76.2817 | 0.13718 | 0.019626 | 0.06291 | 0.071158 | 0.128 | 0.0020593 | -0.0053683 | 0.11429 | -0.0076306 | 0.066828 | 0.058253 | 0.008908 | -0.011119 | 76.1444 | 76.5244 | 4.715 | -46.6919 | 76.5839 | -46.5042 | -46.6095 | -46.344 | 3.1219 | -46.6827 | 76.5015 | 76.3367 | -46.7972 | -46.8475 | 0.13275 | 0.027466 | 0.30212 | 123.1613 | -0.054932 | -0.082398 | -0.13733 | -0.16022 | -0.21057 | 0.21973 | 0.29297 | -0.045776 | 0.1648 | 0.054932 | 123.2208 | 122.7814 | 51.3519 | -122.8912 | 123.1384 | 122.9736 | 49.7589 | -123.1293
2177.0156 | 123.1384 | -46.1838 | 76.6525 | 0.19821 | 0.013431 | 0.06825 | 0.070303 | 0.1327 | -0.00050425 | -0.0034457 | 0.30502 | -0.008058 | 0.062128 | 0.056544 | 0.0099762 | -0.010478 | 76.6022 | 76.8036 | 4.9164 | -46.312 | 76.8219 | -46.2021 | -46.3074 | -45.9274 | 3.0441 | -46.2616 | 76.7395 | 76.6434 | -46.3852 | -46.431 | -0.01831 | -0.1236 | 0.16937 | 122.9874 | -0.12817 | -0.004578 | -0.050354 | -0.20142 | -0.24719 | 0.086975 | 0.25635 | -0.07782 | 0.16937 | -0.009155 | 123.0057 | 122.7859 | 51.1002 | -122.9599 | 122.9233 | 122.8271 | 49.2279 | -123.0835
2178.0156 | 122.9919 | -46.9803 | 75.9384 | 0.045624 | 0.015994 | 0.06825 | 0.071158 | 0.12993 | 0.0016321 | -0.0043003 | -0.015411 | -0.0061352 | 0.062555 | 0.058894 | 0.0074126 | -0.012828 | 75.499 | 75.6088 | 4.4083 | -47.4106 | 75.856 | -47.2321 | -47.3099 | -46.7789 | 3.0441 | -47.2229 | 75.9888 | 75.9567 | -47.1588 | -47.2229 | -0.25177 | -0.32959 | -0.082398 | 122.5891 | -0.4303 | -0.10071 | -0.43945 | -0.17853 | -0.24261 | 0.050354 | 0.20142 | -0.24261 | 0 | 0.01831 | 122.8363 | 122.4792 | 51.3886 | -123.2483 | 122.9691 | 122.937 | 50.0244 | -123.1613
2179.0156 | 123.1247 | -47.6257 | 75.2243 | 0.17532 | 0.013644 | 0.06761 | 0.068808 | 0.13163 | -0.0015723 | -0.0045139 | 0.24399 | -0.0097668 | 0.064691 | 0.058253 | 0.0097626 | -0.01176 | 75.1373 | 75.2335 | 4.3854 | -47.7951 | 75.3891 | -47.6303 | -47.7264 | -47.2687 | 2.9663 | -47.7219 | 75.3571 | 75.293 | -47.7859 | -47.8226 | -0.004578 | -0.10071 | 0.16479 | 122.8592 | -0.16937 | -0.068665 | -0.086975 | -0.16022 | -0.19684 | 0.13275 | 0.35706 | -0.096131 | 0.10071 | 0.068665 | 123.0148 | 122.7631 | 52.0111 | -122.9507 | 122.9828 | 122.9187 | 50.592 | -123.0469
2180.0156 | 123.0103 | -47.8226 | 75.0824 | -0.71732 | 0.01279 | 0.070387 | 0.071799 | 0.13078 | 0.00077755 | -0.0051547 | 0.15244 | -0.0069898 | 0.064051 | 0.059748 | 0.0084808 | -0.010692 | 75.0504 | 75.1373 | 4.4998 | -47.8821 | 75.3845 | -47.7493 | -47.85 | -47.644 | 2.98 | -48.0698 | 75.1602 | 75.0732 | -48.0103 | -48.0698 | 0.073242 | -0.027466 | 0.30212 | 122.9599 | -0.059509 | -0.032043 | -0.032043 | -0.18768 | -0.24719 | 0.07782 | 0.17853 | -0.24719 | 0 | -0.009155 | 123.2071 | 122.8729 | 52.3224 | -122.9324 | 122.9828 | 122.8958 | 50.8026 | -123.1522
2181.0156 | 123.1842 | -47.4518 | 75.3204 | 0.33554 | 0.014926 | 0.068891 | 0.070517 | 0.13057 | -0.0011451 | -0.0047275 | 0.28214 | -0.0089124 | 0.061914 | 0.05633 | 0.0076264 | -0.0089828 | 75.0961 | 75.293 | 4.5914 | -47.7173 | 75.3204 | -47.6395 | -47.699 | -47.1771 | 3.2227 | -47.4518 | 75.4486 | 75.3662 | -47.6807 | -47.6944 | -0.18768 | -0.24719 | 0 | 122.7448 | -0.2655 | -0.01831 | -0.22431 | -0.22888 | -0.24262 | 0.12817 | 0.27466 | 0 | 0.24262 | 0.045776 | 122.7722 | 122.5479 | 52.0432 | -123.0194 | 122.9004 | 122.818 | 50.6744 | -123.0148
2182.0156 | 123.0377 | -48.2666 | 74.6109 | 0.0914 | 0.015567 | 0.068464 | 0.071585 | 0.13014 | 0.0022729 | -0.0045139 | -0.59525 | -0.0076306 | 0.064264 | 0.057826 | 0.006131 | -0.0098374 | 74.6384 | 74.3042 | 4.1107 | -48.23 | 74.8398 | -48.2666 | -48.3444 | -48.0698 | 2.5955 | -48.4406 | 74.7437 | 74.6475 | -48.4772 | -48.5046 | 0 | -0.077819 | 0.22888 | 122.5708 | 0.036622 | 0.11444 | 0.027466 | -0.21057 | -0.23804 | 0.13275 | 0.19684 | -0.17395 | 0.064087 | 0.036621 | 123.1064 | 122.905 | 52.3773 | -122.9553 | 123.0103 | 122.9141 | 50.8621 | -123.1155
2183.0156 | 123.143 | -47.2549 | 75.5859 | 0.17532 | 0.014071 | 0.068678 | 0.069876 | 0.128 | -0.0019995 | -0.0036595 | 0.53391 | -0.0069898 | 0.061273 | 0.057185 | 0.0065582 | -0.0094102 | 75.618 | 75.7416 | 4.6326 | -47.3145 | 75.8194 | -47.2092 | -47.287 | -46.9803 | 3.1219 | -47.3465 | 75.6821 | 75.618 | -47.4289 | -47.4884 | 0.045777 | -0.032043 | 0.23346 | 122.9965 | -0.059509 | -0.027466 | 0.032044 | -0.17395 | -0.23346 | 0.096131 | 0.27466 | -0.091553 | 0.14191 | 0.032044 | 123.0743 | 122.8729 | 51.8875 | -122.8729 | 122.937 | 122.8729 | 50.3769 | -123.0743
2184.0156 | 123.0331 | -45.9778 | 76.9455 | 0.037994 | 0.016849 | 0.065687 | 0.07009 | 0.12907 | 0.00035035 | -0.0068637 | 0.022736 | -0.0061352 | 0.065332 | 0.059962 | 0.0086944 | -0.011974 | 76.6571 | 76.799 | 4.8614 | -46.2067 | 76.9821 | -46.0968 | -46.1655 | -45.8176 | 3.0853 | -46.0968 | 77.0096 | 76.9272 | -46.1517 | -46.2204 | -0.11902 | -0.18768 | 0.036621 | 122.7768 | -0.22888 | -0.041199 | -0.28839 | -0.17395 | -0.24262 | 0.064087 | 0.16022 | -0.11902 | 0.1236 | -0.018311 | 122.9599 | 122.6349 | 50.8392 | -123.111 | 122.9874 | 122.905 | 49.0631 | -123.1659
2185.0156 | 123.0286 | -46.138 | 76.767 | 0.33554 | 0.011081 | 0.069105 | 0.067526 | 0.12993 | 0.00056395 | -0.0038731 | 0.2211 | -0.008058 | 0.064478 | 0.057612 | 0.008908 | -0.010265 | 76.5564 | 76.6846 | 4.7562 | -46.3303 | 76.8906 | -46.1884 | -46.257 | -45.8313 | 3.3096 | -46.051 | 76.9821 | 76.9318 | -46.225 | -46.2936 | -0.050354 | -0.11902 | 0.1236 | 122.8226 | -0.19226 | -0.073242 | -0.21057 | -0.086976 | -0.15564 | 0.21515 | 0.3067 | 0.086975 | 0.24262 | 0.16479 | 123.0286 | 122.6944 | 50.8942 | -123.024 | 123.1201 | 123.0698 | 49.4476 | -123.0606
2186.0156 | 123.0011 | -45.3964 | 77.536 | 0.045624 | 0.016635 | 0.069105 | 0.072012 | 0.12864 | 0.00099115 | -0.0051547 | 0.0914 | -0.006349 | 0.065973 | 0.059748 | 0.0080536 | -0.0087692 | 77.2339 | 77.3758 | 4.6692 | -45.5978 | 77.6001 | -45.4926 | -45.6024 | -45.2591 | 3.3325 | -45.5841 | 77.6321 | 77.5406 | -45.5887 | -45.607 | -0.096131 | -0.20599 | 0.064087 | 122.7722 | -0.20142 | 0.004578 | -0.30212 | -0.19226 | -0.21057 | 0.09613 | 0.13733 | -0.18768 | 0.022889 | 0.004577 | 122.9965 | 122.6303 | 50.0656 | -123.1384 | 123.0286 | 122.937 | 48.7289 | -123.143
2187.0156 | 123.1567 | -45.0394 | 77.7557 | 0.18295 | 0.013217 | 0.069532 | 0.073508 | 0.12907 | -7.6852e-05 | -0.0055821 | 0.3508 | -0.007417 | 0.062342 | 0.058039 | 0.00784 | -0.011119 | 77.6825 | 77.8107 | 4.5959 | -45.1904 | 77.948 | -45.0806 | -45.163 | -44.8929 | 3.2913 | -45.195 | 77.8473 | 77.7969 | -45.2683 | -45.3094 | -0.041198 | -0.1236 | 0.19226 | 122.85 | -0.15106 | -0.027466 | -0.073242 | -0.22888 | -0.27008 | 0.091553 | 0.14649 | -0.15564 | 0.11444 | 0.041199 | 122.9874 | 122.7219 | 49.6353 | -122.9187 | 122.8867 | 122.8363 | 48.3307 | -123.0652
2188.0156 | 122.9736 | -46.2158 | 76.7258 | 0.13718 | 0.017062 | 0.069959 | 0.071158 | 0.12843 | 0.00077755 | -0.0057957 | 0.15244 | -0.0072034 | 0.066828 | 0.05633 | 0.0082672 | -0.011974 | 76.1902 | 76.2772 | 4.248 | -46.669 | 76.5472 | -46.5134 | -46.6599 | -46.0693 | 3.2776 | -46.3577 | 76.7075 | 76.7166 | -46.4081 | -46.4401 | -0.29755 | -0.44403 | -0.17853 | 122.493 | -0.45319 | -0.009155 | -0.53558 | -0.19226 | -0.22431 | -0.018311 | 0.14648 | -0.14191 | 0.082398 | -0.009155 | 122.7631 | 122.406 | 50.4639 | -123.3856 | 122.9233 | 122.9324 | 49.4934 | -123.1659
2189.0156 | 123.0835 | -45.9503 | 76.8997 | 0.19058 | 0.013858 | 0.069746 | 0.071372 | 0.13163 | -0.0013587 | -0.0036595 | 0.20584 | -0.007417 | 0.06341 | 0.05633 | 0.0086944 | -0.0094102 | 76.799 | 76.9318 | 4.5456 | -46.1151 | 77.0737 | -45.9778 | -46.0693 | -45.7031 | 2.7832 | -46.0922 | 77.037 | 76.9547 | -46.1334 | -46.1792 | -0.027466 | -0.11902 | 0.17395 | 122.8821 | -0.1648 | -0.045776 | -0.10071 | -0.18311 | -0.22888 | 0.13733 | 0.24719 | -0.14191 | 0.086975 | 0.054932 | 123.024 | 122.7493 | 50.4959 | -122.9691 | 122.9874 | 122.905 | 48.7335 | -123.0789
2190.0156 | 122.9919 | -48.6603 | 74.2767 | -0.03067 | 0.016635 | 0.067182 | 0.070944 | 0.13334 | 0.00056395 | -0.0034457 | 0.037995 | -0.0054944 | 0.064264 | 0.057398 | 0.00784 | -0.010692 | 74.0524 | 74.1348 | 3.9459 | -48.8937 | 74.3271 | -48.7656 | -48.8617 | -48.4451 | 1.8997 | -48.8251 | 74.3683 | 74.2905 | -48.8205 | -48.8983 | -0.10529 | -0.20142 | 0.050354 | 122.7951 | -0.23346 | -0.032044 | -0.2243 | -0.16022 | -0.23804 | 0.091553 | 0.21515 | -0.1648 | 0.073242 | 0.013733 | 122.9874 | 122.7127 | 52.6062 | -123.1384 | 123.0286 | 122.9507 | 50.56 | -123.175
2191.0156 | 122.9874 | -45.4147 | 77.536 | 0.099029 | 0.017703 | 0.06825 | 0.069663 | 0.13014 | -0.00029045 | -0.0043003 | 0.16769 | -0.0069898 | 0.064478 | 0.057612 | 0.0097626 | -0.0096238 | 77.005 | 77.1011 | 4.6646 | -45.8725 | 77.3804 | -45.7031 | -45.7718 | -45.2866 | 3.1631 | -45.7581 | 77.4948 | 77.4353 | -45.6482 | -45.6757 | -0.28839 | -0.35706 | -0.15564 | 122.5159 | -0.45776 | -0.10071 | -0.53101 | -0.23346 | -0.26093 | -0.041199 | 0.12817 | -0.34332 | -0.082398 | -0.10071 | 122.7951 | 122.4197 | 50.0793 | -123.3078 | 122.9095 | 122.85 | 48.5779 | -123.2117
2192.0156 | 123.0377 | -46.1929 | 76.7166 | -0.015411 | 0.016849 | 0.068678 | 0.071799 | 0.12907 | 0.0016321 | -0.0062229 | -0.038299 | -0.0082716 | 0.063196 | 0.055903 | 0.006131 | -0.010265 | 76.7761 | 76.6525 | 4.7012 | -46.1105 | 76.9913 | -46.0556 | -46.138 | -45.9503 | 2.8152 | -46.2662 | 76.8448 | 76.7761 | -46.3211 | -46.3898 | 0.13733 | 0.054932 | 0.27466 | 122.8455 | 0.082397 | 0.027465 | 0.059509 | -0.12817 | -0.19684 | 0.12817 | 0.24262 | -0.073242 | 0.1236 | 0.059509 | 123.1842 | 122.9691 | 50.8942 | -122.8546 | 123.0377 | 122.9691 | 49.0082 | -123.1064
2193.0156 | 123.0331 | -45.1675 | 77.7466 | 0.10666 | 0.015994 | 0.068037 | 0.071158 | 0.12843 | -0.00050425 | -0.0068637 | -0.2977 | -0.010194 | 0.065546 | 0.058253 | 0.0067718 | -0.011333 | 77.5223 | 77.623 | 4.715 | -45.4239 | 77.8473 | -45.2454 | -45.3232 | -44.9249 | 3.2181 | -45.2042 | 77.8656 | 77.8015 | -45.3461 | -45.3735 | -0.077819 | -0.15564 | 0.10071 | 122.7905 | -0.25635 | -0.10071 | -0.2243 | -0.17853 | -0.20599 | 0.11902 | 0.24262 | -0.036621 | 0.16937 | 0.054932 | 123.0148 | 122.6898 | 49.8825 | -123.0698 | 123.0331 | 122.9691 | 48.3856 | -123.1201
2194.0156 | 123.0148 | -44.3115 | 78.6163 | 0.037994 | 0.017276 | 0.067823 | 0.072012 | 0.13078 | 0.0012047 | -0.0055821 | 0.045624 | -0.008058 | 0.063837 | 0.05633 | 0.0080536 | -0.01176 | 78.2135 | 78.3325 | 4.9072 | -44.6823 | 78.5248 | -44.5084 | -44.5862 | -44.1742 | 3.6758 | -44.4305 | 78.6942 | 78.6163 | -44.5221 | -44.5312 | -0.19684 | -0.27466 | -0.091553 | 122.644 | -0.37079 | -0.09613 | -0.40283 | -0.21057 | -0.21973 | 0.07782 | 0.13733 | -0.11902 | 0.10071 | 0 | 122.8363 | 122.525 | 49.2188 | -123.2025 | 123.0057 | 122.9279 | 47.9874 | -123.1476
2195.0156 | 123.0286 | -44.5953 | 78.3829 | 0.10666 | 0.016208 | 0.067396 | 0.067526 | 0.12651 | -0.0011451 | -0.0098545 | 0.09903 | -0.0093396 | 0.064264 | 0.057185 | 0.010617 | -0.0079148 | 78.447 | 78.0624 | 4.7974 | -44.8563 | 78.4058 | -44.7006 | -44.7922 | -44.4031 | 3.4607 | -44.7556 | 78.4241 | 78.3371 | -44.7784 | -44.8151 | -0.10529 | -0.19684 | 0.022888 | 122.6578 | -0.26093 | -0.064087 | 0.064086 | -0.1831 | -0.21973 | 0.041198 | 0.19226 | -0.16022 | 0.059509 | -0.045777 | 123.0011 | 123.0423 | 49.3927 | -123.175 | 123.0194 | 122.9324 | 48.056 | -123.1979
2196.0156 | 123.0194 | -44.8792 | 78.0487 | 0.068512 | 0.015994 | 0.068464 | 0.070517 | 0.13249 | 0.0018457 | -0.0060093 | 0.015106 | -0.009126 | 0.065332 | 0.057185 | 0.009549 | -0.011119 | 77.8427 | 77.9251 | 4.9942 | -45.1126 | 78.1174 | -44.9524 | -45.0668 | -44.7281 | 3.4332 | -45.0394 | 78.1403 | 78.0716 | -45.0531 | -45.1126 | -0.073243 | -0.18768 | 0.068665 | 122.8043 | -0.23346 | -0.045777 | -0.20599 | -0.17395 | -0.23346 | 0.091553 | 0.15106 | -0.16022 | 0.073242 | 0.022888 | 122.9965 | 122.7219 | 49.8734 | -123.1155 | 123.0194 | 122.9507 | 48.3124 | -123.1613
2197.0156 | 122.9736 | -46.0281 | 76.8723 | -0.0077822 | 0.015353 | 0.069319 | 0.070731 | 0.12928 | 0.00099115 | -0.0062229 | 0.16006 | -0.0082716 | 0.064691 | 0.056758 | 0.0084808 | -0.01176 | 76.6571 | 76.7578 | 4.7653 | -46.1517 | 77.0004 | -46.106 | -46.17 | -45.9412 | 2.9663 | -46.2845 | 76.9318 | 76.8906 | -46.2662 | -46.2708 | -0.07782 | -0.14191 | 0.12817 | 122.7859 | -0.1236 | 0.018311 | -0.21515 | -0.23804 | -0.24262 | 0.05951 | 0.086975 | -0.25635 | -0.013733 | 0.018311 | 123.0286 | 122.6852 | 50.7935 | -123.0423 | 122.9599 | 122.9187 | 48.9944 | -123.143
2198.0156 | 123.0469 | -44.3436 | 78.5202 | -0.0383 | 0.015567 | 0.068678 | 0.070944 | 0.13078 | 0.00056395 | -0.0045139 | -0.023041 | -0.0065626 | 0.063837 | 0.057185 | 0.0069854 | -0.0091966 | 78.1219 | 78.2867 | 5.2002 | -44.7556 | 78.4287 | -44.6411 | -44.7464 | -44.0781 | 3.7949 | -44.1467 | 78.7033 | 78.6667 | -44.4672 | -44.5175 | -0.29755 | -0.40283 | -0.091553 | 122.6303 | -0.41199 | -0.009155 | -0.39825 | -0.1236 | -0.17395 | 0.18311 | 0.2655 | 0.19684 | 0.37079 | 0.14648 | 122.7722 | 122.4655 | 49.5438 | -123.2666 | 123.0469 | 123.0103 | 48.1384 | -123.0377
2199.0156 | 123.0377 | -45.52 | 77.3254 | -0.061188 | 0.021548 | 0.066969 | 0.071585 | 0.12993 | 0.0024865 | -0.0047275 | -0.076446 | -0.008058 | 0.065332 | 0.058467 | 0.0084808 | -0.010692 | 77.4765 | 77.623 | 5.0903 | -45.4239 | 77.742 | -45.3369 | -45.4239 | -45.0897 | 3.392 | -45.4971 | 77.6825 | 77.6001 | -45.5475 | -45.6528 | 0.18311 | 0.096131 | 0.41656 | 123.143 | 0.096131 | 0 | 0.15106 | -0.027465 | -0.13275 | 0.35706 | 0.4303 | 0.022889 | 0.15564 | 0.27466 | 123.262 | 122.9965 | 50.6104 | -122.7493 | 123.2025 | 123.1201 | 48.912 | -122.9782
2200.0156 | 123.056 | -45.0897 | 77.7969 | -0.12222 | 0.015567 | 0.06825 | 0.072653 | 0.12779 | 0.0016321 | -0.0066501 | -0.03067 | -0.0065626 | 0.064905 | 0.059748 | 0.011472 | -0.01176 | 77.5726 | 77.6871 | 4.9622 | -45.3644 | 77.8198 | -45.2545 | -45.3232 | -44.9524 | 3.5843 | -45.2362 | 77.9068 | 77.8564 | -45.2774 | -45.3461 | -0.16479 | -0.23346 | 0.022888 | 122.7768 | -0.27466 | -0.041199 | -0.2243 | -0.18768 | -0.25635 | 0.10986 | 0.13733 | -0.14648 | 0.10986 | 0.059509 | 122.9095 | 122.6624 | 50.0519 | -123.1201 | 122.9965 | 122.9462 | 48.674 | -123.143
2201.0156 | 122.9919 | -44.8013 | 78.1036 | 0.022736 | 0.015994 | 0.069746 | 0.071799 | 0.13142 | 0.0014185 | -0.0038731 | 0.083771 | -0.0067762 | 0.064905 | 0.055689 | 0.008908 | -0.010692 | 77.8976 | 78.0029 | 5.0949 | -45.0119 | 78.1677 | -44.8883 | -44.9982 | -44.6503 | 3.8406 | -44.9158 | 78.1815 | 78.1265 | -44.9753 | -45.0485 | -0.086975 | -0.19684 | 0.064087 | 122.8043 | -0.21057 | -0.013733 | -0.20599 | -0.17395 | -0.24719 | 0.07782 | 0.15106 | -0.11444 | 0.13275 | 0.022888 | 122.9691 | 122.699 | 49.8962 | -123.1018 | 122.9828 | 122.9279 | 48.642 | -123.1522
2202.0156 | 123.024 | -46.3531 | 76.561 | -0.18326 | 0.012576 | 0.069319 | 0.07244 | 0.13121 | 0.0012047 | -0.0057957 | -0.11459 | -0.009126 | 0.06106 | 0.058039 | 0.0091216 | -0.0091966 | 76.4328 | 76.5518 | 4.7012 | -46.4401 | 76.7075 | -46.3806 | -46.4813 | -46.1243 | 3.0853 | -46.5225 | 76.6846 | 76.6205 | -46.5042 | -46.5683 | -0.027466 | -0.12817 | 0.14648 | 122.905 | -0.086976 | 0.041198 | -0.12817 | -0.15106 | -0.21515 | 0.1236 | 0.22888 | -0.16937 | 0.045776 | 0.059509 | 123.0606 | 122.7859 | 51.0544 | -123.0423 | 123.0377 | 122.9736 | 49.4385 | -123.1293
2203.0156 | 123.0652 | -44.9799 | 77.9709 | -0.2977 | 0.015994 | 0.06526 | 0.069235 | 0.13163 | 0.0012047 | -0.0051547 | 0.022736 | -0.0095532 | 0.065332 | 0.057398 | 0.011044 | -0.012187 | 77.7328 | 77.829 | 5.1132 | -45.1492 | 77.9846 | -45.0943 | -45.2225 | -44.7784 | 3.4287 | -45.0577 | 78.0441 | 77.9251 | -45.1675 | -45.1996 | -0.11444 | -0.24262 | 0.013733 | 122.8088 | -0.16937 | 0.073242 | -0.23804 | -0.18768 | -0.21973 | 0.073242 | 0.20142 | -0.07782 | 0.14191 | -0.045776 | 122.9645 | 122.7127 | 50.0931 | -123.1934 | 123.024 | 122.905 | 48.4085 | -123.1705
2204.0156 | 123.0331 | -46.0007 | 76.9272 | -0.168 | 0.010867 | 0.067182 | 0.069876 | 0.12971 | -0.0026405 | -0.0049411 | -0.11459 | -0.0065626 | 0.062342 | 0.057185 | 0.0067718 | -0.010051 | 76.7258 | 76.8585 | 4.8294 | -46.1472 | 77.037 | -46.0648 | -46.1472 | -45.845 | 2.9114 | -46.2158 | 76.9959 | 76.9272 | -46.2021 | -46.2524 | -0.064087 | -0.14649 | 0.10986 | 122.8592 | -0.14649 | 0 | -0.20142 | -0.20142 | -0.25177 | 0.068665 | 0.15564 | -0.21515 | 0.036621 | 0 | 123.0377 | 122.7264 | 50.8301 | -123.0743 | 122.9965 | 122.9279 | 48.912 | -123.1796
2205.0156 | 123.0515 | -45.4468 | 77.4765 | -0.19089 | 0.014712 | 0.06761 | 0.073508 | 0.12907 | -0.0011451 | -0.0055821 | -0.13748 | -0.0095532 | 0.065332 | 0.057612 | 0.0076264 | -0.011119 | 77.4994 | 77.6779 | 5.0354 | -45.3415 | 77.8336 | -45.2637 | -45.3598 | -45.2225 | 3.1998 | -45.6299 | 77.6184 | 77.5269 | -45.5887 | -45.6757 | 0.1831 | 0.086975 | 0.35706 | 123.1247 | 0.10528 | 0.01831 | 0.022889 | -0.14191 | -0.22888 | 0.14191 | 0.2243 | -0.18311 | 0.045776 | 0.050354 | 123.2803 | 122.9462 | 50.4822 | -122.8363 | 123.0652 | 122.9736 | 48.6465 | -123.1522
2206.0156 | 123.0469 | -45.2957 | 77.6505 | -0.25192 | 0.011722 | 0.070173 | 0.073508 | 0.12864 | -0.0041357 | -0.0049411 | -0.4808 | -0.0067762 | 0.065332 | 0.058039 | 0.0063446 | -0.010051 | 77.1194 | 77.2842 | 4.7104 | -45.7672 | 77.4857 | -45.6207 | -45.6757 | -45.1172 | 3.653 | -45.4102 | 77.7191 | 77.6505 | -45.4742 | -45.5338 | -0.32501 | -0.37994 | -0.16479 | 122.58 | -0.4715 | -0.091553 | -0.53101 | -0.17853 | -0.23804 | 0.068664 | 0.17853 | -0.11444 | 0.1236 | 0 | 122.7814 | 122.4152 | 50.0061 | -123.3261 | 123.0148 | 122.9462 | 48.9487 | -123.1842
2207.0156 | 123.0423 | -43.483 | 79.4495 | -0.20615 | 0.01578 | 0.067823 | 0.072653 | 0.12886 | 0.0024865 | -0.0079319 | -0.12985 | -0.0072034 | 0.065119 | 0.057612 | 0.00784 | -0.010692 | 79.1245 | 79.303 | 5.3604 | -43.7073 | 79.4724 | -43.6066 | -43.7027 | -43.3319 | 3.9963 | -43.4601 | 79.5135 | 79.422 | -43.689 | -43.7439 | -0.1236 | -0.21973 | 0.022888 | 122.7859 | -0.2243 | -0.004577 | -0.32501 | -0.20599 | -0.26093 | 0.064087 | 0.15106 | 0.022888 | 0.28381 | -0.027466 | 122.9553 | 122.6074 | 48.8434 | -123.1522 | 122.9965 | 122.905 | 47.4792 | -123.1934
2208.0156 | 123.0148 | -44.7556 | 78.1815 | -0.23666 | 0.012149 | 0.068678 | 0.068808 | 0.1295 | -0.0013587 | -0.0072911 | 0.21347 | -0.0076306 | 0.061273 | 0.058894 | 0.0067718 | -0.010478 | 77.7924 | 78.0029 | 4.9713 | -45.0027 | 78.1631 | -44.9295 | -45.0439 | -44.6136 | 3.1174 | -44.838 | 78.2959 | 78.2135 | -44.9387 | -44.9844 | -0.17395 | -0.28839 | -0.018311 | 122.7585 | -0.24719 | 0.041198 | -0.3891 | -0.18311 | -0.22888 | 0.11444 | 0.14191 | -0.082398 | 0.14648 | 0.032043 | 122.9187 | 122.5479 | 49.7269 | -123.2254 | 123.0515 | 122.9691 | 47.8729 | -123.1659
2209.0156 | 123.056 | -43.7622 | 79.1794 | -0.18326 | 0.014712 | 0.066114 | 0.072226 | 0.12928 | -0.0011451 | -0.0045139 | -0.091705 | -0.0089124 | 0.063623 | 0.05633 | 0.0069854 | -0.010265 | 78.6942 | 78.8818 | 5.2322 | -44.1696 | 78.9963 | -44.0781 | -44.165 | -43.5883 | 3.2547 | -43.7027 | 79.1931 | 79.1382 | -43.9728 | -44.0048 | -0.31586 | -0.40283 | -0.1831 | 122.644 | -0.40741 | -0.004578 | -0.48523 | -0.21057 | -0.24262 | 0.013733 | 0.17395 | 0.059509 | 0.30212 | -0.041198 | 122.7585 | 122.4564 | 48.9944 | -123.3444 | 122.9553 | 122.9004 | 47.0169 | -123.1842
2210.0156 | 123.0148 | -44.0506 | 78.8773 | -0.24429 | 0.0078763 | 0.069746 | 0.071372 | 0.12843 | -0.0052039 | -0.0077183 | -0.10696 | -0.009126 | 0.064691 | 0.058039 | 0.0052764 | -0.0085556 | 78.6667 | 78.8635 | 5.2139 | -44.1559 | 79.0009 | -44.0643 | -44.1696 | -43.8492 | 3.3051 | -44.0826 | 79.0054 | 78.9459 | -44.1971 | -44.22 | -0.013733 | -0.11902 | 0.1236 | 122.9141 | -0.10529 | 0.013733 | -0.21057 | -0.14648 | -0.16937 | 0.12817 | 0.20142 | -0.032044 | 0.13733 | 0.068665 | 123.0515 | 122.7173 | 49.2645 | -123.0469 | 123.056 | 122.9965 | 47.3557 | -123.0972
2211.0156 | 123.0423 | -43.9545 | 78.978 | -0.19089 | 0.013003 | 0.069746 | 0.070303 | 0.12971 | -0.0024269 | -0.0070773 | -0.12985 | -0.008058 | 0.064905 | 0.057398 | 0.0082672 | -0.011119 | 78.6026 | 78.7537 | 5.3604 | -44.3115 | 78.9551 | -44.1467 | -44.2383 | -43.7851 | 3.2776 | -43.9316 | 79.129 | 79.0329 | -44.0964 | -44.1605 | -0.19226 | -0.28381 | -0.022888 | 122.7081 | -0.35706 | -0.073242 | -0.37537 | -0.14191 | -0.20599 | 0.15106 | 0.16937 | 0.022888 | 0.22888 | 0.054932 | 122.9095 | 122.5571 | 49.3149 | -123.2162 | 123.0835 | 122.9874 | 47.2321 | -123.1384
2212.0156 | 123.1476 | -44.6136 | 78.2089 | -0.18326 | 0.0061673 | 0.068891 | 0.070731 | 0.13206 | -0.0058447 | -0.0077183 | -1.1446 | -0.0097668 | 0.061914 | 0.057185 | 0.007199 | -0.0096238 | 78.2364 | 78.4515 | 5.4337 | -44.5221 | 78.5294 | -44.5496 | -44.6136 | -44.3481 | 3.2593 | -44.751 | 78.3966 | 78.2959 | -44.7372 | -44.8425 | 0.064086 | 0 | 0.32044 | 123.0652 | 0.091552 | 0.091552 | 0.027466 | -0.1236 | -0.22888 | 0.18768 | 0.2655 | -0.13733 | 0.091552 | 0.086975 | 123.143 | 122.85 | 50.0473 | -122.8226 | 123.0103 | 122.9095 | 47.8729 | -123.0515
2213.0156 | 123.0469 | -42.8421 | 80.1086 | -0.25192 | 0.010226 | 0.069532 | 0.07479 | 0.12971 | -0.0032813 | -0.0060093 | -0.10696 | -0.0086988 | 0.062555 | 0.055689 | 0.0065582 | -0.011119 | 79.8019 | 79.9805 | 5.864 | -43.0023 | 80.0766 | -42.9565 | -43.0573 | -42.7368 | 3.8361 | -43.0252 | 80.0629 | 80.0446 | -43.0756 | -43.0939 | -0.11444 | -0.21515 | -0.032044 | 122.8226 | -0.16022 | 0.054932 | -0.3067 | -0.23346 | -0.25177 | -0.045777 | 0.10529 | -0.18311 | 0.068664 | -0.064087 | 122.9187 | 122.644 | 48.7061 | -123.1659 | 122.905 | 122.8867 | 46.6782 | -123.2025
2214.0156 | 123.024 | -44.1605 | 78.772 | -0.24429 | 0.0095853 | 0.070387 | 0.067954 | 0.128 | -0.0022131 | -0.0064365 | -0.084076 | -0.0095532 | 0.062128 | 0.05633 | 0.0076264 | -0.0091966 | 78.7857 | 79.0237 | 5.6305 | -43.927 | 79.1153 | -43.9407 | -44.0414 | -44.0598 | 3.186 | -44.4626 | 78.8589 | 78.7582 | -44.3756 | -44.4214 | 0.21973 | 0.11902 | 0.34332 | 123.1842 | 0.23346 | 0.11444 | 0.013733 | -0.21515 | -0.26093 | 0.086975 | 0.10071 | -0.30212 | -0.041198 | -0.013733 | 123.2758 | 122.9462 | 49.791 | -122.8134 | 123.0194 | 122.9187 | 47.3465 | -123.1934
2215.0156 | 123.0011 | -42.9108 | 80.0812 | -0.21378 | 0.01044 | 0.069319 | 0.069876 | 0.13014 | -0.00029045 | -0.0096409 | -1.6023 | -0.0086988 | 0.063623 | 0.056117 | 0.0067718 | -0.013042 | 79.7653 | 79.8477 | 5.6305 | -43.1717 | 80.0354 | -43.071 | -43.1808 | -42.6727 | 3.7949 | -43.0252 | 80.1086 | 80.04 | -43.103 | -43.1168 | -0.16022 | -0.27008 | -0.045777 | 122.7585 | -0.26093 | 0.009155 | -0.31586 | -0.19226 | -0.20599 | 0.027466 | 0.23804 | -0.11444 | 0.091552 | -0.041199 | 122.9462 | 122.6761 | 48.5413 | -123.262 | 123.0194 | 122.9507 | 46.7056 | -123.1979
2216.0156 | 123.1476 | -44.3024 | 78.5156 | -0.19852 | 0.0085171 | 0.069746 | 0.075858 | 0.12928 | 0.00099115 | -0.0064365 | -0.13748 | -0.010194 | 0.064691 | 0.056758 | 0.0065582 | -0.0091966 | 77.9572 | 78.5294 | 5.3146 | -44.6915 | 78.4287 | -44.6091 | -44.7098 | -44.1605 | 3.5934 | -44.2703 | 78.5248 | 78.4836 | -44.5358 | -44.5358 | -0.3067 | -0.40741 | -0.086975 | 122.8317 | -0.3891 | 0.018311 | -0.55847 | -0.23346 | -0.23346 | 0.009155 | 0.14191 | 0.032043 | 0.2655 | -0.032043 | 122.731 | 122.2595 | 49.617 | -123.2254 | 122.8271 | 122.7859 | 47.8958 | -123.0515
2217.0156 | 122.9645 | -44.3436 | 78.6026 | -0.26718 | 0.0070217 | 0.068037 | 0.071585 | 0.12971 | -0.0015723 | -0.0079319 | -0.15274 | -0.0095532 | 0.064691 | 0.057398 | 0.0076264 | -0.013255 | 78.3966 | 78.566 | 5.3101 | -44.5358 | 78.6438 | -44.4672 | -44.5541 | -44.2474 | 3.5477 | -44.5312 | 78.566 | 78.5019 | -44.6182 | -44.6365 | -0.1236 | -0.21057 | 0.041199 | 122.9095 | -0.19226 | 0.01831 | -0.20599 | -0.27466 | -0.29297 | -0.036621 | 0.09613 | -0.18768 | 0.10529 | -0.10071 | 122.9874 | 122.7402 | 49.6536 | -123.1567 | 122.9095 | 122.8455 | 47.8912 | -123.2391
2218.0156 | 123.1018 | -44.5404 | 78.2867 | -0.061188 | 0.0089443 | 0.069959 | 0.071372 | 0.12928 | -0.0043495 | -0.0062229 | -0.061188 | -0.010194 | 0.057428 | 0.058467 | 0.0067718 | -0.0094102 | 78.2135 | 78.4515 | 5.3146 | -44.5221 | 78.4424 | -44.5862 | -44.696 | -44.1742 | 3.6026 | -44.6548 | 78.4195 | 78.3096 | -44.696 | -44.8059 | -0.045777 | -0.15564 | 0.15564 | 122.9919 | 0.01831 | 0.17395 | -0.073242 | -0.15564 | -0.2655 | 0.13275 | 0.36621 | -0.11444 | 0.15106 | 0.022888 | 122.9828 | 122.7539 | 49.855 | -122.9828 | 122.9599 | 122.85 | 48.143 | -123.0927
2219.0156 | 123.1476 | -44.0964 | 78.7674 | -0.168 | 0.0080899 | 0.069532 | 0.069876 | 0.13078 | -0.0030677 | -0.0092137 | 0.55679 | -0.010194 | 0.062982 | 0.058467 | 0.0080536 | -0.011119 | 78.5431 | 79.303 | 5.6259 | -44.3573 | 78.9459 | -44.1147 | -44.2474 | -43.8126 | 3.7354 | -44.1742 | 78.8498 | 78.7399 | -44.2841 | -44.339 | -0.01831 | -0.15106 | 0.17853 | 123.3994 | -0.26093 | -0.10986 | -0.2243 | -0.18768 | -0.24261 | 0.082397 | 0.28381 | -0.077819 | 0.16479 | -0.027466 | 123.0423 | 122.6395 | 49.7223 | -123.0148 | 122.9462 | 122.8363 | 47.8317 | -123.1064
2220.0156 | 123.1293 | -44.8929 | 77.9343 | -0.0077822 | 0.0085171 | 0.069746 | 0.07009 | 0.12736 | -0.0037085 | -0.0087863 | 0.030365 | -0.011689 | 0.061914 | 0.056117 | 0.0057038 | -0.013042 | 77.8061 | 78.0167 | 5.1178 | -45.0439 | 78.0304 | -45.0211 | -45.0623 | -44.6686 | 3.2272 | -45.0485 | 77.9938 | 77.916 | -45.0806 | -45.1538 | -0.12817 | -0.16937 | 0.096131 | 122.9095 | -0.15106 | 0.018311 | -0.12817 | -0.18768 | -0.26093 | 0.059509 | 0.2243 | -0.15564 | 0.10529 | -0.01831 | 122.9233 | 122.699 | 50.0107 | -122.9965 | 122.8867 | 122.8088 | 48.1201 | -123.0881
2221.0156 | 123.0331 | -44.9432 | 77.9205 | -0.22903 | 0.0085171 | 0.069105 | 0.072012 | 0.12971 | 0.00056395 | -0.0077183 | -0.21378 | -0.0095532 | 0.063196 | 0.058894 | 0.0091216 | -0.012401 | 77.8885 | 78.0212 | 5.1498 | -45.076 | 78.0716 | -45.0119 | -45.1035 | -44.6777 | 3.2089 | -44.957 | 78.1036 | 78.0167 | -45.0531 | -45.1218 | -0.068665 | -0.16022 | 0.15106 | 122.9645 | -0.13275 | 0.027466 | -0.032043 | -0.10986 | -0.17853 | 0.18311 | 0.2655 | -0.013733 | 0.1648 | 0.096131 | 123.0148 | 122.8317 | 50.0931 | -123.024 | 123.0469 | 122.9599 | 48.1522 | -123.0423
2222.0156 | 123.1613 | -45.0623 | 77.7603 | -0.061188 | 0.0070217 | 0.070814 | 0.067526 | 0.1295 | -0.0022131 | -0.0075047 | 0.015106 | -0.0099806 | 0.058924 | 0.058894 | 0.00549 | -0.013469 | 77.5314 | 77.7191 | 5.1453 | -45.4285 | 77.7466 | -45.2957 | -45.369 | -44.7876 | 3.3875 | -45.0714 | 77.8061 | 77.7191 | -45.2774 | -45.3323 | -0.23346 | -0.3067 | -0.013733 | 122.7814 | -0.36621 | -0.059509 | -0.22888 | -0.21515 | -0.27008 | 0.045776 | 0.27466 | -0.009155 | 0.26093 | -0.041199 | 122.8088 | 122.5937 | 50.2075 | -123.1293 | 122.8683 | 122.7814 | 48.4497 | -123.0927
2223.0156 | 123.1018 | -43.9728 | 78.9368 | -0.168 | 0.0089443 | 0.068678 | 0.072226 | 0.12843 | 0.00013675 | -0.0068637 | -0.18326 | -0.0093396 | 0.062555 | 0.058467 | 0.0069854 | -0.014537 | 78.8589 | 79.0741 | 5.5389 | -43.9774 | 79.1153 | -43.959 | -44.0735 | -43.6295 | 3.392 | -44.014 | 79.0649 | 78.9093 | -44.1284 | -44.1788 | 0.013733 | -0.10071 | 0.17853 | 123.0469 | -0.004578 | 0.09613 | -0.07782 | -0.15564 | -0.20599 | 0.12817 | 0.34332 | -0.041199 | 0.1648 | -0.027466 | 123.0881 | 122.8317 | 49.5117 | -123.0103 | 123.0377 | 122.8821 | 47.3648 | -123.1155
2224.0156 | 123.1659 | -43.721 | 79.1107 | -0.076447 | 0.0061673 | 0.06825 | 0.070944 | 0.12864 | -0.0030677 | -0.0047275 | -0.015411 | -0.010835 | 0.062555 | 0.058039 | 0.0069854 | -0.012828 | 79.1382 | 79.3259 | 5.4977 | -43.8354 | 79.3991 | -43.6844 | -43.7851 | -43.4189 | 3.0899 | -43.9362 | 79.2435 | 79.1153 | -43.9041 | -43.9499 | 0.036621 | -0.064087 | 0.28839 | 123.0469 | -0.11444 | -0.050354 | 0.027466 | -0.18311 | -0.22888 | 0.13275 | 0.30212 | -0.21515 | 0.013733 | 0.004577 | 123.1201 | 122.8592 | 49.2188 | -122.8958 | 122.9645 | 122.8363 | 46.8109 | -123.0606
2225.0156 | 123.1293 | -42.7139 | 80.1407 | -1.3658 | 0.0078763 | 0.06825 | 0.069663 | 0.12993 | -0.00093145 | -0.0072911 | -0.13748 | -0.0095532 | 0.061273 | 0.058253 | 0.0091216 | -0.011974 | 80.0629 | 80.3604 | 5.8502 | -42.7734 | 80.2872 | -42.6956 | -42.7689 | -42.4576 | 3.8544 | -42.7505 | 80.2505 | 80.0995 | -42.9153 | -42.984 | 0.01831 | -0.054932 | 0.14648 | 123.0743 | -0.059509 | -0.004577 | -0.07782 | -0.20142 | -0.27008 | 0.10986 | 0.25635 | -0.036621 | 0.23346 | -0.041199 | 123.0011 | 122.7768 | 48.5641 | -122.9095 | 122.9645 | 122.8134 | 46.5683 | -123.1247
2226.0156 | 123.0331 | -43.158 | 79.7562 | -0.26718 | 0.011081 | 0.069532 | 0.070944 | 0.13014 | -0.00029045 | -0.0077183 | -0.22903 | -0.0082716 | 0.063837 | 0.057185 | 0.008908 | -0.012187 | 79.7699 | 79.8386 | 5.0858 | -43.1808 | 80.1041 | -43.0298 | -43.103 | -42.9932 | 3.3005 | -43.4509 | 79.9072 | 79.7699 | -43.3502 | -43.3823 | 0.12817 | 0.054932 | 0.3479 | 122.9965 | -0.022888 | -0.07782 | 0.013732 | -0.19226 | -0.2243 | 0.15106 | 0.16479 | -0.29297 | -0.068665 | 0.013732 | 123.262 | 122.9279 | 48.2437 | -122.8592 | 123.0652 | 122.9279 | 46.4584 | -123.1384
2227.0156 | 123.1613 | -42.7917 | 80.0903 | -0.068817 | 0.0065945 | 0.07295 | 0.071585 | 0.12736 | -0.0028541 | -0.0051547 | 0.022736 | -0.0095532 | 0.062128 | 0.057185 | 0.008908 | -0.010692 | 79.9713 | 80.1956 | 5.2094 | -42.8833 | 80.2185 | -42.8101 | -42.9016 | -42.5171 | 3.5294 | -42.8467 | 80.1407 | 80.0491 | -42.9657 | -43.0023 | -0.018311 | -0.10986 | 0.12817 | 122.9874 | -0.091553 | 0.01831 | -0.11902 | -0.17395 | -0.21057 | 0.050354 | 0.27466 | -0.054932 | 0.15564 | -0.041199 | 123.0103 | 122.7631 | 48.0011 | -122.9919 | 122.9324 | 122.8409 | 46.3211 | -123.0927
2228.0156 | 123.1293 | -43.9774 | 78.8498 | -0.084076 | 0.0070217 | 0.070173 | 0.070303 | 0.12886 | -0.0017859 | -0.0079319 | -0.00015237 | -0.010835 | 0.062342 | 0.055262 | 0.00784 | -0.011546 | 78.8818 | 79.0878 | 4.9942 | -44.0002 | 79.1061 | -43.9499 | -44.0689 | -43.6432 | 3.0487 | -44.1788 | 79.0054 | 78.8681 | -44.1559 | -44.2429 | 0.027466 | -0.091553 | 0.25635 | 123.0652 | -0.022888 | 0.068665 | 0.032044 | -0.17853 | -0.2655 | 0.15564 | 0.33417 | -0.20142 | 0.064087 | 0.018311 | 123.0835 | 122.8592 | 48.9716 | -122.9187 | 122.9828 | 122.8455 | 47.0261 | -123.0927
2229.0156 | 123.1293 | -42.7231 | 80.1865 | 0.32028 | 0.0095853 | 0.072309 | 0.072867 | 0.12993 | 0.00013675 | -0.0057957 | -0.16037 | -0.008058 | 0.06106 | 0.055476 | 0.0091216 | -0.012401 | 80.072 | 80.278 | 5.2139 | -42.7689 | 80.3467 | -42.6865 | -42.7734 | -42.3614 | 3.4607 | -42.9108 | 80.2551 | 80.0858 | -42.9291 | -43.0023 | 0.036621 | -0.050354 | 0.16022 | 123.0011 | -0.045777 | 0.004577 | -0.11444 | -0.20599 | -0.27924 | 0.068665 | 0.36163 | -0.18768 | 0.091552 | -0.10071 | 123.0698 | 122.7951 | 47.937 | -122.9599 | 122.9782 | 122.8088 | 46.1838 | -123.1888
2230.0156 | 123.1338 | -43.3868 | 79.4724 | -0.023041 | 0.0050991 | 0.071241 | 0.067954 | 0.12886 | -0.0022131 | -0.0085727 | 0.015106 | -0.011262 | 0.062342 | 0.057398 | 0.0080536 | -0.011546 | 79.2755 | 79.4815 | 5.1819 | -43.5699 | 79.541 | -43.515 | -43.5883 | -43.2037 | 2.8656 | -43.5013 | 79.4952 | 79.3991 | -43.5883 | -43.634 | -0.12817 | -0.20142 | 0.068665 | 122.8683 | -0.18311 | 0.018311 | -0.19684 | -0.20142 | -0.24719 | 0.022888 | 0.18311 | -0.11444 | 0.13275 | -0.073242 | 122.9279 | 122.6624 | 48.5687 | -123.0606 | 122.8821 | 122.7859 | 46.2524 | -123.1064
2231.0312 | 123.0286 | -44.5679 | 78.3051 | -0.27481 | 0.014285 | 0.067182 | 0.073081 | 0.12864 | 0.0052637 | -0.0040867 | 0.12192 | -0.008058 | 0.066187 | 0.058253 | 0.0086944 | -0.012187 | 78.1082 | 78.3051 | 5.2689 | -44.7556 | 78.4698 | -44.5999 | -44.7006 | -44.2841 | 2.7328 | -44.577 | 78.5156 | 78.36 | -44.7189 | -44.7739 | -0.032044 | -0.13275 | 0.16479 | 122.8729 | -0.18768 | -0.054931 | -0.19684 | -0.15106 | -0.20599 | 0.21057 | 0.28381 | -0.009155 | 0.19684 | 0.054931 | 123.0377 | 122.6761 | 49.8367 | -123.0057 | 123.0835 | 122.9279 | 47.3007 | -123.0789
2232.0156 | 123.0743 | -43.8354 | 79.0421 | 0.10666 | 0.0078763 | 0.071455 | 0.070731 | 0.13014 | -0.0034949 | -0.0049411 | 0.13718 | -0.0082716 | 0.060633 | 0.056971 | 0.0080536 | -0.010905 | 78.8956 | 79.0833 | 5.3421 | -44.0552 | 79.184 | -43.895 | -43.9728 | -43.5974 | 2.8152 | -43.8995 | 79.0924 | 79.01 | -44.0002 | -44.0826 | -0.059509 | -0.13733 | 0.14191 | 122.9187 | -0.21973 | -0.082398 | -0.14648 | -0.1648 | -0.24719 | 0.050354 | 0.23804 | -0.064087 | 0.18311 | -0.032043 | 123.0194 | 122.731 | 49.1776 | -123.0148 | 122.9279 | 122.8455 | 46.6507 | -123.1247
2233.0156 | 123.0927 | -43.5562 | 79.248 | -0.099335 | 0.0080899 | 0.068891 | 0.069235 | 0.13014 | -0.0041357 | -0.0066501 | 0.015106 | -0.0084852 | 0.058496 | 0.05633 | 0.0076264 | -0.011974 | 79.0741 | 79.2938 | 5.3787 | -43.8171 | 79.3259 | -43.721 | -43.7942 | -43.3228 | 3.4973 | -43.5608 | 79.3488 | 79.2526 | -43.7759 | -43.8309 | -0.16479 | -0.23804 | 0.07782 | 122.85 | -0.26093 | -0.022889 | -0.17395 | -0.21973 | -0.27466 | 0.10071 | 0.23346 | -0.004578 | 0.27008 | 0.004578 | 122.8821 | 122.6303 | 48.9349 | -123.0423 | 122.905 | 122.8088 | 47.0535 | -123.0789
2234.0156 | 123.0835 | -44.8059 | 78.0487 | -0.053558 | 0.0053129 | 0.071882 | 0.070731 | 0.12587 | -0.0037085 | -0.0070773 | 0.0914 | -0.0099806 | 0.062769 | 0.05633 | 0.01019 | -0.010478 | 78.1677 | 78.3371 | 4.8111 | -44.7784 | 78.5339 | -44.5312 | -44.6274 | -44.4855 | 3.0258 | -45.0394 | 78.2272 | 78.0945 | -44.9478 | -44.989 | 0.27466 | 0.17853 | 0.48523 | 123.143 | 0.027466 | -0.15106 | 0.11902 | -0.14191 | -0.18311 | 0.17853 | 0.32043 | -0.23346 | -0.050354 | 0.045776 | 123.3398 | 122.9736 | 49.617 | -122.6761 | 123.0331 | 122.9004 | 47.8317 | -123.0377
2235.0156 | 123.1155 | -47.3373 | 75.5127 | -0.20615 | 0.010653 | 0.070173 | 0.070944 | 0.12565 | -0.0030677 | -0.0053683 | -0.091705 | -0.0086988 | 0.060205 | 0.054621 | 0.0037812 | -0.010478 | 75.3754 | 75.5859 | 4.4815 | -47.5662 | 75.5219 | -47.4976 | -47.5983 | -47.0169 | 1.8219 | -47.3831 | 75.5447 | 75.4257 | -47.5662 | -47.6028 | -0.16022 | -0.26093 | 0.009156 | 122.9233 | -0.22888 | 0.032044 | -0.13733 | -0.22888 | -0.2655 | 0.032044 | 0.32043 | -0.045777 | 0.21973 | -0.086975 | 122.8592 | 122.7127 | 51.8188 | -123.111 | 122.8821 | 122.7631 | 49.1592 | -123.1155
2236.0156 | 122.9965 | -44.6915 | 78.2135 | -0.24429 | 0.010013 | 0.070173 | 0.071799 | 0.13035 | -0.00029045 | -0.0049411 | -0.21378 | -0.010408 | 0.060846 | 0.056758 | 0.0076264 | -0.011974 | 77.9205 | 78.1494 | 5.04 | -44.9936 | 78.2272 | -44.8425 | -44.9341 | -44.5312 | 3.2593 | -44.8517 | 78.241 | 78.0991 | -44.9295 | -44.9615 | -0.15106 | -0.24261 | 0.013733 | 122.8409 | -0.30212 | -0.059509 | -0.29297 | -0.23804 | -0.27008 | 0.027466 | 0.16022 | -0.16022 | 0.10986 | -0.11444 | 122.9187 | 122.612 | 49.7314 | -123.1476 | 122.9324 | 122.7905 | 47.9507 | -123.175
2237.0156 | 123.175 | -45.8817 | 76.9821 | -0.084076 | 0.0063809 | 0.070387 | 0.070731 | 0.12608 | -0.0024269 | -0.0060093 | -0.084076 | -0.010408 | 0.059351 | 0.056117 | 0.0069854 | -0.011333 | 76.8539 | 77.0187 | 4.8386 | -46.1517 | 77.0187 | -46.019 | -46.1472 | -45.5841 | 2.9297 | -45.8679 | 77.0279 | 76.9135 | -46.0602 | -46.1197 | -0.13733 | -0.2655 | 0.036621 | 122.9004 | -0.27008 | -0.004577 | -0.12817 | -0.17853 | -0.23804 | 0.045776 | 0.29755 | 0.013733 | 0.25177 | -0.068665 | 122.9004 | 122.7356 | 50.7202 | -123.1293 | 122.9095 | 122.7951 | 48.8113 | -123.1018
2238.0156 | 123.056 | -46.8613 | 76.0071 | 0.053253 | 0.0061673 | 0.070814 | 0.07009 | 0.12693 | -0.00093145 | -0.0049411 | 0.068512 | -0.010621 | 0.060846 | 0.055476 | 0.007199 | -0.0094102 | 75.7599 | 75.9659 | 4.6143 | -47.0718 | 76.0574 | -46.962 | -47.0444 | -46.5317 | 2.3895 | -46.843 | 76.1536 | 76.0162 | -47.0032 | -47.1039 | -0.10071 | -0.18311 | 0.050354 | 122.8271 | -0.21057 | -0.027465 | -0.24719 | -0.14191 | -0.24262 | 0.14648 | 0.32959 | 0.01831 | 0.26093 | 0.009155 | 122.9187 | 122.6212 | 51.4755 | -123.0515 | 123.0148 | 122.8775 | 49.2508 | -123.111
2239.0156 | 123.1613 | -47.1771 | 75.65 | -0.045929 | 0.0057401 | 0.071027 | 0.068381 | 0.13099 | -0.00093145 | -0.0062229 | -0.015411 | -0.008058 | 0.062128 | 0.05633 | 0.0074126 | -0.011974 | 75.412 | 75.5768 | 4.6371 | -47.4976 | 75.6454 | -47.3969 | -47.4472 | -46.9391 | 2.4536 | -47.2321 | 75.7095 | 75.5859 | -47.438 | -47.4609 | -0.21973 | -0.27008 | -0.004577 | 122.7539 | -0.32044 | -0.050354 | -0.23804 | -0.26093 | -0.28381 | 0.05951 | 0.23804 | -0.054932 | 0.22888 | -0.064087 | 122.8226 | 122.5891 | 51.8143 | -123.0972 | 122.8867 | 122.7631 | 49.6307 | -123.111
2240.0156 | 123.1338 | -47.1771 | 75.6729 | 0.25162 | 0.0091581 | 0.069319 | 0.068167 | 0.12907 | 0.00035035 | -0.0040867 | 0.2211 | -0.0089124 | 0.061914 | 0.057612 | 0.008908 | -0.014323 | 75.4578 | 75.618 | 4.509 | -47.4838 | 75.6271 | -47.3969 | -47.4976 | -46.907 | 2.1332 | -47.4289 | 75.7187 | 75.5859 | -47.4197 | -47.4472 | -0.21973 | -0.32044 | -0.045777 | 122.7951 | -0.3067 | 0.013733 | -0.21515 | -0.24262 | -0.27008 | 0.045776 | 0.27008 | -0.25177 | 0.018311 | -0.086976 | 122.8043 | 122.6349 | 51.6861 | -123.1705 | 122.8958 | 122.7631 | 49.3103 | -123.1201
2241.0312 | 123.056 | -46.8521 | 76.0574 | -0.168 | 0.016849 | 0.066328 | 0.073721 | 0.13078 | 0.0054773 | -0.0038731 | -0.23666 | -0.009126 | 0.065759 | 0.055476 | 0.007199 | -0.013896 | 75.7599 | 75.8698 | 4.4495 | -47.1588 | 76.0529 | -47.0718 | -47.1359 | -46.5683 | 2.3071 | -46.9666 | 76.1169 | 75.9979 | -47.0306 | -47.0856 | -0.21973 | -0.28381 | -0.004578 | 122.7219 | -0.3067 | -0.022888 | -0.29755 | -0.17853 | -0.23346 | 0.059509 | 0.28381 | -0.11444 | 0.11902 | -0.059509 | 122.905 | 122.612 | 51.3016 | -123.1934 | 122.9691 | 122.85 | 49.1592 | -123.143
2242.0156 | 123.0606 | -47.8958 | 74.968 | 0.13718 | 0.0087307 | 0.070173 | 0.071585 | 0.1295 | -0.0034949 | -0.0053683 | 0.2211 | -0.0095532 | 0.058496 | 0.059321 | 0.0076264 | -0.011546 | 75.0137 | 75.1831 | 4.335 | -47.9507 | 75.2335 | -47.7951 | -47.8912 | -47.6257 | 1.8356 | -48.1155 | 75.0412 | 74.9359 | -48.1247 | -48.1339 | 0.10071 | 0.004578 | 0.2655 | 123.0789 | -0.054932 | -0.05951 | 0.045776 | -0.22888 | -0.23804 | 0.073242 | 0.27008 | -0.21973 | 0.01831 | -0.032044 | 123.1293 | 122.9095 | 52.2308 | -122.8592 | 122.937 | 122.8317 | 49.7314 | -123.1018
2243.0156 | 123.111 | -46.7011 | 76.1444 | -0.24429 | 0.0072355 | 0.070387 | 0.069449 | 0.12693 | -0.0039221 | -0.0040867 | 0.0914 | -0.0095532 | 0.060633 | 0.058894 | 0.0074126 | -0.010692 | 75.9247 | 76.1124 | 4.3762 | -46.9482 | 76.2222 | -46.8109 | -46.9116 | -46.4584 | 2.2202 | -46.7834 | 76.2268 | 76.1536 | -46.8933 | -46.9391 | -0.10986 | -0.21057 | 0.07782 | 122.8134 | -0.24719 | -0.036621 | -0.21973 | -0.19226 | -0.23804 | 0.082398 | 0.24262 | -0.082397 | 0.15564 | 0.009155 | 122.9233 | 122.6257 | 51.0773 | -123.056 | 122.9279 | 122.8546 | 48.9212 | -123.0835
2244.0156 | 123.1155 | -47.5433 | 75.3204 | 0.14481 | 0.013003 | 0.06825 | 0.071799 | 0.12864 | 0.00077755 | -0.0047275 | 0.2211 | -0.008058 | 0.062555 | 0.053126 | 0.0084808 | -0.010692 | 75.0641 | 75.2335 | 4.1885 | -47.8912 | 75.2518 | -47.7722 | -47.8409 | -47.2137 | 1.9455 | -47.58 | 75.3754 | 75.2655 | -47.7356 | -47.7768 | -0.22888 | -0.29755 | -0.068665 | 122.7768 | -0.3479 | -0.050354 | -0.25635 | -0.19226 | -0.23346 | 0.054931 | 0.32959 | -0.036621 | 0.19684 | -0.054932 | 122.7951 | 122.6074 | 51.7319 | -123.1613 | 122.9187 | 122.8088 | 49.4888 | -123.0972
2245.0156 | 123.0606 | -46.6278 | 76.2131 | 0.015106 | 0.0095853 | 0.071241 | 0.068594 | 0.12736 | -0.0019995 | -0.0051547 | 0.0914 | -0.009126 | 0.059992 | 0.058039 | 0.0084808 | -0.011119 | 76.2451 | 76.4053 | 4.5731 | -46.7194 | 76.5106 | -46.5591 | -46.6553 | -46.3623 | 2.3117 | -46.7789 | 76.3092 | 76.1719 | -46.8521 | -46.9025 | 0.068665 | -0.027465 | 0.29755 | 123.0331 | -0.091552 | -0.064087 | 0.032043 | -0.2243 | -0.27466 | 0.09613 | 0.2655 | -0.15106 | 0.1236 | -0.041199 | 123.1384 | 122.8729 | 51.2009 | -122.8683 | 122.937 | 122.7997 | 48.9395 | -123.1155
2246.0156 | 123.1522 | -45.813 | 77.0416 | -0.068817 | 0.0053129 | 0.070814 | 0.069663 | 0.12693 | -0.0022131 | -0.0060093 | -0.12985 | -0.011049 | 0.063623 | 0.055903 | 0.0080536 | -0.010692 | 76.9272 | 77.1286 | 4.6783 | -46.0052 | 77.1561 | -45.8908 | -45.9732 | -45.5017 | 2.774 | -45.813 | 77.1194 | 76.9821 | -46.0052 | -46.051 | -0.07782 | -0.16022 | 0.11444 | 122.9416 | -0.19226 | -0.032043 | -0.11444 | -0.19226 | -0.23804 | 0.07782 | 0.31128 | 0 | 0.23804 | -0.059509 | 122.9691 | 122.7402 | 50.4913 | -123.0148 | 122.9324 | 122.7951 | 48.587 | -123.0927
2247.0156 | 123.1613 | -47.113 | 75.7645 | 1.6783 | 0.01279 | 0.070814 | 0.069876 | 0.12822 | 0.0024865 | -0.0062229 | 0.15244 | -0.008058 | 0.061701 | 0.057612 | 0.01019 | -0.011546 | 75.7187 | 75.8469 | 4.4724 | -47.2687 | 75.8423 | -47.1634 | -47.2641 | -46.8109 | 2.3575 | -47.3328 | 75.8102 | 75.6271 | -47.3602 | -47.374 | -0.050354 | -0.15106 | 0.07782 | 122.9599 | -0.15564 | -0.004578 | -0.045776 | -0.24719 | -0.26093 | 0.045777 | 0.30212 | -0.21973 | 0.041198 | -0.13733 | 122.9553 | 122.8317 | 51.5854 | -123.0286 | 122.9233 | 122.7402 | 49.4705 | -123.1384
2248.0156 | 123.1247 | -45.7993 | 77.0325 | 0.21347 | 0.015353 | 0.069532 | 0.072012 | 0.12928 | 0.0044091 | -0.0032321 | 0.17532 | -0.0093396 | 0.063623 | 0.055262 | 0.011472 | -0.012828 | 76.9363 | 77.0828 | 4.7424 | -45.9641 | 77.1881 | -45.8542 | -45.932 | -45.4559 | 2.7466 | -45.7993 | 77.1927 | 77.0691 | -45.9824 | -46.0144 | -0.054932 | -0.13275 | 0.15564 | 122.8821 | -0.16479 | -0.032043 | -0.096131 | -0.18311 | -0.21515 | 0.16022 | 0.34332 | 0 | 0.21515 | 0.036621 | 122.9874 | 122.7356 | 50.5417 | -122.9645 | 122.9919 | 122.8683 | 48.5458 | -123.0469
2249.0156 | 123.0743 | -47.0764 | 75.8377 | 0.15244 | 0.01044 | 0.069105 | 0.070944 | 0.12907 | -0.0015723 | -0.0070773 | 0.19058 | -0.010408 | 0.060846 | 0.056117 | 0.0063446 | -0.012187 | 75.6592 | 75.8789 | 4.6326 | -47.2137 | 75.9338 | -47.0718 | -47.1588 | -46.7926 | 2.2751 | -47.1954 | 75.8423 | 75.7462 | -47.2687 | -47.319 | 0.004578 | -0.082397 | 0.09613 | 122.9553 | -0.13733 | -0.054932 | -0.17853 | -0.19226 | -0.24262 | 0.004577 | 0.28381 | -0.11902 | 0.1236 | -0.091553 | 123.0103 | 122.7356 | 51.709 | -122.9965 | 122.9187 | 122.8226 | 49.3515 | -123.1567
2250.0156 | 123.1338 | -46.6644 | 76.1124 | 0.19821 | 0.012149 | 0.068891 | 0.072226 | 0.13206 | 0.0022729 | -0.0032321 | 0.20584 | -0.0084852 | 0.060846 | 0.056117 | 0.0093354 | -0.012828 | 76.0025 | 76.149 | 4.628 | -46.9116 | 76.2268 | -46.7972 | -46.8933 | -46.3989 | 2.7969 | -46.6827 | 76.2863 | 76.1719 | -46.8201 | -46.8658 | -0.13275 | -0.22888 | 0.11444 | 122.8134 | -0.24719 | -0.01831 | -0.10986 | -0.15564 | -0.20142 | 0.17395 | 0.2655 | -0.01831 | 0.18311 | 0.059509 | 122.8912 | 122.6669 | 51.2924 | -123.0057 | 122.9507 | 122.8363 | 49.4614 | -122.9782
2251.0156 | 123.1018 | -48.1018 | 74.7757 | 0.16006 | 0.011294 | 0.069746 | 0.069876 | 0.12928 | -0.0039221 | -0.0043003 | 0.22873 | -0.0093396 | 0.064264 | 0.058253 | 0.0074126 | -0.0087692 | 74.5422 | 74.7437 | 4.303 | -48.3353 | 74.7757 | -48.23 | -48.3261 | -47.8317 | 2.5406 | -48.2162 | 74.8215 | 74.7391 | -48.3307 | -48.3536 | -0.12817 | -0.2243 | 0 | 122.8455 | -0.23346 | -0.009155 | -0.23346 | -0.22888 | -0.25177 | 0.045776 | 0.27008 | -0.11444 | 0.13733 | -0.036621 | 122.8775 | 122.644 | 52.4048 | -123.1018 | 122.9233 | 122.8409 | 50.6424 | -123.1293
2252.0156 | 123.056 | -48.0698 | 74.8215 | 0.12955 | 0.017703 | 0.068464 | 0.069876 | 0.12928 | 0.0018457 | -0.0051547 | 0.14481 | -0.008058 | 0.06341 | 0.058894 | 0.0084808 | -0.012828 | 74.5972 | 74.7025 | 4.4037 | -48.3261 | 74.8856 | -48.1888 | -48.2803 | -47.7905 | 2.2705 | -48.1018 | 74.9268 | 74.7894 | -48.2483 | -48.2986 | -0.11902 | -0.21057 | 0.064087 | 122.7722 | -0.25635 | -0.045777 | -0.2243 | -0.17853 | -0.22888 | 0.10529 | 0.27924 | -0.032044 | 0.19684 | -0.032043 | 122.9553 | 122.6669 | 52.4734 | -123.1018 | 122.9965 | 122.8592 | 50.3403 | -123.1201
2253.0156 | 123.1201 | -48.2529 | 74.5743 | 0.19058 | 0.013644 | 0.066541 | 0.070303 | 0.12971 | 0.00099115 | -0.0032321 | 0.19821 | -0.010408 | 0.062555 | 0.057826 | 0.010831 | -0.01176 | 74.6841 | 74.826 | 4.303 | -48.2162 | 75.0183 | -48.0652 | -48.2025 | -48.0789 | 2.1927 | -48.6237 | 74.6521 | 74.5834 | -48.4909 | -48.5229 | 0.18768 | 0.050354 | 0.44403 | 123.0789 | 0.036621 | -0.013733 | 0.10986 | -0.23804 | -0.27008 | 0.07782 | 0.17395 | -0.37079 | -0.10071 | 0.009155 | 123.2712 | 122.937 | 52.5558 | -122.7768 | 122.905 | 122.8363 | 50.4456 | -123.0972
2254.0156 | 122.9553 | -47.3785 | 75.5447 | 0.0074768 | 0.017703 | 0.068678 | 0.073721 | 0.12779 | 0.0024865 | -0.0030185 | -0.038299 | -0.008058 | 0.068109 | 0.055903 | 0.01019 | -0.010478 | 75.5402 | 75.65 | 4.5776 | -47.3969 | 75.824 | -47.2458 | -47.3282 | -47.081 | 2.3758 | -47.5983 | 75.7416 | 75.5676 | -47.5159 | -47.612 | 0.13275 | 0.050354 | 0.27924 | 123.0286 | -0.018311 | -0.068665 | -0.004578 | -0.13733 | -0.23346 | 0.19684 | 0.29755 | -0.21973 | 0.013733 | 0.022888 | 123.2025 | 122.9187 | 51.9562 | -122.8729 | 123.1201 | 122.9462 | 49.7543 | -123.1567
2255.0156 | 123.1155 | -49.5895 | 73.201 | 0.18295 | 0.016208 | 0.066969 | 0.072226 | 0.12993 | 0.00013675 | -0.0049411 | 0.18295 | -0.0078442 | 0.06341 | 0.05868 | 0.0074126 | -0.010692 | 73.6267 | 73.8007 | 4.0192 | -49.2966 | 73.9014 | -49.1776 | -49.324 | -49.0952 | 1.7532 | -50.0519 | 73.526 | 73.3978 | -49.6536 | -49.7635 | 0.41199 | 0.2655 | 0.70038 | 123.3902 | 0.29297 | 0.027466 | 0.42572 | -0.064086 | -0.17395 | 0.32501 | 0.49439 | -0.46234 | -0.28839 | 0.19684 | 123.4909 | 123.2162 | 53.6087 | -122.525 | 123.1155 | 122.9874 | 51.3428 | -122.9645
2256.0156 | 123.0331 | -49.8642 | 73.0408 | 0.14481 | 0.014712 | 0.066328 | 0.071372 | 0.12993 | 0.0024865 | -0.0051547 | -0.66391 | -0.006349 | 0.065546 | 0.059962 | 0.007199 | -0.012614 | 73.027 | 72.8394 | 3.6255 | -49.9603 | 73.3566 | -49.7406 | -49.823 | -49.5987 | 0.86517 | -50.2579 | 73.1873 | 73.0637 | -50.0473 | -50.1114 | 0.1236 | 0.041199 | 0.31586 | 122.7036 | -0.09613 | -0.13733 | -0.013732 | -0.18311 | -0.24719 | 0.14648 | 0.2655 | -0.39368 | -0.14648 | 0.022889 | 123.2208 | 122.8912 | 53.4897 | -122.8638 | 123.0515 | 122.9279 | 50.7294 | -123.1522
2257.0156 | 123.1522 | -50.3174 | 72.4869 | 0.15244 | 0.01279 | 0.06825 | 0.070731 | 0.12886 | -0.00050425 | -0.0040867 | 0.23636 | -0.0078442 | 0.059564 | 0.057398 | 0.00784 | -0.012187 | 72.4182 | 72.6334 | 3.8269 | -50.3952 | 72.6654 | -50.3357 | -50.4501 | -49.9786 | 1.149 | -50.473 | 72.5601 | 72.4594 | -50.56 | -50.592 | -0.01831 | -0.13275 | 0.17853 | 122.9507 | -0.07782 | 0.054931 | -0.068664 | -0.24262 | -0.27466 | 0.073243 | 0.33875 | -0.15564 | 0.11902 | -0.027465 | 122.9828 | 122.7356 | 54.1443 | -122.937 | 122.8775 | 122.7768 | 51.4664 | -123.0789
2258.0156 | 123.0103 | -50.4593 | 72.5098 | 0.030365 | 0.016421 | 0.068037 | 0.073294 | 0.12544 | 0.0022729 | -0.0017369 | 0.16006 | -0.005708 | 0.062982 | 0.055476 | 0.0097626 | -0.011119 | 72.2672 | 72.3816 | 3.6484 | -50.6607 | 72.583 | -50.5142 | -50.5966 | -50.2853 | 0.83313 | -50.6699 | 72.5281 | 72.4365 | -50.6287 | -50.7019 | -0.054931 | -0.13733 | 0.073242 | 122.8409 | -0.20142 | -0.064087 | -0.24262 | -0.16937 | -0.24261 | 0.01831 | 0.17395 | -0.21057 | 0.032043 | -0.073243 | 123.0423 | 122.7264 | 54.1077 | -123.1064 | 122.9874 | 122.8958 | 51.2924 | -123.2117
2259.0156 | 123.1064 | -51.2878 | 71.5576 | 0.16769 | 0.013003 | 0.06825 | 0.069663 | 0.12693 | -0.0011451 | -0.0049411 | 0.20584 | -0.0086988 | 0.064264 | 0.055903 | 0.00784 | -0.010905 | 71.4615 | 71.5942 | 3.5843 | -51.4664 | 71.7224 | -51.3245 | -51.4023 | -50.9811 | 0.75989 | -51.4069 | 71.6629 | 71.5439 | -51.5167 | -51.535 | -0.036621 | -0.11444 | 0.1648 | 122.8821 | -0.17853 | -0.064087 | -0.09613 | -0.22888 | -0.24719 | 0.10529 | 0.3067 | -0.11902 | 0.12817 | -0.013733 | 123.0103 | 122.7493 | 54.8721 | -122.9599 | 122.9507 | 122.8317 | 52.0477 | -123.0927
2260.0156 | 123.0698 | -49.1638 | 73.7503 | -0.11459 | 0.018771 | 0.069532 | 0.069449 | 0.12907 | 0.00013675 | -0.0043003 | -0.00015237 | -0.0099806 | 0.062555 | 0.056758 | 0.00784 | -0.010478 | 73.6816 | 73.819 | 4.1107 | -49.2645 | 73.9609 | -49.1364 | -49.2279 | -48.9624 | 1.5015 | -49.4659 | 73.764 | 73.6725 | -49.4247 | -49.4476 | 0.027465 | -0.064087 | 0.21057 | 122.9828 | -0.10071 | -0.036621 | -0.068664 | -0.26093 | -0.28381 | 0.013733 | 0.20142 | -0.30212 | -0.01831 | -0.07782 | 123.1247 | 122.8455 | 53.2745 | -122.9782 | 122.9279 | 122.8363 | 50.6653 | -123.1979
2261.0156 | 122.9919 | -49.1043 | 73.7 | 0.0074768 | 0.015994 | 0.066328 | 0.073081 | 0.12758 | 0.00099115 | -0.0051547 | 0.068512 | -0.0067762 | 0.065332 | 0.057398 | 0.008908 | -0.010692 | 74.0158 | 74.1898 | 4.0787 | -48.8754 | 74.3317 | -48.7198 | -48.8525 | -48.7839 | 1.5793 | -49.1867 | 74.0616 | 73.97 | -49.1135 | -49.1913 | 0.38452 | 0.25177 | 0.63171 | 123.2941 | 0.22888 | -0.022888 | 0.31586 | -0.009155 | -0.086975 | 0.36163 | 0.32043 | -0.082398 | 0.004577 | 0.27008 | 123.436 | 123.1201 | 53.183 | -122.5525 | 123.1659 | 123.0743 | 50.6836 | -122.8912
2262.0156 | 123.0606 | -49.1867 | 73.6862 | -0.10696 | 0.01813 | 0.068037 | 0.072012 | 0.13206 | 0.0014185 | -0.0049411 | -0.045929 | -0.0059216 | 0.062555 | 0.057398 | 0.011472 | -0.01176 | 73.7778 | 73.9609 | 4.0329 | -49.0448 | 74.0845 | -48.9716 | -49.0494 | -49.0723 | 1.7853 | -49.6124 | 73.7503 | 73.6542 | -49.4339 | -49.4797 | 0.21515 | 0.13733 | 0.39826 | 123.1476 | 0.14191 | 0.004577 | 0.091553 | -0.24719 | -0.29297 | 0.064087 | 0.11444 | -0.42572 | -0.13275 | -0.032043 | 123.2712 | 122.9645 | 53.2196 | -122.7356 | 122.937 | 122.8409 | 50.972 | -123.1659
2263.0156 | 122.9965 | -49.2874 | 73.6542 | -0.061188 | 0.016635 | 0.067182 | 0.070303 | 0.13206 | 0.00056395 | -0.0038731 | 0.12955 | -0.0082716 | 0.062769 | 0.058467 | 0.00784 | -0.010051 | 73.1003 | 73.3246 | 3.8544 | -49.6994 | 73.5397 | -49.5667 | -49.6216 | -49.1089 | 1.7578 | -49.411 | 73.6542 | 73.613 | -49.5117 | -49.53 | -0.27923 | -0.33417 | -0.11444 | 122.612 | -0.41199 | -0.07782 | -0.55389 | -0.2243 | -0.24261 | 0 | 0.17853 | -0.1236 | 0.11902 | -0.041199 | 122.8271 | 122.3877 | 53.1418 | -123.2758 | 122.9416 | 122.9004 | 51.0452 | -123.1842
2264.0156 | 123.0286 | -48.8159 | 74.1028 | -0.091705 | 0.014285 | 0.068678 | 0.073508 | 0.12886 | 0.0014185 | -0.0025913 | -0.045929 | -0.0086988 | 0.063623 | 0.055903 | 0.0063446 | -0.0087692 | 74.0295 | 74.1623 | 3.8864 | -48.8708 | 74.3362 | -48.7656 | -48.8434 | -48.6603 | 1.6251 | -49.0219 | 74.1394 | 74.057 | -49.0356 | -49.0677 | 0.050354 | -0.027466 | 0.23346 | 122.9782 | -0.054932 | -0.027466 | -0.073242 | -0.21973 | -0.25177 | 0.036621 | 0.15564 | -0.20599 | 0.045776 | -0.045776 | 123.1522 | 122.8455 | 52.7023 | -122.9462 | 122.9553 | 122.8729 | 50.441 | -123.1705
2265.0156 | 123.0194 | -49.2599 | 73.6771 | 0.053253 | 0.017062 | 0.071882 | 0.072226 | 0.1295 | -0.0019995 | -0.0047275 | 0.18295 | -0.0082716 | 0.065119 | 0.05633 | 0.0080536 | -0.010692 | 73.2971 | 73.3932 | 3.6346 | -49.6033 | 73.6221 | -49.4431 | -49.5346 | -49.1089 | 1.7258 | -49.5438 | 73.7274 | 73.6404 | -49.4705 | -49.53 | -0.1831 | -0.27466 | -0.054932 | 122.6532 | -0.34332 | -0.068664 | -0.37994 | -0.21057 | -0.27008 | 0.050354 | 0.15106 | -0.28381 | -0.013733 | -0.036621 | 122.8821 | 122.5571 | 52.8946 | -123.2117 | 122.9874 | 122.9004 | 50.9857 | -123.2071
2266.0156 | 123.0835 | -48.6649 | 74.2676 | -0.19089 | 0.015994 | 0.069105 | 0.072226 | 0.13014 | -0.00029045 | -0.0047275 | -0.11459 | -0.0093396 | 0.063623 | 0.05868 | 0.00549 | -0.01176 | 74.1623 | 74.3134 | 3.9734 | -48.7518 | 74.4598 | -48.6237 | -48.7152 | -48.3856 | 1.9455 | -48.9212 | 74.3683 | 74.263 | -48.8342 | -48.9212 | 0.041199 | -0.050354 | 0.19226 | 122.9782 | -0.086975 | -0.036621 | -0.10529 | -0.16937 | -0.25635 | 0.10071 | 0.27924 | -0.25635 | 0 | -0.004578 | 123.1247 | 122.8271 | 52.6382 | -122.9828 | 123.0331 | 122.9279 | 50.6104 | -123.1888
2267.0156 | 123.0881 | -48.1979 | 74.6658 | 0.16006 | 0.011508 | 0.069959 | 0.070731 | 0.12672 | -0.0039221 | -0.0040867 | 0.27451 | -0.0093396 | 0.065973 | 0.056971 | 0.0067718 | -0.010051 | 74.4598 | 74.7574 | 4.2938 | -48.2391 | 74.7803 | -48.1979 | -48.2529 | -47.8363 | 1.8585 | -48.1567 | 74.8215 | 74.7391 | -48.3673 | -48.4406 | 0 | -0.054932 | 0.11444 | 122.9553 | -0.041199 | 0.013733 | -0.20599 | -0.16937 | -0.24261 | 0.15564 | 0.36163 | 0.041199 | 0.28381 | 0.073242 | 122.9782 | 122.6578 | 52.4918 | -122.9187 | 123.0194 | 122.937 | 50.0565 | -123.1064
2268.0156 | 123.0377 | -49.4843 | 73.4299 | -0.23666 | 0.011722 | 0.069746 | 0.071585 | 0.12822 | -0.0028541 | -0.0087863 | -0.091705 | -0.006349 | 0.063196 | 0.056544 | 0.0057038 | -0.010905 | 73.2239 | 73.3383 | 3.3508 | -49.6902 | 73.526 | -49.5529 | -49.6445 | -49.2691 | 1.9913 | -49.6719 | 73.526 | 73.439 | -49.6857 | -49.7269 | -0.068664 | -0.16022 | 0.09613 | 122.8226 | -0.20599 | -0.045777 | -0.20599 | -0.20142 | -0.24262 | 0.09613 | 0.21515 | -0.18768 | 0.054932 | 0.009155 | 123.0103 | 122.7081 | 52.8351 | -123.0743 | 123.0103 | 122.9233 | 51.4755 | -123.1567
2269.0156 | 122.9965 | -49.3698 | 73.5535 | 0.37369 | 0.017489 | 0.071455 | 0.071585 | 0.12971 | 0.0024865 | -0.0036595 | -0.03067 | -0.0084852 | 0.064691 | 0.057826 | 0.0080536 | -0.010265 | 73.2285 | 73.3658 | 3.4882 | -49.7223 | 73.4985 | -49.5621 | -49.6536 | -49.1959 | 2.2476 | -49.5987 | 73.5672 | 73.4756 | -49.6307 | -49.6628 | -0.19226 | -0.28381 | -0.054932 | 122.7356 | -0.35248 | -0.068665 | -0.32501 | -0.26093 | -0.29297 | 0.013733 | 0.17395 | -0.22888 | 0.064087 | -0.07782 | 122.8683 | 122.5983 | 52.858 | -123.2071 | 122.937 | 122.8455 | 51.6174 | -123.2162
2270.0156 | 123.0194 | -48.6053 | 74.3134 | -0.25955 | 0.012362 | 0.069319 | 0.070944 | 0.12758 | -0.00050425 | -0.0062229 | -0.168 | -0.0076306 | 0.062555 | 0.05868 | 0.0091216 | -0.010478 | 74.2355 | 74.3958 | 3.8498 | -48.6694 | 74.5697 | -48.5229 | -48.6145 | -48.3307 | 2.5726 | -48.6969 | 74.4781 | 74.3912 | -48.7244 | -48.7885 | 0.082398 | -0.009155 | 0.25635 | 123.0011 | -0.064087 | -0.054932 | -0.077819 | -0.11902 | -0.1831 | 0.16479 | 0.27466 | -0.091552 | 0.091553 | 0.07782 | 123.175 | 122.8409 | 52.4551 | -122.9279 | 123.0835 | 122.9965 | 51.178 | -123.1018
2271.0156 | 123.0331 | -49.3881 | 73.5443 | -0.22141 | 0.013431 | 0.071455 | 0.072867 | 0.13142 | 0.0014185 | -0.0057957 | -0.091705 | -0.0082716 | 0.063623 | 0.057185 | 0.0063446 | -0.012187 | 73.3154 | 73.494 | 3.6392 | -49.5621 | 73.6496 | -49.4751 | -49.5438 | -49.173 | 2.504 | -49.649 | 73.5535 | 73.4802 | -49.6262 | -49.6445 | -0.086975 | -0.15564 | 0.10528 | 122.8821 | -0.17395 | -0.018311 | -0.22888 | -0.23804 | -0.25635 | 0.009155 | 0.21515 | -0.26093 | -0.004578 | -0.064087 | 123.0377 | 122.7036 | 53.0273 | -123.0881 | 122.9416 | 122.8683 | 51.8921 | -123.1888
2272.0156 | 122.9416 | -49.8825 | 73.0774 | -0.25192 | 0.010013 | 0.071241 | 0.071158 | 0.13035 | -0.0030677 | -0.0079319 | -0.13748 | -0.010835 | 0.064051 | 0.05868 | 0.0052764 | -0.011546 | 72.8119 | 73.0041 | 2.6413 | -50.0885 | 73.1689 | -49.9558 | -50.029 | -49.6353 | 2.1744 | -49.9924 | 73.1461 | 73.0499 | -50.0702 | -50.1022 | -0.073243 | -0.14649 | 0.091552 | 122.8867 | -0.20599 | -0.059509 | -0.2655 | -0.18768 | -0.21973 | 0.068664 | 0.24719 | -0.10986 | 0.10986 | -0.027466 | 123.0515 | 122.6944 | 52.5238 | -123.1064 | 123.0286 | 122.9324 | 52.0569 | -123.1796
2273.0156 | 123.0423 | -48.8113 | 74.1302 | -0.22903 | 0.013858 | 0.06825 | 0.073508 | 0.13099 | -0.0011451 | -0.0053683 | -0.13748 | -0.0082716 | 0.062982 | 0.057185 | 0.0063446 | -0.013255 | 73.8144 | 73.9563 | 2.9114 | -49.0814 | 74.1257 | -48.9487 | -49.054 | -48.5367 | 2.124 | -48.8983 | 74.2355 | 74.1348 | -48.9899 | -49.0494 | -0.13733 | -0.24262 | -0.004578 | 122.7676 | -0.27008 | -0.027466 | -0.31586 | -0.17853 | -0.23804 | 0.10529 | 0.27466 | -0.086975 | 0.15106 | 0.004578 | 122.937 | 122.6257 | 51.7227 | -123.1842 | 123.0469 | 122.9462 | 50.9354 | -123.1796
2274.0156 | 123.1201 | -47.8317 | 75.0504 | -0.168 | 0.0089443 | 0.073805 | 0.077353 | 0.12758 | -0.00071785 | -0.0049411 | -0.076446 | -0.010408 | 0.061914 | 0.058039 | 0.0050628 | -0.0096238 | 74.3317 | 74.8672 | 3.5248 | -48.2986 | 74.8398 | -48.1476 | -48.1934 | -47.5891 | 2.2797 | -47.8317 | 75.0458 | 74.9863 | -48.0652 | -48.0972 | -0.31586 | -0.36163 | -0.21057 | 122.699 | -0.46692 | -0.10529 | -0.71869 | -0.23346 | -0.2655 | -0.004578 | 0.24262 | 0 | 0.2655 | -0.064087 | 122.6715 | 122.1634 | 51.3565 | -123.2437 | 122.8775 | 122.818 | 50.1114 | -123.1476
2275.0156 | 123.056 | -49.8413 | 73.0545 | -0.19852 | 0.014712 | 0.068464 | 0.075644 | 0.12758 | 0.0012047 | -0.0057957 | -0.14511 | -0.0072034 | 0.064691 | 0.056758 | 0.004422 | -0.013896 | 72.908 | 73.0408 | 3.1219 | -50.0381 | 73.2422 | -49.8962 | -49.9878 | -49.6033 | 1.6663 | -50.0473 | 73.1506 | 73.0316 | -50.0336 | -50.0931 | -0.054931 | -0.14648 | 0.18768 | 122.8821 | -0.19684 | -0.050354 | -0.14648 | -0.19226 | -0.25177 | 0.096131 | 0.23804 | -0.20599 | 0.045777 | -0.022888 | 123.0835 | 122.7493 | 52.9633 | -123.0423 | 122.9919 | 122.8729 | 51.5076 | -123.1476
2276.0156 | 123.0652 | -48.7198 | 74.1852 | -0.22903 | 0.0080899 | 0.068678 | 0.07009 | 0.12758 | -0.0043495 | -0.0066501 | -0.11459 | -0.010194 | 0.061273 | 0.05633 | 0.0046356 | -0.011546 | 74.0387 | 74.231 | 3.4287 | -48.8434 | 74.2905 | -48.7656 | -48.8342 | -48.468 | 2.0554 | -48.8525 | 74.2447 | 74.1714 | -48.9029 | -48.967 | -0.045776 | -0.11444 | 0.10528 | 122.9507 | -0.1236 | -0.009155 | -0.14648 | -0.1831 | -0.24719 | 0.059509 | 0.25177 | -0.13275 | 0.11444 | -0.013733 | 123.0103 | 122.7585 | 52.1484 | -123.0194 | 122.9645 | 122.8912 | 50.7751 | -123.1522
2277.0156 | 123.0103 | -49.8047 | 73.1232 | -0.21378 | 0.010226 | 0.06825 | 0.07244 | 0.12886 | -0.00029045 | -0.0085727 | 1.6859 | -0.007417 | 0.064051 | 0.055476 | 0.0080536 | -0.013683 | 72.8577 | 73.0087 | 3.2501 | -50.029 | 73.233 | -49.8962 | -49.9466 | -49.5529 | 1.9135 | -49.8871 | 73.2468 | 73.1598 | -49.9695 | -50.0244 | -0.091553 | -0.14191 | 0.10986 | 122.8134 | -0.22431 | -0.082398 | -0.2655 | -0.16479 | -0.21973 | 0.1236 | 0.25177 | -0.082398 | 0.13733 | 0.036621 | 123.0377 | 122.6624 | 53.0548 | -123.0698 | 123.0515 | 122.9645 | 51.7181 | -123.1476
2278.0156 | 123.1384 | -49.5438 | 73.3292 | -0.17563 | 0.0072355 | 0.072096 | 0.072226 | 0.12779 | -0.0024269 | -0.0070773 | -0.30533 | -0.010835 | 0.060846 | 0.055476 | 0.0067718 | -0.0096238 | 73.2513 | 73.3521 | 3.4653 | -49.7589 | 73.3704 | -49.6445 | -49.7269 | -49.2279 | 2.0828 | -49.5804 | 73.3704 | 73.32 | -49.7269 | -49.7955 | -0.10071 | -0.18311 | 0.041198 | 122.8958 | -0.21515 | -0.032043 | -0.07782 | -0.18311 | -0.25177 | 0.041198 | 0.31586 | -0.036621 | 0.21515 | -0.009156 | 122.9141 | 122.7951 | 53.009 | -123.056 | 122.9141 | 122.8638 | 51.6266 | -123.1247
2279.0156 | 123.0103 | -48.468 | 74.5056 | -0.24429 | 0.0087307 | 0.070387 | 0.071158 | 0.12993 | -0.0015723 | -0.0062229 | -0.2977 | -0.0093396 | 0.062128 | 0.05868 | 0.0059174 | -0.012401 | 74.4095 | 74.5743 | 3.7857 | -48.6099 | 74.6201 | -48.4497 | -48.5687 | -48.23 | 2.1973 | -48.6282 | 74.5148 | 74.437 | -48.6191 | -48.6877 | 0.018311 | -0.10071 | 0.11444 | 123.0423 | -0.14191 | -0.041198 | -0.09613 | -0.15106 | -0.21973 | 0.009156 | 0.23804 | -0.16022 | 0.059509 | -0.068664 | 123.0881 | 122.8775 | 52.2537 | -123.0743 | 122.9828 | 122.905 | 50.6653 | -123.1934
2280.0156 | 123.175 | -48.381 | 74.3729 | -0.068817 | 0.0083035 | 0.071882 | 0.070944 | 0.12822 | -0.0058447 | -0.0062229 | -0.091705 | -0.009126 | 0.063623 | 0.056117 | 0.0059174 | -0.012828 | 74.5193 | 74.7482 | 4.0924 | -48.3948 | 74.7391 | -48.2941 | -48.3856 | -47.9095 | 2.8152 | -48.3078 | 74.7162 | 74.6201 | -48.3994 | -48.4909 | 0.086975 | -0.004578 | 0.36621 | 123.1293 | -0.013733 | -0.009155 | 0.14648 | -0.018311 | -0.10986 | 0.34332 | 0.4715 | 0.073242 | 0.18311 | 0.24719 | 123.1201 | 122.9004 | 52.4734 | -122.7585 | 123.0972 | 123.0011 | 51.1963 | -122.8638
2281.0156 | 123.1247 | -48.5138 | 74.35 | -0.13748 | 0.0083035 | 0.06761 | 0.071158 | 0.12843 | 0.00035035 | -0.010068 | -1.4421 | -0.0089124 | 0.064051 | 0.054835 | 0.004422 | -0.0087692 | 74.3912 | 74.5789 | 3.8864 | -48.5641 | 74.5697 | -48.4634 | -48.5458 | -48.2346 | 2.4078 | -48.5733 | 74.4003 | 74.3042 | -48.7106 | -48.7381 | 0.050354 | -0.032043 | 0.21973 | 123.0927 | -0.050354 | -0.018311 | 0.041198 | -0.19684 | -0.2243 | 0.050354 | 0.27924 | -0.059509 | 0.16479 | -0.045777 | 123.0835 | 122.905 | 52.4002 | -122.8958 | 122.9141 | 122.818 | 50.9216 | -123.0881
2282.0156 | 123.1613 | -49.2188 | 73.6267 | -0.053558 | 0.0065945 | 0.070173 | 0.070517 | 0.12886 | -0.0019995 | -0.0087863 | 0.037995 | -0.0093396 | 0.062982 | 0.056758 | 0.0057038 | -0.0096238 | 73.6038 | 73.7869 | 3.7079 | -49.3286 | 73.8235 | -49.2096 | -49.3423 | -48.9212 | 2.4582 | -49.3515 | 73.7045 | 73.5947 | -49.411 | -49.4705 | 0.009155 | -0.1236 | 0.19684 | 123.0057 | -0.10986 | 0.013733 | -0.022888 | -0.19226 | -0.25177 | 0.07782 | 0.29755 | -0.13275 | 0.11902 | -0.032043 | 123.0423 | 122.8226 | 52.9266 | -122.9691 | 122.9233 | 122.8134 | 51.6769 | -123.0972
2283.0156 | 123.0835 | -48.8983 | 74.0112 | -0.19089 | 0.0097989 | 0.068891 | 0.07009 | 0.12971 | -0.00029045 | -0.0062229 | -0.15274 | -0.0093396 | 0.062982 | 0.055049 | 0.0074126 | -0.013042 | 73.8464 | 74.0433 | 3.4836 | -49.086 | 74.0799 | -48.9853 | -49.0768 | -48.6877 | 2.6276 | -49.2233 | 74.0021 | 73.8968 | -49.1501 | -49.2004 | -0.086976 | -0.17853 | 0.068665 | 122.9416 | -0.18768 | -0.009156 | -0.16479 | -0.25177 | -0.30212 | -0.009155 | 0.21057 | -0.32501 | -0.022889 | -0.11444 | 122.9782 | 122.7448 | 52.3819 | -123.0881 | 122.9004 | 122.7951 | 51.5259 | -123.2117
2284.0156 | 123.1384 | -49.0128 | 73.8739 | -0.084076 | 0.0087307 | 0.069959 | 0.071585 | 0.12758 | -0.0043495 | -0.0087863 | -0.015411 | -0.0089124 | 0.060633 | 0.055262 | 0.0067718 | -0.011546 | 73.6038 | 73.7412 | 3.5294 | -49.4064 | 73.8052 | -49.2645 | -49.3469 | -48.8251 | 2.7237 | -49.2371 | 73.8007 | 73.7091 | -49.2966 | -49.3103 | -0.25177 | -0.33417 | -0.068664 | 122.7539 | -0.39368 | -0.059509 | -0.27008 | -0.28381 | -0.29755 | -0.073242 | 0.18768 | -0.2243 | 0.073242 | -0.16479 | 122.818 | 122.6166 | 52.5421 | -123.2208 | 122.8134 | 122.7219 | 51.7365 | -123.1842
2285.0156 | 123.1247 | -49.1776 | 73.6679 | -0.168 | 0.0085171 | 0.068891 | 0.070731 | 0.12928 | -0.00093145 | -0.0057957 | 0.30502 | -0.010194 | 0.062128 | 0.05633 | 0.00784 | -0.010905 | 73.3704 | 73.6038 | 3.8452 | -49.3286 | 73.732 | -49.292 | -49.3927 | -48.8892 | 2.742 | -49.3195 | 73.7228 | 73.6313 | -49.4019 | -49.4339 | -0.11444 | -0.21515 | 0.064087 | 122.7814 | -0.15106 | 0.064087 | -0.29755 | -0.2243 | -0.25635 | 0.054931 | 0.28839 | -0.14191 | 0.11444 | -0.036621 | 122.9095 | 122.5479 | 53.0228 | -123.0606 | 122.9004 | 122.8088 | 51.9196 | -123.1018
2286.0156 | 123.1293 | -49.4247 | 73.4482 | 0.28976 | 0.0063809 | 0.069532 | 0.069876 | 0.12993 | -0.0045631 | -0.0070773 | 0.076141 | -0.010621 | 0.061487 | 0.055049 | 0.0069854 | -0.012401 | 73.233 | 73.407 | 3.9459 | -49.6262 | 73.5168 | -49.5163 | -49.5987 | -49.1272 | 2.3895 | -49.4797 | 73.5214 | 73.4207 | -49.6078 | -49.6628 | -0.091552 | -0.17395 | 0.068665 | 122.8317 | -0.20142 | -0.027466 | -0.21515 | -0.18311 | -0.23804 | 0.073242 | 0.29755 | -0.054931 | 0.18311 | -0.027466 | 122.9416 | 122.6578 | 53.3707 | -123.0469 | 122.9462 | 122.8455 | 51.8143 | -123.111
2287.0156 | 123.1705 | -48.7381 | 74.0707 | -0.11459 | 0.0059537 | 0.069746 | 0.069663 | 0.12886 | -0.0030677 | -0.0077183 | 0.0074766 | -0.0089124 | 0.059778 | 0.056758 | 0.0074126 | -0.01176 | 74.0204 | 74.2264 | 4.2206 | -48.9029 | 74.2172 | -48.8022 | -48.9304 | -48.468 | 2.5635 | -48.8708 | 74.144 | 74.0341 | -48.9716 | -48.9944 | -0.064087 | -0.19226 | 0.14648 | 122.9645 | -0.16479 | 0.027466 | -0.050354 | -0.23346 | -0.25635 | 0.073242 | 0.27008 | -0.13275 | 0.1236 | -0.036621 | 122.9553 | 122.7585 | 52.9587 | -123.0011 | 122.8821 | 122.7722 | 51.3016 | -123.0652
2288.0156 | 123.1155 | -47.4884 | 75.3799 | 0.16006 | 0.012362 | 0.070387 | 0.070303 | 0.13014 | -0.0015723 | -0.0043003 | 0.19821 | -0.010194 | 0.061701 | 0.059962 | 0.0099762 | -0.0098374 | 75.2106 | 75.3983 | 4.2938 | -47.7539 | 75.3708 | -47.6166 | -47.7127 | -47.2778 | 3.0899 | -47.5342 | 75.3891 | 75.3387 | -47.6898 | -47.731 | -0.12817 | -0.22431 | -0.009155 | 122.8867 | -0.2655 | -0.041198 | -0.16937 | -0.20142 | -0.24262 | 0.009155 | 0.21057 | -0.045777 | 0.19684 | -0.041199 | 122.8592 | 122.699 | 51.7822 | -123.0927 | 122.8775 | 122.8271 | 50.5783 | -123.111
2289.0156 | 123.1247 | -48.8663 | 74.025 | 0.053253 | 0.0068081 | 0.06825 | 0.071585 | 0.128 | -0.0028541 | -0.0040867 | 0.068512 | -0.010408 | 0.061273 | 0.05398 | 0.0069854 | -0.01176 | 73.8968 | 73.938 | 4.1199 | -49.086 | 74.0707 | -48.9807 | -49.0952 | -48.6786 | 2.4765 | -48.967 | 74.0112 | 73.9426 | -49.0906 | -49.118 | -0.11444 | -0.22888 | 0.045777 | 122.8043 | -0.21973 | 0.009155 | -0.12817 | -0.2243 | -0.25177 | -0.013733 | 0.18768 | -0.10071 | 0.15106 | -0.082397 | 122.937 | 122.7631 | 52.9861 | -123.1201 | 122.8775 | 122.8088 | 51.3428 | -123.143
2290.0156 | 123.0698 | -48.2483 | 74.5972 | 0.083771 | 0.0072355 | 0.069532 | 0.07009 | 0.12523 | -7.6852e-05 | -0.0057957 | 0.13718 | -0.011049 | 0.059778 | 0.057185 | 0.0069854 | -0.011333 | 74.5056 | 74.6429 | 4.0649 | -48.436 | 74.7711 | -48.2986 | -48.3673 | -47.9233 | 2.8931 | -48.3124 | 74.7482 | 74.6109 | -48.3994 | -48.4634 | -0.050354 | -0.11902 | 0.17395 | 122.8912 | -0.18768 | -0.068664 | -0.091553 | -0.15106 | -0.21515 | 0.15106 | 0.32501 | -0.064087 | 0.15106 | 0.013733 | 123.0194 | 122.7539 | 52.3132 | -122.9645 | 122.9965 | 122.8592 | 51.1414 | -123.0606
2291.0156 | 123.143 | -49.5392 | 73.3017 | -0.023041 | 0.0085171 | 0.069319 | 0.070944 | 0.13035 | -0.0015723 | -0.0077183 | -0.023041 | -0.011049 | 0.061701 | 0.056117 | 0.0052764 | -0.011546 | 73.1323 | 73.2193 | 3.5248 | -49.9558 | 73.2559 | -49.8138 | -49.9146 | -49.3332 | 2.6001 | -49.6582 | 73.2651 | 73.1873 | -49.8047 | -49.8367 | -0.27466 | -0.37537 | -0.045777 | 122.7585 | -0.41656 | -0.041199 | -0.16937 | -0.2655 | -0.29755 | -0.036621 | 0.20599 | -0.11902 | 0.17853 | -0.11444 | 122.7951 | 122.6715 | 53.064 | -123.2162 | 122.8043 | 122.7264 | 52.1393 | -123.1384
2292.0156 | 123.0972 | -48.7656 | 74.0753 | 0.11429 | 0.012576 | 0.070387 | 0.073294 | 0.12672 | -0.00029045 | -0.0064365 | 0.19058 | -0.010194 | 0.062982 | 0.058467 | 0.0080536 | -0.012401 | 73.8602 | 74.0479 | 3.7765 | -49.1089 | 74.0616 | -48.9532 | -49.0585 | -48.4955 | 2.5497 | -48.8846 | 74.1211 | 74.0204 | -48.9761 | -49.0311 | -0.18768 | -0.29297 | -0.013733 | 122.8134 | -0.34332 | -0.050354 | -0.21515 | -0.21057 | -0.2655 | 0.045777 | 0.27008 | -0.11902 | 0.14648 | -0.054931 | 122.8271 | 122.6257 | 52.5421 | -123.1338 | 122.8867 | 122.7859 | 51.3153 | -123.1064
2293.0156 | 123.0835 | -48.8388 | 73.9975 | -0.18326 | 0.0044583 | 0.068891 | 0.066031 | 0.12736 | 0.00077755 | -0.0062229 | 0.053253 | -0.010194 | 0.059564 | 0.055689 | 0.0074126 | -0.010905 | 73.9609 | 74.1302 | 3.7857 | -48.9349 | 74.2081 | -48.8297 | -48.9532 | -48.468 | 2.4582 | -48.88 | 74.1989 | 74.0707 | -48.9761 | -49.0677 | 0.009155 | -0.11444 | 0.21057 | 122.9691 | -0.096131 | 0.01831 | -0.036622 | -0.13733 | -0.22888 | 0.20142 | 0.37079 | -0.041199 | 0.18768 | 0.073242 | 123.0469 | 122.7997 | 52.6245 | -122.9507 | 123.0377 | 122.9095 | 51.297 | -123.0652
2294.0156 | 123.1842 | -49.2279 | 73.6542 | 0.38132 | 0.015353 | 0.06825 | 0.072012 | 0.13014 | 0.0027001 | -0.0053683 | 0.18295 | -0.0093396 | 0.061701 | 0.056117 | 0.010831 | -0.013255 | 73.6359 | 73.764 | 4.1565 | -49.3103 | 73.7915 | -49.2416 | -49.3057 | -48.9304 | 2.2476 | -49.2462 | 73.7137 | 73.6359 | -49.4019 | -49.4614 | -0.013733 | -0.07782 | 0.13733 | 122.9919 | -0.082398 | -0.004578 | -0.018311 | -0.17395 | -0.23346 | 0.059509 | 0.29755 | -0.018311 | 0.21515 | -0.018311 | 123.0194 | 122.8638 | 53.3844 | -122.9599 | 122.9416 | 122.8638 | 51.4755 | -123.1155
2295.0156 | 123.1018 | -49.3652 | 73.4894 | 0.16006 | 0.011081 | 0.069532 | 0.068381 | 0.12928 | -0.0024269 | -0.0045139 | 0.20584 | -0.0089124 | 0.061701 | 0.055049 | 0.0080536 | -0.010265 | 73.3658 | 73.5352 | 4.3671 | -49.5758 | 73.5809 | -49.4614 | -49.5071 | -49.0402 | 2.2614 | -49.4751 | 73.5672 | 73.4528 | -49.5392 | -49.585 | -0.096131 | -0.14191 | 0.091553 | 122.9004 | -0.21057 | -0.068665 | -0.1236 | -0.17395 | -0.21973 | 0.07782 | 0.32501 | -0.10986 | 0.10986 | -0.036621 | 122.9462 | 122.731 | 53.7323 | -122.9965 | 122.9324 | 122.818 | 51.6266 | -123.0743
2296.0156 | 123.1064 | -49.0906 | 73.7091 | 0.2211 | 0.014712 | 0.069319 | 0.073294 | 0.12971 | 0.0024865 | -0.0034457 | 0.17532 | -0.0076306 | 0.060205 | 0.056117 | 0.008908 | -0.010905 | 73.6084 | 73.8235 | 4.4632 | -49.2233 | 73.9059 | -49.086 | -49.1959 | -48.6237 | 2.3346 | -49.3927 | 73.9059 | 73.764 | -49.2645 | -49.2966 | 0.004577 | -0.10529 | 0.19684 | 122.9141 | -0.13275 | -0.027466 | -0.10071 | -0.17395 | -0.20599 | 0.19684 | 0.46692 | -0.30212 | -0.09613 | 0.054932 | 122.9965 | 122.699 | 53.5538 | -122.905 | 122.9965 | 122.8546 | 51.4252 | -123.0057
2297.0156 | 123.1064 | -49.3378 | 73.5397 | -0.38925 | 0.0046719 | 0.069319 | 0.069235 | 0.12758 | -0.0058447 | -0.0057957 | 0.053253 | -0.0097668 | 0.06106 | 0.056544 | 0.0067718 | -0.011546 | 73.3292 | 73.494 | 4.5776 | -49.5987 | 73.5901 | -49.4705 | -49.585 | -49.0723 | 2.5589 | -49.324 | 73.5809 | 73.4848 | -49.5575 | -49.5941 | -0.13275 | -0.24719 | 0.050354 | 122.8317 | -0.26093 | -0.013733 | -0.21057 | -0.21973 | -0.25635 | 0.041199 | 0.2655 | 0.013733 | 0.27008 | -0.054932 | 122.9279 | 122.6669 | 53.9154 | -123.1247 | 122.9187 | 122.8226 | 51.8967 | -123.1338
2298.0156 | 123.1018 | -49.7726 | 73.0682 | 0.25162 | 0.013217 | 0.070814 | 0.072012 | 0.13014 | 0.00056395 | -0.0055821 | 0.16769 | -0.0099806 | 0.06106 | 0.056117 | 0.0080536 | -0.012828 | 73.1186 | 73.2193 | 4.4724 | -49.9832 | 73.2056 | -49.8276 | -49.9466 | -49.4751 | 2.4902 | -49.9466 | 73.1461 | 73.027 | -49.9786 | -50.029 | -0.054932 | -0.17395 | 0.13733 | 122.9919 | -0.21057 | -0.036621 | 0.050354 | -0.20599 | -0.25635 | 0.07782 | 0.29755 | -0.17395 | 0.082398 | -0.041198 | 122.9782 | 122.8912 | 54.245 | -123.0148 | 122.9187 | 122.7997 | 52.2629 | -123.0972
2299.0156 | 123.1018 | -48.5779 | 74.3042 | 0.12192 | 0.0074491 | 0.069532 | 0.069022 | 0.128 | -0.0019995 | -0.0036595 | 0.11429 | -0.010408 | 0.061487 | 0.056117 | 0.0091216 | -0.011546 | 74.1852 | 74.3774 | 4.7607 | -48.6694 | 74.4873 | -48.5687 | -48.6328 | -48.4131 | 2.6871 | -48.8205 | 74.2859 | 74.1852 | -48.8205 | -48.8434 | 0.009155 | -0.054931 | 0.18311 | 122.9553 | -0.091553 | -0.036622 | -0.11902 | -0.24262 | -0.2655 | -0.01831 | 0.16479 | -0.24262 | 0.022888 | -0.11902 | 123.0652 | 122.7631 | 53.3386 | -122.937 | 122.8638 | 122.7631 | 51.265 | -123.1476
2300.0156 | 123.1247 | -48.8297 | 74.0158 | 0.18295 | 0.018558 | 0.06825 | 0.072867 | 0.12971 | 0.0029137 | -0.0045139 | 0.13718 | -0.0082716 | 0.063623 | 0.057398 | 0.0091216 | -0.0091966 | 73.8968 | 73.97 | 4.5044 | -49.0677 | 74.1394 | -48.9395 | -49.0311 | -48.5092 | 2.3666 | -48.9166 | 74.1669 | 74.0524 | -49.0173 | -49.0677 | -0.10986 | -0.20142 | 0.1236 | 122.7997 | -0.23804 | -0.036621 | -0.11902 | -0.18768 | -0.23804 | 0.15106 | 0.32043 | -0.086975 | 0.15106 | 0.036621 | 122.9691 | 122.7264 | 53.334 | -123.0469 | 122.9965 | 122.8821 | 51.1963 | -123.0835
2301.0156 | 123.1338 | -48.4817 | 74.3454 | 0.16006 | 0.013431 | 0.067396 | 0.072226 | 0.12907 | -7.6852e-05 | -0.0045139 | -0.18326 | -0.0097668 | 0.060419 | 0.057826 | 0.007199 | -0.011546 | 74.501 | 74.4049 | 4.1153 | -48.5596 | 74.5743 | -48.5001 | -48.587 | -48.1888 | 2.8198 | -48.7289 | 74.4186 | 74.3408 | -48.7061 | -48.7427 | -0.018311 | -0.10529 | 0.22888 | 122.8867 | -0.07782 | 0.027466 | 0.15564 | -0.22431 | -0.26093 | 0.073242 | 0.29297 | -0.24719 | 0.013733 | -0.004578 | 123.056 | 122.9828 | 52.597 | -122.9324 | 122.9004 | 122.8226 | 51.3016 | -123.0881
2302.0156 | 122.9874 | -49.3103 | 73.613 | 0.060882 | 0.01578 | 0.068891 | 0.072867 | 0.13014 | 0.0037683 | -0.0032321 | 0.083771 | -0.0086988 | 0.065119 | 0.057398 | 0.0076264 | -0.012828 | 73.3704 | 73.4573 | 3.9642 | -49.5529 | 73.7045 | -49.4247 | -49.5209 | -49.1684 | 2.536 | -49.6078 | 73.6633 | 73.5489 | -49.5483 | -49.6033 | -0.11444 | -0.21057 | 0.091553 | 122.7676 | -0.24261 | -0.032043 | -0.24262 | -0.23804 | -0.29297 | 0.050354 | 0.14191 | -0.29755 | -0.004578 | -0.064087 | 123.0148 | 122.6807 | 53.2745 | -123.1338 | 122.9736 | 122.8592 | 51.8463 | -123.2162
2303.0156 | 123.143 | -49.8367 | 72.9996 | 0.18295 | 0.01279 | 0.068891 | 0.068167 | 0.13035 | 0.0016321 | -0.0051547 | 0.18295 | -0.008058 | 0.063623 | 0.055689 | 0.006131 | -0.010051 | 72.8577 | 72.9767 | 4.1016 | -50.0748 | 73.082 | -49.9878 | -50.0748 | -49.5987 | 2.5635 | -50.0244 | 73.0408 | 72.963 | -50.061 | -50.0931 | -0.15106 | -0.23804 | 0.082397 | 122.8134 | -0.23804 | 0 | -0.14191 | -0.2243 | -0.25635 | 0.041198 | 0.23804 | -0.18768 | 0.068665 | -0.036621 | 122.9187 | 122.6944 | 53.9383 | -123.0743 | 122.8775 | 122.7997 | 52.4002 | -123.0927
2304.0156 | 123.024 | -48.9487 | 73.97 | 0.15244 | 0.01514 | 0.068678 | 0.070731 | 0.12822 | 0.0048363 | -0.0032321 | -0.22903 | -0.0072034 | 0.063623 | 0.058039 | 0.0091216 | -0.010478 | 73.6908 | 74.0936 | 4.4495 | -49.1684 | 74.0845 | -49.0173 | -49.0997 | -48.7244 | 2.6917 | -49.1592 | 74.0616 | 73.9426 | -49.1501 | -49.2096 | -0.068665 | -0.15106 | 0.11444 | 123.0423 | -0.21973 | -0.068665 | -0.27924 | -0.20142 | -0.26093 | 0.091552 | 0.2243 | -0.21057 | 0.050354 | -0.027466 | 123.0331 | 122.6395 | 53.3981 | -123.0698 | 123.0103 | 122.8912 | 51.6403 | -123.1796
2305.0156 | 123.1201 | -49.4156 | 73.4253 | 0.17532 | 0.014285 | 0.067396 | 0.068808 | 0.12779 | 0.00035035 | -0.0047275 | 0.20584 | -0.0086988 | 0.06341 | 0.057612 | 0.0084808 | -0.0098374 | 73.2925 | 73.4207 | 4.0695 | -49.6307 | 73.5306 | -49.5163 | -49.6078 | -49.1409 | 2.3849 | -49.5255 | 73.5168 | 73.407 | -49.6124 | -49.6902 | -0.10071 | -0.19226 | 0.10529 | 122.8363 | -0.21515 | -0.022888 | -0.13275 | -0.19684 | -0.27466 | 0.091553 | 0.27466 | -0.10986 | 0.16479 | -0.018311 | 122.9462 | 122.7081 | 53.4851 | -123.0331 | 122.9324 | 122.8226 | 51.8005 | -123.1155
2306.0156 | 123.0057 | -49.8505 | 73.0682 | 0.015106 | 0.019198 | 0.068891 | 0.072653 | 0.12907 | 0.0024865 | -0.0038731 | -0.045929 | -0.0069898 | 0.062769 | 0.056758 | 0.0097626 | -0.011546 | 72.9675 | 73.0591 | 3.9505 | -50.0107 | 73.2193 | -49.8688 | -49.9786 | -49.617 | 2.3804 | -50.0565 | 73.1644 | 73.0865 | -50.0427 | -50.0885 | -0.01831 | -0.12817 | 0.15106 | 122.9095 | -0.16022 | -0.032043 | -0.10071 | -0.19226 | -0.23804 | 0.096131 | 0.23346 | -0.20599 | 0.032043 | 0.018311 | 123.0698 | 122.818 | 53.801 | -123.0469 | 123.0148 | 122.937 | 52.2308 | -123.1567
2307.0156 | 123.0286 | -49.9558 | 72.9858 | -0.58762 | 0.01514 | 0.066328 | 0.070517 | 0.12629 | -0.00050425 | -0.0030185 | 0.16006 | -0.0078442 | 0.063623 | 0.058467 | 0.0080536 | -0.0096238 | 72.3633 | 72.4823 | 3.6942 | -50.5325 | 72.6974 | -50.3906 | -50.4868 | -49.7314 | 2.3438 | -50.0107 | 73.0179 | 72.9218 | -50.148 | -50.1709 | -0.43487 | -0.53101 | -0.28839 | 122.4381 | -0.57678 | -0.045777 | -0.62256 | -0.19226 | -0.21515 | 0.032043 | 0.22431 | -0.054931 | 0.16022 | -0.064087 | 122.6532 | 122.319 | 53.6499 | -123.4726 | 122.9736 | 122.8775 | 52.2995 | -123.1567
2308.0156 | 123.0927 | -49.9466 | 72.9401 | -0.12985 | 0.015994 | 0.067396 | 0.074362 | 0.13249 | 0.0012047 | -0.0057957 | -0.023041 | -0.0065626 | 0.063837 | 0.058039 | 0.0082672 | -0.01176 | 72.9446 | 73.0728 | 3.8177 | -50.0885 | 73.1415 | -49.9283 | -50.0153 | -49.7635 | 2.4033 | -50.1297 | 73.0362 | 72.9172 | -50.1755 | -50.2075 | 0.01831 | -0.068665 | 0.20142 | 123.0194 | -0.14191 | -0.073242 | 0.004578 | -0.22888 | -0.26093 | 0.096131 | 0.1831 | -0.18311 | 0.07782 | -0.022888 | 123.0881 | 122.8912 | 53.7643 | -122.9553 | 122.9828 | 122.8638 | 52.3499 | -123.1476
2309.0156 | 122.9919 | -48.3582 | 74.5193 | -0.00015269 | 0.013644 | 0.06761 | 0.068808 | 0.12758 | 0.0018457 | -0.0038731 | 0.053253 | -0.0076306 | 0.065332 | 0.055903 | 0.0097626 | -0.012614 | 74.3088 | 74.4644 | 4.0466 | -48.555 | 74.6567 | -48.4268 | -48.5184 | -48.2117 | 2.4857 | -48.5092 | 74.6017 | 74.5285 | -48.587 | -48.642 | -0.068665 | -0.16022 | 0.13733 | 122.8226 | -0.19684 | -0.036621 | -0.21057 | -0.22888 | -0.28381 | 0.082398 | 0.14648 | -0.15106 | 0.13275 | 0.009155 | 123.0148 | 122.6669 | 52.4048 | -123.0377 | 122.9599 | 122.8867 | 50.8438 | -123.1613
2310.0156 | 123.0606 | -50.3494 | 72.5922 | -0.084076 | 0.016635 | 0.068464 | 0.069663 | 0.13249 | 0.00099115 | -0.0053683 | -0.053558 | -0.007417 | 0.063196 | 0.059748 | 0.00784 | -0.013255 | 72.4411 | 72.5693 | 3.3279 | -50.4959 | 72.6883 | -50.3906 | -50.4868 | -49.9924 | 1.9547 | -50.56 | 72.6791 | 72.5784 | -50.5234 | -50.5692 | -0.041199 | -0.13733 | 0.09613 | 122.9187 | -0.14648 | -0.009156 | -0.15106 | -0.17395 | -0.21973 | 0.086975 | 0.35706 | -0.21057 | 0.009155 | -0.013733 | 123.0377 | 122.7905 | 53.6774 | -123.0789 | 123.0286 | 122.9279 | 52.3041 | -123.1613
2311.0156 | 122.9141 | -50.2625 | 72.6608 | 0.11429 | 0.015567 | 0.068891 | 0.073294 | 0.1295 | 0.00077755 | -0.0045139 | 0.12192 | -0.007417 | 0.066187 | 0.056758 | 0.008908 | -0.0072738 | 72.5647 | 72.6837 | 3.1998 | -50.3265 | 72.908 | -50.1938 | -50.2762 | -50.1205 | 1.9318 | -50.441 | 72.757 | 72.6837 | -50.4318 | -50.4593 | 0.068664 | -0.013733 | 0.24719 | 122.9462 | -0.064087 | -0.050354 | -0.096131 | -0.16937 | -0.19684 | 0.09613 | 0.14191 | -0.17853 | 0.018311 | 0.022888 | 123.1705 | 122.8271 | 53.4622 | -122.937 | 123.0194 | 122.9462 | 52.1942 | -123.1201
2312.0156 | 123.0331 | -49.9924 | 72.9172 | -0.10696 | 0.016421 | 0.067823 | 0.073935 | 0.12822 | 0.0029137 | -0.0060093 | 1.3197 | -0.0082716 | 0.062555 | 0.058467 | 0.0080536 | -0.011119 | 72.8851 | 73.0179 | 3.3508 | -50.029 | 73.1369 | -49.9283 | -50.029 | -49.6536 | 2.1011 | -50.1389 | 73.0774 | 72.9721 | -50.1205 | -50.1846 | 0.064087 | -0.036621 | 0.21973 | 123.0103 | -0.036621 | 0 | -0.032043 | -0.12817 | -0.19226 | 0.16022 | 0.33875 | -0.14648 | 0.045776 | 0.054932 | 123.1293 | 122.8775 | 53.3432 | -122.9462 | 123.0698 | 122.9645 | 52.0935 | -123.1018
2313.0156 | 123.0377 | -49.649 | 73.2651 | 0.015106 | 0.017276 | 0.066328 | 0.071585 | 0.12993 | 0.0027001 | -0.0057957 | 0.045624 | -0.0089124 | 0.063623 | 0.057185 | 0.0086944 | -0.010478 | 73.0179 | 73.1644 | 3.7582 | -49.8779 | 73.3658 | -49.7269 | -49.8276 | -49.4888 | 2.1744 | -49.8459 | 73.3658 | 73.2742 | -49.8505 | -49.8871 | -0.07782 | -0.17853 | 0.10071 | 122.8134 | -0.22888 | -0.050354 | -0.24719 | -0.20142 | -0.23804 | 0.10071 | 0.16022 | -0.19684 | 0.041199 | 0.009155 | 123.0148 | 122.6669 | 53.4073 | -123.0927 | 123.0148 | 122.9233 | 51.8234 | -123.1522
2314.0156 | 123.0652 | -49.1821 | 73.7274 | -0.17563 | 0.014926 | 0.070387 | 0.071158 | 0.12843 | 0.00099115 | -0.0047275 | -0.091705 | -0.0082716 | 0.064691 | 0.058039 | 0.0069854 | -0.0096238 | 73.4848 | 73.7 | 4.2206 | -49.2966 | 73.8785 | -49.2371 | -49.2874 | -48.8708 | 1.8768 | -49.1592 | 73.9151 | 73.7869 | -49.3469 | -49.3881 | -0.054932 | -0.10529 | 0.15106 | 122.8821 | -0.11444 | -0.009155 | -0.24262 | -0.16479 | -0.20599 | 0.18768 | 0.31128 | 0.022888 | 0.22888 | 0.059509 | 123.0606 | 122.6669 | 53.4027 | -123.0148 | 123.0972 | 122.9691 | 51.059 | -123.1155
2315.0156 | 123.0927 | -49.2874 | 73.6313 | -0.12222 | 0.01578 | 0.069959 | 0.073508 | 0.13078 | 0.00056395 | -0.0057957 | -0.038299 | -0.0084852 | 0.06341 | 0.05868 | 0.00784 | -0.01176 | 73.3475 | 73.4848 | 3.9963 | -49.5529 | 73.6313 | -49.4339 | -49.5438 | -49.0448 | 2.298 | -49.5209 | 73.6771 | 73.613 | -49.4751 | -49.5117 | -0.14648 | -0.25635 | 0 | 122.7722 | -0.2655 | -0.009155 | -0.28381 | -0.18768 | -0.2243 | 0.045776 | 0.24262 | -0.23346 | -0.009155 | -0.018311 | 122.9187 | 122.6349 | 53.2837 | -123.175 | 122.9645 | 122.9004 | 51.5854 | -123.143
2316.0156 | 123.0423 | -49.8276 | 73.1094 | -0.25955 | 0.012576 | 0.069319 | 0.074362 | 0.12864 | -0.0032813 | -0.0066501 | 0.09903 | -0.007417 | 0.065119 | 0.055689 | 0.0065582 | -0.0070602 | 72.757 | 73.2239 | 4.0787 | -50.1343 | 73.2285 | -49.9146 | -49.9924 | -49.6124 | 1.8402 | -49.9558 | 73.2056 | 73.1323 | -49.9741 | -50.0656 | -0.086975 | -0.16479 | 0.11902 | 123.0515 | -0.3067 | -0.14191 | -0.35248 | -0.14648 | -0.23804 | 0.09613 | 0.21515 | -0.12817 | 0.10986 | 0.022888 | 123.056 | 122.5845 | 53.9062 | -123.1018 | 123.0331 | 122.9599 | 51.6678 | -123.175
2317.0156 | 123.0377 | -48.8892 | 74.025 | -0.10696 | 0.016208 | 0.065473 | 0.07244 | 0.13014 | 0.0012047 | -0.0072911 | 0.55679 | -0.008058 | 0.06341 | 0.058039 | 0.0082672 | -0.011333 | 73.6954 | 73.8739 | 3.9413 | -49.1959 | 74.0067 | -49.0768 | -49.173 | -48.7747 | 1.9913 | -49.118 | 74.0021 | 73.9105 | -49.1821 | -49.2004 | -0.18768 | -0.28381 | -0.01831 | 122.7631 | -0.3067 | -0.022888 | -0.32959 | -0.29297 | -0.31128 | -0.022888 | 0.11444 | -0.22888 | 0.082397 | -0.11444 | 122.8958 | 122.5845 | 52.8305 | -123.1979 | 122.8912 | 122.7997 | 50.8804 | -123.2254
2318.0156 | 123.1018 | -48.9532 | 73.9746 | -0.19852 | 0.014071 | 0.068464 | 0.072012 | 0.12907 | -0.0015723 | -0.0083591 | -0.12222 | -0.0093396 | 0.064478 | 0.057826 | 0.0063446 | -0.0085556 | 73.7823 | 73.9426 | 3.8498 | -49.0952 | 74.1028 | -48.999 | -49.1043 | -48.8068 | 1.6388 | -49.0997 | 74.0112 | 73.9609 | -49.1821 | -49.2188 | -0.045776 | -0.15106 | 0.12817 | 122.8958 | -0.14191 | 0.009155 | -0.19226 | -0.22888 | -0.2655 | 0.036621 | 0.14648 | -0.14648 | 0.11902 | -0.013733 | 123.056 | 122.7356 | 52.803 | -123.0789 | 122.9645 | 122.9141 | 50.592 | -123.1934
2319.0156 | 123.0377 | -49.0448 | 73.8876 | 0.4805 | 0.01514 | 0.067823 | 0.072226 | 0.12779 | 0.00099115 | -0.0045139 | -0.0077819 | -0.007417 | 0.063623 | 0.058253 | 0.0082672 | -0.011119 | 73.7732 | 73.9334 | 3.9276 | -49.1638 | 74.0341 | -49.0311 | -49.1318 | -48.7427 | 1.9821 | -49.2599 | 74.0067 | 73.8739 | -49.2279 | -49.2874 | 0.013733 | -0.086975 | 0.14648 | 122.9782 | -0.11902 | -0.032043 | -0.11444 | -0.1831 | -0.24262 | 0.11902 | 0.30212 | -0.21515 | 0.027466 | -0.013733 | 123.0789 | 122.818 | 52.9724 | -123.0194 | 123.0515 | 122.9187 | 51.0269 | -123.175
2320.0156 | 123.0194 | -48.5779 | 74.3408 | -0.21378 | 0.011508 | 0.070387 | 0.071799 | 0.12907 | -0.00029045 | -0.0079319 | -0.099335 | -0.0082716 | 0.065973 | 0.057185 | 0.00784 | -0.0089828 | 73.8876 | 74.0524 | 4.2526 | -49.0219 | 74.2126 | -48.8754 | -48.9761 | -48.3307 | 2.4261 | -48.6969 | 74.4461 | 74.3729 | -48.761 | -48.7976 | -0.29755 | -0.39825 | -0.12817 | 122.6303 | -0.44403 | -0.045777 | -0.45319 | -0.18311 | -0.21973 | 0.10529 | 0.24719 | -0.11902 | 0.10071 | 0.032044 | 122.7905 | 122.4655 | 52.8305 | -123.317 | 123.024 | 122.9507 | 51.004 | -123.1384
2321.0156 | 123.0652 | -49.6307 | 73.288 | -0.084076 | 0.016421 | 0.068891 | 0.07479 | 0.12928 | 0.00035035 | -0.0051547 | -0.023041 | -0.008058 | 0.063623 | 0.05633 | 0.012326 | -0.013042 | 73.1186 | 73.2697 | 4.0787 | -49.7726 | 73.4161 | -49.6902 | -49.7406 | -49.4019 | 2.4033 | -49.6445 | 73.4482 | 73.3612 | -49.7498 | -49.8184 | -0.05951 | -0.10986 | 0.12817 | 122.9004 | -0.14191 | -0.032043 | -0.16937 | -0.11902 | -0.18768 | 0.16022 | 0.22888 | -0.013733 | 0.17395 | 0.073242 | 123.0469 | 122.7493 | 53.7094 | -123.0286 | 123.0789 | 122.9919 | 52.034 | -123.1064
2322.0156 | 123.024 | -49.5941 | 73.3566 | 0.14481 | 0.014499 | 0.069532 | 0.072867 | 0.12843 | 0.00013675 | -0.0053683 | 0.2211 | -0.007417 | 0.064264 | 0.056971 | 0.0091216 | -0.011333 | 73.1827 | 73.3109 | 3.7491 | -49.7223 | 73.526 | -49.5758 | -49.6628 | -49.3149 | 2.4765 | -49.649 | 73.4711 | 73.3704 | -49.736 | -49.823 | 0.01831 | -0.068665 | 0.16937 | 122.905 | -0.12817 | -0.059509 | -0.17395 | -0.14191 | -0.22888 | 0.11444 | 0.27924 | -0.054932 | 0.17395 | 0.013733 | 123.1201 | 122.7768 | 53.3432 | -123.0194 | 123.0652 | 122.9645 | 52.0706 | -123.1796
2323.0156 | 123.0698 | -49.0631 | 73.8693 | -0.19852 | 0.014285 | 0.070387 | 0.073508 | 0.13099 | -0.0017859 | -0.0066501 | -0.099335 | -0.0072034 | 0.065973 | 0.056544 | 0.0042084 | -0.010905 | 73.645 | 73.7778 | 3.8956 | -49.2554 | 73.9838 | -49.1089 | -49.2279 | -48.8708 | 2.6184 | -49.2188 | 73.9929 | 73.8922 | -49.2325 | -49.2691 | -0.045777 | -0.16479 | 0.11444 | 122.8409 | -0.19226 | -0.027466 | -0.2243 | -0.16937 | -0.20599 | 0.1236 | 0.19226 | -0.15564 | 0.050354 | 0.022888 | 123.0469 | 122.7081 | 52.9587 | -123.0972 | 123.056 | 122.9553 | 51.6815 | -123.1384
2324.0156 | 123.024 | -49.411 | 73.5352 | -0.31296 | 0.013003 | 0.070387 | 0.071158 | 0.12907 | -0.0017859 | -0.0060093 | -0.12222 | -0.0065626 | 0.061273 | 0.057185 | 0.0082672 | -0.012401 | 73.6816 | 73.8373 | 3.6896 | -49.3744 | 73.9426 | -49.2004 | -49.3378 | -49.2462 | 2.5772 | -49.7269 | 73.5809 | 73.4985 | -49.617 | -49.6262 | 0.21057 | 0.073242 | 0.40741 | 123.2483 | 0.036621 | -0.036621 | 0.14648 | -0.20599 | -0.21515 | 0.045777 | 0.1648 | -0.31586 | -0.10071 | -0.036621 | 123.3536 | 123.0927 | 53.1006 | -122.8729 | 122.9919 | 122.9095 | 51.9882 | -123.1613
2325.0156 | 123.0515 | -49.6124 | 73.3109 | -0.061188 | 0.016421 | 0.067823 | 0.071799 | 0.12693 | -7.6852e-05 | -0.0064365 | -0.015411 | -0.009126 | 0.065973 | 0.056544 | 0.0069854 | -0.0098374 | 73.0957 | 73.2285 | 3.4424 | -49.8505 | 73.3566 | -49.7131 | -49.8276 | -49.411 | 2.449 | -49.6811 | 73.3109 | 73.2513 | -49.8367 | -49.8734 | -0.10071 | -0.21515 | 0.045776 | 122.8409 | -0.23804 | -0.022888 | -0.21515 | -0.2243 | -0.26093 | 0 | 0.20142 | -0.068664 | 0.19226 | -0.059509 | 122.9691 | 122.7081 | 53.0548 | -123.1384 | 122.9233 | 122.8638 | 52.0615 | -123.1842
2326.0156 | 123.0606 | -49.5026 | 73.3795 | -0.22903 | 0.010226 | 0.069532 | 0.072226 | 0.12651 | -0.0047767 | -0.010922 | -0.099335 | -0.010194 | 0.063623 | 0.057826 | 0.0080536 | -0.010478 | 73.5352 | 73.2513 | 3.2181 | -49.6353 | 73.6771 | -49.4705 | -49.5667 | -49.3057 | 2.2705 | -49.7223 | 73.5168 | 73.4711 | -49.6994 | -49.7269 | 0.032043 | -0.064087 | 0.29755 | 122.7539 | -0.13275 | -0.068665 | 0.15564 | -0.19684 | -0.22431 | 0.13733 | 0.19684 | -0.21973 | 0.004578 | 0.091552 | 123.1796 | 123.0377 | 52.7206 | -122.9462 | 123.0194 | 122.9736 | 51.7731 | -123.1064
2327.0312 | 123.1384 | -48.9899 | 73.8739 | -0.19089 | 0.0087307 | 0.071241 | 0.068594 | 0.12886 | -0.0084083 | -0.0064365 | -0.54184 | -0.011476 | 0.064691 | 0.05633 | 0.0046356 | -0.010051 | 73.732 | 73.9792 | 3.5934 | -48.8663 | 74.0341 | -48.9899 | -49.0723 | -48.7747 | 2.7145 | -49.1089 | 73.9609 | 73.8831 | -49.205 | -49.2325 | 0 | -0.082398 | 0.16022 | 122.9691 | 0.1236 | 0.20599 | -0.14191 | -0.21515 | -0.24262 | 0.086975 | 0.21515 | -0.11902 | 0.1236 | 0.009156 | 123.024 | 122.7219 | 52.5833 | -122.9462 | 122.9507 | 122.8729 | 51.7044 | -123.1064
2328.0156 | 123.0194 | -48.3902 | 74.5514 | -0.28244 | 0.0083035 | 0.069532 | 0.075858 | 0.12864 | 0.00077755 | -0.0085727 | -0.15274 | -0.0097668 | 0.062982 | 0.05633 | 0.0076264 | -0.012187 | 74.295 | 74.4507 | 3.9139 | -48.6191 | 74.6246 | -48.4772 | -48.5458 | -48.2574 | 2.8656 | -48.3124 | 74.6338 | 74.5651 | -48.555 | -48.6191 | -0.086975 | -0.15564 | 0.073242 | 122.8409 | -0.22888 | -0.073243 | -0.25635 | -0.1648 | -0.22888 | 0.082397 | 0.13275 | 0.07782 | 0.3067 | 0.013733 | 123.0148 | 122.6852 | 52.3041 | -123.0972 | 123.024 | 122.9553 | 51.2558 | -123.1705
2329.0156 | 123.0469 | -47.493 | 75.4623 | -0.084076 | 0.014712 | 0.070814 | 0.073508 | 0.13057 | -0.00029045 | -0.0068637 | -0.20615 | -0.0089124 | 0.064691 | 0.058039 | 0.0063446 | -0.011546 | 75.1648 | 75.3387 | 4.1931 | -47.8088 | 75.4852 | -47.612 | -47.699 | -47.3328 | 3.035 | -47.6395 | 75.5219 | 75.4074 | -47.7036 | -47.7402 | -0.11902 | -0.20599 | 0.022888 | 122.8317 | -0.31586 | -0.10986 | -0.29755 | -0.21057 | -0.24719 | 0.05951 | 0.16022 | -0.14648 | 0.10071 | -0.054931 | 122.9782 | 122.6578 | 51.6861 | -123.1613 | 123.0148 | 122.9004 | 50.528 | -123.2025
2330.0156 | 122.9874 | -48.0194 | 74.9771 | -0.22903 | 0.011935 | 0.070173 | 0.069449 | 0.1295 | -0.0028541 | -0.0089999 | -0.12985 | -0.0086988 | 0.064691 | 0.057185 | 0.0074126 | -0.010265 | 74.707 | 74.9176 | 4.1977 | -48.1567 | 75.0595 | -48.0148 | -48.1018 | -48.0194 | 2.7924 | -48.2437 | 74.8215 | 74.794 | -48.3215 | -48.2849 | 0.004577 | -0.082398 | 0.082397 | 122.937 | -0.13733 | -0.054931 | -0.27008 | -0.30212 | -0.2655 | -0.15564 | 0 | -0.2243 | 0.041199 | -0.18311 | 123.0789 | 122.7264 | 52.2171 | -123.0789 | 122.8409 | 122.8134 | 50.8118 | -123.262
2331.0156 | 123.0606 | -49.4156 | 73.4985 | -0.13748 | 0.014712 | 0.067396 | 0.071372 | 0.128 | 0.00056395 | -0.0057957 | -0.168 | -0.0078442 | 0.064905 | 0.057398 | 0.0076264 | -0.011546 | 73.3383 | 73.4665 | 3.8132 | -49.5941 | 73.6038 | -49.4934 | -49.5987 | -49.2645 | 2.5314 | -49.5941 | 73.5077 | 73.4344 | -49.6536 | -49.6811 | -0.07782 | -0.18311 | 0.10529 | 122.8821 | -0.17853 | 0.004578 | -0.16022 | -0.23804 | -0.2655 | 0.009155 | 0.15106 | -0.17853 | 0.086975 | -0.064087 | 123.0194 | 122.7539 | 53.2288 | -123.0972 | 122.9233 | 122.85 | 51.947 | -123.1796
2332.0156 | 122.9828 | -50.1251 | 72.8165 | 0.076141 | 0.01578 | 0.067396 | 0.072867 | 0.12843 | 0.0029137 | -0.0047275 | 0.0914 | -0.0076306 | 0.067682 | 0.058253 | 0.00784 | -0.011119 | 72.5647 | 72.6929 | 3.4744 | -50.3677 | 72.876 | -50.2167 | -50.3311 | -50.0198 | 2.2705 | -50.3677 | 72.8119 | 72.7341 | -50.3494 | -50.386 | -0.091553 | -0.20599 | 0.05951 | 122.818 | -0.24262 | -0.036621 | -0.25177 | -0.2243 | -0.26093 | -0.004577 | 0.10529 | -0.24262 | 0.01831 | -0.082397 | 123.0011 | 122.6898 | 53.5995 | -123.1476 | 122.937 | 122.8592 | 52.3956 | -123.2025
2333.0156 | 123.0515 | -48.5962 | 74.3362 | -0.20615 | 0.016421 | 0.065901 | 0.070303 | 0.128 | 0.00099115 | -0.0053683 | -0.12222 | -0.0072034 | 0.064051 | 0.058467 | 0.0069854 | -0.011119 | 74.1943 | 74.4095 | 3.9139 | -48.7198 | 74.469 | -48.6237 | -48.7152 | -48.381 | 2.742 | -48.7656 | 74.3774 | 74.3088 | -48.7976 | -48.8159 | -0.027466 | -0.11902 | 0.13275 | 123.0057 | -0.1236 | -0.004578 | -0.14191 | -0.20142 | -0.21973 | 0.041198 | 0.21515 | -0.16937 | 0.050354 | -0.027466 | 123.0652 | 122.7905 | 52.5101 | -123.0515 | 122.9736 | 122.905 | 51.3382 | -123.1522
2334.0156 | 122.9874 | -48.3261 | 74.6201 | -0.19089 | 0.0087307 | 0.069532 | 0.069022 | 0.12928 | -0.0030677 | -0.0060093 | -0.10696 | -0.0069898 | 0.063837 | 0.055689 | 0.0063446 | -0.011119 | 74.3591 | 74.4873 | 4.4128 | -48.5962 | 74.6429 | -48.4268 | -48.5504 | -48.1339 | 3.0029 | -48.4772 | 74.6841 | 74.6017 | -48.5092 | -48.5687 | -0.10071 | -0.2243 | 0.022888 | 122.8134 | -0.27008 | -0.045776 | -0.26093 | -0.18311 | -0.24262 | 0.064087 | 0.19226 | -0.15106 | 0.091553 | -0.01831 | 122.9691 | 122.6852 | 52.739 | -123.1705 | 123.0103 | 122.9279 | 51.329 | -123.1888
2335.0156 | 123.0469 | -47.699 | 75.2335 | -0.19089 | 0.012362 | 0.066969 | 0.073081 | 0.13078 | -7.6852e-05 | -0.0064365 | -0.17563 | -0.0086988 | 0.064905 | 0.056971 | 0.0067718 | -0.0096238 | 75.0366 | 75.2014 | 4.4769 | -47.8638 | 75.3754 | -47.7127 | -47.8317 | -47.5021 | 2.9846 | -47.8043 | 75.3021 | 75.2289 | -47.8912 | -47.9279 | -0.013733 | -0.13275 | 0.14191 | 122.9004 | -0.1648 | -0.032044 | -0.19684 | -0.19226 | -0.22888 | 0.068665 | 0.19684 | -0.10529 | 0.1236 | -0.004577 | 123.0743 | 122.7356 | 52.1759 | -123.0652 | 123.0011 | 122.9279 | 50.6836 | -123.1613
2336.0156 | 123.0881 | -48.2986 | 74.5834 | -0.19852 | 0.01044 | 0.0706 | 0.070731 | 0.12928 | -0.0045631 | -0.0077183 | -0.038299 | -0.011262 | 0.062555 | 0.054835 | 0.0052764 | -0.012187 | 74.4553 | 74.6887 | 4.4266 | -48.436 | 74.6613 | -48.3719 | -48.4634 | -48.0835 | 2.9251 | -48.4817 | 74.6246 | 74.5239 | -48.4817 | -48.5458 | -0.073242 | -0.16479 | 0.07782 | 122.9874 | -0.13733 | 0.027466 | -0.12817 | -0.1831 | -0.24719 | 0.041199 | 0.21515 | -0.1831 | 0.064087 | -0.059509 | 122.9599 | 122.7539 | 52.7252 | -123.0469 | 122.9233 | 122.8226 | 51.2238 | -123.1293
2337.0156 | 123.0423 | -49.0448 | 73.8602 | -0.068817 | 0.016635 | 0.068678 | 0.075003 | 0.1295 | 0.0033411 | -0.0070773 | -0.023041 | -0.0082716 | 0.0664 | 0.058467 | 0.0082672 | -0.011974 | 73.8281 | 73.9334 | 4.303 | -49.1135 | 74.0982 | -48.9899 | -49.0906 | -48.8342 | 2.6459 | -49.2554 | 73.938 | 73.8464 | -49.2416 | -49.2874 | 0.054932 | -0.045776 | 0.23804 | 122.9782 | -0.068664 | -0.022888 | -0.032043 | -0.19684 | -0.24262 | 0.07782 | 0.21057 | -0.21057 | 0.032044 | -0.013732 | 123.143 | 122.8729 | 53.3478 | -122.9507 | 122.9828 | 122.8912 | 51.6907 | -123.1476
2338.0156 | 122.9965 | -48.8663 | 74.0845 | -0.19089 | 0.011081 | 0.068891 | 0.071585 | 0.12886 | -0.0037085 | -0.0083591 | -0.17563 | -0.0089124 | 0.063623 | 0.05633 | 0.0039948 | -0.010692 | 73.6496 | 73.8785 | 4.1931 | -49.1913 | 74.0204 | -49.054 | -49.1272 | -48.7152 | 2.7328 | -48.9807 | 74.1165 | 74.0433 | -49.0997 | -49.118 | -0.18768 | -0.26093 | -0.064087 | 122.7448 | -0.32501 | -0.064087 | -0.43488 | -0.23346 | -0.25177 | 0.032043 | 0.15106 | -0.11444 | 0.13733 | -0.041199 | 122.8867 | 122.5159 | 53.0594 | -123.2117 | 122.9828 | 122.9095 | 51.5991 | -123.2025
2339.0156 | 123.0743 | -47.8226 | 75.0732 | -0.168 | 0.015567 | 0.069959 | 0.070517 | 0.12736 | -0.0015723 | -0.0062229 | -0.17563 | -0.0089124 | 0.064051 | 0.057826 | 0.0069854 | -0.012187 | 74.7437 | 74.9313 | 4.5547 | -48.111 | 75.1236 | -48.0011 | -48.0789 | -47.5296 | 3.1769 | -47.6303 | 75.3021 | 75.2151 | -47.8775 | -47.9691 | -0.17853 | -0.25635 | 0.050354 | 122.7539 | -0.28839 | -0.032044 | -0.32959 | -0.054931 | -0.14648 | 0.22888 | 0.29297 | 0.19226 | 0.33874 | 0.14191 | 122.9462 | 122.5662 | 52.3773 | -123.1522 | 123.1247 | 123.0377 | 50.9995 | -123.0423
2340.125 | 123.0972 | -48.6008 | 74.3042 | -0.17563 | 0.010013 | 0.0706 | 0.071372 | 0.12971 | -0.0056311 | -0.0077183 | -0.11459 | -0.011476 | 0.061487 | 0.057612 | 0.006131 | -0.0096238 | 74.1211 | 74.3729 | 4.5319 | -48.7061 | 74.3866 | -48.6603 | -48.7473 | -48.3994 | 2.8336 | -48.7015 | 74.3271 | 74.2722 | -48.8113 | -48.848 | -0.059509 | -0.14648 | 0.082398 | 122.9736 | -0.10529 | 0.041198 | -0.1831 | -0.21057 | -0.24719 | 0.022888 | 0.20142 | -0.10071 | 0.14648 | -0.032043 | 122.9874 | 122.7219 | 53.1326 | -123.0515 | 122.9279 | 122.8729 | 51.4343 | -123.1522
2341.0156 | 123.0377 | -48.3994 | 74.5239 | -0.16037 | 0.013431 | 0.06825 | 0.073935 | 0.12886 | -0.00071785 | -0.0068637 | -0.168 | -0.0089124 | 0.064691 | 0.056971 | 0.0063446 | -0.012187 | 74.2996 | 74.4553 | 4.2297 | -48.6191 | 74.6292 | -48.468 | -48.5596 | -48.2254 | 2.7283 | -48.5504 | 74.6201 | 74.5056 | -48.6099 | -48.6511 | -0.068665 | -0.16022 | 0.10528 | 122.8546 | -0.21973 | -0.05951 | -0.2243 | -0.21057 | -0.25177 | 0.09613 | 0.17395 | -0.15106 | 0.10071 | -0.018311 | 123.0286 | 122.699 | 52.6291 | -123.0835 | 123.0194 | 122.905 | 51.1276 | -123.175
2342.0156 | 123.0972 | -48.9258 | 73.97 | -0.22141 | 0.011081 | 0.071027 | 0.068594 | 0.12928 | -0.0045631 | -0.0075047 | -0.10696 | -0.010194 | 0.061701 | 0.055689 | 0.0052764 | -0.011333 | 73.732 | 73.9563 | 4.097 | -49.1226 | 74.0067 | -49.0448 | -49.1364 | -48.7152 | 2.8656 | -48.9395 | 74.0616 | 73.9517 | -49.0952 | -49.1867 | -0.11902 | -0.21057 | 0.036621 | 122.8821 | -0.19684 | 0.013733 | -0.23804 | -0.16937 | -0.26093 | 0.091552 | 0.21057 | -0.013733 | 0.24719 | -0.018311 | 122.9324 | 122.6578 | 53.0228 | -123.1064 | 122.9874 | 122.8775 | 51.7914 | -123.1567
2343.0156 | 122.9919 | -48.848 | 74.1257 | -0.19089 | 0.011722 | 0.070173 | 0.072867 | 0.12843 | -0.0032813 | -0.0060093 | -0.091705 | -0.0086988 | 0.064905 | 0.05633 | 0.006131 | -0.011546 | 73.9288 | 74.0616 | 4.0192 | -49.0494 | 74.1989 | -48.8663 | -48.9853 | -48.7106 | 2.7374 | -49.1135 | 74.1257 | 74.0295 | -49.0585 | -49.0631 | -0.018311 | -0.13733 | 0.073243 | 122.9095 | -0.20142 | -0.064086 | -0.19684 | -0.21057 | -0.21515 | 0 | 0.13733 | -0.2655 | -0.050354 | -0.09613 | 123.0469 | 122.7768 | 52.8671 | -123.111 | 122.9736 | 122.8775 | 51.5854 | -123.1888
2344.0469 | 123.1155 | -48.2712 | 74.588 | 0.19058 | 0.014712 | 0.066969 | 0.07009 | 0.12907 | 0.0020593 | -0.0060093 | 0.23636 | -0.006349 | 0.065973 | 0.057185 | 0.0080536 | -0.013683 | 74.3958 | 74.5697 | 3.8177 | -48.5458 | 74.6567 | -48.3948 | -48.468 | -47.9965 | 2.8244 | -48.3673 | 74.6796 | 74.5743 | -48.4268 | -48.4909 | -0.1236 | -0.19684 | 0.068664 | 122.8409 | -0.27466 | -0.077819 | -0.19226 | -0.15564 | -0.21973 | 0.091552 | 0.27466 | -0.096131 | 0.1236 | -0.013733 | 122.9279 | 122.6669 | 52.0889 | -123.056 | 122.9507 | 122.8455 | 51.0956 | -123.0789
2345.0156 | 123.0331 | -49.5255 | 73.3932 | -0.22141 | 0.013858 | 0.069746 | 0.074576 | 0.12822 | 0.00035035 | -0.0049411 | -0.168 | -0.0089124 | 0.066187 | 0.057826 | 0.00549 | -0.010905 | 73.2651 | 73.3887 | 3.6392 | -49.6765 | 73.5764 | -49.5483 | -49.6445 | -49.292 | 2.449 | -49.6124 | 73.4985 | 73.4482 | -49.6765 | -49.7543 | -0.022888 | -0.11902 | 0.18311 | 122.9141 | -0.15106 | -0.032044 | -0.12817 | -0.15106 | -0.22888 | 0.10529 | 0.23346 | -0.086975 | 0.14191 | 0.054931 | 123.1018 | 122.7905 | 53.1647 | -123.0377 | 123.024 | 122.9736 | 51.9745 | -123.1476
2346.0156 | 123.0194 | -48.8663 | 74.0616 | -0.25955 | 0.0057401 | 0.069746 | 0.067313 | 0.12758 | -0.0030677 | -0.0057957 | -0.12222 | -0.0099806 | 0.063837 | 0.056544 | 0.006131 | -0.011333 | 73.8602 | 74.0707 | 3.9047 | -49.0128 | 74.1119 | -48.9166 | -49.0082 | -48.5733 | 2.9892 | -48.8113 | 74.1577 | 74.0524 | -49.0173 | -49.086 | -0.050354 | -0.14191 | 0.050354 | 122.937 | -0.14648 | -0.004577 | -0.20142 | -0.15106 | -0.21973 | 0.096131 | 0.29297 | 0.054932 | 0.27466 | -0.009155 | 122.9782 | 122.7264 | 52.771 | -123.0698 | 123.024 | 122.9187 | 51.8555 | -123.1476
2347.0156 | 123.0423 | -48.9304 | 73.9929 | -0.23666 | 0.0097989 | 0.071241 | 0.075003 | 0.12758 | 0.0022729 | -0.0038731 | -0.19089 | -0.0082716 | 0.065119 | 0.056971 | 0.008908 | -0.011974 | 73.7091 | 74.0799 | 3.6987 | -49.0906 | 74.2035 | -48.9304 | -49.0219 | -48.6282 | 2.6459 | -49.0402 | 74.2035 | 74.0616 | -49.0814 | -49.1272 | 0 | -0.091553 | 0.21057 | 123.0103 | -0.16022 | -0.068664 | -0.28381 | -0.15106 | -0.19684 | 0.21057 | 0.30212 | -0.10986 | 0.086975 | 0.068664 | 123.1338 | 122.6395 | 52.6291 | -123.0148 | 123.1338 | 122.9919 | 51.5762 | -123.1201
2348.0156 | 123.1201 | -48.1247 | 74.7345 | -0.26718 | 0.0055265 | 0.070387 | 0.072653 | 0.12822 | -0.0041357 | -0.0083591 | -0.099335 | -0.0095532 | 0.06106 | 0.053126 | 0.006131 | -0.010478 | 74.5651 | 74.7894 | 4.5136 | -48.3353 | 74.7986 | -48.23 | -48.3261 | -47.9507 | 3.2181 | -48.2666 | 74.7711 | 74.6887 | -48.3627 | -48.4131 | -0.10528 | -0.20142 | 0.064087 | 122.9141 | -0.21057 | -0.009155 | -0.16937 | -0.23804 | -0.28839 | 0.036621 | 0.17395 | -0.14191 | 0.14648 | -0.045776 | 122.9233 | 122.6898 | 52.6382 | -123.0606 | 122.8958 | 122.8134 | 51.3428 | -123.1476
2349.0156 | 123.0423 | -49.9054 | 72.995 | -0.21378 | 0.011935 | 0.071027 | 0.07244 | 0.12886 | -0.0015723 | -0.0051547 | -0.18326 | -0.0093396 | 0.061273 | 0.058039 | 0.0031402 | -0.011333 | 72.8485 | 73.0133 | 4.3488 | -50.0977 | 73.1644 | -49.9374 | -50.0153 | -49.5346 | 2.4307 | -49.9649 | 73.1689 | 73.0728 | -50.061 | -50.1251 | -0.032043 | -0.10986 | 0.16937 | 122.9187 | -0.19226 | -0.082397 | -0.14648 | -0.15564 | -0.21973 | 0.17395 | 0.37079 | -0.059509 | 0.16022 | 0.07782 | 123.0698 | 122.7539 | 54.2542 | -123.0103 | 123.0743 | 122.9782 | 52.3361 | -123.1201
2350.0156 | 123.1796 | -47.6852 | 75.1602 | -0.068817 | 0.0070217 | 0.072736 | 0.067099 | 0.12736 | -0.0058447 | -0.0098545 | 0.015106 | -0.010835 | 0.06106 | 0.055903 | 0.0031402 | -0.0094102 | 74.9954 | 75.2106 | 4.0604 | -47.9462 | 75.2197 | -47.8043 | -47.8867 | -47.2595 | 3.4515 | -47.6395 | 75.3387 | 75.2197 | -47.8088 | -47.905 | -0.11902 | -0.20142 | 0.05951 | 122.8958 | -0.26093 | -0.059509 | -0.16479 | -0.1236 | -0.21973 | 0.17853 | 0.42572 | 0.045777 | 0.2655 | 0.05951 | 122.905 | 122.6807 | 51.7456 | -123.0469 | 123.024 | 122.905 | 51.1368 | -123.0652
2351.0156 | 123.0789 | -48.1796 | 74.7162 | -0.20615 | 0.010867 | 0.068678 | 0.071372 | 0.12864 | -0.0015723 | -0.0068637 | -0.13748 | -0.011262 | 0.064478 | 0.055262 | 0.0069854 | -0.012187 | 74.6292 | 74.8398 | 4.4495 | -48.2849 | 74.8444 | -48.1842 | -48.3032 | -47.9233 | 3.2089 | -48.2758 | 74.7803 | 74.6841 | -48.3673 | -48.4222 | -0.004578 | -0.1236 | 0.12817 | 123.0194 | -0.10529 | 0.018311 | -0.086976 | -0.18768 | -0.24262 | 0.064086 | 0.25635 | -0.096131 | 0.14648 | -0.032044 | 123.024 | 122.8088 | 52.6291 | -123.0194 | 122.9599 | 122.8638 | 51.3885 | -123.1384
2352.0156 | 123.0835 | -48.6511 | 74.2676 | -0.17563 | 0.0085171 | 0.069746 | 0.068808 | 0.12886 | -0.0039221 | -0.0077183 | -0.12985 | -0.0093396 | 0.061701 | 0.055689 | 0.0059174 | -0.011546 | 73.9838 | 74.2538 | 4.4861 | -48.7839 | 74.3042 | -48.7106 | -48.8113 | -48.4314 | 2.9892 | -48.8159 | 74.2493 | 74.176 | -48.8617 | -48.8983 | -0.059509 | -0.16022 | 0.036621 | 122.905 | -0.13275 | 0.027465 | -0.28381 | -0.21057 | -0.24719 | -0.01831 | 0.21973 | -0.1648 | 0.082397 | -0.091553 | 122.9553 | 122.6349 | 53.1372 | -123.0789 | 122.9004 | 122.8271 | 51.6403 | -123.1659
2353.0156 | 123.024 | -49.0219 | 73.9197 | -0.24429 | 0.011508 | 0.069319 | 0.069876 | 0.1295 | 0.0012047 | -0.0079319 | -1.6786 | -0.0086988 | 0.06341 | 0.056758 | 0.0057038 | -0.012401 | 73.7778 | 73.938 | 4.4907 | -49.1226 | 74.1394 | -49.0128 | -49.1043 | -48.7244 | 3.1403 | -49.1226 | 74.0799 | 73.9563 | -49.1455 | -49.2325 | 0.009156 | -0.082397 | 0.21973 | 122.9599 | -0.10071 | -0.018311 | -0.14191 | -0.1236 | -0.21057 | 0.16022 | 0.29755 | -0.10071 | 0.10986 | 0.036621 | 123.1613 | 122.7997 | 53.5126 | -123.024 | 123.1018 | 122.9782 | 52.1622 | -123.1522
2354.0156 | 123.0927 | -48.6694 | 74.1943 | -1.0912 | 0.0091581 | 0.067396 | 0.066885 | 0.12779 | -0.0037085 | -0.0053683 | -0.076446 | -0.010194 | 0.061273 | 0.058253 | 0.0069854 | -0.011974 | 74.0479 | 74.35 | 4.6967 | -48.8297 | 74.2905 | -48.7289 | -48.8297 | -48.3856 | 3.4103 | -48.8113 | 74.2767 | 74.1806 | -48.88 | -48.9166 | -0.059509 | -0.16022 | 0.09613 | 123.0194 | -0.16022 | 0 | -0.14648 | -0.21057 | -0.24719 | 0.082397 | 0.28381 | -0.14191 | 0.10529 | -0.013733 | 122.9599 | 122.7173 | 53.3661 | -123.024 | 122.9462 | 122.85 | 52.0798 | -123.111
2355.0156 | 123.0057 | -48.2025 | 74.762 | -0.20615 | 0.012149 | 0.070173 | 0.072653 | 0.1295 | -0.00050425 | -0.0066501 | -0.21378 | -0.0078442 | 0.063837 | 0.057185 | 0.007199 | -0.012614 | 74.4873 | 74.6979 | 4.6509 | -48.3719 | 74.8215 | -48.2529 | -48.3353 | -48.0652 | 3.3279 | -48.4451 | 74.7528 | 74.6384 | -48.436 | -48.4726 | -0.050354 | -0.13275 | 0.059509 | 122.9004 | -0.16937 | -0.036621 | -0.27466 | -0.23346 | -0.27008 | -0.009155 | 0.13733 | -0.24261 | 0.027466 | -0.1236 | 123.024 | 122.6898 | 52.8534 | -123.0972 | 122.9553 | 122.8409 | 51.5305 | -123.2346
2356.0156 | 123.1567 | -48.2666 | 74.588 | -0.084076 | 0.0061673 | 0.071027 | 0.068594 | 0.12587 | -0.0045631 | -0.0072911 | 0.037995 | -0.012758 | 0.05871 | 0.05633 | 0.006131 | -0.010265 | 74.3637 | 74.6429 | 4.5273 | -48.436 | 74.6658 | -48.3353 | -48.4039 | -47.9736 | 3.3005 | -48.381 | 74.6567 | 74.5377 | -48.4589 | -48.5138 | -0.068664 | -0.13733 | 0.07782 | 122.9095 | -0.16937 | -0.032043 | -0.22431 | -0.19226 | -0.24719 | 0.068664 | 0.29297 | -0.11444 | 0.13275 | -0.050354 | 122.9324 | 122.6303 | 52.7939 | -122.9919 | 122.9233 | 122.8043 | 51.5671 | -123.1018
2357.0156 | 123.0835 | -48.23 | 74.5834 | -0.19089 | 0.010013 | 0.067396 | 0.069663 | 0.128 | -0.0026405 | -0.0062229 | -0.16037 | -0.009126 | 0.062555 | 0.055476 | 0.0059174 | -0.010478 | 74.5148 | 74.762 | 4.5959 | -48.3398 | 74.7574 | -48.2437 | -48.3398 | -48.0057 | 3.1815 | -48.2849 | 74.7299 | 74.588 | -48.4039 | -48.4451 | -0.013733 | -0.10986 | 0.17395 | 122.9919 | -0.10986 | 0 | -0.068664 | -0.17395 | -0.21515 | 0.14648 | 0.2243 | -0.054932 | 0.16022 | 0.004578 | 122.9874 | 122.7448 | 52.8259 | -122.9233 | 122.9599 | 122.818 | 51.4114 | -123.0286
2358.0156 | 123.2712 | -47.6166 | 75.2838 | -0.13748 | 0.0089443 | 0.069746 | 0.067526 | 0.12864 | -0.0026405 | -0.0049411 | -0.076446 | -0.010621 | 0.058924 | 0.056971 | 0.00549 | -0.012828 | 75.206 | 75.4715 | 4.6967 | -47.6807 | 75.4349 | -47.5937 | -47.7036 | -47.3511 | 3.3554 | -47.6212 | 75.3387 | 75.2426 | -47.8134 | -47.8592 | 0.022888 | -0.086975 | 0.15106 | 123.0881 | -0.064087 | 0.022888 | -0.077819 | -0.19684 | -0.24262 | 0.054932 | 0.2655 | -0.004578 | 0.23804 | -0.041198 | 123.0515 | 122.8226 | 52.3132 | -122.9874 | 122.9553 | 122.8592 | 50.972 | -123.143
2359.0156 | 122.9919 | -47.7036 | 75.2975 | -0.58762 | 0.013858 | 0.070387 | 0.07009 | 0.12864 | 0.00056395 | -0.0079319 | -0.19852 | -0.010194 | 0.064264 | 0.05868 | 0.0082672 | -0.012828 | 74.9176 | 75.0504 | 4.2068 | -48.0331 | 75.2197 | -47.8958 | -48.0103 | -47.6624 | 3.0258 | -47.9095 | 75.2426 | 75.1328 | -47.9553 | -47.9736 | -0.19226 | -0.3067 | -0.077819 | 122.7539 | -0.32959 | -0.022888 | -0.37994 | -0.25177 | -0.27008 | -0.054931 | 0.041198 | -0.20599 | 0.064087 | -0.16479 | 122.9233 | 122.6212 | 51.9104 | -123.3078 | 122.9462 | 122.8363 | 50.7294 | -123.2712
2360.0156 | 123.1201 | -47.7493 | 75.119 | -0.18326 | 0.0059537 | 0.069105 | 0.069449 | 0.1295 | -0.0034949 | -0.0087863 | 0.36606 | -0.0082716 | 0.061487 | 0.054621 | 0.0080536 | -0.011333 | 74.8901 | 75.1282 | 4.216 | -47.8088 | 75.1694 | -47.8958 | -48.0148 | -47.5021 | 3.2455 | -47.6852 | 75.1968 | 75.0412 | -47.9324 | -47.9965 | -0.14648 | -0.2655 | 0.050354 | 122.8775 | -0.059509 | 0.20599 | -0.22888 | -0.1831 | -0.24719 | 0.077819 | 0.24719 | 0.064087 | 0.31128 | -0.07782 | 122.9187 | 122.6395 | 51.9653 | -123.1339 | 122.9462 | 122.7905 | 50.9949 | -123.1155
2361.0156 | 123.024 | -47.4747 | 75.4623 | -0.22903 | 0.011294 | 0.068464 | 0.073935 | 0.12907 | -0.00071785 | -0.0064365 | -0.045929 | -0.010194 | 0.061701 | 0.058467 | 0.0080536 | -0.012187 | 75.2426 | 75.4257 | 4.5639 | -47.6715 | 75.5264 | -47.5479 | -47.6395 | -47.3602 | 3.4103 | -47.5845 | 75.499 | 75.3937 | -47.6669 | -47.6898 | -0.073243 | -0.16479 | 0.064087 | 122.9004 | -0.19684 | -0.032044 | -0.21973 | -0.19226 | -0.21515 | 0.036621 | 0.11444 | -0.10986 | 0.10529 | -0.068664 | 123.0011 | 122.7173 | 52.0386 | -123.1018 | 122.9736 | 122.8683 | 50.885 | -123.1522
2362.0156 | 123.1842 | -47.7631 | 75.1144 | -0.14511 | 0.0061673 | 0.070173 | 0.071372 | 0.12971 | -0.0043495 | -0.0087863 | -0.099335 | -0.009126 | 0.061487 | 0.056544 | 0.006131 | -0.010905 | 74.8901 | 75.1099 | 4.6509 | -48.0377 | 75.0824 | -47.9279 | -47.9965 | -47.58 | 3.4332 | -48.0194 | 75.1053 | 75.0183 | -47.9782 | -48.0377 | -0.16479 | -0.23346 | -0.032044 | 122.8729 | -0.27466 | -0.041199 | -0.2243 | -0.21515 | -0.27466 | -0.009155 | 0.18311 | -0.25635 | 0.018311 | -0.09613 | 122.8455 | 122.6532 | 52.4139 | -123.111 | 122.8683 | 122.7814 | 51.1963 | -123.1522
2363.0156 | 123.0743 | -48.4222 | 74.4553 | -0.22141 | 0.0078763 | 0.069319 | 0.070303 | 0.13014 | -0.00093145 | -0.0034457 | -0.16037 | -0.010408 | 0.060419 | 0.05633 | 0.008908 | -0.011119 | 74.2447 | 74.4232 | 4.5044 | -48.674 | 74.469 | -48.6099 | -48.6923 | -48.1659 | 3.6438 | -48.4909 | 74.5331 | 74.4324 | -48.6145 | -48.6832 | -0.18768 | -0.27008 | 0.013733 | 122.8455 | -0.25177 | 0.018311 | -0.21057 | -0.19226 | -0.26093 | 0.07782 | 0.25635 | -0.068665 | 0.19226 | -0.022888 | 122.8912 | 122.6669 | 52.9266 | -123.1476 | 122.9553 | 122.8546 | 52.066 | -123.1384
2364.0156 | 123.1155 | -48.5962 | 74.2996 | 0.015106 | 0.0072355 | 0.071241 | 0.069663 | 0.12864 | -0.0019995 | -0.0070773 | 0.030365 | -0.009126 | 0.060633 | 0.053767 | 0.00784 | -0.013469 | 74.2081 | 74.4324 | 4.3396 | -48.7793 | 74.469 | -48.6099 | -48.7381 | -48.3994 | 3.7308 | -48.6969 | 74.2767 | 74.1669 | -48.8068 | -48.8754 | -0.013733 | -0.14191 | 0.16937 | 123.0286 | -0.18311 | -0.041199 | -0.091553 | -0.21057 | -0.27924 | -0.022889 | 0.19684 | -0.10071 | 0.17853 | -0.13275 | 123.0652 | 122.8043 | 52.9358 | -123.0377 | 122.8729 | 122.7631 | 52.327 | -123.175
2365.0156 | 123.1064 | -47.5571 | 75.3387 | -0.18326 | 0.010226 | 0.070173 | 0.07009 | 0.12736 | -0.0030677 | -0.0064365 | -0.13748 | -0.011689 | 0.062769 | 0.057185 | 0.0084808 | -0.012401 | 74.9817 | 75.206 | 4.8706 | -47.9691 | 75.1648 | -47.8821 | -47.9645 | -47.3602 | 4.2938 | -47.6486 | 75.3204 | 75.2426 | -47.7631 | -47.7859 | -0.32501 | -0.40741 | -0.17395 | 122.7631 | -0.41199 | -0.004577 | -0.35706 | -0.20599 | -0.22888 | -0.01831 | 0.19684 | -0.091553 | 0.13733 | -0.09613 | 122.7219 | 122.5388 | 52.4277 | -123.3032 | 122.8775 | 122.7997 | 51.8509 | -123.1247
2366.0156 | 123.1613 | -47.8226 | 75.0275 | -0.0383 | 0.0061673 | 0.067823 | 0.069876 | 0.13057 | -0.00029045 | -0.0072911 | -0.099335 | -0.010408 | 0.058924 | 0.057398 | 0.0063446 | -0.012401 | 74.9405 | 75.1648 | 4.866 | -48.0194 | 75.0732 | -47.905 | -48.0103 | -47.493 | 4.2114 | -47.85 | 75.1602 | 75.032 | -47.9782 | -48.0331 | -0.082397 | -0.18768 | 0.045776 | 122.9874 | -0.19684 | -0.009155 | -0.086975 | -0.15564 | -0.21057 | 0.13275 | 0.32959 | -0.027466 | 0.1831 | 0.004577 | 122.8958 | 122.7631 | 52.6886 | -123.0377 | 122.9828 | 122.8546 | 52.034 | -123.0606
2367.0156 | 123.0606 | -49.0036 | 73.8647 | -0.20615 | 0.0083035 | 0.069105 | 0.068381 | 0.12971 | -0.00050425 | -0.0072911 | -0.16037 | -0.0095532 | 0.063837 | 0.055903 | 0.0063446 | -0.013255 | 73.8876 | 74.0845 | 4.454 | -49.1043 | 74.057 | -49.0082 | -49.0997 | -48.6786 | 3.9642 | -49.1226 | 74.0204 | 73.8785 | -49.1821 | -49.2279 | -0.004578 | -0.09613 | 0.19226 | 123.0881 | -0.10071 | -0.004578 | 0.022888 | -0.17853 | -0.2243 | 0.15564 | 0.32501 | -0.11902 | 0.10529 | 0.013733 | 123.0606 | 122.8912 | 53.4576 | -122.9645 | 123.024 | 122.8821 | 52.9678 | -123.0927
2368.0156 | 123.1522 | -48.2208 | 74.6338 | -0.053558 | 0.0068081 | 0.0706 | 0.069663 | 0.12715 | -0.0019995 | -0.0089999 | -0.00015237 | -0.011903 | 0.059564 | 0.055689 | 0.00784 | -0.012187 | 74.4598 | 74.7025 | 4.866 | -48.436 | 74.6796 | -48.3719 | -48.4497 | -48.0148 | 4.1382 | -48.3994 | 74.6292 | 74.5514 | -48.4589 | -48.4863 | -0.15106 | -0.22888 | 0.045776 | 122.9233 | -0.21515 | 0.013733 | -0.17395 | -0.23804 | -0.2655 | -0.004578 | 0.20599 | -0.17853 | 0.086975 | -0.082397 | 122.9004 | 122.6807 | 53.0869 | -123.0835 | 122.85 | 122.7722 | 52.359 | -123.1201
2369.0156 | 123.1293 | -49.3607 | 73.4985 | -0.61813 | 0.010867 | 0.069105 | 0.072226 | 0.12907 | 0.00035035 | -0.0062229 | -0.12222 | -0.011049 | 0.061487 | 0.055476 | 0.0069854 | -0.01176 | 73.4894 | 73.732 | 4.3396 | -49.5209 | 73.6588 | -49.4156 | -49.498 | -49.0723 | 3.9871 | -49.5621 | 73.6038 | 73.4619 | -49.5621 | -49.6262 | -0.054931 | -0.13733 | 0.16022 | 123.0927 | -0.16022 | -0.022888 | -0.009155 | -0.20142 | -0.2655 | 0.10529 | 0.28839 | -0.20142 | 0.064087 | -0.036621 | 123.0194 | 122.85 | 53.7003 | -122.9965 | 122.9645 | 122.8226 | 53.3478 | -123.1247
2370.0156 | 123.0835 | -48.6008 | 74.2493 | 0.030365 | 0.0078763 | 0.070814 | 0.068594 | 0.12629 | -0.00093145 | -0.0070773 | 0.10666 | -0.011689 | 0.062342 | 0.055903 | 0.0065582 | -0.011546 | 74.1348 | 74.3546 | 4.0787 | -48.7564 | 74.3912 | -48.6374 | -48.7152 | -48.2346 | 4.0924 | -48.6099 | 74.4186 | 74.2813 | -48.761 | -48.8068 | -0.036621 | -0.11444 | 0.14191 | 122.9553 | -0.15564 | -0.041199 | -0.11444 | -0.16022 | -0.20599 | 0.16937 | 0.36621 | -0.009155 | 0.19684 | 0.032043 | 122.9919 | 122.7356 | 52.6794 | -122.9645 | 123.0194 | 122.8821 | 52.6932 | -123.056
2371.0156 | 123.1522 | -48.9578 | 73.8556 | -0.053558 | 0.0070217 | 0.068464 | 0.069663 | 0.13121 | -0.0015723 | -0.0055821 | 0.0074766 | -0.012117 | 0.06106 | 0.05633 | 0.0059174 | -0.013469 | 73.764 | 73.9792 | 3.6301 | -49.1959 | 73.9792 | -49.0448 | -49.1455 | -48.6649 | 4.01 | -48.999 | 73.9883 | 73.8693 | -49.1409 | -49.1959 | -0.086975 | -0.18768 | 0.1236 | 122.937 | -0.23804 | -0.050354 | -0.091553 | -0.1831 | -0.23804 | 0.13275 | 0.29297 | -0.041198 | 0.19684 | 0.013733 | 122.937 | 122.7219 | 52.5879 | -123.0011 | 122.9462 | 122.8271 | 52.9678 | -123.0515
2372.0156 | 123.1018 | -49.1043 | 73.7137 | 0.076141 | 0.0061673 | 0.071668 | 0.072226 | 0.12886 | -0.00071785 | -0.0072911 | 0.10666 | -0.010835 | 0.062555 | 0.05868 | 0.0076264 | -0.010478 | 73.3978 | 73.7091 | 3.7537 | -49.411 | 73.7549 | -49.2874 | -49.3515 | -48.8342 | 5.3833 | -49.0677 | 73.8739 | 73.7686 | -49.2462 | -49.324 | -0.18311 | -0.24719 | 0.041199 | 122.8134 | -0.3067 | -0.05951 | -0.31586 | -0.14191 | -0.21973 | 0.16022 | 0.27008 | 0.036621 | 0.25635 | 0.054932 | 122.8592 | 122.5021 | 52.858 | -123.0652 | 122.9782 | 122.8729 | 54.4876 | -123.0377
2373.0156 | 123.1567 | -48.5092 | 74.35 | -0.17563 | 0.0085171 | 0.069319 | 0.071585 | 0.12608 | -0.00093145 | -0.0055821 | 0.64835 | -0.010194 | 0.06106 | 0.058253 | 0.0069854 | -0.014323 | 74.057 | 74.588 | 4.3488 | -48.8388 | 74.2676 | -48.8068 | -48.8983 | -48.2986 | 5.6305 | -48.5962 | 74.3683 | 74.2401 | -48.7473 | -48.7473 | -0.29755 | -0.3891 | -0.082398 | 123.0972 | -0.32959 | 0.059509 | -0.29297 | -0.23804 | -0.23804 | 0.01831 | 0.21057 | -0.086975 | 0.15106 | -0.10986 | 122.7768 | 122.5662 | 52.858 | -123.2483 | 122.8775 | 122.7493 | 54.1397 | -123.0972
2374.0156 | 123.1247 | -49.0677 | 73.7686 | 0.21347 | 0.0055265 | 0.069319 | 0.069663 | 0.12864 | -0.0022131 | -0.0051547 | 0.076141 | -0.010408 | 0.061273 | 0.055689 | 0.007199 | -0.011974 | 73.5672 | 73.7686 | 4.1931 | -49.3057 | 73.851 | -49.205 | -49.3011 | -48.8754 | 4.0649 | -49.2233 | 73.8464 | 73.7228 | -49.3149 | -49.3423 | -0.13733 | -0.23346 | 0.082397 | 122.8363 | -0.23804 | -0.004578 | -0.20142 | -0.24719 | -0.27466 | 0.07782 | 0.19226 | -0.15564 | 0.11902 | -0.045777 | 122.9187 | 122.6349 | 53.2608 | -123.0698 | 122.9141 | 122.7905 | 53.1326 | -123.111
2375.0156 | 123.1384 | -48.4177 | 74.4644 | -0.076447 | 0.0070217 | 0.070173 | 0.067954 | 0.12928 | -0.00029045 | -0.0036595 | 0.045624 | -0.011903 | 0.062555 | 0.053767 | 0.006131 | -0.010692 | 74.2996 | 74.4965 | 4.6051 | -48.6328 | 74.501 | -48.5321 | -48.642 | -48.1293 | 5.7404 | -48.6786 | 74.4507 | 74.2996 | -48.7015 | -48.7152 | -0.11444 | -0.2243 | 0.036621 | 122.9141 | -0.21515 | 0.009156 | -0.16479 | -0.28381 | -0.29755 | -0.013733 | 0.28839 | -0.26093 | 0.036621 | -0.16479 | 122.9187 | 122.7173 | 53.0228 | -123.1064 | 122.8683 | 122.7173 | 54.158 | -123.1796
2376.0156 | 123.0698 | -49.9603 | 72.8714 | 0.053253 | 0.0070217 | 0.069319 | 0.069235 | 0.12693 | 0.0014185 | -0.0064365 | 0.12192 | -0.010194 | 0.06106 | 0.056758 | 0.0052764 | -0.01176 | 72.8394 | 73.0179 | 4.0237 | -50.1205 | 73.1049 | -49.9878 | -50.0565 | -49.704 | 6.546 | -50.0153 | 73.0408 | 72.9263 | -50.1114 | -50.1755 | -0.027466 | -0.096131 | 0.23346 | 122.9782 | -0.16022 | -0.064086 | -0.032044 | -0.15106 | -0.21515 | 0.16937 | 0.25635 | -0.054932 | 0.16022 | 0.054932 | 123.0652 | 122.7997 | 53.9841 | -122.9279 | 123.0011 | 122.8867 | 56.5063 | -123.0469
2377.0156 | 123.111 | -47.6303 | 75.2335 | -1.6252 | 0.0089443 | 0.068464 | 0.069235 | 0.12928 | -0.00050425 | -0.0075047 | 0.068512 | -0.0093396 | 0.059564 | 0.056544 | 0.0080536 | -0.011974 | 74.8123 | 75.032 | 4.6646 | -47.9599 | 75.1785 | -47.8592 | -47.937 | -47.4197 | 7.7271 | -47.6898 | 75.3296 | 75.1831 | -47.8363 | -47.8683 | -0.22888 | -0.3067 | -0.054931 | 122.6624 | -0.32959 | -0.022888 | -0.42114 | -0.20599 | -0.23804 | 0.096131 | 0.21057 | -0.059509 | 0.17853 | -0.050354 | 122.8088 | 122.4426 | 52.2949 | -123.1705 | 122.9599 | 122.8134 | 55.3574 | -123.1018
2378.0156 | 123.111 | -49.0448 | 73.764 | 0.25925 | 0.011722 | 0.068891 | 0.068594 | 0.12886 | 0.0027001 | -0.0053683 | 0.15244 | -0.009126 | 0.062982 | 0.058253 | 0.0097626 | -0.014537 | 73.6267 | 73.7778 | 4.2297 | -49.3378 | 73.7869 | -49.2096 | -49.2966 | -48.8205 | 7.2922 | -49.173 | 73.8464 | 73.7412 | -49.2874 | -49.3423 | -0.16479 | -0.25177 | 0.022888 | 122.8226 | -0.29297 | -0.041199 | -0.13733 | -0.24262 | -0.29755 | 0.082398 | 0.2243 | -0.12817 | 0.16937 | -0.022888 | 122.8317 | 122.6715 | 53.2745 | -123.0606 | 122.8912 | 122.786 | 56.337 | -123.1064
2379.0156 | 123.1613 | -48.9853 | 73.8556 | -0.076447 | 0.0050991 | 0.070387 | 0.067954 | 0.12993 | -0.0030677 | -0.0051547 | -0.038299 | -0.010835 | 0.062555 | 0.057398 | 0.0063446 | -0.01176 | 73.764 | 73.9563 | 4.3671 | -49.173 | 73.9609 | -49.0768 | -49.1776 | -48.7473 | 7.1915 | -49.1135 | 73.9151 | 73.8098 | -49.2004 | -49.2554 | -0.091552 | -0.19226 | 0.10528 | 122.9416 | -0.18768 | 0.004577 | -0.091553 | -0.21515 | -0.27008 | 0.059509 | 0.23804 | -0.12817 | 0.14191 | -0.045777 | 122.9462 | 122.7493 | 53.3524 | -123.0331 | 122.9004 | 122.7951 | 56.1768 | -123.111
2380.0156 | 123.0972 | -48.9395 | 73.9334 | 0.12955 | 0.010867 | 0.069959 | 0.071799 | 0.12758 | 0.0018457 | -0.0083591 | 0.20584 | -0.0086988 | 0.061273 | 0.054621 | 0.0099762 | -0.0096238 | 73.9838 | 74.1348 | 4.2252 | -49.0036 | 74.176 | -48.8388 | -48.9304 | -48.6923 | 6.9763 | -49.1272 | 74.0662 | 73.9288 | -49.086 | -49.1547 | 0.10071 | 0.009155 | 0.24261 | 123.0743 | -0.064087 | -0.073242 | 0.050354 | -0.14648 | -0.21515 | 0.13275 | 0.24719 | -0.18768 | 0.027466 | -0.004578 | 123.1155 | 122.9233 | 53.1647 | -122.8638 | 123.0057 | 122.8683 | 55.9158 | -123.0881
2381.0156 | 123.1247 | -49.1089 | 73.7869 | -0.0077822 | 0.0085171 | 0.068891 | 0.069022 | 0.12971 | -0.0015723 | -0.0072911 | 0.053253 | -0.011049 | 0.059992 | 0.057185 | 0.0067718 | -0.013683 | 73.5672 | 73.8281 | 3.8086 | -49.2279 | 73.9243 | -49.1501 | -49.2096 | -48.8846 | 6.8893 | -49.3652 | 73.8556 | 73.6954 | -49.3103 | -49.3698 | -0.041198 | -0.10071 | 0.13733 | 122.937 | -0.11902 | -0.01831 | -0.21973 | -0.20142 | -0.26093 | 0.068665 | 0.2243 | -0.25635 | 0.004578 | -0.091552 | 123.0331 | 122.6761 | 52.9175 | -122.9965 | 122.9645 | 122.8043 | 55.9982 | -123.1567
2382.0156 | 123.1155 | -48.3215 | 74.4965 | 0.16769 | 0.010653 | 0.069319 | 0.070517 | 0.12758 | -0.00071785 | -0.0040867 | 0.16769 | -0.0089124 | 0.060846 | 0.055049 | 0.01019 | -0.013683 | 74.3912 | 74.5102 | 4.1107 | -48.5504 | 74.556 | -48.4406 | -48.5504 | -48.0606 | 7.5211 | -48.3627 | 74.6109 | 74.5056 | -48.5092 | -48.555 | -0.11902 | -0.22888 | 0.059509 | 122.8317 | -0.22888 | 0 | -0.10529 | -0.18768 | -0.23346 | 0.11444 | 0.26093 | -0.041199 | 0.19226 | 0.009155 | 122.8775 | 122.7127 | 52.4323 | -123.0469 | 122.9324 | 122.8271 | 55.8426 | -123.0515
2383.0156 | 123.0652 | -48.0972 | 74.762 | 0.068512 | 0.0061673 | 0.069532 | 0.068808 | 0.12736 | -0.00050425 | -0.0070773 | 0.083771 | -0.0078442 | 0.061701 | 0.054408 | 0.0057038 | -0.012187 | 74.588 | 74.7757 | 4.1199 | -48.3215 | 74.8901 | -48.1796 | -48.2666 | -47.8271 | 7.8186 | -48.0881 | 74.8856 | 74.7711 | -48.2895 | -48.3261 | -0.082397 | -0.16937 | 0.12817 | 122.8729 | -0.2243 | -0.054931 | -0.17395 | -0.19226 | -0.22888 | 0.1236 | 0.27008 | 0.009155 | 0.23804 | 0.009155 | 122.9874 | 122.6852 | 52.2171 | -123.0286 | 122.9828 | 122.8683 | 55.9158 | -123.0881
2384.0156 | 123.1338 | -48.5962 | 74.2538 | 0.18295 | 0.013431 | 0.06825 | 0.070944 | 0.12971 | 0.0052637 | -0.0034457 | 0.26688 | -0.0093396 | 0.061487 | 0.054621 | 0.0080536 | -0.012828 | 74.1577 | 74.263 | 4.0833 | -48.8205 | 74.3362 | -48.6786 | -48.7747 | -48.2941 | 7.4661 | -48.7106 | 74.3225 | 74.2218 | -48.793 | -48.8434 | -0.082398 | -0.17853 | 0.082398 | 122.8592 | -0.22431 | -0.045777 | -0.09613 | -0.19684 | -0.24719 | 0.068665 | 0.30212 | -0.11444 | 0.13275 | -0.032043 | 122.9324 | 122.7539 | 52.6794 | -123.0286 | 122.9187 | 122.818 | 56.0623 | -123.0972
2385.0156 | 123.1338 | -48.2483 | 74.6155 | 0.17532 | 0.01044 | 0.067396 | 0.070303 | 0.12693 | 0.00099115 | -0.0051547 | 0.19821 | -0.009126 | 0.060419 | 0.056117 | 0.00784 | -0.01176 | 74.0295 | 74.2081 | 4.4998 | -48.8983 | 74.2218 | -48.7793 | -48.8525 | -48.2574 | 7.8552 | -48.4772 | 74.4095 | 74.3729 | -48.6008 | -48.555 | -0.53101 | -0.60425 | -0.39368 | 122.4564 | -0.65002 | -0.045776 | -0.58594 | -0.35248 | -0.3067 | -0.20599 | -0.009155 | -0.22888 | 0.07782 | -0.24261 | 122.4701 | 122.2778 | 52.7481 | -123.468 | 122.6578 | 122.6212 | 56.1035 | -123.1705
2386.0156 | 123.1064 | -47.8271 | 75.0229 | 1.7317 | 0.017062 | 0.069532 | 0.072653 | 0.12822 | 0.00035035 | -0.0043003 | 0.16006 | -0.010408 | 0.063837 | 0.056117 | 0.008908 | -0.014323 | 75.0778 | 75.1968 | 4.6188 | -48.0194 | 75.1831 | -47.8638 | -47.9416 | -47.6074 | 5.7587 | -47.9919 | 75.0687 | 74.9634 | -48.056 | -48.0743 | -0.036622 | -0.11444 | 0.16022 | 123.024 | -0.19226 | -0.07782 | 0.054932 | -0.22888 | -0.24719 | 0.045777 | 0.21973 | -0.16479 | 0.082398 | -0.059509 | 123.0103 | 122.905 | 52.446 | -122.9645 | 122.8958 | 122.7905 | 53.5858 | -123.0972
2387.0156 | 123.1247 | -47.5204 | 75.3387 | 1.2434 | 0.011081 | 0.071027 | 0.072226 | 0.12971 | -0.0015723 | -0.0057957 | -0.12222 | -0.0093396 | 0.06106 | 0.056544 | 0.00549 | -0.011333 | 75.2701 | 75.4303 | 4.6463 | -47.6761 | 75.444 | -47.5616 | -47.6807 | -47.2321 | 7.5668 | -47.5067 | 75.4623 | 75.3662 | -47.6715 | -47.7081 | -0.041199 | -0.16022 | 0.10529 | 122.9507 | -0.15564 | 0.004578 | -0.068664 | -0.15106 | -0.18768 | 0.1236 | 0.28839 | 0.013733 | 0.20142 | 0.027466 | 122.9645 | 122.7905 | 52.1667 | -123.0194 | 122.9828 | 122.8867 | 55.0873 | -123.0469
2388.0156 | 123.0835 | -47.1405 | 75.6912 | 0.51865 | 0.013858 | 0.070387 | 0.068381 | 0.12886 | 0.0016321 | -0.0040867 | 0.20584 | -0.009126 | 0.06106 | 0.054621 | 0.010403 | -0.013683 | 75.8011 | 75.943 | 4.8203 | -47.1588 | 75.9842 | -47.0627 | -47.1588 | -46.8018 | 7.4524 | -47.2687 | 75.8789 | 75.7462 | -47.3099 | -47.3602 | 0.07782 | -0.01831 | 0.29297 | 123.0835 | -0.01831 | 0 | 0.10986 | -0.16937 | -0.21973 | 0.18768 | 0.33875 | -0.12817 | 0.091552 | 0.054932 | 123.1247 | 122.9416 | 51.9608 | -122.85 | 123.0194 | 122.8867 | 54.5929 | -123.0515
2389.0156 | 123.1064 | -47.319 | 75.5264 | 0.12955 | 0.0095853 | 0.069105 | 0.069235 | 0.12864 | -0.0019995 | -0.0043003 | 0.18295 | -0.0095532 | 0.06341 | 0.056544 | 0.0086944 | -0.010905 | 75.4349 | 75.618 | 4.8157 | -47.4701 | 75.6638 | -47.3511 | -47.4701 | -47.081 | 6.9122 | -47.406 | 75.6134 | 75.5264 | -47.5067 | -47.5662 | -0.032043 | -0.15106 | 0.13733 | 122.937 | -0.15106 | 0 | -0.091553 | -0.18768 | -0.24719 | 0.086975 | 0.23804 | -0.086975 | 0.16022 | 0 | 122.9828 | 122.7539 | 52.1347 | -122.9965 | 122.9324 | 122.8455 | 54.2313 | -123.0927
2390.0156 | 123.1201 | -47.8043 | 75.0458 | 0.18295 | 0.011722 | 0.06761 | 0.07009 | 0.12672 | 0.0024865 | -0.0053683 | 0.19821 | -0.0097668 | 0.062555 | 0.056117 | 0.0093354 | -0.0096238 | 75.2289 | 75.325 | 4.7791 | -47.7722 | 75.4532 | -47.6349 | -47.7036 | -47.4564 | 5.1544 | -47.9004 | 75.2747 | 75.1328 | -47.9507 | -47.9736 | 0.16937 | 0.10071 | 0.40741 | 123.1293 | 0.032043 | -0.068665 | 0.18311 | -0.14648 | -0.16937 | 0.22888 | 0.3479 | -0.096131 | 0.073242 | 0.086975 | 123.2574 | 123.0331 | 52.5833 | -122.7493 | 123.0789 | 122.937 | 52.9587 | -123.0194
2391.0156 | 123.1064 | -47.1542 | 75.6729 | 0.19058 | 0.013003 | 0.066969 | 0.069449 | 0.12779 | 0.0018457 | -0.0049411 | 0.19058 | -0.0093396 | 0.063837 | 0.054194 | 0.011472 | -0.011546 | 75.6042 | 75.7462 | 4.9805 | -47.3511 | 75.7782 | -47.2549 | -47.319 | -46.8796 | 5.0491 | -47.168 | 75.7782 | 75.6729 | -47.3328 | -47.3602 | -0.10071 | -0.1648 | 0.10529 | 122.9004 | -0.19684 | -0.032043 | -0.068665 | -0.17853 | -0.20599 | 0.10529 | 0.27466 | -0.013733 | 0.19226 | 0 | 122.9324 | 122.7585 | 52.1347 | -122.9919 | 122.9324 | 122.8271 | 52.2034 | -123.0331
2392.0156 | 122.9874 | -47.7219 | 75.2335 | 0.13718 | 0.01578 | 0.067182 | 0.072012 | 0.13057 | 0.0031273 | -0.0034457 | 2.4107 | -0.0086988 | 0.06106 | 0.056758 | 0.011685 | -0.014323 | 75.0137 | 75.1144 | 4.8569 | -47.8867 | 75.3708 | -47.7264 | -47.8043 | -47.6395 | 4.6738 | -48.0515 | 75.2975 | 75.1602 | -47.9462 | -47.9828 | -0.004577 | -0.082397 | 0.13733 | 122.8363 | -0.16479 | -0.082398 | -0.21973 | -0.2243 | -0.26093 | 0.064087 | 0.082398 | -0.32959 | -0.068665 | -0.073242 | 123.0927 | 122.7356 | 52.5787 | -123.0377 | 123.0194 | 122.8821 | 52.3956 | -123.2162
2393.0156 | 123.1247 | -48.8892 | 73.8693 | 0.16006 | 0.011081 | 0.069959 | 0.06774 | 0.12928 | -0.0030677 | -0.0049411 | 0.21347 | -0.0084852 | 0.060633 | 0.05633 | 0.0067718 | -0.0096238 | 74.0799 | 74.2447 | 4.6417 | -48.8892 | 74.2493 | -48.7885 | -48.8937 | -48.5596 | 4.1565 | -49.086 | 74.0753 | 73.9746 | -49.054 | -49.118 | 0.10071 | -0.004578 | 0.37994 | 123.1338 | 0 | 0.004578 | 0.21057 | -0.1648 | -0.22888 | 0.20599 | 0.32959 | -0.19684 | 0.032043 | 0.10528 | 123.1384 | 122.9691 | 53.5309 | -122.7631 | 122.9645 | 122.8638 | 53.0457 | -122.9874
2394.0156 | 123.0698 | -46.9986 | 75.8926 | 0.18295 | 0.014285 | 0.068037 | 0.074149 | 0.12843 | 0.0014185 | -0.0051547 | 0.16769 | -0.0084852 | 0.064905 | 0.055049 | 0.0093354 | -0.013042 | 75.6775 | 75.7507 | 4.7882 | -47.319 | 75.9384 | -47.1405 | -47.2321 | -46.8933 | 4.422 | -47.0261 | 75.9338 | 75.8514 | -47.1909 | -47.2 | -0.14191 | -0.23346 | 0.045777 | 122.7493 | -0.32044 | -0.086975 | -0.21515 | -0.19226 | -0.20142 | 0.041199 | 0.10529 | -0.027466 | 0.17395 | -0.041199 | 122.937 | 122.6761 | 51.7868 | -123.1247 | 122.9324 | 122.85 | 51.4206 | -123.0927
2395.0156 | 123.143 | -47.3602 | 75.4532 | -0.41214 | 0.011722 | 0.068891 | 0.067526 | 0.13228 | -0.0037085 | -0.0040867 | 0.26688 | -0.010194 | 0.061914 | 0.056971 | 0.0093354 | -0.01176 | 75.3799 | 75.5402 | 4.6371 | -47.6074 | 75.5219 | -47.4838 | -47.6028 | -47.0764 | 4.216 | -47.4289 | 75.5676 | 75.4715 | -47.5525 | -47.6303 | -0.1236 | -0.24262 | 0.068665 | 122.9004 | -0.24719 | -0.004578 | -0.073242 | -0.19226 | -0.27008 | 0.11444 | 0.28381 | -0.068665 | 0.20142 | 0.018311 | 122.8821 | 122.7402 | 51.9974 | -123.056 | 122.9279 | 122.8317 | 51.5762 | -123.0835
2396.0156 | 123.0743 | -48.1339 | 74.7391 | 0.13718 | 0.016635 | 0.068037 | 0.070517 | 0.1295 | 0.0020593 | -0.0051547 | 0.21347 | -0.0069898 | 0.063837 | 0.056758 | 0.0086944 | -0.012828 | 74.4781 | 74.556 | 4.4403 | -48.4589 | 74.794 | -48.3215 | -48.4131 | -48.0057 | 3.8544 | -48.2803 | 74.8077 | 74.7391 | -48.3353 | -48.3673 | -0.18768 | -0.27924 | 0.054931 | 122.6898 | -0.32501 | -0.045776 | -0.26093 | -0.20142 | -0.23346 | 0.068664 | 0.12817 | -0.14648 | 0.086976 | 0 | 122.9279 | 122.612 | 52.5742 | -123.1522 | 122.9416 | 122.8729 | 51.9882 | -123.1064
2397.0156 | 123.111 | -47.5525 | 75.2884 | 0.15244 | 0.011294 | 0.070387 | 0.071372 | 0.12928 | -0.0013587 | -0.0038731 | 2.1056 | -0.0093396 | 0.060633 | 0.058253 | 0.0099762 | -0.010905 | 75.3525 | 75.4669 | 5.0537 | -47.6898 | 75.4715 | -47.5388 | -47.6395 | -47.438 | 4.1702 | -47.6074 | 75.3525 | 75.293 | -47.731 | -47.7768 | 0.013733 | -0.086975 | 0.18311 | 123.0194 | -0.13733 | -0.050354 | 0.064087 | -0.17853 | -0.2243 | 0.064087 | 0.11444 | -0.054932 | 0.16937 | 0.004578 | 123.024 | 122.905 | 52.6062 | -122.9279 | 122.905 | 122.8455 | 51.7227 | -123.0652
2398.0156 | 123.1155 | -47.3602 | 75.5264 | -0.00015269 | 0.01813 | 0.068891 | 0.07244 | 0.12736 | 0.0014185 | -0.0036595 | 0.0914 | -0.0052808 | 0.065973 | 0.056117 | 0.010831 | -0.012401 | 75.2838 | 75.3571 | 4.8706 | -47.6761 | 75.6317 | -47.5159 | -47.6257 | -47.3465 | 4.1061 | -47.6669 | 75.5356 | 75.4715 | -47.6166 | -47.6395 | -0.15564 | -0.2655 | 0.10529 | 122.7173 | -0.31586 | -0.050354 | -0.24262 | -0.25635 | -0.27924 | 0.009155 | 0.013732 | -0.3067 | -0.027466 | -0.054931 | 122.9919 | 122.644 | 52.2308 | -123.1522 | 122.8958 | 122.8317 | 51.4664 | -123.1659
2399.0156 | 123.0789 | -47.4976 | 75.3891 | 0.17532 | 0.014499 | 0.067396 | 0.07244 | 0.13057 | -7.6852e-05 | -0.0053683 | 0.19058 | -0.0078442 | 0.063837 | 0.05633 | 0.011685 | -0.01176 | 75.0458 | 75.206 | 4.5044 | -47.818 | 75.3754 | -47.6852 | -47.7539 | -47.2961 | 4.3442 | -47.4518 | 75.4532 | 75.3937 | -47.6944 | -47.7539 | -0.18768 | -0.25635 | -0.013733 | 122.7036 | -0.32043 | -0.064087 | -0.34332 | -0.19684 | -0.25635 | 0.064087 | 0.20142 | 0.045777 | 0.30212 | 0.004578 | 122.8729 | 122.5433 | 52.002 | -123.143 | 122.9507 | 122.8912 | 51.8417 | -123.143
2400.0156 | 122.9965 | -47.4564 | 75.4944 | 0.13718 | 0.017062 | 0.068464 | 0.071799 | 0.12736 | 0.0031273 | -0.0060093 | 0.44235 | -0.0084852 | 0.064051 | 0.055903 | 0.008908 | -0.011974 | 75.2838 | 75.3799 | 4.3121 | -47.5021 | 75.6317 | -47.493 | -47.5937 | -47.3373 | 4.4266 | -47.5983 | 75.5447 | 75.4898 | -47.6624 | -47.7081 | -0.036621 | -0.13733 | 0.13733 | 122.8363 | -0.045776 | 0.091553 | -0.21057 | -0.20599 | -0.25177 | 0.050354 | 0.11902 | -0.14191 | 0.10986 | -0.004578 | 123.0881 | 122.7402 | 51.7685 | -123.0881 | 123.0011 | 122.9462 | 51.8829 | -123.2025
2401.0156 | 123.143 | -47.0718 | 75.8057 | 0.16769 | 0.015994 | 0.068464 | 0.071799 | 0.12886 | -0.00050425 | -0.0055821 | 0.21347 | -0.0097668 | 0.062342 | 0.055689 | 0.008908 | -0.010478 | 75.6409 | 75.7736 | 4.9622 | -47.3007 | 75.8835 | -47.1817 | -47.2549 | -46.8567 | 4.8889 | -47.1268 | 75.9018 | 75.824 | -47.2549 | -47.2961 | -0.10986 | -0.18311 | 0.07782 | 122.8455 | -0.22888 | -0.045776 | -0.16479 | -0.18311 | -0.22431 | 0.09613 | 0.21515 | -0.054932 | 0.16937 | 0.018311 | 122.9553 | 122.7127 | 52.034 | -123.0606 | 122.9736 | 122.8958 | 51.9608 | -123.1018
2402.0156 | 122.9507 | -47.3053 | 75.6088 | -0.023041 | 0.016208 | 0.069532 | 0.071372 | 0.12864 | 0.0033411 | -0.0045139 | 0.12192 | -0.008058 | 0.062982 | 0.056758 | 0.0069854 | -0.011333 | 75.4898 | 75.5722 | 4.9255 | -47.4152 | 75.8514 | -47.2549 | -47.3694 | -47.1863 | 6.6605 | -47.5296 | 75.7416 | 75.6454 | -47.5067 | -47.5662 | 0.050354 | -0.064087 | 0.24261 | 122.8775 | -0.10986 | -0.045776 | -0.11902 | -0.20142 | -0.26093 | 0.13275 | 0.11902 | -0.2243 | 0.036621 | 0.036621 | 123.1567 | 122.7951 | 52.2308 | -122.9782 | 123.0469 | 122.9507 | 53.9658 | -123.175
2403.0156 | 123.1384 | -46.7926 | 76.0529 | 0.19821 | 0.014926 | 0.068037 | 0.072012 | 0.128 | 0.00056395 | -0.0043003 | 0.21347 | -0.0084852 | 0.062769 | 0.057826 | 0.007199 | -0.011974 | 76.0208 | 76.1215 | 5.0308 | -46.907 | 76.2955 | -46.7239 | -46.8613 | -46.4905 | 7.0312 | -46.7331 | 76.268 | 76.1993 | -46.8613 | -46.9437 | 0.068665 | -0.068664 | 0.24262 | 122.9141 | -0.11444 | -0.045776 | -0.032043 | -0.068664 | -0.15106 | 0.21515 | 0.30212 | 0.05951 | 0.21057 | 0.14648 | 123.0881 | 122.8134 | 51.8234 | -122.9141 | 123.0606 | 122.9919 | 53.8239 | -122.9965
2404.0156 | 123.0469 | -47.6486 | 75.2838 | -0.00015269 | 0.017703 | 0.069959 | 0.069663 | 0.1327 | 0.00056395 | -0.0049411 | 0.030365 | -0.0065626 | 0.06106 | 0.057826 | 0.0097626 | -0.010692 | 75.0458 | 75.087 | 4.5547 | -47.937 | 75.3204 | -47.7997 | -47.8592 | -47.5113 | 8.1757 | -47.8363 | 75.3159 | 75.2655 | -47.85 | -47.8683 | -0.15106 | -0.21057 | 0.036622 | 122.7356 | -0.28839 | -0.07782 | -0.23804 | -0.20142 | -0.21973 | 0.032044 | 0.13733 | -0.18768 | 0.032043 | -0.01831 | 122.9691 | 122.6944 | 52.2034 | -123.143 | 122.9645 | 122.9141 | 55.8243 | -123.1522
2405.0156 | 123.0011 | -48.1247 | 74.8077 | 0.11429 | 0.016635 | 0.0706 | 0.068594 | 0.13014 | -0.00029045 | -0.0055821 | -0.084076 | -0.0082716 | 0.066614 | 0.05868 | 0.007199 | -0.012401 | 74.6246 | 74.7437 | 4.1107 | -48.262 | 74.9496 | -48.1567 | -48.23 | -47.8592 | 8.2901 | -48.1659 | 74.9451 | 74.8398 | -48.2803 | -48.3582 | -0.032043 | -0.10528 | 0.14191 | 122.8683 | -0.13733 | -0.032044 | -0.1831 | -0.15564 | -0.23346 | 0.13733 | 0.2655 | -0.041199 | 0.19226 | 0.032044 | 123.0743 | 122.7493 | 52.2354 | -123.0377 | 123.0698 | 122.9645 | 56.4148 | -123.1659
2406.0156 | 122.9919 | -48.5687 | 74.3774 | 0.030365 | 0.020053 | 0.06825 | 0.071372 | 0.12993 | 0.0022729 | -0.0038731 | 0.045624 | -0.0078442 | 0.063837 | 0.057826 | 0.0076264 | -0.013042 | 74.0753 | 74.1989 | 4.3442 | -48.7381 | 74.4278 | -48.6465 | -48.7289 | -48.3307 | 7.933 | -48.5367 | 74.5239 | 74.4186 | -48.6923 | -48.7701 | -0.077819 | -0.16022 | 0.050354 | 122.7676 | -0.16937 | -0.009155 | -0.30212 | -0.1236 | -0.20142 | 0.14648 | 0.23804 | 0.032044 | 0.23346 | 0.041199 | 122.9965 | 122.644 | 52.9129 | -123.1064 | 123.0927 | 122.9874 | 56.5018 | -123.1476
2407.0156 | 123.1476 | -48.8022 | 74.0936 | 0.18295 | 0.017276 | 0.066755 | 0.070303 | 0.12843 | -0.0022131 | -0.0053683 | 0.22873 | -0.010835 | 0.062555 | 0.057398 | 0.0074126 | -0.010051 | 73.7732 | 73.9655 | 4.1702 | -49.0494 | 74.0707 | -48.9716 | -49.0219 | -48.5321 | 7.0953 | -49.086 | 74.1302 | 74.0295 | -49.0402 | -49.0585 | -0.16937 | -0.21973 | -0.022888 | 122.7676 | -0.24719 | -0.027465 | -0.32043 | -0.23804 | -0.25635 | 0.036621 | 0.27008 | -0.28381 | -0.027466 | -0.064087 | 122.8729 | 122.5754 | 52.9724 | -123.1155 | 122.9324 | 122.8317 | 55.8975 | -123.1522
2408.0156 | 123.1018 | -48.2162 | 74.6658 | 0.14481 | 0.011081 | 0.068678 | 0.068808 | 0.12651 | -0.0062721 | -0.0075047 | 0.28214 | -0.0084852 | 0.062982 | 0.055476 | 0.0050628 | -0.010905 | 74.4781 | 74.6338 | 4.3259 | -48.5184 | 74.7116 | -48.3444 | -48.4314 | -48.0469 | 8.3267 | -48.3444 | 74.6613 | 74.6246 | -48.4039 | -48.4634 | -0.12817 | -0.21515 | 0.045776 | 122.85 | -0.30212 | -0.086976 | -0.18768 | -0.18768 | -0.24719 | -0.004578 | 0.16937 | -0.12817 | 0.11902 | -0.041199 | 122.9279 | 122.6944 | 52.5421 | -123.0972 | 122.8775 | 122.8409 | 56.543 | -123.1293
2409.0156 | 123.0789 | -49.1867 | 73.6359 | 0.17532 | 0.01578 | 0.068037 | 0.071799 | 0.12971 | 0.0014185 | -0.0051547 | 0.2211 | -0.0082716 | 0.063837 | 0.055049 | 0.0067718 | -0.012828 | 73.2239 | 73.3658 | 4.0375 | -49.6857 | 73.526 | -49.5483 | -49.6353 | -49.1089 | 8.3313 | -49.4431 | 73.6633 | 73.5855 | -49.4522 | -49.4888 | -0.36163 | -0.44861 | -0.10986 | 122.5525 | -0.49896 | -0.050354 | -0.41199 | -0.2655 | -0.30212 | 0.027466 | 0.07782 | -0.25635 | 0.045777 | -0.050354 | 122.7127 | 122.4106 | 53.2242 | -123.2712 | 122.85 | 122.7722 | 57.518 | -123.1247
2410.0156 | 123.0286 | -49.3286 | 73.6221 | -0.00015269 | 0.016421 | 0.069105 | 0.073081 | 0.13057 | 0.0027001 | -0.0049411 | 0.0914 | -0.0069898 | 0.065332 | 0.058253 | 0.0080536 | -0.01176 | 73.4894 | 73.5626 | 3.8177 | -49.5163 | 73.7503 | -49.3835 | -49.4843 | -49.1409 | 8.3038 | -49.5712 | 73.7045 | 73.5992 | -49.5392 | -49.5895 | -0.054932 | -0.15564 | 0.12817 | 122.8912 | -0.18768 | -0.032043 | -0.13275 | -0.21057 | -0.26093 | 0.082398 | 0.18768 | -0.24262 | 0.018311 | -0.022888 | 123.0789 | 122.818 | 53.1464 | -123.1064 | 123.0331 | 122.9279 | 57.6324 | -123.2117
2411.0156 | 123.0377 | -48.6053 | 74.2767 | 0.19058 | 0.017062 | 0.068891 | 0.071372 | 0.12779 | 0.00056395 | -0.0070773 | 0.19058 | -0.009126 | 0.065973 | 0.056971 | 0.0076264 | -0.010478 | 73.9243 | 74.0295 | 3.7811 | -48.967 | 74.263 | -48.8434 | -48.9304 | -48.3536 | 8.8852 | -48.6923 | 74.3958 | 74.3317 | -48.8022 | -48.8434 | -0.23804 | -0.32501 | -0.013733 | 122.6349 | -0.36163 | -0.036621 | -0.35248 | -0.19684 | -0.23804 | 0.11902 | 0.25177 | -0.086975 | 0.15106 | 0.054932 | 122.8683 | 122.5296 | 52.3865 | -123.2071 | 123.0011 | 122.937 | 57.4905 | -123.1201
2412.0156 | 123.0011 | -48.912 | 74.025 | 0.015106 | 0.017703 | 0.066969 | 0.071585 | 0.12971 | 0.0020593 | -0.0030185 | 0.045624 | -0.0078442 | 0.063196 | 0.054835 | 0.010617 | -0.012614 | 73.9563 | 74.0524 | 4.0833 | -48.9807 | 74.2355 | -48.8617 | -48.9624 | -48.674 | 8.9859 | -49.0448 | 74.1302 | 74.0799 | -49.086 | -49.118 | 0.050354 | -0.050354 | 0.21057 | 122.9645 | -0.068665 | -0.018311 | -0.068664 | -0.17395 | -0.20599 | 0.10529 | 0.23804 | -0.13275 | 0.073242 | 0.054932 | 123.1476 | 122.8683 | 52.9953 | -122.9874 | 123.0423 | 122.9919 | 57.8979 | -123.143
2413.0156 | 123.0743 | -49.5392 | 73.3658 | 0.099029 | 0.0089443 | 0.071882 | 0.067099 | 0.12629 | -0.0062721 | -0.0094273 | 0.12192 | -0.0093396 | 0.060846 | 0.055476 | 0.0057038 | -0.011546 | 73.1827 | 73.3612 | 3.9093 | -49.704 | 73.4482 | -49.5483 | -49.6811 | -49.2554 | 9.0546 | -49.6628 | 73.4253 | 73.3429 | -49.7223 | -49.736 | -0.009155 | -0.14191 | 0.082397 | 122.9004 | -0.16479 | -0.022888 | -0.18311 | -0.1831 | -0.19684 | 0.059509 | 0.28381 | -0.1236 | 0.073242 | -0.022888 | 122.9874 | 122.7219 | 53.4485 | -123.0469 | 122.9645 | 122.8821 | 58.5938 | -123.1018
2414.0156 | 122.9736 | -49.0219 | 73.9059 | 0.076141 | 0.016849 | 0.068891 | 0.072012 | 0.12864 | 0.0018457 | -0.0047275 | 0.0074766 | -0.0084852 | 0.065119 | 0.057185 | 0.0099762 | -0.013469 | 73.8281 | 73.8831 | 3.9963 | -49.1409 | 74.1302 | -48.967 | -49.0814 | -48.88 | 8.9539 | -49.1867 | 74.0112 | 73.938 | -49.2142 | -49.2737 | 0.054932 | -0.059509 | 0.2243 | 122.905 | -0.11902 | -0.059509 | -0.07782 | -0.19226 | -0.25177 | 0.10528 | 0.14191 | -0.16479 | 0.086975 | 0.032043 | 123.1522 | 122.85 | 53.0182 | -122.9874 | 123.0331 | 122.9599 | 57.9758 | -123.1796
2415.0156 | 123.0743 | -49.292 | 73.6084 | 0.15244 | 0.016421 | 0.069746 | 0.071799 | 0.12715 | -0.0024269 | -0.0051547 | 0.17532 | -0.0089124 | 0.064478 | 0.05633 | 0.0086944 | -0.01176 | 73.3749 | 73.4985 | 4.0421 | -49.5255 | 73.6954 | -49.4247 | -49.498 | -49.0631 | 8.7708 | -49.3881 | 73.7091 | 73.645 | -49.4705 | -49.5026 | -0.13275 | -0.20599 | 0.086976 | 122.7905 | -0.23346 | -0.027466 | -0.23346 | -0.17853 | -0.21057 | 0.10071 | 0.22888 | -0.096131 | 0.11444 | 0.036622 | 122.9874 | 122.6669 | 53.334 | -123.1064 | 123.0011 | 122.937 | 58.0627 | -123.111
2416.0156 | 123.024 | -48.88 | 74.0845 | 0.045624 | 0.016421 | 0.068678 | 0.069449 | 0.12928 | 0.0018457 | -0.0043003 | -0.053558 | -0.0084852 | 0.0664 | 0.056971 | 0.009549 | -0.012614 | 73.8922 | 73.97 | 4.2297 | -49.0814 | 74.1394 | -48.9166 | -49.0448 | -48.5733 | 8.9996 | -49.0768 | 74.144 | 74.0753 | -49.0448 | -49.1226 | -0.036621 | -0.1648 | 0.054931 | 122.85 | -0.20142 | -0.036621 | -0.19226 | -0.1648 | -0.24262 | 0.059509 | 0.3067 | -0.19684 | 0.045777 | -0.009156 | 123.0194 | 122.7722 | 53.1097 | -123.1293 | 123.024 | 122.9553 | 57.8796 | -123.2071
2417.0156 | 123.0423 | -48.5229 | 74.382 | 0.16006 | 0.021121 | 0.068037 | 0.074149 | 0.13142 | 0.00013675 | -0.0049411 | 0.11429 | -0.008058 | 0.062555 | 0.057826 | 0.0080536 | -0.010051 | 74.0845 | 74.3271 | 4.3945 | -48.8022 | 74.4873 | -48.6374 | -48.7198 | -48.3536 | 8.876 | -48.6786 | 74.4553 | 74.4049 | -48.7244 | -48.7701 | -0.11444 | -0.19684 | 0.10529 | 122.85 | -0.27924 | -0.082397 | -0.29755 | -0.20142 | -0.24719 | 0.073242 | 0.16937 | -0.15564 | 0.091553 | 0.022888 | 123.0103 | 122.6074 | 52.9175 | -123.1018 | 122.9782 | 122.9279 | 57.399 | -123.1522
2418.0156 | 123.0972 | -49.3561 | 73.4528 | 0.21347 | 0.012362 | 0.066114 | 0.067954 | 0.12736 | -0.0049903 | -0.0062229 | 0.38895 | -0.009126 | 0.06106 | 0.057398 | 0.0063446 | -0.0094102 | 73.4344 | 73.4482 | 4.0329 | -49.5987 | 73.5031 | -49.5026 | -49.5895 | -49.1409 | 8.9676 | -49.4843 | 73.5031 | 73.4619 | -49.5712 | -49.6307 | -0.14648 | -0.23346 | 0.050354 | 122.8043 | -0.24262 | -0.009155 | -0.018311 | -0.21515 | -0.27466 | 0.050354 | 0.21515 | -0.12817 | 0.14648 | 0.009155 | 122.8592 | 122.7905 | 53.389 | -123.0423 | 122.8592 | 122.818 | 58.3237 | -123.0835
2419.0156 | 122.9919 | -49.4202 | 73.5031 | 0.037994 | 0.017489 | 0.067182 | 0.072653 | 0.12993 | 0.0031273 | -0.0043003 | 0.0074766 | -0.0050672 | 0.065759 | 0.055903 | 0.0091216 | -0.012187 | 73.2376 | 73.3292 | 3.5522 | -49.6948 | 73.5672 | -49.5575 | -49.6719 | -49.2508 | 8.8806 | -49.6674 | 73.5672 | 73.4985 | -49.6582 | -49.6948 | -0.13733 | -0.25177 | 0.064087 | 122.7493 | -0.27466 | -0.022888 | -0.2655 | -0.23804 | -0.27466 | 0.064087 | 0.16937 | -0.24719 | 0.027466 | -0.004578 | 122.9874 | 122.6578 | 52.9724 | -123.175 | 122.9874 | 122.9187 | 58.3008 | -123.1979
2420.0156 | 123.056 | -50.1022 | 72.8531 | -0.10696 | 0.017703 | 0.069319 | 0.072867 | 0.13035 | 0.00077755 | -0.0057957 | -0.023041 | -0.0089124 | 0.063837 | 0.055903 | 0.0086944 | -0.012187 | 72.821 | 72.8668 | 3.6758 | -50.2213 | 73.0545 | -50.0656 | -50.1389 | -49.7223 | 8.5419 | -50.4089 | 72.9492 | 72.8806 | -50.2716 | -50.3723 | 0.036621 | -0.036621 | 0.20142 | 122.9691 | -0.11902 | -0.082397 | -0.032043 | -0.16937 | -0.27008 | 0.096131 | 0.37994 | -0.3067 | -0.036622 | 0.027466 | 123.1567 | 122.9233 | 53.7781 | -122.9919 | 123.0515 | 122.9828 | 58.6441 | -123.2254
2421.0156 | 123.0148 | -49.6445 | 73.1369 | 0.10666 | 0.015353 | 0.068037 | 0.068594 | 0.12864 | -0.0013587 | -0.0087863 | 0.12955 | -0.0082716 | 0.064691 | 0.056971 | 0.007199 | -0.0098374 | 73.558 | 73.3337 | 3.8361 | -49.5255 | 73.6542 | -49.4385 | -49.5438 | -49.1684 | 8.9172 | -49.5255 | 73.6496 | 73.5626 | -49.6124 | -49.704 | 0.20599 | 0.10071 | 0.51727 | 122.9782 | 0.11902 | 0.01831 | 0.42114 | 0.032043 | -0.059509 | 0.51269 | 0.47607 | 0.11902 | 0.17853 | 0.42572 | 123.2986 | 123.2025 | 53.4805 | -122.6807 | 123.2941 | 123.2071 | 58.5617 | -122.8409
2422.0156 | 122.9965 | -50.0381 | 72.8851 | -0.0077822 | 0.018771 | 0.068037 | 0.070731 | 0.12864 | 0.0012047 | -0.0047275 | 0.0074766 | -0.0082716 | 0.064478 | 0.058039 | 0.0069854 | -0.0094102 | 72.5372 | 72.6837 | 3.3188 | -50.3494 | 72.8256 | -50.235 | -50.3174 | -49.8276 | 8.9401 | -50.1343 | 72.9309 | 72.8806 | -50.235 | -50.2716 | -0.19684 | -0.27924 | -0.059509 | 122.7219 | -0.31128 | -0.032043 | -0.3479 | -0.19684 | -0.23346 | 0.045776 | 0.21057 | -0.09613 | 0.13733 | -0.004578 | 122.8638 | 122.5754 | 53.3569 | -123.2025 | 122.9691 | 122.9187 | 58.9783 | -123.1567
2423.0312 | 123.1705 | -49.704 | 73.1552 | -0.18326 | 0.0091581 | -0.03557 | 0.069663 | 0.12672 | -0.0058447 | -0.0081455 | -0.0077819 | -0.010835 | 0.061701 | 0.057185 | 0.0042084 | -0.0091966 | 73.0133 | 73.2239 | 3.7857 | -49.9008 | 73.2422 | -49.7818 | -49.8642 | -49.4751 | 8.9767 | -49.8001 | 73.1598 | 73.114 | -49.9558 | -49.9558 | -0.07782 | -0.16022 | 0.086975 | 122.9279 | -0.19684 | -0.036621 | -0.14191 | -0.25177 | -0.25177 | 0.004578 | 0.22888 | -0.096131 | 0.15564 | -0.041198 | 122.9462 | 122.7173 | 53.4897 | -123.0194 | 122.8638 | 122.818 | 58.6807 | -123.111
2424.0156 | 123.0286 | -50.3082 | 72.6151 | -0.076447 | 0.014926 | 0.068891 | 0.071158 | 0.12843 | 0.0022729 | -0.0062229 | -0.068817 | -0.008058 | 0.065759 | 0.059107 | 0.0080536 | -0.01411 | 72.1848 | 72.5327 | 3.5477 | -50.5875 | 72.583 | -50.473 | -50.5463 | -50.061 | 8.6884 | -50.4318 | 72.6425 | 72.5739 | -50.5371 | -50.5554 | -0.16479 | -0.23804 | -0.032043 | 122.8409 | -0.27923 | -0.041198 | -0.4303 | -0.22888 | -0.24719 | 0.027466 | 0.24719 | -0.1236 | 0.1236 | -0.041198 | 122.8912 | 122.493 | 53.8559 | -123.1613 | 122.9507 | 122.8821 | 58.9966 | -123.1705
2425.0156 | 123.0423 | -49.292 | 73.6496 | -0.053558 | 0.020267 | 0.064192 | 0.071158 | 0.12843 | 0.0022729 | -0.0034457 | -0.023041 | -0.0082716 | 0.065546 | 0.057185 | 0.009549 | -0.012187 | 73.288 | 73.4253 | 4.0054 | -49.5255 | 73.6221 | -49.4476 | -49.5071 | -49.054 | 9.137 | -49.4247 | 73.7091 | 73.6221 | -49.4705 | -49.5209 | -0.15564 | -0.21515 | -0.027466 | 122.7173 | -0.23346 | -0.018311 | -0.36163 | -0.17853 | -0.22888 | 0.059509 | 0.23804 | -0.13275 | 0.09613 | -0.027466 | 122.9141 | 122.58 | 53.2974 | -123.1567 | 123.0011 | 122.9141 | 58.429 | -123.1705
2426.0156 | 123.0652 | -49.7681 | 73.1918 | -0.16037 | 0.013644 | 0.066755 | 0.073081 | 0.12779 | -0.00050425 | -0.0079319 | -0.16037 | -0.013185 | 0.063623 | 0.054835 | 0.0065582 | -0.010265 | 72.9172 | 73.082 | 3.8132 | -50.0153 | 73.201 | -49.8871 | -49.9466 | -49.5438 | 9.1187 | -49.8779 | 73.2468 | 73.1598 | -49.9695 | -49.9969 | -0.11902 | -0.17853 | 0.009156 | 122.85 | -0.24719 | -0.068665 | -0.27466 | -0.20142 | -0.22888 | 0.054932 | 0.2243 | -0.10986 | 0.11902 | -0.032043 | 122.9691 | 122.6852 | 53.5812 | -123.1384 | 123.0148 | 122.9279 | 58.8867 | -123.1888
2427.0156 | 122.9691 | -49.2325 | 73.7183 | -0.0077822 | 0.018558 | 0.067182 | 0.073508 | 0.12715 | 0.00077755 | -0.0060093 | 0.12955 | -0.0086988 | 0.064478 | 0.056758 | 0.0059174 | -0.0098374 | 73.4802 | 73.5947 | 3.8635 | -49.53 | 73.7778 | -49.3515 | -49.4522 | -49.1821 | 8.6792 | -49.6719 | 73.6679 | 73.5855 | -49.53 | -49.53 | -0.11902 | -0.21973 | 0.059509 | 122.8271 | -0.29755 | -0.07782 | -0.23804 | -0.29755 | -0.29755 | -0.050354 | 0.050354 | -0.43945 | -0.14191 | -0.13275 | 123.0103 | 122.7127 | 53.096 | -123.1705 | 122.9004 | 122.818 | 57.9117 | -123.2483
2428.0156 | 123.0789 | -50.1892 | 72.6746 | -0.11459 | 0.016421 | 0.064832 | 0.070517 | 0.12971 | 0.00056395 | -0.0051547 | 1.0756 | -0.0076306 | 0.062128 | 0.056971 | 0.0082672 | -0.010905 | 72.9904 | 72.9904 | 3.4103 | -50.1114 | 73.1918 | -49.9695 | -50.0565 | -49.7406 | 8.8989 | -50.2396 | 73.0453 | 72.9767 | -50.1709 | -50.2716 | 0.21973 | 0.13275 | 0.51727 | 123.1796 | 0.07782 | -0.054931 | 0.31586 | 0.018311 | -0.082397 | 0.37079 | 0.44861 | -0.050354 | 0.032043 | 0.30212 | 123.381 | 123.1796 | 53.5995 | -122.731 | 123.2346 | 123.1659 | 59.0881 | -122.9462
2429.0156 | 122.9965 | -49.8184 | 73.1415 | -0.03067 | 0.018344 | 0.06825 | 0.070517 | 0.12693 | 0.00056395 | -0.0053683 | 0.068512 | -0.008058 | 0.065119 | 0.057398 | 0.0084808 | -0.011974 | 73.027 | 73.1873 | 3.4332 | -49.8413 | 73.3704 | -49.7177 | -49.823 | -49.5987 | 8.8989 | -50.0244 | 73.2513 | 73.1827 | -49.9695 | -50.0015 | 0.10071 | -0.004578 | 0.22888 | 123.0057 | -0.022889 | -0.018311 | -0.11444 | -0.15106 | -0.18311 | 0.10986 | 0.21973 | -0.20599 | -0.022888 | 0.041199 | 123.1888 | 122.8455 | 53.2516 | -122.9645 | 123.0698 | 123.0011 | 58.7173 | -123.143
2430.0156 | 123.056 | -49.7269 | 73.2056 | -0.18326 | 0.013003 | 0.06761 | 0.072653 | 0.12864 | -0.00029045 | -0.0053683 | -0.13748 | -0.0084852 | 0.064264 | 0.057185 | 0.0069854 | -0.010905 | 73.32 | 73.4665 | 3.6026 | -49.5529 | 73.613 | -49.4934 | -49.5987 | -49.3423 | 9.0225 | -49.8962 | 73.3704 | 73.233 | -49.8871 | -49.9558 | 0.23346 | 0.12817 | 0.40741 | 123.1934 | 0.17395 | 0.045777 | 0.11444 | -0.16022 | -0.22888 | 0.16479 | 0.38452 | -0.16937 | 0.05951 | 0.027466 | 123.3398 | 123.0469 | 53.3295 | -122.8043 | 123.0972 | 122.9599 | 58.7494 | -123.1613
2431.0156 | 123.024 | -50.9079 | 72.0108 | -0.045929 | 0.016849 | 0.06825 | 0.073294 | 0.12971 | 0.0022729 | -0.0040867 | 0.053253 | -0.0072034 | 0.065973 | 0.05868 | 0.007199 | -0.010692 | 71.7957 | 71.9284 | 2.5864 | -51.1368 | 72.0703 | -51.0269 | -51.1139 | -50.7248 | 8.638 | -51.2146 | 72.0474 | 71.9833 | -51.123 | -51.1688 | -0.11902 | -0.20599 | 0.059509 | 122.8363 | -0.22888 | -0.022888 | -0.21515 | -0.21515 | -0.26093 | 0.036621 | 0.18311 | -0.3067 | -0.045777 | -0.027466 | 122.9782 | 122.7036 | 53.4943 | -123.1247 | 122.9553 | 122.8912 | 59.5459 | -123.1796
2432.0156 | 123.0377 | -49.736 | 73.2056 | -0.24429 | 0.0080899 | 0.0706 | 0.068594 | 0.128 | -0.0026405 | -0.0075047 | -0.10696 | -0.009126 | 0.064264 | 0.057826 | 0.0065582 | -0.012828 | 73.1552 | 73.0545 | 2.6642 | -49.9741 | 73.4207 | -49.7681 | -49.8642 | -49.5255 | 9.3842 | -50.0244 | 73.2742 | 73.2147 | -49.9237 | -49.9786 | -0.032043 | -0.12817 | 0.21515 | 122.7905 | -0.23804 | -0.10986 | -0.050354 | -0.18768 | -0.24261 | 0.068665 | 0.21057 | -0.28839 | -0.045776 | 0.009156 | 123.1567 | 122.8912 | 52.4002 | -123.0698 | 123.0103 | 122.9507 | 59.1202 | -123.1842
2433.0156 | 123.0927 | -49.5712 | 73.3246 | -0.21378 | 0.014712 | 0.068891 | 0.071372 | 0.13014 | -0.00029045 | -0.0070773 | -0.18326 | -0.007417 | 0.0664 | 0.05868 | 0.008908 | -0.012187 | 73.1003 | 73.2468 | 3.1448 | -49.8413 | 73.3795 | -49.7498 | -49.8642 | -49.324 | 9.4711 | -49.6994 | 73.4024 | 73.3383 | -49.7818 | -49.8138 | -0.17853 | -0.29297 | 0.054932 | 122.818 | -0.27008 | 0.022888 | -0.2243 | -0.21057 | -0.24262 | 0.07782 | 0.24719 | -0.12817 | 0.11444 | 0.013733 | 122.9507 | 122.6715 | 52.7161 | -123.1888 | 122.9736 | 122.9095 | 59.0424 | -123.1384
2434.0156 | 123.0469 | -50.9811 | 71.9376 | -0.21378 | 0.015353 | 0.067823 | 0.072012 | 0.13014 | -0.00071785 | -0.0070773 | -0.14511 | -0.0093396 | 0.063196 | 0.055903 | 0.0076264 | -0.01176 | 71.7499 | 71.8781 | 2.7786 | -51.1505 | 72.0566 | -51.0544 | -51.123 | -50.7797 | 9.0546 | -51.2512 | 72.02 | 71.9193 | -51.1917 | -51.2421 | -0.073242 | -0.14191 | 0.11902 | 122.8592 | -0.16937 | -0.027466 | -0.18768 | -0.21057 | -0.26092 | 0.082397 | 0.20142 | -0.27008 | -0.009156 | -0.018311 | 123.0377 | 122.731 | 53.7598 | -123.0606 | 123.0011 | 122.9004 | 60.0357 | -123.1796
2435.0156 | 123.0606 | -50.3036 | 72.6425 | -0.45029 | 0.014926 | 0.071455 | 0.071585 | 0.12928 | 0.0014185 | -0.0032321 | 0.030365 | -0.0093396 | 0.065332 | 0.058467 | 0.007199 | -0.010051 | 72.5189 | 72.6654 | 3.2364 | -50.4044 | 72.7753 | -50.3128 | -50.4135 | -50.0473 | 9.4711 | -50.4227 | 72.6837 | 72.6196 | -50.5234 | -50.5554 | -0.009155 | -0.10986 | 0.13275 | 122.9691 | -0.10071 | 0.009155 | -0.1236 | -0.21973 | -0.25177 | 0.041199 | 0.25635 | -0.11902 | 0.13275 | -0.022888 | 123.0789 | 122.8226 | 53.54 | -123.056 | 122.9874 | 122.9233 | 59.7748 | -123.1979
2436.0156 | 123.0606 | -49.8413 | 73.1003 | -0.20615 | 0.014071 | 0.06761 | 0.071158 | 0.12907 | -0.0011451 | -0.0079319 | -0.12985 | -0.007417 | 0.064691 | 0.056544 | 0.0057038 | -0.0098374 | 72.8668 | 73.0316 | 3.5065 | -50.0198 | 73.1918 | -49.8871 | -50.0107 | -49.6399 | 9.5947 | -50.0473 | 73.1598 | 73.082 | -50.0473 | -50.0793 | -0.045776 | -0.16937 | 0.091552 | 122.8729 | -0.17853 | -0.009155 | -0.23346 | -0.20599 | -0.23804 | 0.059509 | 0.20142 | -0.20599 | 0.032044 | -0.018311 | 123.0331 | 122.7081 | 53.3478 | -123.111 | 123.0011 | 122.9233 | 59.436 | -123.1796
2437.0156 | 123.0423 | -50.1434 | 72.7478 | -0.11459 | 0.014285 | 0.071027 | 0.070517 | 0.13035 | 0.0012047 | -0.0077183 | -0.03067 | -0.0084852 | 0.064264 | 0.05868 | 0.009549 | -0.012187 | 72.6151 | 72.757 | 3.8361 | -50.2945 | 72.8989 | -50.1984 | -50.2945 | -49.9969 | 9.5352 | -50.3494 | 72.8256 | 72.7524 | -50.3586 | -50.4135 | -0.054931 | -0.15106 | 0.15106 | 122.9004 | -0.15106 | 0 | -0.13275 | -0.21515 | -0.27008 | 0.07782 | 0.14648 | -0.20599 | 0.064087 | 0.004577 | 123.0423 | 122.7585 | 53.9795 | -123.0423 | 122.9691 | 122.8958 | 59.6787 | -123.1613
2438.0156 | 123.0103 | -50.2396 | 72.6929 | -0.22903 | 0.013217 | 0.068891 | 0.073081 | 0.13185 | -0.0032813 | -0.0043003 | -0.00015237 | -0.010194 | 0.063623 | 0.058039 | 0.00549 | -0.011333 | 72.3175 | 72.5876 | 3.6758 | -50.4547 | 72.7844 | -50.322 | -50.4135 | -50.0427 | 9.0912 | -50.3769 | 72.757 | 72.6791 | -50.4318 | -50.4593 | -0.082397 | -0.17395 | 0.091553 | 122.8271 | -0.21515 | -0.041199 | -0.37537 | -0.19226 | -0.21973 | 0.064087 | 0.19684 | -0.13733 | 0.082398 | -0.013733 | 123.024 | 122.5571 | 53.9154 | -123.1064 | 122.9965 | 122.9187 | 59.3307 | -123.1522
2439.0156 | 123.0698 | -49.7131 | 73.2468 | -0.18326 | 0.013858 | 0.0706 | 0.072226 | 0.13035 | -0.00029045 | -0.0062229 | -0.18326 | -0.007417 | 0.065546 | 0.057398 | 0.0050628 | -0.010265 | 73.082 | 73.2468 | 3.6255 | -49.8322 | 73.3795 | -49.6948 | -49.8367 | -49.5621 | 9.4528 | -49.8779 | 73.2468 | 73.1781 | -49.9374 | -49.9741 | 0.018311 | -0.1236 | 0.13275 | 122.9599 | -0.11902 | 0.004578 | -0.16479 | -0.2243 | -0.26093 | 0 | 0.15106 | -0.16479 | 0.09613 | -0.068664 | 123.0927 | 122.7951 | 53.3386 | -123.0835 | 122.9599 | 122.8912 | 59.166 | -123.2208
2440.0156 | 123.0515 | -51.1414 | 71.8185 | -0.24429 | 0.0085171 | 0.071455 | 0.071372 | 0.12693 | -0.0017859 | -0.0089999 | -0.11459 | -0.010408 | 0.060419 | 0.05868 | 0.00549 | -0.011119 | 71.6583 | 71.8826 | 3.2684 | -51.21 | 71.9238 | -51.1093 | -51.21 | -50.9537 | 8.931 | -51.2833 | 71.8048 | 71.7636 | -51.3336 | -51.3702 | 0.032043 | -0.068665 | 0.10529 | 123.024 | -0.068665 | 0 | -0.16022 | -0.19226 | -0.22888 | -0.013732 | 0.18768 | -0.14191 | 0.086975 | -0.054931 | 123.0652 | 122.7997 | 54.4098 | -123.0286 | 122.9462 | 122.905 | 60.0723 | -123.1888
2441.0156 | 123.056 | -49.4431 | 73.5168 | -0.091705 | 0.016208 | 0.069319 | 0.071158 | 0.12886 | 0.0022729 | -0.0047275 | -0.03067 | -0.006349 | 0.062555 | 0.057398 | 0.0084808 | -0.010905 | 73.1964 | 73.3109 | 3.7949 | -49.7314 | 73.4573 | -49.6262 | -49.7131 | -49.2554 | 9.9838 | -49.6124 | 73.4848 | 73.4207 | -49.649 | -49.6948 | -0.18311 | -0.27008 | -0.05951 | 122.7539 | -0.28839 | -0.01831 | -0.32044 | -0.20599 | -0.25177 | -0.032044 | 0.18768 | -0.16937 | 0.082397 | -0.096131 | 122.9004 | 122.6395 | 53.2379 | -123.23 | 122.9279 | 122.8638 | 59.4269 | -123.2117
2442.0156 | 123.0652 | -49.2737 | 73.6313 | -0.18326 | 0.014926 | 0.069319 | 0.074362 | 0.12971 | 0.00077755 | -0.0055821 | -0.13748 | -0.011262 | 0.063623 | 0.056544 | 0.0080536 | -0.012828 | 73.4756 | 73.6267 | 3.8086 | -49.4659 | 73.7823 | -49.324 | -49.4247 | -49.0356 | 9.9792 | -49.292 | 73.7686 | 73.7 | -49.4293 | -49.5163 | -0.050354 | -0.15106 | 0.15106 | 122.9004 | -0.19226 | -0.041198 | -0.15564 | -0.15564 | -0.24261 | 0.13733 | 0.23804 | -0.01831 | 0.2243 | 0.068664 | 123.056 | 122.7493 | 53.0823 | -123.056 | 123.0423 | 122.9736 | 59.2529 | -123.1476
2443.0156 | 123.056 | -49.6857 | 73.2697 | -0.18326 | 0.01578 | 0.06825 | 0.070731 | 0.12907 | 0.0014185 | -0.0072911 | -0.16037 | -0.0078442 | 0.063623 | 0.055476 | 0.0050628 | -0.011119 | 73.114 | 73.2513 | 3.5568 | -49.8001 | 73.407 | -49.7086 | -49.8093 | -49.4202 | 10.2631 | -49.8871 | 73.3612 | 73.2697 | -49.8642 | -49.9146 | -0.022888 | -0.1236 | 0.13733 | 122.937 | -0.11444 | 0.009155 | -0.15564 | -0.17853 | -0.22888 | 0.091553 | 0.2655 | -0.20142 | 0.027466 | 0 | 123.0927 | 122.7997 | 53.2425 | -123.0789 | 123.0469 | 122.9553 | 59.9487 | -123.1842
2444.0156 | 123.0148 | -49.2828 | 73.6725 | -0.23666 | 0.011935 | 0.069105 | 0.071585 | 0.13099 | -0.0030677 | -0.0075047 | -0.15274 | -0.0084852 | 0.064264 | 0.056117 | 0.0048492 | -0.010692 | 73.5809 | 73.8327 | 3.9642 | -49.2188 | 73.9288 | -49.1867 | -49.2966 | -49.0173 | 10.611 | -49.4751 | 73.7503 | 73.6679 | -49.5255 | -49.585 | 0.09613 | -0.013733 | 0.25635 | 123.1155 | 0.064087 | 0.07782 | -0.091552 | -0.24262 | -0.30212 | 0.07782 | 0.2655 | -0.19226 | 0.10986 | -0.004577 | 123.2117 | 122.8638 | 53.2471 | -122.9691 | 123.0331 | 122.9507 | 59.8938 | -123.2574
2445.0156 | 123.0194 | -49.7177 | 73.2376 | -0.19089 | 0.013431 | 0.068464 | 0.072226 | 0.12864 | -0.00029045 | -0.0079319 | -0.11459 | -0.011049 | 0.064051 | 0.058467 | 0.0065582 | -0.011974 | 72.9218 | 73.114 | 3.3417 | -49.942 | 73.2697 | -49.8093 | -49.9329 | -49.498 | 10.3958 | -49.8917 | 73.2513 | 73.1644 | -49.9237 | -49.9558 | -0.091553 | -0.21515 | 0.032043 | 122.8317 | -0.22431 | -0.009156 | -0.31586 | -0.20599 | -0.23804 | 0.013733 | 0.21973 | -0.17395 | 0.064087 | -0.073242 | 122.9874 | 122.6395 | 53.0594 | -123.1705 | 122.9691 | 122.8821 | 60.1135 | -123.1934
2446.0156 | 123.143 | -49.8184 | 73.0637 | -0.19852 | 0.0055265 | 0.073164 | 0.064108 | 0.12843 | -0.0073401 | -0.0064365 | -0.038299 | -0.009126 | 0.062128 | 0.055689 | 0.006131 | -0.0094102 | 72.9355 | 73.0682 | 3.978 | -49.9603 | 73.1277 | -49.8871 | -49.9878 | -49.6216 | 10.3592 | -49.9878 | 73.0499 | 72.9904 | -50.0565 | -50.0931 | -0.068665 | -0.16937 | 0.064087 | 122.8867 | -0.14191 | 0.027466 | -0.12817 | -0.23804 | -0.27466 | -0.013733 | 0.19684 | -0.16937 | 0.10529 | -0.073243 | 122.9462 | 122.7539 | 53.7964 | -123.0515 | 122.8683 | 122.8088 | 60.1776 | -123.1567
2447.0156 | 123.0652 | -50.6699 | 72.2168 | -0.12222 | 0.01578 | 0.067823 | 0.07778 | 0.12736 | 0.0012047 | -0.0064365 | -0.12222 | -0.008058 | 0.065119 | 0.055476 | 0.0082672 | -0.012401 | 71.8002 | 71.9559 | 3.2547 | -51.0818 | 72.0978 | -50.9903 | -51.059 | -50.354 | 10.4004 | -50.885 | 72.3175 | 72.2534 | -50.8759 | -50.8896 | -0.32043 | -0.3891 | -0.11902 | 122.6257 | -0.41199 | -0.022888 | -0.41657 | -0.20599 | -0.21973 | 0.10071 | 0.31586 | -0.21515 | 0.004577 | 0.036621 | 122.7676 | 122.4701 | 53.9246 | -123.2758 | 122.9874 | 122.9233 | 61.0703 | -123.1064
2448.0156 | 123.056 | -51.4481 | 71.4798 | -0.24429 | 0.010013 | 0.070387 | 0.069022 | 0.12907 | -0.0043495 | -0.0064365 | -0.12222 | -0.0097668 | 0.059351 | 0.05633 | 0.006131 | -0.011974 | 71.3104 | 71.553 | 3.479 | -51.5442 | 71.5988 | -51.4755 | -51.5762 | -51.123 | 10.1944 | -51.6403 | 71.5897 | 71.4844 | -51.6266 | -51.6861 | -0.027466 | -0.12817 | 0.11902 | 123.0011 | -0.09613 | 0.032044 | -0.16937 | -0.17853 | -0.23804 | 0.10986 | 0.32501 | -0.19226 | 0.045776 | 0.004578 | 123.0469 | 122.7585 | 54.9271 | -123.056 | 123.0377 | 122.9324 | 61.6425 | -123.1659
2449.0156 | 123.056 | -50.2899 | 72.6562 | -0.20615 | 0.013217 | 0.070387 | 0.073508 | 0.12864 | -0.0019995 | -0.0083591 | -0.168 | -0.0072034 | 0.063623 | 0.056971 | 0.0057038 | -0.0096238 | 72.2855 | 72.4411 | 3.2135 | -50.592 | 72.6151 | -50.473 | -50.5783 | -50.0565 | 10.8673 | -50.4044 | 72.6654 | 72.6517 | -50.4868 | -50.5371 | -0.1831 | -0.28839 | -0.041199 | 122.731 | -0.30212 | -0.013733 | -0.37079 | -0.19684 | -0.24719 | 0.009155 | 0.23346 | -0.11444 | 0.13275 | -0.004578 | 122.905 | 122.5754 | 53.5034 | -123.2346 | 122.9553 | 122.9416 | 61.1572 | -123.1934
2450.0156 | 123.0927 | -50.6424 | 72.2626 | -0.18326 | 0.0074491 | 0.069105 | 0.072226 | 0.12993 | -0.0045631 | -0.0096409 | -0.13748 | -0.0089124 | 0.062555 | 0.055476 | 0.0063446 | -0.011333 | 72.377 | 72.5876 | 3.6392 | -50.6287 | 72.551 | -50.5096 | -50.6332 | -50.3403 | 10.524 | -50.7477 | 72.3221 | 72.2122 | -50.8713 | -50.9491 | 0.13275 | 0.009155 | 0.28839 | 123.23 | 0.013733 | 0.004578 | 0.11444 | -0.22888 | -0.3067 | 0.05951 | 0.30212 | -0.10529 | 0.20142 | -0.050354 | 123.1934 | 123.0194 | 54.2816 | -122.8958 | 122.9645 | 122.8546 | 61.1664 | -123.2117
2451.0156 | 122.9919 | -49.9786 | 72.9584 | -0.24429 | 0.011294 | 0.068891 | 0.071585 | 0.13121 | 0.00013675 | -0.0089999 | -0.19852 | -0.0093396 | 0.063837 | 0.057398 | 0.0063446 | -0.010478 | 72.5327 | 72.7661 | 3.7582 | -50.2029 | 72.9721 | -50.116 | -50.235 | -49.791 | 10.8353 | -50.1022 | 73.0453 | 72.9675 | -50.1663 | -50.1984 | -0.13733 | -0.25635 | 0.013733 | 122.7448 | -0.2243 | 0.032043 | -0.42572 | -0.18768 | -0.21973 | 0.086975 | 0.18768 | -0.1236 | 0.09613 | 0.009155 | 122.9507 | 122.5113 | 53.7369 | -123.1934 | 123.024 | 122.9462 | 60.8139 | -123.1567
2452.0156 | 123.1338 | -50.1389 | 72.6654 | -3.1282 | 0.0053129 | 0.066328 | 0.068808 | 0.12736 | -0.0019995 | -0.0057957 | -0.038299 | -0.011262 | 0.062769 | 0.057185 | 0.0069854 | -0.010051 | 72.6288 | 72.9813 | 4.0604 | -50.1938 | 72.9446 | -50.1205 | -50.2213 | -49.6445 | 11.0367 | -50.0931 | 72.9813 | 72.8714 | -50.2304 | -50.3403 | 0.018311 | -0.082397 | 0.27924 | 123.1201 | -0.054932 | 0.027465 | -0.036621 | -0.091553 | -0.20142 | 0.31586 | 0.49439 | 0.045776 | 0.24719 | 0.20599 | 123.0835 | 122.7676 | 54.1992 | -122.8867 | 123.1201 | 123.0103 | 61.1755 | -123.0057
2453.0156 | 123.0927 | -50.3036 | 72.5555 | -0.168 | 0.0089443 | 0.069532 | 0.072226 | 0.12843 | -0.0024269 | -0.0066501 | -0.15274 | -0.011903 | 0.061914 | 0.056758 | 0.0065582 | -0.012187 | 72.4228 | 72.6334 | 3.7811 | -50.4822 | 72.6746 | -50.386 | -50.473 | -50.0061 | 10.7574 | -50.4044 | 72.6837 | 72.5876 | -50.4822 | -50.528 | -0.082397 | -0.16937 | 0.11902 | 122.937 | -0.17853 | -0.009156 | -0.13275 | -0.17853 | -0.2243 | 0.12817 | 0.29755 | -0.10071 | 0.1236 | 0.032043 | 122.9782 | 122.7264 | 54.0848 | -123.0286 | 122.9874 | 122.8912 | 61.0611 | -123.0835
2454.0156 | 123.1155 | -50.6653 | 72.1756 | -0.18326 | 0.0076627 | 0.06761 | 0.069663 | 0.12864 | -0.0039221 | -0.0060093 | -0.091705 | -0.011476 | 0.059351 | 0.052485 | 0.0020722 | -0.010265 | 71.9513 | 72.226 | 3.5934 | -50.8987 | 72.226 | -50.8255 | -50.9125 | -50.5051 | 10.6384 | -50.6378 | 72.2031 | 72.0932 | -50.8896 | -50.9491 | -0.16022 | -0.24719 | 0.050354 | 122.8912 | -0.23346 | 0.013733 | -0.2243 | -0.2243 | -0.28381 | 0.027466 | 0.16022 | 0.027466 | 0.31128 | -0.082397 | 122.8912 | 122.6166 | 54.2587 | -123.0881 | 122.8683 | 122.7585 | 61.3037 | -123.1247
2455.0156 | 123.0423 | -50.1938 | 72.7524 | -0.22903 | 0.014071 | 0.071668 | 0.072653 | 0.12886 | 0.0031273 | -0.0064365 | -0.18326 | -0.0089124 | 0.063837 | 0.056758 | 0.0048492 | -0.012614 | 72.3816 | 72.5739 | 3.392 | -50.5051 | 72.7295 | -50.3723 | -50.473 | -49.9924 | 10.7712 | -50.3311 | 72.7249 | 72.6608 | -50.4364 | -50.4868 | -0.17853 | -0.27923 | -0.022888 | 122.7676 | -0.31128 | -0.032044 | -0.37079 | -0.24261 | -0.29297 | -0.027465 | 0.20142 | -0.13733 | 0.15564 | -0.091552 | 122.9233 | 122.5754 | 53.5858 | -123.2254 | 122.9187 | 122.8546 | 60.965 | -123.2391
2456.0156 | 123.0972 | -50.5508 | 72.3312 | 0.12955 | 0.011935 | 0.067823 | 0.073081 | 0.12693 | -0.0024269 | -0.0075047 | -0.168 | -0.010621 | 0.062982 | 0.056758 | 0.00549 | -0.0098374 | 72.1848 | 72.4045 | 3.0167 | -50.7339 | 72.3907 | -50.6241 | -50.7248 | -50.2213 | 11.0229 | -50.6424 | 72.4091 | 72.2946 | -50.7431 | -50.7935 | -0.073242 | -0.17395 | 0.059509 | 122.9553 | -0.18311 | -0.009156 | -0.14648 | -0.19226 | -0.24261 | 0.07782 | 0.32959 | -0.091553 | 0.15106 | -0.036621 | 122.9416 | 122.7356 | 53.5675 | -123.056 | 122.9599 | 122.8455 | 61.5738 | -123.1247
2457.0156 | 123.0286 | -50.6332 | 72.2946 | -0.22141 | 0.011722 | 0.069746 | 0.072226 | 0.12907 | 0.00013675 | -0.0072911 | -0.19089 | -0.010194 | 0.063837 | 0.056758 | 0.00784 | -0.011974 | 72.2488 | 72.3084 | 2.774 | -50.8163 | 72.5281 | -50.6378 | -50.7248 | -50.3082 | 10.9955 | -50.9033 | 72.4457 | 72.3221 | -50.7706 | -50.8347 | -0.004577 | -0.091552 | 0.23346 | 122.9416 | -0.1831 | -0.091553 | -0.045777 | -0.13733 | -0.20142 | 0.15106 | 0.32501 | -0.27008 | -0.068664 | 0.027466 | 123.1613 | 122.8821 | 53.4073 | -123.0194 | 123.0789 | 122.9553 | 61.6287 | -123.1293
2458.0156 | 123.1567 | -50.528 | 72.3495 | -0.22903 | 0.0059537 | 0.069319 | 0.072226 | 0.13014 | -7.6852e-05 | -0.0085727 | 0.67886 | -0.011476 | 0.059992 | 0.057612 | 0.0080536 | -0.012614 | 72.0886 | 72.377 | 2.8336 | -50.7156 | 72.3816 | -50.6378 | -50.7339 | -50.2029 | 11.2244 | -50.6699 | 72.3862 | 72.2717 | -50.7019 | -50.7843 | -0.10986 | -0.20599 | 0.032044 | 122.905 | -0.18768 | 0.018311 | -0.26093 | -0.17395 | -0.25635 | 0.036621 | 0.32501 | -0.14191 | 0.11444 | -0.077819 | 122.9095 | 122.6166 | 53.3615 | -123.0835 | 122.9141 | 122.7997 | 61.7523 | -123.1338
2459.0156 | 123.0011 | -51.503 | 71.4615 | -0.18326 | 0.010867 | 0.067823 | 0.072226 | 0.12736 | 0.00077755 | -0.0070773 | -0.29007 | -0.0086988 | 0.065119 | 0.058467 | 0.00549 | -0.012401 | 71.2418 | 71.4432 | 2.2247 | -51.6449 | 71.553 | -51.535 | -51.6541 | -51.1688 | 10.643 | -51.6129 | 71.5302 | 71.4203 | -51.7044 | -51.7548 | -0.032043 | -0.15106 | 0.091553 | 122.9462 | -0.14191 | 0.009156 | -0.21973 | -0.20142 | -0.25177 | 0.068664 | 0.33417 | -0.10986 | 0.14191 | -0.041199 | 123.056 | 122.7448 | 53.7277 | -123.1155 | 123.0331 | 122.9233 | 62.146 | -123.2162
2460.0156 | 123.1247 | -51.9791 | 70.8939 | -0.11459 | 0.0087307 | 0.071241 | 0.069235 | 0.12843 | -0.0011451 | -0.0060093 | 0.015106 | -0.011903 | 0.06106 | 0.057185 | 0.0042084 | -0.0096238 | 70.7153 | 70.9579 | 2.0874 | -52.1942 | 70.9488 | -52.1072 | -52.1805 | -51.6312 | 10.5515 | -52.0477 | 70.9167 | 70.8481 | -52.1942 | -52.2675 | -0.12817 | -0.20142 | 0.054932 | 122.937 | -0.21515 | -0.013733 | -0.17853 | -0.21515 | -0.28839 | 0.022888 | 0.3479 | -0.068664 | 0.21973 | -0.045777 | 122.9279 | 122.6944 | 54.0665 | -123.0743 | 122.8958 | 122.8271 | 62.5305 | -123.1613
2461.0156 | 123.1201 | -50.5463 | 72.3633 | 0.54916 | 0.011294 | 0.069105 | 0.070944 | 0.13057 | -0.0039221 | -0.0070773 | -0.10696 | -0.010408 | 0.062769 | 0.054835 | 0.0065582 | -0.012187 | 71.759 | 71.9833 | 2.6596 | -51.0269 | 72.0337 | -50.9583 | -50.9903 | -50.354 | 11.3663 | -50.7248 | 72.2855 | 72.2076 | -50.8392 | -50.853 | -0.41199 | -0.44403 | -0.32959 | 122.5296 | -0.48065 | -0.036622 | -0.60425 | -0.29297 | -0.3067 | -0.07782 | 0.19226 | -0.17853 | 0.12817 | -0.15564 | 122.58 | 122.3053 | 53.2059 | -123.3536 | 122.8317 | 122.7539 | 61.9125 | -123.2162
2462.0156 | 123.1155 | -50.8804 | 71.9788 | 2.8456 | 0.010013 | 0.069959 | 0.069876 | 0.12843 | 0.00056395 | -0.0068637 | -0.13748 | -0.0095532 | 0.062342 | 0.057398 | 0.007199 | -0.011974 | 71.9238 | 72.0978 | 2.7786 | -51.004 | 72.0978 | -50.9354 | -51.0406 | -50.5371 | 11.4532 | -51.0086 | 72.0657 | 71.9101 | -51.0406 | -51.1139 | -0.054932 | -0.16022 | 0.11902 | 122.9782 | -0.1236 | 0.036621 | -0.054932 | -0.16022 | -0.23346 | 0.086975 | 0.34332 | -0.12817 | 0.10529 | -0.068665 | 122.9782 | 122.8043 | 53.6591 | -123.0194 | 122.9462 | 122.7905 | 62.3337 | -123.0927
2463.0156 | 123.0194 | -51.3245 | 71.5988 | -0.22903 | 0.011081 | 0.070173 | 0.072012 | 0.13099 | 0.0020593 | -0.0051547 | -0.2214 | -0.0086988 | 0.063196 | 0.05633 | 0.007199 | -0.013255 | 71.2875 | 71.434 | 2.3163 | -51.622 | 71.5851 | -51.5305 | -51.6037 | -51.0544 | 11.348 | -51.5213 | 71.6721 | 71.5759 | -51.5533 | -51.5579 | -0.20599 | -0.27924 | -0.013733 | 122.7585 | -0.29755 | -0.01831 | -0.31128 | -0.22888 | -0.23346 | 0.073242 | 0.27008 | -0.19684 | 0.036621 | -0.022888 | 122.9095 | 122.612 | 53.6407 | -123.2025 | 122.9965 | 122.9004 | 62.6724 | -123.1567
2464.0156 | 123.1155 | -49.8596 | 72.9813 | -0.168 | 0.0070217 | 0.070814 | 0.069022 | 0.13057 | -0.0043495 | -0.0068637 | -1.2361 | -0.011049 | 0.06106 | 0.056544 | 0.0050628 | -0.010692 | 72.9263 | 73.1781 | 2.6459 | -49.8779 | 73.1689 | -49.8642 | -49.9649 | -49.4064 | 12.6617 | -49.9008 | 73.1781 | 73.0591 | -49.9741 | -50.061 | -0.004578 | -0.10529 | 0.18768 | 123.0377 | -0.018311 | 0.086975 | -0.054931 | -0.11444 | -0.20142 | 0.19684 | 0.45319 | -0.041199 | 0.16022 | 0.07782 | 123.0286 | 122.786 | 52.5055 | -122.9462 | 123.0377 | 122.9187 | 62.5214 | -123.0423
2465.0156 | 123.0377 | -49.9191 | 72.9904 | -0.25955 | 0.011935 | 0.071241 | 0.071372 | 0.13035 | 0.00013675 | -0.0062229 | -0.076446 | -0.0082716 | 0.061914 | 0.056758 | 0.0065582 | -0.012828 | 72.8027 | 73.0041 | 2.5589 | -50.1846 | 73.0637 | -50.0748 | -50.2075 | -49.6628 | 12.8906 | -50.1663 | 73.0637 | 72.9858 | -50.1205 | -50.148 | -0.15564 | -0.28839 | 0.073243 | 122.9233 | -0.2655 | 0.022889 | -0.18768 | -0.20142 | -0.22888 | 0.073243 | 0.25635 | -0.24719 | -0.018311 | -0.004577 | 122.9828 | 122.7219 | 52.478 | -123.1979 | 122.9828 | 122.905 | 62.8098 | -123.1384
2466.0156 | 123.1476 | -49.8093 | 73.0499 | -0.03067 | 0.0061673 | 0.070173 | 0.073294 | 0.12993 | -0.0041357 | -0.0070773 | 0.015106 | -0.011049 | 0.061487 | 0.055476 | 0.0067718 | -0.011546 | 72.8714 | 73.114 | 2.6321 | -50.0107 | 73.1552 | -49.91 | -49.9878 | -49.5575 | 13.1516 | -49.8871 | 73.0728 | 72.9767 | -50.0198 | -50.0839 | -0.10071 | -0.17853 | 0.10529 | 122.9233 | -0.20142 | -0.022888 | -0.17853 | -0.21057 | -0.27466 | 0.022888 | 0.25177 | -0.07782 | 0.19684 | -0.073242 | 122.9645 | 122.6807 | 52.4414 | -123.0377 | 122.8821 | 122.786 | 62.9608 | -123.1338
2467.0156 | 123.111 | -50.5325 | 72.3358 | 0.34317 | 0.0095853 | 0.069959 | 0.069235 | 0.12651 | -0.0019995 | -0.0072911 | -0.045929 | -0.011262 | 0.059564 | 0.05633 | 0.0067718 | -0.010051 | 72.2672 | 72.4503 | 2.2751 | -50.6699 | 72.5098 | -50.5692 | -50.647 | -50.2213 | 13.0783 | -50.7797 | 72.3679 | 72.2488 | -50.7523 | -50.798 | -0.036621 | -0.11444 | 0.17395 | 122.9828 | -0.13733 | -0.022888 | -0.068664 | -0.21973 | -0.2655 | 0.032044 | 0.31128 | -0.24719 | 0.018311 | -0.086975 | 123.0423 | 122.7997 | 52.8076 | -122.9828 | 122.9004 | 122.7814 | 63.6108 | -123.1338
2468.0156 | 123.1476 | -50.4364 | 72.4274 | -0.17563 | 0.0072355 | 0.070814 | 0.07009 | 0.12971 | -0.0060585 | -0.0081455 | -0.2214 | -0.011049 | 0.061701 | 0.053767 | 0.007199 | -0.011333 | 72.2992 | 71.8506 | 2.0645 | -50.8163 | 72.2672 | -50.7477 | -50.798 | -50.1114 | 13.5086 | -50.4639 | 72.5098 | 72.3679 | -50.6378 | -50.6927 | -0.31128 | -0.36163 | -0.16022 | 122.287 | -0.37994 | -0.01831 | -0.12817 | -0.20142 | -0.25635 | 0.082398 | 0.32501 | -0.027466 | 0.22888 | -0.059509 | 122.7036 | 122.7356 | 52.5009 | -123.2254 | 122.9462 | 122.8043 | 63.945 | -123.1201
2469.0156 | 123.0194 | -50.4227 | 72.5235 | -0.25192 | 0.011294 | 0.069105 | 0.073294 | 0.12587 | 0.0012047 | -0.0066501 | -0.45029 | -0.0099806 | 0.064264 | 0.054835 | 0.0076264 | -0.013683 | 72.5647 | 72.7524 | 2.3209 | -50.3494 | 72.8668 | -50.2258 | -50.3311 | -50.2533 | 12.9456 | -50.8575 | 72.5555 | 72.4136 | -50.7248 | -50.7477 | 0.19684 | 0.091552 | 0.34332 | 123.175 | 0.073242 | -0.01831 | 0.041198 | -0.30212 | -0.32501 | 0.032043 | 0.16937 | -0.43488 | -0.10986 | -0.10986 | 123.2895 | 122.9874 | 52.7435 | -122.8546 | 122.9782 | 122.8363 | 63.3682 | -123.2712
2470.0156 | 123.1796 | -50.0793 | 72.7432 | -0.015411 | 0.0091581 | 0.071241 | 0.070517 | 0.12864 | -0.0037085 | -0.0045139 | -0.099335 | -0.011049 | 0.058283 | 0.054621 | 0.0046356 | -0.013896 | 72.9401 | 73.1827 | 2.5223 | -49.9924 | 73.1277 | -49.91 | -49.9741 | -49.5895 | 13.4308 | -49.9741 | 72.9996 | 72.908 | -50.1755 | -50.2579 | 0.16937 | 0.10529 | 0.38452 | 123.262 | 0.086975 | -0.018311 | 0.19684 | -0.09613 | -0.17853 | 0.25635 | 0.48981 | 0.10529 | 0.28381 | 0.16479 | 123.2071 | 123.0194 | 52.6016 | -122.7173 | 123.0789 | 122.9874 | 63.5101 | -123.0011
2471.0156 | 123.0515 | -50.2396 | 72.6883 | -0.23666 | 0.0074491 | 0.071455 | 0.070944 | 0.12822 | -0.00093145 | -0.0066501 | -0.17563 | -0.0097668 | 0.061487 | 0.054408 | 0.0093354 | -0.013255 | 72.5052 | 72.7203 | 2.5177 | -50.3815 | 72.757 | -50.3128 | -50.4044 | -49.942 | 13.0554 | -50.3494 | 72.7295 | 72.6151 | -50.4501 | -50.4959 | -0.073242 | -0.1648 | 0.068665 | 122.9599 | -0.14191 | 0.022888 | -0.1831 | -0.21057 | -0.25635 | 0.041199 | 0.29755 | -0.10986 | 0.14648 | -0.073242 | 122.9965 | 122.7448 | 52.7573 | -123.0927 | 122.9691 | 122.8546 | 63.295 | -123.1842
2472.0156 | 123.143 | -50.0198 | 72.821 | -0.076447 | 0.0036039 | 0.069532 | 0.068594 | 0.12886 | -0.0039221 | -0.0083591 | 0.076141 | -0.012117 | 0.062128 | 0.05868 | 0.0067718 | -0.011119 | 72.5555 | 72.8073 | 2.4765 | -50.2853 | 72.789 | -50.1938 | -50.2487 | -49.4751 | 13.7375 | -50.0336 | 73.0225 | 72.876 | -50.1617 | -50.2304 | -0.17395 | -0.22888 | -0.032044 | 122.8271 | -0.2655 | -0.036621 | -0.2655 | -0.14191 | -0.21057 | 0.20142 | 0.54474 | -0.013733 | 0.19684 | 0.054932 | 122.8088 | 122.5754 | 52.4963 | -123.0698 | 123.0423 | 122.8958 | 63.7573 | -123.0515
2473.0156 | 123.1155 | -49.4934 | 73.3841 | -0.18326 | 0.0068081 | 0.069105 | 0.071158 | 0.12993 | 0.00035035 | -0.0081455 | -0.12222 | -0.0097668 | 0.062342 | 0.055903 | 0.0059174 | -0.013042 | 73.1964 | 73.4116 | 2.5772 | -49.704 | 73.3841 | -49.6399 | -49.6994 | -49.1776 | 14.2731 | -49.5483 | 73.4161 | 73.3292 | -49.6948 | -49.7406 | -0.14648 | -0.20599 | 0 | 122.905 | -0.21057 | -0.004577 | -0.18768 | -0.20142 | -0.24719 | 0.032044 | 0.31586 | -0.054932 | 0.19226 | -0.054931 | 122.8775 | 122.6898 | 52.0706 | -123.0835 | 122.9095 | 122.8226 | 63.7665 | -123.1247
2474.0156 | 123.1064 | -50.322 | 72.5372 | 0.0074768 | 0.0053129 | 0.067823 | 0.067526 | 0.12608 | -0.0030677 | -0.0079319 | 0.060883 | -0.0082716 | 0.061701 | 0.057185 | 0.0050628 | -0.010905 | 72.5189 | 72.7158 | 2.3209 | -50.3769 | 72.7982 | -50.3036 | -50.4089 | -50.0519 | 13.9297 | -50.4501 | 72.5967 | 72.4731 | -50.5692 | -50.6058 | 0.01831 | -0.086976 | 0.26093 | 123.0377 | -0.054932 | 0.032044 | -0.01831 | -0.24719 | -0.28381 | 0.05951 | 0.27008 | -0.12817 | 0.15564 | -0.064086 | 123.1201 | 122.8409 | 52.6428 | -122.9462 | 122.9187 | 122.7951 | 64.2517 | -123.143
2475.0156 | 123.1476 | -50.1709 | 72.6791 | -0.19089 | 0.0070217 | 0.069532 | 0.072226 | 0.13163 | -0.0026405 | -0.0019505 | 0.037995 | -0.010835 | 0.063196 | 0.055476 | 0.00549 | -0.01176 | 72.0703 | 72.7066 | 2.449 | -50.4776 | 72.6288 | -50.3906 | -50.473 | -49.8093 | 14.328 | -50.3403 | 72.702 | 72.6151 | -50.3906 | -50.4593 | -0.21973 | -0.30212 | -0.050354 | 122.8775 | -0.3067 | -0.004578 | -0.60883 | -0.21973 | -0.28839 | 0.022888 | 0.36163 | -0.16937 | 0.11902 | -0.064087 | 122.7997 | 122.2412 | 52.6199 | -123.1522 | 122.8729 | 122.7859 | 64.4989 | -123.1384
2476.0156 | 123.1613 | -50.9445 | 71.8918 | -0.061188 | 0.0057401 | 0.068678 | 0.070731 | 0.12693 | -0.0022131 | -0.0049411 | -0.00015237 | -0.0089124 | 0.05871 | 0.056971 | 0.0057038 | -0.012614 | 71.7499 | 71.9925 | 2.2751 | -51.1047 | 72.0337 | -50.9903 | -51.0773 | -50.5783 | 13.9938 | -51.1093 | 71.9925 | 71.8506 | -51.1459 | -51.1826 | -0.045776 | -0.13275 | 0.14191 | 122.937 | -0.16022 | -0.027465 | -0.14191 | -0.20142 | -0.23804 | 0.10071 | 0.36621 | -0.16479 | 0.073242 | -0.041199 | 122.9782 | 122.6944 | 53.2196 | -122.9691 | 122.937 | 122.7951 | 64.9384 | -123.0743
2477.0156 | 123.1064 | -51.3199 | 71.5027 | -0.00015269 | 0.0080899 | 0.06825 | 0.071158 | 0.12843 | -0.00050425 | -0.0068637 | -0.18326 | -0.0093396 | 0.059992 | 0.056544 | 0.00784 | -0.012828 | 71.1639 | 71.3333 | 2.0782 | -51.8463 | 71.315 | -51.7227 | -51.828 | -51.0452 | 14.0671 | -51.4893 | 71.4935 | 71.3791 | -51.6129 | -51.6129 | -0.40283 | -0.50812 | -0.18768 | 122.6532 | -0.52643 | -0.01831 | -0.33875 | -0.29297 | -0.29297 | -0.009156 | 0.27466 | -0.16937 | 0.1236 | -0.1236 | 122.6349 | 122.4838 | 53.3981 | -123.3307 | 122.8134 | 122.699 | 65.387 | -123.1155
2478.0156 | 123.143 | -50.885 | 71.9696 | -0.0383 | 0.0097989 | 0.068678 | 0.06774 | 0.12822 | -0.00093145 | -0.0070773 | 0.0074766 | -0.0093396 | 0.060846 | 0.056971 | 0.0069854 | -0.013042 | 71.9009 | 72.0795 | 2.0554 | -51.0681 | 72.1481 | -50.9399 | -51.0452 | -50.4913 | 14.2227 | -51.0132 | 72.0383 | 71.9559 | -51.0773 | -51.1139 | -0.054931 | -0.16022 | 0.17853 | 122.9645 | -0.1831 | -0.022888 | -0.068664 | -0.19226 | -0.22888 | 0.068665 | 0.39368 | -0.12817 | 0.10071 | -0.013732 | 123.0331 | 122.786 | 52.9404 | -123.0148 | 122.9233 | 122.8409 | 65.1077 | -123.0835
2479.0156 | 123.143 | -49.8734 | 73.0225 | -0.21378 | 0.0074491 | 0.070173 | 0.069235 | 0.12715 | 0.00013675 | -0.0057957 | 2.8761 | -0.0076306 | 0.06106 | 0.057612 | 0.0076264 | -0.012614 | 72.8073 | 73.0316 | 2.3712 | -50.1205 | 72.9813 | -50.0519 | -50.1572 | -49.8184 | 14.5157 | -50.1434 | 72.821 | 72.7615 | -50.2213 | -50.2075 | -0.17853 | -0.28381 | -0.041199 | 122.905 | -0.24719 | 0.036622 | -0.21515 | -0.3479 | -0.33417 | -0.20142 | 0.054932 | -0.27008 | 0.064087 | -0.26093 | 122.8546 | 122.6807 | 52.2446 | -123.1796 | 122.6944 | 122.6349 | 64.389 | -123.23
2480.0156 | 123.0972 | -49.6811 | 73.2147 | 0.13718 | 0.0087307 | 0.069959 | 0.068167 | 0.128 | -0.0013587 | -0.0049411 | 0.14481 | -0.011476 | 0.06106 | 0.058467 | 0.0067718 | -0.013469 | 73.2193 | 73.407 | 2.4445 | -49.736 | 73.4573 | -49.585 | -49.6902 | -49.3561 | 14.3738 | -49.9649 | 73.2742 | 73.1552 | -49.8596 | -49.8871 | 0.09613 | -0.009156 | 0.24261 | 123.0881 | -0.054932 | -0.045776 | 0.004577 | -0.17853 | -0.20599 | 0.059509 | 0.32501 | -0.28381 | -0.07782 | -0.05951 | 123.1384 | 122.9004 | 52.1255 | -122.905 | 122.9553 | 122.8363 | 64.0549 | -123.1018
2481.0156 | 123.1567 | -49.9786 | 72.8897 | -0.023041 | 0.0057401 | 0.070814 | 0.071799 | 0.12928 | -0.0024269 | -0.0060093 | -0.023041 | -0.008058 | 0.062982 | 0.057826 | 0.00784 | -0.013042 | 72.6517 | 72.8165 | 2.5269 | -50.2716 | 72.9218 | -50.148 | -50.2396 | -49.6902 | 14.5248 | -50.2899 | 72.8989 | 72.789 | -50.2075 | -50.2441 | -0.16937 | -0.26093 | 0.032044 | 122.7951 | -0.29297 | -0.032043 | -0.23804 | -0.22888 | -0.2655 | 0.009156 | 0.28839 | -0.31128 | -0.045776 | -0.10071 | 122.9004 | 122.6303 | 52.5055 | -123.1293 | 122.8775 | 122.7676 | 64.5035 | -123.1338
2482.0156 | 123.1293 | -50.8759 | 71.9879 | 0.022736 | 0.0059537 | 0.069319 | 0.071585 | 0.12928 | -0.0017859 | -0.0083591 | -0.023041 | -0.011049 | 0.061487 | 0.055049 | 0.0057038 | -0.013255 | 71.7133 | 71.9147 | 2.1698 | -51.1688 | 72.0108 | -51.0681 | -51.1322 | -50.5417 | 13.9801 | -51.004 | 72.0428 | 71.9284 | -51.1047 | -51.1185 | -0.19226 | -0.25635 | 0.022888 | 122.7905 | -0.29297 | -0.036621 | -0.27466 | -0.22888 | -0.24262 | 0.054932 | 0.33417 | -0.12817 | 0.11444 | -0.059509 | 122.8867 | 122.5891 | 53.0457 | -123.1201 | 122.9187 | 122.8043 | 64.856 | -123.1064
2483.0156 | 123.1338 | -50.6836 | 72.1756 | -0.11459 | 0.0068081 | 0.069959 | 0.071158 | 0.12907 | -7.6852e-05 | -0.0064365 | -0.11459 | -0.011689 | 0.061273 | 0.054835 | 0.0080536 | -0.011546 | 72.1298 | 72.3267 | 2.3483 | -50.853 | 72.2672 | -50.7889 | -50.8301 | -50.3128 | 14.7125 | -50.5966 | 72.3084 | 72.1756 | -50.8759 | -50.9171 | -0.10529 | -0.14648 | 0.091553 | 123.0103 | -0.16937 | -0.022888 | -0.045776 | -0.19226 | -0.23346 | 0.13275 | 0.37079 | 0.086975 | 0.32043 | 0 | 122.9507 | 122.8134 | 53.0319 | -123.0057 | 122.9919 | 122.8592 | 65.3961 | -123.0927
2484.0156 | 123.111 | -50.885 | 72.02 | -0.015411 | 0.0085171 | 0.069105 | 0.067954 | 0.12758 | -0.00050425 | -0.0087863 | 0.083771 | -0.012544 | 0.061487 | 0.058039 | 0.0065582 | -0.012828 | 72.1298 | 72.0474 | 2.1057 | -50.9033 | 72.2351 | -50.798 | -50.9079 | -50.5554 | 14.36 | -51.1459 | 72.0795 | 71.9467 | -51.0818 | -51.1459 | 0.086975 | -0.022888 | 0.21515 | 122.9324 | -0.01831 | 0.004578 | 0.10986 | -0.19684 | -0.26093 | 0.05951 | 0.32959 | -0.26093 | 0 | -0.073242 | 123.1201 | 123.0148 | 52.9907 | -122.9279 | 122.9645 | 122.8317 | 65.2451 | -123.1659
2485.0156 | 123.1155 | -51.4572 | 71.3379 | -0.061188 | 0.0074491 | 0.070387 | 0.069876 | 0.12843 | -0.0015723 | -0.0053683 | 0.015106 | -0.010408 | 0.060846 | 0.058039 | 0.0076264 | -0.012187 | 71.4111 | 71.5485 | 1.9089 | -51.6037 | 71.608 | -51.4206 | -51.5396 | -51.1047 | 14.2227 | -51.6586 | 71.434 | 71.3242 | -51.6815 | -51.7181 | 0.036621 | -0.082398 | 0.27008 | 123.0057 | -0.14648 | -0.064087 | 0.073242 | -0.22431 | -0.26093 | 0.09613 | 0.35248 | -0.20142 | 0.05951 | -0.013733 | 123.0652 | 122.8683 | 53.3661 | -122.8775 | 122.8912 | 122.7814 | 65.6799 | -123.056
2486.0156 | 123.0469 | -52.2766 | 70.5688 | 0.18295 | 0.0078763 | 0.069319 | 0.072653 | 0.12779 | -0.00050425 | -0.0072911 | 0.0914 | -0.010621 | 0.061273 | 0.056117 | 0.006131 | -0.011546 | 70.4453 | 70.61 | 1.5472 | -52.5284 | 70.6696 | -52.3544 | -52.4551 | -51.8921 | 13.7192 | -52.3865 | 70.7108 | 70.5826 | -52.4506 | -52.5101 | -0.07782 | -0.17853 | 0.10071 | 122.8867 | -0.25177 | -0.073242 | -0.1236 | -0.17395 | -0.23346 | 0.14191 | 0.38452 | -0.10986 | 0.1236 | 0.013733 | 122.9462 | 122.7219 | 53.8239 | -123.024 | 122.9874 | 122.8592 | 65.9958 | -123.0789
2487.0156 | 123.1293 | -51.5579 | 71.3287 | -1.4497 | 0.0078763 | 0.071027 | 0.066458 | 0.12843 | -0.0017859 | -0.0085727 | 0.060883 | -0.010194 | 0.061701 | 0.05398 | 0.00549 | -0.012614 | 71.1914 | 71.3928 | 1.6571 | -51.7044 | 71.4569 | -51.5808 | -51.7136 | -51.2604 | 14.1632 | -51.741 | 71.3379 | 71.2418 | -51.7776 | -51.7914 | -0.022889 | -0.15564 | 0.12817 | 122.9507 | -0.14649 | 0.009155 | -0.13733 | -0.21973 | -0.23346 | 0.009156 | 0.29755 | -0.18311 | 0.050354 | -0.086975 | 123.0148 | 122.7493 | 53.215 | -123.0423 | 122.8958 | 122.7997 | 65.7211 | -123.1201
2488.0156 | 123.1201 | -50.8438 | 72.0154 | 0.19058 | 0.011935 | 0.069532 | 0.069663 | 0.12886 | 0.0012047 | -0.0055821 | 0.13718 | -0.010621 | 0.064264 | 0.055903 | 0.00784 | -0.013469 | 71.9147 | 72.0932 | 1.9638 | -51.059 | 72.0657 | -50.9583 | -51.0727 | -50.4547 | 14.9643 | -50.9079 | 72.084 | 71.9559 | -51.0361 | -51.0773 | -0.11444 | -0.22888 | 0.050354 | 122.937 | -0.21515 | 0.013733 | -0.10071 | -0.19226 | -0.23346 | 0.068664 | 0.3891 | -0.064087 | 0.16937 | -0.059509 | 122.9095 | 122.7585 | 52.8076 | -123.0881 | 122.9279 | 122.7997 | 65.8081 | -123.0927
2489.0156 | 123.0835 | -50.8667 | 72.0932 | -0.17563 | 0.016635 | 0.067396 | 0.071799 | 0.13014 | 0.0054773 | -0.0062229 | -0.17563 | -0.0065626 | 0.061701 | 0.057185 | 0.0091216 | -0.015605 | 72.0795 | 72.1161 | 1.9089 | -50.9995 | 72.2488 | -50.8621 | -50.9445 | -50.4776 | 14.4333 | -51.0956 | 72.1527 | 72.0383 | -51.0498 | -51.1002 | 0.004577 | -0.07782 | 0.15564 | 122.9828 | -0.13275 | -0.054932 | -0.013733 | -0.18311 | -0.23346 | 0.059509 | 0.3891 | -0.22888 | 0.004578 | -0.054932 | 123.1155 | 122.9462 | 52.7756 | -123.0377 | 123.0194 | 122.905 | 65.3 | -123.1934
2490.0156 | 123.2162 | -51.0269 | 71.8277 | 0.16006 | 0.0091581 | 0.069105 | 0.068808 | 0.13014 | -0.0030677 | -0.0047275 | 0.09903 | -0.0095532 | 0.059564 | 0.05633 | 0.00549 | -0.010265 | 71.9971 | 72.1802 | 1.8173 | -50.9354 | 72.2397 | -50.8255 | -50.8987 | -50.6241 | 14.7308 | -51.2512 | 72.02 | 71.8781 | -51.1917 | -51.2421 | 0.20142 | 0.12817 | 0.41199 | 123.2071 | 0.091553 | -0.036621 | 0.16937 | -0.16479 | -0.21515 | 0.19226 | 0.40283 | -0.2243 | -0.009156 | 0.050354 | 123.2666 | 123.024 | 52.8442 | -122.7264 | 123.0469 | 122.905 | 65.7578 | -123.0698
2491.0156 | 123.1613 | -50.4547 | 72.4091 | -0.061188 | 0.0070217 | 0.069532 | 0.070517 | 0.12971 | -0.0026405 | -0.0070773 | 0.060883 | -0.0097668 | 0.058496 | 0.055476 | 0.0059174 | -0.011974 | 72.2488 | 72.4869 | 1.8906 | -50.647 | 72.5006 | -50.5371 | -50.6195 | -50.116 | 14.8727 | -50.4822 | 72.5006 | 72.3587 | -50.679 | -50.7111 | -0.082397 | -0.16479 | 0.091552 | 122.9416 | -0.19226 | -0.027466 | -0.16022 | -0.2243 | -0.25635 | 0.091552 | 0.33875 | -0.027466 | 0.22888 | -0.050354 | 122.9553 | 122.7036 | 52.3453 | -123.0286 | 122.9553 | 122.8134 | 65.3275 | -123.1201
2492.0156 | 123.1247 | -50.7523 | 72.1115 | 0.14481 | 0.0074491 | 0.070173 | 0.069235 | 0.12907 | -0.0019995 | -0.0055821 | 0.15244 | -0.0099806 | 0.062982 | 0.056971 | 0.0074126 | -0.012614 | 71.8826 | 72.0566 | 1.7761 | -51.0864 | 72.1069 | -50.9125 | -51.0086 | -50.3494 | 15.0925 | -50.8759 | 72.1985 | 72.0657 | -50.9628 | -50.9857 | -0.16022 | -0.25635 | -0.004577 | 122.8088 | -0.33417 | -0.07782 | -0.22888 | -0.21057 | -0.23346 | 0.086975 | 0.40283 | -0.1236 | 0.10986 | -0.045776 | 122.8592 | 122.6349 | 52.5284 | -123.1201 | 122.9507 | 122.818 | 65.8447 | -123.0972
2493.0156 | 123.111 | -50.8392 | 72.0337 | 0.0074768 | 0.0072355 | 0.0706 | 0.068594 | 0.13057 | -0.0022131 | -0.0057957 | 0.0074766 | -0.0097668 | 0.060633 | 0.057612 | 0.0050628 | -0.013042 | 71.8781 | 72.0428 | 1.8127 | -51.0498 | 72.1207 | -50.9308 | -51.0086 | -50.4501 | 14.6713 | -50.9079 | 72.1115 | 71.965 | -51.0406 | -51.0818 | -0.091553 | -0.16937 | 0.086976 | 122.8821 | -0.21057 | -0.041199 | -0.15564 | -0.20142 | -0.24262 | 0.07782 | 0.3891 | -0.068665 | 0.17395 | -0.068664 | 122.9599 | 122.7173 | 52.652 | -123.0423 | 122.9507 | 122.8043 | 65.5106 | -123.1155
2494.0156 | 123.0057 | -50.8255 | 72.084 | -0.18326 | 0.013858 | 0.067182 | 0.07244 | 0.12715 | 0.0046227 | -0.0062229 | -0.90042 | -0.0069898 | 0.064264 | 0.058039 | 0.00784 | -0.014323 | 71.8689 | 72.0016 | 1.8127 | -51.0178 | 72.1802 | -50.9079 | -51.004 | -50.4364 | 14.5615 | -50.9445 | 72.2168 | 72.084 | -51.0361 | -51.0452 | -0.082398 | -0.17853 | 0.096131 | 122.8271 | -0.19226 | -0.013733 | -0.21515 | -0.21057 | -0.21973 | 0.13275 | 0.3891 | -0.11902 | 0.10071 | 0 | 123.0057 | 122.6944 | 52.6382 | -123.0881 | 123.0423 | 122.9095 | 65.387 | -123.1293
2495.0156 | 123.1018 | -50.7889 | 72.0291 | 0.12192 | 0.0095853 | 0.070814 | 0.070303 | 0.12843 | -0.00029045 | -0.0034457 | 0.12192 | -0.0095532 | 0.060633 | 0.057185 | 0.0063446 | -0.011333 | 71.9833 | 72.2168 | 1.8677 | -50.9171 | 72.2626 | -50.7751 | -50.8621 | -50.3906 | 14.9002 | -50.8896 | 72.1893 | 72.0886 | -50.9766 | -51.0452 | 0.013733 | -0.073243 | 0.23346 | 123.0057 | -0.12817 | -0.054931 | -0.045777 | -0.18768 | -0.25635 | 0.16022 | 0.39825 | -0.10071 | 0.15564 | 0.059509 | 123.0515 | 122.7722 | 52.6566 | -122.8912 | 122.9782 | 122.8775 | 65.6891 | -123.0743
2496.0156 | 123.0698 | -51.3748 | 71.4569 | 0.12192 | 0.0095853 | 0.069532 | 0.071158 | 0.13014 | -0.00071785 | -0.0055821 | 0.13718 | -0.010408 | 0.062128 | 0.054194 | 0.007199 | -0.010692 | 71.2738 | 71.4523 | 1.4694 | -51.6541 | 71.5302 | -51.5305 | -51.6174 | -51.0452 | 14.4653 | -51.5808 | 71.5118 | 71.4066 | -51.6083 | -51.6632 | -0.15564 | -0.24262 | 0.073242 | 122.8271 | -0.27924 | -0.036621 | -0.1831 | -0.23346 | -0.28839 | 0.054932 | 0.32959 | -0.20599 | 0.082397 | -0.050354 | 122.905 | 122.6486 | 52.8442 | -123.0743 | 122.8867 | 122.7814 | 65.8401 | -123.1201
2497.0156 | 123.1567 | -50.6836 | 72.1939 | -0.03067 | 0.010013 | 0.068678 | 0.07009 | 0.12822 | -0.0034949 | -0.0079319 | 0.022736 | -0.010835 | 0.061914 | 0.054194 | 0.0063446 | -0.013469 | 72.7249 | 72.6883 | 1.4786 | -50.5463 | 72.8073 | -50.3082 | -50.441 | -50.2167 | 14.8178 | -51.1047 | 72.3587 | 72.1893 | -50.8667 | -50.8987 | 0.37537 | 0.24262 | 0.6134 | 123.3719 | 0.13733 | -0.10529 | 0.53101 | -0.1831 | -0.21515 | 0.16479 | 0.46692 | -0.42114 | -0.20599 | -0.004578 | 123.4909 | 123.4085 | 52.1622 | -122.6349 | 123.0423 | 122.8729 | 65.5014 | -123.0927
2498.0156 | 123.0743 | -51.4069 | 71.4386 | 0.14481 | 0.012149 | 0.069746 | 0.071799 | 0.12864 | -0.00093145 | -0.0064365 | 0.19058 | -0.0093396 | 0.060846 | 0.054835 | 0.0086944 | -0.011119 | 71.4386 | 71.6034 | 1.6342 | -51.5305 | 71.6583 | -51.384 | -51.4343 | -50.9399 | 14.6896 | -51.5579 | 71.6125 | 71.4661 | -51.5259 | -51.622 | 0.022888 | -0.027466 | 0.21973 | 123.0103 | -0.1236 | -0.096131 | 0 | -0.11902 | -0.21515 | 0.17395 | 0.46692 | -0.15106 | 0.064087 | 0.027465 | 123.0652 | 122.8455 | 53.0411 | -122.8729 | 123.0194 | 122.8729 | 66.0965 | -123.0606
2499.0156 | 123.024 | -50.8621 | 72.0978 | -0.25955 | 0.011081 | 0.068678 | 0.073721 | 0.12993 | 0.00056395 | -0.0047275 | -1.4116 | -0.0084852 | 0.064478 | 0.058894 | 0.0067718 | -0.012828 | 71.8369 | 71.9742 | 1.6113 | -51.123 | 72.1252 | -50.9995 | -51.0727 | -50.5234 | 14.8224 | -50.9399 | 72.1527 | 72.0428 | -51.0498 | -51.1002 | -0.13733 | -0.21057 | 0.027466 | 122.8363 | -0.26093 | -0.050354 | -0.26093 | -0.18768 | -0.23804 | 0.054932 | 0.33875 | -0.077819 | 0.16022 | -0.054931 | 122.9874 | 122.699 | 52.4734 | -123.1705 | 123.0148 | 122.905 | 65.6845 | -123.1979
2500.0156 | 123.1247 | -51.0132 | 71.7728 | 0.13718 | 0.011294 | 0.071241 | 0.071585 | 0.13377 | -0.0019995 | -0.0064365 | 0.2211 | -0.0086988 | 0.065332 | 0.056758 | 0.0067718 | -0.013896 | 71.9971 | 72.2122 | 1.7944 | -50.9125 | 72.2076 | -50.8026 | -50.8896 | -50.4913 | 14.859 | -51.0315 | 72.0154 | 71.9284 | -51.1139 | -51.1917 | 0.21057 | 0.1236 | 0.43488 | 123.2254 | 0.10071 | -0.022889 | 0.2243 | -0.10071 | -0.17853 | 0.24262 | 0.52185 | -0.01831 | 0.16022 | 0.15564 | 123.2208 | 123.0103 | 52.8076 | -122.6624 | 123.0286 | 122.9416 | 65.8722 | -122.9645
2501.0156 | 123.0972 | -51.8829 | 70.9763 | 0.14481 | 0.0089443 | 0.071027 | 0.066672 | 0.12544 | -0.0011451 | -0.0045139 | 0.16006 | -0.0086988 | 0.062982 | 0.057612 | 0.0046356 | -0.011333 | 71.5118 | 71.6721 | 1.6983 | -51.4389 | 71.7545 | -51.297 | -51.4435 | -51.6403 | 14.0579 | -52.4277 | 70.9717 | 70.8755 | -52.1484 | -52.2034 | 0.58594 | 0.43945 | 0.7782 | 123.555 | 0.44403 | 0.004577 | 0.53558 | -0.2655 | -0.32043 | -0.004577 | 0.24262 | -0.54474 | -0.2243 | -0.10071 | 123.6374 | 123.3948 | 53.5812 | -122.4197 | 122.8546 | 122.7585 | 65.9409 | -123.1796
2502.0156 | 123.0606 | -51.503 | 71.3242 | 0.20584 | 0.014071 | 0.069319 | 0.070731 | 0.13014 | 0.0027001 | -0.0043003 | 0.16006 | -0.008058 | 0.061273 | 0.056117 | 0.0091216 | -0.013255 | 71.5302 | 71.6721 | 1.7395 | -51.4435 | 71.7133 | -51.3382 | -51.4252 | -51.0818 | 14.5569 | -51.6724 | 71.5027 | 71.3608 | -51.6861 | -51.7364 | 0.16479 | 0.07782 | 0.3891 | 123.175 | 0.05951 | -0.01831 | 0.20599 | -0.1831 | -0.23346 | 0.17853 | 0.42114 | -0.16937 | 0.064087 | 0.036621 | 123.2162 | 123.0331 | 53.2425 | -122.7493 | 123.0057 | 122.8638 | 66.0599 | -123.0606
2503.0156 | 123.1064 | -53.4851 | 69.3466 | 0.083771 | 0.0087307 | 0.069746 | 0.067099 | 0.12822 | -0.0034949 | -0.0066501 | 0.060883 | -0.0089124 | 0.060419 | 0.056544 | 0.0048492 | -0.010692 | 69.2047 | 69.3695 | 1.4145 | -53.7231 | 69.429 | -53.6224 | -53.6728 | -53.1052 | 13.5132 | -53.6545 | 69.4473 | 69.342 | -53.6911 | -53.7323 | -0.13733 | -0.18768 | 0.082397 | 122.8546 | -0.23804 | -0.050354 | -0.14191 | -0.20599 | -0.24719 | 0.10071 | 0.37994 | -0.16937 | 0.07782 | -0.004578 | 122.9141 | 122.6898 | 54.8996 | -123.0194 | 122.9324 | 122.8271 | 66.9983 | -123.0789
2504.0156 | 123.056 | -53.5263 | 69.4061 | -0.22141 | 0.014926 | 0.06825 | 0.072012 | 0.12843 | 0.0035547 | -0.0053683 | -0.15274 | -0.0072034 | 0.063196 | 0.058467 | 0.0080536 | -0.01411 | 69.1635 | 69.2642 | 1.3 | -53.7872 | 69.4473 | -53.6865 | -53.7735 | -53.1921 | 13.6688 | -53.7415 | 69.4611 | 69.3512 | -53.7277 | -53.7827 | -0.16022 | -0.24719 | 0.041199 | 122.7905 | -0.26093 | -0.013732 | -0.24262 | -0.20142 | -0.25635 | 0.054932 | 0.33417 | -0.21515 | 0.041199 | -0.054932 | 122.9736 | 122.6898 | 54.8264 | -123.1796 | 122.9874 | 122.8775 | 67.1951 | -123.1888
2505.0156 | 123.1018 | -52.5101 | 70.3629 | 0.060882 | 0.0093717 | 0.0706 | 0.068381 | 0.12736 | -0.0028541 | -0.0066501 | 0.2211 | -0.011903 | 0.060419 | 0.055476 | 0.0063446 | -0.011974 | 70.2347 | 70.491 | 1.4694 | -52.8259 | 70.4407 | -52.6199 | -52.7115 | -52.1667 | 14.1357 | -52.5558 | 70.3857 | 70.3262 | -52.7344 | -52.7573 | -0.10986 | -0.20142 | 0.07782 | 123.0011 | -0.31586 | -0.11444 | -0.12817 | -0.2243 | -0.24719 | 0.022888 | 0.34332 | -0.045776 | 0.20142 | -0.036621 | 122.9507 | 122.7448 | 53.9795 | -123.0743 | 122.8958 | 122.8363 | 66.6458 | -123.1201
2506.0156 | 123.1155 | -52.7481 | 70.047 | 0.15244 | 0.011081 | 0.066114 | 0.07009 | 0.13121 | -0.00029045 | -0.0040867 | 0.22873 | -0.0082716 | 0.06106 | 0.056758 | 0.008908 | -0.013255 | 69.9875 | 70.1569 | 1.4786 | -52.9999 | 70.1431 | -52.8854 | -52.9678 | -52.3407 | 14.2776 | -52.9129 | 70.166 | 70.0562 | -52.9587 | -53.009 | -0.13733 | -0.21973 | 0.09613 | 122.905 | -0.25177 | -0.032044 | -0.059509 | -0.21057 | -0.26093 | 0.11902 | 0.40741 | -0.16479 | 0.09613 | 0.009155 | 122.8912 | 122.7356 | 54.2267 | -123.0148 | 122.9141 | 122.8043 | 67.0258 | -123.056
2507.0156 | 123.1064 | -52.7069 | 70.1523 | 0.076141 | 0.0083035 | 0.069746 | 0.070303 | 0.12758 | -0.0034949 | -0.0053683 | 0.10666 | -0.0099806 | 0.060633 | 0.055476 | 0.0057038 | -0.014751 | 69.841 | 69.9966 | 1.4694 | -53.0823 | 70.0836 | -52.9633 | -53.0411 | -52.4368 | 14.3051 | -52.9495 | 70.1294 | 70.0333 | -52.977 | -53.0228 | -0.25635 | -0.33417 | -0.068665 | 122.7036 | -0.37537 | -0.041198 | -0.31128 | -0.27008 | -0.31586 | -0.022888 | 0.27008 | -0.24261 | 0.073242 | -0.11902 | 122.7905 | 122.5479 | 54.1763 | -123.1934 | 122.8363 | 122.7402 | 67.012 | -123.175
2508.0156 | 123.1522 | -53.2104 | 69.6396 | 0.2211 | 0.015994 | 0.067823 | 0.069449 | 0.13035 | 0.0014185 | -0.0053683 | 0.18295 | -0.0099806 | 0.063196 | 0.055262 | 0.0084808 | -0.012614 | 69.6945 | 69.7861 | 1.4236 | -53.27 | 69.8547 | -53.1692 | -53.2745 | -52.803 | 13.9709 | -53.4943 | 69.6899 | 69.5435 | -53.4531 | -53.4943 | 0.041199 | -0.064087 | 0.21515 | 122.9965 | -0.059509 | 0.004578 | 0.054932 | -0.24262 | -0.28381 | 0.050354 | 0.40741 | -0.28381 | 0 | -0.09613 | 123.0652 | 122.905 | 54.6341 | -122.9141 | 122.9004 | 122.7539 | 67.1814 | -123.1338
2509.0156 | 123.2574 | -52.977 | 69.9188 | -0.13748 | 0.0091581 | 0.06761 | 0.069449 | 0.12672 | -0.0024269 | -0.0047275 | -0.084076 | -0.010621 | 0.065119 | 0.059107 | 0.0059174 | -0.012828 | 69.9554 | 70.1706 | 1.5335 | -52.9633 | 70.1294 | -52.9083 | -53.0045 | -52.565 | 14.2593 | -53.1876 | 69.9234 | 69.8364 | -53.1967 | -53.2516 | 0.068665 | -0.027466 | 0.21057 | 123.1476 | 0.013733 | 0.041199 | 0.036621 | -0.21973 | -0.27466 | 0.004578 | 0.41199 | -0.21057 | 0.064087 | -0.082397 | 123.1064 | 122.9324 | 54.5105 | -122.9233 | 122.9004 | 122.8134 | 67.2363 | -123.1705
2510.0156 | 123.1293 | -52.0615 | 70.7703 | 0.10666 | 0.0097989 | 0.068037 | 0.071799 | 0.12886 | 0.00056395 | -0.0053683 | 0.18295 | -0.0099806 | 0.065119 | 0.057612 | 0.0093354 | -0.012401 | 70.6741 | 70.8298 | 1.4969 | -52.3499 | 70.8298 | -52.2079 | -52.3087 | -51.7044 | 14.7629 | -52.1805 | 70.816 | 70.7108 | -52.2812 | -52.3361 | -0.14648 | -0.24719 | 0.059509 | 122.8912 | -0.28839 | -0.041199 | -0.096131 | -0.21973 | -0.27466 | 0.045776 | 0.35705 | -0.11902 | 0.15564 | -0.05951 | 122.8912 | 122.7356 | 53.5583 | -123.0789 | 122.8775 | 122.7722 | 66.8243 | -123.1064
2511.0156 | 123.0789 | -52.9724 | 69.9005 | 0.037994 | 0.0083035 | 0.069746 | 0.070303 | 0.12886 | -0.0013587 | -0.0068637 | 0.80856 | -0.0082716 | 0.063196 | 0.057826 | 0.0065582 | -0.010265 | 69.7952 | 69.9875 | 1.3779 | -53.1281 | 70.0562 | -53.0228 | -53.1418 | -52.6108 | 14.2319 | -53.1372 | 69.9554 | 69.8456 | -53.1738 | -53.2471 | -0.050354 | -0.16937 | 0.15564 | 122.9599 | -0.15564 | 0.013733 | -0.10529 | -0.20142 | -0.27466 | 0.054931 | 0.36163 | -0.16479 | 0.10986 | -0.054932 | 123.0286 | 122.7676 | 54.3503 | -123.0423 | 122.9279 | 122.818 | 67.2043 | -123.1476
2512.0156 | 123.111 | -52.7756 | 70.0745 | 0.27451 | 0.010226 | 0.068678 | 0.071372 | 0.13078 | 0.0022729 | -0.0045139 | 0.17532 | -0.0089124 | 0.065546 | 0.058253 | 0.007199 | -0.0098374 | 70.0516 | 70.1569 | 1.4053 | -52.9907 | 70.1569 | -52.8809 | -52.9861 | -52.4048 | 14.3875 | -52.858 | 70.1248 | 70.015 | -53.0136 | -53.0411 | -0.10529 | -0.21057 | 0.082397 | 122.9324 | -0.21515 | -0.004578 | -0.022888 | -0.23804 | -0.2655 | 0.050354 | 0.37079 | -0.082397 | 0.18311 | -0.059509 | 122.9324 | 122.8271 | 54.1809 | -123.0606 | 122.9004 | 122.7905 | 67.1631 | -123.1155
2513.0156 | 123.0148 | -52.6108 | 70.2713 | 0.12192 | 0.0076627 | 0.069319 | 0.069235 | 0.12693 | -0.0011451 | -0.0070773 | 0.053253 | -0.011476 | 0.061701 | 0.055903 | 0.0067718 | -0.011119 | 70.0836 | 70.1981 | 1.4923 | -52.9037 | 70.2942 | -52.7802 | -52.8671 | -52.3178 | 14.447 | -52.7069 | 70.2805 | 70.1889 | -52.8122 | -52.8625 | -0.16937 | -0.25635 | 0.022888 | 122.8088 | -0.29297 | -0.036622 | -0.18768 | -0.20142 | -0.25177 | 0.009156 | 0.29297 | -0.09613 | 0.15564 | -0.082397 | 122.905 | 122.6944 | 54.1031 | -123.1384 | 122.8912 | 122.7997 | 67.0578 | -123.1338
2514.0156 | 123.1155 | -51.8875 | 70.9625 | 0.17532 | 0.013858 | 0.067182 | 0.069876 | 0.13014 | 0.0029137 | -0.00024146 | 0.21347 | -0.010408 | 0.063837 | 0.056971 | 0.0091216 | -0.012401 | 70.6741 | 71.2601 | 1.593 | -52.0386 | 71.0175 | -51.9836 | -52.0523 | -51.4572 | 14.9231 | -51.796 | 71.0312 | 70.9213 | -52.0889 | -52.1255 | -0.096131 | -0.16479 | 0.054932 | 123.1476 | -0.15106 | 0.013733 | -0.28839 | -0.20142 | -0.23804 | 0.068665 | 0.4303 | 0.091553 | 0.32959 | -0.041198 | 122.905 | 122.5616 | 53.4805 | -123.0148 | 122.9187 | 122.8088 | 66.8106 | -123.0881
2515.0156 | 123.1293 | -52.4368 | 70.3903 | 0.18295 | 0.013217 | 0.068678 | 0.069663 | 0.13035 | 0.00013675 | -0.0043003 | 0.16006 | -0.0078442 | 0.061701 | 0.056544 | 0.0084808 | -0.012614 | 70.3629 | 70.5688 | 1.6067 | -52.5558 | 70.5643 | -52.4597 | -52.5513 | -51.9699 | 14.5844 | -52.5055 | 70.5414 | 70.4086 | -52.6428 | -52.6886 | -0.022888 | -0.11444 | 0.17395 | 123.0057 | -0.11902 | -0.004577 | -0.027466 | -0.20599 | -0.25177 | 0.15106 | 0.46692 | -0.068664 | 0.18311 | 0.01831 | 123.0011 | 122.7997 | 54.0436 | -122.9416 | 122.9782 | 122.8455 | 67.0212 | -123.0789
2516.0156 | 123.1064 | -52.6932 | 70.1431 | 0.0914 | 0.015994 | 0.06825 | 0.069663 | 0.12928 | -0.00029045 | -0.0049411 | 0.17532 | -0.0082716 | 0.06106 | 0.056117 | 0.0076264 | -0.013255 | 70.0378 | 70.1614 | 1.5198 | -52.9449 | 70.1935 | -52.8625 | -52.9724 | -52.3499 | 14.5432 | -53.0914 | 70.1248 | 69.9921 | -52.9999 | -52.9907 | -0.16937 | -0.27924 | 0.050354 | 122.8546 | -0.25177 | 0.027466 | -0.10529 | -0.3067 | -0.29755 | -0.01831 | 0.34332 | -0.39825 | -0.10071 | -0.15106 | 122.8867 | 122.731 | 54.213 | -123.1155 | 122.818 | 122.6852 | 67.2363 | -123.1339
2517.0156 | 123.0835 | -52.3819 | 70.4865 | 0.19058 | 0.0091581 | 0.070814 | 0.066885 | 0.12907 | -0.0043495 | -0.0055821 | 0.14481 | -0.009126 | 0.060419 | 0.05633 | 0.0039948 | -0.0098374 | 70.4865 | 70.6467 | 1.3779 | -52.5742 | 70.6696 | -52.4277 | -52.5146 | -52.1347 | 14.6896 | -52.6016 | 70.4498 | 70.3812 | -52.6566 | -52.6749 | -0.045776 | -0.13275 | 0.18311 | 123.0286 | -0.19226 | -0.05951 | 0 | -0.27466 | -0.29297 | -0.036621 | 0.24719 | -0.21973 | 0.073242 | -0.10529 | 123.0515 | 122.8683 | 53.7598 | -123.0011 | 122.8317 | 122.7631 | 67.0715 | -123.1613
2518.0156 | 123.1476 | -52.3499 | 70.4819 | 0.17532 | 0.013644 | 0.066755 | 0.069876 | 0.12843 | -7.6852e-05 | -0.0057957 | 0.053253 | -0.0084852 | 0.061487 | 0.055903 | 0.0067718 | -0.013255 | 70.34 | 70.0745 | 0.75989 | -52.6016 | 70.3903 | -52.5787 | -52.6611 | -51.9653 | 14.8132 | -52.5101 | 70.5643 | 70.4407 | -52.5879 | -52.6245 | -0.22888 | -0.31128 | -0.091553 | 122.4243 | -0.25177 | 0.059509 | -0.14191 | -0.23804 | -0.27466 | 0.082397 | 0.38452 | -0.16022 | 0.11444 | -0.041199 | 122.7402 | 122.6898 | 53.1097 | -123.143 | 122.9141 | 122.7905 | 67.1631 | -123.1064
2519.0156 | 123.0698 | -52.6062 | 70.253 | 0.11429 | 0.010653 | 0.06761 | 0.067099 | 0.13014 | -0.0026405 | -0.0062229 | 0.18295 | -0.0097668 | 0.06106 | 0.058253 | 0.0065582 | -0.010692 | 70.1431 | 70.2896 | 1.0345 | -52.7527 | 70.3766 | -52.6291 | -52.7298 | -52.2903 | 14.6439 | -52.6749 | 70.3262 | 70.2484 | -52.803 | -52.8442 | -0.022888 | -0.1236 | 0.1236 | 122.8958 | -0.14648 | -0.022889 | -0.10986 | -0.19684 | -0.23804 | 0.073242 | 0.31586 | -0.068665 | 0.16937 | -0.004578 | 122.9828 | 122.7493 | 53.6407 | -122.9828 | 122.9324 | 122.8546 | 67.2501 | -123.0972
2520.0156 | 123.1155 | -52.1896 | 70.6329 | 0.16006 | 0.014285 | 0.068464 | 0.071372 | 0.13057 | 0.0039819 | -0.0043003 | 0.19058 | -0.0086988 | 0.063623 | 0.055476 | 0.011258 | -0.013683 | 70.5505 | 70.6787 | 1.1353 | -52.4094 | 70.7245 | -52.2858 | -52.3773 | -51.7822 | 15.0146 | -52.3407 | 70.7428 | 70.5826 | -52.4139 | -52.4597 | -0.096131 | -0.18768 | 0.091552 | 122.8683 | -0.21973 | -0.032044 | -0.082398 | -0.2243 | -0.27008 | 0.10986 | 0.40741 | -0.15106 | 0.11902 | -0.050354 | 122.9141 | 122.7402 | 53.3249 | -123.0103 | 122.9324 | 122.7722 | 67.2043 | -123.0927
2521.0156 | 123.0835 | -53.0777 | 69.7998 | 0.083771 | 0.01279 | 0.067182 | 0.069876 | 0.12971 | 0.0012047 | -0.0060093 | 0.20584 | -0.0084852 | 0.059992 | 0.055476 | 0.0067718 | -0.012828 | 69.7311 | 69.8547 | 0.96588 | -53.215 | 69.9051 | -53.1418 | -53.215 | -52.739 | 14.6347 | -53.4531 | 69.7449 | 69.6671 | -53.3615 | -53.3936 | -0.064087 | -0.13733 | 0.10528 | 122.9324 | -0.13733 | 0 | -0.068665 | -0.28381 | -0.31586 | -0.054932 | 0.33874 | -0.37537 | -0.059509 | -0.13275 | 122.9828 | 122.8088 | 54.0436 | -123.0148 | 122.8226 | 122.7448 | 67.7124 | -123.1934
2522.0156 | 123.0377 | -52.2812 | 70.6558 | -0.22903 | 0.016849 | 0.068464 | 0.073721 | 0.13035 | 0.0029137 | -0.0043003 | 0.11429 | -0.0076306 | 0.062982 | 0.05633 | 0.0082672 | -0.012828 | 70.4269 | 70.4819 | 0.93842 | -52.5925 | 70.6924 | -52.4277 | -52.5375 | -51.9699 | 15.2893 | -52.5101 | 70.6421 | 70.5688 | -52.4872 | -52.5192 | -0.14648 | -0.25635 | 0.036621 | 122.7631 | -0.31128 | -0.054931 | -0.22888 | -0.20599 | -0.23804 | -0.013733 | 0.31128 | -0.22888 | 0.009155 | -0.086975 | 122.9736 | 122.7081 | 53.2196 | -123.1934 | 122.9233 | 122.85 | 67.5705 | -123.175
2523.0156 | 123.1247 | -52.7756 | 70.047 | -0.22141 | 0.0087307 | 0.06761 | 0.068167 | 0.12736 | -0.0015723 | -0.0057957 | 0.19821 | -0.0084852 | 0.05871 | 0.058467 | 0.00784 | -0.01176 | 69.9051 | 70.1019 | 1.0529 | -53.0136 | 70.1019 | -52.8946 | -52.9907 | -52.3727 | 15.2298 | -52.8397 | 70.1431 | 70.0287 | -52.977 | -53.0319 | -0.11902 | -0.21515 | 0.054932 | 122.8775 | -0.23804 | -0.022888 | -0.14191 | -0.20142 | -0.25635 | 0.09613 | 0.40283 | -0.064087 | 0.19226 | -0.01831 | 122.8775 | 122.6807 | 53.8284 | -123.0377 | 122.9187 | 122.8043 | 68.0054 | -123.0789
2524.0156 | 123.1567 | -52.533 | 70.285 | 0.19058 | 0.014285 | 0.069319 | 0.071799 | 0.12993 | 0.0012047 | -0.0038731 | 0.22873 | -0.0078442 | 0.061273 | 0.057826 | 0.008908 | -0.011546 | 70.1019 | 70.2072 | 1.1398 | -52.8214 | 70.3079 | -52.7573 | -52.7939 | -52.1439 | 15.4404 | -52.6062 | 70.4041 | 70.3079 | -52.739 | -52.7573 | -0.2243 | -0.26093 | 0.022888 | 122.7402 | -0.28839 | -0.027466 | -0.1831 | -0.20599 | -0.2243 | 0.11902 | 0.3891 | -0.073242 | 0.15106 | 0.022888 | 122.8409 | 122.6349 | 53.6728 | -123.0789 | 122.937 | 122.8409 | 67.9733 | -123.0423
2525.0156 | 123.1293 | -53.0365 | 69.7998 | 0.15244 | 0.012149 | 0.069746 | 0.066672 | 0.1295 | -0.0017859 | -0.0051547 | 0.20584 | -0.011049 | 0.064478 | 0.055689 | 0.007199 | -0.010692 | 69.6259 | 69.8318 | 1.1124 | -53.2745 | 69.8181 | -53.1372 | -53.2471 | -52.6657 | 15.2847 | -53.1921 | 69.8044 | 69.7311 | -53.2837 | -53.3478 | -0.10071 | -0.21057 | 0.01831 | 122.8683 | -0.23804 | -0.027466 | -0.17395 | -0.24719 | -0.31128 | 0.004577 | 0.37079 | -0.15564 | 0.15564 | -0.068665 | 122.8546 | 122.6624 | 54.1489 | -123.0469 | 122.8409 | 122.7676 | 68.3212 | -123.1476
2526.0156 | 123.111 | -52.8122 | 70.0516 | 0.16769 | 0.016208 | 0.06825 | 0.072867 | 0.12715 | 0.0020593 | -0.0064365 | 0.17532 | -0.0076306 | 0.064478 | 0.055476 | 0.0080536 | -0.012187 | 69.8914 | 70.0012 | 1.0162 | -53.1235 | 70.1294 | -52.977 | -53.0457 | -52.4506 | 15.4266 | -52.9404 | 70.1248 | 70.0195 | -53.0457 | -53.0731 | -0.16479 | -0.23346 | 0.07782 | 122.8134 | -0.31128 | -0.07782 | -0.16022 | -0.23346 | -0.26093 | 0.073242 | 0.36163 | -0.12817 | 0.13275 | -0.032044 | 122.9416 | 122.7036 | 53.8284 | -123.0972 | 122.937 | 122.8317 | 68.2388 | -123.1247
2527.0156 | 123.1293 | -52.4963 | 70.34 | 0.16006 | 0.013644 | 0.071882 | 0.067954 | 0.12822 | -0.0026405 | 0.00018594 | 0.35843 | -0.0078442 | 0.061487 | 0.055262 | 0.0069854 | -0.0098374 | 70.0104 | 70.079 | 1.1581 | -52.6749 | 70.2942 | -52.6978 | -52.7573 | -52.0615 | 15.6647 | -52.5696 | 70.4269 | 70.3308 | -52.739 | -52.7481 | -0.20142 | -0.26093 | -0.045777 | 122.5754 | -0.17853 | 0.082397 | -0.32959 | -0.24262 | -0.25177 | 0.086975 | 0.43488 | -0.073242 | 0.17853 | -0.009155 | 122.7905 | 122.5067 | 53.6545 | -123.0972 | 122.9233 | 122.8271 | 68.161 | -123.0881
2528.0156 | 122.9874 | -52.2903 | 70.6284 | 0.037994 | 0.01813 | 0.069319 | 0.071799 | 0.12886 | 0.0029137 | -0.0045139 | 0.083771 | -0.0082716 | 0.065119 | 0.057398 | 0.00784 | -0.013683 | 70.285 | 70.3537 | 0.94757 | -52.6474 | 70.6604 | -52.4689 | -52.565 | -51.9882 | 15.7379 | -52.5192 | 70.7153 | 70.578 | -52.5101 | -52.533 | -0.17853 | -0.27466 | 0.032043 | 122.644 | -0.35706 | -0.082398 | -0.34332 | -0.21973 | -0.24262 | 0.086975 | 0.30212 | -0.22888 | 0.013733 | -0.050354 | 122.9507 | 122.5754 | 53.2379 | -123.1934 | 123.0057 | 122.8683 | 68.0283 | -123.1613
2529.0156 | 123.0743 | -52.478 | 70.4041 | 0.17532 | 0.015994 | 0.067396 | 0.071158 | 0.13014 | -7.6852e-05 | -0.0064365 | 0.22873 | -0.0082716 | 0.062982 | 0.058894 | 0.0069854 | -0.010478 | 70.2805 | 70.4132 | 0.97046 | -52.6245 | 70.5872 | -52.5192 | -52.6062 | -52.1484 | 15.7516 | -52.6611 | 70.4453 | 70.3766 | -52.684 | -52.7252 | -0.041199 | -0.12817 | 0.1831 | 122.8912 | -0.14649 | -0.018311 | -0.1236 | -0.20599 | -0.24719 | 0.041198 | 0.32959 | -0.18311 | 0.064087 | -0.027466 | 123.0652 | 122.7585 | 53.4485 | -123.0103 | 122.9233 | 122.8546 | 68.2297 | -123.1293
2530.0156 | 123.0469 | -52.4414 | 70.4315 | 0.13718 | 0.018771 | 0.070387 | 0.073294 | 0.12693 | -7.6852e-05 | -0.0049411 | 0.15244 | -0.008058 | 0.065546 | 0.058894 | 0.00784 | -0.01176 | 70.2805 | 70.3995 | 1.0071 | -52.6474 | 70.578 | -52.5101 | -52.6108 | -52.0889 | 15.6601 | -52.5787 | 70.5414 | 70.4224 | -52.6566 | -52.7115 | -0.068665 | -0.16937 | 0.14648 | 122.8409 | -0.20599 | -0.036621 | -0.15106 | -0.21515 | -0.27008 | 0.10986 | 0.35248 | -0.13733 | 0.13275 | -0.009156 | 123.0194 | 122.7219 | 53.4485 | -123.0423 | 122.9828 | 122.8638 | 68.1015 | -123.143
2531.0156 | 123.1476 | -52.4597 | 70.3857 | 0.18295 | 0.014712 | 0.06825 | 0.069235 | 0.12971 | -0.00050425 | -0.0055821 | 0.24399 | -0.009126 | 0.062769 | 0.055476 | 0.0052764 | -0.013683 | 70.2255 | 70.3766 | 1.1261 | -52.6566 | 70.4224 | -52.6062 | -52.6657 | -52.1255 | 15.4816 | -52.8305 | 70.3491 | 70.2896 | -52.7618 | -52.7527 | -0.14648 | -0.20599 | 0.036621 | 122.8363 | -0.19684 | 0.009155 | -0.16022 | -0.30212 | -0.29297 | -0.036621 | 0.33417 | -0.37079 | -0.077819 | -0.09613 | 122.8821 | 122.6852 | 53.5858 | -123.0515 | 122.8088 | 122.7493 | 67.9413 | -123.1384
2532.0156 | 123.0057 | -52.8442 | 70.0836 | 0.13718 | 0.017276 | 0.069746 | 0.070944 | 0.12864 | 0.0020593 | -0.0051547 | -0.62576 | -0.0048536 | 0.062128 | 0.056758 | 0.0076264 | -0.010905 | 69.9554 | 69.5297 | 0.8606 | -52.9999 | 70.1065 | -52.9587 | -53.0411 | -52.4689 | 15.2802 | -53.0411 | 70.1843 | 70.0882 | -52.9999 | -53.0777 | -0.11444 | -0.19684 | 0.022888 | 122.374 | -0.15564 | 0.041199 | -0.12817 | -0.15564 | -0.23346 | 0.10071 | 0.37537 | -0.19684 | 0.036621 | 0.004578 | 122.9507 | 122.7997 | 53.7048 | -123.1247 | 123.0286 | 122.9324 | 68.1244 | -123.1613
2533.0156 | 123.1247 | -52.1667 | 70.6512 | 0.17532 | 0.016421 | 0.069746 | 0.068808 | 0.13035 | -0.00071785 | -0.0047275 | 0.21347 | -0.0097668 | 0.062342 | 0.056117 | 0.0086944 | -0.011119 | 70.5231 | 70.6467 | 1.1261 | -52.4048 | 70.7565 | -52.2766 | -52.3773 | -51.8188 | 15.834 | -52.2812 | 70.7153 | 70.6604 | -52.4002 | -52.4094 | -0.10986 | -0.21057 | 0.10529 | 122.8134 | -0.23804 | -0.027466 | -0.12817 | -0.23346 | -0.24262 | 0.064087 | 0.3479 | -0.11444 | 0.12817 | 0.009155 | 122.9233 | 122.6898 | 53.2928 | -123.0286 | 122.8821 | 122.8271 | 68.0008 | -123.0606
2534.0156 | 123.0057 | -51.9791 | 70.9625 | 0.11429 | 0.016849 | 0.068891 | 0.072653 | 0.12758 | 0.00035035 | -0.0034457 | 0.15244 | -0.0076306 | 0.064051 | 0.056758 | 0.010831 | -0.013042 | 70.5597 | 70.6604 | 1.0483 | -52.3453 | 70.8801 | -52.2125 | -52.327 | -51.7593 | 15.7974 | -52.3087 | 70.9351 | 70.8755 | -52.272 | -52.2766 | -0.23346 | -0.3479 | -0.082397 | 122.6395 | -0.36621 | -0.018311 | -0.40283 | -0.29297 | -0.29755 | -0.027465 | 0.21973 | -0.32959 | -0.032044 | -0.086975 | 122.8592 | 122.5388 | 53.0273 | -123.2895 | 122.9141 | 122.8546 | 67.7765 | -123.2391
2535.0156 | 123.0743 | -52.446 | 70.4453 | 0.16769 | 0.014712 | 0.068891 | 0.072653 | 0.12843 | 0.0027001 | -0.0055821 | 0.19821 | -0.0099806 | 0.063837 | 0.056117 | 0.0080536 | -0.0098374 | 70.3262 | 70.4361 | 0.9613 | -52.6108 | 70.6375 | -52.4506 | -52.5238 | -51.9241 | 15.6967 | -52.4597 | 70.6696 | 70.5368 | -52.5879 | -52.6428 | -0.004578 | -0.07782 | 0.19226 | 122.8821 | -0.16479 | -0.086975 | -0.11902 | -0.14191 | -0.19684 | 0.22431 | 0.52185 | -0.013733 | 0.18311 | 0.091553 | 123.0835 | 122.7722 | 53.4073 | -122.9691 | 123.1155 | 122.9828 | 68.1427 | -123.0881
2536.0156 | 123.0423 | -52.3315 | 70.5826 | -0.061188 | 0.017489 | 0.0706 | 0.070731 | 0.13035 | 0.00099115 | -0.0036595 | -0.03067 | -0.0069898 | 0.064264 | 0.057612 | 0.0099762 | -0.011974 | 70.5048 | 70.6375 | 1.1673 | -52.4597 | 70.7703 | -52.327 | -52.4185 | -51.9333 | 15.6235 | -52.5009 | 70.6833 | 70.6192 | -52.4963 | -52.5513 | 0.004578 | -0.086975 | 0.18768 | 122.9691 | -0.12817 | -0.041199 | -0.07782 | -0.16479 | -0.21973 | 0.10071 | 0.39825 | -0.16937 | 0.050354 | 0.036621 | 123.1018 | 122.8363 | 53.4988 | -123.0011 | 123.0148 | 122.9507 | 67.955 | -123.1339
2537.0156 | 123.0194 | -52.8763 | 70.0699 | 0.14481 | 0.015994 | 0.065687 | 0.069235 | 0.12758 | -7.6852e-05 | -0.0062229 | 0.45761 | -0.0097668 | 0.062769 | 0.059535 | 0.0063446 | -0.01176 | 69.7723 | 69.8959 | 1.2085 | -53.3386 | 70.0607 | -53.0228 | -53.1189 | -52.5513 | 15.1886 | -53.0914 | 70.0928 | 69.9829 | -53.0869 | -53.1326 | -0.14648 | -0.24261 | -0.009155 | 122.7722 | -0.46234 | -0.21973 | -0.29755 | -0.21057 | -0.25635 | 0.022888 | 0.32501 | -0.21515 | 0.041198 | -0.086975 | 122.937 | 122.6486 | 54.0848 | -123.1888 | 122.9691 | 122.8592 | 68.0649 | -123.2025
2538.0156 | 123.0011 | -52.1988 | 70.7016 | 0.037994 | 0.017489 | 0.069746 | 0.070731 | 0.12928 | 0.0018457 | -0.0040867 | 0.12955 | -0.010621 | 0.065332 | 0.057612 | 0.0063446 | -0.011333 | 70.6192 | 70.7657 | 1.1261 | -52.2766 | 70.9488 | -52.1576 | -52.272 | -51.7502 | 15.5823 | -52.272 | 70.903 | 70.8481 | -52.2949 | -52.3544 | 0.041199 | -0.073242 | 0.24719 | 122.9645 | -0.077819 | -0.004577 | -0.082397 | -0.09613 | -0.15564 | 0.20142 | 0.44861 | -0.073242 | 0.082397 | 0.14648 | 123.1476 | 122.818 | 53.3249 | -122.9736 | 123.1018 | 123.0469 | 67.7811 | -123.056
2539.0156 | 123.0148 | -52.2812 | 70.6467 | 0.083771 | 0.018344 | 0.066328 | 0.069022 | 0.12779 | 0.0016321 | -0.0096409 | 0.0914 | -0.0078442 | 0.062982 | 0.057826 | 0.0074126 | -0.011333 | 70.7703 | 70.5139 | 0.98877 | -52.4368 | 70.7932 | -52.3132 | -52.4002 | -51.9058 | 15.6372 | -52.5284 | 70.7336 | 70.6696 | -52.4872 | -52.533 | -0.032043 | -0.11902 | 0.14649 | 122.7951 | -0.15564 | -0.036621 | 0.1236 | -0.20599 | -0.25177 | 0.086976 | 0.37537 | -0.24719 | 0.004578 | 0.022889 | 123.0743 | 123.0515 | 53.27 | -123.0469 | 123.0148 | 122.9507 | 67.9184 | -123.1796
2540.0156 | 123.0194 | -52.5787 | 70.34 | -0.15274 | 0.017276 | 0.067823 | 0.070944 | 0.1295 | 0.00056395 | -0.0081455 | -0.015411 | -0.0084852 | 0.064051 | 0.057612 | 0.0082672 | -0.010905 | 70.0058 | 70.1889 | 1.0391 | -52.8763 | 70.3171 | -52.7481 | -52.8305 | -52.1667 | 15.5731 | -52.7252 | 70.4132 | 70.3583 | -52.8259 | -52.8397 | -0.16937 | -0.25177 | -0.022888 | 122.7676 | -0.29755 | -0.045777 | -0.33417 | -0.24719 | -0.26093 | 0.073242 | 0.41199 | -0.14648 | 0.11444 | 0.01831 | 122.8958 | 122.5845 | 53.6179 | -123.1705 | 122.9919 | 122.937 | 68.1519 | -123.1796
2541.0156 | 123.0103 | -52.4048 | 70.5048 | 0.030365 | 0.017276 | 0.066969 | 0.072012 | 0.12886 | -0.00050425 | -0.0047275 | 0.17532 | -0.007417 | 0.066828 | 0.059962 | 0.0091216 | -0.011546 | 70.3766 | 70.4865 | 1.0895 | -52.5055 | 70.7474 | -52.3544 | -52.4597 | -52.0798 | 15.6235 | -52.6474 | 70.6467 | 70.5688 | -52.5879 | -52.6291 | 0.050354 | -0.054932 | 0.24261 | 122.8912 | -0.10071 | -0.045776 | -0.12817 | -0.18311 | -0.2243 | 0.14191 | 0.32501 | -0.24262 | -0.018311 | 0.064087 | 123.1522 | 122.7814 | 53.4943 | -122.9645 | 123.0515 | 122.9736 | 68.0283 | -123.1338
2542.0156 | 123.0881 | -52.0615 | 70.8572 | -0.19089 | 0.017062 | 0.070173 | 0.075217 | 0.13121 | 0.0018457 | -0.0070773 | -0.17563 | -0.0072034 | 0.062342 | 0.056544 | 0.0063446 | -0.012187 | 70.5826 | 70.7611 | 1.1856 | -52.1759 | 70.9579 | -52.1164 | -52.1896 | -51.7181 | 15.9256 | -52.0889 | 70.9625 | 70.8939 | -52.24 | -52.2858 | -0.054932 | -0.12817 | 0.10071 | 122.8226 | -0.11444 | 0.013733 | -0.27466 | -0.17853 | -0.22431 | 0.10528 | 0.34332 | -0.027466 | 0.19684 | 0.036621 | 123.0194 | 122.644 | 53.2471 | -123.0469 | 123.024 | 122.9553 | 67.9871 | -123.143
2543.0156 | 123.0286 | -53.0273 | 69.9326 | -0.0077822 | 0.01813 | 0.0706 | 0.070517 | 0.12758 | 0.00099115 | -0.0045139 | -0.023041 | -0.0065626 | 0.065119 | 0.058253 | 0.00784 | -0.011333 | 69.8639 | 69.9783 | 1.2131 | -53.1647 | 70.079 | -53.0502 | -53.1281 | -52.5925 | 15.3809 | -53.183 | 69.9875 | 69.9234 | -53.2104 | -53.2608 | -0.022888 | -0.10071 | 0.14648 | 123.0057 | -0.13733 | -0.036621 | -0.068664 | -0.1831 | -0.23346 | 0.054932 | 0.43488 | -0.15564 | 0.07782 | -0.009155 | 123.1064 | 122.8912 | 54.2404 | -123.0606 | 123.0148 | 122.9507 | 68.4082 | -123.1934
2544.0156 | 123.056 | -52.0752 | 70.8664 | -0.068817 | 0.017917 | 0.06761 | 0.073721 | 0.128 | 0.0024865 | -0.0032321 | -0.045929 | -0.0095532 | 0.062555 | 0.058467 | 0.0082672 | -0.011333 | 70.7062 | 71.0541 | 1.6251 | -52.0615 | 71.1227 | -51.9745 | -52.034 | -51.6632 | 15.889 | -52.272 | 70.9671 | 70.8984 | -52.2354 | -52.3041 | 0.10071 | 0.041198 | 0.25635 | 123.1293 | 0.013733 | -0.027465 | -0.16022 | -0.16022 | -0.22888 | 0.10071 | 0.41199 | -0.19684 | 0.032043 | 0.032043 | 123.1979 | 122.7814 | 53.7003 | -122.9004 | 123.0423 | 122.9736 | 67.9642 | -123.1705
2545.0156 | 122.9919 | -52.4826 | 70.4727 | 0.022736 | 0.015994 | 0.068678 | 0.072012 | 0.12928 | 0.0024865 | -0.0072911 | 0.083771 | -0.010408 | 0.064051 | 0.058467 | 0.0065582 | -0.010905 | 70.2072 | 70.34 | 1.4374 | -52.6978 | 70.5185 | -52.5787 | -52.6474 | -52.1301 | 15.5869 | -52.6703 | 70.5368 | 70.4498 | -52.6886 | -52.7298 | -0.09613 | -0.16479 | 0.045777 | 122.8226 | -0.21515 | -0.050354 | -0.2655 | -0.20599 | -0.24719 | 0.064087 | 0.35248 | -0.18768 | 0.059509 | -0.022888 | 123.0011 | 122.6898 | 53.92 | -123.1201 | 123.0194 | 122.9324 | 68.0695 | -123.2025
2546.0156 | 123.0469 | -52.066 | 70.8527 | -0.12222 | 0.017276 | 0.069746 | 0.073935 | 0.12843 | -0.0017859 | -0.0049411 | -0.015411 | -0.0076306 | 0.065119 | 0.057612 | 0.0065582 | -0.012187 | 70.7565 | 70.9259 | 1.5884 | -52.121 | 71.0449 | -52.034 | -52.1072 | -51.6083 | 16.0584 | -52.0203 | 71.0587 | 70.99 | -52.1622 | -52.2125 | 0.032043 | -0.041199 | 0.19226 | 122.9919 | -0.054932 | -0.013733 | -0.09613 | -0.09613 | -0.14648 | 0.20599 | 0.45776 | 0.045776 | 0.19226 | 0.13733 | 123.111 | 122.8226 | 53.6545 | -122.9599 | 123.1247 | 123.056 | 68.1244 | -123.0652
2547.0469 | 123.1384 | -52.4689 | 70.4544 | -0.091705 | 0.010013 | 0.069746 | 0.072226 | 0.12886 | -0.0064857 | -0.0089999 | -0.038299 | -0.0099806 | 0.061701 | 0.055903 | 0.0033538 | -0.010265 | 70.2026 | 70.3995 | 1.5289 | -52.6978 | 70.3995 | -52.6199 | -52.6978 | -52.0386 | 16.1179 | -52.4826 | 70.4819 | 70.4041 | -52.6337 | -52.7115 | -0.15106 | -0.22888 | -0.054932 | 122.8683 | -0.22888 | 0 | -0.25177 | -0.1648 | -0.24262 | 0.027466 | 0.4303 | -0.013733 | 0.22888 | -0.050354 | 122.8683 | 122.6715 | 53.9978 | -123.1522 | 122.9507 | 122.8729 | 68.5867 | -123.1659
2548.0156 | 123.0789 | -51.9791 | 70.9625 | -0.20615 | 0.015994 | 0.068037 | 0.074149 | 0.12907 | 0.0029137 | -0.0070773 | -0.17563 | -0.0082716 | 0.064478 | 0.057612 | 0.0093354 | -0.011546 | 70.7565 | 70.8847 | 1.4282 | -52.1622 | 71.0312 | -52.0569 | -52.1576 | -51.5991 | 16.4566 | -52.1439 | 71.0312 | 70.9625 | -52.2034 | -52.2263 | -0.07782 | -0.17853 | 0.068665 | 122.8638 | -0.18311 | -0.004577 | -0.20599 | -0.2243 | -0.24719 | 0.068665 | 0.37994 | -0.16479 | 0.082397 | 0 | 123.0103 | 122.7356 | 53.4073 | -123.1201 | 123.0103 | 122.9416 | 68.4357 | -123.1888
2549.0156 | 123.0652 | -52.1713 | 70.7657 | -0.168 | 0.014712 | 0.069532 | 0.071799 | 0.13035 | 0.0012047 | -0.0062229 | -0.023041 | -0.010194 | 0.064478 | 0.057826 | 0.0069854 | -0.012828 | 70.6192 | 70.8023 | 1.4648 | -52.2629 | 70.9167 | -52.1713 | -52.2766 | -51.7456 | 16.5344 | -52.272 | 70.8618 | 70.8115 | -52.3315 | -52.3773 | 0 | -0.10529 | 0.15106 | 122.9736 | -0.091552 | 0.013733 | -0.14648 | -0.16022 | -0.20599 | 0.09613 | 0.42572 | -0.10071 | 0.10529 | 0.045776 | 123.0881 | 122.7905 | 53.6362 | -123.0423 | 123.0331 | 122.9828 | 68.7057 | -123.143
2550.0156 | 123.0515 | -51.5442 | 71.4249 | -0.21378 | 0.010867 | 0.071882 | 0.073294 | 0.12993 | -0.0019995 | -0.0077183 | -0.168 | -0.0082716 | 0.06106 | 0.057612 | 0.0046356 | -0.011119 | 71.2418 | 71.4615 | 1.5518 | -51.622 | 71.6217 | -51.4938 | -51.6083 | -51.329 | 17.3035 | -51.5854 | 71.4706 | 71.402 | -51.7685 | -51.796 | 0.050354 | -0.064087 | 0.19684 | 123.0057 | -0.07782 | -0.013733 | -0.18311 | -0.2243 | -0.25177 | 0.045776 | 0.21515 | -0.041199 | 0.21057 | -0.022888 | 123.1659 | 122.7859 | 53.096 | -123.0331 | 123.0148 | 122.9462 | 68.8477 | -123.2208
2551.0156 | 123.0331 | -51.6129 | 71.3287 | -0.091705 | 0.01578 | 0.065473 | 0.074149 | 0.12822 | 0.00013675 | -0.0051547 | 0.022736 | -0.0099806 | 0.063837 | 0.058039 | 0.0091216 | -0.011119 | 71.0449 | 71.2372 | 1.4969 | -51.8097 | 71.3425 | -51.7639 | -51.8463 | -51.2329 | 17.0883 | -51.8463 | 71.3699 | 71.2921 | -51.8555 | -51.8555 | -0.15106 | -0.23346 | 0.013733 | 122.85 | -0.19684 | 0.036621 | -0.28381 | -0.24262 | -0.24262 | 0.041199 | 0.37994 | -0.23346 | 0.009156 | -0.036621 | 122.9553 | 122.6578 | 53.1097 | -123.175 | 122.9828 | 122.905 | 68.7012 | -123.1842
2552.0156 | 123.0606 | -51.3748 | 71.5805 | -0.15274 | 0.014071 | 0.069319 | 0.072012 | 0.12736 | -0.0013587 | -0.0043003 | -0.16037 | -0.009126 | 0.064905 | 0.057612 | 0.0084808 | -0.010905 | 71.2921 | 71.4706 | 1.3916 | -51.5991 | 71.6125 | -51.4801 | -51.5625 | -51.0178 | 17.0654 | -51.4618 | 71.6263 | 71.5713 | -51.5625 | -51.5762 | -0.10529 | -0.18768 | 0.032044 | 122.8455 | -0.2243 | -0.036621 | -0.28839 | -0.18768 | -0.20142 | 0.045777 | 0.35706 | -0.086975 | 0.11444 | -0.009155 | 122.9874 | 122.6669 | 52.7664 | -123.143 | 123.0011 | 122.9462 | 68.4402 | -123.1567
2553.0156 | 123.0606 | -52.3224 | 70.5963 | -0.053558 | 0.017917 | 0.069532 | 0.072653 | 0.128 | -0.00029045 | -0.0053683 | -0.39688 | -0.0086988 | 0.065119 | 0.057185 | 0.006131 | -0.013255 | 70.3629 | 70.5734 | 1.2955 | -52.5055 | 70.6558 | -52.4048 | -52.4872 | -51.8509 | 16.745 | -52.4139 | 70.7382 | 70.6604 | -52.446 | -52.5192 | -0.082397 | -0.1648 | 0.05951 | 122.8958 | -0.18311 | -0.01831 | -0.23346 | -0.1236 | -0.19684 | 0.14191 | 0.4715 | -0.091552 | 0.10529 | 0.064087 | 122.9782 | 122.6852 | 53.6179 | -123.0835 | 123.0606 | 122.9828 | 69.0674 | -123.1155
2554.0156 | 123.0103 | -52.5604 | 70.4086 | -0.52658 | 0.014285 | 0.067396 | 0.07244 | 0.128 | -0.0022131 | -0.0077183 | -0.13748 | -0.0097668 | 0.063196 | 0.056758 | 0.006131 | -0.011546 | 70.015 | 70.2164 | 1.0529 | -52.8259 | 70.4041 | -52.7252 | -52.8122 | -52.1667 | 16.6672 | -52.7023 | 70.4681 | 70.3766 | -52.7435 | -52.8122 | -0.16479 | -0.25177 | -0.004577 | 122.7768 | -0.2655 | -0.013733 | -0.39368 | -0.1831 | -0.25177 | 0.05951 | 0.39368 | -0.14191 | 0.10986 | -0.032043 | 122.9645 | 122.5754 | 53.6133 | -123.2208 | 123.0286 | 122.937 | 69.2276 | -123.2208
2555.0156 | 123.0835 | -51.1002 | 71.759 | -0.20615 | 0.01813 | 0.070387 | 0.073721 | 0.12993 | 0.0018457 | -0.0051547 | -0.16037 | -0.0076306 | 0.064905 | 0.05868 | 0.0086944 | -0.011119 | 71.6446 | 71.8185 | 1.3596 | -51.2924 | 71.9376 | -51.1917 | -51.329 | -50.6836 | 17.569 | -51.2192 | 71.8689 | 71.7819 | -51.3199 | -51.3382 | -0.091552 | -0.22888 | 0.17853 | 122.9187 | -0.19226 | 0.036622 | -0.11444 | -0.21973 | -0.23804 | 0.10986 | 0.41656 | -0.11902 | 0.11902 | 0.022888 | 123.0377 | 122.7448 | 52.4597 | -123.0881 | 122.9691 | 122.8821 | 68.6691 | -123.0972
2556.0156 | 123.0469 | -52.3636 | 70.5643 | -0.21378 | 0.0089443 | 0.071882 | 0.07009 | 0.12928 | -0.0052039 | -0.0081455 | -0.091705 | -0.0089124 | 0.064051 | 0.056971 | 0.0052764 | -0.01176 | 70.3629 | 70.5688 | 1.3687 | -52.5284 | 70.6192 | -52.4231 | -52.5192 | -51.9379 | 17.0242 | -52.4368 | 70.6512 | 70.5872 | -52.5696 | -52.6016 | -0.05951 | -0.15564 | 0.054932 | 122.9324 | -0.1648 | -0.009155 | -0.20142 | -0.20599 | -0.23804 | 0.086975 | 0.42572 | -0.073243 | 0.16479 | 0.022888 | 122.9828 | 122.7264 | 53.7323 | -123.0835 | 123.0148 | 122.9507 | 69.3878 | -123.1659
2557.0156 | 123.0881 | -52.4551 | 70.4865 | -0.19089 | 0.01578 | 0.070814 | 0.07244 | 0.13078 | -7.6852e-05 | -0.0051547 | -0.14511 | -0.0084852 | 0.064051 | 0.058467 | 0.0048492 | -0.012187 | 70.5505 | 70.7382 | 1.5244 | -52.3041 | 70.8893 | -52.2125 | -52.2766 | -51.9974 | 17.0975 | -52.6749 | 70.6558 | 70.5597 | -52.6108 | -52.6978 | 0.24262 | 0.17853 | 0.40283 | 123.1934 | 0.15106 | -0.027466 | 0.064087 | -0.15564 | -0.24262 | 0.16937 | 0.45776 | -0.21973 | 0.022888 | 0.073242 | 123.3444 | 123.0057 | 53.9795 | -122.7631 | 123.111 | 123.0148 | 69.5526 | -123.1842
2558.0156 | 123.0377 | -51.7593 | 71.1685 | -0.22141 | 0.013003 | 0.069532 | 0.071158 | 0.12993 | -0.0019995 | -0.0053683 | -0.87753 | -0.0084852 | 0.06341 | 0.056758 | 0.0035674 | -0.0098374 | 70.7794 | 70.9305 | 1.3733 | -52.0798 | 71.1639 | -51.9287 | -52.002 | -51.3657 | 17.3447 | -51.9516 | 71.2784 | 71.1685 | -51.9974 | -51.9974 | -0.16937 | -0.24262 | -0.004578 | 122.6898 | -0.32044 | -0.07782 | -0.3891 | -0.23804 | -0.23804 | 0.10986 | 0.39368 | -0.19226 | 0.045776 | 0 | 122.9233 | 122.5388 | 53.1326 | -123.1705 | 123.0377 | 122.9279 | 69.104 | -123.1659
2559.0156 | 123.0835 | -52.8442 | 70.0516 | -0.19852 | 0.01514 | 0.067396 | 0.070517 | 0.12928 | -0.00050425 | -0.0064365 | -0.091705 | -0.0082716 | 0.062555 | 0.058253 | 0.007199 | -0.012614 | 69.928 | 70.1614 | 1.3184 | -52.9129 | 70.253 | -52.8763 | -52.9633 | -52.4689 | 16.777 | -53.0182 | 70.1614 | 70.0287 | -53.0411 | -53.1052 | -0.032044 | -0.11902 | 0.20142 | 123.0057 | -0.068665 | 0.050354 | -0.1236 | -0.19684 | -0.26093 | 0.10986 | 0.37537 | -0.17395 | 0.086976 | -0.022888 | 123.0972 | 122.7722 | 54.1626 | -123.0148 | 123.0057 | 122.8729 | 69.6213 | -123.1567
2560.0156 | 123.0331 | -52.3819 | 70.5734 | -0.23666 | 0.0095853 | 0.069746 | 0.070731 | 0.13035 | -0.0032813 | -0.0077183 | -0.14511 | -0.010835 | 0.062769 | 0.058039 | 0.0052764 | -0.010051 | 70.3125 | 70.459 | 1.2039 | -52.6291 | 70.6284 | -52.478 | -52.5879 | -51.9882 | 16.9647 | -52.5146 | 70.6741 | 70.578 | -52.5696 | -52.597 | -0.09613 | -0.20599 | 0.054932 | 122.8409 | -0.24719 | -0.041198 | -0.26093 | -0.18768 | -0.21515 | 0.10071 | 0.39368 | -0.13275 | 0.082398 | 0.004578 | 123.0103 | 122.6944 | 53.5858 | -123.1613 | 123.056 | 122.9599 | 69.3466 | -123.1705
2561.0156 | 123.0194 | -51.5671 | 71.402 | -0.16037 | 0.01279 | 0.068037 | 0.07244 | 0.13163 | 0.00077755 | -0.0070773 | -0.16037 | -0.011049 | 0.062342 | 0.057612 | 0.0084808 | -0.012187 | 71.3196 | 71.5073 | 1.4008 | -51.5488 | 71.6675 | -51.4435 | -51.5396 | -51.1185 | 17.3904 | -51.7456 | 71.5347 | 71.4157 | -51.7319 | -51.8005 | 0.1236 | 0.027466 | 0.2655 | 123.0743 | 0.018311 | -0.009155 | -0.082398 | -0.16479 | -0.23346 | 0.13275 | 0.44861 | -0.17853 | 0.054932 | 0.013732 | 123.2346 | 122.8867 | 52.9678 | -122.9416 | 123.1018 | 122.9828 | 68.9575 | -123.2025
2562.0156 | 123.0194 | -51.8921 | 71.0724 | -0.25192 | 0.011935 | 0.06825 | 0.070731 | 0.12715 | -0.0052039 | -0.0064365 | -0.14511 | -0.0093396 | 0.06106 | 0.05868 | 0.0082672 | -0.011333 | 70.9946 | 71.228 | 1.4648 | -51.9104 | 71.2509 | -51.8005 | -51.9058 | -51.4709 | 17.1707 | -52.0386 | 71.1136 | 71.0129 | -52.1027 | -52.1576 | 0.091553 | -0.013733 | 0.17853 | 123.1201 | -0.01831 | -0.004577 | -0.07782 | -0.21057 | -0.2655 | 0.041198 | 0.42114 | -0.14648 | 0.11902 | -0.05951 | 123.143 | 122.8867 | 53.3569 | -122.9782 | 123.0057 | 122.905 | 69.0628 | -123.23
2563.0156 | 123.0423 | -52.327 | 70.6284 | -0.21378 | 0.013858 | 0.069105 | 0.074362 | 0.128 | -0.0052039 | -0.0066501 | -0.14511 | -0.007417 | 0.064051 | 0.058253 | 0.0052764 | -0.010692 | 70.3949 | 70.6284 | 1.0162 | -52.4689 | 70.752 | -52.3544 | -52.4551 | -51.9836 | 16.6901 | -52.6794 | 70.6375 | 70.5597 | -52.5558 | -52.6062 | -0.027466 | -0.12817 | 0.1236 | 122.9553 | -0.14191 | -0.013733 | -0.23346 | -0.22888 | -0.27924 | 0.009155 | 0.34332 | -0.35248 | -0.073242 | -0.068665 | 123.0789 | 122.7219 | 53.3432 | -123.0835 | 122.9645 | 122.8867 | 69.017 | -123.2346
2564.0156 | 123.0881 | -51.9928 | 70.8893 | -0.22141 | 0.010867 | 0.06825 | 0.071158 | 0.12993 | -0.0054175 | -0.0066501 | -0.10696 | -0.011476 | 0.06106 | 0.056758 | 0.00549 | -0.010692 | 70.816 | 71.0678 | 1.1536 | -52.0844 | 71.0678 | -51.9608 | -52.0477 | -51.4709 | 17.3264 | -51.9836 | 71.0403 | 70.9396 | -52.1439 | -52.2034 | 0.032044 | -0.054931 | 0.17853 | 123.0606 | -0.091553 | -0.036622 | -0.073242 | -0.15106 | -0.21057 | 0.15106 | 0.52185 | 0.009155 | 0.21973 | 0.050354 | 123.0606 | 122.8088 | 53.1464 | -122.937 | 123.0331 | 122.9324 | 69.3192 | -123.0927
2565.0156 | 123.0743 | -51.6907 | 71.2509 | -0.23666 | 0.01514 | 0.069959 | 0.072653 | 0.13078 | 0.0020593 | -0.0066501 | -0.14511 | -0.009126 | 0.061701 | 0.056758 | 0.0080536 | -0.013896 | 70.8389 | 71.0129 | 1.3275 | -52.066 | 71.1914 | -51.9333 | -52.0523 | -51.2741 | 17.2852 | -51.7868 | 71.2784 | 71.228 | -51.8967 | -51.915 | -0.24262 | -0.36163 | -0.05951 | 122.7036 | -0.37537 | -0.013733 | -0.41199 | -0.20599 | -0.2243 | 0.027465 | 0.41656 | -0.09613 | 0.12817 | -0.022889 | 122.8821 | 122.5296 | 53.0182 | -123.3032 | 122.9691 | 122.9187 | 68.9758 | -123.1659
2566.0156 | 123.0606 | -51.5076 | 71.3928 | -0.21378 | 0.011722 | 0.068037 | 0.068808 | 0.128 | -0.0039221 | -0.0081455 | -0.14511 | -0.012971 | 0.062769 | 0.05398 | 0.0050628 | -0.010692 | 71.0403 | 71.2738 | 1.4328 | -51.8051 | 71.3562 | -51.7273 | -51.7685 | -51.0086 | 17.4271 | -51.4481 | 71.5393 | 71.4249 | -51.6632 | -51.7319 | -0.21973 | -0.26093 | -0.036621 | 122.7814 | -0.29755 | -0.036621 | -0.35248 | -0.15564 | -0.22431 | 0.14648 | 0.49896 | 0.059509 | 0.28381 | 0.032044 | 122.8638 | 122.5479 | 52.9404 | -123.1613 | 123.0469 | 122.9324 | 68.9346 | -123.1247
2567.0156 | 123.0194 | -52.5055 | 70.3949 | -0.13748 | 0.014926 | 0.068678 | 0.071585 | 0.13078 | 0.0012047 | -0.0030185 | -0.17563 | -0.0089124 | 0.06341 | 0.058253 | 0.007199 | -0.01411 | 70.6284 | 70.7611 | 1.268 | -52.3773 | 70.9259 | -52.24 | -52.3636 | -52.066 | 16.5344 | -52.8351 | 70.5643 | 70.4544 | -52.6703 | -52.7115 | 0.2655 | 0.14191 | 0.53101 | 123.2666 | 0.12817 | -0.013733 | 0.23346 | -0.16479 | -0.20599 | 0.16937 | 0.43945 | -0.32959 | -0.1236 | 0.05951 | 123.4314 | 123.1338 | 53.7735 | -122.7585 | 123.0698 | 122.9599 | 69.0399 | -123.1064
2568.0156 | 123.0377 | -52.4185 | 70.5872 | -0.28244 | 0.010867 | 0.069959 | 0.072012 | 0.12651 | -0.0019995 | -0.0055821 | -0.12222 | -0.008058 | 0.064264 | 0.055903 | 0.0050628 | -0.01176 | 70.1889 | 70.3995 | 1.2405 | -52.7023 | 70.4819 | -52.5787 | -52.6978 | -52.1118 | 16.5161 | -52.7115 | 70.4727 | 70.4041 | -52.6886 | -52.7069 | -0.16022 | -0.27924 | -0.10529 | 122.818 | -0.28381 | -0.004578 | -0.39825 | -0.27008 | -0.28839 | -0.11444 | 0.3067 | -0.29297 | -0.004578 | -0.1831 | 122.9004 | 122.6074 | 53.6591 | -123.2849 | 122.8912 | 122.8226 | 68.9346 | -123.2941
2569.0156 | 123.056 | -51.7044 | 71.1914 | -0.14511 | 0.014926 | 0.069959 | 0.075644 | 0.12993 | 0.00077755 | -0.0040867 | -0.23666 | -0.007417 | 0.062769 | 0.055262 | 0.0086944 | -0.010692 | 70.9396 | 71.1044 | 1.0483 | -51.9699 | 71.2555 | -51.8372 | -51.915 | -51.2558 | 17.1524 | -51.6037 | 71.3242 | 71.2875 | -51.828 | -51.8875 | -0.13275 | -0.21057 | 0.064087 | 122.8088 | -0.2655 | -0.054932 | -0.25177 | -0.1236 | -0.1831 | 0.13275 | 0.44861 | 0.10071 | 0.28381 | 0.096131 | 122.9599 | 122.644 | 52.7527 | -123.1064 | 123.0286 | 122.9919 | 68.8568 | -123.0789
2570.0156 | 123.1384 | -51.5854 | 71.283 | -0.15274 | 0.0078763 | 0.0706 | 0.072226 | 0.12928 | -0.0047767 | -0.0055821 | -0.045929 | -0.013185 | 0.060419 | 0.05633 | 0.0050628 | -0.016032 | 71.2234 | 71.5073 | 1.2405 | -51.6403 | 71.4523 | -51.5945 | -51.6678 | -50.885 | 17.5369 | -51.9379 | 71.4066 | 71.2784 | -51.7685 | -51.828 | -0.009155 | -0.082398 | 0.16937 | 123.0927 | -0.054932 | 0.027466 | -0.059509 | -0.18311 | -0.24262 | 0.1236 | 0.70038 | -0.35248 | -0.10986 | -0.004578 | 123.0377 | 122.8088 | 52.8259 | -122.9507 | 122.9919 | 122.8638 | 69.1223 | -123.111
2571.0156 | 123.0194 | -51.4847 | 71.4294 | -0.16037 | 0.014499 | 0.069105 | 0.073935 | 0.13057 | 0.00035035 | -0.0055821 | -0.12985 | -0.0095532 | 0.064051 | 0.058039 | 0.0080536 | -0.014323 | 71.4523 | 71.6354 | 0.94299 | -51.4572 | 71.8231 | -51.3245 | -51.4206 | -50.7568 | 17.6605 | -51.416 | 71.8048 | 71.6583 | -51.503 | -51.6266 | 0.16022 | 0.064087 | 0.39368 | 123.1201 | 0.027466 | -0.036621 | 0.022889 | -0.018311 | -0.14191 | 0.37537 | 0.72784 | 0.068664 | 0.21057 | 0.22888 | 123.3078 | 122.937 | 52.4277 | -122.85 | 123.2895 | 123.143 | 69.1452 | -123.056
2572.0156 | 123.0331 | -51.059 | 71.8552 | -0.22141 | 0.0093717 | 0.069746 | 0.071585 | 0.12928 | -0.0034949 | -0.0057957 | -0.11459 | -0.010408 | 0.064691 | 0.055903 | 0.0063446 | -0.012187 | 71.4981 | 71.7133 | 0.99335 | -51.4023 | 71.7499 | -51.2741 | -51.3794 | -50.5966 | 17.8253 | -51.0361 | 71.9055 | 71.814 | -51.2787 | -51.2924 | -0.21515 | -0.32044 | -0.10529 | 122.7722 | -0.34332 | -0.022888 | -0.35706 | -0.21973 | -0.23346 | 0.050354 | 0.46234 | 0.022888 | 0.25635 | -0.041199 | 122.8088 | 122.5571 | 52.0523 | -123.2346 | 122.9645 | 122.8729 | 68.8843 | -123.1476
2573.0156 | 123.0606 | -51.2741 | 71.6858 | 0.19821 | 0.014926 | 0.068678 | 0.072867 | 0.1295 | 0.00013675 | -0.0075047 | -0.168 | -0.0069898 | 0.062982 | 0.058894 | 0.0057038 | -0.013255 | 71.5713 | 71.7545 | 0.9613 | -51.4069 | 71.8918 | -51.2741 | -51.3611 | -50.7706 | 17.6788 | -51.3107 | 71.8002 | 71.7178 | -51.4252 | -51.4572 | 0 | -0.086975 | 0.20599 | 123.0286 | -0.13275 | -0.045776 | -0.11444 | -0.15106 | -0.1831 | 0.11444 | 0.50354 | -0.036621 | 0.14648 | 0.032043 | 123.1659 | 122.8455 | 52.2354 | -123.0469 | 123.0743 | 122.9919 | 68.9529 | -123.143
2574.0156 | 123.0789 | -51.1505 | 71.6904 | -0.19089 | 0.01044 | 0.068037 | 0.069449 | 0.12928 | -0.0024269 | -0.0072911 | -0.11459 | -0.011689 | 0.064478 | 0.054835 | 0.0042084 | -0.010905 | 71.8506 | 72.0978 | 1.1261 | -50.9903 | 72.1252 | -50.8987 | -50.972 | -50.5096 | 17.8207 | -50.9628 | 72.0154 | 71.8781 | -51.2192 | -51.3107 | 0.25177 | 0.17853 | 0.43487 | 123.2483 | 0.16022 | -0.01831 | 0.16022 | -0.068664 | -0.16022 | 0.32501 | 0.64087 | 0.18768 | 0.3479 | 0.18768 | 123.2758 | 123.0011 | 52.2766 | -122.6624 | 123.1659 | 123.0286 | 68.9713 | -123.0011
2575.0156 | 123.0698 | -51.3886 | 71.5713 | -0.023041 | 0.017276 | 0.066328 | 0.074362 | 0.12758 | 0.0046227 | -0.0051547 | 0.11429 | -0.0089124 | 0.063196 | 0.056544 | 0.011258 | -0.012828 | 70.8893 | 71.0358 | 0.81024 | -51.9791 | 71.2555 | -51.8051 | -51.8692 | -50.9354 | 17.8345 | -51.4252 | 71.6171 | 71.4844 | -51.5991 | -51.6403 | -0.41656 | -0.48065 | -0.31586 | 122.4243 | -0.59051 | -0.10986 | -0.68207 | -0.21057 | -0.25177 | 0.045776 | 0.45319 | -0.036621 | 0.21515 | -0.086975 | 122.644 | 122.2778 | 52.1988 | -123.4406 | 123.0057 | 122.8729 | 69.223 | -123.2117
2576.0156 | 123.1293 | -51.5442 | 71.3333 | -0.17563 | 0.010867 | 0.067823 | 0.069876 | 0.12715 | -0.0069129 | -0.0072911 | -0.099335 | -0.0089124 | 0.063623 | 0.057398 | 0.0074126 | -0.011119 | 71.1685 | 71.3516 | 0.84686 | -51.741 | 71.4066 | -51.6403 | -51.7227 | -51.0681 | 17.8574 | -51.6266 | 71.3699 | 71.3242 | -51.7548 | -51.796 | -0.096131 | -0.17853 | 0.073242 | 122.8958 | -0.19684 | -0.018311 | -0.16479 | -0.21057 | -0.25177 | 0.036621 | 0.47607 | -0.082398 | 0.16937 | -0.009155 | 122.9507 | 122.7127 | 52.3911 | -123.056 | 122.9141 | 122.8683 | 69.4016 | -123.1293
2577.0156 | 123.0698 | -52.0386 | 70.8801 | -0.24429 | 0.010867 | 0.066541 | 0.07479 | 0.12779 | -0.0019995 | -0.0077183 | -0.15274 | -0.011049 | 0.06341 | 0.056758 | 0.0091216 | -0.011333 | 70.6787 | 70.9076 | 0.90637 | -52.1667 | 70.9717 | -52.0981 | -52.1805 | -51.5579 | 17.5598 | -52.1255 | 70.9763 | 70.8893 | -52.2446 | -52.2766 | -0.059509 | -0.14191 | 0.091553 | 122.9462 | -0.12817 | 0.013733 | -0.20142 | -0.20599 | -0.23804 | 0.09613 | 0.48065 | -0.086975 | 0.15106 | 0.009155 | 123.0103 | 122.7173 | 52.9449 | -123.0606 | 123.0148 | 122.9279 | 69.5984 | -123.1567
2578.0156 | 123.1018 | -53.096 | 69.7861 | 0.55679 | 0.0083035 | 0.068037 | 0.072226 | 0.13014 | -0.00071785 | -0.0083591 | -0.053558 | -0.011689 | 0.062128 | 0.055262 | 0.0063446 | -0.011333 | 69.5343 | 69.7449 | 0.70038 | -53.3844 | 69.7449 | -53.27 | -53.3615 | -52.5879 | 17.0059 | -53.1876 | 69.8227 | 69.722 | -53.3203 | -53.3432 | -0.17395 | -0.2655 | -0.041199 | 122.8409 | -0.28839 | -0.022888 | -0.25177 | -0.2243 | -0.24719 | 0.036621 | 0.50812 | -0.091553 | 0.15564 | -0.064087 | 122.8409 | 122.6303 | 53.7964 | -123.1476 | 122.9187 | 122.818 | 70.1019 | -123.1293
2579.0156 | 123.0743 | -52.2079 | 70.7336 | -0.32822 | 0.01578 | 0.068037 | 0.070731 | 0.12736 | 0.0020593 | -0.0049411 | -0.19852 | -0.0093396 | 0.063623 | 0.056758 | 0.0082672 | -0.010905 | 70.5048 | 70.7199 | 0.75531 | -52.3544 | 70.8435 | -52.2217 | -52.3132 | -51.7044 | 17.2852 | -52.3544 | 70.8801 | 70.7153 | -52.3773 | -52.446 | -0.013733 | -0.10529 | 0.10986 | 122.9279 | -0.14648 | -0.041199 | -0.22888 | -0.16937 | -0.23804 | 0.14648 | 0.50354 | -0.14648 | 0.091553 | -0.018311 | 123.0515 | 122.7127 | 52.9633 | -123.0469 | 123.0881 | 122.9233 | 69.4931 | -123.1796
2580.0156 | 123.0423 | -52.8259 | 70.1157 | 0.0914 | 0.017276 | 0.069105 | 0.072867 | 0.12608 | 0.0018457 | -0.0034457 | 0.16006 | -0.0069898 | 0.071741 | 0.059321 | 0.0080536 | -0.015392 | 69.8456 | 69.9875 | 0.67749 | -53.0685 | 70.2347 | -52.8992 | -52.9953 | -52.2217 | 16.8594 | -53.009 | 70.1889 | 70.0653 | -53.0228 | -53.0457 | -0.073242 | -0.16937 | 0.11902 | 122.8134 | -0.24261 | -0.073242 | -0.27008 | -0.19684 | -0.21973 | 0.073242 | 0.60425 | -0.18311 | 0.036621 | -0.050354 | 123.0606 | 122.6715 | 53.5034 | -123.111 | 123.0148 | 122.8912 | 69.6854 | -123.1613
2581.0156 | 123.0469 | -52.977 | 69.96 | -0.22903 | 0.012362 | 0.068891 | 0.073721 | 0.12822 | -0.0015723 | -0.0047275 | -0.061188 | -0.010835 | 0.064478 | 0.058894 | 0.004422 | -0.012401 | 69.5297 | 69.8502 | 0.68207 | -53.2333 | 69.9921 | -53.1281 | -53.2242 | -52.478 | 16.9968 | -53.1189 | 70.0333 | 69.9326 | -53.1967 | -53.2333 | -0.15106 | -0.24719 | 0.032043 | 122.8271 | -0.25635 | -0.009155 | -0.4303 | -0.21973 | -0.25635 | 0.073242 | 0.49896 | -0.14191 | 0.11444 | -0.027466 | 122.9691 | 122.5067 | 53.6591 | -123.1842 | 123.0103 | 122.9095 | 69.9738 | -123.1934
2582.0156 | 123.0927 | -52.0935 | 70.8069 | -0.24429 | 0.010013 | 0.070173 | 0.067954 | 0.12843 | -0.0039221 | -0.0066501 | -0.11459 | -0.0093396 | 0.060419 | 0.056117 | 0.0074126 | -0.01176 | 70.6741 | 70.9305 | 0.86517 | -52.2034 | 70.9305 | -52.1164 | -52.2217 | -51.6541 | 17.8024 | -52.1347 | 70.8069 | 70.7291 | -52.3132 | -52.3453 | -0.022888 | -0.12817 | 0.1236 | 123.024 | -0.10986 | 0.018311 | -0.13275 | -0.21973 | -0.25177 | 0 | 0.43945 | -0.041199 | 0.21057 | -0.07782 | 123.024 | 122.7676 | 52.9587 | -123.0286 | 122.9004 | 122.8226 | 69.8959 | -123.1522
2583.0156 | 123.0194 | -52.6932 | 70.253 | -0.22141 | 0.013003 | 0.072096 | 0.071799 | 0.12864 | -0.00050425 | -0.0055821 | -0.168 | -0.010835 | 0.061273 | 0.056544 | 0.0050628 | -0.010478 | 69.9966 | 70.1981 | 0.62714 | -52.89 | 70.3629 | -52.7481 | -52.858 | -52.2675 | 17.3904 | -52.7985 | 70.3583 | 70.2667 | -52.8717 | -52.8992 | -0.054932 | -0.16479 | 0.10986 | 122.8912 | -0.19684 | -0.032044 | -0.25635 | -0.17853 | -0.20599 | 0.10529 | 0.42572 | -0.10529 | 0.10071 | 0.013733 | 123.056 | 122.6898 | 53.3203 | -123.111 | 123.0515 | 122.9599 | 70.0836 | -123.1522
2584.0156 | 123.1659 | -51.6037 | 71.1639 | -0.076447 | 0.0074491 | 0.073377 | 0.068594 | 0.12758 | -0.0028541 | -0.0094273 | -0.068817 | -0.012117 | 0.061701 | 0.057185 | 0.0057038 | -0.011119 | 71.1136 | 71.347 | 0.9201 | -51.7914 | 71.3287 | -51.6632 | -51.7731 | -50.9445 | 18.6447 | -51.4435 | 71.4111 | 71.3242 | -51.6861 | -51.796 | -0.059509 | -0.16937 | 0.16479 | 122.9507 | -0.18768 | -0.018311 | -0.050354 | -0.082397 | -0.19226 | 0.24719 | 0.65918 | 0.16022 | 0.35248 | 0.16022 | 122.9324 | 122.7173 | 52.5238 | -122.937 | 123.0148 | 122.9279 | 70.2484 | -122.9599
2585.0156 | 123.0515 | -51.6815 | 71.2189 | 0.14481 | 0.01514 | 0.069319 | 0.073508 | 0.12907 | 0.0033411 | -0.0040867 | 0.19058 | -0.007417 | 0.063196 | 0.056971 | 0.0093354 | -0.012187 | 71.1182 | 71.2692 | 0.76446 | -51.8555 | 71.4249 | -51.7227 | -51.8143 | -51.265 | 18.338 | -51.9562 | 71.2875 | 71.1548 | -51.915 | -51.9653 | -0.041198 | -0.13275 | 0.20599 | 122.9507 | -0.17395 | -0.041199 | -0.10071 | -0.23346 | -0.28381 | 0.068665 | 0.41656 | -0.27466 | 0.009155 | -0.064087 | 123.1064 | 122.7997 | 52.446 | -123.0331 | 122.9691 | 122.8363 | 70.0195 | -123.1842
2586.0156 | 123.1155 | -51.8646 | 71.0312 | -0.18326 | 0.0078763 | 0.069959 | 0.071158 | 0.12843 | -0.0034949 | -0.0057957 | -0.084076 | -0.0097668 | 0.059778 | 0.057398 | 0.0059174 | -0.010905 | 70.7932 | 71.0403 | 0.91095 | -52.1347 | 71.022 | -52.0248 | -52.1164 | -51.3657 | 18.4296 | -51.9882 | 71.0815 | 70.9991 | -52.0615 | -52.1072 | -0.16022 | -0.25177 | -0.009155 | 122.905 | -0.27008 | -0.018311 | -0.23804 | -0.19684 | -0.24262 | 0.050354 | 0.49896 | -0.1236 | 0.11902 | -0.032043 | 122.8867 | 122.6578 | 52.7756 | -123.1476 | 122.9462 | 122.8638 | 70.2942 | -123.1384
2587.0156 | 122.9965 | -51.9104 | 71.0129 | -0.21378 | 0.011508 | 0.067396 | 0.072867 | 0.13014 | 0.00056395 | -0.0079319 | -0.19089 | -0.011262 | 0.063623 | 0.059321 | 0.008908 | -0.011974 | 70.7611 | 70.9488 | 0.85144 | -52.1255 | 71.1182 | -51.9882 | -52.1164 | -51.4206 | 18.2602 | -52.0477 | 71.1227 | 71.0358 | -52.0844 | -52.1805 | -0.07782 | -0.20599 | 0.10529 | 122.8592 | -0.21515 | -0.009155 | -0.25177 | -0.17395 | -0.27008 | 0.10986 | 0.48981 | -0.13733 | 0.13275 | 0.022889 | 123.0286 | 122.6715 | 52.7618 | -123.1293 | 123.0331 | 122.9462 | 70.1706 | -123.1934
2588.0156 | 123.1018 | -51.0361 | 71.8323 | 3.0363 | 0.010653 | 0.072096 | 0.069663 | 0.12864 | -0.0022131 | -0.0070773 | -0.10696 | -0.011262 | 0.061487 | 0.056971 | 0.007199 | -0.0098374 | 71.8552 | 72.0062 | 1.0345 | -51.1734 | 72.0062 | -51.0635 | -51.1963 | -50.5463 | 18.9148 | -51.2009 | 71.8872 | 71.7911 | -51.2466 | -51.3016 | -0.027466 | -0.16022 | 0.17395 | 123.0423 | -0.13733 | 0.022888 | 0.022889 | -0.21057 | -0.2655 | 0.054932 | 0.48981 | -0.1648 | 0.10071 | -0.041198 | 123.0423 | 122.8912 | 52.0706 | -123.0286 | 122.9233 | 122.8271 | 69.9509 | -123.1338
2589.0156 | 123.024 | -51.5121 | 71.4203 | -0.25192 | 0.0074491 | 0.069319 | 0.071799 | 0.13014 | -0.0013587 | -0.0060093 | -0.20615 | -0.011689 | 0.062982 | 0.057185 | 0.0050628 | -0.010905 | 71.2509 | 71.4203 | 0.78735 | -51.6586 | 71.5805 | -51.5396 | -51.6312 | -50.9995 | 18.4616 | -51.6678 | 71.5439 | 71.4386 | -51.7136 | -51.7685 | -0.027466 | -0.11902 | 0.16022 | 122.9324 | -0.14648 | -0.027465 | -0.16937 | -0.20142 | -0.25635 | 0.1236 | 0.5127 | -0.15564 | 0.10071 | 0.018311 | 123.0927 | 122.7631 | 52.2995 | -123.0515 | 123.056 | 122.9507 | 69.9738 | -123.1888
2590.0156 | 123.0423 | -51.9791 | 70.9167 | 1.4952 | 0.01813 | 0.068464 | 0.072012 | 0.12822 | 0.0020593 | -0.0036595 | -0.076446 | -0.0065626 | 0.062982 | 0.056117 | 0.00784 | -0.012187 | 70.9488 | 71.109 | 0.68207 | -51.9791 | 71.2372 | -51.8417 | -51.9287 | -51.4572 | 18.1686 | -52.2812 | 70.9854 | 70.8801 | -52.2217 | -52.2812 | 0.13733 | 0.050354 | 0.32044 | 123.0881 | 0 | -0.050354 | 0.032044 | -0.24262 | -0.30212 | 0.068665 | 0.52185 | -0.30212 | 0 | -0.036621 | 123.2162 | 122.9279 | 52.6611 | -122.8455 | 122.9645 | 122.8592 | 70.1477 | -123.1979
2591.0156 | 123.1018 | -51.86 | 70.9854 | -0.2977 | 0.010226 | 0.067823 | 0.071799 | 0.12736 | -0.0049903 | -0.0053683 | -0.076446 | -0.010621 | 0.059778 | 0.056544 | 0.0059174 | -0.010478 | 70.8298 | 71.077 | 0.9201 | -52.0386 | 71.0632 | -52.0157 | -52.0798 | -51.3382 | 18.6813 | -51.9287 | 71.0449 | 70.9579 | -52.0752 | -52.1164 | -0.15564 | -0.21973 | 0.077819 | 122.937 | -0.17853 | 0.041199 | -0.15564 | -0.21515 | -0.25635 | 0.059509 | 0.52185 | -0.068665 | 0.18768 | -0.027466 | 122.9233 | 122.6898 | 52.7802 | -123.0652 | 122.905 | 122.818 | 70.5414 | -123.1018
2592.0156 | 123.1705 | -51.6403 | 71.2509 | -0.16037 | 0.0012539 | 0.069746 | 0.069022 | 0.13014 | -0.0041357 | -0.0089999 | -0.053558 | -0.0095532 | 0.06106 | 0.056758 | 0.0074126 | -0.0098374 | 71.3287 | 71.2784 | 0.91553 | -51.7273 | 71.3974 | -51.6541 | -51.7868 | -51.1368 | 19.0384 | -51.7914 | 71.2601 | 71.1777 | -51.8784 | -51.8967 | -0.013733 | -0.14648 | 0.14648 | 122.9187 | -0.086975 | 0.059509 | 0.077819 | -0.23804 | -0.25635 | 0.009155 | 0.50354 | -0.15106 | 0.10529 | -0.073243 | 123.0377 | 122.9691 | 52.5558 | -123.0377 | 122.9004 | 122.818 | 70.6787 | -123.1476
2593.0156 | 123.0469 | -52.1667 | 70.784 | -0.22903 | 0.010867 | 0.068891 | 0.071585 | 0.12864 | 0.0012047 | -0.0077183 | -0.17563 | -0.010835 | 0.061914 | 0.057826 | 0.0086944 | -0.011119 | 70.4956 | 70.6833 | 0.88348 | -52.4185 | 70.8298 | -52.2903 | -52.3911 | -51.6724 | 18.7042 | -52.3727 | 70.8298 | 70.7336 | -52.3865 | -52.4368 | -0.1236 | -0.2243 | 0.045776 | 122.85 | -0.25177 | -0.027466 | -0.28839 | -0.21973 | -0.27008 | 0.045776 | 0.49439 | -0.20599 | 0.064087 | -0.050354 | 122.9965 | 122.6624 | 53.0502 | -123.175 | 122.9965 | 122.9004 | 70.871 | -123.2208
2594.0156 | 123.1613 | -50.8301 | 72.0337 | -0.19852 | 0.0080899 | 0.068464 | 0.069235 | 0.13035 | -0.0052039 | -0.0075047 | -0.053558 | -0.010621 | 0.06106 | 0.054194 | 0.00079042 | -0.014964 | 71.9284 | 72.2076 | 1.1673 | -51.0132 | 72.1298 | -50.9171 | -51.0452 | -50.1572 | 19.1528 | -51.0178 | 72.0474 | 71.9833 | -51.059 | -51.0773 | -0.086975 | -0.21515 | 0.096131 | 123.0377 | -0.18311 | 0.032043 | -0.10529 | -0.22888 | -0.24719 | 0.013733 | 0.67291 | -0.18768 | 0.05951 | -0.050354 | 122.9599 | 122.7585 | 51.9974 | -123.0789 | 122.8775 | 122.8134 | 69.9829 | -123.111
2595.0156 | 123.0194 | -51.004 | 71.8826 | -0.03067 | 0.018558 | 0.065687 | 0.075644 | 0.12993 | 0.0041955 | -0.0049411 | -0.00015237 | -0.0084852 | 0.065546 | 0.057398 | 0.0093354 | -0.014323 | 71.5942 | 71.6995 | 0.80109 | -51.3886 | 71.8689 | -51.2833 | -51.3794 | -50.5234 | 19.5236 | -51.1047 | 71.9604 | 71.8597 | -51.21 | -51.2558 | -0.27924 | -0.37537 | -0.013733 | 122.7036 | -0.38452 | -0.009155 | -0.28839 | -0.20599 | -0.25177 | 0.07782 | 0.48065 | -0.10071 | 0.15106 | -0.022888 | 122.8729 | 122.5983 | 51.8051 | -123.262 | 122.9645 | 122.8638 | 70.5276 | -123.1384
2596.0156 | 123.1979 | -51.0086 | 71.8369 | -0.053558 | 0.0074491 | 0.071027 | 0.069449 | 0.12693 | -0.0052039 | -0.0072911 | -0.084076 | -0.010621 | 0.061914 | 0.05868 | 0.00549 | -0.0087692 | 71.5073 | 71.7636 | 0.89264 | -51.4297 | 71.759 | -51.3016 | -51.4114 | -50.6195 | 19.6014 | -51.091 | 71.7636 | 71.7316 | -51.2512 | -51.2878 | -0.29297 | -0.40283 | -0.07782 | 122.7722 | -0.42114 | -0.018311 | -0.32959 | -0.24262 | -0.27924 | -0.073242 | 0.3891 | -0.082397 | 0.19684 | -0.10529 | 122.7676 | 122.5159 | 51.9012 | -123.2483 | 122.7722 | 122.7402 | 70.61 | -123.1247
2597.0156 | 123.1018 | -51.6724 | 71.2234 | -0.18326 | 0.010867 | 0.071027 | 0.07009 | 0.12779 | -0.0030677 | -0.0085727 | -0.14511 | -0.0099806 | 0.06106 | 0.055262 | 0.0052764 | -0.012828 | 71.3287 | 71.5851 | 1.0712 | -51.5167 | 71.5622 | -51.4893 | -51.5808 | -51.2146 | 19.1299 | -51.8646 | 71.2784 | 71.1685 | -51.8875 | -51.915 | 0.1831 | 0.091552 | 0.33875 | 123.2574 | 0.15564 | 0.064087 | 0.10528 | -0.21515 | -0.24262 | 0.054931 | 0.45776 | -0.19226 | 0.050354 | -0.054932 | 123.2346 | 123.0011 | 52.7435 | -122.8043 | 122.9507 | 122.8409 | 70.8023 | -123.1384
2598.0156 | 123.1567 | -51.2833 | 71.6354 | 0.11429 | 0.0061673 | 0.071241 | 0.069663 | 0.12843 | -0.0026405 | -0.0075047 | 0.0914 | -0.011689 | 0.061273 | 0.057826 | 0.0059174 | -0.01176 | 71.3699 | 71.5851 | 0.97504 | -51.5121 | 71.6675 | -51.4206 | -51.4893 | -50.8621 | 19.4275 | -51.4206 | 71.6217 | 71.5118 | -51.5442 | -51.5717 | -0.13733 | -0.20599 | 0.032043 | 122.8683 | -0.22888 | -0.022888 | -0.2655 | -0.26093 | -0.28839 | -0.013733 | 0.42114 | -0.13733 | 0.15106 | -0.1236 | 122.9507 | 122.6532 | 52.2583 | -123.1247 | 122.905 | 122.7951 | 70.7108 | -123.2071
2599.0156 | 123.056 | -51.6769 | 71.2372 | -0.25955 | 0.013003 | 0.069532 | 0.073294 | 0.13163 | 0.00056395 | -0.0055821 | -0.19089 | -0.011903 | 0.061273 | 0.055476 | 0.007199 | -0.010265 | 71.3104 | 71.5164 | 0.99335 | -51.7593 | 71.4935 | -51.5991 | -51.7273 | -51.1047 | 19.2673 | -51.8097 | 71.3654 | 71.2738 | -51.8372 | -51.8921 | 0.07782 | -0.050354 | 0.25635 | 123.1934 | -0.082397 | -0.032043 | 0.073242 | -0.16022 | -0.21515 | 0.12817 | 0.5722 | -0.13275 | 0.082398 | 0.036621 | 123.1705 | 122.9874 | 52.6703 | -122.9645 | 123.0423 | 122.9507 | 70.9442 | -123.1293
2600.0156 | 123.1338 | -51.1505 | 71.6812 | -0.14511 | 0.0080899 | 0.072736 | 0.074362 | 0.13014 | 0.0024865 | -0.0051547 | -0.26718 | -0.0086988 | 0.060205 | 0.057826 | 0.007199 | -0.011119 | 71.3654 | 71.7957 | 1.0941 | -51.4526 | 71.7636 | -51.2695 | -51.3794 | -50.6241 | 19.4321 | -51.2787 | 71.759 | 71.6034 | -51.416 | -51.4252 | -0.11902 | -0.22888 | 0.082398 | 122.9462 | -0.30212 | -0.073242 | -0.31586 | -0.2655 | -0.27466 | 0.07782 | 0.52643 | -0.12817 | 0.14648 | -0.077819 | 122.9141 | 122.5159 | 52.2446 | -123.0606 | 122.9095 | 122.7539 | 70.5826 | -123.1064
2601.0156 | 123.0835 | -50.798 | 72.1115 | -0.16037 | 0.0076627 | 0.069746 | 0.073721 | 0.12928 | 0.00056395 | -0.0051547 | -0.16037 | -0.009126 | 0.063196 | 0.054194 | 0.01019 | -0.013683 | 72.0016 | 72.2214 | 1.1215 | -50.9171 | 72.2214 | -50.8163 | -50.9171 | -50.3403 | 20.0226 | -50.8713 | 72.1573 | 72.0383 | -50.972 | -51.059 | -0.01831 | -0.11902 | 0.10986 | 123.0194 | -0.11902 | 0 | -0.10986 | -0.17395 | -0.26093 | 0.045777 | 0.45776 | -0.073242 | 0.18768 | -0.073242 | 123.0194 | 122.7997 | 51.9196 | -123.0286 | 122.9553 | 122.8363 | 70.8206 | -123.1705
2602.0156 | 123.1293 | -51.1093 | 71.7316 | -0.0383 | 0.0074491 | 0.069319 | 0.06774 | 0.12928 | -0.0028541 | -0.0085727 | 0.015106 | -0.010621 | 0.061487 | 0.057185 | 0.0067718 | -0.012401 | 71.6629 | 71.8964 | 0.92926 | -51.2329 | 71.9055 | -51.1368 | -51.2054 | -50.5142 | 19.8624 | -51.1368 | 71.8506 | 71.727 | -51.3153 | -51.3748 | -0.027466 | -0.09613 | 0.17395 | 123.0057 | -0.1236 | -0.027466 | -0.068664 | -0.20599 | -0.2655 | 0.11902 | 0.59509 | -0.027466 | 0.23804 | -0.004577 | 123.0148 | 122.7722 | 52.0386 | -122.937 | 122.9599 | 122.8363 | 70.9717 | -123.1064
2603.0156 | 123.1201 | -51.2833 | 71.5759 | 2.0979 | 0.0074491 | 0.070814 | 0.070944 | 0.12886 | 0.00013675 | -0.0062229 | -0.12222 | -0.011476 | 0.061487 | 0.056117 | 0.007199 | -0.012828 | 71.5164 | 71.6446 | 1.0345 | -51.4618 | 71.6949 | -51.3977 | -51.4664 | -50.7477 | 19.7708 | -51.3199 | 71.6721 | 71.5439 | -51.4755 | -51.5442 | -0.11444 | -0.18311 | 0.11902 | 122.9279 | -0.17853 | 0.004578 | -0.05951 | -0.19226 | -0.26093 | 0.09613 | 0.53558 | -0.036621 | 0.2243 | -0.032044 | 122.9782 | 122.7997 | 52.3178 | -123.0423 | 122.9553 | 122.8271 | 71.0541 | -123.1201
2604.0156 | 123.111 | -51.4435 | 71.4203 | 0.022736 | 0.0076627 | 0.067823 | 0.069663 | 0.13035 | -0.0024269 | -0.0075047 | 0.076141 | -0.012971 | 0.063623 | 0.056758 | 0.0063446 | -0.010051 | 71.3242 | 71.521 | 0.99792 | -51.59 | 71.5942 | -51.4664 | -51.5717 | -50.9674 | 19.5099 | -51.6174 | 71.4706 | 71.3837 | -51.6724 | -51.7044 | -0.022889 | -0.12817 | 0.17395 | 122.9645 | -0.14648 | -0.018311 | -0.09613 | -0.22888 | -0.26093 | 0.050354 | 0.47607 | -0.17395 | 0.086975 | -0.036621 | 123.0377 | 122.7676 | 52.4414 | -122.9919 | 122.9141 | 122.8271 | 70.9534 | -123.1247
2605.0156 | 123.1705 | -51.8097 | 71.0541 | -0.045929 | 0.0063809 | 0.070814 | 0.071372 | 0.12629 | -0.0022131 | -0.0066501 | 0.022736 | -0.011262 | 0.060846 | 0.05633 | 0.0063446 | -0.010905 | 70.9991 | 71.2051 | 1.062 | -51.9058 | 71.2418 | -51.8097 | -51.8967 | -51.1185 | 19.5236 | -51.9287 | 71.2143 | 71.0541 | -51.9699 | -52.0798 | 0 | -0.086975 | 0.18768 | 123.0148 | -0.096131 | -0.009156 | -0.054931 | -0.16022 | -0.27008 | 0.16022 | 0.69122 | -0.11902 | 0.15106 | 0 | 123.0515 | 122.8088 | 52.8717 | -122.9507 | 123.024 | 122.8638 | 71.3333 | -123.1339
2606.0625 | 123.0881 | -51.9012 | 70.903 | 0.16006 | 0.012362 | 0.067823 | 0.070303 | 0.12822 | 0.0033411 | -0.0060093 | 0.15244 | -0.0089124 | 0.062982 | 0.056117 | 0.0093354 | -0.014964 | 70.9991 | 71.1365 | 1.0208 | -51.9562 | 71.2143 | -51.8417 | -51.947 | -51.3931 | 19.4 | -52.0935 | 71.0175 | 70.903 | -52.1439 | -52.2034 | 0.059509 | -0.045776 | 0.31128 | 123.0377 | -0.054932 | -0.009156 | 0.096131 | -0.24261 | -0.30212 | 0.11444 | 0.50812 | -0.19226 | 0.10986 | 0 | 123.1155 | 122.9004 | 52.9221 | -122.85 | 122.9187 | 122.8043 | 71.3013 | -123.1064
2607.0156 | 123.1384 | -52.1301 | 70.7611 | -0.17563 | 0.0068081 | 0.071027 | 0.069449 | 0.13035 | -0.0037085 | -0.0096409 | 0.083771 | -0.0084852 | 0.061273 | 0.056117 | 0.0093354 | -0.013469 | 70.9534 | 70.6284 | 0.93384 | -52.1301 | 70.9351 | -52.1072 | -52.1851 | -51.6129 | 19.2032 | -52.2308 | 70.8115 | 70.7245 | -52.3087 | -52.3773 | 0.022888 | -0.054932 | 0.17395 | 122.7585 | 0 | 0.054932 | 0.19226 | -0.17853 | -0.24719 | 0.050354 | 0.51727 | -0.10071 | 0.14648 | -0.036621 | 123.0652 | 123.0835 | 53.064 | -122.9462 | 122.9416 | 122.8546 | 71.3333 | -123.1384
2608.0156 | 123.1064 | -51.535 | 71.347 | 0.022736 | 0.0083035 | 0.069532 | 0.070944 | 0.12971 | -0.0019995 | -0.0083591 | 0.076141 | -0.0099806 | 0.062342 | 0.053767 | 0.0037812 | -0.010905 | 71.1227 | 71.3425 | 1.0483 | -51.7593 | 71.4111 | -51.6449 | -51.709 | -50.9903 | 19.5419 | -51.6312 | 71.4432 | 71.3196 | -51.709 | -51.7776 | -0.10986 | -0.17395 | 0.064087 | 122.8775 | -0.2243 | -0.050354 | -0.2243 | -0.17395 | -0.24261 | 0.09613 | 0.54474 | -0.096131 | 0.14648 | -0.027466 | 122.9462 | 122.6578 | 52.5833 | -123.056 | 122.9782 | 122.8546 | 71.077 | -123.1247
2609.0156 | 123.262 | -51.7044 | 71.1365 | -0.16037 | 0.0083035 | 0.069105 | 0.070517 | 0.12822 | -0.0060585 | -0.0049411 | -0.091705 | -0.011903 | 0.06106 | 0.056758 | 0.0069854 | -0.01176 | 71.196 | 71.4386 | 1.1536 | -51.7502 | 71.3791 | -51.6449 | -51.7548 | -51.0635 | 19.8441 | -51.828 | 71.2875 | 71.1502 | -51.8692 | -51.947 | 0.05951 | -0.050354 | 0.24261 | 123.143 | -0.045776 | 0.004578 | 0.059509 | -0.16479 | -0.24261 | 0.15106 | 0.64087 | -0.1236 | 0.11902 | 0.013733 | 123.0835 | 122.9004 | 52.858 | -122.8912 | 122.9919 | 122.8546 | 71.5485 | -123.0835
2610.0156 | 123.1384 | -52.6245 | 70.2255 | -0.015411 | 0.0068081 | 0.069746 | 0.069235 | 0.12779 | -0.0019995 | -0.0062229 | -0.0077819 | -0.011689 | 0.061701 | 0.056971 | 0.0065582 | -0.010051 | 70.2164 | 70.4361 | 0.9613 | -52.6566 | 70.4544 | -52.5558 | -52.6611 | -51.8326 | 19.4138 | -52.5467 | 70.5276 | 70.3537 | -52.7206 | -52.8168 | 0.068665 | -0.036621 | 0.22888 | 123.0606 | -0.032043 | 0.004578 | -0.009155 | -0.09613 | -0.19226 | 0.30212 | 0.79193 | 0.07782 | 0.27008 | 0.12817 | 123.0789 | 122.8409 | 53.5858 | -122.8867 | 123.1522 | 122.9782 | 72.0383 | -123.0423
2611.0156 | 123.0789 | -52.6428 | 70.2713 | -0.12985 | 0.010226 | 0.069959 | 0.070517 | 0.12971 | 0.00056395 | -0.0081455 | -0.18326 | -0.010194 | 0.059992 | 0.054835 | 0.008908 | -0.011546 | 70.0424 | 70.2484 | 0.95215 | -52.8854 | 70.2576 | -52.7893 | -52.8809 | -52.1576 | 19.4321 | -52.7206 | 70.2667 | 70.1614 | -52.858 | -52.9083 | -0.14648 | -0.23804 | -0.013733 | 122.8912 | -0.24262 | -0.004578 | -0.22888 | -0.21515 | -0.2655 | -0.004577 | 0.48523 | -0.07782 | 0.18768 | -0.10986 | 122.9004 | 122.6852 | 53.595 | -123.1522 | 122.9095 | 122.8043 | 72.0749 | -123.1796
2612.0156 | 123.111 | -51.3199 | 71.5302 | 0.12192 | 0.0089443 | 0.06825 | 0.068808 | 0.12608 | -0.0013587 | -0.0070773 | 0.09903 | -0.0097668 | 0.060205 | 0.057398 | 0.007199 | -0.013255 | 71.4294 | 71.6309 | 1.0483 | -51.4435 | 71.727 | -51.3245 | -51.4206 | -50.853 | 20.1782 | -51.4801 | 71.6125 | 71.4661 | -51.535 | -51.6083 | -0.004578 | -0.10071 | 0.19684 | 122.9507 | -0.1236 | -0.022888 | -0.10071 | -0.21515 | -0.28839 | 0.082398 | 0.46692 | -0.16022 | 0.12817 | -0.064087 | 123.0469 | 122.7493 | 52.3682 | -122.9507 | 122.9324 | 122.7859 | 71.4981 | -123.1384
2613.0156 | 123.1934 | -50.5051 | 72.3541 | -0.10696 | 0.0085171 | 0.06825 | 0.069663 | 0.12758 | -0.00071785 | -0.0066501 | -0.03067 | -0.0099806 | 0.061273 | 0.05633 | 0.0069854 | -0.012401 | 72.2626 | 72.4686 | 1.0071 | -50.6561 | 72.464 | -50.5692 | -50.6607 | -49.9191 | 20.9976 | -50.473 | 72.4319 | 72.2992 | -50.6836 | -50.7523 | -0.064087 | -0.15564 | 0.10986 | 122.9736 | -0.15106 | 0.004578 | -0.091553 | -0.17853 | -0.24719 | 0.07782 | 0.58594 | 0.032044 | 0.27924 | -0.054932 | 122.9691 | 122.7676 | 51.5121 | -123.0148 | 122.937 | 122.8043 | 71.5027 | -123.1064
2614.0156 | 123.0927 | -51.1917 | 71.6629 | 0.076141 | 0.0080899 | 0.069105 | 0.070303 | 0.12736 | -0.0022131 | -0.0057957 | 0.0914 | -0.010408 | 0.061914 | 0.056758 | 0.009549 | -0.013683 | 71.7453 | 71.9147 | 0.89264 | -51.2238 | 71.9696 | -51.1047 | -51.1826 | -50.6424 | 20.7687 | -51.3428 | 71.7773 | 71.6446 | -51.3977 | -51.4572 | 0.086975 | 0.009155 | 0.3067 | 123.1064 | -0.032044 | -0.041199 | 0.082397 | -0.20599 | -0.2655 | 0.11444 | 0.54932 | -0.15106 | 0.11444 | -0.018311 | 123.1613 | 122.937 | 52.0844 | -122.8455 | 122.9691 | 122.8363 | 71.9604 | -123.1201
2615.0156 | 123.1522 | -51.2604 | 71.608 | -0.053558 | 0.0076627 | 0.070173 | 0.071158 | 0.12971 | -0.0013587 | -0.0045139 | 0.022736 | -0.009126 | 0.062128 | 0.055476 | 0.007199 | -0.010051 | 71.5759 | 71.6904 | 0.79193 | -51.4389 | 71.7361 | -51.297 | -51.384 | -50.7431 | 20.6726 | -51.3931 | 71.6125 | 71.5164 | -51.4709 | -51.5442 | -0.036621 | -0.1236 | 0.12817 | 122.9507 | -0.17853 | -0.054932 | -0.032043 | -0.21057 | -0.28381 | 0.004578 | 0.51727 | -0.13275 | 0.15106 | -0.091553 | 122.9965 | 122.8363 | 52.0523 | -122.9919 | 122.8729 | 122.7768 | 71.933 | -123.1522
2616.0156 | 123.1247 | -51.123 | 71.7545 | 0.12955 | 0.0078763 | 0.069319 | 0.069663 | 0.12928 | -7.6852e-05 | -0.0070773 | 0.19058 | -0.0099806 | 0.061273 | 0.056544 | 0.0063446 | -0.012614 | 71.5302 | 71.7133 | 0.7782 | -51.384 | 71.7819 | -51.2512 | -51.3611 | -50.6149 | 20.636 | -51.1871 | 71.8185 | 71.7041 | -51.3199 | -51.3886 | -0.12817 | -0.23804 | 0.027465 | 122.8363 | -0.26093 | -0.022888 | -0.22431 | -0.19684 | -0.2655 | 0.064086 | 0.50812 | -0.064087 | 0.20142 | -0.050354 | 122.905 | 122.6532 | 51.9012 | -123.1155 | 122.9416 | 122.8271 | 71.759 | -123.143
2617.0156 | 123.1018 | -51.4847 | 71.3516 | -0.023041 | 0.0065945 | 0.071027 | 0.072012 | 0.12864 | -0.00071785 | -0.0062229 | 0.022736 | -0.0099806 | 0.061487 | 0.055262 | 0.0059174 | -0.01176 | 71.3333 | 71.4844 | 0.78278 | -51.5991 | 71.6034 | -51.4755 | -51.5533 | -50.9674 | 20.462 | -51.7364 | 71.4478 | 71.3242 | -51.7364 | -51.7639 | 0.009155 | -0.068665 | 0.25177 | 122.9691 | -0.11444 | -0.045776 | -0.018311 | -0.25177 | -0.27924 | 0.09613 | 0.51727 | -0.25177 | 0.027466 | -0.027466 | 123.0881 | 122.818 | 52.2675 | -122.905 | 122.9324 | 122.8088 | 71.9467 | -123.1155
2618.0156 | 123.1155 | -51.4389 | 71.4523 | 0.19058 | 0.013858 | 0.06761 | 0.066672 | 0.12886 | -0.00029045 | -0.0051547 | 0.22873 | -0.0099806 | 0.063196 | 0.055689 | 0.0091216 | -0.012828 | 71.4935 | 71.4569 | 0.78735 | -51.4572 | 71.5622 | -51.4343 | -51.503 | -50.6744 | 27.9968 | -51.5442 | 71.6171 | 71.4249 | -51.6312 | -51.7044 | 0.004578 | -0.064087 | 0.10986 | 122.8958 | -0.01831 | 0.045777 | 0.041198 | -0.19226 | -0.2655 | 0.16479 | 0.76447 | -0.10529 | 0.16022 | -0.027466 | 123.0011 | 122.9324 | 52.2263 | -122.9553 | 123.056 | 122.8638 | 79.4357 | -123.1567
2619.0156 | 123.1201 | -51.1322 | 71.7133 | 0.030365 | 0.0087307 | 0.071027 | 0.073935 | 0.12779 | -0.0013587 | -0.0043003 | 0.022736 | -0.011049 | 0.060205 | 0.056117 | 0.0052764 | -0.012187 | 71.5668 | 71.4981 | 0.75531 | -51.4801 | 71.6949 | -51.3702 | -51.4023 | -50.5783 | 27.8824 | -51.2146 | 71.7865 | 71.7133 | -51.3565 | -51.4114 | -0.23804 | -0.27008 | -0.018311 | 122.6303 | -0.3479 | -0.07782 | -0.14648 | -0.2243 | -0.27924 | 0.073242 | 0.55389 | -0.082398 | 0.19684 | 0 | 122.8271 | 122.699 | 51.8875 | -123.1155 | 122.9187 | 122.8455 | 79.0146 | -123.1247
2620.0156 | 123.0789 | -50.7156 | 72.1573 | 0.15244 | 0.010226 | 0.069532 | 0.071585 | 0.12822 | -7.6852e-05 | -0.0060093 | 0.19058 | -0.010408 | 0.063623 | 0.056758 | 0.008908 | -0.013042 | 72.0566 | 72.2305 | 1.1307 | -50.9125 | 72.2717 | -50.7751 | -50.8759 | -50.0793 | 28.363 | -50.6012 | 72.258 | 72.1161 | -50.8713 | -50.9491 | -0.059509 | -0.16022 | 0.11444 | 122.9462 | -0.19684 | -0.036622 | -0.10071 | -0.15564 | -0.23346 | 0.10071 | 0.63629 | 0.11444 | 0.3479 | -0.041199 | 122.9874 | 122.7722 | 51.8463 | -123.0331 | 122.9736 | 122.8317 | 79.0787 | -123.1064
2621.0156 | 123.1384 | -50.5829 | 72.2992 | -0.0383 | 0.0070217 | 0.068891 | 0.07009 | 0.12843 | -0.00071785 | -0.0057957 | 0.076141 | -0.011689 | 0.058924 | 0.057398 | 0.0063446 | -0.011333 | 72.02 | 72.2305 | 0.9201 | -50.8301 | 72.3267 | -50.7111 | -50.8209 | -50.0336 | 28.6011 | -50.647 | 72.3358 | 72.2488 | -50.8026 | -50.8118 | -0.12817 | -0.23804 | 0.027466 | 122.8134 | -0.24719 | -0.009155 | -0.27924 | -0.21973 | -0.22888 | 0.036621 | 0.54932 | -0.064087 | 0.16479 | -0.050354 | 122.9095 | 122.6028 | 51.503 | -123.1201 | 122.9187 | 122.8317 | 79.184 | -123.111
2622.0156 | 123.1247 | -51.5213 | 71.3013 | 0.17532 | 0.010867 | 0.068464 | 0.070944 | 0.12779 | -0.00071785 | -0.0064365 | 0.19058 | -0.011049 | 0.061487 | 0.056117 | 0.0069854 | -0.012401 | 71.1182 | 71.2784 | 0.7782 | -51.8326 | 71.283 | -51.7181 | -51.828 | -50.8575 | 26.8845 | -51.6632 | 71.4294 | 71.3058 | -51.7044 | -51.7502 | -0.19684 | -0.3067 | -0.018311 | 122.7997 | -0.31128 | -0.004578 | -0.18311 | -0.18311 | -0.22888 | 0.12817 | 0.66376 | -0.14191 | 0.086975 | 0.004577 | 122.8043 | 122.6395 | 52.2995 | -123.1293 | 122.9507 | 122.8271 | 78.4058 | -123.0515
2623.0156 | 123.0927 | -52.4506 | 70.4041 | 0.037994 | 0.0087307 | 0.069959 | 0.070517 | 0.13035 | -0.0011451 | -0.0075047 | 0.35843 | -0.0084852 | 0.062128 | 0.057185 | 0.0084808 | -0.0098374 | 70.2667 | 70.3995 | 0.59052 | -52.684 | 70.5002 | -52.5513 | -52.6428 | -51.9058 | 25.7629 | -52.5925 | 70.4681 | 70.3766 | -52.684 | -52.7344 | -0.10071 | -0.19226 | 0.09613 | 122.85 | -0.23346 | -0.041199 | -0.13733 | -0.23346 | -0.28381 | 0.064087 | 0.54474 | -0.14191 | 0.14191 | -0.027466 | 122.9507 | 122.7173 | 53.0411 | -123.0469 | 122.9187 | 122.8271 | 78.2135 | -123.1384
2624.0156 | 123.1247 | -51.5625 | 71.2921 | -1.3963 | 0.011508 | 0.066755 | 0.070517 | 0.12758 | 0.00056395 | -0.0049411 | 0.16006 | -0.0078442 | 0.060633 | 0.055476 | 0.010617 | -0.013042 | 71.3196 | 71.5393 | 1.0986 | -51.6357 | 71.5073 | -51.5213 | -51.5991 | -50.9171 | 25.209 | -51.5488 | 71.3699 | 71.2463 | -51.7456 | -51.8051 | 0.041199 | -0.036621 | 0.21515 | 123.1018 | -0.073242 | -0.036621 | 0.027466 | -0.1831 | -0.24262 | 0.07782 | 0.64545 | 0.013733 | 0.25635 | -0.045776 | 123.0698 | 122.8821 | 52.6611 | -122.8912 | 122.9324 | 122.8088 | 76.7715 | -123.0972
2625.0156 | 123.0972 | -52.4368 | 70.3812 | 0.15244 | 0.0089443 | 0.068037 | 0.068808 | 0.12971 | 0.00099115 | -0.0055821 | 0.16006 | -0.0086988 | 0.060419 | 0.057398 | 0.0082672 | -0.01411 | 70.1889 | 70.34 | 0.80109 | -52.7847 | 70.3583 | -52.6703 | -52.7756 | -51.8234 | 22.0276 | -52.5925 | 70.5048 | 70.3995 | -52.6657 | -52.684 | -0.23346 | -0.33874 | -0.022889 | 122.7768 | -0.3479 | -0.009155 | -0.19226 | -0.22888 | -0.24719 | 0.1236 | 0.6134 | -0.15564 | 0.091553 | 0.01831 | 122.7951 | 122.6257 | 53.2379 | -123.1567 | 122.9416 | 122.8363 | 74.4644 | -123.0652
2626.0156 | 123.1567 | -51.6724 | 71.1365 | 0.12192 | 0.013431 | 0.070387 | 0.069449 | 0.1295 | 0.0033411 | -0.0032321 | 0.20584 | -0.011476 | 0.061487 | 0.055903 | 0.0093354 | -0.011546 | 71.1502 | 71.3058 | 0.93384 | -51.7868 | 71.3196 | -51.7044 | -51.8005 | -50.9537 | 22.9568 | -51.4435 | 71.3287 | 71.1914 | -51.8738 | -51.915 | -0.032044 | -0.12817 | 0.1831 | 122.9782 | -0.11444 | 0.013733 | 0.013733 | -0.20142 | -0.24262 | 0.19226 | 0.71869 | 0.22888 | 0.4715 | 0.054931 | 122.9919 | 122.8226 | 52.6062 | -122.937 | 123.0011 | 122.8638 | 74.6292 | -123.0515
2627.0156 | 123.0835 | -52.0477 | 70.7932 | 0.068512 | 0.0087307 | 0.068891 | 0.068381 | 0.13078 | -0.0032813 | -0.0064365 | 0.10666 | -0.011049 | 0.059778 | 0.056117 | 0.0057038 | -0.010478 | 70.784 | 70.9671 | 0.81482 | -52.1301 | 71.0449 | -51.9745 | -52.0844 | -51.4526 | 22.2839 | -52.0844 | 70.9442 | 70.8389 | -52.2537 | -52.2903 | 0.073242 | -0.036622 | 0.25177 | 123.0148 | -0.082398 | -0.045776 | -0.009155 | -0.20599 | -0.24262 | 0.15106 | 0.59509 | -0.036622 | 0.20599 | 0.045776 | 123.0927 | 122.8317 | 52.8625 | -122.8775 | 122.9919 | 122.8867 | 74.3317 | -123.0835
2628.0156 | 123.1522 | -52.6382 | 70.1981 | 0.18295 | 0.012576 | 0.069319 | 0.070517 | 0.12779 | 0.0027001 | -0.0066501 | -0.03067 | -0.0093396 | 0.062128 | 0.057185 | 0.008908 | -0.013469 | 70.4407 | 70.4773 | 0.71869 | -52.6566 | 70.4636 | -52.5375 | -52.6474 | -51.9562 | 22.3434 | -52.7435 | 70.3217 | 70.2118 | -52.8259 | -52.8763 | 0.10071 | -0.009155 | 0.2655 | 123.1155 | -0.01831 | -0.009155 | 0.24262 | -0.18768 | -0.23804 | 0.1236 | 0.68207 | -0.10529 | 0.13275 | 0.013733 | 123.1018 | 123.0789 | 53.3569 | -122.8455 | 122.9599 | 122.85 | 74.9817 | -123.0743
2629.0156 | 123.0927 | -52.066 | 70.7703 | 0.14481 | 0.0087307 | 0.06825 | 0.069449 | 0.12565 | -0.0017859 | -0.0075047 | 0.10666 | -0.0097668 | 0.060205 | 0.057826 | 0.0046356 | -0.011974 | 70.9167 | 71.0358 | 0.72327 | -52.0294 | 71.1594 | -51.8738 | -51.9562 | -51.384 | 21.6705 | -52.2446 | 70.9763 | 70.8389 | -52.24 | -52.3132 | 0.19226 | 0.10986 | 0.3891 | 123.1018 | 0.036621 | -0.073242 | 0.14648 | -0.17395 | -0.24719 | 0.20599 | 0.68207 | -0.17853 | 0.068664 | 0.068664 | 123.2254 | 122.9828 | 52.7893 | -122.7264 | 123.0423 | 122.905 | 73.7366 | -123.0835
2630.0156 | 123.143 | -52.4323 | 70.3674 | 0.16006 | 0.01578 | 0.068891 | 0.070944 | 0.1295 | 0.0031273 | -0.0036595 | 0.19058 | -0.010194 | 0.063837 | 0.057612 | 0.0097626 | -0.011974 | 70.1202 | 70.2896 | 0.59052 | -52.7939 | 70.3125 | -52.7069 | -52.7802 | -52.002 | 20.9015 | -52.4139 | 70.3949 | 70.3354 | -52.6932 | -52.7115 | -0.27466 | -0.3479 | -0.054932 | 122.7219 | -0.36163 | -0.013733 | -0.24719 | -0.26093 | -0.27924 | 0.027465 | 0.4303 | 0.018311 | 0.29755 | -0.032044 | 122.7448 | 122.5525 | 53.0228 | -123.1476 | 122.8271 | 122.7676 | 73.3337 | -123.0789
2631.0156 | 123.111 | -51.4572 | 71.3562 | 0.15244 | 0.01044 | 0.0706 | 0.070517 | 0.12843 | -0.0019995 | -0.0060093 | 0.22873 | -0.010621 | 0.061914 | 0.057398 | 0.0082672 | -0.012187 | 71.0083 | 71.1685 | 0.74616 | -51.9882 | 71.228 | -51.8326 | -51.8829 | -50.8896 | 21.7438 | -51.4709 | 71.4569 | 71.3928 | -51.6541 | -51.7044 | -0.37537 | -0.42572 | -0.12817 | 122.6257 | -0.53101 | -0.10528 | -0.3479 | -0.19684 | -0.24719 | 0.10071 | 0.56763 | -0.013733 | 0.23346 | 0.036621 | 122.6852 | 122.4655 | 52.2034 | -123.2391 | 122.9141 | 122.85 | 73.201 | -123.0606
2632.0156 | 123.1522 | -51.59 | 71.2326 | 0.18295 | 0.013431 | 0.070173 | 0.070303 | 0.12928 | 0.0022729 | -0.0062229 | 0.2211 | -0.010835 | 0.061273 | 0.056758 | 0.0097626 | -0.011546 | 71.0815 | 71.1456 | 0.737 | -51.8509 | 71.283 | -51.7593 | -51.8372 | -51.0086 | 22.0322 | -51.6907 | 71.3196 | 71.1914 | -51.8417 | -51.8784 | -0.16937 | -0.24719 | 0.050354 | 122.7356 | -0.26093 | -0.013733 | -0.15106 | -0.25177 | -0.28839 | 0.086975 | 0.58136 | -0.10071 | 0.18768 | -0.041199 | 122.8729 | 122.6715 | 52.327 | -123.0698 | 122.9095 | 122.7814 | 73.6221 | -123.111
2633.0156 | 123.1155 | -52.739 | 70.1294 | 0.15244 | 0.0095853 | 0.0706 | 0.07009 | 0.13057 | -0.0041357 | -0.0066501 | 0.083771 | -0.010408 | 0.062342 | 0.054621 | 0.00549 | -0.013042 | 69.8227 | 69.9234 | 0.38452 | -53.1876 | 70.0012 | -53.0319 | -53.1097 | -52.2079 | 20.8557 | -52.7618 | 70.1431 | 70.079 | -52.9724 | -53.0228 | -0.29297 | -0.37079 | -0.12817 | 122.6624 | -0.44861 | -0.07782 | -0.3067 | -0.23346 | -0.28381 | 0.013732 | 0.53101 | -0.022888 | 0.26093 | -0.050354 | 122.7402 | 122.5616 | 53.1235 | -123.2391 | 122.8821 | 122.818 | 73.5947 | -123.1522
2634.0156 | 123.1705 | -51.5991 | 71.2372 | 0.20584 | 0.013431 | 0.068464 | 0.070944 | 0.1295 | 0.0029137 | -0.0047275 | 0.20584 | -0.0093396 | 0.063623 | 0.057612 | 0.00784 | -0.013683 | 70.9991 | 71.0587 | 0.46234 | -52.0294 | 71.1136 | -51.9104 | -51.9699 | -51.0727 | 21.5744 | -51.7181 | 71.2509 | 71.1594 | -51.8646 | -51.86 | -0.31128 | -0.37079 | -0.1236 | 122.6578 | -0.4303 | -0.059509 | -0.23804 | -0.2655 | -0.26093 | 0.013733 | 0.52643 | -0.11902 | 0.14191 | -0.07782 | 122.7127 | 122.5983 | 52.0615 | -123.2071 | 122.85 | 122.7585 | 73.1735 | -123.0972
2635.0156 | 123.1018 | -52.5101 | 70.34 | 0.10666 | 0.010226 | 0.070173 | 0.070303 | 0.12758 | -0.00029045 | -0.0057957 | 0.16769 | -0.010835 | 0.059778 | 0.058253 | 0.007199 | -0.010051 | 70.3491 | 70.4865 | 0.42114 | -52.6703 | 70.5185 | -52.5101 | -52.6016 | -51.9424 | 20.8282 | -52.5833 | 70.4086 | 70.3262 | -52.7344 | -52.771 | 0 | -0.091553 | 0.17853 | 122.9965 | -0.16022 | -0.068664 | 0.009155 | -0.2243 | -0.26092 | 0.068664 | 0.56763 | -0.073242 | 0.18768 | -0.013733 | 123.0286 | 122.8592 | 52.9312 | -122.9416 | 122.9187 | 122.8363 | 73.3383 | -123.111
2636.0156 | 123.0606 | -52.6108 | 70.1385 | 0.25162 | 0.01578 | 0.071455 | 0.074362 | 0.12864 | 0.0018457 | -0.0051547 | 0.19058 | -0.0082716 | 0.062982 | 0.055689 | 0.009549 | -0.012187 | 70.4315 | 70.5139 | 0.39825 | -52.6382 | 70.5368 | -52.5238 | -52.6337 | -51.9196 | 20.9381 | -52.6794 | 70.3949 | 70.2896 | -52.7435 | -52.771 | 0.086975 | -0.022888 | 0.39825 | 123.1247 | -0.027466 | -0.004578 | 0.29297 | -0.13275 | -0.16022 | 0.25635 | 0.69122 | -0.068664 | 0.091553 | 0.15106 | 123.1476 | 123.0423 | 53.009 | -122.7722 | 123.0057 | 122.9004 | 73.5489 | -122.9095
2637.0156 | 123.1018 | -52.7664 | 70.0745 | 0.16006 | 0.010867 | 0.068891 | 0.070303 | 0.12587 | -0.0013587 | -0.0066501 | 0.16769 | -0.0095532 | 0.062342 | 0.056117 | 0.0076264 | -0.010905 | 70.3629 | 70.4315 | 0.37994 | -52.6611 | 70.5322 | -52.5055 | -52.6337 | -52.3224 | 20.6589 | -53.0869 | 70.1385 | 70.0607 | -52.9999 | -53.0136 | 0.26093 | 0.13275 | 0.45776 | 123.1979 | 0.10529 | -0.027466 | 0.28839 | -0.23346 | -0.24719 | 0.064087 | 0.44403 | -0.32043 | -0.073242 | -0.013733 | 123.2986 | 123.1293 | 53.1464 | -122.7081 | 122.905 | 122.8271 | 73.4253 | -123.0881
2638.0156 | 123.1476 | -51.7044 | 71.1136 | 0.18295 | 0.014926 | 0.069959 | 0.070517 | 0.13142 | 0.0020593 | -0.0049411 | 0.083771 | -0.0072034 | 0.065332 | 0.055903 | 0.0093354 | -0.013683 | 70.8252 | 70.9808 | 0.68665 | -51.9928 | 71.0861 | -51.9379 | -52.0157 | -51.1826 | 29.4205 | -51.7136 | 71.2189 | 71.1456 | -51.9104 | -51.9241 | -0.23346 | -0.31128 | -0.027465 | 122.6852 | -0.28839 | 0.022888 | -0.28839 | -0.20599 | -0.21973 | 0.10529 | 0.52185 | -0.009155 | 0.21057 | 0.032044 | 122.7905 | 122.5296 | 52.3911 | -123.1293 | 122.9233 | 122.85 | 81.1249 | -123.0377
2639.0156 | 123.1338 | -51.5579 | 71.2738 | 0.13718 | 0.0097989 | 0.069532 | 0.068167 | 0.13121 | 0.00077755 | -0.0043003 | -1.4345 | -0.012117 | 0.061914 | 0.056117 | 0.01019 | -0.012401 | 71.3333 | 71.4386 | 0.80109 | -51.709 | 71.4294 | -51.5717 | -51.6861 | -51.004 | 30.0797 | -51.709 | 71.3516 | 71.2601 | -51.7685 | -51.8188 | -0.013733 | -0.12817 | 0.15564 | 122.9965 | -0.15106 | -0.022888 | 0.059509 | -0.21057 | -0.26093 | 0.07782 | 0.55389 | -0.15106 | 0.10986 | -0.013733 | 122.9874 | 122.8912 | 52.359 | -122.9599 | 122.9095 | 122.818 | 81.6376 | -123.0927
2640.0156 | 123.1064 | -52.24 | 70.6146 | 0.16006 | 0.016208 | 0.06825 | 0.072012 | 0.12693 | 0.0027001 | -0.0057957 | 0.20584 | -0.0089124 | 0.065119 | 0.057826 | 0.0097626 | -0.011546 | 70.372 | 70.5002 | 0.76904 | -52.5696 | 70.6558 | -52.4506 | -52.5467 | -51.6724 | 29.2603 | -52.2995 | 70.7153 | 70.6192 | -52.4506 | -52.478 | -0.21057 | -0.3067 | 0.041199 | 122.7402 | -0.32959 | -0.022888 | -0.24262 | -0.21057 | -0.23804 | 0.10071 | 0.56763 | -0.05951 | 0.17853 | 0.004578 | 122.8958 | 122.612 | 53.009 | -123.1613 | 122.9553 | 122.8592 | 81.5002 | -123.0927
2641.0156 | 123.111 | -52.2263 | 70.6787 | 0.16769 | 0.01044 | 0.067396 | 0.07009 | 0.12715 | -0.0039221 | -0.0060093 | 0.25162 | -0.009126 | 0.061487 | 0.056544 | 0.0069854 | -0.0096238 | 70.5963 | 70.7474 | 0.83313 | -52.3544 | 70.8069 | -52.2308 | -52.3224 | -51.7731 | 29.3289 | -52.3041 | 70.6833 | 70.6329 | -52.446 | -52.4872 | -0.004578 | -0.096131 | 0.12817 | 122.9736 | -0.12817 | -0.032043 | -0.082398 | -0.21973 | -0.26093 | 0.004578 | 0.45319 | -0.07782 | 0.18311 | -0.045776 | 123.0331 | 122.8226 | 53.0594 | -123.0011 | 122.9095 | 122.8592 | 81.5552 | -123.1659
2642.0156 | 123.1293 | -52.8214 | 70.0104 | 0.19821 | 0.013644 | 0.068678 | 0.072653 | 0.13099 | 0.0031273 | -0.0060093 | 0.29739 | -0.0082716 | 0.062342 | 0.056544 | 0.0093354 | -0.012828 | 69.809 | 69.9371 | 0.70038 | -53.096 | 70.0424 | -52.9907 | -53.0823 | -52.2125 | 29.0634 | -52.9449 | 70.0928 | 70.015 | -53.0365 | -53.0777 | -0.16937 | -0.26093 | 0.032043 | 122.7585 | -0.27466 | -0.013733 | -0.20142 | -0.21515 | -0.25635 | 0.082397 | 0.60883 | -0.1236 | 0.13275 | 0.004578 | 122.8638 | 122.6303 | 53.5217 | -123.0927 | 122.9141 | 122.8363 | 81.8848 | -123.0881
2643.0156 | 123.1155 | -53.3157 | 69.5297 | 0.14481 | 0.0095853 | 0.066755 | 0.071799 | 0.12907 | -0.0019995 | -0.0060093 | 0.24399 | -0.011049 | 0.061914 | 0.058467 | 0.0069854 | -0.011333 | 69.4839 | 69.6304 | 0.46234 | -53.4393 | 69.6716 | -53.3661 | -53.4439 | -52.6245 | 28.7842 | -53.2928 | 69.6671 | 69.603 | -53.4805 | -53.5309 | -0.050354 | -0.12817 | 0.14191 | 122.9462 | -0.1236 | 0.004578 | -0.045776 | -0.1648 | -0.21515 | 0.13733 | 0.69122 | 0.022888 | 0.23804 | 0.073242 | 122.9874 | 122.7997 | 53.7781 | -122.9736 | 122.9828 | 122.9187 | 82.0999 | -123.0606
2644.0156 | 123.1384 | -52.7664 | 70.1157 | 0.16006 | 0.014712 | 0.06825 | 0.073508 | 0.12971 | 0.0033411 | -0.0049411 | 0.18295 | -0.0065626 | 0.064691 | 0.058039 | 0.0084808 | -0.013683 | 69.9783 | 70.0562 | 0.42114 | -52.9999 | 70.2026 | -52.8946 | -52.977 | -52.1988 | 29.1916 | -52.8854 | 70.1431 | 70.047 | -53.0228 | -53.0182 | -0.12817 | -0.21057 | 0.086975 | 122.8226 | -0.23346 | -0.022888 | -0.13733 | -0.25635 | -0.25177 | 0.027465 | 0.56763 | -0.11902 | 0.13275 | -0.068665 | 122.9691 | 122.7448 | 53.1876 | -123.0927 | 122.9095 | 122.8134 | 81.958 | -123.1338
2645.0156 | 123.1018 | -52.1667 | 70.6924 | 0.57205 | 0.014926 | 0.068891 | 0.072012 | 0.12736 | -0.0032813 | -0.0047275 | 0.21347 | -0.0082716 | 0.062555 | 0.056544 | 0.0086944 | -0.010265 | 70.784 | 70.8939 | 0.59509 | -52.2629 | 70.8801 | -52.1439 | -52.24 | -51.6312 | 29.4983 | -52.4689 | 70.6833 | 70.5917 | -52.446 | -52.4689 | 0.022888 | -0.073242 | 0.18768 | 123.0606 | -0.09613 | -0.022888 | 0.091553 | -0.27924 | -0.30212 | -0.009155 | 0.53558 | -0.30212 | 0 | -0.10071 | 123.0469 | 122.9507 | 52.7618 | -122.9324 | 122.85 | 122.7585 | 81.665 | -123.1613
2646.0156 | 122.9919 | -51.622 | 71.3287 | 0.14481 | 0.017276 | 0.068037 | 0.073081 | 0.13014 | 0.0054773 | -0.0038731 | 0.26688 | -0.0020764 | 0.060846 | 0.052485 | 0.0082672 | -0.012828 | 71.109 | 71.1273 | 0.49439 | -51.8921 | 71.4111 | -51.741 | -51.8738 | -51.2146 | 29.9194 | -51.7776 | 71.315 | 71.2601 | -51.8417 | -51.8921 | -0.11902 | -0.25177 | 0.082398 | 122.7493 | -0.27008 | -0.018311 | -0.21973 | -0.21973 | -0.27008 | -0.013733 | 0.40741 | -0.15564 | 0.11444 | -0.068664 | 123.0331 | 122.731 | 52.1164 | -123.2025 | 122.937 | 122.8821 | 81.5414 | -123.2208
2647.0156 | 123.1567 | -51.8372 | 71.022 | 0.19821 | 0.014071 | 0.066541 | 0.071158 | 0.12907 | -0.00071785 | -0.0053683 | 0.23636 | -0.0089124 | 0.061701 | 0.055903 | 0.0082672 | -0.0098374 | 70.7474 | 70.871 | 0.59509 | -52.24 | 70.8893 | -52.1164 | -52.2217 | -51.416 | 29.924 | -51.6541 | 71.0495 | 70.9717 | -52.0477 | -52.0752 | -0.27924 | -0.38452 | -0.13275 | 122.7081 | -0.40283 | -0.01831 | -0.27466 | -0.21057 | -0.23804 | 0.027466 | 0.42114 | 0.18311 | 0.42114 | -0.050354 | 122.7264 | 122.5845 | 52.4323 | -123.2437 | 122.8867 | 122.8088 | 81.7612 | -123.0972
2648.0156 | 123.0606 | -51.7227 | 71.1823 | 0.17532 | 0.016208 | 0.068464 | 0.070944 | 0.12651 | 0.00056395 | -0.0040867 | 0.16769 | -0.0059216 | 0.064478 | 0.054408 | 0.011258 | -0.011546 | 71.1823 | 71.2509 | 0.60425 | -51.741 | 71.4798 | -51.6266 | -51.7502 | -51.1368 | 29.9011 | -51.9745 | 71.2921 | 71.1868 | -51.9241 | -51.9608 | 0.09613 | -0.027466 | 0.29755 | 122.9736 | -0.018311 | 0.009155 | 0 | -0.20142 | -0.23804 | 0.10986 | 0.58594 | -0.25177 | -0.013733 | 0.004578 | 123.2025 | 122.905 | 52.327 | -122.9324 | 123.0148 | 122.9095 | 81.6238 | -123.143
2649.0156 | 123.1522 | -52.6703 | 70.1935 | 0.17532 | 0.014285 | 0.069105 | 0.071372 | 0.12843 | -0.0015723 | -0.0043003 | 0.72464 | -0.0097668 | 0.061914 | 0.05633 | 0.0069854 | -0.010692 | 70.1248 | 70.2621 | 0.49439 | -52.9816 | 70.2621 | -52.7618 | -52.8442 | -52.0432 | 30.1071 | -52.7527 | 70.2576 | 70.1889 | -52.8854 | -52.9083 | -0.091553 | -0.17395 | 0.068665 | 122.9324 | -0.31128 | -0.13733 | -0.068664 | -0.21515 | -0.23804 | 0.064087 | 0.62714 | -0.082398 | 0.15564 | -0.004577 | 122.9324 | 122.7951 | 53.1647 | -123.0377 | 122.9279 | 122.8592 | 82.7774 | -123.1018
2650.0156 | 123.0423 | -53.4256 | 69.5206 | 1.3503 | 0.017062 | 0.069319 | 0.07009 | 0.12971 | 0.0018457 | -0.0049411 | 0.16006 | -0.007417 | 0.063623 | 0.056758 | 0.01019 | -0.010905 | 69.6487 | 69.6579 | 0.3067 | -53.3249 | 69.9097 | -53.2196 | -53.302 | -52.9129 | 25.8224 | -53.833 | 69.5526 | 69.4702 | -53.6453 | -53.6499 | 0.20599 | 0.1236 | 0.3891 | 123.0835 | 0.10071 | -0.022888 | 0.12817 | -0.21973 | -0.2243 | 0.032043 | 0.5127 | -0.40741 | -0.18311 | -0.050354 | 123.3353 | 123.0743 | 53.7323 | -122.8226 | 122.9782 | 122.8958 | 79.248 | -123.1705
2651.0156 | 123.143 | -52.6154 | 70.2576 | 0.18295 | 0.017276 | 0.06825 | 0.070303 | 0.12736 | 0.00056395 | -0.0062229 | 0.16769 | -0.0086988 | 0.064905 | 0.054835 | 0.0074126 | -0.010051 | 70.1248 | 70.1523 | 0.48981 | -52.8442 | 70.2713 | -52.7527 | -52.8442 | -52.0294 | 26.6418 | -52.684 | 70.285 | 70.2026 | -52.8625 | -52.8625 | -0.13733 | -0.22888 | 0.013733 | 122.7676 | -0.22888 | 0 | -0.13275 | -0.24719 | -0.24719 | 0.027466 | 0.58594 | -0.068665 | 0.17853 | -0.054931 | 122.8867 | 122.7402 | 53.1052 | -123.1018 | 122.9004 | 122.818 | 79.2572 | -123.1201
2652.0156 | 123.0057 | -52.4185 | 70.5414 | 0.053253 | 0.016849 | 0.068678 | 0.072226 | 0.12993 | 0.00077755 | -0.0030185 | 0.037995 | -0.006349 | 0.0664 | 0.058894 | 0.0099762 | -0.012828 | 70.546 | 70.6329 | 0.45319 | -52.3727 | 70.8664 | -52.2537 | -52.3727 | -51.9058 | 24.3851 | -52.7893 | 70.6284 | 70.5185 | -52.6199 | -52.684 | 0.16479 | 0.045776 | 0.32501 | 123.0515 | 0.045776 | 0 | 0.004577 | -0.20142 | -0.2655 | 0.086975 | 0.5127 | -0.37079 | -0.10529 | -0.022888 | 123.2849 | 122.9645 | 52.8717 | -122.9141 | 123.0469 | 122.937 | 76.8036 | -123.2254
2653.0156 | 123.1201 | -52.8809 | 69.96 | 0.20584 | 0.014926 | 0.06761 | 0.069235 | 0.13185 | -0.0024269 | -0.0040867 | 0.20584 | -0.0086988 | 0.062342 | 0.057826 | 0.0065582 | -0.010051 | 69.9921 | 70.1294 | 0.40283 | -52.9221 | 70.2576 | -52.7893 | -52.8763 | -52.3132 | 23.0713 | -53.0319 | 70.1065 | 70.0424 | -53.0685 | -53.1097 | 0.091552 | 0.004577 | 0.29755 | 123.0103 | -0.041199 | -0.045776 | 0.032043 | -0.18768 | -0.22888 | 0.14648 | 0.56763 | -0.15106 | 0.07782 | 0.082397 | 123.1384 | 122.8729 | 53.2837 | -122.8363 | 122.9874 | 122.9233 | 75.9521 | -123.0698
2654.0156 | 123.0194 | -52.4506 | 70.4407 | 0.0914 | 0.016421 | 0.06761 | 0.072226 | 0.12758 | 0.00056395 | -0.0025913 | 0.6636 | -0.006349 | 0.064051 | 0.055262 | 0.0097626 | -0.011333 | 70.3857 | 70.4727 | 0.5127 | -52.5238 | 70.6512 | -52.4414 | -52.5467 | -51.9333 | 22.3114 | -52.6474 | 70.5734 | 70.4681 | -52.6657 | -52.6932 | 0.009156 | -0.09613 | 0.21057 | 122.9233 | -0.073242 | 0.022888 | -0.054932 | -0.21515 | -0.24261 | 0.13275 | 0.51727 | -0.19684 | 0.045776 | 0.027466 | 123.1018 | 122.8363 | 52.9633 | -122.9874 | 123.024 | 122.9187 | 74.762 | -123.1338
2655.0156 | 123.0881 | -52.89 | 69.9646 | 0.17532 | 0.012576 | 0.068678 | 0.071372 | 0.13078 | -0.00050425 | -0.0077183 | 0.25925 | -0.0084852 | 0.063196 | 0.055903 | 0.007199 | -0.011974 | 69.9051 | 70.015 | 0.42572 | -53.0411 | 70.1797 | -52.8809 | -52.9953 | -52.121 | 22.2565 | -52.9587 | 70.1889 | 70.0836 | -53.0136 | -53.0731 | 0.009156 | -0.10529 | 0.21515 | 122.905 | -0.15106 | -0.045777 | -0.05951 | -0.1236 | -0.18311 | 0.2243 | 0.76904 | -0.068664 | 0.11444 | 0.11902 | 123.0698 | 122.7951 | 53.3157 | -122.9599 | 123.0789 | 122.9736 | 75.1465 | -123.0377
2656.0156 | 122.9919 | -52.5513 | 70.4041 | 0.037994 | 0.017062 | 0.068678 | 0.074362 | 0.13206 | 0.0018457 | -0.0028049 | 0.060883 | -0.0078442 | 0.065546 | 0.056971 | 0.0093354 | -0.014323 | 69.9966 | 70.0928 | 0.41657 | -52.8946 | 70.3354 | -52.7756 | -52.8397 | -52.121 | 22.6868 | -52.7939 | 70.4269 | 70.3491 | -52.8076 | -52.8397 | -0.2243 | -0.28839 | -0.068665 | 122.644 | -0.34332 | -0.054931 | -0.40741 | -0.25635 | -0.28839 | 0.022888 | 0.4303 | -0.24261 | 0.045777 | -0.054932 | 122.8867 | 122.5479 | 52.9678 | -123.2437 | 122.9782 | 122.9004 | 75.238 | -123.2437
2657.0156 | 123.0652 | -53.2333 | 69.6808 | 0.15244 | 0.016849 | 0.068037 | 0.070731 | 0.12758 | -7.6852e-05 | -0.0047275 | 0.21347 | -0.009126 | 0.065119 | 0.058467 | 0.0065582 | -0.010692 | 69.4748 | 69.5251 | 0.37994 | -53.4897 | 69.7815 | -53.3066 | -53.4393 | -52.6382 | 25.8041 | -53.3752 | 69.7632 | 69.6808 | -53.4073 | -53.4714 | -0.073243 | -0.20599 | 0.10071 | 122.7585 | -0.25635 | -0.050354 | -0.20599 | -0.17395 | -0.23804 | 0.082398 | 0.59509 | -0.14191 | 0.096131 | 0 | 123.0148 | 122.7081 | 53.6133 | -123.1201 | 122.9965 | 122.9141 | 79.0375 | -123.1522
2658.0156 | 123.0057 | -53.4348 | 69.5114 | 0.022736 | 0.019198 | 0.066755 | 0.07244 | 0.1295 | 0.00099115 | -0.0043003 | 0.030365 | -0.0061352 | 0.065973 | 0.057612 | 0.0086944 | -0.011333 | 69.4839 | 69.5618 | 0.42572 | -53.4897 | 69.7678 | -53.3524 | -53.4622 | -52.8625 | 24.527 | -53.5675 | 69.6213 | 69.5389 | -53.5812 | -53.6591 | 0.082397 | -0.027466 | 0.25635 | 122.9965 | -0.054932 | -0.027466 | -0.027466 | -0.14648 | -0.22431 | 0.10986 | 0.5722 | -0.13275 | 0.091553 | 0.027465 | 123.2025 | 122.9187 | 53.8605 | -122.9736 | 123.056 | 122.9736 | 77.9617 | -123.1705
2659.0156 | 122.9965 | -53.6407 | 69.278 | 3.5323 | 0.016635 | 0.073805 | 0.075644 | 0.12693 | 0.00077755 | -0.0057957 | 0.053253 | -0.0086988 | 0.064051 | 0.056758 | 0.0065582 | -0.010692 | 69.072 | 69.0948 | 0.43945 | -53.8971 | 69.31 | -53.7552 | -53.8742 | -53.096 | 23.9044 | -53.8559 | 69.342 | 69.2917 | -53.833 | -53.9017 | -0.11444 | -0.23346 | 0.032044 | 122.7356 | -0.25635 | -0.022888 | -0.20599 | -0.19226 | -0.26093 | 0.064087 | 0.54474 | -0.21515 | 0.045776 | 0.013733 | 122.9507 | 122.7127 | 54.0802 | -123.1522 | 122.9828 | 122.9324 | 77.5452 | -123.1796
2660.0156 | 123.0423 | -51.7273 | 71.1731 | -0.023041 | 0.015567 | 0.066541 | 0.073081 | 0.12928 | 0.0020593 | -0.0038731 | 0.037995 | -0.0061352 | 0.0664 | 0.057612 | 0.0084808 | -0.013683 | 71.0312 | 71.1411 | 0.57678 | -51.8921 | 71.283 | -51.7593 | -51.8509 | -51.0406 | 23.7808 | -51.7868 | 71.3791 | 71.3013 | -51.86 | -51.9241 | -0.032043 | -0.1236 | 0.10986 | 122.8683 | -0.1648 | -0.041199 | -0.14191 | -0.13275 | -0.19684 | 0.20599 | 0.68665 | -0.059509 | 0.13733 | 0.12817 | 123.0103 | 122.7585 | 52.3041 | -123.024 | 123.1064 | 123.0286 | 75.5081 | -123.0972
2661.0156 | 123.0331 | -52.4185 | 70.5185 | 0.068512 | 0.01514 | 0.065473 | 0.068808 | 0.13057 | -0.00050425 | -0.0062229 | 0.19821 | -0.009126 | 0.06341 | 0.056117 | 0.0065582 | -0.010692 | 70.372 | 70.4727 | 0.48065 | -52.5558 | 70.6924 | -52.4002 | -52.5238 | -51.8967 | 23.1628 | -52.5696 | 70.61 | 70.5002 | -52.6611 | -52.6245 | 0.01831 | -0.10529 | 0.17395 | 122.8912 | -0.13733 | -0.032043 | -0.14648 | -0.24262 | -0.20599 | 0.091552 | 0.52185 | -0.15106 | 0.054932 | -0.018311 | 123.111 | 122.7905 | 52.8992 | -123.0423 | 123.0286 | 122.9187 | 75.5814 | -123.143
2662.0156 | 123.0286 | -53.064 | 69.9142 | 0.030365 | 0.016635 | 0.067396 | 0.073081 | 0.12928 | 0.0020593 | -0.0062229 | 0.022736 | -0.0082716 | 0.066187 | 0.055262 | 0.0067718 | -0.01411 | 69.6625 | 69.7678 | 0.45776 | -53.2516 | 69.9326 | -53.1372 | -53.2196 | -52.4963 | 22.6044 | -53.2837 | 69.96 | 69.8868 | -53.2608 | -53.3478 | -0.073242 | -0.15564 | 0.01831 | 122.8317 | -0.18768 | -0.032044 | -0.25177 | -0.19684 | -0.28381 | 0.045776 | 0.56763 | -0.21973 | 0.064087 | -0.027466 | 122.9965 | 122.7264 | 53.5217 | -123.1338 | 123.024 | 122.9507 | 75.6683 | -123.262
2663.0156 | 123.0377 | -51.8921 | 71.022 | 0.14481 | 0.016635 | 0.066541 | 0.072226 | 0.12928 | 0.00056395 | -0.0066501 | 0.54916 | -0.007417 | 0.065119 | 0.059748 | 0.0099762 | -0.010905 | 70.5917 | 70.9763 | 0.66376 | -51.9012 | 71.2326 | -51.8738 | -51.9836 | -51.2009 | 23.4375 | -52.0798 | 71.1823 | 71.0953 | -52.066 | -52.1118 | 0.018311 | -0.091553 | 0.21057 | 122.8683 | -0.009155 | 0.082398 | -0.4303 | -0.17395 | -0.21973 | 0.16022 | 0.69122 | -0.18768 | 0.032043 | 0.073242 | 123.1247 | 122.4838 | 52.5558 | -123.0057 | 123.0743 | 122.9874 | 75.3296 | -123.1338
2664.0156 | 123.0331 | -52.597 | 70.2896 | -0.12222 | 0.016849 | 0.066541 | 0.073508 | 0.12907 | 0.0018457 | -0.0066501 | -0.00015237 | -0.0072034 | 0.062982 | 0.055903 | 0.0097626 | -0.011974 | 70.6284 | 70.7336 | 0.42114 | -52.2995 | 70.8664 | -52.2079 | -52.3315 | -51.8234 | 22.8424 | -52.9129 | 70.5826 | 70.4773 | -52.684 | -52.7802 | 0.3891 | 0.2655 | 0.57678 | 123.3307 | 0.29755 | 0.032043 | 0.33874 | -0.086975 | -0.1831 | 0.29297 | 0.77362 | -0.31586 | -0.13275 | 0.18768 | 123.4634 | 123.2254 | 53.0182 | -122.6212 | 123.1796 | 123.0743 | 75.4395 | -123.0698
2665.0156 | 123.1476 | -51.1826 | 71.7499 | 0.14481 | 0.017489 | 0.068037 | 0.07244 | 0.12886 | 0.0024865 | -0.0055821 | 0.14481 | -0.006349 | 0.064691 | 0.056758 | 0.0091216 | -0.01176 | 71.608 | 71.7133 | 0.55847 | -51.3702 | 71.9376 | -51.2054 | -51.2833 | -50.5554 | 23.3597 | -51.3016 | 71.8964 | 71.814 | -51.3748 | -51.4206 | -0.022888 | -0.10071 | 0.18768 | 122.8958 | -0.18768 | -0.086975 | -0.14191 | -0.19226 | -0.23804 | 0.14648 | 0.62714 | -0.11902 | 0.11902 | 0.064087 | 123.1201 | 122.7905 | 51.741 | -123.0331 | 123.0789 | 122.9965 | 74.5422 | -123.1705
2666.0156 | 123.0789 | -52.3178 | 70.6055 | -0.19089 | 0.014712 | 0.068891 | 0.070944 | 0.12864 | 0.00035035 | -0.0049411 | -0.168 | -0.0086988 | 0.064264 | 0.055689 | 0.006131 | -0.01176 | 70.5505 | 70.6833 | 0.45776 | -52.4231 | 70.8252 | -52.3132 | -52.4185 | -51.7136 | 22.5082 | -52.4734 | 70.7336 | 70.6604 | -52.5146 | -52.5421 | 0.004578 | -0.10071 | 0.21973 | 123.0011 | -0.10529 | -0.004578 | -0.054932 | -0.19684 | -0.2243 | 0.12817 | 0.60425 | -0.15564 | 0.068664 | 0.054931 | 123.143 | 122.8683 | 52.7756 | -123.024 | 123.0515 | 122.9782 | 74.8261 | -123.1476
2667.0156 | 123.0148 | -52.0111 | 70.9579 | 0.068512 | 0.016421 | 0.069959 | 0.073721 | 0.13121 | 0.00013675 | -0.0075047 | 0.2211 | -0.0086988 | 0.065119 | 0.057398 | 0.0082672 | -0.011974 | 70.5963 | 70.7108 | 0.38452 | -52.3178 | 70.9442 | -52.1393 | -52.2263 | -51.5488 | 22.6776 | -52.3956 | 70.9488 | 70.871 | -52.2995 | -52.3499 | -0.12817 | -0.21515 | -0.013733 | 122.7219 | -0.3067 | -0.091553 | -0.36163 | -0.28839 | -0.33875 | -0.009155 | 0.46234 | -0.38452 | -0.045776 | -0.086975 | 122.9553 | 122.6074 | 52.3956 | -123.1842 | 122.9599 | 122.8821 | 74.6887 | -123.3078
2668.0156 | 123.0103 | -52.6749 | 70.2667 | -0.15274 | 0.01813 | 0.06825 | 0.072867 | 0.13185 | -7.6852e-05 | -0.0051547 | 0.022736 | -0.0097668 | 0.064051 | 0.055903 | 0.0082672 | -0.010265 | 70.1477 | 70.2576 | 0.40283 | -52.7939 | 70.4407 | -52.6566 | -52.7664 | -52.0844 | 22.2839 | -53.0319 | 70.3354 | 70.2667 | -52.8717 | -52.9266 | 0.018311 | -0.091552 | 0.17395 | 122.9324 | -0.11902 | -0.027466 | -0.11902 | -0.19684 | -0.25177 | 0.068664 | 0.59052 | -0.35705 | -0.10528 | 0 | 123.1155 | 122.8226 | 53.0777 | -123.0331 | 123.0103 | 122.9416 | 74.9588 | -123.1934
2669.0156 | 123.1247 | -51.7914 | 71.1548 | 0.21347 | 0.015994 | 0.068464 | 0.072012 | 0.12822 | 0.0022729 | -0.0066501 | 0.19821 | -0.0078442 | 0.06341 | 0.05633 | 0.0093354 | -0.010051 | 71.0037 | 71.0953 | 0.40741 | -51.9836 | 71.3058 | -51.8097 | -51.9333 | -51.2833 | 22.76 | -51.9699 | 71.2006 | 71.1365 | -51.9791 | -52.0569 | -0.01831 | -0.14191 | 0.15106 | 122.8867 | -0.19226 | -0.050354 | -0.15106 | -0.18768 | -0.2655 | 0.045777 | 0.50812 | -0.17853 | 0.086975 | -0.01831 | 123.0972 | 122.7951 | 52.1988 | -123.0881 | 122.9919 | 122.9279 | 74.5514 | -123.2117
2670.0156 | 123.0469 | -51.1368 | 71.7865 | -0.099335 | 0.017062 | 0.06825 | 0.072867 | 0.12864 | 0.0014185 | -0.0015231 | -0.015411 | -0.007417 | 0.064478 | 0.05633 | 0.0084808 | -0.01176 | 71.2784 | 71.6217 | 0.75073 | -51.5991 | 71.6858 | -51.4481 | -51.5442 | -50.6058 | 23.4879 | -51.2787 | 71.8094 | 71.7819 | -51.3565 | -51.384 | -0.31128 | -0.40741 | -0.10071 | 122.7585 | -0.46234 | -0.054932 | -0.50812 | -0.21973 | -0.24719 | 0.022888 | 0.53101 | -0.14191 | 0.10529 | -0.004578 | 122.8226 | 122.4152 | 51.8875 | -123.3307 | 122.9462 | 122.9187 | 74.6246 | -123.1705
2671.0156 | 123.143 | -51.7868 | 71.0999 | 0.060882 | 0.011508 | 0.068891 | 0.066672 | 0.12758 | -0.0060585 | -0.0075047 | 0.20584 | -0.0099806 | 0.061487 | 0.055903 | 0.0050628 | -0.0094102 | 70.8847 | 71.0999 | 0.70496 | -51.9974 | 71.1685 | -51.8646 | -52.0065 | -51.2558 | 23.822 | -51.8463 | 71.1685 | 71.1227 | -51.9882 | -51.9791 | -0.07782 | -0.21973 | 0.068664 | 122.8867 | -0.21057 | 0.009156 | -0.21515 | -0.20142 | -0.19226 | 0.068664 | 0.53101 | -0.059509 | 0.13275 | 0.022888 | 122.9553 | 122.6715 | 52.4918 | -123.1064 | 122.9553 | 122.9095 | 75.6088 | -123.0789
2672.0156 | 123.0515 | -52.1027 | 70.7428 | -0.091705 | 0.016635 | 0.071027 | 0.073935 | 0.12843 | 0.0037683 | -0.0070773 | -0.045929 | -0.0093396 | 0.063837 | 0.055476 | 0.007199 | -0.013683 | 70.8847 | 70.9991 | 0.68665 | -52.0386 | 71.1365 | -51.9424 | -52.0157 | -51.4206 | 23.7717 | -52.4414 | 70.9808 | 70.8572 | -52.3041 | -52.3361 | 0.16022 | 0.086975 | 0.39368 | 123.1018 | 0.064087 | -0.022888 | 0.14191 | -0.20142 | -0.23346 | 0.23804 | 0.68207 | -0.33875 | -0.10529 | 0.11444 | 123.2391 | 122.9874 | 52.7893 | -122.7585 | 123.0835 | 122.9599 | 75.8743 | -123.0789
2673.0156 | 123.0789 | -51.5442 | 71.3974 | 0.18295 | 0.017489 | 0.066541 | 0.073081 | 0.12672 | 0.0027001 | -0.0053683 | 0.17532 | -0.006349 | 0.065332 | 0.056758 | 0.0091216 | -0.012187 | 71.2555 | 71.3654 | 0.64087 | -51.6129 | 71.64 | -51.4755 | -51.5442 | -50.8713 | 24.1882 | -51.6769 | 71.6217 | 71.5073 | -51.6769 | -51.7273 | 0.068664 | 0 | 0.24262 | 122.9095 | -0.068665 | -0.068665 | -0.14191 | -0.13275 | -0.18311 | 0.2243 | 0.67291 | -0.13275 | 0.050354 | 0.10986 | 123.1842 | 122.7997 | 52.1851 | -122.9416 | 123.1659 | 123.0515 | 75.7324 | -123.1247
2674.0156 | 123.0789 | -51.4893 | 71.4386 | -0.20615 | 0.015567 | 0.067823 | 0.070944 | 0.13057 | 0.0012047 | -0.0030185 | -0.25955 | -0.0095532 | 0.065119 | 0.056758 | 0.0069854 | -0.011119 | 71.3699 | 71.4432 | 0.71869 | -51.6312 | 71.6171 | -51.4893 | -51.6037 | -50.9583 | 23.7534 | -51.741 | 71.5347 | 71.4294 | -51.6724 | -51.741 | 0 | -0.11444 | 0.17853 | 122.9324 | -0.14191 | -0.027466 | -0.068665 | -0.1831 | -0.25177 | 0.09613 | 0.53101 | -0.25177 | 0 | -0.009156 | 123.1064 | 122.8592 | 52.2079 | -123.0423 | 123.024 | 122.9187 | 75.2426 | -123.1796
2675.0156 | 123.0103 | -51.3245 | 71.608 | 0.030365 | 0.017062 | 0.067182 | 0.072012 | 0.13142 | -7.6852e-05 | -0.0060093 | 0.037995 | -0.0084852 | 0.064264 | 0.057826 | 0.0074126 | -0.012828 | 71.4981 | 71.5622 | 0.70038 | -51.4709 | 71.8277 | -51.329 | -51.4343 | -50.7751 | 23.9273 | -51.6174 | 71.7041 | 71.6171 | -51.5213 | -51.5625 | -0.004578 | -0.10986 | 0.21973 | 122.8867 | -0.14648 | -0.036621 | -0.10986 | -0.19684 | -0.23804 | 0.096131 | 0.54932 | -0.29297 | -0.054932 | 0.009155 | 123.1522 | 122.8226 | 52.0248 | -123.0423 | 123.0286 | 122.9416 | 75.2518 | -123.1705
2676.0156 | 123.1247 | -51.2146 | 71.6354 | 0.16769 | 0.012149 | 0.0706 | 0.070303 | 0.12928 | -0.0052039 | -0.0075047 | 0.25925 | -0.0099806 | 0.060846 | 0.056117 | 0.0059174 | -0.0091966 | 71.5713 | 71.7499 | 0.78278 | -51.3474 | 71.8048 | -51.2283 | -51.3245 | -50.6104 | 24.8016 | -51.2924 | 71.7224 | 71.6583 | -51.3977 | -51.4709 | -0.013733 | -0.10986 | 0.16937 | 122.9645 | -0.13275 | -0.022888 | -0.064087 | -0.18311 | -0.25635 | 0.086975 | 0.60425 | -0.077819 | 0.17853 | 0.022888 | 123.0194 | 122.7859 | 51.9974 | -122.9599 | 122.937 | 122.8729 | 76.0162 | -123.1064
2677.0156 | 123.0057 | -50.9079 | 72.0291 | 0.0074768 | 0.018985 | 0.06761 | 0.073508 | 0.12608 | 0.0031273 | -0.0032321 | 0.053253 | -0.0076306 | 0.064905 | 0.055689 | 0.0086944 | -0.011546 | 71.6721 | 71.7957 | 0.76446 | -51.1963 | 71.9833 | -51.0956 | -51.2054 | -50.3494 | 24.8062 | -51.0086 | 72.1161 | 72.0337 | -51.1002 | -51.123 | -0.18768 | -0.29755 | -0.045777 | 122.7036 | -0.28839 | 0.009155 | -0.35706 | -0.19226 | -0.21515 | 0.086975 | 0.55847 | -0.10071 | 0.11444 | 0.004577 | 122.8912 | 122.58 | 51.6724 | -123.2346 | 123.024 | 122.9416 | 75.7141 | -123.1522
2678.0156 | 123.056 | -50.9857 | 71.965 | -0.20615 | 0.016421 | 0.069746 | 0.07543 | 0.12971 | -0.0011451 | -0.0053683 | -0.099335 | -0.0093396 | 0.064905 | 0.057398 | 0.0091216 | -0.013469 | 71.553 | 71.6675 | 0.76446 | -51.3657 | 71.8506 | -51.2512 | -51.3245 | -50.3906 | 24.8062 | -50.9995 | 72.0337 | 71.9376 | -51.1871 | -51.2192 | -0.2655 | -0.33875 | -0.11444 | 122.6532 | -0.37994 | -0.041199 | -0.41199 | -0.20142 | -0.23346 | 0.068664 | 0.59509 | -0.013733 | 0.21973 | -0.027466 | 122.8363 | 122.5388 | 51.7502 | -123.2895 | 123.0194 | 122.9233 | 75.7919 | -123.1842
2679.0156 | 123.0423 | -50.7065 | 72.2214 | 0.45761 | 0.016635 | 0.070387 | 0.074576 | 0.12886 | 0.0022729 | -0.0062229 | -0.045929 | -0.0078442 | 0.064691 | 0.05633 | 0.0099762 | -0.013469 | 71.9467 | 72.0886 | 0.82855 | -50.9354 | 72.2122 | -50.8438 | -50.9354 | -50.1663 | 25.0351 | -50.8209 | 72.2488 | 72.1939 | -50.9445 | -50.9811 | -0.13733 | -0.22888 | -0.009156 | 122.7951 | -0.22888 | 0 | -0.27466 | -0.23804 | -0.27466 | 0.027465 | 0.54016 | -0.11444 | 0.16022 | -0.027466 | 122.9187 | 122.6532 | 51.535 | -123.1567 | 122.9553 | 122.9004 | 75.7416 | -123.2025
2680.0156 | 123.0011 | -50.3677 | 72.5784 | -0.23666 | 0.010653 | 0.068891 | 0.073721 | 0.12928 | -0.0019995 | -0.0062229 | -0.099335 | -0.009126 | 0.06106 | 0.054408 | 0.0086944 | -0.0072738 | 72.3816 | 72.5372 | 0.75531 | -50.6104 | 72.6746 | -50.4272 | -50.5234 | -49.9558 | 25.4196 | -50.5417 | 72.6059 | 72.5327 | -50.6149 | -50.647 | -0.059509 | -0.15564 | 0.096131 | 122.905 | -0.24262 | -0.086976 | -0.19684 | -0.24719 | -0.27924 | 0.027466 | 0.41199 | -0.17395 | 0.10529 | -0.045776 | 123.0423 | 122.7493 | 51.123 | -123.1018 | 122.9736 | 122.9004 | 75.7874 | -123.2254
2681.0156 | 123.1705 | -51.1505 | 71.6904 | 0.19058 | 0.013644 | 0.070814 | 0.069449 | 0.13014 | -0.0039221 | -0.0060093 | 0.19058 | -0.0082716 | 0.060419 | 0.057185 | 0.0093354 | -0.011333 | 71.8002 | 71.6354 | 0.66834 | -51.091 | 71.9193 | -51.1185 | -51.1963 | -50.5005 | 25.0443 | -51.1505 | 71.7819 | 71.7316 | -51.3702 | -51.4206 | 0.032044 | -0.045776 | 0.22888 | 122.7859 | 0.05951 | 0.10529 | 0.10986 | -0.21973 | -0.27008 | 0.091552 | 0.65002 | 0 | 0.27008 | 0.041198 | 123.0698 | 122.9507 | 51.8188 | -122.8867 | 122.9324 | 122.8821 | 76.1948 | -123.111
2682.0156 | 123.0515 | -51.5671 | 71.3837 | -0.18326 | 0.012362 | 0.069959 | 0.075217 | 0.1295 | -0.00029045 | -0.0064365 | -0.14511 | -0.0076306 | 0.062769 | 0.056544 | 0.0082672 | -0.010905 | 71.1456 | 71.2967 | 0.4715 | -51.7593 | 71.4706 | -51.6678 | -51.8234 | -51.0223 | 24.7559 | -51.7227 | 71.3974 | 71.3699 | -51.7776 | -51.8143 | -0.10071 | -0.25635 | 0.086975 | 122.8638 | -0.19226 | 0.064087 | -0.23804 | -0.21057 | -0.24719 | 0.013733 | 0.54474 | -0.15564 | 0.091553 | -0.013733 | 123.0377 | 122.7127 | 52.0386 | -123.2071 | 122.9645 | 122.937 | 76.3229 | -123.1979
2683.0156 | 123.0698 | -51.3428 | 71.5988 | -0.12222 | 0.017917 | 0.06761 | 0.071158 | 0.12971 | 0.0014185 | -0.0064365 | -0.099335 | -0.0072034 | 0.066828 | 0.056758 | 0.00549 | -0.010692 | 71.2234 | 71.3654 | 0.65002 | -51.7136 | 71.5393 | -51.5579 | -51.6769 | -50.6882 | 24.5728 | -51.4526 | 71.6217 | 71.5393 | -51.6037 | -51.6266 | -0.21515 | -0.33417 | -0.059509 | 122.7081 | -0.37079 | -0.036621 | -0.37537 | -0.26093 | -0.28381 | 0.022888 | 0.6546 | -0.10986 | 0.17395 | -0.059509 | 122.8821 | 122.5662 | 51.9928 | -123.2758 | 122.9645 | 122.8821 | 75.9155 | -123.2254
2684.0156 | 123.0515 | -51.3794 | 71.5439 | -0.19852 | 0.011935 | 0.070173 | 0.070944 | 0.12886 | -0.0045631 | -0.0030185 | 0.053253 | -0.0089124 | 0.065332 | 0.055903 | 0.0063446 | -0.010692 | 71.0724 | 71.3333 | 0.81482 | -51.7319 | 71.5256 | -51.6083 | -51.6861 | -50.8621 | 24.7971 | -51.4572 | 71.5988 | 71.5164 | -51.6312 | -51.6495 | -0.22888 | -0.3067 | -0.01831 | 122.7127 | -0.35248 | -0.045777 | -0.4715 | -0.25177 | -0.27008 | 0.054932 | 0.51727 | -0.077819 | 0.19226 | -0.027466 | 122.905 | 122.4518 | 52.1942 | -123.23 | 122.9782 | 122.8958 | 76.1765 | -123.1934
2685.0156 | 123.0652 | -50.9491 | 72.0291 | -0.17563 | 0.01514 | 0.072523 | 0.072867 | 0.12864 | 0.0018457 | -0.0049411 | -0.12222 | -0.0084852 | 0.065119 | 0.055689 | 0.0086944 | -0.013042 | 71.6995 | 71.8506 | 0.6958 | -51.2192 | 71.9971 | -51.091 | -51.1688 | -50.4822 | 25.0305 | -51.0818 | 71.9971 | 71.9376 | -51.1826 | -51.21 | -0.14191 | -0.21973 | -0.032044 | 122.7997 | -0.27008 | -0.050354 | -0.32959 | -0.23346 | -0.26093 | -0.032044 | 0.46692 | -0.13275 | 0.12817 | -0.091553 | 122.9462 | 122.6486 | 51.6449 | -123.1979 | 122.9462 | 122.8867 | 75.9796 | -123.2391
2686.0156 | 123.1384 | -50.8804 | 71.9559 | 0.18295 | 0.012576 | 0.068464 | 0.07244 | 0.12587 | 0.00077755 | -0.0051547 | 0.10666 | -0.010408 | 0.065546 | 0.056758 | 0.00784 | -0.011333 | 71.7911 | 72.0062 | 0.78278 | -51.0773 | 72.0703 | -50.9354 | -51.0498 | -50.235 | 24.5682 | -50.9033 | 72.0474 | 71.9604 | -51.091 | -51.1276 | -0.054932 | -0.16937 | 0.11444 | 122.8867 | -0.19684 | -0.027466 | -0.16479 | -0.21057 | -0.24719 | 0.091552 | 0.64545 | -0.022888 | 0.22431 | 0.004577 | 122.9507 | 122.6715 | 51.6632 | -123.0057 | 122.9279 | 122.8409 | 75.4486 | -123.0835
2687.0156 | 123.0194 | -51.5533 | 71.4203 | -0.22903 | 0.013431 | 0.070173 | 0.073721 | 0.12843 | 0.0012047 | -0.0051547 | -0.69443 | -0.0089124 | 0.065119 | 0.057185 | 0.0076264 | -0.011546 | 71.1456 | 71.2875 | 0.59509 | -51.6312 | 71.5302 | -51.59 | -51.6724 | -50.9995 | 24.3164 | -51.7548 | 71.4981 | 71.402 | -51.7502 | -51.7822 | -0.036621 | -0.11902 | 0.10986 | 122.8409 | -0.07782 | 0.041198 | -0.27466 | -0.19684 | -0.22888 | 0.07782 | 0.55389 | -0.20142 | 0.027466 | -0.01831 | 123.0835 | 122.699 | 52.1484 | -123.0927 | 123.0515 | 122.9553 | 75.8698 | -123.2025
2688.0156 | 122.9965 | -53.2196 | 69.722 | -0.22141 | 0.0097989 | 0.069319 | 0.072012 | 0.13099 | -0.0060585 | -0.0047275 | -0.11459 | -0.010194 | 0.062769 | 0.057185 | 0.0048492 | -0.01176 | 69.4977 | 69.722 | 0.60425 | -53.3798 | 69.7769 | -53.2745 | -53.3386 | -52.6199 | 23.3963 | -53.3844 | 69.7815 | 69.7266 | -53.4073 | -53.4622 | -0.054932 | -0.11902 | 0.054932 | 122.9416 | -0.16022 | -0.041199 | -0.2243 | -0.18768 | -0.24262 | 0.059509 | 0.59967 | -0.1648 | 0.07782 | 0.004577 | 122.9965 | 122.7173 | 53.8239 | -123.0606 | 123.0011 | 122.9462 | 76.6159 | -123.1842
2689.0156 | 123.0652 | -52.5238 | 70.3812 | -0.19089 | 0.014926 | 0.072309 | 0.071158 | 0.13057 | 0.0018457 | -0.0062229 | -0.19852 | -0.0084852 | 0.062769 | 0.053767 | 0.0080536 | -0.012401 | 70.0241 | 70.2164 | 7.2556 | -52.7573 | 70.4315 | -52.684 | -52.7573 | -51.9012 | 23.877 | -52.6016 | 70.4865 | 70.4041 | -52.7298 | -52.7618 | -0.16022 | -0.23346 | 0.050354 | 122.7402 | -0.23346 | 0 | -0.35706 | -0.20599 | -0.23804 | 0.10529 | 0.62256 | -0.07782 | 0.16022 | 0.022888 | 122.9553 | 122.5479 | 59.7794 | -123.1384 | 123.0103 | 122.9279 | 76.4008 | -123.143
2690.0156 | 122.9965 | -53.4348 | 69.5435 | -0.24429 | 0.011722 | 0.06825 | 0.07009 | 0.12758 | -0.0030677 | -0.0064365 | -0.11459 | -0.010621 | 0.063837 | 0.057185 | 0.0065582 | -0.012401 | 69.4061 | 69.6121 | 11.5677 | -53.4622 | 69.7403 | -53.4073 | -53.508 | -52.8534 | 23.2315 | -53.627 | 69.5343 | 69.4565 | -53.6819 | -53.7003 | 0.027465 | -0.073243 | 0.19684 | 123.0469 | -0.027466 | 0.045777 | -0.13733 | -0.24719 | -0.2655 | -0.009155 | 0.58136 | -0.19226 | 0.073242 | -0.086975 | 123.175 | 122.8409 | 65.0024 | -123.0515 | 122.9691 | 122.8912 | 76.6663 | -123.2437
2691.0156 | 123.0331 | -52.5787 | 70.3629 | 0.13718 | 0.01578 | 0.070173 | 0.073294 | 0.128 | 0.0022729 | -0.0060093 | -0.60287 | -0.0082716 | 0.064691 | 0.055903 | 0.008908 | -0.011974 | 70.166 | 69.7906 | 10.1303 | -52.684 | 70.3583 | -52.7206 | -52.7985 | -51.9791 | 24.5453 | -52.6428 | 70.4727 | 70.3674 | -52.7573 | -52.8351 | -0.14191 | -0.21973 | -0.004578 | 122.3694 | -0.10529 | 0.11444 | -0.19684 | -0.17853 | -0.25635 | 0.10986 | 0.59967 | -0.064087 | 0.19226 | 0.004578 | 122.937 | 122.7448 | 62.709 | -123.1613 | 123.0515 | 122.9462 | 77.124 | -123.1979
2692.0156 | 123.1018 | -53.1967 | 69.6716 | -0.20615 | 0.0087307 | 0.070173 | 0.069663 | 0.13057 | -0.0047767 | -0.0079319 | -0.11459 | -0.010194 | 0.061701 | 0.057612 | 0.0042084 | -0.010265 | 69.6625 | 69.8364 | 12.1353 | -53.3295 | 69.8318 | -53.2288 | -53.334 | -52.5696 | 24.2523 | -53.3157 | 69.7678 | 69.7083 | -53.3615 | -53.4485 | -0.032044 | -0.13733 | 0.16022 | 123.0331 | -0.13275 | 0.004577 | -0.009155 | -0.16479 | -0.25177 | 0.09613 | 0.62714 | -0.11902 | 0.13275 | 0.036621 | 123.0286 | 122.8592 | 65.332 | -123.0057 | 122.9645 | 122.905 | 77.449 | -123.1201
2693.0156 | 123.0148 | -53.2608 | 69.6533 | -0.25192 | 0.013644 | 0.069959 | 0.074362 | 0.12993 | -0.00071785 | -0.0057957 | -0.15274 | -0.0076306 | 0.064264 | 0.056758 | 0.0076264 | -0.012828 | 69.2322 | 69.3924 | 8.4503 | -53.801 | 69.5526 | -53.5721 | -53.6682 | -52.6474 | 24.0829 | -53.3524 | 69.7128 | 69.635 | -53.4851 | -53.5217 | -0.31128 | -0.40741 | -0.10071 | 122.6532 | -0.54016 | -0.13275 | -0.42114 | -0.2243 | -0.26093 | 0.05951 | 0.6134 | -0.091553 | 0.16937 | -0.01831 | 122.8134 | 122.493 | 61.7111 | -123.3215 | 122.9736 | 122.8958 | 77.3438 | -123.175
2694.0156 | 123.1705 | -52.9953 | 69.8868 | -0.023041 | 0.0080899 | 0.071668 | 0.071372 | 0.13121 | -0.0054175 | -0.0083591 | -0.045929 | -0.010835 | 0.060633 | 0.056971 | 0.004422 | -0.010478 | 69.6899 | 69.8868 | 0.87891 | -53.2608 | 69.8822 | -53.1647 | -53.2562 | -52.3544 | 24.646 | -52.977 | 69.9005 | 69.8318 | -53.2196 | -53.2883 | -0.16937 | -0.26093 | -0.004578 | 122.8821 | -0.2655 | -0.004577 | -0.19684 | -0.2243 | -0.29297 | 0.013733 | 0.64087 | 0.01831 | 0.31128 | -0.054932 | 122.8775 | 122.6852 | 53.8742 | -123.143 | 122.8958 | 122.8271 | 77.6413 | -123.175
2695.0156 | 123.0377 | -53.0548 | 69.8959 | -0.95383 | 0.015994 | 0.068037 | 0.073935 | 0.12843 | 0.00077755 | -0.0062229 | -0.21378 | -0.010621 | 0.064264 | 0.057826 | 0.0076264 | -0.012828 | 69.5709 | 69.8044 | 0.62714 | -53.2883 | 69.9554 | -53.1876 | -53.2471 | -52.4872 | 24.5865 | -53.1692 | 69.9371 | 69.8547 | -53.2608 | -53.2837 | -0.13275 | -0.19226 | 0.059509 | 122.8592 | -0.23346 | -0.041199 | -0.32501 | -0.20599 | -0.22888 | 0.041199 | 0.56763 | -0.11444 | 0.11444 | -0.041199 | 123.0103 | 122.6257 | 53.6819 | -123.143 | 122.9919 | 122.9095 | 77.6413 | -123.1796
2696.0156 | 123.0423 | -53.0777 | 69.8502 | -0.24429 | 0.0095853 | 0.068891 | 0.071158 | 0.128 | -0.0022131 | -0.0072911 | -0.15274 | -0.0086988 | 0.061914 | 0.056544 | 0.0059174 | -0.011119 | 69.6213 | 69.7906 | 0.66834 | -53.2974 | 69.9188 | -53.1876 | -53.2883 | -52.4551 | 24.3073 | -53.2196 | 69.9463 | 69.873 | -53.3066 | -53.3295 | -0.10986 | -0.21057 | 0.068664 | 122.8683 | -0.21973 | -0.009155 | -0.22888 | -0.22888 | -0.25177 | 0.09613 | 0.62256 | -0.14191 | 0.10986 | 0.022888 | 122.9965 | 122.699 | 53.746 | -123.1384 | 123.024 | 122.9507 | 77.3849 | -123.1796
2697.0156 | 123.056 | -52.8488 | 70.1111 | -0.25192 | 0.013858 | 0.069959 | 0.07244 | 0.12886 | 0.0016321 | -0.0053683 | -0.15274 | -0.0093396 | 0.061914 | 0.057826 | 0.006131 | -0.01411 | 69.8685 | 70.0241 | 0.59967 | -53.0319 | 70.1935 | -52.9358 | -53.0182 | -52.2629 | 24.5041 | -53.0457 | 70.134 | 70.1019 | -53.0411 | -53.1097 | -0.086975 | -0.16937 | 0.082397 | 122.8729 | -0.1831 | -0.013733 | -0.24262 | -0.19226 | -0.26093 | 0.022888 | 0.58594 | -0.19684 | 0.064087 | -0.009155 | 123.0423 | 122.7173 | 53.4485 | -123.1293 | 122.9828 | 122.9507 | 77.3529 | -123.2208
2698.0156 | 123.1018 | -53.2471 | 69.6625 | -0.22141 | 0.01044 | 0.069959 | 0.069449 | 0.12736 | -0.0037085 | -0.0089999 | -0.12222 | -0.0095532 | 0.060633 | 0.055476 | 0.00549 | -0.010265 | 69.5663 | 69.7952 | 0.63171 | -53.302 | 69.809 | -53.2288 | -53.3249 | -52.5467 | 24.5499 | -53.3478 | 69.7815 | 69.6808 | -53.4302 | -53.476 | 0.01831 | -0.07782 | 0.14648 | 123.0423 | -0.054932 | 0.022888 | -0.096131 | -0.18311 | -0.22888 | 0.11902 | 0.70038 | -0.10071 | 0.12817 | 0.01831 | 123.056 | 122.8134 | 53.8788 | -122.9874 | 123.0286 | 122.9279 | 77.7969 | -123.1384
2699.0156 | 123.0103 | -51.9562 | 70.9808 | -0.25192 | 0.014071 | 0.071668 | 0.073081 | 0.12608 | -0.00029045 | -0.0066501 | -0.38925 | -0.0089124 | 0.064478 | 0.057185 | 0.0074126 | -0.013255 | 70.99 | 71.0037 | 0.54474 | -52.153 | 71.1777 | -51.9516 | -52.0523 | -51.3657 | 28.3997 | -52.1667 | 71.0495 | 70.9122 | -52.1851 | -52.2171 | 0.004578 | -0.09613 | 0.19684 | 122.9599 | -0.19684 | -0.10071 | 0.009155 | -0.22888 | -0.26093 | 0.068665 | 0.59051 | -0.21057 | 0.050354 | -0.068665 | 123.1338 | 122.9462 | 52.5009 | -123.0331 | 123.0057 | 122.8683 | 80.3558 | -123.1979
2700.0156 | 123.0972 | -52.8717 | 70.0378 | 0.24399 | 0.01044 | 0.071455 | 0.071158 | 0.12736 | -0.0028541 | -0.0079319 | -0.099335 | -0.011689 | 0.064264 | 0.056544 | 0.0074126 | -0.011119 | 69.8364 | 70.0653 | 0.58136 | -53.0457 | 70.0745 | -52.9587 | -53.0502 | -52.1942 | 26.3077 | -52.9449 | 70.0516 | 69.9692 | -53.0823 | -53.1097 | -0.086975 | -0.17853 | 0.036621 | 122.937 | -0.17395 | 0.004578 | -0.20142 | -0.21057 | -0.23804 | 0.013733 | 0.67749 | -0.073242 | 0.16479 | -0.068665 | 122.9462 | 122.7081 | 53.4531 | -123.0881 | 122.9233 | 122.8409 | 79.1794 | -123.1476
2701.0156 | 123.0972 | -52.5101 | 70.3812 | -0.20615 | 0.011081 | 0.070387 | 0.073294 | 0.12971 | -0.0030677 | -0.0085727 | -0.168 | -0.009126 | 0.059778 | 0.053767 | 0.0067718 | -0.013469 | 70.1843 | 70.4453 | 0.56763 | -52.6657 | 70.4773 | -52.5787 | -52.6474 | -51.915 | 24.3164 | -52.6474 | 70.4865 | 70.3766 | -52.7115 | -52.7618 | -0.068664 | -0.13733 | 0.09613 | 122.9553 | -0.15564 | -0.01831 | -0.19684 | -0.20142 | -0.25177 | 0.10529 | 0.59509 | -0.13733 | 0.11444 | -0.004578 | 122.9874 | 122.6944 | 53.0777 | -123.0286 | 122.9965 | 122.8867 | 76.8265 | -123.143
2702.0156 | 123.1476 | -52.8214 | 70.0333 | -0.20615 | 0.0072355 | 0.070173 | 0.07009 | 0.12822 | -0.0024269 | -0.0083591 | 0.59494 | -0.010621 | 0.062769 | 0.056544 | 0.006131 | -0.010905 | 69.9738 | 70.2072 | 0.63629 | -52.7344 | 70.2759 | -52.8122 | -52.9129 | -52.1484 | 25.4379 | -52.7573 | 70.1614 | 70.0928 | -52.9633 | -53.0685 | 0.009155 | -0.091553 | 0.24262 | 123.0286 | 0.086975 | 0.17853 | -0.059509 | -0.14191 | -0.24719 | 0.12817 | 0.67291 | 0.064087 | 0.31128 | 0.059509 | 123.0972 | 122.7951 | 53.4576 | -122.9462 | 122.9828 | 122.9141 | 78.2593 | -123.1018
2703.0156 | 123.0515 | -52.2995 | 70.665 | -0.23666 | 0.0095853 | 0.0706 | 0.071372 | 0.12843 | 0.0014185 | -0.0057957 | -0.40451 | -0.008058 | 0.065546 | 0.056758 | 0.00784 | -0.012614 | 69.9417 | 70.0562 | 0.43945 | -52.8763 | 70.34 | -52.7115 | -52.7527 | -51.7319 | 25.676 | -52.3819 | 70.6558 | 70.578 | -52.5055 | -52.5284 | -0.41199 | -0.45319 | -0.32501 | 122.3557 | -0.57678 | -0.1236 | -0.72327 | -0.20599 | -0.22888 | -0.009155 | 0.56763 | -0.082397 | 0.14648 | -0.086975 | 122.6395 | 122.2412 | 52.739 | -123.4177 | 122.9553 | 122.8775 | 77.9755 | -123.1934
2704.0156 | 123.1613 | -53.4027 | 69.4794 | -0.39688 | 0.0085171 | 0.067182 | 0.069663 | 0.12736 | -0.0015723 | -0.0068637 | -0.084076 | -0.012544 | 0.059778 | 0.058467 | 0.0067718 | -0.011119 | 69.6533 | 69.8044 | 0.43488 | -53.3981 | 69.809 | -53.2837 | -53.4073 | -52.8488 | 24.2477 | -53.7231 | 69.516 | 69.397 | -53.6545 | -53.7094 | 0.11902 | -0.004578 | 0.32959 | 123.2071 | 0.004578 | 0.009156 | 0.17395 | -0.25177 | -0.3067 | 0.036621 | 0.55389 | -0.32044 | -0.013733 | -0.082397 | 123.2117 | 123.056 | 53.8376 | -122.8867 | 122.9187 | 122.7997 | 77.6505 | -123.1888
2705.0156 | 122.9965 | -53.4988 | 69.4519 | -0.19089 | 0.011935 | 0.070387 | 0.074149 | 0.13014 | -0.0017859 | -0.0060093 | -0.18326 | -0.010835 | 0.061914 | 0.058039 | 0.0067718 | -0.013683 | 69.0674 | 69.223 | 0.32959 | -53.8971 | 69.3146 | -53.7643 | -53.8605 | -52.9221 | 24.3713 | -53.4988 | 69.4839 | 69.397 | -53.714 | -53.6911 | -0.2655 | -0.36163 | -0.13733 | 122.7219 | -0.39825 | -0.036621 | -0.38452 | -0.21515 | -0.19226 | 0.032044 | 0.57678 | 0 | 0.19226 | -0.054931 | 122.8134 | 122.5662 | 53.8284 | -123.3124 | 122.9828 | 122.8958 | 77.8702 | -123.143
2706.0156 | 123.143 | -54.8355 | 67.9779 | -0.19852 | 0.012149 | 0.073377 | 0.070944 | 0.12822 | -0.0058447 | -0.0081455 | -1.0301 | -0.010835 | 0.061487 | 0.055689 | 0.004422 | -0.01176 | 68.1747 | 68.4311 | 0.37994 | -54.7073 | 68.4082 | -54.6661 | -54.7256 | -53.7643 | 23.7122 | -54.5883 | 68.3945 | 68.2526 | -54.8584 | -54.982 | 0.16937 | 0.10986 | 0.4303 | 123.2666 | 0.12817 | 0.018311 | 0.19684 | -0.022888 | -0.14648 | 0.41656 | 1.0712 | 0.24719 | 0.39368 | 0.27466 | 123.2437 | 123.0103 | 55.2155 | -122.7036 | 123.23 | 123.0881 | 78.5477 | -122.9599
2707.0156 | 123.0194 | -53.9658 | 68.985 | -0.21378 | 0.010653 | 0.06761 | 0.070731 | 0.12822 | -0.00071785 | -0.0079319 | -0.168 | -0.009126 | 0.060846 | 0.057185 | 0.0069854 | -0.013469 | 68.9026 | 69.0308 | 0.29297 | -54.1397 | 69.1086 | -54.007 | -54.1168 | -53.302 | 24.1791 | -54.1489 | 69.0308 | 68.9392 | -54.1534 | -54.1992 | -0.041199 | -0.15106 | 0.1236 | 122.9965 | -0.17395 | -0.022888 | -0.082397 | -0.18768 | -0.23346 | 0.045777 | 0.66376 | -0.18311 | 0.050354 | -0.045776 | 123.0743 | 122.8683 | 54.2587 | -123.1018 | 122.9965 | 122.905 | 78.1448 | -123.1842
2708.0156 | 123.143 | -53.7506 | 69.1177 | -0.061188 | 0.0080899 | 0.069959 | 0.07009 | 0.12843 | -0.0032813 | -0.0051547 | 0.015106 | -0.010835 | 0.060633 | 0.057612 | 0.0050628 | -0.011546 | 69.1406 | 69.3695 | 0.40741 | -53.7781 | 69.4107 | -53.6453 | -53.7552 | -52.9907 | 24.6277 | -53.7918 | 69.2734 | 69.1635 | -53.8879 | -53.9795 | 0.10529 | -0.004578 | 0.29297 | 123.1201 | -0.027466 | -0.022888 | 0.022888 | -0.13733 | -0.22888 | 0.15564 | 0.75989 | -0.041199 | 0.18768 | 0.045776 | 123.1613 | 122.8912 | 54.158 | -122.8729 | 123.024 | 122.9141 | 78.3783 | -123.0972
2709.0156 | 123.0789 | -53.3157 | 69.6899 | -0.30533 | 0.010013 | 0.070173 | 0.074149 | 0.13078 | 0.00035035 | -0.0064365 | -0.22903 | -0.009126 | 0.062769 | 0.05633 | 0.0069854 | -0.01411 | 69.4244 | 69.5755 | 0.27924 | -53.5217 | 69.7311 | -53.4302 | -53.5172 | -52.7618 | 24.8611 | -53.4851 | 69.6213 | 69.5297 | -53.5721 | -53.5995 | -0.11444 | -0.20142 | 0.041199 | 122.8912 | -0.20599 | -0.004578 | -0.2655 | -0.25635 | -0.28381 | -0.068664 | 0.55389 | -0.16937 | 0.11444 | -0.16022 | 123.0469 | 122.7402 | 53.595 | -123.2071 | 122.937 | 122.8455 | 78.1769 | -123.2895
2710.0156 | 123.1476 | -53.7003 | 69.1772 | -0.19852 | 0.0091581 | 0.069959 | 0.070944 | 0.12864 | -0.0013587 | -0.0060093 | 0.77805 | -0.0095532 | 0.062128 | 0.055903 | 0.006131 | -0.011546 | 68.9713 | 69.136 | 0.79651 | -53.7643 | 69.2642 | -53.8193 | -53.9474 | -53.0457 | 24.765 | -53.7735 | 69.1544 | 69.0903 | -53.9383 | -53.9383 | -0.11902 | -0.24719 | 0.086975 | 122.8363 | -0.064087 | 0.18311 | -0.20599 | -0.23804 | -0.23804 | -0.022888 | 0.6546 | -0.073243 | 0.16479 | -0.086975 | 122.9645 | 122.6715 | 54.4968 | -123.1247 | 122.8546 | 122.7905 | 78.4653 | -123.1155
2711.0156 | 123.0103 | -54.1351 | 68.7881 | -0.24429 | 0.0074491 | 0.0706 | 0.072012 | 0.12672 | 0.00056395 | -0.0072911 | -0.03067 | -0.011689 | 0.064264 | 0.056117 | 0.008908 | -0.010692 | 68.5318 | 68.7469 | 0.55847 | -54.3091 | 68.8431 | -54.2267 | -54.3045 | -53.5217 | 24.3439 | -54.3228 | 68.8156 | 68.7149 | -54.3869 | -54.4281 | -0.091553 | -0.16937 | 0.054932 | 122.8821 | -0.17395 | -0.004578 | -0.25635 | -0.25177 | -0.29297 | 0.027466 | 0.6134 | -0.18768 | 0.10529 | -0.073242 | 122.9782 | 122.6669 | 54.6936 | -123.0927 | 122.9507 | 122.85 | 78.479 | -123.2162
2712.0156 | 123.056 | -54.7852 | 68.0466 | -0.22141 | 0.0080899 | 0.071241 | 0.069449 | 0.12993 | -0.0032813 | -0.0077183 | -0.084076 | -0.010835 | 0.061487 | 0.057826 | 0.006131 | -0.011974 | 68.1381 | 68.1747 | 0.34332 | -55.0232 | 68.2068 | -54.8538 | -54.95 | -54.1443 | 23.9868 | -55.0415 | 68.0923 | 68.0008 | -55.0095 | -55.0323 | -0.068665 | -0.16479 | 0.16022 | 122.9599 | -0.23804 | -0.073242 | 0.091553 | -0.2243 | -0.24719 | 0.045776 | 0.64087 | -0.25635 | -0.009155 | -0.045777 | 122.9919 | 122.9233 | 55.1285 | -122.9965 | 122.8775 | 122.7859 | 78.772 | -123.0789
2713.0156 | 123.0835 | -54.2267 | 68.6417 | -0.24429 | 0.0095853 | 0.071668 | 0.074149 | 0.12993 | -0.0019995 | -0.0057957 | -0.16037 | -0.011689 | 0.062555 | 0.055689 | 0.00784 | -0.014537 | 68.6508 | 68.8293 | 0.48065 | -54.2862 | 68.8751 | -54.2038 | -54.3228 | -53.4119 | 24.4492 | -54.2816 | 68.8843 | 68.7103 | -54.3777 | -54.4601 | 0.022889 | -0.09613 | 0.23346 | 123.056 | -0.059509 | 0.036621 | 0.009155 | -0.15106 | -0.23346 | 0.24261 | 0.81482 | -0.054931 | 0.17853 | 0.068664 | 123.1018 | 122.8775 | 54.7073 | -122.9645 | 123.111 | 122.937 | 78.6758 | -123.1018
2714.0156 | 123.0927 | -54.039 | 68.8431 | -0.22903 | 0.0078763 | 0.069746 | 0.07009 | 0.12928 | 0.00013675 | -0.0081455 | -0.168 | -0.012117 | 0.062342 | 0.057612 | 0.0065582 | -0.012187 | 68.8477 | 69.0628 | 0.54474 | -54.0939 | 69.1269 | -53.9841 | -54.071 | -53.4348 | 24.8154 | -54.2038 | 68.8751 | 68.8019 | -54.245 | -54.2725 | 0.054931 | -0.032044 | 0.28381 | 123.1018 | -0.054932 | -0.022888 | 0.004577 | -0.20599 | -0.23346 | 0.032043 | 0.60425 | -0.16479 | 0.068665 | -0.041199 | 123.1659 | 122.8867 | 54.5837 | -122.9141 | 122.9141 | 122.8409 | 78.8544 | -123.1155
2715.0156 | 123.1293 | -54.0482 | 68.811 | -0.16037 | 0.0083035 | 0.070814 | 0.072653 | 0.12886 | -0.0019995 | -0.0083591 | 1.541 | -0.009126 | 0.062128 | 0.055689 | 0.0084808 | -0.011119 | 68.7103 | 68.9255 | 0.65002 | -54.2267 | 68.9209 | -54.126 | -54.245 | -53.3798 | 24.8657 | -54.1626 | 68.8431 | 68.7195 | -54.2725 | -54.3274 | -0.07782 | -0.19684 | 0.10986 | 122.9736 | -0.17853 | 0.01831 | -0.10071 | -0.2243 | -0.27924 | 0.032044 | 0.66834 | -0.11444 | 0.16479 | -0.091553 | 122.9691 | 122.7585 | 54.6982 | -123.056 | 122.8912 | 122.7676 | 78.9139 | -123.1384
2716.0156 | 123.143 | -54.2679 | 68.6005 | -0.03067 | 0.012149 | 0.073377 | 0.070303 | 0.12715 | -0.0015723 | -0.0083591 | -0.0077819 | -0.011689 | 0.062769 | 0.055903 | 0.004422 | -0.01176 | 68.4402 | 68.6554 | 0.60425 | -54.4601 | 68.6783 | -54.3961 | -54.4601 | -53.5583 | 24.6048 | -54.4373 | 68.6005 | 68.4952 | -54.483 | -54.5563 | -0.12817 | -0.19226 | 0.07782 | 122.9233 | -0.19226 | 0 | -0.16022 | -0.21515 | -0.28839 | 0 | 0.70953 | -0.16937 | 0.11902 | -0.10529 | 122.9462 | 122.7081 | 54.8721 | -123.0606 | 122.8683 | 122.7631 | 78.8727 | -123.1567
2717.0156 | 123.024 | -54.2175 | 68.6783 | -0.24429 | 0.0091581 | 0.071668 | 0.07009 | 0.128 | -0.0011451 | -0.0055821 | -0.16037 | -0.010408 | 0.062555 | 0.057612 | 0.006131 | -0.012401 | 68.5913 | 68.7469 | 0.54016 | -54.3823 | 68.7927 | -54.2725 | -54.3732 | -53.4988 | 24.7238 | -54.3869 | 68.7561 | 68.6417 | -54.4464 | -54.4968 | -0.054932 | -0.15564 | 0.11444 | 122.9645 | -0.16479 | -0.009155 | -0.086975 | -0.22888 | -0.27924 | 0.07782 | 0.71869 | -0.16937 | 0.10986 | -0.036621 | 123.0103 | 122.8088 | 54.7577 | -123.0515 | 122.9736 | 122.8592 | 78.9413 | -123.175
2718.0156 | 123.143 | -53.6911 | 69.0948 | -0.0383 | 0.0089443 | 0.0706 | 0.071799 | 0.128 | -0.0026405 | -0.0070773 | -0.11459 | -0.011689 | 0.065546 | 0.056117 | 0.008908 | -0.011333 | 69.3787 | 69.6304 | 0.74158 | -53.4851 | 69.603 | -53.4302 | -53.5217 | -52.5696 | 25.2502 | -53.7003 | 69.4931 | 69.3329 | -53.746 | -53.8605 | 0.26093 | 0.16937 | 0.50812 | 123.3215 | 0.20599 | 0.036622 | 0.28381 | -0.054932 | -0.16937 | 0.39825 | 1.1215 | -0.009155 | 0.16022 | 0.23804 | 123.2941 | 123.0698 | 54.4327 | -122.6166 | 123.1842 | 123.024 | 78.9413 | -122.9553
2719.0156 | 123.0331 | -54.0848 | 68.8477 | -0.17563 | 0.015994 | 0.069319 | 0.074362 | 0.12907 | 0.0048363 | -0.0036595 | -0.12985 | -0.0084852 | 0.066187 | 0.054835 | 0.0084808 | -0.016246 | 68.692 | 68.8065 | 0.51727 | -54.2358 | 68.9438 | -54.158 | -54.2496 | -53.3569 | 24.2889 | -54.1718 | 68.9987 | 68.8797 | -54.2496 | -54.3045 | -0.073242 | -0.16479 | 0.096131 | 122.8912 | -0.15106 | 0.013733 | -0.15564 | -0.16479 | -0.21973 | 0.15106 | 0.72784 | -0.086975 | 0.13275 | 0.032044 | 123.0286 | 122.7768 | 54.6021 | -123.0972 | 123.0835 | 122.9645 | 78.3737 | -123.1522
2720.0156 | 123.1796 | -54.5425 | 68.3121 | -0.061188 | 0.0087307 | 0.0706 | 0.069449 | 0.12864 | -0.0030677 | -0.0072911 | -0.00015237 | -0.011689 | 0.06106 | 0.058894 | 0.0046356 | -0.0098374 | 68.3304 | 68.5593 | 0.54932 | -54.6158 | 68.5501 | -54.5517 | -54.6524 | -53.7781 | 24.7238 | -54.6936 | 68.367 | 68.28 | -54.7577 | -54.7989 | -0.009155 | -0.10986 | 0.23804 | 123.1018 | -0.073242 | 0.036621 | 0.01831 | -0.21515 | -0.25635 | 0.054931 | 0.76447 | -0.15106 | 0.10529 | -0.032044 | 123.0927 | 122.8729 | 55.0919 | -122.9645 | 122.9095 | 122.8226 | 79.2664 | -123.111
2721.0156 | 123.1155 | -53.27 | 69.603 | 0.63309 | 0.0095853 | 0.071882 | 0.072226 | 0.12993 | -0.0015723 | -0.0077183 | -0.11459 | -0.010194 | 0.060846 | 0.056758 | 0.0069854 | -0.015178 | 69.6213 | 69.809 | 0.64087 | -53.3478 | 69.7906 | -53.2471 | -53.3524 | -52.5558 | 25.8179 | -53.3981 | 69.6579 | 69.5343 | -53.5217 | -53.5309 | 0.022888 | -0.082398 | 0.18768 | 123.0789 | -0.07782 | 0.004578 | 0.018311 | -0.25177 | -0.26093 | 0.054932 | 0.71411 | -0.12817 | 0.13275 | -0.068664 | 123.0606 | 122.8912 | 53.9108 | -122.9553 | 122.9279 | 122.8043 | 79.0878 | -123.1338
2722.0156 | 123.1201 | -52.4277 | 70.4498 | 0.11429 | 0.0093717 | 0.071241 | 0.068167 | 0.12843 | -0.0011451 | -0.0068637 | 0.30502 | -0.011262 | 0.06106 | 0.056758 | 0.006131 | -0.010692 | 70.1843 | 70.4224 | 0.6546 | -52.6154 | 70.5002 | -52.565 | -52.6703 | -51.7868 | 26.3168 | -52.4734 | 70.4956 | 70.372 | -52.6657 | -52.7069 | -0.13733 | -0.24262 | 0.050354 | 122.85 | -0.18768 | 0.054932 | -0.2655 | -0.23804 | -0.27924 | 0.045776 | 0.64087 | -0.045777 | 0.23346 | -0.07782 | 122.9279 | 122.612 | 53.0823 | -123.1201 | 122.9233 | 122.7997 | 78.7445 | -123.1567
2723.0156 | 123.143 | -51.9791 | 70.8939 | -0.17563 | 0.010013 | 0.069105 | 0.072012 | 0.12843 | -0.0015723 | -0.0068637 | 0.70175 | -0.0099806 | 0.062342 | 0.057185 | 0.0074126 | -0.012401 | 70.5048 | 70.697 | 0.75989 | -52.446 | 70.7428 | -52.3132 | -52.4139 | -51.4023 | 26.7151 | -52.0798 | 70.8389 | 70.7886 | -52.2675 | -52.272 | -0.33417 | -0.43487 | -0.15106 | 122.6761 | -0.46692 | -0.032044 | -0.3891 | -0.28839 | -0.29297 | -0.054932 | 0.57678 | -0.10071 | 0.19226 | -0.10529 | 122.7219 | 122.4838 | 52.739 | -123.3078 | 122.818 | 122.7676 | 78.6942 | -123.1659
2724.0156 | 122.9965 | -52.9037 | 70.0607 | -0.22903 | 0.012362 | 0.073164 | 0.072012 | 0.13014 | 0.0027001 | -0.0068637 | -0.20615 | -0.012758 | 0.061701 | 0.056758 | 0.0093354 | -0.012401 | 69.9097 | 69.9829 | 0.62714 | -53.0869 | 70.1843 | -52.9587 | -53.0685 | -52.272 | 27.1088 | -53.1052 | 70.1523 | 70.0104 | -53.1189 | -53.1509 | -0.054931 | -0.16479 | 0.1236 | 122.8867 | -0.1831 | -0.018311 | -0.15106 | -0.21515 | -0.24719 | 0.091553 | 0.63171 | -0.20142 | 0.045776 | -0.050354 | 123.0881 | 122.8134 | 53.5309 | -123.1293 | 123.056 | 122.9141 | 80.0125 | -123.2117
2725.0156 | 123.1201 | -53.6316 | 69.2322 | -2.5941 | 0.0076627 | 0.066755 | 0.070731 | 0.128 | -0.00050425 | -0.0017369 | -0.053558 | -0.0084852 | 0.060846 | 0.055262 | 0.0082672 | -0.013469 | 69.4061 | 69.7861 | 0.79193 | -53.3936 | 69.7357 | -53.3249 | -53.3936 | -52.858 | 24.6872 | -53.92 | 69.4199 | 69.2047 | -53.8101 | -53.8971 | 0.3067 | 0.23804 | 0.50354 | 123.4177 | 0.23804 | 0 | 0.17395 | -0.17853 | -0.2655 | 0.18768 | 0.77362 | -0.28839 | -0.022888 | -0.027466 | 123.3673 | 123.0377 | 54.4235 | -122.6257 | 123.0515 | 122.8363 | 78.3188 | -123.1293
2726.0156 | 123.143 | -53.1738 | 69.6854 | 0.022736 | 0.0076627 | 0.07295 | 0.070517 | 0.12629 | -0.0039221 | -0.0077183 | -0.00015237 | -0.011689 | 0.062769 | 0.053767 | 0.0067718 | -0.013469 | 69.429 | 69.6579 | 0.76446 | -53.3752 | 69.754 | -53.27 | -53.3432 | -52.4551 | 25.6439 | -53.27 | 69.7495 | 69.6487 | -53.4073 | -53.4393 | -0.09613 | -0.16937 | 0.068664 | 122.8317 | -0.20142 | -0.032043 | -0.25635 | -0.23346 | -0.2655 | 0.064087 | 0.71869 | -0.09613 | 0.16937 | -0.036621 | 122.9279 | 122.6028 | 53.9383 | -123.0286 | 122.9233 | 122.8226 | 78.8177 | -123.1247
2727.0156 | 123.1567 | -52.8671 | 69.928 | -0.091705 | 0.0095853 | 0.069105 | 0.070303 | 0.13014 | -0.0024269 | -0.0077183 | -0.12222 | -0.011049 | 0.062982 | 0.055903 | 0.0080536 | -0.011333 | 69.9738 | 70.2164 | 0.90179 | -52.9083 | 70.1935 | -52.8534 | -52.977 | -52.0432 | 26.1841 | -52.6657 | 70.2026 | 70.0562 | -53.0045 | -53.0869 | 0.013732 | -0.10986 | 0.2655 | 123.0835 | -0.041199 | 0.068665 | 0.045776 | -0.13733 | -0.21973 | 0.27466 | 0.82397 | 0.20142 | 0.42114 | 0.12817 | 123.0606 | 122.8409 | 53.7689 | -122.905 | 123.0698 | 122.9233 | 79.0512 | -123.0148
2728.0156 | 123.0652 | -52.8625 | 69.9966 | 0.16769 | 0.0076627 | 0.071455 | 0.069235 | 0.12907 | -0.0030677 | -0.0060093 | 0.10666 | -0.010621 | 0.062342 | 0.055262 | 0.008908 | -0.011974 | 69.7128 | 69.9005 | 0.83313 | -53.2196 | 69.96 | -53.0823 | -53.2013 | -52.2034 | 25.9369 | -52.8488 | 70.0195 | 69.9051 | -53.1097 | -53.1235 | -0.21973 | -0.33874 | -0.036621 | 122.7631 | -0.35705 | -0.01831 | -0.28381 | -0.24719 | -0.26093 | 0.022888 | 0.65918 | 0.013733 | 0.27466 | -0.091553 | 122.8226 | 122.5754 | 53.6957 | -123.1979 | 122.8821 | 122.7676 | 78.7994 | -123.1201
2729.0312 | 123.0331 | -53.0594 | 69.8822 | 0.053253 | 0.017489 | 0.065901 | 0.075217 | 0.128 | 0.0067589 | -0.0047275 | 0.030365 | -0.0048536 | 0.065759 | 0.055049 | 0.0097626 | -0.013683 | 69.8502 | 69.8959 | 0.72784 | -53.1967 | 70.0836 | -53.0319 | -53.1464 | -52.2903 | 25.3647 | -53.2379 | 69.9829 | 69.8776 | -53.2425 | -53.3066 | 0.027466 | -0.086975 | 0.20142 | 122.9553 | -0.13733 | -0.050354 | -0.032043 | -0.18311 | -0.24719 | 0.10071 | 0.76904 | -0.17853 | 0.068665 | -0.004577 | 123.143 | 122.9095 | 53.7872 | -123.0286 | 123.0423 | 122.937 | 78.4241 | -123.1888
2730.0156 | 123.143 | -53.6453 | 69.2368 | 0.25162 | 0.0087307 | 0.069532 | 0.068594 | 0.12544 | -0.0037085 | -0.0079319 | 0.068512 | -0.010194 | 0.061701 | 0.056971 | 0.0050628 | -0.010265 | 69.0262 | 69.2459 | 0.9201 | -53.8742 | 69.3283 | -53.7689 | -53.8605 | -52.89 | 25.5569 | -53.6087 | 69.3237 | 69.2184 | -53.8376 | -53.8971 | -0.1236 | -0.21515 | 0.091553 | 122.8912 | -0.22888 | -0.013733 | -0.21057 | -0.19226 | -0.25177 | 0.086975 | 0.75531 | 0.036621 | 0.28839 | -0.01831 | 122.9736 | 122.6715 | 54.5654 | -123.0972 | 122.9691 | 122.8638 | 79.2023 | -123.1338
2731.0156 | 123.1705 | -52.5787 | 70.2438 | -0.053558 | 0.0072355 | 0.070814 | 0.070731 | 0.128 | -0.0045631 | -0.0064365 | 0.0074766 | -0.011476 | 0.062555 | 0.056544 | 0.0046356 | -0.011119 | 70.2209 | 70.3903 | 1.0849 | -52.7527 | 70.3812 | -52.6657 | -52.739 | -51.7502 | 26.4267 | -52.5558 | 70.372 | 70.2621 | -52.771 | -52.8214 | -0.086975 | -0.16022 | 0.13733 | 122.9691 | -0.17395 | -0.013733 | -0.022888 | -0.19226 | -0.24262 | 0.12817 | 0.82855 | 0.022888 | 0.2655 | 0.018311 | 122.9599 | 122.7997 | 53.6636 | -122.9828 | 122.9507 | 122.8409 | 79.0054 | -123.0652
2732.0156 | 123.111 | -53.1876 | 69.6945 | 0.0074768 | 0.0091581 | 0.072309 | 0.070731 | 0.12758 | -0.00050425 | -0.0057957 | 0.11429 | -0.012544 | 0.062555 | 0.058039 | 0.0050628 | -0.01176 | 69.3558 | 69.4519 | 0.81482 | -53.7094 | 69.5206 | -53.5538 | -53.6499 | -52.5101 | 25.9689 | -53.1647 | 69.6762 | 69.5892 | -53.4531 | -53.4531 | -0.36621 | -0.46234 | -0.17395 | 122.6395 | -0.52185 | -0.05951 | -0.33875 | -0.2655 | -0.2655 | -0.018311 | 0.67749 | 0.022888 | 0.28839 | -0.10529 | 122.7081 | 122.5433 | 54.0024 | -123.3444 | 122.8638 | 122.7768 | 79.1565 | -123.1476
2733.0156 | 123.1384 | -53.6087 | 69.191 | -0.0383 | 0.0083035 | 0.070814 | 0.068381 | 0.12693 | -0.00029045 | -0.0077183 | -0.0077819 | -0.0099806 | 0.061273 | 0.055903 | 0.0069854 | -0.012401 | 69.2505 | 69.4473 | 1.0025 | -53.6682 | 69.4794 | -53.5812 | -53.6865 | -52.6978 | 25.9048 | -53.7552 | 69.4153 | 69.2825 | -53.7872 | -53.8422 | 0.027466 | -0.077819 | 0.28839 | 123.056 | -0.059509 | 0.01831 | 0.059509 | -0.17853 | -0.23346 | 0.2243 | 0.91095 | -0.14648 | 0.086975 | 0.091553 | 123.0881 | 122.8592 | 54.6112 | -122.8775 | 123.024 | 122.8912 | 79.5136 | -123.0331
2734.0312 | 123.1338 | -53.0914 | 69.7403 | 0.20584 | 0.015353 | 0.071455 | 0.072012 | 0.12886 | 0.0031273 | -0.0047275 | 0.18295 | -0.0097668 | 0.062769 | 0.055262 | 0.01019 | -0.014751 | 69.5206 | 69.6167 | 0.96588 | -53.3707 | 69.7128 | -53.2974 | -53.3981 | -52.3865 | 26.1475 | -53.1281 | 69.8044 | 69.6899 | -53.3569 | -53.3707 | -0.20599 | -0.3067 | -0.027465 | 122.7081 | -0.27924 | 0.027465 | -0.21973 | -0.2655 | -0.27924 | 0.064087 | 0.70496 | -0.036621 | 0.24262 | -0.050354 | 122.8043 | 122.612 | 54.0573 | -123.1384 | 122.8958 | 122.7814 | 79.2389 | -123.111
2735.0156 | 123.1247 | -53.2333 | 69.6396 | -0.03067 | 0.0065945 | 0.071241 | 0.071158 | 0.12736 | -0.0022131 | -0.0038731 | 0.0074766 | -0.010621 | 0.061701 | 0.056117 | 0.0063446 | -0.012187 | 69.4473 | 69.6625 | 0.97504 | -53.4576 | 69.6945 | -53.3798 | -53.4668 | -52.5558 | 25.9918 | -53.2974 | 69.6625 | 69.5847 | -53.4576 | -53.4943 | -0.14648 | -0.23346 | 0.054932 | 122.8958 | -0.22431 | 0.009155 | -0.19226 | -0.22431 | -0.26093 | 0.022889 | 0.67749 | -0.064087 | 0.19684 | -0.054931 | 122.9279 | 122.6807 | 54.2084 | -123.1064 | 122.8958 | 122.818 | 79.2252 | -123.1338
2736.0156 | 123.0972 | -53.215 | 69.6259 | 0.053253 | 0.0085171 | 0.069959 | 0.069449 | 0.12822 | -0.0022131 | -0.0062229 | 0.12192 | -0.009126 | 0.062342 | 0.056544 | 0.007199 | -0.010905 | 69.5435 | 69.722 | 0.95673 | -53.3936 | 69.8044 | -53.2654 | -53.3798 | -52.4918 | 26.3489 | -53.3295 | 69.7311 | 69.6213 | -53.4073 | -53.4622 | -0.050354 | -0.16479 | 0.17853 | 122.937 | -0.17853 | -0.013733 | -0.082397 | -0.19226 | -0.24719 | 0.10529 | 0.72327 | -0.11444 | 0.13275 | -0.004577 | 123.0194 | 122.7585 | 54.1718 | -123.0057 | 122.9462 | 122.8363 | 79.5639 | -123.0881
2737.0156 | 123.23 | -53.1876 | 69.6854 | -0.16037 | 0.0080899 | 0.068464 | 0.071158 | 0.13057 | -0.00029045 | -0.0075047 | -0.099335 | -0.011049 | 0.061701 | 0.055049 | 0.0065582 | -0.013469 | 69.5892 | 69.8227 | 0.9613 | -53.3386 | 69.7861 | -53.2425 | -53.3249 | -52.4277 | 26.3809 | -53.0869 | 69.8044 | 69.7037 | -53.3661 | -53.4302 | -0.054932 | -0.13733 | 0.10071 | 123.0103 | -0.15106 | -0.013733 | -0.096131 | -0.17853 | -0.24262 | 0.11902 | 0.75989 | 0.10071 | 0.34332 | 0.01831 | 122.9736 | 122.7768 | 54.1489 | -123.0103 | 122.9919 | 122.8912 | 79.5685 | -123.1155
2738.0156 | 123.1567 | -53.1281 | 69.7083 | 2.6701 | 0.012576 | 0.071455 | 0.070303 | 0.13057 | -0.0015723 | -0.0064365 | -0.19089 | -0.010408 | 0.060419 | 0.055903 | 0.0074126 | -0.013683 | 69.5938 | 69.7128 | 0.87891 | -53.3752 | 69.722 | -53.3249 | -53.421 | -52.446 | 26.3672 | -53.2608 | 69.7403 | 69.6304 | -53.3752 | -53.4027 | -0.19684 | -0.29297 | 0.013733 | 122.8409 | -0.24719 | 0.045777 | -0.11444 | -0.24719 | -0.27466 | 0.032043 | 0.68207 | -0.13275 | 0.14191 | -0.07782 | 122.85 | 122.7219 | 54.007 | -123.1293 | 122.8683 | 122.7585 | 79.4952 | -123.111
2739.0312 | 123.1018 | -53.4302 | 69.4427 | 0.037994 | 0.0095853 | 0.070814 | 0.067954 | 0.12736 | -0.0034949 | -0.0049411 | 0.14481 | -0.010194 | 0.061914 | 0.055689 | 0.0059174 | -0.01176 | 69.2093 | 69.5892 | 0.78278 | -53.595 | 69.5984 | -53.4576 | -53.5492 | -52.6566 | 26.2985 | -53.476 | 69.5801 | 69.4244 | -53.595 | -53.6636 | -0.027466 | -0.11902 | 0.15564 | 123.0194 | -0.16479 | -0.045777 | -0.23346 | -0.16479 | -0.23346 | 0.13733 | 0.77362 | -0.045776 | 0.18768 | -0.018311 | 123.0286 | 122.6395 | 54.213 | -122.9919 | 123.0103 | 122.8546 | 79.7287 | -123.1064
2740.0156 | 123.1155 | -53.3066 | 69.5618 | -0.19852 | 0.010867 | 0.071668 | 0.069235 | 0.12907 | 0.00035035 | -0.0064365 | -0.15274 | -0.0076306 | 0.060633 | 0.056117 | 0.0069854 | -0.012828 | 69.4977 | 69.6854 | 0.79193 | -53.421 | 69.6899 | -53.3661 | -53.4393 | -52.6016 | 26.1612 | -53.3844 | 69.6396 | 69.516 | -53.5355 | -53.5355 | -0.059509 | -0.13275 | 0.12817 | 122.9919 | -0.11444 | 0.01831 | -0.064087 | -0.22888 | -0.22888 | 0.077819 | 0.70496 | -0.077819 | 0.15106 | -0.045777 | 122.9965 | 122.8043 | 54.0985 | -123.0011 | 122.9462 | 122.8226 | 79.4678 | -123.0972
2741.0156 | 123.1338 | -52.446 | 70.4361 | 0.053253 | 0.0065945 | 0.071668 | 0.072226 | 0.128 | -0.00071785 | -0.0060093 | 0.10666 | -0.010835 | 0.064478 | 0.056971 | 0.0059174 | -0.010265 | 69.9005 | 70.2988 | 0.93384 | -52.6611 | 70.34 | -52.6337 | -52.739 | -51.741 | 26.7197 | -52.5467 | 70.5322 | 70.3995 | -52.6382 | -52.6703 | -0.18768 | -0.29297 | -0.09613 | 122.7448 | -0.21515 | 0.07782 | -0.53558 | -0.19226 | -0.2243 | 0.096131 | 0.70496 | -0.10071 | 0.1236 | -0.036621 | 122.786 | 122.3465 | 53.3798 | -123.175 | 122.9782 | 122.8455 | 79.1656 | -123.1064
2742.0156 | 123.0972 | -52.3911 | 70.4498 | 0.17532 | 0.0097989 | 0.069746 | 0.072226 | 0.13035 | 0.00077755 | -0.0064365 | 0.19821 | -0.011049 | 0.061487 | 0.055689 | 0.0074126 | -0.011974 | 70.2118 | 70.4178 | 0.84686 | -52.6794 | 70.459 | -52.5742 | -52.652 | -51.6907 | 26.9257 | -52.5421 | 70.5505 | 70.4178 | -52.6062 | -52.6566 | -0.18311 | -0.26093 | 0.009155 | 122.8088 | -0.28839 | -0.027465 | -0.23804 | -0.21515 | -0.2655 | 0.10071 | 0.70038 | -0.15106 | 0.11444 | -0.032043 | 122.85 | 122.6028 | 53.2379 | -123.1018 | 122.9416 | 122.8088 | 79.3167 | -123.1064
2743.0156 | 123.1064 | -52.2125 | 70.6558 | -0.03067 | 0.0083035 | 0.069532 | 0.073081 | 0.12993 | -0.0015723 | -0.0066501 | 0.076141 | -0.010408 | 0.063196 | 0.057826 | 0.0067718 | -0.012187 | 70.5002 | 70.6787 | 0.80566 | -52.3956 | 70.7703 | -52.2903 | -52.3865 | -51.4618 | 26.3718 | -52.2446 | 70.752 | 70.6467 | -52.4185 | -52.4323 | -0.07782 | -0.17395 | 0.11444 | 122.8912 | -0.18311 | -0.009155 | -0.15564 | -0.20599 | -0.21973 | 0.09613 | 0.75073 | -0.032044 | 0.18768 | -0.009156 | 122.9828 | 122.7127 | 53.0182 | -123.0423 | 122.9645 | 122.8592 | 78.5843 | -123.0881
2744.0312 | 123.1613 | -53.5172 | 69.3237 | 0.068512 | 0.01044 | 0.069746 | 0.070517 | 0.12907 | -0.0015723 | -0.0075047 | 0.045624 | -0.0095532 | 0.061273 | 0.05633 | 0.0080536 | -0.012614 | 69.1589 | 69.2871 | 0.61798 | -53.8284 | 69.3787 | -53.7048 | -53.7735 | -52.7527 | 25.6027 | -53.6499 | 69.429 | 69.3146 | -53.7186 | -53.7689 | -0.18768 | -0.25635 | 0.054932 | 122.8043 | -0.31128 | -0.054931 | -0.16479 | -0.20142 | -0.25177 | 0.10529 | 0.76447 | -0.13275 | 0.11902 | -0.009155 | 122.8958 | 122.6761 | 54.1351 | -123.0972 | 122.9462 | 122.8317 | 79.1199 | -123.0927
2745.0156 | 123.0698 | -53.2196 | 69.6213 | 0.068512 | 0.0078763 | 0.069105 | 0.071158 | 0.12907 | 0.00013675 | -0.0083591 | -1.4955 | -0.010408 | 0.060633 | 0.056758 | 0.0076264 | -0.011974 | 69.4885 | 69.6442 | 0.59967 | -53.4897 | 69.7128 | -53.3615 | -53.4348 | -52.5055 | 25.7858 | -53.302 | 69.7037 | 69.6259 | -53.4393 | -53.476 | -0.14191 | -0.21515 | 0.091553 | 122.8638 | -0.27008 | -0.054932 | -0.13275 | -0.21973 | -0.25635 | 0.082397 | 0.71411 | -0.082398 | 0.17395 | 0.004577 | 122.9324 | 122.7081 | 53.8193 | -123.056 | 122.9233 | 122.8455 | 79.0054 | -123.0972
2746.0156 | 123.1201 | -53.5583 | 69.3237 | 0.16006 | 0.0074491 | 0.071668 | 0.069235 | 0.12886 | -0.0019995 | -0.0070773 | 0.068512 | -0.010835 | 0.060633 | 0.056544 | 0.0069854 | -0.012401 | 69.2596 | 69.4199 | 0.67291 | -53.7277 | 69.4748 | -53.6224 | -53.7323 | -52.7481 | 26.4267 | -53.7369 | 69.3924 | 69.2642 | -53.7689 | -53.7872 | -0.064087 | -0.17395 | 0.15106 | 122.9782 | -0.16937 | 0.004578 | -0.064086 | -0.21057 | -0.22888 | 0.068665 | 0.81024 | -0.17853 | 0.050354 | -0.059509 | 123.0331 | 122.818 | 54.2313 | -123.056 | 122.9507 | 122.8226 | 79.985 | -123.111
2747.0156 | 123.1155 | -52.9953 | 69.8593 | 0.037994 | 0.0078763 | 0.072523 | 0.069663 | 0.12736 | -0.0056311 | -0.0060093 | 0.076141 | -0.012758 | 0.061914 | 0.058039 | 0.0080536 | -0.011974 | 69.928 | 69.9326 | 0.78278 | -53.0731 | 70.079 | -52.9724 | -53.0594 | -52.2171 | 26.7151 | -53.1509 | 69.9738 | 69.8318 | -53.1784 | -53.2425 | 0.022888 | -0.064087 | 0.21973 | 122.9279 | -0.07782 | -0.013733 | 0.068665 | -0.18311 | -0.24719 | 0.11444 | 0.7782 | -0.15564 | 0.091553 | -0.027466 | 123.0743 | 122.9233 | 53.7781 | -122.9187 | 122.9691 | 122.8271 | 79.7104 | -123.1018
2748.0156 | 123.1567 | -52.8717 | 69.9554 | -0.061188 | 0.0087307 | 0.073164 | 0.072653 | 0.12672 | -0.0013587 | -0.0040867 | -0.00015237 | -0.010408 | 0.061701 | 0.056117 | 0.0082672 | -0.013042 | 69.8181 | 70.0104 | 1.0071 | -53.1052 | 70.015 | -53.0365 | -53.1326 | -52.1255 | 26.8478 | -52.9221 | 69.9875 | 69.9051 | -53.1464 | -53.1509 | -0.16479 | -0.26093 | 0.05951 | 122.8821 | -0.23346 | 0.027465 | -0.13733 | -0.27466 | -0.27924 | 0.032044 | 0.74616 | -0.050354 | 0.22888 | -0.050354 | 122.8867 | 122.6898 | 53.8788 | -123.0881 | 122.8592 | 122.7768 | 79.7195 | -123.1064
2749.0312 | 123.0881 | -52.9541 | 69.9417 | 0.19821 | 0.017276 | 0.068678 | 0.074362 | 0.12715 | 0.0048363 | -0.0057957 | 0.11429 | -0.009126 | 0.064905 | 0.055476 | 0.010617 | -0.014751 | 69.9097 | 70.015 | 0.99792 | -53.0182 | 70.1843 | -52.9358 | -53.0045 | -52.034 | 26.7838 | -52.9816 | 70.1248 | 69.9417 | -53.1235 | -53.1601 | 0.018311 | -0.050354 | 0.24262 | 122.9691 | -0.064086 | -0.013732 | -0.032043 | -0.16937 | -0.20599 | 0.18311 | 0.9201 | -0.027465 | 0.17853 | 0 | 123.1384 | 122.8638 | 53.952 | -122.9462 | 123.0789 | 122.8958 | 79.7379 | -123.1018
2750.0156 | 123.0835 | -52.2125 | 70.6467 | 0.15244 | 0.013644 | 0.070387 | 0.070731 | 0.12822 | -0.00071785 | -0.0049411 | 0.12955 | -0.0093396 | 0.062982 | 0.056758 | 0.0074126 | -0.01411 | 70.6055 | 70.7703 | 0.97046 | -52.4002 | 70.7748 | -52.2903 | -52.3956 | -51.5213 | 27.2141 | -52.4139 | 70.6467 | 70.5276 | -52.4826 | -52.4963 | -0.07782 | -0.18311 | 0.12817 | 122.9828 | -0.18768 | -0.004578 | -0.041198 | -0.27008 | -0.28381 | 0 | 0.69122 | -0.20142 | 0.082398 | -0.11902 | 122.9874 | 122.818 | 53.183 | -123.0423 | 122.8592 | 122.7402 | 79.4266 | -123.143
2751.0156 | 123.0972 | -54.0573 | 68.8202 | 0.18295 | 0.011081 | 0.068678 | 0.068808 | 0.12629 | -7.6852e-05 | -0.0060093 | 0.19821 | -0.010194 | 0.061273 | 0.056971 | 0.00784 | -0.010692 | 68.7057 | 68.8843 | 0.71869 | -54.2404 | 68.9163 | -54.1077 | -54.1992 | -53.2654 | 26.0239 | -54.2084 | 68.8477 | 68.7744 | -54.2633 | -54.2999 | -0.050354 | -0.14191 | 0.096131 | 122.9416 | -0.1831 | -0.041198 | -0.11444 | -0.20599 | -0.24261 | 0.027466 | 0.79193 | -0.15106 | 0.091553 | -0.045776 | 122.9736 | 122.7631 | 54.776 | -123.0194 | 122.905 | 122.8317 | 80.0812 | -123.1201
2752.0156 | 123.1247 | -53.5995 | 69.2596 | -1.198 | 0.0085171 | 0.069319 | 0.07244 | 0.12544 | -0.00071785 | -0.0057957 | 0.076141 | -0.0099806 | 0.061273 | 0.055049 | 0.0063446 | -0.010692 | 69.223 | 69.3787 | 0.70953 | -53.7003 | 69.4565 | -53.5767 | -53.6774 | -52.7252 | 26.2253 | -53.746 | 69.4061 | 69.2825 | -53.7872 | -53.8559 | 0.022888 | -0.07782 | 0.19684 | 122.9782 | -0.10071 | -0.022888 | -0.036622 | -0.18768 | -0.25635 | 0.14648 | 0.87433 | -0.14648 | 0.10986 | 0.022888 | 123.056 | 122.8226 | 54.3091 | -122.937 | 123.0057 | 122.8821 | 79.8248 | -123.1155
2753.0156 | 123.111 | -53.8925 | 68.985 | 0.17532 | 0.0085171 | 0.067823 | 0.071372 | 0.12907 | -0.00050425 | -0.0077183 | 0.19058 | -0.010835 | 0.061914 | 0.054621 | 0.0076264 | -0.011974 | 68.7469 | 68.9117 | 0.66834 | -54.2542 | 68.9667 | -54.0939 | -54.1763 | -53.0502 | 26.0925 | -53.9474 | 69.0399 | 68.9392 | -54.1031 | -54.1489 | -0.20142 | -0.28381 | -0.01831 | 122.8043 | -0.36163 | -0.077819 | -0.23804 | -0.21057 | -0.25635 | 0.054932 | 0.84228 | -0.054932 | 0.20142 | -0.045776 | 122.8592 | 122.6395 | 54.5609 | -123.1613 | 122.9324 | 122.8317 | 79.985 | -123.1338
2754.0312 | 123.0103 | -53.0319 | 69.8685 | -0.71732 | 0.017062 | 0.067182 | 0.072867 | 0.13142 | 0.0044091 | -0.0036595 | 0.076141 | -0.0084852 | 0.061914 | 0.055049 | 0.00784 | -0.015392 | 69.7128 | 69.7678 | 0.68207 | -53.2883 | 69.9829 | -53.1418 | -53.2333 | -52.1988 | 26.4175 | -53.1601 | 70.015 | 69.873 | -53.2013 | -53.2608 | -0.10986 | -0.20142 | 0.11444 | 122.7997 | -0.25635 | -0.054932 | -0.15564 | -0.16937 | -0.22888 | 0.14648 | 0.83313 | -0.12817 | 0.10071 | 0.004578 | 123.0148 | 122.7448 | 53.714 | -123.1018 | 123.0469 | 122.905 | 79.4495 | -123.1293
2755.0156 | 123.0743 | -52.3819 | 70.5048 | 0.11429 | 0.011508 | 0.070387 | 0.070303 | 0.12736 | -0.0037085 | -0.0072911 | 0.083771 | -0.0084852 | 0.06106 | 0.056117 | 0.0086944 | -0.0098374 | 70.3217 | 70.4727 | 0.84686 | -52.6016 | 70.5597 | -52.4872 | -52.5513 | -51.6129 | 26.9485 | -52.5055 | 70.5643 | 70.4544 | -52.5787 | -52.6199 | -0.10529 | -0.16937 | 0.054931 | 122.8546 | -0.21973 | -0.050354 | -0.18311 | -0.19684 | -0.23804 | 0.059509 | 0.76904 | -0.1236 | 0.11444 | -0.050354 | 122.9416 | 122.7036 | 53.2288 | -123.056 | 122.9462 | 122.8363 | 79.3304 | -123.1247
2756.0156 | 123.111 | -53.1509 | 69.7403 | 0.045624 | 0.0089443 | 0.071668 | 0.068167 | 0.12736 | -0.0030677 | -0.0081455 | 0.34317 | -0.011262 | 0.060419 | 0.05398 | 0.0080536 | -0.011546 | 69.4794 | 69.6396 | 0.75989 | -53.4805 | 69.7174 | -53.334 | -53.421 | -52.3911 | 26.3168 | -53.3249 | 69.7449 | 69.635 | -53.3936 | -53.421 | -0.18311 | -0.27008 | -0.022888 | 122.7905 | -0.32959 | -0.059509 | -0.26093 | -0.24262 | -0.27008 | 0.004578 | 0.75989 | -0.17395 | 0.096131 | -0.10529 | 122.8683 | 122.6303 | 53.9108 | -123.1613 | 122.8958 | 122.7859 | 79.4678 | -123.1613
2757.0312 | 123.024 | -52.1622 | 70.7474 | -0.015411 | 0.019198 | 0.069319 | 0.074362 | 0.13249 | 0.0056909 | -0.0036595 | -0.045929 | -0.0069898 | 0.065332 | 0.054835 | 0.010403 | -0.013255 | 70.6467 | 70.7153 | 0.77362 | -52.3361 | 70.8801 | -52.2354 | -52.327 | -51.4206 | 27.1179 | -52.3682 | 70.8252 | 70.7153 | -52.3819 | -52.3956 | -0.073243 | -0.16479 | 0.13275 | 122.8775 | -0.17395 | -0.009156 | -0.10071 | -0.21973 | -0.23346 | 0.07782 | 0.74158 | -0.20599 | 0.027466 | -0.032043 | 123.0423 | 122.8088 | 52.9358 | -123.0743 | 122.9874 | 122.8775 | 79.2801 | -123.143
2758.0156 | 123.056 | -53.3844 | 69.5572 | 0.10666 | 0.01514 | 0.06825 | 0.072653 | 0.13057 | 0.0024865 | -0.0060093 | 0.16006 | -0.010835 | 0.065973 | 0.057185 | 0.0067718 | -0.012401 | 69.4107 | 69.5251 | 0.63171 | -53.5355 | 69.7037 | -53.4027 | -53.5172 | -52.5513 | 26.1841 | -53.3981 | 69.635 | 69.5206 | -53.5858 | -53.6179 | -0.018311 | -0.13275 | 0.14648 | 122.9095 | -0.15106 | -0.01831 | -0.14648 | -0.20142 | -0.23346 | 0.07782 | 0.83313 | -0.013733 | 0.21973 | -0.036621 | 123.0881 | 122.7951 | 54.0161 | -123.0743 | 123.0194 | 122.905 | 79.5685 | -123.175
2759.0312 | 123.0469 | -53.0273 | 69.9142 | -0.22903 | 0.010653 | 0.0706 | 0.069876 | 0.1295 | -0.0030677 | -0.0066501 | -0.12985 | -0.0082716 | 0.061701 | 0.05633 | 0.0063446 | -0.01411 | 69.8868 | 69.8914 | 0.5722 | -53.2974 | 69.9646 | -53.1509 | -53.2745 | -52.2949 | 26.4038 | -53.3386 | 69.8868 | 69.8135 | -53.3066 | -53.3157 | -0.1236 | -0.24719 | 0.050354 | 122.9187 | -0.27008 | -0.022888 | -0.027466 | -0.27924 | -0.28839 | -0.027466 | 0.73242 | -0.31128 | -0.022888 | -0.10071 | 122.9919 | 122.9141 | 53.5995 | -123.1888 | 122.9141 | 122.8409 | 79.4312 | -123.23
2760.0156 | 123.1018 | -53.4714 | 69.397 | 0.19058 | 0.0087307 | 0.072523 | 0.067954 | 0.12672 | -0.0030677 | -0.0066501 | 0.20584 | -0.010194 | 0.061914 | 0.054835 | 0.007199 | -0.010692 | 69.1315 | 69.3192 | 0.61798 | -53.7415 | 69.3878 | -53.6316 | -53.7186 | -52.6978 | 26.3214 | -53.5538 | 69.4336 | 69.3604 | -53.7003 | -53.7048 | -0.16022 | -0.24719 | -0.009156 | 122.7905 | -0.27008 | -0.022888 | -0.2655 | -0.22888 | -0.23346 | 0.036621 | 0.77362 | -0.082397 | 0.15106 | -0.036621 | 122.8592 | 122.6028 | 54.0894 | -123.1155 | 122.905 | 122.8317 | 79.7928 | -123.1018
2761.0156 | 123.1293 | -53.7964 | 69.0537 | 0.21347 | 0.01578 | 0.06825 | 0.071799 | 0.128 | 0.0024865 | -0.0043003 | 0.19821 | -0.0076306 | 0.065119 | 0.05633 | 0.0086944 | -0.014323 | 69.0674 | 69.2047 | 0.56305 | -53.9017 | 69.2459 | -53.8147 | -53.9062 | -52.9861 | 26.0971 | -53.952 | 69.1177 | 69.017 | -54.039 | -54.0573 | -0.01831 | -0.10986 | 0.19226 | 123.0011 | -0.10528 | 0.004578 | 0.013733 | -0.24261 | -0.26093 | 0.064087 | 0.81024 | -0.15564 | 0.10529 | -0.036621 | 123.0423 | 122.8638 | 54.3594 | -122.9599 | 122.9141 | 122.8134 | 79.8935 | -123.111
2762.0156 | 123.175 | -54.4281 | 68.4448 | -0.12985 | 0.0080899 | 0.073164 | 0.070944 | 0.12928 | -0.0037085 | -0.0066501 | -0.061188 | -0.011903 | 0.060846 | 0.056758 | 0.0050628 | -0.01176 | 68.7286 | 68.9255 | 0.5722 | -54.1855 | 68.9026 | -54.1534 | -54.2862 | -53.6087 | 25.9781 | -54.6936 | 68.5135 | 68.4265 | -54.6753 | -54.7256 | 0.27466 | 0.14191 | 0.45776 | 123.3536 | 0.24262 | 0.10071 | 0.28381 | -0.24719 | -0.29755 | 0.068665 | 0.8194 | -0.2655 | 0.032043 | -0.01831 | 123.3307 | 123.1567 | 55.0003 | -122.731 | 122.9416 | 122.8546 | 80.4062 | -123.1705
2763.0156 | 123.056 | -53.8879 | 69.0079 | 0.35843 | 0.01578 | 0.070814 | 0.071799 | 0.12758 | 0.0031273 | -0.0072911 | 0.13718 | -0.0095532 | 0.065759 | 0.055689 | 0.009549 | -0.01176 | 68.866 | 68.9346 | 0.35706 | -54.0894 | 69.1544 | -53.9474 | -54.0665 | -53.1235 | 26.0696 | -54.1077 | 69.104 | 68.985 | -54.1122 | -54.1809 | -0.05951 | -0.17853 | 0.14648 | 122.8226 | -0.20142 | -0.022888 | -0.14191 | -0.2243 | -0.29297 | 0.09613 | 0.76447 | -0.21973 | 0.073242 | -0.022889 | 123.0423 | 122.7539 | 54.245 | -123.0743 | 122.9919 | 122.8729 | 79.9576 | -123.1888
2764.0312 | 123.1293 | -53.5995 | 69.2505 | -0.19089 | 0.0093717 | 0.071455 | 0.069449 | 0.12886 | -0.0041357 | -0.0051547 | 0.2211 | -0.011476 | 0.062128 | 0.057398 | 0.0069854 | -0.01176 | 69.191 | 69.397 | 0.6134 | -53.7003 | 69.3924 | -53.6179 | -53.7323 | -52.7481 | 26.651 | -53.7048 | 69.3466 | 69.2551 | -53.8147 | -53.8605 | -0.018311 | -0.13275 | 0.14191 | 122.9965 | -0.10071 | 0.032044 | -0.059509 | -0.21515 | -0.26093 | 0.096131 | 0.85144 | -0.10529 | 0.15564 | 0.004578 | 122.9919 | 122.7905 | 54.213 | -122.9828 | 122.9462 | 122.8546 | 80.2505 | -123.111
2765.0156 | 123.1018 | -52.7664 | 70.0928 | 0.13718 | 0.0091581 | 0.071241 | 0.070731 | 0.12651 | -0.0037085 | -0.0064365 | 0.19821 | -0.0097668 | 0.063623 | 0.055689 | 0.0080536 | -0.012828 | 69.8502 | 70.0195 | 0.66834 | -53.0685 | 70.079 | -52.9312 | -53.0136 | -51.9699 | 27.2049 | -52.6932 | 70.1797 | 70.0607 | -52.9724 | -53.009 | -0.16479 | -0.24719 | -0.013732 | 122.7859 | -0.30212 | -0.054931 | -0.24261 | -0.20599 | -0.24262 | 0.086976 | 0.79651 | 0.073242 | 0.31586 | -0.032043 | 122.8455 | 122.6166 | 53.4348 | -123.1064 | 122.9462 | 122.8271 | 79.9713 | -123.1018
2766.0156 | 123.0423 | -53.8239 | 69.0445 | 0.14481 | 0.014499 | 0.069746 | 0.073935 | 0.128 | 0.0029137 | -0.0045139 | 0.16006 | -0.010408 | 0.065332 | 0.055262 | 0.008908 | -0.012401 | 68.7607 | 68.8385 | 0.48065 | -54.1077 | 69.0948 | -54.007 | -54.0665 | -52.9999 | 26.3718 | -53.9749 | 69.1956 | 69.0674 | -54.0207 | -54.0344 | -0.1831 | -0.24261 | 0.050354 | 122.6624 | -0.28381 | -0.041199 | -0.28381 | -0.19684 | -0.21057 | 0.15106 | 0.82397 | -0.15106 | 0.059509 | 0.022888 | 122.9187 | 122.5845 | 54.3045 | -123.111 | 123.0194 | 122.8912 | 80.1956 | -123.0789
2767.0156 | 123.111 | -53.595 | 69.2459 | -0.053558 | 0.0085171 | -0.035998 | 0.070944 | 0.13078 | -0.0052039 | -0.0072911 | 0.022736 | -0.010194 | 0.060846 | 0.055689 | 0.006131 | -0.010692 | 69.1544 | 69.3192 | 0.65002 | -53.746 | 69.3878 | -53.6636 | -53.7369 | -52.7618 | 26.6098 | -53.6407 | 69.3695 | 69.2917 | -53.7781 | -53.8467 | -0.068664 | -0.14191 | 0.14191 | 122.9141 | -0.15106 | -0.009156 | -0.091553 | -0.1831 | -0.25177 | 0.1236 | 0.83313 | -0.045776 | 0.20599 | 0.045776 | 122.9828 | 122.7493 | 54.245 | -122.9828 | 122.9645 | 122.8867 | 80.2048 | -123.0927
2768.0156 | 123.1384 | -53.6682 | 69.1681 | 0.22873 | 0.014712 | 0.068891 | 0.074362 | 0.13057 | 0.0022729 | -0.0045139 | 0.20584 | -0.0097668 | 0.064478 | 0.054408 | 0.0080536 | -0.015178 | 69.1086 | 69.2551 | 0.55847 | -53.8284 | 69.3054 | -53.7323 | -53.8101 | -52.8122 | 26.2527 | -53.8513 | 69.223 | 69.1452 | -53.9017 | -53.9474 | -0.064087 | -0.14191 | 0.13733 | 122.9233 | -0.16022 | -0.01831 | -0.059509 | -0.23346 | -0.27924 | 0.054931 | 0.85602 | -0.1831 | 0.096131 | -0.022888 | 122.9736 | 122.7768 | 54.2267 | -122.9782 | 122.8912 | 122.8134 | 79.921 | -123.1155
2769.0156 | 123.2117 | -53.5538 | 69.223 | 0.068512 | 0.015353 | 0.072736 | 0.070944 | 0.13035 | 0.0020593 | -0.0045139 | 0.2211 | -0.011262 | 0.064478 | 0.05398 | 0.0080536 | -0.012614 | 69.3558 | 69.516 | 0.59967 | -53.5675 | 69.5618 | -53.4897 | -53.5538 | -52.5467 | 26.651 | -53.7048 | 69.4565 | 69.3558 | -53.7048 | -53.7598 | 0.064087 | 0 | 0.33875 | 123.0698 | -0.013733 | -0.013733 | 0.13275 | -0.15106 | -0.20599 | 0.23346 | 1.0071 | -0.15106 | 0.054932 | 0.13275 | 123.1155 | 122.9095 | 54.1534 | -122.7768 | 123.0103 | 122.9095 | 80.2048 | -122.9828
2770.0156 | 123.0286 | -53.4943 | 69.4382 | 0.022736 | 0.019626 | 0.068037 | 0.072012 | 0.13142 | 0.0050499 | -0.0045139 | 0.076141 | -0.0065626 | 0.067041 | 0.058253 | 0.0074126 | -0.011546 | 69.4199 | 69.4656 | 0.4303 | -53.5538 | 69.6945 | -53.4256 | -53.508 | -52.7298 | 26.5686 | -53.8284 | 69.5435 | 69.4473 | -53.6819 | -53.7369 | 0.068665 | -0.013733 | 0.25635 | 122.9599 | -0.059509 | -0.045776 | -0.01831 | -0.18768 | -0.24261 | 0.10529 | 0.76447 | -0.33417 | -0.091553 | 0.009156 | 123.1888 | 122.9141 | 53.9246 | -122.9462 | 123.0377 | 122.9416 | 80.0629 | -123.175
2771.0156 | 123.0606 | -53.096 | 69.8227 | 0.11429 | 0.016635 | 0.070814 | 0.07244 | 0.12907 | 0.0029137 | -0.0051547 | 0.16769 | -0.006349 | 0.063837 | 0.055476 | 0.0093354 | -0.01176 | 69.6304 | 69.7174 | 0.50354 | -53.3249 | 69.9234 | -53.215 | -53.2654 | -52.2858 | 26.7517 | -53.2608 | 69.9188 | 69.8044 | -53.2974 | -53.3157 | -0.11902 | -0.16937 | 0.10071 | 122.8134 | -0.22888 | -0.059509 | -0.19226 | -0.20142 | -0.21973 | 0.09613 | 0.81024 | -0.1648 | 0.054932 | -0.018311 | 123.0194 | 122.7264 | 53.5995 | -123.0881 | 123.0148 | 122.9004 | 79.8477 | -123.1384
2772.0156 | 123.0927 | -53.4485 | 69.4565 | 0.022736 | 0.0091581 | 0.074445 | 0.068167 | 0.12886 | -0.0086219 | -0.0072911 | 0.19058 | -0.010835 | 0.061487 | 0.054621 | 0.0057038 | -0.010692 | 68.9621 | 68.8705 | 0.37537 | -54.0482 | 69.1452 | -53.9246 | -54.0298 | -52.8168 | 26.7242 | -53.6041 | 69.3512 | 69.3146 | -53.7369 | -53.7415 | -0.47607 | -0.58136 | -0.31128 | 122.319 | -0.59967 | -0.018311 | -0.49438 | -0.28839 | -0.29297 | -0.10529 | 0.63171 | -0.15564 | 0.13733 | -0.14191 | 122.5937 | 122.4106 | 53.8239 | -123.4863 | 122.7997 | 122.7631 | 80.1727 | -123.1979
2773.0156 | 123.1064 | -53.302 | 69.5572 | 0.17532 | 0.011508 | 0.072736 | 0.07009 | 0.12907 | -0.0011451 | -0.0064365 | 0.25925 | -0.0099806 | 0.060205 | 0.056117 | 0.0076264 | -0.012614 | 69.4427 | 69.603 | 0.62256 | -53.4714 | 69.6304 | -53.3936 | -53.4805 | -52.4139 | 26.8936 | -53.3295 | 69.6533 | 69.5526 | -53.508 | -53.5583 | -0.091553 | -0.17853 | 0.073242 | 122.905 | -0.16937 | 0.009155 | -0.11444 | -0.20599 | -0.25635 | 0.09613 | 0.88806 | -0.027466 | 0.22888 | -0.004578 | 122.9324 | 122.7448 | 53.9246 | -123.0377 | 122.9553 | 122.8546 | 80.1956 | -123.1155
2774.0156 | 123.1293 | -53.9429 | 68.898 | 0.0914 | 0.0095853 | 0.071455 | 0.07009 | 0.12886 | -0.0056311 | -0.0089999 | 0.13718 | -0.0086988 | 0.061487 | 0.053553 | 0.0039948 | -0.012614 | 68.9575 | 69.1269 | 4.6234 | -53.9749 | 69.2047 | -53.8513 | -53.9658 | -53.2196 | 26.3351 | -54.2358 | 68.9713 | 68.8843 | -54.213 | -54.2633 | 0.091553 | -0.022888 | 0.3067 | 123.0698 | -0.032044 | -0.009156 | 0.05951 | -0.27008 | -0.32044 | 0.073242 | 0.72327 | -0.29297 | 0.027466 | -0.013733 | 123.1476 | 122.9004 | 58.5663 | -122.8638 | 122.9141 | 122.8271 | 80.278 | -123.1613
2775.0156 | 123.0652 | -53.7735 | 69.0811 | 0.18295 | 0.017489 | 0.067396 | 0.073294 | 0.12928 | 0.0033411 | -0.0064365 | 0.18295 | -0.0097668 | 0.062982 | 0.057612 | 0.0084808 | -0.011119 | 68.9987 | 69.0445 | 2.6779 | -54.0024 | 69.2322 | -53.8559 | -53.9886 | -53.0273 | 26.6602 | -53.8651 | 69.1635 | 69.0674 | -54.0344 | -54.0665 | -0.082397 | -0.21515 | 0.15106 | 122.818 | -0.22888 | -0.013733 | -0.082398 | -0.26093 | -0.29297 | 0.082397 | 0.74616 | -0.091552 | 0.20142 | -0.013733 | 123.0057 | 122.7722 | 56.4514 | -123.0698 | 122.937 | 122.8409 | 80.4337 | -123.1476
2776.0156 | 123.1476 | -52.7893 | 70.079 | 0.19058 | 0.013858 | 0.068891 | 0.073508 | 0.12779 | -7.6852e-05 | -0.0055821 | 0.083771 | -0.0089124 | 0.065332 | 0.054835 | 0.01019 | -0.013042 | 69.9371 | 70.0607 | 1.7715 | -52.9999 | 70.1477 | -52.9129 | -53.009 | -51.9241 | 27.5391 | -52.8214 | 70.1523 | 70.079 | -52.9816 | -53.0411 | -0.1236 | -0.21973 | 0.068664 | 122.85 | -0.21057 | 0.009155 | -0.14191 | -0.19226 | -0.25177 | 0.073242 | 0.86517 | -0.032043 | 0.21973 | 0 | 122.937 | 122.7264 | 54.5609 | -123.0881 | 122.9416 | 122.8683 | 80.3284 | -123.1201
2777.0156 | 123.0194 | -52.3499 | 70.6055 | 0.12192 | 0.017062 | 0.068464 | 0.072653 | 0.13398 | 0.0014185 | -0.0055821 | 0.11429 | -0.008058 | 0.066187 | 0.060603 | 0.0082672 | -0.014323 | 70.1431 | 70.2667 | 6.4957 | -52.652 | 70.5505 | -52.5238 | -52.6108 | -51.3977 | 28.0334 | -52.4643 | 70.6604 | 70.6009 | -52.5696 | -52.597 | -0.17395 | -0.26093 | -0.054932 | 122.6166 | -0.30212 | -0.041199 | -0.46234 | -0.21973 | -0.24719 | 0.054931 | 0.95215 | -0.11444 | 0.13275 | -0.004578 | 122.9004 | 122.493 | 58.8455 | -123.2162 | 123.0103 | 122.9507 | 80.3833 | -123.2025
2778.0156 | 123.175 | -53.627 | 69.342 | -0.068817 | 0.018771 | 0.071241 | 0.072653 | 0.12779 | 0.0027001 | -0.0055821 | 0.10666 | -0.0095532 | 0.062769 | 0.056971 | 0.0082672 | -0.01176 | 69.0445 | 69.1223 | 10.3821 | -53.8834 | 69.3924 | -53.7415 | -53.8239 | -52.8717 | 26.8799 | -53.8513 | 69.3375 | 69.2368 | -53.8925 | -53.9383 | -0.11444 | -0.19684 | 0.050354 | 122.7493 | -0.25635 | -0.059509 | -0.29755 | -0.2655 | -0.31128 | -0.004578 | 0.75531 | -0.2243 | 0.086975 | -0.10529 | 123.0194 | 122.6715 | 64.0091 | -123.1659 | 122.9645 | 122.8638 | 80.5069 | -123.2803
2779.0156 | 123.1567 | -52.4506 | 70.4178 | 0.12955 | 0.01578 | 0.070814 | 0.070944 | 0.12736 | -0.0019995 | -0.0043003 | 0.28214 | -0.0093396 | 0.061701 | 0.058039 | 0.0074126 | -0.0098374 | 70.3537 | 70.4819 | 9.9243 | -52.5879 | 70.5597 | -52.5009 | -52.6291 | -51.5808 | 27.3056 | -52.4918 | 70.4224 | 70.3629 | -52.7252 | -52.7115 | -0.050354 | -0.17853 | 0.14191 | 122.9324 | -0.13733 | 0.041198 | -0.064087 | -0.27466 | -0.26093 | 0.004577 | 0.86975 | -0.041198 | 0.21973 | -0.054932 | 123.0103 | 122.8043 | 62.3749 | -123.0469 | 122.8729 | 122.8134 | 79.7562 | -123.1293
2780.0156 | 123.1293 | -53.0228 | 69.8044 | 0.12192 | 0.016208 | 0.069532 | 0.070303 | 0.13099 | -0.0011451 | -0.0055821 | 0.21347 | -0.011049 | 0.064691 | 0.056971 | 0.0082672 | -0.013469 | 69.603 | 69.6671 | 3.2913 | -53.3203 | 69.7723 | -53.2471 | -53.3386 | -52.0432 | 27.0905 | -52.9953 | 69.9509 | 69.8822 | -53.2333 | -53.2471 | -0.2243 | -0.31586 | -0.032043 | 122.6898 | -0.29755 | 0.018311 | -0.20142 | -0.21057 | -0.2243 | 0.14648 | 0.97961 | 0.027466 | 0.25177 | 0.07782 | 122.7951 | 122.6257 | 56.3141 | -123.143 | 122.9736 | 122.905 | 80.1132 | -123.0515
2781.0156 | 123.1293 | -53.2288 | 69.6167 | 0.16769 | 0.015994 | 0.069105 | 0.072012 | 0.128 | -0.0041357 | -0.0049411 | 0.22873 | -0.0076306 | 0.060633 | 0.05633 | 0.0069854 | -0.012401 | 69.3512 | 69.6167 | 3.566 | -53.476 | 69.6121 | -53.3844 | -53.476 | -52.3956 | 26.8112 | -53.2974 | 69.6716 | 69.5984 | -53.4439 | -53.476 | -0.15564 | -0.24719 | -0.004577 | 122.8455 | -0.24719 | 0 | -0.2655 | -0.21515 | -0.24719 | 0.054932 | 0.83313 | -0.068664 | 0.17853 | -0.01831 | 122.8409 | 122.58 | 56.7947 | -123.0927 | 122.9004 | 122.8271 | 80.04 | -123.0927
2782.0156 | 123.0377 | -53.3203 | 69.5755 | 0.12955 | 0.01578 | 0.070387 | 0.07244 | 0.13014 | 0.0022729 | -0.0040867 | 0.19058 | -0.0069898 | 0.064478 | 0.057398 | 0.0082672 | -0.01176 | 69.2871 | 69.3832 | 1.9363 | -53.5721 | 69.635 | -53.4576 | -53.5629 | -52.4872 | 26.738 | -53.5217 | 69.6716 | 69.603 | -53.5217 | -53.5538 | -0.13733 | -0.24262 | 0.05951 | 122.7036 | -0.25177 | -0.009156 | -0.28839 | -0.20142 | -0.23346 | 0.096131 | 0.83313 | -0.20142 | 0.032043 | 0.027466 | 122.9553 | 122.6074 | 55.2567 | -123.1384 | 122.9919 | 122.9233 | 80.0583 | -123.1293
2783.0156 | 123.0515 | -52.8671 | 70.047 | 0.54916 | 0.020694 | 0.069959 | 0.070517 | 0.12993 | 0.0024865 | -0.0036595 | 0.11429 | -0.0082716 | 0.065759 | 0.057185 | 0.010617 | -0.011333 | 70.1019 | 70.1797 | 3.0396 | -53.064 | 70.2988 | -52.8488 | -52.9678 | -52.0981 | 26.944 | -53.0502 | 70.1569 | 70.0607 | -53.0685 | -53.1281 | 0.01831 | -0.10071 | 0.25177 | 123.0469 | -0.19684 | -0.096131 | 0.054932 | -0.20142 | -0.26093 | 0.10986 | 0.76904 | -0.18311 | 0.07782 | 0.013733 | 123.1659 | 122.9691 | 55.9067 | -123.0148 | 123.024 | 122.9279 | 79.8111 | -123.175
2784.0156 | 123.1247 | -53.0319 | 69.8273 | -0.12985 | 0.0091581 | 0.072736 | 0.067526 | 0.128 | -0.0066993 | -0.0070773 | -0.061188 | -0.010835 | 0.061273 | 0.056544 | 0.00549 | -0.0094102 | 69.8959 | 70.1477 | 5.5206 | -52.9221 | 70.134 | -52.8717 | -52.9541 | -52.0615 | 27.1042 | -53.0411 | 70.047 | 69.9738 | -53.1555 | -53.2242 | 0.16022 | 0.077819 | 0.3067 | 123.1796 | 0.10986 | 0.032044 | 0.068664 | -0.1236 | -0.19226 | 0.21973 | 0.97046 | -0.009156 | 0.1831 | 0.14648 | 123.1659 | 122.9279 | 58.5526 | -122.7814 | 123.0789 | 123.0057 | 80.1361 | -123.0515
2785.0156 | 123.143 | -53.6682 | 69.1681 | 0.17532 | 0.016635 | 0.069959 | 0.071799 | 0.13078 | 0.0016321 | -0.0055821 | 0.16006 | -0.011476 | 0.062555 | 0.056117 | 0.01019 | -0.011974 | 69.0491 | 69.1772 | 8.2855 | -53.9246 | 69.3054 | -53.7689 | -53.8788 | -52.858 | 26.738 | -53.9474 | 69.2596 | 69.1727 | -53.8971 | -53.9474 | -0.10071 | -0.21057 | 0.13733 | 122.8455 | -0.25635 | -0.045777 | -0.11902 | -0.22888 | -0.27924 | 0.091553 | 0.81024 | -0.27924 | 0 | 0.004577 | 122.9736 | 122.7173 | 61.9537 | -123.0469 | 122.9279 | 122.8409 | 80.4062 | -123.1155
2786.0156 | 123.0331 | -53.3295 | 69.6075 | 0.16769 | 0.016208 | 0.068037 | 0.073935 | 0.13099 | 0.0033411 | -0.0040867 | 0.076141 | -0.0067762 | 0.065119 | 0.056117 | 0.0080536 | -0.013896 | 69.3649 | 69.4016 | 8.7067 | -53.6133 | 69.6533 | -53.4622 | -53.5675 | -52.6154 | 26.6418 | -53.6499 | 69.5892 | 69.5343 | -53.5583 | -53.627 | -0.13275 | -0.23804 | 0.045776 | 122.731 | -0.28381 | -0.045776 | -0.24262 | -0.22888 | -0.29755 | -0.018311 | 0.71411 | -0.32043 | -0.022888 | -0.073242 | 122.9828 | 122.6944 | 62.0361 | -123.175 | 122.9187 | 122.8638 | 79.9713 | -123.2346
2787.0156 | 123.0377 | -54.4235 | 68.4952 | 2.5099 | 0.018985 | 0.072523 | 0.072012 | 0.12758 | -0.00071785 | -0.0062229 | 0.12955 | -0.0072034 | 0.065119 | 0.057612 | 0.0082672 | -0.012187 | 68.399 | 68.3258 | 6.2851 | -54.6112 | 68.6005 | -54.5334 | -54.6112 | -53.6865 | 26.2207 | -54.57 | 68.5959 | 68.5318 | -54.6066 | -54.6616 | -0.10986 | -0.18768 | 0.10529 | 122.7493 | -0.18768 | 0 | -0.09613 | -0.1831 | -0.23804 | 0.10071 | 0.737 | -0.14648 | 0.091553 | 0.036621 | 123.024 | 122.8226 | 60.7086 | -123.1064 | 123.0194 | 122.9553 | 80.6442 | -123.1567
2788.0156 | 123.0927 | -53.8834 | 68.9896 | 0.13718 | 0.014712 | 0.070173 | 0.071372 | 0.12672 | 0.00013675 | -0.0049411 | 0.2211 | -0.009126 | 0.064478 | 0.055689 | 0.008908 | -0.0089828 | 68.9484 | 69.072 | 7.6813 | -53.9841 | 69.2596 | -53.8284 | -53.9612 | -53.0823 | 26.857 | -54.0024 | 69.1406 | 69.0353 | -54.0848 | -54.1351 | 0.054932 | -0.07782 | 0.27008 | 122.9553 | -0.10071 | -0.022888 | -0.041199 | -0.20142 | -0.25177 | 0.15106 | 0.80109 | -0.11902 | 0.13275 | 0.045776 | 123.143 | 122.8317 | 61.5646 | -122.9507 | 123.024 | 122.9187 | 80.7404 | -123.1247
2789.0156 | 123.1476 | -53.7231 | 69.1452 | -0.11459 | 0.0089443 | 0.070814 | 0.07009 | 0.13078 | -0.0073401 | -0.0083591 | -3.6394 | -0.010835 | 0.065546 | 0.056544 | 0.0063446 | -0.012401 | 69.0903 | 69.3146 | 5.9647 | -53.7964 | 69.2734 | -53.7643 | -53.833 | -52.8946 | 26.9485 | -53.8651 | 69.1589 | 69.0994 | -53.9566 | -54.0298 | -0.041198 | -0.10986 | 0.12817 | 123.0377 | -0.073242 | 0.036621 | -0.054932 | -0.23346 | -0.3067 | 0.013733 | 0.82855 | -0.14191 | 0.16479 | -0.045777 | 122.9965 | 122.8134 | 59.6878 | -122.9782 | 122.8821 | 122.8226 | 80.6717 | -123.175
2790.0156 | 123.0606 | -54.1122 | 68.8568 | -0.18326 | 0.014285 | 0.069959 | 0.074362 | 0.13057 | 0.0029137 | -0.0055821 | -0.11459 | -0.0093396 | 0.0664 | 0.058039 | 0.0091216 | -0.015605 | 68.5593 | 68.7012 | 10.6339 | -54.3045 | 68.811 | -54.2542 | -54.332 | -53.3478 | 27.0081 | -54.2084 | 68.8293 | 68.7607 | -54.3686 | -54.3686 | -0.14191 | -0.21973 | -0.045777 | 122.8134 | -0.19226 | 0.027466 | -0.29755 | -0.25635 | -0.25635 | -0.027466 | 0.76447 | -0.09613 | 0.16022 | -0.096131 | 122.9233 | 122.6715 | 64.7461 | -123.1888 | 122.9416 | 122.8729 | 81.1203 | -123.2254
2791.0156 | 123.0515 | -53.1509 | 69.7632 | -0.12222 | 0.018771 | 0.069319 | 0.072867 | 0.13185 | 0.0029137 | -0.0062229 | -0.015411 | -0.009126 | 0.063623 | 0.058894 | 0.0097626 | -0.011333 | 69.5206 | 69.6671 | 8.9035 | -53.4027 | 69.7815 | -53.3112 | -53.389 | -52.3132 | 27.7359 | -53.27 | 69.8593 | 69.7815 | -53.3386 | -53.3798 | -0.16022 | -0.23804 | 0.01831 | 122.818 | -0.25177 | -0.013733 | -0.24262 | -0.18768 | -0.22888 | 0.09613 | 0.83771 | -0.11902 | 0.10986 | 0.01831 | 122.9324 | 122.6715 | 62.0544 | -123.1522 | 123.0103 | 122.9324 | 80.8868 | -123.143
2792.0156 | 123.0148 | -53.2242 | 69.6991 | 0.022736 | 0.017489 | 0.069532 | 0.07244 | 0.12736 | 0.00035035 | -0.0047275 | 0.037995 | -0.009126 | 0.063837 | 0.057826 | 0.008908 | -0.013042 | 69.4656 | 69.5892 | 14.7949 | -53.4439 | 69.7815 | -53.3157 | -53.421 | -52.4643 | 27.5757 | -53.5217 | 69.7678 | 69.6762 | -53.4668 | -53.4805 | -0.091553 | -0.19684 | 0.082397 | 122.8134 | -0.21973 | -0.022888 | -0.23346 | -0.24262 | -0.25635 | 0.068664 | 0.75989 | -0.29755 | -0.041199 | -0.022889 | 123.0057 | 122.6898 | 68.0191 | -123.1201 | 122.9919 | 122.9004 | 80.7999 | -123.1796
2793.0156 | 123.024 | -53.508 | 69.4565 | 0.16006 | 0.018344 | 0.069319 | 0.071799 | 0.12928 | 0.00056395 | -0.0057957 | 0.12955 | -0.013185 | 0.063837 | 0.056758 | 0.00784 | -0.010905 | 69.0948 | 69.2322 | 21.3547 | -53.7415 | 69.4611 | -53.6682 | -53.7277 | -52.803 | 27.4384 | -53.6316 | 69.4244 | 69.3695 | -53.7598 | -53.7552 | -0.16022 | -0.21973 | 0.004578 | 122.7402 | -0.23346 | -0.013733 | -0.36163 | -0.25177 | -0.24719 | -0.032044 | 0.70496 | -0.1236 | 0.1236 | -0.086975 | 122.9691 | 122.6028 | 74.8627 | -123.1842 | 122.9324 | 122.8775 | 80.9463 | -123.2117
2794.0156 | 123.1979 | -54.6158 | 68.2343 | 0.23636 | 0.013431 | 0.069319 | 0.072012 | 0.13163 | -0.00071785 | -0.0062229 | 0.28976 | -0.0086988 | 0.062342 | 0.055903 | 0.0063446 | -0.012401 | 68.2892 | 68.3945 | 26.0696 | -54.7485 | 68.4311 | -54.6524 | -54.7256 | -53.7369 | 26.5274 | -54.6433 | 68.2755 | 68.2114 | -54.8447 | -54.863 | -0.036621 | -0.10986 | 0.19684 | 123.0103 | -0.13275 | -0.022888 | 0.054932 | -0.22888 | -0.24719 | 0.041199 | 0.87891 | -0.027466 | 0.21973 | -0.022888 | 123.0469 | 122.905 | 80.6854 | -122.9599 | 122.8912 | 122.8271 | 81.1432 | -123.0972
2795.0156 | 123.0423 | -54.6707 | 68.2617 | -0.0383 | 0.017276 | 0.068464 | 0.075644 | 0.12758 | 0.0024865 | -0.0060093 | 0.045624 | -0.0072034 | 0.065973 | 0.056117 | 0.0065582 | -0.010265 | 68.1198 | 68.2205 | 18.6859 | -54.8447 | 68.367 | -54.7073 | -54.8309 | -53.7964 | 26.6739 | -54.6753 | 68.3716 | 68.3166 | -54.8264 | -54.8859 | -0.036621 | -0.16022 | 0.10528 | 122.8912 | -0.17395 | -0.013733 | -0.14191 | -0.15564 | -0.21515 | 0.10986 | 0.87433 | -0.004578 | 0.21057 | 0.054931 | 123.0377 | 122.7905 | 73.3566 | -123.0927 | 123.0423 | 122.9874 | 81.3446 | -123.1476
2796.0156 | 123.0331 | -54.7531 | 68.1747 | -0.24429 | 0.017703 | 0.068678 | 0.07244 | 0.13035 | 0.0024865 | -0.0049411 | -0.0077819 | -0.0086988 | 0.065759 | 0.058039 | 0.0086944 | -0.013255 | 68.0328 | 68.1519 | 19.6976 | -54.9408 | 68.2709 | -54.8584 | -54.95 | -53.9612 | 26.4633 | -54.9454 | 68.1793 | 68.1244 | -55.0095 | -55.0095 | -0.10529 | -0.19684 | 0.09613 | 122.905 | -0.18768 | 0.009155 | -0.14191 | -0.25635 | -0.25635 | 0.004577 | 0.79193 | -0.19226 | 0.064086 | -0.050354 | 123.024 | 122.7859 | 74.4507 | -123.1247 | 122.9324 | 122.8775 | 81.2164 | -123.1842
2797.0156 | 123.0103 | -55.5084 | 67.4469 | 0.0074768 | 0.01813 | 0.067182 | 0.072226 | 0.1295 | 0.0031273 | -0.0049411 | 0.15244 | -0.0052808 | 0.064478 | 0.057185 | 0.0099762 | -0.010905 | 67.1219 | 67.2638 | 25.946 | -55.719 | 67.4789 | -55.6183 | -55.6732 | -54.657 | 26.1566 | -55.7053 | 67.5018 | 67.4469 | -55.7236 | -55.7373 | -0.10986 | -0.16479 | 0.032044 | 122.7722 | -0.21057 | -0.045776 | -0.32501 | -0.21515 | -0.22888 | 0.054932 | 0.85144 | -0.19684 | 0.032044 | 0 | 122.9874 | 122.6303 | 81.4545 | -123.1201 | 123.0103 | 122.9553 | 81.665 | -123.1842
2798.0156 | 123.0103 | -55.3391 | 67.6254 | 0.045624 | 0.014712 | 0.068037 | 0.071585 | 0.12928 | 0.0022729 | -0.0055821 | 0.022736 | -0.0082716 | 0.067041 | 0.05633 | 0.007199 | -0.010905 | 67.2226 | 67.3508 | 31.6818 | -55.632 | 67.5568 | -55.5222 | -55.6366 | -54.538 | 26.3031 | -55.4489 | 67.6254 | 67.5659 | -55.5954 | -55.5954 | -0.18311 | -0.29755 | -0.068664 | 122.6898 | -0.29297 | 0.004578 | -0.40283 | -0.25635 | -0.25635 | 0 | 0.80109 | -0.10986 | 0.14648 | -0.059509 | 122.8958 | 122.5616 | 87.0209 | -123.262 | 122.9645 | 122.905 | 81.6422 | -123.2208
2799.0156 | 122.9874 | -55.687 | 67.2272 | 0.022736 | 0.019839 | 0.070814 | 0.071158 | 0.12907 | 0.0018457 | -0.0060093 | 0.22873 | -0.0099806 | 0.064905 | 0.057826 | 0.0082672 | -0.012401 | 67.0944 | 67.1951 | 37.4405 | -55.8014 | 67.4149 | -55.6961 | -55.7877 | -54.8813 | 26.207 | -55.8014 | 67.3782 | 67.3096 | -55.8701 | -55.9021 | -0.009155 | -0.10071 | 0.18768 | 122.8821 | -0.11444 | -0.013733 | -0.13275 | -0.1831 | -0.21515 | 0.15106 | 0.80566 | -0.11444 | 0.10071 | 0.082397 | 123.1018 | 122.7814 | 93.1274 | -123.0148 | 123.0652 | 122.9965 | 81.8939 | -123.1293
2800.0156 | 123.0515 | -56.1172 | 66.7969 | -0.061188 | 0.017062 | 0.069746 | 0.070731 | 0.13035 | 0.0014185 | -0.0070773 | -0.015411 | -0.0086988 | 0.064478 | 0.059321 | 0.0067718 | -0.0098374 | 66.7236 | 66.8564 | 37.2894 | -56.1264 | 67.0029 | -56.0761 | -56.1676 | -55.1697 | 25.9735 | -56.1859 | 66.9434 | 66.8747 | -56.2912 | -56.3416 | 0.041199 | -0.050354 | 0.20599 | 122.9736 | -0.009155 | 0.041199 | -0.073242 | -0.17395 | -0.2243 | 0.14648 | 0.94757 | -0.068664 | 0.15564 | 0.07782 | 123.1201 | 122.8409 | 93.4067 | -122.9645 | 123.0606 | 122.9919 | 82.0908 | -123.1384
2801.0156 | 123.0515 | -54.8996 | 68.0054 | -0.45029 | 0.015353 | 0.067823 | 0.070944 | 0.12886 | -0.00071785 | -0.0032321 | -0.023041 | -0.0093396 | 0.064478 | 0.058039 | 0.0069854 | -0.0091966 | 67.8131 | 67.9459 | 30.5557 | -55.1056 | 68.1015 | -55.0278 | -55.0827 | -54.0985 | 26.738 | -55.0552 | 68.0374 | 67.9596 | -55.1605 | -55.1788 | -0.12817 | -0.18311 | 0.09613 | 122.8455 | -0.20599 | -0.022888 | -0.19226 | -0.26093 | -0.27924 | 0.032044 | 0.80109 | -0.15564 | 0.1236 | -0.045776 | 123.0011 | 122.7127 | 85.4553 | -123.0881 | 122.937 | 122.8592 | 81.6376 | -123.1842
2802.0156 | 123.0469 | -55.5862 | 67.3599 | -0.17563 | 0.017062 | 0.069532 | 0.071585 | 0.12843 | -0.0015723 | -0.0085727 | -0.061188 | -0.008058 | 0.061914 | 0.055476 | 0.007199 | -0.010478 | 67.0715 | 67.2409 | 27.1912 | -55.806 | 67.4149 | -55.7007 | -55.8151 | -54.7668 | 26.4771 | -55.6274 | 67.4561 | 67.3965 | -55.751 | -55.8105 | -0.11444 | -0.22888 | 0.054932 | 122.8271 | -0.21973 | 0.009156 | -0.28839 | -0.16479 | -0.2243 | 0.096131 | 0.8194 | -0.041198 | 0.18311 | 0.036621 | 123.0011 | 122.6578 | 82.7774 | -123.175 | 123.0423 | 122.9828 | 82.0633 | -123.1705
2803.0156 | 123.0698 | -56.3187 | 66.6138 | -0.18326 | 0.013217 | 0.070173 | 0.072653 | 0.1295 | -0.0017859 | -0.0036595 | -0.12222 | -0.0093396 | 0.064478 | 0.055476 | 0.0065582 | -0.013255 | 66.3025 | 66.4948 | 26.0559 | -56.5521 | 66.6412 | -56.4926 | -56.5704 | -55.5771 | 25.8957 | -56.456 | 66.6046 | 66.5359 | -56.5659 | -56.5796 | -0.17395 | -0.25177 | 0.027465 | 122.8134 | -0.23346 | 0.018311 | -0.31128 | -0.24719 | -0.26093 | -0.009156 | 0.74158 | -0.13733 | 0.1236 | -0.07782 | 122.9599 | 122.6212 | 82.3746 | -123.1842 | 122.9233 | 122.8546 | 82.2144 | -123.1934
2804.0312 | 123.1155 | -54.8401 | 68.0237 | 0.14481 | 0.013858 | 0.070387 | 0.068808 | 0.13035 | -0.0034949 | -0.0070773 | 0.33554 | -0.0099806 | 0.061914 | 0.058467 | 0.0052764 | -0.0094102 | 67.8452 | 68.0283 | 6.4041 | -55.0919 | 68.0283 | -55.0278 | -55.0873 | -54.0802 | 26.8295 | -54.9957 | 68.0328 | 68.0054 | -55.0552 | -55.0964 | -0.18768 | -0.24719 | 0.004577 | 122.8683 | -0.25177 | -0.004578 | -0.17853 | -0.21515 | -0.25635 | 0.009155 | 0.75989 | -0.15564 | 0.10071 | -0.018311 | 122.8683 | 122.6852 | 61.2442 | -123.111 | 122.8729 | 122.8455 | 81.6696 | -123.1201
2805.0156 | 123.056 | -54.5197 | 68.4265 | -0.21378 | 0.014926 | 0.070387 | 0.074362 | 0.12693 | 0.0020593 | -0.0079319 | -0.015411 | -0.0099806 | 0.065332 | 0.059107 | 0.0074126 | -0.014537 | 68.2434 | 68.399 | 5.9875 | -54.6295 | 68.5455 | -54.5609 | -54.6661 | -53.6224 | 27.1957 | -54.6249 | 68.541 | 68.4631 | -54.6982 | -54.7394 | -0.041199 | -0.14648 | 0.11902 | 122.9187 | -0.10986 | 0.036621 | -0.18311 | -0.17853 | -0.21973 | 0.11444 | 0.89722 | -0.10529 | 0.11444 | 0.036621 | 123.0652 | 122.7631 | 60.5072 | -123.0927 | 123.0606 | 122.9828 | 81.7154 | -123.1659
2806.0156 | 123.0606 | -55.0278 | 67.8955 | -0.17563 | 0.015994 | 0.071241 | 0.071799 | 0.12758 | 0.0016321 | -0.0066501 | -0.19089 | -0.0089124 | 0.063623 | 0.057185 | 0.007199 | -0.011974 | 67.6895 | 67.8452 | 4.7699 | -55.2017 | 68.0099 | -55.1056 | -55.1971 | -54.1763 | 26.7883 | -55.1147 | 67.9871 | 67.9138 | -55.2429 | -55.2841 | -0.07782 | -0.16937 | 0.11444 | 122.8729 | -0.17395 | -0.004577 | -0.20599 | -0.21515 | -0.25635 | 0.091553 | 0.85144 | -0.086975 | 0.16937 | 0.01831 | 123.0377 | 122.7173 | 59.7977 | -123.0927 | 123.0148 | 122.9416 | 81.8161 | -123.1796
2807.0156 | 123.0743 | -54.6844 | 68.248 | -0.18326 | 0.017489 | 0.071455 | 0.069876 | 0.13121 | -7.6852e-05 | -0.0053683 | -0.13748 | -0.0082716 | 0.065332 | 0.056544 | 0.008908 | -0.013683 | 68.0008 | 68.161 | 4.6967 | -54.8584 | 68.3304 | -54.7714 | -54.8904 | -53.8422 | 27.0584 | -54.7943 | 68.3395 | 68.2571 | -54.8996 | -54.9316 | -0.086975 | -0.20599 | 0.082397 | 122.8455 | -0.17395 | 0.032044 | -0.24719 | -0.21515 | -0.24719 | 0.091553 | 0.84229 | -0.10986 | 0.13733 | 0.009155 | 123.0148 | 122.6852 | 59.3811 | -123.1384 | 123.024 | 122.9416 | 81.7429 | -123.1796
2808.0156 | 123.1064 | -55.1651 | 67.7582 | -0.16037 | 0.016208 | 0.069959 | 0.07543 | 0.12758 | 0.00056395 | -0.0051547 | -0.061188 | -0.0086988 | 0.064478 | 0.056758 | 0.0086944 | -0.012828 | 67.5201 | 67.6437 | 4.7241 | -55.4123 | 67.7719 | -55.3207 | -55.4123 | -54.3594 | 26.651 | -55.3345 | 67.8131 | 67.7582 | -55.3665 | -55.3848 | -0.15564 | -0.24719 | 0.013733 | 122.8088 | -0.24719 | 0 | -0.23804 | -0.20142 | -0.21973 | 0.054931 | 0.80566 | -0.16937 | 0.050354 | 0 | 122.937 | 122.6852 | 59.8892 | -123.1705 | 122.9782 | 122.9233 | 81.8161 | -123.143
2809.0156 | 122.9828 | -55.4398 | 67.5476 | -0.015411 | 0.017703 | 0.068678 | 0.073721 | 0.12971 | 0.0016321 | -0.0053683 | 0.0074766 | -0.0076306 | 0.063196 | 0.058894 | 0.0057038 | -0.011974 | 67.3782 | 67.5293 | 6.7291 | -55.5038 | 67.6575 | -55.4214 | -55.5176 | -54.5929 | 26.5411 | -55.6274 | 67.5934 | 67.5247 | -55.632 | -55.6458 | 0.01831 | -0.07782 | 0.10986 | 122.9691 | -0.064087 | 0.013733 | -0.16937 | -0.19226 | -0.20599 | 0.045777 | 0.84686 | -0.18768 | 0.018311 | -0.022888 | 123.0972 | 122.818 | 62.1689 | -123.0652 | 123.0331 | 122.9645 | 81.9809 | -123.1934
2810.0156 | 123.0789 | -55.2979 | 67.6163 | -0.22903 | 0.0095853 | 0.068891 | 0.069663 | 0.12715 | -0.0060585 | -0.0075047 | -0.091705 | -0.0099806 | 0.064905 | 0.057612 | 0.0052764 | -0.010478 | 67.4423 | 67.6712 | 6.9305 | -55.4169 | 67.7078 | -55.3619 | -55.426 | -54.3823 | 26.683 | -55.3665 | 67.7536 | 67.6758 | -55.4581 | -55.513 | -0.064086 | -0.12817 | 0.091553 | 122.9691 | -0.11902 | 0.009155 | -0.17395 | -0.16022 | -0.21515 | 0.13733 | 0.91553 | -0.068664 | 0.14648 | 0.059509 | 123.0057 | 122.7402 | 62.2284 | -123.0423 | 123.0515 | 122.9736 | 81.9809 | -123.1293
2811.0156 | 123.0469 | -55.8243 | 67.1448 | -0.27481 | 0.012149 | 0.069746 | 0.073721 | 0.12736 | -0.0024269 | -0.0089999 | -0.068817 | -0.011262 | 0.064264 | 0.055903 | 0.00549 | -0.012401 | 66.7923 | 67.0486 | 8.7616 | -56.0486 | 67.1722 | -55.925 | -56.0211 | -54.9911 | 26.2665 | -55.9479 | 67.1906 | 67.099 | -56.0577 | -56.0898 | -0.10071 | -0.19684 | 0.027466 | 122.8729 | -0.2243 | -0.027466 | -0.35248 | -0.23346 | -0.2655 | 0.045777 | 0.83313 | -0.1236 | 0.14191 | -0.045776 | 122.9965 | 122.6166 | 64.5859 | -123.1659 | 123.0148 | 122.9233 | 82.0908 | -123.2346
2812.0156 | 123.1201 | -56.2637 | 66.655 | -0.14511 | 0.0078763 | 0.071027 | 0.068808 | 0.13035 | -0.0058447 | -0.0085727 | -0.068817 | -0.0099806 | 0.060846 | 0.055903 | 0.007199 | -0.012401 | 66.5771 | 66.806 | 10.3958 | -56.3187 | 66.8015 | -56.2546 | -56.3553 | -55.3528 | 26.1291 | -56.4423 | 66.6916 | 66.6183 | -56.4651 | -56.5018 | 0.009155 | -0.091553 | 0.14648 | 123.0698 | -0.054932 | 0.036621 | -0.07782 | -0.20142 | -0.23804 | 0.036621 | 0.91095 | -0.17853 | 0.059509 | -0.036621 | 123.0652 | 122.8409 | 66.6595 | -123.0103 | 122.9553 | 122.8821 | 82.3929 | -123.1567
2813.0156 | 123.0835 | -55.5496 | 67.4561 | -0.168 | 0.017062 | 0.069959 | 0.073081 | 0.13057 | 0.0024865 | -0.0062229 | -0.15274 | -0.0086988 | 0.064478 | 0.056117 | 0.0076264 | -0.013042 | 67.1173 | 67.2729 | 12.3871 | -55.7831 | 67.4515 | -55.6915 | -55.7922 | -54.7577 | 26.4862 | -55.9662 | 67.3828 | 67.2638 | -55.8334 | -55.8426 | -0.14191 | -0.24261 | -0.004578 | 122.8226 | -0.23346 | 0.009155 | -0.33875 | -0.28381 | -0.29297 | -0.073243 | 0.79193 | -0.41656 | -0.1236 | -0.19226 | 123.0011 | 122.6669 | 67.9367 | -123.2483 | 122.9324 | 122.8134 | 82.0358 | -123.2986
2814.0312 | 123.1476 | -55.9296 | 66.9296 | 0.17532 | 0.014071 | 0.069532 | 0.069876 | 0.12928 | -0.0011451 | -0.0075047 | 0.19821 | -0.011903 | 0.063837 | 0.059321 | 0.006131 | -0.014537 | 66.7007 | 66.9708 | 13.8336 | -56.131 | 66.98 | -56.0486 | -56.1218 | -55.0507 | 26.3077 | -56.0623 | 66.9708 | 66.8793 | -56.163 | -56.1905 | -0.11902 | -0.19226 | 0.050354 | 122.9004 | -0.20142 | -0.009155 | -0.22888 | -0.23346 | -0.26093 | 0.041199 | 0.87891 | -0.13275 | 0.12817 | -0.050354 | 122.9095 | 122.6303 | 69.7632 | -123.0515 | 122.9004 | 122.8088 | 82.2372 | -123.1201
2815.0156 | 123.0103 | -55.3253 | 67.5888 | -0.21378 | 0.011935 | 0.070814 | 0.073721 | 0.12928 | -0.00093145 | -0.0083591 | 0.46524 | -0.006349 | 0.063623 | 0.058039 | 0.0067718 | -0.011546 | 67.4515 | 67.6849 | 12.5244 | -55.4214 | 67.8406 | -55.2887 | -55.394 | -54.4098 | 26.9989 | -55.4169 | 67.8085 | 67.7261 | -55.4443 | -55.481 | 0.036621 | -0.068665 | 0.25177 | 123.0103 | -0.096131 | -0.027466 | -0.13733 | -0.11902 | -0.15564 | 0.21973 | 0.91553 | -0.091553 | 0.064087 | 0.13733 | 123.1659 | 122.7768 | 67.8497 | -122.9828 | 123.1338 | 123.0515 | 82.3242 | -123.0698
2816.0156 | 123.143 | -55.8517 | 67.0258 | -0.37399 | 0.0085171 | 0.069959 | 0.074362 | 0.13014 | -0.0030677 | -0.0053683 | -0.12985 | -0.010621 | 0.06106 | 0.056544 | 0.0059174 | -0.012401 | 66.8152 | 67.1585 | 13.678 | -56.0394 | 67.0898 | -55.9479 | -56.044 | -54.982 | 25.9827 | -56.0577 | 67.0074 | 66.9708 | -56.0852 | -56.0989 | -0.09613 | -0.19226 | 0.064087 | 123.0103 | -0.18768 | 0.004577 | -0.21057 | -0.23346 | -0.24719 | -0.018311 | 0.86975 | -0.20599 | 0.041199 | -0.054932 | 122.9416 | 122.6669 | 69.5297 | -123.0698 | 122.8592 | 122.8226 | 81.8344 | -123.1247
2817.0156 | 123.0606 | -56.3095 | 66.6229 | -0.22141 | 0.014285 | 0.068891 | 0.074576 | 0.128 | 0.00013675 | -0.0036595 | -0.076446 | -0.011689 | 0.064264 | 0.059535 | 0.0069854 | -0.012401 | 66.1652 | 66.4993 | 12.2223 | -56.5887 | 66.6733 | -56.5063 | -56.5842 | -55.5084 | 25.5478 | -56.5521 | 66.6412 | 66.5497 | -56.5704 | -56.5887 | -0.19684 | -0.27466 | 0.050354 | 122.8088 | -0.27924 | -0.004578 | -0.45776 | -0.26093 | -0.27924 | 0.01831 | 0.80109 | -0.24262 | 0.036621 | -0.073242 | 122.9828 | 122.4747 | 68.5318 | -123.2071 | 122.9507 | 122.8592 | 81.8573 | -123.2117
2818.0156 | 123.0286 | -56.3965 | 66.5588 | -0.23666 | 0.013217 | 0.070173 | 0.07479 | 0.13099 | 0.00077755 | -0.0064365 | -0.19089 | -0.0097668 | 0.064264 | 0.056758 | 0.0069854 | -0.012828 | 66.1606 | 66.3574 | 14.035 | -56.6986 | 66.5039 | -56.5796 | -56.7032 | -55.6824 | 25.6302 | -56.5659 | 66.568 | 66.4993 | -56.6528 | -56.6666 | -0.18311 | -0.3067 | -0.054932 | 122.7539 | -0.30212 | 0.004578 | -0.39825 | -0.25635 | -0.27008 | 0.009155 | 0.71411 | -0.16937 | 0.10071 | -0.059509 | 122.9004 | 122.5571 | 70.4315 | -123.262 | 122.9645 | 122.8958 | 82.0267 | -123.2254
2819.0156 | 123.0606 | -56.0303 | 66.8838 | -0.12222 | 0.01813 | 0.068464 | 0.07479 | 0.12822 | 0.0031273 | -0.0047275 | -0.053558 | -0.0095532 | 0.065759 | 0.058039 | 0.0084808 | -0.01411 | 66.7877 | 66.9525 | 10.0525 | -56.1493 | 67.0532 | -56.0577 | -56.1768 | -55.1102 | 25.9186 | -56.3187 | 66.9159 | 66.8152 | -56.2775 | -56.3004 | -0.027466 | -0.14648 | 0.16937 | 122.9828 | -0.11902 | 0.027466 | -0.09613 | -0.24719 | -0.27008 | 0.032044 | 0.9201 | -0.28839 | -0.018311 | -0.068664 | 123.0835 | 122.818 | 66.0828 | -123.0606 | 122.9462 | 122.8455 | 81.9489 | -123.1842
2820.0156 | 123.1247 | -55.925 | 66.9891 | -0.18326 | 0.010226 | 0.069105 | 0.069663 | 0.12779 | -0.0049903 | -0.0077183 | -0.12222 | -0.011262 | 0.062128 | 0.058253 | 0.0052764 | -0.011546 | 67.0029 | 67.2729 | 7.7499 | -55.838 | 67.2501 | -55.7785 | -55.8975 | -55.1651 | 26.0056 | -56.282 | 66.9846 | 66.8655 | -56.2408 | -56.2546 | 0.14648 | 0.027466 | 0.26093 | 123.1979 | 0.086975 | 0.059509 | 0.013733 | -0.31586 | -0.32959 | -0.004578 | 0.75989 | -0.35706 | -0.027465 | -0.1236 | 123.175 | 122.9279 | 63.6749 | -122.8867 | 122.9095 | 122.7905 | 81.9305 | -123.2437
2821.0156 | 123.0377 | -55.6091 | 67.3233 | -0.22141 | 0.013217 | 0.0706 | 0.071372 | 0.12993 | -0.0017859 | -0.0075047 | -0.13748 | -0.009126 | 0.063837 | 0.059321 | 0.0033538 | -0.01176 | 67.0258 | 67.2318 | 9.3613 | -55.8243 | 67.3874 | -55.7281 | -55.8105 | -54.6158 | 26.0239 | -55.7648 | 67.4515 | 67.3325 | -55.7968 | -55.8426 | -0.11902 | -0.20142 | 0.064087 | 122.8409 | -0.21515 | -0.013733 | -0.29755 | -0.18768 | -0.23346 | 0.12817 | 0.99335 | -0.15564 | 0.077819 | 0.009155 | 122.9965 | 122.6349 | 64.9704 | -123.1338 | 123.0606 | 122.9416 | 81.633 | -123.1659
2822.0156 | 123.0148 | -55.6961 | 67.2409 | -0.076447 | 0.011935 | 0.068891 | 0.068594 | 0.12971 | 0.0014185 | -0.0062229 | -0.14511 | -0.0084852 | 0.065119 | 0.056758 | 0.0076264 | -0.010692 | 67.0761 | 67.2043 | 10.5057 | -55.8975 | 67.3782 | -55.7648 | -55.8929 | -54.8355 | 26.2711 | -55.9021 | 67.2958 | 67.2089 | -55.925 | -55.9387 | -0.068665 | -0.19684 | 0.13733 | 122.9004 | -0.20142 | -0.004578 | -0.16479 | -0.22888 | -0.24262 | 0.054931 | 0.8606 | -0.20599 | 0.036621 | -0.032044 | 123.0743 | 122.7722 | 66.2018 | -123.1338 | 122.9919 | 122.905 | 81.9672 | -123.1796
2823.0156 | 123.0835 | -56.3736 | 66.5085 | -0.11459 | 0.0076627 | 0.070387 | 0.068594 | 0.128 | -0.0060585 | -0.0070773 | -0.10696 | -0.012117 | 0.062555 | 0.056117 | 0.0042084 | -0.012828 | 66.5039 | 66.7557 | 9.6909 | -56.3736 | 66.7282 | -56.3232 | -56.4285 | -55.4489 | 25.8087 | -56.5155 | 66.6229 | 66.5222 | -56.5933 | -56.6391 | 0.050354 | -0.054932 | 0.21973 | 123.1293 | 0 | 0.054932 | -0.004578 | -0.21973 | -0.2655 | 0.11444 | 0.92468 | -0.14191 | 0.1236 | 0.013733 | 123.1018 | 122.8775 | 66.0645 | -122.937 | 122.9965 | 122.8958 | 82.1823 | -123.1476
2824.0156 | 123.0469 | -56.3278 | 66.6183 | -0.061188 | 0.018344 | 0.066755 | 0.073721 | 0.13121 | 0.00099115 | -0.0055821 | -1.1293 | -0.0097668 | 0.064691 | 0.05633 | 0.006131 | -0.013255 | 66.4673 | 66.6824 | 8.4457 | -56.4102 | 66.7923 | -56.337 | -56.4468 | -55.3711 | 25.9186 | -56.4743 | 66.687 | 66.5771 | -56.5292 | -56.575 | -0.009155 | -0.11902 | 0.17395 | 123.0103 | -0.082397 | 0.036621 | -0.15106 | -0.20142 | -0.24719 | 0.068665 | 0.95673 | -0.14648 | 0.10071 | -0.041199 | 123.1201 | 122.7951 | 64.7736 | -123.0652 | 123.0148 | 122.905 | 82.2464 | -123.1934
2825.0156 | 123.1613 | -55.8884 | 66.9846 | -0.168 | 0.010013 | 0.070387 | 0.070944 | 0.12864 | -0.0060585 | -0.0077183 | 0.42709 | -0.010621 | 0.062128 | 0.056758 | 0.004422 | -0.010478 | 66.6962 | 66.7419 | 10.0433 | -56.0898 | 66.925 | -56.0989 | -56.1951 | -55.0323 | 26.3168 | -56.131 | 66.9708 | 66.8884 | -56.1447 | -56.1951 | -0.21057 | -0.3067 | -0.059509 | 122.6303 | -0.20142 | 0.10529 | -0.28839 | -0.25635 | -0.3067 | -0.013733 | 0.85602 | -0.24261 | 0.064087 | -0.09613 | 122.8134 | 122.5845 | 65.9317 | -123.1796 | 122.8592 | 122.7768 | 82.2052 | -123.1796
2826.0156 | 123.0972 | -56.2271 | 66.6504 | -0.12985 | 0.011081 | 0.069746 | 0.070517 | 0.12736 | -0.0028541 | -0.0051547 | -0.099335 | -0.01233 | 0.063196 | 0.056544 | 0.0069854 | -0.011974 | 66.3895 | 66.6595 | 7.5623 | -56.4239 | 66.6779 | -56.3599 | -56.4514 | -55.2658 | 26.0513 | -56.3095 | 66.7282 | 66.6321 | -56.4423 | -56.4514 | -0.13275 | -0.2243 | 0.027465 | 122.8867 | -0.19684 | 0.027466 | -0.26093 | -0.21515 | -0.2243 | 0.077819 | 0.9613 | -0.082397 | 0.14191 | -0.018311 | 122.905 | 122.6166 | 63.7894 | -123.1018 | 122.9553 | 122.8592 | 82.2784 | -123.1018
2827.0156 | 123.1522 | -55.4718 | 67.4377 | 0.55679 | 0.0097989 | 0.069959 | 0.070517 | 0.12822 | -0.0054175 | -0.0085727 | -0.053558 | -0.010194 | 0.061701 | 0.057185 | 0.006131 | -0.012614 | 67.2272 | 67.4149 | 7.1228 | -55.6824 | 67.424 | -55.6229 | -55.719 | -54.57 | 26.4816 | -55.6412 | 67.4149 | 67.3141 | -55.7236 | -55.7602 | -0.15106 | -0.24719 | -0.013733 | 122.8867 | -0.21057 | 0.036621 | -0.21057 | -0.25177 | -0.28839 | -0.022888 | 0.90179 | -0.16937 | 0.11902 | -0.1236 | 122.8958 | 122.699 | 62.5946 | -123.1567 | 122.8867 | 122.7859 | 81.9534 | -123.1979
2828.0156 | 123.143 | -55.8929 | 66.9296 | -0.19852 | 0.0097989 | 0.071027 | 0.071158 | 0.13099 | -0.011185 | -0.0089999 | -0.068817 | -0.010408 | 0.061914 | 0.056117 | 0.0067718 | -0.012401 | 67.1677 | 66.7877 | 7.4249 | -55.9891 | 67.1036 | -55.9479 | -56.0257 | -54.9271 | 26.0925 | -55.9021 | 67.0898 | 66.9662 | -56.0669 | -56.1401 | -0.054932 | -0.13275 | 0.17395 | 122.6807 | -0.096131 | 0.036621 | 0.23804 | -0.17395 | -0.24719 | 0.16022 | 0.96588 | -0.009156 | 0.23804 | 0.036622 | 122.9965 | 123.0606 | 63.3179 | -122.9553 | 122.9828 | 122.8592 | 81.9855 | -123.0698
2829.0312 | 123.024 | -55.8517 | 67.1265 | 0.045624 | 0.017917 | 0.068464 | 0.074362 | 0.13185 | 0.0035547 | -0.0034457 | 0.083771 | -0.009126 | 0.0664 | 0.05868 | 0.0086944 | -0.014964 | 66.9342 | 67.0578 | 7.7316 | -55.9753 | 67.2546 | -55.8563 | -55.9387 | -54.9454 | 25.9552 | -56.1401 | 67.186 | 67.0532 | -56.0532 | -56.0944 | -0.004577 | -0.086975 | 0.12817 | 122.9095 | -0.1236 | -0.036621 | -0.19226 | -0.20142 | -0.24261 | 0.059509 | 0.90637 | -0.28839 | -0.045777 | -0.073242 | 123.1064 | 122.7859 | 63.5834 | -123.0652 | 123.0377 | 122.905 | 81.8069 | -123.2208
2830.0156 | 123.0606 | -56.4285 | 66.4627 | -0.21378 | 0.010653 | 0.070173 | 0.070303 | 0.12971 | -0.0032813 | -0.0081455 | -0.16037 | -0.0086988 | 0.063196 | 0.05633 | 0.007199 | -0.012614 | 66.3208 | 66.5222 | 9.6771 | -56.5887 | 66.568 | -56.5109 | -56.5933 | -55.4443 | 25.6348 | -56.5155 | 66.5863 | 66.5085 | -56.6162 | -56.6803 | -0.082397 | -0.16479 | 0.10528 | 122.9507 | -0.16022 | 0.004578 | -0.14191 | -0.18768 | -0.25177 | 0.1236 | 0.98419 | -0.086975 | 0.16479 | 0.045776 | 122.9965 | 122.7493 | 66.1057 | -123.056 | 123.0148 | 122.937 | 82.0633 | -123.143
2831.0156 | 123.1796 | -55.2017 | 67.6346 | -0.015411 | 0.0076627 | 0.071455 | 0.07244 | 0.13014 | -0.0052039 | -0.0066501 | 0.10666 | -0.013185 | 0.061273 | 0.05633 | 0.0052764 | -0.010905 | 67.4057 | 67.6987 | 9.5306 | -55.4306 | 67.6712 | -55.3802 | -55.4306 | -54.2496 | 26.9394 | -55.188 | 67.7032 | 67.6254 | -55.426 | -55.4672 | -0.17853 | -0.22888 | 0.036621 | 122.9004 | -0.22888 | 0 | -0.22888 | -0.2243 | -0.2655 | 0.068664 | 0.95215 | 0.013733 | 0.27924 | -0.009156 | 122.8729 | 122.6074 | 64.7324 | -123.0652 | 122.905 | 122.8271 | 82.1411 | -123.1018
2832.0156 | 123.1155 | -55.2109 | 67.6575 | 0.037994 | 0.0087307 | 0.070173 | 0.072226 | 0.12822 | -0.0030677 | -0.0094273 | 0.09903 | -0.011476 | 0.061273 | 0.055476 | 0.007199 | -0.011333 | 67.4698 | 67.6987 | 6.3171 | -55.4031 | 67.7811 | -55.2841 | -55.3665 | -54.3594 | 26.5274 | -55.3482 | 67.7261 | 67.6392 | -55.426 | -55.4489 | -0.073243 | -0.15564 | 0.1236 | 122.9095 | -0.19226 | -0.036621 | -0.18768 | -0.21515 | -0.23804 | 0.068664 | 0.85144 | -0.13733 | 0.10071 | -0.018311 | 122.9919 | 122.6807 | 61.528 | -123.024 | 122.937 | 122.85 | 81.7383 | -123.1064
2833.0156 | 123.1384 | -55.7602 | 67.1173 | -0.03067 | 0.0072355 | 0.071027 | 0.069235 | 0.12886 | -0.0034949 | -0.0081455 | 0.045624 | -0.01233 | 0.062128 | 0.056117 | 0.0048492 | -0.01176 | 66.8518 | 67.0807 | 7.1045 | -55.9982 | 67.1036 | -55.9341 | -55.9937 | -54.8035 | 26.1063 | -56.0303 | 67.186 | 67.0761 | -55.9753 | -56.0303 | -0.17395 | -0.23346 | -0.013733 | 122.8409 | -0.23804 | -0.004578 | -0.2655 | -0.21515 | -0.27008 | 0.068664 | 0.95673 | -0.27008 | 0 | -0.041199 | 122.8638 | 122.612 | 62.8647 | -123.111 | 122.9462 | 122.8363 | 81.8665 | -123.1476
2834.0312 | 123.024 | -55.6274 | 67.2775 | -0.053558 | 0.014926 | 0.06526 | 0.075217 | 0.12758 | 0.0067589 | -0.0057957 | -0.061188 | -0.0078442 | 0.06875 | 0.059535 | 0.0093354 | -0.014323 | 67.1356 | 67.2684 | 6.4362 | -55.806 | 67.3874 | -55.7053 | -55.7922 | -54.6158 | 26.0696 | -55.8975 | 67.4149 | 67.2958 | -55.8151 | -55.8838 | -0.07782 | -0.1648 | 0.10986 | 122.8958 | -0.17853 | -0.013733 | -0.14191 | -0.18768 | -0.25635 | 0.13733 | 1.0117 | -0.27008 | -0.013733 | 0.01831 | 123.0148 | 122.7631 | 62.0636 | -123.0698 | 123.0423 | 122.9233 | 81.6971 | -123.1613
2835.0156 | 123.1705 | -54.3503 | 68.5043 | -0.076447 | 0.0085171 | 0.0706 | 0.070731 | 0.13014 | -0.0037085 | -0.0064365 | 0.022736 | -0.011689 | 0.062342 | 0.05633 | 0.0046356 | -0.011546 | 68.3166 | 68.5593 | 5.365 | -54.6066 | 68.5638 | -54.4922 | -54.5883 | -53.3981 | 27.0859 | -54.3228 | 68.5822 | 68.5043 | -54.5517 | -54.5883 | -0.14191 | -0.23804 | 0.05951 | 122.9095 | -0.25635 | -0.01831 | -0.18768 | -0.20142 | -0.23804 | 0.07782 | 0.95215 | 0.027466 | 0.2655 | 0 | 122.9141 | 122.6669 | 59.7153 | -123.0927 | 122.9324 | 122.8546 | 81.4362 | -123.0927
2836.0156 | 123.1247 | -54.7852 | 68.0695 | -0.045929 | 0.0078763 | 0.071668 | 0.069876 | 0.12693 | -0.0032813 | -0.0094273 | 0.030365 | -0.012117 | 0.062769 | 0.057398 | 0.0048492 | -0.012828 | 67.955 | 68.1839 | 5.3284 | -54.9271 | 68.2068 | -54.8676 | -54.95 | -53.7598 | 26.8112 | -54.8447 | 68.161 | 68.042 | -54.9957 | -55.0232 | -0.082398 | -0.16479 | 0.13733 | 122.9691 | -0.14191 | 0.022888 | -0.11444 | -0.21057 | -0.23804 | 0.091553 | 1.0254 | -0.05951 | 0.17853 | -0.027466 | 122.9919 | 122.7402 | 60.1135 | -123.0194 | 122.9462 | 122.8271 | 81.5964 | -123.0927
2837.0156 | 123.1842 | -55.069 | 67.7856 | -0.11459 | 0.01044 | 0.071241 | 0.070944 | 0.12864 | -0.0030677 | -0.0077183 | 0.030365 | -0.010835 | 0.062128 | 0.05633 | 0.0067718 | -0.011974 | 67.6758 | 67.8864 | 6.1432 | -55.2567 | 67.8543 | -55.1743 | -55.275 | -54.0939 | 26.6327 | -55.1697 | 67.8223 | 67.717 | -55.2933 | -55.3574 | -0.10529 | -0.20599 | 0.068664 | 122.9553 | -0.18768 | 0.01831 | -0.10986 | -0.2243 | -0.28839 | 0.036621 | 0.97504 | -0.10071 | 0.18768 | -0.068665 | 122.9233 | 122.7448 | 61.2122 | -123.0606 | 122.8912 | 122.786 | 81.7017 | -123.143
2838.0156 | 123.1522 | -54.7256 | 68.1335 | -0.12222 | 0.0053129 | 0.072309 | 0.072226 | 0.12928 | -0.0022131 | -0.0077183 | -0.076446 | -0.0097668 | 0.059351 | 0.051417 | 0.0033538 | -0.0089828 | 68.0511 | 68.2709 | 4.9667 | -54.8904 | 68.2388 | -54.8355 | -54.8859 | -53.8193 | 26.7197 | -54.744 | 68.1976 | 68.1381 | -54.9271 | -54.9591 | -0.10986 | -0.16022 | 0.10529 | 122.9965 | -0.16479 | -0.004578 | -0.082398 | -0.20142 | -0.23346 | 0.064087 | 0.90637 | -0.018311 | 0.21515 | 0.004578 | 122.9645 | 122.7768 | 59.6924 | -123.0194 | 122.9233 | 122.8638 | 81.4453 | -123.0927
2839.0156 | 123.0652 | -54.1855 | 68.7332 | -0.23666 | 0.014285 | 0.071027 | 0.075003 | 0.12693 | 0.0031273 | -0.0057957 | -0.19089 | -0.010194 | 0.062555 | 0.055903 | 0.0091216 | -0.014323 | 68.541 | 68.6783 | 3.566 | -54.364 | 68.8705 | -54.2542 | -54.3686 | -53.2333 | 27.4246 | -54.2587 | 68.8797 | 68.7378 | -54.3594 | -54.4098 | -0.068664 | -0.18311 | 0.13733 | 122.8638 | -0.17853 | 0.004577 | -0.19226 | -0.17395 | -0.2243 | 0.14648 | 0.95215 | -0.073242 | 0.15106 | 0.004578 | 123.056 | 122.7264 | 57.7515 | -123.1018 | 123.0652 | 122.9233 | 81.6101 | -123.143
2840.0156 | 123.0927 | -54.4235 | 68.4494 | 0.12192 | 0.010013 | 0.069746 | 0.071158 | 0.12864 | -0.0017859 | -0.0079319 | 0.19058 | -0.0093396 | 0.062982 | 0.056758 | 0.0067718 | -0.012401 | 68.2755 | 68.4586 | 3.4744 | -54.6249 | 68.4998 | -54.5151 | -54.6112 | -53.4668 | 27.2415 | -54.6341 | 68.5272 | 68.4311 | -54.6249 | -54.6616 | -0.091553 | -0.18768 | 0.050354 | 122.8821 | -0.20142 | -0.013733 | -0.17395 | -0.20142 | -0.23804 | 0.07782 | 0.95673 | -0.21057 | 0.027466 | -0.018311 | 122.9233 | 122.699 | 57.8979 | -123.0606 | 122.9507 | 122.8546 | 81.665 | -123.111
2841.0156 | 123.1476 | -53.9337 | 68.9301 | 0.0914 | 0.0074491 | 0.071455 | 0.07009 | 0.12907 | -0.0039221 | -0.0075047 | 0.068512 | -0.0086988 | 0.062769 | 0.056544 | 0.0063446 | -0.012828 | 68.7653 | 68.9758 | 3.772 | -54.0985 | 69.0674 | -54.0207 | -54.1077 | -53.1097 | 27.4658 | -54.0985 | 68.9484 | 68.8385 | -54.1855 | -54.2038 | -0.086975 | -0.17395 | 0.13733 | 122.9095 | -0.1648 | 0.009155 | -0.16479 | -0.25177 | -0.27008 | 0.01831 | 0.82397 | -0.1648 | 0.10528 | -0.091553 | 123.0011 | 122.699 | 57.7057 | -123.0377 | 122.8821 | 122.7722 | 81.3995 | -123.1338
2842.0156 | 123.1476 | -54.4647 | 68.3807 | -0.068817 | 0.0057401 | 0.068678 | 0.070731 | 0.1295 | -0.0011451 | -0.0066501 | 0.045624 | -0.011262 | 0.062555 | 0.056971 | 0.0069854 | -0.013042 | 68.2892 | 68.4219 | 3.5065 | -54.6616 | 68.4906 | -54.5883 | -54.6616 | -53.508 | 27.3102 | -54.5563 | 68.4814 | 68.3899 | -54.6616 | -54.7028 | -0.1236 | -0.19684 | 0.10986 | 122.8867 | -0.19684 | 0 | -0.091552 | -0.19684 | -0.23804 | 0.10071 | 0.95673 | -0.091552 | 0.14648 | 0.009156 | 122.9553 | 122.7539 | 57.9712 | -123.0423 | 122.9462 | 122.8546 | 81.7749 | -123.0835
2843.0156 | 123.0377 | -54.7302 | 68.2068 | -0.9462 | 0.014285 | 0.069959 | 0.075858 | 0.12993 | 0.0037683 | -0.0075047 | -0.19852 | -0.0086988 | 0.06341 | 0.055903 | 0.0063446 | -0.014323 | 68.0923 | 68.2526 | 2.9251 | -54.7989 | 68.4265 | -54.7073 | -54.7943 | -53.7643 | 26.9943 | -54.9316 | 68.3533 | 68.1885 | -54.9225 | -54.9637 | 0.022889 | -0.064087 | 0.21973 | 122.9828 | -0.068664 | -0.004577 | -0.11444 | -0.19226 | -0.23346 | 0.14648 | 0.96588 | -0.20142 | 0.032043 | -0.01831 | 123.1567 | 122.8226 | 57.6553 | -123.0011 | 123.0835 | 122.9187 | 81.7245 | -123.1705
2844.0156 | 123.1705 | -54.9271 | 67.9596 | -0.14511 | 0.010226 | 0.073591 | 0.070303 | 0.12843 | -0.0019995 | -0.0049411 | 2.075 | -0.0099806 | 0.059137 | 0.056117 | 0.0080536 | -0.011333 | 67.9001 | 68.1198 | 2.9617 | -55.0095 | 68.0786 | -54.95 | -55.0369 | -53.9383 | 27.0309 | -55.0873 | 68.0008 | 67.9138 | -55.1559 | -55.1788 | -0.022888 | -0.10986 | 0.11902 | 123.0469 | -0.082397 | 0.027466 | -0.05951 | -0.22888 | -0.25177 | 0.041198 | 0.98877 | -0.16022 | 0.091553 | -0.045777 | 123.0057 | 122.8271 | 57.8888 | -122.9965 | 122.9279 | 122.8409 | 81.958 | -123.1384
2845.0156 | 123.1018 | -55.4672 | 67.3737 | 0.060882 | 0.0091581 | 0.070814 | 0.072012 | 0.12758 | -0.0026405 | -0.0068637 | 0.09903 | -0.0099806 | 0.060846 | 0.055903 | 0.00549 | -0.013042 | 67.2546 | 67.4469 | 2.3666 | -55.6229 | 67.5247 | -55.545 | -55.6274 | -54.483 | 26.5823 | -55.6046 | 67.4835 | 67.3782 | -55.6641 | -55.7098 | -0.07782 | -0.16022 | 0.15106 | 122.9141 | -0.15564 | 0.004577 | -0.11902 | -0.19684 | -0.24262 | 0.10986 | 0.98419 | -0.13733 | 0.10529 | 0.004578 | 122.9919 | 122.7219 | 57.8339 | -123.0011 | 122.9507 | 122.8455 | 82.0496 | -123.0835
2846.0156 | 123.1293 | -55.2063 | 67.6529 | 0.14481 | 0.0083035 | 0.072309 | 0.070517 | 0.128 | -0.0017859 | -0.0081455 | 0.19058 | -0.0093396 | 0.062128 | 0.058253 | 0.0067718 | -0.012614 | 67.5842 | 67.7582 | 1.4374 | -55.3207 | 67.8314 | -55.2155 | -55.2933 | -54.2542 | 24.5728 | -55.2887 | 67.7856 | 67.6575 | -55.4077 | -55.4535 | -0.009155 | -0.086975 | 0.17853 | 122.9645 | -0.11444 | -0.027466 | -0.068664 | -0.20142 | -0.24719 | 0.13275 | 0.95215 | -0.082397 | 0.16479 | 0.004578 | 123.0377 | 122.7905 | 56.6437 | -122.9462 | 122.9919 | 122.8638 | 79.7791 | -123.1064
2847.0156 | 123.1522 | -54.7943 | 68.0603 | -0.023041 | 0.0091581 | 0.071882 | 0.073935 | 0.12608 | -0.0019995 | -0.0070773 | 0.030365 | -0.012117 | 0.063837 | 0.056971 | 0.0048492 | -0.013469 | 67.9413 | 68.1015 | 1.442 | -55.0049 | 68.1656 | -54.9271 | -55.0186 | -53.8651 | 25.9277 | -54.9271 | 68.1107 | 68.0099 | -55.0507 | -55.0919 | -0.13275 | -0.2243 | 0.10528 | 122.8958 | -0.21057 | 0.013733 | -0.11902 | -0.25635 | -0.29755 | 0.050354 | 0.92926 | -0.13275 | 0.1648 | -0.050354 | 122.9599 | 122.7356 | 56.2363 | -123.0789 | 122.905 | 122.8043 | 80.722 | -123.1522
2848.0312 | 123.0606 | -54.6982 | 68.2526 | -0.17563 | 0.017276 | 0.0706 | 0.075217 | 0.12907 | 0.0041955 | -0.0068637 | -0.20615 | -0.010408 | 0.067041 | 0.056544 | 0.01019 | -0.014751 | 68.2205 | 68.3212 | 0.99792 | -54.7256 | 68.4906 | -54.6616 | -54.776 | -53.8055 | 23.8403 | -55.0003 | 68.3258 | 68.1885 | -54.9271 | -54.9911 | 0.036621 | -0.07782 | 0.23804 | 123.0194 | -0.027466 | 0.050354 | -0.032043 | -0.22888 | -0.29297 | 0.073243 | 0.89264 | -0.30212 | -0.009155 | -0.064086 | 123.1888 | 122.9187 | 55.6961 | -123.0286 | 123.024 | 122.8867 | 78.5385 | -123.2437
2849.0312 | 123.0881 | -54.6753 | 68.1793 | -0.18326 | 0.014712 | 0.068678 | 0.072653 | 0.12928 | 0.0024865 | -0.0064365 | -0.17563 | -0.009126 | 0.064264 | 0.055689 | 0.0084808 | -0.013469 | 68.4357 | 68.5822 | 1.4145 | -54.4876 | 68.6966 | -54.4006 | -54.5197 | -53.4027 | 23.4329 | -54.4968 | 68.66 | 68.4723 | -54.6753 | -54.8218 | 0.27466 | 0.15564 | 0.51727 | 123.2574 | 0.18768 | 0.032043 | 0.25635 | 0 | -0.14648 | 0.48065 | 1.2726 | 0.17853 | 0.32501 | 0.29297 | 123.3719 | 123.111 | 56.0898 | -122.699 | 123.3353 | 123.1476 | 78.1082 | -123.0011
2850.0156 | 123.0972 | -54.4327 | 68.4357 | -0.00015269 | 0.0083035 | 0.072309 | 0.07009 | 0.128 | -0.0032813 | -0.0062229 | -0.03067 | -0.010194 | 0.060846 | 0.054835 | 0.006131 | -0.010051 | 68.2755 | 68.6783 | 1.474 | -54.5792 | 68.5776 | -54.5059 | -54.5654 | -53.5538 | 23.41 | -54.6158 | 68.5226 | 68.4036 | -54.6524 | -54.689 | -0.073242 | -0.13275 | 0.14191 | 123.111 | -0.14648 | -0.013733 | -0.16022 | -0.21973 | -0.25635 | 0.086975 | 0.87891 | -0.18311 | 0.073242 | -0.032044 | 123.0103 | 122.7081 | 55.9067 | -123.0011 | 122.9553 | 122.8363 | 77.8427 | -123.1247
2851.0156 | 123.111 | -54.3411 | 68.486 | 0.18295 | 0.011722 | 0.071455 | 0.07009 | 0.12736 | -0.0022131 | -0.0053683 | 0.21347 | -0.0099806 | 0.062342 | 0.054835 | 0.004422 | -0.013896 | 68.0832 | 68.2983 | 1.2405 | -54.7165 | 68.367 | -54.6021 | -54.6844 | -53.4164 | 23.3139 | -54.4556 | 68.5547 | 68.4586 | -54.5746 | -54.6204 | -0.26093 | -0.34332 | -0.11902 | 122.6395 | -0.37537 | -0.032044 | -0.40283 | -0.23346 | -0.27924 | 0.068664 | 0.92468 | -0.11444 | 0.1648 | -0.027466 | 122.7081 | 122.4243 | 55.5817 | -123.1705 | 122.8958 | 122.7997 | 77.655 | -123.1064
2852.0156 | 123.0835 | -53.8147 | 69.0216 | 0.16006 | 0.011294 | 0.068891 | 0.068808 | 0.12864 | -0.00029045 | -0.0087863 | 0.20584 | -0.0099806 | 0.063837 | 0.054194 | 0.0086944 | -0.012614 | 69.1681 | 69.3466 | 1.4923 | -53.7415 | 69.397 | -53.6453 | -53.7643 | -52.8534 | 25.8316 | -54.0482 | 69.0994 | 69.0262 | -54.039 | -54.071 | 0.16937 | 0.050354 | 0.37537 | 123.1613 | 0.073242 | 0.022888 | 0.14648 | -0.2243 | -0.25635 | 0.07782 | 0.9613 | -0.23346 | 0.022888 | 0.004578 | 123.2117 | 122.9828 | 55.307 | -122.7859 | 122.9141 | 122.8409 | 79.6463 | -123.0927
2853.0312 | 123.0881 | -53.6407 | 69.2642 | -0.10696 | 0.016849 | 0.071455 | 0.07479 | 0.12864 | 0.0046227 | -0.0045139 | -0.14511 | -0.005708 | 0.063623 | 0.055689 | 0.008908 | -0.017741 | 69.1956 | 69.3054 | 1.3321 | -53.7552 | 69.429 | -53.6591 | -53.7369 | -52.8854 | 25.8682 | -53.92 | 69.2551 | 69.1544 | -53.9154 | -53.9337 | -0.018311 | -0.09613 | 0.16479 | 122.9462 | -0.11444 | -0.018311 | -0.068664 | -0.27466 | -0.29297 | -0.009155 | 0.75531 | -0.27924 | 0.013733 | -0.10986 | 123.0698 | 122.8363 | 54.9728 | -123.0011 | 122.8958 | 122.7951 | 79.509 | -123.1979
2854.0156 | 123.0972 | -54.0253 | 68.9026 | -0.23666 | 0.010653 | 0.073591 | 0.070944 | 0.12822 | -0.0024269 | -0.0060093 | -0.14511 | -0.011049 | 0.059778 | 0.055476 | 0.0052764 | -0.010692 | 68.6005 | 68.8614 | 1.5747 | -54.1992 | 68.9026 | -54.1626 | -54.2496 | -53.0319 | 25.6668 | -54.1031 | 68.9301 | 68.8522 | -54.2542 | -54.2633 | -0.13733 | -0.2243 | 0 | 122.8867 | -0.17395 | 0.050354 | -0.30212 | -0.22888 | -0.23804 | 0.027466 | 0.99335 | -0.077819 | 0.16022 | -0.050354 | 122.9279 | 122.6257 | 55.6 | -123.1522 | 122.9553 | 122.8775 | 79.6921 | -123.1659
2855.0156 | 123.1293 | -54.2679 | 68.6096 | -0.00015269 | 0.0068081 | 0.074445 | 0.071799 | 0.12993 | -0.0039221 | -0.0079319 | 0.083771 | -0.012758 | 0.05871 | 0.055262 | 0.0042084 | -0.010692 | 68.4311 | 68.6188 | 1.1398 | -54.4601 | 68.7195 | -54.3503 | -54.4418 | -53.2837 | 25.6531 | -54.4464 | 68.6691 | 68.5501 | -54.5242 | -54.5517 | -0.082398 | -0.17395 | 0.10986 | 122.8867 | -0.19226 | -0.018311 | -0.17853 | -0.25635 | -0.28381 | 0.059509 | 0.98419 | -0.17853 | 0.10529 | -0.059509 | 122.9874 | 122.699 | 55.4077 | -123.0515 | 122.937 | 122.818 | 79.921 | -123.1613
2856.0156 | 123.1567 | -53.6499 | 69.1589 | 0.20584 | 0.012362 | 0.071668 | 0.070944 | 0.1295 | 0.00099115 | -0.0057957 | -0.12222 | -0.009126 | 0.062769 | 0.055689 | 0.0091216 | -0.01176 | 69.2047 | 69.0216 | 0.87433 | -53.714 | 69.2917 | -53.7552 | -53.8467 | -52.6382 | 26.1703 | -53.7094 | 69.2825 | 69.1681 | -53.8651 | -53.9062 | -0.10529 | -0.19684 | 0.13275 | 122.6715 | -0.064087 | 0.13275 | 0.045776 | -0.21515 | -0.25635 | 0.1236 | 1.0117 | -0.05951 | 0.19684 | 0.009155 | 122.9416 | 122.8546 | 54.5242 | -123.0057 | 122.9324 | 122.818 | 79.8203 | -123.0652
2857.0156 | 123.1338 | -53.4943 | 69.342 | 0.099029 | 0.010226 | 0.071027 | 0.069876 | 0.13014 | 0.0012047 | -0.0051547 | 0.22873 | -0.010835 | 0.063196 | 0.056544 | 0.0082672 | -0.013469 | 69.3192 | 69.4702 | 1.3458 | -53.6453 | 69.4931 | -53.54 | -53.6407 | -52.446 | 26.1246 | -53.6041 | 69.4885 | 69.3832 | -53.6957 | -53.7781 | -0.045776 | -0.14648 | 0.15106 | 122.9645 | -0.15106 | -0.004578 | -0.022888 | -0.20142 | -0.28381 | 0.14648 | 1.0483 | -0.10986 | 0.17395 | 0.041199 | 122.9874 | 122.8134 | 54.8401 | -122.9828 | 122.9828 | 122.8775 | 79.6188 | -123.1201
2858.0312 | 123.0515 | -54.5334 | 68.3853 | -0.16037 | 0.01578 | 0.068464 | 0.073508 | 0.12843 | 0.0024865 | -0.0057957 | -0.19852 | -0.009126 | 0.062982 | 0.057612 | 0.0093354 | -0.013469 | 68.2251 | 68.3258 | 0.97961 | -54.7073 | 68.5043 | -54.657 | -54.7211 | -53.5904 | 25.383 | -54.6753 | 68.4631 | 68.3578 | -54.7852 | -54.7897 | -0.1236 | -0.18768 | 0.11902 | 122.8592 | -0.17395 | 0.013733 | -0.16022 | -0.25177 | -0.25635 | 0.07782 | 0.94299 | -0.14191 | 0.11444 | -0.027466 | 123.0377 | 122.7585 | 55.513 | -123.1064 | 122.9965 | 122.8912 | 79.9164 | -123.175
2859.0156 | 123.1384 | -53.6728 | 69.2001 | -0.22903 | 0.0091581 | 0.070814 | 0.067526 | 0.12736 | -0.0022131 | -0.0083591 | -0.061188 | -0.010408 | 0.059564 | 0.054621 | 0.0035674 | -0.0079148 | 69.1177 | 69.3237 | 1.236 | -53.8055 | 69.31 | -53.746 | -53.833 | -52.7847 | 25.9048 | -53.6133 | 69.2825 | 69.1818 | -53.8513 | -53.8971 | -0.073242 | -0.16022 | 0.10986 | 122.9965 | -0.13275 | 0.027466 | -0.082397 | -0.17853 | -0.2243 | 0.082398 | 0.88806 | 0.05951 | 0.28381 | -0.01831 | 122.9828 | 122.7905 | 54.9088 | -123.0331 | 122.9553 | 122.8546 | 79.5776 | -123.0972
2860.0156 | 123.0743 | -53.7781 | 69.136 | 0.13718 | 0.016208 | 0.071027 | 0.071372 | 0.128 | 0.0035547 | -0.0057957 | 0.18295 | -0.010194 | 0.066187 | 0.054835 | 0.0093354 | -0.01176 | 69.0079 | 69.0857 | 0.98877 | -53.9658 | 69.2642 | -53.8605 | -53.9383 | -52.7802 | 25.9872 | -53.8376 | 69.2551 | 69.1315 | -53.9612 | -53.9932 | -0.082398 | -0.16022 | 0.12817 | 122.8638 | -0.18768 | -0.027466 | -0.12817 | -0.18311 | -0.21515 | 0.11902 | 0.99793 | -0.059509 | 0.15564 | -0.004577 | 123.0423 | 122.7859 | 54.7668 | -123.0743 | 123.0331 | 122.9095 | 79.7653 | -123.1293
2861.0312 | 123.0011 | -53.9749 | 68.9484 | 0.022736 | 0.019839 | 0.070387 | 0.074149 | 0.12672 | 0.0039819 | -0.0038731 | 0.11429 | -0.0072034 | 0.064691 | 0.055689 | 0.010831 | -0.013683 | 68.779 | 68.8843 | 0.99792 | -54.1397 | 69.1086 | -54.0024 | -54.1214 | -53.0273 | 25.795 | -54.2633 | 69.0765 | 68.9621 | -54.1534 | -54.2313 | -0.027465 | -0.14648 | 0.16022 | 122.8592 | -0.16479 | -0.01831 | -0.16937 | -0.17853 | -0.25635 | 0.12817 | 0.94757 | -0.28839 | -0.032044 | 0.013733 | 123.0835 | 122.7539 | 54.9728 | -123.0698 | 123.0515 | 122.937 | 79.7699 | -123.1796
2862.0156 | 123.1155 | -54.3365 | 68.5364 | 0.12192 | 0.010226 | 0.071455 | 0.069235 | 0.12672 | -0.0043495 | -0.0068637 | 0.19058 | -0.0099806 | 0.059992 | 0.058253 | 0.0059174 | -0.013255 | 68.3899 | 68.573 | 0.99335 | -54.5242 | 68.6325 | -54.4189 | -54.5105 | -53.4073 | 25.9506 | -54.4418 | 68.6188 | 68.5318 | -54.5334 | -54.5883 | -0.082397 | -0.17395 | 0.09613 | 122.9095 | -0.18768 | -0.013733 | -0.14648 | -0.19684 | -0.25177 | 0.082397 | 0.92926 | -0.10529 | 0.14648 | -0.004578 | 122.9691 | 122.7264 | 55.3299 | -123.0469 | 122.9553 | 122.8683 | 80.2872 | -123.1247
2863.0156 | 123.0835 | -53.3386 | 69.4931 | 0.037994 | 0.0078763 | 0.069746 | 0.070731 | 0.12693 | -0.0026405 | -0.0072911 | 0.18295 | -0.0093396 | 0.062128 | 0.055903 | 0.0093354 | -0.010692 | 69.3466 | 69.5114 | 1.0712 | -53.5538 | 69.6075 | -53.4393 | -53.5217 | -52.3544 | 26.1108 | -53.3707 | 69.6533 | 69.548 | -53.5355 | -53.6133 | -0.10071 | -0.18311 | 0.11444 | 122.85 | -0.21515 | -0.032043 | -0.14648 | -0.19684 | -0.27466 | 0.16022 | 0.98419 | -0.032044 | 0.24261 | 0.054932 | 122.9462 | 122.6852 | 54.4098 | -123.0148 | 122.9919 | 122.8867 | 79.4495 | -123.1064
2864.0156 | 123.143 | -53.1967 | 69.6762 | -0.076447 | 0.0083035 | 0.059065 | 0.070944 | 0.13121 | -0.0043495 | -0.0081455 | 0.022736 | -0.010408 | 0.063196 | 0.054835 | 0.0057038 | -0.011119 | 69.516 | 69.722 | 1.2177 | -53.389 | 69.7266 | -53.3386 | -53.4256 | -52.1988 | 25.7721 | -53.3249 | 69.7128 | 69.6259 | -53.4348 | -53.4714 | -0.14191 | -0.22888 | 0.050354 | 122.9187 | -0.19226 | 0.036621 | -0.16022 | -0.23804 | -0.27466 | 0.036622 | 0.99792 | -0.12817 | 0.14648 | -0.050354 | 122.9233 | 122.7127 | 54.4144 | -123.1018 | 122.9095 | 122.8226 | 78.9688 | -123.1476
2865.0156 | 123.1476 | -53.9062 | 68.9163 | 0.23636 | 0.014499 | 0.070173 | 0.069235 | 0.13014 | 0.00056395 | -0.0081455 | 0.23636 | -0.0099806 | 0.060846 | 0.052272 | 0.0065582 | -0.015392 | 68.6783 | 68.8156 | 1.1581 | -54.2633 | 68.8614 | -54.1992 | -54.2633 | -52.9358 | 24.6552 | -53.92 | 69.0399 | 68.9209 | -54.1168 | -54.1763 | -0.29297 | -0.35706 | -0.054932 | 122.7219 | -0.35706 | 0 | -0.23804 | -0.21057 | -0.27008 | 0.1236 | 0.97046 | -0.013733 | 0.25635 | 0.004577 | 122.7676 | 122.5845 | 55.0644 | -123.1796 | 122.9462 | 122.8271 | 78.5614 | -123.0927
2866.0156 | 123.1659 | -53.6224 | 69.2184 | 0.22873 | 0.010013 | 0.0706 | 0.069449 | 0.12672 | -0.0030677 | -0.0072911 | 0.23636 | -0.011262 | 0.065332 | 0.055476 | 0.0084808 | -0.013255 | 69.2001 | 69.3008 | 1.0941 | -53.8239 | 69.342 | -53.7231 | -53.833 | -52.5879 | 25.145 | -53.746 | 69.3329 | 69.2047 | -53.8376 | -53.8651 | -0.10071 | -0.21057 | 0.1236 | 122.9233 | -0.20142 | 0.009155 | -0.018311 | -0.21515 | -0.24261 | 0.11444 | 1.0345 | -0.1236 | 0.11902 | -0.013733 | 122.9645 | 122.8226 | 54.7165 | -123.0515 | 122.9553 | 122.8271 | 78.7674 | -123.0835
2867.0156 | 123.1476 | -53.5492 | 69.2871 | 0.15244 | 0.0095853 | 0.070173 | 0.068381 | 0.12993 | -0.0017859 | -0.0068637 | 0.28214 | -0.010194 | 0.06106 | 0.056544 | 0.0080536 | -0.013896 | 69.3192 | 69.2505 | 1.3275 | -53.714 | 69.3375 | -53.6682 | -53.7506 | -52.5513 | 24.2615 | -53.6362 | 69.3649 | 69.3008 | -53.7735 | -53.801 | -0.11902 | -0.20142 | 0.050354 | 122.7997 | -0.16479 | 0.036621 | 0.032044 | -0.22431 | -0.25177 | 0.07782 | 0.99792 | -0.086975 | 0.16479 | 0.013733 | 122.8867 | 122.8683 | 54.8767 | -123.0377 | 122.9141 | 122.85 | 77.8107 | -123.0881
2868.0156 | 123.0606 | -53.4256 | 69.4611 | 0.33554 | 0.017917 | 0.069532 | 0.074149 | 0.12864 | 0.0024865 | -0.0051547 | 0.15244 | -0.0084852 | 0.066828 | 0.055476 | 0.0065582 | -0.013255 | 69.2001 | 69.278 | 0.92926 | -53.7277 | 69.4839 | -53.6179 | -53.714 | -52.5101 | 24.4766 | -53.5721 | 69.516 | 69.4473 | -53.6636 | -53.6728 | -0.19226 | -0.28839 | 0.022888 | 122.7036 | -0.30212 | -0.013733 | -0.26093 | -0.23804 | -0.24719 | 0.054931 | 0.91553 | -0.14648 | 0.10071 | -0.013733 | 122.9095 | 122.6257 | 54.3549 | -123.175 | 122.9416 | 122.8729 | 77.9022 | -123.1339
2869.0156 | 123.1842 | -53.8422 | 69.017 | -0.068817 | 0.0083035 | 0.073377 | 0.069235 | 0.13099 | -0.0049903 | -0.0068637 | 0.015106 | -0.011476 | 0.060846 | 0.054835 | 0.0057038 | -0.011546 | 68.7103 | 69.0033 | 1.1765 | -54.0848 | 69.017 | -54.0161 | -54.1122 | -52.8488 | 24.2981 | -53.8147 | 69.0353 | 68.9667 | -54.0802 | -54.0939 | -0.17395 | -0.27008 | 0 | 122.8455 | -0.24262 | 0.027466 | -0.3067 | -0.23804 | -0.25177 | 0.01831 | 0.99335 | 0.027466 | 0.27924 | -0.050354 | 122.8592 | 122.5525 | 55.0186 | -123.1293 | 122.8775 | 122.8088 | 78.1403 | -123.111
2870.0156 | 123.1476 | -52.9037 | 69.9646 | 0.16769 | 0.016208 | 0.0706 | 0.07009 | 0.12993 | 0.0020593 | -0.0062229 | -0.023041 | -0.0097668 | 0.063196 | 0.055903 | 0.0097626 | -0.013469 | 69.8227 | 70.047 | 1.1948 | -53.1921 | 69.9738 | -53.0502 | -53.1418 | -52.002 | 24.6735 | -53.1052 | 69.9417 | 69.8456 | -53.2059 | -53.1921 | -0.14648 | -0.23804 | 0.009155 | 122.9507 | -0.28839 | -0.050354 | -0.14191 | -0.30212 | -0.28839 | -0.022889 | 0.90179 | -0.20142 | 0.086975 | -0.11902 | 122.8775 | 122.7264 | 54.0985 | -123.1064 | 122.8455 | 122.7493 | 77.5772 | -123.1567
2871.0156 | 123.1293 | -54.007 | 68.8293 | 0.12192 | 0.011294 | 0.069532 | 0.066885 | 0.12736 | -0.0019995 | -0.0051547 | 0.16006 | -0.0095532 | 0.06106 | 0.055689 | 0.0076264 | -0.01411 | 68.7378 | 68.9529 | 1.268 | -54.1763 | 68.9438 | -54.0756 | -54.1626 | -52.9633 | 23.7625 | -54.0161 | 69.0033 | 68.8843 | -54.1901 | -54.2313 | -0.068665 | -0.15564 | 0.11444 | 122.9599 | -0.16937 | -0.013733 | -0.091553 | -0.18311 | -0.2243 | 0.17395 | 1.0437 | -0.009155 | 0.21515 | 0.054931 | 122.9507 | 122.7448 | 55.275 | -122.9919 | 123.0103 | 122.8912 | 77.7695 | -123.0606
2872.0156 | 123.0377 | -52.3682 | 70.5643 | 0.13718 | 0.019198 | 0.071241 | 0.067954 | 0.12843 | 0.0027001 | -0.0096409 | -0.00015237 | -0.009126 | 0.064691 | 0.056117 | 0.0099762 | -0.013896 | 70.5093 | 70.1157 | 1.0025 | -52.771 | 70.4727 | -52.652 | -52.771 | -51.5488 | 24.6643 | -52.5101 | 70.5688 | 70.5002 | -52.6199 | -52.6382 | -0.28381 | -0.40283 | -0.091553 | 122.4838 | -0.40283 | 0 | -0.054932 | -0.25177 | -0.27008 | 0.004578 | 0.8194 | -0.14191 | 0.12817 | -0.064087 | 122.8409 | 122.8775 | 53.3707 | -123.3353 | 122.937 | 122.8683 | 77.0325 | -123.2025
2873.0156 | 123.0423 | -53.0411 | 69.9051 | 0.083771 | 0.016421 | 0.066328 | 0.069876 | 0.13014 | 0.0048363 | -0.0072911 | 0.09903 | -0.0059216 | 0.065759 | 0.054621 | 0.0067718 | -0.013683 | 69.6716 | 69.7495 | 0.98419 | -53.3203 | 69.9875 | -53.1555 | -53.2425 | -52.1851 | 24.4812 | -53.2242 | 69.9692 | 69.8456 | -53.2654 | -53.2837 | -0.11444 | -0.20142 | 0.082398 | 122.7905 | -0.27923 | -0.077819 | -0.23346 | -0.2243 | -0.24261 | 0.064087 | 0.85602 | -0.1831 | 0.059509 | -0.059509 | 123.0286 | 122.7127 | 54.0253 | -123.1476 | 123.0103 | 122.8867 | 77.5223 | -123.1888
2874.0156 | 123.0881 | -52.684 | 70.1981 | 0.14481 | 0.013003 | 0.0706 | 0.07009 | 0.12651 | -0.0037085 | -0.0038731 | 0.2211 | -0.010194 | 0.061273 | 0.05633 | 0.0082672 | -0.012187 | 70.0699 | 70.2667 | 1.3046 | -52.8259 | 70.3033 | -52.7481 | -52.9083 | -51.7914 | 35.9528 | -53.0502 | 70.0607 | 70.0241 | -52.9999 | -53.009 | -0.064087 | -0.2243 | 0.10529 | 122.9507 | -0.14191 | 0.082397 | -0.12817 | -0.31586 | -0.32501 | -0.13733 | 0.89264 | -0.36621 | -0.041199 | -0.17395 | 122.9874 | 122.7539 | 53.9886 | -123.1064 | 122.7448 | 122.7081 | 88.6368 | -123.2071
2875.0156 | 123.175 | -52.6611 | 70.1523 | 0.17532 | 0.016635 | 0.069319 | 0.072012 | 0.13078 | 0.00056395 | -0.0051547 | 0.21347 | -0.0097668 | 0.061487 | 0.056117 | 0.0093354 | -0.014537 | 70.2896 | 70.3949 | 1.1444 | -52.6932 | 70.4407 | -52.6016 | -52.6886 | -51.384 | 36.2503 | -52.6703 | 70.4178 | 70.2576 | -52.8351 | -52.89 | 0.059509 | -0.027466 | 0.28839 | 123.056 | -0.032043 | -0.004577 | 0.13733 | -0.17395 | -0.22888 | 0.2655 | 1.2772 | -0.009155 | 0.21973 | 0.10529 | 123.1018 | 122.9507 | 53.8055 | -122.8409 | 123.0789 | 122.9187 | 88.9114 | -123.0423
2876.0156 | 123.0286 | -52.5604 | 70.3903 | -0.00015269 | 0.018344 | 0.067396 | 0.073294 | 0.12651 | 0.0033411 | -0.0051547 | 0.022736 | -0.0072034 | 0.065546 | 0.057826 | 0.008908 | -0.013896 | 69.9921 | 70.0699 | 1.1398 | -52.8442 | 70.3308 | -52.7618 | -52.8397 | -51.6632 | 35.7651 | -52.7344 | 70.3171 | 70.2621 | -52.8625 | -52.858 | -0.20142 | -0.27924 | -0.059509 | 122.6303 | -0.28381 | -0.004577 | -0.39826 | -0.30212 | -0.29755 | -0.073242 | 0.89722 | -0.17395 | 0.1236 | -0.12817 | 122.8912 | 122.5525 | 53.7003 | -123.23 | 122.8775 | 122.8226 | 88.3255 | -123.2483
2877.0156 | 123.0469 | -53.6133 | 69.3283 | 0.0914 | 0.016849 | 0.069746 | 0.074149 | 0.12779 | 0.0016321 | -0.0049411 | 0.14481 | -0.010408 | 0.065332 | 0.056117 | 0.0067718 | -0.010265 | 68.9758 | 69.072 | 1.0666 | -53.9474 | 69.2596 | -53.8422 | -53.9291 | -52.6382 | 35.6003 | -53.7094 | 69.3146 | 69.2871 | -53.8376 | -53.8605 | -0.22888 | -0.31586 | -0.068664 | 122.6852 | -0.33417 | -0.018311 | -0.35248 | -0.2243 | -0.24719 | -0.013733 | 0.97504 | -0.096131 | 0.15106 | -0.041199 | 122.8729 | 122.5891 | 54.6799 | -123.2574 | 122.9279 | 122.9004 | 89.2136 | -123.1888
2878.0156 | 123.0606 | -53.4439 | 69.4748 | 0.15244 | 0.01514 | 0.068464 | 0.071585 | 0.13057 | -7.6852e-05 | -0.0045139 | 0.19058 | -0.0084852 | 0.063196 | 0.056758 | 0.0086944 | -0.011119 | 69.4656 | 69.5709 | 0.90179 | -53.4988 | 69.7311 | -53.3661 | -53.4851 | -52.2308 | 35.7101 | -53.8055 | 69.5847 | 69.4748 | -53.6545 | -53.714 | 0.07782 | -0.041198 | 0.25635 | 123.0148 | -0.054931 | -0.013733 | -0.009155 | -0.21057 | -0.27008 | 0.10986 | 1.2131 | -0.36163 | -0.091553 | 0 | 123.175 | 122.9095 | 54.3457 | -122.9599 | 123.0286 | 122.9187 | 89.1541 | -123.1888
2879.0156 | 123.1247 | -53.2974 | 69.5984 | 0.099029 | 0.0076627 | 0.073805 | 0.068808 | 0.12715 | -0.0043495 | -0.0075047 | 0.13718 | -0.010194 | 0.05871 | 0.057612 | 0.0059174 | -0.010265 | 69.2001 | 69.4199 | 4.9026 | -53.6453 | 69.4931 | -53.5172 | -53.5995 | -52.2995 | 35.6918 | -53.3707 | 69.6167 | 69.5206 | -53.5355 | -53.5675 | -0.21973 | -0.30212 | -0.10529 | 122.7173 | -0.3479 | -0.045777 | -0.39825 | -0.23804 | -0.27008 | 0.01831 | 0.99792 | -0.073243 | 0.19684 | -0.07782 | 122.7905 | 122.4976 | 58.2001 | -123.1979 | 122.9141 | 122.818 | 88.9893 | -123.1659
2880.0156 | 123.0377 | -54.6524 | 68.2434 | -0.22141 | 0.01813 | 0.070387 | 0.073081 | 0.12715 | 0.0027001 | -0.0060093 | -0.076446 | -0.0097668 | 0.066187 | 0.055903 | 0.011472 | -0.014751 | 68.1473 | 68.2526 | 12.2589 | -54.7943 | 68.3716 | -54.7256 | -54.8172 | -53.4897 | 34.6985 | -54.7806 | 68.3762 | 68.2709 | -54.8309 | -54.8813 | -0.073242 | -0.16479 | 0.12817 | 122.905 | -0.14191 | 0.022888 | -0.09613 | -0.17853 | -0.22888 | 0.13275 | 1.1627 | -0.12817 | 0.10071 | 0.027466 | 123.024 | 122.7997 | 66.9113 | -123.0606 | 123.0286 | 122.9233 | 89.3509 | -123.1247
2881.0156 | 123.0148 | -54.7943 | 68.1152 | 0.068512 | 0.016421 | 0.068678 | 0.072012 | 0.12907 | -0.00029045 | -0.0036595 | 0.09903 | -0.0067762 | 0.067896 | 0.057826 | 0.0093354 | -0.013683 | 68.1839 | 68.3075 | 13.9572 | -54.7256 | 68.4814 | -54.657 | -54.7714 | -53.6545 | 33.9569 | -54.657 | 68.3945 | 68.2755 | -54.8904 | -54.9866 | 0.13733 | 0.022889 | 0.36621 | 123.1018 | 0.068665 | 0.045776 | 0.068665 | -0.09613 | -0.19226 | 0.27924 | 1.1398 | 0.13733 | 0.32959 | 0.16022 | 123.2758 | 122.9782 | 68.7515 | -122.8867 | 123.1888 | 123.0698 | 88.7512 | -123.1018
2882.0156 | 123.0057 | -54.3686 | 68.5776 | 0.11429 | 0.017917 | 0.071668 | 0.071372 | 0.12544 | -0.0017859 | -0.0087863 | 0.16769 | -0.0076306 | 0.065759 | 0.058253 | 0.008908 | -0.012187 | 68.6005 | 68.28 | 13.1424 | -54.538 | 68.6554 | -54.4968 | -54.5975 | -53.2745 | 34.2087 | -54.5197 | 68.6554 | 68.5455 | -54.5609 | -54.6021 | -0.12817 | -0.22888 | 0.07782 | 122.6486 | -0.16937 | 0.059509 | 0.022888 | -0.19226 | -0.23346 | 0.07782 | 1.0941 | -0.15106 | 0.082398 | -0.032044 | 123.024 | 122.9691 | 67.511 | -123.175 | 123.024 | 122.9141 | 88.5773 | -123.1796
2883.0156 | 123.0881 | -53.8879 | 69.0445 | 0.17532 | 0.01514 | 0.070173 | 0.074362 | 0.12928 | -0.00050425 | -0.0060093 | 0.19821 | -0.0093396 | 0.065973 | 0.058467 | 0.007199 | -0.012401 | 68.9117 | 69.0262 | 9.4299 | -53.9886 | 69.1864 | -53.8788 | -54.039 | -52.8809 | 32.9224 | -54.1992 | 69.0399 | 68.9484 | -54.1763 | -54.1809 | 0.009155 | -0.15106 | 0.14191 | 122.9141 | -0.10071 | 0.050354 | -0.13275 | -0.28839 | -0.29297 | -0.004578 | 1.0071 | -0.31128 | -0.018311 | -0.096131 | 123.0743 | 122.7997 | 63.3179 | -123.0835 | 122.9279 | 122.8363 | 86.8103 | -123.2254
2884.0156 | 122.9965 | -53.2333 | 69.6808 | 0.13718 | 0.015994 | 0.069532 | 0.072867 | 0.12822 | 0.0029137 | -0.0040867 | 0.15244 | -0.0086988 | 0.062769 | 0.055049 | 0.01489 | -0.011333 | 69.3146 | 69.4199 | 3.4378 | -53.5858 | 69.6762 | -53.4531 | -53.5492 | -52.3636 | 34.3643 | -53.2883 | 69.7861 | 69.7266 | -53.4348 | -53.5034 | -0.21973 | -0.31586 | -0.004578 | 122.6532 | -0.35248 | -0.036621 | -0.36621 | -0.20142 | -0.27008 | 0.10529 | 0.86975 | -0.054932 | 0.21515 | 0.045776 | 122.9095 | 122.5479 | 56.6711 | -123.23 | 123.0194 | 122.9599 | 87.5977 | -123.1842
2885.0156 | 122.9279 | -53.4119 | 69.5801 | 0.083771 | 0.014712 | 0.069532 | 0.070731 | 0.12993 | -0.00029045 | -0.0045139 | 0.16006 | -0.0093396 | 0.064691 | 0.056971 | 0.0086944 | -0.01176 | 69.1086 | 69.1544 | 6.9168 | -53.8513 | 69.4519 | -53.6682 | -53.7872 | -52.3636 | 31.2057 | -53.6407 | 69.5618 | 69.5343 | -53.6362 | -53.6728 | -0.25635 | -0.37537 | -0.12817 | 122.5662 | -0.43945 | -0.064087 | -0.4715 | -0.2243 | -0.26093 | -0.01831 | 1.0483 | -0.22888 | 0.032044 | -0.045776 | 122.8638 | 122.5204 | 60.3287 | -123.3673 | 122.9736 | 122.9462 | 84.6176 | -123.2529
2886.0156 | 123.0423 | -52.8442 | 70.0699 | -0.015411 | 0.018985 | 0.066755 | 0.071799 | 0.13078 | 0.0033411 | -0.0043003 | 0.060883 | -0.0097668 | 0.064051 | 0.05633 | 0.010403 | -0.012401 | 69.8868 | 70.0104 | 8.1848 | -53.0136 | 70.1752 | -52.9221 | -53.0136 | -51.8509 | 31.7047 | -53.0045 | 70.1706 | 70.0928 | -53.0365 | -53.1006 | -0.07782 | -0.16937 | 0.10529 | 122.8546 | -0.16937 | 0 | -0.1831 | -0.19226 | -0.25635 | 0.10071 | 0.99335 | -0.16022 | 0.09613 | 0.022888 | 123.0194 | 122.731 | 61.0291 | -123.0835 | 123.0148 | 122.937 | 84.5489 | -123.1705
2887.0156 | 123.0194 | -53.5858 | 69.4153 | 0.045624 | 0.019626 | 0.068891 | 0.072867 | 0.12971 | 0.0020593 | -0.0045139 | 0.23636 | -0.0069898 | 0.06341 | 0.056971 | 0.0097626 | -0.012401 | 69.2047 | 69.3146 | 9.0134 | -53.7231 | 69.516 | -53.5995 | -53.714 | -52.5009 | 31.3705 | -53.7369 | 69.4885 | 69.4061 | -53.7827 | -53.8422 | -0.013733 | -0.12817 | 0.10071 | 122.9004 | -0.13733 | -0.009156 | -0.21057 | -0.19684 | -0.25635 | 0.073242 | 1.0849 | -0.15106 | 0.10529 | -0.009155 | 123.1018 | 122.7905 | 62.5992 | -123.1293 | 123.0743 | 122.9919 | 84.9564 | -123.2574
2888.0156 | 123.0377 | -53.2608 | 69.6716 | -0.0383 | 0.017703 | 0.068678 | 0.074149 | 0.12843 | 0.0020593 | -0.0055821 | 0.0074766 | -0.0089124 | 0.063623 | 0.056758 | 0.01019 | -0.010051 | 69.3924 | 69.5297 | 4.0009 | -53.5034 | 69.7083 | -53.4393 | -53.4988 | -52.3499 | 32.9132 | -53.4897 | 69.6762 | 69.6396 | -53.5034 | -53.5217 | -0.17853 | -0.23804 | 0.036621 | 122.7905 | -0.24262 | -0.004578 | -0.27924 | -0.24262 | -0.26093 | 0.004577 | 0.91095 | -0.22888 | 0.032044 | -0.032044 | 122.9691 | 122.6532 | 57.2617 | -123.1705 | 122.937 | 122.9004 | 86.174 | -123.1934
2889.0156 | 123.1522 | -53.3844 | 69.4931 | 0.21347 | 0.013644 | 0.070173 | 0.071372 | 0.12971 | -0.0017859 | -0.0040867 | -1.5794 | -0.010835 | 0.06341 | 0.054835 | 0.0059174 | -0.01176 | 69.3375 | 69.4839 | 3.4287 | -53.5995 | 69.516 | -53.5126 | -53.6041 | -52.3682 | 32.9407 | -53.4897 | 69.4839 | 69.4336 | -53.627 | -53.6453 | -0.12817 | -0.21973 | 0.022888 | 122.8683 | -0.21515 | 0.004578 | -0.15564 | -0.24262 | -0.26093 | -0.009155 | 1.0162 | -0.10529 | 0.15564 | -0.059509 | 122.9004 | 122.7219 | 56.813 | -123.0972 | 122.8683 | 122.818 | 86.3251 | -123.1384
2890.0156 | 123.0743 | -53.0548 | 69.8273 | 0.5339 | 0.018771 | 0.071455 | 0.073081 | 0.12864 | 0.00077755 | -0.0070773 | 0.15244 | -0.0065626 | 0.064905 | 0.056971 | 0.0086944 | -0.010905 | 69.7723 | 69.8639 | 2.1744 | -53.1601 | 70.0882 | -53.0411 | -53.1692 | -51.9974 | 33.3298 | -53.1876 | 69.9646 | 69.8593 | -53.2837 | -53.3066 | 0.013733 | -0.11444 | 0.26093 | 122.9187 | -0.10528 | 0.009155 | -0.054932 | -0.22888 | -0.25177 | 0.13733 | 1.0574 | -0.13275 | 0.11902 | 0.032043 | 123.143 | 122.8271 | 55.2292 | -122.9965 | 123.0194 | 122.9141 | 86.3846 | -123.1339
2891.0156 | 123.0972 | -53.6499 | 69.2642 | 0.16006 | 0.015567 | 0.069105 | 0.07244 | 0.12907 | 0.0018457 | -0.0045139 | 0.23636 | -0.0082716 | 0.062982 | 0.056117 | 0.007199 | -0.011546 | 69.2413 | 69.3558 | 1.9913 | -53.6911 | 69.516 | -53.595 | -53.6819 | -52.4918 | 32.373 | -53.7918 | 69.3741 | 69.3375 | -53.8513 | -53.8559 | 0.054931 | -0.032044 | 0.25177 | 123.0057 | -0.041199 | -0.009155 | -0.022888 | -0.20142 | -0.20599 | 0.10986 | 1.1581 | -0.14191 | 0.064087 | 0.073242 | 123.1659 | 122.8912 | 55.6412 | -122.9462 | 123.024 | 122.9874 | 86.0229 | -123.1201
2892.0156 | 123.0606 | -53.6911 | 69.2917 | -0.03067 | 0.017703 | 0.0706 | 0.073294 | 0.12928 | 0.0016321 | -0.0045139 | 0.030365 | -0.0086988 | 0.063196 | 0.057612 | 0.0091216 | -0.013255 | 68.9255 | 68.9896 | 2.0782 | -54.0207 | 69.1681 | -53.92 | -54.0161 | -52.8076 | 32.1808 | -53.9474 | 69.1589 | 69.1315 | -53.9978 | -53.9978 | -0.22888 | -0.32501 | -0.1236 | 122.6807 | -0.32959 | -0.004578 | -0.36621 | -0.3067 | -0.3067 | -0.13275 | 0.88348 | -0.25635 | 0.050354 | -0.16022 | 122.8592 | 122.6166 | 55.7693 | -123.3078 | 122.85 | 122.8226 | 85.8719 | -123.2895
2893.0156 | 123.0194 | -53.6499 | 69.3054 | 0.015106 | 0.019412 | 0.070814 | 0.068594 | 0.128 | 0.00099115 | -0.0049411 | 0.076141 | -0.011689 | 0.065119 | 0.058467 | 0.0086944 | -0.011974 | 69.1177 | 69.2093 | 2.2568 | -53.7598 | 69.4565 | -53.6545 | -53.7643 | -52.6611 | 32.3868 | -53.8559 | 69.3649 | 69.2963 | -53.8788 | -53.8925 | -0.004578 | -0.11444 | 0.15106 | 122.8592 | -0.10986 | 0.004577 | -0.18768 | -0.22888 | -0.24262 | 0.059509 | 0.98877 | -0.20599 | 0.036621 | -0.009155 | 123.1064 | 122.7676 | 55.9067 | -123.0698 | 123.0148 | 122.9462 | 86.0367 | -123.1979
2894.0156 | 123.1338 | -54.0161 | 68.8568 | 0.15244 | 0.014071 | 0.071027 | 0.068167 | 0.12971 | -0.0024269 | -0.0062229 | 1.602 | -0.0099806 | 0.061273 | 0.055476 | 0.007199 | -0.010478 | 68.8751 | 69.0308 | 2.6138 | -54.0436 | 69.0399 | -53.9795 | -54.0619 | -52.977 | 32.1991 | -54.1855 | 68.9026 | 68.8385 | -54.2221 | -54.2633 | 0.036621 | -0.045777 | 0.1831 | 123.0469 | -0.027466 | 0.018311 | 0.01831 | -0.20599 | -0.24719 | 0.045776 | 1.0391 | -0.16937 | 0.07782 | -0.018311 | 123.056 | 122.8912 | 56.6299 | -122.9187 | 122.9187 | 122.8546 | 86.2152 | -123.1201
2895.0156 | 123.0286 | -53.2745 | 69.6762 | -0.00015269 | 0.020053 | 0.069959 | 0.070944 | 0.12822 | 0.00013675 | -0.0051547 | 0.037995 | -0.0084852 | 0.066828 | 0.05633 | 0.01019 | -0.012187 | 69.5938 | 69.6899 | 1.918 | -53.3752 | 69.8364 | -53.2425 | -53.3615 | -52.2812 | 32.6065 | -53.4988 | 69.754 | 69.6945 | -53.508 | -53.5492 | 0.032043 | -0.086975 | 0.16022 | 122.9645 | -0.10071 | -0.013733 | -0.082397 | -0.23346 | -0.27466 | 0.07782 | 0.99335 | -0.2243 | 0.050354 | 0.018311 | 123.111 | 122.8683 | 55.1926 | -123.0377 | 123.0286 | 122.9691 | 85.881 | -123.2254
2896.0156 | 122.9919 | -53.5446 | 69.4153 | 0.053253 | 0.020267 | 0.069105 | 0.07479 | 0.12907 | 0.00099115 | -0.0057957 | 0.09903 | -0.0067762 | 0.066828 | 0.058253 | 0.0082672 | -0.013042 | 68.9713 | 69.0811 | 1.6067 | -53.9017 | 69.3329 | -53.7781 | -53.8742 | -52.5284 | 32.4188 | -53.6453 | 69.4702 | 69.4473 | -53.7643 | -53.801 | -0.23346 | -0.32959 | -0.082397 | 122.6257 | -0.35705 | -0.027465 | -0.44403 | -0.21973 | -0.25635 | 0.054932 | 1.0162 | -0.10071 | 0.15564 | 0.032044 | 122.8775 | 122.5159 | 55.1514 | -123.2895 | 123.0148 | 122.9919 | 85.9634 | -123.2162
2897.0156 | 123.0743 | -53.6545 | 69.2596 | 0.15244 | 0.017489 | 0.069105 | 0.073081 | 0.12758 | 0.00035035 | -0.0066501 | 0.25162 | -0.0078442 | 0.065546 | 0.057826 | 0.0063446 | -0.012614 | 68.8934 | 69.0262 | 2.1378 | -53.9886 | 69.2368 | -53.8742 | -53.9749 | -52.684 | 32.2495 | -53.8376 | 69.278 | 69.2413 | -53.8971 | -53.9291 | -0.21973 | -0.32044 | -0.022889 | 122.6807 | -0.33417 | -0.013732 | -0.36621 | -0.24262 | -0.27466 | 0.01831 | 0.97046 | -0.1831 | 0.091553 | -0.018311 | 122.8912 | 122.5479 | 55.7922 | -123.2346 | 122.9324 | 122.8958 | 85.9039 | -123.1888
2898.0156 | 123.0469 | -53.3707 | 69.5526 | 0.12192 | 0.01813 | 0.071027 | 0.072226 | 0.12886 | 0.00099115 | -0.0075047 | 0.2211 | -0.008058 | 0.065119 | 0.055903 | 0.0069854 | -0.011333 | 69.0903 | 69.2139 | 1.7899 | -53.7506 | 69.4473 | -53.6591 | -53.7415 | -52.4048 | 32.5241 | -53.3661 | 69.5892 | 69.5526 | -53.6133 | -53.6179 | -0.28839 | -0.37079 | -0.10528 | 122.5845 | -0.37994 | -0.009155 | -0.46234 | -0.24261 | -0.24719 | 0.036621 | 0.96588 | 0.004578 | 0.25177 | 0 | 122.818 | 122.4609 | 55.1605 | -123.2941 | 122.9599 | 122.9233 | 85.8948 | -123.1705
2899.0156 | 123.1567 | -54.3594 | 68.4906 | 0.20584 | 0.014499 | 0.066328 | 0.070731 | 0.13057 | 0.00013675 | -0.0075047 | 0.28214 | -0.0099806 | 0.062342 | 0.057398 | 0.0076264 | -0.012828 | 68.4677 | 68.5364 | 1.6342 | -54.4418 | 68.7332 | -54.3457 | -54.4281 | -53.2608 | 31.7368 | -54.6021 | 68.6096 | 68.5455 | -54.5929 | -54.6204 | 0.013733 | -0.068665 | 0.24261 | 122.8958 | -0.082397 | -0.013732 | -0.022889 | -0.23346 | -0.26093 | 0.11902 | 1.0986 | -0.24262 | 0.01831 | 0.054931 | 123.0927 | 122.8271 | 55.9937 | -122.9187 | 122.9691 | 122.905 | 86.0962 | -123.111
2900.0156 | 123.0377 | -53.8559 | 69.0582 | 0.030365 | 0.016421 | 0.070814 | 0.07009 | 0.12843 | 0.00056395 | -0.0064365 | 0.045624 | -0.011476 | 0.064905 | 0.05868 | 0.0086944 | -0.013683 | 68.9713 | 69.0399 | 1.7807 | -53.9703 | 69.2368 | -53.8925 | -53.9703 | -52.8214 | 32.0847 | -54.0298 | 69.1635 | 69.1544 | -54.0482 | -54.1031 | -0.036621 | -0.11444 | 0.17853 | 122.8958 | -0.11444 | 0 | -0.086976 | -0.19226 | -0.24719 | 0.10528 | 1.0345 | -0.17395 | 0.073242 | 0.09613 | 123.0927 | 122.8271 | 55.6366 | -123.0286 | 123.0194 | 123.0103 | 85.9406 | -123.1613
2901.0156 | 123.0331 | -54.6982 | 68.2388 | 1.4799 | 0.01514 | 0.071882 | 0.073294 | 0.13035 | 0.00013675 | -0.0051547 | 0.17532 | -0.0061352 | 0.064478 | 0.056758 | 0.008908 | -0.010692 | 68.2297 | 68.2526 | 1.9409 | -54.7302 | 68.5181 | -54.5975 | -54.6982 | -53.508 | 31.3477 | -54.8904 | 68.4357 | 68.3578 | -54.8538 | -54.9042 | 0.10071 | 0 | 0.27923 | 122.9507 | -0.032044 | -0.032044 | -0.009156 | -0.15564 | -0.20599 | 0.19684 | 1.1902 | -0.19226 | 0.013733 | 0.11902 | 123.2162 | 122.9279 | 56.6391 | -122.937 | 123.1338 | 123.056 | 86.0458 | -123.143
2902.0156 | 123.0194 | -53.4164 | 69.548 | 0.022736 | 0.018985 | 0.069959 | 0.072867 | 0.12736 | 0.00035035 | -0.0051547 | 0.030365 | -0.0095532 | 0.064691 | 0.056971 | 0.01019 | -0.010692 | 69.4199 | 69.4336 | 2.092 | -53.627 | 69.6487 | -53.4439 | -53.5446 | -52.3682 | 32.3822 | -53.6453 | 69.6579 | 69.5984 | -53.6133 | -53.6591 | -0.027466 | -0.12817 | 0.10071 | 122.85 | -0.21057 | -0.082397 | -0.12817 | -0.19684 | -0.24262 | 0.10986 | 1.0483 | -0.22888 | 0.013733 | 0.050354 | 123.0652 | 122.8363 | 55.5084 | -123.0927 | 123.0743 | 123.0148 | 85.7986 | -123.2071
2903.0156 | 123.0789 | -53.7598 | 69.1315 | 0.13718 | 0.017062 | 0.071027 | 0.070944 | 0.12864 | -0.0026405 | -0.0062229 | 0.24399 | -0.007417 | 0.064691 | 0.057612 | 0.0084808 | -0.011974 | 69.2047 | 69.2917 | 1.9455 | -53.7781 | 69.4473 | -53.6453 | -53.7827 | -52.6657 | 32.2495 | -53.9566 | 69.2642 | 69.191 | -53.9612 | -54.0024 | 0.11444 | -0.022888 | 0.31586 | 123.0515 | -0.01831 | 0.004578 | 0.073242 | -0.20142 | -0.24261 | 0.13275 | 1.0941 | -0.19684 | 0.045776 | 0.059509 | 123.2071 | 122.9645 | 55.7053 | -122.9141 | 123.024 | 122.9507 | 86.0092 | -123.1338
2904.0156 | 123.1201 | -54.1763 | 68.7515 | 0.11429 | 0.011508 | 0.070387 | 0.067526 | 0.12864 | -0.0043495 | -0.0066501 | 0.32028 | -0.009126 | 0.061273 | 0.055903 | 0.0052764 | -0.010265 | 68.6554 | 68.8248 | 1.8723 | -54.2267 | 68.8751 | -54.158 | -54.2999 | -53.1464 | 31.897 | -54.3732 | 68.6966 | 68.6737 | -54.4327 | -54.4739 | 0.018311 | -0.1236 | 0.1236 | 123.0011 | -0.050354 | 0.073242 | -0.09613 | -0.25635 | -0.29755 | -0.054932 | 1.03 | -0.19684 | 0.10071 | -0.07782 | 123.0515 | 122.8317 | 56.0486 | -123.0515 | 122.8729 | 122.85 | 86.0733 | -123.2254
2905.0156 | 123.0698 | -53.7231 | 69.1544 | 0.083771 | 0.018558 | 0.069532 | 0.074149 | 0.12886 | -7.6852e-05 | -0.0055821 | 0.20584 | -0.008058 | 0.065546 | 0.054621 | 0.0086944 | -0.012828 | 69.6716 | 69.7403 | 2.3392 | -53.2562 | 69.96 | -53.1418 | -53.2425 | -52.6337 | 32.2083 | -54.1443 | 69.31 | 69.223 | -53.9658 | -53.9841 | 0.58136 | 0.48065 | 0.80566 | 123.4634 | 0.46692 | -0.013733 | 0.51727 | -0.24261 | -0.26093 | 0.15564 | 1.0895 | -0.42114 | -0.16022 | 0.068664 | 123.6832 | 123.3948 | 56.0623 | -122.3969 | 123.0331 | 122.9462 | 85.9314 | -123.1384
2906.0156 | 123.0698 | -53.6636 | 69.2825 | 0.11429 | 0.01578 | 0.068678 | 0.071585 | 0.12928 | 0.00035035 | -0.0075047 | 0.20584 | -0.007417 | 0.064264 | 0.057826 | 0.0069854 | -0.010478 | 69.1452 | 69.2459 | 2.179 | -53.7231 | 69.4656 | -53.627 | -53.746 | -52.597 | 30.7663 | -53.8147 | 69.3649 | 69.3237 | -53.8651 | -53.9154 | 0.036621 | -0.082398 | 0.1831 | 122.9095 | -0.05951 | 0.022888 | -0.13733 | -0.20142 | -0.25177 | 0.082397 | 1.0666 | -0.15106 | 0.10071 | 0.041198 | 123.1293 | 122.8088 | 55.8426 | -123.0286 | 123.0286 | 122.9874 | 84.4299 | -123.1979
2907.0156 | 123.0515 | -53.9474 | 68.9575 | -0.19089 | 0.01813 | 0.069105 | 0.071585 | 0.12928 | 0.0014185 | -0.0045139 | 0.18295 | -0.0089124 | 0.064478 | 0.057826 | 0.0093354 | -0.011546 | 68.9484 | 69.0628 | 2.3621 | -53.9337 | 69.2825 | -53.833 | -53.9383 | -52.977 | 28.5278 | -54.1672 | 69.072 | 69.017 | -54.126 | -54.1672 | 0.11444 | 0.009156 | 0.32501 | 123.0103 | 0.013733 | 0.004577 | -0.009156 | -0.17853 | -0.21973 | 0.11444 | 0.97046 | -0.21973 | 0 | 0.059509 | 123.23 | 122.8958 | 56.3095 | -122.8958 | 123.0194 | 122.9645 | 82.4753 | -123.1247
2908.0156 | 123.0515 | -52.5742 | 70.3674 | -0.03067 | 0.016421 | 0.069319 | 0.075217 | 0.13057 | 0.0022729 | -0.0055821 | 0.068512 | -0.0097668 | 0.06341 | 0.055476 | 0.0086944 | -0.014323 | 70.0745 | 70.134 | 2.6184 | -52.8122 | 70.3903 | -52.6703 | -52.7802 | -51.5671 | 28.9124 | -52.7206 | 70.4498 | 70.3995 | -52.7527 | -52.8076 | -0.09613 | -0.20599 | 0.022888 | 122.7081 | -0.23804 | -0.032044 | -0.29297 | -0.17853 | -0.23346 | 0.082397 | 1.0071 | -0.14648 | 0.086975 | 0.032043 | 122.9645 | 122.6486 | 55.1926 | -123.1476 | 123.024 | 122.9736 | 81.4865 | -123.175
2909.0156 | 123.0881 | -54.0207 | 68.8293 | 0.19821 | 0.014926 | 0.069746 | 0.072226 | 0.1295 | -0.00029045 | -0.0045139 | 0.21347 | -0.0078442 | 0.064905 | 0.058467 | 0.0097626 | -0.01176 | 68.7881 | 68.8843 | 2.655 | -54.1534 | 69.0445 | -54.0344 | -54.1306 | -52.8763 | 27.5803 | -54.1443 | 68.985 | 68.9346 | -54.2175 | -54.2587 | -0.013733 | -0.10986 | 0.21515 | 122.905 | -0.13275 | -0.022888 | -0.041199 | -0.19684 | -0.23804 | 0.15564 | 1.1444 | -0.1236 | 0.11444 | 0.10528 | 123.0652 | 122.8088 | 56.6757 | -122.9599 | 123.0057 | 122.9553 | 81.601 | -123.0881
2910.0156 | 123.0423 | -52.7573 | 70.1431 | 0.0914 | 0.02283 | 0.066541 | 0.078848 | 0.13035 | 0.0037683 | -0.0085727 | 0.053253 | -0.0076306 | 0.063623 | 0.058253 | 0.0080536 | -0.012614 | 69.8914 | 70.0882 | 2.449 | -52.9816 | 70.2759 | -52.8488 | -52.9129 | -51.7502 | 28.3447 | -52.8671 | 70.3079 | 70.2301 | -52.9633 | -53.0182 | -0.091553 | -0.15564 | 0.13275 | 122.8455 | -0.2243 | -0.068664 | -0.25177 | -0.20599 | -0.26093 | 0.16479 | 1.0071 | -0.10986 | 0.15106 | 0.086976 | 123.0331 | 122.6486 | 55.2063 | -123.056 | 123.0652 | 122.9874 | 81.102 | -123.1613
2911.0156 | 123.0972 | -53.8651 | 69.017 | 0.14481 | 0.014926 | 0.070173 | 0.07009 | 0.12886 | -7.6852e-05 | -0.0028049 | 0.24399 | -0.0067762 | 0.065119 | 0.058253 | 0.0076264 | -0.012401 | 68.8568 | 68.9346 | 2.4399 | -54.0848 | 69.1406 | -53.9566 | -54.0482 | -52.7985 | 27.6443 | -54.0344 | 69.1269 | 69.0628 | -54.0482 | -54.0848 | -0.091553 | -0.18311 | 0.1236 | 122.7997 | -0.21973 | -0.036621 | -0.16022 | -0.18311 | -0.21973 | 0.10986 | 1.0666 | -0.16937 | 0.050354 | 0.045776 | 123.0057 | 122.7219 | 56.3049 | -123.0652 | 122.9919 | 122.9279 | 81.5094 | -123.1018
2912.0156 | 122.9874 | -53.7231 | 69.1956 | 0.015106 | 0.017703 | 0.069532 | 0.07244 | 0.12907 | 0.0027001 | -0.0081455 | 0.20584 | -0.0086988 | 0.066614 | 0.05398 | 0.0069854 | -0.013255 | 69.0033 | 69.0765 | 2.4078 | -53.9246 | 69.3054 | -53.833 | -53.9337 | -52.8168 | 27.3056 | -53.8834 | 69.3192 | 69.2871 | -53.9246 | -53.952 | -0.10986 | -0.21057 | 0.10986 | 122.7997 | -0.20142 | 0.009155 | -0.19226 | -0.20142 | -0.22888 | 0.1236 | 0.90637 | -0.16022 | 0.068664 | 0.091552 | 123.0286 | 122.7264 | 56.131 | -123.1293 | 123.0423 | 123.0103 | 81.0287 | -123.1476
2913.0156 | 123.0606 | -53.6682 | 69.3008 | 0.12192 | 0.018558 | 0.068891 | 0.072867 | 0.13078 | 0.00077755 | -0.0049411 | 0.28976 | -0.0095532 | 0.064691 | 0.056758 | 0.0059174 | -0.012401 | 69.1589 | 69.2047 | 2.6276 | -53.9932 | 69.4061 | -53.6911 | -53.7872 | -52.6978 | 27.5482 | -53.801 | 69.3924 | 69.3283 | -53.8376 | -53.9108 | -0.022888 | -0.11902 | 0.10529 | 122.8729 | -0.32501 | -0.20599 | -0.14191 | -0.16937 | -0.24262 | 0.091553 | 0.97046 | -0.13275 | 0.10986 | 0.027466 | 123.0743 | 122.8271 | 56.2958 | -123.0881 | 123.0606 | 122.9965 | 81.2164 | -123.2117
2914.0156 | 123.111 | -54.4373 | 68.4265 | 0.22873 | 0.015994 | 0.069319 | 0.070517 | 0.12907 | -0.0022131 | -0.0057957 | 0.34317 | -0.011049 | 0.064051 | 0.056544 | 0.0069854 | -0.012614 | 68.4082 | 68.5364 | 2.0966 | -54.5334 | 68.5959 | -54.4556 | -54.5563 | -53.3386 | 26.9394 | -54.5013 | 68.5135 | 68.4677 | -54.6478 | -54.6753 | -0.01831 | -0.11902 | 0.16937 | 122.9736 | -0.09613 | 0.022888 | -0.018311 | -0.21057 | -0.23804 | 0.086975 | 1.0986 | -0.064087 | 0.17395 | 0.041198 | 123.0331 | 122.8455 | 56.5338 | -122.9828 | 122.9507 | 122.905 | 81.3766 | -123.1018
2915.0156 | 123.0194 | -53.7186 | 69.2505 | 0.14481 | 0.015353 | 0.0706 | 0.073935 | 0.12843 | 0.00077755 | -0.0064365 | 0.22873 | -0.010194 | 0.065546 | 0.056758 | 0.008908 | -0.012187 | 69.5572 | 69.6304 | 2.0233 | -53.3661 | 69.8776 | -53.2059 | -53.3615 | -52.7252 | 27.4063 | -54.0115 | 69.3146 | 69.2688 | -53.9062 | -53.9246 | 0.5127 | 0.35706 | 0.62714 | 123.349 | 0.35248 | -0.004578 | 0.3067 | -0.18768 | -0.20599 | 0.064087 | 0.99335 | -0.29297 | -0.086975 | 0.018311 | 123.5962 | 123.2758 | 55.7419 | -122.612 | 123.0331 | 122.9874 | 81.1249 | -123.175
2916.0156 | 123.0057 | -53.627 | 69.2871 | 0.060882 | 0.016208 | 0.069532 | 0.070517 | 0.12971 | -7.6852e-05 | -0.0062229 | 0.0914 | -0.0093396 | 0.062555 | 0.05633 | 0.0091216 | -0.01176 | 69.4061 | 69.4839 | 2.3483 | -53.5446 | 69.6945 | -53.476 | -53.6179 | -52.6611 | 27.3514 | -53.9337 | 69.3924 | 69.3695 | -53.7964 | -53.8376 | 0.15106 | 0.009155 | 0.40741 | 123.111 | 0.082397 | 0.073242 | 0.11902 | -0.16937 | -0.21057 | 0.10529 | 0.96588 | -0.3067 | -0.096131 | 0.082398 | 123.3215 | 123.0331 | 55.9753 | -122.905 | 123.0194 | 122.9965 | 80.9784 | -123.1247
2917.0156 | 123.0515 | -53.8422 | 69.136 | 0.12955 | 0.017917 | 0.069532 | 0.07479 | 0.13121 | 0.00077755 | -0.0083591 | 0.0914 | -0.0065626 | 0.067255 | 0.05398 | 0.00549 | -0.0087692 | 68.8248 | 68.9163 | 2.6688 | -54.0756 | 69.1818 | -53.9703 | -54.0207 | -52.7664 | 29.155 | -53.9383 | 69.1498 | 69.0857 | -54.071 | -54.1168 | -0.12817 | -0.17853 | 0.045777 | 122.7585 | -0.23346 | -0.054932 | -0.31128 | -0.22888 | -0.27466 | 0.013733 | 1.0757 | -0.09613 | 0.17853 | -0.050354 | 123.024 | 122.6669 | 56.5109 | -123.1567 | 122.9919 | 122.9279 | 82.9971 | -123.2529
2918.0156 | 123.0606 | -54.3869 | 68.5135 | 0.16006 | 0.015353 | 0.069746 | 0.070944 | 0.12864 | -0.0022131 | -0.0049411 | 0.19058 | -0.0086988 | 0.065973 | 0.056544 | 0.0084808 | -0.010478 | 68.3487 | 68.454 | 2.2568 | -54.6021 | 68.6646 | -54.451 | -54.538 | -53.4073 | 28.5553 | -54.5425 | 68.5684 | 68.5684 | -54.6066 | -54.6341 | -0.064087 | -0.15106 | 0.15106 | 122.8409 | -0.21515 | -0.064087 | -0.1648 | -0.21973 | -0.24719 | 0.054931 | 0.97961 | -0.15564 | 0.091552 | 0.054931 | 123.0515 | 122.7356 | 56.6437 | -123.0515 | 122.9553 | 122.9553 | 82.9422 | -123.1476
2919.0156 | 123.1338 | -53.5126 | 69.3466 | 0.20584 | 0.015353 | 0.070387 | 0.069235 | 0.12715 | -0.0037085 | -0.0055821 | 0.16006 | -0.010621 | 0.065119 | 0.058467 | 0.0063446 | -0.01176 | 69.191 | 69.342 | 2.243 | -53.7186 | 69.3604 | -53.6728 | -53.7323 | -52.5146 | 27.887 | -53.5629 | 69.3787 | 69.3649 | -53.7231 | -53.7552 | -0.16022 | -0.21973 | 0.013733 | 122.8546 | -0.20599 | 0.013733 | -0.15564 | -0.21057 | -0.24261 | 0.032043 | 0.99793 | -0.050354 | 0.19226 | 0.01831 | 122.8729 | 122.7036 | 55.7556 | -123.0789 | 122.8912 | 122.8775 | 81.3995 | -123.1018
2920.0156 | 123.143 | -54.3915 | 68.5822 | 0.12955 | 0.018558 | 0.06761 | 0.073294 | 0.12843 | 0.0014185 | -0.0057957 | 0.16769 | -0.007417 | 0.065332 | 0.056117 | 0.0086944 | -0.012828 | 68.3716 | 68.4265 | 1.9592 | -54.5197 | 68.7012 | -54.4235 | -54.5151 | -53.4805 | 26.8387 | -54.6387 | 68.6508 | 68.5822 | -54.5883 | -54.657 | -0.032044 | -0.1236 | 0.11902 | 122.818 | -0.12817 | -0.004577 | -0.21057 | -0.19684 | -0.2655 | 0.068665 | 0.91095 | -0.24719 | 0.01831 | 0 | 123.0927 | 122.7631 | 56.3507 | -123.0972 | 123.0423 | 122.9736 | 81.2302 | -123.2391
2921.0156 | 123.0377 | -53.6682 | 69.2642 | 0.022736 | 0.017917 | 0.06825 | 0.069449 | 0.13121 | 0.0016321 | -0.0060093 | -0.023041 | -0.0082716 | 0.065759 | 0.059962 | 0.0076264 | -0.010692 | 69.191 | 69.2505 | 2.5818 | -53.8147 | 69.429 | -53.6957 | -53.8101 | -52.6932 | 27.4292 | -53.8055 | 69.3466 | 69.2963 | -53.8925 | -53.92 | -0.027466 | -0.14191 | 0.16479 | 122.9187 | -0.14648 | -0.004577 | -0.073242 | -0.2243 | -0.25177 | 0.082398 | 0.97504 | -0.13733 | 0.11444 | 0.032044 | 123.0972 | 122.8592 | 56.25 | -123.0743 | 123.0148 | 122.9645 | 81.0974 | -123.1842
2922.0156 | 123.0377 | -53.1372 | 69.7906 | 0.099029 | 0.020694 | 0.065901 | 0.075003 | 0.13014 | -0.00071785 | -0.0055821 | 0.12192 | -0.0099806 | 0.064691 | 0.056544 | 0.0067718 | -0.013469 | 69.4427 | 69.7815 | 2.1561 | -53.4073 | 69.8593 | -53.2471 | -53.3524 | -52.1713 | 28.5095 | -53.3569 | 69.8318 | 69.7769 | -53.3798 | -53.3844 | -0.10986 | -0.21515 | 0.068665 | 122.9187 | -0.27008 | -0.054932 | -0.3479 | -0.24262 | -0.24719 | 0.041199 | 0.96588 | -0.21973 | 0.027465 | -0.013732 | 122.9965 | 122.58 | 55.2933 | -123.143 | 122.9691 | 122.9141 | 81.6467 | -123.175
2923.0156 | 123.024 | -54.6707 | 68.2388 | 0.12192 | 0.017276 | 0.069532 | 0.072653 | 0.12843 | -0.00050425 | -0.0070773 | -0.62576 | -0.0086988 | 0.065546 | 0.053767 | 0.0074126 | -0.010905 | 68.1976 | 67.6804 | 1.9272 | -54.7943 | 68.3533 | -54.7714 | -54.8584 | -53.6957 | 27.2324 | -54.9133 | 68.2938 | 68.2297 | -54.9088 | -54.9362 | -0.10071 | -0.18768 | 0.11444 | 122.3511 | -0.1236 | 0.064086 | -0.041199 | -0.23804 | -0.2655 | 0.054931 | 0.97504 | -0.24262 | 0.022888 | -0.009156 | 123.024 | 122.8683 | 56.5979 | -123.0972 | 122.9645 | 122.9004 | 81.9031 | -123.175
2924.0156 | 123.0972 | -54.3777 | 68.5272 | 0.14481 | 0.014285 | 0.067823 | 0.072867 | 0.13057 | -0.00029045 | -0.0040867 | 0.19058 | -0.009126 | 0.065759 | 0.05633 | 0.0076264 | -0.012401 | 68.4036 | 68.5272 | 2.0874 | -54.4785 | 68.7332 | -54.3915 | -54.4876 | -53.2837 | 27.4109 | -54.6707 | 68.6188 | 68.5684 | -54.5929 | -54.6204 | -0.013732 | -0.10986 | 0.20599 | 122.905 | -0.10071 | 0.009155 | -0.1236 | -0.21515 | -0.24261 | 0.091552 | 1.0941 | -0.29297 | -0.050354 | 0.041198 | 123.111 | 122.7814 | 56.4651 | -123.0148 | 122.9965 | 122.9462 | 81.7886 | -123.1476
2925.0156 | 123.0515 | -53.9337 | 69.017 | 0.045624 | 0.016635 | 0.067396 | 0.07244 | 0.13099 | -0.0017859 | -0.0060093 | 0.18295 | -0.007417 | 0.064691 | 0.056758 | 0.0084808 | -0.01176 | 68.8065 | 68.9163 | 2.6184 | -54.0985 | 69.1315 | -54.0024 | -54.0939 | -52.8717 | 27.4841 | -54.0894 | 69.0903 | 69.0353 | -54.1214 | -54.1672 | -0.068664 | -0.16022 | 0.11444 | 122.85 | -0.1648 | -0.004578 | -0.21057 | -0.18768 | -0.23346 | 0.073242 | 1.062 | -0.15564 | 0.07782 | 0.01831 | 123.0652 | 122.7402 | 56.5521 | -123.111 | 123.024 | 122.9691 | 81.4178 | -123.1842
2926.0156 | 123.0286 | -54.3503 | 68.5822 | 0.28213 | 0.013858 | 0.071455 | 0.069663 | 0.12907 | -7.6852e-05 | -0.0064365 | 0.26688 | -0.0084852 | 0.065973 | 0.057612 | 0.0076264 | -0.012614 | 68.2983 | 68.3029 | 2.5131 | -54.6433 | 68.5822 | -54.5288 | -54.6387 | -53.3615 | 27.2781 | -54.4556 | 68.6279 | 68.5822 | -54.6066 | -54.6387 | -0.17853 | -0.28839 | 0 | 122.6532 | -0.29297 | -0.004578 | -0.28381 | -0.25635 | -0.28839 | 0.045777 | 0.98877 | -0.10528 | 0.18311 | 0 | 122.9324 | 122.6486 | 56.8634 | -123.2208 | 122.9782 | 122.9324 | 81.6284 | -123.2208
2927.0156 | 123.024 | -54.7485 | 68.2114 | 0.068512 | 0.018344 | 0.069532 | 0.071158 | 0.13078 | 0.0024865 | -0.0062229 | 0.12955 | -0.0050672 | 0.064051 | 0.057398 | 0.01019 | -0.013042 | 67.8268 | 67.9092 | 2.3529 | -55.0735 | 68.1519 | -54.9957 | -55.0415 | -53.8055 | 26.6785 | -55.0003 | 68.3166 | 68.2617 | -54.9179 | -55.0232 | -0.24719 | -0.29297 | -0.05951 | 122.6578 | -0.32501 | -0.032043 | -0.38452 | -0.16937 | -0.27466 | 0.10528 | 0.94299 | -0.25177 | 0.022888 | 0.050354 | 122.9004 | 122.5754 | 57.1014 | -123.2529 | 123.0652 | 123.0103 | 81.427 | -123.2346
2928.0156 | 123.0652 | -55.307 | 67.4789 | -0.37399 | 0.018344 | 0.06825 | 0.072653 | 0.12629 | 0.0020593 | -0.0064365 | -0.03067 | -0.005708 | 0.065119 | 0.055262 | 0.0080536 | -0.01176 | 67.6209 | 67.7032 | 2.7832 | -55.3024 | 67.868 | -55.22 | -55.3024 | -54.039 | 26.1108 | -55.2017 | 67.9092 | 67.8726 | -55.2979 | -55.394 | 0.086975 | 0.004578 | 0.3891 | 123.0103 | 0.004578 | 0 | 0.14191 | 0.009155 | -0.086975 | 0.4303 | 1.268 | 0.10529 | 0.19226 | 0.39368 | 123.175 | 122.9279 | 58.0902 | -122.7814 | 123.2162 | 123.1796 | 81.4178 | -122.8729
2929.0156 | 123.1293 | -54.1946 | 68.6691 | 0.25925 | 0.015353 | 0.071668 | 0.068594 | 0.12928 | -0.0043495 | -0.0070773 | 0.28214 | -0.012544 | 0.062342 | 0.055689 | 0.0076264 | -0.0098374 | 68.6646 | 68.8293 | 2.4307 | -54.2679 | 68.8568 | -54.1763 | -54.2862 | -53.0594 | 26.7975 | -54.3457 | 68.7698 | 68.7012 | -54.4327 | -54.4601 | 0.01831 | -0.091553 | 0.18768 | 123.024 | -0.073242 | 0.018311 | -0.004577 | -0.23804 | -0.2655 | 0.10071 | 1.1353 | -0.15106 | 0.11444 | 0.032044 | 123.0515 | 122.8592 | 56.6254 | -122.9553 | 122.9645 | 122.8958 | 80.9921 | -123.1293
2930.0156 | 123.0652 | -53.5995 | 69.3558 | 0.18295 | 0.017062 | 0.069532 | 0.072226 | 0.12864 | 0.00056395 | -0.0070773 | -0.28244 | -0.0095532 | 0.065546 | 0.059107 | 0.006131 | -0.013255 | 68.9987 | 69.0903 | 2.3254 | -53.8834 | 69.3375 | -53.7735 | -53.8559 | -52.5375 | 26.6876 | -53.801 | 69.3146 | 69.2642 | -53.8788 | -53.8559 | -0.17395 | -0.25635 | -0.018311 | 122.6898 | -0.28381 | -0.027466 | -0.35706 | -0.27924 | -0.25635 | -0.041199 | 1.062 | -0.20142 | 0.054932 | -0.091553 | 122.937 | 122.5983 | 55.925 | -123.2117 | 122.9141 | 122.8638 | 80.2872 | -123.2117
2931.0156 | 123.0148 | -54.2816 | 68.6325 | 0.030365 | 0.017489 | 0.069319 | 0.072653 | 0.12843 | 0.0027001 | -0.0034457 | 0.045624 | -0.0089124 | 0.063196 | 0.058253 | 0.0093354 | -0.01176 | 68.5867 | 68.7103 | 2.3254 | -54.2999 | 68.8568 | -54.2221 | -54.3274 | -53.0869 | 26.3901 | -54.5288 | 68.8019 | 68.7286 | -54.4785 | -54.5197 | 0.059509 | -0.045777 | 0.22431 | 122.9919 | -0.018311 | 0.027466 | -0.045776 | -0.19684 | -0.23804 | 0.16937 | 1.1948 | -0.24719 | -0.009156 | 0.096131 | 123.1384 | 122.8683 | 56.6071 | -122.9599 | 123.0835 | 123.0103 | 80.6717 | -123.1522
2932.0156 | 123.0789 | -53.4027 | 69.5755 | -0.099335 | 0.017489 | 0.070814 | 0.072012 | 0.12715 | 0.00099115 | -0.0036595 | -0.0077819 | -0.0095532 | 0.065973 | 0.054835 | 0.0086944 | -0.012401 | 69.3558 | 69.5206 | 2.5543 | -53.4714 | 69.6579 | -53.4439 | -53.5263 | -52.533 | 26.9257 | -53.4988 | 69.5709 | 69.5206 | -53.6819 | -53.6591 | -0.041199 | -0.1236 | 0.082398 | 122.9233 | -0.068665 | 0.054931 | -0.21973 | -0.27924 | -0.25635 | -0.004577 | 0.86975 | -0.09613 | 0.16022 | -0.054931 | 123.0606 | 122.7585 | 55.957 | -123.1018 | 122.9736 | 122.9233 | 80.3284 | -123.2346
2933.0156 | 123.056 | -53.2928 | 69.6259 | 0.44998 | 0.017062 | 0.069746 | 0.073935 | 0.12779 | 0.0012047 | -0.0081455 | -0.03067 | -0.0082716 | 0.065332 | 0.05868 | 0.0080536 | -0.01176 | 69.5572 | 69.6899 | 2.3804 | -53.3752 | 69.8181 | -53.2928 | -53.3981 | -52.3453 | 26.8341 | -53.421 | 69.7449 | 69.6579 | -53.5126 | -53.5492 | 0 | -0.10528 | 0.19226 | 122.9828 | -0.082397 | 0.022888 | -0.068664 | -0.21973 | -0.25635 | 0.11902 | 0.94757 | -0.12817 | 0.12817 | 0.032044 | 123.111 | 122.85 | 55.6732 | -123.024 | 123.0377 | 122.9507 | 80.127 | -123.175
2934.0312 | 123.1567 | -54.5151 | 68.3945 | -0.14511 | 0.010013 | 0.071027 | 0.070517 | 0.12822 | -0.0071265 | -0.010282 | -0.099335 | -0.012758 | 0.055292 | 0.056544 | 0.009549 | -0.0091966 | 68.3624 | 68.5272 | 2.8702 | -54.6204 | 68.541 | -54.5517 | -54.6433 | -53.5538 | 26.001 | -54.7073 | 68.4082 | 68.3304 | -54.7302 | -54.7668 | -0.036621 | -0.12817 | 0.14648 | 123.0423 | -0.10529 | 0.022889 | -0.032043 | -0.21515 | -0.25177 | 0.013733 | 0.9613 | -0.19226 | 0.05951 | -0.064087 | 123.056 | 122.8775 | 57.3853 | -123.0377 | 122.9233 | 122.8455 | 80.5161 | -123.1613
2935.0156 | 123.0469 | -53.7781 | 69.1452 | -0.19852 | 0.016635 | 0.071455 | 0.074149 | 0.12779 | 0.00056395 | -0.0081455 | -0.16037 | -0.011476 | 0.064051 | 0.057612 | 0.0069854 | -0.013255 | 68.9255 | 69.0537 | 2.6825 | -53.9978 | 69.2276 | -53.9017 | -54.039 | -52.8076 | 26.3672 | -54.0619 | 69.191 | 69.0857 | -54.0482 | -54.0756 | -0.1236 | -0.26093 | 0.082397 | 122.8317 | -0.21973 | 0.041198 | -0.21973 | -0.27008 | -0.29755 | 0.045776 | 0.97046 | -0.28381 | 0.013733 | -0.05951 | 123.0057 | 122.7036 | 56.4606 | -123.1842 | 122.9691 | 122.8638 | 80.1453 | -123.2208
2936.0156 | 123.0743 | -54.158 | 68.7698 | -0.15274 | 0.015994 | 0.070814 | 0.072653 | 0.12864 | -0.00093145 | -0.0055821 | -0.18326 | -0.010408 | 0.065332 | 0.056758 | 0.0067718 | -0.011333 | 68.8248 | 68.985 | 2.623 | -54.0527 | 69.1589 | -53.9841 | -54.1031 | -52.9175 | 25.9918 | -54.1626 | 69.0537 | 68.9484 | -54.2313 | -54.2953 | 0.17395 | 0.054932 | 0.3891 | 123.143 | 0.10529 | 0.050354 | 0.054932 | -0.073242 | -0.13733 | 0.28381 | 1.2405 | -0.004578 | 0.13275 | 0.17853 | 123.317 | 122.9828 | 56.781 | -122.8729 | 123.2117 | 123.1064 | 80.1498 | -123.0652
2937.0156 | 123.0377 | -54.2679 | 68.7149 | -0.076447 | 0.020053 | 0.06761 | 0.074362 | 0.12971 | -7.6852e-05 | -0.0057957 | -0.015411 | -0.0095532 | 0.066187 | 0.057185 | 0.0074126 | -0.013896 | 68.541 | 68.6462 | 2.5314 | -54.4052 | 68.8065 | -54.2953 | -54.3961 | -53.2516 | 25.6439 | -54.5105 | 68.7561 | 68.6737 | -54.483 | -54.5105 | -0.027466 | -0.12817 | 0.091553 | 122.9141 | -0.13733 | -0.009155 | -0.17395 | -0.21515 | -0.24262 | 0.041199 | 1.0162 | -0.24262 | 0 | -0.041199 | 123.0743 | 122.8088 | 56.7993 | -123.111 | 123.024 | 122.9416 | 79.9118 | -123.2254
2938.0156 | 123.111 | -54.8859 | 68.0283 | -0.045929 | 0.015994 | 0.068464 | 0.073721 | 0.1295 | 0.0016321 | -0.0019505 | -0.061188 | -0.008058 | 0.065546 | 0.059962 | 0.0069854 | -0.013042 | 67.6849 | 67.9733 | 2.5864 | -55.0827 | 68.1015 | -55.0095 | -55.1239 | -53.8193 | 25.4013 | -55.0964 | 68.0511 | 68.0145 | -55.1285 | -55.1559 | -0.1236 | -0.23804 | 0.073242 | 122.8592 | -0.19684 | 0.041198 | -0.34332 | -0.24262 | -0.27008 | 0.022888 | 1.0666 | -0.21057 | 0.059509 | -0.013733 | 122.9874 | 122.5708 | 57.4722 | -123.1522 | 122.937 | 122.9004 | 80.2872 | -123.1842
2939.0312 | 123.0835 | -54.277 | 68.5867 | -1.3734 | 0.0095853 | 0.0706 | 0.069663 | 0.1295 | -0.0064857 | -0.011563 | 0.13718 | -0.011689 | 0.063623 | 0.05633 | 0.0048492 | -0.010265 | 68.3945 | 68.6371 | 2.5177 | -54.4464 | 68.7103 | -54.3503 | -54.483 | -53.1418 | 25.5478 | -54.3594 | 68.6508 | 68.6142 | -54.5059 | -54.5609 | -0.073242 | -0.20599 | 0.1236 | 122.9141 | -0.16937 | 0.036621 | -0.19226 | -0.22888 | -0.28381 | 0.064087 | 1.1353 | -0.082397 | 0.20142 | 0.027466 | 122.9874 | 122.6715 | 56.7947 | -123.0698 | 122.9279 | 122.8912 | 79.8248 | -123.1476
2940.0156 | 123.024 | -54.7623 | 68.1427 | -0.24429 | 0.011935 | 0.072523 | 0.075217 | 0.12864 | -0.0011451 | -0.0081455 | -0.023041 | -0.010621 | 0.063837 | 0.057826 | 0.007199 | -0.013255 | 68.0008 | 68.1702 | 2.8336 | -54.8996 | 68.367 | -54.776 | -54.8264 | -53.5904 | 25.3647 | -54.863 | 68.3166 | 68.2343 | -54.9545 | -54.9637 | -0.013733 | -0.064087 | 0.2243 | 122.9324 | -0.13733 | -0.073242 | -0.14191 | -0.19226 | -0.20142 | 0.17395 | 1.1719 | -0.10071 | 0.10071 | 0.091553 | 123.1293 | 122.7631 | 57.5958 | -122.9691 | 123.0789 | 122.9965 | 80.127 | -123.1064
2941.0156 | 123.0515 | -54.5837 | 68.3624 | -0.34348 | 0.01578 | 0.070814 | 0.076926 | 0.12822 | 0.00035035 | -0.0072911 | -0.14511 | -0.008058 | 0.063837 | 0.056117 | 0.0065582 | -0.011546 | 68.5822 | 68.7515 | 2.9205 | -54.277 | 68.9438 | -54.1946 | -54.2725 | -53.0823 | 26.0971 | -54.895 | 68.7241 | 68.5684 | -54.6616 | -54.7668 | 0.3891 | 0.31128 | 0.58136 | 123.3353 | 0.3067 | -0.004578 | 0.21973 | -0.07782 | -0.18311 | 0.36163 | 1.5015 | -0.31128 | -0.12817 | 0.20599 | 123.5275 | 123.1659 | 57.5043 | -122.6349 | 123.3078 | 123.1522 | 80.6808 | -123.1293
2942.0156 | 123.0469 | -54.3045 | 68.6234 | -0.23666 | 0.014499 | 0.069959 | 0.073721 | 0.12822 | -0.0017859 | -0.0087863 | -0.32059 | -0.0099806 | 0.065759 | 0.05868 | 0.0067718 | -0.011333 | 68.6234 | 68.7561 | 2.1011 | -54.5151 | 68.8293 | -54.3137 | -54.4418 | -53.2974 | 25.6165 | -54.538 | 68.7149 | 68.6371 | -54.5288 | -54.5471 | -0.009156 | -0.13733 | 0.20599 | 123.0606 | -0.21057 | -0.073243 | 0 | -0.22431 | -0.24262 | 0.091553 | 1.0071 | -0.23346 | 0.009155 | 0.013733 | 123.1338 | 122.9279 | 56.4056 | -123.0652 | 123.0194 | 122.9416 | 79.921 | -123.1705
2943.0156 | 123.0194 | -54.7577 | 68.2159 | -0.30533 | 0.014926 | 0.071455 | 0.072867 | 0.12993 | -0.0045631 | -0.0081455 | -0.17563 | -0.010835 | 0.065119 | 0.058039 | 0.0048492 | -0.011333 | 67.7261 | 67.9184 | 2.1606 | -55.1468 | 68.0786 | -55.0415 | -55.1285 | -53.7918 | 27.0905 | -55.0415 | 68.1152 | 68.0328 | -55.0507 | -55.069 | -0.28381 | -0.37079 | -0.13733 | 122.6761 | -0.3891 | -0.018311 | -0.48981 | -0.29297 | -0.31128 | -0.10071 | 0.96588 | -0.28381 | 0.027466 | -0.1831 | 122.8363 | 122.4838 | 56.9183 | -123.3444 | 122.8729 | 122.7905 | 81.8481 | -123.2849
2944.0312 | 123.1476 | -54.0527 | 68.8293 | 0.19821 | 0.014926 | 0.0706 | 0.06774 | 0.12544 | 0.0020593 | -0.0070773 | 0.2211 | -0.010621 | 0.063623 | 0.059321 | 0.009549 | -0.011546 | 68.7012 | 68.8751 | 2.4445 | -54.2633 | 68.9621 | -54.1214 | -54.213 | -52.8214 | 27.562 | -54.2953 | 68.8522 | 68.7836 | -54.277 | -54.3137 | -0.068665 | -0.16022 | 0.13275 | 122.9279 | -0.21057 | -0.050354 | -0.12817 | -0.22431 | -0.26093 | 0.022888 | 1.2314 | -0.24262 | 0.018311 | -0.045777 | 123.0148 | 122.7539 | 56.4972 | -123.0423 | 122.905 | 122.8363 | 81.6147 | -123.143
2945.0156 | 123.0194 | -53.3157 | 69.6259 | 0.060882 | 0.018771 | 0.06761 | 0.072867 | 0.12993 | 0.0044091 | -0.0051547 | 0.12955 | -0.0099806 | 0.064264 | 0.057185 | 0.0093354 | -0.01411 | 69.4748 | 69.5068 | 2.2247 | -53.5538 | 69.7678 | -53.4164 | -53.5126 | -52.1667 | 28.0426 | -53.6728 | 69.6396 | 69.5847 | -53.5583 | -53.595 | -0.10071 | -0.19684 | 0.14191 | 122.8226 | -0.23804 | -0.041199 | -0.15106 | -0.24262 | -0.27924 | 0.013733 | 1.149 | -0.35706 | -0.07782 | -0.041198 | 123.0835 | 122.7905 | 55.5405 | -123.1384 | 122.9553 | 122.9004 | 81.3583 | -123.2208
2946.0156 | 123.0423 | -53.6362 | 69.2459 | 0.44998 | 0.016208 | 0.06761 | 0.07479 | 0.128 | -0.00050425 | -0.0077183 | -0.168 | -0.0084852 | 0.067041 | 0.054835 | 0.0035674 | -0.0091966 | 69.4016 | 69.5572 | 2.7145 | -53.5172 | 69.7128 | -53.421 | -53.54 | -52.4002 | 26.9028 | -53.7186 | 69.4794 | 69.4061 | -53.7552 | -53.8376 | 0.21515 | 0.09613 | 0.46692 | 123.1934 | 0.11902 | 0.022888 | 0.15564 | -0.11902 | -0.20142 | 0.23346 | 1.236 | -0.082398 | 0.11902 | 0.16022 | 123.349 | 123.0377 | 56.3507 | -122.786 | 123.1155 | 123.0423 | 80.5389 | -123.0835
2947.0156 | 123.0057 | -53.0823 | 69.873 | -0.23666 | 0.0097989 | 0.069319 | 0.07009 | 0.13142 | -0.0026405 | -0.0087863 | -0.18326 | -0.0097668 | 0.065119 | 0.05633 | 0.0037812 | -0.013042 | 69.4427 | 69.6671 | 2.861 | -53.4073 | 69.754 | -53.3386 | -53.4073 | -51.9745 | 26.9531 | -53.1189 | 69.8822 | 69.7998 | -53.3157 | -53.3066 | -0.25635 | -0.32501 | -0.11902 | 122.7493 | -0.32501 | 0 | -0.4303 | -0.23346 | -0.2243 | 0.009155 | 1.1078 | -0.036621 | 0.18768 | -0.073242 | 122.8363 | 122.525 | 55.9433 | -123.2803 | 122.9645 | 122.8821 | 80.0354 | -123.1796
2948.0156 | 123.056 | -52.6978 | 70.253 | -0.17563 | 0.017062 | 0.069319 | 0.073935 | 0.13163 | 0.00035035 | -0.0075047 | -0.19852 | -0.010621 | 0.064264 | 0.055262 | 0.0093354 | -0.01176 | 69.928 | 70.1019 | 3.772 | -52.9495 | 70.253 | -52.8763 | -52.9541 | -51.503 | 26.9394 | -52.7161 | 70.34 | 70.2393 | -52.9083 | -52.9312 | -0.17853 | -0.25635 | 0 | 122.7997 | -0.25177 | 0.004578 | -0.32501 | -0.21057 | -0.23346 | 0.086975 | 1.1948 | -0.01831 | 0.21515 | -0.013733 | 122.9507 | 122.6257 | 56.4697 | -123.2071 | 123.0377 | 122.937 | 79.6371 | -123.1842
2949.0312 | 123.1567 | -53.0365 | 69.7861 | -0.015411 | 0.0080899 | 0.072523 | 0.070303 | 0.12928 | -0.0054175 | -0.0072911 | 0.0914 | -0.014039 | 0.062769 | 0.055689 | 0.0037812 | -0.011974 | 69.6533 | 69.9188 | 3.6438 | -53.1647 | 69.9417 | -53.1189 | -53.215 | -51.7364 | 26.651 | -53.0777 | 69.928 | 69.8273 | -53.2288 | -53.2791 | -0.082397 | -0.17853 | 0.15564 | 122.9553 | -0.12817 | 0.050354 | -0.13275 | -0.19226 | -0.24262 | 0.14191 | 1.3 | -0.041199 | 0.20142 | 0.041199 | 122.9782 | 122.6898 | 56.6803 | -123.0011 | 122.9645 | 122.8638 | 79.6875 | -123.0652
2950.0156 | 123.143 | -53.4668 | 69.3924 | 1.2511 | 0.010653 | 0.070387 | 0.071158 | 0.12736 | -0.0034949 | -0.0077183 | -0.015411 | -0.011476 | 0.062555 | 0.057398 | 0.0042084 | -0.012828 | 69.3283 | 69.4611 | 2.7557 | -53.627 | 69.4977 | -53.5812 | -53.6682 | -52.3132 | 26.0696 | -53.508 | 69.4794 | 69.3649 | -53.6865 | -53.7231 | -0.11444 | -0.20142 | 0.10529 | 122.9279 | -0.16022 | 0.041199 | -0.064087 | -0.21973 | -0.25635 | 0.086975 | 1.1536 | -0.041199 | 0.21515 | -0.027466 | 122.9645 | 122.7951 | 56.2225 | -123.0606 | 122.9462 | 122.8317 | 79.5364 | -123.1155
2951.0156 | 123.1064 | -54.3411 | 68.5318 | -0.25192 | 0.010653 | 0.071882 | 0.072226 | 0.128 | -0.00093145 | -0.0085727 | -0.168 | -0.0097668 | 0.063837 | 0.055476 | 0.0065582 | -0.014537 | 68.4265 | 68.6508 | 3.2501 | -54.3915 | 68.6874 | -54.3549 | -54.4601 | -53.2333 | 25.3372 | -54.4556 | 68.6966 | 68.605 | -54.5059 | -54.5288 | -0.013733 | -0.11902 | 0.15564 | 122.9919 | -0.050354 | 0.068665 | -0.10529 | -0.1648 | -0.18768 | 0.16479 | 1.1078 | -0.11444 | 0.073243 | 0.073243 | 123.0286 | 122.7676 | 57.5912 | -122.9919 | 123.0377 | 122.9462 | 79.6783 | -123.0606
2952.0156 | 123.1659 | -54.158 | 68.6691 | -0.091705 | 0.0091581 | 0.070387 | 0.07009 | 0.12608 | -0.0045631 | -0.0087863 | 0.0914 | -0.011262 | 0.06341 | 0.058253 | 0.00549 | -0.012828 | 68.7195 | 68.9529 | 5.4749 | -54.1443 | 69.0033 | -54.0665 | -54.1489 | -52.8214 | 25.6119 | -54.1397 | 68.8522 | 68.7744 | -54.2999 | -54.3549 | 0.091553 | 0.009155 | 0.33417 | 123.111 | 0.013733 | 0.004578 | 0.050354 | -0.14191 | -0.19684 | 0.18311 | 1.3367 | 0.018311 | 0.21515 | 0.10529 | 123.1613 | 122.8775 | 59.6329 | -122.818 | 123.0103 | 122.9324 | 79.7699 | -123.024
2953.0156 | 123.0789 | -53.8239 | 69.0445 | -0.22141 | 0.010226 | 0.071882 | 0.072653 | 0.13121 | 0.00035035 | -0.0077183 | -0.18326 | -0.0089124 | 0.064691 | 0.055262 | 0.0074126 | -0.014323 | 68.9438 | 69.1315 | 5.7449 | -54.039 | 69.1498 | -53.9383 | -54.0344 | -52.6245 | 25.7172 | -54.0573 | 69.1177 | 69.0262 | -54.0665 | -54.1122 | -0.11444 | -0.21057 | 0.10529 | 122.9553 | -0.21515 | -0.004577 | -0.10071 | -0.24261 | -0.28839 | 0.073242 | 1.1993 | -0.23346 | 0.054932 | -0.018311 | 122.9736 | 122.7676 | 59.5688 | -123.0789 | 122.9416 | 122.85 | 79.541 | -123.1567
2954.0156 | 123.1338 | -53.2333 | 69.6304 | 0.060882 | 0.010013 | 0.071027 | 0.072012 | 0.12864 | -0.0022131 | -0.0077183 | 0.0914 | -0.010621 | 0.064051 | 0.05633 | 0.00549 | -0.011546 | 69.5572 | 69.7769 | 6.395 | -53.3203 | 69.8227 | -53.2471 | -53.3112 | -51.9196 | 26.2939 | -53.3386 | 69.7678 | 69.6533 | -53.421 | -53.476 | -0.013733 | -0.07782 | 0.19226 | 123.0103 | -0.086975 | -0.009155 | -0.073242 | -0.18768 | -0.24262 | 0.13733 | 1.3138 | -0.10529 | 0.13733 | 0.022888 | 123.056 | 122.7905 | 59.6283 | -122.9416 | 123.0011 | 122.8867 | 79.5273 | -123.1064
2955.0156 | 123.1338 | -53.5721 | 69.2596 | -0.25192 | 0.0089443 | 0.069532 | 0.070944 | 0.1295 | -0.0039221 | -0.0053683 | -0.12222 | -0.011689 | 0.061701 | 0.056758 | 0.0076264 | -0.013042 | 68.9987 | 69.223 | 5.8731 | -53.8513 | 69.2917 | -53.7918 | -53.8055 | -52.3727 | 25.7217 | -53.4531 | 69.4382 | 69.3604 | -53.7094 | -53.7598 | -0.21973 | -0.23346 | 0.032043 | 122.7951 | -0.27923 | -0.045776 | -0.26093 | -0.13733 | -0.18768 | 0.17853 | 1.1993 | 0.11902 | 0.3067 | 0.10071 | 122.8638 | 122.5708 | 59.4452 | -123.0652 | 123.0103 | 122.9324 | 79.2938 | -123.0194
2956.0156 | 123.1476 | -54.0436 | 68.7561 | -0.168 | 0.0074491 | 0.070173 | 0.069663 | 0.12715 | -0.0052039 | -0.0094273 | -0.14511 | -0.011903 | 0.062128 | 0.054621 | 0.00784 | -0.011974 | 69.0674 | 68.6462 | 3.7216 | -54.0985 | 68.9713 | -54.1122 | -54.1809 | -52.7298 | 25.5112 | -53.9978 | 68.985 | 68.9072 | -54.1763 | -54.2267 | -0.068665 | -0.13733 | 0.21515 | 122.6898 | -0.054932 | 0.082397 | 0.31128 | -0.13275 | -0.18311 | 0.22888 | 1.3138 | 0.045776 | 0.22888 | 0.15106 | 123.0148 | 123.111 | 57.7652 | -122.937 | 123.0286 | 122.9507 | 79.5547 | -122.9828
2957.0156 | 123.1384 | -53.5767 | 69.3054 | -0.023041 | 0.0074491 | 0.069532 | 0.070517 | 0.128 | -0.0017859 | -0.0083591 | 0.037995 | -0.010408 | 0.062982 | 0.058253 | 0.0084808 | -0.011546 | 68.9301 | 69.2047 | 3.1265 | -53.9017 | 69.2047 | -53.8513 | -53.9246 | -52.4597 | 25.9048 | -53.5034 | 69.3192 | 69.2505 | -53.7964 | -53.8284 | -0.27466 | -0.3479 | -0.10071 | 122.7814 | -0.32501 | 0.022889 | -0.37537 | -0.21973 | -0.25177 | 0.013733 | 1.1169 | 0.073242 | 0.32501 | -0.054932 | 122.7814 | 122.5067 | 56.7032 | -123.23 | 122.8958 | 122.8271 | 79.4815 | -123.1338
2958.0156 | 123.0927 | -52.9083 | 69.9829 | -0.091705 | 0.0080899 | 0.069959 | 0.071372 | 0.13057 | -0.0017859 | -0.0081455 | -0.068817 | -0.011262 | 0.063837 | 0.055903 | 0.00784 | -0.013896 | 69.8959 | 70.1019 | 2.5085 | -53.0228 | 70.079 | -52.9724 | -53.064 | -51.7731 | 26.4496 | -53.0365 | 70.0012 | 69.8959 | -53.1555 | -53.1876 | -0.064087 | -0.15564 | 0.096131 | 123.0103 | -0.11444 | 0.041199 | -0.086975 | -0.24719 | -0.27924 | 0.018311 | 1.1353 | -0.12817 | 0.15106 | -0.086975 | 122.9874 | 122.8043 | 55.4169 | -123.0469 | 122.9095 | 122.8043 | 79.3579 | -123.1705
2959.0156 | 123.0194 | -53.1464 | 69.8364 | -0.21378 | 0.011294 | 0.069532 | 0.07009 | 0.12993 | 0.0029137 | -0.0087863 | -0.20615 | -0.011476 | 0.066614 | 0.056117 | 0.00784 | -0.01411 | 69.4656 | 69.6396 | 2.1011 | -53.4439 | 69.7952 | -53.3066 | -53.4027 | -52.0981 | 26.4359 | -53.3478 | 69.8364 | 69.7403 | -53.3661 | -53.4164 | -0.16022 | -0.25635 | -0.041199 | 122.7859 | -0.29755 | -0.041199 | -0.37079 | -0.21973 | -0.27008 | 0 | 1.0483 | -0.20142 | 0.068665 | -0.096131 | 122.9416 | 122.612 | 55.2475 | -123.2391 | 122.9828 | 122.8867 | 79.5822 | -123.2529
2960.0156 | 123.1293 | -52.6154 | 70.1843 | -0.068817 | 0.0095853 | 0.070814 | 0.070517 | 0.12758 | -0.0043495 | -0.0077183 | 0.068512 | -0.010835 | 0.060633 | 0.055903 | 0.0069854 | -0.011546 | 70.1019 | 70.3033 | 2.4902 | -52.7481 | 70.3995 | -52.6611 | -52.7664 | -51.4847 | 26.6327 | -52.6108 | 70.3674 | 70.2988 | -52.7847 | -52.8305 | -0.045777 | -0.15106 | 0.21515 | 122.9187 | -0.13275 | 0.01831 | -0.082397 | -0.16937 | -0.21515 | 0.18311 | 1.1307 | 0.004577 | 0.21973 | 0.11444 | 123.0148 | 122.7173 | 55.1056 | -122.9507 | 122.9828 | 122.9141 | 79.248 | -123.0148
2961.0156 | 123.1522 | -52.8809 | 69.9783 | -0.023041 | 0.0087307 | 0.071882 | 0.070944 | 0.12629 | -0.0024269 | -0.0062229 | -0.061188 | -0.010621 | 0.064264 | 0.055049 | 0.0082672 | -0.013255 | 70.0333 | 70.2255 | 2.7603 | -53.009 | 70.1477 | -52.9449 | -53.0823 | -51.7227 | 26.3214 | -52.9907 | 70.0333 | 69.9783 | -53.0869 | -53.1555 | -0.064087 | -0.20142 | 0.16937 | 123.1064 | -0.12817 | 0.073242 | 0.054931 | -0.20599 | -0.27466 | 0.054931 | 1.1581 | -0.10986 | 0.16479 | 0 | 123.0286 | 122.9141 | 55.6412 | -123.0606 | 122.9141 | 122.8592 | 79.2023 | -123.1339
2962.0156 | 123.1522 | -53.2745 | 69.5755 | -0.068817 | 0.0076627 | 0.06825 | 0.072653 | 0.12629 | -0.0028541 | -0.0087863 | -0.099335 | -0.011689 | 0.062982 | 0.055903 | 0.0067718 | -0.012401 | 69.4656 | 69.6625 | 2.417 | -53.4531 | 69.6625 | -53.3661 | -53.4348 | -52.3361 | 25.7126 | -53.4943 | 69.5114 | 69.4336 | -53.5629 | -53.5767 | -0.091553 | -0.16022 | 0.086976 | 122.937 | -0.17853 | -0.018311 | -0.10986 | -0.28839 | -0.30212 | -0.064086 | 0.93841 | -0.21973 | 0.082397 | -0.14191 | 122.937 | 122.7402 | 55.6915 | -123.0103 | 122.7859 | 122.7081 | 78.9871 | -123.1522
2963.0156 | 123.0927 | -53.1281 | 69.7723 | -0.18326 | 0.0097989 | 0.071455 | 0.073935 | 0.12758 | -0.0011451 | -0.0062229 | -0.16037 | -0.011476 | 0.060633 | 0.05633 | 0.0080536 | -0.014751 | 69.5572 | 69.7769 | 2.3071 | -53.302 | 69.7495 | -53.2654 | -53.3478 | -52.0798 | 25.914 | -53.1967 | 69.841 | 69.7311 | -53.3569 | -53.3844 | -0.13733 | -0.21973 | -0.022888 | 122.905 | -0.17395 | 0.045776 | -0.21515 | -0.22888 | -0.25635 | 0.068664 | 1.0483 | -0.068664 | 0.18768 | -0.041199 | 122.8775 | 122.6852 | 55.4352 | -123.1201 | 122.9691 | 122.8592 | 79.0421 | -123.1567
2964.0156 | 123.0652 | -53.0731 | 69.8502 | -0.19852 | 0.011508 | 0.069319 | 0.072867 | 0.12758 | 0.0022729 | -0.0077183 | -0.27481 | -0.010194 | 0.064905 | 0.056971 | 0.0091216 | -0.015392 | 69.7128 | 69.841 | 2.2247 | -53.2059 | 70.0058 | -53.1189 | -53.2196 | -52.0203 | 26.0193 | -53.2196 | 69.9783 | 69.8593 | -53.27 | -53.3066 | -0.045776 | -0.14648 | 0.15564 | 122.9141 | -0.13275 | 0.013732 | -0.13733 | -0.19684 | -0.23346 | 0.12817 | 1.0529 | -0.14648 | 0.086976 | 0.009155 | 123.0789 | 122.7859 | 55.2979 | -123.0698 | 123.0515 | 122.9324 | 79.0924 | -123.1567
2965.0156 | 123.2712 | -53.6087 | 69.2734 | -0.12222 | 0.0063809 | 0.0706 | 0.070944 | 0.12501 | -0.0028541 | -0.0075047 | -0.084076 | -0.012544 | 0.059778 | 0.057185 | 0.0065582 | -0.011333 | 69.1589 | 69.397 | 2.2659 | -53.7369 | 69.3558 | -53.6957 | -53.7872 | -52.5146 | 25.5066 | -53.6545 | 69.31 | 69.2276 | -53.8284 | -53.8422 | -0.086975 | -0.17853 | 0.082398 | 123.0057 | -0.12817 | 0.050354 | -0.11444 | -0.21973 | -0.23346 | 0.036622 | 1.0941 | -0.045776 | 0.18768 | -0.045776 | 122.9645 | 122.7676 | 55.8746 | -123.0606 | 122.9187 | 122.8363 | 79.1153 | -123.1155
2966.0156 | 123.1293 | -53.92 | 68.9209 | -0.076447 | 0.010013 | 0.071455 | 0.072226 | 0.13078 | -0.0032813 | -0.0057957 | 0.015106 | -0.011049 | 0.062342 | 0.055476 | 0.0050628 | -0.012614 | 68.66 | 68.8797 | 2.1515 | -54.2038 | 68.9301 | -54.1672 | -54.2313 | -52.9083 | 25.3189 | -53.9932 | 68.9804 | 68.866 | -54.158 | -54.2038 | -0.24719 | -0.31128 | 0.009156 | 122.7997 | -0.28381 | 0.027466 | -0.26093 | -0.23804 | -0.28381 | 0.05951 | 1.0117 | -0.073242 | 0.21057 | -0.054931 | 122.85 | 122.58 | 56.0715 | -123.1522 | 122.9004 | 122.7859 | 79.2389 | -123.1247
2967.0156 | 123.1979 | -53.0136 | 69.8273 | -0.12222 | 0.0097989 | 0.070173 | 0.069449 | 0.12758 | -0.0045631 | -0.0066501 | -0.0077819 | -0.010835 | 0.062555 | 0.05633 | 0.0063446 | -0.013683 | 69.8914 | 70.1111 | 2.2476 | -53.009 | 70.0928 | -52.9541 | -53.0319 | -51.7502 | 26.4725 | -52.8397 | 70.079 | 69.96 | -53.0914 | -53.1921 | 0.059509 | -0.01831 | 0.2655 | 123.1247 | 0.004578 | 0.022888 | 0.064086 | -0.07782 | -0.17853 | 0.25177 | 1.2634 | 0.17395 | 0.35248 | 0.13275 | 123.1064 | 122.905 | 55.2612 | -122.8592 | 123.0927 | 122.9736 | 79.4861 | -123.0194
2968.0156 | 123.1201 | -53.8651 | 69.0308 | 0.037994 | 0.0083035 | 0.070173 | 0.071799 | 0.12459 | -0.0011451 | -0.0057957 | -0.25192 | -0.011476 | 0.063196 | 0.057612 | 0.008908 | -0.011974 | 68.8156 | 69.0445 | 2.1561 | -54.0848 | 69.0994 | -53.9703 | -54.0848 | -52.8259 | 25.351 | -53.9429 | 69.0948 | 68.9713 | -54.0939 | -54.1397 | -0.10529 | -0.21973 | 0.068664 | 122.9095 | -0.21973 | 0 | -0.21515 | -0.22888 | -0.27466 | 0.064087 | 1.0391 | -0.07782 | 0.19684 | -0.05951 | 122.9645 | 122.6807 | 56.0211 | -123.1155 | 122.9599 | 122.8363 | 79.216 | -123.1705
2969.0156 | 123.0469 | -53.3981 | 69.4977 | 1.3731 | 0.0095853 | 0.071027 | 0.070944 | 0.12971 | 0.00035035 | -0.0049411 | -0.23666 | -0.009126 | 0.064051 | 0.058253 | 0.0063446 | -0.01411 | 69.2551 | 69.3558 | 2.1606 | -53.6545 | 69.5618 | -53.5812 | -53.6819 | -52.4277 | 25.7172 | -53.5629 | 69.6213 | 69.4656 | -53.6453 | -53.6682 | -0.18311 | -0.28381 | 0.064087 | 122.7539 | -0.25635 | 0.027466 | -0.24262 | -0.24719 | -0.27008 | 0.1236 | 0.97046 | -0.1648 | 0.10529 | -0.032044 | 122.9599 | 122.6532 | 55.5588 | -123.1796 | 123.0194 | 122.8638 | 79.1153 | -123.1659
2970.0156 | 123.1247 | -53.6499 | 69.191 | 0.015106 | 0.0072355 | 0.072096 | 0.075217 | 0.12886 | -0.0017859 | -0.0072911 | -0.015411 | -0.011262 | 0.063196 | 0.056758 | 0.0069854 | -0.011546 | 69.072 | 69.2871 | 2.0462 | -53.8147 | 69.3375 | -53.714 | -53.8101 | -52.5513 | 25.7767 | -53.7048 | 69.3008 | 69.2139 | -53.8513 | -53.8971 | -0.064087 | -0.16022 | 0.14648 | 122.937 | -0.1648 | -0.004577 | -0.11902 | -0.20142 | -0.24719 | 0.10986 | 1.0986 | -0.054932 | 0.19226 | 0.022888 | 122.9874 | 122.7219 | 55.6961 | -123.0011 | 122.9507 | 122.8638 | 79.4266 | -123.0881
2971.0156 | 123.0743 | -54.0024 | 68.9255 | -0.22141 | 0.0080899 | 0.069746 | 0.071799 | 0.12971 | 0.00013675 | -0.0072911 | -0.20615 | -0.011689 | 0.061487 | 0.055262 | 0.0082672 | -0.013896 | 68.7286 | 68.9346 | 2.0645 | -54.1672 | 68.9575 | -54.0802 | -54.1718 | -52.9266 | 25.7538 | -54.039 | 68.9896 | 68.8889 | -54.2084 | -54.2267 | -0.07782 | -0.16937 | 0.032044 | 122.937 | -0.16479 | 0.004578 | -0.19684 | -0.20599 | -0.22431 | 0.064087 | 1.0757 | -0.036621 | 0.18768 | -0.036621 | 122.9599 | 122.731 | 56.0669 | -123.0972 | 122.9919 | 122.8912 | 79.7562 | -123.1522
2972.0156 | 123.0881 | -53.7598 | 69.1544 | -0.22141 | 0.010226 | 0.072096 | 0.071372 | 0.128 | -0.0022131 | -0.0064365 | -0.18326 | -0.010408 | 0.06341 | 0.054835 | 0.0074126 | -0.012614 | 68.9758 | 69.1864 | 2.0737 | -53.9291 | 69.2139 | -53.8696 | -53.9474 | -52.7481 | 26.0376 | -53.8559 | 69.2001 | 69.0903 | -54.0024 | -54.0436 | -0.10986 | -0.18768 | 0.059509 | 122.9462 | -0.16937 | 0.018311 | -0.17853 | -0.24261 | -0.28381 | 0.045776 | 1.0117 | -0.09613 | 0.18768 | -0.064087 | 122.9736 | 122.7356 | 55.8334 | -123.1018 | 122.9599 | 122.85 | 79.7974 | -123.1979
2973.0156 | 123.1064 | -54.5197 | 68.3578 | -0.19089 | 0.0091581 | 0.078077 | 0.075858 | 0.128 | 0.0027001 | -0.0070773 | -0.3511 | -0.010194 | 0.060633 | 0.054621 | 0.007199 | -0.014751 | 68.1061 | 68.335 | 2.0004 | -54.7714 | 68.3304 | -54.6799 | -54.7668 | -53.4714 | 25.1404 | -54.6066 | 68.399 | 68.2938 | -54.7714 | -54.7943 | -0.16022 | -0.24719 | -0.027466 | 122.8546 | -0.25177 | -0.004577 | -0.25177 | -0.25177 | -0.27466 | 0.041199 | 1.0483 | -0.086975 | 0.18768 | -0.064087 | 122.85 | 122.6257 | 56.5201 | -123.1247 | 122.9187 | 122.8134 | 79.66 | -123.1522
2974.0156 | 123.1522 | -53.8284 | 69.1406 | 0.030365 | 0.014071 | 0.0706 | 0.073081 | 0.13099 | 0.0050499 | -0.0060093 | 0.0914 | -0.0069898 | 0.06341 | 0.05868 | 0.0084808 | -0.015178 | 68.8522 | 68.9804 | 1.9684 | -54.0527 | 69.2459 | -53.9246 | -53.9978 | -52.8122 | 25.4745 | -54.071 | 69.2001 | 69.0628 | -54.0756 | -54.0848 | -0.096131 | -0.16937 | 0.10529 | 122.8088 | -0.2243 | -0.054931 | -0.28839 | -0.24719 | -0.25635 | 0.059509 | 1.0162 | -0.24262 | 0.013733 | -0.07782 | 123.0743 | 122.6807 | 55.7968 | -123.1384 | 123.0286 | 122.8912 | 79.303 | -123.2254
2975.0156 | 123.1384 | -53.8834 | 68.9301 | -0.18326 | 0.0095853 | 0.075727 | 0.077994 | 0.12928 | -7.6852e-05 | -0.0057957 | -0.35873 | -0.011476 | 0.063837 | 0.059748 | 0.0048492 | -0.011333 | 68.8614 | 69.1406 | 2.4445 | -53.9749 | 69.1589 | -53.8971 | -53.9886 | -52.7161 | 25.6668 | -53.9566 | 69.1132 | 68.9896 | -54.0848 | -54.1351 | -0.013733 | -0.10529 | 0.22888 | 123.024 | -0.091553 | 0.013732 | -0.068665 | -0.20142 | -0.25177 | 0.1831 | 1.1673 | -0.073242 | 0.17853 | 0.059509 | 123.0423 | 122.7448 | 56.3278 | -122.9187 | 122.9965 | 122.8729 | 79.5502 | -123.0652
2976.0156 | 123.1293 | -52.7344 | 70.1294 | -0.22141 | 0.0093717 | 0.078718 | 0.074362 | 0.12736 | -0.0013587 | -0.0079319 | -0.168 | -0.011903 | 0.060205 | 0.056117 | 0.008908 | -0.01411 | 70.2393 | 70.2301 | 2.8473 | -52.8168 | 70.3079 | -52.7847 | -52.8854 | -51.5854 | 26.7975 | -52.9083 | 70.2255 | 70.1248 | -52.9266 | -52.9816 | -0.050354 | -0.15106 | 0.17853 | 122.9645 | -0.082397 | 0.068665 | 0.10986 | -0.19226 | -0.24719 | 0.09613 | 1.149 | -0.17395 | 0.073242 | -0.004578 | 123.0423 | 122.9736 | 55.5817 | -123.0148 | 122.9599 | 122.8592 | 79.5319 | -123.111
2977.0156 | 123.1522 | -53.3249 | 69.5618 | -0.22141 | 0.0093717 | 0.069319 | 0.072226 | 0.12736 | -0.0032813 | -0.0070773 | -0.061188 | -0.011476 | 0.063196 | 0.055903 | 0.0084808 | -0.01411 | 69.6716 | 69.6533 | 2.5269 | -53.302 | 69.7906 | -53.2562 | -53.3478 | -52.2308 | 26.4542 | -53.4256 | 69.6442 | 69.4931 | -53.5583 | -53.5904 | 0.068664 | -0.022888 | 0.22888 | 122.9782 | 0.022888 | 0.045776 | 0.10986 | -0.23346 | -0.2655 | 0.082397 | 1.0941 | -0.10071 | 0.16479 | -0.068665 | 123.1155 | 122.9965 | 55.8517 | -122.9095 | 122.9691 | 122.818 | 79.7791 | -123.1522
2978.0156 | 123.1201 | -53.0914 | 69.7861 | -2.9985 | 0.0085171 | 0.07295 | 0.06304 | 0.13057 | -0.0026405 | -0.0060093 | -0.045929 | -0.011049 | 0.06341 | 0.057185 | 0.0067718 | -0.012828 | 69.9005 | 70.0928 | 2.655 | -53.0136 | 70.0836 | -52.9724 | -53.0777 | -51.9791 | 26.6373 | -53.2059 | 69.873 | 69.7678 | -53.3066 | -53.3569 | 0.11902 | 0.013733 | 0.29755 | 123.1842 | 0.07782 | 0.064087 | 0.11444 | -0.21515 | -0.2655 | 0.086975 | 1.1124 | -0.11444 | 0.15106 | -0.018311 | 123.175 | 122.9919 | 55.7465 | -122.8638 | 122.9645 | 122.8592 | 79.7287 | -123.143
2979.0156 | 123.1522 | -52.8351 | 70.0836 | -0.23666 | 0.00039951 | 0.072309 | 0.071585 | 0.12843 | -0.0028541 | -0.0077183 | -0.10696 | -0.010194 | 0.062128 | 0.054835 | 0.0082672 | -0.013683 | 69.7769 | 69.7632 | 2.6367 | -53.183 | 69.9051 | -53.1418 | -53.2471 | -51.9562 | 26.4267 | -52.8625 | 69.9417 | 69.8135 | -53.1509 | -53.1509 | -0.3067 | -0.41199 | -0.17853 | 122.5983 | -0.3479 | 0.064087 | -0.3067 | -0.31586 | -0.31586 | -0.14191 | 0.87891 | -0.027466 | 0.28839 | -0.27008 | 122.7402 | 122.612 | 55.4718 | -123.3307 | 122.7768 | 122.6486 | 79.2618 | -123.2346
2980.0156 | 123.1567 | -53.595 | 69.2688 | -0.045929 | 0.0091581 | 0.069959 | 0.073081 | 0.12629 | -0.0026405 | -0.0068637 | 0.022736 | -0.011476 | 0.060205 | 0.056971 | 0.0065582 | -0.013896 | 69.0765 | 69.2871 | 2.7969 | -53.801 | 69.3695 | -53.7186 | -53.7964 | -52.5146 | 25.7904 | -53.7094 | 69.3008 | 69.2139 | -53.8055 | -53.8376 | -0.1236 | -0.20142 | 0.10071 | 122.8821 | -0.20599 | -0.004577 | -0.19226 | -0.21057 | -0.24261 | 0.032043 | 1.0803 | -0.11444 | 0.12817 | -0.054932 | 122.9645 | 122.6715 | 56.3919 | -123.0652 | 122.8958 | 122.8088 | 79.3854 | -123.1064
2981.0156 | 123.0743 | -53.1281 | 69.754 | -0.22903 | 0.0097989 | 0.071027 | 0.072867 | 0.12928 | -7.6852e-05 | -0.0070773 | -0.19089 | -0.0095532 | 0.06341 | 0.055689 | 0.0091216 | -0.01411 | 69.6304 | 69.8273 | 2.9617 | -53.2471 | 69.9005 | -53.2013 | -53.3066 | -52.0615 | 26.0925 | -53.2608 | 69.8318 | 69.7174 | -53.3569 | -53.3844 | -0.073242 | -0.17853 | 0.14648 | 122.9553 | -0.11902 | 0.05951 | -0.1236 | -0.22888 | -0.25635 | 0.07782 | 1.0666 | -0.13275 | 0.1236 | -0.036621 | 123.0286 | 122.7585 | 56.0898 | -123.0606 | 122.9599 | 122.8455 | 79.2206 | -123.1384
2982.0156 | 123.1476 | -53.3295 | 69.5251 | -0.168 | 0.0085171 | 0.069746 | 0.076071 | 0.13249 | -0.0019995 | -0.0034457 | -0.053558 | -0.010408 | 0.062342 | 0.055903 | 0.00784 | -0.011974 | 69.2047 | 69.8547 | 2.9755 | -53.4439 | 69.754 | -53.3295 | -53.421 | -52.2583 | 26.1063 | -53.4805 | 69.5801 | 69.4656 | -53.5721 | -53.627 | 0 | -0.091553 | 0.22888 | 123.1842 | -0.11444 | -0.022888 | -0.32043 | -0.24262 | -0.29755 | 0.054932 | 1.0712 | -0.15106 | 0.14648 | -0.059509 | 123.0835 | 122.5342 | 56.3049 | -122.9462 | 122.9095 | 122.7951 | 79.4357 | -123.1522
2983.0156 | 123.1018 | -53.3066 | 69.5892 | -0.18326 | 0.010867 | 0.069959 | 0.072012 | 0.12843 | -0.0013587 | -0.0064365 | 0.31265 | -0.010835 | 0.059992 | 0.053767 | 0.0076264 | -0.012401 | 69.7083 | 69.5984 | 2.6047 | -53.3203 | 69.8456 | -53.2379 | -53.3569 | -52.2583 | 25.9918 | -53.595 | 69.5984 | 69.4748 | -53.5583 | -53.5767 | 0.068665 | -0.050354 | 0.25635 | 122.905 | -0.013732 | 0.036622 | 0.11902 | -0.25177 | -0.27008 | 0.009156 | 1.0483 | -0.28839 | -0.018311 | -0.11444 | 123.1522 | 123.0148 | 55.9113 | -122.9462 | 122.905 | 122.7814 | 79.2984 | -123.1659
2984.0156 | 123.0698 | -53.0731 | 69.8502 | -0.22903 | 0.011508 | 0.071241 | 0.071799 | 0.12822 | -7.6852e-05 | -0.0062229 | -0.20615 | -0.011049 | 0.061914 | 0.054194 | 0.008908 | -0.012828 | 69.6808 | 69.8822 | 2.7649 | -53.2379 | 69.928 | -53.1601 | -53.2608 | -52.0203 | 26.1291 | -53.1784 | 69.8959 | 69.7586 | -53.2928 | -53.3249 | -0.086975 | -0.18768 | 0.07782 | 122.9553 | -0.16479 | 0.022888 | -0.16937 | -0.21973 | -0.25177 | 0.045776 | 1.0529 | -0.10529 | 0.14648 | -0.091553 | 123.0011 | 122.7539 | 55.838 | -123.111 | 122.9691 | 122.8317 | 79.2023 | -123.175
2985.0156 | 123.0835 | -53.1555 | 69.7495 | -0.14511 | 0.0083035 | 0.069532 | 0.070944 | 0.12886 | -0.00093145 | -0.0079319 | -0.19089 | -0.011262 | 0.061914 | 0.055262 | 0.0076264 | -0.012614 | 69.5984 | 69.8318 | 2.916 | -53.27 | 69.8456 | -53.2333 | -53.3386 | -52.0889 | 26.1841 | -53.1647 | 69.7998 | 69.6808 | -53.3981 | -53.4485 | -0.077819 | -0.1831 | 0.09613 | 122.9874 | -0.11444 | 0.068665 | -0.15106 | -0.24261 | -0.29297 | 0.050354 | 1.0666 | -0.009155 | 0.28381 | -0.068665 | 123.0011 | 122.7539 | 56.0715 | -123.0881 | 122.9553 | 122.8363 | 79.3396 | -123.1979
2986.0156 | 123.0972 | -53.6545 | 69.2825 | -0.18326 | 0.0095853 | 0.071241 | 0.071158 | 0.12651 | -7.6852e-05 | -0.0066501 | -0.168 | -0.011689 | 0.062342 | 0.05633 | 0.006131 | -0.011974 | 69.0445 | 69.2642 | 4.2297 | -53.8879 | 69.2688 | -53.8239 | -53.9383 | -52.6382 | 25.8636 | -53.8376 | 69.278 | 69.1452 | -53.9246 | -53.92 | -0.16937 | -0.28381 | -0.013733 | 122.9187 | -0.23346 | 0.050354 | -0.23804 | -0.27008 | -0.2655 | -0.004578 | 1.0162 | -0.1831 | 0.082398 | -0.13733 | 122.9233 | 122.699 | 57.8842 | -123.2208 | 122.9324 | 122.7997 | 79.5181 | -123.2025
2987.0156 | 123.1567 | -53.8376 | 69.0079 | -0.17563 | 0.0083035 | 0.0706 | 0.070517 | 0.128 | -0.0019995 | -0.0053683 | -1.4268 | -0.008058 | 0.063623 | 0.055476 | 0.0059174 | -0.012614 | 68.8431 | 69.1132 | 2.9572 | -53.8513 | 69.1269 | -53.9658 | -54.0298 | -52.7481 | 25.8133 | -53.9566 | 69.0674 | 68.9438 | -54.0939 | -54.1122 | -0.12817 | -0.19226 | 0.11902 | 122.9507 | -0.013733 | 0.17853 | -0.16479 | -0.25635 | -0.27466 | 0.059509 | 1.0895 | -0.11902 | 0.15564 | -0.064087 | 122.9645 | 122.6807 | 56.7947 | -123.0377 | 122.905 | 122.7814 | 79.6509 | -123.1201
2988.0156 | 123.1567 | -53.7872 | 69.0445 | -0.00015269 | 0.0061673 | 0.070387 | 0.070517 | 0.12758 | -0.0026405 | -0.0085727 | 0.053253 | -0.011903 | 0.064051 | 0.055049 | 0.0063446 | -0.012828 | 68.898 | 69.1315 | 3.8132 | -53.9703 | 69.2001 | -53.8788 | -53.9658 | -52.6886 | 25.8316 | -53.8193 | 69.1772 | 69.0445 | -53.9795 | -54.0253 | -0.091553 | -0.17853 | 0.15564 | 122.9187 | -0.18311 | -0.004578 | -0.14648 | -0.19226 | -0.23804 | 0.13275 | 1.0986 | -0.032044 | 0.20599 | 0 | 122.9874 | 122.6852 | 57.6004 | -123.0103 | 122.9645 | 122.8317 | 79.6188 | -123.0698
2989.0156 | 123.056 | -53.5538 | 69.3832 | -0.17563 | 0.013003 | 0.069959 | 0.071799 | 0.128 | 0.0033411 | -0.0055821 | -0.26718 | -0.008058 | 0.063196 | 0.054835 | 0.00784 | -0.014751 | 69.1956 | 69.3329 | 4.3121 | -53.7186 | 69.4931 | -53.6453 | -53.7369 | -52.478 | 25.8133 | -53.7048 | 69.4794 | 69.3649 | -53.7506 | -53.8055 | -0.091553 | -0.1831 | 0.10986 | 122.8867 | -0.16479 | 0.01831 | -0.18768 | -0.19684 | -0.25177 | 0.09613 | 1.0757 | -0.15106 | 0.10071 | -0.018311 | 123.0469 | 122.7493 | 57.8659 | -123.1201 | 123.0331 | 122.9187 | 79.3671 | -123.1888
2990.0156 | 123.1567 | -52.8305 | 70.0516 | -0.16037 | 0.011294 | 0.068891 | 0.071585 | 0.12459 | -0.0028541 | -0.0079319 | 0.076141 | -0.011689 | 0.062769 | 0.058253 | 0.0074126 | -0.011119 | 69.9783 | 70.1477 | 3.653 | -52.9861 | 70.2393 | -52.8809 | -52.9495 | -51.7319 | 26.4267 | -52.8717 | 70.1614 | 70.047 | -53.0228 | -53.0548 | -0.050354 | -0.11902 | 0.18768 | 122.9782 | -0.15564 | -0.036621 | -0.073242 | -0.19226 | -0.22431 | 0.10986 | 1.0986 | -0.041199 | 0.18311 | -0.004578 | 123.0698 | 122.8088 | 56.4835 | -123.0011 | 122.9919 | 122.8775 | 79.2572 | -123.1064
2991.0156 | 123.1979 | -54.0527 | 68.8019 | -0.17563 | 0.0085171 | 0.069532 | 0.073294 | 0.13035 | -0.0015723 | -0.0070773 | -0.10696 | -0.011049 | 0.062982 | 0.054194 | 0.0069854 | -0.014964 | 68.7424 | 68.9484 | 3.0624 | -54.2038 | 68.9255 | -54.158 | -54.2313 | -52.8992 | 25.5386 | -54.0527 | 68.9163 | 68.7836 | -54.2542 | -54.2999 | -0.10529 | -0.17853 | 0.1236 | 123.0011 | -0.15106 | 0.027466 | -0.059509 | -0.20142 | -0.24719 | 0.11444 | 1.1536 | 0 | 0.24719 | -0.018311 | 122.9782 | 122.7951 | 57.1152 | -123.0331 | 122.9691 | 122.8363 | 79.5914 | -123.1018
2992.0156 | 123.1522 | -52.5879 | 70.3079 | -0.023041 | 0.0095853 | 0.073164 | 0.069876 | 0.12886 | -0.0015723 | -0.0066501 | 0.037995 | -0.010408 | 0.060205 | 0.054835 | 0.0074126 | -0.011974 | 70.134 | 70.3262 | 3.0304 | -52.803 | 70.3537 | -52.739 | -52.7939 | -51.5121 | 26.5732 | -52.565 | 70.3629 | 70.2438 | -52.7985 | -52.8351 | -0.15106 | -0.20599 | 0.045777 | 122.9141 | -0.21515 | -0.009156 | -0.17395 | -0.21057 | -0.24719 | 0.054932 | 1.0757 | 0.022889 | 0.27008 | -0.064087 | 122.9416 | 122.7219 | 55.6183 | -123.1018 | 122.9507 | 122.8317 | 79.1611 | -123.143
2993.0156 | 123.1384 | -52.89 | 69.9738 | -0.168 | 0.0093717 | 0.069319 | 0.07244 | 0.12822 | 0.00035035 | -0.0081455 | -0.40451 | -0.012544 | 0.06341 | 0.055476 | 0.0076264 | -0.014537 | 70.2988 | 70.1431 | 2.8061 | -53.0319 | 70.2118 | -52.8305 | -52.9449 | -51.7868 | 26.3077 | -52.9678 | 70.0333 | 69.9417 | -53.1143 | -53.1418 | 0.05951 | -0.054931 | 0.23804 | 123.0331 | -0.14191 | -0.086975 | 0.32501 | -0.2243 | -0.25177 | 0.059509 | 1.1032 | -0.077819 | 0.17395 | -0.032044 | 123.1018 | 123.1888 | 55.6961 | -122.9187 | 122.9233 | 122.8317 | 79.1977 | -123.1155
2994.0156 | 123.0881 | -52.9495 | 69.9005 | 0.015106 | 0.0097989 | 0.071882 | 0.070303 | 0.12672 | -0.0047767 | -0.0087863 | 0.037995 | -0.011476 | 0.060846 | 0.057398 | 0.0065582 | -0.014323 | 69.7037 | 69.8822 | 2.916 | -53.2104 | 69.9554 | -53.1189 | -53.2013 | -51.9058 | 26.2161 | -52.8534 | 69.9417 | 69.8547 | -53.2013 | -53.2333 | -0.16937 | -0.25177 | 0.054931 | 122.8317 | -0.26093 | -0.009155 | -0.19684 | -0.25177 | -0.28381 | 0.041198 | 1.0437 | 0.09613 | 0.37994 | -0.045777 | 122.905 | 122.6532 | 55.8655 | -123.1018 | 122.8912 | 122.8043 | 79.1656 | -123.1338
2995.0156 | 122.9965 | -52.8305 | 70.1019 | -0.21378 | 0.01044 | 0.0706 | 0.07009 | 0.12822 | 0.00035035 | -0.0085727 | -0.19852 | -0.009126 | 0.062982 | 0.055476 | 0.0084808 | -0.013469 | 69.6762 | 69.9005 | 2.5681 | -53.1509 | 69.9921 | -53.0914 | -53.2013 | -51.796 | 26.2253 | -52.9312 | 70.1294 | 70.0195 | -53.0502 | -53.064 | -0.26093 | -0.37079 | -0.10986 | 122.731 | -0.32043 | 0.050354 | -0.42572 | -0.21973 | -0.23346 | 0.027466 | 1.0345 | -0.10071 | 0.13275 | -0.082398 | 122.8226 | 122.5067 | 55.3986 | -123.3032 | 122.9599 | 122.85 | 79.0558 | -123.1659
2996.0156 | 123.1293 | -53.2333 | 69.6762 | -0.045929 | 0.011294 | 0.069532 | 0.071585 | 0.12993 | -0.0024269 | -0.0085727 | 0.0074766 | -0.011476 | 0.062982 | 0.055903 | 0.0057038 | -0.011546 | 69.3283 | 69.5343 | 2.3666 | -53.5629 | 69.5801 | -53.4943 | -53.5583 | -52.3682 | 26.0513 | -53.3066 | 69.516 | 69.4427 | -53.5355 | -53.54 | -0.26093 | -0.32501 | -0.09613 | 122.7676 | -0.32959 | -0.004577 | -0.3479 | -0.30212 | -0.3067 | -0.16022 | 0.86517 | -0.073243 | 0.23346 | -0.23346 | 122.8134 | 122.5616 | 55.6 | -123.2346 | 122.7493 | 122.6761 | 79.2847 | -123.2162
2997.0156 | 123.1384 | -52.0386 | 70.8389 | -0.16037 | 0.010226 | 0.06825 | 0.073081 | 0.12864 | 0.00013675 | -0.0055821 | 0.77805 | -0.010408 | 0.062342 | 0.055476 | 0.008908 | -0.013683 | 70.7153 | 70.9167 | 2.6001 | -52.272 | 70.9259 | -52.1576 | -52.2629 | -51.004 | 27.2873 | -52.1072 | 70.8435 | 70.7657 | -52.2675 | -52.2766 | -0.11902 | -0.2243 | 0.086975 | 122.9553 | -0.23346 | -0.009156 | -0.1236 | -0.22888 | -0.23804 | 0.004578 | 1.0345 | -0.068665 | 0.16937 | -0.073242 | 122.9645 | 122.7539 | 54.6387 | -123.1018 | 122.8821 | 122.8043 | 79.3259 | -123.1155
2998.0156 | 123.1201 | -53.5583 | 69.3192 | 0.50339 | 0.01044 | 0.070387 | 0.074149 | 0.12672 | -0.0017859 | -0.0077183 | 0.068512 | -0.0099806 | 0.061701 | 0.054194 | 0.0076264 | -0.012828 | 69.0765 | 69.2688 | 2.2568 | -53.7827 | 69.3787 | -53.6774 | -53.7415 | -52.4734 | 26.0468 | -53.6499 | 69.4107 | 69.2642 | -53.7827 | -53.8284 | -0.11902 | -0.18311 | 0.059509 | 122.8271 | -0.2243 | -0.041199 | -0.24262 | -0.2243 | -0.27008 | 0.091553 | 1.0849 | -0.091552 | 0.17853 | -0.054932 | 122.937 | 122.6349 | 55.8151 | -123.0606 | 122.9691 | 122.8226 | 79.6051 | -123.1476
2999.0156 | 123.175 | -53.2516 | 69.6442 | -0.20615 | 0.010226 | 0.069746 | 0.069663 | 0.1295 | -0.0041357 | -0.0092137 | -0.015411 | -0.0097668 | 0.059992 | 0.055689 | 0.0076264 | -0.012614 | 69.7449 | 69.3832 | 2.0554 | -53.334 | 69.6854 | -53.3707 | -53.4805 | -52.2125 | 26.239 | -53.4073 | 69.5938 | 69.4839 | -53.5538 | -53.5538 | -0.11902 | -0.22888 | 0.041199 | 122.6349 | -0.082397 | 0.14648 | 0.10071 | -0.30212 | -0.30212 | -0.050354 | 1.0391 | -0.15564 | 0.14648 | -0.16022 | 122.937 | 122.9965 | 55.307 | -123.1247 | 122.8455 | 122.7356 | 79.4907 | -123.1979
3000.0156 | 123.1155 | -53.2196 | 69.6854 | 0.13718 | 0.0074491 | 0.069959 | 0.069876 | 0.13078 | -0.0011451 | -0.0064365 | 0.045624 | -0.01233 | 0.060846 | 0.055476 | 0.00784 | -0.010692 | 69.4336 | 69.6671 | 2.0279 | -53.4027 | 69.7403 | -53.3066 | -53.4073 | -52.1622 | 26.2207 | -53.3615 | 69.6991 | 69.5847 | -53.4622 | -53.4668 | -0.086976 | -0.18768 | 0.054931 | 122.8867 | -0.18311 | 0.004578 | -0.25177 | -0.24262 | -0.24719 | 0.013733 | 1.0574 | -0.14191 | 0.10529 | -0.10071 | 122.9599 | 122.6532 | 55.2475 | -123.0927 | 122.9187 | 122.8043 | 79.4403 | -123.1522
3001.0156 | 123.1247 | -53.6224 | 69.1864 | 0.068512 | 0.010013 | 0.069959 | 0.072226 | 0.12416 | -0.0017859 | -0.0060093 | 0.4805 | -0.011476 | 0.057428 | 0.05868 | 0.0076264 | -0.014323 | 69.2322 | 69.4244 | 2.0462 | -53.6041 | 69.5251 | -53.5721 | -53.6774 | -52.446 | 25.9689 | -53.7048 | 69.4336 | 69.2871 | -53.7781 | -53.8239 | 0.050354 | -0.054931 | 0.33875 | 123.0469 | 0.018311 | 0.073242 | 0.045777 | -0.15564 | -0.20142 | 0.24719 | 1.1765 | -0.082397 | 0.11902 | 0.10071 | 123.1476 | 122.8546 | 55.6686 | -122.8638 | 123.056 | 122.9095 | 79.5914 | -123.0103
3002.0156 | 123.1476 | -53.5583 | 69.3146 | -0.061188 | 0.0083035 | 0.069532 | 0.071158 | 0.12822 | -0.0017859 | -0.0066501 | 0.0074766 | -0.009126 | 0.062769 | 0.055476 | 0.0074126 | -0.013469 | 69.1635 | 69.342 | 2.1561 | -53.7643 | 69.3924 | -53.7048 | -53.7781 | -52.4094 | 26.033 | -53.7735 | 69.3649 | 69.223 | -53.7918 | -53.8376 | -0.14648 | -0.21973 | 0.07782 | 122.9004 | -0.20599 | 0.013733 | -0.15106 | -0.23346 | -0.27923 | 0.050354 | 1.149 | -0.21515 | 0.064086 | -0.091553 | 122.9507 | 122.7219 | 55.7144 | -123.0927 | 122.9233 | 122.7814 | 79.5914 | -123.1522
3003.0156 | 123.143 | -53.3615 | 69.4931 | -0.10696 | 0.0091581 | 0.069319 | 0.071158 | 0.12651 | -0.0015723 | -0.0077183 | -0.023041 | -0.011476 | 0.062982 | 0.055903 | 0.007199 | -0.013896 | 69.5801 | 69.8044 | 2.2339 | -53.3157 | 69.7906 | -53.2562 | -53.3478 | -52.2446 | 26.3168 | -53.3752 | 69.5663 | 69.4382 | -53.595 | -53.6591 | 0.10529 | 0.013733 | 0.29755 | 123.1659 | 0.045776 | 0.032043 | 0.086975 | -0.23346 | -0.29755 | 0.073242 | 1.1169 | -0.013733 | 0.28381 | -0.054932 | 123.1522 | 122.9416 | 55.5954 | -122.8409 | 122.9279 | 122.7997 | 79.6783 | -123.1522
3004.0156 | 123.143 | -52.8992 | 69.8959 | 1.8538 | 0.014499 | 0.073377 | 0.073935 | 0.13057 | 0.0037683 | -0.0066501 | 0.14481 | -0.0078442 | 0.061487 | 0.055476 | 0.0091216 | -0.014323 | 69.6579 | 69.7861 | 2.0599 | -53.302 | 69.8044 | -53.2333 | -53.3066 | -51.6907 | 26.5732 | -52.977 | 70.0607 | 69.9371 | -53.0731 | -53.1143 | -0.33417 | -0.40741 | -0.091553 | 122.6852 | -0.40283 | 0.004578 | -0.23804 | -0.17395 | -0.21515 | 0.1648 | 1.2085 | -0.07782 | 0.13733 | 0.041199 | 122.7036 | 122.5571 | 54.9591 | -123.2025 | 122.9599 | 122.8363 | 79.4724 | -123.0103
3005.0156 | 123.1155 | -53.6957 | 69.1589 | -0.00015269 | 0.0074491 | 0.071027 | 0.070731 | 0.12779 | -0.0028541 | -0.0070773 | -0.023041 | -0.011262 | 0.06106 | 0.056758 | 0.006131 | -0.01411 | 69.0445 | 69.2459 | 2.1011 | -53.833 | 69.3329 | -53.7735 | -53.833 | -52.4826 | 25.9735 | -53.6957 | 69.2871 | 69.1818 | -53.9062 | -53.9383 | -0.07782 | -0.13733 | 0.17395 | 122.9416 | -0.13733 | 0 | -0.11444 | -0.21057 | -0.24261 | 0.12817 | 1.2131 | 0 | 0.24261 | 0.022888 | 123.0286 | 122.7402 | 55.7968 | -122.9919 | 122.9828 | 122.8775 | 79.6692 | -123.0972
3006.0156 | 123.111 | -52.8076 | 70.0836 | 0.17532 | 0.014499 | 0.06825 | 0.070944 | 0.12736 | 0.0048363 | -0.0055821 | 0.030365 | -0.011903 | 0.06341 | 0.055689 | 0.008908 | -0.014537 | 69.7861 | 70.2118 | 2.092 | -53.27 | 69.9554 | -53.0869 | -53.2013 | -51.8097 | 26.532 | -52.9953 | 69.9783 | 69.8914 | -53.0914 | -53.0914 | -0.27924 | -0.39368 | -0.12817 | 123.0194 | -0.46234 | -0.068664 | -0.29755 | -0.28381 | -0.28381 | -0.10528 | 0.99793 | -0.18768 | 0.096131 | -0.19226 | 122.7631 | 122.5937 | 54.8996 | -123.2849 | 122.786 | 122.699 | 79.3396 | -123.175
3007.0156 | 123.1018 | -53.5492 | 69.2642 | 0.12955 | 0.010226 | 0.070387 | 0.071372 | 0.12864 | -0.00093145 | -0.0066501 | 0.21347 | -0.0089124 | 0.061701 | 0.057398 | 0.007199 | -0.011333 | 69.2001 | 69.3832 | 1.9684 | -53.7872 | 69.397 | -53.6774 | -53.7689 | -52.3773 | 25.9689 | -53.6362 | 69.397 | 69.31 | -53.7552 | -53.8055 | -0.12817 | -0.21973 | 0.13275 | 122.9324 | -0.23804 | -0.01831 | -0.064087 | -0.20599 | -0.25635 | 0.13275 | 1.1719 | -0.086975 | 0.16937 | 0.045777 | 122.9462 | 122.7493 | 55.5176 | -123.0331 | 122.9462 | 122.8592 | 79.5181 | -123.0698
3008.0156 | 123.1522 | -53.5675 | 69.191 | 0.20584 | 0.016635 | 0.069319 | 0.072867 | 0.13057 | 0.0039819 | -0.0030185 | 0.045624 | -0.010194 | 0.065546 | 0.055049 | 0.010617 | -0.013469 | 69.3054 | 69.4885 | 2.2385 | -53.5492 | 69.5114 | -53.5217 | -53.6316 | -52.1255 | 26.1841 | -53.2242 | 69.6396 | 69.5068 | -53.6453 | -53.7231 | 0.045776 | -0.064087 | 0.32044 | 123.056 | 0.018311 | 0.082398 | 0.11444 | -0.07782 | -0.15564 | 0.44861 | 1.442 | 0.34332 | 0.49896 | 0.31586 | 123.0789 | 122.8729 | 55.806 | -122.8226 | 123.2071 | 123.0743 | 79.7516 | -122.9141
3009.0156 | 123.111 | -53.3249 | 69.5389 | 0.015106 | 0.014926 | 0.068678 | 0.070517 | 0.13014 | 0.0022729 | -0.0034457 | 0.19821 | -0.010408 | 0.061701 | 0.056544 | 0.008908 | -0.014537 | 69.2734 | 69.4565 | 1.9684 | -53.627 | 69.4885 | -53.5446 | -53.5995 | -52.153 | 26.3306 | -53.3844 | 69.5892 | 69.4794 | -53.5355 | -53.5721 | -0.21973 | -0.27466 | -0.050354 | 122.7814 | -0.30212 | -0.027466 | -0.2655 | -0.21057 | -0.24719 | 0.050354 | 1.1719 | -0.059509 | 0.18768 | -0.059509 | 122.8134 | 122.5983 | 55.2933 | -123.1384 | 122.9141 | 122.8043 | 79.6555 | -123.111
3010.0156 | 123.1018 | -52.5742 | 70.285 | 0.19058 | 0.017489 | 0.068464 | 0.071372 | 0.12971 | 0.0027001 | -0.0045139 | 0.23636 | -0.0099806 | 0.062342 | 0.056971 | 0.0086944 | -0.013683 | 70.2072 | 70.3583 | 1.918 | -52.6978 | 70.4681 | -52.6199 | -52.7115 | -51.4023 | 26.738 | -52.6382 | 70.372 | 70.2713 | -52.7985 | -52.8214 | -0.045776 | -0.13733 | 0.18311 | 122.9324 | -0.1236 | 0.013733 | -0.07782 | -0.2243 | -0.24719 | 0.086975 | 1.1719 | -0.064087 | 0.18311 | -0.013733 | 123.0423 | 122.7814 | 54.4922 | -122.9965 | 122.9462 | 122.8455 | 79.3121 | -123.1064
3011.0156 | 123.23 | -53.4393 | 69.4336 | 0.44998 | 0.013003 | 0.0706 | 0.069235 | 0.12971 | 0.0020593 | -0.0049411 | 0.21347 | -0.009126 | 0.061914 | 0.054835 | 0.0082672 | -0.013896 | 69.3008 | 69.3787 | 1.7944 | -53.7231 | 69.4153 | -53.6407 | -53.7415 | -52.2308 | 26.1612 | -53.4897 | 69.4839 | 69.3512 | -53.6911 | -53.7323 | -0.20142 | -0.30212 | -0.018311 | 122.818 | -0.28381 | 0.01831 | -0.13275 | -0.25177 | -0.29297 | 0.050354 | 1.2085 | -0.050354 | 0.24262 | -0.082398 | 122.8546 | 122.7402 | 55.2338 | -123.175 | 122.9233 | 122.7905 | 79.6005 | -123.1659
3012.0156 | 123.0835 | -53.5858 | 69.3146 | 0.11429 | 0.018558 | 0.065473 | 0.072226 | 0.128 | 0.0037683 | -0.0062229 | 0.19821 | -0.0082716 | 0.064905 | 0.057612 | 0.0082672 | -0.012614 | 69.2322 | 69.278 | 1.8311 | -53.8055 | 69.4977 | -53.6362 | -53.7506 | -52.446 | 25.8316 | -53.801 | 69.3878 | 69.3008 | -53.8101 | -53.833 | -0.050354 | -0.1648 | 0.18311 | 122.8638 | -0.21973 | -0.054932 | -0.082397 | -0.22431 | -0.24719 | 0.073242 | 1.1398 | -0.21515 | 0.032044 | -0.013733 | 123.0835 | 122.818 | 55.4169 | -123.0652 | 122.9736 | 122.8867 | 79.4174 | -123.1476
3013.0156 | 123.1522 | -52.6611 | 70.2118 | 0.20584 | 0.015353 | 0.068678 | 0.071585 | 0.13057 | 0.0014185 | -0.0062229 | 0.22873 | -0.0078442 | 0.063196 | 0.055903 | 0.01019 | -0.01411 | 70.1111 | 70.2621 | 2.1057 | -52.8122 | 70.3079 | -52.7435 | -52.8397 | -51.4664 | 26.4954 | -52.8946 | 70.2393 | 70.1294 | -52.9221 | -52.9312 | -0.082397 | -0.17853 | 0.09613 | 122.9233 | -0.15106 | 0.027466 | -0.10071 | -0.26093 | -0.27008 | 0.027466 | 1.1948 | -0.23346 | 0.036621 | -0.082397 | 122.9691 | 122.7722 | 54.7668 | -123.0515 | 122.9004 | 122.7905 | 79.1565 | -123.143
3014.0156 | 123.0515 | -54.0848 | 68.8385 | 0.15244 | 0.017489 | 0.067182 | 0.074362 | 0.12971 | 0.0037683 | -0.0034457 | -2.9909 | -0.0082716 | 0.065973 | 0.058039 | 0.0069854 | -0.014537 | 68.6737 | 68.7607 | 1.7441 | -54.2358 | 68.9987 | -54.1077 | -54.2725 | -52.8992 | 25.4288 | -54.245 | 68.9896 | 68.8889 | -54.2587 | -54.3045 | -0.022888 | -0.18768 | 0.16022 | 122.8455 | -0.15106 | 0.036621 | -0.16479 | -0.17395 | -0.21973 | 0.15106 | 1.1856 | -0.16022 | 0.059509 | 0.050354 | 123.0835 | 122.7585 | 55.8289 | -123.111 | 123.0743 | 122.9736 | 79.5135 | -123.143
3015.0156 | 123.0881 | -52.858 | 69.9966 | 0.2211 | 0.015353 | 0.069959 | 0.067526 | 0.12907 | -0.00071785 | -0.0049411 | 0.20584 | -0.0093396 | 0.063623 | 0.055689 | 0.0080536 | -0.01176 | 69.8914 | 69.9966 | 1.9043 | -53.0365 | 70.1569 | -52.9358 | -53.0411 | -51.6403 | 26.6281 | -53.0273 | 70.1385 | 70.0241 | -53.0731 | -53.1097 | -0.07782 | -0.18311 | 0.16022 | 122.8546 | -0.17853 | 0.004578 | -0.10529 | -0.21515 | -0.25177 | 0.14191 | 1.2177 | -0.16937 | 0.082397 | 0.027466 | 123.0148 | 122.7493 | 54.7623 | -123.0377 | 122.9965 | 122.8821 | 79.4861 | -123.1064
3016.0156 | 123.0331 | -52.5879 | 70.3262 | 0.15244 | 0.01514 | 0.066328 | 0.073294 | 0.12886 | 0.0020593 | -0.0038731 | 0.56442 | -0.0084852 | 0.064905 | 0.056544 | 0.0093354 | -0.013255 | 70.1935 | 70.3079 | 1.9592 | -52.7161 | 70.5368 | -52.6154 | -52.7481 | -51.4252 | 26.9531 | -52.6108 | 70.4544 | 70.3857 | -52.7435 | -52.7664 | -0.027465 | -0.16022 | 0.21057 | 122.8958 | -0.12817 | 0.032044 | -0.13275 | -0.15564 | -0.17853 | 0.12817 | 1.1627 | -0.022888 | 0.15564 | 0.059509 | 123.1247 | 122.7814 | 54.5471 | -123.0743 | 123.0423 | 122.9736 | 79.541 | -123.0927
3017.0156 | 123.1201 | -52.9678 | 69.928 | 0.21347 | 0.017276 | 0.069105 | 0.071158 | 0.12736 | 0.00013675 | -0.0060093 | 0.24399 | -0.0061352 | 0.062555 | 0.056758 | 0.0082672 | -0.013255 | 69.8318 | 69.9509 | 1.8906 | -53.1052 | 70.1157 | -53.0182 | -53.1052 | -51.828 | 26.6693 | -53.064 | 69.9966 | 69.9371 | -53.1601 | -53.2104 | -0.050354 | -0.13733 | 0.18768 | 122.9187 | -0.13733 | 0 | -0.096131 | -0.19226 | -0.24261 | 0.068664 | 1.1398 | -0.096131 | 0.14648 | 0.009155 | 123.0835 | 122.7997 | 54.8584 | -123.0331 | 122.9645 | 122.905 | 79.6371 | -123.1384
3018.0156 | 123.0331 | -53.9932 | 68.9667 | -0.0383 | 0.018558 | 0.068891 | 0.07244 | 0.13249 | 0.0027001 | -0.0049411 | 0.030365 | -0.006349 | 0.065759 | 0.056117 | 0.0076264 | -0.010478 | 68.8568 | 68.9484 | 1.8402 | -54.1122 | 69.0903 | -53.9886 | -54.0848 | -52.9175 | 25.914 | -54.213 | 68.9621 | 68.9117 | -54.2358 | -54.2587 | 0.004578 | -0.091553 | 0.1236 | 122.9416 | -0.11902 | -0.027466 | -0.10986 | -0.24262 | -0.2655 | -0.004578 | 1.0757 | -0.21973 | 0.045776 | -0.054932 | 123.0835 | 122.85 | 55.8334 | -123.0515 | 122.9553 | 122.905 | 79.9072 | -123.2254
3019.0156 | 123.0881 | -53.7552 | 69.191 | -0.64865 | 0.014285 | 0.068678 | 0.069876 | 0.12971 | -0.00029045 | -0.0055821 | 0.19058 | -0.0078442 | 0.065119 | 0.05398 | 0.010831 | -0.010051 | 68.9255 | 69.0811 | 1.8997 | -53.9337 | 69.2963 | -53.8467 | -53.9291 | -52.6199 | 26.0559 | -53.8513 | 69.2917 | 69.1727 | -53.952 | -54.007 | -0.091553 | -0.17395 | 0.10529 | 122.8363 | -0.17853 | -0.004578 | -0.2655 | -0.19684 | -0.25177 | 0.10071 | 1.1353 | -0.09613 | 0.15564 | -0.018311 | 123.0515 | 122.6807 | 55.6549 | -123.1201 | 123.0469 | 122.9279 | 79.8111 | -123.1979
3020.0156 | 123.1155 | -53.9658 | 68.898 | 0.17532 | 0.010653 | 0.0706 | 0.070731 | 0.12971 | -0.0062721 | -0.0070773 | 0.30502 | -0.010408 | 0.064478 | 0.057826 | 0.0067718 | -0.011546 | 68.7195 | 68.9255 | 1.9867 | -54.158 | 68.9392 | -54.0802 | -54.1992 | -52.8717 | 26.0147 | -54.1168 | 68.9209 | 68.8385 | -54.213 | -54.2587 | -0.11444 | -0.23346 | 0.041199 | 122.8912 | -0.19226 | 0.041199 | -0.17853 | -0.24719 | -0.29297 | 0.022888 | 1.0941 | -0.15106 | 0.14191 | -0.059509 | 122.905 | 122.6852 | 55.9525 | -123.0972 | 122.8867 | 122.8043 | 79.9805 | -123.1567
3021.0156 | 123.1155 | -52.8625 | 70.0195 | 0.19821 | 0.015994 | 0.06825 | 0.070944 | 0.12928 | -0.00071785 | -0.0079319 | 0.2211 | -0.010621 | 0.065546 | 0.055689 | 0.0099762 | -0.01411 | 69.6991 | 69.841 | 2.1011 | -53.2059 | 70.0058 | -53.0731 | -53.1876 | -51.741 | 26.8341 | -52.8488 | 70.0974 | 69.9692 | -53.1052 | -53.1326 | -0.21057 | -0.32501 | -0.013733 | 122.7036 | -0.34332 | -0.018311 | -0.32043 | -0.24262 | -0.27008 | 0.07782 | 1.1215 | 0.013733 | 0.28381 | -0.050354 | 122.8683 | 122.5616 | 54.9637 | -123.2071 | 122.9599 | 122.8317 | 79.6967 | -123.1522
3022.0156 | 123.0606 | -53.476 | 69.4336 | -0.076447 | 0.019412 | 0.070173 | 0.073081 | 0.12843 | 0.0027001 | -0.0070773 | 0.28976 | -0.0093396 | 0.063196 | 0.057398 | 0.009549 | -0.01176 | 69.2276 | 69.3329 | 1.8219 | -53.6774 | 69.4794 | -53.6133 | -53.714 | -52.3315 | 26.4404 | -53.7506 | 69.4931 | 69.4336 | -53.6774 | -53.7186 | -0.13733 | -0.23804 | 0.045776 | 122.8088 | -0.20142 | 0.036621 | -0.20599 | -0.20142 | -0.24262 | 0.059509 | 1.1444 | -0.27466 | -0.032043 | 0 | 122.9553 | 122.7036 | 55.2979 | -123.1476 | 122.9691 | 122.9095 | 79.9164 | -123.1522
3023.0156 | 123.0789 | -53.6407 | 69.2642 | 0.36606 | 0.01813 | 0.070814 | 0.071585 | 0.128 | 0.00056395 | -0.0070773 | 0.16769 | -0.0084852 | 0.063837 | 0.05398 | 0.0091216 | -0.010692 | 69.0903 | 69.1864 | 1.9043 | -53.8422 | 69.4107 | -53.7415 | -53.8376 | -52.5467 | 26.1978 | -53.7872 | 69.3695 | 69.2917 | -53.8605 | -53.9017 | -0.10071 | -0.19684 | 0.14648 | 122.8271 | -0.20142 | -0.004578 | -0.17395 | -0.21973 | -0.26093 | 0.10529 | 1.0941 | -0.14648 | 0.11444 | 0.027466 | 123.0515 | 122.731 | 55.545 | -123.1018 | 123.0103 | 122.9324 | 79.8386 | -123.1659
3024.0156 | 123.0789 | -54.2908 | 68.6462 | -0.16037 | 0.01813 | 0.068678 | 0.073508 | 0.1295 | -7.6852e-05 | -0.0079319 | -0.14511 | -0.0082716 | 0.067682 | 0.055049 | 0.0059174 | -0.013469 | 68.3304 | 68.4769 | 1.6159 | -54.538 | 68.6508 | -54.483 | -54.5517 | -53.183 | 25.6531 | -54.4785 | 68.6508 | 68.5959 | -54.5609 | -54.57 | -0.19226 | -0.26093 | 0.004578 | 122.7676 | -0.24719 | 0.013733 | -0.31586 | -0.27008 | -0.27924 | 0.004578 | 1.1078 | -0.18768 | 0.091552 | -0.050354 | 122.9416 | 122.6212 | 55.9067 | -123.1979 | 122.9416 | 122.8867 | 79.9438 | -123.2162
3025.0156 | 123.1613 | -53.3203 | 69.5389 | -0.076447 | 0.010653 | -0.03557 | 0.071585 | 0.12693 | -0.0064857 | -0.0098545 | 0.15244 | -0.01233 | 0.059992 | 0.054835 | 0.0039948 | -0.012828 | 69.342 | 69.5297 | 1.9867 | -53.5217 | 69.5847 | -53.4622 | -53.5355 | -52.1439 | 26.4725 | -53.5904 | 69.5938 | 69.5114 | -53.5675 | -53.5812 | -0.14191 | -0.21515 | 0.045777 | 122.85 | -0.20142 | 0.013732 | -0.19684 | -0.24719 | -0.26093 | 0.054932 | 1.1765 | -0.27008 | -0.009155 | -0.027465 | 122.905 | 122.6624 | 55.307 | -123.0743 | 122.9141 | 122.8317 | 79.7928 | -123.1201
3026.0156 | 123.0972 | -53.2562 | 69.6808 | -0.19089 | 0.016635 | 0.072096 | 0.073508 | 0.12822 | 0.0024865 | -0.0055821 | -0.045929 | -0.0082716 | 0.064264 | 0.055476 | 0.00784 | -0.014537 | 69.6075 | 69.7632 | 1.8997 | -53.2745 | 69.9051 | -53.2196 | -53.334 | -52.0203 | 26.5961 | -53.389 | 69.8227 | 69.7128 | -53.4439 | -53.5034 | 0.036622 | -0.077819 | 0.2243 | 123.0194 | -0.01831 | 0.059509 | -0.073242 | -0.18768 | -0.24719 | 0.14191 | 1.236 | -0.13275 | 0.11444 | 0.032044 | 123.1613 | 122.8638 | 55.1559 | -123.0148 | 123.0789 | 122.9691 | 79.8523 | -123.1842
3027.0156 | 123.024 | -51.8921 | 71.077 | 0.053253 | 0.018985 | 0.069532 | 0.071585 | 0.12736 | 0.0016321 | -0.0062229 | 0.030365 | -0.010194 | 0.065332 | 0.055903 | 0.009549 | -0.012401 | 70.8023 | 70.9167 | 1.918 | -52.0844 | 71.109 | -51.9928 | -52.0569 | -50.7385 | 27.5711 | -51.9791 | 71.1731 | 71.0678 | -52.0889 | -52.1118 | -0.10071 | -0.16479 | 0.032044 | 122.8088 | -0.19226 | -0.027466 | -0.27466 | -0.19684 | -0.21973 | 0.096131 | 1.1536 | -0.086975 | 0.13275 | -0.009155 | 123.0011 | 122.6944 | 53.8101 | -123.1338 | 123.0652 | 122.9599 | 79.4632 | -123.1888
3028.0156 | 123.0469 | -53.6636 | 69.2734 | -0.17563 | 0.014499 | 0.068464 | 0.071799 | 0.12843 | -0.00050425 | -0.0072911 | -0.2214 | -0.0089124 | 0.065119 | 0.055689 | 0.006131 | -0.011333 | 69.0674 | 69.1727 | 1.9226 | -53.8376 | 69.3924 | -53.7277 | -53.8559 | -52.4918 | 26.3351 | -53.7735 | 69.397 | 69.3008 | -53.8467 | -53.8971 | -0.064087 | -0.19226 | 0.11902 | 122.8363 | -0.17395 | 0.018311 | -0.20599 | -0.18311 | -0.23346 | 0.1236 | 1.1719 | -0.10986 | 0.1236 | 0.027466 | 123.056 | 122.731 | 55.5862 | -123.1293 | 123.0606 | 122.9645 | 79.9988 | -123.1705
3029.0156 | 123.0652 | -52.6566 | 70.2621 | -0.053558 | 0.01578 | 0.068464 | 0.074149 | 0.12864 | 0.00013675 | -0.0060093 | -0.061188 | -0.008058 | 0.064478 | 0.059107 | 0.0084808 | -0.012828 | 70.1981 | 70.3217 | 1.7807 | -52.7252 | 70.4773 | -52.652 | -52.7435 | -51.4755 | 27.0081 | -52.7481 | 70.3629 | 70.2805 | -52.8809 | -52.9129 | 0.004577 | -0.086975 | 0.21515 | 122.9782 | -0.068665 | 0.01831 | -0.064087 | -0.2243 | -0.25635 | 0.10071 | 1.181 | -0.091553 | 0.16479 | 0.018311 | 123.1338 | 122.8546 | 54.4373 | -123.0057 | 123.0194 | 122.937 | 79.6646 | -123.175
3030.0156 | 123.143 | -52.2537 | 70.6055 | 0.31265 | 0.012149 | 0.072523 | 0.067954 | 0.12886 | -0.0039221 | -0.0064365 | 0.28214 | -0.010408 | 0.063196 | 0.055262 | 0.007199 | -0.011333 | 70.4773 | 70.665 | 1.9547 | -52.4231 | 70.6833 | -52.327 | -52.446 | -51.1322 | 27.42 | -52.3224 | 70.6421 | 70.5643 | -52.5192 | -52.5558 | -0.073242 | -0.19226 | 0.07782 | 122.9187 | -0.16937 | 0.022888 | -0.12817 | -0.2655 | -0.30212 | 0.036621 | 1.1215 | -0.068665 | 0.23346 | -0.041199 | 122.937 | 122.731 | 54.2084 | -123.0515 | 122.8958 | 122.818 | 79.6738 | -123.1613
3031.0156 | 123.0469 | -52.5009 | 70.4178 | -0.12985 | 0.017062 | 0.068037 | 0.073294 | 0.12993 | 0.0014185 | -0.0077183 | -0.045929 | -0.010194 | 0.067682 | 0.057398 | 0.0082672 | -0.0094102 | 70.047 | 70.166 | 1.7761 | -52.8488 | 70.3217 | -52.7618 | -52.8717 | -51.4206 | 27.1683 | -52.4368 | 70.4636 | 70.3949 | -52.7573 | -52.7756 | -0.26093 | -0.37079 | -0.096131 | 122.6669 | -0.3479 | 0.022888 | -0.37079 | -0.25635 | -0.27466 | 0.045776 | 1.0803 | 0.064087 | 0.33874 | -0.022889 | 122.8226 | 122.5479 | 54.277 | -123.2895 | 122.9645 | 122.8958 | 79.6692 | -123.1934
3032.0156 | 123.0377 | -53.4439 | 69.4519 | -0.25192 | 0.013644 | 0.070173 | 0.069876 | 0.12928 | -0.0024269 | -0.0060093 | -0.11459 | -0.007417 | 0.060633 | 0.055262 | 0.0059174 | -0.012401 | 69.6304 | 69.8318 | 1.7899 | -53.2608 | 69.9051 | -53.183 | -53.302 | -52.2079 | 26.5274 | -53.476 | 69.6762 | 69.5526 | -53.6087 | -53.6957 | 0.26093 | 0.14191 | 0.45319 | 123.2758 | 0.18311 | 0.041199 | 0.17853 | -0.1648 | -0.25177 | 0.2243 | 1.236 | -0.032043 | 0.21973 | 0.10071 | 123.349 | 123.0743 | 55.2338 | -122.7539 | 123.1201 | 122.9965 | 79.9713 | -123.1476
3033.0156 | 123.0835 | -52.2079 | 70.7474 | -0.19852 | 0.015353 | 0.069959 | 0.072867 | 0.12928 | -0.00050425 | -0.0049411 | -0.17563 | -0.010621 | 0.067041 | 0.056758 | 0.011685 | -0.012828 | 70.4407 | 70.6238 | 1.9592 | -52.4094 | 70.7932 | -52.3544 | -52.4323 | -51.0361 | 27.3972 | -52.2766 | 70.7748 | 70.697 | -52.4506 | -52.5055 | -0.14648 | -0.2243 | 0.045777 | 122.8317 | -0.20142 | 0.022888 | -0.3067 | -0.24262 | -0.29755 | 0.027466 | 1.1719 | -0.068664 | 0.22888 | -0.050354 | 123.0011 | 122.6486 | 54.1672 | -123.1796 | 122.9828 | 122.905 | 79.6051 | -123.2529
3034.0156 | 123.024 | -53.0273 | 69.9188 | -0.20615 | 0.0093717 | 0.070387 | 0.070517 | 0.12822 | -0.0032813 | -0.0062229 | -0.27481 | -0.011049 | 0.06341 | 0.056758 | 0.0048492 | -0.010478 | 69.7678 | 69.9554 | 2.005 | -53.1372 | 70.047 | -53.0502 | -53.1189 | -51.8372 | 26.8204 | -53.1281 | 70.047 | 69.9234 | -53.2242 | -53.2471 | -0.022888 | -0.091552 | 0.12817 | 122.9828 | -0.10986 | -0.018311 | -0.15106 | -0.19684 | -0.21973 | 0.12817 | 1.1902 | -0.10071 | 0.11902 | 0.004578 | 123.0743 | 122.7951 | 55.0323 | -123.0377 | 123.0743 | 122.9507 | 79.8477 | -123.1659
3035.0156 | 123.1567 | -52.4506 | 70.4224 | 0.21347 | 0.015353 | 0.067396 | 0.07244 | 0.12822 | 0.00099115 | -0.0068637 | 0.40421 | -0.011049 | 0.065759 | 0.058039 | 0.0091216 | -0.011974 | 70.2759 | 70.4498 | 2.211 | -52.6474 | 70.5322 | -52.565 | -52.652 | -51.3016 | 27.0905 | -52.5604 | 70.4681 | 70.3812 | -52.6611 | -52.7161 | -0.11444 | -0.20142 | 0.10986 | 122.9004 | -0.19684 | 0.004578 | -0.14648 | -0.21057 | -0.2655 | 0.045777 | 1.149 | -0.10986 | 0.15564 | -0.041198 | 122.9828 | 122.7264 | 54.6616 | -123.0743 | 122.9187 | 122.8317 | 79.541 | -123.1384
3036.0156 | 123.1201 | -53.0365 | 69.8822 | -0.22903 | 0.011081 | 0.069105 | 0.069876 | 0.13014 | -0.0039221 | -0.0072911 | -0.10696 | -0.011262 | 0.062982 | 0.055262 | 0.0048492 | -0.013683 | 69.8273 | 70.0287 | 2.0782 | -53.0548 | 70.0607 | -52.9953 | -53.0594 | -51.7364 | 26.6922 | -53.1372 | 70.0058 | 69.9234 | -53.2059 | -53.27 | 0.041199 | -0.022888 | 0.17853 | 123.0652 | -0.018311 | 0.004577 | -0.054931 | -0.16937 | -0.23346 | 0.1236 | 1.3 | -0.10071 | 0.13275 | 0.041199 | 123.0972 | 122.8638 | 55.1147 | -122.9416 | 123.0423 | 122.9599 | 79.7287 | -123.1522
3037.0156 | 123.0789 | -52.6016 | 70.4224 | -0.33585 | 0.015567 | 0.068464 | 0.073721 | 0.12779 | 0.0012047 | -0.0079319 | -0.20615 | -0.0093396 | 0.064691 | 0.057185 | 0.009549 | -0.013683 | 69.5343 | 69.7037 | 1.8219 | -53.2745 | 69.9005 | -53.2059 | -53.3066 | -51.7502 | 26.651 | -52.9953 | 70.1202 | 70.0699 | -53.0273 | -52.9678 | -0.60425 | -0.70496 | -0.52185 | 122.3053 | -0.67291 | 0.032044 | -0.88806 | -0.42572 | -0.36621 | -0.30212 | 0.85144 | -0.39368 | -0.027466 | -0.35248 | 122.5021 | 122.1359 | 54.4235 | -123.7289 | 122.7219 | 122.6715 | 79.2526 | -123.3902
3038.0156 | 123.1979 | -53.0136 | 69.9188 | -0.0077822 | 0.0072355 | 0.072309 | 0.069876 | 0.12693 | -0.0060585 | -0.0081455 | 0.0914 | -0.011049 | 0.062342 | 0.055476 | 0.0057038 | -0.011333 | 69.7952 | 70.0378 | 2.916 | -53.0777 | 70.0607 | -53.0228 | -53.1097 | -51.7639 | 26.6098 | -53.0457 | 69.9646 | 69.8593 | -53.2013 | -53.2333 | -0.009155 | -0.09613 | 0.14191 | 123.0515 | -0.064087 | 0.032043 | -0.1236 | -0.18768 | -0.21973 | 0.045777 | 1.2497 | -0.032043 | 0.18768 | -0.059509 | 123.0743 | 122.8088 | 55.9296 | -123.0286 | 122.9782 | 122.8729 | 79.6234 | -123.1522
3039.0156 | 123.024 | -51.7822 | 71.1731 | -0.25192 | 0.015567 | 0.07295 | 0.073508 | 0.12928 | -7.6852e-05 | -0.0089999 | -0.17563 | -0.010408 | 0.063196 | 0.056544 | 0.0067718 | -0.011546 | 70.9854 | 71.1456 | 2.1652 | -51.9058 | 71.2601 | -51.8234 | -51.9241 | -50.6607 | 27.4017 | -51.8417 | 71.2372 | 71.1273 | -52.0065 | -52.002 | -0.041198 | -0.14191 | 0.086975 | 122.9279 | -0.1236 | 0.01831 | -0.18768 | -0.2243 | -0.21973 | 0.064087 | 1.1215 | -0.059509 | 0.16022 | -0.045777 | 123.0423 | 122.7676 | 53.9474 | -123.0972 | 123.0194 | 122.9095 | 79.184 | -123.175
3040.0156 | 123.0286 | -52.5513 | 70.3995 | 0.12955 | 0.014712 | 0.069959 | 0.071158 | 0.1295 | 0.0037683 | -0.0062229 | 3.2881 | -0.0097668 | 0.062982 | 0.054835 | 0.013181 | -0.012828 | 70.2301 | 70.3857 | 3.2776 | -52.6474 | 70.5917 | -52.5375 | -52.6428 | -51.4709 | 26.8845 | -52.7802 | 70.491 | 70.3537 | -52.7802 | -52.803 | 0.013733 | -0.091552 | 0.19226 | 122.937 | -0.09613 | -0.004578 | -0.16937 | -0.22888 | -0.25177 | 0.091553 | 1.0803 | -0.22888 | 0.022889 | -0.045776 | 123.143 | 122.7814 | 55.8289 | -123.0423 | 123.0423 | 122.905 | 79.4357 | -123.2025
3041.0156 | 123.024 | -51.4297 | 71.4981 | -0.22903 | 0.012149 | 0.070173 | 0.072226 | 0.1295 | -0.0013587 | -0.0083591 | -0.13748 | -0.0099806 | 0.061914 | 0.056971 | 0.0074126 | -0.012401 | 71.4111 | 71.5759 | 5.4062 | -51.4984 | 71.6995 | -51.4023 | -51.4893 | -50.386 | 27.5116 | -51.6174 | 71.5302 | 71.4706 | -51.6998 | -51.709 | 0.027466 | -0.059509 | 0.20142 | 123.0057 | -0.068664 | -0.009155 | -0.086975 | -0.27008 | -0.27923 | 0.032043 | 1.0437 | -0.18768 | 0.091552 | -0.027466 | 123.1293 | 122.8409 | 56.8359 | -122.9874 | 122.9599 | 122.9004 | 78.9413 | -123.2071
3042.0156 | 123.1384 | -53.1876 | 69.6945 | -0.19089 | 0.0087307 | 0.071027 | 0.07009 | 0.13014 | -0.0052039 | -0.0079319 | -0.061188 | -0.0097668 | 0.061701 | 0.056544 | 0.0076264 | -0.012614 | 69.5389 | 69.7769 | 4.1565 | -53.3386 | 69.7495 | -53.3066 | -53.3661 | -51.9562 | 26.3031 | -53.2608 | 69.7403 | 69.6396 | -53.4439 | -53.4622 | -0.11902 | -0.17853 | 0.054932 | 122.9645 | -0.15106 | 0.027466 | -0.15564 | -0.25635 | -0.27466 | 0.045776 | 1.2314 | -0.073242 | 0.20142 | -0.054932 | 122.937 | 122.7264 | 57.3441 | -123.0606 | 122.9279 | 122.8271 | 79.4907 | -123.1567
3043.0156 | 123.0652 | -53.1372 | 69.7586 | -0.22141 | 0.0089443 | 0.070387 | 0.070731 | 0.12886 | -0.0017859 | -0.010282 | -0.14511 | -0.011476 | 0.061914 | 0.057185 | 0.0080536 | -0.012828 | 69.7403 | 69.9051 | 3.8452 | -53.3707 | 69.8593 | -53.2562 | -53.3661 | -51.9516 | 26.4587 | -53.2013 | 69.8135 | 69.7128 | -53.3569 | -53.3981 | -0.11902 | -0.22888 | 0.10071 | 123.0423 | -0.23346 | -0.004578 | -0.018311 | -0.21973 | -0.26093 | 0.054932 | 1.1856 | -0.064087 | 0.19684 | -0.045776 | 122.9965 | 122.8775 | 56.9824 | -123.1247 | 122.9507 | 122.85 | 79.5959 | -123.1567
3044.0156 | 123.2025 | -52.7252 | 70.1248 | -0.16037 | 0.010013 | 0.069319 | 0.073294 | 0.12736 | -0.0024269 | -0.0087863 | -0.091705 | -0.013826 | 0.059778 | 0.05633 | 0.0076264 | -0.013042 | 70.1294 | 70.3629 | 4.1107 | -52.7985 | 70.3308 | -52.7206 | -52.8076 | -51.4297 | 26.9485 | -52.5284 | 70.3354 | 70.285 | -52.8717 | -52.9404 | 0.004578 | -0.082397 | 0.20599 | 123.0881 | -0.073242 | 0.009155 | 0.004578 | -0.14648 | -0.21515 | 0.21057 | 1.2955 | 0.19684 | 0.41199 | 0.16022 | 123.056 | 122.8546 | 56.8359 | -122.9324 | 123.0606 | 123.0103 | 79.6738 | -123.0652
3045.0156 | 123.1613 | -51.3886 | 71.4569 | -2.2966 | 0.012576 | 0.066755 | 0.070517 | 0.13099 | -0.0015723 | -0.0047275 | -0.099335 | -0.012117 | 0.064051 | 0.056758 | 0.007199 | -0.013683 | 71.3745 | 71.7453 | 3.1036 | -51.4297 | 71.7133 | -51.3474 | -51.4252 | -50.1846 | 27.7679 | -51.4435 | 71.5805 | 71.4752 | -51.5991 | -51.6449 | 0.041199 | -0.036621 | 0.25635 | 123.1338 | -0.041199 | -0.004578 | -0.082397 | -0.21057 | -0.25635 | 0.1236 | 1.2039 | -0.054931 | 0.20142 | 0.018311 | 123.1018 | 122.7631 | 54.4922 | -122.8821 | 122.9691 | 122.8638 | 79.1565 | -123.1018
3046.0156 | 123.1476 | -52.6154 | 70.2942 | -0.00015269 | 0.0076627 | 0.071668 | 0.072867 | 0.12993 | -0.0024269 | -0.0081455 | 0.022736 | -0.010408 | 0.062769 | 0.056117 | 0.0084808 | -0.011333 | 69.9738 | 70.166 | 3.0029 | -52.8992 | 70.2621 | -52.8076 | -52.9083 | -51.5213 | 26.6968 | -52.858 | 70.2301 | 70.1569 | -52.8763 | -52.9266 | -0.19226 | -0.29297 | -0.032043 | 122.7814 | -0.28381 | 0.009155 | -0.32043 | -0.26093 | -0.31128 | -0.064086 | 1.0941 | -0.24262 | 0.068665 | -0.13733 | 122.8775 | 122.5891 | 55.6183 | -123.2025 | 122.8455 | 122.7722 | 79.3121 | -123.2208
3047.0156 | 123.1155 | -52.5101 | 70.3949 | -0.14511 | 0.010013 | 0.0706 | 0.071158 | 0.12993 | 0.00099115 | -0.0092137 | -0.13748 | -0.010408 | 0.064905 | 0.055476 | 0.0082672 | -0.013896 | 70.2896 | 70.4544 | 2.3483 | -52.7206 | 70.4544 | -52.6245 | -52.7344 | -51.3382 | 27.0584 | -52.6062 | 70.3949 | 70.3445 | -52.7298 | -52.7344 | -0.11444 | -0.2243 | 0.05951 | 122.9645 | -0.21057 | 0.013733 | -0.10528 | -0.21973 | -0.2243 | 0 | 1.1719 | -0.09613 | 0.12817 | -0.050354 | 122.9645 | 122.7997 | 54.8584 | -123.1293 | 122.905 | 122.8546 | 79.5685 | -123.1293
3048.0156 | 123.143 | -53.3249 | 69.5801 | -0.0077822 | 0.0095853 | 0.069746 | 0.071585 | 0.12864 | -0.0015723 | -0.0083591 | 0.015106 | -0.010408 | 0.061273 | 0.056544 | 0.0091216 | -0.012614 | 69.136 | 69.3329 | 2.298 | -53.801 | 69.3558 | -53.7277 | -53.8239 | -52.0935 | 26.4633 | -53.2333 | 69.5938 | 69.4931 | -53.5446 | -53.5629 | -0.40283 | -0.49896 | -0.2243 | 122.6578 | -0.47607 | 0.022889 | -0.44403 | -0.21973 | -0.23804 | 0.013733 | 1.2314 | 0.091553 | 0.32959 | -0.086975 | 122.6807 | 122.4609 | 55.6229 | -123.4039 | 122.9187 | 122.818 | 79.7882 | -123.143
3049.0156 | 123.1567 | -52.2766 | 70.5917 | -0.168 | 0.0078763 | 0.06825 | 0.072012 | 0.12758 | -0.0026405 | -0.0083591 | 0.74753 | -0.0089124 | 0.063623 | 0.055476 | 0.007199 | -0.012401 | 70.4773 | 70.7245 | 2.2888 | -52.4277 | 70.665 | -52.3682 | -52.4597 | -51.1002 | 27.2919 | -52.3544 | 70.6787 | 70.5734 | -52.4918 | -52.5146 | -0.091553 | -0.18311 | 0.073242 | 123.0011 | -0.15106 | 0.032044 | -0.11444 | -0.21515 | -0.23804 | 0.086975 | 1.1765 | -0.07782 | 0.16022 | -0.018311 | 122.9416 | 122.7539 | 54.5654 | -123.0515 | 122.9553 | 122.85 | 79.5685 | -123.1064
3050.0156 | 123.1659 | -52.4277 | 70.4086 | -0.084076 | 0.0091581 | 0.071027 | 0.073508 | 0.12758 | -0.0041357 | -0.0085727 | -0.0077819 | -0.0097668 | 0.061487 | 0.056758 | 0.0059174 | -0.013469 | 70.34 | 70.5734 | 2.1057 | -52.5284 | 70.6055 | -52.4643 | -52.565 | -51.1185 | 27.0493 | -52.5421 | 70.5551 | 70.4407 | -52.6199 | -52.6932 | -0.036621 | -0.13733 | 0.19684 | 123.0011 | -0.10071 | 0.036621 | -0.068664 | -0.19226 | -0.2655 | 0.14648 | 1.3092 | -0.11444 | 0.15106 | 0.032044 | 123.0331 | 122.7676 | 54.5334 | -122.9736 | 122.9828 | 122.8683 | 79.4769 | -123.1018
3051.0156 | 123.143 | -53.0823 | 69.809 | -0.19852 | 0.010226 | 0.070387 | 0.080557 | 0.12864 | 0.0037683 | -0.0049411 | -0.16037 | -0.010621 | 0.060846 | 0.05633 | 0.0065582 | -0.014537 | 69.4427 | 69.9326 | 2.005 | -53.3249 | 69.8456 | -53.1921 | -53.302 | -51.8463 | 26.3809 | -53.1189 | 69.8593 | 69.7449 | -53.2883 | -53.3112 | -0.10986 | -0.21973 | 0.036621 | 123.0148 | -0.24262 | -0.022888 | -0.36621 | -0.20599 | -0.22888 | 0.050354 | 1.236 | -0.036621 | 0.19226 | -0.064087 | 122.9279 | 122.525 | 55.0873 | -123.111 | 122.9416 | 122.8271 | 79.4632 | -123.1201
3052.0156 | 123.1293 | -51.091 | 71.7957 | 0.037994 | 0.0093717 | 0.069959 | 0.071585 | 0.12779 | -0.0011451 | -0.0060093 | 0.083771 | -0.011903 | 0.063196 | 0.055049 | 0.0076264 | -0.012614 | 71.6858 | 71.8643 | 2.3483 | -51.2192 | 71.9421 | -51.1139 | -51.2283 | -49.8688 | 27.8275 | -51.0544 | 71.8689 | 71.8048 | -51.2924 | -51.3245 | -0.022889 | -0.13733 | 0.14648 | 122.9553 | -0.12817 | 0.009156 | -0.10986 | -0.20142 | -0.23346 | 0.073242 | 1.2222 | 0.036621 | 0.27008 | 0.009156 | 123.0331 | 122.7768 | 53.4393 | -123.024 | 122.9599 | 122.8958 | 78.9185 | -123.1201
3053.0156 | 123.2529 | -53.0411 | 69.8364 | -0.10696 | 0.012362 | 0.071668 | 0.071158 | 0.128 | -0.0011451 | -0.0066501 | -0.14511 | -0.011476 | 0.061487 | 0.055476 | 0.0059174 | -0.013469 | 69.6991 | 69.9371 | 2.0737 | -53.1967 | 69.8868 | -53.1464 | -53.2562 | -51.8692 | 26.1566 | -53.1418 | 69.8227 | 69.7449 | -53.2928 | -53.3157 | -0.10529 | -0.21515 | 0.050354 | 122.9782 | -0.15564 | 0.05951 | -0.13733 | -0.25177 | -0.27466 | -0.013733 | 1.1719 | -0.10071 | 0.17395 | -0.091553 | 122.9279 | 122.7402 | 55.1147 | -123.0927 | 122.8638 | 122.7859 | 79.1977 | -123.1522
3054.0156 | 123.0881 | -52.2217 | 70.6512 | 0.11429 | 0.010013 | 0.071668 | 0.072012 | 0.12629 | -0.0022131 | -0.0060093 | 0.64835 | -0.010835 | 0.06106 | 0.054408 | 0.0067718 | -0.013042 | 70.5826 | 70.784 | 2.1973 | -52.327 | 70.8481 | -52.2308 | -52.3041 | -50.9399 | 26.7929 | -52.327 | 70.8115 | 70.6741 | -52.4231 | -52.4826 | -0.009155 | -0.082397 | 0.19684 | 123.0057 | -0.10529 | -0.022888 | -0.068664 | -0.20142 | -0.26093 | 0.16022 | 1.2817 | -0.10529 | 0.15564 | 0.022888 | 123.0698 | 122.8043 | 54.4189 | -122.9553 | 123.0331 | 122.8958 | 79.0146 | -123.1338
3055.0156 | 123.1659 | -54.1122 | 68.7561 | -0.03067 | 0.0076627 | 0.071882 | 0.069235 | 0.12822 | -0.0034949 | -0.0075047 | -0.023041 | -0.013826 | 0.062555 | 0.055689 | 0.006131 | -0.012828 | 68.5913 | 68.8019 | 2.6047 | -54.3137 | 68.8293 | -54.2542 | -54.364 | -52.9083 | 25.4013 | -54.277 | 68.7561 | 68.6417 | -54.4189 | -54.4281 | -0.14191 | -0.25177 | 0.073242 | 122.9141 | -0.20142 | 0.050354 | -0.16479 | -0.3067 | -0.31586 | 0 | 1.2039 | -0.1648 | 0.15106 | -0.11444 | 122.9416 | 122.7036 | 56.7169 | -123.1201 | 122.8683 | 122.7539 | 79.5135 | -123.1842
3056.0156 | 123.0881 | -52.2125 | 70.6787 | 0.16006 | 0.0085171 | 0.071882 | 0.069235 | 0.12693 | 0.00035035 | -0.0075047 | 0.12955 | -0.011903 | 0.062555 | 0.057398 | 0.0076264 | -0.013896 | 70.4773 | 70.6421 | 2.2385 | -52.4643 | 70.7199 | -52.3453 | -52.4551 | -50.972 | 26.683 | -52.1301 | 70.7245 | 70.6421 | -52.4231 | -52.4506 | -0.13275 | -0.24262 | 0.041199 | 122.8546 | -0.25177 | -0.009155 | -0.20142 | -0.21057 | -0.23804 | 0.045776 | 1.2405 | 0.082397 | 0.32043 | -0.036621 | 122.9324 | 122.6898 | 54.451 | -123.1339 | 122.937 | 122.8546 | 78.8956 | -123.1293
3057.0156 | 123.1613 | -52.6886 | 70.1294 | -0.061188 | 0.0087307 | 0.071455 | 0.071799 | 0.12565 | -0.0011451 | -0.0072911 | 0.022736 | -0.011903 | 0.062128 | 0.056971 | 0.0080536 | -0.013255 | 70.0241 | 70.2438 | 2.3254 | -52.8397 | 70.2713 | -52.8076 | -52.8946 | -51.4069 | 26.3351 | -52.7527 | 70.2667 | 70.166 | -52.8671 | -52.9221 | -0.11902 | -0.20599 | 0.14191 | 122.9324 | -0.15106 | 0.054931 | -0.10529 | -0.17853 | -0.23346 | 0.13733 | 1.2817 | -0.064087 | 0.16937 | 0.036621 | 122.9599 | 122.7127 | 55.014 | -123.024 | 122.9553 | 122.8546 | 79.0237 | -123.0515
3058.0156 | 123.1064 | -52.4689 | 70.4041 | 0.12192 | 0.010226 | 0.072309 | 0.071585 | 0.12544 | -0.00029045 | -0.0072911 | 0.14481 | -0.010408 | 0.063837 | 0.055049 | 0.00784 | -0.012614 | 70.2484 | 70.4315 | 2.3026 | -52.6886 | 70.5185 | -52.565 | -52.6611 | -51.2558 | 26.4496 | -52.5604 | 70.4727 | 70.3491 | -52.6886 | -52.7161 | -0.09613 | -0.19226 | 0.11444 | 122.9004 | -0.21973 | -0.027466 | -0.15564 | -0.21973 | -0.24719 | 0.068664 | 1.2131 | -0.091553 | 0.15564 | -0.054932 | 122.9874 | 122.7173 | 54.7714 | -123.0652 | 122.9416 | 122.818 | 78.9185 | -123.1201
3059.0156 | 123.0927 | -52.4734 | 70.4407 | 0.030365 | 0.0072355 | 0.0706 | 0.070731 | 0.12886 | -0.00093145 | -0.0072911 | 0.053253 | -0.010194 | 0.064478 | 0.055903 | 0.00784 | -0.013683 | 70.2209 | 70.4086 | 2.3117 | -52.7206 | 70.5002 | -52.597 | -52.6978 | -51.2375 | 26.7105 | -52.5833 | 70.4498 | 70.3491 | -52.6886 | -52.7252 | -0.1236 | -0.2243 | 0.059509 | 122.8821 | -0.24719 | -0.022888 | -0.21973 | -0.21515 | -0.25177 | 0.009155 | 1.236 | -0.10986 | 0.14191 | -0.091553 | 122.9736 | 122.6944 | 54.7852 | -123.1384 | 122.9233 | 122.8226 | 79.184 | -123.1659
3060.0156 | 123.143 | -51.1826 | 71.6537 | 0.35843 | 0.013858 | 0.069105 | 0.070303 | 0.12758 | 0.0016321 | -0.0053683 | 0.19058 | -0.011262 | 0.062982 | 0.056758 | 0.010831 | -0.013896 | 71.6125 | 71.7682 | 2.6093 | -51.3474 | 71.8002 | -51.265 | -51.3336 | -49.9054 | 27.6627 | -51.2787 | 71.7361 | 71.6125 | -51.4114 | -51.4389 | -0.082398 | -0.15106 | 0.14648 | 122.9507 | -0.1648 | -0.013733 | -0.041199 | -0.22888 | -0.25635 | 0.082397 | 1.2772 | -0.096131 | 0.16022 | -0.041199 | 122.9828 | 122.7951 | 53.7918 | -122.9874 | 122.9187 | 122.7951 | 78.8452 | -123.0927
3061.0156 | 123.1293 | -52.121 | 70.7474 | 0.022736 | 0.0055265 | 0.072736 | 0.069235 | 0.12715 | -0.0011451 | -0.0060093 | 0.037995 | -0.0095532 | 0.06106 | 0.054835 | 0.0076264 | -0.012614 | 70.578 | 70.8252 | 2.5452 | -52.2308 | 70.9167 | -52.1713 | -52.2537 | -50.8438 | 26.9577 | -52.1393 | 70.8801 | 70.7611 | -52.3132 | -52.3682 | -0.050354 | -0.13275 | 0.16937 | 122.9462 | -0.10986 | 0.022888 | -0.16937 | -0.19226 | -0.24719 | 0.13275 | 1.2772 | -0.01831 | 0.22888 | 0.013733 | 123.0377 | 122.699 | 54.6661 | -123.0011 | 123.0011 | 122.8821 | 79.0787 | -123.1155
3062.4531 | 123.0331 | -51.1871 | 71.7728 | -0.21378 | 0.01279 | 0.072523 | 0.069235 | 0.12736 | 0.0014185 | -0.0053683 | -0.21378 | -0.011049 | 0.061701 | 0.054621 | 0.011472 | -0.01176 | 71.5897 | 71.7682 | 2.1973 | -51.3016 | 71.9238 | -51.21 | -51.3474 | -50.0656 | 27.7359 | -51.3474 | 71.846 | 71.7178 | -51.416 | -51.4572 | -0.022888 | -0.16022 | 0.15106 | 122.9553 | -0.11444 | 0.045776 | -0.1831 | -0.22888 | -0.27008 | 0.073242 | 1.1215 | -0.16022 | 0.10986 | -0.054932 | 123.111 | 122.7768 | 53.3844 | -123.1201 | 123.0331 | 122.905 | 78.923 | -123.23
3063.0312 | 123.1064 | -51.4938 | 71.4157 | -0.18326 | 0.010013 | 0.0706 | 0.072012 | 0.12928 | 0.00099115 | -0.0049411 | -0.17563 | -0.011903 | 0.063837 | 0.05633 | 0.0082672 | -0.013255 | 71.2784 | 71.5073 | 2.3621 | -51.6129 | 71.5347 | -51.5717 | -51.6312 | -50.1938 | 27.4841 | -51.5808 | 71.5073 | 71.3516 | -51.6998 | -51.7136 | -0.07782 | -0.13733 | 0.11902 | 123.0011 | -0.11902 | 0.018311 | -0.13733 | -0.20599 | -0.21973 | 0.091553 | 1.3 | -0.086976 | 0.13275 | -0.064086 | 123.0286 | 122.7722 | 53.8559 | -123.0469 | 123.0011 | 122.8455 | 78.978 | -123.1293
3064.0156 | 123.1476 | -51.9562 | 70.9259 | 0.16006 | 0.013431 | 0.069105 | 0.069235 | 0.12928 | 0.00099115 | -0.0045139 | 1.7088 | -0.0076306 | 0.059992 | 0.057826 | 0.011258 | -0.011546 | 70.7291 | 70.9167 | 2.4216 | -52.1942 | 70.9122 | -52.1439 | -52.2354 | -50.6927 | 27.4384 | -51.9928 | 70.9763 | 70.8572 | -52.153 | -52.1759 | -0.18768 | -0.27924 | -0.013733 | 122.8729 | -0.23804 | 0.041199 | -0.19684 | -0.19684 | -0.21973 | 0.050354 | 1.2634 | -0.036621 | 0.1831 | -0.068664 | 122.8683 | 122.6852 | 54.3777 | -123.1613 | 122.9324 | 122.8134 | 79.3945 | -123.1018
3065.0156 | 123.0835 | -52.6062 | 70.3125 | 0.15244 | 0.010867 | 0.068891 | 0.072226 | 0.12886 | -0.00071785 | -0.0045139 | 0.16769 | -0.0084852 | 0.062128 | 0.056117 | 0.00784 | -0.011546 | 70.079 | 70.253 | 2.5269 | -52.8442 | 70.3262 | -52.739 | -52.8305 | -51.3931 | 26.8066 | -52.7161 | 70.2805 | 70.1843 | -52.8717 | -52.8854 | -0.13275 | -0.2243 | 0.013733 | 122.8592 | -0.23804 | -0.013733 | -0.23346 | -0.2655 | -0.27924 | -0.032043 | 1.2131 | -0.10986 | 0.16937 | -0.12817 | 122.9324 | 122.6852 | 55.1331 | -123.143 | 122.8867 | 122.7905 | 79.4128 | -123.1979
3066.0156 | 123.1155 | -51.5808 | 71.2509 | 0.19058 | 0.01578 | 0.069959 | 0.073721 | 0.12993 | 0.0037683 | -0.0057957 | 0.40421 | -0.0086988 | 0.062769 | 0.055689 | 0.011044 | -0.015178 | 71.0953 | 71.2418 | 2.4582 | -51.7685 | 71.3287 | -51.7136 | -51.7822 | -50.2945 | 27.7267 | -51.6357 | 71.3654 | 71.2738 | -51.8051 | -51.8234 | -0.13275 | -0.20142 | 0.077819 | 122.8226 | -0.18768 | 0.013733 | -0.15564 | -0.2243 | -0.24261 | 0.11444 | 1.2863 | -0.054931 | 0.18768 | 0.022888 | 122.9095 | 122.6761 | 54.039 | -123.0331 | 122.9462 | 122.8546 | 79.3076 | -123.0743
3067.0156 | 123.1338 | -52.4231 | 70.4498 | 0.18295 | 0.010653 | 0.06761 | 0.069663 | 0.12693 | 0.00035035 | -0.0030185 | 0.20584 | -0.0082716 | 0.062342 | 0.056758 | 0.0082672 | -0.014323 | 70.2805 | 70.459 | 2.3117 | -52.6428 | 70.4956 | -52.565 | -52.6566 | -51.0956 | 27.2141 | -52.4918 | 70.5231 | 70.4315 | -52.6108 | -52.6932 | -0.14191 | -0.23346 | 0.045776 | 122.8821 | -0.21973 | 0.013733 | -0.16937 | -0.18768 | -0.27008 | 0.073242 | 1.3275 | -0.068664 | 0.20142 | -0.01831 | 122.9187 | 122.7036 | 54.7348 | -123.1064 | 122.9462 | 122.8546 | 79.6371 | -123.143
3068.0156 | 123.1338 | -51.6815 | 71.1411 | 0.12192 | 0.014499 | 0.069532 | 0.076071 | 0.12672 | 0.00099115 | -0.0036595 | 0.17532 | -0.009126 | 0.065546 | 0.055903 | 0.0091216 | -0.014537 | 71.0999 | 71.2006 | 2.3849 | -51.8555 | 71.2555 | -51.7776 | -51.8372 | -50.3677 | 27.7954 | -51.6357 | 71.2738 | 71.1823 | -51.8829 | -51.915 | -0.09613 | -0.15564 | 0.11444 | 122.8821 | -0.17395 | -0.018311 | -0.041198 | -0.20142 | -0.23346 | 0.13275 | 1.3138 | 0.045777 | 0.27924 | 0.041199 | 122.937 | 122.7814 | 54.0665 | -122.9782 | 122.9553 | 122.8638 | 79.4769 | -123.056
3069.0156 | 123.111 | -53.064 | 69.8227 | 0.14481 | 0.013431 | 0.070814 | 0.068594 | 0.1295 | -0.0015723 | -0.0053683 | 0.24399 | -0.012758 | 0.061701 | 0.056971 | 0.0086944 | -0.010905 | 69.8318 | 69.9692 | 2.0554 | -53.1967 | 69.9875 | -53.1097 | -53.2425 | -51.86 | 26.5182 | -53.3752 | 69.7678 | 69.6854 | -53.3752 | -53.3936 | -0.045776 | -0.17853 | 0.16479 | 123.0331 | -0.13275 | 0.045777 | 0.009155 | -0.31128 | -0.32959 | -0.054932 | 1.2039 | -0.31128 | 0.018311 | -0.13733 | 123.0515 | 122.8958 | 55.1193 | -123.0652 | 122.8317 | 122.7493 | 79.5822 | -123.2162
3070.0156 | 123.111 | -51.0452 | 71.8369 | 0.16006 | 0.016208 | 0.06825 | 0.07543 | 0.12971 | 0.00056395 | -0.0057957 | 0.23636 | -0.010621 | 0.064691 | 0.055903 | 0.010403 | -0.013683 | 71.6629 | 71.7728 | 2.3254 | -51.2421 | 71.965 | -51.1322 | -51.21 | -49.6811 | 28.0701 | -51.1322 | 71.9376 | 71.8048 | -51.2787 | -51.297 | -0.086975 | -0.1648 | 0.12817 | 122.818 | -0.19684 | -0.032043 | -0.17395 | -0.23346 | -0.25177 | 0.10071 | 1.3641 | -0.086975 | 0.16479 | -0.032043 | 123.0103 | 122.7081 | 53.3707 | -123.0469 | 122.9828 | 122.85 | 79.1153 | -123.1338
3071.0156 | 123.1384 | -50.8072 | 72.0291 | -0.168 | 0.013858 | 0.069105 | 0.070731 | 0.12672 | -0.00093145 | -0.0040867 | 0.2211 | -0.011476 | 0.063196 | 0.055049 | 0.0084808 | -0.013683 | 72.2076 | 72.3862 | 2.5497 | -50.7156 | 72.4091 | -50.6104 | -50.7111 | -49.4843 | 28.0701 | -50.9949 | 72.1893 | 72.0474 | -51.0086 | -51.0681 | 0.19684 | 0.09613 | 0.37994 | 123.1934 | 0.091553 | -0.004577 | 0.17853 | -0.20142 | -0.26093 | 0.16022 | 1.3229 | -0.18768 | 0.073242 | 0.01831 | 123.2162 | 123.0148 | 53.3569 | -122.7402 | 122.9965 | 122.8546 | 78.8773 | -123.0972
3072.0156 | 123.1201 | -51.5396 | 71.3058 | 0.16006 | 0.01578 | 0.066541 | 0.070517 | 0.12843 | 0.0018457 | -0.0057957 | 0.31265 | -0.0082716 | 0.064905 | 0.056117 | 0.010617 | -0.013255 | 71.1685 | 71.3058 | 2.3758 | -51.7319 | 71.4249 | -51.6129 | -51.7136 | -50.2213 | 27.5299 | -51.6495 | 71.4386 | 71.3287 | -51.7502 | -51.7822 | -0.073242 | -0.17395 | 0.11902 | 122.8455 | -0.19226 | -0.018311 | -0.13733 | -0.21057 | -0.24262 | 0.13275 | 1.3184 | -0.10986 | 0.13275 | 0.022888 | 122.9645 | 122.7081 | 53.9154 | -123.0194 | 122.9782 | 122.8683 | 79.0695 | -123.0881
3073.0156 | 123.1705 | -51.1322 | 71.7316 | 0.12955 | 0.010867 | 0.068891 | 0.069449 | 0.12779 | 0.00035035 | -0.0049411 | 0.24399 | -0.0099806 | 0.063196 | 0.057612 | 0.010403 | -0.014964 | 71.6263 | 71.7728 | 2.6596 | -51.3336 | 71.8414 | -51.2466 | -51.329 | -49.7772 | 27.9694 | -51.2009 | 71.8002 | 71.7087 | -51.3702 | -51.3748 | -0.11444 | -0.19684 | 0.10986 | 122.905 | -0.20142 | -0.004577 | -0.10528 | -0.23804 | -0.24262 | 0.068665 | 1.355 | -0.068665 | 0.17395 | -0.022888 | 122.9736 | 122.7585 | 53.7918 | -123.0606 | 122.9324 | 122.8409 | 79.1016 | -123.1064
3074.0156 | 123.111 | -51.6724 | 71.2097 | 0.13718 | 0.017276 | 0.069532 | 0.074362 | 0.12928 | 0.0014185 | -0.0036595 | 0.19058 | -0.0076306 | 0.064051 | 0.054621 | 0.0086944 | -0.014323 | 70.784 | 70.9259 | 2.6917 | -52.0889 | 71.0953 | -51.9928 | -52.0523 | -50.4089 | 27.4933 | -51.6678 | 71.2875 | 71.196 | -51.9333 | -51.9516 | -0.32044 | -0.37994 | -0.11444 | 122.5983 | -0.41657 | -0.036621 | -0.42572 | -0.26093 | -0.27924 | 0.07782 | 1.2634 | 0.004577 | 0.28381 | -0.013733 | 122.7676 | 122.4564 | 54.364 | -123.262 | 122.9599 | 122.8683 | 79.1656 | -123.1613
3075.0156 | 123.1384 | -50.9811 | 71.8872 | 0.17532 | 0.014071 | 0.070387 | 0.069876 | 0.12843 | 0.00056395 | -0.0053683 | 0.13718 | -0.0089124 | 0.064264 | 0.055903 | 0.0080536 | -0.010905 | 71.6446 | 72.1939 | 2.8519 | -51.1185 | 71.9879 | -51.0269 | -51.1139 | -49.649 | 28.2486 | -51.0956 | 71.9742 | 71.9009 | -51.1734 | -51.2329 | -0.045777 | -0.13275 | 0.10071 | 123.175 | -0.13733 | -0.004577 | -0.24262 | -0.19226 | -0.25177 | 0.086975 | 1.3321 | -0.11444 | 0.13733 | 0.013733 | 122.9691 | 122.6257 | 53.833 | -123.0011 | 122.9553 | 122.8821 | 79.2297 | -123.1201
3076.0156 | 123.0423 | -52.002 | 70.8984 | -0.099335 | 0.017489 | 0.067396 | 0.074149 | 0.12971 | 0.0041955 | -0.0060093 | 0.12192 | -0.0095532 | 0.064051 | 0.056544 | 0.008908 | -0.012828 | 70.7199 | 70.7932 | 2.5772 | -52.1988 | 71.0541 | -52.0935 | -52.1988 | -50.7294 | 27.3102 | -51.9974 | 71.0403 | 70.9442 | -52.1713 | -52.2354 | -0.091553 | -0.19684 | 0.15564 | 122.7951 | -0.19684 | 0 | -0.17853 | -0.16937 | -0.23346 | 0.14191 | 1.2726 | 0.004578 | 0.23804 | 0.045777 | 123.056 | 122.7219 | 54.5792 | -123.0972 | 123.0423 | 122.9462 | 79.3121 | -123.1338
3077.0156 | 123.1018 | -51.5808 | 71.2692 | 0.12192 | 0.013858 | 0.070173 | 0.07009 | 0.12886 | 0.00077755 | -0.0060093 | 0.22873 | -0.0082716 | 0.062555 | 0.055476 | 0.008908 | -0.012401 | 71.2372 | 71.347 | 2.7512 | -51.7868 | 71.3699 | -51.6907 | -51.8005 | -50.2396 | 27.6398 | -51.535 | 71.3974 | 71.3104 | -51.7227 | -51.8097 | -0.10986 | -0.21973 | 0.10071 | 122.9279 | -0.20599 | 0.013733 | -0.032043 | -0.14191 | -0.22888 | 0.12817 | 1.3412 | 0.045777 | 0.27466 | 0.041199 | 122.9507 | 122.818 | 54.332 | -123.0698 | 122.9782 | 122.8912 | 79.2206 | -123.0789
3078.0156 | 123.0286 | -53.5721 | 69.3512 | 0.099029 | 0.017917 | 0.065901 | 0.073721 | 0.12736 | 0.0022729 | -0.0053683 | 1.1366 | -0.007417 | 0.065973 | 0.05633 | 0.008908 | -0.014323 | 69.31 | 69.4016 | 2.5818 | -53.6087 | 69.6396 | -53.4805 | -53.5721 | -52.3453 | 25.8362 | -53.8467 | 69.4931 | 69.3924 | -53.7735 | -53.8239 | 0.091553 | 0 | 0.28839 | 122.9736 | -0.036621 | -0.036621 | -0.041198 | -0.20142 | -0.25177 | 0.14191 | 1.2268 | -0.27466 | -0.022888 | 0.041199 | 123.2117 | 122.8821 | 56.1539 | -122.9233 | 123.0652 | 122.9645 | 79.4083 | -123.175
3079.0156 | 123.1247 | -52.002 | 70.8527 | 0.19058 | 0.014712 | 0.069319 | 0.071799 | 0.13228 | -0.0013587 | -0.0060093 | -1.0988 | -0.0067762 | 0.061487 | 0.055049 | 0.00784 | -0.013469 | 70.7657 | 70.9213 | 2.8061 | -52.1439 | 70.9442 | -52.0889 | -52.2263 | -50.6699 | 27.1454 | -52.0111 | 70.9351 | 70.8481 | -52.2354 | -52.2537 | -0.086975 | -0.2243 | 0.091553 | 122.9233 | -0.14191 | 0.082397 | -0.086975 | -0.23346 | -0.25177 | 0.082398 | 1.3321 | -0.009155 | 0.24262 | -0.004578 | 122.9462 | 122.7676 | 54.808 | -123.0789 | 122.937 | 122.85 | 79.1473 | -123.1064
3080.0156 | 123.0469 | -52.1439 | 70.7657 | 1.1748 | 0.017489 | 0.071668 | 0.072012 | 0.12928 | 0.0029137 | -0.0060093 | 0.10666 | -0.0082716 | 0.065332 | 0.057826 | 0.0099762 | -0.011119 | 70.5185 | 70.5505 | 2.4902 | -52.4185 | 70.8298 | -52.3224 | -52.4231 | -50.9033 | 26.9257 | -52.2446 | 70.8572 | 70.7611 | -52.3956 | -52.4002 | -0.17853 | -0.27924 | 0.064087 | 122.6944 | -0.27466 | 0.004578 | -0.24719 | -0.25177 | -0.25635 | 0.091553 | 1.2405 | -0.10071 | 0.15564 | -0.004578 | 122.9736 | 122.6624 | 54.6341 | -123.1888 | 123.0011 | 122.905 | 79.0695 | -123.1659
3081.0156 | 123.1338 | -53.5858 | 69.2551 | 0.24399 | 0.014285 | 0.068891 | 0.071158 | 0.12907 | 0.00013675 | -0.0032321 | 0.21347 | -0.010408 | 0.062128 | 0.057612 | 0.0093354 | -0.010692 | 69.2322 | 69.3832 | 2.4719 | -53.6728 | 69.4427 | -53.6179 | -53.6957 | -52.2491 | 25.9506 | -53.714 | 69.3695 | 69.2596 | -53.8055 | -53.8147 | -0.032044 | -0.10986 | 0.18768 | 122.9691 | -0.086976 | 0.022888 | -0.022888 | -0.21973 | -0.22888 | 0.11444 | 1.3367 | -0.12817 | 0.10071 | 0.004578 | 123.0286 | 122.818 | 56.0577 | -122.9507 | 122.9553 | 122.8455 | 79.5364 | -123.0698
3082.0156 | 123.0103 | -52.3087 | 70.6284 | 0.0914 | 0.017062 | 0.069319 | 0.073081 | 0.13057 | 0.0024865 | -0.0075047 | 2.9372 | -0.0059216 | 0.062555 | 0.059321 | 0.011472 | -0.014323 | 70.4132 | 70.4681 | 2.5314 | -52.4918 | 70.7703 | -52.3865 | -52.446 | -51.059 | 27.1271 | -52.4231 | 70.7474 | 70.6696 | -52.4918 | -52.5375 | -0.07782 | -0.13733 | 0.14191 | 122.7768 | -0.1831 | -0.045776 | -0.21515 | -0.1831 | -0.22888 | 0.11902 | 1.2497 | -0.11444 | 0.11444 | 0.041199 | 123.0789 | 122.7219 | 54.8401 | -123.0743 | 123.056 | 122.9782 | 79.4357 | -123.1659
3083.0156 | 123.1476 | -50.9308 | 71.9193 | 0.18295 | 0.017917 | 0.069319 | 0.071585 | 0.13014 | -0.00071785 | -0.0053683 | 0.24399 | -0.010194 | 0.064905 | 0.054408 | 0.0093354 | -0.011974 | 71.8094 | 71.9421 | 2.4719 | -51.091 | 72.0886 | -50.9766 | -51.0956 | -49.6262 | 28.0884 | -50.9674 | 72.0062 | 71.9559 | -51.1597 | -51.1826 | -0.045776 | -0.1648 | 0.16937 | 122.8729 | -0.16022 | 0.004578 | -0.10986 | -0.22888 | -0.25177 | 0.086976 | 1.3046 | -0.036621 | 0.21515 | 0.036622 | 123.0194 | 122.7402 | 53.4027 | -123.0148 | 122.937 | 122.8867 | 79.0192 | -123.1018
3084.0156 | 123.0331 | -51.1734 | 71.759 | 0.0074768 | 0.021121 | 0.067823 | 0.07244 | 0.12736 | 0.0039819 | -0.0055821 | 0.09903 | -0.008058 | 0.065546 | 0.056117 | 0.0093354 | -0.013255 | 71.553 | 71.6446 | 2.4261 | -51.3657 | 71.9193 | -51.2375 | -51.3199 | -49.91 | 27.7908 | -51.3153 | 71.8918 | 71.8094 | -51.3657 | -51.416 | -0.064087 | -0.14648 | 0.16022 | 122.818 | -0.19226 | -0.045777 | -0.20599 | -0.19226 | -0.24262 | 0.13275 | 1.2634 | -0.14191 | 0.10071 | 0.050354 | 123.0927 | 122.7264 | 53.5995 | -123.0789 | 123.0652 | 122.9828 | 78.9642 | -123.175
3085.0156 | 123.0881 | -51.3931 | 71.521 | 0.16006 | 0.016635 | 0.069319 | 0.07009 | 0.12864 | -0.00050425 | -0.0043003 | 0.20584 | -0.0097668 | 0.064478 | 0.054621 | 0.0099762 | -0.012401 | 71.3287 | 71.4523 | 2.0096 | -51.59 | 71.64 | -51.4572 | -51.5625 | -50.0977 | 27.8137 | -51.5396 | 71.6125 | 71.521 | -51.59 | -51.5945 | -0.064087 | -0.16937 | 0.11902 | 122.8455 | -0.19684 | -0.027466 | -0.19226 | -0.19684 | -0.20142 | 0.091553 | 1.2955 | -0.14648 | 0.054931 | 0 | 123.0331 | 122.7219 | 53.4027 | -123.0835 | 123.0057 | 122.9141 | 79.2068 | -123.1155
3086.0156 | 123.0011 | -51.5076 | 71.4661 | 0.022736 | 0.019412 | 0.071027 | 0.075003 | 0.12843 | 0.0014185 | -0.0055821 | 0.12955 | -0.0095532 | 0.061487 | 0.055476 | 0.0099762 | -0.011333 | 71.2509 | 71.3287 | 2.1057 | -51.6953 | 71.5393 | -51.59 | -51.6998 | -50.2716 | 27.6581 | -51.6541 | 71.5393 | 71.4615 | -51.7273 | -51.7502 | -0.082398 | -0.19226 | 0.073243 | 122.8363 | -0.18768 | 0.004578 | -0.21515 | -0.21973 | -0.24262 | 0.073243 | 1.236 | -0.14648 | 0.09613 | -0.004577 | 123.0469 | 122.7585 | 53.6133 | -123.1659 | 123.0469 | 122.9691 | 79.1656 | -123.2162
3087.0156 | 123.0743 | -51.4847 | 71.4249 | 0.29739 | 0.01578 | 0.069532 | 0.067526 | 0.12822 | 0.0014185 | -0.0072911 | 0.17532 | -0.0099806 | 0.063837 | 0.058039 | 0.008908 | -0.011119 | 71.3013 | 71.3974 | 2.1149 | -51.6357 | 71.6217 | -51.5259 | -51.6495 | -50.2762 | 27.5848 | -51.5854 | 71.521 | 71.4157 | -51.7639 | -51.7776 | -0.041199 | -0.1648 | 0.19684 | 122.8821 | -0.15106 | 0.013733 | -0.1236 | -0.27924 | -0.29297 | 0.09613 | 1.2085 | -0.10071 | 0.19226 | -0.009156 | 123.1064 | 122.7859 | 53.5995 | -123.0743 | 123.0057 | 122.9004 | 79.0695 | -123.2025
3088.0156 | 123.0103 | -51.7822 | 71.196 | 0.30502 | 0.019626 | 0.066541 | 0.074149 | 0.12993 | -0.00029045 | -0.0045139 | 0.17532 | -0.0072034 | 0.067041 | 0.057826 | 0.011258 | -0.011974 | 71.0129 | 71.0678 | 1.9867 | -51.8967 | 71.3699 | -51.7776 | -51.8555 | -50.5234 | 27.3605 | -51.9333 | 71.3013 | 71.2234 | -51.9699 | -52.0111 | 0.004578 | -0.073242 | 0.17395 | 122.85 | -0.11444 | -0.041198 | -0.18311 | -0.18768 | -0.22888 | 0.10529 | 1.2589 | -0.15106 | 0.077819 | 0.027466 | 123.1522 | 122.7951 | 53.7689 | -123.0515 | 123.0835 | 123.0057 | 79.1428 | -123.2071
3089.0156 | 123.1064 | -52.034 | 70.8527 | 0.16769 | 0.01578 | 0.067182 | 0.070944 | 0.12672 | -0.0013587 | -0.0047275 | 0.2211 | -0.0076306 | 0.065973 | 0.05633 | 0.0074126 | -0.011333 | 70.6329 | 70.7703 | 2.2293 | -52.2812 | 70.9488 | -52.1484 | -52.2491 | -50.6332 | 27.2049 | -52.1393 | 71.022 | 70.9488 | -52.2079 | -52.2491 | -0.11444 | -0.21515 | 0.096131 | 122.8043 | -0.24719 | -0.032043 | -0.21973 | -0.17395 | -0.21515 | 0.16937 | 1.4008 | -0.10529 | 0.10986 | 0.096131 | 122.9828 | 122.6669 | 54.2633 | -123.1018 | 123.056 | 122.9828 | 79.2389 | -123.1018
3090.0156 | 123.0286 | -51.1093 | 71.8597 | 0.015106 | 0.018344 | 0.068037 | 0.075003 | 0.12928 | 0.00099115 | -0.0043003 | 0.21347 | -0.010194 | 0.064478 | 0.057398 | 0.01019 | -0.012614 | 71.553 | 71.6812 | 2.2018 | -51.3062 | 71.9284 | -51.1917 | -51.2878 | -49.8276 | 27.8595 | -51.2009 | 71.933 | 71.8597 | -51.3153 | -51.3702 | -0.082397 | -0.17853 | 0.068665 | 122.7905 | -0.19684 | -0.01831 | -0.3067 | -0.20599 | -0.26093 | 0.073242 | 1.2817 | -0.091553 | 0.16937 | 0 | 123.0377 | 122.6624 | 53.3112 | -123.1476 | 123.0423 | 122.9691 | 78.9688 | -123.23
3091.0156 | 123.0743 | -51.8005 | 71.0999 | 0.16006 | 0.016421 | 0.070387 | 0.07244 | 0.13099 | -7.6852e-05 | -0.0075047 | 0.21347 | -0.010621 | 0.0664 | 0.057612 | 0.0080536 | -0.012401 | 71.0083 | 71.109 | 2.3346 | -51.9424 | 71.3242 | -51.7914 | -51.915 | -50.4959 | 27.3331 | -51.9058 | 71.2418 | 71.1777 | -51.9836 | -51.9928 | 0.009155 | -0.11444 | 0.2243 | 122.9095 | -0.14191 | -0.027466 | -0.091553 | -0.18311 | -0.19226 | 0.14191 | 1.3046 | -0.10529 | 0.086975 | 0.077819 | 123.1247 | 122.8088 | 54.1351 | -123.0148 | 123.0423 | 122.9782 | 79.1336 | -123.0927
3092.0156 | 123.1842 | -51.1047 | 71.8323 | 0.11429 | 0.019412 | 0.068037 | 0.073508 | 0.13121 | 0.0016321 | -0.0060093 | 0.12955 | -0.0067762 | 0.064905 | 0.056758 | 0.0086944 | -0.01176 | 71.6721 | 71.7545 | 2.0325 | -51.2375 | 72.0474 | -51.0956 | -51.21 | -49.8642 | 27.9144 | -51.2558 | 71.9284 | 71.8872 | -51.2878 | -51.3336 | 0.009155 | -0.10529 | 0.21515 | 122.8592 | -0.13275 | -0.027466 | -0.16022 | -0.18311 | -0.22888 | 0.096131 | 1.2405 | -0.15106 | 0.07782 | 0.054932 | 123.1522 | 122.7768 | 53.1372 | -123.0423 | 123.0331 | 122.9919 | 79.0192 | -123.1659
3093.0156 | 123.111 | -50.8759 | 71.9879 | 0.16006 | 0.013217 | 0.06825 | 0.069022 | 0.12971 | -7.6852e-05 | -0.0057957 | 0.25162 | -0.009126 | 0.066614 | 0.055903 | 0.00784 | -0.0091966 | 71.846 | 71.9559 | 2.211 | -51.0681 | 72.1252 | -50.9445 | -51.0498 | -49.5758 | 28.1387 | -50.9491 | 72.1024 | 72.0428 | -51.1139 | -51.123 | -0.068665 | -0.17395 | 0.13733 | 122.8317 | -0.19226 | -0.01831 | -0.14191 | -0.23804 | -0.24719 | 0.11444 | 1.3 | -0.073243 | 0.17395 | 0.054932 | 123.0011 | 122.7219 | 53.0869 | -123.0377 | 122.9782 | 122.9187 | 79.0146 | -123.111
3094.0156 | 123.0377 | -52.7939 | 70.1294 | -0.053558 | 0.016635 | 0.068891 | 0.07009 | 0.12864 | 0.0035547 | -0.0079319 | 0.037995 | -0.0093396 | 0.066828 | 0.056971 | 0.0086944 | -0.012828 | 69.9783 | 70.0745 | 1.9958 | -52.9587 | 70.2484 | -52.8534 | -52.9541 | -51.4801 | 26.7426 | -52.9541 | 70.2393 | 70.1889 | -52.9999 | -53.0457 | -0.05951 | -0.16022 | 0.11902 | 122.8683 | -0.16479 | -0.004577 | -0.15106 | -0.20599 | -0.25177 | 0.10986 | 1.3138 | -0.16022 | 0.091552 | 0.059509 | 123.0423 | 122.7722 | 54.7897 | -123.0835 | 123.0331 | 122.9828 | 79.5364 | -123.175
3095.0156 | 123.0652 | -51.5762 | 71.3699 | 0.15244 | 0.017276 | 0.069746 | 0.072012 | 0.12779 | -0.00029045 | -0.0075047 | 0.23636 | -0.0067762 | 0.064905 | 0.055262 | 0.008908 | -0.010265 | 71.0815 | 71.1777 | 2.0645 | -51.8372 | 71.4111 | -51.6861 | -51.7822 | -50.2533 | 27.681 | -51.6632 | 71.4432 | 71.3974 | -51.7685 | -51.7822 | -0.10986 | -0.20599 | 0.041199 | 122.7539 | -0.26093 | -0.054931 | -0.28839 | -0.19226 | -0.20599 | 0.073242 | 1.3229 | -0.086975 | 0.11902 | 0.027466 | 122.9874 | 122.6578 | 53.6407 | -123.1522 | 123.0194 | 122.9736 | 79.2572 | -123.1522
3096.0156 | 123.0286 | -51.6129 | 71.3379 | 0.045624 | 0.019412 | 0.071455 | 0.073081 | 0.12928 | 0.0027001 | -0.0075047 | 0.083771 | -0.0076306 | 0.067041 | 0.057612 | 0.00784 | -0.012401 | 71.2921 | 71.3928 | 1.9226 | -51.6312 | 71.6171 | -51.5259 | -51.622 | -50.3036 | 27.6855 | -51.8143 | 71.434 | 71.3882 | -51.8143 | -51.8417 | 0.086975 | -0.009155 | 0.27923 | 123.0057 | -0.018311 | -0.009156 | -0.045777 | -0.20142 | -0.22888 | 0.09613 | 1.3092 | -0.20142 | 0.027466 | 0.050354 | 123.23 | 122.905 | 53.5355 | -122.9599 | 123.0469 | 123.0011 | 79.2984 | -123.1796
3097.0156 | 123.0469 | -53.2516 | 69.6762 | -2.1745 | 0.017489 | 0.069532 | 0.069663 | 0.12907 | -0.00029045 | -0.0055821 | 0.2211 | -0.007417 | 0.062555 | 0.05868 | 0.0097626 | -0.012401 | 69.5709 | 69.7723 | 1.9226 | -53.2791 | 69.9875 | -53.1647 | -53.2654 | -51.9424 | 26.4267 | -53.4622 | 69.7632 | 69.7403 | -53.4714 | -53.4851 | 0.086975 | -0.013733 | 0.31128 | 123.024 | -0.027466 | -0.013733 | -0.10529 | -0.21973 | -0.23346 | 0.086976 | 1.3092 | -0.21057 | 0.022888 | 0.064087 | 123.2391 | 122.8226 | 55.1743 | -122.9416 | 123.0148 | 122.9919 | 79.6783 | -123.1613
3098.0156 | 123.0469 | -51.2924 | 71.6629 | -0.00015269 | 0.019839 | 0.067396 | 0.073081 | 0.12993 | 0.0014185 | -0.0051547 | 0.068512 | -0.009126 | 0.065332 | 0.056544 | 0.01019 | -0.011974 | 71.4752 | 71.5668 | 2.3163 | -51.4664 | 71.7682 | -51.3565 | -51.4664 | -49.9558 | 28.0792 | -51.3931 | 71.7545 | 71.7087 | -51.4709 | -51.5259 | -0.064087 | -0.17395 | 0.10528 | 122.8592 | -0.17395 | 0 | -0.18768 | -0.17853 | -0.23346 | 0.091553 | 1.3367 | -0.10071 | 0.13275 | 0.045776 | 123.0606 | 122.7676 | 53.6087 | -123.1293 | 123.0469 | 123.0011 | 79.3716 | -123.1888
3099.0156 | 123.0606 | -51.4664 | 71.4752 | 0.16006 | 0.017062 | 0.0706 | 0.069876 | 0.12928 | -7.6852e-05 | -0.0066501 | 0.17532 | -0.0084852 | 0.068323 | 0.059748 | 0.007199 | -0.014323 | 71.228 | 71.3333 | 2.1103 | -51.7227 | 71.5622 | -51.5717 | -51.6815 | -50.0381 | 27.9602 | -51.6586 | 71.5439 | 71.5118 | -51.6769 | -51.7227 | -0.10529 | -0.21515 | 0.086975 | 122.7997 | -0.25635 | -0.041198 | -0.24719 | -0.21057 | -0.25635 | 0.068664 | 1.4282 | -0.19226 | 0.064087 | 0.036621 | 123.0286 | 122.6944 | 53.5767 | -123.1567 | 123.0103 | 122.9782 | 79.4266 | -123.1979
3100.0156 | 123.0331 | -51.4526 | 71.4844 | 1.2206 | 0.021335 | 0.071455 | 0.073721 | 0.12928 | -0.0011451 | -0.0049411 | -0.015411 | -0.0093396 | 0.0664 | 0.054621 | 0.008908 | -0.012828 | 71.0999 | 71.2463 | 2.2614 | -51.7731 | 71.3882 | -51.7181 | -51.7639 | -50.1114 | 28.1204 | -51.4526 | 71.5668 | 71.5256 | -51.6586 | -51.6953 | -0.2655 | -0.31128 | -0.09613 | 122.699 | -0.32043 | -0.009155 | -0.38452 | -0.20599 | -0.24261 | 0.082397 | 1.3412 | 0 | 0.24261 | 0.041199 | 122.8409 | 122.5525 | 53.714 | -123.2483 | 123.0194 | 122.9782 | 79.5731 | -123.1796
3101.0156 | 123.1338 | -51.3794 | 71.5073 | 0.045624 | 0.0087307 | 0.069319 | 0.072012 | 0.128 | -0.0079811 | -0.0079319 | 0.13718 | -0.01233 | 0.060419 | 0.054835 | 0.0059174 | -0.0098374 | 71.3928 | 71.5805 | 2.211 | -51.4755 | 71.7133 | -51.3702 | -51.4801 | -50.0839 | 28.1433 | -51.4435 | 71.5988 | 71.5393 | -51.6312 | -51.6266 | 0.009156 | -0.10071 | 0.20599 | 122.9599 | -0.09613 | 0.004578 | -0.11444 | -0.25177 | -0.24719 | 0.091553 | 1.2955 | -0.064086 | 0.18311 | 0.032044 | 123.0927 | 122.7722 | 53.5904 | -122.9874 | 122.9782 | 122.9187 | 79.5227 | -123.1338
3102.0156 | 123.0515 | -51.3611 | 71.6171 | -0.03067 | 0.019626 | 0.070387 | 0.074362 | 0.12843 | 0.0024865 | -0.0057957 | -0.0077819 | -0.0065626 | 0.064691 | 0.056758 | 0.01019 | -0.012614 | 71.4981 | 71.5713 | 2.243 | -51.4435 | 71.7728 | -51.3702 | -51.4664 | -50.0381 | 28.1754 | -51.5579 | 71.6675 | 71.6034 | -51.5579 | -51.5808 | -0.009155 | -0.10529 | 0.15564 | 122.9324 | -0.082397 | 0.022889 | -0.11902 | -0.19684 | -0.21973 | 0.050354 | 1.3229 | -0.19684 | 0.022889 | -0.013732 | 123.1338 | 122.8592 | 53.6041 | -123.0835 | 123.0286 | 122.9645 | 79.5364 | -123.1979
3103.0156 | 122.8867 | -50.9903 | 71.8918 | 0.25925 | 0.020053 | 0.070387 | 0.072012 | 0.12907 | 0.0018457 | -0.0077183 | 0.16769 | -0.0078442 | 0.066187 | 0.057612 | 0.0084808 | -0.012828 | 71.8826 | 71.9467 | 2.179 | -51.0178 | 72.2397 | -50.9125 | -51.0132 | -49.5575 | 28.537 | -51.0727 | 72.1802 | 72.084 | -51.123 | -51.1963 | 0.077819 | -0.022889 | 0.3479 | 122.937 | -0.027466 | -0.004577 | -0.009156 | -0.13275 | -0.20599 | 0.28839 | 1.4328 | -0.082398 | 0.1236 | 0.19226 | 123.23 | 122.8729 | 53.1693 | -122.905 | 123.1705 | 123.0743 | 79.5273 | -123.0881
3104.0156 | 123.1018 | -51.6449 | 71.2921 | -0.12985 | 0.018344 | 0.071241 | 0.071158 | 0.128 | 0.00056395 | -0.0070773 | -1.0301 | -0.0086988 | 0.064905 | 0.05633 | 0.0082672 | -0.013683 | 71.077 | 71.1823 | 2.0828 | -51.8784 | 71.3516 | -51.7822 | -51.8692 | -50.3128 | 28.093 | -51.7776 | 71.3379 | 71.2967 | -51.8738 | -51.8921 | -0.13733 | -0.22431 | 0.05951 | 122.8271 | -0.23346 | -0.009155 | -0.21515 | -0.22888 | -0.24719 | 0.045777 | 1.3321 | -0.13275 | 0.11444 | 0.004578 | 122.9965 | 122.7219 | 53.7277 | -123.1613 | 122.9828 | 122.9416 | 79.7379 | -123.1842
3105.0156 | 122.9919 | -52.739 | 70.1797 | 0.045624 | 0.018771 | 0.0706 | 0.073081 | 0.12587 | 0.00035035 | -0.0060093 | 0.068512 | -0.0095532 | 0.067896 | 0.056971 | 0.009549 | -0.012187 | 70.0607 | 70.1797 | 2.0279 | -52.8397 | 70.3812 | -52.739 | -52.8442 | -51.4252 | 27.1774 | -52.9449 | 70.2713 | 70.2347 | -52.9678 | -53.0136 | 0 | -0.10528 | 0.20142 | 122.9187 | -0.10071 | 0.004577 | -0.11902 | -0.22888 | -0.27466 | 0.091552 | 1.3138 | -0.20599 | 0.068665 | 0.054931 | 123.1201 | 122.7997 | 54.7668 | -123.024 | 123.0103 | 122.9736 | 79.9164 | -123.1934
3106.0156 | 123.143 | -51.5808 | 71.2555 | 0.19821 | 0.013858 | 0.069319 | 0.068594 | 0.13035 | -0.0011451 | -0.0066501 | 0.27451 | -0.0099806 | 0.065546 | 0.055476 | 0.007199 | -0.012187 | 71.1182 | 71.2738 | 2.1515 | -51.7868 | 71.3287 | -51.7136 | -51.8188 | -50.2304 | 28.038 | -51.86 | 71.2738 | 71.228 | -51.8784 | -51.8829 | -0.13275 | -0.23804 | 0.073242 | 122.8546 | -0.20599 | 0.032044 | -0.13733 | -0.29755 | -0.30212 | 0.018311 | 1.3504 | -0.27923 | 0.022889 | -0.027466 | 122.9095 | 122.699 | 53.7323 | -123.0743 | 122.8546 | 122.8088 | 79.6188 | -123.1384
3107.0156 | 123.024 | -52.9953 | 69.9051 | -0.015411 | 0.018344 | 0.068464 | 0.072867 | 0.12864 | 0.0018457 | -0.0055821 | 0.022736 | -0.0078442 | 0.067468 | 0.058039 | 0.008908 | -0.013469 | 69.5572 | 69.6304 | 1.9363 | -53.4485 | 69.7998 | -53.3661 | -53.4439 | -51.6907 | 26.8524 | -53.0914 | 69.9509 | 69.8776 | -53.2791 | -53.2608 | -0.37079 | -0.44861 | -0.10528 | 122.6257 | -0.45319 | -0.004577 | -0.3479 | -0.28381 | -0.2655 | 0.045777 | 1.3046 | -0.096131 | 0.16937 | -0.027465 | 122.7951 | 122.5525 | 54.9316 | -123.349 | 122.9462 | 122.8729 | 79.8477 | -123.1659
3108.0156 | 123.1705 | -51.4664 | 71.3882 | 0.16769 | 0.013858 | 0.069319 | 0.069235 | 0.12971 | -0.0015723 | -0.0053683 | 0.25162 | -0.011689 | 0.064905 | 0.055903 | 0.0084808 | -0.011546 | 71.2143 | 71.3654 | 2.211 | -51.6724 | 71.4844 | -51.5945 | -51.6449 | -50.1251 | 28.0655 | -51.5854 | 71.434 | 71.3974 | -51.7273 | -51.7181 | -0.12817 | -0.17853 | 0.09613 | 122.8317 | -0.20599 | -0.027466 | -0.17395 | -0.26093 | -0.25177 | 0.045776 | 1.3412 | -0.11902 | 0.13275 | 0.009155 | 122.9507 | 122.6807 | 53.6774 | -123.0331 | 122.9004 | 122.8638 | 79.5319 | -123.1064
3109.0156 | 123.0331 | -52.4506 | 70.4681 | -0.023041 | 0.017703 | 0.069105 | 0.070944 | 0.12928 | 0.00035035 | -0.0055821 | 0.09903 | -0.0093396 | 0.067255 | 0.054835 | 0.01019 | -0.013255 | 70.34 | 70.4407 | 2.1332 | -52.5696 | 70.6604 | -52.478 | -52.5513 | -51.0818 | 27.2232 | -52.652 | 70.5917 | 70.5505 | -52.6657 | -52.6794 | -0.027465 | -0.10071 | 0.19226 | 122.8912 | -0.11902 | -0.01831 | -0.12817 | -0.21515 | -0.22888 | 0.1236 | 1.3687 | -0.20142 | 0.027465 | 0.082397 | 123.111 | 122.7905 | 54.5837 | -123.0194 | 123.0423 | 123.0011 | 79.6738 | -123.1476
3110.0156 | 123.0881 | -51.2146 | 71.7545 | -0.19089 | 0.014926 | 0.072309 | 0.072653 | 0.12928 | -0.00050425 | -0.0045139 | -0.076446 | -0.009126 | 0.064264 | 0.057398 | 0.008908 | -0.013896 | 71.4294 | 71.5576 | 2.2064 | -51.4801 | 71.7224 | -51.384 | -51.4938 | -49.9741 | 28.1113 | -51.3748 | 71.6995 | 71.6721 | -51.4709 | -51.503 | -0.16937 | -0.27923 | -0.032044 | 122.7722 | -0.2655 | 0.013732 | -0.32501 | -0.25635 | -0.28839 | -0.054932 | 1.2405 | -0.16022 | 0.12817 | -0.082398 | 122.937 | 122.644 | 53.421 | -123.2483 | 122.9141 | 122.8867 | 79.3259 | -123.2574
3111.0312 | 123.1293 | -52.4689 | 70.4132 | 0.045624 | 0.0089443 | 0.074873 | 0.07244 | 0.128 | -0.0060585 | -0.0057957 | 0.21347 | -0.011476 | 0.061701 | 0.054408 | 0.0039948 | -0.0098374 | 70.0745 | 70.4224 | 2.3163 | -52.6749 | 70.4956 | -52.5742 | -52.6886 | -51.1047 | 27.2232 | -52.4918 | 70.4681 | 70.4407 | -52.6794 | -52.7252 | -0.10529 | -0.21973 | 0.082397 | 122.8912 | -0.20599 | 0.013733 | -0.33875 | -0.21057 | -0.25635 | 0.054932 | 1.3641 | -0.022888 | 0.23346 | 0.027466 | 122.9645 | 122.5433 | 54.7852 | -123.1018 | 122.937 | 122.9095 | 79.6921 | -123.1384
3112.0625 | 123.1842 | -53.9062 | 68.9758 | -0.053558 | 0.0091581 | 0.069959 | 0.072226 | 0.12971 | -0.0058447 | -0.0087863 | 0.045624 | -0.010835 | 0.064478 | 0.055476 | 0.0029266 | -0.012828 | 68.9392 | 69.104 | 2.243 | -54.007 | 69.1772 | -53.9246 | -54.0344 | -52.4826 | 26.1932 | -53.9841 | 69.0491 | 69.0033 | -54.1168 | -54.1168 | -0.018311 | -0.12817 | 0.20142 | 123.0103 | -0.10071 | 0.027466 | -0.036621 | -0.21057 | -0.21057 | 0.073242 | 1.4236 | -0.07782 | 0.13275 | 0.027466 | 123.0835 | 122.8455 | 56.1493 | -123.0103 | 122.9553 | 122.9095 | 80.0995 | -123.0927
3113.0156 | 123.0743 | -53.0273 | 69.9051 | -0.091705 | 0.016208 | 0.068891 | 0.071799 | 0.1295 | 0.0033411 | -0.0083591 | 0.28976 | -0.01233 | 0.066187 | 0.057612 | 0.011258 | -0.014537 | 69.7861 | 69.9051 | 2.0874 | -53.1555 | 70.0241 | -53.064 | -53.1784 | -51.59 | 26.8204 | -53.1509 | 70.0195 | 69.9142 | -53.2059 | -53.2562 | -0.036621 | -0.15106 | 0.11902 | 122.9324 | -0.12817 | 0.022888 | -0.11902 | -0.17853 | -0.22888 | 0.11444 | 1.4374 | -0.1236 | 0.10529 | 0.009156 | 123.0515 | 122.8134 | 55.1147 | -123.0835 | 123.0469 | 122.9416 | 79.8477 | -123.1613
3114.0156 | 123.0743 | -51.8463 | 71.1044 | -0.19089 | 0.016208 | 0.071455 | 0.071585 | 0.13099 | -7.6852e-05 | -0.0062229 | -0.16037 | -0.0095532 | 0.067255 | 0.055476 | 0.008908 | -0.013683 | 70.8572 | 70.9808 | 2.243 | -52.0477 | 71.1685 | -51.9836 | -52.0844 | -50.4959 | 27.8 | -51.9791 | 71.2051 | 71.1136 | -52.0432 | -52.0752 | -0.13733 | -0.23804 | 0.064087 | 122.8271 | -0.20142 | 0.036622 | -0.24719 | -0.19684 | -0.22888 | 0.10071 | 1.3504 | -0.13275 | 0.09613 | 0.009155 | 123.0148 | 122.7036 | 54.0894 | -123.1888 | 123.0515 | 122.9599 | 79.6463 | -123.1796
3115.0156 | 123.0789 | -52.9449 | 69.9829 | -0.10696 | 0.01813 | 0.069319 | 0.074576 | 0.12971 | -0.00050425 | -0.010282 | -0.053558 | -0.0082716 | 0.067682 | 0.055689 | 0.008908 | -0.01411 | 69.9829 | 69.9783 | 2.4078 | -53.0319 | 70.1706 | -52.9541 | -53.0823 | -51.5259 | 26.8616 | -53.1509 | 70.079 | 70.015 | -53.1464 | -53.1921 | -0.009156 | -0.13733 | 0.18768 | 122.9233 | -0.086975 | 0.050354 | 0 | -0.20142 | -0.24719 | 0.096131 | 1.4191 | -0.20599 | 0.041199 | 0.032044 | 123.1155 | 122.9279 | 55.3528 | -123.0652 | 123.024 | 122.9599 | 79.8065 | -123.175
3116.0156 | 123.0148 | -52.0615 | 70.8847 | 0.12192 | 0.018344 | 0.068678 | 0.070517 | 0.12736 | 0.00013675 | -0.0057957 | 1.4265 | -0.0095532 | 0.064691 | 0.058039 | 0.008908 | -0.013255 | 70.6421 | 70.7657 | 2.4124 | -52.3636 | 70.9717 | -52.121 | -52.2537 | -50.7248 | 27.6077 | -52.2675 | 70.9671 | 70.9076 | -52.272 | -52.2995 | -0.05951 | -0.19226 | 0.086975 | 122.8271 | -0.30212 | -0.10986 | -0.24262 | -0.21057 | -0.23804 | 0.082397 | 1.3367 | -0.20599 | 0.032044 | 0.022888 | 123.0331 | 122.7036 | 54.4739 | -123.1384 | 123.0286 | 122.9691 | 79.6692 | -123.1842
3117.0156 | 123.0789 | -51.004 | 71.9238 | -0.14511 | 0.017917 | 0.068037 | 0.074149 | 0.12971 | 0.0031273 | -0.0053683 | -0.12222 | -0.0084852 | 0.065332 | 0.056758 | 0.00784 | -0.011119 | 71.6766 | 71.759 | 2.4536 | -51.3336 | 71.9055 | -51.2283 | -51.3428 | -49.6674 | 28.5416 | -51.1459 | 71.9742 | 71.9284 | -51.2421 | -51.2604 | -0.22431 | -0.33875 | -0.01831 | 122.7631 | -0.32959 | 0.009155 | -0.24719 | -0.23804 | -0.25635 | 0.050354 | 1.3367 | -0.14191 | 0.11444 | 0.004578 | 122.9095 | 122.6807 | 53.4576 | -123.2666 | 122.9782 | 122.9324 | 79.5456 | -123.1842
3118.0156 | 123.0148 | -50.7431 | 72.2168 | -0.22141 | 0.011722 | 0.068037 | 0.069663 | 0.13057 | -0.00093145 | -0.0077183 | -0.17563 | -0.0086988 | 0.062555 | 0.058039 | 0.0067718 | -0.010051 | 71.8597 | 72.0428 | 2.5726 | -50.9766 | 72.2397 | -50.8575 | -50.9628 | -49.4751 | 28.9444 | -50.7523 | 72.3221 | 72.2488 | -50.9491 | -50.9537 | -0.11444 | -0.21973 | 0.022888 | 122.7859 | -0.23346 | -0.013732 | -0.35706 | -0.20599 | -0.21057 | 0.10529 | 1.268 | -0.009155 | 0.20142 | 0.032043 | 122.9828 | 122.6028 | 53.3157 | -123.1796 | 123.0652 | 122.9919 | 79.6875 | -123.1705
3119.0156 | 123.0423 | -50.9857 | 71.9467 | -0.11459 | 0.016421 | 0.068464 | 0.072653 | 0.13142 | 0.0035547 | -0.0064365 | -0.015411 | -0.0093396 | 0.065973 | 0.057185 | 0.0086944 | -0.013469 | 71.5851 | 71.8414 | 2.3941 | -51.1826 | 71.9742 | -51.1139 | -51.2283 | -49.6033 | 28.5416 | -51.2329 | 72.0062 | 71.933 | -51.2192 | -51.2421 | -0.12817 | -0.24262 | 0.027466 | 122.8271 | -0.19684 | 0.045777 | -0.36163 | -0.23346 | -0.25635 | 0.05951 | 1.3824 | -0.24719 | 0.009155 | -0.013733 | 122.9599 | 122.5708 | 53.3798 | -123.175 | 122.9919 | 122.9187 | 79.5273 | -123.1888
3120.0156 | 123.0194 | -51.3886 | 71.5713 | -0.22903 | 0.011935 | 0.071027 | 0.071372 | 0.12886 | -0.0015723 | -0.0089999 | 0.3508 | -0.0089124 | 0.065759 | 0.057185 | 0.0065582 | -0.010692 | 71.1777 | 71.5576 | 2.5909 | -51.6769 | 71.5988 | -51.5213 | -51.6495 | -50.061 | 28.2532 | -51.503 | 71.6309 | 71.5851 | -51.6083 | -51.6312 | -0.13275 | -0.26093 | 0.027466 | 122.9462 | -0.28839 | -0.027466 | -0.39368 | -0.21973 | -0.24262 | 0.059509 | 1.3275 | -0.11444 | 0.12817 | 0.013733 | 122.9874 | 122.5662 | 53.9795 | -123.2208 | 123.0194 | 122.9736 | 79.6417 | -123.2025
3121.0312 | 123.1201 | -53.1601 | 69.7311 | 0.16006 | 0.012362 | 0.071241 | 0.067954 | 0.12886 | -0.0041357 | -0.0087863 | 0.29739 | -0.0095532 | 0.060419 | 0.05398 | 0.006131 | -0.010051 | 69.4565 | 69.6808 | 2.2476 | -53.3844 | 69.7449 | -53.3112 | -53.389 | -51.7548 | 26.6327 | -53.3295 | 69.7815 | 69.7128 | -53.3798 | -53.4119 | -0.15106 | -0.22888 | 0.013733 | 122.8409 | -0.2243 | 0.004578 | -0.27466 | -0.21973 | -0.25177 | 0.050354 | 1.4053 | -0.16937 | 0.082397 | -0.01831 | 122.905 | 122.6166 | 55.4077 | -123.1201 | 122.9416 | 122.8729 | 79.7928 | -123.143
3122.0156 | 123.0515 | -50.798 | 72.1619 | -0.17563 | 0.011294 | 0.069959 | 0.073721 | 0.12971 | -0.0032813 | -0.0085727 | -0.14511 | -0.009126 | 0.064051 | 0.054194 | 0.0084808 | -0.013683 | 71.9284 | 72.0657 | 2.2385 | -50.9583 | 72.2855 | -50.8301 | -50.9445 | -49.4202 | 28.5187 | -50.8621 | 72.2809 | 72.1619 | -50.9995 | -51.0223 | -0.032043 | -0.14648 | 0.1236 | 122.8638 | -0.16022 | -0.013733 | -0.23346 | -0.20142 | -0.2243 | 0.11902 | 1.3779 | -0.064087 | 0.16022 | 0 | 123.0835 | 122.7264 | 53.0365 | -123.1064 | 123.0789 | 122.9599 | 79.3167 | -123.1842
3123.0156 | 123.0652 | -50.647 | 72.2855 | -0.17563 | 0.01514 | 0.06825 | 0.072653 | 0.12843 | 0.0027001 | -0.0064365 | -0.12222 | -0.0097668 | 0.064264 | 0.055903 | 0.0097626 | -0.012401 | 72.0703 | 72.1802 | 2.4307 | -50.9354 | 72.3907 | -50.7339 | -50.8392 | -49.2599 | 28.6148 | -50.7523 | 72.3953 | 72.2855 | -50.853 | -50.8713 | -0.086975 | -0.19226 | 0.10529 | 122.8271 | -0.28839 | -0.096131 | -0.21515 | -0.20599 | -0.2243 | 0.10986 | 1.387 | -0.10528 | 0.11902 | 0 | 123.0377 | 122.7173 | 53.0777 | -123.1247 | 123.0423 | 122.9324 | 79.2618 | -123.1567
3124.0156 | 122.9828 | -50.2579 | 72.6837 | -0.19089 | 0.011722 | 0.069532 | 0.071585 | 0.12928 | -0.0026405 | -0.0079319 | -0.16037 | -0.010621 | 0.063837 | 0.058039 | 0.0086944 | -0.011546 | 72.3862 | 72.6059 | 2.417 | -50.4684 | 72.7798 | -50.3632 | -50.4593 | -48.912 | 28.8071 | -50.4547 | 72.7844 | 72.6974 | -50.4639 | -50.4822 | -0.10529 | -0.20142 | 0.09613 | 122.8638 | -0.21057 | -0.009155 | -0.29755 | -0.20599 | -0.2243 | 0.10071 | 1.3458 | -0.19684 | 0.027466 | 0.013733 | 123.0377 | 122.644 | 52.6749 | -123.143 | 123.0423 | 122.9553 | 79.0649 | -123.1659
3125.0156 | 123.0652 | -50.528 | 72.3953 | -0.17563 | 0.013431 | 0.069532 | 0.073508 | 0.12822 | -0.00029045 | -0.0062229 | -0.18326 | -0.011049 | 0.062769 | 0.055262 | 0.0074126 | -0.013469 | 72.2443 | 72.3495 | 2.2705 | -50.647 | 72.5555 | -50.5508 | -50.6424 | -49.1592 | 28.6057 | -50.6561 | 72.5143 | 72.4365 | -50.7156 | -50.7614 | -0.022888 | -0.11444 | 0.16022 | 122.8775 | -0.11902 | -0.004578 | -0.15106 | -0.18768 | -0.23346 | 0.11902 | 1.3687 | -0.12817 | 0.10529 | 0.041198 | 123.0835 | 122.7722 | 52.7985 | -123.0377 | 123.0423 | 122.9645 | 79.1336 | -123.1567
3126.0156 | 123.0377 | -52.4231 | 70.5002 | -0.21378 | 0.01044 | 0.066969 | 0.071799 | 0.12864 | -0.0037085 | -0.010068 | -0.13748 | -0.010194 | 0.063196 | 0.055476 | 0.0076264 | -0.013042 | 70.4544 | 70.5872 | 2.2751 | -52.6291 | 70.6512 | -52.4963 | -52.597 | -51.0544 | 27.1133 | -52.5925 | 70.5597 | 70.491 | -52.652 | -52.6794 | -0.073242 | -0.17395 | 0.15106 | 123.0103 | -0.20599 | -0.032043 | -0.045776 | -0.22888 | -0.25635 | 0.059509 | 1.3687 | -0.16937 | 0.086975 | -0.009155 | 123.0743 | 122.8775 | 54.6982 | -123.0972 | 122.9828 | 122.9141 | 79.5364 | -123.1796
3127.0156 | 123.0515 | -50.354 | 72.6288 | -0.44266 | 0.015567 | 0.068678 | 0.074149 | 0.12928 | 0.0014185 | -0.0083591 | -0.2214 | -0.0086988 | 0.06341 | 0.057398 | 0.0074126 | -0.011546 | 72.4686 | 72.6425 | 2.4857 | -50.4822 | 72.8027 | -50.3403 | -50.4547 | -48.9578 | 28.6606 | -50.4822 | 72.7341 | 72.6517 | -50.5463 | -50.5966 | 0.013733 | -0.10071 | 0.17395 | 122.9965 | -0.12817 | -0.027466 | -0.16022 | -0.19226 | -0.24261 | 0.10529 | 1.3962 | -0.12817 | 0.11444 | 0.022888 | 123.1567 | 122.8226 | 52.8397 | -123.0835 | 123.0881 | 123.0057 | 79.0146 | -123.2254
3128.0156 | 123.1293 | -50.6607 | 72.2031 | -0.12985 | 0.011508 | 0.071455 | 0.071372 | 0.13014 | -0.0039221 | -0.0072911 | -0.076446 | -0.011903 | 0.062555 | 0.054835 | 0.0063446 | -0.013255 | 72.2443 | 72.4594 | 2.6733 | -50.6516 | 72.4915 | -50.5875 | -50.6882 | -49.086 | 28.8025 | -50.5692 | 72.4686 | 72.377 | -50.766 | -50.8484 | 0.073243 | -0.027465 | 0.28839 | 123.1201 | 0.009156 | 0.036621 | 0.041199 | -0.10529 | -0.18768 | 0.2655 | 1.5747 | 0.091553 | 0.27924 | 0.17395 | 123.1522 | 122.905 | 53.334 | -122.8912 | 123.1293 | 123.0377 | 79.4632 | -123.0515
3129.0156 | 123.0194 | -52.5467 | 70.3949 | -0.14511 | 0.01514 | 0.069746 | 0.073508 | 0.12907 | -0.00071785 | -0.0094273 | -0.168 | -0.0089124 | 0.064478 | 0.055903 | 0.0086944 | -0.014537 | 70.0928 | 70.253 | 2.3346 | -52.7756 | 70.4773 | -52.6978 | -52.8076 | -51.1551 | 27.0355 | -52.6016 | 70.4819 | 70.3949 | -52.7573 | -52.7802 | -0.15106 | -0.26093 | 0.082398 | 122.7997 | -0.22888 | 0.032043 | -0.30212 | -0.21057 | -0.23346 | 0.086976 | 1.3916 | -0.054932 | 0.17853 | 0 | 123.024 | 122.6395 | 54.8813 | -123.2025 | 123.0286 | 122.9416 | 79.5822 | -123.175
3130.0156 | 123.111 | -52.6108 | 70.3308 | -0.22903 | 0.011081 | 0.069746 | 0.071799 | 0.12843 | -0.0024269 | -0.0081455 | -0.13748 | -0.011262 | 0.063196 | 0.05633 | 0.007199 | -0.011546 | 70.2026 | 70.4269 | 2.7054 | -52.6657 | 70.4727 | -52.6337 | -52.7298 | -51.1642 | 27.0401 | -52.6794 | 70.3766 | 70.2942 | -52.7939 | -52.858 | -0.022888 | -0.11902 | 0.14191 | 123.0377 | -0.054931 | 0.064087 | -0.12817 | -0.1831 | -0.24719 | 0.045776 | 1.4465 | -0.068664 | 0.17853 | -0.036622 | 123.0835 | 122.8134 | 55.3162 | -123.0606 | 122.9874 | 122.905 | 79.6509 | -123.1888
3131.0156 | 123.024 | -51.5442 | 71.4294 | -0.22141 | 0.013431 | 0.0706 | 0.071799 | 0.13035 | -0.00050425 | -0.0072911 | -0.21378 | -0.011689 | 0.063623 | 0.057612 | 0.0074126 | -0.016887 | 71.0632 | 71.2189 | 2.536 | -51.8646 | 71.434 | -51.7136 | -51.796 | -50.0702 | 27.9922 | -51.7593 | 71.553 | 71.4294 | -51.7181 | -51.7639 | -0.16937 | -0.25177 | 0.004578 | 122.7631 | -0.32043 | -0.068665 | -0.36621 | -0.17395 | -0.21973 | 0.1236 | 1.474 | -0.21515 | 0.004578 | 0 | 122.9782 | 122.6074 | 54.0802 | -123.2254 | 123.0972 | 122.9736 | 79.5364 | -123.1934
3132.0156 | 123.1522 | -51.1826 | 71.7133 | -0.168 | 0.0087307 | 0.072096 | 0.069022 | 0.13057 | -0.0047767 | -0.0070773 | 0.83908 | -0.012544 | 0.063196 | 0.056544 | 0.0084808 | -0.013255 | 71.5393 | 71.8506 | 2.8244 | -51.2741 | 71.814 | -51.3153 | -51.4435 | -49.7955 | 28.2211 | -51.2054 | 71.6995 | 71.6537 | -51.4389 | -51.4664 | -0.13275 | -0.26093 | 0.10071 | 123.0331 | -0.091553 | 0.16937 | -0.17395 | -0.25635 | -0.28381 | -0.013733 | 1.387 | -0.022888 | 0.26093 | -0.059509 | 122.9965 | 122.7219 | 54.007 | -123.1567 | 122.8821 | 122.8363 | 79.4037 | -123.1796
3133.0156 | 123.0606 | -53.5309 | 69.3604 | -0.27481 | 0.013431 | 0.069746 | 0.073294 | 0.12886 | -0.00029045 | -0.0096409 | -0.22903 | -0.010621 | 0.062769 | 0.054835 | 0.0086944 | -0.013255 | 69.603 | 69.7723 | 2.5497 | -53.302 | 69.873 | -53.2288 | -53.334 | -51.7181 | 26.6556 | -53.1967 | 69.8776 | 69.7495 | -53.476 | -53.5995 | 0.30212 | 0.19684 | 0.51269 | 123.3032 | 0.22888 | 0.032043 | 0.24261 | 0.054932 | -0.068664 | 0.51727 | 1.8127 | 0.33417 | 0.40283 | 0.3891 | 123.4039 | 123.1338 | 56.0806 | -122.6944 | 123.4085 | 123.2803 | 80.1865 | -122.9599
3134.0156 | 123.1659 | -52.2263 | 70.6558 | -0.099335 | 0.0091581 | 0.069959 | 0.072867 | 0.1295 | -0.0045631 | -0.0070773 | 0.015106 | -0.010835 | 0.064905 | 0.057185 | 0.0059174 | -0.012401 | 70.4865 | 70.7016 | 2.7328 | -52.3956 | 70.7382 | -52.3361 | -52.4643 | -50.766 | 27.4521 | -52.2675 | 70.6741 | 70.61 | -52.4643 | -52.5238 | -0.10986 | -0.23804 | 0.082397 | 122.9279 | -0.16937 | 0.068664 | -0.16937 | -0.23804 | -0.29755 | 0.01831 | 1.4603 | -0.041199 | 0.25635 | -0.045777 | 122.9645 | 122.7127 | 54.9591 | -123.1201 | 122.9004 | 122.8363 | 79.6783 | -123.1796
3135.0156 | 123.1247 | -50.6699 | 72.2763 | -0.23666 | 0.011722 | 0.069959 | 0.071372 | 0.12693 | -0.0011451 | -0.0075047 | -0.15274 | -0.010408 | 0.064905 | 0.05633 | 0.0084808 | -0.013469 | 72.1252 | 72.3404 | 2.7786 | -50.766 | 72.3724 | -50.6973 | -50.8209 | -49.2462 | 28.6377 | -50.7431 | 72.2992 | 72.1985 | -50.8942 | -50.9079 | -0.027466 | -0.15106 | 0.096131 | 123.0103 | -0.09613 | 0.054932 | -0.15106 | -0.2243 | -0.23804 | 0.022888 | 1.4236 | -0.073242 | 0.1648 | -0.07782 | 123.0423 | 122.7951 | 53.4485 | -123.0972 | 122.9691 | 122.8683 | 79.3076 | -123.1842
3136.0156 | 123.1659 | -53.2928 | 69.5251 | -0.099335 | 0.0093717 | 0.071027 | 0.072226 | 0.12843 | -0.0045631 | -0.0064365 | -0.061188 | -0.010408 | 0.062769 | 0.056758 | 0.00784 | -0.012828 | 69.4153 | 69.635 | 2.5589 | -53.4714 | 69.6671 | -53.4439 | -53.508 | -51.8326 | 26.619 | -53.3707 | 69.6075 | 69.5206 | -53.5538 | -53.5858 | -0.15106 | -0.21515 | 0.14191 | 122.9279 | -0.17853 | 0.036621 | -0.10986 | -0.26093 | -0.29297 | 0.082398 | 1.4603 | -0.07782 | 0.21515 | -0.004577 | 122.9599 | 122.7081 | 55.8517 | -123.0331 | 122.9004 | 122.8134 | 79.9118 | -123.111
3137.0156 | 123.1064 | -51.4618 | 71.4294 | -0.18326 | 0.010226 | 0.071455 | 0.069449 | 0.12993 | 0.00035035 | -0.0079319 | -0.18326 | -0.009126 | 0.060846 | 0.054835 | 0.0074126 | -0.012614 | 71.2692 | 71.4478 | 2.7603 | -51.6449 | 71.5073 | -51.5808 | -51.6907 | -50.0519 | 28.0289 | -51.5808 | 71.4844 | 71.4111 | -51.709 | -51.7181 | -0.11902 | -0.22888 | 0.07782 | 122.9095 | -0.1831 | 0.045777 | -0.16022 | -0.24719 | -0.25635 | 0.054932 | 1.4099 | -0.11902 | 0.13733 | -0.01831 | 122.9691 | 122.731 | 54.2221 | -123.1201 | 122.9462 | 122.8729 | 79.4907 | -123.1476
3138.0156 | 123.1384 | -51.8875 | 70.9854 | -0.068817 | 0.0063809 | 0.069746 | 0.070944 | 0.12864 | -0.0030677 | -0.0094273 | 0.037995 | -0.012971 | 0.062342 | 0.056117 | 0.006131 | -0.013255 | 70.9259 | 71.1502 | 2.7237 | -51.9333 | 71.1868 | -51.9058 | -51.9836 | -50.3769 | 27.5757 | -51.9104 | 71.1044 | 70.9946 | -52.0935 | -52.1164 | -0.018311 | -0.096131 | 0.20142 | 123.0377 | -0.045777 | 0.050354 | -0.05951 | -0.20599 | -0.22888 | 0.11902 | 1.5106 | -0.022888 | 0.20599 | 0.009155 | 123.0743 | 122.8134 | 54.6112 | -122.9691 | 122.9919 | 122.8821 | 79.4632 | -123.1018
3139.0156 | 123.1796 | -49.3927 | 73.494 | -0.17563 | 0.0083035 | 0.071455 | 0.072226 | 0.1295 | -0.00071785 | -0.0085727 | -0.35873 | -0.010621 | 0.065332 | 0.054621 | 0.0080536 | -0.012401 | 73.3521 | 73.6084 | 2.8748 | -49.3195 | 73.613 | -49.4934 | -49.5712 | -47.9416 | 29.5532 | -49.4064 | 73.5626 | 73.4344 | -49.6216 | -49.6536 | -0.10071 | -0.17853 | 0.11902 | 123.0011 | 0.073242 | 0.25177 | -0.14191 | -0.22888 | -0.26093 | 0.068664 | 1.4511 | -0.013733 | 0.24719 | -0.05951 | 123.0057 | 122.7448 | 52.2675 | -123.0652 | 122.9553 | 122.8271 | 78.9459 | -123.1476
3140.0156 | 123.1522 | -50.9628 | 71.9147 | -0.49606 | 0.0091581 | 0.069532 | 0.069022 | 0.12758 | -0.0024269 | -0.0072911 | 0.10666 | -0.011903 | 0.062555 | 0.056971 | 0.008908 | -0.014537 | 71.6492 | 71.8414 | 2.7237 | -51.2283 | 71.9513 | -51.1597 | -51.2375 | -49.5483 | 28.2532 | -50.9995 | 71.9421 | 71.8506 | -51.2283 | -51.2558 | -0.19684 | -0.27466 | 0.036621 | 122.8043 | -0.2655 | 0.009155 | -0.2655 | -0.2655 | -0.29297 | 0.027466 | 1.4145 | -0.036621 | 0.25635 | -0.064087 | 122.9141 | 122.612 | 53.6865 | -123.1522 | 122.905 | 122.8134 | 79.216 | -123.1705
3141.0156 | 123.1201 | -50.3723 | 72.5006 | -0.19852 | 0.0091581 | 0.075514 | 0.076071 | 0.12886 | 0.0027001 | -0.0070773 | -0.37399 | -0.01233 | 0.065332 | 0.057612 | 0.0099762 | -0.013683 | 72.3084 | 72.551 | 2.8931 | -50.5966 | 72.5693 | -50.4913 | -50.5966 | -48.8846 | 28.8025 | -50.4044 | 72.5647 | 72.4594 | -50.5829 | -50.6149 | -0.11902 | -0.2243 | 0.068665 | 122.9233 | -0.2243 | 0 | -0.19226 | -0.21057 | -0.24261 | 0.064087 | 1.4877 | -0.032044 | 0.21057 | -0.041198 | 122.9416 | 122.6807 | 53.2654 | -123.0972 | 122.937 | 122.8317 | 79.1748 | -123.1155
3142.0156 | 123.1247 | -51.5121 | 71.3837 | 0.045624 | 0.0097989 | 0.071668 | 0.070944 | 0.12864 | -0.00050425 | -0.0072911 | 0.0914 | -0.011262 | 0.062342 | 0.056758 | 0.0063446 | -0.012187 | 71.2463 | 71.3928 | 2.8702 | -51.6678 | 71.521 | -51.5854 | -51.6815 | -50.0427 | 27.9465 | -51.4938 | 71.4706 | 71.3791 | -51.7273 | -51.7548 | -0.073242 | -0.16937 | 0.13733 | 122.905 | -0.15564 | 0.013733 | -0.13733 | -0.21515 | -0.24262 | 0.086975 | 1.4694 | 0.018311 | 0.26093 | -0.004578 | 123.0331 | 122.7585 | 54.3823 | -123.0652 | 122.9828 | 122.8912 | 79.4586 | -123.1384
3143.0156 | 123.1842 | -52.0889 | 70.7932 | -0.045929 | 0.0072355 | 0.073164 | 0.070303 | 0.12693 | -0.0026405 | -0.0094273 | 0.053253 | -0.010408 | 0.063623 | 0.056544 | 0.0082672 | -0.014537 | 70.7062 | 70.8984 | 2.948 | -52.2079 | 70.9442 | -52.1484 | -52.2263 | -50.5783 | 27.507 | -52.1622 | 70.8572 | 70.7748 | -52.327 | -52.3499 | -0.059509 | -0.13733 | 0.15106 | 122.9874 | -0.11902 | 0.01831 | -0.086975 | -0.23804 | -0.26093 | 0.064087 | 1.5106 | -0.073242 | 0.18768 | -0.018311 | 123.0331 | 122.7951 | 55.0369 | -123.0194 | 122.9462 | 122.8638 | 79.5959 | -123.143
3144.0156 | 123.1064 | -51.9608 | 70.8939 | 0.022736 | 0.0072355 | 0.0706 | 0.072653 | 0.12971 | -0.0037085 | -0.0072911 | 0.2211 | -0.0097668 | 0.062342 | 0.055689 | 0.0086944 | -0.014537 | 70.8023 | 70.9717 | 3.0121 | -52.0981 | 71.0678 | -52.0111 | -52.0981 | -50.4456 | 27.5986 | -51.9974 | 71.022 | 70.9259 | -52.1393 | -52.2125 | -0.050354 | -0.13733 | 0.17395 | 122.9324 | -0.13733 | 0 | -0.091553 | -0.17853 | -0.25177 | 0.12817 | 1.5152 | -0.036621 | 0.21515 | 0.032043 | 123.0286 | 122.7631 | 54.9728 | -122.9919 | 122.9828 | 122.8867 | 79.5593 | -123.1064
3145.0156 | 123.1522 | -51.4618 | 71.4066 | -0.061188 | 0.0095853 | 0.0706 | 0.068594 | 0.12672 | -7.6852e-05 | -0.0072911 | 0.0074766 | -0.010835 | 0.061273 | 0.056971 | 0.0080536 | -0.012187 | 71.2509 | 71.4478 | 3.0487 | -51.6586 | 71.4935 | -51.6037 | -51.7136 | -49.9237 | 27.9648 | -51.5167 | 71.5027 | 71.3791 | -51.6724 | -51.7044 | -0.14191 | -0.25177 | 0.086975 | 122.9095 | -0.19684 | 0.054932 | -0.15564 | -0.21057 | -0.24262 | 0.096131 | 1.5381 | -0.054932 | 0.18768 | -0.027466 | 122.9553 | 122.7127 | 54.5105 | -123.1201 | 122.9645 | 122.8409 | 79.4266 | -123.111
3146.0156 | 123.1155 | -50.9262 | 71.9971 | 0.037994 | 0.0089443 | 0.069319 | 0.069663 | 0.12928 | -0.0019995 | -0.0064365 | 0.09903 | -0.010835 | 0.062555 | 0.055476 | 0.011685 | -0.013469 | 71.7133 | 71.9009 | 3.1769 | -51.178 | 71.933 | -51.091 | -51.2054 | -49.4843 | 28.2166 | -51.0132 | 72.0154 | 71.9055 | -51.1642 | -51.1734 | -0.16479 | -0.27924 | -0.064087 | 122.8271 | -0.25177 | 0.027465 | -0.28381 | -0.23804 | -0.24719 | 0.018311 | 1.442 | -0.086976 | 0.16022 | -0.091552 | 122.8592 | 122.6395 | 54.1031 | -123.2025 | 122.9416 | 122.8317 | 79.1428 | -123.1705
3147.0156 | 123.1338 | -49.8184 | 73.0499 | -0.068817 | 0.0059537 | 0.070173 | 0.069235 | 0.12672 | -0.0017859 | -0.0079319 | -0.00015237 | -0.0097668 | 0.061914 | 0.055903 | 0.0091216 | -0.012401 | 72.7936 | 72.995 | 3.186 | -50.1068 | 73.0545 | -50.0153 | -50.1343 | -48.3261 | 29.2419 | -49.91 | 73.1186 | 72.9858 | -50.0702 | -50.0977 | -0.19684 | -0.31586 | 0.004577 | 122.8134 | -0.28839 | 0.027465 | -0.25635 | -0.25177 | -0.27924 | 0.068664 | 1.4923 | -0.091553 | 0.18768 | -0.064087 | 122.8729 | 122.612 | 53.0045 | -123.1842 | 122.937 | 122.8043 | 79.0604 | -123.1476
3148.0156 | 123.111 | -52.6199 | 70.2301 | 0.16006 | 0.011935 | 0.073164 | 0.070303 | 0.12672 | 0.00099115 | -0.0075047 | 0.13718 | -0.011262 | 0.062982 | 0.054194 | 0.009549 | -0.013896 | 70.1157 | 70.2896 | 2.6962 | -52.8397 | 70.3537 | -52.7252 | -52.8122 | -51.1276 | 26.9669 | -52.7664 | 70.3079 | 70.2118 | -52.8534 | -52.8809 | -0.10529 | -0.19226 | 0.1236 | 122.9095 | -0.21973 | -0.027466 | -0.11444 | -0.23346 | -0.26093 | 0.077819 | 1.4923 | -0.14648 | 0.11444 | -0.018311 | 122.9736 | 122.7356 | 55.3162 | -123.0423 | 122.9279 | 122.8317 | 79.5868 | -123.111
3149.0156 | 123.1522 | -51.6495 | 71.2097 | -0.03067 | 0.0087307 | 0.072736 | 0.069449 | 0.12736 | -0.0017859 | -0.0053683 | 0.0074766 | -0.011049 | 0.064478 | 0.055903 | 0.0057038 | -0.014537 | 71.1273 | 71.3425 | 2.8381 | -51.8051 | 71.3791 | -51.7044 | -51.8372 | -50.1068 | 27.8458 | -51.6998 | 71.2601 | 71.1777 | -51.8784 | -51.9333 | -0.054932 | -0.18768 | 0.16937 | 122.9919 | -0.15564 | 0.032043 | -0.082398 | -0.22888 | -0.28381 | 0.050354 | 1.5427 | -0.050354 | 0.23346 | -0.032044 | 123.0286 | 122.7768 | 54.4876 | -123.0469 | 122.9095 | 122.8271 | 79.4952 | -123.143
3150.0156 | 123.0972 | -50.1892 | 72.6425 | 0.068512 | 0.01044 | 0.071241 | 0.070517 | 0.12886 | 0.0014185 | -0.0075047 | 0.11429 | -0.010835 | 0.063196 | 0.058467 | 0.0084808 | -0.01176 | 72.6151 | 72.7936 | 3.1265 | -50.3082 | 72.8668 | -50.1892 | -50.2487 | -48.674 | 28.9627 | -50.1068 | 72.8119 | 72.6974 | -50.3677 | -50.3815 | 0 | -0.059509 | 0.2243 | 122.9828 | -0.11902 | -0.05951 | -0.027466 | -0.17853 | -0.19226 | 0.16937 | 1.5152 | 0.082397 | 0.27466 | 0.054932 | 123.056 | 122.8043 | 53.3157 | -122.8912 | 123.0011 | 122.8867 | 79.1519 | -123.024
3151.0156 | 123.175 | -52.4094 | 70.4269 | -0.0383 | 0.0072355 | 0.070387 | 0.071585 | 0.12843 | -7.6852e-05 | -0.0092137 | -0.045929 | -0.011689 | 0.061914 | 0.05633 | 0.0074126 | -0.01411 | 70.372 | 70.5414 | 2.9251 | -52.5558 | 70.5963 | -52.4918 | -52.5787 | -50.8713 | 27.2003 | -52.533 | 70.5368 | 70.4041 | -52.6566 | -52.6932 | -0.082397 | -0.16937 | 0.16937 | 122.9507 | -0.14648 | 0.022888 | -0.054932 | -0.24719 | -0.28381 | 0.10986 | 1.5381 | -0.1236 | 0.16022 | -0.022888 | 123.0057 | 122.7814 | 55.3345 | -123.0057 | 122.9462 | 122.8134 | 79.6097 | -123.1201
3152.0156 | 123.1201 | -51.8921 | 70.9259 | 0.12955 | 0.010867 | 0.070173 | 0.069449 | 0.12886 | 0.00035035 | -0.0040867 | 0.15244 | -0.009126 | 0.06106 | 0.055049 | 0.0099762 | -0.013683 | 70.903 | 71.0678 | 3.0167 | -52.0294 | 71.1594 | -51.9241 | -52.0157 | -50.4227 | 27.5436 | -52.066 | 71.0495 | 70.9305 | -52.1393 | -52.1896 | -0.032043 | -0.1236 | 0.23346 | 122.9599 | -0.13733 | -0.013733 | -0.022888 | -0.24719 | -0.29755 | 0.1236 | 1.4694 | -0.17395 | 0.1236 | 0.004578 | 123.0515 | 122.7951 | 54.9088 | -122.9416 | 122.9416 | 122.8226 | 79.4357 | -123.1155
3153.0156 | 123.1064 | -52.2354 | 70.6284 | -0.053558 | 0.0065945 | 0.071027 | 0.071158 | 0.12736 | -0.0026405 | -0.0085727 | 0.037995 | -0.010408 | 0.06341 | 0.05633 | 0.00784 | -0.013255 | 70.4361 | 70.5734 | 2.9663 | -52.5055 | 70.7016 | -52.3911 | -52.478 | -50.7339 | 27.3239 | -52.3636 | 70.7062 | 70.6009 | -52.4689 | -52.4918 | -0.15564 | -0.24261 | 0.073242 | 122.8088 | -0.27008 | -0.027466 | -0.19226 | -0.23346 | -0.25635 | 0.07782 | 1.5015 | -0.12817 | 0.12817 | -0.027466 | 122.937 | 122.6715 | 55.2017 | -123.1064 | 122.9416 | 122.8363 | 79.5593 | -123.1201
3154.0156 | 123.0927 | -52.0111 | 70.8435 | 0.17532 | 0.012149 | 0.069319 | 0.072653 | 0.12758 | 0.00077755 | -0.0053683 | 0.2211 | -0.010194 | 0.06341 | 0.057398 | 0.008908 | -0.013896 | 70.7016 | 70.8755 | 3.2455 | -52.2446 | 70.9122 | -52.153 | -52.2446 | -50.4593 | 27.5665 | -52.0935 | 70.9259 | 70.784 | -52.24 | -52.2812 | -0.14191 | -0.23346 | 0.068664 | 122.8867 | -0.23346 | 0 | -0.14191 | -0.22888 | -0.27008 | 0.082397 | 1.5518 | -0.082398 | 0.18768 | -0.059509 | 122.9233 | 122.7127 | 55.2567 | -123.0881 | 122.937 | 122.7951 | 79.5776 | -123.1247
3155.0156 | 123.1705 | -50.6012 | 72.2443 | -0.091705 | 0.0093717 | 0.069532 | 0.072867 | 0.12993 | -0.0039221 | -0.0085727 | -0.00015237 | -0.010835 | 0.061914 | 0.054194 | 0.0074126 | -0.014323 | 72.0703 | 72.2443 | 3.3188 | -50.8484 | 72.3084 | -50.7706 | -50.8804 | -49.0952 | 28.7109 | -50.6561 | 72.3129 | 72.2214 | -50.8347 | -50.8713 | -0.16937 | -0.27924 | 0.064087 | 122.8455 | -0.24719 | 0.032043 | -0.17395 | -0.23346 | -0.27008 | 0.068664 | 1.506 | -0.054932 | 0.21515 | -0.022888 | 122.9095 | 122.6715 | 53.92 | -123.1247 | 122.9141 | 122.8226 | 79.3121 | -123.1155
3156.0156 | 123.111 | -51.5396 | 71.3058 | 0.14481 | 0.0095853 | 0.068678 | 0.068594 | 0.128 | 0.0022729 | -0.0075047 | 0.18295 | -0.011262 | 0.063196 | 0.056544 | 0.00784 | -0.014537 | 71.2601 | 71.3058 | 3.0853 | -51.8509 | 71.3516 | -51.709 | -51.828 | -49.9649 | 28.0518 | -51.6266 | 71.402 | 71.283 | -51.7456 | -51.7868 | -0.16937 | -0.28839 | 0.045777 | 122.8455 | -0.31128 | -0.022888 | -0.045776 | -0.20599 | -0.24719 | 0.096131 | 1.5747 | -0.086975 | 0.16022 | -0.022888 | 122.8912 | 122.7997 | 54.6249 | -123.1338 | 122.9416 | 122.8226 | 79.5914 | -123.0927
3157.0156 | 123.1567 | -53.6407 | 69.191 | -0.023041 | 0.0095853 | 0.069746 | 0.071158 | 0.12758 | -0.00093145 | -0.0055821 | -0.0077819 | -0.01233 | 0.060633 | 0.055903 | 0.0069854 | -0.011119 | 69.104 | 69.2917 | 2.5131 | -53.7872 | 69.3878 | -53.7323 | -53.8055 | -52.0569 | 26.4038 | -53.7964 | 69.3329 | 69.2139 | -53.8605 | -53.9154 | -0.091553 | -0.1648 | 0.19684 | 122.9324 | -0.14648 | 0.018311 | -0.086975 | -0.21973 | -0.27466 | 0.14191 | 1.5839 | -0.15564 | 0.11902 | 0.022888 | 123.0286 | 122.7448 | 56.1539 | -122.9965 | 122.9736 | 122.8546 | 80.0446 | -123.1064
3158.0156 | 123.1522 | -53.0685 | 69.8593 | 0.15244 | 0.013644 | 0.0706 | 0.071158 | 0.13099 | 0.00099115 | -0.0045139 | 0.19821 | -0.010408 | 0.063623 | 0.055262 | 0.0057038 | -0.011119 | 69.8593 | 70.015 | 2.623 | -53.064 | 70.0882 | -52.9678 | -53.0777 | -51.4709 | 26.9394 | -53.1281 | 69.928 | 69.8044 | -53.2654 | -53.3066 | 0.10071 | -0.009156 | 0.22888 | 123.0835 | 0.004577 | 0.013733 | 0 | -0.19684 | -0.23804 | 0.068665 | 1.5976 | -0.05951 | 0.17853 | -0.054932 | 123.1567 | 122.9279 | 55.6915 | -122.937 | 122.9965 | 122.8729 | 80.0079 | -123.1659
3159.0156 | 123.143 | -52.0752 | 70.7794 | 0.022736 | 0.0078763 | 0.070173 | 0.071158 | 0.128 | -0.0032813 | -0.0060093 | -0.03067 | -0.01233 | 0.061273 | 0.056971 | 0.0091216 | -0.011974 | 70.8893 | 71.0815 | 2.7374 | -51.9928 | 71.1319 | -51.9333 | -52.0294 | -50.5371 | 27.7405 | -52.2491 | 70.9167 | 70.784 | -52.2903 | -52.3315 | 0.14191 | 0.045776 | 0.35248 | 123.1567 | 0.082397 | 0.036621 | 0.10986 | -0.21515 | -0.25635 | 0.13733 | 1.5381 | -0.17395 | 0.082397 | 0.004578 | 123.2071 | 122.9645 | 54.8126 | -122.8088 | 122.9919 | 122.8592 | 79.8157 | -123.111
3160.0156 | 123.0972 | -51.7319 | 71.1319 | 0.12192 | 0.012149 | 0.07295 | 0.070517 | 0.12907 | -0.0015723 | -0.0032321 | 0.17532 | -0.0093396 | 0.064051 | 0.058467 | 0.010403 | -0.012187 | 71.0129 | 71.1777 | 2.8152 | -51.9287 | 71.2326 | -51.8097 | -51.915 | -50.1755 | 27.8732 | -51.7364 | 71.2326 | 71.0907 | -51.9424 | -51.9974 | -0.077819 | -0.1831 | 0.10071 | 122.9095 | -0.19684 | -0.013733 | -0.11902 | -0.21057 | -0.2655 | 0.10071 | 1.5564 | -0.004577 | 0.26093 | -0.041199 | 122.9645 | 122.7448 | 54.5471 | -123.0469 | 122.9645 | 122.8226 | 79.6051 | -123.1293
3161.0156 | 123.1384 | -53.1784 | 69.6487 | 0.022736 | 0.010226 | 0.071027 | 0.071799 | 0.12629 | -0.0024269 | -0.0075047 | 0.083771 | -0.011049 | 0.062342 | 0.057185 | 0.0084808 | -0.011333 | 69.5251 | 69.7449 | 2.6047 | -53.3386 | 69.8227 | -53.27 | -53.3661 | -51.6861 | 26.7471 | -53.27 | 69.7311 | 69.6304 | -53.4164 | -53.4622 | -0.091552 | -0.18768 | 0.17395 | 122.9233 | -0.16022 | 0.027466 | -0.1236 | -0.23804 | -0.28381 | 0.082397 | 1.4923 | -0.091552 | 0.19226 | -0.018311 | 123.0011 | 122.7036 | 55.7831 | -123.0148 | 122.9095 | 122.8088 | 79.9255 | -123.111
3162.0156 | 123.1201 | -52.6337 | 70.2438 | 0.11429 | 0.0097989 | 0.069105 | 0.068808 | 0.128 | 0.0016321 | -0.0066501 | 0.20584 | -0.010194 | 0.063196 | 0.055262 | 0.008908 | -0.01411 | 70.0012 | 70.1523 | 2.6688 | -52.9221 | 70.2026 | -52.8488 | -52.9404 | -51.1734 | 27.1042 | -52.8076 | 70.2301 | 70.0836 | -52.9175 | -52.9312 | -0.21515 | -0.3067 | -0.041198 | 122.7859 | -0.28839 | 0.018311 | -0.24261 | -0.28381 | -0.29755 | -0.013732 | 1.4603 | -0.17395 | 0.1236 | -0.16022 | 122.8363 | 122.6349 | 55.3024 | -123.1842 | 122.8638 | 122.7173 | 79.7379 | -123.175
3163.0156 | 123.1659 | -52.8214 | 70.0333 | -0.0383 | 0.0080899 | 0.069746 | 0.071372 | 0.1295 | -0.0032813 | -0.0064365 | -0.03067 | -0.012544 | 0.062128 | 0.055903 | 0.0065582 | -0.012614 | 69.9234 | 70.1294 | 2.8885 | -52.9678 | 70.1752 | -52.9312 | -53.0273 | -51.2466 | 27.3056 | -52.8809 | 70.1157 | 70.0241 | -53.0457 | -53.0731 | -0.10986 | -0.20599 | 0.14191 | 122.9507 | -0.14648 | 0.05951 | -0.10986 | -0.2243 | -0.25177 | 0.082398 | 1.5747 | -0.059509 | 0.19226 | -0.009155 | 122.9965 | 122.7448 | 55.7098 | -123.0606 | 122.937 | 122.8455 | 80.127 | -123.1064
3164.0156 | 123.1338 | -51.6129 | 71.2418 | 0.12955 | 0.011081 | 0.069959 | 0.071372 | 0.13121 | 0.00035035 | -0.0083591 | 0.15244 | -0.010835 | 0.063837 | 0.056117 | 0.0063446 | -0.012614 | 70.8618 | 71.1136 | 2.8198 | -51.8463 | 71.2051 | -51.8051 | -51.9196 | -50.0656 | 28.0746 | -51.6129 | 71.3516 | 71.2234 | -51.8555 | -51.9012 | -0.19226 | -0.3067 | -0.036621 | 122.7264 | -0.23346 | 0.073243 | -0.37994 | -0.24262 | -0.28839 | 0.10986 | 1.5472 | 0 | 0.28839 | -0.01831 | 122.818 | 122.4747 | 54.4327 | -123.1613 | 122.9645 | 122.8363 | 79.6875 | -123.143
3165.0156 | 123.143 | -51.6953 | 71.1639 | -0.023041 | 0.0070217 | 0.070173 | 0.068808 | 0.12971 | -0.00050425 | -0.0072911 | -0.0077819 | -0.009126 | 0.06106 | 0.056758 | 0.0076264 | -0.011974 | 71.0632 | 71.2509 | 2.6184 | -51.8417 | 71.3333 | -51.7639 | -51.8738 | -50.1297 | 28.0243 | -51.7502 | 71.2463 | 71.1227 | -51.9104 | -51.9836 | -0.068665 | -0.17853 | 0.16937 | 122.9462 | -0.14648 | 0.032043 | -0.10071 | -0.21515 | -0.28839 | 0.082398 | 1.5656 | -0.054932 | 0.23346 | -0.041198 | 123.0286 | 122.7585 | 54.3137 | -123.0377 | 122.9416 | 122.818 | 79.7195 | -123.1476
3166.0156 | 123.1476 | -51.7685 | 71.1365 | 0.12192 | 0.0093717 | 0.071668 | 0.07009 | 0.13014 | 0.00013675 | -0.0066501 | 0.19821 | -0.0095532 | 0.06341 | 0.053553 | 0.0084808 | -0.012828 | 70.9534 | 71.1227 | 2.774 | -51.9562 | 71.1823 | -51.8692 | -51.9745 | -50.2029 | 27.9602 | -51.8097 | 71.2006 | 71.0632 | -51.9608 | -52.0203 | -0.10071 | -0.20599 | 0.045776 | 122.8912 | -0.18768 | 0.01831 | -0.18311 | -0.19226 | -0.25177 | 0.064087 | 1.5656 | -0.041198 | 0.21057 | -0.073243 | 122.9507 | 122.7219 | 54.5425 | -123.111 | 122.9691 | 122.8317 | 79.7287 | -123.1567
3167.0156 | 123.111 | -51.4343 | 71.4294 | 0.015106 | 0.0083035 | 0.071668 | 0.072867 | 0.12736 | -0.0011451 | -0.0068637 | 0.0074766 | -0.010835 | 0.062342 | 0.05633 | 0.006131 | -0.013469 | 71.2143 | 71.4294 | 2.9892 | -51.6403 | 71.489 | -51.6037 | -51.6953 | -49.8688 | 28.418 | -51.4481 | 71.5164 | 71.402 | -51.6724 | -51.6998 | -0.16937 | -0.26093 | 0.05951 | 122.8638 | -0.20599 | 0.054931 | -0.21515 | -0.23804 | -0.2655 | 0.086975 | 1.5656 | -0.013733 | 0.25177 | -0.027465 | 122.9233 | 122.6486 | 54.4235 | -123.1247 | 122.9507 | 122.8363 | 79.8523 | -123.1293
3168.0156 | 123.1293 | -51.6403 | 71.2784 | -0.19852 | 0.010013 | 0.069746 | 0.072653 | 0.12822 | -0.0032813 | -0.0064365 | -0.17563 | -0.010835 | 0.06341 | 0.055476 | 0.0084808 | -0.011974 | 71.1227 | 71.3425 | 3.0716 | -51.7548 | 71.3699 | -51.7227 | -51.8234 | -50.0931 | 28.2578 | -51.7181 | 71.3562 | 71.2006 | -51.8555 | -51.8921 | -0.082397 | -0.1831 | 0.091553 | 122.9828 | -0.11444 | 0.068664 | -0.15564 | -0.21515 | -0.25177 | 0.07782 | 1.5472 | -0.07782 | 0.17395 | -0.077819 | 123.0103 | 122.7631 | 54.7119 | -123.1018 | 122.9965 | 122.8409 | 79.8981 | -123.1705
3169.0156 | 123.1338 | -51.0223 | 71.8231 | -0.00015269 | 0.0083035 | 0.070173 | 0.071799 | 0.128 | -0.00093145 | -0.0060093 | 0.030365 | -0.010621 | 0.061273 | 0.05633 | 0.008908 | -0.013469 | 71.7407 | 71.9696 | 2.9663 | -51.1139 | 72.0428 | -51.0818 | -51.178 | -49.4751 | 28.656 | -51.1093 | 71.9467 | 71.7865 | -51.2878 | -51.3016 | -0.059509 | -0.15564 | 0.21973 | 122.9919 | -0.091553 | 0.064087 | -0.082397 | -0.2655 | -0.27924 | 0.1236 | 1.5472 | -0.086975 | 0.19226 | -0.036621 | 123.0652 | 122.7631 | 53.9886 | -123.0011 | 122.9691 | 122.8088 | 79.6783 | -123.1247
3170.0156 | 123.1247 | -50.8438 | 72.0337 | 0.16769 | 0.010867 | 0.070814 | 0.071372 | 0.13078 | -7.6852e-05 | -0.0057957 | 0.22873 | -0.010194 | 0.065119 | 0.057826 | 0.00784 | -0.013469 | 71.965 | 72.1344 | 3.1586 | -50.9216 | 72.1848 | -50.8621 | -50.9354 | -49.2966 | 28.83 | -50.9171 | 72.1252 | 71.9925 | -51.0818 | -51.0818 | -0.018311 | -0.091553 | 0.15106 | 122.9782 | -0.07782 | 0.013733 | -0.068664 | -0.23804 | -0.23804 | 0.091553 | 1.5472 | -0.073242 | 0.16479 | -0.041198 | 123.0286 | 122.8088 | 54.0024 | -122.9691 | 122.9691 | 122.8363 | 79.6738 | -123.1155
3171.0156 | 123.1293 | -52.1759 | 70.6467 | -0.061188 | 0.0089443 | 0.068891 | 0.072653 | 0.12971 | -0.0022131 | -0.0060093 | -0.038299 | -0.0089124 | 0.064691 | 0.056544 | 0.0080536 | -0.012401 | 70.5826 | 70.7977 | 2.9709 | -52.2995 | 70.8252 | -52.2263 | -52.3178 | -50.5325 | 27.7817 | -52.272 | 70.7748 | 70.6329 | -52.4002 | -52.4506 | -0.050354 | -0.14191 | 0.17853 | 122.9736 | -0.1236 | 0.01831 | -0.064086 | -0.22431 | -0.27466 | 0.12817 | 1.6434 | -0.096131 | 0.17853 | -0.013732 | 123.0011 | 122.7585 | 55.1468 | -122.9645 | 122.9507 | 122.8088 | 79.9576 | -123.0972
3172.0156 | 123.1338 | -50.4822 | 72.4045 | 0.068512 | 0.011935 | 0.070387 | 0.070944 | 0.12587 | -0.00029045 | -0.0077183 | 0.076141 | -0.011903 | 0.063837 | 0.056544 | 0.0091216 | -0.012828 | 72.1207 | 72.3084 | 3.1677 | -50.8026 | 72.3724 | -50.6653 | -50.7523 | -48.8571 | 29.2145 | -50.4135 | 72.5418 | 72.4228 | -50.6561 | -50.7111 | -0.18311 | -0.27008 | -0.032043 | 122.7905 | -0.32043 | -0.050354 | -0.28381 | -0.17395 | -0.22888 | 0.13733 | 1.6251 | 0.068665 | 0.29755 | 0.018311 | 122.8546 | 122.6028 | 53.6499 | -123.1567 | 123.024 | 122.905 | 79.6967 | -123.1155
3173.0156 | 123.1613 | -50.6058 | 72.258 | -0.045929 | 0.0093717 | 0.071882 | 0.072867 | 0.12907 | -0.0022131 | -0.0092137 | 0.015106 | -0.010408 | 0.062342 | 0.05633 | 0.0097626 | -0.013255 | 71.933 | 72.1436 | 3.2501 | -50.9308 | 72.2031 | -50.8942 | -50.9583 | -49.0723 | 29.1321 | -50.9125 | 72.3175 | 72.1939 | -50.8163 | -50.853 | -0.28839 | -0.35248 | -0.054932 | 122.7493 | -0.32501 | 0.027466 | -0.32501 | -0.21057 | -0.24719 | 0.059509 | 1.5335 | -0.3067 | -0.05951 | -0.064087 | 122.8088 | 122.5388 | 53.8559 | -123.2162 | 122.9233 | 122.7997 | 79.7379 | -123.111
3174.0156 | 123.1018 | -52.1439 | 70.7428 | 0.053253 | 0.010226 | 0.071027 | 0.071585 | 0.12928 | -0.0034949 | -0.0072911 | 0.060883 | -0.010194 | 0.06341 | 0.054621 | 0.0091216 | -0.013255 | 70.6146 | 70.7382 | 2.861 | -52.3041 | 70.8389 | -52.2079 | -52.3361 | -50.5783 | 27.8824 | -52.24 | 70.8344 | 70.6833 | -52.3682 | -52.3819 | -0.064087 | -0.19226 | 0.09613 | 122.8821 | -0.16022 | 0.032044 | -0.12817 | -0.2243 | -0.23804 | 0.091553 | 1.5656 | -0.09613 | 0.14191 | -0.059509 | 122.9828 | 122.7585 | 55.0049 | -123.0789 | 122.9782 | 122.8271 | 80.0262 | -123.1247
3175.0156 | 123.175 | -51.3657 | 71.4844 | -0.0383 | 0.0078763 | 0.071668 | 0.069022 | 0.12779 | -0.0015723 | -0.0062229 | -0.023041 | -0.011476 | 0.064478 | 0.057612 | 0.0074126 | -0.010478 | 71.2875 | 71.5073 | 3.0212 | -51.5808 | 71.5302 | -51.5488 | -51.6312 | -49.7726 | 28.5507 | -51.3382 | 71.5622 | 71.4661 | -51.5991 | -51.6266 | -0.1831 | -0.2655 | 0.045776 | 122.8729 | -0.21515 | 0.050354 | -0.19684 | -0.23346 | -0.26093 | 0.07782 | 1.593 | 0.027466 | 0.28839 | -0.018311 | 122.8958 | 122.6532 | 54.3869 | -123.1155 | 122.9279 | 122.8317 | 79.9164 | -123.111
3176.0156 | 123.111 | -52.002 | 70.8755 | 0.15244 | 0.0097989 | 0.0706 | 0.069449 | 0.12822 | -0.00050425 | -0.0066501 | 0.26688 | -0.0095532 | 0.061914 | 0.056971 | 0.0080536 | -0.013042 | 70.7199 | 70.8893 | 2.8336 | -52.1805 | 71.0037 | -52.0889 | -52.1896 | -50.4227 | 28.1387 | -52.1439 | 70.9671 | 70.8023 | -52.2125 | -52.2537 | -0.086975 | -0.18768 | 0.12817 | 122.8912 | -0.17853 | 0.009155 | -0.15564 | -0.21057 | -0.25177 | 0.091553 | 1.5793 | -0.14191 | 0.10986 | -0.073242 | 123.0057 | 122.7219 | 54.8355 | -123.0652 | 122.9691 | 122.8043 | 80.1407 | -123.1293
3177.0156 | 123.1384 | -51.9241 | 70.9213 | 0.0074768 | 0.0083035 | 0.071882 | 0.071158 | 0.1295 | -0.0030677 | -0.0083591 | -0.00015237 | -0.011689 | 0.062982 | 0.055689 | 0.0067718 | -0.013896 | 70.8115 | 70.99 | 2.829 | -52.0981 | 71.0587 | -52.0386 | -52.1393 | -50.3906 | 28.038 | -52.1301 | 70.9671 | 70.8481 | -52.1805 | -52.2171 | -0.11444 | -0.21515 | 0.13733 | 122.9141 | -0.17395 | 0.041199 | -0.10986 | -0.25635 | -0.29297 | 0.045776 | 1.5335 | -0.20599 | 0.086975 | -0.073243 | 122.9828 | 122.7356 | 54.7531 | -123.0606 | 122.8912 | 122.7722 | 79.9622 | -123.1384
3178.0156 | 123.111 | -51.0406 | 71.8597 | 0.068512 | 0.0074491 | 0.069105 | 0.070517 | 0.12608 | -0.00029045 | -0.0066501 | 0.10666 | -0.013612 | 0.061487 | 0.055903 | 0.0082672 | -0.013469 | 71.6812 | 71.8552 | 3.0441 | -51.2283 | 71.9238 | -51.1505 | -51.2375 | -49.4202 | 28.5919 | -51.0498 | 71.9696 | 71.8231 | -51.2375 | -51.265 | -0.10986 | -0.19684 | 0.064087 | 122.8958 | -0.18768 | 0.009155 | -0.17853 | -0.19684 | -0.22431 | 0.10986 | 1.6205 | -0.009156 | 0.21515 | -0.036621 | 122.9645 | 122.7219 | 54.0848 | -123.0972 | 123.0103 | 122.8638 | 79.6326 | -123.1247
3179.0156 | 123.1613 | -51.1414 | 71.7361 | -0.03067 | 0.0072355 | 0.070387 | 0.072012 | 0.12886 | -0.00050425 | -0.0070773 | -0.12985 | -0.0099806 | 0.059992 | 0.055689 | 0.0086944 | -0.012401 | 71.6675 | 71.8735 | 2.9755 | -51.1963 | 71.9193 | -51.1368 | -51.2695 | -49.5117 | 28.5049 | -51.1734 | 71.8323 | 71.6949 | -51.3657 | -51.384 | 0.004577 | -0.12817 | 0.18311 | 123.0148 | -0.054932 | 0.073242 | -0.068665 | -0.22431 | -0.24262 | 0.09613 | 1.6296 | -0.032044 | 0.21057 | -0.041199 | 123.0606 | 122.8088 | 54.1168 | -123.0057 | 122.9736 | 122.8363 | 79.6463 | -123.1201
3180.0156 | 123.143 | -50.9857 | 71.8643 | 0.068512 | 0.0087307 | 0.069532 | 0.069876 | 0.12907 | -0.00071785 | -0.0057957 | 0.068512 | -0.012971 | 0.064905 | 0.055049 | 0.0084808 | -0.011974 | 71.9238 | 72.1069 | 3.0121 | -50.9674 | 72.1893 | -50.885 | -50.9949 | -49.3698 | 28.5507 | -51.0956 | 72.0383 | 71.9147 | -51.1871 | -51.2283 | 0.10071 | -0.009155 | 0.32501 | 123.0927 | 0.018311 | 0.027466 | 0.059509 | -0.20142 | -0.24262 | 0.17395 | 1.6159 | -0.10986 | 0.13275 | 0.050354 | 123.175 | 122.9095 | 53.9978 | -122.8592 | 123.024 | 122.9004 | 79.5364 | -123.0927
3181.0156 | 123.1705 | -51.2192 | 71.6171 | -0.015411 | 0.0080899 | 0.070814 | 0.073081 | 0.12715 | -0.0022131 | -0.0066501 | -0.015411 | -0.014467 | 0.06106 | 0.055903 | 0.0074126 | -0.014323 | 71.6263 | 71.8002 | 3.0991 | -51.3199 | 71.8414 | -51.2375 | -51.3382 | -49.6216 | 28.4454 | -51.384 | 71.7087 | 71.5759 | -51.4618 | -51.503 | -0.018311 | -0.11902 | 0.22431 | 123.0194 | -0.10071 | 0.018311 | 0.009156 | -0.24262 | -0.28381 | 0.091553 | 1.5976 | -0.16479 | 0.11902 | -0.041198 | 123.0606 | 122.8455 | 54.3182 | -122.9553 | 122.9279 | 122.7951 | 79.6646 | -123.1201
3182.0156 | 123.1155 | -52.2812 | 70.5551 | 0.12192 | 0.010867 | 0.070814 | 0.070944 | 0.12971 | -0.00029045 | -0.0057957 | 0.12192 | -0.011049 | 0.063837 | 0.054621 | 0.009549 | -0.013255 | 70.4865 | 70.6696 | 3.0121 | -52.4185 | 70.7703 | -52.3224 | -52.4185 | -50.6836 | 27.6718 | -52.4002 | 70.6879 | 70.5276 | -52.5284 | -52.5696 | -0.041199 | -0.13733 | 0.21515 | 122.9507 | -0.13733 | 0 | -0.068665 | -0.24719 | -0.28839 | 0.13275 | 1.5976 | -0.11902 | 0.16937 | -0.027466 | 123.0515 | 122.7676 | 55.2933 | -122.9736 | 122.9691 | 122.8088 | 79.953 | -123.1247
3183.0156 | 123.1522 | -51.0864 | 71.7682 | -0.0383 | 0.0097989 | 0.070814 | 0.071585 | 0.12629 | -0.00050425 | -0.0051547 | -0.015411 | -0.010835 | 0.062769 | 0.051844 | 0.0065582 | -0.012614 | 71.6309 | 71.846 | 3.0624 | -51.2512 | 71.9284 | -51.1734 | -51.2604 | -49.4019 | 28.7613 | -51.0361 | 71.8872 | 71.7957 | -51.2695 | -51.297 | -0.086975 | -0.17395 | 0.16022 | 122.9324 | -0.16479 | 0.009155 | -0.13733 | -0.1831 | -0.21057 | 0.11902 | 1.6846 | 0.050354 | 0.26093 | 0.027466 | 123.0148 | 122.7173 | 54.1489 | -123.0286 | 122.9736 | 122.8821 | 79.8477 | -123.0652
3184.0156 | 123.1384 | -50.6332 | 72.2672 | 0.0914 | 0.010226 | 0.070387 | 0.071158 | 0.12715 | -0.0013587 | -0.0038731 | 0.12955 | -0.0097668 | 0.063837 | 0.056758 | 0.0082672 | -0.011333 | 71.8872 | 72.0657 | 3.0029 | -51.059 | 72.1298 | -50.9399 | -51.0544 | -49.0952 | 29.0314 | -50.5966 | 72.2855 | 72.171 | -50.8621 | -50.9033 | -0.3067 | -0.42114 | -0.13733 | 122.699 | -0.42572 | -0.004578 | -0.37994 | -0.22888 | -0.27008 | 0.01831 | 1.5381 | 0.036621 | 0.3067 | -0.09613 | 122.7631 | 122.5204 | 53.6362 | -123.3215 | 122.9187 | 122.8043 | 79.6646 | -123.1705
3185.0156 | 123.1338 | -52.4368 | 70.4269 | 0.0074768 | 0.010013 | 0.069319 | 0.071372 | 0.12501 | -0.0011451 | -0.0072911 | -0.068817 | -0.011689 | 0.060419 | 0.056544 | 0.00784 | -0.011974 | 70.3629 | 70.5826 | 2.861 | -52.5558 | 70.5688 | -52.5009 | -52.5787 | -50.8118 | 27.626 | -52.5558 | 70.4956 | 70.3674 | -52.6657 | -52.6978 | -0.064087 | -0.14191 | 0.14191 | 123.0194 | -0.11902 | 0.022888 | -0.064087 | -0.22888 | -0.26093 | 0.068664 | 1.6251 | -0.11902 | 0.14191 | -0.059509 | 123.0057 | 122.7997 | 55.2979 | -123.0057 | 122.9324 | 122.8043 | 80.0629 | -123.1247
3186.0156 | 123.1842 | -51.4755 | 71.3791 | 0.21347 | 0.0076627 | 0.070387 | 0.071799 | 0.12651 | -0.0013587 | -0.0087863 | 0.09903 | -0.011262 | 0.063623 | 0.056117 | 0.008908 | -0.012401 | 71.5851 | 71.759 | 3.1128 | -51.265 | 71.846 | -51.2054 | -51.2833 | -49.8459 | 28.3447 | -51.7044 | 71.5805 | 71.3928 | -51.6449 | -51.7456 | 0.27008 | 0.19226 | 0.46692 | 123.2346 | 0.21057 | 0.01831 | 0.20599 | -0.16937 | -0.27008 | 0.20142 | 1.6296 | -0.22888 | 0.041198 | 0.013733 | 123.3215 | 123.0606 | 54.5883 | -122.6624 | 123.056 | 122.8683 | 79.8203 | -123.1247
3187.0156 | 123.1934 | -50.2579 | 72.5555 | -0.0383 | 0.0065945 | 0.069959 | 0.07009 | 0.12779 | -0.0017859 | -0.0072911 | -0.00015237 | -0.011049 | 0.063196 | 0.05398 | 0.0086944 | -0.013896 | 72.8439 | 73.0682 | 3.6346 | -50.0198 | 73.1461 | -49.9832 | -50.1434 | -48.5092 | 29.3198 | -50.3174 | 72.8073 | 72.6471 | -50.4227 | -50.4776 | 0.27466 | 0.11444 | 0.59051 | 123.3261 | 0.23804 | 0.1236 | 0.28839 | -0.16479 | -0.21973 | 0.25177 | 1.7487 | -0.059509 | 0.16022 | 0.091553 | 123.4039 | 123.1018 | 53.8925 | -122.699 | 123.0652 | 122.905 | 79.5776 | -123.0331
3188.0156 | 123.111 | -51.5396 | 71.3654 | 0.15244 | 0.0095853 | 0.070814 | 0.069022 | 0.13014 | 0.00013675 | -0.0057957 | 0.26688 | -0.010621 | 0.062342 | 0.055689 | 0.0084808 | -0.01411 | 71.0953 | 71.2967 | 3.772 | -51.7731 | 71.3882 | -51.6815 | -51.7822 | -49.9924 | 28.1525 | -51.5854 | 71.434 | 71.2646 | -51.7593 | -51.7914 | -0.14191 | -0.24262 | 0.022889 | 122.8363 | -0.23346 | 0.009156 | -0.27008 | -0.21973 | -0.25177 | 0.068665 | 1.5472 | -0.045776 | 0.20599 | -0.10071 | 122.9279 | 122.6349 | 55.3116 | -123.1476 | 122.9736 | 122.8043 | 79.6921 | -123.1567
3189.0156 | 123.1934 | -50.6424 | 72.2214 | -0.10696 | 0.0070217 | 0.072736 | 0.071372 | 0.128 | 0.00013675 | -0.0092137 | -0.12985 | -0.011476 | 0.061273 | 0.054621 | 0.0091216 | -0.012828 | 72.0474 | 72.2672 | 3.8452 | -50.8209 | 72.2763 | -50.7889 | -50.8759 | -48.9761 | 28.8986 | -50.6378 | 72.29 | 72.1802 | -50.8667 | -50.8942 | -0.14648 | -0.23346 | 0.054931 | 122.9095 | -0.17853 | 0.054931 | -0.17395 | -0.2243 | -0.25177 | 0.068664 | 1.6663 | 0.004578 | 0.25635 | -0.041199 | 122.9187 | 122.6898 | 54.4876 | -123.0972 | 122.9324 | 122.8226 | 79.541 | -123.1155
3190.0156 | 123.111 | -50.8575 | 72.0291 | 0.13718 | 0.011935 | 0.069319 | 0.070303 | 0.12971 | -0.00050425 | -0.0077183 | 0.23636 | -0.0093396 | 0.063623 | 0.055262 | 0.008908 | -0.012401 | 71.8918 | 72.084 | 3.6346 | -51.0269 | 72.1298 | -50.9445 | -51.0086 | -49.2142 | 28.6835 | -50.9262 | 72.0978 | 71.965 | -51.0727 | -51.1002 | -0.086975 | -0.15106 | 0.10071 | 122.9416 | -0.16937 | -0.018311 | -0.13733 | -0.21515 | -0.24262 | 0.068664 | 1.6434 | -0.068664 | 0.17395 | -0.064087 | 122.9874 | 122.7493 | 54.4922 | -123.0377 | 122.9553 | 122.8226 | 79.541 | -123.1293
3191.0156 | 123.1476 | -50.7889 | 72.084 | 1.068 | 0.0076627 | 0.071882 | 0.071799 | 0.12672 | -0.0022131 | -0.0094273 | 0.060883 | -0.010194 | 0.059778 | 0.055262 | 0.007199 | -0.013896 | 71.9009 | 72.084 | 3.6392 | -50.9857 | 72.2031 | -50.8804 | -50.9811 | -49.173 | 28.5828 | -50.8301 | 72.1619 | 72.052 | -51.0544 | -51.0544 | -0.091553 | -0.19226 | 0.11902 | 122.8729 | -0.19684 | -0.004578 | -0.1831 | -0.2655 | -0.2655 | 0.07782 | 1.6159 | -0.041199 | 0.2243 | -0.032043 | 122.9919 | 122.6898 | 54.4281 | -123.0652 | 122.9507 | 122.8409 | 79.3716 | -123.1384
3192.0156 | 123.0377 | -50.7294 | 72.2443 | -0.31296 | 0.016849 | 0.067823 | 0.075644 | 0.12907 | 0.0014185 | -0.0066501 | -0.22903 | -0.008058 | 0.0664 | 0.054835 | 0.0097626 | -0.011974 | 72.0795 | 72.2076 | 3.7079 | -50.8392 | 72.3953 | -50.7431 | -50.8667 | -49.0906 | 28.9078 | -50.8209 | 72.3724 | 72.2031 | -50.9033 | -50.9537 | -0.013733 | -0.13733 | 0.15106 | 122.937 | -0.10986 | 0.027466 | -0.16479 | -0.17395 | -0.2243 | 0.12817 | 1.6388 | -0.091553 | 0.13275 | -0.041199 | 123.1247 | 122.8088 | 54.4373 | -123.111 | 123.1018 | 122.9324 | 79.6371 | -123.1979
3193.0156 | 123.1659 | -50.6149 | 72.2351 | -0.00015269 | 0.0085171 | 0.072096 | 0.069876 | 0.12501 | -0.0030677 | -0.0053683 | 0.030365 | -0.012117 | 0.060633 | 0.05633 | 0.0082672 | -0.012614 | 72.0245 | 72.258 | 3.4195 | -50.7568 | 72.3999 | -50.6927 | -50.7935 | -48.8937 | 29.2969 | -50.6149 | 72.4091 | 72.2855 | -50.798 | -50.8209 | -0.07782 | -0.17853 | 0.16479 | 122.8729 | -0.14191 | 0.036621 | -0.21057 | -0.18311 | -0.20599 | 0.17395 | 1.7212 | 0 | 0.20599 | 0.050354 | 123.0148 | 122.6395 | 54.0344 | -123.0286 | 123.024 | 122.9004 | 79.9118 | -123.056
3194.0156 | 123.0972 | -52.0935 | 70.784 | 0.15244 | 0.011508 | 0.069959 | 0.070944 | 0.12928 | 0.00013675 | -0.0081455 | 0.19058 | -0.0089124 | 0.065546 | 0.056117 | 0.0086944 | -0.013255 | 70.5551 | 70.7428 | 3.0716 | -52.327 | 70.7886 | -52.2537 | -52.327 | -50.3815 | 28.0792 | -52.1484 | 70.871 | 70.7794 | -52.2949 | -52.3041 | -0.16022 | -0.23346 | 0.004577 | 122.8363 | -0.23346 | 0 | -0.22888 | -0.20142 | -0.21057 | 0.086975 | 1.712 | -0.054931 | 0.15564 | -0.004578 | 122.8821 | 122.6486 | 55.1651 | -123.111 | 122.9645 | 122.8729 | 80.1727 | -123.0881
3195.0156 | 123.1293 | -51.4023 | 71.4935 | 0.022736 | 0.0087307 | 0.073377 | 0.073935 | 0.12736 | -0.0013587 | -0.0070773 | 0.09903 | -0.010408 | 0.062982 | 0.055903 | 0.00784 | -0.012614 | 70.8939 | 71.0632 | 2.8152 | -51.9745 | 71.2006 | -51.8875 | -51.9974 | -49.7726 | 28.5324 | -51.3107 | 71.521 | 71.3654 | -51.6586 | -51.6907 | -0.48523 | -0.59509 | -0.29297 | 122.4655 | -0.5722 | 0.022888 | -0.59967 | -0.25635 | -0.28839 | 0.027466 | 1.6296 | 0.091553 | 0.37994 | -0.12817 | 122.6028 | 122.2961 | 54.2175 | -123.4909 | 122.9233 | 122.7676 | 79.9347 | -123.1842
3196.0156 | 123.143 | -50.6927 | 72.1939 | 0.12955 | 0.010653 | 0.070173 | 0.071585 | 0.12864 | -0.00050425 | -0.0094273 | 0.14481 | -0.010408 | 0.062769 | 0.05633 | 0.0074126 | -0.013683 | 71.8597 | 72.0474 | 2.9984 | -50.9491 | 72.1436 | -50.9125 | -50.9583 | -49.054 | 29.0176 | -50.6744 | 72.2351 | 72.1436 | -50.9216 | -50.9445 | -0.21973 | -0.2655 | -0.050354 | 122.7402 | -0.25635 | 0.009155 | -0.33417 | -0.22888 | -0.25177 | 0.041198 | 1.6388 | 0.018311 | 0.27008 | -0.050354 | 122.8363 | 122.5525 | 53.6911 | -123.1522 | 122.9279 | 122.8363 | 79.7104 | -123.1384
3197.0312 | 123.056 | -50.1205 | 72.7798 | -0.12222 | 0.018771 | 0.067182 | 0.076071 | 0.12886 | 0.0035547 | -0.0036595 | -0.17563 | -0.0078442 | 0.064264 | 0.057185 | 0.0099762 | -0.015605 | 72.7707 | 72.876 | 3.1998 | -50.1846 | 73.0545 | -50.1022 | -50.2213 | -48.4177 | 29.5212 | -50.235 | 72.9721 | 72.821 | -50.2991 | -50.3586 | 0.01831 | -0.10071 | 0.27466 | 122.9965 | -0.064087 | 0.036621 | -0.009155 | -0.17853 | -0.23804 | 0.19226 | 1.7029 | -0.11444 | 0.1236 | 0.041199 | 123.175 | 122.8912 | 53.3203 | -123.0011 | 123.0927 | 122.9416 | 79.6417 | -123.1384
3198.0156 | 123.1293 | -51.265 | 71.6354 | 0.19821 | 0.011722 | 0.067823 | 0.070731 | 0.12993 | 0.0037683 | -0.0032321 | 0.076141 | -0.011262 | 0.062982 | 0.056544 | 0.011044 | -0.01411 | 71.3333 | 71.8964 | 3.1906 | -51.4343 | 71.6904 | -51.3565 | -51.4618 | -49.5438 | 28.7567 | -51.329 | 71.6904 | 71.5897 | -51.4526 | -51.5167 | -0.091552 | -0.19684 | 0.054932 | 123.1613 | -0.16937 | 0.027466 | -0.30212 | -0.18768 | -0.25177 | 0.054932 | 1.7212 | -0.064087 | 0.18768 | -0.045776 | 122.9553 | 122.5983 | 54.4556 | -123.0972 | 122.9553 | 122.8546 | 80.0217 | -123.1522
3199.0156 | 123.1338 | -51.8829 | 71.0175 | 0.060882 | 0.0097989 | 0.069959 | 0.069663 | 0.12779 | -0.0032813 | -0.0064365 | -0.168 | -0.011903 | 0.062128 | 0.056117 | 0.0080536 | -0.010265 | 70.7474 | 71.1411 | 2.8702 | -52.1484 | 71.0495 | -52.034 | -52.1072 | -50.2258 | 28.0792 | -51.9012 | 71.0724 | 70.9579 | -52.0844 | -52.1393 | -0.15106 | -0.2243 | 0.032044 | 123.024 | -0.2655 | -0.041198 | -0.27008 | -0.20142 | -0.25635 | 0.054932 | 1.6571 | -0.01831 | 0.23804 | -0.059509 | 122.9324 | 122.6303 | 54.7531 | -123.1247 | 122.9553 | 122.8409 | 79.9622 | -123.1567
3200.0156 | 123.111 | -51.0773 | 71.7499 | 0.099029 | 0.01279 | 0.068678 | 0.071158 | 0.12843 | -0.00050425 | -0.0064365 | 0.16769 | -0.010621 | 0.064478 | 0.057185 | 0.0097626 | -0.01411 | 71.7087 | 71.8826 | 3.3051 | -51.2192 | 71.9101 | -51.1414 | -51.2283 | -49.3652 | 28.7979 | -51.0178 | 71.8872 | 71.7682 | -51.2878 | -51.3153 | -0.064086 | -0.15106 | 0.16022 | 122.9599 | -0.14191 | 0.009156 | -0.041199 | -0.21057 | -0.23804 | 0.13733 | 1.712 | 0.05951 | 0.29755 | 0.01831 | 122.9874 | 122.786 | 54.3823 | -122.9782 | 122.9645 | 122.8455 | 79.8752 | -123.0652
3201.0156 | 123.1293 | -50.8392 | 72.02 | 0.068512 | 0.01044 | 0.071027 | 0.071372 | 0.12736 | -0.0017859 | -0.0072911 | 0.045624 | -0.010194 | 0.062555 | 0.055689 | 0.0059174 | -0.011974 | 71.9009 | 72.0886 | 3.5019 | -51.0086 | 72.1619 | -50.8804 | -50.9995 | -49.2096 | 28.8986 | -50.972 | 72.139 | 72.0383 | -51.059 | -51.0818 | -0.041199 | -0.16022 | 0.14191 | 122.9279 | -0.16937 | -0.009155 | -0.11902 | -0.21973 | -0.24262 | 0.11902 | 1.6296 | -0.13275 | 0.10986 | 0.018311 | 123.0011 | 122.7402 | 54.3411 | -123.0194 | 122.9782 | 122.8775 | 79.7379 | -123.1018
3202.0156 | 123.143 | -50.1663 | 72.6746 | -0.03067 | 0.0093717 | 0.070814 | 0.070517 | 0.12736 | -0.0017859 | -0.0070773 | -0.084076 | -0.012971 | 0.062342 | 0.054194 | 0.008908 | -0.012828 | 72.3953 | 72.6196 | 3.772 | -50.4639 | 72.6562 | -50.4089 | -50.4868 | -48.4909 | 29.425 | -50.1846 | 72.7707 | 72.6654 | -50.3952 | -50.4364 | -0.24261 | -0.32043 | -0.018311 | 122.786 | -0.29755 | 0.022888 | -0.27924 | -0.22888 | -0.27008 | 0.09613 | 1.6754 | -0.01831 | 0.25177 | -0.009156 | 122.8226 | 122.5616 | 53.9383 | -123.1613 | 122.937 | 122.8317 | 79.5914 | -123.111
3203.0156 | 123.1155 | -51.416 | 71.4661 | 0.030365 | 0.010653 | 0.072523 | 0.069663 | 0.128 | 0.00013675 | -0.0070773 | 0.54153 | -0.011476 | 0.06341 | 0.055903 | 0.0084808 | -0.013896 | 71.3425 | 71.553 | 3.6621 | -51.5762 | 71.6446 | -51.4435 | -51.5579 | -49.7589 | 28.624 | -51.4664 | 71.5439 | 71.4249 | -51.6541 | -51.6769 | -0.027465 | -0.14191 | 0.17853 | 122.9691 | -0.16022 | -0.018311 | -0.1236 | -0.23804 | -0.26093 | 0.07782 | 1.6571 | -0.050354 | 0.21057 | -0.041198 | 123.0606 | 122.7585 | 55.0781 | -123.024 | 122.9599 | 122.8409 | 80.04 | -123.143
3204.0156 | 123.1476 | -51.4755 | 71.3516 | 0.18295 | 0.014712 | 0.069105 | 0.070731 | 0.12864 | 0.0031273 | -0.0053683 | 0.16769 | -0.011476 | 0.062982 | 0.053767 | 0.01019 | -0.01411 | 71.1731 | 71.3013 | 3.6667 | -51.7548 | 71.3699 | -51.6632 | -51.828 | -49.855 | 28.6057 | -51.5488 | 71.4066 | 71.3196 | -51.7181 | -51.7456 | -0.18768 | -0.35248 | 0.01831 | 122.7768 | -0.27924 | 0.073242 | -0.17853 | -0.24262 | -0.27008 | 0.054931 | 1.6205 | -0.073242 | 0.19684 | -0.032044 | 122.8455 | 122.6486 | 55.1422 | -123.1796 | 122.8821 | 122.7951 | 80.0812 | -123.0972
3205.0156 | 123.111 | -50.4272 | 72.4274 | 0.11429 | 0.011081 | 0.067823 | 0.071799 | 0.12758 | 0.0016321 | -0.0066501 | 0.21347 | -0.0093396 | 0.062555 | 0.054835 | 0.0097626 | -0.012828 | 72.3679 | 72.5601 | 4.0878 | -50.5417 | 72.5922 | -50.4364 | -50.5325 | -48.848 | 29.393 | -50.6149 | 72.4915 | 72.4045 | -50.6561 | -50.7065 | -0.009155 | -0.10529 | 0.16479 | 122.9874 | -0.11444 | -0.009155 | -0.059509 | -0.22888 | -0.27924 | 0.064087 | 1.5793 | -0.18768 | 0.091553 | -0.022888 | 123.0194 | 122.7951 | 54.5151 | -122.9599 | 122.9187 | 122.8317 | 79.8203 | -123.1338
3206.0156 | 123.1613 | -50.5692 | 72.2992 | 0.16769 | 0.014926 | 0.068037 | 0.073081 | 0.13078 | 0.0033411 | -0.0068637 | 0.19058 | -0.011903 | 0.0664 | 0.056117 | 0.014249 | -0.011974 | 72.1069 | 72.2305 | 3.8589 | -50.8301 | 72.2763 | -50.7843 | -50.8896 | -49.1547 | 29.425 | -50.647 | 72.2763 | 72.171 | -50.853 | -50.853 | -0.21515 | -0.32043 | -0.022888 | 122.7997 | -0.26093 | 0.059509 | -0.19226 | -0.28381 | -0.28381 | -0.022888 | 1.4145 | -0.07782 | 0.20599 | -0.12817 | 122.8455 | 122.6761 | 54.4281 | -123.1888 | 122.8455 | 122.7402 | 79.9942 | -123.1522
3207.0156 | 123.056 | -50.2762 | 72.6974 | -0.22141 | 0.013003 | 0.072096 | 0.072867 | 0.12928 | -0.00029045 | -0.0062229 | -0.19089 | -0.0095532 | 0.063623 | 0.056117 | 0.008908 | -0.012401 | 72.5647 | 72.7524 | 3.9551 | -50.322 | 72.8714 | -50.2579 | -50.3586 | -48.793 | 29.5578 | -50.5783 | 72.6608 | 72.5464 | -50.56 | -50.5692 | 0.01831 | -0.082398 | 0.17395 | 123.0286 | -0.045776 | 0.036622 | -0.13275 | -0.28381 | -0.29297 | -0.036621 | 1.4832 | -0.30212 | -0.009155 | -0.15106 | 123.1476 | 122.8409 | 54.2313 | -123.056 | 122.937 | 122.8226 | 79.834 | -123.2666
3208.0156 | 123.1613 | -50.56 | 72.2763 | 0.22873 | 0.016421 | 0.069746 | 0.072226 | 0.12864 | 0.0027001 | -0.0055821 | 0.14481 | -0.0093396 | 0.0664 | 0.055689 | 0.012326 | -0.013469 | 72.171 | 72.3038 | 3.6713 | -50.7568 | 72.4365 | -50.6287 | -50.7614 | -48.8892 | 29.3518 | -50.6607 | 72.3953 | 72.2626 | -50.798 | -50.8438 | -0.068664 | -0.20142 | 0.16022 | 122.8638 | -0.19684 | 0.004578 | -0.10529 | -0.23804 | -0.28381 | 0.11902 | 1.6708 | -0.10071 | 0.18311 | -0.013733 | 122.9965 | 122.731 | 54.2313 | -123.0377 | 122.9553 | 122.8226 | 79.9118 | -123.1201
3209.0156 | 123.1384 | -51.0773 | 71.7682 | 0.31265 | 0.015994 | 0.072096 | 0.066672 | 0.12822 | 0.0012047 | -0.0062229 | 0.20584 | -0.010835 | 0.061914 | 0.055476 | 0.0091216 | -0.011333 | 71.6721 | 71.8552 | 3.8818 | -51.2421 | 71.8826 | -51.1459 | -51.2604 | -49.324 | 29.0359 | -51.0452 | 71.9101 | 71.8048 | -51.2421 | -51.3107 | -0.068664 | -0.1831 | 0.11444 | 122.9324 | -0.16479 | 0.018311 | -0.09613 | -0.16479 | -0.23346 | 0.14191 | 1.7532 | 0.032044 | 0.2655 | 0.036622 | 122.9599 | 122.7493 | 54.9591 | -123.0286 | 122.9874 | 122.8821 | 80.1132 | -123.0789
3210.0156 | 123.1064 | -51.1963 | 71.6995 | 0.15244 | 0.017276 | 0.069959 | 0.073081 | 0.12758 | 0.0033411 | -0.0047275 | 0.16769 | -0.0095532 | 0.067896 | 0.056758 | 0.011472 | -0.013896 | 71.5164 | 71.6263 | 3.6896 | -51.4069 | 71.8185 | -51.2924 | -51.3931 | -49.5438 | 28.7659 | -51.4618 | 71.7499 | 71.6309 | -51.4893 | -51.4709 | -0.09613 | -0.19684 | 0.11902 | 122.8226 | -0.21057 | -0.013733 | -0.18311 | -0.29297 | -0.27466 | 0.050354 | 1.6525 | -0.2655 | 0.009155 | -0.068665 | 123.0148 | 122.7127 | 54.8859 | -123.0927 | 122.9462 | 122.8271 | 79.9622 | -123.1705
3211.0156 | 123.1201 | -51.4343 | 71.4249 | 0.16006 | 0.01044 | 0.068464 | 0.069876 | 0.12736 | -0.0028541 | -0.0053683 | 0.20584 | -0.012117 | 0.063196 | 0.055049 | 0.0084808 | -0.013255 | 71.3745 | 71.5576 | 3.7125 | -51.5442 | 71.5759 | -51.4755 | -51.5625 | -49.736 | 28.6697 | -51.5671 | 71.521 | 71.4523 | -51.6586 | -51.6953 | -0.041199 | -0.12817 | 0.15106 | 122.9919 | -0.10986 | 0.018311 | -0.050354 | -0.2243 | -0.26093 | 0.09613 | 1.6983 | -0.13275 | 0.12817 | 0.027466 | 123.0103 | 122.8088 | 55.1468 | -122.9874 | 122.9553 | 122.8867 | 80.1041 | -123.1201
3212.0156 | 123.0927 | -52.272 | 70.6421 | -0.21378 | 0.015353 | 0.072309 | 0.074576 | 0.13121 | 0.0022729 | -0.0075047 | -0.19852 | -0.0072034 | 0.062982 | 0.055903 | 0.010617 | -0.014964 | 70.4178 | 70.5185 | 3.5477 | -52.5284 | 70.7382 | -52.4368 | -52.5192 | -50.7477 | 27.8275 | -52.4872 | 70.6512 | 70.546 | -52.5925 | -52.5742 | -0.1648 | -0.24719 | 0.09613 | 122.7905 | -0.25635 | -0.009155 | -0.2243 | -0.32043 | -0.30212 | 0.009155 | 1.5244 | -0.21515 | 0.086975 | -0.096131 | 123.0103 | 122.6898 | 55.8197 | -123.1613 | 122.9233 | 122.818 | 80.0995 | -123.2162
3213.0156 | 123.1522 | -50.9674 | 71.8826 | 0.16006 | 0.01578 | 0.066755 | 0.065176 | 0.12993 | -0.0037085 | -0.0075047 | 0.32791 | -0.011476 | 0.063196 | 0.058039 | 0.008908 | -0.011119 | 71.9833 | 71.9193 | 3.8589 | -51.0452 | 72.0428 | -51.0132 | -51.0864 | -49.2096 | 29.1367 | -51.0635 | 72.0154 | 71.9101 | -51.1734 | -51.2054 | -0.045777 | -0.11902 | 0.16022 | 122.8867 | -0.07782 | 0.041199 | 0.10071 | -0.20599 | -0.23804 | 0.13275 | 1.7578 | -0.096131 | 0.14191 | 0.027466 | 123.0103 | 122.9507 | 54.8264 | -122.9691 | 122.9828 | 122.8775 | 80.1041 | -123.0881
3214.0156 | 123.0469 | -50.1068 | 72.7203 | 0.076141 | 0.016421 | 0.068037 | 0.073294 | 0.12758 | 0.0048363 | -0.0062229 | 0.16006 | -0.0089124 | 0.065973 | 0.05868 | 0.0099762 | -0.013255 | 72.6379 | 72.7432 | 3.9047 | -50.2716 | 72.9996 | -50.1801 | -50.2625 | -48.3902 | 29.7775 | -50.1389 | 72.9996 | 72.8989 | -50.2487 | -50.2853 | -0.073242 | -0.15564 | 0.27924 | 122.85 | -0.16479 | -0.009155 | -0.082398 | -0.14191 | -0.17853 | 0.27924 | 1.7166 | -0.032043 | 0.14648 | 0.17853 | 123.1064 | 122.7448 | 54.0115 | -122.9828 | 123.1064 | 123.0057 | 79.8843 | -123.0057
3215.0156 | 123.1522 | -50.2625 | 72.5601 | 0.16769 | 0.014926 | 0.069319 | 0.069876 | 0.13014 | -0.0013587 | -0.0053683 | 0.18295 | -0.0089124 | 0.063196 | 0.05868 | 0.0091216 | -0.013683 | 72.4686 | 72.5876 | 3.9139 | -50.4593 | 72.6929 | -50.4135 | -50.4822 | -48.5825 | 29.6814 | -50.2853 | 72.6608 | 72.5784 | -50.5096 | -50.5417 | -0.15106 | -0.21973 | 0.13275 | 122.85 | -0.19684 | 0.022888 | -0.091553 | -0.24719 | -0.27924 | 0.10071 | 1.68 | -0.022888 | 0.25635 | 0.01831 | 122.9553 | 122.731 | 54.1763 | -123.0423 | 122.9233 | 122.8409 | 79.9438 | -123.1018
3216.0156 | 123.0057 | -52.0889 | 70.8344 | 0.12955 | 0.019198 | 0.068891 | 0.074149 | 0.128 | 0.0035547 | -0.0055821 | 3.1584 | -0.0089124 | 0.062982 | 0.057185 | 0.0069854 | -0.011546 | 70.6192 | 70.7016 | 3.0899 | -52.2995 | 70.9488 | -52.2034 | -52.2858 | -50.5096 | 28.1113 | -52.1667 | 70.9625 | 70.8801 | -52.2949 | -52.3224 | -0.11444 | -0.19684 | 0.11444 | 122.7905 | -0.21057 | -0.013733 | -0.21515 | -0.20599 | -0.23346 | 0.12817 | 1.5793 | -0.07782 | 0.15564 | 0.045776 | 123.0377 | 122.7081 | 55.1788 | -123.1201 | 123.0515 | 122.9691 | 80.2002 | -123.1567
3217.0156 | 123.1705 | -51.8143 | 70.9671 | 0.32791 | 0.014926 | 0.069532 | 0.069449 | 0.12928 | 0.00056395 | -0.0049411 | 0.23636 | -0.0097668 | 0.066187 | 0.054835 | 0.008908 | -0.010265 | 71.0953 | 71.2234 | 3.1403 | -51.8234 | 71.2875 | -51.7593 | -51.8509 | -49.9329 | 28.2211 | -51.8921 | 71.2143 | 71.1273 | -51.9791 | -52.0111 | 0.054932 | -0.036621 | 0.32044 | 123.0377 | -0.009155 | 0.027466 | 0.12817 | -0.16479 | -0.19684 | 0.24719 | 1.8814 | -0.07782 | 0.11902 | 0.16022 | 123.1018 | 122.9095 | 54.9545 | -122.818 | 123.0286 | 122.9416 | 80.0354 | -122.9782
3218.0156 | 123.0103 | -50.5234 | 72.4136 | 0.030365 | 0.020053 | 0.070173 | 0.072653 | 0.12715 | 0.0029137 | -0.0060093 | 0.076141 | -0.0089124 | 0.067468 | 0.056544 | 0.011258 | -0.011974 | 72.139 | 72.2763 | 3.1403 | -50.7385 | 72.4777 | -50.6241 | -50.7248 | -48.8937 | 29.3335 | -50.5737 | 72.5143 | 72.4136 | -50.7614 | -50.7935 | -0.10071 | -0.20142 | 0.064087 | 122.7997 | -0.21515 | -0.013733 | -0.27466 | -0.23804 | -0.27008 | 0.10071 | 1.6296 | -0.050354 | 0.21973 | 0 | 123.0011 | 122.6624 | 53.6636 | -123.1384 | 123.0377 | 122.937 | 79.8569 | -123.2071
3219.0156 | 123.1476 | -50.7614 | 72.1115 | 0.18295 | 0.016849 | 0.072309 | 0.072012 | 0.12758 | -7.6852e-05 | -0.0060093 | 0.25162 | -0.0099806 | 0.064691 | 0.056758 | 0.0074126 | -0.011119 | 71.8185 | 71.9559 | 3.2593 | -51.0727 | 72.1024 | -50.9811 | -51.0864 | -49.1135 | 29.1183 | -51.059 | 72.1527 | 72.0703 | -51.0132 | -51.0361 | -0.21973 | -0.32501 | -0.009155 | 122.7173 | -0.31128 | 0.013733 | -0.29297 | -0.25177 | -0.27466 | 0.041199 | 1.648 | -0.29755 | -0.022888 | -0.041199 | 122.8638 | 122.58 | 54.0207 | -123.1979 | 122.9141 | 122.8317 | 79.8798 | -123.1476
3220.0156 | 123.0194 | -50.3632 | 72.5876 | 0.060882 | 0.017703 | 0.070387 | 0.072012 | 0.12608 | 0.0041955 | -0.0038731 | 0.12955 | -0.0086988 | 0.067255 | 0.056544 | 0.01019 | -0.012828 | 72.3038 | 72.3862 | 3.1723 | -50.5692 | 72.6791 | -50.4501 | -50.56 | -48.7198 | 29.5166 | -50.4868 | 72.7203 | 72.6334 | -50.528 | -50.5783 | -0.086975 | -0.19684 | 0.091553 | 122.7493 | -0.20599 | -0.009155 | -0.28381 | -0.16479 | -0.21515 | 0.13275 | 1.6434 | -0.1236 | 0.091553 | 0.045777 | 123.0423 | 122.6669 | 53.5355 | -123.1476 | 123.0835 | 122.9965 | 79.8798 | -123.1659
3221.0156 | 123.1155 | -50.9354 | 71.9833 | 0.11429 | 0.01578 | 0.069319 | 0.069022 | 0.12693 | -0.00050425 | -0.0053683 | 0.21347 | -0.0084852 | 0.064691 | 0.057398 | 0.0082672 | -0.011333 | 71.8231 | 71.9421 | 3.1677 | -51.0864 | 72.139 | -50.972 | -51.1047 | -49.2279 | 28.8483 | -51.0361 | 72.084 | 72.0154 | -51.1688 | -51.1826 | -0.036621 | -0.16937 | 0.15564 | 122.8775 | -0.15106 | 0.01831 | -0.16022 | -0.23346 | -0.24719 | 0.10071 | 1.7075 | -0.10071 | 0.14648 | 0.032044 | 123.0743 | 122.7585 | 54.1031 | -123.0881 | 123.0194 | 122.9507 | 79.7836 | -123.1659
3222.0156 | 123.0515 | -49.8047 | 73.1369 | -0.015411 | 0.01813 | 0.069959 | 0.073508 | 0.128 | 0.0027001 | -0.0062229 | 0.030365 | -0.010194 | 0.065119 | 0.055689 | 0.0097626 | -0.012187 | 72.8394 | 72.963 | 3.5248 | -50.0885 | 73.1689 | -49.9741 | -50.0748 | -48.1613 | 29.7546 | -49.8596 | 73.2239 | 73.1735 | -49.9969 | -50.0519 | -0.16937 | -0.27008 | 0.032043 | 122.7676 | -0.28381 | -0.013733 | -0.29755 | -0.19226 | -0.24719 | 0.086975 | 1.6434 | -0.054932 | 0.19226 | 0.036621 | 122.9736 | 122.644 | 53.3295 | -123.2117 | 123.0286 | 122.9782 | 79.5593 | -123.1888
3223.0156 | 123.0606 | -50.4776 | 72.4319 | 0.11429 | 0.014499 | 0.069532 | 0.075003 | 0.12736 | 0.0024865 | -0.0051547 | 0.16006 | -0.0093396 | 0.065546 | 0.055476 | 0.0099762 | -0.012614 | 72.0612 | 72.4594 | 3.2959 | -50.6699 | 72.5922 | -50.5554 | -50.6653 | -48.8113 | 29.2328 | -50.6058 | 72.5693 | 72.4503 | -50.6882 | -50.7294 | -0.07782 | -0.18768 | 0.16022 | 122.937 | -0.19226 | -0.004578 | -0.37079 | -0.21057 | -0.25177 | 0.13733 | 1.6663 | -0.12817 | 0.1236 | 0.01831 | 123.0698 | 122.5388 | 53.7735 | -123.0972 | 123.0469 | 122.9279 | 79.7104 | -123.1613
3224.0156 | 123.0515 | -50.647 | 72.2992 | -0.076447 | 0.016208 | 0.072523 | 0.072653 | 0.12736 | 0.00077755 | -0.0064365 | 0.0074766 | -0.010621 | 0.067041 | 0.05633 | 0.01019 | -0.012401 | 72.0291 | 72.1252 | 3.7994 | -50.8896 | 72.2809 | -50.7843 | -50.9171 | -48.9807 | 29.1412 | -50.8484 | 72.3633 | 72.3084 | -50.8759 | -50.8987 | -0.13733 | -0.27008 | -0.01831 | 122.7722 | -0.24261 | 0.027466 | -0.27008 | -0.22888 | -0.25177 | 0.064087 | 1.6663 | -0.20142 | 0.050354 | 0.009156 | 122.9279 | 122.6761 | 54.4464 | -123.2162 | 123.0103 | 122.9553 | 79.7882 | -123.1979
3225.0156 | 123.0423 | -50.4456 | 72.4823 | 0.32791 | 0.015353 | 0.070173 | 0.071158 | 0.128 | 0.0018457 | -0.0068637 | 0.20584 | -0.0069898 | 0.064905 | 0.057398 | 0.011044 | -0.012187 | 72.1619 | 72.2534 | 3.9459 | -50.7294 | 72.496 | -50.6241 | -50.7477 | -48.7473 | 29.3198 | -50.56 | 72.5876 | 72.5006 | -50.647 | -50.6653 | -0.17853 | -0.30212 | 0.013733 | 122.699 | -0.28381 | 0.018311 | -0.32043 | -0.20142 | -0.21973 | 0.10529 | 1.6983 | -0.11444 | 0.10529 | 0.01831 | 122.9416 | 122.6074 | 54.3915 | -123.23 | 123.0331 | 122.9462 | 79.7653 | -123.1476
3226.0156 | 123.0423 | -49.6216 | 73.2513 | -0.0383 | 0.018771 | 0.070387 | 0.072653 | 0.1295 | 0.00056395 | -0.0053683 | 0.053253 | -0.010194 | 0.0664 | 0.058039 | 0.0086944 | -0.012401 | 73.1003 | 73.1323 | 4.1519 | -49.9191 | 73.3566 | -49.7726 | -49.8734 | -47.937 | 30.0613 | -49.7086 | 73.4207 | 73.3658 | -49.823 | -49.8642 | -0.15106 | -0.25177 | 0.10528 | 122.7539 | -0.29755 | -0.045776 | -0.15106 | -0.20142 | -0.24262 | 0.16937 | 1.6846 | -0.086975 | 0.15564 | 0.11444 | 122.9782 | 122.7219 | 53.7735 | -123.1247 | 123.0423 | 122.9874 | 79.6829 | -123.1155
3227.0156 | 123.0469 | -51.5671 | 71.3608 | 0.12192 | 0.02048 | 0.070173 | 0.071799 | 0.12928 | 0.0037683 | -0.0053683 | 0.15244 | -0.010408 | 0.0664 | 0.057185 | 0.016171 | -0.012187 | 71.0724 | 71.1639 | 3.5385 | -51.8097 | 71.4569 | -51.709 | -51.796 | -50.0793 | 28.9444 | -51.5717 | 71.434 | 71.402 | -51.7776 | -51.8234 | -0.14191 | -0.22888 | 0.09613 | 122.731 | -0.24261 | -0.013733 | -0.28839 | -0.21057 | -0.25635 | 0.073242 | 1.4877 | -0.004577 | 0.25177 | 0.041199 | 123.024 | 122.6395 | 55.1056 | -123.1567 | 123.0011 | 122.9691 | 80.5115 | -123.1842
3228.0156 | 123.1064 | -50.2625 | 72.6288 | 0.18295 | 0.01813 | 0.069746 | 0.070944 | 0.12843 | -0.00093145 | -0.0085727 | 0.23636 | -0.0084852 | 0.063196 | 0.05633 | 0.008908 | -0.010692 | 72.4594 | 72.5647 | 4.1519 | -50.4547 | 72.7524 | -50.3448 | -50.4456 | -48.5596 | 29.8279 | -50.3357 | 72.7203 | 72.6562 | -50.4959 | -50.4959 | -0.082398 | -0.18311 | 0.1236 | 122.8271 | -0.19226 | -0.009155 | -0.16937 | -0.23346 | -0.23346 | 0.091553 | 1.7029 | -0.073242 | 0.16022 | 0.027466 | 123.0148 | 122.7219 | 54.4144 | -123.0743 | 122.9828 | 122.9187 | 80.0903 | -123.1247
3229.0156 | 123.024 | -50.8072 | 72.1344 | -0.0077822 | 0.016849 | 0.06761 | 0.073508 | 0.13057 | 0.0014185 | -0.0066501 | 0.045624 | -0.0093396 | 0.067896 | 0.057826 | 0.0097626 | -0.013683 | 72.6746 | 72.8119 | 4.2435 | -50.2075 | 72.9858 | -50.1251 | -50.2304 | -48.8388 | 29.155 | -51.3474 | 72.5372 | 72.3633 | -50.8987 | -51.0086 | 0.68207 | 0.57678 | 0.85144 | 123.6191 | 0.59967 | 0.022888 | 0.54016 | -0.091553 | -0.20142 | 0.40283 | 1.9684 | -0.54016 | -0.33875 | 0.22888 | 123.793 | 123.4818 | 55.0507 | -122.3648 | 123.3444 | 123.1705 | 79.9622 | -123.143
3230.0156 | 123.0789 | -48.9624 | 73.9655 | -0.16037 | 0.017489 | 0.070387 | 0.072653 | 0.12928 | -0.00093145 | -0.0066501 | -0.068817 | -0.0086988 | 0.065546 | 0.055049 | 0.01019 | -0.012187 | 73.8419 | 73.9563 | 4.8111 | -49.0906 | 74.1165 | -49.0082 | -49.1135 | -47.2504 | 30.8166 | -49.1135 | 74.0753 | 73.9929 | -49.1913 | -49.2233 | -0.045777 | -0.15106 | 0.15106 | 122.9187 | -0.12817 | 0.022888 | -0.1236 | -0.22888 | -0.26093 | 0.10986 | 1.712 | -0.15106 | 0.10986 | 0.027466 | 123.0789 | 122.8043 | 53.7735 | -123.0789 | 123.0377 | 122.9553 | 79.7791 | -123.1888
3231.0156 | 123.0652 | -49.6445 | 73.3154 | -0.03067 | 0.019198 | 0.069746 | 0.072653 | 0.12864 | 0.0022729 | -0.0072911 | 0.060883 | -0.0086988 | 0.067468 | 0.058467 | 0.010831 | -0.012828 | 73.1461 | 73.2925 | 4.5227 | -49.7314 | 73.4573 | -49.649 | -49.7818 | -47.8592 | 30.336 | -49.5758 | 73.4756 | 73.3978 | -49.8001 | -49.8322 | -0.004578 | -0.13733 | 0.14191 | 122.937 | -0.086975 | 0.050354 | -0.16937 | -0.15564 | -0.18768 | 0.16022 | 1.7853 | 0.068664 | 0.25635 | 0.082397 | 123.1018 | 122.7905 | 54.1672 | -123.0972 | 123.1201 | 123.0423 | 79.9805 | -123.1476
3232.0156 | 123.0698 | -49.205 | 73.7274 | -0.20615 | 0.015353 | 0.071668 | 0.07244 | 0.12758 | 0.0014185 | -0.0089999 | -0.12985 | -0.010408 | 0.066828 | 0.056117 | 0.0082672 | -0.010692 | 73.5489 | 73.6862 | 4.9118 | -49.3149 | 73.9105 | -49.2142 | -49.3286 | -47.4472 | 30.7526 | -49.2416 | 73.9197 | 73.8144 | -49.3652 | -49.4293 | -0.009155 | -0.1236 | 0.1831 | 122.8912 | -0.10986 | 0.013733 | -0.17853 | -0.16022 | -0.2243 | 0.19226 | 1.7578 | -0.036621 | 0.18768 | 0.086975 | 123.1155 | 122.7539 | 54.1168 | -123.056 | 123.1247 | 123.0194 | 79.9576 | -123.1567
3233.0156 | 123.0698 | -51.9424 | 71.0037 | -0.045929 | 0.018558 | 0.070387 | 0.073081 | 0.12629 | 0.0014185 | -0.0062229 | 0.09903 | -0.0089124 | 0.066187 | 0.057398 | 0.0074126 | -0.010478 | 70.8572 | 70.9808 | 4.6326 | -52.0294 | 71.1868 | -51.9424 | -52.0477 | -50.1709 | 28.4729 | -52.1118 | 71.1456 | 71.0541 | -52.1484 | -52.1667 | 0 | -0.10528 | 0.18311 | 122.9233 | -0.086975 | 0.01831 | -0.14648 | -0.20599 | -0.2243 | 0.14191 | 1.7715 | -0.16937 | 0.054932 | 0.050354 | 123.1293 | 122.7997 | 56.575 | -123.0515 | 123.0881 | 122.9965 | 80.4153 | -123.1705
3234.0156 | 123.0789 | -50.853 | 72.1024 | -0.18326 | 0.014285 | 0.069532 | 0.071585 | 0.13142 | -0.00071785 | -0.010068 | -0.15274 | -0.0093396 | 0.065119 | 0.056117 | 0.0084808 | -0.013896 | 71.9467 | 72.1252 | 7.2968 | -50.8804 | 72.3175 | -50.8347 | -50.9537 | -49.0814 | 29.3472 | -50.9079 | 72.2397 | 72.1619 | -51.0361 | -51.0727 | 0.01831 | -0.10071 | 0.21515 | 122.9782 | -0.027466 | 0.073242 | -0.15564 | -0.18311 | -0.21973 | 0.13733 | 1.7715 | -0.054932 | 0.16479 | 0.059509 | 123.1705 | 122.7997 | 58.1497 | -123.056 | 123.0927 | 123.0148 | 80.2002 | -123.175
3235.0156 | 123.0698 | -52.3453 | 70.5872 | -0.099335 | 0.016849 | 0.071027 | 0.075644 | 0.12971 | 0.0012047 | -0.0047275 | -0.00015237 | -0.009126 | 0.067255 | 0.057185 | 0.0074126 | -0.012401 | 70.34 | 70.7108 | 7.2739 | -52.478 | 70.7291 | -52.3819 | -52.4734 | -50.6149 | 28.0518 | -52.478 | 70.665 | 70.6146 | -52.5925 | -52.6108 | -0.036621 | -0.12817 | 0.14191 | 123.056 | -0.13275 | -0.004577 | -0.24719 | -0.24719 | -0.2655 | 0.07782 | 1.7303 | -0.13275 | 0.13275 | 0.027466 | 123.0743 | 122.6852 | 59.6191 | -123.0606 | 123.0103 | 122.9599 | 80.397 | -123.1979
3236.0156 | 123.0698 | -51.4481 | 71.5256 | -0.015411 | 0.01279 | 0.071668 | 0.073935 | 0.12907 | -0.0026405 | -0.0081455 | -0.084076 | -0.0093396 | 0.0664 | 0.057826 | 0.008908 | -0.012614 | 71.3516 | 71.4981 | 5.6488 | -51.535 | 71.6858 | -51.4435 | -51.5213 | -49.8459 | 28.656 | -51.6312 | 71.5759 | 71.5073 | -51.6769 | -51.7136 | 0.004578 | -0.073242 | 0.16022 | 122.9462 | -0.086975 | -0.013733 | -0.17395 | -0.22888 | -0.2655 | 0.050354 | 1.6022 | -0.18311 | 0.082397 | -0.018311 | 123.1338 | 122.7997 | 57.0969 | -123.0469 | 123.024 | 122.9553 | 80.1041 | -123.2391
3237.0156 | 123.0469 | -53.6591 | 69.2734 | 0.43472 | 0.017276 | 0.069319 | 0.072867 | 0.13142 | 0.00056395 | -0.0057957 | -0.038299 | -0.0089124 | 0.0664 | 0.056544 | 0.010403 | -0.013255 | 69.1589 | 69.2734 | 5.8777 | -53.7552 | 69.4199 | -53.6819 | -53.7827 | -51.9012 | 26.9073 | -53.7781 | 69.3741 | 69.31 | -53.8788 | -53.8788 | -0.022888 | -0.1236 | 0.14648 | 122.9324 | -0.09613 | 0.027466 | -0.11444 | -0.21973 | -0.21973 | 0.10071 | 1.7578 | -0.11902 | 0.10071 | 0.036622 | 123.0789 | 122.818 | 59.5367 | -123.056 | 123.0331 | 122.9691 | 80.5664 | -123.1522
3238.0156 | 123.0423 | -51.0406 | 71.9147 | -0.22903 | 0.012362 | 0.071668 | 0.071158 | 0.13142 | -0.0047767 | -0.0072911 | -0.15274 | -0.0095532 | 0.064691 | 0.057398 | 0.006131 | -0.010478 | 71.6446 | 71.8185 | 5.6946 | -51.2192 | 72.02 | -51.1185 | -51.21 | -49.3515 | 29.2374 | -51.0086 | 72.0474 | 72.0108 | -51.21 | -51.2558 | -0.07782 | -0.16937 | 0.10529 | 122.8592 | -0.17853 | -0.009155 | -0.27008 | -0.16937 | -0.21515 | 0.13275 | 1.6891 | 0.032043 | 0.24719 | 0.09613 | 123.0606 | 122.6852 | 56.7352 | -123.1247 | 123.0881 | 123.0515 | 80.278 | -123.1705
3239.0156 | 123.0469 | -51.9516 | 71.0175 | -0.20615 | 0.014285 | 0.073164 | 0.075644 | 0.13099 | -0.0011451 | -0.0083591 | -0.29007 | -0.0086988 | 0.064905 | 0.057398 | 0.0069854 | -0.01176 | 70.7291 | 70.8527 | 4.5776 | -52.1347 | 71.1365 | -52.0248 | -52.1347 | -50.2579 | 28.5278 | -52.0844 | 71.0953 | 71.0312 | -52.1805 | -52.1942 | -0.073242 | -0.18311 | 0.11902 | 122.8043 | -0.18311 | 0 | -0.28839 | -0.22888 | -0.24262 | 0.07782 | 1.6937 | -0.13275 | 0.10986 | 0.013733 | 123.0881 | 122.6807 | 56.5292 | -123.1522 | 123.0469 | 122.9828 | 80.4794 | -123.2117
3240.0156 | 123.0515 | -50.2762 | 72.6791 | -0.23666 | 0.012362 | 0.069319 | 0.070517 | 0.12779 | -0.0062721 | -0.0085727 | -0.12985 | -0.011049 | 0.065119 | 0.057185 | 0.0084808 | -0.012828 | 72.3358 | 72.5281 | 4.39 | -50.5096 | 72.6562 | -50.4181 | -50.5554 | -48.7106 | 29.7318 | -50.3769 | 72.6471 | 72.6196 | -50.5188 | -50.5325 | -0.14191 | -0.27924 | -0.022888 | 122.8043 | -0.23346 | 0.045776 | -0.34332 | -0.24262 | -0.25635 | -0.032043 | 1.5656 | -0.10071 | 0.15564 | -0.059509 | 122.9324 | 122.612 | 54.6661 | -123.2346 | 122.9233 | 122.8958 | 80.0079 | -123.2117
3241.0156 | 123.0515 | -50.4044 | 72.5464 | -0.93094 | 0.01279 | 0.0706 | 0.072653 | 0.13099 | -0.00029045 | -0.0079319 | -0.12222 | -0.0093396 | 0.065973 | 0.056117 | 0.0069854 | -0.012187 | 72.1573 | 72.4136 | 4.4632 | -50.6195 | 72.583 | -50.5417 | -50.6104 | -48.7106 | 29.567 | -50.4822 | 72.6425 | 72.5693 | -50.6058 | -50.6516 | -0.13733 | -0.20599 | 0.036621 | 122.818 | -0.21515 | -0.009155 | -0.3891 | -0.20142 | -0.24719 | 0.09613 | 1.6937 | -0.07782 | 0.16937 | 0.022888 | 122.9874 | 122.5616 | 54.8676 | -123.1567 | 123.0469 | 122.9736 | 79.9713 | -123.1979
3242.0156 | 123.1293 | -52.1851 | 70.7108 | -0.10696 | 0.010226 | 0.070387 | 0.071585 | 0.12843 | -0.0052039 | -0.0077183 | -0.091705 | -0.011262 | 0.062982 | 0.057398 | 0.0059174 | -0.010905 | 70.5551 | 70.7932 | 4.6463 | -52.272 | 70.8252 | -52.2446 | -52.327 | -50.4364 | 28.1754 | -52.2949 | 70.7794 | 70.7245 | -52.4323 | -52.4323 | -0.059509 | -0.14191 | 0.11444 | 122.9782 | -0.086975 | 0.054931 | -0.15564 | -0.24719 | -0.24719 | 0.068665 | 1.7487 | -0.10986 | 0.13733 | 0.013733 | 123.0103 | 122.7402 | 56.8314 | -123.0377 | 122.9645 | 122.9095 | 80.3604 | -123.143
3243.0156 | 123.0469 | -49.9191 | 73.0637 | -0.35873 | 0.016208 | 0.069532 | 0.072653 | 0.12864 | 0.00099115 | -0.0068637 | -0.16037 | -0.009126 | 0.064051 | 0.057185 | 0.011044 | -0.012828 | 72.8989 | 73.0774 | 5.5252 | -49.9558 | 73.3017 | -49.8642 | -49.9786 | -48.1934 | 29.9744 | -50.1434 | 73.1003 | 73.0591 | -50.1114 | -50.1572 | 0.054931 | -0.05951 | 0.23804 | 122.9965 | -0.036622 | 0.022888 | -0.16479 | -0.19226 | -0.23804 | 0.036621 | 1.7258 | -0.22431 | 0.013733 | -0.004578 | 123.2208 | 122.818 | 55.4443 | -123.0423 | 123.0194 | 122.9782 | 79.8935 | -123.2208
3244.0156 | 123.0698 | -52.4643 | 70.4224 | -0.19852 | 0.010867 | 0.071455 | 0.071372 | 0.12758 | -0.0045631 | -0.0085727 | -0.11459 | -0.013826 | 0.064478 | 0.057185 | 0.0057038 | -0.012614 | 70.2393 | 70.459 | 5.0446 | -52.6657 | 70.4819 | -52.6062 | -52.7023 | -50.6882 | 32.872 | -52.565 | 70.4727 | 70.4041 | -52.7298 | -52.7344 | -0.14191 | -0.23804 | 0.05951 | 122.9233 | -0.20142 | 0.036622 | -0.1831 | -0.2655 | -0.27008 | 0.050354 | 1.7761 | -0.10071 | 0.16937 | -0.01831 | 122.9462 | 122.7036 | 57.5089 | -123.1247 | 122.937 | 122.8683 | 85.3363 | -123.1567
3245.0156 | 123.0606 | -50.6653 | 72.2992 | -0.23666 | 0.012362 | 0.072309 | 0.075644 | 0.13014 | -0.0013587 | -0.0079319 | -0.11459 | -0.0086988 | 0.062555 | 0.056971 | 0.0093354 | -0.010905 | 72.1252 | 72.3038 | 5.0537 | -50.7568 | 72.4457 | -50.679 | -50.7523 | -48.848 | 34.9136 | -50.7568 | 72.3862 | 72.3267 | -50.8484 | -50.9079 | -0.013733 | -0.086975 | 0.14648 | 122.9691 | -0.091553 | -0.004578 | -0.17395 | -0.18311 | -0.24262 | 0.086975 | 1.8173 | -0.091553 | 0.15106 | 0.027466 | 123.111 | 122.7905 | 55.719 | -123.0515 | 123.0515 | 122.9919 | 85.5789 | -123.2071
3246.0156 | 123.2117 | -50.2121 | 72.6746 | -0.076447 | 0.0091581 | 0.069746 | 0.071372 | 0.12822 | -0.0058447 | -0.0094273 | -0.0077819 | -0.010408 | 0.06341 | 0.056117 | 0.007199 | -0.012828 | 72.5418 | 72.7936 | 6.1798 | -50.3265 | 72.7844 | -50.2533 | -50.3769 | -48.3673 | 35.4904 | -50.2762 | 72.757 | 72.6562 | -50.4089 | -50.473 | -0.041199 | -0.16479 | 0.10986 | 123.0057 | -0.11444 | 0.050354 | -0.13275 | -0.19684 | -0.26093 | 0.082397 | 1.8448 | -0.064087 | 0.19684 | -0.018311 | 122.9965 | 122.7539 | 56.3919 | -123.0515 | 122.9691 | 122.8683 | 85.7025 | -123.1476
3247.0156 | 123.056 | -51.0498 | 71.8872 | -0.25192 | 0.011081 | 0.071241 | 0.070944 | 0.13249 | 0.0014185 | -0.0057957 | -0.12222 | -0.010194 | 0.063837 | 0.056544 | 0.0084808 | -0.014537 | 71.6766 | 71.7499 | 5.6076 | -51.21 | 72.02 | -51.1688 | -51.2146 | -49.2462 | 34.3918 | -51.2009 | 72.0291 | 71.9238 | -51.2421 | -51.2924 | -0.11902 | -0.16479 | 0.13275 | 122.7997 | -0.16022 | 0.004578 | -0.21057 | -0.19226 | -0.24261 | 0.14191 | 1.8036 | -0.15106 | 0.091552 | 0.036621 | 123.0698 | 122.7264 | 56.6574 | -123.1018 | 123.0789 | 122.9736 | 85.4416 | -123.1796
3248.0156 | 123.1796 | -50.9811 | 71.8964 | -0.12222 | 0.0074491 | 0.0706 | 0.072867 | 0.12736 | -0.0032813 | -0.0089999 | -0.084076 | -0.012117 | 0.064478 | 0.054621 | 0.007199 | -0.015392 | 71.8185 | 72.0657 | 5.8319 | -51.0773 | 72.0383 | -51.0315 | -51.1505 | -49.0585 | 34.9411 | -51.265 | 71.9467 | 71.8781 | -51.2329 | -51.2466 | -0.050354 | -0.16937 | 0.14191 | 123.0469 | -0.096131 | 0.073242 | -0.07782 | -0.25177 | -0.2655 | 0.050354 | 1.9226 | -0.28381 | -0.018311 | -0.01831 | 123.0194 | 122.7997 | 56.813 | -123.0469 | 122.9279 | 122.8592 | 85.9222 | -123.143
3249.0156 | 123.0743 | -51.3062 | 71.6309 | -0.22903 | 0.011508 | 0.070814 | 0.07009 | 0.12928 | -0.0011451 | -0.0087863 | -0.19089 | -0.011049 | 0.062342 | 0.058039 | 0.0063446 | -0.011546 | 71.5256 | 71.7453 | 4.9622 | -51.3519 | 71.8185 | -51.2878 | -51.3931 | -49.4888 | 34.7397 | -51.384 | 71.7453 | 71.6354 | -51.4893 | -51.5213 | 0.01831 | -0.086975 | 0.18768 | 123.0515 | -0.045777 | 0.041198 | -0.10528 | -0.18311 | -0.21515 | 0.11444 | 1.8173 | -0.07782 | 0.13733 | 0.004578 | 123.1247 | 122.8317 | 56.2683 | -123.024 | 123.0515 | 122.9416 | 86.0458 | -123.1522
3250.0156 | 123.1567 | -50.3174 | 72.5418 | -0.12222 | 0.0080899 | 0.071668 | 0.070944 | 0.12779 | -0.0041357 | -0.0070773 | -0.023041 | -0.013826 | 0.062769 | 0.05633 | 0.0063446 | -0.011974 | 72.4274 | 72.6746 | 5.4611 | -50.4547 | 72.67 | -50.4227 | -50.5234 | -48.4451 | 35.6552 | -50.2579 | 72.6105 | 72.5601 | -50.5142 | -50.5646 | -0.10529 | -0.20599 | 0.12817 | 122.9919 | -0.13733 | 0.068664 | -0.11444 | -0.19684 | -0.24719 | 0.068665 | 1.8723 | 0.059509 | 0.3067 | 0.018311 | 122.9874 | 122.7448 | 55.7785 | -123.0652 | 122.9279 | 122.8775 | 85.9726 | -123.1064
3251.0156 | 123.0194 | -50.0793 | 72.9172 | -0.25192 | 0.011294 | 0.070387 | 0.071799 | 0.13078 | 0.0018457 | -0.0089999 | -0.25192 | -0.0097668 | 0.062555 | 0.058467 | 0.0091216 | -0.014537 | 72.583 | 72.7844 | 5.5481 | -50.2625 | 72.9492 | -50.1938 | -50.2899 | -48.2803 | 30.8716 | -50.148 | 72.9858 | 72.8577 | -50.2899 | -50.3265 | -0.11444 | -0.21057 | 0.032044 | 122.8638 | -0.1831 | 0.027466 | -0.33417 | -0.21057 | -0.24719 | 0.068665 | 1.799 | -0.068664 | 0.17853 | -0.059509 | 123.0286 | 122.6624 | 55.6274 | -123.2071 | 123.0652 | 122.937 | 80.9509 | -123.2437
3252.0156 | 123.1384 | -50.6058 | 72.2672 | -0.068817 | 0.010653 | 0.07295 | 0.069449 | 0.12672 | -0.0047767 | -0.0085727 | 0.045624 | -0.011049 | 0.063837 | 0.056117 | 0.0076264 | -0.011546 | 72.1436 | 72.3358 | 6.0287 | -50.7339 | 72.4228 | -50.679 | -50.7843 | -48.8434 | 29.9744 | -50.7751 | 72.2717 | 72.171 | -50.8759 | -50.9308 | -0.073242 | -0.17853 | 0.15564 | 122.9416 | -0.12817 | 0.050354 | -0.1236 | -0.27008 | -0.32501 | 0.004578 | 1.7624 | -0.16937 | 0.15564 | -0.09613 | 123.0286 | 122.7493 | 56.6345 | -123.0515 | 122.8775 | 122.7768 | 80.5801 | -123.1979
3253.0156 | 123.1613 | -49.9191 | 72.9813 | -2.0448 | 0.0074491 | 0.071027 | 0.064749 | 0.12928 | -0.0028541 | -0.0075047 | -0.10696 | -0.012758 | 0.063837 | 0.055476 | 0.0065582 | -0.013469 | 72.876 | 73.0041 | 6.5094 | -50.0473 | 73.1003 | -49.9786 | -50.0885 | -48.1522 | 30.4779 | -50.0793 | 72.9904 | 72.908 | -50.148 | -50.1663 | -0.05951 | -0.16937 | 0.11902 | 122.9233 | -0.12817 | 0.041199 | -0.10528 | -0.22888 | -0.24719 | 0.009155 | 1.767 | -0.16022 | 0.086975 | -0.073242 | 123.0194 | 122.7951 | 56.4285 | -123.0698 | 122.9095 | 122.8271 | 80.397 | -123.1476
3254.0156 | 123.1842 | -49.4247 | 73.4848 | -0.061188 | 0.0080899 | 0.0706 | 0.070303 | 0.12758 | -0.0017859 | -0.0077183 | -0.023041 | -0.013185 | 0.062555 | 0.055903 | 0.0093354 | -0.014323 | 73.3109 | 73.5306 | 6.6559 | -49.5804 | 73.5855 | -49.498 | -49.585 | -47.5708 | 30.8487 | -49.411 | 73.5168 | 73.4116 | -49.6216 | -49.649 | -0.073242 | -0.16022 | 0.10071 | 122.9553 | -0.15564 | 0.004578 | -0.17395 | -0.19684 | -0.2243 | 0.032044 | 1.8539 | 0.013733 | 0.23804 | -0.073242 | 123.0103 | 122.7356 | 56.0806 | -123.0698 | 122.9416 | 122.8363 | 80.2734 | -123.1338
3255.0156 | 123.1155 | -50.5142 | 72.3633 | -0.14511 | 0.0093717 | 0.071241 | 0.072867 | 0.12864 | -7.6852e-05 | -0.0055821 | -0.15274 | -0.010408 | 0.065332 | 0.056117 | 0.0074126 | -0.015178 | 72.1802 | 72.3587 | 9.5627 | -50.6882 | 72.4457 | -50.6424 | -50.7339 | -48.7152 | 29.8462 | -50.6332 | 72.4319 | 72.2946 | -50.7614 | -50.7889 | -0.12817 | -0.21973 | 0.082398 | 122.8729 | -0.17395 | 0.045777 | -0.1831 | -0.24719 | -0.27466 | 0.068665 | 1.799 | -0.11902 | 0.15564 | -0.068664 | 122.9599 | 122.6944 | 60.0769 | -123.0972 | 122.9462 | 122.8088 | 80.3604 | -123.1522
3256.0156 | 123.1659 | -48.9349 | 73.9746 | -0.045929 | 0.0085171 | 0.070173 | 0.072653 | 0.12907 | -0.0022131 | -0.0072911 | -0.015411 | -0.011476 | 0.061487 | 0.05633 | 0.0099762 | -0.01411 | 74.0891 | 74.295 | 8.1985 | -48.8068 | 74.3591 | -48.7198 | -48.8251 | -47.1268 | 31.0776 | -49.0677 | 74.025 | 73.9151 | -49.1501 | -49.173 | 0.21515 | 0.10986 | 0.38452 | 123.23 | 0.12817 | 0.01831 | 0.11444 | -0.21515 | -0.23804 | 0.050354 | 1.8082 | -0.13275 | 0.10529 | -0.059509 | 123.2941 | 123.024 | 57.1335 | -122.7997 | 122.9599 | 122.85 | 80.0125 | -123.1476
3257.0156 | 123.143 | -51.535 | 71.3425 | -0.19089 | 0.010867 | 0.070173 | 0.07778 | 0.12886 | 0.0048363 | -0.0055821 | -0.2214 | -0.0099806 | 0.062769 | 0.057398 | 0.0076264 | -0.011119 | 71.0724 | 71.5256 | 6.752 | -51.7136 | 71.4706 | -51.5808 | -51.6724 | -49.6582 | 28.9398 | -51.5579 | 71.4523 | 71.3104 | -51.7319 | -51.7914 | -0.045777 | -0.13733 | 0.12817 | 123.0606 | -0.17853 | -0.041199 | -0.27008 | -0.19684 | -0.25635 | 0.10986 | 1.8768 | -0.022888 | 0.23346 | -0.032043 | 123.0057 | 122.6074 | 58.287 | -123.0148 | 122.9874 | 122.8455 | 80.4749 | -123.1338
3258.0156 | 123.0927 | -50.2213 | 72.6654 | 0.053253 | 0.0074491 | 0.072523 | 0.069235 | 0.13057 | 0.00056395 | -0.0098545 | 0.045624 | -0.0086988 | 0.064051 | 0.05398 | 0.0099762 | -0.013896 | 72.4045 | 72.6151 | 7.3471 | -50.4364 | 72.702 | -50.3677 | -50.473 | -48.4406 | 29.9149 | -50.2029 | 72.7203 | 72.6242 | -50.4318 | -50.4822 | -0.14648 | -0.25177 | 0.036621 | 122.8363 | -0.21515 | 0.036621 | -0.26093 | -0.21057 | -0.26093 | 0.054932 | 1.7807 | 0.01831 | 0.27924 | -0.041198 | 122.9233 | 122.6257 | 57.5684 | -123.1384 | 122.9416 | 122.8455 | 80.1361 | -123.1476
3259.0156 | 123.1613 | -49.7498 | 73.114 | -0.10696 | 0.0093717 | 0.073164 | 0.07244 | 0.128 | 0.00013675 | -0.0072911 | -0.15274 | -0.010408 | 0.060205 | 0.055049 | 0.0035674 | -0.016246 | 72.9767 | 73.2147 | 6.9992 | -49.9191 | 73.1873 | -49.9008 | -49.9832 | -47.8226 | 29.9332 | -49.9237 | 73.1415 | 73.0362 | -50.0336 | -50.0381 | -0.15106 | -0.23346 | 0.073242 | 122.9645 | -0.16937 | 0.064087 | -0.13733 | -0.28381 | -0.28839 | 0.027465 | 1.9272 | -0.17395 | 0.11444 | -0.07782 | 122.937 | 122.7264 | 56.749 | -123.0972 | 122.8912 | 122.7859 | 79.6829 | -123.1522
3260.0156 | 123.1384 | -48.1247 | 74.762 | -0.061188 | 0.012149 | 0.071455 | 0.070303 | 0.12779 | -0.0019995 | -0.0070773 | 0.022736 | -0.010835 | 0.063623 | 0.055262 | 0.0093354 | -0.010478 | 74.469 | 74.7574 | 7.4249 | -48.3353 | 74.7665 | -48.2803 | -48.3856 | -46.3211 | 31.6269 | -48.0423 | 74.8306 | 74.707 | -48.3444 | -48.3673 | -0.15564 | -0.26093 | 0.004578 | 122.8821 | -0.21057 | 0.050354 | -0.29297 | -0.21973 | -0.24262 | 0.068664 | 1.8036 | 0.082398 | 0.32501 | -0.054932 | 122.8912 | 122.5937 | 55.5496 | -123.1476 | 122.9553 | 122.8317 | 79.7516 | -123.1293
3261.0156 | 123.1522 | -51.3016 | 71.5576 | -0.20615 | 0.010653 | 0.069746 | 0.079276 | 0.128 | 0.0041955 | -0.0047275 | -0.17563 | -0.011262 | 0.062555 | 0.057398 | 0.0097626 | -0.014964 | 71.2463 | 71.7545 | 6.6971 | -51.5167 | 71.6537 | -51.3931 | -51.4938 | -49.4522 | 29.0634 | -51.4114 | 71.6629 | 71.5347 | -51.5259 | -51.5671 | -0.091552 | -0.19226 | 0.096131 | 123.056 | -0.21515 | -0.022889 | -0.31128 | -0.2243 | -0.2655 | 0.10529 | 1.8494 | -0.10986 | 0.15564 | -0.022888 | 122.9553 | 122.5479 | 57.9987 | -123.0515 | 122.9645 | 122.8363 | 80.365 | -123.1247
3262.0156 | 123.1522 | -51.2283 | 71.6721 | -0.023041 | 0.0063809 | 0.072096 | 0.071799 | 0.12715 | -0.0013587 | -0.0083591 | -0.0077819 | -0.009126 | 0.064478 | 0.056758 | 0.0086944 | -0.013255 | 71.5393 | 71.7361 | 5.8685 | -51.3519 | 71.814 | -51.2741 | -51.3748 | -49.3149 | 29.1321 | -51.3428 | 71.759 | 71.5988 | -51.4481 | -51.4893 | -0.045776 | -0.14648 | 0.14191 | 122.9645 | -0.1236 | 0.022888 | -0.13275 | -0.21973 | -0.26093 | 0.086975 | 1.9135 | -0.11444 | 0.14648 | -0.073242 | 123.0423 | 122.7676 | 57.0969 | -123.0469 | 122.9874 | 122.8271 | 80.3604 | -123.1613
3263.0156 | 123.1064 | -50.3769 | 72.4777 | -0.19089 | 0.0085171 | 0.069319 | 0.072226 | 0.13035 | -0.00050425 | -0.0057957 | -0.14511 | -0.012758 | 0.062555 | 0.053553 | 0.0099762 | -0.012187 | 72.3129 | 72.5464 | 5.6076 | -50.6424 | 72.5189 | -50.5829 | -50.7019 | -48.5596 | 30.2719 | -50.4639 | 72.5876 | 72.4594 | -50.6058 | -50.6287 | -0.20599 | -0.32501 | 0.041199 | 122.9233 | -0.2655 | 0.059509 | -0.16479 | -0.22888 | -0.25177 | 0.10986 | 1.8173 | -0.086975 | 0.16479 | -0.01831 | 122.8958 | 122.6898 | 55.9845 | -123.1796 | 122.9645 | 122.8363 | 80.6488 | -123.1064
3264.0156 | 123.1064 | -53.3981 | 69.5023 | 0.0074768 | 0.011508 | 0.070387 | 0.071372 | 0.12993 | -0.0022131 | -0.0070773 | 0.11429 | -0.011476 | 0.064264 | 0.058894 | 0.0048492 | -0.01411 | 69.136 | 69.5297 | 5.1178 | -53.5995 | 69.5892 | -53.5355 | -53.6591 | -51.5625 | 27.2461 | -53.4851 | 69.5251 | 69.429 | -53.6316 | -53.6499 | -0.13733 | -0.26093 | 0.086975 | 122.9279 | -0.20142 | 0.05951 | -0.36621 | -0.23346 | -0.25177 | 0.022888 | 1.8356 | -0.086975 | 0.16479 | -0.073242 | 122.9874 | 122.5342 | 58.5159 | -123.1613 | 122.9233 | 122.8271 | 80.6442 | -123.1522
3265.0156 | 123.1384 | -51.9424 | 70.9488 | -0.15274 | 0.011508 | 0.072309 | 0.072226 | 0.12886 | 0.00013675 | -0.0055821 | 0.22873 | -0.0097668 | 0.061701 | 0.057398 | 0.009549 | -0.01176 | 70.5597 | 71.1548 | 7.2556 | -52.4048 | 70.8801 | -52.1851 | -52.2949 | -50.1205 | 28.3951 | -52.0432 | 70.9167 | 70.8069 | -52.2308 | -52.2354 | -0.24262 | -0.35248 | -0.068665 | 123.0972 | -0.46234 | -0.10986 | -0.3891 | -0.28839 | -0.29297 | -0.032044 | 1.8219 | -0.10071 | 0.19226 | -0.14191 | 122.8226 | 122.5021 | 59.198 | -123.2437 | 122.8592 | 122.7493 | 80.3375 | -123.1842
3266.0156 | 123.1567 | -50.798 | 72.0383 | 0.14481 | 0.0089443 | 0.071882 | 0.071372 | 0.13035 | -7.6852e-05 | -0.0081455 | 0.11429 | -0.011049 | 0.064478 | 0.057185 | 0.00784 | -0.014323 | 72.2626 | 72.4731 | 6.8253 | -50.6424 | 72.5235 | -50.5371 | -50.6561 | -48.6328 | 29.48 | -50.9628 | 72.3816 | 72.1848 | -50.8896 | -50.9995 | 0.26093 | 0.14191 | 0.48523 | 123.2712 | 0.15564 | 0.013733 | 0.2243 | -0.091552 | -0.20142 | 0.34332 | 2.1652 | -0.16479 | 0.036621 | 0.14648 | 123.3215 | 123.0606 | 57.6233 | -122.6944 | 123.1796 | 122.9828 | 80.278 | -123.0377
3267.0156 | 123.1705 | -51.0132 | 71.846 | -0.084076 | 0.010013 | 0.071455 | 0.071799 | 0.12758 | -0.00093145 | -0.0057957 | -0.068817 | -0.012544 | 0.062555 | 0.054621 | 0.0097626 | -0.014323 | 71.7041 | 71.9376 | 6.427 | -51.1963 | 71.9284 | -51.1551 | -51.2421 | -49.1226 | 29.3289 | -51.0956 | 71.8506 | 71.7682 | -51.2695 | -51.2741 | -0.14191 | -0.22888 | 0.082398 | 122.9507 | -0.1831 | 0.045776 | -0.14191 | -0.25635 | -0.26093 | 0.004578 | 1.8906 | -0.082397 | 0.17853 | -0.07782 | 122.9416 | 122.7173 | 57.4402 | -123.0881 | 122.8638 | 122.7814 | 80.3421 | -123.1201
3268.0156 | 123.0972 | -50.6424 | 72.2168 | -0.00015269 | 0.0087307 | 0.069319 | 0.072226 | 0.12715 | -0.0028541 | -0.0087863 | 0.14481 | -0.010408 | 0.061701 | 0.055049 | 0.00784 | -0.015178 | 72.3038 | 72.5143 | 7.4387 | -50.5783 | 72.5922 | -50.5325 | -50.6104 | -48.5779 | 29.3472 | -50.5737 | 72.4777 | 72.3358 | -50.7477 | -50.8301 | 0.10986 | 0.032043 | 0.37537 | 123.1567 | 0.064087 | 0.032044 | 0.086975 | -0.10529 | -0.18768 | 0.26093 | 2.0645 | 0.068665 | 0.25635 | 0.11902 | 123.2346 | 122.9462 | 58.0811 | -122.8271 | 123.1201 | 122.9782 | 79.9896 | -123.0469
3269.0156 | 123.1522 | -51.4984 | 71.3058 | -0.045929 | 0.0065945 | 0.072096 | 0.072012 | 0.12886 | -0.0019995 | -0.0064365 | 0.053253 | -0.0099806 | 0.065119 | 0.055903 | 0.0086944 | -0.013042 | 71.1411 | 71.3425 | 8.6838 | -51.6953 | 71.3974 | -51.6403 | -51.7456 | -49.5163 | 28.8757 | -51.4206 | 71.5347 | 71.402 | -51.6632 | -51.7227 | -0.14191 | -0.24719 | 0.091553 | 122.8409 | -0.19684 | 0.050354 | -0.16479 | -0.16479 | -0.2243 | 0.22888 | 1.9821 | 0.07782 | 0.30212 | 0.096131 | 122.8958 | 122.6395 | 60.1822 | -123.0515 | 123.0331 | 122.9004 | 80.3741 | -123.0286
3270.0156 | 123.1247 | -51.3931 | 71.5485 | 0.15244 | 0.0093717 | 0.069959 | 0.068594 | 0.13014 | -0.0011451 | -0.0089999 | 0.16006 | -0.011903 | 0.065332 | 0.056971 | 0.0086944 | -0.012401 | 71.2326 | 71.4478 | 8.8852 | -51.6495 | 71.5164 | -51.5396 | -51.6495 | -49.5712 | 28.8116 | -51.6403 | 71.4981 | 71.3928 | -51.6769 | -51.6953 | -0.14648 | -0.25635 | -0.032044 | 122.8409 | -0.25635 | 0 | -0.31586 | -0.28381 | -0.30212 | -0.050354 | 1.8219 | -0.24719 | 0.054931 | -0.15564 | 122.9095 | 122.6257 | 60.2783 | -123.1979 | 122.8912 | 122.7859 | 80.2048 | -123.2437
3271.0156 | 123.1659 | -52.272 | 70.5734 | -0.023041 | 0.0076627 | 0.071027 | 0.069876 | 0.12651 | -0.0017859 | -0.0066501 | -0.03067 | -0.011689 | 0.059778 | 0.056971 | 0.0084808 | -0.012401 | 70.6833 | 70.9305 | 8.5556 | -52.2629 | 70.9076 | -52.1988 | -52.3132 | -50.354 | 28.3035 | -52.3407 | 70.6833 | 70.5276 | -52.5192 | -52.533 | 0.073242 | -0.041198 | 0.33417 | 123.2025 | 0.009156 | 0.050354 | 0.10986 | -0.24719 | -0.26093 | 0.10986 | 1.918 | -0.068664 | 0.19226 | -0.045776 | 123.1796 | 122.9553 | 60.8276 | -122.8867 | 122.9553 | 122.7997 | 80.5756 | -123.1064
3272.0156 | 123.0972 | -51.1597 | 71.6537 | 0.19821 | 0.012149 | 0.068464 | 0.074362 | 0.12993 | 0.00099115 | -0.0068637 | 0.11429 | -0.010194 | 0.063196 | 0.055049 | 0.011472 | -0.012187 | 71.5851 | 71.7636 | 6.7932 | -51.3199 | 71.7957 | -51.2558 | -51.3428 | -49.2416 | 29.2007 | -51.2741 | 71.7957 | 71.6354 | -51.3977 | -51.4618 | -0.09613 | -0.1831 | 0.14191 | 122.9233 | -0.16022 | 0.022888 | -0.068665 | -0.23804 | -0.30212 | 0.14191 | 1.918 | -0.11444 | 0.18768 | -0.018311 | 122.9553 | 122.7448 | 57.9529 | -122.9965 | 122.9553 | 122.7951 | 80.3604 | -123.1155
3273.0156 | 123.2254 | -49.4156 | 73.4299 | 0.053253 | 0.01044 | 0.0706 | 0.070944 | 0.12907 | -0.0017859 | -0.0081455 | 0.060883 | -0.0093396 | 0.064051 | 0.056758 | 0.0091216 | -0.012401 | 73.2376 | 73.4253 | 7.4707 | -49.6445 | 73.5214 | -49.5438 | -49.6399 | -47.5616 | 30.5511 | -49.4659 | 73.558 | 73.4207 | -49.6353 | -49.6353 | -0.12817 | -0.22431 | 0.091552 | 122.8409 | -0.22888 | -0.004577 | -0.19226 | -0.21973 | -0.21973 | 0.12817 | 1.8539 | -0.050354 | 0.16937 | -0.009156 | 122.937 | 122.6532 | 56.8863 | -123.0698 | 122.9736 | 122.8363 | 79.9667 | -123.0652
3274.0156 | 123.1338 | -49.5255 | 73.3337 | 0.10666 | 0.014499 | 0.071027 | 0.071372 | 0.12736 | -0.00029045 | -0.0049411 | 0.21347 | -0.0095532 | 0.065119 | 0.055262 | 0.011258 | -0.013255 | 73.3475 | 73.5535 | 7.7637 | -49.5895 | 73.5489 | -49.498 | -49.6445 | -47.6303 | 30.4367 | -49.6536 | 73.4207 | 73.3063 | -49.7635 | -49.7635 | 0.027466 | -0.11902 | 0.21515 | 123.0789 | -0.064087 | 0.054931 | 0.013733 | -0.23804 | -0.23804 | 0.086975 | 1.8951 | -0.12817 | 0.10986 | -0.027466 | 123.0743 | 122.8729 | 57.2891 | -122.9782 | 122.9462 | 122.8317 | 79.9622 | -123.0972
3275.0156 | 123.0606 | -50.5737 | 72.3084 | -0.0077822 | 0.0095853 | 0.070814 | 0.069876 | 0.12758 | -0.0013587 | -0.0075047 | 0.083771 | -0.01233 | 0.062982 | 0.055689 | 0.0093354 | -0.012401 | 72.1161 | 72.3495 | 7.7911 | -50.7339 | 72.4182 | -50.647 | -50.7477 | -48.7106 | 29.5898 | -50.6149 | 72.3816 | 72.2397 | -50.7889 | -50.8163 | -0.073243 | -0.17395 | 0.10986 | 122.9233 | -0.16022 | 0.013733 | -0.19226 | -0.21515 | -0.24262 | 0.073242 | 1.8631 | -0.041199 | 0.20142 | -0.068665 | 122.9919 | 122.6898 | 58.3649 | -123.056 | 122.9553 | 122.8134 | 80.1636 | -123.1247
3276.0156 | 123.1705 | -52.0569 | 70.8115 | 0.19821 | 0.015567 | 0.071027 | 0.073935 | 0.13142 | 0.0024865 | -0.0053683 | 0.85434 | -0.011049 | 0.062982 | 0.054835 | 0.011472 | -0.013042 | 70.7382 | 70.8755 | 7.8461 | -52.1851 | 70.9305 | -52.121 | -52.2583 | -50.1251 | 28.4912 | -52.066 | 70.8893 | 70.7611 | -52.272 | -52.2766 | -0.064087 | -0.20142 | 0.11902 | 122.9324 | -0.12817 | 0.073242 | -0.073242 | -0.21515 | -0.21973 | 0.07782 | 1.9318 | -0.009155 | 0.21057 | -0.050354 | 122.9874 | 122.7951 | 59.903 | -123.0698 | 122.9462 | 122.818 | 80.5481 | -123.0881
3277.0156 | 123.1018 | -50.6882 | 72.1939 | 0.16769 | 0.010226 | 0.074232 | 0.070303 | 0.12928 | -0.0015723 | -0.0066501 | 0.22873 | -0.0089124 | 0.060633 | 0.055689 | 0.0084808 | -0.012828 | 72.1893 | 72.3679 | 7.5668 | -50.7156 | 72.464 | -50.6424 | -50.7431 | -48.7656 | 29.6997 | -50.8072 | 72.3129 | 72.1985 | -50.885 | -50.9491 | 0.045776 | -0.054932 | 0.27008 | 123.056 | -0.027466 | 0.027466 | -0.004578 | -0.19684 | -0.26093 | 0.11902 | 1.9226 | -0.11902 | 0.14191 | 0.004577 | 123.1522 | 122.8775 | 58.255 | -122.937 | 123.0011 | 122.8867 | 80.3879 | -123.143
3278.0156 | 123.1201 | -49.8413 | 73.0133 | 0.13718 | 0.011294 | 0.067396 | 0.071799 | 0.12993 | 0.00099115 | -0.0079319 | 0.19058 | -0.011262 | 0.061701 | 0.055689 | 0.010831 | -0.012828 | 72.8714 | 73.0637 | 6.5094 | -50.0748 | 73.1003 | -49.9512 | -50.0656 | -47.9599 | 30.3909 | -49.9283 | 73.082 | 72.995 | -50.0748 | -50.1114 | -0.10986 | -0.2243 | 0.086975 | 122.905 | -0.23346 | -0.009155 | -0.14191 | -0.23346 | -0.27008 | 0.068664 | 1.8814 | -0.086975 | 0.18311 | -0.018311 | 122.9416 | 122.7127 | 56.3507 | -123.0789 | 122.9233 | 122.8363 | 80.2322 | -123.1247
3279.0156 | 123.1338 | -49.9558 | 72.9446 | 0.22873 | 0.012576 | 0.071455 | 0.068167 | 0.12993 | 0.0014185 | -0.0066501 | 0.18295 | -0.0089124 | 0.062342 | 0.054621 | 0.01019 | -0.01411 | 72.7112 | 72.8622 | 6.0333 | -50.235 | 72.9034 | -50.1846 | -50.267 | -48.1384 | 30.3223 | -50.1617 | 72.8943 | 72.7798 | -50.2579 | -50.2853 | -0.22888 | -0.31128 | -0.041199 | 122.818 | -0.27923 | 0.032044 | -0.23346 | -0.30212 | -0.32959 | -0.050354 | 1.8173 | -0.20599 | 0.1236 | -0.16479 | 122.8592 | 122.6669 | 55.9891 | -123.2117 | 122.85 | 122.7356 | 80.278 | -123.23
3280.0156 | 123.0606 | -52.977 | 69.8639 | 0.14481 | 0.015353 | 0.068464 | 0.070303 | 0.1295 | 0.0018457 | -0.0049411 | 0.15244 | -0.007417 | 0.065119 | 0.057185 | 0.012112 | -0.012187 | 69.7174 | 69.8318 | 4.8431 | -53.1876 | 70.0424 | -53.0823 | -53.1921 | -51.0773 | 27.7267 | -53.064 | 70.0333 | 69.9142 | -53.1692 | -53.2196 | -0.10529 | -0.21515 | 0.17853 | 122.8088 | -0.21057 | 0.004578 | -0.14649 | -0.19226 | -0.24261 | 0.16937 | 1.8997 | -0.086975 | 0.15564 | 0.050354 | 123.0194 | 122.6944 | 57.8201 | -123.056 | 123.0103 | 122.8912 | 80.7037 | -123.0835
3281.0156 | 123.1476 | -51.3794 | 71.4752 | 0.099029 | 0.011935 | 0.0706 | 0.070303 | 0.128 | -0.0013587 | -0.0047275 | 0.17532 | -0.0086988 | 0.062342 | 0.060176 | 0.0086944 | -0.013469 | 71.402 | 71.5897 | 5.072 | -51.5259 | 71.5988 | -51.4664 | -51.5259 | -49.4522 | 29.0359 | -51.4343 | 71.553 | 71.4661 | -51.5808 | -51.6495 | -0.086975 | -0.14648 | 0.1236 | 122.9691 | -0.14648 | 0 | -0.073242 | -0.20142 | -0.27008 | 0.07782 | 1.9272 | -0.054931 | 0.21515 | -0.009156 | 122.9782 | 122.7814 | 56.4514 | -123.0011 | 122.9324 | 122.8455 | 80.4153 | -123.1247
3282.0156 | 123.0743 | -49.7269 | 73.1873 | 0.15244 | 0.016849 | 0.071027 | 0.072012 | 0.13057 | 0.0020593 | -0.0051547 | 0.17532 | -0.009126 | 0.067682 | 0.055262 | 0.011685 | -0.012828 | 73.0728 | 73.1827 | 5.1407 | -49.9008 | 73.3795 | -49.8093 | -49.9146 | -47.8363 | 30.3909 | -49.8367 | 73.2788 | 73.1873 | -49.9466 | -49.9832 | -0.082397 | -0.18768 | 0.19226 | 122.9095 | -0.17395 | 0.013733 | -0.11444 | -0.21973 | -0.25635 | 0.091553 | 1.8906 | -0.10986 | 0.14648 | 0 | 123.1064 | 122.7997 | 54.8676 | -123.1018 | 123.0057 | 122.9141 | 80.1178 | -123.1705
3283.0156 | 123.0698 | -49.6719 | 73.2559 | -0.21378 | 0.013003 | 0.069746 | 0.071372 | 0.13014 | -0.0024269 | -0.0064365 | -0.20615 | -0.010194 | 0.06341 | 0.055903 | 0.010617 | -0.01176 | 73.1277 | 73.3063 | 5.1636 | -49.7635 | 73.3749 | -49.7131 | -49.8184 | -47.7951 | 30.4459 | -49.7772 | 73.3475 | 73.2285 | -49.8688 | -49.9329 | -0.041199 | -0.14648 | 0.11902 | 122.9782 | -0.091553 | 0.054931 | -0.12817 | -0.19684 | -0.26093 | 0.091553 | 1.8768 | -0.10529 | 0.15564 | -0.027465 | 123.0469 | 122.7997 | 54.8355 | -123.0743 | 123.0194 | 122.9004 | 80.1178 | -123.1888
3284.0156 | 123.0743 | -49.791 | 73.1689 | 0.16006 | 0.01813 | 0.065473 | 0.069449 | 0.13078 | -0.00029045 | -0.0062229 | 0.36606 | -0.0078442 | 0.064905 | 0.056117 | 0.011044 | -0.013042 | 72.7661 | 72.9904 | 5.0079 | -50.0336 | 73.2422 | -49.9054 | -50.0107 | -47.8638 | 30.2124 | -49.8184 | 73.3109 | 73.1781 | -49.9786 | -50.0015 | -0.11444 | -0.21973 | 0.073242 | 122.7814 | -0.24261 | -0.022888 | -0.40283 | -0.18768 | -0.21057 | 0.14191 | 1.9272 | -0.027465 | 0.18311 | 0.009156 | 123.0331 | 122.5571 | 54.7989 | -123.1796 | 123.1018 | 122.9691 | 80.0034 | -123.1705
3285.0156 | 123.143 | -51.9882 | 70.8847 | 0.17532 | 0.014926 | 0.068891 | 0.070517 | 0.12886 | -0.0024269 | -0.0051547 | 0.30502 | -0.010835 | 0.061914 | 0.057398 | 0.0093354 | -0.013255 | 70.8298 | 70.9763 | 4.4312 | -52.3224 | 70.9579 | -52.0798 | -52.1851 | -50.0473 | 28.5324 | -52.0523 | 70.9625 | 70.8664 | -52.2034 | -52.2217 | -0.091553 | -0.19684 | 0.073242 | 122.9645 | -0.33417 | -0.13733 | -0.054932 | -0.21515 | -0.23346 | 0.077819 | 1.9409 | -0.064087 | 0.16937 | -0.018311 | 122.9462 | 122.818 | 56.4194 | -123.0698 | 122.9507 | 122.8546 | 80.5206 | -123.1064
3286.0156 | 122.9919 | -51.9379 | 70.9717 | 0.17532 | 0.018558 | 0.070173 | 0.071799 | 0.13014 | 0.0027001 | -0.0045139 | 0.10666 | -0.007417 | 0.063196 | 0.055903 | 0.01019 | -0.012187 | 70.8252 | 70.9122 | 5.7816 | -52.0798 | 71.1823 | -51.9745 | -52.0798 | -50.0656 | 28.5873 | -52.1576 | 71.1136 | 70.9991 | -52.1576 | -52.2034 | -0.036621 | -0.14191 | 0.21057 | 122.85 | -0.14191 | 0 | -0.14649 | -0.21973 | -0.2655 | 0.14191 | 1.8723 | -0.21973 | 0.045776 | 0.027466 | 123.1201 | 122.7631 | 57.7194 | -123.0515 | 123.0515 | 122.937 | 80.5252 | -123.175
3287.0156 | 123.0927 | -50.592 | 72.2992 | 0.12955 | 0.015353 | 0.069532 | 0.070517 | 0.12971 | 0.0037683 | -0.0040867 | 0.16006 | -0.0082716 | 0.065119 | 0.054835 | 0.01019 | -0.010478 | 72.2397 | 72.345 | 5.6717 | -50.6607 | 72.5555 | -50.5463 | -50.6882 | -48.5916 | 29.9698 | -50.647 | 72.5006 | 72.4182 | -50.766 | -50.8072 | 0.045776 | -0.09613 | 0.25635 | 122.937 | -0.068665 | 0.027465 | -0.059509 | -0.17395 | -0.21515 | 0.20142 | 2.0004 | -0.054932 | 0.16022 | 0.11902 | 123.1476 | 122.8317 | 56.2637 | -122.9874 | 123.0927 | 123.0103 | 80.5618 | -123.1064
3288.0312 | 123.143 | -49.8505 | 73.0179 | -0.20615 | 0.010013 | 0.072523 | 0.07009 | 0.12886 | -0.0062721 | -0.015195 | -0.54947 | -0.010408 | 0.062128 | 0.055689 | 0.0065582 | -0.010692 | 73.2697 | 73.3429 | 6.3309 | -50.0244 | 73.2513 | -49.8138 | -49.9603 | -48.0377 | 30.6519 | -50.0244 | 73.0499 | 72.9721 | -50.1251 | -50.1114 | 0.036621 | -0.10986 | 0.23346 | 123.1934 | -0.17395 | -0.064087 | 0.25177 | -0.27466 | -0.26093 | 0.032044 | 1.8127 | -0.17395 | 0.086975 | -0.045776 | 123.1018 | 123.1201 | 56.1813 | -122.9782 | 122.9004 | 122.8226 | 80.5023 | -123.1293
3289.0156 | 123.0972 | -49.3057 | 73.5947 | 0.12192 | 0.01813 | 0.071668 | 0.071799 | 0.12843 | 0.0016321 | -0.0072911 | 0.21347 | -0.0097668 | 0.067041 | 0.056971 | 0.010617 | -0.012614 | 73.2285 | 73.3337 | 5.6717 | -49.5575 | 73.6496 | -49.4659 | -49.5392 | -47.4014 | 30.9265 | -49.4522 | 73.7366 | 73.6267 | -49.5163 | -49.5575 | -0.16022 | -0.23346 | 0.054931 | 122.6395 | -0.25177 | -0.01831 | -0.36621 | -0.21057 | -0.25177 | 0.14191 | 1.9043 | -0.14648 | 0.10529 | 0.032043 | 122.9553 | 122.5342 | 54.9774 | -123.1339 | 123.0423 | 122.9324 | 80.2322 | -123.1522
3290.0156 | 123.0194 | -50.5508 | 72.4182 | 0.0074768 | 0.020267 | 0.068678 | 0.072226 | 0.12928 | 0.0029137 | -0.0053683 | 0.030365 | -0.0086988 | 0.065759 | 0.05868 | 0.010403 | -0.01411 | 72.2809 | 72.3587 | 6.0974 | -50.6287 | 72.5693 | -50.5554 | -50.6424 | -48.6649 | 29.9423 | -50.7889 | 72.5098 | 72.377 | -50.7843 | -50.8301 | -0.004578 | -0.091553 | 0.15106 | 122.9095 | -0.07782 | 0.013733 | -0.13733 | -0.23346 | -0.27924 | 0.091553 | 1.886 | -0.23804 | 0.041199 | -0.041199 | 123.1201 | 122.8317 | 56.6483 | -123.0606 | 123.0606 | 122.9279 | 80.4932 | -123.2483
3291.0156 | 123.0057 | -50.7797 | 72.1664 | 0.12955 | 0.018985 | 0.0706 | 0.075003 | 0.12779 | 0.00035035 | -0.0066501 | 2.9295 | -0.0078442 | 0.064264 | 0.055476 | 0.0099762 | -0.011333 | 72.1069 | 72.1848 | 5.928 | -50.8163 | 72.4503 | -50.6882 | -50.8026 | -48.8754 | 29.8508 | -50.8347 | 72.377 | 72.2626 | -50.9628 | -51.0223 | 0.091553 | -0.022888 | 0.28381 | 122.9645 | -0.036621 | -0.013733 | -0.059509 | -0.18311 | -0.24262 | 0.21057 | 1.9043 | -0.054932 | 0.18768 | 0.09613 | 123.23 | 122.8867 | 56.7078 | -122.9691 | 123.1567 | 123.0423 | 80.6305 | -123.1888
3292.0156 | 123.056 | -50.3448 | 72.6013 | -0.023041 | 0.019412 | 0.070814 | 0.07479 | 0.12843 | 0.0020593 | -0.0060093 | 0.045624 | -0.0076306 | 0.065332 | 0.057826 | 0.012326 | -0.012187 | 72.4091 | 72.5464 | 5.1544 | -50.4684 | 72.7112 | -50.386 | -50.4959 | -48.4085 | 29.9561 | -50.4547 | 72.7386 | 72.6471 | -50.5234 | -50.5646 | -0.041198 | -0.15106 | 0.10986 | 122.8912 | -0.1236 | 0.027466 | -0.19226 | -0.17853 | -0.21973 | 0.13733 | 1.9363 | -0.10986 | 0.10986 | 0.045777 | 123.056 | 122.7539 | 55.4993 | -123.0972 | 123.0835 | 122.9919 | 80.3009 | -123.1659
3293.0312 | 123.1522 | -49.5438 | 73.3704 | -0.46555 | 0.0097989 | 0.070814 | 0.070731 | 0.12928 | -0.0066993 | -0.0089999 | -0.015411 | -0.010835 | 0.064691 | 0.056544 | 0.0065582 | -0.01176 | 73.1003 | 73.3612 | 5.6442 | -49.6628 | 73.4024 | -49.6582 | -49.7726 | -47.6257 | 30.7663 | -49.5987 | 73.4482 | 73.3337 | -49.7406 | -49.7681 | -0.11444 | -0.22888 | 0.032044 | 122.905 | -0.11902 | 0.10986 | -0.27008 | -0.19684 | -0.2243 | 0.07782 | 1.918 | -0.054932 | 0.16937 | -0.036621 | 122.9462 | 122.644 | 55.188 | -123.143 | 122.9919 | 122.8775 | 80.3101 | -123.1384
3294.0156 | 123.0743 | -49.6124 | 73.3154 | -0.18326 | 0.016849 | 0.071882 | 0.069663 | 0.13121 | 0.00013675 | -0.0072911 | -0.099335 | -0.0095532 | 0.068537 | 0.057185 | 0.00784 | -0.014323 | 73.1506 | 73.3017 | 5.3329 | -49.736 | 73.4436 | -49.6811 | -49.7635 | -47.7722 | 30.6244 | -49.6719 | 73.3932 | 73.3063 | -49.823 | -49.8779 | -0.068664 | -0.15106 | 0.12817 | 122.9141 | -0.1236 | 0.027466 | -0.1648 | -0.21057 | -0.2655 | 0.07782 | 1.8402 | -0.059509 | 0.20599 | -0.009156 | 123.056 | 122.7631 | 54.9454 | -123.0789 | 123.0057 | 122.9187 | 80.2368 | -123.1934
3295.0156 | 123.0057 | -51.2146 | 71.6721 | 0.068512 | 0.019626 | 0.0706 | 0.074362 | 0.12779 | 0.0027001 | -0.0062229 | -0.015411 | -0.010408 | 0.062982 | 0.056544 | 0.011044 | -0.013469 | 71.4386 | 71.5713 | 4.8248 | -51.4618 | 71.7728 | -51.3977 | -51.4709 | -49.2828 | 29.2648 | -51.2787 | 71.8643 | 71.7773 | -51.384 | -51.4526 | -0.18311 | -0.25635 | 0.10071 | 122.7859 | -0.24719 | 0.009155 | -0.23346 | -0.16937 | -0.23804 | 0.19226 | 1.9318 | -0.064087 | 0.17395 | 0.10529 | 122.9874 | 122.6532 | 56.0394 | -123.143 | 123.0789 | 122.9919 | 80.4794 | -123.1247
3296.0156 | 123.0469 | -51.0635 | 71.846 | -0.19852 | 0.015994 | 0.069746 | 0.073294 | 0.12736 | -0.00029045 | -0.0072911 | -0.15274 | -0.009126 | 0.065546 | 0.05633 | 0.0093354 | -0.013042 | 71.6537 | 71.8094 | 4.9988 | -51.2421 | 71.9925 | -51.1551 | -51.265 | -49.1226 | 29.4891 | -51.1734 | 72.0016 | 71.8964 | -51.2421 | -51.3016 | -0.091552 | -0.20142 | 0.14648 | 122.8729 | -0.17853 | 0.022889 | -0.19226 | -0.17853 | -0.23804 | 0.15564 | 1.9409 | -0.10986 | 0.12817 | 0.050354 | 123.056 | 122.7173 | 56.0623 | -123.111 | 123.0652 | 122.9599 | 80.5527 | -123.1476
3297.0156 | 123.0835 | -49.7177 | 73.2056 | -0.12222 | 0.017276 | 0.069746 | 0.072653 | 0.12715 | 0.00013675 | -0.0079319 | -0.045929 | -0.0099806 | 0.065546 | 0.057185 | 0.011472 | -0.013255 | 73.1644 | 73.1918 | 5.2597 | -49.8093 | 73.3841 | -49.791 | -49.9008 | -47.7768 | 30.5786 | -49.7726 | 73.3109 | 73.233 | -49.9191 | -49.9329 | -0.073243 | -0.18311 | 0.17853 | 122.9095 | -0.091553 | 0.091553 | -0.041198 | -0.20142 | -0.21515 | 0.10529 | 1.9409 | -0.054932 | 0.16022 | 0.027466 | 123.1018 | 122.8821 | 54.9774 | -123.1064 | 123.0286 | 122.9507 | 80.2963 | -123.1384
3298.0156 | 123.0057 | -49.6628 | 73.3109 | -0.03067 | 0.021121 | 0.068464 | 0.070944 | 0.12693 | 0.0016321 | -0.0047275 | -0.00015237 | -0.0093396 | 0.064905 | 0.058467 | 0.0097626 | -0.012828 | 73.0865 | 73.2376 | 6.1249 | -49.8001 | 73.4436 | -49.7086 | -49.7818 | -47.7676 | 30.6107 | -49.7635 | 73.4299 | 73.3292 | -49.8367 | -49.9146 | -0.045776 | -0.11902 | 0.13275 | 122.9004 | -0.13733 | -0.018311 | -0.2243 | -0.17395 | -0.25177 | 0.11902 | 1.8951 | -0.10071 | 0.15106 | 0.018311 | 123.1064 | 122.7493 | 55.7877 | -123.0927 | 123.0927 | 122.9919 | 80.2734 | -123.2254
3299.0156 | 123.0881 | -52.1805 | 70.7336 | -0.091705 | 0.015353 | 0.069746 | 0.071585 | 0.12993 | 0.00099115 | -0.0072911 | 0.17532 | -0.010621 | 0.067896 | 0.05868 | 0.00784 | -0.012187 | 70.4681 | 70.3857 | 5.5069 | -52.3865 | 70.8298 | -52.3224 | -52.3956 | -50.2213 | 28.5461 | -52.4597 | 70.816 | 70.7611 | -52.4048 | -52.4185 | -0.14191 | -0.21515 | 0.09613 | 122.5662 | -0.20599 | 0.009155 | -0.2655 | -0.2243 | -0.23804 | 0.082397 | 1.9592 | -0.27924 | -0.041199 | 0.027465 | 123.0103 | 122.6486 | 57.6874 | -123.1293 | 122.9965 | 122.9416 | 80.7266 | -123.1522
3300.0156 | 123.0515 | -50.528 | 72.4503 | -0.23666 | 0.012362 | 0.0706 | 0.070944 | 0.12651 | -0.0032813 | -0.0098545 | -0.14511 | -0.011262 | 0.062555 | 0.055476 | 0.0065582 | -0.010692 | 72.3862 | 72.6059 | 6.4636 | -50.5005 | 72.7249 | -50.3998 | -50.5005 | -48.6191 | 29.7775 | -50.5829 | 72.5418 | 72.4411 | -50.7019 | -50.7156 | 0.12817 | 0.027466 | 0.27466 | 123.1338 | 0.027466 | 0 | -0.064087 | -0.17395 | -0.18768 | 0.091553 | 1.9089 | -0.054932 | 0.13275 | -0.009155 | 123.2529 | 122.9141 | 56.9916 | -122.9507 | 123.0698 | 122.9691 | 80.3055 | -123.1659
3301.0156 | 123.0331 | -50.9583 | 71.9971 | -0.20615 | 0.016208 | 0.070387 | 0.074362 | 0.12651 | 0.00035035 | -0.0087863 | -0.099335 | -0.0084852 | 0.065759 | 0.055903 | 0.01019 | -0.013469 | 71.8506 | 72.0154 | 6.5231 | -51.0132 | 72.2168 | -50.9399 | -51.0361 | -49.0952 | 29.6173 | -51.1322 | 72.0657 | 71.9833 | -51.1734 | -51.2054 | 0.018311 | -0.07782 | 0.21973 | 122.9736 | -0.054932 | 0.022888 | -0.14648 | -0.21515 | -0.24719 | 0.068665 | 1.8631 | -0.17395 | 0.073242 | -0.013733 | 123.175 | 122.8088 | 57.4814 | -123.0331 | 123.024 | 122.9416 | 80.5756 | -123.2025
3302.0156 | 123.0606 | -51.3474 | 71.5576 | -0.24429 | 0.0095853 | 0.069959 | 0.073508 | 0.128 | -0.0049903 | -0.0072911 | -0.099335 | -0.011903 | 0.062769 | 0.05633 | 0.007199 | -0.011546 | 71.3379 | 71.5439 | 6.0562 | -51.5076 | 71.7041 | -51.4206 | -51.5442 | -49.4293 | 29.1412 | -51.4114 | 71.6995 | 71.5942 | -51.5808 | -51.6174 | -0.073242 | -0.19684 | 0.14649 | 122.8912 | -0.16022 | 0.036621 | -0.21973 | -0.23346 | -0.27008 | 0.14191 | 1.918 | -0.064087 | 0.20599 | 0.036621 | 123.0515 | 122.6852 | 57.4036 | -123.1018 | 123.0469 | 122.9416 | 80.4886 | -123.175
3303.0156 | 123.024 | -50.6378 | 72.3267 | 0.068512 | 0.01813 | 0.069746 | 0.074149 | 0.12779 | 0.0027001 | -0.0049411 | 0.18295 | -0.0078442 | 0.065332 | 0.058467 | 0.0093354 | -0.013469 | 72.0428 | 72.1756 | 5.8228 | -50.8072 | 72.4136 | -50.7202 | -50.8118 | -48.7061 | 29.6906 | -50.8026 | 72.4091 | 72.3495 | -50.798 | -50.853 | -0.082398 | -0.17395 | 0.086975 | 122.8134 | -0.16937 | 0.004578 | -0.28381 | -0.16022 | -0.21515 | 0.082398 | 1.9318 | -0.1648 | 0.050354 | 0.022888 | 123.0515 | 122.6807 | 56.4606 | -123.1384 | 123.0469 | 122.9874 | 80.3284 | -123.1796
3304.0156 | 123.1018 | -49.6902 | 73.1964 | -0.24429 | 0.011508 | 0.070387 | 0.071585 | 0.12843 | -0.0034949 | -0.0075047 | -0.13748 | -0.0089124 | 0.064691 | 0.057826 | 0.00784 | -0.011974 | 72.9034 | 73.1461 | 5.7632 | -49.9191 | 73.2056 | -49.8917 | -49.9741 | -47.7997 | 30.6564 | -49.6902 | 73.2559 | 73.1827 | -49.9603 | -49.9832 | -0.20142 | -0.28381 | 0.009155 | 122.8363 | -0.22888 | 0.054932 | -0.29297 | -0.27008 | -0.29297 | 0.059509 | 1.8906 | 0 | 0.29297 | -0.013733 | 122.8958 | 122.5937 | 55.4535 | -123.1705 | 122.9462 | 122.8729 | 80.3467 | -123.1796
3305.0156 | 123.0423 | -52.1347 | 70.8206 | -0.28244 | 0.015567 | 0.071241 | 0.073935 | 0.13163 | -0.00029045 | -0.0079319 | 0.55679 | -0.0067762 | 0.063837 | 0.055262 | 0.0069854 | -0.013683 | 70.546 | 70.7245 | 5.4977 | -52.3453 | 70.9167 | -52.2491 | -52.3315 | -50.2029 | 28.656 | -52.2125 | 70.9213 | 70.816 | -52.3499 | -52.3956 | -0.11444 | -0.19684 | 0.09613 | 122.8592 | -0.21057 | -0.013733 | -0.27466 | -0.21515 | -0.26093 | 0.10071 | 1.9318 | -0.077819 | 0.18311 | -0.004578 | 123.0515 | 122.6807 | 57.6324 | -123.1522 | 123.056 | 122.9507 | 80.7907 | -123.2162
3306.0156 | 123.0789 | -51.622 | 71.3242 | -0.22903 | 0.010226 | 0.069746 | 0.071799 | 0.12907 | -0.0034949 | -0.0072911 | -0.12985 | -0.011262 | 0.062342 | 0.058467 | 0.0082672 | -0.013683 | 71.0953 | 71.3333 | 5.809 | -51.741 | 71.3562 | -51.6907 | -51.8326 | -49.6628 | 29.0268 | -51.7639 | 71.3425 | 71.2875 | -51.8646 | -51.8875 | -0.068665 | -0.21057 | 0.032043 | 122.9553 | -0.11902 | 0.091553 | -0.22888 | -0.24262 | -0.2655 | 0.01831 | 1.9592 | -0.14191 | 0.1236 | -0.036621 | 122.9782 | 122.7173 | 57.431 | -123.1567 | 122.9645 | 122.9095 | 80.6488 | -123.2117
3307.0156 | 123.0331 | -50.3357 | 72.6334 | -0.22903 | 0.013644 | 0.0706 | 0.07244 | 0.1295 | -0.0022131 | -0.0079319 | -0.21378 | -0.011262 | 0.063837 | 0.055262 | 0.0076264 | -0.011119 | 72.3129 | 72.5143 | 6.3446 | -50.5371 | 72.6608 | -50.4822 | -50.5692 | -48.436 | 30.0018 | -50.473 | 72.6517 | 72.583 | -50.5692 | -50.592 | -0.14648 | -0.23346 | 0.027466 | 122.85 | -0.20142 | 0.032044 | -0.32044 | -0.23346 | -0.25635 | 0.01831 | 1.8997 | -0.13733 | 0.11902 | -0.050354 | 122.9965 | 122.6486 | 56.6803 | -123.2025 | 122.9874 | 122.9187 | 80.3375 | -123.2254
3308.0156 | 123.1613 | -50.0793 | 72.7936 | -0.63339 | 0.0093717 | 0.068037 | 0.071372 | 0.12779 | -0.00029045 | -0.0098545 | -0.091705 | -0.011903 | 0.062128 | 0.057826 | 0.0063446 | -0.011546 | 72.67 | 72.9309 | 6.1249 | -50.2853 | 72.9034 | -50.1938 | -50.2808 | -48.1155 | 30.4092 | -50.1434 | 72.8394 | 72.7707 | -50.3128 | -50.3311 | -0.11444 | -0.20142 | 0.10986 | 123.0103 | -0.20599 | -0.004577 | -0.1236 | -0.23346 | -0.25177 | 0.045776 | 1.9638 | -0.064087 | 0.18768 | -0.022888 | 122.9828 | 122.7493 | 56.2042 | -123.0743 | 122.9187 | 122.85 | 80.4886 | -123.1247
3309.0156 | 123.0194 | -50.235 | 72.7295 | -0.20615 | 0.012362 | 0.068891 | 0.07543 | 0.12758 | -0.00050425 | -0.010068 | -0.25192 | -0.008058 | 0.064264 | 0.056544 | 0.007199 | -0.01411 | 72.6288 | 72.7158 | 6.1569 | -50.2991 | 72.9309 | -50.1938 | -50.3357 | -48.3215 | 29.7684 | -50.386 | 72.8165 | 72.7112 | -50.4501 | -50.5188 | 0.041198 | -0.10071 | 0.20142 | 122.9507 | -0.064087 | 0.036621 | -0.10071 | -0.21515 | -0.28381 | 0.086975 | 1.9135 | -0.15106 | 0.13275 | -0.01831 | 123.1659 | 122.8638 | 56.3919 | -123.0652 | 123.0515 | 122.9462 | 80.0034 | -123.2483
3310.0156 | 123.1659 | -51.8188 | 71.0587 | -0.11459 | 0.0083035 | 0.071027 | 0.071799 | 0.12886 | -0.0043495 | -0.010068 | -0.045929 | -0.013826 | 0.060846 | 0.059962 | 0.010617 | -0.014964 | 70.903 | 71.1685 | 5.6717 | -51.9745 | 71.1182 | -51.9104 | -52.0386 | -49.8001 | 28.4546 | -51.9882 | 71.077 | 71.0129 | -52.0523 | -52.1072 | -0.091552 | -0.21973 | 0.059509 | 122.9874 | -0.15564 | 0.064087 | -0.15564 | -0.23346 | -0.28839 | 0.01831 | 2.0187 | -0.16937 | 0.11902 | -0.045777 | 122.937 | 122.7219 | 57.4905 | -123.0972 | 122.8958 | 122.8317 | 80.2734 | -123.1659
3311.0156 | 123.0652 | -50.2258 | 72.7341 | -0.22903 | 0.012149 | 0.069105 | 0.07479 | 0.12672 | -0.00050425 | -0.0070773 | -0.17563 | -0.011262 | 0.065332 | 0.056758 | 0.0080536 | -0.01411 | 72.5189 | 72.7112 | 5.8548 | -50.3769 | 72.7982 | -50.3036 | -50.4044 | -48.23 | 29.7638 | -50.3036 | 72.8119 | 72.7112 | -50.4181 | -50.4822 | -0.07782 | -0.17853 | 0.064087 | 122.937 | -0.15106 | 0.027466 | -0.21515 | -0.19226 | -0.25635 | 0.07782 | 1.9959 | -0.07782 | 0.17853 | -0.022888 | 123.024 | 122.7448 | 56.0806 | -123.1384 | 123.0377 | 122.937 | 79.9896 | -123.2162
3312.0156 | 123.1979 | -50.4089 | 72.4731 | -0.12222 | 0.0087307 | 0.0706 | 0.068594 | 0.12779 | -0.0037085 | -0.0070773 | 0.060883 | -0.011689 | 0.062982 | 0.055476 | 0.0080536 | -0.012614 | 72.2717 | 72.4915 | 6.1935 | -50.6104 | 72.5143 | -50.528 | -50.6561 | -48.3444 | 29.7134 | -50.4044 | 72.5418 | 72.464 | -50.6149 | -50.6653 | -0.11902 | -0.24719 | 0.041198 | 122.9004 | -0.20142 | 0.045776 | -0.20142 | -0.20599 | -0.25635 | 0.068664 | 2.0645 | 0.004578 | 0.26093 | -0.009156 | 122.9233 | 122.6807 | 56.6025 | -123.1293 | 122.9507 | 122.8729 | 80.1224 | -123.1384
3313.0156 | 123.0469 | -49.3744 | 73.5947 | -0.21378 | 0.012362 | 0.070387 | 0.073081 | 0.12758 | 0.00077755 | -0.0077183 | -0.29007 | -0.011689 | 0.063196 | 0.055262 | 0.0080536 | -0.012828 | 73.3292 | 73.5168 | 6.1478 | -49.5071 | 73.6679 | -49.4522 | -49.5346 | -47.4792 | 30.4138 | -49.3698 | 73.645 | 73.5489 | -49.5987 | -49.6262 | -0.077819 | -0.16022 | 0.073242 | 122.8912 | -0.13275 | 0.027466 | -0.2655 | -0.2243 | -0.25177 | 0.050354 | 1.8951 | 0.004578 | 0.25635 | -0.045777 | 123.0423 | 122.7036 | 55.5222 | -123.1293 | 123.0194 | 122.9233 | 79.7882 | -123.2208
3314.0156 | 123.1796 | -48.8617 | 74.0158 | -0.076447 | 0.012362 | 0.069105 | 0.069663 | 0.13121 | -0.0028541 | -0.0070773 | 0.015106 | -0.010194 | 0.062769 | 0.057398 | 0.0080536 | -0.013469 | 73.8693 | 74.0753 | 6.134 | -49.0219 | 74.1531 | -48.9349 | -49.0402 | -46.8613 | 30.8762 | -48.9441 | 74.0662 | 74.0112 | -49.0952 | -49.1318 | -0.073243 | -0.17853 | 0.13733 | 122.937 | -0.16022 | 0.01831 | -0.14648 | -0.23346 | -0.27008 | 0.050354 | 2.0004 | -0.082398 | 0.18768 | -0.004578 | 123.0148 | 122.731 | 54.9957 | -123.056 | 122.9279 | 122.8729 | 79.7379 | -123.1476
3315.0156 | 123.143 | -50.0565 | 72.6929 | -0.03067 | 0.012576 | 0.072096 | 0.072012 | 0.12736 | -0.00050425 | -0.0085727 | -0.15274 | -0.011049 | 0.064478 | 0.055689 | 0.0086944 | -0.015178 | 73.3429 | 73.5352 | 6.0791 | -49.5621 | 73.5809 | -49.5209 | -49.5987 | -47.5021 | 30.455 | -49.3561 | 73.5489 | 73.4344 | -49.791 | -50.0198 | 0.53558 | 0.45776 | 0.88806 | 123.5916 | 0.49439 | 0.036621 | 0.65002 | 0.2655 | 0.036622 | 0.85602 | 2.5543 | 0.70038 | 0.66376 | 0.74158 | 123.6374 | 123.3994 | 56.1356 | -122.2916 | 123.6053 | 123.4909 | 80.5115 | -122.7127
3316.0156 | 123.1705 | -49.1501 | 73.7366 | -0.091705 | 0.0065945 | 0.072096 | 0.070517 | 0.12843 | -0.0041357 | -0.0085727 | -0.015411 | -0.0097668 | 0.062982 | 0.056117 | 0.0074126 | -0.013469 | 73.6908 | 73.8785 | 5.9143 | -49.2142 | 73.9243 | -49.1821 | -49.2462 | -46.9116 | 30.7343 | -48.9899 | 73.9243 | 73.8327 | -49.2691 | -49.3515 | -0.032044 | -0.096131 | 0.18768 | 123.0286 | -0.064087 | 0.032044 | -0.045776 | -0.11902 | -0.20142 | 0.18768 | 2.2385 | 0.16022 | 0.36163 | 0.096131 | 123.0743 | 122.8409 | 55.0644 | -122.9828 | 123.0743 | 122.9828 | 79.8843 | -123.0881
3317.0156 | 123.1064 | -50.6287 | 72.3084 | -0.20615 | 0.0091581 | 0.071668 | 0.073081 | 0.13035 | -0.00050425 | -0.0066501 | -0.19852 | -0.01233 | 0.064691 | 0.056544 | 0.00784 | -0.012828 | 72.5189 | 72.7249 | 5.6671 | -50.5737 | 72.6883 | -50.4959 | -50.6332 | -48.6511 | 29.3747 | -50.9445 | 72.3084 | 72.226 | -50.8713 | -50.8942 | 0.13275 | -0.004578 | 0.37994 | 123.3536 | 0.054932 | 0.05951 | 0.21057 | -0.24262 | -0.2655 | 0 | 1.9775 | -0.31586 | -0.050354 | -0.082398 | 123.317 | 123.1476 | 56.2958 | -122.9416 | 122.937 | 122.8546 | 80.0034 | -123.2025
3318.0156 | 123.1842 | -50.1846 | 72.6517 | -0.0383 | 0.010226 | 0.070387 | 0.068381 | 0.12886 | -0.0022131 | -0.0085727 | -0.00015237 | -0.013826 | 0.062769 | 0.056971 | 0.0091216 | -0.013042 | 72.5876 | 72.7936 | 5.603 | -50.3403 | 72.8119 | -50.3036 | -50.3632 | -48.2758 | 29.5715 | -50.3174 | 72.6883 | 72.6151 | -50.4501 | -50.441 | -0.11902 | -0.17853 | 0.16022 | 122.9782 | -0.15564 | 0.022888 | -0.064087 | -0.2655 | -0.25635 | 0.036621 | 1.9089 | -0.13275 | 0.1236 | -0.036621 | 122.9965 | 122.7722 | 55.7877 | -123.0148 | 122.8729 | 122.7997 | 79.7562 | -123.0927
3319.0156 | 123.143 | -49.8688 | 73.027 | -0.19089 | 0.010226 | 0.0706 | 0.072012 | 0.12886 | -0.0017859 | -0.0072911 | -0.13748 | -0.011476 | 0.061914 | 0.056117 | 0.0093354 | -0.013683 | 72.8256 | 73.0499 | 6.2805 | -50.0793 | 73.0728 | -50.0061 | -50.1205 | -47.8455 | 29.8508 | -49.9603 | 73.082 | 72.9538 | -50.1114 | -50.116 | -0.13733 | -0.25177 | 0.045776 | 122.9187 | -0.21057 | 0.041198 | -0.20142 | -0.24262 | -0.24719 | 0.054931 | 2.0233 | -0.091553 | 0.15564 | -0.073243 | 122.9416 | 122.6944 | 56.1493 | -123.1476 | 122.9507 | 122.8226 | 79.7195 | -123.143
3320.0156 | 123.1567 | -49.823 | 73.0362 | -0.091705 | 0.0091581 | 0.072309 | 0.071585 | 0.13078 | -0.0032813 | -0.0092137 | -0.015411 | -0.010835 | 0.060846 | 0.056544 | 0.0080536 | -0.012828 | 72.9218 | 73.1552 | 6.2485 | -49.942 | 73.2422 | -49.8642 | -49.9741 | -47.8592 | 29.7546 | -49.9603 | 73.1003 | 73.0041 | -50.0565 | -50.116 | -0.041199 | -0.15106 | 0.20599 | 122.9782 | -0.11902 | 0.032043 | -0.11444 | -0.23346 | -0.29297 | 0.064087 | 1.9638 | -0.13733 | 0.15564 | -0.032044 | 123.0652 | 122.7448 | 56.0715 | -123.0103 | 122.9233 | 122.8271 | 79.5776 | -123.1522
3321.0156 | 123.1659 | -51.0635 | 71.7957 | -0.19089 | 0.010867 | 0.071668 | 0.073081 | 0.12928 | -0.0062721 | -0.011991 | -0.11459 | -0.0084852 | 0.061914 | 0.05398 | 0.0099762 | -0.012614 | 72.0566 | 71.64 | 6.0379 | -51.0727 | 72.0154 | -51.0727 | -51.1642 | -48.9075 | 28.9902 | -51.0086 | 71.9833 | 71.8689 | -51.1917 | -51.265 | -0.009155 | -0.10071 | 0.21973 | 122.7036 | -0.009155 | 0.091553 | 0.26093 | -0.12817 | -0.20142 | 0.18768 | 2.1561 | 0.054932 | 0.25635 | 0.073242 | 123.0789 | 123.1201 | 57.1014 | -122.9599 | 123.0469 | 122.9324 | 80.0537 | -123.0606
3322.0156 | 123.1567 | -50.2899 | 72.5967 | -0.0077822 | 0.0095853 | 0.071027 | 0.072653 | 0.12629 | -0.00093145 | -0.0077183 | -0.015411 | -0.011049 | 0.062555 | 0.054621 | 0.007199 | -0.013042 | 72.4777 | 72.702 | 5.9463 | -50.4501 | 72.7158 | -50.3815 | -50.4776 | -48.1888 | 29.5853 | -50.3998 | 72.6562 | 72.5006 | -50.5463 | -50.592 | -0.091553 | -0.18768 | 0.11902 | 122.9919 | -0.16022 | 0.027466 | -0.11902 | -0.25635 | -0.30212 | 0.059509 | 2.1011 | -0.10986 | 0.19226 | -0.096131 | 123.0057 | 122.7676 | 56.2363 | -123.0743 | 122.9462 | 122.7905 | 79.8752 | -123.1888
3323.0156 | 123.1201 | -49.942 | 72.9584 | -0.10696 | 0.01279 | 0.071668 | 0.073508 | 0.1295 | 0.00056395 | -0.0077183 | -0.13748 | -0.011689 | 0.064051 | 0.055689 | 0.010403 | -0.017528 | 72.8348 | 73.0133 | 5.6808 | -50.029 | 73.0865 | -49.9969 | -50.0839 | -47.9279 | 29.9423 | -50.0427 | 73.0499 | 72.9263 | -50.1846 | -50.2167 | -0.054931 | -0.14191 | 0.12817 | 122.9553 | -0.086975 | 0.054931 | -0.1236 | -0.24261 | -0.27466 | 0.091553 | 2.0142 | -0.10071 | 0.17395 | -0.032043 | 123.0286 | 122.7768 | 55.6229 | -123.0423 | 122.9919 | 122.8683 | 79.8843 | -123.175
3324.0156 | 123.1293 | -49.3195 | 73.5352 | -0.099335 | 0.0091581 | 0.071668 | 0.07244 | 0.13099 | -0.0026405 | -0.0096409 | -0.061188 | -0.011262 | 0.061914 | 0.056758 | 0.009549 | -0.013469 | 73.4573 | 73.6679 | 5.6671 | -49.4339 | 73.7045 | -49.379 | -49.4431 | -47.2229 | 30.4413 | -49.3378 | 73.6588 | 73.5397 | -49.5163 | -49.5438 | -0.059509 | -0.1236 | 0.16937 | 122.9874 | -0.11444 | 0.009155 | -0.07782 | -0.19684 | -0.2243 | 0.1236 | 2.0966 | -0.018311 | 0.20599 | 0.004578 | 123.024 | 122.7768 | 54.9866 | -122.9782 | 122.9782 | 122.8592 | 79.7607 | -123.0789
3325.0156 | 123.1613 | -49.0768 | 73.8007 | -0.17563 | 0.01044 | 0.077436 | 0.073935 | 0.12758 | 0.0012047 | -0.0064365 | -0.39688 | -0.010621 | 0.062982 | 0.057398 | 0.010403 | -0.013896 | 73.7412 | 73.9471 | 5.5298 | -49.1959 | 73.9517 | -49.1043 | -49.2004 | -47.0123 | 30.7297 | -49.0814 | 73.9151 | 73.7732 | -49.2828 | -49.3195 | -0.027466 | -0.1236 | 0.15106 | 123.024 | -0.11902 | 0.004577 | -0.059509 | -0.20599 | -0.24262 | 0.11444 | 2.0645 | -0.004578 | 0.23804 | -0.027466 | 123.0286 | 122.818 | 54.6066 | -123.0011 | 122.9919 | 122.85 | 79.8065 | -123.1201
3326.0156 | 123.175 | -49.118 | 73.7961 | -0.015411 | 0.0089443 | 0.071668 | 0.072226 | 0.12672 | -0.00029045 | -0.0077183 | 0.022736 | -0.011049 | 0.062769 | 0.056758 | 0.0076264 | -0.012828 | 73.645 | 73.8693 | 5.8136 | -49.1959 | 73.9517 | -49.1455 | -49.2142 | -47.0215 | 30.6381 | -49.0677 | 73.8968 | 73.7732 | -49.2783 | -49.3332 | -0.027466 | -0.09613 | 0.15564 | 122.9874 | -0.07782 | 0.01831 | -0.15106 | -0.16022 | -0.21515 | 0.10071 | 2.0966 | 0.050354 | 0.2655 | -0.022889 | 123.0698 | 122.7631 | 54.9316 | -123.0103 | 123.0148 | 122.8912 | 79.7562 | -123.1293
3327.0156 | 123.1247 | -48.5001 | 74.3774 | -0.091705 | 0.0083035 | 0.069959 | 0.07009 | 0.12715 | 0.00099115 | -0.0053683 | -0.14511 | -0.011903 | 0.061487 | 0.056758 | 0.010831 | -0.013042 | 74.3225 | 74.5193 | 6.1981 | -48.5504 | 74.5743 | -48.5001 | -48.6053 | -46.3257 | 31.1417 | -48.4863 | 74.5331 | 74.4324 | -48.6877 | -48.7427 | 0 | -0.10529 | 0.19684 | 123.0194 | -0.050354 | 0.054932 | -0.054931 | -0.18768 | -0.24262 | 0.15564 | 2.1744 | 0.013733 | 0.25635 | 0.054932 | 123.0743 | 122.8226 | 54.6982 | -122.9828 | 123.0331 | 122.9324 | 79.6417 | -123.1201
3328.0156 | 123.1201 | -49.0814 | 73.8052 | -0.015411 | 0.011508 | 0.068891 | 0.07009 | 0.128 | -0.00071785 | -0.0081455 | 0.083771 | -0.011049 | 0.061701 | 0.055903 | 0.009549 | -0.013469 | 73.5855 | 73.8373 | 6.1523 | -49.2325 | 73.9059 | -49.1821 | -49.2508 | -47.0352 | 30.6564 | -49.054 | 73.8922 | 73.8007 | -49.2874 | -49.3469 | -0.10071 | -0.16937 | 0.10071 | 122.9187 | -0.15106 | 0.01831 | -0.21973 | -0.20599 | -0.2655 | 0.086975 | 2.0462 | 0.027466 | 0.29297 | -0.004578 | 122.9874 | 122.6669 | 55.2338 | -123.056 | 122.9736 | 122.8821 | 79.7379 | -123.1522
3329.0156 | 123.1338 | -48.2071 | 74.6704 | -0.15274 | 0.0093717 | 0.077863 | 0.076712 | 0.12907 | 0.0033411 | -0.0081455 | -0.35873 | -0.0095532 | 0.064051 | 0.056971 | 0.011258 | -0.013469 | 74.2447 | 74.4278 | 6.5872 | -48.4589 | 74.5743 | -48.4451 | -48.5275 | -46.1288 | 31.5079 | -48.175 | 74.7482 | 74.6475 | -48.4085 | -48.4497 | -0.23804 | -0.32043 | -0.09613 | 122.6349 | -0.25177 | 0.068665 | -0.42572 | -0.20142 | -0.24261 | 0.07782 | 2.0782 | 0.032043 | 0.27466 | -0.022888 | 122.7814 | 122.4518 | 54.7943 | -123.1979 | 122.9553 | 122.8546 | 79.715 | -123.1201
3330.0156 | 123.111 | -48.5229 | 74.3134 | 0.0074768 | 0.0095853 | 0.069959 | 0.07009 | 0.12544 | -0.00071785 | -0.0085727 | -0.023041 | -0.011689 | 0.064478 | 0.059107 | 0.0080536 | -0.014537 | 74.5056 | 74.7116 | 6.5323 | -48.3536 | 74.7986 | -48.2758 | -48.3902 | -46.2204 | 31.366 | -48.3078 | 74.6887 | 74.5331 | -48.6145 | -48.7335 | 0.24719 | 0.13275 | 0.48523 | 123.2346 | 0.16937 | 0.036621 | 0.19226 | -0.091553 | -0.21057 | 0.37537 | 2.3026 | 0.21515 | 0.42572 | 0.21973 | 123.3215 | 123.0286 | 55.0552 | -122.7036 | 123.2117 | 123.056 | 79.8889 | -123.0469
3331.0156 | 123.1247 | -50.3036 | 72.5647 | -0.16037 | 0.010653 | 0.072736 | 0.07009 | 0.12993 | 0.0014185 | -0.0079319 | -0.20615 | -0.010621 | 0.065119 | 0.055262 | 0.0091216 | -0.014323 | 72.6471 | 72.8394 | 6.0287 | -50.235 | 72.8531 | -50.2167 | -50.3082 | -48.2117 | 29.8141 | -50.441 | 72.7341 | 72.5876 | -50.5096 | -50.5417 | 0.086975 | -0.004578 | 0.28839 | 123.143 | 0.068665 | 0.073243 | 0.082398 | -0.20599 | -0.23804 | 0.16937 | 2.092 | -0.13733 | 0.10071 | 0.022888 | 123.1567 | 122.9507 | 56.3324 | -122.8729 | 123.0377 | 122.8912 | 80.1178 | -123.1064
3332.0156 | 123.1476 | -49.173 | 73.732 | 0.32028 | 0.0085171 | 0.071882 | 0.069663 | 0.12993 | -0.0019995 | -0.0077183 | 0.0074766 | -0.012544 | 0.06341 | 0.058467 | 0.0086944 | -0.011119 | 73.5489 | 73.7961 | 6.1935 | -49.2966 | 73.8785 | -49.205 | -49.3149 | -47.0993 | 30.7114 | -49.2554 | 73.7961 | 73.6771 | -49.3973 | -49.4064 | -0.032043 | -0.14191 | 0.14648 | 122.9691 | -0.1236 | 0.01831 | -0.18311 | -0.2243 | -0.23346 | 0.064087 | 2.0737 | -0.082397 | 0.15106 | -0.054932 | 123.0515 | 122.7219 | 55.3665 | -123.0469 | 122.9691 | 122.85 | 79.8843 | -123.1384
3333.0156 | 123.1201 | -50.5417 | 72.3221 | 0.14481 | 0.011294 | 0.070387 | 0.071372 | 0.12971 | -0.0017859 | -0.0051547 | -0.19089 | -0.010621 | 0.064478 | 0.054835 | 0.0091216 | -0.011974 | 72.1802 | 72.3816 | 5.7404 | -50.7019 | 72.4136 | -50.6607 | -50.7339 | -48.4177 | 29.6494 | -50.5966 | 72.4594 | 72.3312 | -50.7431 | -50.7797 | -0.11902 | -0.19226 | 0.091552 | 122.9233 | -0.16022 | 0.032044 | -0.14191 | -0.20142 | -0.23804 | 0.13733 | 2.124 | -0.054932 | 0.18311 | 0.009155 | 122.9553 | 122.7219 | 56.282 | -123.056 | 123.0011 | 122.8729 | 80.191 | -123.1018
3334.0156 | 123.1338 | -49.4064 | 73.5077 | 0.053253 | 0.01044 | 0.069532 | 0.071585 | 0.12651 | -0.0019995 | -0.0075047 | 0.045624 | -0.0095532 | 0.062555 | 0.055049 | 0.0086944 | -0.013255 | 73.1827 | 73.3154 | 6.0013 | -49.6948 | 73.4619 | -49.6445 | -49.7498 | -47.3419 | 30.5145 | -49.4019 | 73.5489 | 73.4344 | -49.6445 | -49.6719 | -0.23804 | -0.34332 | -0.045776 | 122.7219 | -0.28839 | 0.054932 | -0.32501 | -0.23804 | -0.2655 | 0.041199 | 2.0645 | 0.004578 | 0.27008 | -0.073242 | 122.8683 | 122.5891 | 55.4077 | -123.2574 | 122.9553 | 122.8409 | 79.921 | -123.1796
3335.0156 | 123.1796 | -50.0198 | 72.8439 | -0.19089 | 0.010867 | 0.069105 | 0.070731 | 0.12843 | -0.0015723 | -0.0064365 | -0.14511 | -0.011049 | 0.061487 | 0.056758 | 0.0093354 | -0.014964 | 72.8531 | 73.0865 | 6.0791 | -50.0473 | 73.082 | -49.9832 | -50.1297 | -47.818 | 30.0751 | -50.0107 | 72.9767 | 72.8531 | -50.1846 | -50.2213 | 0.036621 | -0.10986 | 0.23804 | 123.1064 | -0.027466 | 0.082398 | 0.009155 | -0.1648 | -0.20142 | 0.13275 | 2.2018 | 0.009155 | 0.21057 | 0.009155 | 123.1018 | 122.8729 | 56.0989 | -122.9736 | 122.9965 | 122.8729 | 80.0949 | -123.0652
3336.0156 | 123.143 | -48.7518 | 74.1119 | -0.03067 | 0.0087307 | 0.069959 | 0.070731 | 0.128 | -0.0011451 | -0.0070773 | 0.060883 | -0.011689 | 0.062342 | 0.056117 | 0.010403 | -0.012828 | 73.9883 | 74.2126 | 6.1066 | -48.8708 | 74.295 | -48.8342 | -48.9166 | -46.5866 | 31.0318 | -48.8297 | 74.2813 | 74.0936 | -48.9761 | -49.0311 | -0.082398 | -0.16479 | 0.18311 | 122.9645 | -0.11902 | 0.045776 | -0.1236 | -0.2243 | -0.27924 | 0.16937 | 2.1652 | -0.07782 | 0.20142 | -0.01831 | 123.0469 | 122.7402 | 54.8584 | -123.0286 | 123.0331 | 122.8455 | 79.7836 | -123.143
3337.0156 | 123.1476 | -48.6694 | 74.1806 | -0.168 | 0.0076627 | 0.070814 | 0.070944 | 0.12779 | -0.0047767 | -0.011136 | -0.038299 | -0.012758 | 0.062982 | 0.054835 | 0.008908 | -0.014537 | 74.2767 | 73.9334 | 6.0471 | -48.761 | 74.263 | -48.761 | -48.8525 | -46.5134 | 31.1142 | -48.6145 | 74.3454 | 74.2081 | -48.8525 | -48.9166 | -0.091552 | -0.1831 | 0.082397 | 122.6028 | -0.091552 | 0.091553 | 0.09613 | -0.1831 | -0.24719 | 0.16479 | 2.1561 | 0.054932 | 0.30212 | 0.027466 | 122.9324 | 122.9462 | 54.7165 | -123.0331 | 123.0148 | 122.8775 | 79.7836 | -123.0972
3338.0156 | 123.1293 | -49.9237 | 72.9263 | 0.0074768 | 0.01044 | 0.071027 | 0.072653 | 0.12928 | -0.0026405 | -0.0092137 | 0.0074766 | -0.0097668 | 0.062555 | 0.056758 | 0.0091216 | -0.014323 | 72.9492 | 73.1781 | 6.5506 | -49.91 | 73.2651 | -49.8322 | -49.9374 | -47.8134 | 29.9332 | -50.0244 | 73.0728 | 72.9446 | -50.1572 | -50.1572 | 0.091553 | -0.013733 | 0.33874 | 123.1018 | 0.013733 | 0.027466 | 0.022888 | -0.23346 | -0.23346 | 0.14648 | 2.1103 | -0.10071 | 0.13275 | 0.01831 | 123.1888 | 122.8729 | 56.4743 | -122.8638 | 122.9965 | 122.8683 | 79.8569 | -123.0835
3339.0156 | 123.175 | -49.3286 | 73.5626 | -0.18326 | 0.0093717 | 0.072096 | 0.069663 | 0.12822 | 0.00035035 | -0.0075047 | -1.6862 | -0.01468 | 0.062769 | 0.056971 | 0.0099762 | -0.015178 | 73.494 | 73.7 | 6.926 | -49.4385 | 73.7183 | -49.3881 | -49.4705 | -47.1085 | 30.5054 | -49.3744 | 73.6084 | 73.5077 | -49.5483 | -49.5895 | -0.05951 | -0.14191 | 0.15564 | 123.0286 | -0.10986 | 0.032043 | -0.068664 | -0.21973 | -0.26093 | 0.045776 | 2.2202 | -0.045777 | 0.21515 | -0.054932 | 123.0469 | 122.8226 | 56.2546 | -123.0331 | 122.937 | 122.8363 | 79.834 | -123.1522
3340.0156 | 123.1476 | -50.2579 | 72.5967 | -0.15274 | 0.0093717 | 0.072309 | 0.069876 | 0.12864 | -0.00050425 | -0.0062229 | -0.13748 | -0.0099806 | 0.062982 | 0.056117 | 0.0084808 | -0.015605 | 72.5327 | 72.7753 | 6.9672 | -50.3769 | 72.7066 | -50.3586 | -50.4272 | -48.0331 | 29.7409 | -50.5051 | 72.6746 | 72.5327 | -50.4913 | -50.5096 | -0.10071 | -0.16937 | 0.10986 | 123.0331 | -0.11902 | 0.050354 | -0.064087 | -0.23346 | -0.25177 | 0.07782 | 2.2247 | -0.24719 | 0.004578 | -0.064087 | 122.9645 | 122.7905 | 57.225 | -123.024 | 122.9324 | 122.7905 | 79.9988 | -123.1064
3341.0156 | 123.0652 | -49.5209 | 73.3337 | -0.24429 | 0.0085171 | 0.074018 | 0.072226 | 0.12758 | 0.0012047 | -0.0072911 | -0.099335 | -0.010194 | 0.065546 | 0.055689 | 0.0082672 | -0.013469 | 73.2697 | 73.526 | 6.871 | -49.6216 | 73.5123 | -49.5941 | -49.6902 | -47.3557 | 30.4779 | -49.5163 | 73.4161 | 73.3429 | -49.7452 | -49.7543 | -0.073242 | -0.16937 | 0.17853 | 123.0469 | -0.10071 | 0.068665 | -0.064087 | -0.2243 | -0.23346 | 0.082398 | 2.1652 | 0.004578 | 0.23804 | 0.009156 | 123.0331 | 122.7905 | 56.3919 | -123.024 | 122.937 | 122.8638 | 79.9988 | -123.0881
3342.0156 | 123.111 | -49.1547 | 73.6954 | 0.030365 | 0.0093717 | 0.072523 | 0.070517 | 0.12822 | 0.00099115 | -0.0077183 | 0.10666 | -0.010194 | 0.062769 | 0.057612 | 0.010831 | -0.013683 | 73.5168 | 73.7686 | 6.6055 | -49.3927 | 73.8419 | -49.2737 | -49.379 | -47.0123 | 30.7251 | -49.118 | 73.8693 | 73.7274 | -49.3286 | -49.379 | -0.11902 | -0.2243 | 0.14648 | 122.9233 | -0.23804 | -0.013733 | -0.17853 | -0.17395 | -0.2243 | 0.17395 | 2.1423 | 0.036621 | 0.26093 | 0.032043 | 122.9965 | 122.6715 | 55.7602 | -123.0743 | 123.024 | 122.8821 | 79.8798 | -123.0743
3343.0156 | 123.0515 | -49.5941 | 73.3017 | -0.20615 | 0.01279 | 0.071668 | 0.071799 | 0.13035 | -0.0011451 | -0.0079319 | -0.19852 | -0.010194 | 0.061914 | 0.05398 | 0.010617 | -0.013255 | 73.3704 | 73.5718 | 6.4407 | -49.5438 | 73.6038 | -49.4934 | -49.5804 | -47.406 | 30.3772 | -49.6078 | 73.5352 | 73.4024 | -49.6994 | -49.7726 | 0.10071 | 0.013733 | 0.30212 | 123.1659 | 0.050354 | 0.036621 | 0.068664 | -0.10529 | -0.17853 | 0.23346 | 2.1881 | -0.013733 | 0.16479 | 0.10071 | 123.1979 | 122.9645 | 56.0349 | -122.8821 | 123.1293 | 122.9965 | 79.9713 | -123.0743
3344.0156 | 123.1293 | -49.3607 | 73.5764 | -0.0077822 | 0.0097989 | 0.071668 | 0.067954 | 0.12544 | 0.00013675 | -0.0089999 | -0.038299 | -0.012758 | 0.063196 | 0.059107 | 0.0099762 | -0.011974 | 73.288 | 73.5168 | 7.6492 | -49.5438 | 73.613 | -49.4705 | -49.5621 | -47.2778 | 30.4047 | -49.4064 | 73.5626 | 73.4253 | -49.6353 | -49.6628 | -0.10986 | -0.20142 | 0.036621 | 122.8775 | -0.1831 | 0.018311 | -0.28839 | -0.27466 | -0.30212 | -0.013733 | 2.0828 | -0.045776 | 0.25635 | -0.15106 | 122.9736 | 122.6486 | 57.0099 | -123.1384 | 122.9233 | 122.7859 | 79.7653 | -123.2391
3345.0156 | 123.1613 | -50.2121 | 72.6425 | -0.21378 | 0.011294 | 0.0706 | 0.069663 | 0.128 | -0.00071785 | -0.0079319 | -0.15274 | -0.010194 | 0.062769 | 0.052699 | 0.0097626 | -0.013683 | 72.6425 | 72.8668 | 6.8436 | -50.2487 | 72.8851 | -50.235 | -50.3174 | -47.9874 | 29.7546 | -50.2441 | 72.7982 | 72.6562 | -50.4227 | -50.473 | -0.022888 | -0.10529 | 0.24262 | 123.0789 | -0.036621 | 0.068665 | 0 | -0.21057 | -0.26093 | 0.15564 | 2.2247 | -0.032044 | 0.22888 | 0.013733 | 123.0972 | 122.8546 | 57.0557 | -122.9599 | 123.0103 | 122.8683 | 79.9667 | -123.1155
3346.0156 | 123.1567 | -49.086 | 73.8007 | 0.022736 | 0.0080899 | 0.0706 | 0.067526 | 0.12843 | -0.0013587 | -0.0064365 | 0.045624 | -0.011903 | 0.062555 | 0.055476 | 0.0091216 | -0.011974 | 73.7137 | 73.9426 | 7.0084 | -49.1913 | 74.0112 | -49.1043 | -49.205 | -46.9894 | 30.5191 | -49.2599 | 73.8785 | 73.7503 | -49.3149 | -49.379 | -0.01831 | -0.11902 | 0.21057 | 123.0286 | -0.10529 | 0.013733 | -0.086975 | -0.22888 | -0.29297 | 0.07782 | 2.0966 | -0.17395 | 0.11902 | -0.050354 | 123.0972 | 122.7997 | 56.0944 | -123.0057 | 122.9645 | 122.8363 | 79.6051 | -123.1796
3347.0156 | 123.0606 | -48.4451 | 74.4965 | -0.24429 | 0.012576 | 0.072736 | 0.071158 | 0.12971 | -7.6852e-05 | -0.0070773 | -0.9996 | -0.011262 | 0.063837 | 0.056758 | 0.0084808 | -0.013683 | 74.2722 | 74.4507 | 6.7795 | -48.6191 | 74.5651 | -48.5641 | -48.6694 | -46.3852 | 31.1417 | -48.5458 | 74.5651 | 74.4232 | -48.7152 | -48.7244 | -0.11902 | -0.22431 | 0.068665 | 122.8958 | -0.17395 | 0.050354 | -0.2243 | -0.27008 | -0.27924 | 0.068665 | 2.0599 | -0.10071 | 0.17853 | -0.073242 | 123.0103 | 122.7173 | 55.2246 | -123.1659 | 123.0103 | 122.8683 | 79.5868 | -123.2208
3348.0156 | 123.1293 | -49.1592 | 73.7228 | -0.19852 | 0.011081 | 0.069746 | 0.072653 | 0.12843 | -0.0019995 | -0.0062229 | -0.11459 | -0.011903 | 0.06341 | 0.056544 | 0.0093354 | -0.013255 | 73.7732 | 73.9883 | 6.9489 | -49.1226 | 74.0021 | -49.0997 | -49.1821 | -46.9666 | 30.574 | -49.2279 | 73.8693 | 73.7228 | -49.3423 | -49.4019 | 0.05951 | -0.022888 | 0.27924 | 123.1476 | 0.036621 | 0.059509 | 0.050354 | -0.1831 | -0.24261 | 0.14649 | 2.1927 | -0.068664 | 0.17395 | 0 | 123.1613 | 122.9324 | 56.1081 | -122.905 | 123.0286 | 122.8821 | 79.7333 | -123.1247
3349.0156 | 123.1338 | -48.3124 | 74.5651 | -0.15274 | 0.0097989 | 0.071882 | 0.073935 | 0.13057 | -0.0013587 | -0.0064365 | -0.10696 | -0.012117 | 0.06341 | 0.054408 | 0.010831 | -0.015178 | 74.3271 | 74.5834 | 7.5943 | -48.5504 | 74.5789 | -48.5367 | -48.6237 | -46.2616 | 31.2881 | -48.3261 | 74.588 | 74.4095 | -48.5733 | -48.6008 | -0.2243 | -0.31128 | 0.013732 | 122.8958 | -0.23804 | 0.073242 | -0.23804 | -0.26093 | -0.28839 | 0.022888 | 2.0508 | -0.013733 | 0.27466 | -0.15564 | 122.8912 | 122.6395 | 55.9067 | -123.1888 | 122.9004 | 122.7219 | 79.6005 | -123.1659
3350.0156 | 123.1476 | -49.1776 | 73.6359 | -0.10696 | 0.0095853 | 0.067396 | 0.070731 | 0.12843 | -0.0022131 | -0.0064365 | -0.015411 | -0.010835 | 0.063837 | 0.054621 | 0.0076264 | -0.013896 | 73.5626 | 73.7823 | 7.814 | -49.2966 | 73.8647 | -49.2599 | -49.3469 | -46.9711 | 30.7068 | -49.0997 | 73.8373 | 73.6862 | -49.3423 | -49.379 | -0.082398 | -0.16937 | 0.22888 | 122.9599 | -0.11902 | 0.050354 | -0.073242 | -0.16479 | -0.20142 | 0.20142 | 2.2064 | 0.07782 | 0.27924 | 0.050354 | 123.0423 | 122.7402 | 56.9916 | -122.9828 | 123.0148 | 122.8638 | 79.8843 | -123.0148
3351.0156 | 123.1567 | -50.8209 | 72.0337 | -0.17563 | 0.0085171 | 0.071027 | 0.07244 | 0.12715 | -0.00050425 | -0.0079319 | -0.10696 | -0.0095532 | 0.062769 | 0.056117 | 0.0091216 | -0.013469 | 71.9147 | 72.139 | 8.0521 | -50.972 | 72.1207 | -50.9583 | -51.0498 | -48.6465 | 29.3015 | -50.8713 | 72.1252 | 71.9833 | -51.0727 | -51.1093 | -0.13733 | -0.22888 | 0.086976 | 122.9599 | -0.15106 | 0.07782 | -0.11902 | -0.25177 | -0.28839 | 0.091553 | 2.1744 | -0.050354 | 0.23804 | -0.050354 | 122.9416 | 122.7356 | 58.873 | -123.0835 | 122.9462 | 122.8043 | 80.1224 | -123.143
3352.0156 | 123.1201 | -49.8138 | 73.0499 | 0.099029 | 0.010226 | 0.070814 | 0.070731 | 0.12928 | 0.00077755 | -0.0072911 | 0.083771 | -0.012758 | 0.062555 | 0.057185 | 0.0069854 | -0.013255 | 72.9172 | 73.1186 | 10.4507 | -49.9603 | 73.2101 | -49.8779 | -49.9603 | -47.6395 | 30.9265 | -49.8642 | 73.1689 | 73.027 | -50.0244 | -50.0793 | -0.064087 | -0.14648 | 0.16022 | 122.9324 | -0.14648 | 0 | -0.13275 | -0.21057 | -0.2655 | 0.11902 | 2.1744 | -0.050354 | 0.21515 | -0.022888 | 123.024 | 122.731 | 60.2646 | -123.0103 | 122.9828 | 122.8409 | 80.7404 | -123.1293
3353.0156 | 123.1476 | -48.674 | 74.2218 | -0.061188 | 0.0091581 | 0.072736 | 0.070944 | 0.12651 | -0.0019995 | -0.0094273 | 0.022736 | -0.010408 | 0.062982 | 0.056544 | 0.0093354 | -0.012187 | 74.2264 | 74.4415 | 10.9039 | -48.6237 | 74.501 | -48.5733 | -48.6557 | -46.4584 | 31.897 | -48.7564 | 74.4003 | 74.2218 | -48.8251 | -48.9029 | 0.10071 | 0.01831 | 0.27924 | 123.1155 | 0.050354 | 0.032044 | 0.004577 | -0.15106 | -0.22888 | 0.17853 | 2.2156 | -0.082398 | 0.14648 | 0 | 123.175 | 122.9004 | 59.5779 | -122.8775 | 123.0743 | 122.8958 | 80.571 | -123.1247
3354.0156 | 123.1247 | -51.059 | 71.8277 | 0.099029 | 0.011722 | 0.069532 | 0.071372 | 0.12758 | -7.6852e-05 | -0.0060093 | 0.030365 | -0.011262 | 0.063623 | 0.054194 | 0.0082672 | -0.013469 | 71.5027 | 72.0383 | 10.4004 | -51.1368 | 72.02 | -51.059 | -51.1597 | -48.793 | 29.8691 | -51.1185 | 71.9879 | 71.8414 | -51.2466 | -51.3062 | 0 | -0.10071 | 0.19226 | 123.0972 | -0.07782 | 0.022888 | -0.32501 | -0.18768 | -0.24719 | 0.16022 | 2.2659 | -0.059509 | 0.18768 | 0.013733 | 123.0789 | 122.5616 | 61.4594 | -122.9874 | 123.0469 | 122.9004 | 80.928 | -123.1338
3355.0156 | 123.1018 | -49.7726 | 73.1369 | 1.8538 | 0.0095853 | 0.069746 | 0.069449 | 0.12928 | 0.00013675 | -0.0053683 | 0.09903 | -0.012117 | 0.064051 | 0.055689 | 0.01019 | -0.013042 | 72.9126 | 73.1003 | 11.7783 | -49.9558 | 73.1827 | -49.8642 | -49.9558 | -47.5479 | 31.073 | -49.7314 | 73.2605 | 73.1277 | -49.9512 | -50.0198 | -0.091553 | -0.18311 | 0.045776 | 122.8729 | -0.18311 | 0 | -0.2243 | -0.17853 | -0.24719 | 0.1236 | 2.2247 | 0.041199 | 0.28839 | -0.009155 | 122.9553 | 122.6852 | 61.5509 | -123.0927 | 123.0331 | 122.9004 | 80.8456 | -123.1567
3356.0156 | 123.0972 | -50.4089 | 72.4228 | -1.0149 | 0.014285 | 0.068678 | 0.070303 | 0.12993 | 0.0033411 | -0.0066501 | 0.16769 | -0.011903 | 0.062128 | 0.056758 | 0.012112 | -0.01411 | 72.2946 | 72.5143 | 11.8607 | -50.6058 | 72.5098 | -50.5417 | -50.6149 | -48.1659 | 30.5557 | -50.4272 | 72.5143 | 72.4136 | -50.6607 | -50.679 | -0.13275 | -0.20599 | 0.086975 | 122.9233 | -0.19684 | 0.009155 | -0.12817 | -0.25177 | -0.27008 | 0.091552 | 2.243 | -0.01831 | 0.25177 | -0.009156 | 122.9187 | 122.7036 | 62.2696 | -123.0377 | 122.9233 | 122.8226 | 80.9647 | -123.1018
3357.0156 | 123.143 | -51.0269 | 71.8552 | 0.015106 | 0.0091581 | 0.071455 | 0.069235 | 0.12993 | -0.0019995 | -0.0060093 | -0.03067 | -0.012117 | 0.061701 | 0.055049 | 0.0074126 | -0.010478 | 71.7636 | 71.9604 | 12.2223 | -51.1139 | 72.0383 | -51.059 | -51.1688 | -48.7747 | 30.0888 | -51.0635 | 71.9559 | 71.8277 | -51.2421 | -51.2558 | -0.032043 | -0.14191 | 0.1831 | 122.9874 | -0.086975 | 0.054931 | -0.091553 | -0.21515 | -0.22888 | 0.10071 | 2.2522 | -0.036621 | 0.19226 | -0.027466 | 123.0652 | 122.7905 | 63.2492 | -123.024 | 122.9828 | 122.8546 | 81.1157 | -123.111
3358.0156 | 123.1247 | -51.265 | 71.5805 | 0.17532 | 0.012149 | 0.070814 | 0.071799 | 0.1295 | 0.00013675 | -0.0079319 | 0.19821 | -0.0095532 | 0.062555 | 0.058039 | 0.011044 | -0.01176 | 71.4615 | 71.6492 | 12.7991 | -51.4114 | 71.6995 | -51.3565 | -51.4526 | -49.0036 | 29.7729 | -51.2787 | 71.7178 | 71.6217 | -51.4664 | -51.503 | -0.091552 | -0.18768 | 0.11902 | 122.9141 | -0.14648 | 0.041199 | -0.11902 | -0.20142 | -0.23804 | 0.13733 | 2.2614 | -0.013733 | 0.2243 | 0.041199 | 122.9645 | 122.7264 | 64.064 | -123.0331 | 122.9828 | 122.8867 | 81.0379 | -123.0835
3359.0156 | 123.1018 | -50.8255 | 72.052 | 0.060882 | 0.0093717 | 0.0706 | 0.070944 | 0.12886 | -0.0011451 | -0.0079319 | 0.068512 | -0.011262 | 0.062769 | 0.054835 | 0.0097626 | -0.013683 | 71.8002 | 71.9238 | 12.886 | -51.1505 | 72.0703 | -51.0361 | -51.1368 | -48.6374 | 30.1987 | -50.8987 | 72.1298 | 72.0016 | -51.0544 | -51.1047 | -0.21057 | -0.31128 | 0.01831 | 122.7493 | -0.32501 | -0.013733 | -0.25177 | -0.22888 | -0.27924 | 0.07782 | 2.1881 | -0.073243 | 0.20599 | -0.050354 | 122.8958 | 122.6257 | 63.7115 | -123.1888 | 122.9553 | 122.8271 | 81.0242 | -123.1567
3360.0156 | 123.1155 | -50.6927 | 72.0932 | 0.17532 | 0.015567 | 0.068891 | 0.072012 | 0.1295 | 0.0031273 | -0.0028049 | 0.18295 | -0.0093396 | 0.062128 | 0.055476 | 0.011472 | -0.013896 | 72.1664 | 72.3084 | 13.9572 | -50.7477 | 72.3633 | -50.7019 | -50.7889 | -48.3719 | 30.2902 | -50.6561 | 72.3221 | 72.2031 | -50.853 | -50.8896 | -0.009155 | -0.09613 | 0.27008 | 123.0011 | -0.054932 | 0.041198 | 0.073242 | -0.16022 | -0.19684 | 0.22888 | 2.3209 | 0.036621 | 0.23346 | 0.10986 | 123.056 | 122.8592 | 64.65 | -122.8821 | 123.0148 | 122.8958 | 80.983 | -122.9828
3361.0156 | 123.1155 | -49.9329 | 72.9492 | 0.17532 | 0.012149 | 0.069532 | 0.07009 | 0.12629 | -0.00093145 | -0.0055821 | 0.17532 | -0.010408 | 0.064478 | 0.05633 | 0.008908 | -0.011546 | 72.8073 | 72.9721 | 13.9572 | -50.0748 | 73.0545 | -49.9924 | -50.0977 | -47.731 | 30.542 | -49.9649 | 73.0408 | 72.9172 | -50.148 | -50.1846 | -0.05951 | -0.16479 | 0.10528 | 122.905 | -0.14191 | 0.022888 | -0.14191 | -0.21515 | -0.25177 | 0.091552 | 2.2018 | -0.032044 | 0.21973 | -0.032044 | 122.9874 | 122.7402 | 63.8901 | -123.0469 | 122.9736 | 122.85 | 80.4749 | -123.1338
3362.0156 | 123.0881 | -50.235 | 72.6791 | 0.16769 | 0.01578 | 0.068464 | 0.07543 | 0.12843 | 0.0059045 | -0.0045139 | 0.77805 | -0.0089124 | 0.064478 | 0.056971 | 0.010617 | -0.015819 | 72.2076 | 72.29 | 12.0987 | -50.7889 | 72.4731 | -50.6516 | -50.7523 | -48.0011 | 30.3085 | -50.3403 | 72.7936 | 72.6791 | -50.4822 | -50.4913 | -0.41656 | -0.51727 | -0.20599 | 122.525 | -0.55389 | -0.036621 | -0.4715 | -0.24719 | -0.25635 | 0.11444 | 2.2339 | -0.10529 | 0.15106 | 0 | 122.7081 | 122.4426 | 62.3337 | -123.4314 | 123.0286 | 122.9141 | 80.5435 | -123.1705
3363.0156 | 123.1567 | -49.0173 | 73.8098 | 0.14481 | 0.014712 | 0.071455 | 0.066885 | 0.12971 | 0.0014185 | -0.0047275 | 0.16769 | -0.0099806 | 0.062982 | 0.055049 | 0.011258 | -0.013683 | 73.526 | 73.6725 | 11.3342 | -49.2599 | 73.7915 | -49.2462 | -49.3515 | -46.7972 | 31.3522 | -49.0311 | 73.9151 | 73.8098 | -49.2691 | -49.2599 | -0.22888 | -0.33417 | -0.01831 | 122.6898 | -0.24262 | 0.091552 | -0.28381 | -0.25177 | -0.24262 | 0.10529 | 2.2202 | -0.013733 | 0.22888 | 0 | 122.8088 | 122.5433 | 60.3516 | -123.1613 | 122.9324 | 122.8271 | 80.3696 | -123.0698
3364.0156 | 123.0286 | -50.2167 | 72.7066 | 0.17532 | 0.016421 | 0.068891 | 0.074362 | 0.12629 | 0.0012047 | -0.0047275 | 1.1977 | -0.0082716 | 0.064905 | 0.057398 | 0.0097626 | -0.012614 | 72.496 | 72.5647 | 10.5423 | -50.4227 | 72.8119 | -50.3357 | -50.4456 | -48.0057 | 30.4138 | -50.3128 | 72.789 | 72.6791 | -50.4593 | -50.4639 | -0.11902 | -0.22888 | 0.10529 | 122.7814 | -0.20599 | 0.022889 | -0.21057 | -0.24262 | -0.24719 | 0.082397 | 2.211 | -0.09613 | 0.15106 | -0.027466 | 123.0286 | 122.7127 | 60.759 | -123.1522 | 123.0057 | 122.8958 | 80.6305 | -123.1705
3365.0156 | 123.1796 | -50.7568 | 72.1115 | 0.19058 | 0.016421 | 0.070814 | 0.069449 | 0.12822 | 0.00056395 | -0.0066501 | 0.24399 | -0.011049 | 0.062982 | 0.058253 | 0.011685 | -0.012828 | 72.4548 | 72.6105 | 11.673 | -50.441 | 72.67 | -50.4044 | -50.5051 | -48.4314 | 29.8737 | -51.1047 | 72.3358 | 72.171 | -50.9308 | -50.9857 | 0.35248 | 0.25177 | 0.55847 | 123.3673 | 0.31586 | 0.064087 | 0.34332 | -0.17395 | -0.22888 | 0.2243 | 2.3254 | -0.3479 | -0.11902 | 0.05951 | 123.4268 | 123.2117 | 62.4298 | -122.6166 | 123.0927 | 122.9279 | 80.6305 | -123.0972
3366.0156 | 123.0469 | -49.8825 | 73.0316 | -0.03067 | 0.018344 | 0.069532 | 0.073294 | 0.12843 | 0.0048363 | -0.0043003 | 0.076141 | -0.0086988 | 0.065759 | 0.057826 | 0.008908 | -0.015605 | 72.8714 | 72.963 | 12.2726 | -50.029 | 73.2147 | -49.9237 | -50.029 | -47.6257 | 30.5649 | -49.9969 | 73.2101 | 73.0682 | -50.0839 | -50.1389 | -0.041199 | -0.14649 | 0.18311 | 122.8455 | -0.14649 | 0 | -0.16022 | -0.20142 | -0.25635 | 0.17853 | 2.2568 | -0.11444 | 0.14191 | 0.036621 | 123.0972 | 122.7539 | 62.1552 | -123.0606 | 123.0927 | 122.9507 | 80.4474 | -123.1705
3367.0156 | 123.1293 | -50.116 | 72.757 | 0.19058 | 0.015994 | 0.070814 | 0.069876 | 0.12758 | 0.0014185 | -0.0049411 | 0.29739 | -0.0099806 | 0.063623 | 0.055903 | 0.012326 | -0.011333 | 72.4823 | 72.6654 | 11.4258 | -50.3677 | 72.7295 | -50.3311 | -50.4181 | -47.8592 | 30.4733 | -50.1022 | 72.8394 | 72.7753 | -50.3128 | -50.3311 | -0.21515 | -0.30212 | -0.027466 | 122.7814 | -0.25177 | 0.050354 | -0.27466 | -0.19684 | -0.21515 | 0.082397 | 2.2568 | 0.013733 | 0.22888 | 0.018311 | 122.8455 | 122.5983 | 61.5417 | -123.175 | 122.9553 | 122.8912 | 80.5893 | -123.0881
3368.0156 | 123.0469 | -50.1389 | 72.8165 | 0.060882 | 0.020053 | 0.070387 | 0.072012 | 0.13163 | 0.0039819 | -0.0049411 | 0.13718 | -0.0084852 | 0.064264 | 0.058253 | 0.012967 | -0.01411 | 72.6334 | 72.7203 | 9.3246 | -50.2579 | 73.0087 | -50.1801 | -50.2762 | -47.9507 | 30.2444 | -50.2029 | 72.8943 | 72.8256 | -50.3448 | -50.3769 | -0.041199 | -0.13733 | 0.19226 | 122.8592 | -0.11902 | 0.01831 | -0.1831 | -0.20599 | -0.23804 | 0.07782 | 2.1881 | -0.064087 | 0.17395 | 0.009156 | 123.1476 | 122.7722 | 59.4635 | -123.0927 | 123.0331 | 122.9645 | 80.3833 | -123.1934
3369.0156 | 123.111 | -50.386 | 72.4869 | 0.14481 | 0.011081 | 0.073377 | 0.070517 | 0.128 | -0.0062721 | -0.0077183 | 0.16006 | -0.009126 | 0.064264 | 0.056758 | 0.0093354 | -0.010478 | 72.3633 | 72.5464 | 9.2148 | -50.5234 | 72.6654 | -50.4227 | -50.5234 | -48.1476 | 30.0934 | -50.4318 | 72.6105 | 72.5052 | -50.6058 | -50.647 | -0.036621 | -0.13733 | 0.17853 | 122.9324 | -0.13733 | 0 | -0.1236 | -0.21973 | -0.26093 | 0.1236 | 2.2385 | -0.045777 | 0.21515 | 0.018311 | 123.0515 | 122.7493 | 59.6008 | -123.0103 | 122.9965 | 122.8912 | 80.4794 | -123.1339
3370.0156 | 123.0194 | -50.3174 | 72.5922 | 0.022736 | 0.019412 | 0.071668 | 0.072867 | 0.12971 | 0.0048363 | -0.0066501 | 0.053253 | -0.0082716 | 0.065332 | 0.055262 | 0.01254 | -0.014537 | 72.4594 | 72.5418 | 8.2489 | -50.4547 | 72.7478 | -50.3723 | -50.4822 | -48.1522 | 30.0659 | -50.4181 | 72.7341 | 72.6059 | -50.5234 | -50.5554 | -0.054931 | -0.16479 | 0.15564 | 122.8592 | -0.13733 | 0.027466 | -0.13275 | -0.20599 | -0.23804 | 0.14191 | 2.1652 | -0.10071 | 0.13733 | 0.013733 | 123.0652 | 122.7768 | 58.5663 | -123.0743 | 123.0515 | 122.9233 | 80.3833 | -123.1476
3371.0156 | 123.0423 | -50.8987 | 72.0886 | 0.12955 | 0.01813 | 0.069532 | 0.073081 | 0.12629 | 0.0031273 | -0.0057957 | 0.13718 | -0.0084852 | 0.065759 | 0.059748 | 0.011258 | -0.01176 | 71.9879 | 72.0291 | 7.4799 | -51.0361 | 72.2946 | -50.9262 | -51.004 | -48.6969 | 29.5029 | -51.0544 | 72.1252 | 72.084 | -51.091 | -51.1047 | -0.027465 | -0.10528 | 0.20599 | 122.9279 | -0.13733 | -0.032044 | -0.10071 | -0.19226 | -0.20599 | 0.036621 | 2.2018 | -0.15564 | 0.050354 | -0.004578 | 123.1934 | 122.8867 | 58.3786 | -123.0927 | 123.024 | 122.9828 | 80.4016 | -123.1934
3372.0156 | 123.0698 | -50.2762 | 72.6654 | -0.053558 | 0.019198 | 0.069746 | 0.076071 | 0.12886 | 0.0027001 | -0.0053683 | -0.038299 | -0.0078442 | 0.065546 | 0.057185 | 0.010831 | -0.013896 | 72.3862 | 72.5052 | 8.2626 | -50.5325 | 72.6562 | -50.5096 | -50.56 | -48.024 | 29.9789 | -50.3311 | 72.7478 | 72.67 | -50.4868 | -50.5234 | -0.23346 | -0.28381 | -0.009155 | 122.7814 | -0.25635 | 0.027466 | -0.27924 | -0.21057 | -0.24719 | 0.082398 | 2.2522 | -0.054932 | 0.19226 | 0.004578 | 122.9324 | 122.6624 | 58.5388 | -123.2254 | 123.024 | 122.9462 | 80.2551 | -123.1888
3373.0156 | 123.0148 | -49.0906 | 73.8235 | 0.068512 | 0.017276 | 0.067396 | 0.069449 | 0.128 | 0.0014185 | -0.0028049 | 0.037995 | -0.0093396 | 0.066828 | 0.05633 | 0.010403 | -0.012187 | 73.4619 | 73.5764 | 7.4478 | -49.4247 | 73.8373 | -49.3378 | -49.4202 | -46.8796 | 30.9998 | -49.2233 | 73.9929 | 73.9243 | -49.2645 | -49.3149 | -0.24719 | -0.32959 | 0.013733 | 122.6669 | -0.33417 | -0.004578 | -0.36163 | -0.17395 | -0.2243 | 0.16937 | 2.211 | -0.13275 | 0.091552 | 0.10071 | 122.9279 | 122.5525 | 56.5384 | -123.2437 | 123.0835 | 123.0148 | 80.0903 | -123.1384
3374.0156 | 123.111 | -48.9212 | 73.9288 | -1.4879 | 0.01279 | 0.072523 | 0.068594 | 0.12928 | -0.0043495 | -0.0032321 | 0.26688 | -0.010408 | 0.064264 | 0.055476 | 0.010831 | -0.010905 | 73.7228 | 73.9792 | 7.7911 | -49.1272 | 74.0067 | -49.054 | -49.1455 | -46.6782 | 31.2286 | -48.967 | 74.0341 | 73.9838 | -49.1455 | -49.173 | -0.13275 | -0.2243 | 0.07782 | 122.9004 | -0.20599 | 0.018311 | -0.20599 | -0.2243 | -0.25177 | 0.10529 | 2.243 | -0.045776 | 0.20599 | 0.054932 | 122.9279 | 122.644 | 56.7123 | -123.0743 | 122.9553 | 122.905 | 80.1498 | -123.1018
3375.0625 | 123.0331 | -49.2004 | 73.7457 | -0.23666 | 0.013644 | 0.072736 | 0.073294 | 0.12693 | -0.0030677 | -0.0066501 | -0.13748 | -0.0084852 | 0.063837 | 0.055262 | 0.0084808 | -0.012187 | 73.5855 | 73.7503 | 7.8369 | -49.2737 | 73.9655 | -49.1959 | -49.2828 | -47.0032 | 30.9723 | -49.2416 | 73.8876 | 73.7869 | -49.4156 | -49.4385 | 0.004577 | -0.082398 | 0.21973 | 122.9507 | -0.073243 | 0.009155 | -0.16022 | -0.21515 | -0.23804 | 0.14191 | 2.1973 | -0.041199 | 0.19684 | 0.041198 | 123.1659 | 122.7859 | 57.0374 | -123.0286 | 123.0881 | 122.9874 | 80.1727 | -123.1842
3376.0156 | 123.0606 | -49.2416 | 73.6359 | -0.24429 | 0.01813 | 0.070173 | 0.072867 | 0.12736 | 0.00099115 | -0.0066501 | -0.168 | -0.009126 | 0.067041 | 0.056758 | 0.0086944 | -0.014323 | 73.4528 | 73.6771 | 7.2098 | -49.2828 | 73.9105 | -49.2416 | -49.3286 | -46.9482 | 30.9357 | -49.2416 | 73.9105 | 73.7961 | -49.3423 | -49.4247 | 0 | -0.086975 | 0.27466 | 122.9187 | -0.041199 | 0.045776 | -0.1831 | -0.10071 | -0.18311 | 0.27466 | 2.2934 | 0 | 0.18311 | 0.16022 | 123.1522 | 122.6944 | 56.4514 | -122.9645 | 123.1522 | 123.0377 | 80.1773 | -123.0606
3377.0156 | 123.0286 | -50.116 | 72.8485 | 0.068512 | 0.019198 | 0.069746 | 0.070944 | 0.12886 | 0.0020593 | -0.0070773 | 0.12955 | -0.0093396 | 0.067682 | 0.055262 | 0.0097626 | -0.013683 | 72.6013 | 72.702 | 7.8781 | -50.2991 | 72.9401 | -50.1938 | -50.3082 | -47.9553 | 30.011 | -50.2853 | 72.963 | 72.8302 | -50.3265 | -50.3769 | -0.07782 | -0.19226 | 0.091552 | 122.818 | -0.18311 | 0.009156 | -0.24719 | -0.21057 | -0.26093 | 0.11444 | 2.1606 | -0.16937 | 0.091553 | -0.018311 | 123.056 | 122.7173 | 57.9941 | -123.1567 | 123.0789 | 122.9462 | 80.127 | -123.2254
3378.0156 | 123.0377 | -49.5117 | 73.4436 | -0.053558 | 0.018771 | 0.068464 | 0.075217 | 0.13078 | 0.00056395 | -0.0075047 | -0.061188 | -0.0099806 | 0.067041 | 0.058467 | 0.0097626 | -0.013042 | 73.1689 | 73.3521 | 7.5073 | -49.6765 | 73.4894 | -49.649 | -49.7452 | -47.2961 | 30.7159 | -49.5895 | 73.5031 | 73.4161 | -49.7543 | -49.7589 | -0.13733 | -0.23346 | 0.045776 | 122.8638 | -0.16479 | 0.068664 | -0.27466 | -0.24261 | -0.24719 | 0.059509 | 2.2156 | -0.07782 | 0.16937 | -0.027466 | 123.0011 | 122.6807 | 57.019 | -123.1888 | 123.0148 | 122.9279 | 80.2277 | -123.2025
3379.0156 | 123.1018 | -49.1455 | 73.7732 | 0.12192 | 0.013431 | 0.071027 | 0.070517 | 0.12993 | -0.0064857 | -0.0070773 | 0.30502 | -0.010408 | 0.06341 | 0.055903 | 0.0063446 | -0.010051 | 73.5718 | 73.7823 | 7.2189 | -49.324 | 73.8556 | -49.2325 | -49.3378 | -46.9574 | 31.0684 | -49.2142 | 73.8098 | 73.7137 | -49.3973 | -49.4202 | -0.086975 | -0.19226 | 0.082398 | 122.9279 | -0.17853 | 0.013733 | -0.20142 | -0.25177 | -0.27466 | 0.036621 | 2.1881 | -0.068664 | 0.20599 | -0.059509 | 123.0011 | 122.7173 | 56.3644 | -123.111 | 122.9553 | 122.8592 | 80.2139 | -123.1934
3380.0156 | 123.0881 | -49.6216 | 73.2925 | -0.20615 | 0.01514 | 0.069105 | 0.073721 | 0.12971 | 0.0027001 | -0.0079319 | -0.25192 | -0.0082716 | 0.065332 | 0.057612 | 0.0097626 | -0.013683 | 73.0957 | 73.2285 | 7.3471 | -49.7772 | 73.4207 | -49.7543 | -49.8459 | -47.4014 | 30.629 | -49.6628 | 73.4207 | 73.32 | -49.8459 | -49.8779 | -0.13275 | -0.2243 | 0.12817 | 122.85 | -0.15564 | 0.068664 | -0.19684 | -0.2243 | -0.25635 | 0.12817 | 2.2202 | -0.041199 | 0.21515 | 0.027465 | 123.0423 | 122.7173 | 56.9687 | -123.1384 | 123.0423 | 122.9416 | 80.2505 | -123.1705
3381.0156 | 123.0469 | -49.823 | 73.1323 | 0.015106 | 0.017917 | 0.0706 | 0.074362 | 0.12993 | 0.0024865 | -0.0053683 | 0.0074766 | -0.010621 | 0.0664 | 0.057185 | 0.010831 | -0.013896 | 73.0545 | 73.1781 | 7.4707 | -49.9054 | 73.3154 | -49.8459 | -49.9603 | -47.5845 | 30.5054 | -49.9603 | 73.2193 | 73.114 | -50.029 | -50.0702 | -0.022888 | -0.13733 | 0.18311 | 123.0011 | -0.082398 | 0.054931 | -0.07782 | -0.20599 | -0.24719 | 0.086975 | 2.2385 | -0.13733 | 0.10986 | -0.01831 | 123.1384 | 122.8775 | 57.2937 | -123.0927 | 123.0423 | 122.937 | 80.3284 | -123.2025
3382.0156 | 123.0698 | -49.942 | 72.9996 | -0.19089 | 0.016421 | 0.069532 | 0.073081 | 0.12693 | 0.0016321 | -0.0047275 | -0.061188 | -0.010621 | 0.0664 | 0.055903 | 0.010403 | -0.012401 | 72.8668 | 73.0453 | 7.2144 | -49.9786 | 73.1781 | -49.942 | -50.0473 | -47.6303 | 30.3818 | -49.9466 | 73.1552 | 73.0774 | -50.0977 | -50.1434 | 0 | -0.10529 | 0.17853 | 122.9874 | -0.036621 | 0.068664 | -0.13275 | -0.15564 | -0.20142 | 0.15564 | 2.3117 | -0.004577 | 0.19684 | 0.07782 | 123.1201 | 122.8088 | 57.1564 | -123.0469 | 123.0972 | 123.0194 | 80.3238 | -123.143
3383.0156 | 123.024 | -49.6719 | 73.2651 | -0.0383 | 0.019198 | 0.068891 | 0.073721 | 0.12864 | 0.00077755 | -0.0062229 | 0.015106 | -0.0093396 | 0.066828 | 0.056758 | 0.011685 | -0.013469 | 73.2056 | 73.3658 | 7.4707 | -49.6353 | 73.5168 | -49.585 | -49.6948 | -47.3465 | 30.5466 | -49.6216 | 73.4848 | 73.3658 | -49.7955 | -49.8596 | 0.086975 | -0.022888 | 0.25177 | 123.0377 | 0.036621 | 0.059509 | -0.05951 | -0.1236 | -0.18768 | 0.21973 | 2.3254 | 0.050354 | 0.23804 | 0.10071 | 123.1888 | 122.8775 | 57.1426 | -122.9599 | 123.1567 | 123.0377 | 80.2185 | -123.1247
3384.0156 | 123.0881 | -49.7131 | 73.2697 | 0.14481 | 0.016849 | 0.071241 | 0.070944 | 0.128 | 0.00077755 | -0.0066501 | 0.24399 | -0.010408 | 0.065119 | 0.056117 | 0.0099762 | -0.012187 | 72.9492 | 73.1049 | 7.3883 | -49.8917 | 73.3292 | -49.8047 | -49.8734 | -47.4792 | 30.4779 | -49.7452 | 73.3063 | 73.2376 | -49.9329 | -49.9374 | -0.091552 | -0.16022 | 0.05951 | 122.818 | -0.17853 | -0.018311 | -0.32043 | -0.21973 | -0.2243 | 0.036621 | 2.2339 | -0.032043 | 0.19226 | -0.032043 | 123.0423 | 122.6624 | 57.1014 | -123.143 | 123.0194 | 122.9507 | 80.191 | -123.2071
3385.0156 | 123.0789 | -49.3973 | 73.5489 | 0.76279 | 0.019412 | 0.072736 | 0.073935 | 0.13228 | 0.00099115 | -0.0057957 | -0.0077819 | -0.008058 | 0.066828 | 0.055262 | 0.0093354 | -0.012614 | 73.2376 | 73.4436 | 7.4753 | -49.5575 | 73.6084 | -49.5026 | -49.6124 | -47.2046 | 30.6656 | -49.6719 | 73.5535 | 73.4894 | -49.6902 | -49.7223 | -0.10529 | -0.21515 | 0.059509 | 122.8409 | -0.16022 | 0.054932 | -0.31128 | -0.29297 | -0.32501 | 0.004578 | 2.1927 | -0.27466 | 0.050354 | -0.059509 | 123.0057 | 122.6349 | 56.8726 | -123.1613 | 122.9507 | 122.8867 | 80.0629 | -123.2712
3386.0156 | 123.0743 | -48.7839 | 74.0845 | -0.21378 | 0.012149 | 0.069532 | 0.071585 | 0.13142 | -0.0015723 | -0.0066501 | -0.14511 | -0.010408 | 0.067255 | 0.05633 | 0.01019 | -0.011974 | 73.851 | 73.9792 | 8.3954 | -48.999 | 74.2447 | -48.9075 | -49.0128 | -46.5958 | 31.4117 | -48.8708 | 74.2676 | 74.231 | -48.9578 | -49.0082 | -0.1236 | -0.22888 | 0.16022 | 122.7631 | -0.21515 | 0.013733 | -0.23346 | -0.17395 | -0.2243 | 0.1831 | 2.1881 | -0.086975 | 0.13733 | 0.14648 | 123.0286 | 122.6349 | 57.1793 | -123.0972 | 123.0515 | 123.0148 | 80.1956 | -123.0927
3387.0156 | 123.0606 | -49.585 | 73.3429 | -0.12985 | 0.020053 | 0.069959 | 0.073935 | 0.13014 | 0.0016321 | -0.0060093 | -0.015411 | -0.011262 | 0.065759 | 0.057826 | 0.0086944 | -0.011974 | 73.1186 | 73.2742 | 8.4137 | -49.7452 | 73.4253 | -49.7086 | -49.791 | -47.3511 | 30.7617 | -49.6445 | 73.439 | 73.3749 | -49.8138 | -49.8367 | -0.1236 | -0.20599 | 0.082397 | 122.8592 | -0.16022 | 0.045777 | -0.22431 | -0.22888 | -0.25177 | 0.09613 | 2.2339 | -0.059509 | 0.19226 | 0.032043 | 123.0103 | 122.7036 | 57.9987 | -123.1339 | 123.024 | 122.9599 | 80.3467 | -123.1796
3388.0156 | 123.024 | -49.2325 | 73.7457 | 0.75516 | 0.015994 | 0.073591 | 0.074149 | 0.1295 | -0.0015723 | -0.0081455 | -0.12222 | -0.011049 | 0.064051 | 0.055262 | 0.0084808 | -0.012614 | 73.3749 | 73.5168 | 8.9676 | -49.4568 | 73.764 | -49.3652 | -49.4705 | -47.0398 | 30.9128 | -49.2599 | 73.7961 | 73.7412 | -49.4431 | -49.4705 | -0.13275 | -0.23804 | 0.01831 | 122.7493 | -0.2243 | 0.013733 | -0.37079 | -0.21057 | -0.23804 | 0.050354 | 2.1927 | -0.027466 | 0.21057 | -0.004578 | 122.9965 | 122.6074 | 58.2001 | -123.2162 | 123.0286 | 122.9736 | 80.1453 | -123.2162
3389.0156 | 123.0789 | -52.5238 | 70.372 | -0.00015269 | 0.015994 | 0.069959 | 0.073935 | 0.13014 | 0.0044091 | -0.0066501 | -0.061188 | -0.0089124 | 0.067255 | 0.057826 | 0.0086944 | -0.010905 | 70.3812 | 70.5597 | 7.8964 | -52.4826 | 70.6879 | -52.4094 | -52.5192 | -50.2075 | 28.0655 | -52.7069 | 70.5185 | 70.4453 | -52.7344 | -52.7847 | 0.11444 | 0.004578 | 0.31586 | 123.0835 | 0.041199 | 0.036621 | 0.009156 | -0.21057 | -0.26093 | 0.14648 | 2.3163 | -0.18311 | 0.07782 | 0.073242 | 123.2117 | 122.905 | 60.4202 | -122.8912 | 123.0423 | 122.9691 | 80.5893 | -123.1567
3390.0156 | 123.0331 | -49.7269 | 73.2834 | -0.20615 | 0.012362 | 0.072523 | 0.071799 | 0.12822 | -0.0041357 | -0.0083591 | 0.27451 | -0.010621 | 0.065119 | 0.057612 | 0.0086944 | -0.014964 | 72.9767 | 73.1415 | 8.5693 | -49.8779 | 73.3658 | -49.7772 | -49.8276 | -47.4609 | 30.4596 | -49.855 | 73.3658 | 73.3063 | -49.9283 | -49.9329 | -0.050354 | -0.10071 | 0.082398 | 122.8683 | -0.15106 | -0.050354 | -0.3067 | -0.20142 | -0.20599 | 0.082398 | 2.2659 | -0.12817 | 0.077819 | 0.022888 | 123.0927 | 122.7036 | 58.2962 | -123.111 | 123.0927 | 123.0331 | 80.1865 | -123.2162
3391.0156 | 123.1018 | -49.9558 | 72.9858 | -0.12985 | 0.020907 | 0.070814 | 0.072653 | 0.13163 | 0.00013675 | -0.0049411 | -0.061188 | -0.009126 | 0.067255 | 0.056117 | 0.011899 | -0.012187 | 72.7844 | 72.9355 | 9.3796 | -50.0107 | 73.1094 | -49.9924 | -50.116 | -47.6578 | 30.2719 | -50.0153 | 73.0774 | 73.0133 | -50.1846 | -50.2075 | -0.036621 | -0.16022 | 0.1236 | 122.8912 | -0.054931 | 0.10529 | -0.20142 | -0.22888 | -0.25177 | 0.091553 | 2.298 | -0.059509 | 0.19226 | 0.027466 | 123.0652 | 122.7402 | 59.3353 | -123.1018 | 123.0331 | 122.9691 | 80.2277 | -123.1934
3392.0156 | 123.0698 | -50.0519 | 72.8943 | 0.045624 | 0.014285 | 0.071455 | 0.074149 | 0.12864 | -0.0032813 | -0.0070773 | -0.168 | -0.0078442 | 0.067041 | 0.057185 | 0.0084808 | -0.011546 | 72.6974 | 72.8714 | 10.8261 | -50.1434 | 73.0865 | -50.0885 | -50.1984 | -47.8546 | 29.9744 | -50.1755 | 72.9996 | 72.9126 | -50.2579 | -50.2899 | -0.036621 | -0.14648 | 0.19226 | 122.9233 | -0.091553 | 0.054931 | -0.19684 | -0.20599 | -0.23804 | 0.10529 | 2.1973 | -0.1236 | 0.11444 | 0.018311 | 123.1384 | 122.7493 | 60.878 | -123.0927 | 123.0515 | 122.9645 | 80.0262 | -123.1842
3393.0156 | 123.0377 | -50.2853 | 72.6517 | -0.16037 | 0.016421 | 0.071027 | 0.075217 | 0.12971 | 0.00099115 | -0.0072911 | -0.091705 | -0.009126 | 0.065973 | 0.056117 | 0.01019 | -0.011546 | 72.4136 | 72.5739 | 11.586 | -50.4456 | 72.7478 | -50.386 | -50.4776 | -48.0377 | 29.7546 | -50.4456 | 72.6883 | 72.5967 | -50.5371 | -50.5783 | -0.10071 | -0.19226 | 0.096131 | 122.8592 | -0.16022 | 0.032043 | -0.23804 | -0.25177 | -0.29297 | 0.036621 | 2.2476 | -0.16022 | 0.13275 | -0.054931 | 123.0331 | 122.699 | 61.8713 | -123.1293 | 122.9736 | 122.8821 | 80.04 | -123.23
3394.0156 | 123.024 | -50.6516 | 72.3084 | -0.22141 | 0.011935 | 0.069746 | 0.074149 | 0.12864 | -0.00071785 | -0.0060093 | -0.16037 | -0.012117 | 0.065546 | 0.058467 | 0.0080536 | -0.011119 | 71.933 | 72.3862 | 10.1257 | -50.7294 | 72.5052 | -50.647 | -50.7523 | -48.3994 | 29.425 | -50.853 | 72.4548 | 72.3267 | -50.8804 | -50.9033 | 0.004577 | -0.10071 | 0.19684 | 123.0377 | -0.07782 | 0.022888 | -0.37537 | -0.22888 | -0.25177 | 0.14648 | 2.2522 | -0.20142 | 0.050354 | 0.01831 | 123.1567 | 122.5845 | 60.7773 | -123.0606 | 123.1064 | 122.9782 | 80.0766 | -123.2117
3395.0156 | 123.056 | -50.592 | 72.4091 | -0.068817 | 0.017917 | 0.070814 | 0.073508 | 0.13142 | 0.00077755 | -0.0064365 | -0.00015237 | -0.007417 | 0.0664 | 0.058467 | 0.012326 | -0.013896 | 72.0245 | 72.2076 | 11.1877 | -50.8026 | 72.3816 | -50.7477 | -50.8621 | -48.3215 | 29.4525 | -50.7797 | 72.3953 | 72.3541 | -50.8026 | -50.8484 | -0.15564 | -0.27008 | -0.027466 | 122.7997 | -0.21057 | 0.05951 | -0.38452 | -0.21057 | -0.25635 | -0.013733 | 2.2705 | -0.18768 | 0.068665 | -0.054932 | 122.9736 | 122.6166 | 61.7798 | -123.2712 | 122.9874 | 122.9462 | 80.0446 | -123.2574
3396.0156 | 123.0469 | -50.1892 | 72.7753 | -0.17563 | 0.01279 | 0.071882 | 0.071372 | 0.13185 | -0.0041357 | -0.0087863 | -0.16037 | -0.0084852 | 0.065546 | 0.056758 | 0.01019 | -0.012187 | 72.4823 | 72.67 | 12.7762 | -50.3174 | 72.9034 | -50.2533 | -50.3403 | -48.0194 | 29.9469 | -50.3403 | 72.8851 | 72.8027 | -50.3815 | -50.4089 | -0.064087 | -0.15106 | 0.12817 | 122.8592 | -0.12817 | 0.022888 | -0.29297 | -0.19226 | -0.21973 | 0.10986 | 2.1698 | -0.15106 | 0.068665 | 0.027465 | 123.0927 | 122.6715 | 62.9654 | -123.1155 | 123.0743 | 122.9919 | 80.1361 | -123.1842
3397.0156 | 123.0698 | -49.411 | 73.5535 | -0.13748 | 0.017062 | 0.071027 | 0.073721 | 0.12864 | 0.0012047 | -0.0070773 | 0.045624 | -0.005708 | 0.066828 | 0.056117 | 0.012326 | -0.013896 | 73.1506 | 73.3429 | 12.5839 | -49.5438 | 73.5489 | -49.5529 | -49.6262 | -47.2183 | 30.4871 | -49.4659 | 73.5901 | 73.558 | -49.6445 | -49.6582 | -0.14191 | -0.21515 | -0.004578 | 122.7539 | -0.13275 | 0.082398 | -0.40283 | -0.23346 | -0.24719 | 0.036621 | 2.1927 | -0.054931 | 0.19226 | 0.004577 | 122.9599 | 122.5616 | 61.9949 | -123.1796 | 123.0011 | 122.9691 | 79.8981 | -123.2117
3398.0156 | 123.0652 | -49.6307 | 73.32 | 0.47287 | 0.013431 | 0.071241 | 0.071372 | 0.12886 | -0.0037085 | -0.0064365 | -0.099335 | -0.0099806 | 0.065759 | 0.054194 | 0.0082672 | -0.013042 | 73.1094 | 73.2285 | 13.06 | -49.7177 | 73.5077 | -49.649 | -49.7543 | -47.3511 | 30.2765 | -49.7223 | 73.4756 | 73.407 | -49.8001 | -49.8184 | -0.018311 | -0.1236 | 0.18768 | 122.8592 | -0.086975 | 0.036621 | -0.21057 | -0.16937 | -0.18768 | 0.15564 | 2.2797 | -0.091553 | 0.09613 | 0.086975 | 123.1384 | 122.7402 | 62.6907 | -123.0743 | 123.1064 | 123.0377 | 79.9072 | -123.1384
3399.0156 | 123.0698 | -49.3195 | 73.6221 | -0.19089 | 0.014071 | 0.068891 | 0.07479 | 0.12928 | -0.00093145 | -0.0040867 | -0.168 | -0.0097668 | 0.067255 | 0.059107 | 0.011044 | -0.013255 | 73.4756 | 73.6176 | 12.3734 | -49.3973 | 73.7915 | -49.3607 | -49.4522 | -47.0123 | 30.4962 | -49.4019 | 73.7137 | 73.645 | -49.5209 | -49.53 | -0.041199 | -0.13275 | 0.16937 | 122.937 | -0.07782 | 0.054931 | -0.14648 | -0.20142 | -0.21057 | 0.091553 | 2.3071 | -0.082397 | 0.12817 | 0.022889 | 123.111 | 122.7951 | 61.6928 | -123.0743 | 123.0331 | 122.9645 | 79.8157 | -123.1522
3400.0156 | 123.0011 | -50.0793 | 72.908 | -0.23666 | 0.011508 | 0.071027 | 0.072867 | 0.13014 | -0.0017859 | -0.0068637 | -0.16037 | -0.0084852 | 0.062982 | 0.058039 | 0.0099762 | -0.0098374 | 72.7478 | 72.9721 | 14.4974 | -50.0061 | 73.1873 | -49.9741 | -50.0381 | -47.9553 | 29.8325 | -50.3815 | 72.9996 | 72.8851 | -50.2853 | -50.3403 | 0.10529 | 0.041199 | 0.27924 | 123.0515 | 0.073242 | 0.032043 | -0.16022 | -0.20599 | -0.26093 | 0.091553 | 2.124 | -0.30212 | -0.041199 | -0.022888 | 123.2666 | 122.8271 | 64.5767 | -122.9462 | 123.0789 | 122.9645 | 79.9118 | -123.2483
3401.0156 | 123.0927 | -50.1434 | 72.7386 | -0.21378 | 0.014285 | 0.069532 | 0.072012 | 0.12993 | 0.0031273 | -0.0070773 | -0.15274 | -0.0097668 | 0.067041 | 0.055689 | 0.01019 | -0.012828 | 72.5647 | 72.7478 | 14.621 | -50.267 | 72.9446 | -50.2304 | -50.3357 | -47.9599 | 29.6448 | -50.592 | 72.8073 | 72.7615 | -50.386 | -50.3586 | -0.086975 | -0.19226 | 0.20599 | 122.8912 | -0.1236 | 0.068664 | -0.17395 | -0.24261 | -0.21515 | 0.068665 | 2.1835 | -0.44861 | -0.23346 | 0.022889 | 123.0881 | 122.7081 | 64.7644 | -123.0743 | 122.9507 | 122.905 | 79.7882 | -123.0972
3402.0156 | 123.0286 | -49.91 | 73.0728 | -0.25955 | 0.014285 | 0.071241 | 0.074362 | 0.128 | -0.0030677 | -0.010709 | -0.18326 | -0.0093396 | 0.067255 | 0.056971 | 0.00784 | -0.011546 | 72.8073 | 72.8622 | 16.6031 | -50.0565 | 73.1277 | -50.0473 | -50.1434 | -47.7036 | 30.0064 | -50.2441 | 73.082 | 72.995 | -50.1572 | -50.1617 | -0.13733 | -0.23346 | 0.054932 | 122.7722 | -0.14648 | 0.086975 | -0.2655 | -0.24719 | -0.25177 | 0.009155 | 2.2064 | -0.33417 | -0.082398 | -0.07782 | 123.0377 | 122.7173 | 66.5131 | -123.2162 | 122.9919 | 122.905 | 79.9164 | -123.2346
3403.0156 | 123.0743 | -50.0198 | 72.963 | -0.20615 | 0.015567 | 0.069319 | 0.074149 | 0.13057 | 0.0012047 | -0.0062229 | -0.12985 | -0.011049 | 0.065546 | 0.055689 | 0.0093354 | -0.013255 | 72.6791 | 72.8439 | 15.6555 | -50.2029 | 73.0408 | -50.148 | -50.2487 | -47.699 | 30.043 | -50.0977 | 72.9996 | 72.9126 | -50.2533 | -50.2808 | -0.12817 | -0.22888 | 0.077819 | 122.8638 | -0.18311 | 0.045776 | -0.28381 | -0.23346 | -0.26093 | 0.036621 | 2.3209 | -0.07782 | 0.18311 | -0.050354 | 123.0606 | 122.699 | 65.6754 | -123.2117 | 123.0194 | 122.9324 | 80.0629 | -123.2437
3404.0156 | 123.056 | -50.3403 | 72.583 | -0.23666 | 0.011722 | 0.072736 | 0.071158 | 0.13078 | -0.0034949 | -0.0092137 | -0.10696 | -0.012758 | 0.064905 | 0.054621 | 0.010617 | -0.011974 | 72.2672 | 72.496 | 17.3492 | -50.5417 | 72.6059 | -50.4868 | -50.5829 | -48.0011 | 29.8004 | -50.5096 | 72.6654 | 72.5967 | -50.5463 | -50.5783 | -0.14648 | -0.24262 | 0.022888 | 122.8363 | -0.20142 | 0.041199 | -0.31586 | -0.20599 | -0.23804 | 0.082397 | 2.3392 | -0.16937 | 0.068664 | 0.013733 | 122.9462 | 122.6074 | 67.6895 | -123.1659 | 123.0057 | 122.937 | 80.1407 | -123.1613
3405.0156 | 123.0835 | -50.4318 | 72.5464 | -0.22903 | 0.016849 | 0.071668 | 0.07479 | 0.12822 | 0.0024865 | -0.0066501 | -0.19089 | -0.009126 | 0.066614 | 0.059107 | 0.008908 | -0.015178 | 72.258 | 72.3816 | 15.7471 | -50.5829 | 72.6288 | -50.5005 | -50.6332 | -48.0652 | 29.6402 | -50.4776 | 72.6425 | 72.5967 | -50.6058 | -50.6561 | -0.068664 | -0.20142 | 0.082397 | 122.8134 | -0.15106 | 0.050354 | -0.28839 | -0.17395 | -0.2243 | 0.09613 | 2.3666 | -0.045776 | 0.17853 | 0.050354 | 123.0606 | 122.6898 | 66.1789 | -123.1796 | 123.0743 | 123.0286 | 80.072 | -123.2025
3406.0156 | 123.0148 | -50.0931 | 72.8714 | -0.19089 | 0.014285 | 0.072096 | 0.070944 | 0.12907 | -0.0024269 | -0.0089999 | -0.00015237 | -0.0095532 | 0.062982 | 0.056117 | 0.009549 | -0.011546 | 72.551 | 72.7615 | 15.239 | -50.2716 | 72.8714 | -50.2213 | -50.3357 | -47.8317 | 29.7318 | -50.2258 | 72.9172 | 72.8256 | -50.354 | -50.3357 | -0.12817 | -0.24261 | 0 | 122.8546 | -0.17853 | 0.064087 | -0.32044 | -0.26093 | -0.24261 | 0.045776 | 2.2614 | -0.13275 | 0.10986 | -0.045776 | 122.9645 | 122.644 | 65.332 | -123.2071 | 123.0103 | 122.9187 | 79.8248 | -123.2071
3407.0156 | 123.0606 | -50.1114 | 72.8851 | -0.22141 | 0.017276 | 0.0706 | 0.073294 | 0.128 | 0.00077755 | -0.0083591 | -0.168 | -0.009126 | 0.064905 | 0.056758 | 0.0091216 | -0.013469 | 72.7524 | 72.9034 | 13.2111 | -50.0839 | 73.114 | -50.0244 | -50.1343 | -47.8317 | 29.6997 | -50.2945 | 72.9263 | 72.8256 | -50.3494 | -50.3677 | 0.086975 | -0.022888 | 0.22888 | 123.0148 | 0.027466 | 0.050354 | -0.13275 | -0.23804 | -0.25635 | 0.041199 | 2.2797 | -0.18311 | 0.073242 | -0.059509 | 123.2254 | 122.8638 | 63.3224 | -123.0194 | 123.0377 | 122.937 | 79.8111 | -123.2529
3408.0156 | 123.0606 | -49.2371 | 73.764 | 0.11429 | 0.019626 | 0.0706 | 0.065176 | 0.128 | -0.0024269 | -0.0079319 | 0.18295 | -0.0097668 | 0.06875 | 0.057185 | 0.010617 | -0.01411 | 73.3612 | 73.1964 | 11.0458 | -49.6033 | 73.5626 | -49.5941 | -49.6948 | -47.0032 | 30.3726 | -49.3607 | 73.6954 | 73.6359 | -49.5117 | -49.5026 | -0.35706 | -0.45776 | -0.20142 | 122.4335 | -0.36621 | 0.091553 | -0.40283 | -0.27466 | -0.2655 | -0.068664 | 2.2339 | -0.1236 | 0.14191 | -0.12817 | 122.7997 | 122.5983 | 60.2829 | -123.4589 | 122.9324 | 122.8729 | 79.6097 | -123.2666
3409.0156 | 123.1155 | -49.4751 | 73.4253 | -0.19852 | 0.016849 | 0.067396 | 0.072653 | 0.1295 | -7.6852e-05 | -0.0062229 | -0.13748 | -0.0067762 | 0.065119 | 0.058467 | 0.009549 | -0.012401 | 73.4619 | 73.5992 | 11.7508 | -49.411 | 73.8052 | -49.3515 | -49.4522 | -47.1405 | 30.1895 | -49.5575 | 73.6176 | 73.5535 | -49.6536 | -49.7406 | 0.1236 | 0.022889 | 0.37994 | 123.0743 | 0.064087 | 0.041198 | 0.036621 | -0.17853 | -0.2655 | 0.19226 | 2.3346 | -0.082397 | 0.18311 | 0.12817 | 123.2803 | 122.937 | 61.2259 | -122.8775 | 123.0927 | 123.0286 | 79.6646 | -123.1659
3410.0156 | 123.1155 | -48.9807 | 73.9334 | -0.18326 | 0.010226 | 0.071668 | 0.071585 | 0.12843 | -0.0030677 | -0.0077183 | -0.091705 | -0.009126 | 0.062128 | 0.056117 | 0.0063446 | -0.011546 | 73.6176 | 73.8739 | 15.2985 | -49.1135 | 73.9334 | -49.1272 | -49.1821 | -46.5912 | 30.7251 | -48.9395 | 74.0799 | 73.9975 | -49.1501 | -49.1867 | -0.14648 | -0.20142 | 0 | 122.8546 | -0.13275 | 0.068665 | -0.31586 | -0.16937 | -0.20599 | 0.14648 | 2.3895 | 0.041199 | 0.24719 | 0.064087 | 122.9141 | 122.5983 | 64.2792 | -123.1155 | 123.0606 | 122.9782 | 79.7058 | -123.1201
3411.0156 | 123.0606 | -48.967 | 73.9517 | -0.25955 | 0.013217 | 0.071455 | 0.075003 | 0.13035 | -0.0032813 | -0.0070773 | 0.0914 | -0.010621 | 0.069177 | 0.054408 | 0.011258 | -0.013469 | 73.7045 | 73.8098 | 15.303 | -49.054 | 74.144 | -49.0082 | -49.1318 | -46.6461 | 30.6747 | -49.0265 | 74.1257 | 74.0204 | -49.173 | -49.2004 | -0.041199 | -0.16479 | 0.19226 | 122.7768 | -0.086975 | 0.07782 | -0.24719 | -0.20599 | -0.23346 | 0.17395 | 2.3209 | -0.059509 | 0.17395 | 0.068665 | 123.111 | 122.6715 | 64.27 | -123.0835 | 123.0927 | 122.9874 | 79.6417 | -123.1522
3412.0156 | 123.0286 | -49.9512 | 72.9767 | -0.31296 | 0.013644 | 0.074018 | 0.071799 | 0.128 | -0.0024269 | -0.0077183 | -0.11459 | -0.0097668 | 0.065332 | 0.058039 | 0.01019 | -0.012401 | 72.7753 | 72.9996 | 12.9272 | -50.061 | 73.0865 | -50.0153 | -50.1343 | -47.6624 | 29.8462 | -49.9924 | 73.0682 | 72.9904 | -50.1801 | -50.1938 | -0.064087 | -0.1831 | 0.10986 | 122.9507 | -0.10986 | 0.073242 | -0.20142 | -0.22888 | -0.24262 | 0.091552 | 2.2888 | -0.041199 | 0.20142 | 0.013732 | 123.0377 | 122.7264 | 62.8784 | -123.111 | 123.0194 | 122.9416 | 79.7974 | -123.1705
3413.0156 | 123.0835 | -50.2396 | 72.7203 | -0.22141 | 0.013431 | 0.070387 | 0.073081 | 0.12886 | -0.00093145 | -0.0085727 | -0.12985 | -0.014039 | 0.065973 | 0.057612 | 0.011472 | -0.01176 | 72.4228 | 72.6059 | 12.854 | -50.3769 | 72.821 | -50.3174 | -50.4089 | -47.9004 | 29.4479 | -50.3952 | 72.8302 | 72.7295 | -50.4456 | -50.5005 | -0.07782 | -0.16937 | 0.10071 | 122.8455 | -0.13733 | 0.032044 | -0.29755 | -0.20599 | -0.26093 | 0.10986 | 2.3392 | -0.15564 | 0.10528 | 0.009155 | 123.0606 | 122.6624 | 63.0936 | -123.1293 | 123.0698 | 122.9691 | 79.6875 | -123.2208
3414.0156 | 123.1201 | -49.6902 | 73.233 | -0.22141 | 0.010867 | 0.072523 | 0.07009 | 0.12779 | -0.0043495 | -0.0089999 | -0.099335 | -0.011903 | 0.063837 | 0.05633 | 0.006131 | -0.013255 | 72.995 | 73.2697 | 12.4374 | -49.7955 | 73.3292 | -49.7543 | -49.8505 | -47.3282 | 29.9103 | -49.7223 | 73.2925 | 73.2101 | -49.9008 | -49.9512 | -0.064086 | -0.16022 | 0.096131 | 122.9599 | -0.10529 | 0.054932 | -0.23804 | -0.21057 | -0.26093 | 0.05951 | 2.3621 | -0.032043 | 0.22888 | -0.022888 | 123.0194 | 122.6852 | 62.1277 | -123.0835 | 122.9828 | 122.9004 | 79.6005 | -123.1842
3415.0156 | 123.0286 | -48.8663 | 74.1165 | -0.22903 | 0.01578 | 0.072523 | 0.07543 | 0.12758 | 0.00099115 | -0.0085727 | -0.31296 | -0.0084852 | 0.064691 | 0.057398 | 0.0097626 | -0.014323 | 73.9059 | 73.9609 | 12.4191 | -49.0219 | 74.2172 | -48.9395 | -49.0631 | -46.4859 | 30.423 | -48.9212 | 74.2401 | 74.1302 | -49.0311 | -49.0585 | -0.073242 | -0.19684 | 0.10071 | 122.8271 | -0.15564 | 0.041198 | -0.21057 | -0.16479 | -0.19226 | 0.1236 | 2.3804 | -0.054932 | 0.13733 | 0.013733 | 123.0835 | 122.7722 | 61.2854 | -123.1796 | 123.1064 | 122.9965 | 79.2892 | -123.175
3416.0156 | 123.0698 | -49.3011 | 73.6771 | -0.21378 | 0.01044 | 0.070814 | 0.072653 | 0.13099 | -0.0013587 | -0.0077183 | -0.168 | -0.0093396 | 0.064905 | 0.057826 | 0.0084808 | -0.01176 | 73.4436 | 73.6816 | 12.5198 | -49.3698 | 73.7732 | -49.3423 | -49.4293 | -47.0581 | 29.8782 | -49.4843 | 73.6221 | 73.5672 | -49.5758 | -49.5758 | -0.041199 | -0.12817 | 0.09613 | 122.9828 | -0.068665 | 0.059509 | -0.23346 | -0.27466 | -0.27466 | -0.054932 | 2.243 | -0.18311 | 0.091553 | -0.10986 | 123.0743 | 122.7448 | 61.821 | -123.1064 | 122.9233 | 122.8683 | 79.1794 | -123.2529
3417.0156 | 123.024 | -49.942 | 73.0179 | -0.21378 | 0.014712 | 0.073164 | 0.071799 | 0.1295 | -0.00093145 | -0.0085727 | -0.15274 | -0.011262 | 0.0664 | 0.055689 | 0.0093354 | -0.012401 | 72.7707 | 72.9721 | 12.2314 | -50.0336 | 73.1689 | -49.9832 | -50.0656 | -47.6212 | 29.7775 | -50.2945 | 73.1827 | 73.0499 | -50.1251 | -50.1709 | -0.041198 | -0.1236 | 0.15106 | 122.9141 | -0.091552 | 0.032044 | -0.24719 | -0.1831 | -0.22888 | 0.16479 | 2.3209 | -0.35248 | -0.1236 | 0.032044 | 123.111 | 122.7127 | 62.1735 | -123.0835 | 123.1247 | 122.9919 | 79.7195 | -123.1888
3418.0156 | 123.1476 | -49.6582 | 73.2056 | -0.19089 | 0.0085171 | 0.070814 | 0.071158 | 0.12886 | -0.0047767 | -0.0047275 | 0.19058 | -0.010194 | 0.063196 | 0.057185 | 0.0086944 | -0.012828 | 72.7753 | 73.32 | 12.4191 | -49.736 | 73.3154 | -49.7314 | -49.8413 | -47.2641 | 29.7089 | -49.6948 | 73.288 | 73.201 | -49.91 | -49.9283 | -0.073242 | -0.18311 | 0.10986 | 122.9782 | -0.07782 | 0.10529 | -0.4303 | -0.25177 | -0.27008 | 0.082398 | 2.3941 | -0.036621 | 0.23346 | -0.004577 | 122.9736 | 122.4335 | 62.0773 | -123.0469 | 122.9462 | 122.8592 | 79.3671 | -123.1338
3419.0156 | 123.056 | -48.5367 | 74.4461 | -0.23666 | 0.014071 | 0.071882 | 0.074576 | 0.13099 | 0.0014185 | -0.0057957 | -0.0077819 | -0.0097668 | 0.064905 | 0.058039 | 0.0099762 | -0.014751 | 73.9426 | 74.4965 | 12.7396 | -48.9212 | 74.4415 | -48.7473 | -48.8434 | -46.2891 | 30.4642 | -48.674 | 74.4507 | 74.3317 | -48.8297 | -48.8297 | -0.21057 | -0.3067 | -0.004578 | 123.0331 | -0.38452 | -0.07782 | -0.50354 | -0.29297 | -0.29297 | 0.004578 | 2.2476 | -0.13733 | 0.15564 | -0.11444 | 122.9782 | 122.4792 | 61.2762 | -123.2895 | 122.9874 | 122.8683 | 79.0009 | -123.2758
3420.0156 | 123.1476 | -49.1272 | 73.7366 | -0.45792 | 0.0089443 | 0.071668 | 0.072867 | 0.12715 | -0.0030677 | -0.0083591 | -0.12985 | -0.011689 | 0.065546 | 0.05633 | 0.009549 | -0.013042 | 73.5626 | 73.8602 | 12.4466 | -49.2233 | 73.8693 | -49.2279 | -49.324 | -46.7926 | 30.0659 | -49.1272 | 73.8052 | 73.7045 | -49.3561 | -49.4156 | -0.10071 | -0.19684 | 0.13275 | 122.9874 | -0.096131 | 0.10071 | -0.17395 | -0.22888 | -0.28839 | 0.068665 | 2.3346 | 0 | 0.28839 | -0.032043 | 122.9965 | 122.6898 | 61.5738 | -123.0606 | 122.9324 | 122.8317 | 79.1931 | -123.1522
3421.0156 | 123.0469 | -49.5575 | 73.3887 | -0.26718 | 0.01279 | 0.069105 | 0.074576 | 0.13078 | -0.00029045 | -0.010922 | -0.12222 | -0.010408 | 0.064478 | 0.057826 | 0.0082672 | -0.013683 | 73.0774 | 73.3154 | 12.2131 | -49.7681 | 73.4482 | -49.6902 | -49.7589 | -47.1588 | 29.7363 | -49.6262 | 73.5352 | 73.407 | -49.7269 | -49.7681 | -0.13275 | -0.20142 | 0.059509 | 122.8729 | -0.21057 | -0.009155 | -0.31128 | -0.16937 | -0.21057 | 0.14648 | 2.3987 | -0.068665 | 0.14191 | 0.01831 | 123.0057 | 122.6349 | 61.7706 | -123.1476 | 123.0927 | 122.9645 | 79.2938 | -123.1567
3422.0156 | 123.1888 | -49.1364 | 73.7274 | -0.13748 | 0.011081 | 0.071241 | 0.071585 | 0.13057 | -0.0049903 | -0.0087863 | -2.9756 | -0.012117 | 0.068323 | 0.056758 | 0.0076264 | -0.011974 | 73.6404 | 73.9197 | 13.7329 | -49.173 | 73.9059 | -49.1821 | -49.2966 | -46.6644 | 29.9103 | -49.1547 | 73.8007 | 73.6862 | -49.3881 | -49.4202 | -0.045776 | -0.16022 | 0.17853 | 123.056 | -0.036621 | 0.1236 | -0.086975 | -0.25177 | -0.28381 | 0.073242 | 2.4719 | -0.01831 | 0.2655 | -0.041199 | 123.0423 | 122.7768 | 62.8693 | -123.024 | 122.937 | 122.8226 | 79.0466 | -123.1476
3423.0156 | 123.0377 | -50.6012 | 72.377 | -0.22141 | 0.013217 | 0.071455 | 0.073935 | 0.12822 | -0.00071785 | -0.0085727 | -0.19852 | -0.0095532 | 0.064264 | 0.055476 | 0.0050628 | -0.014751 | 71.9376 | 72.171 | 10.9039 | -50.8484 | 72.3541 | -50.798 | -50.8804 | -48.1888 | 28.4958 | -50.6699 | 72.4182 | 72.345 | -50.8347 | -50.853 | -0.19684 | -0.27924 | -0.022888 | 122.7722 | -0.24719 | 0.032043 | -0.43945 | -0.23346 | -0.25177 | 0.041199 | 2.4124 | -0.068665 | 0.18311 | -0.032043 | 122.9553 | 122.5388 | 61.5051 | -123.2574 | 123.0194 | 122.9462 | 79.097 | -123.23
3424.0156 | 123.1384 | -49.1318 | 73.7732 | -0.099335 | 0.0093717 | 0.071455 | 0.069876 | 0.12864 | -0.0030677 | -0.0060093 | -0.045929 | -0.010194 | 0.063623 | 0.056117 | 0.0084808 | -0.012614 | 73.5947 | 73.8464 | 11.0138 | -49.2645 | 73.8785 | -49.2233 | -49.2783 | -46.6873 | 30.0797 | -49.1364 | 73.8144 | 73.7137 | -49.3423 | -49.3927 | -0.091553 | -0.14648 | 0.10529 | 122.9782 | -0.13275 | 0.013733 | -0.17853 | -0.21057 | -0.26093 | 0.041199 | 2.4445 | -0.004578 | 0.25635 | -0.059509 | 123.0103 | 122.7264 | 60.1456 | -123.0515 | 122.9462 | 122.8455 | 79.2114 | -123.1659
3425.0156 | 123.056 | -49.91 | 73.0408 | -0.24429 | 0.01578 | 0.068678 | 0.077567 | 0.12907 | -7.6852e-05 | -0.0075047 | -0.0077819 | -0.012117 | 0.066187 | 0.057398 | 0.010403 | -0.014323 | 72.7524 | 72.9675 | 9.8557 | -50.0565 | 73.0728 | -50.0336 | -50.1343 | -47.5571 | 29.3564 | -49.9329 | 73.1094 | 72.995 | -50.148 | -50.1617 | -0.1236 | -0.2243 | 0.032044 | 122.8775 | -0.14648 | 0.077819 | -0.28839 | -0.23804 | -0.25177 | 0.068665 | 2.3529 | -0.022888 | 0.22888 | -0.045776 | 122.9828 | 122.6624 | 59.7656 | -123.175 | 123.0194 | 122.905 | 79.2664 | -123.2025
3426.0156 | 123.1384 | -49.2416 | 73.6267 | -0.099335 | 0.010013 | 0.074659 | 0.072226 | 0.12993 | -0.0032813 | -0.0070773 | -0.084076 | -0.011689 | 0.061701 | 0.056758 | 0.0091216 | -0.013896 | 73.5214 | 73.7778 | 11.1191 | -49.2462 | 73.8281 | -49.2142 | -49.2645 | -46.669 | 30.0934 | -49.1592 | 73.8007 | 73.7045 | -49.4064 | -49.4568 | 0.027466 | -0.022888 | 0.20142 | 123.0194 | -0.004578 | 0.01831 | -0.10529 | -0.16479 | -0.21515 | 0.17395 | 2.5726 | 0.082397 | 0.29755 | 0.07782 | 123.0698 | 122.7631 | 60.3607 | -122.8912 | 123.0423 | 122.9462 | 79.335 | -123.0835
3427.0156 | 123.0743 | -49.7818 | 73.1323 | -0.25192 | 0.011081 | 0.070814 | 0.072867 | 0.12843 | -0.0011451 | -0.0075047 | -0.19089 | -0.011262 | 0.0664 | 0.055689 | 0.00784 | -0.013896 | 73.0408 | 73.2697 | 9.407 | -49.8001 | 73.32 | -49.7726 | -49.9054 | -47.4564 | 29.3838 | -49.9558 | 73.1415 | 73.0133 | -50.061 | -50.0702 | 0.009155 | -0.1236 | 0.18768 | 123.0515 | -0.018311 | 0.10529 | -0.091553 | -0.27924 | -0.28839 | 0.009155 | 2.3254 | -0.17395 | 0.11444 | -0.11902 | 123.1018 | 122.8226 | 59.1888 | -123.0377 | 122.9233 | 122.7951 | 79.1656 | -123.2025
3428.0156 | 123.175 | -49.1684 | 73.6954 | -0.091705 | 0.0085171 | 0.071668 | 0.070517 | 0.12864 | -0.0028541 | -0.0087863 | -0.00015237 | -0.010835 | 0.062342 | 0.058467 | 0.00784 | -0.013255 | 73.5947 | 73.8419 | 9.3521 | -49.2279 | 73.8922 | -49.2142 | -49.2828 | -46.6232 | 29.9744 | -49.1135 | 73.8281 | 73.6954 | -49.3927 | -49.4705 | -0.045776 | -0.11444 | 0.19684 | 123.0103 | -0.059509 | 0.054932 | -0.10071 | -0.2243 | -0.30212 | 0.13275 | 2.5452 | 0.054932 | 0.35706 | 0 | 123.0606 | 122.7631 | 58.5205 | -122.9782 | 122.9965 | 122.8638 | 79.1428 | -123.1659
3429.0156 | 123.0972 | -50.5188 | 72.3495 | -0.25955 | 0.011294 | 0.0706 | 0.069663 | 0.1295 | -0.0024269 | -0.0075047 | -0.12985 | -0.012544 | 0.061701 | 0.054194 | 0.009549 | -0.013042 | 72.2443 | 72.4411 | 9.3384 | -50.6378 | 72.464 | -50.6012 | -50.7019 | -48.0377 | 28.9124 | -50.5829 | 72.4503 | 72.345 | -50.7385 | -50.7568 | -0.082397 | -0.1831 | 0.11444 | 122.9599 | -0.11902 | 0.064087 | -0.10528 | -0.21973 | -0.23804 | 0.10071 | 2.4811 | -0.064087 | 0.17395 | -0.004577 | 122.9828 | 122.7631 | 59.8572 | -123.0515 | 122.9691 | 122.8638 | 79.4312 | -123.1064
3430.0156 | 123.2574 | -49.2142 | 73.6588 | -0.068817 | 0.0087307 | 0.071455 | 0.070731 | 0.12993 | -7.6852e-05 | -0.0092137 | -0.099335 | -0.010835 | 0.064691 | 0.053767 | 0.0099762 | -0.013683 | 73.5443 | 73.7961 | 9.169 | -49.324 | 73.7961 | -49.2874 | -49.4156 | -46.7285 | 27.8641 | -49.2279 | 73.7091 | 73.613 | -49.4431 | -49.4751 | -0.073243 | -0.20142 | 0.13733 | 123.0103 | -0.10986 | 0.091552 | -0.11444 | -0.22888 | -0.26093 | 0.050354 | 2.4857 | -0.013733 | 0.24719 | -0.045776 | 123.0103 | 122.7585 | 58.3832 | -123.0743 | 122.9233 | 122.8271 | 77.0782 | -123.1339
3431.0156 | 123.1476 | -48.8113 | 74.0753 | -0.17563 | 0.0080899 | 0.075086 | 0.069663 | 0.12779 | -0.0019995 | -0.0081455 | -0.099335 | -0.012544 | 0.063623 | 0.055903 | 0.009549 | -0.012828 | 74.0616 | 74.025 | 9.407 | -48.8983 | 74.1348 | -48.8892 | -49.0128 | -46.3806 | 28.8208 | -48.7427 | 74.1257 | 73.9746 | -49.0585 | -49.086 | -0.07782 | -0.20142 | 0.05951 | 122.8363 | -0.086975 | 0.11444 | -0.013733 | -0.24719 | -0.27466 | 0.050354 | 2.4307 | 0.068664 | 0.34332 | -0.10071 | 122.9462 | 122.8729 | 58.2184 | -123.0881 | 122.937 | 122.7859 | 77.6321 | -123.1613
3432.0156 | 123.1476 | -48.4497 | 74.4049 | 0.0074768 | 0.011081 | 0.071668 | 0.070944 | 0.13057 | -0.0022131 | -0.0081455 | 0.022736 | -0.014467 | 0.063837 | 0.055903 | 0.0080536 | -0.012401 | 74.1806 | 74.4186 | 9.5947 | -48.6099 | 74.5193 | -48.5687 | -48.6877 | -46.0327 | 28.9124 | -48.5321 | 74.469 | 74.3683 | -48.7244 | -48.7381 | -0.11902 | -0.23804 | 0.11444 | 122.8683 | -0.16022 | 0.07782 | -0.2243 | -0.27466 | -0.28839 | 0.064087 | 2.417 | -0.082397 | 0.20599 | -0.036621 | 122.9691 | 122.6303 | 58.0444 | -123.0927 | 122.9187 | 122.818 | 77.3621 | -123.143
3433.0156 | 123.1338 | -48.9899 | 73.9014 | -0.18326 | 0.0095853 | 0.072096 | 0.073508 | 0.12651 | 0.0014185 | -0.0072911 | -0.15274 | -0.012758 | 0.062555 | 0.053767 | 0.0082672 | -0.01646 | 73.9426 | 74.1623 | 8.3862 | -48.999 | 74.1623 | -48.9487 | -49.1043 | -46.4996 | 28.6194 | -49.1776 | 74.0112 | 73.9243 | -49.1821 | -49.2188 | 0.041199 | -0.11444 | 0.26093 | 123.1522 | -0.009155 | 0.10529 | 0.041199 | -0.19226 | -0.22888 | 0.10986 | 2.4902 | -0.18768 | 0.041199 | 0.022888 | 123.1522 | 122.9324 | 57.3761 | -123.0057 | 123.0011 | 122.9141 | 77.6093 | -123.1201
3434.0156 | 123.175 | -48.8846 | 73.9975 | -0.076447 | 0.010226 | 0.069105 | 0.069022 | 0.128 | -0.0024269 | -0.0070773 | -0.084076 | -0.01233 | 0.061701 | 0.05633 | 0.0097626 | -0.012401 | 73.8098 | 74.0387 | 8.1894 | -48.9944 | 74.1074 | -48.9807 | -49.0723 | -46.4172 | 29.0039 | -48.912 | 74.0707 | 73.9609 | -49.1043 | -49.1547 | -0.09613 | -0.18768 | 0.10986 | 122.9233 | -0.10986 | 0.07782 | -0.18768 | -0.21973 | -0.27008 | 0.073242 | 2.4673 | -0.027465 | 0.24262 | -0.036622 | 122.9919 | 122.6944 | 57.074 | -123.0698 | 122.9553 | 122.8455 | 77.8885 | -123.1522
3435.0156 | 123.1293 | -49.1638 | 73.6816 | -3.6394 | 0.010013 | 0.06825 | 0.070303 | 0.128 | -7.6852e-05 | -0.0083591 | -0.091705 | -0.01233 | 0.061487 | 0.056758 | 0.011472 | -0.013469 | 73.5764 | 73.938 | 9.2239 | -49.1592 | 73.9334 | -49.1455 | -49.2554 | -46.6965 | 28.9993 | -49.2966 | 73.7823 | 73.6633 | -49.3835 | -49.4385 | 0.01831 | -0.091553 | 0.25177 | 123.1018 | 0.004577 | 0.09613 | -0.10529 | -0.21973 | -0.27466 | 0.10071 | 2.4673 | -0.13275 | 0.14191 | -0.018311 | 123.0972 | 122.7402 | 58.3878 | -122.937 | 122.9462 | 122.8271 | 78.1631 | -123.1201
3436.0156 | 123.1796 | -49.6948 | 73.1644 | -0.091705 | 0.0087307 | 0.071241 | 0.069876 | 0.1295 | -0.0015723 | -0.010068 | -0.023041 | -0.012544 | 0.063837 | 0.054621 | 0.0097626 | -0.01411 | 72.9309 | 73.1964 | 8.9035 | -49.9191 | 73.201 | -49.9008 | -49.9924 | -47.2092 | 28.569 | -49.7314 | 73.2376 | 73.1094 | -49.9329 | -49.9741 | -0.20599 | -0.29755 | 0.036621 | 122.8912 | -0.2243 | 0.073243 | -0.23346 | -0.23804 | -0.27924 | 0.073242 | 2.4857 | -0.036621 | 0.24262 | -0.054932 | 122.8958 | 122.6257 | 58.5983 | -123.1567 | 122.9324 | 122.8043 | 78.2639 | -123.1384
3437.0156 | 123.1155 | -48.6099 | 74.3088 | -0.168 | 0.011294 | 0.071882 | 0.071158 | 0.13035 | -0.0019995 | -0.0087863 | -0.18326 | -0.011476 | 0.064478 | 0.057398 | 0.010403 | -0.014537 | 74.1577 | 74.3912 | 9.6039 | -48.674 | 74.4186 | -48.6832 | -48.7747 | -46.1151 | 29.7501 | -48.6557 | 74.4186 | 74.2813 | -48.8159 | -48.8297 | -0.073243 | -0.16479 | 0.10986 | 123.0011 | -0.064087 | 0.10071 | -0.15106 | -0.20599 | -0.21973 | 0.10986 | 2.4948 | -0.045777 | 0.17395 | -0.027466 | 123.0286 | 122.7676 | 58.2138 | -123.0835 | 123.0286 | 122.8912 | 78.36 | -123.1384
3438.0156 | 123.1338 | -50.0793 | 72.7982 | -0.0383 | 0.010013 | 0.071455 | 0.069876 | 0.12886 | -0.0024269 | -0.010709 | 0.068512 | -0.011903 | 0.065759 | 0.054194 | 0.0086944 | -0.014323 | 72.7158 | 72.9492 | 8.5144 | -50.1068 | 73.0591 | -50.0839 | -50.1846 | -47.5891 | 28.3859 | -50.1755 | 72.9034 | 72.7844 | -50.2991 | -50.3448 | -0.004577 | -0.10529 | 0.26093 | 123.0286 | -0.027466 | 0.077819 | -0.082398 | -0.21973 | -0.2655 | 0.10528 | 2.4902 | -0.09613 | 0.16937 | -0.013733 | 123.1384 | 122.7951 | 58.5938 | -122.9828 | 122.9828 | 122.8638 | 78.4653 | -123.143
3439.0156 | 123.1338 | -49.8276 | 73.0591 | -0.40451 | 0.01044 | 0.070814 | 0.073081 | 0.12608 | 0.0012047 | -0.0062229 | -0.12222 | -0.010835 | 0.065759 | 0.057398 | 0.010403 | -0.014323 | 72.8989 | 73.1461 | 8.0292 | -49.91 | 73.1781 | -49.91 | -50.0198 | -47.3236 | 29.0726 | -49.8322 | 73.1552 | 73.0316 | -50.061 | -50.0885 | -0.082397 | -0.19226 | 0.11902 | 122.9736 | -0.082397 | 0.10986 | -0.16022 | -0.23346 | -0.26093 | 0.09613 | 2.504 | -0.004577 | 0.25635 | -0.027466 | 123.0057 | 122.7264 | 57.8568 | -123.0789 | 122.9828 | 122.8592 | 78.9001 | -123.1476
3440.0156 | 123.175 | -49.7406 | 73.1323 | 0.0074768 | 0.01044 | 0.073164 | 0.07009 | 0.12886 | -0.0019995 | -0.0068637 | -0.068817 | -0.010408 | 0.064264 | 0.054621 | 0.0099762 | -0.014964 | 73.0087 | 73.233 | 8.5922 | -49.8459 | 73.288 | -49.8093 | -49.9283 | -47.2504 | 28.9307 | -49.8367 | 73.2101 | 73.0637 | -50.0153 | -50.0244 | -0.068664 | -0.18768 | 0.15564 | 122.9736 | -0.10529 | 0.082398 | -0.1236 | -0.27466 | -0.28381 | 0.07782 | 2.4902 | -0.09613 | 0.18768 | -0.068664 | 123.0286 | 122.7493 | 58.3328 | -123.0606 | 122.9507 | 122.8043 | 78.6713 | -123.1567
3441.0156 | 123.1476 | -49.1501 | 73.7228 | 0.19058 | 0.014499 | 0.068037 | 0.074362 | 0.12971 | 0.00099115 | -0.0092137 | -0.22903 | -0.011689 | 0.065119 | 0.055689 | 0.0097626 | -0.013683 | 73.5901 | 73.8419 | 8.1619 | -49.2691 | 73.8464 | -49.2462 | -49.3378 | -46.6003 | 29.3655 | -49.2325 | 73.8602 | 73.7183 | -49.3423 | -49.3927 | -0.096131 | -0.18768 | 0.1236 | 122.9919 | -0.11902 | 0.068665 | -0.13275 | -0.19226 | -0.24262 | 0.13733 | 2.5497 | -0.082398 | 0.16022 | -0.004577 | 122.9965 | 122.7402 | 57.312 | -123.0606 | 123.0103 | 122.8683 | 78.5156 | -123.1155
3442.0156 | 123.1018 | -51.8188 | 71.0266 | -0.0383 | 0.0070217 | 0.074018 | 0.071372 | 0.12886 | -0.0011451 | -0.0094273 | -0.00015237 | -0.012544 | 0.063196 | 0.057185 | 0.0076264 | -0.014537 | 70.8389 | 71.0495 | 7.1365 | -52.0065 | 71.1411 | -51.9653 | -52.0752 | -49.324 | 27.0859 | -51.8967 | 71.1319 | 71.0083 | -52.0752 | -52.0844 | -0.14648 | -0.25635 | 0.11444 | 122.8683 | -0.18768 | 0.068664 | -0.18768 | -0.25635 | -0.2655 | 0.10529 | 2.4948 | -0.077819 | 0.18768 | -0.01831 | 122.9599 | 122.6578 | 58.9554 | -123.1018 | 122.9507 | 122.8271 | 78.9047 | -123.111
3443.0156 | 123.1338 | -48.9761 | 73.9243 | -0.18326 | 0.010653 | 0.070387 | 0.069449 | 0.12886 | -0.00050425 | -0.0081455 | -0.19852 | -0.010194 | 0.062128 | 0.055903 | 0.0093354 | -0.014751 | 73.6404 | 73.8602 | 7.4112 | -49.1455 | 73.9334 | -49.1455 | -49.2371 | -46.4859 | 29.686 | -48.9532 | 74.0387 | 73.8831 | -49.1913 | -49.2233 | -0.16937 | -0.26093 | 0.009156 | 122.8363 | -0.16937 | 0.091553 | -0.28381 | -0.21515 | -0.24719 | 0.11444 | 2.4902 | 0.022888 | 0.27008 | -0.041198 | 122.9095 | 122.6166 | 56.3873 | -123.1613 | 123.0148 | 122.8592 | 78.6621 | -123.1476
3444.0156 | 123.1476 | -50.9171 | 71.933 | -0.084076 | 0.0095853 | 0.075086 | 0.071158 | 0.12864 | -0.0015723 | -0.0068637 | -0.03067 | -0.010835 | 0.063623 | 0.057612 | 0.0084808 | -0.013255 | 71.8094 | 72.0474 | 6.9031 | -51.0269 | 72.052 | -51.0406 | -51.1185 | -48.3719 | 28.1708 | -50.9308 | 72.0245 | 71.8918 | -51.1642 | -51.1917 | -0.1236 | -0.20142 | 0.11902 | 122.9645 | -0.10986 | 0.091552 | -0.1236 | -0.24719 | -0.27466 | 0.091553 | 2.5452 | -0.013733 | 0.26093 | -0.041198 | 122.9691 | 122.7264 | 57.8201 | -123.0515 | 122.9416 | 122.8088 | 79.0878 | -123.1247
3445.0156 | 123.143 | -50.3403 | 72.5098 | -0.12985 | 0.011081 | 0.069959 | 0.073508 | 0.12843 | 0.00056395 | -0.0066501 | -0.15274 | -0.013185 | 0.062982 | 0.055903 | 0.0097626 | -0.014964 | 72.4594 | 72.6883 | 6.7108 | -50.3769 | 72.7112 | -50.3494 | -50.4593 | -47.7951 | 28.8025 | -50.4501 | 72.6883 | 72.5418 | -50.5325 | -50.5692 | -0.009155 | -0.11902 | 0.20142 | 123.0286 | -0.036621 | 0.082398 | -0.050354 | -0.19226 | -0.22888 | 0.17853 | 2.5452 | -0.10986 | 0.11902 | 0.032043 | 123.0515 | 122.7997 | 57.0511 | -122.9691 | 123.0286 | 122.8821 | 79.1428 | -123.0789
3446.0156 | 123.1476 | -50.0702 | 72.7936 | -0.023041 | 0.0078763 | 0.069532 | 0.071799 | 0.12822 | -0.0011451 | -0.0087863 | 0.045624 | -0.0099806 | 0.062982 | 0.055476 | 0.008908 | -0.011333 | 72.5693 | 72.821 | 6.4911 | -50.2075 | 72.8714 | -50.1984 | -50.2945 | -47.3694 | 29.1046 | -49.9237 | 73.0408 | 72.8577 | -50.2258 | -50.3128 | -0.12817 | -0.22431 | 0.07782 | 122.8912 | -0.13733 | 0.086975 | -0.2243 | -0.15564 | -0.24262 | 0.24719 | 2.7008 | 0.14648 | 0.3891 | 0.064087 | 122.9416 | 122.6395 | 56.5613 | -123.0881 | 123.111 | 122.9279 | 79.1748 | -123.1064
3447.0156 | 123.1659 | -49.173 | 73.7091 | -3.5707 | 0.0095853 | 0.065687 | 0.066245 | 0.13078 | -0.00050425 | -0.0040867 | -0.045929 | -0.010621 | 0.064051 | 0.057612 | 0.0097626 | -0.014964 | 73.764 | 74.0753 | 6.601 | -49.0585 | 74.0433 | -49.054 | -49.1501 | -46.6461 | 29.7821 | -49.3698 | 73.7686 | 73.6588 | -49.3927 | -49.4476 | 0.11902 | 0.022889 | 0.33417 | 123.2483 | 0.11444 | 0.091552 | 0.054932 | -0.21973 | -0.27466 | 0.05951 | 2.5269 | -0.19684 | 0.07782 | -0.050354 | 123.2162 | 122.937 | 55.7739 | -122.8592 | 122.9416 | 122.8317 | 78.9551 | -123.1567
3448.0156 | 123.1293 | -50.5051 | 72.3953 | -0.0077822 | 0.0070217 | 0.069746 | 0.070731 | 0.12736 | 0.00056395 | -0.0075047 | 0.030365 | -0.012117 | 0.062982 | 0.056544 | 0.009549 | -0.013255 | 72.2076 | 72.4228 | 6.958 | -50.5966 | 72.5372 | -50.592 | -50.679 | -47.9919 | 28.6285 | -50.7019 | 72.4228 | 72.2855 | -50.7431 | -50.7935 | -0.086975 | -0.17395 | 0.14191 | 122.9279 | -0.091553 | 0.082397 | -0.18768 | -0.23804 | -0.28839 | 0.027466 | 2.5131 | -0.19684 | 0.091553 | -0.10986 | 123.0423 | 122.7127 | 57.4631 | -123.0743 | 122.9279 | 122.7905 | 79.1336 | -123.1888
3449.0156 | 123.1613 | -49.736 | 73.1552 | -0.168 | 0.0095853 | 0.071668 | 0.071585 | 0.12907 | 0.0014185 | -0.0075047 | -0.099335 | -0.011476 | 0.065759 | 0.052272 | 0.0093354 | -0.011119 | 73.0774 | 73.2925 | 7.0312 | -49.7772 | 73.2834 | -49.7818 | -49.8825 | -47.2961 | 29.567 | -49.6307 | 73.2788 | 73.1232 | -49.9649 | -50.0061 | -0.045776 | -0.14648 | 0.12817 | 123.0286 | -0.041199 | 0.10528 | -0.077819 | -0.22888 | -0.27008 | 0.1236 | 2.4399 | 0.10529 | 0.37537 | -0.032043 | 123.0194 | 122.8134 | 56.7673 | -123.0377 | 123.0148 | 122.8592 | 79.303 | -123.1613
3450.0156 | 123.1705 | -51.0635 | 71.7865 | -0.099335 | 0.010013 | 0.072096 | 0.072012 | 0.12907 | -0.0015723 | -0.0055821 | -0.00015237 | -0.012544 | 0.062555 | 0.055689 | 0.011258 | -0.01411 | 71.6583 | 71.8597 | 7.1457 | -51.1826 | 71.9193 | -51.1597 | -51.2878 | -48.5092 | 28.2898 | -51.1139 | 71.8735 | 71.7499 | -51.3153 | -51.3519 | -0.09613 | -0.2243 | 0.13275 | 122.9233 | -0.11902 | 0.10529 | -0.12817 | -0.25177 | -0.28839 | 0.086975 | 2.5543 | -0.050354 | 0.23804 | -0.036621 | 122.9828 | 122.7219 | 58.2092 | -123.0743 | 122.937 | 122.8134 | 79.3533 | -123.1384
3451.0156 | 123.1522 | -50.386 | 72.4686 | 2.9906 | 0.012149 | 0.071668 | 0.070944 | 0.1295 | -0.0011451 | -0.0068637 | -0.12222 | -0.0099806 | 0.063837 | 0.056758 | 0.011044 | -0.014537 | 72.345 | 72.4548 | 7.0221 | -50.5554 | 72.5647 | -50.5325 | -50.6241 | -47.8592 | 28.894 | -50.4044 | 72.551 | 72.4411 | -50.6104 | -50.6516 | -0.14649 | -0.23804 | 0.09613 | 122.8409 | -0.16937 | 0.068664 | -0.1236 | -0.22431 | -0.2655 | 0.082397 | 2.5269 | -0.018311 | 0.24719 | -0.027466 | 122.9507 | 122.731 | 57.4081 | -123.0927 | 122.937 | 122.8271 | 79.2801 | -123.1201
3452.0156 | 123.1247 | -50.3403 | 72.5235 | 0.015106 | 0.0093717 | 0.071882 | 0.070517 | 0.12843 | 0.00035035 | -0.0066501 | -0.31296 | -0.011476 | 0.064905 | 0.057185 | 0.011472 | -0.014537 | 72.5555 | 72.7661 | 6.8665 | -50.2808 | 72.8348 | -50.235 | -50.3723 | -47.7448 | 29.0176 | -50.2899 | 72.757 | 72.6013 | -50.5005 | -50.5692 | 0.10529 | -0.032043 | 0.31128 | 123.1064 | 0.059509 | 0.091552 | 0.032043 | -0.16022 | -0.22888 | 0.23346 | 2.5955 | 0.050354 | 0.27924 | 0.077819 | 123.175 | 122.8958 | 57.2067 | -122.8958 | 123.0972 | 122.9416 | 79.3579 | -123.0927
3453.0156 | 123.1705 | -50.7019 | 72.1893 | -0.17563 | 0.0093717 | 0.0706 | 0.071372 | 0.12758 | 0.00013675 | -0.0085727 | -1.4421 | -0.013185 | 0.067682 | 0.057185 | 0.0052764 | -0.012401 | 71.933 | 72.1802 | 6.3538 | -50.9033 | 72.139 | -50.9171 | -51.0315 | -48.1155 | 28.6285 | -50.6241 | 72.2397 | 72.0932 | -50.9445 | -50.9445 | -0.21515 | -0.32959 | -0.050354 | 122.8821 | -0.20142 | 0.12817 | -0.25635 | -0.24262 | -0.24262 | 0.050354 | 2.5864 | 0.07782 | 0.32043 | -0.09613 | 122.8409 | 122.6349 | 57.0557 | -123.2208 | 122.9416 | 122.7951 | 79.3304 | -123.1338
3454.0156 | 123.111 | -50.3128 | 72.5876 | -0.084076 | 0.010226 | 0.071027 | 0.073508 | 0.13014 | -0.0015723 | -0.0068637 | 0.076141 | -0.010408 | 0.062769 | 0.057398 | 0.010617 | -0.011546 | 72.4869 | 72.6883 | 6.6788 | -50.3952 | 72.789 | -50.3403 | -50.4501 | -47.7402 | 29.1183 | -50.3769 | 72.6837 | 72.5418 | -50.5096 | -50.5508 | -0.027466 | -0.13733 | 0.20142 | 123.0011 | -0.082398 | 0.054931 | -0.10071 | -0.19684 | -0.23804 | 0.096131 | 2.5726 | -0.064087 | 0.17395 | -0.045776 | 123.1018 | 122.7997 | 56.9916 | -123.0377 | 122.9965 | 122.8546 | 79.4312 | -123.1384
3455.0156 | 123.0515 | -51.4343 | 71.521 | -0.25192 | 0.014926 | 0.072523 | 0.070303 | 0.12886 | 0.00056395 | -0.0064365 | -0.25192 | -0.010194 | 0.065546 | 0.057185 | 0.011258 | -0.01411 | 71.0999 | 71.315 | 6.4041 | -51.6129 | 71.4294 | -51.6998 | -51.7502 | -48.8342 | 28.1525 | -51.6495 | 71.5897 | 71.4661 | -51.6541 | -51.6769 | -0.2655 | -0.31586 | -0.091553 | 122.7493 | -0.17853 | 0.13733 | -0.42114 | -0.21973 | -0.24262 | 0.068665 | 2.6001 | -0.21515 | 0.027466 | -0.054932 | 122.8638 | 122.5342 | 57.8384 | -123.2712 | 123.024 | 122.9004 | 79.5868 | -123.1979
3456.0156 | 123.143 | -50.2716 | 72.6608 | 0.015106 | 0.0097989 | 0.069746 | 0.069876 | 0.1295 | -0.00093145 | -0.0070773 | 0.28214 | -0.010408 | 0.06341 | 0.059748 | 0.010403 | -0.011974 | 72.5189 | 72.6425 | 6.1844 | -50.4593 | 72.7341 | -50.3311 | -50.4272 | -47.699 | 28.9444 | -50.2579 | 72.7203 | 72.6242 | -50.4547 | -50.5142 | -0.05951 | -0.15564 | 0.073242 | 122.9141 | -0.18768 | -0.032044 | -0.14191 | -0.18311 | -0.24262 | 0.059509 | 2.5726 | 0.013732 | 0.25635 | -0.036621 | 123.0057 | 122.7905 | 56.456 | -123.0881 | 122.9919 | 122.8958 | 79.216 | -123.175
3457.0156 | 123.1522 | -49.9649 | 72.8806 | -0.20615 | 0.0093717 | 0.070814 | 0.070731 | 0.13163 | -0.0026405 | -0.0070773 | -0.30533 | -0.011049 | 0.063196 | 0.057398 | 0.009549 | -0.013896 | 73.027 | 72.5876 | 6.1752 | -50.0336 | 72.9721 | -50.1068 | -50.1846 | -47.4655 | 29.2328 | -50.0244 | 72.9309 | 72.8027 | -50.2304 | -50.2441 | -0.14191 | -0.21973 | 0.091553 | 122.5525 | -0.068664 | 0.15106 | 0.14648 | -0.2655 | -0.27924 | 0.050354 | 2.4994 | -0.059509 | 0.21973 | -0.07782 | 122.937 | 122.9919 | 56.1401 | -123.0652 | 122.8958 | 122.7676 | 79.1977 | -123.1247
3458.0156 | 123.0881 | -49.53 | 73.3154 | 0.0914 | 0.0089443 | 0.07295 | 0.069663 | 0.128 | 0.00056395 | -0.0077183 | 0.16006 | -0.0095532 | 0.063837 | 0.055049 | 0.01019 | -0.013683 | 73.32 | 73.5489 | 6.5781 | -49.4934 | 73.6359 | -49.4476 | -49.5575 | -46.7011 | 29.3793 | -49.292 | 73.6176 | 73.4802 | -49.649 | -49.7131 | 0.082397 | -0.027466 | 0.32043 | 123.0789 | 0.036621 | 0.064087 | 0.004577 | -0.11902 | -0.18311 | 0.30212 | 2.829 | 0.23804 | 0.42114 | 0.16479 | 123.1659 | 122.85 | 56.1081 | -122.8729 | 123.1476 | 123.0103 | 78.9093 | -123.0286
3459.0156 | 123.1567 | -50.6058 | 72.2534 | -0.084076 | 0.0087307 | 0.069746 | 0.070944 | 0.12715 | -0.0019995 | -0.0079319 | -0.091705 | -0.012758 | 0.063196 | 0.051844 | 0.0086944 | -0.012187 | 72.1436 | 72.345 | 6.3858 | -50.6927 | 72.3495 | -50.7202 | -50.8347 | -48.23 | 28.6102 | -50.6195 | 72.3267 | 72.1939 | -50.8667 | -50.8896 | -0.11444 | -0.22888 | 0.09613 | 122.9507 | -0.086975 | 0.14191 | -0.10986 | -0.26093 | -0.28381 | 0.073242 | 2.3758 | -0.013733 | 0.27008 | -0.059509 | 122.9553 | 122.7493 | 56.9916 | -123.0881 | 122.9324 | 122.7997 | 79.216 | -123.143
3460.0156 | 123.1613 | -50.1663 | 72.7341 | -0.34348 | 0.010867 | 0.070387 | 0.07244 | 0.12971 | -0.00093145 | -0.0077183 | -0.12222 | -0.011689 | 0.065759 | 0.055689 | 0.010403 | -0.01411 | 72.5693 | 72.7798 | 6.5689 | -50.2625 | 72.8348 | -50.2808 | -50.3723 | -47.5845 | 29.0955 | -50.1663 | 72.7982 | 72.702 | -50.3815 | -50.4044 | -0.11444 | -0.20599 | 0.10071 | 122.9462 | -0.09613 | 0.10986 | -0.16479 | -0.21515 | -0.23804 | 0.064087 | 2.5818 | 0 | 0.23804 | -0.032044 | 123.0011 | 122.7356 | 56.7352 | -123.1064 | 122.9645 | 122.8683 | 79.2618 | -123.1384
3461.0156 | 123.1705 | -49.617 | 73.2742 | -0.084076 | 0.0097989 | 0.072736 | 0.071799 | 0.12993 | -0.0011451 | -0.0075047 | -0.068817 | -0.012971 | 0.062342 | 0.057612 | 0.0091216 | -0.01411 | 73.2468 | 73.4894 | 6.601 | -49.6078 | 73.4985 | -49.6033 | -49.6994 | -46.9391 | 29.7043 | -49.5758 | 73.3612 | 73.2056 | -49.8413 | -49.8779 | 0.013733 | -0.082398 | 0.2243 | 123.1064 | 0.009155 | 0.091553 | -0.027466 | -0.22431 | -0.26093 | 0.086975 | 2.6779 | 0.041198 | 0.30212 | -0.068665 | 123.1155 | 122.8638 | 56.218 | -122.9736 | 122.9782 | 122.8226 | 79.3213 | -123.1522
3462.0156 | 123.1247 | -49.3607 | 73.5214 | -0.023041 | 0.0085171 | 0.07295 | 0.069663 | 0.12779 | -0.00029045 | -0.0081455 | 0.15244 | -0.010621 | 0.06341 | 0.056758 | 0.0084808 | -0.013469 | 73.3749 | 73.5855 | 6.427 | -49.3378 | 73.7183 | -49.411 | -49.5209 | -46.7789 | 29.7821 | -49.3927 | 73.6496 | 73.5168 | -49.5621 | -49.5987 | -0.050354 | -0.16022 | 0.19684 | 122.9462 | 0.022888 | 0.1831 | -0.14648 | -0.20142 | -0.23804 | 0.12817 | 2.5818 | -0.032043 | 0.20599 | -0.004577 | 123.0789 | 122.7356 | 55.7877 | -123.0423 | 123.0103 | 122.8775 | 79.1428 | -123.1201
3463.0156 | 123.1659 | -48.5779 | 74.2538 | -0.053558 | 0.0078763 | 0.070387 | 0.069663 | 0.1295 | -0.00050425 | -0.0077183 | -0.045929 | -0.012544 | 0.063623 | 0.057398 | 0.0099762 | -0.013042 | 74.1531 | 74.3134 | 6.5918 | -48.8388 | 74.3408 | -48.7885 | -48.9166 | -45.9778 | 30.5786 | -48.6008 | 74.3591 | 74.2218 | -48.8205 | -48.8388 | -0.21057 | -0.33875 | 0.086975 | 122.8912 | -0.26093 | 0.07782 | -0.10071 | -0.24262 | -0.26093 | 0.10529 | 2.6001 | -0.022888 | 0.23804 | -0.032043 | 122.9187 | 122.731 | 55.1697 | -123.1705 | 122.937 | 122.7997 | 79.1565 | -123.0927
3464.0156 | 123.1338 | -48.5779 | 74.2996 | 0.0074768 | 0.0095853 | 0.0706 | 0.069876 | 0.12672 | -0.0013587 | -0.0081455 | 0.068512 | -0.010194 | 0.061487 | 0.056971 | 0.0093354 | -0.011119 | 73.8968 | 74.0982 | 6.7062 | -48.912 | 74.1898 | -48.8892 | -48.9487 | -46.106 | 30.4642 | -48.5458 | 74.3271 | 74.2172 | -48.8434 | -48.8892 | -0.31128 | -0.37079 | -0.10986 | 122.6761 | -0.33417 | 0.036621 | -0.40283 | -0.2655 | -0.31128 | 0.027465 | 2.4719 | 0.032044 | 0.34332 | -0.082398 | 122.7676 | 122.4747 | 55.2841 | -123.2483 | 122.905 | 122.7951 | 79.0421 | -123.1888
3465.0156 | 123.1018 | -50.6149 | 72.3084 | -0.23666 | 0.017276 | 0.071241 | 0.074362 | 0.12758 | 0.0052637 | -0.0064365 | -0.20615 | -0.010621 | 0.068537 | 0.057398 | 0.009549 | -0.016673 | 72.0795 | 72.1939 | 6.3171 | -50.7889 | 72.3724 | -50.7935 | -50.8804 | -48.0148 | 28.8208 | -50.6882 | 72.3953 | 72.2351 | -50.8621 | -50.8667 | -0.17853 | -0.2655 | 0.064087 | 122.8088 | -0.17395 | 0.091553 | -0.22888 | -0.24719 | -0.25177 | 0.086975 | 2.6001 | -0.073242 | 0.17853 | -0.073243 | 122.9874 | 122.6944 | 56.9321 | -123.1888 | 123.0103 | 122.85 | 79.4357 | -123.175
3466.0156 | 123.0881 | -49.292 | 73.613 | 0.12955 | 0.0091581 | 0.070814 | 0.069235 | 0.13014 | -7.6852e-05 | -0.0072911 | 0.31265 | -0.012971 | 0.063196 | 0.058253 | 0.009549 | -0.013042 | 73.4711 | 73.7137 | 6.6055 | -49.3286 | 73.7961 | -49.2691 | -49.3973 | -46.6827 | 30.011 | -49.292 | 73.7045 | 73.5855 | -49.5163 | -49.5255 | 0.022888 | -0.10529 | 0.18311 | 123.0057 | -0.036621 | 0.068665 | -0.14191 | -0.2243 | -0.23346 | 0.091553 | 2.6093 | 0 | 0.23346 | -0.027466 | 123.0881 | 122.7631 | 55.8975 | -123.0103 | 122.9965 | 122.8775 | 79.303 | -123.1384
3467.0156 | 123.1888 | -48.468 | 74.3912 | -0.076447 | 0.0091581 | 0.072309 | 0.072012 | 0.128 | -0.0011451 | -0.0053683 | 0.068512 | -0.012117 | 0.064905 | 0.054408 | 0.010617 | -0.012187 | 74.2996 | 74.5605 | 6.7978 | -48.5138 | 74.5422 | -48.5184 | -48.642 | -45.7993 | 30.7022 | -48.3536 | 74.5239 | 74.3912 | -48.6786 | -48.7106 | -0.050354 | -0.17395 | 0.15106 | 123.0286 | -0.045776 | 0.12817 | -0.091552 | -0.21057 | -0.24261 | 0.13275 | 2.6688 | 0.11444 | 0.35705 | 0 | 123.0103 | 122.7676 | 55.2658 | -123.0331 | 122.9919 | 122.8592 | 79.1702 | -123.1018
3468.0156 | 123.0698 | -48.9899 | 73.9334 | -0.19089 | 0.010867 | 0.071027 | 0.073508 | 0.12907 | -7.6852e-05 | -0.0070773 | -0.20615 | -0.0095532 | 0.064051 | 0.055903 | 0.010617 | -0.013896 | 73.9105 | 74.1074 | 6.7108 | -48.9395 | 74.1852 | -48.9349 | -49.0036 | -46.3577 | 30.2032 | -49.0356 | 74.0707 | 73.9243 | -49.1776 | -49.2188 | 0.054931 | -0.013733 | 0.25177 | 123.0972 | 0.050354 | 0.064087 | -0.022889 | -0.18768 | -0.22888 | 0.13733 | 2.6321 | -0.045777 | 0.1831 | -0.009156 | 123.175 | 122.9004 | 55.7007 | -122.937 | 123.0606 | 122.9141 | 79.1931 | -123.1522
3469.0156 | 123.143 | -49.4659 | 73.3795 | -0.084076 | 0.010226 | 0.073377 | 0.073508 | 0.12843 | -0.00093145 | -0.0087863 | -0.0077819 | -0.011049 | 0.063837 | 0.055262 | 0.01019 | -0.012401 | 73.6908 | 73.8785 | 6.6101 | -49.1776 | 73.9609 | -49.1318 | -49.2508 | -46.3898 | 30.0659 | -49.6582 | 73.7732 | 73.5168 | -49.5987 | -49.7086 | 0.33417 | 0.21515 | 0.58136 | 123.3444 | 0.28839 | 0.073242 | 0.31128 | -0.13275 | -0.24262 | 0.39368 | 3.0762 | -0.19226 | 0.050354 | 0.13733 | 123.4268 | 123.1567 | 56.076 | -122.6303 | 123.2391 | 122.9828 | 79.5319 | -123.0881
3470.0156 | 123.024 | -48.0148 | 74.9451 | -0.18326 | 0.014285 | 0.071668 | 0.074362 | 0.128 | 0.0016321 | -0.0079319 | -0.19852 | -0.011476 | 0.0664 | 0.059107 | 0.012753 | -0.014537 | 74.6475 | 74.826 | 6.7245 | -48.1796 | 75.0504 | -48.1339 | -48.2117 | -45.488 | 31.0776 | -48.1659 | 75.0641 | 74.9176 | -48.2483 | -48.2574 | -0.11902 | -0.19684 | 0.10529 | 122.8409 | -0.16479 | 0.032044 | -0.29755 | -0.23346 | -0.24261 | 0.11902 | 2.5269 | -0.15106 | 0.091552 | -0.027465 | 123.0652 | 122.6624 | 54.7394 | -123.1567 | 123.0789 | 122.9324 | 79.0924 | -123.2025
3471.0156 | 123.1796 | -48.6786 | 74.1989 | -0.091705 | 0.0072355 | 0.070814 | 0.069449 | 0.12629 | -0.0032813 | -0.0087863 | -0.11459 | -0.011689 | 0.062128 | 0.057398 | 0.0091216 | -0.011333 | 74.0845 | 74.3225 | 6.7474 | -48.7473 | 74.3546 | -48.7244 | -48.8434 | -45.9869 | 30.6152 | -48.6282 | 74.295 | 74.1669 | -48.8892 | -48.9075 | -0.045776 | -0.16479 | 0.15564 | 123.0011 | -0.068664 | 0.096131 | -0.11444 | -0.21057 | -0.22888 | 0.09613 | 2.6917 | 0.050354 | 0.27924 | -0.032044 | 123.0331 | 122.7631 | 55.426 | -123.0423 | 122.9736 | 122.8455 | 79.2938 | -123.1064
3472.0156 | 123.1064 | -49.5026 | 73.3475 | 0.12192 | 0.011722 | 0.072736 | 0.071158 | 0.13014 | -0.0019995 | -0.0070773 | 0.2211 | -0.011476 | 0.063837 | 0.055476 | 0.010617 | -0.010265 | 73.2971 | 73.4665 | 6.3492 | -49.5712 | 73.558 | -49.5163 | -49.6124 | -46.7697 | 30.5374 | -49.5071 | 73.5397 | 73.4299 | -49.6765 | -49.7406 | -0.013733 | -0.10986 | 0.21057 | 122.9691 | -0.068665 | 0.041199 | -0.050354 | -0.17395 | -0.23804 | 0.19226 | 2.7328 | -0.004578 | 0.23346 | 0.082398 | 123.0606 | 122.7997 | 55.8517 | -122.9599 | 123.0423 | 122.9324 | 80.04 | -123.0881
3473.0156 | 123.1476 | -49.3698 | 73.5168 | 0.015106 | 0.0061673 | 0.071027 | 0.071799 | 0.12928 | -0.0022131 | -0.0089999 | 0.030365 | -0.012117 | 0.064691 | 0.056117 | 0.0080536 | -0.013042 | 73.3475 | 73.5672 | 6.3766 | -49.4614 | 73.6954 | -49.4293 | -49.53 | -46.7056 | 30.5878 | -49.4064 | 73.5901 | 73.4985 | -49.5941 | -49.6307 | -0.059509 | -0.16022 | 0.17853 | 122.937 | -0.091553 | 0.068664 | -0.16937 | -0.2243 | -0.26093 | 0.073242 | 2.6642 | -0.036621 | 0.2243 | -0.018311 | 123.0652 | 122.7173 | 55.7465 | -123.0469 | 122.9599 | 122.8683 | 79.9576 | -123.1476
3474.0156 | 123.1338 | -49.4705 | 73.4299 | 0.14481 | 0.0091581 | 0.06825 | 0.069663 | 0.12629 | -0.00029045 | -0.0068637 | 0.060883 | -0.011476 | 0.061701 | 0.055476 | 0.010617 | -0.01411 | 73.2056 | 73.4161 | 6.2485 | -49.6216 | 73.4985 | -49.6124 | -49.7131 | -46.8475 | 30.3497 | -49.5163 | 73.4756 | 73.3841 | -49.704 | -49.7223 | -0.14191 | -0.24262 | 0.068664 | 122.8867 | -0.15106 | 0.091553 | -0.22431 | -0.23346 | -0.25177 | 0.045776 | 2.623 | -0.045776 | 0.20599 | -0.045777 | 122.9691 | 122.6761 | 55.719 | -123.143 | 122.9462 | 122.8546 | 79.8203 | -123.1522
3475.0312 | 123.0515 | -48.7976 | 74.1623 | -0.0383 | 0.017062 | 0.062696 | 0.07543 | 0.12886 | 0.0069727 | -0.0047275 | -0.091705 | -0.009126 | 0.066614 | 0.056971 | 0.012326 | -0.016246 | 73.9288 | 74.0433 | 6.4499 | -48.9578 | 74.2218 | -48.9166 | -48.999 | -46.2021 | 30.9402 | -48.967 | 74.2035 | 74.0799 | -49.0219 | -49.054 | -0.11902 | -0.20142 | 0.05951 | 122.8409 | -0.16022 | 0.041198 | -0.23346 | -0.22431 | -0.25635 | 0.041199 | 2.5955 | -0.16937 | 0.086975 | -0.082397 | 123.0194 | 122.7264 | 55.2475 | -123.1613 | 123.0011 | 122.8775 | 79.7379 | -123.2162
3476.0156 | 123.1155 | -49.4385 | 73.4848 | 0.20584 | 0.012149 | 0.069959 | 0.072226 | 0.13035 | -0.0026405 | -0.0085727 | 0.20584 | -0.011903 | 0.065119 | 0.057612 | 0.0093354 | -0.011974 | 73.4665 | 73.6954 | 6.7841 | -49.411 | 73.6954 | -49.3881 | -49.4888 | -46.7514 | 30.4779 | -49.411 | 73.5626 | 73.4619 | -49.6445 | -49.6857 | 0.050354 | -0.050354 | 0.21057 | 123.1339 | 0.027466 | 0.07782 | -0.01831 | -0.20599 | -0.24719 | 0.07782 | 2.6871 | 0.027466 | 0.27466 | -0.022888 | 123.1339 | 122.905 | 56.2225 | -122.9736 | 123.0011 | 122.9004 | 79.9164 | -123.1705
3477.0156 | 123.1064 | -49.411 | 73.5031 | 0.030365 | 0.0085171 | 0.072309 | 0.069876 | 0.12758 | -0.0030677 | -0.0077183 | 0.068512 | -0.009126 | 0.063623 | 0.057185 | 0.008908 | -0.012187 | 73.2376 | 73.4344 | 6.4636 | -49.5209 | 73.5855 | -49.5163 | -49.6262 | -46.8384 | 30.5283 | -49.4202 | 73.5397 | 73.4528 | -49.6216 | -49.6628 | -0.10528 | -0.21515 | 0.082397 | 122.8455 | -0.10986 | 0.10529 | -0.2655 | -0.21057 | -0.25177 | 0.036621 | 2.5726 | -0.009155 | 0.24262 | -0.050354 | 122.9965 | 122.6486 | 55.8746 | -123.1293 | 122.9507 | 122.8638 | 79.9393 | -123.1659
3478.0156 | 123.0927 | -49.0356 | 73.8602 | 0.17532 | 0.013003 | 0.069532 | 0.07244 | 0.13057 | -0.0013587 | -0.0070773 | 0.19058 | -0.0099806 | 0.064264 | 0.058467 | 0.008908 | -0.012401 | 73.5992 | 73.7686 | 6.3766 | -49.2371 | 73.8327 | -49.2233 | -49.3286 | -46.3806 | 30.8258 | -49.0128 | 73.8968 | 73.8144 | -49.2645 | -49.2874 | -0.18768 | -0.29297 | -0.027465 | 122.8043 | -0.20142 | 0.091552 | -0.26093 | -0.22888 | -0.25177 | 0.036622 | 2.655 | 0.022889 | 0.27466 | -0.045776 | 122.8683 | 122.6349 | 55.4123 | -123.1888 | 122.9324 | 122.85 | 79.8615 | -123.1476
3479.0156 | 123.111 | -49.5483 | 73.3475 | 0.068512 | 0.010867 | 0.070173 | 0.070517 | 0.12758 | -0.0037085 | -0.0077183 | 0.12955 | -0.011049 | 0.064051 | 0.055262 | 0.0084808 | -0.01176 | 73.32 | 73.4894 | 6.6833 | -49.5026 | 73.6404 | -49.4843 | -49.617 | -46.7926 | 30.4276 | -49.6353 | 73.4985 | 73.3566 | -49.7589 | -49.791 | 0.064087 | -0.068664 | 0.29297 | 123.0377 | 0.045777 | 0.11444 | -0.027466 | -0.21057 | -0.24261 | 0.15106 | 2.7557 | -0.086975 | 0.15564 | 0.009155 | 123.1888 | 122.8683 | 56.2317 | -122.9645 | 123.0469 | 122.905 | 79.9759 | -123.1384
3480.0156 | 123.0881 | -49.6719 | 73.2697 | -0.23666 | 0.010867 | 0.073164 | 0.073721 | 0.13014 | -0.00071785 | -0.0087863 | -0.19089 | -0.011476 | 0.067255 | 0.055903 | 0.010831 | -0.015178 | 73.1277 | 73.3109 | 6.7566 | -49.6902 | 73.4024 | -49.736 | -49.855 | -46.9666 | 30.3864 | -49.8047 | 73.3475 | 73.2422 | -49.9146 | -49.942 | -0.064087 | -0.18311 | 0.13275 | 122.9828 | -0.018311 | 0.16479 | -0.14191 | -0.24262 | -0.27008 | 0.07782 | 2.7054 | -0.13275 | 0.13733 | -0.027466 | 123.0743 | 122.7997 | 56.4285 | -123.1247 | 123.0194 | 122.9141 | 80.0583 | -123.2117
3481.0156 | 123.0789 | -49.6216 | 73.2925 | 0.060882 | 0.010226 | 0.071455 | 0.07009 | 0.13185 | -0.0024269 | -0.010068 | 0.10666 | -0.012117 | 0.065332 | 0.055262 | 0.0097626 | -0.012614 | 73.1277 | 73.3154 | 6.8573 | -49.6902 | 73.4253 | -49.6582 | -49.7498 | -46.8704 | 30.4047 | -49.498 | 73.4344 | 73.2925 | -49.8276 | -49.8642 | -0.036621 | -0.12817 | 0.13275 | 122.937 | -0.068665 | 0.059509 | -0.16479 | -0.20599 | -0.24262 | 0.14191 | 2.7512 | 0.1236 | 0.36621 | 0 | 123.0469 | 122.7493 | 56.4789 | -123.0423 | 123.056 | 122.9141 | 80.0262 | -123.1567
3482.0156 | 123.1247 | -49.2874 | 73.526 | 0.16769 | 0.013644 | 0.069532 | 0.070944 | 0.13099 | 0.0014185 | -0.0081455 | 0.64072 | -0.011262 | 0.062555 | 0.058253 | 0.011044 | -0.016246 | 73.7778 | 73.9243 | 7.1045 | -49.3011 | 73.9517 | -49.1089 | -49.2096 | -46.2845 | 30.9402 | -49.3149 | 73.9334 | 73.7228 | -49.4019 | -49.5071 | 0.17853 | 0.07782 | 0.42572 | 123.2117 | -0.013732 | -0.091552 | 0.25177 | -0.11444 | -0.21973 | 0.40741 | 3.0029 | -0.027465 | 0.19226 | 0.19684 | 123.2391 | 123.0652 | 56.3919 | -122.7356 | 123.2208 | 123.0103 | 80.2277 | -123.0331
3483.0156 | 123.1155 | -48.9807 | 73.9243 | 0.16769 | 0.011722 | 0.069532 | 0.071799 | 0.128 | 0.00056395 | -0.0070773 | 0.18295 | -0.010194 | 0.062769 | 0.057826 | 0.0097626 | -0.012187 | 73.7549 | 73.9288 | 7.2464 | -49.118 | 74.0112 | -49.086 | -49.1776 | -46.2662 | 31.0043 | -48.9304 | 73.9838 | 73.8876 | -49.1913 | -49.2416 | -0.10529 | -0.19684 | 0.086975 | 122.9095 | -0.13733 | 0.059509 | -0.16937 | -0.21057 | -0.26093 | 0.05951 | 2.7145 | 0.050354 | 0.31128 | -0.036621 | 122.9919 | 122.7356 | 56.2271 | -123.1018 | 122.9645 | 122.8683 | 79.985 | -123.1659
3484.0156 | 123.1155 | -49.5117 | 73.3795 | 0.2211 | 0.017703 | 0.071668 | 0.072867 | 0.13313 | 0.0033411 | -0.0051547 | 0.15244 | -0.010194 | 0.062128 | 0.057826 | 0.01019 | -0.01411 | 73.3704 | 73.494 | 6.9489 | -49.5392 | 73.5809 | -49.5163 | -49.6353 | -46.8155 | 30.4871 | -49.6307 | 73.4161 | 73.3063 | -49.7589 | -49.7864 | -0.004577 | -0.1236 | 0.20142 | 123.0057 | -0.027466 | 0.09613 | -0.009156 | -0.24719 | -0.27466 | 0.036621 | 2.6962 | -0.11902 | 0.15564 | -0.073243 | 123.0927 | 122.8821 | 56.4606 | -123.0148 | 122.9279 | 122.818 | 79.9988 | -123.1659
3485.0156 | 123.1522 | -51.5533 | 71.3058 | 0.11429 | 0.011081 | 0.071241 | 0.070517 | 0.128 | -0.0034949 | -0.0079319 | 0.18295 | -0.010194 | 0.06106 | 0.055903 | 0.00784 | -0.012187 | 71.3562 | 71.4752 | 6.6971 | -51.535 | 71.5897 | -51.4801 | -51.622 | -48.7061 | 28.8483 | -51.535 | 71.5439 | 71.4432 | -51.6907 | -51.7548 | 0.073242 | -0.068664 | 0.28381 | 123.0286 | 0.018311 | 0.086975 | 0.050354 | -0.13733 | -0.20142 | 0.23804 | 2.8473 | 0.018311 | 0.21973 | 0.13733 | 123.143 | 122.9095 | 58.2504 | -122.9279 | 123.0972 | 122.9965 | 80.4016 | -123.0606
3486.0156 | 123.1201 | -49.6811 | 73.2285 | 0.17532 | 0.015567 | 0.068037 | 0.069235 | 0.12886 | 0.0029137 | -0.0062229 | 0.13718 | -0.0086988 | 0.062769 | 0.055262 | 0.012967 | -0.015605 | 73.1964 | 73.288 | 6.7932 | -49.7086 | 73.4802 | -49.6811 | -49.7772 | -46.9711 | 30.3131 | -49.7818 | 73.3475 | 73.2147 | -49.9054 | -49.9191 | 0 | -0.096131 | 0.25177 | 122.9691 | -0.027466 | 0.068665 | -0.032044 | -0.22431 | -0.23804 | 0.11902 | 2.71 | -0.10071 | 0.13733 | -0.013733 | 123.1613 | 122.8775 | 56.4743 | -123.0057 | 123.0286 | 122.8958 | 79.9942 | -123.1476
3487.0156 | 123.1064 | -49.7681 | 73.0682 | 0.13718 | 0.013217 | 0.071668 | 0.070303 | 0.12758 | 0.00035035 | -0.0053683 | 0.28214 | -0.01233 | 0.063196 | 0.056971 | 0.01019 | -0.013469 | 73.1094 | 73.2925 | 6.9534 | -49.7269 | 73.3292 | -49.7177 | -49.8367 | -46.8704 | 30.4138 | -49.6811 | 73.3566 | 73.2285 | -49.8459 | -49.9237 | 0.050354 | -0.068665 | 0.26093 | 123.0606 | 0.041198 | 0.10986 | 0.041199 | -0.07782 | -0.15564 | 0.28839 | 2.8976 | 0.086975 | 0.24262 | 0.16022 | 123.0972 | 122.8775 | 56.7215 | -122.905 | 123.1247 | 122.9965 | 80.1819 | -122.9919
3488.0156 | 123.1201 | -49.5712 | 73.3292 | 0.16769 | 0.01813 | 0.0706 | 0.073294 | 0.13078 | 0.0022729 | -0.0077183 | 0.17532 | -0.0086988 | 0.065759 | 0.056117 | 0.011685 | -0.014323 | 73.1049 | 73.2056 | 6.6833 | -49.7864 | 73.3795 | -49.7269 | -49.8322 | -46.8704 | 30.2673 | -49.7452 | 73.3612 | 73.2559 | -49.8596 | -49.855 | -0.15564 | -0.26093 | 0.050354 | 122.7768 | -0.21515 | 0.045776 | -0.22431 | -0.28839 | -0.28381 | 0.032043 | 2.7008 | -0.17395 | 0.10986 | -0.073243 | 122.9507 | 122.6761 | 56.2546 | -123.1613 | 122.9324 | 122.8271 | 79.8386 | -123.1842
3489.0156 | 123.1796 | -50.2029 | 72.6654 | -0.076447 | 0.013003 | 0.070387 | 0.068381 | 0.13078 | -7.6852e-05 | -0.0045139 | 0.23636 | -0.011049 | 0.063837 | 0.055476 | 0.011685 | -0.013042 | 72.4777 | 72.6379 | 6.9901 | -50.3586 | 72.7066 | -50.322 | -50.4272 | -47.5021 | 29.8965 | -50.2304 | 72.7295 | 72.6059 | -50.4593 | -50.4959 | -0.11902 | -0.2243 | 0.041199 | 122.8409 | -0.15564 | 0.068664 | -0.18768 | -0.25635 | -0.29297 | 0.064087 | 2.7008 | -0.027466 | 0.2655 | -0.059509 | 122.9095 | 122.6807 | 57.193 | -123.0927 | 122.9324 | 122.8088 | 80.0995 | -123.1613
3490.0156 | 123.0652 | -50.1068 | 72.8073 | 0.13718 | 0.018771 | 0.070173 | 0.072012 | 0.13014 | 0.0018457 | -0.0064365 | 0.13718 | -0.0089124 | 0.065759 | 0.055903 | 0.010831 | -0.013896 | 72.7203 | 72.789 | 7.4203 | -50.1343 | 73.0637 | -50.0885 | -50.2167 | -47.3465 | 29.9011 | -50.3036 | 72.9538 | 72.8394 | -50.3128 | -50.3448 | 0.018311 | -0.10986 | 0.25635 | 122.8958 | -0.027465 | 0.082398 | -0.086975 | -0.20599 | -0.23804 | 0.14648 | 2.7603 | -0.19684 | 0.041199 | 0.032043 | 123.1705 | 122.8271 | 57.5272 | -123.024 | 123.0606 | 122.9462 | 80.0079 | -123.1522
3491.0156 | 123.143 | -50.473 | 72.3679 | 0.20584 | 0.014926 | 0.069959 | 0.068167 | 0.12736 | -0.00093145 | -0.0053683 | 0.24399 | -0.0095532 | 0.062982 | 0.05633 | 0.010831 | -0.011119 | 72.3175 | 72.4731 | 7.164 | -50.5554 | 72.5372 | -50.5325 | -50.6241 | -47.7493 | 29.718 | -50.4593 | 72.4503 | 72.3862 | -50.7156 | -50.7294 | -0.05951 | -0.15106 | 0.16937 | 122.9462 | -0.082398 | 0.068664 | -0.050354 | -0.24262 | -0.25635 | 0.082397 | 2.7237 | 0.013732 | 0.27008 | 0.01831 | 123.0103 | 122.7905 | 57.637 | -122.9919 | 122.9233 | 122.8592 | 80.191 | -123.0972
3492.0156 | 123.1247 | -49.855 | 73.0545 | 0.14481 | 0.018771 | 0.071455 | 0.070944 | 0.12822 | 0.0039819 | -0.0053683 | 0.16769 | -0.0082716 | 0.068964 | 0.056758 | 0.010617 | -0.011974 | 72.8485 | 72.9721 | 7.1045 | -49.9832 | 73.1873 | -49.9512 | -50.0381 | -47.1222 | 30.1849 | -49.8962 | 73.1232 | 73.0453 | -50.0885 | -50.1205 | -0.09613 | -0.18311 | 0.13275 | 122.8271 | -0.12817 | 0.054932 | -0.20599 | -0.23346 | -0.2655 | 0.068665 | 2.7328 | -0.041198 | 0.2243 | -0.009155 | 123.0423 | 122.7036 | 56.9595 | -123.0927 | 122.9782 | 122.9004 | 80.04 | -123.175
3493.0156 | 123.143 | -49.8779 | 73.0179 | 0.12955 | 0.01514 | 0.068464 | 0.071158 | 0.12715 | 0.00035035 | -0.0055821 | 0.19821 | -0.0089124 | 0.065759 | 0.058894 | 0.011258 | -0.012828 | 72.8851 | 72.9996 | 6.6193 | -49.9832 | 73.1323 | -49.9374 | -50.0702 | -47.0901 | 30.2032 | -49.9329 | 73.0911 | 73.0087 | -50.1022 | -50.1114 | -0.059509 | -0.19226 | 0.11444 | 122.8775 | -0.10529 | 0.086975 | -0.13275 | -0.2243 | -0.23346 | 0.073242 | 2.7878 | -0.054931 | 0.17853 | -0.009155 | 123.0103 | 122.7631 | 56.4972 | -123.0881 | 122.9691 | 122.8867 | 80.0812 | -123.1293
3494.0156 | 123.0057 | -50.1526 | 72.8256 | 0.25925 | 0.017062 | 0.069746 | 0.073294 | 0.12843 | 0.0041955 | -0.0057957 | 0.15244 | -0.0067762 | 0.066187 | 0.055903 | 0.01019 | -0.014964 | 72.5784 | 72.6517 | 6.3309 | -50.267 | 72.9218 | -50.2213 | -50.3494 | -47.4289 | 29.8599 | -50.2396 | 72.908 | 72.8256 | -50.3403 | -50.386 | -0.068664 | -0.19684 | 0.09613 | 122.8043 | -0.11444 | 0.082397 | -0.24719 | -0.18768 | -0.23346 | 0.082397 | 2.7237 | -0.086975 | 0.14648 | 0 | 123.0743 | 122.731 | 56.4835 | -123.175 | 123.0606 | 122.9782 | 80.0125 | -123.2117
3495.0156 | 123.1384 | -49.7818 | 73.0453 | 0.15244 | 0.014926 | 0.0706 | 0.068381 | 0.13057 | 0.00099115 | -0.0062229 | 0.21347 | -0.0086988 | 0.063623 | 0.057612 | 0.009549 | -0.012401 | 72.9767 | 73.1003 | 6.4316 | -49.9008 | 73.1827 | -49.8871 | -49.9924 | -47.0078 | 30.2307 | -49.8093 | 73.1644 | 73.0774 | -50.0061 | -50.061 | -0.10529 | -0.21057 | 0.13733 | 122.8821 | -0.11902 | 0.091553 | -0.068664 | -0.22431 | -0.27924 | 0.11902 | 2.774 | -0.027466 | 0.25177 | 0.032044 | 122.9645 | 122.7585 | 56.2134 | -123.0377 | 122.9462 | 122.8592 | 80.0125 | -123.1064
3496.0156 | 123.0469 | -50.2029 | 72.7707 | 0.14481 | 0.018985 | 0.069105 | 0.071372 | 0.13035 | 0.0024865 | -0.0064365 | -3.0367 | -0.0082716 | 0.06875 | 0.057185 | 0.009549 | -0.014537 | 72.5693 | 72.6974 | 6.1203 | -50.2441 | 72.963 | -50.2121 | -50.2808 | -47.4152 | 29.8096 | -50.3448 | 72.908 | 72.8256 | -50.3723 | -50.3998 | -0.009155 | -0.07782 | 0.19226 | 122.9004 | -0.041199 | 0.036621 | -0.20142 | -0.16937 | -0.19684 | 0.13733 | 2.7878 | -0.14191 | 0.054931 | 0.054932 | 123.1659 | 122.7722 | 56.3232 | -123.0515 | 123.111 | 123.0286 | 80.0125 | -123.1705
3497.0156 | 123.1476 | -49.7543 | 73.114 | 0.25925 | 0.015994 | 0.071241 | 0.069235 | 0.13057 | -0.00071785 | -0.0051547 | 0.23636 | -0.0084852 | 0.066828 | 0.056758 | 0.011258 | -0.013469 | 72.963 | 73.082 | 6.6513 | -49.8962 | 73.233 | -49.855 | -49.9695 | -46.9574 | 30.3131 | -49.8001 | 73.2513 | 73.1598 | -49.9558 | -49.9924 | -0.10071 | -0.21515 | 0.11902 | 122.8363 | -0.14191 | 0.073242 | -0.15106 | -0.20142 | -0.23804 | 0.13733 | 2.7969 | -0.045777 | 0.19226 | 0.045776 | 122.9874 | 122.7173 | 56.4056 | -123.0835 | 123.0057 | 122.9141 | 80.0674 | -123.1064
3498.0156 | 123.0789 | -50.6149 | 72.2946 | -2.8993 | 0.016421 | 0.069319 | 0.074362 | 0.13121 | 0.0033411 | -0.0057957 | 0.14481 | -0.0093396 | 0.064905 | 0.054835 | 0.0093354 | -0.010051 | 72.0657 | 72.2488 | 6.2714 | -50.7339 | 72.4777 | -50.6561 | -50.7339 | -47.8912 | 29.425 | -50.7706 | 72.4136 | 72.3541 | -50.853 | -50.8942 | -0.041199 | -0.11902 | 0.1831 | 122.8638 | -0.11902 | 0 | -0.22888 | -0.23804 | -0.27924 | 0.11902 | 2.7237 | -0.15564 | 0.1236 | 0.059509 | 123.0927 | 122.6807 | 56.8863 | -123.0286 | 123.0286 | 122.9691 | 80.04 | -123.1888
3499.0156 | 123.1476 | -49.4888 | 73.3658 | 0.19821 | 0.01514 | 0.072096 | 0.071799 | 0.12971 | -0.0028541 | -0.0079319 | 0.25162 | -0.0099806 | 0.065973 | 0.058253 | 0.011044 | -0.011974 | 73.3109 | 73.4116 | 6.7017 | -49.5895 | 73.5352 | -49.5667 | -49.6902 | -46.7011 | 30.5511 | -49.4751 | 73.4802 | 73.4482 | -49.6674 | -49.7131 | -0.077819 | -0.20142 | 0.16937 | 122.9004 | -0.10071 | 0.10071 | -0.054932 | -0.17853 | -0.2243 | 0.11444 | 2.7878 | 0.013733 | 0.23804 | 0.082397 | 123.024 | 122.7997 | 56.1905 | -123.056 | 122.9691 | 122.937 | 80.04 | -123.0789
3500.0156 | 123.0011 | -49.8047 | 73.1506 | 0.053253 | 0.017276 | 0.071027 | 0.073935 | 0.12864 | 0.0014185 | -0.0072911 | -0.015411 | -0.010194 | 0.065759 | 0.05633 | 0.009549 | -0.01411 | 73.0087 | 73.114 | 6.3171 | -49.8367 | 73.3337 | -49.8001 | -49.8962 | -47.0673 | 30.2902 | -49.8871 | 73.2788 | 73.1964 | -50.0107 | -50.0473 | 0.004577 | -0.091553 | 0.18311 | 122.9187 | -0.032044 | 0.059509 | -0.14191 | -0.20599 | -0.24262 | 0.12817 | 2.7374 | -0.082398 | 0.16022 | 0.045776 | 123.1384 | 122.8134 | 56.1218 | -123.0469 | 123.0835 | 123.0011 | 80.0949 | -123.1979
3501.0156 | 123.0515 | -49.4156 | 73.526 | 0.083771 | 0.018771 | 0.068891 | 0.073935 | 0.13121 | 0.0035547 | -0.0079319 | 0.13718 | -0.0078442 | 0.065546 | 0.055689 | 0.0097626 | -0.012401 | 73.3795 | 73.5123 | 6.3766 | -49.4476 | 73.7366 | -49.4019 | -49.5117 | -46.669 | 30.7205 | -49.4202 | 73.6908 | 73.6176 | -49.5804 | -49.6307 | 0.013733 | -0.096131 | 0.21057 | 122.9279 | -0.032044 | 0.064087 | -0.14648 | -0.16479 | -0.21515 | 0.1648 | 2.7466 | -0.004578 | 0.21057 | 0.091553 | 123.1522 | 122.7951 | 55.7922 | -123.0377 | 123.1064 | 123.0331 | 80.1361 | -123.1567
3502.0156 | 123.0148 | -50.8163 | 72.1298 | 0.14481 | 0.021976 | 0.070173 | 0.073294 | 0.12758 | 0.0024865 | -0.0068637 | 0.15244 | -0.0076306 | 0.065546 | 0.058467 | 0.011258 | -0.015819 | 71.9147 | 71.9925 | 5.8136 | -50.9079 | 72.2626 | -50.885 | -50.972 | -48.111 | 29.5578 | -50.9583 | 72.2305 | 72.171 | -51.0361 | -51.0773 | -0.068665 | -0.15564 | 0.13275 | 122.8088 | -0.091553 | 0.064087 | -0.21515 | -0.21973 | -0.26093 | 0.10071 | 2.7054 | -0.14191 | 0.11902 | 0.041199 | 123.0789 | 122.731 | 56.6299 | -123.1018 | 123.0469 | 122.9874 | 80.3741 | -123.2071
3503.0156 | 123.111 | -49.5438 | 73.3841 | 0.12192 | 0.021335 | 0.070173 | 0.071585 | 0.13121 | 0.0012047 | -0.0068637 | 0.2211 | -0.007417 | 0.0664 | 0.058039 | 0.011472 | -0.011974 | 73.0591 | 73.1827 | 6.3446 | -49.7314 | 73.4024 | -49.6994 | -49.8047 | -46.788 | 30.7434 | -49.5529 | 73.4711 | 73.4116 | -49.7452 | -49.7635 | -0.15564 | -0.26093 | 0.018311 | 122.7264 | -0.18768 | 0.073242 | -0.32501 | -0.20142 | -0.21973 | 0.086975 | 2.7557 | -0.009155 | 0.21057 | 0.027466 | 122.9462 | 122.6028 | 55.8884 | -123.1888 | 123.0148 | 122.9553 | 80.2872 | -123.1476
3504.0156 | 123.0331 | -49.3149 | 73.6588 | 0.022736 | 0.019412 | 0.070173 | 0.074576 | 0.12736 | 0.0027001 | -0.0038731 | 0.076141 | -0.007417 | 0.069177 | 0.057398 | 0.011685 | -0.012828 | 73.3612 | 73.4756 | 6.0059 | -49.4522 | 73.7366 | -49.4156 | -49.53 | -46.5454 | 31.0318 | -49.4156 | 73.7869 | 73.6908 | -49.5117 | -49.5255 | -0.10071 | -0.21515 | 0.07782 | 122.7905 | -0.13733 | 0.07782 | -0.29755 | -0.19684 | -0.21057 | 0.12817 | 2.7695 | -0.10071 | 0.10986 | 0.032044 | 123.0515 | 122.6761 | 55.3207 | -123.1888 | 123.1018 | 123.0057 | 80.3467 | -123.1842
3505.0156 | 123.1476 | -49.6765 | 73.1598 | 0.16769 | 0.016635 | 0.070387 | 0.069876 | 0.12758 | -0.0019995 | -0.0077183 | 0.28214 | -0.009126 | 0.065546 | 0.057612 | 0.010403 | -0.011974 | 73.1369 | 73.2605 | 5.2322 | -49.6857 | 73.4299 | -49.6582 | -49.7818 | -46.8384 | 30.6839 | -49.7223 | 73.3475 | 73.2559 | -49.8596 | -49.9237 | 0.018311 | -0.10529 | 0.27008 | 122.937 | -0.009155 | 0.09613 | -0.022888 | -0.18311 | -0.24719 | 0.18768 | 2.8381 | -0.045776 | 0.20142 | 0.09613 | 123.1064 | 122.8134 | 54.9088 | -122.9416 | 123.024 | 122.9324 | 80.3604 | -123.0835
3506.0156 | 123.0194 | -50.4593 | 72.5052 | 0.076141 | 0.018558 | 0.072736 | 0.072226 | 0.12758 | 0.0020593 | -0.0070773 | 0.13718 | -0.0078442 | 0.0664 | 0.057185 | 0.010831 | -0.015178 | 72.2168 | 72.3495 | 4.8706 | -50.5692 | 72.6334 | -50.5554 | -50.6332 | -47.7219 | 29.8279 | -50.5875 | 72.6059 | 72.5281 | -50.6424 | -50.679 | -0.09613 | -0.17395 | 0.12817 | 122.8088 | -0.10986 | 0.064087 | -0.28839 | -0.1831 | -0.21973 | 0.10071 | 2.7374 | -0.12817 | 0.091553 | 0.022888 | 123.0927 | 122.6761 | 55.3299 | -123.1384 | 123.0652 | 122.9874 | 80.2872 | -123.1842
3507.0156 | 123.0927 | -49.8779 | 73.0453 | 0.13718 | 0.016208 | 0.069319 | 0.071372 | 0.12971 | -0.0013587 | -0.0064365 | 0.22873 | -0.0097668 | 0.068109 | 0.056758 | 0.01019 | -0.011119 | 72.8989 | 73.0499 | 4.9393 | -49.9237 | 73.2376 | -49.8779 | -49.9786 | -47.0169 | 30.4138 | -49.9741 | 73.1781 | 73.082 | -50.0702 | -50.1022 | 0 | -0.10071 | 0.19226 | 122.9279 | -0.045776 | 0.054932 | -0.14648 | -0.19226 | -0.2243 | 0.13275 | 2.861 | -0.09613 | 0.12817 | 0.036621 | 123.1155 | 122.7768 | 54.8172 | -123.024 | 123.056 | 122.9599 | 80.2917 | -123.1476
3508.0156 | 123.0377 | -49.4019 | 73.5718 | 0.037994 | 0.020267 | 0.069746 | 0.076498 | 0.13185 | 0.00013675 | -0.0053683 | 0.09903 | -0.0089124 | 0.066614 | 0.058039 | 0.011258 | -0.012187 | 73.2422 | 73.3429 | 4.8523 | -49.5987 | 73.5855 | -49.5483 | -49.6811 | -46.6736 | 30.6473 | -49.4522 | 73.6359 | 73.5855 | -49.6307 | -49.6811 | -0.14649 | -0.27924 | 0.013733 | 122.7448 | -0.19684 | 0.082397 | -0.32959 | -0.22888 | -0.27924 | 0.064087 | 2.7283 | -0.050354 | 0.22888 | 0.013733 | 122.9874 | 122.644 | 54.2541 | -123.2529 | 123.0377 | 122.9874 | 80.0491 | -123.2529
3509.0156 | 123.0972 | -49.7543 | 73.1781 | 0.12192 | 0.017703 | 0.072096 | 0.07244 | 0.12864 | 0.00056395 | -0.0094273 | 0.25925 | -0.0076306 | 0.064264 | 0.05868 | 0.00784 | -0.01176 | 73.0499 | 73.201 | 4.8889 | -49.7635 | 73.4482 | -49.7131 | -49.8276 | -46.9482 | 30.4733 | -49.9191 | 73.3063 | 73.2422 | -49.9695 | -49.9832 | 0.041198 | -0.073243 | 0.27008 | 122.9553 | -0.009156 | 0.064087 | -0.12817 | -0.21515 | -0.22888 | 0.12817 | 2.8061 | -0.16479 | 0.064087 | 0.064086 | 123.2025 | 122.8043 | 54.6432 | -123.0057 | 123.0606 | 122.9965 | 80.2277 | -123.1613
3510.0156 | 123.0698 | -49.823 | 73.1277 | -0.023041 | 0.021121 | 0.069746 | 0.073294 | 0.12886 | 0.0024865 | -0.0049411 | 0.045624 | -0.0095532 | 0.066187 | 0.056971 | 0.011685 | -0.011974 | 72.9172 | 73.0362 | 4.9393 | -49.9283 | 73.2468 | -49.8779 | -49.9924 | -47.0535 | 30.3085 | -49.9374 | 73.233 | 73.1598 | -50.0381 | -50.0885 | -0.054932 | -0.16937 | 0.11902 | 122.8592 | -0.10529 | 0.064087 | -0.21057 | -0.21515 | -0.2655 | 0.10528 | 2.7695 | -0.11444 | 0.15106 | 0.032043 | 123.0698 | 122.7402 | 54.7623 | -123.1201 | 123.056 | 122.9828 | 80.1315 | -123.2162
3511.0156 | 123.0331 | -50.4364 | 72.4594 | -0.19089 | 0.019626 | 0.071668 | 0.073081 | 0.12886 | 0.0012047 | -0.0051547 | 0.19058 | -0.011049 | 0.066614 | 0.055689 | 0.011472 | -0.012401 | 72.29 | 72.3953 | 4.9393 | -50.5737 | 72.6471 | -50.5371 | -50.6378 | -47.6898 | 29.7318 | -50.5829 | 72.5601 | 72.5052 | -50.6699 | -50.7156 | -0.10071 | -0.20142 | 0.18768 | 122.8317 | -0.13733 | 0.064087 | -0.16937 | -0.23346 | -0.27924 | 0.10071 | 2.7466 | -0.14649 | 0.13275 | 0.045776 | 123.0835 | 122.7264 | 55.3757 | -123.0972 | 122.9965 | 122.9416 | 80.1682 | -123.175
3512.0156 | 123.0331 | -50.0793 | 72.8714 | 0.037994 | 0.018771 | 0.069746 | 0.073508 | 0.13057 | 0.0031273 | -0.0051547 | 0.15244 | -0.0086988 | 0.0664 | 0.057398 | 0.010403 | -0.012187 | 72.5784 | 72.67 | 4.9026 | -50.235 | 72.9492 | -50.1984 | -50.2945 | -47.3557 | 30.0293 | -50.1892 | 72.9721 | 72.9126 | -50.3036 | -50.3174 | -0.11902 | -0.21515 | 0.07782 | 122.7493 | -0.15564 | 0.05951 | -0.29297 | -0.2243 | -0.23804 | 0.10071 | 2.7237 | -0.10986 | 0.12817 | 0.041199 | 123.0286 | 122.6578 | 54.982 | -123.1659 | 123.0515 | 122.9919 | 80.1086 | -123.1888
3513.0156 | 123.0743 | -49.8459 | 73.0682 | 0.13718 | 0.01813 | 0.070387 | 0.070731 | 0.128 | -7.6852e-05 | -0.0075047 | 0.22873 | -0.0099806 | 0.067041 | 0.058039 | 0.0097626 | -0.01176 | 72.8485 | 72.9996 | 5.0995 | -49.9558 | 73.233 | -49.942 | -50.0244 | -47.0215 | 30.2856 | -49.942 | 73.1506 | 73.1186 | -50.0656 | -50.0839 | -0.096131 | -0.17853 | 0.16479 | 122.8455 | -0.10986 | 0.068664 | -0.21973 | -0.21973 | -0.23804 | 0.082398 | 2.8244 | -0.096131 | 0.14191 | 0.050354 | 123.0789 | 122.6944 | 54.9454 | -123.0927 | 122.9965 | 122.9645 | 80.1315 | -123.1522
3514.0156 | 123.0469 | -49.8688 | 73.0728 | -0.061188 | 0.019839 | 0.070173 | 0.073294 | 0.13057 | 0.0039819 | -0.0077183 | 0.030365 | -0.0099806 | 0.0664 | 0.056758 | 0.011258 | -0.012187 | 72.9218 | 73.027 | 5.2139 | -49.9237 | 73.2239 | -49.8962 | -50.0107 | -47.0352 | 30.3314 | -49.9466 | 73.1918 | 73.1323 | -50.0748 | -50.0931 | -0.027466 | -0.14191 | 0.15106 | 122.8958 | -0.054932 | 0.086975 | -0.15106 | -0.20599 | -0.22431 | 0.11902 | 2.8336 | -0.07782 | 0.14649 | 0.059509 | 123.0927 | 122.7905 | 55.0827 | -123.0835 | 123.0606 | 123.0011 | 80.2002 | -123.1659
3515.0156 | 123.0743 | -49.9603 | 72.9858 | 0.10666 | 0.015994 | 0.072736 | 0.071372 | 0.12864 | -0.0011451 | -0.0077183 | 0.19821 | -0.0089124 | 0.067468 | 0.057612 | 0.008908 | -0.011974 | 72.9263 | 73.027 | 5.1453 | -49.9008 | 73.2559 | -49.8459 | -49.9786 | -47.1588 | 30.2216 | -50.1709 | 73.0865 | 73.0225 | -50.1663 | -50.2029 | 0.11444 | -0.018311 | 0.27008 | 122.9874 | 0.059509 | 0.07782 | -0.059509 | -0.20599 | -0.24262 | 0.10071 | 2.8015 | -0.21057 | 0.032044 | 0.036621 | 123.2162 | 122.8867 | 55.1056 | -122.9645 | 123.0469 | 122.9828 | 80.1819 | -123.1888
3516.0156 | 123.056 | -49.9649 | 72.9858 | -0.03067 | 0.021762 | 0.070173 | 0.072653 | 0.12822 | 0.0022729 | -0.0064365 | 0.053253 | -0.0089124 | 0.068323 | 0.057185 | 0.011899 | -0.012614 | 73.0499 | 73.1506 | 5.0949 | -49.8001 | 73.3475 | -49.7955 | -49.9237 | -47.1954 | 30.1987 | -50.2625 | 73.0316 | 72.9721 | -50.2441 | -50.2716 | 0.16937 | 0.041199 | 0.36163 | 123.1155 | 0.1648 | 0.1236 | 0.064087 | -0.27924 | -0.3067 | 0.045776 | 2.7695 | -0.29755 | 0.009155 | -0.013733 | 123.3124 | 123.0148 | 55.0598 | -122.9095 | 122.9965 | 122.937 | 80.1636 | -123.2574
3517.0156 | 123.0148 | -50.0153 | 72.9401 | 0.13718 | 0.021976 | 0.068891 | 0.076712 | 0.13142 | 0.0033411 | -0.0051547 | 0.13718 | -0.009126 | 0.067041 | 0.057612 | 0.0093354 | -0.011119 | 72.6471 | 72.9263 | 4.9667 | -50.1251 | 73.0865 | -50.0885 | -50.1434 | -47.2183 | 30.1758 | -50.061 | 73.0316 | 72.9675 | -50.2396 | -50.2853 | -0.073242 | -0.12817 | 0.14648 | 122.9416 | -0.10986 | 0.018311 | -0.29297 | -0.2243 | -0.27008 | 0.091553 | 2.7969 | -0.045776 | 0.2243 | 0.027466 | 123.1018 | 122.6624 | 54.982 | -123.0835 | 123.0469 | 122.9828 | 80.191 | -123.2254
3518.0156 | 123.0286 | -50.2213 | 72.7478 | -0.061188 | 0.018985 | 0.070173 | 0.07543 | 0.12779 | 0.0027001 | -0.0057957 | -0.0077819 | -0.0069898 | 0.067682 | 0.057398 | 0.012326 | -0.012828 | 72.5281 | 72.6288 | 4.9667 | -50.3128 | 72.8073 | -50.2945 | -50.3952 | -47.3694 | 30.0797 | -50.3128 | 72.8073 | 72.7707 | -50.4135 | -50.4456 | -0.073243 | -0.17395 | 0.059509 | 122.85 | -0.091553 | 0.082398 | -0.21973 | -0.19226 | -0.22431 | 0.059509 | 2.8519 | -0.091553 | 0.13275 | 0.022888 | 123.0286 | 122.7493 | 55.188 | -123.143 | 123.0286 | 122.9919 | 80.3009 | -123.1934
3519.0156 | 123.056 | -50.2991 | 72.6334 | 0.083771 | 0.01813 | 0.069105 | 0.073294 | 0.12907 | 0.00056395 | -0.0081455 | 0.22873 | -0.0082716 | 0.066614 | 0.056544 | 0.008908 | -0.011546 | 72.3999 | 72.5098 | 4.9347 | -50.4089 | 72.7524 | -50.3998 | -50.4868 | -47.4426 | 30.0293 | -50.4272 | 72.7295 | 72.6517 | -50.5142 | -50.5646 | -0.10071 | -0.18768 | 0.11902 | 122.8088 | -0.10986 | 0.077819 | -0.23346 | -0.21515 | -0.2655 | 0.09613 | 2.8564 | -0.12817 | 0.13733 | 0.01831 | 123.0515 | 122.699 | 55.2338 | -123.1201 | 123.0286 | 122.9507 | 80.3284 | -123.1979
3520.0156 | 123.0515 | -49.5483 | 73.3704 | -0.46555 | 0.016849 | 0.071882 | 0.073935 | 0.13014 | 0.0027001 | -0.0070773 | -0.03067 | -0.0082716 | 0.067255 | 0.057185 | 0.010617 | -0.011546 | 73.2239 | 73.3337 | 5.0949 | -49.6307 | 73.5352 | -49.6033 | -49.7269 | -46.7148 | 30.7068 | -49.649 | 73.4848 | 73.4116 | -49.7726 | -49.8093 | -0.054931 | -0.17853 | 0.16479 | 122.8821 | -0.082397 | 0.096131 | -0.14648 | -0.2243 | -0.26093 | 0.11444 | 2.8336 | -0.10071 | 0.16022 | 0.041199 | 123.0835 | 122.7722 | 54.6433 | -123.0972 | 123.0331 | 122.9599 | 80.2551 | -123.1796
3521.0156 | 123.0469 | -49.4431 | 73.5077 | 0.27451 | 0.012362 | 0.072309 | 0.069449 | 0.12736 | -0.00029045 | -0.0079319 | 0.24399 | -0.0084852 | 0.066828 | 0.060389 | 0.011472 | -0.011974 | 73.4024 | 73.4116 | 5.0949 | -49.411 | 73.7503 | -49.4064 | -49.5209 | -46.5729 | 30.8945 | -49.5621 | 73.6267 | 73.5489 | -49.6216 | -49.6582 | 0.036621 | -0.07782 | 0.24262 | 122.8546 | 0.032043 | 0.10986 | -0.10528 | -0.17853 | -0.21515 | 0.11902 | 2.8702 | -0.11902 | 0.09613 | 0.041199 | 123.1934 | 122.8455 | 54.538 | -123.0286 | 123.0698 | 122.9919 | 80.3375 | -123.1659
3522.0156 | 123.0698 | -49.1547 | 73.7961 | -0.03067 | 0.020053 | 0.068678 | 0.076498 | 0.1295 | 0.0012047 | -0.0064365 | 0.053253 | -0.0095532 | 0.066187 | 0.058467 | 0.011899 | -0.013469 | 73.6221 | 73.7274 | 5.0949 | -49.2004 | 73.9426 | -49.205 | -49.292 | -46.312 | 31.2332 | -49.3378 | 73.8876 | 73.8464 | -49.3835 | -49.4202 | -0.050354 | -0.13733 | 0.14648 | 122.8821 | -0.045776 | 0.091553 | -0.17395 | -0.22888 | -0.2655 | 0.091552 | 2.8427 | -0.18311 | 0.082397 | 0.050354 | 123.0972 | 122.7768 | 54.2496 | -123.0881 | 123.0423 | 123.0011 | 80.3879 | -123.2162
3523.0156 | 123.0148 | -48.8068 | 74.176 | 0.10666 | 0.016849 | 0.069319 | 0.071158 | 0.13057 | 0.0016321 | -0.0055821 | 0.44235 | -0.009126 | 0.062342 | 0.057398 | 0.011044 | -0.013042 | 73.8373 | 73.9563 | 4.9713 | -48.9349 | 74.2584 | -48.8892 | -49.0128 | -45.9869 | 31.5857 | -48.9532 | 74.2218 | 74.1898 | -49.0128 | -49.0585 | -0.082397 | -0.20599 | 0.082398 | 122.7631 | -0.12817 | 0.077819 | -0.33874 | -0.20599 | -0.25177 | 0.045777 | 2.8198 | -0.14648 | 0.10529 | 0.013733 | 123.0652 | 122.644 | 53.7781 | -123.1888 | 123.0286 | 122.9965 | 80.3925 | -123.2346
3524.0156 | 123.0469 | -50.2625 | 72.6974 | -0.076447 | 0.01813 | 0.071241 | 0.072653 | 0.12886 | 0.0018457 | -0.0055821 | -0.03067 | -0.007417 | 0.067041 | 0.05633 | 0.011899 | -0.012614 | 72.4594 | 72.5601 | 4.7745 | -50.3906 | 72.7341 | -50.3815 | -50.5005 | -47.4518 | 30.3406 | -50.4181 | 72.7066 | 72.6929 | -50.5005 | -50.5005 | -0.11902 | -0.23804 | 0.036621 | 122.8226 | -0.12817 | 0.10986 | -0.23804 | -0.23804 | -0.23804 | 0.009155 | 2.8107 | -0.15564 | 0.082397 | -0.004578 | 122.9965 | 122.7219 | 55.0369 | -123.1979 | 122.9691 | 122.9553 | 80.603 | -123.1979
3525.0156 | 123.0148 | -49.5575 | 73.3795 | 0.10666 | 0.021335 | 0.070173 | 0.072226 | 0.128 | 0.0014185 | -0.0077183 | 0.14481 | -0.0076306 | 0.067682 | 0.058467 | 0.0074126 | -0.011974 | 73.1277 | 73.2422 | 4.7653 | -49.6765 | 73.4894 | -49.6628 | -49.7864 | -46.756 | 30.9082 | -49.6948 | 73.4802 | 73.4344 | -49.7726 | -49.8001 | -0.10529 | -0.22888 | 0.10986 | 122.7997 | -0.11902 | 0.10986 | -0.25177 | -0.21515 | -0.24261 | 0.10071 | 2.8015 | -0.13733 | 0.10529 | 0.054931 | 123.0469 | 122.6852 | 54.3228 | -123.1659 | 123.0377 | 122.9919 | 80.4657 | -123.1796
3526.0156 | 123.0194 | -49.6582 | 73.2971 | -0.0383 | 0.020267 | 0.069746 | 0.076285 | 0.12864 | 0.00077755 | -0.0064365 | 0.10666 | -0.0097668 | 0.066187 | 0.058894 | 0.0091216 | -0.01176 | 73.1461 | 73.2468 | 5.0674 | -49.6811 | 73.4756 | -49.6811 | -49.791 | -46.8155 | 30.8075 | -49.8596 | 73.3795 | 73.3383 | -49.8734 | -49.8871 | -0.022888 | -0.13275 | 0.17853 | 122.905 | -0.022888 | 0.10986 | -0.15106 | -0.21515 | -0.22888 | 0.082398 | 2.8427 | -0.20142 | 0.027466 | 0.041199 | 123.1338 | 122.8043 | 54.7256 | -123.0881 | 123.0377 | 122.9965 | 80.4657 | -123.1842
3527.0156 | 123.0103 | -49.2371 | 73.732 | 0.10666 | 0.017703 | 0.070387 | 0.072653 | 0.13014 | 0.0031273 | -0.0085727 | 0.09903 | -0.0099806 | 0.069391 | 0.05868 | 0.011685 | -0.011333 | 73.4619 | 73.5992 | 5.0125 | -49.3652 | 73.8327 | -49.3103 | -49.4156 | -46.3989 | 31.1371 | -49.3698 | 73.8052 | 73.7595 | -49.4522 | -49.4614 | -0.073242 | -0.17853 | 0.10071 | 122.8363 | -0.12817 | 0.050354 | -0.27008 | -0.21515 | -0.2243 | 0.073242 | 2.8381 | -0.13275 | 0.091553 | 0.027465 | 123.0698 | 122.699 | 54.2496 | -123.1476 | 123.0423 | 122.9965 | 80.3741 | -123.1934
3528.0156 | 123.056 | -48.6557 | 74.2996 | -0.29007 | 0.021976 | 0.070173 | 0.07009 | 0.12822 | 0.0016321 | -0.0062229 | -0.053558 | -0.011262 | 0.067255 | 0.056971 | 0.01019 | -0.011546 | 74.0295 | 74.1898 | 5.4199 | -48.761 | 74.3729 | -48.7656 | -48.8754 | -45.8038 | 31.691 | -48.6786 | 74.35 | 74.3088 | -48.8846 | -48.9212 | -0.10986 | -0.21973 | 0.073242 | 122.8455 | -0.10529 | 0.11444 | -0.27008 | -0.22888 | -0.2655 | 0.050354 | 2.8519 | -0.022888 | 0.24262 | 0.009155 | 123.0286 | 122.6852 | 54.0756 | -123.175 | 123.0057 | 122.9645 | 80.3467 | -123.2208
3529.0156 | 123.0377 | -50.5508 | 72.3724 | 0.28976 | 0.019626 | 0.068037 | 0.07543 | 0.12822 | 0.0022729 | -0.0075047 | 0.20584 | -0.010194 | 0.0664 | 0.057612 | 0.0099762 | -0.013469 | 72.0978 | 72.1985 | 4.9484 | -50.679 | 72.4869 | -50.6516 | -50.7614 | -47.7036 | 30.1529 | -50.6882 | 72.4731 | 72.4136 | -50.7935 | -50.853 | -0.10071 | -0.21057 | 0.11444 | 122.7493 | -0.12817 | 0.082398 | -0.27466 | -0.24261 | -0.30212 | 0.10071 | 2.8473 | -0.13733 | 0.1648 | 0.041198 | 123.0377 | 122.6486 | 55.4993 | -123.1339 | 123.024 | 122.9645 | 80.7037 | -123.2254
3530.0156 | 123.0331 | -49.1959 | 73.7366 | -0.10696 | 0.018985 | 0.070173 | 0.069235 | 0.13014 | -0.0015723 | -0.0079319 | -0.045929 | -0.0050672 | 0.067041 | 0.057398 | 0.0097626 | -0.013255 | 73.613 | 73.7 | 5.2094 | -49.2783 | 73.8922 | -49.2416 | -49.3423 | -46.2891 | 31.4484 | -49.2691 | 73.851 | 73.7915 | -49.3881 | -49.4476 | -0.045776 | -0.14648 | 0.15564 | 122.8958 | -0.082397 | 0.064087 | -0.1236 | -0.19226 | -0.25177 | 0.11444 | 2.9068 | -0.073242 | 0.17853 | 0.054932 | 123.0881 | 122.8088 | 54.4052 | -123.0789 | 123.0469 | 122.9874 | 80.6442 | -123.1842
3531.0156 | 123.0057 | -48.9624 | 74.025 | 0.060882 | 0.023471 | 0.070173 | 0.072226 | 0.13014 | 0.0027001 | -0.0060093 | 0.25925 | -0.008058 | 0.066187 | 0.056971 | 0.012326 | -0.012614 | 73.5443 | 73.6862 | 5.1407 | -49.2416 | 73.9334 | -49.1913 | -49.3103 | -46.1151 | 31.485 | -49.054 | 74.0753 | 74.0479 | -49.1867 | -49.1913 | -0.22888 | -0.3479 | -0.091552 | 122.6486 | -0.27924 | 0.068665 | -0.48065 | -0.22431 | -0.22888 | 0.050354 | 2.8473 | -0.091553 | 0.13733 | 0.022889 | 122.8958 | 122.5067 | 54.1031 | -123.3353 | 123.0377 | 123.0103 | 80.4474 | -123.2162
3532.0156 | 123.1018 | -48.3261 | 74.6017 | -0.10696 | 0.019839 | 0.068678 | 0.074576 | 0.13078 | 0.00013675 | -0.0053683 | -0.045929 | -0.0082716 | 0.067896 | 0.060176 | 0.012112 | -0.013896 | 74.3683 | 74.5148 | 5.2368 | -48.4726 | 74.6887 | -48.4497 | -48.5733 | -45.4193 | 32.1304 | -48.3994 | 74.6841 | 74.6613 | -48.5413 | -48.5916 | -0.1236 | -0.24719 | 0.086975 | 122.8409 | -0.14648 | 0.10071 | -0.23346 | -0.21515 | -0.2655 | 0.082397 | 2.9068 | -0.073242 | 0.19226 | 0.059509 | 123.0148 | 122.6944 | 53.5629 | -123.175 | 123.0103 | 122.9874 | 80.4565 | -123.1934
3533.0156 | 123.0148 | -49.9283 | 73.0499 | 0.053253 | 0.021121 | 0.071027 | 0.07479 | 0.13014 | 0.0022729 | -0.0077183 | 0.20584 | -0.0095532 | 0.06875 | 0.059107 | 0.015317 | -0.0077012 | 72.6929 | 72.8073 | 4.9988 | -50.0839 | 73.1003 | -50.0381 | -50.1526 | -47.2229 | 31.073 | -50.0473 | 73.0545 | 73.027 | -50.1938 | -50.1801 | -0.10986 | -0.2243 | 0.050354 | 122.7356 | -0.15564 | 0.068665 | -0.35706 | -0.2655 | -0.25177 | 0.004577 | 2.7054 | -0.11902 | 0.13275 | -0.022888 | 123.0286 | 122.6212 | 54.9271 | -123.2025 | 122.9828 | 122.9553 | 81.0013 | -123.23
3534.0156 | 123.0789 | -49.5712 | 73.3154 | -0.24429 | 0.019412 | 0.070387 | 0.073721 | 0.12971 | 0.0014185 | -0.0075047 | -0.084076 | -0.0093396 | 0.069177 | 0.05868 | 0.0091216 | -0.01176 | 73.3383 | 73.4573 | 5.3055 | -49.4934 | 73.6588 | -49.5026 | -49.585 | -46.5454 | 31.1554 | -49.6948 | 73.558 | 73.4756 | -49.7452 | -49.791 | 0.068665 | -0.013733 | 0.34332 | 123.0286 | 0.07782 | 0.091553 | 0.022888 | -0.17395 | -0.21973 | 0.24261 | 3.0258 | -0.1236 | 0.096131 | 0.16022 | 123.23 | 122.9095 | 54.8767 | -122.9004 | 123.1293 | 123.0469 | 80.7266 | -123.1064
3535.0156 | 123.0515 | -49.3332 | 73.6496 | -0.053558 | 0.021762 | 0.0706 | 0.073508 | 0.12843 | 0.0018457 | -0.0066501 | 0.053253 | -0.0067762 | 0.067682 | 0.057185 | 0.01254 | -0.013255 | 73.4253 | 73.5901 | 5.4062 | -49.3744 | 73.764 | -49.3652 | -49.4751 | -46.3852 | 31.2607 | -49.4064 | 73.732 | 73.6679 | -49.5117 | -49.5438 | -0.032043 | -0.14191 | 0.11444 | 122.9233 | -0.041199 | 0.10071 | -0.2243 | -0.17853 | -0.21057 | 0.082398 | 2.948 | -0.073242 | 0.13733 | 0.018311 | 123.0972 | 122.7585 | 54.7394 | -123.1247 | 123.0652 | 123.0011 | 80.5939 | -123.1934
3536.0156 | 123.0652 | -48.4314 | 74.5422 | -0.12985 | 0.018344 | 0.068678 | 0.071799 | 0.13035 | 0.0024865 | -0.0098545 | -0.061188 | -0.0097668 | 0.0664 | 0.057612 | 0.0099762 | -0.012401 | 74.3134 | 74.4965 | 5.5389 | -48.4589 | 74.675 | -48.4726 | -48.5779 | -45.52 | 31.8008 | -48.5001 | 74.6017 | 74.5651 | -48.6282 | -48.6832 | -0.041199 | -0.14648 | 0.13275 | 122.9279 | -0.027466 | 0.11902 | -0.22888 | -0.19684 | -0.25177 | 0.05951 | 2.9114 | -0.068665 | 0.18311 | 0.022889 | 123.1064 | 122.7448 | 53.9703 | -123.1201 | 123.0331 | 122.9965 | 80.2322 | -123.2254
3537.0156 | 123.0423 | -48.9029 | 74.0936 | 0.0074768 | 0.01813 | 0.070814 | 0.072012 | 0.12886 | 0.0016321 | -0.0062229 | -0.015411 | -0.0072034 | 0.066828 | 0.057398 | 0.0099762 | -0.010692 | 73.8281 | 73.9471 | 5.2048 | -49.0082 | 74.1852 | -48.967 | -49.1043 | -46.0327 | 31.5491 | -49.0677 | 74.1119 | 74.057 | -49.1272 | -49.1547 | -0.064087 | -0.20142 | 0.091553 | 122.85 | -0.10529 | 0.09613 | -0.2655 | -0.2243 | -0.25177 | 0.01831 | 2.8702 | -0.16479 | 0.086975 | -0.036621 | 123.0881 | 122.731 | 54.1077 | -123.1979 | 123.0148 | 122.9599 | 80.452 | -123.2483
3538.0156 | 123.056 | -49.2599 | 73.6725 | -0.19089 | 0.017276 | 0.069746 | 0.072653 | 0.12993 | 0.0022729 | -0.0068637 | -0.10696 | -0.0099806 | 0.065546 | 0.058253 | 0.00784 | -0.013042 | 73.4619 | 73.6267 | 5.1178 | -49.3286 | 73.8098 | -49.3607 | -49.4385 | -46.3669 | 31.3019 | -49.3561 | 73.764 | 73.7 | -49.4934 | -49.498 | -0.10071 | -0.17853 | 0.13733 | 122.8867 | -0.068664 | 0.10986 | -0.21057 | -0.23346 | -0.23804 | 0.091553 | 2.8931 | -0.09613 | 0.14191 | 0.027466 | 123.0698 | 122.7219 | 54.3777 | -123.111 | 123.024 | 122.9599 | 80.5618 | -123.1705
3539.0156 | 123.0698 | -49.1043 | 73.8281 | -0.045929 | 0.020907 | 0.071027 | 0.074576 | 0.12843 | 0.0046227 | -0.0072911 | 0.030365 | -0.009126 | 0.067682 | 0.056544 | 0.011685 | -0.015178 | 73.6404 | 73.7778 | 5.2139 | -49.1638 | 73.9563 | -49.1638 | -49.2462 | -46.1929 | 31.4758 | -49.1821 | 73.9334 | 73.8739 | -49.3195 | -49.3744 | -0.059509 | -0.14191 | 0.12817 | 122.8821 | -0.059509 | 0.082398 | -0.18768 | -0.21515 | -0.27008 | 0.10529 | 2.9114 | -0.07782 | 0.19226 | 0.045776 | 123.0606 | 122.7448 | 54.3182 | -123.0743 | 123.0377 | 122.9782 | 80.5801 | -123.2025
3540.0156 | 123.0835 | -48.8708 | 74.0936 | -0.15274 | 0.016208 | 0.071668 | 0.073935 | 0.12928 | 0.0014185 | -0.0064365 | -0.084076 | -0.0093396 | 0.067468 | 0.055903 | 0.009549 | -0.01176 | 73.9105 | 74.0524 | 5.2505 | -48.9029 | 74.2218 | -48.8983 | -49.0448 | -45.9137 | 31.4941 | -48.9304 | 74.1989 | 74.1302 | -49.0585 | -49.0631 | -0.027465 | -0.17395 | 0.12817 | 122.9233 | -0.032043 | 0.14191 | -0.18311 | -0.18768 | -0.19226 | 0.10529 | 2.9572 | -0.059509 | 0.13275 | 0.036621 | 123.0927 | 122.7814 | 54.1214 | -123.1384 | 123.0698 | 123.0011 | 80.365 | -123.1567
3541.0156 | 123.0606 | -48.5641 | 74.3774 | -0.099335 | 0.019198 | 0.069319 | 0.075217 | 0.13163 | 0.0020593 | -0.0060093 | 0.59494 | -0.0084852 | 0.066828 | 0.057612 | 0.010831 | -0.012828 | 74.2035 | 74.382 | 5.3741 | -48.6099 | 74.5239 | -48.6053 | -48.6877 | -45.6528 | 31.9061 | -48.642 | 74.4644 | 74.3912 | -48.7747 | -48.8022 | -0.041199 | -0.1236 | 0.14648 | 122.9462 | -0.045776 | 0.07782 | -0.17395 | -0.21057 | -0.23804 | 0.086976 | 2.9114 | -0.07782 | 0.16022 | 0.013733 | 123.0881 | 122.7676 | 53.9383 | -123.0652 | 123.0286 | 122.9553 | 80.4703 | -123.1796
3542.0156 | 123.0377 | -48.6511 | 74.3454 | 0.88486 | 0.015567 | 0.070387 | 0.074362 | 0.13078 | -0.0024269 | -0.0077183 | -0.12222 | -0.010621 | 0.066828 | 0.058467 | 0.0086944 | -0.010692 | 74.0662 | 74.2401 | 5.1682 | -48.7106 | 74.4461 | -48.7015 | -48.8342 | -45.7809 | 31.8649 | -48.7564 | 74.4049 | 74.3546 | -48.848 | -48.8663 | -0.050354 | -0.18311 | 0.10071 | 122.8912 | -0.059509 | 0.1236 | -0.27924 | -0.19684 | -0.21515 | 0.059509 | 2.8702 | -0.10529 | 0.10986 | 0.009155 | 123.0972 | 122.7173 | 53.8193 | -123.1796 | 123.056 | 123.0057 | 80.5161 | -123.2117
3543.0156 | 123.0789 | -49.0036 | 73.9517 | -0.11459 | 0.018771 | 0.068037 | 0.071585 | 0.13121 | -0.00050425 | -0.0060093 | -0.061188 | -0.0097668 | 0.06875 | 0.056758 | 0.008908 | -0.013683 | 73.7503 | 73.9655 | 5.2139 | -49.054 | 74.1028 | -49.0356 | -49.1089 | -46.0007 | 31.5628 | -49.0906 | 74.0662 | 73.9746 | -49.2004 | -49.2325 | -0.032044 | -0.10529 | 0.15106 | 122.9691 | -0.050354 | 0.054932 | -0.20142 | -0.19684 | -0.22888 | 0.11444 | 3.0029 | -0.086975 | 0.14191 | 0.022888 | 123.1064 | 122.7539 | 54.2175 | -123.0606 | 123.0698 | 122.9782 | 80.5664 | -123.1842
3544.0156 | 123.0515 | -48.674 | 74.2905 | -0.27481 | 0.014499 | 0.071241 | 0.072653 | 0.12971 | -0.0011451 | -0.0070773 | -0.10696 | -0.0095532 | 0.065759 | 0.058467 | 0.0080536 | -0.012614 | 73.7961 | 73.97 | 5.0674 | -48.9624 | 74.1898 | -48.9441 | -49.0219 | -45.813 | 31.7642 | -48.7473 | 74.35 | 74.2813 | -48.9212 | -48.9395 | -0.27008 | -0.3479 | -0.10071 | 122.644 | -0.28839 | 0.05951 | -0.49438 | -0.24719 | -0.2655 | 0.05951 | 2.861 | -0.073242 | 0.19226 | -0.009155 | 122.8638 | 122.4701 | 53.7415 | -123.3124 | 123.024 | 122.9553 | 80.4382 | -123.23
3545.0156 | 123.1567 | -48.848 | 74.1165 | -0.168 | 0.018985 | 0.069746 | 0.073935 | 0.12928 | 0.0027001 | -0.0070773 | -0.068817 | -0.0097668 | 0.067468 | 0.056544 | 0.010403 | -0.012828 | 73.9059 | 74.0524 | 5.5115 | -48.9212 | 74.2447 | -48.912 | -49.0173 | -45.8908 | 31.6223 | -48.8983 | 74.1898 | 74.1211 | -49.0768 | -49.086 | -0.064087 | -0.16937 | 0.12817 | 122.9004 | -0.073243 | 0.09613 | -0.21057 | -0.22888 | -0.23804 | 0.073242 | 2.9572 | -0.050354 | 0.18768 | 0.004578 | 123.0927 | 122.7539 | 54.3594 | -123.1338 | 123.0377 | 122.9691 | 80.4703 | -123.2025
3546.0156 | 123.1201 | -50.1892 | 72.7112 | 0.16006 | 0.019198 | 0.069105 | 0.073721 | 0.12864 | -0.00093145 | -0.0081455 | 0.24399 | -0.011262 | 0.0664 | 0.058039 | 0.0086944 | -0.01176 | 72.4319 | 72.5967 | 5.1407 | -50.3494 | 72.7798 | -50.3403 | -50.4456 | -47.2641 | 30.5557 | -50.2716 | 72.789 | 72.7203 | -50.4456 | -50.4227 | -0.15106 | -0.25635 | 0.068664 | 122.7859 | -0.16022 | 0.096131 | -0.27924 | -0.25635 | -0.23346 | 0.077819 | 2.9251 | -0.082397 | 0.15106 | 0.009155 | 122.9691 | 122.6212 | 55.3299 | -123.1567 | 122.9782 | 122.9095 | 80.7449 | -123.1338
3547.0156 | 123.0652 | -48.9716 | 73.9563 | -0.10696 | 0.019839 | 0.068678 | 0.073721 | 0.12843 | 0.00099115 | -0.0057957 | -0.03067 | -0.007417 | 0.069177 | 0.05868 | 0.01019 | -0.01411 | 73.8602 | 74.0158 | 5.3696 | -48.9624 | 74.1989 | -48.9716 | -49.0356 | -45.9045 | 31.7093 | -49.0906 | 74.0799 | 74.0341 | -49.1638 | -49.2142 | 0 | -0.064087 | 0.24262 | 122.9874 | 0.009156 | 0.073243 | -0.096131 | -0.19226 | -0.24261 | 0.1236 | 3.067 | -0.11902 | 0.1236 | 0.07782 | 123.1705 | 122.8317 | 54.3411 | -122.9919 | 123.0515 | 123.0057 | 80.6808 | -123.1705
3548.0156 | 123.0377 | -49.9603 | 72.9996 | -0.24429 | 0.013858 | 0.072309 | 0.071585 | 0.12843 | -0.0045631 | -0.0089999 | -0.14511 | -0.011049 | 0.064051 | 0.057398 | 0.0069854 | -0.010905 | 72.8348 | 73.0133 | 5.1544 | -49.9649 | 73.1873 | -49.9512 | -50.0748 | -46.9391 | 31.0272 | -50.0381 | 73.1323 | 73.0774 | -50.1663 | -50.2258 | 0.009155 | -0.11444 | 0.18768 | 122.9736 | -0.004578 | 0.10986 | -0.16479 | -0.20599 | -0.2655 | 0.13275 | 3.0212 | -0.07782 | 0.18768 | 0.07782 | 123.1476 | 122.7951 | 55.1147 | -123.0743 | 123.0927 | 123.0377 | 80.9875 | -123.2254
3549.0156 | 123.0835 | -49.8001 | 73.1781 | -0.23666 | 0.017917 | 0.071882 | 0.073935 | 0.12779 | -0.0011451 | -0.0083591 | -0.168 | -0.010621 | 0.067041 | 0.057612 | 0.0091216 | -0.010905 | 72.8714 | 73.0591 | 5.1086 | -49.8917 | 73.288 | -49.8917 | -50.0153 | -46.8567 | 31.1325 | -49.8779 | 73.2422 | 73.1598 | -50.0244 | -50.0427 | -0.091553 | -0.21515 | 0.10986 | 122.8592 | -0.091553 | 0.1236 | -0.3067 | -0.2243 | -0.24262 | 0.064086 | 2.9434 | -0.07782 | 0.16479 | -0.018311 | 123.0881 | 122.6715 | 54.9088 | -123.1934 | 123.0423 | 122.9599 | 80.9326 | -123.2208
3550.0156 | 122.9782 | -49.2325 | 73.7183 | -0.12222 | 0.013431 | 0.069959 | 0.071799 | 0.13057 | -0.0028541 | -0.0092137 | -0.10696 | -0.010621 | 0.065973 | 0.058467 | 0.0082672 | -0.012828 | 73.4116 | 73.6313 | 5.3329 | -49.3469 | 73.8235 | -49.3286 | -49.4431 | -46.3028 | 31.5628 | -49.3423 | 73.8007 | 73.7137 | -49.4385 | -49.4385 | -0.09613 | -0.21057 | 0.10529 | 122.8638 | -0.11444 | 0.09613 | -0.3067 | -0.20599 | -0.20599 | 0.082397 | 2.9297 | -0.10986 | 0.096131 | -0.004578 | 123.056 | 122.644 | 54.5654 | -123.1613 | 123.0331 | 122.9462 | 80.7953 | -123.1567
3551.0312 | 123.1567 | -48.7198 | 74.1531 | 0.20584 | 0.014499 | 0.069105 | 0.072226 | 0.12907 | 0.00077755 | -0.0077183 | -1.2514 | -0.010835 | 0.067896 | 0.055689 | 0.0097626 | -0.012401 | 74.0021 | 74.1989 | 5.6305 | -48.793 | 74.2813 | -48.793 | -48.8983 | -45.726 | 32.1442 | -48.7656 | 74.1943 | 74.1302 | -48.967 | -48.9716 | -0.073242 | -0.17853 | 0.12817 | 122.9187 | -0.073242 | 0.10528 | -0.15106 | -0.24719 | -0.25177 | 0.041199 | 2.9938 | -0.045776 | 0.20599 | -0.022888 | 123.0011 | 122.7219 | 54.3503 | -123.0515 | 122.9141 | 122.85 | 80.864 | -123.1247
3552.0156 | 123.0469 | -48.4589 | 74.4827 | -0.24429 | 0.010013 | 0.070814 | 0.072012 | 0.12715 | -0.0026405 | -0.0079319 | -0.12985 | -0.0093396 | 0.063623 | 0.05868 | 0.0099762 | -0.012828 | 74.3912 | 74.588 | 5.6534 | -48.3948 | 74.7253 | -48.4039 | -48.4955 | -45.4605 | 32.5287 | -48.5275 | 74.6429 | 74.556 | -48.6328 | -48.6649 | 0.054931 | -0.036621 | 0.24262 | 123.0469 | 0.064087 | 0.10071 | -0.091553 | -0.17395 | -0.20599 | 0.16022 | 2.9984 | -0.068665 | 0.13733 | 0.073242 | 123.1842 | 122.85 | 54.1122 | -122.9782 | 123.1018 | 123.0148 | 80.9875 | -123.1476
3553.0156 | 123.0835 | -48.4039 | 74.5148 | -0.21378 | 0.015994 | 0.071455 | 0.073294 | 0.12587 | 0.0020593 | -0.0068637 | -0.17563 | -0.011476 | 0.065759 | 0.056971 | 0.011472 | -0.012401 | 74.1623 | 74.3088 | 5.5984 | -48.5001 | 74.6017 | -48.5413 | -48.6191 | -45.3781 | 32.4829 | -48.5275 | 74.6475 | 74.5789 | -48.6008 | -48.6465 | -0.13733 | -0.21515 | 0.086975 | 122.7127 | -0.09613 | 0.11902 | -0.35248 | -0.19684 | -0.24261 | 0.13275 | 3.0258 | -0.1236 | 0.11902 | 0.064086 | 123.0057 | 122.5662 | 54.0024 | -123.1339 | 123.0515 | 122.9828 | 80.8868 | -123.1613
3554.0156 | 123.0377 | -48.88 | 74.0799 | -0.24429 | 0.010226 | 0.072309 | 0.073081 | 0.1295 | -0.00071785 | -0.0079319 | -0.061188 | -0.01233 | 0.063196 | 0.057826 | 0.0084808 | -0.012614 | 73.8739 | 74.1348 | 5.4291 | -48.8892 | 74.2813 | -48.8663 | -48.9578 | -45.8588 | 32.1396 | -48.9487 | 74.2081 | 74.1257 | -49.1043 | -49.0952 | 0.013733 | -0.07782 | 0.20142 | 123.0148 | -0.009155 | 0.068665 | -0.20599 | -0.2243 | -0.21515 | 0.12817 | 3.0212 | -0.068664 | 0.14648 | 0.045776 | 123.1613 | 122.7539 | 54.3091 | -123.0377 | 123.0881 | 123.0057 | 81.0196 | -123.175
3555.0156 | 123.056 | -49.0906 | 73.8739 | -0.22903 | 0.014499 | 0.07295 | 0.075217 | 0.12993 | -0.00071785 | -0.0070773 | 0.16769 | -0.0082716 | 0.067041 | 0.055262 | 0.0082672 | -0.011974 | 73.6313 | 73.7778 | 5.6122 | -48.9807 | 74.0982 | -49.0997 | -49.205 | -46.0602 | 32.048 | -49.2233 | 74.0158 | 73.9059 | -49.2874 | -49.3332 | -0.009155 | -0.11444 | 0.22431 | 122.8683 | 0.10986 | 0.2243 | -0.24261 | -0.19684 | -0.24262 | 0.14191 | 3.0304 | -0.13275 | 0.10986 | 0.032044 | 123.1888 | 122.7219 | 54.7028 | -123.0789 | 123.1064 | 122.9965 | 81.1386 | -123.2071
3556.0312 | 123.0698 | -49.9191 | 72.9996 | 0.14481 | 0.017489 | 0.071455 | 0.075217 | 0.12779 | 0.0018457 | -0.0045139 | 0.19058 | -0.0095532 | 0.066828 | 0.057612 | 0.010617 | -0.01176 | 72.7753 | 72.9446 | 5.5344 | -50.0107 | 73.1598 | -49.9832 | -50.0748 | -46.8796 | 31.2241 | -50.1068 | 73.0453 | 72.9721 | -50.1846 | -50.1709 | -0.064087 | -0.15564 | 0.16022 | 122.8638 | -0.091553 | 0.064087 | -0.2243 | -0.2655 | -0.25177 | 0.045776 | 3.0395 | -0.18768 | 0.064086 | -0.027466 | 123.0789 | 122.6944 | 55.4535 | -123.0743 | 122.9645 | 122.8912 | 81.1432 | -123.1705
3557.0156 | 123.0652 | -49.704 | 73.2468 | 0.78567 | 0.013858 | 0.072096 | 0.072867 | 0.12715 | 0.00056395 | -0.0060093 | -0.12985 | -0.010408 | 0.067255 | 0.058894 | 0.0099762 | -0.012614 | 73.027 | 73.1552 | 5.4474 | -49.736 | 73.407 | -49.7726 | -49.8413 | -46.6965 | 31.2653 | -49.7772 | 73.3658 | 73.2742 | -49.9054 | -49.9466 | -0.068665 | -0.13733 | 0.16022 | 122.8592 | -0.032044 | 0.10529 | -0.21973 | -0.20142 | -0.24262 | 0.11902 | 3.0075 | -0.073243 | 0.16937 | 0.027466 | 123.111 | 122.731 | 55.1514 | -123.0881 | 123.0698 | 122.9782 | 80.9692 | -123.1934
3558.0156 | 123.143 | -49.4339 | 73.4619 | -0.12985 | 0.011935 | 0.070387 | 0.071799 | 0.12864 | -0.0039221 | -0.0077183 | -0.13748 | -0.010408 | 0.065546 | 0.055903 | 0.0067718 | -0.011974 | 73.3154 | 73.5443 | 5.7861 | -49.498 | 73.6084 | -49.5026 | -49.6033 | -46.4035 | 31.6544 | -49.4888 | 73.526 | 73.4528 | -49.649 | -49.6857 | -0.068664 | -0.16937 | 0.14648 | 122.9782 | -0.064087 | 0.10529 | -0.14648 | -0.21515 | -0.25177 | 0.064087 | 3.0304 | -0.054932 | 0.19684 | -0.009155 | 123.0423 | 122.7493 | 55.22 | -123.0652 | 122.9599 | 122.8867 | 81.0883 | -123.1476
3559.0156 | 123.0011 | -47.9233 | 75.0732 | -0.15274 | 0.013431 | 0.071882 | 0.072653 | 0.13035 | 0.0012047 | -0.0070773 | -0.168 | -0.0099806 | 0.067468 | 0.056758 | 0.009549 | -0.013042 | 74.7116 | 74.8947 | 5.896 | -48.0789 | 75.1328 | -48.0194 | -48.1247 | -44.9524 | 33.284 | -47.8638 | 75.2106 | 75.1007 | -48.1064 | -48.1476 | -0.09613 | -0.20142 | 0.059509 | 122.818 | -0.15564 | 0.045777 | -0.36163 | -0.1831 | -0.2243 | 0.13733 | 2.9709 | 0.059509 | 0.28381 | 0.027466 | 123.056 | 122.6349 | 53.8193 | -123.1979 | 123.1338 | 123.024 | 81.2073 | -123.2208
3560.0156 | 123.1064 | -48.5413 | 74.3683 | -0.20615 | 0.013431 | 0.071668 | 0.072012 | 0.12672 | -0.0032813 | -0.0072911 | -0.068817 | -0.010194 | 0.061914 | 0.054621 | 0.0099762 | -0.012187 | 74.2172 | 74.4781 | 5.896 | -48.5641 | 74.5468 | -48.555 | -48.6603 | -45.4514 | 32.3364 | -48.5962 | 74.4736 | 74.3866 | -48.7335 | -48.7885 | -0.013733 | -0.11902 | 0.17853 | 123.0194 | -0.022888 | 0.09613 | -0.15106 | -0.19226 | -0.24719 | 0.10529 | 3.0899 | -0.054931 | 0.19226 | 0.018311 | 123.0881 | 122.7585 | 54.4373 | -123.0286 | 123.0148 | 122.9279 | 80.8777 | -123.1567
3561.0156 | 123.0148 | -48.9395 | 74.0021 | 0.037994 | 0.017917 | 0.069959 | 0.07543 | 0.13057 | 0.0050499 | -0.0060093 | 0.076141 | -0.0076306 | 0.070886 | 0.057826 | 0.0093354 | -0.014537 | 73.7183 | 73.7869 | 5.9692 | -49.0906 | 74.1028 | -49.1043 | -49.205 | -45.9641 | 32.048 | -49.0311 | 74.0753 | 73.9929 | -49.173 | -49.1913 | -0.16479 | -0.2655 | 0.10071 | 122.7264 | -0.15106 | 0.11444 | -0.28381 | -0.23346 | -0.25177 | 0.073242 | 2.9755 | -0.091553 | 0.16022 | -0.009155 | 123.0423 | 122.6578 | 54.9088 | -123.2071 | 123.0148 | 122.9324 | 80.9875 | -123.1934
3562.0156 | 123.2025 | -50.7889 | 72.084 | -0.076447 | 0.0080899 | 0.071455 | 0.070517 | 0.12843 | -0.0045631 | -0.0098545 | -0.061188 | -0.011903 | 0.063837 | 0.058253 | 0.0052764 | -0.012401 | 71.8781 | 72.139 | 5.9463 | -50.9079 | 72.1481 | -50.9125 | -51.0132 | -47.6486 | 30.8212 | -50.7431 | 72.1527 | 72.1069 | -50.972 | -51.0315 | -0.1236 | -0.22431 | 0.064087 | 122.9279 | -0.11902 | 0.10529 | -0.20599 | -0.18311 | -0.24262 | 0.068665 | 3.1403 | 0.045776 | 0.28839 | 0.022889 | 122.937 | 122.6669 | 56.7352 | -123.0972 | 122.9416 | 122.8958 | 81.6101 | -123.1155
3563.0156 | 123.0927 | -50.5829 | 72.3312 | -0.19089 | 0.010653 | 0.071455 | 0.07479 | 0.12715 | -0.0034949 | -0.0081455 | -0.15274 | -0.010408 | 0.065119 | 0.055903 | 0.0084808 | -0.013896 | 72.139 | 72.3633 | 5.9647 | -50.6287 | 72.4045 | -50.7019 | -50.7843 | -47.4884 | 31.0455 | -50.6241 | 72.3907 | 72.3221 | -50.798 | -50.8118 | -0.11902 | -0.20142 | 0.073242 | 122.9462 | -0.045776 | 0.15564 | -0.19226 | -0.21515 | -0.22888 | 0.059509 | 3.0945 | -0.041198 | 0.18768 | -0.009155 | 122.9874 | 122.7219 | 56.5475 | -123.1155 | 122.9736 | 122.905 | 81.6284 | -123.143
3564.0156 | 123.111 | -49.2096 | 73.6725 | -0.23666 | 0.010013 | 0.0706 | 0.070517 | 0.12993 | -0.0039221 | -0.010922 | -0.068817 | -0.0099806 | 0.064264 | 0.055689 | 0.0099762 | -0.0096238 | 73.4344 | 73.7045 | 6.3309 | -49.3332 | 73.6816 | -49.3607 | -49.4522 | -46.0693 | 32.5333 | -49.4339 | 73.7869 | 73.6679 | -49.4202 | -49.4522 | -0.15106 | -0.24261 | 0.009156 | 122.9141 | -0.1236 | 0.11902 | -0.23804 | -0.21057 | -0.24261 | 0.11444 | 3.1403 | -0.2243 | 0.01831 | -0.004577 | 122.8912 | 122.644 | 55.5405 | -123.1247 | 122.9965 | 122.8775 | 81.7429 | -123.1247
3565.0156 | 123.0972 | -48.8068 | 74.1302 | -0.19089 | 0.014499 | 0.072523 | 0.074576 | 0.128 | -0.00093145 | -0.0098545 | -0.18326 | -0.012758 | 0.062982 | 0.05633 | 0.0084808 | -0.013255 | 73.9334 | 74.1302 | 6.189 | -48.8846 | 74.1898 | -48.9166 | -49.0082 | -45.7352 | 32.4875 | -48.8754 | 74.1989 | 74.1028 | -49.0265 | -49.0723 | -0.10986 | -0.20142 | 0.059509 | 122.937 | -0.07782 | 0.1236 | -0.19684 | -0.21973 | -0.2655 | 0.068665 | 3.0716 | -0.068664 | 0.19684 | -0.027466 | 122.9965 | 122.7402 | 54.9957 | -123.1384 | 123.0057 | 122.9095 | 81.2943 | -123.2025
3566.0156 | 122.9645 | -49.5483 | 73.3841 | -0.14511 | 0.016849 | 0.072736 | 0.071158 | 0.12993 | 0.0046227 | -0.0079319 | -0.099335 | -0.009126 | 0.067255 | 0.056758 | 0.01254 | -0.015178 | 73.3566 | 73.5031 | 5.8502 | -49.5071 | 73.6862 | -49.5346 | -49.6033 | -46.3074 | 31.8741 | -49.617 | 73.5718 | 73.4344 | -49.736 | -49.791 | 0.013733 | -0.054931 | 0.30212 | 123.0515 | 0.041199 | 0.09613 | -0.027466 | -0.18768 | -0.24261 | 0.18768 | 3.241 | -0.068664 | 0.17395 | 0.050354 | 123.2346 | 122.905 | 55.3986 | -122.9874 | 123.1201 | 122.9828 | 81.4224 | -123.175
3567.0156 | 123.0606 | -48.9441 | 74.0158 | -0.25192 | 0.014712 | 0.072096 | 0.07009 | 0.12672 | -0.0017859 | -0.0085727 | -0.18326 | -0.010408 | 0.063837 | 0.05633 | 0.009549 | -0.01176 | 73.819 | 74.0524 | 5.9235 | -48.9395 | 74.1623 | -48.9853 | -49.0631 | -45.8633 | 32.4097 | -48.9899 | 74.1211 | 74.0021 | -49.1409 | -49.1684 | -0.041199 | -0.11902 | 0.14648 | 122.9965 | 0.004578 | 0.1236 | -0.19684 | -0.19684 | -0.2243 | 0.10529 | 3.0807 | -0.045776 | 0.17853 | -0.013733 | 123.1064 | 122.7631 | 54.8676 | -123.0789 | 123.0652 | 122.9462 | 81.3538 | -123.1842
3568.0156 | 123.1293 | -50.6195 | 72.2763 | -0.045929 | 0.010013 | 0.073164 | 0.072226 | 0.12693 | -0.0037085 | -0.0070773 | 0.068512 | -0.01233 | 0.062128 | 0.056117 | 0.0082672 | -0.010478 | 72.1115 | 72.3404 | 5.722 | -50.6653 | 72.4091 | -50.6882 | -50.7706 | -47.4564 | 30.9586 | -50.6058 | 72.3587 | 72.2626 | -50.8209 | -50.8713 | -0.068664 | -0.15106 | 0.13275 | 122.9599 | -0.045776 | 0.10529 | -0.1648 | -0.20142 | -0.25177 | 0.082398 | 3.1631 | 0.013733 | 0.2655 | -0.013733 | 123.0286 | 122.731 | 56.3416 | -123.0469 | 122.9782 | 122.8821 | 81.5781 | -123.1476
3569.0156 | 123.1293 | -50.2487 | 72.6746 | -0.19089 | 0.012362 | 0.072523 | 0.072012 | 0.12758 | -0.0015723 | -0.0083591 | -0.17563 | -0.010621 | 0.067896 | 0.057398 | 0.0065582 | -0.013469 | 72.4823 | 72.6974 | 5.7632 | -50.3586 | 72.702 | -50.3815 | -50.4822 | -47.1451 | 31.3477 | -50.322 | 72.702 | 72.6379 | -50.4913 | -50.5325 | -0.13275 | -0.23346 | 0.027465 | 122.9462 | -0.10986 | 0.1236 | -0.19226 | -0.24262 | -0.28381 | 0.027465 | 3.1036 | -0.073242 | 0.21057 | -0.036622 | 122.9507 | 122.731 | 56.012 | -123.1567 | 122.9507 | 122.8867 | 81.5964 | -123.2071
3570.0156 | 123.175 | -49.1867 | 73.6816 | -0.045929 | 0.0076627 | 0.071882 | 0.072226 | 0.12993 | -0.0017859 | -0.0089999 | 0.015106 | -0.011262 | 0.066828 | 0.059107 | 0.0084808 | -0.012828 | 73.5626 | 73.8235 | 5.9143 | -49.1867 | 73.8693 | -49.2142 | -49.3057 | -46.0327 | 32.2174 | -49.1684 | 73.8098 | 73.7 | -49.3927 | -49.4476 | -0.027465 | -0.11902 | 0.18768 | 123.0103 | 0 | 0.11902 | -0.11902 | -0.20599 | -0.26093 | 0.12817 | 3.154 | 0.018311 | 0.27924 | 0.01831 | 123.056 | 122.7493 | 55.101 | -122.9874 | 122.9965 | 122.8867 | 81.4041 | -123.1293
3571.0156 | 123.1155 | -48.7427 | 74.1302 | -0.85464 | 0.010013 | 0.071241 | 0.072012 | 0.12971 | -0.0015723 | -0.0072911 | -0.091705 | -0.010621 | 0.063196 | 0.056971 | 0.0086944 | -0.015392 | 73.9151 | 74.2126 | 5.9006 | -48.8342 | 74.2538 | -48.8663 | -48.9395 | -45.6345 | 32.6569 | -48.7564 | 74.231 | 74.0982 | -48.9441 | -48.9944 | -0.1236 | -0.19684 | 0.1236 | 122.9553 | -0.091553 | 0.10529 | -0.21515 | -0.20142 | -0.25177 | 0.10071 | 3.1082 | -0.013733 | 0.23804 | -0.032043 | 122.9965 | 122.6578 | 54.6433 | -123.0698 | 122.9736 | 122.8409 | 81.3995 | -123.1247
3572.0156 | 123.1201 | -50.3952 | 72.5006 | 0.037994 | 0.010226 | 0.072736 | 0.07244 | 0.12629 | -0.0034949 | -0.0098545 | 0.030365 | -0.011689 | 0.063196 | 0.057185 | 0.0069854 | -0.012828 | 72.4045 | 72.5922 | 5.4657 | -50.3815 | 72.7249 | -50.4089 | -50.5371 | -47.2916 | 31.2881 | -50.5051 | 72.5876 | 72.4869 | -50.6241 | -50.6287 | -0.013733 | -0.14191 | 0.22431 | 122.9874 | 0.013733 | 0.15564 | -0.09613 | -0.22888 | -0.23346 | 0.086975 | 3.1036 | -0.10986 | 0.1236 | -0.013733 | 123.1201 | 122.7997 | 55.8609 | -123.0377 | 122.9828 | 122.8821 | 81.6834 | -123.1293
3573.0156 | 123.0148 | -49.0082 | 73.8327 | 0.015106 | 0.0091581 | 0.0706 | 0.071372 | 0.128 | -0.0026405 | -0.0072911 | -0.084076 | -0.0093396 | 0.0664 | 0.056758 | 0.0091216 | -0.013255 | 73.8327 | 74.0524 | 5.9097 | -48.9899 | 74.0707 | -49.0356 | -49.1272 | -45.9412 | 32.5058 | -49.1409 | 73.9059 | 73.8052 | -49.2599 | -49.2691 | -0.027466 | -0.11902 | 0.23804 | 123.0606 | 0.018311 | 0.13733 | 0 | -0.25177 | -0.26093 | 0.073242 | 3.067 | -0.13275 | 0.12817 | -0.027466 | 123.0789 | 122.8409 | 54.9179 | -122.9599 | 122.9141 | 122.8134 | 81.514 | -123.1018
3574.0156 | 123.1293 | -48.3307 | 74.5514 | -0.00015269 | 0.0095853 | 0.071882 | 0.072653 | 0.12886 | -0.00093145 | -0.0087863 | -0.015411 | -0.01233 | 0.064478 | 0.056758 | 0.010403 | -0.013255 | 74.2996 | 74.4827 | 5.8548 | -48.4817 | 74.6109 | -48.4863 | -48.5962 | -45.1813 | 33.1192 | -48.3536 | 74.6246 | 74.5239 | -48.555 | -48.5687 | -0.15564 | -0.2655 | 0.059509 | 122.8134 | -0.15106 | 0.11444 | -0.25177 | -0.22431 | -0.23804 | 0.073242 | 3.1494 | -0.022889 | 0.21515 | -0.027466 | 122.9416 | 122.6303 | 54.1855 | -123.1476 | 122.9553 | 122.8546 | 81.4499 | -123.1201
3575.0156 | 123.1659 | -48.0515 | 74.8215 | -0.10696 | 0.010013 | 0.071455 | 0.071585 | 0.12758 | -0.00093145 | -0.010068 | -0.099335 | -0.010621 | 0.063623 | 0.049067 | 0.0084808 | -0.013042 | 74.707 | 74.913 | 5.9601 | -48.1384 | 74.9176 | -48.1659 | -48.262 | -44.8837 | 33.0643 | -47.9324 | 74.913 | 74.794 | -48.2803 | -48.2986 | -0.11444 | -0.21057 | 0.096131 | 122.9645 | -0.086975 | 0.1236 | -0.11444 | -0.22888 | -0.24719 | 0.091553 | 3.1677 | 0.11902 | 0.36621 | -0.027466 | 122.9691 | 122.7585 | 54.0115 | -123.0835 | 122.9645 | 122.8455 | 81.1157 | -123.1201
3576.0156 | 123.0972 | -51.1551 | 71.7041 | 0.16769 | 0.010226 | 0.0706 | 0.070944 | 0.12779 | -0.0015723 | -0.0070773 | 0.11429 | -0.010194 | 0.064691 | 0.05868 | 0.01019 | -0.012614 | 71.5668 | 71.7728 | 5.2368 | -51.2054 | 71.8643 | -51.2054 | -51.3153 | -48.024 | 30.5557 | -51.2421 | 71.7911 | 71.6721 | -51.4114 | -51.4343 | -0.050354 | -0.16022 | 0.16022 | 122.9279 | -0.050354 | 0.10986 | -0.13733 | -0.25635 | -0.27924 | 0.086975 | 3.1311 | -0.086975 | 0.19226 | -0.032044 | 123.0194 | 122.7219 | 56.3919 | -123.0194 | 122.9462 | 122.8271 | 81.7108 | -123.1384
3577.0156 | 123.1613 | -50.5646 | 72.2992 | -0.0077822 | 0.012362 | 0.070387 | 0.070731 | 0.12672 | -7.6852e-05 | -0.0077183 | -0.0077819 | -0.011049 | 0.063837 | 0.05868 | 0.0091216 | -0.012828 | 72.0337 | 72.2534 | 5.4428 | -50.7523 | 72.2992 | -50.798 | -50.8987 | -47.3831 | 31.1325 | -50.5188 | 72.3495 | 72.2443 | -50.7706 | -50.8118 | -0.23346 | -0.33417 | 0 | 122.818 | -0.18768 | 0.14649 | -0.2655 | -0.20599 | -0.24719 | 0.050354 | 3.1815 | 0.045776 | 0.29297 | -0.054931 | 122.8638 | 122.5983 | 56.0074 | -123.1979 | 122.9141 | 122.8088 | 81.6971 | -123.111
3578.0156 | 123.1201 | -49.9741 | 72.9172 | 0.13718 | 0.010867 | 0.0706 | 0.072012 | 0.12928 | -0.0013587 | -0.010495 | 0.14481 | -0.010835 | 0.06341 | 0.058039 | 0.008908 | -0.013896 | 72.6746 | 72.8714 | 5.4245 | -50.1022 | 72.9767 | -50.0793 | -50.1755 | -46.7834 | 31.6132 | -50.029 | 73.0041 | 72.9172 | -50.1755 | -50.1801 | -0.10529 | -0.20142 | 0.05951 | 122.8455 | -0.12817 | 0.073242 | -0.24261 | -0.20142 | -0.20599 | 0.086975 | 3.1906 | -0.054932 | 0.15106 | 0 | 122.9507 | 122.6486 | 55.3986 | -123.0927 | 122.9782 | 122.8912 | 81.5872 | -123.0972
3579.0156 | 123.1247 | -49.3744 | 73.4894 | 0.0074768 | 0.0078763 | 0.071027 | 0.071585 | 0.12693 | -0.0034949 | -0.0055821 | 0.037995 | -0.0097668 | 0.062982 | 0.055262 | 0.0084808 | -0.012614 | 73.2925 | 73.5077 | 5.5527 | -49.4888 | 73.5855 | -49.498 | -49.6078 | -46.1563 | 32.2266 | -49.3927 | 73.6221 | 73.5214 | -49.5667 | -49.6353 | -0.1236 | -0.23346 | 0.09613 | 122.8821 | -0.11444 | 0.11902 | -0.19684 | -0.19226 | -0.26093 | 0.13275 | 3.2181 | -0.01831 | 0.24262 | 0.032043 | 122.9599 | 122.6669 | 54.9271 | -123.0972 | 122.9965 | 122.8958 | 81.601 | -123.1247
3580.0156 | 123.1064 | -49.8001 | 73.0774 | 0.11429 | 0.010226 | 0.072096 | 0.072226 | 0.12822 | 0.00077755 | -0.0081455 | 0.037995 | -0.011476 | 0.064051 | 0.054408 | 0.011044 | -0.013042 | 72.9218 | 73.1003 | 5.452 | -49.8871 | 73.1873 | -49.8779 | -49.9466 | -46.5729 | 31.8604 | -49.7406 | 73.2101 | 73.0957 | -49.9695 | -49.9969 | -0.07782 | -0.14648 | 0.10986 | 122.9004 | -0.086975 | 0.059509 | -0.15564 | -0.16937 | -0.19684 | 0.13275 | 3.2272 | 0.059509 | 0.25635 | 0.01831 | 122.9874 | 122.7219 | 55.2521 | -123.024 | 123.0103 | 122.8958 | 81.6605 | -123.0743
3581.0156 | 123.1659 | -48.4085 | 74.4598 | -0.015411 | 0.010013 | 0.071668 | 0.070517 | 0.13078 | -0.00071785 | -0.0083591 | -0.00015237 | -0.011262 | 0.064691 | 0.055476 | 0.008908 | -0.014323 | 74.3088 | 74.5102 | 5.8228 | -48.4909 | 74.6109 | -48.5092 | -48.6145 | -45.2454 | 33.0505 | -48.4177 | 74.5331 | 74.4736 | -48.6099 | -48.6511 | -0.10071 | -0.20599 | 0.15106 | 122.9187 | -0.082398 | 0.1236 | -0.15106 | -0.20142 | -0.24262 | 0.073242 | 3.1631 | -0.009156 | 0.23346 | 0.013733 | 123.0194 | 122.7173 | 54.2313 | -123.0743 | 122.9416 | 122.8821 | 81.459 | -123.111
3582.0156 | 123.1613 | -47.4792 | 75.3799 | -1.2056 | 0.013003 | 0.071668 | 0.070517 | 0.12993 | 0.0020593 | -0.0072911 | 0.25925 | -0.011262 | 0.063196 | 0.055262 | 0.013181 | -0.012828 | 75.2701 | 75.4486 | 6.0699 | -47.5433 | 75.5219 | -47.6028 | -47.6532 | -44.2932 | 33.8196 | -47.5388 | 75.4807 | 75.3616 | -47.7081 | -47.7219 | -0.1236 | -0.17395 | 0.14191 | 122.9279 | -0.064087 | 0.10986 | -0.10986 | -0.22888 | -0.24262 | 0.10071 | 3.186 | -0.059509 | 0.18311 | -0.018311 | 123.0011 | 122.7493 | 53.5492 | -123.0331 | 122.9599 | 122.8409 | 81.2988 | -123.1018
3583.0156 | 123.111 | -50.1114 | 72.789 | 0.045624 | 0.0085171 | 0.0706 | 0.07244 | 0.12715 | -0.00050425 | -0.0055821 | 0.16769 | -0.0093396 | 0.065546 | 0.056758 | 0.0099762 | -0.013255 | 72.3999 | 72.789 | 5.6259 | -50.2304 | 72.8577 | -50.2487 | -50.3357 | -46.9299 | 31.5262 | -50.1846 | 72.8668 | 72.7432 | -50.3403 | -50.3815 | -0.13733 | -0.2243 | 0.068665 | 122.9004 | -0.11902 | 0.10529 | -0.3891 | -0.22888 | -0.27008 | 0.07782 | 3.1815 | -0.073242 | 0.19684 | -0.045776 | 122.9691 | 122.5113 | 55.7373 | -123.1247 | 122.9782 | 122.8546 | 81.6376 | -123.1705
3584.0156 | 123.1338 | -51.0956 | 71.7682 | 0.27451 | 0.013217 | 0.071027 | 0.07244 | 0.12758 | 0.0018457 | -0.0057957 | 0.16769 | -0.010621 | 0.067041 | 0.055476 | 0.0091216 | -0.01411 | 71.7041 | 71.8506 | 5.2963 | -51.1322 | 71.8689 | -51.178 | -51.2695 | -47.8592 | 30.748 | -51.1688 | 71.8552 | 71.7407 | -51.3153 | -51.3794 | -0.082398 | -0.17395 | 0.10071 | 122.9462 | -0.036621 | 0.13733 | -0.064086 | -0.21973 | -0.28381 | 0.086976 | 3.2364 | -0.073242 | 0.21057 | -0.027465 | 122.9645 | 122.7997 | 56.3919 | -123.0377 | 122.9507 | 122.8363 | 81.8436 | -123.1476
3585.0156 | 123.2483 | -50.1984 | 72.6791 | 0.12955 | 0.0078763 | 0.071882 | 0.069876 | 0.12715 | -0.00050425 | -0.0072911 | 0.068512 | -0.0099806 | 0.064478 | 0.058467 | 0.0080536 | -0.012401 | 72.5052 | 72.6334 | 5.4062 | -50.3311 | 72.7844 | -50.3128 | -50.4272 | -46.9391 | 31.5811 | -50.1343 | 72.8073 | 72.6974 | -50.386 | -50.4227 | -0.11444 | -0.22888 | 0.10529 | 122.8317 | -0.13275 | 0.09613 | -0.17395 | -0.18768 | -0.2243 | 0.12817 | 3.2593 | 0.064087 | 0.28839 | 0.018311 | 122.9828 | 122.7036 | 55.6046 | -123.1064 | 123.0057 | 122.8958 | 81.7795 | -123.1018
3586.0156 | 123.1613 | -50.6607 | 72.1802 | 0.19821 | 0.01514 | 0.069532 | 0.071799 | 0.12779 | 0.0033411 | -0.0057957 | -1.6939 | -0.0089124 | 0.065546 | 0.057185 | 0.011258 | -0.014751 | 72.1207 | 72.258 | 4.454 | -50.7111 | 72.2992 | -50.7523 | -50.8804 | -47.3602 | 31.0959 | -50.6836 | 72.3267 | 72.2122 | -50.8713 | -50.9125 | -0.091552 | -0.21973 | 0.11902 | 122.9187 | -0.050354 | 0.16937 | -0.059509 | -0.21057 | -0.25177 | 0.14648 | 3.3005 | -0.022888 | 0.22888 | 0.032043 | 122.9599 | 122.7814 | 55.1147 | -123.0606 | 122.9874 | 122.8729 | 81.7566 | -123.0927
3587.0156 | 123.1338 | -50.0839 | 72.7982 | 0.15244 | 0.012362 | 0.0706 | 0.069449 | 0.12907 | -0.00071785 | -0.0077183 | 0.19821 | -0.010408 | 0.06341 | 0.057398 | 0.01019 | -0.011119 | 72.67 | 72.8485 | 4.6738 | -50.1617 | 72.9355 | -50.1617 | -50.2625 | -46.843 | 31.6452 | -50.1297 | 72.9034 | 72.789 | -50.2945 | -50.3357 | -0.07782 | -0.17853 | 0.13733 | 122.9324 | -0.07782 | 0.10071 | -0.12817 | -0.21057 | -0.25177 | 0.10528 | 3.241 | -0.045777 | 0.20599 | -0.009156 | 123.0194 | 122.7539 | 54.7577 | -123.0606 | 122.9874 | 122.8729 | 81.7291 | -123.1338
3588.0156 | 123.1613 | -49.0631 | 73.7503 | 1.8843 | 0.016849 | 0.072096 | 0.074576 | 0.13078 | 0.0046227 | -0.0066501 | 0.16006 | -0.010835 | 0.064691 | 0.055903 | 0.012112 | -0.013042 | 73.4894 | 73.7091 | 4.8523 | -49.2416 | 73.7686 | -49.2828 | -49.3835 | -45.7535 | 32.5424 | -48.9807 | 73.938 | 73.8052 | -49.2645 | -49.2966 | -0.21973 | -0.32043 | 0.018311 | 122.7722 | -0.17853 | 0.14191 | -0.26093 | -0.20142 | -0.23346 | 0.18768 | 3.3096 | 0.082397 | 0.31586 | 0.054932 | 122.8317 | 122.5525 | 53.9154 | -123.1338 | 123.0011 | 122.8683 | 81.6055 | -123.0469
3589.0156 | 123.0972 | -48.8571 | 74.0112 | 0.12192 | 0.013431 | 0.0706 | 0.071372 | 0.12608 | 0.00013675 | -0.0075047 | 0.19821 | -0.0099806 | 0.065973 | 0.058039 | 0.011258 | -0.012187 | 73.9014 | 74.1119 | 5.5298 | -48.9166 | 74.1577 | -48.9395 | -49.054 | -45.6345 | 32.7118 | -49.0036 | 74.0524 | 73.9655 | -49.1043 | -49.1318 | -0.082397 | -0.19684 | 0.14648 | 122.9691 | -0.059509 | 0.13733 | -0.10986 | -0.24719 | -0.27466 | 0.041199 | 3.2227 | -0.14648 | 0.12817 | -0.045776 | 123.0148 | 122.7585 | 54.3869 | -123.0652 | 122.9095 | 122.8226 | 81.5689 | -123.143
3590.0156 | 123.111 | -48.2941 | 74.5422 | 0.20584 | 0.019198 | 0.071027 | 0.076071 | 0.13035 | 0.0029137 | -0.0034457 | 0.16006 | -0.0084852 | 0.066614 | 0.057826 | 0.014035 | -0.013255 | 74.6475 | 74.7849 | 5.6854 | -48.1567 | 74.9725 | -48.1613 | -48.2712 | -44.902 | 33.2932 | -48.5001 | 74.826 | 74.6475 | -48.4863 | -48.5184 | 0.13275 | 0.022888 | 0.4303 | 123.0789 | 0.13733 | 0.11444 | 0.10529 | -0.19226 | -0.22431 | 0.28381 | 3.392 | -0.20599 | 0.018311 | 0.10529 | 123.2666 | 122.9416 | 53.9795 | -122.8134 | 123.1201 | 122.9416 | 81.5872 | -123.0606
3591.0156 | 123.1064 | -47.1725 | 75.7278 | 0.14481 | 0.011935 | 0.070173 | 0.071158 | 0.12822 | -0.0013587 | -0.0081455 | 0.19058 | -0.010835 | 0.064478 | 0.056544 | 0.01254 | -0.012187 | 75.6363 | 75.8331 | 5.9326 | -47.1725 | 75.9338 | -47.1634 | -47.2641 | -43.8492 | 34.2773 | -47.319 | 75.8514 | 75.7324 | -47.3877 | -47.4335 | 0.009155 | -0.091553 | 0.20599 | 123.0057 | 0 | 0.091553 | -0.091552 | -0.21515 | -0.26093 | 0.1236 | 3.3234 | -0.14649 | 0.11444 | 0.004578 | 123.1064 | 122.8088 | 53.1052 | -122.9919 | 123.024 | 122.905 | 81.4499 | -123.1613
3592.0156 | 123.1338 | -50.116 | 72.789 | 0.19058 | 0.01813 | 0.0706 | 0.075217 | 0.12886 | 0.0046227 | -0.0051547 | 0.25162 | -0.0097668 | 0.067041 | 0.055689 | 0.011044 | -0.011333 | 72.6608 | 72.8027 | 5.2872 | -50.1617 | 72.8989 | -50.1892 | -50.3265 | -46.8109 | 31.7368 | -50.0702 | 72.8806 | 72.7341 | -50.3494 | -50.3769 | -0.073242 | -0.21057 | 0.10986 | 122.9187 | -0.045776 | 0.16479 | -0.12817 | -0.23346 | -0.26093 | 0.091553 | 3.3051 | 0.045777 | 0.3067 | -0.054931 | 123.0148 | 122.7768 | 55.4031 | -123.1155 | 122.9965 | 122.85 | 81.8527 | -123.1659
3593.0156 | 123.1247 | -49.649 | 73.2376 | 0.12955 | 0.013217 | 0.071455 | 0.069235 | 0.12907 | -0.0015723 | -0.0064365 | 0.2211 | -0.010835 | 0.065332 | 0.057398 | 0.01019 | -0.010478 | 73.0728 | 73.2468 | 5.4245 | -49.7543 | 73.2925 | -49.7681 | -49.8825 | -46.3943 | 32.0251 | -49.6674 | 73.2788 | 73.1964 | -49.8917 | -49.9146 | -0.11902 | -0.23346 | 0.054932 | 122.8958 | -0.10529 | 0.12817 | -0.16479 | -0.24262 | -0.2655 | 0.041199 | 3.2547 | -0.01831 | 0.24719 | -0.041199 | 122.9416 | 122.7219 | 55.0735 | -123.1201 | 122.9279 | 122.8455 | 81.6742 | -123.1522
3594.0156 | 123.1201 | -49.5438 | 73.2742 | 0.27451 | 0.01813 | 0.070387 | 0.073508 | 0.13035 | 0.0020593 | -0.0049411 | 0.22873 | -0.0089124 | 0.064051 | 0.057398 | 0.011044 | -0.014751 | 73.2605 | 73.3841 | 5.3925 | -49.5667 | 73.4985 | -49.5712 | -49.6948 | -46.2524 | 32.1671 | -49.5987 | 73.4344 | 73.3475 | -49.7406 | -49.7498 | -0.027466 | -0.15106 | 0.2243 | 122.9279 | -0.022888 | 0.12817 | -0.013733 | -0.19684 | -0.20599 | 0.16022 | 3.2913 | -0.054932 | 0.15106 | 0.073242 | 123.0423 | 122.8043 | 54.9362 | -122.9691 | 122.9782 | 122.8912 | 81.7108 | -123.024
3595.0156 | 123.0881 | -48.6465 | 74.2355 | 0.13718 | 0.013217 | 0.072309 | 0.071158 | 0.12928 | -0.0019995 | -0.0060093 | 0.24399 | -0.0093396 | 0.066187 | 0.057612 | 0.01019 | -0.010051 | 74.0982 | 74.263 | 5.397 | -48.7656 | 74.35 | -48.761 | -48.8571 | -45.4697 | 32.8857 | -48.6694 | 74.2859 | 74.1898 | -48.9029 | -48.9304 | -0.11444 | -0.21057 | 0.11444 | 122.9095 | -0.11902 | 0.091553 | -0.13733 | -0.25635 | -0.28381 | 0.050354 | 3.1769 | -0.022889 | 0.26093 | -0.045777 | 122.9965 | 122.7448 | 54.0436 | -123.0927 | 122.9324 | 122.8363 | 81.5323 | -123.1659
3596.0156 | 123.0286 | -48.6099 | 74.2859 | 0.22873 | 0.017276 | 0.068891 | 0.074362 | 0.12672 | 0.0037683 | -0.0057957 | 0.15244 | -0.009126 | 0.066614 | 0.056758 | 0.012112 | -0.013255 | 74.1165 | 74.1852 | 5.4657 | -48.7427 | 74.4507 | -48.7061 | -48.8022 | -45.369 | 32.9407 | -48.6923 | 74.4324 | 74.3179 | -48.8434 | -48.848 | -0.096131 | -0.19226 | 0.16479 | 122.7951 | -0.13275 | 0.059509 | -0.16937 | -0.23346 | -0.23804 | 0.14648 | 3.241 | -0.082398 | 0.15564 | 0.032043 | 123.0606 | 122.7264 | 54.0756 | -123.0881 | 123.0423 | 122.9279 | 81.5506 | -123.1338
3597.0156 | 123.2025 | -47.8683 | 74.9817 | 0.16769 | 0.01578 | 0.070173 | 0.069876 | 0.12843 | 0.00077755 | -0.0066501 | 0.26688 | -0.010194 | 0.066187 | 0.055049 | 0.012753 | -0.014323 | 74.881 | 75.0275 | 5.8273 | -47.9462 | 75.1007 | -47.9736 | -48.0606 | -44.7006 | 33.4717 | -47.7676 | 75.0183 | 74.9817 | -48.1201 | -48.1384 | -0.10529 | -0.19226 | 0.11902 | 122.8958 | -0.07782 | 0.11444 | -0.10071 | -0.25177 | -0.27008 | 0.036622 | 3.1677 | 0.10071 | 0.37079 | 0 | 122.9691 | 122.7493 | 53.6957 | -123.0423 | 122.8867 | 122.85 | 81.34 | -123.1201
3598.0156 | 123.1064 | -48.2803 | 74.6246 | 0.16006 | 0.016635 | 0.072309 | 0.076285 | 0.128 | 0.0033411 | -0.0064365 | 0.20584 | -0.0095532 | 0.067255 | 0.057826 | 0.0099762 | -0.014323 | 74.4232 | 74.5239 | 5.7404 | -48.3307 | 74.762 | -48.381 | -48.4726 | -44.9982 | 33.4946 | -48.3353 | 74.7528 | 74.707 | -48.4589 | -48.4955 | -0.10071 | -0.19226 | 0.13733 | 122.8043 | -0.050354 | 0.14191 | -0.20142 | -0.17853 | -0.21515 | 0.12817 | 3.2822 | -0.054932 | 0.16022 | 0.082397 | 123.0423 | 122.7036 | 54.0207 | -123.0972 | 123.0331 | 122.9874 | 81.7749 | -123.1201
3599.0156 | 123.1567 | -48.0698 | 74.8398 | 0.19821 | 0.01813 | 0.068037 | 0.07009 | 0.12843 | -0.0017859 | -0.0057957 | 0.28214 | -0.009126 | 0.065759 | 0.055903 | 0.011044 | -0.012401 | 74.5926 | 74.8993 | 5.7678 | -48.1155 | 74.9496 | -48.1339 | -48.2117 | -44.8105 | 33.6548 | -48.0743 | 74.8947 | 74.8215 | -48.2712 | -48.2941 | -0.064087 | -0.14191 | 0.10986 | 122.9691 | -0.045777 | 0.09613 | -0.24719 | -0.20142 | -0.2243 | 0.054931 | 3.2593 | -0.004578 | 0.21973 | -0.018311 | 123.0194 | 122.6624 | 53.8376 | -123.0515 | 122.9645 | 122.8912 | 81.7245 | -123.1338
3600.0156 | 123.111 | -48.349 | 74.5514 | 0.12955 | 0.017489 | 0.070173 | 0.073508 | 0.13121 | 0.0027001 | -0.0051547 | 0.19058 | -0.0067762 | 0.067896 | 0.056758 | 0.01254 | -0.012614 | 74.3866 | 74.4781 | 5.6168 | -48.4497 | 74.7482 | -48.4268 | -48.5092 | -45.1447 | 33.3115 | -48.3765 | 74.6658 | 74.5789 | -48.587 | -48.6008 | -0.07782 | -0.16022 | 0.19684 | 122.8271 | -0.10071 | 0.059509 | -0.1648 | -0.23804 | -0.25177 | 0.11444 | 3.2043 | -0.027466 | 0.2243 | 0.027465 | 123.0972 | 122.7356 | 53.9658 | -123.0606 | 123.0148 | 122.9279 | 81.6605 | -123.1522
3601.0156 | 123.1201 | -48.0148 | 74.8581 | 0.16006 | 0.01514 | 0.070387 | 0.070303 | 0.13014 | -0.0032813 | -0.0070773 | 0.24399 | -0.010408 | 0.063837 | 0.057185 | 0.0093354 | -0.0098374 | 74.7757 | 74.9359 | 5.7816 | -48.0515 | 74.9817 | -48.0515 | -48.1613 | -44.7601 | 33.6868 | -48.0194 | 74.9496 | 74.8672 | -48.2437 | -48.2666 | -0.036621 | -0.14648 | 0.1236 | 122.9507 | -0.036621 | 0.10986 | -0.082397 | -0.22888 | -0.25177 | 0.091553 | 3.2547 | -0.004577 | 0.24719 | 0.009156 | 122.9965 | 122.7905 | 53.7964 | -123.0194 | 122.9645 | 122.8821 | 81.7017 | -123.1247
3602.0156 | 123.111 | -47.4106 | 75.444 | 0.18295 | 0.018771 | 0.069746 | 0.075217 | 0.13099 | 0.0018457 | -0.0081455 | 0.23636 | -0.0082716 | 0.065973 | 0.056758 | 0.012112 | -0.013683 | 75.3021 | 75.4257 | 5.69 | -47.5159 | 75.6042 | -47.5021 | -47.6028 | -44.1788 | 34.1675 | -47.4655 | 75.5722 | 75.4669 | -47.6669 | -47.6669 | -0.091553 | -0.19226 | 0.16022 | 122.8363 | -0.10529 | 0.086975 | -0.14191 | -0.25635 | -0.25635 | 0.12817 | 3.2318 | -0.054932 | 0.20142 | 0.022888 | 123.0148 | 122.7127 | 53.1006 | -123.0469 | 122.9828 | 122.8775 | 81.5781 | -123.111
3603.0156 | 123.143 | -50.9033 | 71.9742 | 0.0914 | 0.016421 | 0.071455 | 0.070303 | 0.13014 | 0.0022729 | -0.0057957 | 0.24399 | -0.0099806 | 0.067468 | 0.055689 | 0.012326 | -0.011333 | 71.8689 | 71.9925 | 5.0949 | -50.9445 | 72.0978 | -50.9674 | -51.0635 | -47.5937 | 31.2424 | -51.1551 | 72.0108 | 71.933 | -51.178 | -51.1642 | -0.064087 | -0.16022 | 0.1236 | 122.8958 | -0.041199 | 0.11902 | -0.10529 | -0.27466 | -0.26093 | 0.036621 | 3.3096 | -0.25177 | 0.009156 | -0.041199 | 123.0011 | 122.7722 | 55.9982 | -123.0377 | 122.9141 | 122.8363 | 82.1457 | -123.1384
3604.0156 | 123.1476 | -50.2167 | 72.67 | 0.16769 | 0.016849 | 0.069105 | 0.073508 | 0.128 | 0.00035035 | -0.0072911 | 0.18295 | -0.0097668 | 0.066828 | 0.057398 | 0.011258 | -0.013042 | 72.4777 | 72.583 | 5.0812 | -50.322 | 72.8073 | -50.3128 | -50.4456 | -46.9482 | 31.8375 | -50.3036 | 72.7753 | 72.7158 | -50.4593 | -50.4822 | -0.09613 | -0.22888 | 0.13733 | 122.7997 | -0.10528 | 0.1236 | -0.19226 | -0.24262 | -0.2655 | 0.10529 | 3.2684 | -0.086975 | 0.17853 | 0.045776 | 123.024 | 122.6944 | 55.2979 | -123.1155 | 122.9919 | 122.9324 | 82.0541 | -123.1522
3605.0156 | 123.1338 | -49.1226 | 73.7366 | -0.091705 | 0.013858 | 0.070814 | 0.069876 | 0.13035 | -0.0024269 | -0.0057957 | 0.28214 | -0.010194 | 0.0664 | 0.058253 | 0.010617 | -0.011333 | 73.6771 | 73.8373 | 5.3101 | -49.1364 | 73.9014 | -49.1455 | -49.2645 | -45.8908 | 32.84 | -49.2416 | 73.7915 | 73.7228 | -49.379 | -49.3973 | -0.022888 | -0.14191 | 0.16479 | 122.9599 | -0.013733 | 0.12817 | -0.059509 | -0.25635 | -0.27466 | 0.054932 | 3.2318 | -0.11902 | 0.15564 | -0.013733 | 123.024 | 122.7997 | 54.4327 | -123.0011 | 122.9141 | 122.8455 | 81.9626 | -123.1338
3606.0156 | 123.0606 | -48.0835 | 74.8169 | 0.15244 | 0.018985 | 0.069959 | 0.072226 | 0.12864 | 0.00077755 | -0.0045139 | 0.21347 | -0.007417 | 0.067468 | 0.057612 | 0.012753 | -0.014537 | 74.6521 | 74.7391 | 5.4153 | -48.1705 | 74.9817 | -48.1339 | -48.2574 | -44.7647 | 33.7646 | -48.1888 | 74.9725 | 74.8535 | -48.2803 | -48.3307 | -0.050354 | -0.17395 | 0.16479 | 122.8226 | -0.086975 | 0.086975 | -0.16479 | -0.19684 | -0.24719 | 0.15564 | 3.3188 | -0.10529 | 0.14191 | 0.036621 | 123.0652 | 122.7356 | 53.4988 | -123.0743 | 123.056 | 122.937 | 81.8481 | -123.1476
3607.0156 | 123.1567 | -47.9736 | 74.8718 | 0.19058 | 0.016208 | 0.071241 | 0.070303 | 0.1295 | -0.0013587 | -0.0092137 | 0.12192 | -0.010621 | 0.064264 | 0.056117 | 0.010617 | -0.011119 | 74.9908 | 74.9084 | 5.6076 | -47.9782 | 75.0183 | -48.0469 | -48.111 | -44.6732 | 33.9798 | -47.9416 | 74.9954 | 74.9268 | -48.1934 | -48.2254 | -0.073242 | -0.13733 | 0.14648 | 122.8821 | -0.004577 | 0.13275 | 0.11902 | -0.21973 | -0.25177 | 0.1236 | 3.3005 | 0.032044 | 0.28381 | 0.054932 | 122.9919 | 122.9645 | 53.5812 | -122.9828 | 122.9691 | 122.9004 | 81.9534 | -123.0972
3608.0156 | 123.1293 | -47.5159 | 75.3799 | 0.23636 | 0.017703 | 0.070387 | 0.071372 | 0.13014 | 0.0022729 | -0.0072911 | 0.2211 | -0.0099806 | 0.066828 | 0.055903 | 0.013394 | -0.011974 | 75.1282 | 75.2197 | 5.5618 | -47.6578 | 75.444 | -47.6669 | -47.7859 | -44.2245 | 34.3826 | -47.4472 | 75.4669 | 75.3799 | -47.7631 | -47.7539 | -0.15106 | -0.27008 | 0.064087 | 122.7356 | -0.14191 | 0.12817 | -0.25177 | -0.24719 | -0.23804 | 0.086975 | 3.2913 | 0.068664 | 0.3067 | 0 | 122.9599 | 122.644 | 53.0777 | -123.1659 | 122.9828 | 122.8958 | 81.8985 | -123.1338
3609.0156 | 123.1384 | -49.5987 | 73.2651 | 0.13718 | 0.015994 | 0.069532 | 0.071372 | 0.12886 | -0.0017859 | -0.0085727 | 0.25162 | -0.011262 | 0.064905 | 0.057826 | 0.0091216 | -0.013255 | 73.1232 | 73.2605 | 5.2826 | -49.6857 | 73.3383 | -49.7406 | -49.8138 | -46.2479 | 32.6111 | -49.5758 | 73.3795 | 73.3154 | -49.7864 | -49.855 | -0.14191 | -0.21515 | 0.073242 | 122.8592 | -0.086975 | 0.12817 | -0.14191 | -0.18768 | -0.25635 | 0.11444 | 3.3508 | 0.022888 | 0.27924 | 0.050354 | 122.937 | 122.7219 | 54.8813 | -123.0789 | 122.9782 | 122.9141 | 82.2098 | -123.1201
3610.0156 | 123.0515 | -51.0223 | 71.8964 | 0.45761 | 0.018771 | 0.073164 | 0.073721 | 0.13078 | 0.0039819 | -0.0072911 | 0.0914 | -0.010835 | 0.068537 | 0.058253 | 0.010403 | -0.012828 | 71.6766 | 71.7545 | 4.7287 | -51.1322 | 72.0383 | -51.1414 | -51.2512 | -47.7585 | 31.2469 | -51.1917 | 72.0108 | 71.933 | -51.2558 | -51.2833 | -0.11902 | -0.22888 | 0.14191 | 122.7768 | -0.10986 | 0.11902 | -0.21973 | -0.23346 | -0.26093 | 0.11444 | 3.2639 | -0.16937 | 0.091553 | 0.036621 | 123.0606 | 122.699 | 55.751 | -123.1476 | 123.0331 | 122.9553 | 82.2693 | -123.1796
3611.0156 | 123.2346 | -49.8505 | 73.0133 | 0.18295 | 0.016208 | 0.072309 | 0.070731 | 0.12629 | -0.0017859 | -0.0062229 | 0.24399 | -0.012544 | 0.067255 | 0.057398 | 0.011472 | -0.013896 | 72.9996 | 73.1186 | 5.1865 | -49.8138 | 73.2697 | -49.8413 | -49.9329 | -46.4951 | 32.4097 | -49.9054 | 73.1552 | 73.0774 | -50.0565 | -50.116 | 0.009155 | -0.082397 | 0.25635 | 122.9691 | 0.036621 | 0.11902 | -0.013733 | -0.20599 | -0.2655 | 0.14191 | 3.3554 | -0.054932 | 0.21057 | 0.064087 | 123.1201 | 122.85 | 55.0369 | -122.9462 | 123.0057 | 122.9279 | 82.2601 | -123.1293
3612.0156 | 123.111 | -49.4797 | 73.407 | 0.12955 | 0.020053 | 0.072096 | 0.073508 | 0.1295 | 0.0020593 | -0.0053683 | 0.18295 | -0.008058 | 0.065973 | 0.058894 | 0.01019 | -0.013896 | 73.2559 | 73.3246 | 5.2322 | -49.5712 | 73.5764 | -49.5667 | -49.6674 | -46.1838 | 32.6706 | -49.5483 | 73.5306 | 73.4573 | -49.6948 | -49.7131 | -0.086975 | -0.18768 | 0.16937 | 122.8043 | -0.091553 | 0.09613 | -0.15106 | -0.21515 | -0.23346 | 0.1236 | 3.2959 | -0.068665 | 0.16479 | 0.050354 | 123.056 | 122.7356 | 54.7119 | -123.0743 | 123.0103 | 122.937 | 82.1503 | -123.1201
3613.0156 | 123.1476 | -50.4868 | 72.3724 | 0.23636 | 0.01514 | 0.069319 | 0.071158 | 0.13142 | 0.0016321 | -0.0060093 | 0.24399 | -0.0095532 | 0.064691 | 0.056117 | 0.01019 | -0.011333 | 72.0612 | 72.6883 | 5.2185 | -50.4913 | 72.5098 | -50.5829 | -50.6332 | -47.0856 | 31.9016 | -50.4913 | 72.4869 | 72.4365 | -50.7065 | -50.7385 | -0.096131 | -0.14648 | 0.13733 | 123.175 | -0.004578 | 0.14191 | -0.31128 | -0.21973 | -0.25177 | 0.11444 | 3.4012 | -0.004578 | 0.24719 | 0.064086 | 122.9965 | 122.5479 | 55.7053 | -123.0057 | 122.9736 | 122.9233 | 82.3883 | -123.111
3614.0156 | 123.111 | -49.6262 | 73.2513 | 0.14481 | 0.017062 | 0.068678 | 0.07244 | 0.12736 | 0.0012047 | -0.0070773 | 0.20584 | -0.011262 | 0.066614 | 0.057826 | 0.011258 | -0.013896 | 73.0865 | 73.1781 | 5.1636 | -49.7543 | 73.3658 | -49.7498 | -49.8596 | -46.3211 | 32.5562 | -49.7543 | 73.3063 | 73.2056 | -49.8962 | -49.9008 | -0.1236 | -0.23346 | 0.11444 | 122.8043 | -0.12817 | 0.10529 | -0.1648 | -0.27008 | -0.27466 | 0.054931 | 3.3051 | -0.12817 | 0.14648 | -0.045777 | 122.9919 | 122.7127 | 54.7897 | -123.111 | 122.9324 | 122.8317 | 82.1823 | -123.1522
3615.0156 | 123.143 | -49.498 | 73.3749 | 0.19058 | 0.014499 | 0.071882 | 0.072653 | 0.12928 | -0.0034949 | -0.0047275 | 0.23636 | -0.0084852 | 0.0664 | 0.058253 | 0.0080536 | -0.011974 | 73.2513 | 73.3932 | 5.2231 | -49.5438 | 73.4894 | -49.5804 | -49.6674 | -46.1517 | 32.8125 | -49.5346 | 73.4482 | 73.3932 | -49.7314 | -49.7406 | -0.082397 | -0.16937 | 0.11444 | 122.8912 | -0.045776 | 0.1236 | -0.1236 | -0.23346 | -0.24262 | 0.073242 | 3.3463 | -0.036621 | 0.20599 | 0.018311 | 122.9874 | 122.7493 | 54.7211 | -123.0423 | 122.9462 | 122.8912 | 82.3105 | -123.1155
3616.0156 | 123.0972 | -48.3307 | 74.5651 | 0.18295 | 0.016208 | 0.069532 | 0.07479 | 0.12907 | 0.0022729 | -0.0053683 | 0.22873 | -0.0082716 | 0.066187 | 0.056544 | 0.0097626 | -0.013896 | 74.3591 | 74.4553 | 5.1224 | -48.4314 | 74.7528 | -48.436 | -48.5229 | -45.0073 | 33.8287 | -48.3536 | 74.6979 | 74.6384 | -48.5275 | -48.5596 | -0.10529 | -0.19226 | 0.18768 | 122.7859 | -0.10071 | 0.091553 | -0.20599 | -0.19684 | -0.22888 | 0.13275 | 3.3234 | -0.022889 | 0.20599 | 0.073242 | 123.0835 | 122.6898 | 53.4531 | -123.0881 | 123.0286 | 122.9691 | 82.1594 | -123.1247
3617.0156 | 123.1659 | -50.8621 | 72.0108 | 0.19821 | 0.013431 | 0.06825 | 0.069235 | 0.12843 | 0.0031273 | -0.0045139 | 0.14481 | -0.0093396 | 0.064905 | 0.058039 | 0.0099762 | -0.011333 | 71.727 | 72.3038 | 4.8431 | -50.8759 | 72.1573 | -50.9216 | -51.0132 | -47.4564 | 31.7139 | -50.8896 | 72.1115 | 72.052 | -51.0864 | -51.1002 | -0.059509 | -0.15106 | 0.14648 | 123.1659 | -0.013732 | 0.13733 | -0.28381 | -0.2243 | -0.23804 | 0.10071 | 3.4058 | -0.027465 | 0.21057 | 0.041199 | 123.0194 | 122.5891 | 55.7053 | -123.024 | 122.9736 | 122.9141 | 82.576 | -123.111
3618.0156 | 123.0606 | -50.6561 | 72.2946 | 0.24399 | 0.018558 | 0.071027 | 0.073294 | 0.13163 | 0.0027001 | -0.0060093 | 0.17532 | -0.0084852 | 0.068537 | 0.058253 | 0.010831 | -0.01176 | 72.0337 | 72.0795 | 4.6143 | -50.7889 | 72.3679 | -50.7935 | -50.8987 | -47.3373 | 31.7871 | -50.7706 | 72.3633 | 72.2855 | -50.8759 | -50.8987 | -0.13733 | -0.24262 | 0.073242 | 122.7356 | -0.13275 | 0.10986 | -0.26093 | -0.21973 | -0.24262 | 0.068664 | 3.3188 | -0.11444 | 0.12817 | -0.009156 | 123.024 | 122.6898 | 55.2704 | -123.1934 | 123.0194 | 122.9416 | 82.4432 | -123.1934
3619.0156 | 123.1018 | -49.91 | 72.9767 | 0.19058 | 0.017276 | 0.0706 | 0.072226 | 0.13121 | 0.00056395 | -0.0072911 | 0.22873 | -0.0086988 | 0.064478 | 0.057612 | 0.012753 | -0.011974 | 72.8073 | 72.9172 | 4.7745 | -49.9969 | 73.1323 | -50.0015 | -50.1114 | -46.582 | 32.4234 | -49.9969 | 73.0453 | 72.9904 | -50.148 | -50.1846 | -0.091553 | -0.20142 | 0.15564 | 122.8271 | -0.086975 | 0.11444 | -0.16937 | -0.23804 | -0.27466 | 0.068664 | 3.3279 | -0.086975 | 0.18768 | 0.013732 | 123.0423 | 122.7173 | 54.6844 | -123.0881 | 122.9553 | 122.9004 | 82.3334 | -123.1613
3620.0156 | 123.0377 | -50.8392 | 72.0978 | 0.10666 | 0.017917 | 0.071455 | 0.07244 | 0.12928 | 0.0037683 | -0.0070773 | -0.74783 | -0.0093396 | 0.067896 | 0.058253 | 0.010403 | -0.011974 | 72.084 | 71.6171 | 4.5959 | -50.7156 | 72.2946 | -50.8621 | -50.9628 | -47.5204 | 31.6727 | -50.9903 | 72.2076 | 72.139 | -51.059 | -51.1185 | -0.022889 | -0.1236 | 0.19684 | 122.4564 | 0.1236 | 0.24719 | -0.013733 | -0.21973 | -0.27924 | 0.10986 | 3.3188 | -0.15106 | 0.12817 | 0.041199 | 123.1338 | 122.9233 | 55.4352 | -123.0606 | 123.0469 | 122.9782 | 82.5119 | -123.2162
3621.0156 | 123.1247 | -48.6145 | 74.2676 | 0.16006 | 0.017276 | 0.071027 | 0.071158 | 0.12971 | -0.0015723 | -0.0081455 | 0.25162 | -0.009126 | 0.068323 | 0.056971 | 0.010617 | -0.013683 | 74.1257 | 74.2584 | 5.2094 | -48.6832 | 74.4278 | -48.674 | -48.8022 | -45.2683 | 33.7372 | -48.6649 | 74.3683 | 74.3042 | -48.8617 | -48.8297 | -0.059509 | -0.18768 | 0.16022 | 122.8729 | -0.068665 | 0.11902 | -0.14191 | -0.24719 | -0.21515 | 0.10071 | 3.3463 | -0.050354 | 0.16479 | 0.036621 | 123.0423 | 122.7402 | 53.8239 | -123.0698 | 122.9828 | 122.9187 | 82.3517 | -123.0972
3622.0156 | 123.0515 | -48.4909 | 74.4598 | 0.52628 | 0.017062 | 0.0706 | 0.073081 | 0.12629 | -0.00029045 | -0.0075047 | 0.14481 | -0.0097668 | 0.067041 | 0.056758 | 0.010831 | -0.013255 | 74.2767 | 74.3179 | 4.9484 | -48.5367 | 74.6109 | -48.5367 | -48.6145 | -45.1584 | 33.8516 | -48.5962 | 74.5468 | 74.5056 | -48.6786 | -48.7427 | -0.045776 | -0.1236 | 0.15106 | 122.8088 | -0.045776 | 0.07782 | -0.18311 | -0.18768 | -0.25177 | 0.086975 | 3.3325 | -0.10528 | 0.14649 | 0.045776 | 123.1018 | 122.7676 | 53.4393 | -123.0743 | 123.0377 | 122.9965 | 82.3425 | -123.2025
3623.0156 | 123.1567 | -47.4792 | 75.3891 | 0.20584 | 0.018558 | 0.069746 | 0.072012 | 0.13014 | -0.00050425 | -0.0064365 | 0.24399 | -0.0095532 | 0.067468 | 0.057398 | 0.012112 | -0.012828 | 75.2472 | 75.3433 | 5.1498 | -47.5662 | 75.4852 | -47.5983 | -47.6807 | -44.1238 | 34.8267 | -47.4884 | 75.4761 | 75.412 | -47.7127 | -47.7493 | -0.11902 | -0.20142 | 0.09613 | 122.8226 | -0.086975 | 0.11444 | -0.14191 | -0.23346 | -0.27008 | 0.086975 | 3.3554 | -0.009155 | 0.26093 | 0.022888 | 122.9645 | 122.7264 | 52.6291 | -123.0698 | 122.9553 | 122.8912 | 82.3059 | -123.1384
3624.0156 | 123.0469 | -50.1755 | 72.7844 | 0.015106 | 0.019626 | 0.071241 | 0.072867 | 0.1295 | 0.0029137 | -0.0066501 | 0.045624 | -0.007417 | 0.067682 | 0.058253 | 0.01254 | -0.013469 | 72.5876 | 72.6746 | 4.7333 | -50.2121 | 72.9309 | -50.267 | -50.3448 | -46.843 | 32.4646 | -50.3723 | 72.8806 | 72.8027 | -50.3906 | -50.4456 | -0.091553 | -0.16937 | 0.14648 | 122.85 | -0.036621 | 0.13275 | -0.19684 | -0.21515 | -0.27008 | 0.09613 | 3.3325 | -0.19684 | 0.073243 | 0.01831 | 123.1064 | 122.7631 | 54.9088 | -123.1293 | 123.056 | 122.9782 | 82.6401 | -123.23
3625.0156 | 123.0286 | -49.6262 | 73.3383 | -0.76309 | 0.01813 | 0.069959 | 0.07244 | 0.12822 | 0.0020593 | -0.0075047 | 0.16006 | -0.0089124 | 0.065119 | 0.057398 | 0.0099762 | -0.011119 | 73.0545 | 73.1644 | 4.8431 | -49.6902 | 73.4528 | -49.7223 | -49.8276 | -46.2067 | 32.9727 | -49.7314 | 73.494 | 73.4161 | -49.823 | -49.8367 | -0.09613 | -0.20142 | 0.11444 | 122.7905 | -0.064087 | 0.13733 | -0.28381 | -0.19684 | -0.21057 | 0.15564 | 3.4195 | -0.10529 | 0.10529 | 0.07782 | 123.0789 | 122.6807 | 54.4693 | -123.1659 | 123.1201 | 123.0423 | 82.5989 | -123.175
3626.0156 | 123.0331 | -49.0952 | 73.8785 | -0.015411 | 0.021762 | 0.071668 | 0.071799 | 0.12928 | 0.0027001 | -0.0053683 | 0.053253 | -0.0084852 | 0.069605 | 0.058467 | 0.011685 | -0.011546 | 73.6633 | 73.7732 | 4.8203 | -49.1272 | 73.9883 | -49.1684 | -49.2691 | -45.7214 | 33.4854 | -49.1867 | 73.9838 | 73.9426 | -49.2737 | -49.2828 | -0.073242 | -0.17395 | 0.10986 | 122.8683 | -0.032043 | 0.14191 | -0.21515 | -0.17853 | -0.18768 | 0.10529 | 3.3737 | -0.091553 | 0.09613 | 0.064087 | 123.0835 | 122.7585 | 53.9154 | -123.1476 | 123.0789 | 123.0377 | 82.5806 | -123.1613
3627.0156 | 123.0606 | -48.7747 | 74.1348 | 0.19058 | 0.020053 | 0.068891 | 0.073935 | 0.12822 | 0.0016321 | -0.0087863 | 0.19821 | -0.0086988 | 0.067255 | 0.057185 | 0.012326 | -0.012614 | 73.8007 | 73.9059 | 4.9026 | -49.0448 | 74.1577 | -48.9899 | -49.0997 | -45.5109 | 33.7463 | -48.8297 | 74.1623 | 74.1074 | -49.0631 | -49.054 | -0.21515 | -0.32501 | 0.022888 | 122.6807 | -0.27008 | 0.054931 | -0.33417 | -0.28839 | -0.27924 | 0.027465 | 3.2639 | -0.054932 | 0.2243 | -0.027466 | 122.9324 | 122.5754 | 53.6774 | -123.2346 | 122.937 | 122.8821 | 82.5211 | -123.1888
3628.0156 | 123.0331 | -48.7747 | 74.1531 | -0.0077822 | 0.019626 | 0.071241 | 0.074576 | 0.12864 | 0.00099115 | -0.0081455 | 0.060883 | -0.0099806 | 0.069605 | 0.057612 | 0.011685 | -0.012828 | 74.0891 | 74.1806 | 4.9988 | -48.7289 | 74.4003 | -48.7335 | -48.8571 | -45.433 | 33.9157 | -48.9304 | 74.2584 | 74.2264 | -49.0036 | -49.0219 | 0.041198 | -0.082398 | 0.24719 | 122.9553 | 0.045776 | 0.12817 | -0.064087 | -0.22888 | -0.24719 | 0.10529 | 3.3417 | -0.15564 | 0.091553 | 0.073242 | 123.175 | 122.8638 | 53.7735 | -123.0103 | 123.0331 | 123.0011 | 82.6904 | -123.175
3629.0156 | 123.1018 | -48.5733 | 74.3546 | 0.13718 | 0.017276 | 0.071241 | 0.072653 | 0.13078 | 0.00056395 | -0.0072911 | 0.21347 | -0.0082716 | 0.066614 | 0.054835 | 0.011472 | -0.011333 | 74.1257 | 74.2493 | 4.9118 | -48.6649 | 74.501 | -48.6328 | -48.7473 | -45.2087 | 34.0668 | -48.5779 | 74.4644 | 74.3958 | -48.7976 | -48.8022 | -0.059509 | -0.17395 | 0.14648 | 122.8226 | -0.091553 | 0.082397 | -0.22888 | -0.2243 | -0.22888 | 0.10986 | 3.3646 | -0.004578 | 0.2243 | 0.041199 | 123.0743 | 122.699 | 53.4851 | -123.1018 | 123.0377 | 122.9691 | 82.6401 | -123.1567
3630.0156 | 123.0789 | -48.1888 | 74.7665 | 0.037994 | 0.020694 | 0.071241 | 0.073508 | 0.13121 | 0.0029137 | -0.0062229 | -0.015411 | -0.0076306 | 0.069177 | 0.05868 | 0.01254 | -0.012614 | 74.6017 | 74.7253 | 5.0995 | -48.2162 | 74.8947 | -48.2208 | -48.3444 | -44.7693 | 34.4604 | -48.23 | 74.8718 | 74.8123 | -48.3902 | -48.4039 | -0.032043 | -0.15564 | 0.12817 | 122.9141 | -0.027466 | 0.12817 | -0.16479 | -0.20142 | -0.21515 | 0.10528 | 3.4195 | -0.041198 | 0.17395 | 0.045776 | 123.0835 | 122.7905 | 53.2883 | -123.111 | 123.0606 | 123.0011 | 82.6492 | -123.1705
3631.0156 | 123.0423 | -50.0656 | 72.9218 | 0.11429 | 0.025393 | 0.067396 | 0.075858 | 0.13163 | 0.00013675 | -0.0038731 | 0.12955 | -0.0095532 | 0.067682 | 0.057612 | 0.01019 | -0.013042 | 72.464 | 72.9126 | 4.7379 | -50.1526 | 73.0316 | -50.1068 | -50.2213 | -46.7056 | 32.753 | -50.1572 | 72.995 | 72.9263 | -50.2716 | -50.3082 | -0.041199 | -0.15564 | 0.10986 | 122.9782 | -0.086975 | 0.068664 | -0.45776 | -0.20599 | -0.24262 | 0.073242 | 3.36 | -0.091553 | 0.15106 | 0.004578 | 123.0972 | 122.5296 | 54.8035 | -123.143 | 123.0606 | 122.9919 | 82.8186 | -123.23
3632.0156 | 123.056 | -49.8138 | 73.1415 | -0.091705 | 0.020267 | 0.071027 | 0.073508 | 0.13035 | 0.0020593 | -0.0060093 | -0.0077819 | -0.0065626 | 0.067255 | 0.056758 | 0.010831 | -0.011974 | 72.9172 | 73.0179 | 4.9072 | -49.8917 | 73.2193 | -49.9191 | -50.0427 | -46.4081 | 33.0505 | -49.8688 | 73.2239 | 73.1827 | -50.0198 | -50.0656 | -0.10529 | -0.22888 | 0.07782 | 122.8317 | -0.07782 | 0.15106 | -0.2243 | -0.20599 | -0.25177 | 0.082398 | 3.4058 | -0.054931 | 0.19684 | 0.041199 | 123.0331 | 122.731 | 54.7211 | -123.1842 | 123.0377 | 122.9965 | 82.8644 | -123.2071
3633.0156 | 123.0057 | -48.9532 | 74.0158 | 0.053253 | 0.018985 | 0.069746 | 0.072653 | 0.1295 | 0.0027001 | -0.0064365 | 0.18295 | -0.0067762 | 0.068109 | 0.059535 | 0.01254 | -0.012828 | 73.7686 | 73.8419 | 5.0903 | -49.0311 | 74.1577 | -49.0219 | -49.1272 | -45.6161 | 33.7784 | -49.0631 | 74.1119 | 74.0753 | -49.1776 | -49.1959 | -0.068665 | -0.17395 | 0.14191 | 122.7951 | -0.07782 | 0.09613 | -0.24719 | -0.2243 | -0.24262 | 0.09613 | 3.3371 | -0.10986 | 0.13275 | 0.059509 | 123.111 | 122.7219 | 54.0436 | -123.143 | 123.0652 | 123.0286 | 82.7316 | -123.2117
3634.0156 | 123.0652 | -48.6832 | 74.2401 | 0.022736 | 0.018344 | 0.069746 | 0.07479 | 0.1295 | 0.00099115 | -0.0083591 | -0.068817 | -0.008058 | 0.0664 | 0.057612 | 0.0091216 | -0.012187 | 74.2035 | 74.3225 | 5.3101 | -48.6008 | 74.5148 | -48.642 | -48.7793 | -45.2683 | 34.3231 | -48.7793 | 74.3774 | 74.3362 | -48.848 | -48.9212 | 0.041199 | -0.09613 | 0.27466 | 123.0057 | 0.082398 | 0.17853 | -0.036621 | -0.16479 | -0.23804 | 0.13733 | 3.4149 | -0.09613 | 0.14191 | 0.096131 | 123.1979 | 122.8867 | 53.9932 | -123.0194 | 123.0606 | 123.0194 | 83.0063 | -123.1613
3635.0156 | 122.9095 | -47.8958 | 75.0687 | 0.076141 | 0.020907 | 0.069532 | 0.074576 | 0.13099 | 0.0016321 | -0.0066501 | 0.18295 | -0.0084852 | 0.065546 | 0.056117 | 0.009549 | -0.011333 | 74.8352 | 74.9451 | 5.3558 | -47.9233 | 75.2609 | -47.9279 | -48.0194 | -44.4992 | 34.845 | -47.9416 | 75.1923 | 75.119 | -48.0698 | -48.1201 | -0.032043 | -0.1236 | 0.19226 | 122.8409 | -0.027466 | 0.09613 | -0.23346 | -0.17395 | -0.2243 | 0.1236 | 3.3966 | -0.045776 | 0.17853 | 0.050354 | 123.1567 | 122.731 | 53.2516 | -123.0881 | 123.0881 | 123.0148 | 82.7408 | -123.1888
3636.0156 | 123.0927 | -50.766 | 72.1893 | -0.10696 | 0.019198 | 0.067182 | 0.07479 | 0.13035 | 0.0029137 | -0.0081455 | -0.053558 | -0.011903 | 0.069391 | 0.058467 | 0.01019 | -0.013896 | 71.9604 | 72.1207 | 4.8248 | -50.7935 | 72.2855 | -50.8438 | -50.9491 | -47.3373 | 32.5287 | -50.8347 | 72.29 | 72.2076 | -50.9903 | -50.9811 | -0.07782 | -0.18311 | 0.09613 | 122.8867 | -0.027466 | 0.15564 | -0.22888 | -0.2243 | -0.21515 | 0.10071 | 3.4286 | -0.068665 | 0.14648 | 0.018311 | 123.0515 | 122.7264 | 55.5908 | -123.1384 | 123.056 | 122.9736 | 83.2947 | -123.1705
3637.0312 | 123.2025 | -50.2258 | 72.67 | -0.099335 | 0.011508 | 0.07295 | 0.073294 | 0.12822 | -0.0075537 | -0.010068 | 0.053253 | -0.011476 | 0.064264 | 0.055689 | 0.0076264 | -0.0098374 | 72.4686 | 72.7386 | 5.04 | -50.2487 | 72.757 | -50.3082 | -50.4089 | -46.7377 | 33.0414 | -50.1984 | 72.7066 | 72.67 | -50.4227 | -50.4547 | -0.082398 | -0.18311 | 0.086975 | 122.9645 | -0.022888 | 0.16022 | -0.20142 | -0.19684 | -0.22888 | 0.036621 | 3.4882 | 0.027466 | 0.25635 | 0 | 122.9828 | 122.6944 | 55.2658 | -123.0789 | 122.9324 | 122.8958 | 83.2672 | -123.1247
3638.0156 | 123.0652 | -49.292 | 73.6862 | -0.19852 | 0.014499 | 0.071668 | 0.073508 | 0.12928 | 0.00099115 | -0.0087863 | -0.12222 | -0.0082716 | 0.068109 | 0.055049 | 0.011685 | -0.011974 | 73.4756 | 73.6221 | 5.0903 | -49.2737 | 73.8419 | -49.2966 | -49.3927 | -45.8817 | 33.783 | -49.4064 | 73.7732 | 73.6908 | -49.498 | -49.5529 | -0.004578 | -0.10071 | 0.15564 | 122.9141 | 0.01831 | 0.11902 | -0.21057 | -0.20599 | -0.26093 | 0.086975 | 3.4103 | -0.11444 | 0.14648 | 0.004578 | 123.1338 | 122.7676 | 54.3823 | -123.0789 | 123.0652 | 122.9828 | 83.075 | -123.2391
3639.0156 | 123.0423 | -49.1043 | 73.8785 | 0.015106 | 0.017703 | 0.072523 | 0.073508 | 0.13078 | 0.0035547 | -0.0068637 | -0.00015237 | -0.010408 | 0.065973 | 0.060176 | 0.011899 | -0.014537 | 73.7183 | 73.8419 | 5.1682 | -49.1043 | 74.0021 | -49.1318 | -49.2462 | -45.6207 | 34.0347 | -49.1776 | 73.9517 | 73.8693 | -49.2966 | -49.3195 | -0.027466 | -0.14191 | 0.1236 | 122.9462 | 0 | 0.14191 | -0.16022 | -0.19226 | -0.21515 | 0.073242 | 3.4836 | -0.073242 | 0.14191 | -0.009155 | 123.1064 | 122.8226 | 54.2725 | -123.1247 | 123.056 | 122.9736 | 83.139 | -123.1979
3640.0156 | 123.0972 | -48.2803 | 74.6704 | -0.21378 | 0.018558 | 0.069532 | 0.073508 | 0.12736 | 0.0012047 | -0.0060093 | -0.10696 | -0.011476 | 0.068109 | 0.057185 | 0.0091216 | -0.012828 | 74.3088 | 74.469 | 5.1956 | -48.4177 | 74.6567 | -48.4726 | -48.5641 | -44.838 | 34.845 | -48.2895 | 74.7437 | 74.6841 | -48.4817 | -48.5229 | -0.19226 | -0.28381 | -0.013733 | 122.7493 | -0.13733 | 0.14648 | -0.36163 | -0.20142 | -0.24261 | 0.073242 | 3.4424 | -0.009156 | 0.23346 | 0.013733 | 122.937 | 122.5891 | 53.476 | -123.2346 | 123.024 | 122.9645 | 83.1253 | -123.1934
3641.0156 | 123.1064 | -49.8962 | 73.0453 | -0.068817 | 0.020267 | 0.071241 | 0.07244 | 0.12907 | 0.0024865 | -0.0079319 | 0.0074766 | -0.0089124 | 0.067041 | 0.058467 | 0.011044 | -0.013896 | 72.8027 | 72.9584 | 4.9713 | -49.9466 | 73.1323 | -50.0107 | -50.116 | -46.4035 | 33.4213 | -50.0336 | 73.1369 | 73.0408 | -50.1251 | -50.1434 | -0.11444 | -0.21973 | 0.086975 | 122.8546 | -0.050354 | 0.16937 | -0.24262 | -0.22888 | -0.24719 | 0.091553 | 3.4927 | -0.13733 | 0.10986 | -0.004578 | 123.0286 | 122.699 | 54.8676 | -123.1613 | 123.0331 | 122.937 | 83.3176 | -123.1888
3642.0156 | 123.1018 | -49.7635 | 73.1735 | 0.17532 | 0.018558 | 0.069959 | 0.071372 | 0.13099 | 0.0012047 | -0.0079319 | 0.22873 | -0.0078442 | 0.065546 | 0.058467 | 0.01019 | -0.013255 | 72.9584 | 73.0911 | 4.985 | -49.8459 | 73.2559 | -49.8779 | -49.9878 | -46.257 | 33.5403 | -49.8367 | 73.2742 | 73.1873 | -49.9786 | -49.9741 | -0.11444 | -0.2243 | 0.082397 | 122.8546 | -0.082397 | 0.14191 | -0.21515 | -0.21515 | -0.21057 | 0.10071 | 3.5065 | -0.073242 | 0.13733 | 0.013733 | 123.0194 | 122.7219 | 54.7485 | -123.1613 | 123.0377 | 122.9507 | 83.3038 | -123.1476
3643.0156 | 123.0057 | -49.736 | 73.2056 | -0.076447 | 0.017917 | 0.068464 | 0.075858 | 0.13163 | 0.0029137 | -0.0066501 | -0.061188 | -0.0086988 | 0.068537 | 0.058467 | 0.011044 | -0.011119 | 72.9767 | 73.114 | 5.2414 | -49.8047 | 73.2925 | -49.8642 | -49.9741 | -46.2982 | 33.5724 | -49.8688 | 73.2376 | 73.2239 | -49.9832 | -50.0244 | -0.12817 | -0.23804 | 0.086976 | 122.85 | -0.068664 | 0.16937 | -0.22888 | -0.24719 | -0.28839 | 0.032044 | 3.4378 | -0.13275 | 0.15564 | 0.018311 | 123.0286 | 122.7127 | 54.9774 | -123.1796 | 122.9736 | 122.9599 | 83.3084 | -123.23
3644.0156 | 123.0881 | -49.0082 | 73.9426 | -0.22903 | 0.013644 | 0.071455 | 0.072226 | 0.12736 | -0.0030677 | -0.0085727 | -0.099335 | -0.010621 | 0.066614 | 0.057185 | 0.0076264 | -0.0096238 | 73.7183 | 73.9197 | 5.4703 | -49.0219 | 74.0204 | -49.0768 | -49.1638 | -45.5063 | 34.3506 | -49.0723 | 74.0479 | 73.9792 | -49.205 | -49.2416 | -0.068664 | -0.15564 | 0.07782 | 122.9279 | -0.013733 | 0.14191 | -0.2243 | -0.19684 | -0.23346 | 0.10529 | 3.5019 | -0.064087 | 0.16937 | 0.036621 | 123.0286 | 122.7264 | 54.4785 | -123.1064 | 123.056 | 122.9874 | 83.3588 | -123.1842
3645.0156 | 123.0148 | -50.0107 | 72.963 | 0.015106 | 0.013858 | 0.070173 | 0.073508 | 0.12843 | -0.00029045 | -0.0079319 | -0.11459 | -0.010835 | 0.070032 | 0.057612 | 0.008908 | -0.011546 | 72.6608 | 72.8577 | 5.2826 | -49.9969 | 73.1232 | -50.0519 | -50.1251 | -46.5363 | 33.49 | -50.148 | 73.0225 | 72.9401 | -50.2716 | -50.2808 | -0.041199 | -0.11444 | 0.16022 | 122.8683 | 0.013733 | 0.12817 | -0.30212 | -0.26093 | -0.27008 | 0.059509 | 3.4744 | -0.13733 | 0.13275 | -0.022889 | 123.1338 | 122.6715 | 55.2933 | -123.0881 | 123.0331 | 122.9507 | 83.5007 | -123.2437
3646.0156 | 123.0606 | -50.2075 | 72.7615 | -0.23666 | 0.010867 | 0.071882 | 0.071585 | 0.12971 | -0.0045631 | -0.0089999 | -0.14511 | -0.0099806 | 0.065332 | 0.05868 | 0.0099762 | -0.012187 | 72.5372 | 72.757 | 5.1453 | -50.1755 | 72.8897 | -50.235 | -50.3311 | -46.6965 | 33.403 | -50.2396 | 72.8256 | 72.7478 | -50.4135 | -50.4456 | -0.027465 | -0.1236 | 0.12817 | 122.9645 | 0.032044 | 0.15564 | -0.22431 | -0.20599 | -0.23804 | 0.064087 | 3.511 | -0.032043 | 0.20599 | -0.013733 | 123.0972 | 122.7448 | 55.3528 | -123.0927 | 123.0331 | 122.9553 | 83.6105 | -123.2071
3647.0156 | 123.0789 | -48.6969 | 74.2264 | 0.099029 | 0.020694 | 0.070173 | 0.074149 | 0.12993 | 0.0014185 | -0.0083591 | 0.25925 | -0.0093396 | 0.06875 | 0.056758 | 0.0099762 | -0.012828 | 73.9334 | 74.0936 | 5.246 | -48.8113 | 74.3408 | -48.8113 | -48.9212 | -45.1767 | 34.5795 | -48.7381 | 74.3179 | 74.263 | -48.912 | -48.9395 | -0.11444 | -0.22431 | 0.11444 | 122.7905 | -0.11444 | 0.10986 | -0.29297 | -0.21515 | -0.24262 | 0.091553 | 3.5202 | -0.041199 | 0.20142 | 0.036621 | 123.0377 | 122.6303 | 53.9429 | -123.1476 | 123.0148 | 122.9599 | 83.2764 | -123.1659
3648.0156 | 123.1064 | -48.1979 | 74.6796 | -0.14511 | 0.011935 | 0.071241 | 0.071158 | 0.12886 | -0.0028541 | -0.0064365 | -0.084076 | -0.011049 | 0.065546 | 0.057185 | 0.0076264 | -0.011546 | 74.3637 | 74.6109 | 5.6442 | -48.2391 | 74.7116 | -48.3261 | -48.4268 | -44.6228 | 35.17 | -48.0698 | 74.8581 | 74.7849 | -48.3444 | -48.4177 | -0.12817 | -0.22888 | 0.032044 | 122.8088 | -0.041199 | 0.18768 | -0.31586 | -0.14648 | -0.21973 | 0.17853 | 3.5751 | 0.12817 | 0.3479 | 0.10529 | 122.9095 | 122.5616 | 53.8422 | -123.1064 | 123.056 | 122.9828 | 83.3679 | -123.0972
3649.0156 | 123.056 | -48.8983 | 74.0707 | -0.015411 | 0.017276 | 0.072523 | 0.074362 | 0.12822 | 0.0016321 | -0.0057957 | -0.19089 | -0.010408 | 0.064905 | 0.05633 | 0.010403 | -0.01411 | 73.8419 | 73.9792 | 5.2002 | -48.9212 | 74.2355 | -48.9624 | -49.0494 | -45.401 | 34.4513 | -48.9441 | 74.1943 | 74.0936 | -49.0952 | -49.1089 | -0.064087 | -0.15106 | 0.16479 | 122.8775 | -0.022889 | 0.12817 | -0.22888 | -0.19684 | -0.21057 | 0.1236 | 3.4973 | -0.045777 | 0.1648 | 0.022888 | 123.1338 | 122.7402 | 54.0985 | -123.1201 | 123.0927 | 122.9919 | 83.3496 | -123.1796
3650.0156 | 123.1247 | -47.8592 | 75.0641 | -0.19089 | 0.010013 | 0.071027 | 0.072226 | 0.13014 | -0.0034949 | -0.0087863 | -0.10696 | -0.0099806 | 0.066187 | 0.055262 | 0.008908 | -0.012828 | 74.9359 | 75.1556 | 5.4108 | -47.818 | 75.2106 | -47.8729 | -47.9919 | -44.3207 | 35.5087 | -47.8867 | 75.1511 | 75.0778 | -48.0331 | -48.0972 | -0.013733 | -0.13275 | 0.14648 | 123.0148 | 0.041199 | 0.17395 | -0.12817 | -0.17395 | -0.23804 | 0.086975 | 3.5385 | -0.027466 | 0.21057 | 0.013733 | 123.0698 | 122.7951 | 53.27 | -123.056 | 123.0103 | 122.937 | 83.3679 | -123.1613
3651.0156 | 123.0423 | -47.4518 | 75.4898 | -0.25192 | 0.013003 | 0.071882 | 0.071585 | 0.12864 | -0.00093145 | -0.0079319 | -0.15274 | -0.011262 | 0.066187 | 0.055262 | 0.009549 | -0.013042 | 75.2563 | 75.4761 | 5.5161 | -47.4106 | 75.5814 | -47.5388 | -47.6578 | -43.9865 | 35.8566 | -47.4884 | 75.563 | 75.4761 | -47.6715 | -47.7127 | -0.086975 | -0.20599 | 0.091553 | 122.9279 | 0.041199 | 0.24719 | -0.23346 | -0.21973 | -0.26093 | 0.073242 | 3.4653 | -0.036621 | 0.22431 | -0.013733 | 123.0331 | 122.7081 | 52.9678 | -123.1476 | 123.0148 | 122.9279 | 83.3084 | -123.2025
3652.0156 | 123.143 | -49.8734 | 73.1049 | -0.168 | 0.016849 | 0.0706 | 0.076926 | 0.13099 | 0.0046227 | -0.0034457 | -0.14511 | -0.0078442 | 0.067255 | 0.056971 | 0.0099762 | -0.01411 | 72.8622 | 73.0225 | 5.0125 | -49.9237 | 73.1827 | -49.9741 | -50.061 | -46.3394 | 33.7875 | -49.942 | 73.1415 | 73.0545 | -50.0931 | -50.1297 | -0.10071 | -0.18768 | 0.07782 | 122.8958 | -0.050354 | 0.13733 | -0.24261 | -0.21973 | -0.25635 | 0.036621 | 3.5339 | -0.068665 | 0.18768 | -0.050354 | 123.056 | 122.7356 | 54.8859 | -123.1659 | 123.0148 | 122.9279 | 83.6609 | -123.2346
3653.0156 | 123.0377 | -50.3677 | 72.6059 | -0.24429 | 0.0097989 | 0.071882 | 0.070944 | 0.12822 | -0.0037085 | -0.0079319 | -0.18326 | -0.0093396 | 0.064478 | 0.057612 | 0.0086944 | -0.012614 | 72.4136 | 72.67 | 4.9942 | -50.2945 | 72.7386 | -50.3586 | -50.4639 | -46.8109 | 33.4259 | -50.4135 | 72.6837 | 72.6105 | -50.5829 | -50.6149 | 0.009155 | -0.09613 | 0.13275 | 123.0377 | 0.073242 | 0.16937 | -0.19226 | -0.21515 | -0.24719 | 0.07782 | 3.5568 | -0.045776 | 0.20142 | 0.004578 | 123.1064 | 122.7814 | 55.3619 | -123.0698 | 123.0515 | 122.9782 | 83.7936 | -123.2208
3654.0156 | 123.1384 | -49.4934 | 73.3795 | -0.12222 | 0.010013 | 0.074232 | 0.070944 | 0.12971 | -0.0047767 | -0.0077183 | -0.084076 | -0.011476 | 0.064478 | 0.055903 | 0.0076264 | -0.011974 | 73.1964 | 73.4619 | 5.2094 | -49.53 | 73.4665 | -49.5941 | -49.6902 | -45.9503 | 34.2453 | -49.5255 | 73.4253 | 73.3566 | -49.736 | -49.7772 | -0.10071 | -0.19684 | 0.086975 | 122.9553 | -0.036621 | 0.16022 | -0.18311 | -0.24262 | -0.28381 | 0.045776 | 3.5431 | -0.032044 | 0.25177 | -0.022889 | 122.9599 | 122.6898 | 54.7028 | -123.0698 | 122.9187 | 122.85 | 83.7387 | -123.1567
3655.0156 | 123.1613 | -49.1318 | 73.764 | -0.34348 | 0.011508 | 0.068678 | 0.069235 | 0.12779 | -0.0017859 | -0.010068 | -0.12222 | -0.012758 | 0.065546 | 0.056544 | 0.0082672 | -0.013255 | 73.5443 | 73.8052 | 5.1041 | -49.1867 | 73.8327 | -49.2645 | -49.3515 | -45.5704 | 34.6298 | -49.0585 | 73.8235 | 73.7503 | -49.3607 | -49.3973 | -0.13275 | -0.21973 | 0.068665 | 122.937 | -0.054932 | 0.16479 | -0.21973 | -0.22888 | -0.2655 | 0.059509 | 3.5614 | 0.073242 | 0.33875 | -0.013733 | 122.9645 | 122.6761 | 54.2358 | -123.1155 | 122.9553 | 122.8821 | 83.7616 | -123.1613
3656.0156 | 123.1705 | -49.0265 | 73.8281 | -0.084076 | 0.010226 | 0.072736 | 0.070517 | 0.12843 | -0.0015723 | -0.0083591 | -0.0077819 | -0.010835 | 0.065332 | 0.055903 | 0.010617 | -0.013042 | 73.7823 | 74.0204 | 5.3101 | -48.9532 | 74.0662 | -49.0219 | -49.1226 | -45.4239 | 34.7534 | -49.0631 | 73.9563 | 73.8281 | -49.2462 | -49.2737 | 0.004577 | -0.096131 | 0.23804 | 123.0469 | 0.073242 | 0.16937 | -0.045776 | -0.21973 | -0.24719 | 0.12817 | 3.6026 | -0.036621 | 0.21057 | 0 | 123.0927 | 122.8088 | 54.3365 | -122.9507 | 122.9828 | 122.8546 | 83.7799 | -123.1018
3657.0156 | 123.0743 | -49.118 | 73.8098 | -0.076447 | 0.018558 | 0.071668 | 0.073721 | 0.13057 | 0.0035547 | -0.0087863 | -0.061188 | -0.009126 | 0.0711 | 0.058467 | 0.013181 | -0.015178 | 73.7412 | 73.7869 | 5.1453 | -49.1455 | 73.9975 | -49.1959 | -49.292 | -45.575 | 34.6069 | -49.1776 | 73.9197 | 73.8144 | -49.3423 | -49.3652 | -0.07782 | -0.17395 | 0.18768 | 122.905 | -0.027466 | 0.14648 | -0.068664 | -0.2243 | -0.24719 | 0.10986 | 3.5431 | -0.059509 | 0.18768 | 0.004578 | 123.1155 | 122.8592 | 54.2633 | -123.1018 | 123.0377 | 122.9324 | 83.725 | -123.175
3658.0156 | 123.1247 | -48.2895 | 74.5926 | 0.083771 | 0.0091581 | 0.074232 | 0.073935 | 0.12736 | -0.0049903 | -0.0060093 | 0.57205 | -0.011689 | 0.063837 | 0.057612 | 0.010617 | -0.011333 | 74.2905 | 74.5468 | 4.985 | -48.4497 | 74.6613 | -48.5092 | -48.5733 | -44.783 | 35.3668 | -48.3627 | 74.6567 | 74.5789 | -48.5321 | -48.5504 | -0.21973 | -0.28381 | 0.068665 | 122.8363 | -0.16022 | 0.1236 | -0.30212 | -0.24261 | -0.26093 | 0.064087 | 3.5065 | -0.073242 | 0.18768 | -0.013733 | 122.9507 | 122.58 | 53.2745 | -123.1659 | 122.9462 | 122.8683 | 83.6563 | -123.143
3659.0156 | 123.1293 | -47.7676 | 75.1328 | -0.20615 | 0.010013 | 0.072309 | 0.074149 | 0.128 | -0.0034949 | -0.0075047 | -0.023041 | -0.010835 | 0.064905 | 0.055689 | 0.0074126 | -0.011546 | 74.9954 | 75.2106 | 5.3879 | -47.7631 | 75.2609 | -47.8592 | -47.9599 | -44.3573 | 35.8017 | -47.7676 | 75.206 | 75.087 | -47.9874 | -48.0194 | -0.091553 | -0.19226 | 0.12817 | 122.9782 | 0.004577 | 0.19684 | -0.13733 | -0.21973 | -0.25177 | 0.073243 | 3.4103 | 0 | 0.25177 | -0.045776 | 123.0286 | 122.7631 | 53.1555 | -123.0927 | 122.9736 | 122.8546 | 83.5693 | -123.1522
3660.0156 | 123.0972 | -47.5983 | 75.2838 | -0.015411 | 0.0087307 | 0.073164 | 0.071585 | 0.12715 | -0.0022131 | -0.011777 | 0.28214 | -0.011476 | 0.063837 | 0.055903 | 0.0097626 | -0.013896 | 75.0046 | 75.1007 | 5.2643 | -47.7859 | 75.238 | -47.8317 | -47.9462 | -44.0506 | 36.0123 | -47.5983 | 75.3845 | 75.2747 | -47.85 | -47.8638 | -0.23346 | -0.3479 | -0.045776 | 122.699 | -0.18768 | 0.16022 | -0.27923 | -0.25177 | -0.2655 | 0.10071 | 3.5477 | 0 | 0.2655 | -0.009155 | 122.8363 | 122.6028 | 52.8625 | -123.23 | 122.9828 | 122.8729 | 83.6105 | -123.1476
3661.0156 | 123.1705 | -50.0885 | 72.7936 | -0.084076 | 0.0097989 | 0.070814 | 0.072012 | 0.12864 | -0.0030677 | -0.0096409 | -0.03067 | -0.012544 | 0.062982 | 0.055262 | 0.0080536 | -0.011119 | 72.6105 | 72.8348 | 5.0766 | -50.1389 | 72.876 | -50.2075 | -50.2808 | -46.4767 | 33.8791 | -50.1022 | 72.8439 | 72.7478 | -50.322 | -50.3265 | -0.11902 | -0.19226 | 0.082398 | 122.9233 | -0.050354 | 0.14191 | -0.1831 | -0.23346 | -0.23804 | 0.050354 | 3.6118 | -0.013733 | 0.2243 | -0.045776 | 122.9645 | 122.699 | 55.1651 | -123.0743 | 122.9324 | 122.8363 | 83.9676 | -123.1201
3662.0156 | 123.1201 | -49.9969 | 72.8622 | 0.13718 | 0.012149 | 0.071882 | 0.071799 | 0.1295 | -0.0022131 | -0.0070773 | 0.16006 | -0.011049 | 0.062555 | 0.056758 | 0.0086944 | -0.01176 | 72.702 | 72.9126 | 5.1956 | -50.0336 | 73.0316 | -50.0381 | -50.1526 | -46.2936 | 34.1263 | -49.9649 | 73.0408 | 72.963 | -50.1755 | -50.2167 | -0.041199 | -0.15564 | 0.16937 | 122.9095 | -0.036621 | 0.11902 | -0.16022 | -0.17853 | -0.21973 | 0.17853 | 3.7033 | 0.032043 | 0.25177 | 0.10071 | 123.0286 | 122.699 | 55.1926 | -123.0148 | 123.0377 | 122.9599 | 84.1232 | -123.0789
3663.0156 | 123.1888 | -49.942 | 72.9126 | -0.11459 | 0.0087307 | 0.073377 | 0.071585 | 0.13099 | -0.0017859 | -0.0075047 | -0.03067 | -0.012758 | 0.064905 | 0.056544 | 0.0086944 | -0.011546 | 72.8394 | 73.0637 | 5.2963 | -49.9191 | 73.1094 | -49.9969 | -50.0748 | -46.2753 | 34.1766 | -49.9649 | 72.995 | 72.9034 | -50.1709 | -50.2121 | -0.054931 | -0.13275 | 0.19684 | 123.0057 | 0.022889 | 0.15564 | -0.073243 | -0.22888 | -0.27008 | 0.082397 | 3.6667 | -0.022888 | 0.24719 | -0.009156 | 123.0515 | 122.7814 | 55.2383 | -122.9874 | 122.937 | 122.8455 | 84.1187 | -123.1247
3664.0156 | 123.1293 | -49.3744 | 73.5123 | 0.16006 | 0.010867 | 0.07295 | 0.069663 | 0.128 | 0.00035035 | -0.0092137 | 0.16769 | -0.013398 | 0.066828 | 0.058253 | 0.010831 | -0.015392 | 73.3658 | 73.5352 | 5.3879 | -49.4202 | 73.6633 | -49.4476 | -49.53 | -45.726 | 34.7122 | -49.3744 | 73.613 | 73.4985 | -49.5712 | -49.6216 | -0.073242 | -0.15564 | 0.15106 | 122.9095 | -0.045776 | 0.10986 | -0.14648 | -0.19684 | -0.24719 | 0.10071 | 3.6484 | 0 | 0.24719 | -0.013733 | 123.0377 | 122.7402 | 54.7623 | -123.0423 | 122.9874 | 122.8729 | 84.0866 | -123.1338
3665.0156 | 123.1338 | -48.9716 | 73.9151 | 0.037994 | 0.0091581 | 0.072523 | 0.07244 | 0.12822 | 0.00077755 | -0.0083591 | -1.5642 | -0.011903 | 0.065973 | 0.053126 | 0.0097626 | -0.014323 | 73.7503 | 73.9334 | 5.3513 | -49.0173 | 74.057 | -49.0494 | -49.1364 | -45.3506 | 35.1105 | -48.9441 | 74.0387 | 73.9197 | -49.173 | -49.2004 | -0.077819 | -0.16479 | 0.14191 | 122.905 | -0.045776 | 0.11902 | -0.16479 | -0.20142 | -0.22888 | 0.1236 | 3.6209 | 0.027466 | 0.25635 | 0.004578 | 123.0286 | 122.7219 | 54.3228 | -123.0515 | 123.0103 | 122.8912 | 84.082 | -123.1155
3666.0156 | 123.1293 | -50.0244 | 72.821 | 0.19058 | 0.01813 | 0.068891 | 0.073935 | 0.13206 | 0.0020593 | -0.0057957 | 0.19821 | -0.0093396 | 0.065759 | 0.05633 | 0.012112 | -0.014537 | 72.702 | 73.0225 | 5.2002 | -50.0473 | 72.995 | -50.0885 | -50.2029 | -46.3303 | 34.1629 | -50.0977 | 72.908 | 72.8119 | -50.2441 | -50.2945 | -0.064087 | -0.17853 | 0.17395 | 123.0469 | -0.022888 | 0.15564 | -0.11902 | -0.21973 | -0.27008 | 0.086975 | 3.6942 | -0.073242 | 0.19684 | -0.009155 | 123.0194 | 122.7264 | 55.2246 | -123.024 | 122.9324 | 122.8363 | 84.1873 | -123.1155
3667.0156 | 123.1155 | -48.5504 | 74.3408 | 0.0074768 | 0.0095853 | 0.071027 | 0.071585 | 0.128 | -0.0017859 | -0.0096409 | 0.18295 | -0.01233 | 0.065973 | 0.057826 | 0.010617 | -0.013896 | 74.1211 | 74.437 | 5.3513 | -48.6832 | 74.4736 | -48.6374 | -48.7061 | -44.8837 | 35.5225 | -48.5596 | 74.4461 | 74.3637 | -48.7335 | -48.7656 | -0.086975 | -0.15564 | 0.13275 | 122.9874 | -0.13275 | 0.022888 | -0.21973 | -0.18311 | -0.21515 | 0.10529 | 3.6667 | -0.009155 | 0.20599 | 0.022888 | 123.024 | 122.6715 | 53.9017 | -123.0469 | 122.9965 | 122.9141 | 84.0729 | -123.1064
3668.0156 | 123.143 | -50.0107 | 72.8531 | -0.015411 | 0.013003 | 0.072736 | 0.069663 | 0.12907 | 0.0024865 | -0.0072911 | 0.22873 | -0.012117 | 0.063196 | 0.058894 | 0.010617 | -0.014964 | 72.7936 | 72.9584 | 5.0171 | -49.9969 | 72.9858 | -50.0702 | -50.1755 | -46.3074 | 34.2911 | -50.0565 | 72.9584 | 72.8348 | -50.2625 | -50.2808 | -0.059509 | -0.1648 | 0.13275 | 122.9691 | 0.013733 | 0.17853 | -0.059509 | -0.25177 | -0.27008 | 0.10529 | 3.7033 | -0.045777 | 0.2243 | -0.01831 | 122.9965 | 122.8043 | 55.0278 | -123.0286 | 122.9691 | 122.8455 | 84.3018 | -123.1338
3669.0156 | 123.1476 | -50.9766 | 71.9009 | 0.068512 | 0.010653 | 0.072096 | 0.070517 | 0.12971 | -0.00071785 | -0.0083591 | 0.0914 | -0.010835 | 0.063837 | 0.057612 | 0.0084808 | -0.01176 | 71.727 | 71.9238 | 4.9347 | -51.0132 | 72.0337 | -51.0635 | -51.1688 | -47.2961 | 33.4625 | -51.0544 | 72.0062 | 71.9009 | -51.2146 | -51.2512 | -0.086976 | -0.19226 | 0.13275 | 122.9004 | -0.036622 | 0.15564 | -0.17395 | -0.23804 | -0.27466 | 0.10529 | 3.6804 | -0.07782 | 0.19684 | 0 | 123.0103 | 122.7036 | 55.9113 | -123.0698 | 122.9828 | 122.8775 | 84.4391 | -123.1522
3670.0156 | 123.1567 | -50.267 | 72.5647 | 0.35843 | 0.015567 | 0.0706 | 0.071158 | 0.128 | 0.0018457 | -0.0081455 | 0.15244 | -0.0093396 | 0.066614 | 0.05633 | 0.008908 | -0.011546 | 72.5555 | 72.7066 | 5.0583 | -50.2808 | 72.7524 | -50.3082 | -50.4227 | -46.4767 | 34.1492 | -50.2625 | 72.7432 | 72.6242 | -50.4272 | -50.5096 | -0.041199 | -0.15564 | 0.18768 | 122.9736 | -0.013733 | 0.14191 | -0.009155 | -0.16022 | -0.24262 | 0.17853 | 3.7903 | 0.004578 | 0.24719 | 0.05951 | 123.0194 | 122.8226 | 55.3253 | -122.9874 | 123.0103 | 122.8912 | 84.4162 | -123.0743
3671.0156 | 123.0606 | -49.8505 | 73.0408 | 0.045624 | 0.0091581 | 0.070814 | 0.071372 | 0.12843 | -0.00093145 | -0.0062229 | 0.09903 | -0.010408 | 0.064264 | 0.056758 | 0.010617 | -0.010905 | 72.9401 | 73.1003 | 4.9667 | -49.8413 | 73.233 | -49.8779 | -49.9603 | -46.1655 | 34.5108 | -49.9008 | 73.1598 | 73.0408 | -50.061 | -50.1114 | -0.027466 | -0.10986 | 0.19226 | 122.9507 | 0.009155 | 0.11902 | -0.10071 | -0.21057 | -0.26093 | 0.11902 | 3.685 | -0.050354 | 0.21057 | 0 | 123.0835 | 122.7905 | 54.8172 | -123.0011 | 123.0103 | 122.8912 | 84.3613 | -123.1522
3672.0156 | 123.1247 | -48.7701 | 74.1165 | 0.17532 | 0.01514 | 0.071455 | 0.072012 | 0.12779 | 0.0050499 | -0.0053683 | 0.17532 | -0.010408 | 0.067468 | 0.058039 | 0.011899 | -0.015392 | 73.9929 | 74.1028 | 5.2094 | -48.793 | 74.2722 | -48.8388 | -48.9441 | -45.0806 | 35.4858 | -48.8297 | 74.231 | 74.0936 | -48.9944 | -49.0082 | -0.068664 | -0.17395 | 0.15564 | 122.8729 | -0.022888 | 0.15106 | -0.1236 | -0.2243 | -0.23804 | 0.11444 | 3.6896 | -0.059509 | 0.17853 | -0.022888 | 123.0423 | 122.7631 | 53.9795 | -123.0606 | 123.0011 | 122.8638 | 84.256 | -123.1247
3673.0156 | 123.1613 | -48.4131 | 74.4278 | 0.11429 | 0.012362 | 0.070814 | 0.070303 | 0.12928 | 0.0022729 | -0.0060093 | 0.24399 | -0.0093396 | 0.067255 | 0.055903 | 0.012753 | -0.011546 | 74.3088 | 74.5193 | 5.3375 | -48.4772 | 74.5605 | -48.5138 | -48.6374 | -44.7281 | 35.8521 | -48.4726 | 74.5468 | 74.4141 | -48.6603 | -48.6969 | -0.10071 | -0.2243 | 0.13275 | 122.9324 | -0.064087 | 0.16022 | -0.11902 | -0.24719 | -0.28381 | 0.11902 | 3.685 | -0.059509 | 0.2243 | -0.013733 | 122.9736 | 122.7219 | 53.7506 | -123.0652 | 122.9599 | 122.8271 | 84.2651 | -123.1247
3674.0156 | 123.1659 | -48.3856 | 74.4781 | 0.2211 | 0.018985 | 0.073805 | 0.074149 | 0.12864 | 0.0033411 | -0.0051547 | 0.11429 | -0.0097668 | 0.070886 | 0.058467 | 0.012967 | -0.013255 | 74.2813 | 74.4186 | 5.3284 | -48.5138 | 74.5514 | -48.5641 | -48.6649 | -44.7052 | 35.9848 | -48.3994 | 74.5468 | 74.4553 | -48.6145 | -48.6511 | -0.17853 | -0.27924 | 0.073243 | 122.8043 | -0.12817 | 0.15106 | -0.19684 | -0.22888 | -0.2655 | 0.068665 | 3.6804 | -0.013733 | 0.25177 | -0.022888 | 122.937 | 122.6669 | 53.714 | -123.143 | 122.9324 | 122.8409 | 84.3704 | -123.1293
3675.0156 | 123.1293 | -48.4497 | 74.4141 | 0.14481 | 0.012149 | 0.073377 | 0.073081 | 0.12907 | 0.00013675 | -0.0060093 | 0.26688 | -0.0097668 | 0.067896 | 0.05868 | 0.010831 | -0.01176 | 74.2767 | 74.4553 | 5.3238 | -48.4863 | 74.5148 | -48.5367 | -48.6328 | -44.7556 | 35.939 | -48.4543 | 74.4781 | 74.4324 | -48.6786 | -48.6923 | -0.086975 | -0.18311 | 0.10071 | 122.905 | -0.036621 | 0.14648 | -0.13733 | -0.22888 | -0.24262 | 0.064087 | 3.6942 | -0.004578 | 0.23804 | 0.018311 | 122.9645 | 122.7264 | 53.7735 | -123.0469 | 122.9279 | 122.8821 | 84.3887 | -123.1064
3676.0156 | 123.1247 | -48.1934 | 74.6887 | 0.20584 | 0.018558 | 0.071668 | 0.072653 | 0.12693 | 0.0022729 | -0.0057957 | 0.17532 | -0.008058 | 0.067468 | 0.057185 | 0.014249 | -0.011974 | 74.5102 | 74.6109 | 5.2414 | -48.2941 | 74.8123 | -48.3353 | -48.4222 | -44.5038 | 36.1679 | -48.2208 | 74.8032 | 74.6933 | -48.4085 | -48.4497 | -0.14191 | -0.22888 | 0.1236 | 122.8043 | -0.10071 | 0.12817 | -0.17853 | -0.21515 | -0.25635 | 0.11444 | 3.6896 | -0.027466 | 0.22888 | 0.004577 | 123.0057 | 122.7036 | 53.4348 | -123.111 | 122.9965 | 122.8867 | 84.3613 | -123.1384
3677.0156 | 123.0972 | -47.8043 | 75.032 | 0.19058 | 0.013217 | 0.072523 | 0.072653 | 0.13078 | -0.0013587 | -0.0072911 | 0.19058 | -0.011262 | 0.064905 | 0.057826 | 0.011258 | -0.012828 | 74.9222 | 75.1053 | 5.3375 | -47.8638 | 75.1785 | -47.9141 | -48.0103 | -44.1284 | 36.6074 | -47.8317 | 75.1282 | 75.0687 | -48.0469 | -48.0652 | -0.10986 | -0.20599 | 0.14648 | 122.9095 | -0.05951 | 0.14648 | -0.10986 | -0.24262 | -0.26093 | 0.096131 | 3.6758 | -0.027466 | 0.23346 | 0.036622 | 122.9828 | 122.7264 | 53.1418 | -123.0423 | 122.9324 | 122.8729 | 84.4116 | -123.0972
3678.0156 | 123.1567 | -48.8617 | 74.0158 | 0.16006 | 0.017489 | 0.073377 | 0.073721 | 0.12758 | 0.0024865 | -0.0070773 | 0.21347 | -0.01233 | 0.065973 | 0.05868 | 0.0086944 | -0.014537 | 73.8876 | 74.0158 | 5.2414 | -48.8937 | 74.1898 | -48.9487 | -49.0448 | -45.1492 | 35.6415 | -48.8708 | 74.1211 | 74.0067 | -49.0814 | -49.0997 | -0.086975 | -0.18311 | 0.17395 | 122.8775 | -0.032044 | 0.15106 | -0.12817 | -0.21973 | -0.23804 | 0.10529 | 3.7125 | -0.009156 | 0.22888 | -0.009155 | 123.0515 | 122.7493 | 54.1031 | -123.0606 | 122.9828 | 122.8683 | 84.5032 | -123.1155
3679.0156 | 123.111 | -49.8596 | 73.027 | 0.28976 | 0.013644 | 0.069532 | 0.069022 | 0.12971 | -0.00029045 | -0.0049411 | 0.21347 | -0.011903 | 0.066614 | 0.054621 | 0.012112 | -0.011546 | 72.9355 | 73.0957 | 5.1453 | -49.8276 | 73.1552 | -49.9008 | -50.0015 | -46.1014 | 34.8999 | -49.9146 | 73.1277 | 73.0316 | -50.0793 | -50.116 | -0.041199 | -0.14191 | 0.12817 | 122.9553 | 0.032043 | 0.17395 | -0.091553 | -0.21973 | -0.25635 | 0.10071 | 3.7582 | -0.054932 | 0.20142 | 0.004577 | 123.0148 | 122.7951 | 55.0049 | -123.0286 | 122.9874 | 122.8912 | 84.7595 | -123.143
3680.0156 | 123.0515 | -50.6241 | 72.2946 | 0.14481 | 0.017489 | 0.069959 | 0.074149 | 0.1327 | 0.0022729 | -0.0066501 | 0.19821 | -0.008058 | 0.067468 | 0.055689 | 0.013181 | -0.013469 | 72.1252 | 72.2305 | 4.8752 | -50.6561 | 72.4365 | -50.7156 | -50.8118 | -46.9391 | 34.1812 | -50.7889 | 72.3679 | 72.2717 | -50.8896 | -50.9033 | -0.091553 | -0.18768 | 0.14191 | 122.8546 | -0.032044 | 0.15564 | -0.16937 | -0.2655 | -0.27924 | 0.073242 | 3.685 | -0.16479 | 0.11444 | -0.022888 | 123.0606 | 122.7493 | 55.4993 | -123.1064 | 122.9919 | 122.8958 | 84.8053 | -123.1979
3681.0156 | 123.1659 | -50.1068 | 72.7524 | 0.19821 | 0.016849 | 0.068678 | 0.072867 | 0.12907 | -7.6852e-05 | -0.0062229 | 0.068512 | -0.0097668 | 0.066828 | 0.057398 | 0.010831 | -0.012828 | 72.67 | 72.8165 | 4.9072 | -50.3494 | 72.8348 | -50.2304 | -50.3311 | -46.3394 | 34.7534 | -50.1343 | 72.8439 | 72.7386 | -50.3448 | -50.3677 | -0.1236 | -0.2243 | 0.082398 | 122.9233 | -0.24261 | -0.01831 | -0.082397 | -0.23804 | -0.26093 | 0.091553 | 3.7674 | -0.027465 | 0.23346 | -0.013733 | 122.9416 | 122.7768 | 55.014 | -123.0835 | 122.9507 | 122.8455 | 84.8602 | -123.1201
3682.0156 | 123.0423 | -49.6811 | 73.2697 | -0.80124 | 0.018985 | 0.069746 | 0.074149 | 0.1295 | 0.0031273 | -0.0051547 | 0.13718 | -0.0082716 | 0.067468 | 0.058467 | 0.011685 | -0.013042 | 73.082 | 73.1918 | 5.127 | -49.6857 | 73.4619 | -49.704 | -49.8138 | -45.9412 | 35.1013 | -49.7223 | 73.407 | 73.288 | -49.8642 | -49.91 | -0.022888 | -0.13275 | 0.19226 | 122.8729 | -0.004578 | 0.12817 | -0.18768 | -0.18311 | -0.22888 | 0.13733 | 3.7399 | -0.041199 | 0.18768 | 0.018311 | 123.143 | 122.7631 | 54.808 | -123.0835 | 123.0881 | 122.9691 | 84.7824 | -123.1796
3683.0156 | 123.1201 | -48.9395 | 73.9563 | 0.12192 | 0.012362 | 0.069532 | 0.069449 | 0.12608 | -0.0022131 | -0.0053683 | 0.22873 | -0.011262 | 0.065332 | 0.057398 | 0.011044 | -0.012828 | 73.8007 | 73.9792 | 5.3009 | -48.9807 | 74.0387 | -49.0402 | -49.1318 | -45.2042 | 35.8063 | -48.9899 | 74.0158 | 73.9655 | -49.1592 | -49.1867 | -0.10071 | -0.19226 | 0.082397 | 122.9187 | -0.041199 | 0.15106 | -0.15564 | -0.21973 | -0.24719 | 0.059509 | 3.7354 | -0.050354 | 0.19684 | 0.009155 | 122.9782 | 122.7402 | 54.2404 | -123.0881 | 122.9553 | 122.905 | 84.7458 | -123.143
3684.0156 | 123.0881 | -48.7839 | 74.1028 | 0.20584 | 0.017276 | 0.072736 | 0.07479 | 0.12822 | 0.0029137 | -0.0062229 | 0.16769 | -0.0084852 | 0.066187 | 0.056758 | 0.012326 | -0.013255 | 73.9609 | 74.0662 | 5.2231 | -48.8297 | 74.3088 | -48.8754 | -48.9532 | -45.0668 | 35.9711 | -48.8434 | 74.263 | 74.1486 | -49.0265 | -49.0448 | -0.091552 | -0.16937 | 0.20599 | 122.85 | -0.045776 | 0.1236 | -0.14191 | -0.24261 | -0.26093 | 0.16022 | 3.717 | -0.059509 | 0.20142 | 0.045777 | 123.0927 | 122.7448 | 54.007 | -123.056 | 123.0469 | 122.9324 | 84.7549 | -123.1476
3685.0156 | 123.1293 | -49.3378 | 73.5214 | 0.21347 | 0.016421 | 0.071027 | 0.072226 | 0.128 | 0.00013675 | -0.0075047 | 0.23636 | -0.009126 | 0.066614 | 0.055049 | 0.012326 | -0.011974 | 73.3932 | 73.5443 | 5.1224 | -49.3881 | 73.6038 | -49.4751 | -49.5392 | -45.5704 | 35.376 | -49.4797 | 73.5626 | 73.4848 | -49.6399 | -49.6445 | -0.13733 | -0.20142 | 0.082398 | 122.8821 | -0.050354 | 0.15106 | -0.12817 | -0.30212 | -0.3067 | 0.041199 | 3.7674 | -0.14191 | 0.16479 | -0.036621 | 122.9416 | 122.731 | 54.4601 | -123.0606 | 122.9004 | 122.8226 | 84.7137 | -123.1659
3686.0156 | 122.9965 | -48.5733 | 74.3683 | 0.068512 | 0.01578 | 0.068891 | 0.074362 | 0.1327 | 0.0022729 | -0.0043003 | 0.11429 | -0.0089124 | 0.068537 | 0.056971 | 0.012326 | -0.011974 | 74.1943 | 74.295 | 5.1498 | -48.5641 | 74.5605 | -48.587 | -48.7244 | -44.8975 | 36.232 | -48.6969 | 74.5102 | 74.3958 | -48.7793 | -48.8251 | -0.013733 | -0.15106 | 0.19226 | 122.8683 | 0.009155 | 0.16022 | -0.17395 | -0.20599 | -0.25177 | 0.14191 | 3.6758 | -0.1236 | 0.12817 | 0.027466 | 123.1338 | 122.7676 | 53.7231 | -123.0927 | 123.0835 | 122.9691 | 84.8053 | -123.1934
3687.0156 | 123.143 | -48.2758 | 74.5743 | 0.18295 | 0.01813 | 0.071455 | 0.069022 | 0.12822 | -7.6852e-05 | -0.0047275 | 0.20584 | -0.0089124 | 0.064478 | 0.055903 | 0.012112 | -0.010265 | 74.4049 | 74.5285 | 5.2643 | -48.3765 | 74.7253 | -48.3948 | -48.5046 | -44.545 | 36.5295 | -48.2391 | 74.707 | 74.6246 | -48.4909 | -48.5229 | -0.11902 | -0.22888 | 0.15106 | 122.8043 | -0.10071 | 0.12817 | -0.16937 | -0.21515 | -0.24719 | 0.13275 | 3.7308 | 0.036621 | 0.28381 | 0.050354 | 123.0011 | 122.6807 | 53.54 | -123.0789 | 122.9828 | 122.9004 | 84.8053 | -123.0972
3688.0156 | 122.9965 | -48.0377 | 74.9451 | 0.083771 | 0.019839 | 0.068037 | 0.075003 | 0.12993 | 0.0037683 | -0.0055821 | 0.10666 | -0.006349 | 0.068964 | 0.056971 | 0.013394 | -0.012187 | 74.6613 | 74.7162 | 5.1727 | -48.0652 | 75.0504 | -48.1064 | -48.1842 | -44.371 | 36.7355 | -48.2208 | 75.0275 | 74.9542 | -48.2391 | -48.2758 | -0.068664 | -0.14648 | 0.10529 | 122.7539 | -0.027466 | 0.11902 | -0.28381 | -0.20142 | -0.23804 | 0.082398 | 3.6667 | -0.1831 | 0.054932 | 0.009156 | 123.0881 | 122.699 | 53.2104 | -123.1293 | 123.0652 | 122.9919 | 84.7733 | -123.2208
3689.0156 | 123.056 | -48.0743 | 74.8398 | 0.16006 | 0.017917 | 0.071455 | 0.074362 | 0.12843 | 0.00056395 | -0.0070773 | 0.21347 | -0.008058 | 0.067468 | 0.055689 | 0.010831 | -0.011546 | 74.6246 | 74.7391 | 5.2963 | -48.1522 | 74.9359 | -48.1613 | -48.2895 | -44.3436 | 36.8134 | -48.0515 | 74.9359 | 74.8856 | -48.317 | -48.3215 | -0.086975 | -0.21515 | 0.09613 | 122.8134 | -0.07782 | 0.13733 | -0.21515 | -0.24262 | -0.24719 | 0.09613 | 3.7308 | 0.022888 | 0.27008 | 0.045776 | 123.0103 | 122.699 | 53.3707 | -123.1293 | 123.0103 | 122.9599 | 84.8877 | -123.1613
3690.0156 | 123.0606 | -49.0906 | 73.8464 | 0.12192 | 0.021121 | 0.070814 | 0.07479 | 0.12886 | 0.0018457 | -0.0060093 | 0.14481 | -0.0084852 | 0.070032 | 0.058467 | 0.011258 | -0.013042 | 73.5306 | 73.6084 | 4.9667 | -49.2188 | 73.9151 | -49.2691 | -49.3195 | -45.3598 | 35.582 | -49.2004 | 73.9105 | 73.8693 | -49.3195 | -49.3469 | -0.17853 | -0.22888 | 0.068664 | 122.699 | -0.12817 | 0.10071 | -0.31586 | -0.22888 | -0.25635 | 0.064086 | 3.7308 | -0.10986 | 0.14648 | 0.022888 | 123.0057 | 122.6212 | 54.0573 | -123.1659 | 123.0011 | 122.9599 | 84.6725 | -123.1934
3691.0156 | 123.1064 | -48.0515 | 74.8764 | 0.19058 | 0.018985 | 0.073377 | 0.074362 | 0.12843 | -0.00029045 | -0.0053683 | 0.20584 | -0.0099806 | 0.066614 | 0.056758 | 0.011472 | -0.011333 | 74.6109 | 74.7482 | 5.2963 | -48.143 | 74.9588 | -48.1613 | -48.2529 | -44.2703 | 36.9232 | -48.0331 | 75.0046 | 74.8993 | -48.2574 | -48.2803 | -0.10986 | -0.20142 | 0.082397 | 122.7997 | -0.091552 | 0.10986 | -0.2655 | -0.20599 | -0.22888 | 0.12817 | 3.7811 | 0.018311 | 0.24719 | 0.022888 | 123.0103 | 122.6624 | 53.3478 | -123.1293 | 123.056 | 122.9507 | 84.9747 | -123.1567
3692.0156 | 123.0377 | -48.4817 | 74.501 | -0.023041 | 0.018771 | 0.069532 | 0.076498 | 0.12971 | 0.0022729 | -0.0053683 | -0.0077819 | -0.0082716 | 0.068537 | 0.057398 | 0.013394 | -0.01176 | 74.3362 | 74.4186 | 5.2185 | -48.4726 | 74.5789 | -48.5413 | -48.6237 | -44.7006 | 36.5891 | -48.5184 | 74.5926 | 74.5331 | -48.6694 | -48.7061 | -0.05951 | -0.14191 | 0.077819 | 122.9004 | 0.009155 | 0.15106 | -0.16479 | -0.18768 | -0.22431 | 0.091552 | 3.7811 | -0.036622 | 0.18768 | 0.032043 | 123.0606 | 122.818 | 53.7003 | -123.1247 | 123.0743 | 123.0148 | 85.0708 | -123.2071
3693.0156 | 123.0515 | -48.5733 | 74.3637 | -0.19852 | 0.01813 | 0.069746 | 0.071799 | 0.12886 | 0.00077755 | -0.0066501 | 0.14481 | -0.009126 | 0.068537 | 0.05868 | 0.011472 | -0.011333 | 74.1669 | 74.2813 | 5.3009 | -48.5687 | 74.5697 | -48.6008 | -48.7015 | -44.838 | 36.4929 | -48.642 | 74.501 | 74.4278 | -48.8022 | -48.7976 | -0.027466 | -0.12817 | 0.20599 | 122.8546 | 0.004577 | 0.13275 | -0.19684 | -0.22888 | -0.2243 | 0.13733 | 3.7354 | -0.068665 | 0.15564 | 0.064087 | 123.143 | 122.7402 | 53.8742 | -123.0652 | 123.0743 | 123.0011 | 85.0662 | -123.1613
3694.0156 | 123.0331 | -48.674 | 74.2859 | -0.068817 | 0.018558 | 0.071668 | 0.07479 | 0.12672 | 0.0016321 | -0.0072911 | -0.015411 | -0.0089124 | 0.069818 | 0.05633 | 0.012326 | -0.012828 | 74.0891 | 74.2035 | 5.3833 | -48.7015 | 74.4232 | -48.7198 | -48.8205 | -44.8746 | 36.4929 | -48.6877 | 74.4049 | 74.3591 | -48.8388 | -48.8846 | -0.045777 | -0.14648 | 0.13733 | 122.8775 | -0.027466 | 0.11902 | -0.19684 | -0.16479 | -0.21057 | 0.11902 | 3.7994 | -0.013733 | 0.19684 | 0.073242 | 123.0972 | 122.7631 | 54.0573 | -123.1064 | 123.0789 | 123.0331 | 85.1669 | -123.1705
3695.0156 | 123.0377 | -48.0835 | 74.8581 | 0.022736 | 0.017703 | 0.070173 | 0.073081 | 0.12864 | 0.0024865 | -0.0057957 | 0.16006 | -0.003999 | 0.069605 | 0.057185 | 0.0076264 | -0.01176 | 74.5972 | 74.6979 | 5.397 | -48.1522 | 74.9863 | -48.1567 | -48.2483 | -44.3481 | 36.8958 | -48.0331 | 74.9771 | 74.913 | -48.2941 | -48.317 | -0.073242 | -0.1648 | 0.12817 | 122.7814 | -0.068665 | 0.09613 | -0.26093 | -0.21057 | -0.23346 | 0.11902 | 3.7354 | 0.050354 | 0.28381 | 0.054932 | 123.0698 | 122.6807 | 53.4805 | -123.1064 | 123.0606 | 122.9965 | 84.9792 | -123.175
3696.0156 | 123.1018 | -48.2162 | 74.7162 | 1.541 | 0.020267 | 0.070387 | 0.076498 | 0.1295 | 0.0016321 | -0.0087863 | -0.015411 | -0.0076306 | 0.064478 | 0.061244 | 0.011472 | -0.014751 | 74.4873 | 74.6155 | 5.5206 | -48.2986 | 74.7711 | -48.3582 | -48.4497 | -44.5038 | 36.8362 | -48.317 | 74.7757 | 74.7025 | -48.4772 | -48.4955 | -0.14191 | -0.23346 | 0.054931 | 122.8317 | -0.082397 | 0.15106 | -0.22888 | -0.26093 | -0.27923 | 0.059509 | 3.7125 | -0.10071 | 0.17853 | -0.013733 | 122.9874 | 122.7036 | 53.7369 | -123.1659 | 122.9919 | 122.9187 | 85.0525 | -123.2117
3697.0156 | 123.0515 | -48.555 | 74.4186 | 0.15244 | 0.018344 | 0.070814 | 0.072012 | 0.12779 | 0.0065453 | -0.0060093 | -0.099335 | -0.0095532 | 0.067896 | 0.058467 | 0.011899 | -0.014537 | 74.0112 | 74.5926 | 5.4932 | -48.6557 | 74.5697 | -48.5962 | -48.7061 | -44.8105 | 36.5067 | -48.6008 | 74.4736 | 74.4278 | -48.7473 | -48.7564 | -0.041198 | -0.15106 | 0.15106 | 123.1476 | -0.10071 | 0.050354 | -0.40741 | -0.19226 | -0.20142 | 0.054932 | 3.7445 | -0.045776 | 0.15564 | 0.009155 | 123.1247 | 122.5662 | 54.0482 | -123.1247 | 123.0286 | 122.9828 | 85.0616 | -123.175
3698.0156 | 123.0835 | -48.4131 | 74.5056 | -0.084076 | 0.018771 | 0.068678 | 0.072653 | 0.12715 | 0.0018457 | -0.0066501 | -0.00015237 | -0.0084852 | 0.067682 | 0.056117 | 0.011899 | -0.011546 | 74.4003 | 74.5056 | 5.3696 | -48.3627 | 74.7208 | -48.4314 | -48.5321 | -44.6136 | 36.7813 | -48.6145 | 74.6567 | 74.556 | -48.6191 | -48.6694 | -0.01831 | -0.11902 | 0.21515 | 122.9187 | 0.050354 | 0.16937 | -0.10529 | -0.20599 | -0.25635 | 0.15106 | 3.7994 | -0.20142 | 0.054932 | 0.050354 | 123.1338 | 122.8134 | 53.7827 | -123.0377 | 123.0698 | 122.9691 | 85.1944 | -123.175
3699.0156 | 123.0011 | -48.5687 | 74.382 | 0.037994 | 0.02048 | 0.070814 | 0.074576 | 0.12993 | 0.0014185 | -0.0072911 | 0.10666 | -0.009126 | 0.067896 | 0.058253 | 0.010617 | -0.013683 | 74.1623 | 74.2584 | 5.2505 | -48.5825 | 74.5605 | -48.5962 | -48.6877 | -44.8013 | 36.6165 | -48.7244 | 74.5102 | 74.4415 | -48.7473 | -48.8159 | -0.027465 | -0.11902 | 0.17853 | 122.8271 | -0.013732 | 0.10529 | -0.21973 | -0.17853 | -0.24719 | 0.12817 | 3.7674 | -0.15564 | 0.091553 | 0.059509 | 123.1293 | 122.731 | 53.8193 | -123.0698 | 123.0789 | 123.0103 | 85.1852 | -123.1979
3700.0156 | 123.056 | -48.8571 | 74.057 | -0.19089 | 0.019626 | 0.070814 | 0.073294 | 0.1295 | 0.00077755 | -0.0070773 | -0.14511 | -0.010408 | 0.067041 | 0.057826 | 0.0093354 | -0.012828 | 73.7503 | 73.9197 | 5.2597 | -48.6557 | 74.1623 | -48.999 | -49.0906 | -45.108 | 36.4655 | -49.0173 | 74.1623 | 74.0845 | -49.1226 | -49.1409 | -0.14191 | -0.23346 | 0.10528 | 122.7768 | 0.20142 | 0.43487 | -0.3067 | -0.2655 | -0.28381 | 0.10528 | 3.7491 | -0.16022 | 0.1236 | 0.027466 | 123.0194 | 122.6074 | 54.1168 | -123.1476 | 123.0194 | 122.9416 | 85.3226 | -123.1979
3701.0156 | 123.056 | -48.0927 | 74.8718 | -0.0077822 | 0.019626 | 0.069959 | 0.072226 | 0.12971 | 0.0033411 | -0.0079319 | 0.060883 | -0.010194 | 0.069391 | 0.057398 | 0.0099762 | -0.012828 | 74.6979 | 74.8398 | 5.4062 | -47.9233 | 75.1007 | -48.0698 | -48.1888 | -44.2886 | 37.1246 | -48.2483 | 75.0137 | 74.9039 | -48.2849 | -48.3307 | 0.022888 | -0.096131 | 0.22888 | 122.9324 | 0.16937 | 0.2655 | -0.17395 | -0.19226 | -0.23804 | 0.14191 | 3.804 | -0.15564 | 0.082397 | 0.032044 | 123.1934 | 122.7905 | 53.4988 | -123.0606 | 123.1064 | 122.9965 | 85.2173 | -123.2025
3702.0156 | 123.1064 | -47.7539 | 75.1877 | -0.20615 | 0.017917 | 0.073164 | 0.073508 | 0.12907 | 0.0018457 | -0.0081455 | -0.11459 | -0.0097668 | 0.066614 | 0.057398 | 0.011044 | -0.011119 | 75.0046 | 75.1556 | 5.5939 | -47.612 | 75.3754 | -47.7905 | -47.8958 | -43.9087 | 37.5916 | -47.8409 | 75.3296 | 75.2472 | -47.9691 | -47.9965 | -0.036621 | -0.14191 | 0.18768 | 122.9095 | 0.14191 | 0.28381 | -0.18311 | -0.21515 | -0.24262 | 0.14191 | 3.8452 | -0.086975 | 0.15564 | 0.059509 | 123.1293 | 122.7585 | 53.3478 | -123.0835 | 123.0835 | 123.0011 | 85.3455 | -123.1842
3703.0156 | 123.0423 | -47.3785 | 75.5951 | 0.12192 | 0.018344 | 0.068464 | 0.074576 | 0.13057 | 0.0035547 | -0.0075047 | 0.20584 | -0.011689 | 0.067255 | 0.059107 | 0.011044 | -0.013042 | 75.2975 | 75.4395 | 5.4794 | -47.319 | 75.7416 | -47.4426 | -47.5388 | -43.5287 | 37.7884 | -47.4472 | 75.7187 | 75.6454 | -47.5754 | -47.5891 | -0.064087 | -0.16022 | 0.14648 | 122.818 | 0.059509 | 0.21973 | -0.29755 | -0.19684 | -0.21057 | 0.1236 | 3.8498 | -0.068665 | 0.14191 | 0.050354 | 123.1201 | 122.6761 | 52.858 | -123.1338 | 123.0972 | 123.024 | 85.1669 | -123.1842
3704.0156 | 123.0789 | -47.0718 | 75.9384 | -0.19089 | 0.018771 | 0.071455 | 0.073935 | 0.13057 | 0.0012047 | -0.0062229 | -0.12985 | -0.0089124 | 0.066614 | 0.058253 | 0.011044 | -0.012614 | 75.7187 | 75.8698 | 5.3696 | -46.9025 | 76.0757 | -47.0901 | -47.1771 | -43.2358 | 38.1592 | -47.1634 | 76.0025 | 75.9247 | -47.287 | -47.3373 | -0.018311 | -0.10529 | 0.13733 | 122.9416 | 0.16937 | 0.27466 | -0.21973 | -0.21515 | -0.2655 | 0.064086 | 3.8361 | -0.091553 | 0.17395 | -0.013733 | 123.1476 | 122.7905 | 52.4414 | -123.1155 | 123.0743 | 122.9965 | 85.231 | -123.2758
3705.0156 | 123.056 | -46.7743 | 76.2085 | -0.053558 | 0.018558 | 0.072096 | 0.074149 | 0.12629 | 0.0033411 | -0.0060093 | 0.068512 | -0.010194 | 0.071314 | 0.055903 | 0.012112 | -0.011119 | 75.9842 | 76.1169 | 5.5069 | -46.6553 | 76.3229 | -46.843 | -46.9482 | -42.9794 | 38.4018 | -46.875 | 76.2955 | 76.1948 | -46.9757 | -47.0032 | -0.068665 | -0.17395 | 0.11444 | 122.8912 | 0.11902 | 0.29297 | -0.2243 | -0.20142 | -0.22888 | 0.086975 | 3.7949 | -0.10071 | 0.12817 | -0.013733 | 123.0972 | 122.7585 | 52.2812 | -123.1567 | 123.0698 | 122.9691 | 85.1761 | -123.2117
3706.0156 | 123.0057 | -46.4035 | 76.6022 | -0.23666 | 0.014285 | 0.073377 | 0.075644 | 0.12736 | 0.0029137 | -0.0089999 | -0.29007 | -0.009126 | 0.0664 | 0.059321 | 0.01019 | -0.010692 | 76.1993 | 76.5747 | 5.6946 | -46.2982 | 76.7487 | -46.4539 | -46.5271 | -42.5903 | 38.7863 | -46.4584 | 76.6846 | 76.6479 | -46.5958 | -46.6095 | -0.050354 | -0.1236 | 0.14648 | 122.9782 | 0.10529 | 0.22888 | -0.40283 | -0.19226 | -0.20599 | 0.082397 | 3.8132 | -0.054932 | 0.15106 | 0.045776 | 123.1522 | 122.6028 | 52.0981 | -123.1293 | 123.0881 | 123.0515 | 85.1898 | -123.2117
3707.0156 | 123.0927 | -46.2616 | 76.6983 | -0.22903 | 0.017062 | 0.068891 | 0.07543 | 0.13228 | 0.0029137 | -0.0094273 | -0.091705 | -0.010194 | 0.067255 | 0.05633 | 0.009549 | -0.012187 | 76.4191 | 76.6022 | 5.5023 | -46.17 | 76.7944 | -46.3394 | -46.4447 | -42.4667 | 38.887 | -46.3028 | 76.7853 | 76.6891 | -46.4996 | -46.5363 | -0.07782 | -0.1831 | 0.096131 | 122.8638 | 0.091553 | 0.27466 | -0.27924 | -0.23804 | -0.27466 | 0.086975 | 3.7949 | -0.041198 | 0.23346 | -0.009155 | 123.056 | 122.6807 | 51.7639 | -123.143 | 123.0469 | 122.9507 | 85.1486 | -123.2346
3708.0156 | 123.0377 | -46.4035 | 76.5152 | -0.24429 | 0.017703 | 0.071455 | 0.073721 | 0.128 | 0.0018457 | -0.0060093 | -0.038299 | -0.0095532 | 0.0664 | 0.057398 | 0.011258 | -0.011546 | 76.2497 | 76.442 | 5.6854 | -46.3348 | 76.6342 | -46.5134 | -46.6599 | -42.627 | 38.7268 | -46.5042 | 76.5701 | 76.5015 | -46.6507 | -46.6644 | -0.10986 | -0.25635 | 0.11902 | 122.8455 | 0.068664 | 0.32501 | -0.2655 | -0.24719 | -0.26093 | 0.054931 | 3.7766 | -0.10071 | 0.16022 | -0.013733 | 123.0377 | 122.6532 | 52.0889 | -123.175 | 122.9736 | 122.905 | 85.1303 | -123.1796
3709.0156 | 123.0743 | -46.4813 | 76.474 | -0.15274 | 0.018771 | 0.071455 | 0.074149 | 0.12928 | 0.00099115 | -0.0070773 | -0.076446 | -0.0093396 | 0.067896 | 0.057612 | 0.0099762 | -0.013042 | 75.8835 | 76.0345 | 5.6625 | -46.6003 | 76.3092 | -46.8063 | -46.843 | -42.6315 | 38.7268 | -46.4813 | 76.5839 | 76.5015 | -46.6599 | -46.7194 | -0.32501 | -0.36163 | -0.1648 | 122.5159 | -0.11902 | 0.24262 | -0.59052 | -0.17853 | -0.23804 | 0.10986 | 3.8498 | 0 | 0.23804 | 0.027466 | 122.7905 | 122.3648 | 52.1439 | -123.317 | 123.0652 | 122.9828 | 85.2081 | -123.1934
3710.0156 | 123.0743 | -46.4813 | 76.506 | -0.17563 | 0.01578 | 0.071882 | 0.071585 | 0.12736 | -0.0032813 | -0.010068 | -0.099335 | -0.0097668 | 0.067896 | 0.057826 | 0.0091216 | -0.012187 | 76.2863 | 76.4603 | 5.6625 | -46.3257 | 76.6891 | -46.4996 | -46.6187 | -42.6453 | 38.649 | -46.4905 | 76.6296 | 76.6068 | -46.6232 | -46.6553 | -0.018311 | -0.13733 | 0.18311 | 122.9416 | 0.15564 | 0.29297 | -0.21973 | -0.14191 | -0.17395 | 0.1236 | 3.8361 | -0.009156 | 0.16479 | 0.10071 | 123.1705 | 122.7676 | 52.1439 | -123.1247 | 123.111 | 123.0881 | 85.1303 | -123.1613
3711.0156 | 122.9874 | -46.8292 | 76.1215 | -0.17563 | 0.017917 | 0.072736 | 0.07543 | 0.12971 | 0.0020593 | -0.0079319 | -0.10696 | -0.0099806 | 0.0664 | 0.058039 | 0.01019 | -0.012828 | 75.8743 | 76.0391 | 5.5756 | -46.7148 | 76.2314 | -46.9299 | -47.0215 | -43.0344 | 38.2874 | -46.9345 | 76.1856 | 76.1078 | -47.081 | -47.0901 | -0.10071 | -0.19226 | 0.10986 | 122.8683 | 0.11444 | 0.3067 | -0.24719 | -0.25177 | -0.26092 | 0.064087 | 3.7949 | -0.10528 | 0.15564 | -0.013733 | 123.0606 | 122.7036 | 52.4048 | -123.143 | 123.0148 | 122.937 | 85.1166 | -123.2117
3712.0156 | 123.024 | -46.5591 | 76.387 | -0.22141 | 0.013644 | 0.074232 | 0.070731 | 0.12779 | 0.0012047 | -0.010282 | -0.77835 | -0.0095532 | 0.068964 | 0.056971 | 0.007199 | -0.011119 | 76.0483 | 76.2543 | 5.7037 | -46.4905 | 76.4603 | -46.669 | -46.7743 | -42.7597 | 38.5071 | -46.6324 | 76.4923 | 76.4374 | -46.7926 | -46.8018 | -0.10986 | -0.21515 | 0.073242 | 122.8134 | 0.068664 | 0.28381 | -0.33875 | -0.23346 | -0.24262 | 0.10529 | 3.7994 | -0.073242 | 0.16937 | 0.050354 | 123.0194 | 122.6074 | 52.2629 | -123.1613 | 123.0515 | 122.9965 | 85.0662 | -123.1888
3713.0156 | 123.0469 | -46.5179 | 76.442 | 0.16006 | 0.020053 | 0.06825 | 0.073294 | 0.12886 | 0.0029137 | -0.0072911 | 0.045624 | -0.0089124 | 0.066828 | 0.057398 | 0.013821 | -0.011333 | 76.1948 | 75.9933 | 5.5801 | -46.2936 | 76.5472 | -46.6599 | -46.7285 | -42.7231 | 38.5803 | -46.5729 | 76.5564 | 76.4694 | -46.7331 | -46.7743 | -0.14191 | -0.21057 | 0.10528 | 122.5113 | 0.2243 | 0.43488 | -0.24719 | -0.21515 | -0.25635 | 0.11444 | 3.7949 | -0.054932 | 0.20142 | 0.027465 | 123.0652 | 122.7127 | 52.0981 | -123.1705 | 123.0743 | 122.9874 | 85.0983 | -123.2162
3714.0156 | 123.1293 | -46.6324 | 76.2955 | -0.20615 | 0.0097989 | 0.072736 | 0.073294 | 0.128 | -0.0039221 | -0.0089999 | -0.084076 | -0.0099806 | 0.068109 | 0.056544 | 0.0086944 | -0.012828 | 76.1078 | 76.3412 | 5.658 | -46.4859 | 76.4236 | -46.6873 | -46.8018 | -42.8055 | 38.6124 | -46.6507 | 76.3687 | 76.3 | -46.8475 | -46.8796 | -0.054932 | -0.16937 | 0.12817 | 122.9736 | 0.14648 | 0.31586 | -0.18768 | -0.21515 | -0.24719 | 0.073242 | 3.8269 | -0.018311 | 0.22888 | 0.004578 | 123.056 | 122.7402 | 52.2903 | -123.0972 | 123.0011 | 122.9324 | 85.2448 | -123.175
3715.0156 | 123.0377 | -46.2891 | 76.6617 | -0.19089 | 0.017276 | 0.072523 | 0.07244 | 0.12928 | 0.0041955 | -0.0072911 | -0.15274 | -0.0093396 | 0.066187 | 0.057612 | 0.011472 | -0.013469 | 76.387 | 76.5518 | 5.6259 | -46.1838 | 76.7578 | -46.376 | -46.463 | -42.453 | 38.942 | -46.3211 | 76.7624 | 76.7029 | -46.5088 | -46.5225 | -0.086976 | -0.17395 | 0.09613 | 122.8409 | 0.10529 | 0.27924 | -0.27466 | -0.21973 | -0.23346 | 0.10071 | 3.8361 | -0.032044 | 0.20142 | 0.041199 | 123.0469 | 122.6761 | 51.915 | -123.1247 | 123.0515 | 122.9919 | 85.231 | -123.1842
3716.0156 | 123.056 | -46.3211 | 76.6571 | -0.21378 | 0.011935 | 0.072309 | 0.072012 | 0.12971 | -0.0019995 | -0.0083591 | -0.11459 | -0.010408 | 0.067896 | 0.055049 | 0.0097626 | -0.0098374 | 76.4465 | 76.6617 | 5.8228 | -46.1243 | 76.8173 | -46.3303 | -46.431 | -42.4667 | 39.0244 | -46.3028 | 76.7487 | 76.6525 | -46.5088 | -46.5408 | -0.009155 | -0.10986 | 0.16022 | 122.9828 | 0.19684 | 0.3067 | -0.21057 | -0.18768 | -0.21973 | 0.091553 | 3.8544 | 0.018311 | 0.23804 | -0.004577 | 123.1384 | 122.7676 | 52.1439 | -123.0881 | 123.0698 | 122.9736 | 85.3455 | -123.1979
3717.0156 | 123.0606 | -45.6345 | 77.33 | -0.4274 | 0.016849 | 0.071027 | 0.07543 | 0.13121 | 0.0031273 | -0.0075047 | -0.17563 | -0.011262 | 0.067041 | 0.058039 | 0.010617 | -0.013255 | 77.1011 | 77.2659 | 5.7678 | -45.4926 | 77.504 | -45.6436 | -45.7809 | -41.7847 | 39.6194 | -45.7077 | 77.4811 | 77.3621 | -45.8176 | -45.8496 | -0.009156 | -0.14649 | 0.17395 | 122.9004 | 0.14191 | 0.28839 | -0.22888 | -0.18311 | -0.21515 | 0.15106 | 3.8498 | -0.073243 | 0.14191 | 0.032044 | 123.1384 | 122.7356 | 51.4023 | -123.111 | 123.1155 | 122.9965 | 85.2539 | -123.1796
3718.0156 | 123.0835 | -46.7514 | 76.2177 | 0.12192 | 0.019412 | 0.071455 | 0.074576 | 0.12822 | 0.0052637 | -0.0075047 | 0.15244 | -0.007417 | 0.070459 | 0.059535 | 0.012112 | -0.011974 | 75.8743 | 76.0208 | 5.8594 | -46.6919 | 76.3092 | -46.8842 | -46.9574 | -42.8787 | 38.1775 | -46.7697 | 76.2131 | 76.1948 | -46.9666 | -47.0032 | -0.13275 | -0.20599 | 0.091553 | 122.7722 | 0.059509 | 0.2655 | -0.34332 | -0.21515 | -0.25177 | -0.004577 | 3.8727 | -0.01831 | 0.23346 | -0.022888 | 123.0606 | 122.6257 | 52.6108 | -123.175 | 122.9645 | 122.9462 | 84.9289 | -123.2208
3719.0156 | 123.056 | -46.582 | 76.3229 | -0.21378 | 0.016635 | 0.069959 | 0.073721 | 0.13206 | 0.0016321 | -0.0079319 | -0.2214 | -0.0095532 | 0.068323 | 0.058253 | 0.011899 | -0.013255 | 76.1261 | 76.3 | 5.7587 | -46.4401 | 76.5381 | -46.6507 | -46.756 | -42.7368 | 38.8275 | -46.7056 | 76.4694 | 76.3962 | -46.7834 | -46.843 | -0.068665 | -0.17395 | 0.21515 | 122.8821 | 0.14191 | 0.31586 | -0.19684 | -0.20142 | -0.26093 | 0.14648 | 3.8452 | -0.1236 | 0.13733 | 0.073242 | 123.1201 | 122.7081 | 52.3407 | -123.0789 | 123.0515 | 122.9782 | 85.4095 | -123.1659
3720.0156 | 123.1338 | -46.8887 | 76.0254 | -0.44266 | 0.0083035 | 0.0706 | 0.073081 | 0.12993 | -0.0037085 | -0.0068637 | -0.084076 | -0.012758 | 0.066187 | 0.05633 | 0.0086944 | -0.010905 | 75.7919 | 76.0574 | 5.9006 | -46.7285 | 76.1169 | -46.9528 | -47.0535 | -42.9474 | 38.7268 | -46.8567 | 76.0757 | 76.0574 | -47.1085 | -47.1176 | -0.064087 | -0.16479 | 0.091552 | 122.9462 | 0.16022 | 0.32501 | -0.23346 | -0.21973 | -0.22888 | 0.050354 | 3.9413 | 0.032044 | 0.26093 | 0.032043 | 123.0057 | 122.6807 | 52.7893 | -123.0789 | 122.9645 | 122.9462 | 85.6155 | -123.143
3721.0156 | 123.056 | -46.7926 | 76.1765 | -0.45792 | 0.017489 | 0.072736 | 0.074576 | 0.12864 | 0.0024865 | -0.0075047 | -0.19089 | -0.010835 | 0.067255 | 0.058894 | 0.011258 | -0.012401 | 75.9201 | 76.1078 | 5.896 | -46.6415 | 76.3275 | -46.8384 | -46.9482 | -42.8925 | 38.7497 | -46.8979 | 76.2772 | 76.1948 | -46.994 | -47.0169 | -0.045776 | -0.15564 | 0.15106 | 122.9004 | 0.15106 | 0.3067 | -0.25635 | -0.20142 | -0.2243 | 0.10071 | 3.9001 | -0.10529 | 0.11902 | 0.01831 | 123.1201 | 122.7127 | 52.6886 | -123.1247 | 123.0698 | 122.9874 | 85.5423 | -123.1934
3722.0156 | 123.1201 | -47.9416 | 74.968 | -0.22903 | 0.010867 | 0.071241 | 0.071158 | 0.12758 | -0.0013587 | -0.0066501 | -0.10696 | -0.011476 | 0.067041 | 0.057398 | 0.010617 | -0.013042 | 74.7253 | 75.0092 | 5.7404 | -47.8088 | 75.0687 | -48.056 | -48.1796 | -44.0048 | 37.8387 | -47.9965 | 75.032 | 74.9588 | -48.1842 | -48.1842 | -0.11444 | -0.23804 | 0.10071 | 122.9507 | 0.13275 | 0.37079 | -0.24262 | -0.24262 | -0.24262 | 0.064086 | 3.9368 | -0.054932 | 0.18768 | -0.009156 | 123.0103 | 122.6669 | 53.6819 | -123.1476 | 122.9736 | 122.9004 | 85.7803 | -123.1522
3723.0312 | 123.1293 | -47.0947 | 75.7919 | 0.083771 | 0.014499 | 0.073805 | 0.07009 | 0.12971 | -0.0017859 | -0.0077183 | 0.24399 | -0.011262 | 0.064051 | 0.057398 | 0.010831 | -0.01176 | 75.6226 | 75.8057 | 5.8502 | -46.962 | 75.9293 | -47.1817 | -47.2687 | -43.0984 | 38.6169 | -47.1588 | 75.8743 | 75.7645 | -47.3328 | -47.3602 | -0.086975 | -0.17395 | 0.13733 | 122.9004 | 0.13275 | 0.3067 | -0.16937 | -0.23804 | -0.2655 | 0.082398 | 3.9963 | -0.064086 | 0.20142 | -0.027466 | 123.024 | 122.7173 | 52.9449 | -123.0606 | 122.9691 | 122.8592 | 85.7117 | -123.1522
3724.0156 | 123.1201 | -47.168 | 75.705 | 1.1671 | 0.011294 | 0.074018 | 0.072653 | 0.12928 | -0.00093145 | -0.012418 | -0.045929 | -0.0099806 | 0.065759 | 0.057185 | 0.010403 | -0.013255 | 75.6134 | 75.7645 | 5.8411 | -46.994 | 75.8514 | -47.2549 | -47.3648 | -43.1808 | 38.6627 | -47.1909 | 75.7874 | 75.6958 | -47.3602 | -47.4197 | -0.086975 | -0.19684 | 0.14648 | 122.9324 | 0.17395 | 0.37079 | -0.091553 | -0.19226 | -0.25177 | 0.082398 | 3.9871 | -0.022888 | 0.22888 | -0.009155 | 123.0194 | 122.7814 | 53.009 | -123.0698 | 122.9553 | 122.8638 | 85.8307 | -123.1247
3725.0156 | 123.056 | -46.4264 | 76.5152 | -1.6786 | 0.013858 | 0.071668 | 0.071372 | 0.12886 | 0.0033411 | -0.0087863 | -0.13748 | -0.0099806 | 0.065759 | 0.05633 | 0.010403 | -0.013042 | 76.2634 | 76.4282 | 5.8868 | -46.312 | 76.7075 | -46.5225 | -46.6141 | -42.5034 | 39.2899 | -46.5088 | 76.6525 | 76.5518 | -46.6507 | -46.6644 | -0.09613 | -0.18768 | 0.19226 | 122.8546 | 0.11444 | 0.30212 | -0.25177 | -0.2243 | -0.23804 | 0.13733 | 3.923 | -0.082397 | 0.15564 | 0.036621 | 123.1338 | 122.6898 | 52.3132 | -123.1293 | 123.0789 | 122.9782 | 85.7162 | -123.1796
3726.0156 | 123.1247 | -46.8475 | 76.0483 | -0.18326 | 0.010226 | 0.071668 | 0.070944 | 0.13014 | -0.0022131 | -0.0077183 | -0.10696 | -0.011262 | 0.065332 | 0.058253 | 0.0093354 | -0.013469 | 75.8789 | 76.1444 | 5.9006 | -46.6049 | 76.1856 | -46.8887 | -47.0215 | -42.8421 | 39.0244 | -46.9894 | 76.1444 | 76.0712 | -47.0627 | -47.0718 | -0.041199 | -0.17395 | 0.13733 | 122.9919 | 0.24262 | 0.41656 | -0.16937 | -0.21515 | -0.2243 | 0.09613 | 4.0054 | -0.14191 | 0.082397 | 0.022888 | 123.0331 | 122.7264 | 52.7481 | -123.0698 | 122.9919 | 122.9187 | 85.8719 | -123.1201
3727.0156 | 123.0743 | -46.2204 | 76.7441 | -0.24429 | 0.015353 | 0.071455 | 0.073081 | 0.13035 | 0.0014185 | -0.010709 | -0.12985 | -0.011476 | 0.069818 | 0.058894 | 0.0099762 | -0.012401 | 76.506 | 76.7441 | 5.8136 | -46.0876 | 76.8448 | -46.2662 | -46.3715 | -42.2516 | 39.4913 | -46.2845 | 76.8173 | 76.7303 | -46.4447 | -46.4584 | -0.045776 | -0.15106 | 0.10071 | 122.9645 | 0.13275 | 0.28381 | -0.23804 | -0.2243 | -0.23804 | 0.073242 | 3.9688 | -0.064087 | 0.17395 | -0.013733 | 123.0652 | 122.7264 | 52.034 | -123.1155 | 123.0377 | 122.9507 | 85.7117 | -123.2025
3728.0312 | 123.0652 | -46.0968 | 76.8448 | 0.015106 | 0.01813 | 0.072736 | 0.074362 | 0.12779 | 0.0071863 | -0.0043003 | -0.0077819 | -0.0076306 | 0.068537 | 0.057185 | 0.013394 | -0.017101 | 76.6205 | 76.767 | 5.896 | -45.9915 | 76.9821 | -46.2067 | -46.3074 | -42.1921 | 39.5599 | -46.2158 | 76.9318 | 76.8036 | -46.3211 | -46.3715 | -0.10986 | -0.21057 | 0.13733 | 122.8638 | 0.10529 | 0.31586 | -0.22431 | -0.2243 | -0.27466 | 0.086975 | 3.9047 | -0.11902 | 0.15564 | -0.041199 | 123.0789 | 122.7173 | 51.9928 | -123.1522 | 123.0286 | 122.9004 | 85.6567 | -123.2162
3729.0156 | 123.0331 | -46.5179 | 76.4511 | -0.21378 | 0.01279 | 0.0706 | 0.07244 | 0.13014 | -0.00029045 | -0.0070773 | -0.16037 | -0.011903 | 0.067896 | 0.058039 | 0.011685 | -0.011974 | 76.2085 | 76.4099 | 5.7724 | -46.3623 | 76.6113 | -46.5637 | -46.6782 | -42.54 | 39.3036 | -46.5317 | 76.5656 | 76.4786 | -46.7056 | -46.7468 | -0.045777 | -0.16022 | 0.16022 | 122.9279 | 0.15564 | 0.31586 | -0.24262 | -0.18768 | -0.22888 | 0.11444 | 3.978 | -0.013733 | 0.21515 | 0.027466 | 123.1293 | 122.7264 | 52.2903 | -123.1293 | 123.0835 | 122.9965 | 85.8215 | -123.1979
3730.0156 | 123.0606 | -46.0419 | 76.9272 | -0.22141 | 0.011722 | 0.072523 | 0.070944 | 0.12822 | 0.00013675 | -0.0089999 | -0.168 | -0.010408 | 0.067468 | 0.057185 | 0.0084808 | -0.013469 | 76.6708 | 76.8906 | 5.8777 | -45.8954 | 77.037 | -46.0968 | -46.2112 | -42.0547 | 39.7934 | -46.051 | 77.0233 | 76.9592 | -46.2524 | -46.2799 | -0.054932 | -0.16937 | 0.10986 | 122.9324 | 0.14648 | 0.31586 | -0.25635 | -0.21057 | -0.23804 | 0.09613 | 3.9871 | -0.009155 | 0.22888 | 0.032044 | 123.0789 | 122.7127 | 51.9196 | -123.1384 | 123.0652 | 123.0011 | 85.8353 | -123.2071
3731.0156 | 123.0652 | -46.3486 | 76.593 | -0.23666 | 0.015567 | 0.0706 | 0.076498 | 0.13099 | 0.0020593 | -0.0075047 | -0.18326 | -0.0076306 | 0.066828 | 0.059748 | 0.0097626 | -0.011974 | 76.3458 | 76.5152 | 5.6946 | -46.1929 | 76.7578 | -46.4355 | -46.5179 | -42.421 | 39.6606 | -46.4584 | 76.6846 | 76.5884 | -46.5912 | -46.6415 | -0.086975 | -0.16937 | 0.16479 | 122.8638 | 0.15564 | 0.32501 | -0.24719 | -0.24262 | -0.29297 | 0.091552 | 3.9276 | -0.10986 | 0.18311 | -0.004578 | 123.1064 | 122.6944 | 52.0432 | -123.111 | 123.0331 | 122.937 | 86.0092 | -123.2346
3732.0156 | 123.0835 | -46.8246 | 76.2039 | -0.12985 | 0.014499 | 0.073591 | 0.07479 | 0.12993 | 0.00035035 | -0.010282 | -0.18326 | -0.0089124 | 0.067041 | 0.058253 | 0.01019 | -0.012614 | 75.9109 | 76.1261 | 5.7587 | -46.637 | 76.3138 | -46.8475 | -46.9482 | -42.8467 | 39.1296 | -46.9849 | 76.2726 | 76.1261 | -47.0535 | -47.0901 | -0.022888 | -0.1236 | 0.10986 | 122.9507 | 0.18768 | 0.31128 | -0.29297 | -0.22888 | -0.2655 | 0.068665 | 3.978 | -0.16022 | 0.10529 | -0.077819 | 123.1384 | 122.7356 | 52.5833 | -123.1522 | 123.0972 | 122.9507 | 85.9543 | -123.2941
3733.0312 | 123.0652 | -46.2341 | 76.712 | -0.10696 | 0.02048 | 0.07295 | 0.073081 | 0.12629 | 0.0056909 | -0.0066501 | -0.10696 | -0.00464 | 0.067682 | 0.055689 | 0.011899 | -0.014537 | 76.4877 | 76.68 | 5.8868 | -46.0739 | 76.8356 | -46.3165 | -46.4035 | -42.2195 | 39.7659 | -46.3074 | 76.8219 | 76.7258 | -46.4081 | -46.4813 | -0.082397 | -0.16937 | 0.1236 | 122.9141 | 0.16022 | 0.32959 | -0.2243 | -0.17395 | -0.24719 | 0.10986 | 4.0146 | -0.073242 | 0.17395 | 0.013733 | 123.0698 | 122.7219 | 52.121 | -123.1155 | 123.056 | 122.9599 | 86.0001 | -123.1934
3734.0156 | 123.0194 | -46.0419 | 76.9409 | -0.25192 | 0.015567 | 0.0706 | 0.073081 | 0.1295 | -0.00071785 | -0.0085727 | -0.52658 | -0.010194 | 0.070246 | 0.057185 | 0.0099762 | -0.011333 | 76.6708 | 76.8585 | 5.7175 | -45.6573 | 77.1378 | -46.051 | -46.1472 | -42.0685 | 39.9033 | -46.1472 | 77.0508 | 76.9547 | -46.2479 | -46.2753 | -0.009155 | -0.10529 | 0.19684 | 122.9004 | 0.38452 | 0.48981 | -0.27008 | -0.20599 | -0.23346 | 0.10986 | 3.9734 | -0.10529 | 0.12817 | 0.013733 | 123.1796 | 122.7127 | 51.7593 | -123.0881 | 123.0927 | 122.9965 | 85.9451 | -123.2162
3735.0156 | 123.1476 | -46.756 | 76.1536 | -0.40451 | 0.0097989 | 0.0706 | 0.074362 | 0.12993 | -0.0015723 | -0.0075047 | -0.084076 | -0.011262 | 0.064691 | 0.055262 | 0.0086944 | -0.011333 | 75.9338 | 76.2177 | 5.9418 | -46.5912 | 76.2772 | -46.8246 | -46.9254 | -42.7094 | 39.386 | -46.7789 | 76.1902 | 76.0986 | -46.9711 | -47.0215 | -0.068665 | -0.16937 | 0.1236 | 122.9736 | 0.16479 | 0.33417 | -0.21973 | -0.21515 | -0.2655 | 0.036622 | 4.0466 | -0.022889 | 0.24261 | -0.054931 | 123.0331 | 122.6898 | 52.6978 | -123.0789 | 122.9462 | 122.8546 | 86.142 | -123.175
3736.0156 | 123.1705 | -46.0464 | 76.8127 | -2.2432 | 0.012149 | 0.069959 | 0.072012 | 0.12886 | -0.0017859 | -0.0070773 | -0.076446 | -0.010621 | 0.066828 | 0.05868 | 0.010403 | -0.011546 | 76.593 | 77.0279 | 6.102 | -45.8542 | 77.0279 | -46.0785 | -46.17 | -41.954 | 40.0452 | -46.051 | 76.9867 | 76.8539 | -46.225 | -46.2662 | -0.032043 | -0.1236 | 0.21515 | 123.0743 | 0.19226 | 0.31586 | -0.21973 | -0.17853 | -0.21973 | 0.17395 | 4.0924 | -0.004577 | 0.21515 | 0.041199 | 123.0743 | 122.6395 | 52.1484 | -122.9828 | 123.0331 | 122.9004 | 86.0916 | -123.0789
3737.0156 | 123.0286 | -45.8359 | 77.1515 | -1.3887 | 0.013217 | 0.069532 | 0.072226 | 0.12715 | 0.00077755 | -0.0077183 | -0.14511 | -0.008058 | 0.068964 | 0.058894 | 0.0097626 | -0.015178 | 76.8356 | 77.0325 | 6.0471 | -45.7169 | 77.2614 | -45.9183 | -46.019 | -41.8259 | 40.1505 | -45.8908 | 77.2751 | 77.124 | -46.0327 | -46.0693 | -0.082398 | -0.18311 | 0.10986 | 122.8683 | 0.11902 | 0.30212 | -0.31586 | -0.19684 | -0.23346 | 0.1236 | 4.01 | -0.054932 | 0.17853 | -0.027466 | 123.0972 | 122.6715 | 51.8829 | -123.1705 | 123.111 | 122.9599 | 85.9863 | -123.2208
3738.0469 | 123.0148 | -46.2341 | 76.7395 | 0.022736 | 0.018558 | 0.073164 | 0.075217 | 0.13099 | 0.0048363 | -0.0028049 | 0.037995 | -0.0084852 | 0.069391 | 0.057826 | 0.014249 | -0.014323 | 76.506 | 76.6891 | 6.0974 | -46.0922 | 76.9043 | -46.2891 | -46.3852 | -42.2241 | 39.7751 | -46.3303 | 76.8036 | 76.7303 | -46.4447 | -46.4905 | -0.054931 | -0.15106 | 0.16479 | 122.9233 | 0.14191 | 0.29297 | -0.23346 | -0.21057 | -0.25635 | 0.064087 | 4.01 | -0.09613 | 0.16022 | -0.009155 | 123.1384 | 122.7402 | 52.3315 | -123.1247 | 123.0377 | 122.9645 | 86.0092 | -123.23
3739.0156 | 123.0515 | -46.6553 | 76.2817 | -0.22903 | 0.011081 | 0.069746 | 0.073721 | 0.12907 | -0.0026405 | -0.0087863 | -0.12985 | -0.0093396 | 0.067468 | 0.056544 | 0.0074126 | -0.011546 | 76.1078 | 76.3275 | 5.9555 | -46.4493 | 76.4282 | -46.7056 | -46.7926 | -42.6224 | 39.4867 | -46.7422 | 76.3733 | 76.3138 | -46.8613 | -46.9162 | -0.050354 | -0.13733 | 0.14648 | 122.9828 | 0.20599 | 0.34332 | -0.17395 | -0.20599 | -0.26093 | 0.091553 | 4.0329 | -0.086976 | 0.17395 | 0.032044 | 123.0835 | 122.7631 | 52.6108 | -123.0743 | 123.0286 | 122.9691 | 86.142 | -123.1979
3740.0156 | 123.0469 | -46.4493 | 76.5152 | -0.23666 | 0.011722 | 0.073377 | 0.072012 | 0.12971 | -0.0026405 | -0.0070773 | -0.12985 | -0.010835 | 0.066614 | 0.057612 | 0.0097626 | -0.011546 | 76.2726 | 76.506 | 6.1111 | -46.2936 | 76.5839 | -46.5225 | -46.6324 | -42.4118 | 39.7614 | -46.4676 | 76.593 | 76.4969 | -46.6599 | -46.6873 | -0.073242 | -0.1831 | 0.068664 | 122.9553 | 0.15564 | 0.33874 | -0.24262 | -0.21057 | -0.23804 | 0.07782 | 4.0375 | -0.01831 | 0.21973 | -0.018311 | 123.0331 | 122.7219 | 52.5604 | -123.1476 | 123.0423 | 122.9462 | 86.2106 | -123.2025
3741.0156 | 123.0743 | -45.9045 | 77.0508 | -0.061188 | 0.016635 | 0.071668 | 0.074149 | 0.13057 | 0.0024865 | -0.0098545 | -0.22903 | -0.0069898 | 0.066614 | 0.057612 | 0.013608 | -0.013683 | 76.7715 | 76.9821 | 5.9418 | -45.7581 | 77.2064 | -45.9686 | -46.0739 | -41.8442 | 40.1962 | -45.9 | 77.1835 | 77.0691 | -46.0968 | -46.1563 | -0.064087 | -0.16937 | 0.15564 | 122.8867 | 0.14648 | 0.31586 | -0.27924 | -0.19226 | -0.25177 | 0.13275 | 4.0604 | 0.004578 | 0.25635 | 0.018311 | 123.111 | 122.6761 | 51.8463 | -123.1247 | 123.0881 | 122.9736 | 86.1008 | -123.2071
3742.0156 | 123.0423 | -46.6873 | 76.2588 | -0.23666 | 0.013217 | 0.072096 | 0.072653 | 0.12907 | -0.00071785 | -0.0089999 | -0.18326 | -0.010621 | 0.065332 | 0.059107 | 0.0097626 | -0.01176 | 75.9293 | 76.1124 | 5.8731 | -46.6095 | 76.3275 | -46.8384 | -46.9528 | -42.6544 | 39.5645 | -46.7422 | 76.3962 | 76.2726 | -46.9391 | -46.9345 | -0.15106 | -0.2655 | 0.068665 | 122.7997 | 0.07782 | 0.34332 | -0.32959 | -0.25177 | -0.24719 | 0.13733 | 4.0329 | -0.054932 | 0.19226 | 0.013733 | 123.0148 | 122.6166 | 52.5604 | -123.2117 | 123.0835 | 122.9599 | 86.2518 | -123.1934
3743.0312 | 123.0927 | -45.7352 | 77.2247 | -0.22141 | 0.016849 | 0.070173 | 0.075003 | 0.12864 | 0.0031273 | -0.0070773 | -0.16037 | -0.0086988 | 0.065973 | 0.057612 | 0.011685 | -0.013042 | 76.9684 | 77.179 | 5.9006 | -45.5887 | 77.3666 | -45.7901 | -45.9274 | -41.6611 | 40.5579 | -45.7123 | 77.3117 | 77.1927 | -45.9503 | -45.9778 | -0.054932 | -0.19226 | 0.14191 | 122.9141 | 0.14648 | 0.33874 | -0.25635 | -0.21515 | -0.24262 | 0.086976 | 4.0741 | 0.022888 | 0.2655 | -0.032043 | 123.1018 | 122.7036 | 51.6357 | -123.1522 | 123.0469 | 122.9279 | 86.293 | -123.2025
3744.0156 | 123.1476 | -46.7834 | 76.0941 | -0.19852 | 0.012149 | 0.072096 | 0.071799 | 0.12907 | -0.0041357 | -0.0081455 | 0.73227 | -0.0089124 | 0.067896 | 0.057398 | 0.010403 | -0.012614 | 75.9155 | 76.4099 | 6.0242 | -46.5866 | 76.2497 | -46.8842 | -46.9894 | -42.6773 | 39.7476 | -46.756 | 76.1765 | 76.1078 | -47.0398 | -47.0215 | -0.10071 | -0.20599 | 0.15564 | 123.1934 | 0.19684 | 0.40283 | -0.17853 | -0.25635 | -0.23804 | 0.082398 | 4.1061 | 0.027466 | 0.2655 | 0.013733 | 123.0331 | 122.699 | 52.8076 | -123.0835 | 122.9599 | 122.8912 | 86.5311 | -123.1155
3745.0156 | 123.0606 | -46.7102 | 76.236 | -1.7931 | 0.01279 | 0.071241 | 0.072867 | 0.12907 | 0.00077755 | -0.0083591 | -0.10696 | -0.010621 | 0.065546 | 0.056971 | 0.0093354 | -0.014537 | 75.9796 | 76.1353 | 5.8228 | -46.5546 | 76.3962 | -46.7972 | -46.8658 | -42.6178 | 39.7934 | -46.7926 | 76.4099 | 76.2588 | -46.9162 | -46.9482 | -0.086975 | -0.15564 | 0.16022 | 122.8455 | 0.15564 | 0.31128 | -0.25635 | -0.20599 | -0.23804 | 0.17395 | 4.0924 | -0.082398 | 0.15564 | 0.022888 | 123.1064 | 122.6898 | 52.533 | -123.1018 | 123.1201 | 122.9691 | 86.5036 | -123.1842
3746.0156 | 123.0057 | -47.0856 | 75.8835 | -0.24429 | 0.012362 | 0.072523 | 0.073294 | 0.13099 | 0.0018457 | -0.0072911 | -0.0077819 | -0.010835 | 0.067041 | 0.055049 | 0.01019 | -0.01176 | 75.5997 | 75.8194 | 5.777 | -46.9849 | 76.0162 | -47.1359 | -47.2504 | -43.0023 | 39.4775 | -47.1268 | 75.9842 | 75.8835 | -47.3007 | -47.3236 | -0.050354 | -0.16479 | 0.13275 | 122.905 | 0.10071 | 0.2655 | -0.28381 | -0.21515 | -0.23804 | 0.10071 | 4.0833 | -0.041199 | 0.19684 | 0 | 123.1018 | 122.6852 | 52.8625 | -123.1338 | 123.0698 | 122.9691 | 86.5631 | -123.2071
3747.0156 | 123.0423 | -46.6232 | 76.3367 | -0.25192 | 0.015567 | 0.073591 | 0.075644 | 0.12971 | 0.0024865 | -0.0051547 | -0.22903 | -0.0097668 | 0.067682 | 0.055476 | 0.0099762 | -0.013255 | 75.9659 | 76.4053 | 5.9006 | -46.4264 | 76.5701 | -46.6415 | -46.7239 | -42.5125 | 39.9811 | -46.6507 | 76.5198 | 76.3916 | -46.8292 | -46.8475 | -0.018311 | -0.10071 | 0.23346 | 123.0286 | 0.19684 | 0.29755 | -0.37079 | -0.20599 | -0.2243 | 0.1831 | 4.1107 | -0.027466 | 0.19684 | 0.054932 | 123.1934 | 122.5891 | 52.5238 | -123.0606 | 123.143 | 123.0148 | 86.6043 | -123.1842
3748.0312 | 123.0698 | -46.5042 | 76.4282 | -0.22903 | 0.019626 | 0.071455 | 0.075644 | 0.13014 | 0.0039819 | -0.0085727 | -0.19089 | -0.0089124 | 0.067468 | 0.056758 | 0.0097626 | -0.013683 | 76.181 | 76.4008 | 5.8685 | -46.3211 | 76.6022 | -46.5729 | -46.6965 | -42.421 | 40.0406 | -46.5729 | 76.5244 | 76.442 | -46.7285 | -46.7789 | -0.068665 | -0.19226 | 0.17395 | 122.905 | 0.1831 | 0.37537 | -0.24719 | -0.22431 | -0.27466 | 0.09613 | 4.0833 | -0.068665 | 0.20599 | 0.013733 | 123.1064 | 122.6852 | 52.3727 | -123.1247 | 123.0286 | 122.9462 | 86.5448 | -123.2071
3749.0156 | 123.0743 | -46.6049 | 76.3779 | -1.3811 | 0.021335 | 0.070173 | 0.075644 | 0.13078 | 0.0035547 | -0.0055821 | -0.03067 | -0.0069898 | 0.069391 | 0.057826 | 0.013608 | -0.013042 | 76.1856 | 76.3229 | 5.8411 | -46.4127 | 76.4603 | -46.6599 | -46.7422 | -42.453 | 39.9719 | -46.6782 | 76.4328 | 76.3504 | -46.8109 | -46.8292 | -0.054932 | -0.13733 | 0.082397 | 122.9279 | 0.19226 | 0.32959 | -0.19226 | -0.20599 | -0.22431 | 0.054931 | 4.1519 | -0.073243 | 0.15106 | -0.027466 | 123.0652 | 122.7905 | 52.446 | -123.1201 | 123.0377 | 122.9553 | 86.5768 | -123.2071
3750.0156 | 123.0743 | -46.6965 | 76.2726 | -0.21378 | 0.018344 | 0.071455 | 0.072867 | 0.12971 | 0.0014185 | -0.0057957 | -0.16037 | -0.0097668 | 0.067682 | 0.059107 | 0.010617 | -0.013683 | 75.9705 | 76.1719 | 5.8914 | -46.5225 | 76.4008 | -46.7697 | -46.8613 | -42.5995 | 39.8849 | -46.8246 | 76.3321 | 76.2543 | -46.9162 | -46.9482 | -0.073242 | -0.16479 | 0.12817 | 122.8683 | 0.17395 | 0.33874 | -0.30212 | -0.21973 | -0.25177 | 0.059509 | 4.097 | -0.12817 | 0.1236 | -0.018311 | 123.0972 | 122.6669 | 52.5879 | -123.1338 | 123.0286 | 122.9507 | 86.5814 | -123.2208
3751.0156 | 123.024 | -46.3211 | 76.6388 | -0.18326 | 0.014712 | 0.073377 | 0.07479 | 0.12928 | 0.00013675 | -0.0083591 | 0.32028 | -0.0093396 | 0.067682 | 0.057185 | 0.00784 | -0.011333 | 76.3916 | 76.8631 | 6.2439 | -46.1105 | 76.8723 | -46.3028 | -46.4218 | -42.247 | 40.242 | -46.4355 | 76.767 | 76.6434 | -46.5591 | -46.5546 | 0.018311 | -0.10071 | 0.23346 | 123.1842 | 0.21057 | 0.31128 | -0.24719 | -0.23804 | -0.23346 | 0.12817 | 4.0741 | -0.11444 | 0.11902 | 0.004578 | 123.1934 | 122.7127 | 52.565 | -123.0606 | 123.0881 | 122.9645 | 86.5631 | -123.1934
3752.0156 | 123.0148 | -47.1497 | 75.8286 | -0.23666 | 0.010867 | 0.072523 | 0.073294 | 0.12886 | -0.0019995 | -0.0060093 | -0.091705 | -0.011689 | 0.065546 | 0.058253 | 0.0093354 | -0.010905 | 75.5173 | 75.7828 | 5.658 | -46.9574 | 75.8972 | -47.2275 | -47.3328 | -43.0161 | 39.6652 | -47.1359 | 75.9018 | 75.7919 | -47.3602 | -47.3785 | -0.07782 | -0.18311 | 0.068665 | 122.9324 | 0.19226 | 0.37537 | -0.31128 | -0.21057 | -0.22888 | 0.073242 | 4.1336 | 0.013733 | 0.24262 | -0.036621 | 123.0469 | 122.6669 | 52.8076 | -123.1613 | 123.0515 | 122.9416 | 86.8149 | -123.2071
3753.0156 | 123.0057 | -46.8796 | 76.0941 | 0.037994 | 0.021335 | 0.070173 | 0.075858 | 0.12928 | 0.0071863 | -0.0057957 | 0.0914 | -0.0084852 | 0.069391 | 0.05868 | 0.011472 | -0.011333 | 75.7874 | 75.9888 | 5.365 | -46.7148 | 76.2497 | -46.9299 | -47.0398 | -42.746 | 39.8346 | -46.9849 | 76.2268 | 76.0941 | -47.0627 | -47.1222 | -0.050354 | -0.16022 | 0.15564 | 122.8683 | 0.1648 | 0.32501 | -0.3067 | -0.1831 | -0.24261 | 0.13275 | 4.1336 | -0.10528 | 0.13733 | 0 | 123.1293 | 122.6669 | 52.2446 | -123.1338 | 123.1064 | 122.9736 | 86.7142 | -123.2162
3754.0156 | 123.1476 | -46.8018 | 76.0803 | -0.25192 | 0.012149 | 0.071882 | 0.074149 | 0.13014 | -0.0019995 | -0.010282 | -0.099335 | -0.011049 | 0.064264 | 0.05633 | 0.0086944 | -0.011333 | 75.8331 | 76.1261 | 5.5481 | -46.6461 | 76.1719 | -46.9299 | -47.0581 | -42.6178 | 40.0223 | -46.8063 | 76.1536 | 76.0849 | -47.0306 | -47.0581 | -0.12817 | -0.25635 | 0.091553 | 122.9279 | 0.15564 | 0.41199 | -0.24719 | -0.22888 | -0.25635 | 0.073242 | 4.184 | -0.004577 | 0.25177 | 0.004578 | 122.9736 | 122.6349 | 52.3499 | -123.1384 | 122.9553 | 122.8867 | 86.824 | -123.1384
3755.0156 | 123.0377 | -46.9528 | 76.0208 | -0.19089 | 0.01514 | 0.073591 | 0.076071 | 0.1295 | 0.0022729 | -0.0072911 | 0.81619 | -0.0086988 | 0.066614 | 0.055903 | 0.0093354 | -0.010905 | 75.5585 | 75.7828 | 5.4016 | -46.9299 | 76.0071 | -47.1725 | -47.3099 | -42.8192 | 39.8712 | -47.0215 | 76.1215 | 75.9979 | -47.1497 | -47.1817 | -0.21973 | -0.35705 | -0.013733 | 122.7356 | 0.022888 | 0.37994 | -0.46234 | -0.19684 | -0.22888 | 0.10071 | 4.1336 | -0.068664 | 0.16022 | -0.022888 | 122.9599 | 122.5113 | 52.3544 | -123.3307 | 123.0743 | 122.9507 | 86.824 | -123.2025
3756.0156 | 123.111 | -47.3282 | 75.563 | -0.38925 | 0.011294 | 0.072736 | 0.071585 | 0.12886 | -0.0028541 | -0.010068 | -0.12222 | -0.011262 | 0.066614 | 0.057612 | 0.0067718 | -0.010905 | 75.3616 | 75.6409 | 5.5252 | -47.1359 | 75.6775 | -47.4243 | -47.5296 | -43.1076 | 39.5554 | -47.3145 | 75.6638 | 75.5539 | -47.5571 | -47.5983 | -0.09613 | -0.20142 | 0.11444 | 122.9691 | 0.19226 | 0.39368 | -0.20142 | -0.22888 | -0.27008 | 0.10071 | 4.2206 | 0.013733 | 0.28381 | -0.009155 | 123.0057 | 122.6898 | 52.8534 | -123.0927 | 122.9919 | 122.8821 | 86.8835 | -123.1613
3757.0156 | 123.0606 | -47.8729 | 75.1099 | -0.19852 | 0.013644 | 0.071027 | 0.074149 | 0.12993 | 0.0039819 | -0.0064365 | -0.13748 | -0.0099806 | 0.067682 | 0.058039 | 0.011258 | -0.015605 | 74.7803 | 74.9405 | 5.1498 | -47.7264 | 75.1648 | -47.9874 | -48.0606 | -43.7302 | 39.0564 | -47.9691 | 75.1694 | 75.0687 | -48.0835 | -48.1247 | -0.11444 | -0.18768 | 0.054932 | 122.8134 | 0.14649 | 0.33417 | -0.32959 | -0.21057 | -0.25177 | 0.05951 | 4.1428 | -0.09613 | 0.15564 | -0.041198 | 123.0377 | 122.6532 | 53.0228 | -123.1705 | 123.0423 | 122.9416 | 86.9293 | -123.2346
3758.0156 | 123.056 | -46.7148 | 76.2085 | 0.15244 | 0.024325 | 0.069746 | 0.075003 | 0.12907 | 0.0022729 | -0.0045139 | 0.0914 | -0.008058 | 0.071741 | 0.059321 | 0.008908 | -0.013896 | 75.8743 | 76.3092 | 5.4428 | -46.5363 | 76.4328 | -46.7285 | -46.8567 | -42.4759 | 40.1047 | -46.7743 | 76.4008 | 76.2772 | -46.907 | -46.9254 | -0.013733 | -0.14191 | 0.2243 | 123.024 | 0.17853 | 0.32043 | -0.33417 | -0.19226 | -0.21057 | 0.19226 | 4.2389 | -0.059509 | 0.15106 | 0.068665 | 123.1476 | 122.5891 | 52.1576 | -123.0652 | 123.1155 | 122.9919 | 86.8195 | -123.1338
3759.0156 | 123.0743 | -46.5317 | 76.4282 | -0.18326 | 0.016849 | 0.071241 | 0.075644 | 0.13078 | 0.0014185 | -0.0096409 | -0.18326 | -0.0084852 | 0.068109 | 0.05868 | 0.010617 | -0.011119 | 76.1948 | 76.3916 | 5.3284 | -46.312 | 76.6068 | -46.5546 | -46.6553 | -42.3157 | 40.3244 | -46.6553 | 76.5198 | 76.4374 | -46.7514 | -46.7834 | -0.022888 | -0.1236 | 0.17853 | 122.9233 | 0.21973 | 0.34332 | -0.23346 | -0.21973 | -0.25177 | 0.091552 | 4.216 | -0.1236 | 0.12817 | 0.009155 | 123.1384 | 122.7264 | 51.86 | -123.0835 | 123.0515 | 122.9691 | 86.8561 | -123.2117
3760.0156 | 122.9828 | -46.1746 | 76.7944 | -0.21378 | 0.014712 | 0.073591 | 0.075217 | 0.12715 | 0.0014185 | -0.0072911 | -0.16037 | -0.0095532 | 0.068323 | 0.054408 | 0.011044 | -0.0098374 | 76.474 | 76.6983 | 5.452 | -46.0281 | 76.9272 | -46.2524 | -46.3715 | -42.0547 | 40.5579 | -46.1838 | 76.9043 | 76.8036 | -46.3989 | -46.4172 | -0.077819 | -0.19684 | 0.13275 | 122.8729 | 0.14648 | 0.34332 | -0.32043 | -0.2243 | -0.24261 | 0.10986 | 4.1199 | -0.009155 | 0.23346 | 0.009155 | 123.1018 | 122.6486 | 51.6266 | -123.1659 | 123.0789 | 122.9782 | 86.7325 | -123.2117
3761.0156 | 123.0927 | -45.9 | 77.0554 | -0.19089 | 0.018344 | 0.071455 | 0.075644 | 0.12864 | 0.0037683 | -0.0075047 | -0.168 | -0.0086988 | 0.067896 | 0.057826 | 0.012112 | -0.013042 | 76.8082 | 77.005 | 5.6854 | -45.6802 | 77.1973 | -45.9641 | -46.0602 | -41.684 | 40.9058 | -45.9595 | 77.1423 | 77.0325 | -46.1197 | -46.17 | -0.064087 | -0.16022 | 0.14191 | 122.905 | 0.21973 | 0.37994 | -0.24719 | -0.21973 | -0.27008 | 0.086975 | 4.216 | -0.05951 | 0.21057 | -0.022888 | 123.0972 | 122.7081 | 51.5854 | -123.1155 | 123.0423 | 122.9324 | 86.8057 | -123.2254
3762.0156 | 123.0515 | -46.4355 | 76.5427 | -0.18326 | 0.014071 | 0.073591 | 0.072653 | 0.13035 | -0.0011451 | -0.0075047 | -1.8388 | -0.0089124 | 0.068323 | 0.057612 | 0.0097626 | -0.011546 | 76.1581 | 76.3916 | 5.484 | -46.312 | 76.5976 | -46.5591 | -46.6644 | -42.1829 | 40.4755 | -46.4859 | 76.6205 | 76.5198 | -46.6553 | -46.6782 | -0.1236 | -0.22888 | 0.054931 | 122.8271 | 0.1236 | 0.35248 | -0.38452 | -0.21973 | -0.24262 | 0.077819 | 4.2526 | -0.050354 | 0.19226 | -0.022889 | 123.0331 | 122.5937 | 51.9196 | -123.2071 | 123.056 | 122.9553 | 86.911 | -123.2208
3763.0156 | 123.0331 | -46.2753 | 76.7441 | 0.053253 | 0.020053 | 0.069532 | 0.07479 | 0.12928 | 0.0054773 | -0.0066501 | 0.11429 | -0.0086988 | 0.069818 | 0.059321 | 0.013821 | -0.010692 | 76.3916 | 76.5839 | 5.5664 | -46.0922 | 76.8768 | -46.3211 | -46.4127 | -42.0639 | 40.7272 | -46.3531 | 76.8356 | 76.7075 | -46.4447 | -46.4676 | -0.045776 | -0.13733 | 0.13275 | 122.8592 | 0.18311 | 0.32043 | -0.35248 | -0.16937 | -0.19226 | 0.091552 | 4.2114 | -0.077819 | 0.11444 | -0.036622 | 123.1522 | 122.6669 | 51.8417 | -123.1567 | 123.111 | 122.9828 | 87.0026 | -123.2117
3764.0156 | 123.0057 | -46.5363 | 76.4145 | -0.25192 | 0.012576 | 0.073377 | 0.073081 | 0.12864 | -0.0030677 | -0.0051547 | -0.11459 | -0.010621 | 0.06875 | 0.057826 | 0.011044 | -0.0091966 | 76.1856 | 76.4236 | 5.5801 | -46.2891 | 76.561 | -46.5591 | -46.6553 | -42.3019 | 40.5716 | -46.5958 | 76.5244 | 76.4511 | -46.7468 | -46.7697 | -0.022888 | -0.11902 | 0.14648 | 122.9599 | 0.24719 | 0.36621 | -0.22888 | -0.21057 | -0.23346 | 0.10986 | 4.2343 | -0.059509 | 0.17395 | 0.036621 | 123.0972 | 122.7219 | 52.1164 | -123.0698 | 123.0606 | 122.9874 | 87.1078 | -123.1842
3765.0156 | 123.0972 | -47.0215 | 75.9338 | -0.17563 | 0.021762 | 0.0706 | 0.075217 | 0.13078 | 0.0044091 | -0.0068637 | -0.20615 | -0.008058 | 0.067041 | 0.058894 | 0.013394 | -0.013042 | 75.7004 | 75.8926 | 5.4886 | -46.788 | 76.062 | -47.113 | -47.2183 | -42.8055 | 40.0955 | -47.0993 | 75.9796 | 75.9018 | -47.2458 | -47.2778 | -0.091553 | -0.19684 | 0.12817 | 122.9141 | 0.23346 | 0.4303 | -0.23346 | -0.22431 | -0.25635 | 0.045776 | 4.216 | -0.07782 | 0.17853 | -0.032044 | 123.0835 | 122.7219 | 52.5101 | -123.1522 | 123.0011 | 122.9233 | 87.117 | -123.2117
3766.0156 | 123.0515 | -46.6187 | 76.3275 | -0.23666 | 0.017917 | 0.0706 | 0.071799 | 0.12822 | 0.0027001 | -0.0064365 | -0.17563 | -0.0076306 | 0.069391 | 0.055689 | 0.011899 | -0.013469 | 76.0529 | 76.181 | 5.4245 | -46.4447 | 76.4236 | -46.7651 | -46.8338 | -42.4072 | 40.535 | -46.6827 | 76.4145 | 76.3275 | -46.843 | -46.8658 | -0.14649 | -0.21515 | 0.09613 | 122.7997 | 0.17395 | 0.3891 | -0.27466 | -0.22431 | -0.24719 | 0.086975 | 4.2114 | -0.064087 | 0.18311 | 0 | 123.0423 | 122.6715 | 52.0432 | -123.1613 | 123.0331 | 122.9462 | 87.1536 | -123.1934
3767.0156 | 123.0515 | -46.0327 | 76.9547 | 0.045624 | 0.018985 | 0.069959 | 0.075003 | 0.12907 | 0.0041955 | -0.0060093 | 0.037995 | -0.0061352 | 0.070886 | 0.059107 | 0.012753 | -0.01176 | 76.6617 | 76.8356 | 5.6488 | -45.9412 | 77.0508 | -46.1105 | -46.2387 | -41.8121 | 40.9973 | -46.0602 | 77.0142 | 76.9272 | -46.2433 | -46.2616 | -0.07782 | -0.20599 | 0.09613 | 122.8683 | 0.091553 | 0.29755 | -0.29297 | -0.21057 | -0.22888 | 0.059509 | 4.2206 | -0.027466 | 0.20142 | -0.027466 | 123.0835 | 122.6944 | 51.6815 | -123.1934 | 123.0469 | 122.9599 | 87.03 | -123.2162
3768.0156 | 123.0286 | -45.845 | 77.124 | 0.33554 | 0.019412 | 0.070814 | 0.070303 | 0.12993 | 0.0037683 | -0.0075047 | 0.19058 | -0.0093396 | 0.069605 | 0.059107 | 0.010617 | -0.011546 | 76.8539 | 76.9592 | 5.7587 | -45.694 | 77.2156 | -45.9412 | -46.051 | -41.5878 | 41.2308 | -45.8862 | 77.2247 | 77.1561 | -46.0648 | -46.051 | -0.09613 | -0.20599 | 0.091553 | 122.8043 | 0.15106 | 0.35706 | -0.27008 | -0.21973 | -0.20599 | 0.10071 | 4.2572 | -0.041198 | 0.1648 | 0.032044 | 123.0606 | 122.699 | 51.6037 | -123.175 | 123.0698 | 123.0011 | 87.0758 | -123.175
3769.0156 | 123.0743 | -46.2845 | 76.6937 | -0.17563 | 0.017062 | 0.0706 | 0.073935 | 0.12928 | 0.0012047 | -0.0085727 | -0.16037 | -0.0084852 | 0.065973 | 0.057826 | 0.010831 | -0.011333 | 76.4282 | 76.5747 | 5.6351 | -46.0327 | 76.8173 | -46.3348 | -46.463 | -42.0319 | 40.947 | -46.344 | 76.7761 | 76.6937 | -46.4996 | -46.4996 | -0.050354 | -0.17853 | 0.1236 | 122.8592 | 0.25177 | 0.4303 | -0.2655 | -0.21515 | -0.21515 | 0.082397 | 4.2526 | -0.059509 | 0.15564 | 0 | 123.1018 | 122.7127 | 51.9196 | -123.1567 | 123.0606 | 122.9782 | 87.2314 | -123.1934
3770.0156 | 123.0469 | -46.1288 | 76.8219 | -0.15274 | 0.014926 | 0.072523 | 0.075003 | 0.12886 | 0.00056395 | -0.0066501 | -0.19089 | -0.011049 | 0.068323 | 0.057826 | 0.011044 | -0.011333 | 76.5198 | 76.7166 | 5.7632 | -45.9091 | 76.9547 | -46.2204 | -46.3669 | -41.8991 | 41.0614 | -46.2296 | 76.9089 | 76.8311 | -46.3715 | -46.3898 | -0.091553 | -0.23804 | 0.13275 | 122.8455 | 0.21973 | 0.45776 | -0.30212 | -0.24262 | -0.26093 | 0.086976 | 4.2297 | -0.10071 | 0.16022 | 0.009156 | 123.0835 | 122.6486 | 51.8921 | -123.1888 | 123.0377 | 122.9599 | 87.1902 | -123.2117
3771.0156 | 123.0881 | -46.4996 | 76.4648 | -0.0383 | 0.020267 | 0.071882 | 0.076071 | 0.12822 | 0.0031273 | -0.0089999 | -0.11459 | -0.0078442 | 0.067255 | 0.05868 | 0.013608 | -0.013042 | 76.4008 | 76.4053 | 5.7495 | -46.2433 | 76.5976 | -46.5454 | -46.6507 | -42.1555 | 40.6723 | -46.5271 | 76.5518 | 76.4465 | -46.7011 | -46.7102 | -0.045776 | -0.15106 | 0.13275 | 122.905 | 0.25635 | 0.40741 | -0.064087 | -0.20142 | -0.21057 | 0.086975 | 4.3442 | -0.027466 | 0.18311 | -0.018311 | 123.0972 | 122.9004 | 52.2491 | -123.1155 | 123.0515 | 122.9462 | 87.1719 | -123.175
3772.0156 | 123.0377 | -45.8862 | 77.0782 | -0.22903 | 0.013217 | 0.073591 | 0.075003 | 0.12843 | -0.0015723 | -0.0077183 | -0.75546 | -0.0082716 | 0.067896 | 0.056758 | 0.0093354 | -0.0098374 | 76.7761 | 76.9959 | 5.6946 | -45.6894 | 77.2064 | -45.9595 | -46.0648 | -41.6061 | 41.2033 | -45.8817 | 77.2202 | 77.0966 | -46.0831 | -46.1243 | -0.073243 | -0.17853 | 0.12817 | 122.8821 | 0.19684 | 0.37537 | -0.30212 | -0.19684 | -0.23804 | 0.14191 | 4.2801 | 0.004577 | 0.24262 | 0.018311 | 123.0927 | 122.6624 | 51.5808 | -123.143 | 123.1064 | 122.9828 | 87.0895 | -123.2025
3773.0156 | 123.0789 | -46.344 | 76.5244 | 0.083771 | 0.016421 | 0.07295 | 0.071372 | 0.128 | 0.0014185 | -0.0092137 | 0.25162 | -0.011476 | 0.067468 | 0.059107 | 0.0099762 | -0.011546 | 76.4603 | 76.6251 | 5.809 | -46.0007 | 76.7303 | -46.3715 | -46.431 | -41.9128 | 40.9653 | -46.2845 | 76.6846 | 76.6022 | -46.5271 | -46.5546 | -0.027466 | -0.086975 | 0.20599 | 122.9691 | 0.34332 | 0.4303 | -0.064087 | -0.18311 | -0.21057 | 0.16022 | 4.4312 | 0.059509 | 0.27008 | 0.07782 | 123.0743 | 122.8043 | 52.153 | -122.9553 | 123.0286 | 122.9462 | 87.3093 | -123.0789
3774.0156 | 123.0835 | -46.7148 | 76.2085 | -0.20615 | 0.017276 | 0.071027 | 0.076071 | 0.12779 | 0.0035547 | -0.0089999 | -0.16037 | -0.0084852 | 0.069818 | 0.056117 | 0.013821 | -0.0098374 | 75.9842 | 76.1856 | 5.5206 | -46.4401 | 76.3687 | -46.7972 | -46.9254 | -42.3569 | 40.6128 | -46.8063 | 76.3092 | 76.2268 | -46.9528 | -46.962 | -0.082397 | -0.21057 | 0.16022 | 122.9004 | 0.27466 | 0.48523 | -0.2243 | -0.23804 | -0.24719 | 0.10071 | 4.3579 | -0.091552 | 0.15564 | 0.018311 | 123.0835 | 122.699 | 52.2354 | -123.1338 | 123.024 | 122.9416 | 87.3276 | -123.1705
3775.0156 | 123.0423 | -45.8084 | 77.1515 | 0.10666 | 0.020694 | 0.072096 | 0.076926 | 0.128 | 0.0020593 | -0.010495 | 0.060883 | -0.0097668 | 0.071314 | 0.057612 | 0.011899 | -0.013469 | 77.1378 | 76.8814 | 5.6442 | -45.5475 | 77.298 | -45.8679 | -45.9869 | -41.478 | 41.3773 | -45.8817 | 77.2522 | 77.1927 | -46.0236 | -46.0464 | -0.059509 | -0.17853 | 0.14648 | 122.6898 | 0.26093 | 0.43945 | -0.013733 | -0.21515 | -0.23804 | 0.10071 | 4.3304 | -0.073242 | 0.16479 | 0.041199 | 123.1064 | 122.9462 | 51.4526 | -123.1384 | 123.0606 | 123.0011 | 87.1857 | -123.1979
3776.0156 | 123.056 | -45.7993 | 77.1744 | -0.14511 | 0.01514 | 0.071455 | 0.073081 | 0.13121 | 0.0014185 | -0.0066501 | -0.13748 | -0.0086988 | 0.068323 | 0.057398 | 0.01019 | -0.011974 | 76.886 | 77.0599 | 6.1478 | -45.5475 | 77.298 | -45.8817 | -45.9366 | -41.4642 | 41.4917 | -45.8359 | 77.2751 | 77.1744 | -45.9869 | -46.019 | -0.082398 | -0.13733 | 0.1236 | 122.8592 | 0.25177 | 0.3891 | -0.28839 | -0.18768 | -0.21973 | 0.10071 | 4.335 | -0.036621 | 0.18311 | 0 | 123.0972 | 122.6852 | 51.947 | -123.111 | 123.0743 | 122.9736 | 87.291 | -123.1934
3777.0156 | 123.0606 | -46.0693 | 76.8951 | -0.061188 | 0.021335 | 0.069746 | 0.077567 | 0.13057 | 0.0037683 | -0.0057957 | 0.060883 | -0.009126 | 0.071955 | 0.057612 | 0.013608 | -0.011333 | 76.6708 | 76.8265 | 6.015 | -45.813 | 77.0233 | -46.1197 | -46.2341 | -41.716 | 41.2628 | -46.1151 | 76.9913 | 76.8906 | -46.2982 | -46.3074 | -0.050354 | -0.16479 | 0.12817 | 122.8958 | 0.25635 | 0.42114 | -0.22431 | -0.22888 | -0.23804 | 0.09613 | 4.3533 | -0.045776 | 0.19226 | -0.004578 | 123.0927 | 122.7402 | 52.0844 | -123.1293 | 123.0606 | 122.9599 | 87.3322 | -123.2025
3778.0156 | 123.056 | -46.4676 | 76.5152 | -0.023041 | 0.021335 | 0.072309 | 0.077139 | 0.12715 | 0.0044091 | -0.0068637 | 0.022736 | -0.0082716 | 0.068537 | 0.060176 | 0.012753 | -0.01176 | 76.2588 | 76.442 | 5.9555 | -46.2021 | 76.6296 | -46.5134 | -46.637 | -42.0547 | 40.979 | -46.5134 | 76.5976 | 76.5427 | -46.669 | -46.6873 | -0.045777 | -0.16937 | 0.11444 | 122.9095 | 0.2655 | 0.43488 | -0.25635 | -0.20142 | -0.21973 | 0.082397 | 4.4128 | -0.045777 | 0.17395 | 0.027466 | 123.0972 | 122.7264 | 52.4231 | -123.1522 | 123.0652 | 123.0103 | 87.4466 | -123.2025
3779.0156 | 123.111 | -46.1975 | 76.7624 | -0.099335 | 0.020267 | 0.069746 | 0.074362 | 0.1295 | 0.0024865 | -0.0068637 | -0.053558 | -0.0082716 | 0.067468 | 0.058253 | 0.0082672 | -0.012187 | 76.5564 | 76.7212 | 5.9875 | -45.8817 | 76.9135 | -46.2387 | -46.3577 | -41.7664 | 41.2354 | -46.2753 | 76.8677 | 76.7761 | -46.3943 | -46.4218 | -0.041198 | -0.16022 | 0.15106 | 122.9187 | 0.31586 | 0.47607 | -0.20599 | -0.19684 | -0.2243 | 0.10529 | 4.4312 | -0.07782 | 0.14648 | 0.013733 | 123.111 | 122.7539 | 52.1851 | -123.1201 | 123.0652 | 122.9736 | 87.4329 | -123.1842
3780.0156 | 123.0881 | -45.7535 | 77.1927 | -0.22903 | 0.016421 | 0.07295 | 0.075217 | 0.13014 | 0.00035035 | -0.0079319 | -0.12985 | -0.008058 | 0.06875 | 0.058894 | 0.010831 | -0.013683 | 77.0645 | 77.2476 | 5.9235 | -45.3552 | 77.4811 | -45.6894 | -45.8038 | -41.2491 | 41.7435 | -45.8588 | 77.3804 | 77.2797 | -45.9457 | -45.9778 | 0.064087 | -0.050354 | 0.28839 | 123.0011 | 0.39825 | 0.44861 | -0.12817 | -0.19226 | -0.2243 | 0.18768 | 4.5044 | -0.10529 | 0.11902 | 0.086975 | 123.2346 | 122.818 | 51.6769 | -122.9965 | 123.1338 | 123.0331 | 87.4969 | -123.1705
3781.0156 | 123.0469 | -46.1563 | 76.8356 | -0.045929 | 0.019839 | 0.071882 | 0.073935 | 0.1295 | 0.0044091 | -0.0038731 | 0.045624 | -0.011903 | 0.06875 | 0.057826 | 0.011472 | -0.012187 | 76.5793 | 76.7715 | 5.5939 | -45.8633 | 76.9501 | -46.2067 | -46.2891 | -41.748 | 41.2674 | -46.2204 | 76.8814 | 76.8127 | -46.3715 | -46.3852 | -0.050354 | -0.13275 | 0.11444 | 122.9279 | 0.29297 | 0.42572 | -0.25635 | -0.21515 | -0.22888 | 0.045777 | 4.4083 | -0.064087 | 0.16479 | -0.022888 | 123.1064 | 122.7356 | 51.7502 | -123.1247 | 123.0377 | 122.9691 | 87.4237 | -123.2208
3782.0156 | 123.0927 | -46.1746 | 76.7715 | -0.084076 | 0.01813 | 0.072523 | 0.073721 | 0.13057 | 0.0044091 | -0.0077183 | -0.068817 | -0.0095532 | 0.069177 | 0.056971 | 0.01019 | -0.0089828 | 76.5518 | 76.7258 | 5.8365 | -45.8908 | 76.9318 | -46.2662 | -46.344 | -41.6611 | 41.2308 | -46.1334 | 76.9089 | 76.8356 | -46.3943 | -46.4127 | -0.091552 | -0.16937 | 0.16022 | 122.9004 | 0.28381 | 0.45319 | -0.21973 | -0.21973 | -0.23804 | 0.13733 | 4.5136 | 0.041199 | 0.27924 | 0.064087 | 123.1064 | 122.7264 | 52.0111 | -123.1155 | 123.0835 | 123.0103 | 87.4054 | -123.1842
3783.0156 | 123.1476 | -46.0831 | 76.8036 | 0.17532 | 0.013644 | 0.070173 | 0.069663 | 0.12886 | 0.0067589 | -0.0066501 | 0.39658 | -0.011049 | 0.067682 | 0.05633 | 0.01254 | -0.011333 | 76.3229 | 77.0004 | 6.102 | -45.845 | 76.8173 | -46.2524 | -46.3394 | -41.684 | 41.3681 | -46.106 | 76.8219 | 76.7853 | -46.3074 | -46.3394 | -0.16937 | -0.25635 | 0.013733 | 123.0835 | 0.23804 | 0.49438 | -0.48065 | -0.2243 | -0.25635 | 0.01831 | 4.3991 | -0.022888 | 0.23346 | -0.018311 | 122.9004 | 122.406 | 52.1851 | -123.143 | 122.905 | 122.8683 | 87.4512 | -123.143
3784.0156 | 123.0606 | -46.9299 | 76.0254 | -0.17563 | 0.016635 | 0.071027 | 0.07479 | 0.1295 | 0.0024865 | -0.0072911 | -0.16037 | -0.0084852 | 0.066614 | 0.058253 | 0.011899 | -0.01176 | 75.8102 | 75.9705 | 5.7358 | -46.6187 | 76.2039 | -46.962 | -47.0398 | -42.4072 | 40.7043 | -46.9482 | 76.1765 | 76.1169 | -47.1039 | -47.1359 | -0.032043 | -0.10986 | 0.17853 | 122.9004 | 0.31128 | 0.42114 | -0.21515 | -0.17395 | -0.20599 | 0.15106 | 4.5227 | -0.01831 | 0.18768 | 0.091552 | 123.1338 | 122.7402 | 52.6657 | -123.0652 | 123.1064 | 123.0469 | 87.6343 | -123.1613
3785.0156 | 123.0377 | -46.8018 | 76.1673 | 0.030365 | 0.020694 | 0.069532 | 0.075858 | 0.12693 | 0.0037683 | -0.0072911 | 0.076141 | -0.0082716 | 0.067255 | 0.058253 | 0.012326 | -0.01176 | 75.9293 | 76.0574 | 5.5023 | -46.5317 | 76.3092 | -46.8475 | -46.9391 | -42.3798 | 40.8371 | -46.9208 | 76.2405 | 76.181 | -47.0398 | -47.0444 | -0.045776 | -0.13733 | 0.14191 | 122.8592 | 0.27008 | 0.40741 | -0.23804 | -0.23804 | -0.24262 | 0.073243 | 4.422 | -0.11902 | 0.1236 | 0.013733 | 123.111 | 122.731 | 52.3041 | -123.1064 | 123.0423 | 122.9828 | 87.6389 | -123.2117
3786.0156 | 123.0469 | -46.4722 | 76.4603 | -0.061188 | 0.019198 | 0.0706 | 0.075003 | 0.12629 | 0.0046227 | -0.0068637 | -0.015411 | -0.009126 | 0.069177 | 0.057826 | 0.012112 | -0.011119 | 76.268 | 76.4328 | 5.5984 | -46.1975 | 76.6022 | -46.5408 | -46.5958 | -41.9998 | 41.1163 | -46.5775 | 76.561 | 76.4877 | -46.7056 | -46.7514 | -0.068665 | -0.1236 | 0.14191 | 122.905 | 0.27466 | 0.39825 | -0.19226 | -0.23346 | -0.27924 | 0.10071 | 4.4724 | -0.10529 | 0.17395 | 0.027466 | 123.0743 | 122.7402 | 52.0706 | -123.056 | 123.0331 | 122.9599 | 87.5885 | -123.2117
3787.0156 | 123.056 | -46.376 | 76.5518 | 0.14481 | 0.016421 | 0.072523 | 0.073508 | 0.12928 | 0.0024865 | -0.0085727 | 0.24399 | -0.0086988 | 0.069605 | 0.055903 | 0.01019 | -0.013042 | 76.3367 | 76.4648 | 5.7724 | -46.1014 | 76.7212 | -46.4218 | -46.5225 | -41.8808 | 41.185 | -46.4996 | 76.68 | 76.5884 | -46.582 | -46.637 | -0.045776 | -0.14648 | 0.16937 | 122.8409 | 0.27466 | 0.42114 | -0.21515 | -0.20599 | -0.26093 | 0.12817 | 4.4952 | -0.1236 | 0.13733 | 0.036621 | 123.0972 | 122.7127 | 52.1484 | -123.0743 | 123.056 | 122.9645 | 87.561 | -123.1888
3788.0156 | 123.1476 | -45.8908 | 76.9775 | 0.15244 | 0.016421 | 0.071882 | 0.070944 | 0.128 | -0.00093145 | -0.0072911 | 0.037995 | -0.011903 | 0.069177 | 0.057398 | 0.0093354 | -0.013042 | 76.7761 | 77.0645 | 5.6717 | -45.8862 | 76.9775 | -46.0739 | -46.1655 | -41.3956 | 41.6977 | -45.8633 | 77.0142 | 76.9821 | -46.1426 | -46.1426 | -0.18311 | -0.27466 | 0 | 122.9553 | 0.004578 | 0.27924 | -0.20142 | -0.25177 | -0.25177 | 0.036621 | 4.4952 | 0.027466 | 0.27924 | 0.004578 | 122.8683 | 122.6669 | 51.5625 | -123.143 | 122.905 | 122.8729 | 87.5885 | -123.1201
3789.0156 | 123.0652 | -45.7352 | 77.2156 | -0.076447 | 0.019198 | 0.071668 | 0.073935 | 0.13014 | 0.0063317 | -0.0070773 | -0.015411 | -0.0078442 | 0.069818 | 0.056758 | 0.011899 | -0.014323 | 77.0462 | 77.124 | 5.8868 | -45.4697 | 77.3483 | -45.7947 | -45.9366 | -41.2216 | 41.9357 | -45.813 | 77.298 | 77.2614 | -45.9503 | -45.9732 | -0.05951 | -0.20142 | 0.13275 | 122.8592 | 0.2655 | 0.46692 | -0.16937 | -0.21515 | -0.23804 | 0.082398 | 4.5135 | -0.07782 | 0.16022 | 0.045777 | 123.0835 | 122.7814 | 51.622 | -123.1522 | 123.0331 | 122.9965 | 87.6709 | -123.1888
3790.0156 | 123.0606 | -45.694 | 77.243 | -0.15274 | 0.019198 | 0.072096 | 0.071585 | 0.1295 | 0.0031273 | -0.0085727 | -0.099335 | -0.0093396 | 0.067468 | 0.057398 | 0.013821 | -0.012401 | 77.0599 | 77.2064 | 5.9052 | -45.4056 | 77.4216 | -45.7306 | -45.845 | -41.1346 | 42.041 | -45.694 | 77.3712 | 77.3254 | -45.8954 | -45.9412 | -0.036621 | -0.15106 | 0.17853 | 122.9004 | 0.28839 | 0.43945 | -0.1831 | -0.20142 | -0.24719 | 0.12817 | 4.5593 | 0 | 0.24719 | 0.082397 | 123.1155 | 122.7539 | 51.5991 | -123.0881 | 123.0652 | 123.0194 | 87.735 | -123.1842
3791.0156 | 123.0469 | -45.5383 | 77.4078 | 0.31265 | 0.020053 | 0.072736 | 0.07479 | 0.12843 | 0.0035547 | -0.0068637 | 0.17532 | -0.0082716 | 0.068109 | 0.057398 | 0.011685 | -0.010265 | 77.1698 | 77.3209 | 6.0883 | -45.2866 | 77.5818 | -45.5887 | -45.726 | -41.0294 | 42.1234 | -45.6207 | 77.5085 | 77.4353 | -45.7901 | -45.7855 | -0.050354 | -0.18768 | 0.17395 | 122.8592 | 0.25177 | 0.43945 | -0.23804 | -0.25177 | -0.24719 | 0.10071 | 4.509 | -0.082398 | 0.16479 | 0.027466 | 123.1201 | 122.7081 | 51.6266 | -123.1338 | 123.0469 | 122.9736 | 87.6617 | -123.1934
3792.0156 | 123.0469 | -46.1243 | 76.8356 | -0.6868 | 0.017703 | 0.072096 | 0.073508 | 0.12843 | 0.0067589 | -0.0070773 | -0.00015237 | -0.0078442 | 0.070673 | 0.060176 | 0.013181 | -0.010478 | 76.6708 | 76.7899 | 6.1157 | -45.7947 | 77.0233 | -46.1517 | -46.2341 | -41.5466 | 41.716 | -46.1334 | 76.9455 | 76.8814 | -46.3074 | -46.3531 | -0.027465 | -0.10986 | 0.18768 | 122.9141 | 0.32959 | 0.43945 | -0.16479 | -0.1831 | -0.22888 | 0.10986 | 4.5776 | -0.009155 | 0.21973 | 0.045777 | 123.1476 | 122.7951 | 52.24 | -123.0698 | 123.0698 | 123.0057 | 87.8403 | -123.1888
3793.0156 | 123.0972 | -46.5912 | 76.3046 | 0.12192 | 0.013644 | 0.073805 | 0.072867 | 0.12843 | -0.0030677 | -0.0094273 | 0.26688 | -0.011689 | 0.067682 | 0.057185 | 0.010403 | -0.0089828 | 76.0666 | 76.268 | 6.1981 | -46.344 | 76.3779 | -46.6919 | -46.7651 | -42.0319 | 41.3086 | -46.6415 | 76.3824 | 76.3321 | -46.8155 | -46.8338 | -0.10071 | -0.17395 | 0.073243 | 122.8592 | 0.24719 | 0.42114 | -0.23804 | -0.2243 | -0.24261 | 0.07782 | 4.5593 | -0.050354 | 0.19226 | 0.027466 | 122.9691 | 122.6578 | 52.7893 | -123.0698 | 122.9736 | 122.9233 | 87.8998 | -123.1384
3794.0156 | 123.0652 | -45.5429 | 77.4078 | -0.061188 | 0.020267 | 0.071882 | 0.075217 | 0.12907 | 0.0065453 | -0.0083591 | -0.00015237 | -0.009126 | 0.069605 | 0.05633 | 0.01019 | -0.012828 | 77.2614 | 77.3438 | 6.308 | -45.2683 | 77.5497 | -45.575 | -45.6848 | -40.9653 | 42.2516 | -45.5429 | 77.5497 | 77.4582 | -45.7535 | -45.7901 | -0.032043 | -0.14191 | 0.14191 | 122.8867 | 0.27466 | 0.41656 | -0.14648 | -0.21057 | -0.24719 | 0.14191 | 4.5776 | 0 | 0.24719 | 0.050354 | 123.0927 | 122.8043 | 51.8509 | -123.0927 | 123.0927 | 123.0011 | 87.7945 | -123.1979
3795.0156 | 123.0927 | -45.6848 | 77.2247 | 0.18295 | 0.015567 | 0.071241 | 0.076498 | 0.12993 | 0.0027001 | -0.0060093 | 0.24399 | -0.0095532 | 0.068323 | 0.057826 | 0.012112 | -0.010905 | 77.0004 | 77.1286 | 6.2027 | -45.4559 | 77.3804 | -45.7855 | -45.8862 | -41.1118 | 42.1326 | -45.7031 | 77.3529 | 77.2705 | -45.9091 | -45.932 | -0.10071 | -0.20142 | 0.15564 | 122.8134 | 0.22888 | 0.4303 | -0.2243 | -0.2243 | -0.24719 | 0.12817 | 4.5731 | -0.018311 | 0.22888 | 0.045777 | 123.0652 | 122.6852 | 51.8875 | -123.111 | 123.0377 | 122.9553 | 87.8174 | -123.1567
3796.0156 | 123.056 | -45.7352 | 77.2339 | -0.045929 | 0.019626 | 0.072736 | 0.074362 | 0.13142 | 0.0039819 | -0.0051547 | -0.053558 | -0.0072034 | 0.069818 | 0.057185 | 0.011685 | -0.013255 | 76.9821 | 77.1103 | 6.1935 | -45.488 | 77.3163 | -45.8359 | -45.9503 | -41.1118 | 42.0959 | -45.6436 | 77.33 | 77.2888 | -45.9045 | -45.9503 | -0.10071 | -0.21515 | 0.082397 | 122.8455 | 0.24719 | 0.46234 | -0.25177 | -0.16937 | -0.21515 | 0.09613 | 4.6234 | 0.091552 | 0.3067 | 0.054931 | 123.0515 | 122.7173 | 51.9287 | -123.1842 | 123.0652 | 123.024 | 87.8311 | -123.1842
3797.0156 | 123.0789 | -45.9869 | 76.9638 | -0.15274 | 0.015994 | 0.071241 | 0.073081 | 0.12928 | 0.0061181 | -0.0070773 | -0.038299 | -0.0072034 | 0.070032 | 0.057612 | 0.011472 | -0.012187 | 76.7624 | 76.8951 | 6.1981 | -45.7397 | 77.1057 | -46.0876 | -46.1517 | -41.3773 | 41.9586 | -46.0556 | 77.0691 | 76.9821 | -46.2021 | -46.2341 | -0.10071 | -0.16479 | 0.14191 | 122.8821 | 0.24719 | 0.41199 | -0.20142 | -0.21515 | -0.24719 | 0.10529 | 4.6097 | -0.068665 | 0.17853 | 0.018311 | 123.0927 | 122.7493 | 52.1851 | -123.1155 | 123.056 | 122.9691 | 87.9456 | -123.1979
3798.0156 | 123.1338 | -46.1014 | 76.8219 | 0.15244 | 0.015567 | 0.070814 | 0.072653 | 0.12843 | 0.0027001 | -0.0049411 | 0.24399 | -0.0095532 | 0.067041 | 0.059535 | 0.009549 | -0.012187 | 76.5839 | 76.7395 | 6.2576 | -45.845 | 76.9592 | -46.2021 | -46.2936 | -41.5604 | 41.8991 | -46.1426 | 76.8448 | 76.7715 | -46.3623 | -46.3348 | -0.10071 | -0.19226 | 0.13733 | 122.8409 | 0.25635 | 0.44861 | -0.23804 | -0.26093 | -0.23346 | 0.022889 | 4.541 | -0.041199 | 0.19226 | -0.050354 | 123.0606 | 122.6852 | 52.359 | -123.1155 | 122.9462 | 122.8729 | 88.0005 | -123.1567
3799.0156 | 123.0331 | -45.5704 | 77.3987 | 1.5028 | 0.018344 | 0.072309 | 0.07479 | 0.12907 | 0.0033411 | -0.0079319 | 0.17532 | -0.0086988 | 0.067255 | 0.058467 | 0.01019 | -0.01176 | 77.2339 | 77.2614 | 6.3492 | -45.2408 | 77.6001 | -45.5795 | -45.6711 | -40.9698 | 42.3752 | -45.7031 | 77.4902 | 77.4078 | -45.8084 | -45.8176 | -0.009155 | -0.10071 | 0.20142 | 122.8317 | 0.32959 | 0.4303 | -0.16479 | -0.23804 | -0.24719 | 0.091552 | 4.6005 | -0.13275 | 0.11444 | 0.009155 | 123.1705 | 122.8043 | 51.9196 | -123.0698 | 123.0606 | 122.9782 | 87.9456 | -123.2162
3800.0156 | 123.0698 | -45.9961 | 76.8951 | -0.045929 | 0.01813 | 0.069959 | 0.073721 | 0.12928 | 0.0033411 | -0.0083591 | -0.47317 | -0.0089124 | 0.068964 | 0.059107 | 0.011044 | -0.010905 | 76.8036 | 76.9913 | 6.2302 | -45.5154 | 77.1423 | -45.9686 | -46.0785 | -41.3223 | 42.1188 | -46.1151 | 77.0462 | 76.973 | -46.2158 | -46.2387 | 0.027466 | -0.082397 | 0.24719 | 122.9874 | 0.48065 | 0.56305 | -0.091553 | -0.21973 | -0.24261 | 0.15106 | 4.6738 | -0.11902 | 0.1236 | 0.077819 | 123.1384 | 122.7997 | 52.2263 | -122.9736 | 123.0423 | 122.9691 | 88.1149 | -123.1339
3801.0156 | 123.0103 | -45.9732 | 77.005 | 0.0074768 | 0.019412 | 0.069319 | 0.071585 | 0.12843 | 0.00099115 | -0.0083591 | 0.0914 | -0.0078442 | 0.06875 | 0.056971 | 0.010831 | -0.011546 | 76.7075 | 76.8311 | 6.102 | -45.726 | 77.1103 | -46.0556 | -46.17 | -41.3269 | 42.0731 | -46.0602 | 77.0782 | 77.0142 | -46.1929 | -46.2067 | -0.082397 | -0.19684 | 0.10529 | 122.8043 | 0.24719 | 0.44403 | -0.29755 | -0.21973 | -0.23346 | 0.073242 | 4.6463 | -0.086975 | 0.14648 | 0.009155 | 123.0835 | 122.6807 | 52.0752 | -123.175 | 123.0515 | 122.9874 | 88.0463 | -123.2117
3802.0156 | 123.0377 | -45.7306 | 77.2156 | -0.023041 | 0.018985 | 0.072309 | 0.075217 | 0.12993 | 0.0048363 | -0.0075047 | 0.030365 | -0.009126 | 0.070459 | 0.058894 | 0.015317 | -0.010692 | 77.0096 | 77.1378 | 5.9692 | -45.4559 | 77.3071 | -45.8267 | -45.932 | -41.0934 | 42.2836 | -45.7535 | 77.3026 | 77.2476 | -45.9595 | -45.9778 | -0.09613 | -0.20142 | 0.091553 | 122.8683 | 0.27466 | 0.47607 | -0.20599 | -0.22888 | -0.24719 | 0.086975 | 4.6371 | -0.022888 | 0.2243 | 0.032044 | 123.0377 | 122.7402 | 51.6998 | -123.1476 | 123.0331 | 122.9782 | 88.0142 | -123.1934
3803.0156 | 123.1567 | -45.7031 | 77.2018 | -0.015411 | 0.011294 | -0.03557 | 0.072653 | 0.12907 | -0.0052039 | -0.010495 | 0.09903 | -0.011262 | 0.067896 | 0.056758 | 0.0082672 | -0.010051 | 77.0004 | 77.243 | 6.3217 | -45.3644 | 77.3849 | -45.7535 | -45.8496 | -40.9653 | 42.4576 | -45.6482 | 77.3071 | 77.2385 | -45.8862 | -45.9274 | -0.050354 | -0.14648 | 0.18311 | 122.9462 | 0.33875 | 0.48523 | -0.20142 | -0.1831 | -0.2243 | 0.10529 | 4.7379 | 0.054932 | 0.27924 | 0.036621 | 123.0881 | 122.7036 | 52.0248 | -123.0515 | 123.0103 | 122.9416 | 88.1607 | -123.1293
3804.0156 | 123.0698 | -46.1014 | 76.8402 | -0.16037 | 0.019626 | 0.073164 | 0.075644 | 0.12993 | 0.0059045 | -0.0083591 | -0.084076 | -0.0084852 | 0.069177 | 0.058253 | 0.013181 | -0.014323 | 76.6754 | 76.8311 | 6.2302 | -45.7397 | 77.0187 | -46.1517 | -46.2524 | -41.3635 | 42.0685 | -46.1334 | 76.9775 | 76.886 | -46.3348 | -46.3303 | -0.050354 | -0.15106 | 0.17853 | 122.9324 | 0.36163 | 0.5127 | -0.16479 | -0.23346 | -0.22888 | 0.13733 | 4.7379 | -0.032044 | 0.19684 | 0.045776 | 123.1201 | 122.7768 | 52.3315 | -123.0927 | 123.0789 | 122.9874 | 88.1699 | -123.1705
3805.0156 | 123.0835 | -45.9915 | 76.9638 | -0.0383 | 0.019198 | 0.070173 | 0.073081 | 0.12693 | 0.0080407 | -0.0062229 | 0.037995 | -0.0067762 | 0.070032 | 0.059321 | 0.011258 | -0.012614 | 76.7441 | 76.8768 | 6.1935 | -45.6757 | 77.1149 | -46.0373 | -46.1243 | -41.3132 | 42.1646 | -46.1472 | 77.0462 | 76.9913 | -46.225 | -46.2479 | -0.045776 | -0.13275 | 0.15106 | 122.8683 | 0.31586 | 0.44861 | -0.21973 | -0.23346 | -0.25635 | 0.082398 | 4.6783 | -0.15564 | 0.10071 | 0.027466 | 123.1064 | 122.7356 | 52.1851 | -123.0881 | 123.0377 | 122.9828 | 88.1561 | -123.2117
3806.0156 | 123.0972 | -46.6187 | 76.3275 | -0.023041 | 0.018985 | 0.071668 | 0.073508 | 0.12907 | 0.0031273 | -0.0062229 | -1.2666 | -0.0086988 | 0.069605 | 0.059321 | 0.011472 | -0.012828 | 76.1673 | 76.3092 | 5.8685 | -46.2936 | 76.5106 | -46.6461 | -46.7468 | -41.8945 | 41.7023 | -46.6919 | 76.4191 | 76.3916 | -46.8201 | -46.8658 | -0.027466 | -0.12817 | 0.1831 | 122.9279 | 0.32501 | 0.45319 | -0.16022 | -0.20142 | -0.24719 | 0.091552 | 4.7241 | -0.073243 | 0.17395 | 0.064087 | 123.1293 | 122.7859 | 52.4872 | -123.0743 | 123.0377 | 123.0103 | 88.3209 | -123.1934
3807.0156 | 123.0194 | -46.1288 | 76.886 | 0.099029 | 0.017703 | 0.070387 | 0.076926 | 0.12693 | 0.0056909 | -0.0079319 | -2.7773 | -0.009126 | 0.0711 | 0.058894 | 0.010831 | -0.010692 | 76.506 | 76.6479 | 6.221 | -45.845 | 76.9592 | -46.2296 | -46.3348 | -41.4368 | 41.9678 | -46.2387 | 76.918 | 76.8723 | -46.3623 | -46.3531 | -0.10071 | -0.20599 | 0.073243 | 122.7768 | 0.28381 | 0.48981 | -0.37994 | -0.23346 | -0.2243 | 0.032044 | 4.6921 | -0.10986 | 0.11444 | -0.013733 | 123.0881 | 122.6349 | 52.3499 | -123.2208 | 123.0469 | 123.0011 | 88.0966 | -123.2391
3808.0156 | 123.0698 | -46.0785 | 76.8631 | 0.11429 | 0.018985 | 0.069532 | 0.073508 | 0.12864 | 0.0046227 | -0.0057957 | 0.21347 | -0.0084852 | 0.067041 | 0.060176 | 0.012112 | -0.010265 | 76.5884 | 76.7349 | 6.0196 | -45.813 | 76.9867 | -46.1609 | -46.2799 | -41.3635 | 42.1921 | -46.1243 | 76.973 | 76.8951 | -46.2982 | -46.3257 | -0.082398 | -0.20142 | 0.1236 | 122.8134 | 0.2655 | 0.46692 | -0.27466 | -0.21973 | -0.24719 | 0.10986 | 4.715 | -0.045777 | 0.20142 | 0.032044 | 123.0652 | 122.6669 | 52.0981 | -123.143 | 123.0515 | 122.9736 | 88.2706 | -123.1888
3809.0156 | 123.0057 | -47.0215 | 75.943 | 0.053253 | 0.020267 | 0.071882 | 0.076071 | 0.13078 | 0.0039819 | -0.0070773 | 0.17532 | -0.0084852 | 0.069177 | 0.059962 | 0.011044 | -0.011546 | 75.7004 | 75.8011 | 5.6671 | -46.6873 | 76.0895 | -47.0489 | -47.1634 | -42.3248 | 41.1255 | -47.1222 | 76.0391 | 75.9888 | -47.2137 | -47.2504 | -0.027466 | -0.14191 | 0.14648 | 122.8226 | 0.33417 | 0.47607 | -0.24262 | -0.19226 | -0.22888 | 0.096131 | 4.6967 | -0.10071 | 0.12817 | 0.045777 | 123.111 | 122.7219 | 52.6886 | -123.1064 | 123.0606 | 123.0103 | 88.147 | -123.1934
3810.0156 | 123.056 | -47.3465 | 75.5997 | -0.17563 | 0.017062 | 0.073164 | 0.073935 | 0.1295 | 0.0029137 | -0.0070773 | -0.12222 | -0.0095532 | 0.068323 | 0.060176 | 0.0084808 | -0.010692 | 75.3571 | 75.4852 | 5.7495 | -47.0261 | 75.7324 | -47.4335 | -47.5525 | -42.6224 | 40.8875 | -47.4197 | 75.7278 | 75.6683 | -47.5479 | -47.5845 | -0.086975 | -0.20599 | 0.13275 | 122.8317 | 0.32043 | 0.52643 | -0.24261 | -0.20142 | -0.23804 | 0.12817 | 4.7241 | -0.073242 | 0.16479 | 0.068665 | 123.0789 | 122.7036 | 53.096 | -123.1522 | 123.0743 | 123.0148 | 88.2339 | -123.1842
3811.0156 | 123.0331 | -46.9299 | 76.0529 | 0.045624 | 0.020907 | 0.072736 | 0.074576 | 0.12736 | 0.0048363 | -0.0089999 | 0.076141 | -0.0078442 | 0.071314 | 0.059321 | 0.012753 | -0.011974 | 75.8057 | 75.9476 | 5.8411 | -46.5912 | 76.1902 | -46.9528 | -47.0673 | -42.1829 | 41.2582 | -47.0261 | 76.1353 | 76.0757 | -47.1405 | -47.1771 | -0.022888 | -0.13733 | 0.13733 | 122.8775 | 0.33875 | 0.47607 | -0.24719 | -0.21057 | -0.24719 | 0.082398 | 4.747 | -0.09613 | 0.15106 | 0.022889 | 123.1201 | 122.7356 | 52.771 | -123.1201 | 123.0652 | 123.0057 | 88.1882 | -123.23
3812.0156 | 123.1018 | -46.431 | 76.5472 | -0.168 | 0.017276 | 0.071027 | 0.073935 | 0.13014 | 0.00013675 | -0.0081455 | -0.15274 | -0.0099806 | 0.067682 | 0.058467 | 0.011899 | -0.011546 | 76.2588 | 76.4099 | 5.7999 | -46.1105 | 76.6479 | -46.5225 | -46.6049 | -41.6748 | 41.7526 | -46.4676 | 76.6251 | 76.5656 | -46.6599 | -46.6736 | -0.091553 | -0.17395 | 0.10071 | 122.8409 | 0.32043 | 0.49438 | -0.28839 | -0.22888 | -0.24262 | 0.07782 | 4.7562 | -0.036621 | 0.20599 | 0.018311 | 123.0789 | 122.6898 | 52.2308 | -123.1522 | 123.056 | 122.9965 | 88.1836 | -123.2208
3813.0156 | 123.0057 | -46.1563 | 76.8036 | 0.045624 | 0.019839 | 0.073164 | 0.074149 | 0.12864 | 0.0035547 | -0.0070773 | 0.18295 | -0.0097668 | 0.069177 | 0.057612 | 0.012326 | -0.011974 | 76.5152 | 76.6251 | 5.9967 | -45.8771 | 76.9043 | -46.2708 | -46.3852 | -41.4734 | 42.0181 | -46.3486 | 76.8906 | 76.7853 | -46.3898 | -46.4493 | -0.11444 | -0.22888 | 0.10071 | 122.7814 | 0.27924 | 0.50812 | -0.28839 | -0.23346 | -0.29297 | 0.086975 | 4.6829 | -0.19226 | 0.10071 | -0.018311 | 123.0606 | 122.6715 | 52.153 | -123.1888 | 123.0469 | 122.9416 | 88.1744 | -123.2529
3814.0156 | 123.0743 | -45.6573 | 77.2888 | 0.12955 | 0.018771 | 0.071882 | 0.07479 | 0.12843 | 0.0033411 | -0.0077183 | 0.27451 | -0.010408 | 0.069605 | 0.058253 | 0.011899 | -0.011333 | 77.0279 | 77.1561 | 5.8502 | -45.401 | 77.3895 | -45.7397 | -45.8542 | -40.8783 | 42.5812 | -45.694 | 77.3621 | 77.3117 | -45.8588 | -45.8725 | -0.082397 | -0.19684 | 0.10071 | 122.8134 | 0.25635 | 0.45319 | -0.26093 | -0.20142 | -0.21515 | 0.073243 | 4.7791 | -0.036621 | 0.17853 | 0.022889 | 123.0469 | 122.6852 | 51.5076 | -123.143 | 123.0194 | 122.9691 | 88.2385 | -123.1613
3815.0156 | 123.1064 | -46.6919 | 76.2177 | 0.10666 | 0.017917 | 0.073377 | 0.073935 | 0.12715 | 0.0024865 | -0.0079319 | 0.18295 | -0.0078442 | 0.068964 | 0.060603 | 0.011472 | -0.011546 | 75.9293 | 76.0574 | 5.8548 | -46.4401 | 76.3275 | -46.8384 | -46.9345 | -41.9449 | 41.6428 | -46.7972 | 76.3046 | 76.2497 | -46.9254 | -46.9482 | -0.14648 | -0.24261 | 0.10986 | 122.7493 | 0.25177 | 0.49438 | -0.28839 | -0.23346 | -0.25635 | 0.086975 | 4.747 | -0.10528 | 0.15106 | 0.032044 | 123.0194 | 122.6212 | 52.5467 | -123.1522 | 122.9965 | 122.9416 | 88.3347 | -123.1659
3816.0156 | 123.0652 | -45.6894 | 77.2751 | -0.068817 | 0.017062 | 0.071241 | 0.07479 | 0.12822 | 0.0037683 | -0.0094273 | -0.091705 | -0.0065626 | 0.067682 | 0.058253 | 0.011899 | -0.012187 | 77.2705 | 77.179 | 6.1295 | -45.3506 | 77.417 | -45.7123 | -45.8221 | -40.8234 | 42.7185 | -45.6894 | 77.3758 | 77.2888 | -45.8679 | -45.9183 | -0.022888 | -0.13275 | 0.14191 | 122.8683 | 0.33874 | 0.4715 | -0.004577 | -0.17853 | -0.22888 | 0.10071 | 4.866 | 0 | 0.22888 | 0.013733 | 123.1064 | 122.9599 | 51.8188 | -123.0972 | 123.0652 | 122.9782 | 88.4079 | -123.1934
3817.0156 | 123.0789 | -45.2362 | 77.71 | -0.0383 | 0.01813 | 0.06825 | 0.076071 | 0.13057 | 0.0035547 | -0.0068637 | 1.8767 | -0.0095532 | 0.067468 | 0.059321 | 0.011044 | -0.011119 | 77.5269 | 77.6321 | 6.3858 | -44.9158 | 77.8519 | -45.2866 | -45.4147 | -40.3519 | 43.1351 | -45.2362 | 77.8107 | 77.7603 | -45.4376 | -45.4697 | -0.050354 | -0.17853 | 0.14191 | 122.8683 | 0.32044 | 0.49896 | -0.18311 | -0.20142 | -0.23346 | 0.10071 | 4.8843 | 0 | 0.23346 | 0.050354 | 123.0881 | 122.7631 | 51.622 | -123.1247 | 123.0469 | 122.9965 | 88.3713 | -123.1796
3818.0156 | 123.0194 | -45.7764 | 77.1835 | 0.14481 | 0.016208 | 0.070814 | 0.072012 | 0.12864 | 0.0052637 | -0.0066501 | 0.13718 | -0.0097668 | 0.0711 | 0.058253 | 0.013608 | -0.0091966 | 76.8402 | 76.9775 | 6.3171 | -45.5063 | 77.2934 | -45.8633 | -45.9824 | -41.0706 | 42.9932 | -45.7672 | 77.3117 | 77.211 | -46.0052 | -46.0373 | -0.086975 | -0.20599 | 0.10986 | 122.7539 | 0.27008 | 0.47607 | -0.34332 | -0.22888 | -0.26093 | 0.12817 | 4.7058 | 0.009155 | 0.27008 | 0.027466 | 123.0698 | 122.6166 | 52.0935 | -123.1659 | 123.0881 | 122.9874 | 88.7695 | -123.2208
3819.0312 | 123.1522 | -45.8542 | 77.0462 | 0.037994 | 0.010653 | 0.085127 | 0.070303 | 0.12822 | -0.0047767 | -0.0087863 | 0.09903 | -0.011476 | 0.068537 | 0.059535 | 0.00784 | -0.010051 | 76.7761 | 77.005 | 6.6238 | -45.5475 | 77.1423 | -45.9366 | -46.0648 | -40.979 | 42.4576 | -45.8405 | 77.1286 | 77.0737 | -46.0831 | -46.0968 | -0.082397 | -0.21057 | 0.09613 | 122.8592 | 0.3067 | 0.51727 | -0.27008 | -0.22888 | -0.24261 | 0.082397 | 4.8752 | 0.013733 | 0.25635 | 0.027465 | 122.9965 | 122.6303 | 52.478 | -123.111 | 122.9828 | 122.9279 | 88.3118 | -123.143
3820.0156 | 123.0606 | -45.4926 | 77.4719 | -0.16037 | 0.013431 | 0.072309 | 0.07543 | 0.12693 | 0.0020593 | -0.0094273 | -0.14511 | -0.011262 | 0.068323 | 0.057398 | 0.011258 | -0.012614 | 77.1881 | 77.3529 | 6.8298 | -45.1996 | 77.5864 | -45.5795 | -45.694 | -40.6723 | 42.659 | -45.488 | 77.5955 | 77.5543 | -45.6894 | -45.6985 | -0.086975 | -0.20142 | 0.11444 | 122.8455 | 0.29297 | 0.49439 | -0.28381 | -0.19684 | -0.20599 | 0.1236 | 4.8203 | 0.004578 | 0.21057 | 0.082397 | 123.0789 | 122.6807 | 52.3224 | -123.1659 | 123.0881 | 123.0469 | 88.1516 | -123.1705
3821.0156 | 122.9691 | -45.9 | 77.0462 | -0.22141 | 0.017276 | 0.070814 | 0.076285 | 0.1295 | 0.0052637 | -0.0070773 | -0.045929 | -0.010408 | 0.071314 | 0.058039 | 0.013608 | -0.013469 | 76.6846 | 76.8356 | 6.9534 | -45.6757 | 77.0828 | -46.1014 | -46.2067 | -41.0751 | 42.2974 | -45.9732 | 77.0279 | 76.9775 | -46.2112 | -46.1929 | -0.20142 | -0.3067 | 0.036621 | 122.7356 | 0.2243 | 0.53101 | -0.36163 | -0.31128 | -0.29297 | -0.018311 | 4.8248 | -0.073243 | 0.21973 | -0.068665 | 122.9828 | 122.5845 | 52.8534 | -123.2529 | 122.9279 | 122.8775 | 88.1973 | -123.2391
3822.0156 | 123.0148 | -45.8084 | 77.1835 | -0.168 | 0.014071 | 0.073377 | 0.07479 | 0.13035 | 0.0020593 | -0.010282 | 0.068512 | -0.0089124 | 0.068964 | 0.05868 | 0.010617 | -0.012614 | 76.8677 | 77.0508 | 7.3471 | -45.5063 | 77.3026 | -45.845 | -45.9366 | -40.9195 | 42.4393 | -45.8313 | 77.2797 | 77.2018 | -46.0327 | -46.0373 | -0.036621 | -0.12817 | 0.11902 | 122.8592 | 0.30212 | 0.4303 | -0.31586 | -0.2243 | -0.22888 | 0.09613 | 4.8889 | -0.022888 | 0.20599 | 0.01831 | 123.111 | 122.6761 | 53.1555 | -123.1201 | 123.0881 | 123.0103 | 88.2477 | -123.2208
3823.0156 | 123.056 | -45.7489 | 77.2339 | 0.16006 | 0.020694 | 0.068464 | 0.07543 | 0.12715 | 0.0033411 | -0.0013095 | 0.56442 | -0.0082716 | 0.071314 | 0.057612 | 0.012112 | -0.010478 | 76.7944 | 77.037 | 7.0587 | -45.314 | 77.4124 | -45.7809 | -45.8954 | -40.8279 | 42.4805 | -45.8176 | 77.3163 | 77.2476 | -45.9457 | -45.9869 | -0.032044 | -0.14649 | 0.17853 | 122.7859 | 0.43487 | 0.58136 | -0.43945 | -0.19684 | -0.23804 | 0.082397 | 4.921 | -0.068665 | 0.16937 | 0.013733 | 123.1613 | 122.5433 | 52.8076 | -123.1293 | 123.0652 | 122.9965 | 88.2294 | -123.2208
3824.0156 | 123.0743 | -46.1151 | 76.8402 | 0.10666 | 0.017703 | 0.0706 | 0.073508 | 0.128 | 0.0016321 | -0.0053683 | 0.20584 | -0.0086988 | 0.068323 | 0.060389 | 0.011472 | -0.011974 | 76.561 | 76.6983 | 7.0038 | -45.8221 | 76.9638 | -46.2112 | -46.312 | -41.153 | 42.1738 | -46.1746 | 76.9135 | 76.8723 | -46.3394 | -46.3486 | -0.096131 | -0.19684 | 0.1236 | 122.8134 | 0.29297 | 0.48981 | -0.27924 | -0.2243 | -0.23346 | 0.073242 | 4.9622 | -0.05951 | 0.17395 | 0.032043 | 123.0789 | 122.6761 | 53.1189 | -123.1522 | 123.0286 | 122.9874 | 88.2889 | -123.1888
3825.0156 | 123.0743 | -45.6299 | 77.3575 | -0.22141 | 0.017703 | 0.071882 | 0.074576 | 0.1295 | 0.0039819 | -0.0057957 | -0.168 | -0.0089124 | 0.070032 | 0.05868 | 0.011472 | -0.012187 | 77.1149 | 77.2659 | 7.2235 | -45.2728 | 77.5314 | -45.6757 | -45.7855 | -40.6815 | 42.7185 | -45.6345 | 77.4582 | 77.4078 | -45.7947 | -45.8496 | -0.045776 | -0.15564 | 0.17395 | 122.8958 | 0.35706 | 0.5127 | -0.24262 | -0.16479 | -0.21973 | 0.10071 | 4.9484 | -0.004577 | 0.21515 | 0.050354 | 123.1613 | 122.7448 | 52.8534 | -123.143 | 123.0881 | 123.0377 | 88.3484 | -123.2071
3826.0156 | 123.0698 | -46.019 | 76.9592 | -0.23666 | 0.011294 | 0.073377 | 0.073294 | 0.12928 | -0.00093145 | -0.0081455 | -0.13748 | -0.0099806 | 0.070459 | 0.058894 | 0.011685 | -0.010692 | 76.7258 | 76.9409 | 6.9626 | -45.6345 | 77.0737 | -46.0785 | -46.1975 | -41.0751 | 42.3843 | -46.0098 | 77.0508 | 76.9409 | -46.2387 | -46.2479 | -0.059509 | -0.17853 | 0.11444 | 122.9599 | 0.38452 | 0.56305 | -0.23346 | -0.21973 | -0.22888 | 0.091552 | 4.9438 | 0.009155 | 0.23804 | -0.018311 | 123.0927 | 122.7448 | 52.9816 | -123.1567 | 123.0698 | 122.9599 | 88.4033 | -123.2071
3827.0156 | 123.0835 | -46.0693 | 76.9043 | -0.19852 | 0.014499 | 0.072096 | 0.073508 | 0.12736 | 0.0063317 | -0.0070773 | -0.19089 | -0.0099806 | 0.068964 | 0.059535 | 0.011044 | -0.013469 | 76.6388 | 76.8036 | 6.871 | -45.7077 | 77.0325 | -46.1288 | -46.225 | -41.1072 | 42.4255 | -46.1105 | 77.0004 | 76.9089 | -46.2936 | -46.312 | -0.059509 | -0.15564 | 0.12817 | 122.8729 | 0.36163 | 0.51727 | -0.2655 | -0.2243 | -0.24262 | 0.09613 | 4.9622 | -0.041199 | 0.20142 | 0.004578 | 123.1018 | 122.7081 | 52.9404 | -123.1293 | 123.0698 | 122.9782 | 88.4949 | -123.2162
3828.0156 | 123.0698 | -45.8267 | 77.0966 | -0.41214 | 0.019198 | 0.069959 | 0.075003 | 0.12928 | 0.0061181 | -0.0060093 | -0.045929 | -0.008058 | 0.068964 | 0.057398 | 0.012753 | -0.012828 | 76.918 | 77.0645 | 6.8893 | -45.4742 | 77.2705 | -45.8817 | -46.0327 | -40.9149 | 42.627 | -45.9 | 77.1927 | 77.1194 | -46.0602 | -46.1014 | -0.054932 | -0.20599 | 0.17395 | 122.8912 | 0.35248 | 0.55847 | -0.17853 | -0.23346 | -0.27466 | 0.09613 | 4.9118 | -0.073242 | 0.20142 | 0.022888 | 123.0972 | 122.7448 | 52.7161 | -123.1293 | 123.0194 | 122.9462 | 88.4537 | -123.1979
3829.0312 | 123.1338 | -46.3303 | 76.5335 | 0.12955 | 0.016421 | 0.072096 | 0.072226 | 0.12971 | -0.00050425 | -0.0064365 | 0.24399 | -0.007417 | 0.067468 | 0.061244 | 0.011258 | -0.012187 | 76.3367 | 76.5564 | 7.0312 | -46.0007 | 76.6617 | -46.4127 | -46.5225 | -41.3315 | 42.2607 | -46.344 | 76.6159 | 76.5198 | -46.5866 | -46.6049 | -0.082398 | -0.19226 | 0.12817 | 122.8867 | 0.32959 | 0.52185 | -0.19684 | -0.25635 | -0.27466 | 0.082398 | 4.9988 | -0.013733 | 0.26093 | -0.013733 | 122.9919 | 122.6669 | 53.3615 | -123.056 | 122.9462 | 122.85 | 88.591 | -123.1384
3830.0156 | 123.143 | -46.1197 | 76.8036 | -0.22903 | 0.011722 | 0.073377 | 0.072653 | 0.13014 | -0.0026405 | -0.0081455 | -0.061188 | -0.010408 | 0.067682 | 0.05868 | 0.0093354 | -0.011546 | 76.6022 | 76.8494 | 7.0953 | -45.7306 | 76.8814 | -46.1792 | -46.2708 | -41.1301 | 42.5171 | -46.0831 | 76.8402 | 76.7944 | -46.3211 | -46.3531 | -0.059509 | -0.15106 | 0.07782 | 122.9691 | 0.3891 | 0.54016 | -0.20142 | -0.20142 | -0.23346 | 0.036621 | 4.9896 | 0.036621 | 0.27008 | -0.009155 | 123.0011 | 122.7219 | 53.215 | -123.0743 | 122.9599 | 122.9141 | 88.6368 | -123.1567
3831.0156 | 123.0652 | -45.932 | 77.0508 | 0.015106 | 0.014926 | 0.073591 | 0.079062 | 0.13078 | 0.0039819 | -0.0083591 | -0.12985 | -0.010408 | 0.068323 | 0.056758 | 0.0099762 | -0.013255 | 76.7761 | 76.9226 | 7.2098 | -45.5841 | 77.1744 | -45.9778 | -46.0922 | -41.0019 | 42.5583 | -46.0144 | 77.1606 | 77.037 | -46.1609 | -46.17 | -0.045776 | -0.16022 | 0.1236 | 122.8546 | 0.3479 | 0.50812 | -0.27466 | -0.22888 | -0.23804 | 0.10986 | 4.9301 | -0.082397 | 0.15564 | -0.013733 | 123.1064 | 122.7081 | 53.1418 | -123.143 | 123.0927 | 122.9691 | 88.4903 | -123.2208
3832.0156 | 123.0469 | -45.9824 | 76.9867 | -1.8541 | 0.016208 | 0.071668 | 0.071799 | 0.1295 | 0.0041955 | -0.0087863 | -0.14511 | -0.0097668 | 0.070459 | 0.058039 | 0.011044 | -0.012828 | 76.6159 | 76.8814 | 6.9077 | -45.6757 | 77.1011 | -46.0785 | -46.1975 | -41.0614 | 42.5308 | -46.0464 | 77.0691 | 76.9821 | -46.2387 | -46.2433 | -0.09613 | -0.21515 | 0.11444 | 122.8638 | 0.3067 | 0.52185 | -0.37079 | -0.25635 | -0.26093 | 0.082398 | 4.921 | -0.064087 | 0.19684 | -0.004577 | 123.0835 | 122.5983 | 52.89 | -123.1842 | 123.0515 | 122.9645 | 88.5132 | -123.23
3833.0156 | 123.0194 | -46.0098 | 76.9455 | 0.52628 | 0.02048 | 0.071882 | 0.075003 | 0.12864 | 0.0054773 | -0.0072911 | 0.14481 | -0.0086988 | 0.070459 | 0.058253 | 0.01254 | -0.011333 | 76.6846 | 76.8311 | 6.9214 | -45.6573 | 77.1149 | -46.0693 | -46.1655 | -41.0385 | 42.5262 | -46.0602 | 77.0508 | 76.9501 | -46.2662 | -46.257 | -0.059509 | -0.15564 | 0.16937 | 122.8409 | 0.35248 | 0.50812 | -0.26093 | -0.25635 | -0.24719 | 0.10528 | 4.9713 | -0.050354 | 0.19684 | 0.004577 | 123.1247 | 122.6944 | 52.9312 | -123.111 | 123.0606 | 122.9599 | 88.5361 | -123.2025
3834.0156 | 123.1384 | -46.1472 | 76.7487 | -0.41977 | 0.010867 | 0.071668 | 0.071372 | 0.12779 | -0.0024269 | -0.0068637 | -0.068817 | -0.010621 | 0.068109 | 0.060176 | 0.011258 | -0.013042 | 76.4511 | 76.7212 | 7.0404 | -45.8588 | 76.7853 | -46.3074 | -46.3943 | -41.1713 | 42.485 | -46.1884 | 76.7807 | 76.7761 | -46.4264 | -46.4218 | -0.16022 | -0.24719 | 0.036621 | 122.8683 | 0.28839 | 0.53558 | -0.29755 | -0.27924 | -0.27466 | 0.032044 | 4.9759 | -0.041198 | 0.23346 | 0.027466 | 122.9324 | 122.5983 | 53.1876 | -123.143 | 122.9279 | 122.9233 | 88.6322 | -123.1705
3835.0156 | 123.0469 | -46.0922 | 76.8768 | -0.19089 | 0.013217 | 0.072736 | 0.073508 | 0.1295 | 0.0037683 | -0.0081455 | -0.11459 | -0.0086988 | 0.068323 | 0.060389 | 0.011258 | -0.012187 | 76.6113 | 76.7761 | 6.9443 | -45.7443 | 77.0279 | -46.1655 | -46.2479 | -41.1026 | 42.4759 | -46.1334 | 76.9867 | 76.9043 | -46.2799 | -46.3303 | -0.073242 | -0.15564 | 0.15106 | 122.8683 | 0.3479 | 0.50354 | -0.2655 | -0.18768 | -0.23804 | 0.10986 | 4.9896 | -0.041199 | 0.19684 | 0.027466 | 123.1201 | 122.7036 | 53.0365 | -123.1247 | 123.0789 | 122.9965 | 88.5681 | -123.2071
3836.0156 | 123.0423 | -45.9503 | 77.0142 | -0.45029 | 0.016421 | 0.07295 | 0.075644 | 0.13035 | 0.0027001 | -0.0070773 | -0.168 | -0.011262 | 0.06875 | 0.057398 | 0.011258 | -0.01176 | 76.7075 | 76.8951 | 6.9717 | -45.6116 | 77.124 | -46.0373 | -46.1563 | -40.9332 | 42.6178 | -46.0281 | 77.1332 | 77.0233 | -46.1563 | -46.1929 | -0.086975 | -0.20599 | 0.10986 | 122.8455 | 0.33874 | 0.54474 | -0.3067 | -0.20599 | -0.24262 | 0.11902 | 5.0171 | -0.07782 | 0.16479 | 0.009155 | 123.0743 | 122.6578 | 52.9221 | -123.1705 | 123.0835 | 122.9736 | 88.5681 | -123.2071
3837.0156 | 123.0606 | -46.3165 | 76.6617 | -0.24429 | 0.015994 | 0.078077 | 0.07543 | 0.12971 | 0.0012047 | -0.0087863 | -0.16037 | -0.010408 | 0.068109 | 0.056971 | 0.0091216 | -0.012614 | 76.3 | 76.5472 | 6.9077 | -45.9869 | 76.7349 | -46.4493 | -46.5225 | -41.2582 | 42.3157 | -46.3257 | 76.7624 | 76.6571 | -46.5317 | -46.5317 | -0.13275 | -0.20599 | 0.073242 | 122.8638 | 0.32959 | 0.53558 | -0.36163 | -0.21515 | -0.21515 | 0.10071 | 5.0583 | -0.009156 | 0.20599 | -0.004578 | 123.0515 | 122.6166 | 53.2242 | -123.1842 | 123.0789 | 122.9736 | 88.6322 | -123.1934
3838.0156 | 123.0606 | -45.9732 | 77.0096 | -0.25192 | 0.016421 | 0.073805 | 0.078421 | 0.12843 | 0.0059045 | -0.0087863 | -0.3511 | -0.0082716 | 0.070886 | 0.057826 | 0.010403 | -0.011974 | 76.6663 | 77.0096 | 7.0221 | -45.5978 | 77.211 | -46.0327 | -46.1334 | -40.9241 | 42.6224 | -46.0648 | 77.0966 | 76.9867 | -46.1792 | -46.2158 | -0.059509 | -0.16022 | 0.20142 | 122.9828 | 0.37537 | 0.53558 | -0.34332 | -0.20599 | -0.24261 | 0.086975 | 5.0491 | -0.091552 | 0.15106 | -0.022889 | 123.1842 | 122.6395 | 52.9953 | -123.143 | 123.0698 | 122.9599 | 88.5956 | -123.2254
3839.0156 | 123.0515 | -46.1334 | 76.8173 | -0.19089 | 0.016635 | 0.073164 | 0.071585 | 0.12693 | 0.0039819 | -0.010068 | -0.20615 | -0.0097668 | 0.068109 | 0.059748 | 0.011685 | -0.012401 | 76.5472 | 76.7395 | 6.958 | -45.7809 | 76.9501 | -46.2479 | -46.3257 | -41.0797 | 42.485 | -46.2479 | 76.8951 | 76.8127 | -46.376 | -46.3989 | -0.11444 | -0.19226 | 0.13275 | 122.8729 | 0.35248 | 0.54474 | -0.27008 | -0.24262 | -0.2655 | 0.07782 | 5.0537 | -0.11444 | 0.15106 | -0.004578 | 123.0835 | 122.6807 | 53.0914 | -123.143 | 123.0286 | 122.9462 | 88.6185 | -123.2162
3840.0156 | 123.0515 | -45.9137 | 77.0645 | -0.25955 | 0.015353 | 0.074232 | 0.074362 | 0.13014 | 0.00099115 | -0.0077183 | 1.5181 | -0.010408 | 0.069391 | 0.058894 | 0.012326 | -0.011119 | 76.8402 | 77.0233 | 6.8756 | -45.488 | 77.2568 | -45.9183 | -46.0419 | -40.86 | 42.7597 | -46.0007 | 77.1606 | 77.1103 | -46.1243 | -46.1334 | -0.004578 | -0.12817 | 0.19226 | 122.937 | 0.42572 | 0.55389 | -0.2243 | -0.21057 | -0.21973 | 0.096131 | 5.0537 | -0.086975 | 0.13275 | 0.045777 | 123.1705 | 122.7539 | 52.7893 | -123.1064 | 123.0743 | 123.024 | 88.6734 | -123.1979
3841.0156 | 123.0606 | -45.8954 | 77.0782 | -0.19089 | 0.017276 | 0.072523 | 0.07479 | 0.13035 | 0.0052637 | -0.0066501 | -0.15274 | -0.0093396 | 0.0711 | 0.055903 | 0.010617 | -0.010692 | 76.8585 | 77.0325 | 6.9946 | -45.5338 | 77.2751 | -45.932 | -46.0693 | -40.7639 | 42.7689 | -45.8862 | 77.2156 | 77.1194 | -46.0556 | -46.0922 | -0.036621 | -0.17395 | 0.19684 | 122.9279 | 0.36163 | 0.53558 | -0.21973 | -0.16022 | -0.19684 | 0.13733 | 5.1315 | 0.009156 | 0.20599 | 0.041199 | 123.1705 | 122.7539 | 52.89 | -123.1476 | 123.111 | 123.0148 | 88.6642 | -123.1705
3842.0156 | 123.0698 | -45.5704 | 77.3621 | -0.19852 | 0.011935 | 0.071882 | 0.071585 | 0.12736 | 0.00013675 | -0.0079319 | -0.11459 | -0.010621 | 0.067896 | 0.06103 | 0.011472 | -0.010905 | 77.124 | 77.3804 | 7.0404 | -45.2225 | 77.4628 | -45.6573 | -45.7352 | -40.4846 | 43.0664 | -45.5612 | 77.4399 | 77.3483 | -45.7993 | -45.8359 | -0.086975 | -0.16479 | 0.10071 | 122.9507 | 0.3479 | 0.5127 | -0.23804 | -0.22888 | -0.2655 | 0.077819 | 5.0858 | 0.009156 | 0.27466 | -0.013733 | 123.0331 | 122.6944 | 52.6108 | -123.0972 | 123.0103 | 122.9187 | 88.6368 | -123.1979
3843.0156 | 123.0331 | -45.1813 | 77.774 | 0.13718 | 0.019626 | 0.07295 | 0.07479 | 0.12864 | 0.0065453 | -0.0055821 | -0.83939 | -0.0086988 | 0.071314 | 0.059748 | 0.012326 | -0.013042 | 77.4948 | 77.8976 | 6.8024 | -44.902 | 77.8748 | -45.2454 | -45.3278 | -40.0726 | 43.2953 | -45.282 | 77.861 | 77.7786 | -45.3827 | -45.4605 | -0.064087 | -0.14648 | 0.10071 | 123.0789 | 0.27923 | 0.42572 | -0.27924 | -0.20142 | -0.27924 | 0.086975 | 5.1086 | -0.10071 | 0.17853 | 0.004577 | 123.056 | 122.6761 | 51.9836 | -123.1018 | 123.0423 | 122.9599 | 88.4766 | -123.2346
3844.0156 | 123.0743 | -45.0073 | 77.9984 | -0.22903 | 0.013217 | 0.074659 | 0.07778 | 0.13163 | -0.00050425 | -0.011136 | -0.13748 | -0.010194 | 0.068537 | 0.059107 | 0.010617 | -0.012614 | 77.6047 | 77.8336 | 6.6833 | -44.7052 | 78.0396 | -45.0897 | -45.2362 | -39.9353 | 43.5242 | -45.0943 | 78.0304 | 77.9617 | -45.2408 | -45.3003 | -0.082398 | -0.22888 | 0.041199 | 122.8409 | 0.30212 | 0.53101 | -0.39368 | -0.23346 | -0.29297 | 0.032044 | 5.072 | -0.086975 | 0.20599 | -0.036621 | 123.0469 | 122.612 | 51.6907 | -123.2346 | 123.0377 | 122.9691 | 88.5315 | -123.2986
3845.0156 | 123.0423 | -45.7352 | 77.243 | -0.22903 | 0.017703 | 0.069746 | 0.075003 | 0.12715 | 0.0012047 | -0.0087863 | -0.20615 | -0.0072034 | 0.067682 | 0.058467 | 0.0097626 | -0.010692 | 76.9592 | 77.0874 | 6.5964 | -45.3964 | 77.3575 | -45.8267 | -45.9274 | -40.6082 | 42.9291 | -45.7672 | 77.2888 | 77.2522 | -45.9778 | -45.9778 | -0.091553 | -0.19226 | 0.11444 | 122.8226 | 0.33875 | 0.53101 | -0.28381 | -0.24262 | -0.24262 | 0.045776 | 5.127 | -0.032044 | 0.21057 | 0.009155 | 123.0927 | 122.6944 | 52.3315 | -123.1705 | 123.024 | 122.9874 | 88.6642 | -123.2208
3846.0156 | 123.0881 | -45.3278 | 77.5818 | -0.19852 | 0.011722 | 0.072096 | 0.074149 | 0.12843 | 0.00077755 | -0.010068 | -0.12985 | -0.010194 | 0.0664 | 0.058467 | 0.013181 | -0.01176 | 77.3621 | 77.6047 | 6.5323 | -44.9936 | 77.6825 | -45.4788 | -45.5795 | -40.1276 | 43.4189 | -45.3278 | 77.6505 | 77.5772 | -45.5612 | -45.5841 | -0.15106 | -0.25177 | 0.10071 | 122.9324 | 0.33417 | 0.58594 | -0.21973 | -0.23346 | -0.25635 | 0.068665 | 5.2002 | 0 | 0.25635 | -0.004578 | 123.0103 | 122.6898 | 51.86 | -123.1613 | 122.9782 | 122.905 | 88.7466 | -123.1659
3847.0156 | 123.0698 | -45.3827 | 77.6276 | -0.20615 | 0.017489 | 0.071668 | 0.073508 | 0.12886 | 0.0069727 | -0.0081455 | -0.23666 | -0.009126 | 0.067896 | 0.05868 | 0.011044 | -0.013255 | 77.2797 | 77.449 | 6.4728 | -45.0165 | 77.6779 | -45.4926 | -45.5795 | -40.1825 | 43.3914 | -45.433 | 77.6688 | 77.5909 | -45.5704 | -45.607 | -0.10986 | -0.19684 | 0.050354 | 122.8317 | 0.36621 | 0.56305 | -0.3479 | -0.18768 | -0.22431 | 0.041199 | 5.2002 | -0.050354 | 0.17395 | -0.036621 | 123.0606 | 122.6624 | 51.8555 | -123.2071 | 123.0515 | 122.9736 | 88.7741 | -123.2346
3848.0312 | 123.1338 | -45.4376 | 77.4673 | 0.18295 | 0.016635 | 0.073805 | 0.074149 | 0.1295 | 0.0052637 | -0.0043003 | 0.24399 | -0.0097668 | 0.06875 | 0.058253 | 0.011899 | -0.010051 | 77.243 | 77.4216 | 6.5552 | -45.0989 | 77.5864 | -45.5109 | -45.6345 | -40.1733 | 43.3136 | -45.3827 | 77.5681 | 77.4765 | -45.6482 | -45.6757 | -0.073242 | -0.19684 | 0.11902 | 122.8592 | 0.33874 | 0.53558 | -0.2243 | -0.21057 | -0.23804 | 0.10071 | 5.2643 | 0.054932 | 0.29297 | 0.009155 | 123.024 | 122.6807 | 51.9928 | -123.1018 | 123.0057 | 122.9141 | 88.7512 | -123.143
3849.0156 | 123.024 | -45.4422 | 77.4994 | 0.030365 | 0.020907 | 0.070387 | 0.07479 | 0.13121 | 0.0067589 | -0.0055821 | 0.045624 | -0.0089124 | 0.069818 | 0.059535 | 0.012753 | -0.013683 | 77.2888 | 77.4353 | 6.5186 | -45.0668 | 77.6779 | -45.488 | -45.6024 | -40.274 | 43.2632 | -45.5933 | 77.5909 | 77.5177 | -45.6711 | -45.7031 | -0.045776 | -0.16022 | 0.17853 | 122.8775 | 0.37537 | 0.53558 | -0.21057 | -0.22888 | -0.26093 | 0.091552 | 5.1682 | -0.15106 | 0.10986 | 0.01831 | 123.1201 | 122.731 | 51.9608 | -123.1018 | 123.0331 | 122.9599 | 88.7054 | -123.2025
3850.0156 | 123.0286 | -45.4605 | 77.536 | -0.23666 | 0.013003 | 0.073164 | 0.073294 | 0.12822 | -7.6852e-05 | -0.0094273 | -0.22903 | -0.0099806 | 0.070673 | 0.057612 | 0.011258 | -0.0094102 | 77.2339 | 77.4902 | 6.3675 | -45.0348 | 77.655 | -45.5017 | -45.6253 | -40.2466 | 43.3868 | -45.4468 | 77.5955 | 77.5131 | -45.6528 | -45.6619 | -0.041199 | -0.16479 | 0.11902 | 122.9507 | 0.42572 | 0.59051 | -0.30212 | -0.19226 | -0.20142 | 0.059509 | 5.2139 | 0.013733 | 0.21515 | -0.022888 | 123.1155 | 122.6944 | 51.828 | -123.1613 | 123.056 | 122.9736 | 88.8474 | -123.1979
3851.0156 | 123.0698 | -45.4651 | 77.504 | -0.21378 | 0.016635 | 0.072736 | 0.075003 | 0.12886 | 0.0048363 | -0.0083591 | -0.15274 | -0.010408 | 0.069818 | 0.057612 | 0.012326 | -0.011974 | 77.2202 | 77.3987 | 6.3263 | -45.0806 | 77.6459 | -45.5246 | -45.6528 | -40.2054 | 43.3594 | -45.4056 | 77.6367 | 77.5177 | -45.6436 | -45.6802 | -0.059509 | -0.18768 | 0.14191 | 122.8638 | 0.38452 | 0.57221 | -0.28381 | -0.17853 | -0.21515 | 0.13275 | 5.2597 | 0.059509 | 0.27466 | 0.013733 | 123.111 | 122.6852 | 51.7914 | -123.1567 | 123.1018 | 122.9828 | 88.8245 | -123.1842
3852.0156 | 123.056 | -45.0577 | 77.9388 | -0.22903 | 0.014499 | 0.073805 | 0.074149 | 0.13185 | 0.0012047 | -0.0096409 | -0.3511 | -0.0097668 | 0.0711 | 0.057826 | 0.010831 | -0.010905 | 77.8656 | 77.8473 | 6.0745 | -44.7327 | 78.0899 | -45.0943 | -45.2454 | -39.8254 | 43.7164 | -45.0668 | 78.0396 | 77.9297 | -45.2591 | -45.2774 | -0.036621 | -0.18768 | 0.15106 | 122.905 | 0.32501 | 0.5127 | -0.073242 | -0.20142 | -0.21973 | 0.10071 | 5.2322 | -0.009155 | 0.21057 | -0.009156 | 123.1476 | 122.9233 | 51.1322 | -123.1842 | 123.0972 | 122.9874 | 88.7741 | -123.2162
3853.0156 | 123.1064 | -45.52 | 77.4307 | 0.14481 | 0.020694 | 0.072523 | 0.075858 | 0.128 | 0.0056909 | -0.0045139 | 0.11429 | -0.010621 | 0.071314 | 0.058894 | 0.012967 | -0.013255 | 77.1332 | 77.2842 | 6.0425 | -45.1675 | 77.6001 | -45.575 | -45.7077 | -40.2878 | 43.2404 | -45.5704 | 77.5131 | 77.4536 | -45.7489 | -45.7535 | -0.054931 | -0.18768 | 0.16937 | 122.8043 | 0.35248 | 0.54016 | -0.29755 | -0.22888 | -0.23346 | 0.082398 | 5.2322 | -0.050354 | 0.1831 | 0.022888 | 123.1201 | 122.6532 | 51.5625 | -123.1384 | 123.0331 | 122.9736 | 88.7604 | -123.1842
3854.0156 | 123.0194 | -45.813 | 77.1378 | -0.22141 | 0.011935 | 0.073591 | 0.073508 | 0.1295 | -0.0013587 | -0.0075047 | 0.037995 | -0.0093396 | 0.068537 | 0.056971 | 0.011685 | -0.011333 | 76.886 | 77.1103 | 6.1111 | -45.4056 | 77.2797 | -45.8725 | -45.9549 | -40.6036 | 43.1305 | -45.8817 | 77.243 | 77.1698 | -46.019 | -46.0602 | -0.05951 | -0.14191 | 0.14191 | 122.9233 | 0.40741 | 0.54932 | -0.25177 | -0.20599 | -0.24719 | 0.10529 | 5.2094 | -0.068665 | 0.17853 | 0.032044 | 123.0927 | 122.699 | 51.9241 | -123.0927 | 123.056 | 122.9828 | 88.9435 | -123.1979
3855.0156 | 123.0698 | -45.5566 | 77.3804 | -0.13748 | 0.018985 | 0.072523 | 0.073721 | 0.12779 | 0.0054773 | -0.0051547 | -0.091705 | -0.008058 | 0.068109 | 0.057185 | 0.012967 | -0.013042 | 77.1973 | 77.3117 | 6.0745 | -45.1218 | 77.5589 | -45.6299 | -45.7169 | -40.2512 | 43.3548 | -45.5978 | 77.4994 | 77.4353 | -45.7626 | -45.7855 | -0.073242 | -0.16022 | 0.17853 | 122.8683 | 0.43488 | 0.59509 | -0.1831 | -0.20599 | -0.22888 | 0.11902 | 5.3055 | -0.041198 | 0.18768 | 0.054932 | 123.1155 | 122.7539 | 51.6312 | -123.0972 | 123.056 | 122.9919 | 88.9114 | -123.1659
3856.0156 | 123.0652 | -45.3461 | 77.6276 | -0.21378 | 0.016421 | 0.073805 | 0.07778 | 0.13099 | 0.0044091 | -0.0085727 | -0.19089 | -0.0093396 | 0.070032 | 0.05868 | 0.012967 | -0.013683 | 77.3849 | 77.5589 | 6.102 | -44.957 | 77.7969 | -45.401 | -45.4788 | -40.0681 | 43.5425 | -45.3323 | 77.7512 | 77.6733 | -45.5429 | -45.5566 | -0.054932 | -0.13275 | 0.16937 | 122.905 | 0.3891 | 0.52185 | -0.24261 | -0.19684 | -0.21057 | 0.1236 | 5.278 | 0.013733 | 0.22431 | 0.045777 | 123.143 | 122.731 | 51.4481 | -123.1064 | 123.0972 | 123.0194 | 88.8885 | -123.1842
3857.0156 | 123.0423 | -45.4651 | 77.4902 | 0.015106 | 0.019626 | 0.073164 | 0.075003 | 0.12928 | 0.0052637 | -0.0040867 | -0.015411 | -0.0078442 | 0.072168 | 0.058039 | 0.014249 | -0.01176 | 77.2522 | 77.4124 | 6.2531 | -45.0348 | 77.6459 | -45.5063 | -45.6207 | -40.242 | 43.4097 | -45.5841 | 77.5909 | 77.4582 | -45.6802 | -45.7169 | -0.041199 | -0.15564 | 0.15564 | 122.8775 | 0.4303 | 0.58594 | -0.23804 | -0.21515 | -0.25177 | 0.10071 | 5.2231 | -0.11902 | 0.13275 | -0.032043 | 123.111 | 122.7173 | 51.7181 | -123.111 | 123.056 | 122.9233 | 88.8748 | -123.2071
3858.0156 | 123.0057 | -45.1675 | 77.7603 | -0.015411 | 0.021762 | 0.072309 | 0.075217 | 0.12779 | 0.0048363 | -0.0060093 | 0.053253 | -0.0089124 | 0.071314 | 0.057398 | 0.014249 | -0.01176 | 77.4261 | 77.5864 | 6.2302 | -44.8471 | 77.8519 | -45.3278 | -45.4559 | -39.8895 | 43.7531 | -45.195 | 77.9068 | 77.8564 | -45.3598 | -45.3735 | -0.16022 | -0.28839 | 0.091553 | 122.7539 | 0.32043 | 0.60883 | -0.33417 | -0.19226 | -0.20599 | 0.14648 | 5.278 | -0.027465 | 0.17853 | 0.09613 | 123.0194 | 122.5937 | 51.3977 | -123.2162 | 123.0743 | 123.024 | 88.9206 | -123.1338
3859.0156 | 123.0469 | -45.4468 | 77.4765 | -0.21378 | 0.01578 | 0.072736 | 0.07543 | 0.1295 | 0.0029137 | -0.0064365 | -0.18326 | -0.007417 | 0.06875 | 0.060176 | 0.011258 | -0.011974 | 77.1927 | 77.3575 | 6.2622 | -45.108 | 77.6093 | -45.5704 | -45.6619 | -40.2054 | 43.5379 | -45.5109 | 77.5635 | 77.5269 | -45.6985 | -45.7169 | -0.1236 | -0.21515 | 0.13275 | 122.8043 | 0.33874 | 0.55389 | -0.28381 | -0.25177 | -0.27008 | 0.086976 | 5.2414 | -0.064087 | 0.20599 | 0.050354 | 123.056 | 122.6395 | 51.709 | -123.1384 | 123.0103 | 122.9736 | 88.9847 | -123.1934
3860.0156 | 123.0789 | -45.7077 | 77.2156 | -0.18326 | 0.016635 | 0.073164 | 0.073508 | 0.13228 | 0.0022729 | -0.0092137 | -0.15274 | -0.0097668 | 0.0711 | 0.059107 | 0.010831 | -0.011333 | 76.9638 | 77.1469 | 6.0791 | -45.3415 | 77.3712 | -45.7855 | -45.8908 | -40.4617 | 43.3228 | -45.7535 | 77.3163 | 77.2614 | -45.932 | -45.9732 | -0.077819 | -0.1831 | 0.15564 | 122.8546 | 0.36621 | 0.54932 | -0.25177 | -0.2243 | -0.2655 | 0.10071 | 5.246 | -0.045776 | 0.21973 | 0.045777 | 123.0789 | 122.6715 | 51.7868 | -123.1064 | 123.024 | 122.9691 | 89.0305 | -123.1888
3861.0156 | 123.0652 | -45.3415 | 77.623 | 0.11429 | 0.02283 | 0.073164 | 0.078207 | 0.13057 | 0.0059045 | -0.0077183 | -0.00015237 | -0.0093396 | 0.068109 | 0.058467 | 0.013394 | -0.012401 | 77.4399 | 77.5864 | 6.2256 | -44.9295 | 77.7832 | -45.369 | -45.4834 | -39.9994 | 43.6707 | -45.3323 | 77.7237 | 77.6505 | -45.5429 | -45.5566 | -0.027466 | -0.14191 | 0.16022 | 122.9279 | 0.41199 | 0.55389 | -0.18311 | -0.20142 | -0.21515 | 0.10071 | 5.3421 | 0.009156 | 0.22431 | 0.027466 | 123.1247 | 122.7814 | 51.5671 | -123.1064 | 123.0652 | 122.9919 | 89.0121 | -123.1796
3862.0156 | 123.0652 | -45.1492 | 77.7832 | -0.18326 | 0.020267 | 0.072309 | 0.076285 | 0.13099 | 0.0044091 | -0.0094273 | -0.076446 | -0.0093396 | 0.070246 | 0.058467 | 0.013394 | -0.012614 | 77.6047 | 77.7832 | 6.0974 | -44.7189 | 77.9388 | -45.2179 | -45.3369 | -39.8392 | 43.8492 | -45.1538 | 77.9205 | 77.8336 | -45.3415 | -45.369 | -0.068665 | -0.18768 | 0.15564 | 122.9324 | 0.4303 | 0.61798 | -0.17853 | -0.19226 | -0.21973 | 0.13733 | 5.3101 | -0.004578 | 0.21515 | 0.050354 | 123.0881 | 122.7539 | 51.2466 | -123.1201 | 123.0698 | 122.9828 | 88.9984 | -123.1522
3863.0156 | 123.143 | -44.8654 | 78.1403 | 0.0914 | 0.02048 | 0.071241 | 0.073294 | 0.12993 | 0.0046227 | -0.0075047 | 0.19058 | -0.0095532 | 0.070886 | 0.060816 | 0.012112 | -0.011119 | 77.8244 | 77.9205 | 6.0745 | -44.4992 | 78.2272 | -44.9661 | -45.0485 | -39.6652 | 43.9316 | -45.0439 | 78.1128 | 78.0624 | -45.108 | -45.1218 | -0.10071 | -0.18311 | 0.086975 | 122.7859 | 0.36621 | 0.54932 | -0.31586 | -0.24262 | -0.25635 | -0.027466 | 5.2002 | -0.17853 | 0.07782 | -0.07782 | 123.0927 | 122.6898 | 50.9399 | -123.1888 | 122.9782 | 122.9279 | 88.797 | -123.262
3864.0156 | 123.0927 | -44.8242 | 78.1219 | -0.16037 | 0.021121 | 0.073377 | 0.073081 | 0.128 | 0.0050499 | -0.0060093 | -0.023041 | -0.0086988 | 0.069391 | 0.058253 | 0.011472 | -0.012828 | 77.8976 | 78.1036 | 6.1752 | -44.3939 | 78.2776 | -44.8746 | -44.989 | -39.505 | 44.1147 | -44.8105 | 78.2043 | 78.1586 | -45.0256 | -45.0623 | -0.050354 | -0.16479 | 0.15564 | 122.9279 | 0.4303 | 0.59509 | -0.2243 | -0.20142 | -0.23804 | 0.082398 | 5.3192 | 0.013733 | 0.25177 | 0.036621 | 123.1018 | 122.7219 | 50.9995 | -123.111 | 123.0286 | 122.9828 | 88.9389 | -123.1842
3865.0156 | 123.056 | -44.751 | 78.2547 | 0.022736 | 0.021762 | 0.074445 | 0.075217 | 0.12864 | 0.0059045 | -0.0083591 | -0.00015237 | -0.008058 | 0.070246 | 0.058894 | 0.01254 | -0.012187 | 77.948 | 78.0853 | 6.2668 | -44.3573 | 78.3371 | -44.8471 | -44.9432 | -39.4684 | 44.2245 | -44.7968 | 78.3096 | 78.2639 | -44.9524 | -44.9753 | -0.09613 | -0.19226 | 0.082397 | 122.8363 | 0.39368 | 0.58594 | -0.3067 | -0.20142 | -0.2243 | 0.054931 | 5.2826 | -0.045776 | 0.17853 | 0.009155 | 123.0881 | 122.699 | 51.0178 | -123.1979 | 123.0606 | 123.0148 | 88.9755 | -123.23
3866.0156 | 123.0698 | -44.8608 | 78.0899 | -0.19089 | 0.015567 | 0.074018 | 0.075003 | 0.13185 | 0.00077755 | -0.0081455 | -0.10696 | -0.008058 | 0.069605 | 0.059535 | 0.013608 | -0.013896 | 77.8107 | 77.9709 | 6.2164 | -44.4992 | 78.2089 | -44.9387 | -45.0439 | -39.5554 | 44.1513 | -44.838 | 78.2089 | 78.1403 | -45.0851 | -45.108 | -0.07782 | -0.1831 | 0.11902 | 122.8317 | 0.36163 | 0.54474 | -0.27924 | -0.2243 | -0.24719 | 0.11902 | 5.3055 | 0.022888 | 0.27008 | 0.050354 | 123.0698 | 122.6715 | 51.0773 | -123.1338 | 123.0698 | 123.0011 | 89.0121 | -123.1979
3867.0156 | 123.0469 | -45.1355 | 77.829 | -0.47318 | 0.018344 | 0.073805 | 0.075003 | 0.13057 | 0.0035547 | -0.0062229 | -0.023041 | -0.0067762 | 0.070886 | 0.058467 | 0.013394 | -0.013683 | 77.6321 | 77.7832 | 6.189 | -44.7144 | 77.948 | -45.1904 | -45.2866 | -39.7797 | 43.8904 | -45.1675 | 77.916 | 77.8564 | -45.3415 | -45.3781 | -0.054932 | -0.15106 | 0.11902 | 122.9187 | 0.42114 | 0.57221 | -0.19684 | -0.20599 | -0.24262 | 0.086976 | 5.3558 | -0.032044 | 0.21057 | 0.027466 | 123.0835 | 122.7676 | 51.3245 | -123.1155 | 123.0515 | 122.9919 | 89.0259 | -123.2071
3868.0156 | 123.0286 | -45.4605 | 77.5085 | -0.00015269 | 0.02048 | 0.070387 | 0.073081 | 0.12928 | 0.0073999 | -0.0070773 | 0.068512 | -0.0099806 | 0.071314 | 0.056117 | 0.012112 | -0.013683 | 77.2934 | 77.4216 | 6.1478 | -45.0485 | 77.6505 | -45.5292 | -45.6207 | -40.0909 | 43.6111 | -45.5154 | 77.6276 | 77.5452 | -45.6711 | -45.7077 | -0.068665 | -0.16022 | 0.14191 | 122.8821 | 0.41199 | 0.5722 | -0.21515 | -0.21057 | -0.24719 | 0.11902 | 5.3696 | -0.054932 | 0.19226 | 0.036621 | 123.111 | 122.7539 | 51.6083 | -123.1293 | 123.0881 | 123.0057 | 89.0717 | -123.2162
3869.0156 | 123.056 | -45.52 | 77.4307 | 0.31265 | 0.017917 | 0.071882 | 0.073721 | 0.12779 | 0.0035547 | -0.0053683 | 0.19058 | -0.0072034 | 0.070673 | 0.059535 | 0.011899 | -0.011333 | 77.1927 | 77.3071 | 6.134 | -45.0806 | 77.6093 | -45.5383 | -45.6207 | -40.1459 | 43.5196 | -45.5795 | 77.5452 | 77.4857 | -45.7443 | -45.7581 | -0.01831 | -0.10071 | 0.17853 | 122.8271 | 0.43945 | 0.54016 | -0.23804 | -0.2243 | -0.23804 | 0.11444 | 5.3741 | -0.059509 | 0.17853 | 0.054932 | 123.1293 | 122.7127 | 51.6541 | -123.0515 | 123.0652 | 123.0057 | 89.0396 | -123.1888
3870.0156 | 123.1018 | -45.0439 | 77.9068 | -0.168 | 0.01813 | 0.070173 | 0.075858 | 0.12971 | 0.0039819 | -0.0077183 | -0.038299 | -0.0093396 | 0.068964 | 0.055689 | 0.013394 | -0.010905 | 77.6413 | 77.8107 | 6.3217 | -44.6823 | 78.035 | -45.163 | -45.2499 | -39.6927 | 44.0186 | -45.0943 | 77.98 | 77.8793 | -45.3003 | -45.3232 | -0.11902 | -0.20599 | 0.12817 | 122.8546 | 0.36163 | 0.56763 | -0.2655 | -0.25635 | -0.27924 | 0.073243 | 5.3513 | -0.050354 | 0.22888 | -0.027466 | 123.0789 | 122.6852 | 51.3657 | -123.1567 | 123.024 | 122.9233 | 89.0625 | -123.23
3871.0156 | 123.0194 | -45.0073 | 77.9434 | -0.00015269 | 0.020694 | 0.071455 | 0.074362 | 0.12886 | 0.0046227 | -0.0053683 | 0.037995 | -0.011049 | 0.070886 | 0.058467 | 0.013181 | -0.01176 | 77.7008 | 77.8473 | 6.4178 | -44.6182 | 78.0899 | -45.0714 | -45.1767 | -39.6606 | 43.9957 | -45.0577 | 78.0533 | 77.9938 | -45.2362 | -45.2637 | -0.064087 | -0.16937 | 0.14648 | 122.8546 | 0.3891 | 0.55847 | -0.24261 | -0.22888 | -0.25635 | 0.10986 | 5.3467 | -0.050354 | 0.20599 | 0.050354 | 123.0972 | 122.7081 | 51.4252 | -123.1201 | 123.0606 | 123.0011 | 89.003 | -123.2071
3872.0156 | 123.0606 | -45.5154 | 77.4353 | -0.13748 | 0.019412 | 0.071668 | 0.072012 | 0.13014 | 0.0027001 | -0.0060093 | -0.11459 | -0.0095532 | 0.06875 | 0.059107 | 0.010617 | -0.011974 | 77.2064 | 77.3666 | 6.3538 | -45.0668 | 77.5726 | -45.5795 | -45.6894 | -40.1093 | 43.6935 | -45.5292 | 77.5543 | 77.4765 | -45.7123 | -45.7306 | -0.064087 | -0.17395 | 0.13733 | 122.8821 | 0.44861 | 0.62256 | -0.22888 | -0.19684 | -0.21515 | 0.11902 | 5.4062 | -0.013733 | 0.20142 | 0.041198 | 123.0881 | 122.7219 | 51.8692 | -123.1247 | 123.0698 | 122.9919 | 89.209 | -123.1659
3873.0156 | 123.143 | -45.4788 | 77.3849 | 0.16769 | 0.013858 | 0.075086 | 0.070731 | 0.13057 | -0.0030677 | -0.0083591 | 0.32028 | -0.010194 | 0.068323 | 0.057398 | 0.011044 | -0.010905 | 77.2247 | 77.4445 | 6.4774 | -45.0348 | 77.4902 | -45.5475 | -45.6848 | -40.0497 | 43.7073 | -45.488 | 77.4811 | 77.4307 | -45.7031 | -45.7489 | -0.068664 | -0.20599 | 0.10528 | 122.9233 | 0.44403 | 0.65002 | -0.16022 | -0.2243 | -0.27008 | 0.09613 | 5.4291 | -0.009155 | 0.26092 | 0.045776 | 122.9691 | 122.7036 | 51.9562 | -123.0698 | 122.9599 | 122.9095 | 89.1861 | -123.1338
3874.0156 | 123.0469 | -45.3644 | 77.5635 | -0.13748 | 0.016421 | 0.072096 | 0.075003 | 0.13057 | 0.0052637 | -0.0068637 | -0.053558 | -0.010194 | 0.069391 | 0.056758 | 0.014035 | -0.013255 | 77.3483 | 77.4765 | 6.4178 | -44.9295 | 77.6962 | -45.4788 | -45.5795 | -39.9307 | 43.7988 | -45.4193 | 77.6825 | 77.6093 | -45.5795 | -45.6024 | -0.11444 | -0.21515 | 0.13275 | 122.8409 | 0.43488 | 0.65002 | -0.21515 | -0.21515 | -0.23804 | 0.11902 | 5.4337 | -0.054932 | 0.18311 | 0.045776 | 123.0606 | 122.7127 | 51.7822 | -123.143 | 123.0469 | 122.9736 | 89.1632 | -123.1659
3875.0156 | 123.0103 | -45.6619 | 77.2842 | 0.030365 | 0.019839 | 0.071455 | 0.073721 | 0.13163 | 0.0067589 | -0.0077183 | 0.14481 | -0.0076306 | 0.069818 | 0.059962 | 0.013181 | -0.013683 | 76.9959 | 77.1194 | 6.2759 | -45.3232 | 77.3895 | -45.7489 | -45.8725 | -40.274 | 43.4143 | -45.7581 | 77.3621 | 77.2522 | -45.8771 | -45.9457 | -0.086975 | -0.21057 | 0.10529 | 122.7814 | 0.33875 | 0.54932 | -0.28839 | -0.21515 | -0.28381 | 0.07782 | 5.3879 | -0.096131 | 0.18768 | -0.032044 | 123.0515 | 122.6578 | 51.9379 | -123.1567 | 123.024 | 122.9141 | 89.0762 | -123.23
3876.0156 | 123.0377 | -45.163 | 77.829 | 0.030365 | 0.018985 | 0.073377 | 0.075003 | 0.13078 | 0.0076135 | -0.0062229 | 0.015106 | -0.0082716 | 0.070673 | 0.058039 | 0.013394 | -0.011974 | 77.5909 | 77.7191 | 6.4453 | -44.751 | 77.98 | -45.2087 | -45.3049 | -39.7247 | 43.959 | -45.2271 | 77.8885 | 77.8427 | -45.3918 | -45.4056 | -0.045776 | -0.14191 | 0.15106 | 122.8821 | 0.41199 | 0.55389 | -0.23804 | -0.22888 | -0.24262 | 0.05951 | 5.4382 | -0.064087 | 0.17853 | 0.013733 | 123.143 | 122.7539 | 51.6083 | -123.1338 | 123.0515 | 123.0057 | 89.122 | -123.2346
3877.0156 | 123.1522 | -44.9661 | 77.9297 | 0.18295 | 0.015567 | 0.073164 | 0.072226 | 0.12886 | 0.0033411 | -0.0064365 | 0.2211 | -0.0078442 | 0.069391 | 0.058467 | 0.011044 | -0.0098374 | 77.6093 | 77.7649 | 6.4041 | -44.6548 | 77.98 | -45.1538 | -45.2637 | -39.5279 | 44.101 | -45.0302 | 77.9984 | 77.9297 | -45.2133 | -45.2225 | -0.18768 | -0.29755 | 0.050355 | 122.731 | 0.31128 | 0.60883 | -0.32043 | -0.24719 | -0.25635 | 0.068665 | 5.4382 | -0.064087 | 0.19226 | 0 | 122.9462 | 122.5754 | 51.3702 | -123.1934 | 122.9645 | 122.8958 | 89.0671 | -123.1522
3878.0156 | 123.1293 | -44.9753 | 77.8976 | 0.17532 | 0.02048 | 0.074018 | 0.073721 | 0.13014 | 0.0050499 | -0.0075047 | 0.23636 | -0.0084852 | 0.070459 | 0.058039 | 0.012967 | -0.011546 | 77.7557 | 77.9068 | 6.4224 | -44.5816 | 78.1082 | -45.0348 | -45.1309 | -39.4775 | 44.1833 | -44.9707 | 78.0396 | 78.0167 | -45.1859 | -45.195 | -0.059509 | -0.15564 | 0.21057 | 122.8821 | 0.39368 | 0.54932 | -0.14191 | -0.21057 | -0.21973 | 0.14191 | 5.4977 | 0.004578 | 0.2243 | 0.11902 | 123.0835 | 122.731 | 51.3977 | -123.0286 | 123.0148 | 122.9919 | 89.1586 | -123.0927
3879.0156 | 123.0331 | -45.2866 | 77.6596 | -0.023041 | 0.021121 | 0.073591 | 0.07244 | 0.12843 | 0.0048363 | -0.0079319 | 0.015106 | -0.0086988 | 0.073664 | 0.059321 | 0.012326 | -0.012401 | 77.4857 | 77.5864 | 6.3721 | -44.8654 | 77.829 | -45.3369 | -45.4468 | -39.7659 | 43.8629 | -45.3049 | 77.7924 | 77.7512 | -45.4697 | -45.5109 | -0.050354 | -0.16022 | 0.16937 | 122.8729 | 0.42114 | 0.58136 | -0.17395 | -0.18311 | -0.2243 | 0.13275 | 5.5206 | -0.018311 | 0.20599 | 0.091553 | 123.1155 | 122.7722 | 51.6586 | -123.1064 | 123.0789 | 123.0377 | 89.1495 | -123.1705
3880.0156 | 123.0103 | -44.9112 | 78.067 | -0.045929 | 0.019626 | 0.071882 | 0.073294 | 0.12993 | 0.0063317 | -0.0072911 | 0.060883 | -0.0089124 | 0.070886 | 0.057612 | 0.012967 | -0.012187 | 77.8336 | 77.9709 | 6.1844 | -44.4855 | 78.1769 | -44.9753 | -45.0806 | -39.4226 | 44.2703 | -44.9478 | 78.154 | 78.0899 | -45.108 | -45.1401 | -0.064087 | -0.16937 | 0.10986 | 122.8821 | 0.42572 | 0.59509 | -0.23346 | -0.19684 | -0.22888 | 0.086975 | 5.4886 | -0.036621 | 0.19226 | 0.022888 | 123.0881 | 122.7448 | 51.0956 | -123.1476 | 123.0652 | 123.0011 | 89.1815 | -123.2071
3881.0156 | 123.0881 | -44.7327 | 78.1906 | 0.15244 | 0.01813 | 0.074445 | 0.07244 | 0.12843 | 0.0041955 | -0.0068637 | 0.2211 | -0.0095532 | 0.072382 | 0.059321 | 0.0093354 | -0.011546 | 77.9388 | 78.0762 | 6.5231 | -44.3573 | 78.3279 | -44.8196 | -44.9203 | -39.2258 | 44.4031 | -44.7556 | 78.3005 | 78.2455 | -44.9615 | -44.9799 | -0.086975 | -0.18768 | 0.13733 | 122.8088 | 0.37537 | 0.56305 | -0.25177 | -0.22888 | -0.24719 | 0.10986 | 5.5069 | -0.022888 | 0.2243 | 0.054931 | 123.0606 | 122.6715 | 51.2558 | -123.111 | 123.0331 | 122.9782 | 89.1357 | -123.1705
3882.0156 | 123.0377 | -44.957 | 77.9572 | -0.03067 | 0.019412 | 0.073377 | 0.073935 | 0.12907 | 0.0063317 | -0.0070773 | -0.0077819 | -0.0095532 | 0.073877 | 0.059962 | 0.013394 | -0.012187 | 77.7283 | 77.8336 | 6.5048 | -44.6045 | 78.035 | -45.0851 | -45.2133 | -39.4272 | 44.2337 | -44.9936 | 78.0807 | 77.9938 | -45.1721 | -45.2316 | -0.12817 | -0.25635 | 0.07782 | 122.7905 | 0.35248 | 0.60883 | -0.22888 | -0.21515 | -0.27466 | 0.1236 | 5.5298 | -0.036621 | 0.23804 | 0.036621 | 122.9919 | 122.6852 | 51.4618 | -123.1705 | 123.0377 | 122.9507 | 89.1907 | -123.1888
3883.0156 | 123.1201 | -44.7281 | 78.1769 | 0.18295 | 0.015353 | 0.074659 | 0.071158 | 0.1295 | 0.00035035 | -0.0070773 | -0.72494 | -0.010835 | 0.06875 | 0.058039 | 0.01254 | -0.0098374 | 78.0121 | 78.1723 | 6.6971 | -44.2841 | 78.2867 | -44.8013 | -44.9112 | -39.1571 | 44.4901 | -44.7052 | 78.2364 | 78.2043 | -44.9341 | -44.9753 | -0.073243 | -0.18311 | 0.10986 | 122.9004 | 0.44403 | 0.62714 | -0.16479 | -0.20599 | -0.24719 | 0.059509 | 5.571 | 0.022888 | 0.27008 | 0.027466 | 123.0148 | 122.7402 | 51.4252 | -123.0881 | 122.9645 | 122.9324 | 89.2181 | -123.1522
3884.0156 | 123.0652 | -44.8151 | 78.2043 | 0.0074768 | 0.02048 | 0.073591 | 0.074362 | 0.1295 | 0.0052637 | -0.0047275 | 0.030365 | -0.009126 | 0.071741 | 0.058894 | 0.012753 | -0.013469 | 77.9251 | 78.0212 | 6.5094 | -44.3802 | 78.3005 | -44.8608 | -44.9661 | -39.299 | 44.3481 | -44.902 | 78.2639 | 78.2089 | -45.0165 | -45.0485 | -0.045777 | -0.15106 | 0.09613 | 122.8363 | 0.43488 | 0.58594 | -0.27924 | -0.20142 | -0.23346 | 0.059509 | 5.5161 | -0.086976 | 0.14648 | 0.004577 | 123.1155 | 122.7402 | 51.3245 | -123.1705 | 123.0789 | 123.024 | 89.1632 | -123.2529
3885.0156 | 123.1522 | -44.5816 | 78.3325 | 0.17532 | 0.018985 | 0.073805 | 0.071585 | 0.13014 | 0.0014185 | -0.0079319 | 0.21347 | -0.0097668 | 0.072168 | 0.056971 | 0.01254 | -0.011974 | 78.1036 | 78.2318 | 6.5369 | -44.2245 | 78.479 | -44.6594 | -44.8105 | -39.0152 | 44.6091 | -44.5358 | 78.4287 | 78.392 | -44.8059 | -44.7922 | -0.07782 | -0.22888 | 0.14648 | 122.8134 | 0.35706 | 0.58594 | -0.22888 | -0.2243 | -0.21057 | 0.09613 | 5.5664 | 0.045776 | 0.25635 | 0.059509 | 123.0606 | 122.6852 | 51.1185 | -123.143 | 123.0103 | 122.9736 | 89.1907 | -123.1247
3886.0312 | 123.0331 | -44.4992 | 78.4607 | -0.22903 | 0.016421 | 0.072736 | 0.072226 | 0.13099 | -0.0019995 | -0.010495 | -0.015411 | -0.0089124 | 0.069391 | 0.056117 | 0.012967 | -0.011333 | 78.3096 | 78.1357 | 6.5598 | -44.0735 | 78.6072 | -44.5999 | -44.6777 | -38.9923 | 44.6869 | -44.5541 | 78.5431 | 78.5019 | -44.7281 | -44.7372 | -0.10071 | -0.17853 | 0.14648 | 122.6349 | 0.42572 | 0.60425 | -0.15106 | -0.22888 | -0.23804 | 0.082398 | 5.5069 | -0.054931 | 0.18311 | 0.041199 | 123.1064 | 122.8088 | 51.059 | -123.1384 | 123.0423 | 123.0011 | 89.1861 | -123.1979
3887.0625 | 123.1567 | -44.7372 | 78.1448 | 0.91537 | 0.014071 | 0.07765 | 0.072867 | 0.12843 | -0.00029045 | -0.0089999 | -0.00015237 | -0.0099806 | 0.070459 | 0.056758 | 0.0086944 | -0.012401 | 78.0396 | 78.1906 | 6.8298 | -44.2612 | 78.3051 | -44.7784 | -44.9066 | -39.1479 | 44.5496 | -44.7189 | 78.241 | 78.1631 | -44.9753 | -44.989 | -0.041198 | -0.16937 | 0.16022 | 122.9279 | 0.47607 | 0.64545 | -0.10528 | -0.23804 | -0.25177 | 0.096131 | 5.5893 | 0.018311 | 0.27008 | 0.018311 | 123.0423 | 122.7768 | 51.5671 | -123.0515 | 122.9782 | 122.9004 | 89.2868 | -123.1338
3888.0156 | 123.0743 | -44.7189 | 78.2318 | 0.18295 | 0.018771 | 0.07295 | 0.071158 | 0.12993 | 0.0054773 | -0.0070773 | 0.17532 | -0.0084852 | 0.067255 | 0.058039 | 0.013821 | -0.011974 | 77.98 | 78.0762 | 6.633 | -44.3481 | 78.3417 | -44.8151 | -44.9387 | -39.1479 | 44.4443 | -44.7876 | 78.3371 | 78.2227 | -44.9432 | -44.9661 | -0.09613 | -0.21973 | 0.10986 | 122.7951 | 0.37079 | 0.59051 | -0.25177 | -0.2243 | -0.24719 | 0.10528 | 5.571 | -0.068665 | 0.17853 | -0.009156 | 123.0606 | 122.699 | 51.3519 | -123.1705 | 123.056 | 122.9416 | 89.1632 | -123.1979
3889.0156 | 123.1384 | -44.7052 | 78.1815 | 0.20584 | 0.016849 | 0.073591 | 0.071158 | 0.12907 | 0.0029137 | -0.0077183 | 0.26688 | -0.0089124 | 0.073023 | 0.058467 | 0.012753 | -0.011974 | 78.035 | 78.154 | 6.7429 | -44.2795 | 78.3463 | -44.7647 | -44.8654 | -39.0427 | 44.5724 | -44.7052 | 78.2867 | 78.2227 | -44.9112 | -44.9387 | -0.059509 | -0.16022 | 0.16479 | 122.8592 | 0.42572 | 0.58594 | -0.14649 | -0.20599 | -0.23346 | 0.10528 | 5.6625 | 0 | 0.23346 | 0.041198 | 123.0515 | 122.7402 | 51.4481 | -123.0469 | 122.9919 | 122.9279 | 89.2776 | -123.1201
3890.0156 | 123.0743 | -45.0027 | 77.9343 | -1.3429 | 0.019412 | 0.071668 | 0.077139 | 0.13035 | 0.0048363 | -0.0092137 | -0.061188 | -0.0086988 | 0.070246 | 0.059321 | 0.013394 | -0.014323 | 77.7832 | 77.8702 | 6.4224 | -44.5633 | 78.0945 | -45.076 | -45.1996 | -39.3448 | 44.3481 | -45.0531 | 78.0258 | 78.0075 | -45.2042 | -45.2362 | -0.073242 | -0.19684 | 0.16022 | 122.8729 | 0.43945 | 0.63629 | -0.15106 | -0.20142 | -0.23346 | 0.091553 | 5.658 | -0.050354 | 0.18311 | 0.073242 | 123.0972 | 122.7859 | 51.4252 | -123.1338 | 123.0286 | 123.0103 | 89.3509 | -123.1705
3891.0156 | 123.1155 | -44.6136 | 78.3508 | 0.030365 | 0.02048 | 0.072309 | 0.07244 | 0.12971 | 0.0067589 | -0.0049411 | 0.12192 | -0.007417 | 0.070032 | 0.060816 | 0.013394 | -0.01176 | 78.0853 | 78.1906 | 6.5277 | -44.1971 | 78.511 | -44.6686 | -44.783 | -38.9969 | 44.6045 | -44.6823 | 78.4973 | 78.4012 | -44.7876 | -44.8242 | -0.054932 | -0.16937 | 0.16022 | 122.8043 | 0.41656 | 0.58594 | -0.2655 | -0.17395 | -0.21057 | 0.14648 | 5.6168 | -0.068665 | 0.14191 | 0.050354 | 123.1247 | 122.699 | 51.1414 | -123.1338 | 123.111 | 123.0148 | 89.2181 | -123.175
3892.0156 | 123.0652 | -44.6365 | 78.3005 | -0.13748 | 0.021121 | 0.076154 | 0.075003 | 0.13099 | 0.0054773 | -0.0057957 | -0.17563 | -0.0076306 | 0.069391 | 0.059962 | 0.014249 | -0.010265 | 78.0624 | 78.3371 | 6.9122 | -44.2657 | 78.4698 | -44.6823 | -44.8151 | -38.9328 | 44.4672 | -44.6503 | 78.4103 | 78.3554 | -44.8196 | -44.87 | -0.045776 | -0.17853 | 0.16937 | 122.9736 | 0.37079 | 0.54932 | -0.23804 | -0.1831 | -0.23346 | 0.10986 | 5.7037 | -0.013733 | 0.21973 | 0.054932 | 123.1064 | 122.699 | 51.5488 | -123.1155 | 123.0469 | 122.9919 | 89.1037 | -123.1705
3893.0156 | 123.0377 | -44.6503 | 78.3371 | 0.12192 | 0.020053 | 0.073591 | 0.069022 | 0.12886 | 0.0048363 | -0.0098545 | 0.068512 | -0.0082716 | 0.071314 | 0.059535 | 0.011899 | -0.010478 | 78.3875 | 78.0716 | 6.601 | -44.1788 | 78.4836 | -44.6823 | -44.8013 | -38.9465 | 44.6777 | -44.6777 | 78.4149 | 78.3783 | -44.8334 | -44.8563 | -0.032043 | -0.15106 | 0.14648 | 122.7219 | 0.4715 | 0.62256 | 0.050354 | -0.1831 | -0.20599 | 0.07782 | 5.7037 | -0.027465 | 0.17853 | 0.041199 | 123.1339 | 123.0377 | 51.2512 | -123.1384 | 123.0652 | 123.0286 | 89.328 | -123.1934
3894.0156 | 123.0698 | -44.6182 | 78.3234 | -0.084076 | 0.022189 | 0.071455 | 0.072867 | 0.13057 | 0.0059045 | -0.0089999 | -0.061188 | -0.0097668 | 0.070032 | 0.057398 | 0.010403 | -0.011119 | 78.0991 | 78.2593 | 6.7795 | -44.1788 | 78.4378 | -44.7098 | -44.7968 | -38.9099 | 44.7327 | -44.6274 | 78.4515 | 78.3875 | -44.8105 | -44.87 | -0.091553 | -0.17853 | 0.11444 | 122.8775 | 0.43945 | 0.61798 | -0.2243 | -0.19226 | -0.25177 | 0.12817 | 5.7083 | -0.009155 | 0.24262 | 0.064087 | 123.056 | 122.7173 | 51.3977 | -123.1201 | 123.0698 | 123.0057 | 89.3509 | -123.1934
3895.0156 | 123.0652 | -44.7739 | 78.1815 | 0.13718 | 0.021335 | 0.072523 | 0.07479 | 0.12971 | 0.0018457 | -0.0079319 | 0.2211 | -0.0093396 | 0.072382 | 0.059321 | 0.012967 | -0.011546 | 77.8885 | 78.035 | 6.7108 | -44.4031 | 78.2776 | -44.8654 | -44.9661 | -39.0427 | 44.4443 | -44.751 | 78.2867 | 78.1952 | -44.9982 | -45.0119 | -0.091552 | -0.19226 | 0.09613 | 122.8088 | 0.37079 | 0.56305 | -0.29297 | -0.2243 | -0.23804 | 0.10528 | 5.7312 | 0.022888 | 0.26093 | 0.013732 | 123.0515 | 122.6624 | 51.4847 | -123.1476 | 123.0606 | 122.9691 | 89.2181 | -123.1934
3896.0156 | 123.0286 | -44.7052 | 78.241 | 0.076141 | 0.020267 | 0.073377 | 0.074576 | 0.128 | 0.0041955 | -0.0083591 | 0.022736 | -0.0082716 | 0.0711 | 0.057612 | 0.015317 | -0.013255 | 78.0441 | 78.1677 | 6.7154 | -44.2245 | 78.4287 | -44.7235 | -44.8425 | -38.9923 | 44.632 | -44.783 | 78.392 | 78.3279 | -44.9066 | -44.9387 | -0.018311 | -0.13733 | 0.18768 | 122.8729 | 0.48065 | 0.61798 | -0.19684 | -0.20142 | -0.23346 | 0.15106 | 5.7129 | -0.07782 | 0.15564 | 0.086975 | 123.1338 | 122.7493 | 51.4206 | -123.0835 | 123.0972 | 123.0331 | 89.3372 | -123.1796
3897.0156 | 123.1705 | -44.5679 | 78.2959 | 0.11429 | 0.016421 | 0.073164 | 0.071372 | 0.13185 | 0.00099115 | -0.0072911 | 0.28976 | -0.008058 | 0.070032 | 0.060603 | 0.010831 | -0.011333 | 78.1494 | 78.3142 | 6.7978 | -44.1376 | 78.4287 | -44.6594 | -44.7556 | -38.6948 | 44.7189 | -44.5358 | 78.3691 | 78.3417 | -44.8105 | -44.8334 | -0.091553 | -0.18768 | 0.13275 | 122.8821 | 0.4303 | 0.61798 | -0.14648 | -0.24262 | -0.2655 | 0.073243 | 5.8731 | 0.032043 | 0.29755 | 0.045777 | 122.9965 | 122.7173 | 51.3657 | -123.0515 | 122.937 | 122.9095 | 89.2868 | -123.1293
3898.0156 | 123.0423 | -44.4351 | 78.5065 | 1.4113 | 0.019839 | 0.073591 | 0.073294 | 0.12993 | 0.0067589 | -0.0064365 | 0.18295 | -0.0078442 | 0.06875 | 0.058039 | 0.011472 | -0.011333 | 78.3279 | 78.3554 | 6.6513 | -44.0094 | 78.6896 | -44.4855 | -44.6136 | -38.6398 | 44.9112 | -44.4305 | 78.6484 | 78.5843 | -44.6411 | -44.6777 | -0.050354 | -0.17853 | 0.18311 | 122.7905 | 0.42572 | 0.60425 | -0.17853 | -0.20599 | -0.24261 | 0.14191 | 5.7953 | 0.004578 | 0.24719 | 0.07782 | 123.1247 | 122.7631 | 51.0864 | -123.1201 | 123.0835 | 123.0194 | 89.3463 | -123.1842
3899.0156 | 122.9828 | -44.8471 | 78.1311 | 0.037994 | 0.017703 | 0.071027 | 0.072226 | 0.12822 | 0.0018457 | -0.0066501 | 0.13718 | -0.0082716 | 0.071741 | 0.058253 | 0.012112 | -0.013683 | 77.8748 | 77.9663 | 6.6925 | -44.4077 | 78.2684 | -44.9112 | -45.0119 | -39.0793 | 44.5312 | -44.9387 | 78.2227 | 78.1586 | -45.0577 | -45.1035 | -0.064087 | -0.16479 | 0.13733 | 122.8134 | 0.43945 | 0.60425 | -0.25635 | -0.21057 | -0.25635 | 0.091552 | 5.7678 | -0.091553 | 0.16479 | 0.027465 | 123.1155 | 122.7219 | 51.5396 | -123.143 | 123.0698 | 123.0057 | 89.3784 | -123.2346
3900.0156 | 123.0789 | -44.2841 | 78.685 | -0.084076 | 0.020267 | 0.071455 | 0.076285 | 0.12907 | 0.0050499 | -0.0072911 | -1.3124 | -0.0089124 | 0.069818 | 0.061457 | 0.012753 | -0.012614 | 78.5019 | 78.6163 | 6.7978 | -43.8126 | 78.8361 | -44.3344 | -44.4305 | -38.4293 | 45.1126 | -44.2932 | 78.7811 | 78.7491 | -44.4305 | -44.4946 | -0.050354 | -0.14648 | 0.15106 | 122.9004 | 0.4715 | 0.61798 | -0.18311 | -0.14648 | -0.21057 | 0.09613 | 5.8548 | -0.009155 | 0.20142 | 0.064086 | 123.1201 | 122.7859 | 51.0818 | -123.1155 | 123.0652 | 123.0331 | 89.3967 | -123.1796
3901.0156 | 123.024 | -44.3436 | 78.6346 | 0.12192 | 0.019198 | 0.071455 | 0.074362 | 0.12822 | 0.0027001 | -0.0079319 | 0.83908 | -0.008058 | 0.070673 | 0.058253 | 0.01254 | -0.012401 | 78.3325 | 78.447 | 6.752 | -43.895 | 78.7674 | -44.3848 | -44.5175 | -38.5712 | 44.9844 | -44.3893 | 78.7216 | 78.6804 | -44.5358 | -44.5953 | -0.041199 | -0.17395 | 0.13275 | 122.7905 | 0.44861 | 0.62256 | -0.30212 | -0.19226 | -0.25177 | 0.086975 | 5.7724 | -0.045776 | 0.20599 | 0.045776 | 123.111 | 122.6761 | 51.0956 | -123.1522 | 123.0652 | 123.024 | 89.328 | -123.23
3902.0156 | 123.143 | -44.2657 | 78.6713 | -0.24429 | 0.021121 | 0.071027 | 0.07479 | 0.12928 | 0.0041955 | -0.0060093 | -0.099335 | -0.010835 | 0.0711 | 0.058039 | 0.011472 | -0.011333 | 78.4332 | 78.5706 | 6.7154 | -43.8354 | 78.7903 | -44.3756 | -44.4946 | -38.4705 | 45.076 | -44.3253 | 78.7582 | 78.6896 | -44.5084 | -44.4992 | -0.10986 | -0.22888 | 0.11902 | 122.8363 | 0.4303 | 0.65918 | -0.23804 | -0.24262 | -0.23346 | 0.086975 | 5.7953 | -0.059509 | 0.17395 | 0.01831 | 123.056 | 122.699 | 50.9811 | -123.1659 | 123.024 | 122.9553 | 89.3417 | -123.1705
3903.0156 | 123.0469 | -43.8309 | 79.1153 | 0.28213 | 0.01813 | 0.071882 | 0.072226 | 0.12928 | 0.0031273 | -0.0045139 | 0.2211 | -0.0082716 | 0.070246 | 0.058039 | 0.01254 | -0.0096238 | 78.8589 | 78.9825 | 6.7154 | -43.396 | 79.2526 | -43.927 | -44.0094 | -38.0173 | 45.3827 | -43.8538 | 79.1885 | 79.129 | -44.0369 | -44.0689 | -0.09613 | -0.17853 | 0.13733 | 122.8134 | 0.43488 | 0.6134 | -0.25635 | -0.20599 | -0.23804 | 0.073243 | 5.8136 | -0.022888 | 0.21515 | 0.013733 | 123.0835 | 122.6898 | 50.5463 | -123.1247 | 123.0194 | 122.9599 | 89.2136 | -123.1842
3904.0156 | 123.0331 | -43.8583 | 79.129 | 0.015106 | 0.018771 | 0.073591 | 0.075644 | 0.12608 | 0.0044091 | -0.0072911 | 0.030365 | -0.0078442 | 0.069605 | 0.058039 | 0.01254 | -0.012187 | 78.8773 | 79.01 | 6.839 | -43.4189 | 79.2435 | -43.9041 | -44.014 | -38.0173 | 45.4102 | -43.8766 | 79.1931 | 79.1519 | -44.0598 | -44.0826 | -0.045777 | -0.15564 | 0.11444 | 122.8683 | 0.43945 | 0.59509 | -0.25177 | -0.20142 | -0.22431 | 0.064087 | 5.8411 | -0.018311 | 0.20599 | 0.022889 | 123.1018 | 122.7356 | 50.6973 | -123.143 | 123.0515 | 123.0103 | 89.2685 | -123.2117
3905.0156 | 123.143 | -43.9133 | 78.9688 | -0.091705 | 0.012149 | -0.03557 | 0.070944 | 0.12779 | -0.0037085 | -0.0098545 | 0.09903 | -0.010621 | 0.065119 | 0.057398 | 0.008908 | -0.0079148 | 78.7445 | 78.9597 | 7.0129 | -43.4418 | 79.097 | -44.0048 | -44.101 | -38.0402 | 45.401 | -43.8583 | 79.0283 | 79.01 | -44.1238 | -44.1879 | -0.091553 | -0.18768 | 0.12817 | 122.8729 | 0.4715 | 0.65918 | -0.2243 | -0.21057 | -0.27466 | 0.059509 | 5.8731 | 0.054932 | 0.32959 | 0.041199 | 123.0103 | 122.6578 | 50.9262 | -123.0698 | 122.9416 | 122.9233 | 89.3143 | -123.1567
3906.0156 | 123.0927 | -43.9911 | 78.9734 | -0.168 | 0.018558 | 0.075514 | 0.073508 | 0.12608 | 0.0054773 | -0.0068637 | -0.18326 | -0.0093396 | 0.072382 | 0.058467 | 0.013394 | -0.013042 | 78.7857 | 78.9139 | 6.8985 | -43.4784 | 79.1428 | -44.0323 | -44.1376 | -38.063 | 45.282 | -44.0094 | 79.1016 | 78.9917 | -44.2062 | -44.1879 | -0.041199 | -0.14648 | 0.16937 | 122.905 | 0.5127 | 0.65918 | -0.18768 | -0.21515 | -0.19684 | 0.12817 | 5.928 | -0.01831 | 0.17853 | 0.01831 | 123.1338 | 122.7768 | 50.8896 | -123.111 | 123.0927 | 122.9828 | 89.2731 | -123.1613
3907.0156 | 123.0469 | -43.7164 | 79.2709 | 0.060882 | 0.019412 | 0.071882 | 0.074149 | 0.12907 | 0.0067589 | -0.0060093 | -3.1206 | -0.0084852 | 0.073664 | 0.057826 | 0.011472 | -0.012401 | 78.9551 | 79.0878 | 6.8436 | -43.2724 | 79.3945 | -43.808 | -43.8904 | -37.8021 | 45.4971 | -43.7485 | 79.3762 | 79.2801 | -43.9224 | -43.9362 | -0.091552 | -0.17395 | 0.1236 | 122.8043 | 0.44403 | 0.61798 | -0.31586 | -0.20599 | -0.21973 | 0.10529 | 5.9143 | -0.032043 | 0.18768 | 0.009155 | 123.111 | 122.6715 | 50.56 | -123.1613 | 123.0927 | 122.9965 | 89.2136 | -123.2071
3908.0156 | 123.1522 | -44.2932 | 78.5706 | 0.20584 | 0.017489 | 0.074232 | 0.072653 | 0.13014 | -0.00050425 | -0.0070773 | -1.3734 | -0.011903 | 0.068323 | 0.05868 | 0.0097626 | -0.011974 | 78.4195 | 78.6072 | 6.9855 | -43.7942 | 78.6804 | -44.3756 | -44.5038 | -38.3286 | 45.1309 | -44.2841 | 78.6575 | 78.5889 | -44.5221 | -44.5679 | -0.082397 | -0.21057 | 0.10986 | 122.9004 | 0.49896 | 0.70953 | -0.15106 | -0.22888 | -0.27466 | 0.086975 | 5.9647 | 0.009155 | 0.28381 | 0.01831 | 122.9736 | 122.7127 | 51.2787 | -123.0743 | 122.9507 | 122.8821 | 89.4241 | -123.1384
3909.0156 | 122.8729 | -43.6386 | 79.303 | 0.060882 | 0.021762 | 0.071027 | 0.075644 | 0.13057 | 0.0052637 | -0.0072911 | 0.17532 | -0.0093396 | 0.0711 | 0.062098 | 0.014035 | -0.013255 | 79.0604 | 79.1382 | 6.8848 | -43.1763 | 79.5044 | -43.7027 | -43.8354 | -37.7106 | 45.7443 | -43.7027 | 79.4128 | 79.3716 | -43.8446 | -43.8766 | -0.064087 | -0.19684 | 0.20142 | 122.7768 | 0.46234 | 0.65918 | -0.24261 | -0.20599 | -0.23804 | 0.10986 | 5.928 | -0.064087 | 0.17395 | 0.068664 | 123.143 | 122.699 | 50.5234 | -123.1384 | 123.0515 | 123.0103 | 89.3829 | -123.1796
3910.0156 | 123.0972 | -44.0323 | 78.8818 | 0.15244 | 0.015567 | 0.074659 | 0.070731 | 0.12544 | -0.00071785 | -0.0083591 | 0.31265 | -0.010835 | 0.065973 | 0.059107 | 0.010403 | -0.0091966 | 78.6575 | 78.8544 | 6.8802 | -43.5425 | 78.9871 | -44.1147 | -44.22 | -38.0722 | 45.5292 | -44.0598 | 78.9368 | 78.9047 | -44.2657 | -44.2841 | -0.082397 | -0.18768 | 0.10529 | 122.8867 | 0.48981 | 0.67749 | -0.2243 | -0.23346 | -0.25177 | 0.054932 | 5.9601 | -0.027465 | 0.22431 | 0.022888 | 123.0194 | 122.6898 | 50.9125 | -123.1018 | 122.9691 | 122.937 | 89.5615 | -123.1659
3911.0156 | 123.0743 | -43.8904 | 79.0329 | 0.16769 | 0.016849 | 0.071455 | 0.07543 | 0.12886 | 0.0046227 | -0.0072911 | 0.2211 | -0.0095532 | 0.072382 | 0.059748 | 0.01254 | -0.012828 | 78.8406 | 78.9093 | 6.9717 | -43.4097 | 79.2114 | -43.9728 | -44.0552 | -37.8983 | 45.6207 | -43.9407 | 79.1565 | 79.0924 | -44.101 | -44.1147 | -0.082397 | -0.1648 | 0.17853 | 122.7997 | 0.48065 | 0.64545 | -0.19226 | -0.21057 | -0.2243 | 0.1236 | 5.9921 | -0.050354 | 0.17395 | 0.059509 | 123.1018 | 122.731 | 50.8621 | -123.0881 | 123.0469 | 122.9828 | 89.5111 | -123.1476
3912.0156 | 123.0286 | -43.9682 | 78.9871 | -0.0383 | 0.021335 | 0.074659 | 0.074149 | 0.13035 | 0.0056909 | -0.0062229 | -0.045929 | -0.0093396 | 0.071527 | 0.061885 | 0.013181 | -0.011333 | 78.8223 | 78.9093 | 7.045 | -43.4509 | 79.1519 | -44.014 | -44.0918 | -37.9578 | 45.5475 | -44.0186 | 79.1107 | 79.0466 | -44.1559 | -44.1742 | -0.045776 | -0.1236 | 0.16479 | 122.8775 | 0.51727 | 0.64087 | -0.16479 | -0.18768 | -0.20599 | 0.1236 | 6.0104 | -0.050354 | 0.15564 | 0.059509 | 123.1201 | 122.7905 | 51.0132 | -123.0789 | 123.0789 | 123.0148 | 89.5157 | -123.1613
3913.0156 | 123.1293 | -44.4168 | 78.4836 | -0.023041 | 0.012149 | -0.03557 | 0.072012 | 0.12864 | -0.0032813 | -0.0085727 | 0.083771 | -0.012758 | 0.067682 | 0.059321 | 0.008908 | -0.0091966 | 78.2593 | 78.4882 | 6.9809 | -43.9087 | 78.6072 | -44.4717 | -44.5679 | -38.4155 | 45.2362 | -44.3665 | 78.5568 | 78.511 | -44.6503 | -44.6457 | -0.054932 | -0.15106 | 0.1236 | 122.905 | 0.50812 | 0.65918 | -0.22431 | -0.23346 | -0.22888 | 0.073242 | 6.0013 | 0.050354 | 0.27924 | 0.027465 | 123.024 | 122.6761 | 51.3977 | -123.0515 | 122.9736 | 122.9279 | 89.653 | -123.1293
3914.0156 | 123.0881 | -44.783 | 78.2043 | -0.12222 | 0.019839 | 0.073805 | 0.076498 | 0.13014 | 0.0071863 | -0.0083591 | 0.15244 | -0.008058 | 0.072168 | 0.058039 | 0.014035 | -0.014537 | 78.067 | 77.9205 | 6.9031 | -44.2017 | 78.3646 | -44.8151 | -44.9341 | -38.7039 | 44.8105 | -44.751 | 78.2867 | 78.2089 | -44.9799 | -45.0073 | -0.032043 | -0.15106 | 0.16022 | 122.7036 | 0.58136 | 0.73242 | -0.13733 | -0.19684 | -0.2243 | 0.082397 | 6.0791 | 0.032043 | 0.25635 | 0.004577 | 123.1476 | 122.85 | 51.6861 | -123.1384 | 123.0698 | 122.9919 | 89.5935 | -123.2117
3915.0156 | 123.1705 | -44.2383 | 78.6667 | 0.16006 | 0.018344 | 0.074232 | 0.072012 | 0.12928 | 0.0029137 | -0.0066501 | 0.21347 | -0.0086988 | 0.072595 | 0.057612 | 0.012967 | -0.013896 | 78.4973 | 78.653 | 6.6559 | -43.7714 | 78.7903 | -44.3298 | -44.4489 | -38.1729 | 45.0165 | -44.1833 | 78.7079 | 78.653 | -44.4855 | -44.4855 | -0.091553 | -0.21057 | 0.1236 | 122.8912 | 0.46692 | 0.67749 | -0.16937 | -0.24719 | -0.24719 | 0.041199 | 6.0654 | 0.054931 | 0.30212 | -0.013733 | 123.0286 | 122.7356 | 50.8942 | -123.1155 | 122.9462 | 122.8912 | 89.2548 | -123.1522
3916.0156 | 123.1567 | -44.5908 | 78.3279 | -0.11459 | 0.017489 | 0.073377 | 0.076712 | 0.13099 | 0.0048363 | -0.0083591 | -0.045929 | -0.0078442 | 0.071741 | 0.060603 | 0.014676 | -0.012828 | 78.0624 | 78.186 | 6.7841 | -44.165 | 78.4195 | -44.751 | -44.8563 | -38.5849 | 44.2566 | -44.6777 | 78.392 | 78.3508 | -44.8471 | -44.838 | -0.16022 | -0.2655 | 0.091553 | 122.7768 | 0.42572 | 0.69122 | -0.2655 | -0.25635 | -0.24719 | 0.064087 | 6.0059 | -0.086975 | 0.16022 | 0.022888 | 123.0103 | 122.6532 | 51.3748 | -123.1842 | 122.9828 | 122.9416 | 88.8474 | -123.1659
3917.0156 | 123.056 | -45.1904 | 77.7557 | -0.00015269 | 0.021762 | 0.072736 | 0.07543 | 0.12928 | 0.0054773 | -0.0075047 | 0.0074766 | -0.008058 | 0.075373 | 0.058467 | 0.014676 | -0.010905 | 77.5772 | 77.7008 | 6.3995 | -44.632 | 77.948 | -45.1859 | -45.3323 | -39.1296 | 44.3985 | -45.2774 | 77.8976 | 77.8198 | -45.4147 | -45.4422 | 0.004578 | -0.14191 | 0.19226 | 122.8912 | 0.55847 | 0.70038 | -0.17853 | -0.2243 | -0.25177 | 0.14191 | 6.0608 | -0.086975 | 0.16479 | 0.064087 | 123.1384 | 122.7676 | 51.59 | -123.0881 | 123.0881 | 123.0103 | 89.5889 | -123.1979
3918.0156 | 123.0469 | -45.2545 | 77.6962 | -0.00015269 | 0.021762 | 0.073377 | 0.076926 | 0.12822 | 0.0054773 | -0.0083591 | -0.023041 | -0.0072034 | 0.071527 | 0.059107 | 0.011472 | -0.01176 | 77.449 | 77.5818 | 6.6971 | -44.7739 | 77.8152 | -45.369 | -45.4651 | -39.1846 | 44.0002 | -45.2774 | 77.8152 | 77.7374 | -45.4651 | -45.5154 | -0.11444 | -0.21057 | 0.11902 | 122.8363 | 0.48065 | 0.69122 | -0.24719 | -0.21057 | -0.26093 | 0.11902 | 6.0699 | -0.022888 | 0.23804 | 0.041199 | 123.0698 | 122.7036 | 51.9516 | -123.1613 | 123.0698 | 122.9919 | 89.2548 | -123.2117
3919.0156 | 123.0652 | -44.8517 | 78.0579 | 0.14481 | 0.020267 | 0.073377 | 0.073508 | 0.12758 | 0.0059045 | -0.0070773 | 0.24399 | -0.009126 | 0.069391 | 0.060816 | 0.014462 | -0.011333 | 77.8473 | 77.9663 | 6.7841 | -44.3665 | 78.2272 | -44.9066 | -45.0302 | -38.7543 | 44.8563 | -44.8471 | 78.1998 | 78.1036 | -45.076 | -45.108 | -0.054931 | -0.17853 | 0.16937 | 122.818 | 0.48523 | 0.66376 | -0.21057 | -0.2243 | -0.25635 | 0.14191 | 6.0974 | 0.004578 | 0.26093 | 0.045777 | 123.0789 | 122.699 | 51.6357 | -123.0881 | 123.0515 | 122.9553 | 89.7079 | -123.1659
3920.0156 | 123.1338 | -45.1309 | 77.7878 | 0.053253 | 0.012576 | 0.076368 | 0.072012 | 0.12864 | -0.0037085 | -0.0081455 | 0.30502 | -0.0093396 | 0.068964 | 0.056544 | 0.010617 | -0.0089828 | 77.5589 | 77.742 | 6.8069 | -44.7189 | 77.9297 | -45.2271 | -45.3186 | -38.9923 | 44.6686 | -45.0348 | 77.8793 | 77.8198 | -45.3049 | -45.3598 | -0.096131 | -0.18768 | 0.14191 | 122.8729 | 0.41199 | 0.59967 | -0.22888 | -0.17395 | -0.22888 | 0.091552 | 6.1386 | 0.09613 | 0.32501 | 0.032043 | 123.0606 | 122.6898 | 51.9379 | -123.1064 | 123.0103 | 122.9507 | 89.7995 | -123.1476
3921.0156 | 123.0652 | -44.9707 | 77.9755 | -0.54947 | 0.021548 | 0.076368 | 0.076926 | 0.128 | 0.0073999 | -0.0057957 | -0.053558 | -0.0089124 | 0.07345 | 0.059748 | 0.012967 | -0.013255 | 77.7969 | 77.8931 | 6.8024 | -44.4397 | 78.0899 | -45.0394 | -45.1492 | -38.7863 | 44.8013 | -44.9982 | 78.1036 | 78.035 | -45.1492 | -45.1859 | -0.068665 | -0.17853 | 0.11444 | 122.8638 | 0.53101 | 0.70953 | -0.17853 | -0.17853 | -0.21515 | 0.12817 | 6.1844 | -0.027466 | 0.18768 | 0.059509 | 123.0606 | 122.7676 | 51.7731 | -123.1247 | 123.0743 | 123.0057 | 89.772 | -123.1613
3922.0156 | 123.0515 | -44.9753 | 78.0121 | -0.22903 | 0.017062 | 0.074232 | 0.077353 | 0.13142 | 0.0039819 | -0.0075047 | -0.12222 | -0.009126 | 0.069818 | 0.057612 | 0.012326 | -0.012828 | 77.742 | 77.8931 | 6.6925 | -44.4397 | 78.1677 | -45.0348 | -45.1492 | -38.8412 | 44.7784 | -44.9844 | 78.0762 | 78.0167 | -45.1996 | -45.2087 | -0.059509 | -0.17395 | 0.15564 | 122.8683 | 0.53558 | 0.70953 | -0.27008 | -0.2243 | -0.23346 | 0.064087 | 6.134 | -0.009155 | 0.2243 | 0.004578 | 123.143 | 122.7173 | 51.6678 | -123.1613 | 123.0515 | 122.9919 | 89.7537 | -123.2208
3923.0156 | 123.024 | -45.7809 | 77.1698 | 0.083771 | 0.02048 | 0.069105 | 0.070303 | 0.13078 | 0.0029137 | -0.0066501 | 0.41183 | -0.0097668 | 0.072382 | 0.059748 | 0.012967 | -0.0098374 | 76.9318 | 77.0233 | 6.2531 | -45.2545 | 77.3346 | -45.8954 | -45.9824 | -39.6194 | 44.0094 | -45.8267 | 77.2614 | 77.179 | -46.0007 | -46.0419 | -0.11444 | -0.20142 | 0.16479 | 122.8043 | 0.52643 | 0.72784 | -0.23804 | -0.21973 | -0.26093 | 0.091553 | 6.1615 | -0.045776 | 0.21515 | 0.009155 | 123.1155 | 122.7127 | 52.034 | -123.1522 | 123.0423 | 122.9599 | 89.7903 | -123.2117
3924.0156 | 123.0698 | -45.0302 | 77.8976 | -0.091705 | 0.020907 | 0.074659 | 0.07479 | 0.12843 | 0.0073999 | -0.0077183 | -0.061188 | -0.0084852 | 0.070246 | 0.058894 | 0.012967 | -0.013469 | 77.7237 | 77.8702 | 6.4682 | -44.4534 | 78.0807 | -45.108 | -45.195 | -38.7634 | 44.7372 | -45.0485 | 78.0624 | 77.9343 | -45.2408 | -45.2728 | -0.07782 | -0.16479 | 0.18311 | 122.9004 | 0.57678 | 0.74158 | -0.17395 | -0.21057 | -0.24262 | 0.16479 | 6.2668 | -0.018311 | 0.2243 | 0.036621 | 123.111 | 122.7539 | 51.4984 | -123.0927 | 123.0927 | 122.9645 | 89.7675 | -123.1705
3925.0156 | 123.1384 | -45.1218 | 77.7786 | -0.0077822 | 0.012362 | 0.074659 | 0.073935 | 0.13078 | -0.0034949 | -0.0083591 | 0.076141 | -0.011903 | 0.069391 | 0.058894 | 0.0093354 | -0.010051 | 77.5177 | 77.7603 | 6.7429 | -44.6045 | 77.9205 | -45.2362 | -45.3232 | -38.9099 | 44.7098 | -45.0577 | 77.8519 | 77.7924 | -45.3094 | -45.3827 | -0.11444 | -0.20142 | 0.14191 | 122.8821 | 0.51727 | 0.71869 | -0.26093 | -0.18768 | -0.26092 | 0.073243 | 6.2119 | 0.064087 | 0.32501 | 0.013733 | 123.0423 | 122.6395 | 51.8646 | -123.1018 | 122.9736 | 122.9141 | 89.8315 | -123.1613
3926.0156 | 123.0469 | -45.076 | 77.9114 | -0.25192 | 0.017062 | 0.0753 | 0.076285 | 0.13014 | 0.0022729 | -0.0085727 | 0.0914 | -0.0093396 | 0.071741 | 0.059748 | 0.01254 | -0.011119 | 77.6138 | 77.8015 | 6.5918 | -44.458 | 78.1128 | -45.0897 | -45.2042 | -38.8458 | 44.6045 | -45.108 | 78.0533 | 77.9205 | -45.2683 | -45.2957 | -0.013733 | -0.12817 | 0.20142 | 122.8775 | 0.61798 | 0.74616 | -0.29755 | -0.19226 | -0.21973 | 0.14191 | 6.2302 | -0.032043 | 0.18768 | 0.009155 | 123.1888 | 122.6898 | 51.6678 | -123.1155 | 123.1293 | 122.9965 | 89.6805 | -123.2071
3927.0156 | 123.0331 | -45.4147 | 77.5452 | 0.0074768 | 0.019839 | 0.072309 | 0.07244 | 0.12971 | 0.0069727 | -0.0070773 | -0.038299 | -0.010621 | 0.072382 | 0.060603 | 0.01553 | -0.011974 | 77.3346 | 77.4857 | 6.6605 | -44.8471 | 77.6962 | -45.4559 | -45.5612 | -39.1708 | 44.339 | -45.4285 | 77.6688 | 77.5635 | -45.5887 | -45.6482 | -0.041199 | -0.14648 | 0.15106 | 122.9004 | 0.56763 | 0.71411 | -0.21057 | -0.17395 | -0.23346 | 0.1236 | 6.2439 | -0.013733 | 0.21973 | 0.018311 | 123.111 | 122.7493 | 52.0752 | -123.1064 | 123.0835 | 122.9782 | 89.7537 | -123.1934
3928.0156 | 123.0652 | -45.2728 | 77.6825 | -0.076447 | 0.019198 | 0.073377 | 0.073294 | 0.12843 | 0.0067589 | -0.0057957 | -0.33585 | -0.0069898 | 0.072809 | 0.060176 | 0.015103 | -0.013255 | 77.4948 | 77.6367 | 6.839 | -44.5267 | 77.8702 | -45.2866 | -45.3873 | -38.9832 | 44.4855 | -45.2774 | 77.8152 | 77.7237 | -45.4651 | -45.4651 | -0.013733 | -0.11444 | 0.18768 | 122.9095 | 0.74616 | 0.8606 | -0.18768 | -0.19226 | -0.19226 | 0.13275 | 6.2897 | -0.004578 | 0.18768 | 0.041199 | 123.143 | 122.7676 | 52.1118 | -123.0698 | 123.0881 | 122.9965 | 89.7583 | -123.1476
3929.0156 | 123.1018 | -45.5109 | 77.4353 | -0.10696 | 0.019198 | 0.073377 | 0.075644 | 0.12736 | 0.0069727 | -0.0068637 | -0.015411 | -0.0084852 | 0.070459 | 0.058467 | 0.01489 | -0.010051 | 77.1927 | 77.3712 | 6.6605 | -44.9387 | 77.5818 | -45.5841 | -45.6757 | -39.2578 | 44.3665 | -45.5429 | 77.536 | 77.449 | -45.7031 | -45.7535 | -0.073242 | -0.1648 | 0.14648 | 122.8821 | 0.5722 | 0.737 | -0.24262 | -0.19226 | -0.24262 | 0.10071 | 6.2531 | -0.032044 | 0.21057 | 0.013733 | 123.0927 | 122.7036 | 52.1713 | -123.111 | 123.0469 | 122.9599 | 89.8773 | -123.1888
3930.0156 | 123.056 | -45.2499 | 77.7328 | -0.4808 | 0.016421 | 0.073591 | 0.073508 | 0.1327 | 0.0035547 | -0.0079319 | -0.12985 | -0.0099806 | 0.0711 | 0.058894 | 0.010617 | -0.010692 | 77.3758 | 77.5955 | 6.601 | -44.7418 | 77.8473 | -45.3598 | -45.4697 | -39.061 | 44.4717 | -45.2774 | 77.8061 | 77.7328 | -45.4697 | -45.5017 | -0.10986 | -0.21973 | 0.11444 | 122.8455 | 0.50812 | 0.72784 | -0.35706 | -0.21973 | -0.25177 | 0.073242 | 6.189 | -0.027466 | 0.2243 | 0 | 123.0972 | 122.6257 | 51.8509 | -123.2025 | 123.056 | 122.9828 | 89.7217 | -123.2346
3931.0156 | 123.0469 | -45.5566 | 77.4078 | -0.03067 | 0.020053 | 0.074873 | 0.077567 | 0.13078 | 0.0061181 | -0.0066501 | 0.0074766 | -0.0072034 | 0.072168 | 0.058467 | 0.015317 | -0.012401 | 77.2018 | 77.3575 | 6.5186 | -44.9478 | 77.5909 | -45.5933 | -45.6665 | -39.2944 | 44.2703 | -45.5887 | 77.5314 | 77.4673 | -45.7581 | -45.7718 | -0.036621 | -0.10986 | 0.1831 | 122.9141 | 0.60883 | 0.71869 | -0.20599 | -0.20142 | -0.21515 | 0.1236 | 6.2622 | -0.032043 | 0.18311 | 0.059509 | 123.1476 | 122.7585 | 52.0752 | -123.0743 | 123.0881 | 123.024 | 89.827 | -123.1796
3932.0156 | 123.0835 | -45.3506 | 77.5772 | -0.22141 | 0.017703 | 0.074659 | 0.07543 | 0.12971 | 0.0039819 | -0.0057957 | -0.076446 | -0.0078442 | 0.070246 | 0.059535 | 0.014676 | -0.013896 | 77.2842 | 77.4902 | 6.601 | -44.8425 | 77.6733 | -45.5063 | -45.5841 | -39.1067 | 44.5038 | -45.401 | 77.655 | 77.6047 | -45.5887 | -45.5978 | -0.15564 | -0.23346 | 0.096131 | 122.8409 | 0.50812 | 0.74158 | -0.29297 | -0.23804 | -0.24719 | 0.07782 | 6.2439 | -0.050354 | 0.19684 | 0.027466 | 123.024 | 122.6349 | 51.9516 | -123.1613 | 123.0057 | 122.9553 | 89.8544 | -123.175
3933.0156 | 123.0011 | -45.5017 | 77.4582 | 0.053253 | 0.018771 | 0.072309 | 0.077353 | 0.12971 | 0.0050499 | -0.0079319 | 0.15244 | -0.0086988 | 0.071314 | 0.059321 | 0.013181 | -0.011119 | 77.2293 | 77.3895 | 6.4407 | -44.8792 | 77.6916 | -45.5017 | -45.5978 | -39.2029 | 44.2612 | -45.5612 | 77.623 | 77.5406 | -45.6985 | -45.7031 | 0 | -0.09613 | 0.23346 | 122.8912 | 0.62256 | 0.71869 | -0.22888 | -0.19684 | -0.20142 | 0.16479 | 6.2988 | -0.059509 | 0.14191 | 0.082397 | 123.1934 | 122.731 | 51.9424 | -123.056 | 123.1247 | 123.0423 | 89.7629 | -123.1613
3934.0156 | 123.0103 | -45.401 | 77.5818 | -0.22903 | 0.013217 | 0.077436 | 0.071799 | 0.128 | 0.0029137 | -0.0083591 | -0.10696 | -0.0089124 | 0.069605 | 0.058039 | 0.012326 | -0.011546 | 77.298 | 77.4857 | 6.6879 | -44.838 | 77.7237 | -45.4422 | -45.5658 | -39.0701 | 44.6915 | -45.488 | 77.742 | 77.6413 | -45.5841 | -45.607 | -0.041199 | -0.16479 | 0.14191 | 122.8867 | 0.56305 | 0.72784 | -0.28381 | -0.1831 | -0.20599 | 0.16022 | 6.3309 | -0.086975 | 0.11902 | 0.059509 | 123.1247 | 122.699 | 52.0889 | -123.1476 | 123.143 | 123.0423 | 90.0925 | -123.1888
3935.0156 | 123.056 | -45.4239 | 77.5635 | -0.061188 | 0.020267 | 0.076795 | 0.075217 | 0.1295 | 0.0071863 | -0.0064365 | 0.053253 | -0.0086988 | 0.072809 | 0.058467 | 0.013394 | -0.010905 | 77.3438 | 77.5131 | 6.6559 | -44.8196 | 77.7054 | -45.4422 | -45.5566 | -39.0747 | 44.5633 | -45.401 | 77.655 | 77.5864 | -45.6161 | -45.6573 | -0.018311 | -0.13275 | 0.14191 | 122.937 | 0.60425 | 0.737 | -0.21973 | -0.19226 | -0.23346 | 0.091552 | 6.3492 | 0.022888 | 0.25635 | 0.022888 | 123.1293 | 122.7676 | 52.0798 | -123.1201 | 123.0789 | 123.0103 | 89.9872 | -123.2208
3936.0156 | 123.0927 | -45.4422 | 77.5177 | -0.17563 | 0.016849 | 0.074873 | 0.073508 | 0.12907 | 0.0037683 | -0.0092137 | -0.11459 | -0.0097668 | 0.072168 | 0.059535 | 0.010831 | -0.011974 | 77.2385 | 77.4078 | 6.1844 | -44.8517 | 77.6505 | -45.52 | -45.6024 | -39.1251 | 44.5221 | -45.4422 | 77.6276 | 77.536 | -45.6436 | -45.6757 | -0.07782 | -0.16022 | 0.13275 | 122.85 | 0.59051 | 0.75073 | -0.27924 | -0.20142 | -0.23346 | 0.10986 | 6.3171 | 0 | 0.23346 | 0.018311 | 123.0927 | 122.6807 | 51.6266 | -123.1201 | 123.0698 | 122.9782 | 89.9643 | -123.1934
3937.0156 | 123.056 | -45.6345 | 77.3117 | -0.13748 | 0.018985 | 0.074018 | 0.076498 | 0.12928 | 0.0050499 | -0.0062229 | -0.19089 | -0.010835 | 0.070459 | 0.058894 | 0.013608 | -0.012187 | 77.1011 | 77.2797 | 6.5002 | -45.0302 | 77.4948 | -45.6802 | -45.8221 | -39.2807 | 44.3573 | -45.607 | 77.4216 | 77.33 | -45.8313 | -45.8817 | -0.045777 | -0.18768 | 0.1831 | 122.9141 | 0.60425 | 0.79193 | -0.21057 | -0.19684 | -0.24719 | 0.10986 | 6.3538 | 0.027465 | 0.27466 | 0.01831 | 123.1293 | 122.7356 | 52.1347 | -123.1339 | 123.056 | 122.9645 | 89.9918 | -123.1934
3938.0156 | 122.9919 | -45.5521 | 77.4399 | 0.060882 | 0.020694 | 0.075086 | 0.07479 | 0.128 | 0.0048363 | -0.0070773 | 0.053253 | -0.0069898 | 0.071741 | 0.058894 | 0.015744 | -0.01176 | 77.1378 | 77.2842 | 6.4545 | -44.9844 | 77.5497 | -45.6024 | -45.7123 | -39.2395 | 44.3802 | -45.6024 | 77.5269 | 77.4399 | -45.7718 | -45.7901 | -0.050354 | -0.16022 | 0.10986 | 122.8363 | 0.56763 | 0.72784 | -0.30212 | -0.21973 | -0.23804 | 0.086975 | 6.3126 | -0.050354 | 0.18768 | 0 | 123.1018 | 122.6898 | 52.0065 | -123.1522 | 123.0789 | 122.9919 | 89.9323 | -123.23
3939.0156 | 123.0515 | -45.3873 | 77.5681 | -0.061188 | 0.021121 | 0.074232 | 0.07543 | 0.13185 | 0.0061181 | -0.0068637 | 0.037995 | -0.0082716 | 0.073236 | 0.059107 | 0.014462 | -0.012614 | 77.3254 | 77.4719 | 6.8161 | -44.8105 | 77.6962 | -45.4651 | -45.5795 | -39.0335 | 44.6274 | -45.3873 | 77.6733 | 77.6321 | -45.5933 | -45.6207 | -0.07782 | -0.19226 | 0.12817 | 122.8592 | 0.57678 | 0.76904 | -0.24262 | -0.20599 | -0.23346 | 0.10529 | 6.3538 | 0 | 0.23346 | 0.064087 | 123.0835 | 122.7127 | 52.2034 | -123.1476 | 123.0606 | 123.0194 | 90.0146 | -123.1888
3940.0156 | 123.0423 | -45.1584 | 77.8427 | -0.24429 | 0.013003 | 0.074018 | 0.074149 | 0.12907 | -0.0015723 | -0.011991 | -0.053558 | -0.011262 | 0.069818 | 0.059748 | 0.010403 | -0.010478 | 77.5269 | 77.7557 | 6.8802 | -44.577 | 77.9388 | -45.1996 | -45.3049 | -38.8138 | 44.9249 | -45.1309 | 77.9251 | 77.861 | -45.3461 | -45.3918 | -0.041199 | -0.14648 | 0.096131 | 122.9141 | 0.58136 | 0.72785 | -0.31586 | -0.18768 | -0.23346 | 0.082398 | 6.3446 | 0.027466 | 0.26093 | 0.018311 | 123.0972 | 122.6852 | 52.0386 | -123.1476 | 123.0835 | 123.0194 | 90.0833 | -123.2346
3941.0156 | 123.0606 | -46.0648 | 76.9043 | -0.22141 | 0.02048 | 0.072523 | 0.076071 | 0.1295 | 0.0050499 | -0.0038731 | -0.12985 | -0.0084852 | 0.071955 | 0.060389 | 0.011685 | -0.012828 | 76.7029 | 76.8356 | 6.6193 | -45.4422 | 77.0782 | -46.1197 | -46.2387 | -39.6103 | 44.1193 | -46.0236 | 77.0004 | 76.9272 | -46.2662 | -46.2936 | -0.054932 | -0.17395 | 0.17395 | 122.9004 | 0.62256 | 0.79651 | -0.20142 | -0.20142 | -0.22888 | 0.09613 | 6.4545 | 0.041198 | 0.27008 | 0.022888 | 123.143 | 122.7676 | 52.684 | -123.143 | 123.0652 | 122.9919 | 90.184 | -123.1979
3942.0156 | 123.0423 | -45.5704 | 77.4124 | -0.15274 | 0.014071 | 0.077863 | 0.071372 | 0.13163 | 0.00099115 | -0.010282 | -0.14511 | -0.0097668 | 0.068323 | 0.060816 | 0.011685 | -0.0091966 | 77.1057 | 77.298 | 6.4178 | -44.9936 | 77.5223 | -45.6207 | -45.7397 | -39.1891 | 44.6732 | -45.3598 | 77.5406 | 77.4445 | -45.7764 | -45.7901 | -0.050354 | -0.16937 | 0.10986 | 122.8683 | 0.57678 | 0.74615 | -0.3067 | -0.20599 | -0.21973 | 0.12817 | 6.3812 | 0.21057 | 0.4303 | 0.032043 | 123.0927 | 122.6761 | 51.9882 | -123.1522 | 123.111 | 123.0148 | 90.2435 | -123.2025
3943.0156 | 123.056 | -45.4742 | 77.4994 | 0.12192 | 0.019198 | 0.074232 | 0.077139 | 0.12715 | 0.0050499 | -0.0051547 | 0.18295 | -0.009126 | 0.072595 | 0.061457 | 0.012326 | -0.013896 | 77.2247 | 77.3392 | 6.7978 | -44.8975 | 77.655 | -45.5154 | -45.6528 | -38.942 | 44.4305 | -45.488 | 77.5818 | 77.5131 | -45.6757 | -45.7169 | -0.041199 | -0.17853 | 0.15564 | 122.8134 | 0.57678 | 0.75531 | -0.27466 | -0.20142 | -0.24262 | 0.082397 | 6.5323 | -0.013733 | 0.22888 | 0.013733 | 123.1293 | 122.699 | 52.272 | -123.1522 | 123.056 | 122.9874 | 89.9048 | -123.2162
3944.0156 | 123.0194 | -45.3873 | 77.5543 | -0.25955 | 0.014071 | 0.076795 | 0.074576 | 0.1295 | 0.0016321 | -0.010709 | -0.25192 | -0.0082716 | 0.070673 | 0.059321 | 0.012112 | -0.010478 | 77.5726 | 77.3026 | 6.8573 | -44.8242 | 77.7695 | -45.4559 | -45.5521 | -38.9465 | 44.696 | -45.3735 | 77.6825 | 77.6093 | -45.5933 | -45.6299 | -0.068665 | -0.16479 | 0.21515 | 122.6898 | 0.56305 | 0.72784 | 0.018311 | -0.20599 | -0.24262 | 0.12817 | 6.4407 | 0.013733 | 0.25635 | 0.054932 | 123.1567 | 122.9599 | 52.2446 | -123.1064 | 123.0698 | 122.9965 | 90.0833 | -123.1842
3945.0156 | 123.0652 | -45.5887 | 77.3529 | -0.091705 | 0.018558 | 0.075727 | 0.07778 | 0.12864 | 0.0086815 | -0.0068637 | -0.41977 | -0.0076306 | 0.071741 | 0.060389 | 0.015103 | -0.013255 | 77.1194 | 77.4078 | 6.9763 | -44.8837 | 77.536 | -45.6299 | -45.7443 | -39.1022 | 44.4992 | -45.6207 | 77.4353 | 77.3438 | -45.8359 | -45.8633 | -0.041199 | -0.15564 | 0.18311 | 122.9965 | 0.70496 | 0.8606 | -0.23346 | -0.24719 | -0.27466 | 0.082398 | 6.4865 | -0.032044 | 0.24261 | -0.009155 | 123.1247 | 122.7081 | 52.565 | -123.0972 | 123.024 | 122.9324 | 90.0879 | -123.2162
3946.0156 | 123.0606 | -45.5246 | 77.449 | -0.22903 | 0.016849 | 0.074873 | 0.076285 | 0.13014 | 0.0050499 | -0.0072911 | -0.19089 | -0.0082716 | 0.069818 | 0.057826 | 0.01254 | -0.012828 | 77.2018 | 77.3575 | 6.8893 | -44.8792 | 77.6184 | -45.5658 | -45.6985 | -39.0289 | 44.5587 | -45.4788 | 77.536 | 77.4811 | -45.726 | -45.7626 | -0.041199 | -0.17395 | 0.16937 | 122.8821 | 0.64545 | 0.8194 | -0.24719 | -0.20142 | -0.23804 | 0.086975 | 6.4957 | 0.045776 | 0.28381 | 0.032043 | 123.143 | 122.7264 | 52.4139 | -123.1476 | 123.0606 | 123.0057 | 90.0833 | -123.2117
3947.0156 | 123.0652 | -45.488 | 77.4719 | -0.18326 | 0.018558 | 0.074232 | 0.077353 | 0.12928 | 0.0046227 | -0.0053683 | -0.20615 | -0.0095532 | 0.071527 | 0.059321 | 0.011472 | -0.011333 | 77.1744 | 77.3575 | 6.6742 | -44.8883 | 77.6093 | -45.5704 | -45.6711 | -39.0106 | 44.6228 | -45.4788 | 77.5681 | 77.4948 | -45.7214 | -45.7214 | -0.082398 | -0.18311 | 0.13733 | 122.8455 | 0.59967 | 0.78278 | -0.29755 | -0.23346 | -0.23346 | 0.09613 | 6.4774 | 0.009155 | 0.24261 | 0.022888 | 123.0972 | 122.6624 | 52.1622 | -123.143 | 123.056 | 122.9828 | 90.1108 | -123.1934
3948.0156 | 123.0835 | -45.4926 | 77.4399 | -0.076447 | 0.020267 | 0.074018 | 0.079062 | 0.12886 | 0.0073999 | -0.0057957 | 0.053253 | -0.007417 | 0.074304 | 0.060603 | 0.014462 | -0.011974 | 77.1423 | 77.5085 | 6.9855 | -44.9112 | 77.5818 | -45.5933 | -45.7031 | -38.9694 | 44.6594 | -45.4926 | 77.5223 | 77.4399 | -45.726 | -45.7581 | -0.10071 | -0.21057 | 0.14191 | 123.0011 | 0.58136 | 0.79193 | -0.29755 | -0.23346 | -0.2655 | 0.082398 | 6.5231 | 0 | 0.2655 | 0 | 123.0743 | 122.6349 | 52.478 | -123.143 | 123.0148 | 122.9324 | 90.152 | -123.1979
3949.0156 | 123.0606 | -45.3918 | 77.5955 | -0.32822 | 0.016208 | 0.076795 | 0.075644 | 0.12886 | 0.0012047 | -0.0094273 | -0.13748 | -0.010835 | 0.070459 | 0.061244 | 0.010617 | -0.010051 | 77.2614 | 77.449 | 6.6742 | -44.8105 | 77.6916 | -45.4742 | -45.5978 | -38.8687 | 44.7784 | -45.3964 | 77.6825 | 77.6093 | -45.6116 | -45.6161 | -0.082397 | -0.20599 | 0.09613 | 122.8409 | 0.58136 | 0.78735 | -0.33417 | -0.21973 | -0.2243 | 0.086975 | 6.5231 | -0.004577 | 0.21973 | 0.013733 | 123.0835 | 122.6532 | 52.066 | -123.1934 | 123.0743 | 123.0011 | 90.1703 | -123.2117
3950.0156 | 123.111 | -45.5841 | 77.3346 | -0.19089 | 0.010013 | 0.075514 | 0.074362 | 0.13014 | 0.0014185 | -0.0094273 | -0.13748 | -0.0099806 | 0.066828 | 0.058467 | 0.012753 | -0.0094102 | 77.0828 | 77.3483 | 7.0038 | -44.9432 | 77.4307 | -45.6757 | -45.7855 | -39.061 | 44.6686 | -45.5841 | 77.3804 | 77.3209 | -45.8496 | -45.8405 | -0.091553 | -0.20142 | 0.09613 | 122.9324 | 0.64087 | 0.84228 | -0.25177 | -0.2655 | -0.25635 | 0.045776 | 6.5231 | 0 | 0.25635 | -0.013733 | 123.0148 | 122.6669 | 52.5879 | -123.1201 | 122.9645 | 122.905 | 90.2527 | -123.175
3951.0156 | 123.0743 | -45.314 | 77.6001 | -0.168 | 0.018558 | 0.074659 | 0.076071 | 0.12886 | 0.0071863 | -0.0070773 | -0.10696 | -0.0089124 | 0.070886 | 0.059962 | 0.014462 | -0.01176 | 77.449 | 77.655 | 6.926 | -44.6228 | 77.8839 | -45.3094 | -45.4376 | -38.6856 | 44.9432 | -45.314 | 77.7695 | 77.71 | -45.5063 | -45.5658 | 0.004578 | -0.1236 | 0.28381 | 122.9691 | 0.69122 | 0.81482 | -0.15106 | -0.19226 | -0.25177 | 0.16937 | 6.6284 | 0 | 0.25177 | 0.10986 | 123.1979 | 122.7631 | 52.24 | -123.0377 | 123.0835 | 123.024 | 90.2573 | -123.1659
3952.0156 | 123.0377 | -45.433 | 77.5269 | -0.21378 | 0.013858 | 0.079145 | 0.070731 | 0.12672 | -0.00050425 | -0.0083591 | -0.091705 | -0.010835 | 0.071741 | 0.059107 | 0.011044 | -0.0085556 | 77.2568 | 77.4857 | 7.0724 | -44.7922 | 77.5955 | -45.5292 | -45.607 | -38.8916 | 44.7784 | -45.4193 | 77.6138 | 77.5085 | -45.6573 | -45.6985 | -0.096131 | -0.17395 | 0.068665 | 122.9187 | 0.64087 | 0.81482 | -0.27008 | -0.22431 | -0.2655 | 0.086976 | 6.5414 | 0.013732 | 0.27923 | -0.01831 | 123.0286 | 122.6898 | 52.5055 | -123.1338 | 123.0469 | 122.9416 | 90.2115 | -123.2254
3953.0156 | 123.0103 | -45.5475 | 77.4628 | 0.0914 | 0.018344 | 0.07765 | 0.075858 | 0.13035 | 0.0084679 | -0.0064365 | 0.0074766 | -0.0061352 | 0.071955 | 0.059321 | 0.01489 | -0.012828 | 77.1606 | 77.3254 | 6.9397 | -44.902 | 77.6001 | -45.5795 | -45.6711 | -38.9191 | 44.6228 | -45.5978 | 77.5543 | 77.4628 | -45.7306 | -45.8038 | -0.032044 | -0.1236 | 0.13733 | 122.8729 | 0.64545 | 0.76904 | -0.30212 | -0.18311 | -0.25635 | 0.091552 | 6.6284 | -0.050354 | 0.20599 | 0 | 123.1476 | 122.7081 | 52.4872 | -123.1339 | 123.1018 | 123.0103 | 90.1703 | -123.2666
3954.0156 | 122.9599 | -45.314 | 77.6871 | -0.21378 | 0.016421 | 0.074659 | 0.073721 | 0.12864 | 0.0016321 | -0.0094273 | -0.19089 | -0.0099806 | 0.0711 | 0.061244 | 0.011472 | -0.012401 | 77.33 | 77.5406 | 7.0724 | -44.7372 | 77.7557 | -45.4056 | -45.5017 | -38.7177 | 44.8471 | -45.2866 | 77.7466 | 77.6871 | -45.5475 | -45.5841 | -0.091553 | -0.18768 | 0.068664 | 122.8546 | 0.57678 | 0.76447 | -0.35706 | -0.23346 | -0.27008 | 0.059509 | 6.5964 | 0.027466 | 0.29755 | 0 | 123.0698 | 122.644 | 52.3865 | -123.1888 | 123.0606 | 123.0011 | 90.1611 | -123.2712
3955.0156 | 123.024 | -45.5475 | 77.4124 | -1.3048 | 0.017917 | 0.07295 | 0.074362 | 0.12843 | 0.0039819 | -0.0077183 | -0.13748 | -0.011049 | 0.069818 | 0.060176 | 0.0097626 | -0.0089828 | 77.1011 | 77.3438 | 6.9901 | -44.8975 | 77.5635 | -45.5978 | -45.726 | -38.9099 | 44.6686 | -45.5429 | 77.5131 | 77.4628 | -45.7581 | -45.7626 | -0.050354 | -0.17853 | 0.15106 | 122.8912 | 0.65002 | 0.82855 | -0.31128 | -0.21057 | -0.21515 | 0.10071 | 6.6376 | 0.004577 | 0.21973 | 0.050354 | 123.111 | 122.6486 | 52.5375 | -123.1384 | 123.0606 | 123.0103 | 90.2161 | -123.175
3956.0156 | 123.0835 | -45.4193 | 77.5269 | -0.15274 | 0.010653 | 0.077863 | 0.072867 | 0.12864 | 0.00056395 | -0.0089999 | -0.12222 | -0.010194 | 0.067896 | 0.058039 | 0.012967 | -0.0096238 | 77.298 | 77.5452 | 7.1136 | -44.7464 | 77.6321 | -45.4605 | -45.6207 | -38.7543 | 44.8334 | -45.3232 | 77.5681 | 77.5085 | -45.639 | -45.6528 | -0.041198 | -0.20142 | 0.10529 | 122.9645 | 0.67291 | 0.87433 | -0.22888 | -0.21973 | -0.23346 | 0.041199 | 6.665 | 0.096131 | 0.32959 | -0.01831 | 123.0515 | 122.7173 | 52.533 | -123.1476 | 122.9874 | 122.9279 | 90.2527 | -123.1796
3957.0156 | 123.0698 | -45.1401 | 77.8519 | -0.24429 | 0.013217 | 0.078291 | 0.074149 | 0.1295 | 0.0048363 | -0.0096409 | -0.35873 | -0.012117 | 0.072382 | 0.059535 | 0.012967 | -0.011974 | 77.536 | 77.7466 | 7.1136 | -44.5175 | 77.9892 | -45.1813 | -45.2728 | -38.475 | 44.9295 | -45.1126 | 77.9572 | 77.8656 | -45.3369 | -45.3827 | -0.041198 | -0.13275 | 0.13733 | 122.8867 | 0.62256 | 0.75531 | -0.31586 | -0.19684 | -0.24261 | 0.10529 | 6.665 | 0.027466 | 0.27008 | 0.013733 | 123.1293 | 122.6761 | 52.2537 | -123.1247 | 123.0972 | 123.0057 | 90.0696 | -123.2346
3958.0156 | 123.0606 | -45.1859 | 77.774 | 3.5094 | 0.018771 | 0.076582 | 0.078207 | 0.12864 | 0.0091089 | -0.0077183 | 0.068512 | -0.0089124 | 0.072595 | 0.062525 | 0.014676 | -0.010478 | 77.5269 | 77.6413 | 7.0908 | -44.5908 | 77.9297 | -45.2271 | -45.3781 | -38.53 | 44.902 | -45.1584 | 77.8885 | 77.8015 | -45.3918 | -45.4102 | -0.041199 | -0.19226 | 0.15564 | 122.8271 | 0.59509 | 0.78735 | -0.24719 | -0.20599 | -0.2243 | 0.11444 | 6.6559 | 0.027466 | 0.25177 | 0.027466 | 123.1155 | 122.7127 | 52.2766 | -123.1522 | 123.0743 | 122.9874 | 90.0879 | -123.1842
3959.0156 | 123.0743 | -45.5475 | 77.4216 | -0.26718 | 0.016421 | 0.076154 | 0.075858 | 0.13121 | 0.0059045 | -0.010282 | -0.15274 | -0.0097668 | 0.070032 | 0.059107 | 0.012326 | -0.012401 | 77.1103 | 77.2842 | 7.0267 | -44.9387 | 77.5223 | -45.6665 | -45.7626 | -38.9328 | 44.632 | -45.5658 | 77.4994 | 77.4078 | -45.7443 | -45.7809 | -0.11902 | -0.21515 | 0.10071 | 122.8317 | 0.60883 | 0.82397 | -0.31128 | -0.19684 | -0.23346 | 0.07782 | 6.6147 | -0.018311 | 0.21515 | -0.013733 | 123.0698 | 122.6578 | 52.5742 | -123.1842 | 123.0469 | 122.9553 | 90.1794 | -123.2025
3960.0156 | 123.111 | -45.3644 | 77.6093 | -0.099335 | 0.011294 | 0.075727 | 0.07778 | 0.128 | 0.0018457 | -0.0085727 | -0.2214 | -0.0095532 | 0.071314 | 0.060389 | 0.011899 | -0.010478 | 77.1881 | 77.3758 | 7.1594 | -44.8334 | 77.623 | -45.5292 | -45.6299 | -38.736 | 44.7968 | -45.3644 | 77.6642 | 77.5726 | -45.6619 | -45.6528 | -0.1648 | -0.2655 | 0.013733 | 122.7402 | 0.53101 | 0.79651 | -0.42114 | -0.29755 | -0.28839 | 0.054932 | 6.6284 | 0 | 0.28839 | -0.036621 | 122.9874 | 122.5525 | 52.5238 | -123.2391 | 123.0286 | 122.937 | 90.1611 | -123.262
3961.0156 | 123.0515 | -45.694 | 77.2888 | -0.21378 | 0.014285 | 0.075086 | 0.074576 | 0.1295 | 0.0020593 | -0.010495 | -0.20615 | -0.0099806 | 0.070673 | 0.059321 | 0.011258 | -0.01176 | 77.0004 | 77.1423 | 7.1365 | -45.0302 | 77.4307 | -45.7764 | -45.8542 | -38.9603 | 44.5175 | -45.639 | 77.3895 | 77.2934 | -45.9045 | -45.9091 | -0.082397 | -0.16022 | 0.14191 | 122.8363 | 0.66376 | 0.82398 | -0.28839 | -0.21057 | -0.21515 | 0.10071 | 6.7337 | 0.054932 | 0.27008 | 0.004578 | 123.1247 | 122.6944 | 52.8305 | -123.143 | 123.0835 | 122.9874 | 90.2115 | -123.1979
3962.0156 | 123.0331 | -45.8496 | 77.1515 | -0.24429 | 0.012362 | 0.075086 | 0.075003 | 0.12928 | 0.0048363 | -0.0070773 | -0.15274 | -0.011476 | 0.068323 | 0.058039 | 0.011685 | -0.012614 | 76.8127 | 77.0508 | 7.045 | -45.163 | 77.2522 | -45.8954 | -46.0098 | -39.1388 | 44.3939 | -45.7993 | 77.2202 | 77.1332 | -46.0876 | -46.1105 | -0.045777 | -0.16022 | 0.10071 | 122.9004 | 0.68664 | 0.84686 | -0.33875 | -0.23804 | -0.26093 | 0.068665 | 6.7108 | 0.050354 | 0.31128 | -0.01831 | 123.1018 | 122.6624 | 52.8946 | -123.1613 | 123.0698 | 122.9828 | 90.2435 | -123.262
3963.0156 | 123.0972 | -45.5887 | 77.3804 | 0.14481 | 0.017062 | 0.074659 | 0.07479 | 0.128 | 0.0076135 | -0.0081455 | 0.09903 | -0.0086988 | 0.070459 | 0.060389 | 0.014676 | -0.012401 | 77.0966 | 77.2156 | 6.9717 | -44.9341 | 77.5406 | -45.6528 | -45.7443 | -38.8779 | 44.577 | -45.6024 | 77.4719 | 77.3849 | -45.7855 | -45.8313 | -0.064087 | -0.15564 | 0.16022 | 122.8043 | 0.6546 | 0.81024 | -0.28381 | -0.19684 | -0.24262 | 0.091553 | 6.7108 | -0.013733 | 0.22888 | 0.004578 | 123.1293 | 122.6852 | 52.5604 | -123.1247 | 123.0606 | 122.9736 | 90.1657 | -123.2117
3964.0156 | 123.024 | -45.5109 | 77.4857 | -0.25192 | 0.012576 | 0.07295 | 0.075644 | 0.1295 | 0.0044091 | -0.0075047 | -0.084076 | -0.0078442 | 0.072809 | 0.058253 | 0.014035 | -0.012614 | 77.1652 | 77.655 | 7.1228 | -44.902 | 77.6413 | -45.5109 | -45.639 | -38.8504 | 44.6823 | -45.575 | 77.5131 | 77.449 | -45.7626 | -45.8038 | 0 | -0.12817 | 0.15564 | 123.1659 | 0.60882 | 0.737 | -0.32044 | -0.25177 | -0.29297 | 0.027466 | 6.6605 | -0.064087 | 0.22888 | -0.036621 | 123.1522 | 122.6761 | 52.6337 | -123.1247 | 123.024 | 122.9599 | 90.1932 | -123.2895
3965.0156 | 123.0698 | -45.8679 | 77.124 | -0.22141 | 0.017062 | 0.077009 | 0.076712 | 0.13099 | 0.0056909 | -0.0070773 | -0.19852 | -0.0089124 | 0.071527 | 0.061244 | 0.015103 | -0.012614 | 76.8723 | 77.0508 | 6.926 | -45.0943 | 77.2934 | -45.8725 | -45.9915 | -39.061 | 44.4763 | -45.7809 | 77.2293 | 77.1561 | -46.0464 | -46.0876 | -0.004578 | -0.1236 | 0.16937 | 122.9187 | 0.77362 | 0.89722 | -0.25177 | -0.17853 | -0.21973 | 0.10529 | 6.8069 | 0.086975 | 0.3067 | 0.032044 | 123.1613 | 122.7402 | 52.7939 | -123.1155 | 123.0972 | 123.024 | 90.3442 | -123.2117
3966.0156 | 123.056 | -46.17 | 76.767 | -0.168 | 0.015994 | 0.076795 | 0.075217 | 0.12715 | 0.0059045 | -0.0075047 | -0.168 | -0.011049 | 0.069818 | 0.060176 | 0.013394 | -0.01176 | 76.5427 | 76.7258 | 6.4957 | -45.4376 | 76.9638 | -46.225 | -46.3257 | -39.418 | 44.1788 | -46.1929 | 76.9089 | 76.7944 | -46.3989 | -46.3989 | -0.054932 | -0.15564 | 0.19684 | 122.8958 | 0.73242 | 0.88806 | -0.2243 | -0.22888 | -0.22888 | 0.14191 | 6.752 | -0.022888 | 0.20599 | 0.027466 | 123.1338 | 122.7127 | 52.6657 | -123.0927 | 123.0789 | 122.9645 | 90.3488 | -123.1659
3967.0156 | 123.0835 | -45.8313 | 77.1515 | -0.22141 | 0.017276 | 0.075727 | 0.074149 | 0.128 | 0.0050499 | -0.0085727 | -0.12985 | -0.0097668 | 0.072595 | 0.059321 | 0.013181 | -0.013255 | 76.973 | 77.1515 | 6.9809 | -45.0073 | 77.3712 | -45.8221 | -45.9549 | -38.9008 | 44.6365 | -45.6711 | 77.3071 | 77.2339 | -45.9824 | -46.0373 | 0.009155 | -0.1236 | 0.21973 | 122.9828 | 0.82398 | 0.94757 | -0.17853 | -0.15106 | -0.20599 | 0.15564 | 6.9305 | 0.16022 | 0.36621 | 0.082398 | 123.2025 | 122.8043 | 52.8122 | -123.1064 | 123.1384 | 123.0652 | 90.4678 | -123.1888
3968.0156 | 123.0698 | -45.7581 | 77.2202 | -0.045929 | 0.016421 | 0.074659 | 0.072226 | 0.1327 | 0.0071863 | -0.0060093 | -0.038299 | -0.0082716 | 0.069177 | 0.058894 | 0.016598 | -0.011333 | 76.9592 | 77.1378 | 6.9305 | -45.0485 | 77.3209 | -45.8176 | -45.9183 | -38.9099 | 44.6136 | -45.6848 | 77.3392 | 77.2476 | -45.9274 | -45.9869 | -0.059509 | -0.16022 | 0.10071 | 122.8958 | 0.70953 | 0.86975 | -0.26093 | -0.16937 | -0.22888 | 0.11902 | 6.8481 | 0.073243 | 0.30212 | 0.027466 | 123.0789 | 122.7173 | 52.6886 | -123.1384 | 123.0972 | 123.0057 | 90.3717 | -123.2071
3969.0156 | 123.1018 | -45.9961 | 77.0096 | -0.38925 | 0.012576 | 0.07765 | 0.078635 | 0.12993 | 0.0029137 | -0.0094273 | -0.14511 | -0.009126 | 0.069605 | 0.057612 | 0.011472 | -0.010265 | 76.6296 | 76.8585 | 6.839 | -45.2957 | 77.0874 | -46.1197 | -46.2021 | -39.2303 | 44.339 | -46.0144 | 77.037 | 76.9455 | -46.2799 | -46.257 | -0.1236 | -0.20599 | 0.077819 | 122.8546 | 0.70038 | 0.90637 | -0.37994 | -0.28381 | -0.26093 | 0.027465 | 6.7657 | -0.01831 | 0.24262 | -0.064087 | 123.0835 | 122.6257 | 52.8351 | -123.2117 | 123.0331 | 122.9416 | 90.3351 | -123.2666
3970.0156 | 123.0331 | -46.344 | 76.6068 | -0.21378 | 0.015994 | 0.076582 | 0.076285 | 0.12886 | 0.0063317 | -0.0070773 | -0.19852 | -0.0093396 | 0.071741 | 0.058039 | 0.01553 | -0.013255 | 76.3687 | 76.5564 | 6.6879 | -45.6207 | 76.7624 | -46.3898 | -46.5088 | -39.4867 | 44.1101 | -46.2753 | 76.7075 | 76.6068 | -46.5591 | -46.6095 | -0.045777 | -0.16479 | 0.15564 | 122.9004 | 0.72327 | 0.88806 | -0.23804 | -0.21515 | -0.2655 | 0.10071 | 6.8573 | 0.068664 | 0.33417 | 0 | 123.1064 | 122.7127 | 53.0319 | -123.1155 | 123.0515 | 122.9507 | 90.4541 | -123.2162
3971.0156 | 123.0652 | -45.6711 | 77.2934 | -0.22903 | 0.021121 | 0.073164 | 0.074576 | 0.1295 | 0.0065453 | -0.0075047 | -0.061188 | -0.010194 | 0.071741 | 0.059962 | 0.015317 | -0.011974 | 76.9592 | 77.1652 | 6.5369 | -45.0256 | 77.3392 | -45.8313 | -45.9183 | -38.887 | 44.6411 | -45.6711 | 77.298 | 77.2064 | -45.9503 | -45.9595 | -0.16022 | -0.24719 | 0.045776 | 122.8363 | 0.64545 | 0.89264 | -0.33417 | -0.27923 | -0.28839 | 0.004578 | 6.7841 | 0 | 0.28839 | -0.086975 | 123.0103 | 122.6303 | 52.2079 | -123.2117 | 122.9691 | 122.8775 | 90.3122 | -123.2529
3972.0156 | 123.0606 | -46.1334 | 76.8311 | -0.24429 | 0.014712 | 0.076795 | 0.07244 | 0.128 | 0.00099115 | -0.0085727 | -0.10696 | -0.010194 | 0.072595 | 0.058894 | 0.012967 | -0.010905 | 76.5381 | 76.7532 | 6.8253 | -45.433 | 76.9501 | -46.1792 | -46.312 | -39.2532 | 44.252 | -46.0602 | 76.9409 | 76.8311 | -46.3531 | -46.3898 | -0.045776 | -0.17853 | 0.11902 | 122.8867 | 0.70038 | 0.87891 | -0.29297 | -0.21973 | -0.25635 | 0.10986 | 6.8802 | 0.073242 | 0.32959 | 0 | 123.0835 | 122.6715 | 52.9587 | -123.143 | 123.0743 | 122.9645 | 90.3854 | -123.2208
3973.0156 | 123.1338 | -46.3943 | 76.5701 | 0.13718 | 0.016849 | 0.076795 | 0.075217 | 0.13057 | 0.0067589 | -0.0066501 | 0.13718 | -0.0086988 | 0.073664 | 0.059962 | 0.012753 | -0.010905 | 76.2817 | 76.4053 | 6.7291 | -45.6757 | 76.7349 | -46.4539 | -46.5546 | -39.505 | 43.9774 | -46.3898 | 76.6479 | 76.5518 | -46.5912 | -46.6187 | -0.059509 | -0.16022 | 0.1648 | 122.7997 | 0.71869 | 0.87891 | -0.28839 | -0.19684 | -0.2243 | 0.07782 | 6.8893 | 0.004577 | 0.22888 | -0.01831 | 123.1293 | 122.6761 | 53.1235 | -123.1247 | 123.0423 | 122.9462 | 90.3717 | -123.1888
3974.0156 | 123.0331 | -46.8567 | 76.1169 | -0.25192 | 0.013858 | 0.078291 | 0.073935 | 0.12928 | 0.0044091 | -0.010068 | 0.13718 | -0.0095532 | 0.070032 | 0.059321 | 0.014249 | -0.0087692 | 75.7507 | 76.3504 | 6.8939 | -46.1655 | 76.2817 | -46.8842 | -47.0032 | -39.917 | 43.6615 | -46.8338 | 76.2177 | 76.1627 | -47.0444 | -47.1085 | -0.027466 | -0.14648 | 0.16479 | 123.2071 | 0.69122 | 0.83771 | -0.36621 | -0.18768 | -0.25177 | 0.10071 | 6.9397 | 0.022888 | 0.27466 | 0.045777 | 123.1384 | 122.6074 | 53.7506 | -123.1201 | 123.0743 | 123.0194 | 90.5182 | -123.2254
3975.0156 | 123.1018 | -46.1243 | 76.8356 | -0.21378 | 0.016421 | 0.0753 | 0.077994 | 0.13014 | 0.0071863 | -0.0079319 | -0.15274 | -0.010194 | 0.070032 | 0.058467 | 0.015958 | -0.010051 | 76.593 | 76.7715 | 6.8298 | -45.3644 | 77.0004 | -46.1563 | -46.2845 | -39.1388 | 44.3665 | -46.0464 | 76.9684 | 76.8677 | -46.3028 | -46.3348 | -0.032043 | -0.16022 | 0.16479 | 122.8958 | 0.75989 | 0.9201 | -0.24261 | -0.17853 | -0.21057 | 0.13275 | 6.9855 | 0.07782 | 0.28839 | 0.032044 | 123.1247 | 122.7173 | 52.9541 | -123.1201 | 123.0927 | 122.9919 | 90.4907 | -123.1705
3976.0156 | 123.0606 | -46.106 | 76.8539 | -0.22903 | 0.013003 | 0.077009 | 0.073081 | 0.12822 | 0.0022729 | -0.0087863 | -0.11459 | -0.012544 | 0.070886 | 0.05868 | 0.013181 | -0.01176 | 76.5976 | 76.8311 | 6.9077 | -45.3461 | 76.9638 | -46.1655 | -46.2891 | -39.1434 | 44.3802 | -46.0098 | 76.9409 | 76.8723 | -46.312 | -46.3577 | -0.059509 | -0.18311 | 0.10986 | 122.937 | 0.75989 | 0.94299 | -0.25635 | -0.20599 | -0.25177 | 0.086975 | 6.9626 | 0.09613 | 0.3479 | 0.01831 | 123.0698 | 122.7036 | 53.0136 | -123.143 | 123.0469 | 122.9782 | 90.4861 | -123.2117
3977.0156 | 123.0423 | -45.8588 | 77.0737 | -0.168 | 0.017276 | 0.077436 | 0.076071 | 0.12907 | 0.0056909 | -0.0089999 | -0.12985 | -0.0095532 | 0.070886 | 0.05868 | 0.012326 | -0.011546 | 76.8127 | 76.9913 | 6.7062 | -45.1309 | 77.211 | -45.9503 | -46.0556 | -38.9328 | 44.577 | -45.8267 | 77.1927 | 77.1057 | -46.0968 | -46.1105 | -0.091552 | -0.19684 | 0.13733 | 122.85 | 0.72784 | 0.92468 | -0.26093 | -0.23804 | -0.25177 | 0.11902 | 6.926 | 0.032044 | 0.28381 | 0.032044 | 123.0698 | 122.6715 | 52.565 | -123.1293 | 123.0515 | 122.9645 | 90.4358 | -123.1842
3978.0156 | 123.0927 | -45.8771 | 77.0645 | -0.17563 | 0.016421 | 0.077009 | 0.076071 | 0.12864 | 0.0063317 | -0.0081455 | -0.12985 | -0.0086988 | 0.070673 | 0.060816 | 0.01489 | -0.011119 | 76.8311 | 77.0233 | 6.8344 | -45.108 | 77.243 | -45.9412 | -46.0464 | -38.8458 | 44.6274 | -45.7672 | 77.1973 | 77.0874 | -46.0693 | -46.106 | -0.064087 | -0.16937 | 0.17853 | 122.9004 | 0.76904 | 0.93842 | -0.23346 | -0.19226 | -0.22888 | 0.13275 | 7.0312 | 0.10986 | 0.33874 | 0.022888 | 123.1201 | 122.7081 | 52.7115 | -123.111 | 123.0743 | 122.9645 | 90.5045 | -123.1705
3979.0156 | 123.0789 | -46.7239 | 76.2222 | -0.14511 | 0.017062 | 0.075727 | 0.077353 | 0.12907 | 0.0061181 | -0.0070773 | -0.11459 | -0.0084852 | 0.070673 | 0.059962 | 0.014035 | -0.012401 | 75.975 | 76.1581 | 6.7245 | -45.9641 | 76.3596 | -46.8109 | -46.907 | -39.743 | 43.808 | -46.6827 | 76.3275 | 76.2314 | -46.9482 | -46.9849 | -0.086975 | -0.18311 | 0.13733 | 122.8821 | 0.75989 | 0.94299 | -0.24719 | -0.2243 | -0.26093 | 0.10529 | 6.9809 | 0.041199 | 0.30212 | 0.009155 | 123.0835 | 122.699 | 53.4485 | -123.1293 | 123.0515 | 122.9553 | 90.5319 | -123.2071
3980.0156 | 123.0972 | -46.6003 | 76.387 | -0.52658 | 0.01279 | 0.078932 | 0.07479 | 0.12843 | 0.0039819 | -0.0085727 | -0.099335 | -0.0099806 | 0.070886 | 0.060176 | 0.013394 | -0.011119 | 76.0437 | 76.2634 | 6.6971 | -45.8817 | 76.4786 | -46.6965 | -46.7697 | -39.6515 | 43.9407 | -46.2662 | 76.5244 | 76.4465 | -46.8018 | -46.8155 | -0.09613 | -0.16937 | 0.091553 | 122.8638 | 0.71869 | 0.88806 | -0.34332 | -0.20142 | -0.21515 | 0.13733 | 6.9489 | 0.33417 | 0.54932 | 0.059509 | 123.0789 | 122.644 | 53.2974 | -123.1567 | 123.1247 | 123.0469 | 90.5411 | -123.2025
3981.0156 | 123.0789 | -46.7148 | 76.2588 | -0.17563 | 0.017703 | 0.075514 | 0.076285 | 0.12864 | 0.0063317 | -0.0092137 | -0.17563 | -0.011689 | 0.070459 | 0.059321 | 0.015958 | -0.012614 | 76.0025 | 76.1856 | 6.665 | -45.932 | 76.3916 | -46.8109 | -46.8887 | -39.7018 | 43.9316 | -46.6324 | 76.3641 | 76.2314 | -46.9162 | -46.962 | -0.09613 | -0.17395 | 0.13275 | 122.9004 | 0.78278 | 0.95673 | -0.25635 | -0.20142 | -0.24719 | 0.10529 | 7.0129 | 0.082398 | 0.32959 | -0.027466 | 123.1064 | 122.7173 | 53.3798 | -123.1476 | 123.0789 | 122.9462 | 90.6464 | -123.2208
3982.0156 | 123.0286 | -46.8201 | 76.1124 | -0.20615 | 0.01578 | 0.079572 | 0.073081 | 0.13035 | 0.0041955 | -0.0089999 | -0.19089 | -0.010194 | 0.069605 | 0.060389 | 0.01489 | -0.010051 | 75.9384 | 76.1444 | 6.6238 | -46.0098 | 76.3824 | -46.8292 | -46.9162 | -39.8529 | 43.7805 | -46.8613 | 76.2222 | 76.1307 | -47.0535 | -47.0901 | -0.009156 | -0.096131 | 0.27008 | 122.9645 | 0.81024 | 0.90637 | -0.17395 | -0.23346 | -0.27008 | 0.10986 | 6.9672 | -0.041199 | 0.22888 | 0.01831 | 123.2025 | 122.7585 | 53.4439 | -123.0286 | 123.0423 | 122.9507 | 90.6006 | -123.2025
3983.0156 | 123.024 | -46.843 | 76.1124 | -0.00015269 | 0.020267 | 0.077436 | 0.075858 | 0.12715 | 0.0071863 | -0.0079319 | 0.09903 | -0.0082716 | 0.07345 | 0.060389 | 0.015744 | -0.012401 | 75.737 | 75.9018 | 6.6147 | -46.1838 | 76.1581 | -47.0352 | -47.0993 | -39.9216 | 43.7073 | -46.9208 | 76.1581 | 76.1032 | -47.0718 | -47.1313 | -0.19226 | -0.25635 | 0.045776 | 122.7448 | 0.65918 | 0.91553 | -0.37537 | -0.22888 | -0.28839 | 0.045776 | 6.9214 | -0.077819 | 0.21057 | -0.009156 | 123.0011 | 122.58 | 53.4576 | -123.2117 | 123.0011 | 122.9462 | 90.5502 | -123.2437
3984.0156 | 123.0469 | -47.0032 | 75.9155 | -0.19089 | 0.012576 | 0.07765 | 0.074576 | 0.12886 | 0.0031273 | -0.0079319 | 1.0985 | -0.01233 | 0.069177 | 0.06103 | 0.013181 | -0.0096238 | 75.6821 | 75.8926 | 6.6696 | -46.2479 | 76.0941 | -47.0856 | -47.1909 | -39.9536 | 43.7805 | -46.9299 | 76.0712 | 76.0025 | -47.2046 | -47.2229 | -0.082397 | -0.18768 | 0.17853 | 122.8958 | 0.75531 | 0.94299 | -0.23346 | -0.20142 | -0.21973 | 0.15564 | 7.0496 | 0.073242 | 0.29297 | 0.086975 | 123.0972 | 122.6852 | 53.6728 | -123.1064 | 123.0743 | 123.0057 | 90.7837 | -123.1384
3985.0156 | 123.0469 | -47.3557 | 75.5905 | -0.19852 | 0.017062 | 0.078291 | 0.075644 | 0.13057 | 0.0059045 | -0.0075047 | -0.21378 | -0.0099806 | 0.070246 | 0.058467 | 0.014035 | -0.011119 | 75.3159 | 75.4807 | 6.6238 | -46.55 | 75.7416 | -47.4518 | -47.5433 | -40.2328 | 43.3777 | -47.2275 | 75.6912 | 75.6226 | -47.5616 | -47.612 | -0.09613 | -0.18768 | 0.15106 | 122.8363 | 0.80566 | 0.99335 | -0.27466 | -0.20599 | -0.25635 | 0.10071 | 7.1228 | 0.12817 | 0.38452 | 0.032044 | 123.0972 | 122.6715 | 53.9795 | -123.1338 | 123.0469 | 122.9782 | 90.7333 | -123.2025
3986.0156 | 123.0377 | -47.9782 | 74.9771 | -0.25192 | 0.01514 | 0.078718 | 0.073294 | 0.12672 | 0.0039819 | -0.0098545 | -0.13748 | -0.0099806 | 0.070459 | 0.060603 | 0.014249 | -0.010265 | 74.675 | 74.8627 | 6.4545 | -47.168 | 75.1007 | -48.0423 | -48.1613 | -40.8966 | 42.7734 | -47.9004 | 75.0687 | 74.9908 | -48.2117 | -48.23 | -0.064087 | -0.18311 | 0.1236 | 122.8409 | 0.81024 | 0.99335 | -0.30212 | -0.23346 | -0.25177 | 0.091553 | 7.0816 | 0.077819 | 0.32959 | 0.013733 | 123.0789 | 122.6532 | 54.4327 | -123.1384 | 123.0469 | 122.9691 | 90.7516 | -123.2071
3987.0156 | 123.1018 | -47.6212 | 75.3159 | 0.17532 | 0.020053 | 0.079359 | 0.074576 | 0.13078 | 0.0071863 | -0.0085727 | -0.084076 | -0.0084852 | 0.070459 | 0.060603 | 0.015744 | -0.013255 | 75.087 | 75.2609 | 6.6055 | -46.7789 | 75.4852 | -47.6944 | -47.7859 | -40.48 | 43.1671 | -47.5388 | 75.444 | 75.3296 | -47.8271 | -47.8683 | -0.073242 | -0.16479 | 0.16937 | 122.8821 | 0.84229 | 1.0071 | -0.22888 | -0.20599 | -0.24719 | 0.12817 | 7.1411 | 0.082398 | 0.32959 | 0.013733 | 123.1064 | 122.7081 | 54.2267 | -123.1018 | 123.0652 | 122.9507 | 90.7883 | -123.1842
3988.0156 | 123.0515 | -47.6715 | 75.3067 | -0.20615 | 0.013644 | 0.081495 | 0.074576 | 0.12928 | 0.0027001 | -0.0092137 | -0.16037 | -0.009126 | 0.072168 | 0.058253 | 0.013181 | -0.010692 | 74.9817 | 75.2014 | 6.6147 | -46.8338 | 75.4395 | -47.7219 | -47.8592 | -40.5441 | 43.071 | -47.5891 | 75.4211 | 75.3067 | -47.9004 | -47.9233 | -0.050354 | -0.18768 | 0.13275 | 122.8729 | 0.83771 | 1.0254 | -0.32501 | -0.22888 | -0.25177 | 0.11444 | 7.1274 | 0.082398 | 0.33417 | 0 | 123.111 | 122.6532 | 54.2862 | -123.1659 | 123.0927 | 122.9782 | 90.7425 | -123.23
3989.0156 | 123.0652 | -48.0469 | 74.9039 | -0.24429 | 0.018985 | 0.079359 | 0.076071 | 0.13185 | 0.0084679 | -0.0072911 | -0.19852 | -0.011049 | 0.071955 | 0.059535 | 0.011472 | -0.012187 | 74.5468 | 74.9451 | 6.5323 | -47.2275 | 75.0412 | -48.1293 | -48.2391 | -40.8508 | 42.7322 | -47.9233 | 74.9954 | 74.9039 | -48.2574 | -48.2941 | -0.082397 | -0.19226 | 0.13733 | 122.9919 | 0.8194 | 1.0117 | -0.35706 | -0.21057 | -0.24719 | 0.091552 | 7.196 | 0.1236 | 0.37079 | 0 | 123.0881 | 122.5937 | 54.5792 | -123.143 | 123.0423 | 122.9507 | 90.7791 | -123.1979
3990.0156 | 123.0057 | -47.3648 | 75.5997 | -0.19089 | 0.011722 | 0.080213 | 0.073508 | 0.12928 | 0.0027001 | -0.0070773 | -0.091705 | -0.0086988 | 0.070246 | 0.060816 | 0.011685 | -0.0096238 | 75.2884 | 75.499 | 6.6605 | -46.463 | 75.7324 | -47.4152 | -47.5113 | -40.2008 | 43.3228 | -47.1909 | 75.737 | 75.6638 | -47.5525 | -47.5754 | -0.050354 | -0.14648 | 0.13275 | 122.8638 | 0.90179 | 1.0483 | -0.31128 | -0.18768 | -0.21057 | 0.13733 | 7.164 | 0.17395 | 0.38452 | 0.064087 | 123.0972 | 122.6532 | 54.0253 | -123.111 | 123.1018 | 123.0286 | 90.6876 | -123.175
3991.0156 | 123.056 | -47.5754 | 75.3479 | 0.14481 | 0.021976 | 0.076368 | 0.075644 | 0.12907 | 0.0056909 | -0.0079319 | 0.20584 | -0.007417 | 0.070032 | 0.059107 | 0.017026 | -0.011119 | 75.0412 | 75.1831 | 6.5826 | -46.7422 | 75.4715 | -47.6715 | -47.7997 | -40.4068 | 43.0756 | -47.4884 | 75.4532 | 75.3708 | -47.7768 | -47.8088 | -0.096131 | -0.22431 | 0.1236 | 122.7585 | 0.83313 | 1.0574 | -0.3067 | -0.20142 | -0.23346 | 0.10529 | 7.1686 | 0.086975 | 0.32044 | 0.022889 | 123.0469 | 122.6166 | 54.158 | -123.1476 | 123.0286 | 122.9462 | 90.6509 | -123.1567
3992.0156 | 123.0148 | -47.6166 | 75.3571 | -0.38162 | 0.013431 | 0.079359 | 0.070517 | 0.12886 | 0.0024865 | -0.0092137 | -0.13748 | -0.011262 | 0.070886 | 0.05868 | 0.014035 | -0.0089828 | 75.0916 | 75.3021 | 6.5964 | -46.7377 | 75.4761 | -47.6807 | -47.7814 | -40.4205 | 43.0893 | -47.5067 | 75.4623 | 75.3937 | -47.818 | -47.85 | -0.064087 | -0.16479 | 0.11902 | 122.9187 | 0.87891 | 1.0437 | -0.2655 | -0.20142 | -0.23346 | 0.10528 | 7.196 | 0.10986 | 0.34332 | 0.036621 | 123.0927 | 122.7081 | 54.213 | -123.1384 | 123.0789 | 123.0103 | 90.7059 | -123.2071
3993.0156 | 123.0652 | -48.1293 | 74.8306 | -0.14511 | 0.019412 | 0.078932 | 0.078207 | 0.13057 | 0.0086815 | -0.0072911 | -1.2895 | -0.008058 | 0.072595 | 0.058039 | 0.016812 | -0.012401 | 74.5926 | 74.7803 | 6.4819 | -47.0993 | 75 | -48.1476 | -48.262 | -40.8737 | 42.6315 | -48.0148 | 74.9268 | 74.8169 | -48.317 | -48.3719 | -0.018311 | -0.13275 | 0.16937 | 122.9095 | 1.03 | 1.1627 | -0.23804 | -0.18768 | -0.24262 | 0.096131 | 7.2556 | 0.11444 | 0.35706 | -0.013732 | 123.1293 | 122.7219 | 54.6112 | -123.0927 | 123.056 | 122.9462 | 90.7608 | -123.2025
3994.0156 | 123.0331 | -47.7448 | 75.2106 | -0.168 | 0.010867 | 0.079786 | 0.073508 | 0.13163 | 0.0035547 | -0.0075047 | -0.2214 | -0.012544 | 0.0711 | 0.060176 | 0.015958 | -0.010692 | 75.0137 | 75.3525 | 6.5231 | -46.9574 | 75.3891 | -47.8088 | -47.9004 | -40.5075 | 42.9703 | -47.6257 | 75.3525 | 75.2243 | -47.9782 | -47.9828 | -0.064087 | -0.15564 | 0.17853 | 123.0972 | 0.78735 | 0.94299 | -0.19684 | -0.23346 | -0.23804 | 0.14191 | 7.2372 | 0.11902 | 0.35706 | 0.013733 | 123.1338 | 122.7585 | 54.2679 | -123.111 | 123.0972 | 122.9691 | 90.715 | -123.1934
3995.0156 | 123.0652 | -47.8958 | 75.0595 | -0.17563 | 0.015994 | 0.081068 | 0.07479 | 0.13185 | 0.0063317 | -0.0081455 | -0.15274 | -0.0084852 | 0.072595 | 0.059748 | 0.015958 | -0.013255 | 74.8077 | 74.9588 | 6.3446 | -47.0078 | 75.1968 | -47.9691 | -48.0835 | -40.6403 | 42.8192 | -47.8088 | 75.1602 | 75.087 | -48.0881 | -48.1201 | -0.073242 | -0.18768 | 0.13733 | 122.8546 | 0.88806 | 1.0757 | -0.25177 | -0.19226 | -0.2243 | 0.10071 | 7.2556 | 0.086975 | 0.31128 | 0.027466 | 123.0927 | 122.7036 | 54.2404 | -123.143 | 123.056 | 122.9828 | 90.715 | -123.1796
3996.0156 | 123.0148 | -47.8226 | 75.1328 | -0.03067 | 0.021335 | 0.078504 | 0.078207 | 0.12886 | 0.0086815 | -0.0075047 | 0.030365 | -0.0099806 | 0.073236 | 0.060176 | 0.016171 | -0.011546 | 74.881 | 75.0549 | 6.546 | -46.9574 | 75.2609 | -47.9187 | -48.024 | -40.5441 | 42.8741 | -47.7448 | 75.2243 | 75.1328 | -48.0698 | -48.0881 | -0.09613 | -0.20142 | 0.12817 | 122.8775 | 0.86517 | 1.0666 | -0.25177 | -0.24719 | -0.2655 | 0.091553 | 7.2784 | 0.07782 | 0.34332 | 0 | 123.0835 | 122.7036 | 54.3686 | -123.1567 | 123.0469 | 122.9553 | 90.6967 | -123.2208
3997.0156 | 123.0286 | -48.0103 | 74.9496 | -0.22903 | 0.014499 | 0.077863 | 0.075003 | 0.12822 | 0.0031273 | -0.010282 | -0.23666 | -0.010621 | 0.072382 | 0.061671 | 0.014249 | -0.0094102 | 74.8764 | 74.8718 | 6.4041 | -47.1634 | 75.087 | -48.056 | -48.175 | -40.7501 | 42.7094 | -47.9141 | 75.0412 | 74.9771 | -48.2529 | -48.2712 | -0.045776 | -0.16479 | 0.13733 | 122.8821 | 0.84686 | 1.0117 | -0.073242 | -0.24261 | -0.26092 | 0.091553 | 7.2601 | 0.09613 | 0.35705 | 0.027466 | 123.0972 | 122.8867 | 54.4144 | -123.1247 | 123.0515 | 122.9874 | 90.7196 | -123.2208
3998.0156 | 123.0927 | -48.0148 | 74.913 | -0.21378 | 0.017703 | 0.080641 | 0.073508 | 0.12928 | 0.0059045 | -0.0057957 | -0.084076 | -0.008058 | 0.072168 | 0.058039 | 0.01489 | -0.011119 | 74.6841 | 74.8856 | 6.3263 | -47.1268 | 75.0504 | -48.1018 | -48.2071 | -40.6998 | 42.7368 | -47.8958 | 75.0046 | 74.9405 | -48.2483 | -48.2895 | -0.086975 | -0.19226 | 0.13733 | 122.9004 | 0.88806 | 1.0803 | -0.22888 | -0.23346 | -0.27466 | 0.091553 | 7.3151 | 0.11902 | 0.39368 | 0.027466 | 123.0652 | 122.699 | 54.3411 | -123.1201 | 123.0194 | 122.9553 | 90.7516 | -123.2025
3999.0156 | 123.0652 | -48.7747 | 74.1898 | -0.19852 | 0.017703 | 0.081068 | 0.075003 | 0.1295 | 0.0041955 | -0.0094273 | -0.25192 | -0.0082716 | 0.071741 | 0.060176 | 0.01553 | -0.0091966 | 73.8831 | 74.0799 | 6.2164 | -47.8729 | 74.3088 | -48.88 | -48.9532 | -41.4871 | 42.0593 | -48.6557 | 74.2493 | 74.1898 | -49.0082 | -49.0356 | -0.10529 | -0.17853 | 0.11902 | 122.8546 | 0.90179 | 1.0803 | -0.3067 | -0.23346 | -0.26093 | 0.05951 | 7.2876 | 0.11902 | 0.37994 | 0 | 123.0835 | 122.6578 | 54.9911 | -123.143 | 123.024 | 122.9645 | 90.834 | -123.2254
4000.0156 | 123.1155 | -48.6923 | 74.2126 | -0.168 | 0.013217 | 0.082136 | 0.072653 | 0.12843 | -0.0026405 | -0.010495 | -0.19089 | -0.014039 | 0.071527 | 0.059748 | 0.014462 | -0.0096238 | 74.1211 | 73.9975 | 6.3629 | -47.7402 | 74.3088 | -48.7839 | -48.88 | -41.3132 | 42.2012 | -48.5092 | 74.2767 | 74.2172 | -48.9166 | -48.9532 | -0.091553 | -0.18768 | 0.096131 | 122.6898 | 0.95215 | 1.1398 | -0.091552 | -0.2243 | -0.26093 | 0.064087 | 7.3792 | 0.18311 | 0.44403 | 0.004578 | 123.0011 | 122.8134 | 55.0552 | -123.0927 | 122.9691 | 122.9095 | 90.8936 | -123.1659
4001.0156 | 123.0011 | -48.674 | 74.2996 | 0.045624 | 0.021548 | 0.077009 | 0.078421 | 0.13078 | 0.0097497 | -0.0049411 | 0.11429 | -0.0076306 | 0.075373 | 0.059962 | 0.018948 | -0.013042 | 73.9883 | 74.144 | 6.3263 | -47.7722 | 74.4003 | -48.7793 | -48.8663 | -41.3223 | 42.1051 | -48.5825 | 74.3958 | 74.2676 | -48.9075 | -48.9395 | -0.10529 | -0.19226 | 0.10071 | 122.818 | 0.90179 | 1.0941 | -0.31128 | -0.23346 | -0.2655 | 0.09613 | 7.3517 | 0.091553 | 0.35706 | -0.032044 | 123.0743 | 122.6624 | 55.0003 | -123.1659 | 123.0698 | 122.9416 | 90.7791 | -123.2391
4002.0156 | 123.175 | -48.8297 | 74.0433 | -0.061188 | 0.0097989 | 0.083845 | 0.075003 | 0.128 | 0.00056395 | -0.0096409 | -0.0077819 | -0.011049 | 0.070032 | 0.059962 | 0.013608 | -0.0096238 | 73.8464 | 74.1257 | 6.4957 | -47.8592 | 74.1898 | -48.9075 | -48.999 | -41.3864 | 42.1417 | -48.5733 | 74.1348 | 74.0753 | -49.0265 | -49.0906 | -0.07782 | -0.16937 | 0.14648 | 122.9553 | 0.97046 | 1.1398 | -0.19684 | -0.19684 | -0.26093 | 0.091553 | 7.4432 | 0.25635 | 0.51727 | 0.032043 | 123.0194 | 122.6761 | 55.3253 | -123.0423 | 122.9645 | 122.905 | 90.9714 | -123.1338
4003.0156 | 123.0331 | -47.5113 | 75.4257 | -0.0077822 | 0.013431 | 0.082777 | 0.077353 | 0.12779 | 0.0031273 | -0.010922 | -0.10696 | -0.010835 | 0.070673 | 0.05868 | 0.016812 | -0.011974 | 75.1877 | 75.4028 | 6.7566 | -46.5454 | 75.531 | -47.5845 | -47.6761 | -40.1321 | 43.309 | -47.3511 | 75.499 | 75.4166 | -47.731 | -47.7493 | -0.073242 | -0.16479 | 0.10529 | 122.9141 | 0.96588 | 1.1307 | -0.23804 | -0.21973 | -0.23804 | 0.073242 | 7.3792 | 0.16022 | 0.39826 | -0.009155 | 123.0423 | 122.699 | 54.2679 | -123.1018 | 123.0103 | 122.9279 | 90.8203 | -123.175
4004.0156 | 123.1567 | -48.0148 | 74.8306 | -0.0077822 | 0.011508 | 0.084272 | 0.072653 | 0.128 | 0.0033411 | -0.010068 | 0.015106 | -0.01233 | 0.070886 | 0.060389 | 0.016598 | -0.010905 | 74.6933 | 74.8993 | 6.72 | -47.0856 | 74.9954 | -48.0927 | -48.2254 | -40.5945 | 42.8925 | -47.7951 | 74.9222 | 74.8169 | -48.2529 | -48.3032 | -0.077819 | -0.21057 | 0.16479 | 122.9141 | 0.92926 | 1.1398 | -0.13733 | -0.23804 | -0.28839 | 0.091553 | 7.4203 | 0.21973 | 0.50812 | -0.013732 | 123.0103 | 122.7081 | 54.7348 | -123.056 | 122.937 | 122.8317 | 90.9073 | -123.1339
4005.0156 | 123.0011 | -48.3948 | 74.5514 | -0.25192 | 0.013644 | 0.08235 | 0.075644 | 0.12822 | 0.0069727 | -0.0098545 | -0.168 | -0.010194 | 0.070673 | 0.059962 | 0.01788 | -0.012401 | 74.2767 | 74.469 | 6.3309 | -47.4609 | 74.6979 | -48.4772 | -48.5641 | -41.011 | 42.4713 | -48.2712 | 74.6658 | 74.5743 | -48.6237 | -48.6557 | -0.082398 | -0.16937 | 0.14648 | 122.8638 | 0.93384 | 1.1032 | -0.27466 | -0.22888 | -0.26093 | 0.11444 | 7.3837 | 0.1236 | 0.38452 | 0.022888 | 123.0927 | 122.6715 | 54.7256 | -123.1155 | 123.0606 | 122.9691 | 90.8661 | -123.2071
4006.0156 | 123.0835 | -49.3286 | 73.5901 | -0.0383 | 0.020053 | 0.080641 | 0.075858 | 0.12907 | 0.010818 | -0.0089999 | -0.068817 | -0.0093396 | 0.072809 | 0.059748 | 0.018521 | -0.013042 | 73.4116 | 73.5535 | 5.8365 | -48.3307 | 73.7412 | -49.4156 | -49.5438 | -41.8533 | 41.6336 | -49.2691 | 73.7 | 73.6084 | -49.5621 | -49.5987 | -0.086975 | -0.21515 | 0.15106 | 122.8821 | 0.99792 | 1.2131 | -0.17853 | -0.23346 | -0.27008 | 0.10986 | 7.4753 | 0.059509 | 0.32959 | 0.01831 | 123.0698 | 122.7402 | 55.1651 | -123.1338 | 123.0286 | 122.937 | 90.9622 | -123.1888
4007.0156 | 123.1476 | -49.0173 | 73.8831 | -0.22903 | 0.011722 | 0.081922 | 0.073081 | 0.13014 | 0.0016321 | -0.0081455 | 2.0674 | -0.010835 | 0.070246 | 0.060176 | 0.014676 | -0.011546 | 73.6954 | 73.9243 | 6.4362 | -48.0103 | 73.9655 | -49.0906 | -49.1867 | -41.5604 | 42.0181 | -48.848 | 73.9334 | 73.8785 | -49.2371 | -49.2416 | -0.073242 | -0.16937 | 0.082397 | 122.9416 | 1.0071 | 1.1765 | -0.18768 | -0.21973 | -0.2243 | 0.050354 | 7.457 | 0.16937 | 0.39368 | -0.004578 | 122.9828 | 122.7127 | 55.4535 | -123.0698 | 122.9507 | 122.8958 | 91.0355 | -123.1247
4008.0156 | 123.1659 | -48.9029 | 73.9792 | -1.0988 | 0.01279 | 0.083418 | 0.072012 | 0.13249 | 0.0039819 | -0.0089999 | 0.060883 | -0.012544 | 0.068537 | 0.057826 | 0.01553 | -0.010905 | 73.7549 | 74.0158 | 6.3995 | -47.9004 | 74.1074 | -48.999 | -49.1043 | -41.4093 | 42.0136 | -48.674 | 74.0616 | 73.9746 | -49.1364 | -49.1867 | -0.09613 | -0.20142 | 0.12817 | 122.9187 | 1.0025 | 1.2039 | -0.2243 | -0.23346 | -0.28381 | 0.082397 | 7.4936 | 0.22888 | 0.5127 | -0.004578 | 123.0103 | 122.6578 | 55.3024 | -123.0835 | 122.9645 | 122.8775 | 90.9164 | -123.1659
4009.0156 | 123.143 | -49.0814 | 73.7686 | -0.068817 | 0.010226 | 0.08299 | 0.076498 | 0.12971 | 0.0037683 | -0.0092137 | 0.0074766 | -0.01233 | 0.074304 | 0.058467 | 0.016598 | -0.011119 | 73.6038 | 73.8419 | 6.3721 | -48.0927 | 73.9288 | -49.1867 | -49.2737 | -41.5421 | 41.9312 | -48.8297 | 73.8739 | 73.7595 | -49.3103 | -49.3652 | -0.10529 | -0.19226 | 0.16022 | 122.9233 | 0.98877 | 1.181 | -0.16479 | -0.22888 | -0.28381 | 0.10529 | 7.5394 | 0.25177 | 0.53558 | -0.009156 | 123.0103 | 122.6852 | 55.4535 | -123.0423 | 122.9553 | 122.8409 | 91.0126 | -123.1338
4010.0156 | 123.111 | -49.1318 | 73.7595 | 0.0914 | 0.014071 | 0.084272 | 0.07479 | 0.12864 | 0.0063317 | -0.0081455 | 0.25162 | -0.010835 | 0.068964 | 0.059748 | 0.01788 | -0.012614 | 73.5672 | 73.7778 | 6.2302 | -48.1201 | 73.8831 | -49.1959 | -49.3011 | -41.597 | 41.8213 | -48.9029 | 73.8693 | 73.7228 | -49.3469 | -49.3835 | -0.064087 | -0.16937 | 0.1236 | 122.9095 | 1.0117 | 1.181 | -0.19226 | -0.21515 | -0.25177 | 0.10986 | 7.5348 | 0.22888 | 0.48065 | -0.036621 | 123.0148 | 122.699 | 55.3619 | -123.0606 | 123.0011 | 122.8546 | 90.9531 | -123.143
4011.0312 | 123.0835 | -49.4385 | 73.4619 | -0.045929 | 0.021121 | 0.073591 | 0.078207 | 0.12993 | 0.013595 | -0.0098545 | -0.03067 | -0.0086988 | 0.07345 | 0.059107 | 0.022366 | -0.01411 | 73.3017 | 73.4253 | 6.1569 | -48.4268 | 73.5718 | -49.5438 | -49.6582 | -41.8167 | 41.6245 | -49.3149 | 73.6084 | 73.494 | -49.6628 | -49.6994 | -0.10529 | -0.21973 | 0.10986 | 122.8638 | 1.0117 | 1.2314 | -0.16022 | -0.2243 | -0.26093 | 0.14648 | 7.6218 | 0.1236 | 0.38452 | 0.032044 | 123.0103 | 122.7402 | 55.5954 | -123.1201 | 123.0469 | 122.9324 | 91.0629 | -123.1613
4012.0156 | 123.0972 | -50.5783 | 72.3084 | 0.10666 | 0.010013 | 0.082136 | 0.073508 | 0.128 | 0.0027001 | -0.0083591 | 0.083771 | -0.012117 | 0.070886 | 0.060816 | 0.01553 | -0.012614 | 72.1161 | 72.3312 | 5.9647 | -49.4934 | 72.4274 | -50.6424 | -50.7339 | -42.952 | 40.4846 | -50.354 | 72.4091 | 72.3221 | -50.7797 | -50.8209 | -0.064087 | -0.15564 | 0.11902 | 122.9095 | 1.0849 | 1.2405 | -0.19226 | -0.20142 | -0.24262 | 0.10071 | 7.6263 | 0.2243 | 0.46692 | 0.013733 | 123.0057 | 122.6944 | 56.543 | -123.0423 | 122.9874 | 122.9004 | 91.0629 | -123.1293
4013.0156 | 123.1567 | -50.0107 | 72.821 | -0.11459 | 0.0091581 | 0.085127 | 0.073721 | 0.12544 | 0.0024865 | -0.011777 | 0.0074766 | -0.011476 | 0.066614 | 0.059535 | 0.016385 | -0.010905 | 72.702 | 72.9309 | 6.0837 | -48.9029 | 73.0041 | -50.0977 | -50.1938 | -42.3614 | 41.1118 | -49.7589 | 72.9355 | 72.8622 | -50.2533 | -50.2945 | -0.086975 | -0.18311 | 0.1831 | 122.9416 | 1.1078 | 1.2909 | -0.11902 | -0.24262 | -0.28381 | 0.11444 | 7.6492 | 0.25177 | 0.53558 | 0.041199 | 123.0148 | 122.7127 | 56.0944 | -123.0148 | 122.9462 | 122.8729 | 91.1224 | -123.1155
4014.0156 | 123.1155 | -50.2396 | 72.6425 | 0.16769 | 0.012149 | 0.08299 | 0.073508 | 0.12928 | 0.0059045 | -0.0094273 | 0.0914 | -0.011476 | 0.06875 | 0.060603 | 0.017667 | -0.01176 | 72.4503 | 72.6471 | 6.0196 | -49.1547 | 72.7753 | -50.322 | -50.4089 | -42.6041 | 40.8096 | -49.9969 | 72.7432 | 72.6288 | -50.4639 | -50.4822 | -0.082397 | -0.16937 | 0.13275 | 122.8867 | 1.0849 | 1.2543 | -0.19226 | -0.2243 | -0.24262 | 0.10071 | 7.6355 | 0.24261 | 0.48523 | -0.013733 | 123.0148 | 122.6898 | 56.2592 | -123.0515 | 122.9828 | 122.8683 | 91.0492 | -123.1247
4015.0156 | 123.1476 | -50.1114 | 72.7386 | -0.10696 | 0.0083035 | 0.083845 | 0.072226 | 0.13142 | 0.0050499 | -0.01135 | -0.03067 | -0.010194 | 0.071955 | 0.059535 | 0.016598 | -0.011546 | 72.5876 | 72.8165 | 6.0837 | -49.0082 | 72.8943 | -50.1846 | -50.2991 | -42.4118 | 40.9653 | -49.8184 | 72.8348 | 72.7386 | -50.322 | -50.3723 | -0.073242 | -0.18768 | 0.15564 | 122.9279 | 1.1032 | 1.2909 | -0.15106 | -0.21057 | -0.26093 | 0.096131 | 7.6996 | 0.29297 | 0.55389 | 0 | 123.0057 | 122.699 | 56.1951 | -123.0377 | 122.9462 | 122.85 | 91.0767 | -123.111
4016.0156 | 123.1064 | -50.4318 | 72.4091 | 0.15244 | 0.016208 | 0.08534 | 0.073081 | 0.12886 | 0.011672 | -0.0053683 | 0.25925 | -0.010408 | 0.071314 | 0.057826 | 0.020016 | -0.014964 | 72.3495 | 72.5143 | 6.0837 | -49.2737 | 72.5739 | -50.4959 | -50.6058 | -42.8604 | 40.7272 | -50.0793 | 72.4915 | 72.4136 | -50.6699 | -50.6882 | -0.064087 | -0.17395 | 0.16479 | 122.9462 | 1.1581 | 1.3321 | -0.05951 | -0.23804 | -0.25635 | 0.082397 | 7.5714 | 0.35248 | 0.60882 | 0.004577 | 123.0057 | 122.7814 | 56.5155 | -123.0148 | 122.9233 | 122.8455 | 91.1591 | -123.0972
4017.0156 | 123.1018 | -50.8347 | 72.0337 | 0.16006 | 0.012149 | 0.087476 | 0.073508 | 0.12843 | 0.0067589 | -0.0072911 | 0.21347 | -0.011476 | 0.070673 | 0.063166 | 0.018307 | -0.0098374 | 71.9009 | 72.1024 | 5.5573 | -49.6765 | 72.1848 | -50.853 | -50.9857 | -43.1488 | 40.2328 | -50.6012 | 72.1115 | 72.0291 | -51.0818 | -51.1185 | -0.01831 | -0.15106 | 0.15106 | 122.937 | 1.1581 | 1.3092 | -0.13275 | -0.24719 | -0.28381 | 0.07782 | 7.6859 | 0.23346 | 0.51727 | -0.004577 | 123.0194 | 122.7356 | 56.3919 | -123.0194 | 122.9462 | 122.8638 | 91.0675 | -123.1522
4018.0156 | 123.1201 | -51.3428 | 71.4615 | 0.18295 | 0.015994 | 0.085127 | 0.07479 | 0.12993 | 0.010604 | -0.0075047 | 0.2211 | -0.0097668 | 0.069177 | 0.056544 | 0.018521 | -0.010051 | 71.3837 | 71.5576 | 5.9006 | -50.1617 | 71.6446 | -51.4526 | -51.5442 | -43.6203 | 39.7476 | -51.0635 | 71.5988 | 71.4706 | -51.5945 | -51.6357 | -0.10986 | -0.20142 | 0.1831 | 122.9004 | 1.181 | 1.3824 | -0.07782 | -0.25177 | -0.29297 | 0.13733 | 7.7225 | 0.27923 | 0.5722 | 0.009155 | 122.9874 | 122.7264 | 57.2433 | -123.0057 | 122.9416 | 122.8134 | 91.0904 | -123.0972
4019.0156 | 123.0881 | -51.5121 | 71.3242 | 0.16769 | 0.011508 | 0.087263 | 0.073508 | 0.13057 | 0.0071863 | -0.0081455 | 0.22873 | -0.0095532 | 0.070246 | 0.059962 | 0.021512 | -0.010478 | 71.2006 | 71.3928 | 5.8868 | -50.3494 | 71.4752 | -51.6129 | -51.7319 | -43.7759 | 39.592 | -51.2466 | 71.4523 | 71.3516 | -51.7364 | -51.7639 | -0.10071 | -0.21973 | 0.15106 | 122.905 | 1.1627 | 1.3824 | -0.1236 | -0.2243 | -0.25177 | 0.12817 | 7.7362 | 0.2655 | 0.51727 | 0.027466 | 122.9874 | 122.7127 | 57.399 | -123.056 | 122.9645 | 122.8638 | 91.1041 | -123.0881
4020.0156 | 123.1567 | -51.8692 | 70.9808 | 0.19821 | 0.015353 | 0.087049 | 0.071372 | 0.12993 | 0.0091089 | -0.0075047 | 0.81619 | -0.0099806 | 0.069818 | 0.05868 | 0.020016 | -0.012187 | 70.8984 | 71.0724 | 5.8044 | -50.7477 | 71.1044 | -51.9882 | -52.0889 | -44.0598 | 39.3036 | -51.5717 | 71.0678 | 70.9854 | -52.0935 | -52.1164 | -0.11902 | -0.21973 | 0.1236 | 122.9416 | 1.1215 | 1.3412 | -0.082398 | -0.2243 | -0.24719 | 0.086975 | 7.8094 | 0.29755 | 0.54474 | 0.004578 | 122.9736 | 122.7676 | 57.6736 | -123.0698 | 122.937 | 122.8546 | 91.1728 | -123.0972
4021.0156 | 123.0835 | -52.272 | 70.61 | 0.17532 | 0.014285 | 0.089399 | 0.075644 | 0.128 | 0.0069727 | -0.0075047 | 0.22873 | -0.011903 | 0.068109 | 0.05868 | 0.019162 | -0.010265 | 70.4773 | 70.6741 | 5.6534 | -50.9674 | 70.7611 | -52.3041 | -52.4139 | -44.4626 | 38.9236 | -51.9287 | 70.7245 | 70.6421 | -52.4734 | -52.5009 | -0.032043 | -0.14191 | 0.15106 | 122.9462 | 1.3046 | 1.4465 | -0.13275 | -0.20142 | -0.22888 | 0.11444 | 7.8094 | 0.34332 | 0.5722 | 0.032044 | 123.0331 | 122.7493 | 57.9254 | -123.024 | 122.9965 | 122.9141 | 91.1957 | -123.111
4022.0156 | 123.1522 | -52.1164 | 70.7474 | 0.19821 | 0.017703 | 0.088331 | 0.07244 | 0.12886 | 0.011459 | -0.0072911 | 0.037995 | -0.0084852 | 0.069391 | 0.059962 | 0.023648 | -0.011546 | 70.6146 | 70.752 | 5.6259 | -50.8621 | 70.8893 | -52.1988 | -52.3361 | -44.2841 | 39.093 | -51.8051 | 70.8206 | 70.7336 | -52.3315 | -52.359 | -0.082398 | -0.21973 | 0.14191 | 122.8683 | 1.2543 | 1.474 | -0.13275 | -0.21515 | -0.24262 | 0.073243 | 7.8323 | 0.31128 | 0.55389 | -0.013732 | 123.0057 | 122.731 | 57.7423 | -123.0835 | 122.937 | 122.85 | 91.2094 | -123.1064
4023.0156 | 123.111 | -52.2812 | 70.5688 | 0.25162 | 0.014499 | 0.087049 | 0.074149 | 0.12993 | 0.0093225 | -0.0055821 | 0.19821 | -0.0097668 | 0.069391 | 0.059321 | 0.022794 | -0.011546 | 70.459 | 70.61 | 5.6305 | -50.9766 | 70.7062 | -52.3773 | -52.5009 | -44.4672 | 38.9374 | -51.9745 | 70.6421 | 70.5551 | -52.533 | -52.5833 | -0.09613 | -0.21973 | 0.13733 | 122.8912 | 1.3046 | 1.5244 | -0.10986 | -0.25177 | -0.30212 | 0.073242 | 7.814 | 0.3067 | 0.60883 | -0.013733 | 122.9874 | 122.7402 | 57.9117 | -123.0698 | 122.9233 | 122.8363 | 91.2186 | -123.1522
4024.0156 | 123.0469 | -52.5101 | 70.3995 | 0.17532 | 0.020694 | 0.089399 | 0.076926 | 0.12864 | 0.011886 | -0.0066501 | 0.13718 | -0.009126 | 0.072809 | 0.059535 | 0.023221 | -0.01176 | 70.2255 | 70.3125 | 5.5389 | -51.2283 | 70.5643 | -52.5513 | -52.6932 | -44.6823 | 38.6993 | -52.2079 | 70.5093 | 70.4361 | -52.7252 | -52.7481 | -0.041199 | -0.1831 | 0.16479 | 122.8226 | 1.2817 | 1.4648 | -0.17395 | -0.21515 | -0.23804 | 0.10986 | 7.8278 | 0.30212 | 0.54016 | 0.036621 | 123.0743 | 122.7356 | 58.049 | -123.0927 | 123.0194 | 122.9462 | 91.2094 | -123.1476
4025.0156 | 123.143 | -52.5009 | 70.3308 | 0.0914 | 0.016635 | 0.089399 | 0.072226 | 0.13035 | 0.0086815 | -0.0057957 | 0.2211 | -0.009126 | 0.073664 | 0.062739 | 0.025571 | -0.011119 | 70.2621 | 70.4132 | 5.6351 | -51.1505 | 70.491 | -52.5696 | -52.6657 | -44.7235 | 38.9786 | -52.1851 | 70.4224 | 70.3262 | -52.7344 | -52.7664 | -0.068664 | -0.16479 | 0.16022 | 122.9141 | 1.3504 | 1.5152 | -0.068665 | -0.23346 | -0.2655 | 0.091552 | 7.7774 | 0.31586 | 0.58136 | -0.004578 | 122.9919 | 122.7631 | 58.136 | -122.9965 | 122.9233 | 122.8271 | 91.4795 | -123.0972
4026.0156 | 123.0331 | -52.4139 | 70.5276 | 0.099029 | 0.021121 | 0.088972 | 0.077353 | 0.13014 | 0.013168 | -0.0049411 | -0.4274 | -0.008058 | 0.071527 | 0.059107 | 0.021725 | -0.012187 | 70.5139 | 70.0745 | 5.5389 | -50.9171 | 70.697 | -52.4368 | -52.5513 | -44.5953 | 38.7589 | -52.153 | 70.6238 | 70.5414 | -52.6108 | -52.6566 | -0.022889 | -0.13733 | 0.16937 | 122.4884 | 1.4969 | 1.6342 | -0.013733 | -0.19684 | -0.24262 | 0.09613 | 7.8186 | 0.26092 | 0.50354 | 0.013733 | 123.111 | 122.9279 | 57.9529 | -123.0789 | 123.0377 | 122.9553 | 91.1728 | -123.1842
4027.0156 | 123.1338 | -52.5558 | 70.3033 | 0.35843 | 0.016208 | 0.088545 | 0.07244 | 0.13099 | 0.0088953 | -0.0053683 | 0.21347 | -0.0082716 | 0.071527 | 0.060389 | 0.020657 | -0.0098374 | 70.2026 | 70.3674 | 5.6946 | -51.1597 | 70.4773 | -52.6154 | -52.7161 | -44.5679 | 38.5529 | -52.2125 | 70.3949 | 70.2942 | -52.7802 | -52.7939 | -0.059509 | -0.16022 | 0.17395 | 122.9233 | 1.3962 | 1.5564 | -0.10071 | -0.2243 | -0.23804 | 0.091552 | 7.988 | 0.34332 | 0.58136 | -0.009156 | 123.0331 | 122.7585 | 58.2504 | -123.0194 | 122.9507 | 122.85 | 91.1087 | -123.0972
4028.0156 | 123.0148 | -52.6245 | 70.3217 | 0.16006 | 0.018771 | 0.086622 | 0.077567 | 0.12993 | 0.0121 | -0.0045139 | 0.41183 | -0.0082716 | 0.070673 | 0.058039 | 0.022366 | -0.011333 | 69.8639 | 70.253 | 5.7678 | -51.1597 | 70.5414 | -52.6337 | -52.771 | -44.751 | 38.6078 | -52.3453 | 70.4453 | 70.3491 | -52.8442 | -52.8488 | -0.009155 | -0.14648 | 0.21973 | 122.8775 | 1.4648 | 1.6113 | -0.45776 | -0.21973 | -0.2243 | 0.1236 | 7.8735 | 0.27924 | 0.50354 | 0.027466 | 123.1659 | 122.4884 | 58.3923 | -123.0927 | 123.0698 | 122.9736 | 91.2323 | -123.1705
4029.0156 | 123.111 | -52.9129 | 69.9829 | 0.17532 | 0.018558 | 0.090894 | 0.072653 | 0.12779 | 0.011032 | -0.0066501 | 0.21347 | -0.0093396 | 0.072595 | 0.060389 | 0.02258 | -0.010692 | 69.7815 | 69.9051 | 5.4337 | -51.5167 | 70.1019 | -53.009 | -53.1052 | -45.0211 | 38.3102 | -52.565 | 70.0653 | 69.9875 | -53.1509 | -53.1601 | -0.09613 | -0.19226 | 0.11902 | 122.818 | 1.3962 | 1.5884 | -0.20142 | -0.23804 | -0.24719 | 0.082398 | 7.8918 | 0.3479 | 0.59509 | 0.004578 | 123.0148 | 122.6944 | 58.3466 | -123.0881 | 122.9782 | 122.9004 | 91.2231 | -123.143
4030.0156 | 123.0515 | -53.5629 | 69.3695 | -0.076447 | 0.022189 | 0.091535 | 0.078207 | 0.12843 | 0.012313 | -0.0070773 | -0.0077819 | -0.0089124 | 0.071314 | 0.058894 | 0.024289 | -0.011119 | 69.2139 | 69.3237 | 5.2597 | -52.0706 | 69.5068 | -53.6453 | -53.7277 | -45.6299 | 37.7289 | -53.2471 | 69.4656 | 69.3787 | -53.7918 | -53.7964 | -0.082398 | -0.16479 | 0.13733 | 122.8867 | 1.4923 | 1.6571 | -0.15564 | -0.22888 | -0.23346 | 0.09613 | 7.933 | 0.31586 | 0.54932 | 0.009155 | 123.0698 | 122.7768 | 58.8226 | -123.0972 | 123.0286 | 122.9416 | 91.2918 | -123.1659
4031.0156 | 123.0286 | -54.538 | 68.399 | 0.25925 | 0.019412 | 0.091108 | 0.073935 | 0.12928 | 0.013381 | -0.0060093 | 0.10666 | -0.0082716 | 0.070246 | 0.058039 | 0.022153 | -0.0098374 | 68.1381 | 68.2571 | 4.9667 | -53.0228 | 68.4998 | -54.6387 | -54.7394 | -46.5775 | 36.7538 | -54.1855 | 68.4769 | 68.4311 | -54.7531 | -54.8035 | -0.10071 | -0.20142 | 0.10071 | 122.7951 | 1.5152 | 1.7166 | -0.26093 | -0.21515 | -0.2655 | 0.07782 | 7.9605 | 0.35248 | 0.61798 | 0.032043 | 123.0377 | 122.6761 | 59.5047 | -123.1384 | 123.0148 | 122.9691 | 91.2918 | -123.2025
4032.0156 | 123.0515 | -55.1056 | 67.8314 | -0.061188 | 0.02283 | 0.094526 | 0.074149 | 0.13099 | 0.014236 | -0.0072911 | 0.030365 | -0.0099806 | 0.073236 | 0.059321 | 0.024716 | -0.0068466 | 67.6529 | 67.8085 | 4.9622 | -53.4851 | 67.9504 | -55.1422 | -55.2612 | -47.1039 | 36.2961 | -54.776 | 67.923 | 67.8131 | -55.3345 | -55.3574 | -0.036621 | -0.15564 | 0.11902 | 122.9141 | 1.6205 | 1.7761 | -0.17853 | -0.22888 | -0.25177 | 0.091553 | 8.0017 | 0.32959 | 0.58136 | -0.018311 | 123.056 | 122.7585 | 60.0677 | -123.0927 | 123.0286 | 122.9187 | 91.4017 | -123.1888
4033.0156 | 122.937 | -56.2729 | 66.6412 | 0.030365 | 0.018771 | 0.094099 | 0.075217 | 0.13078 | 0.010818 | -0.0053683 | 0.15244 | -0.0095532 | 0.07345 | 0.060176 | 0.023862 | -0.0098374 | 66.3757 | 66.5222 | 4.7562 | -54.6112 | 66.7923 | -56.3599 | -56.4743 | -48.3078 | 35.1196 | -55.9753 | 66.7374 | 66.6367 | -56.5338 | -56.5384 | -0.086975 | -0.20142 | 0.15106 | 122.7951 | 1.6617 | 1.8631 | -0.2655 | -0.26093 | -0.2655 | 0.096131 | 7.9651 | 0.29755 | 0.56305 | -0.004577 | 123.0652 | 122.6486 | 61.0291 | -123.1155 | 123.0103 | 122.9095 | 91.3925 | -123.1796
4034.0156 | 123.0423 | -56.6437 | 66.275 | -0.045929 | 0.018985 | 0.096021 | 0.07543 | 0.13014 | 0.012527 | -0.0072911 | 0.068512 | -0.0099806 | 0.073877 | 0.060603 | 0.021939 | -0.010051 | 66.0828 | 66.2109 | 4.747 | -54.9133 | 66.4032 | -56.7169 | -56.8222 | -48.6099 | 34.8358 | -56.3095 | 66.3712 | 66.2842 | -56.8726 | -56.9183 | -0.073242 | -0.17853 | 0.12817 | 122.8546 | 1.7303 | 1.9089 | -0.19226 | -0.22888 | -0.27466 | 0.096131 | 8.0338 | 0.33417 | 0.60883 | 0.009156 | 123.0469 | 122.7264 | 61.3907 | -123.0972 | 123.0148 | 122.9279 | 91.4795 | -123.1934
4035.0156 | 123.0743 | -57.5912 | 65.3687 | 0.11429 | 0.021335 | 0.098585 | 0.075858 | 0.12864 | 0.012954 | -0.0070773 | 0.18295 | -0.0084852 | 0.074732 | 0.061671 | 0.024075 | -0.0057786 | 65.094 | 65.1947 | 4.5776 | -55.7831 | 65.4877 | -57.6553 | -57.7698 | -49.4614 | 33.6731 | -56.9778 | 65.4694 | 65.3824 | -57.8201 | -57.8293 | -0.064086 | -0.17853 | 0.11902 | 122.786 | 1.8082 | 1.9867 | -0.27466 | -0.22888 | -0.23804 | 0.10071 | 8.1299 | 0.6134 | 0.85144 | 0.013733 | 123.0789 | 122.6852 | 62.1689 | -123.1384 | 123.0606 | 122.9736 | 91.2643 | -123.1979
4036.0156 | 123.0698 | -58.2825 | 64.65 | -0.22141 | 0.018344 | 0.098585 | 0.074149 | 0.12928 | 0.014022 | -0.0075047 | -0.12985 | -0.0089124 | 0.072809 | 0.060816 | 0.024716 | -0.010478 | 64.4531 | 64.6088 | 4.4998 | -56.3232 | 64.801 | -58.3374 | -58.4564 | -50.116 | 33.3847 | -57.8567 | 64.7324 | 64.6591 | -58.5022 | -58.5297 | -0.054931 | -0.17395 | 0.15106 | 122.8912 | 1.9592 | 2.1332 | -0.19684 | -0.21973 | -0.24719 | 0.082398 | 8.1665 | 0.42572 | 0.67291 | 0.009156 | 123.0835 | 122.7356 | 62.7823 | -123.1064 | 123.0148 | 122.9416 | 91.6672 | -123.1796
4037.0156 | 123.0377 | -59.5596 | 63.3728 | 0.015106 | 0.020907 | 0.10115 | 0.075858 | 0.13035 | 0.014236 | -0.0072911 | 0.076141 | -0.007417 | 0.075159 | 0.057185 | 0.02728 | -0.01176 | 63.1805 | 63.2996 | 4.1656 | -57.4905 | 63.5284 | -59.6054 | -59.7427 | -51.3657 | 32.1442 | -59.0836 | 63.4689 | 63.4048 | -59.7702 | -59.8251 | -0.045777 | -0.18311 | 0.15564 | 122.8592 | 2.0691 | 2.2522 | -0.19226 | -0.21057 | -0.2655 | 0.09613 | 8.194 | 0.47607 | 0.74158 | 0.032043 | 123.0881 | 122.7402 | 63.7253 | -123.1155 | 123.0286 | 122.9645 | 91.7038 | -123.1979
4038.0156 | 123.0606 | -60.8871 | 62.0178 | -0.18326 | 0.015353 | 0.10542 | 0.075003 | 0.13078 | 0.014663 | -0.0077183 | -0.099335 | -0.0086988 | 0.074304 | 0.061457 | 0.026425 | -0.0094102 | 61.8668 | 61.9949 | 3.8681 | -58.6716 | 62.146 | -60.9787 | -61.0748 | -52.6154 | 30.9906 | -60.3241 | 62.1414 | 62.059 | -61.116 | -61.1206 | -0.091553 | -0.18768 | 0.12817 | 122.8821 | 2.2156 | 2.4033 | -0.15106 | -0.22888 | -0.23346 | 0.1236 | 8.2718 | 0.56305 | 0.79651 | 0.041199 | 123.0331 | 122.7539 | 64.7552 | -123.0927 | 123.0286 | 122.9462 | 91.8777 | -123.1384
4039.0156 | 122.9874 | -61.94 | 60.9787 | 0.022736 | 0.020907 | 0.1082 | 0.07244 | 0.13121 | 0.017867 | -0.0049411 | 0.068512 | -0.0078442 | 0.074304 | 0.062098 | 0.028989 | -0.011333 | 60.7132 | 60.8597 | 3.6118 | -59.6603 | 61.0886 | -62.0499 | -62.1002 | -53.6957 | 29.8645 | -61.3998 | 61.1069 | 61.0382 | -62.178 | -62.2055 | -0.10986 | -0.16022 | 0.10986 | 122.7997 | 2.2797 | 2.4399 | -0.2655 | -0.23804 | -0.2655 | 0.12817 | 8.2443 | 0.54016 | 0.80566 | 0.059509 | 123.0286 | 122.6532 | 65.5518 | -123.0789 | 123.0469 | 122.9782 | 91.8045 | -123.1842
4040.0156 | 123.0743 | -64.3112 | 58.6075 | -0.21378 | 0.017703 | 0.11525 | 0.070303 | 0.13035 | 0.016586 | -0.0064365 | -0.12222 | -0.007417 | 0.071741 | 0.059321 | 0.029416 | -0.010905 | 58.4427 | 58.5663 | 3.1723 | -61.6608 | 58.754 | -64.4028 | -64.4852 | -55.9479 | 27.7771 | -63.5605 | 58.7173 | 58.6716 | -64.5264 | -64.5538 | -0.091553 | -0.17395 | 0.14648 | 122.8775 | 2.6505 | 2.8244 | -0.1648 | -0.21515 | -0.24262 | 0.10986 | 8.3633 | 0.75073 | 0.99335 | 0.064087 | 123.0652 | 122.7539 | 67.4835 | -123.0927 | 123.0286 | 122.9828 | 92.0883 | -123.1613
4041.0156 | 123.0377 | -30.2536 | 92.775 | 0.015106 | 0.021335 | 0.071027 | 0.079489 | 0.12843 | 0.0080407 | -0.0079319 | 0.19821 | -0.0069898 | 0.073664 | 0.059107 | 0.017453 | -0.010265 | 92.6651 | 92.807 | 9.6268 | -29.3152 | 93.0725 | -30.0797 | -30.2032 | -22.7875 | 59.3124 | -30.0934 | 92.7658 | 92.72 | -30.4733 | -30.4825 | 0.17395 | 0.050354 | 0.29755 | 123.0606 | 0.93841 | 0.88806 | -0.10986 | -0.21973 | -0.22888 | -0.009155 | 7.4661 | 0.16022 | 0.3891 | -0.054931 | 123.3261 | 122.9187 | 39.8804 | -122.9782 | 123.0194 | 122.9736 | 89.566 | -123.2574
4042.0156 | 123.0698 | -60.8597 | 61.9858 | -0.19852 | 0.018344 | 0.10457 | 0.074576 | 0.13014 | 0.01509 | -0.0081455 | -0.11459 | -0.009126 | 0.073664 | 0.057612 | 0.025998 | -0.0087692 | 61.8118 | 61.9675 | 3.8544 | -58.6807 | 62.1231 | -61.0153 | -61.0931 | -52.5101 | 30.8945 | -60.3333 | 62.1094 | 62.0407 | -61.1526 | -61.171 | -0.15564 | -0.23346 | 0.13733 | 122.8271 | 2.179 | 2.4124 | -0.17395 | -0.29297 | -0.31128 | 0.1236 | 8.3496 | 0.52643 | 0.83771 | 0.054931 | 122.9828 | 122.6715 | 64.7141 | -123.0789 | 122.9691 | 122.9004 | 91.7541 | -123.1567
4043.0156 | 123.0377 | -66.2888 | 56.5842 | -0.0383 | 0.020907 | 0.11461 | 0.075003 | 0.13292 | 0.018722 | -0.0081455 | 0.045624 | -0.0089124 | 0.073236 | 0.060603 | 0.032193 | -0.0096238 | 56.3736 | 56.5521 | 2.7557 | -63.6658 | 56.6711 | -66.4032 | -66.4948 | -57.8384 | 25.8087 | -65.6296 | 56.6711 | 56.6162 | -66.5909 | -66.5726 | -0.11444 | -0.20599 | 0.086976 | 122.8409 | 2.623 | 2.829 | -0.21057 | -0.30212 | -0.28381 | 0.086976 | 8.4503 | 0.65918 | 0.94299 | 0.032044 | 122.9599 | 122.6624 | 69.0445 | -123.0789 | 122.9599 | 122.905 | 92.0975 | -123.1567
4044.0156 | 123.0194 | -66.806 | 56.0761 | -0.068817 | 0.016421 | 0.12315 | 0.073935 | 0.13527 | 0.018081 | -0.0089999 | -0.15274 | -0.0093396 | 0.0711 | 0.058894 | 0.033261 | -0.0091966 | 55.9067 | 56.0761 | 2.7008 | -63.8077 | 56.25 | -66.8655 | -66.9708 | -58.3237 | 25.3372 | -65.9088 | 56.1996 | 56.1401 | -67.0349 | -67.0486 | -0.05951 | -0.16479 | 0.17395 | 122.8821 | 2.9984 | 3.1631 | -0.16937 | -0.22888 | -0.24261 | 0.1236 | 8.4824 | 0.89722 | 1.1398 | 0.064087 | 123.056 | 122.7127 | 69.5068 | -123.0469 | 123.0057 | 122.9462 | 92.1432 | -123.1247
4045.0156 | 123.0515 | -75.3571 | 47.5708 | 0.2211 | 0.019626 | 0.13618 | 0.073721 | 0.13228 | 0.017867 | -0.0083591 | -0.053558 | -0.0095532 | 0.072595 | 0.061885 | 0.051633 | -0.0085556 | 47.7493 | 47.85 | 0.89722 | -81.3034 | 47.9736 | -75.1419 | -75.2472 | -66.6183 | 17.3904 | -73.4756 | 47.6212 | 47.5525 | -75.6317 | -75.6454 | 0.21515 | 0.10986 | 0.40283 | 123.2071 | -5.9463 | -6.0562 | 0.17853 | -0.27466 | -0.28839 | 0.050354 | 8.7387 | 1.8814 | 2.1698 | -0.018311 | 123.3307 | 123.1064 | 76.2543 | -122.818 | 122.9782 | 122.9095 | 92.7475 | -123.2162
4046.0156 | 103.3127 | -22.3709 | 100.6989 | -0.21378 | 0.018771 | 0.072736 | 0.075644 | 0.13099 | 0.0054773 | -0.010495 | 0.015106 | -0.0097668 | 0.073877 | 0.058467 | 0.016171 | -0.011974 | 100.3235 | 100.4974 | 12.0575 | -21.6705 | 100.8408 | -22.348 | -22.467 | -14.5935 | 66.5543 | -22.1603 | 100.8087 | 100.7584 | -22.522 | -22.5174 | 0.022889 | -0.09613 | 0.14191 | 122.8683 | 0.70038 | 0.79651 | -0.37537 | -0.15106 | -0.14648 | 0.10986 | 7.7774 | 0.21057 | 0.35706 | 0.059509 | 123.2117 | 122.6944 | 34.4284 | -123.1659 | 123.1796 | 123.1293 | 88.9252 | -123.2162
4047.0156 | 123.0331 | -88.4308 | 34.4421 | -0.015411 | 0.023044 | 0.18788 | 0.075003 | 0.13334 | 0.034316 | -0.0083591 | -0.061188 | -0.010835 | 0.074732 | 0.059962 | 0.078763 | -0.0096238 | 34.2911 | 34.4101 | -1.8219 | -83.3633 | 34.5474 | -88.6047 | -88.6322 | -79.3945 | 5.0812 | -85.7895 | 34.5108 | 34.4238 | -88.7787 | -88.7787 | -0.17395 | -0.20142 | 0.10529 | 122.8409 | 5.0674 | 5.2689 | -0.15106 | -0.3479 | -0.3479 | 0.068664 | 9.0363 | 2.6413 | 2.9892 | -0.018311 | 122.9782 | 122.7219 | 86.6089 | -123.0743 | 122.9416 | 122.8546 | 93.512 | -123.2208
4048.0156 | 123.0789 | -62.6724 | 60.3149 | -0.17563 | 0.016849 | 0.17442 | 0.073081 | 0.13142 | 0.027481 | -0.0070773 | -0.10696 | -0.0095532 | 0.072595 | 0.062098 | 0.085171 | -0.008342 | 60.2188 | 60.4156 | 3.5934 | -58.5205 | 60.5255 | -62.5626 | -62.6816 | -54.0115 | 29.5029 | -59.9533 | 60.5301 | 60.466 | -62.7686 | -62.8922 | 0.10986 | -0.009156 | 0.21057 | 123.0881 | 4.1519 | 4.1611 | -0.09613 | -0.096131 | -0.21973 | 0.21515 | 8.6609 | 2.7191 | 2.9388 | 0.15106 | 123.1979 | 122.8912 | 66.2659 | -122.9965 | 123.2025 | 123.1384 | 92.1753 | -123.2071
4049.0156 | 123.0423 | -59.6008 | 63.3591 | -0.053558 | 0.023044 | 0.17271 | 0.077353 | 0.13099 | 0.027481 | -0.0075047 | 0.030365 | -0.008058 | 0.0758 | 0.062312 | 0.079831 | -0.0072738 | 62.7274 | 62.6724 | 4.2526 | -55.4169 | 63.1073 | -59.9121 | -59.9487 | -50.7065 | 32.2403 | -57.3669 | 63.6292 | 63.4689 | -59.7885 | -59.8801 | -0.31128 | -0.3479 | -0.25177 | 122.2733 | 4.184 | 4.5319 | -0.63171 | -0.18768 | -0.27924 | 0.27008 | 8.8943 | 2.2339 | 2.5131 | 0.10986 | 122.7081 | 122.3282 | 63.8535 | -123.3078 | 123.23 | 123.0698 | 91.8411 | -123.2391
4050.0156 | 123.0286 | -87.5336 | 35.4446 | -0.29007 | 0.016208 | 0.36818 | 0.073294 | 0.13078 | 0.034957 | -0.0066501 | -0.15274 | -0.0095532 | 0.071955 | 0.060816 | 0.25265 | -0.0091966 | 34.7855 | 34.8312 | -1.5518 | -81.6605 | 35.1654 | -87.9913 | -88.0554 | -78.3966 | 5.9097 | -79.8386 | 35.289 | 35.2615 | -87.8769 | -87.8128 | -0.45776 | -0.52185 | -0.27924 | 122.3648 | 5.8731 | 6.395 | -0.65918 | -0.34332 | -0.27924 | -0.15564 | 9.137 | 7.695 | 7.9742 | -0.1831 | 122.699 | 122.319 | 85.9818 | -123.5001 | 122.8226 | 122.7951 | 93.4433 | -123.2574
4051.0156 | 122.9965 | -103.7384 | 19.1757 | -0.13748 | 0.017703 | 0.23829 | 0.072867 | 0.13441 | 0.0044091 | -0.0081455 | -0.11459 | -0.007417 | 0.072809 | 0.062525 | 0.14755 | -0.0089828 | 18.9011 | 19.0155 | -4.4678 | -112.1155 | 19.1574 | -103.981 | -104.0359 | -93.9789 | -8.9081 | -97.9706 | 19.2398 | 19.1803 | -104.1092 | -104.1 | -0.24262 | -0.29755 | -0.01831 | 122.7539 | -8.3771 | -8.0795 | -0.27466 | -0.37079 | -0.36163 | 0.064087 | 9.7595 | 5.7678 | 6.1295 | 0.004578 | 122.8958 | 122.6395 | 99.2706 | -123.2117 | 122.9782 | 122.9187 | 94.8303 | -123.2758
4052.0156 | 123.0698 | -70.0195 | 52.9404 | -0.19852 | 0.017489 | 0.29747 | 0.075003 | 0.1327 | -0.0011451 | -0.0070773 | -0.10696 | -0.0095532 | 0.071955 | 0.061671 | 0.22531 | -0.0098374 | 52.121 | 52.3315 | 2.0187 | -85.2768 | 52.5558 | -70.4819 | -70.5322 | -60.9009 | 22.5082 | -62.4207 | 52.9999 | 52.9678 | -70.1706 | -70.1889 | -0.46234 | -0.5127 | -0.38452 | 122.3511 | -15.2573 | -14.7446 | -0.8194 | -0.15106 | -0.16937 | 0.059509 | 9.1187 | 7.5989 | 7.7682 | 0.027465 | 122.5754 | 122.1405 | 72.0383 | -123.4726 | 123.0194 | 122.9874 | 92.5278 | -123.1293
4053.0156 | 123.0469 | -11.348 | 111.6623 | -0.061188 | 0.020053 | 0.0706 | 0.080344 | 0.12864 | 0.0067589 | -0.0096409 | 0.25162 | -0.0084852 | 0.074304 | 0.059748 | 0.024289 | -0.012828 | 111.4929 | 111.6165 | 13.3347 | -10.7574 | 111.9736 | -11.3022 | -11.38 | -3.4378 | 76.886 | -11.3983 | 111.7996 | 111.7035 | -11.5311 | -11.5494 | 0.045776 | -0.032044 | 0.31128 | 122.9645 | 0.59051 | 0.62256 | -0.16937 | -0.18311 | -0.20142 | 0.13733 | 7.9102 | -0.050354 | 0.15106 | 0.041199 | 123.3215 | 122.8409 | 24.6826 | -123.0423 | 123.1476 | 123.0515 | 88.2339 | -123.2117
4054.0156 | 123.0423 | -14.4196 | 108.6914 | -0.14511 | 0.017703 | 0.071455 | 0.083975 | 0.13078 | 0.0071863 | -0.0077183 | 0.068512 | -0.011903 | 0.074304 | 0.059321 | 0.025784 | -0.012828 | 108.7784 | 108.9432 | 13.179 | -13.8565 | 109.227 | -13.9664 | -14.1174 | -6.4499 | 74.1577 | -14.6484 | 108.8333 | 108.7692 | -14.4836 | -14.5798 | 0.45319 | 0.30212 | 0.53558 | 123.3627 | 0.56305 | 0.26093 | 0.086975 | -0.064087 | -0.16022 | 0.14191 | 7.9697 | -0.22888 | -0.068664 | 0.07782 | 123.6465 | 123.1979 | 27.5986 | -122.8088 | 123.2529 | 123.1888 | 88.5773 | -123.2712
4055.0156 | 122.5204 | -15.7242 | 103.244 | -0.03067 | 0.021335 | 0.071455 | 0.091666 | 0.13185 | 0.012313 | -0.0092137 | 0.10666 | -0.0072034 | 0.075159 | 0.061244 | 0.030911 | -0.0094102 | 75.0275 | 52.3499 | 0.018311 | -22.2931 | 83.7799 | -40.0406 | -36.644 | -11.9247 | 68.985 | -20.5399 | 102.7267 | 102.8641 | -14.8499 | -13.765 | -24.3164 | -20.9198 | -19.4641 | 68.074 | -6.5689 | 14.3509 | -28.2166 | 0.87433 | 1.9592 | -0.51727 | 3.7994 | -4.8157 | -6.7749 | -0.37994 | 99.5041 | 90.7516 | 15.7425 | -139.888 | 118.4509 | 118.5883 | 84.7092 | -117.009
4056.0156 | 123.0698 | -51.9104 | 70.9717 | -0.19852 | 0.01578 | 0.071455 | 0.17412 | 0.13099 | 0.042434 | -0.0081455 | -0.12985 | -0.0097668 | 0.071314 | 0.061457 | 0.070859 | -0.010265 | 70.6924 | 70.752 | 5.5206 | -45.0119 | 70.9625 | -52.2537 | -52.3041 | -43.6615 | 39.2578 | -49.8779 | 70.8435 | 70.8618 | -52.2308 | -52.1851 | -0.34332 | -0.39368 | -0.009156 | 122.6624 | 6.8985 | 7.2922 | -0.27924 | -0.32043 | -0.27466 | -0.12817 | 8.2489 | 2.0325 | 2.3071 | -0.10986 | 122.8729 | 122.6028 | 57.431 | -123.2758 | 122.7539 | 122.7722 | 91.1682 | -123.1567
4057.0156 | 123.0606 | -40.1917 | 82.4707 | 0.12955 | 0.022616 | 0.071455 | 0.22817 | 0.13185 | 0.050125 | -0.0075047 | 0.0914 | -0.0084852 | 0.074732 | 0.059535 | 0.11871 | -0.010905 | 83.8577 | 83.8165 | 8.2031 | -40.2649 | 83.6884 | -39.4501 | -39.6423 | -32.3502 | 50.1434 | -44.1284 | 82.5394 | 82.4982 | -40.5075 | -40.3656 | 0.74158 | 0.54932 | 1.2177 | 124.0082 | -0.073243 | -0.62256 | 1.387 | -0.31586 | -0.17395 | 0.068665 | 7.8415 | -3.9368 | -3.7628 | 0.027466 | 123.88 | 124.0494 | 48.3948 | -122.113 | 122.731 | 122.6898 | 90.3351 | -122.8363
4058.0156 | 122.9828 | -53.952 | 68.8889 | -0.21378 | 0.016849 | 0.073591 | 0.35677 | 0.13099 | 0.051834 | -0.0079319 | -0.12985 | -0.006349 | 0.071741 | 0.060389 | 0.23898 | -0.0077012 | 68.1564 | 68.3578 | 4.9438 | -43.3548 | 68.573 | -54.5059 | -54.4922 | -44.664 | 37.5229 | -43.0252 | 69.0674 | 68.9621 | -54.1855 | -54.1855 | -0.55389 | -0.54016 | -0.31586 | 122.3099 | 10.5972 | 11.1374 | -0.73242 | -0.23346 | -0.23346 | 0.17853 | 9.288 | 10.9268 | 11.1603 | 0.073242 | 122.525 | 122.1085 | 58.8959 | -123.381 | 123.0194 | 122.9141 | 91.4749 | -123.0743
4059.0156 | 122.9828 | -50.3586 | 72.5739 | -0.045929 | 0.019626 | 0.070387 | 0.40121 | 0.13121 | 0.053329 | -0.0055821 | 0.030365 | -0.0084852 | 0.0711 | 0.060176 | 0.28491 | -0.012614 | 72.4136 | 72.5098 | 5.809 | -41.629 | 72.5693 | -50.4456 | -50.4913 | -41.5466 | 40.5304 | -40.4205 | 72.5235 | 72.4594 | -50.679 | -50.6607 | -0.086975 | -0.13275 | -0.004578 | 122.8683 | 8.7296 | 8.8623 | -0.16022 | -0.32043 | -0.30212 | -0.050354 | 8.812 | 9.938 | 10.2402 | -0.11444 | 122.9279 | 122.7722 | 56.1676 | -123.0652 | 122.8821 | 122.818 | 90.889 | -123.2346
4060.0156 | 123.0011 | -91.1499 | 31.6864 | -0.19089 | 0.016849 | 0.089613 | 0.71908 | 0.13463 | -0.00050425 | -0.0075047 | -0.28244 | -0.0097668 | 0.070459 | 0.064021 | 0.65341 | -0.011119 | 31.6269 | 31.6544 | -2.3941 | -90.9576 | 31.8878 | -91.1728 | -91.2643 | -80.7404 | 2.7557 | -71.1548 | 31.8192 | 31.7322 | -91.3925 | -91.3971 | -0.022889 | -0.11444 | 0.20142 | 122.8043 | 0.19226 | 0.3067 | -0.059509 | -0.24262 | -0.24719 | 0.13275 | 10.4095 | 19.9951 | 20.2423 | 0.045777 | 123.0377 | 122.7768 | 88.7558 | -122.9507 | 122.9691 | 122.8821 | 93.9056 | -123.0835
4061.0156 | 122.9187 | -49.1821 | 74.1623 | -0.023041 | 0.020907 | 0.0706 | 0.54369 | 0.13035 | 0.010818 | -0.0072911 | 0.38132 | -0.0089124 | 0.074945 | 0.064234 | 0.48828 | -0.011119 | 87.9044 | 88.2614 | 8.9035 | -34.0851 | 87.442 | -35.8978 | -36.3098 | -42.0319 | 40.7272 | -18.8004 | 72.1985 | 72.3907 | -50.5005 | -50.2808 | 13.2843 | 12.8723 | 13.2797 | 137.4435 | 15.097 | 2.2247 | 13.7421 | -1.3184 | -1.0986 | -1.9638 | 7.1503 | 30.3818 | 31.4804 | -1.7715 | 136.6241 | 137.0865 | 58.0856 | -110.4721 | 121.3806 | 121.5729 | 89.9094 | -124.4431
4062.0156 | 122.9507 | -47.5479 | 75.2838 | -0.076447 | 0.02048 | 0.16395 | 0.69002 | 0.13035 | 0.031967 | -0.0092137 | -0.038299 | -0.0082716 | 0.074518 | 0.064234 | 0.6846 | -0.010692 | 74.3912 | 74.4232 | 6.4453 | -42.7597 | 74.7528 | -48.23 | -48.3627 | -37.6923 | 43.2495 | -19.1254 | 75.1511 | 75.1236 | -47.9004 | -47.8775 | -0.68207 | -0.81482 | -0.531 | 121.9711 | 4.7882 | 5.603 | -0.89264 | -0.35248 | -0.32959 | -0.13275 | 9.8557 | 28.4225 | 28.7521 | -0.16022 | 122.3007 | 121.9391 | 53.9932 | -123.6465 | 122.699 | 122.6715 | 90.7974 | -123.1613
4063.0156 | 122.7905 | -102.887 | 19.9448 | 0.015106 | 0.018985 | 0.068037 | 0.98589 | 0.13505 | 0.0018457 | -0.0083591 | -0.12985 | -0.0082716 | 0.072809 | 0.067439 | 0.92514 | -0.0074876 | 18.9331 | 19.7479 | -4.541 | -102.5574 | 19.6884 | -103.0609 | -103.0792 | -89.7491 | -8.0338 | -36.1542 | 19.9814 | 19.9585 | -103.0197 | -103.0151 | -0.17395 | -0.19226 | -0.25635 | 122.6349 | 0.32959 | 0.52185 | -1.0117 | -0.13275 | -0.12817 | 0.036621 | 13.1378 | 66.7328 | 66.861 | 0.013733 | 122.5754 | 121.8201 | 98.3459 | -123.024 | 122.8683 | 122.8455 | 94.8532 | -122.9599
4064.0156 | 122.8958 | -105.9906 | 16.8137 | -0.23666 | 0.019839 | 0.12913 | 1.2606 | 0.13548 | -0.00029045 | -0.0070773 | -0.24429 | -0.0097668 | 0.070673 | 0.065516 | 1.2191 | -0.0089828 | 16.5253 | 16.3879 | -5.278 | -105.8945 | 16.7999 | -106.0867 | -106.192 | -93.9789 | -10.9314 | -62.1918 | 16.8732 | 16.832 | -106.1462 | -106.1462 | -0.09613 | -0.20142 | -0.013733 | 122.3785 | 0.096131 | 0.29755 | -0.28839 | -0.15564 | -0.15564 | 0.059509 | 12.0117 | 43.7988 | 43.9545 | 0.01831 | 122.7905 | 122.5159 | 100.7126 | -123.0057 | 122.8638 | 122.8226 | 95.0592 | -122.9599
4065.0156 | 122.818 | -110.1059 | 12.6663 | 0.015106 | 0.021335 | 0.23124 | 1.5257 | 0.13762 | 0.0033411 | -0.0057957 | 0.037995 | -0.0084852 | 0.073236 | 0.066371 | 1.5872 | -0.010478 | 12.2772 | 12.236 | -6.0333 | -110.0281 | 12.6389 | -110.1791 | -110.2798 | -97.6776 | -14.8544 | -58.9096 | 12.7029 | 12.6572 | -110.2661 | -110.2753 | -0.073242 | -0.17395 | -0.027466 | 122.3419 | 0.07782 | 0.25177 | -0.3891 | -0.16022 | -0.16937 | 0.036621 | 12.4283 | 51.1963 | 51.3657 | -0.009155 | 122.7448 | 122.3831 | 104.0726 | -122.9462 | 122.8088 | 122.7631 | 95.2515 | -122.9416
4066.0156 | 122.85 | -112.4039 | 10.3821 | -0.12222 | 0.019412 | 0.196 | 1.4178 | 0.14125 | 0.00056395 | -0.0049411 | -0.03067 | -0.0084852 | 0.072809 | 0.064448 | 1.4445 | -0.0079148 | 9.9655 | 9.9014 | -6.4178 | -112.3215 | 10.2859 | -112.5229 | -112.6556 | -99.9985 | -16.8137 | -62.5214 | 10.3729 | 10.3546 | -112.5549 | -112.5504 | -0.11902 | -0.25177 | -0.09613 | 122.3053 | 0.082398 | 0.33417 | -0.41657 | -0.15106 | -0.14648 | -0.009155 | 12.4054 | 49.8825 | 50.029 | -0.027466 | 122.6898 | 122.3694 | 105.986 | -123.0377 | 122.7768 | 122.7585 | 95.5902 | -122.9324
4067.0156 | 122.7676 | -112.6099 | 10.1761 | 0.0074768 | 0.019412 | 0.1945 | 1.5411 | 0.15535 | 0.0044091 | -0.0043003 | 0.11429 | -0.0082716 | 0.070886 | 0.067866 | 1.5493 | -0.0085556 | 9.7961 | 9.6954 | -6.4957 | -112.5275 | 10.1257 | -112.6373 | -112.7106 | -99.7879 | -17.1158 | -60.6354 | 10.2036 | 10.1578 | -112.7426 | -112.6465 | -0.027466 | -0.10071 | -0.050354 | 122.3053 | 0.082397 | 0.1831 | -0.37994 | -0.13275 | -0.036621 | 0.027466 | 12.822 | 51.9745 | 52.0111 | -0.01831 | 122.7356 | 122.406 | 106.1142 | -122.8867 | 122.8134 | 122.7676 | 95.4941 | -122.8226
4068.0156 | 122.8226 | -112.9578 | 9.7778 | -0.24429 | 0.017489 | 0.1898 | 1.6607 | 0.13185 | 0.0022729 | -0.0064365 | 0.030365 | -0.0072034 | 0.069605 | 0.11721 | 1.6322 | -0.0091966 | 9.4254 | 9.343 | -6.4316 | -112.825 | 9.7183 | -112.9807 | -113.0997 | -10.0479 | -14.8544 | -55.6595 | 9.8145 | 9.7641 | -113.0722 | -113.0814 | -0.022888 | -0.14191 | -0.059509 | 122.3007 | 0.13275 | 0.27466 | -0.35248 | -0.11444 | -0.1236 | 0.036621 | 102.9099 | 57.2983 | 57.4219 | -0.013733 | 122.6761 | 122.3831 | 106.5262 | -122.8775 | 122.7722 | 122.7219 | 98.1033 | -122.8592
4069.0156 | 122.6807 | -111.7905 | 10.9543 | 0.083771 | 0.01813 | 0.20433 | 1.9604 | 0.12993 | 0.0020593 | -0.0064365 | 0.20584 | -0.010194 | 0.071527 | 0.11614 | 1.9435 | -0.0081284 | 10.4874 | 10.318 | -6.2347 | -111.6989 | 10.8444 | -111.8408 | -111.9186 | -11.174 | -13.7466 | -45.2911 | 10.9772 | 10.9222 | -111.8774 | -111.8729 | -0.050354 | -0.12817 | -0.10986 | 122.1085 | 0.091552 | 0.21973 | -0.46692 | -0.086975 | -0.082398 | 0.022888 | 100.6165 | 66.4993 | 66.5817 | -0.032044 | 122.6349 | 122.2778 | 105.5557 | -122.8729 | 122.7676 | 122.7127 | 98.0438 | -122.8271
4070.0156 | 122.7859 | -113.1134 | 9.581 | -0.11459 | 0.01813 | 0.18553 | 1.6409 | 0.13249 | 0.0014185 | -0.0081455 | 0.0914 | -0.009126 | 0.067682 | 0.11401 | 1.6002 | -0.0085556 | 9.2697 | 9.1461 | -6.4499 | -112.9898 | 9.5718 | -113.1317 | -113.2553 | -9.3613 | -15.0055 | -56.6803 | 9.5993 | 9.5856 | -113.2416 | -113.2507 | -0.018311 | -0.14191 | -0.009156 | 122.2595 | 0.1236 | 0.2655 | -0.31128 | -0.12817 | -0.13733 | 0.01831 | 103.7521 | 56.4331 | 56.5704 | 0.004577 | 122.6852 | 122.3831 | 106.6635 | -122.8363 | 122.7127 | 122.699 | 98.1079 | -122.8317
4071.0156 | 122.7997 | -114.6927 | 8.0704 | -0.0077822 | 0.017703 | 0.1584 | 1.4911 | 0.13228 | 0.0046227 | -0.0049411 | 0.18295 | -0.010408 | 0.068109 | 0.11679 | 1.4323 | -0.0074876 | 7.695 | 7.5897 | -6.7886 | -114.5416 | 8.0109 | -114.6973 | -114.8209 | -8.1619 | -16.452 | -67.8223 | 8.0658 | 8.0246 | -114.8254 | -114.8071 | -0.004578 | -0.12817 | -0.05951 | 122.2824 | 0.15106 | 0.27924 | -0.37537 | -0.13275 | -0.11444 | -0.004578 | 106.5308 | 46.8704 | 46.9849 | -0.045777 | 122.7036 | 122.3877 | 107.9041 | -122.8912 | 122.7585 | 122.7173 | 98.2407 | -122.8775
4072.0156 | 122.7997 | -113.2599 | 9.4528 | -0.19852 | 0.016635 | 0.17955 | 1.7511 | 0.13078 | 0.0033411 | -0.0068637 | -0.015411 | -0.010194 | 0.067682 | 0.11465 | 1.7066 | -0.0091966 | 9.05 | 8.963 | -6.4316 | -113.1134 | 9.375 | -113.2782 | -113.4155 | -9.4162 | -15.1245 | -56.5063 | 9.4711 | 9.4254 | -113.3881 | -113.3698 | -0.01831 | -0.15564 | -0.07782 | 122.2229 | 0.14648 | 0.30212 | -0.40283 | -0.12817 | -0.10986 | 0.01831 | 103.8437 | 56.7535 | 56.8634 | -0.027466 | 122.6349 | 122.3099 | 106.8283 | -122.8683 | 122.731 | 122.6852 | 98.1354 | -122.8226
4073.0156 | 122.7264 | -114.592 | 8.139 | 0.0074768 | 0.020053 | 0.16524 | 1.533 | 0.12907 | 0.0014185 | -0.0066501 | 0.31265 | -0.010194 | 0.070673 | 0.11593 | 1.4748 | -0.0081284 | 7.7133 | 7.6126 | -6.8161 | -114.5142 | 8.0658 | -114.6103 | -114.7385 | -8.0612 | -16.42 | -63.1531 | 8.1528 | 8.1299 | -114.7476 | -114.7293 | -0.018311 | -0.14648 | -0.073242 | 122.2046 | 0.07782 | 0.2243 | -0.42572 | -0.15564 | -0.13733 | 0.013733 | 106.5308 | 51.4389 | 51.5762 | -0.009155 | 122.6578 | 122.3053 | 107.7759 | -122.8775 | 122.7448 | 122.7219 | 98.172 | -122.8683
4074.0156 | 122.7356 | -113.5666 | 9.1141 | -0.15274 | 0.018771 | 0.17634 | 1.8545 | 0.13035 | 0.0020593 | -0.0055821 | -1.1751 | -0.010621 | 0.069391 | 0.1155 | 1.8059 | -0.0091966 | 8.7204 | 8.6014 | -6.5186 | -113.4384 | 9.0179 | -113.5757 | -113.6673 | -8.7387 | -15.3717 | -50.4547 | 9.169 | 9.1187 | -113.681 | -113.6765 | -0.009156 | -0.10071 | -0.096131 | 122.168 | 0.12817 | 0.22888 | -0.39368 | -0.11444 | -0.10986 | 0.054931 | 104.8279 | 63.1119 | 63.2217 | 0.004577 | 122.5845 | 122.287 | 107.048 | -122.7814 | 122.7356 | 122.6852 | 98.1949 | -122.7905
4075.0156 | 122.7219 | -114.5874 | 8.1299 | 0.15244 | 0.019839 | 0.1616 | 1.6727 | 0.12843 | 0.0018457 | -0.0043003 | -0.45792 | -0.010835 | 0.0664 | 0.1202 | 1.6098 | -0.0081284 | 7.7225 | 7.7637 | -6.7337 | -114.5782 | 8.1024 | -114.5462 | -114.6744 | -7.6492 | -16.4108 | -62.4161 | 8.1619 | 8.1253 | -114.6973 | -114.6698 | 0.041198 | -0.086975 | -0.027466 | 122.3511 | 0.009155 | 0.09613 | -0.40741 | -0.10986 | -0.082398 | 0.032043 | 106.9382 | 52.1713 | 52.2537 | -0.004578 | 122.6898 | 122.3099 | 107.8537 | -122.8043 | 122.7493 | 122.7127 | 98.1766 | -122.7997
4076.0156 | 122.7219 | -113.5941 | 9.0912 | -0.068817 | 0.018558 | 0.17293 | 1.9017 | 0.12993 | 0.0020593 | -0.0064365 | 0.14481 | -0.0095532 | 0.067896 | 0.11572 | 1.8527 | -0.008342 | 8.7204 | 8.5831 | -6.4545 | -113.4567 | 9.0179 | -113.5941 | -113.7039 | -8.9859 | -15.4633 | -51.2695 | 9.1141 | 9.082 | -113.6993 | -113.6627 | 0 | -0.10986 | -0.073243 | 122.1771 | 0.13733 | 0.24719 | -0.37079 | -0.10529 | -0.068665 | 0.022888 | 104.6082 | 62.3245 | 62.3932 | -0.009156 | 122.612 | 122.3145 | 107.1396 | -122.7951 | 122.7081 | 122.6761 | 98.1308 | -122.7539
4077.0156 | 122.5479 | -113.8504 | 8.8577 | 0.068512 | 0.018985 | 0.17485 | 1.8387 | 0.12971 | 0.0020593 | -0.0077183 | 0.31265 | -0.0093396 | 0.0758 | 0.11978 | 1.7852 | -0.012401 | 8.3862 | 8.2626 | -6.5735 | -113.7131 | 8.7936 | -113.8596 | -113.9648 | -7.8964 | -15.8157 | -49.6353 | 8.9035 | 8.8531 | -113.9603 | -113.9328 | -0.009155 | -0.11444 | -0.064087 | 122.113 | 0.13733 | 0.25177 | -0.4715 | -0.10986 | -0.082397 | 0.045776 | 105.954 | 64.2151 | 64.2975 | -0.004578 | 122.644 | 122.2366 | 107.2769 | -122.8226 | 122.7539 | 122.7036 | 98.0347 | -122.7905
4078.0156 | 122.7173 | -114.1251 | 8.5236 | -0.16037 | 0.017703 | 0.15883 | 1.8028 | 0.13356 | 0.0046227 | -0.0070773 | 0.045624 | -0.0086988 | 0.06875 | 0.117 | 1.738 | -0.0081284 | 8.1024 | 8.0154 | -6.5643 | -114.0427 | 8.4137 | -114.2166 | -114.3082 | -7.2968 | -15.976 | -56.7719 | 8.519 | 8.4686 | -114.2899 | -114.3036 | -0.091553 | -0.18311 | -0.10986 | 122.1405 | 0.082397 | 0.2655 | -0.42114 | -0.16479 | -0.17853 | -0.004578 | 106.8283 | 57.3532 | 57.5317 | -0.054932 | 122.5388 | 122.2275 | 107.5607 | -122.8317 | 122.644 | 122.5937 | 98.1491 | -122.8271
4079.0156 | 122.6669 | -116.1987 | 6.4774 | 0.030365 | 0.021335 | 0.13319 | 1.3693 | 0.13163 | 0.0031273 | -0.0049411 | 0.12955 | -0.0076306 | 0.068109 | 0.11828 | 1.2804 | -0.0074876 | 6.1478 | 6.0196 | -7.0862 | -116.0797 | 6.4682 | -116.2308 | -116.3361 | -5.1819 | -17.8802 | -75.563 | 6.4957 | 6.459 | -116.3864 | -116.3498 | -0.032044 | -0.13733 | -0.009155 | 122.2183 | 0.11902 | 0.25635 | -0.32959 | -0.18768 | -0.15106 | 0.018311 | 111.0168 | 40.6357 | 40.7867 | -0.018311 | 122.6669 | 122.3465 | 109.1125 | -122.8134 | 122.6944 | 122.6578 | 98.3185 | -122.8271
4080.0156 | 122.7631 | -113.9145 | 8.7387 | -0.16037 | 0.019198 | 0.1631 | 1.7342 | 0.13163 | 0.0078271 | -0.0062229 | 0.11429 | -0.0089124 | 0.067041 | 0.11956 | 1.6732 | -0.0072738 | 8.4091 | 8.2855 | -6.4911 | -113.7909 | 8.7387 | -113.9145 | -113.9923 | -6.4911 | -15.7379 | -56.1172 | 8.757 | 8.7296 | -114.0244 | -114.006 | 0 | -0.07782 | 0 | 122.2 | 0.1236 | 0.20142 | -0.32959 | -0.10986 | -0.091552 | 0.018311 | 107.4234 | 57.7972 | 57.8888 | -0.009155 | 122.6532 | 122.3236 | 107.4234 | -122.731 | 122.6715 | 122.644 | 98.1766 | -122.7447
4081.0156 | 122.818 | -114.2944 | 8.3405 | 0.12192 | 0.017489 | 0.15306 | 1.8184 | 0.12822 | 0.0022729 | -0.0047275 | 0.3508 | -0.010835 | 0.067468 | 0.11572 | 1.7525 | -0.0068466 | 7.9285 | 7.8003 | -6.5964 | -117.1555 | 8.3084 | -114.3265 | -114.4455 | -8.4686 | -16.2415 | -56.8176 | 8.3542 | 8.3084 | -114.4226 | -114.4135 | -0.032043 | -0.15106 | -0.032043 | 122.0947 | -2.861 | -2.71 | -0.41199 | -0.12817 | -0.11902 | 0.013733 | 105.8258 | 57.4768 | 57.5958 | -0.032043 | 122.6028 | 122.2229 | 107.6981 | -122.7859 | 122.6486 | 122.6028 | 98.053 | -122.7539
4082.0312 | 122.8088 | -116.9998 | 5.6213 | -0.23666 | 0.011935 | -0.035357 | 1.1581 | 0.12629 | -0.0049903 | -0.0094273 | 0.28214 | -0.012117 | 0.065759 | 0.11871 | 0.89117 | -0.004924 | 5.278 | 5.2643 | -7.1045 | -115.5899 | 5.6168 | -117.041 | -117.1509 | -6.0516 | -18.663 | -75.2838 | 5.6351 | 5.5984 | -117.1692 | -117.1875 | -0.041199 | -0.15106 | -0.004578 | 122.2641 | 1.4099 | 1.561 | -0.34332 | -0.16937 | -0.18768 | 0.013733 | 110.9482 | 41.716 | 41.9037 | -0.022888 | 122.6166 | 122.2778 | 109.8953 | -122.7722 | 122.6349 | 122.5983 | 98.3368 | -122.8088
4083.0156 | 122.6715 | -114.5554 | 8.0521 | 0.10666 | 0.021121 | 0.1522 | 1.8382 | 0.13035 | 0.0061181 | -0.0070773 | 2.2124 | -0.0086988 | 0.06875 | 0.11401 | 1.7649 | -0.0074876 | 7.6126 | 7.4524 | -6.6696 | -114.5096 | 8.0017 | -114.6057 | -114.6835 | -7.576 | -16.4246 | -52.597 | 8.1253 | 8.0475 | -114.6927 | -114.6835 | -0.050354 | -0.12817 | -0.050354 | 122.0078 | 0.045776 | 0.17395 | -0.43945 | -0.13733 | -0.12817 | 0.073242 | 106.9794 | 61.9583 | 62.0865 | -0.004578 | 122.5571 | 122.168 | 107.8857 | -122.7356 | 122.6807 | 122.6028 | 98.1308 | -122.7356
4084.0156 | 122.644 | -115.0635 | 7.5394 | -0.54947 | 0.018771 | 0.14815 | 1.7532 | 0.12928 | 0.0039819 | -0.0051547 | 0.0914 | -0.0097668 | 0.067468 | 0.11828 | 1.6705 | -0.0079148 | 7.2281 | 7.0816 | -6.7017 | -116.5283 | 7.4936 | -115.0772 | -115.21 | -6.8024 | -16.9693 | -56.8726 | 7.5943 | 7.5485 | -115.1916 | -115.1688 | -0.013732 | -0.14648 | -0.045777 | 122.1451 | -1.4648 | -1.3184 | -0.31128 | -0.12817 | -0.10528 | 0.054931 | 108.2611 | 58.1909 | 58.2962 | 0.009155 | 122.5571 | 122.2916 | 108.3618 | -122.7493 | 122.6578 | 122.612 | 98.0942 | -122.7081
4085.0156 | 122.5067 | -115.5304 | 7.0541 | 0.022736 | 0.02048 | 0.14067 | 1.6614 | 0.12822 | 0.0022729 | -0.0047275 | 0.22873 | -0.009126 | 0.070886 | 0.11849 | 1.5786 | -0.0064194 | 6.6513 | 6.4865 | -6.8573 | -115.2374 | 6.9992 | -115.5991 | -115.7227 | -6.0516 | -17.5186 | -63.2446 | 7.0908 | 7.045 | -115.7135 | -115.686 | -0.068664 | -0.19226 | -0.054931 | 122.0169 | 0.29297 | 0.48523 | -0.40283 | -0.1831 | -0.15564 | 0.036621 | 109.4788 | 52.2858 | 52.4414 | -0.009155 | 122.5296 | 122.1817 | 108.6731 | -122.7768 | 122.6212 | 122.5754 | 98.0118 | -122.7402
4086.0156 | 122.7127 | -117.7826 | 4.8798 | -0.099335 | 0.01813 | 0.12529 | 0.92693 | 0.1295 | 0.0014185 | -0.0043003 | -0.084076 | -0.011476 | 0.068964 | 0.12106 | 0.82303 | -0.010265 | 4.8569 | 4.6783 | -7.1732 | -116.478 | 4.9438 | -117.7597 | -117.8879 | -3.0991 | -19.4366 | -86.6776 | 4.8935 | 4.8706 | -117.9749 | -117.9794 | 0.022888 | -0.10528 | 0.064087 | 122.4609 | 1.3046 | 1.4099 | -0.022888 | -0.19226 | -0.19684 | 0.013733 | 114.6835 | 31.105 | 31.3019 | -0.009156 | 122.7264 | 122.6395 | 110.6094 | -122.7676 | 122.6761 | 122.6532 | 98.3459 | -122.8592
4087.0156 | 122.6852 | -113.7085 | 8.8303 | 0.20584 | 0.019198 | 0.16011 | 1.9314 | 0.13035 | -0.0011451 | -0.0075047 | 0.34317 | -0.01233 | 0.067468 | 0.11614 | 1.8696 | -0.008342 | 8.4869 | 8.3954 | -6.2622 | -117.9062 | 8.7433 | -113.7909 | -113.8504 | -9.0958 | -15.7608 | -39.3173 | 8.844 | 8.8211 | -113.8275 | -113.8184 | -0.082398 | -0.14191 | -0.086975 | 122.1039 | -4.1977 | -4.0558 | -0.34332 | -0.11902 | -0.10986 | 0.013733 | 104.6127 | 74.3912 | 74.501 | -0.009155 | 122.4518 | 122.1954 | 107.4463 | -122.6807 | 122.5525 | 122.5296 | 97.9477 | -122.6486
4088.0156 | 122.7539 | -114.3311 | 8.2626 | -0.03067 | 0.020267 | 0.15028 | 2.0555 | 0.12907 | 0.0037683 | -0.0068637 | 0.11429 | -0.010408 | 0.068323 | 0.11828 | 1.9753 | -0.008342 | 7.8918 | 7.7087 | -6.4682 | -119.2657 | 8.1528 | -114.3539 | -114.4363 | -7.1594 | -16.3651 | -44.8242 | 8.2764 | 8.2718 | -114.4455 | -114.4409 | -0.022888 | -0.10528 | -0.10986 | 122.0398 | -4.9347 | -4.8294 | -0.37079 | -0.11444 | -0.10986 | 0.013733 | 107.1716 | 69.5068 | 69.6167 | 0.009156 | 122.4838 | 122.2229 | 107.8629 | -122.699 | 122.6074 | 122.6028 | 97.966 | -122.7036
4089.0156 | 122.6395 | -113.9648 | 8.5602 | 0.19058 | 0.019626 | 0.15498 | 2.1976 | 0.128 | 0.0020593 | -0.0068637 | 0.28214 | -0.010408 | 0.069605 | 0.11614 | 2.1248 | -0.005565 | 8.139 | 7.9514 | -6.4133 | -112.9944 | 8.4686 | -114.0244 | -114.1296 | -8.5144 | -16.1407 | -41.7023 | 8.6105 | 8.5648 | -114.0701 | -114.0656 | -0.059509 | -0.16479 | -0.091553 | 121.9162 | 0.97046 | 1.1353 | -0.42114 | -0.10528 | -0.10071 | 0.050354 | 105.4504 | 72.2626 | 72.3633 | 0.004577 | 122.4335 | 122.1039 | 107.5516 | -122.6898 | 122.5754 | 122.5296 | 97.8241 | -122.6257
4090.0156 | 122.8363 | -114.8483 | 7.7316 | 0.62546 | 0.017917 | 0.149 | 1.9891 | 0.12822 | 0.0029137 | -0.0064365 | 0.045624 | -0.010408 | 0.067468 | 0.1202 | 1.9114 | -0.008342 | 7.3883 | 7.2601 | -6.459 | -116.0614 | 7.6767 | -114.8392 | -114.9307 | -6.514 | -16.8228 | -46.3486 | 7.7774 | 7.7408 | -114.9353 | -114.9216 | 0.009156 | -0.082397 | -0.054931 | 122.1085 | -1.2131 | -1.1307 | -0.34332 | -0.086975 | -0.073242 | 0.045777 | 108.3344 | 68.4998 | 68.573 | 0.009156 | 122.525 | 122.2366 | 108.3893 | -122.6624 | 122.6257 | 122.5891 | 98.0255 | -122.6532
4091.0156 | 122.612 | -115.6586 | 6.9443 | 0.083771 | 0.019198 | 0.14046 | 1.7947 | 0.12993 | 0.0041955 | -0.0064365 | 0.24399 | -0.0084852 | 0.071527 | 0.12106 | 1.7091 | -0.0085556 | 6.5277 | 6.34 | -6.6696 | -116.423 | 6.8665 | -115.6494 | -115.7776 | -4.8752 | -17.688 | -64.6362 | 6.958 | 6.9168 | -115.8005 | -115.7684 | 0.009155 | -0.11902 | -0.07782 | 121.9986 | -0.76447 | -0.64545 | -0.41657 | -0.14191 | -0.10986 | 0.013733 | 110.7834 | 51.0223 | 51.1322 | -0.027466 | 122.525 | 122.1863 | 108.989 | -122.7219 | 122.6166 | 122.5754 | 97.9706 | -122.7127
4092.0156 | 122.6395 | -117.8146 | 4.7836 | 0.14481 | 0.019412 | 0.11674 | 1.1109 | 0.13185 | 0.0016321 | -0.0072911 | 0.30502 | -0.010621 | 0.068109 | 0.12063 | 1.0046 | -0.0059922 | 4.4357 | 4.3579 | -7.164 | -117.5629 | 4.7653 | -117.8558 | -117.952 | -3.6804 | -19.6381 | -84.8145 | 4.7836 | 4.7562 | -118.0023 | -117.9565 | -0.041199 | -0.13733 | -0.01831 | 122.1725 | 0.25177 | 0.3891 | -0.3479 | -0.18768 | -0.14191 | 0 | 114.1342 | 33.0002 | 33.1421 | -0.027465 | 122.58 | 122.2504 | 110.6506 | -122.7356 | 122.5983 | 122.5708 | 98.1766 | -122.7402
4093.0156 | 122.8134 | -115.3473 | 7.2464 | -0.061188 | 0.020907 | 0.14152 | 1.6753 | 0.13078 | 0.0044091 | -0.0057957 | 0.12955 | -0.008058 | 0.067468 | 0.11978 | 1.5889 | -0.0087692 | 6.926 | 6.7932 | -6.633 | -115.0864 | 7.2144 | -115.3564 | -115.4572 | -5.5298 | -17.4042 | -58.2825 | 7.2739 | 7.2418 | -115.4388 | -115.4572 | -0.009155 | -0.10986 | -0.032044 | 122.1405 | 0.26093 | 0.37079 | -0.32044 | -0.091553 | -0.10986 | 0.027466 | 109.8175 | 57.0648 | 57.1747 | -0.004578 | 122.5616 | 122.2733 | 108.7143 | -122.7036 | 122.6212 | 122.5891 | 97.9431 | -122.7036
4094.0156 | 122.6395 | -114.4272 | 8.1482 | -0.17563 | 0.021335 | 0.1475 | 2.0459 | 0.13121 | 0.018081 | -0.0055821 | 0.083771 | -0.010194 | 0.068537 | 0.11871 | 1.9535 | -0.008342 | 7.6859 | 7.5348 | -6.4316 | -111.6486 | 7.9788 | -114.5187 | -114.6103 | -5.9784 | -16.5939 | -44.2657 | 8.1757 | 8.1299 | -114.5233 | -114.5279 | -0.091553 | -0.18311 | -0.16937 | 121.962 | 2.7786 | 2.9617 | -0.46234 | -0.09613 | -0.10071 | 0.027466 | 108.4488 | 70.1614 | 70.2621 | -0.01831 | 122.406 | 122.113 | 107.9956 | -122.7585 | 122.6028 | 122.5571 | 97.8333 | -122.6761
4095.0156 | 122.5708 | -114.2578 | 8.3267 | 0.0914 | 0.020053 | 0.1537 | 2.1685 | 0.12886 | 0.0088953 | -0.0064365 | 0.22873 | -0.011049 | 0.069605 | 0.11785 | 2.0892 | -0.0057786 | 7.8278 | 7.6355 | -6.7474 | -148.8007 | 8.194 | -114.2715 | -114.386 | -6.4407 | -16.5024 | -37.9944 | 8.3405 | 8.2901 | -114.3448 | -114.3219 | -0.013733 | -0.12817 | -0.13275 | 121.8933 | -34.5428 | -34.4147 | -0.49896 | -0.086976 | -0.064087 | 0.013733 | 107.8171 | 76.2634 | 76.3275 | -0.036621 | 122.4518 | 122.0856 | 107.5104 | -122.7127 | 122.5983 | 122.5479 | 97.7554 | -122.6486
4096.0156 | 122.5983 | -114.5142 | 7.9834 | -0.19089 | 0.019839 | 0.14686 | 2.1418 | 0.12993 | 0.0063317 | -0.0068637 | 0.060883 | -0.0089124 | 0.068109 | 0.11785 | 2.062 | -0.006633 | 7.6309 | 7.4799 | -6.395 | -108.8562 | 7.9193 | -114.5645 | -114.6606 | -6.2942 | -16.6992 | -41.2582 | 8.0292 | 8.0017 | -114.5782 | -114.6103 | -0.050354 | -0.14648 | -0.064086 | 121.994 | 5.658 | 5.8044 | -0.35248 | -0.064087 | -0.096131 | 0.045777 | 108.2199 | 73.2559 | 73.3521 | 0.018311 | 122.4335 | 122.1451 | 108.1192 | -122.644 | 122.5433 | 122.5159 | 97.8149 | -122.5937
4097.0156 | 122.5067 | -114.7339 | 7.7179 | 0.12955 | 0.014285 | 0.15135 | 2.0527 | 0.12993 | -0.0026405 | -0.0070773 | 0.38895 | -0.012117 | 0.064691 | 0.117 | 1.9772 | -0.0062058 | 7.3242 | 7.251 | -6.3812 | -115.7089 | 7.6035 | -114.798 | -114.917 | -5.722 | -16.9327 | -43.0847 | 7.7316 | 7.6859 | -114.8804 | -114.8438 | -0.064087 | -0.1831 | -0.11444 | 121.9849 | -0.97504 | -0.79193 | -0.39368 | -0.14648 | -0.10986 | 0.013732 | 109.0118 | 71.6492 | 71.759 | -0.032044 | 122.3373 | 122.0581 | 108.3527 | -122.6349 | 122.4655 | 122.4197 | 97.8012 | -122.5616
4098.0156 | 122.6166 | -115.274 | 7.251 | -0.20615 | 0.018344 | 0.1396 | 1.9562 | 0.12971 | 0.0029137 | -0.0070773 | -0.084076 | -0.010194 | 0.067682 | 0.11679 | 1.8655 | -0.0079148 | 6.839 | 6.7062 | -6.5689 | -116.6977 | 7.1686 | -115.3152 | -115.3793 | -6.1111 | -17.4133 | -49.4476 | 7.2922 | 7.2281 | -115.3839 | -115.3748 | -0.041199 | -0.10529 | -0.082398 | 121.9803 | -1.4236 | -1.3184 | -0.41199 | -0.10986 | -0.10071 | 0.041198 | 109.1629 | 65.8264 | 65.9271 | -0.022889 | 122.4426 | 122.113 | 108.7051 | -122.6303 | 122.5662 | 122.5021 | 97.8607 | -122.6257
4099.0156 | 122.5754 | -117.0273 | 5.5618 | -0.015411 | 0.019626 | 0.12806 | 1.2512 | 0.1327 | 0.0039819 | -0.0051547 | 0.083771 | -0.010408 | 0.067682 | 0.12213 | 1.1544 | -0.0074876 | 5.2048 | 5.1224 | -6.8344 | -118.4418 | 5.5481 | -117.0456 | -117.16 | -3.1677 | -18.5532 | -73.5947 | 5.571 | 5.5435 | -117.1875 | -117.1738 | -0.01831 | -0.13275 | -0.013733 | 122.1497 | -1.4145 | -1.2817 | -0.35706 | -0.16022 | -0.14648 | 0.009155 | 113.8596 | 43.4326 | 43.5791 | -0.018311 | 122.5754 | 122.2321 | 110.1929 | -122.7219 | 122.5983 | 122.5708 | 98.4741 | -122.7356
4100.0156 | 122.6028 | -115.0314 | 7.5027 | -0.11459 | 0.017276 | 0.14857 | 1.9295 | 0.12779 | 0.0031273 | -0.0068637 | 0.0074766 | -0.010621 | 0.068964 | 0.12106 | 1.848 | -0.0079148 | 7.0999 | 6.9672 | -6.4087 | -115.9241 | 7.3929 | -115.1047 | -115.21 | -3.0029 | -16.6763 | -50.6607 | 7.4936 | 7.457 | -115.1596 | -115.155 | -0.073242 | -0.17853 | -0.10986 | 121.9986 | -0.89264 | -0.71411 | -0.40283 | -0.12817 | -0.1236 | -0.009156 | 112.0285 | 64.3707 | 64.4943 | -0.045777 | 122.4243 | 122.1313 | 108.6227 | -122.7127 | 122.525 | 122.4884 | 98.3551 | -122.6578
4101.0156 | 122.5525 | -114.8987 | 7.6355 | -0.023041 | 0.017489 | 0.14772 | 2.0408 | 0.1295 | 0.0031273 | -0.0047275 | 0.09903 | -0.0097668 | 0.06875 | 0.12127 | 1.958 | -0.0070602 | 7.2144 | 7.0816 | -6.3446 | -114.2715 | 7.5211 | -114.9216 | -115.0406 | -3.0121 | -16.5802 | -43.9453 | 7.6492 | 7.5851 | -115.0269 | -114.9948 | -0.022888 | -0.14191 | -0.11444 | 121.9803 | 0.62714 | 0.76904 | -0.42114 | -0.12817 | -0.09613 | 0.013733 | 111.8866 | 70.9534 | 71.0495 | -0.050354 | 122.4197 | 122.113 | 108.5541 | -122.6761 | 122.5479 | 122.4838 | 98.3185 | -122.6303
4102.0156 | 122.6303 | -114.9994 | 7.4432 | 0.75516 | 0.015353 | 0.14708 | 2.0395 | 0.12822 | -0.0017859 | -0.0083591 | 0.37369 | -0.012758 | 0.064051 | 0.12042 | 1.9537 | -0.0068466 | 7.1045 | 6.9855 | -6.221 | -115.7639 | 7.338 | -115.0177 | -115.1276 | -3.0304 | -16.6626 | -46.8887 | 7.4615 | 7.4249 | -115.1184 | -115.0864 | -0.01831 | -0.12817 | -0.10529 | 121.9849 | -0.76447 | -0.63629 | -0.33875 | -0.11902 | -0.086975 | 0.018311 | 111.969 | 68.1107 | 68.1976 | -0.01831 | 122.3373 | 122.1039 | 108.7784 | -122.5708 | 122.4609 | 122.4243 | 98.3368 | -122.5296
4103.0156 | 122.5021 | -114.7018 | 7.7866 | -0.00015269 | 0.018344 | 0.14943 | 2.1715 | 0.13078 | 0.0041955 | -0.0057957 | 0.083771 | -0.010621 | 0.069177 | 0.11935 | 2.0909 | -0.0068466 | 7.338 | 7.164 | -6.2759 | -115.6586 | 7.6584 | -114.7568 | -114.83 | -6.4316 | -16.6077 | -40.0818 | 7.8049 | 7.7637 | -114.8071 | -114.8026 | -0.054932 | -0.12817 | -0.12817 | 121.8658 | -0.95673 | -0.82855 | -0.44861 | -0.10529 | -0.10071 | 0.018311 | 108.2703 | 74.6201 | 74.7208 | -0.022888 | 122.3602 | 122.0398 | 108.4259 | -122.6166 | 122.5067 | 122.4655 | 98.0942 | -122.5891
4104.0156 | 122.4747 | -113.8641 | 8.5464 | -0.11459 | 0.018558 | 0.15263 | 2.5071 | 0.13249 | 0.0035547 | -0.0062229 | -0.023041 | -0.010194 | 0.068964 | 0.11892 | 2.429 | -0.008342 | 8.0429 | 7.8598 | -6.0974 | -114.2349 | 8.3359 | -114.0289 | -114.1342 | -6.8024 | -15.9027 | -27.7222 | 8.5052 | 8.4549 | -114.0656 | -113.9603 | -0.16479 | -0.27008 | -0.21057 | 121.7239 | -0.37079 | -0.10071 | -0.50354 | -0.20142 | -0.09613 | -0.041199 | 107.0618 | 86.142 | 86.2381 | -0.091553 | 122.2 | 121.907 | 107.7667 | -122.6807 | 122.3694 | 122.319 | 97.9614 | -122.5067
4105.0156 | 122.4609 | -113.9557 | 8.5098 | 0.045624 | 0.020053 | 0.15434 | 2.6015 | 0.12864 | 0.0016321 | -0.0053683 | 0.15244 | -0.010408 | 0.070673 | 0.11871 | 2.5292 | -0.0059922 | 7.9376 | 7.7454 | -6.1249 | -113.8321 | 8.3038 | -114.0244 | -114.1251 | -6.6055 | -16.0355 | -24.6323 | 8.4778 | 8.4457 | -114.0335 | -113.9832 | -0.068665 | -0.16937 | -0.20599 | 121.701 | 0.1236 | 0.29297 | -0.5722 | -0.07782 | -0.027466 | -0.032044 | 107.3502 | 89.3234 | 89.3509 | -0.064087 | 122.2595 | 121.8933 | 107.8308 | -122.6349 | 122.4335 | 122.4014 | 97.9202 | -122.493
4106.0156 | 122.493 | -114.0381 | 8.4091 | -0.22903 | 0.014285 | 0.15391 | 2.6972 | 0.13078 | 0.0014185 | -0.0068637 | -0.045929 | -0.01233 | 0.068537 | 0.11807 | 2.6121 | -0.0098374 | 7.8918 | 7.7179 | -6.1844 | -113.7314 | 8.2626 | -114.0427 | -114.1525 | -7.0267 | -15.9988 | -19.4229 | 8.4641 | 8.4 | -114.0701 | -114.0518 | -0.004578 | -0.11444 | -0.14649 | 121.756 | 0.3067 | 0.42114 | -0.51727 | -0.032043 | -0.013733 | 0.054931 | 107.0114 | 94.6152 | 94.6289 | -0.009156 | 122.3007 | 121.9299 | 107.8537 | -122.5616 | 122.5021 | 122.438 | 98.0392 | -122.4609
4107.0156 | 122.5708 | -113.9832 | 8.3908 | -0.52658 | 0.015994 | 0.15156 | 2.8015 | 0.13099 | 0.00013675 | -0.0057957 | 0.3508 | -0.011049 | 0.069177 | 0.11999 | 2.7155 | -0.0064194 | 7.9239 | 7.8323 | -6.0013 | -114.2075 | 8.2123 | -113.9877 | -114.1159 | -7.3471 | -16.04 | -16.4658 | 8.4045 | 8.3542 | -114.0198 | -114.0106 | -0.004578 | -0.13275 | -0.17853 | 121.8155 | -0.2243 | -0.091552 | -0.46692 | -0.036621 | -0.027466 | 0.013733 | 106.636 | 97.5174 | 97.5449 | -0.036621 | 122.1954 | 121.907 | 107.9819 | -122.5067 | 122.3877 | 122.3373 | 97.9431 | -122.4014
4108.0156 | 122.493 | -114.1113 | 8.2993 | -0.18326 | 0.017276 | 0.1537 | 2.8604 | 0.13142 | 0.0029137 | -0.0072911 | -0.084076 | -0.0097668 | 0.068109 | 0.11828 | 2.7781 | -0.0094102 | 7.7728 | 7.5714 | -6.0654 | -113.9603 | 8.1207 | -114.1296 | -114.2578 | -7.4249 | -16.1224 | -16.1911 | 8.3405 | 8.2809 | -114.1434 | -114.1525 | -0.018311 | -0.14648 | -0.17853 | 121.6827 | 0.15106 | 0.29755 | -0.52643 | -0.032044 | -0.041199 | 0.041199 | 106.6864 | 97.9202 | 97.9614 | -0.01831 | 122.2321 | 121.8842 | 108.046 | -122.5571 | 122.4518 | 122.3923 | 97.9889 | -122.4518
4109.0156 | 122.4472 | -114.2899 | 8.1116 | -0.023041 | 0.020267 | 0.15092 | 2.8709 | 0.13228 | 0.0041955 | -0.0070773 | 0.10666 | -0.0095532 | 0.068537 | 0.11721 | 2.7888 | -0.0087692 | 7.5897 | 7.3792 | -6.2256 | -116.2949 | 7.933 | -114.299 | -114.4226 | -7.8415 | -16.4474 | -15.7059 | 8.1436 | 8.1024 | -114.3356 | -114.3311 | -0.009155 | -0.13275 | -0.17853 | 121.669 | -2.005 | -1.8723 | -0.52185 | -0.045776 | -0.041199 | 0.032044 | 106.4484 | 98.584 | 98.6252 | -0.009155 | 122.2229 | 121.8796 | 108.0643 | -122.5342 | 122.4335 | 122.3923 | 97.8424 | -122.4426
4110.0156 | 122.4472 | -114.3356 | 8.0292 | -0.17563 | 0.018558 | 0.149 | 2.9284 | 0.13548 | 0.0016321 | -0.0072911 | -0.00015237 | -0.0082716 | 0.068964 | 0.11914 | 2.842 | -0.0053512 | 7.5211 | 7.3196 | -6.2531 | -116.2445 | 7.869 | -114.4089 | -114.4913 | -6.72 | -16.5298 | -13.5956 | 8.0795 | 8.02 | -114.3951 | -114.3585 | -0.073243 | -0.15564 | -0.16022 | 121.6553 | -1.9089 | -1.7532 | -0.50812 | -0.05951 | -0.022889 | 0.050354 | 107.6157 | 100.7401 | 100.7629 | -0.009155 | 122.2046 | 121.8567 | 108.0826 | -122.5204 | 122.4152 | 122.3557 | 97.8058 | -122.3877
4111.0156 | 122.3831 | -114.4043 | 7.9605 | -0.03067 | 0.019839 | 0.14793 | 2.9907 | 0.13078 | 0.0035547 | -0.0060093 | 0.083771 | -0.0099806 | 0.068964 | 0.11999 | 2.9029 | -0.0077012 | 7.4478 | 7.2235 | -6.1981 | -111.9141 | 7.782 | -114.4363 | -114.5233 | -5.3787 | -16.6122 | -11.467 | 7.988 | 7.9559 | -114.4592 | -114.4501 | -0.032043 | -0.11902 | -0.17853 | 121.6278 | 2.4902 | 2.6093 | -0.51269 | -0.054932 | -0.045776 | 0.027466 | 109.0256 | 102.9373 | 102.9831 | -0.004577 | 122.1863 | 121.8521 | 108.2062 | -122.4838 | 122.3923 | 122.3602 | 97.7921 | -122.4106
4112.0156 | 122.3877 | -114.5279 | 7.8461 | -0.21378 | 0.01514 | 0.14943 | 3.011 | 0.13078 | -0.00093145 | -0.0051547 | -0.053558 | -0.011049 | 0.068109 | 0.11999 | 2.9223 | -0.0072738 | 7.2784 | 7.0862 | -6.2759 | -116.8442 | 7.6584 | -114.5645 | -114.6378 | -5.0125 | -16.6901 | -10.8353 | 7.8873 | 7.8278 | -114.5966 | -114.5416 | -0.036621 | -0.10986 | -0.18768 | 121.6141 | -2.3163 | -2.2064 | -0.56763 | -0.068665 | -0.013733 | 0.041199 | 109.5154 | 103.6926 | 103.7064 | -0.01831 | 122.1863 | 121.8063 | 108.252 | -122.4838 | 122.4152 | 122.3557 | 97.8378 | -122.3877
4113.0156 | 122.3923 | -114.6469 | 7.7133 | -0.023041 | 0.021548 | 0.1458 | 3.0362 | 0.13228 | 0.0059045 | -0.0055821 | 0.12192 | -0.0095532 | 0.068964 | 0.12213 | 2.9428 | -0.0070602 | 7.2281 | 6.9763 | -6.2988 | -112.3077 | 7.5348 | -114.6469 | -114.7522 | -4.7104 | -16.9327 | -10.2768 | 7.7454 | 7.7087 | -114.6378 | -114.6561 | 0 | -0.10528 | -0.17853 | 121.6232 | 2.3392 | 2.4445 | -0.48523 | 0.009156 | -0.009155 | 0.032043 | 109.9365 | 104.3701 | 104.3793 | -0.004578 | 122.1817 | 121.875 | 108.3481 | -122.4655 | 122.3923 | 122.3557 | 97.7142 | -122.3694
4114.0156 | 122.3969 | -114.8209 | 7.5531 | -0.22141 | 0.017703 | 0.1411 | 3.0429 | 0.13057 | 0.0041955 | -0.0068637 | -0.099335 | -0.011262 | 0.068109 | 0.11914 | 2.9422 | -0.0072738 | 7.0221 | 6.7886 | -6.3446 | -117.4484 | 7.3608 | -114.8209 | -114.9261 | -4.4769 | -17.0563 | -10.4095 | 7.5714 | 7.5165 | -114.8438 | -114.8026 | 0 | -0.10528 | -0.19226 | 121.6095 | -2.6276 | -2.5223 | -0.53101 | -0.022888 | 0.018311 | 0.01831 | 110.3439 | 104.4113 | 104.393 | -0.036622 | 122.1817 | 121.843 | 108.4763 | -122.4792 | 122.3923 | 122.3373 | 97.7646 | -122.3557
4115.0156 | 122.3602 | -114.8895 | 7.4249 | -0.099335 | 0.019412 | 0.14067 | 3.0546 | 0.12971 | 0.0027001 | -0.0057957 | 0.076141 | -0.010835 | 0.070246 | 0.1202 | 2.9573 | -0.008342 | 6.9351 | 6.7108 | -6.3354 | -110.3256 | 7.2556 | -114.8987 | -115.0085 | -4.4037 | -17.1524 | -9.938 | 7.4524 | 7.4112 | -114.9399 | -114.917 | -0.009156 | -0.11902 | -0.16937 | 121.6003 | 4.5639 | 4.6829 | -0.48981 | -0.050354 | -0.027466 | 0.027466 | 110.4858 | 104.9515 | 104.9789 | -0.013733 | 122.1451 | 121.8246 | 108.5541 | -122.4335 | 122.3419 | 122.3007 | 97.7371 | -122.3419
4116.0156 | 122.2961 | -114.8712 | 7.3975 | -0.12222 | 0.018771 | 0.13661 | 3.0685 | 0.13292 | 0.0016321 | -0.0089999 | -0.015411 | -0.0089124 | 0.067041 | 0.12084 | 2.9676 | -0.008342 | 6.8298 | 6.6284 | -6.4178 | -115.9424 | 7.1411 | -115.0177 | -115.1138 | -4.2847 | -17.1982 | -9.5947 | 7.3517 | 7.3196 | -115.0085 | -114.9857 | -0.14648 | -0.24262 | -0.25635 | 121.4996 | -1.0712 | -0.82855 | -0.56763 | -0.13733 | -0.11444 | -0.045776 | 110.5865 | 105.2765 | 105.3909 | -0.07782 | 122.0123 | 121.7011 | 108.4534 | -122.5113 | 122.2229 | 122.1909 | 97.673 | -122.3831
4117.0156 | 122.3282 | -115.1047 | 7.2052 | 0.015106 | 0.018985 | 0.13576 | 3.077 | 0.12886 | 0.0039819 | -0.0040867 | 0.15244 | -0.011262 | 0.070459 | 0.12213 | 2.9766 | -0.008342 | 6.6833 | 6.4499 | -6.4911 | -119.0964 | 7.0404 | -115.1184 | -115.2328 | -4.2618 | -17.3035 | -9.462 | 7.2556 | 7.2052 | -115.1138 | -115.0909 | -0.013733 | -0.12817 | -0.16479 | 121.5546 | -3.9917 | -3.8635 | -0.52185 | -0.009156 | 0.013733 | 0.050354 | 110.8429 | 105.6427 | 105.629 | 0 | 122.1451 | 121.788 | 108.6136 | -122.438 | 122.3602 | 122.3099 | 97.8012 | -122.2961
4118.0156 | 122.3602 | -115.1642 | 7.1274 | -0.18326 | 0.01514 | 0.13811 | 3.0832 | 0.13377 | 0.00013675 | -0.0038731 | -0.038299 | -0.011689 | 0.068964 | 0.12362 | 2.9823 | -0.0062058 | 6.6147 | 6.395 | -6.4728 | -114.5554 | 6.9351 | -115.2054 | -115.3198 | -4.2023 | -17.4454 | -9.256 | 7.1732 | 7.1091 | -115.1825 | -115.1825 | -0.041198 | -0.15564 | -0.19226 | 121.5591 | 0.60883 | 0.76447 | -0.51269 | -0.01831 | -0.01831 | 0.045777 | 110.9619 | 105.9082 | 105.9265 | -0.01831 | 122.0993 | 121.7789 | 108.6914 | -122.4472 | 122.3373 | 122.2733 | 97.7188 | -122.3099
4119.0156 | 122.3511 | -115.2374 | 7.0221 | -0.084076 | 0.021121 | 0.13426 | 3.0929 | 0.13228 | 0.0037683 | -0.0066501 | 0.25162 | -0.010835 | 0.068964 | 0.12341 | 2.9877 | -0.0051376 | 6.5186 | 6.3171 | -6.3492 | -115.0177 | 6.8939 | -115.1916 | -115.3244 | -4.0924 | -17.4774 | -9.1187 | 7.0816 | 7.0084 | -115.2786 | -115.2512 | 0.045777 | -0.086975 | -0.12817 | 121.5546 | 0.21973 | 0.3067 | -0.50354 | -0.041198 | -0.013733 | 0.059509 | 111.145 | 106.1188 | 106.1325 | -0.013733 | 122.1313 | 121.756 | 108.8882 | -122.3465 | 122.319 | 122.2458 | 97.76 | -122.2733
4120.0156 | 122.3007 | -115.3061 | 7.0084 | -0.20615 | 0.017276 | 0.11461 | 3.1181 | 0.12886 | -7.6852e-05 | -0.0077183 | -0.038299 | -0.011903 | 0.06875 | 0.11999 | 2.9894 | -0.0068466 | 6.4087 | 6.2027 | -6.5323 | -115.947 | 6.8069 | -115.3336 | -115.4434 | -4.1473 | -17.6285 | -9.0179 | 7.0312 | 6.9763 | -115.3336 | -115.3427 | -0.027466 | -0.13733 | -0.20142 | 121.5088 | -0.64087 | -0.50354 | -0.59967 | -0.027466 | -0.036621 | 0.022888 | 111.1588 | 106.2881 | 106.3248 | -0.032044 | 122.113 | 121.7148 | 108.7738 | -122.4518 | 122.3373 | 122.2824 | 97.6776 | -122.3511
4121.0156 | 122.2778 | -115.3976 | 6.9122 | -0.015411 | 0.018771 | 0.10948 | 3.1234 | 0.13185 | 0.0035547 | -0.0072911 | 0.15244 | -0.0097668 | 0.071955 | 0.12106 | 2.9977 | -0.0059922 | 6.3263 | 6.1111 | -6.4453 | -115.1001 | 6.7062 | -115.3976 | -115.4984 | -4.1016 | -17.7521 | -9.0042 | 6.9122 | 6.8756 | -115.4205 | -115.4022 | 0 | -0.10071 | -0.20599 | 121.5088 | 0.29755 | 0.39825 | -0.58594 | -0.022888 | -0.004578 | 0 | 111.2961 | 106.3934 | 106.398 | -0.036621 | 122.1039 | 121.7239 | 108.9523 | -122.4106 | 122.3099 | 122.2733 | 97.6456 | -122.3145
4122.0156 | 122.3099 | -115.48 | 6.7841 | -0.18326 | 0.01514 | 0.13212 | 3.1063 | 0.13142 | 0.0014185 | -0.0062229 | -0.03067 | -0.010194 | 0.0664 | 0.12255 | 2.9977 | -0.0074876 | 6.2347 | 6.0196 | -6.4224 | -109.6024 | 6.6055 | -115.5167 | -115.5853 | -4.0741 | -17.7658 | -8.8669 | 6.839 | 6.7795 | -115.4846 | -115.4709 | -0.036621 | -0.10529 | -0.17853 | 121.4996 | 5.8777 | 5.983 | -0.54932 | -0.004577 | 0.009156 | 0.054931 | 111.4059 | 106.6132 | 106.604 | -0.004578 | 122.0856 | 121.7148 | 109.0576 | -122.3694 | 122.319 | 122.2595 | 97.7142 | -122.2549
4123.0156 | 122.2733 | -115.5487 | 6.7108 | 0.045624 | 0.018771 | 0.13148 | 3.1123 | 0.13163 | 0.0041955 | -0.0051547 | 0.09903 | -0.010194 | 0.070459 | 0.1217 | 3.0018 | -0.0085556 | 6.1707 | 5.9372 | -6.4957 | -117.2607 | 6.5186 | -115.5579 | -115.6631 | -4.0649 | -17.9398 | -8.8989 | 6.7474 | 6.7017 | -115.5853 | -115.5716 | -0.009155 | -0.11444 | -0.19226 | 121.4859 | -1.712 | -1.5976 | -0.54016 | -0.036621 | -0.022888 | 0.036622 | 111.4838 | 106.6498 | 106.6727 | -0.009155 | 122.0673 | 121.7194 | 109.053 | -122.374 | 122.2961 | 122.2504 | 97.6089 | -122.2824
4124.0156 | 122.3099 | -115.5945 | 6.6559 | -0.18326 | 0.016849 | 0.13106 | 3.1099 | 0.13163 | 0.0031273 | -0.0064365 | 0.015106 | -0.011689 | 0.069177 | 0.1202 | 3.0054 | -0.0047104 | 6.1295 | 5.928 | -6.427 | -114.2578 | 6.4819 | -115.6082 | -115.6998 | -4.0009 | -17.9214 | -8.757 | 6.7017 | 6.6696 | -115.5853 | -115.5945 | -0.013733 | -0.10529 | -0.17395 | 121.5225 | 1.3367 | 1.442 | -0.52643 | 0.009155 | 0 | 0.045776 | 111.5936 | 106.8375 | 106.8375 | 0.013733 | 122.0764 | 121.7239 | 109.1675 | -122.3557 | 122.2961 | 122.2641 | 97.673 | -122.2504
4125.0156 | 122.2733 | -115.6311 | 6.6238 | -0.045929 | 0.017489 | 0.13191 | 3.1153 | 0.12993 | 0.0050499 | -0.0049411 | 0.083771 | -0.0089124 | 0.067682 | 0.12448 | 3.0084 | -0.0068466 | 6.0837 | 5.8411 | -6.4682 | -115.4892 | 6.4133 | -115.6586 | -115.7639 | -4.0237 | -18.0313 | -8.757 | 6.6376 | 6.5826 | -115.6494 | -115.6265 | -0.027465 | -0.13275 | -0.21057 | 121.4722 | 0.14191 | 0.27466 | -0.54016 | -0.01831 | 0.004578 | 0.013733 | 111.6074 | 106.8741 | 106.8695 | -0.041198 | 122.0444 | 121.7148 | 109.1629 | -122.3877 | 122.2687 | 122.2137 | 97.5998 | -122.2504
4126.0156 | 122.2595 | -115.6586 | 6.5689 | -0.17563 | 0.013644 | 0.13041 | 3.1183 | 0.13057 | 0.0016321 | -0.0085727 | -0.053558 | -0.010408 | 0.067896 | 0.12127 | 3.0067 | -0.0057786 | 5.9921 | 5.7816 | -6.5094 | -114.8941 | 6.3766 | -115.686 | -115.8096 | -4.0146 | -18.1137 | -8.6655 | 6.6147 | 6.5689 | -115.7043 | -115.6769 | -0.027466 | -0.15106 | -0.19226 | 121.4401 | 0.76447 | 0.91553 | -0.57678 | -0.045777 | -0.018311 | 0.045776 | 111.644 | 106.9931 | 107.0114 | 0 | 122.0352 | 121.6507 | 109.1492 | -122.3785 | 122.2733 | 122.2275 | 97.5449 | -122.2458
4127.0156 | 122.2549 | -115.6723 | 6.5277 | -0.045929 | 0.020907 | 0.12059 | 3.1292 | 0.13057 | 0.0056909 | -0.0049411 | 0.068512 | -0.011262 | 0.070673 | 0.1202 | 3.0112 | -0.008342 | 6.0242 | 5.7999 | -6.5186 | -116.1575 | 6.3309 | -115.686 | -115.8554 | -3.9688 | -18.1732 | -8.6472 | 6.5689 | 6.5048 | -115.7135 | -115.686 | -0.013733 | -0.18311 | -0.19684 | 121.4722 | -0.48523 | -0.30212 | -0.50354 | -0.041199 | -0.013733 | 0.041199 | 111.7035 | 107.0251 | 107.0389 | -0.022888 | 122.0032 | 121.6965 | 109.1537 | -122.3831 | 122.2412 | 122.1771 | 97.4991 | -122.2137
4128.0156 | 122.2733 | -115.7135 | 6.4865 | -0.17563 | 0.016421 | 0.12016 | 3.1309 | 0.13014 | 0.0012047 | -0.0079319 | -0.10696 | -0.010194 | 0.067468 | 0.12213 | 3.0127 | -0.0042832 | 5.9097 | 5.6854 | -6.5826 | -115.947 | 6.2805 | -115.7639 | -115.8737 | -3.978 | -18.2053 | -8.6014 | 6.5048 | 6.4774 | -115.7684 | -115.7501 | -0.050354 | -0.16022 | -0.20599 | 121.3989 | -0.23346 | -0.073242 | -0.57678 | -0.054932 | -0.036621 | 0.018311 | 111.7355 | 107.1121 | 107.1487 | -0.009155 | 121.994 | 121.6232 | 109.1309 | -122.3602 | 122.2183 | 122.1909 | 97.5082 | -122.2366
4129.0156 | 122.2229 | -115.7547 | 6.4362 | 0.037994 | 0.020267 | 0.1208 | 3.1332 | 0.13099 | 0.0033411 | -0.0047275 | 0.13718 | -0.010621 | 0.071527 | 0.12319 | 3.015 | -0.004924 | 5.8823 | 5.6488 | -6.5826 | -116.2125 | 6.2256 | -115.8051 | -115.9195 | -3.9688 | -18.306 | -8.5922 | 6.4499 | 6.3995 | -115.8188 | -115.7913 | -0.050354 | -0.16479 | -0.21057 | 121.4035 | -0.45776 | -0.29297 | -0.55389 | -0.064087 | -0.036621 | 0.013733 | 111.7859 | 107.1625 | 107.1991 | -0.036621 | 121.9803 | 121.637 | 109.1721 | -122.3557 | 122.2046 | 122.1542 | 97.4487 | -122.2275
4130.0156 | 122.2458 | -115.8096 | 6.3812 | -0.168 | 0.018771 | 0.1223 | 3.1352 | 0.12993 | 0.0022729 | -0.0057957 | -0.015411 | -0.0099806 | 0.065546 | 0.12277 | 3.0176 | -0.0047104 | 5.8456 | 5.6305 | -6.5643 | -115.6631 | 6.189 | -115.8188 | -115.9424 | -3.9001 | -18.3151 | -8.4732 | 6.4041 | 6.3812 | -115.8142 | -115.8142 | -0.009156 | -0.13275 | -0.19226 | 121.4401 | 0.14648 | 0.27924 | -0.53558 | -0.004578 | -0.004578 | 0.022888 | 111.9095 | 107.3364 | 107.341 | 0 | 121.9986 | 121.6553 | 109.2453 | -122.3236 | 122.2137 | 122.1909 | 97.4945 | -122.1954
4131.0156 | 122.2183 | -115.8371 | 6.3309 | -0.023041 | 0.021335 | 0.12187 | 3.1377 | 0.13078 | 0.0027001 | -0.0070773 | 0.15244 | -0.0097668 | 0.070886 | 0.1217 | 3.0195 | -0.006633 | 5.7999 | 5.5847 | -6.5323 | -115.3931 | 6.1478 | -115.8691 | -115.9836 | -3.891 | -18.4433 | -8.4686 | 6.3858 | 6.308 | -115.9058 | -115.8737 | -0.032044 | -0.14648 | -0.18311 | 121.4218 | 0.44403 | 0.59052 | -0.53101 | -0.068665 | -0.036621 | 0.054931 | 111.9461 | 107.3685 | 107.4051 | -0.022889 | 121.9849 | 121.637 | 109.3048 | -122.3145 | 122.2229 | 122.1451 | 97.3938 | -122.2046
4132.0156 | 122.2366 | -115.892 | 6.308 | -0.17563 | 0.015994 | 0.12166 | 3.1369 | 0.13099 | 0.0022729 | -0.0072911 | -0.053558 | -0.011049 | 0.067255 | 0.12106 | 3.018 | -0.0053512 | 5.7449 | 5.5298 | -6.5186 | -115.5945 | 6.1157 | -115.9195 | -116.011 | -3.9322 | -18.4479 | -8.4641 | 6.3354 | 6.2668 | -115.9103 | -115.9012 | -0.027466 | -0.11902 | -0.19226 | 121.4218 | 0.29755 | 0.41657 | -0.56305 | -0.01831 | -0.009155 | 0.027466 | 111.9598 | 107.428 | 107.4371 | -0.041198 | 122.0078 | 121.637 | 109.3735 | -122.319 | 122.2275 | 122.1588 | 97.4442 | -122.2092
4133.0156 | 122.1909 | -115.8646 | 6.3034 | -0.12985 | 0.020694 | 0.12102 | 3.1379 | 0.13228 | 0.0014185 | -0.0057957 | 0.053253 | -0.010408 | 0.073023 | 0.12106 | 3.0184 | -0.0062058 | 5.7541 | 5.5344 | -6.5048 | -116.5604 | 6.0699 | -115.9149 | -116.0156 | -3.8177 | -18.5349 | -8.3908 | 6.3766 | 6.3217 | -115.8875 | -115.8737 | -0.050354 | -0.15106 | -0.23346 | 121.3989 | -0.6958 | -0.54474 | -0.54932 | -0.022888 | -0.009155 | 0.073242 | 112.0468 | 107.4738 | 107.4829 | 0.01831 | 121.9345 | 121.6187 | 109.3597 | -122.319 | 122.2412 | 122.1863 | 97.3297 | -122.1771
4134.0156 | 122.1817 | -115.9241 | 6.2393 | -0.2977 | 0.016208 | 0.12144 | 3.1422 | 0.12993 | 0.0014185 | -0.0075047 | -0.015411 | -0.010621 | 0.068323 | 0.12298 | 3.0176 | -0.0057786 | 5.6625 | 5.452 | -6.4636 | -115.2328 | 6.0654 | -115.947 | -116.066 | -3.9001 | -18.5806 | -8.3633 | 6.2759 | 6.2302 | -115.9836 | -115.9287 | -0.022888 | -0.14191 | -0.17395 | 121.376 | 0.69122 | 0.83313 | -0.57678 | -0.05951 | -0.004578 | 0.036621 | 112.0239 | 107.5607 | 107.5653 | -0.009155 | 121.9894 | 121.5866 | 109.4604 | -122.3053 | 122.2 | 122.1542 | 97.3434 | -122.168
4135.0156 | 122.2137 | -115.9378 | 6.189 | -0.14511 | 0.018985 | 0.11931 | 3.1428 | 0.12971 | 0.0046227 | -0.0057957 | 0.053253 | -0.0097668 | 0.070246 | 0.12234 | 3.0242 | -0.0062058 | 5.6854 | 5.4611 | -6.4087 | -116.6382 | 6.0013 | -115.9561 | -116.0614 | -3.8498 | -18.6172 | -8.3588 | 6.2164 | 6.1844 | -115.9836 | -115.9607 | -0.018311 | -0.1236 | -0.18768 | 121.3989 | -0.70038 | -0.57678 | -0.50354 | -0.045777 | -0.022888 | 0.027466 | 112.088 | 107.579 | 107.6019 | -0.004578 | 121.9391 | 121.6232 | 109.5291 | -122.2504 | 122.1542 | 122.1222 | 97.3206 | -122.1497
4136.0156 | 122.1954 | -115.9332 | 6.1798 | -0.17563 | 0.013858 | 0.11995 | 3.1435 | 0.13035 | 0.00056395 | -0.0087863 | -0.068817 | -0.010408 | 0.067896 | 0.12448 | 3.0244 | -0.0057786 | 5.571 | 5.3787 | -6.4499 | -115.535 | 5.9784 | -115.9882 | -116.098 | -3.8864 | -18.6356 | -8.313 | 6.1981 | 6.1615 | -116.0339 | -116.0065 | -0.054931 | -0.16479 | -0.20142 | 121.312 | 0.39826 | 0.56305 | -0.60883 | -0.10071 | -0.073242 | 0.01831 | 112.0468 | 107.6202 | 107.6935 | -0.018311 | 121.9116 | 121.5042 | 109.4833 | -122.2778 | 122.1313 | 122.0947 | 97.2977 | -122.1863
4137.0156 | 122.1359 | -116.0248 | 6.1386 | 0.022736 | 0.018344 | 0.1176 | 3.1493 | 0.13057 | 0.0048363 | -0.0049411 | 0.10666 | -0.010194 | 0.070032 | 0.12384 | 3.0265 | -0.0051376 | 5.6076 | 5.3604 | -6.4407 | -111.7722 | 5.9692 | -116.0202 | -116.1301 | -3.8452 | -19.9997 | -8.313 | 6.1798 | 6.134 | -116.0385 | -116.0019 | 0.004577 | -0.10529 | -0.16937 | 121.3852 | 4.2526 | 4.3579 | -0.53101 | -0.013733 | 0.022888 | 0.041199 | 112.1796 | 107.7118 | 107.6889 | -0.004578 | 121.994 | 121.6324 | 109.584 | -122.2687 | 122.2046 | 122.1588 | 96.0251 | -122.1405
4138.0156 | 122.1817 | -116.0019 | 6.1111 | -0.23666 | 0.017489 | 0.11098 | 3.1531 | 0.13228 | 0.0020593 | -0.0075047 | -0.061188 | -0.0095532 | 0.068537 | 0.12213 | 3.0263 | -0.0047104 | 5.571 | 5.3741 | -6.3904 | -114.3723 | 5.9235 | -116.0202 | -116.1255 | -3.8132 | -18.7225 | -8.2123 | 6.1432 | 6.1066 | -116.0294 | -116.0248 | -0.018311 | -0.1236 | -0.18768 | 121.376 | 1.6296 | 1.7532 | -0.54016 | -0.027466 | -0.022888 | 0.032043 | 112.1887 | 107.7896 | 107.8125 | -0.004578 | 121.9254 | 121.5729 | 109.6115 | -122.2366 | 122.1451 | 122.1085 | 97.2794 | -122.1359
4139.0156 | 122.1725 | -116.0202 | 6.0654 | -0.068817 | 0.021976 | 0.11119 | 3.1557 | 0.12864 | 0.0041955 | -0.0062229 | 0.083771 | -0.010621 | 0.070246 | 0.12213 | 3.0293 | -0.0051376 | 5.5573 | 5.3192 | -6.4362 | -114.9353 | 5.8777 | -116.0568 | -116.1713 | -3.7994 | -18.8004 | -8.2123 | 6.0974 | 6.0745 | -116.0797 | -116.0522 | -0.036621 | -0.15106 | -0.18768 | 121.3394 | 1.0849 | 1.236 | -0.50812 | -0.059509 | -0.032043 | 0.032043 | 112.2208 | 107.8079 | 107.84 | 0.009155 | 121.8979 | 121.5775 | 109.584 | -122.2366 | 122.1176 | 122.0947 | 97.2198 | -122.1176
4140.0156 | 122.1588 | -116.0568 | 6.0745 | -0.20615 | 0.017703 | 0.11204 | 3.1552 | 0.13249 | -0.00050425 | -0.0051547 | -0.038299 | -0.0093396 | 0.069605 | 0.12277 | 3.0278 | -0.0072738 | 5.4794 | 5.2826 | -6.5186 | -115.0726 | 5.8777 | -116.0751 | -116.1758 | -3.8223 | -18.8599 | -8.1757 | 6.1203 | 6.0562 | -116.0889 | -116.0706 | -0.01831 | -0.11902 | -0.19684 | 121.3394 | 0.98419 | 1.1032 | -0.59509 | -0.032043 | -0.013733 | 0.045776 | 112.2345 | 107.8812 | 107.8949 | -0.018311 | 121.9345 | 121.5363 | 109.5383 | -122.2504 | 122.1771 | 122.113 | 97.197 | -122.1451
4141.0156 | 122.1497 | -116.0522 | 6.0654 | -0.12222 | 0.019198 | 0.1114 | 3.1578 | 0.13121 | 0.00077755 | -0.0072911 | 0.053253 | -0.011262 | 0.06875 | 0.12213 | 3.0302 | -0.0057786 | 5.5115 | 5.2872 | -6.4453 | -116.1118 | 5.8502 | -116.066 | -116.1987 | -3.7079 | -18.9285 | -8.1299 | 6.1295 | 6.0883 | -116.066 | -116.0614 | -0.013733 | -0.14648 | -0.21515 | 121.3394 | -0.059509 | 0.086975 | -0.55389 | -0.013733 | -0.009155 | 0.064087 | 112.3444 | 107.9224 | 107.9315 | 0.022888 | 121.9025 | 121.5637 | 109.6069 | -122.2641 | 122.1817 | 122.1405 | 97.1237 | -122.1268
4142.0156 | 122.1588 | -116.0797 | 6.0104 | -0.21378 | 0.017062 | 0.10756 | 3.1651 | 0.13014 | 0.00035035 | -0.0064365 | -0.038299 | -0.010408 | 0.069605 | 0.1202 | 3.0323 | -0.005565 | 5.4474 | 5.2322 | -6.4545 | -114.6881 | 5.8228 | -116.1163 | -116.2033 | -3.7216 | -18.9651 | -8.0704 | 6.0379 | 6.0059 | -116.1209 | -116.1026 | -0.036621 | -0.1236 | -0.18768 | 121.312 | 1.3916 | 1.5152 | -0.56305 | -0.041199 | -0.022888 | 0.027466 | 112.3581 | 108.0093 | 108.0322 | -0.004578 | 121.9025 | 121.5271 | 109.6252 | -122.2137 | 122.1176 | 122.0856 | 97.1146 | -122.113
4143.0625 | 122.2366 | -116.0522 | 5.9692 | -0.053558 | 0.014071 | 0.11162 | 3.1657 | 0.12928 | -0.0064857 | -0.0092137 | 0.11429 | -0.01468 | 0.067041 | 0.12234 | 3.0291 | -0.005565 | 5.484 | 5.3146 | -6.3538 | -117.5766 | 5.7816 | -116.0934 | -116.2033 | -3.5797 | -18.9056 | -7.9239 | 6.0013 | 5.9418 | -116.1209 | -116.0889 | -0.041199 | -0.15106 | -0.18768 | 121.3669 | -1.5244 | -1.3733 | -0.48523 | -0.068665 | -0.036621 | 0.032044 | 112.4725 | 108.1284 | 108.165 | -0.027466 | 121.8338 | 121.5363 | 109.6985 | -122.1725 | 122.0535 | 121.994 | 97.1466 | -122.0581
4144.0156 | 122.1405 | -116.1255 | 5.9555 | -0.17563 | 0.019198 | 0.1082 | 3.1681 | 0.1342 | 0.0033411 | -0.0070773 | 0.0074766 | -0.0095532 | 0.06875 | 0.12362 | 3.0336 | -0.0057786 | 5.4337 | 5.2231 | -6.4087 | -122.8363 | 5.777 | -116.1255 | -116.2491 | -3.6392 | -19.1025 | -8.0521 | 6.0104 | 5.9509 | -116.1163 | -116.1301 | 0 | -0.1236 | -0.17853 | 121.3486 | -6.7108 | -6.5872 | -0.52185 | 0.009155 | -0.004578 | 0.054932 | 112.4863 | 108.0734 | 108.078 | -0.004577 | 121.9025 | 121.5591 | 109.7168 | -122.2046 | 122.1359 | 122.0764 | 97.023 | -122.0856
4145.0156 | 122.0764 | -116.1346 | 5.9509 | -0.015411 | 0.019839 | 0.10863 | 3.1672 | 0.12928 | 0.0073999 | -0.0057957 | 0.037995 | -0.010194 | 0.06875 | 0.12341 | 3.034 | -0.0064194 | 5.397 | 5.1544 | -6.3858 | -107.4738 | 5.7449 | -116.1575 | -116.2582 | -3.6713 | -19.2444 | -8.0795 | 5.983 | 5.9235 | -116.185 | -116.1392 | -0.022888 | -0.1236 | -0.20599 | 121.2891 | 8.6609 | 8.7845 | -0.55389 | -0.050354 | -0.004577 | 0.032043 | 112.4634 | 108.0551 | 108.0597 | -0.027466 | 121.8796 | 121.5317 | 109.7488 | -122.2092 | 122.1176 | 122.0581 | 96.8903 | -122.0901
4146.0156 | 122.1176 | -116.1301 | 5.9326 | -0.19089 | 0.018985 | 0.095381 | 3.1779 | 0.12928 | 0.0018457 | -0.0079319 | -0.076446 | -0.010835 | 0.065973 | 0.12127 | 3.0332 | -0.0074876 | 5.4291 | 5.1682 | -6.3721 | -112.674 | 5.7449 | -116.1392 | -116.2582 | -3.6255 | -19.194 | -7.988 | 5.9692 | 5.9326 | -116.1438 | -116.1346 | -0.009155 | -0.12817 | -0.18768 | 121.2982 | 3.4561 | 3.5843 | -0.50354 | -0.013733 | -0.004578 | 0.036621 | 112.5046 | 108.1421 | 108.1467 | 0 | 121.875 | 121.5591 | 109.758 | -122.1909 | 122.0993 | 122.0627 | 96.936 | -122.0673
4147.0156 | 122.0947 | -116.1667 | 5.9235 | -0.023041 | 0.019198 | 0.091749 | 3.1809 | 0.12864 | 0.0029137 | -0.0072911 | 0.12192 | -0.009126 | 0.072809 | 0.12084 | 3.0357 | -0.005565 | 5.397 | 5.1682 | -6.4178 | -115.8737 | 5.7083 | -116.1804 | -116.2903 | -3.6758 | -19.3085 | -8.0338 | 5.9555 | 5.8731 | -116.1987 | -116.1438 | -0.013733 | -0.1236 | -0.21515 | 121.3348 | 0.29297 | 0.41657 | -0.52643 | -0.032043 | 0.022888 | 0.032043 | 112.4908 | 108.1329 | 108.11 | -0.050354 | 121.875 | 121.5637 | 109.7488 | -122.2137 | 122.1222 | 122.0398 | 96.8582 | -122.0673
4148.0156 | 122.1176 | -116.1758 | 5.8914 | -0.16037 | 0.016208 | 0.10328 | 3.1721 | 0.13078 | 0.0033411 | -0.0075047 | -0.061188 | -0.010194 | 0.066828 | 0.12149 | 3.0345 | -0.004924 | 5.3375 | 5.1178 | -6.3904 | -106.2195 | 5.6854 | -116.185 | -116.3177 | -3.6392 | -19.3268 | -7.988 | 5.9006 | 5.8594 | -116.2033 | -116.1575 | -0.009156 | -0.14191 | -0.20599 | 121.2936 | 9.9564 | 10.0983 | -0.55389 | -0.027466 | 0.01831 | 0.009156 | 112.5366 | 108.1879 | 108.1696 | -0.032043 | 121.8613 | 121.5134 | 109.7855 | -122.2092 | 122.0764 | 122.0352 | 96.8491 | -122.049
4149.0156 | 122.0535 | -116.1942 | 5.864 | -0.061188 | 0.017489 | 0.10008 | 3.1736 | 0.13057 | 0.0037683 | -0.0060093 | 0.10666 | -0.0095532 | 0.070032 | 0.12277 | 3.0347 | -0.0059922 | 5.3467 | 5.1041 | -6.5323 | -115.9103 | 5.6671 | -116.2125 | -116.3177 | -3.6621 | -19.4916 | -8.0475 | 5.8731 | 5.8456 | -116.2354 | -116.2216 | -0.01831 | -0.1236 | -0.19684 | 121.2982 | 0.28381 | 0.40741 | -0.51727 | -0.041199 | -0.027466 | 0.009155 | 112.532 | 108.1467 | 108.1741 | -0.018311 | 121.8613 | 121.5408 | 109.6619 | -122.1817 | 122.0673 | 122.0398 | 96.7026 | -122.0856
4150.0156 | 122.0856 | -116.1438 | 5.9143 | -0.10696 | 0.018558 | 0.10478 | 3.1695 | 0.13014 | 0.0029137 | -0.0057957 | 0.060883 | -0.010835 | 0.068323 | 0.12234 | 3.034 | -0.0059922 | 5.3238 | 5.0858 | -6.5506 | -115.1505 | 5.6488 | -116.2308 | -116.3498 | -3.6575 | -19.3817 | -7.8781 | 5.8685 | 5.864 | -116.1026 | -116.1438 | -0.086975 | -0.20599 | -0.2655 | 121.2296 | 0.99335 | 1.1993 | -0.59051 | 0.041199 | 0 | -0.045777 | 112.4863 | 108.2657 | 108.2657 | -0.050354 | 121.7926 | 121.4676 | 109.5932 | -122.2641 | 122.0123 | 122.0078 | 96.7621 | -122.0581
4151.0156 | 122.049 | -116.2308 | 5.8319 | 0.030365 | 0.019839 | 0.10435 | 3.1728 | 0.12886 | 0.0039819 | -0.0075047 | 0.11429 | -0.010835 | 0.072168 | 0.12384 | 3.0368 | -0.004924 | 5.2505 | 5.0217 | -6.6055 | -113.7177 | 5.6168 | -116.3132 | -116.3681 | -3.685 | -19.4687 | -8.0429 | 5.8456 | 5.8044 | -116.272 | -116.2445 | -0.082397 | -0.13733 | -0.21515 | 121.2524 | 2.5131 | 2.6505 | -0.58136 | -0.041199 | -0.013733 | 0.013733 | 112.5458 | 108.1879 | 108.2016 | -0.027466 | 121.8475 | 121.4813 | 109.6252 | -122.2 | 122.0764 | 122.0352 | 96.7621 | -122.0764
4152.0156 | 122.0947 | -116.2125 | 5.7999 | -0.15274 | 0.018771 | 0.099012 | 3.1747 | 0.13035 | 0.0014185 | -0.0068637 | 0.0074766 | -0.010621 | 0.072809 | 0.12319 | 3.0338 | -0.0057786 | 5.2643 | 5.0537 | -6.5323 | -114.7888 | 5.6122 | -116.217 | -116.3635 | -3.6346 | -19.4687 | -7.9422 | 5.8365 | 5.7816 | -116.2491 | -116.2354 | -0.004578 | -0.15106 | -0.18768 | 121.2662 | 1.4236 | 1.5747 | -0.53558 | -0.036621 | -0.022889 | 0.036621 | 112.5778 | 108.2703 | 108.2932 | -0.018311 | 121.8246 | 121.4767 | 109.6802 | -122.1634 | 122.049 | 121.994 | 96.7438 | -122.0352
4153.0156 | 122.0352 | -116.2262 | 5.777 | -0.0383 | 0.021121 | 0.094099 | 3.1866 | 0.13035 | 0.0037683 | -0.0068637 | 0.12955 | -0.010835 | 0.070673 | 0.12319 | 3.0347 | -0.0059922 | 5.2597 | 5.0171 | -6.6055 | -116.0339 | 5.603 | -116.2537 | -116.3635 | -3.6804 | -19.5602 | -8.0154 | 5.8228 | 5.7678 | -116.2582 | -116.217 | -0.027466 | -0.13733 | -0.17395 | 121.2433 | 0.19226 | 0.32959 | -0.51727 | -0.032044 | 0.009155 | 0.045776 | 112.5458 | 108.2108 | 108.2016 | -0.009156 | 121.8292 | 121.4859 | 109.6207 | -122.1405 | 122.049 | 121.994 | 96.666 | -121.994
4154.0156 | 122.0261 | -116.2354 | 5.7587 | -0.22903 | 0.014071 | 0.10115 | 3.176 | 0.12928 | 0.0016321 | -0.0062229 | -0.015411 | -0.010835 | 0.0711 | 0.12298 | 3.0347 | -0.0036424 | 5.2002 | 4.9759 | -6.5186 | -116.2125 | 5.5573 | -116.2674 | -116.3864 | -3.6987 | -19.574 | -7.9468 | 5.8228 | 5.777 | -116.3132 | -116.2674 | -0.032043 | -0.15106 | -0.20142 | 121.2112 | 0.022889 | 0.17395 | -0.55847 | -0.077819 | -0.032043 | 0.064087 | 112.5366 | 108.2886 | 108.3206 | 0.018311 | 121.7926 | 121.4355 | 109.7168 | -122.1451 | 122.0581 | 122.0123 | 96.6614 | -122.0261
4155.0156 | 122.0078 | -116.2628 | 5.777 | -0.084076 | 0.01813 | 0.091749 | 3.1856 | 0.12993 | 0.0044091 | -0.0045139 | 0.12955 | -0.010408 | 0.070459 | 0.12234 | 3.0374 | -0.005565 | 5.2505 | 5.0034 | -6.427 | -116.51 | 5.5573 | -116.1118 | -116.3681 | -3.6209 | -19.6655 | -7.9422 | 5.7861 | 5.7587 | -116.2857 | -116.2582 | 0.15106 | -0.10529 | -0.21973 | 121.2662 | -0.24719 | -0.14191 | -0.52643 | -0.022889 | 0.004577 | 0.009155 | 112.6419 | 108.3206 | 108.316 | -0.018311 | 121.8201 | 121.5134 | 109.8358 | -122.1451 | 122.049 | 122.0215 | 96.5973 | -122.0352
4156.0156 | 122.0535 | -116.2445 | 5.7495 | -0.19852 | 0.017703 | 0.093458 | 3.1871 | 0.13249 | 0.0016321 | -0.0057957 | -0.053558 | -0.010621 | 0.068964 | 0.12106 | 3.0377 | -0.0057786 | 5.1773 | 4.9576 | -6.4682 | -110.3806 | 5.5573 | -116.2857 | -116.3864 | -3.6118 | -19.7296 | -7.8598 | 5.7907 | 5.7266 | -116.304 | -116.272 | -0.041199 | -0.14191 | -0.19226 | 121.2021 | 5.864 | 6.0059 | -0.57221 | -0.059509 | -0.027466 | 0.041198 | 112.6328 | 108.3847 | 108.4122 | -0.022888 | 121.8018 | 121.4218 | 109.7763 | -122.1359 | 122.0352 | 121.9711 | 96.5149 | -122.0215
4157.0156 | 122.0078 | -116.272 | 5.7449 | -0.0077822 | 0.019198 | 0.092817 | 3.1886 | 0.12928 | 0.0046227 | -0.0070773 | 0.076141 | -0.011262 | 0.069391 | 0.12255 | 3.0396 | -0.004924 | 5.191 | 4.9484 | -6.4819 | -117.7139 | 5.5389 | -116.185 | -116.4047 | -3.6301 | -19.7342 | -7.8781 | 5.7632 | 5.7266 | -116.2857 | -116.2857 | 0.086975 | -0.13275 | -0.20599 | 121.2204 | -1.442 | -1.3092 | -0.55389 | -0.013733 | -0.013733 | 0.018311 | 112.6419 | 108.3939 | 108.4076 | -0.01831 | 121.8109 | 121.463 | 109.79 | -122.1497 | 122.0352 | 121.9986 | 96.5378 | -122.0306
4158.0156 | 122.0215 | -116.2628 | 5.7129 | -0.19852 | 0.018558 | 0.10029 | 3.1822 | 0.13185 | 0.0029137 | -0.0057957 | 0.060883 | -0.011689 | 0.068323 | 0.1217 | 3.0377 | -0.0053512 | 5.1773 | 4.9438 | -6.3721 | -116.1301 | 5.5298 | -116.3361 | -116.423 | -3.566 | -19.7205 | -7.8232 | 5.7358 | 5.6946 | -116.3132 | -116.2628 | -0.073243 | -0.16022 | -0.18311 | 121.2067 | 0.13275 | 0.29297 | -0.53558 | -0.050354 | 0 | 0.022888 | 112.6968 | 108.4396 | 108.4396 | -0.018311 | 121.7926 | 121.4401 | 109.8907 | -122.1359 | 121.9986 | 121.9574 | 96.5424 | -121.9757
4159.0156 | 121.9849 | -116.304 | 5.6808 | -0.053558 | 0.020053 | 0.10008 | 3.1817 | 0.13206 | 0.0048363 | -0.0049411 | 0.076141 | -0.010194 | 0.06875 | 0.12277 | 3.0404 | -0.0044968 | 5.1682 | 4.9438 | -6.3904 | -117.1371 | 5.484 | -116.3132 | -116.4276 | -3.5843 | -19.8257 | -7.8506 | 5.7266 | 5.6671 | -116.3269 | -116.304 | -0.009155 | -0.1236 | -0.19684 | 121.2479 | -0.83313 | -0.70953 | -0.51269 | -0.022888 | 0 | 0.045777 | 112.7197 | 108.4534 | 108.4534 | -0.013733 | 121.788 | 121.4722 | 109.9136 | -122.1085 | 122.0306 | 121.9711 | 96.4783 | -121.9849
4160.0156 | 122.0078 | -116.3132 | 5.6763 | -0.015411 | 0.014285 | 0.10307 | 3.1832 | 0.13484 | -7.6852e-05 | -0.0062229 | -0.053558 | -0.0097668 | 0.069177 | 0.1217 | 3.0377 | -0.0051376 | 5.1224 | 4.8935 | -6.3171 | -116.835 | 5.5069 | -116.3177 | -116.4368 | -3.5934 | -19.8441 | -7.814 | 5.7312 | 5.6808 | -116.3315 | -116.2994 | -0.004578 | -0.1236 | -0.16937 | 121.2067 | -0.52185 | -0.39825 | -0.55389 | -0.018311 | 0.013733 | 0.054931 | 112.7197 | 108.4991 | 108.4854 | 0.004577 | 121.8201 | 121.4355 | 109.996 | -122.113 | 122.0444 | 121.994 | 96.4691 | -121.9757
4161.0156 | 122.0215 | -116.2949 | 5.6854 | -0.18326 | 0.020694 | 0.097517 | 3.1858 | 0.13676 | 0.0033411 | -0.0068637 | 0.037995 | -0.0093396 | 0.069391 | 0.12298 | 3.0389 | -0.0057786 | 5.1682 | 4.921 | -6.3492 | -116.6061 | 5.4932 | -116.2949 | -116.4093 | -3.511 | -19.8898 | -7.7957 | 5.7037 | 5.6534 | -116.3361 | -116.2949 | 0 | -0.11444 | -0.19226 | 121.2158 | -0.31128 | -0.19684 | -0.51727 | -0.041199 | 0 | 0.01831 | 112.7838 | 108.4991 | 108.4991 | -0.032044 | 121.788 | 121.463 | 109.9457 | -122.0947 | 121.9986 | 121.9482 | 96.405 | -121.9803
4162.0156 | 122.0306 | -116.3177 | 5.6946 | -0.20615 | 0.013858 | 0.09239 | 3.1907 | 0.12779 | 0.0020593 | -0.0066501 | -0.084076 | -0.011049 | 0.069391 | 0.12298 | 3.0387 | -0.0042832 | 5.1041 | 4.866 | -6.4087 | -115.8096 | 5.484 | -116.2994 | -116.4368 | -3.5614 | -19.9722 | -7.7683 | 5.7129 | 5.6625 | -116.3361 | -116.2903 | 0.018311 | -0.11902 | -0.21057 | 121.1838 | 0.50812 | 0.62714 | -0.59051 | -0.018311 | 0.027466 | 0.018311 | 112.7563 | 108.5495 | 108.522 | -0.032043 | 121.8018 | 121.4218 | 109.9091 | -122.1313 | 122.0306 | 121.9803 | 96.3455 | -121.9849
4163.0156 | 122.0123 | -116.2582 | 5.6946 | -0.16037 | 0.019198 | 0.091963 | 3.1896 | 0.12886 | 0.0031273 | -0.0047275 | 0.053253 | -0.011262 | 0.067468 | 0.12213 | 3.0402 | -0.006633 | 5.1407 | 4.9255 | -6.3492 | -116.5787 | 5.4611 | -116.3315 | -116.4322 | -3.4332 | -20.0226 | -7.6904 | 5.7541 | 5.7083 | -116.3177 | -116.2857 | -0.073242 | -0.17395 | -0.23346 | 121.1838 | -0.32043 | -0.14648 | -0.55389 | -0.059509 | -0.027466 | 0.059509 | 112.825 | 108.5678 | 108.5953 | 0.013733 | 121.7194 | 121.3989 | 109.9091 | -122.1268 | 122.0123 | 121.9666 | 96.2357 | -121.9803
4164.0156 | 121.9894 | -116.2811 | 5.6671 | -0.17563 | 0.016421 | 0.093244 | 3.1901 | 0.12928 | 0.0033411 | -0.0049411 | -0.084076 | -0.011049 | 0.069605 | 0.12127 | 3.0372 | -0.0064194 | 5.0812 | 4.866 | -6.4178 | -123.3994 | 5.452 | -116.3269 | -116.4597 | -3.5614 | -19.9768 | -7.7545 | 5.6946 | 5.6351 | -116.3498 | -116.3132 | -0.045776 | -0.17853 | -0.21515 | 121.1472 | -7.1182 | -6.9397 | -0.58594 | -0.068664 | -0.032043 | 0.027466 | 112.7197 | 108.5266 | 108.5587 | -0.032043 | 121.7331 | 121.3623 | 109.8633 | -122.1268 | 121.9757 | 121.9162 | 96.3043 | -121.9803
4165.0156 | 122.0032 | -116.2903 | 5.6213 | -0.084076 | 0.018771 | 0.094099 | 3.2052 | 0.13121 | 0.0033411 | -0.0060093 | -0.10696 | -0.011476 | 0.069177 | 0.12255 | 3.0381 | -0.003856 | 5.2231 | 5.0812 | -6.2759 | -115.5579 | 5.5344 | -116.1667 | -116.3864 | -3.5522 | -20.0226 | -7.7591 | 5.6671 | 5.6122 | -116.3589 | -116.304 | 0.1236 | -0.096131 | -0.086975 | 121.3715 | 0.73242 | 0.82855 | -0.39825 | -0.068665 | -0.013733 | 0.045776 | 112.738 | 108.5312 | 108.5449 | -0.009155 | 121.8246 | 121.5134 | 110.0143 | -122.0078 | 121.9574 | 121.9025 | 96.2677 | -121.9254
4166.0156 | 121.9025 | -116.0248 | 5.9509 | -0.023041 | 0.017062 | 0.096449 | 3.4928 | 0.45036 | -0.00050425 | -0.0075047 | -0.023041 | -0.012117 | 0.067896 | 0.12341 | 3.0259 | -0.0036424 | 5.4932 | 5.2643 | -6.3492 | -119.632 | 5.8914 | -115.892 | -116.0065 | -3.6667 | -19.7937 | -8.0246 | 5.983 | 5.9189 | -116.066 | -116.011 | 0.13275 | 0.01831 | -0.05951 | 121.2891 | -3.6072 | -3.6255 | -0.45776 | -0.041199 | 0.013733 | 0.032043 | 112.3581 | 108.0002 | 107.9865 | -0.032044 | 121.9162 | 121.5179 | 109.6756 | -121.9574 | 122.0078 | 121.9437 | 96.2311 | -121.962
4167.0156 | 122.1359 | -1.1993 | 121.1472 | -0.50369 | 0.019412 | 0.0041634 | 0.014975 | 0.010937 | 0.0027001 | -0.0087863 | -0.0077819 | -0.0078442 | 0.082849 | 0.056544 | 0.04501 | -0.0089828 | -0.064087 | 0.045776 | 0.86975 | -1.6891 | 0.3479 | -2.1149 | -2.1973 | -0.027466 | 84.288 | -0.10071 | 120.7306 | 120.8725 | -1.6342 | -1.5335 | -0.91553 | -0.99792 | -120.7993 | 1.2451 | -0.48981 | 0.50812 | -121.2112 | -0.43487 | -0.33417 | -0.41656 | 1.1719 | 1.0986 | 1.4328 | -0.27466 | 1.5472 | 1.1353 | 2.0691 | -123.3444 | 121.9299 | 122.0718 | 85.4874 | -122.6807
4168.0156 | 122.1725 | -1.1124 | 121.0144 | -0.22141 | 0.013217 | 0.0048044 | 0.019248 | 0.0041016 | -0.0041357 | -0.0098545 | -0.076446 | -0.0086988 | 0.082422 | 0.055049 | 0.03967 | -0.0068466 | -0.022888 | 0.09613 | 0.73242 | -0.99335 | 0.29755 | -1.1581 | -1.3412 | -0.027466 | 84.3246 | -0.068665 | 121.1655 | 121.1197 | -1.3 | -1.2955 | -0.045776 | -0.22888 | -120.7169 | 1.2085 | 0.11902 | 0.3479 | -121.0373 | -0.18768 | -0.18311 | 0.15106 | 1.0849 | 1.0437 | 1.2268 | 0.10529 | 1.4099 | 1.0895 | 1.8448 | -122.3557 | 122.2778 | 122.2321 | 85.437 | -122.3099
4169.0156 | 122.2 | -1.1307 | 121.0831 | -0.16037 | 0.017062 | 0.0043772 | 0.018179 | 0.0038878 | -0.00029045 | -0.0096409 | -0.18326 | -0.0093396 | 0.080499 | 0.053767 | 0.040311 | -0.011546 | -0.064087 | -0.013733 | 0.68207 | -1.03 | 0.31586 | -1.181 | -1.387 | -0.064087 | 84.1187 | -0.11444 | 121.2021 | 121.1792 | -1.3138 | -1.3092 | -0.050354 | -0.25635 | -120.7672 | 1.1169 | 0.10071 | 0.35706 | -121.1472 | -0.18311 | -0.17853 | 0.11902 | 1.0666 | 1.0162 | 1.1948 | 0.09613 | 1.4465 | 1.0666 | 1.8127 | -122.4701 | 122.3328 | 122.3099 | 85.2493 | -122.3923
4170.0156 | 122.2321 | -1.0803 | 121.1563 | -0.23666 | 0.011294 | 0.005018 | 0.018607 | 0.004956 | -0.0047767 | -0.010709 | -0.068817 | -0.010408 | 0.080286 | 0.052912 | 0.038815 | -0.0089828 | -0.022888 | 0.073242 | 0.80566 | -0.91553 | 0.28839 | -1.1215 | -1.2909 | -0.041199 | 84.2377 | -0.10986 | 121.2891 | 121.2158 | -1.2405 | -1.2451 | -0.041199 | -0.21057 | -120.8679 | 1.1536 | 0.1648 | 0.37537 | -121.1792 | -0.16022 | -0.1648 | 0.13275 | 1.0391 | 0.97046 | 1.1353 | 0.059509 | 1.3687 | 1.0574 | 1.886 | -122.4472 | 122.3694 | 122.2961 | 85.318 | -122.4014
4171.0156 | 122.2687 | -1.0803 | 121.1884 | -0.16037 | 0.015994 | 0.0043772 | 0.020102 | 0.0062378 | -0.0013587 | -0.010282 | -0.16037 | -0.0078442 | 0.082849 | 0.052485 | 0.038388 | -0.012614 | -0.054932 | -0.018311 | 0.73242 | -0.94299 | 0.28839 | -1.1169 | -1.2817 | -0.059509 | 84.2194 | -0.1236 | 121.3486 | 121.2524 | -1.2497 | -1.236 | -0.036621 | -0.20142 | -120.9 | 1.062 | 0.13733 | 0.33875 | -121.2433 | -0.16937 | -0.15564 | 0.16022 | 1.0208 | 0.95673 | 1.1124 | 0.064087 | 1.3687 | 1.0254 | 1.8127 | -122.4701 | 122.4289 | 122.3328 | 85.2997 | -122.4243
4172.0156 | 122.2778 | -1.0391 | 121.2296 | -0.20615 | 0.011294 | 0.0048044 | 0.017325 | 0.0088012 | -0.0034949 | -0.0096409 | -0.13748 | -0.010194 | 0.081995 | 0.054621 | 0.037106 | -0.008342 | -0.004578 | 0.064087 | 0.83313 | -0.85602 | 0.28839 | -1.062 | -1.2314 | -0.041199 | 84.288 | -0.082397 | 121.3898 | 121.3303 | -1.2268 | -1.1902 | -0.022888 | -0.19226 | -120.9412 | 1.1032 | 0.18311 | 0.37537 | -121.2341 | -0.18768 | -0.15106 | 0.16022 | 0.99792 | 0.95673 | 1.1078 | 0.10071 | 1.3275 | 1.0345 | 1.8723 | -122.4609 | 122.4289 | 122.3694 | 85.3271 | -122.4197
4173.0156 | 122.2504 | -1.062 | 121.2708 | 0.022736 | 0.017489 | 0.0058724 | 0.020743 | 0.0075194 | 0.00056395 | -0.010922 | -0.18326 | -0.0097668 | 0.081995 | 0.05633 | 0.036252 | -0.0087692 | -0.073242 | -0.022888 | 0.75073 | -0.88348 | 0.34332 | -1.0712 | -1.2726 | -0.068665 | 84.4528 | -0.13733 | 121.4127 | 121.3257 | -1.236 | -1.236 | -0.009155 | -0.21057 | -120.9274 | 1.0391 | 0.17853 | 0.3891 | -121.344 | -0.17395 | -0.17395 | 0.14191 | 0.99335 | 0.92468 | 1.0986 | 0.054932 | 1.4053 | 0.98877 | 1.8127 | -122.5433 | 122.4747 | 122.3877 | 85.5148 | -122.5067
4174.0156 | 122.3785 | -1.0529 | 121.1975 | -0.19852 | 0.010013 | 0.0062998 | 0.017752 | 0.0051696 | -0.0045631 | -0.010282 | -0.091705 | -0.011262 | 0.078363 | 0.049281 | 0.03732 | -0.0085556 | 0.018311 | 0.14648 | 0.90637 | -0.81024 | 0.2655 | -1.0986 | -1.2863 | 0.013733 | 84.4894 | 0.064087 | 121.3028 | 121.2433 | -1.2497 | -1.2314 | -0.045777 | -0.23346 | -120.932 | 1.1993 | 0.24261 | 0.47607 | -121.1792 | -0.19684 | -0.17853 | 0.10529 | 1.0666 | 1.1169 | 1.2955 | 0.045776 | 1.3184 | 1.0712 | 1.9592 | -122.4838 | 122.3557 | 122.2961 | 85.5423 | -122.4289
4175.0156 | 122.1909 | -1.0437 | 121.312 | -0.22141 | 0.014712 | 0.0056588 | 0.020529 | 0.0058106 | -0.0017859 | -0.0094273 | -0.21378 | -0.0095532 | 0.081781 | 0.054194 | 0.037106 | -0.0089828 | -0.073242 | 0 | 0.78278 | -0.89722 | 0.31128 | -1.0986 | -1.3092 | -0.064087 | 84.5901 | -0.13275 | 121.4127 | 121.3623 | -1.236 | -1.2177 | -0.054932 | -0.2655 | -121.0007 | 1.0437 | 0.14648 | 0.41199 | -121.3852 | -0.19226 | -0.17395 | 0.10071 | 0.97961 | 0.91095 | 1.0849 | 0.050354 | 1.355 | 0.97046 | 1.8265 | -122.6212 | 122.4564 | 122.406 | 85.6338 | -122.5296
4176.0156 | 122.4243 | -1.0208 | 121.2433 | -0.11459 | 0.011722 | 0.006086 | 0.019248 | 0.0053832 | -0.0047767 | -0.010068 | 0.46524 | -0.010194 | 0.076441 | 0.053767 | 0.038174 | -0.0089828 | 0.032043 | 0.14191 | 0.91095 | -0.84686 | 0.27924 | -1.0712 | -1.268 | 0.050354 | 84.8145 | 0.004578 | 121.376 | 121.2982 | -1.2039 | -1.2039 | -0.050354 | -0.24719 | -120.9641 | 1.1627 | 0.17395 | 0.42114 | -121.2112 | -0.18311 | -0.18311 | 0.13275 | 1.0712 | 1.0254 | 1.2085 | 0.054932 | 1.3 | 1.0529 | 1.9318 | -122.5113 | 122.3969 | 122.319 | 85.8353 | -122.4472
4177.0156 | 122.2961 | -1.0712 | 121.2799 | -0.28244 | 0.012362 | 0.0075814 | 0.019034 | 0.0068786 | 0.0014185 | -0.010495 | -0.26718 | -0.0078442 | 0.082636 | 0.052485 | 0.039029 | -0.0091966 | -0.082397 | -0.009155 | 0.77362 | -0.94299 | 0.29755 | -1.1536 | -1.3412 | -0.004578 | 84.4849 | -0.091553 | 121.4584 | 121.3486 | -1.236 | -1.2268 | -0.082397 | -0.27008 | -120.9824 | 1.062 | 0.12817 | 0.39826 | -121.3623 | -0.1648 | -0.15564 | 0.17853 | 1.0666 | 0.97961 | 1.1353 | 0.068665 | 1.3687 | 0.98877 | 1.8448 | -122.6212 | 122.5296 | 122.4197 | 85.556 | -122.5067
4178.0156 | 122.3282 | -0.99792 | 121.344 | -0.15274 | 0.020267 | 0.0030954 | 0.021384 | 0.0077332 | 0.00099115 | -0.0072911 | -0.18326 | -0.0097668 | 0.081995 | 0.054835 | 0.042233 | -0.010265 | -0.009155 | 0.041199 | 0.82398 | -0.91095 | 0.3067 | -1.1124 | -1.2817 | -0.004578 | 84.7641 | -0.13275 | 121.4172 | 121.3989 | -1.2085 | -1.1856 | -0.11444 | -0.28381 | -121.0373 | 1.0391 | 0.086975 | 0.37079 | -121.3531 | -0.21057 | -0.18768 | 0.073242 | 0.99335 | 0.86517 | 1.0529 | 0.054932 | 1.3046 | 0.98877 | 1.8219 | -122.6257 | 122.4152 | 122.3969 | 85.762 | -122.5296
4179.0156 | 122.3236 | -1.0666 | 121.2936 | -0.22903 | 0.013217 | 0.0024544 | 0.018393 | 0.0062378 | -0.0037085 | -0.0092137 | -0.2214 | -0.0097668 | 0.080927 | 0.055049 | 0.039456 | -0.0094102 | -0.041199 | 0.059509 | 0.86517 | -0.92926 | 0.28839 | -1.0986 | -1.2772 | -0.041199 | 84.8053 | -0.1236 | 121.4081 | 121.3669 | -1.2451 | -1.236 | -0.032044 | -0.21057 | -121.0052 | 1.1261 | 0.13733 | 0.3479 | -121.3348 | -0.17853 | -0.16937 | 0.11444 | 1.0254 | 0.94299 | 1.1124 | 0.073242 | 1.355 | 1.0254 | 1.9318 | -122.5708 | 122.4747 | 122.4335 | 85.8719 | -122.5296
4180.0156 | 122.4884 | -1.0117 | 121.2936 | -0.061188 | 0.0089443 | 0.0056588 | 0.020102 | 0.006665 | -0.0049903 | -0.0075047 | -0.12985 | -0.010408 | 0.079859 | 0.053553 | 0.038388 | -0.0096238 | -0.004578 | 0.16022 | 0.94299 | -0.86975 | 0.27924 | -1.0849 | -1.2497 | 0.086975 | 85.0159 | 0.032043 | 121.3989 | 121.3028 | -1.2268 | -1.2131 | -0.073242 | -0.23804 | -121.0144 | 1.1719 | 0.14191 | 0.37994 | -121.2982 | -0.21515 | -0.20142 | 0.10529 | 1.0986 | 1.0437 | 1.2451 | 0.009155 | 1.2909 | 1.0071 | 1.9547 | -122.5433 | 122.4106 | 122.3145 | 86.0275 | -122.5067
4181.0156 | 122.438 | -1.0208 | 121.2799 | -0.19852 | 0.0080899 | 0.0048044 | 0.020316 | 0.0068786 | -0.0043495 | -0.01434 | -0.41214 | -0.0099806 | 0.08114 | 0.053767 | 0.038174 | -0.011974 | 0.068665 | 0.059509 | 0.80566 | -0.97046 | 0.25635 | -1.0986 | -1.2909 | 0.064087 | 85.0571 | -0.009155 | 121.4355 | 121.312 | -1.2131 | -1.181 | -0.07782 | -0.27008 | -121.0236 | 1.0803 | 0.050354 | 0.32044 | -121.2112 | -0.19226 | -0.16022 | 0.15564 | 1.0849 | 1.0117 | 1.1719 | 0.032044 | 1.2772 | 1.0895 | 1.8265 | -122.5708 | 122.4564 | 122.3328 | 86.0779 | -122.4609
4182.0156 | 122.4335 | -1.0345 | 121.3028 | -0.076447 | 0.011294 | 0.006086 | 0.017966 | 0.008374 | -0.0045631 | -0.010922 | 0.030365 | -0.010835 | 0.080286 | 0.055689 | 0.038815 | -0.010265 | -0.059509 | 0.054932 | 0.87433 | -0.89722 | 0.27008 | -1.0941 | -1.268 | 0.013733 | 85.0159 | -0.004578 | 121.4355 | 121.3623 | -1.2131 | -1.1993 | -0.059509 | -0.23346 | -121.0327 | 1.0895 | 0.13733 | 0.37079 | -121.3623 | -0.17853 | -0.1648 | 0.13275 | 1.0483 | 1.03 | 1.1948 | 0.05951 | 1.3046 | 0.97504 | 1.9089 | -122.5708 | 122.4701 | 122.3969 | 86.0504 | -122.5021
4183.0156 | 122.3877 | -1.062 | 121.3486 | -0.20615 | 0.01578 | 0.0045908 | 0.023306 | 0.0070922 | 0.0039819 | -0.0094273 | -0.24429 | -0.0089124 | 0.084558 | 0.056544 | 0.038388 | -0.013042 | -0.032043 | -0.004578 | 0.82398 | -0.77362 | 0.29755 | -1.0941 | -1.2909 | 0.004578 | 85.0021 | -0.11902 | 121.5088 | 121.3943 | -1.236 | -1.2268 | -0.032043 | -0.22888 | -121.051 | 1.0574 | 0.28839 | 0.51727 | -121.3806 | -0.17395 | -0.1648 | 0.16022 | 1.0666 | 0.94299 | 1.1078 | 0.045776 | 1.3596 | 1.03 | 1.886 | -122.6395 | 122.5708 | 122.4564 | 86.0641 | -122.5754
4184.0156 | 122.4747 | -1.0162 | 121.3257 | -0.091705 | 0.011508 | 0.0056588 | 0.019034 | 0.0070922 | -0.0056311 | -0.0098545 | -0.023041 | -0.0089124 | 0.077936 | 0.05633 | 0.036893 | -0.0089828 | 0.004578 | 0.13733 | 0.94757 | -0.6958 | 0.28381 | -1.0345 | -1.2177 | 0.07782 | 85.0296 | 0.027466 | 121.463 | 121.3715 | -1.181 | -1.1627 | -0.018311 | -0.20142 | -121.0419 | 1.1536 | 0.32043 | 0.52185 | -121.3211 | -0.1648 | -0.14648 | 0.13733 | 1.0941 | 1.0437 | 1.1902 | 0.045776 | 1.3 | 1.0208 | 1.9638 | -122.5433 | 122.4792 | 122.3877 | 86.0458 | -122.4884
4185.0156 | 122.4426 | -1.0208 | 121.3028 | -0.17563 | 0.010653 | 0.0048044 | 0.018393 | 0.0064514 | -0.0024269 | -0.010068 | -0.2214 | -0.010621 | 0.08114 | 0.05334 | 0.038815 | -0.010905 | 0.022888 | 0.11444 | 0.9201 | -0.79193 | 0.27924 | -1.0895 | -1.2543 | 0.041199 | 85.0983 | -0.041199 | 121.4584 | 121.3669 | -1.2039 | -1.2222 | -0.068665 | -0.23346 | -121.0236 | 1.1353 | 0.22888 | 0.46234 | -121.2799 | -0.18311 | -0.20142 | 0.15564 | 1.062 | 0.97961 | 1.181 | 0.064087 | 1.3 | 1.0437 | 1.9409 | -122.5571 | 122.4792 | 122.3877 | 86.1191 | -122.525
4186.0156 | 122.4701 | -1.03 | 121.3303 | -0.0383 | 0.013217 | 0.0062998 | 0.018179 | 0.0077332 | -0.0049903 | -0.01135 | -0.023041 | -0.011049 | 0.077936 | 0.052912 | 0.039029 | -0.0077012 | -0.004578 | 0.07782 | 0.91553 | -0.78278 | 0.27466 | -1.0849 | -1.268 | 0.059509 | 85.1212 | 0.009155 | 121.4813 | 121.3577 | -1.1719 | -1.181 | -0.054932 | -0.23804 | -121.0556 | 1.1078 | 0.24719 | 0.48523 | -121.3348 | -0.14191 | -0.15106 | 0.15106 | 1.0895 | 1.0391 | 1.1902 | 0.027466 | 1.3046 | 1.0254 | 1.9455 | -122.5983 | 122.5113 | 122.3877 | 86.1511 | -122.5113
4187.0156 | 122.4518 | -1.0345 | 121.3257 | -0.16037 | 0.011081 | 0.0052316 | 0.020102 | 0.0047424 | -0.0026405 | -0.015836 | -0.2977 | -0.0076306 | 0.080072 | 0.054835 | 0.039456 | -0.010905 | 0.15564 | -0.041199 | 0.78278 | -0.78278 | 0.25635 | -1.0803 | -1.2634 | 0.050354 | 85.1257 | 0 | 121.4401 | 121.3623 | -1.2085 | -1.1719 | -0.045776 | -0.22888 | -121.0693 | 0.99335 | 0.25177 | 0.48065 | -121.17 | -0.17395 | -0.13733 | 0.11444 | 1.0849 | 1.0345 | 1.1719 | 0.036621 | 1.2909 | 1.1902 | 1.8173 | -122.5891 | 122.4747 | 122.3969 | 86.1603 | -122.4976
4188.0156 | 122.4884 | -1.0391 | 121.344 | -0.15274 | 0.012576 | 0.0058724 | 0.019888 | 0.0068786 | -0.00093145 | -0.010922 | -0.19089 | -0.0099806 | 0.080927 | 0.057185 | 0.038815 | -0.012187 | 0.022888 | 0.12817 | 0.92926 | -0.71869 | 0.27924 | -1.0666 | -1.2543 | 0.059509 | 85.1074 | -0.027466 | 121.4951 | 121.3486 | -1.2085 | -1.2131 | -0.027465 | -0.21515 | -121.0648 | 1.1673 | 0.32043 | 0.53558 | -121.3211 | -0.16937 | -0.17395 | 0.15106 | 1.0986 | 1.0117 | 1.1856 | 0.004578 | 1.3184 | 1.062 | 1.9684 | -122.5983 | 122.5342 | 122.3877 | 86.1465 | -122.5571
4189.0156 | 122.5342 | -1.0529 | 121.3531 | -0.015411 | 0.0095853 | 0.006086 | 0.018393 | 0.0023926 | -0.0030677 | -0.010495 | -0.053558 | -0.010194 | 0.079004 | 0.055903 | 0.038815 | -0.010905 | -0.018311 | 0.09613 | 0.92926 | -0.75531 | 0.29297 | -1.0941 | -1.2634 | 0.064087 | 85.1349 | 0 | 121.4676 | 121.3669 | -1.2085 | -1.2131 | -0.041199 | -0.21057 | -121.0602 | 1.149 | 0.29755 | 0.50812 | -121.3715 | -0.15564 | -0.16022 | 0.11444 | 1.1169 | 1.0529 | 1.2131 | 0.013733 | 1.3458 | 1.0345 | 1.9821 | -122.6166 | 122.5204 | 122.4197 | 86.1877 | -122.5662
4190.0156 | 122.4701 | -1.0941 | 121.3577 | -0.0077822 | 0.012149 | 0.0035226 | 0.01882 | 0.0060242 | -0.0019995 | -0.0098545 | 0.076141 | -0.013185 | 0.077509 | 0.057398 | 0.039456 | -0.0085556 | -0.018311 | 0.041199 | 0.87891 | -0.75989 | 0.27466 | -1.0757 | -1.268 | 0.036621 | 85.0662 | -0.054932 | 121.4447 | 121.344 | -1.268 | -1.2634 | 0.01831 | -0.17395 | -121.0831 | 1.1353 | 0.33417 | 0.50812 | -121.376 | -0.17395 | -0.16937 | 0.086975 | 1.1307 | 1.0391 | 1.2085 | -0.013733 | 1.3687 | 1.0757 | 1.973 | -122.6257 | 122.5388 | 122.438 | 86.1603 | -122.6212
4191.0156 | 122.4976 | -1.062 | 121.3348 | -0.12985 | 0.010226 | 0.0071542 | 0.018393 | 0.004956 | 0.00013675 | -0.0098545 | -0.19089 | -0.0084852 | 0.081995 | 0.054408 | 0.038174 | -0.010692 | 0.050354 | 0.16022 | 0.94757 | -0.70496 | 0.27466 | -1.0803 | -1.2634 | 0.050354 | 85.4645 | -0.013733 | 121.4905 | 121.3531 | -1.2405 | -1.2268 | -0.01831 | -0.20142 | -121.0602 | 1.2222 | 0.35706 | 0.55847 | -121.2845 | -0.17853 | -0.1648 | 0.15564 | 1.1124 | 1.0483 | 1.2131 | 0.01831 | 1.3367 | 1.1124 | 2.0096 | -122.5983 | 122.5525 | 122.4152 | 86.5265 | -122.5616
4192.0156 | 122.4655 | -1.0483 | 121.344 | 0.022736 | 0.011294 | 0.0075814 | 0.019675 | 0.0028198 | -0.0017859 | -0.0096409 | -0.10696 | -0.0099806 | 0.079218 | 0.055262 | 0.039456 | -0.0098374 | -0.032043 | 0.068665 | 0.75989 | -0.8606 | 0.24261 | -1.1398 | -1.3275 | 0.032043 | 85.1669 | -0.032043 | 121.4951 | 121.3989 | -1.2314 | -1.2222 | -0.091553 | -0.27924 | -121.1014 | 1.1169 | 0.18768 | 0.46692 | -121.376 | -0.18311 | -0.17395 | 0.15106 | 1.0803 | 1.0162 | 1.1902 | 0.054932 | 1.2909 | 1.0162 | 1.8082 | -122.6715 | 122.5433 | 122.4472 | 86.2152 | -122.5662
4193.0156 | 122.4014 | -1.0712 | 121.3623 | -0.023041 | 0.018344 | -0.0033134 | 0.020956 | 0.0047424 | 0.0071863 | -0.0055821 | -0.099335 | -0.0095532 | 0.082208 | 0.054408 | 0.042447 | -0.013042 | 0.018311 | 0.004578 | 0.8606 | -0.79651 | 0.29297 | -1.1353 | -1.2909 | 0 | 85.0983 | -0.16937 | 121.5408 | 121.3989 | -1.2726 | -1.2497 | -0.064087 | -0.21973 | -121.0693 | 1.0757 | 0.27466 | 0.49438 | -121.344 | -0.20142 | -0.17853 | 0.17853 | 1.0712 | 0.90179 | 1.0803 | 0.036621 | 1.3641 | 1.0895 | 1.9318 | -122.6532 | 122.612 | 122.4701 | 86.1694 | -122.612
4194.0156 | 122.493 | -1.0574 | 121.3486 | 0.14481 | 0.011294 | 0.0054452 | 0.01882 | 0.006665 | -0.00029045 | -0.0092137 | 0.17532 | -0.0078442 | 0.080713 | 0.052912 | 0.037747 | -0.0091966 | -0.004578 | 0.073242 | 0.94299 | -0.70953 | 0.28839 | -1.0574 | -1.236 | 0.050354 | 85.1852 | -0.032043 | 121.4996 | 121.4355 | -1.2268 | -1.2177 | 0 | -0.17853 | -121.0602 | 1.1307 | 0.3479 | 0.52643 | -121.3531 | -0.16937 | -0.16022 | 0.15106 | 1.1078 | 1.0254 | 1.1856 | 0.086975 | 1.3458 | 1.0529 | 2.0004 | -122.5845 | 122.5571 | 122.493 | 86.2427 | -122.5662
4195.0156 | 122.5113 | -1.0757 | 121.3348 | 0.053253 | 0.0095853 | 0.006727 | 0.015616 | 0.006665 | -0.00050425 | -0.010068 | 0.053253 | -0.0069898 | 0.080072 | 0.051417 | 0.041592 | -0.0085556 | -0.022888 | 0.054932 | 0.91095 | -0.69122 | 0.28839 | -1.0712 | -1.2589 | -0.041199 | 85.2905 | -0.050354 | 121.4905 | 121.3943 | -1.268 | -1.2497 | 0.004578 | -0.18311 | -121.0464 | 1.1307 | 0.38452 | 0.56763 | -121.3577 | -0.19226 | -0.17395 | 0.15564 | 1.0345 | 1.0254 | 1.1993 | 0.059509 | 1.3641 | 1.0529 | 1.9867 | -122.5937 | 122.5662 | 122.4701 | 86.3663 | -122.5845
4196.0156 | 122.5067 | -1.0254 | 121.4172 | 0.10666 | 0.013217 | 0.0062998 | 0.018179 | 0.0060242 | 0.00099115 | -0.0083591 | 0.17532 | -0.0076306 | 0.07879 | 0.052485 | 0.039029 | -0.0077012 | 0.045776 | 0.086975 | 0.94757 | -0.69122 | 0.28381 | -1.062 | -1.2314 | 0.07782 | 85.2402 | -0.018311 | 121.5317 | 121.4264 | -1.1993 | -1.1856 | -0.036621 | -0.20599 | -121.1334 | 1.1124 | 0.33417 | 0.54016 | -121.3715 | -0.17395 | -0.16022 | 0.11444 | 1.1032 | 1.0071 | 1.1673 | 0.009156 | 1.3092 | 1.0712 | 1.973 | -122.6486 | 122.5571 | 122.4518 | 86.2656 | -122.6028
4197.0156 | 122.5159 | -1.0437 | 121.3898 | 0.060882 | 0.010867 | 0.007795 | 0.019888 | 0.004956 | 0.0014185 | -0.0081455 | -0.19089 | -0.007417 | 0.080713 | 0.052058 | 0.037961 | -0.0081284 | -0.073242 | -0.07782 | 0.79651 | -0.78278 | 0.23346 | -1.1444 | -1.3321 | 0.027466 | 85.1349 | -0.022888 | 121.5225 | 121.4218 | -1.2268 | -1.2177 | -0.10071 | -0.28839 | -121.1563 | 0.96588 | 0.26092 | 0.54932 | -121.463 | -0.18311 | -0.17395 | 0.13275 | 1.0712 | 1.0208 | 1.1948 | 0.032043 | 1.2772 | 0.97046 | 1.8402 | -122.7219 | 122.5662 | 122.4655 | 86.1786 | -122.6074
4198.0156 | 122.5479 | -1.03 | 121.3943 | -0.15274 | 0.010867 | 0.006086 | 0.01882 | 0.0064514 | -0.00093145 | -0.0098545 | -0.168 | -0.0093396 | 0.080927 | 0.052485 | 0.039456 | -0.010905 | 0.064087 | 0.15564 | 0.94757 | -0.63171 | 0.27008 | -1.062 | -1.2451 | 0.045776 | 85.2722 | 0.022888 | 121.55 | 121.431 | -1.2268 | -1.181 | -0.032044 | -0.21515 | -121.1243 | 1.1856 | 0.39825 | 0.6134 | -121.3303 | -0.19684 | -0.15106 | 0.15564 | 1.0757 | 1.0529 | 1.2039 | 0.036621 | 1.3 | 1.0941 | 1.9775 | -122.6395 | 122.58 | 122.4609 | 86.3022 | -122.5754
4199.0156 | 122.5159 | -1.03 | 121.431 | 0.48813 | 0.012362 | 0.0048044 | 0.019248 | 0.0047424 | -0.0019995 | -0.010495 | 0.037995 | -0.011262 | 0.077082 | 0.055903 | 0.038815 | -0.0079148 | -0.027466 | 0.045776 | 0.88348 | -0.70038 | 0.23804 | -1.1078 | -1.268 | 0.045776 | 85.1303 | -0.018311 | 121.582 | 121.4584 | -1.1902 | -1.1948 | -0.07782 | -0.23804 | -121.1929 | 1.0757 | 0.32959 | 0.56763 | -121.4584 | -0.16022 | -0.1648 | 0.15106 | 1.0757 | 1.0117 | 1.1765 | 0.027466 | 1.268 | 1.0025 | 1.9135 | -122.699 | 122.612 | 122.4884 | 86.1603 | -122.6257
4200.0156 | 122.5296 | -1.0895 | 121.3257 | 0.16006 | 0.015567 | 0.0039498 | 0.017752 | 0.0068786 | 0.0020593 | -0.010282 | 0.10666 | -0.010835 | 0.082636 | 0.054835 | 0.040738 | -0.0098374 | 0.050354 | 0.07782 | 0.91095 | -0.68665 | 0.24719 | -1.1444 | -1.3412 | 0.10986 | 85.1395 | -0.018311 | 121.5179 | 121.3715 | -1.2589 | -1.2314 | -0.054931 | -0.25177 | -121.0785 | 1.1673 | 0.40283 | 0.6546 | -121.2753 | -0.16937 | -0.14191 | 0.19226 | 1.1993 | 1.0712 | 1.2131 | 0.045776 | 1.3367 | 1.1398 | 2.0004 | -122.6669 | 122.6074 | 122.4609 | 86.2289 | -122.5571
4201.0156 | 122.5479 | -1.0941 | 121.3943 | 0.099029 | 0.0091581 | 0.0080086 | 0.01882 | 0.0058106 | -0.0013587 | -0.010495 | 0.083771 | -0.0076306 | 0.080072 | 0.055476 | 0.040311 | -0.010265 | -0.004578 | 0.054932 | 0.90179 | -0.69122 | 0.28381 | -1.0666 | -1.2497 | 0.050354 | 85.0067 | -0.21515 | 121.4767 | 121.3715 | -1.2497 | -1.2405 | 0.027466 | -0.15564 | -121.1105 | 1.149 | 0.40283 | 0.55847 | -121.3989 | -0.15564 | -0.14648 | 0.082398 | 1.1444 | 0.87891 | 1.0254 | -0.022888 | 1.3779 | 1.0895 | 1.9958 | -122.644 | 122.5708 | 122.4655 | 86.1008 | -122.6349
4202.0156 | 122.5662 | -1.0254 | 121.4218 | 0.18295 | 0.019412 | 0.0048044 | 0.019461 | 0.0073058 | 0.0029137 | -0.0094273 | 0.068512 | -0.0089124 | 0.082636 | 0.054408 | 0.04202 | -0.010905 | 0.018311 | 0.032043 | 0.87433 | -0.72784 | 0.27924 | -1.0757 | -1.2634 | 0.073242 | 85.2081 | -0.045776 | 121.5729 | 121.4355 | -1.2039 | -1.2039 | -0.050354 | -0.23804 | -121.1426 | 1.0574 | 0.29755 | 0.53558 | -121.4035 | -0.17853 | -0.17853 | 0.15106 | 1.0986 | 0.97961 | 1.1581 | 0.013733 | 1.3046 | 1.0437 | 1.8997 | -122.6852 | 122.5983 | 122.4609 | 86.2335 | -122.6257
4203.0156 | 122.525 | -1.062 | 121.3989 | 0.18295 | 0.011722 | 0.0043772 | 0.017539 | 0.0081604 | -0.0015723 | -0.0083591 | 0.12955 | -0.0078442 | 0.079859 | 0.05398 | 0.041806 | -0.0074876 | 0.018311 | 0.068665 | 0.9201 | -0.84228 | 0.27466 | -1.0941 | -1.2451 | 0.045776 | 85.1486 | -0.041199 | 121.5363 | 121.431 | -1.2314 | -1.2177 | -0.032043 | -0.18311 | -121.1243 | 1.1307 | 0.21973 | 0.40283 | -121.3806 | -0.16937 | -0.15564 | 0.13733 | 1.1078 | 1.0208 | 1.1765 | 0.032043 | 1.3367 | 1.0803 | 1.9821 | -122.644 | 122.5983 | 122.493 | 86.2106 | -122.6166
4204.0156 | 122.5159 | -1.0849 | 121.3348 | 0.16769 | 0.016849 | 0.0039498 | 0.020529 | 0.0075194 | 0.0037683 | -0.0070773 | 0.16006 | -0.0078442 | 0.082208 | 0.05398 | 0.041379 | -0.010905 | 0.054932 | 0.082397 | 0.92926 | -0.78735 | 0.25177 | -1.0986 | -1.2817 | 0.086975 | 85.231 | -0.041199 | 121.5088 | 121.3943 | -1.2222 | -1.2222 | -0.013733 | -0.19684 | -121.0831 | 1.1673 | 0.29755 | 0.49438 | -121.2799 | -0.13733 | -0.13733 | 0.17395 | 1.1719 | 1.0437 | 1.181 | 0.059509 | 1.3367 | 1.1398 | 2.0142 | -122.6166 | 122.5937 | 122.4792 | 86.3159 | -122.5571
4205.0156 | 122.5342 | -1.0895 | 121.376 | 0.083771 | 0.012576 | 0.0043772 | 0.017752 | 0.0038878 | -0.0013587 | -0.0077183 | 0.0914 | -0.0089124 | 0.08114 | 0.052699 | 0.039243 | -0.0098374 | -0.009155 | 0.045776 | 0.92468 | -0.80109 | 0.27466 | -1.0483 | -1.2314 | 0.045776 | 85.2814 | -0.027466 | 121.5683 | 121.4722 | -1.2268 | -1.2268 | 0.041199 | -0.14191 | -121.1014 | 1.1353 | 0.28839 | 0.4303 | -121.3852 | -0.13733 | -0.13733 | 0.19226 | 1.1353 | 1.062 | 1.1993 | 0.09613 | 1.3641 | 1.0803 | 2.0142 | -122.6074 | 122.6578 | 122.5616 | 86.3709 | -122.6028
4206.0156 | 122.5983 | -1.0483 | 121.3989 | 0.13718 | 0.01813 | 0.003309 | 0.017111 | 0.008374 | 0.0014185 | -0.0049411 | 0.38132 | -0.0065626 | 0.082849 | 0.055476 | 0.043515 | -0.0098374 | -0.20599 | 0.10986 | 0.98877 | -0.75073 | 0.21515 | -1.1307 | -1.3092 | 0.07782 | 85.2814 | -0.027466 | 121.5637 | 121.4584 | -1.2131 | -1.2085 | -0.082397 | -0.26093 | -121.1838 | 1.1581 | 0.29755 | 0.55847 | -121.6049 | -0.1648 | -0.16022 | 0.16479 | 1.1261 | 1.0208 | 1.181 | 0.059509 | 1.2634 | 0.84228 | 2.037 | -122.7081 | 122.612 | 122.5067 | 86.3297 | -122.6074
4207.0156 | 122.5342 | -1.0574 | 121.4127 | 0.11429 | 0.011722 | 0.0075814 | 0.019461 | 0.0053832 | -0.00029045 | -0.0077183 | 0.12192 | -0.0099806 | 0.080499 | 0.055049 | 0.040952 | -0.0091966 | 0.022888 | 0.068665 | 0.93842 | -0.75073 | 0.28381 | -1.0803 | -1.2543 | 0.032043 | 85.2493 | -0.032043 | 121.5591 | 121.4951 | -1.1948 | -1.2039 | -0.022888 | -0.19684 | -121.1288 | 1.1261 | 0.3067 | 0.50354 | -121.3898 | -0.13733 | -0.14648 | 0.14648 | 1.0895 | 1.0254 | 1.1719 | 0.082397 | 1.3412 | 1.0803 | 1.9958 | -122.6669 | 122.6166 | 122.5525 | 86.3068 | -122.6166
4208.0156 | 122.5296 | -1.0757 | 121.3348 | 0.19058 | 0.020267 | 0.0058724 | 0.018393 | 0.0075194 | 0.0037683 | -0.0089999 | 0.11429 | -0.0059216 | 0.082422 | 0.055689 | 0.042874 | -0.011119 | -0.018311 | -0.004578 | 0.83771 | -0.79651 | 0.29755 | -1.1261 | -1.3 | 0.027466 | 85.2264 | -0.09613 | 121.5866 | 121.4722 | -1.236 | -1.2177 | -0.050354 | -0.2243 | -121.0373 | 1.0712 | 0.27924 | 0.50354 | -121.3531 | -0.16022 | -0.14191 | 0.25177 | 1.1032 | 0.97961 | 1.1215 | 0.13733 | 1.3733 | 1.0574 | 1.9135 | -122.6349 | 122.6624 | 122.5479 | 86.3022 | -122.5525
4209.0156 | 122.5571 | -1.0483 | 121.4355 | 0.15244 | 0.012149 | 0.0048044 | 0.015616 | 0.006665 | -0.00029045 | -0.0085727 | 0.16769 | -0.0084852 | 0.081354 | 0.054621 | 0.03967 | -0.0077012 | 0.027466 | 0.10071 | 0.9613 | -0.74158 | 0.26093 | -1.062 | -1.2543 | 0.07782 | 85.2951 | -0.036621 | 121.5866 | 121.4951 | -1.2085 | -1.2039 | -0.013733 | -0.20599 | -121.1746 | 1.149 | 0.3067 | 0.5127 | -121.4081 | -0.16022 | -0.15564 | 0.15106 | 1.1261 | 1.0117 | 1.1673 | 0.059509 | 1.3092 | 1.0757 | 2.0096 | -122.6898 | 122.6349 | 122.5433 | 86.3434 | -122.6395
4210.0156 | 122.6074 | -1.062 | 121.3806 | 0.23636 | 0.016849 | 0.0043772 | 0.020956 | 0.0055968 | 0.00035035 | -0.0066501 | 0.30502 | -0.007417 | 0.081995 | 0.052485 | 0.043088 | -0.011333 | 0.022888 | 0.041199 | 0.89722 | -0.82398 | 0.2655 | -1.1078 | -1.2817 | 0.073242 | 85.2493 | -0.032043 | 121.582 | 121.4493 | -1.2177 | -1.2222 | -0.045776 | -0.21973 | -121.1151 | 1.1032 | 0.23804 | 0.45776 | -121.3577 | -0.15564 | -0.16022 | 0.20142 | 1.1353 | 1.03 | 1.1902 | 0.068665 | 1.3275 | 1.0849 | 1.9592 | -122.6624 | 122.644 | 122.5113 | 86.3113 | -122.6028
4211.0156 | 122.58 | -1.0391 | 121.4218 | 0.18295 | 0.014071 | 0.0045908 | 0.018393 | 0.0068786 | 0.00056395 | -0.0062229 | 0.18295 | -0.0067762 | 0.080286 | 0.054621 | 0.039456 | -0.010478 | 0.036621 | 0.10071 | 0.94299 | -0.77362 | 0.26093 | -1.0941 | -1.268 | 0.086975 | 85.2905 | -0.022888 | 121.5683 | 121.4813 | -1.2177 | -1.1993 | -0.054931 | -0.22888 | -121.1609 | 1.1398 | 0.2655 | 0.49438 | -121.3852 | -0.17853 | -0.16022 | 0.14648 | 1.1261 | 1.0162 | 1.1765 | 0.059509 | 1.3 | 1.0757 | 1.9821 | -122.6898 | 122.6074 | 122.5204 | 86.3297 | -122.6212
4212.0156 | 122.58 | -1.0941 | 121.3989 | -0.091705 | 0.018558 | 0.006086 | 0.01647 | 0.0062378 | 0.00056395 | -0.0092137 | 0.16769 | -0.007417 | 0.082849 | 0.053553 | 0.045224 | -0.010051 | 0.050354 | 0.086975 | 0.94299 | -0.81024 | 0.2655 | -1.0941 | -1.268 | -0.050354 | 85.4782 | -0.004578 | 121.55 | 121.4447 | -1.2817 | -1.2543 | 0 | -0.17395 | -121.1334 | 1.181 | 0.28381 | 0.45776 | -121.3486 | -0.18768 | -0.16022 | 0.15106 | 1.0437 | 1.0895 | 1.2497 | 0.045776 | 1.3596 | 1.1444 | 2.037 | -122.6669 | 122.644 | 122.5388 | 86.5723 | -122.6532
4213.0156 | 122.5845 | -1.0529 | 121.4401 | 0.15244 | 0.012149 | 0.006086 | 0.017325 | 0.0070922 | -0.0019995 | -0.0083591 | 0.19821 | -0.0086988 | 0.082849 | 0.05398 | 0.041592 | -0.0068466 | 0.050354 | 0.07782 | 0.95673 | -0.86975 | 0.27924 | -1.0895 | -1.2634 | 0.050354 | 85.2585 | -0.032043 | 121.5912 | 121.5042 | -1.2222 | -1.2314 | -0.036622 | -0.21057 | -121.1609 | 1.1307 | 0.1831 | 0.39368 | -121.3898 | -0.16937 | -0.17853 | 0.15106 | 1.1032 | 1.0208 | 1.1993 | 0.064086 | 1.3321 | 1.1032 | 2.0096 | -122.7036 | 122.644 | 122.5571 | 86.3113 | -122.6715
4214.0156 | 122.6303 | -1.0574 | 121.4355 | 0.19058 | 0.017703 | 0.0065134 | 0.019461 | 0.0077332 | 0.0012047 | -0.0062229 | 0.083771 | -0.008058 | 0.082849 | 0.053553 | 0.04266 | -0.010692 | 0.032043 | 0.059509 | 0.9201 | -0.86517 | 0.2655 | -1.1124 | -1.2955 | 0.068665 | 85.3088 | -0.041199 | 121.5866 | 121.4676 | -1.236 | -1.2314 | -0.054932 | -0.23804 | -121.17 | 1.1169 | 0.19226 | 0.4303 | -121.4035 | -0.17853 | -0.17395 | 0.15106 | 1.1261 | 1.0162 | 1.1902 | 0.032043 | 1.3229 | 1.0895 | 1.9775 | -122.731 | 122.644 | 122.525 | 86.3663 | -122.6669
4215.0156 | 122.5525 | -1.062 | 121.4401 | 0.13718 | 0.013217 | 0.0058724 | 0.016043 | 0.0060242 | -0.0028541 | -0.0089999 | 0.19821 | -0.0089124 | 0.081781 | 0.054194 | 0.041592 | -0.0081284 | 0.022888 | 0.086975 | 0.9613 | -0.80109 | 0.2655 | -1.0941 | -1.2817 | 0.082397 | 85.2402 | -0.009155 | 121.5729 | 121.5042 | -1.2497 | -1.2131 | -0.032043 | -0.21973 | -121.1746 | 1.149 | 0.26093 | 0.48065 | -121.4172 | -0.18768 | -0.15106 | 0.13275 | 1.1444 | 1.0529 | 1.2039 | 0.064086 | 1.3275 | 1.0849 | 2.0233 | -122.7219 | 122.6349 | 122.5662 | 86.3022 | -122.6532
4216.0156 | 122.5159 | -1.1032 | 121.4401 | 0.13718 | 0.017276 | 0.0043772 | 0.020956 | 0.0068786 | 0.0014185 | -0.0081455 | 0.0914 | -0.0072034 | 0.084345 | 0.054408 | 0.041592 | -0.010051 | -0.036621 | -0.050354 | 0.83771 | -0.88348 | 0.29755 | -1.1353 | -1.3275 | -0.004578 | 85.1807 | -0.13275 | 121.6187 | 121.5454 | -1.2726 | -1.2589 | -0.032044 | -0.2243 | -121.1426 | 1.0529 | 0.21973 | 0.44403 | -121.4767 | -0.16937 | -0.15564 | 0.17853 | 1.0986 | 0.97046 | 1.1261 | 0.10529 | 1.4008 | 1.0666 | 1.9409 | -122.7676 | 122.7219 | 122.6486 | 86.2839 | -122.699
4217.0156 | 122.6349 | -1.0529 | 121.4035 | 0.15244 | 0.015567 | 0.0041634 | 0.015616 | 0.0070922 | -0.0028541 | -0.0064365 | 0.18295 | -0.0072034 | 0.080499 | 0.054408 | 0.039243 | -0.010478 | 0.027466 | 0.086975 | 0.97046 | -0.88806 | 0.24261 | -1.1078 | -1.2589 | 0.07782 | 85.2402 | -0.009155 | 121.5866 | 121.4951 | -1.2497 | -1.2222 | -0.054932 | -0.20599 | -121.1609 | 1.1398 | 0.16479 | 0.37079 | -121.376 | -0.19684 | -0.16937 | 0.18311 | 1.1307 | 1.0437 | 1.2131 | 0.091553 | 1.2955 | 1.0803 | 2.0233 | -122.6624 | 122.6395 | 122.5479 | 86.293 | -122.6257
4218.0156 | 122.5937 | -1.0986 | 121.463 | 0.17532 | 0.01813 | 0.005018 | 0.019248 | 0.0070922 | 0.0024865 | -0.0079319 | 0.13718 | -0.0067762 | 0.084986 | 0.055262 | 0.04202 | -0.0094102 | 0.004578 | -0.036621 | 0.85602 | -0.85144 | 0.28381 | -1.1215 | -1.3138 | 0.027466 | 85.2402 | -0.09613 | 121.6415 | 121.5088 | -1.268 | -1.2268 | -0.022888 | -0.21515 | -121.1792 | 1.062 | 0.24719 | 0.46234 | -121.4584 | -0.16937 | -0.12817 | 0.17853 | 1.1261 | 1.0025 | 1.1307 | 0.045776 | 1.3824 | 1.1032 | 1.9547 | -122.7768 | 122.7402 | 122.6074 | 86.3388 | -122.6898
4219.0156 | 122.5845 | -1.0666 | 121.4722 | 0.16769 | 0.013217 | 0.0024544 | 0.01882 | 0.0073058 | -0.0011451 | -0.0098545 | 0.16769 | -0.0089124 | 0.080713 | 0.053767 | 0.041165 | -0.0089828 | 0.032043 | 0.082397 | 0.98419 | -0.8194 | 0.25635 | -1.0941 | -1.2726 | 0.068665 | 85.3226 | -0.018311 | 121.5958 | 121.5179 | -1.2268 | -1.2314 | -0.027466 | -0.20599 | -121.2158 | 1.149 | 0.24719 | 0.45319 | -121.4401 | -0.16022 | -0.1648 | 0.1236 | 1.1353 | 1.0483 | 1.2131 | 0.045776 | 1.3229 | 1.0986 | 2.0508 | -122.7448 | 122.6624 | 122.5845 | 86.3892 | -122.7036
4220.0156 | 122.5616 | -0.99792 | 121.5775 | 0.15244 | 0.019198 | 0.0030954 | 0.020529 | 0.0090148 | 0.0035547 | -0.0079319 | 0.16006 | -0.0054944 | 0.084345 | 0.053767 | 0.03967 | -0.011119 | -0.022888 | -0.045776 | 0.86975 | -0.75989 | 0.29755 | -1.03 | -1.2451 | 0 | 85.3638 | -0.10071 | 121.7194 | 121.6141 | -1.1993 | -1.1719 | -0.032043 | -0.24719 | -121.2799 | 0.95215 | 0.23804 | 0.48523 | -121.6003 | -0.20142 | -0.17395 | 0.14191 | 0.99792 | 0.89722 | 1.0712 | 0.036621 | 1.2955 | 0.97504 | 1.8677 | -122.8226 | 122.7173 | 122.612 | 86.3617 | -122.7493
4221.5938 | 122.6028 | -0.97046 | 121.5912 | -0.44266 | 0.013217 | 0.0071542 | 0.016257 | 0.0098694 | -0.0060585 | -0.010922 | 0.022736 | -0.010194 | 0.08114 | 0.050563 | 0.036679 | -0.0091966 | -0.032043 | 0.013733 | 0.94757 | -0.72327 | 0.23804 | -1.0254 | -1.181 | 0.045776 | 85.4965 | 0.009155 | 121.7194 | 121.6736 | -1.1169 | -1.0986 | -0.054932 | -0.21057 | -121.3531 | 0.98419 | 0.24719 | 0.45776 | -121.6232 | -0.14648 | -0.12817 | 0.12817 | 1.0162 | 0.97961 | 1.1078 | 0.082397 | 1.2085 | 0.93842 | 1.918 | -122.7722 | 122.6898 | 122.644 | 86.467 | -122.6898
4222.1719 | 122.5845 | -0.95673 | 121.5775 | -0.22141 | 0.012576 | 0.0058724 | 0.019675 | 0.011365 | -0.0011451 | -0.011777 | -0.20615 | -0.0097668 | 0.083063 | 0.052912 | 0.037106 | -0.0098374 | 0.045776 | 0.091553 | 0.97046 | -0.72784 | 0.27008 | -1.0117 | -1.1902 | 0.027466 | 85.5606 | -0.027466 | 121.7606 | 121.6461 | -1.1398 | -1.1307 | -0.054932 | -0.23346 | -121.3074 | 1.0483 | 0.22888 | 0.46234 | -121.5317 | -0.18311 | -0.17395 | 0.1831 | 0.98419 | 0.92926 | 1.1032 | 0.068664 | 1.2268 | 1.0025 | 1.9272 | -122.7676 | 122.7173 | 122.6028 | 86.5173 | -122.7081
4223.0156 | 122.5983 | -0.97961 | 121.5866 | 0.14481 | 0.01813 | 0.006086 | 0.017325 | 0.011578 | 0.0018457 | -0.0085727 | 0.12955 | -0.0072034 | 0.083063 | 0.056117 | 0.04202 | -0.0081284 | -0.018311 | -0.004578 | 0.88806 | -0.80109 | 0.28381 | -1.0437 | -1.2131 | 0.022888 | 85.4736 | -0.086975 | 121.7606 | 121.6049 | -1.1444 | -1.1307 | -0.064087 | -0.23346 | -121.3028 | 0.97504 | 0.17853 | 0.41199 | -121.6049 | -0.1648 | -0.15106 | 0.17395 | 1.0025 | 0.89264 | 1.0437 | 0.01831 | 1.2634 | 0.9613 | 1.8677 | -122.7997 | 122.7402 | 122.5845 | 86.4532 | -122.7173
4224.0156 | 122.5479 | -0.97504 | 121.637 | 0.15244 | 0.016421 | 0.0022408 | 0.023093 | 0.0096558 | 0.0027001 | -0.0072911 | -0.39688 | -0.0086988 | 0.082849 | 0.055049 | 0.039029 | -0.0064194 | 0.25177 | -0.25177 | 0.79651 | -0.6546 | 0.32044 | -0.97504 | -1.1581 | -0.022888 | 85.4507 | -0.13275 | 121.8109 | 121.6965 | -1.1353 | -1.1078 | 0 | -0.1831 | -121.3165 | 0.72327 | 0.32044 | 0.50354 | -121.3852 | -0.16022 | -0.13275 | 0.17395 | 0.95215 | 0.84229 | 0.97504 | 0.059509 | 1.2955 | 1.2268 | 1.7715 | -122.7951 | 122.7859 | 122.6715 | 86.4258 | -122.7448
4225.0156 | 122.644 | -0.91553 | 121.6141 | 0.16769 | 0.01813 | 0.0028818 | 0.019034 | 0.010724 | 0.0014185 | -0.0047275 | 0.0914 | -0.0065626 | 0.083917 | 0.056544 | 0.038388 | -0.0091966 | 0.009155 | 0.018311 | 0.97046 | -0.74158 | 0.27924 | -0.96588 | -1.1765 | 0.073242 | 85.7162 | -0.022888 | 121.7651 | 121.6644 | -1.1078 | -1.1032 | -0.050354 | -0.26093 | -121.3348 | 0.93384 | 0.17395 | 0.43488 | -121.6049 | -0.19226 | -0.18768 | 0.15106 | 0.98877 | 0.89264 | 1.0803 | 0.050354 | 1.1948 | 0.92468 | 1.886 | -122.7905 | 122.6807 | 122.58 | 86.6318 | -122.7173
4226.0156 | 122.5708 | -0.94299 | 121.6415 | 0.053253 | 0.019839 | 0.0024544 | 0.021384 | 0.011578 | 0.00056395 | -0.0077183 | 0.0914 | -0.006349 | 0.083063 | 0.053767 | 0.037961 | -0.0081284 | -0.036621 | -0.054932 | 0.90637 | -0.6958 | 0.31128 | -0.9613 | -1.1627 | -0.004578 | 85.6201 | -0.10986 | 121.8246 | 121.756 | -1.1215 | -1.1078 | -0.018311 | -0.21973 | -121.3303 | 0.88806 | 0.24719 | 0.46692 | -121.6782 | -0.17853 | -0.1648 | 0.1831 | 0.93841 | 0.83313 | 0.99792 | 0.11444 | 1.2543 | 0.90637 | 1.8494 | -122.8043 | 122.7676 | 122.699 | 86.5631 | -122.7493
4227.0156 | 122.644 | -0.94757 | 121.6049 | 0.19058 | 0.017062 | 0.0043772 | 0.017966 | 0.010937 | -0.0015723 | -0.0079319 | 0.21347 | -0.0072034 | 0.084345 | 0.05334 | 0.040952 | -0.0070602 | 0.050354 | 0.07782 | 1.0162 | -0.57678 | 0.2655 | -0.92926 | -1.1307 | -0.054932 | 85.9085 | 0.041199 | 121.756 | 121.6736 | -1.1353 | -1.1169 | 0.018311 | -0.1831 | -121.3394 | 1.0254 | 0.37079 | 0.55389 | -121.5546 | -0.18768 | -0.16937 | 0.15106 | 0.89264 | 0.98877 | 1.1581 | 0.068665 | 1.2131 | 0.99793 | 1.9638 | -122.7356 | 122.7036 | 122.6212 | 86.8561 | -122.7219
4228.0156 | 122.5433 | -0.94299 | 121.6736 | -2.7162 | 0.016421 | 0.0022408 | 0.020743 | 0.010724 | 0.0016321 | -0.0077183 | 0.10666 | -0.0069898 | 0.085199 | 0.055262 | 0.038174 | -0.0085556 | -0.068665 | -0.036621 | 0.91553 | -0.67291 | 0.31586 | -0.97961 | -1.1536 | -0.027466 | 85.675 | -0.12817 | 121.8521 | 121.7651 | -1.0986 | -1.0986 | -0.036621 | -0.21057 | -121.3577 | 0.90637 | 0.27008 | 0.48065 | -121.7422 | -0.15564 | -0.15564 | 0.17853 | 0.91553 | 0.81482 | 0.97046 | 0.091553 | 1.2589 | 0.87433 | 1.8585 | -122.8271 | 122.7951 | 122.7081 | 86.618 | -122.7722
4229.0625 | 122.6212 | -0.95215 | 121.6736 | -0.168 | 0.018985 | 0.003309 | 0.019034 | 0.0092284 | 0.0012047 | -0.0075047 | -0.21378 | -0.005708 | 0.084131 | 0.05334 | 0.036465 | -0.006633 | -0.009155 | -0.004578 | 0.9201 | -0.62714 | 0.28381 | -0.98877 | -1.1765 | -0.004578 | 85.762 | -0.10529 | 121.8201 | 121.7651 | -1.0986 | -1.1078 | -0.036622 | -0.2243 | -121.3898 | 0.94757 | 0.32501 | 0.54932 | -121.6827 | -0.14648 | -0.15564 | 0.14648 | 0.94757 | 0.84686 | 1.0025 | 0.091553 | 1.236 | 0.94299 | 1.8723 | -122.85 | 122.7722 | 122.7173 | 86.7142 | -122.7814
4230.0156 | 122.5616 | -0.94299 | 121.6965 | 0.045624 | 0.020694 | 0.0039498 | 0.020102 | 0.011365 | 0.0018457 | -0.0066501 | -0.00015237 | -0.0082716 | 0.086267 | 0.054835 | 0.038388 | -0.010051 | -0.022888 | -0.054932 | 0.89722 | -0.65918 | 0.27008 | -1.0025 | -1.1902 | -0.041199 | 85.7025 | -0.16479 | 121.8658 | 121.7789 | -1.1124 | -1.0941 | -0.059509 | -0.24719 | -121.4264 | 0.88806 | 0.28381 | 0.53101 | -121.7194 | -0.16937 | -0.15106 | 0.16937 | 0.90179 | 0.7782 | 0.92926 | 0.082398 | 1.2131 | 0.9201 | 1.8402 | -122.8867 | 122.8088 | 122.7219 | 86.6455 | -122.7905
4231.0156 | 122.6624 | -0.90179 | 121.7148 | 0.21347 | 0.018985 | 0.0056588 | 0.018393 | 0.016278 | 0.00035035 | -0.0087863 | 0.2211 | -0.007417 | 0.084986 | 0.054621 | 0.036679 | -0.0074876 | -0.009155 | 0.013733 | 0.94757 | -0.63171 | 0.28381 | -0.9613 | -1.1261 | 0.059509 | 85.8215 | -0.013733 | 121.8246 | 121.756 | -1.062 | -1.0666 | -0.05951 | -0.2243 | -121.431 | 0.91553 | 0.27008 | 0.49438 | -121.7239 | -0.16022 | -0.1648 | 0.10986 | 0.9613 | 0.88806 | 1.0529 | 0.041198 | 1.1856 | 0.89264 | 1.8494 | -122.8409 | 122.7264 | 122.6578 | 86.7233 | -122.7814
4232.0156 | 122.5479 | -0.9201 | 121.7102 | 0.015106 | 0.019626 | 0.0037362 | 0.019461 | 0.013928 | 0.00077755 | -0.0057957 | 0.12955 | -0.0048536 | 0.086908 | 0.054835 | 0.039456 | -0.0044968 | -0.059509 | -0.09613 | 0.86975 | -0.65002 | 0.30212 | -0.97504 | -1.1444 | -0.10071 | 86.174 | -0.086975 | 121.8933 | 121.8155 | -1.0757 | -1.0757 | -0.054932 | -0.2243 | -121.4081 | 0.82397 | 0.27008 | 0.49438 | -121.7697 | -0.15564 | -0.15564 | 0.18311 | 0.8194 | 0.83313 | 0.98877 | 0.10529 | 1.2222 | 0.8606 | 1.7899 | -122.8546 | 122.8134 | 122.7356 | 87.0941 | -122.7859
4233.0156 | 122.7081 | -0.92468 | 121.6873 | 0.19058 | 0.017276 | 0.0054452 | 0.016684 | 0.013928 | -0.0028541 | -0.0057957 | 0.22873 | -0.0082716 | 0.084558 | 0.054621 | 0.035825 | -0.010692 | 0.036621 | 0.07782 | 1.0071 | -0.57678 | 0.25177 | -0.9201 | -1.0986 | 0.13275 | 85.762 | 0.009155 | 121.8063 | 121.7285 | -1.1078 | -1.0712 | 0.004578 | -0.17395 | -121.4355 | 1.0025 | 0.3479 | 0.52185 | -121.6507 | -0.1831 | -0.14648 | 0.11902 | 1.0574 | 0.93384 | 1.0803 | 0.041199 | 1.1765 | 0.9613 | 1.9318 | -122.7859 | 122.731 | 122.6532 | 86.6867 | -122.7585
4234.0156 | 122.6074 | -0.96588 | 121.6919 | -0.57236 | 0.01813 | 0.0030954 | 0.022238 | 0.012219 | 0.0018457 | -0.0087863 | 0.10666 | -0.0052808 | 0.086908 | 0.05633 | 0.036038 | -0.0085556 | -0.050354 | -0.054932 | 0.89264 | -0.66376 | 0.31586 | -0.96588 | -1.1719 | -0.022888 | 85.7941 | -0.1236 | 121.8475 | 121.7926 | -1.0941 | -1.1032 | 0 | -0.20599 | -121.376 | 0.91095 | 0.30212 | 0.50812 | -121.7422 | -0.12817 | -0.13733 | 0.15564 | 0.94299 | 0.84228 | 0.97961 | 0.10071 | 1.2817 | 0.91553 | 1.8585 | -122.8638 | 122.8134 | 122.7585 | 86.7599 | -122.7951
4235.0156 | 122.7859 | -1.0208 | 121.4767 | 0.19058 | 0.014926 | 0.003309 | 0.018179 | 0.010724 | -0.0024269 | -0.0092137 | 0.22873 | -0.0078442 | 0.086908 | 0.055049 | 0.038602 | -0.006633 | 0.045776 | 0.059509 | 0.99792 | -0.63629 | 0.2655 | -0.99335 | -1.1719 | 0.086975 | 85.817 | 0 | 121.7331 | 121.6919 | -1.1627 | -1.149 | 0.027466 | -0.15106 | -121.2112 | 1.0803 | 0.38452 | 0.53558 | -121.431 | -0.14191 | -0.12817 | 0.25635 | 1.1078 | 1.0208 | 1.149 | 0.21515 | 1.2863 | 1.0666 | 2.0187 | -122.6486 | 122.7539 | 122.7127 | 86.8378 | -122.6257
4236.0156 | 122.5708 | -0.96588 | 121.7148 | 0.045624 | 0.019412 | 0.0018136 | 0.020529 | 0.01051 | 0.0024865 | -0.0081455 | -0.015411 | -0.0069898 | 0.089258 | 0.055262 | 0.037961 | -0.0085556 | -0.027466 | -0.086975 | 0.88348 | -0.70038 | 0.27924 | -0.99335 | -1.1627 | -0.050354 | 85.8307 | -0.15106 | 121.8704 | 121.8109 | -1.1124 | -1.1398 | -0.027466 | -0.19684 | -121.4355 | 0.87891 | 0.2655 | 0.46234 | -121.7422 | -0.14648 | -0.17395 | 0.15564 | 0.91553 | 0.81482 | 0.98877 | 0.09613 | 1.2451 | 0.93841 | 1.8494 | -122.8775 | 122.8363 | 122.7768 | 86.7966 | -122.8546
4237.0156 | 122.6074 | -0.97961 | 121.6644 | 0.11429 | 0.01813 | 0.0035226 | 0.017752 | 0.011151 | -0.00050425 | -0.0085727 | 0.18295 | -0.0065626 | 0.084986 | 0.055262 | 0.038815 | -0.0068466 | -0.036621 | -0.050354 | 0.9201 | -0.75073 | 0.29297 | -0.99792 | -1.1856 | 0.009155 | 85.8719 | -0.091553 | 121.8155 | 121.7514 | -1.1398 | -1.1169 | -0.018311 | -0.20599 | -121.3715 | 0.92926 | 0.22888 | 0.43488 | -121.701 | -0.16022 | -0.13733 | 0.15106 | 0.98877 | 0.88806 | 1.0254 | 0.086975 | 1.2726 | 0.94299 | 1.8997 | -122.85 | 122.7951 | 122.731 | 86.8515 | -122.7814
4238.0156 | 122.5937 | -0.99335 | 121.6736 | 0.0914 | 0.020267 | 0.0041634 | 0.021597 | 0.012006 | -0.0011451 | -0.0081455 | 0.44998 | -0.0054944 | 0.085199 | 0.056544 | 0.038602 | -0.0077012 | -0.045776 | -0.086975 | 0.90637 | -0.85602 | 0.28839 | -1.0162 | -1.181 | -0.045776 | 85.7391 | -0.15106 | 121.8292 | 121.7606 | -1.1444 | -1.1444 | -0.022888 | -0.18768 | -121.3852 | 0.90637 | 0.13733 | 0.32501 | -121.7194 | -0.15106 | -0.15106 | 0.15564 | 0.94757 | 0.84228 | 0.99335 | 0.086975 | 1.2817 | 0.94757 | 1.8997 | -122.8546 | 122.8226 | 122.7539 | 86.7325 | -122.818
4239.0156 | 122.6761 | -0.95215 | 121.6553 | 0.15244 | 0.015994 | 0.006086 | 0.016898 | 0.010724 | -0.0064857 | -0.0098545 | 0.18295 | -0.0078442 | 0.083277 | 0.056544 | 0.037534 | -0.0059922 | 0.027466 | 0.082397 | 1.0437 | -0.78735 | 0.25635 | -0.98419 | -1.1627 | 0.07782 | 86.0458 | 0.013733 | 121.7789 | 121.7514 | -1.0941 | -1.1078 | -0.032044 | -0.21057 | -121.3989 | 1.0345 | 0.16479 | 0.37537 | -121.6278 | -0.14191 | -0.15564 | 0.1236 | 1.03 | 0.96588 | 1.1215 | 0.096131 | 1.2085 | 0.97961 | 1.9958 | -122.818 | 122.731 | 122.7036 | 86.998 | -122.7631
4240.0156 | 122.6303 | -1.0757 | 121.5866 | 0.045624 | 0.018558 | 0.0045908 | 0.022452 | 0.011365 | 0.00099115 | -0.0079319 | 0.10666 | -0.0069898 | 0.086481 | 0.05334 | 0.039883 | -0.0074876 | -0.045776 | -0.059509 | 0.91553 | -0.9201 | 0.29755 | -1.0666 | -1.2497 | -0.018311 | 85.8627 | -0.13733 | 121.788 | 121.6736 | -1.2451 | -1.2222 | 0.009156 | -0.17395 | -121.2891 | 1.0162 | 0.15564 | 0.32959 | -121.6324 | -0.16937 | -0.14648 | 0.20142 | 1.0574 | 0.93842 | 1.0849 | 0.086975 | 1.3733 | 1.03 | 1.9913 | -122.8363 | 122.8638 | 122.7493 | 86.9385 | -122.8088
4241.0156 | 122.7493 | -1.0254 | 121.5729 | 0.12955 | 0.01813 | 0.0048044 | 0.018179 | 0.0079468 | -0.0032813 | -0.0077183 | 0.21347 | -0.006349 | 0.083917 | 0.053767 | 0.040524 | -0.010265 | 0.041199 | 0.068665 | 1.0529 | -0.83313 | 0.27008 | -1.0162 | -1.2085 | 0.09613 | 86.0687 | -0.050354 | 121.7285 | 121.6782 | -1.2039 | -1.1948 | 0.009156 | -0.18311 | -121.3028 | 1.0941 | 0.19226 | 0.37537 | -121.5317 | -0.17853 | -0.16937 | 0.15564 | 1.1215 | 0.97504 | 1.1444 | 0.10529 | 1.2955 | 1.0666 | 2.0782 | -122.7814 | 122.7539 | 122.7036 | 87.0941 | -122.7676
4242.0156 | 122.612 | -1.0666 | 121.5912 | -0.62576 | 0.017062 | 0.0030954 | 0.020956 | 0.009442 | -0.00029045 | -0.0085727 | 0.12192 | -0.0089124 | 0.086267 | 0.05398 | 0.040097 | -0.0072738 | -0.041199 | -0.091553 | 0.9201 | -0.93384 | 0.32959 | -1.0666 | -1.2634 | -0.027466 | 85.9543 | -0.15564 | 121.7926 | 121.7331 | -1.2085 | -1.2177 | 0 | -0.19684 | -121.2616 | 0.97504 | 0.13275 | 0.32959 | -121.6324 | -0.14191 | -0.15106 | 0.20142 | 1.0391 | 0.91095 | 1.062 | 0.14191 | 1.3962 | 1.0254 | 1.9867 | -122.8546 | 122.8592 | 122.7997 | 87.0209 | -122.8088
4243.0156 | 122.6715 | -1.0483 | 121.5958 | 0.17532 | 0.017489 | 0.0039498 | 0.017966 | 0.010937 | -0.0026405 | -0.0085727 | 0.16769 | -0.0065626 | 0.087122 | 0.055689 | 0.041379 | -0.0098374 | -0.022888 | -0.050354 | 0.94757 | -0.91553 | 0.29297 | -1.0849 | -1.2589 | 0.013733 | 85.9818 | -0.09613 | 121.7651 | 121.6965 | -1.2039 | -1.181 | -0.036621 | -0.21057 | -121.3028 | 0.99792 | 0.13275 | 0.34332 | -121.6187 | -0.15564 | -0.13275 | 0.16937 | 1.062 | 0.95215 | 1.0849 | 0.10071 | 1.3412 | 1.0254 | 1.9958 | -122.8546 | 122.8134 | 122.7448 | 87.03 | -122.7768
4244.0469 | 122.7127 | -1.0574 | 121.5637 | -0.18326 | 0.014712 | 0.01164 | 0.019034 | 0.0077332 | -0.0064857 | -0.010068 | -0.099335 | -0.010194 | 0.084345 | 0.055262 | 0.038602 | -0.0077012 | 0.13733 | -0.009155 | 1.0254 | -0.86517 | 0.24261 | -1.0986 | -1.2817 | 0.064087 | 86.0962 | -0.004578 | 121.6919 | 121.6644 | -1.2314 | -1.1902 | -0.041199 | -0.2243 | -121.3211 | 1.0483 | 0.19226 | 0.41657 | -121.4264 | -0.17395 | -0.13275 | 0.12817 | 1.1215 | 1.0529 | 1.1856 | 0.10071 | 1.3 | 1.1948 | 2.0828 | -122.8455 | 122.7493 | 122.7219 | 87.1536 | -122.7539
4245.0156 | 122.731 | -1.0574 | 121.5591 | -0.96146 | 0.011935 | 0.0037362 | 0.016257 | 0.012219 | -0.0039221 | -0.0094273 | 0.19058 | -0.006349 | 0.084131 | 0.054835 | 0.04266 | -0.0089828 | 0.032043 | 0.068665 | 1.0757 | -0.90179 | 0.2243 | -1.1124 | -1.2955 | 0.082397 | 86.1008 | -0.022888 | 121.7102 | 121.6278 | -1.2497 | -1.2131 | -0.054932 | -0.23804 | -121.3348 | 1.1261 | 0.15564 | 0.39368 | -121.5271 | -0.19226 | -0.15564 | 0.15106 | 1.1398 | 1.0345 | 1.1902 | 0.068665 | 1.2817 | 1.0895 | 2.1332 | -122.8546 | 122.7676 | 122.6852 | 87.1582 | -122.7722
4246.0156 | 122.6715 | -1.1353 | 121.5088 | 0.15244 | 0.017489 | 0.0043772 | 0.020529 | 0.011792 | 0.00077755 | -0.010068 | 0.16006 | -0.007417 | 0.08819 | 0.055262 | 0.044369 | -0.0079148 | -0.022888 | -0.07782 | 0.94299 | -1.0071 | 0.29755 | -1.1765 | -1.3367 | 0.009155 | 85.9772 | -0.1236 | 121.7148 | 121.6507 | -1.2863 | -1.2589 | -0.041199 | -0.20142 | -121.2112 | 1.0574 | 0.12817 | 0.32959 | -121.5317 | -0.15106 | -0.1236 | 0.20599 | 1.1444 | 1.0117 | 1.1353 | 0.14191 | 1.4328 | 1.1124 | 2.0782 | -122.8455 | 122.85 | 122.7859 | 87.1124 | -122.7676
4247.0156 | 122.699 | -1.0666 | 121.5042 | 0.099029 | 0.012149 | 0.0043772 | 0.018179 | 0.006665 | -0.0019995 | -0.0077183 | 0.19058 | -0.008058 | 0.086054 | 0.057398 | 0.041592 | -0.0059922 | 0.018311 | 0.064087 | 1.0574 | -0.92926 | 0.25177 | -1.0895 | -1.2726 | 0.09613 | 86.0962 | -0.032043 | 121.6873 | 121.6324 | -1.2314 | -1.2314 | -0.022889 | -0.20599 | -121.2524 | 1.1307 | 0.13733 | 0.34332 | -121.4859 | -0.1648 | -0.1648 | 0.18311 | 1.1627 | 1.0345 | 1.1993 | 0.12817 | 1.3184 | 1.0849 | 2.124 | -122.7768 | 122.7539 | 122.699 | 87.1628 | -122.7356
4248.0156 | 122.6303 | -1.1307 | 121.55 | 0.12955 | 0.020694 | 0.0073678 | 0.020529 | 0.0092284 | 0.0016321 | -0.0087863 | 0.15244 | -0.0076306 | 0.086908 | 0.055049 | 0.042233 | -0.0094102 | -0.041199 | -0.07782 | 0.94299 | -0.99792 | 0.3067 | -1.1536 | -1.3275 | 0 | 85.9772 | -0.12817 | 121.7422 | 121.669 | -1.268 | -1.2726 | -0.022888 | -0.19684 | -121.2433 | 1.0529 | 0.13275 | 0.32959 | -121.5912 | -0.13733 | -0.14191 | 0.19226 | 1.1307 | 1.0025 | 1.1444 | 0.11902 | 1.4374 | 1.0895 | 2.0737 | -122.8775 | 122.8729 | 122.7997 | 87.1078 | -122.8226
4249.0156 | 122.731 | -1.1032 | 121.5454 | -0.0383 | 0.011508 | -0.035784 | 0.01583 | 0.0081604 | -0.0081947 | -0.0089999 | 0.076141 | -0.0086988 | 0.083277 | 0.055049 | 0.039456 | -0.003856 | -0.004578 | 0.059509 | 1.0483 | -0.92926 | 0.27466 | -1.1169 | -1.3138 | 0.064087 | 86.1465 | 0.013733 | 121.6736 | 121.6415 | -1.2589 | -1.2314 | -0.013733 | -0.21057 | -121.2708 | 1.1627 | 0.17395 | 0.38452 | -121.55 | -0.15564 | -0.12817 | 0.12817 | 1.1673 | 1.1169 | 1.2451 | 0.096131 | 1.3779 | 1.0986 | 2.1515 | -122.8592 | 122.7768 | 122.7448 | 87.2498 | -122.7768
4250.0156 | 122.6166 | -1.1353 | 121.5546 | 0.24399 | 0.019198 | 0.0039498 | 0.021811 | 0.0077332 | 0.0037683 | -0.0096409 | 0.053253 | -0.0072034 | 0.089258 | 0.055903 | 0.043515 | -0.010478 | -0.045776 | -0.10071 | 0.91095 | -1.0162 | 0.29755 | -1.1673 | -1.355 | -0.036621 | 85.8673 | -0.20599 | 121.6919 | 121.6507 | -1.2955 | -1.2817 | -0.032043 | -0.21973 | -121.257 | 1.0345 | 0.11902 | 0.33875 | -121.6003 | -0.16022 | -0.14648 | 0.13733 | 1.0986 | 0.92926 | 1.0757 | 0.096131 | 1.4328 | 1.0895 | 2.0462 | -122.9095 | 122.8271 | 122.7859 | 87.0026 | -122.8363
4251.0156 | 122.7081 | -1.1353 | 121.5271 | 0.2211 | 0.02048 | 0.0026682 | 0.018607 | 0.0096558 | 0.0012047 | -0.0089999 | 0.17532 | -0.0069898 | 0.08349 | 0.055049 | 0.043942 | -0.0072738 | -0.022888 | -0.032043 | 0.97504 | -0.99792 | 0.28381 | -1.1856 | -1.3641 | 0.041199 | 86.0458 | -0.073242 | 121.7056 | 121.6095 | -1.3046 | -1.2909 | -0.050354 | -0.22888 | -121.2433 | 1.1032 | 0.13733 | 0.36621 | -121.55 | -0.16937 | -0.15564 | 0.17853 | 1.1765 | 1.062 | 1.2177 | 0.082397 | 1.4191 | 1.1124 | 2.1103 | -122.8912 | 122.8409 | 122.7448 | 87.1811 | -122.818
4252.0156 | 122.6349 | -1.1536 | 121.5363 | 0.28213 | 0.020907 | 0.0030954 | 0.020743 | 0.0051696 | 0.0018457 | -0.0092137 | 0.0914 | -0.0035718 | 0.087976 | 0.054194 | 0.043088 | -0.008342 | -0.036621 | -0.082397 | 0.92468 | -1.0345 | 0.29755 | -1.1765 | -1.3733 | -0.009155 | 85.9772 | -0.15564 | 121.7102 | 121.6324 | -1.3138 | -1.3 | -0.022889 | -0.21973 | -121.2387 | 1.0712 | 0.11902 | 0.33875 | -121.5729 | -0.16022 | -0.14648 | 0.17395 | 1.1444 | 0.99792 | 1.1444 | 0.09613 | 1.4511 | 1.1169 | 2.0782 | -122.9095 | 122.8638 | 122.7859 | 87.1307 | -122.8363
4253.0156 | 122.7219 | -1.1078 | 121.5088 | 0.27451 | 0.014285 | 0.0037362 | 0.019461 | 0.008374 | -0.0064857 | -0.0079319 | 0.18295 | -0.0072034 | 0.088404 | 0.054408 | 0.04266 | -0.0057786 | 0.032043 | 0.041199 | 1.0529 | -0.94757 | 0.23346 | -1.1398 | -1.3321 | 0.10071 | 86.1328 | -0.027466 | 121.669 | 121.6141 | -1.3092 | -1.2726 | -0.032044 | -0.2243 | -121.2753 | 1.149 | 0.16022 | 0.38452 | -121.4767 | -0.20142 | -0.1648 | 0.16022 | 1.2085 | 1.0803 | 1.2451 | 0.10529 | 1.3412 | 1.1398 | 2.1606 | -122.8409 | 122.7768 | 122.7219 | 87.2406 | -122.7814
4254.0156 | 122.7036 | -1.1902 | 121.5042 | 0.083771 | 0.012576 | 0.0058724 | 0.018393 | 0.0055968 | -0.0069129 | -0.0096409 | 0.09903 | -0.010194 | 0.087122 | 0.054408 | 0.041165 | -0.0057786 | -0.027466 | 0.013733 | 1.0208 | -0.97961 | 0.26093 | -1.1581 | -1.3504 | -0.018311 | 86.0916 | -0.059509 | 121.6324 | 121.5546 | -1.3458 | -1.3412 | 0.032044 | -0.16022 | -121.2433 | 1.2039 | 0.21057 | 0.37079 | -121.5317 | -0.15564 | -0.15106 | 0.12817 | 1.1719 | 1.1307 | 1.2817 | 0.050354 | 1.4511 | 1.1627 | 2.211 | -122.8546 | 122.8226 | 122.7448 | 87.2818 | -122.8455
4255.0156 | 122.6898 | -1.1261 | 121.5271 | 0.14481 | 0.013431 | 0.0056588 | 0.018179 | 0.0079468 | -0.0028541 | -0.010709 | 0.2211 | -0.009126 | 0.086481 | 0.054621 | 0.041806 | -0.0070602 | 0.032043 | 0.059509 | 1.0803 | -0.97504 | 0.24719 | -1.1536 | -1.3367 | 0.064087 | 86.1145 | -0.045776 | 121.6919 | 121.6141 | -1.2817 | -1.268 | -0.027465 | -0.21057 | -121.2799 | 1.1856 | 0.15106 | 0.36163 | -121.4951 | -0.15564 | -0.14191 | 0.16479 | 1.1902 | 1.0803 | 1.2222 | 0.086975 | 1.3733 | 1.1581 | 2.2064 | -122.8638 | 122.818 | 122.7402 | 87.2406 | -122.7951
4256.0156 | 122.6303 | -1.1719 | 121.5271 | 0.12955 | 0.019412 | 0.005018 | 0.022452 | 0.009442 | 0.0016321 | -0.011777 | -0.099335 | -0.005708 | 0.08819 | 0.055903 | 0.043942 | -0.0087692 | 0.18768 | -0.11902 | 0.89722 | -1.03 | 0.3067 | -1.1673 | -1.3641 | -0.036621 | 86.0092 | -0.16022 | 121.7148 | 121.6415 | -1.3367 | -1.3092 | 0.004578 | -0.19226 | -121.2204 | 1.0529 | 0.14191 | 0.33417 | -121.3394 | -0.1648 | -0.13733 | 0.18768 | 1.1353 | 1.0117 | 1.149 | 0.11444 | 1.4786 | 1.3596 | 2.0691 | -122.8912 | 122.8867 | 122.8134 | 87.1811 | -122.8363
4257.0156 | 122.7814 | -1.1078 | 121.5134 | 0.21347 | 0.01578 | 0.0035226 | 0.018393 | 0.0068786 | -0.00093145 | -0.0079319 | -0.038299 | -0.0052808 | 0.091394 | 0.05633 | 0.044583 | -0.0070602 | 0.022888 | 0.027466 | 1.0437 | -0.97961 | 0.25635 | -1.1673 | -1.3367 | 0.07782 | 86.1191 | -0.045776 | 121.669 | 121.6049 | -1.2817 | -1.2726 | -0.059509 | -0.22888 | -121.257 | 1.1353 | 0.12817 | 0.35706 | -121.4905 | -0.17395 | -0.1648 | 0.15564 | 1.1856 | 1.062 | 1.2268 | 0.091552 | 1.3641 | 1.1307 | 2.1515 | -122.85 | 122.7768 | 122.7127 | 87.2269 | -122.7859
4258.0156 | 122.699 | -1.1719 | 121.5179 | 0.14481 | 0.017276 | 0.0048044 | 0.019461 | 0.0077332 | 0.0012047 | -0.0087863 | 0.14481 | -0.006349 | 0.090326 | 0.054835 | 0.043301 | -0.0074876 | -0.027466 | -0.086975 | 0.95673 | -1.0345 | 0.29755 | -1.1765 | -1.3596 | 0.004578 | 86.0687 | -0.12817 | 121.7194 | 121.6324 | -1.3229 | -1.3138 | -0.004578 | -0.18768 | -121.2204 | 1.0849 | 0.13733 | 0.32501 | -121.5454 | -0.15106 | -0.14191 | 0.20142 | 1.1765 | 1.0437 | 1.1856 | 0.11444 | 1.4694 | 1.1444 | 2.1286 | -122.8775 | 122.8912 | 122.8043 | 87.2406 | -122.8317
4259.0156 | 122.8043 | -1.149 | 121.5042 | -0.11459 | 0.010013 | 0.0073678 | 0.01647 | 0.0079468 | -0.0077673 | -0.01135 | -0.12985 | -0.0082716 | 0.083277 | 0.054835 | 0.03967 | -0.0070602 | 0.022888 | 0.12817 | 1.1169 | -0.95215 | 0.24261 | -1.1398 | -1.3367 | 0.082397 | 86.2289 | 0.013733 | 121.6644 | 121.6324 | -1.2772 | -1.2726 | 0.009155 | -0.18768 | -121.2616 | 1.2772 | 0.19684 | 0.38452 | -121.4813 | -0.12817 | -0.1236 | 0.16022 | 1.2314 | 1.1627 | 1.2863 | 0.12817 | 1.3916 | 1.1719 | 2.2659 | -122.8409 | 122.8134 | 122.7814 | 87.3779 | -122.7768
4260.0156 | 122.7539 | -1.1261 | 121.5042 | 0.17532 | 0.01813 | 0.0071542 | 0.018393 | 0.0092284 | 0.0027001 | -0.010922 | 0.17532 | -0.0072034 | 0.088617 | 0.055689 | 0.04202 | -0.008342 | -0.009155 | 0.004578 | 1.0345 | -1.0117 | 0.24719 | -1.1673 | -1.3596 | 0.068665 | 86.1145 | -0.059509 | 121.6782 | 121.5958 | -1.3046 | -1.2909 | -0.041198 | -0.23346 | -121.257 | 1.1307 | 0.11444 | 0.3479 | -121.5134 | -0.17853 | -0.1648 | 0.17395 | 1.1948 | 1.0666 | 1.2314 | 0.091553 | 1.3733 | 1.1169 | 2.1606 | -122.8638 | 122.8043 | 122.7219 | 87.2406 | -122.7951
4261.0156 | 122.7539 | -1.1032 | 121.5134 | 0.19058 | 0.014926 | 0.0048044 | 0.016684 | 0.0081604 | -0.0019995 | -0.0098545 | 0.14481 | -0.0093396 | 0.086054 | 0.054194 | 0.042233 | -0.0091966 | 0.041199 | 0.086975 | 1.0941 | -0.95673 | 0.24261 | -1.1719 | -1.3321 | 0.086975 | 86.1191 | -0.027466 | 121.669 | 121.5912 | -1.2909 | -1.2634 | -0.068665 | -0.22888 | -121.2708 | 1.1902 | 0.14648 | 0.37537 | -121.4722 | -0.18768 | -0.16022 | 0.15564 | 1.1902 | 1.0757 | 1.236 | 0.07782 | 1.3458 | 1.1444 | 2.1973 | -122.8455 | 122.7722 | 122.6944 | 87.2223 | -122.7768
4262.0156 | 122.7402 | -1.1673 | 121.4996 | 0.15244 | 0.02048 | 0.005018 | 0.019675 | 0.008374 | 0.0024865 | -0.0085727 | 0.14481 | -0.0059216 | 0.089258 | 0.055903 | 0.042874 | -0.0089828 | -0.009155 | -0.027466 | 1.0071 | -1.0117 | 0.30212 | -1.1719 | -1.3641 | 0.036621 | 86.0733 | -0.068665 | 121.701 | 121.6095 | -1.3046 | -1.2772 | -0.004578 | -0.19684 | -121.1975 | 1.1398 | 0.15564 | 0.35248 | -121.5088 | -0.13733 | -0.10986 | 0.20142 | 1.2039 | 1.0986 | 1.2085 | 0.10986 | 1.4694 | 1.1581 | 2.1744 | -122.8638 | 122.8683 | 122.7768 | 87.2406 | -122.7768
4263.0156 | 122.7173 | -1.1215 | 121.5591 | 0.16006 | 0.011508 | 0.0073678 | 0.01647 | 0.009442 | -0.0032813 | -0.0094273 | 0.19058 | -0.0097668 | 0.082208 | 0.054621 | 0.043515 | -0.004924 | 0.041199 | 0.054932 | 1.0803 | -0.98419 | 0.25177 | -1.1398 | -1.3275 | 0.041199 | 86.087 | -0.036621 | 121.6827 | 121.6187 | -1.2863 | -1.2909 | -0.018311 | -0.20599 | -121.3074 | 1.1765 | 0.13733 | 0.34332 | -121.5179 | -0.1648 | -0.16937 | 0.1236 | 1.1627 | 1.0849 | 1.2543 | 0.059509 | 1.3733 | 1.1627 | 2.2018 | -122.8867 | 122.8043 | 122.7402 | 87.2086 | -122.85
4264.0156 | 122.7448 | -1.1627 | 121.5408 | 0.037994 | 0.013431 | 0.006086 | 0.014548 | 0.0077332 | -0.0047767 | -0.0072911 | 0.12192 | -0.010194 | 0.083917 | 0.055476 | 0.043301 | -0.0064194 | -0.018311 | 0.027466 | 1.062 | -1.0071 | 0.2655 | -1.1673 | -1.3412 | 0.032043 | 85.9726 | -0.050354 | 121.6415 | 121.5775 | -1.3412 | -1.3504 | -0.004577 | -0.17853 | -121.2753 | 1.1902 | 0.15564 | 0.33417 | -121.5591 | -0.17853 | -0.18768 | 0.10071 | 1.1948 | 1.1124 | 1.3 | 0.036621 | 1.4282 | 1.1444 | 2.2247 | -122.8821 | 122.8043 | 122.7402 | 87.1353 | -122.8912
4265.0156 | 122.7722 | -1.1261 | 121.5225 | -0.20615 | 0.014712 | 0.0048044 | 0.019675 | 0.0077332 | 0.0012047 | -0.0081455 | 0.13718 | -0.0084852 | 0.08584 | 0.05398 | 0.043088 | -0.008342 | 0.045776 | 0.082397 | 1.0849 | -0.97504 | 0.2243 | -1.1673 | -1.355 | 0.10071 | 86.0916 | -0.022888 | 121.701 | 121.6095 | -1.2909 | -1.2817 | -0.041198 | -0.22888 | -121.2982 | 1.2085 | 0.15106 | 0.37994 | -121.4767 | -0.1648 | -0.15564 | 0.17853 | 1.2268 | 1.1032 | 1.2589 | 0.086975 | 1.3504 | 1.1719 | 2.211 | -122.8775 | 122.8271 | 122.7356 | 87.2177 | -122.8043
4266.0156 | 122.7493 | -1.1627 | 121.5546 | 0.16006 | 0.017276 | 0.0062998 | 0.019888 | 0.0077332 | 0.0027001 | -0.0089999 | 0.13718 | -0.005708 | 0.089899 | 0.05334 | 0.043729 | -0.0089828 | -0.013733 | -0.07782 | 0.98419 | -1.0574 | 0.29755 | -1.2085 | -1.3733 | 0.032043 | 85.9909 | -0.10529 | 121.7331 | 121.637 | -1.3275 | -1.3184 | -0.045776 | -0.21057 | -121.257 | 1.0849 | 0.10529 | 0.31586 | -121.5683 | -0.1648 | -0.15564 | 0.17853 | 1.1948 | 1.0574 | 1.2131 | 0.082398 | 1.4603 | 1.149 | 2.1469 | -122.9279 | 122.8958 | 122.7997 | 87.1536 | -122.8729
4267.0156 | 122.7264 | -1.1215 | 121.5454 | 0.11429 | 0.014285 | 0.006086 | 0.018179 | 0.0062378 | -0.0017859 | -0.0085727 | 0.16769 | -0.0076306 | 0.087335 | 0.054621 | 0.04266 | -0.0070602 | 0.032043 | 0.059509 | 1.1032 | -1.0071 | 0.2655 | -1.1719 | -1.3275 | 0.091553 | 86.0916 | -0.022888 | 121.7056 | 121.6232 | -1.2955 | -1.2955 | -0.050354 | -0.20599 | -121.2799 | 1.181 | 0.11444 | 0.32044 | -121.5134 | -0.17395 | -0.17395 | 0.16022 | 1.2131 | 1.0986 | 1.2726 | 0.07782 | 1.387 | 1.1536 | 2.2247 | -122.8729 | 122.8271 | 122.7448 | 87.2131 | -122.8409
4268.0156 | 122.7676 | -1.1398 | 121.5317 | 0.21347 | 0.018985 | 0.0045908 | 0.019248 | 0.010297 | 0.0024865 | -0.0051547 | 0.30502 | -0.0065626 | 0.085413 | 0.055903 | 0.046078 | -0.0077012 | -0.18768 | 0.20599 | 1.1719 | -0.97504 | 0.21057 | -1.2177 | -1.4008 | 0.09613 | 86.1237 | -0.022888 | 121.6919 | 121.6187 | -1.2955 | -1.2863 | -0.077819 | -0.26093 | -121.3211 | 1.3458 | 0.16479 | 0.42572 | -121.7194 | -0.15564 | -0.14648 | 0.16022 | 1.236 | 1.1169 | 1.2634 | 0.086975 | 1.3504 | 0.95215 | 2.3117 | -122.9324 | 122.8317 | 122.7585 | 87.2635 | -122.818
4269.0156 | 122.8226 | -1.1307 | 121.5225 | -0.10696 | 0.011294 | 0.0054452 | 0.01647 | 0.0077332 | -0.0030677 | -0.010495 | -0.091705 | -0.0089124 | 0.085413 | 0.051844 | 0.043301 | -0.005565 | 0.068665 | 0.10986 | 1.1353 | -0.95215 | 0.25635 | -1.1719 | -1.3367 | 0.11444 | 86.174 | 0.036621 | 121.6873 | 121.6187 | -1.2955 | -1.2772 | -0.041199 | -0.20599 | -121.2662 | 1.2405 | 0.17853 | 0.38452 | -121.4539 | -0.1648 | -0.14648 | 0.16479 | 1.2451 | 1.1673 | 1.3138 | 0.09613 | 1.387 | 1.1993 | 2.2659 | -122.8592 | 122.818 | 122.7493 | 87.3047 | -122.7997
4270.0156 | 122.7219 | -1.1673 | 121.5775 | -0.18326 | 0.019412 | 0.0024544 | 0.020956 | 0.009442 | 0.0033411 | -0.0085727 | 0.0914 | -0.0050672 | 0.089044 | 0.056758 | 0.045651 | -0.0079148 | -0.045776 | -0.059509 | 0.97504 | -1.0208 | 0.28839 | -1.2039 | -1.387 | -0.004578 | 86.0138 | -0.14191 | 121.7651 | 121.6415 | -1.3229 | -1.2955 | -0.036621 | -0.21973 | -121.2891 | 1.1078 | 0.14648 | 0.36621 | -121.6232 | -0.15564 | -0.12817 | 0.18768 | 1.1627 | 1.0254 | 1.1536 | 0.064087 | 1.4557 | 1.1215 | 2.1423 | -122.9645 | 122.9324 | 122.8088 | 87.1811 | -122.8729
4271.0156 | 122.7356 | -1.1581 | 121.5363 | 0.14481 | 0.012362 | 0.0069406 | 0.016043 | 0.006665 | -0.0037085 | -0.0089999 | 0.20584 | -0.008058 | 0.085199 | 0.05398 | 0.043088 | -0.0062058 | 0.041199 | 0.064087 | 1.0986 | -0.97046 | 0.26093 | -1.1765 | -1.3458 | 0.073242 | 86.1191 | -0.041199 | 121.6919 | 121.6461 | -1.2955 | -1.2863 | -0.018311 | -0.18768 | -121.2753 | 1.2222 | 0.18768 | 0.37537 | -121.4951 | -0.13733 | -0.12817 | 0.15564 | 1.2314 | 1.1169 | 1.2451 | 0.10986 | 1.4191 | 1.1993 | 2.2568 | -122.8821 | 122.85 | 122.8043 | 87.2772 | -122.8226
4272.0156 | 122.7127 | -1.1765 | 121.5408 | 0.15244 | 0.018344 | 0.0052316 | 0.01882 | 0.0081604 | 0.0027001 | -0.0068637 | 0.09903 | -0.006349 | 0.087763 | 0.055689 | 0.045651 | -0.0081284 | -0.022888 | -0.059509 | 0.99335 | -1.0391 | 0.28381 | -1.2085 | -1.387 | 0.036621 | 86.0001 | -0.11444 | 121.7422 | 121.6415 | -1.3092 | -1.3184 | -0.032043 | -0.21057 | -121.257 | 1.1169 | 0.13733 | 0.3479 | -121.5637 | -0.13275 | -0.14191 | 0.20142 | 1.2131 | 1.062 | 1.2039 | 0.10071 | 1.4603 | 1.1536 | 2.1698 | -122.9279 | 122.9187 | 122.818 | 87.1765 | -122.8592
4273.0156 | 122.8043 | -1.1398 | 121.5225 | 1.8309 | 0.016421 | 0.0056588 | 0.020529 | 0.008374 | -7.6852e-05 | -0.0083591 | 0.14481 | -0.007417 | 0.087335 | 0.05398 | 0.042874 | -0.0077012 | 0.059509 | 0.027466 | 1.0803 | -0.97961 | 0.21057 | -1.1993 | -1.3733 | 0.091553 | 86.0596 | -0.032043 | 121.7056 | 121.6461 | -1.3 | -1.3046 | -0.059509 | -0.23346 | -121.312 | 1.1673 | 0.16022 | 0.39368 | -121.463 | -0.16022 | -0.16479 | 0.18311 | 1.2314 | 1.1078 | 1.2726 | 0.1236 | 1.3504 | 1.1993 | 2.2202 | -122.8958 | 122.8455 | 122.7859 | 87.1994 | -122.8271
4274.0156 | 122.8912 | -1.1719 | 121.5042 | -0.099335 | 0.01514 | 0.006727 | 0.019248 | 0.0064514 | -0.0062721 | -0.010282 | -0.068817 | -0.009126 | 0.086481 | 0.054408 | 0.041165 | -0.0072738 | 0.059509 | 0.091553 | 1.1353 | -0.97504 | 0.24719 | -1.1719 | -1.3412 | 0.10529 | 86.0733 | 0.009155 | 121.7102 | 121.6187 | -1.2863 | -1.2817 | 0 | -0.16937 | -121.257 | 1.2634 | 0.19684 | 0.36621 | -121.4447 | -0.11444 | -0.10986 | 0.20599 | 1.2772 | 1.181 | 1.2909 | 0.11444 | 1.4191 | 1.2314 | 2.3071 | -122.8455 | 122.8821 | 122.7905 | 87.2452 | -122.7859
4275.0156 | 122.7814 | -1.149 | 121.5408 | 0.17532 | 0.01578 | 0.0026682 | 0.016684 | 0.012006 | -0.0022131 | -0.0081455 | 0.16006 | -0.0069898 | 0.08584 | 0.052912 | 0.041592 | -0.0096238 | 0.036621 | 0.07782 | 1.0986 | -1.0025 | 0.24261 | -1.181 | -1.3321 | 0.10986 | 85.9726 | -0.013733 | 121.6965 | 121.6003 | -1.3046 | -1.3 | -0.032043 | -0.18311 | -121.2982 | 1.2268 | 0.14648 | 0.32959 | -121.5042 | -0.15564 | -0.15106 | 0.15564 | 1.2589 | 1.1353 | 1.2863 | 0.059509 | 1.3916 | 1.1856 | 2.2476 | -122.8729 | 122.8455 | 122.7493 | 87.1216 | -122.8409
4276.0156 | 122.7539 | -1.181 | 121.5134 | 0.19058 | 0.018344 | 0.0037362 | 0.021384 | 0.010724 | 0.00099115 | -0.0087863 | 0.12955 | -0.006349 | 0.089258 | 0.055262 | 0.044369 | -0.0077012 | -0.013733 | -0.041199 | 1.0254 | -1.0666 | 0.28381 | -1.1902 | -1.3916 | 0.050354 | 85.9451 | -0.086975 | 121.7148 | 121.6141 | -1.3184 | -1.3184 | -0.009156 | -0.21057 | -121.2296 | 1.1398 | 0.11444 | 0.32501 | -121.5271 | -0.13733 | -0.13733 | 0.20142 | 1.2314 | 1.0941 | 1.2314 | 0.10071 | 1.4648 | 1.1673 | 2.2064 | -122.905 | 122.8958 | 122.7951 | 87.1262 | -122.8317
4277.0156 | 122.8088 | -1.149 | 121.5454 | 0.19058 | 0.015994 | 0.0056588 | 0.01882 | 0.0090148 | 0.0024865 | -0.0070773 | 0.16006 | -0.0072034 | 0.087122 | 0.053553 | 0.044583 | -0.0096238 | 0.059509 | 0.027466 | 1.0803 | -1.0208 | 0.25635 | -1.1856 | -1.3641 | 0.091553 | 86.0046 | -0.036621 | 121.7285 | 121.6278 | -1.3046 | -1.3 | -0.036621 | -0.21515 | -121.2891 | 1.1765 | 0.12817 | 0.34332 | -121.4859 | -0.15564 | -0.15106 | 0.18311 | 1.2405 | 1.1124 | 1.2634 | 0.082398 | 1.4053 | 1.2085 | 2.2293 | -122.9095 | 122.8775 | 122.7768 | 87.1536 | -122.8455
4278.0156 | 122.7081 | -1.1856 | 121.5637 | 0.13718 | 0.018558 | 0.0043772 | 0.021811 | 0.0092284 | 0.0016321 | -0.0081455 | 0.0914 | -0.00464 | 0.089044 | 0.056117 | 0.046719 | -0.0070602 | -0.032043 | -0.07782 | 0.98419 | -1.0849 | 0.28381 | -1.2222 | -1.3962 | -0.018311 | 85.8856 | -0.16022 | 121.7468 | 121.6644 | -1.3412 | -1.355 | -0.036621 | -0.21057 | -121.2799 | 1.1078 | 0.10071 | 0.31128 | -121.5958 | -0.15564 | -0.16937 | 0.1831 | 1.1673 | 1.0254 | 1.1948 | 0.10071 | 1.4694 | 1.1536 | 2.1698 | -122.9599 | 122.9324 | 122.85 | 87.0712 | -122.9187
4279.0156 | 122.7631 | -1.1581 | 121.5088 | 0.12955 | 0.016421 | 0.0041634 | 0.014761 | 0.0088012 | -0.0032813 | -0.0087863 | 0.16006 | -0.0072034 | 0.086908 | 0.054621 | 0.044369 | -0.006633 | 0.013733 | 0.07782 | 1.1169 | -1.03 | 0.22888 | -1.181 | -1.3687 | 0.082397 | 86.0001 | -0.013733 | 121.6919 | 121.6187 | -1.3275 | -1.3138 | -0.022888 | -0.21057 | -121.2799 | 1.236 | 0.12817 | 0.33875 | -121.4951 | -0.16937 | -0.15564 | 0.18311 | 1.2405 | 1.1444 | 1.3 | 0.10986 | 1.387 | 1.1719 | 2.2751 | -122.8775 | 122.85 | 122.7768 | 87.1582 | -122.8226
4280.0156 | 122.6761 | -1.2268 | 121.5546 | 0.15244 | 0.019626 | 0.0045908 | 0.022665 | 0.0075194 | 0.00013675 | -0.0081455 | 0.0914 | -0.0035718 | 0.092035 | 0.054621 | 0.043088 | -0.0079148 | -0.045776 | -0.068665 | 0.99335 | -1.0849 | 0.27466 | -1.2405 | -1.4145 | 0 | 85.9085 | -0.14191 | 121.7514 | 121.637 | -1.3687 | -1.3504 | -0.013733 | -0.18768 | -121.2799 | 1.1581 | 0.14191 | 0.32959 | -121.6003 | -0.14191 | -0.1236 | 0.19684 | 1.2268 | 1.0849 | 1.2085 | 0.082398 | 1.5015 | 1.181 | 2.2202 | -122.9691 | 122.9782 | 122.8638 | 87.1353 | -122.905
4281.0156 | 122.8455 | -1.1719 | 121.5408 | 0.20584 | 0.014926 | 0.0030954 | 0.017539 | 0.0081604 | -0.0028541 | -0.010922 | 0.18295 | -0.0067762 | 0.086267 | 0.053126 | 0.044583 | -0.0070602 | 0.036621 | 0.082397 | 1.1261 | -1.0254 | 0.23804 | -1.1856 | -1.3641 | 0.10071 | 86.0275 | -0.018311 | 121.7102 | 121.5912 | -1.3367 | -1.3138 | -0.013733 | -0.19226 | -121.3028 | 1.2543 | 0.14648 | 0.33875 | -121.5042 | -0.1648 | -0.14191 | 0.16937 | 1.2726 | 1.1536 | 1.2955 | 0.050354 | 1.4099 | 1.2085 | 2.298 | -122.905 | 122.8821 | 122.7631 | 87.1994 | -122.8546
4282.0156 | 122.7448 | -1.2039 | 121.582 | 0.14481 | 0.020694 | 0.0041634 | 0.017752 | 0.0053832 | 0.0014185 | -0.0051547 | 0.16006 | -0.006349 | 0.089685 | 0.057612 | 0.045651 | -0.0068466 | -0.036621 | -0.073242 | 1.0117 | -1.0986 | 0.27466 | -1.2039 | -1.387 | 0.022888 | 85.9222 | -0.11902 | 121.7422 | 121.637 | -1.3504 | -1.3412 | 0 | -0.18311 | -121.3074 | 1.1307 | 0.10529 | 0.28839 | -121.6187 | -0.14648 | -0.13733 | 0.16022 | 1.2268 | 1.0849 | 1.2222 | 0.054932 | 1.4786 | 1.1673 | 2.2156 | -122.9691 | 122.9462 | 122.8409 | 87.1262 | -122.9233
4283.0156 | 122.818 | -1.1719 | 121.5363 | 0.16769 | 0.016208 | 0.0062998 | 0.020102 | 0.0075194 | -0.0022131 | -0.0062229 | 0.22873 | -0.0069898 | 0.088831 | 0.056544 | 0.043942 | -0.0077012 | 0.027466 | 0.059509 | 1.1307 | -1.0254 | 0.23804 | -1.1902 | -1.3962 | 0.10529 | 86.0275 | -0.027466 | 121.6919 | 121.5958 | -1.3275 | -1.3046 | -0.018311 | -0.2243 | -121.2982 | 1.2314 | 0.14648 | 0.37079 | -121.5088 | -0.15564 | -0.13275 | 0.15564 | 1.2772 | 1.1444 | 1.2772 | 0.059509 | 1.4099 | 1.1993 | 2.3026 | -122.9324 | 122.8638 | 122.7676 | 87.1994 | -122.8409
4284.0156 | 122.6715 | -1.2451 | 121.5546 | 0.015106 | 0.020267 | 0.0054452 | 0.020316 | 0.0070922 | 0.0044091 | -0.010068 | 0.015106 | -0.0050672 | 0.090967 | 0.055476 | 0.046292 | -0.008342 | -0.059509 | -0.09613 | 1.0025 | -1.1215 | 0.27924 | -1.236 | -1.4236 | -0.036621 | 85.8948 | -0.16937 | 121.756 | 121.6644 | -1.3824 | -1.3641 | 0.009155 | -0.17853 | -121.2753 | 1.149 | 0.1236 | 0.30212 | -121.6141 | -0.13733 | -0.11902 | 0.20142 | 1.2085 | 1.0757 | 1.1948 | 0.10986 | 1.5244 | 1.1856 | 2.2476 | -122.9782 | 123.0011 | 122.9095 | 87.1399 | -122.9187
4285.0156 | 122.8271 | -1.1765 | 121.5042 | 0.15244 | 0.016208 | 0.0037362 | 0.017752 | 0.0070922 | 0.00099115 | -0.0081455 | 0.23636 | -0.0061352 | 0.088404 | 0.057612 | 0.045651 | -0.008342 | 0.013733 | 0.054932 | 1.1307 | -1.0437 | 0.26093 | -1.2039 | -1.3962 | 0.082397 | 86.0504 | -0.027466 | 121.6736 | 121.5912 | -1.355 | -1.3321 | -0.027465 | -0.21973 | -121.2433 | 1.2314 | 0.13275 | 0.35248 | -121.4905 | -0.17853 | -0.15564 | 0.16937 | 1.2589 | 1.149 | 1.3046 | 0.086976 | 1.4374 | 1.1902 | 2.3071 | -122.9004 | 122.85 | 122.7676 | 87.2269 | -122.8363
4286.0156 | 122.7264 | -1.2405 | 121.5546 | 0.12192 | 0.020053 | 0.006727 | 0.02117 | 0.010083 | 0.00056395 | -0.0070773 | 0.17532 | -0.0065626 | 0.093317 | 0.055049 | 0.04736 | -0.0072738 | -0.059509 | -0.091553 | 1.0162 | -1.1169 | 0.29297 | -1.2497 | -1.4236 | -0.027466 | 85.8948 | -0.16022 | 121.7331 | 121.669 | -1.3733 | -1.3779 | -0.009155 | -0.18311 | -121.2616 | 1.149 | 0.1236 | 0.3067 | -121.6141 | -0.13275 | -0.13733 | 0.17853 | 1.2131 | 1.0803 | 1.2177 | 0.11444 | 1.5335 | 1.181 | 2.2568 | -122.9782 | 122.9736 | 122.9095 | 87.1353 | -122.9324
4287.0156 | 122.8271 | -1.1856 | 121.5408 | 0.19058 | 0.016208 | 0.0037362 | 0.018179 | 0.0077332 | -0.0028541 | -0.0087863 | 0.2211 | -0.0072034 | 0.087335 | 0.056117 | 0.045438 | -0.0064194 | 0.018311 | 0.068665 | 1.1444 | -1.0437 | 0.24719 | -1.2131 | -1.4145 | 0.09613 | 86.0733 | -0.022888 | 121.6965 | 121.6003 | -1.3596 | -1.3458 | -0.027466 | -0.22888 | -121.2936 | 1.2543 | 0.14191 | 0.37079 | -121.5225 | -0.17395 | -0.16022 | 0.15564 | 1.2817 | 1.1627 | 1.3229 | 0.059509 | 1.4328 | 1.2039 | 2.33 | -122.9553 | 122.8821 | 122.7859 | 87.2589 | -122.8867
4288.0156 | 122.7402 | -1.2314 | 121.5134 | 0.0914 | 0.020694 | 0.0035226 | 0.020529 | 0.0092284 | 0.00099115 | -0.0083591 | 0.15244 | -0.0035718 | 0.09289 | 0.055903 | 0.044797 | -0.0079148 | -0.041199 | -0.091553 | 1.0208 | -1.1307 | 0.27924 | -1.268 | -1.442 | 0 | 85.9268 | -0.13733 | 121.7239 | 121.637 | -1.3824 | -1.3733 | -0.036621 | -0.21057 | -121.2341 | 1.1398 | 0.10071 | 0.31128 | -121.5546 | -0.15106 | -0.14191 | 0.21057 | 1.2314 | 1.0941 | 1.236 | 0.1236 | 1.5106 | 1.1902 | 2.2522 | -122.9553 | 122.9553 | 122.8683 | 87.1582 | -122.8867
4289.0156 | 122.8317 | -1.1948 | 121.5088 | 0.099029 | 0.016421 | 0.0048044 | 0.01882 | 0.0098694 | -0.0013587 | -0.0079319 | 0.20584 | -0.0059216 | 0.089899 | 0.056544 | 0.044583 | -0.0062058 | 0.018311 | 0.064087 | 1.1536 | -1.0666 | 0.25177 | -1.2268 | -1.4145 | 0.086975 | 86.0275 | -0.027466 | 121.6507 | 121.6049 | -1.3733 | -1.3504 | -0.032044 | -0.21973 | -121.257 | 1.2589 | 0.12817 | 0.3479 | -121.4905 | -0.17853 | -0.15564 | 0.14191 | 1.2817 | 1.1673 | 1.3229 | 0.09613 | 1.4465 | 1.2131 | 2.3483 | -122.9233 | 122.8455 | 122.7997 | 87.2223 | -122.8592
4290.0156 | 122.7356 | -1.2726 | 121.5179 | 0.14481 | 0.020694 | 0.003309 | 0.020743 | 0.010724 | -0.00029045 | -0.0049411 | 0.12955 | -0.0042126 | 0.091394 | 0.055903 | 0.045865 | -0.0064194 | -0.064087 | -0.07782 | 1.0345 | -1.181 | 0.29297 | -1.3 | -1.4877 | -0.013733 | 85.8719 | -0.15106 | 121.7056 | 121.5958 | -1.4236 | -1.4282 | -0.027466 | -0.21515 | -121.225 | 1.1948 | 0.091553 | 0.3067 | -121.582 | -0.15106 | -0.15564 | 0.18768 | 1.2589 | 1.1215 | 1.2772 | 0.07782 | 1.5656 | 1.2085 | 2.3071 | -123.0057 | 122.9782 | 122.8683 | 87.1445 | -122.9462
4291.0156 | 122.7768 | -1.236 | 121.5088 | 0.16006 | 0.02048 | 0.0045908 | 0.020102 | 0.0088012 | -0.00029045 | -0.0072911 | 0.15244 | -0.0061352 | 0.091394 | 0.05334 | 0.046292 | -0.0057786 | -0.059509 | -0.045776 | 1.062 | -1.1353 | 0.27924 | -1.2772 | -1.4694 | 0.027466 | 85.9268 | -0.10529 | 121.7194 | 121.6415 | -1.3824 | -1.4008 | -0.041199 | -0.23346 | -121.2296 | 1.1902 | 0.10071 | 0.33417 | -121.5683 | -0.14648 | -0.1648 | 0.21057 | 1.2634 | 1.1307 | 1.2955 | 0.13275 | 1.5152 | 1.1765 | 2.298 | -122.9782 | 122.9553 | 122.8775 | 87.1628 | -122.9095
4292.0156 | 122.7173 | -1.2497 | 121.5546 | 0.12192 | 0.021976 | 0.0024544 | 0.019888 | 0.0075194 | 0.0012047 | -0.0079319 | 0.12192 | -0.0037854 | 0.09289 | 0.055262 | 0.046933 | -0.006633 | -0.064087 | -0.082397 | 1.0483 | -1.1581 | 0.27466 | -1.2909 | -1.4648 | -0.022888 | 85.8582 | -0.16022 | 121.7148 | 121.637 | -1.4328 | -1.4053 | -0.041199 | -0.21515 | -121.2799 | 1.1673 | 0.091553 | 0.3067 | -121.6187 | -0.18311 | -0.15564 | 0.16022 | 1.2268 | 1.0895 | 1.2451 | 0.082398 | 1.5244 | 1.1856 | 2.298 | -123.0194 | 122.9645 | 122.8867 | 87.1078 | -122.9599
4293.0156 | 122.8775 | -1.2131 | 121.5225 | 0.18295 | 0.018985 | 0.005018 | 0.018179 | 0.006665 | -0.0045631 | -0.0066501 | 0.24399 | -0.0042126 | 0.089044 | 0.053553 | 0.045651 | -0.0027878 | -0.004578 | -0.004578 | 1.1261 | -1.0849 | 0.26093 | -1.2589 | -1.4465 | 0.068665 | 85.9726 | -0.041199 | 121.6919 | 121.6049 | -1.3733 | -1.3824 | -0.045776 | -0.23346 | -121.2616 | 1.2085 | 0.12817 | 0.36163 | -121.5271 | -0.16022 | -0.16937 | 0.16937 | 1.2817 | 1.1719 | 1.3412 | 0.082397 | 1.474 | 1.2085 | 2.3392 | -122.9691 | 122.905 | 122.818 | 87.1857 | -122.905
4294.0156 | 122.7768 | -1.2451 | 121.5134 | 0.13718 | 0.018344 | 0.0035226 | 0.019675 | 0.012219 | 0.0031273 | -0.0083591 | 0.16006 | -0.0042126 | 0.093317 | 0.055689 | 0.046292 | -0.003856 | -0.054932 | -0.07782 | 1.0574 | -1.1581 | 0.29755 | -1.2863 | -1.4603 | 0 | 85.881 | -0.14191 | 121.7148 | 121.6553 | -1.4099 | -1.4053 | -0.041199 | -0.21515 | -121.2158 | 1.1673 | 0.086975 | 0.30212 | -121.5683 | -0.1648 | -0.16022 | 0.20142 | 1.2451 | 1.1032 | 1.2634 | 0.14191 | 1.5427 | 1.1902 | 2.3026 | -122.9736 | 122.9599 | 122.9004 | 87.1262 | -122.9187
4295.0156 | 122.8455 | -1.2222 | 121.4996 | 0.16769 | 0.015994 | 0.0048044 | 0.019034 | 0.0070922 | -0.0022131 | -0.0068637 | 0.21347 | -0.007417 | 0.091821 | 0.054621 | 0.046506 | -0.0068466 | 0.018311 | 0.073242 | 1.1673 | -1.0803 | 0.23804 | -1.2314 | -1.4145 | 0.082397 | 85.9314 | -0.027466 | 121.6827 | 121.6003 | -1.3733 | -1.3596 | -0.009155 | -0.19226 | -121.2616 | 1.2955 | 0.14191 | 0.33417 | -121.4813 | -0.15106 | -0.13733 | 0.1831 | 1.3046 | 1.1948 | 1.3321 | 0.10071 | 1.4603 | 1.2405 | 2.3895 | -122.9141 | 122.905 | 122.8226 | 87.1536 | -122.8592
4296.0156 | 122.7585 | -1.268 | 121.5408 | 0.19058 | 0.01813 | 0.0065134 | 0.022879 | 0.0098694 | 0.0027001 | -0.0064365 | 0.12955 | -0.005708 | 0.094812 | 0.05633 | 0.047147 | -0.0059922 | -0.054932 | -0.07782 | 1.0529 | -1.1581 | 0.29297 | -1.3 | -1.4694 | -0.013733 | 85.7941 | -0.14191 | 121.7056 | 121.6507 | -1.4236 | -1.4008 | -0.032044 | -0.20142 | -121.2479 | 1.1902 | 0.10986 | 0.31128 | -121.5958 | -0.15564 | -0.13275 | 0.16479 | 1.2543 | 1.1261 | 1.2589 | 0.10986 | 1.561 | 1.2131 | 2.3209 | -123.0103 | 122.9736 | 122.9187 | 87.0621 | -122.9416
4297.0156 | 122.8455 | -1.2039 | 121.5088 | 0.25162 | 0.018558 | 0.0048044 | 0.018607 | 0.0088012 | -0.00071785 | -0.0072911 | 0.25162 | -0.0059216 | 0.090113 | 0.054621 | 0.045224 | -0.0053512 | 0.032043 | 0.045776 | 1.1627 | -1.0803 | 0.21515 | -1.2222 | -1.4282 | 0.073242 | 85.5377 | -0.041199 | 121.6873 | 121.637 | -1.3824 | -1.3641 | -0.018311 | -0.2243 | -121.2936 | 1.2497 | 0.1236 | 0.3479 | -121.4767 | -0.17853 | -0.16022 | 0.17853 | 1.2772 | 1.1627 | 1.3229 | 0.12817 | 1.4191 | 1.236 | 2.3666 | -122.937 | 122.8912 | 122.8409 | 86.7416 | -122.8729
4298.0156 | 122.7448 | -1.2497 | 121.5317 | 0.060882 | 0.021548 | 0.0022408 | 0.02117 | 0.0096558 | 0.00056395 | -0.0068637 | 0.10666 | -0.0050672 | 0.091608 | 0.056117 | 0.04736 | -0.0051376 | -0.050354 | -0.11444 | 1.03 | -1.1627 | 0.27924 | -1.2909 | -1.4603 | -0.050354 | 85.6979 | -0.19226 | 121.7377 | 121.6827 | -1.4465 | -1.4145 | -0.041199 | -0.21057 | -121.2524 | 1.1353 | 0.086975 | 0.29755 | -121.582 | -0.19684 | -0.1648 | 0.20599 | 1.1993 | 1.0574 | 1.2222 | 0.15106 | 1.5289 | 1.1993 | 2.2797 | -122.9919 | 122.9874 | 122.9324 | 86.9476 | -122.9462
4299.0156 | 122.818 | -1.2497 | 121.4996 | 0.17532 | 0.018558 | 0.0048044 | 0.019248 | 0.0096558 | -0.0011451 | -0.0075047 | 0.19058 | -0.00464 | 0.092035 | 0.055262 | 0.046078 | -0.0040696 | -0.054932 | -0.054932 | 1.0895 | -1.1536 | 0.27924 | -1.2909 | -1.4557 | 0.032043 | 85.7483 | -0.091553 | 121.6827 | 121.6324 | -1.3916 | -1.3916 | -0.041199 | -0.20599 | -121.2204 | 1.1948 | 0.096131 | 0.30212 | -121.5546 | -0.14191 | -0.14191 | 0.1831 | 1.2817 | 1.1581 | 1.3 | 0.13275 | 1.5289 | 1.1948 | 2.3392 | -122.9553 | 122.9324 | 122.8821 | 86.998 | -122.8912
4300.0156 | 122.7493 | -1.2634 | 121.5179 | 0.14481 | 0.020694 | 0.0022408 | 0.020102 | 0.012433 | 0.00077755 | -0.0077183 | 0.060883 | -0.006349 | 0.094171 | 0.055476 | 0.045224 | -0.0068466 | -0.082397 | -0.086975 | 1.0483 | -1.1673 | 0.29297 | -1.2955 | -1.4832 | -0.013733 | 85.6705 | -0.16479 | 121.7377 | 121.6278 | -1.4236 | -1.4099 | -0.032043 | -0.21973 | -121.225 | 1.1765 | 0.096131 | 0.31586 | -121.6003 | -0.16022 | -0.14648 | 0.21973 | 1.2497 | 1.0986 | 1.2451 | 0.10986 | 1.5564 | 1.181 | 2.3117 | -123.0011 | 123.0011 | 122.8912 | 86.9339 | -122.9279
4301.0156 | 122.85 | -1.236 | 121.4996 | 0.16006 | 0.015353 | 0.0058724 | 0.016684 | 0.0079468 | -0.0041357 | -0.0081455 | 0.2211 | -0.0069898 | 0.09054 | 0.055689 | 0.045651 | -0.004924 | 0.009155 | 0.054932 | 1.1765 | -1.1215 | 0.23804 | -1.2634 | -1.4511 | 0.086975 | 85.7483 | -0.041199 | 121.6553 | 121.5958 | -1.4099 | -1.3733 | -0.027466 | -0.21515 | -121.2616 | 1.2909 | 0.11444 | 0.32959 | -121.4905 | -0.17395 | -0.13733 | 0.15564 | 1.3229 | 1.1948 | 1.3321 | 0.09613 | 1.474 | 1.2451 | 2.4124 | -122.9507 | 122.8912 | 122.8317 | 86.9843 | -122.8729
4302.0156 | 122.8088 | -1.2589 | 121.5271 | 0.16769 | 0.018558 | 0.0045908 | 0.020529 | 0.0088012 | 0.0016321 | -0.0072911 | 0.16769 | -0.006349 | 0.09353 | 0.057612 | 0.045865 | -0.0062058 | -0.045776 | -0.054932 | 1.0803 | -1.1627 | 0.2655 | -1.3 | -1.4557 | 0.027466 | 85.5743 | -0.091553 | 121.6919 | 121.6324 | -1.4282 | -1.4053 | -0.041199 | -0.19684 | -121.2616 | 1.2039 | 0.09613 | 0.29297 | -121.5729 | -0.16937 | -0.14648 | 0.16479 | 1.2863 | 1.1673 | 1.3138 | 0.10528 | 1.5244 | 1.2131 | 2.3392 | -122.9828 | 122.9507 | 122.8912 | 86.8332 | -122.9324
4303.0156 | 122.8683 | -1.236 | 121.4905 | 0.15244 | 0.017062 | 0.0028818 | 0.019248 | 0.0096558 | -0.0026405 | -0.0094273 | 0.20584 | -0.006349 | 0.093317 | 0.055689 | 0.046078 | -0.0070602 | 0.018311 | 0.064087 | 1.1856 | -1.0941 | 0.21515 | -1.2634 | -1.4236 | 0.07782 | 85.5835 | -0.018311 | 121.6919 | 121.6141 | -1.387 | -1.3733 | -0.027466 | -0.18768 | -121.2753 | 1.3 | 0.14191 | 0.32959 | -121.4722 | -0.15106 | -0.13733 | 0.20142 | 1.3138 | 1.2177 | 1.355 | 0.1236 | 1.4511 | 1.2543 | 2.4216 | -122.9141 | 122.9279 | 122.85 | 86.8195 | -122.8638
4304.0156 | 122.8592 | -1.2405 | 121.4905 | 0.16006 | 0.017917 | 0.005018 | 0.021597 | 0.008374 | -0.00093145 | -0.0075047 | 0.19058 | -0.0035718 | 0.092035 | 0.053553 | 0.046292 | -0.006633 | 0.022888 | 0.032043 | 1.1581 | -1.0941 | 0.21973 | -1.2909 | -1.4465 | 0.082397 | 85.5515 | -0.027466 | 121.6919 | 121.6141 | -1.4008 | -1.3779 | -0.050354 | -0.20599 | -121.2708 | 1.2726 | 0.14648 | 0.35248 | -121.4676 | -0.16022 | -0.13733 | 0.20142 | 1.3229 | 1.2131 | 1.3504 | 0.1236 | 1.4603 | 1.2634 | 2.3987 | -122.937 | 122.9324 | 122.8546 | 86.792 | -122.8683
4305.0156 | 122.8958 | -1.2451 | 121.4996 | 0.14481 | 0.017703 | 0.0037362 | 0.019248 | 0.010937 | -0.0026405 | -0.0081455 | 0.2211 | -0.0035718 | 0.090753 | 0.054408 | 0.047147 | -0.0070602 | 0.027466 | 0.032043 | 1.1719 | -1.1032 | 0.24261 | -1.2497 | -1.4465 | 0.09613 | 85.556 | -0.041199 | 121.6919 | 121.6003 | -1.4191 | -1.4053 | -0.004578 | -0.20142 | -121.257 | 1.2772 | 0.14191 | 0.34332 | -121.4722 | -0.17395 | -0.16022 | 0.19226 | 1.3412 | 1.2039 | 1.3641 | 0.10071 | 1.4877 | 1.2726 | 2.417 | -122.9462 | 122.937 | 122.8455 | 86.8011 | -122.905
4306.0156 | 122.8134 | -1.2909 | 121.4996 | 0.18295 | 0.019839 | 0.0024544 | 0.017111 | 0.0079468 | 0.00013675 | -0.010922 | 0.13718 | -0.006349 | 0.093958 | 0.05633 | 0.047147 | -0.0064194 | -0.027466 | -0.059509 | 1.0849 | -1.181 | 0.27924 | -1.3046 | -1.5015 | 0.022888 | 85.4736 | -0.10071 | 121.7148 | 121.6141 | -1.4374 | -1.4328 | -0.013732 | -0.21057 | -121.2204 | 1.2314 | 0.10986 | 0.32044 | -121.5271 | -0.14648 | -0.14191 | 0.21515 | 1.3138 | 1.1902 | 1.3321 | 0.11444 | 1.5701 | 1.2634 | 2.3758 | -123.0011 | 123.0057 | 122.905 | 86.7645 | -122.9324
4307.0156 | 122.8546 | -1.2543 | 121.5179 | 0.12955 | 0.016635 | 0.0037362 | 0.017752 | 0.0092284 | -0.0013587 | -0.0087863 | 0.22873 | -0.0054944 | 0.091608 | 0.056971 | 0.045438 | -0.0044968 | 0.018311 | 0.059509 | 1.1856 | -1.1215 | 0.23804 | -1.2543 | -1.4603 | 0.091553 | 85.4782 | -0.022888 | 121.6919 | 121.5958 | -1.3962 | -1.4099 | 0 | -0.20599 | -121.2799 | 1.3138 | 0.13275 | 0.33875 | -121.4996 | -0.14191 | -0.15564 | 0.17395 | 1.3458 | 1.2314 | 1.387 | 0.07782 | 1.4923 | 1.2726 | 2.4399 | -122.9782 | 122.9462 | 122.85 | 86.7325 | -122.9279
4308.0156 | 122.8912 | -1.2451 | 121.5042 | 0.21347 | 0.018344 | 0.0043772 | 0.019888 | 0.010724 | -0.0011451 | -0.010282 | 0.2211 | -0.005708 | 0.093317 | 0.054835 | 0.049069 | -0.0053512 | 0.036621 | 0.004578 | 1.1536 | -1.1078 | 0.22888 | -1.2817 | -1.4648 | 0.086975 | 85.4095 | -0.022888 | 121.6644 | 121.6049 | -1.4008 | -1.3962 | -0.036621 | -0.21973 | -121.2753 | 1.2497 | 0.13733 | 0.35706 | -121.4676 | -0.15564 | -0.15106 | 0.16022 | 1.3321 | 1.2222 | 1.3733 | 0.10071 | 1.474 | 1.2817 | 2.3987 | -122.9691 | 122.9095 | 122.85 | 86.6547 | -122.9004
4309.0156 | 122.7814 | -1.2955 | 121.55 | -0.25192 | 0.014071 | 0.0037362 | 0.020956 | 0.009442 | -0.0056311 | -0.010709 | -0.19852 | -0.006349 | 0.093744 | 0.056117 | 0.04501 | -0.0027878 | -0.032043 | 0.032043 | 1.1353 | -1.1673 | 0.2655 | -1.3275 | -1.4923 | -0.009155 | 85.3729 | -0.13733 | 121.6919 | 121.6461 | -1.4557 | -1.4557 | -0.032044 | -0.19684 | -121.2845 | 1.3275 | 0.12817 | 0.32501 | -121.582 | -0.16022 | -0.16022 | 0.14191 | 1.2863 | 1.1581 | 1.3184 | 0.09613 | 1.561 | 1.2634 | 2.4307 | -123.0423 | 122.9874 | 122.9416 | 86.6684 | -123.0057
4310.0156 | 122.8638 | -1.2589 | 121.5042 | 0.19821 | 0.018558 | 0.0065134 | 0.017966 | 0.0098694 | 0.0027001 | -0.0070773 | 0.19821 | -0.0061352 | 0.093958 | 0.054194 | 0.048215 | -0.0068466 | 0.009155 | 0.045776 | 1.1765 | -1.1124 | 0.24719 | -1.2863 | -1.4877 | 0.09613 | 85.3775 | -0.032043 | 121.669 | 121.5958 | -1.442 | -1.4008 | -0.027466 | -0.22888 | -121.257 | 1.3046 | 0.14648 | 0.37537 | -121.4951 | -0.18311 | -0.14191 | 0.16479 | 1.355 | 1.2268 | 1.3687 | 0.091553 | 1.506 | 1.268 | 2.4353 | -122.9919 | 122.9279 | 122.8546 | 86.6364 | -122.905
4311.0156 | 122.8363 | -1.2589 | 121.4722 | 0.083771 | 0.014499 | 0.0018136 | 0.016684 | 0.009442 | -0.0041357 | -0.010068 | 0.2211 | -0.0052808 | 0.094171 | 0.055476 | 0.044797 | -0.0040696 | 0.004578 | 0.064087 | 1.2177 | -1.1581 | 0.25177 | -1.3046 | -1.4786 | 0.073242 | 85.3775 | -0.050354 | 121.6553 | 121.5912 | -1.4282 | -1.4191 | -0.045776 | -0.21973 | -121.2204 | 1.3229 | 0.10071 | 0.32044 | -121.4676 | -0.16937 | -0.16022 | 0.1831 | 1.3321 | 1.2085 | 1.3687 | 0.11902 | 1.5106 | 1.2634 | 2.4765 | -122.9507 | 122.9141 | 122.85 | 86.6364 | -122.8912
4312.0156 | 122.8088 | -1.3046 | 121.5088 | 0.19058 | 0.019198 | 0.003309 | 0.019461 | 0.011578 | 0.00077755 | -0.010922 | 0.13718 | -0.0059216 | 0.093958 | 0.055049 | 0.04971 | -0.0051376 | -0.032043 | -0.054932 | 1.0941 | -1.2131 | 0.2655 | -1.3367 | -1.5198 | 0.032043 | 85.2402 | -0.13733 | 121.6873 | 121.5958 | -1.4511 | -1.4511 | -0.032044 | -0.21515 | -121.2433 | 1.2497 | 0.091552 | 0.3067 | -121.5408 | -0.14648 | -0.14648 | 0.17853 | 1.3367 | 1.1673 | 1.3138 | 0.086975 | 1.5701 | 1.2726 | 2.3987 | -123.0286 | 122.9919 | 122.9004 | 86.5448 | -122.9599
4313.0156 | 122.9736 | -47.3236 | 75.3113 | 0.068512 | 0.011935 | 0.027876 | -0.0048919 | 0.45314 | 0.046493 | -0.0083591 | 0.030365 | -0.0078442 | 0.93756 | 0.085383 | 0.31546 | -0.0034286 | -2.6962 | -2.6184 | -3.8406 | -18.6447 | -2.2934 | -49.9283 | -49.617 | 2.4673 | 42.2607 | -0.064087 | 74.7437 | 74.881 | -47.7356 | -47.6257 | -2.6047 | -2.2934 | -77.6047 | 44.7052 | 28.6789 | 30.9723 | -78.0075 | -0.41199 | -0.30212 | -0.56763 | 49.791 | 47.2595 | 47.5616 | -0.4303 | 45.0302 | 44.6274 | 43.483 | -124.9283 | 122.0673 | 122.2046 | 89.5844 | -122.937
4314.0156 | 122.6578 | -73.5764 | 48.8708 | 0.19821 | 0.01813 | 0.039625 | -0.019205 | 0.38649 | 0.032607 | -0.0079319 | 0.13718 | 1.2111 | 1.2971 | 0.10589 | 1.9698 | -0.0010788 | -3.4424 | -3.4332 | -5.6305 | -68.3121 | -3.2364 | -73.6038 | -73.7 | 3.3737 | 20.0088 | -3.2043 | 48.7747 | 48.6969 | -73.6954 | -73.6908 | -0.027466 | -0.1236 | -52.1072 | 70.1431 | 5.2643 | 5.3879 | -52.3132 | -0.11902 | -0.11444 | -0.096131 | 76.9501 | 70.372 | 70.4865 | -0.17395 | 70.34 | 70.134 | 67.9459 | -122.5708 | 122.3511 | 122.2733 | 93.5852 | -122.5616
4315.0156 | 122.6532 | -63.9954 | 58.4564 | 0.060882 | 0.011081 | 0.039839 | -0.014719 | 0.079297 | 0.1501 | -0.0083591 | 0.0914 | 0.41748 | 1.8232 | 0.097346 | 1.8877 | -0.001506 | -2.948 | -2.8931 | -4.5044 | -39.006 | -2.6413 | -63.9542 | -64.0823 | 2.6779 | 27.2461 | -3.2547 | 58.3832 | 58.3282 | -64.0823 | -64.0915 | 0.041198 | -0.086975 | -61.0977 | 61.1023 | 24.9893 | 25.0763 | -61.4044 | -0.086975 | -0.096131 | -0.073242 | 66.6733 | 60.7407 | 60.8368 | -0.12817 | 61.3541 | 61.0474 | 59.491 | -122.5388 | 122.3785 | 122.3236 | 91.2415 | -122.5479
4316.0156 | 122.6761 | -70.8206 | 51.4984 | 0.24399 | 0.019412 | 0.00095922 | 0.018179 | 0.056226 | 0.26738 | -0.0062229 | 0.38132 | 0.0036914 | 2.4248 | 0.10226 | 1.9821 | -0.0030014 | -63.8626 | -1.6159 | -13.0325 | -19.9127 | -1.4191 | -70.7932 | -70.9534 | 3.2501 | 21.2265 | -3.3325 | 51.4252 | 51.3153 | -70.9625 | -70.9625 | 0.027466 | -0.13275 | -52.9175 | 69.2047 | 50.9079 | 51.0406 | -115.361 | -0.14191 | -0.14191 | -0.073242 | 74.0707 | 67.4881 | 67.63 | -0.1831 | 69.4016 | 6.958 | 57.7881 | -122.4518 | 122.2458 | 122.1359 | 92.0471 | -122.4609
4317.0156 | 122.7768 | -88.678 | 33.5541 | 0.16006 | 0.013003 | 0.050306 | -0.031381 | 0.10942 | -0.00029045 | -0.0070773 | 0.18295 | 2.4225 | 0.27532 | 0.11529 | 2.4485 | -0.00065157 | -3.9276 | -3.8956 | -6.395 | -88.1287 | -3.6346 | -88.6826 | -88.9435 | 2.8198 | 4.1153 | -4.1473 | 33.6227 | 33.577 | -88.7512 | -88.6642 | -0.004577 | -0.2655 | -37.1887 | 84.7824 | 0.54932 | 0.81482 | -37.4817 | -0.073242 | 0.013733 | 0.068665 | 91.4978 | 84.5306 | 84.5169 | 0.022888 | 85.0433 | 84.7504 | 82.283 | -122.4976 | 122.3007 | 122.2549 | 92.7933 | -122.2183
4318.0156 | 122.6669 | -90.6052 | 31.7139 | 0.16006 | 0.018985 | 0.052656 | -0.031168 | 0.1107 | 0.0056909 | -0.0062229 | 0.27451 | 2.5157 | 0.12365 | 0.11486 | 2.382 | -0.001506 | -3.7628 | -3.772 | -6.6055 | -89.9734 | -3.511 | -91.0675 | -91.2415 | 2.8061 | 2.1515 | -3.9505 | 31.5445 | 31.8512 | -89.8911 | -89.7537 | -0.46234 | -0.63629 | -35.2249 | 86.8332 | 0.63171 | 1.268 | -35.4767 | 0.71411 | 0.85144 | -0.16937 | 93.4113 | 86.6547 | 85.8032 | 0.13733 | 87.0941 | 86.8423 | 83.9996 | -122.9553 | 122.1497 | 122.4564 | 92.7567 | -121.4676
4319.0156 | 122.5342 | -96.492 | 25.795 | 0.10666 | 0.011294 | 0.054792 | -0.035013 | 0.11326 | 0.23341 | -0.0077183 | 0.27451 | 2.794 | 0.20034 | 0.1202 | 2.4906 | -0.00043797 | -4.0009 | -3.9734 | -6.926 | -53.6179 | -3.7262 | -96.5057 | -96.6064 | 3.2913 | -3.3829 | -3.6804 | 25.6577 | 25.6073 | -96.5744 | -96.5469 | -0.013733 | -0.11444 | -29.5212 | 92.5186 | 42.8741 | 42.9886 | -29.7958 | -0.082398 | -0.054932 | -0.13733 | 99.7833 | 92.8116 | 92.8665 | -0.18768 | 92.7658 | 92.4911 | 89.566 | -122.4014 | 122.1497 | 122.0993 | 93.1091 | -122.3419
4320.0156 | 122.4976 | -105.7846 | 16.5253 | 0.18295 | 0.015567 | 0.0026682 | 0.014334 | 0.084851 | 0.36693 | -0.0057957 | 0.18295 | 3.295 | 0.16937 | 0.12384 | 2.8516 | -0.00065157 | -77.536 | -2.243 | -16.6397 | -47.1771 | -2.0508 | -105.8304 | -105.867 | 3.4836 | -12.7991 | -3.6942 | 16.2918 | 16.2277 | -105.8075 | -105.7846 | -0.045776 | -0.082397 | -18.5761 | 103.5416 | 58.6075 | 58.6899 | -94.0613 | -0.022888 | 0 | -0.23346 | 109.2682 | 102.0905 | 102.0905 | -0.29755 | 103.7338 | 28.2486 | 89.1449 | -122.3923 | 122.0764 | 122.0123 | 92.9855 | -122.3099
4321.0156 | 122.4747 | -109.8358 | 12.4695 | -0.061188 | 0.01044 | 0.005018 | 0.017966 | 0.093823 | 0.43571 | -0.0051547 | -0.00015237 | 3.4571 | 0.19607 | 0.12704 | 2.9531 | 0.00041663 | -72.5052 | -2.3346 | -15.8112 | -38.1821 | -2.1149 | -109.8495 | -109.9457 | 3.0396 | -17.1753 | -2.4628 | 12.2086 | 12.1536 | -109.8587 | -109.8267 | -0.013733 | -0.10986 | -14.5843 | 107.5012 | 71.6537 | 71.7636 | -84.9747 | -0.022889 | 0.009155 | -0.26092 | 112.8754 | 107.373 | 107.3639 | -0.31586 | 107.7209 | 37.3306 | 94.0247 | -122.4152 | 122.0444 | 121.9894 | 92.6605 | -122.2961
4322.0156 | 122.3877 | -109.3002 | 12.9181 | 0.10666 | 0.014499 | 0.0058724 | 0.01583 | 0.60759 | 0.59315 | -0.0066501 | 0.20584 | 4.1646 | 0.26357 | 0.12918 | 3.033 | -0.00022437 | -68.3487 | -2.33 | -14.9689 | -13.2523 | -2.1332 | -109.227 | -109.3689 | 3.9185 | -17.0425 | -0.41199 | 12.6572 | 12.5885 | -109.2957 | -109.3323 | 0.073242 | -0.068664 | -15.0513 | 106.9702 | 96.048 | 96.1166 | -81.2668 | 0.004578 | -0.032043 | -0.26093 | 113.2187 | 108.8882 | 108.9203 | -0.32959 | 107.1671 | 40.9515 | 94.3314 | -122.287 | 121.9574 | 121.8887 | 92.2577 | -122.2504
4323.0156 | 122.4472 | -79.6738 | 42.4942 | 0.045624 | 0.010867 | 0.0075814 | 0.015616 | 0.089764 | 0.43721 | -0.0089999 | 0.25925 | 2.7037 | 0.17492 | 0.10546 | 2.2045 | 0.00020303 | -51.503 | -1.7441 | -10.9268 | -9.6085 | -1.4832 | -79.5502 | -79.6875 | 2.4536 | 11.1191 | -2.7878 | 42.3798 | 42.3248 | -79.7287 | -79.747 | 0.1236 | -0.013733 | -43.9774 | 77.9297 | 70.0653 | 70.079 | -93.9972 | -0.054932 | -0.073242 | -0.11444 | 82.1274 | 76.886 | 76.9592 | -0.16937 | 78.1906 | 28.1708 | 68.7469 | -122.1817 | 122.0535 | 121.9986 | 90.7928 | -122.2412
4324.0156 | 122.4243 | -77.037 | 45.1401 | 0.17532 | 0.014499 | 0.0037362 | 0.015616 | 0.082715 | 0.42631 | -0.0068637 | 0.33554 | 2.5894 | 0.14694 | 0.10482 | 2.093 | -0.0036424 | -50.4181 | -1.6571 | -10.5927 | -9.1095 | -1.4786 | -77.2385 | -77.3392 | 2.4582 | 13.6414 | -2.6733 | 44.8654 | 44.8196 | -77.1652 | -77.1561 | -0.20142 | -0.30212 | -46.6187 | 75.3799 | 67.9276 | 68.2297 | -95.5582 | -0.12817 | -0.11902 | -0.27466 | 79.4952 | 74.3637 | 74.4827 | -0.32044 | 75.5585 | 26.619 | 66.4444 | -122.4792 | 121.9025 | 121.8567 | 90.6784 | -122.2961
4325.0156 | 122.4472 | -83.7753 | 37.9257 | 0.037994 | 0.0097989 | 0.0048044 | 0.013907 | 0.087628 | 0.45494 | -0.0070773 | 0.20584 | 2.775 | 0.13839 | 0.10675 | 2.2355 | -0.001506 | -51.3565 | -1.7395 | -10.7529 | -9.3018 | -1.4969 | -78.9322 | -78.9917 | 2.5543 | 11.1511 | -2.742 | 42.1005 | 40.9012 | -82.6218 | -83.3221 | 4.8431 | 4.7836 | -39.4226 | 82.0358 | 74.4736 | 69.6899 | -89.2822 | 1.1536 | 0.45319 | 4.1748 | 86.3297 | 81.0333 | 80.5801 | 2.9755 | 82.2784 | 32.4188 | 73.0225 | -116.9174 | 125.8759 | 124.6765 | 94.9265 | -121.2479
4326.0156 | 122.4197 | -80.6717 | 41.4093 | 0.16006 | 0.017489 | 0.0024544 | 0.015189 | 0.089551 | 0.47951 | -0.0053683 | 0.2211 | 3.0352 | 0.13305 | 0.10824 | 2.4581 | -0.0040696 | -52.0752 | -1.7441 | -10.9406 | -9.3521 | -1.5701 | -80.5115 | -80.6168 | 0.74616 | 10.6888 | 1.8173 | 41.3589 | 41.272 | -80.7495 | -80.7999 | 0.16022 | 0.054932 | -42.9794 | 78.9276 | 71.3196 | 71.2646 | -93.4845 | -0.07782 | -0.12817 | -0.050354 | 81.4178 | 82.489 | 82.6172 | -0.13733 | 79.1016 | 28.5965 | 69.7311 | -122.0261 | 122.0306 | 121.9437 | 91.3605 | -122.2092
4327.0156 | 122.4426 | -77.6688 | 44.4992 | 0.083771 | 0.011722 | 0.0030954 | 0.016257 | 0.085065 | 0.4387 | -0.010922 | 0.14481 | 2.8404 | 0.12985 | 0.10504 | 2.3062 | -0.0010788 | -50.5554 | -1.7166 | -10.6476 | -8.4824 | -1.4694 | -77.8336 | -77.9297 | 0.76446 | 13.472 | 1.6983 | 44.2795 | 44.2429 | -77.7512 | -77.7328 | -0.16479 | -0.26093 | -45.9686 | 75.9521 | 69.1864 | 69.4473 | -95.0546 | -0.082398 | -0.064087 | -0.21973 | 78.4332 | 79.3671 | 79.4312 | -0.25635 | 76.1993 | 27.1133 | 67.0212 | -122.4289 | 121.9482 | 121.9116 | 91.1407 | -122.2321
4328.0156 | 122.3007 | -82.5623 | 39.4638 | 0.12955 | 0.011935 | 0.0041634 | 0.015189 | 0.11305 | 0.45537 | -0.0068637 | 0.19821 | 2.8583 | 0.12856 | 0.10675 | 2.2772 | 0.00020303 | -10.7346 | -1.7944 | -6.4316 | -8.6197 | -1.5839 | -82.7911 | -82.8598 | 0.88348 | 8.876 | 1.886 | 39.3173 | 39.2899 | -82.7271 | -82.6996 | -0.22888 | -0.29755 | -41.0477 | 80.7678 | 73.9426 | 74.2401 | -50.1984 | -0.16479 | -0.13733 | -0.14648 | 83.4457 | 84.4482 | 84.5856 | -0.17395 | 80.9784 | 71.8277 | 76.1307 | -122.3236 | 121.8796 | 121.8521 | 91.4383 | -122.1634
4329.0156 | 120.0531 | -80.4199 | 41.5604 | -0.076447 | 0.0097989 | 0.0069406 | 0.014548 | 0.11177 | 0.44255 | -0.0098545 | 0.12192 | 2.8242 | 0.11596 | 0.10717 | 2.2475 | -0.0023606 | -10.405 | -1.712 | -6.1752 | -8.4183 | -1.5381 | -80.5847 | -80.7037 | 0.88806 | 11.0184 | 1.9135 | 41.5375 | 41.4963 | -80.4794 | -80.4932 | -0.16479 | -0.28381 | -43.0984 | 78.7079 | 72.0016 | 72.2855 | -51.9653 | -0.059509 | -0.073242 | -0.022888 | 81.308 | 82.3334 | 82.4066 | -0.064087 | 78.8818 | 70.015 | 74.2447 | -122.2641 | 121.9574 | 121.9162 | 91.4383 | -122.0535
4330.0156 | 122.2778 | 6.1981 | 128.2425 | 0.14481 | 0.014071 | 0.0041634 | 0.017966 | 0.016278 | 0.13045 | -0.0070773 | 0.51865 | -0.0025038 | 0.010645 | -0.22458 | 0.12085 | -0.006633 | 0.27008 | 0.3067 | 0.40741 | -2.5818 | 0.49896 | 6.0425 | 6.0516 | 0.2243 | 2.2888 | 0.68665 | 1.4282 | 1.3641 | 6.0699 | 6.0562 | -0.15564 | -0.14648 | -127.7435 | -5.8914 | -8.7799 | -8.6334 | -127.9724 | -0.12817 | -0.14191 | -126.8143 | -5.9738 | -5.5115 | -5.3696 | -126.8784 | -5.6992 | -5.928 | -5.7907 | -122.1909 | -4.7699 | -4.834 | -3.9093 | -122.1863
4331.0156 | 122.5113 | -0.41657 | 121.9803 | -0.00015269 | 0.0093717 | 0.0075814 | 0.016043 | 0.022046 | 0.0016321 | -0.0089999 | 0.20584 | -0.0059216 | 0.010858 | -0.011388 | 0.022153 | -0.0042832 | -0.027466 | 0.041199 | 0.027466 | 0.004578 | 0.24719 | -0.44403 | -0.60425 | 0.054932 | -0.036621 | 0.009155 | 0.1831 | 0.10071 | -0.52643 | -0.54932 | -0.027466 | -0.18768 | -121.7331 | 0.45776 | 0.42114 | 0.60883 | -122.0078 | -0.10986 | -0.13275 | -121.7972 | 0.4715 | 0.42572 | 0.55847 | -121.8796 | 0.66376 | 0.3891 | 0.44403 | -122.5845 | 0.59967 | 0.51727 | 0.37994 | -122.5296
4332.0156 | 122.5296 | -0.39825 | 122.0261 | 0.19058 | 0.01514 | 0.0024544 | 0.016898 | 0.02525 | 0.0018457 | -0.0077183 | 0.18295 | -0.0052808 | 0.013208 | -0.0098929 | 0.023221 | -0.0053512 | 0.027466 | 0.091553 | 0.068665 | -0.004578 | 0.23804 | -0.42572 | -0.6134 | 0.064087 | -0.045776 | -0.009155 | 0.16937 | 0.10071 | -0.54474 | -0.5722 | -0.027466 | -0.21515 | -121.788 | 0.48981 | 0.39368 | 0.60883 | -121.9986 | -0.14648 | -0.17395 | -121.8567 | 0.46234 | 0.3891 | 0.56305 | -121.9254 | 0.63629 | 0.42572 | 0.46692 | -122.6395 | 0.56763 | 0.49896 | 0.35248 | -122.5983
4333.0156 | 122.5571 | -0.42572 | 122.081 | 0.060882 | 0.01044 | 0.0054452 | 0.013907 | 0.027814 | 0.00013675 | -0.0094273 | 0.083771 | -0.0044264 | 0.012781 | -0.01032 | 0.020871 | -0.0057786 | -0.013733 | 0.045776 | 0.068665 | -0.013733 | 0.24261 | -0.43945 | -0.63629 | 0.013733 | -0.068665 | -0.013733 | 0.16022 | 0.086975 | -0.54016 | -0.56305 | -0.013733 | -0.21057 | -121.8384 | 0.4715 | 0.41199 | 0.62256 | -122.0947 | -0.11444 | -0.13733 | -121.9208 | 0.43945 | 0.41199 | 0.54932 | -121.994 | 0.66834 | 0.41199 | 0.49438 | -122.7173 | 0.58594 | 0.5127 | 0.35706 | -122.644
4334.0156 | 122.5662 | -0.41657 | 122.0947 | 0.14481 | 0.012149 | 0.0054452 | 0.016898 | 0.026532 | 0.0022729 | -0.0079319 | 0.15244 | -0.0059216 | 0.011499 | -0.0096793 | 0.023434 | -0.0062058 | 0.013733 | 0.054932 | 0.064087 | -0.027466 | 0.25635 | -0.40741 | -0.61798 | 0.036621 | -0.082397 | -0.022888 | 0.16022 | 0.091553 | -0.54016 | -0.56763 | 0.009155 | -0.20142 | -121.8384 | 0.4715 | 0.3891 | 0.59052 | -122.081 | -0.1236 | -0.15106 | -121.9345 | 0.45319 | 0.39368 | 0.54474 | -122.0032 | 0.67291 | 0.4303 | 0.48065 | -122.7127 | 0.57678 | 0.50812 | 0.33417 | -122.6624
4335.0156 | 122.5479 | -0.44403 | 122.1268 | -0.22141 | 0.012149 | 0.006086 | 0.016043 | 0.028027 | 0.0014185 | -0.0085727 | -0.25192 | -0.0035718 | 0.012995 | -0.011175 | 0.021725 | -0.0081284 | 0.036621 | 0.10071 | 0.086975 | -0.009155 | 0.27008 | -0.44861 | -0.64545 | 0.013733 | -0.054932 | -0.054932 | 0.15564 | 0.10986 | -0.5722 | -0.58594 | -0.004577 | -0.20142 | -121.8567 | 0.54474 | 0.43488 | 0.63629 | -122.0901 | -0.12817 | -0.14191 | -121.9711 | 0.45776 | 0.3891 | 0.53101 | -122.0169 | 0.71411 | 0.48065 | 0.53101 | -122.7722 | 0.59967 | 0.55389 | 0.3891 | -122.7127
4336.0156 | 122.6212 | -0.42572 | 122.1039 | 0.045624 | 0.0095853 | 0.0035226 | 0.014975 | 0.0276 | 0.0027001 | -0.010282 | 0.030365 | -0.0061352 | 0.012781 | -0.010106 | 0.02258 | -0.0059922 | -0.018311 | 0.064087 | 0.082397 | -0.013733 | 0.27466 | -0.45319 | -0.64087 | 0.032043 | -0.082397 | -0.032043 | 0.14648 | 0.086975 | -0.55847 | -0.58594 | -0.027466 | -0.21515 | -121.8292 | 0.48981 | 0.41199 | 0.62714 | -122.1222 | -0.13275 | -0.16022 | -121.9574 | 0.45776 | 0.39368 | 0.55389 | -122.0169 | 0.70038 | 0.40741 | 0.50812 | -122.7448 | 0.5722 | 0.5127 | 0.34332 | -122.6898
4337.0156 | 122.6486 | -0.42572 | 122.113 | -0.17563 | 0.010226 | 0.0056588 | 0.014548 | 0.0276 | 0.00099115 | -0.010282 | -0.25955 | -0.0044264 | 0.013208 | -0.012029 | 0.023434 | -0.0068466 | 0.041199 | 0.14191 | 0.11902 | 0.013733 | 0.27008 | -0.46692 | -0.63171 | 0.050354 | -0.013733 | -0.013733 | 0.15106 | 0.068665 | -0.55847 | -0.56763 | -0.041199 | -0.20599 | -121.843 | 0.56763 | 0.43945 | 0.64545 | -122.0718 | -0.13275 | -0.14191 | -121.962 | 0.47607 | 0.41199 | 0.55389 | -122.0444 | 0.6958 | 0.46692 | 0.54474 | -122.7448 | 0.57678 | 0.49438 | 0.41199 | -122.6807
4338.0156 | 122.644 | -0.45776 | 122.1039 | -0.023041 | 0.0095853 | 0.0073678 | 0.016257 | 0.024823 | -0.0015723 | -0.0089999 | -0.0077819 | -0.0042126 | 0.01214 | -0.010747 | 0.022794 | -0.005565 | -0.009155 | 0.064087 | 0.091553 | -0.027466 | 0.27008 | -0.46234 | -0.6546 | 0.018311 | -0.091553 | -0.036621 | 0.13733 | 0.064087 | -0.57678 | -0.59967 | -0.004577 | -0.19684 | -121.8338 | 0.52185 | 0.4303 | 0.62714 | -122.113 | -0.11902 | -0.14191 | -121.9666 | 0.47608 | 0.42114 | 0.56305 | -122.0398 | 0.72785 | 0.44861 | 0.54932 | -122.7585 | 0.59509 | 0.52185 | 0.36621 | -122.7036
4339.0156 | 122.7081 | -0.48523 | 122.0856 | -0.061188 | 0.010226 | 0.0054452 | 0.015189 | 0.026746 | -0.0017859 | -0.0087863 | -0.053558 | -0.0059216 | 0.013422 | -0.012029 | 0.023862 | -0.0068466 | 0.018311 | 0.10986 | 0.13275 | -0.32959 | 0.25635 | -0.51727 | -0.70038 | 0.064087 | -0.064087 | -0.018311 | 0.10986 | 0.036621 | -0.6134 | -0.63629 | -0.032044 | -0.21515 | -121.8292 | 0.59509 | 0.15564 | 0.37079 | -122.0673 | -0.12817 | -0.15106 | -121.9757 | 0.54932 | 0.46692 | 0.61798 | -122.049 | 0.74158 | 0.50354 | 0.61798 | -122.7859 | 0.59509 | 0.52185 | 0.42114 | -122.7219
4340.0156 | 122.6303 | -0.54474 | 122.0947 | -0.19852 | 0.01578 | 0.0037362 | 0.022238 | 0.024609 | 0.0061181 | -0.0077183 | -0.35873 | -0.0018628 | 0.016626 | -0.010534 | 0.024075 | -0.0053512 | -0.018311 | -0.013733 | 0.027466 | -0.37079 | 0.28839 | -0.58594 | -0.73242 | -0.036621 | -0.17395 | -0.16479 | 0.15106 | 0.059509 | -0.65918 | -0.67749 | -0.041198 | -0.18768 | -121.8063 | 0.53101 | 0.17395 | 0.36163 | -122.113 | -0.11444 | -0.13275 | -121.9437 | 0.50812 | 0.37994 | 0.5127 | -122.0352 | 0.83313 | 0.52643 | 0.5722 | -122.8271 | 0.6958 | 0.60425 | 0.37079 | -122.7722
4341.0156 | 122.7127 | -0.44403 | 122.1405 | -0.17563 | 0.010867 | 0.0045908 | 0.014975 | 0.02525 | -0.0028541 | -0.0098545 | -0.19089 | -0.0054944 | 0.010431 | -0.010961 | 0.022366 | -0.0044968 | 0.027466 | 0.16022 | 0.16022 | -0.004578 | 0.27008 | -0.48065 | -0.66376 | 0.064087 | -0.027466 | -0.027466 | 0.10529 | 0.036621 | -0.58594 | -0.59967 | -0.036621 | -0.21973 | -121.8704 | 0.60425 | 0.43945 | 0.65918 | -122.113 | -0.14191 | -0.15564 | -122.0352 | 0.50812 | 0.41657 | 0.5722 | -122.1039 | 0.71411 | 0.4715 | 0.60425 | -122.8043 | 0.54932 | 0.48065 | 0.41657 | -122.7402
4342.0156 | 122.731 | -0.48981 | 122.0764 | -0.053558 | 0.010653 | 0.005018 | 0.014121 | 0.022687 | -0.00071785 | -0.0092137 | -0.099335 | -0.003999 | 0.012995 | -0.011175 | 0.025143 | -0.0057786 | 0.018311 | 0.13275 | 0.12817 | -0.33875 | 0.27924 | -0.52643 | -0.72327 | 0.082397 | -0.068665 | -0.013733 | 0.09613 | 0.009155 | -0.63171 | -0.65002 | -0.036621 | -0.23346 | -121.7972 | 0.62256 | 0.15106 | 0.38452 | -122.0581 | -0.14191 | -0.16022 | -121.9803 | 0.5722 | 0.47607 | 0.63629 | -122.0673 | 0.76904 | 0.50812 | 0.61798 | -122.7997 | 0.58594 | 0.49896 | 0.42114 | -122.7264
4343.0156 | 122.6715 | -0.43488 | 122.1451 | -0.19852 | 0.010013 | 0.0058724 | 0.018179 | 0.0276 | 0.0024865 | -0.0083591 | -0.27481 | -0.003999 | 0.012567 | -0.012456 | 0.02258 | -0.0064194 | 0.027466 | 0.11902 | 0.14648 | 0.004578 | 0.27924 | -0.50354 | -0.68665 | 0.032043 | -0.07782 | -0.064087 | 0.13275 | 0.054932 | -0.60425 | -0.6134 | -0.068665 | -0.25177 | -121.8658 | 0.55389 | 0.43945 | 0.69122 | -122.1176 | -0.16937 | -0.17853 | -122.0123 | 0.46692 | 0.37079 | 0.54932 | -122.0901 | 0.71411 | 0.46234 | 0.58136 | -122.8317 | 0.56763 | 0.48981 | 0.35706 | -122.7585
4344.0156 | 122.7448 | -0.45319 | 122.1405 | -0.076447 | 0.0087307 | 0.0062998 | 0.01583 | 0.027814 | 0.0014185 | -0.0083591 | -0.038299 | -0.0050672 | 0.010004 | -0.010961 | 0.023434 | -0.0072738 | 0.022888 | 0.13733 | 0.16022 | 0.009155 | 0.26093 | -0.47607 | -0.66834 | 0.082397 | -0.036621 | -0.004578 | 0.10529 | 0.036621 | -0.57678 | -0.59052 | -0.022888 | -0.21515 | -121.8796 | 0.59052 | 0.46234 | 0.67749 | -122.1176 | -0.1236 | -0.13733 | -122.0352 | 0.53558 | 0.44861 | 0.58594 | -122.1039 | 0.71411 | 0.47607 | 0.6134 | -122.8088 | 0.55847 | 0.48981 | 0.41656 | -122.731
4345.0312 | 122.6303 | -0.55389 | 122.1176 | 0.17532 | 0.020267 | 0.0013864 | 0.019248 | 0.026105 | 0.0041955 | -0.0087863 | 0.076141 | -0.0033582 | 0.017053 | -0.0090385 | 0.025784 | -0.0074876 | -0.013733 | -0.004578 | 0.032043 | -0.38452 | 0.29755 | -0.56763 | -0.74158 | -0.009155 | -0.21973 | -0.16479 | 0.11902 | 0.054932 | -0.68207 | -0.68207 | -0.013733 | -0.18768 | -121.8201 | 0.54932 | 0.16937 | 0.35706 | -122.1313 | -0.12817 | -0.12817 | -121.9986 | 0.54474 | 0.3891 | 0.51727 | -122.0627 | 0.85144 | 0.54016 | 0.58594 | -122.8592 | 0.67291 | 0.60883 | 0.33417 | -122.7997
4346.0156 | 122.7173 | -0.53101 | 122.1222 | -0.0383 | 0.0097989 | 0.0041634 | 0.015616 | 0.025677 | -0.0028541 | -0.0087863 | -0.0077819 | -0.0048536 | 0.010645 | -0.010961 | 0.023007 | -0.003215 | -0.009155 | 0.10071 | 0.1236 | -0.35248 | 0.27466 | -0.54932 | -0.71411 | 0.036621 | -0.10986 | -0.045776 | 0.10529 | 0.036621 | -0.64545 | -0.67291 | -0.01831 | -0.18311 | -121.8475 | 0.63171 | 0.17853 | 0.36163 | -122.1313 | -0.11444 | -0.14191 | -122.0169 | 0.56763 | 0.48523 | 0.62714 | -122.0856 | 0.80566 | 0.52185 | 0.6546 | -122.8363 | 0.63629 | 0.56763 | 0.42114 | -122.7951
4347.0156 | 122.6532 | -0.56305 | 122.1451 | -0.23666 | 0.012362 | 0.0045908 | 0.017325 | 0.026532 | -0.00093145 | -0.0089999 | -0.29007 | -0.0033582 | 0.015558 | -0.0088247 | 0.023648 | -0.0047104 | -0.027466 | 0.004578 | 0.050354 | -0.41199 | 0.28839 | -0.56305 | -0.75073 | -0.059509 | -0.20599 | -0.16937 | 0.1236 | 0.068665 | -0.67291 | -0.70496 | 0 | -0.18768 | -121.8567 | 0.56763 | 0.15106 | 0.33874 | -122.1725 | -0.10986 | -0.14191 | -122.0215 | 0.50354 | 0.39368 | 0.53558 | -122.0764 | 0.85144 | 0.53558 | 0.6134 | -122.8958 | 0.68665 | 0.63171 | 0.35706 | -122.85
4348.0156 | 122.7631 | -0.52643 | 122.113 | -0.068817 | 0.011294 | 0.0054452 | 0.014334 | 0.027386 | -0.0015723 | -0.0083591 | -0.13748 | -0.0044264 | 0.012567 | -0.010534 | 0.023648 | -0.0044968 | 0.036621 | 0.16022 | 0.16022 | -0.32959 | 0.2655 | -0.53101 | -0.72784 | 0.07782 | -0.054932 | -0.009155 | 0.086975 | 0.022888 | -0.63629 | -0.65002 | -0.004578 | -0.20142 | -121.8475 | 0.68664 | 0.19684 | 0.39825 | -122.0764 | -0.10986 | -0.1236 | -122.0261 | 0.60425 | 0.51727 | 0.64087 | -122.0901 | 0.79193 | 0.56305 | 0.68664 | -122.8409 | 0.6134 | 0.54932 | 0.4715 | -122.7631
4349.0156 | 122.6257 | -0.49896 | 122.2229 | -0.20615 | 0.014499 | 0.0048044 | 0.016684 | 0.026532 | 0.0033411 | -0.0098545 | -0.29007 | -0.0050672 | 0.01214 | -0.011175 | 0.023007 | -0.0040696 | -0.045776 | 0.032043 | 0.041199 | -0.064087 | 0.31586 | -0.51727 | -0.70496 | -0.050354 | -0.16479 | -0.15106 | 0.16479 | 0.073242 | -0.62256 | -0.64545 | -0.018311 | -0.20599 | -121.907 | 0.53101 | 0.43488 | 0.64087 | -122.2687 | -0.1236 | -0.14648 | -122.0581 | 0.44861 | 0.3479 | 0.49438 | -122.1497 | 0.81482 | 0.45319 | 0.54016 | -122.9279 | 0.66376 | 0.5722 | 0.33417 | -122.8683
4350.0156 | 122.6578 | -0.48065 | 122.2366 | -0.061188 | 0.019412 | 0.0011728 | 0.01882 | 0.025037 | 0.0054773 | -0.0066501 | -0.091705 | -0.0018628 | 0.015772 | -0.012029 | 0.024503 | -0.006633 | 0.022888 | 0.054932 | 0.054932 | -0.041199 | 0.29297 | -0.5127 | -0.69122 | -0.013733 | -0.16937 | -0.15564 | 0.13733 | 0.086975 | -0.58594 | -0.62714 | -0.032043 | -0.21057 | -121.9437 | 0.53558 | 0.43945 | 0.65002 | -122.2137 | -0.10529 | -0.14648 | -122.0993 | 0.46692 | 0.32501 | 0.4715 | -122.1497 | 0.77362 | 0.50354 | 0.53558 | -122.9279 | 0.61798 | 0.56763 | 0.31128 | -122.8638
4351.0156 | 122.6624 | -0.49896 | 122.2549 | -0.21378 | 0.016635 | 0.0030954 | 0.019461 | 0.02525 | 0.0020593 | -0.0075047 | -0.27481 | -0.0050672 | 0.015131 | -0.010534 | 0.023221 | -0.0057786 | -0.041199 | 0.018311 | 0.036621 | -0.068665 | 0.32501 | -0.51727 | -0.71869 | -0.045776 | -0.16479 | -0.14191 | 0.14648 | 0.073242 | -0.6134 | -0.6546 | -0.018311 | -0.21973 | -121.9299 | 0.51727 | 0.4303 | 0.65002 | -122.2961 | -0.11444 | -0.15564 | -122.1085 | 0.45319 | 0.35706 | 0.5127 | -122.1817 | 0.82397 | 0.45776 | 0.53558 | -122.9736 | 0.64545 | 0.5722 | 0.33417 | -122.9095
4352.0156 | 122.7539 | -0.5127 | 122.1634 | -0.19852 | 0.010653 | 0.005018 | 0.014121 | 0.02525 | -0.0041357 | -0.0079319 | -0.17563 | -0.003999 | 0.012781 | -0.010747 | 0.024503 | -0.0040696 | 0.004578 | 0.16022 | 0.14191 | -0.33417 | 0.27008 | -0.54474 | -0.72784 | 0.032043 | -0.068665 | -0.050354 | 0.07782 | 0.036621 | -0.63629 | -0.65918 | -0.032044 | -0.21515 | -121.8933 | 0.67291 | 0.17853 | 0.39368 | -122.1588 | -0.1236 | -0.14648 | -122.0856 | 0.54474 | 0.46234 | 0.60883 | -122.1268 | 0.78278 | 0.51727 | 0.6546 | -122.8912 | 0.59052 | 0.54932 | 0.44403 | -122.8226
4353.0156 | 122.6807 | -0.47607 | 122.2733 | -0.25192 | 0.01279 | 0.0045908 | 0.016684 | 0.027814 | 0.0012047 | -0.010282 | -0.2214 | -0.0059216 | 0.014704 | -0.010534 | 0.023007 | -0.0025742 | -0.022888 | 0.10529 | 0.091553 | 0 | 0.28839 | -0.49896 | -0.68207 | -0.032043 | -0.14191 | -0.1236 | 0.13733 | 0.082397 | -0.60883 | -0.62256 | -0.022888 | -0.20599 | -121.9849 | 0.58136 | 0.47607 | 0.68207 | -122.2961 | -0.13275 | -0.14648 | -122.1359 | 0.44403 | 0.35248 | 0.49896 | -122.1909 | 0.76446 | 0.45319 | 0.56763 | -122.9553 | 0.6134 | 0.55847 | 0.33417 | -122.8958
4354.0156 | 122.7676 | -0.46234 | 122.2458 | -0.21378 | 0.010013 | 0.0037362 | 0.01348 | 0.024396 | -0.00071785 | -0.0092137 | -0.20615 | -0.005708 | 0.012995 | -0.0096793 | 0.023648 | -0.0062058 | 0.018311 | 0.13275 | 0.16937 | 0.013733 | 0.28381 | -0.4715 | -0.6546 | 0.022888 | -0.059509 | -0.054932 | 0.10071 | 0.054932 | -0.58136 | -0.6134 | -0.009156 | -0.19226 | -121.962 | 0.59509 | 0.47607 | 0.66834 | -122.2275 | -0.11902 | -0.15106 | -122.1451 | 0.48523 | 0.40741 | 0.55847 | -122.1909 | 0.74615 | 0.48065 | 0.63171 | -122.9004 | 0.56305 | 0.51727 | 0.40283 | -122.8592
4355.0156 | 122.6852 | -0.53558 | 122.1771 | 0.17532 | 0.01813 | 0.0030954 | 0.016257 | 0.024396 | 0.0039819 | -0.0066501 | 0.083771 | -0.002931 | 0.015558 | -0.0090385 | 0.027066 | -0.004924 | -0.036621 | -0.009155 | 0.013733 | -0.39825 | 0.3067 | -0.55847 | -0.74616 | -0.027466 | -0.24261 | -0.17395 | 0.14191 | 0.054932 | -0.66834 | -0.69122 | -0.022889 | -0.21057 | -121.8704 | 0.52643 | 0.13733 | 0.3479 | -122.2137 | -0.13275 | -0.15564 | -122.0352 | 0.50812 | 0.36163 | 0.51727 | -122.1222 | 0.84228 | 0.49896 | 0.54932 | -122.9233 | 0.67749 | 0.59052 | 0.29297 | -122.8683
4356.0156 | 122.699 | -0.53558 | 122.2229 | -0.25192 | 0.012149 | 0.0043772 | 0.017966 | 0.0276 | -0.00071785 | -0.0087863 | -0.2977 | -0.0037854 | 0.014276 | -0.0094657 | 0.024075 | -0.0044968 | -0.027466 | 0.050354 | 0.064087 | -0.050354 | 0.30212 | -0.54474 | -0.72327 | -0.068665 | -0.16022 | -0.13275 | 0.13733 | 0.073242 | -0.64545 | -0.67291 | -0.009156 | -0.18768 | -121.9208 | 0.58594 | 0.48523 | 0.67291 | -122.2504 | -0.10986 | -0.13733 | -122.0856 | 0.46692 | 0.40283 | 0.54016 | -122.1497 | 0.83771 | 0.50812 | 0.59967 | -122.9462 | 0.67291 | 0.60883 | 0.37537 | -122.8958
4357.0156 | 122.6944 | -0.48981 | 122.2961 | -0.168 | 0.016208 | 0.0041634 | 0.016684 | 0.024396 | 0.0037683 | -0.0075047 | -0.19089 | -0.0027174 | 0.014276 | -0.014165 | 0.02493 | -0.006633 | -0.041199 | 0.022888 | 0.036621 | -0.045776 | 0.31586 | -0.52643 | -0.70496 | -0.045776 | -0.14191 | -0.13733 | 0.15564 | 0.086975 | -0.62256 | -0.62256 | -0.036621 | -0.21515 | -121.9803 | 0.5127 | 0.44403 | 0.65918 | -122.3373 | -0.13275 | -0.13275 | -122.1405 | 0.44403 | 0.35248 | 0.48523 | -122.2092 | 0.80566 | 0.44861 | 0.52643 | -123.0011 | 0.64545 | 0.57678 | 0.3479 | -122.9187
4358.0156 | 122.6852 | -0.49439 | 122.2824 | -0.28244 | 0.01514 | 0.0052316 | 0.014121 | 0.025677 | -0.0019995 | -0.0083591 | -0.24429 | -0.0037854 | 0.015344 | -0.0094657 | 0.021298 | -0.0070602 | -0.059509 | 0.054932 | 0.054932 | -0.045776 | 0.32044 | -0.5127 | -0.6958 | -0.064087 | -0.16022 | -0.14191 | 0.14648 | 0.10071 | -0.62714 | -0.63629 | -0.01831 | -0.20142 | -121.962 | 0.54932 | 0.44861 | 0.65002 | -122.3419 | -0.13275 | -0.14191 | -122.1359 | 0.4303 | 0.35248 | 0.49438 | -122.1817 | 0.81482 | 0.43488 | 0.54932 | -122.9782 | 0.64087 | 0.59509 | 0.33417 | -122.9187
4359.0156 | 122.7264 | -0.48981 | 122.2824 | -0.20615 | 0.017489 | 0.0037362 | 0.017325 | 0.02525 | 0.0044091 | -0.0081455 | -0.23666 | -0.0037854 | 0.01449 | -0.011815 | 0.023862 | -0.0051376 | -0.036621 | 0.032043 | 0.050354 | -0.027466 | 0.3067 | -0.5127 | -0.70496 | -0.036621 | -0.13275 | -0.11902 | 0.15106 | 0.07782 | -0.61798 | -0.63171 | -0.022888 | -0.21515 | -121.9757 | 0.52185 | 0.46234 | 0.67749 | -122.319 | -0.12817 | -0.14191 | -122.1313 | 0.45319 | 0.37079 | 0.5127 | -122.2046 | 0.79651 | 0.45319 | 0.54016 | -122.9874 | 0.64087 | 0.56763 | 0.35706 | -122.9141
4360.0156 | 122.7264 | -0.46692 | 122.2687 | -0.19089 | 0.012362 | 0.0035226 | 0.014761 | 0.027173 | -0.0017859 | -0.0098545 | -0.18326 | -0.0044264 | 0.011499 | -0.0096793 | 0.022153 | -0.0027878 | -0.013733 | 0.10986 | 0.11902 | 0.004578 | 0.27466 | -0.48523 | -0.65918 | -0.027466 | -0.10529 | -0.07782 | 0.14191 | 0.059509 | -0.58594 | -0.64087 | -0.01831 | -0.19226 | -121.994 | 0.57678 | 0.4715 | 0.66376 | -122.2824 | -0.11902 | -0.17395 | -122.1268 | 0.43945 | 0.3891 | 0.56305 | -122.2092 | 0.74158 | 0.45319 | 0.58594 | -122.9279 | 0.60883 | 0.52643 | 0.36163 | -122.9095
4361.0156 | 122.7402 | -0.48065 | 122.2916 | -0.22141 | 0.017703 | 0.005018 | 0.016257 | 0.02525 | 0.0020593 | -0.0098545 | -0.2214 | -0.0020764 | 0.014917 | -0.012243 | 0.024289 | -0.0051376 | -0.032043 | 0.004578 | 0.032043 | -0.032043 | 0.3067 | -0.51727 | -0.70496 | -0.068665 | -0.1831 | -0.14191 | 0.16479 | 0.07782 | -0.59967 | -0.63629 | -0.036621 | -0.2243 | -121.9849 | 0.48523 | 0.44861 | 0.67291 | -122.3236 | -0.11902 | -0.15564 | -122.1268 | 0.41199 | 0.33875 | 0.49438 | -122.2137 | 0.78735 | 0.44861 | 0.5127 | -122.9965 | 0.64545 | 0.55847 | 0.29755 | -122.9279
4362.0156 | 122.6715 | -0.52185 | 122.3282 | -0.21378 | 0.014285 | 0.006086 | 0.017752 | 0.026532 | -0.00093145 | -0.010709 | -0.2214 | -0.0025038 | 0.014063 | -0.013097 | 0.023862 | -0.0030014 | -0.059509 | 0.009155 | 0.032043 | -0.050354 | 0.31586 | -0.51727 | -0.70496 | -0.068665 | -0.17853 | -0.13733 | 0.15106 | 0.07782 | -0.61798 | -0.63171 | 0.004578 | -0.18311 | -122.0123 | 0.53101 | 0.4715 | 0.6546 | -122.3877 | -0.09613 | -0.10986 | -122.1771 | 0.45319 | 0.38452 | 0.49438 | -122.2504 | 0.83771 | 0.46234 | 0.55389 | -123.0331 | 0.67291 | 0.59967 | 0.34332 | -122.9599
4363.0156 | 122.731 | -0.4715 | 122.3145 | -0.084076 | 0.018985 | 0.0022408 | 0.017752 | 0.026318 | 0.0065453 | -0.0079319 | -0.10696 | 0.00027344 | 0.014917 | -0.0077567 | 0.023434 | -0.0072738 | 0.032043 | 0.045776 | 0.068665 | -0.004578 | 0.32501 | -0.49896 | -0.67291 | -0.004578 | -0.16479 | -0.14648 | 0.13733 | 0.068665 | -0.60425 | -0.63171 | -0.027465 | -0.20142 | -121.9894 | 0.51727 | 0.46692 | 0.66834 | -122.2824 | -0.13275 | -0.16022 | -122.1771 | 0.46692 | 0.32501 | 0.48523 | -122.2458 | 0.79651 | 0.50354 | 0.54016 | -122.9874 | 0.60883 | 0.54016 | 0.3067 | -122.9462
4364.0156 | 122.7219 | -0.49896 | 122.3053 | -0.24429 | 0.016421 | 0.0048044 | 0.018393 | 0.027173 | 0.0031273 | -0.0089999 | -0.24429 | -0.0014356 | 0.015558 | -0.011815 | 0.023648 | -0.0042832 | -0.059509 | -0.004578 | 0.041199 | -0.027466 | 0.3067 | -0.50354 | -0.70953 | -0.073242 | -0.16937 | -0.14648 | 0.15564 | 0.086975 | -0.61798 | -0.62714 | -0.004578 | -0.21057 | -121.9986 | 0.49438 | 0.4715 | 0.68207 | -122.3648 | -0.11902 | -0.12817 | -122.1497 | 0.42572 | 0.35248 | 0.48065 | -122.2183 | 0.80566 | 0.43945 | 0.54016 | -123.0148 | 0.6546 | 0.58594 | 0.32959 | -122.9324
4365.0156 | 122.7036 | -0.54932 | 122.2504 | -0.015411 | 0.019626 | 0.0037362 | 0.016257 | 0.026318 | 0.0039819 | -0.0072911 | 0.015106 | -0.00036736 | 0.015772 | -0.010747 | 0.026212 | -0.0053512 | -0.041199 | 0.009155 | 0.036621 | -0.4303 | 0.3067 | -0.56763 | -0.75073 | -0.050354 | -0.23346 | -0.18768 | 0.11902 | 0.045776 | -0.67291 | -0.6958 | -0.018311 | -0.20142 | -121.9437 | 0.55847 | 0.11902 | 0.32043 | -122.2916 | -0.1236 | -0.14648 | -122.1313 | 0.49896 | 0.36163 | 0.50812 | -122.2046 | 0.85602 | 0.50812 | 0.58594 | -123.0011 | 0.66834 | 0.59509 | 0.31586 | -122.9462
4366.0156 | 122.7402 | -0.54932 | 122.2733 | -0.18326 | 0.017276 | 0.0045908 | 0.018393 | 0.024823 | -7.6852e-05 | -0.0092137 | -0.23666 | -0.0031446 | 0.017267 | -0.0086111 | 0.024289 | -0.004924 | -0.068665 | 0.018311 | 0.027466 | -0.31586 | 0.28839 | -0.54932 | -0.74616 | -0.086975 | -0.17395 | -0.16479 | 0.10071 | 0.059509 | -0.65918 | -0.69122 | 0 | -0.19684 | -121.9849 | 0.56763 | 0.23346 | 0.4303 | -122.3419 | -0.10986 | -0.14191 | -122.1725 | 0.46234 | 0.38452 | 0.52643 | -122.2137 | 0.83771 | 0.48065 | 0.57678 | -123.0194 | 0.65002 | 0.60883 | 0.37537 | -122.9645
4367.0156 | 122.7539 | -0.52185 | 122.2549 | -0.15274 | 0.017703 | 0.0039498 | 0.016257 | 0.024182 | 0.00099115 | -0.0070773 | -0.084076 | -0.0014356 | 0.015344 | -0.012243 | 0.023221 | -0.0040696 | -0.022888 | 0.064087 | 0.064087 | -0.27924 | 0.32044 | -0.55847 | -0.73242 | -0.027466 | -0.16479 | -0.14648 | 0.12817 | 0.050354 | -0.63629 | -0.67291 | -0.036621 | -0.21057 | -121.9345 | 0.58594 | 0.24261 | 0.45319 | -122.2778 | -0.11444 | -0.15106 | -122.1268 | 0.49438 | 0.37537 | 0.52643 | -122.2046 | 0.84229 | 0.49896 | 0.58594 | -122.9874 | 0.65002 | 0.5722 | 0.35706 | -122.9279
4368.0156 | 122.7539 | -0.52643 | 122.2824 | -0.25955 | 0.018344 | 0.0052316 | 0.016684 | 0.026959 | 0.00077755 | -0.0079319 | -0.21378 | -0.001222 | 0.014063 | -0.010534 | 0.024503 | -0.0044968 | -0.064087 | 0.004578 | 0.036621 | -0.23804 | 0.3067 | -0.53558 | -0.73242 | -0.059509 | -0.17853 | -0.14191 | 0.11902 | 0.07782 | -0.65918 | -0.64545 | -0.009155 | -0.20599 | -121.9757 | 0.53101 | 0.28839 | 0.49439 | -122.3465 | -0.13275 | -0.11902 | -122.1634 | 0.46692 | 0.38452 | 0.50354 | -122.2046 | 0.83313 | 0.46234 | 0.56305 | -123.0148 | 0.64545 | 0.60425 | 0.3479 | -122.9279
4369.0156 | 122.7585 | -0.53101 | 122.2778 | -0.068817 | 0.018558 | 0.0028818 | 0.016898 | 0.025464 | 0.0024865 | -0.0096409 | -0.053558 | -0.0044264 | 0.015558 | -0.01032 | 0.025143 | -0.0044968 | 0.004578 | 0.032043 | 0.068665 | -0.23346 | 0.29755 | -0.53558 | -0.72784 | -0.036621 | -0.18768 | -0.16937 | 0.11444 | 0.045776 | -0.65002 | -0.65918 | -0.004577 | -0.19684 | -121.9803 | 0.56305 | 0.29755 | 0.49439 | -122.2733 | -0.11902 | -0.12817 | -122.1634 | 0.49438 | 0.36163 | 0.48981 | -122.2321 | 0.82855 | 0.53558 | 0.59967 | -123.0057 | 0.64545 | 0.57678 | 0.34332 | -122.937
4370.0156 | 122.7585 | -0.52643 | 122.2916 | -0.068817 | 0.019412 | 0.0043772 | 0.018179 | 0.024609 | 0.00099115 | -0.0055821 | -0.061188 | -0.0027174 | 0.015985 | -0.010747 | 0.026425 | -0.004924 | -0.009155 | 0.050354 | 0.064087 | -0.25177 | 0.31128 | -0.53558 | -0.70953 | -0.022888 | -0.15564 | -0.14191 | 0.1236 | 0.054932 | -0.65002 | -0.67291 | -0.009155 | -0.18311 | -121.9803 | 0.57678 | 0.27466 | 0.45776 | -122.3007 | -0.1236 | -0.14648 | -122.168 | 0.50354 | 0.38452 | 0.53101 | -122.2366 | 0.83771 | 0.51727 | 0.59052 | -123.0011 | 0.65002 | 0.58136 | 0.37079 | -122.9645
4371.0156 | 122.7264 | -0.54016 | 122.2778 | -0.00015269 | 0.019839 | 0.0016 | 0.019461 | 0.026318 | 0.0014185 | -0.0075047 | 0.045624 | -0.0018628 | 0.018122 | -0.0094657 | 0.02493 | -0.0044968 | -0.036621 | -0.009155 | 0.027466 | -0.28381 | 0.29297 | -0.54932 | -0.72784 | -0.091553 | -0.19684 | -0.21515 | 0.1236 | 0.064087 | -0.65002 | -0.65918 | -0.009155 | -0.18768 | -121.9849 | 0.53101 | 0.25635 | 0.44403 | -122.3145 | -0.10986 | -0.11902 | -122.1542 | 0.44861 | 0.32501 | 0.44403 | -122.2137 | 0.83313 | 0.50354 | 0.56763 | -123.0057 | 0.66376 | 0.60425 | 0.34332 | -122.937
4372.0156 | 122.7448 | -0.51727 | 122.2916 | -0.061188 | 0.02048 | 0.0041634 | 0.016898 | 0.02525 | 0.0039819 | -0.0079319 | -0.084076 | -0.0014356 | 0.014917 | -0.0098929 | 0.025571 | -0.0062058 | 0 | 0.041199 | 0.050354 | -0.27008 | 0.3067 | -0.54016 | -0.71411 | -0.032043 | -0.16479 | -0.14191 | 0.10986 | 0.059509 | -0.62714 | -0.67291 | -0.022888 | -0.19684 | -121.9849 | 0.55847 | 0.24719 | 0.44403 | -122.2916 | -0.10986 | -0.15564 | -122.1817 | 0.48523 | 0.37537 | 0.53101 | -122.2321 | 0.82397 | 0.51727 | 0.56763 | -123.0057 | 0.62714 | 0.57678 | 0.35248 | -122.9645
4373.0156 | 122.731 | -0.54474 | 122.2687 | 0.16769 | 0.020907 | 0.0062998 | 0.015616 | 0.024609 | 0.0027001 | -0.0083591 | 0.16006 | -0.001222 | 0.018335 | -0.0088247 | 0.023007 | -0.0044968 | -0.064087 | -0.045776 | 0.013733 | -0.33875 | 0.32044 | -0.54474 | -0.72784 | -0.064087 | -0.25177 | -0.19226 | 0.13275 | 0.073242 | -0.65918 | -0.68207 | 0 | -0.18311 | -121.9482 | 0.49896 | 0.20599 | 0.3891 | -122.3328 | -0.11444 | -0.13733 | -122.1359 | 0.48065 | 0.35248 | 0.48981 | -122.1954 | 0.86517 | 0.48065 | 0.55847 | -122.9965 | 0.67749 | 0.61798 | 0.29297 | -122.9507
4374.0156 | 122.8043 | -0.52185 | 122.2961 | -0.23666 | 0.019626 | 0.0039498 | 0.017539 | 0.023541 | -0.0017859 | -0.0077183 | -0.18326 | -0.0010084 | 0.013422 | -0.0094657 | 0.023434 | -0.003856 | -0.009155 | 0.009155 | 0.050354 | -0.28381 | 0.29297 | -0.54016 | -0.71869 | -0.041199 | -0.16937 | -0.12817 | 0.13275 | 0.073242 | -0.65002 | -0.66834 | -0.01831 | -0.19684 | -122.0032 | 0.53101 | 0.23804 | 0.43488 | -122.3053 | -0.12817 | -0.14648 | -122.1634 | 0.48065 | 0.39368 | 0.54016 | -122.2229 | 0.81482 | 0.5127 | 0.5722 | -123.0148 | 0.6546 | 0.59509 | 0.35248 | -122.9645
4375.0156 | 122.7493 | -0.54474 | 122.3053 | 0.099029 | 0.019412 | 0.0062998 | 0.019248 | 0.027173 | 0.0039819 | -0.0087863 | 0.12955 | -0.0037854 | 0.015344 | -0.0098929 | 0.025357 | -0.004924 | -0.041199 | -0.045776 | 0.018311 | -0.29755 | 0.31128 | -0.54932 | -0.74158 | -0.086975 | -0.24261 | -0.17853 | 0.1236 | 0.059509 | -0.65002 | -0.69122 | -0.004577 | -0.19684 | -121.994 | 0.49896 | 0.24719 | 0.44403 | -122.3465 | -0.10529 | -0.14648 | -122.1817 | 0.45776 | 0.36621 | 0.5127 | -122.2458 | 0.85602 | 0.50354 | 0.56305 | -123.0469 | 0.66834 | 0.60425 | 0.30212 | -122.9965
4376.0156 | 122.7814 | -0.53101 | 122.2733 | -0.091705 | 0.020053 | 0.0035226 | 0.016898 | 0.026105 | 0.0024865 | -0.0096409 | -0.0077819 | -0.001222 | 0.014063 | -0.010961 | 0.026212 | -0.0053512 | -0.004578 | 0.045776 | 0.059509 | -0.23804 | 0.27924 | -0.54016 | -0.70953 | -0.032043 | -0.17395 | -0.15106 | 0.11444 | 0.059509 | -0.66834 | -0.67291 | -0.009155 | -0.17853 | -121.994 | 0.57678 | 0.29297 | 0.4715 | -122.2778 | -0.13733 | -0.14191 | -122.1588 | 0.49896 | 0.37994 | 0.52185 | -122.2137 | 0.81024 | 0.52643 | 0.59052 | -122.9828 | 0.64545 | 0.59052 | 0.35706 | -122.9462
4377.0156 | 122.7676 | -0.53558 | 122.2916 | 0.16769 | 0.01813 | 0.0030954 | 0.015616 | 0.027173 | 0.00056395 | -0.0092137 | 0.13718 | -0.0025038 | 0.016199 | -0.011815 | 0.024503 | -0.0053512 | -0.064087 | -0.045776 | 0.013733 | -0.2655 | 0.29755 | -0.55389 | -0.73242 | -0.064087 | -0.23804 | -0.17395 | 0.1236 | 0.07782 | -0.65002 | -0.66376 | -0.018311 | -0.19684 | -121.994 | 0.48981 | 0.27008 | 0.46692 | -122.3557 | -0.11444 | -0.12817 | -122.168 | 0.4715 | 0.36163 | 0.48981 | -122.2137 | 0.83313 | 0.4715 | 0.54932 | -123.024 | 0.65918 | 0.6134 | 0.29755 | -122.9553
4378.0156 | 122.7264 | -0.53558 | 122.2824 | -0.015411 | 0.019839 | 0.0018136 | 0.018393 | 0.025464 | 0.0024865 | -0.0094273 | -0.00015237 | -0.00229 | 0.015772 | -0.01267 | 0.02493 | -0.0040696 | -0.009155 | -0.009155 | 0.041199 | -0.2655 | 0.29755 | -0.54016 | -0.72327 | -0.064087 | -0.22888 | -0.19226 | 0.12817 | 0.068665 | -0.66376 | -0.65918 | -0.004578 | -0.18768 | -121.9849 | 0.52643 | 0.27008 | 0.45776 | -122.2916 | -0.12817 | -0.1236 | -122.1542 | 0.4715 | 0.34332 | 0.46692 | -122.2137 | 0.83313 | 0.52643 | 0.57678 | -123.0057 | 0.66376 | 0.60425 | 0.3067 | -122.9416
4379.0156 | 122.7768 | -0.53558 | 122.3007 | 0.16769 | 0.019412 | 0.0037362 | 0.019675 | 0.027173 | 0.0029137 | -0.0081455 | 0.16769 | -0.0010084 | 0.016626 | -0.0096793 | 0.023862 | -0.0040696 | -0.050354 | -0.045776 | 0.013733 | -0.35248 | 0.30212 | -0.55847 | -0.75073 | -0.059509 | -0.23346 | -0.16937 | 0.11444 | 0.050354 | -0.64545 | -0.66834 | -0.022889 | -0.21515 | -121.9986 | 0.48981 | 0.18311 | 0.39825 | -122.3511 | -0.10986 | -0.13275 | -122.1863 | 0.47607 | 0.36621 | 0.49896 | -122.2504 | 0.83771 | 0.48523 | 0.54932 | -123.0515 | 0.65002 | 0.58594 | 0.30212 | -122.9691
4380.0156 | 122.7997 | -0.52185 | 122.287 | -0.084076 | 0.020267 | 0.0037362 | 0.017539 | 0.024609 | 0.0033411 | -0.0089999 | -0.068817 | -0.0020764 | 0.01449 | -0.012456 | 0.024075 | -0.004924 | 0.027466 | 0.041199 | 0.054932 | -0.29755 | 0.29755 | -0.54474 | -0.74616 | -0.050354 | -0.18768 | -0.16022 | 0.10071 | 0.041199 | -0.65002 | -0.67291 | -0.022888 | -0.2243 | -121.9894 | 0.56305 | 0.2243 | 0.44861 | -122.2595 | -0.12817 | -0.15106 | -122.1863 | 0.4715 | 0.36163 | 0.5127 | -122.2458 | 0.8194 | 0.54932 | 0.57678 | -123.0331 | 0.62256 | 0.56305 | 0.33417 | -122.9599
4381.0156 | 122.7859 | -0.53558 | 122.3007 | 0.13718 | 0.017917 | 0.0030954 | 0.019248 | 0.027814 | 0.00056395 | -0.0087863 | 0.16006 | -0.001222 | 0.015344 | -0.0092521 | 0.024289 | -0.0034286 | -0.041199 | -0.041199 | 0.018311 | -0.27008 | 0.28839 | -0.54016 | -0.72327 | -0.064087 | -0.21973 | -0.15564 | 0.11902 | 0.068665 | -0.63171 | -0.66834 | -0.004578 | -0.18768 | -122.0123 | 0.49438 | 0.2655 | 0.45319 | -122.3419 | -0.096131 | -0.13275 | -122.1817 | 0.4715 | 0.37994 | 0.5127 | -122.2321 | 0.82397 | 0.49438 | 0.55389 | -123.024 | 0.6546 | 0.60425 | 0.31586 | -122.9691
4382.0156 | 122.7585 | -0.54474 | 122.319 | -0.00015269 | 0.020694 | 0.0030954 | 0.020743 | 0.025464 | 0.00099115 | -0.0092137 | 0.037995 | -0.0016492 | 0.018335 | -0.0096793 | 0.025571 | -0.005565 | -0.009155 | -0.027466 | 0.041199 | -0.24261 | 0.31128 | -0.53101 | -0.71869 | -0.082397 | -0.23804 | -0.20599 | 0.1236 | 0.073242 | -0.64087 | -0.67291 | 0.013733 | -0.17395 | -122.0078 | 0.51727 | 0.30212 | 0.47607 | -122.3282 | -0.09613 | -0.12817 | -122.1954 | 0.46234 | 0.33874 | 0.46692 | -122.2458 | 0.85602 | 0.53558 | 0.58594 | -123.0377 | 0.66834 | 0.61798 | 0.3067 | -122.9919
4383.0156 | 122.8043 | -0.55389 | 122.2961 | 0.12192 | 0.018344 | 0.0045908 | 0.01583 | 0.026532 | 0.0020593 | -0.0079319 | 0.20584 | -0.00036736 | 0.015558 | -0.0083975 | 0.02493 | -0.0053512 | -0.036621 | -0.050354 | 0.009155 | -0.41657 | 0.31586 | -0.5722 | -0.75531 | -0.050354 | -0.2243 | -0.15564 | 0.10986 | 0.045776 | -0.66834 | -0.6958 | -0.018311 | -0.20142 | -121.9803 | 0.50354 | 0.13733 | 0.33875 | -122.3328 | -0.11444 | -0.14191 | -122.1863 | 0.50354 | 0.39825 | 0.54016 | -122.2504 | 0.86975 | 0.51727 | 0.56305 | -123.0515 | 0.66376 | 0.59967 | 0.32959 | -122.9919
4384.0156 | 122.7585 | -0.55389 | 122.3099 | 0.15244 | 0.020694 | -0.00032258 | 0.018179 | 0.025891 | 0.0012047 | -0.0092137 | 0.12955 | -0.00058096 | 0.015772 | -0.01032 | 0.024075 | -0.0053512 | -0.045776 | -0.059509 | 0.009155 | -0.40741 | 0.31586 | -0.54932 | -0.75989 | -0.073242 | -0.26093 | -0.18768 | 0.11444 | 0.068665 | -0.68207 | -0.68207 | 0.004578 | -0.20599 | -121.994 | 0.49439 | 0.14648 | 0.35248 | -122.3557 | -0.12817 | -0.12817 | -122.1954 | 0.48065 | 0.36621 | 0.49439 | -122.2412 | 0.86975 | 0.50812 | 0.56305 | -123.0698 | 0.66834 | 0.62256 | 0.29297 | -122.9919
4385.0156 | 122.9095 | -0.52185 | 122.2824 | 0.2211 | 0.017276 | 0.0035226 | 0.015402 | 0.023541 | -0.0022131 | -0.0077183 | 0.2211 | -0.002931 | 0.014276 | -0.0083975 | 0.02493 | -0.0040696 | 0.027466 | 0.064087 | 0.10986 | -0.33875 | 0.2655 | -0.53101 | -0.70038 | 0.027466 | -0.11902 | -0.073242 | 0.073242 | 0.032043 | -0.62714 | -0.64545 | -0.009155 | -0.17853 | -122.0169 | 0.58594 | 0.18311 | 0.36163 | -122.2549 | -0.10529 | -0.1236 | -122.2092 | 0.54932 | 0.44861 | 0.5722 | -122.2504 | 0.78735 | 0.54932 | 0.63171 | -122.9828 | 0.59509 | 0.55389 | 0.40283 | -122.9279
4386.0156 | 122.7997 | -0.55389 | 122.2961 | 0.15244 | 0.021121 | 0.00074562 | 0.018179 | 0.026532 | 0.0020593 | -0.0081455 | 0.12192 | -0.0031446 | 0.018122 | -0.011175 | 0.025143 | -0.0044968 | -0.032043 | -0.064087 | 0 | -0.39825 | 0.3067 | -0.56305 | -0.75531 | -0.068665 | -0.2655 | -0.19684 | 0.1236 | 0.073242 | -0.67749 | -0.70038 | -0.009155 | -0.20142 | -121.9894 | 0.48981 | 0.15564 | 0.35706 | -122.3282 | -0.1236 | -0.14648 | -122.1725 | 0.48523 | 0.35706 | 0.50354 | -122.2229 | 0.8606 | 0.52185 | 0.55389 | -123.0515 | 0.67749 | 0.62714 | 0.28839 | -122.9965
4387.0156 | 122.905 | -0.50354 | 122.2687 | 0.19058 | 0.015353 | 0.0054452 | 0.016684 | 0.0276 | -0.0030677 | -0.010282 | 0.22873 | -0.0050672 | 0.013422 | -0.01032 | 0.023862 | -0.0064194 | 0.041199 | 0.10071 | 0.15106 | -0.32959 | 0.2655 | -0.51727 | -0.71411 | 0.036621 | -0.1236 | -0.045776 | 0.07782 | 0.041199 | -0.62714 | -0.6546 | -0.013733 | -0.21057 | -122.0032 | 0.60425 | 0.17395 | 0.38452 | -122.2275 | -0.1236 | -0.15106 | -122.1909 | 0.54016 | 0.45776 | 0.60883 | -122.2275 | 0.76904 | 0.54474 | 0.6546 | -122.9828 | 0.58136 | 0.54474 | 0.37994 | -122.9233
4388.0156 | 122.7676 | -0.54474 | 122.3236 | 0.037994 | 0.02048 | 0.0024544 | 0.017111 | 0.025677 | 0.0031273 | -0.0070773 | 0.045624 | -0.0035718 | 0.01684 | -0.010106 | 0.025143 | -0.0044968 | -0.013733 | -0.064087 | 0 | -0.42114 | 0.3067 | -0.54474 | -0.737 | -0.09613 | -0.27924 | -0.23346 | 0.13733 | 0.086975 | -0.67749 | -0.70038 | 0 | -0.19226 | -122.0169 | 0.48065 | 0.1236 | 0.31586 | -122.3373 | -0.13275 | -0.15564 | -122.1863 | 0.44861 | 0.31128 | 0.46692 | -122.2366 | 0.85144 | 0.53101 | 0.54474 | -123.0606 | 0.68207 | 0.63171 | 0.2655 | -123.024
4389.0156 | 122.8867 | -0.50354 | 122.2733 | 0.20584 | 0.012576 | 0.0037362 | 0.016684 | 0.026959 | -0.0034949 | -0.0081455 | 0.19821 | -0.0037854 | 0.017481 | -0.0098929 | 0.023862 | -0.005565 | 0.045776 | 0.086975 | 0.13275 | -0.33875 | 0.27008 | -0.52185 | -0.71869 | 0.045776 | -0.15106 | -0.054932 | 0.086975 | 0.036621 | -0.64087 | -0.65002 | -0.018311 | -0.21515 | -122.0032 | 0.59052 | 0.16479 | 0.37994 | -122.2275 | -0.13733 | -0.14648 | -122.1863 | 0.54932 | 0.44861 | 0.59509 | -122.2366 | 0.77362 | 0.54932 | 0.63629 | -122.9919 | 0.59052 | 0.54016 | 0.35248 | -122.9233
4390.0156 | 122.8546 | -0.51727 | 122.2824 | 0.12955 | 0.016849 | 0.0039498 | 0.017752 | 0.025677 | 0.0016321 | -0.0092137 | 0.19058 | -0.002931 | 0.015344 | -0.010747 | 0.024716 | -0.0070602 | 0.013733 | 0 | 0.064087 | -0.39368 | 0.29755 | -0.55389 | -0.737 | 0.022888 | -0.20599 | -0.091553 | 0.10071 | 0.032043 | -0.64087 | -0.6546 | -0.036621 | -0.21973 | -121.9849 | 0.51727 | 0.1236 | 0.34332 | -122.2687 | -0.1236 | -0.13733 | -122.1817 | 0.54016 | 0.42572 | 0.56305 | -122.2504 | 0.81482 | 0.53101 | 0.58136 | -123.0194 | 0.61798 | 0.54932 | 0.31128 | -122.937
4391.0156 | 122.8683 | -0.49896 | 122.2824 | 0.16769 | 0.010653 | 0.0056588 | 0.016257 | 0.027386 | -0.0037085 | -0.010068 | 0.17532 | -0.0050672 | 0.012354 | -0.01032 | 0.021725 | -0.0044968 | 0.004578 | 0.054932 | 0.09613 | -0.35706 | 0.27924 | -0.53558 | -0.73242 | -0.009155 | -0.17853 | -0.07782 | 0.082397 | 0.027466 | -0.64087 | -0.66834 | -0.036621 | -0.23346 | -122.0032 | 0.55389 | 0.14191 | 0.37537 | -122.2778 | -0.14191 | -0.16937 | -122.2 | 0.48981 | 0.42114 | 0.59052 | -122.2549 | 0.7782 | 0.50354 | 0.59509 | -123.0148 | 0.58136 | 0.52643 | 0.32043 | -122.9507
4392.0156 | 122.9004 | -0.5127 | 122.2916 | 0.17532 | 0.018558 | 0.0039498 | 0.015402 | 0.027173 | 0.0027001 | -0.0085727 | 0.18295 | -0.0035718 | 0.016413 | -0.010534 | 0.023648 | -0.0051376 | 0.032043 | -0.004578 | 0.07782 | -0.37537 | 0.27924 | -0.55847 | -0.71869 | 0.036621 | -0.16022 | -0.07782 | 0.073242 | 0.027466 | -0.62714 | -0.64545 | -0.045777 | -0.20599 | -122.0123 | 0.50812 | 0.13733 | 0.34332 | -122.2595 | -0.11444 | -0.13275 | -122.2183 | 0.54932 | 0.43488 | 0.56763 | -122.2641 | 0.79193 | 0.54474 | 0.59052 | -123.0103 | 0.58594 | 0.54016 | 0.35248 | -122.937
4393.0156 | 122.8912 | -0.48523 | 122.2824 | 0.17532 | 0.014285 | 0.0024544 | 0.01583 | 0.025037 | -0.0024269 | -0.0092137 | 0.18295 | -0.0035718 | 0.011926 | -0.010106 | 0.025357 | -0.0042832 | 0.064087 | 0.082397 | 0.14648 | -0.32959 | 0.26093 | -0.51727 | -0.70496 | 0.041199 | -0.14191 | -0.059509 | 0.10071 | 0.032043 | -0.63629 | -0.63629 | -0.032044 | -0.21973 | -122.0215 | 0.56763 | 0.15564 | 0.37537 | -122.2183 | -0.15106 | -0.15106 | -122.1817 | 0.52643 | 0.42572 | 0.57678 | -122.2504 | 0.74615 | 0.54932 | 0.63171 | -122.9874 | 0.58594 | 0.51727 | 0.34332 | -122.9187
4394.0156 | 122.8409 | -0.53101 | 122.319 | 0.15244 | 0.018558 | 0.0043772 | 0.016684 | 0.029736 | 0.0018457 | -0.0092137 | 0.11429 | -0.0025038 | 0.014276 | -0.0094657 | 0.02493 | -0.005565 | 0.004578 | -0.041199 | 0.027466 | -0.40283 | 0.32044 | -0.55847 | -0.75531 | -0.041199 | -0.24719 | -0.16479 | 0.12817 | 0.050354 | -0.63629 | -0.66376 | -0.027466 | -0.2243 | -121.9986 | 0.48981 | 0.12817 | 0.35248 | -122.3145 | -0.10529 | -0.13275 | -122.1909 | 0.48981 | 0.36621 | 0.49896 | -122.2687 | 0.85144 | 0.53558 | 0.55847 | -123.0743 | 0.65918 | 0.58136 | 0.28381 | -122.9828
4395.0156 | 122.8958 | -0.48523 | 122.2916 | 0.17532 | 0.016421 | 0.0020272 | 0.016257 | 0.025891 | -0.00071785 | -0.010495 | 0.2211 | -0.006349 | 0.014917 | -0.010106 | 0.023434 | -0.0068466 | 0.068665 | 0.10071 | 0.13733 | -0.3067 | 0.2655 | -0.53558 | -0.68665 | 0.059509 | -0.11444 | -0.045776 | 0.073242 | 0.032043 | -0.60425 | -0.65002 | -0.050354 | -0.20142 | -122.0261 | 0.58594 | 0.17853 | 0.37994 | -122.2229 | -0.11902 | -0.1648 | -122.2183 | 0.54474 | 0.43945 | 0.60425 | -122.2595 | 0.75073 | 0.55389 | 0.62256 | -122.9782 | 0.55847 | 0.51727 | 0.37079 | -122.9416
4396.0156 | 122.8912 | -0.50354 | 122.3007 | 0.17532 | 0.020907 | 0.0041634 | 0.018179 | 0.026959 | 0.0016321 | -0.0085727 | 0.14481 | -0.00229 | 0.015558 | -0.0094657 | 0.025143 | -0.0053512 | 0.045776 | 0.018311 | 0.09613 | -0.35248 | 0.28839 | -0.52185 | -0.69122 | 0.041199 | -0.13733 | -0.068665 | 0.086975 | 0.036621 | -0.60883 | -0.64545 | -0.018311 | -0.18768 | -122.0123 | 0.52185 | 0.15106 | 0.33875 | -122.2549 | -0.10529 | -0.14191 | -122.2137 | 0.54474 | 0.43488 | 0.57678 | -122.2641 | 0.79193 | 0.54932 | 0.59967 | -122.9919 | 0.59052 | 0.54016 | 0.36621 | -122.9462
4397.0156 | 122.8912 | -0.51727 | 122.3328 | 0.12192 | 0.0091581 | 0.005018 | 0.015616 | 0.024609 | -0.0034949 | -0.0098545 | 0.17532 | -0.0042126 | 0.012781 | -0.010961 | 0.025357 | -0.0027878 | 0.018311 | 0.041199 | 0.10071 | -0.37079 | 0.27008 | -0.49896 | -0.70496 | 0.009155 | -0.15106 | -0.07782 | 0.09613 | 0.054932 | -0.63629 | -0.63629 | 0.018311 | -0.18768 | -122.0627 | 0.55847 | 0.14648 | 0.33417 | -122.3145 | -0.11902 | -0.11902 | -122.2366 | 0.52643 | 0.43945 | 0.55847 | -122.2778 | 0.78735 | 0.53558 | 0.61798 | -123.0377 | 0.6134 | 0.5722 | 0.36621 | -122.9691
4398.0156 | 122.9233 | -0.49439 | 122.2916 | 0.21347 | 0.016421 | 0.0028818 | 0.017966 | 0.027173 | -0.0015723 | -0.0068637 | 0.17532 | -0.0031446 | 0.016626 | -0.010534 | 0.024716 | -0.0074876 | 0.07782 | 0.10071 | 0.12817 | -0.30212 | 0.2655 | -0.52185 | -0.68665 | 0.050354 | -0.11902 | -0.050354 | 0.073242 | 0.022888 | -0.62256 | -0.6546 | -0.027466 | -0.19226 | -122.0261 | 0.59509 | 0.19226 | 0.38452 | -122.2137 | -0.12817 | -0.16022 | -122.2183 | 0.54474 | 0.44403 | 0.60425 | -122.2687 | 0.75989 | 0.57221 | 0.62256 | -122.9782 | 0.56763 | 0.51727 | 0.37537 | -122.9462
4399.0156 | 122.8867 | -0.50812 | 122.319 | 0.037994 | 0.0089443 | 0.0062998 | 0.013266 | 0.024609 | -0.0037085 | -0.012631 | 0.030365 | -0.0037854 | 0.013208 | -0.010961 | 0.023221 | -0.0040696 | 0.004578 | 0.036621 | 0.09613 | -0.34332 | 0.28381 | -0.52185 | -0.71411 | -0.009155 | -0.13275 | -0.059509 | 0.10986 | 0.027466 | -0.62714 | -0.64545 | -0.013733 | -0.20599 | -122.0352 | 0.54474 | 0.16479 | 0.37079 | -122.3145 | -0.11902 | -0.13733 | -122.2092 | 0.49896 | 0.44861 | 0.58594 | -122.2916 | 0.79193 | 0.5127 | 0.60425 | -123.0331 | 0.61798 | 0.53558 | 0.37537 | -122.9645
4400.0156 | 122.9462 | -0.48981 | 122.3419 | 0.22873 | 0.01578 | 0.0039498 | 0.018607 | 0.028668 | 0.0014185 | -0.010282 | 0.18295 | -0.0037854 | 0.013422 | -0.013952 | 0.025357 | -0.0072738 | 0.086975 | 0.082397 | 0.13733 | -0.31128 | 0.25635 | -0.51727 | -0.70038 | 0.050354 | -0.11444 | -0.059509 | 0.073242 | 0.027466 | -0.62714 | -0.6546 | -0.027466 | -0.21057 | -122.0856 | 0.5722 | 0.17853 | 0.3891 | -122.2549 | -0.13733 | -0.1648 | -122.2687 | 0.54016 | 0.4303 | 0.59509 | -122.3145 | 0.74616 | 0.57678 | 0.62714 | -123.0423 | 0.56305 | 0.51727 | 0.37537 | -122.9965
4401.0625 | 122.8546 | -0.53101 | 122.3557 | -0.0383 | 0.01578 | 0.003309 | 0.016043 | 0.026746 | 0.0046227 | -0.0085727 | -0.11459 | -0.0016492 | 0.01449 | -0.0098929 | 0.028775 | -0.0081284 | 0.064087 | 0.041199 | 0.054932 | -0.35706 | 0.29297 | -0.54016 | -0.737 | -0.004578 | -0.1831 | -0.16479 | 0.11444 | 0.073242 | -0.64087 | -0.67291 | -0.009155 | -0.20599 | -122.0627 | 0.5722 | 0.17395 | 0.37994 | -122.2916 | -0.10986 | -0.14191 | -122.2412 | 0.52643 | 0.36621 | 0.50812 | -122.2824 | 0.82397 | 0.59509 | 0.58594 | -123.0927 | 0.64545 | 0.60425 | 0.3479 | -123.0286
4402.0156 | 122.9324 | -0.48981 | 122.3282 | 0.17532 | 0.017062 | 0.0016 | 0.015189 | 0.025037 | 0.0044091 | -0.0077183 | 0.16006 | -0.0025038 | 0.012781 | -0.010534 | 0.024289 | -0.0042832 | 0.022888 | 0.022888 | 0.082397 | -0.35248 | 0.27008 | -0.53101 | -0.69122 | 0.027466 | -0.13733 | -0.082397 | 0.082397 | 0.027466 | -0.63171 | -0.65918 | -0.041199 | -0.20142 | -122.0581 | 0.5127 | 0.13733 | 0.33875 | -122.3053 | -0.14191 | -0.16937 | -122.2458 | 0.51727 | 0.40741 | 0.57678 | -122.3007 | 0.75989 | 0.5127 | 0.5722 | -123.0194 | 0.5722 | 0.51727 | 0.35248 | -122.9874
4403.0156 | 122.8867 | -0.52185 | 122.3557 | 0.0914 | 0.011508 | 0.0056588 | 0.014334 | 0.025891 | -0.0056311 | -0.0087863 | 0.09903 | -0.0035718 | 0.010858 | -0.0094657 | 0.024716 | -0.0040696 | 0.022888 | 0.059509 | 0.10986 | -0.35706 | 0.27466 | -0.53101 | -0.70496 | 0.013733 | -0.15564 | -0.064087 | 0.10071 | 0.022888 | -0.61798 | -0.65002 | -0.009155 | -0.18311 | -122.081 | 0.58136 | 0.16479 | 0.3479 | -122.3328 | -0.09613 | -0.12817 | -122.2549 | 0.53558 | 0.45776 | 0.58594 | -122.3328 | 0.79651 | 0.54474 | 0.63171 | -123.0606 | 0.62256 | 0.54474 | 0.36621 | -123.0057
4404.0156 | 122.9141 | -0.51727 | 122.3099 | 0.15244 | 0.014285 | 0.0056588 | 0.01583 | 0.025037 | 0.00056395 | -0.010068 | 0.15244 | -0.0048536 | 0.015558 | -0.012456 | 0.025143 | -0.0074876 | 0.073242 | 0.10071 | 0.15106 | -0.31586 | 0.24719 | -0.52643 | -0.70038 | 0.041199 | -0.13275 | -0.059509 | 0.086975 | 0.032043 | -0.64087 | -0.64087 | -0.009155 | -0.1831 | -122.0627 | 0.61798 | 0.20142 | 0.38452 | -122.2366 | -0.1236 | -0.1236 | -122.2229 | 0.55847 | 0.45776 | 0.58136 | -122.2778 | 0.76446 | 0.59052 | 0.66834 | -123.0103 | 0.60425 | 0.54932 | 0.38452 | -122.9507
4405.0156 | 122.9141 | -0.50812 | 122.3465 | 0.053253 | 0.0097989 | 0.0039498 | 0.014761 | 0.025464 | -0.0017859 | -0.011563 | 0.0074766 | -0.0042126 | 0.013635 | -0.01032 | 0.022153 | -0.004924 | 0 | 0.050354 | 0.09613 | -0.3479 | 0.27924 | -0.52185 | -0.70496 | -0.004578 | -0.15564 | -0.050354 | 0.10071 | 0.036621 | -0.64087 | -0.66376 | -0.013733 | -0.19684 | -122.0673 | 0.55847 | 0.16022 | 0.35706 | -122.3465 | -0.13275 | -0.15564 | -122.2458 | 0.50354 | 0.45776 | 0.6134 | -122.3099 | 0.78735 | 0.50812 | 0.60425 | -123.0515 | 0.60883 | 0.54474 | 0.35248 | -123.0103
4406.0156 | 122.9141 | -0.48981 | 122.3099 | 0.18295 | 0.013217 | 0.006727 | 0.015189 | 0.028882 | -0.00029045 | -0.010068 | 0.19058 | -0.0035718 | 0.013635 | -0.0090385 | 0.025571 | -0.005565 | 0.082397 | 0.09613 | 0.14648 | -0.31586 | 0.27008 | -0.50812 | -0.68665 | 0.073242 | -0.11902 | -0.064087 | 0.064087 | 0.022888 | -0.61798 | -0.63629 | -0.018311 | -0.19684 | -122.0398 | 0.58594 | 0.17395 | 0.37079 | -122.2275 | -0.12817 | -0.14648 | -122.2458 | 0.56305 | 0.42572 | 0.5722 | -122.287 | 0.75989 | 0.5722 | 0.63629 | -122.9965 | 0.55389 | 0.5127 | 0.37079 | -122.9462
4407.0156 | 122.9324 | -0.51727 | 122.3373 | -0.0077822 | 0.0093717 | 0.006086 | 0.013266 | 0.027173 | -0.0037085 | -0.010922 | -0.061188 | -0.0069898 | 0.012354 | -0.011388 | 0.024075 | -0.0042832 | 0 | 0.064087 | 0.11444 | -0.33417 | 0.29755 | -0.52185 | -0.68665 | 0.032043 | -0.11444 | -0.032043 | 0.091553 | 0.032043 | -0.62256 | -0.64545 | -0.004578 | -0.16937 | -122.0398 | 0.58136 | 0.18311 | 0.35248 | -122.3373 | -0.10529 | -0.12817 | -122.2458 | 0.54932 | 0.48523 | 0.6134 | -122.3053 | 0.81482 | 0.51727 | 0.63171 | -123.024 | 0.60883 | 0.54932 | 0.40283 | -122.9828
4408.0156 | 122.9462 | -0.48981 | 122.3328 | 0.28213 | 0.015353 | 0.0026682 | 0.015402 | 0.026746 | 0.0012047 | -0.010068 | 0.18295 | -0.0059216 | 0.018335 | -0.0090385 | 0.025571 | -0.0074876 | 0.086975 | 0.10071 | 0.13733 | -0.30212 | 0.27924 | -0.53101 | -0.68207 | 0.068665 | -0.1236 | -0.054932 | 0.086975 | 0.009155 | -0.60883 | -0.64545 | -0.041199 | -0.19226 | -122.0535 | 0.59052 | 0.18768 | 0.37994 | -122.2458 | -0.11902 | -0.15564 | -122.2458 | 0.55847 | 0.43488 | 0.59052 | -122.3236 | 0.76904 | 0.57678 | 0.62714 | -123.0148 | 0.57678 | 0.49896 | 0.36621 | -122.9782
4409.0156 | 122.9279 | -0.5127 | 122.3511 | 0.16769 | 0.012149 | 0.0054452 | 0.014975 | 0.024823 | -0.00071785 | -0.010922 | 0.083771 | -0.0035718 | 0.014063 | -0.011388 | 0.024503 | -0.0047104 | 0.027466 | 0.082397 | 0.11902 | -0.35706 | 0.27466 | -0.51727 | -0.71411 | 0.013733 | -0.15106 | -0.073242 | 0.09613 | 0.041199 | -0.6134 | -0.63629 | -0.004578 | -0.20142 | -122.0764 | 0.59509 | 0.15564 | 0.35706 | -122.3236 | -0.10071 | -0.1236 | -122.2549 | 0.52643 | 0.43945 | 0.56305 | -122.3099 | 0.78735 | 0.54016 | 0.63171 | -123.0652 | 0.60882 | 0.55389 | 0.36163 | -122.9874
4410.0156 | 122.9233 | -0.49439 | 122.3419 | 0.17532 | 0.014926 | 0.0039498 | 0.01583 | 0.027386 | 0.0020593 | -0.0079319 | 0.12955 | -0.0035718 | 0.014917 | -0.013738 | 0.025357 | -0.005565 | 0.07782 | 0.10071 | 0.14648 | -0.33417 | 0.25177 | -0.50812 | -0.68665 | 0.068665 | -0.11444 | -0.059509 | 0.091553 | 0.036621 | -0.61798 | -0.65002 | -0.013733 | -0.19226 | -122.0901 | 0.59509 | 0.16022 | 0.35248 | -122.2641 | -0.1236 | -0.15564 | -122.2504 | 0.56305 | 0.43488 | 0.59052 | -122.3053 | 0.74616 | 0.57221 | 0.64087 | -123.0286 | 0.58594 | 0.53101 | 0.37994 | -122.9919
4411.0156 | 122.9553 | -0.50354 | 122.3465 | -0.023041 | 0.01044 | 0.0052316 | 0.017966 | 0.024182 | -0.0015723 | -0.0094273 | -0.045929 | -0.0048536 | 0.013849 | -0.010534 | 0.022794 | -0.006633 | 0.018311 | 0.073242 | 0.11902 | -0.32959 | 0.28839 | -0.53558 | -0.70953 | 0.036621 | -0.11444 | -0.050354 | 0.10071 | 0.027466 | -0.61798 | -0.65918 | -0.032043 | -0.20599 | -122.0581 | 0.57678 | 0.17395 | 0.37994 | -122.3282 | -0.11444 | -0.15564 | -122.2458 | 0.54016 | 0.45319 | 0.60883 | -122.319 | 0.79193 | 0.52185 | 0.62256 | -123.056 | 0.60425 | 0.53101 | 0.3891 | -123.0057
4412.0156 | 122.9324 | -0.52185 | 122.3511 | 0.16769 | 0.013217 | 0.0045908 | 0.015616 | 0.024182 | -0.0011451 | -0.0079319 | 0.14481 | -0.006349 | 0.015344 | -0.010747 | 0.02493 | -0.0053512 | 0.050354 | 0.086975 | 0.11902 | -0.35248 | 0.2655 | -0.5127 | -0.69122 | 0.041199 | -0.15106 | -0.07782 | 0.11444 | 0.004578 | -0.63171 | -0.65002 | 0.009156 | -0.16937 | -122.0856 | 0.60883 | 0.16937 | 0.33875 | -122.3007 | -0.10986 | -0.12817 | -122.2366 | 0.56305 | 0.44403 | 0.5722 | -122.3465 | 0.78735 | 0.5722 | 0.64087 | -123.0423 | 0.63629 | 0.52643 | 0.37079 | -123.0011
4413.0156 | 122.9279 | -0.50354 | 122.3282 | -0.00015269 | 0.0078763 | 0.0048044 | 0.013052 | 0.024182 | -0.0017859 | -0.0098545 | -0.015411 | -0.0035718 | 0.011926 | -0.0092521 | 0.024716 | -0.0057786 | 0.027466 | 0.068665 | 0.13275 | -0.33875 | 0.27008 | -0.53558 | -0.72784 | 0.036621 | -0.11444 | -0.032043 | 0.086975 | 0.032043 | -0.63629 | -0.6546 | -0.032043 | -0.2243 | -122.0581 | 0.5722 | 0.16479 | 0.3891 | -122.3007 | -0.13275 | -0.15106 | -122.2412 | 0.54016 | 0.4715 | 0.62256 | -122.2961 | 0.77362 | 0.53101 | 0.63629 | -123.056 | 0.59052 | 0.53558 | 0.3891 | -122.9828
4414.0156 | 122.905 | -0.50354 | 122.3373 | 0.16769 | 0.012149 | 0.0065134 | 0.013907 | 0.024182 | -7.6852e-05 | -0.0089999 | 0.16006 | -0.0037854 | 0.014704 | -0.012243 | 0.024075 | -0.006633 | 0.050354 | 0.10071 | 0.12817 | -0.32959 | 0.27008 | -0.53101 | -0.6958 | 0.032043 | -0.15106 | -0.068665 | 0.07782 | 0.018311 | -0.62714 | -0.6546 | -0.027466 | -0.19226 | -122.0673 | 0.60425 | 0.17395 | 0.36621 | -122.287 | -0.1236 | -0.15106 | -122.2595 | 0.53558 | 0.43488 | 0.58594 | -122.319 | 0.77362 | 0.55389 | 0.63171 | -123.0331 | 0.58136 | 0.52185 | 0.35248 | -122.9919
4415.0156 | 122.9187 | -0.50812 | 122.3373 | 0.045624 | 0.0095853 | 0.006727 | 0.015402 | 0.025037 | -0.0013587 | -0.0075047 | 0.0914 | -0.0048536 | 0.012354 | -0.010961 | 0.023221 | -0.0057786 | 0.009155 | 0.064087 | 0.09613 | -0.33417 | 0.27466 | -0.5127 | -0.6958 | 0.022888 | -0.14191 | -0.059509 | 0.086975 | 0.032043 | -0.64545 | -0.65002 | -0.004577 | -0.18768 | -122.0627 | 0.5722 | 0.17395 | 0.36163 | -122.3282 | -0.13733 | -0.14191 | -122.2504 | 0.53101 | 0.44861 | 0.59052 | -122.3053 | 0.78278 | 0.51727 | 0.60425 | -123.0331 | 0.59509 | 0.54016 | 0.36621 | -122.9874
4416.0156 | 122.9279 | -0.50354 | 122.3648 | 0.16006 | 0.012149 | 0.005018 | 0.018607 | 0.027173 | 0.00099115 | -0.0083591 | 0.16006 | -0.00464 | 0.015131 | -0.0079703 | 0.023221 | -0.0042832 | 0.050354 | 0.09613 | 0.12817 | -0.33875 | 0.26093 | -0.51727 | -0.68207 | 0.032043 | -0.15106 | -0.068665 | 0.086975 | 0.032043 | -0.59509 | -0.64545 | -0.013733 | -0.17853 | -122.1039 | 0.59967 | 0.16479 | 0.34332 | -122.3145 | -0.091553 | -0.14191 | -122.2778 | 0.53558 | 0.43488 | 0.57678 | -122.3328 | 0.76446 | 0.55389 | 0.63171 | -123.0469 | 0.59052 | 0.53558 | 0.35248 | -123.0103
4417.0156 | 122.9645 | -0.49439 | 122.3465 | -0.084076 | 0.0089443 | 0.0052316 | 0.01583 | 0.02525 | -0.0022131 | -0.0083591 | -0.053558 | -0.0052808 | 0.012781 | -0.010106 | 0.024289 | -0.006633 | 0.068665 | 0.1236 | 0.15106 | -0.3067 | 0.27008 | -0.55389 | -0.70496 | 0.086975 | -0.045776 | -0.013733 | 0.07782 | 0.009155 | -0.60883 | -0.64087 | -0.059509 | -0.21057 | -122.0764 | 0.61798 | 0.18768 | 0.39825 | -122.2778 | -0.11444 | -0.14648 | -122.2687 | 0.58136 | 0.48065 | 0.62714 | -122.3373 | 0.76447 | 0.56305 | 0.64545 | -123.0515 | 0.57221 | 0.50354 | 0.44861 | -122.9874
4418.0156 | 122.9416 | -0.53101 | 122.374 | -0.0077822 | 0.010653 | 0.005018 | 0.015616 | 0.026318 | 0.00056395 | -0.0096409 | 0.12192 | -0.0050672 | 0.012995 | -0.0098929 | 0.026212 | -0.0051376 | 0.004578 | 0.068665 | 0.10986 | -0.34332 | 0.26093 | -0.53558 | -0.70953 | 0.018311 | -0.16022 | -0.068665 | 0.10071 | 0.004578 | -0.61798 | -0.65002 | -0.004577 | -0.17853 | -122.113 | 0.59967 | 0.18768 | 0.36621 | -122.3694 | -0.086975 | -0.11902 | -122.2733 | 0.54932 | 0.46234 | 0.58136 | -122.3694 | 0.79193 | 0.53558 | 0.64087 | -123.0835 | 0.63171 | 0.53558 | 0.37079 | -123.024
4419.0156 | 122.9828 | -0.51727 | 122.3465 | -0.099335 | 0.010226 | 0.0054452 | 0.014975 | 0.026746 | -0.0015723 | -0.0092137 | -0.023041 | -0.002931 | 0.01684 | -0.012029 | 0.025143 | -0.004924 | 0.059509 | 0.09613 | 0.15564 | -0.31586 | 0.27924 | -0.50354 | -0.71411 | 0.068665 | -0.068665 | -0.022888 | 0.086975 | 0.022888 | -0.6134 | -0.63629 | 0.013733 | -0.19684 | -122.0673 | 0.6134 | 0.20142 | 0.39825 | -122.287 | -0.09613 | -0.11902 | -122.2595 | 0.58594 | 0.49438 | 0.6134 | -122.3236 | 0.79651 | 0.57678 | 0.67291 | -123.0606 | 0.60425 | 0.54016 | 0.44861 | -122.9828
4420.0156 | 122.9279 | -0.51727 | 122.3877 | 0.076141 | 0.011081 | 0.0037362 | 0.016043 | 0.023541 | 0.00077755 | -0.0092137 | 0.045624 | -0.0044264 | 0.016626 | -0.010747 | 0.025357 | -0.0070602 | 0 | 0.073242 | 0.10986 | -0.34332 | 0.27466 | -0.53558 | -0.70038 | 0.018311 | -0.16022 | -0.07782 | 0.09613 | 0.022888 | -0.63629 | -0.6546 | -0.01831 | -0.1831 | -122.113 | 0.59052 | 0.17395 | 0.35705 | -122.3877 | -0.11902 | -0.13733 | -122.2916 | 0.53558 | 0.43945 | 0.57678 | -122.3648 | 0.79193 | 0.51727 | 0.62714 | -123.0881 | 0.6134 | 0.54016 | 0.35706 | -123.0423
4421.0156 | 122.8821 | -0.53558 | 122.3831 | -0.16037 | 0.017917 | 0.0054452 | 0.022238 | 0.028241 | 0.0056909 | -0.0079319 | -0.25192 | -0.0027174 | 0.015558 | -0.010747 | 0.027921 | -0.0091966 | 0.068665 | 0.064087 | 0.064087 | -0.3479 | 0.32501 | -0.5722 | -0.72327 | 0.009155 | -0.16937 | -0.16022 | 0.10986 | 0.041199 | -0.65918 | -0.67291 | -0.036622 | -0.18768 | -122.0581 | 0.59967 | 0.18768 | 0.37537 | -122.3145 | -0.1236 | -0.13733 | -122.2733 | 0.54474 | 0.37537 | 0.5127 | -122.3419 | 0.86059 | 0.60425 | 0.59967 | -123.1064 | 0.64545 | 0.57678 | 0.36621 | -123.056
4422.0156 | 122.9462 | -0.50354 | 122.374 | 0.15244 | 0.013003 | 0.0048044 | 0.016043 | 0.025677 | -0.0013587 | -0.0083591 | 0.20584 | -0.0027174 | 0.013422 | -0.01032 | 0.02493 | -0.0051376 | 0.036621 | 0.10529 | 0.13275 | -0.34332 | 0.25635 | -0.53101 | -0.6958 | 0.027466 | -0.15564 | -0.054932 | 0.086975 | 0.032043 | -0.62256 | -0.64545 | -0.027466 | -0.19226 | -122.1176 | 0.60883 | 0.16022 | 0.35248 | -122.3373 | -0.11902 | -0.14191 | -122.287 | 0.53101 | 0.44861 | 0.59052 | -122.3419 | 0.75989 | 0.54016 | 0.63629 | -123.0698 | 0.59052 | 0.53558 | 0.3479 | -123.0194
4423.0156 | 122.9507 | -0.49439 | 122.3419 | -0.00015269 | 0.010013 | 0.0030954 | 0.014548 | 0.025677 | -0.0028541 | -0.0096409 | -0.038299 | -0.00464 | 0.013208 | -0.010747 | 0.023221 | -0.0034286 | 0.004578 | 0.068665 | 0.1236 | -0.34332 | 0.28839 | -0.53101 | -0.72784 | 0.032043 | -0.10529 | -0.041199 | 0.10071 | 0.022888 | -0.62256 | -0.6546 | -0.036621 | -0.23346 | -122.0535 | 0.56305 | 0.15106 | 0.38452 | -122.3373 | -0.12817 | -0.16022 | -122.2412 | 0.52643 | 0.45319 | 0.6134 | -122.319 | 0.78278 | 0.49896 | 0.61798 | -123.0698 | 0.59509 | 0.51727 | 0.3891 | -122.9965
4424.0156 | 122.9782 | -0.5127 | 122.3694 | 0.022736 | 0.0076627 | 0.003309 | 0.013693 | 0.026746 | -0.0039221 | -0.0096409 | -0.038299 | -0.0042126 | 0.014276 | -0.011388 | 0.024289 | -0.0064194 | 0.013733 | 0.059509 | 0.13275 | -0.3479 | 0.28381 | -0.51727 | -0.71411 | 0.027466 | -0.10986 | -0.054932 | 0.11444 | 0.032043 | -0.63171 | -0.65002 | -0.004578 | -0.20142 | -122.0856 | 0.5722 | 0.1648 | 0.36621 | -122.3557 | -0.11902 | -0.13733 | -122.2549 | 0.54016 | 0.45776 | 0.59509 | -122.3373 | 0.79651 | 0.52643 | 0.64545 | -123.0835 | 0.62714 | 0.54474 | 0.40283 | -123.0194
4425.0156 | 122.9736 | -0.4715 | 122.3694 | -0.19089 | 0.011508 | 0.0030954 | 0.017111 | 0.02525 | 0.00013675 | -0.011136 | -0.19852 | -0.00464 | 0.016199 | -0.011175 | 0.024503 | -0.005565 | 0.073242 | 0.14191 | 0.15564 | -0.31128 | 0.27466 | -0.52643 | -0.72327 | 0.059509 | -0.059509 | -0.027466 | 0.086975 | 0.032043 | -0.6134 | -0.64545 | -0.054931 | -0.25177 | -122.0947 | 0.6134 | 0.16022 | 0.41199 | -122.2961 | -0.14191 | -0.17395 | -122.2824 | 0.53101 | 0.44403 | 0.61798 | -122.3373 | 0.74616 | 0.54474 | 0.62714 | -123.0927 | 0.55847 | 0.50354 | 0.41199 | -123.0148
4426.0156 | 122.9095 | -0.50812 | 122.3923 | -0.0383 | 0.018558 | -0.005236 | 0.018393 | 0.025037 | 0.0065453 | -0.0070773 | -0.12985 | -0.0031446 | 0.017053 | -0.010106 | 0.027493 | -0.0072738 | 0.059509 | 0.068665 | 0.059509 | -0.35706 | 0.28839 | -0.54932 | -0.74616 | 0.004578 | -0.1831 | -0.16479 | 0.09613 | 0.041199 | -0.64545 | -0.6958 | -0.041198 | -0.23804 | -122.1039 | 0.57678 | 0.15106 | 0.3891 | -122.3328 | -0.13733 | -0.18768 | -122.2961 | 0.5127 | 0.34332 | 0.53101 | -122.3511 | 0.79651 | 0.56763 | 0.56763 | -123.1384 | 0.60425 | 0.54932 | 0.32501 | -123.0881
4427.0156 | 122.9645 | -0.50354 | 122.3831 | -0.16037 | 0.011508 | 0.0028818 | 0.016257 | 0.026105 | -0.0028541 | -0.0070773 | -0.12985 | -0.003999 | 0.014063 | -0.010961 | 0.022366 | -0.004924 | 0.041199 | 0.16022 | 0.15106 | -0.32044 | 0.2655 | -0.53101 | -0.6958 | 0.041199 | -0.064087 | -0.022888 | 0.073242 | 0.004578 | -0.62256 | -0.62714 | -0.027466 | -0.19226 | -122.1176 | 0.66376 | 0.1831 | 0.37537 | -122.3419 | -0.11902 | -0.1236 | -122.3099 | 0.54474 | 0.48065 | 0.60425 | -122.3785 | 0.76904 | 0.54474 | 0.6546 | -123.0789 | 0.57678 | 0.50812 | 0.43945 | -123.0103
4428.0156 | 122.937 | -0.5127 | 122.4014 | 0.076141 | 0.0097989 | 0.005018 | 0.014548 | 0.023968 | -0.0026405 | -0.010282 | 0.045624 | -0.0059216 | 0.015344 | -0.011388 | 0.023221 | -0.0057786 | -0.027466 | 0.086975 | 0.11444 | -0.34332 | 0.27466 | -0.53101 | -0.71869 | 0.004578 | -0.14648 | -0.064087 | 0.068665 | 0.018311 | -0.63629 | -0.66834 | -0.018311 | -0.20599 | -122.1268 | 0.59967 | 0.16937 | 0.37537 | -122.4289 | -0.1236 | -0.15564 | -122.3328 | 0.51727 | 0.44861 | 0.60425 | -122.3831 | 0.78735 | 0.48523 | 0.62714 | -123.1201 | 0.58136 | 0.53101 | 0.36621 | -123.0698
4429.0156 | 122.9919 | -0.48523 | 122.3557 | -0.068817 | 0.0089443 | 0.0082224 | 0.017325 | 0.02525 | -0.00029045 | -0.010709 | -0.061188 | -0.0052808 | 0.014704 | -0.01267 | 0.024716 | -0.0047104 | 0.045776 | 0.15106 | 0.15106 | -0.33417 | 0.27466 | -0.52185 | -0.71411 | 0.068665 | -0.050354 | 0 | 0.086975 | 0.018311 | -0.62256 | -0.64087 | -0.036622 | -0.22888 | -122.081 | 0.63629 | 0.15106 | 0.37994 | -122.3099 | -0.13733 | -0.15564 | -122.2687 | 0.55389 | 0.48523 | 0.64087 | -122.3373 | 0.75989 | 0.53101 | 0.63629 | -123.0698 | 0.5722 | 0.50354 | 0.43488 | -122.9965
4430.0156 | 122.9782 | -0.50354 | 122.3877 | 0.0074768 | 0.0097989 | 0.0045908 | 0.017111 | 0.024396 | -0.0019995 | -0.0085727 | 0.015106 | -0.0048536 | 0.014704 | -0.011175 | 0.024289 | -0.0064194 | 0.004578 | 0.11444 | 0.10986 | -0.34332 | 0.28839 | -0.53101 | -0.70496 | 0.036621 | -0.10529 | -0.027466 | 0.073242 | 0.027466 | -0.63629 | -0.65002 | -0.027466 | -0.20142 | -122.0993 | 0.61798 | 0.16022 | 0.36163 | -122.3831 | -0.13275 | -0.14648 | -122.3145 | 0.54016 | 0.47607 | 0.62256 | -122.3602 | 0.79193 | 0.50812 | 0.6134 | -123.0927 | 0.57678 | 0.53101 | 0.39825 | -123.0377
4431.0156 | 122.9141 | -0.53101 | 122.4243 | -0.17563 | 0.018558 | 0.003309 | 0.020956 | 0.026959 | 0.0067589 | -0.0070773 | -0.19089 | -0.0016492 | 0.015772 | -0.011388 | 0.02728 | -0.010051 | 0.054932 | 0.050354 | 0.059509 | -0.34332 | 0.30212 | -0.54474 | -0.72784 | 0.022888 | -0.16479 | -0.14648 | 0.13275 | 0.032043 | -0.64087 | -0.67291 | -0.013733 | -0.19684 | -122.1222 | 0.58136 | 0.18768 | 0.38452 | -122.3694 | -0.10986 | -0.14191 | -122.2916 | 0.55389 | 0.38452 | 0.52643 | -122.3923 | 0.83313 | 0.58594 | 0.59052 | -123.1522 | 0.66376 | 0.56305 | 0.36621 | -123.0972
4432.0156 | 123.024 | -0.49439 | 122.3694 | -0.091705 | 0.0089443 | 0.0026682 | 0.014334 | 0.024823 | -0.0052039 | -0.0087863 | -0.038299 | -0.0054944 | 0.012781 | -0.010106 | 0.023007 | -0.0051376 | 0.027466 | 0.17395 | 0.15564 | -0.3067 | 0.2655 | -0.51727 | -0.6958 | 0.07782 | -0.073242 | -0.004578 | 0.091553 | 0.018311 | -0.59052 | -0.66376 | -0.022888 | -0.20142 | -122.1039 | 0.66834 | 0.18768 | 0.3891 | -122.3419 | -0.09613 | -0.16937 | -122.2778 | 0.57221 | 0.48981 | 0.65918 | -122.3511 | 0.75989 | 0.52185 | 0.65003 | -123.0652 | 0.58594 | 0.5127 | 0.42114 | -123.0331
4433.0156 | 122.937 | -0.52643 | 122.406 | -0.23666 | 0.012362 | 0.003309 | 0.018179 | 0.027173 | 0.0012047 | -0.010068 | -0.20615 | -0.003999 | 0.015558 | -0.01267 | 0.024716 | -0.0072738 | 0.027466 | 0.12817 | 0.12817 | -0.33875 | 0.27008 | -0.51727 | -0.71869 | -0.004578 | -0.11902 | -0.10986 | 0.09613 | 0.027466 | -0.63629 | -0.6546 | 0.009155 | -0.19226 | -122.1359 | 0.6546 | 0.18768 | 0.37994 | -122.3785 | -0.10986 | -0.12817 | -122.3099 | 0.52185 | 0.41657 | 0.54474 | -122.3785 | 0.79651 | 0.55389 | 0.6546 | -123.1247 | 0.62256 | 0.55389 | 0.40741 | -123.0606
4434.0156 | 123.0194 | -0.48981 | 122.4014 | -0.091705 | 0.012362 | 0.0058724 | 0.016684 | 0.026105 | -0.0017859 | -0.010922 | -0.15274 | -0.0069898 | 0.013422 | -0.01267 | 0.023434 | -0.0072738 | 0.018311 | 0.16937 | 0.16937 | -0.31128 | 0.27466 | -0.52185 | -0.71411 | 0.07782 | -0.054932 | 0.009155 | 0.073242 | 0.018311 | -0.64087 | -0.64087 | -0.032044 | -0.2243 | -122.1268 | 0.65918 | 0.17853 | 0.40283 | -122.3831 | -0.15106 | -0.15106 | -122.3282 | 0.56763 | 0.49896 | 0.65002 | -122.3831 | 0.76446 | 0.50812 | 0.65918 | -123.1155 | 0.56305 | 0.50812 | 0.43488 | -123.0423
4435.0156 | 122.8867 | -0.53101 | 122.4289 | -0.23666 | 0.011935 | 0.0065134 | 0.015189 | 0.027173 | 0.00056395 | -0.0092137 | -0.2214 | -0.0052808 | 0.011926 | -0.010106 | 0.022794 | -0.0057786 | 0.013733 | 0.10529 | 0.09613 | -0.34332 | 0.29755 | -0.54474 | -0.70953 | -0.041199 | -0.15564 | -0.1236 | 0.09613 | 0.027466 | -0.66834 | -0.68207 | -0.013733 | -0.17853 | -122.1313 | 0.63629 | 0.18768 | 0.36621 | -122.4152 | -0.13733 | -0.15106 | -122.3328 | 0.48981 | 0.40741 | 0.55847 | -122.4014 | 0.82855 | 0.54474 | 0.62714 | -123.1384 | 0.62714 | 0.55847 | 0.37537 | -123.111
4436.0156 | 122.9233 | -0.55389 | 122.4426 | -0.21378 | 0.016849 | 0.0056588 | 0.019248 | 0.025037 | 0.0031273 | -0.0062229 | -0.25192 | -0.0037854 | 0.015772 | -0.0094657 | 0.023648 | -0.0064194 | -0.041199 | 0.018311 | 0.022888 | -0.3891 | 0.30212 | -0.5722 | -0.76904 | -0.054932 | -0.1831 | -0.17395 | 0.11444 | 0.064087 | -0.6546 | -0.68665 | -0.018311 | -0.21515 | -122.1405 | 0.5722 | 0.1648 | 0.37994 | -122.4838 | -0.10071 | -0.13275 | -122.3282 | 0.49896 | 0.37994 | 0.5127 | -122.3785 | 0.85602 | 0.5127 | 0.57678 | -123.2117 | 0.66834 | 0.61798 | 0.37079 | -123.1293
4437.0156 | 122.8958 | -0.54016 | 122.4243 | -0.22141 | 0.012362 | 0.0037362 | 0.015402 | 0.029095 | -0.00071785 | -0.01135 | -0.27481 | -0.0042126 | 0.012354 | -0.011602 | 0.022794 | -0.0057786 | -0.004578 | 0.09613 | 0.07782 | -0.35248 | 0.29297 | -0.54016 | -0.737 | -0.045776 | -0.16479 | -0.12817 | 0.091553 | 0.041199 | -0.63171 | -0.70496 | 0 | -0.19684 | -122.1313 | 0.63629 | 0.18768 | 0.38452 | -122.4289 | -0.091553 | -0.1648 | -122.3328 | 0.49439 | 0.41199 | 0.57678 | -122.3831 | 0.83313 | 0.53558 | 0.61798 | -123.1613 | 0.63171 | 0.58136 | 0.37537 | -123.1293
4438.0156 | 122.9462 | -0.50354 | 122.3785 | -0.168 | 0.011508 | 0.0043772 | 0.014975 | 0.024396 | -0.0015723 | -0.0068637 | -0.19852 | -0.005708 | 0.010217 | -0.01032 | 0.024503 | -0.0047104 | 0.013733 | 0.15106 | 0.15106 | -0.32501 | 0.27008 | -0.53558 | -0.6958 | 0.018311 | -0.082397 | -0.064087 | 0.091553 | 0.013733 | -0.64545 | -0.65002 | -0.032043 | -0.19226 | -122.1085 | 0.6546 | 0.17853 | 0.37079 | -122.3648 | -0.14191 | -0.14648 | -122.287 | 0.52185 | 0.43945 | 0.58594 | -122.3648 | 0.77362 | 0.51727 | 0.6546 | -123.0743 | 0.59509 | 0.51727 | 0.42114 | -123.0286
4439.0156 | 122.8729 | -0.54932 | 122.4197 | -0.21378 | 0.013858 | 0.0028818 | 0.01882 | 0.028668 | 0.0027001 | -0.0083591 | -0.28244 | -0.00229 | 0.012567 | -0.011602 | 0.026212 | -0.004924 | -0.045776 | 0.013733 | 0.036621 | -0.40741 | 0.32044 | -0.5722 | -0.75073 | -0.054932 | -0.20142 | -0.15564 | 0.11444 | 0.036621 | -0.65918 | -0.67291 | -0.022889 | -0.20142 | -122.0993 | 0.56305 | 0.14191 | 0.34332 | -122.4655 | -0.10986 | -0.1236 | -122.3053 | 0.49438 | 0.39368 | 0.51727 | -122.3831 | 0.86975 | 0.50354 | 0.58594 | -123.1705 | 0.66376 | 0.58594 | 0.3479 | -123.0927
4440.0156 | 122.9416 | -0.50812 | 122.438 | -0.22141 | 0.012362 | 0.0054452 | 0.017539 | 0.025677 | -0.0041357 | -0.01135 | -0.19852 | -0.0027174 | 0.016413 | -0.010747 | 0.022366 | -0.0057786 | 0.013733 | 0.16937 | 0.13275 | -0.31128 | 0.27008 | -0.52643 | -0.70496 | 0.009155 | -0.10529 | -0.068665 | 0.082397 | 0.004578 | -0.64087 | -0.66376 | -0.01831 | -0.19684 | -122.168 | 0.67749 | 0.19684 | 0.39368 | -122.4243 | -0.13275 | -0.15564 | -122.3557 | 0.51727 | 0.43945 | 0.59509 | -122.4335 | 0.7782 | 0.52185 | 0.64087 | -123.143 | 0.59051 | 0.5127 | 0.40283 | -123.1018
4441.0156 | 122.9187 | -0.51727 | 122.4335 | -0.19852 | 0.018771 | 0.0041634 | 0.019248 | 0.025464 | 0.0063317 | -0.0077183 | -0.20615 | -0.0014356 | 0.015344 | -0.010961 | 0.027707 | -0.0068466 | 0.018311 | 0.07782 | 0.050354 | -0.3479 | 0.3067 | -0.55389 | -0.73242 | 0 | -0.16937 | -0.15106 | 0.11444 | 0.027466 | -0.64545 | -0.67291 | -0.036621 | -0.21515 | -122.1268 | 0.59509 | 0.16937 | 0.38452 | -122.4152 | -0.12817 | -0.15564 | -122.319 | 0.51727 | 0.36621 | 0.52185 | -122.406 | 0.82397 | 0.53558 | 0.56763 | -123.1659 | 0.63171 | 0.54474 | 0.3479 | -123.1064
4442.0156 | 123.0194 | -0.50812 | 122.4335 | -0.18326 | 0.010867 | 0.0037362 | 0.012839 | 0.024609 | -0.0043495 | -0.011991 | -0.11459 | -0.002931 | 0.013635 | -0.011175 | 0.024075 | -0.0042832 | 0.013733 | 0.16479 | 0.14191 | -0.29755 | 0.27466 | -0.52643 | -0.70953 | 0.041199 | -0.054932 | -0.041199 | 0.07782 | 0.013733 | -0.60883 | -0.64545 | -0.01831 | -0.20142 | -122.1588 | 0.67291 | 0.21057 | 0.41199 | -122.4197 | -0.10071 | -0.13733 | -122.3557 | 0.54932 | 0.46692 | 0.60425 | -122.4197 | 0.78278 | 0.52185 | 0.65002 | -123.143 | 0.58594 | 0.52185 | 0.45319 | -123.0789
4443.0156 | 122.8729 | -0.54016 | 122.4243 | -0.26718 | 0.011722 | 0.006727 | 0.016898 | 0.026532 | -0.00029045 | -0.0094273 | -0.31296 | -0.0031446 | 0.015558 | -0.010106 | 0.024289 | -0.004924 | -0.064087 | 0.022888 | 0.036621 | -0.37994 | 0.3067 | -0.58136 | -0.75073 | -0.059509 | -0.21057 | -0.15564 | 0.11902 | 0.054932 | -0.66376 | -0.68665 | -0.041199 | -0.21057 | -122.1176 | 0.56305 | 0.16022 | 0.37079 | -122.4884 | -0.1236 | -0.14648 | -122.3053 | 0.48065 | 0.38452 | 0.53101 | -122.3694 | 0.84686 | 0.47607 | 0.57678 | -123.175 | 0.65918 | 0.59509 | 0.32959 | -123.111
4444.0156 | 122.9279 | -0.53101 | 122.4426 | -0.21378 | 0.012576 | 0.0039498 | 0.016043 | 0.026532 | 0.0016321 | -0.0096409 | -0.17563 | -0.0018628 | 0.014917 | -0.0096793 | 0.023434 | -0.0036424 | 0 | 0.10529 | 0.09613 | -0.34332 | 0.27924 | -0.54474 | -0.74158 | -0.036621 | -0.16022 | -0.12817 | 0.09613 | 0.022888 | -0.64087 | -0.67749 | -0.013733 | -0.21057 | -122.1634 | 0.63629 | 0.18768 | 0.39825 | -122.4426 | -0.10986 | -0.14648 | -122.3465 | 0.49438 | 0.40283 | 0.54932 | -122.4197 | 0.81024 | 0.53101 | 0.62714 | -123.1842 | 0.62714 | 0.55389 | 0.37079 | -123.1201
4445.0156 | 122.937 | -0.52643 | 122.438 | -0.18326 | 0.017489 | 0.0035226 | 0.017539 | 0.026746 | 0.0046227 | -0.0094273 | -0.23666 | -0.0025038 | 0.014704 | -0.011815 | 0.027707 | -0.0072738 | -0.004578 | 0.059509 | 0.050354 | -0.3479 | 0.31128 | -0.56763 | -0.74158 | -0.018311 | -0.1831 | -0.14191 | 0.11902 | 0.027466 | -0.64087 | -0.67291 | -0.041199 | -0.21515 | -122.1268 | 0.58594 | 0.17853 | 0.39368 | -122.4426 | -0.11444 | -0.14648 | -122.319 | 0.50812 | 0.38452 | 0.53101 | -122.4106 | 0.83771 | 0.52185 | 0.57678 | -123.1796 | 0.64545 | 0.55389 | 0.34332 | -123.111
4446.0156 | 122.9095 | -0.58136 | 122.4472 | -0.25192 | 0.016208 | 0.0045908 | 0.018393 | 0.0276 | 0.0014185 | -0.0087863 | -0.24429 | -0.0037854 | 0.01449 | -0.010106 | 0.023434 | -0.0027878 | -0.059509 | 0.009155 | 0.018311 | -0.40283 | 0.31128 | -0.55847 | -0.76446 | -0.068665 | -0.21057 | -0.17853 | 0.11444 | 0.059509 | -0.6546 | -0.68207 | 0.022888 | -0.1831 | -122.1359 | 0.59052 | 0.17853 | 0.36163 | -122.5067 | -0.073242 | -0.10071 | -122.3328 | 0.5127 | 0.40283 | 0.50354 | -122.3877 | 0.89264 | 0.52185 | 0.59967 | -123.2117 | 0.6958 | 0.64087 | 0.37079 | -123.1293
4447.0156 | 122.9141 | -0.52643 | 122.4609 | -0.015411 | 0.020694 | 0.0041634 | 0.018393 | 0.024182 | 0.0048363 | -0.0047275 | -0.091705 | -0.0018628 | 0.014917 | -0.0092521 | 0.027493 | -0.005565 | 0.041199 | 0.059509 | 0.041199 | -0.36163 | 0.3067 | -0.54016 | -0.73242 | -0.022888 | -0.19684 | -0.16937 | 0.10986 | 0.054932 | -0.6546 | -0.66834 | -0.013733 | -0.20599 | -122.1542 | 0.58594 | 0.1648 | 0.37079 | -122.4197 | -0.12817 | -0.14191 | -122.3511 | 0.50354 | 0.35706 | 0.49896 | -122.406 | 0.83313 | 0.56763 | 0.56763 | -123.1934 | 0.63629 | 0.58136 | 0.32959 | -123.1293
4448.0156 | 122.8912 | -0.54016 | 122.4472 | -0.25192 | 0.015353 | 0.0054452 | 0.017966 | 0.026959 | -0.00093145 | -0.0081455 | -0.2214 | -0.0027174 | 0.012781 | -0.011388 | 0.024716 | -0.0051376 | -0.041199 | 0 | 0.013733 | -0.39368 | 0.31128 | -0.5722 | -0.75989 | -0.073242 | -0.21057 | -0.16479 | 0.1236 | 0.059509 | -0.64545 | -0.67291 | -0.032044 | -0.21973 | -122.1359 | 0.54016 | 0.14648 | 0.36621 | -122.4884 | -0.10529 | -0.13275 | -122.3236 | 0.46692 | 0.37537 | 0.50812 | -122.3877 | 0.85144 | 0.49896 | 0.55389 | -123.2071 | 0.66376 | 0.59967 | 0.32959 | -123.1201
4449.0156 | 122.9736 | -0.52643 | 122.4518 | -0.23666 | 0.017703 | 0.0030954 | 0.018607 | 0.027814 | 0.0020593 | -0.0079319 | -0.19852 | -0.0027174 | 0.015772 | -0.01267 | 0.025357 | -0.0042832 | -0.045776 | 0.022888 | 0.022888 | -0.36621 | 0.3067 | -0.55847 | -0.75531 | -0.045776 | -0.16479 | -0.14191 | 0.11444 | 0.041199 | -0.6546 | -0.68207 | -0.032044 | -0.22888 | -122.1451 | 0.54932 | 0.16022 | 0.3891 | -122.4976 | -0.12817 | -0.15564 | -122.3373 | 0.48065 | 0.38452 | 0.54016 | -122.4106 | 0.83313 | 0.48065 | 0.54932 | -123.2071 | 0.64087 | 0.56763 | 0.36163 | -123.1338
4450.0156 | 122.905 | -0.55389 | 122.4609 | -0.25192 | 0.012576 | 0.0035226 | 0.017111 | 0.028455 | -0.0015723 | -0.010922 | -0.18326 | -0.0037854 | 0.015772 | -0.011175 | 0.024716 | -0.0025742 | -0.064087 | 0.018311 | 0.032043 | -0.39825 | 0.29297 | -0.56763 | -0.75989 | -0.073242 | -0.20599 | -0.15106 | 0.11902 | 0.045776 | -0.67749 | -0.68207 | -0.013733 | -0.20599 | -122.168 | 0.5722 | 0.15564 | 0.36163 | -122.525 | -0.1236 | -0.12817 | -122.3419 | 0.48065 | 0.40283 | 0.53101 | -122.4152 | 0.84686 | 0.48981 | 0.58594 | -123.2208 | 0.67291 | 0.59967 | 0.3479 | -123.143
4451.0156 | 122.9507 | -0.53558 | 122.4564 | -0.084076 | 0.019198 | 0.0052316 | 0.017111 | 0.0276 | 0.0029137 | -0.0083591 | -0.076446 | -0.0042126 | 0.016626 | -0.0092521 | 0.025143 | -0.0068466 | 0.004578 | 0.064087 | 0.050354 | -0.35248 | 0.3067 | -0.54016 | -0.74616 | -0.022888 | -0.17395 | -0.15106 | 0.10071 | 0.041199 | -0.6546 | -0.67749 | -0.004578 | -0.21057 | -122.1497 | 0.59967 | 0.18311 | 0.39368 | -122.4518 | -0.11902 | -0.14191 | -122.3557 | 0.5127 | 0.38452 | 0.52643 | -122.4152 | 0.84228 | 0.54016 | 0.58594 | -123.2025 | 0.63629 | 0.57678 | 0.36163 | -123.1339
4452.0156 | 122.9599 | -0.54016 | 122.4426 | -0.20615 | 0.017917 | 0.005018 | 0.01882 | 0.026318 | 0.00013675 | -0.0070773 | -0.24429 | -0.0020764 | 0.01684 | -0.010961 | 0.025784 | -0.0053512 | 0 | 0.041199 | 0.041199 | -0.33875 | 0.29297 | -0.54932 | -0.73242 | -0.032043 | -0.16479 | -0.14648 | 0.10071 | 0.041199 | -0.65002 | -0.69122 | -0.009155 | -0.19226 | -122.1497 | 0.58136 | 0.20142 | 0.39368 | -122.4426 | -0.10986 | -0.15106 | -122.3419 | 0.50812 | 0.39368 | 0.54474 | -122.4014 | 0.83313 | 0.54016 | 0.58136 | -123.175 | 0.64087 | 0.58136 | 0.37537 | -123.1338
4453.0156 | 122.9141 | -0.54474 | 122.4701 | 0.022736 | 0.019412 | 0.0022408 | 0.016043 | 0.025891 | 0.0039819 | -0.0087863 | 0.022736 | -0.002931 | 0.015131 | -0.010961 | 0.025998 | -0.0051376 | -0.018311 | 0.022888 | 0.013733 | -0.37079 | 0.28839 | -0.54932 | -0.73242 | -0.054932 | -0.2243 | -0.1831 | 0.11444 | 0.059509 | -0.64087 | -0.68665 | -0.004577 | -0.18768 | -122.1817 | 0.56763 | 0.17395 | 0.36163 | -122.4884 | -0.09613 | -0.14191 | -122.3557 | 0.48981 | 0.36163 | 0.50354 | -122.4106 | 0.83313 | 0.52643 | 0.55847 | -123.2025 | 0.65918 | 0.60425 | 0.32043 | -123.1567
4454.0156 | 122.9645 | -0.53558 | 122.4564 | -0.14511 | 0.018344 | 0.0011728 | 0.017966 | 0.025464 | 0.0016321 | -0.0096409 | -0.14511 | -0.0027174 | 0.017053 | -0.0083975 | 0.02493 | -0.0057786 | -0.004578 | 0.054932 | 0.050354 | -0.3479 | 0.3067 | -0.54474 | -0.75073 | -0.027466 | -0.16937 | -0.15106 | 0.10071 | 0.045776 | -0.65002 | -0.66834 | -0.009156 | -0.21515 | -122.1497 | 0.59052 | 0.18768 | 0.40283 | -122.4609 | -0.11444 | -0.13275 | -122.3557 | 0.50812 | 0.38452 | 0.51727 | -122.4106 | 0.84228 | 0.53101 | 0.58594 | -123.2071 | 0.63629 | 0.58136 | 0.36621 | -123.1247
4455.0156 | 122.9095 | -0.54932 | 122.4152 | 0.099029 | 0.021121 | 0.0013864 | 0.017111 | 0.025464 | 0.00077755 | -0.0083591 | 0.12192 | -0.001222 | 0.017908 | -0.011175 | 0.024503 | -0.0053512 | -0.050354 | -0.054932 | -0.004578 | -0.3891 | 0.3067 | -0.56763 | -0.72327 | -0.073242 | -0.26093 | -0.17395 | 0.10529 | 0.050354 | -0.65918 | -0.6546 | -0.018311 | -0.17395 | -122.1085 | 0.49438 | 0.16022 | 0.33417 | -122.4655 | -0.10986 | -0.10529 | -122.3099 | 0.47607 | 0.37537 | 0.48065 | -122.3648 | 0.85602 | 0.49896 | 0.54474 | -123.1384 | 0.6546 | 0.59967 | 0.28839 | -123.0698
4456.0156 | 122.9645 | -0.53558 | 122.4701 | -0.22141 | 0.019839 | 0.0022408 | 0.01882 | 0.024609 | -0.00071785 | -0.010068 | -0.19089 | -0.0031446 | 0.013422 | -0.0094657 | 0.025143 | -0.0040696 | -0.032043 | 0.013733 | 0.041199 | -0.35706 | 0.27924 | -0.56763 | -0.75531 | -0.041199 | -0.16022 | -0.13275 | 0.10071 | 0.064087 | -0.65918 | -0.68207 | -0.032044 | -0.21973 | -122.1909 | 0.54932 | 0.17853 | 0.39825 | -122.5021 | -0.1236 | -0.14648 | -122.3694 | 0.49438 | 0.40283 | 0.54932 | -122.406 | 0.81482 | 0.50354 | 0.57678 | -123.2254 | 0.63629 | 0.59967 | 0.37537 | -123.1522
4457.0156 | 122.9233 | -0.52643 | 122.4609 | -0.00015269 | 0.016421 | 0.003309 | 0.018393 | 0.027173 | 0.0031273 | -0.0077183 | -0.015411 | -0.00229 | 0.015772 | -0.0090385 | 0.025571 | -0.003856 | -0.004578 | 0.004578 | 0.027466 | -0.37994 | 0.31128 | -0.55389 | -0.737 | -0.064087 | -0.21973 | -0.17853 | 0.09613 | 0.073242 | -0.64087 | -0.66376 | -0.027466 | -0.21057 | -122.1497 | 0.53101 | 0.14648 | 0.35706 | -122.4655 | -0.11444 | -0.13733 | -122.3648 | 0.46234 | 0.3479 | 0.48523 | -122.3877 | 0.83771 | 0.52185 | 0.55389 | -123.1979 | 0.62256 | 0.59967 | 0.3067 | -123.1247
4458.0156 | 122.9599 | -0.52643 | 122.4655 | -0.061188 | 0.017917 | 0.0058724 | 0.017111 | 0.028241 | 0.0020593 | -0.0098545 | -0.045929 | -0.0020764 | 0.015772 | -0.012243 | 0.025143 | -0.004924 | 0.013733 | 0.027466 | 0.050354 | -0.36163 | 0.28381 | -0.56305 | -0.74158 | -0.027466 | -0.16937 | -0.16022 | 0.10529 | 0.045776 | -0.63629 | -0.66376 | -0.036621 | -0.21515 | -122.1817 | 0.55389 | 0.1648 | 0.37994 | -122.4518 | -0.10986 | -0.13733 | -122.3602 | 0.49896 | 0.36621 | 0.50354 | -122.4197 | 0.81024 | 0.54016 | 0.57678 | -123.2071 | 0.63171 | 0.5722 | 0.35706 | -123.1293
4459.0156 | 123.0331 | -0.49896 | 122.4197 | 0.16769 | 0.017489 | 0.0030954 | 0.01583 | 0.027386 | -0.0015723 | -0.0092137 | 0.28214 | -0.0037854 | 0.014276 | -0.014165 | 0.023434 | -0.0053512 | 0.050354 | 0.09613 | 0.1236 | -0.32501 | 0.27008 | -0.52643 | -0.70496 | 0.018311 | -0.12817 | -0.045776 | 0.068665 | 0.018311 | -0.61798 | -0.64087 | -0.027466 | -0.20599 | -122.1497 | 0.59509 | 0.17395 | 0.37994 | -122.3694 | -0.11902 | -0.14191 | -122.3511 | 0.51727 | 0.45319 | 0.59509 | -122.4014 | 0.76904 | 0.54932 | 0.62256 | -123.1247 | 0.56763 | 0.51727 | 0.37079 | -123.0606
4460.0156 | 122.9279 | -0.54016 | 122.493 | -0.03067 | 0.020907 | 0.005018 | 0.01583 | 0.025464 | 0.0024865 | -0.0081455 | -0.023041 | -0.0033582 | 0.015772 | -0.011602 | 0.023648 | -0.004924 | -0.013733 | -0.013733 | 0.009155 | -0.37537 | 0.3067 | -0.54932 | -0.73242 | -0.086975 | -0.24719 | -0.19226 | 0.09613 | 0.073242 | -0.66376 | -0.68207 | -0.009155 | -0.19226 | -122.1863 | 0.52643 | 0.1648 | 0.35706 | -122.5067 | -0.1236 | -0.14191 | -122.3969 | 0.45319 | 0.3479 | 0.48981 | -122.4197 | 0.84686 | 0.52643 | 0.54932 | -123.2254 | 0.63629 | 0.6134 | 0.29297 | -123.175
4461.0156 | 122.9965 | -0.5127 | 122.4655 | 0.16769 | 0.01813 | 0.005018 | 0.015616 | 0.025891 | 0.0022729 | -0.011777 | 0.17532 | -0.002931 | 0.014704 | -0.0083975 | 0.022794 | -0.004924 | -0.027466 | -0.041199 | 0.013733 | -0.3891 | 0.29755 | -0.54016 | -0.73242 | -0.032043 | -0.21057 | -0.12817 | 0.10071 | 0.041199 | -0.64087 | -0.67291 | -0.027466 | -0.21973 | -122.168 | 0.4715 | 0.1236 | 0.34332 | -122.493 | -0.12817 | -0.16022 | -122.3648 | 0.48065 | 0.38452 | 0.54474 | -122.4243 | 0.81024 | 0.48523 | 0.52643 | -123.1979 | 0.6134 | 0.55389 | 0.30212 | -123.1384
4462.0156 | 122.9324 | -0.54016 | 122.4655 | 0.030365 | 0.019626 | 0.0073678 | 0.019248 | 0.026746 | 0.0014185 | -0.0075047 | -0.0077819 | -0.001222 | 0.016413 | -0.0092521 | 0.025571 | -0.0057786 | -0.045776 | -0.022888 | -0.004578 | -0.40283 | 0.30212 | -0.5722 | -0.74158 | -0.09613 | -0.25635 | -0.20142 | 0.11902 | 0.054932 | -0.6546 | -0.69122 | -0.032044 | -0.20142 | -122.1634 | 0.51727 | 0.13733 | 0.33875 | -122.5113 | -0.11444 | -0.15106 | -122.3465 | 0.44403 | 0.33874 | 0.48981 | -122.4106 | 0.84228 | 0.49439 | 0.53558 | -123.2071 | 0.65918 | 0.59509 | 0.28381 | -123.1567
4463.0156 | 122.9965 | -0.52185 | 122.4472 | 0.17532 | 0.018985 | 0.0056588 | 0.014548 | 0.026746 | 0.0018457 | -0.0089999 | 0.20584 | -0.002931 | 0.015131 | -0.011388 | 0.025357 | -0.0042832 | -0.013733 | -0.018311 | 0.013733 | -0.37537 | 0.30212 | -0.54474 | -0.72784 | -0.032043 | -0.20599 | -0.11902 | 0.091553 | 0.041199 | -0.65002 | -0.6546 | -0.022888 | -0.20599 | -122.1451 | 0.50354 | 0.14648 | 0.35248 | -122.4609 | -0.12817 | -0.13275 | -122.3557 | 0.48981 | 0.40283 | 0.53558 | -122.406 | 0.82397 | 0.50812 | 0.53558 | -123.175 | 0.6134 | 0.56305 | 0.31586 | -123.1018
4464.0156 | 122.9141 | -0.54932 | 122.4564 | 0.030365 | 0.019198 | 0.0035226 | 0.016257 | 0.026318 | 0.00099115 | -0.0087863 | 0.022736 | -0.0033582 | 0.013635 | -0.010747 | 0.027066 | -0.0051376 | 0 | -0.009155 | 0.013733 | -0.36163 | 0.30212 | -0.54016 | -0.75073 | -0.064087 | -0.21515 | -0.20599 | 0.10071 | 0.059509 | -0.66376 | -0.69122 | 0.009155 | -0.20142 | -122.1542 | 0.54016 | 0.18768 | 0.3891 | -122.4564 | -0.11444 | -0.14191 | -122.3557 | 0.48523 | 0.34332 | 0.48523 | -122.3969 | 0.85144 | 0.54932 | 0.56305 | -123.2071 | 0.65002 | 0.60883 | 0.33417 | -123.1476
4465.0156 | 123.0331 | -0.50812 | 122.4335 | 0.18295 | 0.018344 | 0.0041634 | 0.016898 | 0.024609 | 0.00013675 | -0.0083591 | 0.21347 | -0.001222 | 0.016413 | -0.0092521 | 0.02493 | -0.0057786 | -0.004578 | 0.022888 | 0.050354 | -0.38452 | 0.28381 | -0.52185 | -0.71869 | 0.022888 | -0.17853 | -0.07782 | 0.082397 | 0.022888 | -0.65002 | -0.63171 | -0.013733 | -0.21057 | -122.1497 | 0.53101 | 0.1236 | 0.33417 | -122.438 | -0.14191 | -0.1236 | -122.3511 | 0.53101 | 0.4303 | 0.55389 | -122.4106 | 0.79193 | 0.50354 | 0.55847 | -123.1522 | 0.59051 | 0.53101 | 0.32959 | -123.0652
4466.0156 | 122.9416 | -0.53101 | 122.4609 | 0.12192 | 0.019839 | 0.0056588 | 0.019675 | 0.025891 | 0.00035035 | -0.0096409 | 0.16769 | -0.0010084 | 0.017694 | -0.0075431 | 0.023648 | -0.0059922 | -0.032043 | -0.045776 | -0.009155 | -0.40283 | 0.29297 | -0.55847 | -0.71869 | -0.059509 | -0.25177 | -0.16022 | 0.10986 | 0.068665 | -0.63629 | -0.67291 | -0.027466 | -0.18768 | -122.168 | 0.48523 | 0.12817 | 0.31586 | -122.493 | -0.10529 | -0.14191 | -122.3511 | 0.4715 | 0.37079 | 0.5127 | -122.3923 | 0.82397 | 0.49896 | 0.52185 | -123.1796 | 0.64087 | 0.59967 | 0.27924 | -123.1338
4467.0156 | 123.056 | -0.47607 | 122.4518 | 0.19058 | 0.015994 | 0.005018 | 0.013693 | 0.028027 | -0.0015723 | -0.0094273 | 0.2211 | -0.0048536 | 0.014063 | -0.010534 | 0.025143 | -0.0025742 | 0.059509 | 0.07782 | 0.10986 | -0.32044 | 0.27466 | -0.50354 | -0.68665 | 0.045776 | -0.1236 | -0.050354 | 0.068665 | 0.004578 | -0.59967 | -0.63629 | -0.027466 | -0.21057 | -122.1771 | 0.55389 | 0.15564 | 0.36621 | -122.3923 | -0.1236 | -0.16022 | -122.3831 | 0.52185 | 0.42572 | 0.58594 | -122.4472 | 0.75073 | 0.53558 | 0.58594 | -123.1384 | 0.54474 | 0.48065 | 0.35248 | -123.0881
4468.0156 | 122.9736 | -0.53558 | 122.4609 | 0.16769 | 0.01813 | 0.003309 | 0.018607 | 0.023968 | -0.0011451 | -0.0079319 | 0.16006 | -0.0027174 | 0.015985 | -0.011388 | 0.025998 | -0.004924 | -0.018311 | -0.059509 | 0.009155 | -0.3891 | 0.31128 | -0.56305 | -0.73242 | -0.018311 | -0.24261 | -0.16022 | 0.10529 | 0.054932 | -0.63629 | -0.69122 | -0.027466 | -0.19684 | -122.1497 | 0.47607 | 0.14648 | 0.34332 | -122.4792 | -0.10071 | -0.15564 | -122.3557 | 0.51727 | 0.37537 | 0.53101 | -122.406 | 0.84686 | 0.51727 | 0.54474 | -123.1934 | 0.64087 | 0.59052 | 0.29297 | -123.1522
4469.0156 | 123.0469 | -0.50812 | 122.4426 | 0.18295 | 0.016421 | 0.0041634 | 0.014121 | 0.0276 | -0.0047767 | -0.0092137 | 0.26688 | -0.0031446 | 0.016199 | -0.010961 | 0.023862 | -0.0044968 | 0.073242 | 0.082397 | 0.13275 | -0.29297 | 0.26093 | -0.52643 | -0.68665 | 0.036621 | -0.13733 | -0.064087 | 0.068665 | 0.022888 | -0.59967 | -0.63629 | -0.01831 | -0.17853 | -122.1817 | 0.59051 | 0.21515 | 0.39368 | -122.3694 | -0.091552 | -0.12817 | -122.374 | 0.54474 | 0.44403 | 0.5722 | -122.4197 | 0.76904 | 0.58136 | 0.64087 | -123.1293 | 0.57678 | 0.53101 | 0.37079 | -123.0789
4470.0156 | 122.9279 | -0.53101 | 122.4701 | 0.12955 | 0.01813 | 0.0048044 | 0.015616 | 0.025464 | 0.0024865 | -0.010282 | 0.09903 | -0.0020764 | 0.016413 | -0.011815 | 0.026212 | -0.0040696 | -0.027466 | -0.059509 | -0.013733 | -0.39825 | 0.32044 | -0.55389 | -0.71869 | -0.064087 | -0.25635 | -0.20142 | 0.11902 | 0.045776 | -0.67291 | -0.67291 | -0.022888 | -0.18768 | -122.1497 | 0.4715 | 0.13275 | 0.32044 | -122.4976 | -0.14191 | -0.14191 | -122.3511 | 0.46692 | 0.32959 | 0.4715 | -122.4243 | 0.85144 | 0.50354 | 0.51727 | -123.1888 | 0.65002 | 0.57678 | 0.27466 | -123.143
4471.0156 | 123.0515 | -0.50354 | 122.4518 | 0.23636 | 0.014712 | 0.005018 | 0.015189 | 0.026532 | -0.00050425 | -0.010068 | 0.22873 | -0.0048536 | 0.013208 | -0.010961 | 0.023648 | -0.0057786 | 0.073242 | 0.07782 | 0.12817 | -0.30212 | 0.2655 | -0.51727 | -0.70038 | 0.041199 | -0.12817 | -0.050354 | 0.068665 | 0.027466 | -0.60883 | -0.64087 | -0.013733 | -0.19684 | -122.1863 | 0.58136 | 0.20142 | 0.39825 | -122.3785 | -0.10529 | -0.13733 | -122.3831 | 0.54474 | 0.45319 | 0.59052 | -122.4243 | 0.76904 | 0.57678 | 0.63171 | -123.1522 | 0.5722 | 0.53101 | 0.37537 | -123.0927
4472.0156 | 122.9691 | -0.5127 | 122.4472 | 0.18295 | 0.018558 | 0.0037362 | 0.01882 | 0.026746 | 0.00099115 | -0.0068637 | 0.17532 | -0.0025038 | 0.015131 | -0.0096793 | 0.024503 | -0.0036424 | -0.022888 | -0.022888 | 0.022888 | -0.37994 | 0.29755 | -0.55847 | -0.72327 | -0.022888 | -0.23346 | -0.16022 | 0.12817 | 0.050354 | -0.63629 | -0.66376 | -0.045777 | -0.21057 | -122.1497 | 0.48981 | 0.13275 | 0.34332 | -122.4701 | -0.1236 | -0.15106 | -122.319 | 0.48981 | 0.35248 | 0.50354 | -122.3969 | 0.81024 | 0.48981 | 0.53558 | -123.1705 | 0.64087 | 0.56305 | 0.27924 | -123.111
4473.0156 | 123.024 | -0.5127 | 122.4518 | 0.19821 | 0.013217 | 0.003309 | 0.016043 | 0.024396 | -0.0052039 | -0.010068 | 0.23636 | -0.0044264 | 0.014917 | -0.0086111 | 0.022366 | -0.0047104 | 0.013733 | 0.032043 | 0.082397 | -0.36163 | 0.2655 | -0.5127 | -0.70038 | -0.004578 | -0.17853 | -0.068665 | 0.073242 | 0.022888 | -0.60883 | -0.6546 | 0 | -0.18768 | -122.1863 | 0.54474 | 0.15106 | 0.33874 | -122.438 | -0.096131 | -0.14191 | -122.3785 | 0.50812 | 0.44403 | 0.58594 | -122.4289 | 0.7782 | 0.52643 | 0.59509 | -123.1522 | 0.58594 | 0.53558 | 0.33417 | -123.1064
4474.0156 | 123.0881 | -0.50354 | 122.4564 | 0.13718 | 0.01514 | 0.0020272 | 0.015402 | 0.025677 | 0.0024865 | -0.0092137 | 0.0914 | -0.00464 | 0.014276 | -0.010747 | 0.025357 | -0.0053512 | 0.041199 | 0.041199 | 0.10986 | -0.32959 | 0.28381 | -0.51727 | -0.70038 | 0.032043 | -0.13275 | -0.07782 | 0.064087 | 0.041199 | -0.62256 | -0.63171 | -0.013733 | -0.19684 | -122.1725 | 0.54474 | 0.17395 | 0.37079 | -122.4152 | -0.11902 | -0.12817 | -122.3923 | 0.53558 | 0.42572 | 0.55389 | -122.4152 | 0.78735 | 0.54474 | 0.6134 | -123.1567 | 0.56763 | 0.54474 | 0.37079 | -123.0881
4475.0156 | 123.0057 | -0.48981 | 122.4792 | 0.16006 | 0.014712 | 0.0052316 | 0.01348 | 0.028027 | -0.0041357 | -0.0098545 | 0.12955 | -0.0059216 | 0.014917 | -0.0096793 | 0.024503 | -0.0042832 | 0.050354 | 0.091553 | 0.13275 | -0.32044 | 0.25177 | -0.52185 | -0.6958 | 0.022888 | -0.14648 | -0.064087 | 0.086975 | 0.022888 | -0.62256 | -0.62714 | -0.032044 | -0.20599 | -122.2275 | 0.58136 | 0.16937 | 0.37537 | -122.4289 | -0.13275 | -0.13733 | -122.3923 | 0.5127 | 0.42572 | 0.56305 | -122.4564 | 0.74158 | 0.54016 | 0.62256 | -123.175 | 0.57678 | 0.5127 | 0.34332 | -123.1064
4476.0156 | 123.056 | -0.48981 | 122.4701 | 0.2211 | 0.017703 | 0.003309 | 0.018607 | 0.023755 | 0.0027001 | -0.0087863 | 0.030365 | -0.0035718 | 0.014704 | -0.0094657 | 0.02493 | -0.0074876 | 0.036621 | -0.032043 | 0.073242 | -0.34332 | 0.29755 | -0.53558 | -0.70496 | 0.050354 | -0.16937 | -0.09613 | 0.09613 | 0.022888 | -0.61798 | -0.64545 | -0.045776 | -0.21515 | -122.1725 | 0.45776 | 0.14648 | 0.36163 | -122.4335 | -0.12817 | -0.15564 | -122.374 | 0.54016 | 0.39368 | 0.54932 | -122.4472 | 0.78735 | 0.52643 | 0.56305 | -123.175 | 0.58594 | 0.5127 | 0.32043 | -123.1155
4477.0156 | 123.0789 | -0.46692 | 122.4564 | 0.099029 | 0.014926 | 0.0048044 | 0.01583 | 0.0276 | 0.00077755 | -0.0098545 | 0.31265 | -0.00464 | 0.013849 | -0.0096793 | 0.025143 | -0.0059922 | 0.054932 | 0.10529 | 0.13733 | -0.3067 | 0.26093 | -0.48523 | -0.67291 | 0.032043 | -0.13275 | -0.054932 | 0.07782 | 0.036621 | -0.61798 | -0.61798 | -0.01831 | -0.20599 | -122.1954 | 0.5722 | 0.16022 | 0.36621 | -122.4014 | -0.15106 | -0.15106 | -122.3785 | 0.49896 | 0.41199 | 0.56305 | -122.4197 | 0.72784 | 0.52185 | 0.60425 | -123.1293 | 0.54474 | 0.50354 | 0.33417 | -123.0743
4478.0156 | 123.0515 | -0.51727 | 122.4655 | 0.17532 | 0.019626 | 0.005018 | 0.017966 | 0.025891 | 0.0039819 | -0.0079319 | 0.060883 | -0.0042126 | 0.016199 | -0.011175 | 0.024716 | -0.0059922 | 0.022888 | -0.004578 | 0.050354 | -0.35706 | 0.29755 | -0.52643 | -0.72327 | 0.032043 | -0.17395 | -0.10529 | 0.073242 | 0.041199 | -0.62256 | -0.6546 | -0.009155 | -0.20599 | -122.168 | 0.5127 | 0.16022 | 0.36621 | -122.4426 | -0.10529 | -0.13733 | -122.3923 | 0.54932 | 0.41199 | 0.54932 | -122.4243 | 0.81482 | 0.54016 | 0.56763 | -123.1888 | 0.59052 | 0.55847 | 0.34332 | -123.1201
4479.0156 | 123.0469 | -0.50354 | 122.4655 | 0.0914 | 0.011508 | 0.0054452 | 0.013693 | 0.025464 | -0.0052039 | -0.012631 | 0.18295 | -0.005708 | 0.011713 | -0.011388 | 0.023862 | -0.0040696 | 0.050354 | 0.050354 | 0.07782 | -0.3479 | 0.2655 | -0.52643 | -0.6958 | 0.018311 | -0.16479 | -0.086975 | 0.073242 | 0.027466 | -0.62256 | -0.62714 | -0.022888 | -0.19226 | -122.2 | 0.55389 | 0.15564 | 0.3479 | -122.4152 | -0.11902 | -0.1236 | -122.3923 | 0.52185 | 0.41656 | 0.54016 | -122.438 | 0.76904 | 0.55389 | 0.58136 | -123.1613 | 0.57678 | 0.53101 | 0.33874 | -123.0927
4480.0156 | 123.0743 | -0.49439 | 122.4747 | 0.13718 | 0.016208 | 0.0013864 | 0.016898 | 0.027814 | 0.0029137 | -0.0081455 | 0.17532 | -0.002931 | 0.017694 | -0.010534 | 0.026212 | -0.0079148 | 0.07782 | 0.09613 | 0.1236 | -0.32044 | 0.2655 | -0.49896 | -0.6958 | 0.050354 | -0.13733 | -0.045776 | 0.045776 | 0.018311 | -0.63629 | -0.62714 | -0.004577 | -0.20142 | -122.2092 | 0.59052 | 0.17395 | 0.37537 | -122.3969 | -0.14191 | -0.13275 | -122.4289 | 0.54474 | 0.44861 | 0.58136 | -122.4564 | 0.75989 | 0.57221 | 0.61798 | -123.1705 | 0.54016 | 0.5127 | 0.35706 | -123.1018
4481.0156 | 123.024 | -0.5127 | 122.4747 | -0.023041 | 0.01279 | 0.0065134 | 0.01647 | 0.026746 | -0.0019995 | -0.010709 | 0.14481 | -0.0050672 | 0.014917 | -0.0096793 | 0.023007 | -0.0042832 | 0.013733 | 0.022888 | 0.09613 | -0.3479 | 0.27466 | -0.53101 | -0.71411 | -0.004578 | -0.16479 | -0.082397 | 0.07782 | 0.018311 | -0.63171 | -0.64087 | -0.018311 | -0.20142 | -122.2 | 0.53558 | 0.1648 | 0.36621 | -122.4609 | -0.11902 | -0.12817 | -122.3969 | 0.50812 | 0.4303 | 0.55847 | -122.4564 | 0.78735 | 0.52643 | 0.60882 | -123.1888 | 0.59052 | 0.53101 | 0.3479 | -123.1155
4482.0156 | 123.0789 | -0.48981 | 122.438 | 0.053253 | 0.018558 | 0.0016 | 0.016898 | 0.024823 | -0.00029045 | -0.0072911 | 0.18295 | -0.0054944 | 0.015344 | -0.010961 | 0.025357 | -0.0051376 | 0.082397 | 0.07782 | 0.10071 | -0.28381 | 0.27008 | -0.5127 | -0.69122 | 0.064087 | -0.13275 | -0.073242 | 0.059509 | 0.009155 | -0.6134 | -0.64087 | -0.022888 | -0.20142 | -122.168 | 0.56763 | 0.20599 | 0.40741 | -122.3557 | -0.1236 | -0.15106 | -122.3785 | 0.55389 | 0.41656 | 0.56763 | -122.4289 | 0.75989 | 0.5722 | 0.59052 | -123.1293 | 0.54932 | 0.49896 | 0.35706 | -123.0789
4483.0156 | 123.0377 | -0.50354 | 122.4701 | 0.25162 | 0.011722 | 0.0035226 | 0.015189 | 0.026959 | -0.0017859 | -0.0083591 | 0.045624 | -0.0048536 | 0.01214 | -0.010106 | 0.026639 | -0.006633 | 0.036621 | 0.09613 | 0.13275 | -0.32959 | 0.27466 | -0.52185 | -0.6958 | 0.032043 | -0.1831 | -0.082397 | 0.064087 | 0.018311 | -0.62256 | -0.64545 | -0.018311 | -0.19226 | -122.1954 | 0.59967 | 0.17395 | 0.36621 | -122.4335 | -0.11902 | -0.14191 | -122.406 | 0.53558 | 0.42114 | 0.56305 | -122.4518 | 0.7782 | 0.54016 | 0.63629 | -123.1659 | 0.56763 | 0.52185 | 0.32044 | -123.1155
4484.0156 | 122.9782 | -0.53101 | 122.4792 | 0.15244 | 0.018558 | 0.0048044 | 0.017539 | 0.026959 | 0.0035547 | -0.0070773 | 0.18295 | -0.0037854 | 0.015558 | -0.0096793 | 0.026425 | -0.0062058 | 0.018311 | -0.022888 | 0.009155 | -0.3891 | 0.3067 | -0.53101 | -0.72327 | 0.013733 | -0.22888 | -0.14191 | 0.086975 | 0.004578 | -0.64087 | -0.6546 | 0 | -0.19226 | -122.1725 | 0.50812 | 0.14191 | 0.33417 | -122.4609 | -0.10986 | -0.1236 | -122.3923 | 0.54474 | 0.3891 | 0.5127 | -122.4747 | 0.83771 | 0.54932 | 0.54016 | -123.2025 | 0.61798 | 0.53558 | 0.30212 | -123.1338
4485.0156 | 123.0515 | -0.49896 | 122.4976 | 0.076141 | 0.011935 | 0.0030954 | 0.01583 | 0.024396 | -0.0032813 | -0.0079319 | 0.26688 | -0.0037854 | 0.012781 | -0.01032 | 0.025998 | -0.0042832 | 0.054932 | 0.12817 | 0.12817 | -0.32044 | 0.27466 | -0.52185 | -0.69122 | 0.036621 | -0.15106 | -0.068665 | 0.068665 | 0.022888 | -0.59967 | -0.64087 | -0.022889 | -0.19226 | -122.2229 | 0.62714 | 0.17853 | 0.37079 | -122.4426 | -0.10071 | -0.14191 | -122.4289 | 0.53558 | 0.4303 | 0.5722 | -122.4747 | 0.77362 | 0.55389 | 0.62714 | -123.1888 | 0.56763 | 0.52185 | 0.3479 | -123.1384
4486.0156 | 123.0606 | -0.49896 | 122.4335 | 0.25925 | 0.013858 | 0.0024544 | 0.015616 | 0.023755 | 0.0014185 | -0.0087863 | 0.12955 | -0.00464 | 0.012781 | -0.012456 | 0.025143 | -0.0068466 | 0.07782 | 0.091553 | 0.13733 | -0.31128 | 0.26093 | -0.5127 | -0.6958 | 0.068665 | -0.14191 | -0.059509 | 0.073242 | 0.004578 | -0.60883 | -0.64087 | -0.013733 | -0.19684 | -122.1725 | 0.59052 | 0.18768 | 0.38452 | -122.3557 | -0.10986 | -0.14191 | -122.3602 | 0.56763 | 0.43945 | 0.58136 | -122.4289 | 0.75989 | 0.57678 | 0.63629 | -123.1293 | 0.5722 | 0.50354 | 0.35706 | -123.0743
4487.0156 | 123.0103 | -0.50354 | 122.4609 | 0.16769 | 0.0097989 | 0.0048044 | 0.015616 | 0.024609 | -0.00071785 | -0.010068 | 0.23636 | -0.0048536 | 0.012995 | -0.013311 | 0.023434 | -0.0077012 | 0.009155 | 0.045776 | 0.086975 | -0.34332 | 0.29297 | -0.50812 | -0.70953 | 0.004578 | -0.17853 | -0.07782 | 0.09613 | 0.022888 | -0.63171 | -0.65002 | -0.004578 | -0.20599 | -122.168 | 0.54932 | 0.16022 | 0.36621 | -122.4518 | -0.12817 | -0.14648 | -122.3648 | 0.50812 | 0.42572 | 0.5722 | -122.438 | 0.79651 | 0.5127 | 0.59052 | -123.1705 | 0.59967 | 0.52643 | 0.32501 | -123.111
4488.0156 | 123.0927 | -0.48981 | 122.4472 | 0.053253 | 0.014926 | 0.0035226 | 0.017111 | 0.024609 | 0.0022729 | -0.012204 | 0.19058 | -0.0044264 | 0.013849 | -0.011602 | 0.02728 | -0.006633 | 0.07782 | 0.082397 | 0.1236 | -0.31586 | 0.25177 | -0.50354 | -0.6958 | 0.068665 | -0.13275 | -0.064087 | 0.064087 | 0.009155 | -0.61798 | -0.62256 | -0.013733 | -0.20599 | -122.1954 | 0.5722 | 0.17395 | 0.37994 | -122.3694 | -0.12817 | -0.13275 | -122.3831 | 0.55847 | 0.42572 | 0.55847 | -122.438 | 0.74158 | 0.56763 | 0.6134 | -123.143 | 0.55389 | 0.49896 | 0.35706 | -123.0698
4489.0156 | 123.0423 | -0.5127 | 122.4838 | -0.12985 | 0.011294 | 0.0037362 | 0.015402 | 0.025037 | -0.0062721 | -0.011136 | 0.0074766 | -0.0044264 | 0.011713 | -0.010961 | 0.023862 | -0.0040696 | 0.004578 | 0.050354 | 0.09613 | -0.33417 | 0.28381 | -0.51727 | -0.71869 | 0.022888 | -0.15564 | -0.064087 | 0.07782 | 0.004578 | -0.61798 | -0.64087 | -0.004578 | -0.20599 | -122.2 | 0.56305 | 0.17853 | 0.38452 | -122.4792 | -0.10529 | -0.12817 | -122.406 | 0.53558 | 0.44861 | 0.57678 | -122.4792 | 0.79651 | 0.51727 | 0.60882 | -123.2025 | 0.59052 | 0.51727 | 0.35706 | -123.1247
4490.0156 | 123.0835 | -0.50354 | 122.4838 | 0.18295 | 0.018771 | 0.0056588 | 0.016257 | 0.025891 | 0.0035547 | -0.0075047 | 0.0074766 | -0.002931 | 0.014704 | -0.010534 | 0.025571 | -0.0085556 | 0.068665 | 0.054932 | 0.073242 | -0.32959 | 0.27924 | -0.52185 | -0.70038 | 0.059509 | -0.16022 | -0.07782 | 0.082397 | 0.009155 | -0.63171 | -0.63171 | -0.018311 | -0.19684 | -122.2046 | 0.55847 | 0.17395 | 0.37079 | -122.4152 | -0.12817 | -0.12817 | -122.4014 | 0.56305 | 0.42572 | 0.55389 | -122.4747 | 0.78278 | 0.5722 | 0.57678 | -123.1842 | 0.58594 | 0.5127 | 0.34332 | -123.1155
4491.0156 | 123.024 | -0.51727 | 122.4701 | -0.053558 | 0.013217 | 0.005018 | 0.013693 | 0.026105 | -0.00071785 | -0.0092137 | 0.076141 | -0.003999 | 0.014917 | -0.0096793 | 0.022366 | -0.0042832 | 0.054932 | 0.10986 | 0.11902 | -0.3479 | 0.27008 | -0.53101 | -0.70953 | 0.050354 | -0.14648 | -0.064087 | 0.041199 | 0.004578 | -0.62256 | -0.65918 | -0.013733 | -0.19226 | -122.2 | 0.62714 | 0.16937 | 0.36163 | -122.4152 | -0.10529 | -0.14191 | -122.4289 | 0.56763 | 0.45319 | 0.59509 | -122.4655 | 0.78735 | 0.5722 | 0.63629 | -123.1796 | 0.55847 | 0.52185 | 0.37079 | -123.1293
4492.0156 | 123.0927 | -0.49439 | 122.4655 | 0.33554 | 0.015994 | 0.0018136 | 0.015402 | 0.027814 | 0.00099115 | -0.0083591 | 0.23636 | -0.0037854 | 0.01214 | -0.0094657 | 0.025143 | -0.0057786 | 0.09613 | 0.054932 | 0.10986 | -0.3067 | 0.25177 | -0.52185 | -0.68665 | 0.082397 | -0.12817 | -0.059509 | 0.059509 | -0.009155 | -0.63171 | -0.65002 | -0.027466 | -0.19226 | -122.2137 | 0.54932 | 0.18768 | 0.37994 | -122.3694 | -0.13733 | -0.15564 | -122.406 | 0.57678 | 0.43488 | 0.59052 | -122.4747 | 0.74616 | 0.59052 | 0.60425 | -123.1522 | 0.55389 | 0.48523 | 0.36621 | -123.1155
4493.0156 | 123.0515 | -0.51727 | 122.5021 | 0.099029 | 0.011081 | 0.0045908 | 0.015616 | 0.025037 | -0.0037085 | -0.0083591 | 0.030365 | -0.0042126 | 0.014704 | -0.0090385 | 0.023007 | -0.0047104 | 0.004578 | 0.064087 | 0.09613 | -0.33417 | 0.27924 | -0.53101 | -0.70496 | 0.022888 | -0.14648 | -0.064087 | 0.073242 | 0.022888 | -0.64545 | -0.64545 | -0.013733 | -0.18768 | -122.2229 | 0.58136 | 0.18311 | 0.37079 | -122.4976 | -0.12817 | -0.12817 | -122.4289 | 0.54016 | 0.45319 | 0.58136 | -122.4792 | 0.79651 | 0.52185 | 0.6134 | -123.2071 | 0.59052 | 0.54016 | 0.37079 | -123.1476
4494.0156 | 123.0469 | -0.49896 | 122.493 | 0.16769 | 0.017276 | 0.0054452 | 0.01583 | 0.026532 | -0.0011451 | -0.010709 | 0.076141 | -0.0031446 | 0.015131 | -0.011602 | 0.024503 | -0.003856 | 0.07782 | 0.10071 | 0.11444 | -0.32959 | 0.26093 | -0.49896 | -0.70038 | 0.041199 | -0.14648 | -0.068665 | 0.068665 | 0.009155 | -0.62256 | -0.64545 | 0 | -0.20142 | -122.2321 | 0.59967 | 0.16937 | 0.37079 | -122.4152 | -0.1236 | -0.14648 | -122.4243 | 0.54016 | 0.4303 | 0.57678 | -122.4838 | 0.75989 | 0.57678 | 0.6134 | -123.1934 | 0.56763 | 0.50812 | 0.35248 | -123.1384
4495.0156 | 123.0515 | -0.49439 | 122.4838 | -0.0383 | 0.010867 | 0.003309 | 0.014975 | 0.024823 | -0.0019995 | -0.010282 | 0.022736 | -0.0033582 | 0.013635 | -0.0090385 | 0.022366 | -0.0044968 | 0.018311 | 0.059509 | 0.10529 | -0.34332 | 0.27466 | -0.5127 | -0.70496 | 0.013733 | -0.15106 | -0.059509 | 0.082397 | 0.018311 | -0.63171 | -0.64545 | -0.01831 | -0.21057 | -122.2092 | 0.55389 | 0.15106 | 0.36163 | -122.4655 | -0.13733 | -0.15106 | -122.4014 | 0.50812 | 0.43488 | 0.58594 | -122.4655 | 0.76904 | 0.5127 | 0.59967 | -123.1888 | 0.57678 | 0.5127 | 0.34332 | -123.1293
4496.0156 | 123.0698 | -0.50354 | 122.4792 | 0.11429 | 0.013858 | 0.0045908 | 0.017752 | 0.026105 | 0.0018457 | -0.0096409 | 0.12955 | -0.0033582 | 0.014917 | -0.011388 | 0.025143 | -0.0059922 | 0.082397 | 0.10071 | 0.10529 | -0.32959 | 0.2655 | -0.51727 | -0.69122 | 0.054932 | -0.16479 | -0.082397 | 0.059509 | 0.013733 | -0.62256 | -0.64087 | -0.013733 | -0.18768 | -122.2137 | 0.60425 | 0.17395 | 0.36163 | -122.3969 | -0.11902 | -0.13733 | -122.4197 | 0.55847 | 0.42114 | 0.55847 | -122.4655 | 0.76904 | 0.58594 | 0.60883 | -123.1705 | 0.56305 | 0.51727 | 0.33874 | -123.1201
4497.0156 | 123.0515 | -0.5127 | 122.493 | 0.0074768 | 0.011935 | 0.0039498 | 0.016684 | 0.026318 | -0.0011451 | -0.0094273 | -0.00015237 | -0.0054944 | 0.012567 | -0.0096793 | 0.023007 | -0.0036424 | 0.013733 | 0.045776 | 0.091553 | -0.33875 | 0.28381 | -0.52185 | -0.70953 | 0.022888 | -0.14648 | -0.064087 | 0.07782 | 0.022888 | -0.63171 | -0.65918 | -0.009156 | -0.19684 | -122.2092 | 0.55847 | 0.17395 | 0.37079 | -122.4792 | -0.11902 | -0.14648 | -122.4152 | 0.53558 | 0.44861 | 0.59509 | -122.4701 | 0.79651 | 0.52643 | 0.60425 | -123.2025 | 0.59052 | 0.53558 | 0.36621 | -123.1522
4498.0156 | 123.0881 | -0.48065 | 122.5067 | 0.29739 | 0.017703 | 0.0058724 | 0.014975 | 0.026318 | 0.0052637 | -0.010282 | 0.10666 | -0.003999 | 0.014063 | -0.013097 | 0.026639 | -0.0059922 | 0.09613 | 0.1236 | 0.14191 | -0.29755 | 0.27008 | -0.5127 | -0.67291 | 0.07782 | -0.11444 | -0.059509 | 0.064087 | 0.004578 | -0.60883 | -0.62714 | -0.032043 | -0.19226 | -122.2366 | 0.60425 | 0.18311 | 0.37537 | -122.4106 | -0.12817 | -0.14648 | -122.4426 | 0.55847 | 0.42114 | 0.56763 | -122.5021 | 0.75073 | 0.57678 | 0.62256 | -123.1796 | 0.54474 | 0.48523 | 0.36621 | -123.1338
4499.0156 | 123.0469 | -0.50354 | 122.4884 | -0.068817 | 0.012149 | 0.0062998 | 0.015189 | 0.025464 | -0.0028541 | -0.0079319 | 0.053253 | -0.007417 | 0.011926 | -0.0094657 | 0.02493 | -0.005565 | 0.022888 | 0.064087 | 0.091553 | -0.34332 | 0.27924 | -0.51727 | -0.71411 | 0.018311 | -0.13275 | -0.045776 | 0.07782 | 0.027466 | -0.6134 | -0.66376 | -0.013733 | -0.21057 | -122.2092 | 0.56763 | 0.16022 | 0.37079 | -122.4655 | -0.10986 | -0.16022 | -122.4106 | 0.52185 | 0.45776 | 0.61798 | -122.4609 | 0.78278 | 0.52643 | 0.59509 | -123.2025 | 0.58136 | 0.53101 | 0.37079 | -123.1522
4500.0156 | 123.0835 | -0.49896 | 122.4976 | 0.045624 | 0.010226 | 0.0045908 | 0.013907 | 0.025891 | 0.00077755 | -0.0070773 | 0.083771 | -0.0052808 | 0.013208 | -0.0092521 | 0.023007 | -0.0051376 | 0.022888 | 0.091553 | 0.10986 | -0.3479 | 0.27924 | -0.51727 | -0.6958 | 0.013733 | -0.15106 | -0.07782 | 0.10529 | 0.041199 | -0.62714 | -0.63629 | -0.018311 | -0.19684 | -122.2183 | 0.59052 | 0.15106 | 0.3479 | -122.4747 | -0.12817 | -0.13733 | -122.3923 | 0.5127 | 0.42114 | 0.55847 | -122.4564 | 0.7782 | 0.52185 | 0.60883 | -123.1934 | 0.60425 | 0.54016 | 0.3479 | -123.1339
4501.0156 | 123.111 | -0.50354 | 122.4792 | 0.030365 | 0.0080899 | 0.0043772 | 0.015616 | 0.029095 | -0.0024269 | -0.0098545 | -0.038299 | -0.0061352 | 0.013422 | -0.010534 | 0.022794 | -0.0053512 | 0.064087 | 0.10529 | 0.12817 | -0.3067 | 0.27466 | -0.52643 | -0.70953 | 0.059509 | -0.091553 | -0.013733 | 0.07782 | 0.013733 | -0.60883 | -0.63171 | -0.022888 | -0.20599 | -122.2046 | 0.60883 | 0.19684 | 0.40283 | -122.4152 | -0.10529 | -0.12817 | -122.4014 | 0.56305 | 0.48981 | 0.61798 | -122.4655 | 0.7782 | 0.56763 | 0.63171 | -123.1888 | 0.58136 | 0.51727 | 0.41199 | -123.111
4502.0156 | 123.0469 | -0.52643 | 122.5159 | 0.0074768 | 0.011722 | 0.0048044 | 0.013907 | 0.024823 | 0.00035035 | -0.0096409 | -0.00015237 | -0.0044264 | 0.013422 | -0.011815 | 0.024075 | -0.005565 | 0.027466 | 0.068665 | 0.073242 | -0.33417 | 0.26093 | -0.53101 | -0.68665 | 0.022888 | -0.16937 | -0.059509 | 0.086975 | 0.013733 | -0.63171 | -0.64087 | -0.004578 | -0.16022 | -122.2549 | 0.59509 | 0.19226 | 0.35248 | -122.4884 | -0.10529 | -0.11444 | -122.4289 | 0.54932 | 0.46692 | 0.58136 | -122.5021 | 0.78735 | 0.55389 | 0.59967 | -123.2025 | 0.6134 | 0.54016 | 0.35706 | -123.1567
4503.0156 | 123.111 | -0.49439 | 122.4884 | 0.045624 | 0.0080899 | 0.005018 | 0.017111 | 0.025677 | -0.0024269 | -0.010282 | -0.099335 | -0.0050672 | 0.015131 | -0.011175 | 0.023007 | -0.0036424 | 0.045776 | 0.11902 | 0.1236 | -0.31128 | 0.2655 | -0.52643 | -0.70038 | 0.068665 | -0.10986 | -0.022888 | 0.059509 | 0 | -0.60425 | -0.64545 | -0.032043 | -0.20599 | -122.2229 | 0.6134 | 0.18311 | 0.3891 | -122.4426 | -0.10986 | -0.15106 | -122.4289 | 0.56305 | 0.4715 | 0.62256 | -122.4884 | 0.75989 | 0.54016 | 0.61798 | -123.1888 | 0.55389 | 0.49439 | 0.38452 | -123.1339
4504.0156 | 123.0606 | -0.50354 | 122.4792 | 0.13718 | 0.013644 | 0.0056588 | 0.014975 | 0.026532 | 0.00056395 | -0.0094273 | -0.076446 | -0.00464 | 0.014704 | -0.011175 | 0.02493 | -0.0047104 | 0.059509 | 0.10529 | 0.11902 | -0.33417 | 0.25635 | -0.50354 | -0.70038 | 0.045776 | -0.16937 | -0.07782 | 0.082397 | 0.027466 | -0.61798 | -0.63629 | 0 | -0.19684 | -122.2229 | 0.60883 | 0.16937 | 0.36621 | -122.4197 | -0.11444 | -0.13275 | -122.3969 | 0.54932 | 0.42572 | 0.55847 | -122.4518 | 0.75989 | 0.56305 | 0.62256 | -123.1796 | 0.58594 | 0.53101 | 0.33417 | -123.1155
4505.0156 | 123.1018 | -0.49896 | 122.5113 | -0.015411 | 0.01044 | 0.0041634 | 0.016684 | 0.026318 | -0.0019995 | -0.0098545 | -0.061188 | -0.0042126 | 0.011713 | -0.0096793 | 0.023434 | -0.0059922 | 0.009155 | 0.09613 | 0.10071 | -0.32501 | 0.27466 | -0.54016 | -0.70038 | 0.036621 | -0.12817 | -0.041199 | 0.068665 | 0.004578 | -0.63171 | -0.65002 | -0.041199 | -0.20142 | -122.2366 | 0.59509 | 0.17395 | 0.37537 | -122.5021 | -0.13275 | -0.15106 | -122.4426 | 0.53558 | 0.45776 | 0.60883 | -122.5067 | 0.77362 | 0.50812 | 0.59967 | -123.2117 | 0.56763 | 0.50354 | 0.37079 | -123.1613
4506.0156 | 123.0515 | -0.50812 | 122.5204 | 0.0914 | 0.01044 | 0.003309 | 0.015189 | 0.026959 | -0.0011451 | -0.010709 | 0.022736 | -0.00464 | 0.013422 | -0.01032 | 0.023434 | -0.0053512 | 0.004578 | 0.068665 | 0.09613 | -0.32959 | 0.2655 | -0.5127 | -0.69122 | 0.013733 | -0.16479 | -0.073242 | 0.073242 | 0.013733 | -0.64087 | -0.66834 | -0.004577 | -0.18311 | -122.2549 | 0.57678 | 0.17853 | 0.36163 | -122.5159 | -0.13275 | -0.16022 | -122.4472 | 0.52185 | 0.43488 | 0.59509 | -122.5067 | 0.77362 | 0.5127 | 0.60425 | -123.2117 | 0.58136 | 0.52185 | 0.34332 | -123.1888
4507.0156 | 123.0148 | -0.55389 | 122.5296 | -0.045929 | 0.017276 | -0.0099356 | 0.02117 | 0.026746 | 0.0063317 | -0.0098545 | -0.00015237 | -0.0048536 | 0.017908 | -0.010961 | 0.02728 | -0.0089828 | 0.082397 | 0.032043 | 0.027466 | -0.35248 | 0.30212 | -0.54474 | -0.72784 | -0.004578 | -0.21515 | -0.16937 | 0.10986 | 0.041199 | -0.64087 | -0.68207 | 0.009155 | -0.17395 | -122.2275 | 0.58594 | 0.20142 | 0.37537 | -122.4472 | -0.086975 | -0.12817 | -122.4197 | 0.54932 | 0.38452 | 0.5127 | -122.4884 | 0.85602 | 0.63629 | 0.58136 | -123.2574 | 0.66376 | 0.59509 | 0.33874 | -123.2117
4508.0156 | 123.1567 | -0.48981 | 122.5113 | -0.19852 | 0.010867 | 0.0062998 | 0.015402 | 0.027173 | -0.0024269 | -0.0064365 | -0.11459 | -0.00464 | 0.013422 | -0.010747 | 0.022153 | -0.003856 | 0.027466 | 0.19226 | 0.12817 | -0.3067 | 0.27924 | -0.51727 | -0.70953 | 0.09613 | -0.07782 | 0.004578 | 0.041199 | -0.004578 | -0.61798 | -0.62714 | -0.027466 | -0.21973 | -122.2321 | 0.68207 | 0.18311 | 0.40283 | -122.4838 | -0.12817 | -0.13733 | -122.4701 | 0.58594 | 0.49439 | 0.63171 | -122.5159 | 0.76904 | 0.51727 | 0.61798 | -123.2208 | 0.53101 | 0.48523 | 0.41199 | -123.1384
4509.0156 | 123.1064 | -0.48065 | 122.525 | -0.15274 | 0.012576 | 0.0048044 | 0.016684 | 0.022259 | 0.00077755 | -0.0085727 | -0.18326 | -0.0052808 | 0.011072 | -0.011175 | 0.025357 | -0.0044968 | 0.068665 | 0.16479 | 0.11902 | -0.31128 | 0.28381 | -0.52185 | -0.70953 | 0.050354 | -0.07782 | -0.045776 | 0.064087 | -0.009155 | -0.6134 | -0.65002 | -0.041199 | -0.22888 | -122.2412 | 0.64545 | 0.16937 | 0.39826 | -122.4564 | -0.13275 | -0.16937 | -122.4609 | 0.53101 | 0.43488 | 0.60425 | -122.5342 | 0.76446 | 0.54932 | 0.59967 | -123.2346 | 0.54474 | 0.4715 | 0.40283 | -123.175
4510.0156 | 123.0881 | -0.5127 | 122.5113 | 0.068512 | 0.0070217 | 0.005018 | 0.016898 | 0.026318 | -0.0043495 | -0.0077183 | -0.30533 | -0.0054944 | 0.010858 | -0.012029 | 0.023862 | -0.0030014 | -0.004578 | 0.10529 | 0.10986 | -0.32044 | 0.27008 | -0.50812 | -0.70038 | 0.045776 | -0.10986 | -0.036621 | 0.064087 | 0.004578 | -0.6134 | -0.66834 | 0.004577 | -0.18768 | -122.2412 | 0.61798 | 0.19226 | 0.37994 | -122.5159 | -0.10071 | -0.15564 | -122.4472 | 0.55847 | 0.47607 | 0.63171 | -122.5067 | 0.78278 | 0.50812 | 0.62256 | -123.2117 | 0.57678 | 0.51727 | 0.40283 | -123.1796
4511.0156 | 123.1247 | -0.50354 | 122.5021 | -0.12985 | 0.0078763 | 0.0075814 | 0.017539 | 0.027386 | -0.0022131 | -0.0085727 | -0.14511 | -0.0027174 | 0.011713 | -0.012456 | 0.024289 | -0.0047104 | 0.018311 | 0.17395 | 0.15106 | -0.31128 | 0.26093 | -0.52185 | -0.68665 | 0.091553 | -0.082397 | -0.004578 | 0.054932 | -0.004578 | -0.62256 | -0.63629 | -0.018311 | -0.18311 | -122.2412 | 0.67749 | 0.19226 | 0.37537 | -122.4838 | -0.11902 | -0.13275 | -122.4472 | 0.59509 | 0.49896 | 0.63171 | -122.5067 | 0.76446 | 0.52185 | 0.6546 | -123.1888 | 0.55847 | 0.49896 | 0.42114 | -123.1384
4512.0156 | 123.0606 | -0.49896 | 122.5525 | -0.27481 | 0.013431 | 0.005018 | 0.019248 | 0.0276 | 0.00035035 | -0.0092137 | -0.099335 | -0.0052808 | 0.012354 | -0.012029 | 0.023648 | -0.0072738 | 0.018311 | 0.11444 | 0.09613 | -0.32044 | 0.27924 | -0.54016 | -0.70496 | -0.009155 | -0.13733 | -0.11902 | 0.09613 | 0.032043 | -0.62714 | -0.67291 | -0.041199 | -0.20599 | -122.2733 | 0.6134 | 0.17853 | 0.38452 | -122.5342 | -0.12817 | -0.17395 | -122.4564 | 0.48981 | 0.37994 | 0.55389 | -122.5204 | 0.7782 | 0.51727 | 0.59509 | -123.2574 | 0.59509 | 0.53101 | 0.36163 | -123.2254
4513.0156 | 122.9919 | -0.50812 | 122.5479 | -0.15274 | 0.011508 | 0.0058724 | 0.016898 | 0.026746 | -7.6852e-05 | -0.0089999 | -0.2214 | -0.0042126 | 0.013422 | -0.011175 | 0.024716 | -0.0047104 | 0.022888 | 0.091553 | 0.07782 | -0.32044 | 0.30212 | -0.53558 | -0.70953 | 0 | -0.15564 | -0.10986 | 0.10529 | 0.036621 | -0.64087 | -0.66834 | -0.027465 | -0.20142 | -122.2458 | 0.59967 | 0.18768 | 0.3891 | -122.525 | -0.13275 | -0.16022 | -122.4426 | 0.50812 | 0.39825 | 0.55847 | -122.5113 | 0.81024 | 0.53101 | 0.58594 | -123.2574 | 0.6134 | 0.54474 | 0.35248 | -123.2162
4514.0156 | 123.0972 | -0.50354 | 122.5204 | -0.068817 | 0.010226 | 0.006727 | 0.015189 | 0.025464 | -0.0026405 | -0.0098545 | -0.015411 | -0.00464 | 0.011286 | -0.013524 | 0.024716 | -0.0034286 | 0.041199 | 0.18768 | 0.13733 | -0.28839 | 0.26093 | -0.49439 | -0.68665 | 0.050354 | -0.082397 | -0.009155 | 0.073242 | 0.013733 | -0.59509 | -0.64087 | 0.009155 | -0.18311 | -122.2595 | 0.69122 | 0.21515 | 0.39825 | -122.4792 | -0.091553 | -0.13733 | -122.4472 | 0.55389 | 0.49438 | 0.63171 | -122.5067 | 0.76446 | 0.54474 | 0.64087 | -123.2071 | 0.57678 | 0.51727 | 0.42114 | -123.1613
4515.0156 | 123.0011 | -0.5127 | 122.5937 | -0.26718 | 0.01279 | 0.0037362 | 0.016898 | 0.025037 | 0.00077755 | -0.0092137 | -0.29007 | -0.0035718 | 0.014704 | -0.012243 | 0.024289 | -0.0077012 | 0.027466 | 0.082397 | 0.068665 | -0.31586 | 0.29755 | -0.52643 | -0.71411 | -0.022888 | -0.1831 | -0.12817 | 0.1236 | 0.041199 | -0.63629 | -0.65918 | -0.013733 | -0.20142 | -122.2961 | 0.59509 | 0.19684 | 0.39825 | -122.5662 | -0.1236 | -0.14648 | -122.4701 | 0.48981 | 0.38452 | 0.53101 | -122.5525 | 0.81024 | 0.54016 | 0.58136 | -123.3078 | 0.63629 | 0.55389 | 0.32959 | -123.2529
4516.0156 | 123.1338 | -0.47607 | 122.525 | -0.023041 | 0.0097989 | 0.0043772 | 0.016043 | 0.026532 | -0.00071785 | -0.0098545 | -0.2214 | -0.006349 | 0.010431 | -0.012029 | 0.025784 | -0.004924 | 0.050354 | 0.24719 | 0.15564 | -0.27924 | 0.27466 | -0.50354 | -0.69122 | 0.050354 | -0.064087 | -0.027466 | 0.07782 | 0.004578 | -0.59967 | -0.6546 | -0.027466 | -0.21515 | -122.2504 | 0.72327 | 0.19684 | 0.41199 | -122.4747 | -0.1236 | -0.17853 | -122.4472 | 0.52643 | 0.44861 | 0.62714 | -122.5204 | 0.75073 | 0.52643 | 0.63171 | -123.2162 | 0.55389 | 0.48065 | 0.41199 | -123.1796
4517.0156 | 122.9919 | -0.53101 | 122.5708 | -0.061188 | 0.020267 | 0.0022408 | 0.018607 | 0.02525 | 0.0073999 | -0.0085727 | 0.053253 | -0.0025038 | 0.016413 | -0.010747 | 0.027066 | -0.0068466 | -0.018311 | -0.013733 | -0.018311 | -0.38452 | 0.31586 | -0.54016 | -0.72784 | -0.064087 | -0.2655 | -0.20599 | 0.11902 | 0.036621 | -0.65002 | -0.67291 | -0.009155 | -0.19684 | -122.2549 | 0.51727 | 0.14648 | 0.34332 | -122.5891 | -0.11902 | -0.14191 | -122.4518 | 0.46692 | 0.32501 | 0.46692 | -122.5342 | 0.84686 | 0.5127 | 0.5127 | -123.2986 | 0.65002 | 0.56763 | 0.2655 | -123.2437
4518.0156 | 123.1247 | -0.49896 | 122.5296 | -0.49606 | 0.010653 | 0.0039498 | 0.015402 | 0.023968 | -0.0026405 | -0.0094273 | -0.061188 | -0.0048536 | 0.012781 | -0.0094657 | 0.020871 | -0.003856 | 0.027466 | 0.11444 | 0.13275 | -0.31128 | 0.27008 | -0.52185 | -0.70496 | 0.059509 | -0.091553 | -0.004578 | 0.086975 | 0.027466 | -0.60425 | -0.63171 | -0.022889 | -0.20599 | -122.2595 | 0.6134 | 0.18768 | 0.39368 | -122.5021 | -0.10529 | -0.13275 | -122.4426 | 0.55847 | 0.49438 | 0.62714 | -122.5021 | 0.76904 | 0.52643 | 0.63171 | -123.2346 | 0.58594 | 0.52643 | 0.40741 | -123.1613
4519.0156 | 123.0148 | -0.54016 | 122.5891 | -0.26718 | 0.014285 | 0.0041634 | 0.017966 | 0.025891 | -0.00029045 | -0.0092137 | -0.19852 | -0.0031446 | 0.015772 | -0.011388 | 0.02258 | -0.0053512 | 0.009155 | 0.082397 | 0.059509 | -0.33875 | 0.28381 | -0.52643 | -0.73242 | -0.036621 | -0.1831 | -0.13275 | 0.11444 | 0.027466 | -0.64087 | -0.6546 | 0.013733 | -0.19226 | -122.3053 | 0.62256 | 0.20142 | 0.39368 | -122.58 | -0.10071 | -0.11444 | -122.4747 | 0.50354 | 0.40741 | 0.52185 | -122.5616 | 0.82397 | 0.54932 | 0.59967 | -123.3215 | 0.6546 | 0.56763 | 0.35706 | -123.2437
4520.0156 | 123.1064 | -0.48981 | 122.5479 | -0.20615 | 0.012362 | 0.0030954 | 0.016257 | 0.026105 | -0.0017859 | -0.0085727 | -0.23666 | -0.0054944 | 0.012567 | -0.0081839 | 0.022366 | -0.0040696 | 0.050354 | 0.15564 | 0.13275 | -0.29297 | 0.27008 | -0.52185 | -0.67291 | 0.022888 | -0.082397 | -0.054932 | 0.09613 | 0.018311 | -0.60883 | -0.6546 | -0.032044 | -0.18311 | -122.2778 | 0.64545 | 0.19684 | 0.37994 | -122.4976 | -0.11902 | -0.1648 | -122.4518 | 0.5127 | 0.43488 | 0.59967 | -122.5296 | 0.75989 | 0.54016 | 0.62256 | -123.2208 | 0.58594 | 0.50812 | 0.40741 | -123.2025
4521.0156 | 122.9782 | -0.53558 | 122.5845 | -0.25192 | 0.014926 | 0.0052316 | 0.020102 | 0.027814 | -0.0013587 | -0.0083591 | -0.20615 | -0.0025038 | 0.016626 | -0.010534 | 0.023862 | -0.0074876 | -0.041199 | 0.022888 | -0.004578 | -0.37537 | 0.32501 | -0.56305 | -0.74616 | -0.059509 | -0.21973 | -0.16479 | 0.1236 | 0.054932 | -0.63629 | -0.66834 | -0.027466 | -0.21057 | -122.2595 | 0.55847 | 0.16022 | 0.37079 | -122.6257 | -0.10071 | -0.13275 | -122.4609 | 0.47607 | 0.37079 | 0.50354 | -122.5296 | 0.86059 | 0.49438 | 0.53101 | -123.3307 | 0.65918 | 0.59052 | 0.31586 | -123.2529
4522.0156 | 122.9965 | -0.54016 | 122.5754 | 0.12955 | 0.021762 | 0.0016 | 0.017966 | 0.0276 | 0.0067589 | -0.0072911 | 0.076141 | -0.00079476 | 0.017694 | -0.0090385 | 0.026212 | -0.0072738 | -0.050354 | -0.009155 | -0.022888 | -0.37994 | 0.31128 | -0.54016 | -0.72327 | -0.068665 | -0.27466 | -0.17395 | 0.12817 | 0.054932 | -0.63171 | -0.65918 | 0 | -0.18311 | -122.2641 | 0.53101 | 0.16022 | 0.34332 | -122.6257 | -0.091553 | -0.11902 | -122.4472 | 0.4715 | 0.36621 | 0.48523 | -122.5204 | 0.85144 | 0.48981 | 0.51727 | -123.2986 | 0.66834 | 0.59509 | 0.2655 | -123.2346
4523.0156 | 122.9965 | -0.53101 | 122.5845 | -0.33585 | 0.01279 | 0.0039498 | 0.019248 | 0.027173 | -0.00071785 | -0.0072911 | -0.2214 | -0.0061352 | 0.013635 | -0.0081839 | 0.023862 | -0.0034286 | -0.045776 | 0.018311 | -0.004578 | -0.36163 | 0.3067 | -0.54016 | -0.72784 | -0.073242 | -0.19684 | -0.15564 | 0.12817 | 0.050354 | -0.64545 | -0.66376 | -0.009155 | -0.19684 | -122.2778 | 0.54932 | 0.16937 | 0.36621 | -122.6303 | -0.11444 | -0.13275 | -122.4564 | 0.45776 | 0.37537 | 0.50812 | -122.5342 | 0.83771 | 0.48523 | 0.52643 | -123.3124 | 0.65918 | 0.58136 | 0.33417 | -123.2483
4524.0156 | 123.1155 | -0.49439 | 122.5479 | -0.17563 | 0.013431 | 0.0041634 | 0.013693 | 0.026959 | -0.0054175 | -0.0083591 | -0.20615 | -0.0048536 | 0.01214 | -0.010534 | 0.025571 | -0.003215 | 0.027466 | 0.16479 | 0.13275 | -0.30212 | 0.26093 | -0.5127 | -0.67749 | 0.013733 | -0.07782 | -0.050354 | 0.073242 | 0.022888 | -0.63171 | -0.63629 | -0.01831 | -0.18311 | -122.287 | 0.65918 | 0.19226 | 0.37537 | -122.5204 | -0.13733 | -0.14191 | -122.4747 | 0.50812 | 0.44403 | 0.58594 | -122.525 | 0.75531 | 0.52185 | 0.62714 | -123.2254 | 0.56763 | 0.51727 | 0.41657 | -123.1842
4525.0156 | 122.9828 | -0.54016 | 122.5891 | -0.076447 | 0.01578 | 0.0058724 | 0.017966 | 0.024182 | -0.00071785 | -0.0098545 | -0.35873 | -0.0027174 | 0.013208 | -0.011388 | 0.023434 | -0.005565 | -0.059509 | 0.018311 | -0.009155 | -0.34332 | 0.31128 | -0.54016 | -0.73242 | -0.082397 | -0.18768 | -0.16479 | 0.12817 | 0.054932 | -0.64545 | -0.66834 | 0 | -0.19226 | -122.2778 | 0.55847 | 0.19684 | 0.3891 | -122.6486 | -0.10529 | -0.12817 | -122.4609 | 0.45776 | 0.37537 | 0.50354 | -122.5342 | 0.85144 | 0.48065 | 0.53101 | -123.3215 | 0.66834 | 0.59509 | 0.35248 | -123.2574
4526.0156 | 123.1338 | -0.48981 | 122.5479 | -0.10696 | 0.010013 | 0.0048044 | 0.015189 | 0.026105 | -0.0037085 | -0.0098545 | 0.0074766 | -0.0054944 | 0.010431 | -0.012243 | 0.023221 | -0.0042832 | 0.041199 | 0.20599 | 0.15564 | -0.27924 | 0.27008 | -0.52185 | -0.6958 | 0.050354 | -0.064087 | -0.004578 | 0.073242 | 0.009155 | -0.59509 | -0.63629 | -0.032044 | -0.20599 | -122.2778 | 0.6958 | 0.21057 | 0.41657 | -122.5067 | -0.10529 | -0.14648 | -122.4747 | 0.54016 | 0.48523 | 0.63171 | -122.5388 | 0.75989 | 0.53101 | 0.64545 | -123.2437 | 0.56305 | 0.49896 | 0.42572 | -123.1842
4527.0156 | 123.1018 | -0.50354 | 122.5525 | -0.22141 | 0.01279 | 0.005018 | 0.01647 | 0.026532 | -0.0022131 | -0.010282 | 0.10666 | -0.0050672 | 0.013422 | -0.010106 | 0.023862 | -0.0034286 | -0.036621 | 0.086975 | 0.09613 | -0.32501 | 0.30212 | -0.50354 | -0.6958 | 0.004578 | -0.12817 | -0.022888 | 0.064087 | 0.018311 | -0.60425 | -0.62256 | 0 | -0.19226 | -122.2504 | 0.59052 | 0.17853 | 0.37079 | -122.5891 | -0.10071 | -0.11902 | -122.4884 | 0.50812 | 0.48065 | 0.59967 | -122.5342 | 0.80566 | 0.46692 | 0.59967 | -123.2483 | 0.56763 | 0.52185 | 0.37537 | -123.175
4528.0156 | 123.0423 | -0.53101 | 122.5708 | -0.26718 | 0.014071 | 0.0039498 | 0.016257 | 0.026105 | -0.00093145 | -0.0077183 | -0.29007 | -0.0061352 | 0.012567 | -0.0098929 | 0.025571 | -0.0036424 | 0.004578 | 0.086975 | 0.045776 | -0.31586 | 0.27924 | -0.53101 | -0.70953 | -0.041199 | -0.15564 | -0.11902 | 0.11444 | 0.041199 | -0.64545 | -0.66376 | 0 | -0.17853 | -122.2916 | 0.61798 | 0.21515 | 0.39368 | -122.5662 | -0.11444 | -0.13275 | -122.4564 | 0.48981 | 0.41199 | 0.54474 | -122.5296 | 0.81024 | 0.53558 | 0.57678 | -123.2803 | 0.64545 | 0.5722 | 0.37537 | -123.2346
4529.0156 | 123.0606 | -0.5127 | 122.5708 | -0.31296 | 0.016635 | 0.0016 | 0.017966 | 0.027814 | 0.0024865 | -0.0068637 | -0.34348 | -0.0035718 | 0.014917 | -0.0094657 | 0.027066 | -0.008342 | 0.022888 | 0.050354 | 0.009155 | -0.34332 | 0.29755 | -0.52643 | -0.70038 | -0.004578 | -0.16937 | -0.13275 | 0.1236 | 0.022888 | -0.62256 | -0.66834 | -0.013733 | -0.18768 | -122.2733 | 0.56305 | 0.16937 | 0.35705 | -122.5479 | -0.10986 | -0.15564 | -122.4472 | 0.50812 | 0.37994 | 0.53558 | -122.5479 | 0.81024 | 0.53558 | 0.52185 | -123.2712 | 0.63629 | 0.53558 | 0.34332 | -123.2391
4530.0156 | 123.0011 | -0.53101 | 122.6074 | -0.29007 | 0.01279 | 0.0048044 | 0.016257 | 0.028668 | -0.0015723 | -0.0089999 | -0.32822 | -0.0054944 | 0.015131 | -0.01032 | 0.022794 | -0.0044968 | -0.018311 | 0.10071 | 0.068665 | -0.31128 | 0.28839 | -0.53558 | -0.71869 | -0.054932 | -0.16022 | -0.12817 | 0.10529 | 0.050354 | -0.64545 | -0.6546 | -0.004577 | -0.18768 | -122.319 | 0.63171 | 0.21973 | 0.40741 | -122.6257 | -0.11444 | -0.1236 | -122.5021 | 0.47607 | 0.40283 | 0.52643 | -122.5571 | 0.8194 | 0.5127 | 0.59967 | -123.3261 | 0.63629 | 0.58136 | 0.37079 | -123.262
4531.0156 | 123.0469 | -0.50812 | 122.6074 | -0.19852 | 0.017489 | 0.0041634 | 0.017966 | 0.026318 | 0.0018457 | -0.0087863 | -0.2214 | -0.0035718 | 0.016626 | -0.011175 | 0.025143 | -0.0077012 | -0.041199 | 0.022888 | 0 | -0.34332 | 0.28839 | -0.53558 | -0.73242 | -0.068665 | -0.19684 | -0.15564 | 0.11444 | 0.045776 | -0.63629 | -0.65918 | -0.027465 | -0.2243 | -122.319 | 0.53101 | 0.16479 | 0.3891 | -122.6486 | -0.12817 | -0.15106 | -122.493 | 0.43945 | 0.35248 | 0.50354 | -122.5616 | 0.79651 | 0.46692 | 0.50812 | -123.3398 | 0.62256 | 0.55389 | 0.31128 | -123.2666
4532.0156 | 123.0698 | -0.48065 | 122.5754 | -0.15274 | 0.010013 | 0.005018 | 0.014334 | 0.026959 | -0.0037085 | -0.0098545 | 0.030365 | -0.0042126 | 0.013635 | -0.010747 | 0.023434 | -0.003856 | 0.009155 | 0.10529 | 0.13275 | -0.27466 | 0.27466 | -0.48523 | -0.69122 | 0.018311 | -0.054932 | -0.041199 | 0.07782 | 0.018311 | -0.60425 | -0.62714 | -0.004577 | -0.21057 | -122.3007 | 0.58594 | 0.20599 | 0.41657 | -122.5662 | -0.1236 | -0.14648 | -122.4976 | 0.49896 | 0.43945 | 0.58594 | -122.5571 | 0.75531 | 0.48981 | 0.6134 | -123.2666 | 0.55847 | 0.49896 | 0.42572 | -123.2025
4533.0156 | 123.0515 | -0.53101 | 122.6028 | -0.31296 | 0.015994 | 0.0045908 | 0.017325 | 0.026105 | 0.0018457 | -0.010922 | -0.31296 | -0.0037854 | 0.016199 | -0.010961 | 0.024503 | -0.0036424 | -0.059509 | 0.004578 | 0.004578 | -0.36163 | 0.32044 | -0.55847 | -0.72784 | -0.073242 | -0.21515 | -0.15564 | 0.12817 | 0.054932 | -0.64545 | -0.66376 | -0.027466 | -0.19684 | -122.2824 | 0.53558 | 0.16937 | 0.36621 | -122.6624 | -0.11444 | -0.13275 | -122.4747 | 0.45776 | 0.37537 | 0.50812 | -122.5479 | 0.85144 | 0.4715 | 0.53558 | -123.3307 | 0.65918 | 0.58594 | 0.31586 | -123.2666
4534.0156 | 123.024 | -0.52185 | 122.6074 | -0.20615 | 0.013644 | 0.0048044 | 0.016898 | 0.025464 | 0.00056395 | -0.0083591 | -0.22903 | -0.0025038 | 0.011499 | -0.011815 | 0.022153 | -0.0051376 | -0.07782 | 0.032043 | 0.022888 | -0.37079 | 0.31586 | -0.53558 | -0.73242 | -0.064087 | -0.20142 | -0.15106 | 0.12817 | 0.041199 | -0.64087 | -0.65002 | -0.013732 | -0.21057 | -122.2916 | 0.55389 | 0.15106 | 0.36163 | -122.6852 | -0.11902 | -0.12817 | -122.4792 | 0.45776 | 0.37079 | 0.49896 | -122.5662 | 0.83771 | 0.44403 | 0.54474 | -123.3398 | 0.65002 | 0.56305 | 0.32043 | -123.2574
4535.0156 | 123.056 | -0.52185 | 122.6074 | -0.168 | 0.01813 | 0.0030954 | 0.017539 | 0.027173 | 0.0031273 | -0.0077183 | 0.037995 | -0.0027174 | 0.015344 | -0.0094657 | 0.026639 | -0.0064194 | -0.004578 | 0.054932 | 0.032043 | -0.32044 | 0.32044 | -0.52643 | -0.71411 | -0.022888 | -0.15564 | -0.11444 | 0.13733 | 0.045776 | -0.62714 | -0.64545 | -0.004577 | -0.19226 | -122.287 | 0.57678 | 0.20142 | 0.39368 | -122.612 | -0.10529 | -0.1236 | -122.4701 | 0.49896 | 0.40741 | 0.53101 | -122.5616 | 0.84229 | 0.51727 | 0.55389 | -123.3215 | 0.65918 | 0.56763 | 0.36621 | -123.2529
4536.0156 | 123.0331 | -0.53101 | 122.5983 | -0.29007 | 0.014499 | 0.0052316 | 0.013266 | 0.027173 | -0.00029045 | -0.0079319 | -0.25192 | -0.0025038 | 0.014917 | -0.0086111 | 0.024716 | -0.0042832 | -0.073242 | 0.027466 | 0.022888 | -0.37079 | 0.31586 | -0.55389 | -0.70953 | -0.073242 | -0.21515 | -0.13733 | 0.11902 | 0.064087 | -0.64087 | -0.66376 | -0.022888 | -0.17853 | -122.2824 | 0.55847 | 0.16022 | 0.33875 | -122.6715 | -0.10986 | -0.13275 | -122.4792 | 0.45776 | 0.39368 | 0.52643 | -122.5342 | 0.84686 | 0.45776 | 0.55389 | -123.3078 | 0.65002 | 0.59509 | 0.31586 | -123.262
4537.0156 | 123.0515 | -0.52643 | 122.5983 | -0.29007 | 0.019198 | 0.0020272 | 0.018607 | 0.026105 | 0.00077755 | -0.0081455 | -0.29007 | -0.0044264 | 0.017694 | -0.0086111 | 0.024289 | -0.0079148 | -0.018311 | 0.064087 | 0.022888 | -0.32044 | 0.28839 | -0.53101 | -0.72784 | -0.036621 | -0.17853 | -0.1236 | 0.13275 | 0.050354 | -0.62714 | -0.65002 | -0.004578 | -0.20142 | -122.3099 | 0.59052 | 0.20599 | 0.40741 | -122.6166 | -0.10071 | -0.1236 | -122.4655 | 0.48981 | 0.40283 | 0.52643 | -122.5479 | 0.81482 | 0.50812 | 0.54932 | -123.3261 | 0.65918 | 0.57678 | 0.3479 | -123.2483
4538.0156 | 123.0286 | -0.50354 | 122.5891 | -0.18326 | 0.019626 | 0.003309 | 0.018179 | 0.025464 | 0.0027001 | -0.0096409 | -0.12985 | -0.002931 | 0.014917 | -0.011175 | 0.025784 | -0.0074876 | -0.004578 | 0.045776 | 0.032043 | -0.31128 | 0.29297 | -0.55847 | -0.70038 | -0.036621 | -0.16022 | -0.1236 | 0.10529 | 0.041199 | -0.64087 | -0.6546 | -0.054932 | -0.19684 | -122.2961 | 0.54932 | 0.19226 | 0.3891 | -122.5937 | -0.13733 | -0.15106 | -122.4838 | 0.46692 | 0.37994 | 0.53101 | -122.5479 | 0.79651 | 0.49896 | 0.53558 | -123.2895 | 0.60883 | 0.54474 | 0.34332 | -123.2437
4539.0156 | 123.0423 | -0.51727 | 122.612 | -0.14511 | 0.018558 | 0.0073678 | 0.019034 | 0.029095 | -0.00071785 | -0.0081455 | -0.038299 | -0.00229 | 0.01449 | -0.0079703 | 0.022794 | -0.0040696 | -0.064087 | 0 | -0.004578 | -0.35706 | 0.30212 | -0.52643 | -0.71411 | -0.07782 | -0.21057 | -0.14648 | 0.12817 | 0.068665 | -0.64087 | -0.6546 | -0.009155 | -0.19684 | -122.3099 | 0.51727 | 0.16022 | 0.35706 | -122.6761 | -0.1236 | -0.13733 | -122.4838 | 0.43945 | 0.37079 | 0.50812 | -122.5433 | 0.8194 | 0.45319 | 0.5127 | -123.3261 | 0.64545 | 0.58594 | 0.3067 | -123.2666
4540.0156 | 123.0652 | -0.53558 | 122.6166 | -0.3511 | 0.014285 | 0.0039498 | 0.015402 | 0.024396 | -0.0013587 | -0.010068 | -0.45029 | -0.0044264 | 0.01449 | -0.011815 | 0.023434 | -0.0040696 | -0.07782 | 0.027466 | 0 | -0.35248 | 0.30212 | -0.52643 | -0.70496 | -0.086975 | -0.20599 | -0.15564 | 0.11902 | 0.054932 | -0.65918 | -0.66376 | 0.009155 | -0.16937 | -122.3145 | 0.56305 | 0.18311 | 0.35248 | -122.6944 | -0.1236 | -0.12817 | -122.4976 | 0.44861 | 0.37994 | 0.50812 | -122.5616 | 0.83771 | 0.45776 | 0.53558 | -123.3215 | 0.6546 | 0.59052 | 0.32959 | -123.2803
4541.0156 | 123.0698 | -0.50812 | 122.6074 | -0.12985 | 0.019412 | 0.005018 | 0.018607 | 0.02525 | 0.0033411 | -0.0077183 | -0.099335 | -0.00464 | 0.017267 | -0.012029 | 0.026212 | -0.005565 | 0.009155 | 0.064087 | 0.022888 | -0.31128 | 0.30212 | -0.53101 | -0.70953 | -0.022888 | -0.17395 | -0.13275 | 0.10986 | 0.041199 | -0.62256 | -0.6546 | -0.022888 | -0.20142 | -122.3053 | 0.5722 | 0.19684 | 0.39826 | -122.5983 | -0.11444 | -0.14648 | -122.4976 | 0.48523 | 0.37537 | 0.52185 | -122.5662 | 0.81024 | 0.51727 | 0.53101 | -123.317 | 0.61798 | 0.54932 | 0.33417 | -123.262
4542.0156 | 123.0423 | -0.48981 | 122.6212 | -0.26718 | 0.01279 | 0.0056588 | 0.019034 | 0.025677 | -0.0015723 | -0.0079319 | -0.168 | -0.003999 | 0.015131 | -0.011602 | 0.02258 | -0.0057786 | -0.064087 | 0 | -0.004578 | -0.34332 | 0.29755 | -0.53101 | -0.71869 | -0.082397 | -0.19226 | -0.13275 | 0.1236 | 0.059509 | -0.64087 | -0.67291 | -0.041199 | -0.22888 | -122.3236 | 0.48981 | 0.14648 | 0.37537 | -122.6852 | -0.15106 | -0.18311 | -122.4976 | 0.40741 | 0.35706 | 0.54016 | -122.5616 | 0.78735 | 0.42572 | 0.48523 | -123.3398 | 0.6134 | 0.54932 | 0.29755 | -123.2941
4543.0156 | 122.9919 | -0.53558 | 122.6257 | 0.099029 | 0.020267 | 0.0052316 | 0.017752 | 0.026318 | 0.0024865 | -0.0081455 | 0.12192 | -0.0016492 | 0.015558 | -0.010961 | 0.026425 | -0.0051376 | -0.032043 | -0.022888 | -0.018311 | -0.36621 | 0.28839 | -0.53558 | -0.71869 | -0.07782 | -0.24261 | -0.20142 | 0.10529 | 0.050354 | -0.64087 | -0.68207 | 0 | -0.18311 | -122.3373 | 0.5127 | 0.16937 | 0.35248 | -122.6578 | -0.10529 | -0.14648 | -122.5204 | 0.45776 | 0.33417 | 0.48065 | -122.5754 | 0.82397 | 0.50354 | 0.51727 | -123.3444 | 0.64087 | 0.58594 | 0.29297 | -123.3078
4544.0156 | 123.0606 | -0.50812 | 122.5891 | -0.17563 | 0.022403 | 0.0045908 | 0.019248 | 0.027173 | 0.00056395 | -0.0092137 | -0.091705 | -0.00036736 | 0.015772 | -0.0098929 | 0.025571 | -0.005565 | 0.018311 | 0.045776 | 0.004578 | -0.33417 | 0.3067 | -0.52185 | -0.71869 | -0.032043 | -0.16937 | -0.16022 | 0.086975 | 0.036621 | -0.63629 | -0.65002 | -0.013733 | -0.21057 | -122.2824 | 0.55389 | 0.17395 | 0.38452 | -122.5708 | -0.12817 | -0.14191 | -122.5021 | 0.47607 | 0.3479 | 0.48981 | -122.5525 | 0.81482 | 0.52643 | 0.5127 | -123.3078 | 0.59509 | 0.54474 | 0.33874 | -123.2391
4545.0156 | 123.0789 | -0.51727 | 122.5754 | -0.17563 | 0.018985 | 0.0018136 | 0.020316 | 0.025464 | 0.00013675 | -0.0098545 | -0.038299 | -0.0031446 | 0.014063 | -0.010747 | 0.025571 | -0.0051376 | 0 | 0.041199 | 0.050354 | -0.34332 | 0.29755 | -0.55389 | -0.73242 | -0.022888 | -0.18768 | -0.14648 | 0.10529 | 0.036621 | -0.62714 | -0.66376 | -0.036621 | -0.21515 | -122.2778 | 0.55847 | 0.17395 | 0.3891 | -122.5754 | -0.10986 | -0.14648 | -122.4701 | 0.49438 | 0.37079 | 0.51727 | -122.5388 | 0.81482 | 0.51727 | 0.56763 | -123.3078 | 0.62256 | 0.55389 | 0.32959 | -123.2391
4546.0156 | 123.0377 | -0.52643 | 122.6074 | -0.18326 | 0.013217 | 0.0054452 | 0.016684 | 0.026318 | -0.0054175 | -0.0081455 | -0.084076 | -0.0027174 | 0.013635 | -0.010534 | 0.020871 | -0.0017196 | -0.068665 | 0.032043 | 0 | -0.36163 | 0.28839 | -0.54474 | -0.72327 | -0.091553 | -0.23346 | -0.14191 | 0.11444 | 0.050354 | -0.6546 | -0.65918 | -0.018311 | -0.19684 | -122.319 | 0.55847 | 0.1648 | 0.36163 | -122.6761 | -0.12817 | -0.13275 | -122.493 | 0.43488 | 0.38452 | 0.51727 | -122.5571 | 0.81482 | 0.45776 | 0.52643 | -123.3307 | 0.64087 | 0.57678 | 0.29297 | -123.2666
4547.0156 | 123.0698 | -0.51727 | 122.5754 | -0.20615 | 0.021976 | 0.0018136 | 0.017752 | 0.029309 | 0.00077755 | -0.0083591 | -0.10696 | -0.00058096 | 0.016199 | -0.0094657 | 0.026852 | -0.0051376 | 0 | 0.045776 | 0.032043 | -0.32959 | 0.32044 | -0.52643 | -0.70038 | -0.022888 | -0.18768 | -0.14648 | 0.10071 | 0.041199 | -0.61798 | -0.63629 | -0.009155 | -0.1831 | -122.2549 | 0.56305 | 0.18768 | 0.37079 | -122.5754 | -0.10071 | -0.11902 | -122.4747 | 0.49438 | 0.37079 | 0.48981 | -122.5342 | 0.83771 | 0.51727 | 0.54932 | -123.2758 | 0.61798 | 0.55847 | 0.32959 | -123.2117
4548.0156 | 123.0423 | -0.52185 | 122.5891 | 0.11429 | 0.019626 | 0.0024544 | 0.015189 | 0.028882 | 0.0033411 | -0.0079319 | 0.09903 | -0.0033582 | 0.017267 | -0.0090385 | 0.023862 | -0.004924 | -0.050354 | -0.013733 | -0.004578 | -0.37079 | 0.3067 | -0.56763 | -0.70953 | -0.050354 | -0.23804 | -0.13275 | 0.086975 | 0.032043 | -0.62714 | -0.6546 | -0.045776 | -0.18768 | -122.2824 | 0.50812 | 0.15106 | 0.33875 | -122.6395 | -0.10529 | -0.13275 | -122.5021 | 0.4715 | 0.3891 | 0.52185 | -122.5571 | 0.82855 | 0.4715 | 0.51727 | -123.2986 | 0.60883 | 0.55389 | 0.28381 | -123.2437
4549.0156 | 123.0652 | -0.50812 | 122.612 | -0.12985 | 0.020694 | 0.005018 | 0.018393 | 0.023968 | 0.0031273 | -0.0047275 | 0.0074766 | -0.0027174 | 0.014276 | -0.010534 | 0.026425 | -0.0057786 | 0.022888 | 0.032043 | 0.013733 | -0.34332 | 0.30212 | -0.5127 | -0.69122 | -0.022888 | -0.18768 | -0.15106 | 0.10986 | 0.07782 | -0.62714 | -0.65002 | -0.004577 | -0.18311 | -122.3099 | 0.54016 | 0.16479 | 0.3479 | -122.5891 | -0.11902 | -0.14191 | -122.5021 | 0.48523 | 0.35706 | 0.49896 | -122.5342 | 0.81024 | 0.53101 | 0.52185 | -123.3032 | 0.61798 | 0.58594 | 0.32043 | -123.262
4550.0156 | 123.0698 | -0.52185 | 122.612 | -0.12985 | 0.018344 | 0.006086 | 0.015616 | 0.026746 | -0.00050425 | -0.0081455 | -0.19089 | -0.0020764 | 0.01449 | -0.0094657 | 0.023648 | -0.0062058 | -0.032043 | 0.004578 | -0.022888 | -0.32501 | 0.31128 | -0.53101 | -0.73242 | -0.064087 | -0.17853 | -0.14191 | 0.10071 | 0.059509 | -0.63629 | -0.65918 | -0.009155 | -0.21057 | -122.3007 | 0.52643 | 0.19684 | 0.40741 | -122.644 | -0.11444 | -0.13733 | -122.5113 | 0.45776 | 0.37994 | 0.51727 | -122.5525 | 0.83313 | 0.48981 | 0.49896 | -123.3444 | 0.62256 | 0.58136 | 0.34332 | -123.2712
4551.0156 | 123.0789 | -0.51727 | 122.5983 | 0.076141 | 0.019839 | 0.0048044 | 0.019034 | 0.026746 | 0.0022729 | -0.0089999 | -0.25192 | -0.0031446 | 0.016413 | -0.0086111 | 0.02493 | -0.0064194 | -0.009155 | 0.045776 | 0.027466 | -0.34332 | 0.30212 | -0.54474 | -0.70038 | -0.027466 | -0.19226 | -0.15564 | 0.11444 | 0.059509 | -0.64545 | -0.65918 | -0.027466 | -0.1831 | -122.2961 | 0.56305 | 0.17395 | 0.35705 | -122.6074 | -0.12817 | -0.14191 | -122.4838 | 0.48981 | 0.36163 | 0.50354 | -122.5388 | 0.8194 | 0.50812 | 0.54474 | -123.2986 | 0.63171 | 0.57678 | 0.32501 | -123.2574
4552.0156 | 123.0606 | -0.55389 | 122.612 | -0.091705 | 0.014285 | 0.0039498 | 0.017111 | 0.02525 | -0.0039221 | -0.0098545 | -0.23666 | -0.0035718 | 0.018335 | -0.010106 | 0.022153 | -0.0044968 | -0.059509 | -0.004578 | -0.018311 | -0.35706 | 0.32044 | -0.53558 | -0.72327 | -0.086975 | -0.21515 | -0.15106 | 0.12817 | 0.059509 | -0.64545 | -0.65002 | 0.018311 | -0.16937 | -122.2916 | 0.54932 | 0.19684 | 0.36621 | -122.6715 | -0.091553 | -0.09613 | -122.4838 | 0.46692 | 0.40283 | 0.49896 | -122.5525 | 0.87433 | 0.49439 | 0.53558 | -123.3353 | 0.68207 | 0.6134 | 0.33874 | -123.262
4553.0156 | 123.1155 | -0.49439 | 122.6028 | -0.17563 | 0.01044 | 0.006727 | 0.016043 | 0.022687 | -0.0056311 | -0.010709 | 0.076141 | -0.003999 | 0.011926 | -0.010961 | 0.02258 | -0.0027878 | -0.059509 | 0.064087 | 0.082397 | -0.30212 | 0.27008 | -0.50812 | -0.68665 | -0.022888 | -0.13733 | -0.018311 | 0.086975 | 0.041199 | -0.59509 | -0.63171 | -0.013733 | -0.19226 | -122.3328 | 0.55847 | 0.19226 | 0.38452 | -122.6624 | -0.10071 | -0.13733 | -122.5159 | 0.4715 | 0.47607 | 0.6134 | -122.5616 | 0.76447 | 0.43488 | 0.57678 | -123.2895 | 0.58136 | 0.53558 | 0.35706 | -123.2346
4554.0156 | 123.056 | -0.51727 | 122.6212 | -0.45792 | 0.016421 | 0.0035226 | 0.016898 | 0.0276 | 0.00056395 | -0.0092137 | -0.26718 | -0.0050672 | 0.014276 | -0.012456 | 0.025998 | -0.0036424 | -0.041199 | -0.022888 | -0.013733 | -0.33875 | 0.3067 | -0.54016 | -0.71411 | -0.086975 | -0.19684 | -0.14191 | 0.11444 | 0.050354 | -0.63629 | -0.6546 | -0.022888 | -0.19684 | -122.3145 | 0.49438 | 0.17853 | 0.37537 | -122.6624 | -0.11902 | -0.13733 | -122.5067 | 0.4303 | 0.37537 | 0.5127 | -122.5708 | 0.82397 | 0.47607 | 0.50354 | -123.3353 | 0.63171 | 0.56763 | 0.32043 | -123.2758
4555.0156 | 123.0286 | -0.51727 | 122.6166 | -0.023041 | 0.020694 | 0.0028818 | 0.019461 | 0.025037 | 0.0041955 | -0.0087863 | -0.00015237 | -0.0031446 | 0.017053 | -0.012243 | 0.028348 | -0.0070602 | 0.004578 | 0.022888 | -0.004578 | -0.32959 | 0.29755 | -0.54016 | -0.71411 | -0.054932 | -0.2243 | -0.17853 | 0.10986 | 0.064087 | -0.63629 | -0.66834 | -0.022888 | -0.19684 | -122.319 | 0.54016 | 0.18768 | 0.38452 | -122.612 | -0.11902 | -0.15106 | -122.5067 | 0.46234 | 0.33874 | 0.48981 | -122.5525 | 0.81482 | 0.52185 | 0.5127 | -123.3307 | 0.62714 | 0.58136 | 0.29297 | -123.2849
4556.0156 | 123.0789 | -0.50812 | 122.6212 | -0.13748 | 0.019626 | 0.0028818 | 0.016684 | 0.0276 | 0.0018457 | -0.0096409 | -0.19089 | -0.00079476 | 0.015344 | -0.010961 | 0.023648 | -0.004924 | -0.004578 | 0.045776 | -0.004578 | -0.3067 | 0.28381 | -0.53558 | -0.737 | -0.022888 | -0.17853 | -0.13733 | 0.10986 | 0.045776 | -0.61798 | -0.64087 | -0.027465 | -0.22888 | -122.3373 | 0.55389 | 0.20142 | 0.4303 | -122.6257 | -0.10986 | -0.13275 | -122.5113 | 0.48523 | 0.37079 | 0.50354 | -122.5754 | 0.79193 | 0.50354 | 0.50354 | -123.3582 | 0.61798 | 0.55389 | 0.32959 | -123.262
4557.0156 | 123.0789 | -0.51727 | 122.6212 | 0.068512 | 0.020694 | 0.0037362 | 0.014975 | 0.025037 | 0.0029137 | -0.0070773 | -0.053558 | -0.0020764 | 0.015344 | -0.010534 | 0.026639 | -0.0042832 | 0.022888 | 0.004578 | -0.009155 | -0.33875 | 0.29755 | -0.51727 | -0.72327 | -0.045776 | -0.21973 | -0.16479 | 0.10529 | 0.054932 | -0.63171 | -0.66376 | 0 | -0.20599 | -122.3236 | 0.52185 | 0.17853 | 0.38452 | -122.5983 | -0.11444 | -0.14648 | -122.5159 | 0.4715 | 0.35248 | 0.49896 | -122.5662 | 0.81482 | 0.54016 | 0.50812 | -123.3444 | 0.62256 | 0.5722 | 0.29755 | -123.2849
4558.0312 | 123.143 | -0.49439 | 122.5937 | 0.015106 | 0.011081 | -0.035784 | 0.011557 | 0.026746 | -0.0056311 | -0.010709 | 0.0914 | -0.0042126 | 0.010858 | -0.010534 | 0.022153 | -0.001506 | -0.050354 | 0.073242 | 0.07782 | -0.31128 | 0.27008 | -0.49439 | -0.69122 | -0.009155 | -0.12817 | -0.018311 | 0.068665 | 0.050354 | -0.60883 | -0.63171 | 0 | -0.19684 | -122.3236 | 0.56763 | 0.18311 | 0.37994 | -122.644 | -0.11444 | -0.13733 | -122.525 | 0.48523 | 0.47607 | 0.6134 | -122.5433 | 0.76447 | 0.44403 | 0.57221 | -123.2849 | 0.56305 | 0.54474 | 0.36621 | -123.2254
4559.0156 | 123.0789 | -0.52643 | 122.6212 | -0.13748 | 0.019626 | 0.0054452 | 0.019461 | 0.027386 | 0.0029137 | -0.0079319 | -0.168 | -0.0050672 | 0.016199 | -0.012456 | 0.025571 | -0.0059922 | 0.022888 | 0.027466 | 0.009155 | -0.32044 | 0.3067 | -0.51727 | -0.71869 | -0.032043 | -0.17395 | -0.12817 | 0.11444 | 0.041199 | -0.62714 | -0.65918 | 0.009155 | -0.19226 | -122.3145 | 0.55389 | 0.20599 | 0.39825 | -122.5983 | -0.10071 | -0.13275 | -122.5067 | 0.49439 | 0.39825 | 0.53101 | -122.58 | 0.83313 | 0.54932 | 0.53558 | -123.3398 | 0.64087 | 0.56763 | 0.35248 | -123.2803
4560.0156 | 123.0881 | -0.53101 | 122.6486 | -0.22141 | 0.015994 | 0.0062998 | 0.017325 | 0.026959 | -0.00093145 | -0.010068 | -0.053558 | -0.0044264 | 0.01684 | -0.0090385 | 0.024716 | -0.0051376 | -0.073242 | -0.027466 | -0.009155 | -0.35248 | 0.32044 | -0.52185 | -0.737 | -0.073242 | -0.21057 | -0.15106 | 0.1236 | 0.059509 | -0.62714 | -0.65002 | 0.009155 | -0.20599 | -122.3282 | 0.50354 | 0.17853 | 0.38452 | -122.7219 | -0.09613 | -0.11902 | -122.525 | 0.45776 | 0.37994 | 0.49896 | -122.5891 | 0.85144 | 0.45776 | 0.52185 | -123.3856 | 0.6546 | 0.59052 | 0.32043 | -123.2986
4561.0156 | 123.0515 | -0.51727 | 122.6212 | 0.083771 | 0.022616 | 0.0041634 | 0.019888 | 0.026532 | 0.0029137 | -0.0083591 | 0.015106 | -0.002931 | 0.01684 | -0.011388 | 0.028348 | -0.006633 | -0.041199 | -0.009155 | -0.009155 | -0.3479 | 0.30212 | -0.54016 | -0.72327 | -0.082397 | -0.2655 | -0.19226 | 0.1236 | 0.064087 | -0.63629 | -0.6546 | -0.022888 | -0.20599 | -122.319 | 0.50812 | 0.16937 | 0.37537 | -122.6624 | -0.11902 | -0.13733 | -122.4976 | 0.43488 | 0.32501 | 0.46234 | -122.5571 | 0.8194 | 0.47607 | 0.50812 | -123.3444 | 0.64087 | 0.58136 | 0.25177 | -123.2758
4562.0156 | 123.0743 | -0.5127 | 122.6395 | -0.10696 | 0.020267 | 0.003309 | 0.017325 | 0.0229 | 0.0012047 | -0.0072911 | -0.10696 | -0.002931 | 0.016626 | -0.0096793 | 0.024716 | -0.004924 | 0.013733 | 0.036621 | 0.022888 | -0.3067 | 0.28839 | -0.52185 | -0.70038 | -0.036621 | -0.1831 | -0.15564 | 0.09613 | 0.059509 | -0.65002 | -0.64087 | -0.009156 | -0.18768 | -122.3511 | 0.54932 | 0.20599 | 0.39368 | -122.6257 | -0.13733 | -0.12817 | -122.5433 | 0.47607 | 0.35706 | 0.48523 | -122.58 | 0.80109 | 0.52643 | 0.53558 | -123.3398 | 0.60882 | 0.5722 | 0.32959 | -123.2803
4563.0312 | 123.0652 | -0.54474 | 122.6212 | -0.18326 | 0.014499 | 0.0069406 | 0.019248 | 0.026959 | -0.00050425 | -0.010068 | -0.22903 | -0.0052808 | 0.015131 | -0.0088247 | 0.022366 | -0.0057786 | -0.050354 | -0.013733 | -0.022888 | -0.32501 | 0.29297 | -0.54474 | -0.74616 | -0.086975 | -0.21973 | -0.14191 | 0.11902 | 0.064087 | -0.65002 | -0.66834 | 0 | -0.20142 | -122.3282 | 0.53101 | 0.21973 | 0.42114 | -122.6715 | -0.10529 | -0.1236 | -122.5021 | 0.45776 | 0.40283 | 0.52643 | -122.5571 | 0.83771 | 0.49438 | 0.52185 | -123.3673 | 0.66376 | 0.60883 | 0.32501 | -123.2895
4564.0156 | 123.1018 | -0.50812 | 122.6532 | -0.25192 | 0.017276 | 0.0013864 | 0.018179 | 0.026318 | 0.00099115 | -0.0077183 | -0.12222 | -0.0014356 | 0.018762 | -0.011602 | 0.028775 | -0.0044968 | 0.009155 | 0.036621 | 0.009155 | -0.30212 | 0.31128 | -0.54016 | -0.68665 | -0.036621 | -0.1831 | -0.12817 | 0.10071 | 0.045776 | -0.63171 | -0.6546 | -0.032043 | -0.17853 | -122.3419 | 0.54474 | 0.20599 | 0.38452 | -122.644 | -0.1236 | -0.14648 | -122.5525 | 0.4715 | 0.37994 | 0.52643 | -122.6074 | 0.8194 | 0.51727 | 0.51727 | -123.3398 | 0.60883 | 0.55389 | 0.32501 | -123.3078
4565.0156 | 123.0286 | -0.52643 | 122.6257 | 0.19058 | 0.018985 | 0.0022408 | 0.01882 | 0.022687 | 0.0020593 | -0.0068637 | 0.0914 | -0.002931 | 0.015558 | -0.0083975 | 0.026639 | -0.0051376 | -0.073242 | -0.068665 | -0.054932 | -0.3891 | 0.31128 | -0.53101 | -0.72784 | -0.09613 | -0.27008 | -0.17853 | 0.10071 | 0.059509 | -0.64087 | -0.65002 | -0.004578 | -0.20142 | -122.3145 | 0.45776 | 0.13733 | 0.33875 | -122.699 | -0.11444 | -0.1236 | -122.525 | 0.4303 | 0.3479 | 0.4715 | -122.5662 | 0.83771 | 0.45319 | 0.4715 | -123.3536 | 0.62714 | 0.58594 | 0.25635 | -123.2758
4566.0156 | 123.1201 | -0.5127 | 122.6303 | -0.045929 | 0.020694 | 0.0020272 | 0.01882 | 0.02525 | 0.0014185 | -0.0060093 | -0.099335 | -0.00229 | 0.018122 | -0.01032 | 0.027493 | -0.0053512 | 0.022888 | 0.022888 | 0.013733 | -0.31586 | 0.29297 | -0.51727 | -0.70038 | -0.032043 | -0.20599 | -0.15106 | 0.10986 | 0.050354 | -0.63171 | -0.66376 | -0.004578 | -0.18768 | -122.3373 | 0.53558 | 0.19684 | 0.38452 | -122.6074 | -0.11902 | -0.15106 | -122.5204 | 0.48065 | 0.36163 | 0.5127 | -122.58 | 0.80566 | 0.53558 | 0.52643 | -123.3307 | 0.62256 | 0.56305 | 0.3067 | -123.2941
4567.0156 | 123.1476 | -0.48523 | 122.6074 | 0.14481 | 0.014712 | 0.0054452 | 0.013907 | 0.028241 | -0.0011451 | -0.0092137 | 0.26688 | -0.0027174 | 0.015131 | -0.0096793 | 0.025998 | -0.0034286 | -0.018311 | 0.032043 | 0.027466 | -0.32959 | 0.28839 | -0.50354 | -0.6958 | 0.004578 | -0.13733 | -0.073242 | 0.082397 | 0.018311 | -0.60425 | -0.61798 | -0.018311 | -0.21057 | -122.319 | 0.51727 | 0.15564 | 0.36621 | -122.6257 | -0.11902 | -0.13275 | -122.525 | 0.48981 | 0.41199 | 0.54474 | -122.5891 | 0.77362 | 0.46692 | 0.5127 | -123.3032 | 0.56763 | 0.50354 | 0.3479 | -123.2254
4568.0312 | 123.0881 | -0.51727 | 122.612 | -0.15274 | 0.017703 | 0.0048044 | 0.018393 | 0.025891 | 0.0012047 | -0.0075047 | -0.015411 | -0.0033582 | 0.017053 | -0.010747 | 0.024716 | -0.0051376 | 0.018311 | 0.022888 | 0.004578 | -0.32501 | 0.29297 | -0.51727 | -0.70038 | -0.027466 | -0.16937 | -0.15106 | 0.10529 | 0.050354 | -0.59967 | -0.63171 | 0 | -0.1831 | -122.319 | 0.54016 | 0.19226 | 0.37537 | -122.5937 | -0.082397 | -0.11444 | -122.5067 | 0.48981 | 0.36621 | 0.48065 | -122.5616 | 0.81024 | 0.53558 | 0.52185 | -123.3124 | 0.62256 | 0.56763 | 0.3479 | -123.2437
4569.0156 | 123.0515 | -0.54016 | 122.6257 | 0.16006 | 0.019412 | 0.005018 | 0.01882 | 0.0276 | 0.0018457 | -0.010282 | 0.15244 | -0.00229 | 0.015985 | -0.010106 | 0.026425 | -0.006633 | -0.041199 | -0.059509 | -0.045776 | -0.36163 | 0.28381 | -0.53558 | -0.70953 | -0.073242 | -0.25177 | -0.16937 | 0.11444 | 0.073242 | -0.62256 | -0.65918 | 0.004578 | -0.16937 | -122.3419 | 0.48065 | 0.17853 | 0.3479 | -122.6669 | -0.082398 | -0.11902 | -122.5113 | 0.46692 | 0.37079 | 0.48981 | -122.5525 | 0.82397 | 0.49896 | 0.49439 | -123.3353 | 0.6546 | 0.6134 | 0.28839 | -123.2849
4570.0156 | 123.0286 | -0.52643 | 122.6395 | 0.053253 | 0.019412 | 0.006727 | 0.01647 | 0.025037 | 0.0022729 | -0.0089999 | -0.03067 | -0.00036736 | 0.017267 | -0.0088247 | 0.026425 | -0.0072738 | -0.004578 | -0.009155 | -0.004578 | -0.33417 | 0.29297 | -0.54932 | -0.70953 | -0.068665 | -0.23346 | -0.1831 | 0.11444 | 0.059509 | -0.63629 | -0.6546 | -0.022888 | -0.18311 | -122.3465 | 0.51727 | 0.19226 | 0.37537 | -122.644 | -0.10986 | -0.12817 | -122.525 | 0.45776 | 0.34332 | 0.4715 | -122.58 | 0.8194 | 0.52185 | 0.52185 | -123.349 | 0.64087 | 0.58594 | 0.29297 | -123.2941
4571.0156 | 123.143 | -0.48523 | 122.644 | 0.053253 | 0.017703 | 0.003309 | 0.01583 | 0.025677 | 0.0014185 | -0.010282 | 0.42709 | -0.0033582 | 0.014704 | -0.0098929 | 0.024503 | -0.0040696 | -0.013733 | 0.009155 | 0.013733 | -0.33417 | 0.27466 | -0.52185 | -0.70496 | -0.013733 | -0.17853 | -0.07782 | 0.086975 | 0.041199 | -0.60425 | -0.63629 | -0.036622 | -0.21973 | -122.3694 | 0.49438 | 0.15106 | 0.37079 | -122.6578 | -0.11902 | -0.15106 | -122.5571 | 0.4715 | 0.40741 | 0.55847 | -122.6028 | 0.75989 | 0.4715 | 0.49896 | -123.349 | 0.5722 | 0.52643 | 0.3067 | -123.2803
4572.0156 | 123.0835 | -0.5127 | 122.6257 | 0.068512 | 0.019412 | 0.0045908 | 0.017111 | 0.028027 | 0.0031273 | -0.0092137 | 0.0074766 | -0.0037854 | 0.013635 | -0.0092521 | 0.025143 | -0.005565 | -0.004578 | -0.022888 | -0.013733 | -0.32501 | 0.27008 | -0.52643 | -0.70953 | -0.064087 | -0.21973 | -0.17853 | 0.10529 | 0.068665 | -0.64087 | -0.66376 | -0.013733 | -0.19684 | -122.3557 | 0.48981 | 0.18768 | 0.38452 | -122.6303 | -0.12817 | -0.15106 | -122.5204 | 0.44861 | 0.33417 | 0.48523 | -122.5571 | 0.78278 | 0.50812 | 0.49896 | -123.3353 | 0.61798 | 0.58136 | 0.29297 | -123.2895
4573.0312 | 123.175 | -0.45776 | 122.5983 | 0.0914 | 0.017276 | 0.0016 | 0.015402 | 0.026959 | -0.0034949 | -0.0096409 | 0.40421 | -0.0048536 | 0.012781 | -0.0096793 | 0.024716 | -0.0040696 | 0.027466 | 0.09613 | 0.10071 | -0.27466 | 0.25177 | -0.49896 | -0.67749 | 0.045776 | -0.1236 | -0.036621 | 0.073242 | 0.027466 | -0.59052 | -0.62256 | -0.041198 | -0.21973 | -122.3465 | 0.55389 | 0.18311 | 0.40283 | -122.5708 | -0.13275 | -0.16479 | -122.525 | 0.50354 | 0.42114 | 0.58594 | -122.5708 | 0.70953 | 0.48523 | 0.55847 | -123.2758 | 0.53101 | 0.48523 | 0.33417 | -123.2208
4574.0156 | 123.0652 | -0.52185 | 122.6303 | -0.099335 | 0.018344 | 0.0039498 | 0.018179 | 0.027386 | 0.0029137 | -0.0062229 | 0.015106 | -0.0018628 | 0.014917 | -0.011815 | 0.025998 | -0.0057786 | 0.013733 | 0 | -0.013733 | -0.33875 | 0.27924 | -0.54016 | -0.72327 | -0.064087 | -0.21973 | -0.17395 | 0.10529 | 0.068665 | -0.63171 | -0.68207 | -0.01831 | -0.20142 | -122.3511 | 0.52185 | 0.18311 | 0.38452 | -122.6166 | -0.10986 | -0.16022 | -122.525 | 0.45776 | 0.3479 | 0.50812 | -122.5616 | 0.80109 | 0.53558 | 0.50812 | -123.3536 | 0.62714 | 0.59052 | 0.30212 | -123.3124
4575.0156 | 123.1293 | -0.49896 | 122.6212 | 0.20584 | 0.018558 | 0.0041634 | 0.01647 | 0.026532 | 0.0016321 | -0.010282 | 0.24399 | -0.0020764 | 0.013849 | -0.0086111 | 0.026212 | -0.002147 | -0.022888 | -0.013733 | 0.004578 | -0.35248 | 0.28839 | -0.52643 | -0.70496 | 0 | -0.19684 | -0.10986 | 0.086975 | 0.027466 | -0.61798 | -0.62256 | -0.027466 | -0.20599 | -122.3328 | 0.48523 | 0.14648 | 0.35248 | -122.644 | -0.11902 | -0.1236 | -122.5342 | 0.49896 | 0.3891 | 0.5127 | -122.5937 | 0.78735 | 0.47607 | 0.50354 | -123.3261 | 0.58594 | 0.52643 | 0.30212 | -123.2437
4576.0156 | 123.0515 | -0.54474 | 122.644 | -0.045929 | 0.020053 | 0.0035226 | 0.015616 | 0.025464 | 0.0031273 | -0.0092137 | -0.061188 | -0.0018628 | 0.019403 | -0.0094657 | 0.025143 | -0.0051376 | -0.041199 | -0.064087 | -0.059509 | -0.35248 | 0.29755 | -0.54474 | -0.70953 | -0.10071 | -0.25635 | -0.2243 | 0.10986 | 0.068665 | -0.64087 | -0.66834 | 0 | -0.1648 | -122.3465 | 0.48065 | 0.19226 | 0.35706 | -122.6852 | -0.09613 | -0.1236 | -122.5342 | 0.44403 | 0.32043 | 0.44403 | -122.5754 | 0.84228 | 0.50354 | 0.48523 | -123.3536 | 0.6546 | 0.6134 | 0.28839 | -123.3124
4577.0156 | 123.1384 | -0.50812 | 122.5983 | 0.12192 | 0.018771 | 0.0058724 | 0.017752 | 0.025464 | -0.0011451 | -0.010068 | 0.25925 | -0.0037854 | 0.016199 | -0.0094657 | 0.024503 | -0.0051376 | -0.013733 | -0.013733 | 0 | -0.35706 | 0.28381 | -0.52185 | -0.70953 | -0.022888 | -0.20599 | -0.11444 | 0.086975 | 0.027466 | -0.6134 | -0.64545 | -0.013733 | -0.20142 | -122.3145 | 0.49438 | 0.15106 | 0.35248 | -122.612 | -0.10529 | -0.13733 | -122.5113 | 0.48523 | 0.39368 | 0.53101 | -122.5708 | 0.79193 | 0.49438 | 0.50812 | -123.3078 | 0.59509 | 0.53558 | 0.30212 | -123.2437
4578.0312 | 123.1064 | -0.50812 | 122.6166 | -0.015411 | 0.020053 | 0.005018 | 0.016043 | 0.026318 | 0.00035035 | -0.010495 | -0.038299 | -0.0025038 | 0.016626 | -0.010961 | 0.025571 | -0.0059922 | 0.027466 | 0.041199 | 0 | -0.32501 | 0.28839 | -0.51727 | -0.72327 | -0.036621 | -0.19684 | -0.16022 | 0.10529 | 0.036621 | -0.63171 | -0.64545 | -0.009155 | -0.21515 | -122.3282 | 0.54932 | 0.18311 | 0.39825 | -122.5891 | -0.1236 | -0.13733 | -122.5113 | 0.4715 | 0.3479 | 0.48523 | -122.58 | 0.79651 | 0.53558 | 0.50812 | -123.3398 | 0.6134 | 0.54474 | 0.31128 | -123.262
4579.0156 | 123.1567 | -0.4715 | 122.6074 | 0.12192 | 0.016208 | 0.0041634 | 0.013266 | 0.0276 | -0.0034949 | -0.010709 | 0.29739 | -0.0042126 | 0.013635 | -0.01267 | 0.024075 | -0.0053512 | 0.036621 | 0.10529 | 0.09613 | -0.29297 | 0.25635 | -0.5127 | -0.66376 | 0.032043 | -0.13275 | -0.041199 | 0.068665 | 0.009155 | -0.61798 | -0.63171 | -0.041198 | -0.19226 | -122.3511 | 0.57678 | 0.17853 | 0.37079 | -122.5708 | -0.14648 | -0.16022 | -122.5388 | 0.50354 | 0.4303 | 0.59052 | -122.5983 | 0.72785 | 0.50812 | 0.56763 | -123.2712 | 0.54016 | 0.48065 | 0.33875 | -123.2391
4580.0156 | 123.1201 | -0.51727 | 122.6715 | -0.22141 | 0.019412 | 0.0048044 | 0.021384 | 0.026318 | 0.00035035 | -0.0092137 | 0.15244 | -0.0027174 | 0.016413 | -0.012029 | 0.024075 | -0.0062058 | 0.032043 | 0.036621 | 0.004578 | -0.32959 | 0.27924 | -0.52185 | -0.70953 | -0.027466 | -0.18768 | -0.15564 | 0.10529 | 0.054932 | -0.62714 | -0.66376 | -0.004578 | -0.19226 | -122.3923 | 0.55389 | 0.18768 | 0.37994 | -122.6395 | -0.10986 | -0.14648 | -122.5662 | 0.48981 | 0.36163 | 0.50812 | -122.6166 | 0.79651 | 0.54932 | 0.52185 | -123.381 | 0.62256 | 0.5722 | 0.32959 | -123.3353
4581.0156 | 123.1705 | -0.46692 | 122.5891 | 0.16006 | 0.013858 | 0.0052316 | 0.016257 | 0.024396 | -0.0022131 | -0.0087863 | 0.17532 | -0.0050672 | 0.015558 | -0.010534 | 0.024503 | -0.0062058 | 0.041199 | 0.068665 | 0.07782 | -0.29755 | 0.26093 | -0.49896 | -0.68207 | 0.036621 | -0.13733 | -0.045776 | 0.059509 | 0 | -0.62256 | -0.6134 | -0.032043 | -0.21515 | -122.3282 | 0.53558 | 0.16937 | 0.38452 | -122.5479 | -0.15564 | -0.14648 | -122.5296 | 0.50354 | 0.42114 | 0.56763 | -122.5891 | 0.72784 | 0.50812 | 0.54474 | -123.2712 | 0.52643 | 0.46692 | 0.32959 | -123.2025
4582.0156 | 123.111 | -0.48981 | 122.644 | 0.27451 | 0.017489 | 0.0030954 | 0.017325 | 0.025464 | 0.00077755 | -0.0079319 | 0.14481 | -0.0035718 | 0.016199 | -0.011602 | 0.024503 | -0.0047104 | -0.004578 | -0.027466 | -0.004578 | -0.35248 | 0.29297 | -0.52185 | -0.70953 | -0.032043 | -0.21973 | -0.11444 | 0.091553 | 0.036621 | -0.62714 | -0.64087 | -0.032044 | -0.21973 | -122.3511 | 0.46234 | 0.13733 | 0.35706 | -122.6486 | -0.13733 | -0.15106 | -122.5525 | 0.45776 | 0.37537 | 0.52643 | -122.6074 | 0.78278 | 0.48523 | 0.48523 | -123.3536 | 0.58136 | 0.52643 | 0.27008 | -123.2849
4583.0312 | 123.0652 | -0.50812 | 122.6303 | 0.083771 | 0.017917 | 0.0052316 | 0.019461 | 0.026532 | 0.0014185 | -0.0075047 | 0.2211 | -0.0042126 | 0.016199 | -0.0086111 | 0.024716 | -0.0042832 | -0.013733 | -0.11444 | -0.027466 | -0.35248 | 0.30212 | -0.52185 | -0.71869 | -0.059509 | -0.25177 | -0.16937 | 0.11902 | 0.068665 | -0.63629 | -0.65918 | -0.013733 | -0.21057 | -122.3282 | 0.39368 | 0.15564 | 0.36621 | -122.644 | -0.12817 | -0.15106 | -122.5113 | 0.44861 | 0.33874 | 0.48981 | -122.5616 | 0.81024 | 0.49438 | 0.48065 | -123.349 | 0.62714 | 0.57678 | 0.25635 | -123.2895
4584.0156 | 123.1293 | -0.52185 | 122.6395 | 0.11429 | 0.018771 | 0.0048044 | 0.016898 | 0.027386 | 0.0024865 | -0.0079319 | 0.21347 | -0.0020764 | 0.01684 | -0.010747 | 0.025784 | -0.0044968 | -0.009155 | -0.032043 | -0.022888 | -0.36163 | 0.29297 | -0.52185 | -0.70038 | -0.027466 | -0.2243 | -0.11444 | 0.091553 | 0.041199 | -0.63171 | -0.63629 | 0 | -0.17853 | -122.3465 | 0.48981 | 0.16022 | 0.33874 | -122.6486 | -0.10986 | -0.11444 | -122.5479 | 0.49438 | 0.40741 | 0.52185 | -122.5983 | 0.81482 | 0.5127 | 0.49896 | -123.3398 | 0.6134 | 0.56305 | 0.29755 | -123.2758
4585.0156 | 123.0927 | -0.5127 | 122.6212 | 0.17532 | 0.018771 | 0.0056588 | 0.01583 | 0.026746 | -0.0013587 | -0.0087863 | 0.18295 | -0.0018628 | 0.014276 | -0.0096793 | 0.024289 | -0.004924 | -0.022888 | -0.036621 | -0.009155 | -0.35706 | 0.28839 | -0.51727 | -0.70496 | -0.018311 | -0.21515 | -0.12817 | 0.07782 | 0.036621 | -0.60883 | -0.6546 | -0.004578 | -0.19226 | -122.3328 | 0.47607 | 0.15564 | 0.3479 | -122.644 | -0.096131 | -0.14191 | -122.5433 | 0.49438 | 0.38452 | 0.52643 | -122.5845 | 0.80109 | 0.48981 | 0.50354 | -123.3261 | 0.59052 | 0.54932 | 0.29755 | -123.2758
4586.0156 | 123.111 | -0.50812 | 122.6349 | 0.19058 | 0.019198 | 0.0065134 | 0.018393 | 0.026532 | 0.00035035 | -0.0075047 | 0.022736 | -0.0014356 | 0.017053 | -0.0088247 | 0.025571 | -0.005565 | -0.018311 | -0.027466 | -0.032043 | -0.35706 | 0.30212 | -0.54016 | -0.72327 | -0.041199 | -0.22888 | -0.12817 | 0.10071 | 0.036621 | -0.6134 | -0.63629 | -0.032043 | -0.21515 | -122.3328 | 0.48065 | 0.15106 | 0.36621 | -122.6532 | -0.10529 | -0.12817 | -122.5342 | 0.46692 | 0.37994 | 0.50812 | -122.5983 | 0.81024 | 0.48981 | 0.47607 | -123.3582 | 0.60883 | 0.54474 | 0.27924 | -123.2712
4587.0156 | 123.2162 | -0.48981 | 122.5845 | 0.25925 | 0.015353 | 0.0043772 | 0.014121 | 0.026532 | -0.0024269 | -0.010282 | 0.23636 | -0.0037854 | 0.017053 | -0.010534 | 0.024716 | -0.0047104 | 0.07782 | 0.064087 | 0.082397 | -0.28839 | 0.24719 | -0.48981 | -0.67291 | 0.041199 | -0.1236 | -0.041199 | 0.054932 | 0.022888 | -0.59052 | -0.61798 | 0 | -0.18311 | -122.3373 | 0.55389 | 0.20142 | 0.38452 | -122.5067 | -0.10071 | -0.12817 | -122.5296 | 0.53101 | 0.44861 | 0.57678 | -122.5616 | 0.737 | 0.56763 | 0.5722 | -123.2574 | 0.54474 | 0.5127 | 0.36621 | -123.2025
4588.0156 | 123.1384 | -0.48981 | 122.6074 | 0.16769 | 0.011722 | 0.0075814 | 0.010703 | 0.026105 | -0.0032813 | -0.010068 | 0.27451 | -0.006349 | 0.014276 | -0.011175 | 0.024075 | -0.0030014 | 0.064087 | 0.07782 | 0.07782 | -0.27924 | 0.25635 | -0.50812 | -0.67291 | 0.036621 | -0.14191 | -0.045776 | 0.064087 | 0.018311 | -0.60425 | -0.64087 | -0.018311 | -0.18311 | -122.3511 | 0.56763 | 0.21057 | 0.39368 | -122.5433 | -0.11444 | -0.15106 | -122.5433 | 0.52643 | 0.44403 | 0.59509 | -122.5891 | 0.74616 | 0.55389 | 0.56763 | -123.2803 | 0.55389 | 0.50812 | 0.3479 | -123.2483
4589.0156 | 123.2025 | -0.48065 | 122.6074 | 0.0914 | 0.016849 | 0.005018 | 0.014975 | 0.024182 | -0.0015723 | -0.0089999 | 0.22873 | -0.0042126 | 0.015344 | -0.011602 | 0.026852 | -0.0079148 | 0.082397 | 0.082397 | 0.082397 | -0.29755 | 0.25635 | -0.5127 | -0.66376 | 0.041199 | -0.11902 | -0.050354 | 0.07782 | 0.018311 | -0.60425 | -0.63171 | -0.032043 | -0.18311 | -122.3511 | 0.56305 | 0.18311 | 0.36621 | -122.525 | -0.1236 | -0.15106 | -122.5296 | 0.52185 | 0.4303 | 0.58136 | -122.5891 | 0.737 | 0.56305 | 0.56305 | -123.2712 | 0.55847 | 0.49896 | 0.36163 | -123.2391
4590.0156 | 123.1064 | -0.53558 | 122.6349 | 0.17532 | 0.021335 | 0.0041634 | 0.019461 | 0.025037 | 0.0033411 | -0.0077183 | 0.13718 | -0.0016492 | 0.015985 | -0.010534 | 0.027921 | -0.0079148 | 0.004578 | -0.064087 | -0.036621 | -0.37994 | 0.29755 | -0.55389 | -0.73242 | -0.032043 | -0.2655 | -0.15564 | 0.11444 | 0.050354 | -0.64087 | -0.66376 | -0.018311 | -0.19684 | -122.3373 | 0.4715 | 0.15564 | 0.35248 | -122.6303 | -0.10529 | -0.12817 | -122.5204 | 0.50354 | 0.37994 | 0.50812 | -122.5845 | 0.83313 | 0.54016 | 0.49896 | -123.3673 | 0.65002 | 0.58594 | 0.27008 | -123.2986
4591.0156 | 123.1888 | -0.50354 | 122.5754 | 0.11429 | 0.015567 | 0.0056588 | 0.014334 | 0.026746 | -0.0017859 | -0.0092137 | 0.17532 | -0.0044264 | 0.015131 | -0.010106 | 0.023862 | -0.0064194 | 0.064087 | 0.091553 | 0.091553 | -0.32959 | 0.24261 | -0.50354 | -0.68665 | 0.036621 | -0.13733 | -0.059509 | 0.054932 | 0.022888 | -0.59967 | -0.63629 | 0 | -0.18311 | -122.3328 | 0.59509 | 0.17395 | 0.35706 | -122.5113 | -0.09613 | -0.13275 | -122.5204 | 0.54016 | 0.44403 | 0.57678 | -122.5525 | 0.74616 | 0.56763 | 0.59509 | -123.262 | 0.55847 | 0.52643 | 0.36621 | -123.2117
4592.0156 | 123.0789 | -0.55389 | 122.6074 | 0.13718 | 0.020267 | 0.0035226 | 0.018393 | 0.026532 | 0.0050499 | -0.0072911 | 0.053253 | -0.0025038 | 0.018335 | -0.0094657 | 0.027493 | -0.0079148 | 0 | -0.059509 | -0.059509 | -0.37994 | 0.29755 | -0.55389 | -0.72327 | -0.07782 | -0.27008 | -0.21515 | 0.09613 | 0.064087 | -0.64545 | -0.67291 | 0 | -0.16937 | -122.3099 | 0.49439 | 0.17395 | 0.34332 | -122.6074 | -0.091553 | -0.11902 | -122.5113 | 0.47607 | 0.33874 | 0.45776 | -122.5433 | 0.85144 | 0.55389 | 0.49439 | -123.3307 | 0.65002 | 0.61798 | 0.28381 | -123.2803
4593.0156 | 123.1064 | -0.52643 | 122.6532 | -0.28244 | 0.012362 | 0.0039498 | 0.013693 | 0.027814 | -0.0045631 | -0.0092137 | -0.23666 | -0.0033582 | 0.013849 | -0.012243 | 0.023221 | -0.0051376 | 0 | 0.045776 | 0.041199 | -0.32501 | 0.28839 | -0.51727 | -0.70953 | -0.050354 | -0.1831 | -0.13275 | 0.086975 | 0.054932 | -0.62256 | -0.66834 | 0.009155 | -0.18311 | -122.3648 | 0.5722 | 0.20142 | 0.38452 | -122.6532 | -0.096131 | -0.14191 | -122.5662 | 0.47607 | 0.39368 | 0.53558 | -122.5983 | 0.81482 | 0.52643 | 0.56763 | -123.3627 | 0.6134 | 0.58136 | 0.34332 | -123.3215
4594.0156 | 123.0286 | -0.53101 | 122.644 | -0.053558 | 0.018771 | 0.0030954 | 0.014548 | 0.026105 | 0.0050499 | -0.0092137 | -0.023041 | -0.0014356 | 0.018549 | -0.0092521 | 0.027921 | -0.0074876 | -0.004578 | -0.045776 | -0.054932 | -0.36163 | 0.28839 | -0.54016 | -0.71869 | -0.086975 | -0.28839 | -0.21973 | 0.10071 | 0.045776 | -0.65002 | -0.67291 | -0.009155 | -0.18768 | -122.3557 | 0.48523 | 0.16937 | 0.35706 | -122.6486 | -0.11902 | -0.14191 | -122.5433 | 0.44403 | 0.31128 | 0.45319 | -122.5983 | 0.8194 | 0.52643 | 0.47607 | -123.3627 | 0.63171 | 0.57678 | 0.24261 | -123.317
4595.0156 | 123.1567 | -0.49439 | 122.6257 | 0.076141 | 0.014926 | 0.0056588 | 0.012625 | 0.025037 | -0.0062721 | -0.0098545 | 0.32028 | -0.0048536 | 0.012995 | -0.0094657 | 0.023434 | -0.002147 | 0.027466 | 0.086975 | 0.091553 | -0.31586 | 0.27008 | -0.48981 | -0.69122 | 0 | -0.14648 | -0.050354 | 0.064087 | 0.009155 | -0.60425 | -0.64087 | 0.004578 | -0.19684 | -122.3557 | 0.58136 | 0.17853 | 0.37537 | -122.5983 | -0.10986 | -0.14648 | -122.5616 | 0.49439 | 0.44403 | 0.59052 | -122.6166 | 0.76447 | 0.52185 | 0.58594 | -123.317 | 0.55847 | 0.50354 | 0.3479 | -123.2666
4596.0156 | 123.2162 | -0.48065 | 122.6303 | 0.12955 | 0.017917 | 0.0026682 | 0.017539 | 0.024823 | 0.0014185 | -0.0085727 | 0.18295 | -0.0050672 | 0.017053 | -0.013311 | 0.025357 | -0.0057786 | 0.054932 | 0.073242 | 0.064087 | -0.31128 | 0.2655 | -0.50812 | -0.67749 | 0.050354 | -0.15564 | -0.059509 | 0.068665 | 0.004578 | -0.58594 | -0.63171 | -0.027466 | -0.19684 | -122.3648 | 0.55389 | 0.16937 | 0.36621 | -122.5754 | -0.10529 | -0.15106 | -122.5616 | 0.53101 | 0.42114 | 0.5722 | -122.6257 | 0.74616 | 0.53558 | 0.54474 | -123.3078 | 0.54932 | 0.48523 | 0.32501 | -123.262
4597.0156 | 123.2025 | -0.4715 | 122.5983 | 0.16006 | 0.017276 | 0.0041634 | 0.016257 | 0.026532 | 0.00077755 | -0.0055821 | 0.14481 | -0.0044264 | 0.014276 | -0.012243 | 0.025143 | -0.0070602 | 0.041199 | 0.009155 | 0.045776 | -0.29755 | 0.28381 | -0.49896 | -0.68665 | 0.032043 | -0.15106 | -0.068665 | 0.050354 | 0.004578 | -0.59509 | -0.62256 | -0.027465 | -0.21515 | -122.3145 | 0.48065 | 0.17395 | 0.3891 | -122.5571 | -0.1236 | -0.15106 | -122.5479 | 0.50354 | 0.40283 | 0.55389 | -122.5937 | 0.75531 | 0.5127 | 0.51727 | -123.2849 | 0.52185 | 0.47608 | 0.32044 | -123.2208
4598.0312 | 123.1476 | -0.53101 | 122.6166 | -0.076447 | 0.018558 | 0.0045908 | 0.016898 | 0.026959 | 0.0035547 | -0.0087863 | -0.14511 | -0.00079476 | 0.017908 | -0.011602 | 0.027066 | -0.0070602 | 0.064087 | 0.004578 | 0.013733 | -0.33875 | 0.27924 | -0.53101 | -0.70953 | -0.009155 | -0.20599 | -0.16479 | 0.091553 | 0.050354 | -0.63629 | -0.64545 | 0 | -0.17853 | -122.3373 | 0.53558 | 0.19226 | 0.37079 | -122.5525 | -0.10529 | -0.11444 | -122.525 | 0.52185 | 0.36621 | 0.48065 | -122.5662 | 0.81024 | 0.59509 | 0.54474 | -123.3261 | 0.62256 | 0.58136 | 0.32501 | -123.262
4599.0156 | 123.1934 | -0.49896 | 122.6257 | 0.14481 | 0.013217 | 0.0037362 | 0.015616 | 0.025464 | -0.0034949 | -0.010068 | 0.25925 | -0.003999 | 0.013422 | -0.010534 | 0.023648 | -0.0030014 | 0.041199 | 0.10071 | 0.10071 | -0.32501 | 0.25635 | -0.49439 | -0.70038 | 0.027466 | -0.14191 | -0.050354 | 0.064087 | 0 | -0.6134 | -0.63171 | 0.004577 | -0.20142 | -122.3694 | 0.59967 | 0.17395 | 0.37537 | -122.5845 | -0.11444 | -0.13275 | -122.5616 | 0.52643 | 0.44861 | 0.58136 | -122.6257 | 0.75531 | 0.54016 | 0.59967 | -123.3261 | 0.56305 | 0.49896 | 0.35706 | -123.2574
4600.0156 | 123.0835 | -0.51727 | 122.6303 | 0.24399 | 0.022403 | 0.0039498 | 0.020102 | 0.026532 | 0.0035547 | -0.0068637 | -0.34348 | -0.0025038 | 0.017481 | -0.0094657 | 0.027493 | -0.0057786 | 0.013733 | 0.013733 | -0.013733 | -0.36621 | 0.29297 | -0.54932 | -0.72784 | -0.059509 | -0.26093 | -0.17853 | 0.10071 | 0.041199 | -0.63629 | -0.66834 | -0.032043 | -0.21057 | -122.3373 | 0.53101 | 0.15106 | 0.36163 | -122.6166 | -0.11902 | -0.15106 | -122.5296 | 0.45776 | 0.33874 | 0.48981 | -122.5891 | 0.81024 | 0.53101 | 0.50354 | -123.3582 | 0.61798 | 0.55847 | 0.25635 | -123.2986
4601.0156 | 123.1796 | -0.48065 | 122.5983 | 0.16769 | 0.016849 | 0.0058724 | 0.014121 | 0.026532 | 0.00056395 | -0.0085727 | 0.12955 | -0.0042126 | 0.011926 | -0.012243 | 0.025143 | -0.0053512 | 0.059509 | 0.059509 | 0.068665 | -0.27924 | 0.26093 | -0.49439 | -0.67749 | 0.041199 | -0.14648 | -0.045776 | 0.059509 | -0.004578 | -0.60883 | -0.62256 | -0.013733 | -0.19684 | -122.3373 | 0.54016 | 0.20142 | 0.39825 | -122.5388 | -0.12817 | -0.14191 | -122.5388 | 0.52185 | 0.43488 | 0.57678 | -122.6028 | 0.74158 | 0.54016 | 0.54932 | -123.2758 | 0.54016 | 0.47607 | 0.33417 | -123.2208
4602.0156 | 123.0927 | -0.53558 | 122.644 | 0.13718 | 0.017489 | 0.0056588 | 0.01583 | 0.025891 | 0.0012047 | -0.0072911 | 0.19058 | -0.0035718 | 0.015131 | -0.013311 | 0.027707 | -0.0047104 | -0.022888 | -0.064087 | -0.041199 | -0.37537 | 0.29755 | -0.54016 | -0.72327 | -0.059509 | -0.2655 | -0.17853 | 0.10986 | 0.041199 | -0.63171 | -0.66834 | -0.004578 | -0.18768 | -122.3465 | 0.4715 | 0.16022 | 0.3479 | -122.6669 | -0.096131 | -0.13275 | -122.5342 | 0.47607 | 0.35706 | 0.48981 | -122.6028 | 0.83313 | 0.5127 | 0.49438 | -123.3673 | 0.64545 | 0.57678 | 0.27008 | -123.3124
4603.0312 | 123.1201 | -0.51727 | 122.6349 | -0.0383 | 0.019626 | 0.0041634 | 0.019248 | 0.025891 | 0.0016321 | -0.0077183 | -0.12222 | -0.002931 | 0.015558 | -0.0096793 | 0.023862 | -0.0064194 | 0.041199 | 0.032043 | 0.004578 | -0.33875 | 0.28839 | -0.53101 | -0.737 | -0.009155 | -0.20599 | -0.16479 | 0.10071 | 0.045776 | -0.63171 | -0.66376 | -0.013733 | -0.21973 | -122.3465 | 0.54932 | 0.17853 | 0.39825 | -122.5937 | -0.11444 | -0.14648 | -122.5342 | 0.50812 | 0.35248 | 0.49896 | -122.5891 | 0.80566 | 0.55847 | 0.52185 | -123.3719 | 0.61798 | 0.56305 | 0.31128 | -123.2986
4604.0156 | 123.2071 | -0.48981 | 122.6303 | 0.19058 | 0.017276 | 0.0018136 | 0.01583 | 0.026532 | -0.0013587 | -0.0075047 | 0.16769 | -0.0031446 | 0.015558 | -0.011602 | 0.023648 | -0.0044968 | 0.032043 | 0.073242 | 0.059509 | -0.31586 | 0.2655 | -0.51727 | -0.69122 | 0.027466 | -0.15106 | -0.050354 | 0.059509 | -0.013733 | -0.6134 | -0.63171 | -0.027466 | -0.20142 | -122.3648 | 0.56305 | 0.17395 | 0.37537 | -122.5983 | -0.1236 | -0.14191 | -122.5708 | 0.51727 | 0.43945 | 0.58136 | -122.644 | 0.75531 | 0.52185 | 0.54932 | -123.3215 | 0.54932 | 0.47607 | 0.33874 | -123.262
4605.0156 | 123.2208 | -0.49439 | 122.6074 | 0.16769 | 0.013644 | 0.0035226 | 0.014975 | 0.024609 | -0.0017859 | -0.0072911 | 0.46524 | -0.002931 | 0.015558 | -0.010106 | 0.024716 | -0.0059922 | 0.059509 | 0.10071 | 0.07782 | -0.29755 | 0.26093 | -0.50812 | -0.68207 | 0.041199 | -0.14191 | -0.064087 | 0.059509 | 0.009155 | -0.62256 | -0.6546 | -0.013733 | -0.18768 | -122.3465 | 0.59509 | 0.19684 | 0.38452 | -122.5479 | -0.12817 | -0.16022 | -122.5479 | 0.53558 | 0.4303 | 0.59052 | -122.5983 | 0.75531 | 0.55389 | 0.57221 | -123.2895 | 0.55389 | 0.50354 | 0.35248 | -123.262
4606.0156 | 123.175 | -0.52185 | 122.6303 | 0.15244 | 0.017703 | 0.0043772 | 0.017111 | 0.024609 | 0.0029137 | -0.010068 | 0.14481 | -0.00058096 | 0.015558 | -0.011388 | 0.024289 | -0.005565 | -0.009155 | -0.050354 | -0.041199 | -0.37994 | 0.3067 | -0.52185 | -0.73242 | -0.032043 | -0.25177 | -0.15106 | 0.10071 | 0.045776 | -0.64087 | -0.6546 | 0 | -0.21057 | -122.3236 | 0.4715 | 0.14191 | 0.35248 | -122.6395 | -0.11902 | -0.13275 | -122.5296 | 0.48981 | 0.37079 | 0.50354 | -122.5845 | 0.82855 | 0.5127 | 0.48065 | -123.3627 | 0.62256 | 0.56763 | 0.27008 | -123.2849
4607.0156 | 123.2071 | -0.49896 | 122.5983 | 0.15244 | 0.014499 | 0.0048044 | 0.013693 | 0.026532 | -0.0030677 | -0.0087863 | 0.26688 | -0.0025038 | 0.012781 | -0.0086111 | 0.024289 | -0.0036424 | 0.050354 | 0.10529 | 0.086975 | -0.3067 | 0.25635 | -0.49439 | -0.68665 | 0.041199 | -0.15106 | -0.041199 | 0.059509 | 0.009155 | -0.61798 | -0.63629 | 0.004577 | -0.18768 | -122.3419 | 0.60425 | 0.19226 | 0.37994 | -122.5479 | -0.11902 | -0.13733 | -122.5388 | 0.54016 | 0.45776 | 0.59509 | -122.5891 | 0.75531 | 0.54932 | 0.58594 | -123.2849 | 0.55847 | 0.50812 | 0.3479 | -123.2346
4608.0312 | 123.1201 | -0.53558 | 122.6578 | -0.18326 | 0.015567 | 0.006727 | 0.015402 | 0.028241 | 0.0018457 | -0.0077183 | -0.19089 | -0.0027174 | 0.013422 | -0.011602 | 0.02493 | -0.005565 | 0.022888 | -0.036621 | -0.027466 | -0.33417 | 0.29297 | -0.55847 | -0.737 | -0.027466 | -0.18768 | -0.14648 | 0.10529 | 0.036621 | -0.65002 | -0.67749 | -0.022889 | -0.20142 | -122.3648 | 0.49896 | 0.20142 | 0.40283 | -122.6349 | -0.11444 | -0.14191 | -122.5525 | 0.50812 | 0.3891 | 0.53101 | -122.6212 | 0.82855 | 0.55847 | 0.50812 | -123.3948 | 0.64087 | 0.5722 | 0.3479 | -123.3353
4609.0156 | 123.1842 | -0.49896 | 122.6074 | 0.28976 | 0.014926 | 0.0041634 | 0.014121 | 0.027386 | -0.0015723 | -0.0085727 | 0.060883 | -0.0033582 | 0.015131 | -0.011388 | 0.024716 | -0.004924 | 0.054932 | 0.11902 | 0.07782 | -0.30212 | 0.26093 | -0.49896 | -0.68665 | 0.045776 | -0.14191 | -0.050354 | 0.059509 | 0.013733 | -0.60425 | -0.62714 | 0 | -0.18768 | -122.3465 | 0.61798 | 0.19684 | 0.38452 | -122.5525 | -0.10529 | -0.12817 | -122.5479 | 0.54474 | 0.44861 | 0.57678 | -122.5937 | 0.75989 | 0.55389 | 0.57678 | -123.2941 | 0.55847 | 0.5127 | 0.35706 | -123.2346
4610.0156 | 123.1613 | -0.51727 | 122.6303 | 0.19058 | 0.017703 | 0.0039498 | 0.017325 | 0.025037 | 0.00013675 | -0.0081455 | 0.10666 | -0.0037854 | 0.016413 | -0.01032 | 0.025998 | -0.0042832 | -0.009155 | -0.009155 | -0.004578 | -0.35706 | 0.28839 | -0.50812 | -0.71411 | -0.027466 | -0.21057 | -0.1236 | 0.09613 | 0.027466 | -0.6134 | -0.64545 | 0.009155 | -0.19684 | -122.3419 | 0.50812 | 0.16022 | 0.35706 | -122.6395 | -0.09613 | -0.12817 | -122.5342 | 0.48981 | 0.39368 | 0.52185 | -122.6028 | 0.80566 | 0.50812 | 0.5127 | -123.3444 | 0.6134 | 0.54474 | 0.3067 | -123.2758
4611.0156 | 123.2025 | -0.49439 | 122.6349 | 0.22873 | 0.01578 | 0.0026682 | 0.015402 | 0.024396 | -0.00093145 | -0.0077183 | 0.10666 | -0.0025038 | 0.014917 | -0.010747 | 0.023221 | -0.0051376 | 0.045776 | 0.12817 | 0.086975 | -0.29755 | 0.27008 | -0.48065 | -0.68207 | 0.054932 | -0.13733 | -0.041199 | 0.068665 | 0.027466 | -0.60883 | -0.63629 | 0.013733 | -0.18768 | -122.3648 | 0.62256 | 0.19684 | 0.38452 | -122.5891 | -0.11444 | -0.14191 | -122.5662 | 0.54932 | 0.45319 | 0.59509 | -122.6074 | 0.76447 | 0.54016 | 0.58136 | -123.317 | 0.56305 | 0.52185 | 0.35706 | -123.2712
4612.0156 | 123.2117 | -0.48981 | 122.6349 | 0.31265 | 0.015994 | 0.0024544 | 0.014548 | 0.025891 | 0.00077755 | -0.0096409 | 0.0914 | -0.0031446 | 0.015131 | -0.010106 | 0.024503 | -0.0081284 | 0.050354 | 0.041199 | 0.054932 | -0.32501 | 0.28839 | -0.52185 | -0.69122 | 0.045776 | -0.15564 | -0.054932 | 0.073242 | 0.009155 | -0.60883 | -0.61798 | -0.032044 | -0.20142 | -122.3465 | 0.53101 | 0.16479 | 0.36621 | -122.5845 | -0.11902 | -0.12817 | -122.5616 | 0.53558 | 0.43488 | 0.56305 | -122.6257 | 0.7782 | 0.54016 | 0.54474 | -123.3261 | 0.56305 | 0.49896 | 0.33417 | -123.2529
4613.0312 | 123.1338 | -0.53558 | 122.6395 | 0.24399 | 0.017917 | 0.0028818 | 0.01647 | 0.023968 | 0.0020593 | -0.0066501 | 0.12192 | -0.0027174 | 0.017481 | -0.010106 | 0.025998 | -0.004924 | -0.013733 | -0.064087 | -0.045776 | -0.3891 | 0.30212 | -0.51727 | -0.737 | -0.068665 | -0.27008 | -0.16937 | 0.086975 | 0.059509 | -0.62256 | -0.65918 | 0.01831 | -0.20142 | -122.3373 | 0.4715 | 0.14648 | 0.3479 | -122.6532 | -0.086976 | -0.1236 | -122.5525 | 0.46692 | 0.36621 | 0.48981 | -122.58 | 0.83771 | 0.52185 | 0.48981 | -123.3765 | 0.62256 | 0.59509 | 0.2655 | -123.2986
4614.0156 | 123.0881 | -0.54016 | 122.644 | 0.15244 | 0.019198 | 0.0026682 | 0.016898 | 0.023968 | 0.0035547 | -0.0066501 | 0.14481 | -0.0016492 | 0.018549 | -0.0098929 | 0.023434 | -0.0068466 | -0.009155 | -0.068665 | -0.068665 | -0.3891 | 0.30212 | -0.53558 | -0.72327 | -0.073242 | -0.23804 | -0.17853 | 0.10071 | 0.050354 | -0.64545 | -0.67291 | 0.004578 | -0.18311 | -122.3419 | 0.4715 | 0.15106 | 0.33417 | -122.6532 | -0.10529 | -0.13275 | -122.5433 | 0.46692 | 0.36163 | 0.49438 | -122.5937 | 0.84228 | 0.53101 | 0.4715 | -123.3673 | 0.64087 | 0.59052 | 0.30212 | -123.317
4615.0156 | 123.2391 | -0.4715 | 122.6303 | 0.19821 | 0.017276 | 0.0037362 | 0.014334 | 0.026318 | -0.0022131 | -0.0077183 | 0.19058 | -0.0031446 | 0.014063 | -0.011815 | 0.026425 | -0.0064194 | 0.064087 | 0.10071 | 0.082397 | -0.28839 | 0.26093 | -0.49896 | -0.6958 | 0.041199 | -0.13733 | -0.045776 | 0.068665 | 0 | -0.60883 | -0.6134 | -0.027465 | -0.2243 | -122.3694 | 0.5722 | 0.18311 | 0.40741 | -122.5662 | -0.13733 | -0.14191 | -122.5616 | 0.5127 | 0.42572 | 0.56763 | -122.6303 | 0.73242 | 0.53558 | 0.55389 | -123.3261 | 0.54016 | 0.4715 | 0.33417 | -123.2437
4616.0156 | 123.2208 | -0.48981 | 122.6395 | 0.29739 | 0.01514 | 0.0024544 | 0.017111 | 0.027386 | -0.0013587 | -0.0085727 | 0.35843 | -0.0018628 | 0.014063 | -0.0096793 | 0.02493 | -0.0051376 | 0.059509 | 0.064087 | 0.07782 | -0.27008 | 0.24261 | -0.50812 | -0.66834 | 0.045776 | -0.13275 | -0.054932 | 0.064087 | 0.013733 | -0.60425 | -0.62714 | -0.018311 | -0.17853 | -122.3969 | 0.55389 | 0.21973 | 0.39825 | -122.58 | -0.11444 | -0.13733 | -122.5754 | 0.53558 | 0.43488 | 0.5722 | -122.6257 | 0.73242 | 0.54932 | 0.56763 | -123.3078 | 0.55389 | 0.50354 | 0.35706 | -123.2666
4617.0156 | 123.175 | -0.48981 | 122.6624 | 0.030365 | 0.01044 | 0.0054452 | 0.013693 | 0.024609 | -0.0054175 | -0.0094273 | 0.10666 | -0.0054944 | 0.013849 | -0.012029 | 0.021939 | -0.0023606 | -0.009155 | 0.036621 | 0.045776 | -0.33417 | 0.28381 | -0.52185 | -0.6958 | -0.018311 | -0.16022 | -0.059509 | 0.082397 | 0.027466 | -0.6134 | -0.63171 | -0.032044 | -0.20599 | -122.3785 | 0.52643 | 0.15564 | 0.36163 | -122.6715 | -0.1236 | -0.14191 | -122.58 | 0.4715 | 0.4303 | 0.5722 | -122.6349 | 0.77362 | 0.48065 | 0.53558 | -123.3582 | 0.5722 | 0.51727 | 0.32959 | -123.2941
4618.0156 | 123.175 | -0.48523 | 122.6166 | 0.15244 | 0.013858 | 0.006727 | 0.014975 | 0.026746 | -0.0017859 | -0.012631 | 0.15244 | -0.002931 | 0.015131 | -0.011388 | 0.02258 | -0.0042832 | 0.050354 | 0.086975 | 0.07782 | -0.3067 | 0.26093 | -0.50354 | -0.68207 | 0.022888 | -0.15106 | -0.050354 | 0.054932 | 0.009155 | -0.59509 | -0.64087 | -0.018311 | -0.19684 | -122.3557 | 0.5722 | 0.17853 | 0.37537 | -122.5662 | -0.10986 | -0.15564 | -122.5616 | 0.50812 | 0.43488 | 0.59052 | -122.6074 | 0.74615 | 0.53558 | 0.56305 | -123.2986 | 0.54016 | 0.49438 | 0.33417 | -123.2574
4619.0156 | 123.2162 | -0.4715 | 122.612 | 0.16006 | 0.016849 | 0.0054452 | 0.016898 | 0.026746 | -0.00050425 | -0.01135 | 0.16769 | -0.0027174 | 0.013208 | -0.011815 | 0.027066 | -0.004924 | 0.082397 | 0.07782 | 0.086975 | -0.27924 | 0.25177 | -0.50354 | -0.66834 | 0.064087 | -0.13733 | -0.059509 | 0.054932 | 0 | -0.60425 | -0.63171 | -0.032043 | -0.19684 | -122.3602 | 0.54932 | 0.19226 | 0.3891 | -122.5296 | -0.13275 | -0.16022 | -122.5571 | 0.53558 | 0.41199 | 0.5722 | -122.612 | 0.72327 | 0.55389 | 0.55847 | -123.2803 | 0.52643 | 0.4715 | 0.33417 | -123.2437
4620.0156 | 123.2162 | -0.48981 | 122.6166 | 0.2211 | 0.015567 | 0.0041634 | 0.015189 | 0.025037 | 0.0016321 | -0.0092137 | 0.09903 | -0.0042126 | 0.015344 | -0.0092521 | 0.024716 | -0.0057786 | 0.032043 | 0.009155 | 0.013733 | -0.33875 | 0.27008 | -0.52643 | -0.70496 | 0.036621 | -0.16479 | -0.068665 | 0.068665 | 0.013733 | -0.59967 | -0.61798 | -0.036621 | -0.21515 | -122.3465 | 0.49896 | 0.15106 | 0.36621 | -122.5845 | -0.10986 | -0.12817 | -122.5479 | 0.52643 | 0.42114 | 0.54932 | -122.6028 | 0.75989 | 0.52185 | 0.50354 | -123.3215 | 0.55847 | 0.50354 | 0.32501 | -123.2346
4621.0156 | 123.1567 | -0.50354 | 122.6395 | 0.0914 | 0.01279 | 0.0024544 | 0.014121 | 0.026532 | -0.0030677 | -0.0096409 | 0.12192 | -0.0037854 | 0.014276 | -0.012029 | 0.024075 | -0.0062058 | 0.036621 | 0.082397 | 0.068665 | -0.33875 | 0.27466 | -0.5127 | -0.67291 | 0.009155 | -0.17395 | -0.059509 | 0.068665 | 0.022888 | -0.59967 | -0.63171 | -0.009155 | -0.16937 | -122.3648 | 0.58594 | 0.16479 | 0.33417 | -122.6028 | -0.09613 | -0.12817 | -122.5708 | 0.5127 | 0.44403 | 0.5722 | -122.6166 | 0.7782 | 0.54016 | 0.5722 | -123.3124 | 0.5722 | 0.52643 | 0.32959 | -123.2712
4622.0156 | 123.0972 | -0.52643 | 122.6624 | 0.19058 | 0.019626 | 0.0045908 | 0.017539 | 0.024609 | 0.0041955 | -0.0075047 | 0.09903 | -0.0010084 | 0.014917 | -0.010961 | 0.024289 | -0.0094102 | 0.009155 | -0.064087 | -0.041199 | -0.37079 | 0.3067 | -0.53101 | -0.72327 | -0.041199 | -0.27466 | -0.17395 | 0.09613 | 0.036621 | -0.65002 | -0.66376 | -0.004578 | -0.19684 | -122.3557 | 0.46234 | 0.15564 | 0.35248 | -122.6532 | -0.1236 | -0.13733 | -122.5662 | 0.48523 | 0.35248 | 0.48981 | -122.6257 | 0.83313 | 0.53558 | 0.48523 | -123.3856 | 0.62256 | 0.56305 | 0.25177 | -123.3261
4623.0156 | 123.2162 | -0.48981 | 122.6715 | 0.16769 | 0.010226 | 0.0071542 | 0.014761 | 0.026105 | -0.0047767 | -0.0094273 | 0.18295 | -0.0059216 | 0.014917 | -0.010106 | 0.021298 | -0.0051376 | 0.013733 | 0.059509 | 0.050354 | -0.34332 | 0.27008 | -0.50354 | -0.6958 | -0.027466 | -0.16022 | -0.073242 | 0.086975 | 0.018311 | -0.59967 | -0.65002 | -0.013733 | -0.20599 | -122.4014 | 0.54932 | 0.14648 | 0.35248 | -122.6578 | -0.10986 | -0.16022 | -122.5845 | 0.46234 | 0.41656 | 0.57678 | -122.6532 | 0.75989 | 0.50354 | 0.54016 | -123.3673 | 0.57678 | 0.50812 | 0.32959 | -123.3215
4624.0156 | 123.1796 | -0.49896 | 122.6486 | 0.19821 | 0.018985 | 0.0035226 | 0.017539 | 0.025891 | 0.0041955 | -0.0089999 | 0.12955 | -0.0050672 | 0.012995 | -0.0096793 | 0.024716 | -0.004924 | 0.004578 | -0.022888 | -0.018311 | -0.36621 | 0.29755 | -0.52185 | -0.71869 | -0.018311 | -0.23804 | -0.13275 | 0.09613 | 0.027466 | -0.65002 | -0.6546 | -0.022889 | -0.21973 | -122.3511 | 0.47607 | 0.13275 | 0.35248 | -122.644 | -0.15106 | -0.15564 | -122.5525 | 0.48065 | 0.36621 | 0.52185 | -122.6212 | 0.79651 | 0.50354 | 0.48065 | -123.3673 | 0.59509 | 0.52643 | 0.26093 | -123.3032
4625.0156 | 123.1796 | -0.48523 | 122.6624 | 0.12192 | 0.013858 | 0.0048044 | 0.015189 | 0.028455 | -0.00093145 | -0.0079319 | 0.18295 | -0.0048536 | 0.01449 | -0.011175 | 0.024289 | -0.0044968 | 0.068665 | 0.10529 | 0.073242 | -0.29755 | 0.24719 | -0.48523 | -0.67291 | 0.045776 | -0.14191 | -0.050354 | 0.059509 | 0.009155 | -0.59509 | -0.6134 | 0 | -0.18768 | -122.4152 | 0.59052 | 0.18768 | 0.37537 | -122.5937 | -0.10986 | -0.12817 | -122.6028 | 0.53101 | 0.43488 | 0.56305 | -122.6532 | 0.73242 | 0.55389 | 0.55847 | -123.3353 | 0.54474 | 0.49438 | 0.34332 | -123.2758
4626.0156 | 123.1522 | -0.51727 | 122.6715 | 0.17532 | 0.017917 | 0.0030954 | 0.01583 | 0.0276 | 0.0024865 | -0.0064365 | 0.20584 | -0.0027174 | 0.016626 | -0.010534 | 0.025784 | -0.0053512 | 0 | -0.027466 | -0.041199 | -0.36163 | 0.30212 | -0.53101 | -0.71411 | -0.027466 | -0.25635 | -0.15564 | 0.11444 | 0.045776 | -0.63171 | -0.66376 | -0.013733 | -0.19684 | -122.3694 | 0.48981 | 0.15564 | 0.35248 | -122.6715 | -0.11444 | -0.14648 | -122.5571 | 0.48981 | 0.36163 | 0.50812 | -122.6257 | 0.8194 | 0.51727 | 0.47607 | -123.3856 | 0.63171 | 0.56305 | 0.26092 | -123.3353
4627.0156 | 123.23 | -0.48981 | 122.6349 | 0.2211 | 0.016208 | 0.0037362 | 0.014975 | 0.026959 | 0.0020593 | -0.0087863 | 0.20584 | -0.00464 | 0.014276 | -0.011175 | 0.023862 | -0.005565 | 0.073242 | 0.086975 | 0.07782 | -0.27008 | 0.24261 | -0.49439 | -0.67749 | 0.059509 | -0.1236 | -0.054932 | 0.068665 | -0.004578 | -0.59967 | -0.62714 | -0.004578 | -0.18768 | -122.3923 | 0.57678 | 0.21973 | 0.40741 | -122.5616 | -0.10986 | -0.13733 | -122.5662 | 0.54932 | 0.43488 | 0.5722 | -122.6395 | 0.73242 | 0.56305 | 0.56763 | -123.3124 | 0.55847 | 0.48523 | 0.36621 | -123.262
4628.0156 | 123.2025 | -0.48523 | 122.644 | -0.061188 | 0.01044 | 0.010572 | 0.012839 | 0.024609 | -0.0041357 | -0.0094273 | -0.099335 | -0.0052808 | 0.012567 | -0.010747 | 0.022794 | -0.0040696 | 0.022888 | 0.073242 | 0.073242 | -0.31128 | 0.27924 | -0.50354 | -0.68665 | 0.018311 | -0.14191 | -0.013733 | 0.086975 | 0.018311 | -0.6134 | -0.64545 | -0.018311 | -0.20142 | -122.3648 | 0.55847 | 0.17395 | 0.37537 | -122.6212 | -0.12817 | -0.16022 | -122.5571 | 0.50354 | 0.4715 | 0.63171 | -122.6257 | 0.76446 | 0.50812 | 0.55847 | -123.3307 | 0.5722 | 0.50354 | 0.34332 | -123.2895
4629.0156 | 123.2071 | -0.48981 | 122.644 | 0.18295 | 0.013858 | 0.0035226 | 0.01113 | 0.024182 | -0.0011451 | -0.0075047 | 0.11429 | -0.0035718 | 0.013635 | -0.0096793 | 0.025571 | -0.0036424 | 0.082397 | 0.09613 | 0.086975 | -0.30212 | 0.23804 | -0.48981 | -0.67749 | 0.045776 | -0.15106 | -0.059509 | 0.054932 | 0.004578 | -0.60425 | -0.62256 | 0 | -0.18768 | -122.406 | 0.58594 | 0.18768 | 0.37537 | -122.5616 | -0.11444 | -0.13275 | -122.5891 | 0.53558 | 0.4303 | 0.56305 | -122.6395 | 0.72784 | 0.5722 | 0.57678 | -123.3215 | 0.54474 | 0.49439 | 0.33874 | -123.2666
4630.0156 | 123.2071 | -0.48981 | 122.6669 | 0.25162 | 0.014285 | 0.0056588 | 0.015402 | 0.025891 | -7.6852e-05 | -0.0075047 | 0.20584 | -0.0059216 | 0.015772 | -0.010534 | 0.025357 | -0.0044968 | 0.082397 | 0.09613 | 0.082397 | -0.29755 | 0.25177 | -0.48523 | -0.67749 | 0.050354 | -0.13733 | -0.041199 | 0.091553 | 0.018311 | -0.60425 | -0.60425 | 0.004578 | -0.18768 | -122.4152 | 0.58594 | 0.19226 | 0.37994 | -122.5845 | -0.11444 | -0.11444 | -122.5754 | 0.54016 | 0.44861 | 0.56305 | -122.6486 | 0.74158 | 0.5722 | 0.5722 | -123.3444 | 0.58136 | 0.50812 | 0.35248 | -123.2712
4631.0156 | 123.1934 | -0.49896 | 122.6349 | 0.12192 | 0.013858 | 0.0065134 | 0.016898 | 0.025677 | -0.0015723 | -0.010495 | 0.16769 | -0.005708 | 0.013635 | -0.011602 | 0.023221 | -0.003856 | 0.068665 | 0.07782 | 0.064087 | -0.33417 | 0.27008 | -0.49439 | -0.69122 | 0.027466 | -0.16937 | -0.068665 | 0.086975 | 0.013733 | -0.59967 | -0.61798 | 0.004577 | -0.19226 | -122.3648 | 0.57678 | 0.1648 | 0.35706 | -122.5662 | -0.10071 | -0.11902 | -122.5479 | 0.52643 | 0.4303 | 0.54932 | -122.6212 | 0.76904 | 0.56763 | 0.56305 | -123.3261 | 0.58594 | 0.5127 | 0.32959 | -123.2529
4632.0156 | 123.2346 | -0.46692 | 122.6349 | 0.18295 | 0.015353 | 0.005018 | 0.016898 | 0.0276 | 0.0016321 | -0.0098545 | -0.03067 | -0.0035718 | 0.013635 | -0.0094657 | 0.025998 | -0.0072738 | 0.09613 | 0.086975 | 0.07782 | -0.30212 | 0.27466 | -0.47607 | -0.65918 | 0.054932 | -0.14191 | -0.059509 | 0.073242 | 0.013733 | -0.60425 | -0.63171 | -0.009155 | -0.19226 | -122.3602 | 0.55389 | 0.16479 | 0.35706 | -122.5388 | -0.13733 | -0.1648 | -122.5616 | 0.52185 | 0.40741 | 0.5722 | -122.6212 | 0.74158 | 0.56305 | 0.54474 | -123.2941 | 0.54016 | 0.48065 | 0.32501 | -123.2666
4633.0312 | 123.1338 | -0.52643 | 122.6852 | -0.22141 | 0.013644 | 0.0054452 | 0.014975 | 0.027386 | -0.00050425 | -0.010282 | -0.4274 | -0.0052808 | 0.015772 | -0.01267 | 0.023862 | -0.005565 | 0.022888 | 0.013733 | -0.013733 | -0.33417 | 0.28381 | -0.52185 | -0.70953 | -0.054932 | -0.20142 | -0.14648 | 0.12817 | 0.059509 | -0.62714 | -0.68665 | 0.004577 | -0.18311 | -122.4014 | 0.54016 | 0.19226 | 0.37537 | -122.6624 | -0.10071 | -0.16022 | -122.5571 | 0.4715 | 0.37994 | 0.54016 | -122.6257 | 0.81024 | 0.54932 | 0.5127 | -123.3948 | 0.6546 | 0.58594 | 0.32501 | -123.3719
4634.0156 | 123.1979 | -0.50354 | 122.6761 | 0.14481 | 0.017062 | 0.0039498 | 0.018179 | 0.026318 | 0.0016321 | -0.0062229 | 0.17532 | -0.00079476 | 0.016199 | -0.010747 | 0.026212 | -0.0074876 | 0.022888 | -0.018311 | -0.009155 | -0.35248 | 0.31128 | -0.51727 | -0.70038 | 0 | -0.21057 | -0.10986 | 0.07782 | 0.022888 | -0.60425 | -0.63629 | -0.013733 | -0.19684 | -122.3648 | 0.48523 | 0.15106 | 0.3479 | -122.6532 | -0.10071 | -0.13275 | -122.5983 | 0.50354 | 0.39368 | 0.52643 | -122.6532 | 0.81482 | 0.52643 | 0.49438 | -123.3765 | 0.58136 | 0.52643 | 0.29297 | -123.3124
4635.0156 | 123.2254 | -0.48065 | 122.6349 | 0.18295 | 0.017703 | 0.0041634 | 0.017539 | 0.028027 | 0.0024865 | -0.0083591 | 0.16769 | -0.0042126 | 0.013635 | -0.0098929 | 0.025998 | -0.0053512 | 0.09613 | 0.10071 | 0.068665 | -0.29297 | 0.25635 | -0.50354 | -0.68665 | 0.054932 | -0.13275 | -0.054932 | 0.045776 | 0.013733 | -0.59509 | -0.60425 | -0.022888 | -0.20599 | -122.3785 | 0.58136 | 0.18768 | 0.39368 | -122.5388 | -0.11444 | -0.1236 | -122.5891 | 0.53558 | 0.42572 | 0.54932 | -122.6212 | 0.737 | 0.57678 | 0.54932 | -123.3215 | 0.52643 | 0.49439 | 0.3479 | -123.2391
4636.0156 | 123.1934 | -0.49896 | 122.6578 | 0.15244 | 0.018344 | 0.0030954 | 0.016684 | 0.029736 | 0.0029137 | -0.0066501 | 0.16006 | -0.0016492 | 0.012354 | -0.010961 | 0.026639 | -0.0068466 | 0.018311 | -0.009155 | 0.004578 | -0.35248 | 0.30212 | -0.52185 | -0.71411 | 0 | -0.21973 | -0.11902 | 0.091553 | 0.036621 | -0.61798 | -0.65918 | -0.022889 | -0.21515 | -122.3557 | 0.48981 | 0.14648 | 0.36163 | -122.6395 | -0.11902 | -0.16022 | -122.5662 | 0.49896 | 0.37994 | 0.54016 | -122.6212 | 0.80109 | 0.51727 | 0.50354 | -123.3719 | 0.59052 | 0.53558 | 0.27924 | -123.317
4637.0156 | 123.1705 | -0.49439 | 122.6715 | -0.10696 | 0.011508 | 0.0054452 | 0.015616 | 0.023541 | -0.0052039 | -0.011991 | 0.0074766 | -0.0054944 | 0.01214 | -0.010106 | 0.024716 | -0.0034286 | 0.004578 | 0.054932 | 0.036621 | -0.32044 | 0.27924 | -0.51727 | -0.69122 | 0 | -0.15564 | -0.059509 | 0.073242 | 0.027466 | -0.60425 | -0.61798 | -0.022888 | -0.19684 | -122.3923 | 0.54932 | 0.17395 | 0.37079 | -122.6669 | -0.10986 | -0.1236 | -122.5983 | 0.49439 | 0.43488 | 0.55847 | -122.644 | 0.77362 | 0.49896 | 0.53101 | -123.3627 | 0.56763 | 0.52185 | 0.33875 | -123.2895
4638.0312 | 123.111 | -0.53101 | 122.6761 | -0.29007 | 0.014285 | 0.0054452 | 0.016898 | 0.029736 | 0.00056395 | -0.0085727 | -0.20615 | -0.0035718 | 0.017694 | -0.010106 | 0.023434 | -0.003856 | -0.013733 | -0.022888 | -0.027466 | -0.36621 | 0.32501 | -0.54016 | -0.72784 | -0.064087 | -0.21057 | -0.15106 | 0.10071 | 0.059509 | -0.65002 | -0.66834 | -0.009155 | -0.19684 | -122.3511 | 0.50812 | 0.16479 | 0.36163 | -122.6898 | -0.11902 | -0.13733 | -122.5754 | 0.46692 | 0.37994 | 0.51727 | -122.6166 | 0.85602 | 0.51727 | 0.50354 | -123.4039 | 0.63171 | 0.59052 | 0.32043 | -123.3444
4639.0156 | 123.1979 | -0.48523 | 122.6624 | 0.31265 | 0.011722 | 0.0045908 | 0.014761 | 0.0276 | -0.0017859 | -0.0081455 | 0.18295 | -0.0031446 | 0.012567 | -0.011388 | 0.022794 | -0.0051376 | 0.07782 | 0.10071 | 0.054932 | -0.3067 | 0.24719 | -0.48981 | -0.67749 | 0.027466 | -0.16022 | -0.059509 | 0.073242 | 0.013733 | -0.59509 | -0.62714 | -0.004578 | -0.19226 | -122.4152 | 0.58594 | 0.17853 | 0.37079 | -122.5845 | -0.10986 | -0.14191 | -122.5891 | 0.5127 | 0.42572 | 0.56763 | -122.6486 | 0.73242 | 0.56305 | 0.54016 | -123.3398 | 0.55847 | 0.49896 | 0.32501 | -123.2895
4640.0156 | 123.2529 | -0.48981 | 122.6532 | 0.19058 | 0.017062 | 0.0075814 | 0.015402 | 0.025464 | 0.00035035 | -0.0070773 | 0.17532 | -0.00229 | 0.015131 | -0.011175 | 0.026852 | -0.0064194 | 0.068665 | 0.10071 | 0.082397 | -0.28839 | 0.27924 | -0.48981 | -0.67291 | 0.059509 | -0.12817 | -0.068665 | 0.073242 | 0.009155 | -0.59052 | -0.62714 | 0 | -0.18311 | -122.374 | 0.59052 | 0.20142 | 0.38452 | -122.5845 | -0.10071 | -0.13733 | -122.58 | 0.54932 | 0.42114 | 0.55847 | -122.644 | 0.76904 | 0.55847 | 0.5722 | -123.3261 | 0.56305 | 0.49896 | 0.36163 | -123.2803
4641.0156 | 123.1796 | -0.49896 | 122.6486 | 0.19058 | 0.011508 | 0.0062998 | 0.014975 | 0.026318 | -0.0017859 | -0.0096409 | -0.061188 | -0.0044264 | 0.010004 | -0.01032 | 0.023434 | -0.0068466 | 0.018311 | 0.059509 | 0.045776 | -0.32959 | 0.2655 | -0.5127 | -0.69122 | 0.013733 | -0.17395 | -0.054932 | 0.082397 | 0.009155 | -0.60425 | -0.62714 | -0.013733 | -0.19226 | -122.3831 | 0.55847 | 0.16937 | 0.36163 | -122.6303 | -0.10529 | -0.12817 | -122.5662 | 0.5127 | 0.44403 | 0.5722 | -122.6395 | 0.76446 | 0.51727 | 0.54474 | -123.3398 | 0.58136 | 0.50812 | 0.32501 | -123.2758
4642.0156 | 123.2483 | -0.48065 | 122.6669 | 0.21347 | 0.014926 | 0.0056588 | 0.015616 | 0.025464 | 0.0039819 | -0.0075047 | 0.33554 | -0.0033582 | 0.013422 | -0.0088247 | 0.025998 | -0.006633 | 0.068665 | 0.07782 | 0.032043 | -0.32501 | 0.27924 | -0.50354 | -0.68665 | 0.054932 | -0.13275 | -0.068665 | 0.068665 | 0.013733 | -0.60425 | -0.59967 | -0.022888 | -0.20599 | -122.3877 | 0.55847 | 0.15564 | 0.36163 | -122.5983 | -0.1236 | -0.11902 | -122.5983 | 0.53558 | 0.41199 | 0.53101 | -122.6532 | 0.75989 | 0.54932 | 0.5127 | -123.3536 | 0.54932 | 0.49439 | 0.3479 | -123.2666
4643.0156 | 123.2574 | -0.49896 | 122.6578 | -0.068817 | 0.011935 | 0.005018 | 0.013266 | 0.027173 | -0.0026405 | -0.010495 | -0.099335 | -0.0050672 | 0.01214 | -0.012029 | 0.023007 | -0.0062058 | 0.086975 | 0.14648 | 0.10986 | -0.28381 | 0.26093 | -0.48523 | -0.70038 | 0.045776 | -0.07782 | -0.013733 | 0.073242 | -0.009155 | -0.59967 | -0.62714 | 0.013733 | -0.20142 | -122.3969 | 0.64545 | 0.21515 | 0.41656 | -122.5708 | -0.10071 | -0.12817 | -122.5845 | 0.54474 | 0.48523 | 0.6134 | -122.6669 | 0.75989 | 0.58594 | 0.60883 | -123.3582 | 0.5722 | 0.48981 | 0.42114 | -123.2849
4644.0156 | 123.2758 | -0.48981 | 122.6669 | 0.20584 | 0.018344 | 0.003309 | 0.016257 | 0.025464 | 0.0041955 | -0.0064365 | 0.12955 | -0.0035718 | 0.014276 | -0.01032 | 0.024289 | -0.0059922 | 0.091553 | 0.068665 | 0.086975 | -0.27924 | 0.24719 | -0.49439 | -0.67749 | 0.068665 | -0.12817 | -0.050354 | 0.064087 | -0.013733 | -0.60883 | -0.6134 | -0.004578 | -0.18768 | -122.4197 | 0.55847 | 0.21057 | 0.39825 | -122.5754 | -0.11902 | -0.1236 | -122.6028 | 0.55847 | 0.43945 | 0.56305 | -122.6807 | 0.737 | 0.58136 | 0.57678 | -123.3444 | 0.55389 | 0.47607 | 0.36163 | -123.2803
4645.0156 | 123.2437 | -0.48981 | 122.699 | 0.099029 | 0.012362 | 0.005018 | 0.016257 | 0.025464 | -0.0024269 | -0.011991 | 0.053253 | -0.0061352 | 0.012995 | -0.010534 | 0.022794 | -0.0042832 | 0.004578 | 0.07782 | 0.050354 | -0.32501 | 0.27924 | -0.49896 | -0.69122 | 0.004578 | -0.15564 | -0.045776 | 0.086975 | -0.004578 | -0.6134 | -0.64545 | -0.009155 | -0.20142 | -122.4197 | 0.56763 | 0.16479 | 0.36621 | -122.6944 | -0.1236 | -0.15564 | -122.612 | 0.49439 | 0.44403 | 0.59967 | -122.7036 | 0.76904 | 0.49439 | 0.54016 | -123.3902 | 0.57678 | 0.48523 | 0.33417 | -123.3444
4646.0156 | 123.2208 | -0.48065 | 122.6532 | 0.14481 | 0.010867 | 0.0041634 | 0.014548 | 0.025037 | -0.00071785 | -0.010495 | 0.030365 | -0.0044264 | 0.012781 | -0.011175 | 0.023007 | -0.006633 | 0.050354 | 0.082397 | 0.050354 | -0.32959 | 0.27008 | -0.51727 | -0.68207 | 0.004578 | -0.16022 | -0.082397 | 0.059509 | 0.004578 | -0.61798 | -0.63171 | -0.036621 | -0.20142 | -122.3831 | 0.56305 | 0.15106 | 0.35248 | -122.6028 | -0.13733 | -0.15106 | -122.5937 | 0.48523 | 0.39826 | 0.54932 | -122.6486 | 0.75073 | 0.53101 | 0.53101 | -123.3353 | 0.54016 | 0.48523 | 0.32044 | -123.2849
4647.0156 | 123.2162 | -0.48065 | 122.6669 | 0.060882 | 0.010653 | 0.0041634 | 0.015189 | 0.028882 | 0.00056395 | -0.0087863 | 0.045624 | -0.0044264 | 0.012567 | -0.01502 | 0.023434 | -0.0042832 | 0.022888 | 0.059509 | 0.045776 | -0.32044 | 0.27008 | -0.49896 | -0.68665 | 0.004578 | -0.16479 | -0.045776 | 0.086975 | 0.027466 | -0.6134 | -0.61798 | -0.01831 | -0.20599 | -122.3969 | 0.54016 | 0.16022 | 0.36621 | -122.644 | -0.13275 | -0.13733 | -122.58 | 0.48523 | 0.43488 | 0.5722 | -122.6395 | 0.75073 | 0.50354 | 0.52643 | -123.3536 | 0.56763 | 0.50812 | 0.31586 | -123.2849
4648.125 | 123.1979 | -0.50354 | 122.6578 | -0.14511 | 0.015994 | 0.0071542 | 0.016684 | 0.024182 | -0.00029045 | -0.010068 | -0.34348 | -0.006349 | 0.016199 | -0.011388 | 0.025143 | -0.0074876 | 0.073242 | 0.09613 | 0.059509 | -0.28381 | 0.2655 | -0.5127 | -0.70496 | 0.013733 | -0.14648 | -0.07782 | 0.082397 | 0.022888 | -0.60883 | -0.61798 | -0.009155 | -0.20142 | -122.3923 | 0.59967 | 0.21973 | 0.42114 | -122.5845 | -0.10529 | -0.11444 | -122.5754 | 0.51727 | 0.42572 | 0.54016 | -122.6349 | 0.76904 | 0.57678 | 0.56305 | -123.3627 | 0.58594 | 0.52643 | 0.35706 | -123.2758
4649.125 | 123.2025 | -0.50812 | 122.6852 | -0.2977 | 0.0091581 | 0.0065134 | 0.014334 | 0.02525 | -0.0022131 | -0.0087863 | -0.17563 | -0.0054944 | 0.011499 | -0.010961 | 0.023648 | -0.0074876 | 0.068665 | 0.11902 | 0.068665 | -0.28381 | 0.27924 | -0.49896 | -0.67749 | -0.004578 | -0.13733 | -0.091553 | 0.082397 | 0.018311 | -0.6134 | -0.62256 | 0.009156 | -0.16937 | -122.406 | 0.62714 | 0.2243 | 0.39368 | -122.6166 | -0.10529 | -0.11444 | -122.6028 | 0.50354 | 0.41656 | 0.53101 | -122.6669 | 0.78735 | 0.57678 | 0.57678 | -123.3627 | 0.59051 | 0.52643 | 0.37079 | -123.3078
4650.5625 | 123.111 | -0.52643 | 122.7127 | 0.022736 | 0.023898 | 0.0062998 | 0.014975 | 0.028027 | 0.0061181 | -0.0070773 | -0.038299 | -0.0031446 | 0.018549 | -0.011388 | 0.029202 | -0.0059922 | 0 | -0.032043 | -0.059509 | -0.37079 | 0.3067 | -0.54016 | -0.72327 | -0.068665 | -0.27924 | -0.20599 | 0.10986 | 0.050354 | -0.61798 | -0.66376 | -0.013733 | -0.19684 | -122.406 | 0.49439 | 0.15564 | 0.35248 | -122.7127 | -0.091553 | -0.13733 | -122.6028 | 0.45776 | 0.32043 | 0.45776 | -122.6624 | 0.83313 | 0.52643 | 0.46692 | -123.436 | 0.63629 | 0.57678 | 0.24719 | -123.3765
4651.8438 | 123.175 | -0.5127 | 122.6807 | -0.045929 | 0.018558 | 0.0037362 | 0.016684 | 0.027386 | 0.0046227 | -0.0068637 | -0.11459 | -0.00229 | 0.014063 | -0.010106 | 0.028134 | -0.0072738 | 0.050354 | 0.036621 | -0.022888 | -0.32959 | 0.29297 | -0.53558 | -0.6958 | -0.004578 | -0.21973 | -0.17395 | 0.09613 | 0.036621 | -0.62714 | -0.65918 | -0.022888 | -0.18311 | -122.3877 | 0.54932 | 0.18311 | 0.36621 | -122.6303 | -0.11444 | -0.14648 | -122.5845 | 0.50812 | 0.33875 | 0.48523 | -122.644 | 0.80566 | 0.56305 | 0.48981 | -123.3765 | 0.60882 | 0.54932 | 0.29297 | -123.3398
4652.6719 | 123.1567 | -0.53101 | 122.7036 | -0.03067 | 0.018771 | 0.0041634 | 0.017752 | 0.025464 | 0.0033411 | -0.0060093 | 0.33554 | -0.0035718 | 0.01449 | -0.010961 | 0.02728 | -0.0044968 | -0.032043 | -0.07782 | -0.07782 | -0.36621 | 0.30212 | -0.54016 | -0.72327 | -0.054932 | -0.25635 | -0.17853 | 0.09613 | 0.045776 | -0.64087 | -0.67291 | -0.009155 | -0.19226 | -122.4014 | 0.45319 | 0.16479 | 0.35706 | -122.7356 | -0.10986 | -0.14191 | -122.6074 | 0.47607 | 0.35248 | 0.49438 | -122.6578 | 0.83313 | 0.49896 | 0.45319 | -123.4268 | 0.62714 | 0.57678 | 0.27466 | -123.3765
4654.6562 | 123.2208 | -0.50812 | 122.6715 | -0.00015269 | 0.010653 | 0.0045908 | 0.015616 | 0.0276 | -0.0054175 | -0.010709 | 0.037995 | -0.0044264 | 0.012995 | -0.010534 | 0.021298 | -0.0017196 | -0.004578 | 0.064087 | 0.054932 | -0.31586 | 0.2655 | -0.48981 | -0.6958 | -0.013733 | -0.16022 | -0.054932 | 0.073242 | 0.004578 | -0.6134 | -0.63629 | 0.018311 | -0.18768 | -122.406 | 0.5722 | 0.19226 | 0.37994 | -122.6761 | -0.10529 | -0.12817 | -122.5983 | 0.49438 | 0.45319 | 0.58136 | -122.6669 | 0.77362 | 0.50354 | 0.56305 | -123.3673 | 0.58136 | 0.5127 | 0.3479 | -123.3078
4655.9219 | 123.1934 | -0.51727 | 122.6944 | -0.22903 | 0.019839 | 0.0043772 | 0.017111 | 0.026318 | 0.0020593 | -0.0075047 | -0.26718 | -0.0025038 | 0.015344 | -0.011602 | 0.025784 | -0.0085556 | -0.018311 | -0.009155 | -0.032043 | -0.3479 | 0.29755 | -0.53558 | -0.71869 | -0.045776 | -0.17853 | -0.15106 | 0.09613 | 0.050354 | -0.62256 | -0.64545 | -0.01831 | -0.20142 | -122.3969 | 0.50812 | 0.16937 | 0.37079 | -122.7127 | -0.10529 | -0.12817 | -122.5983 | 0.4715 | 0.36621 | 0.49438 | -122.644 | 0.81482 | 0.49896 | 0.48523 | -123.4131 | 0.6134 | 0.56763 | 0.33874 | -123.3398
4656.5469 | 123.2758 | -0.49439 | 122.6624 | -0.03067 | 0.010226 | 0.0052316 | 0.013266 | 0.027814 | -0.0060585 | -0.011136 | -0.091705 | -0.0065626 | 0.012781 | -0.012029 | 0.021939 | -0.003856 | 0.032043 | 0.10529 | 0.091553 | -0.2655 | 0.25635 | -0.50812 | -0.69122 | 0.041199 | -0.07782 | -0.004578 | 0.064087 | 0.009155 | -0.60883 | -0.64087 | -0.013733 | -0.19684 | -122.406 | 0.59967 | 0.22888 | 0.42572 | -122.6303 | -0.11444 | -0.14648 | -122.5983 | 0.53558 | 0.48981 | 0.63629 | -122.6532 | 0.75073 | 0.52643 | 0.58594 | -123.3536 | 0.55847 | 0.50354 | 0.41657 | -123.3032
4660.6719 | 123.2254 | -0.50354 | 122.7036 | 0.16769 | 0.019839 | 0.0048044 | 0.015189 | 0.027386 | 0.0033411 | -0.0066501 | 0.21347 | -0.003999 | 0.015344 | -0.0088247 | 0.025998 | -0.0059922 | 0.013733 | -0.013733 | 0.004578 | -0.34332 | 0.28381 | -0.52643 | -0.70496 | 0.013733 | -0.17395 | -0.086975 | 0.07782 | 0.018311 | -0.6134 | -0.64545 | -0.022888 | -0.20142 | -122.4197 | 0.48981 | 0.16022 | 0.36163 | -122.6898 | -0.10986 | -0.14191 | -122.6257 | 0.51727 | 0.41656 | 0.55847 | -122.6852 | 0.78735 | 0.51727 | 0.50812 | -123.4085 | 0.58136 | 0.52185 | 0.32959 | -123.349
4661.6875 | 123.1659 | -0.53101 | 122.7081 | 0.17532 | 0.02048 | 0.005018 | 0.016684 | 0.025677 | 0.0024865 | -0.0094273 | 0.12192 | -0.0048536 | 0.017481 | -0.011602 | 0.027066 | -0.0072738 | -0.022888 | -0.022888 | -0.054932 | -0.35706 | 0.32044 | -0.51727 | -0.72327 | -0.045776 | -0.26093 | -0.15106 | 0.10529 | 0.036621 | -0.62714 | -0.66834 | 0.013733 | -0.19226 | -122.3877 | 0.50812 | 0.17395 | 0.36621 | -122.731 | -0.09613 | -0.13733 | -122.6028 | 0.48523 | 0.37994 | 0.51727 | -122.6715 | 0.85144 | 0.50812 | 0.47607 | -123.4314 | 0.63629 | 0.56763 | 0.27008 | -123.3765
4662.2656 | 123.1567 | -0.52185 | 122.699 | -0.19852 | 0.011508 | 0.005018 | 0.016684 | 0.026746 | -0.0019995 | -0.0092137 | -0.12222 | -0.003999 | 0.011499 | -0.011388 | 0.023648 | -0.0034286 | 0.004578 | 0.064087 | 0.032043 | -0.31586 | 0.2655 | -0.5127 | -0.6958 | -0.045776 | -0.16022 | -0.10986 | 0.10986 | 0.036621 | -0.62714 | -0.65002 | 0.009156 | -0.17395 | -122.4335 | 0.58594 | 0.20599 | 0.37994 | -122.6944 | -0.10529 | -0.12817 | -122.5891 | 0.47607 | 0.41199 | 0.54016 | -122.6624 | 0.78735 | 0.52643 | 0.55389 | -123.3948 | 0.63171 | 0.55847 | 0.36163 | -123.349
4663.0156 | 123.2117 | -0.49439 | 122.6852 | 0.083771 | 0.011935 | 0.0071542 | 0.015616 | 0.024609 | -0.0039221 | -0.010709 | -0.053558 | -0.00464 | 0.012354 | -0.010534 | 0.023648 | -0.0025742 | -0.004578 | 0.064087 | 0.032043 | -0.32044 | 0.27466 | -0.48523 | -0.67749 | -0.013733 | -0.14648 | -0.050354 | 0.07782 | 0.018311 | -0.62256 | -0.64545 | 0.009156 | -0.18311 | -122.4106 | 0.55847 | 0.17395 | 0.35706 | -122.6898 | -0.12817 | -0.15106 | -122.6074 | 0.48065 | 0.44403 | 0.59509 | -122.6669 | 0.76904 | 0.48981 | 0.52643 | -123.3627 | 0.57221 | 0.5127 | 0.3479 | -123.3307
4664.0156 | 123.23 | -0.48981 | 122.7036 | -0.068817 | 0.010867 | 0.0065134 | 0.017111 | 0.024396 | -0.0058447 | -0.010922 | -0.015411 | -0.0050672 | 0.014276 | -0.01267 | 0.021939 | -0.0059922 | -0.009155 | 0.050354 | 0.059509 | -0.31128 | 0.2655 | -0.49439 | -0.69122 | 0.027466 | -0.14648 | -0.032043 | 0.073242 | 0.013733 | -0.59967 | -0.6134 | -0.004578 | -0.20142 | -122.438 | 0.54016 | 0.17853 | 0.37994 | -122.7127 | -0.10986 | -0.1236 | -122.6303 | 0.51727 | 0.45776 | 0.58136 | -122.6898 | 0.75531 | 0.48065 | 0.54932 | -123.3948 | 0.56305 | 0.50354 | 0.34332 | -123.317
4665.0312 | 123.1796 | -0.50812 | 122.7127 | -0.19852 | 0.018344 | 0.00095922 | 0.020102 | 0.026105 | 0.0046227 | -0.0066501 | -0.22903 | -0.002931 | 0.018549 | -0.010534 | 0.025784 | -0.0098374 | 0.054932 | 0.050354 | -0.013733 | -0.32044 | 0.3067 | -0.53558 | -0.70496 | 0 | -0.19226 | -0.14191 | 0.09613 | 0.036621 | -0.61798 | -0.65002 | -0.027465 | -0.19684 | -122.406 | 0.55847 | 0.18768 | 0.38452 | -122.6578 | -0.10986 | -0.14191 | -122.6166 | 0.50812 | 0.36621 | 0.50812 | -122.6761 | 0.81482 | 0.56305 | 0.49438 | -123.4177 | 0.60425 | 0.54474 | 0.31586 | -123.3627
4666.0156 | 123.262 | -0.49439 | 122.7081 | -0.15274 | 0.0087307 | 0.003309 | 0.01647 | 0.026318 | -0.0030677 | -0.0096409 | -0.23666 | -0.0054944 | 0.012995 | -0.010106 | 0.021725 | -0.0068466 | 0.032043 | 0.15106 | 0.082397 | -0.27924 | 0.25635 | -0.48981 | -0.66834 | 0.041199 | -0.073242 | -0.027466 | 0.059509 | 0 | -0.59967 | -0.62256 | 0.004578 | -0.17395 | -122.4518 | 0.64545 | 0.21515 | 0.3891 | -122.6761 | -0.10529 | -0.12817 | -122.6486 | 0.53558 | 0.46692 | 0.59509 | -122.7081 | 0.75073 | 0.52643 | 0.57678 | -123.3765 | 0.55389 | 0.49439 | 0.42114 | -123.3307
4667.0156 | 123.2849 | -0.49439 | 122.6852 | -0.2977 | 0.011081 | 0.0056588 | 0.014548 | 0.026532 | -0.0024269 | -0.0077183 | -0.15274 | -0.0050672 | 0.013849 | -0.0098929 | 0.024716 | -0.0064194 | 0.064087 | 0.16022 | 0.09613 | -0.27008 | 0.27924 | -0.5127 | -0.68207 | 0.050354 | -0.07782 | -0.032043 | 0.045776 | 0.013733 | -0.59509 | -0.62714 | -0.01831 | -0.18768 | -122.406 | 0.6546 | 0.2243 | 0.41199 | -122.6212 | -0.10071 | -0.13275 | -122.6395 | 0.54474 | 0.46234 | 0.59509 | -122.6715 | 0.77362 | 0.55847 | 0.59052 | -123.3673 | 0.54016 | 0.50812 | 0.41657 | -123.3124
4668.0156 | 123.2712 | -0.48981 | 122.6715 | -0.0077822 | 0.01044 | 0.0052316 | 0.016257 | 0.028668 | -0.0028541 | -0.0092137 | -0.023041 | -0.0067762 | 0.015985 | -0.012243 | 0.022153 | -0.0062058 | -0.004578 | 0.10529 | 0.064087 | -0.3067 | 0.2655 | -0.50354 | -0.69122 | 0.022888 | -0.14191 | -0.032043 | 0.068665 | 0.009155 | -0.6134 | -0.64087 | -0.013733 | -0.20142 | -122.406 | 0.59509 | 0.18311 | 0.38452 | -122.6761 | -0.1236 | -0.15106 | -122.6028 | 0.5127 | 0.45776 | 0.60883 | -122.6624 | 0.75531 | 0.48523 | 0.55389 | -123.3627 | 0.55847 | 0.49896 | 0.3479 | -123.3124
4669.0156 | 123.1796 | -0.50354 | 122.7173 | -0.19089 | 0.013003 | 0.0043772 | 0.017539 | 0.025464 | -0.00093145 | -0.0087863 | -0.26718 | -0.0044264 | 0.011926 | -0.01267 | 0.023434 | -0.0072738 | 0.018311 | 0.1236 | 0.041199 | -0.28839 | 0.26093 | -0.50812 | -0.70038 | -0.009155 | -0.15106 | -0.082397 | 0.073242 | 0.022888 | -0.61798 | -0.63171 | -0.004578 | -0.19684 | -122.4564 | 0.62714 | 0.21515 | 0.41199 | -122.699 | -0.11444 | -0.12817 | -122.644 | 0.49438 | 0.42114 | 0.54932 | -122.6944 | 0.76446 | 0.52185 | 0.54474 | -123.4177 | 0.57678 | 0.52643 | 0.35248 | -123.349
4670.0312 | 123.2117 | -0.48523 | 122.6944 | 0.045624 | 0.013644 | 0.0048044 | 0.012198 | 0.0276 | -0.0032813 | -0.0094273 | 0.060883 | -0.0054944 | 0.01214 | -0.013311 | 0.025357 | -0.0040696 | -0.013733 | 0.054932 | 0.027466 | -0.32044 | 0.26093 | -0.49439 | -0.67291 | 0.013733 | -0.16937 | -0.059509 | 0.082397 | 0.013733 | -0.6134 | -0.64087 | -0.009156 | -0.18768 | -122.4335 | 0.54016 | 0.16479 | 0.35248 | -122.7081 | -0.12817 | -0.15564 | -122.612 | 0.49896 | 0.42572 | 0.58136 | -122.6807 | 0.74615 | 0.4715 | 0.5127 | -123.3673 | 0.56763 | 0.49896 | 0.31586 | -123.3353
4671.0156 | 123.2437 | -0.4715 | 122.699 | -0.27481 | 0.012149 | 0.0052316 | 0.017325 | 0.027386 | -0.00071785 | -0.0068637 | -0.19852 | -0.0061352 | 0.012781 | -0.012243 | 0.023862 | -0.0053512 | 0.059509 | 0.14191 | 0.07782 | -0.27466 | 0.2655 | -0.49896 | -0.67749 | 0.027466 | -0.10071 | -0.050354 | 0.054932 | 0.013733 | -0.59509 | -0.62256 | -0.027465 | -0.20599 | -122.4335 | 0.6134 | 0.19684 | 0.40283 | -122.6395 | -0.1236 | -0.15106 | -122.644 | 0.49896 | 0.42114 | 0.5722 | -122.6852 | 0.737 | 0.53101 | 0.54932 | -123.3765 | 0.52643 | 0.48523 | 0.37079 | -123.3215
4672.0156 | 123.2895 | -0.48981 | 122.699 | 0.060882 | 0.010867 | 0.0043772 | 0.016257 | 0.023328 | -0.0022131 | -0.011777 | -0.24429 | -0.0069898 | 0.01214 | -0.010534 | 0.023434 | -0.003856 | 0.064087 | 0.17853 | 0.10986 | -0.27466 | 0.26093 | -0.49439 | -0.67291 | 0.059509 | -0.086975 | -0.022888 | 0.082397 | -0.009155 | -0.59509 | -0.61798 | -0.004578 | -0.18311 | -122.4381 | 0.66834 | 0.21515 | 0.39825 | -122.6349 | -0.10529 | -0.12817 | -122.6166 | 0.54932 | 0.46692 | 0.59509 | -122.7081 | 0.75073 | 0.55389 | 0.59967 | -123.3719 | 0.5722 | 0.48065 | 0.40283 | -123.317
4673.0625 | 123.262 | -0.48065 | 122.7173 | 0.053253 | 0.012576 | 0.006086 | 0.016684 | 0.025891 | 0.0033411 | -0.011777 | 0.26688 | -0.0037854 | 0.014704 | -0.0096793 | 0.024075 | -0.0072738 | 0.054932 | 0.12817 | 0.07782 | -0.29755 | 0.24261 | -0.50354 | -0.67291 | 0.054932 | -0.16022 | -0.036621 | 0.059509 | 0 | -0.60883 | -0.6134 | -0.022888 | -0.19226 | -122.4747 | 0.60883 | 0.18311 | 0.37537 | -122.6624 | -0.12817 | -0.13275 | -122.6578 | 0.53558 | 0.44403 | 0.57678 | -122.7173 | 0.72327 | 0.53558 | 0.55847 | -123.3902 | 0.54016 | 0.48065 | 0.32044 | -123.3307
4674.0156 | 123.175 | -0.50812 | 122.7036 | -0.38925 | 0.013003 | 0.0041634 | 0.017111 | 0.023328 | -0.0017859 | -0.010709 | -0.21378 | -0.0027174 | 0.014063 | -0.01032 | 0.021085 | -0.0064194 | 0.009155 | 0.086975 | 0.054932 | -0.30212 | 0.27008 | -0.5127 | -0.68665 | -0.013733 | -0.18768 | -0.12817 | 0.12817 | 0.036621 | -0.62714 | -0.64087 | -0.004577 | -0.17853 | -122.4335 | 0.59509 | 0.20599 | 0.38452 | -122.6944 | -0.11902 | -0.13275 | -122.5754 | 0.49438 | 0.37994 | 0.5127 | -122.6669 | 0.7782 | 0.51727 | 0.56305 | -123.3902 | 0.63629 | 0.54474 | 0.32043 | -123.3444
4675.0156 | 123.2162 | -0.50812 | 122.7219 | 0.19058 | 0.018558 | 0.0058724 | 0.021384 | 0.027173 | 0.0044091 | -0.0092137 | -0.00015237 | -0.0020764 | 0.016199 | -0.010747 | 0.025571 | -0.0074876 | -0.009155 | -0.013733 | -0.050354 | -0.35706 | 0.29297 | -0.51727 | -0.70038 | -0.004578 | -0.22888 | -0.15106 | 0.10071 | 0.036621 | -0.60883 | -0.64087 | -0.009155 | -0.19226 | -122.4289 | 0.49438 | 0.15106 | 0.34332 | -122.731 | -0.10071 | -0.13275 | -122.6212 | 0.50354 | 0.35706 | 0.48981 | -122.6852 | 0.80109 | 0.49896 | 0.45776 | -123.4222 | 0.60883 | 0.54474 | 0.27924 | -123.3627
4676.0156 | 123.2712 | -0.48065 | 122.6807 | -0.168 | 0.011722 | 0.0043772 | 0.014761 | 0.025037 | -0.0024269 | -0.0081455 | -0.14511 | -0.0037854 | 0.011926 | -0.010747 | 0.022794 | -0.0068466 | 0.041199 | 0.17395 | 0.091553 | -0.28839 | 0.26093 | -0.50354 | -0.65918 | 0.054932 | -0.086975 | -0.013733 | 0.082397 | 0.022888 | -0.60883 | -0.63171 | -0.022888 | -0.17853 | -122.4197 | 0.6546 | 0.19226 | 0.37079 | -122.6395 | -0.12817 | -0.15106 | -122.5983 | 0.53558 | 0.46692 | 0.61798 | -122.6578 | 0.74158 | 0.52185 | 0.57221 | -123.3398 | 0.56305 | 0.50354 | 0.39368 | -123.3124
4677.0156 | 123.1796 | -0.52185 | 122.7219 | -0.17563 | 0.014285 | 0.0062998 | 0.01882 | 0.027386 | 0.00013675 | -0.0075047 | -0.44266 | -0.0014356 | 0.015558 | -0.012456 | 0.023434 | -0.005565 | 0.004578 | 0.10986 | 0.027466 | -0.31586 | 0.27466 | -0.53101 | -0.69122 | -0.041199 | -0.20142 | -0.14648 | 0.082397 | 0.032043 | -0.62714 | -0.63171 | -0.009155 | -0.16937 | -122.4472 | 0.63171 | 0.20599 | 0.37537 | -122.7173 | -0.10529 | -0.10986 | -122.6395 | 0.48065 | 0.37537 | 0.48523 | -122.6898 | 0.79651 | 0.52643 | 0.54932 | -123.4131 | 0.60425 | 0.55389 | 0.32043 | -123.3536
4678.0156 | 123.2529 | -0.48065 | 122.699 | -0.22141 | 0.0083035 | 0.0048044 | 0.017539 | 0.0276 | -0.0013587 | -0.010495 | -0.18326 | -0.0031446 | 0.014276 | -0.010961 | 0.025357 | -0.0057786 | 0.022888 | 0.16937 | 0.07782 | -0.27924 | 0.27924 | -0.49896 | -0.66834 | 0.018311 | -0.07782 | -0.054932 | 0.059509 | -0.018311 | -0.59967 | -0.62256 | -0.01831 | -0.18768 | -122.4197 | 0.65003 | 0.20142 | 0.3891 | -122.6761 | -0.11902 | -0.14191 | -122.6395 | 0.49896 | 0.42572 | 0.56763 | -122.7173 | 0.75989 | 0.50354 | 0.55847 | -123.3673 | 0.54016 | 0.46234 | 0.40283 | -123.3215
4679.0156 | 123.1476 | -0.53558 | 122.731 | -0.48843 | 0.014926 | 0.0056588 | 0.016898 | 0.025891 | 0.0016321 | -0.01135 | -0.24429 | -0.003999 | 0.015344 | -0.010961 | 0.024289 | -0.0070602 | -0.059509 | 0 | -0.032043 | -0.36621 | 0.31128 | -0.54016 | -0.70496 | -0.054932 | -0.21515 | -0.16479 | 0.1236 | 0.054932 | -0.62714 | -0.66834 | -0.004578 | -0.16937 | -122.4197 | 0.53558 | 0.16937 | 0.33875 | -122.7905 | -0.091553 | -0.13275 | -122.6074 | 0.48065 | 0.37079 | 0.50354 | -122.6761 | 0.84686 | 0.47607 | 0.50354 | -123.436 | 0.65918 | 0.59052 | 0.32043 | -123.3994
4680.0312 | 123.2437 | -0.48981 | 122.7356 | 0.17532 | 0.017062 | 0.0030954 | 0.016898 | 0.030591 | 0.0020593 | -0.0087863 | 0.076141 | -0.001222 | 0.015558 | -0.011815 | 0.027921 | -0.005565 | 0 | 0.036621 | -0.004578 | -0.33875 | 0.27924 | -0.51727 | -0.6958 | 0.022888 | -0.19684 | -0.082397 | 0.064087 | 0.018311 | -0.6134 | -0.6134 | -0.027466 | -0.20599 | -122.4564 | 0.52643 | 0.15106 | 0.35706 | -122.7356 | -0.1236 | -0.1236 | -122.6715 | 0.5127 | 0.40741 | 0.53101 | -122.7173 | 0.76904 | 0.48981 | 0.48523 | -123.4314 | 0.55389 | 0.50812 | 0.29297 | -123.349
4681.0156 | 123.1705 | -0.51727 | 122.7081 | -0.099335 | 0.019839 | 0.0028818 | 0.018179 | 0.0276 | 0.0048363 | -0.0092137 | -0.19089 | 0.00027344 | 0.017267 | -0.011815 | 0.024716 | -0.0089828 | 0.018311 | 0.064087 | -0.009155 | -0.31586 | 0.30212 | -0.53558 | -0.70496 | 0.004578 | -0.17853 | -0.13733 | 0.086975 | 0.036621 | -0.60883 | -0.6546 | -0.01831 | -0.18768 | -122.406 | 0.58136 | 0.20142 | 0.3891 | -122.6898 | -0.091553 | -0.13733 | -122.6212 | 0.52185 | 0.37994 | 0.51727 | -122.6715 | 0.8194 | 0.53558 | 0.50812 | -123.4131 | 0.60425 | 0.55389 | 0.33874 | -123.3627
4682.0156 | 123.1979 | -0.49439 | 122.7127 | -0.16037 | 0.010226 | 0.006086 | 0.014975 | 0.026105 | -0.0015723 | -0.0077183 | -0.12985 | -0.0033582 | 0.01214 | -0.010534 | 0.023648 | -0.0042832 | 0.018311 | 0.13733 | 0.068665 | -0.27924 | 0.27008 | -0.49896 | -0.69122 | -0.004578 | -0.10071 | -0.068665 | 0.07782 | 0.022888 | -0.60425 | -0.62714 | -0.004577 | -0.19684 | -122.4426 | 0.63171 | 0.21515 | 0.41199 | -122.6944 | -0.10986 | -0.13275 | -122.6349 | 0.48981 | 0.42572 | 0.55847 | -122.6898 | 0.76447 | 0.5127 | 0.56305 | -123.4039 | 0.57221 | 0.51727 | 0.39368 | -123.3398
4683.0156 | 123.1888 | -0.53101 | 122.7493 | -0.39688 | 0.014499 | 0.0030954 | 0.016898 | 0.0276 | -0.00093145 | -0.010068 | -0.068817 | -0.003999 | 0.013208 | -0.010534 | 0.024289 | -0.0044968 | -0.064087 | 0.041199 | -0.018311 | -0.35706 | 0.3067 | -0.54016 | -0.72327 | -0.050354 | -0.2243 | -0.14191 | 0.10986 | 0.032043 | -0.63629 | -0.6546 | -0.009155 | -0.19226 | -122.4426 | 0.5722 | 0.17395 | 0.36621 | -122.8134 | -0.10529 | -0.1236 | -122.6395 | 0.48065 | 0.3891 | 0.5127 | -122.7173 | 0.83771 | 0.46692 | 0.5127 | -123.4726 | 0.64087 | 0.56305 | 0.3067 | -123.4039
4684.0156 | 123.2208 | -0.52185 | 122.731 | -0.21378 | 0.01044 | 0.0041634 | 0.017325 | 0.026105 | -0.0011451 | -0.011777 | -0.10696 | -0.0082716 | 0.01449 | -0.011388 | 0.022366 | -0.0068466 | 0.013733 | 0.13275 | 0.050354 | -0.29297 | 0.27924 | -0.48981 | -0.70496 | -0.009155 | -0.1236 | -0.082397 | 0.073242 | 0.018311 | -0.62714 | -0.63171 | 0.032044 | -0.18311 | -122.4518 | 0.6546 | 0.22888 | 0.41199 | -122.7173 | -0.10529 | -0.10986 | -122.6578 | 0.5127 | 0.43945 | 0.54932 | -122.7127 | 0.80109 | 0.53558 | 0.5722 | -123.436 | 0.59509 | 0.54016 | 0.39825 | -123.3627
4685.0312 | 123.2346 | -0.48523 | 122.6852 | -0.0077822 | 0.013858 | 0.007795 | 0.012412 | 0.026105 | -0.00093145 | -0.0094273 | 0.10666 | -0.0037854 | 0.012995 | -0.011175 | 0.024075 | -0.0044968 | 0.013733 | 0.13733 | 0.064087 | -0.30212 | 0.23804 | -0.49439 | -0.68207 | 0.041199 | -0.16022 | -0.045776 | 0.082397 | -0.004578 | -0.57678 | -0.63629 | -0.009156 | -0.19684 | -122.4472 | 0.62256 | 0.18311 | 0.37994 | -122.6715 | -0.091553 | -0.15106 | -122.6028 | 0.52643 | 0.43945 | 0.59052 | -122.6898 | 0.72327 | 0.49896 | 0.54932 | -123.3673 | 0.56763 | 0.48065 | 0.32501 | -123.3215
4686.0156 | 123.1613 | -0.53101 | 122.7219 | -0.0383 | 0.013858 | 0.0037362 | 0.016898 | 0.0276 | 0.00099115 | -0.0085727 | -0.19852 | -0.0037854 | 0.013208 | -0.0098929 | 0.025784 | -0.0070602 | -0.036621 | 0.041199 | -0.054932 | -0.37537 | 0.3067 | -0.54474 | -0.72784 | -0.07782 | -0.23346 | -0.15106 | 0.10529 | 0.045776 | -0.64545 | -0.67291 | -0.013733 | -0.19684 | -122.4152 | 0.5722 | 0.15564 | 0.35248 | -122.7585 | -0.11444 | -0.14191 | -122.6166 | 0.45319 | 0.37994 | 0.52185 | -122.6761 | 0.83771 | 0.49438 | 0.47607 | -123.4497 | 0.63629 | 0.57678 | 0.29755 | -123.3948
4687.0156 | 123.1842 | -0.52185 | 122.7264 | -0.30533 | 0.018344 | 0.0022408 | 0.018179 | 0.026746 | 0.0033411 | -0.0098545 | -0.24429 | -0.0033582 | 0.01684 | -0.011175 | 0.025784 | -0.0042832 | -0.004578 | 0.041199 | 0 | -0.31128 | 0.3067 | -0.54016 | -0.73242 | -0.032043 | -0.17853 | -0.14648 | 0.086975 | 0.013733 | -0.63171 | -0.65918 | -0.01831 | -0.21057 | -122.4197 | 0.56305 | 0.21057 | 0.42114 | -122.731 | -0.10986 | -0.13733 | -122.6395 | 0.48981 | 0.37537 | 0.5127 | -122.7127 | 0.82855 | 0.51727 | 0.52185 | -123.4589 | 0.60883 | 0.53558 | 0.34332 | -123.3856
4688.0156 | 123.1842 | -0.51727 | 122.7173 | -0.19089 | 0.016635 | 0.0048044 | 0.017539 | 0.030164 | 0.00099115 | -0.0081455 | -0.12985 | -0.0018628 | 0.015344 | -0.011388 | 0.025784 | -0.0059922 | -0.041199 | 0.004578 | -0.059509 | -0.33875 | 0.27924 | -0.53558 | -0.71411 | -0.07782 | -0.20142 | -0.15106 | 0.10529 | 0.036621 | -0.63171 | -0.66834 | -0.01831 | -0.19684 | -122.438 | 0.52185 | 0.17853 | 0.37537 | -122.7585 | -0.11444 | -0.15106 | -122.612 | 0.43945 | 0.36621 | 0.51727 | -122.6807 | 0.79651 | 0.47607 | 0.45776 | -123.4314 | 0.62256 | 0.55389 | 0.31586 | -123.3856
4689.0156 | 123.1842 | -0.54016 | 122.7539 | -0.053558 | 0.020907 | 0.0030954 | 0.01583 | 0.025037 | 0.0029137 | -0.0083591 | 0.045624 | -0.0031446 | 0.016199 | -0.0088247 | 0.026212 | -0.0064194 | 0.004578 | 0.036621 | -0.036621 | -0.34332 | 0.29755 | -0.54016 | -0.72327 | -0.045776 | -0.23346 | -0.16479 | 0.091553 | 0.054932 | -0.62256 | -0.66376 | 0 | -0.18311 | -122.4564 | 0.57678 | 0.19684 | 0.37994 | -122.7493 | -0.082398 | -0.1236 | -122.6624 | 0.49439 | 0.37537 | 0.49896 | -122.699 | 0.83771 | 0.54474 | 0.50354 | -123.4772 | 0.63171 | 0.59509 | 0.3067 | -123.4177
4690.0156 | 123.1201 | -0.53558 | 122.7402 | 0.083771 | 0.014712 | 0.0024544 | 0.01583 | 0.024396 | 0.0037683 | -0.0085727 | 0.068512 | -0.0014356 | 0.013208 | -0.012029 | 0.025143 | -0.004924 | -0.064087 | -0.022888 | -0.07782 | -0.37994 | 0.27924 | -0.54932 | -0.73242 | -0.09613 | -0.28381 | -0.1831 | 0.11444 | 0.027466 | -0.63171 | -0.64087 | -0.013733 | -0.19684 | -122.4609 | 0.5127 | 0.15564 | 0.35248 | -122.8043 | -0.096131 | -0.10529 | -122.6257 | 0.43945 | 0.35248 | 0.45776 | -122.7127 | 0.81482 | 0.4715 | 0.45776 | -123.4726 | 0.65002 | 0.56305 | 0.25177 | -123.381
4691.0156 | 123.1842 | -0.54016 | 122.7539 | -0.27481 | 0.016421 | 0.0024544 | 0.018179 | 0.02525 | -0.00071785 | -0.0077183 | -0.14511 | -0.0025038 | 0.015985 | -0.0090385 | 0.02258 | -0.0062058 | -0.036621 | -0.004578 | -0.027466 | -0.35248 | 0.29755 | -0.54474 | -0.72784 | -0.068665 | -0.20599 | -0.14191 | 0.11444 | 0.054932 | -0.63171 | -0.66376 | -0.004578 | -0.18768 | -122.4564 | 0.53558 | 0.18768 | 0.37537 | -122.7905 | -0.091553 | -0.1236 | -122.6395 | 0.4715 | 0.39825 | 0.52185 | -122.699 | 0.83771 | 0.50354 | 0.5127 | -123.4818 | 0.6546 | 0.59509 | 0.33417 | -123.4177
4692.0156 | 123.1979 | -0.52643 | 122.7402 | -0.21378 | 0.015567 | 0.005018 | 0.018179 | 0.025677 | -0.00029045 | -0.0068637 | -0.26718 | -0.0018628 | 0.015131 | -0.010534 | 0.026425 | -0.0040696 | -0.050354 | 0.009155 | -0.050354 | -0.3479 | 0.29755 | -0.55389 | -0.74158 | -0.07782 | -0.21057 | -0.15106 | 0.10986 | 0.041199 | -0.64087 | -0.66376 | -0.027466 | -0.21515 | -122.4426 | 0.53558 | 0.17853 | 0.39368 | -122.7905 | -0.11444 | -0.13733 | -122.6303 | 0.44861 | 0.37537 | 0.5127 | -122.699 | 0.82397 | 0.47607 | 0.47607 | -123.4818 | 0.63629 | 0.56763 | 0.31586 | -123.4039
4693.0156 | 123.1705 | -0.50812 | 122.7264 | 0.15244 | 0.020267 | 0.0048044 | 0.020316 | 0.026959 | 0.0046227 | -0.0098545 | -0.14511 | -0.003999 | 0.015985 | -0.011175 | 0.025784 | -0.0062058 | -0.018311 | 0.013733 | -0.045776 | -0.35706 | 0.28839 | -0.52185 | -0.72327 | -0.045776 | -0.23804 | -0.16937 | 0.091553 | 0.027466 | -0.63629 | -0.66376 | -0.013733 | -0.21515 | -122.438 | 0.52185 | 0.15106 | 0.36621 | -122.7448 | -0.12817 | -0.15564 | -122.6349 | 0.46234 | 0.33874 | 0.49438 | -122.699 | 0.79651 | 0.48981 | 0.46234 | -123.4497 | 0.59967 | 0.53558 | 0.27008 | -123.3902
4694.0156 | 123.2071 | -0.53101 | 122.731 | -0.12222 | 0.016208 | 0.0058724 | 0.018179 | 0.027386 | 0.00099115 | -0.0075047 | -0.22903 | -0.003999 | 0.013849 | -0.011388 | 0.024503 | -0.003856 | -0.050354 | -0.004578 | -0.050354 | -0.36621 | 0.29297 | -0.56305 | -0.72327 | -0.064087 | -0.20142 | -0.12817 | 0.10071 | 0.041199 | -0.64087 | -0.66834 | -0.032043 | -0.19226 | -122.438 | 0.52643 | 0.16479 | 0.35706 | -122.7814 | -0.10986 | -0.13733 | -122.6303 | 0.46692 | 0.40283 | 0.54016 | -122.6898 | 0.82397 | 0.48065 | 0.48065 | -123.4543 | 0.63171 | 0.5722 | 0.32959 | -123.3994
4695.0156 | 123.175 | -0.54474 | 122.7356 | -0.16037 | 0.020267 | 0.0052316 | 0.018179 | 0.025677 | 0.0012047 | -0.0092137 | 0.0074766 | -0.0027174 | 0.017908 | -0.011175 | 0.025998 | -0.0042832 | -0.004578 | 0.041199 | -0.022888 | -0.34332 | 0.27466 | -0.53558 | -0.70953 | -0.027466 | -0.18768 | -0.16937 | 0.082397 | 0.041199 | -0.64087 | -0.66834 | 0.009156 | -0.1648 | -122.4609 | 0.58594 | 0.20142 | 0.36621 | -122.7402 | -0.09613 | -0.1236 | -122.6532 | 0.51727 | 0.37537 | 0.49896 | -122.6944 | 0.8194 | 0.54016 | 0.52185 | -123.4451 | 0.62714 | 0.58594 | 0.35706 | -123.4039
4696.0156 | 123.23 | -0.53101 | 122.7081 | -0.3511 | 0.018344 | 0.0065134 | 0.018179 | 0.025891 | 0.00013675 | -0.0081455 | -0.15274 | -0.00079476 | 0.014704 | -0.011815 | 0.026425 | -0.0062058 | -0.027466 | 0.050354 | -0.018311 | -0.33875 | 0.28839 | -0.55389 | -0.72327 | -0.032043 | -0.1831 | -0.14648 | 0.091553 | 0.032043 | -0.63629 | -0.66376 | -0.022888 | -0.19226 | -122.4197 | 0.58136 | 0.19226 | 0.38452 | -122.7356 | -0.10529 | -0.13275 | -122.6166 | 0.49896 | 0.38452 | 0.51727 | -122.6761 | 0.8194 | 0.50354 | 0.5127 | -123.4314 | 0.62256 | 0.56305 | 0.3479 | -123.3719
4697.0156 | 123.2208 | -0.54016 | 122.7127 | -0.061188 | 0.018985 | 0.0018136 | 0.016684 | 0.026105 | 0.0016321 | -0.0075047 | -0.30533 | -0.0025038 | 0.013208 | -0.0088247 | 0.025357 | -0.004924 | 0.009155 | 0.059509 | -0.032043 | -0.34332 | 0.30212 | -0.54016 | -0.72327 | -0.045776 | -0.21973 | -0.17395 | 0.091553 | 0.027466 | -0.63171 | -0.66376 | 0 | -0.18311 | -122.4106 | 0.59967 | 0.19684 | 0.37994 | -122.7036 | -0.091553 | -0.1236 | -122.6212 | 0.49439 | 0.36621 | 0.48981 | -122.6852 | 0.84228 | 0.54932 | 0.50812 | -123.436 | 0.63171 | 0.56763 | 0.32043 | -123.3765
4698.0156 | 123.2162 | -0.54932 | 122.7264 | -0.27481 | 0.016635 | 0.006086 | 0.017539 | 0.025891 | 0.0022729 | -0.0075047 | -0.22903 | -0.0020764 | 0.014276 | -0.0083975 | 0.023007 | -0.0047104 | -0.064087 | 0.013733 | -0.041199 | -0.35248 | 0.29297 | -0.54016 | -0.74616 | -0.064087 | -0.19684 | -0.15106 | 0.07782 | 0.036621 | -0.63629 | -0.68207 | 0.009155 | -0.19684 | -122.4335 | 0.56305 | 0.19684 | 0.39368 | -122.7905 | -0.086976 | -0.13275 | -122.6486 | 0.48523 | 0.39825 | 0.53101 | -122.6898 | 0.84228 | 0.48523 | 0.50812 | -123.4726 | 0.62714 | 0.58594 | 0.35248 | -123.4085
4699.0156 | 123.1567 | -0.53101 | 122.7356 | 0.21347 | 0.019412 | 0.005018 | 0.01583 | 0.024609 | 0.0022729 | -0.0083591 | 0.11429 | -0.0027174 | 0.014276 | -0.011602 | 0.026639 | -0.0051376 | -0.054932 | -0.027466 | -0.068665 | -0.37994 | 0.30212 | -0.53558 | -0.72327 | -0.086975 | -0.2655 | -0.19684 | 0.10986 | 0.041199 | -0.6546 | -0.67291 | -0.004577 | -0.19226 | -122.4335 | 0.50354 | 0.15106 | 0.34332 | -122.7905 | -0.1236 | -0.14191 | -122.6257 | 0.44403 | 0.33417 | 0.47607 | -122.6944 | 0.83313 | 0.47607 | 0.46234 | -123.4589 | 0.64087 | 0.5722 | 0.2655 | -123.4085
4700.0156 | 123.1476 | -0.53101 | 122.7402 | -0.053558 | 0.020907 | 0.0045908 | 0.017966 | 0.027173 | -7.6852e-05 | -0.0079319 | -0.045929 | -0.0014356 | 0.015772 | -0.0094657 | 0.025571 | -0.003856 | -0.032043 | -0.018311 | -0.07782 | -0.37994 | 0.29297 | -0.55389 | -0.73242 | -0.086975 | -0.28381 | -0.19684 | 0.09613 | 0.027466 | -0.65002 | -0.68207 | -0.022888 | -0.20142 | -122.4472 | 0.5127 | 0.15106 | 0.35248 | -122.7722 | -0.11902 | -0.15106 | -122.644 | 0.44403 | 0.33417 | 0.48523 | -122.7127 | 0.82397 | 0.49896 | 0.45319 | -123.4726 | 0.62714 | 0.55847 | 0.24719 | -123.4222
4701.0156 | 123.1522 | -0.56305 | 122.7264 | 0.34317 | 0.02048 | 0.0028818 | 0.014548 | 0.024182 | 0.0024865 | -0.0085727 | 0.21347 | -0.0031446 | 0.015344 | -0.0098929 | 0.022794 | -0.0062058 | -0.059509 | -0.054932 | -0.068665 | -0.39368 | 0.28839 | -0.54932 | -0.74616 | -0.10071 | -0.27008 | -0.16937 | 0.073242 | 0.041199 | -0.64087 | -0.66376 | 0.013733 | -0.18311 | -122.438 | 0.50812 | 0.16937 | 0.35248 | -122.7859 | -0.07782 | -0.10071 | -122.6532 | 0.46234 | 0.39368 | 0.49438 | -122.6852 | 0.85144 | 0.50354 | 0.49438 | -123.4726 | 0.63629 | 0.60425 | 0.29297 | -123.3902
4702.0156 | 123.1888 | -0.54474 | 122.699 | -0.31296 | 0.01813 | 0.0041634 | 0.014975 | 0.024182 | 0.0029137 | -0.0096409 | -0.2977 | -0.0016492 | 0.015558 | -0.010534 | 0.025143 | -0.0057786 | 0 | 0.004578 | -0.022888 | -0.33417 | 0.28839 | -0.54016 | -0.73242 | -0.045776 | -0.19684 | -0.14648 | 0.082397 | 0.032043 | -0.64545 | -0.65918 | 0.004578 | -0.18768 | -122.4106 | 0.54932 | 0.21057 | 0.39826 | -122.699 | -0.10071 | -0.11444 | -122.6166 | 0.49896 | 0.39825 | 0.5127 | -122.6669 | 0.83313 | 0.54474 | 0.52185 | -123.4314 | 0.62714 | 0.57678 | 0.3479 | -123.3582
4703.0156 | 123.1476 | -0.54474 | 122.7493 | 0.045624 | 0.021548 | 0.0035226 | 0.014975 | 0.025677 | 0.0018457 | -0.0096409 | 0.030365 | -0.0020764 | 0.015344 | -0.0094657 | 0.02493 | -0.0047104 | -0.032043 | -0.022888 | -0.068665 | -0.37079 | 0.29755 | -0.54474 | -0.71869 | -0.10986 | -0.29297 | -0.2243 | 0.10071 | 0.054932 | -0.65002 | -0.67291 | 0 | -0.17395 | -122.4518 | 0.52185 | 0.17395 | 0.3479 | -122.7814 | -0.10529 | -0.12817 | -122.6486 | 0.43488 | 0.32043 | 0.44861 | -122.6944 | 0.84228 | 0.5127 | 0.47607 | -123.468 | 0.64545 | 0.59967 | 0.25177 | -123.4222
4704.0156 | 123.1842 | -0.53101 | 122.7264 | -0.16037 | 0.018558 | 0.0065134 | 0.019034 | 0.026746 | 0.0020593 | -0.0070773 | -0.061188 | -0.0020764 | 0.017694 | -0.010534 | 0.025571 | -0.0051376 | 0.004578 | 0.045776 | -0.018311 | -0.32501 | 0.28839 | -0.55389 | -0.71411 | -0.041199 | -0.20599 | -0.13733 | 0.082397 | 0.018311 | -0.64087 | -0.66834 | -0.022888 | -0.18311 | -122.438 | 0.57678 | 0.20599 | 0.3891 | -122.7219 | -0.10986 | -0.13733 | -122.644 | 0.48981 | 0.39368 | 0.53101 | -122.7081 | 0.8194 | 0.53558 | 0.5127 | -123.4406 | 0.6134 | 0.54932 | 0.32501 | -123.3948
4705.0156 | 123.2391 | -0.49896 | 122.7173 | 0.022736 | 0.014071 | 0.0086496 | 0.012625 | 0.025464 | -0.0043495 | -0.0094273 | 0.24399 | -0.0050672 | 0.012781 | -0.011602 | 0.02493 | -0.0027878 | 0.004578 | 0.10071 | 0.027466 | -0.32044 | 0.25635 | -0.50812 | -0.70038 | -0.009155 | -0.1831 | -0.068665 | 0.050354 | 0.004578 | -0.6134 | -0.63629 | -0.009156 | -0.20142 | -122.4609 | 0.59967 | 0.17853 | 0.37994 | -122.7127 | -0.11444 | -0.13733 | -122.6669 | 0.48981 | 0.4303 | 0.56763 | -122.7127 | 0.75531 | 0.50354 | 0.52643 | -123.4177 | 0.54932 | 0.50354 | 0.31586 | -123.3536
4706.0156 | 123.1888 | -0.54932 | 122.7264 | 0.12192 | 0.02048 | 0.005018 | 0.016898 | 0.024396 | 0.0022729 | -0.0092137 | 0.14481 | -0.00229 | 0.01684 | -0.010961 | 0.025143 | -0.0051376 | -0.045776 | -0.050354 | -0.054932 | -0.37079 | 0.3067 | -0.53101 | -0.737 | -0.073242 | -0.27924 | -0.17395 | 0.091553 | 0.022888 | -0.65002 | -0.66376 | 0.01831 | -0.18768 | -122.4197 | 0.49896 | 0.17853 | 0.36621 | -122.7722 | -0.10071 | -0.11444 | -122.6349 | 0.47607 | 0.37537 | 0.48981 | -122.7036 | 0.85602 | 0.50354 | 0.49438 | -123.4634 | 0.64087 | 0.5722 | 0.27008 | -123.3902
4707.0156 | 123.1796 | -0.54016 | 122.7127 | 0.15244 | 0.021121 | 0.003309 | 0.019248 | 0.024396 | 0.0022729 | -0.0096409 | 0.0914 | -0.00229 | 0.017694 | -0.013311 | 0.025357 | -0.005565 | -0.036621 | -0.041199 | -0.050354 | -0.38452 | 0.30212 | -0.54932 | -0.71411 | -0.054932 | -0.27924 | -0.16937 | 0.082397 | 0.041199 | -0.63629 | -0.66376 | -0.009155 | -0.17395 | -122.4106 | 0.49896 | 0.15564 | 0.32959 | -122.7493 | -0.096131 | -0.1236 | -122.6303 | 0.48523 | 0.37079 | 0.49438 | -122.6715 | 0.84228 | 0.50354 | 0.48981 | -123.4268 | 0.62256 | 0.58136 | 0.26093 | -123.3765
4708.0156 | 123.1888 | -0.54474 | 122.7356 | 0.22873 | 0.022403 | 0.0048044 | 0.020956 | 0.02525 | 0.0018457 | -0.010068 | -0.19852 | -0.002931 | 0.018549 | -0.0094657 | 0.026852 | -0.0040696 | -0.013733 | -0.018311 | -0.059509 | -0.36163 | 0.27924 | -0.56305 | -0.70953 | -0.068665 | -0.24719 | -0.20142 | 0.073242 | 0.041199 | -0.63629 | -0.66834 | -0.01831 | -0.1648 | -122.4564 | 0.52643 | 0.18311 | 0.3479 | -122.7493 | -0.091553 | -0.1236 | -122.6624 | 0.47607 | 0.34332 | 0.46692 | -122.6944 | 0.82397 | 0.53101 | 0.48523 | -123.4451 | 0.61798 | 0.58594 | 0.29755 | -123.4039
4709.0156 | 123.2986 | -0.50354 | 122.7173 | 0.14481 | 0.018344 | 0.0039498 | 0.01583 | 0.025677 | 0.00013675 | -0.0096409 | 0.28976 | -0.0014356 | 0.016199 | -0.01032 | 0.024503 | -0.0027878 | 0.004578 | 0.013733 | 0 | -0.33875 | 0.27466 | -0.52185 | -0.70038 | -0.004578 | -0.14648 | -0.091553 | 0.050354 | 0.018311 | -0.59052 | -0.64087 | -0.018311 | -0.19684 | -122.4426 | 0.51727 | 0.16479 | 0.36163 | -122.7127 | -0.086975 | -0.13733 | -122.6669 | 0.49896 | 0.41199 | 0.54932 | -122.699 | 0.7782 | 0.50812 | 0.50354 | -123.4177 | 0.55389 | 0.52185 | 0.35706 | -123.3582
4710.0156 | 123.2803 | -0.50354 | 122.6944 | 0.068512 | 0.016849 | 0.0041634 | 0.01647 | 0.026105 | 0.00056395 | -0.0089999 | 0.16769 | -0.0031446 | 0.016413 | -0.0094657 | 0.02493 | -0.0062058 | 0.013733 | 0.013733 | 0.009155 | -0.32501 | 0.27008 | -0.52185 | -0.71411 | 0.022888 | -0.13733 | -0.086975 | 0.059509 | 0.013733 | -0.60425 | -0.64087 | -0.018311 | -0.21057 | -122.4243 | 0.51727 | 0.17853 | 0.3891 | -122.6807 | -0.10071 | -0.13733 | -122.6349 | 0.52643 | 0.41656 | 0.55389 | -122.6807 | 0.77362 | 0.51727 | 0.5127 | -123.4085 | 0.56305 | 0.51727 | 0.36621 | -123.3353
4711.0156 | 123.2208 | -0.50812 | 122.7219 | 0.11429 | 0.018985 | 0.0041634 | 0.014975 | 0.024182 | 0.0018457 | -0.0096409 | 0.26688 | -0.0033582 | 0.015772 | -0.013097 | 0.025571 | -0.003856 | -0.022888 | -0.032043 | -0.054932 | -0.36163 | 0.30212 | -0.54474 | -0.71869 | -0.054932 | -0.24719 | -0.15564 | 0.086975 | 0.013733 | -0.63171 | -0.65002 | -0.036621 | -0.21057 | -122.4197 | 0.47607 | 0.14648 | 0.35706 | -122.7448 | -0.1236 | -0.14191 | -122.6349 | 0.45319 | 0.35248 | 0.49438 | -122.7081 | 0.81024 | 0.48523 | 0.45319 | -123.4406 | 0.59509 | 0.52185 | 0.26093 | -123.3719
4712.0156 | 123.1888 | -0.52643 | 122.7219 | 0.10666 | 0.018558 | 0.0035226 | 0.016898 | 0.027173 | 0.0012047 | -0.0085727 | 0.19058 | -0.0016492 | 0.015985 | -0.0094657 | 0.02493 | -0.0025742 | -0.041199 | -0.059509 | -0.068665 | -0.38452 | 0.27924 | -0.53558 | -0.737 | -0.073242 | -0.28839 | -0.1831 | 0.068665 | 0.041199 | -0.63629 | -0.68207 | -0.009155 | -0.21057 | -122.4426 | 0.46692 | 0.14191 | 0.35248 | -122.7631 | -0.10986 | -0.15564 | -122.6532 | 0.45319 | 0.34332 | 0.49896 | -122.6807 | 0.80566 | 0.48523 | 0.45776 | -123.4589 | 0.59509 | 0.56763 | 0.23804 | -123.4039
4713.0156 | 123.2529 | -0.51727 | 122.7127 | 0.25162 | 0.013644 | 0.006086 | 0.014121 | 0.024396 | -0.0037085 | -0.0089999 | 0.26688 | -0.0042126 | 0.015344 | -0.012029 | 0.023648 | -0.0023606 | 0.009155 | 0.059509 | 0.027466 | -0.35248 | 0.27466 | -0.49439 | -0.6958 | -0.004578 | -0.21515 | -0.07782 | 0.068665 | 0.022888 | -0.6134 | -0.64087 | 0.022888 | -0.17853 | -122.4381 | 0.57678 | 0.16479 | 0.34332 | -122.7036 | -0.09613 | -0.1236 | -122.644 | 0.5127 | 0.43945 | 0.56305 | -122.6898 | 0.79193 | 0.52643 | 0.54474 | -123.4085 | 0.58594 | 0.54016 | 0.30212 | -123.3536
4714.0156 | 123.2986 | -0.49439 | 122.6944 | 0.083771 | 0.016635 | 0.0043772 | 0.019034 | 0.026532 | -0.0026405 | -0.010495 | 0.20584 | -0.003999 | 0.01449 | -0.010961 | 0.023862 | -0.0068466 | 0.064087 | 0.09613 | 0.050354 | -0.29755 | 0.25635 | -0.49896 | -0.6958 | 0.045776 | -0.16479 | -0.068665 | 0.064087 | -0.013733 | -0.60883 | -0.62714 | -0.004577 | -0.20142 | -122.438 | 0.59052 | 0.19684 | 0.39826 | -122.6303 | -0.11444 | -0.13275 | -122.6303 | 0.54016 | 0.42572 | 0.55847 | -122.7081 | 0.75073 | 0.55847 | 0.54474 | -123.3902 | 0.55847 | 0.48065 | 0.32959 | -123.3215
4715.0156 | 123.2758 | -0.48523 | 122.7036 | 0.13718 | 0.011508 | 0.0016 | 0.01647 | 0.024823 | -0.0030677 | -0.0096409 | 0.24399 | -0.0044264 | 0.012567 | -0.01032 | 0.023007 | -0.0042832 | 0.032043 | 0.07782 | 0.045776 | -0.32501 | 0.24719 | -0.50812 | -0.6958 | 0.004578 | -0.19684 | -0.07782 | 0.054932 | 0.018311 | -0.59509 | -0.62714 | -0.022889 | -0.21057 | -122.4564 | 0.56305 | 0.16022 | 0.37079 | -122.6715 | -0.10986 | -0.14191 | -122.6486 | 0.48981 | 0.40741 | 0.54932 | -122.6852 | 0.73242 | 0.51727 | 0.53101 | -123.3994 | 0.54016 | 0.50354 | 0.28839 | -123.3307
4716.0156 | 123.2895 | -0.52643 | 122.699 | 0.25925 | 0.017917 | 0.0058724 | 0.01882 | 0.023328 | 0.0022729 | -0.0098545 | 0.0914 | -0.0042126 | 0.018122 | -0.011815 | 0.025571 | -0.0068466 | 0.004578 | 0.009155 | -0.013733 | -0.35706 | 0.27466 | -0.52185 | -0.70038 | 0.013733 | -0.21057 | -0.10986 | 0.073242 | -0.004578 | -0.62714 | -0.64087 | 0.004577 | -0.17395 | -122.4243 | 0.53558 | 0.16937 | 0.34332 | -122.6944 | -0.10071 | -0.11444 | -122.6257 | 0.54016 | 0.41657 | 0.53101 | -122.7036 | 0.80109 | 0.53101 | 0.5127 | -123.3994 | 0.59967 | 0.52185 | 0.31586 | -123.3398
4717.0156 | 123.262 | -0.49439 | 122.6852 | -0.076447 | 0.011722 | 0.0052316 | 0.014975 | 0.028241 | -0.0041357 | -0.010282 | 0.0914 | -0.0059216 | 0.013422 | -0.012029 | 0.021939 | -0.003856 | -0.018311 | 0.050354 | 0.022888 | -0.31128 | 0.25635 | -0.52185 | -0.6958 | -0.013733 | -0.1831 | -0.073242 | 0.064087 | 0.009155 | -0.59509 | -0.65002 | -0.027466 | -0.20142 | -122.4289 | 0.54474 | 0.18311 | 0.38452 | -122.7036 | -0.10071 | -0.15564 | -122.6212 | 0.48065 | 0.42114 | 0.57678 | -122.6761 | 0.75073 | 0.47607 | 0.51727 | -123.381 | 0.55847 | 0.50354 | 0.31128 | -123.3353
4718.0156 | 123.175 | -0.52185 | 122.7081 | 0.33554 | 0.018985 | 0.0026682 | 0.018607 | 0.029736 | 0.0027001 | -0.0089999 | 0.12955 | -0.0044264 | 0.014704 | -0.0090385 | 0.025143 | -0.0068466 | -0.009155 | -0.013733 | -0.059509 | -0.36163 | 0.29297 | -0.53558 | -0.70496 | -0.022888 | -0.25635 | -0.14191 | 0.091553 | 0.022888 | -0.63629 | -0.6546 | -0.013732 | -0.18311 | -122.4152 | 0.50812 | 0.16022 | 0.34332 | -122.7173 | -0.11444 | -0.13275 | -122.6166 | 0.49896 | 0.37994 | 0.5127 | -122.6852 | 0.81482 | 0.5127 | 0.46234 | -123.4131 | 0.6134 | 0.54474 | 0.2655 | -123.3627
4719.0156 | 123.2712 | -0.49896 | 122.6898 | 0.11429 | 0.010867 | 0.006727 | 0.014761 | 0.025464 | -0.0054175 | -0.0094273 | 0.40421 | -0.0069898 | 0.012995 | -0.011602 | 0.021512 | -0.003856 | 0 | 0.041199 | 0.027466 | -0.32959 | 0.27008 | -0.50354 | -0.68665 | 0 | -0.19684 | -0.064087 | 0.050354 | 0.004578 | -0.63171 | -0.64087 | -0.004578 | -0.18768 | -122.4197 | 0.54016 | 0.16937 | 0.35706 | -122.6898 | -0.13275 | -0.14191 | -122.6395 | 0.49896 | 0.43488 | 0.57678 | -122.6852 | 0.76904 | 0.49896 | 0.52643 | -123.3765 | 0.54932 | 0.50354 | 0.30212 | -123.3307
4720.0156 | 123.262 | -0.50354 | 122.7081 | -0.053558 | 0.010226 | 0.0065134 | 0.015402 | 0.026532 | -0.0043495 | -0.010282 | 0.015106 | -0.0076306 | 0.014917 | -0.011815 | 0.022366 | -0.0057786 | 0.004578 | 0.064087 | 0.022888 | -0.32959 | 0.26093 | -0.50812 | -0.70496 | -0.013733 | -0.19226 | -0.068665 | 0.068665 | 0.027466 | -0.60883 | -0.63171 | -0.004578 | -0.20142 | -122.4472 | 0.56763 | 0.17395 | 0.37537 | -122.7036 | -0.10529 | -0.12817 | -122.6395 | 0.48981 | 0.43488 | 0.56305 | -122.6807 | 0.76446 | 0.50812 | 0.52643 | -123.4131 | 0.5722 | 0.53101 | 0.31128 | -123.3398
4721.0156 | 123.3078 | -0.49439 | 122.6852 | -0.17563 | 0.0097989 | 0.0052316 | 0.017966 | 0.028027 | -0.0011451 | -0.010922 | 0.053253 | -0.0067762 | 0.013635 | -0.010961 | 0.023434 | -0.0057786 | 0.032043 | 0.073242 | 0.045776 | -0.31128 | 0.27008 | -0.52185 | -0.67291 | 0.041199 | -0.14648 | -0.050354 | 0.059509 | -0.013733 | -0.60883 | -0.64087 | -0.027466 | -0.17853 | -122.4152 | 0.56763 | 0.18311 | 0.36163 | -122.6532 | -0.11444 | -0.14648 | -122.6257 | 0.53558 | 0.44403 | 0.59052 | -122.699 | 0.76447 | 0.52643 | 0.54016 | -123.3582 | 0.55389 | 0.48065 | 0.3479 | -123.3261
4722.0156 | 123.3032 | -0.49896 | 122.7036 | 0.076141 | 0.014071 | 0.0056588 | 0.018393 | 0.023755 | -0.0011451 | -0.010922 | -0.00015237 | -0.0059216 | 0.013422 | -0.013738 | 0.023862 | -0.0062058 | 0.018311 | 0.045776 | 0.018311 | -0.31586 | 0.27008 | -0.5127 | -0.70953 | 0 | -0.17853 | -0.07782 | 0.054932 | 0.027466 | -0.62256 | -0.6546 | -0.013733 | -0.21057 | -122.4335 | 0.54474 | 0.18311 | 0.39368 | -122.6852 | -0.1236 | -0.15564 | -122.6486 | 0.49896 | 0.42114 | 0.57678 | -122.6761 | 0.76904 | 0.51727 | 0.51727 | -123.4131 | 0.55389 | 0.52643 | 0.32043 | -123.3582
4723.0156 | 123.3398 | -0.50354 | 122.7081 | -0.091705 | 0.0095853 | 0.0039498 | 0.016684 | 0.026959 | -0.0019995 | -0.011136 | -0.038299 | -0.005708 | 0.013422 | -0.012029 | 0.023007 | -0.0062058 | 0.041199 | 0.10529 | 0.054932 | -0.31586 | 0.2655 | -0.52185 | -0.70953 | 0.036621 | -0.16022 | -0.036621 | 0.050354 | -0.013733 | -0.6134 | -0.64087 | -0.018311 | -0.20599 | -122.4426 | 0.60883 | 0.18768 | 0.39368 | -122.6669 | -0.10986 | -0.13733 | -122.6578 | 0.54016 | 0.46692 | 0.60425 | -122.7219 | 0.76904 | 0.54474 | 0.55847 | -123.4177 | 0.55389 | 0.48981 | 0.34332 | -123.349
4724.0156 | 123.3032 | -0.49439 | 122.6761 | 0.16769 | 0.014926 | 0.0043772 | 0.017111 | 0.026105 | 0.0014185 | -0.0077183 | 0.12955 | -0.0044264 | 0.014276 | -0.01032 | 0.025784 | -0.0072738 | 0.091553 | 0.10529 | 0.050354 | -0.27924 | 0.23346 | -0.5127 | -0.68207 | 0.064087 | -0.16022 | -0.059509 | 0.054932 | -0.009155 | -0.60883 | -0.63171 | -0.01831 | -0.18768 | -122.4426 | 0.59967 | 0.21515 | 0.40283 | -122.5845 | -0.11444 | -0.13733 | -122.6212 | 0.55847 | 0.43488 | 0.5722 | -122.6852 | 0.72784 | 0.58594 | 0.54474 | -123.3582 | 0.54932 | 0.48523 | 0.33417 | -123.3078
4725.0156 | 123.2986 | -0.48981 | 122.699 | -0.20615 | 0.010653 | 0.0056588 | 0.016257 | 0.025677 | -0.0015723 | -0.0098545 | -0.25955 | -0.0042126 | 0.012567 | -0.011175 | 0.021725 | -0.0051376 | 0.045776 | 0.086975 | 0.064087 | -0.32501 | 0.29297 | -0.54016 | -0.70496 | 0.064087 | -0.12817 | -0.041199 | 0.050354 | -0.009155 | -0.60425 | -0.64087 | -0.050354 | -0.21515 | -122.406 | 0.57678 | 0.16479 | 0.37994 | -122.6532 | -0.11444 | -0.15106 | -122.6486 | 0.55389 | 0.44861 | 0.59967 | -122.7081 | 0.78278 | 0.53558 | 0.55389 | -123.4039 | 0.54016 | 0.48065 | 0.36163 | -123.3398
4726.0156 | 123.2574 | -0.50354 | 122.7219 | 0.28213 | 0.015353 | 0.0045908 | 0.016684 | 0.026746 | 0.0018457 | -0.0089999 | 0.16006 | -0.0067762 | 0.015344 | -0.010106 | 0.023648 | -0.0040696 | 0.050354 | 0.086975 | 0.041199 | -0.32959 | 0.24261 | -0.52185 | -0.6958 | 0.013733 | -0.1831 | -0.09613 | 0.064087 | 0.009155 | -0.62256 | -0.64545 | -0.018311 | -0.19226 | -122.4792 | 0.59052 | 0.17395 | 0.36621 | -122.6715 | -0.11902 | -0.14191 | -122.6578 | 0.51727 | 0.40741 | 0.54932 | -122.7127 | 0.74616 | 0.55389 | 0.54474 | -123.4177 | 0.56763 | 0.5127 | 0.32044 | -123.3673
4727.0156 | 123.3124 | -0.49896 | 122.7081 | -0.03067 | 0.010013 | 0.006086 | 0.014334 | 0.023114 | -0.0028541 | -0.010709 | -0.03067 | -0.0050672 | 0.013635 | -0.010106 | 0.023862 | -0.0072738 | 0.059509 | 0.13275 | 0.073242 | -0.28839 | 0.26093 | -0.5127 | -0.69122 | 0.068665 | -0.10071 | -0.013733 | 0.050354 | -0.009155 | -0.61798 | -0.62256 | -0.013733 | -0.19226 | -122.4472 | 0.63171 | 0.21057 | 0.40283 | -122.6486 | -0.11902 | -0.1236 | -122.6578 | 0.56763 | 0.48523 | 0.60883 | -122.7173 | 0.75989 | 0.55847 | 0.5722 | -123.3994 | 0.54932 | 0.48981 | 0.39825 | -123.3307
4728.0156 | 123.2666 | -0.50354 | 122.7219 | 0.015106 | 0.0095853 | 0.0035226 | 0.017539 | 0.026318 | -0.0017859 | -0.0079319 | 0.076141 | -0.0037854 | 0.013849 | -0.011175 | 0.025143 | -0.0077012 | 0.022888 | 0.059509 | 0.022888 | -0.3479 | 0.2655 | -0.52643 | -0.70038 | 0.013733 | -0.1831 | -0.07782 | 0.068665 | -0.009155 | -0.60425 | -0.65918 | -0.022888 | -0.19684 | -122.4564 | 0.56305 | 0.15564 | 0.35248 | -122.699 | -0.10071 | -0.15564 | -122.6532 | 0.51727 | 0.42572 | 0.58136 | -122.731 | 0.76904 | 0.52643 | 0.52643 | -123.4222 | 0.5722 | 0.49438 | 0.32044 | -123.381
4729.0156 | 123.3444 | -0.5127 | 122.7036 | -0.12222 | 0.010867 | 0.0080086 | 0.014121 | 0.0229 | -0.0019995 | -0.0092137 | -0.076446 | -0.0052808 | 0.013849 | -0.012029 | 0.023007 | -0.0072738 | 0.073242 | 0.11902 | 0.07782 | -0.30212 | 0.24719 | -0.50354 | -0.6958 | 0.07782 | -0.09613 | -0.009155 | 0.045776 | -0.018311 | -0.6134 | -0.63171 | 0.009155 | -0.18311 | -122.4564 | 0.63171 | 0.21057 | 0.39368 | -122.6303 | -0.10071 | -0.11902 | -122.6578 | 0.59052 | 0.50354 | 0.62256 | -122.7219 | 0.75989 | 0.58594 | 0.59052 | -123.3994 | 0.55847 | 0.49438 | 0.41657 | -123.3353
4730.0156 | 123.1979 | -0.55847 | 122.7264 | -0.38925 | 0.01578 | 0.0041634 | 0.01583 | 0.026105 | 0.0031273 | -0.010068 | -0.3511 | -0.003999 | 0.015558 | -0.0096793 | 0.024716 | -0.0079148 | -0.018311 | 0.009155 | -0.050354 | -0.39368 | 0.29755 | -0.55389 | -0.75073 | -0.045776 | -0.25177 | -0.17853 | 0.10071 | 0.036621 | -0.67749 | -0.66834 | 0.004578 | -0.19226 | -122.4289 | 0.56763 | 0.16479 | 0.35705 | -122.7448 | -0.11902 | -0.10986 | -122.6257 | 0.5127 | 0.37994 | 0.48981 | -122.6898 | 0.85602 | 0.54016 | 0.50812 | -123.4772 | 0.65918 | 0.59509 | 0.3067 | -123.3948
4731.0156 | 123.3032 | -0.49439 | 122.7264 | -0.19852 | 0.0091581 | 0.0037362 | 0.016043 | 0.026746 | -0.00093145 | -0.010282 | -0.10696 | -0.0035718 | 0.012995 | -0.013097 | 0.025357 | -0.004924 | 0.022888 | 0.14648 | 0.064087 | -0.30212 | 0.25177 | -0.53101 | -0.71411 | 0.054932 | -0.10986 | -0.064087 | 0.054932 | -0.004578 | -0.6134 | -0.65002 | -0.036621 | -0.21973 | -122.4747 | 0.64087 | 0.19226 | 0.41199 | -122.7036 | -0.11902 | -0.15564 | -122.6715 | 0.54932 | 0.4303 | 0.58594 | -122.731 | 0.74616 | 0.51727 | 0.55847 | -123.4406 | 0.54932 | 0.48981 | 0.38452 | -123.3765
4732.0156 | 123.2758 | -0.52643 | 122.7219 | 0.0914 | 0.010867 | 0.0045908 | 0.014975 | 0.026746 | -0.00029045 | -0.0096409 | 0.068512 | -0.0044264 | 0.01449 | -0.012884 | 0.025143 | -0.0064194 | -0.018311 | 0.07782 | 0.041199 | -0.33875 | 0.26093 | -0.5127 | -0.68207 | 0.022888 | -0.19684 | -0.07782 | 0.068665 | -0.004578 | -0.61798 | -0.64087 | 0.013733 | -0.15564 | -122.4609 | 0.60425 | 0.18768 | 0.34332 | -122.7402 | -0.091553 | -0.11444 | -122.6532 | 0.54932 | 0.44861 | 0.56305 | -122.7264 | 0.78735 | 0.50812 | 0.56763 | -123.4039 | 0.59509 | 0.52185 | 0.32959 | -123.3627
4733.0156 | 123.1888 | -0.53101 | 122.7631 | -0.28244 | 0.01514 | 0.0030954 | 0.019248 | 0.028882 | 0.0024865 | -0.010709 | -0.2977 | -0.0050672 | 0.016413 | -0.0098929 | 0.023862 | -0.0057786 | 0.013733 | 0.091553 | 0.004578 | -0.33875 | 0.27466 | -0.55389 | -0.737 | -0.036621 | -0.15564 | -0.16937 | 0.082397 | 0.009155 | -0.62256 | -0.67291 | -0.022888 | -0.20599 | -122.4884 | 0.62256 | 0.19226 | 0.39825 | -122.7493 | -0.091553 | -0.14191 | -122.6807 | 0.49438 | 0.36163 | 0.50354 | -122.7539 | 0.80566 | 0.54474 | 0.53558 | -123.5001 | 0.6134 | 0.54016 | 0.37537 | -123.436
4734.0156 | 123.317 | -0.48523 | 122.7036 | -0.14511 | 0.0095853 | 0.0045908 | 0.015189 | 0.028668 | -0.0013587 | -0.0089999 | -0.2214 | -0.0048536 | 0.01214 | -0.011388 | 0.027066 | -0.0072738 | 0.059509 | 0.16937 | 0.073242 | -0.28381 | 0.26093 | -0.51727 | -0.70038 | 0.068665 | -0.10529 | -0.022888 | 0.032043 | -0.022888 | -0.60425 | -0.65002 | -0.032044 | -0.21515 | -122.4426 | 0.6546 | 0.20142 | 0.41656 | -122.644 | -0.11902 | -0.1648 | -122.6715 | 0.55389 | 0.46234 | 0.62714 | -122.7264 | 0.74615 | 0.54474 | 0.55847 | -123.4039 | 0.51727 | 0.46234 | 0.37994 | -123.3536
4735.0156 | 123.2391 | -0.54016 | 122.7402 | -0.19089 | 0.015994 | 0.0041634 | 0.018393 | 0.027386 | 0.0048363 | -0.0092137 | -0.32822 | -0.0048536 | 0.017053 | -0.010106 | 0.025357 | -0.008342 | -0.022888 | 0.027466 | -0.050354 | -0.35248 | 0.27466 | -0.55389 | -0.737 | -0.027466 | -0.19226 | -0.16022 | 0.09613 | 0.032043 | -0.64545 | -0.67291 | -0.013733 | -0.19684 | -122.4655 | 0.56763 | 0.18768 | 0.38452 | -122.7631 | -0.10529 | -0.13275 | -122.644 | 0.5127 | 0.37994 | 0.5127 | -122.7081 | 0.81482 | 0.51727 | 0.48981 | -123.4772 | 0.63629 | 0.5722 | 0.3479 | -123.4131
4736.0156 | 123.3307 | -0.48981 | 122.6898 | -0.099335 | 0.012362 | 0.0052316 | 0.013693 | 0.024609 | -0.0030677 | -0.0081455 | -0.061188 | -0.0054944 | 0.010431 | -0.01032 | 0.023648 | -0.0062058 | 0.050354 | 0.14648 | 0.068665 | -0.3067 | 0.26093 | -0.49896 | -0.67749 | 0.073242 | -0.07782 | -0.009155 | 0.059509 | -0.013733 | -0.59967 | -0.64545 | -0.009155 | -0.18768 | -122.4289 | 0.63629 | 0.18311 | 0.37079 | -122.6395 | -0.10986 | -0.15564 | -122.6303 | 0.56305 | 0.48065 | 0.63629 | -122.7036 | 0.75073 | 0.54016 | 0.55847 | -123.3673 | 0.54932 | 0.47607 | 0.41199 | -123.3353
4737.0156 | 123.2162 | -0.50812 | 122.7356 | -0.26718 | 0.013003 | 0.0022408 | 0.016043 | 0.026105 | -7.6852e-05 | -0.010922 | -0.17563 | -0.00464 | 0.012354 | -0.012884 | 0.02493 | -0.005565 | 0.013733 | 0.11444 | 0.032043 | -0.31586 | 0.2655 | -0.53101 | -0.71869 | -0.018311 | -0.15564 | -0.11902 | 0.064087 | 0.022888 | -0.62256 | -0.65002 | -0.022888 | -0.21057 | -122.4701 | 0.62256 | 0.19226 | 0.40283 | -122.7219 | -0.11444 | -0.14191 | -122.6715 | 0.48981 | 0.3891 | 0.53101 | -122.7127 | 0.77362 | 0.52185 | 0.54016 | -123.4543 | 0.5722 | 0.53101 | 0.35248 | -123.3856
4738.0156 | 123.3032 | -0.50812 | 122.7356 | -0.21378 | 0.0095853 | 0.0058724 | 0.015189 | 0.026532 | -0.0011451 | -0.0079319 | -0.12985 | -0.006349 | 0.0097903 | -0.010534 | 0.021512 | -0.0051376 | 0.032043 | 0.15564 | 0.10071 | -0.31586 | 0.2655 | -0.50354 | -0.69122 | 0.059509 | -0.091553 | -0.045776 | 0.054932 | -0.018311 | -0.62256 | -0.63629 | 0.004578 | -0.18311 | -122.4701 | 0.66376 | 0.19226 | 0.37537 | -122.7036 | -0.11444 | -0.12817 | -122.6807 | 0.56763 | 0.46234 | 0.59052 | -122.7539 | 0.77362 | 0.54016 | 0.60883 | -123.4268 | 0.56305 | 0.48981 | 0.41656 | -123.3719
4739.0156 | 123.2162 | -0.52643 | 122.7402 | -0.20615 | 0.013003 | 0.006086 | 0.01647 | 0.023968 | 0.00077755 | -0.010282 | -0.27481 | -0.0018628 | 0.013422 | -0.012029 | 0.023221 | -0.0064194 | 0.013733 | 0.09613 | 0.027466 | -0.31586 | 0.27924 | -0.53101 | -0.70496 | -0.036621 | -0.19226 | -0.14191 | 0.073242 | 0.013733 | -0.64087 | -0.66376 | -0.004578 | -0.17853 | -122.4609 | 0.62256 | 0.21057 | 0.3891 | -122.7264 | -0.11444 | -0.13733 | -122.6669 | 0.48981 | 0.38452 | 0.52185 | -122.7264 | 0.80566 | 0.54016 | 0.55389 | -123.4451 | 0.59967 | 0.54016 | 0.33417 | -123.4039
4740.0156 | 123.1979 | -0.55389 | 122.7722 | -0.28244 | 0.011935 | 0.005018 | 0.01882 | 0.027386 | 0.00099115 | -0.0092137 | -0.25955 | -0.0016492 | 0.015558 | -0.010961 | 0.025571 | -0.0062058 | -0.050354 | 0.032043 | -0.054932 | -0.36621 | 0.31586 | -0.55389 | -0.74158 | -0.054932 | -0.25177 | -0.16479 | 0.10986 | 0.027466 | -0.63629 | -0.65918 | 0 | -0.18768 | -122.4564 | 0.58594 | 0.18768 | 0.37537 | -122.8226 | -0.082398 | -0.10529 | -122.6624 | 0.49896 | 0.3891 | 0.49438 | -122.7448 | 0.86975 | 0.50354 | 0.49896 | -123.5138 | 0.66376 | 0.58136 | 0.30212 | -123.4314
4741.0156 | 123.1842 | -0.53558 | 122.7676 | -0.19852 | 0.014285 | 0.0026682 | 0.017752 | 0.026746 | -0.0017859 | -0.010068 | -0.2214 | -0.005708 | 0.010004 | -0.012456 | 0.023434 | -0.0053512 | -0.027466 | 0.09613 | -0.022888 | -0.32959 | 0.30212 | -0.53101 | -0.71411 | -0.041199 | -0.20142 | -0.15106 | 0.09613 | 0.036621 | -0.64087 | -0.66834 | 0.004577 | -0.17853 | -122.4655 | 0.63171 | 0.20599 | 0.38452 | -122.7951 | -0.10529 | -0.13275 | -122.6715 | 0.49438 | 0.38452 | 0.51727 | -122.731 | 0.83771 | 0.50812 | 0.5127 | -123.4818 | 0.63171 | 0.5722 | 0.33417 | -123.436
4742.0156 | 123.2071 | -0.53558 | 122.7859 | -0.11459 | 0.011294 | 0.0056588 | 0.016684 | 0.026105 | 0.0018457 | -0.011777 | -0.26718 | -0.0059216 | 0.012781 | -0.010747 | 0.023434 | -0.0053512 | -0.027466 | 0.054932 | -0.022888 | -0.35706 | 0.28381 | -0.55847 | -0.71869 | -0.059509 | -0.21515 | -0.15106 | 0.091553 | 0.027466 | -0.63629 | -0.66376 | -0.022889 | -0.18311 | -122.5021 | 0.59052 | 0.17853 | 0.36163 | -122.8134 | -0.10071 | -0.12817 | -122.6944 | 0.47607 | 0.38452 | 0.5127 | -122.7585 | 0.8194 | 0.50812 | 0.5127 | -123.5046 | 0.62714 | 0.56305 | 0.32043 | -123.4497
4743.0156 | 123.2025 | -0.54016 | 122.7676 | -0.22141 | 0.01578 | 0.0075814 | 0.019034 | 0.025891 | 0.0039819 | -0.0092137 | -0.2977 | -0.0031446 | 0.014917 | -0.0094657 | 0.024075 | -0.0042832 | -0.054932 | -0.004578 | -0.059509 | -0.37994 | 0.31586 | -0.56763 | -0.73242 | -0.064087 | -0.23346 | -0.16022 | 0.11444 | 0.036621 | -0.65918 | -0.67749 | -0.027466 | -0.19226 | -122.4518 | 0.53558 | 0.16022 | 0.35248 | -122.8226 | -0.11902 | -0.13733 | -122.6532 | 0.47607 | 0.37994 | 0.51727 | -122.731 | 0.85602 | 0.48523 | 0.48065 | -123.5001 | 0.6546 | 0.57678 | 0.3067 | -123.4451
4744.0156 | 123.2346 | -0.50812 | 122.7676 | -0.22141 | 0.010013 | 0.0056588 | 0.014548 | 0.024823 | -0.0013587 | -0.0085727 | -0.14511 | -0.0052808 | 0.013422 | -0.012456 | 0.02258 | -0.0053512 | -0.004578 | 0.11444 | 0.050354 | -0.29755 | 0.2655 | -0.5127 | -0.70496 | 0 | -0.14191 | -0.086975 | 0.07782 | 0.009155 | -0.62714 | -0.65002 | -0.004577 | -0.19684 | -122.5021 | 0.62256 | 0.21057 | 0.40741 | -122.7722 | -0.11902 | -0.14191 | -122.6898 | 0.50812 | 0.42114 | 0.56305 | -122.7585 | 0.77362 | 0.50354 | 0.55847 | -123.4726 | 0.58594 | 0.51727 | 0.36621 | -123.4177
4745.0156 | 123.2254 | -0.52643 | 122.7814 | -0.38925 | 0.016421 | 0.0043772 | 0.017111 | 0.027173 | 0.0039819 | -0.0087863 | -0.084076 | -0.0027174 | 0.014063 | -0.010747 | 0.023007 | -0.0064194 | -0.064087 | 0.032043 | -0.054932 | -0.37079 | 0.30212 | -0.55389 | -0.72327 | -0.054932 | -0.22888 | -0.17395 | 0.09613 | 0.027466 | -0.64545 | -0.6546 | -0.027466 | -0.19684 | -122.4792 | 0.55847 | 0.15564 | 0.35248 | -122.8455 | -0.11902 | -0.12817 | -122.6852 | 0.4715 | 0.35248 | 0.48065 | -122.7539 | 0.82855 | 0.46234 | 0.4715 | -123.5046 | 0.62256 | 0.55389 | 0.29755 | -123.436
4746.0156 | 123.2162 | -0.54016 | 122.7951 | -0.015411 | 0.01514 | 0.0054452 | 0.017111 | 0.026532 | 0.00056395 | -0.0089999 | -0.25955 | -0.0031446 | 0.012995 | -0.010961 | 0.024503 | -0.0053512 | -0.064087 | 0.059509 | -0.050354 | -0.36163 | 0.29755 | -0.55847 | -0.71869 | -0.064087 | -0.21973 | -0.15564 | 0.091553 | 0.027466 | -0.64545 | -0.66376 | -0.018311 | -0.17853 | -122.4976 | 0.59967 | 0.17853 | 0.35706 | -122.8592 | -0.10529 | -0.1236 | -122.7036 | 0.47607 | 0.38452 | 0.50812 | -122.7676 | 0.83771 | 0.47607 | 0.48981 | -123.5138 | 0.63171 | 0.56763 | 0.32043 | -123.4589
4747.0156 | 123.1979 | -0.52643 | 122.7768 | -0.14511 | 0.016849 | 0.0041634 | 0.019034 | 0.027386 | 0.0041955 | -0.0075047 | -0.25192 | -0.0033582 | 0.012781 | -0.011602 | 0.025357 | -0.0064194 | -0.013733 | 0.059509 | -0.036621 | -0.32501 | 0.29755 | -0.55847 | -0.71869 | -0.032043 | -0.20142 | -0.13733 | 0.082397 | 0.013733 | -0.62714 | -0.65918 | -0.032044 | -0.19226 | -122.4792 | 0.58594 | 0.20142 | 0.39368 | -122.7905 | -0.10071 | -0.13275 | -122.6944 | 0.49439 | 0.3891 | 0.52185 | -122.7631 | 0.82397 | 0.5127 | 0.48981 | -123.4955 | 0.60882 | 0.54016 | 0.32501 | -123.436
4748.0156 | 123.1888 | -0.55389 | 122.7859 | -0.30533 | 0.013217 | 0.003309 | 0.017325 | 0.026959 | -0.0037085 | -0.010068 | -0.20615 | -0.0042126 | 0.015772 | -0.0094657 | 0.02258 | -0.0034286 | -0.073242 | 0.013733 | -0.050354 | -0.36621 | 0.31128 | -0.54932 | -0.72784 | -0.07782 | -0.20599 | -0.16479 | 0.10071 | 0.032043 | -0.61798 | -0.66834 | 0.004578 | -0.17395 | -122.4747 | 0.56763 | 0.18768 | 0.36163 | -122.8592 | -0.064087 | -0.11444 | -122.6852 | 0.47607 | 0.3891 | 0.50354 | -122.7539 | 0.86517 | 0.48065 | 0.50354 | -123.5138 | 0.6546 | 0.58594 | 0.3479 | -123.4543
4749.0156 | 123.2117 | -0.53558 | 122.7722 | -0.14511 | 0.02048 | 0.0016 | 0.018393 | 0.024823 | 0.0037683 | -0.0089999 | -0.0077819 | -0.0025038 | 0.017053 | -0.010747 | 0.025357 | -0.0057786 | -0.032043 | 0.041199 | -0.059509 | -0.35248 | 0.29755 | -0.53558 | -0.71869 | -0.036621 | -0.22888 | -0.17853 | 0.086975 | 0.027466 | -0.64087 | -0.65918 | 0 | -0.18311 | -122.4747 | 0.57678 | 0.18311 | 0.36621 | -122.8043 | -0.10529 | -0.1236 | -122.6852 | 0.49896 | 0.35706 | 0.48065 | -122.7448 | 0.83313 | 0.50354 | 0.47607 | -123.4909 | 0.62256 | 0.56305 | 0.3067 | -123.4314
4750.0156 | 123.1979 | -0.53101 | 122.7676 | -0.068817 | 0.018344 | 0.0043772 | 0.018179 | 0.028027 | 0.0029137 | -0.0096409 | -0.25192 | -0.0027174 | 0.017267 | -0.0094657 | 0.024503 | -0.0040696 | 0 | 0.045776 | -0.018311 | -0.32959 | 0.28839 | -0.53101 | -0.74158 | -0.013733 | -0.18768 | -0.13733 | 0.07782 | 0.013733 | -0.62714 | -0.65918 | 0 | -0.21057 | -122.4792 | 0.57678 | 0.20142 | 0.41199 | -122.7676 | -0.09613 | -0.12817 | -122.6898 | 0.51727 | 0.39368 | 0.52185 | -122.7539 | 0.8194 | 0.53101 | 0.5127 | -123.5092 | 0.60883 | 0.54474 | 0.34332 | -123.4268
4751.0156 | 123.2208 | -0.52643 | 122.7722 | -0.10696 | 0.019839 | 0.0018136 | 0.016898 | 0.025891 | 0.0044091 | -0.0077183 | -0.10696 | -0.001222 | 0.014063 | -0.0081839 | 0.025357 | -0.0053512 | 0 | 0.064087 | -0.036621 | -0.32501 | 0.30212 | -0.53101 | -0.70953 | -0.041199 | -0.19226 | -0.15106 | 0.073242 | 0.027466 | -0.62714 | -0.6546 | -0.004578 | -0.18311 | -122.4701 | 0.59052 | 0.20142 | 0.38452 | -122.7722 | -0.10071 | -0.12817 | -122.699 | 0.48523 | 0.37537 | 0.50354 | -122.7448 | 0.82855 | 0.52643 | 0.48981 | -123.4818 | 0.59967 | 0.55389 | 0.33417 | -123.4268
4752.0156 | 123.2574 | -0.48981 | 122.7585 | -0.20615 | 0.011508 | 0.006727 | 0.016684 | 0.026746 | -0.0037085 | -0.0081455 | -0.061188 | -0.003999 | 0.014063 | -0.012243 | 0.022794 | -0.0044968 | -0.004578 | 0.13275 | 0.045776 | -0.29755 | 0.26093 | -0.50812 | -0.70953 | -0.045776 | -0.13275 | -0.07782 | 0.073242 | 0.013733 | -0.63171 | -0.63629 | -0.018311 | -0.21973 | -122.4976 | 0.62256 | 0.19226 | 0.41199 | -122.7631 | -0.14191 | -0.14648 | -122.6852 | 0.44403 | 0.41199 | 0.55847 | -122.7448 | 0.75073 | 0.48523 | 0.53558 | -123.468 | 0.56305 | 0.50354 | 0.35706 | -123.3948
4753.0156 | 123.1934 | -0.53558 | 122.7859 | -0.076447 | 0.02048 | 0.0041634 | 0.01882 | 0.025037 | 0.0029137 | -0.0087863 | 0.015106 | -0.0014356 | 0.017908 | -0.010961 | 0.026639 | -0.0074876 | -0.022888 | -0.004578 | -0.059509 | -0.3479 | 0.28381 | -0.53101 | -0.72327 | -0.07782 | -0.27924 | -0.18768 | 0.073242 | 0.036621 | -0.63629 | -0.66376 | 0.004577 | -0.18768 | -122.5021 | 0.53101 | 0.18768 | 0.37537 | -122.8088 | -0.10071 | -0.12817 | -122.7127 | 0.45776 | 0.3479 | 0.47607 | -122.7493 | 0.8194 | 0.5127 | 0.47607 | -123.5092 | 0.60883 | 0.5722 | 0.25635 | -123.4497
4754.0156 | 123.2803 | -0.52185 | 122.7631 | -0.20615 | 0.019412 | 0.005018 | 0.016898 | 0.028668 | 0.0044091 | -0.0077183 | -0.091705 | -0.0014356 | 0.014063 | -0.0098929 | 0.025998 | -0.0062058 | -0.004578 | 0.050354 | -0.018311 | -0.33875 | 0.27924 | -0.52185 | -0.73242 | -0.022888 | -0.19226 | -0.14648 | 0.07782 | 0.032043 | -0.63629 | -0.64545 | 0 | -0.21057 | -122.4838 | 0.5722 | 0.18311 | 0.39368 | -122.7676 | -0.11444 | -0.1236 | -122.6852 | 0.49896 | 0.37537 | 0.49896 | -122.731 | 0.80109 | 0.51727 | 0.50354 | -123.4955 | 0.59967 | 0.55389 | 0.32959 | -123.4085
4755.0156 | 123.2117 | -0.56305 | 122.7631 | 0.16769 | 0.023257 | 0.0048044 | 0.014121 | 0.026746 | 0.0014185 | -0.0062229 | 0.13718 | -0.00079476 | 0.01684 | -0.01032 | 0.024716 | -0.0047104 | -0.068665 | -0.045776 | -0.082397 | -0.3891 | 0.29297 | -0.54016 | -0.71411 | -0.07782 | -0.27466 | -0.17853 | 0.082397 | 0.027466 | -0.65002 | -0.67749 | 0.022888 | -0.15106 | -122.4701 | 0.51727 | 0.17395 | 0.32501 | -122.8317 | -0.086975 | -0.11444 | -122.6807 | 0.48523 | 0.38452 | 0.49896 | -122.7356 | 0.85602 | 0.49438 | 0.48065 | -123.4772 | 0.64545 | 0.59052 | 0.28839 | -123.4406
4756.0156 | 123.2483 | -0.53101 | 122.7814 | -0.15274 | 0.01813 | 0.0035226 | 0.01647 | 0.026959 | 0.00035035 | -0.0087863 | -0.27481 | -0.0031446 | 0.01449 | -0.0096793 | 0.022794 | -0.0044968 | -0.013733 | 0.022888 | -0.045776 | -0.34332 | 0.29755 | -0.54932 | -0.74158 | -0.041199 | -0.18768 | -0.15106 | 0.068665 | 0.022888 | -0.64545 | -0.6546 | -0.01831 | -0.21057 | -122.4838 | 0.55389 | 0.18768 | 0.39825 | -122.7951 | -0.11444 | -0.1236 | -122.7127 | 0.48981 | 0.37994 | 0.50354 | -122.7585 | 0.82855 | 0.51727 | 0.48523 | -123.5229 | 0.59967 | 0.55389 | 0.34332 | -123.436
4757.0156 | 123.2254 | -0.53558 | 122.7859 | 0.19058 | 0.017489 | 0.005018 | 0.014761 | 0.028882 | 0.00056395 | -0.0068637 | 0.17532 | -0.0035718 | 0.016199 | -0.010534 | 0.025784 | -0.0062058 | -0.050354 | -0.059509 | -0.064087 | -0.39368 | 0.29297 | -0.52643 | -0.73242 | -0.068665 | -0.28381 | -0.16479 | 0.07782 | 0.027466 | -0.63629 | -0.67291 | 0.009155 | -0.19684 | -122.493 | 0.47607 | 0.14191 | 0.33875 | -122.8363 | -0.10071 | -0.13733 | -122.7081 | 0.46692 | 0.37079 | 0.50812 | -122.7585 | 0.82855 | 0.48523 | 0.4715 | -123.5184 | 0.6134 | 0.56305 | 0.25177 | -123.4589
4758.0156 | 123.23 | -0.52185 | 122.7493 | 0.076141 | 0.022403 | 0.0037362 | 0.020743 | 0.02995 | 0.0033411 | -0.010068 | -0.076446 | -0.0044264 | 0.017053 | -0.013097 | 0.025784 | -0.006633 | 0.018311 | 0.018311 | -0.050354 | -0.35706 | 0.28381 | -0.52643 | -0.71869 | -0.032043 | -0.21515 | -0.17853 | 0.064087 | 0.018311 | -0.63629 | -0.6546 | -0.004577 | -0.19684 | -122.4655 | 0.54016 | 0.16479 | 0.36163 | -122.731 | -0.11444 | -0.13275 | -122.6852 | 0.48981 | 0.34332 | 0.47607 | -122.731 | 0.80566 | 0.54016 | 0.4715 | -123.468 | 0.58594 | 0.54016 | 0.3067 | -123.4039
4759.0156 | 123.2391 | -0.53558 | 122.7631 | -0.099335 | 0.018985 | 0.006727 | 0.018607 | 0.02525 | 0.0039819 | -0.011136 | -0.14511 | -0.0033582 | 0.015985 | -0.0094657 | 0.025143 | -0.005565 | -0.004578 | 0.036621 | -0.032043 | -0.34332 | 0.27466 | -0.51727 | -0.72784 | -0.027466 | -0.20142 | -0.15106 | 0.073242 | 0.022888 | -0.65918 | -0.66834 | 0.01831 | -0.19226 | -122.4884 | 0.5722 | 0.19226 | 0.38452 | -122.7676 | -0.1236 | -0.13275 | -122.6898 | 0.50812 | 0.38452 | 0.51727 | -122.7402 | 0.81024 | 0.53101 | 0.50354 | -123.4909 | 0.60883 | 0.55847 | 0.33417 | -123.4314
4760.0156 | 123.262 | -0.5127 | 122.7585 | -0.16037 | 0.018985 | 0.0041634 | 0.01583 | 0.027173 | 0.00035035 | -0.0085727 | -0.084076 | -0.002931 | 0.012781 | -0.011388 | 0.024716 | -0.003215 | -0.009155 | 0.068665 | -0.018311 | -0.3479 | 0.28381 | -0.53558 | -0.737 | -0.036621 | -0.1831 | -0.15106 | 0.091553 | 0.032043 | -0.64087 | -0.65002 | -0.022888 | -0.2243 | -122.4747 | 0.58136 | 0.1648 | 0.3891 | -122.7676 | -0.12817 | -0.13733 | -122.6669 | 0.47607 | 0.36163 | 0.49896 | -122.7264 | 0.79651 | 0.50354 | 0.49438 | -123.4955 | 0.60425 | 0.54474 | 0.32959 | -123.4085
4761.0312 | 123.3398 | -0.47607 | 122.7402 | -0.12985 | 0.012576 | -0.03557 | 0.012839 | 0.0276 | -0.0071265 | -0.011563 | -0.00015237 | -0.005708 | 0.013849 | -0.012456 | 0.022366 | -0.003856 | 0.009155 | 0.15106 | 0.050354 | -0.28381 | 0.27008 | -0.49439 | -0.67749 | 0.018311 | -0.09613 | -0.022888 | 0.059509 | 0 | -0.60425 | -0.62714 | -0.018311 | -0.20142 | -122.4701 | 0.62714 | 0.19226 | 0.39368 | -122.731 | -0.12817 | -0.15106 | -122.6807 | 0.49439 | 0.45319 | 0.60425 | -122.7402 | 0.74616 | 0.48523 | 0.52643 | -123.4177 | 0.53558 | 0.47607 | 0.37994 | -123.3673
4762.0156 | 123.2071 | -0.52643 | 122.7768 | 0.0074768 | 0.019839 | 0.0043772 | 0.017966 | 0.027173 | 0.0031273 | -0.0079319 | -0.038299 | -0.0037854 | 0.015985 | -0.011815 | 0.026852 | -0.003856 | -0.032043 | -0.013733 | -0.073242 | -0.36163 | 0.29755 | -0.53101 | -0.71411 | -0.086975 | -0.27924 | -0.21973 | 0.10071 | 0.032043 | -0.64545 | -0.67291 | -0.004578 | -0.18768 | -122.4792 | 0.5127 | 0.1648 | 0.35248 | -122.8088 | -0.11902 | -0.14648 | -122.6761 | 0.43945 | 0.3067 | 0.45319 | -122.7448 | 0.82397 | 0.49439 | 0.45319 | -123.4909 | 0.62714 | 0.55847 | 0.24719 | -123.4497
4763.0156 | 123.2162 | -0.53558 | 122.7676 | 0.068512 | 0.022616 | 0.0056588 | 0.018179 | 0.029095 | 0.0024865 | -0.0098545 | 0.053253 | -0.0014356 | 0.015344 | -0.01032 | 0.023648 | -0.0042832 | -0.027466 | -0.050354 | -0.073242 | -0.37079 | 0.29755 | -0.54474 | -0.72327 | -0.073242 | -0.29755 | -0.17395 | 0.10529 | 0.032043 | -0.63629 | -0.64545 | -0.009156 | -0.18768 | -122.4701 | 0.48523 | 0.16479 | 0.35248 | -122.7951 | -0.10071 | -0.10986 | -122.6624 | 0.46234 | 0.36163 | 0.4715 | -122.7356 | 0.83313 | 0.50812 | 0.46234 | -123.4909 | 0.64087 | 0.56763 | 0.23804 | -123.4131
4764.0156 | 123.2117 | -0.5127 | 122.7585 | 0.022736 | 0.020694 | 0.0045908 | 0.017539 | 0.023755 | 0.0046227 | -0.010709 | -0.091705 | -0.0042126 | 0.015558 | -0.010534 | 0.024503 | -0.0042832 | 0.009155 | 0.004578 | -0.059509 | -0.35248 | 0.27466 | -0.53558 | -0.70496 | -0.050354 | -0.2655 | -0.16937 | 0.10529 | 0.050354 | -0.64087 | -0.65918 | -0.022888 | -0.19226 | -122.4838 | 0.51727 | 0.16022 | 0.35248 | -122.7493 | -0.12817 | -0.14648 | -122.6532 | 0.46234 | 0.34332 | 0.48981 | -122.7081 | 0.78735 | 0.52185 | 0.45319 | -123.4634 | 0.61798 | 0.56305 | 0.24719 | -123.4177
4765.0156 | 123.2666 | -0.50812 | 122.7585 | 0.022736 | 0.011508 | 0.0048044 | 0.01583 | 0.025677 | -0.0062721 | -0.0096409 | 0.14481 | -0.00229 | 0.012567 | -0.011602 | 0.021512 | -0.002147 | -0.059509 | 0.073242 | 0.009155 | -0.33417 | 0.26093 | -0.51727 | -0.69122 | -0.032043 | -0.1831 | -0.059509 | 0.054932 | 0.013733 | -0.61798 | -0.63171 | -0.009155 | -0.18311 | -122.4976 | 0.58136 | 0.17395 | 0.35706 | -122.818 | -0.10986 | -0.1236 | -122.7036 | 0.47607 | 0.44861 | 0.5722 | -122.7448 | 0.76904 | 0.44861 | 0.51727 | -123.4497 | 0.56305 | 0.52185 | 0.32501 | -123.3902
4766.0156 | 123.3124 | -0.4715 | 122.7402 | 0.16769 | 0.014071 | 0.0048044 | 0.015616 | 0.025464 | -0.0011451 | -0.0096409 | 0.33554 | -0.0031446 | 0.013849 | -0.011175 | 0.026212 | -0.004924 | 0.059509 | 0.10071 | 0.045776 | -0.29755 | 0.26093 | -0.48065 | -0.68207 | 0.050354 | -0.16022 | -0.050354 | 0.027466 | -0.004578 | -0.5722 | -0.62256 | -0.009155 | -0.21057 | -122.4792 | 0.5722 | 0.17395 | 0.38452 | -122.6807 | -0.10071 | -0.15106 | -122.7127 | 0.52185 | 0.42114 | 0.5722 | -122.7448 | 0.73242 | 0.53101 | 0.51727 | -123.4222 | 0.49896 | 0.46692 | 0.31128 | -123.3627
4767.0156 | 123.143 | -0.52643 | 122.7676 | 0.14481 | 0.020053 | 0.0045908 | 0.019888 | 0.026746 | 0.0037683 | -0.010922 | 0.13718 | -0.0020764 | 0.012354 | -0.01032 | 0.027493 | -0.0057786 | -0.036621 | -0.086975 | -0.09613 | -0.3891 | 0.28381 | -0.54932 | -0.70496 | -0.07782 | -0.29297 | -0.18768 | 0.091553 | 0.032043 | -0.64545 | -0.6546 | -0.022888 | -0.17853 | -122.4838 | 0.43945 | 0.13733 | 0.31586 | -122.8043 | -0.11902 | -0.12817 | -122.6761 | 0.44861 | 0.33875 | 0.46692 | -122.7356 | 0.81024 | 0.48981 | 0.4303 | -123.4726 | 0.61798 | 0.55847 | 0.23346 | -123.4222
4768.0156 | 123.2574 | -0.52185 | 122.7859 | 0.11429 | 0.02283 | 0.005018 | 0.016898 | 0.026959 | 0.0024865 | -0.0089999 | 0.0914 | -0.00464 | 0.013849 | -0.011175 | 0.024289 | -0.0087692 | -0.018311 | -0.059509 | -0.086975 | -0.37079 | 0.29297 | -0.53101 | -0.71869 | -0.082397 | -0.29755 | -0.18768 | 0.086975 | 0.041199 | -0.63629 | -0.66376 | -0.009155 | -0.19684 | -122.493 | 0.46234 | 0.15106 | 0.3479 | -122.8043 | -0.11444 | -0.14191 | -122.699 | 0.43945 | 0.33417 | 0.47607 | -122.7448 | 0.81482 | 0.50354 | 0.43488 | -123.5046 | 0.60883 | 0.56305 | 0.2243 | -123.4497
4769.0156 | 123.3215 | -0.48981 | 122.7402 | 0.099029 | 0.013217 | 0.007795 | 0.013907 | 0.025464 | -0.0049903 | -0.011136 | 0.21347 | -0.00464 | 0.013208 | -0.010747 | 0.024289 | -0.0036424 | 0.022888 | 0.086975 | 0.041199 | -0.33417 | 0.25635 | -0.50354 | -0.68665 | -0.004578 | -0.19684 | -0.064087 | 0.059509 | 0.027466 | -0.59509 | -0.63171 | -0.013733 | -0.19684 | -122.4838 | 0.57678 | 0.15564 | 0.35248 | -122.7173 | -0.10529 | -0.14191 | -122.6807 | 0.48523 | 0.42572 | 0.56763 | -122.7127 | 0.74616 | 0.5127 | 0.53101 | -123.4268 | 0.54932 | 0.51727 | 0.29297 | -123.3719
4770.0156 | 123.2895 | -0.48065 | 122.7356 | 0.10666 | 0.016421 | 0.0048044 | 0.01583 | 0.024609 | -0.0037085 | -0.010282 | 0.19058 | -0.0050672 | 0.015344 | -0.012456 | 0.025571 | -0.0057786 | 0.050354 | 0.086975 | 0.036621 | -0.29755 | 0.23804 | -0.49896 | -0.68207 | 0.032043 | -0.16022 | -0.064087 | 0.054932 | 0.009155 | -0.60883 | -0.60883 | -0.01831 | -0.20142 | -122.4976 | 0.56763 | 0.18311 | 0.38452 | -122.6852 | -0.12817 | -0.12817 | -122.6807 | 0.5127 | 0.41657 | 0.54474 | -122.7264 | 0.71869 | 0.53101 | 0.51727 | -123.4177 | 0.53558 | 0.48981 | 0.32044 | -123.3444
4771.0156 | 123.3444 | -0.49896 | 122.7219 | -0.084076 | 0.010867 | 0.0045908 | 0.015402 | 0.025464 | -0.0045631 | -0.010922 | -0.19089 | -0.0069898 | 0.01214 | -0.013952 | 0.022153 | -0.0047104 | 0.054932 | 0.16022 | 0.059509 | -0.29297 | 0.27008 | -0.49896 | -0.67749 | 0.050354 | -0.09613 | -0.032043 | 0.045776 | 0.018311 | -0.59509 | -0.61798 | 0 | -0.17853 | -122.4518 | 0.65918 | 0.20599 | 0.38452 | -122.6669 | -0.096131 | -0.11902 | -122.6761 | 0.54932 | 0.46692 | 0.58594 | -122.7036 | 0.76904 | 0.55389 | 0.55847 | -123.3994 | 0.54474 | 0.51727 | 0.40283 | -123.3398
4772.0156 | 123.2483 | -0.51727 | 122.7722 | 0.11429 | 0.016635 | 0.0041634 | 0.019034 | 0.026746 | 0.0012047 | -0.011136 | 0.18295 | -0.0033582 | 0.015772 | -0.010747 | 0.025784 | -0.0077012 | 0.004578 | -0.027466 | -0.059509 | -0.36621 | 0.29755 | -0.52185 | -0.70496 | -0.013733 | -0.25635 | -0.12817 | 0.10529 | 0.032043 | -0.62714 | -0.64087 | -0.004578 | -0.18768 | -122.4747 | 0.48981 | 0.15106 | 0.33875 | -122.7676 | -0.10986 | -0.1236 | -122.6669 | 0.50354 | 0.3891 | 0.5127 | -122.7402 | 0.81482 | 0.52185 | 0.45776 | -123.4772 | 0.62256 | 0.54932 | 0.26092 | -123.4131
4773.0156 | 123.2758 | -0.48981 | 122.7356 | 0.10666 | 0.01044 | 0.0062998 | 0.014548 | 0.026959 | -0.0030677 | -0.010068 | 0.28214 | -0.0052808 | 0.01449 | -0.010747 | 0.02258 | -0.0051376 | 0.054932 | 0.054932 | 0.027466 | -0.34332 | 0.25635 | -0.50812 | -0.67749 | 0.018311 | -0.19226 | -0.07782 | 0.045776 | 0.004578 | -0.59509 | -0.62256 | -0.018311 | -0.18768 | -122.4792 | 0.54474 | 0.14648 | 0.33417 | -122.6807 | -0.10529 | -0.13275 | -122.6898 | 0.50812 | 0.41199 | 0.54474 | -122.731 | 0.74616 | 0.54474 | 0.51727 | -123.4131 | 0.53558 | 0.49439 | 0.29755 | -123.3582
4774.0156 | 123.317 | -0.47607 | 122.7402 | 0.22873 | 0.02048 | 0.0016 | 0.014548 | 0.024823 | 0.0029137 | -0.0092137 | 0.18295 | -0.0037854 | 0.015558 | -0.013097 | 0.025357 | -0.005565 | 0.022888 | -0.009155 | -0.027466 | -0.34332 | 0.27924 | -0.50354 | -0.68665 | 0.050354 | -0.1831 | -0.091553 | 0.064087 | 0 | -0.60425 | -0.63171 | -0.027466 | -0.21057 | -122.4609 | 0.46692 | 0.13275 | 0.34332 | -122.7173 | -0.12817 | -0.15564 | -122.6761 | 0.52643 | 0.38452 | 0.54016 | -122.7402 | 0.75531 | 0.49896 | 0.44861 | -123.4268 | 0.54016 | 0.47607 | 0.29297 | -123.3719
4775.0156 | 123.3582 | -0.48065 | 122.7631 | -0.13748 | 0.010653 | 0.0041634 | 0.014334 | 0.026746 | -0.0039221 | -0.012418 | -0.2214 | -0.0054944 | 0.010431 | -0.012456 | 0.021939 | -0.0036424 | 0.068665 | 0.14191 | 0.082397 | -0.25177 | 0.27466 | -0.50812 | -0.67749 | 0.041199 | -0.082397 | -0.036621 | 0.032043 | 0.004578 | -0.59509 | -0.62714 | -0.027466 | -0.19684 | -122.4884 | 0.62256 | 0.22888 | 0.42572 | -122.6944 | -0.11444 | -0.14648 | -122.731 | 0.52185 | 0.44403 | 0.59052 | -122.7585 | 0.75531 | 0.54932 | 0.56305 | -123.4406 | 0.5127 | 0.48523 | 0.39826 | -123.3902
4776.0156 | 123.2712 | -0.52185 | 122.7814 | -0.12985 | 0.017276 | 0.0054452 | 0.018179 | 0.026746 | 0.0027001 | -0.0087863 | -0.20615 | -0.0037854 | 0.014276 | -0.0086111 | 0.026425 | -0.0091966 | 0.022888 | 0.013733 | -0.032043 | -0.32959 | 0.29297 | -0.54016 | -0.73242 | -0.004578 | -0.19226 | -0.15564 | 0.10529 | 0.004578 | -0.63171 | -0.6546 | -0.01831 | -0.21057 | -122.4884 | 0.53558 | 0.19226 | 0.40283 | -122.7585 | -0.10986 | -0.13275 | -122.6761 | 0.51727 | 0.36621 | 0.49896 | -122.7768 | 0.81482 | 0.54474 | 0.48981 | -123.5138 | 0.62714 | 0.52643 | 0.32959 | -123.436
4777.0156 | 123.3673 | -0.4715 | 122.7493 | -0.28244 | 0.0085171 | 0.006086 | 0.014548 | 0.025891 | -0.0073401 | -0.0092137 | -0.10696 | -0.0067762 | 0.011713 | -0.012456 | 0.022153 | -0.0062058 | 0.045776 | 0.11902 | 0.064087 | -0.28839 | 0.25177 | -0.49896 | -0.66834 | 0.073242 | -0.082397 | 0 | 0.045776 | -0.013733 | -0.60425 | -0.63171 | -0.027465 | -0.19684 | -122.4976 | 0.59052 | 0.18311 | 0.37994 | -122.7036 | -0.13275 | -0.16022 | -122.7036 | 0.54474 | 0.4715 | 0.63171 | -122.7631 | 0.72327 | 0.51727 | 0.53558 | -123.4177 | 0.51727 | 0.45776 | 0.3891 | -123.381
4778.0156 | 123.2758 | -0.48065 | 122.7814 | 0.17532 | 0.014071 | 0.0069406 | 0.016684 | 0.025037 | -0.0011451 | -0.010282 | 0.26688 | -0.0059216 | 0.010858 | -0.012456 | 0.024503 | -0.0034286 | 0.013733 | 0.045776 | 0.018311 | -0.33417 | 0.25177 | -0.49439 | -0.68665 | 0.018311 | -0.18768 | -0.082397 | 0.073242 | -0.013733 | -0.60883 | -0.63171 | -0.013733 | -0.20599 | -122.5296 | 0.52643 | 0.14649 | 0.35248 | -122.7676 | -0.12817 | -0.15106 | -122.7081 | 0.49896 | 0.39826 | 0.54932 | -122.7951 | 0.73242 | 0.49439 | 0.49896 | -123.468 | 0.55389 | 0.46692 | 0.29297 | -123.4131
4779.0156 | 123.3078 | -0.49439 | 122.7676 | -0.03067 | 0.0095853 | 0.0045908 | 0.016898 | 0.025891 | -0.0022131 | -0.0087863 | -0.099335 | -0.0033582 | 0.012781 | -0.011388 | 0.023648 | -0.006633 | -0.036621 | 0.07782 | 0.032043 | -0.31586 | 0.27466 | -0.50354 | -0.65918 | 0.022888 | -0.16022 | -0.050354 | 0.068665 | -0.004578 | -0.59967 | -0.63629 | -0.009155 | -0.16479 | -122.493 | 0.57221 | 0.17853 | 0.34332 | -122.8043 | -0.10529 | -0.14191 | -122.699 | 0.51727 | 0.44403 | 0.58594 | -122.7722 | 0.76904 | 0.45776 | 0.52643 | -123.4268 | 0.56305 | 0.48981 | 0.33417 | -123.4039
4780.0156 | 123.3261 | -0.49439 | 122.7722 | -0.023041 | 0.012362 | 0.006727 | 0.016043 | 0.024609 | -0.0024269 | -0.011136 | -0.015411 | -0.005708 | 0.01214 | -0.013952 | 0.022153 | -0.0059922 | 0.009155 | 0.073242 | 0.022888 | -0.29755 | 0.26093 | -0.49439 | -0.68207 | 0.018311 | -0.14648 | -0.050354 | 0.059509 | 0.009155 | -0.60883 | -0.62256 | 0 | -0.18768 | -122.5113 | 0.56763 | 0.19684 | 0.38452 | -122.7631 | -0.11444 | -0.12817 | -122.7127 | 0.5127 | 0.44403 | 0.5722 | -122.7631 | 0.75531 | 0.50354 | 0.51727 | -123.4543 | 0.55389 | 0.50354 | 0.3479 | -123.3948
4781.0156 | 123.381 | -0.4715 | 122.7493 | -0.18326 | 0.0089443 | 0.0039498 | 0.01583 | 0.025464 | -0.0019995 | -0.010922 | -0.14511 | -0.007417 | 0.01214 | -0.011815 | 0.021085 | -0.008342 | 0.068665 | 0.14191 | 0.064087 | -0.28839 | 0.25635 | -0.49439 | -0.67291 | 0.073242 | -0.07782 | -0.041199 | 0.054932 | 0.004578 | -0.5722 | -0.61798 | -0.022888 | -0.20142 | -122.493 | 0.6134 | 0.18311 | 0.38452 | -122.6807 | -0.10071 | -0.14648 | -122.6944 | 0.54474 | 0.4303 | 0.57678 | -122.7448 | 0.72785 | 0.54016 | 0.53558 | -123.4222 | 0.52643 | 0.47608 | 0.39368 | -123.3673
4782.0156 | 123.317 | -0.48981 | 122.7722 | 0.022736 | 0.010653 | 0.0056588 | 0.012412 | 0.024609 | -0.0028541 | -0.0096409 | -0.00015237 | -0.0069898 | 0.012995 | -0.011815 | 0.024289 | -0.0053512 | 0 | 0.059509 | 0.013733 | -0.31586 | 0.25635 | -0.49439 | -0.68665 | 0.022888 | -0.16937 | -0.068665 | 0.064087 | 0 | -0.60425 | -0.63629 | -0.004578 | -0.19684 | -122.5159 | 0.54932 | 0.17395 | 0.37079 | -122.7722 | -0.11444 | -0.14648 | -122.7081 | 0.5127 | 0.42114 | 0.56763 | -122.7722 | 0.74616 | 0.48981 | 0.50354 | -123.4589 | 0.55389 | 0.48981 | 0.32043 | -123.4085
4783.0156 | 123.3353 | -0.47607 | 122.7585 | -0.14511 | 0.0076627 | 0.0041634 | 0.01583 | 0.024609 | -0.0030677 | -0.011777 | -0.16037 | -0.0065626 | 0.01214 | -0.011602 | 0.023862 | -0.0057786 | 0.068665 | 0.13733 | 0.054932 | -0.27924 | 0.25635 | -0.49439 | -0.6958 | 0.064087 | -0.10529 | -0.041199 | 0.07782 | 0 | -0.59052 | -0.61798 | -0.018311 | -0.21973 | -122.5021 | 0.6134 | 0.19684 | 0.41657 | -122.6898 | -0.11444 | -0.14191 | -122.6807 | 0.54016 | 0.43488 | 0.57678 | -122.7585 | 0.73242 | 0.54474 | 0.53101 | -123.4543 | 0.55389 | 0.47607 | 0.37079 | -123.3765
4784.0156 | 123.3124 | -0.48065 | 122.7814 | -0.03067 | 0.013431 | 0.003309 | 0.015616 | 0.025891 | -0.0022131 | -0.011777 | -0.00015237 | -0.005708 | 0.012354 | -0.010106 | 0.021939 | -0.006633 | 0.018311 | 0.073242 | 0.045776 | -0.31586 | 0.27466 | -0.50812 | -0.68207 | 0.045776 | -0.13733 | -0.045776 | 0.068665 | -0.004578 | -0.60425 | -0.63171 | -0.027466 | -0.20142 | -122.5067 | 0.55389 | 0.1648 | 0.36621 | -122.7631 | -0.1236 | -0.15106 | -122.7127 | 0.52643 | 0.43488 | 0.58594 | -122.7859 | 0.75531 | 0.49896 | 0.52643 | -123.4634 | 0.54932 | 0.47607 | 0.34332 | -123.4131
4785.0156 | 123.2849 | -0.51727 | 122.7951 | -0.22903 | 0.014712 | 0.0037362 | 0.01348 | 0.026318 | 0.0039819 | -0.0075047 | -0.34348 | -0.002931 | 0.015772 | -0.01032 | 0.026212 | -0.008342 | 0 | 0 | -0.068665 | -0.35248 | 0.29755 | -0.52643 | -0.72327 | 0 | -0.21515 | -0.14648 | 0.10529 | 0.032043 | -0.63171 | -0.6546 | -0.009155 | -0.20599 | -122.4976 | 0.51727 | 0.16479 | 0.37079 | -122.7951 | -0.11444 | -0.13733 | -122.6898 | 0.51727 | 0.37079 | 0.50812 | -122.7631 | 0.81482 | 0.51727 | 0.44861 | -123.5184 | 0.62256 | 0.54932 | 0.30212 | -123.4497
4786.0156 | 123.3124 | -0.48065 | 122.7768 | -0.22141 | 0.012362 | 0.0054452 | 0.014548 | 0.029736 | -0.0011451 | -0.010068 | -0.19852 | -0.0059216 | 0.011926 | -0.0096793 | 0.023862 | -0.005565 | 0.050354 | 0.15106 | 0.050354 | -0.29297 | 0.27008 | -0.50354 | -0.68207 | 0.027466 | -0.10071 | -0.059509 | 0.068665 | 0.009155 | -0.60425 | -0.61798 | -0.022888 | -0.20142 | -122.5067 | 0.63171 | 0.18768 | 0.3891 | -122.7264 | -0.1236 | -0.13733 | -122.7081 | 0.50812 | 0.42114 | 0.55847 | -122.7676 | 0.75073 | 0.53101 | 0.53101 | -123.4589 | 0.54932 | 0.48981 | 0.37994 | -123.3948
4787.0156 | 123.2941 | -0.50354 | 122.7859 | -0.26718 | 0.012149 | 0.0069406 | 0.01647 | 0.023968 | -0.0015723 | -0.0075047 | -0.18326 | -0.0044264 | 0.012354 | -0.011815 | 0.02258 | -0.0068466 | 0.054932 | 0.14648 | 0.064087 | -0.29755 | 0.26093 | -0.50812 | -0.67749 | 0.045776 | -0.09613 | -0.064087 | 0.082397 | 0 | -0.59967 | -0.62256 | -0.004578 | -0.17395 | -122.525 | 0.65002 | 0.20599 | 0.37994 | -122.731 | -0.09613 | -0.11902 | -122.7036 | 0.54932 | 0.43945 | 0.55847 | -122.7859 | 0.76446 | 0.55847 | 0.56763 | -123.4634 | 0.58594 | 0.50354 | 0.40741 | -123.4085
4788.0156 | 123.3307 | -0.49439 | 122.7814 | -0.11459 | 0.0085171 | 0.0043772 | 0.01583 | 0.025677 | -0.00071785 | -0.0081455 | -0.091705 | -0.005708 | 0.013422 | -0.0088247 | 0.024716 | -0.0051376 | 0.054932 | 0.14648 | 0.059509 | -0.27008 | 0.27924 | -0.50354 | -0.66834 | 0.059509 | -0.10529 | -0.032043 | 0.054932 | 0 | -0.59967 | -0.62256 | -0.009155 | -0.17395 | -122.5021 | 0.64087 | 0.2243 | 0.39825 | -122.7264 | -0.10529 | -0.12817 | -122.7264 | 0.55389 | 0.46234 | 0.59052 | -122.7814 | 0.77362 | 0.54932 | 0.55389 | -123.4497 | 0.54932 | 0.49439 | 0.3891 | -123.4039
4789.0156 | 123.2574 | -0.50812 | 122.7951 | -0.22141 | 0.018344 | 0.0052316 | 0.016898 | 0.026746 | 0.0046227 | -0.0053683 | -0.31296 | -0.003999 | 0.012781 | -0.010747 | 0.026852 | -0.0077012 | -0.018311 | 0 | -0.059509 | -0.34332 | 0.27008 | -0.53101 | -0.72327 | -0.022888 | -0.20142 | -0.16022 | 0.10071 | 0.022888 | -0.62714 | -0.64545 | -0.022888 | -0.21515 | -122.525 | 0.50812 | 0.16479 | 0.37994 | -122.8134 | -0.11902 | -0.13733 | -122.6944 | 0.48523 | 0.3479 | 0.48523 | -122.7722 | 0.7782 | 0.48981 | 0.44861 | -123.5184 | 0.60883 | 0.53101 | 0.3067 | -123.4406
4790.0156 | 123.2437 | -0.52185 | 122.8363 | -0.12985 | 0.014285 | 0.0054452 | 0.017111 | 0.028668 | 0.0016321 | -0.0075047 | -0.10696 | -0.0014356 | 0.016626 | -0.0096793 | 0.024716 | -0.0068466 | -0.022888 | 0.009155 | -0.073242 | -0.33417 | 0.28381 | -0.52643 | -0.71869 | -0.032043 | -0.1831 | -0.14648 | 0.09613 | 0.022888 | -0.62256 | -0.65002 | -0.004577 | -0.19684 | -122.5525 | 0.53101 | 0.18768 | 0.38452 | -122.8592 | -0.10071 | -0.12817 | -122.7402 | 0.48981 | 0.37537 | 0.50354 | -122.8134 | 0.80566 | 0.49896 | 0.44861 | -123.555 | 0.61798 | 0.54474 | 0.33875 | -123.4863
4791.0156 | 123.2162 | -0.53558 | 122.8271 | -0.20615 | 0.013858 | 0.0045908 | 0.014761 | 0.025464 | -0.00050425 | -0.0098545 | -0.21378 | -0.0033582 | 0.015344 | -0.0092521 | 0.022366 | -0.0044968 | -0.045776 | 0.022888 | -0.050354 | -0.36621 | 0.28381 | -0.52185 | -0.72784 | -0.068665 | -0.20142 | -0.14191 | 0.09613 | 0.027466 | -0.63629 | -0.6546 | 0.013732 | -0.19226 | -122.5433 | 0.55847 | 0.16937 | 0.36163 | -122.8729 | -0.10071 | -0.11902 | -122.731 | 0.46692 | 0.39368 | 0.5127 | -122.7997 | 0.8194 | 0.48981 | 0.48523 | -123.555 | 0.63171 | 0.56305 | 0.33417 | -123.4817
4792.0156 | 123.3215 | -0.48523 | 122.7722 | -0.26718 | 0.013003 | 0.0048044 | 0.014121 | 0.026959 | -0.0028541 | -0.0096409 | -0.084076 | -0.00464 | 0.013208 | -0.0094657 | 0.021512 | -0.0051376 | 0.032043 | 0.14191 | 0.059509 | -0.28839 | 0.23346 | -0.49896 | -0.67291 | 0.018311 | -0.086975 | -0.018311 | 0.073242 | -0.009155 | -0.59052 | -0.60883 | -0.013733 | -0.18768 | -122.5388 | 0.62714 | 0.19684 | 0.38452 | -122.7402 | -0.10529 | -0.1236 | -122.699 | 0.50354 | 0.46692 | 0.59052 | -122.7814 | 0.71869 | 0.51727 | 0.54474 | -123.4451 | 0.55847 | 0.47607 | 0.39825 | -123.381
4793.0156 | 123.2208 | -0.54474 | 122.7905 | -0.33585 | 0.013431 | 0.0054452 | 0.01647 | 0.025464 | -7.6852e-05 | -0.0089999 | -0.091705 | -0.0027174 | 0.013422 | -0.0098929 | 0.023221 | -0.0047104 | -0.045776 | -0.004578 | -0.064087 | -0.35248 | 0.30212 | -0.54932 | -0.71411 | -0.059509 | -0.23804 | -0.15564 | 0.09613 | 0.036621 | -0.62714 | -0.6546 | -0.004577 | -0.16937 | -122.4884 | 0.54016 | 0.19226 | 0.36163 | -122.8363 | -0.082397 | -0.10986 | -122.6944 | 0.48523 | 0.3891 | 0.49896 | -122.7539 | 0.84686 | 0.49896 | 0.48065 | -123.5046 | 0.64087 | 0.58136 | 0.3067 | -123.4451
4794.0156 | 123.317 | -0.48981 | 122.7722 | -0.20615 | 0.010226 | 0.0073678 | 0.014334 | 0.026959 | -0.0030677 | -0.010922 | -0.15274 | -0.0059216 | 0.013635 | -0.011602 | 0.023648 | -0.0040696 | 0.032043 | 0.16479 | 0.032043 | -0.28381 | 0.26093 | -0.48523 | -0.65918 | 0.027466 | -0.11444 | -0.064087 | 0.050354 | 0 | -0.58594 | -0.61798 | 0.004578 | -0.16937 | -122.5113 | 0.6546 | 0.20599 | 0.37537 | -122.7402 | -0.09613 | -0.12817 | -122.7219 | 0.51727 | 0.42572 | 0.55389 | -122.7722 | 0.75073 | 0.52185 | 0.52185 | -123.4314 | 0.54016 | 0.48981 | 0.37537 | -123.3902
4795.0156 | 123.2437 | -0.50354 | 122.7997 | -0.13748 | 0.016849 | 0.0052316 | 0.017539 | 0.026532 | 0.0048363 | -0.0070773 | -0.45792 | -0.0035718 | 0.014063 | -0.0098929 | 0.025784 | -0.0089828 | 0.004578 | 0.07782 | -0.022888 | -0.32044 | 0.29755 | -0.52185 | -0.70496 | -0.009155 | -0.17853 | -0.15564 | 0.082397 | 0.018311 | -0.63629 | -0.6546 | -0.018311 | -0.20142 | -122.5021 | 0.58136 | 0.1831 | 0.38452 | -122.7951 | -0.13275 | -0.15106 | -122.7173 | 0.49438 | 0.3479 | 0.49896 | -122.7814 | 0.80109 | 0.50812 | 0.48065 | -123.5046 | 0.58594 | 0.52185 | 0.32501 | -123.4543
4796.0156 | 123.3124 | -0.48065 | 122.7951 | -0.28244 | 0.010653 | 0.0052316 | 0.017111 | 0.025891 | -0.0032813 | -0.0096409 | -0.091705 | -0.0035718 | 0.012567 | -0.010106 | 0.023007 | -0.0070602 | 0.027466 | 0.14648 | 0.054932 | -0.29297 | 0.25177 | -0.51727 | -0.68665 | 0.009155 | -0.10071 | -0.064087 | 0.059509 | 0.004578 | -0.60883 | -0.62714 | -0.036621 | -0.20599 | -122.5433 | 0.62714 | 0.18768 | 0.39368 | -122.7676 | -0.12817 | -0.14648 | -122.7356 | 0.48981 | 0.41657 | 0.56305 | -122.7905 | 0.73242 | 0.50812 | 0.53558 | -123.4818 | 0.54016 | 0.48523 | 0.37994 | -123.4222
4797.0156 | 123.2574 | -0.50354 | 122.8088 | -0.18326 | 0.017489 | 0.0037362 | 0.016684 | 0.026318 | 0.0027001 | -0.0072911 | -0.12985 | -0.0016492 | 0.013849 | -0.013097 | 0.026425 | -0.0047104 | 0.036621 | -0.013733 | -0.032043 | -0.33875 | 0.29297 | -0.53101 | -0.71411 | -0.036621 | -0.18768 | -0.15106 | 0.07782 | 0.013733 | -0.61798 | -0.63171 | -0.027466 | -0.21057 | -122.5159 | 0.48981 | 0.16479 | 0.37537 | -122.7722 | -0.11444 | -0.12817 | -122.731 | 0.46692 | 0.35248 | 0.48065 | -122.7951 | 0.79651 | 0.54016 | 0.4715 | -123.5229 | 0.58136 | 0.51727 | 0.31586 | -123.4406
4798.0156 | 123.2254 | -0.53558 | 122.8088 | -0.12222 | 0.010867 | 0.0065134 | 0.016898 | 0.028668 | 0.00077755 | -0.0087863 | -0.25955 | -0.00229 | 0.015985 | -0.0096793 | 0.024289 | -0.0040696 | -0.054932 | -0.009155 | -0.07782 | -0.35248 | 0.31586 | -0.54474 | -0.71869 | -0.073242 | -0.23346 | -0.15564 | 0.09613 | 0.027466 | -0.6546 | -0.66834 | -0.009156 | -0.18311 | -122.493 | 0.52643 | 0.18311 | 0.36621 | -122.8638 | -0.11902 | -0.13275 | -122.7127 | 0.46234 | 0.37994 | 0.5127 | -122.7814 | 0.85144 | 0.48065 | 0.45776 | -123.5275 | 0.63171 | 0.56305 | 0.30212 | -123.4772
4799.0156 | 123.2758 | -0.51727 | 122.7951 | -0.30533 | 0.016421 | 0.0058724 | 0.017325 | 0.02525 | 0.0018457 | -0.0092137 | -0.17563 | -0.0020764 | 0.014704 | -0.011175 | 0.025143 | -0.005565 | -0.041199 | 0 | -0.064087 | -0.33875 | 0.28381 | -0.54932 | -0.71869 | -0.064087 | -0.1831 | -0.15564 | 0.10071 | 0.032043 | -0.65002 | -0.68207 | -0.032043 | -0.20142 | -122.5113 | 0.51727 | 0.17853 | 0.37994 | -122.8363 | -0.13275 | -0.1648 | -122.6944 | 0.45319 | 0.36163 | 0.52643 | -122.7631 | 0.80109 | 0.47607 | 0.45319 | -123.5138 | 0.61798 | 0.54932 | 0.33417 | -123.4772
4800.0156 | 123.2666 | -0.53558 | 122.7951 | -0.23666 | 0.013003 | 0.0052316 | 0.01583 | 0.023968 | -0.0011451 | -0.010068 | -0.19089 | -0.0061352 | 0.013849 | -0.010534 | 0.022794 | -0.0044968 | -0.041199 | 0.027466 | -0.036621 | -0.34332 | 0.27924 | -0.54016 | -0.71869 | -0.059509 | -0.21057 | -0.15564 | 0.09613 | 0.041199 | -0.64545 | -0.6546 | -0.004578 | -0.18311 | -122.5159 | 0.56305 | 0.19226 | 0.37537 | -122.8363 | -0.10986 | -0.11902 | -122.699 | 0.47607 | 0.37994 | 0.49896 | -122.7539 | 0.81482 | 0.49438 | 0.49896 | -123.5138 | 0.63171 | 0.57678 | 0.32501 | -123.4497
4801.0156 | 123.2803 | -0.53101 | 122.818 | -0.068817 | 0.014712 | 0.0054452 | 0.017966 | 0.028668 | -0.0015723 | -0.0094273 | -0.35873 | -0.003999 | 0.017053 | -0.010747 | 0.02258 | -0.0059922 | -0.059509 | -0.022888 | -0.082397 | -0.35706 | 0.29297 | -0.54016 | -0.72784 | -0.07782 | -0.23804 | -0.16479 | 0.10529 | 0.032043 | -0.63629 | -0.66834 | -0.009155 | -0.19684 | -122.525 | 0.50812 | 0.17395 | 0.37079 | -122.8775 | -0.10529 | -0.13733 | -122.7127 | 0.45319 | 0.36621 | 0.50354 | -122.7859 | 0.82397 | 0.4715 | 0.44861 | -123.5458 | 0.63629 | 0.56305 | 0.29297 | -123.4863
4802.0156 | 123.2071 | -0.54016 | 122.7905 | -0.19852 | 0.01578 | 0.0039498 | 0.016898 | 0.027173 | 0.0012047 | -0.011777 | -0.15274 | -0.001222 | 0.014917 | -0.010961 | 0.024289 | -0.0064194 | -0.082397 | 0.013733 | -0.064087 | -0.36621 | 0.3067 | -0.55389 | -0.72784 | -0.073242 | -0.22888 | -0.16479 | 0.09613 | 0.041199 | -0.65002 | -0.63171 | -0.013733 | -0.18768 | -122.4838 | 0.55389 | 0.17395 | 0.36163 | -122.8729 | -0.10986 | -0.091553 | -122.6944 | 0.46692 | 0.37537 | 0.46692 | -122.7493 | 0.84686 | 0.45776 | 0.47607 | -123.5184 | 0.63629 | 0.58136 | 0.31128 | -123.4222
4803.0156 | 123.2758 | -0.50354 | 122.7951 | -0.14511 | 0.01813 | 0.0056588 | 0.018179 | 0.024823 | 0.0031273 | -0.0079319 | -0.061188 | -0.0042126 | 0.013208 | -0.010961 | 0.02493 | -0.0059922 | -0.004578 | 0.073242 | -0.027466 | -0.31128 | 0.29297 | -0.51727 | -0.72327 | -0.022888 | -0.18768 | -0.14191 | 0.091553 | 0.022888 | -0.63629 | -0.64545 | -0.013733 | -0.21973 | -122.5021 | 0.57678 | 0.19226 | 0.41199 | -122.7997 | -0.13275 | -0.14191 | -122.7036 | 0.48065 | 0.36163 | 0.50354 | -122.7722 | 0.79651 | 0.49896 | 0.47607 | -123.5184 | 0.59509 | 0.52643 | 0.31586 | -123.4406
4804.0156 | 123.2529 | -0.53558 | 122.7859 | -0.3511 | 0.017276 | 0.0058724 | 0.015616 | 0.0276 | -0.00093145 | -0.0092137 | -0.21378 | -0.0027174 | 0.015131 | -0.011388 | 0.023007 | -0.005565 | -0.073242 | 0.009155 | -0.064087 | -0.3479 | 0.29297 | -0.55847 | -0.74158 | -0.068665 | -0.22888 | -0.15564 | 0.091553 | 0.036621 | -0.64087 | -0.64545 | -0.022889 | -0.20599 | -122.493 | 0.54474 | 0.18768 | 0.39368 | -122.8592 | -0.10529 | -0.10986 | -122.6944 | 0.46692 | 0.37994 | 0.48981 | -122.7493 | 0.82855 | 0.46234 | 0.4715 | -123.5275 | 0.62714 | 0.5722 | 0.3067 | -123.4314
4805.0156 | 123.2529 | -0.51727 | 122.8043 | -0.0077822 | 0.019626 | 0.0028818 | 0.017539 | 0.027173 | 0.0061181 | -0.0081455 | -0.12222 | -0.002931 | 0.015344 | -0.0083975 | 0.026639 | -0.0047104 | 0 | 0.045776 | -0.054932 | -0.34332 | 0.29297 | -0.5127 | -0.70496 | -0.045776 | -0.2243 | -0.16022 | 0.068665 | 0.018311 | -0.63629 | -0.64545 | 0.004578 | -0.18768 | -122.5113 | 0.56305 | 0.17395 | 0.36163 | -122.8043 | -0.11902 | -0.12817 | -122.7356 | 0.4715 | 0.35706 | 0.48523 | -122.7859 | 0.81024 | 0.51727 | 0.46234 | -123.5092 | 0.58594 | 0.53558 | 0.29297 | -123.4497
4806.0156 | 123.2437 | -0.54016 | 122.8455 | -0.21378 | 0.014499 | 0.0045908 | 0.017752 | 0.026746 | -0.0026405 | -0.0096409 | -0.22903 | -0.0027174 | 0.014276 | -0.0098929 | 0.023648 | -0.0068466 | -0.064087 | -0.013733 | -0.07782 | -0.36621 | 0.31586 | -0.52643 | -0.737 | -0.082397 | -0.2243 | -0.14648 | 0.09613 | 0.045776 | -0.65002 | -0.65918 | 0.013733 | -0.19684 | -122.5296 | 0.52643 | 0.17395 | 0.37079 | -122.9095 | -0.10986 | -0.11902 | -122.7493 | 0.45776 | 0.39368 | 0.5127 | -122.7997 | 0.85602 | 0.47607 | 0.46234 | -123.5825 | 0.63629 | 0.58594 | 0.31586 | -123.5046
4807.0156 | 123.2758 | -0.52643 | 122.8226 | -0.10696 | 0.018985 | 0.0065134 | 0.019461 | 0.028668 | 0.00056395 | -0.010068 | -0.076446 | -0.0025038 | 0.015985 | -0.010534 | 0.02493 | -0.0059922 | -0.036621 | -0.013733 | -0.059509 | -0.35248 | 0.29755 | -0.53558 | -0.72327 | -0.068665 | -0.17853 | -0.14191 | 0.091553 | 0.032043 | -0.63171 | -0.65918 | -0.009155 | -0.19684 | -122.525 | 0.5127 | 0.17395 | 0.37079 | -122.8592 | -0.10529 | -0.13275 | -122.731 | 0.45776 | 0.38452 | 0.51727 | -122.7905 | 0.82397 | 0.48981 | 0.46692 | -123.5458 | 0.61798 | 0.55847 | 0.3479 | -123.4818
4808.0156 | 123.2071 | -0.53101 | 122.8271 | -0.34348 | 0.017062 | 0.0086496 | 0.016043 | 0.026959 | -0.0026405 | -0.0096409 | -0.076446 | -0.00229 | 0.015772 | -0.011388 | 0.022153 | -0.0051376 | -0.059509 | -0.004578 | -0.07782 | -0.36621 | 0.29297 | -0.52185 | -0.72784 | -0.082397 | -0.23346 | -0.16022 | 0.091553 | 0.036621 | -0.64545 | -0.64087 | 0.009155 | -0.19684 | -122.5342 | 0.52643 | 0.16479 | 0.36163 | -122.8867 | -0.11444 | -0.10986 | -122.7356 | 0.44861 | 0.37079 | 0.48065 | -122.7905 | 0.82397 | 0.4715 | 0.45319 | -123.555 | 0.62256 | 0.56763 | 0.29755 | -123.468
4809.0156 | 123.2391 | -0.5127 | 122.7997 | -0.0383 | 0.022189 | 0.0048044 | 0.017111 | 0.0276 | 0.0022729 | -0.0075047 | -0.084076 | -0.0044264 | 0.017481 | -0.011388 | 0.025143 | -0.0085556 | 0.009155 | 0.036621 | -0.041199 | -0.33417 | 0.30212 | -0.5127 | -0.70496 | -0.045776 | -0.2243 | -0.19226 | 0.10071 | 0.009155 | -0.60425 | -0.6546 | 0 | -0.19226 | -122.4976 | 0.54932 | 0.17853 | 0.37079 | -122.7905 | -0.091553 | -0.14191 | -122.699 | 0.46692 | 0.32043 | 0.46234 | -122.7905 | 0.81482 | 0.52185 | 0.4715 | -123.5046 | 0.6134 | 0.52185 | 0.28839 | -123.4543
4810.0156 | 123.262 | -0.51727 | 122.8317 | -0.0077822 | 0.017703 | 0.0045908 | 0.017111 | 0.026318 | 0.00099115 | -0.0077183 | -0.099335 | -0.002931 | 0.018335 | -0.0098929 | 0.02493 | -0.0059922 | -0.032043 | 0 | -0.064087 | -0.3479 | 0.28839 | -0.52643 | -0.71411 | -0.041199 | -0.18768 | -0.13733 | 0.082397 | 0.036621 | -0.63171 | -0.6546 | -0.009155 | -0.19684 | -122.5433 | 0.51727 | 0.16937 | 0.36621 | -122.8638 | -0.11444 | -0.13733 | -122.7493 | 0.47607 | 0.37994 | 0.51727 | -122.7951 | 0.80566 | 0.48523 | 0.45319 | -123.5458 | 0.59967 | 0.55389 | 0.32959 | -123.4863
4811.0156 | 123.2346 | -0.51727 | 122.8088 | 0.037994 | 0.02048 | 0.0039498 | 0.017752 | 0.024609 | 0.0031273 | -0.0075047 | -0.015411 | -0.002931 | 0.017694 | -0.010106 | 0.025143 | -0.0057786 | -0.009155 | 0.018311 | -0.064087 | -0.33875 | 0.28381 | -0.5127 | -0.6958 | -0.041199 | -0.23804 | -0.16937 | 0.082397 | 0.022888 | -0.62714 | -0.64087 | 0.004578 | -0.17853 | -122.525 | 0.53558 | 0.17853 | 0.35706 | -122.818 | -0.10986 | -0.1236 | -122.7264 | 0.47607 | 0.3479 | 0.4715 | -122.7859 | 0.80109 | 0.50812 | 0.45319 | -123.5046 | 0.59967 | 0.54016 | 0.27924 | -123.4497
4812.0156 | 123.2529 | -0.50812 | 122.7814 | -0.25192 | 0.016635 | 0.0018136 | 0.016684 | 0.026318 | 0.00056395 | -0.0075047 | -0.38162 | -0.0027174 | 0.013635 | -0.011388 | 0.02493 | -0.005565 | -0.032043 | 0.013733 | -0.041199 | -0.34332 | 0.27924 | -0.51727 | -0.72327 | -0.054932 | -0.18768 | -0.12817 | 0.082397 | 0.041199 | -0.62714 | -0.6546 | -0.009155 | -0.21515 | -122.5021 | 0.52185 | 0.16479 | 0.37994 | -122.8134 | -0.11902 | -0.14648 | -122.699 | 0.45319 | 0.37994 | 0.52643 | -122.7402 | 0.78735 | 0.47607 | 0.46692 | -123.5046 | 0.59051 | 0.54932 | 0.32043 | -123.436
4813.0156 | 123.2758 | -0.50812 | 122.8043 | -0.053558 | 0.019412 | 0.0018136 | 0.016684 | 0.027173 | 0.0014185 | -0.0087863 | 0.030365 | -0.002931 | 0.016626 | -0.01032 | 0.02493 | -0.0059922 | 0 | 0.009155 | -0.054932 | -0.33875 | 0.28839 | -0.52185 | -0.69122 | -0.050354 | -0.23346 | -0.1831 | 0.086975 | 0.036621 | -0.63171 | -0.65002 | -0.013733 | -0.18311 | -122.5159 | 0.51727 | 0.16937 | 0.35248 | -122.8043 | -0.1236 | -0.14191 | -122.7173 | 0.45776 | 0.32501 | 0.46692 | -122.7676 | 0.79651 | 0.50812 | 0.45319 | -123.4955 | 0.59509 | 0.54474 | 0.27466 | -123.4543
4814.0156 | 123.2254 | -0.52185 | 122.8271 | -0.015411 | 0.02048 | 0.0020272 | 0.01647 | 0.026532 | 0.0029137 | -0.0070773 | 0.015106 | -0.0035718 | 0.015131 | -0.010106 | 0.023648 | -0.0064194 | -0.018311 | 0.045776 | -0.045776 | -0.35248 | 0.27466 | -0.52643 | -0.69122 | -0.059509 | -0.22888 | -0.16937 | 0.091553 | 0.041199 | -0.6134 | -0.65918 | -0.004577 | -0.16937 | -122.5525 | 0.56763 | 0.16937 | 0.33875 | -122.8455 | -0.091552 | -0.13733 | -122.7356 | 0.46234 | 0.35248 | 0.48981 | -122.7859 | 0.79651 | 0.50354 | 0.47607 | -123.5184 | 0.6134 | 0.56305 | 0.29297 | -123.4863
4815.0156 | 123.2391 | -0.5127 | 122.8455 | 0.12192 | 0.020907 | 0.0037362 | 0.019034 | 0.025464 | 0.0018457 | -0.0094273 | 0.076141 | -0.0014356 | 0.017053 | -0.0071157 | 0.024716 | -0.0051376 | -0.032043 | -0.036621 | -0.10529 | -0.36621 | 0.3067 | -0.50812 | -0.70496 | -0.11444 | -0.27924 | -0.21515 | 0.082397 | 0.050354 | -0.64545 | -0.66376 | 0.004577 | -0.19226 | -122.5388 | 0.47607 | 0.14648 | 0.33875 | -122.8775 | -0.13275 | -0.15106 | -122.7631 | 0.39825 | 0.29755 | 0.44861 | -122.7951 | 0.8194 | 0.48065 | 0.40741 | -123.5504 | 0.59509 | 0.56305 | 0.23346 | -123.5092
4816.0156 | 123.2666 | -0.50812 | 122.818 | -0.17563 | 0.019198 | 0.0045908 | 0.017539 | 0.026532 | 0.00077755 | -0.0092137 | -0.17563 | -0.0031446 | 0.015985 | -0.01032 | 0.023434 | -0.006633 | -0.013733 | 0.027466 | -0.059509 | -0.32044 | 0.27466 | -0.52643 | -0.72784 | -0.045776 | -0.20599 | -0.13275 | 0.082397 | 0.032043 | -0.63171 | -0.6546 | -0.01831 | -0.21973 | -122.5433 | 0.53558 | 0.18768 | 0.40741 | -122.8317 | -0.1236 | -0.14648 | -122.7356 | 0.46234 | 0.37537 | 0.52185 | -122.7859 | 0.78278 | 0.49438 | 0.44861 | -123.5458 | 0.59051 | 0.54016 | 0.30212 | -123.4726
4817.0156 | 123.2758 | -0.50354 | 122.7859 | 0.24399 | 0.018344 | 0.0035226 | 0.017325 | 0.026318 | 0.00035035 | -0.0083591 | 0.19821 | -0.00015376 | 0.014917 | -0.0092521 | 0.023862 | -0.0044968 | -0.041199 | -0.022888 | -0.068665 | -0.3479 | 0.28839 | -0.5127 | -0.6958 | -0.036621 | -0.23804 | -0.11444 | 0.091553 | 0.022888 | -0.6134 | -0.63629 | -0.009155 | -0.19226 | -122.4976 | 0.48065 | 0.15564 | 0.3479 | -122.8271 | -0.10986 | -0.13275 | -122.6944 | 0.46692 | 0.3891 | 0.52185 | -122.7631 | 0.79193 | 0.46234 | 0.43488 | -123.4818 | 0.59509 | 0.52643 | 0.2655 | -123.4222
4818.0156 | 123.317 | -0.52643 | 122.7951 | -0.17563 | 0.020267 | 0.0043772 | 0.017325 | 0.026105 | 0.0018457 | -0.0085727 | -0.11459 | -0.0027174 | 0.015772 | -0.010106 | 0.024075 | -0.005565 | 0.022888 | 0.018311 | -0.041199 | -0.34332 | 0.28839 | -0.52185 | -0.70953 | -0.032043 | -0.2243 | -0.16022 | 0.073242 | 0.054932 | -0.63171 | -0.63629 | 0.004577 | -0.18311 | -122.5067 | 0.54474 | 0.18311 | 0.36621 | -122.7722 | -0.10529 | -0.10986 | -122.7219 | 0.49439 | 0.36621 | 0.47607 | -122.7402 | 0.81482 | 0.54932 | 0.48523 | -123.5046 | 0.59967 | 0.58136 | 0.30212 | -123.4314
4819.0156 | 123.2666 | -0.53101 | 122.8317 | -0.03067 | 0.021762 | 0.0045908 | 0.019034 | 0.02525 | 0.0029137 | -0.0089999 | 0.083771 | -0.0014356 | 0.015558 | -0.010747 | 0.024716 | -0.003856 | -0.032043 | -0.027466 | -0.10071 | -0.35706 | 0.27924 | -0.52643 | -0.6958 | -0.10529 | -0.29297 | -0.20599 | 0.091553 | 0.027466 | -0.65002 | -0.6546 | 0.004578 | -0.1648 | -122.5525 | 0.50354 | 0.17395 | 0.33875 | -122.8638 | -0.11902 | -0.1236 | -122.7402 | 0.42572 | 0.32501 | 0.44861 | -122.8043 | 0.81024 | 0.49896 | 0.4303 | -123.5275 | 0.62256 | 0.55847 | 0.23804 | -123.4863
4820.0156 | 123.2529 | -0.52185 | 122.8043 | 0.14481 | 0.017917 | 0.0024544 | 0.015402 | 0.026105 | 0.0024865 | -0.0085727 | -0.091705 | -0.0027174 | 0.016626 | -0.014165 | 0.024503 | -0.0057786 | 0.032043 | 0.027466 | -0.045776 | -0.33417 | 0.30212 | -0.51727 | -0.71411 | -0.032043 | -0.18768 | -0.14648 | 0.086975 | 0.036621 | -0.62256 | -0.64087 | 0.004578 | -0.19226 | -122.5021 | 0.54932 | 0.18768 | 0.37994 | -122.7722 | -0.10071 | -0.11902 | -122.7173 | 0.48981 | 0.37537 | 0.49439 | -122.7676 | 0.82397 | 0.55389 | 0.47607 | -123.5184 | 0.60883 | 0.55847 | 0.33417 | -123.4451
4821.0156 | 123.2483 | -0.50812 | 122.8134 | -0.015411 | 0.019198 | 0.0026682 | 0.020102 | 0.028027 | 0.0014185 | -0.0079319 | -0.038299 | -0.0035718 | 0.014917 | -0.0096793 | 0.023648 | -0.0053512 | 0.009155 | -0.004578 | -0.068665 | -0.33875 | 0.28839 | -0.51727 | -0.70953 | -0.050354 | -0.24261 | -0.16479 | 0.073242 | 0.022888 | -0.6134 | -0.6546 | -0.009155 | -0.20142 | -122.525 | 0.50354 | 0.16937 | 0.37079 | -122.8043 | -0.10529 | -0.14648 | -122.7402 | 0.45776 | 0.34332 | 0.48981 | -122.7905 | 0.79651 | 0.51727 | 0.43945 | -123.523 | 0.58136 | 0.53101 | 0.2655 | -123.468
4822.0156 | 123.2666 | -0.52185 | 122.8317 | -0.0383 | 0.021335 | 0.006086 | 0.016684 | 0.026318 | -7.6852e-05 | -0.0094273 | 0.045624 | -0.0025038 | 0.014063 | -0.010747 | 0.025143 | -0.005565 | -0.009155 | 0.050354 | -0.041199 | -0.33417 | 0.28381 | -0.52185 | -0.70496 | -0.022888 | -0.19684 | -0.15106 | 0.07782 | 0.050354 | -0.60425 | -0.6546 | 0 | -0.18311 | -122.5479 | 0.5722 | 0.18768 | 0.37079 | -122.8409 | -0.082397 | -0.13275 | -122.7539 | 0.49896 | 0.37079 | 0.50354 | -122.7814 | 0.80566 | 0.5127 | 0.48065 | -123.5367 | 0.59967 | 0.5722 | 0.32501 | -123.4863
4823.0156 | 123.2071 | -0.52643 | 122.8363 | 0.022736 | 0.022189 | 0.0016 | 0.018179 | 0.026532 | 0.0029137 | -0.0060093 | 0.037995 | -0.0027174 | 0.014276 | -0.010106 | 0.023434 | -0.0042832 | -0.054932 | -0.045776 | -0.10529 | -0.35706 | 0.29297 | -0.50354 | -0.71411 | -0.09613 | -0.27008 | -0.19226 | 0.07782 | 0.059509 | -0.61798 | -0.6546 | 0.022888 | -0.18768 | -122.5433 | 0.48065 | 0.16937 | 0.35706 | -122.8912 | -0.091553 | -0.12817 | -122.7585 | 0.4303 | 0.33417 | 0.46234 | -122.7768 | 0.8194 | 0.4715 | 0.42114 | -123.5504 | 0.60425 | 0.58594 | 0.25635 | -123.4909
4824.375 | 123.3627 | -0.4715 | 122.7951 | 0.15244 | 0.014712 | 0.0022408 | 0.01583 | 0.026746 | -0.0011451 | -0.010922 | 0.26688 | -0.0033582 | 0.016199 | -0.0092521 | 0.021939 | -0.0036424 | 0.027466 | 0.10071 | 0.027466 | -0.27466 | 0.24261 | -0.47607 | -0.65918 | 0.022888 | -0.15106 | -0.045776 | 0.059509 | -0.004578 | -0.59509 | -0.59967 | -0.004577 | -0.18768 | -122.5525 | 0.5722 | 0.19684 | 0.38452 | -122.7676 | -0.1236 | -0.12817 | -122.7356 | 0.49439 | 0.42572 | 0.55389 | -122.7997 | 0.71411 | 0.49896 | 0.49896 | -123.4543 | 0.53101 | 0.46692 | 0.32044 | -123.3948
4825.0156 | 123.2162 | -0.5127 | 122.8271 | -0.03067 | 0.019626 | 0.0041634 | 0.017966 | 0.025891 | 0.0035547 | -0.0094273 | -0.00015237 | -0.0035718 | 0.017481 | -0.0094657 | 0.024503 | -0.0068466 | -0.050354 | -0.050354 | -0.10529 | -0.35248 | 0.28839 | -0.53101 | -0.70038 | -0.10071 | -0.28381 | -0.20599 | 0.09613 | 0.064087 | -0.63629 | -0.65002 | -0.018311 | -0.18768 | -122.5388 | 0.46234 | 0.16022 | 0.3479 | -122.8775 | -0.1236 | -0.13733 | -122.731 | 0.41199 | 0.3067 | 0.44403 | -122.7631 | 0.80109 | 0.46234 | 0.40741 | -123.5275 | 0.60882 | 0.57678 | 0.22888 | -123.4772
4826.0156 | 123.2849 | -0.52185 | 122.818 | -0.053558 | 0.019626 | 0.0028818 | 0.01647 | 0.029309 | 0.0014185 | -0.0083591 | -0.2214 | -0.0033582 | 0.015558 | -0.011175 | 0.025571 | -0.0077012 | 0.018311 | 0.032043 | -0.050354 | -0.31128 | 0.28381 | -0.50812 | -0.68207 | -0.041199 | -0.19684 | -0.13733 | 0.082397 | 0.041199 | -0.62256 | -0.63629 | 0.013733 | -0.16022 | -122.5342 | 0.55389 | 0.21057 | 0.37079 | -122.7997 | -0.10071 | -0.11444 | -122.7356 | 0.48065 | 0.38452 | 0.49896 | -122.7768 | 0.80566 | 0.54016 | 0.4715 | -123.5001 | 0.60425 | 0.56305 | 0.32501 | -123.4543
4827.0156 | 123.2391 | -0.5127 | 122.8455 | -0.045929 | 0.02048 | 0.003309 | 0.016043 | 0.026746 | 0.0031273 | -0.0087863 | 0.015106 | -0.0018628 | 0.015772 | -0.010961 | 0.025357 | -0.004924 | -0.050354 | -0.045776 | -0.09613 | -0.35248 | 0.29297 | -0.52185 | -0.70496 | -0.091553 | -0.30212 | -0.20599 | 0.09613 | 0.050354 | -0.63171 | -0.6546 | -0.009156 | -0.19226 | -122.5525 | 0.46692 | 0.16022 | 0.35248 | -122.8958 | -0.11902 | -0.14191 | -122.7493 | 0.42114 | 0.3067 | 0.44861 | -122.7951 | 0.80566 | 0.46234 | 0.41657 | -123.5504 | 0.60882 | 0.56305 | 0.21057 | -123.5001
4828.0156 | 123.2849 | -0.50354 | 122.8226 | -0.099335 | 0.020907 | 0.0043772 | 0.016684 | 0.025037 | -0.00050425 | -0.0075047 | -0.12985 | -0.0020764 | 0.013849 | -0.011602 | 0.02258 | -0.0057786 | 0 | 0.032043 | -0.036621 | -0.33875 | 0.27924 | -0.52643 | -0.70038 | -0.032043 | -0.19684 | -0.15564 | 0.073242 | 0.050354 | -0.60883 | -0.63629 | -0.022888 | -0.19684 | -122.5433 | 0.53558 | 0.16479 | 0.36163 | -122.8226 | -0.10529 | -0.13275 | -122.7493 | 0.4715 | 0.3479 | 0.48065 | -122.7722 | 0.78278 | 0.50354 | 0.46692 | -123.5229 | 0.57678 | 0.55389 | 0.3067 | -123.4589
4829.0156 | 123.2666 | -0.54474 | 122.8271 | 0.15244 | 0.018558 | 0.0041634 | 0.017752 | 0.025677 | -0.00029045 | -0.01135 | 0.2211 | -0.0031446 | 0.012567 | -0.013097 | 0.026212 | -0.0053512 | -0.054932 | -0.036621 | -0.09613 | -0.37079 | 0.29755 | -0.51727 | -0.70496 | -0.082397 | -0.30212 | -0.17395 | 0.10986 | 0.045776 | -0.62714 | -0.6546 | 0.027466 | -0.16022 | -122.5296 | 0.50812 | 0.17395 | 0.33417 | -122.8821 | -0.082397 | -0.10986 | -122.7173 | 0.46234 | 0.37079 | 0.48065 | -122.7814 | 0.84228 | 0.48981 | 0.44861 | -123.5321 | 0.6546 | 0.59052 | 0.24261 | -123.4817
4830.0156 | 123.2483 | -0.5127 | 122.8409 | 0.030365 | 0.020053 | 0.0056588 | 0.016898 | 0.027173 | 0.0016321 | -0.0096409 | -0.091705 | -0.0025038 | 0.017267 | -0.010106 | 0.024075 | -0.005565 | 0 | 0.013733 | -0.082397 | -0.32501 | 0.29755 | -0.52185 | -0.68665 | -0.064087 | -0.24261 | -0.17395 | 0.091553 | 0.050354 | -0.61798 | -0.63171 | -0.009156 | -0.17395 | -122.5433 | 0.52643 | 0.18768 | 0.36163 | -122.8409 | -0.10529 | -0.11902 | -122.7493 | 0.44861 | 0.33875 | 0.45776 | -122.7905 | 0.81024 | 0.5127 | 0.4303 | -123.5275 | 0.60425 | 0.56305 | 0.27008 | -123.4726
4831.0156 | 123.2437 | -0.52185 | 122.8134 | 0.0914 | 0.021976 | 0.0041634 | 0.016257 | 0.026959 | 0.00013675 | -0.0075047 | 0.14481 | -0.0025038 | 0.017053 | -0.0088247 | 0.024716 | -0.0030014 | -0.050354 | -0.041199 | -0.09613 | -0.37537 | 0.29297 | -0.54932 | -0.70953 | -0.082397 | -0.27924 | -0.17853 | 0.091553 | 0.045776 | -0.6134 | -0.63629 | -0.027465 | -0.18768 | -122.5204 | 0.48065 | 0.14648 | 0.33417 | -122.8638 | -0.091552 | -0.11444 | -122.7219 | 0.43945 | 0.34332 | 0.45776 | -122.7676 | 0.81482 | 0.4715 | 0.42572 | -123.523 | 0.6134 | 0.56763 | 0.24261 | -123.4497
4832.0156 | 123.3673 | -0.47607 | 122.8088 | 0.21347 | 0.01578 | 0.0035226 | 0.016898 | 0.026318 | -0.0041357 | -0.0096409 | 0.23636 | -0.00464 | 0.013635 | -0.012029 | 0.022366 | -0.003856 | 0.036621 | 0.086975 | 0.022888 | -0.28839 | 0.21973 | -0.4715 | -0.66376 | 0.022888 | -0.14648 | -0.059509 | 0.054932 | 0.027466 | -0.58136 | -0.60425 | 0.004577 | -0.18768 | -122.5891 | 0.56305 | 0.18768 | 0.37537 | -122.7722 | -0.10529 | -0.12817 | -122.7539 | 0.49896 | 0.41657 | 0.54474 | -122.7814 | 0.6958 | 0.5127 | 0.49896 | -123.4726 | 0.53101 | 0.50354 | 0.32959 | -123.4131
4833.0156 | 123.23 | -0.52643 | 122.8363 | 0.20584 | 0.018985 | 0.0052316 | 0.016684 | 0.026532 | 0.0020593 | -0.0083591 | 0.0914 | -0.0044264 | 0.015131 | -0.012243 | 0.024289 | -0.0047104 | -0.022888 | -0.054932 | -0.10071 | -0.36621 | 0.29755 | -0.52185 | -0.71411 | -0.064087 | -0.27466 | -0.15564 | 0.07782 | 0.045776 | -0.60425 | -0.6546 | 0.004577 | -0.18768 | -122.5388 | 0.4715 | 0.16022 | 0.3479 | -122.8592 | -0.07782 | -0.12817 | -122.7585 | 0.46234 | 0.37079 | 0.49896 | -122.7905 | 0.82397 | 0.50354 | 0.42572 | -123.5504 | 0.60425 | 0.5722 | 0.25177 | -123.4909
4834.0156 | 123.262 | -0.5127 | 122.8363 | -0.053558 | 0.019626 | 0.0039498 | 0.016898 | 0.028027 | 0.0016321 | -0.0081455 | -0.061188 | -0.003999 | 0.017053 | -0.011388 | 0.024503 | -0.0068466 | 0.041199 | 0.032043 | -0.059509 | -0.34332 | 0.27466 | -0.50354 | -0.6958 | -0.022888 | -0.20599 | -0.15106 | 0.082397 | 0.050354 | -0.62256 | -0.62714 | 0.009155 | -0.18311 | -122.5616 | 0.54474 | 0.16937 | 0.35248 | -122.7951 | -0.10986 | -0.11444 | -122.7539 | 0.48981 | 0.36163 | 0.47607 | -122.7859 | 0.78735 | 0.55389 | 0.45319 | -123.5321 | 0.59509 | 0.56305 | 0.3067 | -123.4634
4835.0156 | 123.23 | -0.52185 | 122.8271 | 0.099029 | 0.02048 | 0.0037362 | 0.017111 | 0.025891 | 0.0016321 | -0.0096409 | 0.076141 | -0.0033582 | 0.015772 | -0.010534 | 0.025571 | -0.003856 | -0.054932 | -0.064087 | -0.11444 | -0.37079 | 0.28839 | -0.52185 | -0.70953 | -0.07782 | -0.27924 | -0.20142 | 0.09613 | 0.050354 | -0.6134 | -0.65918 | 0 | -0.18768 | -122.5388 | 0.45776 | 0.15106 | 0.33875 | -122.8821 | -0.091552 | -0.13733 | -122.731 | 0.44403 | 0.32043 | 0.45776 | -122.7768 | 0.81024 | 0.46692 | 0.40741 | -123.5367 | 0.61798 | 0.5722 | 0.24261 | -123.4863
4836.0156 | 123.2574 | -0.5127 | 122.8455 | 0.053253 | 0.019626 | 0.0026682 | 0.016898 | 0.026105 | 0.00056395 | -0.0092137 | 0.13718 | -0.0033582 | 0.018762 | -0.010106 | 0.024503 | -0.0044968 | -0.064087 | -0.09613 | -0.11444 | -0.37994 | 0.30212 | -0.52185 | -0.71869 | -0.086975 | -0.28839 | -0.1831 | 0.09613 | 0.059509 | -0.63629 | -0.65002 | -0.009156 | -0.20599 | -122.5433 | 0.41657 | 0.13275 | 0.33875 | -122.9095 | -0.1236 | -0.13733 | -122.7493 | 0.42572 | 0.32959 | 0.46692 | -122.7859 | 0.81482 | 0.44861 | 0.39825 | -123.5641 | 0.60882 | 0.5722 | 0.2243 | -123.4955
4837.0156 | 123.3536 | -0.48981 | 122.7997 | -0.0077822 | 0.012362 | 0.010359 | 0.011984 | 0.025677 | -0.0073401 | -0.01135 | 0.12192 | -0.0044264 | 0.012995 | -0.012243 | 0.022366 | -0.003215 | -0.045776 | 0.045776 | 0 | -0.32044 | 0.2655 | -0.48981 | -0.66834 | -0.032043 | -0.16479 | -0.036621 | 0.059509 | 0.022888 | -0.59967 | -0.61798 | 0 | -0.17853 | -122.5342 | 0.53558 | 0.16937 | 0.3479 | -122.8455 | -0.10986 | -0.12817 | -122.7402 | 0.45776 | 0.45319 | 0.58136 | -122.7768 | 0.75531 | 0.44403 | 0.48981 | -123.468 | 0.54932 | 0.5127 | 0.32501 | -123.4177
4838.0156 | 0.07782 | -0.054932 | 0.21057 | 0.16006 | 0.017489 | 0.0045908 | 0.016257 | 0.025037 | 0.0031273 | -0.010495 | 0.12192 | -0.0031446 | 0.014917 | -0.015447 | 0.016385 | -0.0072738 | -0.009155 | -0.050354 | -0.045776 | -0.004578 | 0.3067 | -0.09613 | -0.29297 | -0.050354 | -0.07782 | -0.082397 | 0.24261 | 0.19684 | -0.20599 | -0.24719 | -0.041198 | -0.23804 | 0.096131 | 0.004578 | 0.050354 | 0.28839 | -0.21973 | -0.15106 | -0.19226 | 0.032044 | 0.004578 | -0.027465 | 0.16479 | -0.013733 | 0.36163 | 0.045777 | 0.009156 | -0.50354 | 0.29755 | 0.25177 | -0.022888 | -0.45776
4839.0156 | 0.15106 | -0.018311 | 0.17853 | 0.23636 | 0.018344 | 0.0037362 | 0.016898 | 0.026532 | 0.00035035 | -0.010282 | 0.11429 | -0.003999 | 0.016626 | -0.014379 | 0.017453 | -0.005565 | 0.054932 | 0.10071 | 0.07782 | 0.073242 | 0.27466 | -0.07782 | -0.2655 | 0.036621 | 0.064087 | 0.054932 | 0.1831 | 0.14191 | -0.17395 | -0.19684 | -0.059509 | -0.24719 | 0.09613 | 0.11902 | 0.091553 | 0.33874 | -0.1236 | -0.15564 | -0.17853 | 0.004577 | 0.054932 | 0.073243 | 0.25177 | -0.036621 | 0.29297 | 0.073243 | 0.096131 | -0.44403 | 0.20142 | 0.16022 | 0.082398 | -0.37537
4840.0156 | 0.036621 | -0.064087 | 0.22888 | 0.13718 | 0.019198 | 0.005018 | 0.01647 | 0.023968 | 0.00013675 | -0.010709 | 0.15244 | -0.0020764 | 0.016626 | -0.012243 | 0.016385 | -0.003856 | -0.013733 | -0.032043 | -0.045776 | 0.004578 | 0.31586 | -0.10986 | -0.29297 | -0.036621 | -0.082397 | -0.059509 | 0.25177 | 0.1831 | -0.21515 | -0.24261 | -0.045776 | -0.22888 | 0.086975 | 0.032044 | 0.068665 | 0.29755 | -0.24261 | -0.15106 | -0.17853 | 0.022888 | 0.027466 | 0.004578 | 0.18311 | -0.045777 | 0.37994 | 0.050354 | 0.018311 | -0.52185 | 0.31586 | 0.24719 | -0.01831 | -0.4715
4841.0156 | 0.11444 | -0.036621 | 0.21057 | 0.18295 | 0.01813 | 0.0035226 | 0.014975 | 0.02525 | 0.00035035 | -0.0094273 | 0.13718 | -0.0018628 | 0.017053 | -0.011815 | 0.016385 | -0.0044968 | 0.013733 | 0.004578 | 0.009155 | 0.022888 | 0.31128 | -0.10529 | -0.27466 | 0.004578 | -0.009155 | -0.009155 | 0.21057 | 0.17395 | -0.17853 | -0.20599 | -0.068665 | -0.23804 | 0.10071 | 0.041199 | 0.059509 | 0.29755 | -0.19684 | -0.14191 | -0.16937 | 0 | 0.041199 | 0.027466 | 0.19684 | -0.036621 | 0.3479 | 0.050354 | 0.045776 | -0.48523 | 0.24719 | 0.21057 | 0.027466 | -0.41657
4842.0625 | 0.041199 | -0.068665 | 0.23346 | -0.25955 | 0.01578 | 0.0062998 | 0.014761 | 0.023541 | -0.0030677 | -0.010922 | -0.10696 | -0.0042126 | 0.013208 | -0.014379 | 0.015103 | -0.004924 | -0.013733 | 0.050354 | -0.009155 | -0.009155 | 0.29297 | -0.10071 | -0.28839 | -0.054932 | 0 | -0.054932 | 0.25177 | 0.19684 | -0.23346 | -0.24719 | -0.032043 | -0.21973 | 0.05951 | 0.11902 | 0.05951 | 0.27924 | -0.24719 | -0.16479 | -0.17853 | 0.018311 | 0.013733 | 0.013733 | 0.19226 | -0.036621 | 0.36163 | 0.054932 | 0.05951 | -0.52185 | 0.32044 | 0.2655 | 0.068665 | -0.48065
4843.0156 | 0.13275 | -0.022888 | 0.19684 | 0.16769 | 0.016208 | 0.0092904 | 0.014121 | 0.025891 | -0.0032813 | -0.010495 | 0.16006 | -0.0048536 | 0.012354 | -0.016301 | 0.014249 | -0.0047104 | 0.068665 | 0.11902 | 0.086975 | 0.064087 | 0.27008 | -0.068665 | -0.24719 | 0.045776 | 0.054932 | 0.068665 | 0.20142 | 0.15564 | -0.19226 | -0.19684 | -0.045777 | -0.2243 | 0.073243 | 0.14191 | 0.086975 | 0.31128 | -0.12817 | -0.16937 | -0.17395 | 0.004578 | 0.068664 | 0.091553 | 0.2655 | -0.041198 | 0.29297 | 0.091553 | 0.10986 | -0.44403 | 0.2243 | 0.17853 | 0.07782 | -0.39368
4844.0156 | 0.14648 | -0.032043 | 0.19684 | 0.20584 | 0.018558 | 0.0043772 | 0.016257 | 0.02525 | 0.0022729 | -0.010495 | 0.19821 | -0.0033582 | 0.01684 | -0.013738 | 0.015744 | -0.0070602 | 0.036621 | 0.022888 | 0.022888 | 0.032043 | 0.32501 | -0.09613 | -0.27924 | 0.041199 | 0.027466 | 0.022888 | 0.21515 | 0.16022 | -0.17853 | -0.20142 | -0.064087 | -0.24719 | 0.12817 | 0.054931 | 0.064086 | 0.31128 | -0.16022 | -0.14648 | -0.16937 | 0.018311 | 0.073242 | 0.054931 | 0.2243 | -0.036621 | 0.35706 | 0.068664 | 0.054931 | -0.47607 | 0.24719 | 0.19226 | 0.059509 | -0.39825
4845.0156 | 0.1236 | -0.018311 | 0.1831 | 0.20584 | 0.015353 | 0.003309 | 0.015402 | 0.024609 | -0.0032813 | -0.0089999 | 0.16769 | -0.003999 | 0.011499 | -0.013097 | 0.012753 | -0.0062058 | 0.068665 | 0.10071 | 0.07782 | 0.064087 | 0.27924 | -0.07782 | -0.23804 | 0.059509 | 0.059509 | 0.045776 | 0.20142 | 0.15106 | -0.19226 | -0.21057 | -0.059509 | -0.21973 | 0.096131 | 0.11902 | 0.082398 | 0.30212 | -0.11444 | -0.17395 | -0.19226 | 0.018311 | 0.07782 | 0.064087 | 0.25635 | -0.032043 | 0.29755 | 0.086976 | 0.096131 | -0.42114 | 0.21973 | 0.16937 | 0.07782 | -0.39368
4846.0156 | 0.13733 | -0.022888 | 0.17853 | 0.11429 | 0.019626 | 0.0045908 | 0.01647 | 0.023968 | 0.00099115 | -0.010495 | 0.2211 | -0.0035718 | 0.014917 | -0.01267 | 0.016385 | -0.0074876 | 0.032043 | 0.022888 | 0.013733 | 0.032043 | 0.28381 | -0.086975 | -0.27008 | 0.050354 | 0.022888 | 0.022888 | 0.21057 | 0.15106 | -0.18768 | -0.19684 | -0.064087 | -0.24719 | 0.10528 | 0.045776 | 0.054931 | 0.30212 | -0.14648 | -0.16479 | -0.17395 | 0.032043 | 0.073242 | 0.045776 | 0.21973 | -0.027466 | 0.3067 | 0.054931 | 0.036621 | -0.44861 | 0.23346 | 0.17395 | 0.045776 | -0.37537
4847.0156 | 0.18768 | -0.009155 | 0.19226 | -0.12222 | 0.0095853 | 0.005018 | 0.014975 | 0.024609 | -0.0058447 | -0.012418 | -0.19089 | -0.0072034 | 0.010004 | -0.013311 | 0.012753 | -0.0057786 | 0.068665 | 0.14648 | 0.086975 | 0.073242 | 0.27008 | -0.073242 | -0.2655 | 0.041199 | 0.10986 | 0.07782 | 0.18768 | 0.15564 | -0.19226 | -0.21515 | -0.064087 | -0.25635 | 0.07782 | 0.15564 | 0.082397 | 0.33874 | -0.1236 | -0.18311 | -0.20599 | -0.004578 | 0.050354 | 0.086975 | 0.29297 | -0.036621 | 0.27924 | 0.07782 | 0.09613 | -0.45776 | 0.19684 | 0.16479 | 0.11902 | -0.40741
4848.0156 | 0.07782 | -0.059509 | 0.21973 | 0.19058 | 0.020053 | 0.0022408 | 0.018179 | 0.026318 | 0.0037683 | -0.0081455 | 0.12192 | -0.0052808 | 0.01684 | -0.011815 | 0.019162 | -0.0057786 | 0.018311 | -0.018311 | -0.036621 | 0.004578 | 0.32044 | -0.10071 | -0.28839 | -0.013733 | -0.054932 | -0.054932 | 0.24261 | 0.17395 | -0.21515 | -0.23346 | -0.041199 | -0.22888 | 0.10071 | 0.041198 | 0.064087 | 0.29297 | -0.20142 | -0.15564 | -0.17395 | 0.022888 | 0.045776 | 0.004577 | 0.17853 | -0.045777 | 0.37994 | 0.07782 | 0.022888 | -0.50812 | 0.30212 | 0.23346 | 0.004577 | -0.45319
4849.0156 | 0.16479 | -0.009155 | 0.20142 | 0.037994 | 0.016849 | 0.0035226 | 0.016043 | 0.026318 | 0.00013675 | -0.0083591 | 0.16006 | -0.0037854 | 0.013208 | -0.01267 | 0.018307 | -0.0072738 | 0.068665 | 0.11902 | 0.073242 | 0.091553 | 0.27466 | -0.064087 | -0.23804 | 0.073242 | 0.054932 | 0.059509 | 0.18768 | 0.13275 | -0.17853 | -0.19226 | -0.054932 | -0.22888 | 0.073242 | 0.12817 | 0.10071 | 0.32959 | -0.13275 | -0.16937 | -0.18311 | -0.013733 | 0.082397 | 0.068664 | 0.25177 | -0.068665 | 0.28381 | 0.07782 | 0.082397 | -0.43945 | 0.19684 | 0.14191 | 0.064087 | -0.39368
4850.0156 | 0.1236 | -0.027466 | 0.19684 | 0.15244 | 0.015994 | 0.0037362 | 0.016043 | 0.027173 | -0.0013587 | -0.0098545 | 0.21347 | -0.002931 | 0.015985 | -0.014165 | 0.016171 | -0.008342 | 0.09613 | 0.1236 | 0.082397 | 0.082397 | 0.28381 | -0.059509 | -0.25635 | 0.07782 | 0.07782 | 0.041199 | 0.19684 | 0.15564 | -0.17853 | -0.21057 | -0.032043 | -0.22888 | 0.086975 | 0.15106 | 0.10986 | 0.33875 | -0.10071 | -0.15106 | -0.18311 | 0 | 0.10529 | 0.068665 | 0.25177 | -0.041198 | 0.31128 | 0.1236 | 0.10986 | -0.45319 | 0.2243 | 0.18311 | 0.10529 | -0.40741
4851.0156 | 0.10529 | -0.022888 | 0.1831 | 0.20584 | 0.01279 | 0.0043772 | 0.01583 | 0.023328 | -0.0026405 | -0.010068 | 0.11429 | -0.0048536 | 0.015558 | -0.013311 | 0.016385 | -0.0047104 | 0.064087 | 0.091553 | 0.059509 | 0.032043 | 0.27924 | -0.091553 | -0.26093 | 0.045776 | 0.036621 | 0.036621 | 0.18768 | 0.16022 | -0.16479 | -0.21057 | -0.068665 | -0.23804 | 0.096131 | 0.11444 | 0.054931 | 0.29297 | -0.11902 | -0.14191 | -0.18768 | 0.004578 | 0.068664 | 0.059509 | 0.24719 | -0.022888 | 0.30212 | 0.086975 | 0.082397 | -0.44403 | 0.21057 | 0.1831 | 0.059509 | -0.39368
4852.0156 | 0.10071 | -0.032043 | 0.19684 | -0.03067 | 0.011935 | 0.0062998 | 0.016257 | 0.024182 | -0.0056311 | -0.0094273 | -0.27481 | -0.0054944 | 0.013422 | -0.01267 | 0.014676 | -0.0042832 | 0.036621 | 0.10071 | 0.068665 | 0.045776 | 0.29755 | -0.086975 | -0.27008 | 0.032043 | 0.073242 | 0.064087 | 0.20599 | 0.13733 | -0.19226 | -0.2243 | -0.054932 | -0.23804 | 0.10071 | 0.13275 | 0.077819 | 0.31586 | -0.16022 | -0.16022 | -0.19226 | 0.009156 | 0.064086 | 0.09613 | 0.28839 | -0.059509 | 0.32959 | 0.068664 | 0.10071 | -0.46692 | 0.23804 | 0.16937 | 0.10529 | -0.42114
4853.0156 | 0.064087 | -0.018311 | 0.17853 | 0.24399 | 0.013644 | 0.0048044 | 0.01647 | 0.0229 | -0.0013587 | -0.010709 | 0.25162 | -0.0054944 | 0.015558 | -0.016088 | 0.015317 | -0.0064194 | 0.07782 | 0.13275 | 0.07782 | 0.041199 | 0.27008 | -0.07782 | -0.24719 | 0.050354 | 0.050354 | 0.041199 | 0.19226 | 0.13275 | -0.17853 | -0.21515 | -0.059509 | -0.22888 | 0.091553 | 0.15106 | 0.05951 | 0.28839 | -0.10071 | -0.16022 | -0.19684 | 0.013733 | 0.068665 | 0.05951 | 0.25635 | -0.045777 | 0.28839 | 0.096131 | 0.096131 | -0.42572 | 0.21057 | 0.15106 | 0.068665 | -0.39368
4854.0156 | 0.16022 | -0.018311 | 0.16022 | 0.3508 | 0.017703 | 0.0048044 | 0.019675 | 0.025891 | 0.00099115 | -0.0094273 | 0.16006 | -0.002931 | 0.012995 | -0.015661 | 0.013821 | -0.0074876 | 0.091553 | 0.082397 | 0.054932 | 0.068665 | 0.27008 | -0.068665 | -0.2655 | 0.073242 | 0.073242 | 0.041199 | 0.19226 | 0.14648 | -0.17853 | -0.19684 | -0.050354 | -0.24719 | 0.10986 | 0.10071 | 0.086976 | 0.33417 | -0.068664 | -0.16022 | -0.17853 | 0.032044 | 0.091553 | 0.05951 | 0.23804 | -0.013733 | 0.28839 | 0.10986 | 0.073243 | -0.42572 | 0.21057 | 0.16479 | 0.091553 | -0.35706
4855.0156 | 0.17395 | -0.013733 | 0.18768 | 0.015106 | 0.014499 | 0.0056588 | 0.013907 | 0.026746 | -0.00029045 | -0.010068 | 0.16006 | -0.003999 | 0.016626 | -0.013738 | 0.017239 | -0.0070602 | 0.10071 | 0.10071 | 0.073242 | 0.07782 | 0.27466 | -0.07782 | -0.24261 | 0.07782 | 0.082397 | 0.050354 | 0.17853 | 0.13733 | -0.17853 | -0.19684 | -0.064087 | -0.22888 | 0.086975 | 0.11444 | 0.091553 | 0.32044 | -0.086975 | -0.16479 | -0.18311 | -0.009155 | 0.091553 | 0.064087 | 0.24719 | -0.050354 | 0.28839 | 0.11444 | 0.086975 | -0.4303 | 0.19226 | 0.15106 | 0.09613 | -0.38452
4856.0156 | 0.07782 | -0.045776 | 0.21057 | 0.0914 | 0.016421 | 0.003309 | 0.016257 | 0.023541 | 0.0024865 | -0.0089999 | 0.28976 | -0.003999 | 0.015985 | -0.013524 | 0.016171 | -0.0068466 | 0.027466 | 0.013733 | -0.027466 | -0.004578 | 0.29755 | -0.09613 | -0.28381 | 0.009155 | -0.027466 | -0.045776 | 0.22888 | 0.16479 | -0.21973 | -0.23804 | -0.050354 | -0.23804 | 0.086975 | 0.059509 | 0.041198 | 0.27923 | -0.18311 | -0.17395 | -0.19226 | 0.018311 | 0.054931 | 0 | 0.19226 | -0.045776 | 0.34332 | 0.073242 | 0.01831 | -0.49438 | 0.27466 | 0.21057 | 0.01831 | -0.44861
4857.0156 | 0.14648 | -0.018311 | 0.20599 | 0.076141 | 0.012576 | 0.005018 | 0.014975 | 0.024609 | -0.0056311 | -0.0089999 | 0.076141 | -0.003999 | 0.014063 | -0.015233 | 0.01489 | -0.0027878 | 0.009155 | 0.073242 | 0.054932 | 0.045776 | 0.2655 | -0.073242 | -0.26093 | 0.041199 | 0.009155 | 0.041199 | 0.19684 | 0.15106 | -0.17853 | -0.20599 | -0.054931 | -0.24261 | 0.059509 | 0.091553 | 0.064087 | 0.3067 | -0.19684 | -0.16022 | -0.18768 | -0.009156 | 0.05951 | 0.05951 | 0.24719 | -0.054932 | 0.28381 | 0.027466 | 0.073243 | -0.46692 | 0.21515 | 0.16937 | 0.027466 | -0.41199
4858.0156 | 0.14648 | -0.018311 | 0.18768 | 0.18295 | 0.019412 | 0.005018 | 0.012839 | 0.024823 | 0.00013675 | -0.0087863 | 0.16006 | -0.00464 | 0.014276 | -0.014379 | 0.016598 | -0.0074876 | 0.086975 | 0.13275 | 0.086975 | 0.086975 | 0.27466 | -0.073242 | -0.26093 | 0.082397 | 0.073242 | 0.068665 | 0.1831 | 0.13275 | -0.1831 | -0.19226 | -0.054931 | -0.24261 | 0.086975 | 0.15106 | 0.10529 | 0.3479 | -0.10071 | -0.16479 | -0.17395 | -0.004578 | 0.10071 | 0.086976 | 0.26093 | -0.054932 | 0.29297 | 0.10529 | 0.10529 | -0.44861 | 0.20142 | 0.15106 | 0.091553 | -0.37994
4859.0156 | 0.13275 | -0.045776 | 0.1831 | 0.12192 | 0.011722 | 0.006727 | 0.017325 | 0.025677 | -0.0030677 | -0.0083591 | -0.061188 | -0.0035718 | 0.010217 | -0.014806 | 0.01553 | -0.0068466 | 0.027466 | 0.09613 | 0.050354 | 0.027466 | 0.29297 | -0.073242 | -0.25635 | 0.032043 | 0.050354 | 0.045776 | 0.20599 | 0.15106 | -0.16937 | -0.20142 | -0.027466 | -0.21057 | 0.10986 | 0.14191 | 0.073242 | 0.28381 | -0.15564 | -0.1236 | -0.15564 | 0.022889 | 0.077819 | 0.091552 | 0.24719 | -0.032043 | 0.33874 | 0.073242 | 0.09613 | -0.43945 | 0.25177 | 0.19684 | 0.09613 | -0.38452
4860.0156 | 0.13733 | -0.032043 | 0.1831 | 0.2211 | 0.018344 | 0.0028818 | 0.015402 | 0.023968 | 0.0024865 | -0.0087863 | 0.20584 | -0.0042126 | 0.016199 | -0.012243 | 0.016385 | -0.008342 | 0.086975 | 0.11902 | 0.07782 | 0.073242 | 0.27924 | -0.082397 | -0.24261 | 0.07782 | 0.07782 | 0.050354 | 0.20599 | 0.13275 | -0.1831 | -0.1831 | -0.050354 | -0.21057 | 0.096131 | 0.15106 | 0.10529 | 0.31586 | -0.09613 | -0.15106 | -0.15106 | 0.022889 | 0.10986 | 0.082397 | 0.23346 | -0.050354 | 0.31128 | 0.11902 | 0.10986 | -0.42572 | 0.23804 | 0.16479 | 0.10986 | -0.36621
4861.0156 | 0.17395 | -0.032043 | 0.18768 | -0.19089 | 0.0087307 | 0.006086 | 0.01348 | 0.026959 | -0.0062721 | -0.010922 | -0.12985 | -0.0054944 | 0.012995 | -0.014165 | 0.013608 | -0.006633 | 0.064087 | 0.16022 | 0.11444 | 0.059509 | 0.28839 | -0.07782 | -0.26093 | 0.082397 | 0.13733 | 0.091553 | 0.19226 | 0.12817 | -0.1831 | -0.20142 | -0.045777 | -0.22888 | 0.10071 | 0.19226 | 0.091552 | 0.32043 | -0.1236 | -0.15106 | -0.16937 | 0.004578 | 0.11444 | 0.1236 | 0.29297 | -0.059509 | 0.32043 | 0.09613 | 0.14648 | -0.44861 | 0.2243 | 0.16022 | 0.16937 | -0.3891
4862.0156 | 0.15564 | -0.036621 | 0.1831 | 0.20584 | 0.016635 | 0.0037362 | 0.018179 | 0.024396 | 0.0014185 | -0.0070773 | 0.12192 | -0.0035718 | 0.018122 | -0.013311 | 0.018307 | -0.0072738 | 0.059509 | 0.086975 | 0.022888 | 0.036621 | 0.29755 | -0.10071 | -0.27466 | 0.064087 | 0.054932 | 0.041199 | 0.19684 | 0.13275 | -0.19226 | -0.19226 | -0.064087 | -0.23804 | 0.11444 | 0.1236 | 0.073242 | 0.31128 | -0.1236 | -0.15564 | -0.15564 | 0.013733 | 0.10071 | 0.07782 | 0.23346 | -0.050354 | 0.33417 | 0.09613 | 0.059509 | -0.45776 | 0.23346 | 0.16937 | 0.091553 | -0.37537
4863.0156 | 0.1831 | -0.004578 | 0.16022 | 0.11429 | 0.01279 | 0.0035226 | 0.013266 | 0.026105 | -0.0019995 | -0.0085727 | 0.17532 | -0.003999 | 0.014063 | -0.01502 | 0.015958 | -0.0051376 | 0.059509 | 0.14191 | 0.086975 | 0.064087 | 0.27924 | -0.064087 | -0.25635 | 0.073242 | 0.064087 | 0.054932 | 0.20599 | 0.11902 | -0.1831 | -0.21057 | -0.059509 | -0.25177 | 0.11902 | 0.14649 | 0.068665 | 0.32044 | -0.10071 | -0.17853 | -0.20599 | 0.045777 | 0.07782 | 0.05951 | 0.2655 | -0.041198 | 0.28381 | 0.064087 | 0.091553 | -0.41657 | 0.21057 | 0.1236 | 0.068665 | -0.37079
4864.0156 | 0.12817 | -0.022888 | 0.17853 | 0.17532 | 0.013858 | 0.0039498 | 0.016043 | 0.02525 | 0.00035035 | -0.0081455 | 0.22873 | -0.003999 | 0.013849 | -0.0096793 | 0.016385 | -0.0059922 | 0.064087 | 0.11902 | 0.068665 | 0.068665 | 0.27924 | -0.091553 | -0.25177 | 0.068665 | 0.07782 | 0.054932 | 0.20142 | 0.12817 | -0.16479 | -0.19684 | -0.068665 | -0.22888 | 0.10071 | 0.14191 | 0.091553 | 0.32044 | -0.11444 | -0.14191 | -0.17395 | 0.022888 | 0.091553 | 0.07782 | 0.25177 | -0.050354 | 0.30212 | 0.086975 | 0.091553 | -0.4303 | 0.2243 | 0.15106 | 0.10071 | -0.37537
4865.0156 | 0.14191 | -0.018311 | 0.17853 | 0.030365 | 0.010013 | 0.006727 | 0.017539 | 0.024396 | -0.0039221 | -0.010495 | 0.053253 | -0.0044264 | 0.014917 | -0.012456 | 0.014035 | -0.0053512 | 0.013733 | 0.054932 | 0.064087 | 0.041199 | 0.28381 | -0.082397 | -0.27924 | 0.041199 | 0.050354 | 0.059509 | 0.20599 | 0.14191 | -0.16937 | -0.20599 | -0.064086 | -0.26092 | 0.10528 | 0.073243 | 0.05951 | 0.32043 | -0.16479 | -0.15106 | -0.18768 | 0.027466 | 0.05951 | 0.07782 | 0.2655 | -0.036621 | 0.30212 | 0.032044 | 0.082398 | -0.45776 | 0.22431 | 0.16022 | 0.068665 | -0.38452
4866.0156 | 0.15106 | -0.004578 | 0.16937 | 0.076141 | 0.013431 | 0.003309 | 0.015189 | 0.02525 | -0.00093145 | -0.010282 | 0.0914 | -0.0054944 | 0.014276 | -0.014379 | 0.016171 | -0.0059922 | 0.07782 | 0.13275 | 0.07782 | 0.068665 | 0.27008 | -0.082397 | -0.2655 | 0.082397 | 0.032043 | 0.064087 | 0.21057 | 0.14191 | -0.17395 | -0.19226 | -0.077819 | -0.26092 | 0.10071 | 0.13733 | 0.073243 | 0.33417 | -0.091553 | -0.16937 | -0.18768 | 0.041198 | 0.086975 | 0.068665 | 0.25635 | -0.027466 | 0.27466 | 0.082398 | 0.082398 | -0.43488 | 0.21515 | 0.14649 | 0.036621 | -0.36163
4867.0156 | 0.12817 | -0.041199 | 0.17853 | 0.045624 | 0.010867 | 0.0058724 | 0.01647 | 0.022687 | -0.0030677 | -0.011991 | 0.045624 | -0.0052808 | 0.013208 | -0.014806 | 0.013608 | -0.0053512 | 0.022888 | 0.07782 | 0.054932 | 0.032043 | 0.28381 | -0.064087 | -0.2655 | 0.041199 | 0.064087 | 0.054932 | 0.20599 | 0.16479 | -0.17395 | -0.18768 | -0.022888 | -0.2243 | 0.10528 | 0.11902 | 0.073242 | 0.29755 | -0.15564 | -0.13275 | -0.14648 | 0.027466 | 0.082398 | 0.096131 | 0.24261 | -0.013733 | 0.32501 | 0.064087 | 0.096131 | -0.44403 | 0.24719 | 0.20599 | 0.10529 | -0.36621
4868.0156 | 0.12817 | -0.027466 | 0.17395 | 0.16006 | 0.016635 | 0.0035226 | 0.016043 | 0.024609 | 0.0014185 | -0.0087863 | 0.15244 | -0.0042126 | 0.012781 | -0.012243 | 0.017667 | -0.0059922 | 0.09613 | 0.12817 | 0.064087 | 0.073242 | 0.2655 | -0.068665 | -0.2655 | 0.086975 | 0.082397 | 0.059509 | 0.21515 | 0.1236 | -0.18768 | -0.19684 | -0.041199 | -0.23804 | 0.091553 | 0.15564 | 0.10071 | 0.33874 | -0.07782 | -0.16022 | -0.16937 | 0.041199 | 0.11444 | 0.086975 | 0.25635 | -0.050354 | 0.29297 | 0.1236 | 0.091553 | -0.43945 | 0.24261 | 0.15106 | 0.10986 | -0.37079
4869.0156 | 0.13733 | -0.041199 | 0.17853 | 0.16769 | 0.011722 | 0.0037362 | 0.015189 | 0.026318 | 0.00056395 | -0.0094273 | 0.11429 | -0.0037854 | 0.011926 | -0.012456 | 0.015103 | -0.005565 | 0.045776 | 0.073242 | 0.045776 | 0.045776 | 0.27924 | -0.082397 | -0.24261 | 0.041199 | 0.036621 | 0.032043 | 0.21515 | 0.13733 | -0.17853 | -0.20599 | -0.041198 | -0.20142 | 0.10071 | 0.11444 | 0.086975 | 0.28839 | -0.13275 | -0.13733 | -0.1648 | 0.036621 | 0.082398 | 0.073242 | 0.23804 | -0.041199 | 0.32043 | 0.086975 | 0.086975 | -0.42114 | 0.25635 | 0.17853 | 0.07782 | -0.38452
4870.0156 | 0.13733 | -0.018311 | 0.17395 | 0.16006 | 0.015994 | 0.0024544 | 0.017111 | 0.023541 | 0.0014185 | -0.0094273 | 0.13718 | -0.0031446 | 0.01214 | -0.013952 | 0.017667 | -0.0074876 | 0.091553 | 0.11902 | 0.082397 | 0.054932 | 0.2655 | -0.073242 | -0.24261 | 0.10071 | 0.07782 | 0.059509 | 0.19226 | 0.13275 | -0.19226 | -0.21057 | -0.054931 | -0.2243 | 0.091553 | 0.13733 | 0.073243 | 0.29755 | -0.082397 | -0.17395 | -0.19226 | 0.018311 | 0.11902 | 0.07782 | 0.27008 | -0.041199 | 0.28381 | 0.10986 | 0.10071 | -0.41656 | 0.21057 | 0.15106 | 0.096131 | -0.38452
4871.0156 | 0.15564 | -0.032043 | 0.17853 | -0.023041 | 0.012576 | 0.0041634 | 0.017539 | 0.021619 | -0.0032813 | -0.0098545 | -0.0077819 | -0.0052808 | 0.011713 | -0.013097 | 0.015317 | -0.0068466 | 0.041199 | 0.09613 | 0.068665 | 0.059509 | 0.28381 | -0.07782 | -0.26093 | 0.059509 | 0.073242 | 0.064087 | 0.20142 | 0.13275 | -0.17395 | -0.20599 | -0.045777 | -0.22888 | 0.10528 | 0.12817 | 0.091552 | 0.32043 | -0.13733 | -0.14191 | -0.17395 | 0.022888 | 0.091552 | 0.09613 | 0.27008 | -0.045777 | 0.31586 | 0.073242 | 0.10071 | -0.43945 | 0.23346 | 0.16479 | 0.10529 | -0.38452
4872.0156 | 0.13275 | -0.041199 | 0.1831 | 0.037994 | 0.011722 | 0.0039498 | 0.015189 | 0.022473 | 0.00035035 | -0.0089999 | 0.0074766 | -0.0050672 | 0.011926 | -0.01267 | 0.016812 | -0.0070602 | 0.045776 | 0.10071 | 0.027466 | 0.036621 | 0.2655 | -0.086975 | -0.25635 | 0.041199 | 0.054932 | 0.045776 | 0.21973 | 0.13275 | -0.1831 | -0.20142 | -0.045776 | -0.21515 | 0.082398 | 0.14191 | 0.07782 | 0.29297 | -0.13733 | -0.14191 | -0.16022 | 0.036622 | 0.082398 | 0.086975 | 0.24719 | -0.050354 | 0.3067 | 0.086975 | 0.068665 | -0.43945 | 0.26093 | 0.17395 | 0.096131 | -0.38452
4873.0156 | 0.11902 | -0.032043 | 0.1831 | 0.022736 | 0.0097989 | 0.0045908 | 0.016257 | 0.024609 | -0.0022131 | -0.0081455 | 0.022736 | -0.0048536 | 0.012781 | -0.014165 | 0.016171 | -0.0062058 | 0.059509 | 0.11902 | 0.082397 | 0.059509 | 0.27466 | -0.10071 | -0.24719 | 0.059509 | 0.07782 | 0.064087 | 0.19684 | 0.14191 | -0.1831 | -0.21057 | -0.068665 | -0.21515 | 0.091553 | 0.15106 | 0.091552 | 0.3067 | -0.1236 | -0.15106 | -0.17853 | 0.013733 | 0.091552 | 0.09613 | 0.27466 | -0.041198 | 0.3067 | 0.091552 | 0.11444 | -0.4303 | 0.22888 | 0.17395 | 0.10986 | -0.39368
4874.0156 | 0.11902 | -0.032043 | 0.19684 | 0.045624 | 0.01044 | 0.0048044 | 0.016257 | 0.025037 | 0.0012047 | -0.010068 | 0.060883 | -0.0048536 | 0.013422 | -0.013952 | 0.016171 | -0.0068466 | 0.041199 | 0.082397 | 0.036621 | 0.032043 | 0.28381 | -0.082397 | -0.2655 | 0.050354 | 0.041199 | 0.041199 | 0.20599 | 0.16022 | -0.1831 | -0.21515 | -0.050354 | -0.23346 | 0.086975 | 0.11444 | 0.064086 | 0.29755 | -0.15564 | -0.15106 | -0.18311 | 0.009156 | 0.082397 | 0.073242 | 0.25635 | -0.036621 | 0.31586 | 0.073242 | 0.068664 | -0.46234 | 0.23804 | 0.19226 | 0.073242 | -0.41199
4875.0156 | 0.15106 | -0.018311 | 0.16479 | -0.14511 | 0.0095853 | 0.0054452 | 0.017325 | 0.021619 | -0.0024269 | -0.0096409 | -0.12222 | -0.005708 | 0.011286 | -0.013311 | 0.016385 | -0.006633 | 0.059509 | 0.11444 | 0.064087 | 0.064087 | 0.28839 | -0.091553 | -0.27008 | 0.073242 | 0.12817 | 0.07782 | 0.20142 | 0.13275 | -0.18768 | -0.20142 | -0.073242 | -0.25177 | 0.1236 | 0.13275 | 0.082398 | 0.33417 | -0.10529 | -0.16937 | -0.18311 | 0.036621 | 0.091553 | 0.096131 | 0.27924 | -0.032044 | 0.3067 | 0.07782 | 0.082398 | -0.43488 | 0.21973 | 0.15106 | 0.14649 | -0.36621
4876.0156 | 0.12817 | -0.036621 | 0.17395 | 0.17532 | 0.014071 | 0.0039498 | 0.017325 | 0.024396 | 0.00056395 | -0.0092137 | 0.14481 | -0.0033582 | 0.013208 | -0.014592 | 0.016171 | -0.0074876 | 0.068665 | 0.14648 | 0.068665 | 0.064087 | 0.28839 | -0.073242 | -0.24719 | 0.068665 | 0.022888 | 0.045776 | 0.19684 | 0.1236 | -0.16937 | -0.20599 | -0.036621 | -0.21057 | 0.11444 | 0.18311 | 0.10071 | 0.31128 | -0.10528 | -0.13275 | -0.16937 | 0.022888 | 0.10529 | 0.082397 | 0.25177 | -0.050354 | 0.32501 | 0.10529 | 0.10529 | -0.42114 | 0.23346 | 0.16022 | 0.059509 | -0.37994
4877.0156 | 0.17853 | -0.036621 | 0.18768 | -0.076447 | 0.011081 | 0.0043772 | 0.017325 | 0.026532 | -0.00050425 | -0.0094273 | -0.18326 | -0.0048536 | 0.013422 | -0.015447 | 0.015103 | -0.0062058 | 0.059509 | 0.13275 | 0.091553 | 0.07782 | 0.27924 | -0.086975 | -0.25635 | 0.10529 | 0.11902 | 0.10529 | 0.18768 | 0.13275 | -0.16937 | -0.18768 | -0.050354 | -0.21973 | 0.091553 | 0.16937 | 0.11444 | 0.33417 | -0.12817 | -0.13275 | -0.15106 | 0 | 0.14191 | 0.14191 | 0.29297 | -0.054932 | 0.31586 | 0.09613 | 0.12817 | -0.44403 | 0.2243 | 0.16937 | 0.15564 | -0.37537
4878.0156 | 0.15564 | -0.022888 | 0.16479 | 0.022736 | 0.010226 | 0.0056588 | 0.014121 | 0.026105 | -0.0019995 | -0.0098545 | 0.030365 | -0.0054944 | 0.011072 | -0.013097 | 0.016171 | -0.0042832 | 0.045776 | 0.10071 | 0.064087 | 0.050354 | 0.27924 | -0.082397 | -0.27924 | 0.068665 | 0.086975 | 0.073242 | 0.20599 | 0.14191 | -0.17853 | -0.19684 | -0.059509 | -0.25635 | 0.11444 | 0.1236 | 0.073242 | 0.32959 | -0.11902 | -0.15564 | -0.17395 | 0.041199 | 0.091553 | 0.09613 | 0.27008 | -0.022888 | 0.30212 | 0.068664 | 0.086975 | -0.44403 | 0.22888 | 0.16479 | 0.10986 | -0.36163
4879.0156 | 0.16479 | -0.018311 | 0.19226 | -0.23666 | 0.011081 | 0.0037362 | 0.017966 | 0.0276 | -0.00029045 | -0.010495 | -0.13748 | -0.0050672 | 0.013635 | -0.015661 | 0.014676 | -0.0059922 | 0.082397 | 0.17395 | 0.086975 | 0.086975 | 0.27924 | -0.082397 | -0.25635 | 0.059509 | 0.13275 | 0.059509 | 0.20142 | 0.14648 | -0.17395 | -0.18768 | -0.064086 | -0.23804 | 0.086975 | 0.19226 | 0.10529 | 0.34332 | -0.10986 | -0.15564 | -0.16937 | 0.009155 | 0.07782 | 0.07782 | 0.24719 | -0.045777 | 0.29755 | 0.10071 | 0.10529 | -0.44861 | 0.21973 | 0.16479 | 0.15106 | -0.37994
4880.0156 | 0.15106 | -0.032043 | 0.1831 | -0.03067 | 0.01044 | 0.0054452 | 0.016684 | 0.024823 | -0.0028541 | -0.0092137 | -0.0077819 | -0.0048536 | 0.01214 | -0.013738 | 0.017667 | -0.0070602 | 0.027466 | 0.13733 | 0.068665 | 0.054932 | 0.27924 | -0.082397 | -0.25635 | 0.07782 | 0.10071 | 0.07782 | 0.19226 | 0.13733 | -0.16937 | -0.20142 | -0.050354 | -0.22431 | 0.096131 | 0.16937 | 0.086975 | 0.31128 | -0.15564 | -0.13733 | -0.16937 | 0.009156 | 0.10986 | 0.10986 | 0.27924 | -0.045776 | 0.31128 | 0.059509 | 0.10071 | -0.43945 | 0.2243 | 0.16937 | 0.13275 | -0.38452
4881.0156 | 0.10529 | -0.022888 | 0.16937 | -0.13748 | 0.012362 | 0.0058724 | 0.01647 | 0.026746 | -0.00071785 | -0.0085727 | -0.27481 | -0.002931 | 0.013635 | -0.01502 | 0.015744 | -0.0085556 | 0.064087 | 0.16479 | 0.07782 | 0.073242 | 0.27466 | -0.073242 | -0.24719 | 0.054932 | 0.10986 | 0.054932 | 0.20142 | 0.12817 | -0.18768 | -0.19684 | -0.050354 | -0.2243 | 0.10529 | 0.18768 | 0.09613 | 0.32043 | -0.10529 | -0.16479 | -0.17395 | 0.032043 | 0.07782 | 0.07782 | 0.25177 | -0.041199 | 0.29755 | 0.086975 | 0.10071 | -0.41656 | 0.2243 | 0.15106 | 0.13275 | -0.36621
4882.0156 | 0.16937 | -0.032043 | 0.17395 | -0.0077822 | 0.0091581 | 0.0052316 | 0.014121 | 0.025464 | -0.0026405 | -0.01135 | -0.25192 | -0.005708 | 0.012995 | -0.012456 | 0.016385 | -0.006633 | 0.064087 | 0.16479 | 0.082397 | 0.064087 | 0.28839 | -0.082397 | -0.27008 | 0.10071 | 0.10071 | 0.091553 | 0.19226 | 0.14648 | -0.18768 | -0.20599 | -0.050354 | -0.23804 | 0.11444 | 0.19684 | 0.09613 | 0.33417 | -0.10986 | -0.15564 | -0.17395 | 0.018311 | 0.13275 | 0.1236 | 0.29755 | -0.027466 | 0.32043 | 0.09613 | 0.11444 | -0.44403 | 0.2243 | 0.17853 | 0.13275 | -0.37994
4883.0156 | 0.16022 | -0.050354 | 0.17395 | -0.084076 | 0.011722 | 0.0054452 | 0.015616 | 0.026318 | -0.0019995 | -0.0092137 | -0.068817 | -0.006349 | 0.013208 | -0.014806 | 0.016171 | -0.0062058 | 0.064087 | 0.18768 | 0.10071 | 0.086975 | 0.27008 | -0.07782 | -0.25635 | 0.091553 | 0.14191 | 0.07782 | 0.19684 | 0.13733 | -0.17395 | -0.19684 | -0.027466 | -0.20599 | 0.096131 | 0.23804 | 0.13733 | 0.34332 | -0.10986 | -0.1236 | -0.14648 | 0.022888 | 0.14191 | 0.12817 | 0.27466 | -0.036621 | 0.32044 | 0.11444 | 0.15106 | -0.4303 | 0.24719 | 0.18768 | 0.19226 | -0.37079
4884.0156 | 0.21973 | -0.009155 | 0.1831 | -0.22141 | 0.010653 | 0.003309 | 0.014121 | 0.027386 | -0.0019995 | -0.0094273 | -0.32059 | -0.0054944 | 0.010004 | -0.015233 | 0.014462 | -0.0068466 | 0.082397 | 0.16022 | 0.09613 | 0.073242 | 0.2655 | -0.086975 | -0.27466 | 0.068665 | 0.12817 | 0.07782 | 0.20599 | 0.13733 | -0.16022 | -0.20599 | -0.07782 | -0.2655 | 0.082398 | 0.16937 | 0.082397 | 0.3479 | -0.10071 | -0.15106 | -0.19684 | 0.022889 | 0.07782 | 0.086975 | 0.28381 | -0.045776 | 0.27466 | 0.091552 | 0.10528 | -0.45776 | 0.21515 | 0.14648 | 0.13733 | -0.3891
4885.0156 | 0.022888 | -0.054932 | 0.20142 | -0.15274 | 0.01514 | 0.0054452 | 0.017539 | 0.025464 | 0.0016321 | -0.0085727 | -0.15274 | -0.003999 | 0.012567 | -0.013311 | 0.014462 | -0.008342 | -0.013733 | 0.045776 | -0.027466 | 0.004578 | 0.31128 | -0.10986 | -0.31128 | -0.032043 | -0.018311 | -0.032043 | 0.24719 | 0.16022 | -0.20599 | -0.22888 | -0.054931 | -0.25635 | 0.10986 | 0.10071 | 0.05951 | 0.31586 | -0.21515 | -0.15106 | -0.17395 | 0.045776 | 0.022889 | 0.022889 | 0.19684 | -0.041199 | 0.36621 | 0.041199 | 0.027466 | -0.5127 | 0.30212 | 0.21515 | 0.036621 | -0.4303
4886.0156 | 0.13733 | -0.022888 | 0.16937 | -0.16037 | 0.011081 | 0.0045908 | 0.016684 | 0.025464 | -0.00050425 | -0.0083591 | -0.2214 | -0.0037854 | 0.011286 | -0.014379 | 0.015744 | -0.0053512 | 0.064087 | 0.16937 | 0.091553 | 0.10071 | 0.29297 | -0.086975 | -0.2655 | 0.064087 | 0.12817 | 0.064087 | 0.19684 | 0.13733 | -0.17853 | -0.19684 | -0.064087 | -0.24261 | 0.1236 | 0.19226 | 0.1236 | 0.36621 | -0.10529 | -0.15564 | -0.17395 | 0.027465 | 0.086975 | 0.086975 | 0.26093 | -0.032044 | 0.31586 | 0.086975 | 0.11444 | -0.43488 | 0.21973 | 0.16022 | 0.15106 | -0.36621
4887.0156 | -0.013733 | -0.059509 | 0.20599 | -0.18326 | 0.016635 | 0.0058724 | 0.01647 | 0.0276 | 0.0020593 | -0.0075047 | -0.168 | -0.0042126 | 0.014917 | -0.012456 | 0.018094 | -0.0068466 | -0.009155 | 0.036621 | -0.041199 | -0.004578 | 0.31128 | -0.13275 | -0.30212 | -0.032043 | 0.004578 | -0.041199 | 0.24261 | 0.18768 | -0.21973 | -0.24719 | -0.073242 | -0.24261 | 0.10528 | 0.09613 | 0.054931 | 0.29755 | -0.21515 | -0.16022 | -0.18768 | 0.036621 | 0.027466 | 0.01831 | 0.20599 | -0.018311 | 0.37079 | 0.050354 | 0.01831 | -0.50812 | 0.30212 | 0.24719 | 0.064087 | -0.45319
4888.0156 | 0.12817 | -0.027466 | 0.18768 | -0.19089 | 0.011935 | 0.0041634 | 0.014334 | 0.023328 | -0.00050425 | -0.0096409 | -0.12985 | -0.0033582 | 0.012995 | -0.011388 | 0.014676 | -0.005565 | 0.054932 | 0.16937 | 0.086975 | 0.086975 | 0.27008 | -0.082397 | -0.27008 | 0.036621 | 0.1236 | 0.050354 | 0.20142 | 0.14648 | -0.1831 | -0.21515 | -0.054931 | -0.24262 | 0.082398 | 0.19684 | 0.11444 | 0.35706 | -0.13275 | -0.15564 | -0.18768 | 0.013733 | 0.064087 | 0.07782 | 0.2655 | -0.041199 | 0.29755 | 0.082398 | 0.11444 | -0.45776 | 0.22888 | 0.17395 | 0.15106 | -0.40283
4889.0156 | 0.064087 | -0.059509 | 0.21515 | -0.084076 | 0.016849 | 0.0043772 | 0.015402 | 0.026746 | 0.00056395 | -0.010068 | -0.27481 | -0.003999 | 0.015344 | -0.015233 | 0.016171 | -0.0079148 | -0.009155 | 0.041199 | -0.041199 | 0.009155 | 0.31128 | -0.11902 | -0.3067 | -0.027466 | 0.004578 | -0.036621 | 0.23346 | 0.18768 | -0.21515 | -0.24719 | -0.05951 | -0.24719 | 0.09613 | 0.10071 | 0.068664 | 0.31586 | -0.2243 | -0.15564 | -0.18768 | 0.01831 | 0.032043 | 0.022888 | 0.21057 | -0.027466 | 0.37079 | 0.050354 | 0.01831 | -0.52185 | 0.29297 | 0.24719 | 0.064087 | -0.46234
4890.0156 | 0.13275 | -0.018311 | 0.1831 | -0.28244 | 0.010226 | 0.0054452 | 0.017325 | 0.02525 | -0.0041357 | -0.0079319 | -0.12985 | -0.0050672 | 0.013635 | -0.01502 | 0.01553 | -0.0053512 | 0.054932 | 0.17853 | 0.091553 | 0.064087 | 0.28381 | -0.073242 | -0.2655 | 0.068665 | 0.15106 | 0.091553 | 0.17853 | 0.12817 | -0.17853 | -0.21057 | -0.054931 | -0.24719 | 0.10071 | 0.19684 | 0.082398 | 0.32959 | -0.12817 | -0.16022 | -0.19226 | -0.004577 | 0.086976 | 0.10986 | 0.30212 | -0.054931 | 0.30212 | 0.073243 | 0.10986 | -0.44861 | 0.19684 | 0.14649 | 0.16937 | -0.39368
4891.0156 | 0.086975 | -0.064087 | 0.20142 | -0.27481 | 0.019198 | 0.0056588 | 0.017752 | 0.025677 | 0.0029137 | -0.0083591 | -0.25192 | -0.0037854 | 0.014917 | -0.012243 | 0.017239 | -0.0068466 | 0 | 0.032043 | -0.018311 | 0.022888 | 0.30212 | -0.11902 | -0.31128 | -0.009155 | 0.022888 | -0.022888 | 0.2243 | 0.16479 | -0.21057 | -0.24261 | -0.054932 | -0.24719 | 0.10071 | 0.09613 | 0.086975 | 0.33417 | -0.20142 | -0.14648 | -0.17853 | 0.022888 | 0.054932 | 0.041199 | 0.21973 | -0.036621 | 0.36621 | 0.064087 | 0.045776 | -0.5127 | 0.28839 | 0.22888 | 0.086975 | -0.44403
4892.0156 | 0.073242 | -0.068665 | 0.21057 | -0.21378 | 0.013858 | 0.0041634 | 0.016898 | 0.026746 | -0.0013587 | -0.0081455 | -0.20615 | -0.0027174 | 0.014276 | -0.013524 | 0.015103 | -0.0044968 | -0.027466 | 0.07782 | -0.018311 | 0.027466 | 0.31128 | -0.10529 | -0.30212 | -0.045776 | 0.009155 | -0.041199 | 0.23804 | 0.16937 | -0.22888 | -0.24719 | -0.036621 | -0.23346 | 0.10071 | 0.14649 | 0.096131 | 0.32959 | -0.23804 | -0.16022 | -0.17853 | 0.027466 | 0.022889 | 0.027466 | 0.20599 | -0.041198 | 0.37994 | 0.041199 | 0.050354 | -0.5127 | 0.3067 | 0.23804 | 0.07782 | -0.45776
4893.0156 | 0.091553 | -0.064087 | 0.21057 | -0.18326 | 0.018558 | 0.0035226 | 0.01882 | 0.029309 | 0.0037683 | -0.0079319 | -0.45792 | -0.0020764 | 0.013849 | -0.011602 | 0.017453 | -0.006633 | -0.013733 | 0.050354 | -0.022888 | 0.022888 | 0.31586 | -0.10529 | -0.29755 | -0.018311 | 0.045776 | -0.022888 | 0.24261 | 0.16937 | -0.21515 | -0.25635 | -0.041199 | -0.23346 | 0.10529 | 0.11444 | 0.086975 | 0.32043 | -0.2243 | -0.15106 | -0.19226 | 0.032044 | 0.045776 | 0.041199 | 0.23346 | -0.041198 | 0.37994 | 0.050354 | 0.041199 | -0.50812 | 0.3067 | 0.23346 | 0.10986 | -0.46692
4894.0156 | 0.027466 | -0.041199 | 0.20599 | -0.19089 | 0.014285 | 0.0045908 | 0.017966 | 0.027386 | -0.00050425 | -0.0077183 | -0.19089 | -0.0042126 | 0.013849 | -0.013311 | 0.01489 | -0.0044968 | -0.032043 | 0.054932 | -0.013733 | 0.022888 | 0.31128 | -0.10986 | -0.29297 | -0.054932 | 0.009155 | -0.045776 | 0.2243 | 0.17395 | -0.23346 | -0.23346 | -0.068664 | -0.25177 | 0.10528 | 0.096131 | 0.064087 | 0.31586 | -0.23804 | -0.19226 | -0.19226 | 0.01831 | -0.013733 | -0.004577 | 0.18768 | -0.032044 | 0.35248 | 0.009156 | 0.027466 | -0.49896 | 0.2655 | 0.21515 | 0.050354 | -0.43945
4895.0156 | 0.064087 | -0.068665 | 0.19684 | -0.21378 | 0.018344 | 0.0018136 | 0.017752 | 0.028241 | 0.0018457 | -0.0092137 | -0.168 | -0.0035718 | 0.015344 | -0.014379 | 0.016598 | -0.0072738 | -0.004578 | 0.036621 | -0.032043 | 0.041199 | 0.3067 | -0.10529 | -0.32044 | -0.018311 | 0.036621 | -0.018311 | 0.23346 | 0.16479 | -0.20599 | -0.22888 | -0.036621 | -0.25177 | 0.10986 | 0.10529 | 0.10986 | 0.36163 | -0.20142 | -0.13733 | -0.16022 | 0.036621 | 0.050354 | 0.050354 | 0.21057 | -0.032043 | 0.37537 | 0.064087 | 0.036622 | -0.51727 | 0.30212 | 0.23346 | 0.10529 | -0.42572
4896.0156 | 0.082397 | -0.013733 | 0.1831 | -0.22141 | 0.011294 | 0.0054452 | 0.015616 | 0.025037 | -0.0047767 | -0.0072911 | -0.19852 | -0.0025038 | 0.014704 | -0.014165 | 0.013608 | -0.0044968 | 0.027466 | 0.14191 | 0.050354 | 0.073242 | 0.29755 | -0.07782 | -0.25177 | 0.004578 | 0.086975 | 0.022888 | 0.19226 | 0.15106 | -0.20599 | -0.23346 | -0.064087 | -0.23804 | 0.11444 | 0.15564 | 0.086975 | 0.32501 | -0.15564 | -0.19226 | -0.21973 | 0.009156 | 0.018311 | 0.036621 | 0.25635 | -0.032043 | 0.31128 | 0.041199 | 0.064087 | -0.43488 | 0.20599 | 0.16479 | 0.10071 | -0.41656
4897.0156 | 0.009155 | -0.054932 | 0.20599 | -0.19852 | 0.017062 | 0.0035226 | 0.017539 | 0.024609 | 0.00077755 | -0.0098545 | -0.23666 | -0.00229 | 0.015558 | -0.012243 | 0.016598 | -0.0072738 | -0.022888 | 0.018311 | -0.041199 | -0.004578 | 0.31586 | -0.12817 | -0.30212 | -0.050354 | 0.009155 | -0.041199 | 0.22888 | 0.17853 | -0.23804 | -0.20599 | -0.073242 | -0.24719 | 0.10986 | 0.073243 | 0.050354 | 0.29755 | -0.22888 | -0.1831 | -0.15106 | 0.022888 | 0.004578 | 0.013733 | 0.1648 | -0.027466 | 0.37079 | 0.032044 | 0.013733 | -0.50812 | 0.28381 | 0.23346 | 0.064087 | -0.41199
4898.0156 | 0.032043 | -0.045776 | 0.20142 | -0.14511 | 0.016635 | 0.0048044 | 0.01647 | 0.025464 | 0.00099115 | -0.0079319 | -0.29007 | -0.0035718 | 0.016626 | -0.012243 | 0.015744 | -0.005565 | -0.045776 | 0.027466 | -0.036621 | 0.027466 | 0.32501 | -0.11444 | -0.30212 | -0.059509 | 0 | -0.041199 | 0.25177 | 0.16022 | -0.20599 | -0.26093 | -0.068665 | -0.25635 | 0.1236 | 0.073242 | 0.073242 | 0.32959 | -0.24719 | -0.16022 | -0.21515 | 0.050354 | -0.013733 | 0.004577 | 0.21973 | -0.041199 | 0.37079 | 0 | 0.009155 | -0.50354 | 0.29755 | 0.20599 | 0.045776 | -0.46234
4899.0156 | 0.073242 | -0.045776 | 0.1831 | -0.10696 | 0.019412 | 0.0039498 | 0.016684 | 0.025464 | 0.0031273 | -0.0066501 | -0.15274 | -0.0027174 | 0.016199 | -0.012243 | 0.017453 | -0.0044968 | 0.032043 | 0.07782 | -0.009155 | 0.036621 | 0.29297 | -0.10071 | -0.29755 | 0 | 0.027466 | -0.041199 | 0.21057 | 0.1831 | -0.21973 | -0.23346 | -0.054932 | -0.25177 | 0.10986 | 0.1236 | 0.082397 | 0.33417 | -0.15106 | -0.17395 | -0.18768 | 0.027466 | 0.045776 | 0.004577 | 0.19226 | 0 | 0.33874 | 0.077819 | 0.036621 | -0.48065 | 0.25635 | 0.22888 | 0.073242 | -0.41656
4900.0156 | 0.045776 | -0.041199 | 0.20599 | -0.28244 | 0.015994 | 0.0035226 | 0.015402 | 0.025464 | -0.0024269 | -0.0077183 | -0.068817 | -0.0044264 | 0.013422 | -0.012884 | 0.013394 | -0.0040696 | -0.018311 | 0.036621 | -0.050354 | 0.018311 | 0.3067 | -0.11902 | -0.29297 | -0.045776 | 0 | -0.027466 | 0.22888 | 0.17853 | -0.2243 | -0.24261 | -0.07782 | -0.25177 | 0.10071 | 0.07782 | 0.05951 | 0.31128 | -0.22431 | -0.18311 | -0.20142 | 0.022888 | -0.004577 | 0.013733 | 0.21515 | -0.027466 | 0.3479 | 0.022888 | -0.009155 | -0.49896 | 0.27008 | 0.21973 | 0.041199 | -0.44861
4901.0156 | 0.064087 | -0.054932 | 0.19226 | -0.084076 | 0.018985 | 0.0058724 | 0.01647 | 0.026105 | 0.0018457 | -0.0064365 | -0.10696 | -0.0027174 | 0.013208 | -0.013738 | 0.017453 | -0.0059922 | 0.032043 | 0.064087 | -0.009155 | 0.045776 | 0.31128 | -0.10986 | -0.27466 | 0.004578 | 0.027466 | -0.022888 | 0.2243 | 0.15106 | -0.20142 | -0.22888 | -0.054931 | -0.21973 | 0.11902 | 0.11902 | 0.10071 | 0.32043 | -0.16022 | -0.14648 | -0.17395 | 0.032043 | 0.05951 | 0.032044 | 0.20599 | -0.041199 | 0.36621 | 0.086975 | 0.045777 | -0.46692 | 0.27924 | 0.20599 | 0.082398 | -0.42114
4902.0156 | 0.018311 | -0.036621 | 0.20142 | -0.27481 | 0.013858 | 0.005018 | 0.016257 | 0.027173 | -7.6852e-05 | -0.0081455 | -0.18326 | -0.0050672 | 0.013422 | -0.012243 | 0.013181 | -0.0047104 | -0.032043 | 0.022888 | -0.050354 | 0.009155 | 0.31128 | -0.10529 | -0.29755 | -0.059509 | -0.009155 | -0.050354 | 0.22888 | 0.16937 | -0.21515 | -0.23346 | -0.068665 | -0.26092 | 0.10986 | 0.059509 | 0.045776 | 0.3067 | -0.23346 | -0.17853 | -0.19684 | 0.027466 | -0.022888 | -0.013733 | 0.1831 | -0.032043 | 0.3479 | 0.004578 | -0.013733 | -0.49896 | 0.2655 | 0.20599 | 0.027466 | -0.43488
4903.0156 | 0.059509 | -0.050354 | 0.19684 | -0.23666 | 0.017917 | 0.0045908 | 0.017539 | 0.026105 | 0.00013675 | -0.0083591 | -0.31296 | -0.0042126 | 0.013208 | -0.010534 | 0.014462 | -0.0044968 | -0.045776 | 0.041199 | -0.022888 | 0.027466 | 0.32044 | -0.11444 | -0.28839 | -0.022888 | 0.022888 | -0.022888 | 0.24261 | 0.1831 | -0.21515 | -0.22888 | -0.064087 | -0.23804 | 0.1236 | 0.091553 | 0.07782 | 0.31586 | -0.24261 | -0.16479 | -0.17853 | 0.045777 | 0.027466 | 0.027466 | 0.20599 | -0.013733 | 0.37079 | 0.004578 | 0.027466 | -0.48523 | 0.29297 | 0.23346 | 0.073242 | -0.42572
4904.0156 | 0.027466 | -0.036621 | 0.20142 | -0.17563 | 0.013217 | 0.0043772 | 0.016898 | 0.024823 | -0.0049903 | -0.0096409 | -0.17563 | -0.003999 | 0.015772 | -0.011602 | 0.014249 | -0.0051376 | -0.054932 | 0.045776 | -0.018311 | 0.004578 | 0.31586 | -0.10529 | -0.27924 | -0.050354 | -0.013733 | -0.032043 | 0.24719 | 0.1831 | -0.2243 | -0.26093 | -0.068665 | -0.24261 | 0.11444 | 0.082397 | 0.041199 | 0.28381 | -0.25635 | -0.18768 | -0.2243 | 0.045776 | -0.013733 | 0.004578 | 0.22888 | -0.018311 | 0.35248 | -0.018311 | 0.01831 | -0.48065 | 0.28381 | 0.21973 | 0.022888 | -0.46234
4905.0156 | 0.050354 | -0.050354 | 0.18768 | -0.068817 | 0.02048 | 0.0037362 | 0.01647 | 0.02525 | 0.0041955 | -0.0081455 | -0.053558 | -0.0035718 | 0.015344 | -0.014379 | 0.017239 | -0.0059922 | 0.032043 | 0.036621 | -0.009155 | 0.036621 | 0.29755 | -0.10529 | -0.27924 | -0.027466 | 0 | -0.054932 | 0.20599 | 0.15106 | -0.20599 | -0.2243 | -0.054932 | -0.22888 | 0.10986 | 0.086975 | 0.086975 | 0.31586 | -0.15564 | -0.15564 | -0.17395 | 0.018311 | 0.022888 | -0.004578 | 0.16937 | -0.036621 | 0.3479 | 0.082397 | 0.041199 | -0.46692 | 0.25635 | 0.20142 | 0.050354 | -0.41199
4906.0156 | 0.054932 | -0.059509 | 0.19684 | -0.27481 | 0.018771 | 0.0041634 | 0.016684 | 0.025891 | 0.00013675 | -0.0079319 | -0.17563 | -0.0025038 | 0.01449 | -0.015447 | 0.016598 | -0.0051376 | -0.022888 | 0.032043 | -0.027466 | 0.027466 | 0.29755 | -0.11902 | -0.28839 | -0.036621 | 0.041199 | -0.009155 | 0.23804 | 0.17853 | -0.20599 | -0.23804 | -0.05951 | -0.22888 | 0.10071 | 0.091552 | 0.086975 | 0.31586 | -0.21973 | -0.14649 | -0.17853 | 0.041199 | 0.022888 | 0.050354 | 0.22888 | -0.01831 | 0.35705 | 0.036621 | 0.032043 | -0.48523 | 0.29755 | 0.23804 | 0.10071 | -0.43488
4907.0156 | 0.064087 | -0.059509 | 0.18768 | -0.0383 | 0.018344 | 0.0056588 | 0.019248 | 0.025464 | 0.0018457 | -0.0092137 | -0.00015237 | -0.0025038 | 0.016626 | -0.012029 | 0.017239 | -0.005565 | 0.018311 | 0.045776 | -0.032043 | 0.032043 | 0.28839 | -0.10071 | -0.28839 | -0.032043 | 0.004578 | -0.059509 | 0.2243 | 0.17395 | -0.19226 | -0.22888 | -0.041199 | -0.22888 | 0.10071 | 0.10528 | 0.091552 | 0.32043 | -0.16937 | -0.13275 | -0.16937 | 0.036621 | 0.027466 | 0 | 0.16937 | -0.013733 | 0.3479 | 0.07782 | 0.027466 | -0.47607 | 0.28381 | 0.23346 | 0.064087 | -0.41656
4908.0156 | 0.068665 | -0.032043 | 0.20142 | -0.21378 | 0.020053 | 0.0026682 | 0.016043 | 0.024823 | -7.6852e-05 | -0.0081455 | -0.18326 | -0.0035718 | 0.014917 | -0.011815 | 0.015103 | -0.005565 | -0.004578 | 0.032043 | -0.027466 | 0.059509 | 0.30212 | -0.09613 | -0.28381 | -0.022888 | 0.036621 | -0.032043 | 0.22888 | 0.17853 | -0.20599 | -0.2243 | -0.064087 | -0.25177 | 0.10071 | 0.064086 | 0.091552 | 0.34332 | -0.20599 | -0.17395 | -0.19226 | 0.027466 | 0.009155 | 0 | 0.19226 | -0.022888 | 0.33417 | 0.027465 | 0.004577 | -0.48523 | 0.26093 | 0.21057 | 0.068664 | -0.42572
4909.0156 | 0.064087 | -0.054932 | 0.19684 | -0.0383 | 0.020907 | 0.0022408 | 0.018607 | 0.023968 | 0.0014185 | -0.0087863 | -0.00015237 | -0.0037854 | 0.018122 | -0.014592 | 0.017026 | -0.0051376 | 0.036621 | 0.041199 | -0.041199 | 0.027466 | 0.3067 | -0.10529 | -0.29755 | -0.050354 | -0.009155 | -0.054932 | 0.21515 | 0.1831 | -0.20599 | -0.24261 | -0.050354 | -0.24261 | 0.10986 | 0.096131 | 0.082398 | 0.32501 | -0.16022 | -0.15106 | -0.18768 | 0.018311 | 0.004578 | 0 | 0.18768 | -0.013733 | 0.36163 | 0.091553 | 0.013733 | -0.49438 | 0.27008 | 0.23804 | 0.045777 | -0.43945
4910.0156 | 0.018311 | -0.059509 | 0.20599 | -0.23666 | 0.014285 | 0.0056588 | 0.017325 | 0.025891 | -0.0011451 | -0.012418 | -0.099335 | -0.00229 | 0.014276 | -0.013524 | 0.01553 | -0.0036424 | -0.022888 | 0.013733 | -0.041199 | 0.022888 | 0.3067 | -0.10986 | -0.3067 | -0.050354 | 0 | -0.032043 | 0.24719 | 0.18768 | -0.20599 | -0.24261 | -0.050354 | -0.24719 | 0.10071 | 0.073242 | 0.082397 | 0.32959 | -0.22888 | -0.14649 | -0.18311 | 0.041198 | 0.009155 | 0.027466 | 0.21057 | -0.018311 | 0.36621 | 0.036621 | 0.01831 | -0.5127 | 0.3067 | 0.24719 | 0.059509 | -0.44861
4911.0156 | 0.064087 | -0.036621 | 0.1831 | 0.076141 | 0.020267 | 0.0030954 | 0.017752 | 0.024823 | 0.0029137 | -0.0092137 | -0.053558 | -0.002931 | 0.014917 | -0.01502 | 0.015317 | -0.0053512 | 0.022888 | 0.059509 | -0.022888 | 0.059509 | 0.31586 | -0.10529 | -0.28381 | -0.004578 | 0.013733 | -0.027466 | 0.23346 | 0.16937 | -0.21515 | -0.22888 | -0.068665 | -0.24719 | 0.13275 | 0.09613 | 0.09613 | 0.34332 | -0.16022 | -0.17853 | -0.19226 | 0.050354 | 0.032043 | 0.009155 | 0.20142 | -0.013732 | 0.35248 | 0.059509 | 0.013733 | -0.46692 | 0.27008 | 0.20599 | 0.050354 | -0.41199
4912.0156 | 0.059509 | -0.045776 | 0.18768 | -0.21378 | 0.018558 | 0.003309 | 0.017325 | 0.026532 | 0.00013675 | -0.0096409 | -0.099335 | -0.0025038 | 0.01684 | -0.013952 | 0.016598 | -0.006633 | 0.022888 | 0.073242 | -0.013733 | 0.032043 | 0.3067 | -0.09613 | -0.26093 | -0.009155 | 0.022888 | -0.027466 | 0.21057 | 0.15564 | -0.21515 | -0.23804 | -0.050354 | -0.21515 | 0.11902 | 0.11902 | 0.077819 | 0.29297 | -0.16479 | -0.16937 | -0.19226 | 0.022888 | 0.036621 | 0.01831 | 0.21057 | -0.032043 | 0.35248 | 0.068664 | 0.032043 | -0.44861 | 0.25635 | 0.20142 | 0.068664 | -0.42572
4913.0156 | 0.022888 | -0.082397 | 0.19684 | -0.023041 | 0.020907 | 0.00074562 | 0.017111 | 0.028027 | -0.00050425 | -0.0072911 | 0.16769 | -0.0018628 | 0.015772 | -0.012884 | 0.016812 | -0.0072738 | -0.045776 | -0.018311 | -0.054932 | 0.013733 | 0.29755 | -0.10071 | -0.27924 | -0.10071 | -0.059509 | -0.09613 | 0.24719 | 0.16479 | -0.21973 | -0.21973 | -0.018311 | -0.19684 | 0.10071 | 0.064086 | 0.09613 | 0.29297 | -0.24261 | -0.13733 | -0.13733 | 0.050354 | -0.018311 | -0.013733 | 0.1236 | -0.032043 | 0.37994 | 0.036621 | 0.027465 | -0.47607 | 0.32959 | 0.24719 | 0.022888 | -0.41657
4914.0156 | 0.07782 | -0.041199 | 0.19226 | -0.076447 | 0.019839 | 0.0024544 | 0.01647 | 0.024823 | 0.00077755 | -0.0077183 | -0.084076 | -0.00464 | 0.017694 | -0.012456 | 0.016812 | -0.0059922 | 0.032043 | 0.050354 | 0.004578 | 0.045776 | 0.29755 | -0.09613 | -0.27466 | 0 | 0.018311 | -0.036621 | 0.22888 | 0.17395 | -0.20599 | -0.21515 | -0.054931 | -0.23346 | 0.10528 | 0.091553 | 0.086975 | 0.32043 | -0.16022 | -0.1648 | -0.17395 | 0.036621 | 0.041199 | 0.004578 | 0.17853 | -0.018311 | 0.33874 | 0.073242 | 0.045777 | -0.46692 | 0.27008 | 0.21515 | 0.05951 | -0.40741
4915.0156 | 0.022888 | -0.073242 | 0.19684 | -0.061188 | 0.02048 | 0.006086 | 0.01647 | 0.023114 | 0.0035547 | -0.010068 | 0.0074766 | -0.0033582 | 0.015344 | -0.014592 | 0.015958 | -0.0057786 | -0.027466 | -0.041199 | -0.073242 | 0.009155 | 0.31128 | -0.10529 | -0.29297 | -0.082397 | -0.054932 | -0.091553 | 0.24261 | 0.17853 | -0.22888 | -0.24261 | -0.032044 | -0.21973 | 0.11444 | 0.032043 | 0.082397 | 0.30212 | -0.2243 | -0.15564 | -0.16937 | 0.045777 | -0.009155 | -0.018311 | 0.15106 | -0.01831 | 0.38452 | 0.045776 | 0 | -0.48981 | 0.31586 | 0.25177 | 0.01831 | -0.43945
4916.0156 | 0.068665 | -0.036621 | 0.18768 | -0.12222 | 0.021121 | 0.0052316 | 0.018393 | 0.023328 | 0.0014185 | -0.011563 | -0.053558 | -0.0035718 | 0.015131 | -0.012029 | 0.01553 | -0.0064194 | 0.018311 | 0.064087 | -0.013733 | 0.050354 | 0.30212 | -0.10986 | -0.3067 | -0.004578 | 0.018311 | -0.041199 | 0.2243 | 0.16022 | -0.18768 | -0.22888 | -0.073242 | -0.27008 | 0.11444 | 0.10071 | 0.086975 | 0.35706 | -0.16937 | -0.15106 | -0.19226 | 0.036621 | 0.032043 | -0.004578 | 0.18768 | -0.027466 | 0.33875 | 0.054932 | 0.022888 | -0.49438 | 0.26093 | 0.19684 | 0.054932 | -0.41656
4917.0156 | 0.045776 | -0.036621 | 0.19226 | 0.030365 | 0.021121 | 0.0041634 | 0.019034 | 0.024609 | 0.0016321 | -0.010282 | -0.076446 | -0.0020764 | 0.015772 | -0.013311 | 0.016385 | -0.0074876 | 0.009155 | 0.036621 | -0.054932 | 0.032043 | 0.32044 | -0.10529 | -0.28381 | -0.036621 | -0.018311 | -0.059509 | 0.22888 | 0.17853 | -0.20599 | -0.23346 | -0.068665 | -0.24719 | 0.12817 | 0.073242 | 0.068664 | 0.31586 | -0.18311 | -0.16937 | -0.19684 | 0.036621 | 0 | -0.022888 | 0.17395 | -0.013733 | 0.35706 | 0.045776 | -0.018311 | -0.47607 | 0.2655 | 0.21515 | 0.01831 | -0.42572
4918.0156 | 0.07782 | -0.045776 | 0.1831 | 0.015106 | 0.018985 | 0.0048044 | 0.01647 | 0.0229 | -0.00071785 | -0.0075047 | -0.25192 | -0.0031446 | 0.015558 | -0.013311 | 0.015744 | -0.0051376 | -0.013733 | 0.036621 | -0.009155 | 0.054932 | 0.31128 | -0.11902 | -0.30212 | -0.022888 | 0.022888 | -0.018311 | 0.2243 | 0.17853 | -0.21973 | -0.23804 | -0.073243 | -0.25635 | 0.12817 | 0.082397 | 0.10071 | 0.35706 | -0.19684 | -0.17395 | -0.19226 | 0.041199 | 0.022888 | 0.027465 | 0.21973 | -0.004577 | 0.35705 | 0.032043 | 0.036621 | -0.48523 | 0.27008 | 0.2243 | 0.068664 | -0.42114
4919.0156 | 0.059509 | -0.082397 | 0.18768 | 0.19058 | 0.021548 | 0.005018 | 0.019461 | 0.02525 | 0.00077755 | -0.0083591 | 0.18295 | -0.0016492 | 0.016199 | -0.012884 | 0.013394 | -0.0044968 | -0.041199 | -0.045776 | -0.059509 | 0 | 0.32044 | -0.11902 | -0.29297 | -0.054932 | -0.036621 | -0.059509 | 0.24261 | 0.19226 | -0.20599 | -0.24261 | -0.036622 | -0.21057 | 0.13275 | 0.036621 | 0.082397 | 0.29297 | -0.22888 | -0.1236 | -0.16022 | 0.054932 | 0.027465 | 0.022888 | 0.18311 | 0.004578 | 0.40283 | 0.041198 | 0.022888 | -0.48065 | 0.32501 | 0.27466 | 0.045776 | -0.4303
4920.0156 | 0.064087 | -0.068665 | 0.20142 | -0.045929 | 0.018558 | 0.0035226 | 0.017752 | 0.026532 | 0.0024865 | -0.0087863 | -0.038299 | -0.0010084 | 0.015344 | -0.011815 | 0.015744 | -0.0059922 | 0.027466 | 0.036621 | -0.027466 | 0.027466 | 0.29755 | -0.10071 | -0.28381 | -0.036621 | -0.013733 | -0.059509 | 0.2243 | 0.1831 | -0.20142 | -0.23346 | -0.032043 | -0.21515 | 0.09613 | 0.10529 | 0.096131 | 0.31128 | -0.17395 | -0.13275 | -0.16479 | 0.022888 | 0.032044 | 0.009156 | 0.17395 | -0.018311 | 0.36621 | 0.096131 | 0.041199 | -0.48523 | 0.29297 | 0.25177 | 0.054932 | -0.43488
4921.0156 | 0.045776 | -0.073242 | 0.19226 | 0.25925 | 0.021548 | 0.0026682 | 0.01882 | 0.024182 | 0.0018457 | -0.0089999 | 0.083771 | -0.0018628 | 0.017053 | -0.014379 | 0.016385 | -0.0064194 | -0.059509 | -0.068665 | -0.073242 | -0.018311 | 0.32044 | -0.091553 | -0.29297 | -0.059509 | -0.054932 | -0.073242 | 0.23346 | 0.17395 | -0.23346 | -0.22888 | -0.018311 | -0.21973 | 0.12817 | 0.004577 | 0.054931 | 0.27466 | -0.25177 | -0.16022 | -0.15564 | 0.041198 | 0.013733 | 0 | 0.15564 | -0.018311 | 0.39368 | 0.013733 | 0 | -0.48523 | 0.3067 | 0.24719 | 0.01831 | -0.42114
4922.0156 | 0.045776 | -0.050354 | 0.17853 | -0.061188 | 0.018344 | 0.0043772 | 0.016257 | 0.02525 | 0.0022729 | -0.010495 | -0.084076 | -0.00058096 | 0.016626 | -0.013524 | 0.015744 | -0.0040696 | 0.054932 | 0.050354 | -0.013733 | 0.027466 | 0.32959 | -0.10071 | -0.28839 | -0.022888 | -0.009155 | -0.050354 | 0.21515 | 0.16937 | -0.20142 | -0.2243 | -0.050354 | -0.23804 | 0.15106 | 0.10071 | 0.07782 | 0.31586 | -0.1236 | -0.15106 | -0.17395 | 0.036621 | 0.027466 | 0 | 0.17395 | -0.009155 | 0.37994 | 0.10529 | 0.036621 | -0.46692 | 0.2655 | 0.21973 | 0.041199 | -0.40283
4923.0156 | 0.054932 | -0.086975 | 0.20142 | 0.0074768 | 0.021121 | 0.0030954 | 0.017325 | 0.025464 | -0.0015723 | -0.0096409 | 0.16006 | -0.0033582 | 0.014917 | -0.012029 | 0.01489 | -0.0047104 | -0.045776 | -0.064087 | -0.086975 | -0.009155 | 0.32501 | -0.10071 | -0.29755 | -0.059509 | -0.068665 | -0.068665 | 0.2243 | 0.16022 | -0.20599 | -0.24261 | -0.013733 | -0.21057 | 0.1236 | 0.022888 | 0.07782 | 0.28839 | -0.24719 | -0.11902 | -0.15564 | 0.022888 | 0.027466 | 0.01831 | 0.17395 | -0.041199 | 0.41199 | 0.041199 | 0 | -0.49896 | 0.31128 | 0.24719 | 0.01831 | -0.44403
4924.0156 | 0.086975 | -0.054932 | 0.1831 | -0.19089 | 0.017489 | 0.0024544 | 0.016684 | 0.026105 | 0.0020593 | -0.010495 | -0.168 | -0.0050672 | 0.016626 | -0.01267 | 0.014249 | -0.004924 | 0.041199 | 0.068665 | 0 | 0.045776 | 0.29755 | -0.10986 | -0.28839 | -0.018311 | 0.018311 | -0.027466 | 0.21515 | 0.17395 | -0.20599 | -0.21515 | -0.054931 | -0.23346 | 0.11444 | 0.1236 | 0.10071 | 0.33417 | -0.14191 | -0.15106 | -0.16022 | 0.032044 | 0.036621 | 0.027466 | 0.18768 | -0.009155 | 0.35248 | 0.096131 | 0.054932 | -0.4715 | 0.27008 | 0.22888 | 0.073243 | -0.39825
4925.0156 | 0.068665 | -0.073242 | 0.17395 | 0.13718 | 0.018558 | 0.0028818 | 0.014975 | 0.023755 | 0.00056395 | -0.0081455 | 0.19058 | -0.0035718 | 0.016199 | -0.012884 | 0.015744 | -0.0040696 | -0.022888 | -0.041199 | -0.068665 | 0.004578 | 0.3067 | -0.10986 | -0.2655 | -0.050354 | -0.059509 | -0.068665 | 0.23346 | 0.1831 | -0.20142 | -0.2243 | -0.036621 | -0.19226 | 0.13275 | 0.032043 | 0.07782 | 0.27008 | -0.19684 | -0.12817 | -0.15106 | 0.059509 | 0.022888 | 0.004577 | 0.15564 | 0.009155 | 0.37994 | 0.050354 | 0.004577 | -0.43945 | 0.3067 | 0.25635 | 0.013733 | -0.39825
4926.0156 | 0.059509 | -0.059509 | 0.19684 | -0.0383 | 0.019626 | 0.0011728 | 0.017111 | 0.023755 | 0.0041955 | -0.0083591 | -0.00015237 | -0.0016492 | 0.015558 | -0.011388 | 0.015317 | -0.0051376 | 0.013733 | 0.009155 | -0.041199 | 0.013733 | 0.30212 | -0.09613 | -0.28381 | -0.050354 | -0.032043 | -0.064087 | 0.22888 | 0.17853 | -0.20599 | -0.23346 | -0.036621 | -0.2243 | 0.10529 | 0.068664 | 0.073242 | 0.29755 | -0.18311 | -0.14649 | -0.17395 | 0.032044 | 0.009155 | -0.004578 | 0.16937 | -0.01831 | 0.36163 | 0.073242 | 0.01831 | -0.48065 | 0.28839 | 0.23804 | 0.027466 | -0.4303
4927.0156 | 0.10986 | -0.068665 | 0.18768 | 0.16006 | 0.016849 | 0.0039498 | 0.017325 | 0.023968 | 0.0012047 | -0.0087863 | 0.28214 | -0.0031446 | 0.014917 | -0.012243 | 0.016598 | -0.003856 | -0.004578 | 0.009155 | -0.045776 | 0.009155 | 0.29755 | -0.10986 | -0.27924 | -0.004578 | -0.009155 | -0.009155 | 0.2243 | 0.14648 | -0.19226 | -0.20599 | -0.041198 | -0.21057 | 0.10986 | 0.07782 | 0.07782 | 0.28839 | -0.19226 | -0.1236 | -0.13733 | 0.036621 | 0.064087 | 0.05951 | 0.19684 | -0.041199 | 0.36621 | 0.064087 | 0.022889 | -0.46692 | 0.29297 | 0.21515 | 0.05951 | -0.39368
4928.0156 | 0.027466 | -0.073242 | 0.19684 | -0.00015269 | 0.020053 | 0.0039498 | 0.017752 | 0.026318 | 0.00056395 | -0.0072911 | 0.083771 | -0.0031446 | 0.013422 | -0.011388 | 0.016812 | -0.0040696 | 0.009155 | -0.009155 | -0.041199 | 0.013733 | 0.31128 | -0.09613 | -0.30212 | -0.068665 | -0.050354 | -0.09613 | 0.21057 | 0.17853 | -0.21973 | -0.23346 | -0.022888 | -0.22888 | 0.11444 | 0.064087 | 0.086975 | 0.31586 | -0.18768 | -0.14649 | -0.16022 | 0.013733 | 0.004577 | -0.022888 | 0.13733 | -0.01831 | 0.38452 | 0.082397 | 0.032043 | -0.49896 | 0.28381 | 0.25177 | 0.022888 | -0.4303
4929.0156 | 0.073242 | -0.068665 | 0.16937 | 0.14481 | 0.02048 | 0.0035226 | 0.015616 | 0.024609 | 0.0012047 | -0.0083591 | 0.20584 | -0.0020764 | 0.015558 | -0.01267 | 0.016385 | -0.0044968 | -0.018311 | -0.027466 | -0.050354 | 0.018311 | 0.30212 | -0.11444 | -0.29297 | -0.036621 | -0.050354 | -0.027466 | 0.22888 | 0.17395 | -0.21973 | -0.23346 | -0.045776 | -0.2243 | 0.13275 | 0.041199 | 0.086976 | 0.31128 | -0.18768 | -0.15106 | -0.16479 | 0.059509 | 0.032044 | 0.041199 | 0.20599 | 0.004577 | 0.37079 | 0.050354 | 0.018311 | -0.46234 | 0.29755 | 0.24261 | 0.018311 | -0.40283
4930.0156 | 0.045776 | -0.068665 | 0.18768 | 0.076141 | 0.019412 | 0.0030954 | 0.017966 | 0.027814 | 0.0029137 | -0.0081455 | -0.015411 | -0.0016492 | 0.01684 | -0.013952 | 0.017453 | -0.0072738 | 0.022888 | 0.009155 | -0.032043 | 0.004578 | 0.31128 | -0.091553 | -0.3067 | -0.050354 | -0.022888 | -0.086975 | 0.21973 | 0.18768 | -0.19226 | -0.24261 | -0.022888 | -0.23804 | 0.1236 | 0.07782 | 0.073243 | 0.31128 | -0.16479 | -0.1236 | -0.17395 | 0.032044 | 0.018311 | -0.01831 | 0.15564 | 0 | 0.37994 | 0.091553 | 0.036622 | -0.49438 | 0.28839 | 0.25635 | 0.045777 | -0.4303
4931.0156 | 0.050354 | -0.07782 | 0.1831 | 0.060882 | 0.020053 | 0.003309 | 0.016684 | 0.024182 | 0.0016321 | -0.0085727 | -0.03067 | -0.002931 | 0.016199 | -0.013738 | 0.016171 | -0.004924 | -0.022888 | -0.059509 | -0.082397 | -0.004578 | 0.32501 | -0.09613 | -0.27924 | -0.054932 | -0.054932 | -0.082397 | 0.24719 | 0.17395 | -0.2243 | -0.23804 | -0.01831 | -0.20142 | 0.14191 | 0.018311 | 0.073242 | 0.27466 | -0.20599 | -0.14648 | -0.16022 | 0.064087 | 0.022888 | -0.004577 | 0.15564 | -0.009155 | 0.40283 | 0.054932 | -0.004577 | -0.46234 | 0.32501 | 0.25177 | 0.022888 | -0.42114
4932.0156 | 0.045776 | -0.068665 | 0.18768 | 0.022736 | 0.020907 | 0.0035226 | 0.018607 | 0.026532 | 0.00013675 | -0.0087863 | 0.076141 | -0.00229 | 0.014276 | -0.013311 | 0.01553 | -0.0068466 | 0.032043 | -0.004578 | -0.050354 | 0.018311 | 0.30212 | -0.091553 | -0.28839 | -0.045776 | -0.032043 | -0.064087 | 0.21973 | 0.19684 | -0.21057 | -0.23346 | -0.022888 | -0.21973 | 0.11444 | 0.064087 | 0.086976 | 0.3067 | -0.15564 | -0.14191 | -0.16479 | 0.032044 | 0.022889 | 0.004578 | 0.16937 | 0.009155 | 0.37079 | 0.10071 | 0.018311 | -0.47607 | 0.28839 | 0.2655 | 0.036622 | -0.42114
4933.0312 | 0.14191 | 0 | 0.17395 | -0.023041 | 0.013431 | 0.0056588 | 0.014334 | 0.022259 | -0.0071265 | -0.011991 | -0.16037 | -0.0037854 | 0.011072 | -0.01502 | 0.01254 | -0.0023606 | 0.045776 | 0.15564 | 0.068665 | 0.073242 | 0.2655 | -0.086975 | -0.28839 | 0.032043 | 0.11902 | 0.082397 | 0.21057 | 0.14648 | -0.1831 | -0.20142 | -0.086975 | -0.28839 | 0.091553 | 0.15564 | 0.073242 | 0.36163 | -0.12817 | -0.1831 | -0.20142 | 0.036621 | 0.032043 | 0.082397 | 0.28381 | -0.027466 | 0.2655 | 0.045776 | 0.068665 | -0.46234 | 0.21057 | 0.14648 | 0.11902 | -0.37537
4934.0156 | 0.027466 | -0.086975 | 0.19684 | 0.083771 | 0.020907 | 0.0041634 | 0.019034 | 0.022259 | 0.0022729 | -0.010282 | -0.03067 | -0.0048536 | 0.020685 | -0.013952 | 0.017453 | -0.0059922 | -0.036621 | -0.036621 | -0.059509 | 0 | 0.31586 | -0.091553 | -0.27924 | -0.091553 | -0.068665 | -0.086975 | 0.21515 | 0.1831 | -0.21973 | -0.25635 | -0.004578 | -0.19226 | 0.11902 | 0.050354 | 0.086975 | 0.27924 | -0.23346 | -0.13275 | -0.16937 | 0.018311 | -0.004578 | 0 | 0.16937 | -0.013733 | 0.40283 | 0.050354 | 0.027466 | -0.47607 | 0.30212 | 0.27008 | 0.01831 | -0.45319
4935.0156 | 0.11444 | -0.054932 | 0.15106 | 0.22873 | 0.020053 | 0.0041634 | 0.014548 | 0.024396 | 0.00099115 | -0.0089999 | 0.14481 | -0.0025038 | 0.017053 | -0.013097 | 0.01553 | -0.0044968 | -0.018311 | -0.013733 | -0.018311 | 0.018311 | 0.31586 | -0.10071 | -0.28381 | -0.013733 | -0.027466 | -0.032043 | 0.21057 | 0.16937 | -0.18768 | -0.22888 | -0.045776 | -0.22888 | 0.16479 | 0.041199 | 0.073243 | 0.30212 | -0.16937 | -0.13275 | -0.17395 | 0.059509 | 0.041199 | 0.022889 | 0.19684 | 0.018311 | 0.37079 | 0.036621 | 0.036621 | -0.43488 | 0.2655 | 0.22431 | 0.027466 | -0.37994
4936.0156 | 0.050354 | -0.068665 | 0.19684 | 0.19821 | 0.019412 | 0.003309 | 0.018179 | 0.024823 | -7.6852e-05 | -0.0064365 | 0.19821 | -0.0037854 | 0.017908 | -0.01267 | 0.014249 | -0.004924 | -0.022888 | -0.054932 | -0.068665 | 0.004578 | 0.31586 | -0.09613 | -0.28839 | -0.064087 | -0.054932 | -0.064087 | 0.2243 | 0.21057 | -0.20599 | -0.24719 | -0.027465 | -0.21973 | 0.11902 | 0.013733 | 0.073243 | 0.29297 | -0.21973 | -0.13733 | -0.17853 | 0.027466 | 0.004578 | 0.004578 | 0.1831 | 0.013733 | 0.38452 | 0.045777 | 0 | -0.48523 | 0.29297 | 0.27924 | 0.013733 | -0.44403
4937.0156 | 0.17395 | -0.032043 | 0.15106 | 0.21347 | 0.017703 | 0.00095922 | 0.016684 | 0.026105 | -0.0024269 | -0.0087863 | 0.16006 | -0.00464 | 0.014704 | -0.01267 | 0.014035 | -0.0070602 | 0.086975 | 0.09613 | 0.059509 | 0.07782 | 0.25177 | -0.07782 | -0.25177 | 0.059509 | 0.082397 | 0.059509 | 0.18768 | 0.12817 | -0.16479 | -0.20142 | -0.045777 | -0.21973 | 0.10071 | 0.12817 | 0.10986 | 0.32959 | -0.064087 | -0.13275 | -0.16937 | 0.036621 | 0.091552 | 0.091552 | 0.26093 | -0.022888 | 0.28381 | 0.11902 | 0.091552 | -0.40283 | 0.21973 | 0.16022 | 0.11444 | -0.35248
4938.0156 | 0.14191 | -0.045776 | 0.16937 | -0.053558 | 0.012149 | 0.0056588 | 0.013693 | 0.024396 | -0.0062721 | -0.0089999 | 0.15244 | -0.0042126 | 0.011926 | -0.015874 | 0.013181 | -0.0047104 | 0.009155 | 0.064087 | 0.022888 | 0.050354 | 0.28839 | -0.082397 | -0.24719 | -0.004578 | 0.036621 | 0.068665 | 0.1831 | 0.16479 | -0.17395 | -0.2243 | -0.036621 | -0.20142 | 0.11902 | 0.10986 | 0.09613 | 0.29755 | -0.16022 | -0.12817 | -0.17853 | 0.013732 | 0.041198 | 0.11444 | 0.29297 | -0.004578 | 0.33417 | 0.054931 | 0.068664 | -0.41656 | 0.22888 | 0.21057 | 0.082397 | -0.39368
4939.0156 | 0.064087 | -0.091553 | 0.18768 | 0.11429 | 0.021121 | 0.0026682 | 0.019461 | 0.023328 | 0.0022729 | -0.0081455 | 0.17532 | -0.0042126 | 0.015344 | -0.013524 | 0.019803 | -0.0064194 | 0.013733 | -0.032043 | -0.068665 | -0.009155 | 0.32044 | -0.09613 | -0.29755 | -0.027466 | -0.059509 | -0.07782 | 0.23804 | 0.1831 | -0.21057 | -0.22888 | -0.004577 | -0.20599 | 0.13275 | 0.05951 | 0.082398 | 0.28839 | -0.17395 | -0.11902 | -0.13733 | 0.050354 | 0.064087 | 0.013733 | 0.15106 | -0.004578 | 0.41199 | 0.10529 | 0.022888 | -0.48523 | 0.32959 | 0.27466 | 0.032044 | -0.41656
4940.0156 | 0.050354 | -0.082397 | 0.1831 | 0.13718 | 0.022616 | 0.0037362 | 0.019461 | 0.024823 | 0.0033411 | -0.0079319 | 0.12955 | -0.0016492 | 0.017694 | -0.012243 | 0.017026 | -0.005565 | -0.018311 | -0.050354 | -0.073242 | 0 | 0.32044 | -0.10529 | -0.30212 | -0.068665 | -0.07782 | -0.086975 | 0.24261 | 0.17853 | -0.20599 | -0.24261 | -0.022889 | -0.21973 | 0.13733 | 0.032043 | 0.082397 | 0.30212 | -0.20142 | -0.1236 | -0.16022 | 0.05951 | 0.013732 | -0.004578 | 0.15564 | -0.004577 | 0.40283 | 0.064086 | 0.009155 | -0.48523 | 0.32501 | 0.26092 | 0.004577 | -0.42572
4941.0156 | 0.1236 | -0.054932 | 0.16022 | 0.16769 | 0.01813 | 0.0054452 | 0.019461 | 0.024396 | -0.00093145 | -0.010922 | 0.16769 | -0.003999 | 0.015985 | -0.011175 | 0.017667 | -0.006633 | 0.009155 | 0.018311 | -0.018311 | 0.032043 | 0.30212 | -0.10529 | -0.27924 | 0 | 0 | -0.013733 | 0.20142 | 0.16479 | -0.19226 | -0.21057 | -0.050354 | -0.2243 | 0.14191 | 0.073243 | 0.086975 | 0.31128 | -0.15106 | -0.13733 | -0.15564 | 0.041199 | 0.054932 | 0.041199 | 0.19684 | 0.004578 | 0.35706 | 0.064087 | 0.036621 | -0.43945 | 0.25635 | 0.21973 | 0.054932 | -0.37079
4942.0156 | 0.036621 | -0.054932 | 0.1831 | -0.068817 | 0.021548 | 0.0043772 | 0.020316 | 0.025891 | 0.0012047 | -0.0092137 | -0.076446 | -0.00229 | 0.015131 | -0.01502 | 0.016171 | -0.0072738 | -0.022888 | -0.027466 | -0.064087 | -0.009155 | 0.30212 | -0.10071 | -0.28381 | -0.07782 | -0.068665 | -0.10986 | 0.23346 | 0.18768 | -0.22888 | -0.2243 | -0.045776 | -0.22888 | 0.11902 | 0.027466 | 0.045777 | 0.27466 | -0.20599 | -0.17395 | -0.16937 | 0.050354 | -0.022888 | -0.054931 | 0.11444 | 0.004578 | 0.35706 | 0.032044 | -0.009155 | -0.46692 | 0.28839 | 0.24261 | -0.013733 | -0.40741
4943.0156 | 0.12817 | 0.009155 | 0.15564 | -0.168 | 0.011935 | 0.006086 | 0.017111 | 0.021619 | -0.0071265 | -0.010282 | -0.168 | -0.007417 | 0.010858 | -0.01502 | 0.01553 | -0.005565 | 0.050354 | 0.14648 | 0.07782 | 0.082397 | 0.2655 | -0.073242 | -0.25635 | 0.032043 | 0.10071 | 0.064087 | 0.19684 | 0.12817 | -0.18768 | -0.2243 | -0.082397 | -0.2655 | 0.10986 | 0.13733 | 0.073242 | 0.33875 | -0.10529 | -0.19684 | -0.23346 | 0.041198 | 0.022888 | 0.054932 | 0.28839 | -0.027466 | 0.25635 | 0.041199 | 0.068665 | -0.41199 | 0.18768 | 0.11902 | 0.091553 | -0.37994
4944.0156 | 0.027466 | -0.082397 | 0.18768 | -0.00015269 | 0.02048 | 0.003309 | 0.017111 | 0.024396 | 0.0014185 | -0.0083591 | 0.10666 | -0.002931 | 0.015558 | -0.013097 | 0.017239 | -0.0068466 | -0.018311 | 0.009155 | -0.059509 | 0.013733 | 0.31128 | -0.10071 | -0.28381 | -0.054932 | -0.073242 | -0.10529 | 0.24261 | 0.17395 | -0.2243 | -0.24719 | -0.018311 | -0.20142 | 0.1236 | 0.091552 | 0.09613 | 0.29755 | -0.20599 | -0.14191 | -0.16479 | 0.054932 | 0.027465 | -0.022889 | 0.14191 | -0.013733 | 0.39368 | 0.064086 | 0.022888 | -0.4715 | 0.32501 | 0.25635 | 0.009155 | -0.43488
4945.0156 | 0.086975 | -0.059509 | 0.1831 | 0.19821 | 0.020053 | 0.003309 | 0.017111 | 0.023114 | -7.6852e-05 | -0.0089999 | 0.12955 | -0.0027174 | 0.015558 | -0.012456 | 0.016598 | -0.0059922 | 0 | -0.027466 | -0.050354 | 0 | 0.3067 | -0.10071 | -0.27466 | -0.004578 | -0.004578 | -0.027466 | 0.20599 | 0.15106 | -0.20142 | -0.23346 | -0.041199 | -0.21515 | 0.1236 | 0.032043 | 0.059509 | 0.27466 | -0.1831 | -0.14191 | -0.17395 | 0.022889 | 0.054931 | 0.032043 | 0.20599 | -0.032043 | 0.36621 | 0.059509 | 0.009155 | -0.45776 | 0.2655 | 0.21057 | 0.054931 | -0.41656
4946.0156 | 0.041199 | -0.07782 | 0.19226 | 0.13718 | 0.023898 | 0.005018 | 0.01882 | 0.026105 | 0.00035035 | -0.0072911 | 0.12955 | -0.0033582 | 0.015558 | -0.01267 | 0.013608 | -0.0074876 | -0.022888 | -0.045776 | -0.064087 | 0.009155 | 0.32044 | -0.11444 | -0.29297 | -0.041199 | -0.068665 | -0.07782 | 0.22888 | 0.16937 | -0.21057 | -0.22888 | -0.036621 | -0.21515 | 0.12817 | 0.032044 | 0.086975 | 0.30212 | -0.21515 | -0.13275 | -0.15106 | 0.036621 | 0.036621 | 0 | 0.15106 | -0.022888 | 0.39826 | 0.054932 | 0.013733 | -0.48523 | 0.3067 | 0.24719 | 0.009155 | -0.42114
4947.0156 | 0.15106 | -0.032043 | 0.16022 | 0.16769 | 0.019412 | 0.0045908 | 0.011984 | 0.025037 | 0.00035035 | -0.0096409 | 0.36606 | -0.0037854 | 0.015131 | -0.013311 | 0.015317 | -0.0053512 | 0.045776 | 0.059509 | 0.036621 | 0.073242 | 0.28839 | -0.073242 | -0.27008 | 0.054932 | 0.073242 | 0.059509 | 0.19684 | 0.14648 | -0.17853 | -0.20142 | -0.041199 | -0.23804 | 0.12817 | 0.091552 | 0.10529 | 0.34332 | -0.11444 | -0.14648 | -0.16937 | 0.036621 | 0.086975 | 0.091552 | 0.26093 | -0.013733 | 0.32043 | 0.077819 | 0.068664 | -0.4303 | 0.22888 | 0.17853 | 0.10529 | -0.36163
4948.0156 | 0.13733 | -0.022888 | 0.16937 | -0.023041 | 0.010653 | 0.0090768 | 0.014761 | 0.025037 | -0.0077673 | -0.010922 | 0.12192 | -0.0052808 | 0.012995 | -0.01502 | 0.014462 | -0.003856 | -0.004578 | 0.050354 | 0.045776 | 0.045776 | 0.27924 | -0.082397 | -0.25635 | 0.009155 | 0.054932 | 0.059509 | 0.19226 | 0.16937 | -0.17395 | -0.21057 | -0.059509 | -0.23346 | 0.10986 | 0.073242 | 0.068664 | 0.30212 | -0.17395 | -0.15106 | -0.18768 | 0.022888 | 0.032043 | 0.082397 | 0.27008 | 0 | 0.30212 | 0.01831 | 0.068664 | -0.42572 | 0.21515 | 0.19226 | 0.07782 | -0.37994
4949.0156 | 0.1831 | -0.041199 | 0.14648 | 0.060882 | 0.017062 | 0.0043772 | 0.017539 | 0.024609 | 0.0027001 | -0.0098545 | 0.0914 | -0.0033582 | 0.016199 | -0.014592 | 0.015744 | -0.0070602 | 0.036621 | 0.032043 | 0.009155 | 0.041199 | 0.29755 | -0.064087 | -0.2655 | 0.041199 | 0.054932 | 0.032043 | 0.20142 | 0.13733 | -0.15564 | -0.19226 | -0.022888 | -0.2243 | 0.15106 | 0.073242 | 0.082398 | 0.3067 | -0.10986 | -0.11444 | -0.15106 | 0.054932 | 0.082398 | 0.073242 | 0.2243 | -0.009155 | 0.33874 | 0.07782 | 0.050354 | -0.41199 | 0.24262 | 0.17853 | 0.096131 | -0.33874
4950.0156 | 0.036621 | -0.054932 | 0.19684 | 0.045624 | 0.018985 | 0.0052316 | 0.019461 | 0.026959 | 0.0016321 | -0.0089999 | 0.14481 | -0.003999 | 0.014917 | -0.013097 | 0.015958 | -0.006633 | -0.013733 | -0.091553 | -0.054932 | -0.009155 | 0.31128 | -0.10071 | -0.28381 | -0.036621 | -0.059509 | -0.073242 | 0.23804 | 0.1831 | -0.20142 | -0.23804 | -0.045776 | -0.22888 | 0.11444 | -0.036621 | 0.045777 | 0.27466 | -0.21057 | -0.14648 | -0.1831 | 0.041199 | 0.018311 | -0.01831 | 0.16479 | -0.013733 | 0.36621 | 0.041199 | 0 | -0.48065 | 0.29297 | 0.23804 | -0.004577 | -0.43488

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2 | Cable 3
-0.8865 | 24.679 | 25.5327 | 25.6549 | 25.4979
0.1135 | 24.6845 | 25.5159 | 25.6523 | 25.4948
1.1135 | 24.6644 | 25.5205 | 25.652 | 25.5014
2.1135 | 24.6855 | 25.5252 | 25.6539 | 25.4999
3.1135 | 25.0017 | 25.53 | 25.6551 | 25.5
4.1135 | 26.0393 | 25.5307 | 25.6572 | 25.4919
5.1135 | 27.8582 | 25.533 | 25.6619 | 25.495
6.1135 | 30.3761 | 25.541 | 25.6713 | 25.4902
7.1135 | 33.4215 | 25.5492 | 25.6833 | 25.4956
8.1135 | 36.9491 | 25.5533 | 25.7006 | 25.4928
9.1135 | 40.866 | 25.5529 | 25.7179 | 25.4946
10.1135 | 45.095 | 25.5795 | 25.7342 | 25.4917
11.1135 | 49.6076 | 25.597 | 25.7623 | 25.4872
12.1135 | 54.2899 | 25.619 | 25.7991 | 25.4879
13.1135 | 59.1918 | 25.6415 | 25.8202 | 25.4913
14.1135 | 64.2203 | 25.6698 | 25.8606 | 25.4901
15.1135 | 69.4006 | 25.7147 | 25.9204 | 25.4932
16.1135 | 74.6781 | 25.746 | 25.9689 | 25.491
17.1135 | 80.1259 | 25.8006 | 26.0294 | 25.4927
18.1135 | 85.6518 | 25.8481 | 26.0827 | 25.4887
19.1135 | 91.1921 | 25.9117 | 26.1654 | 25.4929
20.1135 | 96.8417 | 25.9753 | 26.2484 | 25.493
21.1135 | 102.5868 | 26.0478 | 26.3062 | 25.4928
22.1135 | 108.4862 | 26.1138 | 26.3972 | 25.4917
23.1135 | 114.4291 | 26.2058 | 26.5164 | 25.4886
24.1135 | 120.4165 | 26.2922 | 26.6179 | 25.4909
25.1135 | 126.3766 | 26.4032 | 26.7272 | 25.4971
26.1135 | 132.311 | 26.4801 | 26.9019 | 25.4963
27.1135 | 138.3562 | 26.6176 | 27.0536 | 25.5017
28.1135 | 144.3916 | 26.7357 | 27.0745 | 25.4981
29.1135 | 150.3973 | 26.8621 | 27.1214 | 25.5047
30.1135 | 156.3725 | 27.0041 | 27.2497 | 25.5048
31.1135 | 162.2891 | 27.1116 | 27.4291 | 25.5102
32.1135 | 168.244 | 27.2554 | 27.5606 | 25.514
33.1135 | 174.2102 | 27.4055 | 27.7406 | 25.516
34.1135 | 180.0897 | 27.5562 | 27.8472 | 25.5215
35.1135 | 185.9614 | 27.7575 | 27.9511 | 25.5291
36.1135 | 191.898 | 27.9385 | 28.13 | 25.5327
37.1135 | 197.8205 | 28.1219 | 28.2679 | 25.5506
38.1135 | 203.8273 | 28.3409 | 28.4353 | 25.5522
39.1135 | 209.7419 | 28.5798 | 28.5956 | 25.5608
40.1135 | 215.7412 | 28.7743 | 28.7981 | 25.5639
41.1135 | 221.7746 | 29.0108 | 29.0527 | 25.5794
42.1135 | 227.757 | 29.2565 | 29.2769 | 25.5863
43.1135 | 233.7429 | 29.491 | 29.5151 | 25.6004
44.1135 | 239.7744 | 29.759 | 29.8798 | 25.6092
45.1135 | 245.6981 | 30.0047 | 30.1678 | 25.6261
46.1135 | 251.5635 | 30.3103 | 30.3544 | 25.6431
47.1135 | 257.527 | 30.664 | 30.6748 | 25.6525
48.1135 | 263.3252 | 30.9479 | 30.9185 | 25.6701
49.1135 | 269.0069 | 31.3143 | 31.1612 | 25.6911
50.1135 | 274.8632 | 31.6511 | 31.4469 | 25.7037
51.1135 | 280.6659 | 31.9635 | 31.7699 | 25.7145
52.1135 | 286.4874 | 32.3132 | 32.1442 | 25.7302
53.1135 | 292.2994 | 32.6439 | 32.3801 | 25.7521
54.1135 | 298.0824 | 32.977 | 32.6752 | 25.7824
55.1135 | 303.7924 | 33.367 | 33.0168 | 25.8017
56.1135 | 309.327 | 33.8094 | 33.4059 | 25.821
57.1135 | 314.8755 | 34.2211 | 33.7739 | 25.8485
58.1135 | 320.3267 | 34.6683 | 34.1778 | 25.8794
59.1135 | 325.7568 | 35.1173 | 34.5936 | 25.9083
60.1135 | 331.1953 | 35.5978 | 35.0232 | 25.9383
61.1135 | 336.792 | 36.0788 | 35.4735 | 25.9719
62.1135 | 342.3077 | 36.4991 | 35.9815 | 26.0137
63.1135 | 347.8349 | 36.9905 | 36.4117 | 26.047
64.1135 | 353.2995 | 37.5222 | 36.8954 | 26.0819
65.1135 | 358.8155 | 38.0597 | 37.3761 | 26.1276
66.1135 | 364.2447 | 38.5898 | 37.9171 | 26.1727
67.1135 | 369.6309 | 39.1106 | 38.4291 | 26.2129
68.1135 | 374.8686 | 39.727 | 38.8837 | 26.2626
69.1135 | 380.1178 | 40.326 | 39.4225 | 26.3055
70.1135 | 385.3206 | 40.9273 | 39.9705 | 26.3565
71.1135 | 390.5411 | 41.5484 | 40.6393 | 26.4167
72.1135 | 395.8704 | 42.1776 | 41.1987 | 26.474
73.1135 | 401.073 | 42.9058 | 41.898 | 26.5248
74.1135 | 405.9131 | 43.5547 | 42.5189 | 26.5888
75.1135 | 410.3384 | 44.2179 | 43.0507 | 26.648
76.1135 | 414.2833 | 44.9098 | 43.6949 | 26.7146
77.1135 | 417.8979 | 45.611 | 44.3055 | 26.7827
78.1135 | 421.3001 | 46.3391 | 44.9066 | 26.8553
79.1135 | 424.5475 | 47.1021 | 45.5659 | 26.9315
80.1135 | 427.6699 | 47.8703 | 46.2133 | 27.0093
81.1135 | 430.805 | 48.563 | 46.8439 | 27.0883
82.1135 | 433.6784 | 49.2411 | 47.5547 | 27.1662
83.1135 | 436.3275 | 49.934 | 48.2481 | 27.2565
84.1135 | 438.8808 | 50.6219 | 48.8937 | 27.3497
85.1135 | 441.0845 | 51.3475 | 49.5647 | 27.4376
86.1135 | 442.9811 | 52.0906 | 50.2183 | 27.5309
87.1135 | 444.6134 | 52.8614 | 50.8722 | 27.6298
88.1135 | 446.1299 | 53.6704 | 51.4513 | 27.7313
89.1135 | 447.3066 | 54.3501 | 52.0925 | 27.8353
90.1135 | 448.1732 | 55.1234 | 52.7336 | 27.9477
91.1135 | 449.0124 | 55.879 | 53.4081 | 28.0645
92.1135 | 449.5662 | 56.5961 | 54.1002 | 28.1726
93.1135 | 450.057 | 57.327 | 54.7323 | 28.2856
94.1135 | 450.3915 | 58.0554 | 55.3408 | 28.4095
95.1135 | 450.4517 | 58.7895 | 55.9714 | 28.532
96.1135 | 450.4488 | 59.4093 | 56.6141 | 28.6627
97.1135 | 450.416 | 60.0984 | 57.234 | 28.787
98.1135 | 450.3782 | 60.8449 | 57.8411 | 28.9219
99.1135 | 450.3079 | 61.535 | 58.5927 | 29.0625
100.1135 | 450.2049 | 62.2768 | 59.3141 | 29.1981
101.1135 | 450.2011 | 63.0271 | 59.895 | 29.3504
102.1135 | 449.9526 | 63.6706 | 60.5025 | 29.4943
103.1135 | 449.8394 | 64.3543 | 61.0714 | 29.6477
104.1135 | 449.7303 | 65.0323 | 61.6661 | 29.8066
105.1135 | 449.4961 | 65.7681 | 62.293 | 29.9619
106.1135 | 449.2812 | 66.5484 | 62.9067 | 30.1258
107.1135 | 449.0942 | 67.2458 | 63.5702 | 30.2959
108.1135 | 448.9037 | 67.8865 | 64.1537 | 30.4606
109.1135 | 448.6747 | 68.591 | 64.8836 | 30.6467
110.1135 | 448.5211 | 69.3099 | 65.5229 | 30.8257
111.1135 | 448.2833 | 70.0159 | 66.0872 | 30.9987
112.1135 | 448.1758 | 70.6611 | 66.6424 | 31.1767
113.1135 | 448.1161 | 71.3387 | 67.3549 | 31.3596
114.1135 | 447.8982 | 72.0026 | 67.9527 | 31.5502
115.1135 | 447.8111 | 72.6379 | 68.5142 | 31.7338
116.1135 | 447.8102 | 73.2719 | 69.0907 | 31.9257
117.1135 | 447.8339 | 73.9612 | 69.7152 | 32.122
118.1135 | 447.9223 | 74.7054 | 70.3108 | 32.3171
119.1135 | 448.0466 | 75.3657 | 70.8954 | 32.522
120.1135 | 448.0992 | 76.0084 | 71.5333 | 32.7246
121.1135 | 448.1603 | 76.6905 | 72.1605 | 32.9228
122.1135 | 448.2665 | 77.388 | 72.6991 | 33.13
123.1135 | 448.2923 | 78.0386 | 73.295 | 33.3422
124.1135 | 448.4899 | 78.7166 | 73.8795 | 33.5494
125.1135 | 448.6541 | 79.3993 | 74.4936 | 33.759
126.1135 | 448.7431 | 80.08 | 75.1175 | 33.9803
127.1135 | 448.7921 | 80.8614 | 75.726 | 34.1913
128.1135 | 448.8742 | 81.4203 | 76.3633 | 34.4033
129.1135 | 449.0246 | 82.0787 | 76.9465 | 34.6305
130.1135 | 449.1904 | 82.7398 | 77.5686 | 34.8464
131.1135 | 449.4156 | 83.3999 | 78.1662 | 35.065
132.1135 | 449.5306 | 84.0517 | 78.7659 | 35.2936
133.1135 | 449.7337 | 84.7308 | 79.3179 | 35.5057
134.1135 | 449.7508 | 85.4393 | 79.8735 | 35.7335
135.1135 | 449.7245 | 86.0837 | 80.5228 | 35.9658
136.1135 | 449.7619 | 86.7325 | 81.1375 | 36.1887
137.1135 | 449.8618 | 87.4063 | 81.7817 | 36.418
138.1135 | 449.9771 | 88.043 | 82.43 | 36.6539
139.1135 | 449.9825 | 88.6991 | 83.0807 | 36.8772
140.1135 | 450.1529 | 89.4051 | 83.6369 | 37.1089
141.1135 | 450.3113 | 90.107 | 84.1499 | 37.3433
142.1135 | 450.3592 | 90.7675 | 84.6885 | 37.5752
143.1135 | 450.3926 | 91.4095 | 85.3536 | 37.8101
144.1135 | 450.4608 | 92.0327 | 85.933 | 38.0474
145.1135 | 450.5659 | 92.8133 | 86.5253 | 38.278
146.1135 | 450.6912 | 93.3825 | 87.0698 | 38.5148
147.1135 | 450.7781 | 93.9783 | 87.6575 | 38.7504
148.1135 | 450.7591 | 94.6122 | 88.2802 | 38.985
149.1135 | 450.6861 | 95.2563 | 88.8819 | 39.2197
150.1135 | 450.6512 | 95.867 | 89.4859 | 39.4635
151.1135 | 450.7225 | 96.5015 | 90.0799 | 39.6967
152.1135 | 450.7758 | 97.1489 | 90.6814 | 39.9368
153.1135 | 450.8813 | 97.7762 | 91.3451 | 40.1795
154.1135 | 450.9593 | 98.4368 | 91.9321 | 40.426
155.1135 | 450.989 | 99.1043 | 92.4783 | 40.6709
156.1135 | 451.0158 | 99.7067 | 93.0211 | 40.9087
157.1135 | 451.0235 | 100.3848 | 93.6635 | 41.1395
158.1135 | 451.1777 | 101.0264 | 94.271 | 41.3886
159.1135 | 451.1705 | 101.6353 | 94.8716 | 41.6245
160.1135 | 451.1764 | 102.2773 | 95.4234 | 41.8639
161.1135 | 451.1809 | 102.846 | 95.9628 | 42.1032
162.1135 | 451.1378 | 103.47 | 96.5494 | 42.3504
163.1135 | 451.0631 | 104.0944 | 97.1156 | 42.5889
164.1135 | 451.0418 | 104.703 | 97.7466 | 42.8373
165.1135 | 450.9068 | 105.3139 | 98.3064 | 43.0776
166.1135 | 450.9119 | 105.9392 | 98.8973 | 43.3234
167.1135 | 450.9163 | 106.5757 | 99.5337 | 43.5615
168.1135 | 450.9218 | 107.197 | 100.0828 | 43.8098
169.1135 | 451.0087 | 107.8157 | 100.6213 | 44.0484
170.1135 | 451.0737 | 108.4399 | 101.2275 | 44.3042
171.1135 | 451.0395 | 109.1453 | 101.8324 | 44.5459
172.1135 | 451.0489 | 109.7112 | 102.4625 | 44.7968
173.1135 | 451.0728 | 110.3054 | 102.9833 | 45.0369
174.1135 | 451.0707 | 110.9107 | 103.489 | 45.2892
175.1135 | 451.1535 | 111.5055 | 104.172 | 45.5354
176.1135 | 451.1242 | 112.1454 | 104.7943 | 45.7836
177.1135 | 451.278 | 112.7498 | 105.3547 | 46.0311
178.1135 | 451.3045 | 113.4665 | 105.881 | 46.2813
179.1135 | 451.3328 | 114.0725 | 106.485 | 46.5297
180.1135 | 451.2219 | 114.6931 | 107.0609 | 46.783
181.1135 | 451.2564 | 115.2358 | 107.6542 | 47.0344
182.1135 | 451.3068 | 115.8115 | 108.1202 | 47.2857
183.1135 | 451.3371 | 116.4301 | 108.6814 | 47.5399
184.1135 | 451.3885 | 117.0109 | 109.2384 | 47.7882
185.1135 | 451.5011 | 117.6248 | 109.8237 | 48.0477
186.1135 | 451.6429 | 118.214 | 110.4159 | 48.3015
187.1135 | 451.7188 | 118.7854 | 111.0004 | 48.5627
188.1135 | 451.7486 | 119.3441 | 111.5324 | 48.8088
189.1135 | 451.7641 | 119.9532 | 112.1201 | 49.0778
190.1135 | 451.7781 | 120.5659 | 112.6492 | 49.3329
191.1135 | 451.8743 | 121.1801 | 113.2014 | 49.5982
192.1135 | 451.9664 | 121.7692 | 113.7474 | 49.8673
193.1135 | 451.9876 | 122.3683 | 114.3145 | 50.1258
194.1135 | 451.9862 | 122.9371 | 114.8888 | 50.3939
195.1135 | 451.9677 | 123.4904 | 115.4803 | 50.6612
196.1135 | 451.9256 | 124.1011 | 116.0054 | 50.9223
197.1135 | 451.788 | 124.7113 | 116.5427 | 51.1969
198.1135 | 451.7914 | 125.2982 | 117.0756 | 51.4577
199.1135 | 451.6787 | 125.9196 | 117.6697 | 51.7325
200.1135 | 451.6111 | 126.5168 | 118.1799 | 52.0016
201.1135 | 451.459 | 127.0823 | 118.7814 | 52.2762
202.1135 | 451.3932 | 127.6659 | 119.3364 | 52.552
203.1135 | 451.386 | 128.2436 | 119.8881 | 52.8245
204.1135 | 451.3345 | 128.7506 | 120.3873 | 53.1057
205.1135 | 451.2624 | 129.2711 | 120.9481 | 53.3787
206.1135 | 451.2376 | 129.9376 | 121.5799 | 53.6659
207.1135 | 451.2171 | 130.5481 | 122.1477 | 53.9458
208.1135 | 451.2434 | 131.1315 | 122.6311 | 54.2333
209.1135 | 451.2303 | 131.6829 | 123.2138 | 54.5141
210.1135 | 451.2091 | 132.2946 | 123.7088 | 54.8094
211.1135 | 451.1204 | 132.9318 | 124.2695 | 55.0952
212.1135 | 451.1806 | 133.5499 | 124.8495 | 55.3865
213.1135 | 451.1514 | 134.1166 | 125.414 | 55.6782
214.1135 | 451.0643 | 134.6546 | 125.9707 | 55.9793
215.1135 | 450.9672 | 135.2147 | 126.497 | 56.2703
216.1135 | 450.8477 | 135.7808 | 127.0935 | 56.5726
217.1135 | 450.8649 | 136.4134 | 127.6481 | 56.8749
218.1135 | 450.9307 | 137.0194 | 128.1955 | 57.1787
219.1135 | 451.0451 | 137.5829 | 128.7026 | 57.4765
220.1135 | 451.0765 | 138.1756 | 129.1891 | 57.7892
221.1135 | 451.0752 | 138.7207 | 129.7021 | 58.0991
222.1135 | 451.1564 | 139.2894 | 130.261 | 58.415
223.1135 | 451.0996 | 139.8914 | 130.7837 | 58.7278
224.1135 | 451.128 | 140.4939 | 131.3319 | 59.0548
225.1135 | 451.1857 | 141.0319 | 131.8772 | 59.3806
226.1135 | 451.1066 | 141.6284 | 132.4167 | 59.7006
227.1135 | 451.1447 | 142.2208 | 132.9412 | 60.0289
228.1135 | 451.2274 | 142.7926 | 133.4749 | 60.36
229.1135 | 451.3385 | 143.3648 | 133.9927 | 60.6877
230.1135 | 451.4122 | 144.02 | 134.487 | 61.0213
231.1135 | 451.4443 | 144.6032 | 135.0193 | 61.3605
232.1135 | 451.4608 | 145.2013 | 135.572 | 61.6933
233.1135 | 451.4383 | 145.7242 | 136.1171 | 62.0333
234.1135 | 451.4755 | 146.3372 | 136.6353 | 62.3774
235.1135 | 451.4585 | 146.9059 | 137.1698 | 62.7231
236.1135 | 451.4651 | 147.4442 | 137.6773 | 63.0722
237.1135 | 451.4803 | 147.9982 | 138.2274 | 63.4171
238.1135 | 451.4957 | 148.5512 | 138.767 | 63.7723
239.1135 | 451.5553 | 149.1086 | 139.3144 | 64.1217
240.1135 | 451.579 | 149.7023 | 139.8395 | 64.4784
241.1135 | 451.5531 | 150.2444 | 140.3193 | 64.8408
242.1135 | 451.5412 | 150.8536 | 140.8247 | 65.2036
243.1135 | 451.4615 | 151.468 | 141.3572 | 65.5718
244.1135 | 451.4291 | 152.0305 | 141.8896 | 65.9327
245.1135 | 451.3664 | 152.6003 | 142.431 | 66.3131
246.1135 | 451.3921 | 153.1714 | 142.9536 | 66.6832
247.1292 | 451.4084 | 153.7201 | 143.4725 | 67.0471
248.1448 | 451.3457 | 154.3069 | 143.9935 | 67.4389
249.1292 | 451.4316 | 154.8545 | 144.4802 | 67.8179
250.1292 | 451.3834 | 155.4476 | 144.9857 | 68.1882
251.1292 | 451.3753 | 155.9728 | 145.4515 | 68.5736
252.1135 | 451.4145 | 156.5253 | 145.9296 | 68.9696
253.1135 | 451.3778 | 157.0497 | 146.5349 | 69.3508
254.1135 | 451.4444 | 157.6357 | 147.079 | 69.7315
255.1135 | 451.5035 | 158.228 | 147.5847 | 70.1168
256.1135 | 451.6006 | 158.8755 | 148.0848 | 70.5102
257.1135 | 451.5266 | 159.388 | 148.5877 | 70.8975
258.1135 | 451.5717 | 159.996 | 149.0439 | 71.293
259.1135 | 451.6658 | 160.5347 | 149.6073 | 71.6815
260.1135 | 451.749 | 161.0469 | 150.1452 | 72.0815
261.1135 | 451.7661 | 161.5668 | 150.6936 | 72.4741
262.1135 | 451.8219 | 162.0987 | 151.1721 | 72.8796
263.1135 | 451.8797 | 162.6304 | 151.6535 | 73.2807
264.1135 | 451.9929 | 163.1979 | 152.1113 | 73.6834
265.1135 | 451.9572 | 163.7551 | 152.6265 | 74.096
266.1135 | 451.9532 | 164.2647 | 153.1168 | 74.4999
267.1135 | 452.001 | 164.8208 | 153.5848 | 74.9049
268.1135 | 452.0523 | 165.2637 | 154.105 | 75.3255
269.1135 | 452.0318 | 165.7955 | 154.5833 | 75.7438
270.1135 | 451.977 | 166.3926 | 155.0719 | 76.1639
271.1135 | 452.0562 | 166.9793 | 155.5926 | 76.5806
272.1135 | 452.1201 | 167.4541 | 156.1106 | 76.9988
273.1135 | 451.9965 | 167.9547 | 156.6157 | 77.4113
274.1135 | 451.9694 | 168.5446 | 157.0621 | 77.8219
275.1135 | 451.9655 | 169.1327 | 157.527 | 78.2498
276.1135 | 451.9873 | 169.6731 | 158.0506 | 78.677
277.1135 | 451.9849 | 170.1708 | 158.5729 | 79.1045
278.1135 | 452.0733 | 170.6646 | 159.0604 | 79.5302
279.1135 | 451.9767 | 171.1909 | 159.5265 | 79.9603
280.1135 | 451.8312 | 171.7242 | 160.0089 | 80.4043
281.1135 | 451.7141 | 172.2464 | 160.5271 | 80.8416
282.1135 | 451.6073 | 172.7416 | 161.0713 | 81.2841
283.1135 | 451.6279 | 173.2211 | 161.5557 | 81.7209
284.1135 | 451.6827 | 173.7673 | 161.9985 | 82.1624
285.1135 | 451.7287 | 174.2682 | 162.4388 | 82.6191
286.1135 | 451.7089 | 174.807 | 162.9811 | 83.0661
287.1135 | 451.7466 | 175.3187 | 163.4857 | 83.5262
288.1135 | 451.7922 | 175.8471 | 163.9427 | 83.9782
289.1135 | 451.8842 | 176.3828 | 164.5001 | 84.4366
290.1135 | 451.8843 | 176.8605 | 164.9504 | 84.8965
291.1135 | 451.9315 | 177.3493 | 165.3857 | 85.3634
292.1135 | 452.0243 | 177.9072 | 165.8541 | 85.8222
293.1135 | 452.0467 | 178.4022 | 166.3415 | 86.2878
294.1135 | 452.0802 | 178.8811 | 166.7935 | 86.7578
295.1135 | 452.1361 | 179.3849 | 167.2751 | 87.2228
296.1135 | 452.1257 | 179.8956 | 167.7596 | 87.7052
297.1135 | 452.0671 | 180.3875 | 168.1714 | 88.1785
298.1135 | 451.8248 | 180.918 | 168.6404 | 88.6704
299.1135 | 451.7376 | 181.4081 | 169.1061 | 89.1639
300.1135 | 451.7168 | 181.9281 | 169.5763 | 89.6511
301.1135 | 451.6829 | 182.4229 | 169.9853 | 90.1437
302.1135 | 451.5786 | 182.9035 | 170.4143 | 90.6396
303.1135 | 451.5451 | 183.4247 | 170.8722 | 91.1336
304.1135 | 451.4485 | 183.8667 | 171.3732 | 91.6246
305.1135 | 451.4683 | 184.3802 | 171.8499 | 92.118
306.1135 | 451.3986 | 184.897 | 172.3158 | 92.5968
307.1135 | 451.2465 | 185.3749 | 172.7886 | 93.0827
308.1135 | 451.2162 | 185.8696 | 173.2733 | 93.5615
309.1135 | 451.1457 | 186.3134 | 173.7105 | 94.0431
310.1135 | 450.9555 | 186.7832 | 174.1898 | 94.5188
311.1135 | 450.791 | 187.2943 | 174.6187 | 94.9838
312.1135 | 450.8566 | 187.7771 | 175.0688 | 95.461
313.1135 | 450.918 | 188.2385 | 175.5526 | 95.9259
314.1135 | 450.9081 | 188.7178 | 175.976 | 96.398
315.1135 | 450.9685 | 189.2288 | 176.4401 | 96.8808
316.1135 | 451.0129 | 189.7186 | 176.8915 | 97.352
317.1135 | 450.9309 | 190.1903 | 177.3309 | 97.837
318.1135 | 450.8936 | 190.7018 | 177.7408 | 98.3145
319.1135 | 450.9063 | 191.184 | 178.191 | 98.7859
320.1135 | 450.9571 | 191.6156 | 178.6476 | 99.26
321.1135 | 450.9616 | 192.0787 | 179.0992 | 99.7281
322.1135 | 450.8916 | 192.49 | 179.5278 | 100.1978
323.1135 | 450.9059 | 192.933 | 180.0102 | 100.6713
324.1135 | 450.8809 | 193.4014 | 180.4448 | 101.128
325.1135 | 450.8694 | 193.9043 | 180.8737 | 101.6063
326.1135 | 450.8961 | 194.37 | 181.2868 | 102.0775
327.1135 | 450.8609 | 194.8517 | 181.7087 | 102.5523
328.1135 | 450.8871 | 195.2896 | 182.169 | 103.0521
329.1135 | 450.8614 | 195.7409 | 182.5818 | 103.5354
330.1135 | 450.7835 | 196.2162 | 183.0304 | 104.0284
331.1135 | 450.7586 | 196.6815 | 183.4861 | 104.5368
332.1135 | 450.741 | 197.176 | 183.9208 | 105.0268
333.1135 | 450.5073 | 197.6422 | 184.3313 | 105.5316
334.1135 | 450.441 | 198.1071 | 184.7581 | 106.0328
335.1135 | 450.4835 | 198.5655 | 185.2105 | 106.5506
336.1135 | 450.3879 | 199.0323 | 185.6689 | 107.0689
337.1135 | 450.3507 | 199.4891 | 186.1023 | 107.5931
338.1135 | 450.4492 | 199.9287 | 186.5279 | 108.1109
339.1135 | 450.5069 | 200.3575 | 186.967 | 108.6409
340.1135 | 450.551 | 200.8164 | 187.3696 | 109.1699
341.1135 | 450.5779 | 201.2862 | 187.8304 | 109.7004
342.1135 | 450.5425 | 201.7438 | 188.2686 | 110.2479
343.1135 | 450.6202 | 202.2277 | 188.7184 | 110.7909
344.1135 | 450.7708 | 202.6859 | 189.1145 | 111.3319
345.1135 | 450.8197 | 203.1012 | 189.5472 | 111.8829
346.1135 | 450.8972 | 203.5518 | 190.0353 | 112.4342
347.1135 | 451.011 | 203.9629 | 190.4187 | 112.9917
348.1135 | 451.0109 | 204.3932 | 190.8596 | 113.5542
349.1135 | 451.1397 | 204.8368 | 191.2719 | 114.1212
350.1135 | 451.1451 | 205.2909 | 191.6436 | 114.6524
351.1135 | 451.1554 | 205.7841 | 191.9743 | 115.2058
352.1135 | 451.0842 | 206.2107 | 192.4251 | 115.7766
353.1135 | 451.0805 | 206.6178 | 192.8677 | 116.3622
354.1135 | 451.0453 | 207.0703 | 193.3028 | 116.9454
355.1135 | 451.0348 | 207.54 | 193.7165 | 117.5389
356.1135 | 450.9897 | 207.9834 | 194.1261 | 118.1478
357.1135 | 450.9725 | 208.4457 | 194.56 | 118.7492
358.1135 | 450.9736 | 208.909 | 194.9565 | 119.3719
359.1135 | 450.9505 | 209.3735 | 195.3706 | 119.9879
360.1135 | 450.8161 | 209.7768 | 195.7921 | 120.6125
361.1135 | 450.7055 | 210.2139 | 196.1908 | 121.2456
362.1135 | 450.5907 | 210.6365 | 196.5956 | 121.8843
363.1135 | 450.6235 | 211.0739 | 197.0027 | 122.5204
364.1135 | 450.6088 | 211.5075 | 197.4248 | 123.1786
365.1135 | 450.4977 | 211.9804 | 197.8146 | 123.8279
366.1135 | 450.4394 | 212.3743 | 198.2114 | 124.4936
367.1135 | 450.4453 | 212.7802 | 198.6077 | 125.1526
368.1135 | 450.4738 | 213.1699 | 199.0537 | 125.8438
369.1135 | 450.5626 | 213.6013 | 199.4463 | 126.5056
370.1135 | 450.568 | 214.0598 | 199.8416 | 127.1842
371.1135 | 450.5726 | 214.4971 | 200.2071 | 127.8721
372.1135 | 450.5705 | 214.9118 | 200.6045 | 128.5631
373.1135 | 450.5624 | 215.3542 | 201.0045 | 129.261
374.1135 | 450.5006 | 215.7843 | 201.4215 | 129.9709
375.1135 | 450.453 | 216.2465 | 201.8109 | 130.6842
376.1135 | 450.4583 | 216.6592 | 202.2072 | 131.397
377.1135 | 450.4951 | 217.0366 | 202.6116 | 132.1189
378.1135 | 450.4541 | 217.4266 | 203.0126 | 132.8564
379.1135 | 450.4371 | 217.8304 | 203.44 | 133.5927
380.1135 | 450.2971 | 218.2673 | 203.8363 | 134.3347
381.1135 | 450.3179 | 218.6868 | 204.245 | 135.0988
382.1135 | 450.2475 | 219.0834 | 204.5947 | 135.8553
383.1135 | 450.2767 | 219.4714 | 204.9844 | 136.6199
384.1135 | 450.4115 | 219.8707 | 205.3643 | 137.3945
385.1135 | 450.4509 | 220.281 | 205.8086 | 138.1689
386.1135 | 450.5125 | 220.6899 | 206.1691 | 138.9545
387.1135 | 450.5404 | 221.098 | 206.5691 | 139.7444
388.1135 | 450.5793 | 221.5096 | 206.9687 | 140.5444
389.1135 | 450.5908 | 221.906 | 207.3718 | 141.3619
390.1135 | 450.5822 | 222.3237 | 207.7594 | 142.1773
391.1135 | 450.5921 | 222.7308 | 208.1398 | 143.0069
392.1135 | 450.6029 | 223.1888 | 208.535 | 143.8502
393.1135 | 450.6617 | 223.5952 | 208.9172 | 144.7184
394.1135 | 450.7734 | 223.9628 | 209.3148 | 145.5717
395.1135 | 450.7999 | 224.3709 | 209.7101 | 146.4466
396.1135 | 450.8071 | 224.7722 | 210.0354 | 147.3309
397.1135 | 450.8474 | 225.1989 | 210.3869 | 148.2276
398.1135 | 450.7793 | 225.5875 | 210.801 | 149.1356
399.1135 | 450.8095 | 225.9982 | 211.2082 | 150.051
400.1135 | 450.759 | 226.3893 | 211.5864 | 150.9737
401.1135 | 450.7473 | 226.7705 | 211.9199 | 151.9125
402.1135 | 450.7914 | 227.1447 | 212.3325 | 152.8624
403.1135 | 450.8394 | 227.5736 | 212.7511 | 153.8199
404.1135 | 450.925 | 227.9675 | 213.1426 | 154.7932
405.1135 | 451.0239 | 228.3439 | 213.5403 | 155.775
406.1135 | 451.0411 | 228.729 | 213.9045 | 156.7681
407.1135 | 450.9497 | 229.1573 | 214.2866 | 157.7701
408.1135 | 450.9716 | 229.6262 | 214.6539 | 158.7799
409.1135 | 451.0615 | 229.9977 | 215.0254 | 159.7965
410.1135 | 451.1438 | 230.3906 | 215.3835 | 160.8351
411.1135 | 451.1258 | 230.7619 | 215.6381 | 161.8987
412.1135 | 451.1671 | 231.1435 | 216.0329 | 162.9724
413.1135 | 451.1974 | 231.5421 | 216.4576 | 164.0832
414.1135 | 451.1477 | 231.9236 | 216.8397 | 165.212
415.1135 | 451.1826 | 232.3124 | 217.1419 | 166.3478
416.1135 | 451.2123 | 232.6828 | 217.4989 | 167.4853
417.1135 | 451.2048 | 233.0823 | 217.8837 | 168.6158
418.1135 | 451.1579 | 233.4362 | 218.2786 | 169.74
419.1135 | 451.0873 | 233.8323 | 218.6422 | 170.8483
420.1135 | 451.189 | 234.2158 | 219.0307 | 171.9503
421.1135 | 451.2876 | 234.6056 | 219.3972 | 173.0462
422.1135 | 451.354 | 235.0098 | 219.7906 | 174.1418
423.1135 | 451.3005 | 235.4173 | 220.1729 | 175.1916
424.1135 | 451.1838 | 235.7901 | 220.5418 | 176.2153
425.1135 | 451.2383 | 236.1531 | 220.9057 | 177.21
426.1135 | 451.1948 | 236.5284 | 221.2636 | 178.1697
427.1135 | 451.2639 | 236.8949 | 221.6439 | 179.0942
428.1135 | 451.3822 | 237.2805 | 222.0154 | 179.9783
429.1135 | 451.5383 | 237.6691 | 222.4041 | 180.8548
430.1135 | 451.5823 | 238.0619 | 222.7714 | 181.7036
431.1135 | 451.6128 | 238.443 | 223.1282 | 182.5003
432.1135 | 451.6436 | 238.8348 | 223.4431 | 183.2569
433.1135 | 451.6257 | 239.1949 | 223.7124 | 184.0058
434.1135 | 451.6276 | 239.5524 | 224.1007 | 184.6989
435.1135 | 451.5312 | 239.955 | 224.4709 | 185.3774
436.1135 | 451.5173 | 240.3156 | 224.8634 | 186.0277
437.1135 | 451.5473 | 240.6804 | 225.1915 | 186.6257
438.1135 | 451.5249 | 241.0593 | 225.5377 | 187.198
439.1135 | 451.5565 | 241.4222 | 225.9047 | 187.7514
440.1135 | 451.5297 | 241.7935 | 226.2751 | 188.2745
441.1135 | 451.5335 | 242.1625 | 226.5209 | 188.75
442.1135 | 451.5856 | 242.5344 | 226.9086 | 189.2127
443.1135 | 451.5645 | 242.8992 | 227.2757 | 189.6511
444.1135 | 451.5721 | 243.2763 | 227.6516 | 190.0667
445.1135 | 451.6183 | 243.6227 | 228.0123 | 190.4738
446.1135 | 451.6199 | 243.9631 | 228.3461 | 190.8762
447.1135 | 451.6865 | 244.3438 | 228.6852 | 191.2328
448.1135 | 451.64 | 244.7204 | 229.0502 | 191.5657
449.1135 | 451.6167 | 245.0597 | 229.3988 | 191.8973
450.1135 | 451.5697 | 245.4132 | 229.7531 | 192.2162
451.1135 | 451.5827 | 245.7697 | 229.9612 | 192.5518
452.1135 | 451.6621 | 246.1271 | 230.3598 | 192.87
453.1135 | 451.7479 | 246.4962 | 230.7355 | 193.1807
454.1135 | 451.781 | 246.8787 | 231.085 | 193.5015
455.1135 | 451.6915 | 247.2276 | 231.3086 | 193.8301
456.1135 | 451.5629 | 247.5712 | 231.7136 | 194.1287
457.1135 | 451.5468 | 247.9232 | 232.0792 | 194.413
458.1135 | 451.4759 | 248.2618 | 232.4246 | 194.7033
459.1135 | 451.4732 | 248.6258 | 232.7617 | 194.9853
460.1135 | 451.412 | 248.9873 | 233.097 | 195.2648
461.1135 | 451.4475 | 249.3477 | 233.4104 | 195.5441
462.1135 | 451.5493 | 249.6837 | 233.7628 | 195.8303
463.1135 | 451.5299 | 250.0076 | 234.101 | 196.1237
464.1135 | 451.424 | 250.3542 | 234.4289 | 196.409
465.1135 | 451.4023 | 250.7158 | 234.7131 | 196.675
466.1135 | 451.3855 | 251.0489 | 235.0607 | 196.9292
467.1135 | 451.2971 | 251.3937 | 235.4088 | 197.173
468.1135 | 451.2514 | 251.7378 | 235.7651 | 197.4394
469.1135 | 451.1423 | 252.0864 | 236.0072 | 197.6867
470.1135 | 451.1188 | 252.4219 | 236.3129 | 197.9462
471.1135 | 451.0873 | 252.7716 | 236.6393 | 198.2166
472.1135 | 451.045 | 253.1102 | 236.9552 | 198.4917
473.1135 | 450.9102 | 253.4724 | 237.2784 | 198.7572
474.1135 | 450.7031 | 253.8267 | 237.5941 | 199.0069
475.1135 | 450.7163 | 254.1506 | 237.9481 | 199.2236
476.1135 | 450.6669 | 254.4693 | 238.2376 | 199.4156
477.1135 | 450.7257 | 254.8004 | 238.5164 | 199.6203
478.1135 | 450.6649 | 255.1283 | 238.8492 | 199.8476
479.1135 | 450.6638 | 255.4678 | 239.2057 | 200.096
480.1135 | 450.6892 | 255.7891 | 239.4802 | 200.3619
481.1135 | 450.6668 | 256.1207 | 239.8079 | 200.5721
482.1135 | 450.7887 | 256.4542 | 240.1483 | 200.7615
483.1135 | 450.8756 | 256.8206 | 240.4413 | 200.9716
484.1135 | 450.8988 | 257.1425 | 240.7549 | 201.2067
485.1135 | 450.8127 | 257.455 | 241.0741 | 201.4157
486.1135 | 450.7904 | 257.7877 | 241.3776 | 201.599
487.1135 | 450.7036 | 258.1165 | 241.7085 | 201.8019
488.1135 | 450.6877 | 258.442 | 241.9716 | 202.0402
489.1135 | 450.6397 | 258.7682 | 242.2552 | 202.3014
490.1135 | 450.6892 | 259.0887 | 242.5623 | 202.544
491.1135 | 450.6827 | 259.4042 | 242.8616 | 202.7853
492.1135 | 450.7388 | 259.7206 | 243.1547 | 203.0165
493.1135 | 450.7926 | 260.0348 | 243.4582 | 203.2508
494.1135 | 450.856 | 260.3622 | 243.6747 | 203.4942
495.1135 | 450.8211 | 260.6628 | 243.7485 | 203.7425
496.1135 | 450.7041 | 260.9923 | 244.1602 | 203.9914
497.1135 | 450.7667 | 261.3058 | 244.4864 | 204.2462
498.1135 | 450.7512 | 261.6409 | 244.8439 | 204.4789
499.1135 | 450.8283 | 261.9691 | 245.208 | 204.6802
500.1135 | 450.8859 | 262.2838 | 245.5324 | 204.8528
501.1135 | 451.0129 | 262.6153 | 245.8384 | 205.0541
502.1135 | 451.1047 | 262.9324 | 246.1204 | 205.245
503.1135 | 451.1866 | 263.2487 | 246.3557 | 205.4466
504.1135 | 451.2422 | 263.5672 | 246.6638 | 205.5852
505.1135 | 451.1962 | 263.9061 | 246.9991 | 205.7563
506.1135 | 451.1674 | 264.2063 | 247.2926 | 205.9732
507.1135 | 451.1148 | 264.5293 | 247.5817 | 206.2229
508.1135 | 451.1195 | 264.8316 | 247.8596 | 206.4022
509.1135 | 451.2159 | 265.1403 | 248.1568 | 206.5921
510.1135 | 451.1169 | 265.4472 | 248.4472 | 206.8209
511.1135 | 451.1067 | 265.7567 | 248.7449 | 207.04
512.1135 | 451.0968 | 266.0462 | 249.0131 | 207.2143
513.1135 | 450.9771 | 266.351 | 249.2765 | 207.3306
514.1135 | 450.9134 | 266.6734 | 249.571 | 207.4574
515.1135 | 450.7757 | 266.9894 | 249.8706 | 207.5957
516.1135 | 450.7924 | 267.2811 | 250.1354 | 207.7731
517.1135 | 450.7961 | 267.6 | 250.4311 | 207.9471
518.1135 | 450.8547 | 267.8895 | 250.7106 | 208.1201
519.1135 | 450.8407 | 268.1794 | 251.0018 | 208.3174
520.1135 | 450.8393 | 268.5078 | 251.2702 | 208.5319
521.1135 | 450.7432 | 268.7891 | 251.5318 | 208.7073
522.1135 | 450.7369 | 269.0889 | 251.7452 | 208.8989
523.1135 | 450.7187 | 269.3688 | 252.013 | 209.0703
524.1135 | 450.7409 | 269.6876 | 252.3335 | 209.2414
525.1135 | 450.5914 | 269.979 | 252.6411 | 209.448
526.1135 | 450.5579 | 270.2912 | 252.9196 | 209.6445
527.1135 | 450.5234 | 270.5911 | 253.2031 | 209.8497
528.1135 | 450.4949 | 270.8799 | 253.4891 | 210.0175
529.1135 | 450.4974 | 271.1869 | 253.8058 | 210.1677
530.1135 | 450.4584 | 271.4955 | 254.0911 | 210.3498
531.1135 | 450.4748 | 271.7659 | 254.3077 | 210.5319
532.1135 | 450.3436 | 272.0483 | 254.5482 | 210.7133
533.1135 | 450.3083 | 272.3303 | 254.8497 | 210.8764
534.1135 | 450.2781 | 272.6362 | 255.1036 | 211.0441
535.1135 | 450.3128 | 272.929 | 255.3661 | 211.2151
536.1135 | 450.2953 | 273.2153 | 255.5867 | 211.3989
537.1135 | 450.232 | 273.4999 | 255.8795 | 211.582
538.1135 | 450.2478 | 273.7798 | 256.1512 | 211.774
539.1135 | 450.2449 | 274.0915 | 256.4143 | 211.9421
540.1135 | 450.2464 | 274.345 | 256.6948 | 212.107
541.1135 | 450.2647 | 274.6326 | 256.9962 | 212.2884
542.1135 | 450.2526 | 274.9271 | 257.2864 | 212.5053
543.1135 | 450.2525 | 275.2159 | 257.5666 | 212.6988
544.1135 | 450.334 | 275.5003 | 257.8396 | 212.8685
545.1135 | 450.385 | 275.779 | 258.0117 | 213.044
546.1135 | 450.389 | 276.0602 | 258.2817 | 213.2326
547.1135 | 450.4911 | 276.3401 | 258.584 | 213.4479
548.1135 | 450.4736 | 276.6332 | 258.8312 | 213.6702
549.1135 | 450.4444 | 276.9274 | 259.0627 | 213.9076
550.1135 | 450.4722 | 277.1985 | 259.3096 | 214.117
551.1135 | 450.49 | 277.4811 | 259.5813 | 214.336
552.1135 | 450.4476 | 277.7418 | 259.8356 | 214.518
553.1135 | 450.4106 | 278.0197 | 260.0936 | 214.6598
554.1135 | 450.3877 | 278.302 | 260.3131 | 214.8321
555.1135 | 450.4844 | 278.5812 | 260.5904 | 215.0086
556.1135 | 450.5359 | 278.8636 | 260.8495 | 215.169
557.1135 | 450.5397 | 279.1315 | 261.1154 | 215.2947
558.1135 | 450.539 | 279.4253 | 261.4024 | 215.4473
559.1135 | 450.6133 | 279.6957 | 261.6473 | 215.5805
560.1135 | 450.6889 | 279.9785 | 261.9212 | 215.7413
561.1135 | 450.7142 | 280.2558 | 262.1694 | 215.9174
562.1135 | 450.7693 | 280.5168 | 262.3969 | 216.0662
563.1135 | 450.853 | 280.7847 | 262.6285 | 216.2253
564.1135 | 450.9344 | 281.0534 | 262.9165 | 216.4171
565.1135 | 450.9472 | 281.3359 | 263.1675 | 216.6177
566.1135 | 450.8911 | 281.5989 | 263.4176 | 216.8371
567.1135 | 450.8856 | 281.8379 | 263.6844 | 217.0361
568.1135 | 450.8268 | 282.1233 | 263.9228 | 217.253
569.1135 | 450.748 | 282.3774 | 264.1518 | 217.4785
570.1135 | 450.6928 | 282.6478 | 264.434 | 217.723
571.1135 | 450.6422 | 282.9254 | 264.6388 | 217.9471
572.1135 | 450.6781 | 283.2014 | 264.898 | 218.1546
573.1135 | 450.7101 | 283.4688 | 265.1369 | 218.3572
574.1135 | 450.6035 | 283.7397 | 265.3751 | 218.5621
575.1135 | 450.4113 | 284.0195 | 265.6416 | 218.7629
576.1135 | 450.3561 | 284.2816 | 265.7519 | 218.9601
577.1135 | 450.3896 | 284.5335 | 265.9791 | 219.162
578.1135 | 450.3594 | 284.7871 | 266.2407 | 219.3832
579.1135 | 450.3067 | 285.0644 | 266.4485 | 219.5985
580.1135 | 450.2752 | 285.2968 | 266.7234 | 219.8446
581.1135 | 450.2198 | 285.5863 | 266.9508 | 220.0956
582.1135 | 450.2089 | 285.8297 | 267.2102 | 220.3109
583.1135 | 450.1679 | 286.1177 | 267.503 | 220.5326
584.1135 | 450.1015 | 286.3895 | 267.7291 | 220.7538
585.1135 | 450.1228 | 286.6235 | 267.9837 | 220.9713
586.1135 | 450.103 | 286.8872 | 268.1481 | 221.1759
587.1135 | 449.9971 | 287.1253 | 268.3982 | 221.3606
588.1135 | 449.9609 | 287.4007 | 268.6793 | 221.5629
589.1135 | 449.8724 | 287.6502 | 268.9193 | 221.7506
590.1135 | 449.8508 | 287.9056 | 269.122 | 221.9415
591.1135 | 449.8073 | 288.1358 | 269.2962 | 222.1725
592.1135 | 449.7834 | 288.3946 | 269.4782 | 222.3946
593.1135 | 449.7396 | 288.6498 | 269.7242 | 222.5832
594.1135 | 449.762 | 288.916 | 270.0095 | 222.7619
595.1135 | 449.7828 | 289.1777 | 270.2116 | 222.9229
596.1135 | 449.7359 | 289.441 | 270.4777 | 223.0901
597.1135 | 449.8038 | 289.6949 | 270.7279 | 223.2656
598.1135 | 449.8004 | 289.9455 | 270.9876 | 223.4493
599.1135 | 449.7364 | 290.1965 | 271.2206 | 223.6255
600.1135 | 449.7105 | 290.4469 | 271.4092 | 223.7865
601.1135 | 449.7469 | 290.6893 | 271.6497 | 223.9548
602.1135 | 449.7705 | 290.9457 | 271.872 | 224.1402
603.1135 | 449.7597 | 291.1723 | 272.1244 | 224.3453
604.1135 | 449.7384 | 291.4433 | 272.3778 | 224.4984
605.1135 | 449.6839 | 291.6998 | 272.5623 | 224.6591
606.1135 | 449.674 | 291.9452 | 272.7417 | 224.8174
607.1135 | 449.6188 | 292.2131 | 272.9886 | 224.9373
608.1135 | 449.6764 | 292.4428 | 273.2192 | 225.0264
609.1135 | 449.7134 | 292.6914 | 273.3905 | 225.1477
610.1135 | 449.7311 | 292.9405 | 273.6196 | 225.2277
611.1135 | 449.7876 | 293.16 | 273.8606 | 225.3213
612.1135 | 449.7501 | 293.4027 | 274.1006 | 225.3823
613.1135 | 449.6296 | 293.6743 | 274.328 | 225.4679
614.1135 | 449.6287 | 293.9146 | 274.5608 | 225.5613
615.1135 | 449.5933 | 294.1586 | 274.7774 | 225.6483
616.1135 | 449.6367 | 294.4161 | 274.997 | 225.722
617.1135 | 449.6341 | 294.6607 | 275.2164 | 225.7507
618.1135 | 449.6265 | 294.8999 | 275.4063 | 225.8043
619.1135 | 449.6176 | 295.1466 | 275.6286 | 225.886
620.1135 | 449.5556 | 295.3739 | 275.8816 | 225.9664
621.1135 | 449.4983 | 295.5954 | 276.0962 | 226.1106
622.1135 | 449.5038 | 295.8433 | 276.3382 | 226.2563
623.1135 | 449.5048 | 296.0853 | 276.5386 | 226.3581
624.1135 | 449.5342 | 296.3202 | 276.6807 | 226.4539
625.1135 | 449.5053 | 296.528 | 276.8786 | 226.6103
626.1135 | 449.5311 | 296.7523 | 277.0932 | 226.7628
627.1135 | 449.5571 | 296.9861 | 277.3347 | 226.8731
628.1135 | 449.5469 | 297.2271 | 277.5906 | 227.0518
629.1135 | 449.5654 | 297.4715 | 277.8175 | 227.2898
630.1135 | 449.6378 | 297.6975 | 277.9854 | 227.5613
631.1135 | 449.67 | 297.8966 | 278.2376 | 227.8177
632.1135 | 449.712 | 298.1366 | 278.5042 | 228.0488
633.1135 | 449.7529 | 298.3643 | 278.697 | 228.2276
634.1135 | 449.8272 | 298.6025 | 278.9173 | 228.4486
635.1135 | 449.9716 | 298.8604 | 279.1361 | 228.6343
636.1135 | 450.0436 | 299.0713 | 279.3668 | 228.7558
637.1135 | 450.1231 | 299.3034 | 279.61 | 228.8613
638.1135 | 450.2119 | 299.5463 | 279.8344 | 228.9497
639.1135 | 450.2441 | 299.7583 | 280.0259 | 229.0819
640.1135 | 450.2629 | 299.8947 | 280.2528 | 229.2226
641.1135 | 450.3 | 300.1698 | 280.4986 | 229.3584
642.1135 | 450.2973 | 300.4099 | 280.7515 | 229.5093
643.1135 | 450.2349 | 300.6553 | 281.0025 | 229.6834
644.1135 | 450.2452 | 300.9005 | 281.1903 | 229.8615
645.1135 | 450.2374 | 301.1269 | 281.3933 | 230.0452
646.1135 | 450.2193 | 301.3969 | 281.6308 | 230.2303
647.1135 | 450.2246 | 301.6389 | 281.8738 | 230.4521
648.1135 | 450.2069 | 301.8538 | 282.1001 | 230.6688
649.1135 | 450.2656 | 302.0652 | 282.3157 | 230.9073
650.1135 | 450.3474 | 302.3083 | 282.4743 | 231.1152
651.1135 | 450.4118 | 302.5489 | 282.7351 | 231.3965
652.1135 | 450.3905 | 302.7589 | 282.9028 | 231.5919
653.1135 | 450.5108 | 302.936 | 283.141 | 231.7548
654.1135 | 450.4944 | 303.1801 | 283.3863 | 231.9238
655.1135 | 450.5294 | 303.4247 | 283.5655 | 232.0996
656.1135 | 450.5323 | 303.6438 | 283.8078 | 232.2372
657.1135 | 450.5594 | 303.8522 | 284.0337 | 232.4392
658.1135 | 450.5468 | 304.0923 | 284.2776 | 232.6524
659.1135 | 450.6008 | 304.3345 | 284.5132 | 232.8572
660.1135 | 450.5653 | 304.546 | 284.7197 | 233.0305
661.1135 | 450.4633 | 304.7789 | 284.9323 | 233.2046
662.1135 | 450.4287 | 304.9786 | 285.0987 | 233.4072
663.1135 | 450.4926 | 305.2032 | 285.3438 | 233.6606
664.1135 | 450.5075 | 305.4188 | 285.6141 | 233.873
665.1135 | 450.5726 | 305.6564 | 285.8225 | 234.0864
666.1135 | 450.6227 | 305.8741 | 286.0218 | 234.3152
667.1135 | 450.5754 | 306.0602 | 286.2326 | 234.5455
668.1135 | 450.5541 | 306.2901 | 286.4331 | 234.7705
669.1135 | 450.5854 | 306.5057 | 286.6445 | 234.9749
670.1135 | 450.6459 | 306.7433 | 286.836 | 235.1239
671.1135 | 450.7079 | 306.9646 | 287.0779 | 235.2473
672.1135 | 450.7681 | 307.1841 | 287.2614 | 235.3943
673.1135 | 450.7975 | 307.3822 | 287.4678 | 235.5776
674.1135 | 450.8188 | 307.6002 | 287.6434 | 235.7717
675.1135 | 450.8389 | 307.8379 | 287.839 | 235.9774
676.1135 | 450.9161 | 308.0351 | 288.1185 | 236.1888
677.1135 | 450.9557 | 308.2354 | 288.249 | 236.4257
678.1135 | 450.9618 | 308.4543 | 288.4503 | 236.6261
679.1135 | 450.9529 | 308.6879 | 288.6935 | 236.7788
680.1135 | 450.9415 | 308.8944 | 288.8907 | 236.9142
681.1135 | 450.9527 | 309.0784 | 289.0885 | 237.0611
682.1135 | 450.8992 | 309.2974 | 289.3236 | 237.2138
683.1135 | 450.8311 | 309.5293 | 289.5394 | 237.4059
684.1135 | 450.8616 | 309.7138 | 289.6737 | 237.594
685.1135 | 450.8191 | 309.9163 | 289.9106 | 237.8063
686.1135 | 450.897 | 310.1305 | 290.1709 | 238.0734
687.1135 | 450.8668 | 310.3131 | 290.4278 | 238.2937
688.1135 | 450.8078 | 310.5205 | 290.6171 | 238.4323
689.1135 | 450.7896 | 310.7202 | 290.899 | 238.5686
690.1135 | 450.8346 | 310.9501 | 291.152 | 238.702
691.1135 | 450.8236 | 311.1496 | 291.3356 | 238.8274
692.1135 | 450.7203 | 311.3328 | 291.5033 | 238.9703
693.1135 | 450.6411 | 311.5489 | 291.6942 | 239.1452
694.1135 | 450.5461 | 311.7826 | 291.8606 | 239.3293
695.1135 | 450.5441 | 311.9872 | 292.0341 | 239.5035
696.1135 | 450.546 | 312.1841 | 292.2423 | 239.7011
697.1135 | 450.4768 | 312.4001 | 292.446 | 239.9001
698.1135 | 450.3797 | 312.5863 | 292.6755 | 240.0789
699.1135 | 450.326 | 312.7858 | 292.8769 | 240.2326
700.1135 | 450.2723 | 312.9722 | 292.9334 | 240.4166
701.1135 | 450.2025 | 313.1929 | 293.2135 | 240.6401
702.1135 | 450.1247 | 313.393 | 293.4026 | 240.8879
703.1135 | 450.0948 | 313.6092 | 293.6288 | 241.139
704.1135 | 450.072 | 313.803 | 293.7734 | 241.4148
705.1135 | 450.0859 | 313.9607 | 293.9596 | 241.6454
706.1135 | 450.1266 | 314.2005 | 294.1982 | 241.8813
707.1135 | 450.1267 | 314.3914 | 294.4204 | 242.1063
708.1135 | 450.2396 | 314.5677 | 294.6632 | 242.3527
709.1135 | 450.313 | 314.7625 | 294.8662 | 242.6304
710.1135 | 450.3387 | 314.9616 | 295.0814 | 242.8911
711.1135 | 450.2818 | 315.1535 | 295.2387 | 243.1386
712.1135 | 450.2 | 315.3581 | 295.4586 | 243.3553
713.1135 | 450.2726 | 315.5884 | 295.713 | 243.5513
714.1135 | 450.3056 | 315.8172 | 295.8998 | 243.744
715.1135 | 450.3064 | 315.9504 | 296.0733 | 243.9647
716.1135 | 450.2337 | 316.1632 | 296.2894 | 244.1942
717.1135 | 450.1768 | 316.3641 | 296.4895 | 244.4282
718.1135 | 450.1788 | 316.5538 | 296.6449 | 244.7
719.1135 | 450.1799 | 316.7114 | 296.8673 | 244.9346
720.1135 | 450.091 | 316.9228 | 297.1046 | 245.1728
721.1135 | 450.1174 | 317.1352 | 297.2852 | 245.4054
722.1135 | 450.1032 | 317.3614 | 297.4608 | 245.6502
723.1135 | 450.0516 | 317.5578 | 297.4415 | 245.9204
724.1135 | 449.9834 | 317.7652 | 297.723 | 246.1603
725.1135 | 449.9577 | 317.9376 | 297.947 | 246.4122
726.1135 | 449.9245 | 318.0888 | 298.1219 | 246.6734
727.1135 | 449.8886 | 318.2589 | 298.3497 | 246.9028
728.1135 | 449.8933 | 318.4569 | 298.5419 | 247.1163
729.1135 | 449.9872 | 318.6345 | 298.7817 | 247.3136
730.1135 | 450.0819 | 318.8614 | 299.0063 | 247.54
731.1135 | 450.1142 | 319.0367 | 299.2079 | 247.7528
732.1135 | 450.0673 | 319.2296 | 299.3809 | 247.9554
733.1135 | 450.0493 | 319.4151 | 299.5722 | 248.1783
734.1135 | 450.0753 | 319.6112 | 299.7588 | 248.4266
735.1135 | 450.1503 | 319.7852 | 299.8999 | 248.6551
736.1135 | 450.1093 | 319.957 | 300.1124 | 248.8993
737.1135 | 450.1226 | 320.1215 | 300.3247 | 249.1599
738.1135 | 450.1421 | 320.3238 | 300.5071 | 249.4387
739.1135 | 450.0749 | 320.5224 | 300.6824 | 249.7143
740.1135 | 450.0901 | 320.7124 | 300.9026 | 250.0058
741.1135 | 450.1476 | 320.9066 | 301.0993 | 250.3062
742.1135 | 450.1564 | 321.0627 | 301.2733 | 250.5973
743.1135 | 450.1135 | 321.2343 | 301.4683 | 250.8223
744.1135 | 450.148 | 321.4213 | 301.679 | 251.0662
745.1135 | 450.23 | 321.6208 | 301.8605 | 251.3033
746.1135 | 450.2791 | 321.7875 | 301.9938 | 251.5571
747.1135 | 450.3323 | 321.9686 | 302.1962 | 251.8672
748.1135 | 450.4236 | 322.1859 | 302.3905 | 252.1983
749.1135 | 450.444 | 322.3979 | 302.5717 | 252.5232
750.1135 | 450.3857 | 322.5813 | 302.8008 | 252.8383
751.1135 | 450.3227 | 322.7697 | 302.9998 | 253.1259
752.1135 | 450.2993 | 322.9408 | 303.1991 | 253.3995
753.1135 | 450.2824 | 323.0932 | 303.4168 | 253.6528
754.1135 | 450.2767 | 323.2857 | 303.6165 | 253.9273
755.1135 | 450.2581 | 323.4616 | 303.7909 | 254.1804
756.1135 | 450.2337 | 323.6451 | 303.9648 | 254.4546
757.1135 | 450.3006 | 323.8318 | 304.169 | 254.7459
758.1135 | 450.3219 | 324.0056 | 304.3553 | 255.017
759.1135 | 450.3348 | 324.1926 | 304.5429 | 255.2483
760.1135 | 450.2948 | 324.4015 | 304.6588 | 255.5083
761.1135 | 450.1998 | 324.5253 | 304.8788 | 255.7073
762.1135 | 450.0582 | 324.7056 | 304.9657 | 255.8963
763.1135 | 450.1159 | 324.8745 | 305.2073 | 256.0682
764.1135 | 450.1926 | 325.0671 | 305.3641 | 256.2788
765.1135 | 450.3185 | 325.2693 | 305.5595 | 256.4587
766.1135 | 450.4069 | 325.4412 | 305.7705 | 256.6177
767.1135 | 450.4304 | 325.6296 | 305.9796 | 256.7956
768.1135 | 450.3969 | 325.8165 | 306.1059 | 256.9883
769.1135 | 450.4402 | 325.9871 | 306.294 | 257.1633
770.1135 | 450.4347 | 326.1318 | 306.4826 | 257.3111
771.1135 | 450.4535 | 326.3297 | 306.7278 | 257.4736
772.1135 | 450.4726 | 326.4959 | 306.9276 | 257.6626
773.1135 | 450.5314 | 326.6855 | 307.1431 | 257.8442
774.1135 | 450.4727 | 326.8658 | 307.226 | 258.0593
775.1135 | 450.3838 | 327.045 | 307.4122 | 258.3003
776.1135 | 450.3095 | 327.1592 | 307.4756 | 258.51
777.1135 | 450.2271 | 327.3096 | 307.7363 | 258.7229
778.1135 | 450.2329 | 327.5276 | 307.8064 | 259.0015
779.1135 | 450.2772 | 327.6913 | 308.0089 | 259.2612
780.1135 | 450.2543 | 327.8662 | 308.2897 | 259.4638
781.1135 | 450.1923 | 328.0189 | 308.5302 | 259.6525
782.1135 | 450.1453 | 328.1944 | 308.5965 | 259.8829
783.1135 | 450.147 | 328.3656 | 308.85 | 260.1159
784.1135 | 450.112 | 328.5122 | 309.0372 | 260.3816
785.1135 | 450.1255 | 328.6712 | 309.2092 | 260.6144
786.1135 | 450.1068 | 328.8684 | 309.3984 | 260.8477
787.1135 | 450.0882 | 329.0204 | 309.5465 | 261.0741
788.1135 | 450.0199 | 329.205 | 309.709 | 261.2773
789.1135 | 449.9448 | 329.3779 | 309.9214 | 261.5002
790.1135 | 449.9963 | 329.5508 | 310.1316 | 261.7423
791.1135 | 450.0035 | 329.7075 | 310.343 | 261.9969
792.1135 | 450.0155 | 329.865 | 310.5079 | 262.2864
793.1135 | 450.03 | 330.0311 | 310.6334 | 262.5534
794.1135 | 450.0426 | 330.1931 | 310.7723 | 262.816
795.1135 | 450.1657 | 330.3396 | 310.9717 | 263.0874
796.1135 | 450.1295 | 330.5364 | 311.1728 | 263.3665
797.1135 | 450.1049 | 330.6823 | 311.3361 | 263.6061
798.1135 | 450.1018 | 330.8486 | 311.5092 | 263.8538
799.1135 | 450.1578 | 331.0431 | 311.7213 | 264.1363
800.1135 | 450.2706 | 331.2092 | 311.9457 | 264.3672
801.1135 | 450.2566 | 331.3725 | 312.0636 | 264.6094
802.1135 | 450.2904 | 331.4862 | 312.0143 | 264.8679
803.1135 | 450.2521 | 331.6293 | 312.1231 | 265.167
804.1135 | 450.2265 | 331.803 | 312.4274 | 265.4611
805.1135 | 450.2477 | 331.9841 | 312.6689 | 265.726
806.1135 | 450.3192 | 332.1628 | 312.8477 | 265.9666
807.1135 | 450.4035 | 332.3521 | 313.0843 | 266.1926
808.1135 | 450.4509 | 332.5247 | 313.288 | 266.4025
809.1135 | 450.5088 | 332.6541 | 313.4727 | 266.6114
810.1135 | 450.5047 | 332.8471 | 313.6162 | 266.8482
811.1135 | 450.5025 | 332.9866 | 313.7581 | 267.0972
812.1135 | 450.4937 | 333.1609 | 313.9548 | 267.2745
813.1135 | 450.4681 | 333.2989 | 314.1076 | 267.5066
814.1135 | 450.3928 | 333.4411 | 314.3095 | 267.7357
815.1135 | 450.3632 | 333.6105 | 314.5461 | 267.9669
816.1135 | 450.3996 | 333.7831 | 314.7257 | 268.2004
817.1135 | 450.3952 | 333.9658 | 314.8776 | 268.4387
818.1135 | 450.3585 | 334.1267 | 315.1067 | 268.6951
819.1135 | 450.3267 | 334.2657 | 315.2535 | 268.9274
820.1135 | 450.342 | 334.3855 | 315.2932 | 269.2036
821.1135 | 450.3848 | 334.5355 | 315.5302 | 269.4833
822.1135 | 450.3538 | 334.6972 | 315.7506 | 269.7561
823.1135 | 450.414 | 334.8781 | 315.9421 | 269.9803
824.1135 | 450.4629 | 335.0488 | 316.0137 | 270.2225
825.1135 | 450.5034 | 335.184 | 316.3113 | 270.4821
826.1135 | 450.6254 | 335.3757 | 316.5232 | 270.6905
827.1135 | 450.7086 | 335.5221 | 316.7248 | 270.9035
828.1135 | 450.7392 | 335.7106 | 316.9272 | 271.1055
829.1135 | 450.8957 | 335.8872 | 317.1017 | 271.3275
830.1135 | 450.9133 | 336.009 | 317.2639 | 271.5723
831.1135 | 450.8831 | 336.1854 | 317.4357 | 271.8348
832.1135 | 450.8075 | 336.3602 | 317.5841 | 272.0437
833.1135 | 450.8296 | 336.5335 | 317.549 | 272.2787
834.1135 | 450.7369 | 336.6861 | 317.3619 | 272.5229
835.1135 | 450.6785 | 336.8756 | 317.5881 | 272.7872
836.1135 | 450.7405 | 336.9848 | 317.9784 | 273.0645
837.1135 | 450.8224 | 337.1397 | 318.282 | 273.2877
838.1135 | 450.8444 | 337.2641 | 318.381 | 273.5168
839.1135 | 450.8651 | 337.4278 | 318.5825 | 273.7523
840.1135 | 450.8847 | 337.6045 | 318.7843 | 274.0214
841.1135 | 450.8372 | 337.701 | 319.0156 | 274.2264
842.1135 | 450.7027 | 337.882 | 319.1077 | 274.416
843.1135 | 450.6768 | 338.0753 | 319.2276 | 274.6233
844.1135 | 450.5968 | 338.1841 | 319.5124 | 274.7914
845.1135 | 450.5758 | 338.3296 | 319.7655 | 274.9913
846.1135 | 450.5365 | 338.4658 | 319.9195 | 275.186
847.1135 | 450.5941 | 338.6106 | 319.9811 | 275.3882
848.1135 | 450.5936 | 338.7761 | 320.2021 | 275.5979
849.1135 | 450.6326 | 338.9416 | 320.435 | 275.8044
850.1135 | 450.6338 | 339.1148 | 320.6427 | 276.0149
851.1135 | 450.6395 | 339.2918 | 320.7537 | 276.2294
852.1135 | 450.6195 | 339.4565 | 320.952 | 276.4053
853.1135 | 450.6218 | 339.5696 | 321.1275 | 276.5842
854.1135 | 450.6025 | 339.6706 | 321.2693 | 276.789
855.1135 | 450.5665 | 339.8407 | 321.4433 | 276.9835
856.1292 | 450.5898 | 340.0103 | 321.6217 | 277.2044
857.1135 | 450.5632 | 340.1606 | 321.8404 | 277.3805
858.1135 | 450.5618 | 340.2764 | 322.0544 | 277.5547
859.1135 | 450.4908 | 340.4342 | 322.2328 | 277.716
860.1135 | 450.4279 | 340.5738 | 322.4411 | 277.9144
861.1135 | 450.4737 | 340.7389 | 322.6163 | 278.1234
862.1135 | 450.4906 | 340.8792 | 322.7802 | 278.3572
863.1135 | 450.545 | 341.0081 | 322.9427 | 278.6008
864.1135 | 450.5122 | 341.1645 | 323.0777 | 278.8378
865.1135 | 450.4995 | 341.3237 | 323.3389 | 279.0742
866.1135 | 450.5734 | 341.4617 | 323.4731 | 279.2542
867.1135 | 450.5893 | 341.6226 | 323.6605 | 279.5146
868.1135 | 450.5681 | 341.8036 | 323.879 | 279.7167
869.1135 | 450.5622 | 341.9376 | 324.0322 | 279.9204
870.1135 | 450.653 | 342.0793 | 324.2084 | 280.1427
871.1135 | 450.721 | 342.2336 | 324.3914 | 280.3917
872.1135 | 450.7673 | 342.4056 | 324.6219 | 280.6081
873.1135 | 450.8241 | 342.5178 | 324.7848 | 280.8234
874.1135 | 450.7559 | 342.6688 | 324.9299 | 281.0273
875.1135 | 450.7492 | 342.8389 | 325.1402 | 281.2373
876.1135 | 450.7698 | 342.9712 | 325.2859 | 281.4675
877.1135 | 450.772 | 343.1089 | 325.4638 | 281.6722
878.1135 | 450.6637 | 343.2022 | 325.62 | 281.8416
879.1135 | 450.6577 | 343.353 | 325.8206 | 282.0357
880.1135 | 450.6649 | 343.4935 | 326.0368 | 282.2672
881.1135 | 450.5997 | 343.6463 | 326.2358 | 282.4122
882.1135 | 450.5832 | 343.8047 | 326.4445 | 282.583
883.1135 | 450.5954 | 343.9753 | 326.5789 | 282.813
884.1135 | 450.5068 | 344.137 | 326.7282 | 283.0188
885.1135 | 450.4173 | 344.2698 | 326.924 | 283.2546
886.1292 | 450.5239 | 344.417 | 327.1487 | 283.4839
887.1135 | 450.5304 | 344.5568 | 327.2954 | 283.6653
888.1135 | 450.4845 | 344.7249 | 327.4151 | 283.814
889.1135 | 450.4996 | 344.8605 | 327.544 | 283.9537
890.1135 | 450.565 | 345.0025 | 327.6688 | 284.134
891.1135 | 450.5994 | 345.1392 | 327.8 | 284.3435
892.1135 | 450.6163 | 345.238 | 328.0132 | 284.5854
893.1135 | 450.468 | 345.3872 | 328.2662 | 284.8134
894.1135 | 450.4406 | 345.5358 | 328.3137 | 284.9835
895.1135 | 450.3833 | 345.6647 | 328.4871 | 285.1825
896.1135 | 450.3436 | 345.8384 | 328.757 | 285.4039
897.1135 | 450.3502 | 345.9082 | 328.8574 | 285.5878
898.1135 | 450.3103 | 346.0686 | 329.0584 | 285.7559
899.1135 | 450.2172 | 346.2302 | 329.258 | 285.9693
900.1135 | 450.1625 | 346.3835 | 329.3919 | 286.1885
901.1135 | 450.0914 | 346.5074 | 329.53 | 286.3879
902.1135 | 450.0484 | 346.6364 | 329.6544 | 286.6057
903.1135 | 450.0852 | 346.7785 | 329.8784 | 286.8077
904.1135 | 450.0994 | 346.9012 | 330.0202 | 286.9643
905.1135 | 450.1762 | 347.0148 | 330.1408 | 287.1186
906.1135 | 450.1654 | 347.2124 | 330.3033 | 287.2932
907.1135 | 450.1789 | 347.3489 | 330.4719 | 287.5019
908.1135 | 450.1252 | 347.5065 | 330.6313 | 287.7133
909.1135 | 450.1112 | 347.6565 | 330.8126 | 287.8709
910.1135 | 450.091 | 347.7958 | 330.966 | 287.9677
911.1135 | 450.0208 | 347.9129 | 331.191 | 288.0687
912.1135 | 450.0338 | 348.038 | 331.3498 | 288.1429
913.1135 | 450.0234 | 348.1607 | 331.5325 | 288.2542
914.1135 | 449.9986 | 348.2765 | 331.6712 | 288.4017
915.1135 | 450.0098 | 348.422 | 331.8338 | 288.5338
916.1292 | 450.015 | 348.5949 | 331.9927 | 288.6754
917.1135 | 450.008 | 348.7135 | 332.2224 | 288.7119
918.1135 | 449.973 | 348.8726 | 332.3659 | 288.7021
919.1135 | 449.9394 | 349.0354 | 332.5068 | 288.6992
920.1135 | 449.9551 | 349.1353 | 332.6906 | 288.7742
921.1135 | 449.9104 | 349.2773 | 332.8444 | 288.8739
922.1135 | 449.8986 | 349.4113 | 332.9468 | 288.9276
923.1135 | 449.9363 | 349.5534 | 333.1465 | 289.0463
924.1135 | 449.925 | 349.6425 | 333.3135 | 289.1406
925.1135 | 449.882 | 349.8254 | 333.4669 | 289.2376
926.1135 | 449.8755 | 349.9164 | 333.6468 | 289.2369
927.1135 | 450.0314 | 350.1027 | 333.8174 | 289.2998
928.1135 | 450.1705 | 350.2531 | 333.8997 | 289.4112
929.1135 | 450.1794 | 350.3291 | 334.051 | 289.4491
930.1135 | 450.3096 | 350.4647 | 334.1002 | 289.4737
931.1135 | 450.3799 | 350.5857 | 334.3035 | 289.5302
932.1135 | 450.4558 | 350.6939 | 334.4936 | 289.6486
933.1135 | 450.4296 | 350.8632 | 334.4432 | 289.7837
934.1135 | 450.4554 | 351.0103 | 334.5208 | 289.9965
935.1135 | 450.4537 | 351.1262 | 334.6473 | 290.1754
936.1135 | 450.5344 | 351.2799 | 334.9875 | 290.3835
937.1135 | 450.5713 | 351.4185 | 335.1257 | 290.6239
938.1135 | 450.5959 | 351.5575 | 335.3504 | 290.8902
939.1135 | 450.6028 | 351.697 | 335.5128 | 291.0708
940.1135 | 450.5884 | 351.8134 | 335.6501 | 291.1867
941.1135 | 450.6622 | 351.988 | 335.8135 | 291.364
942.1135 | 450.6647 | 352.1244 | 335.9771 | 291.6065
943.1135 | 450.7 | 352.2836 | 336.1559 | 291.8424
944.1135 | 450.6819 | 352.4103 | 336.2779 | 291.9854
945.1135 | 450.6944 | 352.4828 | 336.4565 | 292.1571
946.1135 | 450.5989 | 352.648 | 336.6358 | 292.2261
947.1135 | 450.575 | 352.8159 | 336.7792 | 292.3072
948.1135 | 450.517 | 352.9484 | 336.8966 | 292.3378
949.1135 | 450.3752 | 353.1083 | 337.0713 | 292.2736
950.1135 | 450.342 | 353.269 | 337.2531 | 292.1062
951.1135 | 450.2884 | 353.4391 | 337.4679 | 291.8618
952.1135 | 450.2036 | 353.5418 | 337.5827 | 291.6019
953.1135 | 450.1541 | 353.6517 | 337.6155 | 291.4796
954.1135 | 450.011 | 353.7573 | 337.7627 | 291.4698
955.1135 | 450.0402 | 353.8949 | 337.9764 | 291.5594
956.1135 | 450.0145 | 354.047 | 338.1647 | 291.6648
957.1135 | 450.0138 | 354.1885 | 338.3686 | 291.7218
958.1135 | 450.004 | 354.3375 | 338.4922 | 291.7776
959.1135 | 450.0069 | 354.489 | 338.6021 | 291.843
960.1135 | 449.9621 | 354.6449 | 338.7645 | 291.9448
961.1135 | 449.9565 | 354.7872 | 338.9434 | 292.0171
962.1135 | 449.8969 | 354.9224 | 339.0874 | 292.0984
963.1135 | 449.8908 | 355.0124 | 339.2289 | 292.123
964.1135 | 449.9153 | 355.1182 | 339.4007 | 292.1833
965.1135 | 449.9704 | 355.288 | 339.6509 | 292.2759
966.1135 | 450.0049 | 355.4688 | 339.8016 | 292.3572
967.1135 | 450.0101 | 355.6088 | 339.9057 | 292.4943
968.1135 | 450.0424 | 355.7992 | 340.0477 | 292.591
969.1135 | 450.0643 | 355.9464 | 340.1809 | 292.6512
970.1135 | 450.0381 | 356.0817 | 340.2803 | 292.6341
971.1135 | 449.9681 | 356.1904 | 340.3918 | 292.5689
972.1135 | 449.9114 | 356.3227 | 340.5217 | 292.5438
973.1135 | 449.9821 | 356.4593 | 340.667 | 292.5715
974.1135 | 450.0749 | 356.6185 | 340.8029 | 292.6591
975.1135 | 450.0898 | 356.7779 | 341.0122 | 292.6973
976.1135 | 450.0408 | 356.9302 | 341.1786 | 292.8002
977.1135 | 450.1925 | 357.0837 | 341.3671 | 292.9572
978.1135 | 450.2369 | 357.2096 | 341.5245 | 293.0473
979.1135 | 450.2564 | 357.3496 | 341.6664 | 293.1979
980.1135 | 450.2632 | 357.4767 | 341.7455 | 293.3425
981.1135 | 450.3393 | 357.6375 | 341.8636 | 293.3965
982.1135 | 450.4206 | 357.782 | 342.0527 | 293.4079
983.1135 | 450.5689 | 357.8919 | 342.2048 | 293.4382
984.1135 | 450.6918 | 358.0555 | 342.364 | 293.4934
985.1135 | 450.7012 | 358.1751 | 342.5121 | 293.566
986.1135 | 450.7505 | 358.3287 | 342.6738 | 293.5052
987.1135 | 450.85 | 358.5009 | 342.7712 | 293.4191
988.1135 | 450.8594 | 358.6542 | 342.9235 | 293.2704
989.1135 | 450.9017 | 358.7969 | 343.0976 | 293.1936
990.1135 | 450.908 | 358.9191 | 343.3021 | 293.0482
991.1135 | 450.89 | 359.1011 | 343.4859 | 292.9672
992.1135 | 450.9221 | 359.2474 | 343.6373 | 293.0108
993.1135 | 450.962 | 359.3971 | 343.7614 | 293.0815
994.1135 | 451.0163 | 359.5687 | 343.9028 | 293.1278
995.1135 | 451.1165 | 359.7039 | 344.0316 | 293.2721
996.1135 | 451.223 | 359.8443 | 344.2575 | 293.3889
997.1135 | 451.2827 | 360.02 | 344.3714 | 293.5051
998.1135 | 451.3383 | 360.1649 | 344.5059 | 293.6352
999.1135 | 451.4474 | 360.3344 | 344.6309 | 293.7257
1000.1135 | 451.4547 | 360.4742 | 344.7558 | 293.8456
1001.1135 | 451.4044 | 360.5788 | 344.8164 | 294.0053
1002.1135 | 451.3943 | 360.785 | 344.9698 | 294.1534
1003.1135 | 451.469 | 360.9263 | 345.1495 | 294.432
1004.1135 | 451.4731 | 361.0956 | 345.3103 | 294.6246
1005.1135 | 451.4364 | 361.2876 | 345.4936 | 294.8169
1006.1135 | 451.4132 | 361.4284 | 345.6564 | 295.0185
1007.1135 | 451.3749 | 361.5877 | 345.7204 | 295.2931
1008.1135 | 451.4394 | 361.7851 | 345.8128 | 295.5527
1009.1135 | 451.294 | 361.9136 | 345.9883 | 295.7346
1010.1135 | 451.2149 | 362.0936 | 346.0965 | 295.9511
1011.1135 | 451.1933 | 362.2885 | 346.1671 | 296.1273
1012.1135 | 451.143 | 362.474 | 346.3471 | 296.3293
1013.1135 | 451.1486 | 362.6204 | 346.3604 | 296.6728
1014.1135 | 451.1088 | 362.773 | 346.5935 | 297.0853
1015.1135 | 451.1064 | 362.9721 | 346.8031 | 297.44
1016.1135 | 451.1152 | 363.0926 | 346.9594 | 297.9148
1017.1135 | 451.0292 | 363.2431 | 347.113 | 298.3813
1018.1135 | 450.8348 | 363.3746 | 347.2391 | 298.8298
1019.1135 | 450.7509 | 363.5264 | 347.3186 | 299.2164
1020.1135 | 450.7292 | 363.6672 | 347.4568 | 299.8395
1021.1135 | 450.7012 | 363.8061 | 347.6332 | 300.265
1022.1135 | 450.619 | 363.9981 | 347.7787 | 300.8989
1023.1135 | 450.4936 | 364.1891 | 347.9018 | 301.3202
1024.1135 | 450.5615 | 364.2997 | 347.9763 | 301.8044
1025.1135 | 450.532 | 364.5011 | 347.9554 | 302.3474
1026.1135 | 450.4813 | 364.6883 | 348.2398 | 302.789
1027.1135 | 450.4886 | 364.8434 | 348.4732 | 303.2593
1028.1135 | 450.4547 | 365.001 | 348.6248 | 303.8177
1029.1135 | 450.4267 | 365.1654 | 348.7297 | 304.4104
1030.1135 | 450.3746 | 365.3415 | 348.8953 | 304.864
1031.1135 | 450.241 | 365.5064 | 349.0265 | 305.3113
1032.1135 | 450.1559 | 365.6193 | 349.1353 | 305.5506
1033.1135 | 450.1268 | 365.7802 | 349.2663 | 305.8001
1034.1135 | 450.1381 | 365.9327 | 349.4836 | 306.0885
1035.1135 | 450.0972 | 366.1372 | 349.6659 | 306.4597
1036.1135 | 450.0382 | 366.2798 | 349.7555 | 306.7239
1037.1135 | 449.9761 | 366.4303 | 349.9192 | 307.1606
1038.1135 | 449.9466 | 366.5954 | 350.0488 | 307.4948
1039.1135 | 449.9622 | 366.7599 | 350.1976 | 307.8043
1040.1135 | 449.9888 | 366.9165 | 350.1327 | 308.1436
1041.1135 | 449.9379 | 367.0803 | 350.259 | 308.5507
1042.1135 | 449.9436 | 367.2215 | 350.3263 | 308.9718
1043.1135 | 449.9343 | 367.3672 | 350.3812 | 309.3439
1044.1135 | 449.8983 | 367.4916 | 350.6106 | 309.6532
1045.1135 | 449.8673 | 367.6512 | 350.8231 | 309.9811
1046.1135 | 449.9181 | 367.79 | 350.9832 | 310.2536
1047.1135 | 449.9257 | 367.9727 | 351.1824 | 310.4958
1048.1135 | 450.0075 | 368.1434 | 351.3277 | 310.8197
1049.1135 | 450.0709 | 368.2814 | 351.4071 | 311.2211
1050.1135 | 450.0816 | 368.417 | 351.5185 | 311.4982
1051.1135 | 450.0736 | 368.5801 | 351.6828 | 311.6611
1052.1135 | 450.0539 | 368.7473 | 351.8434 | 311.7806
1053.1135 | 450.0994 | 368.8731 | 351.9793 | 311.9107
1054.1135 | 450.0241 | 369.0027 | 352.0867 | 312.1745
1055.1135 | 450.0195 | 369.1202 | 352.0947 | 312.4333
1056.1135 | 450.095 | 369.2878 | 352.2243 | 312.6386
1057.1135 | 450.0337 | 369.4003 | 352.4702 | 312.9183
1058.1135 | 450.0784 | 369.5501 | 352.6145 | 313.1907
1059.1135 | 450.0758 | 369.7213 | 352.7526 | 313.2574
1060.1135 | 450.083 | 369.8912 | 352.9439 | 313.4629
1061.1135 | 450.0981 | 369.9836 | 353.0641 | 313.5686
1062.1135 | 450.1251 | 370.1495 | 353.189 | 313.6921
1063.1135 | 450.1156 | 370.2975 | 353.3539 | 313.8278
1064.1135 | 450.1561 | 370.375 | 353.5609 | 313.9478
1065.1135 | 450.2294 | 370.568 | 353.7216 | 314.1018
1066.1135 | 450.2633 | 370.7552 | 353.7827 | 314.2662
1067.1135 | 450.2764 | 370.8979 | 353.9437 | 314.5116
1068.1135 | 450.287 | 371.0172 | 354.0413 | 314.6388
1069.1135 | 450.2962 | 371.1798 | 354.1494 | 314.6812
1070.1135 | 450.2815 | 371.3188 | 354.3204 | 314.7164
1071.1135 | 450.2339 | 371.4303 | 354.3927 | 314.7857
1072.1135 | 450.2033 | 371.5944 | 354.4777 | 314.9192
1073.1135 | 450.2524 | 371.7605 | 354.6098 | 315.0544
1074.1135 | 450.2936 | 371.9056 | 354.7624 | 314.9814
1075.1135 | 450.2977 | 372.013 | 354.8989 | 315.2184
1076.1135 | 450.3298 | 372.1379 | 355.0328 | 315.2166
1077.1135 | 450.3428 | 372.2645 | 355.1268 | 315.2753
1078.1135 | 450.3315 | 372.4196 | 355.1792 | 315.3432
1079.1135 | 450.3379 | 372.5409 | 355.2143 | 315.7341
1080.1135 | 450.3582 | 372.6681 | 355.4519 | 315.8059
1081.1135 | 450.305 | 372.8277 | 355.6294 | 315.8697
1082.1135 | 450.2899 | 372.9594 | 355.7356 | 315.9363
1083.1135 | 450.2235 | 373.1299 | 355.8642 | 316.0475
1084.1135 | 450.1633 | 373.2404 | 355.97 | 316.1636
1085.1135 | 450.0259 | 373.4243 | 356.0797 | 316.4819
1086.1135 | 450.0073 | 373.5869 | 356.1781 | 316.8623
1087.1135 | 450.0047 | 373.7143 | 356.368 | 317.2884
1088.1135 | 450.1062 | 373.8554 | 356.5844 | 317.5443
1089.1135 | 450.1657 | 374.0162 | 356.7468 | 317.82
1090.1135 | 450.1881 | 374.1267 | 356.7757 | 318.0897
1091.1135 | 450.2187 | 374.2156 | 356.9006 | 318.3588
1092.1135 | 450.1813 | 374.3218 | 357.0129 | 318.6492
1093.1135 | 450.0986 | 374.4513 | 357.1677 | 318.7257
1094.1135 | 450.126 | 374.6134 | 357.3097 | 319.0346
1095.1135 | 450.1124 | 374.7212 | 357.3528 | 319.2266
1096.1135 | 450.0461 | 374.871 | 357.4876 | 319.367
1097.1135 | 450.106 | 374.9425 | 357.6295 | 319.5526
1098.1135 | 450.12 | 375.0736 | 357.7766 | 319.6357
1099.1135 | 450.0936 | 375.1966 | 357.9063 | 319.6978
1100.1135 | 450.1364 | 375.2938 | 357.9913 | 319.9707
1101.1135 | 450.155 | 375.4266 | 358.0559 | 320.3189
1102.1604 | 450.1821 | 375.5648 | 358.1569 | 320.6096
1103.1135 | 450.228 | 375.6876 | 358.3556 | 320.6294
1104.1135 | 450.2802 | 375.798 | 358.4424 | 320.8641
1105.1135 | 450.3027 | 375.9025 | 358.5762 | 320.7631
1106.1135 | 450.3644 | 376.0524 | 358.6273 | 320.983
1107.1135 | 450.3342 | 376.1678 | 358.7663 | 321.1711
1108.1135 | 450.3186 | 376.2363 | 358.7471 | 321.3808
1109.1135 | 450.269 | 376.3694 | 358.9363 | 321.6389
1110.1135 | 450.2847 | 376.5042 | 359.0719 | 321.9794
1111.1135 | 450.2683 | 376.6199 | 359.21 | 322.4201
1112.1135 | 450.2102 | 376.7919 | 359.3471 | 322.6338
1113.1135 | 450.1522 | 376.9564 | 359.4377 | 322.9333
1114.1135 | 450.1375 | 377.0898 | 359.5594 | 322.6994
1115.1135 | 450.1589 | 377.2005 | 359.6965 | 323.0047
1116.1135 | 450.0269 | 377.2969 | 359.7603 | 323.6099
1117.1135 | 449.9439 | 377.3602 | 359.8964 | 323.8866
1118.1135 | 449.8861 | 377.457 | 360.0267 | 324.087
1119.1135 | 449.8378 | 377.5745 | 360.1418 | 323.977
1120.1135 | 449.8632 | 377.6592 | 360.224 | 323.9634
1121.1135 | 449.8102 | 377.834 | 360.3928 | 323.9617
1122.1135 | 449.8352 | 377.9593 | 360.5498 | 324.4988
1123.1135 | 449.8322 | 378.0345 | 360.6522 | 324.8119
1124.1135 | 449.8804 | 378.1492 | 360.6549 | 325.1706
1125.1135 | 449.8885 | 378.221 | 360.6972 | 325.3302
1126.1292 | 449.9837 | 378.3359 | 360.8797 | 325.5409
1127.1135 | 449.9932 | 378.4858 | 361.0042 | 325.9037
1128.1135 | 449.9632 | 378.644 | 361.156 | 326.295
1129.1135 | 449.9897 | 378.7003 | 361.2365 | 326.6536
1130.1135 | 449.9844 | 378.8495 | 361.378 | 327.1665
1131.1135 | 449.9662 | 378.9359 | 361.4736 | 327.6756
1132.1135 | 449.8787 | 379.0309 | 361.5355 | 328.1984
1133.1135 | 449.9136 | 379.0597 | 361.708 | 328.6803
1134.1135 | 450.0054 | 379.1893 | 361.8762 | 329.2425
1135.1135 | 449.9829 | 379.3581 | 362.0079 | 329.6323
1136.1135 | 449.9634 | 379.5089 | 362.1063 | 330.0996
1137.1135 | 449.9592 | 379.6342 | 362.1372 | 330.68
1138.1135 | 449.9338 | 379.7307 | 362.2676 | 331.3239
1139.1135 | 449.9529 | 379.8287 | 362.3967 | 331.9384
1140.1135 | 449.9355 | 380.0055 | 362.4085 | 332.4767
1141.1135 | 449.9549 | 380.0935 | 362.5269 | 333.0117
1142.1135 | 449.8757 | 380.1682 | 362.6221 | 333.3565
1143.1135 | 449.9273 | 380.2705 | 362.7049 | 333.875
1144.1135 | 449.8924 | 380.3798 | 362.8263 | 334.292
1145.1135 | 449.7526 | 380.4622 | 362.9548 | 334.5094
1146.1135 | 449.6962 | 380.5334 | 363.0023 | 334.4697
1147.1135 | 449.7229 | 380.6187 | 363.1092 | 334.5168
1148.1135 | 449.6755 | 380.7512 | 363.176 | 334.4882
1149.1135 | 449.698 | 380.9008 | 363.2441 | 334.5094
1150.1135 | 449.7366 | 381.0002 | 363.3019 | 334.5371
1151.1135 | 449.7801 | 381.0402 | 363.4002 | 334.6666
1152.1135 | 449.7834 | 381.1365 | 363.5372 | 334.7307
1153.1135 | 449.7468 | 381.2451 | 363.6127 | 334.9882
1154.1135 | 449.6806 | 381.3409 | 363.7253 | 335.2392
1155.1135 | 449.6874 | 381.4926 | 363.9111 | 335.4773
1156.1135 | 449.6813 | 381.6808 | 363.8948 | 335.6715
1157.1135 | 449.6712 | 381.7381 | 363.9604 | 335.8061
1158.1135 | 449.6601 | 381.8472 | 364.1125 | 336.0417
1159.1135 | 449.66 | 381.8973 | 364.2927 | 336.2167
1160.1135 | 449.5939 | 381.934 | 364.3863 | 336.3789
1161.1135 | 449.5304 | 382.0757 | 364.4873 | 336.6603
1162.1135 | 449.5822 | 382.169 | 364.577 | 336.8266
1163.1135 | 449.6826 | 382.2595 | 364.7141 | 337.0073
1164.1135 | 449.6677 | 382.3285 | 364.7203 | 337.4178
1165.1135 | 449.706 | 382.4615 | 364.8814 | 337.7039
1166.1135 | 449.6969 | 382.5741 | 364.9943 | 338.0611
1167.1135 | 449.7167 | 382.6522 | 365.1319 | 338.5766
1168.1135 | 449.6969 | 382.6965 | 365.2047 | 338.9513
1169.1135 | 449.6973 | 382.7823 | 365.2752 | 339.3559
1170.1135 | 449.7355 | 382.8964 | 365.4478 | 339.8771
1171.1135 | 449.7735 | 383.0134 | 365.5522 | 340.0475
1172.1135 | 449.8441 | 383.1085 | 365.6278 | 340.047
1173.1135 | 449.9377 | 383.2302 | 365.7537 | 340.0974
1174.1135 | 450.0012 | 383.344 | 365.8394 | 340.3075
1175.1135 | 450.0659 | 383.4186 | 365.9623 | 340.4204
1176.1135 | 450.1448 | 383.5432 | 366.1094 | 341.0375
1177.1135 | 450.1618 | 383.6146 | 366.1288 | 341.5065
1178.1135 | 450.1467 | 383.6966 | 366.1601 | 341.8306
1179.1135 | 450.2134 | 383.7689 | 366.3069 | 342.194
1180.1135 | 450.2499 | 383.8832 | 366.2703 | 342.4335
1181.1135 | 450.2473 | 383.9959 | 366.3971 | 342.9459
1182.1135 | 450.2888 | 384.0763 | 366.433 | 343.29
1183.1135 | 450.3161 | 384.1824 | 366.5178 | 343.5937
1184.1135 | 450.3441 | 384.2521 | 366.579 | 343.6009
1185.1135 | 450.3418 | 384.3317 | 366.7524 | 343.7386
1186.1135 | 450.3707 | 384.4127 | 366.8284 | 344.0303
1187.1135 | 450.3203 | 384.4844 | 366.883 | 344.3302
1188.1135 | 450.292 | 384.5481 | 367.0332 | 344.7142
1189.1135 | 450.379 | 384.6527 | 367.0915 | 344.8611
1190.1135 | 450.3408 | 384.6929 | 366.9235 | 345.1913
1191.1135 | 450.2237 | 384.8211 | 366.7961 | 345.5258
1192.1135 | 450.1061 | 384.9526 | 367.0972 | 345.7268
1193.1135 | 450.0344 | 385.0626 | 367.3589 | 346.1199
1194.1135 | 450.0297 | 385.1607 | 367.475 | 346.5657
1195.1135 | 450.0824 | 385.2214 | 367.5963 | 346.6616
1196.1135 | 450.1193 | 385.3377 | 367.69 | 346.9895
1197.1135 | 450.0875 | 385.369 | 367.8102 | 347.4742
1198.1135 | 450.0575 | 385.4735 | 367.9335 | 347.8863
1199.1135 | 450.0509 | 385.5828 | 367.9632 | 348.1156
1200.1135 | 450.112 | 385.6322 | 367.973 | 348.3474
1201.1135 | 450.1647 | 385.646 | 368.1458 | 348.8021
1202.1135 | 450.1252 | 385.79 | 368.329 | 349.1844
1203.1135 | 449.9959 | 385.8959 | 368.3655 | 349.7599
1204.1135 | 450.0277 | 385.9842 | 368.4047 | 350.3276
1205.1135 | 450.0288 | 386.0791 | 368.494 | 350.5881
1206.1135 | 450.0404 | 386.1234 | 368.6361 | 350.9563
1207.1135 | 450.1165 | 386.2242 | 368.6817 | 351.1731
1208.1135 | 450.1093 | 386.3161 | 368.7666 | 351.5372
1209.1135 | 450.1064 | 386.4005 | 368.831 | 351.8401
1210.1135 | 450.1052 | 386.5279 | 368.9463 | 352.1225
1211.1135 | 450.117 | 386.6261 | 368.9886 | 352.5903
1212.1135 | 450.1621 | 386.6939 | 369.122 | 352.998
1213.1135 | 450.2162 | 386.7904 | 369.2199 | 353.3862
1214.1135 | 450.2137 | 386.8668 | 369.2429 | 353.7847
1215.1135 | 450.2092 | 386.9593 | 369.2559 | 354.2074
1216.1135 | 450.1606 | 387.0326 | 369.1729 | 354.2602
1217.1292 | 450.1337 | 387.0727 | 369.303 | 354.1482
1218.1135 | 450.1159 | 387.154 | 369.4623 | 354.8856
1219.1135 | 450.0541 | 387.1913 | 369.6672 | 355.828
1220.1135 | 450.0528 | 387.2961 | 369.7422 | 356.6544
1221.1135 | 449.9259 | 387.3505 | 369.8337 | 357.2281
1222.1135 | 449.902 | 387.4313 | 369.7388 | 357.6242
1223.1135 | 449.9338 | 387.5201 | 369.8455 | 357.7912
1224.1135 | 449.9544 | 387.6202 | 370.0083 | 357.9397
1225.1135 | 449.9576 | 387.7222 | 370.0904 | 358.0968
1226.1135 | 449.9987 | 387.7658 | 370.1897 | 358.5271
1227.1135 | 449.9253 | 387.8608 | 370.2365 | 359.008
1228.1135 | 449.8778 | 387.9531 | 370.299 | 359.185
1229.1135 | 449.8496 | 388.0277 | 370.3631 | 359.4277
1230.1135 | 449.8845 | 388.1437 | 370.4576 | 359.737
1231.1135 | 449.9162 | 388.2296 | 370.5817 | 359.7978
1232.1135 | 449.9425 | 388.1938 | 370.6391 | 360.1234
1233.1135 | 450.0185 | 388.2463 | 370.7898 | 360.4432
1234.1135 | 450.1097 | 388.4014 | 370.8128 | 360.8618
1235.1135 | 450.1412 | 388.4977 | 370.8261 | 361.2829
1236.1135 | 450.1414 | 388.5736 | 370.8833 | 361.9709
1237.1135 | 450.2266 | 388.64 | 370.9771 | 362.3744
1238.1135 | 450.2513 | 388.701 | 371.1324 | 362.8142
1239.1135 | 450.339 | 388.8184 | 371.2341 | 362.936
1240.1135 | 450.4027 | 388.8933 | 371.1158 | 363.2625
1241.1135 | 450.4349 | 388.9321 | 371.3417 | 363.3662
1242.1135 | 450.4413 | 389.0355 | 371.3426 | 363.4157
1243.1135 | 450.4128 | 389.0635 | 371.4086 | 363.7683
1244.1135 | 450.4315 | 389.141 | 371.5274 | 364.1677
1245.1135 | 450.4799 | 389.1447 | 371.6264 | 364.8112
1246.1135 | 450.4891 | 389.2262 | 371.7776 | 365.014
1247.1135 | 450.4826 | 389.3356 | 371.8709 | 365.3894
1248.1135 | 450.4484 | 389.4072 | 371.9704 | 365.924
1249.1135 | 450.434 | 389.4628 | 372.1197 | 366.212
1250.1135 | 450.4217 | 389.5266 | 372.2445 | 366.7021
1251.1135 | 450.4664 | 389.5962 | 372.3044 | 367.0969
1252.1135 | 450.4956 | 389.6566 | 372.4515 | 367.5494
1253.1135 | 450.5163 | 389.7571 | 372.5396 | 367.895
1254.1135 | 450.3851 | 389.8056 | 372.5666 | 368.1163
1255.1135 | 450.3001 | 389.8481 | 372.6017 | 368.4707
1256.1135 | 450.3698 | 389.964 | 372.5714 | 368.9649
1257.1135 | 450.3847 | 390.0262 | 372.6285 | 369.2238
1258.1135 | 450.4137 | 390.0784 | 372.7254 | 369.2742
1259.1135 | 450.4272 | 390.1797 | 372.8139 | 369.5063
1260.1135 | 450.3332 | 390.2731 | 372.855 | 369.4377
1261.1135 | 450.2673 | 390.2983 | 372.9376 | 369.9632
1262.1135 | 450.1858 | 390.3462 | 373.0007 | 370.268
1263.1135 | 450.1846 | 390.4312 | 372.9098 | 370.7755
1264.1135 | 450.1813 | 390.4985 | 372.8101 | 371.366
1265.1135 | 450.0698 | 390.5315 | 372.9984 | 371.8351
1266.1135 | 449.9477 | 390.6294 | 373.1886 | 372.3189
1267.1135 | 449.8932 | 390.6427 | 373.28 | 372.7907
1268.1135 | 449.8814 | 390.7278 | 373.3792 | 373.2559
1269.1135 | 449.8831 | 390.8122 | 373.4514 | 373.4057
1270.1135 | 449.873 | 390.8525 | 373.5063 | 373.8203
1271.1135 | 449.9184 | 390.964 | 373.5738 | 374.4736
1272.1135 | 449.9727 | 391.0142 | 373.6938 | 374.8402
1273.1135 | 450.0071 | 391.0565 | 373.8055 | 375.4068
1274.1135 | 449.9751 | 391.1522 | 373.8948 | 375.6715
1275.1135 | 449.9339 | 391.2304 | 373.9172 | 375.7526
1276.1135 | 449.9442 | 391.303 | 373.9675 | 376.2237
1277.1135 | 449.9713 | 391.3724 | 374.1147 | 376.4833
1278.1135 | 449.9014 | 391.4429 | 374.0443 | 377.0879
1279.1135 | 449.8777 | 391.52 | 374.0304 | 377.3457
1280.1135 | 449.82 | 391.5955 | 374.136 | 378.1076
1281.1135 | 449.8896 | 391.6361 | 374.1904 | 378.4857
1282.1135 | 449.9378 | 391.7432 | 374.3443 | 378.9545
1283.1135 | 450.0364 | 391.8419 | 374.4718 | 379.2554
1284.1135 | 450.0815 | 391.8914 | 374.5226 | 379.7088
1285.1135 | 450.0478 | 391.959 | 374.5298 | 380.0016
1286.1135 | 450.0434 | 392.008 | 374.7155 | 380.4951
1287.1135 | 450.0952 | 392.0806 | 374.8637 | 381.1021
1288.1135 | 450.0937 | 392.0976 | 374.9041 | 381.4435
1289.1135 | 450.0711 | 392.1114 | 374.9283 | 381.7531
1290.1135 | 450.0354 | 392.2019 | 374.9717 | 382.416
1291.1135 | 450.0453 | 392.2967 | 374.9866 | 382.6011
1292.1135 | 450.1329 | 392.3261 | 375.0742 | 383.1593
1293.1135 | 450.1475 | 392.3867 | 375.1692 | 383.5634
1294.1135 | 450.2064 | 392.4878 | 375.2649 | 383.8636
1295.1135 | 450.2584 | 392.5596 | 375.3607 | 384.2851
1296.1135 | 450.3048 | 392.606 | 375.3798 | 384.8848
1297.1135 | 450.2892 | 392.6997 | 375.4654 | 385.2573
1298.1135 | 450.3162 | 392.7822 | 375.4564 | 385.6243
1299.1135 | 450.3572 | 392.829 | 375.5584 | 385.8581
1300.1135 | 450.3056 | 392.9116 | 375.4848 | 385.9111
1301.1135 | 450.3509 | 392.9813 | 375.5772 | 386.4221
1302.1135 | 450.3162 | 393.0376 | 375.6937 | 386.5297
1303.1135 | 450.2548 | 393.0885 | 375.8059 | 386.6608
1304.1135 | 450.1648 | 393.0925 | 375.896 | 387.1977
1305.1135 | 450.1686 | 393.164 | 375.9967 | 387.863
1306.1135 | 450.2034 | 393.2205 | 376.0683 | 388.3072
1307.1135 | 450.3018 | 393.253 | 376.1079 | 388.7905
1308.1135 | 450.3602 | 393.3614 | 376.1561 | 389.1082
1309.1135 | 450.3681 | 393.4009 | 376.2292 | 389.3675
1310.1135 | 450.4071 | 393.5194 | 376.344 | 389.7179
1311.1135 | 450.412 | 393.575 | 376.4078 | 389.9363
1312.1135 | 450.3936 | 393.587 | 376.3759 | 390.3992
1313.1135 | 450.4104 | 393.6434 | 376.5531 | 390.5086
1314.1135 | 450.4323 | 393.7232 | 376.6457 | 390.9812
1315.1135 | 450.4762 | 393.8391 | 376.7085 | 391.6753
1316.1135 | 450.4878 | 393.8944 | 376.703 | 391.7078
1317.1135 | 450.5167 | 393.9053 | 376.7641 | 392.2749
1318.1135 | 450.6036 | 393.9916 | 376.9018 | 392.9389
1319.1135 | 450.6348 | 394.0692 | 376.9962 | 393.1073
1320.1135 | 450.6277 | 394.1511 | 377.0577 | 393.5224
1321.1135 | 450.5908 | 394.1895 | 377.1579 | 394.0201
1322.1135 | 450.6002 | 394.2746 | 377.1607 | 394.098
1323.1135 | 450.5982 | 394.3324 | 377.2515 | 394.1399
1324.1135 | 450.5324 | 394.4257 | 377.277 | 394.4994
1325.1135 | 450.562 | 394.4428 | 377.4005 | 394.8629
1326.1135 | 450.5958 | 394.4562 | 377.5133 | 394.9373
1327.1135 | 450.5856 | 394.5191 | 377.5315 | 395.2208
1328.1135 | 450.632 | 394.5014 | 377.5867 | 395.666
1329.1135 | 450.6235 | 394.6177 | 377.6725 | 395.9306
1330.1135 | 450.6305 | 394.6631 | 377.7462 | 396.0835
1331.1135 | 450.6384 | 394.7367 | 377.7419 | 396.2923
1332.1135 | 450.6232 | 394.8154 | 377.7709 | 396.4533
1333.1135 | 450.588 | 394.8814 | 377.7768 | 397.2302
1334.1135 | 450.5936 | 394.914 | 377.7602 | 397.4651
1335.1135 | 450.5491 | 394.9507 | 377.8993 | 397.9284
1336.1135 | 450.5388 | 395.0601 | 377.9968 | 397.9596
1337.1135 | 450.5036 | 395.1603 | 378.0207 | 398.412
1338.1135 | 450.5198 | 395.1766 | 378.1255 | 399.0973
1339.1135 | 450.5554 | 395.2071 | 378.2821 | 399.5632
1340.1135 | 450.4872 | 395.2383 | 378.2984 | 399.7156
1341.1135 | 450.4706 | 395.2757 | 378.4715 | 399.6323
1342.1135 | 450.4126 | 395.3683 | 378.6509 | 400.0042
1343.1135 | 450.2881 | 395.4338 | 378.7085 | 400.3518
1344.1135 | 450.2155 | 395.4942 | 378.6082 | 400.8507
1345.1135 | 450.1359 | 395.4912 | 378.7305 | 401.4081
1346.1135 | 450.0207 | 395.5366 | 378.8192 | 401.976
1347.1135 | 449.9366 | 395.6165 | 378.8529 | 402.1142
1348.1135 | 449.8723 | 395.6942 | 378.8174 | 401.7221
1349.1135 | 449.8723 | 395.7372 | 378.783 | 402.3348
1350.1135 | 449.8595 | 395.7742 | 378.953 | 402.8193
1351.1135 | 449.9077 | 395.8162 | 379.098 | 403.3056
1352.1135 | 449.9391 | 395.8867 | 379.1231 | 403.4437
1353.1135 | 450.012 | 395.9184 | 379.1304 | 403.9612
1354.1135 | 449.9824 | 395.9643 | 379.2509 | 404.2702
1355.1135 | 449.9911 | 396.0303 | 379.3565 | 404.5073
1356.1135 | 450.0323 | 396.1115 | 379.3143 | 404.6485
1357.1135 | 450.138 | 396.1356 | 379.365 | 404.6479
1358.1135 | 450.1633 | 396.2172 | 379.3223 | 404.9012
1359.1135 | 450.1624 | 396.2439 | 379.3466 | 405.0557
1360.1135 | 450.2395 | 396.301 | 379.441 | 405.4422
1361.1135 | 450.3894 | 396.3485 | 379.514 | 405.7926
1362.1135 | 450.5241 | 396.4381 | 379.6265 | 406.1431
1363.1135 | 450.6039 | 396.5143 | 379.6214 | 406.3788
1364.1135 | 450.579 | 396.4968 | 379.7233 | 406.4494
1365.1135 | 450.5605 | 396.5363 | 379.7722 | 406.6236
1366.1135 | 450.5828 | 396.574 | 379.8513 | 406.8374
1367.1135 | 450.5864 | 396.592 | 379.9205 | 406.8988
1368.1135 | 450.6035 | 396.6871 | 380.0683 | 407.3311
1369.1135 | 450.5894 | 396.7937 | 380.1321 | 407.5163
1370.1135 | 450.6024 | 396.8581 | 380.2536 | 408.1622
1371.1135 | 450.5881 | 396.8778 | 380.1788 | 408.522
1372.1135 | 450.4985 | 396.7853 | 380.3023 | 408.6684
1373.1135 | 450.4131 | 396.8615 | 380.3603 | 408.7991
1374.1135 | 450.4163 | 396.9036 | 380.4036 | 408.8619
1375.1135 | 450.3276 | 396.9725 | 380.3864 | 409.018
1376.1135 | 450.2319 | 397.0456 | 380.4871 | 409.7801
1377.1135 | 450.1956 | 397.0984 | 380.4177 | 409.8426
1378.1135 | 450.1352 | 397.1812 | 380.5054 | 410.1833
1379.1135 | 450.0899 | 397.2394 | 380.5384 | 410.3413
1380.1135 | 450.0113 | 397.2533 | 380.6777 | 410.3667
1381.1135 | 449.8786 | 397.2829 | 380.6544 | 410.2647
1382.1135 | 449.8147 | 397.3845 | 380.7097 | 410.6307
1383.1135 | 449.773 | 397.4403 | 380.7351 | 410.5186
1384.1135 | 449.7458 | 397.4399 | 380.7659 | 410.2621
1385.1135 | 449.6574 | 397.5141 | 380.9275 | 410.5859
1386.1135 | 449.6126 | 397.5982 | 381.0496 | 410.3707
1387.1135 | 449.5541 | 397.621 | 381.106 | 410.486
1388.1135 | 449.5306 | 397.6933 | 381.2304 | 410.9168
1389.1135 | 449.5187 | 397.7493 | 381.3443 | 410.8436
1390.1135 | 449.5305 | 397.775 | 381.308 | 410.8447
1391.1135 | 449.4303 | 397.7767 | 381.28 | 410.91
1392.1135 | 449.3828 | 397.8208 | 381.3115 | 410.915
1393.1135 | 449.3203 | 397.9456 | 381.4505 | 410.9948
1394.1135 | 449.3447 | 397.9929 | 381.5242 | 411.4698
1395.1135 | 449.4098 | 397.9844 | 381.6113 | 411.6
1396.1135 | 449.4704 | 398.0151 | 381.6314 | 411.981
1397.1135 | 449.5829 | 398.082 | 381.6861 | 411.7486
1398.1135 | 449.642 | 398.1635 | 381.7455 | 412.2384
1399.1135 | 449.7344 | 398.2853 | 381.7669 | 412.3625
1400.1135 | 449.8363 | 398.338 | 381.8067 | 412.2896
1401.1135 | 449.9493 | 398.3267 | 381.9541 | 412.73
1402.1135 | 450.0088 | 398.4154 | 381.9535 | 413.0778
1403.1135 | 450.0341 | 398.4711 | 381.9919 | 413.6965
1404.1135 | 450.0288 | 398.4647 | 382.0533 | 413.8709
1405.1135 | 450.032 | 398.5287 | 382.0784 | 413.9314
1406.1135 | 450.0839 | 398.5609 | 382.1431 | 413.9567
1407.1135 | 450.0926 | 398.5779 | 382.2013 | 414.0592
1408.1135 | 450.1202 | 398.6084 | 382.2338 | 414.0555
1409.1135 | 450.1804 | 398.6475 | 382.2823 | 413.8226
1410.1135 | 450.0849 | 398.7192 | 382.2409 | 413.5807
1411.1135 | 450.0096 | 398.7474 | 382.273 | 413.4514
1412.1135 | 450.0212 | 398.7873 | 382.2934 | 413.5804
1413.1135 | 450.0963 | 398.8593 | 382.3107 | 414.0885
1414.1135 | 450.1453 | 398.9659 | 382.3435 | 414.0183
1415.1135 | 450.1303 | 398.9872 | 382.2842 | 414.0454
1416.1135 | 450.1027 | 399.0415 | 382.2799 | 413.8691
1417.1135 | 450.0863 | 399.0468 | 382.3779 | 413.6554
1418.1135 | 450.0613 | 399.0916 | 382.2053 | 414.0691
1419.1135 | 450.1256 | 399.0956 | 382.4318 | 414.1993
1420.1135 | 450.1559 | 399.1911 | 382.589 | 414.5778
1421.1135 | 450.2152 | 399.2287 | 382.526 | 414.4615
1422.1135 | 450.3244 | 399.3361 | 382.445 | 414.7826
1423.1135 | 450.4132 | 399.3959 | 382.4737 | 414.4985
1424.1135 | 450.4997 | 399.4139 | 382.5683 | 414.1363
1425.1135 | 450.4867 | 399.4608 | 382.7468 | 414.6146
1426.1135 | 450.5005 | 399.4836 | 382.931 | 414.8603
1427.1135 | 450.4379 | 399.5711 | 382.9133 | 415.3369
1428.1135 | 450.5008 | 399.583 | 383.0209 | 415.0519
1429.1135 | 450.5387 | 399.6522 | 383.0785 | 414.9
1430.1135 | 450.5053 | 399.7261 | 383.1644 | 414.7406
1431.1135 | 450.4217 | 399.7503 | 383.2413 | 414.5522
1432.1135 | 450.3192 | 399.7637 | 383.203 | 414.4525
1433.1135 | 450.2735 | 399.7918 | 383.2776 | 415.0089
1434.1135 | 450.2409 | 399.8599 | 383.3797 | 415.1663
1435.1135 | 450.1515 | 399.9193 | 383.4403 | 415.6521
1436.1135 | 450.1374 | 399.8851 | 383.5982 | 415.4388
1437.1135 | 450.0317 | 399.797 | 383.7077 | 415.9377
1438.1135 | 449.9333 | 399.8569 | 383.6486 | 415.8338
1439.1135 | 449.92 | 399.9855 | 383.7685 | 416.0516
1440.1135 | 449.7825 | 400.039 | 383.6544 | 416.5496
1441.1135 | 449.6899 | 400.1545 | 383.695 | 416.8274
1442.1135 | 449.6948 | 400.1929 | 383.8491 | 415.9321
1443.1135 | 449.7173 | 400.2814 | 383.9326 | 416.2379
1444.1135 | 449.6159 | 400.3079 | 384.0299 | 416.2429
1445.1135 | 449.5553 | 400.3879 | 384.0806 | 416.1421
1446.1135 | 449.5393 | 400.4522 | 384.1456 | 415.8506
1447.1135 | 449.5667 | 400.5184 | 384.1659 | 416.1206
1448.1135 | 449.6507 | 400.4841 | 384.1071 | 416.588
1449.1135 | 449.6626 | 400.4861 | 384.2754 | 416.7728
1450.1135 | 449.6395 | 400.5829 | 384.34 | 416.2291
1451.1135 | 449.5509 | 400.6622 | 384.3955 | 416.3218
1452.1135 | 449.4349 | 400.7257 | 384.439 | 416.1748
1453.1135 | 449.3969 | 400.7922 | 384.5229 | 416.4947
1454.1135 | 449.3775 | 400.8426 | 384.6235 | 415.9022
1455.1135 | 449.4661 | 400.824 | 384.5915 | 415.7731
1456.1135 | 449.5223 | 400.8873 | 384.6156 | 416.0214
1457.1135 | 449.5322 | 400.9244 | 384.6969 | 416.238
1458.1135 | 449.5636 | 400.9667 | 384.8119 | 416.4899
1459.1135 | 449.55 | 400.973 | 384.8218 | 416.4736
1460.1135 | 449.5087 | 401.0374 | 384.8517 | 416.4425
1461.1135 | 449.495 | 401.0361 | 384.883 | 417.0435
1462.1135 | 449.5308 | 401.0783 | 384.9069 | 417.1446
1463.1135 | 449.5415 | 401.1239 | 385.0392 | 417.445
1464.1135 | 449.5008 | 401.2139 | 385.0771 | 417.0793
1465.1135 | 449.4878 | 401.3068 | 385.1093 | 416.9145
1466.1135 | 449.438 | 401.3411 | 385.1927 | 416.3867
1467.1135 | 449.425 | 401.3617 | 385.1807 | 416.052
1468.1135 | 449.3699 | 401.3741 | 385.2042 | 416.2386
1469.1135 | 449.4024 | 401.3856 | 385.1884 | 416.8283
1470.1135 | 449.4246 | 401.4217 | 385.2741 | 417.3368
1471.1135 | 449.4467 | 401.3875 | 385.3644 | 417.0891
1472.1135 | 449.4609 | 401.4244 | 385.4017 | 417.2415
1473.1135 | 449.4696 | 401.478 | 385.4888 | 417.7349
1474.1135 | 449.454 | 401.5178 | 385.5823 | 417.915
1475.1135 | 449.4369 | 401.5375 | 385.6392 | 418.0255
1476.1135 | 449.4957 | 401.6648 | 385.6398 | 418.4562
1477.1135 | 449.5788 | 401.705 | 385.6065 | 418.0262
1478.1135 | 449.6414 | 401.7722 | 385.6401 | 418.3547
1479.1135 | 449.6811 | 401.8485 | 385.5691 | 418.4839
1480.1135 | 449.6562 | 401.7815 | 385.655 | 418.6073
1481.1135 | 449.6248 | 401.8569 | 385.5647 | 419.2037
1482.1135 | 449.5912 | 401.8749 | 385.6357 | 419.2286
1483.1135 | 449.6174 | 401.9803 | 385.7858 | 419.3725
1484.1135 | 449.6675 | 402.0002 | 385.8386 | 418.8043
1485.1135 | 449.7073 | 402.0434 | 385.9505 | 418.6833
1486.1135 | 449.8468 | 402.0909 | 385.9879 | 418.9251
1487.1135 | 449.9371 | 402.1154 | 386.0051 | 419.1346
1488.1135 | 450.0589 | 402.0548 | 385.7547 | 419.6779
1489.1135 | 450.2027 | 402.1081 | 385.9359 | 419.9194
1490.1135 | 450.2878 | 402.2076 | 386.0916 | 420.061
1491.1135 | 450.2225 | 402.2683 | 386.1597 | 419.8129
1492.1135 | 450.2999 | 402.2755 | 386.2064 | 419.7881
1493.1135 | 450.2979 | 402.3539 | 386.2191 | 420.3241
1494.1135 | 450.3872 | 402.5045 | 386.3709 | 420.7808
1495.1135 | 450.3853 | 402.4249 | 386.3897 | 421.5276
1496.1135 | 450.3821 | 402.5059 | 386.3542 | 421.5496
1497.1135 | 450.4287 | 402.5671 | 386.3827 | 421.8262
1498.1135 | 450.4276 | 402.6184 | 386.4514 | 421.4436
1499.1135 | 450.4588 | 402.6534 | 386.4545 | 421.2951
1500.1135 | 450.5045 | 402.6792 | 386.5962 | 422.0116
1501.1135 | 450.5172 | 402.7465 | 386.7121 | 421.3591
1502.1135 | 450.5269 | 402.7378 | 386.6633 | 421.3588
1503.1135 | 450.4011 | 402.7973 | 386.7429 | 420.9474
1504.1135 | 450.4107 | 402.8995 | 386.9187 | 420.043
1505.1135 | 450.4238 | 402.9115 | 386.9319 | 419.9453
1506.1135 | 450.4485 | 402.8923 | 386.975 | 419.7942
1507.1135 | 450.5875 | 402.9257 | 386.9844 | 419.7249
1508.1135 | 450.5896 | 402.9985 | 387.0096 | 420.0269
1509.1135 | 450.5983 | 403.0684 | 387.0962 | 419.9039
1510.1135 | 450.6451 | 403.1295 | 387.1787 | 421.0437
1511.1135 | 450.6102 | 403.1695 | 387.2349 | 419.9167
1512.1135 | 450.614 | 403.1613 | 387.1635 | 421.4518
1513.1135 | 450.573 | 403.2271 | 387.1661 | 421.4095
1514.1135 | 450.522 | 403.288 | 387.1851 | 421.4345
1515.1135 | 450.5858 | 403.3116 | 387.211 | 420.7683
1516.1135 | 450.5739 | 403.3552 | 387.2642 | 421.1012
1517.1135 | 450.4438 | 403.4029 | 387.2238 | 421.5721
1518.1135 | 450.3263 | 403.4319 | 387.4201 | 421.3477
1519.1135 | 450.2172 | 403.4455 | 387.4568 | 421.2816
1520.1135 | 450.219 | 403.5315 | 387.5089 | 421.5505
1521.1135 | 450.1908 | 403.5384 | 387.5772 | 421.8497
1522.1135 | 450.1359 | 403.5542 | 387.5842 | 421.7398
1523.1135 | 450.0106 | 403.6356 | 387.6203 | 420.9306
1524.1135 | 449.9196 | 403.6943 | 387.6416 | 420.6979
1525.1135 | 449.9057 | 403.7366 | 387.7087 | 420.6838
1526.1135 | 449.8692 | 403.7625 | 387.8769 | 421.1939
1527.1135 | 449.8318 | 403.8157 | 387.939 | 421.4578
1528.1135 | 449.7864 | 403.8443 | 388.0028 | 421.5586
1529.1135 | 449.6719 | 403.8755 | 388.0298 | 421.1167
1530.1135 | 449.6279 | 403.8678 | 388.0972 | 421.4133
1531.1135 | 449.553 | 403.9059 | 388.0532 | 421.391
1532.1135 | 449.5906 | 403.9083 | 388.0894 | 421.6497
1533.1135 | 449.6164 | 403.9673 | 388.1519 | 421.5781
1534.1135 | 449.6442 | 403.9909 | 388.2113 | 421.6098
1535.1135 | 449.6764 | 404.0089 | 388.2179 | 422.3491
1536.1135 | 449.6257 | 404.0247 | 388.2254 | 422.5953
1537.1135 | 449.61 | 404.1291 | 388.3642 | 421.8584
1538.1135 | 449.5469 | 404.1597 | 388.4152 | 421.3898
1539.1135 | 449.5935 | 404.19 | 388.3487 | 421.3692
1540.1135 | 449.5385 | 404.2557 | 388.5052 | 421.6674
1541.1135 | 449.4715 | 404.2817 | 388.5924 | 422.4158
1542.1135 | 449.5102 | 404.267 | 388.5878 | 423.0292
1543.1135 | 449.4611 | 404.3482 | 388.6038 | 422.6307
1544.1135 | 449.4716 | 404.3765 | 388.572 | 422.3741
1545.1135 | 449.4431 | 404.4516 | 388.6328 | 422.8181
1546.1135 | 449.3899 | 404.5046 | 388.7049 | 423.0947
1547.1135 | 449.3702 | 404.5253 | 388.7151 | 422.9452
1548.1135 | 449.3282 | 404.5675 | 388.655 | 423.3487
1549.1135 | 449.2962 | 404.5706 | 388.6307 | 423.0239
1550.1135 | 449.2899 | 404.6375 | 388.6685 | 423.3909
1551.1135 | 449.2407 | 404.6647 | 388.783 | 423.3589
1552.1135 | 449.1415 | 404.6845 | 388.8395 | 423.67
1553.1135 | 449.0995 | 404.7199 | 388.811 | 423.2194
1554.1135 | 449.1228 | 404.6938 | 388.8623 | 423.3125
1555.1135 | 449.134 | 404.7261 | 389.0118 | 423.79
1556.1135 | 449.0796 | 404.7716 | 388.8832 | 424.02
1557.1135 | 448.9985 | 404.8331 | 388.8875 | 424.1642
1558.1135 | 449.0207 | 404.8662 | 388.9119 | 424.4415
1559.1135 | 449.013 | 404.7892 | 388.9714 | 424.2647
1560.1135 | 449.0088 | 404.8649 | 389.0761 | 424.7466
1561.1135 | 449.097 | 405.0041 | 388.9062 | 424.5135
1562.1135 | 449.2163 | 405.077 | 389.0513 | 424.8262
1563.1135 | 449.3053 | 405.1075 | 389.1196 | 425.2111
1564.1135 | 449.3804 | 405.1068 | 389.2553 | 425.1909
1565.1135 | 449.4048 | 405.0866 | 389.2534 | 425.4222
1566.1135 | 449.4847 | 405.1126 | 389.3382 | 425.3045
1567.1135 | 449.4862 | 405.1469 | 389.3874 | 424.8124
1568.1135 | 449.5567 | 405.1501 | 389.5013 | 424.1113
1569.1135 | 449.6091 | 405.2374 | 389.6052 | 423.353
1570.1135 | 449.6563 | 405.271 | 389.6359 | 423.5283
1571.1135 | 449.7684 | 405.2962 | 389.6631 | 423.6885
1572.1135 | 449.831 | 405.3416 | 389.6818 | 424.0139
1573.1135 | 449.8723 | 405.374 | 389.6968 | 424.0221
1574.1135 | 449.8362 | 405.3928 | 389.7808 | 424.7928
1575.1135 | 449.7062 | 405.4402 | 389.8171 | 425.5118
1576.1135 | 449.7325 | 405.5173 | 389.8672 | 425.1661
1577.1135 | 449.7961 | 405.5208 | 389.9001 | 424.8889
1578.1135 | 449.8705 | 405.5485 | 389.8509 | 425.1599
1579.1135 | 449.8852 | 405.6002 | 389.9091 | 425.0296
1580.1135 | 449.803 | 405.6761 | 389.8833 | 425.5768
1581.1135 | 449.8316 | 405.7108 | 390.0007 | 424.7663
1582.1135 | 449.9025 | 405.7576 | 390.0902 | 424.8574
1583.1135 | 449.838 | 405.7957 | 389.9926 | 424.5539
1584.1135 | 449.7955 | 405.8252 | 390.0609 | 424.5425
1585.1135 | 449.7866 | 405.8072 | 390.1071 | 424.7591
1586.1135 | 449.7618 | 405.8363 | 390.1451 | 425.4959
1587.1135 | 449.8372 | 405.8359 | 389.9415 | 425.6518
1588.1135 | 449.813 | 405.9143 | 389.7862 | 425.3195
1589.1135 | 449.8091 | 405.921 | 389.9467 | 425.4665
1590.1135 | 449.6699 | 405.9671 | 390.1355 | 425.465
1591.1135 | 449.6694 | 406.0245 | 390.2496 | 425.3097
1592.1135 | 449.6633 | 406.0311 | 390.3629 | 425.6022
1593.1135 | 449.6655 | 406.0869 | 390.3738 | 424.6551
1594.1135 | 449.6017 | 406.1223 | 390.4411 | 424.3097
1595.1135 | 449.5383 | 406.0736 | 390.5345 | 424.7659
1596.1135 | 449.4862 | 406.1227 | 390.5446 | 423.6836
1597.1135 | 449.4898 | 406.114 | 390.4851 | 423.7003
1598.1135 | 449.4718 | 406.2074 | 390.4715 | 423.7941
1599.1135 | 449.5246 | 406.2342 | 390.5586 | 423.7031
1600.1135 | 449.544 | 406.2687 | 390.5554 | 424.553
1601.1135 | 449.5522 | 406.3277 | 390.588 | 424.2845
1602.1135 | 449.6768 | 406.3665 | 390.6161 | 424.8032
1603.1135 | 449.6484 | 406.3939 | 390.3661 | 425.2475
1604.1135 | 449.54 | 406.4345 | 390.5744 | 425.3471
1605.1135 | 449.541 | 406.5132 | 390.6609 | 425.5494
1606.1135 | 449.6064 | 406.585 | 390.6605 | 425.9956
1607.1135 | 449.6898 | 406.5652 | 390.7499 | 426.5288
1608.1135 | 449.7748 | 406.5772 | 390.7644 | 426.8622
1609.1135 | 449.754 | 406.6219 | 390.9023 | 427.1361
1610.1135 | 449.6704 | 406.6346 | 391.0127 | 428.1029
1611.1135 | 449.6267 | 406.6977 | 391.0692 | 428.0835
1612.1135 | 449.6838 | 406.7318 | 391.1173 | 428.0833
1613.1135 | 449.7015 | 406.7604 | 391.1481 | 428.2911
1614.1135 | 449.7219 | 406.7951 | 391.2246 | 428.7576
1615.1135 | 449.7726 | 406.7837 | 391.2563 | 428.6845
1616.1135 | 449.6558 | 406.8287 | 391.3375 | 428.8581
1617.1135 | 449.621 | 406.8964 | 391.2958 | 429.1067
1618.1135 | 449.5865 | 406.8654 | 391.3521 | 429.3339
1619.1135 | 449.5933 | 406.8715 | 391.3442 | 429.2493
1620.1135 | 449.5945 | 406.8422 | 391.4761 | 428.7529
1621.1135 | 449.6597 | 406.9411 | 391.5031 | 428.1486
1622.1135 | 449.719 | 406.968 | 391.591 | 428.1237
1623.1135 | 449.6952 | 407.0469 | 391.5796 | 427.91
1624.1135 | 449.7671 | 407.0567 | 391.59 | 427.8847
1625.1135 | 449.8472 | 407.0353 | 391.639 | 428.3552
1626.1135 | 449.9288 | 407.1127 | 391.7082 | 428.2608
1627.1135 | 450.0232 | 407.09 | 391.7106 | 428.0192
1628.1135 | 450.1292 | 407.1411 | 391.7394 | 427.8012
1629.1135 | 450.1223 | 407.1632 | 391.6966 | 427.1782
1630.1135 | 450.1051 | 407.1951 | 391.7612 | 426.919
1631.1135 | 450.1322 | 407.2971 | 391.8863 | 426.8045
1632.1135 | 450.1131 | 407.3196 | 391.8803 | 426.4483
1633.1135 | 450.1129 | 407.3759 | 391.9267 | 426.636
1634.1135 | 450.1013 | 407.4041 | 391.9881 | 426.5747
1635.1135 | 450.1023 | 407.3903 | 391.932 | 426.0144
1636.1135 | 450.0527 | 407.3771 | 391.9331 | 425.8742
1637.1135 | 450.1099 | 407.4194 | 391.8908 | 425.9285
1638.1135 | 450.1443 | 407.4844 | 392.0096 | 425.015
1639.1135 | 450.2226 | 407.4889 | 392.0429 | 425.0508
1640.1135 | 450.2109 | 407.5208 | 392.0925 | 425.5472
1641.1135 | 450.2388 | 407.5571 | 392.1721 | 424.9215
1642.1135 | 450.1506 | 407.581 | 392.2445 | 425.239
1643.1135 | 450.1185 | 407.6008 | 392.3015 | 423.9507
1644.1135 | 450.1853 | 407.6537 | 392.3031 | 423.3561
1645.1135 | 450.1905 | 407.6851 | 392.4051 | 423.8436
1646.1135 | 450.2131 | 407.6716 | 392.5329 | 423.5848
1647.1135 | 450.2476 | 407.7255 | 392.4819 | 423.7881
1648.1135 | 450.1577 | 407.7554 | 392.4881 | 424.4686
1649.1135 | 450.2113 | 407.7812 | 392.3723 | 424.549
1650.1135 | 450.2045 | 407.8243 | 392.3635 | 425.1703
1651.1135 | 450.2005 | 407.8429 | 392.3697 | 425.0464
1652.1135 | 450.2143 | 407.8917 | 392.4901 | 425.0043
1653.1135 | 450.1903 | 407.9306 | 392.4602 | 425.2035
1654.1135 | 450.1175 | 407.9223 | 392.552 | 425.6721
1655.1135 | 450.1317 | 407.9008 | 392.6317 | 426.3703
1656.1135 | 450.0385 | 407.9437 | 392.6643 | 425.9571
1657.1135 | 450.0014 | 407.9183 | 392.5125 | 425.0921
1658.1135 | 449.9581 | 408.0047 | 392.6199 | 424.9185
1659.1135 | 449.9811 | 408.0451 | 392.6349 | 425.5952
1660.1135 | 450.0039 | 408.0532 | 392.69 | 425.9085
1661.1135 | 449.8688 | 408.0948 | 392.7254 | 426.0472
1662.1135 | 449.856 | 408.0932 | 392.7903 | 425.678
1663.1135 | 449.8685 | 408.143 | 392.7552 | 424.5765
1664.1135 | 449.8455 | 408.0511 | 392.7678 | 424.6721
1665.1135 | 449.8698 | 408.1535 | 392.9361 | 424.4926
1666.1135 | 449.9121 | 408.2247 | 392.8754 | 424.1307
1667.1135 | 449.9727 | 408.1622 | 393.0028 | 423.6998
1668.1135 | 450.002 | 408.2109 | 393.1276 | 423.3005
1669.1135 | 449.9114 | 408.2802 | 393.0511 | 423.9467
1670.1135 | 449.8694 | 408.3055 | 393.0858 | 424.7535
1671.1135 | 449.9057 | 408.3356 | 393.1528 | 424.9125
1672.1135 | 449.9757 | 408.3847 | 393.2588 | 425.0875
1673.1135 | 450.047 | 408.4337 | 393.3509 | 425.4651
1674.1135 | 450.0077 | 408.4867 | 393.3505 | 425.4112
1675.1135 | 450.0385 | 408.4898 | 393.4251 | 425.6896
1676.1135 | 450.0532 | 408.5011 | 393.3977 | 425.589
1677.1135 | 450.1079 | 408.5428 | 393.3427 | 425.7279
1678.1135 | 450.114 | 408.5835 | 393.3149 | 425.6147
1679.1135 | 450.0602 | 408.5925 | 393.364 | 425.5881
1680.1135 | 450.0231 | 408.5912 | 393.328 | 425.4047
1681.1135 | 449.9325 | 408.5628 | 393.3812 | 425.6919
1682.1135 | 449.9018 | 408.6291 | 393.4342 | 426.0474
1683.1135 | 449.8439 | 408.6592 | 393.5498 | 426.0879
1684.1135 | 449.868 | 408.7676 | 393.5133 | 426.1169
1685.1135 | 449.8154 | 408.7901 | 393.4771 | 426.8493
1686.1135 | 449.7087 | 408.7958 | 393.4344 | 426.1385
1687.1135 | 449.7143 | 408.8485 | 393.5168 | 426.0495
1688.1135 | 449.6844 | 408.8534 | 393.557 | 426.4455
1689.1135 | 449.6686 | 408.9084 | 393.6945 | 426.2908
1690.1135 | 449.6244 | 408.9698 | 393.8423 | 426.5225
1691.1135 | 449.6065 | 408.9735 | 393.8885 | 425.8996
1692.1135 | 449.4665 | 408.9888 | 393.8462 | 426.2743
1693.1135 | 449.4409 | 408.9842 | 393.8705 | 426.3316
1694.1135 | 449.4818 | 408.9667 | 393.9256 | 426.5759
1695.1135 | 449.5424 | 408.9972 | 394.0507 | 426.1993
1696.1135 | 449.488 | 409.0134 | 394.0739 | 425.7068
1697.1135 | 449.4515 | 409.0572 | 394.0785 | 425.6177
1698.1135 | 449.4904 | 409.0858 | 394.0927 | 425.8009
1699.1135 | 449.4542 | 409.0983 | 394.1188 | 426.1074
1700.1135 | 449.4639 | 409.1369 | 394.2073 | 426.603
1701.1135 | 449.4382 | 409.1345 | 394.1666 | 426.5369
1702.1135 | 449.4437 | 409.166 | 394.1261 | 425.5066
1703.1135 | 449.488 | 409.2195 | 394.0458 | 425.8488
1704.1135 | 449.4897 | 409.2671 | 394.1572 | 426.3531
1705.1135 | 449.5186 | 409.2305 | 394.224 | 426.869
1706.1135 | 449.5063 | 409.2487 | 394.2841 | 427.4376
1707.1135 | 449.5494 | 409.2929 | 394.2272 | 426.8603
1708.1135 | 449.5884 | 409.3643 | 394.3036 | 425.9468
1709.1135 | 449.6097 | 409.3693 | 394.3694 | 426.2851
1710.1135 | 449.6783 | 409.4094 | 394.4115 | 427.1397
1711.1135 | 449.7069 | 409.4119 | 394.4135 | 427.5847
1712.1135 | 449.6942 | 409.4747 | 394.4292 | 428.2591
1713.1135 | 449.721 | 409.5062 | 394.4662 | 428.7118
1714.1135 | 449.7652 | 409.532 | 394.5445 | 428.6385
1715.1135 | 449.7779 | 409.5424 | 394.6472 | 429.1389
1716.1135 | 449.7844 | 409.5841 | 394.6472 | 429.2786
1717.1135 | 449.7595 | 409.6014 | 394.5723 | 430.0761
1718.1135 | 449.7265 | 409.5996 | 394.5526 | 430.8093
1719.1135 | 449.7155 | 409.6606 | 394.6117 | 430.8784
1720.1135 | 449.6729 | 409.6353 | 394.7064 | 431.487
1721.1135 | 449.7648 | 409.6758 | 394.7135 | 431.5618
1722.1135 | 449.8654 | 409.699 | 394.7522 | 431.5958
1723.1135 | 449.8843 | 409.767 | 394.8029 | 431.7486
1724.1135 | 449.9137 | 409.8279 | 394.8224 | 432.1932
1725.1135 | 449.9665 | 409.8704 | 394.8306 | 432.3658
1726.1135 | 449.9793 | 409.9037 | 394.7695 | 433.0638
1727.1135 | 449.9951 | 409.9436 | 394.8715 | 432.9222
1728.1135 | 449.9897 | 409.9409 | 394.9974 | 433.2671
1729.1135 | 450.0939 | 409.9598 | 395.0833 | 433.5925
1730.1135 | 450.1018 | 409.949 | 395.0768 | 433.9896
1731.1135 | 450.1059 | 409.9831 | 395.1522 | 433.7759
1732.1135 | 450.1258 | 409.9898 | 394.9732 | 433.961
1733.1135 | 450.1593 | 409.9348 | 395.0321 | 434.8815
1734.1135 | 450.19 | 410.0135 | 395.1584 | 435.166
1735.1135 | 450.206 | 410.029 | 395.1916 | 435.3562
1736.1135 | 450.332 | 410.0251 | 395.2259 | 435.4618
1737.1135 | 450.3488 | 410.0589 | 395.2057 | 434.9763
1738.1135 | 450.3097 | 410.145 | 395.1722 | 434.6507
1739.1135 | 450.3304 | 410.1968 | 395.1511 | 434.7199
1740.1135 | 450.3782 | 410.1869 | 395.2735 | 435.146
1741.1135 | 450.4138 | 410.2162 | 395.3273 | 435.2966
1742.1135 | 450.402 | 410.216 | 395.3318 | 434.6115
1743.1135 | 450.4687 | 410.2499 | 395.4002 | 434.3936
1744.1135 | 450.4323 | 410.3222 | 395.4546 | 434.3763
1745.1135 | 450.4529 | 410.3083 | 395.468 | 434.9155
1746.1135 | 450.4254 | 410.3411 | 395.552 | 435.0368
1747.1135 | 450.3844 | 410.3619 | 395.5516 | 434.6933
1748.1135 | 450.3254 | 410.4017 | 395.4802 | 434.3025
1749.1135 | 450.329 | 410.4998 | 395.4935 | 433.9886
1750.1135 | 450.3536 | 410.5364 | 395.5483 | 433.5708
1751.1135 | 450.4467 | 410.501 | 395.6537 | 433.7492
1752.1135 | 450.435 | 410.4936 | 395.7101 | 433.7835
1753.1135 | 450.4526 | 410.519 | 395.7505 | 433.9433
1754.1135 | 450.5028 | 410.6168 | 395.7248 | 434.0947
1755.1135 | 450.4829 | 410.6198 | 395.7943 | 434.318
1756.1135 | 450.4786 | 410.6201 | 395.8098 | 434.4467
1757.1135 | 450.5015 | 410.5798 | 395.8078 | 434.4619
1758.1135 | 450.5954 | 410.6358 | 395.8168 | 434.0436
1759.1135 | 450.6268 | 410.6263 | 395.8395 | 434.6333
1760.1135 | 450.6602 | 410.6576 | 395.9702 | 435.0022
1761.1135 | 450.6418 | 410.7037 | 396.0597 | 435.6801
1762.1135 | 450.6644 | 410.7514 | 396.076 | 436.0899
1763.1135 | 450.6581 | 410.8059 | 395.7916 | 437.2235
1764.1135 | 450.6587 | 410.8091 | 395.8968 | 437.4623
1765.1135 | 450.6085 | 410.8301 | 395.9018 | 437.9536
1766.1135 | 450.5578 | 410.8692 | 396.0348 | 437.8443
1767.1135 | 450.5935 | 410.9134 | 396.1194 | 438.5746
1768.1135 | 450.5395 | 410.9591 | 396.124 | 438.9224
1769.1135 | 450.548 | 410.9721 | 396.0571 | 439.4642
1770.1135 | 450.4343 | 411.0203 | 396.1042 | 439.1699
1771.1135 | 450.3581 | 411.0733 | 396.1646 | 439.8979
1772.1135 | 450.4518 | 411.0882 | 396.1909 | 440.2932
1773.1135 | 450.4313 | 411.13 | 396.2425 | 440.1831
1774.1135 | 450.4804 | 411.1484 | 396.1806 | 440.0787
1775.1135 | 450.5204 | 411.1703 | 396.2991 | 440.4361
1776.1135 | 450.51 | 411.1472 | 396.2393 | 440.5371
1777.1135 | 450.5403 | 411.1304 | 396.2451 | 440.8681
1778.1135 | 450.5466 | 411.1706 | 396.3449 | 441.0956
1779.1135 | 450.5343 | 411.2403 | 396.5002 | 441.2223
1780.1135 | 450.4369 | 411.2818 | 396.6004 | 440.8403
1781.1135 | 450.3876 | 411.3073 | 396.6492 | 440.8631
1782.1135 | 450.3173 | 411.2929 | 396.6613 | 440.6538
1783.1135 | 450.2367 | 411.3212 | 396.6799 | 441.0051
1784.1135 | 450.1403 | 411.3648 | 396.7245 | 441.0962
1785.1135 | 450.2278 | 411.4104 | 396.8096 | 440.734
1786.1135 | 450.2083 | 411.4301 | 396.8216 | 440.6262
1787.1135 | 450.1819 | 411.4405 | 396.7018 | 440.6565
1788.1135 | 450.1609 | 411.475 | 396.7037 | 440.8294
1789.1135 | 450.1213 | 411.4829 | 396.7925 | 441.0939
1790.1135 | 450.1325 | 411.4714 | 396.8249 | 440.9004
1791.1135 | 450.0671 | 411.5183 | 396.8576 | 441.5147
1792.1135 | 450.0824 | 411.5466 | 396.89 | 441.5022
1793.1135 | 450.097 | 411.5387 | 396.8776 | 441.8557
1794.1135 | 450.0946 | 411.5601 | 396.8943 | 442.0199
1795.1135 | 450.0499 | 411.6079 | 396.8895 | 442.3298
1796.1135 | 449.9867 | 411.6588 | 396.8683 | 441.6619
1797.1135 | 449.9691 | 411.6287 | 396.969 | 441.8625
1798.1135 | 449.9796 | 411.6224 | 397.1441 | 441.6139
1799.1135 | 449.9456 | 411.6318 | 397.2577 | 441.4346
1800.1135 | 449.8663 | 411.6895 | 397.1787 | 441.8597
1801.1135 | 449.8436 | 411.6897 | 397.1732 | 442.3448
1802.1135 | 449.8606 | 411.7024 | 397.2143 | 442.0575
1803.2854 | 449.8355 | 411.7235 | 397.2025 | 442.298
1804.1135 | 449.8541 | 411.7534 | 397.2285 | 442.5102
1805.1135 | 449.9059 | 411.8173 | 397.3115 | 442.9691
1806.1135 | 450.0385 | 411.7724 | 397.2629 | 443.5229
1807.1135 | 450.0868 | 411.7776 | 397.2924 | 443.1433
1808.1135 | 450.1936 | 411.8196 | 397.3378 | 443.4284
1809.1135 | 450.2451 | 411.832 | 397.3656 | 443.1754
1810.1135 | 450.2008 | 411.8787 | 397.3313 | 443.2736
1811.1135 | 450.2753 | 411.8958 | 397.3376 | 443.0105
1812.1135 | 450.3494 | 411.912 | 397.3909 | 443.0972
1813.1135 | 450.3479 | 411.9336 | 397.3291 | 443.258
1814.1135 | 450.3962 | 411.9684 | 397.3615 | 442.7305
1815.1135 | 450.4336 | 412.0013 | 397.4795 | 443.4765
1816.1135 | 450.5404 | 412.0251 | 397.5429 | 442.9232
1817.1292 | 450.6006 | 412.0484 | 397.6178 | 442.9695
1818.1135 | 450.6576 | 412.054 | 397.7177 | 442.819
1819.1135 | 450.7138 | 412.0348 | 397.7328 | 442.7998
1820.1135 | 450.7648 | 412.0799 | 397.8029 | 443.5179
1821.1135 | 450.8494 | 412.1536 | 397.7852 | 443.7443
1822.1135 | 450.9589 | 412.1937 | 397.7863 | 443.7357
1823.1135 | 451.0355 | 412.2061 | 397.8524 | 443.9979
1824.1135 | 451.0177 | 412.261 | 397.8233 | 443.2452
1825.1135 | 451.0436 | 412.3032 | 397.8201 | 442.9982
1826.1135 | 451.0661 | 412.2819 | 397.865 | 443.1687
1827.1135 | 451.011 | 412.3659 | 397.7959 | 444.149
1828.1135 | 451.0574 | 412.4039 | 397.8467 | 443.7859
1829.1135 | 451.1612 | 412.4617 | 397.7188 | 444.0746
1830.1135 | 451.0916 | 412.4667 | 397.7831 | 444.967
1831.1135 | 451.0525 | 412.4653 | 397.8963 | 445.2033
1832.1135 | 451.0864 | 412.457 | 397.9415 | 445.4702
1833.1135 | 451.1297 | 412.5443 | 398.0091 | 446.0702
1834.1135 | 451.1924 | 412.5639 | 397.9779 | 446.4175
1835.1135 | 451.1651 | 412.531 | 397.9009 | 446.487
1836.1135 | 451.1651 | 412.5893 | 397.9629 | 446.4363
1837.1135 | 451.2236 | 412.6652 | 398.034 | 446.7084
1838.1135 | 451.2008 | 412.6285 | 398.0074 | 446.6355
1839.1135 | 451.1446 | 412.6357 | 397.9076 | 447.0676
1840.1135 | 451.0443 | 412.6524 | 397.7551 | 447.3577
1841.1135 | 451.027 | 412.6929 | 397.9275 | 446.7738
1842.1135 | 451.057 | 412.6976 | 398.1047 | 446.5745
1843.1135 | 451.0101 | 412.6836 | 398.1989 | 446.8737
1844.1135 | 450.9517 | 412.7022 | 398.1511 | 446.743
1845.1135 | 450.8894 | 412.7374 | 398.1159 | 447.2759
1846.1135 | 450.7544 | 412.7941 | 398.1953 | 446.9274
1847.1292 | 450.7165 | 412.8164 | 398.2 | 446.691
1848.1135 | 450.7145 | 412.8595 | 398.2909 | 447.0689
1849.1135 | 450.7291 | 412.8545 | 398.25 | 446.9644
1850.1135 | 450.7841 | 412.8525 | 398.3075 | 447.4562
1851.1135 | 450.7425 | 412.9251 | 398.3115 | 447.0516
1852.1135 | 450.5652 | 412.9902 | 398.3241 | 447.3377
1853.1135 | 450.4456 | 413.0433 | 398.4139 | 447.3063
1854.1135 | 450.401 | 413.0173 | 398.4541 | 447.1306
1855.1135 | 450.3033 | 413.04 | 398.3715 | 447.1609
1856.1135 | 450.2116 | 413.053 | 398.435 | 446.9874
1857.1135 | 450.1035 | 413.1298 | 398.4781 | 447.444
1858.1135 | 450.0618 | 413.1589 | 398.5682 | 447.8999
1859.1135 | 450.0306 | 413.1612 | 398.6468 | 447.3672
1860.1135 | 449.9846 | 413.1636 | 398.601 | 447.5084
1861.1135 | 450.0313 | 413.169 | 398.6571 | 448.485
1862.1135 | 450.1492 | 413.1908 | 398.6394 | 448.3832
1863.1135 | 450.0707 | 413.1024 | 398.6472 | 448.4319
1864.1135 | 449.983 | 413.1254 | 398.5751 | 448.1572
1865.1135 | 449.976 | 413.2154 | 398.5939 | 448.9816
1866.1135 | 449.9438 | 413.2017 | 398.6865 | 449.5407
1867.1135 | 449.9348 | 413.2223 | 398.7525 | 449.8965
1868.1135 | 449.8077 | 413.2726 | 398.7353 | 450.5866
1869.1135 | 449.7474 | 413.2989 | 398.6462 | 449.9319
1870.1135 | 449.6788 | 413.3993 | 398.7101 | 449.992
1871.1135 | 449.6661 | 413.4324 | 398.7794 | 449.9077
1872.1135 | 449.6385 | 413.3785 | 398.828 | 449.5632
1873.1135 | 449.5321 | 413.3789 | 398.8026 | 450.1372
1874.1135 | 449.5063 | 413.4058 | 398.8087 | 450.1965
1875.1135 | 449.5304 | 413.423 | 398.9526 | 450.5025
1876.1135 | 449.4997 | 413.4754 | 398.9753 | 450.8289
1877.1292 | 449.4819 | 413.5033 | 398.8674 | 451.2627
1878.1135 | 449.465 | 413.5318 | 398.8718 | 450.9365
1879.1135 | 449.4708 | 413.6091 | 398.9818 | 449.7061
1880.1135 | 449.4679 | 413.545 | 399.0583 | 449.7734
1881.1135 | 449.4909 | 413.5628 | 399.0979 | 449.3141
1882.1135 | 449.5119 | 413.5969 | 399.1434 | 449.4846
1883.1135 | 449.5379 | 413.632 | 399.1121 | 449.4406
1884.1135 | 449.4978 | 413.5945 | 399.1955 | 449.5265
1885.1135 | 449.4176 | 413.6653 | 399.2656 | 450.2217
1886.1135 | 449.4021 | 413.6488 | 399.2135 | 450.7481
1887.1135 | 449.5156 | 413.6599 | 399.1779 | 451.2422
1888.1135 | 449.5879 | 413.7161 | 399.2767 | 451.0893
1889.1135 | 449.6073 | 413.7021 | 399.2663 | 451.6689
1890.1135 | 449.6566 | 413.7244 | 399.2129 | 452.094
1891.1135 | 449.7005 | 413.8337 | 399.1378 | 452.7149
1892.1135 | 449.7518 | 413.7402 | 399.1957 | 452.527
1893.1135 | 449.8186 | 413.7492 | 399.2287 | 451.6882
1894.1135 | 449.8601 | 413.8162 | 399.3158 | 451.7581
1895.1135 | 449.896 | 413.8304 | 399.3444 | 452.5532
1896.1135 | 449.9958 | 413.8863 | 399.3526 | 452.3603
1897.1135 | 450.0073 | 413.871 | 399.4032 | 452.5394
1898.1135 | 450.0694 | 413.8488 | 399.4251 | 452.3904
1899.1135 | 450.0375 | 413.862 | 399.5198 | 452.3741
1900.1135 | 450.0216 | 413.9036 | 399.5923 | 452.8579
1901.1135 | 450.0684 | 413.9477 | 399.5348 | 453.0254
1902.1135 | 450.1562 | 414.0263 | 399.4755 | 453.2231
1903.1135 | 450.234 | 414.0673 | 399.5354 | 451.955
1904.1135 | 450.3232 | 414.0875 | 399.6108 | 452.091
1905.1135 | 450.261 | 414.1887 | 399.6325 | 452.079
1906.1135 | 450.2857 | 414.1736 | 399.5721 | 451.8993
1907.1135 | 450.3437 | 414.1704 | 399.6184 | 451.5436
1908.1135 | 450.3266 | 414.1402 | 399.6867 | 451.1661
1909.1135 | 450.2631 | 414.139 | 399.6578 | 451.3751
1910.1135 | 450.2686 | 414.141 | 399.6556 | 451.8065
1911.1135 | 450.3077 | 414.1696 | 399.7084 | 452.0243
1912.1135 | 450.3434 | 414.0939 | 399.8468 | 451.9893
1913.1135 | 450.2964 | 414.1457 | 399.8582 | 452.7146
1914.1135 | 450.3517 | 414.1909 | 399.9049 | 452.518
1915.1135 | 450.3945 | 414.1579 | 399.7916 | 452.9996
1916.1135 | 450.3908 | 414.1835 | 399.8243 | 453.573
1917.1135 | 450.3171 | 414.2068 | 399.9096 | 453.583
1918.1135 | 450.299 | 414.2661 | 399.8649 | 454.0154
1919.1135 | 450.2605 | 414.2869 | 399.8459 | 453.2806
1920.1135 | 450.3202 | 414.3512 | 399.9542 | 453.4228
1921.1135 | 450.3955 | 414.3973 | 400.0456 | 453.3207
1922.1135 | 450.447 | 414.3515 | 400.0399 | 453.5564
1923.1135 | 450.4459 | 414.3915 | 400.0226 | 452.9992
1924.1135 | 450.3674 | 414.4246 | 399.9239 | 452.0677
1925.1135 | 450.3002 | 414.4287 | 400.057 | 452.2215
1926.1135 | 450.2645 | 414.4 | 400.0805 | 453.3605
1927.1135 | 450.2635 | 414.5548 | 400.0919 | 453.4343
1928.1135 | 450.33 | 414.54 | 400.1227 | 453.3901
1929.1135 | 450.3441 | 414.5525 | 400.21 | 452.8344
1930.1135 | 450.3322 | 414.5735 | 400.1925 | 452.9993
1931.1135 | 450.3402 | 414.6065 | 399.7315 | 452.9825
1932.1135 | 450.2269 | 414.5835 | 400.0307 | 453.6255
1933.1135 | 450.2446 | 414.5954 | 400.1572 | 453.6487
1934.1135 | 450.2287 | 414.6399 | 400.2439 | 453.8633
1935.1135 | 450.1885 | 414.7009 | 400.2933 | 454.2075
1936.1135 | 450.1321 | 414.8039 | 400.2751 | 455.186
1937.1292 | 450.1739 | 414.7737 | 400.2202 | 455.8905
1938.1135 | 450.2035 | 414.7879 | 400.2216 | 455.2853
1939.1135 | 450.298 | 414.7342 | 400.2583 | 455.2549
1940.1135 | 450.3186 | 414.7495 | 400.2433 | 455.9282
1941.1135 | 450.3169 | 414.7927 | 400.3062 | 456.1674
1942.1135 | 450.3161 | 414.8024 | 400.3385 | 455.7543
1943.1135 | 450.2577 | 414.8251 | 400.3737 | 456.3122
1944.1135 | 450.2631 | 414.8518 | 400.5412 | 456.8774
1945.1135 | 450.2651 | 414.8794 | 400.5856 | 456.8317
1946.1135 | 450.3513 | 414.8153 | 400.5878 | 457.5709
1947.1135 | 450.322 | 414.914 | 400.6282 | 457.0288
1948.1135 | 450.3493 | 414.9567 | 400.7562 | 456.5722
1949.1135 | 450.3319 | 414.9798 | 400.7584 | 456.6186
1950.1135 | 450.3599 | 414.9601 | 400.6737 | 456.8585
1951.1135 | 450.3396 | 414.9208 | 400.6734 | 456.2862
1952.1135 | 450.3022 | 414.8956 | 400.7652 | 456.5847
1953.1135 | 450.2644 | 414.9191 | 400.8123 | 457.0346
1954.1135 | 450.1873 | 414.9772 | 400.9089 | 456.3052
1955.1135 | 450.152 | 415.0053 | 400.8763 | 456.1454
1956.1135 | 450.1739 | 415.0094 | 400.8865 | 457.0201
1957.1135 | 450.224 | 415.0604 | 400.9189 | 456.4577
1958.1135 | 450.198 | 415.1187 | 400.9174 | 455.8941
1959.1135 | 450.1676 | 415.0851 | 400.9226 | 455.3855
1960.1135 | 450.1563 | 415.1085 | 400.9795 | 455.705
1961.1135 | 450.0615 | 415.1664 | 400.9022 | 455.5956
1962.1135 | 449.9959 | 415.1853 | 400.8532 | 455.3552
1963.1135 | 449.9991 | 415.2053 | 400.9125 | 456.119
1964.1135 | 449.9771 | 415.2254 | 401.0172 | 456.1882
1965.1135 | 449.9206 | 415.25 | 401.0691 | 458.2538
1966.1135 | 449.8763 | 415.2439 | 401.1073 | 457.6114
1967.1135 | 449.8773 | 415.2397 | 401.0676 | 457.37
1968.1135 | 449.8918 | 415.3002 | 401.1025 | 457.1521
1969.1135 | 449.8592 | 415.2801 | 401.1323 | 457.157
1970.1135 | 449.8151 | 415.2498 | 401.2218 | 457.9004
1971.1135 | 449.7106 | 415.2991 | 401.2711 | 457.4279
1972.1135 | 449.7094 | 415.3373 | 401.2298 | 457.6467
1973.1135 | 449.8126 | 415.293 | 401.2313 | 457.6446
1974.1135 | 449.9109 | 415.3579 | 401.2815 | 457.4153
1975.1135 | 449.9001 | 415.4221 | 401.2899 | 457.5893
1976.1135 | 449.9282 | 415.4099 | 401.1969 | 457.8265
1977.1135 | 449.9535 | 415.4686 | 401.2903 | 458.4037
1978.1135 | 450.0009 | 415.5425 | 401.345 | 458.5863
1979.1135 | 450.1408 | 415.5537 | 401.3476 | 458.4393
1980.1135 | 450.1693 | 415.5719 | 401.4465 | 458.5324
1981.1135 | 450.2947 | 415.6019 | 401.5195 | 458.547
1982.1135 | 450.3592 | 415.5672 | 401.5265 | 458.2608
1983.1135 | 450.4075 | 415.5553 | 401.5347 | 457.3434
1984.1135 | 450.573 | 415.5431 | 401.5055 | 457.8012
1985.1135 | 450.574 | 415.5188 | 401.4724 | 458.5382
1986.1135 | 450.6246 | 415.5727 | 401.4453 | 458.8849
1987.1135 | 450.7368 | 415.5666 | 401.4453 | 459.1366
1988.1135 | 450.7949 | 415.6314 | 401.5127 | 459.3201
1989.1135 | 450.8154 | 415.6525 | 401.5291 | 459.0517
1990.1135 | 450.8161 | 415.6788 | 401.5053 | 458.7609
1991.1135 | 450.7907 | 415.6978 | 401.6039 | 458.9078
1992.1135 | 450.8629 | 415.726 | 401.5531 | 459.0567
1993.1135 | 450.922 | 415.7432 | 401.5136 | 459.1167
1994.1135 | 450.9314 | 415.7802 | 401.6126 | 459.652
1995.1135 | 450.791 | 415.8326 | 401.654 | 459.6055
1996.1135 | 450.7289 | 415.867 | 401.6836 | 458.9944
1997.1135 | 450.6866 | 415.8782 | 401.6893 | 458.6568
1998.1135 | 450.7249 | 415.9047 | 401.788 | 459.0805
1999.1135 | 450.7078 | 415.9155 | 401.8557 | 459.1444
2000.1135 | 450.6534 | 415.9203 | 401.7479 | 459.2775
2001.1135 | 450.6625 | 416.002 | 401.8521 | 458.9953
2002.1135 | 450.6694 | 415.9304 | 401.9283 | 458.8678
2003.1135 | 450.6868 | 415.9866 | 401.8209 | 459.1048
2004.1135 | 450.6477 | 415.9873 | 401.7762 | 458.7353
2005.1135 | 450.6333 | 415.9401 | 401.8811 | 459.3519
2006.1135 | 450.5648 | 415.9585 | 401.9892 | 459.1637
2007.1135 | 450.5988 | 416.0156 | 402.0821 | 459.0908
2008.1135 | 450.564 | 415.9849 | 402.0493 | 458.9391
2009.1135 | 450.5786 | 416.0263 | 402.0039 | 459.2674
2010.1135 | 450.5882 | 416.0595 | 401.8716 | 460.048
2011.1135 | 450.6769 | 416.0639 | 401.9322 | 459.994
2012.1135 | 450.7418 | 416.1263 | 402.0038 | 459.6929
2013.1135 | 450.6897 | 416.0858 | 402.0969 | 460.1837
2014.1135 | 450.7232 | 416.1752 | 402.1064 | 459.1072
2015.1135 | 450.6905 | 416.2048 | 402.0633 | 460.0427
2016.1135 | 450.693 | 416.2309 | 402.1157 | 460.058
2017.1135 | 450.7554 | 416.2633 | 402.1066 | 459.6129
2018.1135 | 450.8004 | 416.2678 | 402.1226 | 459.4548
2019.1135 | 450.7834 | 416.2501 | 402.1846 | 459.8381
2020.1135 | 450.6886 | 416.2772 | 402.184 | 460.2222
2021.1135 | 450.5661 | 416.2979 | 402.1792 | 460.072
2022.1135 | 450.5988 | 416.2845 | 402.2254 | 460.172
2023.1135 | 450.5411 | 416.281 | 402.2669 | 460.5805
2024.1135 | 450.5352 | 416.3291 | 402.2938 | 460.7488
2025.1135 | 450.5171 | 416.3597 | 402.3245 | 461.4094
2026.1135 | 450.578 | 416.3961 | 402.4172 | 461.411
2027.1135 | 450.567 | 416.41 | 402.4386 | 460.6807
2028.1135 | 450.5216 | 416.4699 | 402.4383 | 460.5634
2029.1135 | 450.5381 | 416.5011 | 402.4678 | 460.2483
2030.1135 | 450.5319 | 416.5022 | 402.3379 | 460.2276
2031.1135 | 450.5247 | 416.5273 | 402.4457 | 460.027
2032.1135 | 450.5181 | 416.5492 | 402.4087 | 460.1642
2033.1135 | 450.4026 | 416.5655 | 402.4063 | 459.9797
2034.1135 | 450.3368 | 416.6216 | 402.4085 | 460.213
2035.1135 | 450.2748 | 416.5789 | 402.401 | 460.1707
2036.1135 | 450.1561 | 416.5374 | 402.314 | 460.0696
2037.1135 | 450.0491 | 416.5918 | 402.3805 | 460.1236
2038.1135 | 450.1342 | 416.6235 | 402.4929 | 460.1217
2039.1135 | 450.1111 | 416.6265 | 402.4794 | 460.3712
2040.1135 | 450.0965 | 416.6577 | 402.553 | 460.5616
2041.1135 | 450.1645 | 416.743 | 402.5596 | 460.3385
2042.1135 | 450.2159 | 416.7531 | 402.6014 | 459.9861
2043.1135 | 450.1991 | 416.7319 | 402.6438 | 459.61
2044.1135 | 450.2288 | 416.7848 | 402.6245 | 459.5358
2045.1135 | 450.2064 | 416.7113 | 402.687 | 459.6101
2046.1135 | 450.2075 | 416.7243 | 402.7726 | 459.2968
2047.1135 | 450.1924 | 416.7465 | 402.7811 | 458.4987
2048.1135 | 450.1099 | 416.7121 | 402.8457 | 458.8165
2049.1135 | 450.109 | 416.7376 | 402.8061 | 458.4595
2050.1135 | 450.1005 | 416.7832 | 402.7573 | 459.3398
2051.1135 | 450.1601 | 416.7971 | 402.7527 | 458.8625
2052.1135 | 450.1906 | 416.8325 | 402.7534 | 458.8268
2053.1135 | 450.1833 | 416.9037 | 402.8077 | 458.6823
2054.1135 | 450.23 | 416.9264 | 402.8668 | 458.5324
2055.1135 | 450.3766 | 416.978 | 402.8795 | 458.5408
2056.1135 | 450.4088 | 416.9963 | 402.8788 | 458.4737
2057.1135 | 450.4302 | 416.9789 | 402.8816 | 457.8628
2058.1135 | 450.406 | 416.9855 | 402.8837 | 458.3194
2059.1135 | 450.4258 | 417.0109 | 402.8304 | 458.6593
2060.1135 | 450.4965 | 417.0226 | 402.7996 | 458.4203
2061.1135 | 450.5714 | 417.0858 | 402.8904 | 458.1746
2062.1135 | 450.5883 | 417.1507 | 402.9486 | 457.9258
2063.1135 | 450.6101 | 417.1164 | 402.8103 | 458.3851
2064.1135 | 450.6058 | 417.1049 | 402.898 | 457.99
2065.1135 | 450.5805 | 417.1502 | 402.9296 | 457.8381
2066.1135 | 450.6036 | 417.2012 | 402.9137 | 457.9844
2067.1135 | 450.6111 | 417.1828 | 403.0329 | 457.9232
2068.1135 | 450.663 | 417.1581 | 403.0834 | 458.3609
2069.1135 | 450.6138 | 417.1908 | 403.1603 | 458.5175
2070.1135 | 450.6093 | 417.2758 | 403.0862 | 459.0263
2071.1135 | 450.5624 | 417.3436 | 403.0794 | 459.2497
2072.1135 | 450.5098 | 417.3309 | 402.9887 | 459.1993
2073.1135 | 450.5049 | 417.2863 | 403.0911 | 458.7923
2074.1135 | 450.5505 | 417.2846 | 403.165 | 459.0916
2075.1135 | 450.6304 | 417.3658 | 403.2024 | 459.2529
2076.1135 | 450.6397 | 417.3608 | 403.2202 | 458.5503
2077.1135 | 450.6248 | 417.3299 | 403.1344 | 458.3316
2078.1135 | 450.5968 | 417.3849 | 403.3338 | 458.3776
2079.1135 | 450.5953 | 417.4562 | 403.4098 | 458.6719
2080.1135 | 450.6119 | 417.4831 | 403.2911 | 458.8393
2081.1135 | 450.6005 | 417.4887 | 403.2834 | 459.2924
2082.1135 | 450.6293 | 417.5188 | 403.309 | 459.446
2083.1135 | 450.6245 | 417.5413 | 403.1635 | 459.4586
2084.1135 | 450.5808 | 417.5999 | 403.2419 | 459.3899
2085.1135 | 450.5392 | 417.6103 | 403.3411 | 459.328
2086.1135 | 450.4765 | 417.5925 | 403.3241 | 459.1452
2087.1135 | 450.4621 | 417.6083 | 403.3996 | 458.6126
2088.1135 | 450.387 | 417.6764 | 403.5496 | 458.4178
2089.1135 | 450.3584 | 417.682 | 403.5848 | 458.6715
2090.1135 | 450.3634 | 417.6969 | 403.5819 | 458.3041
2091.1135 | 450.3601 | 417.6905 | 403.5848 | 458.2313
2092.1135 | 450.3474 | 417.6939 | 403.6157 | 458.4307
2093.1135 | 450.3485 | 417.7404 | 403.6834 | 458.3453
2094.1135 | 450.3201 | 417.8276 | 403.7447 | 458.3971
2095.1135 | 450.3263 | 417.8477 | 403.7302 | 457.7898
2096.1135 | 450.3355 | 417.8398 | 403.7611 | 457.6984
2097.1135 | 450.2947 | 417.8585 | 403.7866 | 457.6548
2098.1135 | 450.2492 | 417.8682 | 403.7374 | 457.6281
2099.1135 | 450.2881 | 417.8312 | 403.7755 | 457.5162
2100.1135 | 450.3097 | 417.8335 | 403.7051 | 458.0549
2101.1135 | 450.314 | 417.8524 | 403.7423 | 457.7372
2102.1135 | 450.2609 | 417.904 | 403.8509 | 458.1458
2103.1135 | 450.2325 | 417.8887 | 403.8304 | 457.9541
2104.1135 | 450.198 | 417.9416 | 403.8037 | 458.2482
2105.1135 | 450.2386 | 417.9982 | 403.8345 | 458.2815
2106.1135 | 450.2495 | 417.9597 | 403.8117 | 458.0711
2107.1135 | 450.2681 | 417.9396 | 403.6402 | 457.6027
2108.1135 | 450.1919 | 417.9457 | 403.7974 | 457.4179
2109.1135 | 450.1273 | 418.0443 | 403.8708 | 457.125
2110.1135 | 450.1326 | 418.0801 | 403.9516 | 457.0567
2111.1135 | 450.2257 | 418.1297 | 403.9478 | 456.7938
2112.1135 | 450.2804 | 418.1061 | 403.8281 | 456.5426
2113.1135 | 450.261 | 418.1108 | 403.903 | 456.1862
2114.1135 | 450.1738 | 418.1423 | 403.9584 | 456.0115
2115.1135 | 450.1133 | 418.1374 | 403.9898 | 455.9001
2116.1135 | 450.1059 | 418.1147 | 403.9429 | 455.9833
2117.1292 | 450.0526 | 418.1354 | 403.991 | 455.8593
2118.1135 | 449.9681 | 418.1301 | 404.0119 | 456.0162
2119.1135 | 449.8722 | 418.0896 | 403.9636 | 455.8406
2120.1135 | 449.8591 | 418.1131 | 404.0506 | 456.2015
2121.1135 | 449.7955 | 418.1505 | 404.2117 | 455.9242
2122.1135 | 449.7683 | 418.1927 | 404.2578 | 455.7622
2123.1135 | 449.7916 | 418.2894 | 404.3436 | 455.8096
2124.1135 | 449.8433 | 418.2467 | 404.3491 | 456.2035
2125.1135 | 449.8311 | 418.3102 | 404.3387 | 456.3809
2126.1135 | 449.7676 | 418.2859 | 404.3466 | 456.1092
2127.1135 | 449.672 | 418.2536 | 404.3195 | 455.8322
2128.1135 | 449.6879 | 418.2938 | 404.2757 | 455.1205
2129.1135 | 449.7595 | 418.2966 | 404.3281 | 455.7115
2130.1135 | 449.7758 | 418.2988 | 404.3634 | 455.7552
2131.1135 | 449.7505 | 418.2907 | 404.2654 | 455.4617
2132.1135 | 449.7377 | 418.3532 | 404.2206 | 455.3859
2133.1135 | 449.6977 | 418.3848 | 404.4009 | 455.5207
2134.1135 | 449.7676 | 418.4715 | 404.5471 | 455.1106
2135.1135 | 449.8651 | 418.5095 | 404.5938 | 455.1871
2136.1135 | 449.8894 | 418.4266 | 404.5506 | 455.161
2137.1135 | 449.8188 | 418.4724 | 404.4683 | 454.846
2138.1135 | 449.8874 | 418.4939 | 404.4876 | 454.6126
2139.1135 | 449.9126 | 418.5181 | 404.4735 | 454.4412
2140.1135 | 449.8865 | 418.5038 | 404.4361 | 454.5628
2141.1135 | 449.8723 | 418.5315 | 404.4582 | 454.3591
2142.1135 | 449.9076 | 418.5518 | 404.4463 | 454.4992
2143.1135 | 449.9235 | 418.6031 | 404.448 | 454.5265
2144.1135 | 449.9292 | 418.6863 | 404.468 | 454.4739
2145.1135 | 449.9116 | 418.6915 | 404.6303 | 454.746
2146.1135 | 449.8885 | 418.6744 | 404.6543 | 454.1496
2147.1135 | 449.8997 | 418.6809 | 404.7356 | 453.6286
2148.1135 | 449.9426 | 418.6948 | 404.7495 | 453.788
2149.1135 | 449.9597 | 418.6306 | 404.6973 | 453.9575
2150.1135 | 450.022 | 418.6585 | 404.7492 | 453.0702
2151.1135 | 450.1036 | 418.6765 | 404.8044 | 453.0734
2152.1135 | 450.1797 | 418.7083 | 404.9766 | 452.5986
2153.1135 | 450.2856 | 418.7035 | 404.9163 | 452.9089
2154.1135 | 450.3603 | 418.692 | 404.7874 | 452.3832
2155.1135 | 450.3418 | 418.6097 | 404.8017 | 452.6706
2156.1135 | 450.3393 | 418.6722 | 404.8892 | 452.6024
2157.1135 | 450.243 | 418.662 | 404.8597 | 452.5331
2158.1135 | 450.1744 | 418.682 | 404.7708 | 452.5462
2159.1135 | 450.1954 | 418.7403 | 404.7919 | 452.5614
2160.1135 | 450.1874 | 418.7751 | 404.8462 | 452.4975
2161.1135 | 450.244 | 418.7716 | 404.8371 | 452.5596
2162.1135 | 450.2607 | 418.7948 | 404.9116 | 452.5166
2163.1135 | 450.2793 | 418.7648 | 404.9211 | 452.7632
2164.1135 | 450.2896 | 418.8376 | 405.0091 | 452.6451
2165.1135 | 450.3143 | 418.9146 | 405.0439 | 453.3632
2166.1135 | 450.263 | 418.8874 | 404.9825 | 453.0022
2167.1135 | 450.2898 | 418.8889 | 405.0095 | 452.8732
2168.1135 | 450.2961 | 418.9383 | 405.008 | 452.9377
2169.1135 | 450.252 | 418.8869 | 405.019 | 452.5898
2170.1135 | 450.2835 | 418.9269 | 404.9492 | 452.8923
2171.1135 | 450.2901 | 418.9502 | 405.0527 | 453.1851
2172.1135 | 450.2871 | 418.9905 | 405.1353 | 452.7982
2173.1135 | 450.308 | 418.9936 | 405.0962 | 452.3766
2174.1135 | 450.3815 | 418.9924 | 405.0446 | 452.3886
2175.1135 | 450.4663 | 419.032 | 405.0349 | 452.5932
2176.1135 | 450.5 | 419.0355 | 405.1465 | 452.0646
2177.1135 | 450.4935 | 419.1002 | 405.2283 | 451.6459
2178.1135 | 450.4702 | 419.1339 | 405.1826 | 451.4253
2179.1135 | 450.4791 | 419.0954 | 405.1962 | 451.669
2180.1135 | 450.4422 | 419.1244 | 405.2496 | 451.7733
2181.1135 | 450.4326 | 419.1065 | 405.2197 | 451.753
2182.1135 | 450.4686 | 419.1245 | 405.1585 | 450.5236
2183.1135 | 450.535 | 419.1478 | 405.2575 | 450.552
2184.1135 | 450.5585 | 419.2452 | 405.301 | 450.2034
2185.1135 | 450.5266 | 419.2156 | 405.3108 | 450.2248
2186.1135 | 450.5717 | 419.2197 | 405.3138 | 450.3012
2187.1135 | 450.6798 | 419.2495 | 405.1294 | 450.2357
2188.1135 | 450.6688 | 419.322 | 404.9942 | 449.9465
2189.1135 | 450.6284 | 419.2836 | 405.0967 | 449.4115
2190.1135 | 450.5523 | 419.3074 | 405.1867 | 449.6147
2191.1135 | 450.5593 | 419.3529 | 405.2485 | 449.7476
2192.1135 | 450.519 | 419.3644 | 405.401 | 449.1264
2193.1135 | 450.4626 | 419.3914 | 405.4721 | 449.8305
2194.1135 | 450.3903 | 419.4113 | 405.4964 | 449.1692
2195.1135 | 450.3965 | 419.3848 | 405.5508 | 449.2476
2196.1135 | 450.3775 | 419.4319 | 405.4429 | 449.3473
2197.1135 | 450.3774 | 419.4603 | 405.5387 | 449.51
2198.1135 | 450.2896 | 419.5001 | 405.5871 | 449.9315
2199.1135 | 450.2913 | 419.4653 | 405.5188 | 450.266
2200.1135 | 450.3082 | 419.4948 | 405.6008 | 450.4093
2201.1135 | 450.2366 | 419.5388 | 405.6162 | 450.1188
2202.1135 | 450.1351 | 419.5006 | 405.6696 | 450.0195
2203.1135 | 450.0986 | 419.4127 | 405.6958 | 449.9515
2204.1135 | 450.065 | 419.4777 | 405.6984 | 449.8833
2205.1135 | 450.0547 | 419.5194 | 405.7606 | 449.9104
2206.1135 | 450.0158 | 419.5656 | 405.7839 | 450.1531
2207.1135 | 450.0037 | 419.5935 | 405.85 | 450.3924
2208.1135 | 449.995 | 419.5693 | 405.8651 | 450.5211
2209.1135 | 449.991 | 419.6245 | 405.9193 | 449.9346
2210.1135 | 449.9377 | 419.6304 | 405.9151 | 450.0931
2211.1135 | 449.9963 | 419.6132 | 405.7508 | 449.6581
2212.1135 | 450.0318 | 419.633 | 405.7587 | 448.9762
2213.1135 | 450.0905 | 419.6941 | 405.9037 | 448.9563
2214.1135 | 450.1057 | 419.7912 | 405.9159 | 449.1969
2215.1135 | 450.0802 | 419.8147 | 405.9056 | 449.3887
2216.1135 | 450.0965 | 419.7928 | 405.9783 | 449.8258
2217.1135 | 450.1462 | 419.7663 | 405.9521 | 449.8045
2218.1135 | 450.1107 | 419.7992 | 406.1014 | 448.7731
2219.1135 | 450.1495 | 419.8286 | 406.1827 | 448.5313
2220.1135 | 450.182 | 419.8198 | 406.1744 | 449.2902
2221.1135 | 450.1825 | 419.8383 | 406.1024 | 448.5794
2222.1135 | 450.0919 | 419.8488 | 406.0667 | 448.689
2223.1135 | 450.0576 | 419.8167 | 406.0765 | 447.8908
2224.1135 | 450.0032 | 419.8177 | 406.0215 | 447.5482
2225.1135 | 449.9928 | 419.7974 | 406.0016 | 447.7803
2226.1135 | 449.9771 | 419.8334 | 406.0736 | 448.0202
2227.1135 | 449.9379 | 419.896 | 406.1427 | 448.4575
2228.1135 | 449.9591 | 419.884 | 406.2237 | 448.577
2229.1135 | 449.9613 | 419.9409 | 406.0858 | 447.9374
2230.1135 | 449.9885 | 419.9613 | 406.171 | 448.5174
2231.1135 | 449.937 | 419.9875 | 406.1872 | 448.436
2232.1135 | 449.9189 | 419.9461 | 406.1834 | 448.4895
2233.1135 | 449.9652 | 419.9516 | 406.1656 | 448.4866
2234.1135 | 449.9446 | 420.0121 | 406.2104 | 448.4488
2235.1135 | 449.9519 | 420.097 | 406.2384 | 447.6667
2236.1135 | 450.0005 | 420.1414 | 406.3214 | 447.3734
2237.1135 | 450.045 | 420.1988 | 406.3154 | 446.9416
2238.1135 | 450.0389 | 420.1691 | 406.2303 | 446.6732
2239.1135 | 450.0118 | 420.1312 | 406.2276 | 446.4485
2240.1135 | 449.9841 | 420.0581 | 406.2525 | 446.7948
2241.1135 | 449.9839 | 420.0965 | 406.2436 | 446.989
2242.1135 | 449.9567 | 420.1155 | 406.2529 | 446.7999
2243.1135 | 449.9518 | 420.1263 | 406.2207 | 446.8044
2244.1135 | 449.9331 | 420.1916 | 406.2972 | 446.8157
2245.1135 | 449.8963 | 420.1985 | 406.2828 | 446.5714
2246.1135 | 449.8411 | 420.2331 | 406.3182 | 446.7937
2247.1135 | 449.8785 | 420.2671 | 406.2752 | 446.644
2248.1135 | 449.9211 | 420.3545 | 406.4017 | 446.4383
2249.1135 | 449.8405 | 420.3774 | 406.4921 | 446.1486
2250.1135 | 449.7638 | 420.3628 | 406.5209 | 446.1794
2251.1135 | 449.7808 | 420.298 | 406.4168 | 446.279
2252.1135 | 449.794 | 420.3586 | 406.4338 | 445.7842
2253.1135 | 449.8091 | 420.3046 | 406.4645 | 445.4484
2254.1135 | 449.793 | 420.3443 | 406.477 | 445.4363
2255.1135 | 449.8121 | 420.3615 | 406.4794 | 445.795
2256.1135 | 449.8026 | 420.2917 | 406.5083 | 445.6263
2257.1135 | 449.7999 | 420.2926 | 406.4792 | 445.3429
2258.1135 | 449.8531 | 420.3494 | 406.5153 | 444.6488
2259.1135 | 449.8769 | 420.3394 | 406.4615 | 444.4775
2260.1135 | 449.9883 | 420.3115 | 406.5214 | 444.1096
2261.1135 | 450.0005 | 420.365 | 406.4964 | 443.7233
2262.1135 | 450.0582 | 420.3427 | 406.6606 | 443.9401
2263.1135 | 450.1375 | 420.3803 | 406.6267 | 444.1582
2264.1135 | 450.1808 | 420.368 | 406.664 | 444.5964
2265.1135 | 450.1205 | 420.3851 | 406.6956 | 444.4097
2266.1135 | 450.1918 | 420.3736 | 406.75 | 444.2652
2267.1135 | 450.2105 | 420.381 | 406.7901 | 443.8309
2268.1135 | 450.2306 | 420.426 | 406.7894 | 443.8394
2269.1135 | 450.2046 | 420.4268 | 406.9076 | 443.9651
2270.1135 | 450.1145 | 420.4827 | 406.9779 | 443.9946
2271.1135 | 450.1131 | 420.494 | 406.6743 | 443.7185
2272.1135 | 450.1536 | 420.5194 | 406.7517 | 444.1229
2273.1135 | 450.1886 | 420.572 | 406.7728 | 443.9779
2274.1135 | 450.2435 | 420.5916 | 406.7617 | 443.438
2275.1135 | 450.2658 | 420.5932 | 406.7498 | 443.0084
2276.1135 | 450.2056 | 420.5881 | 406.7385 | 443.1098
2277.1135 | 450.2441 | 420.6247 | 406.7637 | 442.8299
2278.1135 | 450.2814 | 420.7591 | 406.8907 | 442.9391
2279.1135 | 450.2412 | 420.7185 | 406.9078 | 442.9992
2280.1135 | 450.1793 | 420.6875 | 406.8951 | 443.3121
2281.1135 | 450.1144 | 420.7208 | 406.7971 | 443.3992
2282.1135 | 449.9326 | 420.6992 | 406.8226 | 443.7342
2283.1135 | 449.8831 | 420.6989 | 406.8146 | 443.2693
2284.1135 | 449.8383 | 420.7433 | 406.9034 | 443.0584
2285.1135 | 449.8927 | 420.7554 | 406.9916 | 443.1947
2286.1135 | 449.8638 | 420.7679 | 406.9698 | 442.9248
2287.1135 | 449.6934 | 420.7891 | 406.9418 | 442.5866
2288.1135 | 449.5821 | 420.7687 | 407.0381 | 443.1343
2289.1135 | 449.5906 | 420.7754 | 407.0995 | 442.8619
2290.1135 | 449.6119 | 420.8183 | 407.0704 | 442.7696
2291.1135 | 449.6302 | 420.8144 | 407.0275 | 442.6941
2292.1135 | 449.6508 | 420.843 | 406.9439 | 442.3031
2293.1135 | 449.6435 | 420.8331 | 407.0679 | 442.0018
2294.1135 | 449.6194 | 420.8 | 407.1764 | 442.1279
2295.1135 | 449.595 | 420.859 | 407.2694 | 442.0591
2296.1135 | 449.6128 | 420.9373 | 407.2624 | 441.6253
2297.1135 | 449.6408 | 420.9205 | 407.2209 | 441.6805
2298.1135 | 449.7382 | 420.9326 | 407.2407 | 441.7449
2299.1135 | 449.7567 | 420.9663 | 407.221 | 442.2482
2300.1135 | 449.7995 | 420.9727 | 407.1715 | 442.7084
2301.1135 | 449.8035 | 420.9958 | 407.1474 | 442.7144
2302.1448 | 449.7719 | 421.0151 | 407.1665 | 441.6708
2303.1135 | 449.7598 | 421.076 | 407.182 | 442.2174
2304.1135 | 449.8203 | 421.0753 | 407.1381 | 441.8423
2305.1135 | 449.8266 | 420.9701 | 407.2194 | 441.7693
2306.1135 | 449.8124 | 420.9807 | 407.1327 | 441.5282
2307.1135 | 449.7528 | 421.0654 | 407.1048 | 440.9898
2308.1135 | 449.8301 | 421.0576 | 407.1778 | 440.5151
2309.1135 | 449.7991 | 421.0543 | 407.1841 | 440.5969
2310.1135 | 449.7638 | 421.0732 | 407.1669 | 440.7726
2311.1135 | 449.7066 | 421.116 | 407.0959 | 440.9603
2312.1135 | 449.6901 | 421.1377 | 407.1452 | 440.1631
2313.1135 | 449.7082 | 421.1392 | 407.2374 | 440.1632
2314.1135 | 449.7449 | 421.1142 | 407.2503 | 439.9742
2315.1135 | 449.8627 | 421.1732 | 407.4092 | 440.5564
2316.1135 | 449.9377 | 421.1318 | 407.5566 | 440.3976
2317.1135 | 449.9114 | 421.1249 | 407.626 | 440.3865
2318.1135 | 449.9144 | 421.1129 | 407.6361 | 440.0949
2319.1135 | 449.9147 | 421.0994 | 407.59 | 440.1686
2320.1135 | 449.895 | 421.0734 | 407.3924 | 439.9029
2321.1135 | 449.8531 | 421.1837 | 407.4001 | 439.4217
2322.1135 | 449.8213 | 421.2344 | 407.4601 | 439.6231
2323.1135 | 449.8671 | 421.2292 | 407.4836 | 439.7994
2324.1135 | 449.9238 | 421.2369 | 407.514 | 439.5846
2325.1135 | 449.9811 | 421.2198 | 407.5157 | 439.9341
2326.1135 | 450.0513 | 421.1612 | 407.5023 | 439.6318
2327.1135 | 449.9782 | 421.2493 | 407.5484 | 439.103
2328.1135 | 449.8812 | 421.2874 | 407.5839 | 438.8349
2329.1135 | 449.9306 | 421.2963 | 407.5594 | 439.0003
2330.1135 | 450.0893 | 421.2774 | 407.5315 | 439.1765
2331.1135 | 450.1675 | 421.3153 | 407.4933 | 439.3174
2332.1135 | 450.2164 | 421.3517 | 407.5418 | 439.7884
2333.1135 | 450.271 | 421.3579 | 407.6787 | 439.1517
2334.1135 | 450.3192 | 421.3586 | 407.6692 | 438.9242
2335.1135 | 450.3328 | 421.4555 | 407.6533 | 439.3133
2336.1135 | 450.4157 | 421.4741 | 407.5938 | 439.2312
2337.1135 | 450.5051 | 421.5197 | 407.4702 | 439.2946
2338.1135 | 450.5364 | 421.4332 | 407.6298 | 439.1872
2339.1135 | 450.5249 | 421.4499 | 407.5919 | 439.0025
2340.1135 | 450.4541 | 421.4748 | 407.6664 | 439.1144
2341.1135 | 450.3951 | 421.452 | 407.6796 | 439.006
2342.1135 | 450.3622 | 421.5156 | 407.7241 | 439.1688
2343.1135 | 450.3788 | 421.5598 | 407.8414 | 439.0286
2344.1135 | 450.3371 | 421.5822 | 407.7898 | 438.3488
2345.1135 | 450.3071 | 421.6063 | 407.8437 | 438.4261
2346.1135 | 450.2248 | 421.5666 | 407.7814 | 438.6715
2347.1135 | 450.1735 | 421.5772 | 407.8176 | 438.4658
2348.1135 | 450.1412 | 421.6397 | 407.8674 | 438.0168
2349.1135 | 450.1272 | 421.6598 | 407.8691 | 437.9306
2350.1135 | 450.1704 | 421.645 | 407.806 | 438.1368
2351.1135 | 450.1204 | 421.6739 | 407.8025 | 438.2619
2352.1135 | 450.1175 | 421.6326 | 407.8522 | 437.9572
2353.1135 | 450.1483 | 421.6194 | 407.8449 | 437.6676
2354.1135 | 450.1153 | 421.6207 | 407.8509 | 437.7531
2355.1135 | 450.1517 | 421.6386 | 407.8264 | 437.9721
2356.1135 | 450.1315 | 421.6705 | 407.7819 | 437.6615
2357.1135 | 450.1541 | 421.6893 | 407.8027 | 437.5775
2358.1135 | 450.168 | 421.689 | 407.3849 | 437.6347
2359.1135 | 450.0937 | 421.5904 | 407.607 | 437.539
2360.1135 | 449.9962 | 421.6083 | 407.5767 | 437.6001
2361.1135 | 449.965 | 421.604 | 407.6588 | 437.5006
2362.1135 | 449.9302 | 421.6719 | 407.7528 | 437.3744
2363.1135 | 449.8713 | 421.7028 | 407.7772 | 437.646
2364.1135 | 449.8268 | 421.7711 | 407.7847 | 437.7182
2365.1135 | 449.8557 | 421.7558 | 407.6608 | 437.5211
2366.1135 | 449.8842 | 421.8146 | 407.6559 | 437.6283
2367.1135 | 449.8535 | 421.7852 | 407.6885 | 437.5149
2368.1135 | 449.8579 | 421.7992 | 407.6987 | 437.009
2369.1135 | 449.8262 | 421.8154 | 407.8226 | 436.8391
2370.1135 | 449.8187 | 421.857 | 407.7834 | 436.9441
2371.1135 | 449.7556 | 421.8718 | 407.9004 | 436.6815
2372.1135 | 449.689 | 421.8315 | 407.8297 | 436.3236
2373.1135 | 449.6813 | 421.8346 | 407.8755 | 436.0594
2374.1135 | 449.7265 | 421.9039 | 407.9463 | 435.9769
2375.1135 | 449.6779 | 421.8722 | 407.9136 | 435.7573
2376.1135 | 449.6018 | 421.7878 | 407.8209 | 435.8711
2377.1135 | 449.535 | 421.8476 | 407.9275 | 435.8662
2378.1135 | 449.601 | 421.9151 | 407.9516 | 435.9858
2379.1135 | 449.7076 | 421.9098 | 408.0109 | 436.0974
2380.1135 | 449.7554 | 421.9597 | 408.0094 | 436.1946
2381.1135 | 449.7668 | 422.0052 | 408.0878 | 435.7068
2382.1135 | 449.703 | 422.0221 | 408.1034 | 435.8975
2383.1135 | 449.7371 | 422.0301 | 408.1319 | 435.5606
2384.1135 | 449.7553 | 422.0708 | 408.0978 | 435.4935
2385.1135 | 449.713 | 422.0184 | 408.2334 | 435.7775
2386.1135 | 449.647 | 422.0327 | 408.2924 | 435.9892
2387.1135 | 449.6472 | 421.9901 | 408.1999 | 435.6009
2388.1135 | 449.7144 | 421.9872 | 408.0949 | 435.6975
2389.1135 | 449.7955 | 421.9331 | 408.1866 | 435.6915
2390.1135 | 449.8396 | 421.9634 | 408.2359 | 435.7258
2391.1135 | 449.8905 | 422.0648 | 408.201 | 435.4936
2392.1135 | 449.9443 | 422.0508 | 408.128 | 435.2914
2393.1135 | 449.9474 | 422.0446 | 408.1828 | 435.1654
2394.1135 | 449.9198 | 422.1032 | 408.0181 | 434.9748
2395.1135 | 449.861 | 422.1259 | 408.0284 | 434.8655
2396.1135 | 449.8802 | 422.1177 | 408.23 | 434.8997
2397.1135 | 449.8445 | 422.1194 | 408.3193 | 434.599
2398.1135 | 449.8028 | 422.1358 | 408.2538 | 434.8594
2399.1135 | 449.8495 | 422.0972 | 408.2463 | 435.3022
2400.1135 | 449.8886 | 422.156 | 408.2915 | 434.925
2401.1135 | 450.0078 | 422.1912 | 408.2943 | 434.7717
2402.1135 | 450.0705 | 422.1713 | 408.3364 | 435.0131
2403.1135 | 450.1183 | 422.1403 | 408.3679 | 434.628
2404.1135 | 450.1317 | 422.1472 | 408.4034 | 434.8488
2405.1135 | 450.1408 | 422.1655 | 408.2093 | 434.7727
2406.1135 | 450.1065 | 422.1631 | 408.3862 | 434.895
2407.1135 | 450.1033 | 422.2582 | 408.431 | 434.7554
2408.1135 | 450.1514 | 422.2145 | 408.4521 | 434.5811
2409.1135 | 450.1462 | 422.2442 | 408.504 | 434.0214
2410.1135 | 450.1572 | 422.3337 | 408.4386 | 434.4993
2411.1135 | 450.1856 | 422.3377 | 408.4862 | 434.6553
2412.1135 | 450.2169 | 422.2725 | 408.462 | 434.5608
2413.1135 | 450.1251 | 422.3451 | 408.4332 | 434.0203
2414.1135 | 450.1033 | 422.4099 | 408.4674 | 434.0965
2415.1135 | 450.1036 | 422.4508 | 408.4721 | 434.0827
2416.1135 | 450.1721 | 422.4015 | 408.5287 | 433.9689
2417.1135 | 450.0534 | 422.3742 | 408.5199 | 433.8067
2418.1135 | 450.0188 | 422.3096 | 408.5445 | 433.9862
2419.1135 | 449.9983 | 422.3532 | 408.5911 | 433.8883
2420.1135 | 450.0474 | 422.3562 | 408.6027 | 434.138
2421.1135 | 450.1281 | 422.3889 | 408.599 | 434.0097
2422.1135 | 450.1359 | 422.4461 | 408.5747 | 434.0177
2423.1135 | 450.174 | 422.5048 | 408.6045 | 433.6203
2424.1135 | 450.1591 | 422.5053 | 408.6646 | 433.6879
2425.1135 | 450.1534 | 422.4184 | 408.6625 | 433.4973
2426.1135 | 450.1216 | 422.4012 | 408.6492 | 433.5958
2427.1135 | 450.0391 | 422.4392 | 408.587 | 433.4626
2428.1135 | 449.9358 | 422.4433 | 408.5984 | 433.2555
2429.1135 | 449.8709 | 422.4537 | 408.7146 | 433.1183
2430.1135 | 449.9396 | 422.4818 | 408.7344 | 433.5712
2431.1135 | 450.0124 | 422.5037 | 408.7681 | 433.2747
2432.1135 | 450.0349 | 422.5245 | 408.7732 | 432.9051
2433.1135 | 450.0195 | 422.5108 | 408.8276 | 432.7753
2434.1135 | 449.966 | 422.4888 | 408.871 | 433.0192
2435.1135 | 449.9991 | 422.5267 | 408.9232 | 433.398
2436.1135 | 450.1038 | 422.5092 | 408.9754 | 433.4985
2437.1135 | 450.1867 | 422.5709 | 409.023 | 433.1028
2438.1135 | 450.2844 | 422.5832 | 409.0778 | 432.961
2439.1135 | 450.3503 | 422.6503 | 408.9764 | 432.8141
2440.1135 | 450.4595 | 422.5941 | 408.9296 | 432.7135
2441.1135 | 450.567 | 422.7248 | 408.969 | 432.8051
2442.1135 | 450.6397 | 422.7518 | 409.096 | 432.8343
2443.1135 | 450.756 | 422.718 | 409.0755 | 432.7876
2444.1135 | 450.8266 | 422.6992 | 409.0778 | 432.8582
2445.1135 | 450.8448 | 422.6894 | 409.1608 | 432.8013
2446.1135 | 450.7688 | 422.7679 | 409.0324 | 432.9181
2447.1135 | 450.6335 | 422.7782 | 408.9668 | 432.4498
2448.1135 | 450.6349 | 422.7546 | 408.7585 | 432.7229
2449.1135 | 450.7022 | 422.7814 | 408.8946 | 432.5043
2450.1135 | 450.7307 | 422.8162 | 408.9486 | 432.891
2451.1135 | 450.7102 | 422.8011 | 408.9435 | 432.6969
2452.1135 | 450.5985 | 422.8488 | 408.97 | 432.7115
2453.1135 | 450.56 | 422.8551 | 409.0275 | 432.5797
2454.1135 | 450.5506 | 422.8461 | 409.0686 | 432.0093
2455.1135 | 450.4886 | 422.8905 | 409.1677 | 432.1643
2456.1135 | 450.4604 | 422.8751 | 409.1449 | 432.2366
2457.1135 | 450.5386 | 422.8823 | 409.1683 | 431.9982
2458.1135 | 450.5598 | 422.8601 | 409.0568 | 432.2962
2459.1135 | 450.4977 | 422.9016 | 409.0789 | 432.0288
2460.1135 | 450.4762 | 422.8628 | 409.1659 | 432.0923
2461.1135 | 450.5523 | 422.9287 | 409.2383 | 431.5941
2462.1135 | 450.5715 | 423.0257 | 409.3499 | 431.6347
2463.1135 | 450.5577 | 423.0595 | 409.3024 | 431.4976
2464.1135 | 450.4198 | 423.0232 | 409.3632 | 431.722
2465.1135 | 450.3865 | 422.9492 | 409.4147 | 431.6024
2466.1135 | 450.2519 | 422.9671 | 409.4126 | 431.9415
2467.1135 | 450.2002 | 422.96 | 409.303 | 431.9389
2468.1135 | 450.1827 | 422.9548 | 409.1945 | 431.8781
2469.1135 | 450.1662 | 422.9924 | 409.2556 | 431.9656
2470.1135 | 450.1828 | 422.9806 | 409.2466 | 432.3369
2471.1135 | 450.1709 | 422.9949 | 409.3051 | 431.9998
2472.1135 | 450.1607 | 423.0573 | 409.2936 | 432.386
2473.1135 | 450.1377 | 423.042 | 409.3277 | 432.2106
2474.1135 | 450.1081 | 423.0771 | 409.2496 | 432.2045
2475.1135 | 449.9926 | 423.1362 | 409.3186 | 431.9719
2476.1135 | 449.972 | 423.15 | 409.331 | 432.0709
2477.1135 | 449.9351 | 423.1295 | 409.4337 | 431.9746
2478.1135 | 450.0033 | 423.0532 | 409.4896 | 432.0661
2479.1135 | 450.0375 | 423.054 | 409.5762 | 431.7667
2480.1135 | 450.0873 | 423.1051 | 409.5315 | 431.8936
2481.1135 | 450.0512 | 423.086 | 409.4519 | 431.7157
2482.1135 | 450.0143 | 423.0639 | 409.3704 | 431.3906
2483.1135 | 450.0126 | 423.0755 | 409.4581 | 431.1901
2484.1135 | 449.9352 | 423.1225 | 409.4916 | 430.9423
2485.1135 | 449.9384 | 423.1853 | 409.4892 | 431.1892
2486.1135 | 450.0111 | 423.1736 | 409.5462 | 430.8503
2487.1135 | 450.0808 | 423.1621 | 409.5108 | 430.6418
2488.1135 | 450.0876 | 423.1566 | 409.3451 | 430.6676
2489.1135 | 450.111 | 423.1413 | 409.4353 | 430.477
2490.1135 | 450.1548 | 423.2425 | 409.6166 | 430.8234
2491.1135 | 450.322 | 423.2983 | 409.5577 | 430.6663
2492.1135 | 450.3859 | 423.3363 | 409.534 | 430.5857
2493.1135 | 450.3703 | 423.2879 | 409.5858 | 430.704
2494.1135 | 450.4019 | 423.2461 | 409.5991 | 430.6846
2495.1135 | 450.4196 | 423.3114 | 409.5744 | 430.3705
2496.1135 | 450.3518 | 423.2969 | 409.5595 | 430.5027
2497.1135 | 450.3405 | 423.2645 | 409.5372 | 430.3754
2498.1135 | 450.3999 | 423.2783 | 409.5828 | 430.4911
2499.1135 | 450.405 | 423.2752 | 409.6643 | 430.4874
2500.1135 | 450.4421 | 423.3327 | 409.4471 | 430.6017
2501.1135 | 450.4409 | 423.3739 | 409.4121 | 430.6046
2502.1135 | 450.4334 | 423.4083 | 409.4627 | 430.5583
2503.1135 | 450.3126 | 423.365 | 409.5343 | 430.501
2504.1135 | 450.3012 | 423.3151 | 409.6267 | 430.5162
2505.1135 | 450.3003 | 423.3525 | 409.6551 | 430.6113
2506.1135 | 450.2941 | 423.429 | 409.6618 | 430.4376
2507.1135 | 450.1333 | 423.4481 | 409.6722 | 430.066
2508.1135 | 450.027 | 423.4626 | 409.7961 | 429.9553
2509.1135 | 450.03 | 423.4659 | 409.7557 | 430.2057
2510.1135 | 450.0345 | 423.4789 | 409.708 | 430.721
2511.1135 | 450.0309 | 423.4379 | 409.6532 | 430.6524
2512.1135 | 449.9264 | 423.4626 | 409.6403 | 430.5021
2513.1135 | 449.8946 | 423.456 | 409.6754 | 430.1382
2514.1135 | 449.8984 | 423.4681 | 409.6354 | 430.0993
2515.1135 | 449.9436 | 423.4785 | 409.6862 | 430.2271
2516.1135 | 449.9644 | 423.511 | 409.7813 | 429.9169
2517.1135 | 449.9784 | 423.4921 | 409.8052 | 429.6822
2518.1135 | 449.979 | 423.4945 | 409.8342 | 430.113
2519.1135 | 449.9529 | 423.4868 | 409.8777 | 429.8896
2520.1135 | 449.9272 | 423.4644 | 409.888 | 429.925
2521.1135 | 449.9388 | 423.5221 | 409.9314 | 429.903
2522.1135 | 449.9684 | 423.6612 | 409.9221 | 430.044
2523.1135 | 449.9965 | 423.6945 | 409.7267 | 430.1176
2524.1135 | 450.0619 | 423.6882 | 409.5892 | 429.9468
2525.1135 | 450.1333 | 423.6708 | 409.674 | 429.9195
2526.1135 | 450.1803 | 423.6619 | 409.8323 | 430.0551
2527.1135 | 450.2679 | 423.684 | 409.9671 | 430.1242
2528.1135 | 450.3659 | 423.6243 | 410.0174 | 430.198
2529.1135 | 450.4449 | 423.6439 | 410.0589 | 429.9797
2530.1135 | 450.4665 | 423.717 | 409.9828 | 429.6895
2531.1135 | 450.4667 | 423.7548 | 409.9868 | 429.8904
2532.1135 | 450.5536 | 423.7238 | 409.9052 | 429.8672
2533.1135 | 450.5633 | 423.721 | 409.9405 | 429.4272
2534.1135 | 450.447 | 423.71 | 409.9455 | 429.297
2535.1135 | 450.5038 | 423.7069 | 410.0124 | 429.4719
2536.1135 | 450.5586 | 423.6779 | 409.8086 | 429.5563
2537.1135 | 450.5163 | 423.7688 | 409.8659 | 429.2278
2538.1135 | 450.5072 | 423.802 | 409.9637 | 429.4597
2539.1135 | 450.4623 | 423.8268 | 409.9838 | 429.2997
2540.1135 | 450.3762 | 423.8574 | 409.9714 | 429.2896
2541.1135 | 450.3312 | 423.8333 | 409.9933 | 429.5746
2542.1135 | 450.269 | 423.8295 | 410.047 | 429.1985
2543.1135 | 450.1811 | 423.8282 | 410.0946 | 429.2815
2544.1135 | 450.1462 | 423.8106 | 410.0842 | 429.2048
2545.1135 | 450.1344 | 423.8405 | 410.0546 | 429.3955
2546.1135 | 450.096 | 423.8286 | 410.0894 | 429.5013
2547.1135 | 450.1217 | 423.7813 | 410.0526 | 429.5778
2548.1135 | 450.1018 | 423.8384 | 409.8772 | 429.3462
2549.1135 | 450.0503 | 423.8719 | 409.9548 | 429.7068
2550.1135 | 449.9911 | 423.8847 | 410.0362 | 430.0793
2551.1135 | 449.9828 | 423.8706 | 410.0848 | 429.8526
2552.1135 | 450.0014 | 423.9135 | 410.0299 | 429.6915
2553.1135 | 450.0695 | 423.9604 | 410.1359 | 429.5866
2554.1135 | 450.0323 | 423.9623 | 410.1631 | 429.5048
2555.1135 | 450.0266 | 423.9455 | 410.1858 | 429.3571
2556.1135 | 449.9503 | 423.965 | 410.1902 | 429.1908
2557.1135 | 449.9961 | 424.037 | 410.2288 | 429.1397
2558.1135 | 449.9834 | 424.0909 | 410.2007 | 429.0083
2559.1135 | 449.9941 | 424.0613 | 410.214 | 428.672
2560.1135 | 450.038 | 424.0955 | 410.2445 | 429.2501
2561.1135 | 450.1099 | 424.0662 | 410.2939 | 428.6223
2562.1135 | 450.1765 | 424.0616 | 410.4343 | 428.6989
2563.1135 | 450.2464 | 424.1222 | 410.4029 | 428.5924
2564.1135 | 450.2807 | 424.0891 | 410.341 | 428.4263
2565.1135 | 450.2679 | 424.1521 | 410.3888 | 428.647
2566.1135 | 450.1477 | 424.1842 | 410.4374 | 428.3055
2567.1135 | 450.1068 | 424.2025 | 410.1546 | 428.2493
2568.1135 | 450.1228 | 424.1253 | 410.3299 | 428.2291
2569.1135 | 450.1818 | 424.1113 | 410.3353 | 428.0166
2570.1135 | 450.1704 | 424.1082 | 410.4222 | 428.1423
2571.1135 | 450.2096 | 424.1385 | 410.2064 | 428.1824
2572.1135 | 450.2261 | 424.1789 | 410.3125 | 427.8713
2573.1135 | 450.306 | 424.1917 | 410.4138 | 428.0261
2574.1135 | 450.3705 | 424.2108 | 410.4885 | 427.6593
2575.1135 | 450.3536 | 424.1761 | 410.481 | 427.9856
2576.1135 | 450.4459 | 424.1401 | 410.596 | 427.9954
2577.1135 | 450.485 | 424.17 | 410.5611 | 427.6903
2578.1135 | 450.5282 | 424.2324 | 410.6335 | 427.4885
2579.1135 | 450.5101 | 424.271 | 410.6165 | 427.7631
2580.1135 | 450.4531 | 424.2285 | 410.6023 | 427.8108
2581.1135 | 450.4475 | 424.2662 | 410.7576 | 427.5791
2582.1135 | 450.5103 | 424.2775 | 410.7529 | 427.4788
2583.1135 | 450.5165 | 424.2786 | 410.7466 | 427.7714
2584.1135 | 450.5156 | 424.2508 | 410.7521 | 427.5931
2585.1135 | 450.5576 | 424.2798 | 410.7809 | 427.7049
2586.1135 | 450.5319 | 424.3165 | 410.8019 | 427.8527
2587.1135 | 450.574 | 424.3303 | 410.532 | 427.592
2588.1135 | 450.6267 | 424.3249 | 410.6612 | 427.4495
2589.1135 | 450.5944 | 424.3718 | 410.6943 | 427.257
2590.1135 | 450.5165 | 424.3903 | 410.726 | 427.4568
2591.1135 | 450.4526 | 424.3284 | 410.6839 | 427.6778
2592.1135 | 450.3875 | 424.3795 | 410.7119 | 427.4931
2593.1135 | 450.3943 | 424.3357 | 410.7169 | 427.637
2594.1135 | 450.3062 | 424.3301 | 410.7801 | 427.3831
2595.1135 | 450.2166 | 424.3358 | 410.8364 | 427.4813
2596.1135 | 450.187 | 424.3456 | 410.8769 | 427.6228
2597.1135 | 450.2303 | 424.2869 | 410.8568 | 427.3948
2598.1135 | 450.2326 | 424.2905 | 410.8621 | 427.3985
2599.1135 | 450.2721 | 424.275 | 410.7937 | 427.3102
2600.1135 | 450.323 | 424.3165 | 410.7905 | 427.5471
2601.1135 | 450.3335 | 424.2729 | 410.6969 | 427.35
2602.1135 | 450.384 | 424.3296 | 410.7315 | 427.6274
2603.1135 | 450.4213 | 424.3402 | 410.818 | 427.6095
2604.1135 | 450.3777 | 424.4248 | 410.8394 | 427.469
2605.1135 | 450.4466 | 424.4579 | 410.8814 | 427.4807
2606.1135 | 450.4233 | 424.4679 | 410.934 | 427.5051
2607.1135 | 450.3895 | 424.4375 | 410.9331 | 427.3721
2608.1135 | 450.4409 | 424.433 | 410.8966 | 427.4235
2609.1135 | 450.4932 | 424.4621 | 410.8991 | 427.3272
2610.1135 | 450.4719 | 424.5336 | 410.9191 | 427.5225
2611.1135 | 450.426 | 424.5634 | 410.8709 | 427.8411
2612.1135 | 450.4653 | 424.5976 | 410.9631 | 428.2185
2613.1135 | 450.4486 | 424.5841 | 410.8556 | 427.8727
2614.1135 | 450.4682 | 424.6474 | 410.8558 | 428.0223
2615.1135 | 450.5747 | 424.6564 | 410.8622 | 427.9105
2616.1135 | 450.5991 | 424.6202 | 410.9294 | 427.7884
2617.1135 | 450.5129 | 424.5239 | 410.915 | 427.5152
2618.1135 | 450.5528 | 424.5478 | 411.0105 | 427.495
2619.1135 | 450.484 | 424.595 | 411.0298 | 427.2998
2620.1135 | 450.4134 | 424.623 | 410.9979 | 427.6809
2621.1135 | 450.4521 | 424.6726 | 410.9884 | 427.8835
2622.1135 | 450.5175 | 424.6957 | 411.0651 | 427.7637
2623.1135 | 450.473 | 424.7093 | 411.0386 | 427.616
2624.1135 | 450.4631 | 424.7274 | 410.8422 | 427.6795
2625.1135 | 450.5399 | 424.7145 | 410.8146 | 427.514
2626.1135 | 450.6079 | 424.7012 | 410.8667 | 427.6623
2627.1135 | 450.5134 | 424.7251 | 410.8538 | 427.6211
2628.1135 | 450.4593 | 424.7372 | 410.9598 | 427.6258
2629.1135 | 450.4037 | 424.7211 | 411.0562 | 427.8095
2630.1135 | 450.3915 | 424.7398 | 411.0757 | 427.8033
2631.1135 | 450.4224 | 424.7562 | 411.1182 | 427.3941
2632.1135 | 450.4383 | 424.7444 | 411.0942 | 427.3852
2633.1135 | 450.4854 | 424.6951 | 411.0607 | 427.5455
2634.1135 | 450.6187 | 424.7256 | 411.0533 | 427.7083
2635.1135 | 450.6385 | 424.7485 | 411.0666 | 427.9905
2636.1135 | 450.6467 | 424.8129 | 411.0991 | 428.0384
2637.1135 | 450.7037 | 424.8395 | 411.1167 | 427.9705
2638.1135 | 450.7687 | 424.8099 | 411.2582 | 428.059
2639.1135 | 450.7576 | 424.8566 | 411.2906 | 427.7591
2640.1135 | 450.7843 | 424.8283 | 411.2798 | 427.835
2641.1135 | 450.8555 | 424.8384 | 411.3411 | 427.7898
2642.1135 | 450.8874 | 424.8653 | 411.1586 | 427.7701
2643.1135 | 450.9279 | 424.8616 | 411.0739 | 428.0268
2644.1135 | 450.917 | 424.8771 | 411.0883 | 427.9703
2645.1135 | 450.8846 | 424.9033 | 411.1348 | 428.047
2646.1135 | 450.8401 | 424.8789 | 411.1399 | 428.2412
2647.1135 | 450.8289 | 424.9016 | 411.2789 | 428.2205
2648.1135 | 450.8136 | 424.9237 | 411.2728 | 428.3697
2649.1135 | 450.8362 | 424.9126 | 411.2619 | 428.1572
2650.1135 | 450.8608 | 424.9954 | 411.2272 | 428.2058
2651.1135 | 450.81 | 424.992 | 411.2939 | 428.2605
2652.1135 | 450.7837 | 425.0376 | 411.371 | 428.0756
2653.1135 | 450.7774 | 425.0202 | 411.4347 | 427.9563
2654.1135 | 450.7964 | 425.0044 | 411.5296 | 427.7451
2655.1135 | 450.7551 | 424.9891 | 411.4895 | 428.0512
2656.1135 | 450.7637 | 424.9997 | 411.4431 | 428.1028
2657.1135 | 450.7044 | 425.0105 | 411.3968 | 427.7195
2658.1135 | 450.6727 | 425.0387 | 411.4305 | 428.117
2659.1135 | 450.6282 | 425.0827 | 411.3422 | 428.0156
2660.1135 | 450.5578 | 425.0875 | 411.4582 | 428.4398
2661.1135 | 450.5562 | 425.0505 | 411.4015 | 428.2544
2662.1135 | 450.5641 | 425.0613 | 411.4536 | 428.1522
2663.1135 | 450.4693 | 425.02 | 411.518 | 428.0339
2664.1135 | 450.418 | 425.0152 | 411.4688 | 427.8203
2665.1135 | 450.413 | 425.0313 | 411.4986 | 428.1631
2666.1135 | 450.4231 | 425.0314 | 411.4182 | 428.0334
2667.1135 | 450.3952 | 425.0393 | 411.3968 | 427.7694
2668.1135 | 450.3699 | 425.0603 | 411.4781 | 428.1136
2669.1135 | 450.4115 | 425.0231 | 411.4013 | 427.9668
2670.1135 | 450.3559 | 425.0274 | 411.4321 | 428.4617
2671.1135 | 450.3063 | 425.0872 | 411.5541 | 428.4977
2672.1135 | 450.2737 | 425.1764 | 411.5588 | 428.2787
2673.1135 | 450.3703 | 425.0925 | 411.6348 | 428.2441
2674.1135 | 450.3712 | 425.0665 | 411.6664 | 428.1731
2675.1135 | 450.3145 | 425.0869 | 411.5187 | 428.2202
2676.1135 | 450.2737 | 425.1103 | 411.6092 | 428.1674
2677.1135 | 450.2832 | 425.1285 | 411.629 | 428.1176
2678.1135 | 450.2134 | 425.2067 | 411.6855 | 428.3052
2679.1135 | 450.0937 | 425.1896 | 411.7675 | 428.308
2680.1135 | 450.1173 | 425.2194 | 411.7004 | 428.3016
2681.1135 | 450.0951 | 425.229 | 411.609 | 428.3335
2682.1135 | 450.0629 | 425.2547 | 411.7239 | 428.2794
2683.1135 | 450.0486 | 425.2154 | 411.6658 | 428.2272
2684.1135 | 449.9593 | 425.1961 | 411.7218 | 428.2674
2685.1135 | 449.9493 | 425.1881 | 411.728 | 428.4821
2686.1135 | 449.9359 | 425.1537 | 411.6553 | 428.425
2687.1135 | 449.9345 | 425.2664 | 411.6463 | 428.411
2688.1135 | 449.9209 | 425.2741 | 411.7697 | 428.4466
2689.1135 | 449.9698 | 425.3037 | 411.8936 | 428.3517
2690.1135 | 449.8902 | 425.3136 | 411.9076 | 428.5808
2691.1135 | 449.8614 | 425.302 | 411.7683 | 428.4709
2692.1135 | 449.8026 | 425.2971 | 411.7109 | 428.6053
2693.1135 | 449.8059 | 425.3067 | 411.8197 | 428.5233
2694.1135 | 449.8361 | 425.2976 | 411.8857 | 428.3544
2695.1135 | 449.8311 | 425.2561 | 411.9048 | 428.6617
2696.1135 | 449.8334 | 425.2865 | 411.9134 | 428.3238
2697.1135 | 449.8526 | 425.2269 | 411.8351 | 428.317
2698.1135 | 449.9226 | 425.2783 | 411.8614 | 428.3139
2699.1135 | 449.9289 | 425.3242 | 411.9758 | 428.2141
2700.1135 | 449.9594 | 425.3594 | 411.9598 | 428.5278
2701.1135 | 449.8919 | 425.3418 | 411.9699 | 428.5232
2702.1135 | 449.894 | 425.3389 | 411.9235 | 428.7255
2703.1135 | 449.9586 | 425.3155 | 412.02 | 428.6688
2704.1135 | 449.9329 | 425.348 | 411.9861 | 428.3436
2705.1135 | 450.0505 | 425.3417 | 411.9412 | 428.6247
2706.1135 | 450.1015 | 425.3391 | 411.917 | 428.2956
2707.1135 | 450.1751 | 425.3688 | 412.0216 | 428.3983
2708.1135 | 450.223 | 425.4031 | 412.0672 | 428.2995
2709.1135 | 450.3055 | 425.4251 | 412.1649 | 428.2598
2710.1135 | 450.3475 | 425.2428 | 412.1612 | 428.4119
2711.1135 | 450.4235 | 425.3116 | 412.211 | 428.5858
2712.1135 | 450.4899 | 425.3214 | 411.8884 | 428.9824
2713.1135 | 450.5256 | 425.3076 | 411.9167 | 430.3776
2714.1135 | 450.5172 | 425.3255 | 412.1101 | 430.2742
2715.1135 | 450.4996 | 425.4014 | 411.7163 | 429.7424
2716.1135 | 450.5681 | 425.4181 | 411.7139 | 430.1322
2717.1135 | 450.588 | 425.4879 | 411.6847 | 430.354
2718.1135 | 450.5134 | 425.4772 | 411.7163 | 430.346
2719.1135 | 450.4151 | 425.4802 | 411.958 | 430.513
2720.1135 | 450.4469 | 425.4863 | 411.9984 | 430.5749
2721.1135 | 450.4708 | 425.456 | 412.0196 | 430.4562
2722.1135 | 450.4882 | 425.4858 | 411.955 | 430.5065
2723.1135 | 450.5474 | 425.555 | 412.0399 | 430.5592
2724.1135 | 450.5744 | 425.5809 | 412.1028 | 430.377
2725.1135 | 450.4943 | 425.5475 | 412.0568 | 430.7144
2726.1135 | 450.4969 | 425.5364 | 412.0702 | 431.0214
2727.1135 | 450.5101 | 425.5462 | 412.1015 | 430.9844
2728.1135 | 450.4569 | 425.5527 | 412.2762 | 431.0414
2729.1135 | 450.3897 | 425.5168 | 412.3203 | 430.9603
2730.1135 | 450.4434 | 425.5241 | 412.2532 | 430.9656
2731.1135 | 450.4107 | 425.5442 | 412.1759 | 431.127
2732.1135 | 450.4089 | 425.5031 | 412.2382 | 431.0859
2733.1135 | 450.4601 | 425.6157 | 412.1675 | 431.3728
2734.1135 | 450.4312 | 425.6629 | 412.1624 | 431.0303
2735.1135 | 450.4 | 425.6461 | 412.1497 | 431.5491
2736.1135 | 450.3808 | 425.6024 | 412.2877 | 431.3309
2737.1135 | 450.3758 | 425.6547 | 412.2884 | 431.3609
2738.1135 | 450.3752 | 425.6524 | 412.3759 | 431.6272
2739.1135 | 450.449 | 425.6868 | 412.384 | 431.6519
2740.1135 | 450.5712 | 425.6978 | 412.3948 | 431.6388
2741.1135 | 450.6341 | 425.7013 | 412.3859 | 431.7264
2742.1135 | 450.664 | 425.6975 | 412.3942 | 431.4695
2743.1135 | 450.6868 | 425.7056 | 412.4358 | 431.3461
2744.1135 | 450.7388 | 425.7468 | 412.392 | 431.5217
2745.1135 | 450.8707 | 425.6029 | 412.2995 | 431.5339
2746.1135 | 450.8743 | 425.6505 | 412.2204 | 431.7292
2747.1135 | 450.9493 | 425.7275 | 412.3811 | 431.7599
2748.1135 | 450.99 | 425.6615 | 412.2774 | 431.7726
2749.1135 | 450.9162 | 425.7658 | 412.3569 | 431.9616
2750.1135 | 450.9699 | 425.7717 | 412.4138 | 432.0032
2751.1135 | 451.0343 | 425.8864 | 412.3697 | 432.1168
2752.1135 | 451.0823 | 425.887 | 412.4711 | 431.7654
2753.1135 | 451.1256 | 425.8798 | 412.48 | 431.8207
2754.1135 | 451.1186 | 425.8693 | 412.5355 | 431.6917
2755.1135 | 451.0425 | 425.8812 | 412.5404 | 431.944
2756.1135 | 450.9907 | 425.8712 | 412.5259 | 431.7999
2757.1135 | 450.9705 | 425.8151 | 412.4456 | 431.9315
2758.1135 | 451.0172 | 425.8627 | 412.5002 | 431.825
2759.1135 | 451.094 | 425.8799 | 412.6145 | 432.0059
2760.1135 | 451.1289 | 425.9204 | 412.6027 | 432.1862
2761.1135 | 451.1242 | 425.9246 | 412.5909 | 432.3376
2762.1135 | 451.0805 | 425.9697 | 412.5908 | 432.1694
2763.1135 | 450.9833 | 425.9635 | 412.5824 | 432.2175
2764.1135 | 450.9686 | 425.916 | 412.4657 | 432.0807
2765.1135 | 450.9707 | 425.8941 | 412.5022 | 432.1353
2766.1135 | 450.991 | 425.903 | 412.6068 | 431.9159
2767.1135 | 450.9021 | 425.909 | 412.7002 | 432.1542
2768.1135 | 450.8969 | 425.8953 | 412.682 | 431.8796
2769.1135 | 450.7866 | 425.9142 | 412.5997 | 431.7316
2770.1135 | 450.6479 | 425.8969 | 412.6712 | 431.9053
2771.1135 | 450.5722 | 425.9411 | 412.5871 | 431.9172
2772.1135 | 450.4847 | 425.9362 | 412.7226 | 431.8422
2773.1135 | 450.4776 | 426.0353 | 412.8268 | 431.8074
2774.1135 | 450.3945 | 425.9886 | 412.7669 | 431.7933
2775.1135 | 450.3576 | 425.9476 | 412.7204 | 431.8516
2776.1135 | 450.3356 | 425.9563 | 412.7035 | 431.5692
2777.1135 | 450.3438 | 425.9575 | 412.7179 | 431.7724
2778.1135 | 450.2781 | 425.9613 | 412.7102 | 432.1461
2779.1135 | 450.2615 | 425.9884 | 412.7159 | 432.0381
2780.1135 | 450.2825 | 425.9968 | 412.7287 | 432.1722
2781.1135 | 450.254 | 426.0139 | 412.6344 | 432.2532
2782.1135 | 450.1995 | 425.9812 | 412.6813 | 432.0615
2783.1135 | 450.174 | 426.011 | 412.6385 | 431.9244
2784.1135 | 450.1583 | 426.0168 | 412.5494 | 432.0422
2785.1135 | 450.1783 | 426.0623 | 412.6236 | 432.188
2786.1135 | 450.2541 | 426.0309 | 412.7051 | 432.2279
2787.1135 | 450.2923 | 426.0642 | 412.8332 | 432.1042
2788.1135 | 450.3914 | 426.0926 | 412.8652 | 432.1948
2789.1135 | 450.4673 | 426.0671 | 412.8928 | 432.1622
2790.1135 | 450.556 | 426.1148 | 412.8825 | 432.3121
2791.1135 | 450.6065 | 426.1339 | 412.91 | 432.096
2792.1135 | 450.5611 | 426.1581 | 412.8669 | 432.2848
2793.1135 | 450.5825 | 426.1258 | 412.8305 | 432.3873
2794.1135 | 450.6059 | 426.17 | 412.7051 | 432.3831
2795.1135 | 450.6355 | 426.2094 | 412.7875 | 432.4551
2796.1135 | 450.7517 | 426.2229 | 412.6948 | 432.599
2797.1135 | 450.7839 | 426.1901 | 412.7999 | 432.5525
2798.1135 | 450.7774 | 426.1921 | 412.8574 | 432.3125
2799.1135 | 450.8569 | 426.1317 | 412.9502 | 432.321
2800.1135 | 450.9725 | 426.1865 | 412.9835 | 432.6512
2801.1135 | 451.0557 | 426.1926 | 413.0591 | 432.5687
2802.1135 | 451.1202 | 426.194 | 412.9493 | 432.3772
2803.1135 | 451.0868 | 426.2066 | 413.1087 | 432.2406
2804.1135 | 451.1009 | 426.2037 | 413.1202 | 432.6189
2805.1135 | 451.1597 | 426.1827 | 413.1232 | 432.7183
2806.1135 | 451.1883 | 426.1715 | 413.081 | 432.6262
2807.1135 | 451.2203 | 426.2127 | 413.0652 | 432.6974
2808.1135 | 451.225 | 426.2098 | 412.9588 | 432.6686
2809.1135 | 451.2495 | 426.1978 | 413.0018 | 432.5951
2810.1135 | 451.1488 | 426.2398 | 412.9404 | 432.6033
2811.1135 | 451.1755 | 426.2303 | 413.0188 | 432.6267
2812.1135 | 451.1709 | 426.2837 | 412.9857 | 432.6258
2813.1135 | 451.1147 | 426.2671 | 412.8976 | 432.4479
2814.1135 | 451.1225 | 426.2346 | 412.7767 | 432.6645
2815.1135 | 451.1318 | 426.2787 | 412.8594 | 432.5549
2816.1135 | 451.0927 | 426.2639 | 412.88 | 432.7535
2817.1135 | 451.076 | 426.3241 | 412.8915 | 432.6783
2818.1135 | 450.9988 | 426.3093 | 412.9593 | 432.8819
2819.1135 | 450.9483 | 426.322 | 412.9813 | 432.7444
2820.1135 | 450.9923 | 426.4052 | 413.042 | 432.8985
2821.1135 | 451.0051 | 426.4539 | 413.0985 | 433.0354
2822.1135 | 450.994 | 426.4039 | 413.1529 | 433.0066
2823.1135 | 450.9712 | 426.4212 | 413.2076 | 433.096
2824.1135 | 451.0168 | 426.432 | 413.181 | 433.047
2825.1135 | 450.9737 | 426.4287 | 413.1669 | 432.9752
2826.1135 | 450.8827 | 426.3902 | 413.1104 | 433.2611
2827.1135 | 450.8998 | 426.3464 | 412.9478 | 433.282
2828.1135 | 450.8621 | 426.3472 | 413.154 | 433.3595
2829.1135 | 450.7993 | 426.3589 | 413.1881 | 433.0653
2830.1135 | 450.7725 | 426.3991 | 413.287 | 433.1109
2831.1135 | 450.7993 | 426.414 | 413.3355 | 433.3623
2832.1135 | 450.822 | 426.4314 | 413.1586 | 433.4177
2833.1135 | 450.7455 | 426.4508 | 413.1655 | 433.3719
2834.1135 | 450.7485 | 426.4297 | 413.2518 | 433.3033
2835.1135 | 450.7053 | 426.4206 | 413.2555 | 433.2907
2836.1135 | 450.6044 | 426.5013 | 413.2688 | 433.2272
2837.1135 | 450.5955 | 426.5339 | 413.2538 | 433.354
2838.1135 | 450.5819 | 426.4788 | 413.1374 | 433.5134
2839.1135 | 450.6096 | 426.4106 | 413.0872 | 433.4102
2840.1135 | 450.5589 | 426.4937 | 413.218 | 433.2845
2841.1135 | 450.5571 | 426.4857 | 413.2371 | 433.4603
2842.1135 | 450.4837 | 426.5076 | 413.3314 | 433.3538
2843.1135 | 450.4299 | 426.5313 | 413.2771 | 433.4872
2844.1135 | 450.4704 | 426.5477 | 413.2536 | 433.5616
2845.1135 | 450.4191 | 426.5502 | 413.2675 | 433.7063
2846.1135 | 450.3817 | 426.5484 | 413.3049 | 433.7226
2847.1135 | 450.3313 | 426.5847 | 413.4123 | 433.4846
2848.1135 | 450.3386 | 426.5947 | 413.4507 | 433.7255
2849.1135 | 450.3633 | 426.6107 | 413.3936 | 433.7662
2850.1135 | 450.3503 | 426.631 | 413.3605 | 433.6617
2851.1135 | 450.3435 | 426.6218 | 413.4147 | 433.7852
2852.1135 | 450.3889 | 426.5935 | 413.4937 | 433.5729
2853.1135 | 450.4025 | 426.5997 | 413.492 | 433.6439
2854.1135 | 450.4186 | 426.6031 | 413.4607 | 433.8016
2855.1135 | 450.4113 | 426.5491 | 413.4032 | 433.5441
2856.1135 | 450.4713 | 426.5643 | 413.401 | 433.4581
2857.1135 | 450.5357 | 426.5125 | 413.2594 | 433.4578
2858.1135 | 450.4716 | 426.5724 | 413.4038 | 433.571
2859.1135 | 450.4599 | 426.6043 | 413.4567 | 433.6237
2860.1135 | 450.4916 | 426.6339 | 413.4552 | 434.1038
2861.1135 | 450.5693 | 426.54 | 413.5993 | 433.9942
2862.1135 | 450.5826 | 426.558 | 413.5474 | 433.9685
2863.1135 | 450.4859 | 426.5753 | 413.5609 | 433.8208
2864.1135 | 450.4636 | 426.6188 | 413.6749 | 433.7485
2865.1135 | 450.3976 | 426.5888 | 413.5981 | 433.5217
2866.1135 | 450.3292 | 426.6094 | 413.3211 | 433.5203
2867.1135 | 450.2539 | 426.6438 | 413.3544 | 433.5294
2868.1135 | 450.1116 | 426.7261 | 413.5197 | 433.5607
2869.1135 | 450.0684 | 426.7207 | 413.544 | 433.6357
2870.1135 | 450.0782 | 426.7586 | 413.46 | 433.7341
2871.1135 | 450.0321 | 426.7575 | 413.5338 | 433.655
2872.1135 | 450.0632 | 426.8097 | 413.5347 | 433.6348
2873.1135 | 450.0086 | 426.788 | 413.4658 | 433.9189
2874.1135 | 449.966 | 426.7315 | 413.4078 | 433.7956
2875.1135 | 449.9959 | 426.7113 | 413.417 | 433.7359
2876.1135 | 450.0341 | 426.7191 | 413.5991 | 434.1197
2877.1135 | 450.0239 | 426.8275 | 413.5492 | 433.9323
2878.1135 | 449.9557 | 426.8299 | 413.575 | 433.9275
2879.1135 | 449.9929 | 426.7806 | 413.5743 | 433.9817
2880.1135 | 450.0571 | 426.767 | 413.6006 | 434.0148
2881.1135 | 450.0713 | 426.7896 | 413.5788 | 434.0822
2882.1135 | 450.0931 | 426.8014 | 413.6772 | 434.295
2883.1135 | 450.1169 | 426.7715 | 413.7329 | 434.3159
2884.1135 | 450.0689 | 426.7951 | 413.764 | 434.371
2885.1135 | 450.0879 | 426.7941 | 413.7592 | 434.6315
2886.1135 | 450.1158 | 426.7952 | 413.6654 | 434.598
2887.1135 | 450.1672 | 426.7993 | 413.6158 | 434.1351
2888.1135 | 450.1318 | 426.8263 | 413.5712 | 434.2275
2889.1135 | 450.1284 | 426.8398 | 413.6388 | 434.1353
2890.1135 | 450.1517 | 426.8243 | 413.6869 | 434.3226
2891.1135 | 450.1839 | 426.8318 | 413.68 | 434.3694
2892.1135 | 450.2174 | 426.822 | 413.6447 | 434.3873
2893.1135 | 450.3144 | 426.8422 | 413.7716 | 434.1691
2894.1135 | 450.3962 | 426.8413 | 413.8466 | 434.2694
2895.1135 | 450.4522 | 426.8623 | 413.832 | 434.3372
2896.1135 | 450.4248 | 426.9205 | 413.7871 | 434.3027
2897.1135 | 450.4689 | 426.9677 | 413.8535 | 434.3365
2898.1292 | 450.506 | 426.9181 | 413.7876 | 434.3104
2899.1135 | 450.5678 | 426.9777 | 413.7829 | 434.9004
2900.1135 | 450.6022 | 426.9957 | 413.7678 | 434.7196
2901.1135 | 450.6305 | 426.9723 | 413.7635 | 434.6366
2902.1135 | 450.6197 | 426.9566 | 413.851 | 435.0095
2903.1135 | 450.6389 | 426.9974 | 413.8844 | 434.7267
2904.1135 | 450.6712 | 427.047 | 413.8728 | 434.4884
2905.1135 | 450.7364 | 427 | 413.9128 | 434.7053
2906.1135 | 450.7413 | 427.0302 | 413.9272 | 434.9674
2907.1135 | 450.7699 | 426.9498 | 413.8169 | 434.8044
2908.1135 | 450.8653 | 426.982 | 413.7301 | 434.7374
2909.1135 | 450.9433 | 426.967 | 413.6995 | 434.7613
2910.1135 | 450.9504 | 426.9706 | 413.824 | 435.6624
2911.1135 | 450.8785 | 426.9842 | 413.8275 | 435.8267
2912.1135 | 450.9009 | 426.9766 | 413.7511 | 435.9351
2913.1135 | 450.9066 | 427.0175 | 413.7328 | 435.2801
2914.1135 | 450.9532 | 427.043 | 413.8654 | 435.181
2915.1135 | 451.0054 | 427.0742 | 413.8297 | 435.1721
2916.1135 | 450.9382 | 427.0634 | 413.8376 | 435.1423
2917.1292 | 450.9064 | 427.0372 | 413.9247 | 435.374
2918.1135 | 450.9711 | 426.9754 | 413.9239 | 435.7641
2919.1135 | 450.9081 | 426.9796 | 414.0193 | 435.2998
2920.1135 | 450.9382 | 426.9964 | 414.0708 | 435.4276
2921.1135 | 450.8895 | 427.0505 | 414.0836 | 435.3372
2922.1135 | 450.7826 | 427.0994 | 413.9542 | 435.2848
2923.1135 | 450.7416 | 427.0873 | 413.9858 | 435.5331
2924.1135 | 450.7358 | 427.0788 | 413.9324 | 435.4201
2925.1135 | 450.7158 | 427.0953 | 413.9201 | 435.9096
2926.1135 | 450.689 | 427.1368 | 414.0413 | 435.9333
2927.1135 | 450.7065 | 427.1517 | 414.0208 | 435.4398
2928.1135 | 450.7007 | 427.1624 | 414.0863 | 435.5249
2929.1135 | 450.5908 | 427.162 | 414.046 | 435.2448
2930.1135 | 450.5829 | 427.1134 | 413.9438 | 435.3422
2931.1135 | 450.5715 | 427.092 | 413.9954 | 435.4865
2932.1135 | 450.6587 | 427.1371 | 413.9708 | 435.6915
2933.1135 | 450.6498 | 427.0795 | 413.9981 | 435.3693
2934.1135 | 450.5481 | 427.0706 | 413.8768 | 435.8365
2935.1135 | 450.4585 | 427.11 | 414.0196 | 435.9097
2936.1135 | 450.3746 | 427.1619 | 414.0678 | 435.6367
2937.1135 | 450.3129 | 427.1395 | 414.1436 | 435.5374
2938.1135 | 450.2416 | 427.161 | 414.0604 | 435.2877
2939.1135 | 450.1852 | 427.142 | 414.0952 | 435.3503
2940.1135 | 450.0473 | 427.1554 | 414.0946 | 435.2587
2941.1135 | 449.9856 | 427.1362 | 414.0337 | 435.2002
2942.1135 | 449.9127 | 427.1837 | 414.0378 | 435.033
2943.1135 | 449.8884 | 427.2 | 414.1132 | 434.9397
2944.1135 | 449.958 | 427.2282 | 414.1585 | 435.2309
2945.1135 | 449.8691 | 427.1724 | 414.1928 | 435.3576
2946.1135 | 449.7425 | 427.1336 | 414.218 | 435.6021
2947.1135 | 449.703 | 427.1042 | 414.2837 | 435.5318
2948.1135 | 449.7498 | 427.1081 | 414.2664 | 435.2452
2949.1135 | 449.794 | 427.1191 | 414.2478 | 435.4117
2950.1135 | 449.8323 | 427.1489 | 414.2989 | 435.1261
2951.1135 | 449.8265 | 427.1665 | 414.3229 | 434.9968
2952.1135 | 449.9035 | 427.2092 | 414.4236 | 435.4386
2953.1135 | 449.9479 | 427.2706 | 414.355 | 435.2983
2954.1135 | 449.9871 | 427.2685 | 414.3295 | 435.365
2955.1135 | 449.9686 | 427.2351 | 413.9255 | 435.5407
2956.1135 | 450.0093 | 427.254 | 414.0651 | 435.8138
2957.1135 | 450.0527 | 427.3268 | 414.1207 | 436.0966
2958.1135 | 450.0561 | 427.3506 | 414.223 | 436.1372
2959.1135 | 450.0391 | 427.3124 | 414.2114 | 436.0957
2960.1135 | 449.9751 | 427.2863 | 414.2197 | 436.215
2961.1135 | 449.9827 | 427.2529 | 414.2746 | 436.4304
2962.1135 | 450.0155 | 427.2622 | 414.4181 | 436.5512
2963.1135 | 450.0036 | 427.2872 | 414.4319 | 436.3895
2964.1135 | 449.9932 | 427.3001 | 414.1767 | 436.2997
2965.1135 | 450.0963 | 427.2627 | 414.3038 | 436.3762
2966.1135 | 450.0675 | 427.2293 | 414.356 | 436.3245
2967.1135 | 450.117 | 427.2887 | 414.4248 | 436.3944
2968.1135 | 450.1904 | 427.3035 | 414.3957 | 436.2606
2969.1135 | 450.2445 | 427.3406 | 414.2268 | 436.339
2970.1135 | 450.2519 | 427.3158 | 414.3922 | 436.2501
2971.1135 | 450.3242 | 427.321 | 414.3719 | 436.2302
2972.1135 | 450.3042 | 427.3437 | 414.3742 | 436.1582
2973.1135 | 450.3426 | 427.2999 | 414.3977 | 436.0605
2974.1135 | 450.4298 | 427.2979 | 414.5542 | 436.0569
2975.1135 | 450.4329 | 427.3334 | 414.5846 | 436.1677
2976.1135 | 450.4404 | 427.3199 | 414.5932 | 436.3298
2977.1135 | 450.3706 | 427.3387 | 414.6093 | 436.2243
2978.1135 | 450.3721 | 427.397 | 414.6474 | 436.3029
2979.1135 | 450.4361 | 427.3638 | 414.6763 | 436.7079
2980.1135 | 450.4686 | 427.3105 | 414.5833 | 436.7365
2981.1135 | 450.4574 | 427.3486 | 414.5301 | 436.9619
2982.1135 | 450.511 | 427.4295 | 414.3776 | 436.7963
2983.1135 | 450.4601 | 427.3766 | 414.5122 | 436.8916
2984.1135 | 450.3876 | 427.436 | 414.5776 | 436.8781
2985.1135 | 450.2929 | 427.4307 | 414.2947 | 437.192
2986.1135 | 450.2462 | 427.4623 | 414.3904 | 436.7371
2987.1135 | 450.1601 | 427.4854 | 414.3409 | 436.9436
2988.1135 | 450.1704 | 427.4122 | 414.3327 | 436.9037
2989.1135 | 450.1581 | 427.4329 | 414.2094 | 437.0065
2990.1135 | 450.1283 | 427.4188 | 414.3725 | 436.8283
2991.1135 | 450.1013 | 427.4107 | 414.4821 | 437.0263
2992.1135 | 450.0352 | 427.4429 | 414.5908 | 437.0972
2993.1135 | 449.9086 | 427.4759 | 414.5695 | 436.9926
2994.1135 | 449.926 | 427.4482 | 414.521 | 437.0089
2995.1135 | 449.9523 | 427.3743 | 414.4556 | 437.0343
2996.1135 | 449.8774 | 427.4229 | 414.4792 | 437.1469
2997.1135 | 449.7652 | 427.4016 | 414.5426 | 436.9862
2998.1135 | 449.7674 | 427.37 | 414.6798 | 436.9652
2999.1135 | 449.7687 | 427.3981 | 414.6516 | 436.9423
3000.1135 | 449.8603 | 427.3586 | 414.6524 | 437.191
3001.1135 | 449.8664 | 427.3791 | 414.5677 | 437.2853
3002.1135 | 449.8741 | 427.4171 | 414.5695 | 437.0128
3003.1135 | 449.852 | 427.4111 | 414.546 | 437.2481
3004.1135 | 449.8746 | 427.4192 | 414.5336 | 437.4941
3005.1135 | 449.869 | 427.3674 | 414.535 | 437.8209
3006.1135 | 449.847 | 427.3823 | 414.5522 | 437.8454
3007.1135 | 449.7968 | 427.3408 | 414.5771 | 437.6368
3008.1135 | 449.8048 | 427.3934 | 414.5985 | 437.7433
3009.1135 | 449.9396 | 427.4473 | 414.5787 | 437.6109
3010.1135 | 450.0292 | 427.4726 | 414.5678 | 437.8866
3011.1135 | 450.02 | 427.418 | 414.573 | 437.8328
3012.1135 | 449.9904 | 427.4087 | 414.5089 | 437.8163
3013.1135 | 450.0085 | 427.3847 | 414.4793 | 438.1302
3014.1135 | 450.0321 | 427.4457 | 414.4263 | 438.0014
3015.1135 | 450.1476 | 427.487 | 414.4187 | 438.0936
3016.1135 | 450.2015 | 427.5082 | 414.5708 | 437.9861
3017.1135 | 450.2469 | 427.5393 | 414.5158 | 438.2353
3018.1135 | 450.1696 | 427.563 | 414.436 | 438.297
3019.1135 | 450.159 | 427.5691 | 414.5357 | 438.0621
3020.1135 | 450.1719 | 427.5573 | 414.5882 | 437.9173
3021.1135 | 450.1881 | 427.5213 | 414.5861 | 437.7604
3022.1135 | 450.2654 | 427.5158 | 414.5878 | 438.0186
3023.1135 | 450.3463 | 427.5391 | 414.6103 | 437.7995
3024.1135 | 450.3951 | 427.4799 | 414.5823 | 437.777
3025.1135 | 450.4562 | 427.4981 | 414.6254 | 437.9818
3026.1135 | 450.5699 | 427.5228 | 414.7067 | 438.0577
3027.1135 | 450.6535 | 427.5493 | 414.7317 | 438.0307
3028.1135 | 450.6947 | 427.5612 | 414.7215 | 438.0131
3029.1135 | 450.777 | 427.5254 | 414.7009 | 438.0288
3030.1135 | 450.8091 | 427.5806 | 414.4629 | 438.0671
3031.1135 | 450.8591 | 427.6269 | 414.6283 | 438.1455
3032.1135 | 450.8761 | 427.5733 | 414.6658 | 438.1033
3033.1135 | 450.8885 | 427.5993 | 414.6221 | 437.9912
3034.1135 | 450.8873 | 427.5325 | 414.614 | 438.3486
3035.1135 | 450.8365 | 427.5861 | 414.5802 | 438.459
3036.1135 | 450.8648 | 427.5792 | 414.6502 | 438.3894
3037.1135 | 450.8837 | 427.5318 | 414.7581 | 438.2385
3038.1135 | 450.8716 | 427.5834 | 414.7343 | 438.0735
3039.1135 | 450.8664 | 427.5641 | 414.7323 | 438.1082
3040.1135 | 450.8637 | 427.5194 | 414.7678 | 437.917
3041.1135 | 450.813 | 427.5596 | 414.801 | 437.8946
3042.1135 | 450.7875 | 427.5426 | 414.7486 | 438.2148
3043.1135 | 450.7162 | 427.5157 | 414.7717 | 438.1529
3044.1135 | 450.6579 | 427.4991 | 414.687 | 438.0859
3045.1135 | 450.5753 | 427.5286 | 414.6599 | 438.1797
3046.1135 | 450.5391 | 427.5703 | 414.737 | 438.2187
3047.1135 | 450.5092 | 427.648 | 414.7638 | 438.4118
3048.1292 | 450.5719 | 427.6451 | 414.7969 | 438.4977
3049.1135 | 450.5934 | 427.6754 | 414.7496 | 438.0946
3050.1135 | 450.4892 | 427.6572 | 414.6283 | 438.7348
3051.1135 | 450.4056 | 427.658 | 414.6945 | 438.5119
3052.1135 | 450.3162 | 427.657 | 414.7384 | 438.3496
3053.1135 | 450.2145 | 427.6541 | 414.719 | 438.7429
3054.1135 | 450.1585 | 427.6096 | 414.765 | 438.4487
3055.1135 | 450.1221 | 427.677 | 414.7613 | 438.4878
3056.1135 | 450.1427 | 427.6531 | 414.7078 | 438.4263
3057.1135 | 450.0667 | 427.671 | 414.717 | 438.4002
3058.1135 | 450.0152 | 427.6597 | 414.6053 | 438.488
3059.1135 | 450.0783 | 427.6635 | 414.7513 | 438.398
3060.1135 | 450.1168 | 427.6767 | 414.7385 | 438.7426
3061.1135 | 450.0415 | 427.7036 | 414.737 | 438.8933
3062.1135 | 449.983 | 427.7165 | 414.5432 | 438.9824
3063.1135 | 449.9924 | 427.7296 | 414.6293 | 438.6522
3064.1135 | 449.8965 | 427.6959 | 414.6583 | 438.9029
3065.1135 | 449.8067 | 427.6528 | 414.7963 | 439.0185
3066.1135 | 449.7645 | 427.647 | 414.7637 | 438.8761
3067.1135 | 449.7425 | 427.733 | 414.7584 | 438.9526
3068.1135 | 449.8054 | 427.6884 | 414.7949 | 438.9705
3069.1135 | 449.8751 | 427.6874 | 414.7765 | 438.9801
3070.1135 | 449.8924 | 427.6395 | 414.7195 | 439.0199
3071.1135 | 449.8808 | 427.7146 | 414.7898 | 438.807
3072.1135 | 449.8959 | 427.7068 | 414.7698 | 439.0217
3073.1135 | 449.8424 | 427.6744 | 414.6836 | 439.2089
3074.1135 | 449.8747 | 427.677 | 414.753 | 439.2915
3075.1135 | 449.8925 | 427.6938 | 414.7333 | 439.193
3076.1135 | 449.9608 | 427.6533 | 414.5969 | 439.5232
3077.1135 | 450.0163 | 427.6892 | 414.6383 | 439.4327
3078.1135 | 450.0611 | 427.7269 | 414.7268 | 439.3632
3079.1135 | 450.0492 | 427.714 | 414.786 | 439.3909
3080.1135 | 450.1268 | 427.6985 | 414.8214 | 439.5461
3081.1135 | 450.1936 | 427.6746 | 414.9731 | 439.3977
3082.1135 | 450.2497 | 427.7375 | 414.9928 | 439.5598
3083.1135 | 450.3005 | 427.7483 | 415.0609 | 439.3942
3084.1135 | 450.3462 | 427.7027 | 414.912 | 439.4635
3085.1135 | 450.3281 | 427.6844 | 414.7875 | 439.6271
3086.1135 | 450.405 | 427.7142 | 414.8678 | 439.7098
3087.1135 | 450.433 | 427.7021 | 414.9077 | 439.669
3088.1135 | 450.4921 | 427.7425 | 414.8597 | 439.7262
3089.1135 | 450.5636 | 427.7946 | 414.8593 | 439.6299
3090.1135 | 450.5142 | 427.7576 | 414.8146 | 439.6615
3091.1135 | 450.4982 | 427.7901 | 414.8442 | 439.5382
3092.1135 | 450.4801 | 427.8135 | 414.8803 | 439.4964
3093.1135 | 450.4543 | 427.8687 | 414.9051 | 439.7143
3094.1135 | 450.4066 | 427.7751 | 414.9946 | 439.4951
3095.1135 | 450.3701 | 427.8022 | 415.0204 | 439.7094
3096.1135 | 450.3426 | 427.7817 | 414.9941 | 439.6002
3097.1135 | 450.34 | 427.7912 | 414.9222 | 439.4458
3098.1135 | 450.3184 | 427.7713 | 414.9656 | 439.4788
3099.1135 | 450.1795 | 427.7518 | 414.9149 | 439.6184
3100.1135 | 450.0957 | 427.7449 | 414.8905 | 439.4803
3101.1135 | 450.088 | 427.7628 | 414.9875 | 439.5999
3102.1135 | 450.0823 | 427.7952 | 414.9852 | 440.1779
3103.1135 | 450.079 | 427.815 | 414.9429 | 440.7965
3104.1135 | 450.1013 | 427.7888 | 414.807 | 440.5747
3105.1135 | 450.0956 | 427.8319 | 414.6706 | 440.352
3106.1135 | 449.8831 | 427.7646 | 414.875 | 439.8463
3107.1135 | 449.8182 | 427.7891 | 414.9232 | 441.0829
3108.1135 | 449.8588 | 427.804 | 414.931 | 440.5879
3109.1135 | 449.9239 | 427.8096 | 415.0186 | 440.8843
3110.1135 | 449.9371 | 427.8284 | 414.9833 | 440.89
3111.1135 | 450.0146 | 427.8007 | 414.9315 | 441.1666
3112.1135 | 450.0443 | 427.8232 | 414.9924 | 441.0696
3113.1135 | 450.0624 | 427.8229 | 414.9713 | 440.9378
3114.1135 | 450.0696 | 427.8324 | 414.9048 | 439.7784
3115.1135 | 450.1012 | 427.8866 | 414.8915 | 439.7524
3116.1135 | 450.0472 | 427.8756 | 414.9869 | 439.7567
3117.1135 | 450.0646 | 427.9126 | 414.9893 | 440.082
3118.1135 | 450.1277 | 427.9151 | 415.0191 | 440.9753
3119.1135 | 450.1069 | 427.891 | 415.0435 | 440.9433
3120.1135 | 450.1079 | 427.9177 | 415.0679 | 441.3376
3121.1135 | 450.1398 | 427.8823 | 415.1322 | 441.5031
3122.1135 | 450.0692 | 427.8627 | 415.1259 | 440.9966
3123.1135 | 450.0211 | 427.8593 | 415.1227 | 441.1768
3124.1135 | 450.0072 | 427.8363 | 415.0494 | 441.3186
3125.1135 | 450.0246 | 427.7867 | 415.0202 | 440.2928
3126.1135 | 450.0041 | 427.8279 | 415.0823 | 440.3744
3127.1135 | 450.0206 | 427.8228 | 415.129 | 440.6037
3128.1135 | 450.1003 | 427.901 | 415.1834 | 440.4503
3129.1135 | 450.188 | 427.8158 | 415.2298 | 440.9991
3130.1135 | 450.2354 | 427.8164 | 415.1273 | 440.6144
3131.1135 | 450.2329 | 427.814 | 415.069 | 440.8491
3132.1135 | 450.1748 | 427.8365 | 415.1901 | 440.8406
3133.1135 | 450.1259 | 427.8676 | 415.2205 | 441.4588
3134.1135 | 450.1216 | 427.9105 | 415.1955 | 440.8689
3135.1135 | 450.167 | 427.9477 | 415.2039 | 440.7894
3136.1135 | 450.1617 | 427.9748 | 415.1037 | 440.8958
3137.1135 | 450.0852 | 427.9365 | 415.0939 | 440.9158
3138.1135 | 450.0749 | 427.9033 | 415.0356 | 441.2749
3139.1135 | 450.1267 | 427.9161 | 415.0453 | 442.0596
3140.1135 | 450.1702 | 427.8861 | 415.144 | 441.505
3141.1135 | 450.15 | 427.9008 | 415.1592 | 441.0884
3142.1135 | 450.1651 | 427.9015 | 415.2243 | 440.8235
3143.1135 | 450.1797 | 427.8594 | 415.2306 | 440.9352
3144.1135 | 450.2273 | 427.8442 | 415.0285 | 440.508
3145.1135 | 450.2344 | 427.927 | 415.091 | 440.9357
3146.1135 | 450.1397 | 427.9693 | 415.0632 | 440.8573
3147.1135 | 450.1004 | 427.8889 | 415.1725 | 440.9653
3148.1135 | 450.1224 | 427.9076 | 414.9613 | 441.0561
3149.1135 | 450.0837 | 427.9168 | 414.9887 | 441.6055
3150.1135 | 449.9646 | 427.9607 | 415.0593 | 441.3177
3151.1135 | 449.9378 | 427.9392 | 415.1642 | 440.9494
3152.1135 | 449.8849 | 427.9305 | 415.0733 | 441.0648
3153.1135 | 449.8213 | 427.9792 | 415.0587 | 442.1813
3154.1135 | 449.8053 | 428.0158 | 415.1046 | 441.1381
3155.1135 | 449.8239 | 427.982 | 415.1566 | 440.9504
3156.1135 | 449.8291 | 428.0144 | 415.158 | 440.9493
3157.1135 | 449.8898 | 428.0365 | 415.1813 | 440.8147
3158.1135 | 449.8969 | 428.0141 | 415.1953 | 440.7995
3159.1135 | 449.873 | 428.0464 | 415.1166 | 441.0388
3160.1135 | 449.7816 | 428.0185 | 415.136 | 441.1464
3161.1135 | 449.7417 | 427.9645 | 415.101 | 441.1871
3162.1135 | 449.673 | 427.9322 | 415.1503 | 441.1512
3163.1135 | 449.7323 | 427.9316 | 415.2375 | 441.3207
3164.1135 | 449.7636 | 427.9866 | 415.2354 | 441.3078
3165.1135 | 449.7457 | 427.9611 | 415.2799 | 441.1533
3166.1135 | 449.7864 | 427.9305 | 415.2586 | 440.9513
3167.1135 | 449.8761 | 428.0058 | 415.227 | 441.0057
3168.1135 | 449.9106 | 427.9643 | 415.2214 | 441.2649
3169.1135 | 450.0068 | 427.9918 | 415.2787 | 442.0233
3170.1135 | 450.0372 | 427.9659 | 415.1369 | 441.8118
3171.1135 | 450.0997 | 428.0095 | 415.1753 | 441.1717
3172.1135 | 450.2219 | 428.0491 | 415.1364 | 441.1765
3173.1135 | 450.2645 | 428.0652 | 415.2057 | 441.1494
3174.1135 | 450.2644 | 428.0805 | 415.2411 | 442.0525
3175.1135 | 450.2844 | 428.0428 | 415.2388 | 442.5924
3176.1135 | 450.3484 | 428.0752 | 415.1461 | 442.5789
3177.1135 | 450.2873 | 428.1265 | 415.2074 | 442.5741
3178.1135 | 450.3845 | 428.1161 | 415.282 | 442.4901
3179.1135 | 450.4596 | 428.1157 | 415.3357 | 442.5562
3180.1135 | 450.4874 | 428.1154 | 415.3322 | 442.7822
3181.1135 | 450.5611 | 428.0916 | 415.311 | 442.7574
3182.1135 | 450.4987 | 428.1043 | 415.3107 | 441.5581
3183.1135 | 450.4997 | 428.1154 | 415.2606 | 441.7021
3184.1135 | 450.5544 | 428.134 | 415.2799 | 441.6869
3185.1135 | 450.6145 | 428.1316 | 415.2858 | 441.6991
3186.1135 | 450.6431 | 428.0778 | 415.2333 | 441.9169
3187.1135 | 450.7189 | 428.0661 | 415.2339 | 441.7515
3188.1135 | 450.761 | 428.0275 | 415.2652 | 441.7905
3189.1135 | 450.8251 | 428.051 | 415.3335 | 441.7777
3190.1135 | 450.8856 | 428.043 | 415.3902 | 441.9403
3191.1135 | 450.8692 | 428.0865 | 415.3946 | 441.9181
3192.1135 | 450.8457 | 428.0738 | 415.403 | 441.8357
3193.1135 | 450.7725 | 428.0888 | 415.3708 | 441.9211
3194.1135 | 450.7519 | 428.1179 | 415.3113 | 442.7058
3195.1135 | 450.748 | 428.1654 | 415.3429 | 443.0635
3196.1135 | 450.7057 | 428.1622 | 415.2932 | 442.2972
3197.1135 | 450.7077 | 428.1257 | 415.0905 | 441.9631
3198.1135 | 450.7172 | 428.0844 | 415.0805 | 441.9515
3199.1135 | 450.6366 | 428.1011 | 415.1615 | 441.9331
3200.1135 | 450.531 | 428.0959 | 415.3436 | 441.9358
3201.1135 | 450.4711 | 428.1177 | 415.3395 | 442.5496
3202.1135 | 450.4742 | 428.1676 | 415.3358 | 442.0786
3203.1135 | 450.3895 | 428.2056 | 415.3775 | 441.762
3204.1135 | 450.3908 | 428.202 | 415.331 | 441.8305
3205.1135 | 450.3702 | 428.1652 | 415.4083 | 442.5632
3206.1135 | 450.4237 | 428.2027 | 415.4107 | 442.9275
3207.1135 | 450.4354 | 428.182 | 415.3597 | 442.6289
3208.1135 | 450.4439 | 428.2412 | 415.3892 | 442.6599
3209.1135 | 450.4451 | 428.1597 | 415.4898 | 442.7698
3210.1135 | 450.471 | 428.163 | 415.4678 | 442.6403
3211.1135 | 450.5032 | 428.1392 | 415.5136 | 442.7836
3212.1135 | 450.5132 | 428.1362 | 415.5395 | 442.7845
3213.1135 | 450.5374 | 428.1679 | 415.4782 | 442.8701
3214.1135 | 450.5894 | 428.2198 | 415.3412 | 442.8325
3215.1135 | 450.5812 | 428.2257 | 415.3922 | 443.1518
3216.1135 | 450.6127 | 428.2715 | 415.5191 | 443.1634
3217.1135 | 450.6592 | 428.2282 | 415.5127 | 443.173
3218.1135 | 450.7021 | 428.2082 | 415.4638 | 443.346
3219.1135 | 450.7552 | 428.1733 | 415.445 | 442.8851
3220.1135 | 450.8377 | 428.2282 | 415.3591 | 443.4868
3221.1135 | 450.828 | 428.218 | 415.5381 | 443.5016
3222.1135 | 450.8173 | 428.2043 | 415.5263 | 443.4782
3223.1135 | 450.8132 | 428.2631 | 415.4947 | 443.2112
3224.1135 | 450.8261 | 428.293 | 415.5354 | 443.2455
3225.1135 | 450.8232 | 428.2923 | 415.4063 | 443.2444
3226.1135 | 450.7871 | 428.2866 | 415.4798 | 443.1461
3227.1135 | 450.7896 | 428.2257 | 415.5741 | 443.0271
3228.1135 | 450.7151 | 428.3255 | 415.6723 | 443.1292
3229.1135 | 450.6209 | 428.328 | 415.656 | 443.2547
3230.1135 | 450.6842 | 428.2977 | 415.6141 | 443.6149
3231.1135 | 450.6623 | 428.2375 | 415.6847 | 443.7783
3232.1135 | 450.5888 | 428.2267 | 415.6719 | 443.8058
3233.1135 | 450.5126 | 428.2911 | 415.6473 | 443.6483
3234.1135 | 450.4707 | 428.3104 | 415.5774 | 443.8715
3235.1135 | 450.3828 | 428.2668 | 415.6228 | 444.0091
3236.1135 | 450.3053 | 428.3046 | 415.6464 | 444.0763
3237.1135 | 450.188 | 428.2879 | 415.6813 | 443.8268
3238.1135 | 450.1643 | 428.2687 | 415.5061 | 443.8458
3239.1135 | 450.1884 | 428.2517 | 415.5932 | 444.1663
3240.1135 | 450.1901 | 428.2597 | 415.6979 | 443.9784
3241.1135 | 450.1265 | 428.3019 | 415.7398 | 444.095
3242.1135 | 450.0726 | 428.2811 | 415.8589 | 444.2024
3243.1135 | 450.0696 | 428.3031 | 415.6279 | 443.94
3244.1135 | 450.0627 | 428.3192 | 415.6865 | 443.9239
3245.1135 | 450.0945 | 428.271 | 415.6961 | 443.8438
3246.1135 | 450.2627 | 428.2801 | 415.7353 | 444.3266
3247.1135 | 450.3008 | 428.2796 | 415.6917 | 444.1883
3248.1135 | 450.3067 | 428.2865 | 415.5985 | 444.3246
3249.1135 | 450.3119 | 428.3071 | 415.7468 | 444.1293
3250.1135 | 450.3656 | 428.2896 | 415.6641 | 444.2718
3251.1135 | 450.2892 | 428.3203 | 415.6 | 444.2029
3252.1135 | 450.2875 | 428.2453 | 415.6075 | 444.0008
3253.1135 | 450.2036 | 428.2862 | 415.6671 | 444.0663
3254.1135 | 450.1392 | 428.2828 | 415.6828 | 443.8968
3255.1135 | 450.1788 | 428.3075 | 415.623 | 443.9107
3256.1135 | 450.2304 | 428.3425 | 415.6029 | 443.9461
3257.1135 | 450.174 | 428.2817 | 415.7579 | 443.907
3258.1135 | 450.1996 | 428.2298 | 415.7647 | 443.8748
3259.1135 | 450.1658 | 428.2402 | 415.6983 | 443.8116
3260.1135 | 450.1141 | 428.2832 | 415.7129 | 443.6318
3261.1135 | 450.122 | 428.312 | 415.6875 | 443.7705
3262.1135 | 450.1075 | 428.3606 | 415.6239 | 443.7491
3263.1135 | 450.0899 | 428.3388 | 415.6293 | 443.9727
3264.1135 | 450.0957 | 428.3323 | 415.71 | 443.6462
3265.1135 | 450.037 | 428.296 | 415.6432 | 443.6524
3266.1135 | 450.0337 | 428.2552 | 415.5798 | 443.9128
3267.1135 | 450.064 | 428.2886 | 415.6006 | 443.761
3268.1135 | 450.0316 | 428.3139 | 415.7799 | 443.9062
3269.1135 | 450.0014 | 428.4207 | 415.8176 | 443.9276
3270.1135 | 450.0023 | 428.3566 | 415.6733 | 443.8709
3271.1135 | 450.0015 | 428.3377 | 415.692 | 444.0647
3272.1135 | 449.9388 | 428.4285 | 415.7307 | 444.6875
3273.1135 | 449.9683 | 428.4067 | 415.6791 | 444.6882
3274.1135 | 449.9929 | 428.3866 | 415.7338 | 444.5542
3275.1135 | 449.9087 | 428.3384 | 415.7626 | 444.472
3276.1135 | 449.8755 | 428.3635 | 415.7826 | 444.4081
3277.1135 | 449.9067 | 428.3303 | 415.7479 | 444.2518
3278.1135 | 449.9408 | 428.3153 | 415.6885 | 444.4366
3279.1135 | 449.9643 | 428.3572 | 415.6581 | 444.3634
3280.1135 | 449.9126 | 428.3893 | 415.7365 | 444.2813
3281.1135 | 449.7969 | 428.3914 | 415.714 | 444.4948
3282.1135 | 449.7701 | 428.385 | 415.7171 | 444.5122
3283.1135 | 449.7096 | 428.3368 | 415.6343 | 444.4851
3284.1135 | 449.6733 | 428.323 | 415.6194 | 444.3986
3285.1135 | 449.6763 | 428.3801 | 415.6806 | 444.6942
3286.1135 | 449.7156 | 428.3027 | 415.7733 | 444.7929
3287.1135 | 449.7128 | 428.3249 | 415.7544 | 444.5541
3288.1135 | 449.6833 | 428.3437 | 415.7722 | 444.3029
3289.1135 | 449.6428 | 428.3818 | 415.8401 | 444.5503
3290.1135 | 449.7143 | 428.386 | 415.8831 | 444.6732
3291.1135 | 449.735 | 428.4352 | 416.0214 | 444.5118
3292.1135 | 449.698 | 428.4363 | 416.0099 | 444.7248
3293.1135 | 449.6944 | 428.4509 | 415.9503 | 444.6732
3294.1135 | 449.7084 | 428.3695 | 415.8756 | 444.6028
3295.1135 | 449.7353 | 428.4194 | 415.7549 | 444.7631
3296.1135 | 449.7768 | 428.4328 | 415.7208 | 444.7064
3297.1135 | 449.804 | 428.3972 | 415.7439 | 444.332
3298.1135 | 449.7455 | 428.3923 | 415.8249 | 444.8023
3299.1135 | 449.731 | 428.3595 | 415.8491 | 444.6321
3300.1135 | 449.7323 | 428.3629 | 415.8586 | 444.8678
3301.1135 | 449.7393 | 428.3349 | 415.772 | 444.783
3302.1135 | 449.7239 | 428.4079 | 415.8234 | 444.7253
3303.1135 | 449.7174 | 428.4541 | 415.7455 | 444.9224
3304.1135 | 449.7106 | 428.5173 | 415.7701 | 444.6358
3305.1135 | 449.6827 | 428.4994 | 415.8491 | 444.7033
3306.1135 | 449.625 | 428.506 | 415.6875 | 444.8201
3307.1135 | 449.7207 | 428.4742 | 415.7794 | 444.699
3308.1135 | 449.7754 | 428.4691 | 415.8952 | 444.5452
3309.1135 | 449.8266 | 428.4285 | 415.9235 | 444.5876
3310.1135 | 449.8613 | 428.3905 | 415.9277 | 444.8183
3311.1135 | 449.8654 | 428.3182 | 416.0201 | 445.1148
3312.1135 | 449.8232 | 428.3635 | 416.0245 | 444.8958
3313.1135 | 449.8877 | 428.3794 | 415.9612 | 445.1862
3314.1135 | 449.9655 | 428.4107 | 415.9964 | 444.9707
3315.1135 | 449.9757 | 428.4181 | 415.9576 | 445.4041
3316.1135 | 450.0512 | 428.4043 | 415.9045 | 445.1782
3317.1135 | 450.1002 | 428.3876 | 415.8603 | 445.5578
3318.1135 | 450.1821 | 428.4298 | 415.8821 | 445.2558
3319.1135 | 450.2336 | 428.4287 | 415.8328 | 445.5645
3320.1135 | 450.2034 | 428.3751 | 415.9026 | 445.5209
3321.1135 | 450.1986 | 428.4076 | 415.9173 | 445.3677
3322.1135 | 450.2325 | 428.4368 | 415.874 | 445.1208
3323.1135 | 450.3294 | 428.4649 | 415.9452 | 445.0186
3324.1135 | 450.4162 | 428.4931 | 415.9556 | 445.3181
3325.1135 | 450.3794 | 428.3861 | 415.9481 | 445.3497
3326.1135 | 450.3827 | 428.4264 | 415.9711 | 445.7741
3327.1135 | 450.4122 | 428.4795 | 415.9297 | 445.948
3328.1135 | 450.4787 | 428.5392 | 416.0248 | 445.7784
3329.1135 | 450.5289 | 428.5021 | 416.046 | 445.855
3330.1135 | 450.5715 | 428.5204 | 415.8444 | 445.7112
3331.1135 | 450.5976 | 428.4797 | 415.889 | 445.8223
3332.1135 | 450.5578 | 428.495 | 415.8994 | 445.5144
3333.1135 | 450.4981 | 428.4336 | 415.8528 | 445.9127
3334.1135 | 450.5194 | 428.4402 | 415.8391 | 445.4783
3335.1135 | 450.5203 | 428.4373 | 415.8842 | 445.7375
3336.1135 | 450.428 | 428.4455 | 415.9323 | 445.6262
3337.1135 | 450.3717 | 428.4309 | 415.8961 | 445.6112
3338.1135 | 450.3832 | 428.4379 | 415.8355 | 445.8741
3339.1135 | 450.2687 | 428.451 | 415.7979 | 445.9916
3340.1135 | 450.2602 | 428.4309 | 415.8516 | 445.4943
3341.1135 | 450.2756 | 428.4333 | 415.8329 | 445.574
3342.1135 | 450.3027 | 428.4187 | 415.846 | 445.7576
3343.1135 | 450.2967 | 428.4661 | 415.8076 | 445.7338
3344.1135 | 450.2795 | 428.5164 | 415.7543 | 445.9327
3345.1135 | 450.2035 | 428.4849 | 415.7498 | 446.2485
3346.1135 | 450.2073 | 428.4095 | 415.7889 | 446.1087
3347.1135 | 450.305 | 428.4135 | 415.6767 | 446.0957
3348.1135 | 451.0362 | 428.4533 | 415.6223 | 446.0092
3349.1135 | 452.4836 | 428.5439 | 415.8291 | 446.3965
3350.1135 | 454.6924 | 428.5481 | 415.624 | 446.4138
3351.1135 | 457.4106 | 428.6914 | 415.8015 | 446.3704
3352.1135 | 460.559 | 428.7708 | 415.8316 | 446.2327
3353.1135 | 464.0718 | 428.8689 | 416.0509 | 446.151
3354.1135 | 467.6186 | 429.0483 | 416.1515 | 446.3371
3355.1135 | 471.1257 | 429.0744 | 416.3232 | 446.3802
3356.1135 | 474.2957 | 429.2035 | 416.1264 | 446.361
3357.1135 | 477.155 | 429.3737 | 416.4787 | 446.4286
3358.1135 | 479.6244 | 429.5195 | 416.7559 | 446.3801
3359.1135 | 481.6658 | 429.6115 | 416.8522 | 446.6151
3360.1135 | 483.3481 | 429.7358 | 417.0092 | 446.593
3361.1135 | 484.631 | 429.839 | 417.195 | 446.7856
3362.1135 | 485.407 | 429.877 | 417.1923 | 447.0778
3363.1135 | 485.9779 | 430.0128 | 417.2763 | 447.087
3364.1135 | 486.3311 | 430.1273 | 417.2869 | 447.0899
3365.1135 | 486.5717 | 430.2755 | 417.4171 | 446.8967
3366.1135 | 486.5323 | 430.342 | 417.6095 | 447.0305
3367.1135 | 486.3687 | 430.4317 | 417.7886 | 447.1614
3368.1135 | 486.1479 | 430.546 | 417.8901 | 447.1907
3369.1135 | 485.7045 | 430.6224 | 417.9882 | 447.1448
3370.1135 | 485.3083 | 430.7071 | 417.9768 | 447.3748
3371.1135 | 484.8782 | 430.8744 | 418.0119 | 447.2941
3372.1135 | 484.2997 | 431.0151 | 418.1473 | 447.6432
3373.1135 | 483.801 | 431.0674 | 418.2258 | 447.6065
3374.1135 | 483.1679 | 431.0962 | 418.1683 | 448.0276
3375.1135 | 482.5423 | 431.2002 | 418.3746 | 447.8522
3376.1135 | 481.898 | 431.316 | 418.3784 | 447.7911
3377.1135 | 481.2636 | 431.349 | 418.3932 | 447.7965
3378.1135 | 480.6664 | 431.5037 | 418.5953 | 447.9217
3379.1135 | 480.0971 | 431.5686 | 418.7358 | 447.8455
3380.1135 | 479.4303 | 431.6154 | 418.8197 | 448.0657
3381.1135 | 478.8466 | 431.659 | 418.8484 | 448.2172
3382.1135 | 478.2995 | 431.7494 | 418.8845 | 448.4863
3383.1135 | 477.7809 | 431.809 | 419.0436 | 448.6948
3384.1292 | 477.3181 | 431.899 | 419.0853 | 448.7469
3385.1135 | 476.9046 | 431.9557 | 419.1155 | 448.5843
3386.1135 | 476.5732 | 432.1126 | 419.2295 | 448.6631
3387.1135 | 476.2257 | 432.1572 | 419.2959 | 449.2152
3388.1135 | 475.8707 | 432.1152 | 419.2904 | 449.34
3389.1135 | 475.5652 | 432.251 | 419.4255 | 449.1773
3390.1135 | 475.309 | 432.3305 | 419.5234 | 448.9593
3391.1135 | 475.0585 | 432.3661 | 419.6137 | 449.0088
3392.1135 | 474.7978 | 432.4384 | 419.5736 | 449.5273
3393.1135 | 474.6048 | 432.4858 | 419.5907 | 449.7707
3394.1135 | 474.4657 | 432.55 | 419.7051 | 450.026
3395.1135 | 474.1944 | 432.5884 | 419.7363 | 449.7997
3396.1135 | 474.1983 | 432.7125 | 419.7919 | 449.9918
3397.1135 | 474.2241 | 432.748 | 419.873 | 450.0766
3398.1135 | 474.1968 | 432.8443 | 419.9685 | 450.0984
3399.1135 | 474.1935 | 432.933 | 420.0074 | 450.5176
3400.1135 | 474.215 | 433.032 | 420.0165 | 450.732
3401.1135 | 474.2644 | 433.0799 | 420.037 | 450.3946
3402.1135 | 474.3524 | 433.1105 | 420.2296 | 450.4
3403.1135 | 474.4456 | 433.1958 | 420.2322 | 450.3945
3404.1135 | 474.6516 | 433.3135 | 420.3046 | 450.3942
3405.1135 | 474.8011 | 433.3324 | 420.4096 | 450.5691
3406.1135 | 474.8607 | 433.3702 | 420.3879 | 450.7151
3407.1135 | 474.997 | 433.4748 | 420.4677 | 450.8959
3408.1135 | 475.0535 | 433.556 | 420.5376 | 450.7771
3409.1135 | 475.0705 | 433.6457 | 420.6029 | 450.7619
3410.1135 | 475.0762 | 433.6893 | 420.6479 | 450.7497
3411.1135 | 475.0911 | 433.7801 | 420.8483 | 450.7649
3412.1135 | 475.1506 | 433.9058 | 420.954 | 450.8766
3413.1135 | 475.1892 | 433.9555 | 420.9858 | 451.0408
3414.1135 | 475.2632 | 434.0067 | 421.1083 | 451.1211
3415.1135 | 475.3666 | 434.0539 | 421.0365 | 451.0568
3416.1135 | 475.3869 | 434.0712 | 421.121 | 451.367
3417.1135 | 475.3789 | 434.1224 | 421.0859 | 451.4453
3418.1135 | 475.397 | 434.1234 | 421.0312 | 451.3399
3419.1135 | 475.5091 | 434.2953 | 421.2113 | 451.5227
3420.1135 | 475.6166 | 434.4185 | 421.2525 | 451.5931
3421.1135 | 475.7603 | 434.503 | 421.2522 | 451.8104
3422.1135 | 475.8459 | 434.5011 | 421.4215 | 452.0369
3423.1135 | 475.8864 | 434.5884 | 421.5383 | 451.6792
3424.1135 | 475.9008 | 434.6073 | 421.275 | 452.2499
3425.1135 | 475.972 | 434.6786 | 421.3503 | 452.4292
3426.1135 | 475.9798 | 434.7355 | 421.4809 | 452.1136
3427.1135 | 476.0253 | 434.7827 | 421.5955 | 452.2436
3428.1135 | 476.0285 | 434.8777 | 421.7175 | 452.4416
3429.1135 | 476.0589 | 435.0036 | 421.8127 | 452.4376
3430.1135 | 476.0248 | 435.0961 | 421.8957 | 452.6256
3431.1135 | 476.1052 | 435.1181 | 421.9928 | 452.5564
3432.1135 | 476.2053 | 435.1506 | 421.9093 | 452.4571
3433.1135 | 476.1189 | 435.2411 | 421.9813 | 452.503
3434.1135 | 476.0485 | 435.2519 | 422.0964 | 452.5255
3435.1135 | 476.064 | 435.2955 | 422.1903 | 452.4626
3436.1135 | 476.0484 | 435.434 | 422.3103 | 452.7395
3437.1135 | 476.0264 | 435.4538 | 422.3676 | 452.7647
3438.1135 | 476.0177 | 435.5366 | 422.2449 | 452.9033
3439.1135 | 476.0095 | 435.6909 | 422.2301 | 453.1994
3440.1135 | 476.0863 | 435.8123 | 422.3652 | 453.2553
3441.1135 | 476.1074 | 435.7832 | 422.459 | 453.1842
3442.1135 | 476.0756 | 435.8303 | 422.5665 | 453.2622
3443.1135 | 476.1068 | 435.8674 | 422.696 | 453.4179
3444.1135 | 476.0843 | 435.9258 | 422.7451 | 453.2647
3445.1135 | 476.0551 | 436.027 | 422.8474 | 453.0956
3446.1135 | 475.998 | 436.1216 | 422.7863 | 453.207
3447.1135 | 476.0437 | 436.117 | 422.8481 | 453.3601
3448.1135 | 475.9758 | 436.2363 | 422.8314 | 453.839
3449.1135 | 475.8397 | 436.2781 | 422.7735 | 453.9962
3450.1135 | 475.8685 | 436.3418 | 422.9196 | 453.8391
3451.1135 | 475.8659 | 436.411 | 422.956 | 454.197
3452.1135 | 475.8662 | 436.3856 | 423.0615 | 453.9297
3453.1135 | 475.8945 | 436.4469 | 423.0861 | 454.0898
3454.1135 | 475.7812 | 436.502 | 423.1219 | 454.2848
3455.1135 | 475.7547 | 436.6161 | 423.156 | 454.2503
3456.1135 | 475.7721 | 436.5967 | 423.196 | 454.3331
3457.1135 | 475.7574 | 436.6641 | 423.3185 | 454.0645
3458.1135 | 475.6711 | 436.7091 | 423.4442 | 454.2334
3459.1135 | 475.5813 | 436.8091 | 423.5563 | 454.3865
3460.1135 | 475.5569 | 436.8884 | 423.4441 | 454.4866
3461.1135 | 475.5288 | 436.9554 | 423.5281 | 454.4206
3462.1135 | 475.5394 | 437.009 | 423.6638 | 454.5153
3463.1135 | 475.5682 | 437.0714 | 423.7562 | 454.629
3464.1135 | 475.5777 | 437.0879 | 423.8084 | 454.5582
3465.1135 | 475.6263 | 437.1764 | 423.8451 | 454.6854
3466.1135 | 475.5965 | 437.207 | 423.9139 | 454.9853
3467.1135 | 475.6256 | 437.2542 | 424.1043 | 454.6708
3468.1135 | 475.7586 | 437.345 | 424.2136 | 455.0192
3469.1135 | 475.8052 | 437.3447 | 424.2101 | 455.3957
3470.1135 | 475.7813 | 437.3998 | 424.2955 | 455.565
3471.1135 | 475.9211 | 437.4569 | 424.3241 | 455.5388
3472.1135 | 475.9549 | 437.5244 | 424.4308 | 455.5314
3473.1135 | 476.0368 | 437.5939 | 424.4048 | 455.6343
3474.1135 | 476.1785 | 437.6468 | 424.3976 | 455.9844
3475.1135 | 476.1986 | 437.7 | 424.5146 | 456.0829
3476.1135 | 476.0745 | 437.7511 | 424.6203 | 456.2065
3477.1135 | 476.064 | 437.7805 | 424.6214 | 456.2431
3478.1135 | 476.1324 | 437.9153 | 424.7206 | 456.2221
3479.1135 | 476.2126 | 437.9985 | 424.7254 | 456.1897
3480.1135 | 476.1694 | 438.1004 | 424.6683 | 456.3992
3481.1135 | 476.105 | 438.0681 | 424.7517 | 456.4209
3482.1135 | 476.121 | 438.1024 | 424.7894 | 456.4093
3483.1135 | 476.0068 | 438.1373 | 424.8518 | 457.1156
3484.1135 | 475.9859 | 438.2252 | 424.8748 | 457.134
3485.1135 | 475.9088 | 438.2431 | 425.0951 | 457.2806
3486.1135 | 475.8909 | 438.3402 | 425.1408 | 457.2841
3487.1135 | 475.7711 | 438.3948 | 425.0831 | 457.3027
3488.1135 | 475.6945 | 438.4286 | 425.1779 | 457.3319
3489.1135 | 475.6417 | 438.515 | 425.2176 | 457.1193
3490.1135 | 475.5469 | 438.5279 | 425.2637 | 456.8068
3491.1135 | 475.4571 | 438.5502 | 425.174 | 457.3278
3492.1135 | 475.4195 | 438.6266 | 425.3529 | 457.7712
3493.1135 | 475.4073 | 438.7218 | 425.2957 | 457.2677
3494.1135 | 475.3536 | 438.7887 | 425.4849 | 457.2322
3495.1135 | 475.2874 | 438.9087 | 425.5345 | 457.4033
3496.1135 | 475.265 | 438.9128 | 425.6423 | 457.2428
3497.1135 | 475.2282 | 438.9448 | 425.6897 | 457.3547
3498.1135 | 475.2845 | 438.9956 | 425.624 | 457.4911
3499.1135 | 475.3007 | 439.0056 | 425.5695 | 457.6656
3500.1135 | 475.3128 | 439.0559 | 425.5225 | 457.6917
3501.1135 | 475.3098 | 439.0457 | 425.5474 | 457.7474
3502.1135 | 475.2781 | 439.1155 | 425.623 | 457.9106
3503.1135 | 475.1849 | 439.1819 | 425.6523 | 457.9634
3504.1135 | 475.2127 | 439.2128 | 425.6758 | 457.4424
3505.1135 | 475.2039 | 439.207 | 425.783 | 457.6887
3506.1135 | 475.2085 | 439.214 | 425.8317 | 457.9702
3507.1135 | 475.1857 | 439.2607 | 425.9252 | 458.0698
3508.1135 | 475.165 | 439.3917 | 425.9734 | 458.4291
3509.1135 | 475.1844 | 439.4663 | 426.0258 | 458.3722
3510.1135 | 475.1552 | 439.5024 | 425.9918 | 458.5119
3511.1135 | 475.0342 | 439.5116 | 426.039 | 458.409
3512.1135 | 475.0068 | 439.5804 | 426.1318 | 458.5359
3513.1135 | 474.9862 | 439.7247 | 426.196 | 458.4495
3514.1135 | 475.0804 | 439.7089 | 426.1632 | 458.5405
3515.1135 | 475.027 | 439.7373 | 426.2212 | 458.632
3516.1135 | 474.9772 | 439.7295 | 426.2584 | 458.8407
3517.1135 | 474.9465 | 439.7654 | 426.2937 | 459.2513
3518.1135 | 474.9813 | 439.8494 | 426.3644 | 459.2756
3519.1135 | 474.9066 | 439.9286 | 426.4423 | 459.0745
3520.1135 | 474.84 | 439.9286 | 426.5492 | 458.9485
3521.1135 | 474.7978 | 439.9759 | 426.5829 | 459.0597
3522.1135 | 474.743 | 440.0826 | 426.5772 | 459.17
3523.1135 | 474.7499 | 440.0856 | 426.6649 | 459.2058
3524.1135 | 474.7724 | 440.1829 | 426.7283 | 459.0348
3525.1135 | 474.6849 | 440.1875 | 426.7471 | 459.3166
3526.1135 | 474.6996 | 440.2285 | 426.8322 | 460.0509
3527.1135 | 474.6559 | 440.3122 | 426.8189 | 459.8465
3528.1135 | 474.7168 | 440.3797 | 426.8496 | 460.1506
3529.1135 | 474.803 | 440.4209 | 426.7648 | 460.029
3530.1135 | 474.9156 | 440.513 | 426.6281 | 460.0469
3531.1135 | 474.9025 | 440.5682 | 426.8233 | 460.0713
3532.1135 | 474.9452 | 440.525 | 426.8315 | 460.1601
3533.1135 | 474.8969 | 440.5468 | 426.9483 | 460.2819
3534.1135 | 474.8635 | 440.6415 | 427.1366 | 460.3972
3535.1135 | 474.9464 | 440.7133 | 427.2174 | 460.5623
3536.1135 | 475.0141 | 440.7502 | 427.127 | 460.6724
3537.1135 | 475.0531 | 440.7644 | 427.2171 | 460.6926
3538.1135 | 475.1132 | 440.7723 | 427.2858 | 460.7814
3539.1135 | 475.1171 | 440.8016 | 427.2467 | 460.3229
3540.1135 | 475.1456 | 440.862 | 427.2082 | 460.8276
3541.1135 | 475.2542 | 440.9053 | 427.1251 | 460.855
3542.1135 | 475.3596 | 440.9879 | 427.1779 | 460.8466
3543.1135 | 475.4268 | 441.0161 | 427.2189 | 460.7245
3544.1135 | 475.4634 | 440.9962 | 427.3291 | 461.0177
3545.1135 | 475.4143 | 441.0396 | 427.4297 | 461.0107
3546.1135 | 475.4267 | 441.0456 | 427.4636 | 460.6121
3547.1135 | 475.5187 | 441.0678 | 427.5194 | 460.9563
3548.1135 | 475.5268 | 441.1404 | 427.6068 | 460.9231
3549.1135 | 475.4677 | 441.2468 | 427.6523 | 460.9079
3550.1135 | 475.3937 | 441.332 | 427.6816 | 460.8999
3551.1135 | 475.3138 | 441.3588 | 427.7255 | 460.7641
3552.1135 | 475.3115 | 441.4172 | 427.6909 | 461.1734
3553.1135 | 475.2507 | 441.4322 | 427.6402 | 461.3546
3554.1135 | 475.221 | 441.4719 | 427.6611 | 461.5737
3555.1135 | 475.1246 | 441.4634 | 427.7382 | 461.5703
3556.1135 | 475.0939 | 441.5576 | 427.7883 | 462.0446
3557.1135 | 475.1461 | 441.5912 | 427.8541 | 461.9261
3558.1135 | 475.2111 | 441.6042 | 427.9657 | 462.2535
3559.1135 | 475.2325 | 441.6497 | 428.0574 | 461.9471
3560.1135 | 475.2302 | 441.6865 | 428.1915 | 462.034
3561.1135 | 475.2444 | 441.6987 | 428.1267 | 462.0805
3562.1135 | 475.193 | 441.6887 | 428.1592 | 462.1156
3563.1135 | 475.2059 | 441.7635 | 428.3295 | 461.9912
3564.1135 | 475.1776 | 441.8133 | 428.3164 | 462.0987
3565.1135 | 475.1895 | 441.878 | 428.3927 | 462.0533
3566.1135 | 475.1796 | 441.8768 | 428.3379 | 462.4235
3567.1135 | 475.1047 | 441.8865 | 428.3902 | 462.8311
3568.1135 | 475.125 | 441.95 | 428.402 | 462.4156
3569.1135 | 475.1494 | 441.9879 | 428.4222 | 462.7103
3570.1135 | 475.1824 | 442.0793 | 428.4014 | 462.7637
3571.1135 | 475.3076 | 442.2065 | 428.4908 | 462.5213
3572.1135 | 475.2899 | 442.27 | 428.5742 | 462.5709
3573.1135 | 475.2993 | 442.2947 | 428.6156 | 462.3699
3574.1135 | 475.4013 | 442.3791 | 428.6507 | 462.5025
3575.1135 | 475.4411 | 442.3396 | 428.7128 | 462.7731
3576.1135 | 475.5406 | 442.2953 | 428.7066 | 462.5685
3577.1135 | 475.5287 | 442.2943 | 428.8562 | 462.8359
3578.1135 | 475.5375 | 442.3415 | 428.7275 | 462.9587
3579.1135 | 475.5599 | 442.3664 | 428.8998 | 462.9429
3580.1135 | 475.5844 | 442.3004 | 429.0018 | 463.0461
3581.1135 | 475.5938 | 442.4144 | 429.0311 | 463.0517
3582.1135 | 475.6877 | 442.4316 | 429.0059 | 463.1727
3583.1135 | 475.6436 | 442.468 | 429.0416 | 463.3334
3584.1135 | 475.6514 | 442.5613 | 429.1087 | 463.4145
3585.1135 | 475.6351 | 442.5557 | 429.1927 | 463.4225
3586.1135 | 475.6447 | 442.5211 | 429.2365 | 463.4206
3587.1135 | 475.6994 | 442.6567 | 429.3318 | 463.7054
3588.1135 | 475.7302 | 442.771 | 429.2877 | 463.9623
3589.1135 | 475.7867 | 442.8615 | 429.1977 | 463.9735
3590.1135 | 475.7628 | 442.8024 | 429.1858 | 463.9805
3591.1135 | 475.8331 | 442.8615 | 429.2139 | 463.9789
3592.1135 | 475.8495 | 442.989 | 429.2057 | 464.2332
3593.1135 | 475.8065 | 443.0321 | 429.3746 | 464.0773
3594.1135 | 475.8144 | 443.0735 | 429.4612 | 463.9987
3595.1135 | 475.8098 | 443.0912 | 429.5123 | 463.9354
3596.1135 | 475.7099 | 443.0515 | 429.5574 | 464.088
3597.1135 | 475.6812 | 443.1492 | 429.6822 | 463.7807
3598.1135 | 475.6075 | 443.1902 | 429.7036 | 463.7903
3599.1135 | 475.5896 | 443.2039 | 429.7198 | 463.8965
3600.1135 | 475.4776 | 443.218 | 429.6444 | 464.1227
3601.1135 | 475.3887 | 443.3241 | 429.7287 | 464.0012
3602.1135 | 475.2949 | 443.3912 | 429.7445 | 464.1434
3603.1135 | 475.2924 | 443.3689 | 429.6766 | 464.4762
3604.1135 | 475.283 | 443.3883 | 429.6189 | 464.487
3605.1135 | 475.2879 | 443.4912 | 429.808 | 464.5067
3606.1135 | 475.2776 | 443.5182 | 429.9073 | 464.359
3607.1135 | 475.34 | 443.5287 | 429.9003 | 464.5539
3608.1135 | 475.4408 | 443.5063 | 429.8823 | 464.7987
3609.1135 | 475.5323 | 443.5651 | 429.8717 | 464.85
3610.1135 | 475.5179 | 443.6651 | 429.9376 | 465.1911
3611.1135 | 475.5074 | 443.6864 | 430.0307 | 464.4679
3612.1135 | 475.5417 | 443.7622 | 430.1928 | 464.6325
3613.1135 | 475.6101 | 443.8066 | 430.1573 | 464.9883
3614.1135 | 475.7318 | 443.845 | 430.1563 | 465.1238
3615.1135 | 475.7634 | 443.8206 | 430.1735 | 465.138
3616.1135 | 475.7959 | 443.8982 | 430.268 | 464.9151
3617.1135 | 475.8295 | 443.93 | 430.3118 | 465.2732
3618.1135 | 475.7913 | 443.9432 | 430.2467 | 465.0351
3619.1135 | 475.8512 | 444.0083 | 430.334 | 464.927
3620.1135 | 476.0271 | 444.0503 | 430.3836 | 465.0783
3621.1135 | 476.1273 | 444.1226 | 430.3339 | 465.2429
3622.1135 | 476.2125 | 444.1515 | 430.4245 | 465.3155
3623.1135 | 476.2817 | 444.2142 | 430.4659 | 465.557
3624.1135 | 476.3306 | 444.2053 | 430.4498 | 465.8601
3625.1135 | 476.3711 | 444.2118 | 430.4219 | 466.0176
3626.1135 | 476.3767 | 444.267 | 430.549 | 465.3574
3627.1135 | 476.415 | 444.3127 | 430.7742 | 465.3319
3628.1135 | 476.4936 | 444.3864 | 430.6811 | 465.4722
3629.1135 | 476.5039 | 444.3263 | 430.7131 | 465.2786
3630.1135 | 476.5363 | 444.4122 | 430.771 | 465.368
3631.1135 | 476.5214 | 444.5026 | 430.8332 | 465.5765
3632.1135 | 476.5407 | 444.5566 | 430.9516 | 465.7279
3633.1135 | 476.6036 | 444.6126 | 431.0218 | 466.0097
3634.1135 | 476.6094 | 444.6587 | 431.0836 | 465.904
3635.1135 | 476.5877 | 444.6322 | 431.1454 | 466.0805
3636.1135 | 476.5749 | 444.6702 | 431.1536 | 466.3593
3637.1135 | 476.514 | 444.681 | 431.0778 | 466.5387
3638.1135 | 476.4712 | 444.709 | 431.2275 | 466.4582
3639.1135 | 476.3685 | 444.8245 | 431.2597 | 466.1452
3640.1135 | 476.2822 | 444.8039 | 431.0209 | 466.2921
3641.1135 | 476.2448 | 444.8304 | 431.0799 | 466.7372
3642.1135 | 476.1805 | 444.8607 | 431.1237 | 466.5997
3643.1135 | 476.1216 | 444.8632 | 431.1347 | 466.3689
3644.1135 | 476.0801 | 444.9512 | 431.1632 | 466.4366
3645.1135 | 476.0189 | 444.9906 | 431.2524 | 466.4769
3646.1135 | 475.9503 | 445.0323 | 431.1733 | 466.6585
3647.1135 | 475.857 | 444.978 | 431.1739 | 466.8704
3648.1135 | 475.7333 | 445.0292 | 431.2777 | 466.6552
3649.1135 | 475.7063 | 445.1405 | 431.3235 | 466.3425
3650.1135 | 475.6597 | 445.1807 | 431.3606 | 466.7788
3651.1135 | 475.6296 | 445.1688 | 431.4693 | 467.1351
3652.1135 | 475.6075 | 445.2633 | 431.5349 | 467.252
3653.1135 | 475.56 | 445.2753 | 431.4847 | 467.538
3654.1135 | 475.521 | 445.2469 | 431.4746 | 467.1411
3655.1135 | 475.4055 | 445.2753 | 431.5523 | 467.041
3656.1135 | 475.3286 | 445.349 | 431.5985 | 467.2724
3657.1135 | 475.1708 | 445.3717 | 431.6583 | 467.2533
3658.1135 | 475.111 | 445.4094 | 431.6625 | 467.1421
3659.1135 | 475.0147 | 445.4028 | 431.6521 | 467.2007
3660.1135 | 475.0175 | 445.4973 | 431.5648 | 467.1927
3661.1135 | 475.0686 | 445.5384 | 431.614 | 467.1858
3662.1135 | 475.0884 | 445.5231 | 431.6853 | 467.1215
3663.1135 | 475.0454 | 445.6089 | 431.7946 | 466.9953
3664.1135 | 474.9897 | 445.5551 | 431.781 | 467.2424
3665.1135 | 475.0312 | 445.5969 | 431.7711 | 467.2123
3666.1135 | 475.0673 | 445.5633 | 431.7966 | 467.1278
3667.1135 | 475.073 | 445.6139 | 431.8374 | 467.1402
3668.1135 | 475.1338 | 445.6887 | 431.882 | 467.4687
3669.1135 | 475.0918 | 445.7558 | 431.8437 | 467.481
3670.1135 | 475.0537 | 445.6997 | 431.9595 | 467.8172
3671.1135 | 475.0687 | 445.8009 | 431.967 | 467.4773
3672.1135 | 475.0174 | 445.8448 | 431.9251 | 467.7085
3673.1135 | 474.9839 | 445.7931 | 432.1012 | 467.7534
3674.1135 | 474.9292 | 445.8529 | 432.1314 | 467.9737
3675.1135 | 474.9054 | 445.884 | 432.192 | 468.0389
3676.1135 | 474.9345 | 445.8904 | 432.24 | 468.1378
3677.1135 | 474.9401 | 445.9081 | 432.356 | 468.1367
3678.1135 | 474.9783 | 445.9499 | 432.3765 | 468.0247
3679.1135 | 475.0006 | 445.9539 | 432.3427 | 467.9534
3680.1135 | 474.9491 | 445.9915 | 432.3387 | 468.3327
3681.1135 | 474.946 | 446.0512 | 432.3486 | 468.1398
3682.1135 | 474.924 | 446.0933 | 432.2895 | 468.2268
3683.1135 | 474.893 | 446.1775 | 432.0065 | 468.2891
3684.1135 | 474.8655 | 446.2016 | 431.9381 | 468.5623
3685.1135 | 474.9254 | 446.2718 | 432.1548 | 468.3152
3686.1135 | 474.9317 | 446.2855 | 432.2771 | 468.2637
3687.1135 | 474.8693 | 446.2764 | 432.3247 | 468.2349
3688.1135 | 474.8487 | 446.2858 | 432.3754 | 468.1597
3689.1135 | 474.821 | 446.2625 | 432.4463 | 468.4062
3690.1135 | 474.7981 | 446.2911 | 432.4102 | 468.5228
3691.1135 | 474.8091 | 446.3515 | 432.4237 | 468.5749
3692.1135 | 474.8436 | 446.3669 | 432.2673 | 468.7042
3693.1135 | 474.8905 | 446.434 | 432.3822 | 468.6469
3694.1135 | 474.8999 | 446.4384 | 432.3868 | 468.5678
3695.1135 | 474.8458 | 446.4277 | 432.5025 | 468.8977
3696.1135 | 474.8653 | 446.4928 | 432.4512 | 468.8974
3697.1135 | 474.8489 | 446.5066 | 432.4913 | 468.9105
3698.1135 | 474.8031 | 446.5516 | 432.5649 | 468.8814
3699.1135 | 474.8477 | 446.5407 | 432.5291 | 468.926
3700.1135 | 474.8388 | 446.614 | 432.6033 | 469.0482
3701.1135 | 474.7965 | 446.6026 | 432.6315 | 469.116
3702.1135 | 474.8493 | 446.7059 | 432.6149 | 469.2668
3703.1135 | 474.8902 | 446.6378 | 432.6321 | 469.0845
3704.1135 | 474.9093 | 446.6883 | 432.7173 | 469.3205
3705.1135 | 474.8872 | 446.7382 | 432.718 | 469.2159
3706.1135 | 474.8333 | 446.7326 | 432.7605 | 469.2557
3707.1135 | 474.8869 | 446.78 | 432.8672 | 469.1872
3708.1135 | 474.9246 | 446.8172 | 432.9129 | 469.6849
3709.1135 | 474.9205 | 446.7923 | 432.9647 | 469.6648
3710.1135 | 475.0311 | 446.8086 | 432.9313 | 469.5362
3711.1135 | 475.1763 | 446.8933 | 433.0463 | 469.432
3712.1135 | 475.2513 | 446.9568 | 433.0217 | 469.5067
3713.1135 | 475.2689 | 446.9624 | 433.0432 | 469.407
3714.1135 | 475.2727 | 447.007 | 433.0493 | 469.6026
3715.1135 | 475.2982 | 446.9981 | 433.043 | 469.6628
3716.1135 | 475.2685 | 447.0672 | 433.1115 | 469.8794
3717.1135 | 475.2902 | 447.1032 | 433.1512 | 470.0146
3718.1135 | 475.3296 | 447.1045 | 432.8966 | 470.0775
3719.1135 | 475.3027 | 447.1866 | 433.0183 | 469.877
3720.1135 | 475.3106 | 447.2228 | 433.0989 | 469.4206
3721.1135 | 475.3756 | 447.1966 | 433.1737 | 469.6116
3722.1135 | 475.4333 | 447.2452 | 433.1304 | 469.6934
3723.1135 | 475.4906 | 447.224 | 433.2227 | 469.757
3724.1135 | 475.4913 | 447.2889 | 433.2904 | 469.7636
3725.1135 | 475.4974 | 447.3622 | 433.2585 | 469.8099
3726.1135 | 475.4934 | 447.2364 | 433.3241 | 470.0692
3727.1135 | 475.4843 | 447.313 | 433.3784 | 470.4172
3728.1135 | 475.3857 | 447.3268 | 433.4099 | 470.0886
3729.1135 | 475.4288 | 447.3838 | 433.3887 | 470.208
3730.1135 | 475.4511 | 447.4252 | 433.2613 | 470.3556
3731.1135 | 475.4409 | 447.4803 | 433.3916 | 470.2537
3732.1135 | 475.4631 | 447.3944 | 433.3775 | 470.3562
3733.1135 | 475.3447 | 447.4475 | 433.3493 | 470.3215
3734.1135 | 475.2803 | 447.487 | 433.4055 | 470.2474
3735.1135 | 475.2271 | 447.5064 | 433.4483 | 470.3312
3736.1135 | 475.2186 | 447.5223 | 433.4183 | 470.4776
3737.1135 | 475.199 | 447.5628 | 433.5253 | 470.1396
3738.1135 | 475.1894 | 447.5103 | 433.6164 | 470.4959
3739.1135 | 475.219 | 447.5623 | 433.5533 | 470.4247
3740.1135 | 475.329 | 447.6822 | 433.5384 | 470.3413
3741.1135 | 475.3442 | 447.6458 | 433.6149 | 470.5555
3742.1135 | 475.2816 | 447.669 | 433.6477 | 470.8079
3743.1135 | 475.2095 | 447.7476 | 433.7078 | 470.8199
3744.1135 | 475.1092 | 447.8201 | 433.7318 | 470.9201
3745.1135 | 475.1114 | 447.8074 | 433.8677 | 470.8771
3746.1135 | 475.0903 | 447.8666 | 433.7202 | 470.9642
3747.1135 | 475.1445 | 447.8235 | 433.7217 | 470.84
3748.1135 | 475.2098 | 447.8318 | 433.7834 | 470.8297
3749.1135 | 475.1838 | 447.894 | 433.8404 | 470.6547
3750.1135 | 475.178 | 447.9395 | 433.8631 | 470.8651
3751.1135 | 475.1845 | 447.9808 | 433.9676 | 470.8861
3752.1135 | 475.2132 | 447.9284 | 433.9833 | 470.7514
3753.1135 | 475.2216 | 447.9905 | 434.0736 | 470.7438
3754.1135 | 475.2169 | 448.023 | 434.1639 | 470.7453
3755.1135 | 475.1816 | 448.0144 | 434.1607 | 470.461
3756.1135 | 475.1997 | 448.0565 | 434.0423 | 470.6014
3757.1135 | 475.2646 | 448.099 | 433.9485 | 470.6385
3758.1135 | 475.3079 | 448.1055 | 433.9688 | 470.9085
3759.1135 | 475.2597 | 448.105 | 434.0401 | 471.1671
3760.1135 | 475.1669 | 448.0757 | 433.925 | 471.0607
3761.1135 | 475.2128 | 448.1235 | 433.978 | 470.8211
3762.1135 | 475.2263 | 448.1464 | 434.0689 | 470.7944
3763.1135 | 475.188 | 448.2307 | 434.1159 | 470.8708
3764.1135 | 475.2341 | 448.2521 | 434.1446 | 471.0379
3765.1135 | 475.2598 | 448.267 | 434.153 | 471.1532
3766.1135 | 475.3639 | 448.2253 | 434.2144 | 471.2107
3767.1135 | 475.3614 | 448.1046 | 434.3695 | 471.2463
3768.1135 | 475.3571 | 448.2465 | 434.3632 | 471.2969
3769.1135 | 475.2974 | 448.3197 | 434.2546 | 471.2641
3770.1135 | 475.2646 | 448.3442 | 434.3008 | 471.4183
3771.1135 | 475.1869 | 448.4106 | 434.2922 | 471.3162
3772.1135 | 475.1026 | 448.4095 | 434.2658 | 471.6161
3773.1135 | 475.047 | 448.4406 | 434.3167 | 471.6471
3774.1135 | 475.0011 | 448.4773 | 434.3107 | 471.8101
3775.1135 | 475.0142 | 448.5042 | 434.3949 | 471.735
3776.1135 | 475.035 | 448.5722 | 434.4577 | 471.7116
3777.1135 | 475.111 | 448.6373 | 434.4142 | 471.7425
3778.1135 | 475.171 | 448.6128 | 434.4102 | 471.6482
3779.1135 | 475.1342 | 448.6128 | 434.5444 | 471.6979
3780.1135 | 475.122 | 448.6641 | 434.6306 | 471.7628
3781.1135 | 475.043 | 448.7442 | 434.6802 | 471.9067
3782.1135 | 474.9985 | 448.7678 | 434.6389 | 471.8301
3783.1135 | 474.9869 | 448.7954 | 434.7032 | 471.8057
3784.1135 | 475.0981 | 448.8743 | 434.6695 | 471.8347
3785.1135 | 475.1529 | 448.839 | 434.7162 | 471.8162
3786.1135 | 475.1301 | 448.833 | 434.7023 | 471.8246
3787.1135 | 475.1187 | 448.8532 | 434.6943 | 471.8347
3788.1135 | 475.1282 | 448.8455 | 434.6429 | 471.9096
3789.1135 | 475.1037 | 448.8799 | 434.6144 | 471.9182
3790.1135 | 475.1621 | 448.8532 | 434.6764 | 471.7871
3791.1135 | 475.1637 | 448.8943 | 434.638 | 471.7786
3792.1135 | 475.1416 | 448.9107 | 434.7079 | 471.8023
3793.1135 | 475.12 | 448.9229 | 434.7362 | 471.9067
3794.1135 | 475.0645 | 448.9465 | 434.8612 | 471.9747
3795.1135 | 475.0953 | 448.9782 | 434.8655 | 472.4992
3796.1135 | 475.2016 | 449.0398 | 434.8671 | 472.2896
3797.1135 | 475.2687 | 448.9958 | 434.8975 | 472.3435
3798.1135 | 475.2836 | 448.9921 | 434.8596 | 472.1976
3799.1135 | 475.3774 | 449.0414 | 434.9659 | 472.5186
3800.1135 | 475.405 | 449.114 | 434.8596 | 472.1599
3801.1135 | 475.4579 | 449.0824 | 434.9426 | 472.2918
3802.1135 | 475.474 | 449.1443 | 434.9826 | 472.2196
3803.1135 | 475.563 | 449.1537 | 434.9676 | 472.4059
3804.1135 | 475.7001 | 449.1856 | 435.0373 | 472.2853
3805.1135 | 475.6887 | 449.2157 | 435.1223 | 472.5673
3806.1135 | 475.7323 | 449.1968 | 435.1309 | 472.4688
3807.1135 | 475.8847 | 449.2265 | 435.2373 | 472.1981
3808.1135 | 475.9787 | 449.2449 | 435.2229 | 471.9522
3809.1135 | 476.0123 | 449.3063 | 435.2216 | 471.9697
3810.1135 | 476.0158 | 449.3567 | 435.2109 | 472.0972
3811.1135 | 476.0549 | 449.3655 | 435.2413 | 472.2674
3812.1135 | 476.0496 | 449.3796 | 435.3788 | 472.2379
3813.1135 | 476.0235 | 449.3629 | 435.3455 | 472.2475
3814.1135 | 475.9606 | 449.4045 | 435.3505 | 472.0562
3815.1135 | 475.9806 | 449.4203 | 435.3793 | 472.1129
3816.1135 | 475.896 | 449.4438 | 435.3797 | 472.3455
3817.1135 | 475.8774 | 449.3961 | 435.4455 | 472.4255
3818.1135 | 475.8272 | 449.446 | 435.4541 | 472.2363
3819.1135 | 475.815 | 449.4154 | 435.5138 | 472.4044
3820.1135 | 475.7687 | 449.5132 | 435.5753 | 472.6679
3821.1135 | 475.7798 | 449.643 | 435.5774 | 472.5846
3822.1135 | 475.8213 | 449.6352 | 435.5208 | 472.637
3823.1135 | 475.8524 | 449.5668 | 435.6112 | 472.6943
3824.1135 | 475.8314 | 449.5352 | 435.5137 | 472.6219
3825.1135 | 475.6856 | 449.546 | 435.5333 | 472.8837
3826.1135 | 475.5794 | 449.6233 | 435.6278 | 472.7596
3827.1135 | 475.565 | 449.7259 | 435.581 | 472.9546
3828.1135 | 475.6 | 449.7131 | 435.6185 | 472.7478
3829.1135 | 475.4784 | 449.7441 | 435.7109 | 472.6753
3830.1135 | 475.4162 | 449.7483 | 435.634 | 472.572
3831.1135 | 475.4567 | 449.7736 | 435.5375 | 472.5232
3832.1135 | 475.4498 | 449.8177 | 435.5117 | 472.5354
3833.1135 | 475.5189 | 449.8279 | 435.4873 | 472.7996
3834.1135 | 475.4562 | 449.8055 | 435.5368 | 472.8036
3835.1135 | 475.3808 | 449.8231 | 435.6048 | 472.6596
3836.1135 | 475.3735 | 449.8806 | 435.69 | 472.9124
3837.1135 | 475.4121 | 449.899 | 435.7858 | 473.1405
3838.1135 | 475.5227 | 449.8968 | 435.8265 | 473.0858
3839.1135 | 475.5591 | 449.9007 | 435.9183 | 473.4936
3840.1135 | 475.4618 | 449.9389 | 435.7936 | 473.2238
3841.1135 | 475.4112 | 449.9588 | 435.7193 | 473.2547
3842.1135 | 475.4217 | 450.0048 | 435.7556 | 472.8006
3843.1135 | 475.3772 | 450.0144 | 435.7001 | 472.9898
3844.1135 | 475.4255 | 449.9756 | 435.7694 | 472.8191
3845.1135 | 475.4744 | 449.9755 | 435.7909 | 473.0282
3846.1135 | 475.4562 | 450.0754 | 435.785 | 473.1671
3847.1135 | 475.4431 | 450.0636 | 435.8308 | 473.2194
3848.1135 | 475.4518 | 450.1429 | 435.9015 | 473.1845
3849.1135 | 475.4517 | 450.1671 | 435.8547 | 473.3872
3850.1135 | 475.4136 | 450.1402 | 435.8404 | 473.6046
3851.1135 | 475.4064 | 450.1854 | 435.9558 | 473.8919
3852.1135 | 475.4106 | 450.136 | 436.033 | 473.702
3853.1135 | 475.4519 | 450.1294 | 435.9222 | 473.6172
3854.1135 | 475.5362 | 450.2176 | 435.9754 | 473.5909
3855.1135 | 475.5045 | 450.1952 | 436.0533 | 473.7331
3856.1135 | 475.5014 | 450.2216 | 436.1593 | 473.7231
3857.1135 | 475.4782 | 450.2517 | 436.2061 | 473.8188
3858.1135 | 475.4531 | 450.3156 | 436.1185 | 473.6588
3859.1135 | 475.4536 | 450.2634 | 436.0198 | 473.5251
3860.1135 | 475.5616 | 450.3327 | 436.005 | 473.6633
3861.1135 | 475.5909 | 450.3727 | 436.0455 | 473.8443
3862.1135 | 475.5581 | 450.3495 | 436.0437 | 473.8496
3863.1135 | 475.5346 | 450.3772 | 436.1058 | 473.9224
3864.1135 | 475.5766 | 450.4056 | 436.145 | 473.6944
3865.1135 | 475.5739 | 450.436 | 436.2571 | 473.8326
3866.1135 | 475.5164 | 450.4846 | 436.2342 | 473.6912
3867.1135 | 475.4578 | 450.4815 | 436.2131 | 473.517
3868.1135 | 475.3669 | 450.5309 | 436.1976 | 473.5849
3869.1135 | 475.4115 | 450.5449 | 436.3483 | 473.7537
3870.1135 | 475.3858 | 450.6203 | 436.3219 | 473.7961
3871.1135 | 475.3731 | 450.5126 | 436.1343 | 473.9152
3872.1135 | 475.3089 | 450.5228 | 436.2144 | 473.8628
3873.1135 | 475.2837 | 450.5288 | 436.32 | 473.977
3874.1135 | 475.3033 | 450.6075 | 436.382 | 473.969
3875.1135 | 475.399 | 450.6511 | 436.3982 | 473.7921
3876.1135 | 475.3729 | 450.7482 | 436.4383 | 473.6966
3877.1135 | 475.3299 | 450.7337 | 436.4575 | 474.0014
3878.1135 | 475.3181 | 450.6894 | 436.3711 | 474.1073
3879.1135 | 475.2959 | 450.7253 | 436.3327 | 474.0574
3880.1135 | 475.3796 | 450.751 | 436.516 | 474.0045
3881.1135 | 475.4566 | 450.7743 | 436.4977 | 473.9304
3882.1135 | 475.4288 | 450.7758 | 436.3737 | 473.8541
3883.1135 | 475.4732 | 450.8525 | 436.5176 | 473.923
3884.1135 | 475.5192 | 450.8914 | 436.3857 | 473.7924
3885.1135 | 475.4802 | 450.9202 | 436.4223 | 474.0015
3886.1135 | 475.5035 | 450.8997 | 436.4785 | 474.2055
3887.1135 | 475.4943 | 450.8312 | 436.5103 | 474.1592
3888.1135 | 475.4868 | 450.8009 | 436.5208 | 474.0421
3889.1135 | 475.4712 | 450.8745 | 436.509 | 474.2286
3890.1135 | 475.5128 | 450.8877 | 436.6382 | 474.2274
3891.1135 | 475.5881 | 450.9178 | 436.6609 | 474.1749
3892.1135 | 475.5981 | 450.93 | 436.6555 | 474.3094
3893.1135 | 475.6366 | 450.9598 | 436.6699 | 474.2748
3894.1135 | 475.677 | 450.9912 | 436.6258 | 474.0403
3895.1135 | 475.7226 | 451.0221 | 436.6518 | 473.975
3896.1135 | 475.7853 | 451.0459 | 436.6651 | 474.0672
3897.1135 | 475.8112 | 451.0534 | 436.666 | 474.1905
3898.1135 | 475.8849 | 451.0887 | 436.7252 | 474.1731
3899.1135 | 475.9715 | 451.1599 | 436.776 | 474.2784
3900.1135 | 475.9215 | 451.2074 | 436.7676 | 474.239
3901.1135 | 475.93 | 451.2005 | 436.825 | 474.2041
3902.1135 | 475.9448 | 451.2265 | 436.9348 | 474.3232
3903.1135 | 475.9491 | 451.2231 | 436.6896 | 474.1669
3904.1135 | 476.0168 | 451.2719 | 436.7215 | 474.4384
3905.1135 | 476.099 | 451.2175 | 436.9267 | 474.413
3906.1135 | 476.2138 | 451.2355 | 436.9583 | 474.4241
3907.1135 | 476.2252 | 451.2464 | 437.0078 | 474.2926
3908.1135 | 476.1795 | 451.2234 | 437.0294 | 474.143
3909.1135 | 476.2301 | 451.3113 | 437.1096 | 474.024
3910.1135 | 476.1269 | 451.4027 | 437.1102 | 474.1898
3911.1135 | 476.0427 | 451.3922 | 437.0174 | 474.1535
3912.1135 | 476.0274 | 451.3703 | 437.0433 | 474.5299
3913.1135 | 476.0498 | 451.3618 | 437.0665 | 474.9461
3914.1135 | 476.1121 | 451.3708 | 436.9791 | 474.6748
3915.1135 | 476.0745 | 451.3581 | 436.9597 | 474.9416
3916.1135 | 476.0465 | 451.3733 | 436.94 | 474.7717
3917.1135 | 476.0102 | 451.4274 | 437.0189 | 474.5704
3918.1135 | 476.0206 | 451.4576 | 437.0668 | 474.4398
3919.1135 | 476.0235 | 451.5205 | 437.1098 | 474.5507
3920.1135 | 475.9844 | 451.5068 | 437.1317 | 474.7526
3921.1135 | 475.9219 | 451.4893 | 437.1892 | 474.4427
3922.1135 | 475.9042 | 451.5086 | 437.2085 | 474.7564
3923.1135 | 475.9064 | 451.56 | 437.2743 | 474.8893
3924.1135 | 475.9012 | 451.56 | 437.206 | 474.1041
3925.1135 | 475.8559 | 451.5664 | 437.2273 | 473.8761
3926.1135 | 475.8515 | 451.5906 | 437.2479 | 473.6405
3927.1135 | 475.8177 | 451.62 | 437.2276 | 474.3473
3928.1135 | 475.8216 | 451.6673 | 437.1159 | 473.5536
3929.1135 | 475.7975 | 451.6574 | 437.2071 | 474.525
3930.1135 | 475.7633 | 451.6484 | 437.2542 | 473.4017
3931.1135 | 475.6863 | 451.6708 | 437.2504 | 474.0441
3932.1135 | 475.5962 | 451.6714 | 437.2667 | 473.0044
3933.1135 | 475.484 | 451.6846 | 437.2597 | 473.7642
3934.1135 | 475.4277 | 451.7121 | 437.336 | 472.7516
3935.1135 | 475.3781 | 451.7187 | 437.3408 | 473.6968
3936.1135 | 475.3309 | 451.7592 | 437.3528 | 474.2968
3937.1135 | 475.3241 | 451.8351 | 437.3283 | 474.4768
3938.1135 | 475.2821 | 451.8166 | 437.3509 | 474.2145
3939.1135 | 475.2751 | 451.8593 | 437.4833 | 474.7251
3940.1135 | 475.2637 | 451.8703 | 437.5717 | 474.2887
3941.1135 | 475.2589 | 451.9089 | 437.6385 | 474.0554
3942.1135 | 475.2205 | 451.9272 | 437.6062 | 474.3783
3943.1135 | 475.0737 | 451.9868 | 437.5555 | 474.4168
3944.1135 | 474.9567 | 451.9967 | 437.4325 | 473.9741
3945.1135 | 474.9326 | 452.001 | 437.3341 | 474.286
3946.1135 | 474.9595 | 451.9943 | 437.5061 | 474.694
3947.1135 | 474.8909 | 451.9742 | 437.5919 | 474.4289
3948.1135 | 474.9461 | 452.0107 | 437.5763 | 474.2874
3949.1135 | 474.9342 | 452.0839 | 437.648 | 474.2315
3950.1135 | 474.9466 | 452.1766 | 437.661 | 474.2298
3951.1135 | 474.8784 | 452.1422 | 437.6438 | 474.4224
3952.1135 | 474.8277 | 452.0838 | 437.6742 | 474.2179
3953.1135 | 474.8953 | 452.1461 | 437.6196 | 474.321
3954.1135 | 474.9606 | 452.1624 | 437.6403 | 474.2799
3955.1135 | 474.9854 | 452.1502 | 437.6672 | 473.051
3956.1135 | 475.0028 | 452.2478 | 437.6754 | 473.5628
3957.1135 | 474.9791 | 452.1416 | 437.7705 | 470.6015
3958.1135 | 475.0644 | 452.0989 | 437.7502 | 474.7943
3959.1135 | 475.1697 | 452.1421 | 437.6611 | 474.8182
3960.1135 | 475.1612 | 452.1674 | 437.625 | 474.7004
3961.1135 | 475.2698 | 452.1777 | 437.8169 | 475.109
3962.1135 | 475.24 | 452.2096 | 437.7619 | 475.1627
3963.1135 | 475.2609 | 452.2448 | 437.7574 | 475.1046
3964.1135 | 475.1944 | 452.2965 | 437.7405 | 474.5024
3965.1135 | 475.2384 | 452.3325 | 437.8109 | 474.8655
3966.1135 | 475.2472 | 452.4424 | 437.7506 | 474.5603
3967.1135 | 475.1901 | 452.4221 | 437.6994 | 474.5011
3968.1135 | 475.1885 | 452.3833 | 437.8173 | 474.3939
3969.1135 | 475.0928 | 452.3722 | 437.8979 | 474.6686
3970.1135 | 475.1183 | 452.3836 | 437.9197 | 474.8208
3971.1135 | 475.117 | 452.3934 | 437.9621 | 475.0003
3972.1135 | 475.122 | 452.3831 | 437.918 | 474.9983
3973.1135 | 475.094 | 452.4202 | 437.9727 | 474.9952
3974.1135 | 475.0421 | 452.4605 | 437.96 | 474.5869
3975.1135 | 474.9639 | 452.4873 | 437.9872 | 474.5511
3976.1135 | 474.8924 | 452.506 | 438.0044 | 474.8055
3977.1135 | 474.8095 | 452.5031 | 437.9909 | 475.0038
3978.1135 | 474.7281 | 452.5455 | 437.9338 | 475.0146
3979.1135 | 474.7124 | 452.5709 | 437.9224 | 474.8497
3980.1135 | 474.6826 | 452.5914 | 438.0719 | 474.9891
3981.1135 | 474.6951 | 452.6472 | 437.9899 | 474.4534
3982.1135 | 474.7549 | 452.6894 | 437.8241 | 474.8645
3983.1135 | 474.7612 | 452.7012 | 437.9573 | 474.9969
3984.1135 | 474.8163 | 452.69 | 438.0123 | 474.989
3985.1135 | 474.8824 | 452.7933 | 437.954 | 475.0493
3986.1135 | 475.0081 | 452.7559 | 437.9235 | 475.0379
3987.1135 | 475.2701 | 452.698 | 437.9853 | 475.0365
3988.1135 | 476.2854 | 452.8171 | 437.9472 | 474.6204
3989.1135 | 478.1909 | 452.8752 | 438.1378 | 474.787
3990.1135 | 480.6442 | 452.962 | 438.2893 | 475.1669
3991.1135 | 483.5502 | 453.0358 | 438.4878 | 475.0894
3992.1135 | 486.7095 | 453.1484 | 438.5616 | 474.9259
3993.1135 | 490.1428 | 453.09 | 438.6104 | 474.6207
3994.1135 | 493.8074 | 453.2987 | 438.7359 | 474.6725
3995.1135 | 497.3689 | 453.568 | 438.8738 | 474.9187
3996.1135 | 500.4124 | 453.8246 | 439.0499 | 474.8375
3997.1135 | 503.1971 | 454.024 | 439.1348 | 475.2203
3998.1135 | 505.4961 | 454.1592 | 439.3216 | 475.2226
3999.1135 | 507.4132 | 454.2206 | 439.4915 | 475.4374
4000.1135 | 508.8892 | 454.355 | 439.503 | 475.5278
4001.1135 | 509.9536 | 454.4602 | 439.7265 | 475.5171
4002.1135 | 510.7252 | 454.6178 | 439.9663 | 475.8563
4003.1135 | 511.2496 | 454.9004 | 440.024 | 475.6831
4004.1135 | 511.4972 | 455.038 | 440.1109 | 475.5435
4005.1135 | 511.524 | 455.1208 | 440.1018 | 475.7109
4006.1135 | 511.4808 | 455.2738 | 440.2294 | 475.7747
4007.1135 | 511.1956 | 455.3668 | 440.3665 | 476.478
4008.1135 | 510.7905 | 455.4964 | 440.6243 | 476.3128
4009.1135 | 510.298 | 455.6236 | 440.6806 | 476.1683
4010.1135 | 509.791 | 455.6645 | 440.7029 | 476.3846
4011.1135 | 509.249 | 455.7815 | 440.7108 | 476.8125
4012.1135 | 508.6596 | 455.917 | 440.7464 | 476.9913
4013.1135 | 508.1056 | 456.0207 | 440.8497 | 476.9625
4014.1135 | 507.4548 | 456.1478 | 441.0114 | 476.6918
4015.1135 | 506.7623 | 456.262 | 441.1854 | 476.503
4016.1135 | 506.1087 | 456.3732 | 441.3468 | 476.6321
4017.1135 | 505.4097 | 456.4592 | 441.3378 | 476.8168
4018.1135 | 504.7465 | 456.6008 | 441.3814 | 476.9751
4019.1135 | 504.0978 | 456.7304 | 441.3284 | 477.0373
4020.1135 | 503.5169 | 456.7723 | 441.0429 | 477.0905
4021.1135 | 502.9538 | 456.822 | 441.3416 | 477.271
4022.1135 | 502.4562 | 457.0088 | 441.5369 | 477.4493
4023.1135 | 502.0159 | 457.0947 | 441.5049 | 477.5842
4024.1135 | 501.5427 | 457.1539 | 441.4388 | 477.5987
4025.1135 | 501.1898 | 457.2857 | 441.7147 | 477.7987
4026.1135 | 500.8246 | 457.31 | 441.89 | 477.9229
4027.1135 | 500.5555 | 457.318 | 442.096 | 478.0807
4028.1135 | 500.2142 | 457.5002 | 442.0775 | 477.8496
4029.1135 | 500.0643 | 457.5978 | 442.1151 | 478.0158
4030.1135 | 499.9521 | 457.7888 | 442.1337 | 478.0638
4031.1135 | 499.8474 | 457.87 | 442.1368 | 478.4712
4032.1135 | 499.8063 | 457.9372 | 442.2011 | 478.5328
4033.1135 | 499.7937 | 458.0107 | 442.3454 | 478.3788
4034.1135 | 499.807 | 458.0582 | 442.3656 | 478.464
4035.1135 | 499.8723 | 458.1961 | 442.4421 | 478.437
4036.1135 | 499.8496 | 458.2081 | 442.5547 | 477.9155
4037.1135 | 499.7185 | 458.3173 | 442.7314 | 478.2176
4038.1135 | 499.7169 | 458.4032 | 442.9174 | 478
4039.1135 | 499.8404 | 458.5448 | 442.9914 | 478.1022
4040.1135 | 499.971 | 458.6955 | 442.9537 | 478.2754
4041.1135 | 500.0672 | 458.7539 | 443.0443 | 478.6355
4042.1135 | 499.9565 | 458.7894 | 443.0465 | 478.426
4043.1135 | 500.0842 | 458.8897 | 443.0714 | 480.9191
4044.1135 | 500.1357 | 459.0116 | 443.1091 | 478.9055
4045.1135 | 500.2218 | 459.0464 | 443.204 | 478.3753
4046.1135 | 500.3539 | 459.172 | 443.3112 | 477.8105
4047.1135 | 500.4575 | 459.2482 | 443.4338 | 478.3614
4048.1135 | 500.4388 | 459.2982 | 443.5544 | 478.9676
4049.1135 | 500.4564 | 459.4061 | 443.6314 | 481.8487
4050.1135 | 500.5288 | 459.5226 | 443.721 | 478.0336
4051.1135 | 500.601 | 459.6212 | 443.8158 | 479.7299
4052.1135 | 500.7223 | 459.6037 | 443.8324 | 476.9607
4053.1135 | 500.74 | 459.7152 | 443.8951 | 475.383
4054.1135 | 500.6348 | 459.7556 | 443.993 | 477.0589
4055.1135 | 500.6227 | 459.8517 | 444.0379 | 478.9495
4056.1135 | 500.6927 | 460.0061 | 444.0754 | 483.0152
4057.1135 | 500.5931 | 460.1521 | 444.157 | 482.9704
4058.1135 | 500.6012 | 460.2336 | 444.2482 | 482.1626
4059.1135 | 500.6698 | 460.3019 | 444.3062 | 480.9602
4060.1135 | 500.6845 | 460.3438 | 444.3848 | 481.1546
4061.1135 | 500.6764 | 460.4274 | 444.3815 | 481.1522
4062.1135 | 500.7156 | 460.5254 | 444.4874 | 477.8622
4063.1135 | 500.7705 | 460.6105 | 444.6313 | 482.8153
4064.1135 | 500.783 | 460.6949 | 444.6701 | 482.624
4065.1135 | 500.7143 | 460.7408 | 444.6625 | 479.2674
4066.1135 | 500.5949 | 460.8243 | 444.8065 | 477.1748
4067.1135 | 500.5324 | 460.849 | 444.9986 | 477.0303
4068.1135 | 500.53 | 460.9206 | 445.0332 | 477.1733
4069.1135 | 500.5632 | 461.0361 | 445.0384 | 476.9417
4070.1135 | 500.4426 | 461.0897 | 445.0687 | 477.1039
4071.1135 | 500.3699 | 461.1551 | 445.0218 | 477.2529
4072.1135 | 500.3505 | 461.2582 | 445.1428 | 477.4141
4073.1135 | 500.3522 | 461.3356 | 445.2844 | 477.6651
4074.1135 | 500.3658 | 461.4589 | 445.4498 | 477.4138
4075.1135 | 500.4306 | 461.573 | 445.555 | 477.6192
4076.1135 | 500.4243 | 461.5665 | 445.5543 | 477.6452
4077.1292 | 500.3616 | 461.6369 | 445.6344 | 477.866
4078.1135 | 500.2691 | 461.7431 | 445.694 | 477.8166
4079.1135 | 500.2154 | 461.8265 | 445.7049 | 477.6091
4080.1135 | 500.2757 | 461.9206 | 445.8315 | 477.9094
4081.1135 | 500.265 | 461.9785 | 445.9461 | 478.1382
4082.1135 | 500.2645 | 462.0695 | 446.0044 | 478.2128
4083.1135 | 500.2501 | 462.1466 | 446.1066 | 478.4295
4084.1135 | 500.208 | 462.2129 | 446.1757 | 478.2687
4085.1135 | 500.2076 | 462.2686 | 446.1865 | 478.2795
4086.1135 | 500.2307 | 462.3863 | 446.2472 | 478.3568
4087.1135 | 500.2212 | 462.474 | 446.2842 | 478.6602
4088.1135 | 500.2063 | 462.5581 | 446.3299 | 478.4589
4089.1135 | 500.2282 | 462.6262 | 446.4982 | 478.4622
4090.1135 | 500.1936 | 462.7432 | 446.4749 | 478.7626
4091.1135 | 500.1406 | 462.7442 | 446.4645 | 478.6385
4092.1135 | 500.1007 | 462.7973 | 446.5298 | 479.1492
4093.1135 | 500.0417 | 462.9199 | 446.7056 | 479.3635
4094.1135 | 500.0283 | 462.9726 | 446.8221 | 479.0086
4095.1135 | 499.9966 | 463.0415 | 446.9564 | 478.9297
4096.1135 | 499.9392 | 463.0924 | 447.0024 | 479.2783
4097.1135 | 499.9311 | 463.0446 | 446.9741 | 479.4305
4098.1135 | 499.9544 | 463.142 | 447.0138 | 479.7178
4099.1135 | 499.9719 | 463.2872 | 447.0756 | 479.2891
4100.1135 | 499.985 | 463.4144 | 446.7918 | 479.4202
4101.1135 | 499.9276 | 463.3596 | 447.0232 | 479.2544
4102.1135 | 499.8321 | 463.4917 | 447.1821 | 479.7463
4103.1135 | 499.7629 | 463.5941 | 447.0621 | 479.8917
4104.1135 | 499.8304 | 463.723 | 447.0608 | 479.7452
4105.1135 | 499.8844 | 463.8228 | 447.1813 | 479.7561
4106.1135 | 499.8981 | 463.8737 | 447.3297 | 479.9251
4107.1135 | 499.9381 | 463.787 | 447.4049 | 480.2425
4108.1135 | 499.9003 | 463.8481 | 447.3394 | 480.4089
4109.1135 | 499.9647 | 463.9776 | 447.5139 | 480.3298
4110.1135 | 499.9574 | 464.0584 | 447.6215 | 480.3109
4111.1135 | 500.0033 | 464.1181 | 447.501 | 480.2437
4112.1135 | 499.9657 | 464.221 | 447.5692 | 480.5907
4113.1135 | 500.0126 | 464.2932 | 447.7777 | 480.7176
4114.1135 | 500.0337 | 464.3575 | 447.9589 | 480.4481
4115.1135 | 500.1197 | 464.4417 | 448.0422 | 480.6344
4116.1135 | 500.1799 | 464.59 | 448.1944 | 480.5766
4117.1135 | 500.3201 | 464.6463 | 448.1957 | 480.9077
4118.1135 | 500.4066 | 464.7102 | 448.2275 | 481.0053
4119.1135 | 500.451 | 464.8066 | 448.3383 | 480.8931
4120.1135 | 500.4778 | 464.8733 | 448.3065 | 481.086
4121.1135 | 500.4836 | 464.9234 | 448.4622 | 481.0526
4122.1135 | 500.4926 | 464.9471 | 448.4746 | 481.3703
4123.1135 | 500.5229 | 465.0368 | 448.4383 | 481.3183
4124.1135 | 500.5605 | 465.1497 | 448.4282 | 481.3875
4125.1135 | 500.5261 | 465.2221 | 448.4925 | 481.4448
4126.1135 | 500.5456 | 465.2844 | 448.5054 | 481.6114
4127.1135 | 500.5195 | 465.3879 | 448.6173 | 481.9952
4128.1135 | 500.4949 | 465.4729 | 448.6884 | 481.7842
4129.1135 | 500.5355 | 465.5196 | 448.7226 | 481.8001
4130.1135 | 500.4673 | 465.6206 | 448.8613 | 481.7911
4131.1135 | 500.468 | 465.6329 | 448.9572 | 481.8016
4132.1135 | 500.419 | 465.6585 | 448.9877 | 482.1857
4133.1135 | 500.3773 | 465.7543 | 449.0048 | 482.0761
4134.1135 | 500.3817 | 465.8292 | 449.0136 | 481.9761
4135.1135 | 500.3477 | 465.862 | 449.1098 | 482.0377
4136.1135 | 500.3331 | 465.9552 | 449.1411 | 482.1854
4137.1135 | 500.3461 | 465.9488 | 449.1531 | 482.7331
4138.1135 | 500.352 | 465.9937 | 449.22 | 482.6126
4139.1135 | 500.3054 | 466.1353 | 449.1705 | 482.4251
4140.1135 | 500.3049 | 466.2186 | 449.2754 | 482.2715
4141.1135 | 500.2769 | 466.3203 | 449.365 | 482.4323
4142.1135 | 500.2584 | 466.3376 | 449.517 | 482.7588
4143.1135 | 500.1834 | 466.4931 | 449.6079 | 482.8218
4144.1135 | 500.2441 | 466.4529 | 449.6569 | 482.3497
4145.1135 | 500.2984 | 466.5263 | 449.8 | 482.5768
4146.1135 | 500.289 | 466.6162 | 449.8636 | 482.5376
4147.1135 | 500.2571 | 466.6987 | 449.8711 | 482.8642
4148.1135 | 500.2359 | 466.7525 | 449.8814 | 482.8713
4149.1135 | 500.2406 | 466.7911 | 449.8613 | 482.9395
4150.1135 | 500.2649 | 466.8226 | 449.9491 | 482.91
4151.1135 | 500.1997 | 466.9173 | 449.9398 | 483.0711
4152.1135 | 500.2253 | 466.9856 | 450.0618 | 483.2706
4153.1135 | 500.2214 | 467.019 | 449.7913 | 483.4596
4154.1135 | 500.1893 | 467.0925 | 449.913 | 483.2503
4155.1135 | 500.0361 | 467.1859 | 450.0313 | 483.2112
4156.1135 | 500.006 | 467.226 | 450.1372 | 483.3902
4157.1135 | 499.9437 | 467.3321 | 450.2608 | 483.6753
4158.1135 | 499.8913 | 467.2701 | 450.3208 | 483.6929
4159.1292 | 499.8028 | 467.3412 | 450.4652 | 483.4827
4160.1135 | 499.7711 | 467.3731 | 450.5186 | 483.5837
4161.1135 | 499.7679 | 467.4798 | 450.5427 | 483.6944
4162.1135 | 499.6624 | 467.5162 | 450.5263 | 484.1051
4163.1135 | 499.5828 | 467.6234 | 450.6282 | 484.1061
4164.1135 | 499.6546 | 467.6989 | 450.7208 | 483.9381
4165.1135 | 499.7256 | 467.7398 | 450.9189 | 484.0813
4166.1135 | 499.7323 | 467.7953 | 450.9174 | 484.2739
4167.1135 | 499.7795 | 467.8596 | 450.9444 | 484.4129
4168.1135 | 499.7977 | 467.9201 | 450.9629 | 484.2898
4169.1135 | 499.8005 | 467.9783 | 451.0378 | 488.7622
4170.1135 | 499.8368 | 468.0478 | 451.0799 | 488.7303
4171.1135 | 499.7963 | 468.1183 | 451.0361 | 488.927
4172.1135 | 499.8155 | 468.1861 | 450.9613 | 489.1953
4173.1135 | 499.7987 | 468.2615 | 450.977 | 489.3628
4174.1135 | 499.785 | 468.3605 | 451.0868 | 489.3213
4175.1135 | 499.794 | 468.3732 | 451.126 | 489.2773
4176.1135 | 499.8052 | 468.4613 | 451.2354 | 489.3164
4177.1135 | 499.8591 | 468.4864 | 451.2579 | 489.943
4178.1135 | 499.948 | 468.5535 | 451.3434 | 489.8421
4179.1135 | 499.9005 | 468.6329 | 451.3929 | 489.8859
4180.1135 | 499.8677 | 468.6777 | 451.4792 | 490.0135
4181.1135 | 499.9443 | 468.8011 | 451.5233 | 490.012
4182.1135 | 500.0466 | 468.9123 | 451.58 | 490.3536
4183.1135 | 499.948 | 468.9111 | 451.5792 | 490.3075
4184.1135 | 500.058 | 468.9489 | 451.6215 | 490.3269
4185.1135 | 500.0611 | 469.0361 | 451.5849 | 490.1494
4186.1135 | 500.0285 | 469.0854 | 451.5217 | 490.3472
4187.1135 | 500.0594 | 469.1621 | 451.648 | 490.8061
4188.1135 | 500.0368 | 469.1642 | 451.6887 | 490.8739
4189.1135 | 500.0712 | 469.2366 | 451.8116 | 490.6003
4190.1135 | 500.0684 | 469.3009 | 451.8463 | 490.8815
4191.1135 | 500.0765 | 469.3209 | 452.0679 | 490.8873
4192.1135 | 500.1108 | 469.3984 | 452.061 | 491.1578
4193.1135 | 500.1099 | 469.3855 | 451.9213 | 490.9852
4194.1135 | 500.0428 | 469.4271 | 451.8041 | 490.9707
4195.1292 | 499.9729 | 469.5127 | 452.0132 | 490.8181
4196.1135 | 500.0667 | 469.6513 | 452.1422 | 491.2913
4197.1135 | 500.0745 | 469.6879 | 452.1716 | 491.5141
4198.1135 | 500.0728 | 469.749 | 452.2071 | 491.5603
4199.1135 | 500.051 | 469.7588 | 452.3245 | 491.4804
4200.1135 | 500.0204 | 469.8082 | 452.2917 | 491.4383
4201.1135 | 499.9661 | 469.8328 | 452.3884 | 491.4425
4202.1135 | 499.9759 | 469.9384 | 452.4314 | 491.9553
4203.1135 | 499.9544 | 469.9763 | 452.5012 | 491.9132
4204.1135 | 499.889 | 470.0889 | 452.4607 | 491.7827
4205.1135 | 499.8972 | 470.0168 | 452.4957 | 491.8062
4206.1135 | 499.8268 | 470.0162 | 452.6213 | 491.9212
4207.1135 | 499.7661 | 470.0549 | 452.7126 | 492.2155
4208.1135 | 499.8505 | 470.0683 | 452.7216 | 492.1242
4209.1135 | 499.8635 | 470.2428 | 452.4794 | 492.044
4210.1135 | 499.8706 | 470.288 | 452.4858 | 492.3159
4211.1135 | 499.895 | 470.344 | 452.6817 | 492.3579
4212.1135 | 499.9104 | 470.4158 | 452.7255 | 492.463
4213.1135 | 499.8582 | 470.4373 | 452.6634 | 492.4013
4214.1135 | 499.8722 | 470.4983 | 452.7658 | 492.4201
4215.1135 | 499.8886 | 470.5933 | 452.9093 | 492.3408
4216.1135 | 499.8041 | 470.6088 | 453.0274 | 492.6027
4217.1135 | 499.7211 | 470.6529 | 452.9729 | 492.7385
4218.1135 | 499.6994 | 470.6356 | 452.9907 | 492.5947
4219.1292 | 499.6912 | 470.6919 | 453.0748 | 492.4932
4220.1135 | 499.757 | 470.7822 | 453.1066 | 492.5379
4221.1135 | 499.7783 | 470.8668 | 453.1916 | 492.574
4222.1135 | 499.7806 | 470.8993 | 453.2506 | 492.7055
4223.1135 | 499.6473 | 470.9302 | 453.303 | 492.6873
4224.1135 | 499.5422 | 470.9628 | 453.2654 | 492.5144
4225.1135 | 499.5302 | 471.0577 | 453.352 | 492.3962
4226.1135 | 499.5448 | 471.1335 | 453.3643 | 492.7031
4227.1135 | 499.5167 | 471.177 | 453.4457 | 493.1538
4228.1135 | 499.4836 | 471.2348 | 453.5583 | 493.2822
4229.1135 | 499.4834 | 471.3074 | 453.5766 | 492.9835
4230.1135 | 499.4832 | 471.3339 | 453.5667 | 493.2297
4231.1135 | 499.4835 | 471.3396 | 453.6154 | 493.1758
4232.1135 | 499.4312 | 471.4399 | 453.6066 | 493.3192
4233.1135 | 499.3836 | 471.4743 | 453.6971 | 493.1714
4234.1135 | 499.4077 | 471.5198 | 453.7154 | 493.2142
4235.1135 | 499.437 | 471.6056 | 453.7446 | 493.2949
4236.1135 | 499.4008 | 471.5973 | 453.8206 | 493.5161
4237.1135 | 499.3779 | 471.6514 | 453.9423 | 493.7918
4238.1135 | 499.3986 | 471.6527 | 453.9532 | 493.5818
4239.1135 | 499.4289 | 471.7759 | 454.0117 | 493.7907
4240.1135 | 499.4587 | 471.8016 | 454.0299 | 493.4899
4241.1135 | 499.4955 | 471.7105 | 454.093 | 493.9004
4242.1135 | 499.4952 | 471.8365 | 454.1494 | 494.1777
4243.1135 | 499.5016 | 471.9733 | 454.1666 | 494.2439
4244.1135 | 499.4375 | 472.012 | 454.2949 | 494.0256
4245.1135 | 499.43 | 472.0484 | 454.2467 | 494.2311
4246.1135 | 499.5213 | 472.0901 | 454.2524 | 494.2479
4247.1135 | 499.5709 | 472.0725 | 454.2359 | 494.5793
4248.1135 | 499.5559 | 472.0713 | 454.2842 | 494.4825
4249.1135 | 499.5554 | 472.1523 | 454.3617 | 494.2728
4250.1135 | 499.5032 | 472.2334 | 454.4561 | 494.4379
4251.1135 | 499.5215 | 472.2304 | 454.4446 | 494.4555
4252.1135 | 499.5781 | 472.2676 | 454.336 | 494.8005
4253.1135 | 499.5746 | 472.3464 | 454.3704 | 494.8849
4254.1135 | 499.6298 | 472.3864 | 454.5452 | 494.6562
4255.1135 | 499.6792 | 472.4619 | 454.6384 | 494.6148
4256.1135 | 499.7188 | 472.5606 | 454.7319 | 494.7613
4257.1135 | 499.7357 | 472.6424 | 454.9034 | 494.1553
4258.1135 | 499.6272 | 472.7361 | 454.8784 | 494.3657
4259.1135 | 499.501 | 472.8039 | 454.8384 | 494.0905
4260.1135 | 499.4119 | 472.7718 | 454.811 | 494.1673
4261.1135 | 499.4314 | 472.8462 | 454.7772 | 494.677
4262.1135 | 499.4359 | 472.9292 | 454.7892 | 494.6818
4263.1135 | 499.4903 | 472.9508 | 454.8546 | 494.6564
4264.1135 | 499.5425 | 472.9746 | 454.8555 | 495.0748
4265.1135 | 499.5481 | 472.9564 | 455.0095 | 494.9846
4266.1135 | 499.5317 | 473.0416 | 455.1295 | 494.8456
4267.1135 | 499.5086 | 473.1013 | 455.1167 | 495.4306
4268.1135 | 499.5271 | 473.1842 | 455.1949 | 495.4795
4269.1135 | 499.4878 | 473.227 | 455.1599 | 495.5242
4270.1135 | 499.5516 | 473.2796 | 455.1772 | 495.1126
4271.1135 | 499.5487 | 473.2005 | 455.2393 | 495.4508
4272.1135 | 499.5922 | 473.3227 | 455.287 | 495.6722
4273.1135 | 499.6545 | 473.3451 | 455.3821 | 495.7113
4274.1135 | 499.6729 | 473.3916 | 455.4039 | 495.6838
4275.1135 | 499.7347 | 473.414 | 455.3188 | 495.4843
4276.1135 | 499.8019 | 473.5096 | 455.3792 | 495.5532
4277.1135 | 499.8299 | 473.5921 | 455.476 | 495.8422
4278.1292 | 499.8303 | 473.6552 | 455.4428 | 495.8105
4279.1292 | 499.7666 | 473.7019 | 455.556 | 495.6366
4280.1135 | 499.4955 | 473.7802 | 455.6325 | 495.5799
4281.1135 | 499.155 | 473.7667 | 455.7124 | 495.6347
4282.1135 | 498.7413 | 473.7972 | 455.7445 | 495.955
4283.1135 | 498.2337 | 473.8603 | 455.7243 | 495.8782
4284.1135 | 497.6246 | 473.8753 | 455.771 | 495.8146
4285.1135 | 497.0989 | 473.9003 | 455.7331 | 495.6585
4286.1135 | 496.4376 | 473.8492 | 455.7893 | 495.717
4287.1135 | 495.7773 | 473.8903 | 455.6517 | 495.932
4288.1135 | 495.0965 | 473.9298 | 455.4968 | 496.0688
4289.1135 | 494.3487 | 473.9466 | 455.5789 | 495.8947
4290.1135 | 493.548 | 473.9044 | 455.6712 | 495.9104
4291.1135 | 492.7893 | 473.8514 | 455.5093 | 495.9072
4292.1135 | 491.9457 | 473.8719 | 455.6272 | 495.9527
4293.1135 | 491.0671 | 473.9167 | 455.6805 | 495.8444
4294.1135 | 490.2694 | 473.9154 | 455.5778 | 495.8779
4295.1135 | 489.4527 | 473.923 | 455.5962 | 495.7393
4296.1135 | 488.6319 | 473.9286 | 455.6763 | 495.7729
4297.1135 | 487.8546 | 473.947 | 455.6698 | 495.8726
4298.1135 | 487.0923 | 473.9415 | 455.6221 | 495.8904
4299.1135 | 486.2537 | 473.8889 | 455.6108 | 495.9763
4300.1135 | 485.3084 | 473.8456 | 455.6308 | 495.8721
4301.1135 | 484.4211 | 473.8858 | 455.6104 | 495.8949
4302.1135 | 483.4826 | 473.9011 | 455.6393 | 496.1565
4303.1135 | 482.6417 | 473.9086 | 455.4985 | 496.096
4304.1135 | 481.8871 | 473.8873 | 455.4983 | 496.0461
4305.1135 | 481.0785 | 473.8166 | 455.4545 | 495.768
4306.1135 | 480.2567 | 473.71 | 455.4251 | 495.8602
4307.1135 | 479.3871 | 473.6229 | 455.3353 | 496.0432
4308.1135 | 478.5717 | 473.5883 | 455.4006 | 495.9553
4309.1135 | 477.7708 | 473.5651 | 455.4854 | 495.7551
4310.1135 | 476.9171 | 473.4613 | 455.4348 | 495.8638
4311.1135 | 476.1006 | 473.3091 | 455.2006 | 495.8473
4312.1135 | 475.2648 | 473.3173 | 455.1433 | 495.8224
4313.1135 | 474.4096 | 473.3504 | 455.12 | 495.8301
4314.1135 | 473.5607 | 473.3157 | 455.0873 | 495.5089
4315.1135 | 472.7346 | 473.3337 | 455.0245 | 494.5423
4316.1135 | 471.9709 | 473.245 | 455.0055 | 490.9843
4317.1135 | 471.1252 | 473.1671 | 454.9234 | 491.5326
4318.1135 | 470.3328 | 473.1508 | 454.9181 | 492.5888
4319.1135 | 469.4854 | 473.1457 | 454.8137 | 491.0279
4320.1135 | 468.6627 | 473.0608 | 454.7019 | 490.9845
4321.1135 | 467.8413 | 472.908 | 454.7127 | 491.4866
4322.1135 | 467.0241 | 472.8007 | 454.6045 | 489.9585
4323.1135 | 466.226 | 472.7819 | 454.5951 | 489.9307
4324.1135 | 465.3467 | 472.6962 | 454.4396 | 489.8571
4325.1135 | 464.4692 | 472.5845 | 454.3886 | 490.8662
4326.1135 | 463.646 | 472.5542 | 454.2524 | 491.5722
4327.1135 | 462.8929 | 472.5286 | 454.2228 | 491.379
4328.1135 | 462.1237 | 472.4323 | 454.3126 | 491.3644
4329.1135 | 461.3861 | 472.3386 | 454.3031 | 491.1055
4330.1135 | 460.5579 | 472.1458 | 454.205 | 493.1149
4331.1135 | 459.6643 | 472.089 | 454.1885 | 491.7441
4332.1135 | 458.8555 | 471.9799 | 454.0698 | 491.7203
4333.1135 | 458.0051 | 471.8808 | 453.8308 | 492.9627
4334.1135 | 457.1989 | 471.8295 | 453.7501 | 493.0109
4335.1135 | 456.3901 | 471.8274 | 453.6695 | 493.1169
4336.1135 | 455.5997 | 471.7105 | 453.4521 | 492.8873
4337.1135 | 454.8308 | 471.5548 | 453.4032 | 492.8457
4338.1135 | 454.0597 | 471.527 | 453.2493 | 492.8594
4339.1292 | 453.3405 | 471.4624 | 453.1527 | 492.4952
4340.1135 | 452.5742 | 471.3856 | 453.1137 | 492.6314
4341.1135 | 451.768 | 471.3014 | 453.0233 | 492.5516
4342.1135 | 450.991 | 471.2123 | 452.8802 | 492.881
4343.1135 | 450.2592 | 471.1773 | 452.7928 | 492.7755
4344.1135 | 449.5331 | 471.019 | 452.5579 | 492.74
4345.1135 | 448.6421 | 470.9406 | 452.5138 | 492.5148
4346.1135 | 447.7272 | 470.8435 | 452.498 | 492.5799
4347.1135 | 446.8994 | 470.7134 | 452.3048 | 492.7945
4348.1135 | 446.1055 | 470.6092 | 452.3218 | 492.6336
4349.1135 | 445.2892 | 470.4691 | 452.183 | 492.4375
4350.1135 | 444.5429 | 470.3301 | 452.1423 | 492.4158
4351.1135 | 443.796 | 470.2314 | 452.128 | 492.2623
4352.1135 | 443.0243 | 470.167 | 452.0522 | 492.4461
4353.1135 | 442.2842 | 470.0401 | 451.8545 | 492.3127
4354.1135 | 441.5561 | 469.898 | 451.7256 | 492.1191
4355.1135 | 440.8512 | 469.7312 | 451.5691 | 492.0698
4356.1135 | 440.116 | 469.5589 | 451.4026 | 491.9183
4357.1135 | 439.2835 | 469.3994 | 451.2031 | 492.054
4358.1135 | 438.4885 | 469.3048 | 450.8351 | 492.0595
4359.1135 | 437.722 | 469.2675 | 450.8548 | 491.6836
4360.1135 | 436.9251 | 469.0468 | 450.6832 | 491.5294
4361.1135 | 436.156 | 468.8695 | 450.6053 | 491.4362
4362.1135 | 435.432 | 468.7469 | 450.2707 | 491.428
4363.1135 | 434.7628 | 468.6164 | 450.2511 | 491.2107
4364.1135 | 434.0591 | 468.4045 | 450.2134 | 490.834
4365.1135 | 433.3392 | 468.2345 | 450.1069 | 490.7438
4366.1135 | 432.5385 | 468.1119 | 450.0202 | 490.8126
4367.1135 | 431.8388 | 467.9187 | 449.8774 | 490.8028
4368.1135 | 431.0889 | 467.7166 | 449.8442 | 490.4385
4369.1135 | 430.3537 | 467.6015 | 449.8194 | 490.1286
4370.1135 | 429.631 | 467.4533 | 449.6729 | 490.2359
4371.1135 | 428.9226 | 467.1851 | 449.4692 | 490.0432
4372.1135 | 428.2841 | 467.0365 | 449.4302 | 490.1522
4373.1135 | 427.5879 | 466.8193 | 449.0674 | 489.7647
4374.1135 | 426.8295 | 466.6518 | 448.8926 | 489.7548
4375.1135 | 426.0848 | 466.4167 | 448.6864 | 489.5386
4376.1135 | 425.3614 | 466.289 | 448.6046 | 489.3439
4377.1135 | 424.6214 | 466.1301 | 448.4427 | 489.2321
4378.1135 | 423.9143 | 465.9702 | 448.2293 | 489.0367
4379.1135 | 423.1851 | 465.8558 | 447.8552 | 488.757
4380.1135 | 422.4359 | 465.6402 | 447.7853 | 488.6497
4381.1135 | 421.7031 | 465.4065 | 447.7262 | 488.4136
4382.1135 | 421.0021 | 465.217 | 447.6277 | 488.4887
4383.1135 | 420.3451 | 465.0332 | 447.3973 | 488.1172
4384.1135 | 419.6226 | 464.8315 | 447.2526 | 487.9025
4385.1135 | 418.897 | 464.6629 | 447.1894 | 487.5079
4386.1135 | 418.236 | 464.3899 | 446.8884 | 487.4673
4387.1135 | 417.5711 | 464.2411 | 446.7551 | 487.5053
4388.1135 | 416.8801 | 464.0496 | 446.6198 | 487.2356
4389.1135 | 416.1531 | 463.8851 | 446.5718 | 486.9073
4390.1135 | 415.4174 | 463.6909 | 446.3213 | 486.6078
4391.1135 | 414.7231 | 463.5496 | 446.153 | 486.4742
4392.1135 | 414.0244 | 463.2702 | 445.9467 | 486.4721
4393.1135 | 413.4006 | 463.0449 | 445.7723 | 485.8892
4394.1135 | 412.6981 | 462.8341 | 445.5458 | 485.7756
4395.1135 | 411.9906 | 462.6596 | 445.5083 | 485.527
4396.1135 | 411.26 | 462.4495 | 445.5157 | 485.2658
4397.1135 | 410.6532 | 462.2356 | 445.3266 | 485.2654
4398.1135 | 410.0292 | 462.0365 | 445.0085 | 485.0675
4399.1135 | 409.2917 | 461.8095 | 444.8151 | 484.4572
4400.1135 | 408.6426 | 461.6446 | 444.5877 | 484.3121
4401.1135 | 408.0342 | 461.5327 | 444.2773 | 484.2068
4402.1135 | 407.3906 | 461.295 | 444.2355 | 484.2735
4403.1135 | 406.7846 | 461.0277 | 444.0852 | 483.8017
4404.1135 | 406.1522 | 460.8131 | 444.0439 | 483.7519
4405.1135 | 405.488 | 460.6489 | 444.0659 | 483.2961
4406.1135 | 404.8085 | 460.4628 | 443.562 | 483.0852
4407.1135 | 404.2056 | 460.1758 | 443.3276 | 483.0378
4408.1135 | 403.6021 | 459.9576 | 443.22 | 482.7761
4409.1135 | 402.8944 | 459.754 | 443.1026 | 482.4033
4410.1135 | 402.225 | 459.5469 | 442.6237 | 482.2426
4411.1135 | 401.6091 | 459.3251 | 442.4815 | 481.8862
4412.1135 | 400.9889 | 459.1128 | 442.6152 | 481.8009
4413.1135 | 400.3322 | 458.9525 | 442.3558 | 481.5967
4414.1135 | 399.6832 | 458.7978 | 442.202 | 481.1094
4415.1135 | 399.0548 | 458.5735 | 442.0072 | 480.7441
4416.1135 | 398.4246 | 458.2563 | 441.7251 | 480.5922
4417.1135 | 397.7669 | 457.9918 | 441.4862 | 480.6181
4418.1135 | 397.1922 | 457.7501 | 441.2259 | 480.5405
4419.1135 | 396.6196 | 457.6041 | 441.1611 | 479.9397
4420.1135 | 396.0211 | 457.2791 | 440.9484 | 479.7609
4421.1135 | 395.39 | 457.0873 | 440.8123 | 479.4932
4422.1135 | 394.761 | 456.8682 | 440.6259 | 479.3586
4423.1135 | 394.1158 | 456.64 | 440.453 | 479.0413
4424.1135 | 393.4971 | 456.4831 | 440.2564 | 478.914
4425.1135 | 392.9452 | 456.2798 | 440.0549 | 478.5202
4426.1135 | 392.3388 | 455.9312 | 439.8707 | 478.2147
4427.1135 | 391.78 | 455.702 | 439.7229 | 478.1488
4428.1135 | 391.2237 | 455.4758 | 439.5465 | 477.7737
4429.1135 | 390.5826 | 455.2154 | 439.2439 | 477.4907
4430.1135 | 389.9228 | 454.9769 | 439.0474 | 477.0672
4431.1135 | 389.2967 | 454.7487 | 438.7639 | 476.7811
4432.1135 | 388.7209 | 454.5014 | 438.5263 | 476.5809
4433.1135 | 388.1249 | 454.2758 | 438.3438 | 476.4586
4434.1135 | 387.5076 | 454.0148 | 438.2526 | 475.9973
4435.1135 | 386.8644 | 453.8211 | 438.0603 | 475.656
4436.1135 | 386.2606 | 453.557 | 437.8223 | 475.2494
4437.1135 | 385.6626 | 453.3706 | 437.6948 | 475.2711
4438.1135 | 385.0665 | 453.199 | 437.4311 | 475.0018
4439.1135 | 384.4255 | 452.8959 | 437.1528 | 474.7366
4440.1135 | 383.8137 | 452.6656 | 437.0452 | 474.338
4441.1135 | 383.2345 | 452.4834 | 436.8842 | 474.009
4442.1135 | 382.6586 | 452.2202 | 436.7973 | 473.9387
4443.1135 | 382.0509 | 451.9103 | 436.5892 | 473.7696
4444.1135 | 381.4934 | 451.6847 | 436.3856 | 473.4483
4445.1135 | 380.9842 | 451.4658 | 436.192 | 473.092
4446.1135 | 380.3655 | 451.1749 | 435.9939 | 472.7345
4447.1135 | 379.8057 | 450.9314 | 435.7863 | 472.7151
4448.1135 | 379.2295 | 450.752 | 435.6072 | 472.3687
4449.1135 | 378.6839 | 450.4611 | 435.2968 | 472.0489
4450.1135 | 378.1369 | 450.157 | 434.9932 | 471.6103
4451.1135 | 377.6302 | 449.9766 | 434.8384 | 471.3372
4452.1135 | 377.1395 | 449.6734 | 434.4263 | 471.2018
4453.1135 | 376.5852 | 449.4276 | 434.2236 | 471.0189
4454.1135 | 376.0892 | 449.1464 | 434.0722 | 470.6033
4455.1135 | 375.5396 | 448.9302 | 433.8937 | 470.3821
4456.1135 | 374.9987 | 448.6982 | 433.5968 | 469.9364
4457.1135 | 374.4475 | 448.5516 | 433.4138 | 469.8882
4458.1135 | 373.88 | 448.2709 | 433.3239 | 469.5013
4459.1135 | 373.3193 | 447.9426 | 433.0698 | 469.3173
4460.1135 | 372.7655 | 447.7047 | 432.9587 | 468.9016
4461.1135 | 372.1507 | 447.4671 | 432.844 | 468.5433
4462.1135 | 371.6015 | 447.2751 | 432.5807 | 468.4815
4463.1135 | 371.0388 | 447.0054 | 432.2808 | 468.2708
4464.1135 | 370.4972 | 446.7298 | 432.0932 | 467.9219
4465.1135 | 369.9258 | 446.3812 | 431.9723 | 467.6398
4466.1135 | 369.3361 | 446.1254 | 431.666 | 467.3562
4467.1135 | 368.7874 | 445.8957 | 431.3523 | 467.0808
4468.1135 | 368.2523 | 445.5853 | 431.1216 | 466.7187
4469.1135 | 367.7325 | 445.3669 | 430.9594 | 466.5655
4470.1135 | 367.2443 | 445.1174 | 430.6921 | 466.0874
4471.1135 | 366.7208 | 444.9143 | 430.455 | 465.8622
4472.1135 | 366.1843 | 444.6705 | 430.2164 | 465.7303
4473.1135 | 365.6244 | 444.3865 | 429.9221 | 465.5839
4474.1135 | 365.0634 | 444.1538 | 429.722 | 465.0179
4475.1135 | 364.4897 | 443.9347 | 429.6082 | 464.689
4476.1135 | 363.9525 | 443.6279 | 429.4618 | 464.4039
4477.1135 | 363.3722 | 443.4152 | 429.2394 | 464.1851
4478.1135 | 362.7987 | 443.2051 | 428.9793 | 463.756
4479.1135 | 362.2472 | 442.8503 | 428.7483 | 463.5816
4480.1135 | 361.7187 | 442.5421 | 428.5056 | 463.1674
4481.1135 | 361.1783 | 442.3066 | 428.3154 | 462.9363
4482.1135 | 360.6851 | 442.0535 | 427.9334 | 462.7912
4483.1135 | 360.1411 | 441.9141 | 427.8535 | 462.3571
4484.1135 | 359.6464 | 441.6036 | 427.5621 | 462.197
4485.1135 | 359.1485 | 441.2949 | 427.3607 | 461.6282
4486.1135 | 358.607 | 441.0481 | 427.144 | 461.252
4487.1135 | 358.1287 | 440.729 | 426.9712 | 461.3366
4488.1135 | 357.6256 | 440.4641 | 426.6867 | 461.0223
4489.1135 | 357.0731 | 440.2458 | 426.4258 | 460.7411
4490.1135 | 356.6345 | 440.0945 | 426.1846 | 460.2874
4491.1135 | 356.1393 | 439.7689 | 425.9832 | 460.0622
4492.1135 | 355.6688 | 439.5294 | 425.6816 | 459.926
4493.1135 | 355.1964 | 439.2396 | 425.449 | 459.6917
4494.1135 | 354.6923 | 438.9166 | 425.301 | 459.1675
4495.1135 | 354.2006 | 438.5806 | 425.0543 | 458.8979
4496.1135 | 353.6843 | 438.3093 | 424.8586 | 458.5567
4497.1135 | 353.159 | 438.1165 | 424.6396 | 458.5554
4498.1135 | 352.6549 | 437.8324 | 424.392 | 458.2516
4499.1135 | 352.1427 | 437.5271 | 424.0557 | 458.0947
4500.1135 | 351.6634 | 437.2842 | 423.887 | 457.578
4501.1135 | 351.2157 | 437.0619 | 423.7314 | 457.2782
4502.1135 | 350.7278 | 436.8938 | 423.4675 | 457.1621
4503.1135 | 350.2326 | 436.6004 | 423.1774 | 456.8591
4504.1135 | 349.7413 | 436.2889 | 423.0483 | 456.4923
4505.1135 | 349.2313 | 436.0376 | 422.857 | 456.0674
4506.1135 | 348.7053 | 435.7171 | 422.7119 | 455.6851
4507.1135 | 348.1621 | 435.4145 | 422.4581 | 455.6386
4508.1135 | 347.6692 | 435.1647 | 422.3119 | 455.2936
4509.1135 | 347.1904 | 434.9005 | 422.1324 | 454.8535
4510.1135 | 346.7349 | 434.5036 | 421.856 | 454.4175
4511.1135 | 346.2649 | 434.223 | 421.596 | 454.1972
4512.1135 | 345.7962 | 433.9966 | 421.3787 | 453.9689
4513.1135 | 345.3493 | 433.8236 | 421.129 | 453.7282
4514.1135 | 344.8876 | 433.5266 | 420.9383 | 453.2875
4515.1135 | 344.4417 | 433.2768 | 420.6906 | 452.848
4516.1135 | 343.9734 | 433.0028 | 420.437 | 452.4764
4517.1135 | 343.4767 | 432.7681 | 420.174 | 452.4161
4518.1292 | 342.9939 | 432.4587 | 420.0479 | 452.1511
4519.1135 | 342.5641 | 432.1799 | 419.9262 | 451.9088
4520.1135 | 342.1013 | 432.0205 | 419.6098 | 451.4867
4521.1135 | 341.6629 | 431.8002 | 419.3361 | 451.2314
4522.1135 | 341.2088 | 431.4723 | 419.2582 | 450.9649
4523.1135 | 340.7008 | 431.2027 | 419.0553 | 450.6989
4524.1135 | 340.2292 | 430.8438 | 418.6367 | 450.28
4525.1135 | 339.793 | 430.5545 | 418.4844 | 449.8879
4526.1135 | 339.303 | 430.2507 | 418.1514 | 449.5515
4527.1135 | 338.8325 | 430.0424 | 417.8168 | 449.4471
4528.1135 | 338.3527 | 429.755 | 417.5581 | 449.1021
4529.1135 | 337.8865 | 429.5181 | 417.4231 | 448.847
4530.1135 | 337.4207 | 429.2885 | 417.2238 | 448.5086
4531.1135 | 337.0309 | 428.964 | 417.0234 | 448.2985
4532.1135 | 336.5405 | 428.5659 | 416.7219 | 448.1645
4533.1135 | 336.0555 | 428.164 | 416.4041 | 447.8886
4534.1135 | 335.5626 | 428.0114 | 416.3824 | 447.4996
4535.1135 | 335.1375 | 427.696 | 416.1264 | 447.1103
4536.1135 | 334.6877 | 427.4307 | 415.8824 | 446.8043
4537.1135 | 334.2589 | 427.1728 | 415.738 | 446.7073
4538.1135 | 333.7531 | 426.972 | 415.4296 | 446.4666
4539.1135 | 333.2406 | 426.7828 | 415.1118 | 445.8934
4540.1135 | 332.8204 | 426.4179 | 414.8868 | 445.5871
4541.1135 | 332.4566 | 426.1462 | 414.7361 | 445.2646
4542.1135 | 332.0222 | 425.8349 | 414.3915 | 445.1622
4543.1135 | 331.6087 | 425.6066 | 414.1843 | 444.833
4544.1135 | 331.1684 | 425.3569 | 413.9596 | 444.4076
4545.1135 | 330.7219 | 425.1206 | 413.8167 | 444.0713
4546.1135 | 330.3652 | 424.7572 | 413.6497 | 443.7888
4547.1135 | 329.9722 | 424.5348 | 413.2899 | 443.6258
4548.1135 | 329.5589 | 424.2992 | 412.9504 | 443.4854
4549.1135 | 329.1575 | 424.0091 | 412.7664 | 443.1251
4550.1135 | 328.7066 | 423.7645 | 412.51 | 442.8567
4551.1135 | 328.2862 | 423.5453 | 412.3545 | 442.4997
4552.1135 | 327.8208 | 423.2336 | 412.0768 | 442.4127
4553.1135 | 327.3704 | 422.9654 | 411.7456 | 442.0689
4554.1135 | 326.9271 | 422.7156 | 411.4902 | 441.6675
4555.1135 | 326.4964 | 422.5116 | 411.323 | 441.3873
4556.1135 | 326.0445 | 422.1423 | 410.9303 | 441.0994
4557.1135 | 325.5726 | 421.8189 | 410.8206 | 440.9406
4558.1135 | 325.2014 | 421.5551 | 410.5814 | 440.6453
4559.1135 | 324.8103 | 421.329 | 410.2491 | 440.2102
4560.1135 | 324.3977 | 421.0026 | 410.0938 | 439.8207
4561.1135 | 323.963 | 420.8271 | 409.9006 | 439.5784
4562.1135 | 323.5317 | 420.5836 | 409.6805 | 439.4702
4563.1135 | 323.1259 | 420.3097 | 409.4437 | 439.0165
4564.1135 | 322.6711 | 419.9076 | 409.1909 | 438.7704
4565.1135 | 322.217 | 419.5918 | 408.9474 | 438.3904
4566.1135 | 321.8012 | 419.3568 | 408.7529 | 438.1043
4567.1135 | 321.3704 | 419.1178 | 408.6167 | 438.0663
4568.1135 | 320.9472 | 418.8507 | 408.2129 | 437.8214
4569.1135 | 320.5261 | 418.6215 | 407.9803 | 437.507
4570.1135 | 320.1493 | 418.2699 | 407.813 | 437.0527
4571.1135 | 319.7649 | 417.9953 | 407.6409 | 436.6708
4572.1135 | 319.3119 | 417.7481 | 407.3771 | 436.4585
4573.1135 | 318.8886 | 417.5246 | 407.0825 | 436.1382
4574.1135 | 318.4872 | 417.2604 | 406.7525 | 435.8096
4575.1135 | 318.0679 | 417.0717 | 406.5177 | 435.3343
4576.1135 | 317.7158 | 416.691 | 406.4178 | 434.9893
4577.1135 | 317.3643 | 416.339 | 406.1794 | 434.8465
4578.1135 | 316.9521 | 416.0595 | 405.9265 | 434.5155
4579.1135 | 316.5252 | 415.8489 | 405.7097 | 434.1824
4580.1135 | 316.1072 | 415.5974 | 405.5285 | 433.6439
4581.1135 | 315.6703 | 415.294 | 405.2031 | 433.3992
4582.1135 | 315.2616 | 415.0184 | 404.9512 | 433.2291
4583.1135 | 314.8604 | 414.7159 | 404.5612 | 433.0203
4584.1135 | 314.4667 | 414.4762 | 404.3816 | 432.7687
4585.1135 | 314.1117 | 414.3334 | 404.2262 | 432.4258
4586.1135 | 313.7495 | 414.1221 | 403.9732 | 432.1152
4587.1135 | 313.3411 | 413.8172 | 403.7716 | 431.9682
4588.1135 | 312.9615 | 413.4605 | 403.5175 | 431.7225
4589.1135 | 312.599 | 413.1627 | 403.2192 | 431.4781
4590.1135 | 312.2024 | 412.8473 | 402.9655 | 431.0898
4591.1135 | 311.85 | 412.6384 | 402.7535 | 430.768
4592.1135 | 311.4941 | 412.3709 | 402.5043 | 430.5752
4593.1135 | 311.0988 | 412.0448 | 402.3314 | 430.2804
4594.1135 | 310.7182 | 411.7451 | 402.1304 | 430.0157
4595.1135 | 310.2831 | 411.4667 | 401.8521 | 429.6638
4596.1135 | 309.8641 | 411.1701 | 401.6055 | 429.3359
4597.1135 | 309.4736 | 410.8874 | 401.3854 | 429.1804
4598.1135 | 309.0641 | 410.6169 | 401.0977 | 428.8431
4599.1135 | 308.695 | 410.3919 | 400.9033 | 428.5199
4600.1135 | 308.3085 | 410.084 | 400.5888 | 428.008
4601.1135 | 307.884 | 409.7795 | 400.2199 | 427.752
4602.1135 | 307.4624 | 409.4925 | 400.0052 | 427.5704
4603.1135 | 307.0672 | 409.2394 | 399.7724 | 427.3888
4604.1135 | 306.6664 | 409.0156 | 399.6339 | 427.0486
4605.1135 | 306.2776 | 408.7423 | 399.4935 | 426.6377
4606.1135 | 305.9209 | 408.5144 | 399.2616 | 426.3116
4607.1135 | 305.5471 | 408.2025 | 399.1217 | 426.1718
4608.1135 | 305.17 | 408.0369 | 398.9337 | 425.8939
4609.1135 | 304.7959 | 407.7559 | 398.7598 | 425.623
4610.1135 | 304.3649 | 407.436 | 398.372 | 425.2123
4611.1135 | 303.9628 | 407.1803 | 398.1427 | 424.942
4612.1135 | 303.5862 | 406.9043 | 397.7826 | 424.7392
4613.1135 | 303.243 | 406.6259 | 397.4305 | 424.4861
4614.1135 | 302.8997 | 406.3199 | 397.2183 | 424.1713
4615.1135 | 302.5377 | 406.0143 | 397.0306 | 423.8042
4616.1135 | 302.2035 | 405.769 | 396.7534 | 423.5436
4617.1135 | 301.8354 | 405.5682 | 396.6518 | 423.3704
4618.1135 | 301.5226 | 405.3397 | 396.4084 | 423.0903
4619.1135 | 301.17 | 405.0959 | 395.9825 | 422.7593
4620.1135 | 300.8198 | 404.7119 | 395.8975 | 422.3403
4621.1135 | 300.4487 | 404.4006 | 395.6646 | 422.0872
4622.1135 | 300.0684 | 404.0949 | 395.4114 | 421.8943
4623.1135 | 299.6289 | 403.8929 | 395.1252 | 421.6743
4624.1135 | 299.2469 | 403.6203 | 394.8209 | 421.4247
4625.1135 | 298.8797 | 403.3457 | 394.675 | 421.0675
4626.1135 | 298.4724 | 403.1134 | 394.4718 | 420.8741
4627.1135 | 298.1246 | 402.883 | 394.1958 | 420.661
4628.1135 | 297.7526 | 402.5836 | 393.9154 | 420.3635
4629.1135 | 297.427 | 402.287 | 393.6809 | 420.0018
4630.1135 | 297.0499 | 401.9919 | 393.638 | 419.5866
4631.1135 | 296.6988 | 401.7749 | 393.3446 | 419.2841
4632.1135 | 296.368 | 401.5466 | 392.9579 | 419.1124
4633.1135 | 296.0152 | 401.2625 | 392.7255 | 418.7484
4634.1135 | 295.6994 | 401.0674 | 392.5212 | 418.4614
4635.1135 | 295.366 | 400.6721 | 392.3268 | 418.1093
4636.1135 | 294.9873 | 400.4136 | 392.1889 | 417.8628
4637.1135 | 294.6054 | 400.0974 | 391.8926 | 417.6907
4638.1135 | 294.2795 | 399.9606 | 391.7391 | 417.3395
4639.1135 | 293.957 | 399.6928 | 391.5289 | 417.076
4640.1135 | 293.5885 | 399.3776 | 391.2372 | 416.8081
4641.1135 | 293.2615 | 399.1274 | 391.0482 | 416.5507
4642.1135 | 292.913 | 398.8665 | 390.7777 | 416.4169
4643.1135 | 292.5613 | 398.5333 | 390.472 | 416.1481
4644.1135 | 292.1501 | 398.2731 | 390.1164 | 415.9026
4645.1135 | 291.7779 | 397.9819 | 389.9278 | 415.5622
4646.1135 | 291.4525 | 397.7192 | 389.8404 | 415.2673
4647.1135 | 291.0705 | 397.446 | 389.4743 | 415.062
4648.1135 | 290.724 | 397.1338 | 389.29 | 414.7859
4649.1135 | 290.342 | 396.8938 | 389.1364 | 414.4231
4650.1135 | 290.0164 | 396.7466 | 389.0028 | 414.0689
4651.1135 | 289.6696 | 396.5206 | 388.7222 | 413.8548
4652.1135 | 289.3301 | 396.2976 | 388.4581 | 413.7496
4653.1135 | 288.9961 | 396.0091 | 388.1115 | 413.461
4654.1135 | 288.6929 | 395.7578 | 387.9479 | 413.2257
4655.1135 | 288.3502 | 395.5018 | 387.6807 | 412.8294
4656.1135 | 288.0095 | 395.2288 | 387.3039 | 412.7018
4657.1135 | 287.6383 | 394.9744 | 387.116 | 412.5193
4658.1135 | 287.2971 | 394.6253 | 386.9448 | 412.2474
4659.1135 | 286.9402 | 394.3324 | 386.8343 | 411.9348
4660.1135 | 286.6217 | 394.1111 | 386.534 | 411.6949
4661.1135 | 286.2686 | 393.8236 | 386.425 | 411.4044
4662.1135 | 285.9455 | 393.4803 | 386.1411 | 411.2459
4663.1135 | 285.628 | 393.2308 | 385.6692 | 410.9428
4664.1135 | 285.3442 | 393.0024 | 385.3952 | 410.5113
4665.1135 | 285.0258 | 392.7555 | 385.2116 | 410.1678
4666.1135 | 284.678 | 392.5138 | 384.971 | 409.9629
4667.1135 | 284.3428 | 392.3657 | 384.7645 | 409.7114
4668.1135 | 283.9977 | 392.0247 | 384.6186 | 409.4654
4669.1135 | 283.6684 | 391.6899 | 384.4327 | 409.1652
4670.1135 | 283.335 | 391.4113 | 384.1854 | 408.8178
4671.1135 | 282.9788 | 391.1449 | 383.9103 | 408.4533
4672.1135 | 282.6146 | 390.8441 | 383.7204 | 408.0998
4673.1135 | 282.2725 | 390.5952 | 383.379 | 407.8014
4674.1135 | 281.9483 | 390.2994 | 383.1994 | 407.4462
4675.1135 | 281.6256 | 390.0634 | 382.976 | 407.1772
4676.1135 | 281.3428 | 389.8286 | 382.7506 | 406.9014
4677.1135 | 281.0282 | 389.5459 | 382.3618 | 406.7078
4678.1135 | 280.7308 | 389.2661 | 382.1682 | 406.4384
4679.1135 | 280.4192 | 389.0477 | 382.0406 | 406.1474
4680.1135 | 280.0904 | 388.785 | 381.7783 | 405.8497
4681.1135 | 279.7663 | 388.5754 | 381.5909 | 405.5248
4682.1135 | 279.429 | 388.3677 | 381.3671 | 405.2962
4683.1135 | 279.1091 | 388.0768 | 381.2277 | 404.9499
4684.1135 | 278.8126 | 387.8476 | 380.9815 | 404.6488
4685.1135 | 278.4682 | 387.5219 | 380.6922 | 404.3257
4686.1135 | 278.172 | 387.2792 | 380.5179 | 404.0798
4687.1135 | 277.8587 | 387.0057 | 380.3279 | 403.9294
4688.1135 | 277.5291 | 386.7561 | 380.0282 | 403.6186
4689.1135 | 277.1933 | 386.4604 | 379.7399 | 403.2513
4690.1135 | 276.8607 | 386.1877 | 379.5034 | 402.9726
4691.1135 | 276.5432 | 385.9666 | 379.2779 | 402.7382
4692.1135 | 276.247 | 385.7566 | 379.0108 | 402.5533
4693.1135 | 275.9545 | 385.4737 | 378.7586 | 402.2547
4694.1135 | 275.6297 | 385.189 | 378.5027 | 401.9012
4695.1135 | 275.2923 | 384.8709 | 378.2804 | 401.5497
4696.1135 | 274.9402 | 384.6126 | 378.0002 | 401.3164
4697.1135 | 274.6483 | 384.3858 | 377.7888 | 401.0787
4698.1135 | 274.3362 | 384.0885 | 377.6018 | 400.8271
4699.1135 | 274.0504 | 383.8856 | 377.3906 | 400.5027
4700.1135 | 273.7158 | 383.6462 | 377.1809 | 400.1737
4701.1135 | 273.3958 | 383.4078 | 377.0264 | 399.9599
4702.1135 | 273.0378 | 383.1372 | 376.8499 | 399.7546
4703.1135 | 272.7243 | 382.8773 | 376.6412 | 399.4615
4704.1135 | 272.4134 | 382.659 | 376.4608 | 399.1512
4705.1135 | 272.1074 | 382.4247 | 376.2433 | 398.8511
4706.1135 | 271.8452 | 382.2484 | 375.9064 | 398.5552
4707.1135 | 271.5426 | 381.9654 | 375.5999 | 398.3619
4708.1135 | 271.2517 | 381.6351 | 375.3475 | 398.109
4709.1135 | 270.9307 | 381.3663 | 375.0737 | 397.79
4710.1135 | 270.6262 | 381.1199 | 374.8963 | 397.4891
4711.1135 | 270.3205 | 380.9217 | 374.6831 | 397.2082
4712.1135 | 270.0153 | 380.6728 | 374.4288 | 397.0659
4713.1135 | 269.7095 | 380.4569 | 374.2934 | 396.8001
4714.1135 | 269.4017 | 380.1493 | 374.0892 | 396.4888
4715.1135 | 269.0882 | 379.8846 | 373.8293 | 396.1801
4716.1135 | 268.7714 | 379.5795 | 373.6443 | 395.9318
4717.1135 | 268.494 | 379.3372 | 373.3641 | 395.7215
4718.1135 | 268.1918 | 379.1207 | 373.1665 | 395.4526
4719.1135 | 267.9581 | 378.8741 | 372.8707 | 395.1759
4720.1135 | 267.7074 | 378.6244 | 372.5581 | 394.8782
4721.1135 | 267.4522 | 378.3463 | 372.2645 | 394.5876
4722.1135 | 267.1705 | 378.1259 | 372.1174 | 394.4846
4723.1135 | 266.8392 | 377.8549 | 371.8083 | 394.2114
4724.1135 | 266.5039 | 377.6944 | 371.5695 | 393.9305
4725.1135 | 266.204 | 377.4503 | 371.3787 | 393.6568
4726.1135 | 265.9107 | 377.1745 | 371.2044 | 393.4301
4727.1135 | 265.6654 | 376.8838 | 371.0362 | 393.3193
4728.1135 | 265.3699 | 376.6683 | 370.8196 | 393.0255
4729.1135 | 265.0865 | 376.5157 | 370.5663 | 392.733
4730.1135 | 264.796 | 376.2554 | 370.3775 | 392.421
4731.1135 | 264.4918 | 375.9381 | 370.2141 | 392.1842
4732.1135 | 264.1813 | 375.6885 | 370.0223 | 392.0258
4733.1135 | 263.8624 | 375.4226 | 369.7144 | 391.7314
4734.1135 | 263.5699 | 375.1662 | 369.5677 | 391.4654
4735.1135 | 263.288 | 374.9524 | 369.3109 | 391.1595
4736.1135 | 263.0533 | 374.6829 | 369.038 | 390.9572
4737.1135 | 262.7627 | 374.4179 | 368.8019 | 390.7403
4738.1135 | 262.4577 | 374.1552 | 368.5338 | 390.4806
4739.1135 | 262.165 | 373.895 | 368.3555 | 390.1922
4740.1135 | 261.8641 | 373.6059 | 368.1899 | 389.8946
4741.1135 | 261.5524 | 373.3779 | 367.9085 | 389.6461
4742.1135 | 261.239 | 373.1573 | 367.7959 | 389.4215
4743.1135 | 260.9502 | 372.934 | 367.5555 | 389.1673
4744.1135 | 260.692 | 372.7131 | 367.1423 | 388.8738
4745.1135 | 260.3997 | 372.3942 | 366.8016 | 388.5305
4746.1135 | 260.082 | 372.1756 | 366.7474 | 388.265
4747.1135 | 259.7817 | 371.9059 | 366.5963 | 388.1241
4748.1135 | 259.4883 | 371.5473 | 366.4294 | 387.8909
4749.1135 | 259.2069 | 371.334 | 366.1136 | 387.6219
4750.1135 | 258.9156 | 371.0669 | 365.8186 | 387.349
4751.1135 | 258.6377 | 370.8708 | 365.5563 | 387.069
4752.1135 | 258.3345 | 370.6205 | 365.3251 | 386.8661
4753.1135 | 258.0514 | 370.3742 | 365.1411 | 386.6482
4754.1135 | 257.776 | 370.0856 | 364.914 | 386.3954
4755.1135 | 257.519 | 369.8068 | 364.775 | 386.127
4756.1135 | 257.2382 | 369.5711 | 364.5381 | 385.8646
4757.1135 | 256.9389 | 369.3983 | 364.2184 | 385.6458
4758.1135 | 256.6558 | 369.186 | 363.9889 | 385.4532
4759.1135 | 256.3751 | 368.8937 | 363.7916 | 385.1865
4760.1135 | 256.1124 | 368.6778 | 363.5389 | 384.8958
4761.1135 | 255.8363 | 368.4496 | 363.283 | 384.6194
4762.1135 | 255.5446 | 368.236 | 363.1016 | 384.4716
4763.1135 | 255.2836 | 367.9984 | 362.9249 | 384.1833
4764.1135 | 255.0029 | 367.7838 | 362.706 | 383.8973
4765.1135 | 254.7197 | 367.5416 | 362.4361 | 383.652
4766.1135 | 254.4664 | 367.3267 | 362.2378 | 383.3879
4767.1135 | 254.1897 | 367.0333 | 362.1876 | 383.2037
4768.1135 | 253.9394 | 366.8118 | 361.9548 | 382.9567
4769.1135 | 253.6621 | 366.5432 | 361.729 | 382.6989
4770.1135 | 253.3878 | 366.3216 | 361.361 | 382.4111
4771.1135 | 253.1429 | 366.054 | 361.2485 | 382.1557
4772.1135 | 252.8782 | 365.7903 | 360.9154 | 381.9505
4773.1135 | 252.5933 | 365.5396 | 360.6582 | 381.6889
4774.1135 | 252.3374 | 365.3079 | 360.5089 | 381.4214
4775.1135 | 252.0913 | 365.0789 | 360.2799 | 381.0839
4776.1135 | 251.8093 | 364.8755 | 360.0725 | 380.8279
4777.1135 | 251.5575 | 364.6414 | 359.913 | 380.6573
4778.1135 | 251.2742 | 364.3442 | 359.7122 | 380.4045
4779.1135 | 250.9842 | 364.073 | 359.48 | 380.1666
4780.1135 | 250.6881 | 363.8356 | 359.1705 | 379.8677
4781.1135 | 250.4098 | 363.596 | 358.9562 | 379.6518
4782.1135 | 250.1612 | 363.364 | 358.7415 | 379.4572
4783.1135 | 249.8788 | 363.0974 | 358.3492 | 379.222
4784.1135 | 249.6171 | 362.9057 | 358.2265 | 378.9514
4785.1135 | 249.3717 | 362.6835 | 358.0667 | 378.6952
4786.1135 | 249.1056 | 362.5488 | 357.8136 | 378.4477
4787.1135 | 248.8552 | 362.28 | 357.6383 | 378.2914
4788.1135 | 248.6065 | 362.0103 | 357.5063 | 378.0503
4789.1135 | 248.3452 | 361.8055 | 357.3383 | 377.8109
4790.1135 | 248.1225 | 361.5016 | 357.026 | 377.5625
4791.1135 | 247.8672 | 361.3217 | 356.8203 | 377.2891
4792.1135 | 247.6356 | 361.0465 | 356.6632 | 377.1284
4793.1135 | 247.3714 | 360.892 | 356.489 | 376.8531
4794.1135 | 247.1067 | 360.5712 | 356.3234 | 376.6301
4795.1135 | 246.8208 | 360.2911 | 356.0621 | 376.3887
4796.1135 | 246.5559 | 360.1529 | 355.8042 | 376.1682
4797.1135 | 246.3121 | 359.8589 | 355.5705 | 375.9492
4798.1135 | 246.0684 | 359.541 | 355.3682 | 375.6983
4799.1135 | 245.8426 | 359.2956 | 355.215 | 375.4625
4800.1135 | 245.6366 | 359.0828 | 354.8929 | 375.2072
4801.1135 | 245.3638 | 358.8464 | 354.5955 | 374.9563
4802.1135 | 245.0964 | 358.6119 | 354.3973 | 374.7805
4803.1135 | 244.8083 | 358.4333 | 354.1862 | 374.5244
4804.1135 | 244.5463 | 358.1607 | 353.9265 | 374.2536
4805.1135 | 244.3034 | 357.8905 | 353.717 | 373.9703
4806.1135 | 244.0777 | 357.6131 | 353.5932 | 373.6551
4807.1135 | 243.8343 | 357.4539 | 353.3932 | 373.4586
4808.1135 | 243.5769 | 357.2909 | 353.2925 | 373.1924
4809.1135 | 243.3227 | 356.9766 | 353.0749 | 372.9557
4810.1135 | 243.065 | 356.728 | 352.83 | 372.6528
4811.1135 | 242.828 | 356.4516 | 352.5398 | 372.3542
4812.1135 | 242.5641 | 356.2334 | 352.3048 | 372.1948
4813.1135 | 242.2942 | 356.0933 | 351.9816 | 371.947
4814.1135 | 242.0351 | 355.8663 | 351.7522 | 371.7674
4815.1135 | 241.801 | 355.621 | 351.6358 | 371.4425
4816.1135 | 241.5635 | 355.3018 | 351.2796 | 371.2128
4817.1135 | 241.3408 | 355.0088 | 350.9404 | 371.0182
4818.1135 | 241.1188 | 354.7622 | 350.8259 | 370.801
4819.1135 | 240.8962 | 354.5883 | 350.7372 | 370.5874
4820.1135 | 240.6663 | 354.3913 | 350.5922 | 370.3212
4821.1135 | 240.4465 | 354.2128 | 350.4356 | 370.0965
4822.1135 | 240.1736 | 353.9592 | 350.2021 | 369.907
4823.1135 | 239.9177 | 353.7404 | 349.8714 | 369.6909
4824.1135 | 239.6556 | 353.555 | 349.711 | 369.4757
4825.1135 | 239.3713 | 353.2876 | 349.4919 | 369.2123
4826.1135 | 239.0836 | 353.0626 | 349.2636 | 369.0266
4827.1135 | 238.7883 | 352.8485 | 348.9908 | 368.7784
4828.1135 | 238.5319 | 352.59 | 348.828 | 368.5597
4829.1135 | 238.2731 | 352.3784 | 348.448 | 368.3218
4830.1135 | 238.024 | 352.1737 | 348.2817 | 368.1337
4831.1135 | 237.7752 | 351.9758 | 348.0169 | 367.875
4832.1135 | 237.5387 | 351.7322 | 347.7883 | 367.7389
4833.1135 | 237.2856 | 351.5494 | 347.6061 | 367.4947
4834.1135 | 237.0358 | 351.2506 | 347.5215 | 367.2516
4835.1135 | 236.8051 | 350.9884 | 347.35 | 366.9922
4836.1135 | 236.5868 | 350.7037 | 347.1715 | 366.7699
4837.1135 | 236.3616 | 350.4353 | 346.9238 | 366.5604
4838.1135 | 236.1182 | 350.2096 | 346.749 | 366.3317
4839.1135 | 235.8971 | 349.977 | 346.5167 | 366.074
4840.1135 | 235.6638 | 349.8165 | 346.3994 | 365.835
4841.1135 | 235.4374 | 349.6036 | 346.208 | 365.6178
4842.1135 | 235.2218 | 349.3391 | 345.9277 | 365.4582
4843.1135 | 234.9887 | 349.1087 | 345.6632 | 365.2139
4844.1135 | 234.7393 | 348.9258 | 345.4863 | 364.9508
4845.1135 | 234.4942 | 348.7204 | 345.3085 | 364.7132
4846.1135 | 234.2581 | 348.4942 | 345.1171 | 364.478
4847.1135 | 233.9992 | 348.2402 | 344.9341 | 364.3091
4848.1135 | 233.7483 | 347.9624 | 344.7062 | 364.071
4849.1135 | 233.5327 | 347.7576 | 344.5605 | 363.8568
4850.1135 | 233.2822 | 347.5198 | 344.4 | 363.5695
4851.1135 | 233.0654 | 347.2751 | 344.2147 | 363.3726
4852.1135 | 232.8472 | 347.0327 | 343.9113 | 363.1521
4853.1135 | 232.6181 | 346.8205 | 343.7428 | 362.9261
4854.1135 | 232.364 | 346.5722 | 343.6784 | 362.7208
4855.1135 | 232.1369 | 346.3405 | 343.4313 | 362.4644
4856.1135 | 231.9171 | 346.1688 | 343.2124 | 362.2671
4857.1135 | 231.6864 | 345.9204 | 342.8877 | 362.0707
4858.1135 | 231.4536 | 345.7183 | 342.6874 | 361.8886
4859.1135 | 231.2189 | 345.5243 | 342.5269 | 361.6131
4860.1135 | 230.978 | 345.3778 | 342.3259 | 361.3667
4861.1135 | 230.7318 | 345.1356 | 342.1014 | 361.1539
4862.1135 | 230.4699 | 344.9256 | 341.8449 | 360.9743
4863.1135 | 230.2531 | 344.7038 | 341.6561 | 360.7574
4864.1135 | 230.0286 | 344.5236 | 341.4231 | 360.5273
4865.1135 | 229.7594 | 344.3041 | 341.1483 | 360.266
4866.1135 | 229.5269 | 344.0113 | 340.9554 | 360.0448
4867.1135 | 229.3003 | 343.7231 | 340.81 | 359.8534
4868.1135 | 229.0646 | 343.4901 | 340.6446 | 359.6329
4869.1135 | 228.841 | 343.2919 | 340.4144 | 359.4017
4870.1135 | 228.6446 | 343.0325 | 340.1571 | 359.1581
4871.1135 | 228.4195 | 342.7541 | 339.8915 | 358.9204
4872.1135 | 228.2018 | 342.5585 | 339.7319 | 358.7329
4873.1135 | 227.9845 | 342.3512 | 339.6006 | 358.5167
4874.1135 | 227.7514 | 342.1933 | 339.4533 | 358.2901
4875.1135 | 227.5356 | 341.998 | 339.1921 | 358.042
4876.1135 | 227.3066 | 341.7536 | 339.0282 | 357.8172
4877.1135 | 227.0802 | 341.4867 | 338.9612 | 357.6362
4878.1135 | 226.8535 | 341.227 | 338.7043 | 357.3996
4879.1135 | 226.6461 | 341.0516 | 338.5051 | 357.1782
4880.1135 | 226.4313 | 340.8332 | 338.2679 | 356.9278
4881.1135 | 226.2149 | 340.6265 | 337.9901 | 356.6999
4882.1135 | 226.0286 | 340.4031 | 337.8164 | 356.5228
4883.1135 | 225.796 | 340.1728 | 337.5691 | 356.2912
4884.1135 | 225.6077 | 339.9557 | 337.335 | 356.0514
4885.1135 | 225.4198 | 339.7278 | 337.0673 | 355.8174
4886.1135 | 225.1753 | 339.535 | 336.8787 | 355.6038
4887.1135 | 224.9271 | 339.2589 | 336.6965 | 355.4105
4888.1135 | 224.7211 | 339.0362 | 336.5476 | 355.1901
4889.1135 | 224.5134 | 338.8483 | 336.2991 | 354.9465
4890.1135 | 224.2778 | 338.6797 | 336.0485 | 354.6824
4891.1135 | 224.0553 | 338.4226 | 335.8027 | 354.4114
4892.1135 | 223.8251 | 338.18 | 335.6168 | 354.2362
4893.1135 | 223.5987 | 337.9469 | 335.4386 | 354.003
4894.1135 | 223.3504 | 337.7033 | 335.1558 | 353.7607
4895.1135 | 223.1559 | 337.4481 | 334.9913 | 353.5315
4896.1135 | 222.9158 | 337.2369 | 334.8049 | 353.2971
4897.1135 | 222.6904 | 337.0693 | 334.6319 | 353.1051
4898.1135 | 222.4774 | 336.8677 | 334.422 | 352.8748
4899.1135 | 222.251 | 336.6284 | 334.3161 | 352.6527
4900.1135 | 222.0422 | 336.4178 | 334.0218 | 352.4105
4901.1135 | 221.8174 | 336.3161 | 333.7866 | 352.1821
4902.1135 | 221.5829 | 336.0808 | 333.5075 | 352.0153
4903.1135 | 221.3559 | 335.8299 | 333.3038 | 351.7903
4904.1135 | 221.1377 | 335.512 | 333.1376 | 351.5553
4905.1135 | 220.8689 | 335.339 | 332.9851 | 351.2509
4906.1135 | 220.6721 | 335.1036 | 332.7684 | 351.0537
4907.1135 | 220.4906 | 334.9044 | 332.5835 | 350.8747
4908.1135 | 220.3263 | 334.6663 | 332.3048 | 350.6628
4909.1135 | 220.1107 | 334.4493 | 332.1229 | 350.4266
4910.1135 | 219.8885 | 334.3259 | 331.9075 | 350.2325
4911.1135 | 219.6392 | 334.025 | 331.7271 | 350.014
4912.1135 | 219.4318 | 333.7505 | 331.5728 | 349.8253
4913.1135 | 219.2189 | 333.5552 | 331.4033 | 349.6196
4914.1135 | 218.9973 | 333.3871 | 331.2648 | 349.374
4915.1135 | 218.813 | 333.1985 | 331.0224 | 349.1836
4916.1135 | 218.6203 | 332.9986 | 330.7842 | 348.962
4917.1135 | 218.4117 | 332.7524 | 330.59 | 348.7722
4918.1135 | 218.1984 | 332.5579 | 330.4326 | 348.5672
4919.1135 | 218.0129 | 332.358 | 330.1612 | 348.3312
4920.1135 | 217.8117 | 332.1993 | 329.9325 | 348.1281
4921.1135 | 217.5929 | 331.9552 | 329.7627 | 347.9034
4922.1135 | 217.3677 | 331.6952 | 329.6399 | 347.7352
4923.1135 | 217.1679 | 331.5203 | 329.4393 | 347.4976
4924.1135 | 216.9714 | 331.2796 | 329.3348 | 347.2852
4925.1135 | 216.7594 | 331.0813 | 329.1489 | 347.0754
4926.1135 | 216.5569 | 330.8483 | 328.9084 | 346.8682
4927.1135 | 216.3827 | 330.6398 | 328.6861 | 346.6589
4928.1135 | 216.1739 | 330.3632 | 328.501 | 346.443
4929.1135 | 215.9987 | 330.219 | 328.3632 | 346.2394
4930.1135 | 215.7814 | 330.0256 | 328.0732 | 345.9809
4931.1135 | 215.571 | 329.8105 | 327.7335 | 345.7632
4932.1135 | 215.3754 | 329.6132 | 327.7326 | 345.5748
4933.1135 | 215.1811 | 329.407 | 327.5405 | 345.3697
4934.1135 | 214.9809 | 329.3007 | 327.2916 | 345.1462
4935.1135 | 214.7697 | 329.0329 | 327.1185 | 344.911
4936.1135 | 214.5365 | 328.7652 | 326.9486 | 344.6974
4937.1135 | 214.3037 | 328.5703 | 326.6766 | 344.5144
4938.1135 | 214.0956 | 328.3165 | 326.4678 | 344.2914
4939.1135 | 213.877 | 328.1186 | 326.3388 | 344.0911
4940.1135 | 213.6894 | 327.8845 | 326.1386 | 343.8767
4941.1135 | 213.4851 | 327.6507 | 325.8941 | 343.6629
4942.1135 | 213.2937 | 327.4375 | 325.6869 | 343.4687
4943.1135 | 213.0553 | 327.2468 | 325.6171 | 343.2562
4944.1135 | 212.8597 | 327.0757 | 325.4658 | 343.0397
4945.1135 | 212.6405 | 326.9449 | 325.251 | 342.7741
4946.1135 | 212.4761 | 326.6808 | 324.9607 | 342.5708
4947.1135 | 212.287 | 326.4313 | 324.7301 | 342.4328
4948.1135 | 212.1109 | 326.2116 | 324.5188 | 342.2208
4949.1135 | 211.9054 | 325.9882 | 324.4007 | 342.0133
4950.1135 | 211.7258 | 325.7943 | 324.1969 | 341.78